NRC INSPECTION MANUAL	CCIB

MANUAL CHAPTER 0613

DOCUMENTING 10 CFR PART 52

CONSTRUCTION INSPECTIONS

Page Intentionally Left Blank

0613-01	PURPOSE	1

0613-02	OBJECTIVES	1

0613-03	DEFINITIONS	1

0613-04	RESPONSIBILITIES AND AUTHORITIES	6

04.01	General Responsibilities	6

04.02	Inspectors	6

04.03	Deputy Regional Administrator for Construction	7

04.04	Regional Branch Chiefs and Division Directors	7

04.05	Division of Construction Inspection and Operational Programs (DCIP), Office of New Reactors (NRO)	7

0613-05	SCREENING INSPECTION RESULTS	7

05.01	Screen for a Violation of Regulatory Requirements or Failure to Meet Licensee or Contractor Commitments	7

05.02	Screen for Enforcement Categories	8

05.03	Screen for Greater-than-Minor Significance	8

05.04	Screen for Identification Credit	8

05.05	Analyze for Construction Safety Focus Component Aspects	9

05.06	Screening for Type of Finding and Applicable Enforcement Action	9

0613-06	DOCUMENTING INSPECTION RESULTS	10

0613-07	DOCUMENTING INSPECTION RESULTS WITH NO FINDINGS AND DOCUMENTING OBSERVATIONS	10

0613-08	DOCUMENTING NRC-IDENTIFIED, SELF-REVEALING, AND LICENSEE-IDENTIFIED FINDINGS THAT MEET THE SCREENING CRITERIA SPECIFIED IN APPENDIX B, SECTION 1-4	10

08.01	Title	11

08.02	Scope	11

08.03	Summary	11

08.04	Findings	11

08.05  	Documents Reviewed	14

0613-09	DOCUMENTING SELF-REVEALING AND LICENSEE-IDENTIFIED FINDINGS THAT DO NOT MEET THE SCREENING CRITERIA SPECIFIED IN APPENDIX B, SECTION 1-4	14

0613-10	DOCUMENTING UNRESOLVED ITEMS	15

10.01 	Opening URIs	15

10.02  	Closing URIs	15

0613-11	DOCUMENTING MINOR VIOLATIONS	16

11.01	Minor Violations	16

0613-12	DOCUMENTING FINDINGS ASSOCIATED WITH LICENSEE EVENT REPORTS AND CONSTRUCTION DEFICIENCY REPORTS	16

12.01	Closure of CDRs	16

12.02 	Closure of Cited Violations	17

0613-13	OTHER GUIDANCE	17

13.01	Treatment of Third Party Reviews	17

13.02	Non-Routine Inspections	18

13.03	Documenting Backfit Items	18

0613-14	COMPILING AN INSPECTION REPORT	18

14.01	Cover Letter	18

14.02	Notice of Violation	20

14.03	Cover Page	20

14.04	Table of Contents	20

14.05	Inspection Report Content	20

0613-15	ISSUING INSPECTION REPORTS	23

15.01	Report Issuance	23

15.02	Report Timeliness	23

0613-16	RELEASE AND DISCLOSURE OF INSPECTION REPORTS AND ASSOCIATED DOCUMENTS	24

APPENDIX A	Acronyms Used in IMC 0613

APPENDIX B	Issue Screening

APPENDIX C	Guidance for Expanded Inspection Reports

APPENDIX D	Guidance for Documenting Inspection Procedure 35007 “Part 52, Identification and Resolution of Construction Problems”

APPENDIX E	Examples of Greater-than-Minor Construction Violations

APPENDIX F		Construction Safety Focus Components and Aspects

APPENDIX G	Guidance for the Use of the Construction Inspection Program Information Management System (CIPIMS) for Documenting Inspections and Developing Inspection Reports

ATTACHMENT 1	Construction Findings Flowchart

ATTACHMENT 2	Revision History for IMC 0613

# 0613-01	PURPOSE

To provide guidance for screening inspection results and define the content and format for power reactor construction inspection reports.

# 0613-02	OBJECTIVES

02.01 To screen inspection results to determine if issues warrant documentation in inspection reports.

02.02 To ensure inspection reports clearly communicate significant inspection results in a consistent manner to licensees, NRC staff, and the public.

02.03 To document the basis for enforcement action.

02.04 To provide inspection results as input to the “Periodic Assessment of Construction Inspection Program Results,” (IMC 2505).

# 0613-03	DEFINITIONS

Apparent Violation (AV):  A violation of regulatory requirements that is being considered for potential escalated enforcement action.

Applicant:  A person or an entity applying for a license, permit, or other form of Commission permission or approval under 10 CFR Part 50 or 10 CFR Part 52.

Closed Item: A matter previously reported as an inspection finding, a deviation, a non-conformance, an item reported by the licensee (e.g., 10 CFR Part 21 report, 10 CFR Part 50.55(e) construction deficiency report or licensee event report), or an unresolved item that the inspector concludes has been satisfactorily resolved based on information obtained during the current inspection.

Construction Activity:  As used in this manual chapter, any activity associated with the construction, fabrication, or testing of structures, components, subcomponents, subsystems, or systems that are subject to NRC regulations, either at the construction site or at remote fabrication or testing facilities.  Construction activities also include related design and engineering activities including design changes for the structures, systems, and components.

Construction Deficiency Report:   As described in 10 CFR 50.55(e), an official notification to the NRC of a construction defect or failure to comply that could create a substantial safety hazard, were it to remain uncorrected.  A “substantial safety hazard” means a loss of safety function to the extent that there is a major reduction in the degree of protection provided to public health and safety from the facility.

Construction Finding:  A violation of regulatory requirements that is of greater-than-minor significance and is not material to ITAAC Acceptance Criteria.

Construction Inspection Program Information Management System (CIPIMS):  The database that provides the means to document, report, and track NRC inspection activities and their results.

Construction Issue:  An inspection result that is dispositioned in accordance with the guidance in this manual chapter.

Contractor:  Any organization or individual under contract to furnish items or services to a licensee engaging in an NRC-regulated activity.  It includes the terms consultant, vendor, supplier, fabricator, constructor, and sub-tier levels of these organizations.

Construction Safety Focus Component:  Fundamental performance attributes that extend across areas important to safety culture.  The construction safety focus components in alphabetical order are:   Accountability; Construction Experience; Corrective Action Program; Decision-Making; Environment for Raising Concerns; Preventing, Detecting, and Mitigating Perceptions of Retaliation; Resources; Self and Independent Assessments; Work Control; and Work Practices.

Construction Safety Focus Component Aspect:  A safety culture performance characteristic that is the most significant contributor to a finding.

Construction Safety Focus Issue (CSFI):   A CSFI is a theme made up of four or more inspection findings (more than minor) that are assigned the same construction safety focus component aspect about which the NRC staff has a concern with the licensee’s scope of efforts or progress in addressing the theme.  The CSFI theme will be identified as the safety focus component aspect.  A CSFI in the safety conscious work environment (SCWE) construction safety focus area exists if there is a single finding with a documented construction safety focus component aspect in the SCWE area, or the licensee has received a chilling effect letter, or the licensee has received correspondence from the NRC which transmitted an enforcement action with a Severity Level of I, II, or III, and which involved discrimination, or a confirmatory order which involved discrimination and the Agency has a concern with the licensee’s scope of efforts or progress in addressing the SCWE concern.

Escalated Enforcement Action:  A notice of violation or civil penalty for any Severity Level I, II, or III violation; or an order based upon a violation.

Family of ITAAC:  A grouping of ITAAC that are related through similar construction processes, resulting products, and general inspection attributes.

Finding:  A violation of regulatory requirements that has greater-than-minor significance.  Examples of findings include a Construction Finding, an ITAAC-Related Construction Finding, or an ITAAC Finding, per the definitions and guidance in this manual chapter.

Inspection:  (1) An NRC activity consisting of examination, observation, or measurement to determine applicant/licensee/contractor/vendor conformance with requirements and/or standards.  (2) Applicant/licensee/contractor/vendor quality control measures consisting of examination, observation, or measurements to determine the conformance of materials, supplies, components, parts, systems, processes or structures to pre-determined quality requirements.

Inspection Document:  Any material obtained or developed during an inspection that is considered to be an NRC record.  (Inspectors should review IMC 0620, “Inspection Documents and Records,” for clarification on how materials become agency records.)

Integrated Inspection Report: A construction inspection report that combines inspection items from all inspections (resident, regional, etc.) conducted during a specific time period.

Inspections, Tests, Analyses, and Acceptance Criteria (ITAAC):  Those inspections, tests, analyses, and acceptance criteria identified in the combined license that if met are necessary and sufficient to provide reasonable assurance that the facility has been constructed and will operate in conformity with the license, the provisions of the Atomic Energy Act, as amended, and the Commission’s rules and regulations.  The ITAAC identified in a combined license referencing a certified design will include the ITAAC defined in the Tier 1 documentation.  Site-specific ITAAC, which include emergency planning ITAAC and ITAAC that are not part of the certified design, will also be included in a combined license.  ITAAC are conditions of the license and must be satisfactorily completed before an affirmative 10 CFR 52.103(g) finding can be made.

ITAAC Finding:  A violation of regulatory requirements that is of greater-than-minor significance, is associated with a specific ITAAC for which the licensee has submitted the ITAAC closeout letter, and is material to the ITAAC acceptance criteria.  This type of finding could prevent the ITAAC from being verified as met by the NRC and could require that previously closed ITAAC be re-opened.  An ITAAC finding may be related to a single ITAAC or a family of ITACC.

ITAAC-Related Construction Finding:  A violation of regulatory requirements that is of greater-than-minor significance, is associated with a specific ITAAC for which the licensee has not yet submitted the ITAAC closeout letter, and is material to the ITAAC acceptance criteria.  This type of finding could prevent the ITAAC from being closed out and therefore must be corrected and addressed in the licensee’s ITAAC closure letter.  An ITAAC-Related Construction finding may be related to a single ITAAC or a family of ITACC.

Licensee:  A person or entity authorized to conduct activities under a license (e.g., early site permit, construction permit, combined license, or limited work authorization) issued by the Commission.

Licensee-Identified:  For the purpose of this inspection manual chapter (IMC), licensee-identified findings are those findings that are not NRC-identified or self-revealing.  Most, but not all, licensee-identified findings are discovered through a licensee program or process.  Some examples of licensee programs or processes that will likely result in such findings are the identification and documentation of findings (e.g., procedural violations, procedure inadequacies, etc.) by craft workers and/or licensee/contractor supervision during routine construction activities, construction quality assurance activities, self-assessments, independent assessments, audits and surveillances.  Additional examples may include preoperational testing, start-up testing, hydrostatic testing, non-destructive testing, EP drills, and critiques conducted by or for the licensee.

Minor Violation:  A violation that is of such low significance that documentation in an NRC inspection report is not normally warranted.   Although minor violations must be corrected, they are not usually described in inspection reports.

Non-Cited Violation (NCV):  A method for dispositioning a Severity Level IV violation. Provided applicable criteria in the Enforcement Policy are met, such findings are documented as violations, but are not cited in notices of violation, which normally require written responses from licensees.  As discussed in IMC 2505, a prerequisite for issuing NCVs is that the licensee must have satisfactorily completed a Corrective Action Program (CAP) effectiveness review.

Notice of Nonconformance:   Written notices describing contractors' failures to meet commitments which have not been made legally binding requirements by NRC. An example is a commitment made in a procurement contract with a licensee as required by 10 CFR Part 50, Appendix B.  A Notice of Nonconformance requests that non-licensees provide written explanations or statements describing corrective steps (taken or planned), the results achieved, the dates when corrective actions will be completed, and measures taken to preclude recurrence.

Notice of Deviation:  A licensee's failure to satisfy a written commitment, such as a commitment to conform to the provisions of applicable codes, standards, guides, or accepted industry practices when the commitment, code, standard, guide, or practice involved has not been made a requirement by the Commission.

Notice of Violation (NOV):  A formal, written citation in accordance with 10 CFR 2.201 that sets forth one or more violations of a regulatory requirement.

NRC-Identified:  For the purposes of this manual chapter, NRC-Identified findings are those that are found by NRC inspectors that the licensee was not previously aware of or had not been previously documented in the licensee’s corrective action program.  NRC-identified findings also include previously documented licensee findings to which the inspector has significantly added value.  Added value means that the inspector has identified a previously unknown significant weakness in the licensee’s classification, evaluation, or corrective actions associated with the licensee’s correction of a finding.

NRC Record:  Any written, electronic, or photographic record under legal NRC control that documents the policy or activities of the NRC or an NRC licensee (see also the definition in 10 CFR Part 9).

Observation:  As used in this manual chapter, a factual detail noted during a power reactor construction inspection.  Observations not directly related to a finding may only be documented if allowed by an appendix to this manual chapter or by a specific inspection procedure or temporary instruction.

Pre-operational Testing:  For the purposes of this manual chapter, Pre-operational Testing includes the testing categories normally identified as construction tests (e.g. activities such as chemical cleaning, flushing, continuity testing, piping and valve testing, calibration of instrumentation) and pre-operational tests to demonstrate SSC function and conformance to design requirements.

Quality Assurance:  Quality Assurance (QA) comprises all those planned and systematic actions necessary to provide adequate confidence that a structure, system or component will perform satisfactorily in service.  QA includes quality control.

Regulatory Commitment:  An explicit statement of “intent” or “agreement” to take a specific action agreed to or volunteered by a licensee, where the statement has been submitted in writing on the docket to the NRC.  This may include a commitment in the licensee’s application, a response to a Notice of Violation, etc.

Requirement:  A legally binding obligation such as a statute, regulation, license condition, technical specification, or an order.

Safety-Conscious Work Environment (SCWE):  An environment in which employees feel free to raise safety-significant construction quality concerns, both to their management and to the NRC, without fear of retaliation and where such concerns are promptly reviewed, given the proper priority based on their potential safety significance, and appropriately resolved with timely feedback to employees.

Safety Culture (as it applies in the new reactor construction environment):  That assembly of characteristics and attitudes in organizations and individuals which establishes that, as an overriding priority, a nuclear plant is constructed as designed with a focus on quality.

Safety Culture Assessment: A comprehensive evaluation of the assembly of characteristics and attitudes related to all of the safety culture components.  Individuals performing the evaluation can be qualified through experience or formal training.  A licensee independent safety culture assessment is performed by qualified individuals that have no direct authority and have not been responsible for any of the areas being evaluated (for example, staff from another of the licensee’s facilities, or corporate staff who have no direct authority or direct responsibility for the areas being evaluated).  A licensee third-party safety culture assessment is performed by qualified individuals who are not members of the licensee’s organization or utility operators of the plant (licensee team liaison and support activities are not team membership).

Self-Revealing:  For the purposes of this manual chapter, self-revealing findings are those that become self-evident and require no active and deliberate observation by the licensee or NRC inspectors to determine whether a change in process or equipment capability or function has occurred.  Self-revealing findings become readily apparent to either NRC or licensee personnel through a readily detectable degradation in the material condition, capability, or functionality of equipment and require minimal analysis to detect.  Some examples of self-revealing findings include failure of equipment or instrumentation to operate properly during testing that was not related to the purpose of the test (e.g., inadequate foreign material controls cause the failure) and violation of radiography exclusion area requirements that are subsequently identified through an electronic dosimeter alarm.

Startup Testing:  The testing program conducted after the authorization to load fuel. It includes initial fuel loading and pre-criticality tests, and continues until the plant reaches commercial operating status at or near its licensed power rating. The Startup Test Program includes low power, physics and power ascension testing.

Unresolved Item (URI):  An issue of concern about which more information is required to determine if a violation exists or if a violation is greater-than-minor. Such a matter may require additional information from the licensee or cannot be resolved without additional guidance or clarification/interpretation of the existing guidance.

Vendor:  Any company or organization that provides products such as material, equipment, components, or services to be used in an NRC-licensed facility or activity.  In certain cases the vendor may be an NRC licensee (e.g., a nuclear fuel fabricator) or the product may have NRC certificates (e.g., a transportation cask).

Violation:  The failure to comply with any portion of a regulatory requirement, such as a statute, regulation, order, license condition, or technical specification.

# 0613-04	RESPONSIBILITIES AND AUTHORITIES

## 04.01	General Responsibilities. NRC inspection results associated with new reactor construction shall be screened and documented in accordance with the guidance provided in this inspection manual chapter.  NRC inspection results associated with vendor inspections and quality assurance inspections led by NRC Headquarters related to new reactor construction shall follow the guidance provided in IMC 0617.

## 04.02	Inspectors.

a.	All power reactor construction inspectors have the primary responsibility for ensuring that their inspection activities and findings are accurately reported and documented in CIPIMS for the areas they inspected; that referenced material is correctly identified; and that the scope and depth of findings are adequately supported by documented examples.

b.	All power reactor construction inspectors are responsible for ensuring that the content of inspection reports does not conflict with information presented at exit meetings.  When inspection report contents differ significantly from the information presented at an exit meeting, the inspector (or the report reviewer) shall discuss those differences with the licensee before the report is issued.  All such discussions with the licensee shall be documented in a summary statement in the inspection report.

## 04.03	Deputy Regional Administrator for Construction. The Deputy Regional Administrator for Construction shall determine the appropriate level of management responsible to review and approve power reactor construction inspection reports.

## 04.04	Regional Branch Chiefs and Division Directors.

a.	The management reviewer shall ensure that inspection observations and findings are consistent with NRC policies and technical requirements, and ensure that violations are addressed in accordance with the NRC Enforcement Policy and the NRC Enforcement Manual.

b.	The applicable management reviewer is responsible for inspection report content, tone, regulatory focus, and issuance timeliness.

c.	The management reviewer responsible for the associated project shall approve final inspection reports.  Reports containing potential escalated enforcement should be approved at least one management level above the Branch Chief.

## 04.05	Division of Construction Inspection and Operational Programs (DCIP), Office of New Reactors (NRO).

a.	The NRO Branch responsible for inspection program development will provide interpretations of the information contained in this manual chapter, for answering questions related to the guidance, and for providing guidance for situations not covered in this manual chapter.

b.	The NRO branch responsible for inspection program development will process feedback and comments associated with this manual chapter.

# 0613-05	SCREENING INSPECTION RESULTS

The evaluation of 10 CFR Part 52 power reactor construction inspection results begins with a screening to determine if a construction issue will be documented for consideration in the periodic assessment of construction inspection program results.  The process for screening construction issues is described in the following sections.  Detailed instructions are provided in Appendix B of this Chapter.

## 05.01	Screen for a Violation of Regulatory Requirements. The evaluation of a construction issue begins with a screening to determine if it is a violation of regulatory requirements. Use Section 1-1 of Appendix B to screen construction issues.  For issues with multiple examples, each example should be screened separately.  Deviations from licensee commitments and contractor Nonconformances with commitments related to 10 CFR Part 50, Appendix B should also be screened separately.

If the construction issue is determined not to be a violation, the issue is not normally documented and the licensee is informed.  Since observations are not findings, they will not be considered in the construction inspection program (CIP) assessment process, and in most cases will not be documented.  See Section 0613-07 for exceptions for documenting observations.  If the construction issue is determined to be a violation, then proceed to Section 05.02.

If additional information is needed to determine if the construction issue is a violation, then the issue is an unresolved item (URI) and should be documented in accordance with Section 0613-10.  URIs should be used infrequently as they are only for issues that cannot be finalized during the inspection and are likely to result in a violation.

## 05.02	Screen for Enforcement Categories. This screen is used to determine if a violation warrants consideration of enforcement action using severity levels and possible civil penalties by virtue of being in one of the following categories:  had potential or actual safety consequences; had the potential to impact the NRC’s ability to perform its regulatory function; or involved willful aspects.  Screen the violation using Section 1-2 of Appendix B.

If the violation is involved with one of these categories, it is a finding.  Proceed to Section 05.04 to screen for identification credit.

If the violation is not involved with one of these categories, then continue to Section 05.03 to screen for greater-than minor significance.

## 05.03	Screen for Greater-than-Minor Significance. A violation must be greater-than minor to be considered a finding.  For construction issues, examples of minor violations are provided in Appendix E to this chapter.  Examples of minor violations are also provided in the Enforcement Manual.  If the violation is similar to a minor example, then the violation is minor.  If the violation is not similar to the “minor” description, then the “screen for greater-than-minor” questions in Appendix B, Section 1-3, must be used to determine if the violation is greater-than-minor and, therefore, a finding that warrants documentation.

If the violation is minor, it is not a finding, will not be considered in the CIP assessment process, and, in most cases, will not be documented.  See Section 0613-11 for the exceptions to documenting minor issues.

## Screen for Identification Credit.  Findings must be analyzed using the screening criteria listed in Appendix B, Section 1-4, to determine the appropriate identification credit for the finding (i.e., NRC-identified, licensee-identified, or self-revealing).

Licensee-identified and self-revealing findings that do not meet the screening criteria in Appendix B, Section 1-4, will not be considered in the CIP assessment process.  These findings will be documented in accordance with Section 0613-09.  Proceed to Section 05.06.b to determine the appropriate enforcement action for the finding.

NRC-identified findings and findings that meet the screening criteria specified in Appendix B, Section 1-4, are subject to enforcement action and are considered in the CIP assessment process.  These findings will be documented in accordance with Section 0613-08.  Proceed to Section 05.05 to analyze for construction safety focus component aspects.

## 05.05	Analyze for Construction Safety Focus Component (CSFC) Aspects. All NRC-identified, all self-revealing, and licensee-identified findings that meet the screening criteria specified in Appendix B, Section 1-4, shall be assessed for potential construction safety focus component aspects.

Assess the cause(s) of the finding to identify a potential construction safety focus component aspect using the guidance and questions in Appendix B, Section 1-5.  The construction safety focus component aspect of a finding is not considered a separate finding but rather a performance characteristic that is the most significant contributor to the finding, if applicable.  The intent of identifying the construction safety focus component aspect of a finding is so that insight can be used in the assessment process.  It should be noted that not all findings have a construction safety focus component aspect associated with them.

Once the issue is screened for construction safety focus component aspects, proceed to Section 05.06 to screen for the type of finding and the appropriate enforcement action.

## 05.06	Screening for Type of Finding and Applicable Enforcement Action. All NRC-identified findings and self-revealing and licensee-identified findings that meet the screening criteria specified in Appendix B, Section 1-4, must be analyzed using the screening criteria listed in Appendix B, Section 1-6, to determine the type of finding (i.e., Construction Finding, ITAAC-Related Construction Finding, or ITAAC Finding).

All findings must be analyzed using the screening criteria listed in Appendix B, Section 1-7, to determine the appropriate enforcement action.  If the finding is Severity Level IV, then the issue must be evaluated to determine if it should be cited or non-cited in accordance with the NRC Enforcement Policy.  In order to designate a finding as a non-cited violation (NCV), the effectiveness of the licensee’s CAP must have been verified through NRC inspection in accordance with IP 35007 “QA Program Implementation During Construction,” Appendix 16.  Document NRC-identified findings in accordance with Section 0613-08.  Document licensee-identified and self-revealing findings that do not meet the screening criteria specified in Appendix B, Section 1-4, in accordance with Section 0613-09.

If the finding is potentially greater than Severity Level IV, then the finding is an apparent violation (AV).  The appropriate enforcement action will be determined in accordance with the NRC Enforcement Policy.  Document the finding in accordance with Section 0613-08.

# 0613-06	DOCUMENTING INSPECTION RESULTS

To support the CIP, a computer based application called the Construction Inspection Program Information Management System (CIPIMS) has been developed.  CIPIMS is a tool that collects, organizes, manages, and generates reports on information pertaining to (1) ITAAC description, status, and closeout process (2) inspection findings, (3) inspection report generation, and (4) assessment information.

Report numbers for all inspections will be assigned as the planned inspections are entered into the Inspection Planning (IP) module of the Reactor Programs System (RPS).  Instructions for entering data into RPS are contained in IMC-0306, “Information Technology Support for the Reactor Oversight Process.”

Inspectors will enter inspection results into CIPIMS under a specific docket number and inspection report number that are associated with the facility being inspected and the inspection report period.  Each separate inspection result entry into CIPIMS is designated as an inspection item and will be assigned a sequential number.  Inspection activities that result in a violation and are greater-than-minor will be designated as a “Finding.”  Inspection items for which it is unknown whether or not a violation occurred will be designated as an “Unresolved Item.”  Further information on the use of CIPIMS is available in the “Construction Inspection Program Information Management System (CIPIMS) User’s Guide,” and in Appendix G.  Sample inspection report cover letters and a sample inspection report are located on the NRO Construction Inspection Program  Web site.

# 0613-07	DOCUMENTING INSPECTION RESULTS WITH NO FINDINGS AND DOCUMENTING OBSERVATIONS

Documentation of inspection results for which there is no associated finding in CIPIMS requires four sections to be completed:  title, scope, summary, and documents reviewed.  Follow the guidance in the appropriate sub-sections in Section 0613-08 on how to document these areas.  In the findings section include the statement “No findings of significance were identified.”  The discussion of the observation, if warranted, should follow this sentence.

Observations not directly related to a finding may be documented if allowed by an appendix to this manual chapter or by a specific inspection procedure or temporary instruction.  Otherwise, if an observation has no NRC regulatory significance, the observation is not documented in the inspection report, is not discussed in the NRC inspection exit meeting, and is not considered in the periodic assessment of construction performance.  Observations should be entered into CIPIMS as noted above only if there is a compelling reason to include the observation.  It is expected that the documentation of observations occurs only infrequently.

# 0613-08	DOCUMENTING NRC-IDENTIFIED, SELF-REVEALING, AND LICENSEE-IDENTIFIED FINDINGS THAT MEET THE SCREENING CRITERIA SPECIFIED IN APPENDIX B, SECTION 1-4

Documentation of findings in CIPIMS requires five sections to be completed: title, scope, summary, findings, and documents reviewed.  In the findings section of CIPIMS, a three-part format is used to document findings: description, analysis, and enforcement.  The sample inspection report provides examples on how to apply the principles described in the sections below.

## 08.01	Title. The finding title should concisely describe the focus of the inspection.

## 08.02	Scope. The scope identifies the areas of focus for the inspection and how the inspector(s) examined these areas (document review, visual verification, associated ITAAC or ITAAC family, etc.).  Sufficient detail should be provided so that a knowledgeable person could understand exactly what was inspected.  A complete and accurate description is important so that when the construction inspection program concludes, the NRC can demonstrate that all required inspection areas were completed.  The results of the inspection should not be included in the scope.

## 08.03 	Summary. The summary section of the construction issue is used to briefly document the overall conclusions reached during the inspection.  These conclusions should include a brief synopsis of what type of finding was identified and what regulatory requirement was not met.  Note- the summary section write-up will not show up in the body of the inspection report but will be used by CIPIMS to generate the Summary of Findings portion of the inspection report.

## 08.04	Findings. The findings section is used to document the following:

•	Construction Findings

•	ITAAC-Related Construction Findings

•	ITAAC Findings

The findings text will be further divided into the following subsections: Description, Analysis, and Enforcement.

### a.	Description.  This section provides the details, facts and supporting information associated with the finding.  There should be sufficient detail for the reader to understand the issue.  The level of detail should reflect the actual or potential safety consequence associated with the finding.  Significant or potentially significant findings may merit more discussion.

If a finding is likely to have generic construction or design concerns, then include specific details to identify the item of concern.  Describe the generic aspect in sufficient detail commensurate with the significance for the reader to understand the issue or event, evaluation of significance and construction safety focus component aspect and enforcement conclusions.  Findings with generic concerns should include specific details to identify the item of concern.

### b.	Analysis.  The Analysis section describes the nature of the finding and should provide sufficient detail in discussing the logic used by the inspector in screening an issue.  Include a description of any positive or negative licensee performance that either mitigated or exacerbated a potential problem and influenced the significance of the finding.  Discuss licensee corrective actions, as applicable

Describe the logic used to determine the violation, the bases for greater-than-minor, the severity level of the violation (except for apparent violations), and applicability of the construction safety focus component aspects.  The level of detail must allow a knowledgeable reader to reconstruct the decision logic used to arrive at the final conclusion.

1.	The first part shall include the following attributes:

•	A concise restatement of the violation (i.e., the issue of concern that resulted from the requirement not met);

•	The enforcement screening category (Section 05.02) that was met, if applicable; and

•	The specific circumstances for a “greater-than-minor” determination.

2.	The second part should include the specific basis for the determination of the significance (severity level) of the finding so the reader can independently arrive at the same conclusion.  The second part of the analysis section should describe the logic for determining the severity level, including reference to the Enforcement Policy supplement, as applicable.

3.	The third part of the analysis section should include the basis for assigning, or not assigning, the construction safety focus component aspect, if applicable.  Specifically:

•	If the finding has a construction safety focus component aspect, inspectors shall specify which construction safety focus component was selected and briefly state the construction safety focus component aspect.  Additional information is necessary to explain how the selected construction safety focus component aspect is applicable to the specific circumstances of the finding.  The inspectors shall also include the corresponding alphanumeric identifier (paragraph number, e.g. A.3(a)) from Appendix F for the construction safety focus component aspect;

•	If it was determined the finding does not have a construction safety focus component aspect, the analysis section must include a statement briefly stating the reason for not assigning a construction safety focus component aspect; and

•	If the licensee provides new information after the inspection report is issued, this information will be assessed to determine if a change in the original construction safety focus component aspect of the finding is appropriate.

### c.	Enforcement.  Describe the applicable enforcement action for the finding.   Findings found or reviewed during inspections are documented in accordance with the NRC Enforcement Policy and the guidance provided below.  The enforcement discussion and subsequent enforcement action must be consistent with the significance determination.

Do not speculate or reach conclusions about the intent behind a finding.  Conclusions about the willfulness of a violation are agency decisions, and are normally not made until after the Office of Investigations (OI) has completed an investigation.  A premature or inaccurate discussion of the willfulness of a violation in the inspection report could result in later conflicts based on additional input and review.  Inspection reports that include potentially willful violations or containing material that may be related to an ongoing investigation must be reviewed by OI and the Office of Enforcement (OE) prior to issuance.

In addition, 10 CFR Part 50, Appendix B, Criterion XVI, violations for failure to preclude repetition can only be written for significant conditions adverse to quality (SCAQ).  The inspection report details must clearly explain the basis for determining the previous condition was a SCAQ (e.g., the condition meets the definition of a SCAQ per the licensee's corrective action program or a construction deficiency per 10 CFR part 50.55(e)), the relationship between the previous SCAQ and the current one, and the corrective actions from the previous SCAQ that failed to prevent recurrence.

Document the enforcement aspect of the finding as described below:

•	What requirement was violated;

•	When the violation occurred and how long it existed;

•	Any actual or potential safety consequence (if not described earlier);

•	Immediate corrective actions taken to restore compliance (if not described earlier);

•	A reference to the licensee’s corrective action document number;

•	Specific enforcement actions (except for apparent violations); and

•	Tracking number resulting from the violation (e.g., NCV, NOV, or AV Tracking Number).

For Severity Level IV violations that meet NCV criteria, state:

“Because this violation was of very low safety significance, was not repetitive or willful, and was entered into the licensee’s corrective action program, this violation is being treated as an NCV (insert the tracking number here), consistent with the NRC Enforcement Policy.”

For an NOV, the specific enforcement action should state:

“Because the [licensee failed to (correct the violation, enter the condition into the corrective action program, prevent recurrence)] or [licensee’s corrective action program had not yet been demonstrated to be effectively implemented] this violation is being treated as an NOV, consistent with the NRC Enforcement Policy.”   In addition, see the Enforcement Manual for guidance on developing the notice and cover letter.

For a finding with a violation in which enforcement discretion is applied and for apparent violations, work with the Office of Enforcement through the Regional Enforcement Coordinator to develop appropriate wording for the Enforcement section.  See the Enforcement Manual for standard paragraphs to be included and additional guidance on apparent violations.

## 08.05	Documents Reviewed. The Documents Reviewed area in CIPIMS allows an inspector to provide a list of documents that were inspected.  The entries in this area will be consolidated by CIPIMS when an inspection report is generated to produce the List of Documents Reviewed attachment.  The inspector has the discretion on how many and which documents to include.  The intent of the List of Documents Reviewed attachment is to provide sufficient detail of those documents specifically required to support a finding.  The intent is not to document every record or document an inspector reviewed, but rather to document only those that were reviewed in detail and are essential in supporting a conclusion on the adequacy of licensee work, including supporting a finding.

# 0613-09	DOCUMENTING SELF-REVEALING AND LICENSEE-IDENTIFIED FINDINGS THAT DO NOT MEET THE SCREENING CRITERIA SPECIFIED IN APPENDIX B, SECTION 1-4

NRC policy requires that all documented violations be dispositioned in accordance with the Enforcement Policy, regardless of who identified them.  However, licensee-identified findings and self-revealing findings that do not meet the screening criteria specified in Appendix B, Section 1-4 and are incorporated into the licensee’s corrective action program should have minimal documentation.  See Section 0613-03 for definitions of licensee-identified and self-revealing findings.

If the licensee-identified or self-revealing finding is a violation of very low safety significance (Severity Level IV) and the licensee has correctly evaluated the finding and has developed appropriate corrective actions, then briefly describe the violation.  Include the requirement(s) violated, describe how it was violated, identify the licensee’s corrective action tracking number(s), and provide a very brief justification why the violation is of very low safety significance.

Licensee-identified and self-revealing findings that do not meet the criteria of Appendix B, Section 1-4, shall be screened in accordance with Appendix B, Section 1-7, to determine if they meet the non-cited violation (NCV) criteria.  If the finding meets the non-cited violation criteria, the following introductory paragraph must be included:  “The following Severity Level IV violation(s) was/were identified by the licensee (or were self-revealing) and are violations of NRC requirements which meet the criteria of the NRC Enforcement Policy, for being dispositioned as a Non-Cited Violation.”

If the finding does not meet the NCV criteria, document the finding in accordance with Section 0613-08.

NOTE: In accordance with the Enforcement Policy, the approval of the Director, Office of Enforcement, with consultation with the Deputy Executive Director as warranted, is required for dispositioning willful violations as NCVs.

# 0613-10	DOCUMENTING UNRESOLVED ITEMS (URIs)

## 10.01 Opening URIs. Open a URI when an issue requires additional information from the licensee or cannot be resolved without additional guidance or clarification/interpretation of the existing guidance.  The action of documenting an URI is a commitment of future resources, and shall not be opened to track completion of licensee’s actions associated with a finding or an inspection question.

Documenting URIs requires four sections to be completed in CIPIMS: title, scope, findings, and documents reviewed.  Because URIs are not findings, the summary section is not required.  The findings section should describe the issue with sufficient detail to allow another inspector to complete the inspection effort, if necessary.  The report must clearly identify the specific licensee or NRC actions needed to resolve the issue.  The URI should be assigned a tracking number the same as a finding but with a URI designator in the front.  Unresolved items are not documented in the inspection report cover letter.

## 10.02   Closing URIs. The level of detail devoted to closing URIs depends on the nature and significance of the additional information identified.  The closure of an URI must summarize the topic, summarize the inspector's follow-up actions, evaluate the adequacy of any licensee actions, determine if a violation has occurred, and provide enough detail to justify closing the item.  If resolution to an URI was based on discussions between inspector(s) and NRO technical staff(s), concisely document the details of these discussions as the basis for the regulatory decision. Additionally, branch chiefs of inspector(s) and technical staff(s) who were involved in these discussions should concur on the inspection report.

If a finding is identified, follow the guidance described in Section 0613-08.  If no findings were identified, follow the guidance in Section 0613-07.  If a minor violation is identified, document it in accordance with Section 0613-11.

# 0613-11	DOCUMENTING MINOR VIOLATIONS

## 11.01	Minor Violations. Minor violations are not routinely documented in inspection reports.  However, as stated in the Enforcement Policy/Manual, there may be exceptions.  Documenting a minor violation may be warranted as part of closing out a Construction Deficiency Report (CDR), Unresolved Item, or follow-up to an allegation. Licensees are required to correct minor violations.  If it is necessary to document a minor violation, then only minimal discussion is required.  Documentation of minor violations requires three sections to be completed in CIPIMS: title, scope, and findings.  Complete the title and scope as described above.  In the findings section, briefly describe the issue of concern, state that the issue has been addressed by the licensee and include the following:

AThis failure to comply with {requirement} constitutes a violation of minor significance that is not subject to enforcement action in accordance with the NRC=s Enforcement Policy.@

Do not use the Description, Analysis, or Enforcement sub sections when documenting minor violations.

# 0613-12	DOCUMENTING FINDINGS ASSOCIATED WITH CONSTRUCTION DEFICIENCY REPORTS (10 CFR PART 50.55(e))

## 12.01	Closure of CDRs. Document reviews and closures of CDRs, including revisions to CDRs, in the inspection report under Part III, Other Inspection Results.  In general, CDR reviews should have a brief description of the event and reference the docketed CDR.  If a CDR review is already documented in a separate NRC correspondence, then close the CDR with a brief statement in an inspection report referencing the separate correspondence.

The event described in the CDR needs to be evaluated for a potential violation and  must be identified clearly in the inspection report as a cited violation, non-cited violation, or as a minor violation, as appropriate, or warranting enforcement discretion.  Screen any violations in accordance with Section 0613-05.  In addition to the information described above, document closure of the CDR as follows:

a.	No violations:  state the CDR was reviewed and that no findings of significance were identified.

b.	Minor Violations.  Use guidance in Section 0613-11.

c.	NRC-Identified or licensee-identified/self-revealed violations that meet the screening criteria of Appendix B, Section 1-4: The safety significance and enforcement should be discussed per Section 0613-08 of this manual chapter and not in the CDR closeout section.  A statement, such as “The enforcement aspects of this finding are discussed in Part II of this report,” should be included in the CDR closeout section.

d.	Licensee-identified/self-revealed violations that do not meet the screening criteria of Appendix B, Section 1-4:  The safety significance and enforcement should be discussed per Section 0613-09 of this manual chapter and not in the CDR closeout section.  A statement, such as “The enforcement aspects of this finding are discussed in Part II of this report,” should be included in the CDR closeout section.

## 12.02 Closure of Cited Violations. Document the closure of cited violations in Part III.  The level of detail required to document closure of cited violations depends on the extent of corrective actions conducted by the licensee.  In general, the write-up must summarize the inspector's follow-up actions which evaluated the adequacy of any licensee actions and provide enough detail to justify closing the violation.

# 0613-13	OTHER GUIDANCE

## 13.01	Treatment of Third Party Reviews. Detailed NRC reviews of Institute of Nuclear Power Operations (INPO) evaluations, accreditation reports, findings, recommendations, and corrective actions, or other third party reviews with similar information are not referenced in NRC inspection reports, tracking tools, or other agency documents unless the issue is of such safety significance that no other reasonable alternative is acceptable.  INPO findings, recommendations and associated licensee corrective actions are not normally tracked by the NRC.  If a finding warrants tracking, it should be independently evaluated, documented, and tracked as an NRC finding in Part II of the report.

INPO findings, recommendations, corrective actions, and operating experience which are placed in the licensee’s corrective action program, can be considered appropriate for inspection.  Additionally, when documenting review of these issues which originated from INPO, inspection reports should not refer to any proprietary INPO reports or documents, INPO reference numbers, or identify specific sites when referencing operating experience.  If it is necessary to document review of an INPO document (i.e., an evaluation referring to the INPO document was an inspection sample or justification for a construction safety focus component aspect), then state the reference number of the reviewed item (e.g., condition report or evaluation number) and provide general words for the title, if applicable (e.g., “Condition Report No. 235235 concerning industry information on pumps”).

Include a short statement in the inspection report to document that a review of a specified INPO evaluation or accreditation report was completed, if applicable.  Do not include a recounting or listing of INPO findings or reference a final INPO rating when documenting an INPO evaluation or accreditation report review.  Discuss the specifics of any significant differences between NRC and INPO perceptions with regional management.

## 13.02	Non-Routine Inspections. Document inspection activities related to Expanded Inspections in accordance with Appendix C.  Document in Part III inspection results from temporary instructions (TIs) and other non-routine inspection activities (generic communication closure, etc.) not addressed in this manual chapter.  In some cases, factual observations may have to be documented.  If it is necessary to document an observation or a minor violation, follow the guidance in Section 0613-07 or Section 0613-11 respectively.

## 13.03	Documenting Backfit Items. When a backfit is identified, it is necessary to track the completion of the licensee's actions to correct the identified condition.  Document this tracking in Part III and classify the backfit item as a violation.  When inputting into CIPIMS, enter the following:

“This issue is a compliance backfit.  By definition, the licensee was put on notice that they are in violation.  This item was created to ensure appropriate NRC inspection of the licensee's corrective actions required to ensure compliance - similar to follow-up from an NOV.”

# 0613-14	COMPILING AN INSPECTION REPORT

Each inspection report will have a cover letter, cover page, summary of findings, report details, and attachments as described in this section.  A table of contents is optional.  Once CIPIMS is fully deployed, it is expected that inspection reports in the required format will be generated by CIPIMS.  The following additional guidance applies:

•	Expanded inspection results must also reflect the additional guidance provided in Appendix C;

•	IP 35007, “Part 52, Identification and Resolution of Construction Problems,” results have varying thresholds for documentation and must reflect the guidance provided in Appendix D;

•	Escalated enforcement actions and cited violations must reflect the guidance found in the Enforcement Manual, Appendix B, “Standard Formats for Enforcement Packages”; and

•	Issues which are subject to enforcement discretion must reflect the guidance found in the Enforcement Manual.

## 14.01	Cover Letter. The purpose of the cover letter is to transmit the inspection report results.  Inspection reports are transmitted using a cover letter from the applicable NRC official to the designated licensee executive.  Appendix B of the Enforcement Manual contains sample cover letters for inspection reports containing enforcement actions (violations, apparent violations, deviations, non-conformances, etc.).  Cover letter content varies somewhat depending on whether the inspection identified significant findings.  In general, every cover letter has the same basic structure, as follows:

a.	Date, Addressee, and Salutation.  At the top of the first page, the cover letter begins with the NRC seal and address, followed by the date on which the cover letter is signed and the report issued.  The name and title of the principal addressee are placed at least four lines below the letterhead, followed by the licensee’s name and address.  Note that the salutation is placed after the subject line.

For cover letters transmitting reports with findings assigned an enforcement action (EA) number, the EA number should be placed in the upper left-hand corner above the principal addressee’s name.

b. 	Subject Line.  The subject line of the letter should state the facility name (if it is not apparent from the Addressee line) and the inspection subject.  The words “NOTICE OF VIOLATION” should be included if such a notice accompanies the inspection report.  The entire subject line should be capitalized.

c.	Introductory Paragraph. The first two paragraphs of the cover letter should give a brief introduction, including the type of inspection report.

d. 	Body of the Letter.  In keeping with the need to communicate in “Plain English”, the body of the letter should discuss the most important topics first.

The cover letter is written to transmit the inspection report to the licensee’s management, and to deliver the “big picture” message regarding the inspection.  Because it is the highest-level document, it does not need to (and normally won’t) detail all of the items inspected and the inspection procedures used.  It will note the areas covered by the inspection.

In general, the body of the cover letter should focus on clearly communicating a few main points (or a single point) that are well-supported by the report details, rather than attempting to deliver a large number of points or extensive detail.  If no significant issues were raised by the inspection, this section should briefly summarize the scope of specific inspection activities performed to give perspective to the conclusion that no deficiencies or significant issues were identified.

e.	Closing.  The final paragraph consists of standard legal language that varies depending on whether enforcement action is involved.

The final paragraph consists of a statement regarding the public availability of the inspection report and associated correspondence.  The signature of the appropriate NRC official is followed by the list of enclosures and distribution.

## 14.02	Notice of Violation. Licensees are officially notified that they have failed to meet regulatory requirements when NRC issues a Notice of Violation (NOV).  NOVs may be sent to licensees as part of a package of documents which also includes a cover letter and associated inspection report.  NOVs may be sent with a cover letter which refers to an inspection report that was distributed previously.  An NOV should not be sent to the licensee in advance of the inspection report.

Every NOV must be clear, so that there is little doubt that the licensee (or other interested reader) can understand the basis for the violation.  The licensee may not agree with the basis, but they must understand the NRC position.

Every NOV must clearly state what the requirement was that was not met.  That may mean that the date and revision number of the applicable document will need to be provided.  Then a clear statement of what happened (including when, if timing is important) will be provided.  The intent is that any interested reader will be able to clearly see and understand what the requirement was and how it was not met.  For additional guidance on documenting violations, refer to the NRC Enforcement Manual.  The NOV should be an enclosure to the cover letter.

## 14.03	Cover Page. The inspection report cover page will be generated from CIPIMS based on information provided via a pop-up window at the time the report is generated and provides a quick-glance summary of inspection information.  It contains the docket number, license number, report number, licensee, facility, location, dates of inspection, the names and titles of participating inspection team members, accompanying individuals, and the name, and title of the approving NRC official.

## 14.04	Table of Contents. If a report is considered complicated or of significant length, then use of a table of contents is encouraged but not required.  If the inspection report, from the Report Details section to the exit interview section, is more than 20 pages long, a table of contents should be considered.

## 14.05	Inspection Report Content. The detailed content of the body of the inspection report is discussed in the following sections.  Parts I through III will be automatically generated by CIPIMS for the designated inspection period.

a.	Summary of Findings [Part I of the Report].  The Summary of Findings section will automatically be generated by CIPIMS and will consist of identified findings.  If there are no findings the section will consist of the statement ‘No Findings of Significance’.  Information in this section includes:

•	Inspection Procedure and Title

•	Additional Procedure and Title

•	Finding Number (which is automatically assigned when the report is generated)

•	Finding Title

•	Summary Text

b.	Report Details [Part II of the Report].  The Report Details section will automatically be generated by CIPIMS and will consist of all inspection activities entered for the Inspection Report.  Information in this section includes:

•	EA Number (if applicable)

•	Finding/Inspection Item title

•	Family / ITAAC No. (if applicable)

•	Inspection Procedure and Title

•	Additional Procedure and Title

•	Scope text

•	Findings text (if applicable):

1.	The Findings section should be used to present, in a concise but narrative format, the findings identified by the inspection team members.  This should include a discussion of the policies and procedures governing the licensee’s programs for each area reviewed, a description of the inspection sample evaluated by the inspection team (e.g., portions of the  combined license (COL), test results, calculations, design packages, drawings, technical reports, etc.), and the results of the inspection evaluations conducted.  The inspector may choose to simply number issues sequentially, with appropriate subheadings, or may use another method of organizing the findings.

The Findings section is subdivided into three distinct sections:  Description, Analysis, and Enforcement.

If no findings were identified, the Findings section should not be subdivided as discussed above and should include the following statement:  “No significant findings were identified.”

2.	In those cases where a standard format is not readily applied, the most important subject should be identified first, followed by a discussion of major topics identified in descending order of significance.  Exceptions to the standard format include:

•	Expanded Inspection (EI) reports;

•	Augmented Inspection Team (AIT) reports;

•	Special Inspection Team (SIT) reports, and;

•	Other cases where the specifically directed focus of the inspection does not easily fit into the standardized report outline.

c.	Other Inspection Results [Part III of the Report].  The other inspection results section will be used to document the results of inspections, such as license-identified or self- revealing NCVs, closing URIs with no findings, closing CDRs etc.

d.	Exit Meeting Summary [Part IV of the Report].  The final section of each inspection report should include a brief summary of the exit meeting conducted in conjunction with the inspection.  This information will also be described in the first paragraph of the cover letter.  The exit meeting summary must also include the following information:

- Proprietary Information.  At the exit meeting, the inspectors will verify whether the licensee considers any materials provided to or reviewed by the inspectors to be proprietary. If the licensee did not identify any material as proprietary, include a sentence to that effect in the exit meeting summary.  Refer to IMC 0620 for actions to take if the report includes proprietary material.

NOTE: Inspectors should be aware of minimum requirements for handling classified and sensitive non-classified information.  When an inspection is likely to involve proprietary information (i.e., given the technical area or other considerations of inspection scope), handling of proprietary information should be discussed at the entrance meeting.

- Subsequent Contacts or Changes in NRC Position.  If the NRC position on an inspection finding changes after the exit meeting, conduct an additional exit meeting to discuss that change with the licensee.  Also, document the additional exit meeting in the inspection report.

- Characterization of Licensee Response.  Do not characterize a licensee’s exit meeting response.  If the licensee disagrees with an inspection finding, this position may be characterized by the licensee in its formal response to the inspection report, if applicable.

- Oral Statements and Regulatory Commitments.  Do not attempt to characterize or interpret any oral statements the licensee makes, at the exit meeting or at any other time during the inspection, as a commitment.   Licensee commitments are documented by licensee correspondence, after which they may be referenced in the inspection report.  Oral statements made or endorsed by a member of licensee management authorized to make commitments are not regulatory commitments unless they are documented as such by the licensee.  For further guidance on licensee commitments, see Agency-wide Documents Access and Management System (ADAMS) Accession Nos. ML003680088 (NEI 99-04), ML003680078 and ML003679799 (NEI Cover Letter and SECY 00-045 endorsing NEI 99-04 guidance).  Because regulatory commitments are a sensitive area, ensure that any reporting of licensee statements contain appropriate reference to the licensee’s document.

e.	Personnel Contacted.  The inspection report should include a list of the individuals who furnished relevant information or were key points of contact during the inspection (except in cases where there is a need to protect the identity of an individual).  The list should not be exhaustive but should identify those individuals who provided information related to developing and understanding findings.  The list includes the most senior licensee manager present at the exit meeting and NRC technical personnel who were involved in the inspection if they are not listed as inspectors on the cover page.

f.	List of Acronyms.  Consider including a list of acronyms for any report whose Details section exceeds 20 pages.  For reports in which a relatively small number of acronyms have been used, the list is optional.  The list is also optional if more than 20 pages and the number of acronyms are relatively small.  In all cases, however, acronyms should be spelled out when first used in inspection report text.

# 0613-15	ISSUING INSPECTION REPORTS

## 15.01	Report Issuance

a.	Periodicity of Issuing Reports during Construction and Testing. Post-COL or Limited Work Authorization (LWA) Issuance, but Pre-Fuel Load:  During the course of site construction activities, the responsible inspection organization should establish an appropriate periodicity (e.g., 30, 60, or 90 days) for integrated reports.

b.	Responsible Organization for Reports.  For each reactor docket, the assigned division director or designated branch chief shall be responsible for the report content, tone, conclusions, and overall regulatory focus for all inspection reports.  This responsibility includes resolution of discrepancies discovered during the review process, and the final “locking” of applicable CIPIMS entries by the entry of the ADAMS ML number for the report.

## 15.02	Report Timeliness

a.	General Timeliness Guidance

1.	CIPIMS entries should be completed, and reviewed by supervision within guidelines established by the appropriate Division of Construction Projects Branch Chief.

Note: Even without access to CIPIMS during inspections, inspectors can complete their inspection inputs in any word processing program available and later cut and paste the construction issue into CIPIMS.  CIPIMS will be available via Citrix.

2.	Inspection reports should be issued in a time frame no longer than the length of the report period but in no case later than 45 calendar days after inspection completion.  For example, if the report period is 30 days then the report should be issued within 30 days.  If the report period is 60 days then the report should be issued within 45 days.  Special inspection reports should be issued within 45 days and AIT reports should be issued within 30 days.

3.	Inspection reports covering potential escalated enforcement action should be accelerated, as necessary, and issued no later than 30 calendar days after inspection completion.  Consideration should be given to creating a separate report to document apparent violations.

Note: Inspection completion for team inspections is defined as the day of the exit meeting.  For integrated or resident inspection reports, inspection completion is defined as the last day covered by the inspection period.

b.	Expedited Reports Documenting Significant Impact on ITAAC.  Inspection reports covering ITAAC findings, especially during the final few months prior to the scheduled fuel load, should be considered for acceleration of timeliness goals.  In these cases, an expedited inspection report should be prepared that is limited in scope to the ITAAC finding(s) involved.

# 0613-16	RELEASE AND DISCLOSURE OF INSPECTION REPORTS AND ASSOCIATED DOCUMENTS

Except for report enclosures containing exempt information, all final inspection reports will be routinely disclosed to the public.  Exempt information includes, but is not limited to, the following:

•	Information meeting the requirements for withholding from public disclosure as specified in 10CFR 2.390 and 10 CFR 9.17

•	Information pertaining to ongoing allegations as discussed in Management Directive 8.8, “Management of Allegations”

•	Exempt information as described in IMC 0620, “Inspection Documents and Records”

•	Sensitive unclassified information (e.g., safeguards information, official use only, proprietary information)

•	Proprietary and Business Sensitive Information

END

APPENDIX A

Acronyms Used in IMC 0613

ADAMS	Agency-wide Documents Access and Management System

AIT		Augmented Inspection Team

AV		Apparent Violation

CAP		Corrective Action Program

CAQ		Condition Adverse to Quality

CCIB		Construction Inspection and Allegation Branch (of NRO DCIP)

CDR		Construction Deficiency Report

CFR		Code of Federal Regulations

CIP		Construction Inspection Program

CIPIMS	Construction Inspection Program Information Management System

COL		Combined License

COLA		Combined License Application

CSFC		Construction Safety Focus Component

CSFI		Construction Safety Focus Issue

DCIP		Division of Construction Inspection & Operational Programs

EA		Enforcement Action

ECR		Engineering Change Request

EI			Expanded Inspection

ESP		Early Site Permit

IMC		Inspection Manual Chapter

INPO		Institute of Nuclear Power Operations

IP			Inspection Procedure

ITAAC		Inspections, Tests, Analyses, and Acceptance Criteria

LWA		Limited Work Authorization

M&TE		Measuring and Test Equipment

NCV		Non-Cited Violation

NEI		Nuclear Energy Institute

NOV		Notice of Violation

NRC		Nuclear Regulatory Commission

NRO		Office of New Reactors

NRR		Office of Nuclear Reactor Regulation

OE		Office of Enforcement

OI			Office of Investigations

PDF		Portable Document Format

PI&R		Problem Identification and Resolution

QA		Quality Assurance

ROP		Regulatory Oversight Process

RPS		Reactor Program System

SCAQ		Significant Condition Adverse to Quality

SIT		Special Inspection Team

SSC		Structure, System or Component

SCWE		Safety Conscious Work Environment

TI			Temporary Instruction

URI		Unresolved Item

APPENDIX B

Issue Screening

Use the following instructions and Figure 1 to determine if (1) a construction issue has significance to warrant further analysis and/or documentation; (2) a finding has a construction safety focus component aspect; (3) the type of finding, and (4) if the violation should be cited or non-cited.

Section 1-1.	Screen for Violation of Regulatory Requirements

- Answer the following question to determine if the issue of concern is a violation:

Was the construction issue the result of the licensee’s failure to meet an NRC requirement?

- If additional information is needed to determine if the construction issue is a violation, then the issue is a URI.  Go to Section 0613-10 for documentation guidance.

- If the answer to the violation question is ANo,@ the construction issue is not normally documented.  Go to Section 0613-07 for documentation guidance.

- If the answer to the violation question is “Yes,” then the construction issue is a violation.  Go to Section 1-2 to screen for enforcement categories.

NOTE

Deviations and Nonconformances should be dispositioned in accordance with Section 2.2 of the NRC Enforcement Manual.

Section 1-2.	Screen for Enforcement Categories

The inspector is expected to refer to the Enforcement Policy/Manual for guidance on addressing the following questions:

- Does the issue have actual or potential safety consequence (e.g., overexposure, credible scenarios with potentially significant actual consequences)?

- Does the issue have the potential for impacting the NRC’s ability to perform its regulatory function? For example, a failure to provide complete and accurate information or failure to receive NRC approval for a change in licensee activity, etc.

- Has the Office of Investigations determined that there were willful aspects of the violation?

If the answer to any of the enforcement category questions is AYes,@ then the construction issue is a finding.  Go to Section 1-4 of this appendix to screen for identification credit.

If the answer to all of the enforcement category questions is ANo,@ then continue to Section 1-3.

Section 1-3.	Screen for Greater-Than-Minor

Determine whether the violation is greater-than-minor.  If the answer to any of the following questions is “YES,” the violation is greater-than-minor. If the answer to all four questions is “NO,” the violation is not greater-than-minor.

The violation:

1.	Is the issue similar to the “not minor if” statement of an example in Appendix E?

2.	Does the issue, if left uncorrected, represent a condition adverse to quality that renders the quality of a structure, system, or component (SSC) or activity, unacceptable or indeterminate, AND the issue is associated with any one or more of the following?

A.	A deficiency in the design, manufacture, construction, installation, inspection, or testing of a SSC, which required one of the following to establish the adequacy of the SSC to perform its intended safety function: (i) detailed engineering justification; (ii) redesign; (iii) replacement; (iv) supplemental examination, inspection, or test; (v) substantial rework; or (vi) repair

B.	A non-conservative error in a computer program, design specification, construction specification, design report, drawing, calculation, or other design output document that defines the technical requirements for the SSC

C.	An irretrievable loss of a quality assurance record; or a record-keeping issue that could preclude the licensee from being able to take appropriate action on safety-significant matters, or from objectively or properly assessing, auditing, or otherwise evaluating safety-significant activities, or

D.	An unqualified process, procedure, tool, instrument or personnel used for a construction activity that either invalidated previously accepted activities, or required requalification

3.	Does the issue, if left uncorrected, represent a failure to establish, implement or maintain an adequate process, program, procedure, or quality oversight function that could render the quality of the construction activity unacceptable or indeterminate?

4.	If left uncorrected, could the issue adversely affect the closure of an Inspection, Test, Analyses, and Acceptance Criteria (ITAAC)?

NOTES

1) For these Questions, the associated work activity must have been reviewed by at least one level of applicant / licensee quality assurance, quality control, or other authorized personnel.

2) SSC: Any Structure, System, and Component, which is Safety-Related or has ITAAC requirements.

If the answer to all of the preceding questions is no, the violation is a minor violation.  The inspectors inform the licensee of the minor violation and the licensee dispositions the minor violation in accordance with its CAP.  If the licensee does not disposition the minor violation in accordance with its CAP, then the inspectors screen this as a new construction issue.  Normally, minor violations will not be documented.  See section 0613-11 for the exceptions to documenting minor violations.

If the answer to any of the preceding questions is yes, the violation is a greater-than-minor violation and is considered a finding.  Proceed to Section 1-4 to screen for identification credit.

Section 1-4.	Screen for Identification Credit

- NRC-identified findings are findings found by NRC inspectors, of which the licensee was not previously aware or had not been previously documented in the licensee’s corrective action program.  NRC-identified findings also include previously documented licensee findings to which the inspector has significantly added value.  Added value means that the inspector has identified a previously unknown weakness in the licensee’s classification, evaluation, or corrective actions associated with the licensee’s correction of a finding.

- Self-revealing findings are those findings that become self-evident and require no active and deliberate observation by the licensee or NRC inspectors to determine whether a change in process or equipment capability or function has occurred.  In most cases, the NRC will not take enforcement action for self-revealing issues.  However, the NRC will treat a self-revealing issue in the same manner as NRC-identified when one of the following criteria is met:

1.	Any of the conditions listed below for licensee-identified issues that result in NRC taking specific follow-up actions.

  - Inspections or tests that yield unexpected results that are outside the scope of the test.

  - Any issue that resulted from prior missed opportunities or is repetitive in nature due to inadequate corrective action.

  - Inadequately controlled construction activities that directly cause an event, such as fire which causes damage to safety-related SSCs, etc.

- Licensee-identified findings are those findings that are not NRC-identified or self-revealing.  Most, but not all, licensee-identified findings are discovered through a licensee program or process.  In most cases, the NRC will not take enforcement action for licensee-identified issues.  However, the NRC will treat a licensee-identified issue in the same manner as NRC-identified when one of the following criteria is met:

1.	Any issue that appears to meet the threshold for escalated enforcement action.

2.	Any issue that is related to potential harassment and intimidation or willfulness.

3. 	Any technical issue or environmental condition that yields unexpected results not previously observed by the licensee or the NRC such as a significant common cause factor.

4.	Any issue that invalidates the acceptance criteria of a previously closed ITAAC.

5.	An NRC inspector’s identification of a previously unknown significant weakness in a licensee’s classification, evaluation, or corrective action associated with the licensee’s correction of an issue.

- If the finding is licensee-identified or self-revealing and did not meet the screening criteria above, proceed to Section 1-7 to determine whether or not the finding should be cited.  Document the finding in accordance with Section 0613-09.

- If the finding is NRC-identified or is licensee-identified or self-revealing and meets the screening criteria above, proceed to Section 1-5 to screen for construction safety focus component aspects.  Document the finding in accordance with Section 0613-08.

Section 1-5.	Screen for Construction Safety Focus Component Aspect(s)

- Based on the information developed during the inspection, attempt to identify the most significant contributor that provides the most meaningful insight into what caused the finding to occur.  There should typically be only one principal cause and one construction safety focus component aspect associated with each finding.  However, on rare occasions it may be appropriate for some unique or complex inspection findings with multiple root causes to be associated with more than one construction safety focus component aspect.  In these cases, the regional office must obtain concurrence from the NRO Branch Chief responsible for developing and maintaining the construction inspection program.  For the case of a finding with multiple examples, consistent with the Enforcement Manual guidance, it is appropriate for the multiple examples to have the same construction safety focus component aspect.

- Answer the following question with respect to the most significant contributor of the finding to determine if it has a construction safety focus component aspect:

(NOTE:  Not all findings have construction safety focus component aspects.)

Is the most significant contributor of the finding similar to one of the construction safety focus component aspects described in Appendix F?

- Proceed to Section 1-6 to determine the type of finding that was identified.

Section 1-6.	Screen for Type of Finding

Determine whether the finding will be documented as a construction finding, an ITACC-related construction finding, or an ITAAC finding.

a.	If the finding is not associated with a specific ITAAC, then it should be documented as a construction finding.

b.	If the finding is associated with a specific ITAAC, determine whether the licensee has issued the ITAAC closure letter.

1. 	If the answer is no, then determine whether it is material to the ITAAC acceptance criteria.

(a)	If the answer is no, then it should be documented as a construction finding.

(b)	If the answer is yes, then it should be documented as an ITAAC-related construction finding.

2.	If the answer is yes, then determine whether it is material to the ITAAC acceptance criteria.

(a)	If the answer is no, then it should be documented as a construction finding.

(b)	If the answer is yes, then it should be documented as an ITAAC finding.

c.	NRC Response to Different Types of Findings.  NRC dispositions the finding in accordance with Figure 1, “Construction Findings Flowchart.”

1. 	If the issue is determined not to be related to a specific ITAAC, NRC will designate it as a construction finding, inform the licensee, and evaluate the deficiency via the Enforcement Policy.

2.	If the issue is determined to be an ITAAC-related construction finding, the staff will inform the licensee and evaluate the deficiency via the Enforcement Policy.

- If the issued is determined to be an ITAAC finding, the staff will inform the licensee and evaluate the deficiency via the traditional enforcement process.  Furthermore, the staff will evaluate the need to re-open other closed ITAACs, determine whether the NRC staff has accepted the licensee’s ITAAC closure letter, and, if not, how it will treat the invalid closeout letter.  If the staff has not yet accepted the letter, it may reject the closeout letter.

- Proceed to Section 1-7 to determine the significance of the finding and the appropriate enforcement action to be taken.

Section 1-7	Screening for Significance and Appropriate Enforcement Action

Refer to the guidance in Supplement 6.5 of the Enforcement Policy to determine the appropriate severity level for the violation.

If the significance of the finding is potentially greater than Severity Level IV, then the finding is an apparent violation.  The appropriate enforcement action will be determined in accordance with the Enforcement Policy.  Document the finding in accordance with Section 0613-08.

If the finding is Severity Level IV, determine if the finding is appropriate to be treated as a non-cited violation.  If the licensee’s CAP effectiveness has not been validated, all violations will be cited (see IMC 2505, Section 06.08 for more details).  If the CAP effectiveness has been validated, the inspector is expected to refer to the Enforcement Policy/Manual for guidance on addressing the following questions:

- Did the licensee fail to restore compliance within a reasonable time?

- Did the licensee fail to enter the violation into its corrective action program to address recurrence?

- Was the violation willful?

- Was the violation repetitive and NRC-identified?

If the answer to any of the above questions is “Yes”, the violation should be considered for a Notice of Violation.  Document these findings in accordance with Section 0613-08.

If the answer to all of the applicable questions is “No”, the violation may be dispositioned as a non-cited violation.  If the violation is licensee-identified or self-revealing and does not meet the criteria in Section 1-4, go to Section 0613-09 for documentation guidance.  If the violation is NRC-identified, go to Section 0613-08 for documentation guidance.

Construction

Issue

Licensee- Identified or Self-Revealing?

Minor Violation Doc Screening Met?

Greater-than-minor

Associated with Specific ITAAC?

Closeout Letter Issued?

Material to ITAAC Acceptance Criteria?

ITAAC

Finding

Has the NRC

Accepted ITAAC?

Closure?

NRC rejects

Closeout Letter

Treatment of Invalid Closeout Letter

Construction Finding

Material to ITAAC Acceptance Criteria?

Greater than SL IV violation?

SL IV

NOV

SL IV

NCV

Yes

Yes

Yes

Yes

Yes

Yes

Yes

Yes

No

Yes

Yes

No

No

No

No

No

Yes

No

No

No

CAP effectiveness validated?

NCV Criteria met?

Screening Criteria Met?

No

No

Evaluate need

to re-open other

closed ITAAC’s

ITAAC

Related Construction Finding

Violation of

NRC

Requirements?

Disposition IAW CAP?

Construction

Issue

Review Actions

Inform Licensee

Don’t Document

Yes

No

No

Document Violation IAW 0613

Finding

Yes

Unresolved

Issue

Unknown

Associated with Enforcement Categories?

No

Yes

Exceptions for  Documenting a Minor Violation Met?

Yes

No

Determine Severity Level iAW Enforcement Policy

Screen for CSFC Aspects

APPENDIX C

Guidance for Expanded Inspection Reports

One of the objectives of Inspection Procedures (IP) 90001 and 90002 is to provide an assessment of the licensee’s analysis and corrective actions associated with the issue(s) that prompted the expanded inspection.  The guidance contained in Inspection Manual Chapter (IMC) 0613 applies equally to the baseline and expanded portions of the power reactor construction inspection program; however, given the nature of expanded inspections, the type of documentation for expanded inspections will be different than for baseline inspections.  An expanded inspection report will document the NRC’s independent assessment of each inspection requirement and pertinent qualitative observations of the licensee’s efforts to identify and address the root cause of the issue prompting the expanded inspection.  A separate inspection report will usually be generated for each expanded inspection.  All violations and findings must conform to the format guidance provided in IMC 0613.  The independent review of the extent of condition and extent of cause called for in IP 90002 and performed using one or more procedure(s) chosen from Appendix B to IMC 2506 should be documented in addition to the other inspection requirements contained in IP 90002.  Specific documentation requirements and report format for inspections conducted in accordance with IP 90003 will be provided by the team leader.

Listed below are some general principles that apply to documenting the results of the expanded inspections performed in accordance with IP 90001/90002.  These principles supplement the guidance contained elsewhere in IMC 0613.

1.	The cover letter of the expanded inspection report should conform to the guidance given for baseline inspection reports, but it should also contain a brief description of the inspection staff’s overall conclusion regarding the effectiveness of the licensee’s evaluation and corrective actions associated with the issue(s) that prompted the inspection.

2.	A summary of issues for the expanded inspection report should contain the inspection staff’s overall assessment of the issue(s).  The summary will include any specific findings associated with the licensee’s evaluation and findings that emerged during the inspection.

3.	The expanded inspection report should contain a description of the inspection scope.  This section should describe the purpose and objectives of the inspection and the issue(s) that prompted the inspection.  This summary can be taken from a previous inspection report for an inspection-related issue.  This section can also include a description of the licensee’s preparation efforts for the inspection.

4.	The expanded inspection report should contain an assessment for each of the areas listed below, as applicable.  For each area, state the inspection requirements prescribed in Section 9000X-02, “Inspection Requirements,” of IP 90001/90002.  Provide a synopsis of the licensee’s assessment related to the inspection requirement, the inspection staff’s assessment of the licensee’s evaluation, and any additional actions taken by the inspector to assess the validity of the licensee’s evaluation.

a.	Problem Identification

b.	Root Cause, Extent-of-Condition, and Extent-of-Cause Evaluation

c.	Corrective Actions

d.	Independent Assessment of Extent-of-Condition and Extent-of-Cause (only for IP 90002 inspection reports)

e.	Safety Culture Consideration (only for IP 90002 inspection reports)

5.	For all expanded inspections conducted in accordance with IP 90001/90002, an assessment of the licensee’s evaluation and corrective actions associated with the issue(s) should be documented.  Negative conclusions regarding aspects of the licensee’s evaluation and corrective actions should be supported by examples of violations (i.e., observations or findings).  Other conclusions should be supported by a brief statement describing their bases.

6.	The expanded inspection report should contain an exit meeting summary, a list of persons contacted, licensee documents reviewed during the inspection, and acronyms used in the inspection report.

7.	The recommended signature authority for expanded inspection reports is as follows:

a.	For an inspection performed in accordance with IP 90001/90002 that resulted in no findings or severity level IV violations, the responsible branch chief will sign out the report.

b.	For an inspection performed in accordance with IP 90001/90002 that resulted in greater than severity level IV violations, the responsible division director will sign out the report.

c.	For an inspection performed in accordance with IP 90003, the deputy regional administrator for construction will sign out the report.

8.	Inspectors should follow the guidance in this manual chapter to record expanded inspection results in CIPIMS.

9.	Expanded Inspection reports should be issued within 45 days of the exit meeting.

APPENDIX D

Guidance For Documenting Inspection Procedure 35007

Part 52, Identification and Resolution of Construction Problems

One of the objectives of Inspection Procedure 35007 is to provide an assessment of the effectiveness of the licensee’s corrective action programs (CAP).  Consequently, the type of documentation for this inspection should be different than for other baseline inspections and may include more qualitative observations.  Listed below are some general principles that apply to documenting the results of IP 35007.  These principles supplement the guidance contained elsewhere in Inspection Manual Chapter (IMC) 0613.

1.	The cover letter for this report should conform to the guidance given for other baseline inspections, but it should also contain a brief description of the team’s overall conclusion regarding the effectiveness of the licensee’s CAP.

2.	The summary of issues for this report should contain the team’s overall assessment of the licensee’s CAP, on the basis of both the biennial in-depth samples and routine baseline inspections.  This overall assessment should also be placed in CIPIMS as an observation.

3.	The inspection report should contain an assessment for each of the inspection requirements as follows.

a.	Assessment of the Corrective Action Program Effectiveness

Inspection Scope - Identify the documents that were reviewed and, if   applicable, the other activities that were competed to verify that:

- The licensee is identifying problems at the proper threshold and entering them into the corrective action system;

- The licensee is adequately prioritizing and evaluating issues, include pertinent reference numbers (for example, NCR #s, violations #s, etc.); and

- Corrective actions are effective at preventing recurrence and timely.

Include samples taken from the previous 12 months of routine baseline inspection reports.  Also include assessments and audits of the corrective action program that were completed within the previous 12 months.

Assessment - Effectiveness of Problem Identification Document a general conclusion regarding the licensee’s effectiveness in problem identification.  Include the bases for the general conclusion.  Discuss issues and relevant observations regarding problem identification, and properly disposition any related findings.

Assessment - Effectiveness of Prioritization and Evaluation of Issues Document a general conclusion regarding the licensee’s effectiveness in problem evaluation, and include the bases for that conclusion.  Discuss issues relative to:

- The effectiveness of the licensee’s process for prioritizing issues

- Technical adequacy and depth of evaluations (including root cause analysis where appropriate)

- Adequate consideration of operability and reportability requirements

- Appropriate consideration of risk in prioritizing or evaluating issues.

Assessment - Effectiveness of Corrective Actions Document a general conclusion regarding the licensee’s ability to develop and implement effective corrective actions.  Include the bases for the general conclusion and an assessment of the licensee’s consideration of risk insights in prioritizing corrective actions.  Discuss issues and relevant observations regarding corrective actions, including, for significant conditions adverse to quality, issues associated with the effectiveness of corrective actions to prevent recurrence.

b.	Assessment Use of Operating Experience

Inspection Scope - Identify the documents that were reviewed and, if applicable, the other activities that were completed to verify that the licensee appropriately used operating experience information.

Assessment - Document a general conclusion regarding the licensee’s use of operating experience information.  Include the bases for the general conclusion.

c.	Assessment of the Self-Assessments and Audits

Inspection Scope - Identify the documents that were reviewed and, if applicable, the other activities that were completed to verify that the licensee conducted self- and independent assessments of their activities and practices, as appropriate to assess performance and identify areas for improvement.

Assessment - Document a general conclusion regarding the licensee’s self-assessments and audits.  Include in the conclusion if issues identified by those self-assessments were addressed.  Incorporate into the discussion the bases for the general conclusion

d.	Assessment of Safety Conscious Work Environment

Inspection Scope - Identify the documents that were reviewed and, if applicable, the other activities that were completed to assess whether issues exist that may represent challenges to the free flow of information, and to determine whether underlying factors exist that would produce a reluctance to raise nuclear safety concerns.

Assessment - Document a general conclusion regarding the existence of issues that may represent challenges to the free flow of information, and of underlying factors that could produce a reluctance to raise nuclear safety concerns.  Include the bases for the general conclusion.

4.	Negative conclusions regarding aspects of the CAP should be supported by examples of violations.  Other conclusions should be supported by a brief statement of the basis for the conclusion, including the scope of material reviewed.

APPENDIX E

Examples of Greater-Than-Minor Construction Violations

E.1	PURPOSE

The purpose of this appendix is to provide additional guidance to the Nuclear Regulatory Commission (NRC) staff regarding the difference between minor and greater-than-minor construction issues.  The information contained in this section provides clarification and examples that may help the inspector determine if an inspection finding is greater than minor.  The examples contained herein are minor construction issues referenced by Question 1 of Appendix B to aid the inspector in determining if a violation is “greater-than-minor.”

Section 2.10, “MINOR VIOLATIONS,” of the NRC ENFORCEMENT MANUAL acknowledges that there is no set rule as to what is minor and what is not (i.e., the determination that an issue is minor will depend on the circumstances of the particular issue.)

E.2	DEFINITION OF MINOR VIOLATION

Minor violations are below the significance of that associated with Severity Level IV violations and are not the subject of formal enforcement action or documentation.  Failures to implement requirements that have insignificant safety or regulatory impact or findings that have no more than minimal risk should normally be categorized as minor.  While licensees must correct minor violations, minor violations do not normally warrant documentation in inspection reports or inspection records and do not warrant enforcement action.

As used in this appendix, the term “insignificant” relates to a condition adverse to quality that has a minimal safety or regulatory impact.

E.3	WORK IN PROGRESS FINDINGS

All examples in this appendix assume (unless otherwise stated) that the construction activity had been released for use.  This does not imply that “actual” work on an SSC had to have been performed for an issue to be greater-than-minor.  For example, if a design drawing had been released for use (i.e., the licensee had reviewed and approved the drawing), and it contained significant errors, the issue may be greater-than-minor even if no SSCs had been constructed with the incorrect drawing.

All examples in this appendix assume that the licensee had an opportunity to identify and correct the issue (i.e., the construction activity had been reviewed by at least one level of licensee quality assurance, quality control, or other designated / authorized personnel.)

This does not imply that the licensee must have “signed-off” the construction activity as complete.  If the licensee had performed a quality control acceptance inspection, check, or review, which would reasonably be expected to identify and correct the issue, then the specific construction activity may not be a “work-in-progress.”

E.4	ISOLATED ISSUES

THE NRC ENFORCEMENT MANUAL, SECTION 2.10, “MINOR VIOLATIONS,” states:

Issues that represent isolated (i.e., “isolated” in that based on a reasonable effort, the staff determines that the issue is not recurring nor is it indicative of a programmatic issue such as inadequate supervision, resources, etc.) failures to implement a requirement and have insignificant safety or regulatory impact should normally be categorized as minor violations.

If possible, the inspector should determine whether the issue represented an isolated failure to implement a requirement which had an insignificant safety or regulatory impact.  For an issue to be considered isolated, the inspector has determined that the issue is not indicative of a programmatic issue.  If the inspector did not sample enough to make this determination, the issue should not be considered isolated.  The determination that an issue is isolated should imply that the licensee had established adequate measure to control the construction activity.

Recurring issues that are NOT indicative of a programmatic deficiency, and have an insignificant safety or regulatory impact, should be considered minor.

EXAMPLE OF AN ISOLATED ISSUE:

Issue:			The NRC inspectors identified that the licensee failed to implement a requirement.

Minor Because:	Based on the number of similar samples inspected, independent review and/or observation of construction activities, and discussion with appropriate licensee personnel, the inspectors determined that the issue was not recurring, and not indicative of a programmatic issue, and that the issue had an insignificant safety or regulatory impact.

E.5	ISSUES RELATED TO THE QUALITY OF A SSC OR ACTIVITY (APPENDIX B MINOR SCREENING QUESTION 2)

Issues that could render the quality of a SSC or activity, unacceptable or indeterminate, would generally be associated with violations.

An issue that could adversely affect a SSC’s ability to perform its intended safety function, or could impair the accomplishment of another SSC’s safety function, should generally be considered greater-than-minor.  Also, issues that represent a reduction in safety margin compared to the latest safety analysis approved by the NRC should also be considered greater-than-minor.

["Could" does NOT imply that the issue would absolutely adversely affect the SSC.  It implies a probability that the ability of the SSC to perform its intended safety function may be adversely affected if the proper conditions existed.]

The non-existence of a detailed engineering justification does not necessarily imply that the issue is minor, in that the inspector should consider that the lack of a more detailed evaluation may indicate that the licensee failed to adequately consider the scope of the issue or fully understand the technical and quality requirements.  In some cases, re-design may appear to be a simple corrective action, and minor on the surface; however, the staff should verify that all interactions and interfaces have been considered and that sufficient design margin is available.

E.6	ISSUES RELATED TO THE FAILURE TO ESTABLISH, IMPLEMENT, OR MAINTAIN AN ADEQUATE PROCESS, PROGRAM, PROCEDURE OR QUALITY OVERSIGHT FUNCTION (APPENDIX B MINOR SCREENING QUESTION 3)

Depending on the particular circumstances, issues related to the “Failure to ESTABLISH an adequate process, program, procedure, or quality oversight function that could render the quality of the construction activity unacceptable or indeterminate,” should be considered greater-than-minor.  These issues are more significant, in that the licensee will depend on these processes, programs, procedures, and quality oversight functions to establish the basis that the SSC is constructed in accordance with the approved design (i.e., the SSC will perform its intended safety function.)

E.7	ISSUES THAT COULD ADVERSELY AFFECT THE CLOSURE OF AN INSPECTION, TEST, ANALYSIS, AND ACCEPTANCE CRITERIA (ITAAC)

An issue, that if left uncorrected, could potentially prevent the licensee from closing an ITAAC, should be considered greater than minor.  The issue must be material to the acceptance criteria of the ITAAC.

E.8	GENERAL DOCUMENT NOTES

a.	As used in this appendix, the terms “licensee” and “applicant” are interchangeable.

b.	As used in this appendix, the term “Inspector” relates to the NRC inspector (unless otherwise stated.)

c.	In all examples, it is assumed that the licensee documents and corrects the issue, even if the issue is determined to be minor.  If the licensee fails to correct a minor violation, that would be screened as a different issue.

d.	The referenced quality assurance (QA) Criterion may be the 10 CFR 50, Appendix B criterion, the corresponding ASME NQA-1, or other equivalent QA criteria which were approved by the NRC staff as part of the license.

E.9	CONSTRUCTION ISSUE EXAMPLES (APPENDIX B- QUESTION 1)

| TABLE 1: ISSUES RELATED TO THE APPENDIX B MINOR SCREENING QUESTIONS |  | EXAMPLE |
| --- | --- | --- |
| QUESTION 2: Does the issue, if left uncorrected, represent a condition adverse to quality that renders the quality of a structure, system, or component (SSC) or activity, unacceptable or indeterminate, AND the issue is associated with any one or more of the following [A-D]? | A. A deficiency in the design, manufacture, construction, installation, inspection, or testing of a SSC, which required one of the following to establish the adequacy of the SSC to perform its intended safety function: (i) a detailed engineering justification; (ii) redesign; (iii) replacement; (iv) supplemental examination, inspection, or test; (v) substantial rework; or (vi) repair | 1, 12; 13; 16; 17; 19; 22; 24; 25; 26 |
|  | B. A non-conservative error in a computer program, design specification, construction specification, design report, drawing, calculation, or other design output document that defines the technical requirements for the SSC | 2; 3; 9; 14; 17; |
|  | C. An irretrievable loss of a quality assurance record; or a record-keeping issue that could preclude the licensee from being able to take appropriate action on safety-significant matters, or from objectively or properly assessing, auditing, or otherwise evaluating safety-significant activities | 4; 10; |
|  | D. An unqualified process, procedure, tool, instrument or personnel used for a construction activity that either invalidated previously accepted activities, or required requalification | 5; 6; 7; 11; 13; 15; 16; 20; 21; |
| QUESTION 3: Does the issue, if left uncorrected, represent a failure to establish, implement or maintain an adequate process, program, procedure, or quality oversight function that could render the quality of the construction activity unacceptable or indeterminate? |  | 2; 3; 4; 6; 7; 8; 9; 10; 15; 17; 18; 19; 22; 23; 24; 25 |

| TABLE 2: ISSUES RELATED TO SPECIFIC QA CRITERIA |  |  |  |
| --- | --- | --- | --- |
| Category | 10 CFR Part 50, Appendix B Criteria |  | Example |
| Management Controls | 1 | Organization | None |
|  | 2 | QA Program | 5; 13; 15; 21; |
|  | 18 | Audits | 8 |
| Design Control | 3 | Design Control | 1; 2; 3; 9; 14; 17; |
| Procurement | 4 | Procurement Document Control | None |
|  | 7 | Control of Purchased Material, Equipment and Services | 8 |
| Work Controlling Documents and Records | 5 | Instructions, Procedures and Drawings | 2; 3; 6; 7; 8; 10; 12; 17; 18; 19; 20; 22; 24; |
|  | 6 | Document Control | 14; 17; 18; 19; |
|  | 17 | QA Records | 4; 10; 11; 26 |
| Materials and Equipment | 8 | Identification and Control of Materials, Parts, and Components | 23; |
|  | 12 | Control of Measuring and Test Equipment | 11; |
|  | 13 | Handling, Storage and Shipping | 22; 23; 24 |
|  | 14 | Inspection, Test and Operating Status | None |
| Special Processes, Inspection, and Test Control | 9 | Control of Special Processes | 5; 6; 13; 15; 16; 20; 26 |
|  | 10 | Inspection | 5; 7; 12; 13; 16; 21; 25; 26; |
|  | 11 | Test Control | None |
| Nonconformance and Corrective Action | 15 | Nonconforming Materials, Parts or Components | 12; 17; 25; |
|  | 16 | Corrective Action | 25; |

EXAMPLE 1

Issue:			The NRC inspectors identified that the as-built SSC did not meet the applicable design or construction specification.

Minor because:	The as-built SSC was acceptable without the support of a detailed engineering justification, or amendment to the licensing basis document (i.e., the issue was insignificant.)

Or: the as-built SSC was an alternate design that the governing code allowed, and the use of this alternate design only required a minor revision to the specification.

Or the as-built SSC did not conform to the specification, but was made acceptable with minor re-work (e.g., minor adjustment or minor grinding) or completion of originally prescribed processing.

Or the as-built structure was more conservative than the as-designed.

Not minor if:		The use of that alternate design required a detailed justification by the licensee to ensure that the as-built structure did not adversely affect the SSC’s ability to perform its intended safety function and would not impair the accomplishment of a safety function through adverse interaction.

Or the use of the alternate design resulted in the licensee having to meet other technical requirements, which were not part of the original design.  For example, the use of the as-built structure would require additional inspections, tests, re-work, maintenance, etc., to ensure that the SSC would perform its intended safety function.

Or the as-built SSC required substantial rework or repair.

Or the use of the as-built SSC required a supplemental examination in order to establish the ability to perform its intended safety function.

EXAMPLE 2

Issue:			The inspectors identified that the licensee’s design specification does not conform to the design basis (i.e., the licensee failed to adequately translate the approved design to appropriate drawings, instruction, procedures, etc.).

Minor because:	The design error resulted in a more conservative analysis than what was required by the governing technical requirements.

Or the design error was insignificant, in that the ability of the as-designed SSC to perform its intended safety function was not challenged.

Not minor if:		The design error resulted in a less conservative analysis that could have adversely affected the SSC’s ability to perform its intended safety function.

EXAMPLE 3

Issue:			The inspectors identified that an electrical drawing (design output document) failed to adequately translate the design basis requirements by omitting the voltage output regulation required to feed a safety significant SSC.  The SSC had not been constructed, but the drawing had been released for use.

Minor because:	The error was insignificant, in that SSC could perform its intended safety function, within the operating range of the degraded voltage level.

Not minor if:		The design error could have caused the SSC to not perform its intended safety function.

EXAMPLE 4

Issue:			The inspectors identified that the licensee failed to store quality-related records in accordance with QA program requirements.

Minor because:	The licensee had established adequate procedures for the retention (storage) of records and the records were not damaged or lost.

Or an insignificant portion of a record was damaged or lost, such as a cover page, index, etc., which did not provide the documentary evidence that the SSC would perform its intended safety function.

Not minor if:		Actual records were lost or damaged, and the licensee could not easily recreate the records with reasonable assurance of their accuracy (i.e., supplemental inspections were required to recreate the missing information.)  [Note: If actual records were lost, the issue may be indicative of a programmatic deficiency, even if the records were able to be recreated]

Or the licensee had not established adequate procedures for the retention of QA records (e.g., the licensee had not purchased adequate storage cabinets for permanent or temporary storage of QA records.)

EXAMPLE 5

Issue:			The NRC inspectors identified that the licensee’s QC inspector was not qualified in accordance with the QA program requirements.

Minor because:	The inspector’s unqualified status was a result of an administrative issue, and the ability or competence of the inspector was not suspect.  For example, the inspector’s certification paperwork was not signed by his employer, but he had completed all other required training and qualification requirements.

Not minor if:		The QC inspector was not qualified to perform the inspection, in that his ability or competence was suspect.  For example, the QC inspector’s eye examination had expired, or corrective lenses were not worn when performing the QC inspection.

Or the inspector’s unqualified status resulted in the invalidation of previously accepted inspections.

EXAMPLE 6

Issue:			The inspectors identified that the licensee was welding with a different size and type of tungsten electrode than that allowed by the welding procedure specification.

Minor because:	According to the ASME code, a change in the electrode size or type is a nonessential variable; therefore, the welding procedure specification does not need to be re-qualified.

Not minor if:		If the issue is related to a change in an essential variable, and the procedure was required to be re-qualified.

EXAMPLE 7

Issue:			The inspectors identified that the licensee’s test procedure was not compliant with technical or quality requirements, or both.

Minor because:	The issue was insignificant, in that the procedure was not unqualified due to a technical issue (i.e., the procedure did not require requalification, and the results of previous inspections were not suspect).

Not minor if:		The procedure was required to be qualified by performance demonstration.

Or, the results of previous inspections were invalid.

EXAMPLE 8

Issue:			The inspectors identified that the licensee failed to conduct a required annual surveillance of their supplier.

Minor because:	The licensee had established adequate measures to control purchased items and services, and the licensee had completed an initial audit of the supplier; therefore, the supplier was approved to provide safety-related SSCs.  The supplier continued to demonstrate adequate controls over technical and quality requirements as evidenced by acceptable receipt inspections performed upon delivery of the SSCs to the licensee.

Not minor if:		The licensee or the NRC identified violation related to the SSCs supplied by the supplier, which may have been prevented or identified by the surveillance.

Or the licensee had not established measures to ensure that purchased items and services conformed to applicable technical and quality requirements.

EXAMPLE 9

Issue:			A design change was made to a SSC, but the change was not controlled by measures commensurate with those applied to the original design.

Minor because:	The design change did not contain technical errors that rendered the quality of the SSC unacceptable or indeterminate, and was isolated.

Not minor if:		The design change contained errors that could affect the quality of the SSC and the ability of the SSC to perform its intended safety function.

EXAMPLE 10

Issue:			The inspectors identified that the licensee failed to authenticate QA records as required by the QA program.

Minor because:	The failure to authenticate QA records was isolated to one work activity, and the licensee had established measures to ensure that records were complete and accurate, and the actual records were complete and accurate (i.e., the failure to formally validate the QA records did not adversely affect the quality of the construction activity.)

Not minor if:		The licensee had failed to establish a process or program to ensure that QA records were complete and accurate.

Or the failure to authenticate QA records was not isolated, in that records for multiple work activities were not authenticated.

Or the record issue was significant, in that the records were found to be incomplete or inaccurate such that the quality of the construction activity was indeterminate (i.e., the QA records did not contain information needed to provide reasonable evidence that the SSC could perform its intended safety function.)

EXAMPLE 11

Issue:			Inspectors identified an error on the calibration records for measuring & test equipment (M&TE.)

Minor because:	The M&TE can be retested and the results are clearly within the prescribed acceptance standards (i.e., the error was a documentation error and not evidence of an M&TE that was out of calibration.)

Not minor if:		If the issue requires an evaluation of out of tolerance, lost, or damaged M&TE that indicates questionable acceptability for previous inspection or test results indicating the need to re-inspect or re-test.

EXAMPLE 12

Issue:			For a completed inspection, the inspectors identified that the licensee failed to meet the acceptance limit.

Minor because:	The acceptance limit was more conservative than the governing regulatory requirement.

Not minor if:		The acceptance limit was a regulatory limit, and the failed test rendered the quality of the SSC unacceptable or indeterminate.

EXAMPLE 13

Issue:			During construction of a SSC, the NRC inspectors identified a deficiency with the inspection of a safety-related SSC.

Minor because:	The inspection was not required by any regulation (i.e., “For Information Only”), and the qualification of the examiner and procedure were adequate.

Not minor if:		If the inspection was required by regulation.  (i.e., the examination would be used to establish the adequacy of the SSC to perform its intended safety function)

Or, the qualifications of the examiner or the procedure (if either were used for quality-related inspection activities) were suspect such that the acceptability of completed, quality-related inspections was, unacceptable or indeterminate.

EXAMPLE 14

Issue:			The as-built SSC did not match the design drawing, because the drawing was not updated with an approved engineering change request.

Minor because:	The failure to update the design drawing was isolated, and the as-built is acceptable as is.

Not minor if:		The failure to update design drawings was not isolated.

Or the as-built was unacceptable, in that the engineering change request was inappropriately approved.

Or the incorrect drawing adversely affected other construction activities, such as other engineering activities.

EXAMPLE 15

Issue:			The NRC inspector identified that a licensee QC inspector had not completed required refresher training, and therefore had expired certifications.

Minor because:	Initial qualification training had been performed, and the ability of the inspector to perform the technical inspection was not suspect.

Or the inspector had not performed any inspections while his training was expired.

Not minor if:		The refresher training was significant in that the ability of the inspector to perform adequately was suspect

Or the licensee was required to reexamine safety-related SSCs because of the expired certifications.

EXAMPLE 16

Issue:			During visual examination of a weld, the inspectors identified that the licensee’s QC inspector failed to verify that he had the minimum required light intensity

Minor because:	Although the QC inspector did not measure the light intensity, the ambient lighting was greater than the minimum, and a visual indication could have been seen by the inspector.

Or the QC inspector used an acceptable alternative method to verify the minimum light intensity.

Not minor if:		If the ambient lighting was less than the minimum, and the welds were required to be re-inspected.

Or the lighting could have been less than the required minimum and the welds were not accessible for re-inspection.

EXAMPLE 17

Issue:			To disposition a nonconformance with technical requirements, the licensee initiated and approved an engineering change request (ECR.)  However, the licensee failed to post the ECR to the affected drawing.

Minor because:	The licensee did not perform any construction work to the affected drawing.

Or the licensee continued construction work to the affected drawing, but the change did not directly affect the work performed.

Not minor if:		If the ECR was directly related to work performed, and rendered the quality of the SSC unacceptable or indeterminate.

EXAMPLE 18

Issue:			NRC inspectors identified that a licensee procedure had undergone major revision and contained reference to another site procedure which had been cancelled prior to the date of the revision.

Minor because:	The issue was insignificant, in that the cancelled procedure was not required to provide information that was material to the successful completion of the specific work activity (i.e., the issue was administrative.)

Not minor if:		The issue was significant, in that the revised procedure relied on a cancelled procedure to provide information that was important to the successful completion of a work activity that affected a SSC (e.g., acceptance criteria for an inspection, guidance for technical evaluation of data, qualification criteria, etc.)

EXAMPLE 19

Issue:			During inspection of construction activities, the NRC inspector found a superseded copy of the installation work procedure beside some tools staged at the job site.

Minor because:	Work activities had not been conducted with the outdated procedure.

Or work activities had been completed with the outdated procedure, but the difference between the outdated procedure and current revision did not render the quality of the construction activity unacceptable or indeterminate.

Not minor if:		The outdated procedure was being used and the differences were not insignificant (i.e., the quality of the construction activity was unacceptable or indeterminate.)

EXAMPLE 20

Issue:			The licensee’s welding procedure allowed higher limits on amperage than that allowed by the welding code.

Minor because:	No welding had been performed in the unacceptable range.

Or welding at the higher amperage would not adversely affect the weld.

Not minor if:		If welding had been performed (or would be performed) at amperage higher than what the code allowed, and the welding procedure had not been re-qualified at the higher amperage.

EXAMPLE 21

Issue:			NRC inspectors identified that a licensee QC inspector had expired training and certification records related to concrete cylinder break tests.  The QC inspector’s certifications had been expired for three months.

Minor because:	The issue was isolated, and the expired certification documents was an administrative issue, in that, the inspector maintained adequate knowledge and experience to perform the break tests, and interpret the results in accordance with the approved test procedures.

Not minor if:		If deficiencies were identified with the concrete cylinder break tests that can be attributed to expired certification.

Or the results of the previous break tests were invalid.

EXAMPLE 22

Issue:			Licensee procedures require that all safety-related structural steel be stored off the ground to prevent corrosion.  The inspectors identified structural steel that was lying directly on the ground.

Minor because:	The steel had not been damaged and there was no active corrosion that would require a detailed engineering evaluation, re-design or repair to establish the adequacy of the structural steel to perform its intended safety function.

Not minor if:		The structural steel was damaged such that a detailed engineering evaluation, re-design, or repair was necessary to establish the adequacy of the structural steel to perform its intended safety function.

EXAMPLE 23

Issue:			The inspectors identified that items in a lay-down area were missing tags which were required by a licensee QA procedure.

Minor because:	The tags were an administrative control, in that the items did not rely on the tags to maintain material traceability as required by a regulatory requirement.

Not minor if:		The tags were required to maintain traceability, and the licensee had installed items for which they had lost material traceability.

EXAMPLE 24

Issue:			Inspectors identified that the environmental storage conditions of SSCs did not meet the licensee’s QA program requirements.

Minor because:	Storage conditions had an insignificant impact on the SSC.

Not minor if:		Inadequate environmental storage conditions adversely affected stored items.

EXAMPLE 25

Issue:			The inspectors identified that the licensee failed to initiate a nonconformance report for a licensee-identified deficiency discovered during the final inspection of an item.

Minor because:	The licensee maintained another process for documentation (identification) of the nonconformance, and the deficiency was corrected with minor rework, completion of originally prescribed processing, or was acceptable “as-is” without a detailed engineering justification.

Not minor if:		The licensee failed to document (identify) the nonconformance.

EXAMPLE 26

Issue:			The NRC inspectors identified a technical error on an inspection record for a code required examination.

Minor because:	The technical error was insignificant.

Or the person responsible for the completeness and accuracy of the information on the report had not signed it.

Not minor if:		The error was not insignificant, and the person responsible for the completeness and accuracy of the information on the report had signed it.

APPENDIX F

Construction Safety Focus Components and Aspects

Because the causes of inspection findings are unique to each finding, inspectors should use their judgment in deciding which construction safety focus component (CSFC) aspect is most appropriate, if any.  For conditions adverse to quality, licensees will typically perform an apparent cause evaluation.  As part of the inspection process, inspectors should have identified the cause that provides the most meaningful insight into the performance deficiency.  Inspectors are not expected to perform independent causal evaluation beyond what would be appropriate for the significance of the issue.  Selection of the CSFC aspect should very closely align with the violation.  Usually, there should be only one principal cause and one CSFC aspect associated with each finding.  More detailed guidance can be found in IMC 2505 “Periodic Assessment of Construction Inspection Program Results.”

Inspectors are not expected to document a CSFC aspect for each and every inspection finding.  A CSFC aspect of an inspection finding should be discussed in the report details if the inspector determines that the CSFC aspect of the finding was a significant contributor to the performance deficiency.

Inspectors shall not use the existence of a CSFC aspect to determine that a finding is greater than minor. Appendix B, “Issue Screening” should be used to determine whether the inspection finding is greater than minor.

A.	Baseline Inspection

1.	Decision-Making – Licensee decisions demonstrate that construction quality is an overriding priority.   Specifically (as applicable):

(a)	The licensee makes decisions related to construction quality that reflect the potential to impact ITAAC (closure or affect on already closed ITAAC) using a systematic process to ensure construction quality is maintained.

Authority and roles for evaluating these decisions are formally defined and communicated to applicable personnel including contractors and subcontractors.

Interdisciplinary input and review are attained on decisions that relate to more than one discipline.

Management uses a systematic process for planning, coordinating, and evaluating major changes in the construction environment.  When deviations from design or specifications are needed or recognized, the condition is promptly brought to the attention of the design authority. The condition is then carefully evaluated and is addressed though a formal design-change process before personnel proceed, thereby minimizing the potential for rework or nonconformance with the COL.

(b)	The licensee uses conservative assumptions in decision-making and adopts a requirement to demonstrate that the proposed construction activity does not adversely impact construction quality or ITAAC closure. The licensee conducts effectiveness reviews (e.g. self assessments or audits) of these decisions to verify the validity of the underlying assumptions, identify possible unintended consequences, and determine how to improve future decisions.

For example, when making decisions related to testing, individuals ensure that they are on the correct unit and question the validity of their underlying assumptions, identify possible unintended consequences, and obtain appropriate management involvement and/or interdisciplinary input and reviews.

(c)	The licensee communicates decisions and the basis for decisions, in a timely manner, to personnel who have a need to know the information in order to perform work properly.

2.	Resources - The licensee ensures that personnel, equipment, procedures, and other resources are available and adequate to assure construction quality. Specifically, those necessary for:

(a)	Sufficient number of qualified personnel available to ensure the plant is constructed using a quality process in accordance with the design.

Training is developed and implemented to ensure technical competency and reinforces that safety significant construction quality is of the highest priority.  The licensee ensures that contractor and licensee staffs have the necessary training and qualifications.  Management ensures individuals maintain their professional and technical knowledge, skills, and abilities.

The licensee ensures adequate knowledge transfer from contract personnel to licensee personnel ensuring technical competency once the contract work is completed.

(b)	Complete, accurate and up-to-date design documentation (field drawings), procedures, and work packages, and correct labeling of components.

(c)	Adequate and available facilities and equipment, including temporary construction structures.

3.	Work Control - The licensee plans and coordinates work activities, consistent with ensuring construction quality.  Specifically (as applicable):

(a)	The licensee appropriately plans construction activities by addressing:

- The potential to impact quality (CAQ/SCAQ)

- Job site conditions, including environmental conditions which may impact human performance; previously/concurrently built structures, systems, and components; human-system interface; or radiological safety; and

- Abort criteria to prevent inadvertent equipment damage, either to equipment being operated or connected systems

(b)	The licensee appropriately coordinates work activities by incorporating actions to address:

- The impact of changes to the work scope or other planned construction activities and work environment conditions (lighting, energy sources, etc.) that may affect work activities,

- The impact of the work on different job activities, and the need for work groups to maintain interfaces with offsite organizations, and communicate, coordinate, and cooperate with each other during activities in which interdepartmental or multiple vendor coordination is necessary to assure quality construction,

- Communication and coordination is maintained among on-site vendors, contractors, licensee personnel, and site support staff including transitory personnel.

- The need to keep personnel apprised of construction work status that may affect work activities.

4.	Work Practices - Personnel work practices support human performance.  Specifically (as applicable):

(a)	The licensee communicates human error prevention techniques, such as holding pre-job briefings, self and peer checking, and proper documentation of activities. These techniques are used commensurate with the potential to impact construction quality for the assigned task, such that work activities are performed in a quality manner with appropriate attention to detail.

Personnel are fit for duty. In addition, personnel do not proceed in the face of uncertainty or unexpected circumstances (maintain a questioning attitude).

(b)	The licensee defines and effectively communicates expectations regarding procedural compliance and personnel follow procedures and work instructions.

(c)	The licensee ensures supervisory and management oversight of work activities, including contractors, such that construction quality is supported.

5.	Corrective Action Program – The licensee ensures that issues potentially impacting construction quality are promptly identified, fully evaluated, and that actions are taken to address construction quality concerns in a timely manner, commensurate with their significance.  Specifically (as applicable):

(a)	The licensee implements a corrective action program with a defined threshold for identifying issues. The licensee identifies such issues completely, accurately, and in a timely manner commensurate with their impact on construction quality.

(b)	The licensee periodically trends and assesses information from the CAP and other assessments in the aggregate to identify programmatic and common cause problems.  The licensee communicates the results of the trending to applicable personnel (licensee personnel, contractors, subcontractors, and vendors).

(c)	The licensee thoroughly evaluates problems such that the resolutions address causes and extent of conditions, as necessary including properly classifying conditions adverse to quality. This also includes, for significant problems, conducting effectiveness reviews of corrective actions to ensure that the problems are resolved.  Classifying of events should include review for impact to ITAAC conclusions or reliability assumptions used in the plant-specific Design Reliability Assurance Program (DRAP).

(d)	The licensee takes appropriate corrective actions to address construction quality issues and adverse trends in a timely manner, commensurate with their significance (CAQ/SCAQ), complexity, and ability to impact ongoing construction activities.

(e)	If an alternative process (i.e., a process for raising concerns that is an alternate to the licensee’s corrective action program or line management) for raising construction quality concerns exists, then it results in appropriate and timely resolutions of identified problems.

6.	Construction Experience - The licensee uses construction experience (Con E) information, including vendor recommendations and internally generated lessons learned, to ensure construction quality. Specifically (as applicable):

(a)	The licensee systematically collects, evaluates, and communicates to affected internal stakeholders in a timely manner relevant internal and external Con E.

(b)	The licensee implements and institutionalizes Con E through changes to construction processes, procedures, materials, and training programs.

7.	Self and Independent Assessments – The licensee conducts self- and independent assessments of their activities and practices, as appropriate, to assess performance and identify areas for improvement. Specifically (as applicable):

(a)	The licensee conducts self-assessments at an appropriate frequency; such assessments are of sufficient depth, are comprehensive, are appropriately objective, and are self-critical. The licensee periodically assesses the effectiveness of oversight groups and programs such as CAP and policies.

(b)	The licensee tracks and trends safety and construction quality indicators (performance goals), which provide an accurate representation of performance.

(c)	The licensee coordinates and communicates results from assessments to affected personnel, and takes corrective actions to address issues commensurate with their significance.

8.	Accountability - Management defines the line of authority and responsibility for construction quality. Specifically (as applicable):

(a)	Accountability is maintained for significant quality assurance decisions in that the system of rewards and sanctions is aligned with construction quality and reinforces behaviors and outcomes, which reflect construction quality as an overriding priority.

(b)	Management communicates and reinforces quality assurance standards and displays behaviors that reflect construction quality as an overriding priority.

(c)	The workforce demonstrates a proper construction quality focus and reinforces quality assurance principles among their peers.

B.	Safety Conscious Work Environment

1.	Environment for Raising Concerns - An environment exists in which employees feel free to raise concerns both to their management and/or the NRC without fear of retaliation and employees are encouraged to raise such concerns.  Specifically (as applicable):

(a)	Behaviors and interactions of licensee personnel, contractors, subcontractors, and vendors encourage free flow of information related to raising construction quality concerns, differing professional opinions, and identifying issues in the CAP and through self-assessments. Such behaviors include supervisors responding to employee safety concerns in an open, honest, and non-defensive manner and providing complete, accurate, and forthright information to oversight, audit, and regulatory organizations. Past behaviors, actions, or interactions that may reasonably discourage the raising of such issues are actively mitigated.  As a result, personnel freely and openly communicate in a clear manner conditions or behaviors, such as fitness for duty issues that may impact quality and personnel raise construction quality issues without fear of retaliation.

(b)	If an alternative processes (i.e., a process for raising concerns or resolving differing professional opinions that are alternates to the licensee’s corrective action program or line management) for raising concerns or resolving differing professional opinions exists, then they are communicated, accessible, have an option to raise issues in confidence, and are independent, in the sense that the program does not report to line management (i.e., those who would in the normal course of activities be responsible for addressing the issue raised).

2.	Preventing, Detecting, and Mitigating Perceptions of Retaliation – A policy for prohibiting harassment and retaliation for raising safety significant construction quality concerns exists and is consistently enforced in that:

(a)	All personnel are effectively trained that harassment and retaliation for raising safety significant construction quality (i.e. nuclear safety related) concerns is a violation of law and policy and will not be tolerated.

(b)	Claims of discrimination are investigated consistent with the content of the regulations regarding employee protection and any necessary corrective actions are taken in a timely manner, including actions to mitigate any potential chilling effect on others due to the personnel action under investigation.

(c)	The potential chilling effects of disciplinary actions and other potentially adverse personnel actions (e.g., reductions, outsourcing, and reorganizations) are considered and compensatory actions are taken when appropriate.

APPENDIX G

Guidance for the Use of the Construction Inspection Program Information Management System (CIPIMS) for Documenting Inspections and Developing Inspection Reports

A.	Inspection Detail Entry and Review.  The scope and results of each inspection activity involving the construction of a reactor facility shall be documented in a narrative report entry in CIPIMS.

Completed CIPIMS entries will periodically be extracted for input into an integrated report consisting of a cover letter, a cover page, a summary of findings and inspection details.  Final reports will be entered into ADAMS as the official record of inspection results.

1.	Inspectors.  All NRC inspectors are required to prepare construction inspection report input in accordance with the guidance provided in this manual chapter.

a.	Inspectors shall categorize all inspection results into inspection items and link each inspection item to the appropriate ITAAC(s) and/or Program(s).

Inspection items may stand alone as inspection results and indicate that no findings were identified.

The inspector shall screen construction issues in accordance with Section 0613-05.

b.	The inspector shall prepare a write-up of inspection results in a succinct narrative fashion appropriate for inclusion in a finished report.  The write-up shall include the scope of the inspection, the results of the inspection (no significant findings identified, findings, deviations, or non-conformances), and appropriate conclusions.

Reports should be written in the past tense.  The inspection was conducted before the report was written. The inspector is describing what he did and what he found.  Use plain language.  The purpose of the report is to report facts and the interpretation of those facts.  Most of the time, simpler language is better.

2.	Documenting Inspections in CIPIMS.  The inspector’s narrative write-up shall be entered into CIPIMS and shall include all information required by CIPIMS to link the inspection results to the appropriate docket number, assigned report number, and the area(s) of inspection (e.g., ITAAC family, Construction or Operational Program, etc.).

Refer to the CIPIMS Users Guide for detailed guidance in recording inspection items, generating inspection reports, and obtaining database information in report format.

a. 	Create and Update Inspection Items.  The Create/Update Inspection Item process provides the ability to create inspection items for a specific Docket and Inspection Report as well as view and update existing inspection items.  The inspector has the capability to create and categorize each inspection item as either ITAAC or Non-ITAAC.  Further categorization and detail is available to help further define inspection items such as Summary, Procedure number referenced, and Findings/Deviations/Non-Conformance Text.  The information entered in this window will be used in the generation of the inspection report.

Once an inspection item is defined, it will go through a process of state changes from “Draft” to “Locked” so as to be included in the Inspection Report.  An inspection item in draft form indicates that it may be edited.

An inspection item that is “Ready for Approval” has all fields disabled.  The approver reviewing the inspection item may send the draft to the inspector for additional changes or set it to Approved status.  Once an inspection report is finalized, the approved inspection items become locked and no further entries are permitted.

Note:  An inspection item may be changed from Locked to Draft; however, this will result in the inspection report no longer being finalized and requiring the report to once again go through the review process.  CIPIMS will not permit the user to unlock an observation that is on a finalized report or has been pulled into a subsequent report for follow-up.  Within the 3-day grace period the inspection report can be un-finalized which will set all inspection items (excluding those that have been pulled into a subsequent report) back to the approved state.

b.	Open Item Inspection Items.  The Open Item Inspection Items window provides the ability to pull an open inspection item into a new inspection report.  The user can select an inspection report and see all the available inspection items that can be pulled into the report.  When the inspection item is pulled into a new report, a new sequence is created for the inspection item.  The new sequence will contain information from the previous sequence such as Title, ITAAC/Program, and CAP Numbers.  Fields available for editing on the new sequence will be limited to Inspection Procedure No., Additional Procedure No, inspector, contractor location, contractor name, Status of Follow-up, notes, blank CAP Numbers, and the Text fields.  By pulling the inspection item into a new report, the inspection item can either be updated or closed.

c.	Additional Information.  In cases where listing(s) of documents reviewed for an inspection item are too extensive to enter into the CIPIMS inspection item for the report, the inspector shall prepare a special feeder report containing the required information (referencing the CIPIMS entry being supported) and forward it to the lead inspector for later inclusion in the report containing the related CIPIMS inspection item.

Listing of personnel contacted during the inspection shall be included as a special feeder report containing the required information (referencing the CIPIMS entry being supported) and forwarded to the lead inspector for possible inclusion in the report containing the related CIPIMS inspection item.

B.	Organization of CIPIMS Inspection Items into a Periodic Report.

1.	Inspectors.  At the specified periodicity, the lead inspector for the project will extract completed inspection items from CIPIMS for assembly into an inspection report.  The lead inspector will typically be responsible for the preparation of the cover letter and other report sections required by this manual chapter.

a.	When CIPIMS is queried for inspection items assigned to an inspection report, CIPIMS is designed to automatically provide all associated inspection items. Those inspection items that are categorized as incomplete by the inspector and/or have not been approved by the inspector’s supervisor will be flagged.  The lead inspector shall contact the inspection supervisor(s) to have the inspection items completed and approved or reassigned to the next integrated report number.

b.	If the inspection supervisor(s) have justification why the inspection item cannot be completed in time for the issue of the next periodic report, the lead inspector shall confirm that the inspection item has been re-assigned to the next integrated report number prior to extracting the completed inspection items to build the report.

2.	Reviewers.  Before issuance, each inspection report should be reviewed by a member of NRC management familiar with NRC requirements in the area inspected.  All CIPIMS inspection items shall be reviewed and approved by a member of management for content and format as required by this manual chapter and the CIPIMS User’s Guide.  The review shall include the appropriate categorization of any finding.

a.	Final reports shall be approved by the Branch Chief responsible for the project.  Reports containing potential escalated enforcement should be approved at least one management level above Branch Chief.

b.	This review should establish that conclusions are logically drawn and sufficiently supported by inspection items and findings, and that the inspection items, findings, and conclusions are consistent with NRC policies and requirements.

c.	There will be occasions during the management review of prepared reports when a decision will be made to change the category of a finding (i.e., from a construction finding to an ITAAC finding or vice versa, from an inspection item to a finding, etc.)  As a minimum, these changes should be discussed with the inspector(s) of record for the affected CIPIMS entry, or at the very least, the approving supervisor for the CIPIMS entry, to ensure continued concurrence.  CIPIMS entries shall be adjusted to agree with the management position.  (Note: the category (outcome) of the finding can be changed while the inspection item is in the draft state.

3.	Report Issuing Organization.  Periodic assessment of licensee/vendor performance and assessment of inspection documentation for completion of ITAAC will be done through a search of CIPIMS to validate that the information is accurate and complete.

4.	Generating an Inspection Report.  The Generate Inspection Report window provides the ability to view the details of, as well as, generate an inspection report. Users can view a list of inspectors that have made inspection items for a specific inspection report along with the lowest state of the inspection item.  Further details of the inspection items made by the inspectors can be viewed from this window.  Users will also have the ability to reassign inspection items that have not been approved to a different inspection report.

The Generate Inspection Report button provides the ability to finalize an inspection report, as well as generate a portable document format (PDF) version of the report.  Users with the appropriate authority will have the ability to Finalize the inspection report.

Finalizing an inspection report means that all the inspection items have been recorded, approved, and the inspection report is ready to be put into ADAMS.  When Finalized, all associated inspection items will be put into the Locked state and no further inspection items may be recorded for that inspection report.  When a report is Finalized, a PDF version of the document can be created (if Adobe Acrobat PDF Writer is installed) or a hard copy version of the document can be printed.

C.	Procedures for Concurrence Reviews.  The inspector and reviewer concurrence process shall be in accordance with agency-approved procedures.  These procedures address how to ensure continued inspector concurrence when substantive changes are made to the report as originally submitted, and how to address and resolve any internal differences that may occur during the review process.

D.	Procedure for Non-concurrence.  The agency has a mechanism for inspectors and reviewers to document “non-concurrences” when inspection report issues or substantive changes cannot be adequately resolved.  The procedure addresses how to document these non-concurrences and the criteria for when and how a documented non-concurrence will be attached to the inspection report.

ATTACHMENT 2

Revision History for IMC 0613

| Commitment Tracking Number | Issue Date | Description of Change | Training Required | Training Completion Date | Comment Resolution Accession Number |
| --- | --- | --- | --- | --- | --- |
| N/A | 10/20/08 CN 08-029 | Researched commitments for 4 years and found none. Initial issuance to provide direction for format and content when writing construction inspection reports. | Yes | N/A | N/A |
| N/A | 12/02/09 CN 09-029 | Major document development and revision constituting complete re-write. Incorporation of construction inspection screening process, inspection reporting guidance and additional guidance in new Appendices C through G. | No | N/A | ML093140539 |