## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Preliminary Test 2, 7/C Cable in Location A
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III control cable. (Item #10) Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: One cable temperature (see thermocouple map), air temperatures above and below the cable, and the cable tray rung temperature. Gas burner initiated: Following 220 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
220 | 0 | Ignited Gas Burner
285-290 | 65-70 | Conductors 5, 6 & 7 all short to ground at less than 1000 ohms (795, 475 & 369) | Initial failures are by conductors shorting to ground
301 | 81 | Conductors 5 & 6 short together at less than 1000 ohms (425) | Failures progress to additional conductor-to-conductor shorts and shorts to ground
306 | 86 | Conductors 6 & 7 short together at less than 1000 ohms (474)
404-418 |  | Conductor 1 shorts to all other conductors (1 - 7) at less than 100 ohms (25, 3, 20, 8, 6 & 10)
411 | 191 | Conductor 1 shorts to ground at less than 100 ohms (4)
421-432 | 201-212 | Conductor 2 shorts to conductors 3, 4, 5, 6 & 7 at less than 100 ohms (9, 12, 16, 27 & 29)
423-436 | 203-416 | Conductors 2, 3 & 4 all short to ground at less than 100 ohms (10, 4 & 1) | All conductors have shorted to external ground.
435-444 | 215-224 | Conductor 3 shorts to conductors 4, 5, 6 & 7 at less than 100 ohms (27, 18, 2 & 4)
439-444 | 219-224 | The existing ground faults on conductors 5, 6 & 7 all decrease to less than 100 ohms (1, 2 & 1)
446-452 | 226-232 | Conductor 4 shorts to conductors 5, 6 & 7 at less than 100 ohms (2, 12 & 29)
455-458 | 235-238 | The existing short between conductors 5 & 6 decreases to less than 100 ohms (12) and conductor 5 shorts to conductor 7 at much less than 100 ohms (<1)
460 | 240 | The existing short between conductors 6 & 7 decreases to less than 100 ohms (27) | All conductors have shorted together at less than 100 ohms
1167 | 947 | Extinguished Gas Burner
Additional Observations

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable = | XLPE, 7/C | (Item #10)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| A4 | = | Within cable just below cable jacket, center position
| A5 | = | Air temperature above cable
| A6 | = | Air temperature below cable

## C-C Individuals
Conductor to Conductor Resistances
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59
XLPE | 7-C | Tray A
0 | 250 kW
Burner Time | C1-2 | Burner Time | C1-3 | Burner Time | C1-4 | Burner Time | C1-5 | Burner Time | C1-6 | Burner Time | C1-7 | Burner Time | C2-3 | Burner Time | C2-4 | Burner Time | C2-5 | Burner Time | C2-6 | Burner Time | C2-7 | Burner Time | C3-4 | Burner Time | C3-5 | Burner Time | C3-6 | Burner Time | C3-7 | Burner Time | C4-5 | Burner Time | C4-6 | Burner Time | C4-7 | Burner Time | C5-6 | Burner Time | C5-7 | Burner Time | C6-7 | Burner Time | Minimums
-124 | 258037.9994 | -121 | 256137.9994 | -118.5 | 254837.9994 | -115.5 | 238837.9994 | -112.5 | 254537.9994 | -110 | 517575.9997 | -107 | 254737.9994 | -104.5 | 258537.9994 | -101.5 | 253837.9994 | -98.5 | 253337.9994 | -95.5 | 259737.9994 | -93 | 258437.9994 | -90.5 | 245337.9994 | -87.5 | 258637.9994 | -84.5 | 259737.9994 | -82 | 260037.9994 | -79 | 252037.9994 | -76 | 258537.9994 | -73.5 | 259137.9994 | -70.5 | 259237.9994 | -68 | 253337.9994 | -124 | 238837.9994
30 | 258037.9994 | 33 | 256137.9994 | 35.5 | 254837.9994 | 39 | 238837.9994 | 41.5 | 254537.9994 | 44 | 517575.9997 | 47 | 254737.9994 | 49.5 | 258537.9994 | 52.5 | 253837.9994 | 55.5 | 253337.9994 | 58 | 259737.9994 | 61 | 258437.9994 | 63.5 | 40806.3297 | 66.5 | 258637.9994 | 69.5 | 259737.9994 | 72 | 51927.5969 | 75 | 2526.3789 | 77.5 | 2019.9091 | 80.5 | 425.1002 | 83.5 | 1236.6754 | 86 | 474.4201 | 30 | 425.1002
184 | 25.2928 | 187 | 2.9615 | 189.5 | 20.2339 | 192.5 | 7.7167 | 195.5 | 5.6746 | 198 | 10.298 | 201 | 8.8609 | 203.5 | 12.3994 | 206.5 | 15.8065 | 209.5 | 26.7902 | 212 | 28.9608 | 215 | 26.8199 | 217.5 | 18.0626 | 220.5 | 2.2638 | 223.5 | 4.3853 | 226 | 2.1502 | 229 | 11.6024 | 231.5 | 29.1507 | 234.5 | 12.0571 | 237.5 | 0.34726 | 240 | 26.7902 | 184 | 0.34726
338 | 16.4255 | 341 | 0.91097 | 343.5 | 1.4943 | 346.5 | 7.1652 | 349.5 | 0.89714 | 352 | 23.2925 | 355 | 16.8278 | 357.5 | 4.1583 | 360.5 | 12.1002 | 363.5 | 26.5947 | 366 | 9.1347 | 369 | 3.9427 | 371.5 | 17.7702 | 374.5 | 28.2787 | 377.5 | 5.0456 | 380 | 15.0284 | 383 | 3.1943 | 385.5 | 17.2004 | 388.5 | 4.5351 | 391.5 | 3.7032 | 394 | 7.3965 | 338 | 0.89714
492 | 8.1279 | 494.5 | 21.8019 | 497.5 | 0.036568 | 500.5 | 0.75845 | 503.5 | 16.6245 | 506 | 0.93335 | 509 | 0.89887 | 511.5 | 0.93163 | 514.5 | 23.9779 | 517 | 11.2148 | 520 | 26.951 | 523 | 0.27664 | 525.5 | 10.6317 | 528.5 | 10.0114 | 531.5 | 0.94192 | 534 | 0.94449 | 537 | 6.1364 | 539.5 | 7.126 | 542.5 | 17.2556 | 545 | 13.2689 | 548 | 17.0666 | 492 | 0.036568
646 | 0.44697 | 649 | 18.7712 | 651.5 | 0.0044923 | 654.5 | 3.7793 | 657.5 | 0.74411 | 660 | 7.1176 | 663 | 12.9676 | 665.5 | 0.031683 | 668.5 | 23.9779 | 671.5 | 26.2055 | 674 | 14.4224 | 677 | 0.72643 | 679.5 | 22.3088 | 682.5 | 10.5975 | 685.5 | 21.2708 | 688 | 15.1338 | 691 | 8.3177 | 693.5 | 6.3006 | 696.5 | 19.7185 | 699.5 | 6.4101 | 702 | 0.88672 | 646 | 0.0044923
800 | 5.685 | 802.5 | 2.8752 | 805.5 | 1.4521 | 808.5 | 5.6399 | 811 | 14.8288 | 814 | 3586.7824 | 816.5 | 11246.6251 | 819.5 | 5.5772 | 822.5 | 6678.9105 | 825.5 | 465.4427 | 828 | 1347.6432 | 831 | 133.8259 | 833.5 | 101.4531 | 836.5 | 24.9884 | 839.5 | 21.398 | 842 | 108.2529 | 845 | 1238.3174 | 847.5 | 476.104 | 850.5 | 1044.4684 | 853.5 | 780.3241 | 856 | 801.9111 | 800 | 1.4521
954 | 69.4875 | 956.5 | 18.8212 | 959.5 | 61.9768 | 962.5 | 34.8499 | 965.5 | 9.4541 | 968 | 46.2072 | 971 | 53.6254 | 973.5 | 47.9283 | 976.5 | 69.369 | 979 | 69.1835 | 982 | 42.6086 | 984.5 | 43.1272 | 987.5 | 56.9281 | 990.5 | 36.1971 | 993.5 | 25.6919 | 996 | 76.1904 | 998.5 | 16.2588 | 1001.5 | 15.3202 | 1004.5 | 41.1637 | 1007 | 41.5953 | 1010 | 61.9374 | 954 | 9.4541
1108 | 28.5111 | 1110.5 | 33.1556 | 1113.5 | 60.7152 | 1116.5 | 34.8258 | 1119.5 | 69.0965 | 1122 | 34.0256 | 1124.5 | 51.0668 | 1127.5 | 43.0641 | 1130.5 | 39.6512 | 1133 | 25.1166 | 1136 | 22.4085 | 1138.5 | 71.8729 | 1141.5 | 20.4537 | 1144.5 | 41.975 | 1147 | 47.5882 | 1150 | 66.7547 | 1152.5 | 39.1639 | 1155.5 | 59.2383 | 1158.5 | 44.3988 | 1161 | 64.6633 | 1164 | 15.8132 | 1108 | 15.8132

## C-G Min
Average Conductor to Ground Resistances
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59
XLPE | 7-C | Tray A
0 | 250 kW
Burner Time | C1-G |  | Burner Time | C2-G | Burner Time | C3-G | Burner Time | C4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | C7-G | Burner Time | Minimums Overall
-116.9167 | 238838 |  | -105.1667 | 253338 | -97.25 | 245338 | -92.1667 | 252038 | -88.9167 | 238838 | -86.5 | 252038 | -84.0833 | 253338 | -116.9167 | 238838
37.1667 | 238838 |  | 48.75 | 253338 | 56.75 | 40806.3333 | 61.75 | 2019.9836 | 65.1667 | 795.105 | 67.5 | 474.6893 | 69.75 | 369.3296 | 37.1667 | 369.3296
191.0833 | 4.459 |  | 202.75 | 10.2717 | 210.75 | 3.7858 | 215.75 | 0.64666 | 219.0833 | 0.67186 | 221.5 | 1.9051 | 223.75 | 0.91221 | 191.0833 | 0.64666
345.0833 | 0.64336 |  | 356.75 | 5.105 | 364.75 | 5.0878 | 369.75 | 0.6376 | 373.0833 | 1.6565 | 375.5 | 0.65052 | 377.75 | 0.63562 | 345.0833 | 0.63562
499 | 0.63686 |  | 510.6667 | 0.63735 | 518.6667 | 0.63439 | 523.75 | 0.63366 | 527 | 4.7974 | 529.4167 | 0.63587 | 531.6667 | 0.63735 | 499 | 0.63366
653.0833 | 1.1116 |  | 664.75 | 0.6386 | 672.75 | 1.7317 | 677.75 | 2.6759 | 681.0833 | 0.64923 | 683.5 | 0.65052 | 685.75 | 0.63439 | 653.0833 | 0.63439
806.9167 | 2.9637 |  | 818.6667 | 5.7076 | 826.5833 | 26.2825 | 831.75 | 7.611 | 835.0833 | 6.5981 | 837.4167 | 3.763 | 839.75 | 6.365 | 806.9167 | 2.9637
961 | 716.7568 |  | 972.6667 | 6700.4033 | 980.5833 | 4383.7677 | 985.5833 | 5145.9847 | 989 | 311.7391 | 991.3333 | 570.7438 | 993.6667 | 5784.4891 | 961 | 311.7391
1115 | 1722.9682 |  | 1126.5833 | 209.0544 | 1134.4167 | 947.6241 | 1139.5833 | 355.6493 | 1143 | 810.8659 | 1145.3333 | 251.1843 | 1147.5833 | 1908.9283 | 1115 | 209.0544

## C6-7
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 154.7241 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 6 & 7
Time-109 | N11 | N12 | Time-110 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
39003.4132 | 1 | 0 | 39003.4132 | 1 | 0 | -68 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39003.415 | 441 | 0 | 39003.415 | 553 | 13 | 86 | 306 | 26.9231 | 0 | 33.7607 | 0.79365 | 0.26923 | 0 | 0.33761 | 0.0079365 | 0.26923 | 0.32967 | 474.6893 | 369.3296 | 474.4201
39003.4168 | 1980 | 0 | 39003.4168 | 2344 | 0 | 240 | 460 | 120.8791 | 0 | 143.1013 | 0 | 1.2088 | 0 | 1.431 | 0 | 1.2088 | 1.431 | 27.999 | 8.122 | 26.7902
39003.4186 | 2329 | 0 | 39003.4186 | 2307 | 0 | 394 | 614 | 142.1856 | 0 | 140.8425 | 0 | 1.4219 | 0 | 1.4084 | 0 | 1.4219 | 1.4084 | 8.8184 | 9.8561 | 7.3965
39003.4203 | 2141 | 0 | 39003.4204 | 2054 | 0 | 548 | 768 | 130.7082 | 0 | 125.3968 | 0 | 1.3071 | 0 | 1.254 | 0 | 1.3071 | 1.254 | 18.3737 | 23.3875 | 17.0666
39003.4221 | 2518 | 0 | 39003.4221 | 2321 | 0 | 702 | 922 | 153.7241 | 0 | 141.6972 | 0 | 1.5372 | 0 | 1.417 | 0 | 1.5372 | 1.417 | 0.65052 | 9.1935 | 0.88672
39003.4239 | 2206 | 7 | 39003.4239 | 2101 | 7 | 856 | 1076 | 134.6764 | 0.42735 | 128.2662 | 0.42735 | 1.3468 | 0.0042735 | 1.2827 | 0.0042735 | 1.3425 | 1.2784 | 15.1612 | 21.1629 | 801.9111
39003.4257 | 940 | 980 | 39003.4257 | 1007 | 1114 | 1010 | 1230 | 57.3871 | 59.8291 | 61.4774 | 68.0098 | 0.57387 | 0.59829 | 0.61477 | 0.6801 | 0.02442 | 0.065324 | 3069.8281 | 8209.6921 | 61.9374
39003.4275 | 1142 | 1198 | 39003.4275 | 1099 | 1157 | 1164 | 1384 | 69.7192 | 73.138 | 67.094 | 70.6349 | 0.69719 | 0.73138 | 0.67094 | 0.70635 | 0.034188 | 0.035409 | 5620.7458 | 3836.3201 | 15.8132

## C5-7
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 158.326 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 5 & 7
Time-107 | N11 | N12 | Time-108 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
39003.4132 | 1 | 0 | 39003.4132 | 1 | 0 | -70.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
39003.415 | 194 | 0 | 39003.415 | 325 | 0 | 83.5 | 303.5 | 11.8437 | 0 | 19.8413 | 0 | 0.11844 | 0 | 0.19841 | 0 | 0.11844 | 0.19841 | 1236.7938 | 697.9631 | 1236.6754
39003.4167 | 2545 | 0 | 39003.4168 | 2564 | 0 | 237.5 | 457.5 | 155.3724 | 0 | 156.5324 | 0 | 1.5537 | 0 | 1.5653 | 0 | 1.5537 | 1.5653 | 1.901 | 1.1459 | 0.34726
39003.4185 | 2465 | 0 | 39003.4185 | 2577 | 0 | 391.5 | 611.5 | 150.4884 | 0 | 157.326 | 0 | 1.5049 | 0 | 1.5733 | 0 | 1.5049 | 1.5733 | 5.2081 | 0.63562 | 3.7032
39003.4203 | 2262 | 0 | 39003.4203 | 2238 | 0 | 545 | 765 | 138.0952 | 0 | 136.63 | 0 | 1.381 | 0 | 1.3663 | 0 | 1.381 | 1.3663 | 14.6499 | 15.8794 | 13.2689
39003.4221 | 2404 | 0 | 39003.4221 | 2090 | 0 | 699.5 | 919.5 | 146.7643 | 0 | 127.5946 | 0 | 1.4676 | 0 | 1.2759 | 0 | 1.4676 | 1.2759 | 7.8777 | 24.0852 | 6.4101
39003.4239 | 1934 | 6 | 39003.4239 | 2410 | 9 | 853.5 | 1073.5 | 118.0708 | 0.3663 | 147.1306 | 0.54945 | 1.1807 | 0.003663 | 1.4713 | 0.0054945 | 1.177 | 1.4658 | 35.637 | 7.7188 | 780.3241
39003.4256 | 1045 | 1088 | 39003.4257 | 1220 | 1196 | 1007 | 1227 | 63.7973 | 66.4225 | 74.4811 | 73.0159 | 0.63797 | 0.66422 | 0.74481 | 0.73016 | 0.026252 | 0.014652 | 2505.1076 | 5784.4891 | 41.5953
39003.4274 | 992 | 970 | 39003.4275 | 977 | 957 | 1161 | 1381 | 60.5617 | 59.2186 | 59.6459 | 58.4249 | 0.60562 | 0.59219 | 0.59646 | 0.58425 | 0.013431 | 0.01221 | 10272.968 | 15128.5686 | 64.6633

## C5-6
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 158.265 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 5 & 6
Time-105 | N11 | N12 | Time-106 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39003.4131 | 1 | 0 | 39003.4132 | 1 | 0 | -73.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259138 | 259138 | 259137.9994
39003.4149 | 628 | 345 | 39003.4149 | 944 | 686 | 80.5 | 300.5 | 38.3394 | 21.0623 | 57.6313 | 41.8803 | 0.38339 | 0.21062 | 0.57631 | 0.4188 | 0.17277 | 0.15751 | 795.105 | 959.9114 | 425.1002
39003.4167 | 2285 | 0 | 39003.4167 | 2149 | 0 | 234.5 | 454.5 | 139.4994 | 0 | 131.1966 | 0 | 1.395 | 0 | 1.312 | 0 | 1.395 | 1.312 | 13.4521 | 20.6319 | 12.0571
39003.4185 | 2445 | 0 | 39003.4185 | 2100 | 0 | 388.5 | 608.5 | 149.2674 | 0 | 128.2051 | 0 | 1.4927 | 0 | 1.2821 | 0 | 1.4927 | 1.2821 | 6.0278 | 23.4467 | 4.5351
39003.4203 | 2186 | 0 | 39003.4203 | 2576 | 0 | 542.5 | 762.5 | 133.4554 | 0 | 157.265 | 0 | 1.3346 | 0 | 1.5726 | 0 | 1.3346 | 1.5726 | 18.5901 | 0.63587 | 17.2556
39003.4221 | 2142 | 0 | 39003.4221 | 1990 | 0 | 696.5 | 916.5 | 130.7692 | 0 | 121.4896 | 0 | 1.3077 | 0 | 1.2149 | 0 | 1.3077 | 1.2149 | 21.0261 | 30.2704 | 19.7185
39003.4238 | 2192 | 9 | 39003.4239 | 1982 | 8 | 850.5 | 1070.5 | 133.8217 | 0.54945 | 121.0012 | 0.4884 | 1.3382 | 0.0054945 | 1.21 | 0.004884 | 1.3327 | 1.2051 | 18.5832 | 31.6103 | 1044.4684
39003.4256 | 1211 | 931 | 39003.4256 | 985 | 959 | 1004.5 | 1224.5 | 73.9316 | 56.8376 | 60.1343 | 58.547 | 0.73932 | 0.56838 | 0.60134 | 0.58547 | 0.17094 | 0.015873 | 311.7391 | 570.7438 | 41.1637
39003.4274 | 1031 | 1078 | 39003.4274 | 1058 | 1035 | 1158.5 | 1378.5 | 62.9426 | 65.812 | 64.591 | 63.1868 | 0.62943 | 0.65812 | 0.64591 | 0.63187 | 0.028694 | 0.014042 | 2704.9238 | 10052.5729 | 44.3988

## C4-7
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 157.8987 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 7
Time-103 | N11 | N12 | Time-104 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39003.4131 | 1 | 0 | 39003.4131 | 1 | 0 | -76 | 144 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39003.4149 | 122 | 0 | 39003.4149 | 15 | 0 | 77.5 | 297.5 | 7.4481 | 0 | 0.91575 | 0 | 0.074481 | 0 | 0.0091575 | 0 | 0.074481 | 0.0091575 | 2019.9836 | 17142.5333 | 2019.9091
39003.4167 | 1984 | 0 | 39003.4167 | 2563 | 0 | 231.5 | 451.5 | 121.1233 | 0 | 156.4713 | 0 | 1.2112 | 0 | 1.5647 | 0 | 1.2112 | 1.5647 | 30.3619 | 0.91221 | 29.1507
39003.4185 | 2182 | 0 | 39003.4185 | 2087 | 0 | 385.5 | 605.5 | 133.2112 | 0 | 127.4115 | 0 | 1.3321 | 0 | 1.2741 | 0 | 1.3321 | 1.2741 | 18.5325 | 23.9281 | 17.2004
39003.4202 | 2382 | 0 | 39003.4203 | 2570 | 0 | 539.5 | 759.5 | 145.4212 | 0 | 156.8987 | 0 | 1.4542 | 0 | 1.569 | 0 | 1.4542 | 1.569 | 8.5802 | 0.63735 | 7.126
39003.422 | 2400 | 0 | 39003.422 | 2033 | 0 | 693.5 | 913.5 | 146.5201 | 0 | 124.1148 | 0 | 1.4652 | 0 | 1.2411 | 0 | 1.4652 | 1.2411 | 7.7658 | 27.2199 | 6.3006
39003.4238 | 2406 | 9 | 39003.4238 | 1968 | 8 | 847.5 | 1067.5 | 146.8864 | 0.54945 | 120.1465 | 0.4884 | 1.4689 | 0.0054945 | 1.2015 | 0.004884 | 1.4634 | 1.1966 | 7.611 | 33.3379 | 476.104
39003.4256 | 1188 | 1210 | 39003.4256 | 1060 | 1031 | 1001.5 | 1221.5 | 72.5275 | 73.8706 | 64.7131 | 62.9426 | 0.72527 | 0.73871 | 0.64713 | 0.62943 | 0.013431 | 0.017705 | 58752.3691 | 6167.2157 | 15.3202
39003.4274 | 1009 | 987 | 39003.4274 | 1068 | 1045 | 1155.5 | 1375.5 | 61.5995 | 60.2564 | 65.2015 | 63.7973 | 0.616 | 0.60256 | 0.65201 | 0.63797 | 0.013431 | 0.014042 | 12740.3661 | 10260.9024 | 59.2383

## C4-6
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 153.9304 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 6
Time-101 | N11 | N12 | Time-102 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39003.4131 | 1 | 0 | 39003.4131 | 1 | 0 | -79 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39003.4149 | 96 | 0 | 39003.4149 | 87 | 0 | 75 | 295 | 5.8608 | 0 | 5.3114 | 0 | 0.058608 | 0 | 0.053114 | 0 | 0.058608 | 0.053114 | 2526.4375 | 2798.1379 | 2526.3789
39003.4166 | 2232 | 0 | 39003.4167 | 2004 | 0 | 229 | 449 | 136.2637 | 0 | 122.3443 | 0 | 1.3626 | 0 | 1.2234 | 0 | 1.3626 | 1.2234 | 12.9651 | 25.8174 | 11.6024
39003.4184 | 2409 | 0 | 39003.4184 | 1973 | 0 | 383 | 603 | 147.0696 | 0 | 120.4518 | 0 | 1.4707 | 0 | 1.2045 | 0 | 1.4707 | 1.2045 | 4.665 | 27.7942 | 3.1943
39003.4202 | 2344 | 0 | 39003.4202 | 2429 | 0 | 537 | 757 | 143.1013 | 0 | 148.2906 | 0 | 1.431 | 0 | 1.4829 | 0 | 1.431 | 1.4829 | 7.5674 | 3.8032 | 6.1364
39003.422 | 2298 | 0 | 39003.422 | 2505 | 0 | 691 | 911 | 140.293 | 0 | 152.9304 | 0 | 1.4029 | 0 | 1.5293 | 0 | 1.4029 | 1.5293 | 9.7206 | 0.65389 | 8.3177
39003.4238 | 1902 | 8 | 39003.4238 | 2118 | 8 | 845 | 1065 | 116.1172 | 0.4884 | 129.304 | 0.4884 | 1.1612 | 0.004884 | 1.293 | 0.004884 | 1.1563 | 1.2882 | 33.4325 | 19.3368 | 1238.3174
39003.4256 | 1182 | 1150 | 39003.4256 | 1133 | 1101 | 998.5 | 1218.5 | 72.1612 | 70.2076 | 69.1697 | 67.2161 | 0.72161 | 0.70208 | 0.6917 | 0.67216 | 0.019536 | 0.019536 | 7779.3125 | 7779.3125 | 16.2588
39003.4273 | 1121 | 945 | 39003.4273 | 1182 | 1215 | 1152.5 | 1372.5 | 68.4371 | 57.6923 | 72.1612 | 74.1758 | 0.68437 | 0.57692 | 0.72161 | 0.74176 | 0.10745 | 0.020147 | 355.6493 | 433.9778 | 39.1639

## C4-5
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 158.8144 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 5
Time-99 | N11 | N12 | Time-100 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39003.413 | 1 | 0 | 39003.4131 | 1 | 0 | -82 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260038 | 260038 | 260037.9994
39003.4148 | 5 | 0 | 39003.4148 | 4 | 0 | 72 | 292 | 0.30525 | 0 | 0.2442 | 0 | 0.0030525 | 0 | 0.002442 | 0 | 0.0030525 | 0.002442 | 51927.6 | 64934.5 | 51927.5969
39003.4166 | 2509 | 0 | 39003.4166 | 2353 | 0 | 226 | 446 | 153.1746 | 0 | 143.6508 | 0 | 1.5317 | 0 | 1.4365 | 0 | 1.5317 | 1.4365 | 3.6819 | 10.5559 | 2.1502
39003.4184 | 2235 | 0 | 39003.4184 | 2417 | 0 | 380 | 600 | 136.4469 | 0 | 147.558 | 0 | 1.3645 | 0 | 1.4756 | 0 | 1.3645 | 1.4756 | 16.3928 | 7.6285 | 15.0284
39003.4202 | 2585 | 0 | 39003.4202 | 2092 | 0 | 534 | 754 | 157.8144 | 0 | 127.7167 | 0 | 1.5781 | 0 | 1.2772 | 0 | 1.5781 | 1.2772 | 0.63366 | 24.3489 | 0.94449
39003.422 | 2233 | 0 | 39003.422 | 2149 | 0 | 688 | 908 | 136.3248 | 0 | 131.1966 | 0 | 1.3632 | 0 | 1.312 | 0 | 1.3632 | 1.312 | 16.4971 | 21.0507 | 15.1338
39003.4237 | 2398 | 11 | 39003.4238 | 2447 | 9 | 842 | 1062 | 146.398 | 0.67155 | 149.3895 | 0.54945 | 1.464 | 0.0067155 | 1.4939 | 0.0054945 | 1.4573 | 1.4884 | 9.1601 | 6.5981 | 108.2529
39003.4255 | 949 | 931 | 39003.4255 | 972 | 1006 | 996 | 1216 | 57.9365 | 56.8376 | 59.3407 | 61.4164 | 0.57937 | 0.56838 | 0.59341 | 0.61416 | 0.010989 | 0.020757 | 75511.7465 | 5888.0235 | 76.1904
39003.4273 | 960 | 938 | 39003.4273 | 1119 | 946 | 1150 | 1370 | 58.6081 | 57.265 | 68.315 | 57.7534 | 0.58608 | 0.57265 | 0.68315 | 0.57753 | 0.013431 | 0.10562 | 1192.1806 | 810.8659 | 66.7547

## C3-7
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 158.6313 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 7
Time-97 | N11 | N12 | Time-98 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39003.413 | 1 | 0 | 39003.413 | 1 | 0 | -84.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39003.4148 | 1 | 0 | 39003.4148 | 1 | 0 | 69.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39003.4166 | 2454 | 0 | 39003.4166 | 2379 | 0 | 223.5 | 443.5 | 149.8168 | 0 | 145.2381 | 0 | 1.4982 | 0 | 1.4524 | 0 | 1.4982 | 1.4524 | 5.8835 | 9.2215 | 4.3853
39003.4184 | 2439 | 0 | 39003.4184 | 2073 | 0 | 377.5 | 597.5 | 148.9011 | 0 | 126.5568 | 0 | 1.489 | 0 | 1.2656 | 0 | 1.489 | 1.2656 | 6.5346 | 25.3439 | 5.0456
39003.4202 | 2582 | 0 | 39003.4202 | 2517 | 0 | 531.5 | 751.5 | 157.6313 | 0 | 153.663 | 0 | 1.5763 | 0 | 1.5366 | 0 | 1.5763 | 1.5366 | 0.63439 | 3.2332 | 0.94192
39003.4219 | 2120 | 0 | 39003.4219 | 2458 | 0 | 685.5 | 905.5 | 129.4261 | 0 | 150.0611 | 0 | 1.2943 | 0 | 1.5006 | 0 | 1.2943 | 1.5006 | 22.5651 | 5.7111 | 21.2708
39003.4237 | 2275 | 78 | 39003.4237 | 2425 | 11 | 839.5 | 1059.5 | 138.8889 | 4.7619 | 148.0464 | 0.67155 | 1.3889 | 0.047619 | 1.4805 | 0.0067155 | 1.3413 | 1.4737 | 28.6619 | 7.2983 | 21.398
39003.4255 | 1167 | 1135 | 39003.4255 | 984 | 1020 | 993.5 | 1213.5 | 71.2454 | 69.2918 | 60.0733 | 62.2711 | 0.71245 | 0.69292 | 0.60073 | 0.62271 | 0.019536 | 0.021978 | 10676.6126 | 6104.345 | 25.6919
39003.4273 | 970 | 1085 | 39003.4273 | 1030 | 1006 | 1147 | 1367 | 59.2186 | 66.2393 | 62.8816 | 61.4164 | 0.59219 | 0.66239 | 0.62882 | 0.61416 | 0.070208 | 0.014652 | 947.6241 | 1908.9283 | 47.5882

## C3-6
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 157.9597 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 6
Time-95 | N11 | N12 | Time-96 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39003.413 | 1 | 0 | 39003.413 | 1 | 0 | -87.5 | 132.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39003.4148 | 1 | 0 | 39003.4148 | 1 | 0 | 66.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39003.4166 | 2493 | 0 | 39003.4166 | 2367 | 0 | 220.5 | 440.5 | 152.1978 | 0 | 144.5055 | 0 | 1.522 | 0 | 1.4451 | 0 | 1.522 | 1.4451 | 3.7858 | 9.3105 | 2.2638
39003.4183 | 1998 | 0 | 39003.4183 | 2537 | 0 | 374.5 | 594.5 | 121.978 | 0 | 154.884 | 0 | 1.2198 | 0 | 1.5488 | 0 | 1.2198 | 1.5488 | 29.4985 | 1.9858 | 28.2787
39003.4201 | 2322 | 0 | 39003.4201 | 2571 | 0 | 528.5 | 748.5 | 141.7582 | 0 | 156.9597 | 0 | 1.4176 | 0 | 1.5696 | 0 | 1.4176 | 1.5696 | 11.4289 | 0.63711 | 10.0114
39003.4219 | 2310 | 0 | 39003.4219 | 2101 | 0 | 682.5 | 902.5 | 141.0256 | 0 | 128.2662 | 0 | 1.4103 | 0 | 1.2827 | 0 | 1.4103 | 1.2827 | 12.0078 | 23.1499 | 10.5975
39003.4237 | 2065 | 119 | 39003.4237 | 2402 | 39 | 836.5 | 1056.5 | 126.0684 | 7.265 | 146.6422 | 2.381 | 1.2607 | 0.07265 | 1.4664 | 0.02381 | 1.188 | 1.4426 | 115.8956 | 7.9584 | 24.9884
39003.4255 | 1111 | 1081 | 39003.4255 | 1050 | 1021 | 990.5 | 1210.5 | 67.8266 | 65.9951 | 64.1026 | 62.3321 | 0.67827 | 0.65995 | 0.64103 | 0.62332 | 0.018315 | 0.017705 | 7893.4776 | 9569.587 | 36.1971
39003.4272 | 1039 | 1088 | 39003.4273 | 986 | 963 | 1144.5 | 1364.5 | 63.431 | 66.4225 | 60.1954 | 58.7912 | 0.63431 | 0.66422 | 0.60195 | 0.58791 | 0.029915 | 0.014042 | 2679.0864 | 12370.5599 | 41.975

## C3-5
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 149.84 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 5
Time-93 | N11 | N12 | Time-94 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39003.413 | 1 | 0 | 39003.413 | 1 | 0 | -90.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245338 | 245338 | 245337.9994
39003.4147 | 6 | 0 | 39003.4147 | 0 | 0 | 63.5 | 283.5 | 0.3663 | 0 | 0.030525 | 0 | 0.003663 | 0 | 0.00030525 | 0 | 0.003663 | 0.00030525 | 40806.3333 | 490776 | 40806.3297
39003.4165 | 2057 | 0 | 39003.4165 | 2438 | 0 | 217.5 | 437.5 | 125.58 | 0 | 148.84 | 0 | 1.2558 | 0 | 1.4884 | 0 | 1.2558 | 1.4884 | 19.3184 | 0.67186 | 18.0626
39003.4183 | 2062 | 0 | 39003.4183 | 2248 | 0 | 371.5 | 591.5 | 125.8852 | 0 | 137.2405 | 0 | 1.2589 | 0 | 1.3724 | 0 | 1.2589 | 1.3724 | 19.0291 | 9.1806 | 17.7702
39003.4201 | 2192 | 0 | 39003.4201 | 2332 | 0 | 525.5 | 745.5 | 133.8217 | 0 | 142.3687 | 0 | 1.3382 | 0 | 1.4237 | 0 | 1.3382 | 1.4237 | 11.9699 | 5.2479 | 10.6317
39003.4219 | 1987 | 0 | 39003.4219 | 2162 | 0 | 679.5 | 899.5 | 121.3065 | 0 | 131.9902 | 0 | 1.2131 | 0 | 1.3199 | 0 | 1.2131 | 1.3199 | 23.5219 | 13.5236 | 22.3088
39003.4236 | 1997 | 57 | 39003.4237 | 2122 | 34 | 833.5 | 1053.5 | 121.917 | 3.4799 | 129.5482 | 2.0757 | 1.2192 | 0.034799 | 1.2955 | 0.020757 | 1.1844 | 1.2747 | 28.5442 | 16.8816 | 101.4531
39003.4254 | 969 | 940 | 39003.4254 | 1172 | 1139 | 987.5 | 1207.5 | 59.1575 | 57.3871 | 71.5507 | 69.536 | 0.59158 | 0.57387 | 0.71551 | 0.69536 | 0.017705 | 0.020147 | 13521.7847 | 5217.8996 | 56.9281
39003.4272 | 1126 | 1102 | 39003.4272 | 951 | 931 | 1141.5 | 1361.5 | 68.7424 | 67.2772 | 58.0586 | 56.8376 | 0.68742 | 0.67277 | 0.58059 | 0.56838 | 0.014652 | 0.01221 | 6916.1002 | 22992.185 | 20.4537

## C3-4
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 157.8376 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 4
Time-91 | N11 | N12 | Time-92 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39003.4129 | 1 | 0 | 39003.4129 | 1 | 0 | -93 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39003.4147 | 1 | 0 | 39003.4147 | 1 | 0 | 61 | 281 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258438 | 258438 | 258437.9994
39003.4165 | 2019 | 0 | 39003.4165 | 2063 | 0 | 215 | 435 | 123.2601 | 0 | 125.9463 | 0 | 1.2326 | 0 | 1.2595 | 0 | 1.2326 | 1.2595 | 28.0525 | 25.3214 | 26.8199
39003.4183 | 2452 | 0 | 39003.4183 | 2569 | 0 | 369 | 589 | 149.6947 | 0 | 156.8376 | 0 | 1.4969 | 0 | 1.5684 | 0 | 1.4969 | 1.5684 | 5.4396 | 0.6376 | 3.9427
39003.42 | 2539 | 0 | 39003.4201 | 2351 | 0 | 523 | 743 | 155.0061 | 0 | 143.5287 | 0 | 1.5501 | 0 | 1.4353 | 0 | 1.5501 | 1.4353 | 1.8267 | 9.9694 | 0.27664
39003.4218 | 2528 | 0 | 39003.4219 | 2518 | 0 | 677 | 897 | 154.3346 | 0 | 153.7241 | 0 | 1.5433 | 0 | 1.5372 | 0 | 1.5433 | 1.5372 | 2.2698 | 2.6759 | 0.72643
39003.4236 | 2054 | 87 | 39003.4236 | 1968 | 54 | 831 | 1051 | 125.3968 | 5.3114 | 120.1465 | 3.2967 | 1.254 | 0.053114 | 1.2015 | 0.032967 | 1.2009 | 1.1685 | 30.8593 | 35.5018 | 133.8259
39003.4254 | 1039 | 1079 | 39003.4254 | 995 | 966 | 984.5 | 1204.5 | 63.431 | 65.873 | 60.7448 | 58.9744 | 0.63431 | 0.65873 | 0.60745 | 0.58974 | 0.02442 | 0.017705 | 4383.7677 | 22836.6359 | 43.1272
39003.4272 | 946 | 944 | 39003.4272 | 1201 | 1179 | 1138.5 | 1358.5 | 57.7534 | 57.6313 | 73.3211 | 71.978 | 0.57753 | 0.57631 | 0.73321 | 0.71978 | 0.001221 | 0.013431 | 6425.5429 | 4014.7173 | 71.8729

## C2-7
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 158.6313 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 7
Time-89 | N11 | N12 | Time-90 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
39003.4129 | 1 | 0 | 39003.4129 | 1 | 0 | -95.5 | 124.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39003.4147 | 1 | 0 | 39003.4147 | 1 | 0 | 58 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259738 | 259738 | 259737.9994
39003.4164 | 1996 | 0 | 39003.4165 | 2253 | 0 | 212 | 432 | 121.8559 | 0 | 137.5458 | 0 | 1.2186 | 0 | 1.3755 | 0 | 1.2186 | 1.3755 | 30.1794 | 15.3298 | 28.9608
39003.4182 | 2350 | 0 | 39003.4183 | 2134 | 0 | 366 | 586 | 143.4676 | 0 | 130.2808 | 0 | 1.4347 | 0 | 1.3028 | 0 | 1.4347 | 1.3028 | 10.5694 | 21.761 | 9.1347
39003.42 | 2027 | 0 | 39003.42 | 2341 | 0 | 520 | 740 | 123.7485 | 0 | 142.9182 | 0 | 1.2375 | 0 | 1.4292 | 0 | 1.2375 | 1.4292 | 28.1885 | 10.9944 | 26.951
39003.4218 | 2244 | 0 | 39003.4218 | 2582 | 0 | 674 | 894 | 136.9963 | 0 | 157.6313 | 0 | 1.37 | 0 | 1.5763 | 0 | 1.37 | 1.5763 | 15.7923 | 0.63439 | 14.4224
39003.4236 | 2327 | 9 | 39003.4236 | 1797 | 91 | 828 | 1048 | 142.0635 | 0.54945 | 109.707 | 5.5556 | 1.4206 | 0.0054945 | 1.0971 | 0.055556 | 1.4151 | 1.0415 | 11.7606 | 85.9636 | 1347.6432
39003.4254 | 1087 | 1056 | 39003.4254 | 1075 | 1044 | 982 | 1202 | 66.3614 | 64.4689 | 65.6288 | 63.7363 | 0.66361 | 0.64469 | 0.65629 | 0.63736 | 0.018926 | 0.018926 | 8281.871 | 8281.871 | 42.6086
39003.4271 | 1125 | 1196 | 39003.4272 | 1027 | 1005 | 1136 | 1356 | 68.6813 | 73.0159 | 62.6984 | 61.3553 | 0.68681 | 0.73016 | 0.62698 | 0.61355 | 0.043346 | 0.013431 | 1305.7851 | 2858.8638 | 22.4085

## C2-6
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 154.7241 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 6
Time-87 | N11 | N12 | Time-88 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39003.4129 | 1 | 0 | 39003.4129 | 1 | 0 | -98.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39003.4146 | 1 | 0 | 39003.4147 | 1 | 0 | 55.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253338 | 253338 | 253337.9994
39003.4164 | 1980 | 0 | 39003.4164 | 2487 | 0 | 209.5 | 429.5 | 120.8791 | 0 | 151.8315 | 0 | 1.2088 | 0 | 1.5183 | 0 | 1.2088 | 1.5183 | 27.999 | 1.9051 | 26.7902
39003.4182 | 1983 | 0 | 39003.4182 | 2518 | 0 | 363.5 | 583.5 | 121.0623 | 0 | 153.7241 | 0 | 1.2106 | 0 | 1.5372 | 0 | 1.2106 | 1.5372 | 27.8053 | 0.65052 | 26.5947
39003.42 | 2251 | 0 |  | 2495 | 0 | 517 | 737 | 137.4237 | 0 | 152.3199 | 0 | 1.3742 | 0 | 1.5232 | 0 | 1.3742 | 1.5232 | 12.5891 | 1.5784 | 11.2148
39003.4218 | 1989 | 0 | 39003.4218 | 2471 | 0 | 671.5 | 891.5 | 121.4286 | 0 | 150.8547 | 0 | 1.2143 | 0 | 1.5085 | 0 | 1.2143 | 1.5085 | 27.4198 | 2.565 | 26.2055
39003.4236 | 2017 | 4 | 39003.4236 | 2444 | 9 | 825.5 | 1045.5 | 123.138 | 0.2442 | 149.2063 | 0.54945 | 1.2314 | 0.002442 | 1.4921 | 0.0054945 | 1.2289 | 1.4866 | 27.1348 | 3.763 | 465.4427
39003.4253 | 950 | 928 | 39003.4253 | 1181 | 1148 | 979 | 1199 | 57.9976 | 56.6545 | 72.1001 | 70.0855 | 0.57998 | 0.56654 | 0.721 | 0.70085 | 0.013431 | 0.020147 | 126986.0417 | 4471.7893 | 69.1835
39003.4271 | 1217 | 975 | 39003.4271 | 1175 | 1215 | 1133 | 1353 | 74.2979 | 59.5238 | 71.7338 | 74.1758 | 0.74298 | 0.59524 | 0.71734 | 0.74176 | 0.14774 | 0.02442 | 209.0544 | 251.1843 | 25.1166

## C2-5
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 155.0293 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 5
Time-85 | N11 | N12 | Time-86 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39003.4128 | 1 | 0 | 39003.4128 | 1 | 0 | -101.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
39003.4146 | 1 | 0 | 39003.4146 | 1 | 0 | 52.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
39003.4164 | 2168 | 0 | 39003.4164 | 2407 | 0 | 206.5 | 426.5 | 132.3565 | 0 | 146.9475 | 0 | 1.3236 | 0 | 1.4695 | 0 | 1.3236 | 1.4695 | 17.1301 | 5.4998 | 15.8065
39003.4182 | 2238 | 0 | 39003.4182 | 2498 | 0 | 360.5 | 580.5 | 136.63 | 0 | 152.5031 | 0 | 1.3663 | 0 | 1.525 | 0 | 1.3663 | 1.525 | 13.4665 | 1.6565 | 12.1002
39003.42 | 2028 | 0 | 39003.42 | 2001 | 0 | 514.5 | 734.5 | 123.8095 | 0 | 122.1612 | 0 | 1.2381 | 0 | 1.2216 | 0 | 1.2381 | 1.2216 | 25.216 | 26.9055 | 23.9779
39003.4217 | 2028 | 0 | 39003.4217 | 2523 | 0 | 668.5 | 888.5 | 123.8095 | 0 | 154.0293 | 0 | 1.2381 | 0 | 1.5403 | 0 | 1.2381 | 1.5403 | 25.216 | 0.64923 | 23.9779
39003.4235 | 2223 | 1 | 39003.4235 | 2005 | 2 | 822.5 | 1042.5 | 135.7143 | 0.06105 | 122.4054 | 0.1221 | 1.3571 | 0.0006105 | 1.2241 | 0.001221 | 1.3565 | 1.2228 | 14.2624 | 26.8671 | 6678.9105
39003.4253 | 959 | 928 | 39003.4253 | 1008 | 976 | 976.5 | 1196.5 | 58.547 | 56.6545 | 61.5385 | 59.5849 | 0.58547 | 0.56654 | 0.61538 | 0.59585 | 0.018926 | 0.019536 | 8519.1712 | 7454.3335 | 69.369
39003.4271 | 978 | 1091 | 39003.4271 | 1128 | 1104 | 1130.5 | 1350.5 | 59.707 | 66.6056 | 68.8645 | 67.3993 | 0.59707 | 0.66606 | 0.68864 | 0.67399 | 0.068987 | 0.014652 | 749.6039 | 1144.8778 | 39.6512

## C2-4
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 157.8987 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 4
Time-83 | N11 | N12 | Time-84 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39003.4128 | 1 | 0 | 39003.4128 | 1 | 0 | -104.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39003.4146 | 1 | 0 | 39003.4146 | 1 | 0 | 49.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39003.4164 | 2273 | 0 | 39003.4164 | 2070 | 0 | 203.5 | 423.5 | 138.7668 | 0 | 126.3736 | 0 | 1.3877 | 0 | 1.2637 | 0 | 1.3877 | 1.2637 | 13.7871 | 24.9459 | 12.3994
39003.4181 | 2448 | 0 | 39003.4181 | 2094 | 0 | 357.5 | 577.5 | 149.4505 | 0 | 127.8388 | 0 | 1.4945 | 0 | 1.2784 | 0 | 1.4945 | 1.2784 | 5.6528 | 23.5138 | 4.1583
39003.4199 | 2570 | 0 | 39003.4199 | 2394 | 0 | 511.5 | 731.5 | 156.8987 | 0 | 146.1538 | 0 | 1.569 | 0 | 1.4615 | 0 | 1.569 | 1.4615 | 0.63735 | 8.0359 | 0.93163
39003.4217 | 2546 | 0 | 39003.4217 | 2118 | 0 | 665.5 | 885.5 | 155.4335 | 0 | 129.304 | 0 | 1.5543 | 0 | 1.293 | 0 | 1.5543 | 1.293 | 1.586 | 22.1143 | 0.031683
39003.4235 | 2416 | 0 | 39003.4235 | 2374 | 1 | 819.5 | 1039.5 | 147.4969 | 0 | 144.9328 | 0.06105 | 1.475 | 0 | 1.4493 | 0.0006105 | 1.475 | 1.4487 | 7.0522 | 8.992 | 5.5772
39003.4253 | 1060 | 1027 | 39003.4253 | 1185 | 1151 | 973.5 | 1193.5 | 64.7131 | 62.6984 | 72.3443 | 70.2686 | 0.64713 | 0.62698 | 0.72344 | 0.70269 | 0.020147 | 0.020757 | 8448.0956 | 6877.7268 | 47.9283
39003.427 | 1078 | 1053 | 39003.4271 | 1210 | 1188 | 1127.5 | 1347.5 | 65.812 | 64.2857 | 73.8706 | 72.5275 | 0.65812 | 0.64286 | 0.73871 | 0.72527 | 0.015263 | 0.013431 | 7338.8186 | 23681.2518 | 43.0641

## C2-3
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 155.5788 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 3
Time-81 | N11 | N12 | Time-82 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39003.4128 | 1 | 0 | 39003.4128 | 1 | 0 | -107 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39003.4145 | 1 | 0 | 39003.4146 | 1 | 0 | 47 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254738 | 254738 | 254737.9994
39003.4163 | 2311 | 0 | 39003.4163 | 2173 | 0 | 201 | 421 | 141.0867 | 0 | 132.6618 | 0 | 1.4109 | 0 | 1.3266 | 0 | 1.4109 | 1.3266 | 10.2717 | 17.2747 | 8.8609
39003.4181 | 2157 | 0 | 39003.4181 | 2425 | 0 | 355 | 575 | 131.685 | 0 | 148.0464 | 0 | 1.3168 | 0 | 1.4805 | 0 | 1.3168 | 1.4805 | 18.1446 | 5.0878 | 16.8278
39003.4199 | 2532 | 0 | 39003.4199 | 2462 | 0 | 509 | 729 | 154.5788 | 0 | 150.3053 | 0 | 1.5458 | 0 | 1.5031 | 0 | 1.5458 | 1.5031 | 0.64692 | 3.5085 | 0.89887
39003.4217 | 2229 | 0 | 39003.4217 | 2505 | 0 | 663 | 883 | 136.0806 | 0 | 152.9304 | 0 | 1.3608 | 0 | 1.5293 | 0 | 1.3608 | 1.5293 | 14.3284 | 1.7317 | 12.9676
39003.4234 | 2007 | 1 | 39003.4235 | 2018 | 0 | 816.5 | 1036.5 | 122.5275 | 0.06105 | 123.199 | 0 | 1.2253 | 0.0006105 | 1.232 | 0 | 1.2247 | 1.232 | 27.0393 | 26.2825 | 11246.6251
39003.4252 | 1023 | 989 | 39003.4253 | 990 | 958 | 971 | 1191 | 62.4542 | 60.3785 | 60.4396 | 58.486 | 0.62454 | 0.60379 | 0.6044 | 0.58486 | 0.020757 | 0.019536 | 6700.4033 | 8803.2364 | 53.6254
39003.427 | 1027 | 1004 | 39003.427 | 1180 | 1157 | 1124.5 | 1344.5 | 62.6984 | 61.2943 | 72.0391 | 70.6349 | 0.62698 | 0.61294 | 0.72039 | 0.70635 | 0.014042 | 0.014042 | 10979.913 | 10979.913 | 51.0668

## C1-7
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 158.0208 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 7
Time-79 | N11 | N12 | Time-80 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
39003.4127 | 0 | 0 | 39003.4127 | 1 | 0 | -110 | 110 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 517576 | 258738 | 517575.9997
39003.4145 | 0 | 0 | 39003.4145 | 1 | 0 | 44 | 264 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 517576 | 258738 | 517575.9997
39003.4163 | 2317 | 0 | 39003.4163 | 2428 | 0 | 198 | 418 | 141.453 | 0 | 148.2295 | 0 | 1.4145 | 0 | 1.4823 | 0 | 1.4145 | 1.4823 | 11.7126 | 6.6054 | 10.298
39003.4181 | 2078 | 0 | 39003.4181 | 2549 | 0 | 352 | 572 | 126.862 | 0 | 155.6166 | 0 | 1.2686 | 0 | 1.5562 | 0 | 1.2686 | 1.5562 | 24.5611 | 1.5449 | 23.2925
39003.4198 | 2572 | 0 | 39003.4199 | 2295 | 0 | 506 | 726 | 157.0208 | 0 | 140.1099 | 0 | 1.5702 | 0 | 1.4011 | 0 | 1.5702 | 1.4011 | 0.63686 | 12.7834 | 0.93335
39003.4216 | 2384 | 0 | 39003.4217 | 2239 | 0 | 660 | 880 | 145.5433 | 0 | 136.6911 | 0 | 1.4554 | 0 | 1.3669 | 0 | 1.4554 | 1.3669 | 8.573 | 15.6043 | 7.1176
39003.4234 | 1988 | 1 | 39003.4234 | 2434 | 2 | 814 | 1034 | 121.3675 | 0.06105 | 148.5958 | 0.1221 | 1.2137 | 0.0006105 | 1.486 | 0.001221 | 1.2131 | 1.4847 | 30.4562 | 6.365 | 3586.7824
39003.4252 | 1029 | 1065 | 39003.4252 | 951 | 925 | 968 | 1188 | 62.8205 | 65.0183 | 58.0586 | 56.4713 | 0.62821 | 0.65018 | 0.58059 | 0.56471 | 0.021978 | 0.015873 | 5017.2405 | 21648.2413 | 46.2072
39003.427 | 1071 | 1123 | 39003.427 | 1192 | 1169 | 1122 | 1342 | 65.3846 | 68.5592 | 72.7717 | 71.3675 | 0.65385 | 0.68559 | 0.72772 | 0.71368 | 0.031746 | 0.014042 | 1722.9682 | 3113.5815 | 34.0256

## C1-6
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 155.4567 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 6
Time-77 | N11 | N12 | Time-78 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39003.4127 | 1 | 0 | 39003.4127 | 1 | 0 | -112.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
39003.4145 | 1 | 0 | 39003.4145 | 0 | 0 | 41.5 | 261.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 254538 | 509176 | 254537.9994
39003.4163 | 2377 | 0 | 39003.4163 | 2017 | 0 | 195.5 | 415.5 | 145.116 | 0 | 123.138 | 0 | 1.4512 | 0 | 1.2314 | 0 | 1.4512 | 1.2314 | 7.1258 | 26.2459 | 5.6746
39003.418 | 2530 | 0 | 39003.4181 | 2197 | 0 | 349.5 | 569.5 | 154.4567 | 0 | 134.127 | 0 | 1.5446 | 0 | 1.3413 | 0 | 1.5446 | 1.3413 | 0.64743 | 15.9026 | 0.89714
39003.4198 | 2159 | 0 | 39003.4198 | 2458 | 0 | 503.5 | 723.5 | 131.8071 | 0 | 150.0611 | 0 | 1.3181 | 0 | 1.5006 | 0 | 1.3181 | 1.5006 | 17.9426 | 3.5956 | 16.6245
39003.4216 | 2490 | 0 | 39003.4216 | 2427 | 0 | 657.5 | 877.5 | 152.0147 | 0 | 148.1685 | 0 | 1.5201 | 0 | 1.4817 | 0 | 1.5201 | 1.4817 | 2.2643 | 4.9188 | 0.74411
39003.4234 | 2192 | 0 | 39003.4234 | 2160 | 0 | 811 | 1031 | 133.8217 | 0 | 131.8681 | 0 | 1.3382 | 0 | 1.3187 | 0 | 1.3382 | 1.3187 | 16.167 | 17.888 | 14.8288
39003.4252 | 1225 | 1194 | 39003.4252 | 1078 | 945 | 965.5 | 1185.5 | 74.7863 | 72.8938 | 65.812 | 57.6923 | 0.74786 | 0.72894 | 0.65812 | 0.57692 | 0.018926 | 0.081197 | 716.7568 | 778.5835 | 9.4541
39003.427 | 958 | 936 | 39003.427 | 983 | 961 | 1119.5 | 1339.5 | 58.486 | 57.1429 | 60.0122 | 58.6691 | 0.58486 | 0.57143 | 0.60012 | 0.58669 | 0.013431 | 0.013431 | 11474.4545 | 11474.4545 | 69.0965

## C1-5
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 145.8718 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 5
Time-75 | N11 | N12 | Time-76 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39003.4127 | 1 | 0 | 39003.4127 | 1 | 0 | -115.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
| 1 | 0 | 39003.4145 | 1 | 0 | 39 | 259 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
39003.4162 | 2191 | 0 | 39003.4162 | 2227 | 0 | 192.5 | 412.5 | 133.7607 | 0 | 135.9585 | 0 | 1.3376 | 0 | 1.3596 | 0 | 1.3376 | 1.3596 | 9.0543 | 7.2914 | 7.7167
39003.418 | 2202 | 0 | 39003.418 | 2065 | 0 | 346.5 | 566.5 | 134.4322 | 0 | 126.0684 | 0 | 1.3443 | 0 | 1.2607 | 0 | 1.3443 | 1.2607 | 8.5095 | 15.7085 | 7.1652
39003.4198 | 2373 | 0 | 39003.4198 | 2280 | 0 | 500.5 | 720.5 | 144.8718 | 0 | 139.1941 | 0 | 1.4487 | 0 | 1.3919 | 0 | 1.4487 | 1.3919 | 0.69027 | 4.7974 | 0.75845
39003.4216 | 2272 | 0 | 39003.4216 | 2050 | 0 | 654.5 | 874.5 | 138.7057 | 0 | 125.1526 | 0 | 1.3871 | 0 | 1.2515 | 0 | 1.3871 | 1.2515 | 5.1664 | 16.5551 | 3.7793
39003.4234 | 2233 | 0 | 39003.4234 | 2056 | 0 | 808.5 | 1028.5 | 136.3248 | 0 | 125.5189 | 0 | 1.3632 | 0 | 1.2552 | 0 | 1.3632 | 1.2552 | 7.0031 | 16.215 | 5.6399
39003.4251 | 1033 | 998 | 39003.4252 | 944 | 998 | 962.5 | 1182.5 | 63.0647 | 60.928 | 57.6313 | 60.928 | 0.63065 | 0.60928 | 0.57631 | 0.60928 | 0.021368 | 0.032967 | 29193.9499 | 3287.8806 | 34.8499
39003.4269 | 1031 | 1007 | 39003.4269 | 1028 | 1075 | 1116.5 | 1336.5 | 62.9426 | 61.4774 | 62.7595 | 65.6288 | 0.62943 | 0.61477 | 0.62759 | 0.65629 | 0.014652 | 0.028694 | 5231.6638 | 51257.5385 | 34.8258

## C1-4
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 155.6398 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 4
Time-73 | N11 | N12 | Time-74 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39003.4126 | 1 | 0 | 39003.4126 | 1 | 0 | -118.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39003.4144 | 1 | 0 | 39003.4144 | 1 | 0 | 35.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254838 | 254838 | 254837.9994
39003.4162 | 2098 | 0 | 39003.4162 | 2533 | 0 | 189.5 | 409.5 | 128.083 | 0 | 154.6398 | 0 | 1.2808 | 0 | 1.5464 | 0 | 1.2808 | 1.5464 | 21.5148 | 0.64666 | 20.2339
39003.418 | 2475 | 0 | 39003.418 | 2489 | 0 | 343.5 | 563.5 | 151.0989 | 0 | 151.9536 | 0 | 1.511 | 0 | 1.5195 | 0 | 1.511 | 1.5195 | 3.0053 | 2.4259 | 1.4943
39003.4198 | 2510 | 0 | 39003.4198 | 2089 | 0 | 497.5 | 717.5 | 153.2357 | 0 | 127.5336 | 0 | 1.5324 | 0 | 1.2753 | 0 | 1.5324 | 1.2753 | 1.5689 | 22.0383 | 0.036568
39003.4215 | 2511 | 0 | 39003.4216 | 2456 | 1 | 651.5 | 871.5 | 153.2967 | 0 | 149.9389 | 0.06105 | 1.533 | 0 | 1.4994 | 0.0006105 | 1.533 | 1.4988 | 1.5285 | 3.8444 | 0.0044923
39003.4233 | 2476 | 0 | 39003.4233 | 2285 | 0 | 805.5 | 1025.5 | 151.16 | 0 | 139.4994 | 0 | 1.5116 | 0 | 1.395 | 0 | 1.5116 | 1.395 | 2.9637 | 11.5702 | 1.4521
39003.4251 | 991 | 955 | 39003.4251 | 948 | 946 | 959.5 | 1179.5 | 60.5006 | 58.3028 | 57.8755 | 57.7534 | 0.60501 | 0.58303 | 0.57875 | 0.57753 | 0.021978 | 0.001221 | 2856.3647 | 5145.9847 | 61.9768
39003.4269 | 992 | 969 | 39003.4269 | 1161 | 1209 | 1113.5 | 1333.5 | 60.5617 | 59.1575 | 70.8791 | 73.8095 | 0.60562 | 0.59158 | 0.70879 | 0.7381 | 0.014042 | 0.029304 | 6795.3671 | 1185485.1419 | 60.7152

## C1-3
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 156.4335 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 3
Time-71 | N11 | N12 | Time-72 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39003.4126 | 1 | 0 | 39003.4126 | 1 | 0 | -121 | 99 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
39003.4144 | 1 | 0 | 39003.4144 | 1 | 0 | 33 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256138 | 256138 | 256137.9994
39003.4162 | 2453 | 0 | 39003.4162 | 2106 | 0 | 187 | 407 | 149.7558 | 0 | 128.5714 | 0 | 1.4976 | 0 | 1.2857 | 0 | 1.4976 | 1.2857 | 4.459 | 21.6705 | 2.9615
39003.4179 | 2546 | 0 | 39003.418 | 2256 | 0 | 341 | 561 | 155.4335 | 0 | 137.7289 | 0 | 1.5543 | 0 | 1.3773 | 0 | 1.5543 | 1.3773 | 0.64336 | 13.5807 | 0.91097
39003.4197 | 2082 | 0 | 39003.4197 | 2199 | 0 | 494.5 | 714.5 | 127.1062 | 0 | 134.2491 | 0 | 1.2711 | 0 | 1.3425 | 0 | 1.2711 | 1.3425 | 23.073 | 16.5248 | 21.8019
39003.4215 | 2134 | 0 | 39003.4215 | 2459 | 0 | 649 | 869 | 130.2808 | 0 | 150.1221 | 0 | 1.3028 | 0 | 1.5012 | 0 | 1.3028 | 1.5012 | 20.074 | 4.2041 | 18.7712
39003.4233 | 2455 | 0 | 39003.4233 | 1962 | 0 | 802.5 | 1022.5 | 149.8779 | 0 | 119.7802 | 0 | 1.4988 | 0 | 1.1978 | 0 | 1.4988 | 1.1978 | 4.3739 | 30.6004 | 2.8752
39003.4251 | 1146 | 1191 | 39003.4251 | 1059 | 1023 | 956.5 | 1176.5 | 69.9634 | 72.7106 | 64.652 | 62.4542 | 0.69963 | 0.72711 | 0.64652 | 0.62454 | 0.027473 | 0.021978 | 3676.7868 | 18385.9374 | 18.8212
39003.4269 | 1069 | 1119 | 39003.4269 | 956 | 933 | 1110.5 | 1330.5 | 65.2625 | 68.315 | 58.3639 | 56.9597 | 0.65263 | 0.68315 | 0.58364 | 0.5696 | 0.030525 | 0.014042 | 2482.3362 | 11013.4948 | 33.1556

## C1-2
OB Prelim Test 2 |  |  | 2006-10-13 | 9:59 |  | Vs = |  | 157.5934 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 2
Time-69 | N11 | N12 | Time-70 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39003.4126 | 1 | 0 | 39003.4126 | 1 | 0 | -124 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39003.4143 | 1 | 0 | 39003.4144 | 0 | 0 | 30 | 250 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 258038 | 516176 | 258037.9994
39003.4161 | 2040 | 0 | 39003.4161 | 2228 | 0 | 184 | 404 | 124.5421 | 0 | 136.0195 | 0 | 1.2454 | 0 | 1.3602 | 0 | 1.2454 | 1.3602 | 26.5382 | 15.8609 | 25.2928
39003.4179 | 2192 | 0 | 39003.4179 | 2456 | 0 | 338 | 558 | 133.8217 | 0 | 149.9389 | 0 | 1.3382 | 0 | 1.4994 | 0 | 1.3382 | 1.4994 | 17.7637 | 5.105 | 16.4255
39003.4197 | 2356 | 0 | 39003.4197 | 2097 | 0 | 492 | 712 | 143.8339 | 0 | 128.022 | 0 | 1.4383 | 0 | 1.2802 | 0 | 1.4383 | 1.2802 | 9.5662 | 23.0987 | 8.1279
39003.4215 | 2553 | 0 | 39003.4215 | 2565 | 0 | 646 | 866 | 155.8608 | 0 | 156.5934 | 0 | 1.5586 | 0 | 1.5659 | 0 | 1.5586 | 1.5659 | 1.1116 | 0.6386 | 0.44697
39003.4233 | 2409 | 0 | 39003.4233 | 2443 | 1 | 800 | 1020 | 147.0696 | 0 | 149.1453 | 0.06105 | 1.4707 | 0 | 1.4915 | 0.0006105 | 1.4707 | 1.4908 | 7.1557 | 5.7076 | 5.685
39003.425 | 948 | 962 | 39003.4251 | 1072 | 1033 | 954 | 1174 | 57.8755 | 58.7302 | 65.4457 | 63.0647 | 0.57875 | 0.5873 | 0.65446 | 0.63065 | 0.008547 | 0.02381 | 8980.7399 | 22972.6496 | 69.4875
39003.4268 | 1096 | 1149 | 39003.4268 | 1104 | 1183 | 1108 | 1328 | 66.9109 | 70.1465 | 67.3993 | 72.2222 | 0.66911 | 0.70147 | 0.67399 | 0.72222 | 0.032357 | 0.04823 | 6697.7793 | 3727.7601 | 28.5111

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | OB Prelim Test 2 |  |  | 2006-10-13 | 9:59
39003.4115 | 1 | 0 | 1 | XLPE | 7-C | Tray A | IRMS | 1
39003.4132 | 1 | 0 | 1 |  | 250 kW |  | Cable
39003.415 | 1 | 0 | 1
39003.4168 | 2537 | 0 | 1
39003.4186 | 2341 | 0 | 1
39003.4204 | 2526 | 0 | 1
39003.4222 | 2533 | 0 | 1
39003.4239 | 2276 | 0 | 1
39003.4257 | 1235 | 1174 | 1
1
39003.4115 | 1 | 0 | 2
39003.4133 | 1 | 0 | 2
39003.415 | 1 | 0 | 2
39003.4168 | 2336 | 0 | 2
39003.4186 | 2152 | 0 | 2
39003.4204 | 2116 | 0 | 2
39003.4222 | 2350 | 0 | 2
39003.4239 | 2443 | 0 | 2
39003.4257 | 951 | 944 | 2
2
39003.4115 | 1 | 0 | 3
39003.4133 | 1 | 0 | 3
39003.4151 | 1 | 0 | 3
39003.4168 | 2195 | 0 | 3
39003.4186 | 2090 | 0 | 3
39003.4204 | 2543 | 0 | 3
39003.4222 | 2538 | 0 | 3
39003.424 | 2415 | 0 | 3
39003.4258 | 989 | 948 | 3
3
39003.4115 | 1 | 0 | 4
39003.4133 | 1 | 0 | 4
39003.4151 | 1 | 0 | 4
39003.4169 | 2450 | 0 | 4
39003.4186 | 2169 | 0 | 4
39003.4204 | 2013 | 0 | 4
39003.4222 | 2553 | 0 | 4
39003.424 | 2023 | 0 | 4
39003.4258 | 1114 | 1071 | 4
4
39003.4115 | 1 | 0 | 5
39003.4133 | 1 | 0 | 5
39003.4151 | 1 | 0 | 5
39003.4169 | 2281 | 0 | 5
39003.4187 | 2414 | 0 | 5
39003.4204 | 2202 | 0 | 5
39003.4222 | 2362 | 0 | 5
39003.424 | 2351 | 0 | 5
39003.4258 | 1098 | 1057 | 5
5
39003.4115 | 1 | 0 | 6
39003.4133 | 1 | 0 | 6
39003.4151 | 337 | 0 | 6
39003.4169 | 2346 | 0 | 6
39003.4187 | 2188 | 0 | 6
39003.4205 | 2404 | 0 | 6
39003.4222 | 2185 | 0 | 6
39003.424 | 2163 | 0 | 6
39003.4258 | 985 | 946 | 6
6
39003.4116 | 1 | 0 | 7
39003.4133 | 1 | 0 | 7
39003.4151 | 1 | 0 | 7
39003.4169 | 2238 | 0 | 7
39003.4187 | 2136 | 0 | 7
39003.4205 | 2298 | 0 | 7
39003.4222 | 2052 | 0 | 7
39003.424 | 2475 | 0 | 7
39003.4258 | 1756 | 0 | 7
7
39003.4116 | 1 | 0 | 8
39003.4134 | 1 | 0 | 8
39003.4151 | 1 | 0 | 8
39003.4169 | 2046 | 0 | 8
39003.4187 | 2333 | 0 | 8
39003.4205 | 2220 | 0 | 8
39003.4223 | 2349 | 0 | 8
39003.4241 | 2391 | 0 | 8
39003.4258 | 866 | 0 | 8
8
39003.4116 | 1 | 0 | 9
39003.4134 | 1 | 0 | 9
39003.4152 | 1 | 1 | 9
39003.4169 | 2575 | 0 | 9
39003.4187 | 2535 | 0 | 9
39003.4205 | 2178 | 0 | 9
39003.4223 | 2564 | 0 | 9
39003.4241 | 2028 | 0 | 9
39003.4258 | 1675 | 0 | 9
9
39003.4116 | 0 | 0 | 10
39003.4134 | 1 | 0 | 10
39003.4152 | 996 | 0 | 10
39003.417 | 2560 | 0 | 10
39003.4187 | 2026 | 0 | 10
39003.4205 | 2182 | 0 | 10
39003.4223 | 1973 | 0 | 10
39003.4241 | 2097 | 0 | 10
39003.4259 | 857 | 0 | 10
10
39003.4116 | 1 | 0 | 11
39003.4134 | 1 | 0 | 11
39003.4152 | 1 | 0 | 11
39003.417 | 2255 | 0 | 11
39003.4187 | 2582 | 0 | 11
39003.4205 | 2593 | 0 | 11
39003.4223 | 2602 | 0 | 11
39003.4241 | 2534 | 0 | 11
39003.4259 | 1674 | 0 | 11
11
39003.4116 | 1 | 0 | 12
39003.4134 | 1 | 0 | 12
39003.4152 | 797 | 0 | 12
39003.417 | 2202 | 0 | 12
39003.4188 | 2118 | 0 | 12
39003.4206 | 2296 | 0 | 12
39003.4223 | 2463 | 0 | 12
39003.4241 | 2045 | 0 | 12
39003.4259 | 1 | 0 | 12
12
39003.4117 | 1 | 0 | 13
39003.4134 | 1 | 0 | 13
39003.4152 | 1 | 0 | 13
39003.417 | 2469 | 0 | 13
39003.4188 | 2257 | 0 | 13
39003.4206 | 2586 | 0 | 13
39003.4223 | 2037 | 0 | 13
39003.4241 | 2167 | 0 | 13
39003.4259 | 1279 | 0 | 13
13
39003.4117 | 1 | 0 | 14
39003.4134 | 1 | 0 | 14
39003.4152 | 871 | 0 | 14
39003.417 | 2496 | 0 | 14
39003.4188 | 2103 | 0 | 14
39003.4206 | 2224 | 0 | 14
39003.4224 | 2565 | 0 | 14
39003.4241 | 2037 | 0 | 14
39003.4259 | 1 | 0 | 14
14
39003.4117 | 1 | 0 | 15
39003.4135 | 0 | 0 | 15
39003.4153 | 1 | 0 | 15
39003.417 | 2243 | 0 | 15
39003.4188 | 2097 | 0 | 15
39003.4206 | 2163 | 0 | 15
39003.4224 | 2097 | 0 | 15
39003.4242 | 2314 | 0 | 15
39003.4259 | 537 | 0 | 15
15
39003.4117 | 1 | 0 | 16
39003.4135 | 1 | 0 | 16
39003.4153 | 1065 | 0 | 16
39003.417 | 2242 | 0 | 16
39003.4188 | 2301 | 0 | 16
39003.4206 | 2189 | 0 | 16
39003.4224 | 2196 | 0 | 16
39003.4242 | 2047 | 0 | 16
39003.426 | 1 | 0 | 16
16
39003.4117 | 1 | 0 | 17
39003.4135 | 1 | 0 | 17
39003.4153 | 3 | 0 | 17
39003.4171 | 2313 | 0 | 17
39003.4189 | 2433 | 0 | 17
39003.4206 | 2583 | 0 | 17
39003.4224 | 2179 | 0 | 17
39003.4242 | 2012 | 0 | 17
39003.426 | 725 | 0 | 17
17
39003.4117 | 1 | 0 | 18
39003.4135 | 1 | 0 | 18
39003.4153 | 1654 | 0 | 18
39003.4171 | 2201 | 0 | 18
39003.4189 | 2268 | 0 | 18
39003.4206 | 2063 | 0 | 18
39003.4224 | 2318 | 0 | 18
39003.4242 | 2287 | 0 | 18
39003.426 | 1 | 0 | 18
18
39003.4117 | 1 | 0 | 19
39003.4135 | 1 | 0 | 19
39003.4153 | 12 | 0 | 19
39003.4171 | 2454 | 0 | 19
39003.4189 | 2251 | 0 | 19
39003.4207 | 2187 | 0 | 19
39003.4224 | 2211 | 0 | 19
39003.4242 | 2074 | 0 | 19
39003.426 | 326 | 0 | 19
19
39003.4118 | 0 | 0 | 20
39003.4136 | 1 | 0 | 20
39003.4153 | 1397 | 0 | 20
39003.4171 | 2146 | 0 | 20
39003.4189 | 2304 | 0 | 20
39003.4207 | 1995 | 0 | 20
39003.4225 | 1972 | 0 | 20
39003.4242 | 2068 | 0 | 20
39003.426 | 1 | 0 | 20
20
39003.4118 | 1 | 0 | 21
39003.4136 | 1 | 0 | 21
39003.4153 | 206 | 0 | 21
39003.4171 | 2494 | 0 | 21
39003.4189 | 2199 | 0 | 21
39003.4207 | 2610 | 0 | 21
39003.4225 | 2261 | 0 | 21
39003.4243 | 2079 | 0 | 21
39003.426 | 1010 | 974 | 21
21
39003.4118 | 1 | 0 | 22
39003.4136 | 1 | 0 | 22
39003.4154 | 1 | 0 | 22
39003.4172 | 2216 | 0 | 22
39003.4189 | 2004 | 0 | 22
39003.4207 | 2064 | 0 | 22
39003.4225 | 2439 | 0 | 22
39003.4243 | 2594 | 0 | 22
39003.4261 | 1042 | 1078 | 22
22
39003.4118 | 1 | 0 | 23
39003.4136 | 1 | 0 | 23
39003.4154 | 230 | 51 | 23
39003.4172 | 2058 | 0 | 23
39003.4189 | 2283 | 0 | 23
39003.4207 | 2480 | 0 | 23
39003.4225 | 2199 | 0 | 23
39003.4243 | 2480 | 0 | 23
39003.4261 | 959 | 926 | 23
23
39003.4118 | 1 | 0 | 24
39003.4136 | 1 | 0 | 24
39003.4154 | 285 | 0 | 24
39003.4172 | 2592 | 0 | 24
39003.419 | 2456 | 0 | 24
39003.4207 | 2146 | 0 | 24
39003.4225 | 2052 | 0 | 24
39003.4243 | 2378 | 0 | 24
39003.4261 | 1058 | 1022 | 24
24
39003.4119 | 1 | 0 | 25
39003.4136 | 1 | 0 | 25
39003.4154 | 474 | 0 | 25
39003.4172 | 2412 | 0 | 25
39003.419 | 2339 | 0 | 25
39003.4208 | 2365 | 0 | 25
39003.4225 | 2032 | 0 | 25
39003.4243 | 2269 | 0 | 25
39003.4261 | 886 | 0 | 25
25
39003.4119 | 1 | 0 | 26
39003.4136 | 1 | 0 | 26
39003.4154 | 1793 | 0 | 26
39003.4172 | 2246 | 0 | 26
39003.419 | 2506 | 0 | 26
39003.4208 | 2088 | 0 | 26
39003.4226 | 1965 | 0 | 26
39003.4243 | 1868 | 0 | 26
39003.4261 | 1 | 0 | 26
26
39003.4119 | 1 | 0 | 27
39003.4137 | 1 | 0 | 27
39003.4155 | 633 | 0 | 27
39003.4172 | 2227 | 0 | 27
39003.419 | 2216 | 0 | 27
39003.4208 | 2067 | 0 | 27
39003.4226 | 2216 | 0 | 27
39003.4244 | 2004 | 0 | 27
39003.4261 | 401 | 0 | 27
27
39003.4119 | 1 | 0 | 28
39003.4137 | 1 | 0 | 28
39003.4155 | 1636 | 0 | 28
39003.4172 | 2056 | 0 | 28
39003.419 | 2117 | 0 | 28
39003.4208 | 2151 | 0 | 28
39003.4226 | 2437 | 0 | 28
39003.4244 | 2015 | 0 | 28
39003.4262 | 1 | 0 | 28
28
39003.4119 | 1 | 0 | 29
39003.4137 | 1 | 0 | 29
39003.4155 | 1053 | 0 | 29
39003.4173 | 2574 | 0 | 29
39003.419 | 2360 | 0 | 29
39003.4208 | 2416 | 0 | 29
39003.4226 | 2265 | 0 | 29
39003.4244 | 2298 | 0 | 29
39003.4262 | 597 | 0 | 29
29
39003.4119 | 1 | 0 | 30
39003.4137 | 1 | 0 | 30
39003.4155 | 1647 | 0 | 30
39003.4173 | 2074 | 0 | 30
39003.4191 | 2104 | 0 | 30
39003.4208 | 2537 | 0 | 30
39003.4226 | 2034 | 0 | 30
39003.4244 | 2310 | 0 | 30
39003.4262 | 1 | 0 | 30
30
39003.4119 | 1 | 0 | 31
39003.4137 | 1 | 0 | 31
39003.4155 | 1394 | 0 | 31
39003.4173 | 2590 | 0 | 31
39003.4191 | 2399 | 0 | 31
39003.4209 | 2544 | 0 | 31
39003.4226 | 2377 | 0 | 31
39003.4244 | 2324 | 0 | 31
39003.4262 | 1792 | 0 | 31
31
39003.412 | 1 | 0 | 32
39003.4137 | 1 | 0 | 32
39003.4155 | 1895 | 0 | 32
39003.4173 | 2372 | 0 | 32
39003.4191 | 2419 | 0 | 32
39003.4209 | 2140 | 0 | 32
39003.4227 | 2547 | 0 | 32
39003.4244 | 2239 | 0 | 32
39003.4262 | 1 | 0 | 32
32
39003.412 | 1 | 0 | 33
39003.4138 | 0 | 0 | 33
39003.4155 | 1140 | 0 | 33
39003.4173 | 2243 | 0 | 33
39003.4191 | 2043 | 0 | 33
39003.4209 | 2048 | 0 | 33
39003.4227 | 2430 | 0 | 33
39003.4245 | 2580 | 0 | 33
39003.4262 | 659 | 0 | 33
33
39003.412 | 1 | 0 | 34
39003.4138 | 1 | 0 | 34
39003.4156 | 1783 | 0 | 34
39003.4173 | 2006 | 0 | 34
39003.4191 | 2273 | 0 | 34
39003.4209 | 2122 | 0 | 34
39003.4227 | 2400 | 0 | 34
39003.4245 | 2090 | 0 | 34
39003.4262 | 0 | 0 | 34
34
39003.412 | 1 | 0 | 35
39003.4138 | 1 | 0 | 35
39003.4156 | 1528 | 0 | 35
39003.4174 | 2341 | 0 | 35
39003.4191 | 2314 | 1 | 35
39003.4209 | 2148 | 0 | 35
39003.4227 | 2113 | 0 | 35
39003.4245 | 2089 | 0 | 35
39003.4263 | 2 | 0 | 35
35
39003.412 | 1 | 0 | 36
39003.4138 | 1 | 0 | 36
39003.4156 | 1865 | 0 | 36
39003.4174 | 2045 | 0 | 36
39003.4192 | 2553 | 0 | 36
39003.4209 | 2171 | 0 | 36
39003.4227 | 1995 | 0 | 36
39003.4245 | 1930 | 0 | 36
39003.4263 | 1 | 0 | 36
36
39003.412 | 1 | 0 | 37
39003.4138 | 0 | 0 | 37
39003.4156 | 1632 | 0 | 37
39003.4174 | 2590 | 0 | 37
39003.4192 | 2510 | 0 | 37
39003.421 | 2617 | 0 | 37
39003.4227 | 2151 | 0 | 37
39003.4245 | 2575 | 0 | 37
39003.4263 | 1 | 0 | 37
37
39003.4121 | 1 | 0 | 38
39003.4138 | 1 | 0 | 38
39003.4156 | 1919 | 0 | 38
39003.4174 | 2526 | 0 | 38
39003.4192 | 2241 | 0 | 38
39003.421 | 2234 | 0 | 38
39003.4228 | 2068 | 0 | 38
39003.4245 | 2162 | 0 | 38
39003.4263 | 0 | 0 | 38
38
39003.4121 | 1 | 0 | 39
39003.4139 | 1 | 0 | 39
39003.4156 | 41 | 0 | 39
39003.4174 | 2136 | 0 | 39
39003.4192 | 2129 | 0 | 39
39003.421 | 2212 | 0 | 39
39003.4228 | 2356 | 0 | 39
39003.4245 | 2549 | 0 | 39
39003.4263 | 1112 | 1082 | 39
39
39003.4121 | 1 | 0 | 40
39003.4139 | 1 | 0 | 40
39003.4157 | 1966 | 0 | 40
39003.4174 | 2073 | 0 | 40
39003.4192 | 2591 | 0 | 40
39003.421 | 2409 | 0 | 40
39003.4228 | 2477 | 0 | 40
39003.4246 | 2025 | 0 | 40
39003.4264 | 1194 | 1167 | 40
40
39003.4121 | 0 | 0 | 41
39003.4139 | 0 | 0 | 41
39003.4157 | 91 | 0 | 41
39003.4175 | 2473 | 0 | 41
39003.4192 | 2547 | 0 | 41
39003.421 | 2135 | 0 | 41
39003.4228 | 2571 | 0 | 41
39003.4246 | 2119 | 0 | 41
39003.4264 | 1 | 0 | 41
41
39003.4121 | 1 | 0 | 42
39003.4139 | 1 | 0 | 42
39003.4157 | 1753 | 0 | 42
39003.4175 | 2324 | 0 | 42
39003.4193 | 2497 | 0 | 42
39003.421 | 2058 | 0 | 42
39003.4228 | 2014 | 0 | 42
39003.4246 | 2142 | 0 | 42
39003.4264 | 1 | 0 | 42
42
39003.4121 | 1 | 0 | 43
39003.4139 | 1 | 0 | 43
39003.4157 | 776 | 0 | 43
39003.4175 | 2553 | 0 | 43
39003.4193 | 2074 | 0 | 43
39003.4211 | 2346 | 0 | 43
39003.4228 | 2281 | 0 | 43
39003.4246 | 2563 | 0 | 43
39003.4264 | 1 | 0 | 43
43
39003.4122 | 1 | 0 | 44
39003.4139 | 1 | 0 | 44
39003.4157 | 1995 | 0 | 44
39003.4175 | 2527 | 0 | 44
39003.4193 | 2244 | 0 | 44
39003.4211 | 1994 | 0 | 44
39003.4228 | 2461 | 0 | 44
39003.4246 | 2014 | 0 | 44
39003.4264 | 1 | 0 | 44
44
39003.4122 | 1 | 0 | 45
39003.414 | 1 | 0 | 45
39003.4157 | 1581 | 0 | 45
39003.4175 | 2106 | 0 | 45
39003.4193 | 2390 | 0 | 45
39003.4211 | 2552 | 0 | 45
39003.4229 | 2481 | 0 | 45
39003.4247 | 2096 | 0 | 45
39003.4264 | 1577 | 0 | 45
45
39003.4122 | 1 | 0 | 46
39003.414 | 1 | 0 | 46
39003.4158 | 1813 | 0 | 46
39003.4175 | 2076 | 1 | 46
39003.4193 | 2465 | 0 | 46
39003.4211 | 2165 | 0 | 46
39003.4229 | 2114 | 0 | 46
39003.4247 | 1811 | 0 | 46
39003.4264 | 1 | 0 | 46
46
39003.4122 | 1 | 0 | 47
39003.414 | 1 | 0 | 47
39003.4158 | 1714 | 0 | 47
39003.4176 | 2597 | 0 | 47
39003.4193 | 2329 | 0 | 47
39003.4211 | 2101 | 0 | 47
39003.4229 | 2610 | 0 | 47
39003.4247 | 2180 | 0 | 47
39003.4265 | 1 | 0 | 47
47
39003.4122 | 1 | 0 | 48
39003.414 | 1 | 0 | 48
39003.4158 | 1836 | 0 | 48
39003.4176 | 2474 | 0 | 48
39003.4194 | 1977 | 0 | 48
39003.4211 | 2002 | 0 | 48
39003.4229 | 2217 | 0 | 48
39003.4247 | 2204 | 0 | 48
39003.4265 | 1 | 0 | 48
48
39003.4122 | 1 | 0 | 49
39003.414 | 1 | 0 | 49
39003.4158 | 2337 | 0 | 49
39003.4176 | 2287 | 0 | 49
39003.4194 | 2391 | 0 | 49
39003.4211 | 2613 | 0 | 49
39003.4229 | 2460 | 0 | 49
39003.4247 | 2346 | 0 | 49
39003.4265 | 1 | 0 | 49
49
39003.4123 | 1 | 0 | 50
39003.414 | 1 | 0 | 50
39003.4158 | 2150 | 0 | 50
39003.4176 | 2131 | 1 | 50
39003.4194 | 2436 | 0 | 50
39003.4212 | 2037 | 0 | 50
39003.423 | 2532 | 0 | 50
39003.4247 | 1827 | 0 | 50
39003.4265 | 1 | 0 | 50
50
39003.4123 | 1 | 0 | 51
39003.4141 | 1 | 0 | 51
39003.4158 | 2015 | 0 | 51
39003.4176 | 2509 | 0 | 51
39003.4194 | 2600 | 0 | 51
39003.4212 | 2256 | 0 | 51
39003.423 | 2260 | 0 | 51
39003.4247 | 2505 | 0 | 51
39003.4265 | 1873 | 0 | 51
51
39003.4123 | 1 | 0 | 52
39003.4141 | 1 | 0 | 52
39003.4159 | 2243 | 0 | 52
39003.4176 | 2526 | 0 | 52
39003.4194 | 2185 | 0 | 52
39003.4212 | 1967 | 0 | 52
39003.423 | 2225 | 0 | 52
39003.4248 | 1912 | 0 | 52
39003.4265 | 1 | 0 | 52
52
39003.4123 | 1 | 0 | 53
39003.4141 | 1 | 0 | 53
39003.4159 | 2229 | 0 | 53
39003.4177 | 2447 | 0 | 53
39003.4194 | 2546 | 0 | 53
39003.4212 | 2571 | 0 | 53
39003.423 | 2010 | 0 | 53
39003.4248 | 2305 | 0 | 53
39003.4266 | 1 | 0 | 53
53
39003.4123 | 1 | 0 | 54
39003.4141 | 1 | 0 | 54
39003.4159 | 2235 | 0 | 54
39003.4177 | 2246 | 0 | 54
39003.4194 | 2434 | 0 | 54
39003.4212 | 2366 | 0 | 54
39003.423 | 2224 | 0 | 54
39003.4248 | 2031 | 0 | 54
39003.4266 | 1 | 0 | 54
54
39003.4123 | 1 | 0 | 55
39003.4141 | 1 | 0 | 55
39003.4159 | 2378 | 0 | 55
39003.4177 | 2368 | 0 | 55
39003.4195 | 2192 | 0 | 55
39003.4212 | 2131 | 0 | 55
39003.423 | 2441 | 0 | 55
39003.4248 | 1998 | 0 | 55
39003.4266 | 1 | 0 | 55
55
39003.4123 | 1 | 0 | 56
39003.4141 | 1 | 0 | 56
39003.4159 | 2354 | 0 | 56
39003.4177 | 2574 | 0 | 56
39003.4195 | 2246 | 0 | 56
39003.4213 | 2012 | 0 | 56
39003.423 | 2475 | 0 | 56
39003.4248 | 2329 | 0 | 56
39003.4266 | 1 | 0 | 56
56
39003.4124 | 1 | 0 | 57
39003.4142 | 1 | 0 | 57
39003.4159 | 2133 | 0 | 57
39003.4177 | 2149 | 0 | 57
39003.4195 | 2561 | 0 | 57
39003.4213 | 2559 | 0 | 57
39003.4231 | 2547 | 0 | 57
39003.4248 | 2236 | 0 | 57
39003.4266 | 1 | 0 | 57
57
39003.4124 | 1 | 0 | 58
39003.4142 | 1 | 0 | 58
39003.4159 | 2488 | 0 | 58
39003.4177 | 2572 | 0 | 58
39003.4195 | 2551 | 0 | 58
39003.4213 | 2413 | 0 | 58
39003.4231 | 2277 | 0 | 58
39003.4266 | 1 | 0 | 58
58
39003.4124 | 1 | 0 | 59
39003.4142 | 1 | 0 | 59
39003.416 | 2408 | 0 | 59
39003.4177 | 2552 | 0 | 59
39003.4195 | 2533 | 0 | 59
39003.4213 | 2382 | 0 | 59
39003.4231 | 2603 | 0 | 59
39003.4249 | 2370 | 0 | 59
39003.4267 | 1 | 0 | 59
59
39003.4124 | 1 | 0 | 60
39003.4142 | 1 | 0 | 60
39003.416 | 2038 | 0 | 60
39003.4178 | 2001 | 0 | 60
39003.4195 | 2564 | 0 | 60
39003.4213 | 2009 | 0 | 60
39003.4231 | 1993 | 0 | 60
39003.4249 | 2319 | 0 | 60
39003.4267 | 1 | 0 | 60
60
39003.4124 | 1 | 0 | 61
39003.4142 | 1 | 0 | 61
39003.416 | 2190 | 0 | 61
39003.4178 | 2542 | 0 | 61
39003.4196 | 2575 | 0 | 61
39003.4213 | 2284 | 0 | 61
39003.4231 | 2092 | 0 | 61
39003.4249 | 1731 | 0 | 61
39003.4267 | 1 | 0 | 61
61
39003.4125 | 0 | 0 | 62
39003.4142 | 1 | 0 | 62
39003.416 | 2455 | 0 | 62
39003.4178 | 2442 | 0 | 62
39003.4196 | 2491 | 0 | 62
39003.4214 | 2526 | 0 | 62
39003.4231 | 2002 | 0 | 62
39003.4249 | 2301 | 0 | 62
39003.4267 | 1 | 0 | 62
62
39003.4125 | 1 | 0 | 63
39003.4142 | 0 | 0 | 63
39003.416 | 1939 | 0 | 63
39003.4178 | 2344 | 0 | 63
39003.4196 | 2284 | 0 | 63
39003.4214 | 2395 | 0 | 63
39003.4232 | 2179 | 0 | 63
39003.4249 | 2187 | 0 | 63
39003.4267 | 1 | 0 | 63
63
39003.4125 | 1 | 0 | 64
39003.4143 | 1 | 0 | 64
39003.416 | 2091 | 0 | 64
39003.4178 | 2012 | 0 | 64
39003.4196 | 2137 | 0 | 64
39003.4214 | 2264 | 0 | 64
39003.4232 | 2444 | 0 | 64
39003.425 | 1890 | 0 | 64
39003.4267 | 1 | 0 | 64
64
39003.4125 | 1 | 0 | 65
39003.4143 | 1 | 0 | 65
39003.4161 | 1872 | 0 | 65
39003.4178 | 2595 | 0 | 65
39003.4196 | 2147 | 0 | 65
39003.4214 | 2039 | 0 | 65
39003.4232 | 2086 | 0 | 65
39003.425 | 1671 | 0 | 65
39003.4268 | 1 | 0 | 65
65
39003.4125 | 1 | 0 | 66
39003.4143 | 1 | 0 | 66
39003.4161 | 2536 | 0 | 66
39003.4179 | 2352 | 0 | 66
39003.4196 | 2158 | 0 | 66
39003.4214 | 2207 | 0 | 66
39003.4232 | 2073 | 0 | 66
39003.425 | 1569 | 0 | 66
39003.4268 | 1 | 0 | 66
66
39003.4125 | 1 | 0 | 67
39003.4143 | 1 | 0 | 67
39003.4161 | 2379 | 0 | 67
39003.4179 | 2318 | 0 | 67
39003.4197 | 2071 | 0 | 67
39003.4214 | 2266 | 0 | 67
39003.4232 | 2349 | 0 | 67
39003.425 | 1898 | 0 | 67
39003.4268 | 1 | 0 | 67
67
39003.4125 | 1 | 0 | 68
39003.4143 | 1 | 0 | 68
39003.4161 | 2384 | 0 | 68
39003.4179 | 2163 | 0 | 68
39003.4197 | 2303 | 0 | 68
39003.4215 | 2275 | 0 | 68
39003.4232 | 2157 | 0 | 68
39003.425 | 1812 | 0 | 68
39003.4268 | 1 | 0 | 68
68
39003.4126 | 1 | 0 | 69
39003.4143 | 1 | 0 | 69
39003.4161 | 2040 | 0 | 69
39003.4179 | 2192 | 0 | 69
39003.4197 | 2356 | 0 | 69
39003.4215 | 2553 | 0 | 69
39003.4233 | 2409 | 0 | 69
39003.425 | 948 | 962 | 69
39003.4268 | 1096 | 1149 | 69
69
39003.4126 | 1 | 0 | 70
39003.4144 | 0 | 0 | 70
39003.4161 | 2228 | 0 | 70
39003.4179 | 2456 | 0 | 70
39003.4197 | 2097 | 0 | 70
39003.4215 | 2565 | 0 | 70
39003.4233 | 2443 | 1 | 70
39003.4251 | 1072 | 1033 | 70
39003.4268 | 1104 | 1183 | 70
70
39003.4126 | 1 | 0 | 71
39003.4144 | 1 | 0 | 71
39003.4162 | 2453 | 0 | 71
39003.4179 | 2546 | 0 | 71
39003.4197 | 2082 | 0 | 71
39003.4215 | 2134 | 0 | 71
39003.4233 | 2455 | 0 | 71
39003.4251 | 1146 | 1191 | 71
39003.4269 | 1069 | 1119 | 71
71
39003.4126 | 1 | 0 | 72
39003.4144 | 1 | 0 | 72
39003.4162 | 2106 | 0 | 72
39003.418 | 2256 | 0 | 72
39003.4197 | 2199 | 0 | 72
39003.4215 | 2459 | 0 | 72
39003.4233 | 1962 | 0 | 72
39003.4251 | 1059 | 1023 | 72
39003.4269 | 956 | 933 | 72
72
39003.4126 | 1 | 0 | 73
39003.4144 | 1 | 0 | 73
39003.4162 | 2098 | 0 | 73
39003.418 | 2475 | 0 | 73
39003.4198 | 2510 | 0 | 73
39003.4215 | 2511 | 0 | 73
39003.4233 | 2476 | 0 | 73
39003.4251 | 991 | 955 | 73
39003.4269 | 992 | 969 | 73
73
39003.4126 | 1 | 0 | 74
39003.4144 | 1 | 0 | 74
39003.4162 | 2533 | 0 | 74
39003.418 | 2489 | 0 | 74
39003.4198 | 2089 | 0 | 74
39003.4216 | 2456 | 1 | 74
39003.4233 | 2285 | 0 | 74
39003.4251 | 948 | 946 | 74
39003.4269 | 1161 | 1209 | 74
74
39003.4127 | 1 | 0 | 75
39003.4162 | 2191 | 0 | 75
39003.418 | 2202 | 0 | 75
39003.4198 | 2373 | 0 | 75
39003.4216 | 2272 | 0 | 75
39003.4234 | 2233 | 0 | 75
39003.4251 | 1033 | 998 | 75
39003.4269 | 1031 | 1007 | 75
75
39003.4127 | 1 | 0 | 76
39003.4145 | 1 | 0 | 76
39003.4162 | 2227 | 0 | 76
39003.418 | 2065 | 0 | 76
39003.4198 | 2280 | 0 | 76
39003.4216 | 2050 | 0 | 76
39003.4234 | 2056 | 0 | 76
39003.4252 | 944 | 998 | 76
39003.4269 | 1028 | 1075 | 76
76
39003.4127 | 1 | 0 | 77
39003.4145 | 1 | 0 | 77
39003.4163 | 2377 | 0 | 77
39003.418 | 2530 | 0 | 77
39003.4198 | 2159 | 0 | 77
39003.4216 | 2490 | 0 | 77
39003.4234 | 2192 | 0 | 77
39003.4252 | 1225 | 1194 | 77
39003.427 | 958 | 936 | 77
77
39003.4127 | 1 | 0 | 78
39003.4145 | 0 | 0 | 78
39003.4163 | 2017 | 0 | 78
39003.4181 | 2197 | 0 | 78
39003.4198 | 2458 | 0 | 78
39003.4216 | 2427 | 0 | 78
39003.4234 | 2160 | 0 | 78
39003.4252 | 1078 | 945 | 78
39003.427 | 983 | 961 | 78
78
39003.4127 | 0 | 0 | 79
39003.4145 | 0 | 0 | 79
39003.4163 | 2317 | 0 | 79
39003.4181 | 2078 | 0 | 79
39003.4198 | 2572 | 0 | 79
39003.4216 | 2384 | 0 | 79
39003.4234 | 1988 | 1 | 79
39003.4252 | 1029 | 1065 | 79
39003.427 | 1071 | 1123 | 79
79
39003.4127 | 1 | 0 | 80
39003.4145 | 1 | 0 | 80
39003.4163 | 2428 | 0 | 80
39003.4181 | 2549 | 0 | 80
39003.4199 | 2295 | 0 | 80
39003.4217 | 2239 | 0 | 80
39003.4234 | 2434 | 2 | 80
39003.4252 | 951 | 925 | 80
39003.427 | 1192 | 1169 | 80
80
39003.4128 | 1 | 0 | 81
39003.4145 | 1 | 0 | 81
39003.4163 | 2311 | 0 | 81
39003.4181 | 2157 | 0 | 81
39003.4199 | 2532 | 0 | 81
39003.4217 | 2229 | 0 | 81
39003.4234 | 2007 | 1 | 81
39003.4252 | 1023 | 989 | 81
39003.427 | 1027 | 1004 | 81
81
39003.4128 | 1 | 0 | 82
39003.4146 | 1 | 0 | 82
39003.4163 | 2173 | 0 | 82
39003.4181 | 2425 | 0 | 82
39003.4199 | 2462 | 0 | 82
39003.4217 | 2505 | 0 | 82
39003.4235 | 2018 | 0 | 82
39003.4253 | 990 | 958 | 82
39003.427 | 1180 | 1157 | 82
82
39003.4128 | 1 | 0 | 83
39003.4146 | 1 | 0 | 83
39003.4164 | 2273 | 0 | 83
39003.4181 | 2448 | 0 | 83
39003.4199 | 2570 | 0 | 83
39003.4217 | 2546 | 0 | 83
39003.4235 | 2416 | 0 | 83
39003.4253 | 1060 | 1027 | 83
39003.427 | 1078 | 1053 | 83
83
39003.4128 | 1 | 0 | 84
39003.4146 | 1 | 0 | 84
39003.4164 | 2070 | 0 | 84
39003.4181 | 2094 | 0 | 84
39003.4199 | 2394 | 0 | 84
39003.4217 | 2118 | 0 | 84
39003.4235 | 2374 | 1 | 84
39003.4253 | 1185 | 1151 | 84
39003.4271 | 1210 | 1188 | 84
84
39003.4128 | 1 | 0 | 85
39003.4146 | 1 | 0 | 85
39003.4164 | 2168 | 0 | 85
39003.4182 | 2238 | 0 | 85
39003.42 | 2028 | 0 | 85
39003.4217 | 2028 | 0 | 85
39003.4235 | 2223 | 1 | 85
39003.4253 | 959 | 928 | 85
39003.4271 | 978 | 1091 | 85
85
39003.4128 | 1 | 0 | 86
39003.4146 | 1 | 0 | 86
39003.4164 | 2407 | 0 | 86
39003.4182 | 2498 | 0 | 86
39003.42 | 2001 | 0 | 86
39003.4217 | 2523 | 0 | 86
39003.4235 | 2005 | 2 | 86
39003.4253 | 1008 | 976 | 86
39003.4271 | 1128 | 1104 | 86
86
39003.4129 | 1 | 0 | 87
39003.4146 | 1 | 0 | 87
39003.4164 | 1980 | 0 | 87
39003.4182 | 1983 | 0 | 87
39003.42 | 2251 | 0 | 87
39003.4218 | 1989 | 0 | 87
39003.4236 | 2017 | 4 | 87
39003.4253 | 950 | 928 | 87
39003.4271 | 1217 | 975 | 87
87
39003.4129 | 1 | 0 | 88
39003.4147 | 1 | 0 | 88
39003.4164 | 2487 | 0 | 88
39003.4182 | 2518 | 0 | 88
39003.4218 | 2471 | 0 | 88
39003.4236 | 2444 | 9 | 88
39003.4253 | 1181 | 1148 | 88
39003.4271 | 1175 | 1215 | 88
88
39003.4129 | 1 | 0 | 89
39003.4147 | 1 | 0 | 89
39003.4164 | 1996 | 0 | 89
39003.4182 | 2350 | 0 | 89
39003.42 | 2027 | 0 | 89
39003.4218 | 2244 | 0 | 89
39003.4236 | 2327 | 9 | 89
39003.4254 | 1087 | 1056 | 89
39003.4271 | 1125 | 1196 | 89
89
39003.4129 | 1 | 0 | 90
39003.4147 | 1 | 0 | 90
39003.4165 | 2253 | 0 | 90
39003.4183 | 2134 | 0 | 90
39003.42 | 2341 | 0 | 90
39003.4218 | 2582 | 0 | 90
39003.4236 | 1797 | 91 | 90
39003.4254 | 1075 | 1044 | 90
39003.4272 | 1027 | 1005 | 90
90
39003.4129 | 1 | 0 | 91
39003.4147 | 1 | 0 | 91
39003.4165 | 2019 | 0 | 91
39003.4183 | 2452 | 0 | 91
39003.42 | 2539 | 0 | 91
39003.4218 | 2528 | 0 | 91
39003.4236 | 2054 | 87 | 91
39003.4254 | 1039 | 1079 | 91
39003.4272 | 946 | 944 | 91
91
39003.4129 | 1 | 0 | 92
39003.4147 | 1 | 0 | 92
39003.4165 | 2063 | 0 | 92
39003.4183 | 2569 | 0 | 92
39003.4201 | 2351 | 0 | 92
39003.4219 | 2518 | 0 | 92
39003.4236 | 1968 | 54 | 92
39003.4254 | 995 | 966 | 92
39003.4272 | 1201 | 1179 | 92
92
39003.413 | 1 | 0 | 93
39003.4147 | 6 | 0 | 93
39003.4165 | 2057 | 0 | 93
39003.4183 | 2062 | 0 | 93
39003.4201 | 2192 | 0 | 93
39003.4219 | 1987 | 0 | 93
39003.4236 | 1997 | 57 | 93
39003.4254 | 969 | 940 | 93
39003.4272 | 1126 | 1102 | 93
93
39003.413 | 1 | 0 | 94
39003.4147 | 0 | 0 | 94
39003.4165 | 2438 | 0 | 94
39003.4183 | 2248 | 0 | 94
39003.4201 | 2332 | 0 | 94
39003.4219 | 2162 | 0 | 94
39003.4237 | 2122 | 34 | 94
39003.4254 | 1172 | 1139 | 94
39003.4272 | 951 | 931 | 94
94
39003.413 | 1 | 0 | 95
39003.4148 | 1 | 0 | 95
39003.4166 | 2493 | 0 | 95
39003.4183 | 1998 | 0 | 95
39003.4201 | 2322 | 0 | 95
39003.4219 | 2310 | 0 | 95
39003.4237 | 2065 | 119 | 95
39003.4255 | 1111 | 1081 | 95
39003.4272 | 1039 | 1088 | 95
95
39003.413 | 1 | 0 | 96
39003.4148 | 1 | 0 | 96
39003.4166 | 2367 | 0 | 96
39003.4183 | 2537 | 0 | 96
39003.4201 | 2571 | 0 | 96
39003.4219 | 2101 | 0 | 96
39003.4237 | 2402 | 39 | 96
39003.4255 | 1050 | 1021 | 96
39003.4273 | 986 | 963 | 96
96
39003.413 | 1 | 0 | 97
39003.4148 | 1 | 0 | 97
39003.4166 | 2454 | 0 | 97
39003.4184 | 2439 | 0 | 97
39003.4202 | 2582 | 0 | 97
39003.4219 | 2120 | 0 | 97
39003.4237 | 2275 | 78 | 97
39003.4255 | 1167 | 1135 | 97
39003.4273 | 970 | 1085 | 97
97
39003.413 | 1 | 0 | 98
39003.4148 | 1 | 0 | 98
39003.4166 | 2379 | 0 | 98
39003.4184 | 2073 | 0 | 98
39003.4202 | 2517 | 0 | 98
39003.4219 | 2458 | 0 | 98
39003.4237 | 2425 | 11 | 98
39003.4255 | 984 | 1020 | 98
39003.4273 | 1030 | 1006 | 98
98
39003.413 | 1 | 0 | 99
39003.4148 | 5 | 0 | 99
39003.4166 | 2509 | 0 | 99
39003.4184 | 2235 | 0 | 99
39003.4202 | 2585 | 0 | 99
39003.422 | 2233 | 0 | 99
39003.4237 | 2398 | 11 | 99
39003.4255 | 949 | 931 | 99
39003.4273 | 960 | 938 | 99
99
39003.4131 | 1 | 0 | 100
39003.4148 | 4 | 0 | 100
39003.4166 | 2353 | 0 | 100
39003.4184 | 2417 | 0 | 100
39003.4202 | 2092 | 0 | 100
39003.422 | 2149 | 0 | 100
39003.4238 | 2447 | 9 | 100
39003.4255 | 972 | 1006 | 100
39003.4273 | 1119 | 946 | 100
100
39003.4131 | 1 | 0 | 101
39003.4149 | 96 | 0 | 101
39003.4166 | 2232 | 0 | 101
39003.4184 | 2409 | 0 | 101
39003.4202 | 2344 | 0 | 101
39003.422 | 2298 | 0 | 101
39003.4238 | 1902 | 8 | 101
39003.4256 | 1182 | 1150 | 101
39003.4273 | 1121 | 945 | 101
101
39003.4131 | 1 | 0 | 102
39003.4149 | 87 | 0 | 102
39003.4167 | 2004 | 0 | 102
39003.4184 | 1973 | 0 | 102
39003.4202 | 2429 | 0 | 102
39003.422 | 2505 | 0 | 102
39003.4238 | 2118 | 8 | 102
39003.4256 | 1133 | 1101 | 102
39003.4273 | 1182 | 1215 | 102
102
39003.4131 | 1 | 0 | 103
39003.4149 | 122 | 0 | 103
39003.4167 | 1984 | 0 | 103
39003.4185 | 2182 | 0 | 103
39003.4202 | 2382 | 0 | 103
39003.422 | 2400 | 0 | 103
39003.4238 | 2406 | 9 | 103
39003.4256 | 1188 | 1210 | 103
39003.4274 | 1009 | 987 | 103
103
39003.4131 | 1 | 0 | 104
39003.4149 | 15 | 0 | 104
39003.4167 | 2563 | 0 | 104
39003.4185 | 2087 | 0 | 104
39003.4203 | 2570 | 0 | 104
39003.422 | 2033 | 0 | 104
39003.4238 | 1968 | 8 | 104
39003.4256 | 1060 | 1031 | 104
39003.4274 | 1068 | 1045 | 104
104
39003.4131 | 1 | 0 | 105
39003.4149 | 628 | 345 | 105
39003.4167 | 2285 | 0 | 105
39003.4185 | 2445 | 0 | 105
39003.4203 | 2186 | 0 | 105
39003.4221 | 2142 | 0 | 105
39003.4238 | 2192 | 9 | 105
39003.4256 | 1211 | 931 | 105
39003.4274 | 1031 | 1078 | 105
105
39003.4132 | 1 | 0 | 106
39003.4149 | 944 | 686 | 106
39003.4167 | 2149 | 0 | 106
39003.4185 | 2100 | 0 | 106
39003.4203 | 2576 | 0 | 106
39003.4221 | 1990 | 0 | 106
39003.4239 | 1982 | 8 | 106
39003.4256 | 985 | 959 | 106
39003.4274 | 1058 | 1035 | 106
106
39003.4132 | 1 | 0 | 107
39003.415 | 194 | 0 | 107
39003.4167 | 2545 | 0 | 107
39003.4185 | 2465 | 0 | 107
39003.4203 | 2262 | 0 | 107
39003.4221 | 2404 | 0 | 107
39003.4239 | 1934 | 6 | 107
39003.4256 | 1045 | 1088 | 107
39003.4274 | 992 | 970 | 107
107
39003.4132 | 1 | 0 | 108
39003.415 | 325 | 0 | 108
39003.4168 | 2564 | 0 | 108
39003.4185 | 2577 | 0 | 108
39003.4203 | 2238 | 0 | 108
39003.4221 | 2090 | 0 | 108
39003.4239 | 2410 | 9 | 108
39003.4257 | 1220 | 1196 | 108
39003.4275 | 977 | 957 | 108
108
39003.4132 | 1 | 0 | 109
39003.415 | 441 | 0 | 109
39003.4168 | 1980 | 0 | 109
39003.4186 | 2329 | 0 | 109
39003.4203 | 2141 | 0 | 109
39003.4221 | 2518 | 0 | 109
39003.4239 | 2206 | 7 | 109
39003.4257 | 940 | 980 | 109
39003.4275 | 1142 | 1198 | 109
109
39003.4132 | 1 | 0 | 110
39003.415 | 553 | 13 | 110
39003.4168 | 2344 | 0 | 110
39003.4186 | 2307 | 0 | 110
39003.4204 | 2054 | 0 | 110
39003.4221 | 2321 | 0 | 110
39003.4239 | 2101 | 7 | 110
39003.4257 | 1007 | 1114 | 110
39003.4275 | 1099 | 1157 | 110
110

## Temperatures
DAQ Time | Burner Time | Cable center | Air above cable | Air below cable | TRAY A
0 | -220 | 16.8 | 16.2 | 16.4 | 17.8
1 | -219 | 16.8 | 16.2 | 16.4 | 17.8
2 | -218 | 16.8 | 16.2 | 16.4 | 17.8
3 | -217 | 16.8 | 16.2 | 16.4 | 17.8
4 | -216 | 16.8 | 16.2 | 16.4 | 17.8
5 | -215 | 16.8 | 16.2 | 16.4 | 17.8
6 | -214 | 16.8 | 16.2 | 16.4 | 17.8
7 | -213 | 16.8 | 16.2 | 16.4 | 17.8
8 | -212 | 16.8 | 16.2 | 16.4 | 17.8
9 | -211 | 16.8 | 16.2 | 16.4 | 17.8
10 | -210 | 16.8 | 16.2 | 16.4 | 17.8
11 | -209 | 16.8 | 16.2 | 16.4 | 17.8
12 | -208 | 16.8 | 16.2 | 16.4 | 17.8
13 | -207 | 16.8 | 16.2 | 16.4 | 17.8
14 | -206 | 16.8 | 16.2 | 16.4 | 17.8
15 | -205 | 16.8 | 16.2 | 16.4 | 17.8
16 | -204 | 16.8 | 16.2 | 16.4 | 17.8
17 | -203 | 16.8 | 16.2 | 16.4 | 17.8
18 | -202 | 16.8 | 16.2 | 16.4 | 17.8
19 | -201 | 16.8 | 16.2 | 16.4 | 17.8
20 | -200 | 16.8 | 16.2 | 16.4 | 17.8
21 | -199 | 16.8 | 16.2 | 16.4 | 17.8
22 | -198 | 16.8 | 16.2 | 16.4 | 17.8
23 | -197 | 16.8 | 16.2 | 16.4 | 17.8
24 | -196 | 16.8 | 16.2 | 16.4 | 17.8
25 | -195 | 16.8 | 16.2 | 16.4 | 17.8
26 | -194 | 16.8 | 16.2 | 16.4 | 17.8
27 | -193 | 16.8 | 16.2 | 16.4 | 17.8
28 | -192 | 16.8 | 16.2 | 16.4 | 17.8
29 | -191 | 16.8 | 16.2 | 16.4 | 17.8
30 | -190 | 16.8 | 16.2 | 16.4 | 17.8
31 | -189 | 16.8 | 16.2 | 16.4 | 17.8
32 | -188 | 16.8 | 16.2 | 16.4 | 17.8
33 | -187 | 16.8 | 16.2 | 16.4 | 17.8
34 | -186 | 16.8 | 16.2 | 16.4 | 17.8
35 | -185 | 16.8 | 16.2 | 16.4 | 17.8
36 | -184 | 16.8 | 16.2 | 16.4 | 17.8
37 | -183 | 16.8 | 16.2 | 16.4 | 17.8
38 | -182 | 16.8 | 16.2 | 16.4 | 17.8
39.2 | -180.8 | 16.8 | 16.2 | 16.4 | 17.8
40.2 | -179.8 | 16.8 | 16.2 | 16.4 | 17.8
41.2 | -178.8 | 16.8 | 16.2 | 16.4 | 17.8
42.2 | -177.8 | 16.8 | 16.2 | 16.4 | 17.8
43.2 | -176.8 | 16.8 | 16.2 | 16.4 | 17.8
44.2 | -175.8 | 16.8 | 16.2 | 16.4 | 17.8
45.2 | -174.8 | 16.8 | 16.2 | 16.4 | 17.8
46.2 | -173.8 | 16.8 | 16.2 | 16.4 | 17.8
47.2 | -172.8 | 16.8 | 16.2 | 16.4 | 17.8
48.2 | -171.8 | 16.8 | 16.2 | 16.4 | 17.8
49.2 | -170.8 | 16.8 | 16.2 | 16.4 | 17.8
50.2 | -169.8 | 16.8 | 16.2 | 16.5 | 17.8
51.2 | -168.8 | 16.8 | 16.2 | 16.5 | 17.8
52.2 | -167.8 | 16.8 | 16.2 | 16.4 | 17.8
53.2 | -166.8 | 16.8 | 16.2 | 16.4 | 17.8
54.2 | -165.8 | 16.8 | 16.2 | 16.5 | 17.8
55.2 | -164.8 | 16.8 | 16.2 | 16.5 | 17.8
56.2 | -163.8 | 16.8 | 16.2 | 16.5 | 17.8
57.2 | -162.8 | 16.8 | 16.2 | 16.5 | 17.8
58.2 | -161.8 | 16.8 | 16.2 | 16.4 | 17.8
59.2 | -160.8 | 16.8 | 16.2 | 16.5 | 17.8
60.2 | -159.8 | 16.8 | 16.2 | 16.5 | 17.8
61.2 | -158.8 | 16.8 | 16.2 | 16.5 | 17.8
62.2 | -157.8 | 16.8 | 16.2 | 16.5 | 17.8
63.2 | -156.8 | 16.8 | 16.2 | 16.5 | 17.8
64.2 | -155.8 | 16.8 | 16.2 | 16.5 | 17.8
65.2 | -154.8 | 16.8 | 16.2 | 16.5 | 17.8
66.2 | -153.8 | 16.8 | 16.2 | 16.5 | 17.8
67.2 | -152.8 | 16.8 | 16.2 | 16.5 | 17.8
68.2 | -151.8 | 16.8 | 16.2 | 16.5 | 17.8
69.2 | -150.8 | 16.8 | 16.2 | 16.5 | 17.8
70.2 | -149.8 | 16.8 | 16.2 | 16.5 | 17.8
71.2 | -148.8 | 16.8 | 16.2 | 16.5 | 17.8
72.2 | -147.8 | 16.8 | 16.2 | 16.5 | 17.8
73.2 | -146.8 | 16.8 | 16.2 | 16.5 | 17.8
74.2 | -145.8 | 16.8 | 16.2 | 16.5 | 17.8
75.2 | -144.8 | 16.8 | 16.2 | 16.5 | 17.8
76.2 | -143.8 | 16.8 | 16.2 | 16.5 | 17.8
77.2 | -142.8 | 16.8 | 16.2 | 16.5 | 17.8
78.2 | -141.8 | 16.8 | 16.2 | 16.5 | 17.8
79.2 | -140.8 | 16.8 | 16.2 | 16.5 | 17.8
80.2 | -139.8 | 16.8 | 16.2 | 16.5 | 17.8
81.2 | -138.8 | 16.8 | 16.2 | 16.5 | 17.8
82.2 | -137.8 | 16.8 | 16.2 | 16.5 | 17.8
83.2 | -136.8 | 16.8 | 16.2 | 16.5 | 17.8
84.2 | -135.8 | 16.8 | 16.2 | 16.5 | 17.8
85.2 | -134.8 | 16.8 | 16.2 | 16.5 | 17.8
86.2 | -133.8 | 16.8 | 16.2 | 16.5 | 17.8
87.2 | -132.8 | 16.8 | 16.2 | 16.5 | 17.8
88.2 | -131.8 | 16.8 | 16.2 | 16.5 | 17.8
89.2 | -130.8 | 16.8 | 16.2 | 16.5 | 17.8
90.2 | -129.8 | 16.8 | 16.2 | 16.5 | 17.8
91.2 | -128.8 | 16.8 | 16.2 | 16.4 | 17.8
92.2 | -127.8 | 16.8 | 16.2 | 16.5 | 17.8
93.2 | -126.8 | 16.8 | 16.2 | 16.4 | 17.8
94.2 | -125.8 | 16.8 | 16.2 | 16.5 | 17.8
95.2 | -124.8 | 16.8 | 16.2 | 16.4 | 17.8
96.2 | -123.8 | 16.8 | 16.2 | 16.4 | 17.8
97.2 | -122.8 | 16.8 | 16.2 | 16.4 | 17.8
98.2 | -121.8 | 16.8 | 16.2 | 16.5 | 17.8
99.2 | -120.8 | 16.8 | 16.2 | 16.5 | 17.8
100.2 | -119.8 | 16.8 | 16.2 | 16.5 | 17.8
101.2 | -118.8 | 16.8 | 16.2 | 16.5 | 17.8
102.2 | -117.8 | 16.8 | 16.2 | 16.5 | 17.8
103.2 | -116.8 | 16.8 | 16.2 | 16.5 | 17.8
104.2 | -115.8 | 16.8 | 16.2 | 16.5 | 17.8
105.2 | -114.8 | 16.8 | 16.2 | 16.5 | 17.8
106.2 | -113.8 | 16.8 | 16.2 | 16.5 | 17.8
107.2 | -112.8 | 16.8 | 16.2 | 16.5 | 17.8
108.2 | -111.8 | 16.8 | 16.2 | 16.5 | 17.8
109.2 | -110.8 | 16.8 | 16.2 | 16.5 | 17.8
110.2 | -109.8 | 16.8 | 16.2 | 16.5 | 17.8
111.2 | -108.8 | 16.8 | 16.2 | 16.5 | 17.8
112.2 | -107.8 | 16.8 | 16.2 | 16.5 | 17.8
113.2 | -106.8 | 16.8 | 16.2 | 16.5 | 17.8
114.2 | -105.8 | 16.8 | 16.2 | 16.5 | 17.8
115.2 | -104.8 | 16.8 | 16.2 | 16.5 | 17.8
116.2 | -103.8 | 16.8 | 16.2 | 16.5 | 17.8
117.2 | -102.8 | 16.8 | 16.2 | 16.5 | 17.8
118.2 | -101.8 | 16.8 | 16.2 | 16.5 | 17.8
119.2 | -100.8 | 16.8 | 16.2 | 16.5 | 17.8
120.2 | -99.8 | 16.8 | 16.2 | 16.5 | 17.8
121.2 | -98.8 | 16.8 | 16.2 | 16.5 | 17.8
122.2 | -97.8 | 16.8 | 16.2 | 16.5 | 17.8
123.2 | -96.8 | 16.8 | 16.2 | 16.5 | 17.8
124.2 | -95.8 | 16.8 | 16.2 | 16.5 | 17.8
125.2 | -94.8 | 16.8 | 16.2 | 16.5 | 17.8
126.2 | -93.8 | 16.8 | 16.2 | 16.5 | 17.8
127.2 | -92.8 | 16.8 | 16.2 | 16.5 | 17.8
128.2 | -91.8 | 16.8 | 16.2 | 16.5 | 17.8
129.2 | -90.8 | 16.8 | 16.2 | 16.5 | 17.8
130.2 | -89.8 | 16.8 | 16.2 | 16.5 | 17.8
131.2 | -88.8 | 16.8 | 16.2 | 16.5 | 17.8
132.2 | -87.8 | 16.8 | 16.2 | 16.5 | 17.8
133.2 | -86.8 | 16.8 | 16.2 | 16.5 | 17.8
134.2 | -85.8 | 16.8 | 16.2 | 16.4 | 17.8
135.2 | -84.8 | 16.8 | 16.2 | 16.5 | 17.8
136.2 | -83.8 | 16.8 | 16.2 | 16.5 | 17.8
137.2 | -82.8 | 16.8 | 16.2 | 16.5 | 17.8
138.2 | -81.8 | 16.8 | 16.2 | 16.4 | 17.8
139.2 | -80.8 | 16.8 | 16.2 | 16.5 | 17.8
140.2 | -79.8 | 16.8 | 16.2 | 16.5 | 17.8
141.2 | -78.8 | 16.8 | 16.2 | 16.4 | 17.8
142.2 | -77.8 | 16.8 | 16.2 | 16.5 | 17.8
143.2 | -76.8 | 16.8 | 16.2 | 16.5 | 17.8
144.2 | -75.8 | 16.8 | 16.2 | 16.5 | 17.8
145.2 | -74.8 | 16.8 | 16.2 | 16.5 | 17.8
146.2 | -73.8 | 16.8 | 16.2 | 16.5 | 17.8
147.2 | -72.8 | 16.8 | 16.2 | 16.5 | 17.8
148.2 | -71.8 | 16.8 | 16.2 | 16.5 | 17.8
149.2 | -70.8 | 16.8 | 16.2 | 16.5 | 17.8
150.2 | -69.8 | 16.8 | 16.2 | 16.5 | 17.8
151.2 | -68.8 | 16.8 | 16.2 | 16.5 | 17.8
152.2 | -67.8 | 16.8 | 16.2 | 16.5 | 17.8
153.2 | -66.8 | 16.8 | 16.2 | 16.5 | 17.8
154.2 | -65.8 | 16.8 | 16.2 | 16.5 | 17.8
155.2 | -64.8 | 16.8 | 16.2 | 16.5 | 17.8
156.2 | -63.8 | 16.8 | 16.2 | 16.5 | 17.8
157.2 | -62.8 | 16.8 | 16.2 | 16.5 | 17.8
158.2 | -61.8 | 16.8 | 16.2 | 16.5 | 17.8
159.2 | -60.8 | 16.8 | 16.2 | 16.5 | 17.8
160.2 | -59.8 | 16.8 | 16.2 | 16.5 | 17.8
161.2 | -58.8 | 16.8 | 16.2 | 16.5 | 17.8
162.2 | -57.8 | 16.8 | 16.2 | 16.5 | 17.8
163.2 | -56.8 | 16.8 | 16.2 | 16.5 | 17.8
164.2 | -55.8 | 16.8 | 16.2 | 16.5 | 17.8
165.2 | -54.8 | 16.8 | 16.2 | 16.5 | 17.8
166.2 | -53.8 | 16.8 | 16.2 | 16.5 | 17.8
167.2 | -52.8 | 16.8 | 16.2 | 16.5 | 17.8
168.2 | -51.8 | 16.8 | 16.2 | 16.5 | 17.8
169.2 | -50.8 | 16.8 | 16.2 | 16.5 | 17.8
170.2 | -49.8 | 16.8 | 16.2 | 16.5 | 17.8
171.2 | -48.8 | 16.8 | 16.2 | 16.5 | 17.8
172.2 | -47.8 | 16.8 | 16.2 | 16.5 | 17.8
173.2 | -46.8 | 16.8 | 16.2 | 16.5 | 17.8
174.2 | -45.8 | 16.8 | 16.2 | 16.5 | 17.8
175.2 | -44.8 | 16.8 | 16.2 | 16.5 | 17.8
176.2 | -43.8 | 16.8 | 16.2 | 16.5 | 17.8
177.2 | -42.8 | 16.8 | 16.2 | 16.5 | 17.8
178.2 | -41.8 | 16.8 | 16.2 | 16.5 | 17.8
179.2 | -40.8 | 16.8 | 16.2 | 16.5 | 17.8
180.2 | -39.8 | 16.8 | 16.2 | 16.5 | 17.8
181.2 | -38.8 | 16.8 | 16.2 | 16.5 | 17.8
182.2 | -37.8 | 16.8 | 16.2 | 16.5 | 17.8
183.2 | -36.8 | 16.8 | 16.2 | 16.5 | 17.8
184.2 | -35.8 | 16.8 | 16.2 | 16.5 | 17.8
185.2 | -34.8 | 16.8 | 16.2 | 16.5 | 17.8
186.2 | -33.8 | 16.8 | 16.2 | 16.5 | 17.8
187.2 | -32.8 | 16.8 | 16.2 | 16.5 | 17.8
188.2 | -31.8 | 16.8 | 16.2 | 16.5 | 17.8
189.2 | -30.8 | 16.8 | 16.2 | 16.5 | 17.8
190.2 | -29.8 | 16.8 | 16.2 | 16.5 | 17.8
191.2 | -28.8 | 16.8 | 16.2 | 16.5 | 17.8
192.2 | -27.8 | 16.8 | 16.2 | 16.5 | 17.8
193.2 | -26.8 | 16.8 | 16.2 | 16.5 | 17.8
194.2 | -25.8 | 16.8 | 16.2 | 16.5 | 17.8
195.2 | -24.8 | 16.8 | 16.2 | 16.5 | 17.8
196.2 | -23.8 | 16.8 | 16.2 | 16.5 | 17.8
197.2 | -22.8 | 16.8 | 16.2 | 16.5 | 17.8
198.2 | -21.8 | 16.8 | 16.2 | 16.5 | 17.8
199.2 | -20.8 | 16.8 | 16.2 | 16.5 | 17.8
200.2 | -19.8 | 16.8 | 16.2 | 16.5 | 17.8
201.2 | -18.8 | 16.8 | 16.3 | 16.5 | 17.8
202.2 | -17.8 | 16.8 | 16.2 | 16.5 | 17.8
203.2 | -16.8 | 16.8 | 16.2 | 16.5 | 17.8
204.2 | -15.8 | 16.8 | 16.2 | 16.5 | 17.8
205.2 | -14.8 | 16.8 | 16.3 | 16.5 | 17.8
206.2 | -13.8 | 16.8 | 16.3 | 16.5 | 17.8
207.2 | -12.8 | 16.8 | 16.3 | 16.5 | 17.8
208.2 | -11.8 | 16.8 | 16.3 | 16.5 | 17.8
209.2 | -10.8 | 16.8 | 16.3 | 16.5 | 17.8
210.2 | -9.8 | 16.8 | 16.3 | 16.5 | 17.8
211.2 | -8.8 | 16.8 | 16.3 | 16.5 | 17.8
212.2 | -7.8 | 16.8 | 16.3 | 16.5 | 17.8
213.2 | -6.8 | 16.8 | 16.2 | 16.5 | 17.8
214.2 | -5.8 | 16.8 | 16.3 | 16.5 | 17.8
215.2 | -4.8 | 16.8 | 16.3 | 16.5 | 17.8
216.2 | -3.8 | 16.8 | 16.3 | 16.5 | 17.8
217.2 | -2.8 | 16.8 | 16.3 | 16.5 | 17.8
218.2 | -1.8 | 16.8 | 16.3 | 16.5 | 17.8
219.2 | -0.8 | 16.8 | 16.3 | 16.6 | 17.8
220.2 | 0.2 | 16.8 | 16.3 | 16.6 | 17.8
221.2 | 1.2 | 16.8 | 16.3 | 16.6 | 17.9
222.2 | 2.2 | 16.8 | 16.3 | 16.6 | 17.9
223.2 | 3.2 | 16.8 | 16.7 | 18.1 | 18.1
224.2 | 4.2 | 16.8 | 21 | 29.8 | 21.3
225.2 | 5.2 | 16.9 | 31.3 | 51 | 29.8
226.2 | 6.2 | 16.8 | 48.3 | 80.1 | 40.1
227.2 | 7.2 | 16.9 | 68.2 | 122 | 54.4
228.2 | 8.2 | 17.1 | 92.2 | 153.6 | 65.8
229.2 | 9.2 | 17.4 | 112.9 | 185.1 | 81.1
230.2 | 10.2 | 17.9 | 143.7 | 238.9 | 109
231.2 | 11.2 | 18.6 | 173.5 | 276.5 | 133.2
232.2 | 12.2 | 19.4 | 199.3 | 301.7 | 144.8
233.2 | 13.2 | 20.4 | 203.5 | 310.9 | 159.8
234.2 | 14.2 | 21.7 | 215.2 | 345.9 | 184.5
235.2 | 15.2 | 23.1 | 242.2 | 387.7 | 205.5
236.2 | 16.2 | 24.7 | 279.2 | 392 | 200.9
237.2 | 17.2 | 26.4 | 314.4 | 401.5 | 188.6
238.2 | 18.2 | 28.4 | 346.9 | 441.1 | 199
239.2 | 19.2 | 30.6 | 371.5 | 488.9 | 228.2
240.2 | 20.2 | 33 | 396.8 | 518.3 | 246.9
241.2 | 21.2 | 35.7 | 436.8 | 540.4 | 250.5
242.2 | 22.2 | 38.6 | 464.4 | 546.6 | 249.3
243.2 | 23.2 | 41.7 | 500.3 | 566.4 | 255.2
244.2 | 24.2 | 45 | 513.7 | 576.4 | 266
245.2 | 25.2 | 48.6 | 504 | 562.2 | 263.7
246.2 | 26.2 | 52.5 | 491.1 | 545.5 | 259.5
247.2 | 27.2 | 56.8 | 469.7 | 530.1 | 264.2
248.2 | 28.2 | 61.2 | 452.8 | 516.2 | 264
249.2 | 29.2 | 65.3 | 440.8 | 519.5 | 278.9
250.2 | 30.2 | 69.3 | 430.8 | 511.2 | 278.4
251.2 | 31.2 | 73.4 | 419.7 | 500.3 | 277
252.2 | 32.2 | 77.1 | 408.7 | 498.4 | 289.7
253.2 | 33.2 | 80.8 | 399.4 | 488.7 | 292.2
254.2 | 34.2 | 84 | 392.2 | 482.3 | 296.1
255.2 | 35.2 | 86.5 | 396 | 469.3 | 289.9
256.2 | 36.2 | 88.9 | 401.7 | 460.8 | 284.7
257.2 | 37.2 | 91.2 | 424.3 | 463 | 285.5
258.2 | 38.2 | 93.5 | 439.4 | 470.5 | 285.9
259.2 | 39.2 | 95.7 | 455.3 | 484.7 | 297.5
260.2 | 40.2 | 97.9 | 474.7 | 470.2 | 295
261.2 | 41.2 | 100.2 | 489.2 | 472.9 | 298.8
262.2 | 42.2 | 102.6 | 506.5 | 484.1 | 305.9
263.2 | 43.2 | 104.8 | 516.8 | 511.7 | 324.7
264.2 | 44.2 | 106.8 | 533.7 | 543 | 346.6
265.2 | 45.2 | 109.2 | 554.1 | 580.7 | 369.1
266.2 | 46.2 | 111.8 | 577.3 | 604.1 | 389.5
267.2 | 47.2 | 114.1 | 610.4 | 619.6 | 401.9
268.2 | 48.2 | 116.3 | 608.2 | 626.8 | 407.7
269.2 | 49.2 | 119.3 | 583.7 | 627 | 417.4
270.2 | 50.2 | 122.3 | 563.3 | 614.6 | 411.5
271.2 | 51.2 | 125.2 | 542.3 | 599.4 | 412.1
272.2 | 52.2 | 127.9 | 529.8 | 602.8 | 420.3
273.2 | 53.2 | 130.8 | 514.5 | 599.1 | 432.9
274.2 | 54.2 | 134.1 | 515.5 | 612.8 | 447
275.2 | 55.2 | 137.1 | 517.1 | 629.1 | 457.6
276.2 | 56.2 | 139.9 | 517.1 | 641.4 | 468.9
277.2 | 57.2 | 142.4 | 522.7 | 654.9 | 482.2
278.2 | 58.2 | 144.8 | 527.8 | 668.3 | 498.3
279.2 | 59.2 | 145.9 | 532.7 | 684.9 | 500.9
280.2 | 60.2 | 146.8 | 551.3 | 699.6 | 503.7
281.2 | 61.2 | 148.1 | 559.8 | 712.5 | 504.8
282.2 | 62.2 | 149.4 | 586.2 | 726.9 | 518.8
283.2 | 63.2 | 151.1 | 615.9 | 745.8 | 534.7
284.2 | 64.2 | 153 | 641.6 | 761.4 | 545.2
285.2 | 65.2 | 155.4 | 653.8 | 764.2 | 553.6
286.2 | 66.2 | 157.7 | 660.7 | 762.7 | 558
287.2 | 67.2 | 160.3 | 661.6 | 758 | 559.5
288.2 | 68.2 | 162.9 | 656.8 | 750 | 557.5
289.2 | 69.2 | 165.6 | 663.3 | 758.2 | 564.5
290.2 | 70.2 | 168.4 | 684.9 | 770.7 | 575.4
291.2 | 71.2 | 171.2 | 703.9 | 774.4 | 578.3
292.2 | 72.2 | 174.2 | 719.7 | 775.7 | 574
293.2 | 73.2 | 177.3 | 725.9 | 781.8 | 576.8
294.2 | 74.2 | 180.6 | 735.6 | 785.5 | 583.1
295.2 | 75.2 | 184 | 741.1 | 772 | 586
296.2 | 76.2 | 187.3 | 748.4 | 766.9 | 589.6
297.2 | 77.2 | 190 | 755.8 | 752.8 | 579.5
298.2 | 78.2 | 192.2 | 760.7 | 734.9 | 569.8
299.2 | 79.2 | 194.2 | 767.9 | 720.1 | 562.9
300.2 | 80.2 | 196.3 | 761 | 738.5 | 584.1
301.2 | 81.2 | 198.4 | 768.8 | 755.2 | 603.6
302.2 | 82.2 | 200.2 | 762 | 762.7 | 613
303.2 | 83.2 | 201.7 | 760.1 | 775.8 | 620.3
304.2 | 84.2 | 203 | 766.2 | 789.9 | 624.7
305.2 | 85.2 | 204.2 | 776 | 798.7 | 631.3
306.2 | 86.2 | 205.6 | 788.5 | 795.7 | 632.3
307.2 | 87.2 | 206.8 | 800 | 796 | 626.1
308.2 | 88.2 | 208.1 | 798.1 | 795.9 | 630.7
309.2 | 89.2 | 209.7 | 770.8 | 788 | 635.9
310.2 | 90.2 | 211.7 | 753.5 | 772 | 636.6
311.2 | 91.2 | 213.7 | 752.7 | 765.5 | 638.4
312.2 | 92.2 | 215.9 | 748.1 | 760.6 | 636.9
313.2 | 93.2 | 218 | 756.8 | 747.3 | 632.1
314.2 | 94.2 | 220.1 | 774.1 | 741.7 | 627.9
315.2 | 95.2 | 222.6 | 761 | 734.9 | 634.8
316.2 | 96.2 | 224.9 | 751.5 | 704.5 | 624.2
317.2 | 97.2 | 227.4 | 747 | 716.5 | 626.6
318.2 | 98.2 | 208.2 | 723.1 | 653.4 | 639.4
319.2 | 99.2 | 132.4 | 684.9 | 395.9 | 645
320.2 | 100.2 | 235.5 | 763.5 | 758.9 | 651.9
321.2 | 101.2 | 191.2 | 611.2 | 593.5 | 655.1
322.2 | 102.2 | 181.8 | 552.7 | 537.1 | 663.1
323.2 | 103.2 | 243.9 | 776.5 | 775.1 | 668.3
324.2 | 104.2 | 246.6 | 768.8 | 769.2 | 663.5
325.2 | 105.2 | 249.2 | 763.6 | 755.2 | 660.3
326.2 | 106.2 | 251.4 | 750.3 | 750.1 | 667.8
327.2 | 107.2 | 252.9 | 732.3 | 757.4 | 682.4
328.2 | 108.2 | 253.7 | 712.8 | 747.1 | 680.8
329.2 | 109.2 | 254.6 | 708.7 | 751.7 | 681.4
330.2 | 110.2 | 256 | 696.2 | 741.5 | 678.1
331.2 | 111.2 | 257.8 | 705.8 | 748 | 674.4
332.2 | 112.2 | 259.6 | 720.5 | 759.6 | 685.3
333.2 | 113.2 | 261.7 | 723.6 | 755.7 | 692.4
334.2 | 114.2 | 263.6 | 729.9 | 761.5 | 692.2
335.2 | 115.2 | 265.4 | 744.1 | 777.3 | 700.2
336.2 | 116.2 | 266.7 | 748.4 | 784 | 701.3
337.2 | 117.2 | 265.6 | 742.8 | 773.6 | 697.9
338.2 | 118.2 | 263 | 737.5 | 768.5 | 695.2
339.2 | 119.2 | 263.5 | 736.5 | 770.8 | 699
340.2 | 120.2 | 265.5 | 718.2 | 755.5 | 702.6
341.2 | 121.2 | 268.4 | 699 | 746.5 | 704.1
342.2 | 122.2 | 271.8 | 687.4 | 741.9 | 711.8
343.2 | 123.2 | 275.8 | 667.9 | 737.1 | 708.6
344.2 | 124.2 | 279.9 | 653.3 | 728.6 | 702.9
345.2 | 125.2 | 284.4 | 647.1 | 733.6 | 713.6
346.2 | 126.2 | 289.1 | 628.2 | 716.1 | 708.8
347.2 | 127.2 | 293.5 | 608.9 | 709.3 | 710.3
348.2 | 128.2 | 298.5 | 593.8 | 711.7 | 719.6
349.2 | 129.2 | 303.8 | 596 | 724.3 | 725.5
350.2 | 130.2 | 308.6 | 625.2 | 731.4 | 724.5
351.2 | 131.2 | 312.9 | 647.7 | 747.7 | 724.8
352.2 | 132.2 | 315.1 | 673.9 | 770.5 | 732.7
353.2 | 133.2 | 317.1 | 680.4 | 783.5 | 737.9
354.2 | 134.2 | 319.9 | 669.8 | 769.8 | 731.1
355.2 | 135.2 | 323.3 | 652.6 | 757.5 | 726.9
356.2 | 136.2 | 326.7 | 647.9 | 755 | 728.4
357.2 | 137.2 | 329.8 | 651.1 | 760.6 | 729.7
358.2 | 138.2 | 333.1 | 645.3 | 754.7 | 738.1
359.2 | 139.2 | 244.3 | 473.3 | 739.5 | 738.7
360.2 | 140.2 | 263.7 | 494.2 | 736.6 | 739.3
361.2 | 141.2 | 342.4 | 632 | 734.6 | 733.8
362.2 | 142.2 | 346.1 | 634.9 | 736.4 | 733.7
363.2 | 143.2 | 349.8 | 651.2 | 740.2 | 730.3
364.2 | 144.2 | 354.9 | 658.1 | 741.6 | 732.7
365.2 | 145.2 | 359.8 | 646.6 | 747.2 | 740.5
366.2 | 146.2 | 365.5 | 657.1 | 756.1 | 750.5
367.2 | 147.2 | 371.2 | 667.4 | 759.5 | 749.3
368.2 | 148.2 | 377.3 | 663.8 | 746.3 | 744.3
369.2 | 149.2 | 385.2 | 667.4 | 756.5 | 745.6
370.2 | 150.2 | 397.8 | 663.6 | 758.5 | 751.6
371.2 | 151.2 | 419.7 | 664.2 | 756.9 | 745.3
372.2 | 152.2 | 444.7 | 655.6 | 755 | 745.1
373.2 | 153.2 | 471.8 | 668.2 | 758.8 | 746.1
374.2 | 154.2 | 503.7 | 684 | 771.8 | 752.8
375.2 | 155.2 | 535.7 | 703.8 | 788.2 | 755.2
376.2 | 156.2 | 572 | 723.1 | 802.3 | 763.1
377.2 | 157.2 | 610.7 | 723.2 | 804.9 | 766.1
378.2 | 158.2 | 646.3 | 716.8 | 801.5 | 758.6
379.2 | 159.2 | 676.9 | 700.1 | 793.9 | 759.5
380.2 | 160.2 | 701.9 | 684.5 | 790.5 | 756.5
381.2 | 161.2 | 726.1 | 677.9 | 790.3 | 759.7
382.2 | 162.2 | 756.8 | 665.2 | 787.5 | 759.5
383.2 | 163.2 | 781.1 | 680.6 | 787 | 759.4
384.2 | 164.2 | 796.9 | 701 | 783.5 | 753.8
385.2 | 165.2 | 819.5 | 713 | 790.5 | 751.9
386.2 | 166.2 | 840 | 700.6 | 799.8 | 745.7
387.2 | 167.2 | 850.4 | 726.3 | 807.7 | 750.4
388.2 | 168.2 | 854.3 | 662.6 | 813.4 | 750.9
389.2 | 169.2 | 854.9 | 405 | 800.1 | 749.3
390.2 | 170.2 | 822.7 | 738.6 | 778.7 | 740.7
391.2 | 171.2 | 800.3 | 537.3 | 762.8 | 734.4
392.2 | 172.2 | 784.1 | 416 | 740 | 732.1
393.2 | 173.2 | 784.9 | 696 | 734.8 | 735.2
394.2 | 174.2 | 809 | 703.3 | 739.5 | 737
395.2 | 175.2 | 800 | 696.8 | 736.8 | 738.4
396.2 | 176.2 | 813.5 | 703.8 | 756.5 | 753.1
397.2 | 177.2 | 820.9 | 711.6 | 765.1 | 760
398.2 | 178.2 | 818.4 | 703.9 | 772 | 760.7
399.2 | 179.2 | 820.8 | 704.7 | 777.2 | 760.8
400.2 | 180.2 | 818.6 | 702.8 | 777.9 | 761.9
401.2 | 181.2 | 806.6 | 695.6 | 759.5 | 752.8
402.2 | 182.2 | 778.3 | 680.8 | 743.4 | 747.3
403.2 | 183.2 | 736.5 | 655 | 722 | 742.5
404.2 | 184.2 | 722.5 | 638.7 | 719.3 | 749.2
405.2 | 185.2 | 724.2 | 629.9 | 730.8 | 753.6
406.2 | 186.2 | 696.4 | 617 | 721.5 | 749.3
407.2 | 187.2 | 668.4 | 467.2 | 712 | 745.2
408.2 | 188.2 | 621.5 | 585.6 | 683.4 | 736.2
409.2 | 189.2 | 577.1 | 526.7 | 683.8 | 735.8
410.2 | 190.2 | 539 | 379.2 | 697.9 | 738.4
411.2 | 191.2 | 512.5 | 597 | 695.7 | 732.1
412.2 | 192.2 | 483.7 | 467 | 720.8 | 737.6
413.2 | 193.2 | 465.4 | 429.7 | 740.2 | 745.3
414.2 | 194.2 | 449.8 | 682.6 | 757.4 | 753
415.2 | 195.2 | 433 | 424.2 | 758.4 | 759.9
416.2 | 196.2 | 413.8 | 531.4 | 756.2 | 751.7
417.2 | 197.2 | 395.1 | 675.4 | 758.7 | 748.4
418.2 | 198.2 | 378.7 | 581.2 | 762.1 | 749.9
419.2 | 199.2 | 366.4 | 656.6 | 763.3 | 754.2
420.2 | 200.2 | 351.2 | 662.7 | 774.6 | 757.2
421.2 | 201.2 | 338.7 | 559.8 | 777 | 762.4
422.2 | 202.2 | 331.9 | 651 | 759.1 | 756
423.2 | 203.2 | 324 | 638.7 | 743.3 | 758.3
424.2 | 204.2 | 315.2 | 631.5 | 731.8 | 756.7
425.2 | 205.2 | 308.3 | 622.2 | 716.6 | 756.7
426.2 | 206.2 | 303.6 | 610 | 708.2 | 749.8
427.2 | 207.2 | 304.1 | 610.4 | 717.1 | 749.8
428.2 | 208.2 | 298.3 | 604.4 | 717.2 | 748.9
429.2 | 209.2 | 290.3 | 441.5 | 715.3 | 749.7
430.2 | 210.2 | 285.7 | 530.4 | 714.8 | 748.4
431.2 | 211.2 | 283 | 599 | 707.7 | 749.9
432.2 | 212.2 | 276.9 | 593.1 | 733 | 760.4
433.2 | 213.2 | 272.4 | 642.4 | 742.4 | 756.1
434.2 | 214.2 | 272.1 | 667.8 | 750.1 | 749.7
435.2 | 215.2 | 272 | 569.6 | 747.5 | 743.3
436.2 | 216.2 | 269.4 | 697.7 | 750.5 | 744.9
437.2 | 217.2 | 263.1 | 703.7 | 748.9 | 748.8
438.2 | 218.2 | 256.1 | 692.2 | 742.9 | 748.5
439.2 | 219.2 | 247.8 | 678.4 | 732.9 | 748.2
440.2 | 220.2 | 242.4 | 672.2 | 741.5 | 752
441.2 | 221.2 | 236.7 | 670.6 | 746.3 | 759.4
442.2 | 222.2 | 233.9 | 675.7 | 749.2 | 758.6
443.2 | 223.2 | 231.9 | 684.3 | 734.9 | 748.9
444.2 | 224.2 | 232.1 | 686 | 715.4 | 734.2
445.2 | 225.2 | 227.9 | 701.7 | 714.5 | 727.2
446.2 | 226.2 | 224.7 | 721.1 | 728.6 | 731.1
447.2 | 227.2 | 220.2 | 738.2 | 749.5 | 743.6
448.2 | 228.2 | 219.9 | 756.7 | 762.5 | 752.5
449.2 | 229.2 | 219.5 | 777.8 | 774.3 | 753.1
450.2 | 230.2 | 215.6 | 789.7 | 781.8 | 757.7
451.2 | 231.2 | 215.4 | 797.1 | 784.8 | 747.7
452.2 | 232.2 | 212.2 | 801 | 792 | 747.1
453.2 | 233.2 | 214.2 | 786.1 | 793.1 | 757.9
454.2 | 234.2 | 212.9 | 782.2 | 799.3 | 765.4
455.2 | 235.2 | 218.6 | 780.2 | 804.6 | 767.8
456.2 | 236.2 | 229.1 | 769.2 | 797.3 | 769.6
457.2 | 237.2 | 235 | 764.6 | 794.3 | 766.3
458.2 | 238.2 | 244.9 | 768.2 | 805.9 | 771.6
459.2 | 239.2 | 242.8 | 758.3 | 798.8 | 767.3
460.2 | 240.2 | 238 | 760.6 | 811.1 | 775
461.2 | 241.2 | 237 | 774.2 | 809.5 | 771.9
462.2 | 242.2 | 232.4 | 787.2 | 797.2 | 756.3
463.2 | 243.2 | 228.6 | 805.6 | 799.5 | 754.5
464.2 | 244.2 | 228 | 813.3 | 800.9 | 752.7
465.2 | 245.2 | 229.2 | 814.5 | 807.7 | 760.2
466.2 | 246.2 | 231.2 | 815 | 806.1 | 757.7
467.2 | 247.2 | 234 | 803.2 | 801.5 | 758.5
468.2 | 248.2 | 232.6 | 805.4 | 787.1 | 758.1
469.2 | 249.2 | 230.8 | 792.6 | 755.2 | 745.7
470.2 | 250.2 | 230.4 | 782.6 | 752.4 | 739
471.2 | 251.2 | 230.7 | 776 | 768.1 | 754.7
472.2 | 252.2 | 230.9 | 752.4 | 767.1 | 764
473.2 | 253.2 | 227.2 | 737.9 | 767.7 | 771.7
474.2 | 254.2 | 222.9 | 727 | 773.9 | 774.8
475.2 | 255.2 | 220.3 | 723.3 | 779.6 | 779.7
476.2 | 256.2 | 218.4 | 726.5 | 778.6 | 772
477.2 | 257.2 | 218.2 | 716.9 | 776.6 | 765.1
478.2 | 258.2 | 217.4 | 716.8 | 767.3 | 756.7
479.2 | 259.2 | 217.6 | 717.7 | 758.3 | 752.3
480.2 | 260.2 | 219 | 726.5 | 761.8 | 753.2
481.2 | 261.2 | 218 | 718.3 | 768.1 | 761.4
482.2 | 262.2 | 216 | 709.6 | 760.2 | 758.5
483.2 | 263.2 | 214.8 | 726.1 | 757.3 | 752.1
484.2 | 264.2 | 212.8 | 738.4 | 764.9 | 751.3
485.2 | 265.2 | 210 | 728.5 | 770.7 | 760.4
486.2 | 266.2 | 207.1 | 732.7 | 775.8 | 760.9
487.2 | 267.2 | 207.8 | 747.4 | 780.7 | 765.3
488.2 | 268.2 | 209.9 | 757.1 | 786.6 | 771.3
489.2 | 269.2 | 206.2 | 752.6 | 781.4 | 772.5
490.2 | 270.2 | 204.1 | 739.5 | 770.7 | 768.5
491.2 | 271.2 | 202.5 | 713.5 | 743 | 759.8
492.2 | 272.2 | 201.7 | 692.7 | 726.6 | 750.8
493.2 | 273.2 | 200.9 | 669.1 | 712.8 | 752.1
494.2 | 274.2 | 202.4 | 652.6 | 713 | 763.3
495.2 | 275.2 | 202.8 | 652 | 733.5 | 772
496.2 | 276.2 | 201.9 | 646.5 | 736.3 | 775.8
497.2 | 277.2 | 201.8 | 643.9 | 744.9 | 776.2
498.2 | 278.2 | 201.6 | 650.7 | 749.7 | 774.4
499.2 | 279.2 | 201.6 | 656.4 | 754.9 | 775.4
500.2 | 280.2 | 202.4 | 655 | 743.8 | 761.3
501.2 | 281.2 | 208.1 | 648.4 | 725.5 | 744.9
502.2 | 282.2 | 210.3 | 648.2 | 720.4 | 743.5
503.2 | 283.2 | 210.8 | 640 | 718.8 | 752.7
504.2 | 284.2 | 215.2 | 636.5 | 713.9 | 754.6
505.2 | 285.2 | 216.2 | 622.1 | 696.6 | 752.7
506.2 | 286.2 | 220.1 | 620.8 | 696.3 | 744.3
507.2 | 287.2 | 231.2 | 615.9 | 700.6 | 740.2
508.2 | 288.2 | 227.9 | 640.3 | 704.9 | 738.2
509.2 | 289.2 | 223.3 | 672.2 | 731.8 | 745
510.2 | 290.2 | 220.9 | 689.5 | 752 | 754.9
511.2 | 291.2 | 220.8 | 712 | 767.1 | 752.7
512.2 | 292.2 | 220.9 | 723.6 | 784.8 | 765.2
513.2 | 293.2 | 222.9 | 738.2 | 802.2 | 766.6
514.2 | 294.2 | 224.2 | 755.3 | 806.5 | 765.3
515.2 | 295.2 | 225.4 | 774.5 | 807.8 | 767.5
516.2 | 296.2 | 228.8 | 777.7 | 815.7 | 771.6
517.2 | 297.2 | 228.3 | 790.5 | 819.2 | 766.5
518.2 | 298.2 | 227.1 | 781.8 | 817.6 | 766.6
519.2 | 299.2 | 224.6 | 773.8 | 823.1 | 765.5
520.2 | 300.2 | 222.2 | 779.3 | 816.8 | 773.1
521.2 | 301.2 | 219.9 | 763 | 805.7 | 773
522.2 | 302.2 | 217.1 | 752.9 | 798.2 | 768
523.2 | 303.2 | 218.2 | 753.3 | 789.4 | 762
524.2 | 304.2 | 217.2 | 770.8 | 803.8 | 767.3
525.2 | 305.2 | 214.3 | 781.7 | 793.9 | 760.5
526.2 | 306.2 | 210.1 | 772.9 | 782.3 | 749.5
527.2 | 307.2 | 210.5 | 773.1 | 777.1 | 745.9
528.2 | 308.2 | 212 | 770.2 | 788.5 | 751.7
529.2 | 309.2 | 214.3 | 762.8 | 780.1 | 752.3
530.2 | 310.2 | 216.5 | 755.3 | 766.3 | 750.4
531.2 | 311.2 | 215.1 | 726.3 | 759.6 | 753.4
532.2 | 312.2 | 214.7 | 712.3 | 763.9 | 767
533.2 | 313.2 | 215.8 | 705.7 | 772.6 | 777.8
534.2 | 314.2 | 214.3 | 706.6 | 785 | 777.9
535.2 | 315.2 | 210.9 | 710.9 | 778.3 | 770.1
536.2 | 316.2 | 208.6 | 693.1 | 777.4 | 767.8
537.2 | 317.2 | 205.8 | 703.1 | 785.9 | 770.4
538.2 | 318.2 | 205.4 | 691.1 | 773.9 | 770.6
539.2 | 319.2 | 204.3 | 671.3 | 768.4 | 775.7
540.2 | 320.2 | 202.7 | 665.2 | 769.9 | 781
541.2 | 321.2 | 201.3 | 663 | 776.7 | 789
542.2 | 322.2 | 204.5 | 673.3 | 778.4 | 785.9
543.2 | 323.2 | 207.1 | 677.2 | 790.6 | 782.7
544.2 | 324.2 | 207.5 | 695.2 | 795.9 | 780.5
545.2 | 325.2 | 208.1 | 707.7 | 785.2 | 768.7
546.2 | 326.2 | 209.7 | 724.9 | 775.4 | 758.2
547.2 | 327.2 | 209.2 | 730 | 778 | 757.4
548.2 | 328.2 | 210.8 | 752 | 780 | 767
549.2 | 329.2 | 211 | 776 | 773.8 | 763.8
550.2 | 330.2 | 214.2 | 786.1 | 788.9 | 764.5
551.2 | 331.2 | 214.6 | 790.7 | 805.9 | 778
552.2 | 332.2 | 216.6 | 794.8 | 804.6 | 778.5
553.2 | 333.2 | 220.2 | 806 | 794.3 | 769.1
554.2 | 334.2 | 222.8 | 804.3 | 782.3 | 761.3
555.2 | 335.2 | 222.3 | 812 | 776.2 | 752.4
556.2 | 336.2 | 225.4 | 800.5 | 780.7 | 759.4
557.2 | 337.2 | 227.2 | 785.4 | 790.6 | 777.1
558.2 | 338.2 | 229.3 | 775.2 | 796.6 | 779.8
559.2 | 339.2 | 233.1 | 768.9 | 791.6 | 769.6
560.2 | 340.2 | 232.4 | 764.7 | 797.2 | 771.8
561.2 | 341.2 | 230.7 | 738.6 | 788.5 | 776.4
562.2 | 342.2 | 231.4 | 719.1 | 780.4 | 778.8
563.2 | 343.2 | 225.9 | 708 | 776.6 | 783.4
564.2 | 344.2 | 222.9 | 714.5 | 793.4 | 786.9
565.2 | 345.2 | 222.3 | 713 | 804.7 | 791.9
566.2 | 346.2 | 219 | 721.7 | 816.9 | 793.8
567.2 | 347.2 | 215.5 | 714 | 826.1 | 799.6
568.2 | 348.2 | 212.8 | 714.4 | 819.3 | 796.8
569.2 | 349.2 | 211.4 | 716.9 | 822.6 | 795.5
570.2 | 350.2 | 214.9 | 731.7 | 829.3 | 797.1
571.2 | 351.2 | 220.2 | 752.2 | 834 | 799.4
572.2 | 352.2 | 224.1 | 755.7 | 828.6 | 795.3
573.2 | 353.2 | 224.8 | 734.5 | 786 | 773.8
574.2 | 354.2 | 227.7 | 721.9 | 766.4 | 757.3
575.2 | 355.2 | 225.1 | 741.8 | 779.1 | 757.9
576.2 | 356.2 | 223.6 | 757.1 | 776.7 | 757.3
577.2 | 357.2 | 224.3 | 752 | 766.1 | 756.8
578.2 | 358.2 | 225.6 | 731.2 | 755.8 | 762.4
579.2 | 359.2 | 226.2 | 705.8 | 740.5 | 755.7
580.2 | 360.2 | 225.2 | 696.3 | 757.8 | 769.8
581.2 | 361.2 | 223.7 | 712.9 | 777.4 | 779.1
582.2 | 362.2 | 223.6 | 715.7 | 784.2 | 781.7
583.2 | 363.2 | 224.4 | 698 | 764.6 | 778.2
584.2 | 364.2 | 223.9 | 669.3 | 733.2 | 770.5
585.2 | 365.2 | 221 | 645.2 | 705.2 | 760.7
586.2 | 366.2 | 219.5 | 619.5 | 681.5 | 756.1
587.2 | 367.2 | 217.4 | 597.9 | 664.1 | 754.5
588.2 | 368.2 | 215.9 | 588.1 | 671.5 | 756.2
589.2 | 369.2 | 216.5 | 594.6 | 694.4 | 767.3
590.2 | 370.2 | 215.9 | 616.1 | 721.2 | 774.8
591.2 | 371.2 | 216.1 | 643.6 | 745.8 | 781.1
592.2 | 372.2 | 217.5 | 676.5 | 768.1 | 783.9
593.2 | 373.2 | 216.5 | 685.5 | 771.4 | 781.8
594.2 | 374.2 | 217.9 | 698.7 | 773.6 | 779.6
595.2 | 375.2 | 218.8 | 704.7 | 760.4 | 768
596.2 | 376.2 | 218.7 | 695.8 | 745.9 | 767.3
597.2 | 377.2 | 215.6 | 667.2 | 721.6 | 759.7
598.2 | 378.2 | 214.1 | 651.4 | 722.8 | 756
599.2 | 379.2 | 213.3 | 640.1 | 739.6 | 769.9
600.2 | 380.2 | 215.4 | 631.4 | 750.6 | 782.4
601.2 | 381.2 | 217.1 | 620.7 | 742.3 | 784.5
602.2 | 382.2 | 218.7 | 629.2 | 756.3 | 782
603.2 | 383.2 | 219.5 | 646.8 | 753.9 | 777.5
604.2 | 384.2 | 217.5 | 660.1 | 746.5 | 774
605.2 | 385.2 | 215.4 | 675.6 | 741 | 772.1
606.2 | 386.2 | 214.1 | 686.9 | 748.2 | 771.6
607.2 | 387.2 | 212.2 | 701.5 | 759.3 | 774.9
608.2 | 388.2 | 214.4 | 720.8 | 765.3 | 762.3
609.2 | 389.2 | 213.5 | 746 | 776.9 | 758.1
610.2 | 390.2 | 212.8 | 757.2 | 785.3 | 760.8
611.2 | 391.2 | 211.4 | 738.6 | 793.1 | 774.3
612.2 | 392.2 | 215.2 | 719.5 | 788.6 | 779.9
613.2 | 393.2 | 219.7 | 693.5 | 767.9 | 774
614.2 | 394.2 | 220.6 | 673.4 | 762.3 | 771.6
615.2 | 395.2 | 233.7 | 686.3 | 771.8 | 770.5
616.2 | 396.2 | 239.1 | 714 | 767.7 | 759.3
617.2 | 397.2 | 240.1 | 722.1 | 780.6 | 761.2
618.2 | 398.2 | 237.8 | 704.4 | 771.3 | 762.7
619.2 | 399.2 | 238.3 | 693.5 | 771.7 | 760.1
620.2 | 400.2 | 236.4 | 709.8 | 771.2 | 759
621.2 | 401.2 | 238.9 | 728.9 | 776 | 760.6
622.2 | 402.2 | 233.1 | 742.5 | 798.7 | 772.6
623.2 | 403.2 | 232.2 | 739.5 | 809.4 | 781
624.2 | 404.2 | 233.6 | 726.1 | 811.6 | 784.6
625.2 | 405.2 | 229.2 | 718.2 | 811 | 786.9
626.2 | 406.2 | 226.5 | 703.3 | 806.2 | 788.3
627.2 | 407.2 | 224.5 | 682 | 781.2 | 779.4
628.2 | 408.2 | 227.2 | 685.9 | 784.1 | 789
629.2 | 409.2 | 229 | 693.1 | 795.1 | 789.3
630.2 | 410.2 | 229.6 | 705.2 | 806.5 | 790.8
631.2 | 411.2 | 230.6 | 707.4 | 814.4 | 785.9
632.2 | 412.2 | 232.7 | 714.3 | 814.8 | 784.8
633.2 | 413.2 | 236.6 | 714 | 811.6 | 787.7
634.2 | 414.2 | 236.7 | 717.5 | 813.7 | 787.8
635.2 | 415.2 | 236.8 | 740.8 | 811.9 | 780.6
636.2 | 416.2 | 235.3 | 746.7 | 781.2 | 761.5
637.2 | 417.2 | 231.9 | 755 | 763.4 | 752.3
638.2 | 418.2 | 230.2 | 764.3 | 750.8 | 745.8
639.2 | 419.2 | 233.3 | 773.4 | 771.2 | 755.9
640.2 | 420.2 | 230.5 | 779.1 | 788.5 | 768.2
641.2 | 421.2 | 226.4 | 758.1 | 781.9 | 779.6
642.2 | 422.2 | 223.4 | 736.7 | 765.8 | 779.9
643.2 | 423.2 | 223 | 745.1 | 781.1 | 788.1
644.2 | 424.2 | 226.2 | 748.3 | 790.6 | 786
645.2 | 425.2 | 226.4 | 742.8 | 798.6 | 788.4
646.2 | 426.2 | 224.8 | 733.9 | 796.6 | 791.7
647.2 | 427.2 | 225.2 | 741.1 | 815.2 | 791
648.2 | 428.2 | 224.3 | 735.1 | 818.1 | 792.1
649.2 | 429.2 | 222.8 | 725.4 | 807.5 | 791.2
650.2 | 430.2 | 220.4 | 720.2 | 810.1 | 788.4
651.2 | 431.2 | 220.8 | 716.1 | 811.3 | 786.9
652.2 | 432.2 | 225 | 722.5 | 778.6 | 771.3
653.2 | 433.2 | 226 | 727.2 | 765.2 | 761.8
654.2 | 434.2 | 225 | 724.1 | 753.7 | 757.7
655.2 | 435.2 | 223.2 | 742.6 | 764.4 | 760.1
656.2 | 436.2 | 220.9 | 749 | 767.8 | 759.1
657.2 | 437.2 | 219.8 | 748.2 | 757.2 | 757.9
658.2 | 438.2 | 222.2 | 740.1 | 740.4 | 758.6
659.2 | 439.2 | 223.9 | 731.4 | 744.7 | 766
660.2 | 440.2 | 226.1 | 728.6 | 744.4 | 779.1
661.2 | 441.2 | 226.1 | 726.5 | 734.4 | 781.7
662.2 | 442.2 | 227.4 | 737.1 | 725 | 773.7
663.2 | 443.2 | 228 | 748.1 | 711.4 | 761.2
664.2 | 444.2 | 226.3 | 736.5 | 714.1 | 758.3
665.2 | 445.2 | 226.1 | 720.2 | 715.5 | 760.1
666.2 | 446.2 | 225.6 | 696 | 703.6 | 754.5
667.2 | 447.2 | 226 | 683.8 | 700.6 | 761.7
668.2 | 448.2 | 229.2 | 670.1 | 699.7 | 773.5
669.2 | 449.2 | 231.4 | 678 | 701.8 | 766.4
670.2 | 450.2 | 233.3 | 701.5 | 710.9 | 753.6
671.2 | 451.2 | 231.2 | 712.5 | 707.5 | 745
672.2 | 452.2 | 228.9 | 713.9 | 701.6 | 739.3
673.2 | 453.2 | 229.8 | 732.4 | 704.5 | 740.4
674.2 | 454.2 | 230.3 | 746.2 | 705.8 | 739.7
675.2 | 455.2 | 230 | 748.9 | 684 | 725.2
676.2 | 456.2 | 232.2 | 742.6 | 667.3 | 720.7
677.2 | 457.2 | 230.9 | 765.4 | 687.6 | 725.6
678.2 | 458.2 | 228.7 | 779.7 | 706.7 | 732.5
679.2 | 459.2 | 229.7 | 789.4 | 722.9 | 736.9
680.2 | 460.2 | 231.2 | 790.8 | 748.2 | 749.6
681.2 | 461.2 | 230.9 | 774.3 | 754.8 | 759.3
682.2 | 462.2 | 229.5 | 759.8 | 763.4 | 766.4
683.2 | 463.2 | 226.9 | 757.3 | 777.5 | 772
684.2 | 464.2 | 223.5 | 755.1 | 786.5 | 772.4
685.2 | 465.2 | 218.7 | 749.7 | 787.8 | 774.1
686.2 | 466.2 | 216 | 744.4 | 800.2 | 779.1
687.2 | 467.2 | 214.8 | 747.2 | 798.8 | 781.7
688.2 | 468.2 | 215.6 | 754.4 | 807.3 | 781
689.2 | 469.2 | 217.6 | 767.3 | 810.9 | 775.1
690.2 | 470.2 | 219.3 | 764.8 | 819.1 | 774.5
691.2 | 471.2 | 223.3 | 742.6 | 823.8 | 774.4
692.2 | 472.2 | 226.4 | 724 | 810.8 | 776.6
693.2 | 473.2 | 225.4 | 704.5 | 804.4 | 781
694.2 | 474.2 | 223.3 | 699.4 | 803.8 | 781.4
695.2 | 475.2 | 221.6 | 711.1 | 812.6 | 780
696.2 | 476.2 | 220.8 | 726.4 | 811.3 | 779.8
697.2 | 477.2 | 219.3 | 744.7 | 782.9 | 760.3
698.2 | 478.2 | 218.6 | 754.2 | 789.3 | 756
699.2 | 479.2 | 218.1 | 761.4 | 781.1 | 752.1
700.2 | 480.2 | 216.1 | 756.5 | 755.8 | 739.4
701.2 | 481.2 | 215.9 | 762.1 | 745.3 | 734.8
702.2 | 482.2 | 217.4 | 776.6 | 768.1 | 747.7
703.2 | 483.2 | 223.2 | 786.3 | 772.1 | 753.4
704.2 | 484.2 | 225.2 | 770.6 | 785 | 762
705.2 | 485.2 | 222.4 | 756.1 | 793.1 | 767
706.2 | 486.2 | 219.2 | 751.4 | 806 | 777.8
707.2 | 487.2 | 217.7 | 754.7 | 809.4 | 782.5
708.2 | 488.2 | 216.2 | 759.8 | 807.6 | 776.8
709.2 | 489.2 | 214.6 | 769.4 | 808.2 | 765.1
710.2 | 490.2 | 221 | 772.6 | 811.5 | 761.8
711.2 | 491.2 | 224.3 | 782.5 | 815.2 | 763.3
712.2 | 492.2 | 227.2 | 787.4 | 810.7 | 754.8
713.2 | 493.2 | 228.5 | 795.5 | 802.7 | 752.2
714.2 | 494.2 | 228.3 | 797.2 | 798 | 755.1
715.2 | 495.2 | 229.6 | 794.2 | 792.6 | 759.9
716.2 | 496.2 | 229.7 | 797.1 | 798.7 | 765
717.2 | 497.2 | 231.4 | 794.1 | 805.6 | 773.6
718.2 | 498.2 | 230.6 | 765.8 | 803.7 | 778.9
719.2 | 499.2 | 237.9 | 742.9 | 784 | 773.7
720.2 | 500.2 | 242.7 | 714.7 | 778.7 | 772.3
721.2 | 501.2 | 248.4 | 707.3 | 790.6 | 770.7
722.2 | 502.2 | 248.8 | 712 | 808.3 | 778.9
723.2 | 503.2 | 251.6 | 729.8 | 803.8 | 778
724.2 | 504.2 | 247.9 | 741.3 | 784.1 | 761.4
725.2 | 505.2 | 243.1 | 734.6 | 760.7 | 744.7
726.2 | 506.2 | 237.4 | 719.8 | 746.8 | 745.3
727.2 | 507.2 | 233.7 | 722.6 | 732.7 | 742.9
728.2 | 508.2 | 234.2 | 709.7 | 738.5 | 752.3
729.2 | 509.2 | 236.3 | 706 | 755 | 768.2
730.2 | 510.2 | 234.7 | 706.2 | 749.1 | 768.3
731.2 | 511.2 | 231.5 | 710.2 | 718.9 | 748.7
732.2 | 512.2 | 229.5 | 714.6 | 714.4 | 739.6
733.2 | 513.2 | 227.4 | 715 | 700.1 | 734
734.2 | 514.2 | 229 | 720.6 | 690.2 | 728.2
735.2 | 515.2 | 228.3 | 741 | 699.5 | 724.6
736.2 | 516.2 | 230.7 | 760.2 | 713 | 724.5
737.2 | 517.2 | 234.1 | 775 | 724 | 727.8
738.2 | 518.2 | 233.3 | 788.3 | 740.4 | 728.6
739.2 | 519.2 | 233.4 | 800.3 | 749.2 | 729.5
740.2 | 520.2 | 232.2 | 795.1 | 760.8 | 734.3
741.2 | 521.2 | 231.8 | 806.8 | 783.5 | 746.9
742.2 | 522.2 | 231 | 805.2 | 780.3 | 745.1
743.2 | 523.2 | 230.7 | 801.9 | 778.4 | 747.3
744.2 | 524.2 | 234.3 | 805.9 | 799.9 | 751.2
745.2 | 525.2 | 235.1 | 811.7 | 813.7 | 760.5
746.2 | 526.2 | 240 | 811.3 | 815.5 | 760
747.2 | 527.2 | 236.6 | 811.2 | 820.8 | 755.2
748.2 | 528.2 | 235.7 | 814.3 | 821.3 | 758.4
749.2 | 529.2 | 234.2 | 808.2 | 821.7 | 765.1
750.2 | 530.2 | 232.3 | 783.6 | 812.8 | 767.6
751.2 | 531.2 | 230.4 | 759.5 | 805.7 | 772.8
752.2 | 532.2 | 228.9 | 734.9 | 792 | 773.3
753.2 | 533.2 | 229 | 712.6 | 778.4 | 770
754.2 | 534.2 | 230.8 | 712.4 | 776.8 | 767.3
755.2 | 535.2 | 231.4 | 721.1 | 773.4 | 759.8
756.2 | 536.2 | 232.7 | 738.1 | 765.4 | 749.3
757.2 | 537.2 | 232.1 | 765.1 | 757.2 | 738.1
758.2 | 538.2 | 234.4 | 766 | 714.1 | 724.9
759.2 | 539.2 | 234.6 | 767.7 | 697.3 | 719.7
760.2 | 540.2 | 233.5 | 770.5 | 676.7 | 713.2
761.2 | 541.2 | 232.9 | 755.4 | 647.8 | 705.2
762.2 | 542.2 | 231.9 | 755.7 | 665.4 | 707.8
763.2 | 543.2 | 230 | 758.8 | 685.7 | 720.6
764.2 | 544.2 | 231 | 761.1 | 677.2 | 720.1
765.2 | 545.2 | 233.1 | 767.1 | 673.1 | 711.3
766.2 | 546.2 | 237.1 | 759.5 | 676.3 | 715.2
767.2 | 547.2 | 233.9 | 760.5 | 662.6 | 707.6
768.2 | 548.2 | 237.8 | 756.7 | 673.5 | 708.2
769.2 | 549.2 | 239.1 | 765.8 | 690.9 | 714.7
770.2 | 550.2 | 257.1 | 786.6 | 725.9 | 719.7
771.2 | 551.2 | 260.4 | 802.4 | 745.4 | 727.9
772.2 | 552.2 | 260.5 | 801.3 | 750.7 | 725.3
773.2 | 553.2 | 253.9 | 800.5 | 762.8 | 726.2
774.2 | 554.2 | 250.1 | 801.5 | 777.4 | 727.1
775.2 | 555.2 | 245.7 | 799 | 782.8 | 732
776.2 | 556.2 | 241.9 | 796.3 | 793.7 | 746.5
777.2 | 557.2 | 244.3 | 795.1 | 790.8 | 751.3
778.2 | 558.2 | 249.8 | 794.1 | 791.5 | 741.6
779.2 | 559.2 | 248.3 | 791.2 | 781.5 | 737.2
780.2 | 560.2 | 247.6 | 784.4 | 780.3 | 746.7
781.2 | 561.2 | 244.6 | 781.1 | 802.2 | 762.5
782.2 | 562.2 | 242.5 | 762.7 | 788.4 | 767
783.2 | 563.2 | 245 | 742.7 | 786 | 766.6
784.2 | 564.2 | 244.5 | 751.5 | 796.6 | 764.7
785.2 | 565.2 | 245.5 | 740.2 | 813.6 | 770.9
786.2 | 566.2 | 243.9 | 726.5 | 807.5 | 777.5
787.2 | 567.2 | 243.6 | 711.9 | 810.6 | 781
788.2 | 568.2 | 245.5 | 701.4 | 797.5 | 779.2
789.2 | 569.2 | 242.8 | 678.5 | 776.1 | 768.7
790.2 | 570.2 | 241.3 | 676.8 | 780.5 | 776.4
791.2 | 571.2 | 241.1 | 691.2 | 795.1 | 786.1
792.2 | 572.2 | 246.4 | 717 | 796.4 | 775.7
793.2 | 573.2 | 251.9 | 729.5 | 784.6 | 757.7
794.2 | 574.2 | 254.6 | 725.5 | 752.1 | 739.5
795.2 | 575.2 | 256.1 | 733.5 | 745.7 | 734.5
796.2 | 576.2 | 251.6 | 747.3 | 751.4 | 737.1
797.2 | 577.2 | 249.9 | 743.3 | 768.3 | 756.4
798.2 | 578.2 | 247.5 | 734.7 | 771.6 | 762.4
799.2 | 579.2 | 244.7 | 734.6 | 780.4 | 764.6
800.2 | 580.2 | 243.5 | 731 | 774.9 | 773.1
801.2 | 581.2 | 242.1 | 740.4 | 773.5 | 772.3
802.2 | 582.2 | 240.3 | 742.7 | 769.3 | 760.3
803.2 | 583.2 | 239.3 | 740.8 | 783.7 | 766.6
804.2 | 584.2 | 239.7 | 748 | 787.2 | 771
805.2 | 585.2 | 240.5 | 757.9 | 778.8 | 763.2
806.2 | 586.2 | 239.4 | 769.1 | 770.8 | 762.1
807.2 | 587.2 | 238.1 | 759.3 | 765.7 | 757
808.2 | 588.2 | 236.6 | 764.2 | 765.1 | 760.3
809.2 | 589.2 | 236.3 | 774.4 | 767.2 | 764.4
810.2 | 590.2 | 233.9 | 778.8 | 784.6 | 762.1
811.2 | 591.2 | 230 | 774.8 | 803.5 | 769.5
812.2 | 592.2 | 226.9 | 768.9 | 812.7 | 777.1
813.2 | 593.2 | 225.2 | 764.9 | 818.7 | 783.6
814.2 | 594.2 | 227.8 | 778.2 | 829.2 | 792.2
815.2 | 595.2 | 231.6 | 776.6 | 824.7 | 793.9
816.2 | 596.2 | 230.5 | 773.2 | 809.7 | 786.3
817.2 | 597.2 | 233.3 | 774.7 | 815 | 782.9
818.2 | 598.2 | 235.6 | 771.8 | 831.8 | 791.3
819.2 | 599.2 | 242.9 | 755.7 | 833.7 | 791.5
820.2 | 600.2 | 247.6 | 752.8 | 820.1 | 785
821.2 | 601.2 | 250.8 | 758.5 | 798.5 | 766.8
822.2 | 602.2 | 253.1 | 770.9 | 797 | 767.1
823.2 | 603.2 | 251.9 | 782.1 | 796 | 763.6
824.2 | 604.2 | 248.8 | 789.4 | 811.5 | 769.2
825.2 | 605.2 | 250.2 | 801.6 | 817.3 | 773.1
826.2 | 606.2 | 250.3 | 803.6 | 825.8 | 777.7
827.2 | 607.2 | 248.1 | 803.1 | 832.8 | 784
828.2 | 608.2 | 247.3 | 797.6 | 833.4 | 783.8
829.2 | 609.2 | 245.7 | 782.5 | 813.4 | 790.7
830.2 | 610.2 | 244.9 | 790.2 | 814.8 | 789
831.2 | 611.2 | 245.5 | 783.3 | 812.7 | 786.4
832.2 | 612.2 | 242.9 | 764.5 | 789.4 | 789.2
833.2 | 613.2 | 241.1 | 737 | 750.2 | 769.9
834.2 | 614.2 | 240.1 | 741.2 | 725.6 | 751.9
835.2 | 615.2 | 241.1 | 754 | 709.7 | 744.4
836.2 | 616.2 | 239.6 | 757.5 | 723.4 | 757.2
837.2 | 617.2 | 238.2 | 753.4 | 735.1 | 761.1
838.2 | 618.2 | 236.6 | 749.4 | 740.7 | 765.5
839.2 | 619.2 | 237.7 | 741.7 | 744.5 | 766.5
840.2 | 620.2 | 239.4 | 745.5 | 726 | 759.4
841.2 | 621.2 | 240.8 | 764.5 | 729.4 | 760.3
842.2 | 622.2 | 240.2 | 785.3 | 731 | 751.2
843.2 | 623.2 | 241.7 | 804.7 | 740.9 | 748.4
844.2 | 624.2 | 242.9 | 809.1 | 728.4 | 743
845.2 | 625.2 | 243.1 | 797.7 | 718.6 | 738
846.2 | 626.2 | 240.5 | 790 | 726.6 | 749.6
847.2 | 627.2 | 240.9 | 771.3 | 721.9 | 761
848.2 | 628.2 | 244.1 | 754.7 | 720 | 763.5
849.2 | 629.2 | 243.4 | 761.2 | 712.5 | 759.8
850.2 | 630.2 | 242 | 766 | 704.5 | 753.4
851.2 | 631.2 | 239.6 | 780.8 | 715.9 | 748.4
852.2 | 632.2 | 235.8 | 789.4 | 726.5 | 753.8
853.2 | 633.2 | 233.5 | 788.6 | 731.5 | 767.5
854.2 | 634.2 | 234 | 761.5 | 746.7 | 776.1
855.2 | 635.2 | 233.2 | 740 | 763.2 | 781
856.2 | 636.2 | 234.1 | 738.5 | 770.7 | 777.7
857.2 | 637.2 | 234.3 | 743.2 | 784.9 | 778.5
858.2 | 638.2 | 232.6 | 743.2 | 799.3 | 783.6
859.2 | 639.2 | 232.4 | 751.4 | 806.4 | 781
860.2 | 640.2 | 233.2 | 755.8 | 798.5 | 775.9
861.2 | 641.2 | 230.5 | 763.2 | 785 | 765.7
862.2 | 642.2 | 228.4 | 769.8 | 778.5 | 761.1
863.2 | 643.2 | 228.3 | 781.8 | 756.4 | 756.2
864.2 | 644.2 | 232 | 775 | 734.7 | 750.7
865.2 | 645.2 | 236.3 | 768.3 | 720.2 | 743.5
866.2 | 646.2 | 236 | 772.1 | 716.9 | 744.3
867.2 | 647.2 | 237.8 | 775 | 721.4 | 749.3
868.2 | 648.2 | 239.3 | 775.8 | 735.6 | 756
869.2 | 649.2 | 240.8 | 791.9 | 743.5 | 750.8
870.2 | 650.2 | 244.4 | 809.8 | 750.5 | 750.2
871.2 | 651.2 | 247 | 808.3 | 738.6 | 744
872.2 | 652.2 | 247.7 | 811.7 | 732.5 | 739.4
873.2 | 653.2 | 247.3 | 811.2 | 715.3 | 734
874.2 | 654.2 | 256.6 | 822.9 | 724.8 | 732.3
875.2 | 655.2 | 257.5 | 811.9 | 697.7 | 723.8
876.2 | 656.2 | 255.5 | 804.2 | 677.3 | 715.7
877.2 | 657.2 | 253.4 | 801.6 | 693.9 | 715.8
878.2 | 658.2 | 248.6 | 804.5 | 713.1 | 726.4
879.2 | 659.2 | 246.1 | 800.1 | 700 | 723.7
880.2 | 660.2 | 246.2 | 799 | 685.8 | 710.7
881.2 | 661.2 | 247.9 | 809.5 | 698.5 | 713.7
882.2 | 662.2 | 247.8 | 811.2 | 715.6 | 724
883.2 | 663.2 | 246.1 | 804.6 | 720.8 | 732.1
884.2 | 664.2 | 245.9 | 787.3 | 722.9 | 740.5
885.2 | 665.2 | 246 | 786.5 | 729.6 | 747.6
886.2 | 666.2 | 248.4 | 781.1 | 728.9 | 745
887.2 | 667.2 | 250.4 | 766.4 | 729.8 | 737.3
888.2 | 668.2 | 249.3 | 767.4 | 755.8 | 740.1
889.2 | 669.2 | 245.4 | 746.6 | 759.2 | 744.2
890.2 | 670.2 | 243.2 | 712.9 | 748.9 | 746.5
891.2 | 671.2 | 239.6 | 688.5 | 745.5 | 750.5
892.2 | 672.2 | 240.1 | 681.5 | 753.3 | 759
893.2 | 673.2 | 242.6 | 699.2 | 752.6 | 757.5
894.2 | 674.2 | 244.1 | 728.7 | 760.7 | 750.9
895.2 | 675.2 | 245.9 | 745 | 769 | 748.9
896.2 | 676.2 | 244.3 | 751.4 | 767.7 | 751.9
897.2 | 677.2 | 245 | 763.7 | 769 | 755.7
898.2 | 678.2 | 244 | 777 | 782.3 | 754.5
899.2 | 679.2 | 244.2 | 787.3 | 799.3 | 763.8
900.2 | 680.2 | 243.9 | 787.6 | 796.6 | 771.8
901.2 | 681.2 | 241 | 778.8 | 775.3 | 755.9
902.2 | 682.2 | 239.5 | 766.7 | 771.6 | 744.7
903.2 | 683.2 | 242.7 | 766 | 765.5 | 745.5
904.2 | 684.2 | 241.5 | 771.2 | 756.5 | 747.9
905.2 | 685.2 | 239.8 | 770 | 759.1 | 744.9
906.2 | 686.2 | 239.6 | 769.6 | 770.9 | 744.4
907.2 | 687.2 | 242 | 778.7 | 779.3 | 747.9
908.2 | 688.2 | 240.6 | 778.5 | 781.4 | 748.3
909.2 | 689.2 | 239.3 | 764.6 | 785.1 | 753
910.2 | 690.2 | 238.7 | 749.5 | 772.3 | 748.3
911.2 | 691.2 | 239.7 | 730.7 | 748.8 | 742.7
912.2 | 692.2 | 239.2 | 706.3 | 741 | 746.8
913.2 | 693.2 | 240.1 | 688.1 | 752.3 | 755.4
914.2 | 694.2 | 243.7 | 686.1 | 771.8 | 768.9
915.2 | 695.2 | 242.3 | 665.6 | 753.6 | 765
916.2 | 696.2 | 241.1 | 645.4 | 728.6 | 758.9
917.2 | 697.2 | 238.4 | 632.9 | 730.1 | 756.6
918.2 | 698.2 | 236.8 | 656.1 | 766.3 | 768.9
919.2 | 699.2 | 235.4 | 656.6 | 771.6 | 772.4
920.2 | 700.2 | 231.7 | 649 | 787.1 | 773.4
921.2 | 701.2 | 231.3 | 668.6 | 794 | 777.4
922.2 | 702.2 | 233 | 704.2 | 804.5 | 770.1
923.2 | 703.2 | 235.7 | 732 | 796.2 | 754.9
924.2 | 704.2 | 236 | 743.1 | 807.3 | 759.9
925.2 | 705.2 | 235.5 | 724.9 | 798.3 | 763.8
926.2 | 706.2 | 232.8 | 700.1 | 773.4 | 766.8
927.2 | 707.2 | 233.4 | 687.5 | 780.5 | 774.2
928.2 | 708.2 | 236.2 | 678.9 | 788.2 | 778.3
929.2 | 709.2 | 235.4 | 663.5 | 787.6 | 782.8
930.2 | 710.2 | 235.7 | 669 | 790.6 | 786
931.2 | 711.2 | 234.8 | 677.8 | 784.2 | 785.2
932.2 | 712.2 | 235.1 | 702.1 | 798.5 | 788.4
933.2 | 713.2 | 235.3 | 698.6 | 802.7 | 786.7
934.2 | 714.2 | 232.1 | 688.4 | 805.6 | 782
935.2 | 715.2 | 230.7 | 693.6 | 805.8 | 778.8
936.2 | 716.2 | 229.2 | 711.7 | 792 | 770.2
937.2 | 717.2 | 228.4 | 714.8 | 783 | 762.9
938.2 | 718.2 | 227.7 | 715.4 | 776.2 | 760.4
939.2 | 719.2 | 224.6 | 735.6 | 775.9 | 756.8
940.2 | 720.2 | 223.7 | 748.7 | 804.9 | 773.1
941.2 | 721.2 | 226 | 772.9 | 818 | 772
942.2 | 722.2 | 228.5 | 781.7 | 816.1 | 774.8
943.2 | 723.2 | 229.3 | 788.5 | 812.5 | 767.4
944.2 | 724.2 | 232.7 | 792.4 | 813.9 | 767.6
945.2 | 725.2 | 233.3 | 799.2 | 817.4 | 771.1
946.2 | 726.2 | 233.8 | 807.4 | 822.8 | 769.6
947.2 | 727.2 | 236.5 | 817.4 | 817 | 764.3
948.2 | 728.2 | 238.4 | 808.5 | 810.4 | 762.4
949.2 | 729.2 | 242.2 | 808.9 | 820.1 | 770.7
950.2 | 730.2 | 245.1 | 810.6 | 826.4 | 777.9
951.2 | 731.2 | 243.6 | 820.8 | 823.2 | 775.7
952.2 | 732.2 | 244.4 | 814.5 | 811.3 | 768.8
953.2 | 733.2 | 245.3 | 826.8 | 816 | 766.2
954.2 | 734.2 | 247.2 | 814.4 | 822.5 | 769.4
955.2 | 735.2 | 250.1 | 803.5 | 821.9 | 780.3
956.2 | 736.2 | 248.9 | 806 | 814.2 | 772.3
957.2 | 737.2 | 249.7 | 822.8 | 812.8 | 768.5
958.2 | 738.2 | 251.6 | 816.7 | 798.7 | 765.4
959.2 | 739.2 | 247.1 | 810.6 | 788.7 | 761.4
960.2 | 740.2 | 244.1 | 799.4 | 792.7 | 762
961.2 | 741.2 | 242.2 | 796.4 | 790.9 | 763.7
962.2 | 742.2 | 240.5 | 784.1 | 793.1 | 768.3
963.2 | 743.2 | 237.7 | 757.7 | 797.7 | 777.3
964.2 | 744.2 | 234.9 | 754.2 | 795.8 | 782.5
965.2 | 745.2 | 233.6 | 753.6 | 789.7 | 782.1
966.2 | 746.2 | 235.2 | 744.8 | 792.7 | 783.3
967.2 | 747.2 | 235.7 | 748.4 | 794.8 | 785.1
968.2 | 748.2 | 238.9 | 763.9 | 798.9 | 781.9
969.2 | 749.2 | 240.7 | 760.7 | 799 | 774.1
970.2 | 750.2 | 239.5 | 772.8 | 793.2 | 768.6
971.2 | 751.2 | 237.6 | 786.6 | 778.4 | 758.1
972.2 | 752.2 | 234.7 | 797.8 | 779.6 | 757.8
973.2 | 753.2 | 236.1 | 795.5 | 789.4 | 764.4
974.2 | 754.2 | 238 | 793.4 | 796.3 | 767.9
975.2 | 755.2 | 239.6 | 804.3 | 804.8 | 769.7
976.2 | 756.2 | 240.9 | 806.6 | 813.3 | 766.9
977.2 | 757.2 | 241.9 | 800.6 | 815 | 769.5
978.2 | 758.2 | 246 | 780.1 | 817.8 | 775.9
979.2 | 759.2 | 250.2 | 780.4 | 810.1 | 773.5
980.2 | 760.2 | 256.5 | 787.4 | 798.2 | 758.6
981.2 | 761.2 | 260.5 | 793.6 | 798.5 | 756.3
982.2 | 762.2 | 262.4 | 798.7 | 804.9 | 763.5
983.2 | 763.2 | 262.5 | 800.2 | 822.9 | 773.8
984.2 | 764.2 | 263.3 | 812.2 | 813.7 | 768.2
985.2 | 765.2 | 267.1 | 822 | 788 | 751.1
986.2 | 766.2 | 268.6 | 825.8 | 778.4 | 745.9
987.2 | 767.2 | 269.1 | 813.4 | 752 | 737.1
988.2 | 768.2 | 271.2 | 802.9 | 728.9 | 728.3
989.2 | 769.2 | 267.4 | 795.7 | 695.7 | 719.5
990.2 | 770.2 | 264.7 | 800.5 | 679.8 | 717.8
991.2 | 771.2 | 267.2 | 810.7 | 694.4 | 724.6
992.2 | 772.2 | 262.3 | 803.3 | 709.5 | 729.7
993.2 | 773.2 | 261.3 | 793.8 | 685.7 | 718.7
994.2 | 774.2 | 260.4 | 787.9 | 668.5 | 708.3
995.2 | 775.2 | 262 | 794.7 | 693.2 | 713.9
996.2 | 776.2 | 262.2 | 794.5 | 695.8 | 716.4
997.2 | 777.2 | 258.8 | 793 | 706 | 717.2
998.2 | 778.2 | 255.9 | 792 | 719.8 | 722.6
999.2 | 779.2 | 253.6 | 801.3 | 733.7 | 723.2
1000.2 | 780.2 | 252.2 | 801.3 | 738 | 726.7
1001.2 | 781.2 | 251.7 | 794.6 | 745.1 | 725.6
1002.2 | 782.2 | 252.5 | 790.6 | 758.9 | 733.3
1003.2 | 783.2 | 254.7 | 793.3 | 762 | 732.3
1004.2 | 784.2 | 253.5 | 789.1 | 774.4 | 735.8
1005.2 | 785.2 | 250 | 793.1 | 777.6 | 737.9
1006.2 | 786.2 | 251.1 | 792.3 | 790.5 | 739.3
1007.2 | 787.2 | 252.6 | 803.1 | 787.4 | 733
1008.2 | 788.2 | 254.7 | 805.9 | 777.7 | 724.3
1009.2 | 789.2 | 251.8 | 782 | 739.1 | 712.4
1010.2 | 790.2 | 252.7 | 774.6 | 716.4 | 703.1
1011.2 | 791.2 | 253.2 | 778 | 728.1 | 718.3
1012.2 | 792.2 | 255.6 | 786.9 | 729.9 | 732.2
1013.2 | 793.2 | 256.8 | 800.9 | 733.9 | 726
1014.2 | 794.2 | 256.4 | 804.8 | 747 | 727.3
1015.2 | 795.2 | 251.5 | 799.3 | 746.9 | 732.5
1016.2 | 796.2 | 251 | 812.4 | 743.9 | 730.9
1017.2 | 797.2 | 257.4 | 819.3 | 743.8 | 724.9
1018.2 | 798.2 | 258.3 | 809.6 | 754.5 | 734.2
1019.2 | 799.2 | 258.3 | 815.8 | 771.3 | 744.7
1020.2 | 800.2 | 260.5 | 818.4 | 781.7 | 744
1021.2 | 801.2 | 262.2 | 810.8 | 795.5 | 750.4
1022.2 | 802.2 | 263.5 | 793.3 | 807.4 | 757.3
1023.2 | 803.2 | 261.1 | 783.9 | 809 | 765.5
1024.2 | 804.2 | 258.3 | 771.6 | 801.6 | 767.2
1025.2 | 805.2 | 255.5 | 741 | 792.2 | 770.6
1026.2 | 806.2 | 261 | 718.5 | 770.8 | 767
1027.2 | 807.2 | 268.6 | 708.3 | 758.3 | 761.4
1028.2 | 808.2 | 270.7 | 728.6 | 777.4 | 763
1029.2 | 809.2 | 272.4 | 744.4 | 759.6 | 758.2
1030.2 | 810.2 | 272.7 | 751.8 | 756 | 751.3
1031.2 | 811.2 | 272.2 | 749.3 | 736.3 | 743.1
1032.2 | 812.2 | 271.1 | 755.9 | 724 | 730.9
1033.2 | 813.2 | 271 | 774.9 | 695.7 | 717.6
1034.2 | 814.2 | 269 | 784.5 | 660.9 | 704.5
1035.2 | 815.2 | 266.4 | 793.8 | 662.6 | 700.1
1036.2 | 816.2 | 265.2 | 794.8 | 672.6 | 707.5
1037.2 | 817.2 | 262.9 | 797.1 | 677.8 | 707.5
1038.2 | 818.2 | 265.6 | 792.8 | 684.5 | 711.5
1039.2 | 819.2 | 264.7 | 806.5 | 714.1 | 722.6
1040.2 | 820.2 | 263.8 | 807.2 | 715.3 | 719.2
1041.2 | 821.2 | 260.6 | 813.1 | 711.5 | 709.2
1042.2 | 822.2 | 258.1 | 806.1 | 696.7 | 707.9
1043.2 | 823.2 | 256 | 802 | 672.4 | 697.9
1044.2 | 824.2 | 256.1 | 792.9 | 659.1 | 691.3
1045.2 | 825.2 | 257.8 | 788.9 | 695.4 | 707.5
1046.2 | 826.2 | 258.9 | 767.1 | 714.1 | 728.5
1047.2 | 827.2 | 259.5 | 767.4 | 730.7 | 731.8
1048.2 | 828.2 | 263.9 | 778.1 | 725.9 | 723.6
1049.2 | 829.2 | 264.3 | 788 | 724.8 | 713.2
1050.2 | 830.2 | 267.5 | 790.4 | 706.8 | 705.6
1051.2 | 831.2 | 269 | 793.6 | 688.7 | 692.8
1052.2 | 832.2 | 267.8 | 812.6 | 706.2 | 693.5
1053.2 | 833.2 | 267.2 | 824.2 | 736.3 | 709.2
1054.2 | 834.2 | 267.9 | 826.3 | 750.4 | 725.1
1055.2 | 835.2 | 265.7 | 816.2 | 761 | 729.8
1056.2 | 836.2 | 265.4 | 810.4 | 776.8 | 734.6
1057.2 | 837.2 | 266.4 | 798.8 | 792.8 | 746.2
1058.2 | 838.2 | 269.5 | 773.9 | 784.5 | 752.1
1059.2 | 839.2 | 269 | 756.5 | 787.5 | 753.8
1060.2 | 840.2 | 268.7 | 749 | 783.4 | 749.1
1061.2 | 841.2 | 270.6 | 728.1 | 764.7 | 741.6
1062.2 | 842.2 | 272.3 | 731.1 | 764.3 | 738.2
1063.2 | 843.2 | 272.2 | 751.7 | 776.1 | 740.4
1064.2 | 844.2 | 270.5 | 759 | 782.2 | 746.9
1065.2 | 845.2 | 268.4 | 771.4 | 779.6 | 734.7
1066.2 | 846.2 | 268.6 | 769.2 | 767.7 | 735.3
1067.2 | 847.2 | 270.1 | 777.1 | 762.3 | 731.7
1068.2 | 848.2 | 274.1 | 765.7 | 761.5 | 733.5
1069.2 | 849.2 | 274.3 | 757.8 | 747.9 | 724.5
1070.2 | 850.2 | 272.7 | 768.8 | 750.3 | 718.4
1071.2 | 851.2 | 273.3 | 772.8 | 734.6 | 715.9
1072.2 | 852.2 | 274.7 | 780.9 | 713.3 | 710.5
1073.2 | 853.2 | 272.7 | 778.3 | 715.3 | 704.8
1074.2 | 854.2 | 271.1 | 771.3 | 740.4 | 716.9
1075.2 | 855.2 | 267.8 | 763.1 | 759.7 | 729.5
1076.2 | 856.2 | 262.9 | 730 | 742.5 | 739.3
1077.2 | 857.2 | 258.4 | 700.3 | 709.9 | 733.4
1078.2 | 858.2 | 256.6 | 679.4 | 722.6 | 737.7
1079.2 | 859.2 | 259.3 | 682.2 | 752.5 | 748.4
1080.2 | 860.2 | 261.8 | 710.9 | 762.1 | 749.5
1081.2 | 861.2 | 262.4 | 740.2 | 764.2 | 744.1
1082.2 | 862.2 | 267.6 | 763 | 774.1 | 740.8
1083.2 | 863.2 | 269.5 | 752.2 | 786.4 | 746.9
1084.2 | 864.2 | 270.4 | 742.8 | 789.1 | 752.3
1085.2 | 865.2 | 267.1 | 739 | 780.5 | 752.5
1086.2 | 866.2 | 264 | 737 | 761.4 | 741.5
1087.2 | 867.2 | 261.2 | 721.6 | 743 | 734
1088.2 | 868.2 | 259 | 702.8 | 744.3 | 726.5
1089.2 | 869.2 | 257.7 | 684 | 747.3 | 742.4
1090.2 | 870.2 | 259.8 | 672.7 | 741.4 | 745.3
1091.2 | 871.2 | 259.6 | 670.8 | 715.8 | 731.8
1092.2 | 872.2 | 259.1 | 679.4 | 695.9 | 716
1093.2 | 873.2 | 258.8 | 701.4 | 666 | 702.1
1094.2 | 874.2 | 256.4 | 713.4 | 654.6 | 694.9
1095.2 | 875.2 | 256 | 739.1 | 642.8 | 688.9
1096.2 | 876.2 | 259.5 | 764.8 | 669.6 | 695.3
1097.2 | 877.2 | 260.3 | 781.6 | 708.5 | 711.4
1098.2 | 878.2 | 261.2 | 791.2 | 734.9 | 726.3
1099.2 | 879.2 | 263.3 | 805.1 | 752.1 | 731.4
1100.2 | 880.2 | 264.3 | 808.1 | 770.8 | 735.6
1101.2 | 881.2 | 261.9 | 826.5 | 772.6 | 736.3
1102.2 | 882.2 | 261.4 | 821.7 | 781.3 | 740.9
1103.2 | 883.2 | 259.9 | 801.3 | 779.5 | 742.8
1104.2 | 884.2 | 259.8 | 774.9 | 752.8 | 732.4
1105.2 | 885.2 | 257.8 | 768 | 719.4 | 720.2
1106.2 | 886.2 | 257.8 | 764 | 699.5 | 710.6
1107.2 | 887.2 | 259.6 | 772.4 | 718.2 | 711.1
1108.2 | 888.2 | 255.7 | 771.9 | 736.1 | 725.8
1109.2 | 889.2 | 253.2 | 765.3 | 728 | 725.1
1110.2 | 890.2 | 252.9 | 763.4 | 735.6 | 728
1111.2 | 891.2 | 254.6 | 749.6 | 735.3 | 733.4
1112.2 | 892.2 | 256.7 | 745.9 | 737.1 | 741.4
1113.2 | 893.2 | 258 | 757.3 | 726.5 | 733.6
1114.2 | 894.2 | 257.7 | 784.1 | 722.3 | 723.8
1115.2 | 895.2 | 257.9 | 802.8 | 746 | 722.5
1116.2 | 896.2 | 256 | 817.6 | 778 | 731.8
1117.2 | 897.2 | 255.9 | 828.6 | 787.6 | 741.4
1118.2 | 898.2 | 255.4 | 828.4 | 758.9 | 729
1119.2 | 899.2 | 254.5 | 820.9 | 731.6 | 713.1
1120.2 | 900.2 | 252.6 | 814.1 | 736.3 | 710.8
1121.2 | 901.2 | 252.6 | 808.8 | 740 | 714.8
1122.2 | 902.2 | 256 | 809 | 744.7 | 715.2
1123.2 | 903.2 | 256.7 | 798.7 | 715.1 | 703.3
1124.2 | 904.2 | 261.1 | 781.2 | 701.3 | 694
1125.2 | 905.2 | 261.4 | 778.4 | 685.9 | 690.4
1126.2 | 906.2 | 259.7 | 781.5 | 677.5 | 685.7
1127.2 | 907.2 | 261.1 | 776.6 | 654.9 | 680.4
1128.2 | 908.2 | 262.1 | 758.5 | 662.1 | 680.7
1129.2 | 909.2 | 260.5 | 748.3 | 644.7 | 680.2
1130.2 | 910.2 | 258.1 | 761.3 | 648.5 | 672.8
1131.2 | 911.2 | 255.4 | 791.7 | 687.2 | 682.9
1132.2 | 912.2 | 254.9 | 797.3 | 715.4 | 700.3
1133.2 | 913.2 | 258.2 | 777.9 | 731 | 718.4
1134.2 | 914.2 | 257.1 | 770.5 | 755.2 | 729.3
1135.2 | 915.2 | 256 | 779.4 | 771.4 | 736.9
1136.2 | 916.2 | 256.3 | 749.1 | 752.8 | 735.1
1137.2 | 917.2 | 255.8 | 722.5 | 732.7 | 730.7
1138.2 | 918.2 | 258.1 | 706.8 | 748.9 | 736.9
1139.2 | 919.2 | 259.6 | 699.8 | 756.8 | 739.6
1140.2 | 920.2 | 257 | 702.2 | 758.2 | 745.1
1141.2 | 921.2 | 254.7 | 700.8 | 754.1 | 741.7
1142.2 | 922.2 | 251.3 | 684.4 | 744.6 | 730.9
1143.2 | 923.2 | 249 | 677.5 | 737.7 | 729.8
1144.2 | 924.2 | 251.4 | 669.2 | 743.2 | 733
1145.2 | 925.2 | 253.1 | 677.4 | 765.6 | 738.9
1146.2 | 926.2 | 252.7 | 695.3 | 757.6 | 739.5
1147.2 | 927.2 | 250.4 | 721.4 | 761.7 | 732.1
1148.2 | 928.2 | 251.2 | 748.7 | 788.6 | 737.2
1149.2 | 929.2 | 253.5 | 747.5 | 796.2 | 744.8
1150.2 | 930.2 | 253.3 | 757.5 | 811.5 | 749.6
1151.2 | 931.2 | 255.5 | 774.7 | 781.2 | 736.8
1152.2 | 932.2 | 254.6 | 781.2 | 753.7 | 718.5
1153.2 | 933.2 | 252.7 | 780.1 | 751.3 | 712.6
1154.2 | 934.2 | 253.7 | 780.1 | 721.8 | 702
1155.2 | 935.2 | 255.2 | 776.1 | 683 | 693.4
1156.2 | 936.2 | 256.1 | 769.4 | 668.8 | 688.5
1157.2 | 937.2 | 254.5 | 768 | 704.8 | 704.8
1158.2 | 938.2 | 256 | 774.1 | 719.9 | 722.8
1159.2 | 939.2 | 254.9 | 784.1 | 739.9 | 728.4
1160.2 | 940.2 | 250.2 | 789.7 | 750.9 | 729.9
1161.2 | 941.2 | 248.8 | 798.1 | 749.9 | 731.4
1162.2 | 942.2 | 248.7 | 786.7 | 772.7 | 742.6
1163.2 | 943.2 | 245.9 | 787.7 | 777.8 | 740.2
1164.2 | 944.2 | 243.8 | 797 | 767.4 | 729.7
1165.2 | 945.2 | 244.1 | 800 | 787.2 | 739.9
1166.2 | 946.2 | 244 | 788.4 | 793.4 | 748
1167.2 | 947.2 | 244.3 | 776.8 | 803.4 | 754
1168.2 | 948.2 | 244.8 | 747.2 | 756.6 | 735.7
1169.2 | 949.2 | 240.8 | 693.8 | 687.3 | 704
1170.2 | 950.2 | 235.8 | 649.6 | 630.8 | 683.3
1171.2 | 951.2 | 231.1 | 613.4 | 584.6 | 670.7
1172.2 | 952.2 | 225 | 579.2 | 545.9 | 660.9
1173.2 | 953.2 | 220.1 | 549.2 | 511.4 | 656.4
1174.2 | 954.2 | 214.6 | 519.8 | 479.8 | 647.9
1175.2 | 955.2 | 208 | 498.7 | 454.6 | 642.2
1176.2 | 956.2 | 202.2 | 481.5 | 432.5 | 639
1177.2 | 957.2 | 195.8 | 465.2 | 413.2 | 637.1
1178.2 | 958.2 | 191.2 | 448.8 | 394.8 | 632.8
1179.2 | 959.2 | 186.5 | 433.1 | 378 | 627.5
1180.2 | 960.2 | 182.3 | 420.3 | 363 | 623.6
1181.2 | 961.2 | 178.4 | 408.4 | 348.8 | 618.3
1182.2 | 962.2 | 174.7 | 397.4 | 335.6 | 613.8
1183.2 | 963.2 | 172 | 386.8 | 323.9 | 609.8
1184.2 | 964.2 | 169 | 376.3 | 312.8 | 605.3
1185.2 | 965.2 | 166.4 | 365.8 | 300.4 | 598.5
1186.2 | 966.2 | 164.1 | 356.3 | 289.3 | 593.4
1187.2 | 967.2 | 161.4 | 347 | 278.2 | 589
1188.2 | 968.2 | 158.9 | 337.9 | 269.1 | 586
1189.2 | 969.2 | 156.4 | 329 | 260.4 | 582.5
1190.2 | 970.2 | 154.5 | 320.5 | 252.1 | 578.6
1191.2 | 971.2 | 152.8 | 312.3 | 243.9 | 574.5
1192.2 | 972.2 | 150.8 | 304.7 | 236.1 | 570
1193.2 | 973.2 | 148.6 | 297.5 | 228.8 | 565.5
1194.2 | 974.2 | 146.2 | 290.5 | 222 | 561.3
1195.2 | 975.2 | 144.1 | 283.7 | 215.4 | 557.1
1196.2 | 976.2 | 142.5 | 277.3 | 209.6 | 553.1
1197.2 | 977.2 | 141.2 | 271.6 | 204.3 | 549
1198.2 | 978.2 | 139.9 | 266.3 | 199.4 | 544.6
1199.2 | 979.2 | 138.7 | 261.2 | 194.5 | 540.3
1200.2 | 980.2 | 137.3 | 256.1 | 190 | 536.7
1201.2 | 981.2 | 135.7 | 251.2 | 185.3 | 532.6
1202.2 | 982.2 | 134.4 | 246.3 | 180.6 | 528.2
1203.2 | 983.2 | 132.8 | 241.7 | 176.2 | 524.2
1204.2 | 984.2 | 130.3 | 237.2 | 172.1 | 520.3
1205.2 | 985.2 | 128.3 | 233 | 168.2 | 516.1
1206.2 | 986.2 | 126.7 | 228.9 | 164.4 | 512.2
1207.2 | 987.2 | 125.4 | 224.8 | 160.8 | 508.3
1208.2 | 988.2 | 124.4 | 220.7 | 157.4 | 504.6
1209.2 | 989.2 | 123.1 | 217.1 | 154.1 | 500.9
1210.2 | 990.2 | 121.4 | 213.5 | 151.1 | 497.4
1211.2 | 991.2 | 119.8 | 210.1 | 148.3 | 493.7
1212.2 | 992.2 | 118.7 | 206.7 | 145.4 | 490
1213.2 | 993.2 | 117.7 | 203.3 | 142.7 | 486.3
1214.2 | 994.2 | 116.4 | 200 | 140.2 | 482.8
1215.2 | 995.2 | 115.4 | 196.8 | 137.7 | 479.2
1216.2 | 996.2 | 114.7 | 193.7 | 134.8 | 475.6
1217.2 | 997.2 | 113.6 | 190.5 | 132 | 472.3
1218.2 | 998.2 | 112.4 | 187.7 | 129.3 | 469
1219.2 | 999.2 | 111.8 | 184.8 | 127 | 465.9
1220.2 | 1000.2 | 111.2 | 182.1 | 125 | 463.1
1221.2 | 1001.2 | 110.4 | 179.7 | 123 | 460.1
1222.2 | 1002.2 | 109.1 | 177 | 121.1 | 457.3
1223.2 | 1003.2 | 108 | 174.6 | 119.2 | 454.2
1224.2 | 1004.2 | 107.4 | 172.3 | 117.4 | 451.1
1225.2 | 1005.2 | 106.2 | 171.3 | 115.7 | 448.5
1226.2 | 1006.2 | 105.5 | 168.8 | 114 | 445.9
1227.2 | 1007.2 | 105 | 166 | 112.1 | 442.8
1228.2 | 1008.2 | 104.2 | 163.5 | 110.4 | 439.8
1229.2 | 1009.2 | 103.4 | 161.7 | 108.9 | 437.1
1230.2 | 1010.2 | 102.6 | 160.4 | 107.5 | 434.6
1231.2 | 1011.2 | 102.1 | 158.9 | 106 | 431.6
1232.2 | 1012.2 | 101.6 | 157.4 | 104.6 | 428.7
1233.2 | 1013.2 | 101 | 155.2 | 103 | 426.3
1234.2 | 1014.2 | 100.1 | 153.2 | 101.6 | 424.1
1235.2 | 1015.2 | 98.9 | 151 | 100.4 | 421.4
1236.2 | 1016.2 | 98.1 | 149.2 | 99.2 | 418.6
1237.2 | 1017.2 | 97.2 | 147.1 | 97.9 | 415.7
1238.2 | 1018.2 | 96.6 | 145 | 96.7 | 413.2
1239.2 | 1019.2 | 95.8 | 143 | 95.5 | 410.6
1240.2 | 1020.2 | 95.2 | 141 | 94.2 | 408.1
1241.2 | 1021.2 | 94.8 | 138.8 | 93 | 405.8
1242.2 | 1022.2 | 93.9 | 136.9 | 91.7 | 403.3
1243.2 | 1023.2 | 93.1 | 135.4 | 90.6 | 400.9
1244.2 | 1024.2 | 92.5 | 133.8 | 89.5 | 398.5
1245.2 | 1025.2 | 92.2 | 132.3 | 88.4 | 396.2
1246.2 | 1026.2 | 91.7 | 130.5 | 87.4 | 394.1
1247.2 | 1027.2 | 90.9 | 129.2 | 86.4 | 391.6
1248.2 | 1028.2 | 90 | 128 | 85.4 | 389.1
1249.2 | 1029.2 | 89.3 | 126.7 | 84.4 | 386.2
1250.2 | 1030.2 | 88.7 | 125.2 | 83.6 | 384.1
1251.2 | 1031.2 | 87.9 | 124.1 | 82.8 | 381.8
1252.2 | 1032.2 | 87.3 | 122.7 | 82.1 | 379.6
1253.2 | 1033.2 | 86.8 | 121.4 | 81.4 | 377.6
1254.2 | 1034.2 | 86.2 | 120.1 | 80.7 | 376
1255.2 | 1035.2 | 85.4 | 119.2 | 79.8 | 375.1
1256.2 | 1036.2 | 84.6 | 118.3 | 79.2 | 373.2
1257.2 | 1037.2 | 83.9 | 117 | 78.6 | 371.2
1258.2 | 1038.2 | 83.6 | 115.9 | 78 | 368.9
1259.2 | 1039.2 | 83 | 114.8 | 77.3 | 366.1
1260.2 | 1040.2 | 82.3 | 113.9 | 76.7 | 363.4
1261.2 | 1041.2 | 81.8 | 113.2 | 76.1 | 361.2
1262.2 | 1042.2 | 81.3 | 112.5 | 75.6 | 359.3
1263.2 | 1043.2 | 80.7 | 111.7 | 75.1 | 357.8
1264.2 | 1044.2 | 80.2 | 110.8 | 74.6 | 356.2
1265.2 | 1045.2 | 79.6 | 109.9 | 74.1 | 354.5
1266.2 | 1046.2 | 79 | 109 | 73.7 | 352.8
1267.2 | 1047.2 | 78.7 | 108.2 | 73.2 | 351.1
1268.2 | 1048.2 | 78.1 | 107.4 | 72.6 | 349.2
1269.2 | 1049.2 | 77.6 | 106.6 | 72.1 | 347.6
1270.2 | 1050.2 | 77.2 | 105.8 | 71.7 | 346
1271.2 | 1051.2 | 76.9 | 105 | 71.4 | 344.2
1272.2 | 1052.2 | 76.4 | 104.2 | 71 | 342.6
1273.2 | 1053.2 | 76.2 | 103.4 | 70.6 | 341.2
1274.2 | 1054.2 | 75.8 | 102.6 | 70.3 | 340
1275.2 | 1055.2 | 75.8 | 101.9 | 70 | 338.3
1276.2 | 1056.2 | 75.5 | 101.2 | 69.5 | 336
1277.2 | 1057.2 | 75.1 | 100.5 | 69.1 | 334.1
1278.2 | 1058.2 | 74.5 | 99.8 | 68.7 | 332.5
1279.2 | 1059.2 | 74.1 | 99.1 | 68.3 | 331.2
1280.2 | 1060.2 | 73.5 | 98.5 | 67.9 | 329.6
1281.2 | 1061.2 | 72.9 | 97.9 | 67.4 | 327.8
1282.2 | 1062.2 | 72.5 | 97.2 | 67 | 326
1283.2 | 1063.2 | 72.4 | 96.5 | 66.7 | 324.4
1284.2 | 1064.2 | 72.3 | 95.9 | 66.3 | 322.5
1285.2 | 1065.2 | 72.5 | 95.2 | 66 | 320.7
1286.2 | 1066.2 | 72.5 | 94.6 | 65.7 | 319.3
1287.2 | 1067.2 | 72.3 | 94.1 | 65.4 | 317.8
1288.2 | 1068.2 | 72.2 | 93.5 | 65.2 | 316.4
1289.2 | 1069.2 | 72.2 | 93 | 64.9 | 315.2
1290.2 | 1070.2 | 72.2 | 92.5 | 64.5 | 313.7
1291.2 | 1071.2 | 72.2 | 92.1 | 64.2 | 312.4
1292.2 | 1072.2 | 71.9 | 91.6 | 64 | 310.9
1293.2 | 1073.2 | 72 | 91.1 | 63.8 | 309.2
1294.2 | 1074.2 | 71.9 | 90.8 | 63.6 | 307.7
1295.2 | 1075.2 | 71.3 | 90.3 | 63.3 | 306.3
1296.2 | 1076.2 | 71.2 | 89.9 | 63.1 | 305.2
1297.2 | 1077.2 | 70.8 | 89.5 | 62.8 | 304.3
1298.2 | 1078.2 | 70.7 | 89.2 | 62.5 | 303
1299.2 | 1079.2 | 70.6 | 89 | 62.1 | 301.4
1300.2 | 1080.2 | 70.3 | 88.8 | 61.8 | 300.1
1301.2 | 1081.2 | 70.3 | 88.7 | 61.6 | 299
1302.2 | 1082.2 | 70.3 | 88 | 61.3 | 297.6
1303.2 | 1083.2 | 70.3 | 88.5 | 61 | 296
1304.2 | 1084.2 | 70.1 | 89.3 | 60.8 | 294.6
1305.2 | 1085.2 | 69.8 | 89.6 | 60.6 | 292.7
1306.2 | 1086.2 | 69.5 | 89.2 | 60.4 | 291.4
1307.2 | 1087.2 | 69.7 | 88.2 | 60 | 289.9
1308.2 | 1088.2 | 69.4 | 87.3 | 59.7 | 288.2
1309.2 | 1089.2 | 68.9 | 86.4 | 59.5 | 287
1310.2 | 1090.2 | 68.7 | 85.7 | 59.3 | 285.7
1311.2 | 1091.2 | 68.8 | 85.1 | 59 | 284.3
1312.2 | 1092.2 | 69 | 84.5 | 58.8 | 282.9
1313.2 | 1093.2 | 69.2 | 83.9 | 58.6 | 281.5
1314.2 | 1094.2 | 69.4 | 83.4 | 58.5 | 280.5
1315.2 | 1095.2 | 69.5 | 82.9 | 58.2 | 279.3
1316.2 | 1096.2 | 69.5 | 82.3 | 58 | 277.9
1317.2 | 1097.2 | 69.1 | 81.9 | 57.9 | 276.9
1318.2 | 1098.2 | 69.2 | 81.5 | 57.7 | 275.8
1319.2 | 1099.2 | 69.2 | 80.9 | 57.5 | 274.5
1320.2 | 1100.2 | 68.6 | 80.5 | 57.3 | 273.3
1321.2 | 1101.2 | 68.2 | 80 | 57.1 | 272.3
1322.2 | 1102.2 | 67.7 | 79.6 | 56.8 | 271.4
1323.2 | 1103.2 | 67.3 | 79.1 | 56.6 | 269.8
1324.2 | 1104.2 | 67.3 | 78.7 | 56.3 | 268.1
1325.2 | 1105.2 | 67.2 | 78.4 | 56.1 | 266.7
1326.2 | 1106.2 | 66.9 | 78 | 55.8 | 265.9
1327.2 | 1107.2 | 66.5 | 77.6 | 55.6 | 265
1328.2 | 1108.2 | 66.1 | 77.2 | 55.4 | 263.9
1329.2 | 1109.2 | 65.8 | 76.9 | 55.2 | 262.6
1330.2 | 1110.2 | 65.6 | 76.5 | 55.1 | 261.6
1331.2 | 1111.2 | 65.2 | 76.3 | 54.9 | 260.5
1332.2 | 1112.2 | 64.9 | 76 | 54.7 | 259.4
1333.2 | 1113.2 | 64.8 | 75.7 | 54.5 | 258.3
1334.2 | 1114.2 | 64.6 | 75.3 | 54.3 | 257.3
1335.2 | 1115.2 | 64.4 | 74.9 | 54 | 256.5
1336.2 | 1116.2 | 63.8 | 74.7 | 54 | 255.2
1337.2 | 1117.2 | 63.9 | 74.6 | 53.9 | 254.2
1338.2 | 1118.2 | 64.2 | 74.4 | 53.7 | 253.7
1339.2 | 1119.2 | 64.2 | 74.3 | 53.7 | 252.3
1340.2 | 1120.2 | 64.1 | 74 | 53.4 | 251.3
1341.2 | 1121.2 | 63.7 | 73.6 | 53.1 | 250.3
1342.2 | 1122.2 | 63.2 | 73.3 | 53 | 248.6
1343.2 | 1123.2 | 62.9 | 73.1 | 52.8 | 247.6
1344.2 | 1124.2 | 62.8 | 72.8 | 52.5 | 246.3
1345.2 | 1125.2 | 62.8 | 72.6 | 52.4 | 244.7
1346.2 | 1126.2 | 62.8 | 72.5 | 52.2 | 243.5
1347.2 | 1127.2 | 62.7 | 72.3 | 52.1 | 242.7
1348.2 | 1128.2 | 62.4 | 72.1 | 52 | 242.2
1349.2 | 1129.2 | 62.2 | 71.8 | 51.8 | 241.6
1350.2 | 1130.2 | 62.1 | 71.6 | 51.7 | 241.1
1351.2 | 1131.2 | 61.7 | 71.3 | 51.6 | 240.6
1352.2 | 1132.2 | 61.6 | 70.9 | 51.5 | 240.3
1353.2 | 1133.2 | 61.4 | 70.6 | 51.4 | 239
1354.2 | 1134.2 | 61.1 | 70.2 | 51.3 | 237.9
1355.2 | 1135.2 | 60.8 | 69.8 | 51.2 | 237
1356.2 | 1136.2 | 60.5 | 69.5 | 51.1 | 236
1357.2 | 1137.2 | 60.3 | 69.6 | 50.9 | 235.5
1358.2 | 1138.2 | 60 | 69.5 | 50.8 | 234.9
1359.2 | 1139.2 | 59.7 | 69.2 | 50.8 | 234
1360.2 | 1140.2 | 59.7 | 68.9 | 50.5 | 233.2
1361.2 | 1141.2 | 59.6 | 68.7 | 50.4 | 232
1362.2 | 1142.2 | 59.9 | 68.4 | 50.4 | 230.7
1363.2 | 1143.2 | 60.1 | 68.2 | 50.2 | 229.7
1364.2 | 1144.2 | 60 | 67.8 | 50.1 | 228.6
1365.2 | 1145.2 | 59.7 | 67.5 | 49.9 | 227.2
1366.2 | 1146.2 | 59.6 | 67.1 | 49.7 | 226.3
1367.2 | 1147.2 | 59.6 | 66.8 | 49.6 | 225.4
1368.2 | 1148.2 | 59.6 | 66.6 | 49.5 | 224.4
1369.2 | 1149.2 | 59.3 | 66.4 | 49.4 | 223.3
1370.2 | 1150.2 | 59.1 | 66.2 | 49.2 | 222.4
1371.2 | 1151.2 | 58.9 | 65.9 | 49.1 | 221.7
1372.2 | 1152.2 | 58.6 | 65.7 | 49 | 221
1373.2 | 1153.2 | 58.3 | 65.6 | 48.9 | 220
1374.2 | 1154.2 | 58 | 65.6 | 48.8 | 219
1375.2 | 1155.2 | 57.9 | 65.4 | 48.6 | 217.9
1376.2 | 1156.2 | 57.5 | 65.3 | 48.5 | 217.1
1377.2 | 1157.2 | 57.2 | 65.1 | 48.3 | 216.4
1378.2 | 1158.2 | 57.3 | 65.2 | 48.2 | 215.9
1379.2 | 1159.2 | 57.3 | 65.3 | 48 | 215.4
1380.2 | 1160.2 | 57 | 64.9 | 47.8 | 214.6
1381.2 | 1161.2 | 56.8 | 64.5 | 47.7 | 213.6
1382.2 | 1162.2 | 56.8 | 64.2 | 47.7 | 213.1
1383.2 | 1163.2 | 56.5 | 63.8 | 47.6 | 212.4
1384.2 | 1164.2 | 56.3 | 63.5 | 47.5 | 211.4
1385.2 | 1165.2 | 56.2 | 63.1 | 47.3 | 210.4
1386.2 | 1166.2 | 56 | 62.9 | 47.2 | 209.3
1387.2 | 1167.2 | 55.8 | 62.7 | 47.2 | 208.3
1388.2 | 1168.2 | 56 | 62.6 | 47.2 | 207.5
1389.2 | 1169.2 | 56 | 62.4 | 47.2 | 207.1
1390.2 | 1170.2 | 56 | 62.2 | 47.1 | 206.2
1391.2 | 1171.2 | 55.9 | 62 | 47.1 | 205.3
1392.2 | 1172.2 | 55.9 | 61.8 | 47 | 204.4
1393.2 | 1173.2 | 56.1 | 61.7 | 46.9 | 203.5
1394.2 | 1174.2 | 56.2 | 61.7 | 46.9 | 203
1395.2 | 1175.2 | 56.4 | 61.6 | 46.8 | 202.4
1396.2 | 1176.2 | 56.6 | 61.5 | 46.7 | 201.7
1397.2 | 1177.2 | 56.8 | 61.3 | 46.7 | 201.1
1398.2 | 1178.2 | 56.8 | 61.1 | 46.6 | 200.4
1399.2 | 1179.2 | 56.9 | 60.9 | 46.5 | 199.3
1400.2 | 1180.2 | 56.8 | 60.6 | 46.4 | 198.5
1401.2 | 1181.2 | 56.7 | 60.5 | 46.3 | 197.8
1402.2 | 1182.2 | 56.9 | 60.4 | 46.2 | 196.8
1403.2 | 1183.2 | 56.9 | 60.4 | 46.2 | 196.3
1404.2 | 1184.2 | 56.6 | 60.4 | 46 | 195.6
1405.2 | 1185.2 | 56.3 | 60.5 | 45.9 | 195
1406.2 | 1186.2 | 56 | 60.2 | 45.9 | 194.8
1407.2 | 1187.2 | 55.7 | 60.2 | 45.8 | 194.2
1408.2 | 1188.2 | 55.4 | 60.4 | 45.7 | 193.5
1409.2 | 1189.2 | 55.2 | 60.6 | 45.7 | 193
1410.2 | 1190.2 | 55.1 | 60.5 | 45.5 | 192.6
1411.2 | 1191.2 | 55.2 | 60.2 | 45.5 | 191.9
1412.2 | 1192.2 | 55.3 | 60 | 45.3 | 191.2
1413.2 | 1193.2 | 55 | 59.8 | 45.2 | 190.5
1414.2 | 1194.2 | 54.7 | 59.7 | 45.1 | 189.8
1415.2 | 1195.2 | 54.5 | 59.8 | 45.1 | 188.8
1416.2 | 1196.2 | 54.5 | 59.6 | 45 | 187.9
1417.2 | 1197.2 | 54.7 | 59.3 | 44.8 | 187
1418.2 | 1198.2 | 54.4 | 59 | 44.8 | 186.5
1419.2 | 1199.2 | 54.2 | 58.8 | 44.6 | 185.4
1420.2 | 1200.2 | 54 | 58.6 | 44.6 | 184.5
1421.2 | 1201.2 | 54 | 58.4 | 44.6 | 184
1422.2 | 1202.2 | 53.8 | 58.1 | 44.5 | 183.5
1423.2 | 1203.2 | 53.6 | 57.9 | 44.5 | 182.7
1424.2 | 1204.2 | 53.5 | 57.8 | 44.4 | 181.8
1425.2 | 1205.2 | 53.5 | 57.6 | 44.3 | 181.2
1426.2 | 1206.2 | 53.3 | 57.5 | 44.3 | 180.8
1427.2 | 1207.2 | 53.1 | 57.5 | 44.2 | 180.3
1428.2 | 1208.2 | 53.1 | 57.4 | 44.1 | 179.7
1429.2 | 1209.2 | 53 | 57.3 | 44 | 179.1
1430.2 | 1210.2 | 52.9 | 57.1 | 44 | 178.5
1431.2 | 1211.2 | 52.8 | 57 | 43.9 | 178.2
1432.2 | 1212.2 | 52.8 | 57 | 43.9 | 177.6
1433.2 | 1213.2 | 52.7 | 56.9 | 43.8 | 177.1
1434.2 | 1214.2 | 52.5 | 56.7 | 43.8 | 176.7
1435.2 | 1215.2 | 52.4 | 56.7 | 43.8 | 176.6
1436.2 | 1216.2 | 52.2 | 56.5 | 43.8 | 176.2
1437.2 | 1217.2 | 52.1 | 56.4 | 43.8 | 175.5
1438.2 | 1218.2 | 52 | 56.3 | 43.8 | 175.1
1439.2 | 1219.2 | 52 | 56.2 | 43.8 | 174.7
1440.2 | 1220.2 | 52 | 56.1 | 43.7 | 173.7
1441.2 | 1221.2 | 52.3 | 56 | 43.6 | 172.9
1442.2 | 1222.2 | 52.4 | 55.9 | 43.5 | 171.9
1443.2 | 1223.2 | 52.4 | 55.7 | 43.4 | 171
1444.2 | 1224.2 | 52.1 | 55.5 | 43.3 | 170.3
1445.2 | 1225.2 | 51.9 | 55.4 | 43.3 | 169.8
1446.2 | 1226.2 | 51.8 | 55.3 | 43.1 | 169.3
1447.2 | 1227.2 | 51.6 | 55.3 | 43 | 168.5
1448.2 | 1228.2 | 51.4 | 55.3 | 42.9 | 167.8
1449.2 | 1229.2 | 51.2 | 55.2 | 42.9 | 167.4
1450.2 | 1230.2 | 51 | 55.1 | 42.8 | 166.9
1451.2 | 1231.2 | 50.9 | 55 | 42.8 | 166.4
1452.2 | 1232.2 | 50.7 | 54.9 | 42.7 | 166
1453.2 | 1233.2 | 50.7 | 54.9 | 42.7 | 165.5
1454.2 | 1234.2 | 50.9 | 54.9 | 42.7 | 165.2
1455.2 | 1235.2 | 51 | 54.9 | 42.7 | 164.7
1456.2 | 1236.2 | 51 | 54.8 | 42.7 | 164.3
1457.2 | 1237.2 | 50.8 | 54.7 | 42.7 | 163.6
1458.2 | 1238.2 | 50.7 | 54.6 | 42.7 | 163.2
1459.2 | 1239.2 | 50.7 | 54.5 | 42.6 | 162.9
1460.2 | 1240.2 | 51 | 54.5 | 42.6 | 162.4
1461.2 | 1241.2 | 51.2 | 54.4 | 42.6 | 161.9
1462.2 | 1242.2 | 51.3 | 54.3 | 42.5 | 161.5
1463.2 | 1243.2 | 51.6 | 54.3 | 42.5 | 161
1464.2 | 1244.2 | 51.5 | 54.2 | 42.4 | 160.3
1465.2 | 1245.2 | 51.4 | 54.2 | 42.3 | 159.8
1466.2 | 1246.2 | 51.3 | 54.2 | 42.2 | 159.3
1467.2 | 1247.2 | 51.3 | 54.3 | 42.1 | 158.8
1468.2 | 1248.2 | 51.3 | 54.5 | 42 | 158.2
1469.2 | 1249.2 | 51.2 | 54.2 | 42 | 157.6
1470.2 | 1250.2 | 51.2 | 54.1 | 41.9 | 157.4
1471.2 | 1251.2 | 51.3 | 54 | 41.9 | 156.7
1472.2 | 1252.2 | 51.3 | 53.8 | 41.8 | 155.9
1473.2 | 1253.2 | 51.2 | 53.5 | 41.7 | 155.4
1474.2 | 1254.2 | 51.1 | 53.3 | 41.7 | 154.7

## Test Facts
Last row in IRMS data sheets: | 14
Time when gas burner was ignited: | 220