## Test Conditions
CAROLFIRE Intermediate Scale Preliminary Test Number IP-2
Test Date: | 2006-10-12
Ignition Time Relative to Thermal Data: | 526 | s
Ignition Time Relative to Electrical Data: | 220 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Thermal Data
Time (s) |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | Location A - 3/C cable |  |  | Location A - 7/C cable |  |  | Location A - Tray
Recorded Time (s) | Offset Time (s) | Gas Flow Controller Flow Rate Reading | Actual Gas Flow Rate (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | Oxygen concentration (%) | Outlet stack Temperature | Differential pressure at stack *10 | Cable Temp | Temp Above Cable | Temp Below Cable | Cable Temp | Temp Above Cable | Temp Below Cable | DUT 8: cable tray rung above the flame
0 | -526 | -6.5 | 0 | 0 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
1 | -525 | -6.6 | 0 | 0 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.3 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
2 | -524 | -6.5 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.6 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
3 | -523 | -6.5 | 0 | 0 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
4 | -522 | -6.5 | 0 | 0 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.3 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
5 | -521 | -6.4 | 0 | 0 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
6 | -520 | -6.5 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
7 | -519 | -6.5 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
8 | -518 | -6.6 | 0 | 0 | 17.6 | 17.6 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.4 | 17.8
9 | -517 | -6.5 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.3 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
10 | -516 | -6.6 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.3 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
11 | -515 | -6.6 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.8 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
12 | -514 | -6.5 | 0 | 0 | 17.6 | 17.5 | 17.4 | 17.4 | 17.4 | 16.7 | 21.5 | 16.8 | 1.4 | 16.4 | 16.3 | 16.4 | 16.8 | 16.1 | 16.3 | 17.8
495.2 | -30.8 | -6.7 | 0 | 0 | 17.5 | 17.7 | 17.5 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.3 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
496.2 | -29.8 | -6.6 | 0 | 0 | 17.5 | 17.7 | 17.5 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
497.2 | -28.8 | -6 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.6 | 17 | 1.5 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
498.2 | -27.8 | -6.5 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.6 | 17 | 1.4 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
499.2 | -26.8 | -6.5 | 0 | 0 | 17.5 | 17.7 | 17.5 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
500.2 | -25.8 | -6.4 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.3 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
501.2 | -24.8 | -6.6 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.6 | 17 | 1.7 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
502.2 | -23.8 | -6.7 | 0 | 0 | 17.5 | 17.7 | 17.5 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.7 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
503.2 | -22.8 | -6.7 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.6 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
504.2 | -21.8 | -6.7 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.7 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
505.2 | -20.8 | -6.7 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.8 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
506.2 | -19.8 | -6.7 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.6 | 17 | 1.9 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
507.2 | -18.8 | -6.6 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.9 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
508.2 | -17.8 | -6.4 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.8 | 16.5 | 16.4 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
509.2 | -16.8 | -6.1 | 0 | 0 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.8 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
510.2 | -15.8 | -6 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.5 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
511.2 | -14.8 | -5.8 | 0 | 0 | 17.5 | 17.8 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.8 | 16.5 | 16.4 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
512.2 | -13.8 | -5.7 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.9 | 16.5 | 16.4 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
513.2 | -12.8 | -5.6 | 0 | 0 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.8 | 16.5 | 16.4 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
514.2 | -11.8 | -5.4 | 0 | 0 | 17.5 | 17.8 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.8 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
515.2 | -10.8 | -5.3 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.6 | 17.6 | 17 | 21.7 | 17 | 1.7 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
516.2 | -9.8 | -5.2 | 0 | 0 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.3 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
517.2 | -8.8 | -5.3 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
518.2 | -7.8 | -5.2 | 0 | 0 | 17.5 | 17.8 | 17.6 | 17.6 | 17.6 | 17 | 21.7 | 17 | 1.7 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
519.2 | -6.8 | -5.1 | 0 | 0 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.3 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
520.2 | -5.8 | -5.2 | 0 | 0 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.7 | 16.5 | 16.5 | 16.6 | 16.8 | 16.2 | 16.5 | 17.8
521.2 | -4.8 | -5.3 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.7 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
522.2 | -3.8 | -5.3 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.5 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
523.2 | -2.8 | -5.3 | 0 | 0 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
524.2 | -1.8 | -5.4 | 0 | 0 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
525.2 | -0.8 | -5.2 | 0 | 0 | 17.5 | 17.8 | 17.6 | 17.6 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.5 | 17.8
526.2 | 0.2 | 93.8 | 37.52 | 43.8587 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.6 | 17.8
527.2 | 1.2 | 373.7 | 149.48 | 174.7335 | 17.6 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.5 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.6 | 17.8
528.2 | 2.2 | 492.6 | 197.04 | 230.3284 | 17.5 | 17.7 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.5 | 16.5 | 16.5 | 16.6 | 16.8 | 16.3 | 16.6 | 17.9
529.2 | 3.2 | 516.1 | 206.44 | 241.3165 | 17.5 | 17.8 | 17.6 | 17.5 | 17.6 | 17 | 21.7 | 17 | 1.6 | 16.5 | 16.5 | 16.7 | 16.8 | 16.3 | 16.6 | 17.9
530.2 | 4.2 | 504.9 | 201.96 | 236.0796 | 17.6 | 17.8 | 17.6 | 17.6 | 17.6 | 17 | 21.7 | 17 | 1.6 | 16.5 | 16.5 | 17.2 | 16.8 | 16.7 | 18.1 | 18.1
531.2 | 5.2 | 484 | 193.6 | 226.3072 | 17.6 | 17.8 | 17.7 | 17.6 | 17.6 | 17 | 21.7 | 17 | 1.4 | 16.5 | 20.5 | 26.1 | 16.8 | 21 | 29.8 | 21.3
532.2 | 6.2 | 466.4 | 186.56 | 218.0779 | 17.7 | 17.9 | 17.8 | 17.8 | 20.1 | 17 | 21.7 | 17 | 1.4 | 16.5 | 27.5 | 42.1 | 16.9 | 31.3 | 51 | 29.8
533.2 | 7.2 | 463.1 | 185.24 | 216.5349 | 18 | 18 | 18 | 18 | 28.7 | 17 | 21.7 | 17 | 1.7 | 16.5 | 36.3 | 56.4 | 16.8 | 48.3 | 80.1 | 40.1
534.2 | 8.2 | 452.8 | 181.12 | 211.7188 | 18.3 | 18.3 | 18.4 | 18.2 | 40.1 | 17 | 21.7 | 17 | 1.9 | 16.5 | 45.5 | 82.7 | 16.9 | 68.2 | 122 | 54.4
535.2 | 9.2 | 440.7 | 176.28 | 206.0612 | 18.9 | 19.2 | 19.9 | 19 | 54.1 | 17.1 | 21.7 | 17 | 2.2 | 16.6 | 54.9 | 106.7 | 17.1 | 92.2 | 153.6 | 65.8
536.2 | 10.2 | 433.9 | 173.56 | 202.8816 | 19.9 | 20 | 22.1 | 20.2 | 65.7 | 17.1 | 21.7 | 17 | 2.4 | 16.7 | 66.3 | 133.3 | 17.4 | 112.9 | 185.1 | 81.1
537.2 | 11.2 | 430.5 | 172.2 | 201.2919 | 21 | 21 | 24.3 | 22.5 | 77.5 | 17.1 | 21.7 | 17 | 2.6 | 16.8 | 87.6 | 178.1 | 17.9 | 143.7 | 238.9 | 109
538.2 | 12.2 | 428.5 | 171.4 | 200.3567 | 22.4 | 22.2 | 26.5 | 25.7 | 88.2 | 17.1 | 21.7 | 17 | 2.7 | 16.9 | 111.6 | 215.3 | 18.6 | 173.5 | 276.5 | 133.2
539.2 | 13.2 | 427.9 | 171.16 | 200.0762 | 24.5 | 24.4 | 29.6 | 29.5 | 95.9 | 17.2 | 21.7 | 17 | 2.9 | 17.1 | 127.4 | 246 | 19.4 | 199.3 | 301.7 | 144.8
540.2 | 14.2 | 428.2 | 171.28 | 200.2165 | 26.8 | 27.8 | 32.3 | 32.9 | 103.4 | 17.2 | 21.7 | 17 | 2.7 | 17.4 | 133 | 264.1 | 20.4 | 203.5 | 310.9 | 159.8
541.2 | 15.2 | 428 | 171.2 | 200.1229 | 29.8 | 31.8 | 35.8 | 37.4 | 113.1 | 17.2 | 21.7 | 17 | 3 | 18 | 143.9 | 302.8 | 21.7 | 215.2 | 345.9 | 184.5
542.2 | 16.2 | 428.4 | 171.36 | 200.31 | 32.7 | 36 | 40.3 | 42.8 | 126.4 | 17.3 | 21.7 | 17 | 2.9 | 18.6 | 168.7 | 336.2 | 23.1 | 242.2 | 387.7 | 205.5
543.2 | 17.2 | 433.3 | 173.32 | 202.6011 | 35.7 | 39.1 | 45.7 | 47.8 | 139.1 | 17.3 | 21.7 | 17 | 2.9 | 19.2 | 174.3 | 331.6 | 24.7 | 279.2 | 392 | 200.9
544.2 | 18.2 | 437.7 | 175.08 | 204.6584 | 39.2 | 41.9 | 51.4 | 52.6 | 149.9 | 17.3 | 21.7 | 17 | 2.8 | 20 | 180.5 | 330.4 | 26.4 | 314.4 | 401.5 | 188.6
545.2 | 19.2 | 438.8 | 175.52 | 205.1728 | 42.7 | 45.9 | 57.1 | 57.7 | 162.5 | 17.3 | 21.7 | 17 | 2.6 | 20.8 | 193.7 | 367.3 | 28.4 | 346.9 | 441.1 | 199
546.2 | 20.2 | 436.8 | 174.72 | 204.2376 | 47 | 51.3 | 62.4 | 62.8 | 173.4 | 17.4 | 21.7 | 17.1 | 2.3 | 21.8 | 218.5 | 417.1 | 30.6 | 371.5 | 488.9 | 228.2
547.2 | 21.2 | 435.4 | 174.16 | 203.583 | 52 | 56.4 | 67.8 | 68.5 | 185.6 | 17.4 | 21.7 | 17.1 | 2.5 | 23 | 224 | 436.9 | 33 | 396.8 | 518.3 | 246.9
548.2 | 22.2 | 437.6 | 175.04 | 204.6117 | 56.8 | 61.1 | 74.1 | 73.4 | 196.2 | 17.4 | 21.7 | 17.1 | 2.5 | 24.2 | 231 | 444.1 | 35.7 | 436.8 | 540.4 | 250.5
549.2 | 23.2 | 438.7 | 175.48 | 205.126 | 62.1 | 66.2 | 80.1 | 77.6 | 211.6 | 17.4 | 21.7 | 17.4 | 2.3 | 25.6 | 238 | 449.9 | 38.6 | 464.4 | 546.6 | 249.3
550.2 | 24.2 | 438.4 | 175.36 | 204.9857 | 67 | 71.1 | 85.3 | 82.3 | 222.5 | 17.5 | 21.7 | 17.8 | 2.5 | 27.1 | 246.6 | 451.1 | 41.7 | 500.3 | 566.4 | 255.2
551.2 | 25.2 | 436.8 | 174.72 | 204.2376 | 72.1 | 75 | 90.9 | 87.6 | 226.5 | 17.5 | 21.7 | 18.4 | 2.9 | 28.7 | 250.9 | 461.3 | 45 | 513.7 | 576.4 | 266
552.2 | 26.2 | 437 | 174.8 | 204.3311 | 77.3 | 79.1 | 96.9 | 93.3 | 228.7 | 17.5 | 21.7 | 18.9 | 2.5 | 30.4 | 246.2 | 451.6 | 48.6 | 504 | 562.2 | 263.7
553.2 | 27.2 | 436.1 | 174.44 | 203.9103 | 82.1 | 83.3 | 102.5 | 98.7 | 231.4 | 17.5 | 21.7 | 19.5 | 2.6 | 32.1 | 241.4 | 438.1 | 52.5 | 491.1 | 545.5 | 259.5
554.2 | 28.2 | 436.4 | 174.56 | 204.0506 | 85.3 | 90.4 | 108.6 | 103.3 | 231.3 | 17.6 | 21.7 | 20.1 | 2.8 | 33.9 | 240.8 | 434.7 | 56.8 | 469.7 | 530.1 | 264.2
555.2 | 29.2 | 436.9 | 174.76 | 204.2844 | 88.9 | 99 | 113.5 | 107.4 | 229.4 | 17.6 | 21.7 | 20.9 | 2.4 | 35.8 | 239.8 | 429.9 | 61.2 | 452.8 | 516.2 | 264
556.2 | 30.2 | 436 | 174.4 | 203.8636 | 94.7 | 104.7 | 118.3 | 111.5 | 230.3 | 17.6 | 21.7 | 21.6 | 2.8 | 37.8 | 246.2 | 438.1 | 65.3 | 440.8 | 519.5 | 278.9
557.2 | 31.2 | 436 | 174.4 | 203.8636 | 99.7 | 109.5 | 124.6 | 117.2 | 231.4 | 17.6 | 21.7 | 22.3 | 3.1 | 39.7 | 245 | 428.3 | 69.3 | 430.8 | 511.2 | 278.4
558.2 | 32.2 | 435.9 | 174.36 | 203.8168 | 102.8 | 116.5 | 130.4 | 122.1 | 233 | 17.7 | 21.7 | 23 | 2.7 | 41.5 | 239.8 | 423.9 | 73.4 | 419.7 | 500.3 | 277
559.2 | 33.2 | 437.2 | 174.88 | 204.4246 | 107.8 | 120.7 | 135.2 | 127.1 | 234 | 17.8 | 21.7 | 23.8 | 2.8 | 43.2 | 236.5 | 426.9 | 77.1 | 408.7 | 498.4 | 289.7
560.2 | 34.2 | 438.2 | 175.28 | 204.8922 | 112.1 | 124.3 | 139.2 | 131.6 | 236.9 | 17.9 | 21.7 | 24.5 | 2.4 | 45 | 233.7 | 421.3 | 80.8 | 399.4 | 488.7 | 292.2
561.2 | 35.2 | 440.6 | 176.24 | 206.0144 | 114.8 | 129.5 | 142.9 | 136.2 | 239.8 | 18 | 21.7 | 25.2 | 2.2 | 46.7 | 231.3 | 417.5 | 84 | 392.2 | 482.3 | 296.1
562.2 | 36.2 | 445 | 178 | 208.0717 | 116.7 | 134.4 | 146.2 | 140 | 245.2 | 18.2 | 21.7 | 26 | 2.4 | 48.3 | 226.6 | 402.3 | 86.5 | 396 | 469.3 | 289.9
563.2 | 37.2 | 445.7 | 178.28 | 208.399 | 120.6 | 137.9 | 149.4 | 143.7 | 252.5 | 18.3 | 21.7 | 26.7 | 2.1 | 49.9 | 224.7 | 395.4 | 88.9 | 401.7 | 460.8 | 284.7
564.2 | 38.2 | 444.7 | 177.88 | 207.9315 | 124.2 | 140.9 | 154 | 146.7 | 259.7 | 18.4 | 21.7 | 27.4 | 2.2 | 51.4 | 223.4 | 385.4 | 91.2 | 424.3 | 463 | 285.5
565.2 | 39.2 | 444.9 | 177.96 | 208.025 | 126.6 | 143.8 | 156.9 | 149.6 | 265.9 | 18.5 | 21.7 | 28.1 | 2.5 | 52.9 | 229.2 | 388.8 | 93.5 | 439.4 | 470.5 | 285.9
566.2 | 40.2 | 444.4 | 177.76 | 207.7912 | 130 | 146.4 | 159.8 | 152.1 | 266.9 | 18.5 | 21.7 | 28.9 | 2.6 | 54.3 | 238.6 | 396.9 | 95.7 | 455.3 | 484.7 | 297.5
567.2 | 41.2 | 443.5 | 177.4 | 207.3704 | 133.4 | 148.8 | 162.8 | 154.3 | 266.5 | 18.7 | 21.7 | 29.8 | 2.6 | 55.8 | 235.8 | 384.6 | 97.9 | 474.7 | 470.2 | 295
568.2 | 42.2 | 443.8 | 177.52 | 207.5107 | 137.1 | 151.4 | 165.4 | 156.4 | 269.1 | 18.8 | 21.7 | 30.4 | 2.2 | 57.2 | 237.9 | 390.4 | 100.2 | 489.2 | 472.9 | 298.8
569.2 | 43.2 | 443.4 | 177.36 | 207.3236 | 139.4 | 153.4 | 167.8 | 158.4 | 273.8 | 19 | 21.7 | 31.1 | 2.3 | 58.6 | 240.7 | 395.2 | 102.6 | 506.5 | 484.1 | 305.9
570.2 | 44.2 | 443.3 | 177.32 | 207.2769 | 142.6 | 154.7 | 169.4 | 160.1 | 283.3 | 19.1 | 21.7 | 31.8 | 2.4 | 60 | 249 | 409.3 | 104.8 | 516.8 | 511.7 | 324.7
571.2 | 45.2 | 444.2 | 177.68 | 207.6977 | 144.7 | 156.4 | 170.8 | 162.1 | 289.8 | 19.3 | 21.7 | 32.1 | 2.7 | 61.5 | 282 | 448 | 106.8 | 533.7 | 543 | 346.6
572.2 | 46.2 | 443.2 | 177.28 | 207.2301 | 145.7 | 159.4 | 172.8 | 165.1 | 292.7 | 19.4 | 21.7 | 32.2 | 2.5 | 62.9 | 314.9 | 480.6 | 109.2 | 554.1 | 580.7 | 369.1
573.2 | 47.2 | 443.4 | 177.36 | 207.3236 | 146.6 | 162.1 | 175.7 | 167.5 | 300.1 | 19.4 | 21.7 | 32.5 | 2.6 | 64.4 | 345.5 | 505.2 | 111.8 | 577.3 | 604.1 | 389.5
574.2 | 48.2 | 443.5 | 177.4 | 207.3704 | 148.7 | 164.7 | 178.4 | 170.9 | 312.7 | 19.5 | 21.7 | 32.9 | 2.6 | 66 | 362.3 | 511.8 | 114.1 | 610.4 | 619.6 | 401.9
575.2 | 49.2 | 442.9 | 177.16 | 207.0898 | 150.8 | 165.8 | 180.5 | 173.6 | 329.8 | 19.7 | 21.7 | 33.1 | 2.7 | 67.6 | 368.1 | 528.5 | 116.3 | 608.2 | 626.8 | 407.7
576.2 | 50.2 | 443.6 | 177.44 | 207.4171 | 153.5 | 167.2 | 182.2 | 176.5 | 330 | 19.9 | 21.7 | 33.5 | 2.8 | 69.3 | 374.6 | 543.3 | 119.3 | 583.7 | 627 | 417.4
577.2 | 51.2 | 444.2 | 177.68 | 207.6977 | 157.4 | 170.2 | 183.5 | 180 | 325.2 | 20 | 21.6 | 33.9 | 3.3 | 71.2 | 381.8 | 544.3 | 122.3 | 563.3 | 614.6 | 411.5
578.2 | 52.2 | 443.5 | 177.4 | 207.3704 | 159.3 | 172.2 | 184 | 183.4 | 319.6 | 20.1 | 21.6 | 34.2 | 3.5 | 73.2 | 380.4 | 545.4 | 125.2 | 542.3 | 599.4 | 412.1
579.2 | 53.2 | 444.2 | 177.68 | 207.6977 | 160.4 | 175.1 | 184 | 186 | 317.6 | 20.1 | 21.6 | 34.4 | 3.1 | 75.4 | 393.4 | 561.1 | 127.9 | 529.8 | 602.8 | 420.3
580.2 | 54.2 | 443.7 | 177.48 | 207.4639 | 161.8 | 177.9 | 185 | 187.7 | 313.9 | 20.2 | 21.6 | 34.5 | 2.9 | 77.7 | 401.7 | 578.6 | 130.8 | 514.5 | 599.1 | 432.9
581.2 | 55.2 | 443.8 | 177.52 | 207.5107 | 163 | 179.5 | 186.9 | 189.4 | 315.1 | 20.2 | 21.6 | 34.7 | 2.9 | 80.1 | 419.2 | 597.2 | 134.1 | 515.5 | 612.8 | 447
582.2 | 56.2 | 444.6 | 177.84 | 207.8847 | 163.9 | 180.6 | 188.7 | 191 | 317.8 | 20.3 | 21.6 | 35 | 2.6 | 82.5 | 433.3 | 617.7 | 137.1 | 517.1 | 629.1 | 457.6
583.2 | 57.2 | 443.7 | 177.48 | 207.4639 | 164.8 | 182.7 | 189.7 | 192.4 | 323.4 | 20.3 | 21.6 | 35.3 | 2.3 | 85.3 | 442.4 | 634.4 | 139.9 | 517.1 | 641.4 | 468.9
584.2 | 58.2 | 444.6 | 177.84 | 207.8847 | 165.7 | 183.9 | 190.5 | 193 | 330.1 | 20.3 | 21.6 | 35.5 | 2.2 | 89.3 | 454.5 | 637 | 142.4 | 522.7 | 654.9 | 482.2
585.2 | 59.2 | 444.2 | 177.68 | 207.6977 | 166.6 | 185.7 | 191 | 194.3 | 335.4 | 20.3 | 21.6 | 35.8 | 2.5 | 94.8 | 482 | 660.6 | 144.8 | 527.8 | 668.3 | 498.3
586.2 | 60.2 | 444.5 | 177.8 | 207.838 | 167.9 | 188.3 | 191.6 | 195.8 | 337.7 | 20.3 | 21.6 | 36 | 2.9 | 100.8 | 508.2 | 682.7 | 145.9 | 532.7 | 684.9 | 500.9
587.2 | 61.2 | 446 | 178.4 | 208.5393 | 169.8 | 189.4 | 191.7 | 197.5 | 345.9 | 20.4 | 21.6 | 36.2 | 2.5 | 104.5 | 567.9 | 713 | 146.8 | 551.3 | 699.6 | 503.7
588.2 | 62.2 | 445.2 | 178.08 | 208.1653 | 171.2 | 189.4 | 192.2 | 199.2 | 359.6 | 20.4 | 21.6 | 36.4 | 2.6 | 105.8 | 621.5 | 738.9 | 148.1 | 559.8 | 712.5 | 504.8
589.2 | 63.2 | 445.1 | 178.04 | 208.1185 | 172.8 | 190.3 | 194 | 201.2 | 370 | 20.4 | 21.6 | 36.6 | 2.8 | 105.3 | 651.4 | 748.1 | 149.4 | 586.2 | 726.9 | 518.8
590.2 | 64.2 | 447 | 178.8 | 209.0069 | 174 | 192 | 195.8 | 202.9 | 370.7 | 20.4 | 21.6 | 36.8 | 2.9 | 103.8 | 650.8 | 742.7 | 151.1 | 615.9 | 745.8 | 534.7
591.2 | 65.2 | 446.6 | 178.64 | 208.8199 | 174.4 | 193.9 | 196.8 | 204.2 | 373.2 | 20.3 | 21.6 | 37.1 | 2.5 | 104.9 | 671.7 | 751.2 | 153 | 641.6 | 761.4 | 545.2
592.2 | 66.2 | 445.9 | 178.36 | 208.4926 | 176.3 | 196.5 | 197.3 | 205.4 | 382.2 | 20.3 | 21.6 | 37.4 | 2.8 | 107 | 694.2 | 753.1 | 155.4 | 653.8 | 764.2 | 553.6
593.2 | 67.2 | 447 | 178.8 | 209.0069 | 178 | 198.7 | 198.7 | 205.9 | 384.2 | 20.3 | 21.6 | 37.5 | 3 | 109.3 | 711.2 | 756.6 | 157.7 | 660.7 | 762.7 | 558
594.2 | 68.2 | 446.6 | 178.64 | 208.8199 | 179.7 | 199.6 | 199.6 | 206.4 | 382.9 | 20.2 | 21.6 | 37.5 | 3.4 | 112.1 | 710.7 | 748.6 | 160.3 | 661.6 | 758 | 559.5
595.2 | 69.2 | 446.3 | 178.52 | 208.6796 | 181.6 | 199.7 | 201.2 | 207.2 | 376.8 | 20.2 | 21.6 | 37.6 | 3 | 114.7 | 707.4 | 740.2 | 162.9 | 656.8 | 750 | 557.5
596.2 | 70.2 | 447.5 | 179 | 209.2407 | 183.7 | 201 | 203.1 | 207.8 | 367 | 20.4 | 21.6 | 37.8 | 3 | 117.7 | 701.1 | 730.8 | 165.6 | 663.3 | 758.2 | 564.5
597.2 | 71.2 | 447.4 | 178.96 | 209.1939 | 186.4 | 202.2 | 204.3 | 208.4 | 366.9 | 20.4 | 21.6 | 38 | 2.7 | 121.2 | 700.4 | 728.5 | 168.4 | 684.9 | 770.7 | 575.4
598.2 | 72.2 | 446.5 | 178.6 | 208.7731 | 187.1 | 204.1 | 205.7 | 208.3 | 372.1 | 20.6 | 21.6 | 38.2 | 2.8 | 124.8 | 717.6 | 720 | 171.2 | 703.9 | 774.4 | 578.3
599.2 | 73.2 | 447.6 | 179.04 | 209.2874 | 186 | 206.5 | 206.4 | 207.5 | 383.6 | 20.7 | 21.5 | 38.3 | 2.7 | 127.9 | 718.2 | 718 | 174.2 | 719.7 | 775.7 | 574
600.2 | 74.2 | 449 | 179.6 | 209.9421 | 185.8 | 207 | 207.2 | 207.4 | 389 | 20.7 | 21.5 | 38.4 | 2.3 | 132.4 | 726.6 | 725.4 | 177.3 | 725.9 | 781.8 | 576.8
601.2 | 75.2 | 448.4 | 179.36 | 209.6615 | 185.5 | 205.6 | 208.6 | 208.6 | 388.8 | 20.8 | 21.5 | 38.6 | 1.8 | 138.1 | 726.2 | 716.2 | 180.6 | 735.6 | 785.5 | 583.1
602.2 | 76.2 | 448.6 | 179.44 | 209.755 | 186.5 | 205.8 | 209.9 | 209.7 | 388.3 | 20.8 | 21.5 | 38.7 | 2 | 145 | 712.3 | 700.5 | 184 | 741.1 | 772 | 586
603.2 | 77.2 | 448.6 | 179.44 | 209.755 | 188.3 | 206.6 | 210.8 | 209.9 | 387.6 | 20.9 | 21.5 | 38.9 | 2.1 | 154.8 | 700.8 | 688.6 | 187.3 | 748.4 | 766.9 | 589.6
604.2 | 78.2 | 448.3 | 179.32 | 209.6147 | 188.8 | 206.6 | 212 | 210.1 | 386.7 | 21 | 21.5 | 39.1 | 2.3 | 161.4 | 691.3 | 667 | 190 | 755.8 | 752.8 | 579.5
605.2 | 79.2 | 448.9 | 179.56 | 209.8953 | 189.9 | 206.7 | 213.5 | 210 | 383.5 | 21.1 | 21.5 | 39.2 | 2.2 | 167.2 | 680.9 | 646.5 | 192.2 | 760.7 | 734.9 | 569.8
606.2 | 80.2 | 448.8 | 179.52 | 209.8485 | 191.2 | 208.3 | 214.5 | 210.2 | 384.7 | 21 | 21.5 | 39.4 | 2.4 | 172.6 | 674.5 | 630.4 | 194.2 | 767.9 | 720.1 | 562.9
607.2 | 81.2 | 449.4 | 179.76 | 210.1291 | 192.9 | 210.1 | 216.6 | 211 | 381 | 20.9 | 21.5 | 39.7 | 2.7 | 178.2 | 676.3 | 644 | 196.3 | 761 | 738.5 | 584.1
608.2 | 82.2 | 450 | 180 | 210.4096 | 195.1 | 210.5 | 217.3 | 211.7 | 382.5 | 20.9 | 21.5 | 40.1 | 2.3 | 183.1 | 685.2 | 659.3 | 198.4 | 768.8 | 755.2 | 603.6
609.2 | 83.2 | 449.9 | 179.96 | 210.3629 | 195.8 | 209.8 | 217.4 | 212.9 | 381.1 | 20.8 | 21.5 | 40.5 | 2.5 | 188 | 703.9 | 678 | 200.2 | 762 | 762.7 | 613
610.2 | 84.2 | 451.7 | 180.68 | 211.2045 | 195.9 | 209 | 218.4 | 214.8 | 378.6 | 20.9 | 21.5 | 40.8 | 2.7 | 192.8 | 732.8 | 686.9 | 201.7 | 760.1 | 775.8 | 620.3
611.2 | 85.2 | 452.8 | 181.12 | 211.7188 | 196.5 | 207.1 | 219.5 | 216.2 | 386.1 | 20.9 | 21.5 | 41 | 2.1 | 198.1 | 746.3 | 699.5 | 203 | 766.2 | 789.9 | 624.7
612.2 | 86.2 | 454.1 | 181.64 | 212.3267 | 196.1 | 207.3 | 220.1 | 217.2 | 391.7 | 21 | 21.5 | 41.1 | 2.3 | 203.6 | 749.3 | 697.6 | 204.2 | 776 | 798.7 | 631.3
613.2 | 87.2 | 453.9 | 181.56 | 212.2332 | 198.3 | 209.2 | 220.7 | 217.7 | 405.9 | 21.2 | 21.5 | 41.2 | 2.8 | 209.4 | 744.6 | 689.4 | 205.6 | 788.5 | 795.7 | 632.3
614.2 | 88.2 | 452.9 | 181.16 | 211.7656 | 200.8 | 210.6 | 220.8 | 218.5 | 409.8 | 21.4 | 21.5 | 41.1 | 2.1 | 215.2 | 746 | 679.6 | 206.8 | 800 | 796 | 626.1
615.2 | 89.2 | 452.2 | 180.88 | 211.4383 | 201.5 | 211.3 | 222.5 | 220.4 | 416.4 | 21.5 | 21.5 | 41.1 | 2 | 220.1 | 747.3 | 678.4 | 208.1 | 798.1 | 795.9 | 630.7
616.2 | 90.2 | 452.8 | 181.12 | 211.7188 | 201.1 | 212.3 | 224.2 | 221.9 | 415.8 | 21.6 | 21.5 | 41.1 | 2 | 226 | 741.1 | 683 | 209.7 | 770.8 | 788 | 635.9
617.2 | 91.2 | 452.9 | 181.16 | 211.7656 | 200.8 | 214.1 | 224.8 | 222.3 | 409.4 | 21.6 | 21.5 | 41 | 1.8 | 232.2 | 727.1 | 664.3 | 211.7 | 753.5 | 772 | 636.6
618.2 | 92.2 | 453.3 | 181.32 | 211.9526 | 201.3 | 215.2 | 225.1 | 223.6 | 401.8 | 21.6 | 21.5 | 41 | 2.1 | 238.4 | 714.3 | 650.2 | 213.7 | 752.7 | 765.5 | 638.4
619.2 | 93.2 | 453.5 | 181.4 | 212.0461 | 199.7 | 215.1 | 226 | 224.2 | 400.6 | 21.6 | 21.5 | 41.1 | 2.3 | 244.3 | 696.7 | 642.2 | 215.9 | 748.1 | 760.6 | 636.9
620.2 | 94.2 | 453.5 | 181.4 | 212.0461 | 198.6 | 215.8 | 226.5 | 224.6 | 393.2 | 21.7 | 21.5 | 41.2 | 2.9 | 250.1 | 683.8 | 628.8 | 218 | 756.8 | 747.3 | 632.1
621.2 | 95.2 | 454.9 | 181.96 | 212.7008 | 199.9 | 216.6 | 227.1 | 225.5 | 393 | 21.7 | 21.5 | 41.5 | 3.2 | 256 | 686.3 | 621.4 | 220.1 | 774.1 | 741.7 | 627.9
622.2 | 96.2 | 454.3 | 181.72 | 212.4202 | 200.7 | 216.9 | 227 | 225.8 | 389 | 21.9 | 21.5 | 41.7 | 2.9 | 262.7 | 700.3 | 630.9 | 222.6 | 761 | 734.9 | 634.8
623.2 | 97.2 | 453.3 | 181.32 | 211.9526 | 200.8 | 217.4 | 226.6 | 225.5 | 384.7 | 22 | 21.5 | 41.7 | 2.6 | 270 | 699.8 | 612 | 224.9 | 751.5 | 704.5 | 624.2
624.2 | 98.2 | 453 | 181.2 | 211.8124 | 202.7 | 217.7 | 225.6 | 225.1 | 384.9 | 22.1 | 21.5 | 41.8 | 2.4 | 276.4 | 706.1 | 615.2 | 227.4 | 747 | 716.5 | 626.6
625.2 | 99.2 | 453.9 | 181.56 | 212.2332 | 203 | 218 | 225.6 | 225.8 | 383 | 22.2 | 21.5 | 41.9 | 2.5 | 283.3 | 704.9 | 635.3 | 208.2 | 723.1 | 653.4 | 639.4
626.2 | 100.2 | 454.5 | 181.8 | 212.5137 | 203.1 | 219.3 | 226.2 | 226.6 | 380.4 | 22.3 | 21.5 | 42 | 2.4 | 290.6 | 709.7 | 639.1 | 132.4 | 684.9 | 395.9 | 645
627.2 | 101.2 | 454.9 | 181.96 | 212.7008 | 202.6 | 220.1 | 227.1 | 227.1 | 382.1 | 22.4 | 21.5 | 42 | 2.9 | 298.9 | 708.5 | 646.5 | 235.5 | 763.5 | 758.9 | 651.9
628.2 | 102.2 | 455.4 | 182.16 | 212.9345 | 202.1 | 220.6 | 226.9 | 227.2 | 380.4 | 22.5 | 21.5 | 42.2 | 3.2 | 308.1 | 706.4 | 645.8 | 191.2 | 611.2 | 593.5 | 655.1
629.2 | 103.2 | 454.6 | 181.84 | 212.5605 | 204.1 | 220.1 | 227 | 227.5 | 378.8 | 22.9 | 21.5 | 42.4 | 2.9 | 317.4 | 719.6 | 659.8 | 181.8 | 552.7 | 537.1 | 663.1
630.2 | 104.2 | 454.3 | 181.72 | 212.4202 | 203.9 | 219.6 | 227 | 227.8 | 383.7 | 23.1 | 21.4 | 42.5 | 3 | 327.3 | 725.4 | 676 | 243.9 | 776.5 | 775.1 | 668.3
631.2 | 105.2 | 454.5 | 181.8 | 212.5137 | 203.2 | 219.4 | 227.5 | 228.3 | 392.5 | 23.3 | 21.4 | 42.7 | 2.7 | 338 | 725.9 | 673.8 | 246.6 | 768.8 | 769.2 | 663.5
632.2 | 106.2 | 454 | 181.6 | 212.2799 | 203.3 | 220.1 | 227.7 | 228.4 | 393.8 | 23.5 | 21.4 | 42.9 | 2.7 | 348.4 | 719.2 | 661.3 | 249.2 | 763.6 | 755.2 | 660.3
633.2 | 107.2 | 451.6 | 180.64 | 211.1578 | 205.7 | 221.1 | 227 | 228.3 | 392.3 | 23.6 | 21.4 | 43.1 | 3 | 358.2 | 706.8 | 651.8 | 251.4 | 750.3 | 750.1 | 667.8
634.2 | 108.2 | 451.1 | 180.44 | 210.924 | 206.4 | 221.8 | 226.4 | 227.2 | 387.8 | 23.7 | 21.4 | 43.2 | 3.2 | 368 | 693.6 | 645.4 | 252.9 | 732.3 | 757.4 | 682.4
635.2 | 109.2 | 450.5 | 180.2 | 210.6434 | 204.8 | 222.8 | 226.6 | 226.8 | 386.8 | 23.9 | 21.4 | 43.2 | 3.5 | 377.9 | 687.9 | 649.9 | 253.7 | 712.8 | 747.1 | 680.8
636.2 | 110.2 | 451.8 | 180.72 | 211.2513 | 204.5 | 223.5 | 226.5 | 226.4 | 378.2 | 23.9 | 21.4 | 43.3 | 3.1 | 388.3 | 684.1 | 645.8 | 254.6 | 708.7 | 751.7 | 681.4
637.2 | 111.2 | 451.7 | 180.68 | 211.2045 | 204.4 | 223.3 | 225.7 | 226.3 | 374.1 | 23.9 | 21.4 | 43.3 | 2.9 | 398.2 | 668.5 | 636.4 | 256 | 696.2 | 741.5 | 678.1
638.2 | 112.2 | 452.6 | 181.04 | 211.6253 | 204 | 222.5 | 225.7 | 226.5 | 368.3 | 23.9 | 21.4 | 43.3 | 3.1 | 407.6 | 659 | 636.3 | 257.8 | 705.8 | 748 | 674.4
639.2 | 113.2 | 454 | 181.6 | 212.2799 | 203 | 222.5 | 224.7 | 227.1 | 368 | 23.9 | 21.4 | 43.5 | 2.8 | 418 | 659.7 | 636.8 | 259.6 | 720.5 | 759.6 | 685.3
640.2 | 114.2 | 455.5 | 182.2 | 212.9813 | 203.3 | 222.6 | 225 | 227.1 | 369 | 24 | 21.4 | 43.7 | 2.7 | 428.5 | 660.2 | 634.8 | 261.7 | 723.6 | 755.7 | 692.4
641.2 | 115.2 | 456.3 | 182.52 | 213.3554 | 203 | 222.9 | 224.9 | 226.8 | 366.6 | 24.1 | 21.4 | 43.8 | 2.8 | 437.9 | 661 | 637.7 | 263.6 | 729.9 | 761.5 | 692.2
642.2 | 116.2 | 456.4 | 182.56 | 213.4021 | 202.4 | 224.8 | 223.8 | 226.9 | 374.1 | 24.1 | 21.4 | 44 | 2.4 | 447.9 | 682.6 | 659.7 | 265.4 | 744.1 | 777.3 | 700.2
643.2 | 117.2 | 455.6 | 182.24 | 213.0281 | 202.5 | 224.9 | 223.4 | 226.9 | 386.1 | 24.2 | 21.4 | 44.2 | 2.2 | 457.9 | 689.5 | 663.4 | 266.7 | 748.4 | 784 | 701.3
644.2 | 118.2 | 455.8 | 182.32 | 213.1216 | 202.9 | 224.9 | 223.4 | 227.2 | 385.8 | 24.3 | 21.4 | 44.6 | 2.1 | 466.1 | 682.7 | 657.5 | 265.6 | 742.8 | 773.6 | 697.9
645.2 | 119.2 | 455.3 | 182.12 | 212.8878 | 202.9 | 225.4 | 223.8 | 227.9 | 381.4 | 24.3 | 21.4 | 44.8 | 2.3 | 472.7 | 684 | 659.9 | 263 | 737.5 | 768.5 | 695.2
646.2 | 120.2 | 455.8 | 182.32 | 213.1216 | 201.7 | 225.8 | 224.4 | 228.5 | 377.7 | 24.2 | 21.3 | 44.9 | 2.9 | 480.3 | 680.5 | 660.4 | 263.5 | 736.5 | 770.8 | 699
647.2 | 121.2 | 456.2 | 182.48 | 213.3086 | 201.6 | 224.8 | 224.7 | 228.7 | 373.7 | 24.3 | 21.3 | 44.8 | 2.9 | 486.3 | 671.1 | 662.1 | 265.5 | 718.2 | 755.5 | 702.6
648.2 | 122.2 | 455.8 | 182.32 | 213.1216 | 201.4 | 224.9 | 225.3 | 229 | 366.3 | 24.3 | 21.3 | 44.7 | 2.6 | 491.3 | 664.7 | 659.4 | 268.4 | 699 | 746.5 | 704.1
649.2 | 123.2 | 456.2 | 182.48 | 213.3086 | 201.3 | 226.3 | 225.6 | 230.1 | 359.9 | 24.3 | 21.3 | 44.7 | 2.9 | 496.7 | 647.4 | 647.5 | 271.8 | 687.4 | 741.9 | 711.8
650.2 | 124.2 | 455.6 | 182.24 | 213.0281 | 201.2 | 225.8 | 225.2 | 230.7 | 358.3 | 24.3 | 21.3 | 44.6 | 2.7 | 501.5 | 636 | 651 | 275.8 | 667.9 | 737.1 | 708.6
651.2 | 125.2 | 455.2 | 182.08 | 212.841 | 200.8 | 225.9 | 225.4 | 230.9 | 354.5 | 24.2 | 21.3 | 44.6 | 2.5 | 505.7 | 624.4 | 650.4 | 279.9 | 653.3 | 728.6 | 702.9
652.2 | 126.2 | 456.3 | 182.52 | 213.3554 | 198.8 | 226.6 | 226.4 | 231.9 | 348.9 | 24.2 | 21.3 | 44.7 | 2.5 | 512.7 | 623.1 | 662.5 | 284.4 | 647.1 | 733.6 | 713.6
653.2 | 127.2 | 456.9 | 182.76 | 213.6359 | 197.2 | 227.3 | 227.6 | 232.3 | 346.3 | 24.5 | 21.3 | 44.8 | 2.8 | 518.4 | 608.7 | 656.6 | 289.1 | 628.2 | 716.1 | 708.8
654.2 | 128.2 | 455.9 | 182.36 | 213.1683 | 196.1 | 228.9 | 228.2 | 233 | 338.9 | 25 | 21.3 | 44.9 | 2.7 | 524 | 600.4 | 657.5 | 293.5 | 608.9 | 709.3 | 710.3
655.2 | 129.2 | 455.4 | 182.16 | 212.9345 | 195.1 | 228.1 | 229.1 | 234.4 | 336 | 25.4 | 21.3 | 44.9 | 2.8 | 531.3 | 592.2 | 660.9 | 298.5 | 593.8 | 711.7 | 719.6
656.2 | 130.2 | 455.4 | 182.16 | 212.9345 | 195.3 | 225.4 | 229.7 | 236.1 | 331.7 | 25.8 | 21.3 | 44.9 | 2.8 | 541.4 | 600.1 | 664.7 | 303.8 | 596 | 724.3 | 725.5
657.2 | 131.2 | 454.1 | 181.64 | 212.3267 | 194.1 | 223.8 | 230.3 | 237.4 | 335.2 | 26 | 21.3 | 45 | 2.4 | 552 | 596.7 | 657.8 | 308.6 | 625.2 | 731.4 | 724.5
658.2 | 132.2 | 453.5 | 181.4 | 212.0461 | 192.9 | 223.6 | 230.4 | 238.1 | 343.5 | 26.1 | 21.3 | 45.2 | 2.2 | 563.5 | 605.4 | 672.5 | 312.9 | 647.7 | 747.7 | 724.8
659.2 | 133.2 | 453.8 | 181.52 | 212.1864 | 194 | 223.9 | 230.5 | 238.2 | 357.1 | 26.1 | 21.3 | 45.5 | 2.9 | 574.4 | 610.8 | 675.6 | 315.1 | 673.9 | 770.5 | 732.7
660.2 | 134.2 | 452.9 | 181.16 | 211.7656 | 197.4 | 224.4 | 230.4 | 237.9 | 368.2 | 26.1 | 21.3 | 45.8 | 2.6 | 585.7 | 632.8 | 689.3 | 317.1 | 680.4 | 783.5 | 737.9
661.2 | 135.2 | 456.1 | 182.44 | 213.2618 | 199.7 | 224.9 | 229.8 | 238.2 | 374.6 | 26 | 21.3 | 46.2 | 2.9 | 593.9 | 628.1 | 675.3 | 319.9 | 669.8 | 769.8 | 731.1
662.2 | 136.2 | 459 | 183.6 | 214.6178 | 199.1 | 225.5 | 229.4 | 238.2 | 369.7 | 26 | 21.3 | 46.3 | 2.6 | 601 | 613.3 | 663.3 | 323.3 | 652.6 | 757.5 | 726.9
663.2 | 137.2 | 460.5 | 184.2 | 215.3192 | 198.2 | 225.9 | 228.1 | 238.6 | 361.8 | 26 | 21.3 | 46.3 | 3.1 | 608.3 | 612.7 | 669.2 | 326.7 | 647.9 | 755 | 728.4
664.2 | 138.2 | 460.6 | 184.24 | 215.3659 | 197.3 | 225.4 | 227.8 | 238.4 | 358.2 | 25.9 | 21.3 | 46.3 | 2.7 | 615.9 | 605.1 | 661.2 | 329.8 | 651.1 | 760.6 | 729.7
665.2 | 139.2 | 460.3 | 184.12 | 215.2257 | 196.7 | 225.9 | 227.9 | 237.9 | 360.6 | 25.8 | 21.3 | 46.3 | 2.2 | 620.8 | 600.7 | 661.2 | 333.1 | 645.3 | 754.7 | 738.1
666.2 | 140.2 | 461 | 184.4 | 215.553 | 197.2 | 226.9 | 228.4 | 236.9 | 364 | 25.8 | 21.3 | 46.4 | 2.5 | 624 | 593.8 | 663.6 | 244.3 | 473.3 | 739.5 | 738.7
667.2 | 141.2 | 460.1 | 184.04 | 215.1322 | 197 | 227.2 | 228.6 | 236.9 | 363.4 | 25.8 | 21.3 | 46.5 | 2.8 | 627.7 | 594.4 | 673.4 | 263.7 | 494.2 | 736.6 | 739.3
668.2 | 142.2 | 459.9 | 183.96 | 215.0386 | 196.8 | 227.2 | 228.2 | 237.3 | 360 | 25.8 | 21.3 | 46.6 | 2.8 | 631.5 | 590.4 | 662 | 342.4 | 632 | 734.6 | 733.8
669.2 | 143.2 | 459.2 | 183.68 | 214.7113 | 197.1 | 228.6 | 227.5 | 237.5 | 366.2 | 25.8 | 21.3 | 46.7 | 3.1 | 636 | 588 | 659.2 | 346.1 | 634.9 | 736.4 | 733.7
670.2 | 144.2 | 459.5 | 183.8 | 214.8516 | 198.9 | 229.4 | 227 | 237.9 | 361.9 | 25.8 | 21.2 | 46.9 | 2.8 | 640.4 | 583.5 | 656.9 | 349.8 | 651.2 | 740.2 | 730.3
671.2 | 145.2 | 459.7 | 183.88 | 214.9451 | 199.4 | 229.9 | 227 | 238 | 363 | 25.8 | 21.3 | 47.3 | 2.9 | 644.3 | 583.6 | 649.5 | 354.9 | 658.1 | 741.6 | 732.7
672.2 | 146.2 | 463.2 | 185.28 | 216.5816 | 198.5 | 231 | 226.6 | 238.2 | 365.1 | 25.8 | 21.2 | 47.7 | 2.5 | 646.4 | 595.8 | 669.2 | 359.8 | 646.6 | 747.2 | 740.5
673.2 | 147.2 | 460 | 184 | 215.0854 | 198.9 | 232 | 225.1 | 238.2 | 369 | 25.8 | 21.2 | 48 | 2.2 | 651.2 | 612.6 | 680.7 | 365.5 | 657.1 | 756.1 | 750.5
674.2 | 148.2 | 462.9 | 185.16 | 216.4414 | 199.8 | 231.7 | 224.6 | 238.4 | 372.9 | 25.8 | 21.2 | 48.3 | 2.3 | 656.7 | 616.9 | 685.6 | 371.2 | 667.4 | 759.5 | 749.3
675.2 | 149.2 | 462.8 | 185.12 | 216.3946 | 200.1 | 230.7 | 223.7 | 239 | 368.5 | 25.9 | 21.2 | 48.6 | 2.9 | 661.6 | 610.7 | 682.9 | 377.3 | 663.8 | 746.3 | 744.3
676.2 | 150.2 | 463.1 | 185.24 | 216.5349 | 201.7 | 229.9 | 223.6 | 239.7 | 371 | 26 | 21.2 | 48.7 | 2.8 | 666 | 608.5 | 676.8 | 385.2 | 667.4 | 756.5 | 745.6
677.2 | 151.2 | 463.6 | 185.44 | 216.7687 | 203.8 | 229.4 | 224.4 | 239.7 | 375.4 | 26.3 | 21.2 | 48.8 | 2.7 | 669.6 | 602.5 | 666.2 | 397.8 | 663.6 | 758.5 | 751.6
678.2 | 152.2 | 462.6 | 185.04 | 216.3011 | 204.1 | 229.2 | 224.2 | 240 | 374.4 | 26.4 | 21.2 | 48.8 | 2.4 | 670.8 | 602.3 | 664.6 | 419.7 | 664.2 | 756.9 | 745.3
679.2 | 153.2 | 463 | 185.2 | 216.4881 | 205.3 | 228.4 | 223.8 | 240.6 | 375.3 | 26.5 | 21.2 | 48.9 | 2.4 | 673.3 | 601.7 | 664.4 | 444.7 | 655.6 | 755 | 745.1
680.2 | 154.2 | 462.8 | 185.12 | 216.3946 | 206.4 | 229.6 | 224.2 | 241.9 | 376.2 | 26.5 | 21.2 | 49.2 | 2.5 | 676.3 | 603.6 | 670.6 | 471.8 | 668.2 | 758.8 | 746.1
681.2 | 155.2 | 463.2 | 185.28 | 216.5816 | 206.8 | 230.1 | 225 | 243.1 | 379.9 | 26.5 | 21.2 | 49.4 | 2.5 | 679.6 | 616.9 | 691.1 | 503.7 | 684 | 771.8 | 752.8
682.2 | 156.2 | 463 | 185.2 | 216.4881 | 208.1 | 231.9 | 226.5 | 243.9 | 384.1 | 26.4 | 21.2 | 49.4 | 2.6 | 684.3 | 618.2 | 697 | 535.7 | 703.8 | 788.2 | 755.2
683.2 | 157.2 | 463.8 | 185.52 | 216.8622 | 210.6 | 232.7 | 227.1 | 244.2 | 388.3 | 26.5 | 21.2 | 49.4 | 2.6 | 689.9 | 625.4 | 699.1 | 572 | 723.1 | 802.3 | 763.1
684.2 | 158.2 | 464.4 | 185.76 | 217.1427 | 212.3 | 232.4 | 227.6 | 244.6 | 394.5 | 26.4 | 21.2 | 49.4 | 2.3 | 692.6 | 641.5 | 709.7 | 610.7 | 723.2 | 804.9 | 766.1
685.2 | 159.2 | 464.5 | 185.8 | 217.1895 | 212.8 | 233.4 | 227.6 | 245.3 | 395.7 | 26.3 | 21.2 | 49.3 | 2.1 | 695.3 | 639.3 | 705.5 | 646.3 | 716.8 | 801.5 | 758.6
686.2 | 160.2 | 465 | 186 | 217.4233 | 212.3 | 234.5 | 227.3 | 245.8 | 394.2 | 26.3 | 21.2 | 49.2 | 2.3 | 695.2 | 642.6 | 708.8 | 676.9 | 700.1 | 793.9 | 759.5
687.2 | 161.2 | 464.5 | 185.8 | 217.1895 | 211.7 | 234.6 | 226.7 | 245.8 | 386.8 | 26.3 | 21.2 | 49.1 | 2.4 | 695.4 | 646 | 708.9 | 701.9 | 684.5 | 790.5 | 756.5
688.2 | 162.2 | 463.3 | 185.32 | 216.6284 | 211.4 | 235.8 | 227.1 | 245.7 | 380.5 | 26.3 | 21.2 | 49.1 | 2.6 | 695.2 | 651.6 | 718.8 | 726.1 | 677.9 | 790.3 | 759.7
689.2 | 163.2 | 462.9 | 185.16 | 216.4414 | 210.9 | 236.6 | 228 | 245.9 | 376.2 | 26.5 | 21.2 | 49.2 | 2.9 | 697.5 | 651 | 706.3 | 756.8 | 665.2 | 787.5 | 759.5
690.2 | 164.2 | 463.9 | 185.56 | 216.9089 | 210.4 | 236.9 | 228.5 | 245.9 | 375.9 | 26.7 | 21.2 | 49.1 | 2.7 | 700.3 | 649.3 | 694.3 | 781.1 | 680.6 | 787 | 759.4
691.2 | 165.2 | 464.2 | 185.68 | 217.0492 | 210.7 | 236.6 | 228.9 | 244.9 | 379.3 | 26.8 | 21.2 | 49.3 | 2.9 | 702.8 | 648.6 | 685.1 | 796.9 | 701 | 783.5 | 753.8
692.2 | 166.2 | 463.2 | 185.28 | 216.5816 | 211.8 | 236.5 | 229.3 | 244.8 | 380.8 | 26.9 | 21.2 | 49.6 | 3 | 705.3 | 650.7 | 691.2 | 819.5 | 713 | 790.5 | 751.9
693.2 | 167.2 | 463.8 | 185.52 | 216.8622 | 212.4 | 236.8 | 228.8 | 245.2 | 384.2 | 27.1 | 21.2 | 49.7 | 2.9 | 706.6 | 653.7 | 683.7 | 840 | 700.6 | 799.8 | 745.7
694.2 | 168.2 | 464 | 185.6 | 216.9557 | 213.5 | 237 | 229.3 | 245.8 | 387.8 | 27.3 | 21.2 | 49.7 | 2.9 | 706.2 | 662.4 | 696.6 | 850.4 | 726.3 | 807.7 | 750.4
695.2 | 169.2 | 464.4 | 185.76 | 217.1427 | 214 | 236.8 | 230 | 245.9 | 388.4 | 27.6 | 21.2 | 49.7 | 2.7 | 709.1 | 669.1 | 689.7 | 854.3 | 662.6 | 813.4 | 750.9
696.2 | 170.2 | 463.8 | 185.52 | 216.8622 | 214.8 | 237.4 | 230.8 | 245.8 | 389.5 | 27.7 | 21.2 | 49.8 | 2.8 | 712.5 | 674.6 | 689.2 | 854.9 | 405 | 800.1 | 749.3
697.2 | 171.2 | 463.9 | 185.56 | 216.9089 | 216.1 | 238.1 | 232 | 245.8 | 394.6 | 27.7 | 21.2 | 49.9 | 2.7 | 714.2 | 659.2 | 667.6 | 822.7 | 738.6 | 778.7 | 740.7
698.2 | 172.2 | 463.3 | 185.32 | 216.6284 | 217.8 | 238.1 | 232.8 | 245.5 | 387.4 | 27.6 | 21.2 | 50.1 | 2.7 | 710.1 | 648.2 | 664.1 | 800.3 | 537.3 | 762.8 | 734.4
699.2 | 173.2 | 464 | 185.6 | 216.9557 | 218.4 | 238.3 | 233 | 245.5 | 378.7 | 27.6 | 21.2 | 50.3 | 3.1 | 704.9 | 634 | 654.5 | 784.1 | 416 | 740 | 732.1
700.2 | 174.2 | 464.1 | 185.64 | 217.0025 | 219 | 239.5 | 234 | 245.6 | 369.7 | 27.6 | 21.2 | 50.4 | 3 | 701.5 | 625.2 | 647.2 | 784.9 | 696 | 734.8 | 735.2
701.2 | 175.2 | 464.5 | 185.8 | 217.1895 | 219.9 | 239.5 | 234.7 | 246.1 | 373.9 | 27.7 | 21.2 | 50.4 | 2.6 | 699.8 | 626.9 | 649.1 | 809 | 703.3 | 739.5 | 737
702.2 | 176.2 | 464.7 | 185.88 | 217.283 | 219.5 | 239.9 | 235.8 | 245.8 | 377.6 | 27.9 | 21.2 | 50.6 | 2.4 | 697.9 | 626.4 | 656.9 | 800 | 696.8 | 736.8 | 738.4
703.2 | 177.2 | 463.1 | 185.24 | 216.5349 | 218 | 241.4 | 236.3 | 245.5 | 381.6 | 28.2 | 21.2 | 50.7 | 2.5 | 697.5 | 637.5 | 680.7 | 813.5 | 703.8 | 756.5 | 753.1
704.2 | 178.2 | 463.2 | 185.28 | 216.5816 | 217.9 | 241.9 | 235.7 | 246 | 384.9 | 28.5 | 21.2 | 50.8 | 2.5 | 698.9 | 643.4 | 685.2 | 820.9 | 711.6 | 765.1 | 760
705.2 | 179.2 | 462.9 | 185.16 | 216.4414 | 216.7 | 241.6 | 235.1 | 246.7 | 385.1 | 28.7 | 21.2 | 51.1 | 2.7 | 698.5 | 650.3 | 695.5 | 818.4 | 703.9 | 772 | 760.7
706.2 | 180.2 | 462.3 | 184.92 | 216.1608 | 215.5 | 242.4 | 234.9 | 247.4 | 384.9 | 28.8 | 21.2 | 51.4 | 2.8 | 699.1 | 660.4 | 701.1 | 820.8 | 704.7 | 777.2 | 760.8
707.2 | 181.2 | 462.2 | 184.88 | 216.1141 | 214.6 | 242.5 | 234.5 | 247.4 | 386.6 | 28.9 | 21.1 | 51.5 | 2.5 | 699 | 666.6 | 712.2 | 818.6 | 702.8 | 777.9 | 761.9
708.2 | 182.2 | 463.2 | 185.28 | 216.5816 | 215.3 | 241.8 | 234.2 | 247.2 | 383.2 | 29 | 21.1 | 51.6 | 2.4 | 697.6 | 667.2 | 712.7 | 806.6 | 695.6 | 759.5 | 752.8
709.2 | 183.2 | 463.8 | 185.52 | 216.8622 | 215.9 | 240.2 | 234.2 | 248 | 377.5 | 28.9 | 21.1 | 51.6 | 2.6 | 695.4 | 663.6 | 710.6 | 778.3 | 680.8 | 743.4 | 747.3
710.2 | 184.2 | 462 | 184.8 | 216.0206 | 215.7 | 238.9 | 233.7 | 248.4 | 368.9 | 28.9 | 21.1 | 51.6 | 2.5 | 693.4 | 654.1 | 698.9 | 736.5 | 655 | 722 | 742.5
711.2 | 185.2 | 462.8 | 185.12 | 216.3946 | 215 | 239.1 | 233.4 | 249.2 | 362 | 28.9 | 21.1 | 51.7 | 2.5 | 690.6 | 650.2 | 695.4 | 722.5 | 638.7 | 719.3 | 749.2
712.2 | 186.2 | 463.7 | 185.48 | 216.8154 | 213.6 | 239.4 | 233.7 | 250.1 | 359.3 | 28.8 | 21.1 | 51.8 | 2.7 | 688.1 | 646.7 | 700.9 | 724.2 | 629.9 | 730.8 | 753.6
713.2 | 187.2 | 464.2 | 185.68 | 217.0492 | 212.9 | 238.9 | 234.5 | 249.8 | 356.5 | 28.8 | 21.1 | 52 | 2.6 | 686.3 | 641.2 | 696.7 | 696.4 | 617 | 721.5 | 749.3
714.2 | 188.2 | 464.3 | 185.72 | 217.096 | 212.1 | 239.9 | 235.1 | 249.6 | 351.2 | 28.8 | 21.1 | 52.1 | 2.6 | 683.4 | 632.4 | 690.6 | 668.4 | 467.2 | 712 | 745.2
715.2 | 189.2 | 463.5 | 185.4 | 216.7219 | 211 | 241 | 235.3 | 250.5 | 346 | 28.8 | 21.1 | 52.2 | 2.7 | 678.7 | 618.9 | 667.3 | 621.5 | 585.6 | 683.4 | 736.2
716.2 | 190.2 | 464.1 | 185.64 | 217.0025 | 210.3 | 242.4 | 235.8 | 252.3 | 338.8 | 28.8 | 21.1 | 52.4 | 2.9 | 675.9 | 618.6 | 674.8 | 577.1 | 526.7 | 683.8 | 735.8
717.2 | 191.2 | 464 | 185.6 | 216.9557 | 210 | 242.7 | 236.5 | 252.8 | 336.5 | 28.9 | 21.1 | 52.6 | 3.4 | 676.8 | 617.5 | 668.4 | 539 | 379.2 | 697.9 | 738.4
718.2 | 192.2 | 463.6 | 185.44 | 216.7687 | 208.7 | 241.6 | 237.4 | 252.7 | 336.8 | 28.9 | 21.1 | 52.7 | 3 | 677.6 | 608 | 654.8 | 512.5 | 597 | 695.7 | 732.1
719.2 | 193.2 | 464.2 | 185.68 | 217.0492 | 208.3 | 241.2 | 237.6 | 251.5 | 339.1 | 29 | 21.1 | 52.8 | 2.7 | 682.6 | 614.7 | 667.1 | 483.7 | 467 | 720.8 | 737.6
720.2 | 194.2 | 463.6 | 185.44 | 216.7687 | 209.9 | 241 | 237.7 | 250.9 | 343.4 | 29 | 21.1 | 52.9 | 2.6 | 690 | 637 | 681.8 | 465.4 | 429.7 | 740.2 | 745.3
721.2 | 195.2 | 464 | 185.6 | 216.9557 | 210.6 | 240.6 | 237.3 | 249.9 | 350 | 29.1 | 21.1 | 53.2 | 2.7 | 698 | 649.7 | 697.7 | 449.8 | 682.6 | 757.4 | 753
722.2 | 196.2 | 463.6 | 185.44 | 216.7687 | 210.2 | 240.8 | 236.4 | 250 | 352.9 | 29.1 | 21.1 | 53.4 | 2.7 | 704.1 | 656.7 | 710.1 | 433 | 424.2 | 758.4 | 759.9
723.2 | 197.2 | 464.3 | 185.72 | 217.096 | 210.9 | 241 | 235.9 | 250.7 | 356.6 | 29.1 | 21.1 | 53.5 | 2.4 | 707 | 653.2 | 698.7 | 413.8 | 531.4 | 756.2 | 751.7
724.2 | 198.2 | 463.6 | 185.44 | 216.7687 | 211.3 | 241 | 236 | 251.1 | 354 | 29.1 | 21.1 | 53.8 | 2.3 | 706.1 | 651.2 | 696.4 | 395.1 | 675.4 | 758.7 | 748.4
725.2 | 199.2 | 464.7 | 185.88 | 217.283 | 211.8 | 242.6 | 235.4 | 251.3 | 350.2 | 29.2 | 21.1 | 54 | 3.1 | 705.8 | 649.3 | 686.4 | 378.7 | 581.2 | 762.1 | 749.9
726.2 | 200.2 | 464.1 | 185.64 | 217.0025 | 211.8 | 243.7 | 234.8 | 250.7 | 357.4 | 29.3 | 21.1 | 53.9 | 3.6 | 708.4 | 658.3 | 688.7 | 366.4 | 656.6 | 763.3 | 754.2
727.2 | 201.2 | 463.4 | 185.36 | 216.6752 | 211.6 | 244.5 | 235.3 | 250.5 | 362.4 | 29.5 | 21.1 | 53.9 | 2.9 | 710.4 | 660.6 | 687.4 | 351.2 | 662.7 | 774.6 | 757.2
728.2 | 202.2 | 463.7 | 185.48 | 216.8154 | 212.6 | 245.6 | 236.1 | 251.8 | 366.3 | 29.6 | 21.1 | 53.8 | 2.6 | 712.2 | 652.1 | 686.4 | 338.7 | 559.8 | 777 | 762.4
729.2 | 203.2 | 463.9 | 185.56 | 216.9089 | 212.5 | 246 | 237 | 252.7 | 365.1 | 29.8 | 21.1 | 53.9 | 2.7 | 710.7 | 645.8 | 680.9 | 331.9 | 651 | 759.1 | 756
730.2 | 204.2 | 463.6 | 185.44 | 216.7687 | 213.2 | 246.2 | 237.7 | 253.4 | 361.6 | 29.8 | 21.1 | 54 | 2.4 | 709.9 | 643.9 | 684.6 | 324 | 638.7 | 743.3 | 758.3
731.2 | 205.2 | 464 | 185.6 | 216.9557 | 214 | 248.1 | 238.3 | 253.9 | 359.4 | 29.8 | 21.1 | 54 | 2.5 | 708.6 | 648.7 | 689 | 315.2 | 631.5 | 731.8 | 756.7
732.2 | 206.2 | 463.2 | 185.28 | 216.5816 | 213.8 | 248.5 | 238.8 | 254.1 | 358.8 | 29.8 | 21.1 | 53.9 | 2.5 | 707.2 | 648.7 | 690.9 | 308.3 | 622.2 | 716.6 | 756.7
733.2 | 207.2 | 462.6 | 185.04 | 216.3011 | 214.1 | 248.9 | 238.8 | 254.9 | 356.1 | 30.1 | 21.1 | 54 | 2.4 | 705.7 | 643.3 | 680.7 | 303.6 | 610 | 708.2 | 749.8
734.2 | 208.2 | 462.2 | 184.88 | 216.1141 | 215 | 249.8 | 238.3 | 255.6 | 351.3 | 30.4 | 21.1 | 54 | 2.6 | 705 | 646.6 | 680.2 | 304.1 | 610.4 | 717.1 | 749.8
735.2 | 209.2 | 463.1 | 185.24 | 216.5349 | 215.7 | 251.1 | 238.1 | 255.5 | 349.7 | 30.6 | 21.1 | 54.2 | 2.7 | 706.1 | 637.7 | 668 | 298.3 | 604.4 | 717.2 | 748.9
736.2 | 210.2 | 463.8 | 185.52 | 216.8622 | 215.9 | 251.5 | 237.2 | 255.1 | 349.9 | 30.6 | 21.1 | 54.3 | 2.5 | 706.4 | 630.4 | 668.1 | 290.3 | 441.5 | 715.3 | 749.7
737.2 | 211.2 | 464.2 | 185.68 | 217.0492 | 215.7 | 250.5 | 236.2 | 256.2 | 350.9 | 30.7 | 21.1 | 54.5 | 2.7 | 706.2 | 624.7 | 653.9 | 285.7 | 530.4 | 714.8 | 748.4
738.2 | 212.2 | 463.6 | 185.44 | 216.7687 | 216.3 | 251.2 | 235.7 | 256.7 | 351.6 | 31 | 21 | 54.7 | 2.7 | 705.5 | 625.7 | 656.9 | 283 | 599 | 707.7 | 749.9
739.2 | 213.2 | 464.2 | 185.68 | 217.0492 | 217.3 | 253 | 235.8 | 256.5 | 347.6 | 31.3 | 21 | 54.8 | 2.4 | 708.5 | 639.7 | 683.4 | 276.9 | 593.1 | 733 | 760.4
740.2 | 214.2 | 464.1 | 185.64 | 217.0025 | 217.3 | 253.1 | 235.4 | 255.9 | 349.4 | 31.4 | 21 | 54.9 | 2.8 | 712.7 | 649.1 | 673.4 | 272.4 | 642.4 | 742.4 | 756.1
741.2 | 215.2 | 464.4 | 185.76 | 217.1427 | 216.4 | 252.9 | 234.9 | 255.9 | 352.3 | 31.3 | 21 | 55.2 | 2.6 | 716.3 | 657.5 | 669.9 | 272.1 | 667.8 | 750.1 | 749.7
742.2 | 216.2 | 462 | 184.8 | 216.0206 | 215.4 | 253.1 | 234.6 | 255.8 | 357.2 | 31.2 | 21 | 55.4 | 2.3 | 715.8 | 656.3 | 660.9 | 272 | 569.6 | 747.5 | 743.3
743.2 | 217.2 | 464.2 | 185.68 | 217.0492 | 215.5 | 252.3 | 235.3 | 255.7 | 359.9 | 31.1 | 21 | 55.4 | 2.7 | 718.3 | 666.1 | 665.4 | 269.4 | 697.7 | 750.5 | 744.9
744.2 | 218.2 | 463.2 | 185.28 | 216.5816 | 215.7 | 250.9 | 234.4 | 255 | 361.6 | 31 | 21 | 55.4 | 2.6 | 718.5 | 665.7 | 669.9 | 263.1 | 703.7 | 748.9 | 748.8
745.2 | 219.2 | 463.1 | 185.24 | 216.5349 | 215.5 | 249.8 | 234.3 | 254.6 | 364 | 30.9 | 21 | 55.4 | 2.6 | 717.1 | 667.6 | 675.3 | 256.1 | 692.2 | 742.9 | 748.5
746.2 | 220.2 | 461.8 | 184.72 | 215.927 | 213.9 | 250.4 | 233.8 | 255.4 | 360.9 | 30.9 | 21 | 55.4 | 2.7 | 715.4 | 664.6 | 674.9 | 247.8 | 678.4 | 732.9 | 748.2
747.2 | 221.2 | 463.8 | 185.52 | 216.8622 | 214.1 | 250.3 | 234.3 | 255.7 | 355.2 | 30.9 | 21 | 55.5 | 2.8 | 715.2 | 668.4 | 685.9 | 242.4 | 672.2 | 741.5 | 752
748.2 | 222.2 | 464 | 185.6 | 216.9557 | 213.8 | 248.7 | 234.5 | 256.7 | 351.3 | 31 | 21 | 55.5 | 2.9 | 717.2 | 670.9 | 700.6 | 236.7 | 670.6 | 746.3 | 759.4
749.2 | 223.2 | 463.7 | 185.48 | 216.8154 | 212.9 | 247.2 | 235.6 | 257.5 | 351.4 | 31.1 | 21 | 55.6 | 3.3 | 717.7 | 674.5 | 702.9 | 233.9 | 675.7 | 749.2 | 758.6
750.2 | 224.2 | 462.2 | 184.88 | 216.1141 | 212.8 | 247.3 | 236.2 | 257.7 | 353.1 | 31 | 21 | 55.7 | 3.1 | 716.4 | 663.2 | 686.2 | 231.9 | 684.3 | 734.9 | 748.9
751.2 | 225.2 | 463.7 | 185.48 | 216.8154 | 212.3 | 247.6 | 236.5 | 257.5 | 359.4 | 31 | 21 | 55.7 | 3.1 | 710.6 | 652.4 | 666.2 | 232.1 | 686 | 715.4 | 734.2
752.2 | 226.2 | 463.9 | 185.56 | 216.9089 | 212.8 | 247.8 | 237.1 | 257.2 | 372.2 | 31 | 21 | 55.8 | 2.7 | 709.3 | 653.4 | 660 | 227.9 | 701.7 | 714.5 | 727.2
753.2 | 227.2 | 464.2 | 185.68 | 217.0492 | 213.6 | 248.3 | 237.9 | 256.4 | 377.4 | 31 | 21 | 55.9 | 2.4 | 711.5 | 677.4 | 677.3 | 224.7 | 721.1 | 728.6 | 731.1
754.2 | 228.2 | 463.2 | 185.28 | 216.5816 | 214.5 | 248.5 | 237 | 255.5 | 386.1 | 31.1 | 21 | 55.8 | 2.1 | 716 | 701.7 | 699.3 | 220.2 | 738.2 | 749.5 | 743.6
755.2 | 229.2 | 462.5 | 185 | 216.2543 | 215.6 | 249.3 | 235.5 | 255.7 | 391.8 | 31.2 | 21 | 55.9 | 2.1 | 721.5 | 711.7 | 701 | 219.9 | 756.7 | 762.5 | 752.5
756.2 | 230.2 | 463.2 | 185.28 | 216.5816 | 215.9 | 250 | 234.8 | 256.8 | 397.6 | 31.2 | 21 | 56.1 | 2.4 | 725.8 | 716.4 | 704.4 | 219.5 | 777.8 | 774.3 | 753.1
757.2 | 231.2 | 461.9 | 184.76 | 215.9738 | 215.6 | 249.7 | 236 | 257.9 | 398.2 | 31.1 | 21 | 56.3 | 2.4 | 727.7 | 731.3 | 721.7 | 215.6 | 789.7 | 781.8 | 757.7
758.2 | 232.2 | 463.2 | 185.28 | 216.5816 | 215.6 | 249.2 | 236.9 | 258.6 | 401.4 | 31 | 21 | 56.5 | 2.4 | 728.8 | 739.2 | 720.7 | 215.4 | 797.1 | 784.8 | 747.7
759.2 | 233.2 | 463.5 | 185.4 | 216.7219 | 215.8 | 250 | 237.8 | 258.3 | 405.8 | 31 | 21 | 56.5 | 2.3 | 728.7 | 745.6 | 730.8 | 212.2 | 801 | 792 | 747.1
760.2 | 234.2 | 463.9 | 185.56 | 216.9089 | 216.1 | 251.5 | 237.9 | 258 | 406 | 31 | 21 | 56.5 | 2.6 | 726.4 | 748.6 | 750.6 | 214.2 | 786.1 | 793.1 | 757.9
761.2 | 235.2 | 464.1 | 185.64 | 217.0025 | 217.3 | 252.1 | 238 | 258.8 | 401.7 | 31 | 21 | 56.7 | 3.3 | 723.4 | 747.7 | 762.8 | 212.9 | 782.2 | 799.3 | 765.4
762.2 | 236.2 | 463.4 | 185.36 | 216.6752 | 216.5 | 252.7 | 238.1 | 259.3 | 401.4 | 31.3 | 21 | 56.7 | 2.5 | 721.3 | 742.9 | 762.2 | 218.6 | 780.2 | 804.6 | 767.8
763.2 | 237.2 | 464 | 185.6 | 216.9557 | 215.4 | 253 | 239.1 | 259.2 | 401.4 | 31.4 | 21 | 56.5 | 2.5 | 718 | 737.3 | 750.7 | 229.1 | 769.2 | 797.3 | 769.6
764.2 | 238.2 | 463.1 | 185.24 | 216.5349 | 217.3 | 253.8 | 240.5 | 259 | 398.8 | 31.6 | 21 | 56.5 | 3 | 714.7 | 727.8 | 737.8 | 235 | 764.6 | 794.3 | 766.3
765.2 | 239.2 | 464.1 | 185.64 | 217.0025 | 218.8 | 254.6 | 240.8 | 258.2 | 402.7 | 31.6 | 21 | 56.5 | 3.2 | 713.7 | 726.1 | 740.6 | 244.9 | 768.2 | 805.9 | 771.6
766.2 | 240.2 | 463.9 | 185.56 | 216.9089 | 219.6 | 255.7 | 240.2 | 257.9 | 403.5 | 31.7 | 21 | 56.6 | 3 | 710.3 | 724.6 | 736.6 | 242.8 | 758.3 | 798.8 | 767.3
767.2 | 241.2 | 463.3 | 185.32 | 216.6284 | 220.1 | 255.9 | 239.9 | 258 | 402.8 | 31.9 | 21 | 56.6 | 2.9 | 707.1 | 724.8 | 739.2 | 238 | 760.6 | 811.1 | 775
768.2 | 242.2 | 463.9 | 185.56 | 216.9089 | 220 | 254.5 | 239.7 | 257.8 | 405.2 | 32.2 | 21 | 56.7 | 3.5 | 706.5 | 735.5 | 742.8 | 237 | 774.2 | 809.5 | 771.9
769.2 | 243.2 | 463.6 | 185.44 | 216.7687 | 221.4 | 252.9 | 239.6 | 258.6 | 407.6 | 32.5 | 20.9 | 56.8 | 3.1 | 706.4 | 735.4 | 732.3 | 232.4 | 787.2 | 797.2 | 756.3
770.2 | 244.2 | 463.6 | 185.44 | 216.7687 | 222.5 | 250.9 | 239.7 | 258.6 | 409 | 32.7 | 21 | 56.9 | 2.6 | 708.9 | 745.8 | 738.9 | 228.6 | 805.6 | 799.5 | 754.5
771.2 | 245.2 | 464.1 | 185.64 | 217.0025 | 223.2 | 249 | 239.2 | 258.7 | 417.2 | 32.8 | 21 | 56.9 | 2.4 | 710.5 | 750.3 | 722.5 | 228 | 813.3 | 800.9 | 752.7
772.2 | 246.2 | 463.8 | 185.52 | 216.8622 | 223.3 | 248.3 | 238.9 | 259.1 | 425.3 | 32.7 | 20.9 | 56.9 | 2.3 | 712.3 | 755.5 | 733.7 | 229.2 | 814.5 | 807.7 | 760.2
773.2 | 247.2 | 463.3 | 185.32 | 216.6284 | 223.6 | 247.4 | 239.8 | 259.5 | 428 | 32.7 | 20.9 | 57 | 2.6 | 712.1 | 750.8 | 734.3 | 231.2 | 815 | 806.1 | 757.7
774.2 | 248.2 | 463.6 | 185.44 | 216.7687 | 224.6 | 246 | 240.8 | 260 | 427.1 | 32.6 | 20.9 | 57.2 | 3.2 | 709.4 | 743 | 730.2 | 234 | 803.2 | 801.5 | 758.5
775.2 | 249.2 | 464.1 | 185.64 | 217.0025 | 226.6 | 246.6 | 242.3 | 260.5 | 419.6 | 32.6 | 20.9 | 57.5 | 3.4 | 707.7 | 741.7 | 725.7 | 232.6 | 805.4 | 787.1 | 758.1
776.2 | 250.2 | 463.3 | 185.32 | 216.6284 | 227.4 | 248.2 | 244 | 260 | 419.4 | 32.7 | 20.9 | 57.5 | 3 | 701.1 | 726 | 700.7 | 230.8 | 792.6 | 755.2 | 745.7
777.2 | 251.2 | 464 | 185.6 | 216.9557 | 227.3 | 249.4 | 245.9 | 258.4 | 414.1 | 32.7 | 20.9 | 57.4 | 2.8 | 694.6 | 716.2 | 697.5 | 230.4 | 782.6 | 752.4 | 739
778.2 | 252.2 | 463.2 | 185.28 | 216.5816 | 228.2 | 248.8 | 245.7 | 256.6 | 411.3 | 32.7 | 20.9 | 57.3 | 2.5 | 693.7 | 720.6 | 717.6 | 230.7 | 776 | 768.1 | 754.7
779.2 | 253.2 | 463.8 | 185.52 | 216.8622 | 229.6 | 248.9 | 245.3 | 255.2 | 405.9 | 32.8 | 20.9 | 57.2 | 2.3 | 693.2 | 717 | 722.3 | 230.9 | 752.4 | 767.1 | 764
780.2 | 254.2 | 462.8 | 185.12 | 216.3946 | 230.8 | 250.5 | 245 | 254.6 | 400.6 | 33 | 20.9 | 57.3 | 2.3 | 694.2 | 730.4 | 741.1 | 227.2 | 737.9 | 767.7 | 771.7
781.2 | 255.2 | 463.1 | 185.24 | 216.5349 | 229.9 | 252.5 | 245.7 | 254.1 | 396.2 | 33.3 | 20.9 | 57.4 | 2.1 | 695.1 | 735.5 | 742.1 | 222.9 | 727 | 773.9 | 774.8
782.2 | 256.2 | 464.1 | 185.64 | 217.0025 | 227.7 | 253.7 | 246.1 | 254.4 | 395.1 | 33.5 | 20.9 | 57.5 | 2 | 696 | 739.2 | 745.5 | 220.3 | 723.3 | 779.6 | 779.7
783.2 | 257.2 | 464.4 | 185.76 | 217.1427 | 225.9 | 253.7 | 246.9 | 255 | 392.2 | 33.6 | 20.9 | 57.6 | 2.1 | 694.9 | 737.3 | 740.9 | 218.4 | 726.5 | 778.6 | 772
784.2 | 258.2 | 463.1 | 185.24 | 216.5349 | 226 | 253.5 | 247.9 | 255.3 | 390.3 | 33.7 | 20.9 | 57.8 | 2.2 | 694.2 | 736.2 | 736.4 | 218.2 | 716.9 | 776.6 | 765.1
785.2 | 259.2 | 463.6 | 185.44 | 216.7687 | 226.1 | 253.5 | 248.3 | 255.4 | 385.6 | 33.8 | 20.9 | 57.9 | 2.7 | 693.2 | 728.8 | 719.1 | 217.4 | 716.8 | 767.3 | 756.7
786.2 | 260.2 | 462.6 | 185.04 | 216.3011 | 225.9 | 254.1 | 248.2 | 254.7 | 385.3 | 33.8 | 20.9 | 58 | 2.6 | 691.4 | 724.4 | 708.5 | 217.6 | 717.7 | 758.3 | 752.3
787.2 | 261.2 | 463.3 | 185.32 | 216.6284 | 224.7 | 254.5 | 248.6 | 255.3 | 387 | 33.7 | 20.9 | 58.1 | 2.3 | 691.5 | 718.4 | 698.9 | 219 | 726.5 | 761.8 | 753.2
788.2 | 262.2 | 464.2 | 185.68 | 217.0492 | 224.3 | 253.4 | 249.6 | 257 | 387.8 | 33.7 | 20.9 | 58.1 | 2.3 | 691.3 | 711.7 | 699.3 | 218 | 718.3 | 768.1 | 761.4
789.2 | 263.2 | 463.4 | 185.36 | 216.6752 | 224.7 | 252.1 | 250.3 | 258.1 | 386.1 | 33.6 | 20.9 | 58.2 | 2.3 | 689.9 | 709.5 | 692.2 | 216 | 709.6 | 760.2 | 758.5
790.2 | 264.2 | 464.2 | 185.68 | 217.0492 | 225.3 | 251.2 | 251.1 | 258.3 | 382 | 33.6 | 20.9 | 58.5 | 2.6 | 690.8 | 707.8 | 687.5 | 214.8 | 726.1 | 757.3 | 752.1
791.2 | 265.2 | 463.6 | 185.44 | 216.7687 | 227 | 250.6 | 250.9 | 258.9 | 379.5 | 33.7 | 20.9 | 58.8 | 2.9 | 692.1 | 713.3 | 697.8 | 212.8 | 738.4 | 764.9 | 751.3
792.2 | 266.2 | 463.7 | 185.48 | 216.8154 | 227.3 | 249.6 | 250.5 | 259 | 387.7 | 33.7 | 20.9 | 59 | 2.8 | 695.4 | 735.3 | 726.8 | 210 | 728.5 | 770.7 | 760.4
793.2 | 267.2 | 464.5 | 185.8 | 217.1895 | 227.1 | 249.3 | 248.7 | 259.3 | 395.4 | 33.7 | 20.9 | 59.1 | 2.5 | 698.7 | 746.2 | 729.5 | 207.1 | 732.7 | 775.8 | 760.9
794.2 | 268.2 | 464.7 | 185.88 | 217.283 | 227.5 | 248.8 | 247.7 | 260 | 402.9 | 33.7 | 20.9 | 59.3 | 2.3 | 701.1 | 746 | 739.5 | 207.8 | 747.4 | 780.7 | 765.3
795.2 | 269.2 | 469.1 | 187.64 | 219.3403 | 228.2 | 249 | 248 | 261.2 | 402.7 | 33.7 | 20.9 | 59.4 | 2.5 | 703.2 | 748.4 | 745.4 | 209.9 | 757.1 | 786.6 | 771.3
796.2 | 270.2 | 470.8 | 188.32 | 220.1352 | 228.3 | 247.8 | 248.7 | 262.5 | 409.9 | 33.6 | 20.9 | 59.6 | 2.6 | 702.2 | 744.1 | 731.4 | 206.2 | 752.6 | 781.4 | 772.5
797.2 | 271.2 | 470.5 | 188.2 | 219.995 | 228.1 | 248.4 | 249.9 | 263.7 | 409.8 | 33.6 | 20.9 | 59.6 | 2.4 | 699 | 738.6 | 719.6 | 204.1 | 739.5 | 770.7 | 768.5
798.2 | 272.2 | 470.4 | 188.16 | 219.9482 | 228.1 | 250.7 | 250.4 | 264 | 403.6 | 33.6 | 20.9 | 59.5 | 2.6 | 694.2 | 726.3 | 700.5 | 202.5 | 713.5 | 743 | 759.8
799.2 | 273.2 | 469.7 | 187.88 | 219.6209 | 226.6 | 252.2 | 250.6 | 263.5 | 395.5 | 33.6 | 20.9 | 59.4 | 2.9 | 688.9 | 716.5 | 689.7 | 201.7 | 692.7 | 726.6 | 750.8
800.2 | 274.2 | 469.1 | 187.64 | 219.3403 | 224.9 | 254.4 | 250.9 | 263.7 | 386.8 | 34 | 20.9 | 59.4 | 2.9 | 683.8 | 709.7 | 686.1 | 200.9 | 669.1 | 712.8 | 752.1
801.2 | 275.2 | 469.7 | 187.88 | 219.6209 | 224 | 256.1 | 251.9 | 263.8 | 379 | 34.3 | 20.9 | 59.4 | 2.4 | 681.4 | 710.2 | 694.6 | 202.4 | 652.6 | 713 | 763.3
802.2 | 276.2 | 469.4 | 187.76 | 219.4806 | 222.6 | 256.1 | 252.4 | 264.4 | 377.5 | 34.4 | 20.9 | 59.5 | 2.2 | 682.5 | 713.7 | 704.2 | 202.8 | 652 | 733.5 | 772
803.2 | 277.2 | 468.1 | 187.24 | 218.8728 | 221.6 | 255.9 | 253.3 | 264.6 | 377.1 | 34.6 | 20.9 | 59.5 | 2.2 | 681.8 | 714.9 | 707.3 | 201.9 | 646.5 | 736.3 | 775.8
804.2 | 278.2 | 467.9 | 187.16 | 218.7793 | 220.4 | 256.3 | 253.5 | 265.1 | 378.1 | 34.6 | 20.9 | 59.6 | 2.2 | 683.8 | 721 | 718.9 | 201.8 | 643.9 | 744.9 | 776.2
805.2 | 279.2 | 468.2 | 187.28 | 218.9195 | 219.5 | 256.5 | 252.7 | 265.2 | 374.3 | 34.7 | 20.9 | 59.7 | 3.2 | 685.9 | 730.8 | 735.2 | 201.6 | 650.7 | 749.7 | 774.4
806.2 | 280.2 | 467.8 | 187.12 | 218.7325 | 220.2 | 256.3 | 251.4 | 266 | 374.2 | 34.8 | 20.9 | 60 | 3.4 | 687.3 | 733.7 | 738.7 | 201.6 | 656.4 | 754.9 | 775.4
807.2 | 281.2 | 467.3 | 186.92 | 218.4987 | 220.9 | 255.6 | 250.9 | 266.7 | 372.6 | 34.8 | 20.9 | 60.2 | 3.7 | 686.4 | 726.3 | 721.8 | 202.4 | 655 | 743.8 | 761.3
808.2 | 282.2 | 468 | 187.2 | 218.826 | 220 | 254.2 | 250.8 | 266.9 | 370.2 | 34.8 | 20.9 | 60.3 | 3.4 | 682.6 | 713.2 | 703.6 | 208.1 | 648.4 | 725.5 | 744.9
809.2 | 283.2 | 468.1 | 187.24 | 218.8728 | 219.4 | 254.4 | 251.5 | 267 | 370.9 | 34.7 | 20.9 | 60.3 | 3.6 | 678.1 | 703.1 | 691.4 | 210.3 | 648.2 | 720.4 | 743.5
810.2 | 284.2 | 466.9 | 186.76 | 218.3117 | 220 | 254.6 | 251.3 | 266.5 | 370.2 | 34.7 | 20.9 | 60.2 | 2.8 | 674.1 | 695.4 | 685.8 | 210.8 | 640 | 718.8 | 752.7
811.2 | 285.2 | 467.3 | 186.92 | 218.4987 | 221 | 256.2 | 251 | 266.4 | 368.9 | 34.8 | 20.9 | 60.2 | 2.8 | 669.7 | 685.4 | 680.8 | 215.2 | 636.5 | 713.9 | 754.6
812.2 | 286.2 | 468.3 | 187.32 | 218.9663 | 220.6 | 257.3 | 251 | 265.7 | 367.3 | 35 | 20.9 | 60.3 | 2.8 | 664.7 | 673.8 | 667.4 | 216.2 | 622.1 | 696.6 | 752.7
813.2 | 287.2 | 467.5 | 187 | 218.5922 | 219.9 | 258.3 | 250.8 | 265.5 | 364.4 | 35.1 | 20.9 | 60.5 | 3 | 660.5 | 661.3 | 657.5 | 220.1 | 620.8 | 696.3 | 744.3
814.2 | 288.2 | 466.5 | 186.6 | 218.1246 | 220.5 | 257.4 | 250.4 | 265.3 | 364 | 35.1 | 20.9 | 60.6 | 4.2 | 657.7 | 653.3 | 654.6 | 231.2 | 615.9 | 700.6 | 740.2
815.2 | 289.2 | 466.1 | 186.44 | 217.9376 | 221.9 | 256.7 | 249.5 | 265.1 | 364.3 | 35.6 | 20.9 | 60.9 | 3.4 | 657.3 | 655.8 | 655 | 227.9 | 640.3 | 704.9 | 738.2
816.2 | 290.2 | 467.3 | 186.92 | 218.4987 | 223 | 257 | 249.6 | 264.5 | 370 | 36 | 20.9 | 60.9 | 2.9 | 663.3 | 677 | 682.9 | 223.3 | 672.2 | 731.8 | 745
817.2 | 291.2 | 466.7 | 186.68 | 218.2182 | 223.1 | 256.2 | 249.1 | 263.3 | 383 | 36.3 | 20.9 | 61 | 3.2 | 671 | 702.5 | 711.7 | 220.9 | 689.5 | 752 | 754.9
818.2 | 292.2 | 465.7 | 186.28 | 217.7506 | 223.8 | 254.5 | 248.1 | 262.7 | 393 | 36.4 | 20.9 | 61.2 | 2.6 | 676.5 | 715.9 | 719.2 | 220.8 | 712 | 767.1 | 752.7
819.2 | 293.2 | 466.5 | 186.6 | 218.1246 | 225.1 | 252.8 | 247.7 | 263 | 398.8 | 36.2 | 20.9 | 61.4 | 2.4 | 681.8 | 732.3 | 732.8 | 220.9 | 723.6 | 784.8 | 765.2
820.2 | 294.2 | 465.5 | 186.2 | 217.6571 | 226.8 | 252 | 247.6 | 263.7 | 402.3 | 35.9 | 20.9 | 61.5 | 2.3 | 685.7 | 741.5 | 736.9 | 222.9 | 738.2 | 802.2 | 766.6
821.2 | 295.2 | 465.4 | 186.16 | 217.6103 | 226.4 | 251.6 | 248 | 263.8 | 404.1 | 35.7 | 20.8 | 61.7 | 2.7 | 687.5 | 744.8 | 735.7 | 224.2 | 755.3 | 806.5 | 765.3
822.2 | 296.2 | 466 | 186.4 | 217.8909 | 226.2 | 251.2 | 248.7 | 264.6 | 404.6 | 35.6 | 20.9 | 61.7 | 2.7 | 689.4 | 750.9 | 737 | 225.4 | 774.5 | 807.8 | 767.5
823.2 | 297.2 | 465.2 | 186.08 | 217.5168 | 225.4 | 251.4 | 248.9 | 265.1 | 407.2 | 35.8 | 20.8 | 61.6 | 2.5 | 690.2 | 751.4 | 731.6 | 228.8 | 777.7 | 815.7 | 771.6
824.2 | 298.2 | 465.7 | 186.28 | 217.7506 | 224.6 | 252.3 | 249 | 265.3 | 411.9 | 36.1 | 20.8 | 61.6 | 2.5 | 692.2 | 757.8 | 730.4 | 228.3 | 790.5 | 819.2 | 766.5
825.2 | 299.2 | 466.3 | 186.52 | 218.0311 | 224.7 | 253.6 | 249.3 | 266.2 | 412.1 | 36.1 | 20.8 | 61.6 | 2.9 | 692.9 | 759.7 | 726.8 | 227.1 | 781.8 | 817.6 | 766.6
826.2 | 300.2 | 466.1 | 186.44 | 217.9376 | 225.7 | 254 | 249.2 | 265.6 | 413.6 | 36.2 | 20.8 | 61.5 | 2.7 | 691.8 | 757.7 | 718.1 | 224.6 | 773.8 | 823.1 | 765.5
827.2 | 301.2 | 465.8 | 186.32 | 217.7973 | 226 | 253.7 | 248.6 | 264.3 | 412.2 | 36.6 | 20.8 | 61.4 | 2.5 | 692 | 757 | 725.5 | 222.2 | 779.3 | 816.8 | 773.1
828.2 | 302.2 | 464.7 | 185.88 | 217.283 | 226.4 | 254 | 249 | 263.2 | 413.5 | 37 | 20.8 | 61.4 | 2.9 | 690.1 | 752.1 | 725.9 | 219.9 | 763 | 805.7 | 773
829.2 | 303.2 | 466.1 | 186.44 | 217.9376 | 225.9 | 255.5 | 248.8 | 263.2 | 407.9 | 37.1 | 20.8 | 61.4 | 2.9 | 686.3 | 746.8 | 714.8 | 217.1 | 752.9 | 798.2 | 768
830.2 | 304.2 | 465.2 | 186.08 | 217.5168 | 226.3 | 256.7 | 248.4 | 263.8 | 405.3 | 37 | 20.8 | 61.3 | 3.1 | 683 | 740.3 | 697.2 | 218.2 | 753.3 | 789.4 | 762
831.2 | 305.2 | 466.3 | 186.52 | 218.0311 | 226.3 | 257.6 | 248.7 | 264.4 | 403 | 36.9 | 20.8 | 61.4 | 2.8 | 684.7 | 750.1 | 712.4 | 217.2 | 770.8 | 803.8 | 767.3
832.2 | 306.2 | 466 | 186.4 | 217.8909 | 226.4 | 259 | 248.9 | 264.9 | 406.1 | 36.8 | 20.8 | 61.4 | 2.7 | 687.6 | 757 | 703.9 | 214.3 | 781.7 | 793.9 | 760.5
833.2 | 307.2 | 466.7 | 186.68 | 218.2182 | 228.1 | 259.7 | 249.6 | 264.3 | 404.1 | 36.8 | 20.8 | 61.5 | 2.9 | 688.7 | 759.9 | 698.7 | 210.1 | 772.9 | 782.3 | 749.5
834.2 | 308.2 | 466.2 | 186.48 | 217.9844 | 229.9 | 259.4 | 250.5 | 265.5 | 397.9 | 36.7 | 20.8 | 61.6 | 2.8 | 693.3 | 768.1 | 697.4 | 210.5 | 773.1 | 777.1 | 745.9
835.2 | 309.2 | 466.5 | 186.6 | 218.1246 | 230.9 | 258.9 | 251.7 | 266 | 395.4 | 36.9 | 20.8 | 61.8 | 2.6 | 694.9 | 774.5 | 702.6 | 212 | 770.2 | 788.5 | 751.7
836.2 | 310.2 | 465.6 | 186.24 | 217.7038 | 230.7 | 258.2 | 251.8 | 265.8 | 394.7 | 37.1 | 20.8 | 62 | 3 | 693.9 | 776.2 | 699.8 | 214.3 | 762.8 | 780.1 | 752.3
837.2 | 311.2 | 463.4 | 185.36 | 216.6752 | 229.7 | 258.8 | 251.2 | 265.8 | 390.7 | 37.1 | 20.8 | 62.1 | 3 | 690.8 | 768.4 | 691.8 | 216.5 | 755.3 | 766.3 | 750.4
838.2 | 312.2 | 464 | 185.6 | 216.9557 | 229.7 | 259.1 | 251.9 | 265.8 | 384.8 | 37 | 20.8 | 62.1 | 3.1 | 687.1 | 760.4 | 690 | 215.1 | 726.3 | 759.6 | 753.4
839.2 | 313.2 | 467.3 | 186.92 | 218.4987 | 228.4 | 258.6 | 252.8 | 266.3 | 379.6 | 37 | 20.8 | 62.1 | 2.9 | 685.4 | 765.2 | 706.9 | 214.7 | 712.3 | 763.9 | 767
840.2 | 314.2 | 465.1 | 186.04 | 217.47 | 226 | 257.8 | 253.4 | 266.4 | 382 | 37 | 20.8 | 62.2 | 2.6 | 685.5 | 771 | 727.6 | 215.8 | 705.7 | 772.6 | 777.8
841.2 | 315.2 | 463.7 | 185.48 | 216.8154 | 224.3 | 256.5 | 253.1 | 265.6 | 386.6 | 36.9 | 20.8 | 62.2 | 2.7 | 687 | 776.7 | 728.5 | 214.3 | 706.6 | 785 | 777.9
842.2 | 316.2 | 464.1 | 185.64 | 217.0025 | 224 | 256.1 | 253 | 265.1 | 389.8 | 36.8 | 20.8 | 62.4 | 3 | 685.4 | 767.7 | 709.3 | 210.9 | 710.9 | 778.3 | 770.1
843.2 | 317.2 | 465.4 | 186.16 | 217.6103 | 224.7 | 256.8 | 252.4 | 265.8 | 385.8 | 36.8 | 20.8 | 62.7 | 3.5 | 682 | 759.8 | 701.3 | 208.6 | 693.1 | 777.4 | 767.8
844.2 | 318.2 | 464.4 | 185.76 | 217.1427 | 223.9 | 257.1 | 251.3 | 266.4 | 381.9 | 36.8 | 20.8 | 62.9 | 3.4 | 682.1 | 763.1 | 706.4 | 205.8 | 703.1 | 785.9 | 770.4
845.2 | 319.2 | 463.7 | 185.48 | 216.8154 | 223.7 | 256.5 | 251.1 | 266.1 | 384.4 | 36.8 | 20.8 | 62.9 | 2.9 | 681.2 | 769.2 | 710.6 | 205.4 | 691.1 | 773.9 | 770.6
846.2 | 320.2 | 463.8 | 185.52 | 216.8622 | 223.5 | 256.6 | 250.5 | 266.2 | 381.1 | 36.6 | 20.8 | 63 | 2.6 | 679.5 | 773.2 | 711 | 204.3 | 671.3 | 768.4 | 775.7
847.2 | 321.2 | 465.2 | 186.08 | 217.5168 | 222.8 | 258.1 | 249.3 | 266.8 | 377 | 36.6 | 20.8 | 63.3 | 2.7 | 680.1 | 781.2 | 725.3 | 202.7 | 665.2 | 769.9 | 781
848.2 | 322.2 | 465.3 | 186.12 | 217.5636 | 222.7 | 260.1 | 248.9 | 267.1 | 379.3 | 36.5 | 20.8 | 63.5 | 2.8 | 682 | 789.2 | 746 | 201.3 | 663 | 776.7 | 789
849.2 | 323.2 | 463.9 | 185.56 | 216.9089 | 223 | 260.1 | 249.4 | 268.3 | 378 | 36.5 | 20.8 | 63.6 | 2.6 | 683 | 795.9 | 745.2 | 204.5 | 673.3 | 778.4 | 785.9
850.2 | 324.2 | 464.1 | 185.64 | 217.0025 | 223.3 | 258.6 | 250 | 269.3 | 379.9 | 36.5 | 20.8 | 63.7 | 3 | 683.7 | 798.5 | 749.8 | 207.1 | 677.2 | 790.6 | 782.7
851.2 | 325.2 | 464.4 | 185.76 | 217.1427 | 223.4 | 257.6 | 249.7 | 268.8 | 383.2 | 36.6 | 20.8 | 63.7 | 3 | 686.7 | 807.5 | 757.7 | 207.5 | 695.2 | 795.9 | 780.5
852.2 | 326.2 | 464.4 | 185.76 | 217.1427 | 223.7 | 257.4 | 249.9 | 268.5 | 389.3 | 36.9 | 20.8 | 63.8 | 3 | 689.4 | 812.4 | 744.2 | 208.1 | 707.7 | 785.2 | 768.7
853.2 | 327.2 | 464.1 | 185.64 | 217.0025 | 223.1 | 256.9 | 250.4 | 268.8 | 390.7 | 37.1 | 20.8 | 63.9 | 3.2 | 688.4 | 805.6 | 721.9 | 209.7 | 724.9 | 775.4 | 758.2
854.2 | 328.2 | 465.1 | 186.04 | 217.47 | 224 | 256.6 | 250 | 268.3 | 391.2 | 37.2 | 20.8 | 63.9 | 2.6 | 687.2 | 799.4 | 703.8 | 209.2 | 730 | 778 | 757.4
855.2 | 329.2 | 465.5 | 186.2 | 217.6571 | 225.6 | 256.4 | 249.3 | 268.5 | 392.3 | 37.1 | 20.8 | 63.9 | 3.2 | 685.1 | 797 | 693.7 | 210.8 | 752 | 780 | 767
856.2 | 330.2 | 465.5 | 186.2 | 217.6571 | 227.7 | 256.2 | 250 | 268.1 | 402.6 | 37.3 | 20.8 | 64.1 | 3.2 | 685.4 | 794.7 | 694.7 | 211 | 776 | 773.8 | 763.8
857.2 | 331.2 | 464.2 | 185.68 | 217.0492 | 228.9 | 254.8 | 251.2 | 267.5 | 405 | 37.4 | 20.8 | 64.1 | 2.6 | 684.4 | 790.6 | 698.5 | 214.2 | 786.1 | 788.9 | 764.5
858.2 | 332.2 | 464.5 | 185.8 | 217.1895 | 229.7 | 254.1 | 250.8 | 267.6 | 408.1 | 37.5 | 20.8 | 64.1 | 2.7 | 684.4 | 789.5 | 705.4 | 214.6 | 790.7 | 805.9 | 778
859.2 | 333.2 | 464.3 | 185.72 | 217.096 | 231.1 | 255.5 | 250.1 | 267.3 | 410.2 | 37.6 | 20.8 | 64.3 | 3 | 684.8 | 794.9 | 712 | 216.6 | 794.8 | 804.6 | 778.5
860.2 | 334.2 | 464.5 | 185.8 | 217.1895 | 232.2 | 256.2 | 250.3 | 267 | 414.9 | 37.6 | 20.8 | 64.5 | 3.4 | 687.6 | 800.5 | 715.8 | 220.2 | 806 | 794.3 | 769.1
861.2 | 335.2 | 463.9 | 185.56 | 216.9089 | 232.3 | 255.9 | 250.3 | 266.2 | 421.6 | 37.7 | 20.8 | 64.5 | 3 | 687.9 | 799.2 | 720.2 | 222.8 | 804.3 | 782.3 | 761.3
862.2 | 336.2 | 464.5 | 185.8 | 217.1895 | 232 | 256.9 | 250.3 | 265.3 | 421 | 37.8 | 20.8 | 64.3 | 2.6 | 689.7 | 796 | 717 | 222.3 | 812 | 776.2 | 752.4
863.2 | 337.2 | 464.4 | 185.76 | 217.1427 | 232.5 | 258.3 | 251.7 | 265 | 427.6 | 37.9 | 20.8 | 64.3 | 2.8 | 695 | 810.9 | 737.2 | 225.4 | 800.5 | 780.7 | 759.4
864.2 | 338.2 | 462.3 | 184.92 | 216.1608 | 234.2 | 259.2 | 252.8 | 264.6 | 434.4 | 38 | 20.8 | 64.2 | 2.7 | 701.9 | 823.1 | 763.4 | 227.2 | 785.4 | 790.6 | 777.1
865.2 | 339.2 | 460.2 | 184.08 | 215.1789 | 235.3 | 259 | 254 | 264.5 | 434.2 | 38.1 | 20.8 | 64.1 | 2.9 | 706.8 | 829.6 | 768.4 | 229.3 | 775.2 | 796.6 | 779.8
866.2 | 340.2 | 463.3 | 185.32 | 216.6284 | 235 | 258.9 | 255.6 | 265.4 | 431.5 | 38.2 | 20.8 | 64.1 | 2.5 | 712.6 | 833.5 | 772.1 | 233.1 | 768.9 | 791.6 | 769.6
867.2 | 341.2 | 462 | 184.8 | 216.0206 | 235.1 | 259 | 256.6 | 265.9 | 429.2 | 38.2 | 20.7 | 64 | 2.2 | 716.8 | 833 | 774.9 | 232.4 | 764.7 | 797.2 | 771.8
868.2 | 342.2 | 463.2 | 185.28 | 216.5816 | 234.7 | 259.5 | 256.8 | 266.1 | 422.5 | 38.2 | 20.7 | 63.8 | 2.5 | 717.7 | 827.3 | 768 | 230.7 | 738.6 | 788.5 | 776.4
869.2 | 343.2 | 463.2 | 185.28 | 216.5816 | 234.3 | 260.5 | 257.3 | 265.2 | 413.4 | 38.3 | 20.7 | 63.7 | 2.6 | 717.7 | 817.1 | 770.5 | 231.4 | 719.1 | 780.4 | 778.8
870.2 | 344.2 | 464.2 | 185.68 | 217.0492 | 233.5 | 260.9 | 258.2 | 264.7 | 407.4 | 38.4 | 20.7 | 63.7 | 2.5 | 719.6 | 816.4 | 780.2 | 225.9 | 708 | 776.6 | 783.4
871.2 | 345.2 | 462.8 | 185.12 | 216.3946 | 232.2 | 262 | 258.6 | 264.8 | 412.9 | 39.1 | 20.7 | 63.7 | 2.6 | 725.5 | 813.7 | 782.8 | 222.9 | 714.5 | 793.4 | 786.9
872.2 | 346.2 | 464.4 | 185.76 | 217.1427 | 231.1 | 262.3 | 258.2 | 265.5 | 418.5 | 39.3 | 20.7 | 63.8 | 3.1 | 732.4 | 813.9 | 786.2 | 222.3 | 713 | 804.7 | 791.9
873.2 | 347.2 | 463.9 | 185.56 | 216.9089 | 230.7 | 262.2 | 258.8 | 265.9 | 421.1 | 39.4 | 20.7 | 63.8 | 3.9 | 739.2 | 817.9 | 787.5 | 219 | 721.7 | 816.9 | 793.8
874.2 | 348.2 | 464.1 | 185.64 | 217.0025 | 231.5 | 262.2 | 259.9 | 266 | 428.3 | 39.4 | 20.7 | 63.7 | 3.7 | 744.7 | 822.3 | 792.8 | 215.5 | 714 | 826.1 | 799.6
875.2 | 349.2 | 464.7 | 185.88 | 217.283 | 231.1 | 262.3 | 260.3 | 266.6 | 438.6 | 39.3 | 20.7 | 63.8 | 3 | 749.4 | 825 | 797.8 | 212.8 | 714.4 | 819.3 | 796.8
876.2 | 350.2 | 463.9 | 185.56 | 216.9089 | 230.6 | 262.8 | 261.1 | 266.7 | 435.3 | 39.1 | 20.7 | 63.8 | 3.2 | 752.7 | 823.6 | 805.5 | 211.4 | 716.9 | 822.6 | 795.5
877.2 | 351.2 | 463.7 | 185.48 | 216.8154 | 230.9 | 262.1 | 261.8 | 267.8 | 430.7 | 38.9 | 20.7 | 63.8 | 3.5 | 755.1 | 816.4 | 798.6 | 214.9 | 731.7 | 829.3 | 797.1
878.2 | 352.2 | 463.1 | 185.24 | 216.5349 | 231.4 | 260.7 | 261.9 | 268.6 | 433.8 | 39 | 20.7 | 63.8 | 3.5 | 756.7 | 807.7 | 780.6 | 220.2 | 752.2 | 834 | 799.4
879.2 | 353.2 | 464 | 185.6 | 216.9557 | 233.4 | 259.1 | 263 | 269 | 439.8 | 39.2 | 20.7 | 63.7 | 3.7 | 755.5 | 790.5 | 758.9 | 224.1 | 755.7 | 828.6 | 795.3
880.2 | 354.2 | 464.3 | 185.72 | 217.096 | 234.5 | 259 | 262.9 | 269 | 432 | 39.2 | 20.7 | 63.6 | 3.2 | 750 | 759.8 | 727.9 | 224.8 | 734.5 | 786 | 773.8
881.2 | 355.2 | 464.5 | 185.8 | 217.1895 | 236 | 260.5 | 262.6 | 269.6 | 420.8 | 39 | 20.7 | 63.6 | 3.1 | 743.1 | 727.1 | 699 | 227.7 | 721.9 | 766.4 | 757.3
882.2 | 356.2 | 463.8 | 185.52 | 216.8622 | 235.6 | 261.4 | 262.4 | 270.2 | 414.5 | 38.9 | 20.7 | 63.6 | 2.9 | 739.8 | 708.6 | 689.5 | 225.1 | 741.8 | 779.1 | 757.9
883.2 | 357.2 | 464.3 | 185.72 | 217.096 | 235.4 | 261.3 | 260.7 | 270 | 415.7 | 38.8 | 20.7 | 63.8 | 2.9 | 738.1 | 697.5 | 670.9 | 223.6 | 757.1 | 776.7 | 757.3
884.2 | 358.2 | 463.8 | 185.52 | 216.8622 | 236.6 | 260.1 | 258.7 | 269.9 | 410.4 | 38.9 | 20.7 | 63.9 | 3.4 | 734.7 | 675 | 660.5 | 224.3 | 752 | 766.1 | 756.8
885.2 | 359.2 | 462.4 | 184.96 | 216.2076 | 236.8 | 259.5 | 258.1 | 269.2 | 406.9 | 39 | 20.7 | 64 | 3.1 | 731.9 | 659.8 | 651.9 | 225.6 | 731.2 | 755.8 | 762.4
886.2 | 360.2 | 461.1 | 184.44 | 215.5997 | 237.4 | 260.9 | 257.7 | 268.7 | 399.7 | 38.9 | 20.7 | 64.3 | 2.9 | 727.9 | 641.8 | 641.3 | 226.2 | 705.8 | 740.5 | 755.7
887.2 | 361.2 | 462.3 | 184.92 | 216.1608 | 237.4 | 262.1 | 257.1 | 268.3 | 390.3 | 38.8 | 20.7 | 64.7 | 2.9 | 726.4 | 644.9 | 663.6 | 225.2 | 696.3 | 757.8 | 769.8
888.2 | 362.2 | 464.2 | 185.68 | 217.0492 | 236.6 | 261.2 | 257.5 | 267.9 | 392.4 | 38.8 | 20.7 | 64.8 | 2.8 | 729.3 | 655.1 | 667.4 | 223.7 | 712.9 | 777.4 | 779.1
889.2 | 363.2 | 461.4 | 184.56 | 215.74 | 236.6 | 260.2 | 257.6 | 268.1 | 391.9 | 38.7 | 20.7 | 64.9 | 3 | 730.6 | 659.5 | 678.7 | 223.6 | 715.7 | 784.2 | 781.7
890.2 | 364.2 | 462.3 | 184.92 | 216.1608 | 235.3 | 260.9 | 257 | 268.8 | 388.3 | 38.6 | 20.7 | 65.1 | 3.3 | 730.3 | 652.8 | 683.7 | 224.4 | 698 | 764.6 | 778.2
891.2 | 365.2 | 462 | 184.8 | 216.0206 | 233.8 | 261 | 256.8 | 269.4 | 383.1 | 38.5 | 20.7 | 65.1 | 2.6 | 727.2 | 639.2 | 669.3 | 223.9 | 669.3 | 733.2 | 770.5
892.2 | 366.2 | 461.4 | 184.56 | 215.74 | 233.7 | 260.4 | 256.4 | 269.8 | 376 | 38.4 | 20.7 | 65.2 | 3 | 724.3 | 627.3 | 652.2 | 221 | 645.2 | 705.2 | 760.7
893.2 | 367.2 | 461.5 | 184.6 | 215.7868 | 233.4 | 260.4 | 255.7 | 269.9 | 369.5 | 38.5 | 20.7 | 65.3 | 3.3 | 720.9 | 618.7 | 642.5 | 219.5 | 619.5 | 681.5 | 756.1
894.2 | 368.2 | 461.2 | 184.48 | 215.6465 | 232.5 | 260.4 | 255.6 | 270.4 | 366 | 39 | 20.7 | 65.2 | 2.8 | 718.2 | 612.1 | 644.1 | 217.4 | 597.9 | 664.1 | 754.5
895.2 | 369.2 | 462.1 | 184.84 | 216.0673 | 231 | 260.7 | 256 | 271.2 | 364.9 | 39.3 | 20.7 | 65.1 | 3.3 | 716.2 | 606.9 | 651.8 | 215.9 | 588.1 | 671.5 | 756.2
896.2 | 370.2 | 462.6 | 185.04 | 216.3011 | 230.9 | 260.3 | 256.9 | 272.4 | 367.7 | 39.6 | 20.7 | 65.1 | 3.2 | 717.2 | 621.1 | 680.9 | 216.5 | 594.6 | 694.4 | 767.3
897.2 | 371.2 | 463.5 | 185.4 | 216.7219 | 230.9 | 260.4 | 257.1 | 272.9 | 373.2 | 39.8 | 20.7 | 65.2 | 2.8 | 721.2 | 632.2 | 684 | 215.9 | 616.1 | 721.2 | 774.8
898.2 | 372.2 | 463.2 | 185.28 | 216.5816 | 230.1 | 260.2 | 257 | 272.7 | 377.1 | 39.9 | 20.7 | 65.3 | 2.6 | 727.1 | 656.9 | 700.5 | 216.1 | 643.6 | 745.8 | 781.1
899.2 | 373.2 | 462.5 | 185 | 216.2543 | 230 | 259.5 | 256.4 | 272.3 | 389.1 | 39.8 | 20.7 | 65.5 | 2.9 | 734.9 | 677.8 | 711.3 | 217.5 | 676.5 | 768.1 | 783.9
900.2 | 374.2 | 461.8 | 184.72 | 215.927 | 228.8 | 259.5 | 255.7 | 272.1 | 393 | 39.6 | 20.7 | 65.6 | 2.9 | 738.7 | 687.6 | 725.4 | 216.5 | 685.5 | 771.4 | 781.8
901.2 | 375.2 | 461.6 | 184.64 | 215.8335 | 228.4 | 259.7 | 255.9 | 272.5 | 392.8 | 39.5 | 20.7 | 65.7 | 3.1 | 742.8 | 702.5 | 723.6 | 217.9 | 698.7 | 773.6 | 779.6
902.2 | 376.2 | 461.4 | 184.56 | 215.74 | 228.5 | 259.8 | 255.8 | 273.2 | 391.1 | 39.5 | 20.7 | 65.8 | 3.3 | 742.3 | 687.4 | 696.3 | 218.8 | 704.7 | 760.4 | 768
903.2 | 377.2 | 462.4 | 184.96 | 216.2076 | 229.1 | 261 | 255.6 | 274.5 | 386.8 | 39.5 | 20.7 | 65.9 | 3.1 | 741.1 | 676.6 | 689.8 | 218.7 | 695.8 | 745.9 | 767.3
904.2 | 378.2 | 463.3 | 185.32 | 216.6284 | 230.2 | 262.1 | 254.7 | 274.4 | 380.2 | 39.4 | 20.7 | 65.9 | 2.6 | 736.2 | 656.8 | 676.4 | 215.6 | 667.2 | 721.6 | 759.7
905.2 | 379.2 | 462.3 | 184.92 | 216.1608 | 230.9 | 262.3 | 255 | 273.7 | 369.5 | 39.5 | 20.7 | 66 | 2.9 | 733.8 | 655.4 | 683.1 | 214.1 | 651.4 | 722.8 | 756
906.2 | 380.2 | 461.9 | 184.76 | 215.9738 | 230.8 | 261.3 | 255.4 | 273.4 | 370.5 | 39.4 | 20.7 | 66.1 | 2.7 | 735.1 | 668.1 | 711 | 213.3 | 640.1 | 739.6 | 769.9
907.2 | 381.2 | 461.9 | 184.76 | 215.9738 | 230.3 | 260.9 | 255.9 | 273.6 | 381.7 | 39.3 | 20.7 | 66.1 | 3.1 | 738.9 | 681.6 | 740.2 | 215.4 | 631.4 | 750.6 | 782.4
908.2 | 382.2 | 462.3 | 184.92 | 216.1608 | 229.6 | 262.6 | 256.8 | 274.5 | 383.5 | 39.3 | 20.7 | 66 | 2.7 | 740.5 | 680.8 | 738.8 | 217.1 | 620.7 | 742.3 | 784.5
909.2 | 383.2 | 462.2 | 184.88 | 216.1141 | 229.2 | 264.3 | 256.7 | 276 | 377 | 39.4 | 20.7 | 66 | 2.8 | 740.6 | 672.6 | 726.4 | 218.7 | 629.2 | 756.3 | 782
910.2 | 384.2 | 463.1 | 185.24 | 216.5349 | 229 | 265.3 | 256.7 | 277.6 | 373.6 | 39.5 | 20.7 | 66 | 3.4 | 743.3 | 683.7 | 736.2 | 219.5 | 646.8 | 753.9 | 777.5
911.2 | 385.2 | 462.9 | 185.16 | 216.4414 | 229.3 | 266.3 | 256.6 | 277.8 | 376.5 | 39.7 | 20.7 | 66.2 | 2.9 | 748.3 | 701.6 | 754.1 | 217.5 | 660.1 | 746.5 | 774
912.2 | 386.2 | 463.1 | 185.24 | 216.5349 | 229.6 | 266.7 | 256.9 | 277.7 | 385.8 | 39.7 | 20.7 | 66.4 | 2.9 | 754.6 | 719.6 | 762.1 | 215.4 | 675.6 | 741 | 772.1
913.2 | 387.2 | 463.3 | 185.32 | 216.6284 | 229.6 | 266.1 | 256.7 | 277.9 | 391.6 | 39.8 | 20.7 | 66.6 | 3.2 | 762.1 | 737.3 | 759.4 | 214.1 | 686.9 | 748.2 | 771.6
914.2 | 388.2 | 462.5 | 185 | 216.2543 | 229.9 | 265.4 | 256.6 | 277.9 | 402 | 39.8 | 20.7 | 66.7 | 3.9 | 763.9 | 727.3 | 747.2 | 212.2 | 701.5 | 759.3 | 774.9
915.2 | 389.2 | 463.3 | 185.32 | 216.6284 | 229.8 | 264.7 | 256.8 | 278.2 | 400.8 | 39.7 | 20.7 | 66.8 | 2.9 | 763.5 | 718.3 | 721.7 | 214.4 | 720.8 | 765.3 | 762.3
916.2 | 390.2 | 462.9 | 185.16 | 216.4414 | 230 | 265.2 | 256.7 | 278.6 | 403.2 | 39.5 | 20.7 | 66.8 | 2.8 | 764.9 | 717 | 718 | 213.5 | 746 | 776.9 | 758.1
917.2 | 391.2 | 464.2 | 185.68 | 217.0492 | 231 | 265.5 | 256.7 | 278.1 | 404.3 | 39.5 | 20.7 | 66.7 | 2.6 | 766.1 | 717.9 | 716.7 | 212.8 | 757.2 | 785.3 | 760.8
918.2 | 392.2 | 463.6 | 185.44 | 216.7687 | 231.8 | 266.2 | 256.7 | 277.8 | 402.7 | 39.7 | 20.7 | 66.6 | 2.7 | 765.6 | 710.2 | 720.8 | 211.4 | 738.6 | 793.1 | 774.3
919.2 | 393.2 | 463 | 185.2 | 216.4881 | 231.8 | 266.8 | 256.9 | 277.3 | 397.9 | 39.8 | 20.7 | 66.5 | 2.8 | 762.6 | 690.2 | 708.2 | 215.2 | 719.5 | 788.6 | 779.9
920.2 | 394.2 | 462.8 | 185.12 | 216.3946 | 232.4 | 267.4 | 256.2 | 277 | 394.4 | 39.8 | 20.7 | 66.5 | 2.8 | 757.5 | 667.8 | 694.6 | 219.7 | 693.5 | 767.9 | 774
921.2 | 395.2 | 461.9 | 184.76 | 215.9738 | 231.9 | 267.3 | 255.6 | 276.2 | 385.1 | 39.8 | 20.7 | 66.5 | 2.6 | 752.1 | 653.3 | 690.8 | 220.6 | 673.4 | 762.3 | 771.6
922.2 | 396.2 | 461.3 | 184.52 | 215.6932 | 232.2 | 266.9 | 255.1 | 275.6 | 376.7 | 39.7 | 20.7 | 66.6 | 2.7 | 751.2 | 651.8 | 685.2 | 233.7 | 686.3 | 771.8 | 770.5
923.2 | 397.2 | 462.6 | 185.04 | 216.3011 | 232.1 | 266.7 | 254.6 | 275.4 | 379.5 | 39.7 | 20.7 | 66.7 | 2.9 | 751.2 | 637.9 | 665.2 | 239.1 | 714 | 767.7 | 759.3
924.2 | 398.2 | 464 | 185.6 | 216.9557 | 231.4 | 266.5 | 253.9 | 274.7 | 380.8 | 39.9 | 20.7 | 66.8 | 3.2 | 749.1 | 633.9 | 669.6 | 240.1 | 722.1 | 780.6 | 761.2
925.2 | 399.2 | 463.4 | 185.36 | 216.6752 | 231.2 | 266.3 | 253.7 | 273.2 | 380.9 | 40.2 | 20.7 | 67 | 3.4 | 748.9 | 636 | 676.2 | 237.8 | 704.4 | 771.3 | 762.7
926.2 | 400.2 | 463.1 | 185.24 | 216.5349 | 231.9 | 266 | 254.2 | 271.7 | 376.1 | 40.4 | 20.7 | 67.2 | 3.4 | 746.5 | 622.6 | 668.7 | 238.3 | 693.5 | 771.7 | 760.1
927.2 | 401.2 | 463.3 | 185.32 | 216.6284 | 232.1 | 266.4 | 253.6 | 270.5 | 372.5 | 40.4 | 20.7 | 67.4 | 3.5 | 745.7 | 620.2 | 663.4 | 236.4 | 709.8 | 771.2 | 759
928.2 | 402.2 | 463.2 | 185.28 | 216.5816 | 231.1 | 266.9 | 253.5 | 270 | 373.2 | 40.4 | 20.6 | 67.5 | 3.8 | 746 | 620.2 | 675.8 | 238.9 | 728.9 | 776 | 760.6
929.2 | 403.2 | 463.3 | 185.32 | 216.6284 | 230.4 | 266.5 | 252.8 | 270 | 383.4 | 40.6 | 20.6 | 67.5 | 4 | 750.5 | 637.8 | 692.6 | 233.1 | 742.5 | 798.7 | 772.6
930.2 | 404.2 | 463.8 | 185.52 | 216.8622 | 229.8 | 265.4 | 252.4 | 269.8 | 397.6 | 40.7 | 20.6 | 67.5 | 3.1 | 756.1 | 656.6 | 704.6 | 232.2 | 739.5 | 809.4 | 781
931.2 | 405.2 | 464.9 | 185.96 | 217.3765 | 230.3 | 265.4 | 252.6 | 270 | 396.8 | 40.6 | 20.6 | 67.5 | 2.7 | 758.4 | 653.9 | 704.8 | 233.6 | 726.1 | 811.6 | 784.6
932.2 | 406.2 | 464.3 | 185.72 | 217.096 | 230.6 | 265.4 | 252.6 | 270.9 | 395.7 | 40.5 | 20.6 | 67.6 | 3.1 | 759.1 | 654.7 | 722.8 | 229.2 | 718.2 | 811 | 786.9
933.2 | 407.2 | 463.8 | 185.52 | 216.8622 | 231.8 | 265.8 | 252.8 | 271.9 | 398.2 | 40.5 | 20.6 | 67.7 | 3.5 | 759.4 | 653.5 | 742.7 | 226.5 | 703.3 | 806.2 | 788.3
934.2 | 408.2 | 463.7 | 185.48 | 216.8154 | 232.6 | 265.8 | 252.5 | 272.6 | 398.5 | 40.9 | 20.6 | 67.7 | 3.4 | 759.4 | 664.1 | 759.3 | 224.5 | 682 | 781.2 | 779.4
935.2 | 409.2 | 463 | 185.2 | 216.4881 | 232 | 266.2 | 252.2 | 273.2 | 396 | 41.3 | 20.6 | 67.6 | 3.7 | 765.9 | 694.4 | 776.2 | 227.2 | 685.9 | 784.1 | 789
936.2 | 410.2 | 462.4 | 184.96 | 216.2076 | 231.9 | 267.5 | 252.4 | 273.4 | 398.3 | 41.4 | 20.6 | 67.4 | 3.2 | 771.7 | 707.5 | 771.9 | 229 | 693.1 | 795.1 | 789.3
937.2 | 411.2 | 462.7 | 185.08 | 216.3479 | 232.6 | 268.4 | 252.8 | 274.4 | 397.2 | 41.2 | 20.6 | 67.3 | 3.3 | 774.8 | 717.7 | 772.1 | 229.6 | 705.2 | 806.5 | 790.8
938.2 | 412.2 | 464.2 | 185.68 | 217.0492 | 233.7 | 267.6 | 253.4 | 274.5 | 407.6 | 41 | 20.6 | 67.3 | 2.8 | 773.6 | 710.7 | 759.9 | 230.6 | 707.4 | 814.4 | 785.9
939.2 | 413.2 | 464 | 185.6 | 216.9557 | 233.1 | 266.6 | 252.8 | 274.2 | 405.4 | 41.1 | 20.6 | 67.2 | 2.6 | 771.8 | 716.7 | 755.6 | 232.7 | 714.3 | 814.8 | 784.8
940.2 | 414.2 | 463.6 | 185.44 | 216.7687 | 231.6 | 266.4 | 252.5 | 273.4 | 402.8 | 41.3 | 20.6 | 67.3 | 2.7 | 773.3 | 719.5 | 753.1 | 236.6 | 714 | 811.6 | 787.7
941.2 | 415.2 | 464.6 | 185.84 | 217.2363 | 230.8 | 266.5 | 251.9 | 272.1 | 398.8 | 41.4 | 20.6 | 67.4 | 2.9 | 770 | 708.2 | 739.2 | 236.7 | 717.5 | 813.7 | 787.8
942.2 | 416.2 | 464 | 185.6 | 216.9557 | 230.4 | 267.3 | 251.8 | 272.1 | 395.7 | 41.5 | 20.6 | 67.5 | 2.7 | 766.7 | 696.3 | 729.2 | 236.8 | 740.8 | 811.9 | 780.6
943.2 | 417.2 | 462.6 | 185.04 | 216.3011 | 231 | 268.2 | 251.8 | 271.6 | 397.7 | 41.5 | 20.6 | 67.6 | 2.6 | 759.6 | 685.2 | 700.3 | 235.3 | 746.7 | 781.2 | 761.5
944.2 | 418.2 | 462.9 | 185.16 | 216.4414 | 232.4 | 268.4 | 252 | 271 | 400.8 | 41.3 | 20.6 | 67.7 | 2.7 | 752.8 | 676.2 | 680.7 | 231.9 | 755 | 763.4 | 752.3
945.2 | 419.2 | 463.3 | 185.32 | 216.6284 | 232.9 | 268 | 251.5 | 270.5 | 403.6 | 41.3 | 20.6 | 67.7 | 3 | 746.5 | 664.5 | 657.5 | 230.2 | 764.3 | 750.8 | 745.8
946.2 | 420.2 | 463.8 | 185.52 | 216.8622 | 233.2 | 267.2 | 252.8 | 271 | 409 | 41.2 | 20.6 | 68 | 3.8 | 742.9 | 665.9 | 654.6 | 233.3 | 773.4 | 771.2 | 755.9
947.2 | 421.2 | 464.6 | 185.84 | 217.2363 | 232.8 | 267.1 | 253.8 | 270.9 | 415.5 | 41.2 | 20.6 | 68.2 | 4 | 750.5 | 698.5 | 682.4 | 230.5 | 779.1 | 788.5 | 768.2
948.2 | 422.2 | 464 | 185.6 | 216.9557 | 233 | 267.1 | 254.4 | 271.2 | 423.7 | 41.1 | 20.6 | 68.4 | 3.6 | 757.6 | 714.7 | 725 | 226.4 | 758.1 | 781.9 | 779.6
949.2 | 423.2 | 463.4 | 185.36 | 216.6752 | 232.8 | 267.6 | 254 | 271.7 | 417.8 | 41.5 | 20.6 | 68.7 | 3.4 | 755.3 | 711.9 | 745.8 | 223.4 | 736.7 | 765.8 | 779.9
950.2 | 424.2 | 464 | 185.6 | 216.9557 | 233 | 268.2 | 254.5 | 271.9 | 410.8 | 41.8 | 20.6 | 68.9 | 2.9 | 757.8 | 715.8 | 752.7 | 223 | 745.1 | 781.1 | 788.1
951.2 | 425.2 | 464.1 | 185.64 | 217.0025 | 233.1 | 268 | 253.9 | 272.8 | 408.6 | 42 | 20.6 | 68.9 | 3.1 | 756.1 | 710.5 | 741.2 | 226.2 | 748.3 | 790.6 | 786
952.2 | 426.2 | 461.5 | 184.6 | 215.7868 | 232.7 | 268 | 253.9 | 273.5 | 408.3 | 42.1 | 20.6 | 68.9 | 3.5 | 756.5 | 712.8 | 752.9 | 226.4 | 742.8 | 798.6 | 788.4
953.2 | 427.2 | 460 | 184 | 215.0854 | 233.3 | 269.2 | 254.1 | 274.2 | 409.5 | 42.2 | 20.6 | 68.8 | 3.6 | 757 | 709.7 | 759 | 224.8 | 733.9 | 796.6 | 791.7
954.2 | 428.2 | 462.3 | 184.92 | 216.1608 | 234.6 | 270 | 253.8 | 275.1 | 410.2 | 42.2 | 20.6 | 68.8 | 3.4 | 756.8 | 707 | 754.7 | 225.2 | 741.1 | 815.2 | 791
955.2 | 429.2 | 463 | 185.2 | 216.4881 | 234.9 | 270.3 | 254.1 | 275.3 | 412.6 | 42.1 | 20.6 | 68.7 | 3.7 | 752.2 | 689.3 | 727.8 | 224.3 | 735.1 | 818.1 | 792.1
956.2 | 430.2 | 463.3 | 185.32 | 216.6284 | 234.8 | 271.1 | 255.2 | 275.2 | 410.4 | 42.1 | 20.6 | 68.8 | 3.9 | 744.3 | 668.9 | 713.5 | 222.8 | 725.4 | 807.5 | 791.2
957.2 | 431.2 | 462.5 | 185 | 216.2543 | 235.8 | 272.3 | 255.9 | 275.4 | 407.7 | 42 | 20.6 | 68.9 | 3.3 | 740.4 | 661.7 | 714.7 | 220.4 | 720.2 | 810.1 | 788.4
958.2 | 432.2 | 462.3 | 184.92 | 216.1608 | 234.9 | 271.7 | 256.2 | 276.5 | 405.5 | 42.1 | 20.6 | 68.8 | 3.2 | 735 | 649.1 | 695.7 | 220.8 | 716.1 | 811.3 | 786.9
959.2 | 433.2 | 463.2 | 185.28 | 216.5816 | 234.7 | 271.2 | 256.7 | 276.7 | 405.9 | 42.4 | 20.6 | 68.9 | 4.5 | 726 | 626.3 | 667.9 | 225 | 722.5 | 778.6 | 771.3
960.2 | 434.2 | 463.2 | 185.28 | 216.5816 | 234.1 | 269.6 | 256.7 | 276.7 | 403 | 42.6 | 20.6 | 69 | 3.4 | 715.1 | 605.6 | 648.2 | 226 | 727.2 | 765.2 | 761.8
961.2 | 435.2 | 462.8 | 185.12 | 216.3946 | 233.9 | 268.8 | 257 | 276.3 | 399 | 42.6 | 20.6 | 69 | 3 | 706.3 | 590.8 | 633.1 | 225 | 724.1 | 753.7 | 757.7
962.2 | 436.2 | 463.7 | 185.48 | 216.8154 | 235.2 | 268.2 | 256.9 | 275.6 | 400.1 | 42.5 | 20.6 | 69 | 3.7 | 702.4 | 587.8 | 630.5 | 223.2 | 742.6 | 764.4 | 760.1
963.2 | 437.2 | 463.2 | 185.28 | 216.5816 | 236.9 | 267.7 | 258.1 | 274.1 | 405.1 | 42.5 | 20.6 | 68.9 | 3.8 | 707.5 | 617.2 | 641.2 | 220.9 | 749 | 767.8 | 759.1
964.2 | 438.2 | 461.3 | 184.52 | 215.6932 | 237.1 | 267.7 | 259.3 | 273.2 | 415 | 42.4 | 20.6 | 68.9 | 3.2 | 715.4 | 648.6 | 652.4 | 219.8 | 748.2 | 757.2 | 757.9
965.2 | 439.2 | 463.3 | 185.32 | 216.6284 | 237 | 267.5 | 258 | 272.3 | 416.3 | 42.3 | 20.6 | 69 | 3.2 | 725.2 | 680.3 | 685.7 | 222.2 | 740.1 | 740.4 | 758.6
966.2 | 440.2 | 462.6 | 185.04 | 216.3011 | 237.2 | 267 | 257.9 | 271.8 | 415.9 | 42.2 | 20.6 | 69.1 | 3.4 | 728.9 | 693 | 713.6 | 223.9 | 731.4 | 744.7 | 766
967.2 | 441.2 | 463.7 | 185.48 | 216.8154 | 237.5 | 266.7 | 257.9 | 273.2 | 415.3 | 42.3 | 20.6 | 69.2 | 3.6 | 736.2 | 710 | 742.2 | 226.1 | 728.6 | 744.4 | 779.1
968.2 | 442.2 | 463.6 | 185.44 | 216.7687 | 238.7 | 266.7 | 258.2 | 274.3 | 419.7 | 42.2 | 20.6 | 69.2 | 3.6 | 746.4 | 740.5 | 758.9 | 226.1 | 726.5 | 734.4 | 781.7
969.2 | 443.2 | 463.6 | 185.44 | 216.7687 | 239.1 | 268.2 | 258.8 | 274.2 | 437.4 | 42 | 20.6 | 69.1 | 3.1 | 757 | 770.7 | 765.1 | 227.4 | 737.1 | 725 | 773.7
970.2 | 444.2 | 463.9 | 185.56 | 216.9089 | 239.5 | 269 | 259.8 | 274.1 | 447.8 | 41.9 | 20.6 | 69.1 | 2.9 | 764.3 | 790.2 | 757 | 228 | 748.1 | 711.4 | 761.2
971.2 | 445.2 | 463 | 185.2 | 216.4881 | 241.1 | 269.8 | 260.6 | 273.8 | 448.6 | 41.9 | 20.6 | 69.2 | 2.9 | 768.9 | 802 | 764.9 | 226.3 | 736.5 | 714.1 | 758.3
972.2 | 446.2 | 463.1 | 185.24 | 216.5349 | 242.5 | 269.9 | 261.5 | 273.4 | 449.8 | 41.9 | 20.6 | 69.1 | 2.8 | 773.4 | 813.3 | 770.2 | 226.1 | 720.2 | 715.5 | 760.1
973.2 | 447.2 | 464 | 185.6 | 216.9557 | 242.3 | 270.2 | 262 | 272.8 | 465.7 | 42 | 20.6 | 69.1 | 2.7 | 777.3 | 823.9 | 779.9 | 225.6 | 696 | 703.6 | 754.5
974.2 | 448.2 | 462.8 | 185.12 | 216.3946 | 242.3 | 269.4 | 263.4 | 273.3 | 479.5 | 42.2 | 20.6 | 69.1 | 2.6 | 782.8 | 832.2 | 801.9 | 226 | 683.8 | 700.6 | 761.7
975.2 | 449.2 | 463.6 | 185.44 | 216.7687 | 242.8 | 268.1 | 264.2 | 273.2 | 482 | 42.2 | 20.6 | 69 | 3.2 | 783.7 | 825.6 | 809.8 | 229.2 | 670.1 | 699.7 | 773.5
976.2 | 450.2 | 463.4 | 185.36 | 216.6752 | 244.2 | 267.3 | 265.7 | 273.4 | 475.5 | 42.1 | 20.6 | 69 | 3.6 | 778.4 | 807.2 | 797.1 | 231.4 | 678 | 701.8 | 766.4
977.2 | 451.2 | 463.9 | 185.56 | 216.9089 | 245.2 | 267.2 | 267.1 | 274.1 | 468 | 42.1 | 20.6 | 68.8 | 3 | 772.4 | 786.9 | 762.2 | 233.3 | 701.5 | 710.9 | 753.6
978.2 | 452.2 | 463.4 | 185.36 | 216.6752 | 245.1 | 267.9 | 267.7 | 274.3 | 460.1 | 42.1 | 20.6 | 68.6 | 3 | 761.6 | 754.3 | 722.7 | 231.2 | 712.5 | 707.5 | 745
979.2 | 453.2 | 464 | 185.6 | 216.9557 | 244.3 | 268.4 | 267.9 | 274.9 | 445 | 42.1 | 20.6 | 68.5 | 3.4 | 749.9 | 729.7 | 698.4 | 228.9 | 713.9 | 701.6 | 739.3
980.2 | 454.2 | 463.4 | 185.36 | 216.6752 | 244.1 | 268.4 | 267.9 | 273.8 | 434.3 | 42.1 | 20.6 | 68.5 | 3 | 746.1 | 729.9 | 687.5 | 229.8 | 732.4 | 704.5 | 740.4
981.2 | 455.2 | 463.8 | 185.52 | 216.8622 | 244.9 | 268.2 | 268.1 | 272.7 | 430 | 41.9 | 20.5 | 68.7 | 3.3 | 743 | 728.3 | 677.5 | 230.3 | 746.2 | 705.8 | 739.7
982.2 | 456.2 | 463.1 | 185.24 | 216.5349 | 245.7 | 268.2 | 268 | 272.5 | 429.7 | 41.9 | 20.5 | 68.8 | 3.3 | 734.7 | 711.8 | 651.5 | 230 | 748.9 | 684 | 725.2
983.2 | 457.2 | 464.3 | 185.72 | 217.096 | 246.2 | 267.7 | 267.8 | 272.5 | 429.3 | 41.9 | 20.5 | 69 | 3.4 | 722.6 | 682.4 | 633.1 | 232.2 | 742.6 | 667.3 | 720.7
984.2 | 458.2 | 463.2 | 185.28 | 216.5816 | 246.8 | 266.5 | 267.4 | 272.4 | 421.9 | 42 | 20.5 | 69.2 | 3.4 | 713.6 | 667 | 624.1 | 230.9 | 765.4 | 687.6 | 725.6
985.2 | 459.2 | 463.8 | 185.52 | 216.8622 | 247.8 | 266 | 268.1 | 271.9 | 420.3 | 42.1 | 20.5 | 69.4 | 2.9 | 711 | 660.4 | 623.1 | 228.7 | 779.7 | 706.7 | 732.5
986.2 | 460.2 | 462.9 | 185.16 | 216.4414 | 247.5 | 266.4 | 268 | 271.5 | 416.9 | 42.2 | 20.5 | 69.6 | 2.9 | 715.5 | 672.6 | 644.9 | 229.7 | 789.4 | 722.9 | 736.9
987.2 | 461.2 | 463.3 | 185.32 | 216.6284 | 246.5 | 266.4 | 267.7 | 271.3 | 415.1 | 42.3 | 20.5 | 69.8 | 2.8 | 716.8 | 676.1 | 654.4 | 231.2 | 790.8 | 748.2 | 749.6
988.2 | 462.2 | 463.9 | 185.56 | 216.9089 | 246 | 265.8 | 266.9 | 272.8 | 410.8 | 42.2 | 20.5 | 69.8 | 2.7 | 723.1 | 692.8 | 686.5 | 230.9 | 774.3 | 754.8 | 759.3
989.2 | 463.2 | 463.8 | 185.52 | 216.8622 | 245.4 | 265.7 | 267.1 | 272.8 | 410.6 | 42.1 | 20.5 | 69.7 | 2.6 | 728.1 | 706.9 | 710.4 | 229.5 | 759.8 | 763.4 | 766.4
990.2 | 464.2 | 463.7 | 185.48 | 216.8154 | 244.4 | 266.6 | 267.5 | 272.9 | 410.9 | 41.9 | 20.5 | 69.7 | 3.3 | 734.9 | 724.6 | 728.8 | 226.9 | 757.3 | 777.5 | 772
991.2 | 465.2 | 464.1 | 185.64 | 217.0025 | 243.8 | 266.9 | 267.6 | 273.5 | 410.9 | 41.7 | 20.5 | 69.8 | 3.1 | 742.5 | 735 | 739.9 | 223.5 | 755.1 | 786.5 | 772.4
992.2 | 466.2 | 463.6 | 185.44 | 216.7687 | 243.4 | 266.8 | 268 | 273.9 | 415.5 | 41.6 | 20.5 | 69.8 | 3.1 | 747.4 | 741.3 | 741.8 | 218.7 | 749.7 | 787.8 | 774.1
993.2 | 467.2 | 463.8 | 185.52 | 216.8622 | 243.6 | 267.3 | 268.4 | 274.3 | 420.1 | 41.8 | 20.5 | 69.8 | 3.3 | 745.3 | 730 | 737.5 | 216 | 744.4 | 800.2 | 779.1
994.2 | 468.2 | 463.3 | 185.32 | 216.6284 | 243.5 | 267.8 | 268.2 | 274.9 | 418.6 | 41.9 | 20.5 | 69.8 | 3.4 | 739.1 | 711.6 | 721.1 | 214.8 | 747.2 | 798.8 | 781.7
995.2 | 469.2 | 464.4 | 185.76 | 217.1427 | 244.6 | 268.8 | 268.9 | 275.6 | 420.5 | 42 | 20.5 | 69.9 | 3.3 | 733.5 | 695.2 | 709.9 | 215.6 | 754.4 | 807.3 | 781
996.2 | 470.2 | 463.9 | 185.56 | 216.9089 | 245.4 | 269.6 | 268.8 | 275.9 | 424.4 | 41.9 | 20.5 | 69.9 | 3.1 | 730.6 | 694.3 | 709.5 | 217.6 | 767.3 | 810.9 | 775.1
997.2 | 471.2 | 464.2 | 185.68 | 217.0492 | 246 | 269.4 | 268.4 | 276.7 | 431.2 | 41.8 | 20.5 | 70 | 2.9 | 727.8 | 688.3 | 697.5 | 219.3 | 764.8 | 819.1 | 774.5
998.2 | 472.2 | 464.7 | 185.88 | 217.283 | 246.8 | 268.7 | 268.7 | 276.7 | 432.7 | 41.8 | 20.5 | 69.9 | 3 | 718.5 | 666.8 | 700.8 | 223.3 | 742.6 | 823.8 | 774.4
999.2 | 473.2 | 463.5 | 185.4 | 216.7219 | 247.2 | 269 | 268.6 | 276.5 | 424.6 | 41.9 | 20.5 | 69.9 | 3.3 | 714.4 | 661.8 | 721.8 | 226.4 | 724 | 810.8 | 776.6
1000.2 | 474.2 | 462.8 | 185.12 | 216.3946 | 247.1 | 270.1 | 268.2 | 276.7 | 422.4 | 42 | 20.5 | 70 | 3.3 | 711.4 | 656 | 748.1 | 225.4 | 704.5 | 804.4 | 781
1001.2 | 475.2 | 464.3 | 185.72 | 217.096 | 246.1 | 270.1 | 266.7 | 277.8 | 419.3 | 42.1 | 20.5 | 70 | 3 | 710.5 | 657.7 | 758.1 | 223.3 | 699.4 | 803.8 | 781.4
1002.2 | 476.2 | 463.4 | 185.36 | 216.6752 | 246.5 | 270.3 | 266.1 | 278.3 | 416.2 | 42.2 | 20.5 | 70.2 | 2.7 | 704.4 | 641.8 | 740.2 | 221.6 | 711.1 | 812.6 | 780
1003.2 | 477.2 | 463.4 | 185.36 | 216.6752 | 245.9 | 270.9 | 265.7 | 277.6 | 414.6 | 42.3 | 20.5 | 70.4 | 3.3 | 703.9 | 640.7 | 732.6 | 220.8 | 726.4 | 811.3 | 779.8
1004.2 | 478.2 | 464.5 | 185.8 | 217.1895 | 244.8 | 271.1 | 265.2 | 277.2 | 418.1 | 42.5 | 20.5 | 70.7 | 3 | 703.7 | 639.7 | 711.8 | 219.3 | 744.7 | 782.9 | 760.3
1005.2 | 479.2 | 464.2 | 185.68 | 217.0492 | 243.4 | 271.4 | 264.3 | 276.8 | 416.8 | 42.5 | 20.5 | 70.9 | 3.2 | 708.5 | 659 | 700.4 | 218.6 | 754.2 | 789.3 | 756
1006.2 | 480.2 | 463.7 | 185.48 | 216.8154 | 242.8 | 271.4 | 263.1 | 276.4 | 420.7 | 42.5 | 20.5 | 70.9 | 2.8 | 705.9 | 659.1 | 687.5 | 218.1 | 761.4 | 781.1 | 752.1
1007.2 | 481.2 | 465.2 | 186.08 | 217.5168 | 243 | 271.6 | 263.4 | 275.9 | 417.5 | 42.4 | 20.5 | 70.8 | 2.5 | 699.8 | 648.3 | 666.3 | 216.1 | 756.5 | 755.8 | 739.4
1008.2 | 482.2 | 464.8 | 185.92 | 217.3298 | 243.9 | 271.7 | 263.6 | 275.9 | 414.1 | 42.3 | 20.5 | 70.9 | 2.8 | 694.9 | 637.3 | 655 | 215.9 | 762.1 | 745.3 | 734.8
1009.2 | 483.2 | 464.8 | 185.92 | 217.3298 | 245.1 | 271.5 | 264.3 | 276 | 415.5 | 42.2 | 20.5 | 70.9 | 2.8 | 691.4 | 632.2 | 652.5 | 217.4 | 776.6 | 768.1 | 747.7
1010.2 | 484.2 | 464.6 | 185.84 | 217.2363 | 247 | 271 | 264.8 | 276.2 | 416.9 | 42 | 20.5 | 71 | 3 | 684.1 | 616.6 | 635.6 | 223.2 | 786.3 | 772.1 | 753.4
1011.2 | 485.2 | 465.3 | 186.12 | 217.5636 | 247.7 | 270.3 | 264.6 | 276 | 415.3 | 42 | 20.5 | 71.1 | 2.9 | 679.9 | 612.6 | 630 | 225.2 | 770.6 | 785 | 762
1012.2 | 486.2 | 465.4 | 186.16 | 217.6103 | 246.8 | 270.1 | 264.1 | 276 | 409.6 | 42 | 20.5 | 71.2 | 3 | 673.7 | 602.5 | 650.6 | 222.4 | 756.1 | 793.1 | 767
1013.2 | 487.2 | 464.9 | 185.96 | 217.3765 | 246.8 | 270.1 | 264.1 | 275.8 | 410.7 | 42.2 | 20.5 | 71.3 | 2.8 | 684.7 | 633.3 | 675.1 | 219.2 | 751.4 | 806 | 777.8
1014.2 | 488.2 | 464.8 | 185.92 | 217.3298 | 246.8 | 269.4 | 264.1 | 275.3 | 415.6 | 42.3 | 20.5 | 71.3 | 3.3 | 693.4 | 652.7 | 688.7 | 217.7 | 754.7 | 809.4 | 782.5
1015.2 | 489.2 | 465.3 | 186.12 | 217.5636 | 246.2 | 269.1 | 263.8 | 274.3 | 416.5 | 42.4 | 20.5 | 71.3 | 3.9 | 703.9 | 680.1 | 694.7 | 216.2 | 759.8 | 807.6 | 776.8
1016.2 | 490.2 | 465.2 | 186.08 | 217.5168 | 246.4 | 268.6 | 264 | 273.7 | 420.2 | 42.4 | 20.5 | 71.4 | 4.3 | 703.6 | 674.8 | 679.6 | 214.6 | 769.4 | 808.2 | 765.1
1017.2 | 491.2 | 464.3 | 185.72 | 217.096 | 247.3 | 268 | 264.1 | 273.9 | 420.5 | 42.4 | 20.5 | 71.3 | 3.8 | 698.6 | 666.2 | 676.3 | 221 | 772.6 | 811.5 | 761.8
1018.2 | 492.2 | 463.9 | 185.56 | 216.9089 | 248 | 267.8 | 263.8 | 273.8 | 422.6 | 42.4 | 20.5 | 71.4 | 3.7 | 698.2 | 667.5 | 674.7 | 224.3 | 782.5 | 815.2 | 763.3
1019.2 | 493.2 | 464.8 | 185.92 | 217.3298 | 247.9 | 267.5 | 264.5 | 273 | 423.3 | 42.3 | 20.5 | 71.4 | 3.4 | 696.6 | 662.9 | 670.2 | 227.2 | 787.4 | 810.7 | 754.8
1020.2 | 494.2 | 464.7 | 185.88 | 217.283 | 247.2 | 266.6 | 264.7 | 272.7 | 430.6 | 42.1 | 20.5 | 71.6 | 3.6 | 696.2 | 663.8 | 658.4 | 228.5 | 795.5 | 802.7 | 752.2
1021.2 | 495.2 | 464.6 | 185.84 | 217.2363 | 247.4 | 266.5 | 264.8 | 271.8 | 433.4 | 42 | 20.5 | 71.8 | 3.7 | 698.3 | 670.6 | 674.8 | 228.3 | 797.2 | 798 | 755.1
1022.2 | 496.2 | 464.3 | 185.72 | 217.096 | 247.9 | 267 | 264.6 | 271.4 | 430.1 | 42 | 20.5 | 71.9 | 3.1 | 702.6 | 681.6 | 690.6 | 229.6 | 794.2 | 792.6 | 759.9
1023.2 | 497.2 | 463.9 | 185.56 | 216.9089 | 248.5 | 266.7 | 264.5 | 271.1 | 429.3 | 42.2 | 20.5 | 71.9 | 3.3 | 709.4 | 699.2 | 711 | 229.7 | 797.1 | 798.7 | 765
1024.2 | 498.2 | 464.6 | 185.84 | 217.2363 | 249.3 | 266.7 | 264 | 271.3 | 433.7 | 42.4 | 20.5 | 71.8 | 3.2 | 710.9 | 699.3 | 732.6 | 231.4 | 794.1 | 805.6 | 773.6
1025.2 | 499.2 | 464.7 | 185.88 | 217.283 | 249.7 | 267.2 | 263.5 | 271.6 | 427.7 | 42.5 | 20.5 | 71.7 | 2.9 | 703.4 | 680.7 | 722.3 | 230.6 | 765.8 | 803.7 | 778.9
1026.2 | 500.2 | 464.8 | 185.92 | 217.3298 | 249.7 | 268.1 | 263.6 | 271.9 | 420.1 | 42.7 | 20.5 | 71.7 | 3.1 | 690.5 | 655.3 | 705.9 | 237.9 | 742.9 | 784 | 773.7
1027.2 | 501.2 | 463.7 | 185.48 | 216.8154 | 248.5 | 269.2 | 263.9 | 272 | 411.4 | 42.8 | 20.5 | 71.8 | 3.4 | 683.1 | 640.1 | 705 | 242.7 | 714.7 | 778.7 | 772.3
1028.2 | 502.2 | 464.1 | 185.64 | 217.0025 | 247.8 | 270.8 | 263.9 | 271.6 | 404.7 | 42.8 | 20.5 | 71.8 | 3.2 | 682.9 | 637.9 | 711.7 | 248.4 | 707.3 | 790.6 | 770.7
1029.2 | 503.2 | 464.1 | 185.64 | 217.0025 | 247.7 | 271.5 | 263.8 | 270.9 | 403.9 | 42.9 | 20.5 | 71.8 | 2.8 | 685.5 | 638.9 | 722.8 | 248.8 | 712 | 808.3 | 778.9
1030.2 | 504.2 | 463.9 | 185.56 | 216.9089 | 249.3 | 271.8 | 263.4 | 270 | 409.2 | 42.9 | 20.5 | 71.8 | 3 | 692.7 | 660.6 | 721.6 | 251.6 | 729.8 | 803.8 | 778
1031.2 | 505.2 | 464.8 | 185.92 | 217.3298 | 249.4 | 270.7 | 262.6 | 269.8 | 414.4 | 43 | 20.5 | 71.8 | 3.1 | 697.2 | 675.4 | 702 | 247.9 | 741.3 | 784.1 | 761.4
1032.2 | 506.2 | 464.4 | 185.76 | 217.1427 | 249.8 | 269.2 | 261.1 | 269.9 | 412.1 | 43.1 | 20.4 | 71.9 | 3.4 | 697.6 | 688.7 | 687 | 243.1 | 734.6 | 760.7 | 744.7
1033.2 | 507.2 | 464.7 | 185.88 | 217.283 | 249.6 | 268.2 | 261.1 | 270.1 | 414.8 | 43.2 | 20.5 | 72 | 3.5 | 705.2 | 717.7 | 700.6 | 237.4 | 719.8 | 746.8 | 745.3
1034.2 | 508.2 | 465.1 | 186.04 | 217.47 | 249.5 | 267.3 | 261.4 | 270.4 | 417.8 | 43.4 | 20.5 | 72.1 | 3.5 | 713.5 | 747.7 | 704.6 | 233.7 | 722.6 | 732.7 | 742.9
1035.2 | 509.2 | 464.5 | 185.8 | 217.1895 | 249.9 | 266.7 | 261.4 | 270.4 | 423.1 | 43.5 | 20.5 | 72.2 | 3.3 | 722.2 | 766.1 | 730.9 | 234.2 | 709.7 | 738.5 | 752.3
1036.2 | 510.2 | 464.6 | 185.84 | 217.2363 | 249.9 | 267.4 | 261.9 | 270.7 | 426.4 | 43.5 | 20.5 | 72.2 | 2.9 | 727.4 | 773.3 | 746.7 | 236.3 | 706 | 755 | 768.2
1037.2 | 511.2 | 464.9 | 185.96 | 217.3765 | 249.5 | 268.3 | 262.9 | 271.4 | 426.7 | 43.4 | 20.5 | 72.2 | 2.8 | 735.6 | 780.7 | 758.3 | 234.7 | 706.2 | 749.1 | 768.3
1038.2 | 512.2 | 464.5 | 185.8 | 217.1895 | 248.7 | 269.2 | 263.9 | 273 | 423 | 43.3 | 20.4 | 72.1 | 2.9 | 725.5 | 750.7 | 718.6 | 231.5 | 710.2 | 718.9 | 748.7
1039.2 | 513.2 | 464 | 185.6 | 216.9557 | 248.4 | 269.7 | 265.5 | 274.1 | 414.6 | 43.2 | 20.4 | 72.1 | 2.8 | 712.7 | 727.9 | 691.8 | 229.5 | 714.6 | 714.4 | 739.6
1040.2 | 514.2 | 464.7 | 185.88 | 217.283 | 247.8 | 270.1 | 266.1 | 274.6 | 411.9 | 43.1 | 20.4 | 72.2 | 3 | 708.7 | 729.4 | 681.6 | 227.4 | 715 | 700.1 | 734
1041.2 | 515.2 | 464.7 | 185.88 | 217.283 | 247.6 | 270.5 | 266.4 | 274.8 | 415.7 | 43 | 20.4 | 72.3 | 2.8 | 711 | 736.2 | 669.8 | 229 | 720.6 | 690.2 | 728.2
1042.2 | 516.2 | 464.1 | 185.64 | 217.0025 | 248.3 | 270.5 | 266.4 | 274.5 | 425.7 | 43.1 | 20.4 | 72.3 | 2.7 | 712.6 | 737 | 652.2 | 228.3 | 741 | 699.5 | 724.6
1043.2 | 517.2 | 464.8 | 185.92 | 217.3298 | 248.9 | 270.8 | 267.1 | 274.4 | 436.1 | 43.2 | 20.4 | 72.3 | 2.9 | 707.1 | 715.1 | 641.6 | 230.7 | 760.2 | 713 | 724.5
1044.2 | 518.2 | 464.4 | 185.76 | 217.1427 | 249.8 | 269.9 | 267.6 | 275 | 442.5 | 43.2 | 20.4 | 72.4 | 3.1 | 703.3 | 706.1 | 635.2 | 234.1 | 775 | 724 | 727.8
1045.2 | 519.2 | 464.1 | 185.64 | 217.0025 | 250.6 | 269.4 | 268.2 | 275.7 | 440.1 | 43.2 | 20.4 | 72.4 | 3.2 | 698.9 | 698.9 | 631.9 | 233.3 | 788.3 | 740.4 | 728.6
1046.2 | 520.2 | 464.6 | 185.84 | 217.2363 | 250.6 | 268.6 | 269.1 | 275.9 | 432.7 | 43.2 | 20.4 | 72.4 | 2.9 | 694.4 | 687.3 | 635.2 | 233.4 | 800.3 | 749.2 | 729.5
1047.2 | 521.2 | 464.2 | 185.68 | 217.0492 | 250.6 | 268.4 | 269.4 | 275.9 | 432.3 | 43.3 | 20.4 | 72.6 | 3.3 | 695.4 | 697.4 | 638.3 | 232.2 | 795.1 | 760.8 | 734.3
1048.2 | 522.2 | 463.7 | 185.48 | 216.8154 | 251.1 | 268.9 | 269.2 | 275.5 | 433.9 | 43.2 | 20.4 | 72.6 | 2.8 | 701.4 | 702.9 | 654 | 231.8 | 806.8 | 783.5 | 746.9
1049.2 | 523.2 | 464.8 | 185.92 | 217.3298 | 252.1 | 268.4 | 268.7 | 275 | 450.1 | 43.2 | 20.4 | 72.6 | 2.8 | 707.6 | 713.4 | 663.9 | 231 | 805.2 | 780.3 | 745.1
1050.2 | 524.2 | 464.3 | 185.72 | 217.096 | 252 | 267.3 | 268.6 | 274.8 | 458.1 | 43.3 | 20.4 | 72.7 | 2.9 | 713.7 | 723.7 | 686 | 230.7 | 801.9 | 778.4 | 747.3
1051.2 | 525.2 | 465.2 | 186.08 | 217.5168 | 251.4 | 266.4 | 269.1 | 275.6 | 452.5 | 43.5 | 20.4 | 72.6 | 2.9 | 718.6 | 735.3 | 698.7 | 234.3 | 805.9 | 799.9 | 751.2
1052.2 | 526.2 | 465 | 186 | 217.4233 | 250.3 | 266.4 | 269.3 | 276 | 455.1 | 43.5 | 20.4 | 72.6 | 3.2 | 726.6 | 752.5 | 722.3 | 235.1 | 811.7 | 813.7 | 760.5
1053.2 | 527.2 | 464.9 | 185.96 | 217.3765 | 250.2 | 266.6 | 270.3 | 276.5 | 456.7 | 43.4 | 20.4 | 72.8 | 3.5 | 732.5 | 760.5 | 723.1 | 240 | 811.3 | 815.5 | 760
1054.2 | 528.2 | 464.8 | 185.92 | 217.3298 | 250.8 | 268.2 | 271.2 | 276.7 | 455.6 | 43.5 | 20.4 | 72.9 | 3.2 | 737.4 | 771 | 721.1 | 236.6 | 811.2 | 820.8 | 755.2
1055.2 | 529.2 | 465 | 186 | 217.4233 | 250.3 | 270.1 | 271.8 | 276.3 | 453.7 | 43.4 | 20.4 | 72.8 | 3.1 | 739.4 | 771.1 | 722.2 | 235.7 | 814.3 | 821.3 | 758.4
1056.2 | 530.2 | 464.2 | 185.68 | 217.0492 | 249.7 | 272 | 271.9 | 276.1 | 452.5 | 43.4 | 20.4 | 72.7 | 2.9 | 738.3 | 763.7 | 724.9 | 234.2 | 808.2 | 821.7 | 765.1
1057.2 | 531.2 | 465.2 | 186.08 | 217.5168 | 248.9 | 272.3 | 272 | 276 | 448.7 | 43.6 | 20.4 | 72.6 | 2.7 | 730.7 | 746.7 | 717.8 | 232.3 | 783.6 | 812.8 | 767.6
1058.2 | 532.2 | 465.5 | 186.2 | 217.6571 | 250.2 | 272.5 | 271.1 | 275.8 | 441 | 43.7 | 20.4 | 72.6 | 2.7 | 728.4 | 739.4 | 733.3 | 230.4 | 759.5 | 805.7 | 772.8
1059.2 | 533.2 | 465.1 | 186.04 | 217.47 | 251.5 | 273.2 | 270.7 | 275.6 | 442.7 | 43.6 | 20.4 | 72.6 | 2.5 | 717.8 | 715.7 | 739.9 | 228.9 | 734.9 | 792 | 773.3
1060.2 | 534.2 | 464.8 | 185.92 | 217.3298 | 252.1 | 275.1 | 271.1 | 276 | 431.2 | 43.9 | 20.4 | 72.7 | 3.1 | 714.2 | 713.1 | 754.5 | 229 | 712.6 | 778.4 | 770
1061.2 | 535.2 | 464.7 | 185.88 | 217.283 | 252.8 | 276.7 | 271.6 | 276 | 427.9 | 44.1 | 20.4 | 72.6 | 2.7 | 724.2 | 743.6 | 785.1 | 230.8 | 712.4 | 776.8 | 767.3
1062.2 | 536.2 | 465.4 | 186.16 | 217.6103 | 252.8 | 276.8 | 271.5 | 275.9 | 444.3 | 44.1 | 20.4 | 72.6 | 3 | 737.8 | 774.3 | 789.7 | 231.4 | 721.1 | 773.4 | 759.8
1063.2 | 537.2 | 463.9 | 185.56 | 216.9089 | 253.2 | 277.3 | 271.4 | 276.2 | 453.8 | 44.2 | 20.4 | 72.6 | 3 | 742.8 | 784.1 | 783 | 232.7 | 738.1 | 765.4 | 749.3
1064.2 | 538.2 | 464.4 | 185.76 | 217.1427 | 253.4 | 277.3 | 271 | 276.4 | 456.8 | 44.2 | 20.4 | 72.8 | 3 | 736.8 | 764.5 | 749 | 232.1 | 765.1 | 757.2 | 738.1
1065.2 | 539.2 | 465 | 186 | 217.4233 | 253.6 | 276.7 | 270.5 | 276.2 | 457.5 | 44.3 | 20.4 | 73 | 3.1 | 719.7 | 722.5 | 703.4 | 234.4 | 766 | 714.1 | 724.9
1066.2 | 540.2 | 464.7 | 185.88 | 217.283 | 253.8 | 276.5 | 270.9 | 276.2 | 453.2 | 44.3 | 20.4 | 73 | 2.7 | 706.1 | 694.1 | 675.4 | 234.6 | 767.7 | 697.3 | 719.7
1067.2 | 541.2 | 465.2 | 186.08 | 217.5168 | 256.6 | 277.5 | 272.4 | 276 | 446.8 | 44.3 | 20.4 | 72.9 | 2.8 | 698.5 | 684.8 | 653.6 | 233.5 | 770.5 | 676.7 | 713.2
1068.2 | 542.2 | 464.1 | 185.64 | 217.0025 | 258 | 277.8 | 272.8 | 274.8 | 439.9 | 44.3 | 20.4 | 72.8 | 3 | 688.6 | 675.7 | 634.1 | 232.9 | 755.4 | 647.8 | 705.2
1069.2 | 543.2 | 464.9 | 185.96 | 217.3765 | 260 | 277.2 | 272.2 | 274.2 | 434.9 | 44.3 | 20.4 | 72.7 | 3.6 | 692 | 699.6 | 640.7 | 231.9 | 755.7 | 665.4 | 707.8
1070.2 | 544.2 | 464.3 | 185.72 | 217.096 | 261.4 | 277.5 | 272 | 274.8 | 444.8 | 44.3 | 20.4 | 72.7 | 3.6 | 703.4 | 730 | 654.2 | 230 | 758.8 | 685.7 | 720.6
1071.2 | 545.2 | 464.7 | 185.88 | 217.283 | 261.2 | 277.7 | 272.5 | 275.2 | 456.2 | 44.3 | 20.4 | 72.7 | 3.5 | 709.4 | 745.6 | 649.5 | 231 | 761.1 | 677.2 | 720.1
1072.2 | 546.2 | 464.6 | 185.84 | 217.2363 | 261.2 | 277.4 | 273.1 | 275.7 | 464.2 | 44.3 | 20.4 | 72.8 | 3.4 | 708 | 739 | 638.7 | 233.1 | 767.1 | 673.1 | 711.3
1073.2 | 547.2 | 464.3 | 185.72 | 217.096 | 260.4 | 276.2 | 274.1 | 276.6 | 455.3 | 44.3 | 20.4 | 72.8 | 3.4 | 708 | 739 | 650 | 237.1 | 759.5 | 676.3 | 715.2
1074.2 | 548.2 | 464.4 | 185.76 | 217.1427 | 261.3 | 276.2 | 274.8 | 277.7 | 449.5 | 44.3 | 20.4 | 72.8 | 3.5 | 704.5 | 735.3 | 627.5 | 233.9 | 760.5 | 662.6 | 707.6
1075.2 | 549.2 | 464.3 | 185.72 | 217.096 | 262 | 276 | 275.4 | 277.3 | 439.3 | 44.3 | 20.4 | 72.9 | 3.7 | 701.4 | 733.5 | 638.9 | 237.8 | 756.7 | 673.5 | 708.2
1076.2 | 550.2 | 464.9 | 185.96 | 217.3765 | 261.9 | 275.7 | 276 | 276.4 | 433.5 | 44.1 | 20.4 | 72.9 | 3.5 | 700.5 | 729.5 | 641.6 | 239.1 | 765.8 | 690.9 | 714.7
1077.2 | 551.2 | 464.3 | 185.72 | 217.096 | 261.7 | 275.2 | 276.4 | 275.9 | 426.2 | 43.9 | 20.4 | 73.1 | 4.2 | 696.4 | 711.7 | 640.8 | 257.1 | 786.6 | 725.9 | 719.7
1078.2 | 552.2 | 464.7 | 185.88 | 217.283 | 261.2 | 275.5 | 276 | 275.6 | 431.6 | 43.9 | 20.4 | 73.1 | 4.3 | 696.3 | 701.5 | 628.6 | 260.4 | 802.4 | 745.4 | 727.9
1079.2 | 553.2 | 464 | 185.6 | 216.9557 | 260 | 275.7 | 275.8 | 275 | 437.9 | 43.9 | 20.4 | 73.2 | 3.9 | 688.1 | 681.3 | 616.7 | 260.5 | 801.3 | 750.7 | 725.3
1080.2 | 554.2 | 463.8 | 185.52 | 216.8622 | 260.2 | 274.8 | 275.2 | 273.8 | 437.7 | 43.9 | 20.4 | 73.2 | 3.5 | 692 | 694.8 | 633.7 | 253.9 | 800.5 | 762.8 | 726.2
1081.2 | 555.2 | 464.4 | 185.76 | 217.1427 | 260.9 | 273.8 | 274.2 | 272.9 | 440.1 | 43.9 | 20.4 | 73.3 | 3.4 | 699.5 | 710.6 | 644.1 | 250.1 | 801.5 | 777.4 | 727.1
1082.2 | 556.2 | 464.3 | 185.72 | 217.096 | 260.7 | 273.2 | 273.2 | 272.6 | 445.6 | 43.8 | 20.4 | 73.4 | 3.1 | 710.2 | 724.9 | 672.4 | 245.7 | 799 | 782.8 | 732
1083.2 | 557.2 | 464.5 | 185.8 | 217.1895 | 260.2 | 273.3 | 272.5 | 273.1 | 452.3 | 44 | 20.4 | 73.6 | 3.8 | 717.4 | 727.4 | 694.2 | 241.9 | 796.3 | 793.7 | 746.5
1084.2 | 558.2 | 464 | 185.6 | 216.9557 | 260.6 | 273.5 | 273.5 | 273.5 | 450.7 | 44.2 | 20.4 | 73.7 | 3.9 | 722.3 | 734 | 703.8 | 244.3 | 795.1 | 790.8 | 751.3
1085.2 | 559.2 | 464.4 | 185.76 | 217.1427 | 260.6 | 274.2 | 273.3 | 273.8 | 446 | 44.3 | 20.4 | 73.8 | 3.6 | 728.3 | 747.3 | 708.5 | 249.8 | 794.1 | 791.5 | 741.6
1086.2 | 560.2 | 464.4 | 185.76 | 217.1427 | 260.3 | 274.1 | 273.4 | 274.3 | 448.3 | 44.3 | 20.4 | 73.9 | 3 | 740.4 | 773.5 | 738.8 | 248.3 | 791.2 | 781.5 | 737.2
1087.2 | 561.2 | 463.6 | 185.44 | 216.7687 | 260.5 | 273.4 | 274.3 | 274.6 | 456.7 | 44.3 | 20.4 | 74 | 2.9 | 750.2 | 789.4 | 763.1 | 247.6 | 784.4 | 780.3 | 746.7
1088.2 | 562.2 | 464.7 | 185.88 | 217.283 | 260.4 | 273.4 | 274.8 | 275.1 | 460.1 | 44.4 | 20.4 | 74.2 | 3.2 | 754.6 | 785.8 | 772.6 | 244.6 | 781.1 | 802.2 | 762.5
1089.2 | 563.2 | 464.2 | 185.68 | 217.0492 | 259.6 | 273.8 | 275.1 | 275.4 | 465.8 | 44.5 | 20.4 | 74.2 | 2.9 | 749.7 | 769.6 | 769 | 242.5 | 762.7 | 788.4 | 767
1090.2 | 564.2 | 464.1 | 185.64 | 217.0025 | 259.4 | 275 | 275.3 | 275.4 | 465.7 | 44.6 | 20.4 | 74.3 | 2.9 | 738.5 | 749.6 | 762.7 | 245 | 742.7 | 786 | 766.6
1091.2 | 565.2 | 463.7 | 185.48 | 216.8154 | 259.5 | 275.6 | 275.4 | 275 | 459.5 | 44.6 | 20.4 | 74.6 | 3.2 | 737.7 | 745.1 | 755.1 | 244.5 | 751.5 | 796.6 | 764.7
1092.2 | 566.2 | 464.2 | 185.68 | 217.0492 | 259 | 275 | 274.6 | 275.3 | 455.4 | 44.5 | 20.4 | 74.7 | 2.7 | 730.2 | 723.5 | 753 | 245.5 | 740.2 | 813.6 | 770.9
1093.2 | 567.2 | 463.7 | 185.48 | 216.8154 | 258.6 | 274.4 | 273.8 | 275.7 | 450 | 44.4 | 20.4 | 74.8 | 3.2 | 728.9 | 719.7 | 772.4 | 243.9 | 726.5 | 807.5 | 777.5
1094.2 | 568.2 | 464.8 | 185.92 | 217.3298 | 258.8 | 274 | 273.4 | 275.8 | 450.1 | 44.5 | 20.4 | 74.9 | 3 | 727 | 714 | 779.9 | 243.6 | 711.9 | 810.6 | 781
1095.2 | 569.2 | 463.9 | 185.56 | 216.9089 | 257.9 | 273.6 | 273 | 276 | 448.8 | 44.8 | 20.4 | 75 | 2.9 | 736.1 | 735.2 | 793.8 | 245.5 | 701.4 | 797.5 | 779.2
1096.2 | 570.2 | 464.2 | 185.68 | 217.0492 | 257.4 | 272.9 | 272.6 | 276.5 | 452 | 44.9 | 20.4 | 75 | 3.4 | 743.8 | 753.7 | 803.7 | 242.8 | 678.5 | 776.1 | 768.7
1097.2 | 571.2 | 464.2 | 185.68 | 217.0492 | 256.9 | 272.2 | 270.9 | 276.3 | 451.1 | 44.8 | 20.4 | 75 | 3.6 | 749.6 | 763 | 814.4 | 241.3 | 676.8 | 780.5 | 776.4
1098.2 | 572.2 | 464.5 | 185.8 | 217.1895 | 255.9 | 271.3 | 269.7 | 276.8 | 450.1 | 44.6 | 20.4 | 75.1 | 3.6 | 754.7 | 772.1 | 817.2 | 241.1 | 691.2 | 795.1 | 786.1
1099.2 | 573.2 | 463.4 | 185.36 | 216.6752 | 254.8 | 270.5 | 268.9 | 277.3 | 453.4 | 44.4 | 20.4 | 75 | 3.6 | 753.8 | 765.2 | 783.4 | 246.4 | 717 | 796.4 | 775.7
1100.2 | 574.2 | 463.4 | 185.36 | 216.6752 | 253.7 | 269.4 | 268.6 | 278 | 452.1 | 44.2 | 20.4 | 74.9 | 3.1 | 743.7 | 743.1 | 747.9 | 251.9 | 729.5 | 784.6 | 757.7
1101.2 | 575.2 | 463.2 | 185.28 | 216.5816 | 253 | 268.3 | 268.7 | 278.3 | 449.6 | 44.5 | 20.4 | 74.8 | 2.9 | 725.3 | 707.2 | 709 | 254.6 | 725.5 | 752.1 | 739.5
1102.2 | 576.2 | 464.3 | 185.72 | 217.096 | 252.9 | 268.6 | 270.4 | 278.4 | 440.6 | 44.7 | 20.4 | 74.7 | 2.8 | 713.4 | 693.4 | 688.8 | 256.1 | 733.5 | 745.7 | 734.5
1103.2 | 577.2 | 464 | 185.6 | 216.9557 | 254.3 | 269.2 | 271.5 | 278 | 431.8 | 44.5 | 20.4 | 74.8 | 3.7 | 705.5 | 678.4 | 685.1 | 251.6 | 747.3 | 751.4 | 737.1
1104.2 | 578.2 | 463.3 | 185.32 | 216.6284 | 256.6 | 270.1 | 271.9 | 277 | 429.4 | 44.5 | 20.4 | 75 | 3.5 | 707.4 | 681 | 698.8 | 249.9 | 743.3 | 768.3 | 756.4
1105.2 | 579.2 | 464 | 185.6 | 216.9557 | 257.6 | 271.7 | 271.5 | 276.1 | 426.9 | 44.6 | 20.4 | 75.3 | 3.1 | 711.4 | 695.2 | 723.8 | 247.5 | 734.7 | 771.6 | 762.4
1106.2 | 580.2 | 463.3 | 185.32 | 216.6284 | 257.2 | 272.7 | 271.3 | 276 | 427.2 | 44.6 | 20.4 | 75.4 | 2.6 | 718.2 | 710.7 | 731 | 244.7 | 734.6 | 780.4 | 764.6
1107.2 | 581.2 | 463.4 | 185.36 | 216.6752 | 255.8 | 272.8 | 270.6 | 276.4 | 437.3 | 44.5 | 20.4 | 75.4 | 3 | 727.8 | 726.2 | 736.9 | 243.5 | 731 | 774.9 | 773.1
1108.2 | 582.2 | 463.3 | 185.32 | 216.6284 | 255.6 | 272.4 | 270.7 | 276.6 | 446.7 | 44.5 | 20.4 | 75.5 | 3.7 | 732.2 | 734.1 | 743.5 | 242.1 | 740.4 | 773.5 | 772.3
1109.2 | 583.2 | 463.1 | 185.24 | 216.5349 | 255.1 | 271.6 | 270.7 | 276.9 | 445.8 | 44.5 | 20.4 | 75.5 | 3.8 | 730.2 | 732.2 | 742.6 | 240.3 | 742.7 | 769.3 | 760.3
1110.2 | 584.2 | 464.2 | 185.68 | 217.0492 | 254.2 | 271.7 | 270.6 | 277.3 | 450.1 | 44.5 | 20.4 | 75.6 | 4.1 | 734 | 743.2 | 754.4 | 239.3 | 740.8 | 783.7 | 766.6
1111.2 | 585.2 | 463.3 | 185.32 | 216.6284 | 253.8 | 272.1 | 270.4 | 277.6 | 450.3 | 44.4 | 20.4 | 75.6 | 3.6 | 734.8 | 739.4 | 761.4 | 239.7 | 748 | 787.2 | 771
1112.2 | 586.2 | 464.1 | 185.64 | 217.0025 | 253.5 | 272.9 | 270.2 | 277 | 446.6 | 44.4 | 20.4 | 75.6 | 3.6 | 731.4 | 730.5 | 758.6 | 240.5 | 757.9 | 778.8 | 763.2
1113.2 | 587.2 | 462.5 | 185 | 216.2543 | 253.5 | 274.1 | 270.4 | 277.2 | 444.3 | 44.4 | 20.4 | 75.5 | 3.1 | 738.6 | 747.6 | 761.2 | 239.4 | 769.1 | 770.8 | 762.1
1114.2 | 588.2 | 463.1 | 185.24 | 216.5349 | 252.9 | 275.2 | 270.8 | 277.2 | 446.7 | 44.3 | 20.4 | 75.4 | 2.8 | 746.7 | 766 | 761.6 | 238.1 | 759.3 | 765.7 | 757
1115.2 | 589.2 | 463.7 | 185.48 | 216.8154 | 253 | 275.9 | 270.8 | 277.2 | 447.3 | 44.3 | 20.3 | 75.3 | 3.3 | 757 | 790.1 | 779.1 | 236.6 | 764.2 | 765.1 | 760.3
1116.2 | 590.2 | 463.4 | 185.36 | 216.6752 | 253.6 | 276.3 | 270.4 | 276.9 | 452.8 | 44.4 | 20.3 | 75.2 | 3.3 | 765.2 | 803.6 | 784.6 | 236.3 | 774.4 | 767.2 | 764.4
1117.2 | 591.2 | 463.6 | 185.44 | 216.7687 | 254.8 | 276 | 270.5 | 277.4 | 462.1 | 44.4 | 20.3 | 75.3 | 3.4 | 772.1 | 809.1 | 782.4 | 233.9 | 778.8 | 784.6 | 762.1
1118.2 | 592.2 | 463.3 | 185.32 | 216.6284 | 254.8 | 276.3 | 270.7 | 278.5 | 467.8 | 44.4 | 20.3 | 75.2 | 3.4 | 772.6 | 796.4 | 774.8 | 230 | 774.8 | 803.5 | 769.5
1119.2 | 593.2 | 464.1 | 185.64 | 217.0025 | 254.6 | 276.5 | 270.9 | 278.2 | 474 | 44.4 | 20.3 | 75.1 | 3.4 | 772 | 785.1 | 779.1 | 226.9 | 768.9 | 812.7 | 777.1
1120.2 | 594.2 | 463.5 | 185.4 | 216.7219 | 254.8 | 277.4 | 271.4 | 277.9 | 468.9 | 44.3 | 20.3 | 75.1 | 3.3 | 776.1 | 785.7 | 784.4 | 225.2 | 764.9 | 818.7 | 783.6
1121.2 | 595.2 | 463.4 | 185.36 | 216.6752 | 255.3 | 278.4 | 272.2 | 278.5 | 475 | 44.1 | 20.3 | 75 | 3.9 | 783.6 | 799.3 | 805.5 | 227.8 | 778.2 | 829.2 | 792.2
1122.2 | 596.2 | 463.6 | 185.44 | 216.7687 | 254.9 | 278.7 | 272.7 | 279.4 | 494.1 | 44 | 20.3 | 74.9 | 3.8 | 787.9 | 803.6 | 813.3 | 231.6 | 776.6 | 824.7 | 793.9
1123.2 | 597.2 | 462.8 | 185.12 | 216.3946 | 255.2 | 278.1 | 272.8 | 279.9 | 497.1 | 44 | 20.3 | 75 | 4 | 793.4 | 815.2 | 819.6 | 230.5 | 773.2 | 809.7 | 786.3
1124.2 | 598.2 | 464.2 | 185.68 | 217.0492 | 255.9 | 278.3 | 273.9 | 280.3 | 505.3 | 44 | 20.3 | 74.9 | 3.5 | 794.4 | 817.3 | 819.5 | 233.3 | 774.7 | 815 | 782.9
1125.2 | 599.2 | 462.4 | 184.96 | 216.2076 | 256.8 | 279.1 | 275.5 | 280.1 | 503.4 | 44 | 20.3 | 74.8 | 3.7 | 791.2 | 807.4 | 806.7 | 235.6 | 771.8 | 831.8 | 791.3
1126.2 | 600.2 | 464.2 | 185.68 | 217.0492 | 256.5 | 279.5 | 276.4 | 280.7 | 492.4 | 44.1 | 20.3 | 74.6 | 3.5 | 777.4 | 774.3 | 782.1 | 242.9 | 755.7 | 833.7 | 791.5
1127.2 | 601.2 | 464.2 | 185.68 | 217.0492 | 257 | 280.1 | 276.9 | 281.4 | 482.3 | 44.4 | 20.3 | 74.4 | 2.9 | 765.2 | 747.2 | 763.5 | 247.6 | 752.8 | 820.1 | 785
1128.2 | 602.2 | 464.4 | 185.76 | 217.1427 | 258 | 280.5 | 277.6 | 281.4 | 473.4 | 44.8 | 20.3 | 74.4 | 3.6 | 747.6 | 713 | 727.8 | 250.8 | 758.5 | 798.5 | 766.8
1129.2 | 603.2 | 463.7 | 185.48 | 216.8154 | 258.6 | 280.5 | 278.5 | 280.9 | 470.6 | 45 | 20.3 | 74.3 | 3.8 | 740.4 | 703.5 | 702.4 | 253.1 | 770.9 | 797 | 767.1
1130.2 | 604.2 | 462.7 | 185.08 | 216.3479 | 259.3 | 279.5 | 279.2 | 280.7 | 470.3 | 45 | 20.3 | 74.2 | 3.4 | 737.2 | 702.5 | 694.4 | 251.9 | 782.1 | 796 | 763.6
1131.2 | 605.2 | 464.5 | 185.8 | 217.1895 | 259.4 | 279.4 | 278.8 | 280.5 | 462.7 | 45 | 20.3 | 74.1 | 4.2 | 740.1 | 713.3 | 699 | 248.8 | 789.4 | 811.5 | 769.2
1132.2 | 606.2 | 463.3 | 185.32 | 216.6284 | 259.4 | 279.3 | 277.7 | 280.5 | 460.2 | 45 | 20.3 | 74.2 | 3.9 | 741.7 | 715.9 | 702.5 | 250.2 | 801.6 | 817.3 | 773.1
1133.2 | 607.2 | 463 | 185.2 | 216.4881 | 259.8 | 278.9 | 277.7 | 280.8 | 462.5 | 45 | 20.3 | 74.2 | 3.4 | 741.3 | 716.7 | 702.6 | 250.3 | 803.6 | 825.8 | 777.7
1134.2 | 608.2 | 463.5 | 185.4 | 216.7219 | 260.3 | 277.7 | 277.3 | 282.3 | 453.9 | 45 | 20.3 | 74.3 | 3.6 | 735.1 | 710.2 | 701.5 | 248.1 | 803.1 | 832.8 | 784
1135.2 | 609.2 | 463.7 | 185.48 | 216.8154 | 260.2 | 276.6 | 278.2 | 282.9 | 453.8 | 44.9 | 20.3 | 74.4 | 3.5 | 742.6 | 727.1 | 722 | 247.3 | 797.6 | 833.4 | 783.8
1136.2 | 610.2 | 463.9 | 185.56 | 216.9089 | 260.2 | 276.9 | 278.4 | 283.1 | 452.8 | 44.9 | 20.3 | 74.5 | 3.5 | 746.1 | 736.9 | 746 | 245.7 | 782.5 | 813.4 | 790.7
1137.2 | 611.2 | 464 | 185.6 | 216.9557 | 260.6 | 277.3 | 278.3 | 283.3 | 448.9 | 44.9 | 20.3 | 74.5 | 3.3 | 747.9 | 743.9 | 759.7 | 244.9 | 790.2 | 814.8 | 789
1138.2 | 612.2 | 464.2 | 185.68 | 217.0492 | 260.4 | 277.9 | 278.2 | 283.3 | 457.7 | 45 | 20.3 | 74.7 | 3.4 | 755.1 | 757.8 | 763.2 | 245.5 | 783.3 | 812.7 | 786.4
1139.2 | 613.2 | 463.8 | 185.52 | 216.8622 | 260 | 278.6 | 278.1 | 283.3 | 470 | 45 | 20.3 | 74.9 | 3.7 | 765.1 | 781 | 782.3 | 242.9 | 764.5 | 789.4 | 789.2
1140.2 | 614.2 | 464.5 | 185.8 | 217.1895 | 259.8 | 279.5 | 278.1 | 283.1 | 484 | 45 | 20.3 | 74.9 | 3.7 | 769.6 | 795.8 | 761 | 241.1 | 737 | 750.2 | 769.9
1141.2 | 615.2 | 464 | 185.6 | 216.9557 | 259.1 | 279.9 | 278.6 | 283.2 | 478.7 | 44.6 | 20.3 | 75 | 3.5 | 762.6 | 779.1 | 727.7 | 240.1 | 741.2 | 725.6 | 751.9
1142.2 | 616.2 | 464.3 | 185.72 | 217.096 | 258.8 | 280.4 | 279.2 | 283.6 | 476.4 | 44.4 | 20.3 | 75.1 | 4.5 | 754.7 | 767.8 | 702 | 241.1 | 754 | 709.7 | 744.4
1143.2 | 617.2 | 463.4 | 185.36 | 216.6752 | 259.3 | 280.6 | 279.5 | 283.3 | 476.4 | 44.3 | 20.3 | 75.2 | 3.9 | 750.9 | 765 | 709.8 | 239.6 | 757.5 | 723.4 | 757.2
1144.2 | 618.2 | 464.4 | 185.76 | 217.1427 | 261.1 | 280.5 | 280.7 | 283.3 | 481.3 | 44.3 | 20.3 | 75.1 | 3.5 | 761.5 | 787.9 | 724.8 | 238.2 | 753.4 | 735.1 | 761.1
1145.2 | 619.2 | 464.5 | 185.8 | 217.1895 | 262.3 | 279.9 | 281.4 | 282.7 | 487.1 | 44.3 | 20.3 | 75 | 3.3 | 771.9 | 805 | 741.5 | 236.6 | 749.4 | 740.7 | 765.5
1146.2 | 620.2 | 464.5 | 185.8 | 217.1895 | 263.3 | 279.2 | 281.9 | 282.6 | 501.3 | 44.7 | 20.3 | 74.8 | 3.5 | 778.4 | 816.4 | 749.9 | 237.7 | 741.7 | 744.5 | 766.5
1147.2 | 621.2 | 464.2 | 185.68 | 217.0492 | 262.7 | 279.2 | 282.1 | 284.2 | 504.9 | 44.9 | 20.3 | 74.7 | 2.9 | 781.8 | 821.2 | 751.4 | 239.4 | 745.5 | 726 | 759.4
1148.2 | 622.2 | 464.1 | 185.64 | 217.0025 | 262.5 | 279.7 | 282.4 | 285.6 | 501.7 | 45 | 20.3 | 74.6 | 3 | 783.9 | 822.7 | 746.8 | 240.8 | 764.5 | 729.4 | 760.3
1149.2 | 623.2 | 464.4 | 185.76 | 217.1427 | 262.9 | 279.9 | 283 | 286.1 | 502.5 | 45.2 | 20.3 | 74.5 | 3.4 | 779.6 | 815.9 | 729.1 | 240.2 | 785.3 | 731 | 751.2
1150.2 | 624.2 | 464.2 | 185.68 | 217.0492 | 263.2 | 279.8 | 283.7 | 286.5 | 497.2 | 45.3 | 20.3 | 74.5 | 4 | 772.5 | 797.2 | 721.5 | 241.7 | 804.7 | 740.9 | 748.4
1151.2 | 625.2 | 463 | 185.2 | 216.4881 | 263.7 | 279.5 | 284.8 | 286.2 | 491.2 | 45.3 | 20.3 | 74.5 | 3.8 | 771.8 | 802.5 | 707.4 | 242.9 | 809.1 | 728.4 | 743
1152.2 | 626.2 | 464.2 | 185.68 | 217.0492 | 263.9 | 280.5 | 285.4 | 285.3 | 489.6 | 45.2 | 20.3 | 74.5 | 4.4 | 773.7 | 810.2 | 700.1 | 243.1 | 797.7 | 718.6 | 738
1153.2 | 627.2 | 464.3 | 185.72 | 217.096 | 264.5 | 281.6 | 285.6 | 284.5 | 496 | 45.2 | 20.3 | 74.6 | 4.2 | 778.2 | 820.9 | 725.2 | 240.5 | 790 | 726.6 | 749.6
1154.2 | 628.2 | 464 | 185.6 | 216.9557 | 265.2 | 282.5 | 285.5 | 284.1 | 513.5 | 45 | 20.3 | 74.9 | 3.8 | 783.6 | 827.3 | 755.3 | 240.9 | 771.3 | 721.9 | 761
1155.2 | 629.2 | 463.8 | 185.52 | 216.8622 | 266.7 | 282.9 | 284.9 | 284.1 | 515.1 | 44.9 | 20.3 | 74.9 | 4 | 789 | 837.3 | 776.8 | 244.1 | 754.7 | 720 | 763.5
1156.2 | 630.2 | 463.7 | 185.48 | 216.8154 | 267.6 | 283.3 | 284.4 | 284.3 | 512.5 | 44.7 | 20.3 | 74.9 | 3.1 | 793.8 | 844.3 | 784 | 243.4 | 761.2 | 712.5 | 759.8
1157.2 | 631.2 | 464.2 | 185.68 | 217.0492 | 267.3 | 282.9 | 284.9 | 284.3 | 518.7 | 44.6 | 20.3 | 74.9 | 3 | 799.1 | 851.2 | 787.1 | 242 | 766 | 704.5 | 753.4
1158.2 | 632.2 | 464.2 | 185.68 | 217.0492 | 267.6 | 282.8 | 285.3 | 284.3 | 510.9 | 44.7 | 20.3 | 74.7 | 3.3 | 798.3 | 846.1 | 763.3 | 239.6 | 780.8 | 715.9 | 748.4
1159.2 | 633.2 | 464.1 | 185.64 | 217.0025 | 268.1 | 283.3 | 285.7 | 284.5 | 512.8 | 44.7 | 20.3 | 74.6 | 3 | 801 | 849.8 | 766.9 | 235.8 | 789.4 | 726.5 | 753.8
1160.2 | 634.2 | 462.8 | 185.12 | 216.3946 | 268.1 | 283.6 | 285.9 | 284.1 | 518.8 | 44.9 | 20.3 | 74.5 | 3.4 | 803.2 | 846.2 | 789.1 | 233.5 | 788.6 | 731.5 | 767.5
1161.2 | 635.2 | 464.3 | 185.72 | 217.096 | 269.6 | 283.2 | 285.9 | 284.2 | 521.8 | 45 | 20.3 | 74.5 | 3 | 797.8 | 828.4 | 798.2 | 234 | 761.5 | 746.7 | 776.1
1162.2 | 636.2 | 463.7 | 185.48 | 216.8154 | 270.6 | 283.6 | 286.1 | 284.7 | 508.3 | 45.2 | 20.3 | 74.6 | 3.2 | 785 | 801.9 | 779.3 | 233.2 | 740 | 763.2 | 781
1163.2 | 637.2 | 464 | 185.6 | 216.9557 | 270.8 | 284.3 | 286.3 | 285.8 | 495.4 | 45.3 | 20.3 | 74.8 | 3.2 | 771.4 | 768.4 | 755.3 | 234.1 | 738.5 | 770.7 | 777.7
1164.2 | 638.2 | 463.8 | 185.52 | 216.8622 | 271 | 284.5 | 285.9 | 286.8 | 486.8 | 45.5 | 20.3 | 74.9 | 4 | 761.7 | 745.9 | 737.5 | 234.3 | 743.2 | 784.9 | 778.5
1165.2 | 639.2 | 463.7 | 185.48 | 216.8154 | 270.7 | 284.3 | 286.8 | 287.3 | 479.9 | 45.6 | 20.3 | 74.9 | 4.4 | 759 | 732.3 | 730.5 | 232.6 | 743.2 | 799.3 | 783.6
1166.2 | 640.2 | 464 | 185.6 | 216.9557 | 269.5 | 285 | 287.7 | 287.6 | 475.4 | 45.7 | 20.3 | 75 | 4.6 | 752.6 | 718.2 | 731 | 232.4 | 751.4 | 806.4 | 781
1167.2 | 641.2 | 464.6 | 185.84 | 217.2363 | 269 | 286.1 | 287.8 | 288 | 468.1 | 45.8 | 20.2 | 75.1 | 4 | 742.9 | 701.9 | 712.1 | 233.2 | 755.8 | 798.5 | 775.9
1168.2 | 642.2 | 463.9 | 185.56 | 216.9089 | 268.7 | 286.9 | 287.6 | 287.8 | 455.5 | 45.8 | 20.2 | 75.2 | 3.5 | 735.4 | 689.6 | 697.3 | 230.5 | 763.2 | 785 | 765.7
1169.2 | 643.2 | 464.2 | 185.68 | 217.0492 | 267.4 | 286.7 | 286.9 | 287.2 | 447.6 | 45.8 | 20.2 | 75.2 | 3.8 | 743 | 712.3 | 702.2 | 228.4 | 769.8 | 778.5 | 761.1
1170.2 | 644.2 | 463.8 | 185.52 | 216.8622 | 267.2 | 285.7 | 286.5 | 286.7 | 452.5 | 45.9 | 20.2 | 75.4 | 3.6 | 748.8 | 732.2 | 710.4 | 228.3 | 781.8 | 756.4 | 756.2
1171.2 | 645.2 | 463.8 | 185.52 | 216.8622 | 268 | 285.4 | 285.9 | 285.9 | 466.4 | 46.2 | 20.2 | 75.5 | 3.3 | 753.3 | 750.6 | 721.4 | 232 | 775 | 734.7 | 750.7
1172.2 | 646.2 | 462.9 | 185.16 | 216.4414 | 268.4 | 284.6 | 284.9 | 286.1 | 469 | 46.5 | 20.2 | 75.6 | 3.4 | 753.2 | 753.6 | 722.6 | 236.3 | 768.3 | 720.2 | 743.5
1173.2 | 647.2 | 462.3 | 184.92 | 216.1608 | 268.4 | 284.6 | 284.4 | 287.3 | 465.1 | 46.7 | 20.2 | 75.9 | 3.5 | 753.6 | 757.6 | 726.2 | 236 | 772.1 | 716.9 | 744.3
1174.2 | 648.2 | 463.5 | 185.4 | 216.7219 | 268 | 284.7 | 284.9 | 288.3 | 466.2 | 46.9 | 20.2 | 76 | 3.7 | 761 | 773.9 | 744.9 | 237.8 | 775 | 721.4 | 749.3
1175.2 | 649.2 | 464.4 | 185.76 | 217.1427 | 267.3 | 284.8 | 285.2 | 288.6 | 481.1 | 47 | 20.2 | 76 | 3.5 | 770.8 | 794.6 | 762.4 | 239.3 | 775.8 | 735.6 | 756
1176.2 | 650.2 | 464.2 | 185.68 | 217.0492 | 266.9 | 285.3 | 285 | 288.2 | 494.3 | 46.9 | 20.2 | 75.9 | 3.3 | 772.4 | 795.5 | 743.6 | 240.8 | 791.9 | 743.5 | 750.8
1177.2 | 651.2 | 464.5 | 185.8 | 217.1895 | 266.8 | 285.7 | 284.2 | 287.9 | 489.9 | 46.6 | 20.2 | 75.8 | 3.3 | 770.2 | 785.6 | 738.5 | 244.4 | 809.8 | 750.5 | 750.2
1178.2 | 652.2 | 463.4 | 185.36 | 216.6752 | 266.3 | 286 | 284.6 | 287.2 | 486.2 | 46.2 | 20.2 | 75.7 | 3.2 | 762.8 | 763.8 | 714.1 | 247 | 808.3 | 738.6 | 744
1179.2 | 653.2 | 464.4 | 185.76 | 217.1427 | 266.4 | 285.9 | 285 | 286.7 | 473.7 | 46 | 20.2 | 75.7 | 3.6 | 758.3 | 756.7 | 702.3 | 247.7 | 811.7 | 732.5 | 739.4
1180.2 | 654.2 | 463.2 | 185.28 | 216.5816 | 266.4 | 285.9 | 285.7 | 286 | 470.2 | 46 | 20.2 | 75.7 | 2.9 | 753.2 | 750.9 | 685.3 | 247.3 | 811.2 | 715.3 | 734
1181.2 | 655.2 | 464.1 | 185.64 | 217.0025 | 266.3 | 285.3 | 285.9 | 285.2 | 467.9 | 46.1 | 20.2 | 75.5 | 2.8 | 739.8 | 726.1 | 665.8 | 256.6 | 822.9 | 724.8 | 732.3
1182.2 | 656.2 | 463.3 | 185.32 | 216.6284 | 266.7 | 284.7 | 286.3 | 284.4 | 457.4 | 46.4 | 20.2 | 75.5 | 3 | 734.2 | 725 | 672.1 | 257.5 | 811.9 | 697.7 | 723.8
1183.2 | 657.2 | 463 | 185.2 | 216.4881 | 267.8 | 284 | 286.9 | 284.6 | 449.6 | 46.5 | 20.2 | 75.5 | 3.7 | 732.3 | 726.8 | 653.9 | 255.5 | 804.2 | 677.3 | 715.7
1184.2 | 658.2 | 463.7 | 185.48 | 216.8154 | 267.9 | 283 | 287.2 | 284.3 | 442.6 | 46.5 | 20.2 | 75.8 | 3.6 | 728.3 | 727.5 | 654.7 | 253.4 | 801.6 | 693.9 | 715.8
1185.2 | 659.2 | 462.7 | 185.08 | 216.3479 | 268.6 | 282.6 | 287 | 284.1 | 442.7 | 46.6 | 20.2 | 76 | 4 | 730.3 | 738.2 | 663.9 | 248.6 | 804.5 | 713.1 | 726.4
1186.2 | 660.2 | 463.8 | 185.52 | 216.8622 | 268.9 | 282.1 | 286.5 | 283.8 | 444.4 | 46.5 | 20.2 | 76.1 | 4 | 730.5 | 748.1 | 647.8 | 246.1 | 800.1 | 700 | 723.7
1187.2 | 661.2 | 464.5 | 185.8 | 217.1895 | 269 | 280.6 | 286.8 | 283.5 | 443.1 | 46.4 | 20.2 | 76.1 | 3 | 727.1 | 748.8 | 636 | 246.2 | 799 | 685.8 | 710.7
1188.2 | 662.2 | 463.4 | 185.36 | 216.6752 | 269.1 | 280.1 | 287 | 283.9 | 442.7 | 46.3 | 20.2 | 76.1 | 3 | 726.8 | 749.6 | 636.2 | 247.9 | 809.5 | 698.5 | 713.7
1189.2 | 663.2 | 464.1 | 185.64 | 217.0025 | 270.4 | 280 | 287.6 | 283.3 | 444.2 | 46.2 | 20.2 | 76.4 | 3.1 | 725.5 | 742.6 | 663.2 | 247.8 | 811.2 | 715.6 | 724
1190.2 | 664.2 | 464.6 | 185.84 | 217.2363 | 271 | 280.5 | 287 | 282.7 | 448.4 | 46.1 | 20.2 | 76.6 | 3.3 | 732.7 | 756.4 | 699.3 | 246.1 | 804.6 | 720.8 | 732.1
1191.2 | 665.2 | 464.1 | 185.64 | 217.0025 | 271.2 | 281.8 | 285.8 | 282.1 | 460.5 | 46.2 | 20.2 | 76.7 | 3.2 | 746.3 | 782 | 734.4 | 245.9 | 787.3 | 722.9 | 740.5
1192.2 | 666.2 | 463.7 | 185.48 | 216.8154 | 271.6 | 282.7 | 285.4 | 282.5 | 472 | 46.8 | 20.2 | 76.9 | 3.8 | 756.5 | 794.6 | 753.4 | 246 | 786.5 | 729.6 | 747.6
1193.2 | 667.2 | 464.7 | 185.88 | 217.283 | 271.4 | 283.2 | 285.4 | 283.2 | 478.2 | 47.1 | 20.2 | 77.1 | 3.8 | 762.2 | 804.6 | 744.4 | 248.4 | 781.1 | 728.9 | 745
1194.2 | 668.2 | 464.1 | 185.64 | 217.0025 | 271.1 | 282.9 | 286.5 | 283.6 | 482.6 | 47.2 | 20.2 | 77.2 | 3.9 | 762.8 | 807.5 | 729.4 | 250.4 | 766.4 | 729.8 | 737.3
1195.2 | 669.2 | 463.5 | 185.4 | 216.7219 | 271.2 | 282.7 | 286.8 | 284.2 | 479.4 | 47.2 | 20.2 | 77.2 | 3.7 | 764.4 | 805 | 726.2 | 249.3 | 767.4 | 755.8 | 740.1
1196.2 | 670.2 | 463.9 | 185.56 | 216.9089 | 271.1 | 283.3 | 287.2 | 285 | 481.4 | 47.1 | 20.2 | 77.2 | 3.6 | 752.9 | 772.9 | 703.7 | 245.4 | 746.6 | 759.2 | 744.2
1197.2 | 671.2 | 464.4 | 185.76 | 217.1427 | 270.8 | 284.7 | 288 | 285.5 | 471.3 | 47.2 | 20.2 | 77.1 | 3.5 | 732.9 | 732.9 | 685 | 243.2 | 712.9 | 748.9 | 746.5
1198.2 | 672.2 | 464.4 | 185.76 | 217.1427 | 270.8 | 286.3 | 288.8 | 286 | 459.6 | 47.2 | 20.2 | 77.3 | 4.3 | 722.2 | 711.7 | 696.2 | 239.6 | 688.5 | 745.5 | 750.5
1199.2 | 673.2 | 463.9 | 185.56 | 216.9089 | 269.9 | 287.7 | 289.2 | 286.8 | 455.4 | 47.2 | 20.2 | 77.5 | 4 | 719.1 | 706.6 | 724.6 | 240.1 | 681.5 | 753.3 | 759
1200.2 | 674.2 | 464.5 | 185.8 | 217.1895 | 269.4 | 288.2 | 289 | 287.6 | 449.6 | 47.1 | 20.2 | 77.5 | 4 | 725.7 | 712.4 | 744.6 | 242.6 | 699.2 | 752.6 | 757.5
1201.2 | 675.2 | 464.5 | 185.8 | 217.1895 | 269 | 287.9 | 288.8 | 289.1 | 453 | 47 | 20.2 | 77.5 | 3.8 | 732.4 | 720 | 721 | 244.1 | 728.7 | 760.7 | 750.9
1202.2 | 676.2 | 464.5 | 185.8 | 217.1895 | 268.8 | 287.8 | 289.2 | 289.8 | 463.2 | 46.9 | 20.2 | 77.4 | 4.5 | 737.6 | 728.1 | 731.2 | 245.9 | 745 | 769 | 748.9
1203.2 | 677.2 | 464.2 | 185.68 | 217.0492 | 268.2 | 287.5 | 289.7 | 289.7 | 470.2 | 46.7 | 20.2 | 77.1 | 3.6 | 746 | 747.5 | 740.7 | 244.3 | 751.4 | 767.7 | 751.9
1204.2 | 678.2 | 464.5 | 185.8 | 217.1895 | 268.2 | 287.3 | 289.8 | 289.1 | 479 | 46.4 | 20.2 | 77.1 | 3.9 | 755.2 | 762.7 | 742.5 | 245 | 763.7 | 769 | 755.7
1205.2 | 679.2 | 464 | 185.6 | 216.9557 | 267.8 | 287.5 | 288.9 | 289.1 | 482 | 46.4 | 20.2 | 77.2 | 3.9 | 760.9 | 767.8 | 750.5 | 244 | 777 | 782.3 | 754.5
1206.2 | 680.2 | 464.2 | 185.68 | 217.0492 | 267.2 | 287.2 | 288 | 289.4 | 478.4 | 46.6 | 20.2 | 77.4 | 3.6 | 762.6 | 765.8 | 757.2 | 244.2 | 787.3 | 799.3 | 763.8
1207.2 | 681.2 | 463.6 | 185.44 | 216.7687 | 266.7 | 286.5 | 287.3 | 289.7 | 479.3 | 46.9 | 20.2 | 77.6 | 3.7 | 766.6 | 773.5 | 769.8 | 243.9 | 787.6 | 796.6 | 771.8
1208.2 | 682.2 | 463.9 | 185.56 | 216.9089 | 266.8 | 286.4 | 285.8 | 290.2 | 472.4 | 47.1 | 20.2 | 77.5 | 4.3 | 768.5 | 781.4 | 761.8 | 241 | 778.8 | 775.3 | 755.9
1209.2 | 683.2 | 464 | 185.6 | 216.9557 | 266.8 | 286 | 284.2 | 290.2 | 467.7 | 47.1 | 20.2 | 77.3 | 3.8 | 767.5 | 781.6 | 746 | 239.5 | 766.7 | 771.6 | 744.7
1210.2 | 684.2 | 463.7 | 185.48 | 216.8154 | 265.9 | 285.6 | 283.8 | 289.2 | 460.6 | 47 | 20.2 | 77.3 | 3.5 | 761.5 | 771.8 | 737.5 | 242.7 | 766 | 765.5 | 745.5
1211.2 | 685.2 | 463.8 | 185.52 | 216.8622 | 267.3 | 284.5 | 283.5 | 288.8 | 459 | 47.1 | 20.2 | 77.5 | 3.7 | 764.6 | 779.3 | 750.5 | 241.5 | 771.2 | 756.5 | 747.9
1212.2 | 686.2 | 464.8 | 185.92 | 217.3298 | 268.3 | 283.7 | 283.1 | 288.1 | 455.9 | 47.1 | 20.2 | 77.6 | 4.1 | 760.4 | 765.2 | 733.3 | 239.8 | 770 | 759.1 | 744.9
1213.2 | 687.2 | 464.4 | 185.76 | 217.1427 | 267.8 | 284 | 283.2 | 288.5 | 450.1 | 47 | 20.2 | 77.6 | 3.7 | 750.1 | 745.9 | 708.7 | 239.6 | 769.6 | 770.9 | 744.4
1214.2 | 688.2 | 463.8 | 185.52 | 216.8622 | 266.8 | 284.6 | 282.7 | 288.1 | 443.5 | 46.9 | 20.2 | 77.6 | 3.6 | 742.2 | 733.1 | 703.1 | 242 | 778.7 | 779.3 | 747.9
1215.2 | 689.2 | 465.3 | 186.12 | 217.5636 | 266.4 | 285.7 | 282.2 | 287.4 | 436.2 | 46.8 | 20.2 | 77.6 | 3.4 | 727.2 | 702.6 | 676.6 | 240.6 | 778.5 | 781.4 | 748.3
1216.2 | 690.2 | 466.3 | 186.52 | 218.0311 | 266.1 | 287.1 | 281.7 | 287.1 | 429.2 | 46.7 | 20.2 | 77.6 | 3.5 | 712.7 | 675.5 | 666 | 239.3 | 764.6 | 785.1 | 753
1217.2 | 691.2 | 466.3 | 186.52 | 218.0311 | 265.2 | 287.5 | 281.7 | 287.2 | 422.9 | 46.7 | 20.2 | 77.7 | 3.2 | 693.9 | 643.6 | 644.2 | 238.7 | 749.5 | 772.3 | 748.3
1218.2 | 692.2 | 465.8 | 186.32 | 217.7973 | 264.5 | 287.1 | 282.2 | 287.4 | 415.2 | 46.5 | 20.2 | 77.9 | 3.1 | 675.7 | 618.4 | 629.8 | 239.7 | 730.7 | 748.8 | 742.7
1219.2 | 693.2 | 466.2 | 186.48 | 217.9844 | 264.8 | 286.9 | 282.2 | 286.7 | 409.2 | 46.4 | 20.2 | 78 | 2.9 | 663.6 | 602.6 | 630.9 | 239.2 | 706.3 | 741 | 746.8
1220.2 | 694.2 | 466.4 | 186.56 | 218.0779 | 264.1 | 286.3 | 281.2 | 286.2 | 400.3 | 46.5 | 20.2 | 78.1 | 3.3 | 658.7 | 594.1 | 654.6 | 240.1 | 688.1 | 752.3 | 755.4
1221.2 | 695.2 | 465.5 | 186.2 | 217.6571 | 263.2 | 287.3 | 279.9 | 285.6 | 399.2 | 46.5 | 20.2 | 78.2 | 3.9 | 663.8 | 607 | 675.4 | 243.7 | 686.1 | 771.8 | 768.9
1222.2 | 696.2 | 465.3 | 186.12 | 217.5636 | 262.9 | 287.6 | 279.2 | 285.6 | 400 | 46.5 | 20.2 | 78.3 | 3.7 | 657.7 | 600.3 | 679.7 | 242.3 | 665.6 | 753.6 | 765
1223.2 | 697.2 | 465.5 | 186.2 | 217.6571 | 262.9 | 288.3 | 278.9 | 285.7 | 394.1 | 46.7 | 20.2 | 78.3 | 3.5 | 647 | 589.2 | 667.1 | 241.1 | 645.4 | 728.6 | 758.9
1224.2 | 698.2 | 465.4 | 186.16 | 217.6103 | 262.9 | 288 | 278.5 | 285.4 | 389.2 | 46.9 | 20.2 | 78.3 | 3 | 647 | 591.5 | 682.7 | 238.4 | 632.9 | 730.1 | 756.6
1225.2 | 699.2 | 464.6 | 185.84 | 217.2363 | 262.6 | 287.8 | 278.3 | 285.3 | 389.9 | 47 | 20.2 | 78.3 | 3.4 | 651.7 | 600.9 | 678.8 | 236.8 | 656.1 | 766.3 | 768.9
1226.2 | 700.2 | 464.7 | 185.88 | 217.283 | 261.9 | 288 | 278 | 286.2 | 397.2 | 46.9 | 20.2 | 78.2 | 3.4 | 658.3 | 610 | 689.8 | 235.4 | 656.6 | 771.6 | 772.4
1227.2 | 701.2 | 465 | 186 | 217.4233 | 261 | 288.7 | 277.6 | 286.7 | 402.6 | 46.9 | 20.2 | 78.1 | 3.8 | 663.5 | 618 | 699.7 | 231.7 | 649 | 787.1 | 773.4
1228.2 | 702.2 | 465.9 | 186.36 | 217.8441 | 260.4 | 289 | 277.3 | 286.6 | 408.4 | 47.1 | 20.2 | 78.1 | 4.2 | 675.4 | 639.2 | 714.3 | 231.3 | 668.6 | 794 | 777.4
1229.2 | 703.2 | 465.3 | 186.12 | 217.5636 | 259.8 | 289.5 | 276.8 | 286.8 | 415.7 | 47.1 | 20.1 | 78.3 | 4.5 | 685.5 | 654.7 | 703.6 | 233 | 704.2 | 804.5 | 770.1
1230.2 | 704.2 | 465.1 | 186.04 | 217.47 | 259.1 | 290 | 276.1 | 287.5 | 423.1 | 46.8 | 20.2 | 78.4 | 3.8 | 679.5 | 641.9 | 676.5 | 235.7 | 732 | 796.2 | 754.9
1231.2 | 705.2 | 465.3 | 186.12 | 217.5636 | 258.4 | 289.7 | 276.1 | 287.5 | 430.1 | 46.7 | 20.2 | 78.2 | 3.3 | 683.7 | 659.4 | 686.8 | 236 | 743.1 | 807.3 | 759.9
1232.2 | 706.2 | 465.6 | 186.24 | 217.7038 | 258.8 | 288.8 | 276.2 | 286.9 | 441.6 | 46.7 | 20.2 | 78.2 | 3.2 | 696.3 | 689.6 | 706.2 | 235.5 | 724.9 | 798.3 | 763.8
1233.2 | 707.2 | 465.4 | 186.16 | 217.6103 | 258.8 | 288.7 | 275.6 | 287.2 | 444.6 | 46.8 | 20.1 | 78.3 | 3.5 | 712.2 | 721 | 743 | 232.8 | 700.1 | 773.4 | 766.8
1234.2 | 708.2 | 465.2 | 186.08 | 217.5168 | 259.2 | 289.7 | 274.7 | 287.7 | 452.9 | 46.9 | 20.1 | 78.4 | 4.2 | 722.6 | 746.8 | 771 | 233.4 | 687.5 | 780.5 | 774.2
1235.2 | 709.2 | 466.1 | 186.44 | 217.9376 | 259.4 | 291.5 | 275 | 289.3 | 455.4 | 46.9 | 20.1 | 78.6 | 4 | 719.8 | 736.5 | 757.9 | 236.2 | 678.9 | 788.2 | 778.3
1236.2 | 710.2 | 466.2 | 186.48 | 217.9844 | 259.9 | 293.4 | 276.5 | 291.8 | 446.4 | 46.9 | 20.1 | 78.6 | 4.2 | 714.3 | 723.7 | 758.2 | 235.4 | 663.5 | 787.6 | 782.8
1237.2 | 711.2 | 465.8 | 186.32 | 217.7973 | 260 | 294.7 | 278.6 | 292.4 | 439.9 | 46.8 | 20.1 | 78.7 | 3.7 | 719.4 | 729.7 | 762.6 | 235.7 | 669 | 790.6 | 786
1238.2 | 712.2 | 466.2 | 186.48 | 217.9844 | 260 | 294.7 | 279.7 | 293.4 | 444.5 | 46.7 | 20.1 | 78.7 | 3.6 | 729.6 | 748.7 | 778.8 | 234.8 | 677.8 | 784.2 | 785.2
1239.2 | 713.2 | 466.3 | 186.52 | 218.0311 | 260.5 | 294.4 | 280.5 | 293.9 | 448 | 46.7 | 20.1 | 78.6 | 3.6 | 731.4 | 743.5 | 768 | 235.1 | 702.1 | 798.5 | 788.4
1240.2 | 714.2 | 466.7 | 186.68 | 218.2182 | 259.9 | 294 | 280.9 | 294.2 | 446.2 | 46.7 | 20.1 | 78.6 | 3.9 | 720.5 | 714.7 | 761 | 235.3 | 698.6 | 802.7 | 786.7
1241.2 | 715.2 | 465.8 | 186.32 | 217.7973 | 259 | 293.8 | 280.9 | 294.4 | 436.1 | 46.7 | 20.1 | 78.5 | 4.5 | 715.5 | 699.7 | 752.6 | 232.1 | 688.4 | 805.6 | 782
1242.2 | 716.2 | 465.7 | 186.28 | 217.7506 | 259.9 | 292.9 | 281.4 | 294.8 | 426.5 | 46.7 | 20.1 | 78.5 | 4.5 | 720.2 | 708.9 | 750.7 | 230.7 | 693.6 | 805.8 | 778.8
1243.2 | 717.2 | 465.6 | 186.24 | 217.7038 | 259.9 | 292.4 | 281.7 | 294.9 | 426.1 | 46.8 | 20.1 | 78.5 | 4.3 | 721 | 703.5 | 733.7 | 229.2 | 711.7 | 792 | 770.2
1244.2 | 718.2 | 465.8 | 186.32 | 217.7973 | 259.8 | 292.4 | 281.9 | 294.1 | 424.7 | 46.8 | 20.1 | 78.5 | 3.9 | 715 | 694.1 | 723.8 | 228.4 | 714.8 | 783 | 762.9
1245.2 | 719.2 | 465.4 | 186.16 | 217.6103 | 260.6 | 291.9 | 281.9 | 293.2 | 425.5 | 46.8 | 20.1 | 78.4 | 3.7 | 717.4 | 709.4 | 724.9 | 227.7 | 715.4 | 776.2 | 760.4
1246.2 | 720.2 | 465.1 | 186.04 | 217.47 | 261.1 | 291.2 | 282.3 | 292.6 | 428.5 | 46.8 | 20.1 | 78.3 | 3.8 | 724.4 | 723.4 | 730.8 | 224.6 | 735.6 | 775.9 | 756.8
1247.2 | 721.2 | 464.9 | 185.96 | 217.3765 | 260.3 | 290.3 | 281.5 | 291.9 | 439.9 | 46.9 | 20.1 | 78.5 | 4 | 732.6 | 741.6 | 743.8 | 223.7 | 748.7 | 804.9 | 773.1
1248.2 | 722.2 | 464.7 | 185.88 | 217.283 | 261.5 | 289.4 | 280.8 | 292 | 452.7 | 47.1 | 20.1 | 78.7 | 4 | 730.6 | 726.5 | 725.1 | 226 | 772.9 | 818 | 772
1249.2 | 723.2 | 465.4 | 186.16 | 217.6103 | 262.2 | 288.9 | 280.5 | 291.9 | 456.5 | 47.1 | 20.1 | 78.9 | 3.9 | 722.8 | 713.4 | 731.2 | 228.5 | 781.7 | 816.1 | 774.8
1250.2 | 724.2 | 465.5 | 186.2 | 217.6571 | 262.6 | 288.1 | 280.6 | 291.5 | 461.4 | 47.1 | 20.1 | 79 | 3.2 | 727.8 | 729.2 | 731.3 | 229.3 | 788.5 | 812.5 | 767.4
1251.2 | 725.2 | 464 | 185.6 | 216.9557 | 262.3 | 287.7 | 280.3 | 291.1 | 464.5 | 47.1 | 20.1 | 79.2 | 3.5 | 735.3 | 744.8 | 734.7 | 232.7 | 792.4 | 813.9 | 767.6
1252.2 | 726.2 | 465.4 | 186.16 | 217.6103 | 262.8 | 288 | 280.4 | 290.6 | 465.9 | 46.9 | 20.1 | 79.3 | 3.4 | 741.4 | 749.2 | 738.6 | 233.3 | 799.2 | 817.4 | 771.1
1253.2 | 727.2 | 464.5 | 185.8 | 217.1895 | 263.6 | 288.9 | 280.5 | 290.2 | 466.2 | 46.8 | 20.1 | 79.3 | 3.6 | 749.6 | 764.3 | 751.9 | 233.8 | 807.4 | 822.8 | 769.6
1254.2 | 728.2 | 464.8 | 185.92 | 217.3298 | 264.8 | 290 | 281.1 | 289.7 | 472.7 | 47 | 20.1 | 79.1 | 3.9 | 753 | 766.4 | 748.5 | 236.5 | 817.4 | 817 | 764.3
1255.2 | 729.2 | 465 | 186 | 217.4233 | 264.8 | 290.2 | 282.1 | 288.9 | 467.7 | 46.8 | 20.1 | 78.8 | 3.4 | 755 | 775.7 | 748.4 | 238.4 | 808.5 | 810.4 | 762.4
1256.2 | 730.2 | 463.4 | 185.36 | 216.6752 | 266.1 | 290.6 | 283.4 | 288.7 | 462 | 46.7 | 20.1 | 78.7 | 4.2 | 751.4 | 764.8 | 763.1 | 242.2 | 808.9 | 820.1 | 770.7
1257.2 | 731.2 | 465.3 | 186.12 | 217.5636 | 267 | 290.1 | 284.1 | 288.4 | 466 | 46.7 | 20.1 | 78.7 | 4 | 748.6 | 757.6 | 755.1 | 245.1 | 810.6 | 826.4 | 777.9
1258.2 | 732.2 | 464.2 | 185.68 | 217.0492 | 268 | 289.5 | 283.8 | 287.8 | 468.6 | 46.7 | 20.1 | 78.5 | 4 | 744.2 | 740.1 | 732.6 | 243.6 | 820.8 | 823.2 | 775.7
1259.2 | 733.2 | 464.6 | 185.84 | 217.2363 | 268 | 288.9 | 283.3 | 287.4 | 473.9 | 46.6 | 20.1 | 78.5 | 4.4 | 738.5 | 729.7 | 743.8 | 244.4 | 814.5 | 811.3 | 768.8
1260.2 | 734.2 | 464.3 | 185.72 | 217.096 | 267.6 | 288.7 | 283.8 | 287.8 | 467.1 | 46.4 | 20.1 | 78.5 | 4.3 | 731.4 | 714.6 | 733.1 | 245.3 | 826.8 | 816 | 766.2
1261.2 | 735.2 | 464.3 | 185.72 | 217.096 | 267.5 | 288.6 | 284 | 288.2 | 463.4 | 46.4 | 20.1 | 78.3 | 3.5 | 728.5 | 709.8 | 731.9 | 247.2 | 814.4 | 822.5 | 769.4
1262.2 | 736.2 | 464.5 | 185.8 | 217.1895 | 267.1 | 288.5 | 283.7 | 288.6 | 455.2 | 46.4 | 20.1 | 78.3 | 3.9 | 727.4 | 708.8 | 749.2 | 250.1 | 803.5 | 821.9 | 780.3
1263.2 | 737.2 | 463.9 | 185.56 | 216.9089 | 266.7 | 288.5 | 283.5 | 288.6 | 449.2 | 46.3 | 20.1 | 78.5 | 3.6 | 725.8 | 707.7 | 734.5 | 248.9 | 806 | 814.2 | 772.3
1264.2 | 738.2 | 464.3 | 185.72 | 217.096 | 266.6 | 289.4 | 284.5 | 287.4 | 454.5 | 46.3 | 20.1 | 78.7 | 3.4 | 726.8 | 710.7 | 730.2 | 249.7 | 822.8 | 812.8 | 768.5
1265.2 | 739.2 | 464 | 185.6 | 216.9557 | 266.8 | 291.1 | 284.9 | 286.2 | 460.1 | 46.2 | 20.1 | 78.8 | 3.5 | 727.3 | 712.5 | 724.7 | 251.6 | 816.7 | 798.7 | 765.4
1266.2 | 740.2 | 463.6 | 185.44 | 216.7687 | 267.8 | 291.9 | 285.1 | 284.7 | 463.3 | 46.3 | 20.1 | 78.8 | 4 | 728.7 | 711.1 | 711.3 | 247.1 | 810.6 | 788.7 | 761.4
1267.2 | 741.2 | 464.1 | 185.64 | 217.0025 | 269.2 | 292.2 | 284.6 | 284.4 | 463.7 | 46.4 | 20.1 | 78.8 | 3.7 | 720.7 | 694.2 | 702.7 | 244.1 | 799.4 | 792.7 | 762
1268.2 | 742.2 | 463.9 | 185.56 | 216.9089 | 269.9 | 292.2 | 284.5 | 284 | 460.3 | 46.4 | 20.1 | 78.6 | 3.2 | 713.3 | 682.6 | 691.8 | 242.2 | 796.4 | 790.9 | 763.7
1269.2 | 743.2 | 465 | 186 | 217.4233 | 270.3 | 291.5 | 284.1 | 283.9 | 460.8 | 46.3 | 20.1 | 78.6 | 3.2 | 702.2 | 667 | 693.2 | 240.5 | 784.1 | 793.1 | 768.3
1270.2 | 744.2 | 464.9 | 185.96 | 217.3765 | 269.5 | 290.8 | 283.7 | 284.5 | 448.6 | 46.4 | 20.1 | 78.6 | 3 | 694.1 | 654.2 | 696.9 | 237.7 | 757.7 | 797.7 | 777.3
1271.2 | 745.2 | 465.2 | 186.08 | 217.5168 | 268.7 | 289.9 | 283.8 | 284.6 | 441.1 | 46.6 | 20.1 | 78.5 | 2.9 | 696.4 | 664 | 702.7 | 234.9 | 754.2 | 795.8 | 782.5
1272.2 | 746.2 | 465.1 | 186.04 | 217.47 | 268.5 | 288.4 | 282.9 | 284.1 | 443.8 | 46.7 | 20.1 | 78.5 | 3.3 | 711.1 | 703 | 728.4 | 233.6 | 753.6 | 789.7 | 782.1
1273.2 | 747.2 | 465 | 186 | 217.4233 | 268.5 | 287.8 | 282.2 | 283.4 | 447.1 | 46.5 | 20.1 | 78.6 | 3.8 | 722.8 | 729 | 749 | 235.2 | 744.8 | 792.7 | 783.3
1274.2 | 748.2 | 464.7 | 185.88 | 217.283 | 268.1 | 287.8 | 282 | 282.9 | 444.8 | 46.5 | 20.1 | 78.9 | 4.2 | 722.9 | 725.6 | 743.2 | 235.7 | 748.4 | 794.8 | 785.1
1275.2 | 749.2 | 465.7 | 186.28 | 217.7506 | 267.6 | 287.6 | 281.8 | 283.2 | 443.5 | 46.6 | 20.1 | 79.1 | 3.6 | 717 | 704.5 | 733.5 | 238.9 | 763.9 | 798.9 | 781.9
1276.2 | 750.2 | 465.3 | 186.12 | 217.5636 | 267.5 | 287.1 | 281.3 | 284.1 | 448.1 | 46.7 | 20.1 | 79.2 | 3.6 | 712.1 | 688.6 | 723.2 | 240.7 | 760.7 | 799 | 774.1
1277.2 | 751.2 | 465 | 186 | 217.4233 | 267.5 | 286.5 | 282 | 284.5 | 446.5 | 46.7 | 20.1 | 79.3 | 3.5 | 716.1 | 691.8 | 719.6 | 239.5 | 772.8 | 793.2 | 768.6
1278.2 | 752.2 | 464.4 | 185.76 | 217.1427 | 267.6 | 287.3 | 282.1 | 284.8 | 455.4 | 46.7 | 20.1 | 79.2 | 3.4 | 722 | 698.2 | 710 | 237.6 | 786.6 | 778.4 | 758.1
1279.2 | 753.2 | 463.6 | 185.44 | 216.7687 | 268 | 288.7 | 282.4 | 285.5 | 461.7 | 46.7 | 20.1 | 79.3 | 3.2 | 725.2 | 701.2 | 700.7 | 234.7 | 797.8 | 779.6 | 757.8
1280.2 | 754.2 | 465.3 | 186.12 | 217.5636 | 268.7 | 289.3 | 282.6 | 285.6 | 460.6 | 46.7 | 20.1 | 79.5 | 4.1 | 723.2 | 697.1 | 684.4 | 236.1 | 795.5 | 789.4 | 764.4
1281.2 | 755.2 | 465 | 186 | 217.4233 | 268.5 | 290 | 282.7 | 286 | 455.1 | 47 | 20.1 | 79.6 | 3.7 | 713.7 | 681.2 | 674.6 | 238 | 793.4 | 796.3 | 767.9
1282.2 | 756.2 | 463.5 | 185.4 | 216.7219 | 268.1 | 289.6 | 283.2 | 286.3 | 448.7 | 47.3 | 20.1 | 79.7 | 3 | 708.3 | 675.3 | 664.9 | 239.6 | 804.3 | 804.8 | 769.7
1283.2 | 757.2 | 463.6 | 185.44 | 216.7687 | 268.3 | 289.1 | 284.1 | 286.1 | 448.1 | 47.2 | 20.1 | 79.8 | 3.1 | 703.5 | 669.4 | 657.3 | 240.9 | 806.6 | 813.3 | 766.9
1284.2 | 758.2 | 463.1 | 185.24 | 216.5349 | 268.5 | 288.2 | 284.5 | 286.5 | 448.4 | 47.2 | 20.1 | 80 | 3.8 | 700.2 | 664.4 | 672.1 | 241.9 | 800.6 | 815 | 769.5
1285.2 | 759.2 | 462 | 184.8 | 216.0206 | 268.5 | 287.3 | 284.9 | 286.4 | 444.8 | 47.1 | 20.1 | 80 | 3.9 | 701 | 669.4 | 699.7 | 246 | 780.1 | 817.8 | 775.9
1286.2 | 760.2 | 461.5 | 184.6 | 215.7868 | 269.2 | 287.7 | 285.2 | 285.9 | 442 | 47.1 | 20.1 | 80 | 3.7 | 700.5 | 673.4 | 699.2 | 250.2 | 780.4 | 810.1 | 773.5
1287.2 | 761.2 | 462.8 | 185.12 | 216.3946 | 270.1 | 288.5 | 284.8 | 286.1 | 440.3 | 47.1 | 20.1 | 80.1 | 3.8 | 697.3 | 663.4 | 674.6 | 256.5 | 787.4 | 798.2 | 758.6
1288.2 | 762.2 | 463.6 | 185.44 | 216.7687 | 270.9 | 289.9 | 284.6 | 286.3 | 440.5 | 47.3 | 20.1 | 80.1 | 3.3 | 686.5 | 645.8 | 674.2 | 260.5 | 793.6 | 798.5 | 756.3
1289.2 | 763.2 | 464.3 | 185.72 | 217.096 | 270.3 | 290.8 | 284.8 | 286.5 | 440.5 | 47.6 | 20.1 | 80.1 | 3 | 690.9 | 661.8 | 682.5 | 262.4 | 798.7 | 804.9 | 763.5
1290.2 | 764.2 | 464.3 | 185.72 | 217.096 | 270.2 | 290.3 | 284.9 | 285.8 | 447.8 | 47.7 | 20.1 | 80.1 | 3.6 | 698.9 | 681.6 | 701.3 | 262.5 | 800.2 | 822.9 | 773.8
1291.2 | 765.2 | 463.5 | 185.4 | 216.7219 | 271.8 | 290.5 | 284.1 | 285.7 | 462.6 | 47.8 | 20.1 | 80.1 | 3.9 | 701.6 | 691.1 | 685 | 263.3 | 812.2 | 813.7 | 768.2
1292.2 | 766.2 | 463.2 | 185.28 | 216.5816 | 271.8 | 290.3 | 284.2 | 286.4 | 464.8 | 47.8 | 20.1 | 80 | 3.3 | 697.7 | 685.1 | 666.1 | 267.1 | 822 | 788 | 751.1
1293.2 | 767.2 | 463.2 | 185.28 | 216.5816 | 271 | 289.2 | 285.4 | 286.5 | 459 | 47.8 | 20.1 | 79.9 | 3 | 694.1 | 678.8 | 659.4 | 268.6 | 825.8 | 778.4 | 745.9
1294.2 | 768.2 | 464.5 | 185.8 | 217.1895 | 270.5 | 288.5 | 287 | 286 | 453.9 | 47.7 | 20.1 | 79.8 | 3.3 | 689.2 | 672.1 | 650.1 | 269.1 | 813.4 | 752 | 737.1
1295.2 | 769.2 | 464.4 | 185.76 | 217.1427 | 271.2 | 289.4 | 287.7 | 285.8 | 443.5 | 47.7 | 20.1 | 79.8 | 3.6 | 681.9 | 655.9 | 620.4 | 271.2 | 802.9 | 728.9 | 728.3
1296.2 | 770.2 | 464.7 | 185.88 | 217.283 | 271.3 | 290.4 | 289.1 | 285 | 435 | 47.5 | 20.1 | 79.7 | 4.1 | 673.4 | 641.3 | 592.3 | 267.4 | 795.7 | 695.7 | 719.5
1297.2 | 771.2 | 463.7 | 185.48 | 216.8154 | 271.4 | 291.5 | 290.1 | 284.6 | 432.6 | 47.5 | 20.1 | 79.7 | 4.1 | 662.9 | 625.7 | 572.3 | 264.7 | 800.5 | 679.8 | 717.8
1298.2 | 772.2 | 464.1 | 185.64 | 217.0025 | 271.8 | 292.5 | 290.4 | 284 | 430.9 | 47.8 | 20.1 | 79.7 | 4 | 651.1 | 607.2 | 566.6 | 267.2 | 810.7 | 694.4 | 724.6
1299.2 | 773.2 | 463.3 | 185.32 | 216.6284 | 272.4 | 293.2 | 290.7 | 284 | 427.7 | 48 | 20 | 79.7 | 3.4 | 651.9 | 616.7 | 568.7 | 262.3 | 803.3 | 709.5 | 729.7
1300.2 | 774.2 | 464.3 | 185.72 | 217.096 | 271.9 | 292.4 | 290.5 | 284.2 | 428.4 | 48 | 20 | 79.8 | 3.8 | 646.4 | 611 | 552.4 | 261.3 | 793.8 | 685.7 | 718.7
1301.2 | 775.2 | 464.3 | 185.72 | 217.096 | 271.4 | 290.8 | 289.3 | 284.8 | 425 | 47.8 | 20 | 79.8 | 4 | 637.8 | 602 | 546.5 | 260.4 | 787.9 | 668.5 | 708.3
1302.2 | 776.2 | 464.5 | 185.8 | 217.1895 | 271.2 | 288.9 | 289 | 285.4 | 424.6 | 47.7 | 20 | 79.8 | 4.2 | 633.7 | 593.9 | 559 | 262 | 794.7 | 693.2 | 713.9
1303.2 | 777.2 | 464.3 | 185.72 | 217.096 | 270.2 | 287.3 | 288.8 | 284.9 | 425.2 | 47.7 | 20 | 79.8 | 3.7 | 626.4 | 580.7 | 546.2 | 262.2 | 794.5 | 695.8 | 716.4
1304.2 | 778.2 | 465.1 | 186.04 | 217.47 | 269.3 | 286.4 | 288.1 | 284.7 | 421.7 | 47.7 | 20 | 79.9 | 3.5 | 616.5 | 566.8 | 537.2 | 258.8 | 793 | 706 | 717.2
1305.2 | 779.2 | 464.3 | 185.72 | 217.096 | 268.4 | 287 | 287.4 | 284.6 | 422.1 | 47.6 | 20 | 80.1 | 4 | 609.6 | 557.2 | 529 | 255.9 | 792 | 719.8 | 722.6
1306.2 | 780.2 | 463.8 | 185.52 | 216.8622 | 267.9 | 287.5 | 287 | 284.3 | 424.9 | 47.6 | 20 | 80.6 | 4.6 | 619.4 | 573.4 | 559.2 | 253.6 | 801.3 | 733.7 | 723.2
1307.2 | 781.2 | 463.2 | 185.28 | 216.5816 | 267.9 | 287.8 | 287.2 | 284.2 | 436.1 | 47.6 | 20 | 80.9 | 3.9 | 626.1 | 587.5 | 578.7 | 252.2 | 801.3 | 738 | 726.7
1308.2 | 782.2 | 460.9 | 184.36 | 215.5062 | 267.1 | 288.2 | 286.7 | 284.7 | 434.5 | 47.8 | 20 | 81 | 4.1 | 629.5 | 597.6 | 586.9 | 251.7 | 794.6 | 745.1 | 725.6
1309.2 | 783.2 | 461.9 | 184.76 | 215.9738 | 266.7 | 287.4 | 286.3 | 284.8 | 434.7 | 47.9 | 20 | 80.8 | 3.9 | 633.7 | 609.9 | 599.4 | 252.5 | 790.6 | 758.9 | 733.3
1310.2 | 784.2 | 463.1 | 185.24 | 216.5349 | 266.1 | 286.7 | 285.3 | 284.8 | 435.4 | 48.2 | 20 | 80.8 | 3.4 | 633.5 | 610.6 | 600.3 | 254.7 | 793.3 | 762 | 732.3
1311.2 | 785.2 | 463.2 | 185.28 | 216.5816 | 265.5 | 286.6 | 285 | 284.1 | 431.8 | 48.4 | 20 | 80.9 | 4.2 | 635.8 | 615.5 | 619.3 | 253.5 | 789.1 | 774.4 | 735.8
1312.2 | 786.2 | 463.2 | 185.28 | 216.5816 | 264.8 | 286.9 | 284.4 | 283.7 | 433.7 | 48.4 | 20 | 81.1 | 4.5 | 646.3 | 631.8 | 628.9 | 250 | 793.1 | 777.6 | 737.9
1313.2 | 787.2 | 464.2 | 185.68 | 217.0492 | 264.4 | 286.6 | 284.3 | 283.1 | 434.6 | 48.2 | 20 | 81.1 | 3.9 | 649.7 | 638.5 | 642.6 | 251.1 | 792.3 | 790.5 | 739.3
1314.2 | 788.2 | 463.9 | 185.56 | 216.9089 | 264.3 | 286.5 | 284.1 | 282.9 | 435.7 | 48.1 | 20 | 81.1 | 4.2 | 654.6 | 643.1 | 636.4 | 252.6 | 803.1 | 787.4 | 733
1315.2 | 789.2 | 464.2 | 185.68 | 217.0492 | 265.1 | 286.2 | 283.5 | 282.3 | 444.3 | 47.9 | 20 | 80.9 | 4.3 | 656.7 | 650.2 | 628.4 | 254.7 | 805.9 | 777.7 | 724.3
1316.2 | 790.2 | 463.9 | 185.56 | 216.9089 | 266.5 | 287.5 | 284 | 281.6 | 446.6 | 47.8 | 20 | 81 | 4.4 | 656.2 | 652.7 | 611.1 | 251.8 | 782 | 739.1 | 712.4
1317.2 | 791.2 | 463.9 | 185.56 | 216.9089 | 267.9 | 288.4 | 284.7 | 282.1 | 443.6 | 48 | 20 | 81.2 | 4.4 | 663.5 | 675 | 614.3 | 252.7 | 774.6 | 716.4 | 703.1
1318.2 | 792.2 | 463.8 | 185.52 | 216.8622 | 268.7 | 288.6 | 284.9 | 282 | 442.8 | 48.3 | 20 | 81.2 | 4.2 | 674.7 | 700.8 | 637.7 | 253.2 | 778 | 728.1 | 718.3
1319.2 | 793.2 | 463.8 | 185.52 | 216.8622 | 269.5 | 288.9 | 284.6 | 282.1 | 444.9 | 48.4 | 20 | 81.1 | 5 | 682.5 | 713 | 654.1 | 255.6 | 786.9 | 729.9 | 732.2
1320.2 | 794.2 | 464.7 | 185.88 | 217.283 | 270.1 | 289.1 | 285.3 | 282.7 | 452.7 | 48.5 | 20 | 81.3 | 4.8 | 683.4 | 712.5 | 652.7 | 256.8 | 800.9 | 733.9 | 726
1321.2 | 795.2 | 464 | 185.6 | 216.9557 | 270.5 | 288.7 | 286.6 | 283.1 | 454 | 48.4 | 20 | 81.4 | 4.3 | 685.4 | 711.3 | 656.2 | 256.4 | 804.8 | 747 | 727.3
1322.2 | 796.2 | 464.6 | 185.84 | 217.2363 | 271 | 288.7 | 287.3 | 283.2 | 458.4 | 48.5 | 20 | 81.4 | 3.6 | 698.1 | 735.4 | 693.9 | 251.5 | 799.3 | 746.9 | 732.5
1323.2 | 797.2 | 464.3 | 185.72 | 217.096 | 271.5 | 289.2 | 288.3 | 283.2 | 469.4 | 48.4 | 20 | 81.3 | 3.4 | 707.5 | 745.7 | 691.4 | 251 | 812.4 | 743.9 | 730.9
1324.2 | 798.2 | 464.9 | 185.96 | 217.3765 | 271.9 | 289.5 | 288.8 | 283.7 | 469.7 | 48.2 | 20 | 81.2 | 3.9 | 706 | 735.3 | 674.7 | 257.4 | 819.3 | 743.8 | 724.9
1325.2 | 799.2 | 464.3 | 185.72 | 217.096 | 272 | 289.7 | 289.7 | 284.5 | 464.2 | 48 | 20 | 81.1 | 3.9 | 701.9 | 720.6 | 677.6 | 258.3 | 809.6 | 754.5 | 734.2
1326.2 | 800.2 | 464 | 185.6 | 216.9557 | 272.1 | 289.5 | 290.8 | 284.9 | 463 | 47.9 | 20 | 81.1 | 4.1 | 698 | 705.7 | 681.2 | 258.3 | 815.8 | 771.3 | 744.7
1327.2 | 801.2 | 465.2 | 186.08 | 217.5168 | 272.7 | 289.9 | 290.9 | 284.9 | 465.8 | 47.8 | 20 | 81.2 | 4.4 | 702.7 | 710.1 | 689.2 | 260.5 | 818.4 | 781.7 | 744
1328.2 | 802.2 | 464.9 | 185.96 | 217.3765 | 273.1 | 289.3 | 290.7 | 285.5 | 471.3 | 48.2 | 20 | 81.2 | 4.5 | 713.1 | 733.5 | 723.4 | 262.2 | 810.8 | 795.5 | 750.4
1329.2 | 803.2 | 464 | 185.6 | 216.9557 | 273.4 | 288.7 | 290.5 | 285.8 | 470.2 | 48.5 | 20 | 81.4 | 4.9 | 718.2 | 739.4 | 751.6 | 263.5 | 793.3 | 807.4 | 757.3
1330.2 | 804.2 | 464.7 | 185.88 | 217.283 | 273.2 | 289.6 | 290.8 | 285.8 | 463.5 | 48.7 | 20 | 81.4 | 5.7 | 719.5 | 737.8 | 763.4 | 261.1 | 783.9 | 809 | 765.5
1331.2 | 805.2 | 465 | 186 | 217.4233 | 273.4 | 290.3 | 290.2 | 286.3 | 464 | 48.8 | 20 | 81.4 | 5.7 | 724.4 | 745.7 | 776.5 | 258.3 | 771.6 | 801.6 | 767.2
1332.2 | 806.2 | 464.8 | 185.92 | 217.3298 | 273.6 | 290.6 | 288.9 | 286.7 | 469.7 | 48.9 | 20 | 81.3 | 5 | 721.7 | 731 | 787.6 | 255.5 | 741 | 792.2 | 770.6
1333.2 | 807.2 | 463.9 | 185.56 | 216.9089 | 273 | 290.9 | 287.9 | 287.7 | 464.8 | 48.8 | 20 | 81.3 | 4 | 703.7 | 698.7 | 764.5 | 261 | 718.5 | 770.8 | 767
1334.2 | 808.2 | 464 | 185.6 | 216.9557 | 272.6 | 291.6 | 287.3 | 288.1 | 452.1 | 48.5 | 20 | 81.1 | 4 | 690.9 | 682.2 | 761.2 | 268.6 | 708.3 | 758.3 | 761.4
1335.2 | 809.2 | 463.9 | 185.56 | 216.9089 | 272.5 | 292.7 | 287.2 | 287.7 | 444.9 | 48.4 | 20 | 81 | 5 | 695.1 | 686.9 | 760.1 | 270.7 | 728.6 | 777.4 | 763
1336.2 | 810.2 | 463.6 | 185.44 | 216.7687 | 273.4 | 293.3 | 286.8 | 287.3 | 449.3 | 48.4 | 20 | 81.1 | 4.5 | 704.1 | 707.8 | 767.4 | 272.4 | 744.4 | 759.6 | 758.2
1337.2 | 811.2 | 464.3 | 185.72 | 217.096 | 273.2 | 293.3 | 286.7 | 286.7 | 459.7 | 48.3 | 20 | 81.2 | 4.4 | 715.5 | 735.8 | 758.6 | 272.7 | 751.8 | 756 | 751.3
1338.2 | 812.2 | 465 | 186 | 217.4233 | 274.1 | 292.3 | 285.1 | 286.2 | 463.2 | 48.2 | 20 | 81.3 | 4.1 | 724.2 | 754.5 | 750.6 | 272.2 | 749.3 | 736.3 | 743.1
1339.2 | 813.2 | 464.3 | 185.72 | 217.096 | 274.6 | 291.7 | 284 | 286.1 | 469.4 | 48.2 | 20 | 81.3 | 4.2 | 727.5 | 765.5 | 721.8 | 271.1 | 755.9 | 724 | 730.9
1340.2 | 814.2 | 465.5 | 186.2 | 217.6571 | 274.5 | 290.9 | 284.9 | 286.5 | 490.1 | 48.2 | 20 | 81.4 | 4.3 | 722.6 | 757 | 683.9 | 271 | 774.9 | 695.7 | 717.6
1341.2 | 815.2 | 465.6 | 186.24 | 217.7038 | 274.9 | 289.7 | 285.9 | 287.3 | 496.9 | 48.3 | 20 | 81.3 | 4.4 | 710 | 733.6 | 651.2 | 269 | 784.5 | 660.9 | 704.5
1342.2 | 816.2 | 465.1 | 186.04 | 217.47 | 275.8 | 289.2 | 286.9 | 288 | 487.2 | 48.3 | 20 | 81.1 | 4.6 | 701.9 | 722.6 | 640.2 | 266.4 | 793.8 | 662.6 | 700.1
1343.2 | 817.2 | 464.6 | 185.84 | 217.2363 | 276.4 | 288.5 | 288.3 | 288.4 | 483.8 | 48.3 | 20 | 80.9 | 5 | 700.4 | 725.9 | 652.2 | 265.2 | 794.8 | 672.6 | 707.5
1344.2 | 818.2 | 464.6 | 185.84 | 217.2363 | 277.3 | 288.1 | 289.2 | 289.1 | 487.2 | 48.4 | 20 | 80.7 | 5.4 | 704.7 | 742.4 | 652.7 | 262.9 | 797.1 | 677.8 | 707.5
1345.2 | 819.2 | 464.5 | 185.8 | 217.1895 | 278 | 288.3 | 291.1 | 289.5 | 498 | 48.6 | 20 | 80.6 | 5.8 | 715.1 | 765.5 | 676.8 | 265.6 | 792.8 | 684.5 | 711.5
1346.2 | 820.2 | 464.2 | 185.68 | 217.0492 | 278.7 | 288.5 | 292.6 | 290.2 | 497.2 | 48.6 | 20 | 80.5 | 5.5 | 719.9 | 765.1 | 692.8 | 264.7 | 806.5 | 714.1 | 722.6
1347.2 | 821.2 | 464.9 | 185.96 | 217.3765 | 279.6 | 288.6 | 293.1 | 290.3 | 492.5 | 48.4 | 20 | 80.3 | 5.2 | 708.7 | 732.7 | 669.9 | 263.8 | 807.2 | 715.3 | 719.2
1348.2 | 822.2 | 465.6 | 186.24 | 217.7038 | 280.2 | 289.4 | 293.1 | 290.7 | 477.9 | 48.4 | 20 | 80.2 | 4.5 | 695.6 | 706.2 | 648.2 | 260.6 | 813.1 | 711.5 | 709.2
1349.2 | 823.2 | 465 | 186 | 217.4233 | 280.2 | 289.7 | 293.1 | 290.7 | 469.4 | 48.4 | 20 | 80.1 | 4.1 | 694.6 | 706.7 | 646.5 | 258.1 | 806.1 | 696.7 | 707.9
1350.2 | 824.2 | 464.3 | 185.72 | 217.096 | 280 | 290.1 | 293.1 | 290.4 | 465.3 | 48.3 | 20 | 79.9 | 3.9 | 689.9 | 703.2 | 619.6 | 256 | 802 | 672.4 | 697.9
1351.2 | 825.2 | 464.4 | 185.76 | 217.1427 | 280.5 | 290.5 | 293.4 | 290.4 | 464.1 | 48.2 | 20 | 79.8 | 3.4 | 694.3 | 721.8 | 623.8 | 256.1 | 792.9 | 659.1 | 691.3
1352.2 | 826.2 | 464.8 | 185.92 | 217.3298 | 280.4 | 290.3 | 293.5 | 290.5 | 469.6 | 48.2 | 20 | 79.7 | 3 | 700.1 | 724.7 | 659.3 | 257.8 | 788.9 | 695.4 | 707.5
1353.2 | 827.2 | 464 | 185.6 | 216.9557 | 280.3 | 291.3 | 293.3 | 290.7 | 462.6 | 48.2 | 20 | 79.8 | 3.1 | 702.2 | 717.1 | 694.9 | 258.9 | 767.1 | 714.1 | 728.5
1354.2 | 828.2 | 465.4 | 186.16 | 217.6103 | 280.5 | 291.9 | 293 | 291.1 | 452.8 | 48.2 | 20 | 79.9 | 3.9 | 709 | 727.8 | 721.9 | 259.5 | 767.4 | 730.7 | 731.8
1355.2 | 829.2 | 464 | 185.6 | 216.9557 | 280.6 | 291.9 | 293 | 291.4 | 453.6 | 48.2 | 20 | 79.9 | 4 | 717.4 | 741 | 720.1 | 263.9 | 778.1 | 725.9 | 723.6
1356.2 | 830.2 | 464.9 | 185.96 | 217.3765 | 280.6 | 292.4 | 293.1 | 291.5 | 454.2 | 48 | 20 | 80.1 | 4.6 | 715.6 | 726.2 | 707.6 | 264.3 | 788 | 724.8 | 713.2
1357.2 | 831.2 | 464.7 | 185.88 | 217.283 | 280.1 | 292.8 | 293.9 | 291.6 | 451.7 | 47.9 | 20 | 80.2 | 4.3 | 706.1 | 706.3 | 691.4 | 267.5 | 790.4 | 706.8 | 705.6
1358.2 | 832.2 | 464.7 | 185.88 | 217.283 | 279.6 | 292.8 | 293.8 | 291.3 | 449.1 | 47.7 | 20 | 80.5 | 4.8 | 699.2 | 701.4 | 667.1 | 269 | 793.6 | 688.7 | 692.8
1359.2 | 833.2 | 464.1 | 185.64 | 217.0025 | 279.7 | 292.3 | 294 | 290.2 | 452.8 | 47.6 | 20 | 80.6 | 4.7 | 695.1 | 699.4 | 659.7 | 267.8 | 812.6 | 706.2 | 693.5
1360.2 | 834.2 | 463.9 | 185.56 | 216.9089 | 279.9 | 291.5 | 294.8 | 289.1 | 457 | 47.5 | 20 | 80.6 | 4.4 | 697.2 | 705.2 | 676.4 | 267.2 | 824.2 | 736.3 | 709.2
1361.2 | 835.2 | 464.1 | 185.64 | 217.0025 | 279.6 | 290.8 | 294.1 | 288.7 | 460.2 | 47.6 | 20 | 80.7 | 4.3 | 707.3 | 718.8 | 698.8 | 267.9 | 826.3 | 750.4 | 725.1
1362.2 | 836.2 | 464.6 | 185.84 | 217.2363 | 279.3 | 290.1 | 293.7 | 288.7 | 468.4 | 47.9 | 20 | 80.8 | 4.4 | 720.6 | 746.7 | 718.3 | 265.7 | 816.2 | 761 | 729.8
1363.2 | 837.2 | 465.5 | 186.2 | 217.6571 | 279.5 | 289.9 | 293.3 | 289.3 | 475.7 | 48.1 | 20 | 80.8 | 4.4 | 730.9 | 760.4 | 725.7 | 265.4 | 810.4 | 776.8 | 734.6
1364.2 | 838.2 | 464.5 | 185.8 | 217.1895 | 279.9 | 289.9 | 293.1 | 290.3 | 473.5 | 48.3 | 20 | 80.8 | 5.3 | 735 | 757.1 | 738.5 | 266.4 | 798.8 | 792.8 | 746.2
1365.2 | 839.2 | 464.7 | 185.88 | 217.283 | 280.2 | 290.3 | 293 | 291 | 469.8 | 48.3 | 20 | 80.9 | 5.3 | 727 | 738.1 | 729.9 | 269.5 | 773.9 | 784.5 | 752.1
1366.2 | 840.2 | 464.4 | 185.76 | 217.1427 | 279.7 | 289.6 | 292.8 | 291.5 | 459.1 | 48.3 | 20 | 80.9 | 4.8 | 717 | 718.9 | 719.2 | 269 | 756.5 | 787.5 | 753.8
1367.2 | 841.2 | 465.8 | 186.32 | 217.7973 | 279.2 | 290.1 | 292.6 | 292.1 | 454.4 | 48.3 | 20 | 80.8 | 4.6 | 716.8 | 709.2 | 730.5 | 268.7 | 749 | 783.4 | 749.1
1368.2 | 842.2 | 464.9 | 185.96 | 217.3765 | 278.1 | 291.4 | 293 | 291.6 | 451.2 | 48.6 | 20 | 80.6 | 3.9 | 703.2 | 687.7 | 724.9 | 270.6 | 728.1 | 764.7 | 741.6
1369.2 | 843.2 | 465.1 | 186.04 | 217.47 | 277.7 | 291.6 | 293 | 291.8 | 442.7 | 48.7 | 20 | 80.7 | 4.7 | 703.5 | 686.4 | 734.4 | 272.3 | 731.1 | 764.3 | 738.2
1370.2 | 844.2 | 465.1 | 186.04 | 217.47 | 277.4 | 291.6 | 292.2 | 291.5 | 439.6 | 48.7 | 20 | 80.8 | 5.4 | 711.7 | 704.5 | 750.9 | 272.2 | 751.7 | 776.1 | 740.4
1371.2 | 845.2 | 465.5 | 186.2 | 217.6571 | 276.3 | 291.6 | 291.1 | 290.9 | 444.8 | 48.7 | 20 | 80.9 | 5.3 | 724.7 | 734.6 | 746 | 270.5 | 759 | 782.2 | 746.9
1372.2 | 846.2 | 465.4 | 186.16 | 217.6103 | 276.3 | 291.3 | 290.9 | 289.8 | 456.3 | 48.6 | 20 | 80.9 | 4.1 | 735.8 | 759.2 | 736.2 | 268.4 | 771.4 | 779.6 | 734.7
1373.2 | 847.2 | 465.6 | 186.24 | 217.7038 | 276.8 | 290.6 | 290.8 | 289.7 | 465.5 | 48.6 | 19.9 | 80.9 | 3.8 | 743.9 | 774.6 | 741.4 | 268.6 | 769.2 | 767.7 | 735.3
1374.2 | 848.2 | 465.4 | 186.16 | 217.6103 | 277.2 | 289.6 | 290.5 | 289.9 | 475.9 | 48.4 | 19.9 | 81 | 4.2 | 752.5 | 797 | 754.5 | 270.1 | 777.1 | 762.3 | 731.7
1375.2 | 849.2 | 464.2 | 185.68 | 217.0492 | 277.8 | 289.2 | 289.8 | 289.5 | 485.2 | 48.2 | 19.9 | 81.2 | 5 | 759.9 | 806.5 | 753.3 | 274.1 | 765.7 | 761.5 | 733.5
1376.2 | 850.2 | 464.7 | 185.88 | 217.283 | 278.3 | 289.7 | 289 | 289.6 | 487.3 | 48.2 | 19.9 | 81.3 | 5.2 | 764.9 | 818.6 | 745.3 | 274.3 | 757.8 | 747.9 | 724.5
1377.2 | 851.2 | 464.9 | 185.96 | 217.3765 | 278.6 | 289.9 | 289 | 290.2 | 485.7 | 48.4 | 19.9 | 81.5 | 5.9 | 766.1 | 820.2 | 735.9 | 272.7 | 768.8 | 750.3 | 718.4
1378.2 | 852.2 | 464.6 | 185.84 | 217.2363 | 278.4 | 289.9 | 289.7 | 290.7 | 485.5 | 48.6 | 19.9 | 81.5 | 5.4 | 766.7 | 821.1 | 725.8 | 273.3 | 772.8 | 734.6 | 715.9
1379.2 | 853.2 | 465.1 | 186.04 | 217.47 | 278.5 | 289.5 | 290.3 | 291.1 | 490.9 | 48.8 | 19.9 | 81.6 | 5.1 | 761.7 | 806.9 | 705.9 | 274.7 | 780.9 | 713.3 | 710.5
1380.2 | 854.2 | 464.3 | 185.72 | 217.096 | 279.2 | 290.2 | 291.2 | 291.6 | 487.3 | 48.9 | 19.9 | 81.7 | 5.3 | 757.3 | 795.2 | 689.7 | 272.7 | 778.3 | 715.3 | 704.8
1381.2 | 855.2 | 464.1 | 185.64 | 217.0025 | 279.7 | 291.1 | 291.8 | 291.6 | 486.5 | 48.9 | 19.9 | 81.6 | 5.1 | 753.3 | 782.3 | 703.3 | 271.1 | 771.3 | 740.4 | 716.9
1382.2 | 856.2 | 464.8 | 185.92 | 217.3298 | 280.1 | 291.9 | 292.2 | 291.6 | 481.2 | 48.9 | 19.9 | 81.5 | 5.4 | 754 | 777.1 | 723 | 267.8 | 763.1 | 759.7 | 729.5
1383.2 | 857.2 | 465.3 | 186.12 | 217.5636 | 279.8 | 293.3 | 292.6 | 291.1 | 474.3 | 48.9 | 19.9 | 81.6 | 5.4 | 744.9 | 757.2 | 729.3 | 262.9 | 730 | 742.5 | 739.3
1384.2 | 858.2 | 465.1 | 186.04 | 217.47 | 279.5 | 294.7 | 293.1 | 291.5 | 461.3 | 48.9 | 19.9 | 81.4 | 4.8 | 722.6 | 719 | 711.5 | 258.4 | 700.3 | 709.9 | 733.4
1385.2 | 859.2 | 465.2 | 186.08 | 217.5168 | 279.3 | 295.7 | 293.2 | 293 | 449.4 | 48.9 | 19.9 | 81.1 | 3.3 | 708.8 | 695.4 | 714.8 | 256.6 | 679.4 | 722.6 | 737.7
1386.2 | 860.2 | 465 | 186 | 217.4233 | 278.4 | 296.7 | 293.3 | 293.6 | 442.5 | 48.9 | 19.9 | 80.9 | 3.4 | 704 | 684.7 | 732.1 | 259.3 | 682.2 | 752.5 | 748.4
1387.2 | 861.2 | 465.2 | 186.08 | 217.5168 | 277.1 | 297.4 | 294 | 294 | 440 | 48.7 | 19.9 | 80.8 | 4.1 | 707.6 | 684.7 | 730 | 261.8 | 710.9 | 762.1 | 749.5
1388.2 | 862.2 | 464.9 | 185.96 | 217.3765 | 276.4 | 297.1 | 294.3 | 294.2 | 444.6 | 48.6 | 19.9 | 80.9 | 4.1 | 711.7 | 691.3 | 723.8 | 262.4 | 740.2 | 764.2 | 744.1
1389.2 | 863.2 | 464.9 | 185.96 | 217.3765 | 275.6 | 297.5 | 294.2 | 294 | 445.6 | 48.8 | 19.9 | 81.1 | 3.9 | 715.2 | 693.7 | 726.9 | 267.6 | 763 | 774.1 | 740.8
1390.2 | 864.2 | 465 | 186 | 217.4233 | 274.9 | 296.8 | 293.5 | 293.1 | 447.5 | 49 | 19.9 | 81.4 | 4 | 715.3 | 695 | 733.7 | 269.5 | 752.2 | 786.4 | 746.9
1391.2 | 865.2 | 464.4 | 185.76 | 217.1427 | 274.6 | 296.6 | 293.2 | 292.2 | 449.4 | 48.8 | 19.9 | 81.5 | 3.8 | 720.4 | 709.8 | 736.1 | 270.4 | 742.8 | 789.1 | 752.3
1392.2 | 866.2 | 464.5 | 185.8 | 217.1895 | 274.7 | 296.2 | 293.1 | 291.9 | 453.9 | 48.7 | 19.9 | 81.6 | 3.5 | 731.9 | 740.5 | 758.4 | 267.1 | 739 | 780.5 | 752.5
1393.2 | 867.2 | 464.6 | 185.84 | 217.2363 | 275.3 | 296.6 | 291.9 | 291.7 | 464.8 | 48.6 | 19.9 | 81.7 | 3.5 | 742.5 | 764.7 | 747.9 | 264 | 737 | 761.4 | 741.5
1394.2 | 868.2 | 465 | 186 | 217.4233 | 275.9 | 296.4 | 291.4 | 292 | 476 | 48.5 | 19.9 | 81.8 | 3.5 | 748.7 | 778.4 | 748 | 261.2 | 721.6 | 743 | 734
1395.2 | 869.2 | 464.4 | 185.76 | 217.1427 | 276.2 | 296.7 | 291 | 292.3 | 484.1 | 48.3 | 19.9 | 81.7 | 3.6 | 754.9 | 792.5 | 754 | 259 | 702.8 | 744.3 | 726.5
1396.2 | 870.2 | 464 | 185.6 | 216.9557 | 275.8 | 296.6 | 290.9 | 293.1 | 492.5 | 48.2 | 19.9 | 81.6 | 4.1 | 762.1 | 804.4 | 783.6 | 257.7 | 684 | 747.3 | 742.4
1397.2 | 871.2 | 464.4 | 185.76 | 217.1427 | 276 | 296 | 291.2 | 294.8 | 499.6 | 48.2 | 19.9 | 81.5 | 4.2 | 767 | 810.5 | 790.8 | 259.8 | 672.7 | 741.4 | 745.3
1398.2 | 872.2 | 464.8 | 185.92 | 217.3298 | 277.1 | 295.3 | 291.8 | 295.8 | 512.2 | 48.1 | 19.9 | 81.4 | 4.1 | 767.2 | 814.4 | 756.5 | 259.6 | 670.8 | 715.8 | 731.8
1399.2 | 873.2 | 464.7 | 185.88 | 217.283 | 277.1 | 294.7 | 292.1 | 295.7 | 514.4 | 48 | 19.9 | 81.4 | 3.9 | 760.3 | 802.1 | 716.3 | 259.1 | 679.4 | 695.9 | 716
1400.2 | 874.2 | 464.8 | 185.92 | 217.3298 | 277.3 | 294.5 | 292.5 | 295.9 | 501.1 | 48 | 19.9 | 81.3 | 3.9 | 746.1 | 771.8 | 678.4 | 258.8 | 701.4 | 666 | 702.1
1401.2 | 875.2 | 465.1 | 186.04 | 217.47 | 277.9 | 295.1 | 293.4 | 296 | 492.9 | 48 | 19.9 | 81.2 | 3.8 | 734.7 | 756.7 | 653.1 | 256.4 | 713.4 | 654.6 | 694.9
1402.2 | 876.2 | 464.5 | 185.8 | 217.1895 | 278.5 | 296.3 | 294.6 | 295.5 | 488.9 | 48.2 | 19.9 | 81.2 | 4.6 | 727 | 746.7 | 628.8 | 256 | 739.1 | 642.8 | 688.9
1403.2 | 877.2 | 464.7 | 185.88 | 217.283 | 279.4 | 297.8 | 295.3 | 294.9 | 491.5 | 48.2 | 19.9 | 81.3 | 4.5 | 727.2 | 756.8 | 632.4 | 259.5 | 764.8 | 669.6 | 695.3
1404.2 | 878.2 | 465.1 | 186.04 | 217.47 | 280.5 | 298.7 | 295.6 | 294.5 | 491.6 | 48.1 | 19.9 | 81.4 | 4.1 | 731.3 | 753.7 | 649 | 260.3 | 781.6 | 708.5 | 711.4
1405.2 | 879.2 | 465.4 | 186.16 | 217.6103 | 281.6 | 298.5 | 296.3 | 294 | 495.3 | 48.1 | 19.9 | 81.4 | 3.8 | 736.9 | 753.1 | 666.5 | 261.2 | 791.2 | 734.9 | 726.3
1406.2 | 880.2 | 464.6 | 185.84 | 217.2363 | 282.4 | 298 | 296.7 | 294.1 | 500.9 | 48.2 | 19.9 | 81.5 | 4.1 | 735.9 | 741.5 | 666.1 | 263.3 | 805.1 | 752.1 | 731.4
1407.2 | 881.2 | 465.3 | 186.12 | 217.5636 | 282.9 | 297.5 | 296.8 | 294.8 | 496.1 | 48.3 | 19.9 | 81.5 | 4.2 | 736.3 | 736.7 | 673.3 | 264.3 | 808.1 | 770.8 | 735.6
1408.2 | 882.2 | 464.6 | 185.84 | 217.2363 | 283.8 | 297 | 297.4 | 294.8 | 492.4 | 48.4 | 19.9 | 81.5 | 3.9 | 740.7 | 739.6 | 679.2 | 261.9 | 826.5 | 772.6 | 736.3
1409.2 | 883.2 | 465 | 186 | 217.4233 | 284 | 297 | 297.9 | 294.3 | 496.6 | 48.5 | 19.9 | 81.4 | 3.7 | 751.5 | 762.7 | 705.9 | 261.4 | 821.7 | 781.3 | 740.9
1410.2 | 884.2 | 465 | 186 | 217.4233 | 283.7 | 297.7 | 298.1 | 294.4 | 511.3 | 48.5 | 19.9 | 81.3 | 3.4 | 760.2 | 777 | 722.2 | 259.9 | 801.3 | 779.5 | 742.8
1411.2 | 885.2 | 465.1 | 186.04 | 217.47 | 283.9 | 297.9 | 297.8 | 295.4 | 513.7 | 48.4 | 19.9 | 81.2 | 4 | 766.8 | 795.4 | 725.6 | 259.8 | 774.9 | 752.8 | 732.4
1412.2 | 886.2 | 465.1 | 186.04 | 217.47 | 283.9 | 298.2 | 297.6 | 296.3 | 509.5 | 48.4 | 19.9 | 81.3 | 3.6 | 768.8 | 803.8 | 706.1 | 257.8 | 768 | 719.4 | 720.2
1413.2 | 887.2 | 465 | 186 | 217.4233 | 283.6 | 298.8 | 298.5 | 296.8 | 514.2 | 48.4 | 19.9 | 81.5 | 3.7 | 767.1 | 798.4 | 685.6 | 257.8 | 764 | 699.5 | 710.6
1414.2 | 888.2 | 465.1 | 186.04 | 217.47 | 283.6 | 299.4 | 298.8 | 297.4 | 509.4 | 48.6 | 19.9 | 81.5 | 4 | 770 | 805.3 | 688.2 | 259.6 | 772.4 | 718.2 | 711.1
1415.2 | 889.2 | 465 | 186 | 217.4233 | 283.4 | 299.5 | 298.6 | 297.9 | 513.4 | 48.8 | 19.9 | 81.5 | 3.8 | 774.9 | 813.1 | 713.4 | 255.7 | 771.9 | 736.1 | 725.8
1416.2 | 890.2 | 464.4 | 185.76 | 217.1427 | 284.4 | 299.7 | 297.9 | 298 | 504.5 | 48.8 | 19.9 | 81.5 | 4 | 776.6 | 816.1 | 718.3 | 253.2 | 765.3 | 728 | 725.1
1417.2 | 891.2 | 464.3 | 185.72 | 217.096 | 286.3 | 299.2 | 297.2 | 297.5 | 514.1 | 48.6 | 19.9 | 81.5 | 3.6 | 782.5 | 828.7 | 735 | 252.9 | 763.4 | 735.6 | 728
1418.2 | 892.2 | 464.8 | 185.92 | 217.3298 | 286.5 | 299.1 | 297.7 | 298 | 549.8 | 48.7 | 19.9 | 81.4 | 3.4 | 787.7 | 840.9 | 750.6 | 254.6 | 749.6 | 735.3 | 733.4
1419.2 | 893.2 | 465.2 | 186.08 | 217.5168 | 287 | 299.6 | 297.6 | 299.3 | 559.2 | 48.6 | 19.9 | 81.4 | 3.7 | 793.8 | 850.7 | 762 | 256.7 | 745.9 | 737.1 | 741.4
1420.2 | 894.2 | 465.1 | 186.04 | 217.47 | 286.8 | 300.1 | 297.8 | 299.5 | 556.6 | 48.4 | 19.9 | 81.4 | 3.7 | 793.4 | 842.1 | 745.2 | 258 | 757.3 | 726.5 | 733.6
1421.2 | 895.2 | 464.5 | 185.8 | 217.1895 | 286.1 | 301.6 | 298.5 | 300.3 | 543.7 | 48.3 | 19.9 | 81.5 | 4.1 | 788.4 | 822.5 | 715 | 257.7 | 784.1 | 722.3 | 723.8
1422.2 | 896.2 | 464.9 | 185.96 | 217.3765 | 285.5 | 302.2 | 299.8 | 301.3 | 547.2 | 48.1 | 19.9 | 81.5 | 3.9 | 784.9 | 817.4 | 699 | 257.9 | 802.8 | 746 | 722.5
1423.2 | 897.2 | 464.2 | 185.68 | 217.0492 | 285.4 | 301.9 | 300.7 | 300.7 | 556.6 | 48 | 19.9 | 81.5 | 3.8 | 784 | 809 | 701.4 | 256 | 817.6 | 778 | 731.8
1424.2 | 898.2 | 464.5 | 185.8 | 217.1895 | 285.2 | 301.3 | 300.7 | 300.1 | 554.3 | 48 | 19.9 | 81.4 | 3.5 | 784.2 | 797.7 | 707.8 | 255.9 | 828.6 | 787.6 | 741.4
1425.2 | 899.2 | 464.6 | 185.84 | 217.2363 | 286.1 | 300.4 | 300.5 | 300.1 | 550.5 | 48.3 | 19.9 | 81.2 | 3 | 779 | 790.4 | 685.5 | 255.4 | 828.4 | 758.9 | 729
1426.2 | 900.2 | 465 | 186 | 217.4233 | 288.3 | 299.4 | 300.7 | 301.3 | 541.6 | 48.4 | 19.9 | 81.1 | 3 | 766.5 | 774 | 664.2 | 254.5 | 820.9 | 731.6 | 713.1
1427.2 | 901.2 | 463.2 | 185.28 | 216.5816 | 288.8 | 298.6 | 301.7 | 301.6 | 534.7 | 48.6 | 19.9 | 81 | 3.2 | 764.6 | 781 | 670.9 | 252.6 | 814.1 | 736.3 | 710.8
1428.2 | 902.2 | 463.9 | 185.56 | 216.9089 | 290.2 | 299.4 | 302.1 | 301.7 | 536.4 | 48.8 | 19.9 | 81 | 3.3 | 764.9 | 786.6 | 680.8 | 252.6 | 808.8 | 740 | 714.8
1429.2 | 903.2 | 463.5 | 185.4 | 216.7219 | 290.4 | 299.8 | 302.5 | 301.9 | 527.8 | 48.8 | 19.9 | 81.1 | 3.6 | 751.5 | 758.8 | 657.6 | 256 | 809 | 744.7 | 715.2
1430.2 | 904.2 | 464.1 | 185.64 | 217.0025 | 290.5 | 299.4 | 303.8 | 301.3 | 515.4 | 48.7 | 19.9 | 81.1 | 3.3 | 732.4 | 720.7 | 626.4 | 256.7 | 798.7 | 715.1 | 703.3
1431.2 | 905.2 | 464.9 | 185.96 | 217.3765 | 290.6 | 299.1 | 304.6 | 301.4 | 504.8 | 48.5 | 19.9 | 81.1 | 3.1 | 712.7 | 687.5 | 599.8 | 261.1 | 781.2 | 701.3 | 694
1432.2 | 906.2 | 464.3 | 185.72 | 217.096 | 290.9 | 298.8 | 305.8 | 300.9 | 487.9 | 48.4 | 19.9 | 81.1 | 3.1 | 694.6 | 657.3 | 583.8 | 261.4 | 778.4 | 685.9 | 690.4
1433.2 | 907.2 | 463.8 | 185.52 | 216.8622 | 291.6 | 298.5 | 306.7 | 299.9 | 474 | 48.4 | 19.9 | 81.2 | 3.2 | 682.4 | 636.5 | 577.5 | 259.7 | 781.5 | 677.5 | 685.7
1434.2 | 908.2 | 463.7 | 185.48 | 216.8154 | 291.4 | 299.2 | 307.2 | 299.1 | 465.6 | 48.6 | 19.9 | 81.3 | 3.4 | 677.9 | 645.5 | 566.1 | 261.1 | 776.6 | 654.9 | 680.4
1435.2 | 909.2 | 464.5 | 185.8 | 217.1895 | 291.3 | 299.2 | 307.9 | 298.1 | 457.4 | 48.7 | 19.9 | 81.3 | 3.1 | 678.5 | 661.8 | 578.1 | 262.1 | 758.5 | 662.1 | 680.7
1436.2 | 910.2 | 464.3 | 185.72 | 217.096 | 291 | 298.9 | 308.2 | 297.7 | 454.4 | 48.7 | 19.9 | 81.5 | 3.2 | 677 | 668.3 | 576.9 | 260.5 | 748.3 | 644.7 | 680.2
1437.2 | 911.2 | 464 | 185.6 | 216.9557 | 290.8 | 298.5 | 307.7 | 297.4 | 453.9 | 48.7 | 19.9 | 81.6 | 3.6 | 678.3 | 676.4 | 562.1 | 258.1 | 761.3 | 648.5 | 672.8
1438.2 | 912.2 | 464.6 | 185.84 | 217.2363 | 290.7 | 298.5 | 307.3 | 297.7 | 468.7 | 48.6 | 19.9 | 81.8 | 3.3 | 682.6 | 681 | 566.8 | 255.4 | 791.7 | 687.2 | 682.9
1439.2 | 913.2 | 464.5 | 185.8 | 217.1895 | 290.4 | 299 | 307 | 297.3 | 476 | 48.3 | 19.8 | 81.9 | 3.5 | 689.9 | 696.1 | 601.5 | 254.9 | 797.3 | 715.4 | 700.3
1440.2 | 914.2 | 464.8 | 185.92 | 217.3298 | 289.8 | 298.9 | 306.6 | 297.1 | 471.4 | 48.2 | 19.9 | 81.9 | 3.9 | 690.9 | 699.7 | 645.5 | 258.2 | 777.9 | 731 | 718.4
1441.2 | 915.2 | 464.8 | 185.92 | 217.3298 | 288.9 | 299.7 | 305.9 | 297.6 | 470.9 | 48.1 | 19.9 | 82.2 | 4.5 | 698 | 715.8 | 674.5 | 257.1 | 770.5 | 755.2 | 729.3
1442.2 | 916.2 | 465 | 186 | 217.4233 | 288.2 | 300.8 | 304.8 | 299.1 | 470.7 | 48.3 | 19.9 | 82.4 | 4.5 | 712.6 | 739.5 | 700.5 | 256 | 779.4 | 771.4 | 736.9
1443.2 | 917.2 | 464.2 | 185.68 | 217.0492 | 287.8 | 299.8 | 303.9 | 299.7 | 471.3 | 48.5 | 19.8 | 82.6 | 4.5 | 718.3 | 748.5 | 727.5 | 256.3 | 749.1 | 752.8 | 735.1
1444.2 | 918.2 | 464.1 | 185.64 | 217.0025 | 287 | 298.9 | 303.4 | 300 | 475.2 | 49 | 19.8 | 82.7 | 4.6 | 729.3 | 767.8 | 756.8 | 255.8 | 722.5 | 732.7 | 730.7
1445.2 | 919.2 | 465 | 186 | 217.4233 | 286.3 | 298.4 | 302.3 | 300.2 | 474.8 | 49.3 | 19.8 | 82.7 | 4.4 | 731.7 | 763 | 753.7 | 258.1 | 706.8 | 748.9 | 736.9
1446.2 | 920.2 | 464.3 | 185.72 | 217.096 | 286 | 298.1 | 302 | 301.1 | 469.1 | 49.2 | 19.9 | 82.7 | 3.9 | 728.3 | 749.4 | 752.7 | 259.6 | 699.8 | 756.8 | 739.6
1447.2 | 921.2 | 464.1 | 185.64 | 217.0025 | 286.2 | 297.7 | 302.1 | 302.1 | 463.3 | 49.2 | 19.8 | 82.9 | 4.7 | 736.2 | 764.9 | 768.3 | 257 | 702.2 | 758.2 | 745.1
1448.2 | 922.2 | 464.8 | 185.92 | 217.3298 | 285.6 | 296.9 | 302.6 | 302.4 | 469.4 | 49.1 | 19.8 | 82.9 | 4.4 | 744.6 | 780.1 | 777.1 | 254.7 | 700.8 | 754.1 | 741.7
1449.2 | 923.2 | 464.9 | 185.96 | 217.3765 | 285.7 | 296 | 303.4 | 302.9 | 479 | 49 | 19.8 | 82.9 | 4.2 | 748.8 | 790.1 | 765.6 | 251.3 | 684.4 | 744.6 | 730.9
1450.2 | 924.2 | 464 | 185.6 | 216.9557 | 285.8 | 295.4 | 303.9 | 303.7 | 485.5 | 49.1 | 19.8 | 82.9 | 4.4 | 754.5 | 804.6 | 772.4 | 249 | 677.5 | 737.7 | 729.8
1451.2 | 925.2 | 464 | 185.6 | 216.9557 | 285.3 | 295.5 | 304.2 | 305.3 | 489.7 | 49.2 | 19.8 | 83 | 4.5 | 759.9 | 803.3 | 775.1 | 251.4 | 669.2 | 743.2 | 733
1452.2 | 926.2 | 464.5 | 185.8 | 217.1895 | 285.6 | 295.2 | 305 | 305.5 | 488 | 49.2 | 19.8 | 82.9 | 4.6 | 767.8 | 814.3 | 774.3 | 253.1 | 677.4 | 765.6 | 738.9
1453.2 | 927.2 | 464 | 185.6 | 216.9557 | 285.3 | 295 | 306.1 | 305 | 508 | 49.2 | 19.8 | 82.9 | 4.6 | 773.9 | 825 | 768 | 252.7 | 695.3 | 757.6 | 739.5
1454.2 | 928.2 | 464.7 | 185.88 | 217.283 | 285.3 | 295.3 | 305.9 | 304.4 | 519.6 | 49.2 | 19.8 | 82.9 | 4.5 | 777.8 | 824.2 | 764.7 | 250.4 | 721.4 | 761.7 | 732.1
1455.2 | 929.2 | 464.4 | 185.76 | 217.1427 | 284.3 | 296.7 | 306.3 | 305 | 522.5 | 49.2 | 19.8 | 83 | 4.3 | 773.7 | 805.3 | 743 | 251.2 | 748.7 | 788.6 | 737.2
1456.2 | 930.2 | 464.8 | 185.92 | 217.3298 | 283.7 | 297.4 | 306.6 | 304.8 | 513.5 | 49.3 | 19.8 | 83.2 | 4.9 | 761.8 | 779.8 | 740.7 | 253.5 | 747.5 | 796.2 | 744.8
1457.2 | 931.2 | 464.6 | 185.84 | 217.2363 | 283.1 | 298.3 | 306.4 | 304.2 | 498 | 49.3 | 19.8 | 83 | 3.6 | 760.9 | 780.3 | 748.5 | 253.3 | 757.5 | 811.5 | 749.6
1458.2 | 932.2 | 464.1 | 185.64 | 217.0025 | 282.9 | 298.2 | 306.1 | 303.9 | 491.2 | 49.4 | 19.8 | 82.8 | 3.3 | 756 | 775.1 | 720.4 | 255.5 | 774.7 | 781.2 | 736.8
1459.2 | 933.2 | 464.1 | 185.64 | 217.0025 | 284.5 | 297.8 | 305.5 | 303.5 | 492.9 | 49.5 | 19.8 | 82.7 | 3.6 | 748.3 | 764.8 | 697.2 | 254.6 | 781.2 | 753.7 | 718.5
1460.2 | 934.2 | 464.9 | 185.96 | 217.3765 | 285.4 | 299.1 | 305.4 | 302.4 | 493.4 | 49.5 | 19.8 | 82.5 | 3.4 | 735.9 | 740.6 | 669.6 | 252.7 | 780.1 | 751.3 | 712.6
1461.2 | 935.2 | 464.8 | 185.92 | 217.3298 | 286.1 | 300.6 | 305.1 | 301.2 | 481.5 | 49.4 | 19.8 | 82.6 | 3.8 | 720.7 | 716 | 643 | 253.7 | 780.1 | 721.8 | 702
1462.2 | 936.2 | 464.1 | 185.64 | 217.0025 | 287.6 | 300.9 | 305.2 | 300.5 | 471.7 | 49.2 | 19.8 | 82.6 | 3.2 | 707.8 | 705.1 | 619 | 255.2 | 776.1 | 683 | 693.4
1463.2 | 937.2 | 465.3 | 186.12 | 217.5636 | 288.5 | 300.4 | 305.1 | 299.8 | 467.3 | 49 | 19.8 | 82.7 | 3.1 | 701.5 | 706.4 | 606.7 | 256.1 | 769.4 | 668.8 | 688.5
1464.2 | 938.2 | 466.4 | 186.56 | 218.0779 | 288.9 | 300.5 | 305.4 | 298.9 | 477.3 | 49.1 | 19.8 | 82.9 | 4 | 711 | 723.6 | 636 | 254.5 | 768 | 704.8 | 704.8
1465.2 | 939.2 | 467 | 186.8 | 218.3584 | 289 | 301.2 | 305.4 | 298.1 | 479.8 | 49.5 | 19.8 | 83.1 | 4.2 | 719.9 | 736.9 | 666.5 | 256 | 774.1 | 719.9 | 722.8
1466.2 | 940.2 | 466.9 | 186.76 | 218.3117 | 289.1 | 302.5 | 304.6 | 298.6 | 481.8 | 50 | 19.8 | 83.3 | 4.2 | 726.5 | 742.5 | 670.4 | 254.9 | 784.1 | 739.9 | 728.4
1467.2 | 941.2 | 466.5 | 186.6 | 218.1246 | 288.9 | 302.2 | 304.2 | 299.5 | 496.6 | 50.1 | 19.8 | 83.2 | 4.3 | 735 | 751.7 | 679.3 | 250.2 | 789.7 | 750.9 | 729.9
1468.2 | 942.2 | 465.3 | 186.12 | 217.5636 | 288.5 | 301.6 | 303.7 | 299.6 | 507.1 | 50.1 | 19.8 | 82.9 | 4 | 744.9 | 766.3 | 706 | 248.8 | 798.1 | 749.9 | 731.4
1469.2 | 943.2 | 465.1 | 186.04 | 217.47 | 288.4 | 301.7 | 302.9 | 300.3 | 502.1 | 50.3 | 19.8 | 82.8 | 4.4 | 750.2 | 766.9 | 726.2 | 248.7 | 786.7 | 772.7 | 742.6
1470.2 | 944.2 | 465.9 | 186.36 | 217.8441 | 289.3 | 302 | 302.6 | 300.8 | 497.5 | 50.3 | 19.8 | 82.8 | 4.8 | 759.2 | 784 | 725.4 | 245.9 | 787.7 | 777.8 | 740.2
1471.2 | 945.2 | 467 | 186.8 | 218.3584 | 289.8 | 301.7 | 301.9 | 301 | 497.9 | 50.3 | 19.8 | 82.7 | 4.6 | 764 | 794.7 | 719 | 243.8 | 797 | 767.4 | 729.7
1472.2 | 946.2 | 466.1 | 186.44 | 217.9376 | 290.5 | 302.4 | 301 | 300.6 | 499.7 | 50.3 | 19.8 | 82.6 | 4.1 | 760.6 | 779.2 | 720.3 | 244.1 | 800 | 787.2 | 739.9
1473.2 | 947.2 | 387.3 | 154.92 | 181.0926 | 290.3 | 303.2 | 301.1 | 299.8 | 498.2 | 50.2 | 19.8 | 82.5 | 3.8 | 764.3 | 786.2 | 754.1 | 244 | 788.4 | 793.4 | 748
1474.2 | 948.2 | 18.8 | 7.52 | 8.7904 | 290 | 302.9 | 301 | 299.5 | 500.9 | 50.2 | 19.8 | 82.5 | 3.2 | 768.9 | 786.2 | 767.1 | 244.3 | 776.8 | 803.4 | 754
1475.2 | 949.2 | -6.8 | 0 | 0 | 289.2 | 301.6 | 301 | 299.3 | 485.4 | 50.3 | 19.8 | 82.6 | 3.7 | 750.6 | 742.8 | 722.6 | 244.8 | 747.2 | 756.6 | 735.7
1476.2 | 950.2 | -6.8 | 0 | 0 | 288 | 299.2 | 300.9 | 298.4 | 462 | 50.2 | 19.8 | 82.9 | 3.2 | 724.8 | 692.2 | 660.4 | 240.8 | 693.8 | 687.3 | 704
1477.2 | 951.2 | -6.8 | 0 | 0 | 286.7 | 297.2 | 299.8 | 297.4 | 442.7 | 50 | 19.8 | 83 | 3 | 698 | 650.2 | 610.4 | 235.8 | 649.6 | 630.8 | 683.3
1478.2 | 952.2 | -6.8 | 0 | 0 | 285.1 | 295.5 | 298.1 | 295.8 | 427.3 | 49.6 | 19.8 | 83.1 | 3.4 | 672.4 | 613.7 | 568.5 | 231.1 | 613.4 | 584.6 | 670.7
1479.2 | 953.2 | -6.8 | 0 | 0 | 283.3 | 293.3 | 295.8 | 293.4 | 415.1 | 49.5 | 19.8 | 83.1 | 3.5 | 648.3 | 580.9 | 530.4 | 225 | 579.2 | 545.9 | 660.9
1480.2 | 954.2 | -6.8 | 0 | 0 | 281.5 | 291.1 | 292.9 | 290.7 | 403.4 | 49.3 | 19.8 | 82.8 | 3.5 | 630.4 | 550.6 | 498.8 | 220.1 | 549.2 | 511.4 | 656.4
1481.2 | 955.2 | -6.8 | 0 | 0 | 279.5 | 289.2 | 289.8 | 287.4 | 392.5 | 49 | 19.8 | 82.4 | 4 | 613.8 | 524.7 | 472.8 | 214.6 | 519.8 | 479.8 | 647.9
1482.2 | 956.2 | -6.8 | 0 | 0 | 277.5 | 286.9 | 286.5 | 283.5 | 382.6 | 48.7 | 19.8 | 81.8 | 4 | 595.8 | 501 | 452 | 208 | 498.7 | 454.6 | 642.2
1483.2 | 957.2 | -6.8 | 0 | 0 | 275.7 | 284.5 | 283 | 279.7 | 373.9 | 48.5 | 19.8 | 81.1 | 3.5 | 581.5 | 480.3 | 432.4 | 202.2 | 481.5 | 432.5 | 639
1484.2 | 958.2 | -6.8 | 0 | 0 | 273.7 | 282 | 279.9 | 276.2 | 366 | 48.4 | 19.8 | 80.3 | 3.5 | 570 | 460.9 | 414.1 | 195.8 | 465.2 | 413.2 | 637.1
1485.2 | 959.2 | -6.8 | 0 | 0 | 271.5 | 279 | 276.9 | 273 | 358.5 | 48.2 | 19.8 | 79.6 | 4 | 558.1 | 443.7 | 396.7 | 191.2 | 448.8 | 394.8 | 632.8
1486.2 | 960.2 | -6.7 | 0 | 0 | 269 | 275.9 | 274 | 270 | 351.6 | 48.1 | 19.8 | 78.8 | 4 | 547.5 | 426.7 | 380.8 | 186.5 | 433.1 | 378 | 627.5
1487.2 | 961.2 | -6.7 | 0 | 0 | 265.9 | 272.6 | 271 | 267 | 345.1 | 48.3 | 19.8 | 78.1 | 3.6 | 538.5 | 411.4 | 367 | 182.3 | 420.3 | 363 | 623.6
1488.2 | 962.2 | -6.7 |  |  | 263 | 269.5 | 268.1 | 264.2 | 338.8 | 48.6 | 19.8 | 77.4 | 3.7 | 530.1 | 397.6 | 354.1 | 178.4 | 408.4 | 348.8 | 618.3
1489.2 | 963.2 | -6.7 |  |  | 260.4 | 266.6 | 265.3 | 261.5 | 333 | 48.7 | 19.8 | 76.8 | 3.6 | 521.1 | 385.3 | 342.1 | 174.7 | 397.4 | 335.6 | 613.8
1490.2 | 964.2 | -6.7 |  |  | 258.1 | 264 | 262.4 | 259 | 327.5 | 48.8 | 19.8 | 76.2 | 3.4 | 512.4 | 374.3 | 331.6 | 172 | 386.8 | 323.9 | 609.8
1491.2 | 965.2 | -6.7 |  |  | 255.8 | 261.5 | 259.5 | 256.7 | 322.4 | 48.8 | 19.8 | 75.7 | 3.1 | 505 | 362.6 | 320.5 | 169 | 376.3 | 312.8 | 605.3
1492.2 | 966.2 | -6.7 |  |  | 253.4 | 258.9 | 256.6 | 254.3 | 317.6 | 48.8 | 19.8 | 75.3 | 2.8 | 496.2 | 351.9 | 310.3 | 166.4 | 365.8 | 300.4 | 598.5
1493.2 | 967.2 | -6.7 |  |  | 251 | 256.2 | 253.8 | 251.8 | 313.1 | 48.8 | 19.8 | 74.8 | 2.9 | 487.4 | 341.3 | 300.6 | 164.1 | 356.3 | 289.3 | 593.4
1494.2 | 968.2 | -6.7 |  |  | 248.6 | 253.7 | 251 | 249.2 | 308.7 | 48.6 | 19.8 | 74.4 | 3.4 | 479.1 | 331.3 | 290.6 | 161.4 | 347 | 278.2 | 589
1495.2 | 969.2 | -6.7 |  |  | 246.4 | 251.3 | 248.2 | 246.5 | 304.4 | 48.5 | 19.8 | 74 | 3.6 | 471.9 | 321.4 | 281.1 | 158.9 | 337.9 | 269.1 | 586
1496.2 | 970.2 | -6.7 |  |  | 244.1 | 249.1 | 245.6 | 243.9 | 300.3 | 48.4 | 19.8 | 73.6 | 3.3 | 465.7 | 312.2 | 271.9 | 156.4 | 329 | 260.4 | 582.5
1497.2 | 971.2 | -6.7 |  |  | 242.2 | 247 | 243.1 | 241.4 | 296.5 | 48.5 | 19.8 | 73.3 | 3.5 | 459.9 | 303.2 | 263.4 | 154.5 | 320.5 | 252.1 | 578.6
1498.2 | 972.2 | -6.7 |  |  | 240.4 | 245 | 240.8 | 239 | 292.8 | 48.5 | 19.8 | 73 | 3.8 | 454.2 | 294.5 | 255.3 | 152.8 | 312.3 | 243.9 | 574.5
1499.2 | 973.2 | -6.7 |  |  | 238.7 | 243.1 | 238.5 | 236.6 | 289.3 | 48.4 | 19.8 | 72.6 | 4.2 | 449.1 | 286.5 | 247.6 | 150.8 | 304.7 | 236.1 | 570
1500.2 | 974.2 | -6.7 |  |  | 237 | 241.3 | 236.2 | 234.4 | 286.2 | 48 | 19.8 | 72.2 | 4.6 | 443.6 | 278.8 | 240.1 | 148.6 | 297.5 | 228.8 | 565.5
1501.2 | 975.2 | -6.7 |  |  | 235.3 | 239.5 | 234.1 | 232.4 | 283.1 | 47.7 | 19.8 | 71.9 | 3.9 | 438.4 | 271.6 | 233.1 | 146.2 | 290.5 | 222 | 561.3
1502.2 | 976.2 | -6.7 |  |  | 233.5 | 237.8 | 232.1 | 230.3 | 280.2 | 47.5 | 19.8 | 71.6 | 3.7 | 433.2 | 264.9 | 226.7 | 144.1 | 283.7 | 215.4 | 557.1
1503.2 | 977.2 | -6.7 |  |  | 231.9 | 236 | 230.2 | 228.2 | 277.3 | 47.5 | 19.8 | 71.4 | 3.5 | 428.1 | 258.8 | 220.9 | 142.5 | 277.3 | 209.6 | 553.1
1504.2 | 978.2 | -6.7 |  |  | 230.3 | 234.2 | 228.3 | 226.2 | 274.4 | 47.7 | 19.8 | 71.2 | 3.4 | 423.3 | 253.1 | 215.5 | 141.2 | 271.6 | 204.3 | 549
1505.2 | 979.2 | -6.7 |  |  | 228.7 | 232.3 | 226.6 | 224.2 | 271.6 | 47.9 | 19.8 | 71 | 3.7 | 418.2 | 247.7 | 210.3 | 139.9 | 266.3 | 199.4 | 544.6
1506.2 | 980.2 | -6.7 |  |  | 227.3 | 230.6 | 224.9 | 222.4 | 268.9 | 47.9 | 19.8 | 70.7 | 3.2 | 413.1 | 242.6 | 205.6 | 138.7 | 261.2 | 194.5 | 540.3
1507.2 | 981.2 | -6.7 |  |  | 225.9 | 229 | 223.2 | 220.7 | 266.5 | 47.8 | 19.8 | 70.4 | 3 | 407.7 | 237.8 | 201 | 137.3 | 256.1 | 190 | 536.7
1508.2 | 982.2 | -6.7 |  |  | 224.6 | 227.4 | 221.6 | 219.1 | 264.4 | 47.6 | 19.8 | 70.2 | 3 | 402.9 | 232.9 | 196.4 | 135.7 | 251.2 | 185.3 | 532.6
1509.2 | 983.2 | -6.7 |  |  | 223.2 | 225.8 | 220 | 217.6 | 262.2 | 47.4 | 19.8 | 69.9 | 2.8 | 398.3 | 227.8 | 191.6 | 134.4 | 246.3 | 180.6 | 528.2
1510.2 | 984.2 | -6.7 |  |  | 221.9 | 224.3 | 218.4 | 216.1 | 260 | 47.3 | 19.8 | 69.6 | 2.7 | 393.8 | 223.2 | 187.2 | 132.8 | 241.7 | 176.2 | 524.2
1511.2 | 985.2 | -6.7 |  |  | 220.7 | 222.8 | 216.7 | 214.7 | 258 | 47.3 | 19.8 | 69.3 | 2.9 | 389.6 | 218.5 | 182.9 | 130.3 | 237.2 | 172.1 | 520.3
1512.2 | 986.2 | -6.7 |  |  | 219.4 | 221.3 | 215.2 | 213.3 | 256.1 | 47.2 | 19.8 | 69 | 2.4 | 385.7 | 214.2 | 178.8 | 128.3 | 233 | 168.2 | 516.1
1513.2 | 987.2 | -6.7 |  |  | 218.2 | 219.8 | 213.9 | 212 | 254.5 | 47.1 | 19.8 | 68.7 | 2.8 | 381.2 | 210.4 | 175 | 126.7 | 228.9 | 164.4 | 512.2
1514.2 | 988.2 | -6.7 |  |  | 217 | 218.3 | 212.6 | 210.7 | 252.8 | 46.9 | 19.8 | 68.5 | 2.7 | 376.9 | 206.9 | 171.3 | 125.4 | 224.8 | 160.8 | 508.3
1515.2 | 989.2 | -6.7 |  |  | 215.7 | 216.8 | 211.4 | 209.4 | 251 | 46.5 | 19.8 | 68.1 | 2.9 | 373.2 | 203.4 | 167.8 | 124.4 | 220.7 | 157.4 | 504.6
1516.2 | 990.2 | -6.7 |  |  | 214.4 | 215.5 | 210 | 208.2 | 249.3 | 46.1 | 19.8 | 67.7 | 3.2 | 369 | 199.9 | 164.4 | 123.1 | 217.1 | 154.1 | 500.9
1517.2 | 991.2 | -6.7 |  |  | 213.2 | 214.3 | 208.6 | 206.9 | 247.7 | 46 | 19.8 | 67.2 | 3.3 | 364.1 | 196.8 | 161.4 | 121.4 | 213.5 | 151.1 | 497.4
1518.2 | 992.2 | -6.7 |  |  | 211.9 | 213.1 | 207.5 | 205.8 | 246 | 46.4 | 19.8 | 66.9 | 3.5 | 360.4 | 193.8 | 158.2 | 119.8 | 210.1 | 148.3 | 493.7
1519.2 | 993.2 | -6.7 |  |  | 210.7 | 212 | 206.4 | 204.6 | 244.4 | 46.3 | 19.8 | 66.6 | 3.6 | 356.9 | 190.7 | 155.3 | 118.7 | 206.7 | 145.4 | 490
1520.2 | 994.2 | -6.7 |  |  | 209.7 | 210.8 | 205.4 | 203.4 | 242.9 | 46 | 19.8 | 66.2 | 3.4 | 354.2 | 187.5 | 152.3 | 117.7 | 203.3 | 142.7 | 486.3
1521.2 | 995.2 | -6.7 |  |  | 208.7 | 209.6 | 204.4 | 202.3 | 241.5 | 45.9 | 19.8 | 65.8 | 4.2 | 351.6 | 184.4 | 149.5 | 116.4 | 200 | 140.2 | 482.8
1522.2 | 996.2 | -6.7 |  |  | 207.6 | 208.4 | 203.4 | 201.1 | 240.2 | 45.9 | 19.8 | 65.5 | 4.1 | 348.9 | 181.4 | 147.1 | 115.4 | 196.8 | 137.7 | 479.2
1523.2 | 997.2 | -6.7 |  |  | 206.6 | 207.3 | 202.4 | 199.9 | 238.9 | 45.9 | 19.8 | 65.2 | 3.8 | 346.4 | 178.7 | 144.3 | 114.7 | 193.7 | 134.8 | 475.6
1524.2 | 998.2 | -6.7 |  |  | 205.6 | 206.3 | 201.4 | 198.9 | 237.7 | 45.7 | 19.8 | 65 | 3.4 | 343.4 | 176.6 | 141.5 | 113.6 | 190.5 | 132 | 472.3
1525.2 | 999.2 | -6.7 |  |  | 204.7 | 205.2 | 200.4 | 197.9 | 236.5 | 45.7 | 19.8 | 64.8 | 3.2 | 339.5 | 174.8 | 138.9 | 112.4 | 187.7 | 129.3 | 469
1526.2 | 1000.2 | -6.7 |  |  | 203.6 | 204.2 | 199.5 | 196.9 | 235.3 | 45.5 | 19.8 | 64.6 | 3.3 | 335.7 | 172.7 | 136.8 | 111.8 | 184.8 | 127 | 465.9
1527.2 | 1001.2 | -6.7 |  |  | 202.6 | 203.3 | 198.6 | 195.9 | 234.1 | 45.2 | 19.8 | 64.3 | 3.2 | 332.7 | 170.4 | 134.6 | 111.2 | 182.1 | 125 | 463.1
1528.2 | 1002.2 | -6.7 |  |  | 201.8 | 202.4 | 197.7 | 194.9 | 233 | 44.6 | 19.8 | 64 | 3.6 | 330.4 | 168.2 | 132.4 | 110.4 | 179.7 | 123 | 460.1
1529.2 | 1003.2 | -6.7 |  |  | 200.9 | 201.7 | 196.8 | 193.9 | 231.9 | 44.5 | 19.8 | 63.7 | 3.7 | 328 | 166.3 | 130.3 | 109.1 | 177 | 121.1 | 457.3
1530.2 | 1004.2 | -6.7 |  |  | 200.1 | 201 | 196 | 192.9 | 230.8 | 44.3 | 19.8 | 63.4 | 3.6 | 325.2 | 164.3 | 128.3 | 108 | 174.6 | 119.2 | 454.2
1531.2 | 1005.2 | -6.7 |  |  | 199.5 | 200.1 | 195.1 | 191.9 | 229.7 | 43.9 | 19.8 | 63.2 | 3.3 | 322.7 | 162.3 | 126.3 | 107.4 | 172.3 | 117.4 | 451.1
1532.2 | 1006.2 | -6.7 |  |  | 198.8 | 199.3 | 194.3 | 191 | 228.7 | 43.5 | 19.8 | 63 | 2.9 | 319.9 | 160.9 | 124.4 | 106.2 | 171.3 | 115.7 | 448.5
1533.2 | 1007.2 | -6.7 |  |  | 198 | 198.4 | 193.5 | 190.2 | 227.8 | 43.3 | 19.8 | 62.8 | 2.8 | 316.9 | 158.9 | 122.6 | 105.5 | 168.8 | 114 | 445.9
1534.2 | 1008.2 | -6.7 |  |  | 197.2 | 197.6 | 192.8 | 189.4 | 226.9 | 43.1 | 19.8 | 62.6 | 3.2 | 314.3 | 157.3 | 120.7 | 105 | 166 | 112.1 | 442.8
1535.2 | 1009.2 | -6.7 |  |  | 196.4 | 196.9 | 192 | 188.6 | 225.9 | 43.1 | 19.8 | 62.4 | 3.2 | 311.3 | 155.9 | 119 | 104.2 | 163.5 | 110.4 | 439.8
1536.2 | 1010.2 | -6.7 |  |  | 195.5 | 196.1 | 191.2 | 187.8 | 224.9 | 43.1 | 19.8 | 62.2 | 3 | 306.7 | 154.8 | 117.4 | 103.4 | 161.7 | 108.9 | 437.1
1537.2 | 1011.2 | -6.7 |  |  | 194.6 | 195.5 | 190.4 | 187.1 | 223.9 | 43 | 19.8 | 61.9 | 2.9 | 305.1 | 153.4 | 115.8 | 102.6 | 160.4 | 107.5 | 434.6
1538.2 | 1012.2 | -6.7 |  |  | 193.7 | 194.9 | 189.6 | 186.4 | 223 | 43 | 19.8 | 61.7 | 3 | 303.7 | 152 | 114.4 | 102.1 | 158.9 | 106 | 431.6
1539.2 | 1013.2 | -6.7 |  |  | 192.9 | 194.3 | 188.9 | 185.6 | 222.1 | 42.5 | 19.8 | 61.5 | 3.4 | 302.2 | 150.4 | 112.8 | 101.6 | 157.4 | 104.6 | 428.7
1540.2 | 1014.2 | -6.7 |  |  | 192 | 193.6 | 188.2 | 184.9 | 221.2 | 42.4 | 19.8 | 61.3 | 3.3 | 300.7 | 149.1 | 111 | 101 | 155.2 | 103 | 426.3
1541.2 | 1015.2 | -6.7 |  |  | 191.3 | 192.8 | 187.6 | 184.2 | 220.3 | 42.3 | 19.8 | 61.1 | 3.5 | 298.9 | 148.2 | 109.4 | 100.1 | 153.2 | 101.6 | 424.1
1542.2 | 1016.2 | -6.7 |  |  | 190.7 | 192.1 | 186.9 | 183.4 | 219.3 | 42.2 | 19.8 | 61 | 3.5 | 297.1 | 146.7 | 108 | 98.9 | 151 | 100.4 | 421.4
1543.2 | 1017.2 | -6.7 |  |  | 190.1 | 191.5 | 186.3 | 182.6 | 218.4 | 42.1 | 19.8 | 60.8 | 3.7 | 295.2 | 145.1 | 106.6 | 98.1 | 149.2 | 99.2 | 418.6
1544.2 | 1018.2 | -6.7 |  |  | 189.4 | 191 | 185.6 | 181.9 | 217.6 | 42 | 19.8 | 60.5 | 3.9 | 293.7 | 143.9 | 105.2 | 97.2 | 147.1 | 97.9 | 415.7
1545.2 | 1019.2 | -6.7 |  |  | 188.9 | 190.4 | 185 | 181.2 | 216.8 | 42 | 19.8 | 60.4 | 3.8 | 292.1 | 142.5 | 103.9 | 96.6 | 145 | 96.7 | 413.2
1546.2 | 1020.2 | -6.7 |  |  | 188.3 | 189.8 | 184.4 | 180.5 | 216.2 | 42 | 19.8 | 60.2 | 4 | 290.5 | 141.2 | 102.5 | 95.8 | 143 | 95.5 | 410.6
1547.2 | 1021.2 | -6.7 |  |  | 187.6 | 189.1 | 183.8 | 179.8 | 215.5 | 41.8 | 19.8 | 60.1 | 3.4 | 288 | 140.4 | 101.1 | 95.2 | 141 | 94.2 | 408.1
1548.2 | 1022.2 | -6.7 |  |  | 187 | 188.4 | 183.2 | 179.1 | 214.9 | 41.6 | 19.8 | 60 | 3.1 | 284.2 | 139.7 | 99.7 | 94.8 | 138.8 | 93 | 405.8
1549.2 | 1023.2 | -6.7 |  |  | 186.4 | 187.8 | 182.6 | 178.5 | 214.2 | 41.7 | 19.8 | 59.9 | 2.9 | 282.3 | 139.4 | 98.4 | 93.9 | 136.9 | 91.7 | 403.3
1550.2 | 1024.2 | -6.7 |  |  | 185.7 | 187.3 | 182 | 177.8 | 213.6 | 41.7 | 19.8 | 59.8 | 3.1 | 278.2 | 138.9 | 97 | 93.1 | 135.4 | 90.6 | 400.9
1551.2 | 1025.2 | -6.7 |  |  | 185.2 | 186.8 | 181.4 | 177.2 | 213 | 41.5 | 19.8 | 59.6 | 3.1 | 275.7 | 138.3 | 95.8 | 92.5 | 133.8 | 89.5 | 398.5
1552.2 | 1026.2 | -6.7 |  |  | 184.7 | 186.3 | 180.7 | 176.5 | 212.5 | 41.4 | 19.8 | 59.4 | 3.1 | 273.7 | 137.7 | 94.6 | 92.2 | 132.3 | 88.4 | 396.2
1553.2 | 1027.2 | -6.7 |  |  | 184 | 185.8 | 180.1 | 175.9 | 211.9 | 41.3 | 19.8 | 59.2 | 3 | 271.9 | 136.7 | 93.4 | 91.7 | 130.5 | 87.4 | 394.1
1554.2 | 1028.2 | -6.7 |  |  | 183.4 | 185.2 | 179.5 | 175.3 | 211.3 | 41.3 | 19.9 | 59 | 3.1 | 268.7 | 137 | 92.3 | 90.9 | 129.2 | 86.4 | 391.6
1555.2 | 1029.2 | -6.7 |  |  | 182.5 | 184.8 | 179.1 | 174.9 | 210.7 | 41.1 | 19.9 | 58.9 | 2.8 | 266.5 | 137.1 | 91.2 | 90 | 128 | 85.4 | 389.1
1556.2 | 1030.2 | -6.7 |  |  | 182.3 | 184.1 | 178.3 | 174.3 | 210.2 | 40.9 | 19.9 | 58.8 | 2.9 | 265 | 137.2 | 90.3 | 89.3 | 126.7 | 84.4 | 386.2
1557.2 | 1031.2 | -6.7 |  |  | 182 | 183.5 | 177.7 | 173.6 | 209.7 | 40.9 | 19.9 | 58.6 | 2.6 | 263.9 | 136.5 | 89.4 | 88.7 | 125.2 | 83.6 | 384.1
1558.2 | 1032.2 | -6.7 |  |  | 181.1 | 183.2 | 177.3 | 173.1 | 209.1 | 40.9 | 19.9 | 58.5 | 3 | 260.9 | 135.9 | 88.4 | 87.9 | 124.1 | 82.8 | 381.8
1559.2 | 1033.2 | -6.7 |  |  | 180.9 | 182.6 | 176.4 | 172.4 | 208.5 | 40.9 | 19.9 | 58.3 | 3.6 | 258.3 | 135.2 | 87.4 | 87.3 | 122.7 | 82.1 | 379.6
1560.2 | 1034.2 | -6.7 |  |  | 180.4 | 182.2 | 175.8 | 171.9 | 208 | 40.8 | 19.9 | 58.2 | 3.6 | 256.3 | 134.2 | 86.7 | 86.8 | 121.4 | 81.4 | 377.6
1561.2 | 1035.2 | -6.7 |  |  | 179.5 | 181.9 | 175.6 | 171.5 | 207.4 | 40.8 | 19.9 | 58.1 | 3.3 | 256.2 | 133.7 | 85.8 | 86.2 | 120.1 | 80.7 | 376
1562.2 | 1036.2 | -6.7 |  |  | 178.2 | 181.7 | 175.7 | 171.2 | 206.8 | 41 | 19.9 | 58 | 3.2 | 255 | 133.6 | 85.1 | 85.4 | 119.2 | 79.8 | 375.1
1563.2 | 1037.2 | -6.7 |  |  | 178.4 | 181 | 174.8 | 170.5 | 206.4 | 41.3 | 19.9 | 57.9 | 3.3 | 253.6 | 133.3 | 84.3 | 84.6 | 118.3 | 79.2 | 373.2
1564.2 | 1038.2 | -6.7 |  |  | 177.9 | 180.5 | 174.3 | 169.9 | 205.9 | 41.4 | 19.9 | 57.7 | 3 | 251.4 | 133.3 | 83.5 | 83.9 | 117 | 78.6 | 371.2
1565.2 | 1039.2 | -6.7 |  |  | 176.9 | 180.2 | 174.2 | 169.6 | 205.5 | 41.5 | 19.9 | 57.6 | 2.6 | 250.3 | 133 | 82.6 | 83.6 | 115.9 | 78 | 368.9
1566.2 | 1040.2 | -6.7 |  |  | 177.6 | 179.2 | 173 | 168.7 | 205.2 | 41.4 | 19.9 | 57.5 | 2.6 | 247.1 | 131.9 | 81.8 | 83 | 114.8 | 77.3 | 366.1
1567.2 | 1041.2 | -6.7 |  |  | 177.2 | 178.7 | 172.5 | 168.2 | 204.8 | 41.2 | 19.9 | 57.3 | 2.8 | 245.2 | 131 | 81.1 | 82.3 | 113.9 | 76.7 | 363.4
1568.2 | 1042.2 | -6.7 |  |  | 176.7 | 178.1 | 172 | 167.7 | 204.4 | 41.1 | 19.9 | 57.2 | 3 | 243.5 | 129.8 | 80.4 | 81.8 | 113.2 | 76.1 | 361.2
1569.2 | 1043.2 | -6.7 |  |  | 176.2 | 177.6 | 171.4 | 167.2 | 204 | 40.9 | 19.9 | 57 | 2.9 | 243.1 | 128.6 | 79.8 | 81.3 | 112.5 | 75.6 | 359.3
1570.2 | 1044.2 | -6.7 |  |  | 175.8 | 177.2 | 170.8 | 166.7 | 203.5 | 40.7 | 19.9 | 56.9 | 2.8 | 243.2 | 127.5 | 79.2 | 80.7 | 111.7 | 75.1 | 357.8
1571.2 | 1045.2 | -6.7 |  |  | 175.3 | 176.8 | 170.3 | 166.2 | 202.9 | 40.7 | 19.9 | 56.8 | 3 | 243.2 | 126.4 | 78.7 | 80.2 | 110.8 | 74.6 | 356.2
1572.2 | 1046.2 | -6.7 |  |  | 174.8 | 176.4 | 169.8 | 165.7 | 202.3 | 40.6 | 19.9 | 56.7 | 3 | 243.1 | 125.1 | 78.2 | 79.6 | 109.9 | 74.1 | 354.5
1573.2 | 1047.2 | -6.7 |  |  | 174.5 | 175.9 | 169.2 | 165.2 | 201.6 | 40.6 | 19.9 | 56.6 | 2.8 | 242.6 | 124 | 77.7 | 79 | 109 | 73.7 | 352.8
1574.2 | 1048.2 | -6.7 |  |  | 174.2 | 175.5 | 168.6 | 164.8 | 200.9 | 40.6 | 19.9 | 56.5 | 2.6 | 241.9 | 122.7 | 77.2 | 78.7 | 108.2 | 73.2 | 351.1
1575.2 | 1049.2 | -6.7 |  |  | 173.8 | 175 | 168 | 164.3 | 200.2 | 40.8 | 19.9 | 56.5 | 2.3 | 240.7 | 121.6 | 76.8 | 78.1 | 107.4 | 72.6 | 349.2
1576.2 | 1050.2 | -6.7 |  |  | 173.4 | 174.5 | 167.5 | 163.9 | 199.6 | 40.8 | 19.9 | 56.4 | 2.2 | 239.2 | 120.6 | 76.3 | 77.6 | 106.6 | 72.1 | 347.6
1577.2 | 1051.2 | -6.7 |  |  | 173 | 174 | 167 | 163.6 | 199.1 | 40.9 | 19.9 | 56.3 | 2.4 | 237.7 | 119.7 | 75.9 | 77.2 | 105.8 | 71.7 | 346
1578.2 | 1052.2 | -6.7 |  |  | 172.6 | 173.6 | 166.6 | 163.2 | 198.6 | 40.9 | 19.9 | 56.2 | 2.3 | 236.5 | 118.8 | 75.4 | 76.9 | 105 | 71.4 | 344.2
1579.2 | 1053.2 | -6.7 |  |  | 172.2 | 173.2 | 166.2 | 162.9 | 198.1 | 40.8 | 19.9 | 56 | 2.4 | 235.5 | 118 | 74.9 | 76.4 | 104.2 | 71 | 342.6
1580.2 | 1054.2 | -6.7 |  |  | 171.9 | 172.9 | 165.7 | 162.5 | 197.6 | 40.7 | 19.9 | 55.8 | 2.8 | 234 | 117.7 | 74.4 | 76.2 | 103.4 | 70.6 | 341.2
1581.2 | 1055.2 | -6.7 |  |  | 171.5 | 172.6 | 165.3 | 162.1 | 197.1 | 40.7 | 19.9 | 55.7 | 2.6 | 232.6 | 116.8 | 73.8 | 75.8 | 102.6 | 70.3 | 340
1582.2 | 1056.2 | -6.7 |  |  | 171.2 | 172.1 | 164.8 | 161.6 | 196.7 | 40.7 | 19.9 | 55.5 | 2.9 | 231.9 | 115.9 | 73.4 | 75.8 | 101.9 | 70 | 338.3
1583.2 | 1057.2 | -6.7 |  |  | 170.9 | 171.6 | 164.4 | 161.1 | 196.3 | 40.8 | 19.9 | 55.3 | 3.1 | 231.3 | 114.9 | 72.8 | 75.5 | 101.2 | 69.5 | 336
1584.2 | 1058.2 | -6.7 |  |  | 170.6 | 171.3 | 163.9 | 160.7 | 195.8 | 40.9 | 19.9 | 55.2 | 3.1 | 230.5 | 114 | 72.3 | 75.1 | 100.5 | 69.1 | 334.1
1585.2 | 1059.2 | -6.7 |  |  | 170.2 | 171 | 163.5 | 160.3 | 195.4 | 40.8 | 20 | 55.1 | 3.1 | 229.6 | 113.3 | 71.9 | 74.5 | 99.8 | 68.7 | 332.5
1586.2 | 1060.2 | -6.7 |  |  | 169.8 | 170.7 | 163.1 | 159.9 | 195 | 40.8 | 20 | 55 | 3.3 | 228.5 | 113 | 71.5 | 74.1 | 99.1 | 68.3 | 331.2
1587.2 | 1061.2 | -6.7 |  |  | 169.4 | 170.3 | 162.8 | 159.5 | 194.6 | 40.8 | 20 | 54.9 | 2.8 | 227.2 | 112.6 | 71.1 | 73.5 | 98.5 | 67.9 | 329.6
1588.2 | 1062.2 | -6.7 |  |  | 169 | 169.8 | 162.4 | 159.1 | 194.2 | 40.8 | 20 | 54.9 | 2.8 | 226.1 | 112.6 | 70.6 | 72.9 | 97.9 | 67.4 | 327.8
1589.2 | 1063.2 | -6.7 |  |  | 168.7 | 169.4 | 162.1 | 158.7 | 193.8 | 40.7 | 20 | 54.8 | 3.5 | 224.9 | 112 | 70.2 | 72.5 | 97.2 | 67 | 326
1590.2 | 1064.2 | -6.7 |  |  | 168.3 | 169 | 161.7 | 158.4 | 193.4 | 40.5 | 20 | 54.7 | 3.4 | 223.6 | 111.2 | 69.8 | 72.4 | 96.5 | 66.7 | 324.4
1591.2 | 1065.2 | -6.7 |  |  | 168 | 168.6 | 161.3 | 158 | 193 | 40.3 | 20 | 54.6 | 3.1 | 222.5 | 110.4 | 69.4 | 72.3 | 95.9 | 66.3 | 322.5
1592.2 | 1066.2 | -6.7 |  |  | 167.7 | 168.2 | 160.9 | 157.6 | 192.5 | 40.2 | 20 | 54.5 | 3.3 | 220.7 | 109.3 | 69 | 72.5 | 95.2 | 66 | 320.7
1593.2 | 1067.2 | -6.7 |  |  | 167.4 | 167.9 | 160.6 | 157.2 | 192 | 40.1 | 20 | 54.4 | 3.3 | 219.4 | 108.3 | 68.8 | 72.5 | 94.6 | 65.7 | 319.3
1594.2 | 1068.2 | -6.7 |  |  | 167.1 | 167.7 | 160.2 | 156.9 | 191.5 | 39.9 | 20 | 54.3 | 3.4 | 218.6 | 107.3 | 68.5 | 72.3 | 94.1 | 65.4 | 317.8
1595.2 | 1069.2 | -6.7 |  |  | 166.8 | 167.4 | 159.8 | 156.6 | 191 | 39.9 | 20 | 54.2 | 3.4 | 217.6 | 106.6 | 68.2 | 72.2 | 93.5 | 65.2 | 316.4
1596.2 | 1070.2 | -6.7 |  |  | 166.5 | 167.1 | 159.5 | 156.2 | 190.5 | 39.8 | 20 | 54.1 | 3.1 | 216.6 | 106.2 | 67.9 | 72.2 | 93 | 64.9 | 315.2
1597.2 | 1071.2 | -6.7 |  |  | 166.1 | 166.8 | 159.2 | 155.9 | 190 | 39.6 | 20 | 53.9 | 2.9 | 215.9 | 105.5 | 67.7 | 72.2 | 92.5 | 64.5 | 313.7
1598.2 | 1072.2 | -6.7 |  |  | 165.7 | 166.5 | 158.8 | 155.6 | 189.5 | 39.4 | 20 | 53.8 | 2.9 | 215 | 104.7 | 67.4 | 72.2 | 92.1 | 64.2 | 312.4
1599.2 | 1073.2 | -6.7 |  |  | 165.4 | 166.1 | 158.4 | 155.3 | 189 | 39.1 | 20 | 53.7 | 2.8 | 214 | 103.8 | 67.1 | 71.9 | 91.6 | 64 | 310.9
1600.2 | 1074.2 | -6.7 |  |  | 165 | 165.7 | 158 | 154.9 | 188.4 | 39.1 | 20 | 53.6 | 2.7 | 213.1 | 102.9 | 66.8 | 72 | 91.1 | 63.8 | 309.2
1601.2 | 1075.2 | -6.7 |  |  | 164.7 | 165.3 | 157.7 | 154.6 | 187.9 | 39 | 20 | 53.5 | 2.6 | 212.1 | 102.1 | 66.5 | 71.9 | 90.8 | 63.6 | 307.7
1602.2 | 1076.2 | -6.7 |  |  | 164.4 | 165 | 157.3 | 154.3 | 187.4 | 38.8 | 20 | 53.4 | 2.6 | 210.8 | 101.3 | 66.3 | 71.3 | 90.3 | 63.3 | 306.3
1603.2 | 1077.2 | -6.7 |  |  | 164.1 | 164.7 | 157 | 154 | 186.9 | 38.9 | 20 | 53.4 | 2.8 | 209.2 | 100.8 | 66 | 71.2 | 89.9 | 63.1 | 305.2
1604.2 | 1078.2 | -6.7 |  |  | 163.9 | 164.4 | 156.7 | 153.6 | 186.5 | 38.9 | 20 | 53.3 | 2.5 | 207.7 | 100.7 | 65.7 | 70.8 | 89.5 | 62.8 | 304.3
1605.2 | 1079.2 | -6.7 |  |  | 163.6 | 164.1 | 156.4 | 153.3 | 186 | 38.9 | 20 | 53.2 | 2.7 | 206.2 | 100.6 | 65.3 | 70.7 | 89.2 | 62.5 | 303
1606.2 | 1080.2 | -6.7 |  |  | 163.2 | 163.7 | 156.1 | 153 | 185.6 | 38.9 | 20 | 53.1 | 2.7 | 204.2 | 100 | 64.9 | 70.6 | 89 | 62.1 | 301.4
1607.2 | 1081.2 | -6.7 |  |  | 162.9 | 163.3 | 155.8 | 152.6 | 185.3 | 38.7 | 20 | 53 | 2.9 | 203 | 99.7 | 64.6 | 70.3 | 88.8 | 61.8 | 300.1
1608.2 | 1082.2 | -6.7 |  |  | 162.7 | 163.1 | 155.6 | 152.3 | 184.9 | 38.5 | 20 | 52.8 | 2.8 | 201.6 | 99.5 | 64.3 | 70.3 | 88.7 | 61.6 | 299
1609.2 | 1083.2 | -6.7 |  |  | 162.5 | 162.8 | 155.3 | 152 | 184.6 | 38.4 | 20 | 52.7 | 2.9 | 200.2 | 99.4 | 64.1 | 70.3 | 88 | 61.3 | 297.6
1610.2 | 1084.2 | -6.7 |  |  | 162.2 | 162.5 | 155 | 151.7 | 184.2 | 38.4 | 20 | 52.6 | 3 | 198.8 | 99.9 | 63.7 | 70.3 | 88.5 | 61 | 296
1611.2 | 1085.2 | -6.7 |  |  | 161.9 | 162.2 | 154.8 | 151.4 | 183.9 | 38.4 | 20 | 52.6 | 2.8 | 197 | 100.6 | 63.4 | 70.1 | 89.3 | 60.8 | 294.6
1612.2 | 1086.2 | -6.7 |  |  | 161.6 | 161.7 | 154.5 | 151.1 | 183.5 | 38.3 | 20 | 52.5 | 2.8 | 195.2 | 101 | 63.2 | 69.8 | 89.6 | 60.6 | 292.7
1613.2 | 1087.2 | -6.7 |  |  | 161.3 | 161.3 | 154.2 | 150.9 | 183.1 | 38.2 | 20 | 52.4 | 3 | 193.7 | 101.2 | 62.8 | 69.5 | 89.2 | 60.4 | 291.4
1614.2 | 1088.2 | -6.7 |  |  | 161 | 160.9 | 153.9 | 150.6 | 182.7 | 38.2 | 20 | 52.3 | 2.8 | 192.3 | 101.3 | 62.5 | 69.7 | 88.2 | 60 | 289.9
1615.2 | 1089.2 | -6.7 |  |  | 160.8 | 160.6 | 153.6 | 150.3 | 182.3 | 38.3 | 20 | 52.2 | 2.9 | 191 | 101.3 | 62.1 | 69.4 | 87.3 | 59.7 | 288.2
1616.2 | 1090.2 | -6.7 |  |  | 160.5 | 160.3 | 153.3 | 150.1 | 181.9 | 38.3 | 20 | 52.1 | 2.8 | 190 | 101 | 61.8 | 68.9 | 86.4 | 59.5 | 287
1617.2 | 1091.2 | -6.7 |  |  | 160.2 | 160 | 153 | 149.8 | 181.5 | 38.4 | 20 | 52 | 2.8 | 189.4 | 100.4 | 61.6 | 68.7 | 85.7 | 59.3 | 285.7
1618.2 | 1092.2 | -6.7 |  |  | 159.9 | 159.9 | 152.7 | 149.5 | 181.1 | 38.5 | 20 | 51.9 | 2.8 | 189 | 99.7 | 61.4 | 68.8 | 85.1 | 59 | 284.3
1619.2 | 1093.2 | -6.7 |  |  | 159.6 | 159.7 | 152.4 | 149.2 | 180.6 | 38.5 | 20 | 51.9 | 3 | 188.6 | 98.8 | 61.2 | 69 | 84.5 | 58.8 | 282.9
1620.2 | 1094.2 | -6.7 |  |  | 159.3 | 159.6 | 152.2 | 149 | 180.2 | 38.5 | 20 | 51.8 | 3 | 188.2 | 98.2 | 61 | 69.2 | 83.9 | 58.6 | 281.5
1621.2 | 1095.2 | -6.7 |  |  | 159 | 159.4 | 151.9 | 148.7 | 179.9 | 38.4 | 20 | 51.7 | 3.5 | 187.3 | 97.6 | 60.7 | 69.4 | 83.4 | 58.5 | 280.5
1622.2 | 1096.2 | -6.7 |  |  | 158.7 | 159.1 | 151.6 | 148.5 | 179.5 | 38.5 | 20 | 51.7 | 3.2 | 186.1 | 97 | 60.5 | 69.5 | 82.9 | 58.2 | 279.3
1623.2 | 1097.2 | -6.7 |  |  | 158.5 | 158.7 | 151.3 | 148.2 | 179.1 | 38.6 | 20 | 51.7 | 3 | 184.7 | 96.5 | 60.2 | 69.5 | 82.3 | 58 | 277.9
1624.2 | 1098.2 | -6.7 |  |  | 158.3 | 158.4 | 151.1 | 148 | 178.7 | 38.6 | 20 | 51.6 | 2.9 | 183.8 | 96 | 60.1 | 69.1 | 81.9 | 57.9 | 276.9
1625.2 | 1099.2 | -6.7 |  |  | 157.9 | 158.2 | 151 | 147.7 | 178.3 | 38.6 | 20 | 51.6 | 2.7 | 182.7 | 95.3 | 59.9 | 69.2 | 81.5 | 57.7 | 275.8
1626.2 | 1100.2 | -6.7 |  |  | 157.7 | 157.9 | 150.7 | 147.5 | 177.9 | 38.6 | 20 | 51.5 | 2.4 | 181.9 | 94.7 | 59.7 | 69.2 | 80.9 | 57.5 | 274.5
1627.2 | 1101.2 | -6.7 |  |  | 157.3 | 157.8 | 150.4 | 147.2 | 177.5 | 38.4 | 20 | 51.5 | 2.6 | 181.2 | 94.3 | 59.4 | 68.6 | 80.5 | 57.3 | 273.3
1628.2 | 1102.2 | -6.7 |  |  | 157 | 157.6 | 150.2 | 147 | 177.2 | 38.4 | 20 | 51.3 | 2.6 | 180.5 | 94.4 | 59.2 | 68.2 | 80 | 57.1 | 272.3
1629.2 | 1103.2 | -6.7 |  |  | 156.8 | 157.3 | 149.9 | 146.7 | 177 | 38.3 | 20 | 51.2 | 2.5 | 179.5 | 94.4 | 58.9 | 67.7 | 79.6 | 56.8 | 271.4
1630.2 | 1104.2 | -6.7 |  |  | 156.5 | 157.1 | 149.7 | 146.5 | 176.7 | 38.2 | 20.1 | 51.1 | 2.9 | 178.6 | 93.9 | 58.6 | 67.3 | 79.1 | 56.6 | 269.8
1631.2 | 1105.2 | -6.7 |  |  | 156.3 | 156.9 | 149.5 | 146.3 | 176.5 | 38.1 | 20 | 51 | 3 | 177.9 | 93.3 | 58.3 | 67.3 | 78.7 | 56.3 | 268.1
1632.2 | 1106.2 | -6.7 |  |  | 156.1 | 156.7 | 149.2 | 146.1 | 176.2 | 37.9 | 20 | 50.9 | 3 | 177.4 | 93.2 | 58.1 | 67.2 | 78.4 | 56.1 | 266.7
1633.2 | 1107.2 | -6.7 |  |  | 155.3 | 156.7 | 149.3 | 146 | 175.9 | 37.8 | 20.1 | 50.8 | 3.2 | 177.1 | 93.2 | 57.9 | 66.9 | 78 | 55.8 | 265.9
1634.2 | 1108.2 | -6.7 |  |  | 154.7 | 156.6 | 149.3 | 145.8 | 175.6 | 37.8 | 20.1 | 50.8 | 3.2 | 176.7 | 92.7 | 57.7 | 66.5 | 77.6 | 55.6 | 265
1635.2 | 1109.2 | -6.7 |  |  | 154.1 | 156.5 | 149.2 | 145.7 | 175.3 | 37.7 | 20.1 | 50.7 | 2.9 | 176.3 | 92.2 | 57.5 | 66.1 | 77.2 | 55.4 | 263.9
1636.2 | 1110.2 | -6.7 |  |  | 154.6 | 155.9 | 148.6 | 145.2 | 175 | 37.7 | 20.1 | 50.6 | 2.5 | 175.9 | 91.8 | 57.3 | 65.8 | 76.9 | 55.2 | 262.6
1637.2 | 1111.2 | -6.7 |  |  | 154.5 | 155.4 | 148.3 | 145 | 174.7 | 37.8 | 20.1 | 50.5 | 2.5 | 175.5 | 91.3 | 57.1 | 65.6 | 76.5 | 55.1 | 261.6
1638.2 | 1112.2 | -6.7 |  |  | 154.3 | 155 | 148 | 144.8 | 174.4 | 37.8 | 20.1 | 50.5 | 3 | 175 | 90.8 | 56.8 | 65.2 | 76.3 | 54.9 | 260.5
1639.2 | 1113.2 | -6.7 |  |  | 153.9 | 154.8 | 147.9 | 144.6 | 174 | 37.9 | 20.1 | 50.4 | 3.1 | 174.6 | 90.3 | 56.6 | 64.9 | 76 | 54.7 | 259.4
1640.2 | 1114.2 | -6.7 |  |  | 154 | 154.5 | 147.5 | 144.2 | 173.8 | 37.8 | 20.1 | 50.3 | 3.7 | 174.1 | 89.7 | 56.3 | 64.8 | 75.7 | 54.5 | 258.3
1641.2 | 1115.2 | -6.7 |  |  | 154 | 154.2 | 147.1 | 143.9 | 173.5 | 37.6 | 20.1 | 50.2 | 3.4 | 173.7 | 89.4 | 56.1 | 64.6 | 75.3 | 54.3 | 257.3
1642.2 | 1116.2 | -6.7 |  |  | 152.2 | 154.7 | 148 | 144.3 | 173 | 37.6 | 20.1 | 50.2 | 3.1 | 173 | 89.1 | 55.9 | 64.4 | 74.9 | 54 | 256.5
1643.2 | 1117.2 | -6.7 |  |  | 154 | 153.8 | 146.6 | 143.5 | 172.9 | 37.3 | 20.1 | 50.2 | 3.4 | 172.7 | 88.5 | 55.8 | 63.8 | 74.7 | 54 | 255.2
1644.2 | 1118.2 | -6.7 |  |  | 153.9 | 153.6 | 146.4 | 143.3 | 172.6 | 37.3 | 20.1 | 50.2 | 3.7 | 172.5 | 88 | 55.7 | 63.9 | 74.6 | 53.9 | 254.2
1645.2 | 1119.2 | -6.7 |  |  | 152.6 | 153.8 | 146.9 | 143.6 | 172.2 | 37.2 | 20.1 | 50.2 | 3.1 | 172.2 | 87.7 | 55.6 | 64.2 | 74.4 | 53.7 | 253.7
1646.2 | 1120.2 | -6.7 |  |  | 153.6 | 153.2 | 145.9 | 143 | 172 | 37 | 20.1 | 50.2 | 3.5 | 171.5 | 87.7 | 55.4 | 64.2 | 74.3 | 53.7 | 252.3
1647.2 | 1121.2 | -6.7 |  |  | 152.9 | 153.2 | 145.9 | 142.9 | 171.7 | 37 | 20.1 | 50.2 | 3.6 | 170.2 | 87.4 | 55.1 | 64.1 | 74 | 53.4 | 251.3
1648.2 | 1122.2 | -6.7 |  |  | 152 | 153.4 | 146.2 | 142.9 | 171.4 | 37.1 | 20.1 | 50.2 | 3.8 | 169 | 87.1 | 54.9 | 63.7 | 73.6 | 53.1 | 250.3
1649.2 | 1123.2 | -6.7 |  |  | 152.8 | 152.7 | 145.3 | 142.4 | 171.2 | 37.1 | 20.1 | 50.1 | 3.8 | 167.9 | 86.6 | 54.6 | 63.2 | 73.3 | 53 | 248.6
1650.2 | 1124.2 | -6.7 |  |  | 152 | 152.5 | 145.4 | 142.3 | 170.9 | 37.3 | 20.1 | 50 | 3.4 | 167.3 | 86.2 | 54.5 | 62.9 | 73.1 | 52.8 | 247.6
1651.2 | 1125.2 | -6.7 |  |  | 151.9 | 152.1 | 145.2 | 142.1 | 170.7 | 37.3 | 20.1 | 49.9 | 3 | 166.5 | 85.6 | 54.3 | 62.8 | 72.8 | 52.5 | 246.3
1652.2 | 1126.2 | -6.7 |  |  | 152.2 | 151.6 | 144.7 | 141.7 | 170.4 | 37.4 | 20.1 | 49.9 | 3.9 | 165.8 | 84.9 | 54.1 | 62.8 | 72.6 | 52.4 | 244.7
1653.2 | 1127.2 | -6.7 |  |  | 152 | 151.4 | 144.5 | 141.5 | 170.2 | 37.4 | 20.1 | 49.7 | 4.4 | 165.1 | 84.3 | 54 | 62.8 | 72.5 | 52.2 | 243.5
1654.2 | 1128.2 | -6.7 |  |  | 151.9 | 151.3 | 144.3 | 141.3 | 169.9 | 37.5 | 20.1 | 49.6 | 3.8 | 164.7 | 83.8 | 53.9 | 62.7 | 72.3 | 52.1 | 242.7
1655.2 | 1129.2 | -6.7 |  |  | 151.6 | 151.2 | 144.1 | 141.1 | 169.7 | 37.4 | 20.1 | 49.5 | 4 | 164.2 | 83.3 | 53.7 | 62.4 | 72.1 | 52 | 242.2
1656.2 | 1130.2 | -6.7 |  |  | 151.4 | 151 | 143.9 | 140.9 | 169.5 | 37.3 | 20.1 | 49.4 | 3.7 | 163.7 | 82.7 | 53.6 | 62.2 | 71.8 | 51.8 | 241.6
1657.2 | 1131.2 | -6.7 |  |  | 151.2 | 150.7 | 143.7 | 140.6 | 169.2 | 37.1 | 20.1 | 49.3 | 3.3 | 163.1 | 82.2 | 53.5 | 62.1 | 71.6 | 51.7 | 241.1
1658.2 | 1132.2 | -6.7 |  |  | 150.9 | 150.4 | 143.6 | 140.4 | 168.9 | 37.1 | 20.1 | 49.2 | 3 | 162.4 | 81.9 | 53.4 | 61.7 | 71.3 | 51.6 | 240.6
1659.2 | 1133.2 | -6.7 |  |  | 149.9 | 150.4 | 144 | 140.5 | 168.6 | 37.1 | 20.1 | 49.1 | 3 | 161.6 | 81.6 | 53.3 | 61.6 | 70.9 | 51.5 | 240.3
1660.2 | 1134.2 | -6.7 |  |  | 150.6 | 149.7 | 143.2 | 140 | 168.4 | 37 | 20.1 | 49 | 3.2 | 161 | 81.4 | 53.2 | 61.4 | 70.6 | 51.4 | 239
1661.2 | 1135.2 | -6.7 |  |  | 150.4 | 149.5 | 143 | 139.8 | 168.1 | 37 | 20.1 | 49 | 3.7 | 160.6 | 81.2 | 53 | 61.1 | 70.2 | 51.3 | 237.9
1662.2 | 1136.2 | -6.7 |  |  | 150 | 149.4 | 142.9 | 139.8 | 167.8 | 37 | 20.1 | 48.9 | 3.8 | 159.5 | 81.1 | 52.8 | 60.8 | 69.8 | 51.2 | 237
1663.2 | 1137.2 | -6.7 |  |  | 150 | 149.2 | 142.5 | 139.5 | 167.6 | 36.9 | 20.1 | 48.8 | 3.3 | 158.6 | 81.1 | 52.6 | 60.5 | 69.5 | 51.1 | 236
1664.2 | 1138.2 | -6.7 |  |  | 149.4 | 149.2 | 142.5 | 139.5 | 167.3 | 36.7 | 20.1 | 48.8 | 3.1 | 157.7 | 80.9 | 52.5 | 60.3 | 69.6 | 50.9 | 235.5
1665.2 | 1139.2 | -6.7 |  |  | 149.3 | 149 | 142.3 | 139.2 | 167.1 | 36.6 | 20.1 | 48.7 | 3.3 | 156.9 | 80.5 | 52.4 | 60 | 69.5 | 50.8 | 234.9
1666.2 | 1140.2 | -6.7 |  |  | 149.3 | 148.7 | 141.9 | 138.9 | 166.9 | 36.5 | 20.1 | 48.6 | 3.5 | 156 | 80.7 | 52.2 | 59.7 | 69.2 | 50.8 | 234
1667.2 | 1141.2 | -6.7 |  |  | 148.3 | 148.7 | 142.3 | 138.9 | 166.5 | 36.4 | 20.1 | 48.5 | 3.2 | 155.3 | 80.9 | 52.1 | 59.7 | 68.9 | 50.5 | 233.2
1668.2 | 1142.2 | -6.7 |  |  | 148.6 | 148.3 | 141.8 | 138.6 | 166.3 | 36.3 | 20.1 | 48.4 | 2.8 | 154.7 | 80.9 | 51.9 | 59.6 | 68.7 | 50.4 | 232
1669.2 | 1143.2 | -6.7 |  |  | 148.8 | 147.9 | 141.3 | 138.3 | 166 | 36.2 | 20.1 | 48.3 | 2.9 | 153.9 | 81 | 51.7 | 59.9 | 68.4 | 50.4 | 230.7
1670.2 | 1144.2 | -6.7 |  |  | 148.2 | 147.9 | 141.3 | 138.3 | 165.7 | 36.2 | 20.2 | 48.2 | 3.2 | 152.5 | 81.1 | 51.5 | 60.1 | 68.2 | 50.2 | 229.7
1671.2 | 1145.2 | -6.7 |  |  | 148.4 | 147.5 | 140.9 | 138 | 165.5 | 36.2 | 20.2 | 48.1 | 3.2 | 152.3 | 81.3 | 51.3 | 60 | 67.8 | 50.1 | 228.6
1672.2 | 1146.2 | -6.7 |  |  | 148.1 | 147.3 | 140.7 | 137.9 | 165.2 | 36.2 | 20.2 | 48.1 | 3.6 | 151.9 | 81.8 | 51.1 | 59.7 | 67.5 | 49.9 | 227.2
1673.2 | 1147.2 | -6.7 |  |  | 147.8 | 147.3 | 140.6 | 137.7 | 165 | 36 | 20.2 | 48 | 3.3 | 151.2 | 81.8 | 50.9 | 59.6 | 67.1 | 49.7 | 226.3
1674.2 | 1148.2 | -6.7 |  |  | 147.7 | 147.1 | 140.3 | 137.5 | 164.8 | 36.2 | 20.2 | 47.9 | 3.3 | 150 | 81.5 | 50.8 | 59.6 | 66.8 | 49.6 | 225.4
1675.2 | 1149.2 | -6.7 |  |  | 147.6 | 147 | 140.1 | 137.3 | 164.6 | 36.4 | 20.2 | 47.9 | 3.2 | 149.5 | 81.3 | 50.7 | 59.6 | 66.6 | 49.5 | 224.4
1676.2 | 1150.2 | -6.7 |  |  | 147.4 | 146.8 | 140 | 137.1 | 164.4 | 36.5 | 20.2 | 47.8 | 3.1 | 149.6 | 80.8 | 50.5 | 59.3 | 66.4 | 49.4 | 223.3
1677.2 | 1151.2 | -6.7 |  |  | 147.2 | 146.6 | 139.8 | 136.9 | 164.2 | 36.6 | 20.2 | 47.7 | 2.8 | 149.3 | 80.5 | 50.4 | 59.1 | 66.2 | 49.2 | 222.4
1678.2 | 1152.2 | -6.7 |  |  | 147.1 | 146.4 | 139.6 | 136.7 | 164 | 36.8 | 20.2 | 47.7 | 2.7 | 148.8 | 80.3 | 50.3 | 58.9 | 65.9 | 49.1 | 221.7
1679.2 | 1153.2 | -6.7 |  |  | 146.9 | 146.2 | 139.4 | 136.5 | 163.8 | 36.8 | 20.2 | 47.6 | 3.3 | 148.8 | 80.2 | 50.2 | 58.6 | 65.7 | 49 | 221
1680.2 | 1154.2 | -6.7 |  |  | 146.6 | 146 | 139.3 | 136.4 | 163.6 | 36.7 | 20.2 | 47.5 | 3 | 148.6 | 79.9 | 50.1 | 58.3 | 65.6 | 48.9 | 220
1681.2 | 1155.2 | -6.7 |  |  | 146.5 | 145.9 | 139.1 | 136.2 | 163.4 | 36.6 | 20.2 | 47.5 | 2.7 | 147.4 | 79.7 | 49.9 | 58 | 65.6 | 48.8 | 219
1682.2 | 1156.2 | -6.7 |  |  | 146.3 | 145.8 | 138.9 | 136 | 163.2 | 36.7 | 20.2 | 47.4 | 2.7 | 146.9 | 79.6 | 49.7 | 57.9 | 65.4 | 48.6 | 217.9
1683.2 | 1157.2 | -6.7 |  |  | 146.1 | 145.7 | 138.7 | 135.8 | 163.1 | 36.8 | 20.2 | 47.4 | 2.6 | 146.8 | 79.6 | 49.6 | 57.5 | 65.3 | 48.5 | 217.1
1684.2 | 1158.2 | -6.7 |  |  | 145.8 | 145.4 | 138.5 | 135.6 | 162.9 | 36.9 | 20.2 | 47.3 | 2.7 | 146 | 79.7 | 49.4 | 57.2 | 65.1 | 48.3 | 216.4
1685.2 | 1159.2 | -6.7 |  |  | 145.6 | 145.1 | 138.3 | 135.4 | 162.7 | 37 | 20.2 | 47.3 | 2.5 | 145.2 | 79.9 | 49.2 | 57.3 | 65.2 | 48.2 | 215.9
1686.2 | 1160.2 | -6.7 |  |  | 145.4 | 144.9 | 138.2 | 135.3 | 162.5 | 37 | 20.2 | 47.2 | 2.4 | 144.6 | 80.1 | 49.1 | 57.3 | 65.3 | 48 | 215.4
1687.2 | 1161.2 | -6.7 |  |  | 145 | 144.8 | 138.2 | 135.1 | 162.2 | 36.9 | 20.2 | 47.1 | 2.1 | 143.4 | 80.4 | 48.9 | 57 | 64.9 | 47.8 | 214.6
1688.2 | 1162.2 | -6.7 |  |  | 145.1 | 144.5 | 137.9 | 134.9 | 162 | 36.7 | 20.2 | 47 | 2.2 | 143.3 | 80.7 | 48.7 | 56.8 | 64.5 | 47.7 | 213.6
1689.2 | 1163.2 | -6.7 |  |  | 144.9 | 144.2 | 137.7 | 134.7 | 161.8 | 36.6 | 20.2 | 46.9 | 2.7 | 142.8 | 80.9 | 48.6 | 56.8 | 64.2 | 47.7 | 213.1
1690.2 | 1164.2 | -6.7 |  |  | 144.7 | 144 | 137.6 | 134.5 | 161.6 | 36.4 | 20.2 | 46.8 | 2.6 | 142 | 81.1 | 48.5 | 56.5 | 63.8 | 47.6 | 212.4
1691.2 | 1165.2 | -6.7 |  |  | 144.5 | 143.8 | 137.4 | 134.4 | 161.4 | 36.2 | 20.2 | 46.8 | 2.3 | 141.6 | 81.1 | 48.4 | 56.3 | 63.5 | 47.5 | 211.4
1692.2 | 1166.2 | -6.7 |  |  | 144.3 | 143.7 | 137.2 | 134.2 | 161.2 | 36.1 | 20.2 | 46.8 | 2.5 | 141.2 | 80.9 | 48.3 | 56.2 | 63.1 | 47.3 | 210.4
1693.2 | 1167.2 | -6.7 |  |  | 144.1 | 143.5 | 137 | 134.1 | 161 | 36 | 20.2 | 46.7 | 1.9 | 140.8 | 80.7 | 48.1 | 56 | 62.9 | 47.2 | 209.3
1694.2 | 1168.2 | -6.7 |  |  | 143.9 | 143.3 | 136.9 | 133.9 | 160.8 | 35.9 | 20.2 | 46.7 | 2 | 140.5 | 80.3 | 48.1 | 55.8 | 62.7 | 47.2 | 208.3
1695.2 | 1169.2 | -6.7 |  |  | 143.7 | 143.2 | 136.7 | 133.8 | 160.7 | 35.9 | 20.2 | 46.7 | 1.9 | 140.1 | 79.9 | 48.1 | 56 | 62.6 | 47.2 | 207.5
1696.2 | 1170.2 | -6.7 |  |  | 143.5 | 143.1 | 136.6 | 133.7 | 160.5 | 35.9 | 20.2 | 46.6 | 2.3 | 139.8 | 79.6 | 48 | 56 | 62.4 | 47.2 | 207.1
1697.2 | 1171.2 | -6.7 |  |  | 143.5 | 143 | 136.3 | 133.5 | 160.4 | 35.9 | 20.2 | 46.6 | 2.5 | 139.4 | 79.5 | 47.9 | 56 | 62.2 | 47.1 | 206.2
1698.2 | 1172.2 | -6.7 |  |  | 143.2 | 142.8 | 136.2 | 133.4 | 160.3 | 35.8 | 20.2 | 46.6 | 2.8 | 139 | 79.1 | 47.9 | 55.9 | 62 | 47.1 | 205.3
1699.2 | 1173.2 | -6.7 |  |  | 143.1 | 142.7 | 136 | 133.2 | 160.2 | 35.8 | 20.2 | 46.6 | 2.9 | 138.5 | 78.4 | 47.8 | 55.9 | 61.8 | 47 | 204.4
1700.2 | 1174.2 | -6.7 |  |  | 142.9 | 142.6 | 135.9 | 133.1 | 160.1 | 35.7 | 20.2 | 46.6 | 2.6 | 138.1 | 78 | 47.8 | 56.1 | 61.7 | 46.9 | 203.5
1701.2 | 1175.2 | -6.7 |  |  | 142.8 | 142.4 | 135.7 | 133 | 160 | 35.6 | 20.2 | 46.6 | 2.9 | 137.8 | 77.6 | 47.7 | 56.2 | 61.7 | 46.9 | 203
1702.2 | 1176.2 | -6.7 |  |  | 142.6 | 142.2 | 135.6 | 132.8 | 159.9 | 35.5 | 20.2 | 46.5 | 2.7 | 137.7 | 77.2 | 47.7 | 56.4 | 61.6 | 46.8 | 202.4
1703.2 | 1177.2 | -6.7 |  |  | 142.5 | 142 | 135.4 | 132.6 | 159.7 | 35.4 | 20.2 | 46.5 | 2.6 | 137.6 | 76.8 | 47.6 | 56.6 | 61.5 | 46.7 | 201.7
1704.2 | 1178.2 | -6.7 |  |  | 142.3 | 141.8 | 135.3 | 132.5 | 159.5 | 35.3 | 20.2 | 46.4 | 2.4 | 137.5 | 76.4 | 47.6 | 56.8 | 61.3 | 46.7 | 201.1
1705.2 | 1179.2 | -6.7 |  |  | 142.1 | 141.7 | 135.1 | 132.3 | 159.3 | 35.1 | 20.2 | 46.4 | 2.5 | 137.1 | 76.2 | 47.4 | 56.8 | 61.1 | 46.6 | 200.4
1706.2 | 1180.2 | -6.7 |  |  | 142 | 141.6 | 134.9 | 132.1 | 159.1 | 35 | 20.2 | 46.4 | 2.7 | 136.4 | 75.7 | 47.3 | 56.9 | 60.9 | 46.5 | 199.3
1707.2 | 1181.2 | -6.7 |  |  | 141.8 | 141.4 | 134.8 | 131.9 | 158.9 | 35 | 20.2 | 46.4 | 2.7 | 136.1 | 75.2 | 47.3 | 56.8 | 60.6 | 46.4 | 198.5
1708.2 | 1182.2 | -6.7 |  |  | 141.6 | 141.3 | 134.7 | 131.8 | 158.7 | 35 | 20.2 | 46.4 | 2.4 | 135.8 | 74.6 | 47.2 | 56.7 | 60.5 | 46.3 | 197.8
1709.2 | 1183.2 | -6.7 |  |  | 141.3 | 141.2 | 134.6 | 131.6 | 158.5 | 35 | 20.2 | 46.3 | 2.3 | 135.6 | 74.1 | 47.1 | 56.9 | 60.4 | 46.2 | 196.8
1710.2 | 1184.2 | -6.7 |  |  | 141.2 | 141.2 | 134.4 | 131.4 | 158.4 | 34.9 | 20.2 | 46.3 | 2.4 | 135.4 | 73.7 | 47.1 | 56.9 | 60.4 | 46.2 | 196.3
1711.2 | 1185.2 | -6.7 |  |  | 141.2 | 141.2 | 134.2 | 131.3 | 158.2 | 34.8 | 20.2 | 46.3 | 2.4 | 135.1 | 73.5 | 46.9 | 56.6 | 60.4 | 46 | 195.6
1712.2 | 1186.2 | -6.7 |  |  | 141.1 | 141.1 | 134.1 | 131.1 | 158 | 34.7 | 20.2 | 46.2 | 2.5 | 134.6 | 73.3 | 46.9 | 56.3 | 60.5 | 45.9 | 195
1713.2 | 1187.2 | -6.7 |  |  | 141.1 | 140.9 | 133.9 | 131 | 157.8 | 34.6 | 20.2 | 46.2 | 2.6 | 134 | 73.2 | 46.9 | 56 | 60.2 | 45.9 | 194.8
1714.2 | 1188.2 | -6.7 |  |  | 140.9 | 140.7 | 133.7 | 130.9 | 157.7 | 34.5 | 20.2 | 46.1 | 2.6 | 132.5 | 73.4 | 46.8 | 55.7 | 60.2 | 45.8 | 194.2
1715.2 | 1189.2 | -6.7 |  |  | 140.7 | 140.5 | 133.6 | 130.8 | 157.5 | 34.4 | 20.2 | 46 | 2.7 | 131.6 | 73.6 | 46.7 | 55.4 | 60.4 | 45.7 | 193.5
1716.2 | 1190.2 | -6.7 |  |  | 140.6 | 140.2 | 133.5 | 130.7 | 157.3 | 34.3 | 20.2 | 46 | 2.8 | 130.5 | 74 | 46.6 | 55.2 | 60.6 | 45.7 | 193
1717.2 | 1191.2 | -6.7 |  |  | 140.4 | 140.1 | 133.5 | 130.5 | 157.1 | 34.3 | 20.2 | 46 | 2.7 | 129.4 | 74.5 | 46.4 | 55.1 | 60.5 | 45.5 | 192.6
1718.2 | 1192.2 | -6.7 |  |  | 140.1 | 139.9 | 133.3 | 130.4 | 156.9 | 34.3 | 20.3 | 45.9 | 2.7 | 128.8 | 74.8 | 46.3 | 55.2 | 60.2 | 45.5 | 191.9
1719.2 | 1193.2 | -6.7 |  |  | 139.9 | 139.7 | 133.2 | 130.3 | 156.7 | 34.4 | 20.3 | 45.9 | 2.5 | 128.5 | 74.9 | 46.2 | 55.3 | 60 | 45.3 | 191.2
1720.2 | 1194.2 | -6.7 |  |  | 139.7 | 139.5 | 133 | 130.1 | 156.5 | 34.6 | 20.3 | 45.9 | 2.5 | 127.7 | 75 | 46.1 | 55 | 59.8 | 45.2 | 190.5
1721.2 | 1195.2 | -6.7 |  |  | 139.6 | 139.3 | 132.8 | 129.9 | 156.3 | 34.6 | 20.3 | 45.8 | 2.4 | 127 | 75.1 | 46 | 54.7 | 59.7 | 45.1 | 189.8
1722.2 | 1196.2 | -6.7 |  |  | 139.4 | 139.2 | 132.6 | 129.8 | 156.1 | 34.6 | 20.3 | 45.8 | 2.3 | 126.8 | 75.2 | 45.9 | 54.5 | 59.8 | 45.1 | 188.8
1723.2 | 1197.2 | -6.7 |  |  | 139.4 | 139 | 132.5 | 129.6 | 155.9 | 34.7 | 20.3 | 45.7 | 2.4 | 126.3 | 75.1 | 45.8 | 54.5 | 59.6 | 45 | 187.9
1724.2 | 1198.2 | -6.7 |  |  | 139.3 | 138.8 | 132.3 | 129.5 | 155.7 | 34.8 | 20.3 | 45.5 | 2.3 | 125.8 | 75 | 45.7 | 54.7 | 59.3 | 44.8 | 187
1725.2 | 1199.2 | -6.7 |  |  | 139.2 | 138.5 | 132.2 | 129.5 | 155.5 | 34.9 | 20.3 | 45.5 | 2.4 | 125.9 | 74.6 | 45.7 | 54.4 | 59 | 44.8 | 186.5
1726.2 | 1200.2 | -6.7 |  |  | 139 | 138.3 | 132.1 | 129.5 | 155.4 | 34.9 | 20.3 | 45.5 | 2.5 | 125.8 | 74.1 | 45.6 | 54.2 | 58.8 | 44.6 | 185.4
1727.2 | 1201.2 | -6.7 |  |  | 138.9 | 138.2 | 131.9 | 129.4 | 155.2 | 34.8 | 20.3 | 45.4 | 2.4 | 125.6 | 73.6 | 45.5 | 54 | 58.6 | 44.6 | 184.5
1728.2 | 1202.2 | -6.7 |  |  | 138.7 | 138.2 | 131.8 | 129.2 | 155 | 34.8 | 20.3 | 45.3 | 2.2 | 125.4 | 73.2 | 45.4 | 54 | 58.4 | 44.6 | 184
1729.2 | 1203.2 | -6.7 |  |  | 138.4 | 138 | 131.7 | 129 | 154.9 | 34.8 | 20.3 | 45.2 | 2.2 | 125.4 | 72.9 | 45.3 | 53.8 | 58.1 | 44.5 | 183.5
1730.2 | 1204.2 | -6.7 |  |  | 138.3 | 137.9 | 131.5 | 128.9 | 154.7 | 34.9 | 20.3 | 45.2 | 2.2 | 125.3 | 72.7 | 45.2 | 53.6 | 57.9 | 44.5 | 182.7
1731.2 | 1205.2 | -6.7 |  |  | 138.1 | 137.8 | 131.4 | 128.7 | 154.6 | 35 | 20.3 | 45.2 | 2.2 | 125.3 | 72.2 | 45.1 | 53.5 | 57.8 | 44.4 | 181.8
1732.2 | 1206.2 | -6.7 |  |  | 137.9 | 137.6 | 131.2 | 128.6 | 154.5 | 35.2 | 20.3 | 45.1 | 2.3 | 125.1 | 71.7 | 45.1 | 53.5 | 57.6 | 44.3 | 181.2
1733.2 | 1207.2 | -6.7 |  |  | 137.8 | 137.4 | 131.1 | 128.5 | 154.3 | 35.2 | 20.3 | 45.1 | 2.3 | 124.8 | 71.4 | 45 | 53.3 | 57.5 | 44.3 | 180.8
1734.2 | 1208.2 | -6.7 |  |  | 137.7 | 137.3 | 131 | 128.3 | 154.2 | 35.1 | 20.3 | 45 | 2.2 | 123.9 | 71 | 44.9 | 53.1 | 57.5 | 44.2 | 180.3
1735.2 | 1209.2 | -6.7 |  |  | 137.6 | 137.3 | 130.8 | 128.2 | 154.1 | 35 | 20.3 | 44.9 | 2.4 | 123.2 | 70.6 | 44.8 | 53.1 | 57.4 | 44.1 | 179.7
1736.2 | 1210.2 | -6.7 |  |  | 137.4 | 137.3 | 130.7 | 128 | 153.9 | 35 | 20.3 | 44.8 | 2.2 | 122.5 | 70.2 | 44.8 | 53 | 57.3 | 44 | 179.1
1737.2 | 1211.2 | -6.7 |  |  | 137.2 | 137.2 | 130.6 | 127.9 | 153.7 | 35 | 20.3 | 44.8 | 2.3 | 122.5 | 69.8 | 44.7 | 52.9 | 57.1 | 44 | 178.5
1738.2 | 1212.2 | -6.7 |  |  | 137.1 | 137.2 | 130.5 | 127.7 | 153.5 | 34.9 | 20.3 | 44.7 | 2.4 | 122.6 | 69.5 | 44.7 | 52.8 | 57 | 43.9 | 178.2
1739.2 | 1213.2 | -6.7 |  |  | 136.9 | 137 | 130.4 | 127.6 | 153.3 | 34.8 | 20.3 | 44.7 | 2.6 | 122.5 | 69.1 | 44.6 | 52.8 | 57 | 43.9 | 177.6
1740.2 | 1214.2 | -6.7 |  |  | 136.7 | 136.8 | 130.2 | 127.5 | 153.2 | 34.8 | 20.3 | 44.6 | 2.6 | 122.3 | 68.8 | 44.6 | 52.7 | 56.9 | 43.8 | 177.1
1741.2 | 1215.2 | -6.7 |  |  | 136.6 | 136.6 | 130.1 | 127.4 | 153 | 34.8 | 20.3 | 44.6 | 2.5 | 121.7 | 68.7 | 44.6 | 52.5 | 56.7 | 43.8 | 176.7
1742.2 | 1216.2 | -6.7 |  |  | 136.5 | 136.5 | 129.9 | 127.3 | 152.8 | 34.9 | 20.3 | 44.6 | 2.6 | 120.8 | 68.6 | 44.6 | 52.4 | 56.7 | 43.8 | 176.6
1743.2 | 1217.2 | -6.6 |  |  | 136.3 | 136.4 | 129.8 | 127.2 | 152.6 | 34.8 | 20.3 | 44.6 | 2.6 | 120.1 | 68.6 | 44.6 | 52.2 | 56.5 | 43.8 | 176.2
1744.2 | 1218.2 | -6.7 |  |  | 136.2 | 136.3 | 129.6 | 127.2 | 152.5 | 34.7 | 20.3 | 44.6 | 2.4 | 119.5 | 69 | 44.5 | 52.1 | 56.4 | 43.8 | 175.5
1745.2 | 1219.2 | -6.7 |  |  | 136.1 | 136.2 | 129.4 | 127.1 | 152.3 | 34.7 | 20.3 | 44.6 | 2.7 | 118.8 | 69.1 | 44.5 | 52 | 56.3 | 43.8 | 175.1
1746.2 | 1220.2 | -6.6 |  |  | 136 | 135.9 | 129.3 | 127 | 152.2 | 34.7 | 20.3 | 44.6 | 2.9 | 118.3 | 69 | 44.4 | 52 | 56.2 | 43.8 | 174.7
1747.2 | 1221.2 | -6.6 |  |  | 136 | 135.7 | 129.2 | 126.9 | 152.1 | 34.7 | 20.3 | 44.6 | 2.4 | 118.1 | 68.8 | 44.4 | 52 | 56.1 | 43.7 | 173.7
1748.2 | 1222.2 | -6.6 |  |  | 136 | 135.5 | 129.1 | 126.7 | 151.9 | 34.8 | 20.3 | 44.6 | 2.3 | 117.9 | 68.8 | 44.3 | 52.3 | 56 | 43.6 | 172.9
1749.2 | 1223.2 | -6.7 |  |  | 135.8 | 135.4 | 128.9 | 126.5 | 151.8 | 34.9 | 20.3 | 44.6 | 2.4 | 117.7 | 68.9 | 44.1 | 52.4 | 55.9 | 43.5 | 171.9
1750.2 | 1224.2 | -6.7 |  |  | 135.6 | 135.3 | 128.8 | 126.4 | 151.6 | 35 | 20.3 | 44.5 | 2.4 | 117.4 | 68.8 | 44 | 52.4 | 55.7 | 43.4 | 171
1751.2 | 1225.2 | -6.7 |  |  | 135.5 | 135.3 | 128.7 | 126.3 | 151.5 | 35 | 20.3 | 44.5 | 2.3 | 117.2 | 68.8 | 43.9 | 52.1 | 55.5 | 43.3 | 170.3
1752.2 | 1226.2 | -6.7 |  |  | 135.3 | 135.2 | 128.5 | 126.3 | 151.3 | 35 | 20.3 | 44.4 | 2.3 | 117.2 | 68.5 | 43.9 | 51.9 | 55.4 | 43.3 | 169.8
1753.2 | 1227.2 | -6.7 |  |  | 135.1 | 135.1 | 128.5 | 126.1 | 151.2 | 35 | 20.3 | 44.4 | 2.4 | 117.2 | 68.1 | 43.8 | 51.8 | 55.3 | 43.1 | 169.3
1754.2 | 1228.2 | -6.6 |  |  | 135 | 135.1 | 128.4 | 126 | 151.1 | 34.9 | 20.3 | 44.3 | 2.2 | 117.3 | 67.8 | 43.6 | 51.6 | 55.3 | 43 | 168.5
1755.2 | 1229.2 | -6.7 |  |  | 134.9 | 135 | 128.2 | 125.8 | 150.9 | 34.7 | 20.3 | 44.3 | 2 | 117.3 | 67.6 | 43.6 | 51.4 | 55.3 | 42.9 | 167.8
1756.2 | 1230.2 | -6.7 |  |  | 134.7 | 134.8 | 128.1 | 125.6 | 150.8 | 34.5 | 20.3 | 44.2 | 2.1 | 117.3 | 67.3 | 43.5 | 51.2 | 55.2 | 42.9 | 167.4
1757.2 | 1231.2 | -6.7 |  |  | 134.5 | 134.7 | 128 | 125.5 | 150.7 | 34.5 | 20.3 | 44.2 | 2 | 117.3 | 66.9 | 43.4 | 51 | 55.1 | 42.8 | 166.9
1758.2 | 1232.2 | -6.7 |  |  | 134.4 | 134.7 | 127.9 | 125.3 | 150.5 | 34.5 | 20.3 | 44.1 | 2.3 | 117.1 | 66.5 | 43.4 | 50.9 | 55 | 42.8 | 166.4
1759.2 | 1233.2 | -6.7 |  |  | 134.3 | 134.5 | 127.8 | 125.2 | 150.4 | 34.4 | 20.4 | 44.1 | 2.4 | 116.8 | 66.2 | 43.4 | 50.7 | 54.9 | 42.7 | 166
1760.2 | 1234.2 | -6.7 |  |  | 134.2 | 134.4 | 127.7 | 125 | 150.3 | 34.2 | 20.4 | 44 | 2.5 | 116.6 | 65.9 | 43.5 | 50.7 | 54.9 | 42.7 | 165.5
1761.2 | 1235.2 | -6.7 |  |  | 134.1 | 134.3 | 127.6 | 124.9 | 150.1 | 34.2 | 20.4 | 44 | 2.1 | 116.4 | 65.7 | 43.5 | 50.9 | 54.9 | 42.7 | 165.2
1762.2 | 1236.2 | -6.7 |  |  | 134.1 | 134.2 | 127.4 | 124.7 | 149.9 | 34.2 | 20.4 | 43.9 | 2.4 | 116 | 65.5 | 43.5 | 51 | 54.9 | 42.7 | 164.7
1763.2 | 1237.2 | -6.7 |  |  | 133.9 | 134.1 | 127.3 | 124.6 | 149.8 | 34.3 | 20.4 | 43.8 | 2.5 | 115.6 | 65.2 | 43.5 | 51 | 54.8 | 42.7 | 164.3
1764.2 | 1238.2 | -6.7 |  |  | 133.8 | 134 | 127.2 | 124.5 | 149.6 | 34.4 | 20.4 | 43.8 | 2.6 | 114.9 | 65.1 | 43.5 | 50.8 | 54.7 | 42.7 | 163.6
1765.2 | 1239.2 | -6.7 |  |  | 133.6 | 133.9 | 127.1 | 124.4 | 149.5 | 34.4 | 20.4 | 43.7 | 2.8 | 114.6 | 65 | 43.5 | 50.7 | 54.6 | 42.7 | 163.2
1766.2 | 1240.2 | -6.7 |  |  | 133.5 | 133.8 | 127 | 124.3 | 149.3 | 34.3 | 20.4 | 43.7 | 2.7 | 114.3 | 65 | 43.5 | 50.7 | 54.5 | 42.6 | 162.9
1767.2 | 1241.2 | -6.7 |  |  | 133.3 | 133.6 | 126.9 | 124.2 | 149.1 | 34.3 | 20.4 | 43.6 | 2.6 | 114.1 | 65 | 43.4 | 51 | 54.5 | 42.6 | 162.4
1768.2 | 1242.2 | -6.7 |  |  | 133.2 | 133.5 | 126.8 | 124.1 | 148.9 | 34.2 | 20.4 | 43.6 | 2.4 | 114 | 64.8 | 43.4 | 51.2 | 54.4 | 42.6 | 161.9
1769.2 | 1243.2 | -6.7 |  |  | 133 | 133.4 | 126.7 | 124 | 148.8 | 34.1 | 20.4 | 43.6 | 2.6 | 113.8 | 64.5 | 43.2 | 51.3 | 54.3 | 42.5 | 161.5
1770.2 | 1244.2 | -6.7 |  |  | 132.9 | 133.3 | 126.5 | 123.9 | 148.6 | 34.1 | 20.4 | 43.6 | 2.5 | 113.7 | 64.4 | 43.2 | 51.6 | 54.3 | 42.5 | 161
1771.2 | 1245.2 | -6.7 |  |  | 132.8 | 133.2 | 126.4 | 123.8 | 148.5 | 34.2 | 20.4 | 43.6 | 2.6 | 113.5 | 64.3 | 43.1 | 51.5 | 54.2 | 42.4 | 160.3
1772.2 | 1246.2 | -6.7 |  |  | 132.7 | 133 | 126.2 | 123.7 | 148.3 | 34.3 | 20.4 | 43.5 | 2.5 | 113.3 | 64 | 43 | 51.4 | 54.2 | 42.3 | 159.8
1773.2 | 1247.2 | -6.7 |  |  | 132.6 | 132.9 | 126.1 | 123.6 | 148.2 | 34.3 | 20.4 | 43.5 | 2.1 | 113 | 64 | 42.9 | 51.3 | 54.2 | 42.2 | 159.3
1774.2 | 1248.2 | -6.7 |  |  | 132.5 | 132.8 | 125.9 | 123.5 | 148 | 34.2 | 20.4 | 43.4 | 2.3 | 112.3 | 64.1 | 42.8 | 51.3 | 54.3 | 42.1 | 158.8
1775.2 | 1249.2 | -6.7 |  |  | 132.3 | 132.7 | 125.8 | 123.4 | 147.9 | 34.1 | 20.4 | 43.3 | 2.3 | 112.1 | 64.1 | 42.7 | 51.3 | 54.5 | 42 | 158.2
1776.2 | 1250.2 | -6.7 |  |  | 132.2 | 132.5 | 125.7 | 123.3 | 147.7 | 34.1 | 20.4 | 43.2 | 2.2 | 111.8 | 64 | 42.6 | 51.2 | 54.2 | 42 | 157.6
1777.2 | 1251.2 | -6.7 |  |  | 132 | 132.4 | 125.6 | 123.2 | 147.6 | 33.9 | 20.4 | 43.2 | 2.4 | 111.5 | 64.1 | 42.6 | 51.2 | 54.1 | 41.9 | 157.4
1778.2 | 1252.2 | -6.7 |  |  | 131.9 | 132.2 | 125.5 | 123.2 | 147.5 | 33.9 | 20.4 | 43.1 | 2.7 | 111.4 | 64.2 | 42.5 | 51.3 | 54 | 41.9 | 156.7
1779.2 | 1253.2 | -6.7 |  |  | 131.9 | 132 | 125.4 | 123 | 147.4 | 33.8 | 20.4 | 43 | 2.9 | 111.2 | 64.2 | 42.4 | 51.3 | 53.8 | 41.8 | 155.9
1780.2 | 1254.2 | -6.7 |  |  | 131.9 | 131.9 | 125.3 | 122.9 | 147.2 | 33.7 | 20.4 | 43 | 2.8 | 111 | 64.2 | 42.3 | 51.2 | 53.5 | 41.7 | 155.4
1781.2 | 1255.2 | -6.7 |  |  | 131.9 | 131.8 | 125.1 | 122.7 | 147.1 | 33.5 | 20.4 | 42.9 | 3 | 111.1 | 64 | 42.3 | 51.1 | 53.3 | 41.7 | 154.7

## First Electrical Failures
First electrical failures observed for the two cables present extracted from the corresponding IRMS files
3/C Cable | [5 empty] | 7/C Cable
Time | Offset time | C4-Grnd | Time | Offset time | C1-C2 | Time | Offset time | C5-Grnd
30.8333 | -189.1667 | 242938 | 1 | -219 | 255237.9994 | 131.0833 | -88.9167 | 238838
184.6667 | -35.3333 | 242938 | 155 | -65 | 255237.9994 | 285.1667 | 65.1667 | 795.105
338.6667 | 118.6667 | 32.6236 | 309 | 89 | 255237.9994 | 439.0833 | 219.0833 | 0.67186
492.6667 | 272.6667 | 0.63194 | 463 | 243 | 0.9032 | 593.0833 | 373.0833 | 1.6565
646.6667 | 426.6667 | 0.63219 | 617 | 397 | 7.643 | 747 | 527 | 4.7974
800.6667 | 580.6667 | 1.0973 | 771 | 551 | 0.4582 | 901.0833 | 681.0833 | 0.64923
954.6667 | 734.6667 | 5.2636 | 924.5 | 704.5 | 0.74182 | 1055.0833 | 835.0833 | 6.5981
1108.6667 | 888.6667 | 9.688 | 1078.5 | 858.5 | 10.7977 | 1209 | 989 | 311.7391
1262.6667 | 1042.6667 | 6279.4864 | 1233 | 1013 | 11.7332 | 1363 | 1143 | 810.8659
Note: for 3/C cable, conductor 4 (C4) is the un-insulated drain wire so the first failure involving an insulated conductor is also shown.