## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Preliminary Test 3, 7/C Cable in Location A
Test conditions: Cable: 7-conductor, 12 AWG, PVC insulated, PVC jacketed, industrial grade control cable. (Item #1) Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: One cable temperature (see thermocouple map), air temperatures above and below the cable, and the cable tray rung temperature. Gas burner initiated: Following 208 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
208 | 0 | Ignited Gas Burner
268 | 60 | Conductor 2 shorts to ground at less than 100 ohms (28) | Initial failure is by conductor shorting to ground
285-289 | 77-81 | Conductors 5, 6 & 7 all short to ground at less than 100 ohms (69, 14 & 22) | Failures progress to additional shorts to ground and conductor-to-conductor shorts
300-303 | 92-95 | Conductor 5 shorts to conductors 6 & 7 (364 & 68)
306 | 98 | Conductor 6 shorts to conductor 7 at less than 100 ohms (13)
404-418 | 196-210 | Conductor 1 shorts to conductors 2, 3, 4, 5, 6 & 7 at less than 100 ohms (1, 1, 1, 9, 1 & 21)
410 | 202 | Conductor 1 shorts to ground at less than 100 ohms (1)
420-432 | 212-224 | Conductor 2 shorts to conductors 3, 4, 5, 6 & 7 at less than 100 ohms (9, 9, 1, 4 & 1)
430-435 | 222-227 | Conductors 3 & 4 both short to ground at less than 100 ohms (1 & 1) | All conductors have shorted to external ground.
435-443 | 227-235 | Conductor 3 shorts to conductors 4, 5, 6 & 7 at less than 100 ohms (1, 10, 4 & 1)
444 | 236 | Extinguished Gas Burner
446-451 | 238-243 | Conductor 4 shorts to conductors 5, 6 & 7 at less than 100 ohms (4, 1 & 16)
454 | 246 | The existing short between conductors 5 & 6 decreases to less than 100 ohms (1) | All conductors have shorted together at less than 100 ohms
Additional Observations

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable = | PVC, 7/C | (Item #1)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| A4 | = | Within cable just below cable jacket, center position
| A5 | = | Air temperature above cable
| A6 | = | Air temperature below cable

## C-C Individuals
Conductor to Conductor Resistances
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38
PVC | 7-C | Tray A
0 | 250 kW
Burner Time | C1-2 | Burner Time | C1-3 | Burner Time | C1-4 | Burner Time | C1-5 | Burner Time | C1-6 | Burner Time | C1-7 | Burner Time | C2-3 | Burner Time | C2-4 | Burner Time | C2-5 | Burner Time | C2-6 | Burner Time | C2-7 | Burner Time | C3-4 | Burner Time | C3-5 | Burner Time | C3-6 | Burner Time | C3-7 | Burner Time | C4-5 | Burner Time | C4-6 | Burner Time | C4-7 | Burner Time | C5-6 | Burner Time | C5-7 | Burner Time | C6-7 | Burner Time | Minimums
-112.5 | 257237.9994 | -109.5 | 256537.9994 | -106.5 | 262637.9994 | -104 | 252137.9994 | -101 | 261837.9994 | -98.5 | 247037.9994 | -95.5 | 223737.9994 | -92.5 | 249637.9994 | -90 | 238837.9994 | -87 | 234137.9994 | -84.5 | 239537.9994 | -81.5 | 249537.9994 | -78.5 | 257737.9994 | -76 | 244037.9994 | -73 | 260537.9994 | -70.5 | 235737.9994 | -67.5 | 255037.9994 | -64.5 | 253837.9994 | -62 | 249037.9994 | -59 | 253137.9994 | -56.5 | 244237.9994 | -112.5 | 223737.9994
41.5 | 257237.9994 | 44.5 | 256537.9994 | 47 | 262637.9994 | 50 | 252137.9994 | 52.5 | 261837.9994 | 55.5 | 247037.9994 | 58.5 | 223737.9994 | 61.5 | 249637.9994 | 64 | 238837.9994 | 67 | 53914.973 | 69.5 | 52616.0344 | 72.5 | 249537.9994 | 75.5 | 257737.9994 | 78 | 27026.4389 | 81 | 260537.9994 | 83.5 | 235737.9994 | 86.5 | 255037.9994 | 89.5 | 126868.9988 | 92 | 364.4825 | 95 | 67.9096 | 97.5 | 12.9242 | 41.5 | 12.9242
195.5 | 0.92046 | 198.5 | 0.91442 | 201.5 | 0.96667 | 204 | 9.3864 | 206.5 | 0.95986 | 209.5 | 20.8072 | 212 | 9.0807 | 215 | 8.9261 | 218 | 0.75845 | 221 | 3.5351 | 223.5 | 0.76476 | 226.5 | 1.334 | 229.5 | 9.8178 | 232 | 4.2308 | 234.5 | 0.94876 | 237.5 | 4.2037 | 240.5 | 0.90147 | 243 | 15.8612 | 246 | 0.84917 | 249 | 1.6105 | 251.5 | 0.80678 | 195.5 | 0.75845
349.5 | 805.1408 | 352.5 | 6711.2261 | 355 | 5432.1824 | 358 | 383.3077 | 361 | 11.4284 | 363.5 | 0.056547 | 366.5 | 15.2129 | 369.5 | 5.4359 | 372 | 6487.5297 | 375 | 2.6265 | 377.5 | 48.8748 | 380.5 | 516.7075 | 383.5 | 30.7409 | 386 | 1620.9344 | 389 | 8.9043 | 391.5 | 0.32688 | 394.5 | 8.4131 | 397.5 | 179.7871 | 400 | 180.0599 | 403 | 356.6449 | 405.5 | 407.8213 | 349.5 | 0.056547

## C-G Min
Average Conductor to Ground Resistances
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38
PVC | 7-C | Tray A
0 | 250 kW
Burner Time | C1-G |  | Burner Time | C2-G | Burner Time | C3-G | Burner Time | C4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | C7-G | Burner Time | Minimums Overall
-105.3333 | 247038 |  | -93.6667 | 223738 | -85.6667 | 223738 | -80.5 | 235738 | -77.3333 | 235738 | -75 | 234138 | -72.6667 | 239538 | -105.3333 | 223738
48.5 | 247038 |  | 60.3333 | 28.2323 | 68.3333 | 27026.4444 | 73.4167 | 126869 | 76.6667 | 68.8253 | 78.9167 | 14.23 | 81.3333 | 22.047 | 48.5 | 14.23
202.5833 | 0.62735 |  | 214.1667 | 0.68824 | 222.1667 | 0.63243 | 227.3333 | 0.64615 | 230.6667 | 0.63934 | 232.9167 | 0.67491 | 235.1667 | 0.64923 | 202.5833 | 0.62735
356.5833 | 0.91868 |  | 368.3333 | 2.3091 | 376.3333 | 1.1152 | 381.4167 | 1.742 | 384.6667 | 0.65573 | 387 | 2.5062 | 389.3333 | 0.65103 | 356.5833 | 0.65103

## C6-7
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 149.1685 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 6 & 7
Time-109 | N11 | N12 | Time-110 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
39006.5643 | 1 | 0 | 39006.5643 | 1 | 0 | -56.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244238 | 244238 | 244237.9994
39006.5661 | 2139 | 0 | 39006.5661 | 2002 | 0 | 97.5 | 305.5 | 130.5861 | 0 | 122.2222 | 0 | 1.3059 | 0 | 1.2222 | 0 | 1.3059 | 1.2222 | 14.23 | 22.047 | 12.9242
39006.5678 | 2427 | 0 | 39006.5678 | 2353 | 0 | 251.5 | 459.5 | 148.1685 | 0 | 143.6508 | 0 | 1.4817 | 0 | 1.4365 | 0 | 1.4817 | 1.4365 | 0.67491 | 3.8411 | 0.80678
39006.5696 | 2359 | 2 | 39006.5696 | 2306 | 122 | 405.5 | 613.5 | 144.0171 | 0.1221 | 140.7814 | 7.4481 | 1.4402 | 0.001221 | 1.4078 | 0.074481 | 1.4389 | 1.3333 | 3.5525 | 10.989 | 407.8213

## C5-7
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 154.602 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 5 & 7
Time-107 | N11 | N12 | Time-108 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
39006.5642 | 1 | 0 | 39006.5643 | 1 | 0 | -59 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253138 | 253138 | 253137.9994
39006.566 | 1500 | 0 | 39006.566 | 1982 | 0 | 95 | 303 | 91.5751 | 0 | 121.0012 | 0 | 0.91575 | 0 | 1.21 | 0 | 0.91575 | 1.21 | 68.8253 | 27.7689 | 67.9096
39006.5678 | 2456 | 0 | 39006.5678 | 2246 | 0 | 249 | 457 | 149.9389 | 0 | 137.1184 | 0 | 1.4994 | 0 | 1.3712 | 0 | 1.4994 | 1.3712 | 3.1099 | 12.7507 | 1.6105
39006.5696 | 1980 | 1 | 39006.5696 | 2516 | 0 | 403 | 611 | 120.8791 | 0.06105 | 153.602 | 0 | 1.2088 | 0.0006105 | 1.536 | 0 | 1.2082 | 1.536 | 30.2608 | 0.65103 | 356.6449

## C5-6
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 152.0989 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 5 & 6
Time-105 | N11 | N12 | Time-106 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39006.5642 | 1 | 0 | 39006.5642 | 1 | 0 | -62 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249038 | 249038 | 249037.9994
39006.566 | 536 | 0 | 39006.566 | 2049 | 0 | 92 | 300 | 32.7228 | 0 | 125.0916 | 0 | 0.32723 | 0 | 1.2509 | 0 | 0.32723 | 1.2509 | 364.8097 | 21.59 | 364.4825
39006.5678 | 2475 | 0 | 39006.5678 | 2187 | 0 | 246 | 454 | 151.0989 | 0 | 133.5165 | 0 | 1.511 | 0 | 1.3352 | 0 | 1.511 | 1.3352 | 0.66182 | 13.9177 | 0.84917
39006.5695 | 2304 | 9 | 39006.5696 | 2301 | 31 | 400 | 608 | 140.6593 | 0.54945 | 140.4762 | 1.8926 | 1.4066 | 0.0054945 | 1.4048 | 0.018926 | 1.4011 | 1.3858 | 8.4982 | 9.9926 | 180.0599

## C4-7
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 155.0293 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 7
Time-103 | N11 | N12 | Time-104 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39006.5642 | 1 | 0 | 39006.5642 | 1 | 0 | -64.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253838 | 253838 | 253837.9994
39006.566 | 2 | 0 | 39006.566 | 1858 | 0 | 89.5 | 297.5 | 0.1221 | 0 | 113.431 | 0 | 0.001221 | 0 | 1.1343 | 0 | 0.001221 | 1.1343 | 126869 | 36.6728 | 126868.9988
39006.5677 | 2167 | 0 | 39006.5678 | 2523 | 0 | 243 | 451 | 132.2955 | 0 | 154.0293 | 0 | 1.323 | 0 | 1.5403 | 0 | 1.323 | 1.5403 | 17.1841 | 0.64923 | 15.8612
39006.5695 | 2444 | 1 | 39006.5695 | 2492 | 2 | 397.5 | 605.5 | 149.2063 | 0.06105 | 152.1368 | 0.1221 | 1.4921 | 0.0006105 | 1.5214 | 0.001221 | 1.4915 | 1.5201 | 3.9883 | 1.9419 | 179.7871

## C4-6
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 155.7619 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 6
Time-101 | N11 | N12 | Time-102 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39006.5641 | 1 | 0 | 39006.5642 | 1 | 0 | -67.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255038 | 255038 | 255037.9994
39006.5659 | 1 | 0 | 39006.5659 | 1150 | 0 | 86.5 | 294.5 | 0.06105 | 0 | 70.2076 | 0 | 0.0006105 | 0 | 0.70208 | 0 | 0.0006105 | 0.70208 | 255038 | 121.8591 | 255037.9994
39006.5677 | 2535 | 0 | 39006.5677 | 2085 | 0 | 240.5 | 448.5 | 154.7619 | 0 | 127.2894 | 0 | 1.5476 | 0 | 1.2729 | 0 | 1.5476 | 1.2729 | 0.64615 | 22.3683 | 0.90147
39006.5695 | 2323 | 0 | 39006.5695 | 2489 | 0 | 394.5 | 602.5 | 141.8193 | 0 | 151.9536 | 0 | 1.4182 | 0 | 1.5195 | 0 | 1.4182 | 1.5195 | 9.8313 | 2.5062 | 8.4131

## C4-5
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 143.9792 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 5
Time-99 | N11 | N12 | Time-100 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39006.5641 | 1 | 0 | 39006.5641 | 1 | 0 | -70.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235738 | 235738 | 235737.9994
39006.5659 | 1 | 0 | 39006.5659 | 1 | 0 | 83.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 235738 | 235738 | 235737.9994
39006.5677 | 2234 | 0 | 39006.5677 | 2046 | 0 | 237.5 | 445.5 | 136.3858 | 0 | 124.9084 | 0 | 1.3639 | 0 | 1.2491 | 0 | 1.3639 | 1.2491 | 5.5676 | 15.2678 | 4.2037
39006.5695 | 2318 | 0 | 39006.5695 | 2342 | 0 | 391.5 | 599.5 | 141.514 | 0 | 142.9792 | 0 | 1.4151 | 0 | 1.4298 | 0 | 1.4151 | 1.4298 | 1.742 | 0.6994 | 0.32688

## C3-7
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 159.1197 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 7
Time-97 | N11 | N12 | Time-98 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39006.5641 | 1 | 0 | 39006.5641 | 1 | 0 | -73 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39006.5659 | 1 | 0 | 39006.5659 | 2 | 0 | 81 | 289 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 260538 | 130219 | 260537.9994
39006.5676 | 2590 | 0 | 39006.5677 | 2356 | 0 | 234.5 | 442.5 | 158.1197 | 0 | 143.8339 | 0 | 1.5812 | 0 | 1.4383 | 0 | 1.5812 | 1.4383 | 0.63243 | 10.6273 | 0.94876
39006.5694 | 2362 | 0 | 39006.5694 | 2522 | 0 | 389 | 597 | 144.2002 | 0 | 153.9683 | 0 | 1.442 | 0 | 1.5397 | 0 | 1.442 | 1.5397 | 10.3463 | 3.3458 | 8.9043

## C3-6
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 149.0464 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 6
Time-95 | N11 | N12 | Time-96 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39006.564 | 1 | 0 | 39006.5641 | 1 | 0 | -76 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244038 | 244038 | 244037.9994
39006.5658 | 9 | 0 | 39006.5658 | 1 | 0 | 78 | 286 | 0.54945 | 0 | 0.06105 | 0 | 0.0054945 | 0 | 0.0006105 | 0 | 0.0054945 | 0.0006105 | 27026.4444 | 244038 | 27026.4389
39006.5676 | 2311 | 0 | 39006.5676 | 2425 | 0 | 232 | 440 | 141.0867 | 0 | 148.0464 | 0 | 1.4109 | 0 | 1.4805 | 0 | 1.4109 | 1.4805 | 5.6417 | 0.67546 | 4.2308
39006.5694 | 2023 | 4 | 39006.5694 | 2194 | 149 | 386 | 594 | 123.5043 | 0.2442 | 133.9438 | 9.0965 | 1.235 | 0.002442 | 1.3394 | 0.090965 | 1.2326 | 1.2485 | 20.9459 | 18.5492 | 1620.9344

## C3-5
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 157.4103 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 5
Time-93 | N11 | N12 | Time-94 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39006.564 | 1 | 0 | 39006.564 | 1 | 0 | -78.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
39006.5658 | 1 | 0 | 39006.5658 | 1 | 0 | 75.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257738 | 257738 | 257737.9994
39006.5676 | 2318 | 0 | 39006.5676 | 2562 | 0 | 229.5 | 437.5 | 141.514 | 0 | 156.4103 | 0 | 1.4151 | 0 | 1.5641 | 0 | 1.4151 | 1.5641 | 11.233 | 0.63934 | 9.8178
39006.5694 | 1900 | 176 | 39006.5694 | 2301 | 2 | 383.5 | 591.5 | 115.9951 | 10.7448 | 140.4762 | 0.1221 | 1.16 | 0.10745 | 1.4048 | 0.001221 | 1.0525 | 1.4035 | 255.2586 | 12.0694 | 30.7409

## C3-4
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 152.4042 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 4
Time-91 | N11 | N12 | Time-92 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39006.564 | 1 | 0 | 39006.564 | 1 | 0 | -81.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
39006.5658 | 1 | 0 | 39006.5658 | 1 | 0 | 72.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249538 | 249538 | 249537.9994
39006.5675 | 2428 | 0 | 39006.5676 | 2480 | 0 | 226.5 | 434.5 | 148.2295 | 0 | 151.4042 | 0 | 1.4823 | 0 | 1.514 | 0 | 1.4823 | 1.514 | 2.8163 | 0.66048 | 1.334
39006.5693 | 2105 | 10 | 39006.5693 | 2159 | 1 | 380.5 | 588.5 | 128.5104 | 0.6105 | 131.8071 | 0.06105 | 1.2851 | 0.006105 | 1.3181 | 0.0006105 | 1.279 | 1.3175 | 19.2685 | 15.6716 | 516.7075

## C2-7
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 146.2991 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 7
Time-89 | N11 | N12 | Time-90 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
39006.5639 | 1 | 0 | 39006.564 | 1 | 0 | -84.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239538 | 239538 | 239537.9994
39006.5657 | 1869 | 1 | 39006.5657 | 1 | 0 | 69.5 | 277.5 | 114.1026 | 0.06105 | 0.06105 | 0 | 1.141 | 0.0006105 | 0.0006105 | 0 | 1.1404 | 0.0006105 | 28.2323 | 239538.0003 | 52616.0344
39006.5675 | 2380 | 0 | 39006.5675 | 2224 | 0 | 223.5 | 431.5 | 145.2991 | 0 | 135.7753 | 0 | 1.453 | 0 | 1.3578 | 0 | 1.453 | 1.3578 | 0.68824 | 7.7509 | 0.76476
39006.5693 | 2195 | 23 | 39006.5693 | 2246 | 1 | 377.5 | 585.5 | 134.0049 | 1.4042 | 137.1184 | 0.06105 | 1.34 | 0.014042 | 1.3712 | 0.0006105 | 1.326 | 1.3706 | 11.0042 | 6.7257 | 48.8748

## C2-6
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 143.0024 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 6
Time-87 | N11 | N12 | Time-88 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39006.5639 | 1 | 0 | 39006.5639 | 1 | 0 | -87 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234138 | 234138 | 234137.9994
39006.5657 | 1802 | 1 | 39006.5657 | 1 | 0 | 67 | 275 | 110.0122 | 0.06105 | 0.06105 | 0 | 1.1001 | 0.0006105 | 0.0006105 | 0 | 1.0995 | 0.0006105 | 30.0044 | 234138.0001 | 53914.973
39006.5675 | 2233 | 0 | 39006.5675 | 2326 | 0 | 221 | 429 | 136.3248 | 0 | 142.0024 | 0 | 1.3632 | 0 | 1.42 | 0 | 1.3632 | 1.42 | 4.8983 | 0.70421 | 3.5351
39006.5693 | 2222 | 76 | 39006.5693 | 2238 | 4 | 375 | 583 | 135.6532 | 4.6398 | 136.63 | 0.2442 | 1.3565 | 0.046398 | 1.3663 | 0.002442 | 1.3101 | 1.3639 | 22.6158 | 4.7096 | 2.6265

## C2-5
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 145.8718 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 5
Time-85 | N11 | N12 | Time-86 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39006.5639 | 1 | 0 | 39006.5639 | 1 | 0 | -90 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
39006.5657 | 1 | 0 | 39006.5657 | 1 | 0 | 64 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 238838 | 238838 | 238837.9994
39006.5674 | 2373 | 0 | 39006.5675 | 2346 | 0 | 218 | 426 | 144.8718 | 0 | 143.2234 | 0 | 1.4487 | 0 | 1.4322 | 0 | 1.4487 | 1.4322 | 0.69027 | 1.8491 | 0.75845
39006.5692 | 2042 | 1 | 39006.5692 | 1956 | 11 | 372 | 580 | 124.6642 | 0.06105 | 119.4139 | 0.67155 | 1.2466 | 0.0006105 | 1.1941 | 0.0067155 | 1.246 | 1.1874 | 17.0563 | 23.0459 | 6487.5297

## C2-4
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 152.4652 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 4
Time-83 | N11 | N12 | Time-84 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39006.5639 | 1 | 0 | 39006.5639 | 1 | 0 | -92.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
39006.5656 | 1 | 0 | 39006.5656 | 1 | 0 | 61.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249638 | 249638 | 249637.9994
39006.5674 | 2264 | 0 | 39006.5674 | 2481 | 0 | 215 | 423 | 138.2173 | 0 | 151.4652 | 0 | 1.3822 | 0 | 1.5147 | 0 | 1.3822 | 1.5147 | 10.3083 | 0.66022 | 8.9261
39006.5692 | 2337 | 0 | 39006.5692 | 2174 | 0 | 369.5 | 577.5 | 142.674 | 0 | 132.7228 | 0 | 1.4267 | 0 | 1.3272 | 0 | 1.4267 | 1.3272 | 6.8626 | 14.8749 | 5.4359

## C2-3
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 136.6532 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 3
Time-81 | N11 | N12 | Time-82 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39006.5638 | 1 | 0 | 39006.5638 | 1 | 0 | -95.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223738 | 223738 | 223737.9994
39006.5656 | 1 | 0 | 39006.5656 | 1 | 0 | 58.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223738 | 223738 | 223737.9994
39006.5674 | 2029 | 0 |  | 2057 | 0 | 212 | 420 | 123.8706 | 0 | 125.58 | 0 | 1.2387 | 0 | 1.2558 | 0 | 1.2387 | 1.2558 | 10.3194 | 8.8177 | 9.0807
39006.5692 | 2194 | 3 | 39006.5692 | 2222 | 17 | 366.5 | 574.5 | 133.9438 | 0.18315 | 135.6532 | 1.0379 | 1.3394 | 0.0018315 | 1.3565 | 0.010379 | 1.3376 | 1.3462 | 2.3091 | 1.1152 | 15.2129

## C1-7
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 150.8779 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 7
Time-79 | N11 | N12 | Time-80 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
39006.5638 | 1 | 0 | 39006.5638 | 1 | 0 | -98.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247038 | 247038 | 247037.9994
39006.5656 | 1 | 0 | 39006.5656 | 2 | 0 | 55.5 | 263.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 247038 | 123469 | 247037.9994
39006.5673 | 2025 | 0 | 39006.5674 | 2039 | 0 | 209.5 | 417.5 | 123.6264 | 0 | 124.4811 | 0 | 1.2363 | 0 | 1.2448 | 0 | 1.2363 | 1.2448 | 22.0435 | 21.2055 | 20.8072
39006.5691 | 2455 | 16 | 39006.5691 | 2423 | 4 | 363.5 | 571.5 | 149.8779 | 0.9768 | 147.9243 | 0.2442 | 1.4988 | 0.009768 | 1.4792 | 0.002442 | 1.489 | 1.4768 | 0.91868 | 2.439 | 0.056547

## C1-6
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 159.9133 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 6
Time-77 | N11 | N12 | Time-78 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39006.5638 | 1 | 0 | 39006.5638 | 1 | 0 | -101 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39006.5655 | 1 | 0 | 39006.5655 | 1 | 0 | 52.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39006.5673 | 2603 | 0 | 39006.5673 | 2594 | 0 | 206.5 | 414.5 | 158.9133 | 0 | 158.3639 | 0 | 1.5891 | 0 | 1.5836 | 0 | 1.5891 | 1.5836 | 0.62927 | 0.97841 | 0.95986
39006.5691 | 2274 | 222 | 39006.5691 | 2089 | 9 | 361 | 569 | 138.8278 | 13.5531 | 127.5336 | 0.54945 | 1.3883 | 0.13553 | 1.2753 | 0.0054945 | 1.2527 | 1.2698 | 28.9165 | 25.8864 | 11.4284

## C1-5
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 153.9915 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 5
Time-75 | N11 | N12 | Time-76 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39006.5637 | 1 | 0 | 39006.5637 | 1 | 0 | -104 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39006.5655 | 1 | 0 | 39006.5655 | 1 | 0 | 50 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252138 | 252138 | 252137.9994
39006.5673 | 2277 | 0 | 39006.5673 | 2063 | 0 | 204 | 412 | 139.011 | 0 | 125.9463 | 0 | 1.3901 | 0 | 1.2595 | 0 | 1.3901 | 1.2595 | 10.7765 | 22.2676 | 9.3864
39006.5691 | 1933 | 1 | 39006.5691 | 2506 | 2 | 358 | 566 | 118.0098 | 0.06105 | 152.9915 | 0.1221 | 1.1801 | 0.0006105 | 1.5299 | 0.001221 | 1.1795 | 1.5287 | 33.1206 | 0.65573 | 383.3077

## C1-4
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 160.4017 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 4
Time-73 | N11 | N12 | Time-74 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39006.5637 | 1 | 0 | 39006.5637 | 1 | 0 | -106.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39006.5655 | 1 | 0 | 39006.5655 | 1 | 0 | 47 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262638 | 262638 | 262637.9994
39006.5673 | 2611 | 0 | 39006.5673 | 2473 | 0 | 201.5 | 409.5 | 159.4017 | 0 | 150.9768 | 0 | 1.594 | 0 | 1.5098 | 0 | 1.594 | 1.5098 | 0.62735 | 6.2426 | 0.96667
39006.569 | 2134 | 3 | 39006.5691 | 1853 | 56 | 355 | 563 | 130.2808 | 0.18315 | 113.1258 | 3.4188 | 1.3028 | 0.0018315 | 1.1313 | 0.034188 | 1.301 | 1.0971 | 23.2182 | 49.7734 | 5432.1824

## C1-3
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 156.6777 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 3
Time-71 | N11 | N12 | Time-72 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39006.5637 | 1 | 0 | 39006.5637 | 1 | 0 | -109.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
39006.5654 | 1 | 0 | 39006.5655 | 1 | 0 | 44.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
39006.5672 | 2550 | 0 | 39006.5672 | 2266 | 0 | 198.5 | 406.5 | 155.6777 | 0 | 138.3394 | 0 | 1.5568 | 0 | 1.3834 | 0 | 1.5568 | 1.3834 | 0.64235 | 13.256 | 0.91442
39006.569 | 2152 | 3 | 39006.569 | 1773 | 153 | 352.5 | 560.5 | 131.3797 | 0.18315 | 108.2418 | 9.3407 | 1.3138 | 0.0018315 | 1.0824 | 0.093407 | 1.312 | 0.98901 | 19.3106 | 95.8549 | 6711.2261

## C1-2
OB Prelim Test 3 |  |  | 2006-10-16 | 13:38 |  | Vs = |  | 157.105 |  | R = | 100
PVC | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 2
Time-69 | N11 | N12 | Time-70 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39006.5636 | 1 | 0 | 39006.5636 | 1 | 0 | -112.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39006.5654 | 1 | 0 | 39006.5654 | 1 | 0 | 41.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257238 | 257238 | 257237.9994
39006.5672 | 2557 | 0 | 39006.5672 | 2402 | 0 | 195.5 | 403.5 | 156.105 | 0 | 146.6422 | 0 | 1.5611 | 0 | 1.4664 | 0 | 1.5611 | 1.4664 | 0.64059 | 7.1349 | 0.92046
39006.569 | 2045 | 15 | 39006.569 | 1968 | 0 | 349.5 | 557.5 | 124.8474 | 0.91575 | 120.1465 | 0 | 1.2485 | 0.0091575 | 1.2015 | 0 | 1.2393 | 1.2015 | 26.6692 | 30.7612 | 805.1408

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | OB Prelim Test 3 |  |  | 2006-10-16 | 13:38
39006.5625 | 1 | 0 | 1 | PVC | 7-C | Tray A | IRMS | 1
39006.5643 | 1 | 0 | 1 |  | 250 kW |  | Cable
39006.5661 | 2 | 0 | 1
39006.5679 | 2329 | 0 | 1
1
39006.5625 | 1 | 0 | 2
39006.5643 | 1 | 0 | 2
39006.5661 | 1 | 0 | 2
39006.5679 | 2210 | 0 | 2
2
39006.5626 | 1 | 0 | 3
39006.5643 | 1 | 0 | 3
39006.5661 | 1 | 0 | 3
39006.5679 | 2471 | 0 | 3
3
39006.5626 | 1 | 0 | 4
39006.5644 | 1 | 0 | 4
39006.5661 | 2240 | 0 | 4
39006.5679 | 2052 | 0 | 4
4
39006.5626 | 1 | 0 | 5
39006.5644 | 1 | 0 | 5
39006.5661 | 1 | 0 | 5
39006.5679 | 2338 | 0 | 5
5
39006.5626 | 1 | 0 | 6
39006.5644 | 1 | 0 | 6
39006.5662 | 2469 | 0 | 6
39006.568 | 2537 | 0 | 6
6
39006.5626 | 1 | 0 | 7
39006.5644 | 1 | 0 | 7
39006.5662 | 2 | 0 | 7
39006.568 | 2463 | 0 | 7
7
39006.5626 | 1 | 0 | 8
39006.5644 | 1 | 0 | 8
39006.5662 | 2494 | 0 | 8
39006.568 | 2099 | 0 | 8
8
39006.5627 | 1 | 0 | 9
39006.5644 | 1 | 0 | 9
39006.5662 | 2043 | 18 | 9
39006.568 | 2029 | 0 | 9
9
39006.5627 | 1 | 0 | 10
39006.5644 | 1 | 0 | 10
39006.5662 | 2408 | 0 | 10
39006.568 | 2408 | 0 | 10
10
39006.5627 | 1 | 0 | 11
39006.5645 | 1 | 0 | 11
39006.5663 | 2354 | 0 | 11
39006.568 | 2315 | 0 | 11
11
39006.5627 | 1 | 0 | 12
39006.5645 | 1 | 0 | 12
39006.5663 | 2079 | 0 | 12
39006.568 | 2358 | 0 | 12
12
39006.5627 | 0 | 0 | 13
39006.5645 | 1 | 0 | 13
39006.5663 | 2282 | 0 | 13
39006.5681 | 2554 | 0 | 13
13
39006.5627 | 1 | 0 | 14
39006.5645 | 1 | 0 | 14
39006.5663 | 2474 | 0 | 14
39006.5681 | 2341 | 0 | 14
14
39006.5627 | 1 | 0 | 15
39006.5645 | 1 | 0 | 15
39006.5663 | 2367 | 0 | 15
15
39006.5628 | 1 | 0 | 16
39006.5645 | 0 | 0 | 16
39006.5663 | 2456 | 0 | 16
39006.5681 | 1955 | 0 | 16
16
39006.5628 | 1 | 0 | 17
39006.5646 | 1 | 0 | 17
39006.5663 | 2509 | 0 | 17
39006.5681 | 2099 | 0 | 17
17
39006.5628 | 1 | 0 | 18
39006.5646 | 1 | 0 | 18
39006.5664 | 2516 | 0 | 18
39006.5681 | 1951 | 0 | 18
18
39006.5628 | 1 | 0 | 19
39006.5646 | 1 | 0 | 19
39006.5664 | 2161 | 0 | 19
39006.5682 | 2061 | 0 | 19
19
39006.5628 | 1 | 0 | 20
39006.5646 | 1 | 0 | 20
39006.5664 | 2424 | 0 | 20
39006.5682 | 2297 | 0 | 20
20
39006.5628 | 1 | 0 | 21
39006.5646 | 1 | 0 | 21
39006.5664 | 2519 | 0 | 21
39006.5682 | 2565 | 0 | 21
21
39006.5629 | 1 | 0 | 22
39006.5646 | 1 | 0 | 22
39006.5664 | 2446 | 0 | 22
39006.5682 | 2569 | 0 | 22
22
39006.5629 | 1 | 0 | 23
39006.5647 | 1 | 0 | 23
39006.5664 | 2520 | 0 | 23
39006.5682 | 2573 | 0 | 23
23
39006.5629 | 1 | 0 | 24
39006.5647 | 1 | 0 | 24
39006.5665 | 4 | 0 | 24
39006.5682 | 2102 | 0 | 24
24
39006.5629 | 1 | 0 | 25
39006.5647 | 1 | 0 | 25
39006.5665 | 120 | 0 | 25
39006.5683 | 2330 | 0 | 25
25
39006.5629 | 1 | 0 | 26
39006.5647 | 1 | 0 | 26
39006.5665 | 2098 | 0 | 26
39006.5683 | 1954 | 0 | 26
26
39006.5629 | 1 | 0 | 27
39006.5647 | 1 | 0 | 27
39006.5665 | 2003 | 0 | 27
39006.5683 | 2168 | 0 | 27
27
39006.563 | 1 | 0 | 28
39006.5647 | 1 | 0 | 28
39006.5665 | 2485 | 0 | 28
39006.5683 | 2475 | 0 | 28
28
39006.563 | 1 | 0 | 29
39006.5648 | 1 | 0 | 29
39006.5665 | 1985 | 0 | 29
39006.5683 | 1982 | 0 | 29
29
39006.563 | 1 | 0 | 30
39006.5648 | 1 | 0 | 30
39006.5666 | 2123 | 0 | 30
39006.5683 | 1971 | 0 | 30
30
39006.563 | 1 | 0 | 31
39006.5648 | 1 | 0 | 31
39006.5666 | 2256 | 0 | 31
39006.5684 | 1972 | 0 | 31
31
39006.563 | 1 | 0 | 32
39006.5648 | 1 | 0 | 32
39006.5666 | 2564 | 0 | 32
39006.5684 | 2079 | 0 | 32
32
39006.563 | 1 | 0 | 33
39006.5648 | 1 | 0 | 33
39006.5666 | 2265 | 0 | 33
39006.5684 | 2320 | 0 | 33
33
39006.5631 | 1 | 0 | 34
39006.5648 | 1 | 0 | 34
39006.5666 | 2245 | 0 | 34
39006.5684 | 1990 | 0 | 34
34
39006.5631 | 1 | 0 | 35
39006.5648 | 1 | 0 | 35
39006.5666 | 2348 | 0 | 35
39006.5684 | 2096 | 0 | 35
35
39006.5631 | 1 | 0 | 36
39006.5649 | 1 | 0 | 36
39006.5667 | 2550 | 0 | 36
39006.5684 | 2414 | 0 | 36
36
39006.5631 | 1 | 0 | 37
39006.5649 | 1 | 0 | 37
39006.5667 | 2477 | 0 | 37
39006.5684 | 2055 | 0 | 37
37
39006.5631 | 1 | 0 | 38
39006.5649 | 1 | 0 | 38
39006.5667 | 2345 | 0 | 38
39006.5685 | 2334 | 0 | 38
38
39006.5631 | 1 | 0 | 39
39006.5649 | 1 | 0 | 39
39006.5667 | 2183 | 0 | 39
39006.5685 | 2092 | 0 | 39
39
39006.5631 | 1 | 0 | 40
39006.5649 | 1 | 0 | 40
39006.5667 | 2408 | 0 | 40
39006.5685 | 2219 | 0 | 40
40
39006.5632 | 1 | 0 | 41
39006.565 | 1 | 0 | 41
39006.5667 | 2061 | 0 | 41
39006.5685 | 2324 | 0 | 41
41
39006.5632 | 1 | 0 | 42
39006.565 | 1 | 0 | 42
39006.5667 | 2613 | 0 | 42
39006.5685 | 2511 | 0 | 42
42
39006.5632 | 1 | 0 | 43
39006.565 | 1 | 0 | 43
39006.5668 | 2447 | 0 | 43
39006.5685 | 1970 | 0 | 43
43
39006.5632 | 1 | 0 | 44
39006.565 | 1 | 0 | 44
39006.5668 | 2587 | 0 | 44
39006.5686 | 2055 | 0 | 44
44
39006.5632 | 1 | 0 | 45
39006.565 | 1 | 0 | 45
39006.5668 | 2230 | 0 | 45
39006.5686 | 2287 | 0 | 45
45
39006.5633 | 1 | 0 | 46
39006.565 | 1 | 0 | 46
39006.5668 | 2576 | 0 | 46
39006.5686 | 1992 | 0 | 46
46
39006.5633 | 1 | 0 | 47
39006.565 | 1 | 0 | 47
39006.5668 | 2197 | 0 | 47
39006.5686 | 2312 | 0 | 47
47
39006.5633 | 1 | 0 | 48
39006.5651 | 1 | 0 | 48
39006.5668 | 2448 | 0 | 48
39006.5686 | 2455 | 0 | 48
48
39006.5633 | 1 | 0 | 49
39006.5651 | 1 | 0 | 49
39006.5669 | 2512 | 0 | 49
39006.5686 | 1767 | 0 | 49
49
39006.5633 | 1 | 0 | 50
39006.5651 | 1 | 0 | 50
39006.5669 | 2030 | 0 | 50
39006.5687 | 2395 | 0 | 50
50
39006.5633 | 1 | 0 | 51
39006.5651 | 1 | 0 | 51
39006.5669 | 2003 | 0 | 51
39006.5687 | 2033 | 0 | 51
51
39006.5633 | 1 | 0 | 52
39006.5651 | 1 | 0 | 52
39006.5669 | 2290 | 0 | 52
39006.5687 | 2402 | 0 | 52
52
39006.5634 | 1 | 0 | 53
39006.5652 | 1 | 0 | 53
39006.5669 | 2028 | 0 | 53
39006.5687 | 2493 | 0 | 53
53
39006.5634 | 1 | 0 | 54
39006.5652 | 1 | 0 | 54
39006.5669 | 2626 | 0 | 54
39006.5687 | 2001 | 0 | 54
54
39006.5634 | 1 | 0 | 55
39006.5652 | 1 | 0 | 55
39006.567 | 2042 | 0 | 55
39006.5687 | 1961 | 0 | 55
55
39006.5634 | 1 | 0 | 56
39006.5652 | 1 | 0 | 56
39006.567 | 2171 | 0 | 56
39006.5688 | 2154 | 0 | 56
56
39006.5634 | 1 | 0 | 57
39006.5652 | 1 | 0 | 57
39006.567 | 2571 | 0 | 57
39006.5688 | 2205 | 0 | 57
57
39006.5634 | 1 | 0 | 58
39006.5652 | 1 | 0 | 58
39006.567 | 2570 | 0 | 58
39006.5688 | 2414 | 0 | 58
58
39006.5635 | 1 | 0 | 59
39006.5652 | 1 | 0 | 59
39006.567 | 2357 | 0 | 59
39006.5688 | 2219 | 0 | 59
59
39006.5635 | 1 | 0 | 60
39006.5653 | 1 | 0 | 60
39006.567 | 2406 | 0 | 60
39006.5688 | 2240 | 0 | 60
60
39006.5635 | 1 | 0 | 61
39006.5653 | 1 | 0 | 61
39006.5671 | 2571 | 0 | 61
39006.5688 | 2153 | 0 | 61
61
39006.5635 | 1 | 0 | 62
39006.5653 | 1 | 0 | 62
39006.5671 | 2089 | 0 | 62
39006.5689 | 1995 | 0 | 62
62
39006.5635 | 1 | 0 | 63
39006.5653 | 1 | 0 | 63
39006.5671 | 2210 | 0 | 63
39006.5689 | 2130 | 0 | 63
63
39006.5635 | 1 | 0 | 64
39006.5653 | 1 | 0 | 64
39006.5671 | 2152 | 0 | 64
39006.5689 | 1946 | 0 | 64
64
39006.5636 | 1 | 0 | 65
39006.5653 | 1 | 0 | 65
39006.5671 | 2203 | 0 | 65
39006.5689 | 1875 | 0 | 65
65
39006.5636 | 1 | 0 | 66
39006.5654 | 1 | 0 | 66
39006.5671 | 2524 | 0 | 66
39006.5689 | 2102 | 0 | 66
66
39006.5636 | 1 | 0 | 67
39006.5654 | 1 | 0 | 67
39006.5672 | 2212 | 0 | 67
39006.5689 | 1732 | 0 | 67
67
39006.5636 | 1 | 0 | 68
39006.5654 | 1 | 0 | 68
39006.5672 | 2355 | 0 | 68
39006.569 | 2350 | 0 | 68
68
39006.5636 | 1 | 0 | 69
39006.5654 | 1 | 0 | 69
39006.5672 | 2557 | 0 | 69
39006.569 | 2045 | 15 | 69
69
39006.5636 | 1 | 0 | 70
39006.5654 | 1 | 0 | 70
39006.5672 | 2402 | 0 | 70
39006.569 | 1968 | 0 | 70
70
39006.5637 | 1 | 0 | 71
39006.5654 | 1 | 0 | 71
39006.5672 | 2550 | 0 | 71
39006.569 | 2152 | 3 | 71
71
39006.5637 | 1 | 0 | 72
39006.5655 | 1 | 0 | 72
39006.5672 | 2266 | 0 | 72
39006.569 | 1773 | 153 | 72
72
39006.5637 | 1 | 0 | 73
39006.5655 | 1 | 0 | 73
39006.5673 | 2611 | 0 | 73
39006.569 | 2134 | 3 | 73
73
39006.5637 | 1 | 0 | 74
39006.5655 | 1 | 0 | 74
39006.5673 | 2473 | 0 | 74
39006.5691 | 1853 | 56 | 74
74
39006.5637 | 1 | 0 | 75
39006.5655 | 1 | 0 | 75
39006.5673 | 2277 | 0 | 75
39006.5691 | 1933 | 1 | 75
75
39006.5637 | 1 | 0 | 76
39006.5655 | 1 | 0 | 76
39006.5673 | 2063 | 0 | 76
39006.5691 | 2506 | 2 | 76
76
39006.5638 | 1 | 0 | 77
39006.5655 | 1 | 0 | 77
39006.5673 | 2603 | 0 | 77
39006.5691 | 2274 | 222 | 77
77
39006.5638 | 1 | 0 | 78
39006.5655 | 1 | 0 | 78
39006.5673 | 2594 | 0 | 78
39006.5691 | 2089 | 9 | 78
78
39006.5638 | 1 | 0 | 79
39006.5656 | 1 | 0 | 79
39006.5673 | 2025 | 0 | 79
39006.5691 | 2455 | 16 | 79
79
39006.5638 | 1 | 0 | 80
39006.5656 | 2 | 0 | 80
39006.5674 | 2039 | 0 | 80
39006.5691 | 2423 | 4 | 80
80
39006.5638 | 1 | 0 | 81
39006.5656 | 1 | 0 | 81
39006.5674 | 2029 | 0 | 81
39006.5692 | 2194 | 3 | 81
81
39006.5638 | 1 | 0 | 82
39006.5656 | 1 | 0 | 82
39006.5692 | 2222 | 17 | 82
82
39006.5639 | 1 | 0 | 83
39006.5656 | 1 | 0 | 83
39006.5674 | 2264 | 0 | 83
39006.5692 | 2337 | 0 | 83
83
39006.5639 | 1 | 0 | 84
39006.5656 | 1 | 0 | 84
39006.5674 | 2481 | 0 | 84
39006.5692 | 2174 | 0 | 84
84
39006.5639 | 1 | 0 | 85
39006.5657 | 1 | 0 | 85
39006.5674 | 2373 | 0 | 85
39006.5692 | 2042 | 1 | 85
85
39006.5639 | 1 | 0 | 86
39006.5657 | 1 | 0 | 86
39006.5675 | 2346 | 0 | 86
39006.5692 | 1956 | 11 | 86
86
39006.5639 | 1 | 0 | 87
39006.5657 | 1802 | 0 | 87
39006.5675 | 2233 | 0 | 87
39006.5693 | 2222 | 76 | 87
87
39006.5639 | 1 | 0 | 88
39006.5657 | 1 | 0 | 88
39006.5675 | 2326 | 0 | 88
39006.5693 | 2238 | 4 | 88
88
39006.5639 | 1 | 0 | 89
39006.5657 | 1869 | 0 | 89
39006.5675 | 2380 | 0 | 89
39006.5693 | 2195 | 23 | 89
89
39006.564 | 1 | 0 | 90
39006.5657 | 1 | 0 | 90
39006.5675 | 2224 | 0 | 90
39006.5693 | 2246 | 1 | 90
90
39006.564 | 1 | 0 | 91
39006.5658 | 1 | 0 | 91
39006.5675 | 2428 | 0 | 91
39006.5693 | 2105 | 10 | 91
91
39006.564 | 1 | 0 | 92
39006.5658 | 1 | 0 | 92
39006.5676 | 2480 | 0 | 92
39006.5693 | 2159 | 1 | 92
92
39006.564 | 1 | 0 | 93
39006.5658 | 1 | 0 | 93
39006.5676 | 2318 | 0 | 93
39006.5694 | 1900 | 176 | 93
93
39006.564 | 1 | 0 | 94
39006.5658 | 1 | 0 | 94
39006.5676 | 2562 | 0 | 94
39006.5694 | 2301 | 2 | 94
94
39006.564 | 1 | 0 | 95
39006.5658 | 9 | 0 | 95
39006.5676 | 2311 | 0 | 95
39006.5694 | 2023 | 4 | 95
95
39006.5641 | 1 | 0 | 96
39006.5658 | 1 | 0 | 96
39006.5676 | 2425 | 0 | 96
39006.5694 | 2194 | 149 | 96
96
39006.5641 | 1 | 0 | 97
39006.5659 | 1 | 0 | 97
39006.5676 | 2590 | 0 | 97
39006.5694 | 2362 | 0 | 97
97
39006.5641 | 1 | 0 | 98
39006.5659 | 2 | 0 | 98
39006.5677 | 2356 | 0 | 98
39006.5694 | 2522 | 0 | 98
98
39006.5641 | 1 | 0 | 99
39006.5659 | 1 | 0 | 99
39006.5677 | 2234 | 0 | 99
39006.5695 | 2318 | 0 | 99
99
39006.5641 | 1 | 0 | 100
39006.5659 | 1 | 0 | 100
39006.5677 | 2046 | 0 | 100
39006.5695 | 2342 | 0 | 100
100
39006.5641 | 1 | 0 | 101
39006.5659 | 1 | 0 | 101
39006.5677 | 2535 | 0 | 101
39006.5695 | 2323 | 0 | 101
101
39006.5642 | 1 | 0 | 102
39006.5659 | 1150 | 0 | 102
39006.5677 | 2085 | 0 | 102
39006.5695 | 2489 | 0 | 102
102
39006.5642 | 1 | 0 | 103
39006.566 | 2 | 0 | 103
39006.5677 | 2167 | 0 | 103
39006.5695 | 2444 | 1 | 103
103
39006.5642 | 1 | 0 | 104
39006.566 | 1858 | 0 | 104
39006.5678 | 2523 | 0 | 104
39006.5695 | 2492 | 2 | 104
104
39006.5642 | 1 | 0 | 105
39006.566 | 536 | 0 | 105
39006.5678 | 2475 | 0 | 105
39006.5695 | 2304 | 9 | 105
105
39006.5642 | 1 | 0 | 106
39006.566 | 2049 | 0 | 106
39006.5678 | 2187 | 0 | 106
39006.5696 | 2301 | 31 | 106
106
39006.5642 | 1 | 0 | 107
39006.566 | 1500 | 0 | 107
39006.5678 | 2456 | 0 | 107
39006.5696 | 1980 | 1 | 107
107
39006.5643 | 1 | 0 | 108
39006.566 | 1982 | 0 | 108
39006.5678 | 2246 | 0 | 108
39006.5696 | 2516 | 0 | 108
108
39006.5643 | 1 | 0 | 109
39006.5661 | 2139 | 0 | 109
39006.5678 | 2427 | 0 | 109
39006.5696 | 2359 | 2 | 109
109
39006.5643 | 1 | 0 | 110
39006.5661 | 2002 | 0 | 110
39006.5678 | 2353 | 0 | 110
39006.5696 | 2306 | 122 | 110
110

## Temperatures
DAQ Time | Burner Time | Cable center | Air above cable | Air below cable | TRAY A
0 | -208 | 17.2 | 17.2 | 16.8 | 18.2
1 | -207 | 17.2 | 17.2 | 16.8 | 18.2
2 | -206 | 17.2 | 17.2 | 16.8 | 18.2
3 | -205 | 17.2 | 17.2 | 16.8 | 18.2
4 | -204 | 17.2 | 17.2 | 16.8 | 18.2
5 | -203 | 17.2 | 17.2 | 16.8 | 18.2
6 | -202 | 17.2 | 17.2 | 16.8 | 18.2
7 | -201 | 17.2 | 17.2 | 16.8 | 18.2
8 | -200 | 17.2 | 17.2 | 16.8 | 18.2
9 | -199 | 17.2 | 17.2 | 16.8 | 18.2
10 | -198 | 17.2 | 17.2 | 16.8 | 18.2
11 | -197 | 17.2 | 17.2 | 16.8 | 18.2
12 | -196 | 17.2 | 17.2 | 16.8 | 18.2
13 | -195 | 17.2 | 17.2 | 16.8 | 18.2
14 | -194 | 17.2 | 17.2 | 16.8 | 18.2
15 | -193 | 17.2 | 17.2 | 16.8 | 18.2
16 | -192 | 17.2 | 17.2 | 16.8 | 18.2
17 | -191 | 17.2 | 17.2 | 16.8 | 18.2
18 | -190 | 17.2 | 17.2 | 16.8 | 18.2
19 | -189 | 17.2 | 17.2 | 16.8 | 18.2
20 | -188 | 17.2 | 17.2 | 16.8 | 18.2
21 | -187 | 17.2 | 17.2 | 16.8 | 18.2
22 | -186 | 17.2 | 17.2 | 16.8 | 18.2
23 | -185 | 17.2 | 17.2 | 16.8 | 18.2
24 | -184 | 17.2 | 17.2 | 16.8 | 18.2
25 | -183 | 17.2 | 17.2 | 16.8 | 18.2
26 | -182 | 17.2 | 17.2 | 16.8 | 18.2
27 | -181 | 17.2 | 17.2 | 16.8 | 18.2
28 | -180 | 17.2 | 17.2 | 16.8 | 18.2
29 | -179 | 17.2 | 17.2 | 16.8 | 18.2
30 | -178 | 17.2 | 17.2 | 16.8 | 18.2
31 | -177 | 17.2 | 17.2 | 16.8 | 18.2
32 | -176 | 17.2 | 17.2 | 16.8 | 18.2
33 | -175 | 17.2 | 17.2 | 16.8 | 18.2
34 | -174 | 17.2 | 17.2 | 16.8 | 18.2
35 | -173 | 17.2 | 17.2 | 16.8 | 18.2
36 | -172 | 17.2 | 17.2 | 16.8 | 18.2
37 | -171 | 17.2 | 17.2 | 16.8 | 18.2
38 | -170 | 17.2 | 17.2 | 16.8 | 18.2
39 | -169 | 17.2 | 17.2 | 16.8 | 18.2
40 | -168 | 17.2 | 17.2 | 16.8 | 18.2
41 | -167 | 17.2 | 17.2 | 16.8 | 18.2
42 | -166 | 17.2 | 17.2 | 16.8 | 18.2
43 | -165 | 17.2 | 17.2 | 16.8 | 18.2
44 | -164 | 17.2 | 17.2 | 16.8 | 18.2
45 | -163 | 17.2 | 17.2 | 16.8 | 18.2
46 | -162 | 17.2 | 17.2 | 16.8 | 18.2
47 | -161 | 17.2 | 17.2 | 16.8 | 18.2
48 | -160 | 17.2 | 17.2 | 16.8 | 18.2
49 | -159 | 17.2 | 17.2 | 16.8 | 18.2
50 | -158 | 17.2 | 17.2 | 16.8 | 18.2
51 | -157 | 17.2 | 17.2 | 16.8 | 18.2
52 | -156 | 17.2 | 17.2 | 16.8 | 18.2
53 | -155 | 17.2 | 17.2 | 16.8 | 18.2
54 | -154 | 17.2 | 17.2 | 16.8 | 18.2
55 | -153 | 17.2 | 17.2 | 16.8 | 18.2
56 | -152 | 17.2 | 17.2 | 16.8 | 18.2
57 | -151 | 17.2 | 17.2 | 16.8 | 18.2
58 | -150 | 17.2 | 17.2 | 16.8 | 18.2
59 | -149 | 17.2 | 17.2 | 16.8 | 18.2
60 | -148 | 17.2 | 17.2 | 16.8 | 18.2
61 | -147 | 17.2 | 17.2 | 16.8 | 18.2
62 | -146 | 17.2 | 17.2 | 16.8 | 18.2
63 | -145 | 17.2 | 17.2 | 16.8 | 18.2
64 | -144 | 17.2 | 17.2 | 16.8 | 18.2
65 | -143 | 17.2 | 17.2 | 16.8 | 18.2
66 | -142 | 17.2 | 17.2 | 16.8 | 18.2
67 | -141 | 17.2 | 17.2 | 16.8 | 18.2
68 | -140 | 17.2 | 17.2 | 16.8 | 18.2
69 | -139 | 17.2 | 17.2 | 16.8 | 18.2
70 | -138 | 17.2 | 17.2 | 16.8 | 18.2
71 | -137 | 17.2 | 17.2 | 16.8 | 18.2
72 | -136 | 17.2 | 17.2 | 16.8 | 18.2
73 | -135 | 17.2 | 17.2 | 16.8 | 18.2
74 | -134 | 17.2 | 17.2 | 16.8 | 18.2
75 | -133 | 17.2 | 17.2 | 16.8 | 18.2
76 | -132 | 17.2 | 17.2 | 16.8 | 18.2
77 | -131 | 17.2 | 17.2 | 16.8 | 18.2
78 | -130 | 17.2 | 17.2 | 16.8 | 18.2
79 | -129 | 17.2 | 17.2 | 16.8 | 18.2
80 | -128 | 17.2 | 17.2 | 16.8 | 18.2
81 | -127 | 17.2 | 17.2 | 16.8 | 18.2
82 | -126 | 17.2 | 17.2 | 16.8 | 18.2
83 | -125 | 17.2 | 17.2 | 16.8 | 18.2
84 | -124 | 17.2 | 17.2 | 16.8 | 18.2
85 | -123 | 17.2 | 17.2 | 16.8 | 18.2
86 | -122 | 17.2 | 17.2 | 16.8 | 18.2
87 | -121 | 17.2 | 17.2 | 16.8 | 18.2
88 | -120 | 17.2 | 17.2 | 16.8 | 18.2
89 | -119 | 17.2 | 17.2 | 16.8 | 18.2
90 | -118 | 17.2 | 17.2 | 16.8 | 18.2
91 | -117 | 17.2 | 17.2 | 16.8 | 18.2
92 | -116 | 17.2 | 17.2 | 16.8 | 18.2
93 | -115 | 17.2 | 17.2 | 16.8 | 18.2
94 | -114 | 17.2 | 17.2 | 16.8 | 18.2
95 | -113 | 17.2 | 17.2 | 16.8 | 18.2
96 | -112 | 17.2 | 17.2 | 16.8 | 18.2
97 | -111 | 17.2 | 17.2 | 16.8 | 18.2
98 | -110 | 17.2 | 17.2 | 16.8 | 18.2
99 | -109 | 17.2 | 17.2 | 16.8 | 18.2
100 | -108 | 17.2 | 17.2 | 16.8 | 18.2
101 | -107 | 17.2 | 17.2 | 16.8 | 18.2
102 | -106 | 17.2 | 17.2 | 16.8 | 18.2
103 | -105 | 17.2 | 17.2 | 16.8 | 18.2
104 | -104 | 17.2 | 17.2 | 16.8 | 18.2
105 | -103 | 17.2 | 17.2 | 16.8 | 18.2
106 | -102 | 17.2 | 17.2 | 16.8 | 18.2
107 | -101 | 17.2 | 17.2 | 16.8 | 18.2
108 | -100 | 17.2 | 17.2 | 16.8 | 18.2
109 | -99 | 17.2 | 17.2 | 16.8 | 18.2
110 | -98 | 17.2 | 17.2 | 16.8 | 18.2
111 | -97 | 17.2 | 17.2 | 16.8 | 18.2
112 | -96 | 17.2 | 17.2 | 16.8 | 18.2
113 | -95 | 17.2 | 17.2 | 16.8 | 18.2
114 | -94 | 17.2 | 17.2 | 16.8 | 18.2
115 | -93 | 17.2 | 17.2 | 16.8 | 18.2
116 | -92 | 17.2 | 17.2 | 16.8 | 18.2
117 | -91 | 17.2 | 17.2 | 16.8 | 18.2
118 | -90 | 17.2 | 17.2 | 16.8 | 18.2
119 | -89 | 17.2 | 17.2 | 16.8 | 18.2
120 | -88 | 17.2 | 17.2 | 16.8 | 18.2
121 | -87 | 17.2 | 17.2 | 16.8 | 18.2
122 | -86 | 17.2 | 17.2 | 16.8 | 18.2
123 | -85 | 17.2 | 17.2 | 16.8 | 18.2
124 | -84 | 17.2 | 17.2 | 16.8 | 18.2
125 | -83 | 17.2 | 17.2 | 16.8 | 18.2
126 | -82 | 17.2 | 17.2 | 16.8 | 18.2
127 | -81 | 17.2 | 17.2 | 16.8 | 18.2
128 | -80 | 17.2 | 17.2 | 16.8 | 18.2
129 | -79 | 17.2 | 17.2 | 16.8 | 18.2
130 | -78 | 17.2 | 17.2 | 16.8 | 18.2
131 | -77 | 17.2 | 17.2 | 16.8 | 18.2
132 | -76 | 17.2 | 17.2 | 16.8 | 18.2
133 | -75 | 17.2 | 17.2 | 16.8 | 18.2
134 | -74 | 17.2 | 17.2 | 16.8 | 18.2
135 | -73 | 17.2 | 17.2 | 16.8 | 18.2
136 | -72 | 17.2 | 17.2 | 16.8 | 18.2
137 | -71 | 17.2 | 17.2 | 16.8 | 18.2
138 | -70 | 17.2 | 17.2 | 16.8 | 18.2
139 | -69 | 17.2 | 17.2 | 16.8 | 18.2
140 | -68 | 17.2 | 17.2 | 16.8 | 18.2
141 | -67 | 17.2 | 17.2 | 16.8 | 18.2
142 | -66 | 17.2 | 17.2 | 16.8 | 18.2
143 | -65 | 17.2 | 17.2 | 16.8 | 18.2
144 | -64 | 17.2 | 17.2 | 16.8 | 18.2
145 | -63 | 17.2 | 17.2 | 16.8 | 18.2
146 | -62 | 17.2 | 17.2 | 16.8 | 18.2
147 | -61 | 17.2 | 17.2 | 16.8 | 18.2
148 | -60 | 17.2 | 17.2 | 16.8 | 18.2
149 | -59 | 17.2 | 17.2 | 16.8 | 18.2
150 | -58 | 17.2 | 17.2 | 16.8 | 18.2
151 | -57 | 17.2 | 17.2 | 16.8 | 18.2
152 | -56 | 17.2 | 17.2 | 16.8 | 18.2
153 | -55 | 17.2 | 17.2 | 16.8 | 18.2
154 | -54 | 17.2 | 17.2 | 16.8 | 18.2
155 | -53 | 17.2 | 17.2 | 16.8 | 18.2
156 | -52 | 17.2 | 17.2 | 16.8 | 18.2
157 | -51 | 17.2 | 17.2 | 16.8 | 18.2
158 | -50 | 17.2 | 17.2 | 16.8 | 18.2
159 | -49 | 17.2 | 17.2 | 16.8 | 18.2
160 | -48 | 17.2 | 17.2 | 16.8 | 18.2
161 | -47 | 17.2 | 17.2 | 16.8 | 18.2
162 | -46 | 17.2 | 17.2 | 16.8 | 18.2
163 | -45 | 17.2 | 17.2 | 16.8 | 18.2
164 | -44 | 17.2 | 17.2 | 16.8 | 18.2
165 | -43 | 17.2 | 17.2 | 16.8 | 18.2
166 | -42 | 17.2 | 17.2 | 16.8 | 18.2
167 | -41 | 17.2 | 17.2 | 16.8 | 18.2
168 | -40 | 17.2 | 17.2 | 16.8 | 18.2
169 | -39 | 17.2 | 17.2 | 16.8 | 18.2
170 | -38 | 17.2 | 17.2 | 16.8 | 18.2
171 | -37 | 17.2 | 17.2 | 16.8 | 18.2
172 | -36 | 17.2 | 17.2 | 16.8 | 18.2
173 | -35 | 17.2 | 17.2 | 16.8 | 18.2
174 | -34 | 17.2 | 17.2 | 16.8 | 18.2
175 | -33 | 17.2 | 17.2 | 16.8 | 18.2
176 | -32 | 17.2 | 17.2 | 16.8 | 18.2
177 | -31 | 17.2 | 17.2 | 16.8 | 18.2
178 | -30 | 17.2 | 17.2 | 16.8 | 18.2
179 | -29 | 17.2 | 17.2 | 16.8 | 18.2
180 | -28 | 17.2 | 17.2 | 16.8 | 18.2
181 | -27 | 17.2 | 17.2 | 16.8 | 18.2
182 | -26 | 17.2 | 17.2 | 16.8 | 18.2
183 | -25 | 17.2 | 17.2 | 16.8 | 18.2
184 | -24 | 17.2 | 17.2 | 16.8 | 18.2
185 | -23 | 17.2 | 17.2 | 16.8 | 18.2
186 | -22 | 17.2 | 17.2 | 16.8 | 18.2
187 | -21 | 17.2 | 17.2 | 16.8 | 18.2
188 | -20 | 17.2 | 17.2 | 16.8 | 18.2
189 | -19 | 17.2 | 17.2 | 16.8 | 18.2
190 | -18 | 17.2 | 17.2 | 16.8 | 18.2
191 | -17 | 17.2 | 17.2 | 16.8 | 18.2
192 | -16 | 17.2 | 17.2 | 16.8 | 18.2
193 | -15 | 17.2 | 17.2 | 16.8 | 18.2
194 | -14 | 17.2 | 17.2 | 16.9 | 18.2
195 | -13 | 17.2 | 17.3 | 16.9 | 18.2
196 | -12 | 17.2 | 17.2 | 16.9 | 18.2
197 | -11 | 17.2 | 17.2 | 16.9 | 18.2
198 | -10 | 17.2 | 17.2 | 16.9 | 18.2
199 | -9 | 17.2 | 17.2 | 16.9 | 18.2
200 | -8 | 17.2 | 17.2 | 16.9 | 18.2
201 | -7 | 17.2 | 17.2 | 16.9 | 18.2
202 | -6 | 17.2 | 17.2 | 16.9 | 18.2
203 | -5 | 17.2 | 17.3 | 16.9 | 18.2
204 | -4 | 17.2 | 17.3 | 16.9 | 18.2
205 | -3 | 17.2 | 17.3 | 16.9 | 18.2
206 | -2 | 17.2 | 17.2 | 16.9 | 18.2
207 | -1 | 17.2 | 17.2 | 16.9 | 18.3
208 | 0 | 17.2 | 17.3 | 16.9 | 18.3
209 | 1 | 17.2 | 17.3 | 16.9 | 18.3
210 | 2 | 17.2 | 17.3 | 16.9 | 18.3
211 | 3 | 17.2 | 17.3 | 16.9 | 18.3
212 | 4 | 17.2 | 19.5 | 19.1 | 18.8
213 | 5 | 17.2 | 23.4 | 25.2 | 23
214 | 6 | 17.3 | 27.9 | 33.3 | 32.4
215 | 7 | 17.6 | 33.6 | 43.9 | 42.8
216 | 8 | 18.3 | 43.4 | 54.1 | 49.8
217 | 9 | 19.4 | 50.3 | 62.5 | 54
218 | 10 | 21.1 | 61.6 | 81 | 65.1
219 | 11 | 23.1 | 72.4 | 101.7 | 77.9
220 | 12 | 25.7 | 93.2 | 151.4 | 90.1
221 | 13 | 28.7 | 126.7 | 212.3 | 114.8
222 | 14 | 32.4 | 139.2 | 244.7 | 144.4
223 | 15 | 36.8 | 148.5 | 249.7 | 149
224 | 16 | 41.6 | 166.2 | 278.3 | 162.7
225 | 17 | 46.9 | 183.9 | 303.5 | 168.8
226 | 18 | 52.6 | 203.6 | 325 | 168.2
227 | 19 | 58.8 | 229.4 | 345.6 | 174.5
228 | 20 | 65.5 | 249.3 | 357.5 | 175.9
229 | 21 | 72.3 | 265 | 371.4 | 176.5
230 | 22 | 78.7 | 282.6 | 398.5 | 189.7
231 | 23 | 84.9 | 295.7 | 412.3 | 195.9
232 | 24 | 91.9 | 309.6 | 429.1 | 202.2
233 | 25 | 99.9 | 323.6 | 454.3 | 220.1
234 | 26 | 109.3 | 329.1 | 462.1 | 231.1
235 | 27 | 120.7 | 332.8 | 473.9 | 240.8
236 | 28 | 133.3 | 336.3 | 476.4 | 243.4
237 | 29 | 146.4 | 342.7 | 481.6 | 250.1
238 | 30 | 160.2 | 346.1 | 482.6 | 254.9
239 | 31 | 173.9 | 357.3 | 497.2 | 262.4
240 | 32 | 187.5 | 371.3 | 500.1 | 274.1
241 | 33 | 201.1 | 382.7 | 524.3 | 282
242 | 34 | 213 | 392.8 | 531.7 | 293.6
243 | 35 | 223.9 | 405.6 | 541 | 298.5
244 | 36 | 234.6 | 417.4 | 538.4 | 295.8
245 | 37 | 245.5 | 427.1 | 527.9 | 299.9
246 | 38 | 255.6 | 428.2 | 535 | 306.7
247 | 39 | 264.4 | 434.7 | 548.5 | 323.9
248 | 40 | 272 | 451.5 | 567.6 | 339.8
249 | 41 | 278.8 | 463.2 | 581 | 346.6
250 | 42 | 284.6 | 480.2 | 604.2 | 357.4
251 | 43 | 290.8 | 503.6 | 621.4 | 365.4
252 | 44 | 297.8 | 522.1 | 648.5 | 377.3
253 | 45 | 304.7 | 531.3 | 661.6 | 382
254 | 46 | 311.2 | 537.3 | 656.5 | 385.5
255 | 47 | 318.4 | 540.2 | 645.8 | 391.1
256 | 48 | 325.9 | 540 | 643.7 | 394.6
257 | 49 | 333.7 | 544.8 | 649.8 | 412.7
258 | 50 | 340.6 | 549.4 | 656.4 | 436.5
259 | 51 | 347.6 | 552.3 | 654.8 | 441.9
260 | 52 | 354.5 | 556.8 | 650.8 | 440.8
261 | 53 | 360.9 | 562.5 | 651.1 | 446.7
262 | 54 | 367.6 | 565.4 | 650.9 | 452.4
263 | 55 | 374.9 | 568.7 | 637.8 | 453
264 | 56 | 382.5 | 567.6 | 627.9 | 448.2
265 | 57 | 389.3 | 571.9 | 630.6 | 451
266 | 58 | 395.8 | 569.8 | 635 | 453.2
267 | 59 | 402.2 | 588.1 | 651.3 | 467
268 | 60 | 408.8 | 602 | 651.8 | 475.5
269 | 61 | 415.6 | 609.1 | 658.9 | 482.4
270 | 62 | 422.7 | 619 | 661.8 | 486
271 | 63 | 429.3 | 620.5 | 658 | 489.3
272 | 64 | 435.1 | 617.2 | 645.9 | 495.7
273 | 65 | 440.4 | 607.6 | 630.5 | 498.8
274 | 66 | 446 | 601.1 | 618.1 | 502.8
275 | 67 | 452 | 597.5 | 621 | 506.8
276 | 68 | 457.9 | 591.2 | 628.9 | 514.5
277 | 69 | 462.5 | 584.3 | 621.6 | 517.3
278 | 70 | 465.9 | 581.9 | 614.3 | 522.4
279 | 71 | 470 | 582.2 | 605.5 | 516.7
280 | 72 | 474.1 | 583 | 598.1 | 516.4
281 | 73 | 477.9 | 582.1 | 594.2 | 515.5
282 | 74 | 482.5 | 589.2 | 608.5 | 527.8
283 | 75 | 487.2 | 594.2 | 617.8 | 539
284 | 76 | 491.5 | 609.2 | 632.4 | 541.1
285 | 77 | 495.9 | 628.7 | 637.8 | 543.5
286 | 78 | 500.4 | 636.3 | 650.2 | 543.1
287 | 79 | 504.7 | 658.7 | 672.7 | 555.9
288 | 80 | 508.8 | 679.6 | 694.5 | 570.4
289 | 81 | 512.1 | 685.8 | 705.1 | 576.7
290 | 82 | 515.4 | 683.2 | 715.5 | 579.4
291 | 83 | 519.1 | 676 | 695.9 | 577.6
292 | 84 | 522.7 | 682.8 | 678 | 568.4
293 | 85 | 526.5 | 690.8 | 686.4 | 578
294 | 86 | 530.5 | 693.1 | 688.2 | 590.3
295 | 87 | 534.2 | 692.5 | 684.5 | 596.2
296 | 88 | 537.3 | 678.5 | 683.9 | 601.3
297 | 89 | 540 | 671.3 | 675 | 599.1
298 | 90 | 542.6 | 675.5 | 664.4 | 590.4
299 | 91 | 545.7 | 689.3 | 670.1 | 584
300 | 92 | 549 | 698.4 | 676.9 | 587.9
301 | 93 | 552.6 | 697.2 | 673.7 | 589.2
302 | 94 | 556.1 | 707 | 675.7 | 592.2
303 | 95 | 559.7 | 708.4 | 666.6 | 596.8
304 | 96 | 563.7 | 699.6 | 656.7 | 590.7
305 | 97 | 567.6 | 697.2 | 647.2 | 586.7
306 | 98 | 571.2 | 696.6 | 639.6 | 583.3
307 | 99 | 573.8 | 695.4 | 629.3 | 589.1
308 | 100 | 575.9 | 685.3 | 626.1 | 591
309 | 101 | 577.8 | 676.8 | 614.7 | 587.4
310 | 102 | 580.1 | 677.4 | 601.6 | 583.1
311 | 103 | 582.4 | 682 | 604 | 583.2
312 | 104 | 584.2 | 676.6 | 602.9 | 582.4
313 | 105 | 585.5 | 667.4 | 587 | 582.9
314 | 106 | 586.6 | 656.9 | 570.3 | 583.3
315 | 107 | 587.7 | 647.7 | 570.6 | 584.2
316 | 108 | 589.1 | 643.9 | 561 | 584.5
317 | 109 | 590.4 | 642.9 | 554.7 | 584.5
318 | 110 | 592.1 | 640.4 | 546.9 | 588.5
319 | 111 | 594.7 | 639.5 | 544.3 | 585.3
320 | 112 | 595.2 | 641.6 | 547.7 | 586.1
321 | 113 | 596.7 | 642.6 | 548.5 | 590.6
322 | 114 | 597.5 | 637.1 | 536.4 | 589.3
323 | 115 | 597.9 | 636.3 | 527.2 | 582.4
324 | 116 | 598.3 | 639.9 | 522.6 | 580.4
325 | 117 | 599.6 | 643.4 | 526 | 580.2
326 | 118 | 601.4 | 643 | 527.5 | 585.2
327 | 119 | 602.6 | 639.7 | 528.1 | 588.3
328 | 120 | 603.2 | 635.5 | 530.4 | 591.3
329 | 121 | 603.9 | 635.6 | 529.3 | 594.1
330 | 122 | 604.2 | 630.9 | 524.4 | 591.6
331 | 123 | 604.4 | 625.8 | 529.1 | 592.6
332 | 124 | 605.3 | 621.1 | 531.2 | 592.6
333 | 125 | 606.8 | 616.7 | 522 | 588.4
334 | 126 | 608.5 | 617.4 | 521.2 | 587.3
335 | 127 | 610.7 | 613 | 525 | 589.2
336 | 128 | 613.7 | 613.6 | 533.6 | 599.1
337 | 129 | 617.4 | 614.8 | 533.8 | 604.6
338 | 130 | 620.2 | 614.5 | 528.2 | 602.1
339 | 131 | 621.7 | 610.8 | 524.7 | 605
340 | 132 | 622.8 | 608.8 | 526 | 608.9
341 | 133 | 624.4 | 608.3 | 533.3 | 616.1
342 | 134 | 626.6 | 606.9 | 543.8 | 624.4
343 | 135 | 628.9 | 606.1 | 554.2 | 637.5
344 | 136 | 631.8 | 606.9 | 567.4 | 637.4
345 | 137 | 634.7 | 612.6 | 578.9 | 645.3
346 | 138 | 637.1 | 613.8 | 588.6 | 649.4
347 | 139 | 639.2 | 617.2 | 597.3 | 649.4
348 | 140 | 641.6 | 620 | 602 | 648.4
349 | 141 | 644 | 624 | 598.4 | 645.4
350 | 142 | 646 | 627.6 | 592.2 | 639.3
351 | 143 | 647.8 | 629.7 | 593.4 | 637.6
352 | 144 | 649.6 | 634 | 594.8 | 639.5
353 | 145 | 651.4 | 636.2 | 599.1 | 642.9
354 | 146 | 653.2 | 640.1 | 604.7 | 644.5
355 | 147 | 654.4 | 646.5 | 619.4 | 641.4
356 | 148 | 655.3 | 648 | 615.1 | 640.6
357 | 149 | 656.5 | 651.6 | 623.2 | 643.8
358 | 150 | 657.9 | 651.6 | 624.9 | 647.8
359 | 151 | 658.7 | 646.6 | 613.7 | 648.3
360 | 152 | 658.7 | 641 | 600.3 | 643.6
361 | 153 | 658.4 | 633.1 | 582.2 | 634
362 | 154 | 657.9 | 629.2 | 572.3 | 632.6
363 | 155 | 657.6 | 626.7 | 576.2 | 647.8
364 | 156 | 658.1 | 624.5 | 588.6 | 657.9
365 | 157 | 659.2 | 624.5 | 597 | 660.8
366 | 158 | 660.9 | 623.7 | 601.6 | 658.6
367 | 159 | 662.5 | 625.6 | 602.3 | 653.8
368 | 160 | 664.6 | 633.2 | 602.5 | 652
369 | 161 | 667 | 634.1 | 595.2 | 651.5
370 | 162 | 669 | 635.6 | 596.9 | 654
371 | 163 | 670.8 | 643.8 | 604 | 662.6
372 | 164 | 673 | 648.5 | 616.8 | 662.6
373 | 165 | 675.4 | 652 | 621.2 | 660.2
374 | 166 | 677.7 | 656.8 | 627.2 | 660.9
375 | 167 | 680.3 | 659.4 | 625.7 | 663.5
376 | 168 | 682.6 | 663.5 | 632.7 | 665.4
377 | 169 | 684.3 | 659.5 | 630.8 | 664.5
378 | 170 | 685.2 | 659.3 | 621.2 | 657.8
379 | 171 | 686.4 | 658.4 | 612.8 | 653.8
380 | 172 | 687.3 | 658.4 | 606.1 | 656.5
381 | 173 | 688.2 | 658.1 | 595.2 | 656.1
382 | 174 | 689 | 662.4 | 602.5 | 660.9
383 | 175 | 689.7 | 667.1 | 601.5 | 655.7
384 | 176 | 691 | 673.7 | 591.6 | 652.2
385 | 177 | 692.4 | 675.7 | 583 | 646
386 | 178 | 693.7 | 678.8 | 591.5 | 647.9
387 | 179 | 695.6 | 683.7 | 597.5 | 651.1
388 | 180 | 697.4 | 679.6 | 585.4 | 647.9
389 | 181 | 698.1 | 674.1 | 575.1 | 642.4
390 | 182 | 698.3 | 667.7 | 561.6 | 642.1
391 | 183 | 698.3 | 661 | 543.7 | 638.7
392 | 184 | 697.5 | 656.4 | 529.6 | 636.2
393 | 185 | 697.1 | 651.7 | 522.7 | 638.9
394 | 186 | 697.5 | 648 | 520.8 | 637.7
395 | 187 | 698.8 | 644.8 | 523.7 | 646.5
396 | 188 | 700.9 | 642.7 | 538.6 | 664.9
397 | 189 | 703.9 | 644.2 | 547.4 | 660.9
398 | 190 | 707.1 | 640.5 | 549.8 | 655.1
399 | 191 | 710.5 | 641 | 550.8 | 651.8
400 | 192 | 713.9 | 642.7 | 548.3 | 647.3
401 | 193 | 716.8 | 647.3 | 546.5 | 644.3
402 | 194 | 719.2 | 652.3 | 551 | 646.4
403 | 195 | 721.6 | 656.7 | 560 | 650.2
404 | 196 | 723.9 | 657.5 | 558.3 | 646.8
405 | 197 | 724.9 | 657.2 | 550.4 | 640.6
406 | 198 | 725.1 | 651.9 | 546.7 | 640
407 | 199 | 725.4 | 658 | 558.9 | 644.2
408 | 200 | 727 | 664.8 | 563 | 642.6
409 | 201 | 728.9 | 666.9 | 572.7 | 643.4
410 | 202 | 730.6 | 667.4 | 574.9 | 648.1
411 | 203 | 731.6 | 665.1 | 571 | 643.5
412 | 204 | 732.2 | 660.6 | 567.6 | 641.4
413 | 205 | 732.4 | 656.4 | 562.8 | 639.1
414 | 206 | 732.8 | 652.6 | 555.3 | 636.5
415 | 207 | 732.5 | 647.7 | 545.9 | 632.2
416 | 208 | 731.8 | 644.6 | 534.9 | 630
417 | 209 | 730.4 | 640.6 | 532.7 | 630.3
418 | 210 | 729.5 | 636.2 | 526.7 | 632.2
419 | 211 | 728.8 | 632 | 516.9 | 628.3
420 | 212 | 727.6 | 627.3 | 509.5 | 622.4
421 | 213 | 725.8 | 624.1 | 497.9 | 617.5
422 | 214 | 723.9 | 620.5 | 492.6 | 615.1
423 | 215 | 722.3 | 617.9 | 485.9 | 615.4
424 | 216 | 720.9 | 617.1 | 479.1 | 615.5
425 | 217 | 720.8 | 615.6 | 480.6 | 613.3
426 | 218 | 721.2 | 613.7 | 480.1 | 616.9
427 | 219 | 721.8 | 612.1 | 482.9 | 615.2
428 | 220 | 722.1 | 609.5 | 480.3 | 612.8
429 | 221 | 721.9 | 607.2 | 473.2 | 609.8
430 | 222 | 721.8 | 605.3 | 467.1 | 607.9
431 | 223 | 721.4 | 603.1 | 460.6 | 606.2
432 | 224 | 720.5 | 600.6 | 461.5 | 605.1
433 | 225 | 718.4 | 596.8 | 454.4 | 600.8
434 | 226 | 715.7 | 593.7 | 446.6 | 596.8
435 | 227 | 713.2 | 590.6 | 444.6 | 593
436 | 228 | 710.8 | 589.6 | 448.5 | 593
437 | 229 | 709.2 | 588.9 | 448.4 | 588.2
438 | 230 | 708.5 | 588.9 | 455.3 | 594
439 | 231 | 708.1 | 589.3 | 461.2 | 594.9
440 | 232 | 708.4 | 587.2 | 461.8 | 592.5
441 | 233 | 709 | 591.3 | 472.4 | 592.9
442 | 234 | 710.6 | 591.6 | 481.9 | 596.8
443 | 235 | 711.4 | 589.7 | 486.6 | 595.3
444 | 236 | 710.3 | 587.1 | 486.4 | 592.4
445 | 237 | 708.2 | 582.8 | 476.1 | 585.8
446 | 238 | 703.7 | 576.9 | 456.4 | 574.2
447 | 239 | 696.9 | 571.3 | 437 | 563
448 | 240 | 689.4 | 565.5 | 418.7 | 555.1
449 | 241 | 681.5 | 559.4 | 401.2 | 548.8
450 | 242 | 673.7 | 553.2 | 384.8 | 542.8
451 | 243 | 665.9 | 547.3 | 369.6 | 537.3
452 | 244 | 658.4 | 541.5 | 355.8 | 532.7
453 | 245 | 651.3 | 535.8 | 343.4 | 529
454 | 246 | 644.5 | 530 | 331.4 | 524.2
455 | 247 | 638 | 524.3 | 320.3 | 520.3
456 | 248 | 631.5 | 518.6 | 309.8 | 516.6
457 | 249 | 625.4 | 513.1 | 299.5 | 511.8
458 | 250 | 619.5 | 507.8 | 290 | 508
459 | 251 | 613.8 | 502.1 | 280.6 | 504
460 | 252 | 608.2 | 496.7 | 270.8 | 499.1
461 | 253 | 603 | 490.7 | 261.9 | 494.3
462 | 254 | 598.1 | 484.9 | 253.4 | 489.6
463 | 255 | 593.3 | 479.2 | 245.8 | 486.8
464 | 256 | 588.6 | 473.7 | 238.9 | 483.8
465 | 257 | 584.1 | 468.1 | 232.5 | 481.5
466 | 258 | 579.6 | 462.9 | 226.6 | 479.6
467 | 259 | 575.3 | 457.6 | 221.1 | 475.7
468 | 260 | 571.2 | 452.6 | 215.6 | 471.1
469 | 261 | 567.3 | 448 | 210.2 | 466.4
470 | 262 | 563.4 | 443.4 | 204.8 | 463
471 | 263 | 559.8 | 438.9 | 199.5 | 461.3
472 | 264 | 556.3 | 434.6 | 194.5 | 456.6
473 | 265 | 552.9 | 430 | 190 | 452.1
474 | 266 | 549.7 | 425.4 | 185.7 | 446.9
475 | 267 | 546.6 | 420.2 | 181.4 | 442.4
476 | 268 | 543.5 | 415.1 | 177.1 | 437.8
477 | 269 | 540.4 | 410 | 173.3 | 434.2
478 | 270 | 537.3 | 405.5 | 169.5 | 429.9
479 | 271 | 534.2 | 400.7 | 165.6 | 428.4
480 | 272 | 531.1 | 396.5 | 162.5 | 426.2
481 | 273 | 528 | 392.7 | 159.7 | 422.6
482 | 274 | 525 | 389 | 156.8 | 419.1
483 | 275 | 522.1 | 385.4 | 153.7 | 415.1
484 | 276 | 519.3 | 382.1 | 150.7 | 412.9
485 | 277 | 516.5 | 378.9 | 148.1 | 411.2
486 | 278 | 513.8 | 375.5 | 145.7 | 410.1
487 | 279 | 511 | 372.1 | 143.2 | 405.9
488 | 280 | 508.1 | 368.7 | 140.8 | 401.5
489 | 281 | 505.2 | 365.4 | 138.8 | 397.2
490 | 282 | 502.5 | 362.2 | 136.9 | 393.9
491 | 283 | 499.7 | 358.9 | 134.8 | 392.5
492 | 284 | 496.9 | 355.4 | 132.7 | 389.3
493 | 285 | 494.3 | 352.1 | 130.8 | 386.4
494 | 286 | 491.6 | 348.6 | 128.8 | 382.7
495 | 287 | 488.9 | 345 | 126.9 | 379.9
496 | 288 | 486.2 | 341.2 | 125.1 | 377.5
497 | 289 | 483.7 | 337.9 | 123.3 | 375.2
498 | 290 | 481.1 | 334.7 | 121.6 | 372.5
499 | 291 | 478.5 | 331.9 | 119.9 | 371.9
500 | 292 | 475.9 | 328.7 | 118.5 | 371
501 | 293 | 473.3 | 326 | 117 | 369
502 | 294 | 470.7 | 323.3 | 115.6 | 366.3
503 | 295 | 468.2 | 320.8 | 114.5 | 364.9
504 | 296 | 465.9 | 318.3 | 113.4 | 363.1
505 | 297 | 463.6 | 316.1 | 112.3 | 361.6
506 | 298 | 461.4 | 313.9 | 111.3 | 359.7
507 | 299 | 459.2 | 311.8 | 110.2 | 357.8
508 | 300 | 456.9 | 309.7 | 109.2 | 355.9
509 | 301 | 454.7 | 307.6 | 108.4 | 353.6
510 | 302 | 452.5 | 305.6 | 107.2 | 352
511 | 303 | 450.4 | 303.7 | 106.2 | 349.9
512 | 304 | 448.3 | 301.5 | 104.9 | 347.9
513 | 305 | 446 | 299.5 | 103.8 | 346.1
514 | 306 | 443.7 | 297.5 | 102.7 | 344.2
515 | 307 | 441.6 | 295.6 | 101.7 | 342.6
516 | 308 | 439.4 | 293.5 | 100.7 | 341.3
517 | 309 | 437.3 | 291.4 | 99.8 | 339.9
518 | 310 | 435.2 | 289.5 | 99 | 338.3
519 | 311 | 433.3 | 287.6 | 98.1 | 336.6
520 | 312 | 431.4 | 285.6 | 97 | 334.9
521 | 313 | 429.5 | 283.7 | 95.9 | 333
522 | 314 | 427.7 | 281.8 | 94.8 | 330.7
523 | 315 | 425.9 | 279.9 | 93.7 | 328.4
524 | 316 | 424.2 | 277.9 | 92.7 | 326.6
525 | 317 | 422.3 | 275.8 | 91.6 | 325.5
526 | 318 | 420.5 | 273.8 | 90.6 | 323.7
527 | 319 | 418.7 | 271.8 | 89.6 | 321.7
528 | 320 | 416.9 | 269.8 | 88.7 | 319.9
529 | 321 | 414.9 | 267.9 | 87.9 | 318.7
530 | 322 | 413 | 266.2 | 87.1 | 317.3
531 | 323 | 411.1 | 264.4 | 86.1 | 315.9
532 | 324 | 409.2 | 262.5 | 84.9 | 314.7
533 | 325 | 407.3 | 260.6 | 83.9 | 314.1
534 | 326 | 405.3 | 258.8 | 82.8 | 312.4
535 | 327 | 403.4 | 257 | 81.7 | 310.2
536 | 328 | 401.5 | 255.1 | 80.7 | 308.7
537 | 329 | 399.6 | 253.2 | 79.9 | 307.1
538 | 330 | 397.8 | 251.3 | 79.2 | 305.2
539 | 331 | 396 | 249.6 | 78.5 | 303.6
540 | 332 | 394.4 | 247.8 | 77.7 | 302.6
541 | 333 | 392.8 | 246.3 | 76.9 | 301.5
542 | 334 | 391.2 | 244.9 | 76.1 | 300.2
543 | 335 | 389.5 | 243.3 | 75.3 | 298.7
544 | 336 | 387.6 | 241.8 | 74.5 | 297.3
545 | 337 | 385.7 | 240.4 | 73.9 | 295.8
546 | 338 | 384 | 239.2 | 73.2 | 294.3
547 | 339 | 382.4 | 238 | 72.4 | 292.4
548 | 340 | 380.5 | 236.7 | 71.6 | 290.4
549 | 341 | 378.6 | 235.2 | 70.8 | 288.9

## Test Facts
Last row in IRMS data sheets: | 9
Time when gas burner was ignited: | 208