## Test Conditions
CAROLFIRE Intermediate Scale Preliminary Test Number IP-3 - Circuit Simulator Data Only
Test Date: 10/16/2006
Circuit Simulator Configurations and connections:
|  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 150 VA | 150 VA | 200 VA | 100 VA
| CPT Grounding: | NOT Grounded | Grounded | Grounded | Grounded
| General Config. | Generic MOV-1 | not connected | not connected | not connected
| Cable Type | Item 1: PVC 7/C 12 AWG in a 6-cable bundle in the cable tray at location A | None | None | None
| Wiring Config: | Source Centered
| Circuit Path 1: | Switch Closed: Energized source (connected to fused side of CPT)
| Circuit Path 2: | Switch Closed: Energized source. Conductor is also connected ( at far end of cable) through 1.75 k-ohm resistor to conductor on Circuit Path 7 (indicator simulation)
| Circuit Path 3: | Switch open: not connected
| Circuit Path 4: | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation)
| Circuit Path 5: | Active Target: Connected to Motor Starter
| Circuit Path 6: | Active Target: Connected to Motor Starter
| Circuit Path 7: | Switch Closed - Connects conductor to CPT neutral return. This conductor also connected and to Circuit Path 2 through a 1.75 k-ohm resistor (indicator light simulation)
| Circuit Path 8: | Switch Open: Path is connected to cable's last conductor (spare conductor simulation)
| Circuit Path 9: | Switch Open: not connected
Note: This represents a reduced data file. That is, the raw data was 'filtered' to reduce the high density of data associated with the 5hz scan rate for the circuit simulators in order to maintain a manageable file size for this processed data file. The data between 0 and 325 seconds reports the values recorded every five seconds. The data between 325 and 350 seconds reports the values recorded every 1 second. The data beyond 350 s is the full density 5hz data as recorded. Data after the circuit simulator was turned off has also been deleted. The full raw data files are available as a part of the test records.

## C1 Circuit Response
Summary of Observed Faulting Behavior for Circuit #1
DAQ Time | Burner Time | Event | Discussion
208 | 0 | Ignited Gas Burner
365 | 157 | Increase in Current on Circuit Paths 2 and 7 | While the leakage current is initially small (on the order of 0.1 amps) this is the first clear indication of cable degradation. The initial leakage is observed between one of the two energized source conductor and the one grounded return conductor (Path 7).
366 | 158 | Increase in voltage on Path 6 | The target conductor on Path 6 takes a solid hit from one of the two source conductors, most likely the conductor on Path 2 given essentially no current indicated for the conductor on Path 1.
367 | 159 | Increase in voltage on Path 5 | Shortly after actuation of the motor starter on path 6, an actuation of the motor starter on Path 5 also was observed. The starter initially chattered, but then did lock in.
368-372 | 160-164 | Increased in leakage from Path 2 to Path 7 | During this period the leakage from the conductor on Path 2 to that on Path 7 increases to a peak of about 2A.
375 | 167 | Decreased voltage on Path 6 | At this point, a chattering of one or both motor starters was noted. Based on the data, it appears the motor starter on Path 6 was the likely cause, and that it did chatter for a short period of time (1-2 seconds) before re-locking.
377 | 169 | Sharp drop in leakage to Path 7 | A sharp drop in the leakage current from Path 2 to Path 7 is observed. The leakage remains at a level of less than 1A.
401 | 193 | Fuse Blow | A spike in current is observed on Path 7, and while the data do not reflect a current high enough to trip the fuse, the fuse did trip and likely the peak occurred between data samples. Loss of the fuse de-energized the circuit.
Final Observations |  | Hot short spurious actuations were observed and were sustained for a total of approximately 35s. Voltages to the targets do fluctuate, and some chattering and drop out was noted before re-locking. There are only minimal signs of voltage degradation (~10V drop) prior to fuse blow.

## Converted Data C1
DAQ Time | Burner Time | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V3 | C1 A3 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6 | C1 V7 | C1 A7 | C1 V8 | C1 A8
0 | -208 | 132.5735 | 0.091876 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208 | 0.20087 | 0.076367 | 1.9442 | 0.0019433
60 | -148 | 132.3787 | 0.088629 | 132.0758 | 0.0048528 | 0.0053935 | 1.6859e-05 | 0.092701 | -0.0026345 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777 | 0.10349 | 0.076367 | 1.8468 | 0.00032025
120 | -88 | 132.7683 | 0.082136 | 132.3679 | 0.0016062 | 0.20015 | 0.0016399 | 0.48226 | 0.00061214 | 0.53384 | 0.00012922 | 0.48328 | 0.0019208 | 0.29825 | 0.079614 | 2.2364 | 0.0019433
180 | -28 | 132.6709 | 0.091876 | 132.2706 | 0.0064758 | 0.0053935 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.076367 | 1.9442 | 0.0019433
240 | 32 | 132.4761 | 0.091876 | 132.0758 | 0.0048528 | 0.10277 | 0.0016399 | 0.19008 | 0.00061214 | 0.33904 | 0.00012922 | 0.28848 | 0.0019208 | 0.20087 | 0.077991 | 1.9442 | 0.0019433
300 | 92 | 132.3787 | 0.087005 | 131.881 | 0.0016062 | 0.10277 | 1.6859e-05 | 0.38488 | 0.00061214 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.10349 | 0.077991 | 2.2364 | 0.0019433
330 | 122 | 132.6709 | 0.082136 | 132.2706 | 0.0016062 | 0.10277 | 0.0016399 | 0.38488 | 0.00061214 | 0.53384 | 0.0017522 | 0.48328 | 0.00029777 | 0.39567 | 0.079614 | 3.0156 | 0.0035663
350 | 142 | 132.0865 | 0.085382 | 131.6862 | 0.0016062 | 0.10277 | 0.0016399 | 0.28746 | 0.0022351 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.077991 | 8.9568 | 0.0019433
360 | 152 | 131.8917 | 0.087005 | 131.2966 | 0.0016062 | 0.10277 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.29825 | 0.079614 | 12.7552 | 0.0019433
360.2 | 152.2 | 132.0865 | 0.085382 | 131.4914 | 0.0016062 | 0.49237 | -0.0016068 | 0.38488 | 0.00061214 | 0.33904 | 0.00012922 | 0.28848 | 0.00029777 | 0.59047 | 0.081237 | 12.7552 | 0.0019433
360.4 | 152.4 | 131.7944 | 0.082136 | 131.4914 | 0.0016062 | 0.10277 | -0.0032298 | 0.38488 | 0.00061214 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.081237 | 12.7552 | 0.0019433
360.6 | 152.6 | 131.7944 | 0.087005 | 131.6862 | 0.0016062 | 0.10277 | 1.6859e-05 | 0.28746 | -0.0010109 | 0.33904 | 0.00012922 | 0.28848 | 0.00029777 | 0.10349 | 0.081237 | 13.2422 | 0.0019433
360.8 | 152.8 | 131.7944 | 0.087005 | 131.2966 | 0.0016062 | 0.10277 | 1.6859e-05 | 0.38488 | 0.00061214 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.081237 | 13.6318 | 0.0019433
361 | 153 | 131.8917 | 0.085382 | 131.394 | -0.0016405 | 0.10277 | 1.6859e-05 | 0.092701 | 0.0038588 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.08286 | 13.2422 | 0.0019433
361.2 | 153.2 | 131.8917 | 0.087005 | 131.4914 | 0.0016062 | 0.10277 | 0.0032635 | 0.38488 | 0.00061214 | 0.24166 | 0.00012922 | 0.77546 | 0.00029777 | 0.29825 | 0.081237 | 12.95 | -0.0013034
361.4 | 153.4 | 131.6969 | 0.085382 | 131.4914 | -0.0032635 | 0.10277 | 1.6859e-05 | 0.092701 | -0.0010109 | 0.33904 | 0.00012922 | 0.38586 | -0.0013259 | 0.20087 | 0.081237 | 12.6579 | 0.0051899
361.6 | 153.6 | 131.8917 | 0.087005 | 131.4914 | 0.0032298 | -0.092027 | 0.0048865 | 0.28746 | -0.0010109 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.081237 | 12.7552 | 0.0019433
361.8 | 153.8 | 131.9892 | 0.085382 | 131.4914 | 0.0016062 | 0.10277 | 0.0065095 | 0.28746 | 0.00061214 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.084483 | 13.0474 | 0.0019433
362 | 154 | 131.7944 | 0.083759 | 131.394 | 0.0016062 | 0.0053935 | 0.0032635 | 0.28746 | 0.0038588 | 0.33904 | -0.0014944 | 0.48328 | 0.00029777 | 0.39567 | 0.08286 | 11.5865 | 0.0068129
362.2 | 154.2 | 131.8917 | 0.085382 | 131.4914 | 0.0016062 | 0.0053935 | 0.0032635 | 0.48226 | 0.0038588 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.08286 | 11.4891 | 0.00032025
362.4 | 154.4 | 131.8917 | 0.083759 | 131.4914 | 0.0032298 | 0.10277 | 1.6859e-05 | 0.28746 | -0.0010109 | 0.33904 | -0.0014944 | 0.38586 | 0.00029777 | 0.20087 | 0.084483 | 12.95 | -0.0013034
362.6 | 154.6 | 131.8917 | 0.085382 | 131.5888 | 0.0016062 | 0.10277 | 0.0032635 | -0.0047195 | 0.0022351 | 0.24166 | 0.00012922 | 0.38586 | 0.0051674 | 0.29825 | 0.084483 | 13.437 | 0.0019433
362.8 | 154.8 | 131.6969 | 0.087005 | 131.4914 | 0.0016062 | 0.10277 | 0.0016399 | 0.28746 | 0.0022351 | 0.43642 | 0.00012922 | 0.38586 | 0.00029777 | 0.20087 | 0.08773 | 16.9433 | 0.0035663
363 | 155 | 131.7944 | 0.085382 | 131.394 | 0.0016062 | 0.20015 | 0.0016399 | 0.38488 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777 | 0.68785 | 0.08286 | 11.9761 | 0.0019433
363.2 | 155.2 | 131.9892 | 0.088629 | 131.6862 | -1.6843e-05 | 0.20015 | 1.6859e-05 | 0.38488 | 0.0022351 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.084483 | 12.5604 | 0.0019433
363.4 | 155.4 | 131.7944 | 0.083759 | 131.394 | 0.0016062 | 0.10277 | 0.0016399 | 0.28746 | 0.00061214 | 0.43642 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.08773 | 15.2876 | 0.0019433
363.6 | 155.6 | 131.8917 | 0.087005 | 131.2966 | 0.0032298 | 0.0053935 | 0.0016399 | 0.38488 | -0.0010109 | 0.14424 | -0.0014944 | 0.38586 | 0.00029777 | 0.29825 | 0.094223 | 19.3782 | 0.0019433
363.8 | 155.8 | 131.8917 | 0.085382 | 131.1992 | 0.0048528 | 0.10277 | 1.6859e-05 | 0.57968 | 0.00061214 | 0.9234 | 0.00012922 | 0.67808 | 0.00029777 | 0.39567 | 0.08286 | 8.5672 | 0.0019433
364 | 156 | 131.6969 | 0.083759 | 131.2966 | 0.0032298 | 0.10277 | 1.6859e-05 | 0.28746 | 0.0022351 | 0.53384 | 0.0017522 | 0.19109 | 0.00029777 | 0.20087 | 0.086107 | 9.6385 | 0.0019433
364.2 | 156.2 | 131.6969 | 0.083759 | 131.2966 | 0.0032298 | 0.20015 | 1.6859e-05 | 0.28746 | 0.00061214 | 0.43642 | -0.0014944 | 0.38586 | 0.00029777 | 0.29825 | 0.08773 | 11.2943 | 0.0019433
364.4 | 156.4 | 131.6969 | 0.083759 | 131.2966 | 0.0097225 | 0.10277 | 1.6859e-05 | 0.48226 | -0.0010109 | 0.33904 | 0.0033759 | 0.28848 | 0.00029777 | 0.29825 | 0.09747 | 24.248 | 0.0068129
364.6 | 156.6 | 131.5996 | 0.083759 | 131.1992 | 0.050304 | 0.20015 | 1.6859e-05 | 1.4562 | 0.00061214 | 0.33904 | 0.0033759 | 0.19109 | 0.0035444 | 0.20087 | 0.11857 | 25.9038 | 0.0051899
364.8 | 156.8 | 131.0152 | 0.085382 | 130.7122 | 0.089263 | 0.10277 | 1.6859e-05 | 1.8458 | 0.0022351 | 0.82602 | 0.00012922 | 0.48328 | 0.0051674 | 0.29825 | 0.13318 | 21.2287 | 0.0051899
365 | 157 | 130.8204 | 0.085382 | 130.7122 | 0.11199 | 0.20015 | 0.0032635 | 1.7484 | 0.0022351 | 4.8193 | 0.026101 | 0.58066 | 0.0019208 | 0.20087 | 0.15428 | 19.086 | 0.0035663
365.2 | 157.2 | 131.5996 | 0.085382 | 129.8357 | 0.10712 | 0.20015 | -0.0016068 | 2.4302 | 0.0054818 | 2.5791 | 0.013115 | 0.97026 | 0.0019208 | 0.49305 | 0.1624 | 20.547 | -0.0013034
365.4 | 157.4 | 130.8204 | 0.085382 | 130.5174 | 0.13309 | 0.10277 | -0.0080995 | 1.9432 | 0.0022351 | 2.6766 | 0.068307 | 1.2624 | 0.0035444 | 0.39567 | 0.16889 | 17.3329 | 0.0019433
365.6 | 157.6 | 130.6256 | 0.087005 | 130.2252 | 0.17692 | 0.10277 | 0.0048865 | 1.5536 | 0.00061214 | 7.1568 | 0.0049989 | 5.6453 | 0.0019208 | 0.20087 | 0.17214 | 15.2876 | 0.0019433
365.8 | 157.8 | 130.1386 | 0.070772 | 130.42 | 0.19315 | 0.20015 | 0.0048865 | 1.0667 | 0.00061214 | 6.1828 | 0.013115 | 7.5932 | 0.011661 | 0.39567 | 0.17052 | 17.7225 | 0.0019433
366 | 158 | 129.1647 | 0.057786 | 128.1799 | 0.2873 | 0.58976 | 0.0048865 | 0.96924 | -0.0010109 | 3.9427 | 0.021232 | 26.5855 | 0.48566 | 0.98003 | 0.18513 | 20.2548 | 0.0051899
366.2 | 158.2 | 121.3729 | 0.098368 | 126.3294 | 0.1266 | 0.88194 | 0.0097562 | 6.8131 | 0.0071055 | 2.0922 | 0.011492 | 13.924 | 0.16587 | 0.39567 | 0.20136 | 17.8198 | 0.0019433
366.4 | 158.4 | 129.4568 | 0.085382 | 128.8617 | 0.35061 | 0.10277 | 0.0016399 | 1.5536 | 0.00061214 | 5.7933 | 0.021232 | 31.358 | 0.17236 | 0.29825 | 0.20461 | 19.3782 | 0.00032025
366.6 | 158.6 | 127.9959 | 0.085382 | 127.7903 | 0.51294 | 0.10277 | 1.6859e-05 | 1.2614 | -0.0010109 | 10.5657 | 0.058567 | 52.493 | 0.31034 | 0.10349 | 0.21435 | 20.2548 | 0.0019433
366.8 | 158.8 | 127.9959 | 0.080513 | 127.4007 | 0.58923 | 0.20015 | 1.6859e-05 | 1.4562 | 0.0022351 | 5.0141 | 0.027725 | 64.5702 | 0.38014 | 0.39567 | 0.24194 | 21.6183 | 0.0035663
367 | 159 | 128.5803 | 0.085382 | 127.9851 | 0.47398 | 0.10277 | 0.0032635 | 1.164 | -0.0010109 | 6.0854 | 0.039088 | 44.7987 | 0.26976 | 0.29825 | 0.2598 | 17.625 | 0.00032025
367.2 | 159.2 | 127.0219 | 0.069149 | 127.0111 | 0.51294 | 0.20015 | -0.0048528 | 1.2614 | 0.00061214 | 3.7479 | 0.021232 | 48.1102 | 0.27301 | 0.39567 | 0.29551 | 17.7225 | 0.0051899
367.4 | 159.4 | 126.3401 | 0.13246 | 125.745 | 0.59735 | 0.49237 | 1.6859e-05 | 0.87186 | 0.0022351 | 3.3583 | 0.017985 | 52.006 | 0.35417 | 0.78523 | 0.34258 | 14.1188 | 0.00032025
367.6 | 159.6 | 127.4115 | 0.088629 | 127.2059 | 0.59086 | -0.092027 | -0.0016068 | 0.77444 | 0.00061214 | 8.8125 | 0.063437 | 45.3831 | 0.25353 | 0.29825 | 0.33447 | 15.4823 | -0.0013034
367.8 | 159.8 | 126.6323 | 0.083759 | 126.4267 | 0.73208 | 0.0053935 | 1.6859e-05 | 0.87186 | 0.00061214 | 22.0585 | 0.17382 | 50.6425 | 0.3006 | 0.29825 | 0.34908 | 19.2808 | 0.0019433
368 | 160 | 125.9505 | 0.077266 | 125.9398 | 0.78403 | 0.20015 | 1.6859e-05 | 1.2614 | 0.0022351 | 47.479 | 0.30206 | 83.7573 | 0.13178 | 0.59047 | 0.4903 | 41.2924 | 0.0035663
368.2 | 160.2 | 126.7297 | 0.069149 | 124.771 | 0.79214 | -1.066 | 0.0065095 | 7.5922 | 0.013598 | 60.3353 | 0.37835 | 81.712 | 0.74376 | 0.68785 | 0.44972 | 47.818 | 0.019799
368.4 | 160.4 | 125.4636 | 0.085382 | 124.771 | 0.93824 | 0.10277 | 1.6859e-05 | 11.0011 | 0.0038588 | 53.7123 | 0.34426 | 80.251 | 0.084708 | 0.10349 | 0.62179 | 59.3108 | 0.0019433
368.6 | 160.6 | 121.8599 | 0.083759 | 121.6543 | 1.4106 | 0.20015 | 0.0032635 | 8.274 | 0.00061214 | 62.3806 | 0.41893 | 96.3215 | 0.071722 | 0.29825 | 1.086 | 64.278 | 0.0068129
368.8 | 160.8 | 121.5677 | 0.083759 | 121.0699 | 1.4658 | 0.20015 | 1.6859e-05 | 8.5662 | 0.0022351 | 65.9843 | 0.43517 | 99.7303 | 0.065229 | 0.29825 | 1.1088 | 62.3301 | 0.0068129
369 | 161 | 122.3469 | 0.074019 | 122.4335 | 1.2353 | 0.0053935 | -0.0016068 | 11.1959 | -0.0075042 | 80.0094 | 0.097525 | 107.9116 | 0.070098 | -0.48092 | 1.2045 | 67.7843 | 0.011683
369.2 | 161.2 | 122.5417 | 0.085382 | 121.4595 | 1.3002 | 0.49237 | 1.6859e-05 | 7.1052 | 0.028208 | 77.0875 | 0.053697 | 107.7168 | 0.061982 | 0.39567 | 1.3019 | 57.9472 | 0.0019433
369.4 | 161.4 | 125.6584 | 0.080513 | 125.258 | 0.92038 | 0.20015 | -0.0032298 | 22.1043 | -0.0042575 | 104.3585 | 0.061813 | 114.9242 | 0.065229 | 0.0060648 | 0.888 | 78.8875 | 0.0051899
369.6 | 161.6 | 125.3662 | 0.091876 | 125.0632 | 0.90902 | -0.092027 | -0.0048528 | 23.4678 | -0.0026345 | 96.9564 | 0.06993 | 116.2877 | 0.087955 | 0.29825 | 0.888 | 65.0572 | 0.0019433
369.8 | 161.8 | 124.0026 | 0.087005 | 123.6023 | 1.1476 | 0.20015 | -0.0016068 | 34.571 | 0.00061214 | 98.32 | 0.06506 | 116.2877 | 0.084708 | 0.20087 | 1.1218 | 68.953 | -0.0029264
370 | 162 | 125.6584 | 0.087005 | 125.1606 | 0.91226 | 0.20015 | 1.6859e-05 | 37.9799 | 0.0022351 | 86.2428 | 0.055321 | 120.6706 | 0.087955 | 0.10349 | 0.888 | 75.8682 | 0.0019433
370.2 | 162.2 | 126.1453 | 0.085382 | 125.745 | 0.84084 | 0.10277 | 0.0016399 | 48.9858 | 0.0054818 | 88.6777 | 0.055321 | 121.5472 | 0.087955 | 0.29825 | 0.80684 | 70.3166 | 0.0051899
370.4 | 162.4 | 125.3662 | 0.088629 | 124.6736 | 0.89765 | -0.38421 | -0.0097232 | 44.7003 | 0.011975 | 86.9245 | 0.058567 | 119.307 | 0.070098 | 0.49305 | 0.87502 | 76.9396 | 0.0084366
370.6 | 162.6 | 124.6844 | 0.090252 | 124.0893 | 1.0502 | 0.0053935 | -0.0032298 | 47.33 | 0.016845 | 86.6324 | 0.05045 | 116.8721 | 0.066852 | 0.68785 | 1.0227 | 74.9916 | 0.0051899
370.8 | 162.8 | 123.9052 | 0.074019 | 123.0179 | 1.1606 | 0.20015 | 1.6859e-05 | 45.0899 | 0.023338 | 86.048 | 0.048827 | 116.0929 | 0.089578 | 0.0060648 | 1.1185 | 62.3301 | 0.00032025
371 | 163 | 123.7104 | 0.05454 | 122.8231 | 1.0681 | 0.39495 | -0.0016068 | 45.8691 | 0.016845 | 85.9506 | 0.052074 | 116.2877 | 0.065229 | 0.20087 | 1.0341 | 58.5316 | 0.0051899
371.2 | 163.2 | 124.1974 | 0.082136 | 123.6997 | 1.1087 | 0.39495 | 0.0065095 | 61.3551 | 0.024961 | 94.8137 | 0.06019 | 116.5799 | 0.083085 | 0.29825 | 1.0584 | 67.0051 | 0.0068129
371.4 | 163.4 | 118.451 | 0.15356 | 122.9205 | 1.1184 | 1.0767 | 0.0097562 | 43.8237 | 0.031455 | 86.048 | 0.052074 | 116.6773 | 0.12042 | 0.68785 | 1.0877 | 69.3426 | 0.0035663
371.6 | 163.6 | 122.5417 | 0.10486 | 123.1153 | 1.1217 | 0.29757 | 1.6859e-05 | 53.8556 | 0.041194 | 92.2813 | 0.052074 | 117.2617 | 0.12204 | 1.6618 | 1.0974 | 62.9144 | 0.00032025
371.8 | 163.8 | 122.5417 | 0.075642 | 121.0699 | 1.1558 | 0.0053935 | -0.0048528 | 51.9076 | 0.015222 | 92.184 | 0.053697 | 116.3851 | 0.083085 | 0.29825 | 1.1445 | 60.2847 | 0.0035663
372 | 164 | 119.2302 | 0.080513 | 119.3168 | 1.6281 | 0.20015 | 1.6859e-05 | 31.844 | 0.015222 | 89.5542 | 0.056944 | 113.5606 | 0.079838 | 0.20087 | 1.6087 | 63.8884 | 0.0019433
372.2 | 164.2 | 117.8667 | 0.075642 | 117.0767 | 1.9706 | 0.10277 | -0.0016068 | 45.0899 | 0.015222 | 96.7616 | 0.058567 | 108.8856 | 0.071722 | 0.29825 | 1.9464 | 61.2587 | -0.0013034
372.4 | 164.4 | 116.6979 | 0.075642 | 116.2001 | 2.146 | 0.20015 | 1.6859e-05 | 37.6877 | 0.015222 | 89.8464 | 0.058567 | 110.2492 | 0.073345 | 0.0060648 | 2.1282 | 61.8431 | 0.0035663
372.6 | 164.6 | 117.3797 | 0.078889 | 116.8819 | 2.0372 | -0.092027 | -0.0032298 | 39.5383 | 0.0087285 | 83.0287 | 0.045581 | 111.0283 | 0.052243 | 0.10349 | 2.0211 | 44.1169 | 0.00032025
372.8 | 164.8 | 119.912 | 0.080513 | 119.5116 | 1.719 | 0.20015 | -0.0032298 | 48.4014 | 0.018468 | 78.8406 | 0.052074 | 114.4372 | 0.079838 | 0.10349 | 1.685 | 57.655 | 0.00032025
373 | 165 | 123.7104 | 0.083759 | 123.2127 | 1.198 | 0.20015 | 0.0016399 | 78.2047 | 0.037947 | 96.859 | 0.073176 | 118.9175 | 0.086331 | 0.29825 | 1.1396 | 64.9598 | 0.0035663
373.2 | 165.2 | 121.8599 | 0.067526 | 121.6543 | 1.3197 | 0.20015 | 1.6859e-05 | 74.114 | 0.033078 | 94.8137 | 0.06019 | 116.8721 | 0.079838 | 0.29825 | 1.2711 | 64.3754 | 0.0035663
373.4 | 165.4 | 123.9052 | 0.085382 | 123.4075 | 1.1493 | 0.20015 | 1.6859e-05 | 83.5615 | 0.046064 | 101.4366 | 0.06993 | 118.82 | 0.087955 | 0.20087 | 1.0942 | 64.765 | 0.0019433
373.6 | 165.6 | 124.0026 | 0.082136 | 123.6023 | 1.1525 | 0.10277 | 1.6859e-05 | 80.0552 | 0.046064 | 99.7809 | 0.066683 | 120.1836 | 0.086331 | 0.29825 | 1.0974 | 61.2587 | 0.0035663
373.8 | 165.8 | 122.8339 | 0.083759 | 122.3361 | 1.3181 | 0.20015 | 1.6859e-05 | 70.6078 | 0.039571 | 95.398 | 0.06506 | 119.2096 | 0.087955 | 0.29825 | 1.276 | 52.2008 | 0.0035663
374 | 166 | 121.9573 | 0.087005 | 121.6543 | 1.383 | 0.10277 | 1.6859e-05 | 75.3802 | 0.041194 | 98.1252 | 0.06506 | 116.5799 | 0.083085 | 0.29825 | 1.3328 | 59.2134 | 0.0019433
374.2 | 166.2 | 123.0287 | 0.083759 | 122.6283 | 1.2645 | 0.10277 | 1.6859e-05 | 85.1198 | 0.047687 | 110.8841 | 0.078046 | 119.794 | 0.084708 | 0.10349 | 1.2029 | 65.1546 | 0.0035663
374.4 | 166.4 | 122.1521 | 0.083759 | 121.6543 | 1.3976 | 0.20015 | 0.0016399 | 85.5094 | 0.047687 | 110.8841 | 0.078046 | 118.9175 | 0.084708 | 0.29825 | 1.336 | 63.4988 | 0.0019433
374.6 | 166.6 | 118.0615 | 0.083759 | 117.4663 | 1.9869 | 0.10277 | 1.6859e-05 | 72.8479 | 0.047687 | 101.1444 | 0.073176 | 104.5028 | 0.073345 | 0.20087 | 1.9399 | 69.7322 | 0.0035663
374.8 | 166.8 | 119.2302 | 0.078889 | 118.8298 | 1.8083 | 0.0053935 | 0.0016399 | 66.4197 | 0.033078 | 92.6709 | 0.061813 | 72.3619 | 0.25678 | 0.49305 | 1.5454 | 39.7341 | -0.0013034
375 | 167 | 121.8599 | 0.083759 | 121.5569 | 1.4236 | 0.20015 | 0.0016399 | 70.5104 | 0.037947 | 95.3006 | 0.063437 | 72.1671 | 0.086331 | 0.29825 | 1.3652 | 43.2403 | 0.0035663
375.2 | 167.2 | 119.912 | 0.083759 | 119.2194 | 1.7499 | 0.10277 | 1.6859e-05 | 71.6791 | 0.039571 | 97.6382 | 0.068307 | 60.8691 | 0.27463 | 0.29825 | 1.4886 | 48.2076 | 0.0035663
375.4 | 167.4 | 118.938 | 0.077266 | 118.3429 | 1.8651 | 0.29757 | 0.0016399 | 72.2635 | 0.039571 | 99.8783 | 0.068307 | 55.9993 | 0.32982 | 0.39567 | 1.5406 | 43.0455 | -0.0013034
375.6 | 167.6 | 118.8406 | 0.078889 | 118.4402 | 1.8262 | 0.0053935 | 1.6859e-05 | 80.1526 | 0.044441 | 106.7934 | 0.078046 | 45.0909 | 0.31197 | 0.39567 | 1.5341 | 50.9347 | 0.0035663
375.8 | 167.8 | 119.425 | 0.082136 | 119.122 | 1.7791 | 0.29757 | 1.6859e-05 | 83.8537 | 0.04931 | 109.3258 | 0.07967 | 45.4804 | 0.30223 | 0.29825 | 1.4773 | 58.2394 | 0.0035663
376 | 168 | 121.6651 | 0.083759 | 121.0699 | 1.469 | 0.20015 | 0.0016399 | 90.3793 | 0.05418 | 113.2216 | 0.084539 | 69.3426 | 0.15289 | 0.20087 | 1.336 | 70.1218 | 0.0035663
376.2 | 168.2 | 121.9573 | 0.085382 | 121.2647 | 1.4869 | 0.20015 | 0.0016399 | 85.9964 | 0.050934 | 113.0268 | 0.082916 | 67.2973 | 0.11068 | 0.20087 | 1.4026 | 67.979 | 0.0035663
376.4 | 168.4 | 118.1588 | 0.082136 | 117.2715 | 2.0664 | 0.10277 | 1.6859e-05 | 70.413 | 0.042818 | 107.67 | 0.076423 | 64.8624 | 0.26976 | 0.29825 | 1.875 | 63.791 | 0.0035663
376.6 | 168.6 | 119.0354 | 0.083759 | 116.9793 | 2.055 | 0.20015 | 0.0016399 | 50.9337 | 0.029831 | 107.67 | 0.078046 | 58.142 | 0.32982 | 0.29825 | 1.7938 | 57.9472 | 0.0035663
376.8 | 168.8 | 117.5745 | 0.082136 | 116.7845 | 2.1005 | 0.20015 | 0.0016399 | 64.1796 | 0.031455 | 107.183 | 0.076423 | 66.9077 | 0.28924 | 0.29825 | 1.8961 | 64.3754 | 0.0035663
377 | 169 | 117.8667 | 0.085382 | 117.4663 | 2.068 | 0.20015 | 1.6859e-05 | 67.1989 | 0.034701 | 107.2804 | 0.076423 | 63.304 | 0.066852 | 0.39567 | 2.0243 | 61.9405 | 0.0035663
377.2 | 169.2 | 115.7239 | 0.082136 | 115.1288 | 2.3554 | 0.20015 | 0.0016399 | 67.6859 | 0.039571 | 105.4299 | 0.078046 | 64.765 | 0.38988 | 0.29825 | 2.0519 | 63.4014 | 0.0035663
377.4 | 169.4 | 123.7104 | 0.085382 | 123.5049 | 1.1655 | 0.10277 | 1.6859e-05 | 82.6849 | 0.046064 | 117.9941 | 0.084539 | 81.9067 | 0.10906 | 0.29825 | 1.0698 | 78.3031 | 0.0035663
377.6 | 169.6 | 123.5156 | 0.078889 | 124.284 | 0.73208 | 0.97936 | 0.01625 | 101.9695 | 0.15807 | 115.2669 | 0.061813 | 87.0688 | 0.053866 | 1.8566 | 0.60393 | 83.0755 | 0.0051899
377.8 | 169.8 | 125.2688 | 0.087005 | 124.8684 | 0.95772 | 0.10277 | 0.0016399 | 86.7756 | 0.050934 | 118.0914 | 0.086162 | 90.5751 | 0.058735 | 0.29825 | 0.87664 | 89.4063 | 0.0068129
378 | 170 | 124.3922 | 0.080513 | 123.6997 | 0.85707 | 2.6351 | -0.021086 | 93.3011 | 0.050934 | 115.7539 | 0.076423 | 89.3089 | 0.061982 | 1.467 | 0.77438 | 90.1855 | 0.00032025
378.2 | 170.2 | 123.6131 | 0.083759 | 125.8424 | 0.86357 | 2.5377 | 0.0016399 | 97.5866 | 0.05418 | 118.0914 | 0.082916 | 88.0427 | 0.053866 | 0.78523 | 0.77438 | 84.8287 | 0.0035663
378.4 | 170.4 | 127.8011 | 0.085382 | 127.5955 | 0.53729 | 0.0053935 | 0.0016399 | 109.2742 | 0.065543 | 122.8639 | 0.091033 | 103.9184 | 0.068475 | 0.29825 | 0.41726 | 97.5876 | 0.0035663
378.6 | 170.6 | 126.6323 | 0.083759 | 126.5242 | 0.68987 | -0.092027 | 0.0016399 | 105.6705 | 0.062296 | 120.9159 | 0.087786 | 104.8923 | 0.066852 | 0.29825 | 0.57958 | 68.1738 | 0.0019433
378.8 | 170.8 | 126.8271 | 0.083759 | 126.719 | 0.68014 | 0.10277 | 0.0016399 | 111.6117 | 0.065543 | 121.6951 | 0.089409 | 118.4305 | 0.079838 | 0.29825 | 0.56822 | 83.4651 | 0.0051899
379 | 171 | 127.8985 | 0.085382 | 127.6929 | 0.54053 | 0.10277 | 1.6859e-05 | 117.8451 | 0.06879 | 123.643 | 0.091033 | 122.5211 | 0.087955 | 0.39567 | 0.41563 | 78.4005 | 0.0035663
379.2 | 171.2 | 128.4829 | 0.085382 | 128.4721 | 0.44801 | 0.10277 | 0.0016399 | 119.793 | 0.073659 | 124.2274 | 0.092656 | 123.5925 | 0.094447 | 0.29825 | 0.32473 | 106.4507 | 0.0019433
379.4 | 171.4 | 128.6777 | 0.085382 | 128.6669 | 0.39282 | 0.10277 | 1.6859e-05 | 104.7939 | 0.062296 | 119.0654 | 0.087786 | 122.2289 | 0.087955 | 0.29825 | 0.27441 | 113.658 | 0.0035663
379.6 | 171.6 | 129.6516 | 0.087005 | 129.3486 | 0.29704 | 0.20015 | 0.0016399 | 81.0292 | 0.046064 | 117.1175 | 0.082916 | 122.3263 | 0.087955 | 0.10349 | 0.18188 | 117.4565 | 0.0035663
379.8 | 171.8 | 127.7037 | 0.085382 | 128.7643 | 0.29704 | 0.29757 | 1.6859e-05 | 101.1903 | 0.05418 | 115.1695 | 0.086162 | 122.4237 | 0.089578 | 0.10349 | 0.17214 | 118.7227 | 0.0051899
380 | 172 | 123.3208 | 0.077266 | 125.6476 | 0.33438 | 18.8029 | 0.0016399 | 85.8016 | 0.044441 | 112.6372 | 0.07967 | 120.6706 | 0.086331 | 10.3301 | 0.21435 | 117.2617 | 0.0051899
380.2 | 172.2 | 129.262 | 0.085382 | 129.0565 | 0.33762 | 0.20015 | 1.6859e-05 | 104.8914 | 0.05905 | 113.806 | 0.07967 | 121.4497 | 0.089578 | 0.29825 | 0.20623 | 117.6513 | 0.0051899
380.4 | 172.4 | 129.6516 | 0.085382 | 129.4461 | 0.32464 | 0.10277 | 1.6859e-05 | 89.7949 | 0.05418 | 116.6305 | 0.066683 | 118.4305 | 0.084708 | 8.4796 | 0.19487 | 114.632 | 0.0068129
380.6 | 172.6 | 128.8725 | 0.085382 | 128.4721 | 0.41716 | 0.10277 | 1.6859e-05 | 86.5808 | 0.052557 | 107.9622 | 0.078046 | 118.9175 | 0.084708 | 0.39567 | 0.302 | 113.0736 | 0.0035663
380.8 | 172.8 | 127.3141 | 0.085382 | 127.2059 | 0.61845 | 0.10277 | 1.6859e-05 | 75.6724 | 0.042818 | 99.3913 | 0.06506 | 113.8528 | 0.076592 | 0.20087 | 0.53413 | 98.2694 | 0.0035663
381 | 173 | 126.6323 | 0.099992 | 126.2319 | 0.65741 | 0.49237 | 0.0065095 | 68.5624 | 0.044441 | 98.1252 | 0.071553 | 112.6841 | 0.079838 | 0.29825 | 0.56984 | 92.036 | 0.00032025
381.2 | 173.2 | 129.0672 | 0.083759 | 128.8617 | 0.40905 | 0.10277 | 1.6859e-05 | 89.9897 | 0.044441 | 112.9294 | 0.078046 | 121.255 | 0.084708 | 0.29825 | 0.29389 | 112.9763 | 0.0035663
381.4 | 173.4 | 129.749 | 0.087005 | 129.4461 | 0.32302 | 0.10277 | 0.0016399 | 109.956 | 0.060673 | 116.8253 | 0.082916 | 123.3003 | 0.087955 | 0.29825 | 0.19324 | 118.7227 | 0.0035663
381.6 | 173.6 | 128.9699 | 0.088629 | 128.2773 | 0.37658 | -0.38421 | 0.0048865 | 103.9174 | 0.05418 | 111.5659 | 0.078046 | 118.5279 | 0.092824 | -0.48092 | 0.21922 | 104.9898 | -0.0094198
381.8 | 173.8 | 129.0672 | 0.085382 | 128.7643 | 0.42528 | 0.10277 | 0.0016399 | 109.2742 | 0.062296 | 112.345 | 0.078046 | 120.768 | 0.086331 | 0.29825 | 0.30525 | 117.0669 | 0.0035663
382 | 174 | 128.7751 | 0.093499 | 128.4721 | 0.43015 | 0.29757 | 0.0048865 | 107.1315 | 0.060673 | 109.2283 | 0.078046 | 118.82 | 0.086331 | 0.39567 | 0.30363 | 114.632 | -0.0094198
382.2 | 174.2 | 128.7751 | 0.085382 | 128.5695 | 0.44638 | 0.10277 | 1.6859e-05 | 109.8586 | 0.06392 | 112.4425 | 0.078046 | 119.8914 | 0.084708 | 0.29825 | 0.32473 | 114.7294 | 0.0035663
382.4 | 174.4 | 127.4115 | 0.083759 | 127.5955 | 0.33113 | 0.20015 | 0.0048865 | 106.3523 | 0.06392 | 109.8127 | 0.081293 | 97.5876 | 0.086331 | 4.4863 | 0.31499 | 109.5674 | 0.0035663
382.6 | 174.6 | 127.9959 | 0.087005 | 127.3033 | 0.53891 | 0.29757 | -0.0064765 | 101.9695 | 0.05418 | 106.3065 | 0.071553 | 117.3591 | 0.076592 | 0.59047 | 0.41238 | 114.3398 | -0.0013034
382.8 | 174.8 | 128.4829 | 0.082136 | 128.3747 | 0.3847 | 0.68714 | 0.0032635 | 109.0794 | 0.067167 | 113.0268 | 0.073176 | 120.3784 | 0.087955 | 0.29825 | 0.2598 | 118.333 | 0.00032025
383 | 175 | 127.8985 | 0.080513 | 126.5242 | 0.57787 | 0.0053935 | 0.0097562 | 102.1642 | 0.05905 | 105.5273 | 0.082916 | 115.3138 | 0.092824 | 0.49305 | 0.46433 | 109.5674 | 0.0035663
383.2 | 175.2 | 129.0672 | 0.087005 | 128.5695 | 0.44638 | 0.10277 | 1.6859e-05 | 99.4371 | 0.05905 | 102.1184 | 0.06993 | 108.7882 | 0.076592 | 0.29825 | 0.36044 | 105.5741 | 0.0035663
383.4 | 175.4 | 129.1647 | 0.087005 | 129.1539 | 0.32302 | 0.29757 | 0.0016399 | 99.0475 | 0.055804 | 100.4627 | 0.061813 | 104.8923 | 0.068475 | 0.49305 | 0.24032 | 103.0418 | 0.0051899
383.6 | 175.6 | 129.5542 | 0.087005 | 129.1539 | 0.3636 | 0.10277 | 1.6859e-05 | 97.0996 | 0.05418 | 98.7095 | 0.061813 | 102.2626 | 0.065229 | 0.29825 | 0.2809 | 98.659 | 0.0035663
383.8 | 175.8 | 129.6516 | 0.085382 | 129.2513 | 0.35548 | 0.20015 | 0.0016399 | 95.2491 | 0.05418 | 96.372 | 0.061813 | 99.6329 | 0.066852 | 0.29825 | 0.26791 | 94.8605 | 0.0035663
384 | 176 | 129.749 | 0.085382 | 129.3486 | 0.3149 | 0.20015 | 1.6859e-05 | 99.0475 | 0.05418 | 99.5861 | 0.061813 | 102.2626 | 0.065229 | 0.29825 | 0.22408 | 98.2694 | 0.0035663
384.2 | 176.2 | 127.3141 | 0.074019 | 104.5125 | 0.33113 | 0.39495 | 0.0016399 | 117.0659 | 0.055804 | 111.6633 | 0.061813 | 116.9695 | 0.065229 | 0.68785 | 0.26467 | 104.9898 | 0.0035663
384.4 | 176.4 | 111.7307 | 0.083759 | 114.2522 | 0.25484 | 0.68714 | 0.0016399 | 119.9878 | 0.05418 | 127.0519 | 0.058567 | 107.9116 | 0.068475 | 0.68785 | 0.25817 | 98.9512 | 0.0019433
384.6 | 176.6 | 127.0219 | 0.087005 | 127.0111 | 0.2938 | 1.0767 | -0.0016068 | 99.4371 | 0.055804 | 101.7288 | 0.074799 | 105.9637 | 0.071722 | 0.68785 | 0.17701 | 104.1132 | 0.0051899
384.8 | 176.8 | 130.236 | 0.087005 | 129.1539 | 0.2938 | 0.39495 | 0.0016399 | 103.333 | 0.05418 | 104.1637 | 0.06993 | 107.522 | 0.071722 | 0.78523 | 0.18513 | 104.4054 | 0.0035663
385 | 177 | 130.0412 | 0.099992 | 128.5695 | 0.32464 | 0.49237 | 0.01138 | 100.5085 | 0.057427 | 101.1444 | 0.066683 | 103.9184 | 0.068475 | 3.1228 | 0.30525 | 77.6213 | 0.0035663
385.2 | 177.2 | 127.8011 | 0.087005 | 127.6929 | 0.31003 | 0.10277 | 0.01138 | 99.4371 | 0.05905 | 99.8783 | 0.16408 | 105.1846 | 0.068475 | 0.68785 | 0.24519 | 98.5616 | 0.0019433
385.4 | 177.4 | 127.8985 | 0.085382 | 127.4981 | 0.61033 | 0.20015 | 1.6859e-05 | 64.0822 | 0.036324 | 61.8937 | 0.1722 | 86.6792 | 0.052243 | 0.49305 | 0.42212 | 86.1922 | 0.0035663
385.6 | 177.6 | 125.1714 | 0.085382 | 125.6476 | 0.61358 | 0.29757 | 0.0032635 | 68.952 | 0.034701 | 60.6275 | 0.4303 | 91.4516 | 0.058735 | 0.49305 | 0.18837 | 92.036 | 0.044149
385.8 | 177.8 | 128.5803 | 0.087005 | 128.0825 | 0.55352 | 0.29757 | -0.0016068 | 84.5355 | 0.042818 | 81.4703 | 0.2907 | 92.1334 | 0.055489 | 0.59047 | 0.25817 | 91.9386 | 0.0035663
386 | 178 | 129.0672 | 0.077266 | 128.3747 | 0.47073 | 0.68714 | -0.0032298 | 91.6454 | 0.046064 | 92.184 | 0.081293 | 96.1267 | 0.058735 | -0.3835 | 0.36044 | 94.5683 | 0.018176
386.2 | 178.2 | 130.0412 | 0.085382 | 129.5434 | 0.35873 | 0.29757 | 0.0032635 | 101.872 | 0.062296 | 103.5794 | 0.06993 | 106.7429 | 0.071722 | 0.59047 | 0.26142 | 106.6455 | 0.0051899
386.4 | 178.4 | 130.723 | 0.085382 | 130.3226 | 0.23536 | 0.49237 | 1.6859e-05 | 100.4111 | 0.057427 | 101.3392 | 0.068307 | 102.0679 | 0.070098 | 0.59047 | 0.13967 | 101.9704 | 0.0019433
386.6 | 178.6 | 129.1647 | 0.088629 | 129.2513 | 0.35548 | -0.092027 | 1.6859e-05 | 84.7303 | 0.050934 | 88.2881 | 0.058567 | 89.1141 | 0.047373 | 0.10349 | 0.27765 | 88.6271 | 0.0019433
386.8 | 178.8 | 124.8792 | 0.082136 | 125.1606 | 0.7824 | 0.39495 | 0.0032635 | 58.628 | 0.029831 | 59.4587 | 0.22739 | 61.6483 | 0.23405 | 0.29825 | 0.33447 | 62.2327 | 0.0019433
387 | 179 | 126.6323 | 0.083759 | 126.2319 | 0.82623 | 0.49237 | 0.0016399 | 56.3879 | 0.028208 | 51.9592 | 0.37024 | 56.8759 | 0.40125 | 0.88265 | 0.12344 | 56.4863 | 0.0035663
387.2 | 179.2 | 125.3662 | 0.082136 | 124.6736 | 0.99018 | 0.39495 | 0.0016399 | 54.9269 | 0.026584 | 51.3748 | 0.37998 | 55.9993 | 0.41099 | 0.59047 | 0.25817 | 55.9993 | 0.0019433
387.4 | 179.4 | 125.8532 | 0.087005 | 125.6476 | 0.96259 | 16.9524 | 0.0048865 | 59.6993 | 0.029831 | 56.7316 | 0.42056 | 62.1353 | 0.45157 | 4.2915 | 0.16402 | 62.0379 | 0.0035663
387.6 | 179.6 | 127.1193 | 0.085382 | 126.6215 | 0.78727 | 0.58976 | 0.0016399 | 68.952 | 0.033078 | 63.939 | 0.46276 | 82.0042 | 0.10419 | 0.49305 | 0.29713 | 82.1015 | 0.00032025
387.8 | 179.8 | 129.0672 | 0.087005 | 128.4721 | 0.56001 | 0.58976 | 0.0032635 | 93.009 | 0.047687 | 94.1319 | 0.12512 | 97.5876 | 0.066852 | 1.0774 | 0.43186 | 97.3928 | 0.0035663
388 | 180 | 130.3334 | 0.061033 | 129.4461 | 0.32788 | 0.68714 | 0.0048865 | 109.0794 | 0.05905 | 110.2997 | 0.076423 | 109.7622 | 0.074968 | 0.88265 | 0.17701 | 107.0351 | 0.01006
388.2 | 180.2 | 130.9178 | 0.087005 | 130.3226 | 0.30841 | 0.68714 | 0.0032635 | 111.5143 | 0.062296 | 114.0982 | 0.07967 | 114.632 | 0.078215 | 1.0774 | 0.19974 | 114.632 | 0.0035663
388.4 | 180.4 | 130.9178 | 0.087005 | 130.3226 | 0.30029 | 0.58976 | 0.0048865 | 118.7216 | 0.072036 | 120.9159 | 0.087786 | 119.5018 | 0.086331 | 1.0774 | 0.17052 | 119.307 | 0.0035663
388.6 | 180.6 | 124.4896 | 0.083759 | 125.1606 | 0.38957 | 3.0247 | 0.0048865 | 101.5799 | 0.060673 | 108.0596 | 0.07967 | 104.6975 | 0.078215 | 1.3696 | 0.27928 | 92.4256 | 0.0035663
388.8 | 180.8 | 130.5282 | 0.087005 | 129.933 | 0.37171 | 0.68714 | 0.0048865 | 111.5143 | 0.065543 | 116.8253 | 0.07967 | 112.4893 | 0.073345 | 1.1748 | 0.27116 | 112.2945 | 0.0051899
389 | 181 | 131.1126 | 0.087005 | 130.6148 | 0.28893 | 0.68714 | 0.0048865 | 119.2086 | 0.06879 | 122.2795 | 0.087786 | 121.9367 | 0.086331 | 1.2722 | 0.1624 | 121.742 | 0.0035663
389.2 | 181.2 | 129.749 | 0.065903 | 129.4461 | 0.35548 | 0.39495 | 0.0065095 | 101.9695 | 0.065543 | 113.806 | 0.086162 | 113.0736 | 0.078215 | 0.39567 | 0.24032 | 113.7554 | 0.0068129
389.4 | 181.4 | 131.1126 | 0.087005 | 130.6148 | 0.29867 | 0.78456 | 0.0048865 | 118.1373 | 0.06879 | 119.455 | 0.082916 | 119.8914 | 0.083085 | 1.3696 | 0.18026 | 119.8914 | 0.0051899
389.6 | 181.6 | 128.8725 | 0.087005 | 128.1799 | 0.50157 | 0.29757 | 0.0097562 | 100.4111 | 0.055804 | 108.0596 | 0.076423 | 102.1652 | 0.070098 | 0.49305 | 0.38317 | 101.8731 | 0.00032025
389.8 | 181.8 | 128.2881 | 0.088629 | 128.1799 | 0.61196 | 0.78456 | 0.0081332 | 67.1989 | 0.041194 | 86.048 | 0.061813 | 81.0302 | 0.044126 | 1.6618 | 0.56984 | 80.9328 | 0.0019433
390 | 182 | 126.048 | 0.082136 | 124.9658 | 0.91876 | 0.10277 | -0.0016068 | 61.2577 | 0.029831 | 94.0345 | 0.061813 | 82.5885 | 0.052243 | 0.10349 | 0.89287 | 82.199 | 0.011683
390.2 | 182.2 | 127.8011 | 0.083759 | 127.0111 | 0.76779 | 0.78456 | 0.0048865 | 87.36 | 0.037947 | 99.1965 | 0.06019 | 88.9193 | 0.23405 | 1.1748 | 0.5666 | 88.8219 | 0.0051899
390.4 | 182.4 | 129.6516 | 0.083759 | 128.5695 | 0.53079 | 0.58976 | 0.0048865 | 110.0534 | 0.06392 | 116.5331 | 0.084539 | 107.522 | 0.086331 | 0.98003 | 0.43836 | 107.522 | 0.0068129
390.6 | 182.6 | 130.5282 | 0.087005 | 129.8357 | 0.41229 | 0.39495 | 0.0048865 | 117.8451 | 0.065543 | 120.7211 | 0.086162 | 115.5086 | 0.078215 | 1.1748 | 0.3085 | 115.2164 | 0.0051899
390.8 | 182.8 | 130.723 | 0.085382 | 130.0304 | 0.32626 | 0.49237 | 0.0048865 | 114.8258 | 0.06879 | 121.0133 | 0.087786 | 115.4112 | 0.081461 | 1.0774 | 0.20623 | 115.5086 | 0.0051899
391 | 183 | 129.9438 | 0.083759 | 128.9591 | 0.44801 | 0.58976 | 0.0048865 | 96.2231 | 0.055804 | 99.3913 | 0.06506 | 94.2761 | 0.061982 | 1.1748 | 0.40102 | 94.0813 | 0.00032025
391.2 | 183.2 | 130.1386 | 0.087005 | 129.5434 | 0.45288 | 0.68714 | 0.0048865 | 105.2809 | 0.05905 | 105.3325 | 0.06993 | 104.795 | 0.066852 | 1.2722 | 0.3783 | 105.2819 | 0.0051899
391.4 | 183.4 | 130.3334 | 0.083759 | 129.8357 | 0.39931 | 0.88194 | 0.0048865 | 105.0862 | 0.062296 | 103.5794 | 0.06993 | 103.1392 | 0.071722 | 1.0774 | 0.31499 | 103.0418 | 0.0035663
391.6 | 183.6 | 130.236 | 0.085382 | 129.7382 | 0.44638 | 0.68714 | 0.0048865 | 106.1575 | 0.05905 | 102.995 | 0.068307 | 103.5288 | 0.065229 | 1.0774 | 0.36693 | 103.4314 | 0.0035663
391.8 | 183.8 | 129.0672 | 0.080513 | 128.6669 | 0.53404 | 0.58976 | 0.0048865 | 103.7226 | 0.060673 | 101.1444 | 0.068307 | 100.9965 | 0.070098 | 1.467 | 0.45784 | 100.9965 | 0.0051899
392 | 184 | 130.236 | 0.087005 | 129.5434 | 0.45125 | 0.78456 | 0.0065095 | 115.118 | 0.065543 | 114.0982 | 0.081293 | 113.3659 | 0.079838 | 1.3696 | 0.35395 | 113.4632 | 0.0035663
392.2 | 184.2 | 129.1647 | 0.085382 | 128.3747 | 0.59248 | 0.78456 | 0.0065095 | 108.5924 | 0.065543 | 106.8908 | 0.081293 | 106.6455 | 0.079838 | 1.2722 | 0.50491 | 106.5481 | 0.0035663
392.4 | 184.4 | 129.8464 | 0.087005 | 129.1539 | 0.51456 | 0.88194 | 0.0065095 | 116.4815 | 0.067167 | 114.4878 | 0.076423 | 115.5086 | 0.078215 | 1.3696 | 0.42862 | 115.4112 | 0.0051899
392.6 | 184.6 | 128.7751 | 0.083759 | 128.0825 | 0.72234 | 0.88194 | 0.0065095 | 113.3648 | 0.065543 | 114.0008 | 0.074799 | 112.5867 | 0.073345 | 1.467 | 0.64289 | 112.3919 | 0.0035663
392.8 | 184.8 | 130.0412 | 0.085382 | 129.2513 | 0.51943 | 0.78456 | 0.0048865 | 122.1305 | 0.070413 | 123.4482 | 0.087786 | 121.742 | 0.084708 | 1.3696 | 0.42699 | 121.6445 | 0.0035663
393 | 185 | 128.8725 | 0.085382 | 128.1799 | 0.68176 | 0.97936 | 0.0065095 | 119.2086 | 0.067167 | 120.7211 | 0.082916 | 118.4305 | 0.079838 | 1.3696 | 0.59906 | 118.333 | 0.0035663
393.2 | 185.2 | 127.0219 | 0.083759 | 126.2319 | 0.92687 | 0.88194 | 0.0081332 | 114.2414 | 0.067167 | 116.9227 | 0.081293 | 112.3919 | 0.076592 | 1.3696 | 0.85067 | 112.2945 | 0.0019433
393.4 | 185.4 | 127.6063 | 0.083759 | 126.8163 | 0.83597 | 0.97936 | 0.0048865 | 118.0399 | 0.067167 | 120.0394 | 0.082916 | 117.7487 | 0.079838 | 1.3696 | 0.75327 | 117.6513 | 0.0051899
393.6 | 185.6 | 127.6063 | 0.083759 | 126.8163 | 0.8587 | 0.88194 | 0.0065095 | 115.8972 | 0.065543 | 120.8186 | 0.084539 | 113.658 | 0.081461 | 1.2722 | 0.77438 | 113.5606 | 0.0019433
393.8 | 185.8 | 128.0933 | 0.083759 | 127.4007 | 0.75805 | 0.88194 | 0.0065095 | 119.4034 | 0.067167 | 122.7665 | 0.087786 | 117.4565 | 0.081461 | 1.2722 | 0.67536 | 117.2617 | 0.0051899
394 | 186 | 126.5349 | 0.083759 | 126.1346 | 0.88304 | 0.88194 | 0.0048865 | 115.118 | 0.06879 | 119.7472 | 0.086162 | 113.8528 | 0.081461 | 1.3696 | 0.80522 | 113.4632 | 0.0035663
394.2 | 186.2 | 127.4115 | 0.083759 | 127.4007 | 0.7402 | 0.97936 | 0.0065095 | 119.5008 | 0.070413 | 121.8899 | 0.086162 | 117.3591 | 0.079838 | 1.3696 | 0.64776 | 117.1643 | 0.0035663
394.4 | 186.4 | 129.3595 | 0.085382 | 129.7382 | 0.53404 | 0.88194 | 0.0065095 | 122.9097 | 0.070413 | 124.7144 | 0.086162 | 122.5211 | 0.084708 | 1.3696 | 0.4416 | 122.3263 | 0.0019433
394.6 | 186.6 | 129.0672 | 0.085382 | 128.5695 | 0.62981 | 0.88194 | 0.0065095 | 122.2279 | 0.072036 | 124.8118 | 0.089409 | 122.8133 | 0.086331 | 1.3696 | 0.539 | 122.8133 | 0.0035663
394.8 | 186.8 | 127.9959 | 0.083759 | 127.2059 | 0.77104 | 0.88194 | 0.0065095 | 120.6696 | 0.06879 | 122.7665 | 0.086162 | 120.768 | 0.084708 | 1.3696 | 0.68834 | 120.6706 | 0.0019433
395 | 187 | 127.5089 | 0.083759 | 126.8163 | 0.82461 | 0.88194 | 0.0065095 | 121.6436 | 0.070413 | 123.4482 | 0.087786 | 122.0341 | 0.084708 | 1.3696 | 0.74191 | 121.742 | 0.0035663
395.2 | 187.2 | 127.1193 | 0.083759 | 126.4267 | 0.89278 | 0.88194 | 0.0065095 | 121.254 | 0.070413 | 123.0587 | 0.086162 | 121.742 | 0.084708 | 1.467 | 0.81496 | 121.6445 | 0.0035663
395.4 | 187.4 | 127.8011 | 0.083759 | 127.0111 | 0.82948 | 0.97936 | 0.0065095 | 120.0852 | 0.06879 | 123.2535 | 0.086162 | 120.5732 | 0.084708 | 0.98003 | 0.72568 | 120.6706 | 0.0035663
395.6 | 187.6 | 127.6063 | 0.083759 | 126.9137 | 0.84733 | 0.97936 | 0.0048865 | 120.767 | 0.06879 | 123.643 | 0.086162 | 122.8133 | 0.084708 | 1.3696 | 0.74516 | 122.8133 | 0.0019433
395.8 | 187.8 | 128.9699 | 0.085382 | 128.2773 | 0.66228 | 0.88194 | 0.0065095 | 121.6436 | 0.072036 | 124.3248 | 0.089409 | 122.4237 | 0.086331 | 1.467 | 0.55199 | 122.3263 | 0.0035663
396 | 188 | 128.1907 | 0.088629 | 127.6929 | 0.75318 | 1.3689 | 0.0065095 | 120.8644 | 0.072036 | 122.5717 | 0.091033 | 121.5472 | 0.076592 | 1.8566 | 0.6364 | 120.8654 | 0.0084366
396.2 | 188.2 | 130.0412 | 0.087005 | 129.3486 | 0.49995 | 0.97936 | 0.0048865 | 121.7409 | 0.06879 | 123.5456 | 0.091033 | 120.768 | 0.084708 | 1.1748 | 0.38804 | 120.3784 | 0.0035663
396.4 | 188.4 | 131.0152 | 0.087005 | 130.3226 | 0.336 | 0.68714 | 0.0065095 | 124.0785 | 0.070413 | 125.6884 | 0.089409 | 123.9821 | 0.084708 | 1.1748 | 0.22408 | 123.8847 | 0.0035663
396.6 | 188.6 | 131.0152 | 0.087005 | 130.0304 | 0.35548 | 0.58976 | 0.0032635 | 122.4227 | 0.070413 | 124.3248 | 0.089409 | 121.1576 | 0.084708 | 1.0774 | 0.25006 | 121.255 | 0.0035663
396.8 | 188.8 | 130.4308 | 0.083759 | 129.933 | 0.37658 | 0.78456 | 0.0081332 | 120.3774 | 0.070413 | 123.2535 | 0.092656 | 119.794 | 0.083085 | 1.467 | 0.27603 | 119.794 | 0.0035663
397 | 189 | 130.236 | 0.087005 | 129.5434 | 0.39444 | 0.68714 | 0.0016399 | 119.6956 | 0.06879 | 122.7665 | 0.082916 | 117.6513 | 0.081461 | 0.68785 | 0.29226 | 117.8461 | 0.0019433
397.2 | 189.2 | 129.8464 | 0.080513 | 128.5695 | 0.48697 | 0.97936 | 0.0048865 | 115.0206 | 0.067167 | 119.2602 | 0.084539 | 111.6127 | 0.073345 | 0.68785 | 0.40914 | 110.7361 | 0.0051899
397.4 | 189.4 | 129.3595 | 0.085382 | 128.6669 | 0.51131 | 0.49237 | 0.0032635 | 114.9232 | 0.067167 | 119.6498 | 0.081293 | 111.2231 | 0.078215 | 1.1748 | 0.42537 | 110.7361 | 0.0068129
397.6 | 189.6 | 130.4308 | 0.087005 | 129.4461 | 0.39931 | 1.1741 | 0.0065095 | 117.9425 | 0.06392 | 122.4743 | 0.086162 | 118.82 | 0.084708 | 1.0774 | 0.30525 | 118.7227 | 0.0051899
397.8 | 189.8 | 130.9178 | 0.088629 | 130.2252 | 0.30191 | 0.49237 | 0.0032635 | 119.6956 | 0.06879 | 125.3962 | 0.087786 | 121.5472 | 0.086331 | 1.0774 | 0.17863 | 120.3784 | -0.0061731
398 | 190 | 130.6256 | 0.085382 | 129.933 | 0.37821 | 0.58976 | 0.0016399 | 117.3581 | 0.06879 | 124.5196 | 0.087786 | 119.1123 | 0.087955 | 0.59047 | 0.26142 | 119.4044 | 0.0019433
398.2 | 190.2 | 131.21 | 0.087005 | 130.5174 | 0.28893 | 0.58976 | 0.0032635 | 121.9357 | 0.06879 | 126.7597 | 0.092656 | 125.443 | 0.083085 | 1.2722 | 0.16565 | 125.0534 | 0.0019433
398.4 | 190.4 | 129.8464 | 0.083759 | 129.1539 | 0.39606 | 1.5637 | 0.0032635 | 115.9945 | 0.070413 | 123.4482 | 0.092656 | 119.5018 | 0.078215 | 0.88265 | 0.27603 | 119.0148 | 0.01006
398.6 | 190.6 | 125.9505 | 0.085382 | 125.258 | 0.93661 | 0.58976 | 0.0032635 | 109.5664 | 0.067167 | 116.8253 | 0.081293 | 107.6195 | 0.074968 | 0.68785 | 0.85716 | 107.522 | 0.0051899
398.8 | 190.8 | 128.0933 | 0.078889 | 128.0825 | 0.57462 | 0.58976 | 0.0032635 | 117.2607 | 0.067167 | 122.5717 | 0.084539 | 117.6513 | 0.066852 | 0.98003 | 0.46595 | 117.4565 | 0.0019433
399 | 191 | 129.5542 | 0.088629 | 128.3747 | 0.58112 | 0.58976 | 0.0048865 | 116.2867 | 0.06879 | 122.3769 | 0.086162 | 116.0929 | 0.076592 | 0.68785 | 0.47082 | 115.9956 | 0.0068129
399.2 | 191.2 | 128.4829 | 0.083759 | 127.5955 | 0.70286 | 1.0767 | 0.0048865 | 116.5789 | 0.070413 | 122.0847 | 0.082916 | 115.8981 | 0.078215 | 1.467 | 0.59257 | 116.1903 | 0.0035663
399.4 | 191.4 | 125.3662 | 0.080513 | 126.3294 | 0.71422 | 1.8559 | -0.012969 | 115.2154 | 0.05905 | 119.455 | 0.082916 | 114.4372 | 0.083085 | 0.59047 | 0.59744 | 113.7554 | 0.0084366
399.6 | 191.6 | 129.262 | 0.085382 | 128.8617 | 0.48697 | 0.68714 | 0.0065095 | 115.6049 | 0.067167 | 123.8378 | 0.089409 | 117.7487 | 0.079838 | 0.59047 | 0.37018 | 117.7487 | 0.0051899
399.8 | 191.8 | 128.9699 | 0.085382 | 128.1799 | 0.50482 | 0.39495 | 0.0016399 | 115.5076 | 0.072036 | 121.6951 | 0.084539 | 113.7554 | 0.074968 | 0.68785 | 0.3994 | 113.1711 | 0.0035663
400 | 192 | 127.6063 | 0.083759 | 126.719 | 0.67364 | 0.49237 | 0.0032635 | 110.0534 | 0.06392 | 117.6044 | 0.081293 | 103.1392 | 0.066852 | 1.0774 | 0.57796 | 103.0418 | 0.0035663
400.2 | 192.2 | 127.1193 | 0.093499 | 124.4788 | 1.1834 | 2.2455 | 0.0081332 | 103.5278 | 0.062296 | 112.1502 | 0.076423 | 92.036 | 0.060359 | 0.49305 | 1.0844 | 91.8412 | 0.023046
400.4 | 192.4 | 125.3662 | 0.085382 | 124.9658 | 0.96908 | 0.39495 | 0.0032635 | 104.307 | 0.060673 | 113.319 | 0.073176 | 90.4777 | 0.053866 | 0.59047 | 0.89287 | 90.2829 | -0.0013034
400.6 | 192.6 | 122.6391 | 0.078889 | 122.0439 | 1.232 | 0.0053935 | -0.021086 | 101.1903 | 0.057427 | 111.0789 | 0.078046 | 88.4323 | 0.04088 | 0.78523 | 1.1867 | 88.4323 | 0.0051899
400.8 | 192.8 | 19.1066 | 1.3872 | 18.0244 | 0.17043 | 0.10277 | 0.0016399 | 14.9944 | 0.023338 | 17.286 | 0.042334 | 13.5344 | 0.037633 | 0.39567 | 1.4708 | 13.5344 | 0.0019433
401 | 193 | 3.3283 | 0.10811 | 2.928 | 0.027579 | 0.20015 | 1.6859e-05 | 2.625 | 0.011975 | 2.8714 | 0.0098686 | 2.5286 | 0.013284 | 0.29825 | 0.11046 | 2.2364 | 0.0035663
401.2 | 193.2 | 1.283 | 0.026944 | 1.0774 | 0.011346 | 0.10277 | 1.6859e-05 | 1.164 | 0.0071055 | 1.2156 | 0.0066219 | 1.1651 | 0.0067905 | 0.29825 | 0.027669 | 0.77546 | 0.0019433
401.4 | 193.4 | 0.79601 | 0.013958 | 0.59043 | 0.0048528 | 0.10277 | 0.0016399 | 0.77444 | 0.0022351 | 0.82602 | 0.0049989 | 0.77546 | 0.0019208 | 0.20087 | 0.014683 | 0.67808 | 0.0019433
401.6 | 193.6 | 0.69863 | 0.010711 | 0.49305 | 0.0048528 | 0.20015 | 0.0016399 | 0.57968 | 0.0038588 | 0.63122 | 0.0033759 | 0.67808 | 0.0051674 | 0.20087 | 0.011436 | 0.28848 | 0.0019433
401.8 | 193.8 | 0.69863 | 0.0090883 | 0.49305 | 0.0032298 | 0.0053935 | 0.0016399 | 0.57968 | 0.00061214 | 0.63122 | 0.0017522 | 0.67808 | 0.0019208 | 0.29825 | 0.009813 | 0.093675 | 0.0051899
402 | 194 | 0.40645 | 0.0090883 | 0.39567 | 0.0032298 | 0.20015 | 0.0016399 | 0.38488 | 0.00061214 | 0.53384 | 0.0017522 | 0.48328 | 0.00029777 | 0.20087 | 0.0065663 | 0.19109 | 0.0019433
405 | 197 | 0.40645 | 0.0058416 | 0.29825 | -1.6843e-05 | 0.0053935 | 0.0016399 | 0.38488 | 0.00061214 | 0.53384 | 0.00012922 | 0.48328 | 0.00029777 | 0.20087 | 0.0049427 | 0.093675 | 0.0019433
410 | 202 | 0.21165 | 0.0042186 | 0.20087 | -1.6843e-05 | 0.10277 | 0.0016399 | 0.28746 | 0.00061214 | 0.43642 | 0.00012922 | 0.38586 | 0.00029777 | 0.29825 | 0.0049427 | -0.0037056 | 0.0019433
413.4 | 205.4 | 0.21165 | 0.0042186 | 0.10345 | 0.0016062 | 0.0053935 | 1.6859e-05 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | -0.0013259 | 0.10349 | 0.0033197 | 0.093675 | 0.00032025