## Test Conditions
CAROLFIRE Intermediate Scale Test Number IP-3
Test Date: | 2006-10-12
Ignition Time Relative to Thermal Data: | 208 | s
Ignition Time Relative to Electrical Data: | 208 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
3/C cable temperatures and IRMS data
7/C cable temperatures and SCDU data

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 3/C PVC Cable |  |  | Location A - 7/C PVC Cable |  |  | Location A - Tray
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | Cable Temp | Temp Above Cable | Temp Below Cable | Cable Temp | Temp Above Cable | Temp Below Cable | Tray Rung Temp
0 | -208 | -6.2 | 0 | 0 | 17.4 | 18.2 | 18.2 | 18 | 18 | 17.2 | 22.1 | 17.5 | 2.9 | 257.8 | 13.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
1 | -207 | -6.2 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.6 | 250.1 | 14.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
2 | -206 | -6.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.5 | 252.5 | 15.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
3 | -205 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.5 | 254 | 14.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
4 | -204 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.2 | 18 | 18 | 17.2 | 22.1 | 17.5 | 3 | 263.2 | 13.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
5 | -203 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 18 | 18 | 17.2 | 22.1 | 17.5 | 2.7 | 264.9 | 11.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
6 | -202 | -6.8 | 0 | 0 | 17.5 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.4 | 269.7 | 10.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
7 | -201 | -6.8 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.4 | 275.8 | 10 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
8 | -200 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.3 | 276.4 | 9.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
9 | -199 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.4 | 264.7 | 8.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
10 | -198 | -6.7 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.3 | 280.6 | 8.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
11 | -197 | -6.1 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 2.5 | 289.2 | 9.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
12 | -196 | -6.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 3 | 282.7 | 10.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
13 | -195 | -6.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.4 | 272.7 | 10.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
14 | -194 | -6.5 | 0 | 0 | 17.4 | 18.2 | 18.2 | 18 | 18 | 17.3 | 22.1 | 17.5 | 4 | 266.4 | 9.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
15 | -193 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.2 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 3.9 | 264.1 | 11 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
16 | -192 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.2 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.8 | 266.2 | 11.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
17 | -191 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.2 | 18 | 18 | 17.3 | 22.1 | 17.5 | 3.3 | 274.2 | 10.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
18 | -190 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 18 | 17.3 | 22.1 | 17.5 | 2.9 | 257 | 11.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
19 | -189 | -6.2 | 0 | 0 | 17.4 | 18.2 | 18.2 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3 | 257.9 | 10.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
20 | -188 | -6.2 | 0 | 0 | 17.5 | 18.1 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.5 | 252.6 | 10.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
21 | -187 | -6.3 | 0 | 0 | 17.5 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 3.5 | 250.7 | 10.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
22 | -186 | -6.4 | 0 | 0 | 17.5 | 18.1 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.7 | 257.5 | 10.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
23 | -185 | -6.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.7 | 255.6 | 9.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
24 | -184 | -6.5 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.6 | 262.2 | 9.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
25 | -183 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.6 | 258.9 | 11.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
26 | -182 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.2 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.7 | 251.2 | 11.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
27 | -181 | -6.6 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 18 | 17.2 | 22.1 | 17.5 | 3.6 | 251 | 11.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
28 | -180 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4 | 246.9 | 13.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
29 | -179 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4.5 | 253.8 | 14.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
30 | -178 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4 | 262 | 16.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
31 | -177 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4.2 | 261.6 | 15.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
32 | -176 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.2 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4.1 | 261.3 | 14.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
33 | -175 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4.5 | 261.7 | 12.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
34 | -174 | -6.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 4.2 | 266.7 | 10.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
35 | -173 | -6.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.8 | 280.1 | 10.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
36 | -172 | -6.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.6 | 275.7 | 12 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
37 | -171 | -6.7 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.5 | 278.1 | 13.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
38 | -170 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.2 | 278.8 | 14.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
39 | -169 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3 | 293.9 | 12.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
40 | -168 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.9 | 286.3 | 12.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
41 | -167 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.7 | 271 | 11.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
42 | -166 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.7 | 283.3 | 10.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
43 | -165 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.7 | 289.1 | 10.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
44 | -164 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.9 | 297 | 11.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
45 | -163 | -6.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3 | 293 | 11.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
46 | -162 | -6.2 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.1 | 280.2 | 9.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
47 | -161 | -6.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.1 | 230.9 | 6.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
48 | -160 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.6 | 280.9 | 5.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
49 | -159 | -6.6 | 0 | 0 | 17.5 | 18.1 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.4 | 273.4 | 5.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
50 | -158 | -6.2 | 0 | 0 | 17.5 | 18.1 | 18 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.3 | 240.3 | 5.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
51 | -157 | -6.7 | 0 | 0 | 17.5 | 18.1 | 18 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.2 | 273.7 | 6.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
52 | -156 | -6.8 | 0 | 0 | 17.5 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.3 | 264.4 | 7.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
53 | -155 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 18 | 17.3 | 22.1 | 17.5 | 2.1 | 243.7 | 7.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
54 | -154 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 18 | 17.3 | 22.1 | 17.5 | 2.3 | 256.2 | 7.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
55 | -153 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 18 | 17.3 | 22.1 | 17.5 | 2.4 | 227.2 | 8.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
56 | -152 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.3 | 263.7 | 7.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
57 | -151 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2 | 236.3 | 6.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
58 | -150 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.1 | 245.8 | 6.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
59 | -149 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.4 | 244.5 | 7.2 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
60 | -148 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.5 | 252.2 | 7.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
61 | -147 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.7 | 253.5 | 8.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
62 | -146 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.8 | 239.7 | 8.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
63 | -145 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.7 | 239.3 | 8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
64 | -144 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.9 | 256.8 | 8.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
65 | -143 | -6.3 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.1 | 250.5 | 8.9 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
66 | -142 | -6.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.8 | 261.8 | 9.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
67 | -141 | -6.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.4 | 267.7 | 11 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
68 | -140 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.6 | 261.3 | 12 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
69 | -139 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.9 | 249.5 | 11.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
70 | -138 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.3 | 240.2 | 11.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
71 | -137 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.4 | 3.5 | 247.7 | 11 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
72 | -136 | -6.5 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.4 | 3.2 | 248.6 | 10.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
73 | -135 | -6.5 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.4 | 3 | 249.6 | 10.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
74 | -134 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.4 | 2.4 | 251.9 | 9.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
75 | -133 | -6.5 | 0 | 0 | 17.3 | 18.2 | 18.1 | 18 | 18 | 17.3 | 22.1 | 17.5 | 2.2 | 248.9 | 9.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
76 | -132 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 2.5 | 249.3 | 10.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
77 | -131 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 18 | 18 | 17.3 | 22.1 | 17.4 | 3.2 | 239.1 | 10.3 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
78 | -130 | -6.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.4 | 4.2 | 241.7 | 9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
79 | -129 | -6.5 | 0 | 0 | 17.4 | 18.2 | 18 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 4.4 | 234.1 | 7.3 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
80 | -128 | -6.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 4.2 | 252.9 | 6.5 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
81 | -127 | -6.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.5 | 233.3 | 7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
82 | -126 | -6.3 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 18 | 17.3 | 22.1 | 17.5 | 3.7 | 249.4 | 6.6 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
83 | -125 | -6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.5 | 229.9 | 7.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
84 | -124 | -6.4 | 0 | 0 | 17.2 | 18.2 | 18.2 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 3.2 | 251.5 | 9.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
85 | -123 | -5.6 | 0 | 0 | 17.2 | 18.2 | 18.2 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 3 | 247 | 11.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
86 | -122 | -5.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.7 | 242.7 | 12.3 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
87 | -121 | -5.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.9 | 231.6 | 11.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
88 | -120 | -5.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.1 | 235.6 | 11.1 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
89 | -119 | -5.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.6 | 230.6 | 9.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
90 | -118 | -5.9 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.3 | 249.2 | 10 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
91 | -117 | -6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.4 | 238.7 | 11.3 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
92 | -116 | -6.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3 | 216.9 | 10.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
93 | -115 | -5.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.6 | 232.7 | 9.2 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
94 | -114 | -6.1 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.1 | 237.9 | 8.8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
95 | -113 | -6.3 | 0 | 0 | 17.3 | 18.2 | 18.1 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 2.6 | 233.8 | 8.5 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
96 | -112 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.7 | 242.1 | 7.9 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
97 | -111 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.6 | 240.3 | 8.3 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
98 | -110 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.4 | 250.7 | 8 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
99 | -109 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.6 | 227.1 | 7.6 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
100 | -108 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.3 | 208.2 | 6.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
101 | -107 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2 | 219.6 | 6.1 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
102 | -106 | -6.6 | 0 | 0 | 17.2 | 18.2 | 18.2 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 2 | 199.8 | 7.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
103 | -105 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 2.7 | 252.7 | 6.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
104 | -104 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 2.5 | 228.7 | 6.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
105 | -103 | -6.8 | 0 | 0 | 17.2 | 18.2 | 18.2 | 18 | 17.9 | 17.3 | 22.1 | 17.5 | 2.3 | 213.4 | 7.7 | 16.8 | 16.7 | 17 | 17.2 | 17.2 | 16.8 | 18.2
106 | -102 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.6 | 193.6 | 8.5 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
107 | -101 | -6.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3 | 210.3 | 8.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
108 | -100 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3 | 207.4 | 8.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
109 | -99 | -6.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.3 | 220.2 | 10.7 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
110 | -98 | -6.3 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.1 | 237.1 | 11.1 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
111 | -97 | -6.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 2.8 | 266.5 | 6 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
112 | -96 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.3 | 192.1 | 4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
113 | -95 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.9 | 231 | 4.6 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
114 | -94 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.1 | 244.7 | 4.3 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
115 | -93 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.3 | 22.1 | 17.5 | 3.2 | 241.5 | 5.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
116 | -92 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 3.4 | 224.4 | 6.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
117 | -91 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.2 | 225.9 | 5.8 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
118 | -90 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.5 | 257.4 | 5.5 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
119 | -89 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 3.6 | 254.3 | 6.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
120 | -88 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.4 | 240.4 | 11 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
121 | -87 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.8 | 231.7 | 11.1 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
122 | -86 | -6.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 239.4 | 10.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
123 | -85 | -6.5 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 2.4 | 244.8 | 10.5 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
124 | -84 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 243.6 | 11.1 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
125 | -83 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.7 | 245.9 | 11.4 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
126 | -82 | -6.3 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.7 | 224 | 9.8 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
127 | -81 | -5.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.7 | 252.2 | 8.6 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
128 | -80 | -5.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3 | 204.9 | 8 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
129 | -79 | -6.2 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.1 | 219.2 | 7.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
130 | -78 | -5.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3 | 212.3 | 9.2 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
131 | -77 | -5.4 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.5 | 225.1 | 9.5 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
132 | -76 | -5.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.6 | 231.3 | 8.9 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
133 | -75 | -6 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.8 | 250.6 | 7.6 | 16.8 | 16.7 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
134 | -74 | -6.3 | 0 | 0 | 17.3 | 18.2 | 18.2 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2 | 223.4 | 6.8 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
135 | -73 | -6.5 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.1 | 247.3 | 6.8 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
136 | -72 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2 | 223.1 | 6.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
137 | -71 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.3 | 250.6 | 6.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
138 | -70 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.6 | 247.3 | 5.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
139 | -69 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 215.4 | 5.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
140 | -68 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.8 | 208.8 | 8.7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
141 | -67 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.3 | 210.5 | 11.1 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
142 | -66 | -6.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.8 | 214.8 | 10.3 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
143 | -65 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.6 | 213.8 | 8.2 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
144 | -64 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.8 | 262.6 | 7 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
145 | -63 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.7 | 243.5 | 6 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
146 | -62 | -6.3 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.5 | 211.2 | 5 | 16.9 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
147 | -61 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 3.2 | 254 | 6.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
148 | -60 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 2.9 | 233.7 | 8.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
149 | -59 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.4 | 245.6 | 9.4 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
150 | -58 | -5.9 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.4 | 241.2 | 9.5 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
151 | -57 | -5.1 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 233.1 | 9.9 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
152 | -56 | -4.9 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 217.3 | 9.3 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
153 | -55 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.8 | 236.3 | 8 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
154 | -54 | -6.7 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.2 | 236 | 7.5 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
155 | -53 | -6.8 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.9 | 192 | 7.2 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
156 | -52 | -6.7 | 0 | 0 | 17.4 | 18.1 | 18 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.9 | 233.9 | 6.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
157 | -51 | -6.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.4 | 231.7 | 6.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
158 | -50 | -6.6 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.2 | 245.3 | 6.8 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
159 | -49 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.4 | 229.3 | 6.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
160 | -48 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.2 | 242 | 6.8 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
161 | -47 | -6.2 | 0 | 0 | 17.3 | 18.2 | 18.1 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 2.7 | 246.6 | 6.2 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
162 | -46 | -6.4 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.6 | 238 | 6.5 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
163 | -45 | -0.5 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 224.6 | 6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
164 | -44 | -6.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 18 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 245.2 | 5.5 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
165 | -43 | -6.8 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.6 | 232.6 | 4.9 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
166 | -42 | -5.7 | 0 | 0 | 17.4 | 18.1 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.2 | 216.8 | 4.4 | 16.8 | 16.8 | 16.9 | 17.2 | 17.2 | 16.8 | 18.2
167 | -41 | -1.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3 | 252.4 | 5.4 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
168 | -40 | -0.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.4 | 243 | 6.9 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
169 | -39 | -0.3 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.8 | 200.1 | 7.5 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
170 | -38 | -2.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.6 | 211.2 | 6.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
171 | -37 | -3.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.5 | 240.4 | 5.9 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
172 | -36 | -3.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.4 | 249.9 | 7.4 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
173 | -35 | -5.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3 | 232 | 7.4 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
174 | -34 | -5.9 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3 | 222.2 | 7.1 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
175 | -33 | -4.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.6 | 216.7 | 6.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
176 | -32 | -2.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.3 | 237.7 | 6.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
177 | -31 | -1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.7 | 220.1 | 7.8 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
178 | -30 | 0 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.6 | 248 | 8.4 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
179 | -29 | -0.3 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.2 | 245.8 | 9.1 | 16.9 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
180 | -28 | -1.6 | 0 | 0 | 17.5 | 18.1 | 18 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.1 | 241.9 | 10.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
181 | -27 | -0.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.6 | 262.6 | 11.1 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
182 | -26 | -0.3 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.6 | 2.8 | 220.9 | 9.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
183 | -25 | -1 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.6 | 2.8 | 220.1 | 9.2 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
184 | -24 | -2 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.9 | 212 | 8.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
185 | -23 | -2.9 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.6 | 226.7 | 8.3 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
186 | -22 | -3.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.6 | 240.6 | 8.2 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
187 | -21 | -4.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.8 | 237.3 | 8.6 | 16.9 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
188 | -20 | -4.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 251.6 | 9.7 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
189 | -19 | -4.4 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.3 | 243.6 | 9.2 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
190 | -18 | -4.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.3 | 276.4 | 7.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
191 | -17 | -4.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.3 | 262.9 | 6.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
192 | -16 | -4.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 2.5 | 225.8 | 7.8 | 16.9 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
193 | -15 | -4.2 | 0 | 0 | 17.3 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.1 | 240.3 | 8.6 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.8 | 18.2
194 | -14 | -3.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.5 | 3.1 | 232.3 | 8 | 16.9 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
195 | -13 | -4 | 0 | 0 | 17.5 | 18.1 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.5 | 250 | 6.8 | 16.9 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.2
196 | -12 | -4.2 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.5 | 247.9 | 7.5 | 16.9 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
197 | -11 | -3.9 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.3 | 240.1 | 11.1 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
198 | -10 | -3.5 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.3 | 251.8 | 11.1 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
199 | -9 | -3.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.7 | 252.4 | 11.4 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
200 | -8 | -4.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.1 | 252.5 | 12 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
201 | -7 | -4.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.4 | 253.3 | 12 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
202 | -6 | -3.8 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.6 | 254.9 | 10.8 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
203 | -5 | -4.1 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.1 | 252.4 | 10.7 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.2
204 | -4 | -4.5 | 0 | 0 | 17.5 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3 | 252.9 | 10.5 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.2
205 | -3 | -4.7 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.4 | 257.7 | 11 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.2
206 | -2 | -4.6 | 0 | 0 | 17.4 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 2.6 | 252.3 | 11.5 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.2
207 | -1 | -1.9 | 0 | 0 | 17.3 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.6 | 2.6 | 246.4 | 11.3 | 16.8 | 16.8 | 17 | 17.2 | 17.2 | 16.9 | 18.3
208 | 0 | 168.2 | 67.28 | 78.6464 | 17.4 | 18.2 | 18.2 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.4 | 249 | 11 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.3
209 | 1 | 433.3 | 173.32 | 202.6011 | 17.5 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 3.8 | 257.2 | 11 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.3
210 | 2 | 514.8 | 205.92 | 240.7086 | 17.5 | 18.2 | 18.1 | 17.9 | 17.9 | 17.4 | 22.1 | 17.6 | 4 | 266.1 | 10.1 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.3
211 | 3 | 521 | 208.4 | 243.6076 | 17.4 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.6 | 5.7 | 279.2 | 10.7 | 16.8 | 16.8 | 17 | 17.2 | 17.3 | 16.9 | 18.3
212 | 4 | 506.7 | 202.68 | 236.9212 | 17.5 | 18.2 | 18.2 | 18 | 17.9 | 17.4 | 22.1 | 17.6 | 5.5 | 261.3 | 11.6 | 16.8 | 19 | 21.1 | 17.2 | 19.5 | 19.1 | 18.8
213 | 5 | 489.3 | 195.72 | 228.7854 | 17.6 | 18.3 | 18.3 | 18.1 | 18.6 | 17.5 | 22.1 | 17.6 | 4.7 | 252.1 | 14.9 | 16.9 | 35.2 | 40.8 | 17.2 | 23.4 | 25.2 | 23
214 | 6 | 478.1 | 191.24 | 223.5485 | 17.8 | 18.4 | 18.5 | 18.2 | 26.2 | 17.5 | 22.1 | 17.6 | 5.3 | 244.5 | 16.3 | 16.9 | 55.4 | 73.5 | 17.3 | 27.9 | 33.3 | 32.4
215 | 7 | 473.1 | 189.24 | 221.2107 | 18.1 | 18.6 | 18.7 | 18.5 | 37.6 | 17.5 | 22.1 | 17.6 | 6.3 | 268 | 14.9 | 16.9 | 97.6 | 115.5 | 17.6 | 33.6 | 43.9 | 42.8
216 | 8 | 472.7 | 189.08 | 221.0236 | 18.6 | 19.1 | 19 | 19.7 | 53.5 | 17.5 | 22.1 | 17.6 | 6.4 | 266.9 | 14 | 16.9 | 140.4 | 155.7 | 18.3 | 43.4 | 54.1 | 49.8
217 | 9 | 462.7 | 185.08 | 216.3479 | 19.3 | 19.7 | 19.9 | 20.8 | 73.1 | 17.6 | 22.1 | 17.6 | 7.4 | 271.2 | 16.2 | 17 | 204.3 | 204.2 | 19.4 | 50.3 | 62.5 | 54
218 | 10 | 454.4 | 181.76 | 212.467 | 20.1 | 20.5 | 21.9 | 23 | 87.3 | 17.6 | 22.1 | 17.6 | 7.6 | 262.5 | 13.4 | 17.1 | 246.1 | 264.4 | 21.1 | 61.6 | 81 | 65.1
219 | 11 | 449.2 | 179.68 | 210.0356 | 21.2 | 21.6 | 24.3 | 25.4 | 98.9 | 17.6 | 22.1 | 17.6 | 7.1 | 262.2 | 11.4 | 17.4 | 302.5 | 305.8 | 23.1 | 72.4 | 101.7 | 77.9
220 | 12 | 447.4 | 178.96 | 209.1939 | 23 | 22.8 | 26.5 | 28.4 | 114.2 | 17.7 | 22.1 | 17.6 | 7.9 | 251.5 | 14.6 | 17.8 | 347.4 | 351.2 | 25.7 | 93.2 | 151.4 | 90.1
221 | 13 | 446.4 | 178.56 | 208.7264 | 25.8 | 24.9 | 28.7 | 31.8 | 128.3 | 17.7 | 22.1 | 17.6 | 6.3 | 254.8 | 15.8 | 18.3 | 383.5 | 415.1 | 28.7 | 126.7 | 212.3 | 114.8
222 | 14 | 444.8 | 177.92 | 207.9782 | 28.9 | 28.2 | 31.6 | 35.5 | 146.6 | 17.7 | 22.1 | 17.6 | 5.2 | 247.6 | 16.5 | 19 | 430 | 471.5 | 32.4 | 139.2 | 244.7 | 144.4
223 | 15 | 443.2 | 177.28 | 207.2301 | 32.3 | 31.2 | 34.6 | 40 | 167.6 | 17.8 | 22.1 | 17.6 | 5.7 | 247.9 | 15.5 | 19.9 | 485.3 | 494.4 | 36.8 | 148.5 | 249.7 | 149
224 | 16 | 443.2 | 177.28 | 207.2301 | 35.2 | 33.9 | 38.4 | 44.3 | 192.1 | 17.8 | 22.1 | 17.7 | 4 | 232.7 | 14.7 | 20.9 | 531.7 | 533.1 | 41.6 | 166.2 | 278.3 | 162.7
225 | 17 | 444 | 177.6 | 207.6042 | 38.4 | 36.7 | 43.2 | 48.5 | 216.9 | 17.8 | 22.1 | 17.7 | 4.4 | 243.2 | 12.6 | 22.3 | 574.1 | 548 | 46.9 | 183.9 | 303.5 | 168.8
226 | 18 | 444.1 | 177.64 | 207.6509 | 42.2 | 40.3 | 48.7 | 53.3 | 232.1 | 17.8 | 22.1 | 17.8 | 5.4 | 232.1 | 12.9 | 23.9 | 621.1 | 547.9 | 52.6 | 203.6 | 325 | 168.2
227 | 19 | 444.6 | 177.84 | 207.8847 | 46.5 | 43.9 | 54.2 | 59.5 | 254.7 | 17.9 | 22.1 | 17.9 | 4.6 | 264 | 10.9 | 26 | 667.3 | 563.1 | 58.8 | 229.4 | 345.6 | 174.5
228 | 20 | 446.5 | 178.6 | 208.7731 | 51.6 | 47.7 | 60.1 | 65.4 | 280.1 | 17.9 | 22.1 | 18 | 4.1 | 259.9 | 9.9 | 28.5 | 707.5 | 583.8 | 65.5 | 249.3 | 357.5 | 175.9
229 | 21 | 447.2 | 178.88 | 209.1004 | 56.7 | 52.1 | 66.3 | 71.7 | 296.7 | 17.9 | 22.1 | 18.1 | 3.5 | 248.4 | 12.6 | 31.6 | 747.4 | 583.2 | 72.3 | 265 | 371.4 | 176.5
230 | 22 | 447.5 | 179 | 209.2407 | 62.3 | 57.5 | 72.8 | 79.9 | 311.5 | 17.9 | 22.1 | 18.2 | 4 | 254.7 | 12.4 | 35.7 | 774.5 | 596.6 | 78.7 | 282.6 | 398.5 | 189.7
231 | 23 | 447.4 | 178.96 | 209.1939 | 68.4 | 64.2 | 80.5 | 87.3 | 334.2 | 17.9 | 22.1 | 18.4 | 4.6 | 240.5 | 12 | 40.8 | 794.6 | 614 | 84.9 | 295.7 | 412.3 | 195.9
232 | 24 | 448.8 | 179.52 | 209.8485 | 73.3 | 70.1 | 86.8 | 94.9 | 354 | 17.9 | 22.1 | 18.7 | 5.4 | 254.6 | 11.1 | 46.3 | 817.6 | 622.5 | 91.9 | 309.6 | 429.1 | 202.2
233 | 25 | 450 | 180 | 210.4096 | 78.4 | 75.5 | 94.1 | 102.3 | 360.3 | 18 | 22.1 | 19.1 | 5 | 250 | 9.6 | 52.2 | 834.6 | 647.8 | 99.9 | 323.6 | 454.3 | 220.1
234 | 26 | 450.3 | 180.12 | 210.5499 | 83.7 | 81.7 | 101.4 | 109.1 | 376 | 18 | 22.1 | 19.8 | 4.4 | 258.8 | 10.8 | 59.3 | 844.8 | 674.4 | 109.3 | 329.1 | 462.1 | 231.1
235 | 27 | 451.7 | 180.68 | 211.2045 | 89.3 | 87.5 | 108.2 | 114.7 | 391.1 | 18 | 22.1 | 20.6 | 4.5 | 255.6 | 12.8 | 66.9 | 853.6 | 680.2 | 120.7 | 332.8 | 473.9 | 240.8
236 | 28 | 451.6 | 180.64 | 211.1578 | 94.5 | 93.4 | 114.8 | 120.7 | 392.3 | 18.1 | 22.1 | 21.4 | 4.2 | 259.1 | 12.8 | 75.9 | 850.8 | 672.3 | 133.3 | 336.3 | 476.4 | 243.4
237 | 29 | 452.5 | 181 | 211.5786 | 98.3 | 99.7 | 120.7 | 127.1 | 394.8 | 18.1 | 22.1 | 22 | 4.5 | 247.4 | 14.7 | 85.8 | 849.6 | 674.3 | 146.4 | 342.7 | 481.6 | 250.1
238 | 30 | 452 | 180.8 | 211.3448 | 103 | 104.6 | 126.8 | 132.2 | 397 | 18.1 | 22.1 | 22.8 | 4.3 | 236.3 | 15.4 | 94.9 | 844.7 | 678.6 | 160.2 | 346.1 | 482.6 | 254.9
239 | 31 | 452.5 | 181 | 211.5786 | 107.4 | 110.5 | 132.2 | 137.6 | 405.8 | 18.1 | 22.1 | 23.4 | 3.6 | 251.6 | 13.5 | 106 | 854.4 | 687.9 | 173.9 | 357.3 | 497.2 | 262.4
240 | 32 | 454.9 | 181.96 | 212.7008 | 111.3 | 115.9 | 137.3 | 142.5 | 416.3 | 18.1 | 22.1 | 24 | 4.2 | 280 | 11.2 | 120.5 | 855.2 | 686.5 | 187.5 | 371.3 | 500.1 | 274.1
241 | 33 | 455.3 | 182.12 | 212.8878 | 114.8 | 120.2 | 141.9 | 146.6 | 419.6 | 18.1 | 22.1 | 24.7 | 5.5 | 240.9 | 9.5 | 136.4 | 854 | 687.5 | 201.1 | 382.7 | 524.3 | 282
242 | 34 | 455.2 | 182.08 | 212.841 | 117.8 | 123.9 | 145.8 | 150.6 | 421.4 | 18.1 | 22.1 | 25.4 | 5.2 | 264.9 | 8.7 | 155.3 | 852.6 | 683.3 | 213 | 392.8 | 531.7 | 293.6
243 | 35 | 455.1 | 182.04 | 212.7943 | 121.6 | 128.1 | 149.5 | 154.9 | 426.7 | 18.2 | 22.1 | 26.2 | 5.1 | 252.8 | 10.5 | 174.4 | 850.5 | 669.5 | 223.9 | 405.6 | 541 | 298.5
244 | 36 | 455.4 | 182.16 | 212.9345 | 125.9 | 131.9 | 153 | 159 | 420.4 | 18.5 | 22.1 | 26.9 | 4.9 | 265.1 | 14.7 | 191.4 | 859.3 | 664.1 | 234.6 | 417.4 | 538.4 | 295.8
245 | 37 | 456.3 | 182.52 | 213.3554 | 130.5 | 136.5 | 157.1 | 163 | 416.2 | 18.7 | 22.1 | 27.6 | 5.3 | 251.5 | 15.4 | 204.4 | 863.3 | 656.2 | 245.5 | 427.1 | 527.9 | 299.9
246 | 38 | 457.5 | 183 | 213.9165 | 134 | 139.7 | 161.3 | 166.3 | 413.5 | 18.7 | 22.1 | 28.3 | 5.1 | 247.6 | 14.9 | 215.4 | 861.4 | 654.1 | 255.6 | 428.2 | 535 | 306.7
247 | 39 | 457.7 | 183.08 | 214.01 | 137.7 | 142.9 | 164.5 | 169.6 | 415.7 | 18.7 | 22.1 | 28.8 | 4.9 | 245.1 | 14.9 | 227.7 | 846.3 | 667.9 | 264.4 | 434.7 | 548.5 | 323.9
248 | 40 | 457.8 | 183.12 | 214.0567 | 140.9 | 147.2 | 168.6 | 172.8 | 424.4 | 18.7 | 22.1 | 29.4 | 4.8 | 257.4 | 14.5 | 240.8 | 846.8 | 688.6 | 272 | 451.5 | 567.6 | 339.8
249 | 41 | 458.1 | 183.24 | 214.197 | 144.9 | 151.5 | 171.9 | 176.4 | 441.6 | 18.7 | 22.1 | 29.9 | 4.9 | 244.2 | 13.2 | 252.9 | 871.9 | 688.6 | 278.8 | 463.2 | 581 | 346.6
250 | 42 | 458 | 183.2 | 214.1502 | 147.6 | 156 | 174.4 | 179.5 | 461.6 | 18.8 | 22.1 | 30.3 | 5.4 | 260.3 | 11.3 | 263 | 877.3 | 687.5 | 284.6 | 480.2 | 604.2 | 357.4
251 | 43 | 458.2 | 183.28 | 214.2438 | 150.8 | 160.1 | 176.9 | 182.5 | 475 | 18.8 | 22.1 | 30.7 | 6.2 | 253.4 | 11.8 | 271.5 | 866.5 | 681.3 | 290.8 | 503.6 | 621.4 | 365.4
252 | 44 | 458.1 | 183.24 | 214.197 | 153.6 | 163.4 | 180 | 185.6 | 480.9 | 18.7 | 22.1 | 31 | 6.6 | 224 | 12.7 | 280.9 | 867 | 670.6 | 297.8 | 522.1 | 648.5 | 377.3
253 | 45 | 458.1 | 183.24 | 214.197 | 156.7 | 166.9 | 183.1 | 188.6 | 481.2 | 18.7 | 22.1 | 31.2 | 6.8 | 234 | 11.4 | 289.6 | 863.3 | 685.3 | 304.7 | 531.3 | 661.6 | 382
254 | 46 | 459.9 | 183.96 | 215.0386 | 159.7 | 169.6 | 185.6 | 191.2 | 483 | 18.7 | 22.1 | 31.4 | 7.3 | 234.8 | 13.1 | 298.8 | 856.2 | 673.7 | 311.2 | 537.3 | 656.5 | 385.5
255 | 47 | 459.1 | 183.64 | 214.6646 | 160.9 | 172.8 | 187.8 | 192.9 | 478.1 | 18.7 | 22.1 | 31.5 | 6 | 265.5 | 13.5 | 308.3 | 853.4 | 671.5 | 318.4 | 540.2 | 645.8 | 391.1
256 | 48 | 459.4 | 183.76 | 214.8049 | 162 | 176.2 | 190.1 | 195.7 | 490.3 | 18.6 | 22.1 | 31.7 | 4.9 | 251.3 | 12.1 | 318.6 | 861.2 | 670.1 | 325.9 | 540 | 643.7 | 394.6
257 | 49 | 459.9 | 183.96 | 215.0386 | 163.3 | 179.3 | 193 | 198.1 | 492.1 | 18.6 | 22 | 31.8 | 4.2 | 245.7 | 14.7 | 329.5 | 856.3 | 687.7 | 333.7 | 544.8 | 649.8 | 412.7
258 | 50 | 460.2 | 184.08 | 215.1789 | 166.2 | 182 | 195.1 | 200.8 | 487.7 | 18.7 | 22 | 31.8 | 4 | 244.6 | 17 | 340.9 | 856.2 | 702.8 | 340.6 | 549.4 | 656.4 | 436.5
259 | 51 | 461.1 | 184.44 | 215.5997 | 170.1 | 184.5 | 197.2 | 202.4 | 478.8 | 18.7 | 22 | 32 | 3.3 | 246.4 | 17.3 | 352.6 | 864 | 705.7 | 347.6 | 552.3 | 654.8 | 441.9
260 | 52 | 460.3 | 184.12 | 215.2257 | 173 | 186.3 | 199.4 | 203.6 | 477.2 | 18.6 | 22 | 32.1 | 3.4 | 246.2 | 16.8 | 365.1 | 869 | 700.8 | 354.5 | 556.8 | 650.8 | 440.8
261 | 53 | 462 | 184.8 | 216.0206 | 175.2 | 188.4 | 201.1 | 204.7 | 481.1 | 18.6 | 22 | 32.3 | 4.3 | 245.3 | 15.9 | 377.2 | 869.2 | 691.4 | 360.9 | 562.5 | 651.1 | 446.7
262 | 54 | 461.7 | 184.68 | 215.8803 | 177.2 | 190.3 | 202.4 | 205.9 | 478.9 | 18.7 | 22 | 32.5 | 4.5 | 259.6 | 14.9 | 389.8 | 869.2 | 697 | 367.6 | 565.4 | 650.9 | 452.4
263 | 55 | 464.7 | 185.88 | 217.283 | 178.7 | 192.8 | 204.2 | 207.7 | 490.1 | 18.7 | 22 | 32.7 | 4.6 | 250.4 | 14.3 | 402.4 | 870.7 | 694.8 | 374.9 | 568.7 | 637.8 | 453
264 | 56 | 466.3 | 186.52 | 218.0311 | 181.3 | 195.6 | 205.3 | 209 | 485.7 | 18.8 | 22 | 32.9 | 4.4 | 255.5 | 15.1 | 414.1 | 867.8 | 681.1 | 382.5 | 567.6 | 627.9 | 448.2
265 | 57 | 466.5 | 186.6 | 218.1246 | 182.6 | 197.8 | 206.3 | 211.6 | 472 | 18.8 | 22 | 33 | 4.2 | 253.3 | 15 | 425.1 | 864.2 | 688.9 | 389.3 | 571.9 | 630.6 | 451
266 | 58 | 466.8 | 186.72 | 218.2649 | 183.7 | 198.8 | 207.6 | 213.2 | 472.5 | 18.8 | 22 | 33.2 | 4.2 | 249.6 | 14.3 | 436.3 | 857.7 | 697.3 | 395.8 | 569.8 | 635 | 453.2
267 | 59 | 467.4 | 186.96 | 218.5455 | 184.4 | 199.4 | 208.9 | 215.1 | 465.5 | 18.9 | 22 | 33.3 | 4.4 | 259 | 12.6 | 445.3 | 856.6 | 688.4 | 402.2 | 588.1 | 651.3 | 467
268 | 60 | 467.9 | 187.16 | 218.7793 | 185.6 | 201.7 | 209.5 | 216.8 | 470.3 | 18.9 | 22 | 33.6 | 5.4 | 271.1 | 12.7 | 452.2 | 852.4 | 670.5 | 408.8 | 602 | 651.8 | 475.5
269 | 61 | 468 | 187.2 | 218.826 | 186.5 | 203.9 | 210.6 | 217.9 | 462.9 | 19 | 22 | 33.9 | 5.8 | 261.7 | 12.7 | 458 | 846.5 | 653.2 | 415.6 | 609.1 | 658.9 | 482.4
270 | 62 | 470 | 188 | 219.7612 | 187.6 | 205.6 | 212.1 | 219.5 | 472.4 | 19 | 22 | 34.4 | 5 | 268.9 | 11.7 | 466 | 606.6 | 656.7 | 422.7 | 619 | 661.8 | 486
271 | 63 | 469.5 | 187.8 | 219.5274 | 189.5 | 206.5 | 214.6 | 220.5 | 468.9 | 19 | 22 | 34.6 | 3.9 | 258.5 | 13 | 475.5 | 811.3 | 666.9 | 429.3 | 620.5 | 658 | 489.3
272 | 64 | 467.5 | 187 | 218.5922 | 190.8 | 207.9 | 216.6 | 221.4 | 477.6 | 19 | 22 | 34.9 | 3.4 | 236 | 12.9 | 487.3 | 751.1 | 684.2 | 435.1 | 617.2 | 645.9 | 495.7
273 | 65 | 463.5 | 185.4 | 216.7219 | 192.9 | 208.1 | 217.4 | 222.5 | 470.9 | 19 | 22 | 35.3 | 4.3 | 249.1 | 13.8 | 496.6 | 822.3 | 710.9 | 440.4 | 607.6 | 630.5 | 498.8
274 | 66 | 464.2 | 185.68 | 217.0492 | 194.5 | 208.3 | 217.8 | 223.6 | 463.9 | 19 | 22 | 35.6 | 4.3 | 248.8 | 12.1 | 505.2 | 807.9 | 717.6 | 446 | 601.1 | 618.1 | 502.8
275 | 67 | 465.2 | 186.08 | 217.5168 | 196.3 | 209.2 | 218 | 224.2 | 455.4 | 19 | 22 | 35.9 | 3.8 | 252 | 12.4 | 514.6 | 800.3 | 717.3 | 452 | 597.5 | 621 | 506.8
276 | 68 | 466.3 | 186.52 | 218.0311 | 197.4 | 210.2 | 217.9 | 224.6 | 452.7 | 19 | 22 | 36.1 | 3.6 | 251.2 | 13.7 | 523 | 795 | 721.3 | 457.9 | 591.2 | 628.9 | 514.5
277 | 69 | 466.5 | 186.6 | 218.1246 | 195.6 | 211.5 | 219.4 | 225.1 | 442.3 | 19.2 | 22 | 36.4 | 4.8 | 254.4 | 14.7 | 531.8 | 799.1 | 721.4 | 462.5 | 584.3 | 621.6 | 517.3
278 | 70 | 465.4 | 186.16 | 217.6103 | 195.8 | 211.6 | 219.1 | 225.1 | 433.3 | 19.1 | 21.9 | 36.7 | 5 | 257.5 | 14.6 | 540.3 | 809.9 | 710 | 465.9 | 581.9 | 614.3 | 522.4
279 | 71 | 465.8 | 186.32 | 217.7973 | 196.3 | 212.2 | 220.1 | 225.6 | 430 | 19.1 | 21.9 | 37 | 5.8 | 247.9 | 13.7 | 550.1 | 815.5 | 699.1 | 470 | 582.2 | 605.5 | 516.7
280 | 72 | 465.1 | 186.04 | 217.47 | 196.9 | 212.7 | 220.2 | 226.3 | 428.5 | 19.1 | 21.9 | 37.3 | 5.6 | 244.8 | 14.5 | 557.5 | 817.3 | 686.1 | 474.1 | 583 | 598.1 | 516.4
281 | 73 | 466.1 | 186.44 | 217.9376 | 197.9 | 213.1 | 220.5 | 227.3 | 424.2 | 19.1 | 21.9 | 37.7 | 5.2 | 244.7 | 14.6 | 564.5 | 824.7 | 682.8 | 477.9 | 582.1 | 594.2 | 515.5
282 | 74 | 466.4 | 186.56 | 218.0779 | 199.8 | 213.5 | 220.6 | 227.5 | 429.4 | 19.2 | 21.9 | 38 | 4.6 | 236.7 | 13.2 | 572.9 | 836.7 | 674.9 | 482.5 | 589.2 | 608.5 | 527.8
283 | 75 | 468.8 | 187.52 | 219.2001 | 201.8 | 214.1 | 221.8 | 228.1 | 443.3 | 19.2 | 21.9 | 38.3 | 4.4 | 237.5 | 14.1 | 579.9 | 838.8 | 666.9 | 487.2 | 594.2 | 617.8 | 539
284 | 76 | 467.7 | 187.08 | 218.6857 | 202.8 | 214.5 | 222.7 | 229.2 | 450 | 19.3 | 21.9 | 38.5 | 4.5 | 242.6 | 15.1 | 585.7 | 840.8 | 662 | 491.5 | 609.2 | 632.4 | 541.1
285 | 77 | 466.8 | 186.72 | 218.2649 | 202.4 | 215.3 | 223.7 | 229.7 | 449.8 | 19.3 | 21.9 | 38.6 | 3.3 | 255 | 14.3 | 590.8 | 842.2 | 652.9 | 495.9 | 628.7 | 637.8 | 543.5
286 | 78 | 466.1 | 186.44 | 217.9376 | 202.3 | 215.9 | 224.5 | 230.1 | 452.8 | 19.4 | 21.9 | 38.8 | 3.7 | 248.3 | 14.1 | 594.1 | 848.4 | 637.5 | 500.4 | 636.3 | 650.2 | 543.1
287 | 79 | 465.5 | 186.2 | 217.6571 | 204 | 216.4 | 225.3 | 231.3 | 468.4 | 19.5 | 21.9 | 39 | 4 | 255.4 | 13.5 | 598.7 | 849.9 | 648.7 | 504.7 | 658.7 | 672.7 | 555.9
288 | 80 | 467 | 186.8 | 218.3584 | 205.4 | 217.3 | 225.5 | 231.9 | 479.4 | 19.6 | 21.9 | 39.1 | 4.1 | 249.5 | 12.3 | 599.7 | 847.2 | 650 | 508.8 | 679.6 | 694.5 | 570.4
289 | 81 | 467.7 | 187.08 | 218.6857 | 205.2 | 218.5 | 226 | 233.3 | 477.7 | 19.6 | 21.9 | 39.3 | 4 | 250.3 | 10.8 | 600.3 | 838.5 | 642.8 | 512.1 | 685.8 | 705.1 | 576.7
290 | 82 | 468.7 | 187.48 | 219.1533 | 206.3 | 219.2 | 226.7 | 234.6 | 487.5 | 19.7 | 21.9 | 39.4 | 3.9 | 255.9 | 9.2 | 605.7 | 833.2 | 650.6 | 515.4 | 683.2 | 715.5 | 579.4
291 | 83 | 469.2 | 187.68 | 219.3871 | 206.4 | 218.7 | 227.4 | 235.9 | 480.9 | 19.7 | 21.9 | 39.5 | 4.2 | 268.4 | 8.4 | 612 | 833.7 | 647.7 | 519.1 | 676 | 695.9 | 577.6
292 | 84 | 469.3 | 187.72 | 219.4339 | 207.2 | 218.5 | 228.4 | 237.1 | 466.6 | 19.7 | 21.9 | 39.5 | 3.5 | 263.1 | 9.6 | 616.1 | 835.3 | 632.1 | 522.7 | 682.8 | 678 | 568.4
293 | 85 | 468.7 | 187.48 | 219.1533 | 208.6 | 218.7 | 229.2 | 237.3 | 478 | 19.7 | 21.9 | 39.6 | 3.8 | 259.9 | 11.8 | 622.2 | 838.7 | 640.5 | 526.5 | 690.8 | 686.4 | 578
294 | 86 | 468.4 | 187.36 | 219.013 | 209.9 | 219.4 | 230.2 | 236.7 | 482.6 | 19.8 | 21.9 | 39.7 | 4.6 | 254.3 | 12.7 | 629.3 | 841.5 | 662.3 | 530.5 | 693.1 | 688.2 | 590.3
295 | 87 | 469.6 | 187.84 | 219.5741 | 210.2 | 220 | 231.3 | 236.1 | 487.3 | 19.8 | 21.9 | 39.8 | 4.9 | 263.8 | 12.9 | 637.9 | 841.9 | 679.5 | 534.2 | 692.5 | 684.5 | 596.2
296 | 88 | 469.9 | 187.96 | 219.7144 | 210.4 | 220.5 | 231.5 | 236 | 476.6 | 19.9 | 21.9 | 39.9 | 5.1 | 273.8 | 13.4 | 644.8 | 841.2 | 691.3 | 537.3 | 678.5 | 683.9 | 601.3
297 | 89 | 468.7 | 187.48 | 219.1533 | 211.1 | 221.5 | 231.7 | 236.8 | 465 | 19.9 | 21.8 | 40.1 | 6.5 | 263.2 | 13.8 | 650.8 | 838.2 | 700.6 | 540 | 671.3 | 675 | 599.1
298 | 90 | 468.6 | 187.44 | 219.1066 | 212.2 | 222.7 | 232.3 | 237.2 | 463.5 | 20 | 21.8 | 40.2 | 6.5 | 255.2 | 13.4 | 656.7 | 837.6 | 675.3 | 542.6 | 675.5 | 664.4 | 590.4
299 | 91 | 468.9 | 187.56 | 219.2468 | 212.7 | 223.8 | 232.9 | 237.4 | 457.6 | 20.1 | 21.8 | 40.2 | 5.2 | 254.5 | 14 | 661.8 | 836.8 | 658.4 | 545.7 | 689.3 | 670.1 | 584
300 | 92 | 467.7 | 187.08 | 218.6857 | 212.6 | 224.3 | 233 | 237.8 | 478.2 | 20.1 | 21.8 | 40.3 | 5.6 | 255.5 | 13.7 | 671.1 | 840.5 | 667.2 | 549 | 698.4 | 676.9 | 587.9
301 | 93 | 468.6 | 187.44 | 219.1066 | 213.2 | 224.4 | 232.9 | 238.1 | 488.6 | 20.2 | 21.8 | 40.3 | 5.3 | 255.6 | 12.6 | 678.4 | 843.3 | 673.5 | 552.6 | 697.2 | 673.7 | 589.2
302 | 94 | 469.7 | 187.88 | 219.6209 | 214.7 | 223.8 | 232.7 | 238.3 | 482.5 | 20.2 | 21.8 | 40.4 | 4.1 | 263.4 | 12.8 | 684.5 | 848 | 676.7 | 556.1 | 707 | 675.7 | 592.2
303 | 95 | 470 | 188 | 219.7612 | 215.1 | 223.7 | 232.3 | 237.8 | 481.3 | 20.3 | 21.8 | 40.5 | 4.2 | 253.6 | 13.6 | 691.3 | 854.2 | 681.9 | 559.7 | 708.4 | 666.6 | 596.8
304 | 96 | 470 | 188 | 219.7612 | 215 | 224.3 | 232.1 | 237.1 | 482.1 | 20.3 | 21.8 | 40.7 | 4.7 | 251.3 | 13.1 | 694.3 | 857.4 | 676.2 | 563.7 | 699.6 | 656.7 | 590.7
305 | 97 | 470.1 | 188.04 | 219.8079 | 215.1 | 224.6 | 232.4 | 237 | 482.2 | 20.3 | 21.8 | 40.9 | 4.2 | 251.9 | 11.9 | 700.5 | 857.6 | 663.4 | 567.6 | 697.2 | 647.2 | 586.7
306 | 98 | 471.2 | 188.48 | 220.3223 | 216.3 | 225 | 232.7 | 237.3 | 489.8 | 20.3 | 21.8 | 41 | 4.5 | 265.8 | 10.1 | 703.1 | 860.1 | 642.9 | 571.2 | 696.6 | 639.6 | 583.3
307 | 99 | 470.5 | 188.2 | 219.995 | 216.4 | 224.5 | 232.8 | 238.3 | 484.8 | 20.3 | 21.8 | 41.1 | 5.3 | 273.7 | 8.8 | 706.8 | 862.2 | 640.7 | 573.8 | 695.4 | 629.3 | 589.1
308 | 100 | 470.7 | 188.28 | 220.0885 | 216.3 | 223.9 | 233.6 | 239.7 | 470.8 | 20.3 | 21.8 | 41.4 | 5.3 | 264.1 | 11 | 711.7 | 860.2 | 632.5 | 575.9 | 685.3 | 626.1 | 591
309 | 101 | 470.3 | 188.12 | 219.9014 | 217.3 | 224 | 235.2 | 240.6 | 464 | 20.3 | 21.8 | 41.7 | 5.7 | 267.7 | 12 | 717.8 | 854.7 | 636.5 | 577.8 | 676.8 | 614.7 | 587.4
310 | 102 | 470.6 | 188.24 | 220.0417 | 218.2 | 224.9 | 236.1 | 241.2 | 459.8 | 20.3 | 21.8 | 42 | 5.3 | 259.5 | 12.5 | 719.8 | 856.9 | 616.7 | 580.1 | 677.4 | 601.6 | 583.1
311 | 103 | 472.8 | 189.12 | 221.0704 | 218.6 | 225.2 | 237 | 241.3 | 464.4 | 20.3 | 21.8 | 42.1 | 5.3 | 263.8 | 13.4 | 715.6 | 852.2 | 603.3 | 582.4 | 682 | 604 | 583.2
312 | 104 | 473.8 | 189.52 | 221.538 | 218.1 | 225.4 | 238.4 | 241.6 | 471.2 | 20.3 | 21.8 | 42.2 | 5.2 | 268 | 14 | 334.7 | 307.1 | 323.4 | 584.2 | 676.6 | 602.9 | 582.4
313 | 105 | 472.8 | 189.12 | 221.0704 | 218.6 | 226.2 | 239.5 | 242.8 | 468.7 | 20.4 | 21.8 | 42.3 | 5.9 | 258.7 | 16.8 | 728.5 | 848.3 | 612.3 | 585.5 | 667.4 | 587 | 582.9
314 | 106 | 471.9 | 188.76 | 220.6496 | 219 | 226.8 | 240.1 | 243.4 | 471.9 | 20.4 | 21.8 | 42.6 | 6.1 | 267 | 17.2 | 739.1 | 849.6 | 631.3 | 586.6 | 656.9 | 570.3 | 583.3
315 | 107 | 472.5 | 189 | 220.9301 | 219.6 | 227.1 | 240.2 | 244.3 | 470.2 | 20.5 | 21.8 | 42.8 | 6 | 269.7 | 16.8 | 747 | 849 | 645.5 | 587.7 | 647.7 | 570.6 | 584.2
316 | 108 | 471.6 | 188.64 | 220.5093 | 221.2 | 228.6 | 240.5 | 245.3 | 469.9 | 20.6 | 21.8 | 42.9 | 5.9 | 270.7 | 15.3 | 749.9 | 844.4 | 648.6 | 589.1 | 643.9 | 561 | 584.5
317 | 109 | 470.2 | 188.08 | 219.8547 | 222.8 | 229.4 | 240.5 | 245.2 | 465.9 | 20.6 | 21.8 | 42.9 | 4.7 | 268.2 | 15.4 | 753.1 | 846.3 | 649.1 | 590.4 | 642.9 | 554.7 | 584.5
318 | 110 | 470.5 | 188.2 | 219.995 | 223.6 | 229.7 | 240.6 | 245.4 | 464.9 | 20.7 | 21.8 | 43 | 4.9 | 268.8 | 14.7 | 757.3 | 856.7 | 652.1 | 592.1 | 640.4 | 546.9 | 588.5
319 | 111 | 469.9 | 187.96 | 219.7144 | 222.7 | 230.8 | 242.3 | 245.8 | 458 | 21.2 | 21.8 | 43.2 | 4.9 | 282 | 13.3 | 752.8 | 855.6 | 634.5 | 594.7 | 639.5 | 544.3 | 585.3
320 | 112 | 471.2 | 188.48 | 220.3223 | 226 | 230.1 | 239.9 | 244.5 | 449.7 | 20.8 | 21.8 | 43.1 | 4.4 | 283.9 | 13.4 | 752.4 | 861.5 | 639.4 | 595.2 | 641.6 | 547.7 | 586.1
321 | 113 | 470.4 | 188.16 | 219.9482 | 226.4 | 230.5 | 239.4 | 245.6 | 447.5 | 20.9 | 21.8 | 43.2 | 4.2 | 273.8 | 14.1 | 757.3 | 865.6 | 648.2 | 596.7 | 642.6 | 548.5 | 590.6
322 | 114 | 471.1 | 188.44 | 220.2755 | 227.3 | 230.9 | 239.3 | 246.4 | 456.8 | 21 | 21.8 | 43.4 | 4.3 | 253.1 | 12.7 | 765.4 | 863.4 | 657.9 | 597.5 | 637.1 | 536.4 | 589.3
323 | 115 | 473.1 | 189.24 | 221.2107 | 226.9 | 231.1 | 240.5 | 247.2 | 455.3 | 21 | 21.8 | 43.4 | 4.2 | 249.3 | 12.7 | 764.5 | 858 | 644.2 | 597.9 | 636.3 | 527.2 | 582.4
324 | 116 | 472.9 | 189.16 | 221.1171 | 227 | 231.2 | 241 | 247.8 | 456.5 | 21 | 21.8 | 43.5 | 3.4 | 231.8 | 12.6 | 767.1 | 860.1 | 632.4 | 598.3 | 639.9 | 522.6 | 580.4
325 | 117 | 472.9 | 189.16 | 221.1171 | 226.5 | 231.3 | 241.2 | 248.3 | 466.1 | 21 | 21.7 | 43.6 | 3.6 | 239.5 | 10.6 | 772.3 | 868.6 | 641.4 | 599.6 | 643.4 | 526 | 580.2
326 | 118 | 473.7 | 189.48 | 221.4912 | 226.1 | 232 | 241.1 | 248.9 | 480.1 | 21.1 | 21.7 | 43.8 | 3.8 | 240 | 10.1 | 772.7 | 876.4 | 646.2 | 601.4 | 643 | 527.5 | 585.2
327 | 119 | 473.5 | 189.4 | 221.3977 | 227 | 232.7 | 239.7 | 249.2 | 477.4 | 21.2 | 21.7 | 43.9 | 4.6 | 239.8 | 9.9 | 772.2 | 875.1 | 657.6 | 602.6 | 639.7 | 528.1 | 588.3
328 | 120 | 471.8 | 188.72 | 220.6028 | 228.7 | 233.2 | 239.1 | 249.5 | 474.6 | 21.3 | 21.7 | 44 | 4 | 248.6 | 9.7 | 770 | 862.2 | 672.7 | 603.2 | 635.5 | 530.4 | 591.3
329 | 121 | 471.8 | 188.72 | 220.6028 | 228.4 | 233.3 | 239.5 | 250.1 | 468.4 | 21.4 | 21.7 | 44.2 | 3.7 | 242.4 | 8.8 | 772.2 | 856.3 | 685.7 | 603.9 | 635.6 | 529.3 | 594.1
330 | 122 | 471.8 | 188.72 | 220.6028 | 227.6 | 233.4 | 239.4 | 250.2 | 465.4 | 21.4 | 21.7 | 44.4 | 4.3 | 256.3 | 8.5 | 775.8 | 850.7 | 687.5 | 604.2 | 630.9 | 524.4 | 591.6
331 | 123 | 472 | 188.8 | 220.6963 | 227.3 | 233.6 | 239.5 | 250 | 463.2 | 21.5 | 21.7 | 44.4 | 3.7 | 238 | 8.4 | 776.3 | 844.7 | 692.2 | 604.4 | 625.8 | 529.1 | 592.6
332 | 124 | 472.3 | 188.92 | 220.8366 | 228.4 | 234.3 | 239.9 | 249.8 | 463.1 | 21.5 | 21.7 | 44.5 | 4.8 | 243.4 | 8.4 | 768 | 826.6 | 677.4 | 605.3 | 621.1 | 531.2 | 592.6
333 | 125 | 472.6 | 189.04 | 220.9769 | 229.2 | 234.3 | 240.5 | 249.6 | 456.6 | 21.6 | 21.7 | 44.7 | 5 | 264.9 | 9.1 | 711.6 | 760.6 | 633.7 | 606.8 | 616.7 | 522 | 588.4
334 | 126 | 472.8 | 189.12 | 221.0704 | 230.5 | 234.1 | 240.2 | 249.1 | 451.9 | 21.6 | 21.7 | 44.8 | 4.2 | 254.7 | 9.3 | 780.1 | 832.8 | 688.2 | 608.5 | 617.4 | 521.2 | 587.3
335 | 127 | 472.5 | 189 | 220.9301 | 231.5 | 233.5 | 240.6 | 249.1 | 451.3 | 21.7 | 21.7 | 44.9 | 5 | 238.7 | 9.3 | 719.8 | 763.4 | 651.8 | 610.7 | 613 | 525 | 589.2
336 | 128 | 473.2 | 189.28 | 221.2574 | 231.6 | 234.4 | 241 | 249.4 | 462.3 | 21.7 | 21.7 | 45 | 5.8 | 253 | 9.2 | 775.7 | 831.4 | 717.3 | 613.7 | 613.6 | 533.6 | 599.1
337 | 129 | 472.8 | 189.12 | 221.0704 | 232.2 | 235.7 | 241.7 | 249.3 | 468 | 21.8 | 21.7 | 45.1 | 5.2 | 248 | 9.7 | 785.4 | 847.3 | 723 | 617.4 | 614.8 | 533.8 | 604.6
338 | 130 | 472.6 | 189.04 | 220.9769 | 234.2 | 236.8 | 242.6 | 249.5 | 464.7 | 21.8 | 21.7 | 45.2 | 5.3 | 231.3 | 10.2 | 786.3 | 831.9 | 729.5 | 620.2 | 614.5 | 528.2 | 602.1
339 | 131 | 472.3 | 188.92 | 220.8366 | 234.5 | 237.8 | 243.3 | 249.6 | 462.8 | 21.9 | 21.7 | 45.3 | 4.8 | 248.3 | 10.2 | 786 | 815.6 | 736.2 | 621.7 | 610.8 | 524.7 | 605
340 | 132 | 474.3 | 189.72 | 221.7717 | 233.9 | 239.6 | 243.5 | 250.3 | 464.8 | 22 | 21.7 | 45.3 | 4.5 | 249.9 | 9.5 | 784.7 | 805.7 | 735.1 | 622.8 | 608.8 | 526 | 608.9
341 | 133 | 473.5 | 189.4 | 221.3977 | 234.5 | 241.2 | 243.9 | 250.2 | 467.2 | 22 | 21.7 | 45.3 | 4.3 | 247.5 | 8.4 | 782.5 | 814 | 737.3 | 624.4 | 608.3 | 533.3 | 616.1
342 | 134 | 473.5 | 189.4 | 221.3977 | 234 | 242.4 | 243.8 | 249.7 | 469.3 | 22 | 21.7 | 45.4 | 4.3 | 261.3 | 11 | 784.8 | 818.7 | 757.4 | 626.6 | 606.9 | 543.8 | 624.4
343 | 135 | 473.9 | 189.56 | 221.5847 | 232 | 242.7 | 243.1 | 249.6 | 469.7 | 22 | 21.7 | 45.6 | 5.1 | 259.1 | 14.1 | 788 | 827.5 | 758.7 | 628.9 | 606.1 | 554.2 | 637.5
344 | 136 | 472.8 | 189.12 | 221.0704 | 231 | 242.7 | 243.6 | 249.5 | 479.5 | 22 | 21.7 | 45.7 | 5.2 | 259.3 | 13.9 | 736.2 | 774.5 | 700.1 | 631.8 | 606.9 | 567.4 | 637.4
345 | 137 | 472.6 | 189.04 | 220.9769 | 231.1 | 242.5 | 244 | 249.6 | 489.5 | 22.1 | 21.6 | 45.8 | 4.5 | 250.2 | 14.2 | 781.5 | 828.8 | 743.4 | 634.7 | 612.6 | 578.9 | 645.3
346 | 138 | 472.6 | 189.04 | 220.9769 | 231 | 243.1 | 244.9 | 250.5 | 486.2 | 22.2 | 21.6 | 46 | 5.2 | 238 | 13.3 | 781.3 | 820.2 | 740.8 | 637.1 | 613.8 | 588.6 | 649.4
347 | 139 | 474.3 | 189.72 | 221.7717 | 231 | 243.6 | 246 | 251.2 | 485.4 | 22.3 | 21.6 | 46.3 | 4.8 | 249.2 | 11.7 | 716.8 | 747.9 | 676.4 | 639.2 | 617.2 | 597.3 | 649.4
348 | 140 | 473.5 | 189.4 | 221.3977 | 231.5 | 243.3 | 246.3 | 252.2 | 491.7 | 22.4 | 21.6 | 46.5 | 4 | 239.3 | 9.3 | 782 | 819.8 | 733.7 | 641.6 | 620 | 602 | 648.4
349 | 141 | 473 | 189.2 | 221.1639 | 232 | 243.7 | 246.4 | 253.2 | 502.4 | 22.4 | 21.6 | 46.5 | 4.3 | 260.3 | 8 | 738 | 774.7 | 702.6 | 644 | 624 | 598.4 | 645.4
350 | 142 | 472.6 | 189.04 | 220.9769 | 232.4 | 243.8 | 247.3 | 253.2 | 504.5 | 22.5 | 21.6 | 46.8 | 5.2 | 256.7 | 7.8 | 779.7 | 817.6 | 738.8 | 646 | 627.6 | 592.2 | 639.3
351 | 143 | 471.4 | 188.56 | 220.4158 | 232.8 | 244 | 247.6 | 254.1 | 496.8 | 22.5 | 21.6 | 47 | 5.8 | 240.2 | 7.4 | 782.3 | 819.9 | 730.2 | 647.8 | 629.7 | 593.4 | 637.6
352 | 144 | 471.7 | 188.68 | 220.556 | 233.4 | 244.4 | 247.8 | 254.3 | 500 | 22.5 | 21.6 | 47.2 | 5.9 | 235.9 | 8.8 | 739.1 | 784.2 | 682.5 | 649.6 | 634 | 594.8 | 639.5
353 | 145 | 471.9 | 188.76 | 220.6496 | 233.6 | 243.7 | 248.6 | 254.2 | 516.1 | 22.5 | 21.6 | 47.3 | 7.8 | 240.7 | 10.4 | 785.2 | 836.3 | 723.5 | 651.4 | 636.2 | 599.1 | 642.9
354 | 146 | 472 | 188.8 | 220.6963 | 233 | 243.5 | 248.8 | 254.8 | 519.4 | 22.7 | 21.6 | 47.5 | 7.5 | 242.2 | 12.6 | 786.5 | 835.7 | 728.6 | 653.2 | 640.1 | 604.7 | 644.5
355 | 147 | 472.1 | 188.84 | 220.7431 | 233.2 | 244.1 | 249.8 | 255.1 | 522 | 22.8 | 21.6 | 47.6 | 5.2 | 237.3 | 13.3 | 784.9 | 829.7 | 733.6 | 654.4 | 646.5 | 619.4 | 641.4
356 | 148 | 472.5 | 189 | 220.9301 | 232.8 | 244.4 | 250.3 | 255.3 | 521.8 | 22.9 | 21.6 | 47.6 | 4.8 | 237.1 | 14.6 | 784.7 | 817.5 | 734.3 | 655.3 | 648 | 615.1 | 640.6
357 | 149 | 472.7 | 189.08 | 221.0236 | 232.8 | 244.8 | 250.9 | 256.2 | 519.9 | 22.9 | 21.6 | 47.7 | 4.1 | 241.7 | 14.7 | 782.2 | 812.8 | 739 | 656.5 | 651.6 | 623.2 | 643.8
358 | 150 | 473.2 | 189.28 | 221.2574 | 232.8 | 245.1 | 251.5 | 256.4 | 526.6 | 23 | 21.6 | 47.7 | 2.9 | 242.9 | 15.5 | 785.1 | 807.3 | 750 | 657.9 | 651.6 | 624.9 | 647.8
359 | 151 | 472.7 | 189.08 | 221.0236 | 232.4 | 245.1 | 251.8 | 256.7 | 525.3 | 23 | 21.6 | 47.6 | 2.9 | 237.1 | 14.4 | 790 | 790.5 | 757.6 | 658.7 | 646.6 | 613.7 | 648.3
360 | 152 | 472.9 | 189.16 | 221.1171 | 232.6 | 246.2 | 252.1 | 256.9 | 517.7 | 23.2 | 21.6 | 47.5 | 3.2 | 239.2 | 12.3 | 789 | 769.1 | 764.7 | 658.7 | 641 | 600.3 | 643.6
361 | 153 | 473.1 | 189.24 | 221.2107 | 233.1 | 247.7 | 252.1 | 256.4 | 509.9 | 23.4 | 21.6 | 47.7 | 3.9 | 246 | 11 | 792.4 | 764.6 | 763.3 | 658.4 | 633.1 | 582.2 | 634
362 | 154 | 473.2 | 189.28 | 221.2574 | 234.3 | 248.6 | 252.6 | 255.8 | 501.1 | 23.5 | 21.6 | 47.8 | 3.6 | 244.9 | 12.7 | 793.7 | 762.7 | 776.8 | 657.9 | 629.2 | 572.3 | 632.6
363 | 155 | 473.3 | 189.32 | 221.3042 | 235.1 | 250.6 | 252.9 | 256 | 500.9 | 23.6 | 21.6 | 47.8 | 3.5 | 250 | 13.7 | 791.8 | 768.3 | 786.1 | 657.6 | 626.7 | 576.2 | 647.8
364 | 156 | 472.9 | 189.16 | 221.1171 | 235.7 | 251.7 | 253.2 | 255.8 | 499.1 | 23.7 | 21.6 | 47.9 | 3.3 | 248.5 | 12.8 | 792.2 | 770.1 | 788.9 | 658.1 | 624.5 | 588.6 | 657.9
365 | 157 | 473 | 189.2 | 221.1639 | 236.1 | 251.3 | 253.3 | 255.8 | 485.9 | 23.9 | 21.6 | 47.9 | 2.9 | 241.4 | 12.6 | 789.4 | 785.5 | 787.1 | 659.2 | 624.5 | 597 | 660.8
366 | 158 | 473 | 189.2 | 221.1639 | 236.3 | 250.3 | 253.7 | 256.4 | 491.2 | 24 | 21.6 | 47.9 | 2.6 | 251.9 | 10.5 | 793.4 | 798.1 | 781.1 | 660.9 | 623.7 | 601.6 | 658.6
367 | 159 | 473.1 | 189.24 | 221.2107 | 236.5 | 248.9 | 254.3 | 257.5 | 496.2 | 24.1 | 21.6 | 47.8 | 2.8 | 237.4 | 8.8 | 798.1 | 816.7 | 773.8 | 662.5 | 625.6 | 602.3 | 653.8
368 | 160 | 472.7 | 189.08 | 221.0236 | 236.2 | 248 | 254.6 | 257.8 | 497.5 | 24.2 | 21.6 | 47.8 | 3.1 | 247.6 | 10.5 | 800.4 | 825.8 | 769.9 | 664.6 | 633.2 | 602.5 | 652
369 | 161 | 472.9 | 189.16 | 221.1171 | 236 | 248 | 254.2 | 257.7 | 499.3 | 24.2 | 21.5 | 47.9 | 2.9 | 238.9 | 11.1 | 800.8 | 845.2 | 765.4 | 667 | 634.1 | 595.2 | 651.5
370 | 162 | 472 | 188.8 | 220.6963 | 234.7 | 247.7 | 254.1 | 258.2 | 488.5 | 24.2 | 21.5 | 48 | 3.5 | 239.1 | 11.9 | 805.8 | 838.5 | 781 | 669 | 635.6 | 596.9 | 654
371 | 163 | 472.3 | 188.92 | 220.8366 | 234.8 | 248.6 | 254.2 | 259 | 485.4 | 24.3 | 21.5 | 48.1 | 3.6 | 236.4 | 11.8 | 803.8 | 832.6 | 769.9 | 670.8 | 643.8 | 604 | 662.6
372 | 164 | 473.2 | 189.28 | 221.2574 | 235.3 | 249.9 | 254.2 | 258.5 | 479.9 | 24.4 | 21.5 | 48.2 | 3.9 | 234.2 | 11.3 | 801 | 837.4 | 744.6 | 673 | 648.5 | 616.8 | 662.6
373 | 165 | 473.3 | 189.32 | 221.3042 | 235.2 | 250.3 | 254 | 258.6 | 477.3 | 24.4 | 21.5 | 48.4 | 3.9 | 226.1 | 11.1 | 798.8 | 857.3 | 729.7 | 675.4 | 652 | 621.2 | 660.2
374 | 166 | 473.2 | 189.28 | 221.2574 | 234.6 | 250.1 | 253.5 | 259.3 | 490.2 | 24.5 | 21.5 | 48.5 | 4.7 | 236.4 | 10.9 | 799.3 | 870.1 | 721.8 | 677.7 | 656.8 | 627.2 | 660.9
375 | 167 | 473.5 | 189.4 | 221.3977 | 233.8 | 250.1 | 253.2 | 259.1 | 492.9 | 24.5 | 21.5 | 48.7 | 7.8 | 245 | 10.4 | 801.8 | 875.1 | 722.3 | 680.3 | 659.4 | 625.7 | 663.5
376 | 168 | 472.5 | 189 | 220.9301 | 234 | 250 | 253.5 | 259.2 | 498.9 | 24.6 | 21.5 | 48.9 | 7.9 | 236.1 | 10 | 800.8 | 858.3 | 735.8 | 682.6 | 663.5 | 632.7 | 665.4
377 | 169 | 475.2 | 190.08 | 222.1926 | 234.8 | 250.3 | 254 | 259 | 492 | 24.6 | 21.5 | 49.1 | 6.1 | 255.5 | 9.5 | 800.8 | 839.3 | 735.7 | 684.3 | 659.5 | 630.8 | 664.5
378 | 170 | 476.7 | 190.68 | 222.8939 | 235 | 250.9 | 254.5 | 259.3 | 478.5 | 24.6 | 21.5 | 49.2 | 6.4 | 242.7 | 11.5 | 799.3 | 833.9 | 727 | 685.2 | 659.3 | 621.2 | 657.8
379 | 171 | 476.6 | 190.64 | 222.8472 | 235.9 | 252.1 | 254.7 | 259 | 469.5 | 24.6 | 21.5 | 49.2 | 5.8 | 252 | 14.4 | 799.7 | 837.9 | 713.7 | 686.4 | 658.4 | 612.8 | 653.8
380 | 172 | 475.2 | 190.08 | 222.1926 | 236.7 | 252.2 | 254.2 | 259 | 463.1 | 24.7 | 21.5 | 49.2 | 5.9 | 236.2 | 18.5 | 802.5 | 837.3 | 717.3 | 687.3 | 658.4 | 606.1 | 656.5
381 | 173 | 473.7 | 189.48 | 221.4912 | 237.1 | 252.3 | 254.1 | 259 | 463.9 | 24.8 | 21.5 | 49.3 | 6.4 | 235.2 | 18.7 | 800.7 | 833.4 | 723.5 | 688.2 | 658.1 | 595.2 | 656.1
382 | 174 | 474.1 | 189.64 | 221.6782 | 237.1 | 252.5 | 253.3 | 258.8 | 454.3 | 24.8 | 21.5 | 49.4 | 6.5 | 238.6 | 17.6 | 796.8 | 824.9 | 722.6 | 689 | 662.4 | 602.5 | 660.9
383 | 175 | 474.3 | 189.72 | 221.7717 | 237.1 | 252.9 | 252.6 | 258.7 | 445.6 | 24.9 | 21.5 | 49.6 | 8.6 | 235.3 | 17 | 794.8 | 817.1 | 718.8 | 689.7 | 667.1 | 601.5 | 655.7
384 | 176 | 474.4 | 189.76 | 221.8185 | 237.3 | 253 | 252.7 | 258.3 | 444.4 | 24.9 | 21.5 | 49.8 | 6.7 | 239.4 | 15.7 | 797.7 | 830.1 | 713.1 | 691 | 673.7 | 591.6 | 652.2
385 | 177 | 474 | 189.6 | 221.6315 | 237.8 | 252.9 | 252 | 258.4 | 445.2 | 25 | 21.5 | 50 | 7 | 247.7 | 17.3 | 799.7 | 837 | 701.6 | 692.4 | 675.7 | 583 | 646
386 | 178 | 473.7 | 189.48 | 221.4912 | 237.7 | 251.8 | 250.2 | 258.2 | 446 | 25 | 21.5 | 50.5 | 7 | 241.4 | 16.9 | 799.3 | 843.6 | 696.7 | 693.7 | 678.8 | 591.5 | 647.9
387 | 179 | 473.5 | 189.4 | 221.3977 | 237.8 | 250.7 | 249.1 | 257.9 | 444.4 | 25 | 21.5 | 51 | 5.9 | 245.9 | 17.8 | 804.5 | 861.5 | 709.9 | 695.6 | 683.7 | 597.5 | 651.1
388 | 180 | 473.3 | 189.32 | 221.3042 | 238.3 | 250 | 249.2 | 257.2 | 446.1 | 25.1 | 21.5 | 51.2 | 4.7 | 254.1 | 17.9 | 811.1 | 853.9 | 723.4 | 697.4 | 679.6 | 585.4 | 647.9
389 | 181 | 475.6 | 190.24 | 222.3796 | 238.9 | 249.7 | 249.4 | 257.5 | 453.9 | 25.2 | 21.5 | 51.3 | 5.2 | 276 | 15.8 | 813.9 | 836.2 | 726 | 698.1 | 674.1 | 575.1 | 642.4
390 | 182 | 474 | 189.6 | 221.6315 | 239.3 | 249.9 | 248.6 | 257.5 | 455 | 25.2 | 21.5 | 51.5 | 5.2 | 256 | 16.1 | 814.1 | 812.8 | 730.8 | 698.3 | 667.7 | 561.6 | 642.1
391 | 183 | 473.1 | 189.24 | 221.2107 | 240.2 | 250.7 | 247.9 | 256.5 | 460.5 | 25.2 | 21.5 | 51.6 | 6.6 | 252.3 | 18.5 | 814.2 | 805.4 | 735 | 698.3 | 661 | 543.7 | 638.7
392 | 184 | 473.8 | 189.52 | 221.538 | 241.5 | 250.9 | 247.2 | 256 | 461 | 25.2 | 21.5 | 51.7 | 7.3 | 252.4 | 17.9 | 815.3 | 797.3 | 744.4 | 697.5 | 656.4 | 529.6 | 636.2
393 | 185 | 474.2 | 189.68 | 221.725 | 242.4 | 251.4 | 246.3 | 255.9 | 466.1 | 25.2 | 21.5 | 51.6 | 5.3 | 240.2 | 18 | 814.7 | 794 | 751.5 | 697.1 | 651.7 | 522.7 | 638.9
394 | 186 | 472.3 | 188.92 | 220.8366 | 242.6 | 250.9 | 246.8 | 255.8 | 474.5 | 25.4 | 21.5 | 51.5 | 5.7 | 248 | 19.4 | 817.7 | 801.4 | 759.7 | 697.5 | 648 | 520.8 | 637.7
395 | 187 | 472.6 | 189.04 | 220.9769 | 242.9 | 250.2 | 247.1 | 255.8 | 480.7 | 25.5 | 21.5 | 51.4 | 7.4 | 244.3 | 17.7 | 819.5 | 807.8 | 772 | 698.8 | 644.8 | 523.7 | 646.5
396 | 188 | 472.3 | 188.92 | 220.8366 | 242.3 | 249.6 | 247.1 | 255.9 | 480.4 | 25.6 | 21.5 | 51.5 | 7.3 | 247.1 | 19.9 | 817.8 | 814.2 | 770.3 | 700.9 | 642.7 | 538.6 | 664.9
397 | 189 | 472.9 | 189.16 | 221.1171 | 242 | 248.6 | 247.6 | 256.3 | 474.6 | 25.6 | 21.5 | 51.5 | 5.9 | 249.7 | 21.5 | 811.5 | 826 | 752.8 | 703.9 | 644.2 | 547.4 | 660.9
398 | 190 | 473.1 | 189.24 | 221.2107 | 241.8 | 247.7 | 248.7 | 256.8 | 475.1 | 25.6 | 21.5 | 51.5 | 4.8 | 262.7 | 18.4 | 811.2 | 846.3 | 751.5 | 707.1 | 640.5 | 549.8 | 655.1
399 | 191 | 472.4 | 188.96 | 220.8834 | 241.1 | 247.6 | 250.3 | 257.7 | 483.7 | 25.6 | 21.5 | 51.4 | 4.7 | 256.3 | 18.8 | 813.5 | 867.1 | 737.7 | 710.5 | 641 | 550.8 | 651.8
400 | 192 | 472.5 | 189 | 220.9301 | 240.9 | 247.6 | 251.4 | 258.6 | 492.7 | 25.6 | 21.4 | 51.3 | 4.8 | 261.6 | 19.7 | 806.8 | 875.5 | 710.6 | 713.9 | 642.7 | 548.3 | 647.3
401 | 193 | 473.2 | 189.28 | 221.2574 | 241.4 | 248.2 | 252.1 | 259.4 | 486.5 | 25.7 | 21.4 | 51.4 | 5.3 | 253.9 | 17.4 | 801.9 | 871.9 | 699.9 | 716.8 | 647.3 | 546.5 | 644.3
402 | 194 | 473 | 189.2 | 221.1639 | 241.4 | 248.9 | 253.2 | 260.1 | 483.4 | 25.8 | 21.5 | 51.4 | 5.4 | 257.3 | 16.5 | 801 | 862.8 | 695.3 | 719.2 | 652.3 | 551 | 646.4
403 | 195 | 473.2 | 189.28 | 221.2574 | 241.7 | 249.1 | 253.8 | 260.5 | 482.5 | 25.8 | 21.5 | 51.5 | 6.9 | 272 | 14.5 | 801.8 | 866.5 | 680.5 | 721.6 | 656.7 | 560 | 650.2
404 | 196 | 472.9 | 189.16 | 221.1171 | 242.7 | 248.5 | 254.4 | 261.5 | 487.3 | 26 | 21.4 | 51.6 | 7.4 | 265.1 | 14.4 | 800 | 855.1 | 672.4 | 723.9 | 657.5 | 558.3 | 646.8
405 | 197 | 473.2 | 189.28 | 221.2574 | 243.5 | 247.9 | 255.4 | 262.4 | 475.5 | 26.1 | 21.4 | 51.7 | 6.8 | 253 | 14.6 | 800.3 | 842.9 | 664.9 | 724.9 | 657.2 | 550.4 | 640.6
406 | 198 | 473.4 | 189.36 | 221.3509 | 244.1 | 247.4 | 255.7 | 262 | 463.2 | 26.1 | 21.4 | 51.8 | 7.5 | 249.9 | 17.6 | 800.7 | 816.8 | 671 | 725.1 | 651.9 | 546.7 | 640
407 | 199 | 473.3 | 189.32 | 221.3042 | 244 | 246.5 | 255.7 | 261.7 | 462.8 | 26.1 | 21.4 | 51.9 | 7 | 237.1 | 17.1 | 802.2 | 826.4 | 669.4 | 725.4 | 658 | 558.9 | 644.2
408 | 200 | 472.9 | 189.16 | 221.1171 | 244 | 246 | 255.7 | 261.6 | 459 | 26.1 | 21.4 | 52 | 5.9 | 257.8 | 15.9 | 799.5 | 843.7 | 655 | 727 | 664.8 | 563 | 642.6
409 | 201 | 472.7 | 189.08 | 221.0236 | 244.7 | 246.6 | 255.4 | 262 | 459.8 | 26.1 | 21.4 | 52 | 7.1 | 252.9 | 17.1 | 801.6 | 841.5 | 664.7 | 728.9 | 666.9 | 572.7 | 643.4
410 | 202 | 472.3 | 188.92 | 220.8366 | 245.3 | 247.8 | 255.5 | 262.9 | 461 | 26.1 | 21.4 | 52.1 | 7.1 | 252 | 14.8 | 805.1 | 840.1 | 683.1 | 730.6 | 667.4 | 574.9 | 648.1
411 | 203 | 473.2 | 189.28 | 221.2574 | 244.8 | 247.5 | 255 | 262.3 | 455.7 | 26.2 | 21.4 | 52.2 | 7.6 | 252 | 14.6 | 806.2 | 834 | 684 | 731.6 | 665.1 | 571 | 643.5
412 | 204 | 471.5 | 188.6 | 220.4625 | 244.8 | 247.9 | 255.4 | 262.1 | 446.8 | 26.3 | 21.4 | 52.3 | 7.3 | 246.2 | 13.2 | 808.5 | 832.8 | 678 | 732.2 | 660.6 | 567.6 | 641.4
413 | 205 | 471.1 | 188.44 | 220.2755 | 245.5 | 248.1 | 255.5 | 261.9 | 443.4 | 26.3 | 21.4 | 52.3 | 6.3 | 240.3 | 13.8 | 810.8 | 820.4 | 675.6 | 732.4 | 656.4 | 562.8 | 639.1
414 | 206 | 470.3 | 188.12 | 219.9014 | 246.5 | 247.6 | 255.3 | 261.9 | 446.2 | 26.4 | 21.4 | 52.2 | 6.7 | 244.1 | 12.8 | 810.9 | 821.9 | 677.2 | 732.8 | 652.6 | 555.3 | 636.5
415 | 207 | 469.7 | 187.88 | 219.6209 | 247.8 | 247.2 | 255.8 | 262.2 | 446.5 | 26.4 | 21.4 | 52.2 | 6.9 | 244.5 | 15.8 | 811.2 | 814.2 | 662.5 | 732.5 | 647.7 | 545.9 | 632.2
416 | 208 | 472 | 188.8 | 220.6963 | 248.5 | 246.6 | 256.1 | 262.3 | 440.7 | 26.5 | 21.4 | 52.3 | 6.6 | 240.4 | 16.9 | 809.7 | 793.2 | 664.3 | 731.8 | 644.6 | 534.9 | 630
417 | 209 | 472.2 | 188.88 | 220.7898 | 248.7 | 246.5 | 255.7 | 261.7 | 433.5 | 26.5 | 21.4 | 52.4 | 4.8 | 238.3 | 16.2 | 814.5 | 787.4 | 679.8 | 730.4 | 640.6 | 532.7 | 630.3
418 | 210 | 472.5 | 189 | 220.9301 | 249.3 | 246.9 | 255.5 | 260.5 | 433 | 26.6 | 21.4 | 52.4 | 5.7 | 239 | 15.6 | 815 | 790.5 | 676.3 | 729.5 | 636.2 | 526.7 | 632.2
419 | 211 | 473.6 | 189.44 | 221.4444 | 249.4 | 246.6 | 255.4 | 258.7 | 428.2 | 26.7 | 21.4 | 52.5 | 5.1 | 237.7 | 14.7 | 810 | 793.8 | 656.5 | 728.8 | 632 | 516.9 | 628.3
420 | 212 | 473.1 | 189.24 | 221.2107 | 249.8 | 246.2 | 255.6 | 258.3 | 422.1 | 26.8 | 21.4 | 52.6 | 5.1 | 243.6 | 13.2 | 804.1 | 798.4 | 643.3 | 727.6 | 627.3 | 509.5 | 622.4
421 | 213 | 473.1 | 189.24 | 221.2107 | 250.1 | 247 | 256 | 258 | 412.9 | 26.9 | 21.4 | 52.6 | 4.8 | 237.9 | 12.6 | 800.7 | 790.1 | 632.2 | 725.8 | 624.1 | 497.9 | 617.5
422 | 214 | 474 | 189.6 | 221.6315 | 250.1 | 247.4 | 256.9 | 257.6 | 407.5 | 27 | 21.4 | 52.7 | 4.7 | 232.7 | 12 | 798.1 | 787.8 | 629.2 | 723.9 | 620.5 | 492.6 | 615.1
423 | 215 | 471.5 | 188.6 | 220.4625 | 250.1 | 248.1 | 257 | 257.2 | 406.1 | 27 | 21.4 | 52.7 | 3.9 | 245.4 | 13.3 | 795.4 | 786.2 | 630.7 | 722.3 | 617.9 | 485.9 | 615.4
424 | 216 | 471.3 | 188.52 | 220.369 | 249.8 | 248.7 | 256.3 | 256.6 | 404.6 | 27 | 21.4 | 52.7 | 4.6 | 241.8 | 13.8 | 790.8 | 795 | 627.4 | 720.9 | 617.1 | 479.1 | 615.5
425 | 217 | 472 | 188.8 | 220.6963 | 249.8 | 248.2 | 254.9 | 256.2 | 403 | 27.1 | 21.4 | 52.8 | 5.3 | 240.2 | 14.5 | 787.3 | 809 | 624.9 | 720.8 | 615.6 | 480.6 | 613.3
426 | 218 | 471.5 | 188.6 | 220.4625 | 249.7 | 246.8 | 253.6 | 256.3 | 399.3 | 27.1 | 21.4 | 53.1 | 5 | 238.8 | 14.5 | 790.5 | 820 | 631.8 | 721.2 | 613.7 | 480.1 | 616.9
427 | 219 | 471.5 | 188.6 | 220.4625 | 249 | 245.7 | 252.9 | 256.1 | 397.4 | 27.1 | 21.4 | 53.5 | 5.2 | 235.4 | 13.9 | 790.6 | 822.9 | 627.9 | 721.8 | 612.1 | 482.9 | 615.2
428 | 220 | 471.4 | 188.56 | 220.4158 | 248.3 | 245.6 | 252.8 | 257.1 | 395.1 | 27.1 | 21.4 | 53.9 | 5.2 | 246.3 | 13.8 | 789.3 | 803.3 | 631.8 | 722.1 | 609.5 | 480.3 | 612.8
429 | 221 | 472.2 | 188.88 | 220.7898 | 248.4 | 246.8 | 252.5 | 257.6 | 392.7 | 27.1 | 21.4 | 54.1 | 5.4 | 254.2 | 13.3 | 783.2 | 793.9 | 637.4 | 721.9 | 607.2 | 473.2 | 609.8
430 | 222 | 473.6 | 189.44 | 221.4444 | 248.5 | 247.4 | 251.7 | 256.9 | 393.1 | 27.2 | 21.4 | 54.4 | 4.4 | 241.7 | 12.9 | 783.8 | 794.5 | 634.9 | 721.8 | 605.3 | 467.1 | 607.9
431 | 223 | 472.6 | 189.04 | 220.9769 | 248.6 | 247.6 | 251.1 | 256.4 | 394.9 | 27.3 | 21.4 | 54.7 | 4.6 | 248.7 | 12.3 | 782 | 795.4 | 635.8 | 721.4 | 603.1 | 460.6 | 606.2
432 | 224 | 471.9 | 188.76 | 220.6496 | 248.7 | 248.2 | 249.8 | 256.5 | 394.9 | 27.3 | 21.4 | 55 | 5.3 | 280.3 | 9.7 | 780.9 | 791 | 626.3 | 720.5 | 600.6 | 461.5 | 605.1
433 | 225 | 473.5 | 189.4 | 221.3977 | 249 | 249 | 249 | 256.3 | 394.5 | 27.3 | 21.4 | 55.3 | 6.4 | 232.5 | 7.8 | 773.8 | 757.1 | 620.3 | 718.4 | 596.8 | 454.4 | 600.8
434 | 226 | 473.4 | 189.36 | 221.3509 | 249.8 | 248.4 | 248.4 | 257 | 390.6 | 27.4 | 21.4 | 55.6 | 6 | 238.4 | 7.2 | 772 | 750.5 | 616.7 | 715.7 | 593.7 | 446.6 | 596.8
435 | 227 | 472.6 | 189.04 | 220.9769 | 250.2 | 247.9 | 248.6 | 256.7 | 384.6 | 27.4 | 21.3 | 56 | 4.5 | 238.1 | 7.2 | 762.9 | 734.1 | 595.6 | 713.2 | 590.6 | 444.6 | 593
436 | 228 | 472.9 | 189.16 | 221.1171 | 250.3 | 247.2 | 248.2 | 255.5 | 380.4 | 27.4 | 21.4 | 56.1 | 3.7 | 236.9 | 7.1 | 757.1 | 724 | 582.7 | 710.8 | 589.6 | 448.5 | 593
437 | 229 | 473.8 | 189.52 | 221.538 | 250.5 | 247.3 | 247.1 | 254.6 | 378.8 | 27.5 | 21.3 | 56.2 | 4.4 | 249.2 | 7.7 | 758.9 | 727.7 | 600.3 | 709.2 | 588.9 | 448.4 | 588.2
438 | 230 | 473.7 | 189.48 | 221.4912 | 249.9 | 246.9 | 246.3 | 254.5 | 381.8 | 27.5 | 21.3 | 56.2 | 3.6 | 222.9 | 9.7 | 764.9 | 744.7 | 605 | 708.5 | 588.9 | 455.3 | 594
439 | 231 | 474.4 | 189.76 | 221.8185 | 249.2 | 246.2 | 246.5 | 254.2 | 384.4 | 27.6 | 21.3 | 56.3 | 4.4 | 215.5 | 10.8 | 763.9 | 757.3 | 605.1 | 708.1 | 589.3 | 461.2 | 594.9
440 | 232 | 474.2 | 189.68 | 221.725 | 248.6 | 245.2 | 247 | 253.6 | 386.9 | 27.6 | 21.3 | 56.5 | 4.6 | 232.9 | 9.5 | 763.1 | 759.4 | 607.5 | 708.4 | 587.2 | 461.8 | 592.5
441 | 233 | 473.5 | 189.4 | 221.3977 | 247.5 | 243.8 | 246.9 | 253.7 | 388.5 | 27.7 | 21.4 | 56.6 | 4.1 | 240 | 8.4 | 766.9 | 784 | 607.1 | 709 | 591.3 | 472.4 | 592.9
442 | 234 | 473.8 | 189.52 | 221.538 | 247.3 | 243.3 | 247.3 | 253.5 | 393.9 | 27.8 | 21.3 | 56.6 | 4.1 | 239.9 | 8.1 | 774 | 796.1 | 627.5 | 710.6 | 591.6 | 481.9 | 596.8
443 | 235 | 473.2 | 189.28 | 221.2574 | 247.2 | 243.2 | 247.4 | 253.5 | 398.3 | 27.9 | 21.3 | 56.7 | 5 | 245.2 | 9.2 | 780.9 | 772.6 | 637 | 711.4 | 589.7 | 486.6 | 595.3
444 | 236 | 292.3 | 116.92 | 136.6727 | 246.9 | 243.3 | 247.7 | 253.4 | 398.9 | 27.9 | 21.3 | 56.7 | 4.7 | 260.9 | 9 | 784.4 | 763.4 | 641.1 | 710.3 | 587.1 | 486.4 | 592.4
445 | 237 | -6.2 | 0 | 0 | 246.4 | 243.3 | 247.8 | 253 | 404.5 | 27.9 | 21.3 | 56.7 | 4.3 | 238.9 | 8.7 | 780.6 | 745.4 | 621.2 | 708.2 | 582.8 | 476.1 | 585.8
446 | 238 | -6.9 | 0 | 0 | 245.8 | 242.7 | 247.7 | 253.2 | 395.6 | 27.9 | 21.3 | 56.7 | 4 | 237.1 | 8.6 | 756.1 | 692.9 | 584.4 | 703.7 | 576.9 | 456.4 | 574.2
447 | 239 | -6.9 | 0 | 0 | 244.6 | 241.4 | 247.6 | 252.3 | 380 | 27.9 | 21.3 | 56.7 | 3.4 | 250.4 | 8.5 | 733.2 | 649.8 | 552.9 | 696.9 | 571.3 | 437 | 563
448 | 240 | -6.9 | 0 | 0 | 242.4 | 239.6 | 246.7 | 251 | 366.4 | 27.9 | 21.3 | 56.7 | 4.5 | 266.4 | 8.5 | 714.3 | 613.5 | 523.5 | 689.4 | 565.5 | 418.7 | 555.1
449 | 241 | -6.8 | 0 | 0 | 239.5 | 237.1 | 244.1 | 248.6 | 355.1 | 28 | 21.3 | 56.7 | 5.1 | 256.8 | 10.6 | 700.4 | 586.4 | 497.4 | 681.5 | 559.4 | 401.2 | 548.8
450 | 242 | -6.8 | 0 | 0 | 236.8 | 234.2 | 241 | 246 | 344.9 | 28 | 21.3 | 56.7 | 5 | 231.4 | 11.6 | 687.4 | 563 | 473.7 | 673.7 | 553.2 | 384.8 | 542.8
451 | 243 | -6.8 | 0 | 0 | 233.9 | 231.7 | 238.2 | 243.6 | 335.3 | 27.9 | 21.3 | 56.5 | 5 | 238.6 | 10 | 674.3 | 536 | 452.1 | 665.9 | 547.3 | 369.6 | 537.3
452 | 244 | -6.8 | 0 | 0 | 230.4 | 229.5 | 235.8 | 240.6 | 326.9 | 27.9 | 21.3 | 56.2 | 5.1 | 238.2 | 9.8 | 661.4 | 514.4 | 432.7 | 658.4 | 541.5 | 355.8 | 532.7
453 | 245 | -6.8 | 0 | 0 | 227.2 | 227.1 | 233.2 | 236.8 | 319.3 | 27.9 | 21.3 | 55.8 | 4.2 | 248.5 | 8.7 | 647.2 | 490.2 | 414.2 | 651.3 | 535.8 | 343.4 | 529
454 | 246 | -6.8 | 0 | 0 | 224.1 | 224.4 | 230.4 | 233 | 312.4 | 27.9 | 21.3 | 55.3 | 3.2 | 242.9 | 8.2 | 634.4 | 467.4 | 397.2 | 644.5 | 530 | 331.4 | 524.2
455 | 247 | -6.8 | 0 | 0 | 221.6 | 222 | 227.3 | 229.7 | 305.8 | 28 | 21.3 | 54.7 | 2.6 | 232.3 | 8.2 | 622.3 | 446.9 | 383.1 | 638 | 524.3 | 320.3 | 520.3
456 | 248 | -6.8 | 0 | 0 | 218.9 | 219.3 | 224.2 | 226.4 | 299.6 | 28 | 21.3 | 54.1 | 2.4 | 237.6 | 8.4 | 611.2 | 429 | 369 | 631.5 | 518.6 | 309.8 | 516.6
457 | 249 | -6.8 | 0 | 0 | 216 | 216 | 221.3 | 223.4 | 293.4 | 28 | 21.3 | 53.5 | 2.7 | 214 | 9.5 | 600.1 | 411 | 354.7 | 625.4 | 513.1 | 299.5 | 511.8
458 | 250 | -6.8 | 0 | 0 | 212.7 | 213.1 | 218.9 | 220.5 | 287.9 | 28 | 21.3 | 52.9 | 3.1 | 243.8 | 8.9 | 586.2 | 388.6 | 341.1 | 619.5 | 507.8 | 290 | 508
459 | 251 | -6.8 | 0 | 0 | 209.5 | 210.5 | 216.3 | 217.7 | 283.1 | 28 | 21.3 | 52.4 | 3 | 214.9 | 7.4 | 574.2 | 367.9 | 328.3 | 613.8 | 502.1 | 280.6 | 504
460 | 252 | -6.8 | 0 | 0 | 206.9 | 207.7 | 213.6 | 214.9 | 278.4 | 28 | 21.3 | 51.9 | 3.4 | 228.6 | 5.9 | 563.8 | 346.8 | 314.3 | 608.2 | 496.7 | 270.8 | 499.1
461 | 253 | -6.8 | 0 | 0 | 204.5 | 205 | 210.6 | 212.1 | 273.7 | 27.9 | 21.3 | 51.4 | 3.6 | 215 | 6.2 | 553.7 | 329.2 | 302.7 | 603 | 490.7 | 261.9 | 494.3
462 | 254 | -6.8 | 0 | 0 | 201.4 | 202.5 | 207.9 | 209.4 | 268.5 | 27.9 | 21.3 | 51 | 3.9 | 209.3 | 7.9 | 545.1 | 313.3 | 292.3 | 598.1 | 484.9 | 253.4 | 489.6
463 | 255 | -6.8 | 0 | 0 | 198.2 | 200.3 | 205.2 | 206.6 | 263.3 | 27.9 | 21.3 | 50.6 | 3.8 | 214.9 | 9 | 536.8 | 298.4 | 282.5 | 593.3 | 479.2 | 245.8 | 486.8
464 | 256 | -6.8 | 0 | 0 | 195.8 | 198 | 202.5 | 203.8 | 258.5 | 27.8 | 21.3 | 50.2 | 3.8 | 211 | 9.6 | 529.4 | 286.1 | 274.5 | 588.6 | 473.7 | 238.9 | 483.8
465 | 257 | -6.8 | 0 | 0 | 193.4 | 195.5 | 200 | 201.1 | 254.2 | 27.8 | 21.3 | 49.9 | 4.3 | 205.2 | 10.3 | 522.7 | 275.1 | 266.7 | 584.1 | 468.1 | 232.5 | 481.5
466 | 258 | -6.8 | 0 | 0 | 191.1 | 193 | 197.6 | 198.5 | 250.1 | 27.8 | 21.3 | 49.5 | 3.9 | 206.1 | 10 | 517.4 | 264.1 | 260 | 579.6 | 462.9 | 226.6 | 479.6
467 | 259 | -6.8 | 0 | 0 | 188.8 | 190.5 | 195.2 | 195.9 | 246.4 | 27.8 | 21.3 | 49.2 | 3.8 | 203.3 | 8.5 | 510.7 | 253.3 | 253.5 | 575.3 | 457.6 | 221.1 | 475.7
468 | 260 | -6.8 | 0 | 0 | 186.4 | 188.1 | 192.8 | 193.5 | 242.8 | 27.8 | 21.3 | 48.9 | 3.7 | 245.8 | 7.4 | 504.1 | 243.2 | 245.8 | 571.2 | 452.6 | 215.6 | 471.1
469 | 261 | -6.8 | 0 | 0 | 184.2 | 185.8 | 190.5 | 191.3 | 239.2 | 27.8 | 21.3 | 48.6 | 3.9 | 211.5 | 6.8 | 497.5 | 234.2 | 237.6 | 567.3 | 448 | 210.2 | 466.4
470 | 262 | -6.8 | 0 | 0 | 182.5 | 183.7 | 188.1 | 189 | 235.8 | 27.9 | 21.3 | 48.3 | 4.4 | 210.4 | 7 | 490.4 | 226.1 | 229.9 | 563.4 | 443.4 | 204.8 | 463
471 | 263 | -6.8 | 0 | 0 | 180.9 | 181.5 | 185.7 | 186.8 | 232.7 | 28 | 21.3 | 48.1 | 4.6 | 238.3 | 6.2 | 484.1 | 217.6 | 223 | 559.8 | 438.9 | 199.5 | 461.3
472 | 264 | -6.8 | 0 | 0 | 179 | 179.5 | 183.6 | 184.8 | 229.6 | 28 | 21.3 | 47.8 | 4.2 | 250.4 | 7.1 | 478.7 | 210.3 | 216.5 | 556.3 | 434.6 | 194.5 | 456.6
473 | 265 | -6.8 | 0 | 0 | 177 | 177.3 | 181.5 | 182.9 | 226.4 | 27.9 | 21.3 | 47.5 | 4.2 | 228.9 | 7.8 | 473.2 | 203.6 | 210.3 | 552.9 | 430 | 190 | 452.1
474 | 266 | -6.8 | 0 | 0 | 175.5 | 175 | 179.3 | 180.9 | 223.3 | 27.9 | 21.3 | 47.2 | 3.7 | 256.9 | 8.5 | 469.1 | 198.1 | 204.3 | 549.7 | 425.4 | 185.7 | 446.9
475 | 267 | -6.8 | 0 | 0 | 173.4 | 173.1 | 177.3 | 179 | 220.2 | 28.1 | 21.2 | 46.9 | 3.6 | 246.1 | 9.8 | 464.5 | 191.4 | 199 | 546.6 | 420.2 | 181.4 | 442.4
476 | 268 | -6.8 | 0 | 0 | 171.2 | 171.6 | 175.5 | 177 | 217.2 | 28.2 | 21.3 | 46.7 | 3.6 | 261 | 11 | 460.8 | 187.4 | 193.9 | 543.5 | 415.1 | 177.1 | 437.8
477 | 269 | -6.8 | 0 | 0 | 169.2 | 170.1 | 173.8 | 175 | 214.4 | 28.3 | 21.3 | 46.4 | 3.9 | 263.2 | 11 | 456.3 | 181.7 | 189.1 | 540.4 | 410 | 173.3 | 434.2
478 | 270 | -6.8 | 0 | 0 | 167.5 | 168.4 | 172.1 | 173.1 | 211.7 | 28.2 | 21.3 | 46.2 | 4 | 257.1 | 11.6 | 452.9 | 176 | 184.9 | 537.3 | 405.5 | 169.5 | 429.9
479 | 271 | -6.8 | 0 | 0 | 165.9 | 166.9 | 170.4 | 171.2 | 209.2 | 28.2 | 21.3 | 45.9 | 4.1 | 262.9 | 11.1 | 448.1 | 170.2 | 180.9 | 534.2 | 400.7 | 165.6 | 428.4
480 | 272 | -6.8 | 0 | 0 | 164.4 | 165.2 | 168.7 | 169.4 | 206.7 | 28.1 | 21.3 | 45.7 | 4.1 | 245.2 | 11.8 | 443.2 | 165.2 | 176.9 | 531.1 | 396.5 | 162.5 | 426.2
481 | 273 | -6.8 | 0 | 0 | 162.8 | 163.6 | 167.3 | 167.8 | 204.3 | 28.1 | 21.3 | 45.4 | 4 | 257.1 | 12.2 | 438 | 160.7 | 172.9 | 528 | 392.7 | 159.7 | 422.6
482 | 274 | -6.8 | 0 | 0 | 161.2 | 162 | 165.8 | 166 | 202 | 28.1 | 21.3 | 45.1 | 3.6 | 243.9 | 12.7 | 433.9 | 156.6 | 169.4 | 525 | 389 | 156.8 | 419.1
483 | 275 | -6.8 | 0 | 0 | 159.8 | 160.3 | 164.3 | 164.5 | 199.7 | 28.1 | 21.3 | 44.9 | 3.9 | 250 | 12.9 | 430 | 152.4 | 166 | 522.1 | 385.4 | 153.7 | 415.1
484 | 276 | -6.8 | 0 | 0 | 158.2 | 158.7 | 162.8 | 163 | 197.6 | 28.1 | 21.3 | 44.6 | 4.4 | 248.4 | 13.1 | 426.1 | 148.8 | 162.8 | 519.3 | 382.1 | 150.7 | 412.9
485 | 277 | -6.8 | 0 | 0 | 157.1 | 157.1 | 161 | 161.4 | 195.6 | 28.1 | 21.2 | 44.3 | 4.5 | 252.5 | 13.2 | 422.2 | 145.4 | 159.8 | 516.5 | 378.9 | 148.1 | 411.2
486 | 278 | -6.8 | 0 | 0 | 155.8 | 155.7 | 159.1 | 159.8 | 193.6 | 28 | 21.2 | 44.1 | 4.1 | 244.5 | 13.5 | 418.9 | 142 | 156.7 | 513.8 | 375.5 | 145.7 | 410.1
487 | 279 | -6.8 | 0 | 0 | 154.3 | 154.6 | 157.7 | 158.5 | 191.7 | 28 | 21.3 | 43.9 | 3.9 | 253.5 | 12.6 | 415.8 | 138.9 | 153.6 | 511 | 372.1 | 143.2 | 405.9
488 | 280 | -6.8 | 0 | 0 | 153 | 153.4 | 156.4 | 157.1 | 190 | 28 | 21.3 | 43.6 | 3.5 | 247.9 | 12.9 | 413.1 | 136.2 | 150.6 | 508.1 | 368.7 | 140.8 | 401.5
489 | 281 | -6.8 | 0 | 0 | 151.8 | 152.1 | 155.1 | 155.8 | 188.2 | 28.1 | 21.3 | 43.4 | 3.5 | 251.2 | 13.4 | 411 | 133.5 | 147.8 | 505.2 | 365.4 | 138.8 | 397.2
490 | 282 | -6.8 | 0 | 0 | 150.5 | 150.9 | 153.9 | 154.4 | 186.5 | 28.1 | 21.3 | 43.1 | 3.5 | 247.3 | 13.5 | 408.4 | 130.7 | 145.1 | 502.5 | 362.2 | 136.9 | 393.9
491 | 283 | -6.8 | 0 | 0 | 149.5 | 149.6 | 152.6 | 153.1 | 184.7 | 28 | 21.3 | 42.9 | 3.4 | 252 | 13.3 | 405.8 | 128.3 | 142.6 | 499.7 | 358.9 | 134.8 | 392.5
492 | 284 | -6.8 | 0 | 0 | 148.5 | 148.5 | 151.4 | 151.7 | 183.1 | 27.9 | 21.3 | 42.7 | 3.8 | 247.6 | 12.3 | 402.6 | 125.9 | 140.2 | 496.9 | 355.4 | 132.7 | 389.3
493 | 285 | -6.8 | 0 | 0 | 147.5 | 147.5 | 150.4 | 150.5 | 181.5 | 27.7 | 21.3 | 42.5 | 4.3 | 245.5 | 11.5 | 399.6 | 123.4 | 137.9 | 494.3 | 352.1 | 130.8 | 386.4
494 | 286 | -6.8 | 0 | 0 | 146.5 | 146.4 | 149.3 | 149.3 | 180 | 27.6 | 21.3 | 42.3 | 3.6 | 237.6 | 11.7 | 396.4 | 120.8 | 136.3 | 491.6 | 348.6 | 128.8 | 382.7
495 | 287 | -6.8 | 0 | 0 | 145.7 | 145.4 | 148.1 | 148.2 | 178.5 | 27.5 | 21.3 | 42.1 | 4 | 244.3 | 11.4 | 393.7 | 118.9 | 134.3 | 488.9 | 345 | 126.9 | 379.9
496 | 288 | -6.8 | 0 | 0 | 144.8 | 144.3 | 147.1 | 147.1 | 177 | 27.5 | 21.3 | 41.8 | 4.5 | 240.5 | 11.5 | 391.1 | 117.3 | 132.7 | 486.2 | 341.2 | 125.1 | 377.5
497 | 289 | -6.8 | 0 | 0 | 143.9 | 143.3 | 146.1 | 146 | 175.6 | 27.4 | 21.3 | 41.6 | 4.4 | 236.7 | 11.3 | 387.8 | 115 | 130.9 | 483.7 | 337.9 | 123.3 | 375.2
498 | 290 | -6.8 | 0 | 0 | 142.9 | 142.4 | 145.2 | 144.9 | 174.3 | 27.4 | 21.3 | 41.4 | 4.1 | 245.7 | 10.6 | 384.8 | 113.2 | 129.3 | 481.1 | 334.7 | 121.6 | 372.5
499 | 291 | -6.8 | 0 | 0 | 142.1 | 141.5 | 144.1 | 144 | 173.1 | 27.3 | 21.3 | 41.2 | 3.7 | 250.2 | 10.5 | 381 | 111.6 | 127.9 | 478.5 | 331.9 | 119.9 | 371.9
500 | 292 | -6.7 | 0 | 0 | 141.3 | 140.7 | 143 | 143 | 171.9 | 27.3 | 21.3 | 40.9 | 4.2 | 258.4 | 10.4 | 377.4 | 109.7 | 125.8 | 475.9 | 328.7 | 118.5 | 371
501 | 293 | -6.8 | 0 | 0 | 140.4 | 139.8 | 142.2 | 142.2 | 170.8 | 27.3 | 21.3 | 40.8 | 4.2 | 243.6 | 10.1 | 374.5 | 107.9 | 124 | 473.3 | 326 | 117 | 369
502 | 294 | -6.8 | 0 | 0 | 139.6 | 139 | 141.4 | 141.3 | 169.7 | 27.3 | 21.3 | 40.6 | 4 | 247.3 | 10.8 | 371.7 | 106.1 | 122.3 | 470.7 | 323.3 | 115.6 | 366.3
503 | 295 | -6.8 | 0 | 0 | 138.8 | 138.1 | 140.6 | 140.4 | 168.7 | 27.3 | 21.3 | 40.5 | 4.2 | 240.8 | 11.2 | 367.9 | 104.5 | 121 | 468.2 | 320.8 | 114.5 | 364.9
504 | 296 | -6.8 | 0 | 0 | 137.9 | 137.3 | 139.8 | 139.5 | 167.7 | 27.3 | 21.3 | 40.3 | 4.3 | 251.7 | 10.5 | 364.8 | 103.1 | 119.7 | 465.9 | 318.3 | 113.4 | 363.1
505 | 297 | -6.8 | 0 | 0 | 137.2 | 136.4 | 139 | 138.6 | 166.7 | 27.3 | 21.3 | 40.1 | 4.7 | 259.6 | 10.7 | 362.4 | 102.3 | 118.2 | 463.6 | 316.1 | 112.3 | 361.6
506 | 298 | -6.8 | 0 | 0 | 136.4 | 135.7 | 138.2 | 137.7 | 165.7 | 27.3 | 21.3 | 39.9 | 6.3 | 241.3 | 12 | 359.9 | 101.6 | 117 | 461.4 | 313.9 | 111.3 | 359.7
507 | 299 | -6.8 | 0 | 0 | 135.5 | 134.9 | 137.5 | 136.9 | 164.7 | 27.2 | 21.3 | 39.8 | 7.1 | 244.9 | 12.6 | 357.6 | 100.9 | 115.8 | 459.2 | 311.8 | 110.2 | 357.8
508 | 300 | -5.9 | 0 | 0 | 134.7 | 134.1 | 136.7 | 136.2 | 163.6 | 27.3 | 21.3 | 39.5 | 6.3 | 240.3 | 11.6 | 355.6 | 100.2 | 114.6 | 456.9 | 309.7 | 109.2 | 355.9
509 | 301 | -6.5 | 0 | 0 | 134.1 | 133.4 | 136 | 135.4 | 162.7 | 27.3 | 21.3 | 39.3 | 4.4 | 259 | 12.1 | 353 | 99.5 | 113.5 | 454.7 | 307.6 | 108.4 | 353.6
510 | 302 | -6.8 | 0 | 0 | 133.4 | 132.7 | 135.4 | 134.6 | 161.7 | 27.3 | 21.3 | 39.1 | 3.5 | 236.1 | 12.5 | 349.9 | 98.5 | 112.6 | 452.5 | 305.6 | 107.2 | 352
511 | 303 | -6.8 | 0 | 0 | 132.7 | 132.1 | 134.7 | 133.9 | 160.8 | 27.3 | 21.3 | 38.9 | 3.6 | 253.2 | 14.2 | 346.9 | 97 | 111.7 | 450.4 | 303.7 | 106.2 | 349.9
512 | 304 | -6.8 | 0 | 0 | 132 | 131.5 | 134 | 133.2 | 159.8 | 27.3 | 21.3 | 38.8 | 3.1 | 236.3 | 15.3 | 344.2 | 95.5 | 110.7 | 448.3 | 301.5 | 104.9 | 347.9
513 | 305 | -6.8 | 0 | 0 | 131.5 | 130.9 | 133.3 | 132.5 | 158.9 | 27.2 | 21.3 | 38.7 | 3.2 | 235.4 | 14.3 | 341.6 | 94.5 | 109.9 | 446 | 299.5 | 103.8 | 346.1
514 | 306 | -6.8 | 0 | 0 | 131 | 130.3 | 132.6 | 131.7 | 158.1 | 27.2 | 21.3 | 38.6 | 3.8 | 236 | 13.9 | 338.5 | 93.4 | 108.8 | 443.7 | 297.5 | 102.7 | 344.2
515 | 307 | -6.8 | 0 | 0 | 130.4 | 129.7 | 132 | 131 | 157.3 | 27.2 | 21.3 | 38.5 | 4.3 | 227.6 | 11.8 | 335.6 | 92.3 | 107.8 | 441.6 | 295.6 | 101.7 | 342.6
516 | 308 | -6.8 | 0 | 0 | 129.9 | 129.1 | 131.3 | 130.3 | 156.5 | 27.1 | 21.3 | 38.4 | 4.2 | 224.8 | 10 | 332.9 | 91.1 | 106.8 | 439.4 | 293.5 | 100.7 | 341.3
517 | 309 | -6.8 | 0 | 0 | 129.2 | 128.5 | 130.8 | 129.6 | 155.7 | 27.1 | 21.3 | 38.3 | 4 | 219.1 | 11 | 330.8 | 90.3 | 105.8 | 437.3 | 291.4 | 99.8 | 339.9
518 | 310 | -6.2 | 0 | 0 | 128.5 | 128.1 | 130.3 | 129.1 | 155 | 27.1 | 21.3 | 38.1 | 3.7 | 218.6 | 10.7 | 328.7 | 89.7 | 104.9 | 435.2 | 289.5 | 99 | 338.3
519 | 311 | -5.9 | 0 | 0 | 128 | 127.6 | 129.6 | 128.5 | 154.3 | 27.2 | 21.3 | 38 | 3.9 | 240.7 | 9.1 | 326.8 | 90.2 | 104 | 433.3 | 287.6 | 98.1 | 336.6
520 | 312 | -6.3 | 0 | 0 | 127.6 | 127 | 129.1 | 127.9 | 153.7 | 27.1 | 21.3 | 37.9 | 4.2 | 239.4 | 10.5 | 325.6 | 89.9 | 103 | 431.4 | 285.6 | 97 | 334.9
521 | 313 | -5.9 | 0 | 0 | 127.2 | 126.4 | 128.4 | 127.4 | 153 | 27.1 | 21.3 | 37.7 | 5.1 | 248.4 | 10 | 324.4 | 89.7 | 101.9 | 429.5 | 283.7 | 95.9 | 333
522 | 314 | -6.2 | 0 | 0 | 126.6 | 126 | 127.9 | 126.9 | 152.3 | 27.1 | 21.3 | 37.6 | 5.2 | 240.1 | 11.2 | 323 | 89.5 | 100.6 | 427.7 | 281.8 | 94.8 | 330.7
523 | 315 | -6.8 | 0 | 0 | 126.2 | 125.5 | 127.2 | 126.3 | 151.6 | 27.1 | 21.3 | 37.4 | 4.6 | 248.2 | 11.3 | 321.5 | 89.1 | 99.3 | 425.9 | 279.9 | 93.7 | 328.4
524 | 316 | -6.8 | 0 | 0 | 125.9 | 125 | 126.6 | 125.7 | 150.8 | 27 | 21.3 | 37.2 | 3.8 | 269.9 | 9.3 | 319.8 | 88.6 | 98.1 | 424.2 | 277.9 | 92.7 | 326.6
525 | 317 | -6.8 | 0 | 0 | 125.3 | 124.5 | 126.1 | 125.2 | 150.1 | 27 | 21.3 | 37.1 | 3.3 | 243 | 9.3 | 318.2 | 88.2 | 96.8 | 422.3 | 275.8 | 91.6 | 325.5
526 | 318 | -6.8 | 0 | 0 | 124.8 | 124.1 | 125.6 | 124.8 | 149.5 | 26.9 | 21.3 | 37.1 | 3.4 | 232.7 | 11.1 | 317.2 | 87.9 | 95.2 | 420.5 | 273.8 | 90.6 | 323.7
527 | 319 | -6.8 | 0 | 0 | 124.4 | 123.6 | 125 | 124.2 | 149 | 26.9 | 21.3 | 36.9 | 3 | 237.1 | 10.6 | 316.2 | 88 | 93.9 | 418.7 | 271.8 | 89.6 | 321.7
528 | 320 | -6.8 | 0 | 0 | 123.9 | 123.2 | 124.6 | 123.7 | 148.5 | 27 | 21.3 | 36.8 | 3.5 | 242.6 | 10.2 | 314.4 | 88.4 | 92.9 | 416.9 | 269.8 | 88.7 | 319.9
529 | 321 | -6.8 | 0 | 0 | 123.4 | 122.8 | 124.1 | 123.3 | 147.9 | 27 | 21.3 | 36.7 | 4.1 | 227.6 | 9.2 | 312.9 | 88 | 91.7 | 414.9 | 267.9 | 87.9 | 318.7
530 | 322 | -6.8 | 0 | 0 | 123 | 122.3 | 123.7 | 122.7 | 147.2 | 27.1 | 21.3 | 36.6 | 4.1 | 237.5 | 8.3 | 311.3 | 87.6 | 90.6 | 413 | 266.2 | 87.1 | 317.3
531 | 323 | -6.8 | 0 | 0 | 122.5 | 122 | 123.2 | 122.2 | 146.6 | 27.1 | 21.3 | 36.5 | 3.9 | 253.7 | 7.1 | 309.5 | 87.2 | 89.8 | 411.1 | 264.4 | 86.1 | 315.9
532 | 324 | -6.8 | 0 | 0 | 122 | 121.6 | 122.8 | 121.8 | 146 | 27.1 | 21.3 | 36.4 | 3.5 | 229 | 6.7 | 307.8 | 86.6 | 88.8 | 409.2 | 262.5 | 84.9 | 314.7
533 | 325 | -6.7 | 0 | 0 | 121.7 | 121.2 | 122.3 | 121.4 | 145.3 | 27 | 21.3 | 36.3 | 3.7 | 255.5 | 6.9 | 305.6 | 86.1 | 88 | 407.3 | 260.6 | 83.9 | 314.1
534 | 326 | -6.8 | 0 | 0 | 121.3 | 120.9 | 121.9 | 121.1 | 144.7 | 27 | 21.3 | 36.1 | 4.1 | 242.5 | 7.4 | 304 | 85.7 | 87.1 | 405.3 | 258.8 | 82.8 | 312.4
535 | 327 | -6.7 | 0 | 0 | 120.8 | 120.5 | 121.5 | 120.7 | 144.2 | 27 | 21.3 | 36 | 4.2 | 247.8 | 8.9 | 302.5 | 85.4 | 86.1 | 403.4 | 257 | 81.7 | 310.2
536 | 328 | -6.8 | 0 | 0 | 120.3 | 120.2 | 121.1 | 120.3 | 143.7 | 27 | 21.3 | 35.9 | 4 | 244.6 | 8.9 | 301 | 84.8 | 85.2 | 401.5 | 255.1 | 80.7 | 308.7
537 | 329 | -6.3 | 0 | 0 | 119.8 | 119.9 | 120.6 | 119.8 | 143.1 | 27 | 21.3 | 35.7 | 4.6 | 249.9 | 7.3 | 299.2 | 84.3 | 84.4 | 399.6 | 253.2 | 79.9 | 307.1
538 | 330 | -6.1 | 0 | 0 | 119.4 | 119.5 | 120.3 | 119.4 | 142.6 | 26.9 | 21.3 | 35.5 | 5.1 | 236 | 7.2 | 297.6 | 83.9 | 83.7 | 397.8 | 251.3 | 79.2 | 305.2
539 | 331 | -6 | 0 | 0 | 119 | 119.2 | 120 | 119 | 142 | 26.9 | 21.3 | 35.4 | 5.6 | 245.7 | 7.2 | 295.5 | 83.7 | 83 | 396 | 249.6 | 78.5 | 303.6
540 | 332 | -5.3 | 0 | 0 | 118.5 | 118.8 | 119.5 | 118.6 | 141.4 | 26.9 | 21.3 | 35.3 | 6.4 | 188.9 | 6.8 | 293.8 | 83.8 | 82.4 | 394.4 | 247.8 | 77.7 | 302.6
541 | 333 | -6.1 | 0 | 0 | 118.1 | 118.5 | 119.1 | 118.2 | 140.9 | 26.9 | 21.3 | 35.1 | 5.4 | 224 | 9.8 | 292.1 | 84.2 | 81.8 | 392.8 | 246.3 | 76.9 | 301.5
542 | 334 | -6.7 | 0 | 0 | 117.8 | 118.1 | 118.7 | 117.8 | 140.4 | 26.9 | 21.3 | 35 | 4.6 | 216.4 | 12.2 | 290.5 | 84.8 | 81.1 | 391.2 | 244.9 | 76.1 | 300.2
543 | 335 | -6.8 | 0 | 0 | 117.6 | 117.7 | 118.2 | 117.3 | 139.9 | 26.8 | 21.3 | 34.9 | 5.2 | 212.2 | 13.2 | 289.2 | 85.1 | 80.4 | 389.5 | 243.3 | 75.3 | 298.7
544 | 336 | -6.8 | 0 | 0 | 117.3 | 117.3 | 117.8 | 116.9 | 139.4 | 26.8 | 21.3 | 34.8 | 4.5 | 219.7 | 12.8 | 287.9 | 85.6 | 79.8 | 387.6 | 241.8 | 74.5 | 297.3
545 | 337 | -6.8 | 0 | 0 | 116.9 | 117 | 117.5 | 116.5 | 138.8 | 26.8 | 21.3 | 34.7 | 4.9 | 205.2 | 11.1 | 286.2 | 84.3 | 79.3 | 385.7 | 240.4 | 73.9 | 295.8
546 | 338 | -6.8 | 0 | 0 | 116.6 | 116.7 | 117.1 | 116.1 | 138.3 | 26.8 | 21.3 | 34.5 | 5.4 | 219.5 | 13.7 | 284.4 | 83.3 | 78.6 | 384 | 239.2 | 73.2 | 294.3
547 | 339 | -6.8 | 0 | 0 | 116.1 | 116.4 | 116.8 | 115.7 | 137.8 | 26.8 | 21.3 | 34.5 | 5.4 | 226.3 | 16.1 | 282.8 | 83.5 | 77.9 | 382.4 | 238 | 72.4 | 292.4
548 | 340 | -6.8 | 0 | 0 | 115.8 | 116.1 | 116.5 | 115.3 | 137.4 | 26.7 | 21.3 | 34.4 | 5.2 | 222.5 | 15.6 | 281.1 | 83.9 | 77.1 | 380.5 | 236.7 | 71.6 | 290.4
549 | 341 | -6.5 | 0 | 0 | 115.4 | 115.8 | 116.1 | 115 | 136.9 | 26.7 | 21.3 | 34.3 | 5 | 227.8 | 14 | 279.6 | 83.4 | 76.4 | 378.6 | 235.2 | 70.8 | 288.9

## First Electrical Failures
First electrical failures observed for the two cables present extracted from the corresponding IRMS and SCDU data files
3/C Cable |  |  | 7/C IRMS Cable |  |  | 7/C SCDU Cable
Time | Offset Time (s) | C2-G | Time | Offset Time (s) | C2-G | Time (s) | Offset Time (s) | C1 V1 | C1 V6
20.1667 | -187.8333 | 234438 | 114.3333 | -93.6667 | 223738 | 0 | -208 | 132.5735 | 0.28848
174.1667 | -33.8333 | 234438 | 268.3333 | 60.3333 | 28.2323 | 60 | -148 | 132.3787 | 0.19109
328.1667 | 120.1667 | 2.6352 | 422.1667 | 214.1667 | 0.68824 | 120 | -88 | 132.7683 | 0.48328
482.1667 | 274.1667 | 0.63661 | 576.3333 | 368.3333 | 2.3091 | 180 | -28 | 132.6709 | 0.38586
[6 empty] | 240 | 32 | 132.4761 | 0.28848
[6 empty] | 300 | 92 | 132.3787 | 0.38586
[6 empty] | 330 | 122 | 132.6709 | 0.48328
[6 empty] | 350 | 142 | 132.0865 | 0.38586
[6 empty] | 360 | 152 | 131.8917 | 0.28848
[6 empty] | 360.2 | 152.2 | 132.0865 | 0.28848
[6 empty] | 360.4 | 152.4 | 131.7944 | 0.38586
[6 empty] | 360.6 | 152.6 | 131.7944 | 0.28848
[6 empty] | 360.8 | 152.8 | 131.7944 | 0.38586
[6 empty] | 361 | 153 | 131.8917 | 0.38586
[6 empty] | 361.2 | 153.2 | 131.8917 | 0.77546
[6 empty] | 361.4 | 153.4 | 131.6969 | 0.38586
[6 empty] | 361.6 | 153.6 | 131.8917 | 0.38586
[6 empty] | 361.8 | 153.8 | 131.9892 | 0.38586
[6 empty] | 362 | 154 | 131.7944 | 0.48328
[6 empty] | 362.2 | 154.2 | 131.8917 | 0.38586
[6 empty] | 362.4 | 154.4 | 131.8917 | 0.38586
[6 empty] | 362.6 | 154.6 | 131.8917 | 0.38586
[6 empty] | 362.8 | 154.8 | 131.6969 | 0.38586
[6 empty] | 363 | 155 | 131.7944 | 0.28848
[6 empty] | 363.2 | 155.2 | 131.9892 | 0.38586
[6 empty] | 363.4 | 155.4 | 131.7944 | 0.38586
[6 empty] | 363.6 | 155.6 | 131.8917 | 0.38586
[6 empty] | 363.8 | 155.8 | 131.8917 | 0.67808
[6 empty] | 364 | 156 | 131.6969 | 0.19109
[6 empty] | 364.2 | 156.2 | 131.6969 | 0.38586
[6 empty] | 364.4 | 156.4 | 131.6969 | 0.28848
[6 empty] | 364.6 | 156.6 | 131.5996 | 0.19109
[6 empty] | 364.8 | 156.8 | 131.0152 | 0.48328
[6 empty] | 365 | 157 | 130.8204 | 0.58066
[6 empty] | 365.2 | 157.2 | 131.5996 | 0.97026
[6 empty] | 365.4 | 157.4 | 130.8204 | 1.2624
[6 empty] | 365.6 | 157.6 | 130.6256 | 5.6453
[6 empty] | 365.8 | 157.8 | 130.1386 | 7.5932
[6 empty] | 366 | 158 | 129.1647 | 26.5855
[6 empty] | 366.2 | 158.2 | 121.3729 | 13.924
[6 empty] | 366.4 | 158.4 | 129.4568 | 31.358
[6 empty] | 366.6 | 158.6 | 127.9959 | 52.493
[6 empty] | 366.8 | 158.8 | 127.9959 | 64.5702
[6 empty] | 367 | 159 | 128.5803 | 44.7987
[6 empty] | 367.2 | 159.2 | 127.0219 | 48.1102
[6 empty] | 367.4 | 159.4 | 126.3401 | 52.006
[6 empty] | 367.6 | 159.6 | 127.4115 | 45.3831
[6 empty] | 367.8 | 159.8 | 126.6323 | 50.6425
[6 empty] | 368 | 160 | 125.9505 | 83.7573
[6 empty] | 368.2 | 160.2 | 126.7297 | 81.712
[6 empty] | 368.4 | 160.4 | 125.4636 | 80.251
[6 empty] | 368.6 | 160.6 | 121.8599 | 96.3215
[6 empty] | 368.8 | 160.8 | 121.5677 | 99.7303
[6 empty] | 369 | 161 | 122.3469 | 107.9116
[6 empty] | 369.2 | 161.2 | 122.5417 | 107.7168
[6 empty] | 369.4 | 161.4 | 125.6584 | 114.9242
[6 empty] | 369.6 | 161.6 | 125.3662 | 116.2877
[6 empty] | 369.8 | 161.8 | 124.0026 | 116.2877
[6 empty] | 370 | 162 | 125.6584 | 120.6706
[6 empty] | 370.2 | 162.2 | 126.1453 | 121.5472
[6 empty] | 370.4 | 162.4 | 125.3662 | 119.307
[6 empty] | 370.6 | 162.6 | 124.6844 | 116.8721
[6 empty] | 370.8 | 162.8 | 123.9052 | 116.0929
[6 empty] | 371 | 163 | 123.7104 | 116.2877
[6 empty] | 371.2 | 163.2 | 124.1974 | 116.5799
[6 empty] | 371.4 | 163.4 | 118.451 | 116.6773
[6 empty] | 371.6 | 163.6 | 122.5417 | 117.2617
[6 empty] | 371.8 | 163.8 | 122.5417 | 116.3851
[6 empty] | 372 | 164 | 119.2302 | 113.5606
[6 empty] | 372.2 | 164.2 | 117.8667 | 108.8856
[6 empty] | 372.4 | 164.4 | 116.6979 | 110.2492
[6 empty] | 372.6 | 164.6 | 117.3797 | 111.0283
[6 empty] | 372.8 | 164.8 | 119.912 | 114.4372
[6 empty] | 373 | 165 | 123.7104 | 118.9175
[6 empty] | 373.2 | 165.2 | 121.8599 | 116.8721
[6 empty] | 373.4 | 165.4 | 123.9052 | 118.82
[6 empty] | 373.6 | 165.6 | 124.0026 | 120.1836
[6 empty] | 373.8 | 165.8 | 122.8339 | 119.2096
[6 empty] | 374 | 166 | 121.9573 | 116.5799
[6 empty] | 374.2 | 166.2 | 123.0287 | 119.794
[6 empty] | 374.4 | 166.4 | 122.1521 | 118.9175
[6 empty] | 374.6 | 166.6 | 118.0615 | 104.5028
[6 empty] | 374.8 | 166.8 | 119.2302 | 72.3619
[6 empty] | 375 | 167 | 121.8599 | 72.1671
[6 empty] | 375.2 | 167.2 | 119.912 | 60.8691
[6 empty] | 375.4 | 167.4 | 118.938 | 55.9993
[6 empty] | 375.6 | 167.6 | 118.8406 | 45.0909
[6 empty] | 375.8 | 167.8 | 119.425 | 45.4804
[6 empty] | 376 | 168 | 121.6651 | 69.3426
[6 empty] | 376.2 | 168.2 | 121.9573 | 67.2973
[6 empty] | 376.4 | 168.4 | 118.1588 | 64.8624
[6 empty] | 376.6 | 168.6 | 119.0354 | 58.142
[6 empty] | 376.8 | 168.8 | 117.5745 | 66.9077
[6 empty] | 377 | 169 | 117.8667 | 63.304
[6 empty] | 377.2 | 169.2 | 115.7239 | 64.765
[6 empty] | 377.4 | 169.4 | 123.7104 | 81.9067
[6 empty] | 377.6 | 169.6 | 123.5156 | 87.0688
[6 empty] | 377.8 | 169.8 | 125.2688 | 90.5751
[6 empty] | 378 | 170 | 124.3922 | 89.3089
[6 empty] | 378.2 | 170.2 | 123.6131 | 88.0427
[6 empty] | 378.4 | 170.4 | 127.8011 | 103.9184
[6 empty] | 378.6 | 170.6 | 126.6323 | 104.8923
[6 empty] | 378.8 | 170.8 | 126.8271 | 118.4305
[6 empty] | 379 | 171 | 127.8985 | 122.5211
[6 empty] | 379.2 | 171.2 | 128.4829 | 123.5925
[6 empty] | 379.4 | 171.4 | 128.6777 | 122.2289
[6 empty] | 379.6 | 171.6 | 129.6516 | 122.3263
[6 empty] | 379.8 | 171.8 | 127.7037 | 122.4237
[6 empty] | 380 | 172 | 123.3208 | 120.6706
[6 empty] | 380.2 | 172.2 | 129.262 | 121.4497
[6 empty] | 380.4 | 172.4 | 129.6516 | 118.4305
[6 empty] | 380.6 | 172.6 | 128.8725 | 118.9175
[6 empty] | 380.8 | 172.8 | 127.3141 | 113.8528
[6 empty] | 381 | 173 | 126.6323 | 112.6841
[6 empty] | 381.2 | 173.2 | 129.0672 | 121.255
[6 empty] | 381.4 | 173.4 | 129.749 | 123.3003
[6 empty] | 381.6 | 173.6 | 128.9699 | 118.5279
[6 empty] | 381.8 | 173.8 | 129.0672 | 120.768
[6 empty] | 382 | 174 | 128.7751 | 118.82
[6 empty] | 382.2 | 174.2 | 128.7751 | 119.8914
[6 empty] | 382.4 | 174.4 | 127.4115 | 97.5876
[6 empty] | 382.6 | 174.6 | 127.9959 | 117.3591
[6 empty] | 382.8 | 174.8 | 128.4829 | 120.3784
[6 empty] | 383 | 175 | 127.8985 | 115.3138
[6 empty] | 383.2 | 175.2 | 129.0672 | 108.7882
[6 empty] | 383.4 | 175.4 | 129.1647 | 104.8923
[6 empty] | 383.6 | 175.6 | 129.5542 | 102.2626
[6 empty] | 383.8 | 175.8 | 129.6516 | 99.6329
[6 empty] | 384 | 176 | 129.749 | 102.2626
[6 empty] | 384.2 | 176.2 | 127.3141 | 116.9695
[6 empty] | 384.4 | 176.4 | 111.7307 | 107.9116
[6 empty] | 384.6 | 176.6 | 127.0219 | 105.9637
[6 empty] | 384.8 | 176.8 | 130.236 | 107.522
[6 empty] | 385 | 177 | 130.0412 | 103.9184
[6 empty] | 385.2 | 177.2 | 127.8011 | 105.1846
[6 empty] | 385.4 | 177.4 | 127.8985 | 86.6792
[6 empty] | 385.6 | 177.6 | 125.1714 | 91.4516
[6 empty] | 385.8 | 177.8 | 128.5803 | 92.1334
[6 empty] | 386 | 178 | 129.0672 | 96.1267
[6 empty] | 386.2 | 178.2 | 130.0412 | 106.7429
[6 empty] | 386.4 | 178.4 | 130.723 | 102.0679
[6 empty] | 386.6 | 178.6 | 129.1647 | 89.1141
[6 empty] | 386.8 | 178.8 | 124.8792 | 61.6483
[6 empty] | 387 | 179 | 126.6323 | 56.8759
[6 empty] | 387.2 | 179.2 | 125.3662 | 55.9993
[6 empty] | 387.4 | 179.4 | 125.8532 | 62.1353
[6 empty] | 387.6 | 179.6 | 127.1193 | 82.0042
[6 empty] | 387.8 | 179.8 | 129.0672 | 97.5876
[6 empty] | 388 | 180 | 130.3334 | 109.7622
[6 empty] | 388.2 | 180.2 | 130.9178 | 114.632
[6 empty] | 388.4 | 180.4 | 130.9178 | 119.5018
[6 empty] | 388.6 | 180.6 | 124.4896 | 104.6975
[6 empty] | 388.8 | 180.8 | 130.5282 | 112.4893
[6 empty] | 389 | 181 | 131.1126 | 121.9367
[6 empty] | 389.2 | 181.2 | 129.749 | 113.0736
[6 empty] | 389.4 | 181.4 | 131.1126 | 119.8914
[6 empty] | 389.6 | 181.6 | 128.8725 | 102.1652
[6 empty] | 389.8 | 181.8 | 128.2881 | 81.0302
[6 empty] | 390 | 182 | 126.048 | 82.5885
[6 empty] | 390.2 | 182.2 | 127.8011 | 88.9193
[6 empty] | 390.4 | 182.4 | 129.6516 | 107.522
[6 empty] | 390.6 | 182.6 | 130.5282 | 115.5086
[6 empty] | 390.8 | 182.8 | 130.723 | 115.4112
[6 empty] | 391 | 183 | 129.9438 | 94.2761
[6 empty] | 391.2 | 183.2 | 130.1386 | 104.795
[6 empty] | 391.4 | 183.4 | 130.3334 | 103.1392
[6 empty] | 391.6 | 183.6 | 130.236 | 103.5288
[6 empty] | 391.8 | 183.8 | 129.0672 | 100.9965
[6 empty] | 392 | 184 | 130.236 | 113.3659
[6 empty] | 392.2 | 184.2 | 129.1647 | 106.6455
[6 empty] | 392.4 | 184.4 | 129.8464 | 115.5086
[6 empty] | 392.6 | 184.6 | 128.7751 | 112.5867
[6 empty] | 392.8 | 184.8 | 130.0412 | 121.742
[6 empty] | 393 | 185 | 128.8725 | 118.4305
[6 empty] | 393.2 | 185.2 | 127.0219 | 112.3919
[6 empty] | 393.4 | 185.4 | 127.6063 | 117.7487
[6 empty] | 393.6 | 185.6 | 127.6063 | 113.658
[6 empty] | 393.8 | 185.8 | 128.0933 | 117.4565
[6 empty] | 394 | 186 | 126.5349 | 113.8528
[6 empty] | 394.2 | 186.2 | 127.4115 | 117.3591
[6 empty] | 394.4 | 186.4 | 129.3595 | 122.5211
[6 empty] | 394.6 | 186.6 | 129.0672 | 122.8133
[6 empty] | 394.8 | 186.8 | 127.9959 | 120.768
[6 empty] | 395 | 187 | 127.5089 | 122.0341
[6 empty] | 395.2 | 187.2 | 127.1193 | 121.742
[6 empty] | 395.4 | 187.4 | 127.8011 | 120.5732
[6 empty] | 395.6 | 187.6 | 127.6063 | 122.8133
[6 empty] | 395.8 | 187.8 | 128.9699 | 122.4237
[6 empty] | 396 | 188 | 128.1907 | 121.5472
[6 empty] | 396.2 | 188.2 | 130.0412 | 120.768
[6 empty] | 396.4 | 188.4 | 131.0152 | 123.9821
[6 empty] | 396.6 | 188.6 | 131.0152 | 121.1576
[6 empty] | 396.8 | 188.8 | 130.4308 | 119.794
[6 empty] | 397 | 189 | 130.236 | 117.6513
[6 empty] | 397.2 | 189.2 | 129.8464 | 111.6127
[6 empty] | 397.4 | 189.4 | 129.3595 | 111.2231
[6 empty] | 397.6 | 189.6 | 130.4308 | 118.82
[6 empty] | 397.8 | 189.8 | 130.9178 | 121.5472
[6 empty] | 398 | 190 | 130.6256 | 119.1123
[6 empty] | 398.2 | 190.2 | 131.21 | 125.443
[6 empty] | 398.4 | 190.4 | 129.8464 | 119.5018
[6 empty] | 398.6 | 190.6 | 125.9505 | 107.6195
[6 empty] | 398.8 | 190.8 | 128.0933 | 117.6513
[6 empty] | 399 | 191 | 129.5542 | 116.0929
[6 empty] | 399.2 | 191.2 | 128.4829 | 115.8981
[6 empty] | 399.4 | 191.4 | 125.3662 | 114.4372
[6 empty] | 399.6 | 191.6 | 129.262 | 117.7487
[6 empty] | 399.8 | 191.8 | 128.9699 | 113.7554
[6 empty] | 400 | 192 | 127.6063 | 103.1392
[6 empty] | 400.2 | 192.2 | 127.1193 | 92.036
[6 empty] | 400.4 | 192.4 | 125.3662 | 90.4777
[6 empty] | 400.6 | 192.6 | 122.6391 | 88.4323
[6 empty] | 400.8 | 192.8 | 19.1066 | 13.5344
[6 empty] | 401 | 193 | 3.3283 | 2.5286
[6 empty] | 401.2 | 193.2 | 1.283 | 1.1651
[6 empty] | 401.4 | 193.4 | 0.79601 | 0.77546
[6 empty] | 401.6 | 193.6 | 0.69863 | 0.67808
[6 empty] | 401.8 | 193.8 | 0.69863 | 0.67808
[6 empty] | 402 | 194 | 0.40645 | 0.48328
[6 empty] | 405 | 197 | 0.40645 | 0.48328
[6 empty] | 410 | 202 | 0.21165 | 0.38586
[6 empty] | 413.4 | 205.4 | 0.21165 | 0.28848