## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Preliminary Test 4, 7/C Cable in Location A
Test conditions: Cable: 7-conductor, 12 AWG, PVC insulated, PVC jacketed, industrial grade control cable. (Item #1) Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 200 kW heat release rate. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: One cable temperature (see thermocouple map), air temperatures above and below the cable, and the cable tray rung temperature. Gas burner initiated: Following 191 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
191 | 0 | Ignited Gas Burner
268-276 | 77-85 | Conductors 2 & 3 both short to ground at less than 100 ohms (99 & 1) | Initial failures are by conductors shorting to ground
278 | 87 | Conductor 2 shorts to conductor 7 at less than 100 ohms (58) | Failures progress to additional shorts to ground and conductor-to-conductor shorts
282-289 | 91-98 | Conductors 4, 5, 6 & 7 all short to ground at less than 100 ohms (1, 1, 6 & 1)
284-289 | 93-98 | Conductor 3 shorts to conductors 5, 6 & 7 at less than 100 ohms (15, 1 & 45)
292-298 | 101-107 | Conductor 4 shorts to conductors 5, 6 & 7 at less than 100 ohms (16, 1 & 3)
300-303 | 109-112 | Conductor 5 shorts to conductors 6 & 7 at less than 100 ohms (1 & 27)
306 | 115 | Conductor 6 shorts to conductor 7 at less than 100 ohms (5)
404-418 | 213-227 | Conductor 1 shorts to conductors 2, 3, 4, 5, 6 & 7 at less than 100 ohms (1, 1, 7, 1, 18 & 22)
410 | 219 | Conductor 1 shorts to ground at less than 100 ohms (1) | All conductors have shorted to external ground.
421-429 | 230-238 | Conductor 2 shorts to conductors 3, 4, 5 & 6 at less than 100 ohms (3, 1, 22 & 1)
435 | 244 | Conductor 3 shorts to conductor 4 at less than 100 ohms (1) | All conductors have shorted together at less than 100 ohms
459 | 268 | Extinguished Gas Burner
Additional Observations

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable = | PVC, 7/C | (Item #1)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| A4 | = | Within cable just below cable jacket, center position
| A5 | = | Air temperature above cable
| A6 | = | Air temperature below cable

## C-C Individuals
Conductor to Conductor Resistances
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00
PVC | 7-C | Tray A
0 | 200 kW
Burner Time | C1-2 | Burner Time | C1-3 | Burner Time | C1-4 | Burner Time | C1-5 | Burner Time | C1-6 | Burner Time | C1-7 | Burner Time | C2-3 | Burner Time | C2-4 | Burner Time | C2-5 | Burner Time | C2-6 | Burner Time | C2-7 | Burner Time | C3-4 | Burner Time | C3-5 | Burner Time | C3-6 | Burner Time | C3-7 | Burner Time | C4-5 | Burner Time | C4-6 | Burner Time | C4-7 | Burner Time | C5-6 | Burner Time | C5-7 | Burner Time | C6-7 | Burner Time | Minimums
-95.5 | 240637.9994 | -92.5 | 258837.9994 | -89.5 | 254937.9994 | -87 | 248237.9994 | -84 | 257337.9994 | -81.5 | 255737.9994 | -78.5 | 264337.9994 | -75.5 | 524575.9997 | -73 | 253537.9994 | -70 | 249237.9994 | -67.5 | 242137.9994 | -64.5 | 251237.9994 | -61.5 | 255837.9994 | -59 | 253037.9994 | -56 | 247737.9994 | -53.5 | 260137.9994 | -50.5 | 263937.9994 | -47.5 | 246137.9994 | -45 | 224637.9994 | -42 | 260537.9994 | -39.5 | 241137.9994 | -95.5 | 224637.9994
58.5 | 240637.9994 | 61.5 | 258837.9994 | 64.5 | 254937.9994 | 67 | 248237.9994 | 70 | 257337.9994 | 72.5 | 255737.9994 | 75.5 | 264337.9994 | 78.5 | 262237.9994 | 81 | 63309.4976 | 84 | 12366.8878 | 86.5 | 58.4728 | 89.5 | 1184.1141 | 92.5 | 14.9924 | 95 | 0.88412 | 98 | 45.4434 | 100.5 | 15.9225 | 103.5 | 0.97772 | 106.5 | 3.167 | 109 | 0.62783 | 112 | 26.5183 | 114.5 | 5.3627 | 58.5 | 0.62783
212.5 | 0.65459 | 215.5 | 0.93421 | 218.5 | 6.5798 | 221 | 0.84214 | 224 | 18.2012 | 226.5 | 22.0887 | 229.5 | 2.5172 | 232.5 | 0.96327 | 235 | 21.747 | 237.5 | 0.95365 | 240.5 | 17.3812 | 243.5 | 0.86843 | 246 | 0.90838 | 249 | 24.02 | 251.5 | 4.9921 | 254.5 | 11.2963 | 257.5 | 0.2717 | 260.5 | 1.5257 | 263 | 5.1717 | 266 | 9.3319 | 268.5 | 0.77912 | 212.5 | 0.2717
366.5 | 0.77464 | 369.5 | 37.3322 | 372.5 | 0.9006 | 375 | 1444.7276 | 378 | 97.7677 | 380.5 | 21.0583 | 383.5 | 3.1443 | 386.5 | 2.7739 | 389 | 6.0791 | 392 | 109.2301 | 394.5 | 31.4045 | 397.5 | 31.0808 | 400.5 | 15.758 | 403 | 0.88172 | 406 | 1.4659 | 408.5 | 0.0076569 | 411.5 | 48.3052 | 414.5 | 0.028439 | 417 | 37.2605 | 420 | 14.2833 | 422.5 | 9.3747 | 366.5 | 0.0076569

## C-G Min
Average Conductor to Ground Resistances
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00
PVC | 7-C | Tray A
0 | 200 kW
Burner Time | C1-G |  | Burner Time | C2-G | Burner Time | C3-G | Burner Time | C4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | C7-G | Burner Time | Minimums Overall
-88.3333 | 240638 |  | -76.6667 | 240638 | -68.6667 | 247738 | -63.5 | 246138 | -60.3333 | 224638 | -58 | 224638 | -55.6667 | 241138 | -88.3333 | 224638
65.6667 | 240638 |  | 77.3333 | 99.3355 | 85.3333 | 0.65129 | 90.5 | 0.62424 | 93.6667 | 0.7342 | 96 | 0.66128 | 98.3333 | 0.66531 | 65.6667 | 0.62424
219.6667 | 0.63661 |  | 231.25 | 0.62831 | 239.1667 | 0.62329 | 244.5 | 0.62831 | 247.5833 | 0.63341 | 249.9167 | 0.64034 | 252.25 | 0.63243 | 219.6667 | 0.62329
373.6667 | 0.64641 |  | 385.3333 | 4.3093 | 393.3333 | 3.8233 | 398.5 | 0.035828 | 401.6667 | 0.043547 | 404 | 16.613 | 406.3333 | 0.083657 | 373.6667 | 0.035828

## C6-7
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 147.2759 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 6 & 7
Time-109 | N11 | N12 | Time-110 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
39007.4184 | 1 | 0 | 39007.4184 | 1 | 0 | -39.5 | 151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241138 | 241138 | 241137.9994
39007.4202 | 2260 | 0 | 39007.4202 | 2023 | 0 | 114.5 | 305.5 | 137.9731 | 0 | 123.5043 | 0 | 1.3797 | 0 | 1.235 | 0 | 1.3797 | 1.235 | 6.7425 | 19.2477 | 5.3627
39007.4219 | 2396 | 0 | 39007.422 | 2320 | 0 | 268.5 | 459.5 | 146.2759 | 0 | 141.6361 | 0 | 1.4628 | 0 | 1.4164 | 0 | 1.4628 | 1.4164 | 0.68364 | 3.9819 | 0.77912
39007.4237 | 1717 | 534 | 39007.4237 | 2186 | 610 | 422.5 | 613.5 | 104.823 | 32.6007 | 133.4554 | 37.2405 | 1.0482 | 0.32601 | 1.3346 | 0.37241 | 0.72222 | 0.96215 | 29.3354 | 44.9706 | 9.3747

## C5-7
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 159.1197 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 5 & 7
Time-107 | N11 | N12 | Time-108 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
39007.4183 | 1 | 0 | 39007.4184 | 1 | 0 | -42 | 149 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260538 | 260538 | 260537.9994
39007.4201 | 2040 | 0 | 39007.4202 | 2353 | 0 | 112 | 303 | 124.5421 | 0 | 143.6508 | 0 | 1.2454 | 0 | 1.4365 | 0 | 1.2454 | 1.4365 | 27.7637 | 10.7684 | 26.5183
39007.4219 | 2353 | 0 | 39007.4219 | 2590 | 0 | 266 | 457 | 143.6508 | 0 | 158.1197 | 0 | 1.4365 | 0 | 1.5812 | 0 | 1.4365 | 1.5812 | 10.7684 | 0.63243 | 9.3319
39007.4237 | 2077 | 369 | 39007.4237 | 2051 | 327 | 420 | 611 | 126.801 | 22.5275 | 125.2137 | 19.9634 | 1.268 | 0.22527 | 1.2521 | 0.19963 | 1.0427 | 1.0525 | 55.482 | 48.9486 | 14.2833

## C5-6
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 137.2027 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 5 & 6
Time-105 | N11 | N12 | Time-106 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39007.4183 | 1 | 0 | 39007.4183 | 1 | 0 | -45 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 224638 | 224638 | 224637.9994
39007.4201 | 2231 | 0 | 39007.4201 | 2118 | 0 | 109 | 300 | 136.2027 | 0 | 129.304 | 0 | 1.362 | 0 | 1.293 | 0 | 1.362 | 1.293 | 0.7342 | 6.1086 | 0.62783
39007.4219 | 2111 | 0 | 39007.4219 | 2192 | 0 | 263 | 454 | 128.8767 | 0 | 133.8217 | 0 | 1.2888 | 0 | 1.3382 | 0 | 1.2888 | 1.3382 | 6.4604 | 2.5265 | 5.1717
39007.4237 | 2081 | 476 | 39007.4237 | 2067 | 227 | 417 | 608 | 127.0452 | 29.0598 | 126.1905 | 13.8584 | 1.2705 | 0.2906 | 1.2619 | 0.13858 | 0.97985 | 1.1233 | 13.31 | 134.0997 | 37.2605

## C4-7
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 150.3284 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 4 & 7
Time-103 | N11 | N12 | Time-104 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39007.4183 | 1 | 0 | 39007.4183 | 1 | 0 | -47.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246138 | 246138 | 246137.9994
39007.4201 | 2354 | 0 | 39007.4201 | 2025 | 0 | 106.5 | 297.5 | 143.7118 | 0 | 123.6264 | 0 | 1.4371 | 0 | 1.2363 | 0 | 1.4371 | 1.2363 | 4.6041 | 21.599 | 3.167
39007.4219 | 2391 | 0 | 39007.4219 | 2446 | 0 | 260.5 | 451.5 | 145.9707 | 0 | 149.3284 | 0 | 1.4597 | 0 | 1.4933 | 0 | 1.4597 | 1.4933 | 2.9854 | 0.66966 | 1.5257
39007.4236 | 2000 | 345 | 39007.4236 | 2289 | 231 | 414.5 | 605.5 | 122.1001 | 21.0623 | 139.7436 | 14.1026 | 1.221 | 0.21062 | 1.3974 | 0.14103 | 1.0104 | 1.2564 | 0.11167 | 0.083657 | 0.028439

## C4-6
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 161.1954 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 4 & 6
Time-101 | N11 | N12 | Time-102 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39007.4183 | 1 | 0 | 39007.4183 | 1 | 0 | -50.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263938 | 263938 | 263937.9994
39007.42 | 2624 | 0 | 39007.42 | 2434 | 0 | 103.5 | 294.5 | 160.1954 | 0 | 148.5958 | 0 | 1.602 | 0 | 1.486 | 0 | 1.602 | 1.486 | 0.62424 | 8.479 | 0.97772
39007.4218 | 2606 | 0 | 39007.4218 | 2561 | 0 | 257.5 | 448.5 | 159.0965 | 0 | 156.3492 | 0 | 1.591 | 0 | 1.5635 | 0 | 1.591 | 1.5635 | 1.3193 | 3.0996 | 0.2717
39007.4236 | 1934 | 242 | 39007.4236 | 2163 | 313 | 411.5 | 602.5 | 118.0708 | 14.7741 | 132.0513 | 19.1087 | 1.1807 | 0.14774 | 1.3205 | 0.19109 | 1.033 | 1.1294 | 72.6239 | 33.6417 | 48.3052

## C4-5
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 158.8755 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 4 & 5
Time-99 | N11 | N12 | Time-100 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39007.4182 | 1 | 0 | 39007.4182 | 1 | 0 | -53.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
39007.42 | 2219 | 0 | 39007.42 | 2474 | 0 | 100.5 | 291.5 | 135.4701 | 0 | 151.0379 | 0 | 1.3547 | 0 | 1.5104 | 0 | 1.3547 | 1.5104 | 17.2772 | 5.1892 | 15.9225
39007.4218 | 2309 | 0 | 39007.4218 | 2586 | 0 | 254.5 | 445.5 | 140.9646 | 0 | 157.8755 | 0 | 1.4096 | 0 | 1.5788 | 0 | 1.4096 | 1.5788 | 12.7059 | 0.63341 | 11.2963
39007.4236 | 2220 | 464 | 39007.4236 | 2042 | 462 | 408.5 | 599.5 | 135.5311 | 28.3272 | 124.6642 | 28.2051 | 1.3553 | 0.28327 | 1.2466 | 0.28205 | 1.072 | 0.96459 | 0.035828 | 0.043547 | 0.0076569

## C3-7
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 151.3053 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 3 & 7
Time-97 | N11 | N12 | Time-98 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39007.4182 | 1 | 0 | 39007.4182 | 1 | 0 | -56 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247738 | 247738 | 247737.9994
39007.42 | 1692 | 0 | 39007.42 | 2462 | 0 | 98 | 289 | 103.2967 | 0 | 150.3053 | 0 | 1.033 | 0 | 1.5031 | 0 | 1.033 | 1.5031 | 46.4764 | 0.66531 | 45.4434
39007.4217 | 2329 | 0 | 39007.4218 | 2381 | 0 | 251.5 | 442.5 | 142.1856 | 0 | 145.3602 | 0 | 1.4219 | 0 | 1.4536 | 0 | 1.4219 | 1.4536 | 6.4139 | 4.0899 | 4.9921
39007.4235 | 2034 | 419 | 39007.4236 | 2381 | 354 | 406 | 597 | 124.1758 | 25.58 | 145.3602 | 21.6117 | 1.2418 | 0.2558 | 1.4536 | 0.21612 | 0.98596 | 1.2375 | 15.18 | 31.9261 | 1.4659

## C3-6
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 154.5409 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 3 & 6
Time-95 | N11 | N12 | Time-96 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39007.4181 | 1 | 0 | 39007.4182 | 1 | 0 | -59 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
39007.4199 | 2515 | 0 | 39007.42 | 2203 | 0 | 95 | 286 | 153.5409 | 0 | 134.4933 | 0 | 1.5354 | 0 | 1.3449 | 0 | 1.5354 | 1.3449 | 0.65129 | 14.906 | 0.88412
39007.4217 | 2021 | 0 | 39007.4217 | 2021 | 0 | 249 | 440 | 123.3822 | 0 | 123.3822 | 0 | 1.2338 | 0 | 1.2338 | 0 | 1.2338 | 1.2338 | 25.2538 | 25.2538 | 24.02
39007.4235 | 2144 | 405 | 39007.4235 | 1928 | 448 | 403 | 594 | 130.8913 | 24.7253 | 117.7045 | 27.3504 | 1.3089 | 0.24725 | 1.177 | 0.2735 | 1.0617 | 0.90354 | 11.6248 | 25.418 | 0.88172

## C3-5
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 156.2503 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 3 & 5
Time-93 | N11 | N12 | Time-94 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39007.4181 | 1 | 0 | 39007.4181 | 1 | 0 | -61.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39007.4199 | 2200 | 0 | 39007.4199 | 1771 | 0 | 92.5 | 283.5 | 134.3101 | 0 | 108.1197 | 0 | 1.3431 | 0 | 1.0812 | 0 | 1.3431 | 1.0812 | 16.3355 | 44.5161 | 14.9924
39007.4217 | 2543 | 0 | 39007.4217 | 2219 | 0 | 246 | 437 | 155.2503 | 0 | 135.4701 | 0 | 1.5525 | 0 | 1.3547 | 0 | 1.5525 | 1.3547 | 0.64412 | 15.3393 | 0.90838
39007.4235 | 1738 | 598 | 39007.4235 | 1883 | 379 | 400.5 | 591.5 | 106.105 | 36.5079 | 114.9573 | 23.138 | 1.0611 | 0.36508 | 1.1496 | 0.23138 | 0.69597 | 0.91819 | 256.3327 | 72.9656 | 15.758

## C3-4
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 153.442 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 3 & 4
Time-91 | N11 | N12 | Time-92 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39007.4181 | 1 | 0 | 39007.4181 | 1 | 0 | -64.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251238 | 251238 | 251237.9994
39007.4199 | 2220 | 4 | 39007.4199 | 2102 | 0 | 89.5 | 280.5 | 135.5311 | 0.2442 | 128.3272 | 0 | 1.3553 | 0.002442 | 1.2833 | 0 | 1.3529 | 1.2833 | 13.3624 | 19.5709 | 1184.1141
39007.4217 | 2497 | 0 | 39007.4217 | 2298 | 0 | 243.5 | 434.5 | 152.442 | 0 | 140.293 | 0 | 1.5244 | 0 | 1.4029 | 0 | 1.5244 | 1.4029 | 0.65599 | 9.3725 | 0.86843
39007.4234 | 1954 | 360 | 39007.4234 | 1809 | 376 | 397.5 | 588.5 | 119.2918 | 21.978 | 110.4396 | 22.9548 | 1.1929 | 0.21978 | 1.1044 | 0.22955 | 0.97314 | 0.87485 | 42.6191 | 127.8908 | 31.0808

## C2-7
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 147.8864 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 2 & 7
Time-89 | N11 | N12 | Time-90 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
39007.4181 | 1 | 0 | 39007.4181 | 1 | 0 | -67.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 242138 | 242138 | 242137.9994
39007.4198 | 897 | 531 | 39007.4198 | 1893 | 416 | 86.5 | 277.5 | 54.7619 | 32.4176 | 115.5678 | 25.3968 | 0.54762 | 0.32418 | 1.1557 | 0.25397 | 0.22344 | 0.90171 | 99.3355 | 45.4007 | 58.4728
39007.4216 | 2042 | 0 | 39007.4216 | 2406 | 0 | 240.5 | 431.5 | 124.6642 | 0 | 146.8864 | 0 | 1.2466 | 0 | 1.4689 | 0 | 1.2466 | 1.4689 | 18.6278 | 0.6808 | 17.3812
39007.4234 | 1969 | 233 | 39007.4234 | 1889 | 215 | 394.5 | 585.5 | 120.2076 | 14.2247 | 115.3236 | 13.1258 | 1.2021 | 0.14225 | 1.1532 | 0.13126 | 1.0598 | 1.022 | 35.7766 | 49.707 | 31.4045

## C2-6
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 152.221 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 2 & 6
Time-87 | N11 | N12 | Time-88 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39007.418 | 1 | 0 | 39007.418 | 1 | 0 | -70 | 121 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39007.4198 | 20 | 0 | 39007.4198 | 2477 | 0 | 84 | 275 | 1.221 | 0 | 151.221 | 0 | 0.01221 | 0 | 1.5122 | 0 | 0.01221 | 1.5122 | 12366.9 | 0.66128 | 12366.8878
39007.4216 | 2434 | 0 | 39007.4216 | 2085 | 0 | 237.5 | 428.5 | 148.5958 | 0 | 127.2894 | 0 | 1.486 | 0 | 1.2729 | 0 | 1.486 | 1.2729 | 2.4396 | 19.5866 | 0.95365
39007.4234 | 1826 | 77 | 39007.4234 | 2139 | 2 | 392 | 583 | 111.4774 | 4.7009 | 130.5861 | 0.1221 | 1.1148 | 0.047009 | 1.3059 | 0.001221 | 1.0678 | 1.3046 | 51.9157 | 16.613 | 109.2301

## C2-5
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 154.8462 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 2 & 5
Time-85 | N11 | N12 | Time-86 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39007.418 | 1 | 0 | 39007.418 | 1 | 0 | -73 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253538 | 253538 | 253537.9994
39007.4198 | 4 | 0 | 39007.4198 | 1 | 0 | 81 | 272 | 0.2442 | 0 | 0.06105 | 0 | 0.002442 | 0 | 0.0006105 | 0 | 0.002442 | 0.0006105 | 63309.5 | 253538 | 63309.4976
39007.4216 | 2062 | 0 | 39007.4216 | 2520 | 0 | 235 | 426 | 125.8852 | 0 | 153.8462 | 0 | 1.2589 | 0 | 1.5385 | 0 | 1.2589 | 1.5385 | 23.0058 | 0.65 | 21.747
39007.4233 | 2359 | 0 | 39007.4234 | 2338 | 117 | 389 | 580 | 144.0171 | 0 | 142.735 | 7.1429 | 1.4402 | 0 | 1.4274 | 0.071429 | 1.4402 | 1.3559 | 7.5193 | 14.1999 | 6.0791

## C2-4
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 160.1575 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 2 & 4
Time-83 | N11 | N12 | Time-84 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39007.418 | 0 | 0 | 39007.418 | 1 | 0 | -75.5 | 115.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 524576 | 262238 | 524575.9997
39007.4197 | 1 | 0 | 39007.4198 | 1 | 0 | 78.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39007.4215 | 2607 | 0 | 39007.4215 | 2607 | 0 | 232.5 | 423.5 | 159.1575 | 0 | 159.1575 | 0 | 1.5916 | 0 | 1.5916 | 0 | 1.5916 | 1.5916 | 0.62831 | 0.62831 | 0.96327
39007.4233 | 2515 | 0 | 39007.4233 | 2386 | 20 | 386.5 | 577.5 | 153.5409 | 0 | 145.6654 | 1.221 | 1.5354 | 0 | 1.4567 | 0.01221 | 1.5354 | 1.4444 | 4.3093 | 10.8783 | 2.7739

## C2-3
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 161.4396 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 2 & 3
Time-81 | N11 | N12 | Time-82 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39007.4179 | 1 | 0 | 39007.4179 | 1 | 0 | -78.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264338 | 264338 | 264337.9994
39007.4197 | 1 | 0 | 39007.4197 | 1 | 0 | 75.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264338 | 264338 | 264337.9994
39007.4215 | 2541 | 0 | 39007.4215 | 2628 | 0 | 229.5 | 420.5 | 155.1282 | 0 | 160.4396 | 0 | 1.5513 | 0 | 1.6044 | 0 | 1.5513 | 1.6044 | 4.0685 | 0.62329 | 2.5172
39007.4233 | 2526 | 0 | 39007.4233 | 2547 | 0 | 383.5 | 574.5 | 154.2125 | 0 | 155.4945 | 0 | 1.5421 | 0 | 1.5549 | 0 | 1.5421 | 1.5549 | 4.6865 | 3.8233 | 3.1443

## C1-7
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 156.1893 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 1 & 7
Time-79 | N11 | N12 | Time-80 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
39007.4179 | 1 | 0 | 39007.4179 | 1 | 0 | -81.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255738 | 255738 | 255737.9994
39007.4197 | 1 | 0 | 39007.4197 | 2210 | 0 | 72.5 | 263.5 | 0.06105 | 0 | 134.9206 | 0 | 0.0006105 | 0 | 1.3492 | 0 | 0.0006105 | 1.3492 | 255738 | 15.7638 | 255737.9994
39007.4215 | 2074 | 0 | 39007.4215 | 2542 | 0 | 226.5 | 417.5 | 126.6178 | 0 | 155.1893 | 0 | 1.2662 | 0 | 1.5519 | 0 | 1.2662 | 1.5519 | 23.3549 | 0.64437 | 22.0887
39007.4232 | 2502 | 9 | 39007.4233 | 2322 | 163 | 380.5 | 571.5 | 152.7473 | 0.54945 | 141.7582 | 9.9512 | 1.5275 | 0.0054945 | 1.4176 | 0.099512 | 1.522 | 1.3181 | 2.0812 | 4.1668 | 21.0583

## C1-6
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 157.1661 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 1 & 6
Time-77 | N11 | N12 | Time-78 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39007.4179 | 1 | 0 | 39007.4179 | 1 | 0 | -84 | 107 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257338 | 257338 | 257337.9994
39007.4196 | 1 | 0 | 39007.4197 | 2057 | 0 | 70 | 261 | 0.06105 | 0 | 125.58 | 0 | 0.0006105 | 0 | 1.2558 | 0 | 0.0006105 | 1.2558 | 257338 | 25.1522 | 257337.9994
39007.4214 | 2154 | 0 | 39007.4214 | 2558 | 0 | 224 | 415 | 131.5018 | 0 | 156.1661 | 0 | 1.315 | 0 | 1.5617 | 0 | 1.315 | 1.5617 | 19.5162 | 0.64034 | 18.2012
39007.4232 | 1872 | 151 | 39007.4232 | 1892 | 9 | 378 | 569 | 114.2857 | 9.2186 | 115.5067 | 0.54945 | 1.1429 | 0.092186 | 1.1551 | 0.0054945 | 1.0507 | 1.1496 | 53.6975 | 36.5644 | 97.7677

## C1-5
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 151.6105 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 1 & 5
Time-75 | N11 | N12 | Time-76 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39007.4178 | 1 | 0 | 39007.4178 | 1 | 0 | -87 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
39007.4196 | 1 | 0 | 39007.4196 | 1 | 0 | 67 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248238 | 248238 | 248237.9994
39007.4214 | 2467 | 0 | 39007.4214 | 2108 | 0 | 221 | 412 | 150.6105 | 0 | 128.6935 | 0 | 1.5061 | 0 | 1.2869 | 0 | 1.5061 | 1.2869 | 0.66396 | 17.8074 | 0.84214
39007.4232 | 2085 | 10 | 39007.4232 | 1961 | 175 | 375 | 566 | 127.2894 | 0.6105 | 119.7192 | 10.6838 | 1.2729 | 0.006105 | 1.1972 | 0.10684 | 1.2668 | 1.0904 | 19.3565 | 59.2327 | 1444.7276

## C1-4
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 155.7009 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 1 & 4
Time-73 | N11 | N12 | Time-74 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39007.4178 | 1 | 0 | 39007.4178 | 1 | 0 | -89.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
39007.4196 | 1 | 0 | 39007.4196 | 1 | 0 | 64.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
39007.4214 | 2361 | 0 | 39007.4214 | 2469 | 0 | 218.5 | 409.5 | 144.1392 | 0 | 150.7326 | 0 | 1.4414 | 0 | 1.5073 | 0 | 1.4414 | 1.5073 | 8.0212 | 3.2961 | 6.5798
39007.4231 | 2534 | 0 | 39007.4232 | 2398 | 5 | 372.5 | 563.5 | 154.7009 | 0 | 146.398 | 0.30525 | 1.547 | 0 | 1.464 | 0.0030525 | 1.547 | 1.4609 | 0.64641 | 6.5767 | 0.9006

## C1-3
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 158.0818 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 1 & 3
Time-71 | N11 | N12 | Time-72 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39007.4178 | 1 | 0 | 39007.4178 | 1 | 0 | -92.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39007.4195 | 1 | 0 | 39007.4196 | 1 | 0 | 61.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39007.4213 | 2573 | 0 | 39007.4213 | 2107 | 0 | 215.5 | 406.5 | 157.0818 | 0 | 128.6325 | 0 | 1.5708 | 0 | 1.2863 | 0 | 1.5708 | 1.2863 | 0.63661 | 22.8942 | 0.93421
39007.4231 | 2382 | 32 | 39007.4231 | 2413 | 0 | 369.5 | 560.5 | 145.4212 | 1.9536 | 147.3138 | 0 | 1.4542 | 0.019536 | 1.4731 | 0 | 1.4347 | 1.4731 | 10.845 | 7.3096 | 37.3322

## C1-2
OB Prelim Test 4 |  |  | 2006-10-17 | 10:00 |  | Vs = |  | 146.9707 |  | R = | 100
PVC | 7-C | Tray A
0 | 200 kW |  | Cable | 1 & 2
Time-69 | N11 | N12 | Time-70 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39007.4177 | 1 | 0 | 39007.4177 | 1 | 0 | -95.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
39007.4195 | 1 | 0 | 39007.4195 | 1 | 0 | 58.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 240638 | 240638 | 240637.9994
39007.4213 | 2358 | 0 | 39007.4213 | 2255 | 0 | 212.5 | 403.5 | 143.956 | 0 | 137.6679 | 0 | 1.4396 | 0 | 1.3767 | 0 | 1.4396 | 1.3767 | 2.0941 | 6.7574 | 0.65459
39007.4231 | 2391 | 0 | 39007.4231 | 2221 | 0 | 366.5 | 557.5 | 145.9707 | 0 | 135.5922 | 0 | 1.4597 | 0 | 1.3559 | 0 | 1.4597 | 1.3559 | 0.68507 | 8.3917 | 0.77464

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | OB Prelim Test 4 |  |  | 2006-10-17 | 10:00
39007.4166 | 1 | 0 | 1 | PVC | 7-C | Tray A | IRMS | 1
39007.4184 | 1 | 0 | 1 |  | 200 kW |  | Cable
39007.4202 | 2146 | 0 | 1
39007.422 | 2091 | 0 | 1
1
39007.4166 | 1 | 0 | 2
39007.4184 | 1 | 0 | 2
39007.4202 | 2 | 0 | 2
39007.422 | 2217 | 0 | 2
2
39007.4167 | 1 | 0 | 3
39007.4184 | 1 | 0 | 3
39007.4202 | 2575 | 0 | 3
39007.422 | 2634 | 0 | 3
3
39007.4167 | 1 | 0 | 4
39007.4185 | 1 | 0 | 4
39007.4202 | 2015 | 0 | 4
39007.422 | 2629 | 0 | 4
4
39007.4167 | 0 | 0 | 5
39007.4185 | 1 | 0 | 5
39007.4203 | 2550 | 0 | 5
39007.422 | 2523 | 0 | 5
5
39007.4167 | 1 | 0 | 6
39007.4185 | 1 | 0 | 6
39007.4203 | 2051 | 0 | 6
39007.4221 | 2171 | 0 | 6
6
39007.4167 | 1 | 0 | 7
39007.4185 | 1 | 0 | 7
39007.4203 | 2137 | 0 | 7
39007.4221 | 2426 | 0 | 7
7
39007.4167 | 1 | 0 | 8
39007.4185 | 1 | 0 | 8
39007.4203 | 2067 | 0 | 8
39007.4221 | 2609 | 0 | 8
8
39007.4168 | 1 | 0 | 9
39007.4185 | 1 | 0 | 9
39007.4203 | 2024 | 0 | 9
39007.4221 | 2145 | 0 | 9
9
39007.4168 | 1 | 0 | 10
39007.4186 | 1 | 0 | 10
39007.4203 | 2260 | 0 | 10
39007.4221 | 2441 | 0 | 10
10
39007.4168 | 1 | 0 | 11
39007.4186 | 1 | 0 | 11
39007.4204 | 2474 | 0 | 11
39007.4221 | 2432 | 0 | 11
11
39007.4168 | 1 | 0 | 12
39007.4186 | 1 | 0 | 12
39007.4204 | 2185 | 0 | 12
39007.4222 | 2477 | 0 | 12
12
39007.4168 | 1 | 0 | 13
39007.4186 | 1 | 0 | 13
39007.4204 | 2602 | 0 | 13
39007.4222 | 2272 | 0 | 13
13
39007.4168 | 1 | 0 | 14
39007.4186 | 1 | 0 | 14
39007.4204 | 2364 | 0 | 14
39007.4222 | 2472 | 0 | 14
14
39007.4169 | 1 | 0 | 15
39007.4186 | 1 | 0 | 15
39007.4204 | 2576 | 0 | 15
39007.4222 | 2518 | 0 | 15
15
39007.4169 | 1 | 0 | 16
39007.4187 | 1 | 0 | 16
39007.4204 | 2544 | 0 | 16
39007.4222 | 2532 | 0 | 16
16
39007.4169 | 1 | 0 | 17
39007.4187 | 1 | 0 | 17
39007.4205 | 2448 | 0 | 17
39007.4222 | 2308 | 0 | 17
17
39007.4169 | 1 | 0 | 18
39007.4187 | 1 | 0 | 18
39007.4205 | 2348 | 0 | 18
39007.4223 | 2247 | 0 | 18
18
39007.4169 | 1 | 0 | 19
39007.4187 | 1 | 0 | 19
39007.4205 | 2611 | 0 | 19
39007.4223 | 2270 | 0 | 19
19
39007.4169 | 1 | 0 | 20
39007.4187 | 0 | 0 | 20
39007.4205 | 2089 | 0 | 20
39007.4223 | 2305 | 0 | 20
20
39007.417 | 1 | 0 | 21
39007.4187 | 1 | 0 | 21
39007.4205 | 2514 | 0 | 21
39007.4223 | 2251 | 0 | 21
21
39007.417 | 1 | 0 | 22
39007.4187 | 1 | 0 | 22
39007.4205 | 2434 | 0 | 22
39007.4223 | 2504 | 0 | 22
22
39007.417 | 1 | 0 | 23
39007.4188 | 1 | 0 | 23
39007.4206 | 2250 | 0 | 23
39007.4223 | 2254 | 0 | 23
23
39007.417 | 0 | 0 | 24
39007.4188 | 1 | 0 | 24
39007.4206 | 12 | 0 | 24
39007.4223 | 2074 | 0 | 24
24
39007.417 | 0 | 0 | 25
39007.4188 | 1 | 0 | 25
39007.4206 | 33 | 0 | 25
39007.4224 | 2621 | 0 | 25
25
39007.417 | 1 | 0 | 26
39007.4188 | 1 | 0 | 26
39007.4206 | 2599 | 0 | 26
39007.4224 | 2572 | 0 | 26
26
39007.417 | 1 | 0 | 27
39007.4188 | 1 | 0 | 27
39007.4206 | 1820 | 0 | 27
39007.4224 | 2144 | 0 | 27
27
39007.4171 | 1 | 0 | 28
39007.4189 | 1 | 0 | 28
39007.4206 | 2555 | 0 | 28
39007.4224 | 2151 | 0 | 28
28
39007.4171 | 0 | 0 | 29
39007.4189 | 1 | 0 | 29
39007.4206 | 1841 | 0 | 29
39007.4224 | 2112 | 0 | 29
29
39007.4171 | 1 | 0 | 30
39007.4189 | 1 | 0 | 30
39007.4207 | 2131 | 0 | 30
39007.4224 | 2312 | 0 | 30
30
39007.4171 | 1 | 0 | 31
39007.4189 | 1 | 0 | 31
39007.4207 | 2153 | 0 | 31
39007.4225 | 2422 | 0 | 31
31
39007.4171 | 1 | 0 | 32
39007.4189 | 1 | 0 | 32
39007.4207 | 2623 | 0 | 32
39007.4225 | 2525 | 0 | 32
32
39007.4172 | 1 | 0 | 33
39007.4189 | 0 | 0 | 33
39007.4207 | 2072 | 0 | 33
39007.4225 | 2271 | 0 | 33
33
39007.4172 | 1 | 0 | 34
39007.4189 | 1 | 0 | 34
39007.4207 | 2435 | 0 | 34
39007.4225 | 2570 | 0 | 34
34
39007.4172 | 1 | 0 | 35
39007.419 | 1 | 0 | 35
39007.4207 | 2006 | 0 | 35
39007.4225 | 2612 | 0 | 35
35
39007.4172 | 1 | 0 | 36
39007.419 | 1 | 0 | 36
39007.4208 | 2257 | 0 | 36
39007.4225 | 2515 | 0 | 36
36
39007.4172 | 0 | 0 | 37
39007.419 | 1 | 0 | 37
39007.4208 | 2531 | 0 | 37
39007.4226 | 2073 | 0 | 37
37
39007.4172 | 1 | 0 | 38
39007.419 | 1 | 0 | 38
39007.4208 | 2394 | 0 | 38
39007.4226 | 2500 | 0 | 38
38
39007.4172 | 1 | 0 | 39
39007.419 | 0 | 0 | 39
39007.4208 | 2253 | 0 | 39
39007.4226 | 2115 | 0 | 39
39
39007.4173 | 1 | 0 | 40
39007.419 | 1 | 0 | 40
39007.4208 | 2457 | 0 | 40
39007.4226 | 2029 | 0 | 40
40
39007.4173 | 1 | 0 | 41
39007.4191 | 1 | 0 | 41
39007.4208 | 2162 | 0 | 41
39007.4226 | 2005 | 0 | 41
41
39007.4173 | 1 | 0 | 42
39007.4191 | 1 | 0 | 42
39007.4209 | 2546 | 0 | 42
39007.4226 | 2223 | 0 | 42
42
39007.4173 | 1 | 0 | 43
39007.4191 | 1 | 0 | 43
39007.4209 | 2583 | 0 | 43
39007.4227 | 2605 | 0 | 43
43
39007.4173 | 1 | 0 | 44
39007.4191 | 1 | 0 | 44
39007.4209 | 2612 | 0 | 44
39007.4227 | 2512 | 0 | 44
44
39007.4173 | 1 | 0 | 45
39007.4191 | 1 | 0 | 45
39007.4209 | 2359 | 0 | 45
39007.4227 | 2269 | 0 | 45
45
39007.4174 | 1 | 0 | 46
39007.4191 | 1 | 0 | 46
39007.4209 | 2251 | 0 | 46
39007.4227 | 2451 | 0 | 46
46
39007.4174 | 1 | 0 | 47
39007.4192 | 1 | 0 | 47
39007.4209 | 2120 | 0 | 47
39007.4227 | 2368 | 0 | 47
47
39007.4174 | 1 | 0 | 48
39007.4192 | 1 | 0 | 48
39007.421 | 2283 | 0 | 48
39007.4227 | 2210 | 0 | 48
48
39007.4174 | 1 | 0 | 49
39007.4192 | 1 | 0 | 49
39007.421 | 2126 | 0 | 49
39007.4228 | 2026 | 0 | 49
49
39007.4174 | 1 | 0 | 50
39007.4192 | 1 | 0 | 50
39007.421 | 2360 | 0 | 50
39007.4228 | 2510 | 0 | 50
50
39007.4174 | 1 | 0 | 51
39007.4192 | 1 | 0 | 51
39007.421 | 2564 | 0 | 51
39007.4228 | 2589 | 0 | 51
51
39007.4175 | 1 | 0 | 52
39007.4192 | 1 | 0 | 52
39007.421 | 2423 | 0 | 52
39007.4228 | 2301 | 0 | 52
52
39007.4175 | 1 | 0 | 53
39007.4193 | 1 | 0 | 53
39007.421 | 2571 | 0 | 53
39007.4228 | 2006 | 0 | 53
53
39007.4175 | 1 | 0 | 54
39007.4193 | 1 | 0 | 54
39007.4211 | 2083 | 0 | 54
39007.4228 | 2277 | 0 | 54
54
39007.4175 | 1 | 0 | 55
39007.4193 | 1 | 0 | 55
39007.4211 | 2527 | 0 | 55
39007.4228 | 2477 | 0 | 55
55
39007.4175 | 1 | 0 | 56
39007.4193 | 1 | 0 | 56
39007.4211 | 2512 | 0 | 56
39007.4229 | 2234 | 0 | 56
56
39007.4175 | 1 | 0 | 57
39007.4193 | 1 | 0 | 57
39007.4211 | 2387 | 0 | 57
39007.4229 | 2141 | 0 | 57
57
39007.4176 | 1 | 0 | 58
39007.4193 | 1 | 0 | 58
39007.4211 | 2496 | 0 | 58
39007.4229 | 2376 | 0 | 58
58
39007.4176 | 1 | 0 | 59
39007.4194 | 1 | 0 | 59
39007.4211 | 2600 | 0 | 59
39007.4229 | 2587 | 0 | 59
59
39007.4176 | 1 | 0 | 60
39007.4194 | 1 | 0 | 60
39007.4211 | 2627 | 0 | 60
39007.4229 | 1989 | 0 | 60
60
39007.4176 | 1 | 0 | 61
39007.4194 | 1 | 0 | 61
39007.4212 | 2135 | 0 | 61
39007.423 | 2145 | 0 | 61
61
39007.4176 | 0 | 0 | 62
39007.4194 | 1 | 0 | 62
39007.4212 | 2626 | 0 | 62
39007.423 | 1986 | 0 | 62
62
39007.4176 | 1 | 0 | 63
39007.4194 | 1 | 0 | 63
39007.4212 | 2203 | 0 | 63
39007.423 | 2305 | 0 | 63
63
39007.4177 | 1 | 0 | 64
39007.4194 | 1 | 0 | 64
39007.4212 | 2276 | 0 | 64
39007.423 | 2082 | 0 | 64
64
39007.4177 | 1 | 0 | 65
39007.4194 | 1 | 0 | 65
39007.4212 | 2366 | 0 | 65
39007.423 | 1995 | 0 | 65
65
39007.4177 | 1 | 0 | 66
39007.4195 | 1917 | 0 | 66
39007.4212 | 2164 | 0 | 66
39007.423 | 1981 | 0 | 66
66
39007.4177 | 1 | 0 | 67
39007.4195 | 1 | 0 | 67
39007.4213 | 2013 | 0 | 67
39007.423 | 2328 | 0 | 67
67
39007.4177 | 1 | 0 | 68
39007.4195 | 3 | 0 | 68
39007.4213 | 2320 | 0 | 68
39007.4231 | 2363 | 0 | 68
68
39007.4177 | 1 | 0 | 69
39007.4195 | 1 | 0 | 69
39007.4213 | 2358 | 0 | 69
39007.4231 | 2391 | 0 | 69
69
39007.4177 | 1 | 0 | 70
39007.4195 | 1 | 0 | 70
39007.4213 | 2255 | 0 | 70
39007.4231 | 2221 | 0 | 70
70
39007.4178 | 1 | 0 | 71
39007.4195 | 1 | 0 | 71
39007.4213 | 2573 | 0 | 71
39007.4231 | 2382 | 32 | 71
71
39007.4178 | 1 | 0 | 72
39007.4196 | 1 | 0 | 72
39007.4213 | 2107 | 0 | 72
39007.4231 | 2413 | 0 | 72
72
39007.4178 | 1 | 0 | 73
39007.4196 | 1 | 0 | 73
39007.4214 | 2361 | 0 | 73
39007.4231 | 2534 | 0 | 73
73
39007.4178 | 1 | 0 | 74
39007.4196 | 1 | 0 | 74
39007.4214 | 2469 | 0 | 74
39007.4232 | 2398 | 5 | 74
74
39007.4178 | 1 | 0 | 75
39007.4196 | 1 | 0 | 75
39007.4214 | 2467 | 0 | 75
39007.4232 | 2085 | 10 | 75
75
39007.4178 | 1 | 0 | 76
39007.4196 | 1 | 0 | 76
39007.4214 | 2108 | 0 | 76
39007.4232 | 1961 | 175 | 76
76
39007.4179 | 1 | 0 | 77
39007.4196 | 1 | 0 | 77
39007.4214 | 2154 | 0 | 77
39007.4232 | 1872 | 151 | 77
77
39007.4179 | 1 | 0 | 78
39007.4197 | 2057 | 0 | 78
39007.4214 | 2558 | 0 | 78
39007.4232 | 1892 | 9 | 78
78
39007.4179 | 1 | 0 | 79
39007.4197 | 1 | 0 | 79
39007.4215 | 2074 | 0 | 79
39007.4232 | 2502 | 9 | 79
79
39007.4179 | 1 | 0 | 80
39007.4197 | 2210 | 0 | 80
39007.4215 | 2542 | 0 | 80
39007.4233 | 2322 | 163 | 80
80
39007.4179 | 1 | 0 | 81
39007.4197 | 1 | 0 | 81
39007.4215 | 2541 | 0 | 81
39007.4233 | 2526 | 0 | 81
81
39007.4179 | 1 | 0 | 82
39007.4197 | 1 | 0 | 82
39007.4215 | 2628 | 0 | 82
39007.4233 | 2547 | 0 | 82
82
39007.418 | 0 | 0 | 83
39007.4197 | 1 | 0 | 83
39007.4215 | 2607 | 0 | 83
39007.4233 | 2515 | 0 | 83
83
39007.418 | 1 | 0 | 84
39007.4198 | 1 | 0 | 84
39007.4215 | 2607 | 0 | 84
39007.4233 | 2386 | 20 | 84
84
39007.418 | 1 | 0 | 85
39007.4198 | 4 | 0 | 85
39007.4216 | 2062 | 0 | 85
39007.4233 | 2359 | 0 | 85
85
39007.418 | 1 | 0 | 86
39007.4198 | 1 | 0 | 86
39007.4216 | 2520 | 0 | 86
39007.4234 | 2338 | 117 | 86
86
39007.418 | 1 | 0 | 87
39007.4198 | 20 | 0 | 87
39007.4216 | 2434 | 0 | 87
39007.4234 | 1826 | 77 | 87
87
39007.418 | 1 | 0 | 88
39007.4198 | 2477 | 0 | 88
39007.4216 | 2085 | 0 | 88
39007.4234 | 2139 | 2 | 88
88
39007.4181 | 1 | 0 | 89
39007.4198 | 897 | 531 | 89
39007.4216 | 2042 | 0 | 89
39007.4234 | 1969 | 233 | 89
89
39007.4181 | 1 | 0 | 90
39007.4198 | 1893 | 416 | 90
39007.4216 | 2406 | 0 | 90
39007.4234 | 1889 | 215 | 90
90
39007.4181 | 1 | 0 | 91
39007.4199 | 2220 | 4 | 91
39007.4217 | 2497 | 0 | 91
39007.4234 | 1954 | 360 | 91
91
39007.4181 | 1 | 0 | 92
39007.4199 | 2102 | 0 | 92
39007.4217 | 2298 | 0 | 92
39007.4234 | 1809 | 376 | 92
92
39007.4181 | 1 | 0 | 93
39007.4199 | 2200 | 0 | 93
39007.4217 | 2543 | 0 | 93
39007.4235 | 1738 | 598 | 93
93
39007.4181 | 1 | 0 | 94
39007.4199 | 1771 | 0 | 94
39007.4217 | 2219 | 0 | 94
39007.4235 | 1883 | 379 | 94
94
39007.4181 | 1 | 0 | 95
39007.4199 | 2515 | 0 | 95
39007.4217 | 2021 | 0 | 95
39007.4235 | 2144 | 405 | 95
95
39007.4182 | 1 | 0 | 96
39007.42 | 2203 | 0 | 96
39007.4217 | 2021 | 0 | 96
39007.4235 | 1928 | 448 | 96
96
39007.4182 | 1 | 0 | 97
39007.42 | 1692 | 0 | 97
39007.4217 | 2329 | 0 | 97
39007.4235 | 2034 | 419 | 97
97
39007.4182 | 1 | 0 | 98
39007.42 | 2462 | 0 | 98
39007.4218 | 2381 | 0 | 98
39007.4236 | 2381 | 354 | 98
98
39007.4182 | 1 | 0 | 99
39007.42 | 2219 | 0 | 99
39007.4218 | 2309 | 0 | 99
39007.4236 | 2220 | 464 | 99
99
39007.4182 | 1 | 0 | 100
39007.42 | 2474 | 0 | 100
39007.4218 | 2586 | 0 | 100
39007.4236 | 2042 | 462 | 100
100
39007.4183 | 1 | 0 | 101
39007.42 | 2624 | 0 | 101
39007.4218 | 2606 | 0 | 101
39007.4236 | 1934 | 242 | 101
101
39007.4183 | 1 | 0 | 102
39007.42 | 2434 | 0 | 102
39007.4218 | 2561 | 0 | 102
39007.4236 | 2163 | 313 | 102
102
39007.4183 | 1 | 0 | 103
39007.4201 | 2354 | 0 | 103
39007.4219 | 2391 | 0 | 103
39007.4236 | 2000 | 345 | 103
103
39007.4183 | 1 | 0 | 104
39007.4201 | 2025 | 0 | 104
39007.4219 | 2446 | 0 | 104
39007.4236 | 2289 | 231 | 104
104
39007.4183 | 1 | 0 | 105
39007.4201 | 2231 | 0 | 105
39007.4219 | 2111 | 0 | 105
39007.4237 | 2081 | 476 | 105
105
39007.4183 | 1 | 0 | 106
39007.4201 | 2118 | 0 | 106
39007.4219 | 2192 | 0 | 106
39007.4237 | 2067 | 227 | 106
106
39007.4183 | 1 | 0 | 107
39007.4201 | 2040 | 0 | 107
39007.4219 | 2353 | 0 | 107
39007.4237 | 2077 | 369 | 107
107
39007.4184 | 1 | 0 | 108
39007.4202 | 2353 | 0 | 108
39007.4219 | 2590 | 0 | 108
39007.4237 | 2051 | 327 | 108
108
39007.4184 | 1 | 0 | 109
39007.4202 | 2260 | 0 | 109
39007.4219 | 2396 | 0 | 109
39007.4237 | 1717 | 534 | 109
109
39007.4184 | 1 | 0 | 110
39007.4202 | 2023 | 0 | 110
39007.422 | 2320 | 0 | 110
39007.4237 | 2186 | 610 | 110
110

## Temperatures
DAQ Time | Burner Time | Cable center | Air above cable | Air below cable | TRAY A
0 | -191 | 16.6 | 15.7 | 15.9 | 17.6
1 | -190 | 16.6 | 15.7 | 15.9 | 17.6
2 | -189 | 16.6 | 15.7 | 15.9 | 17.6
3 | -188 | 16.6 | 15.7 | 15.9 | 17.6
4 | -187 | 16.6 | 15.7 | 15.9 | 17.6
5 | -186 | 16.6 | 15.7 | 15.9 | 17.6
6 | -185 | 16.6 | 15.7 | 15.9 | 17.6
7 | -184 | 16.6 | 15.7 | 15.9 | 17.6
8 | -183 | 16.6 | 15.7 | 15.9 | 17.6
9 | -182 | 16.6 | 15.7 | 15.9 | 17.6
10 | -181 | 16.6 | 15.7 | 15.9 | 17.6
11 | -180 | 16.6 | 15.8 | 15.9 | 17.6
12 | -179 | 16.6 | 15.8 | 15.9 | 17.6
13 | -178 | 16.6 | 15.7 | 15.9 | 17.6
14 | -177 | 16.6 | 15.7 | 15.9 | 17.6
15 | -176 | 16.6 | 15.8 | 15.9 | 17.6
16 | -175 | 16.6 | 15.8 | 15.9 | 17.6
17 | -174 | 16.6 | 15.8 | 15.9 | 17.6
18 | -173 | 16.6 | 15.8 | 15.9 | 17.6
19 | -172 | 16.6 | 15.8 | 15.9 | 17.6
20 | -171 | 16.6 | 15.8 | 15.9 | 17.6
21 | -170 | 16.6 | 15.8 | 15.9 | 17.6
22 | -169 | 16.6 | 15.8 | 15.9 | 17.6
23 | -168 | 16.6 | 15.7 | 15.9 | 17.6
24 | -167 | 16.6 | 15.7 | 15.9 | 17.6
25 | -166 | 16.6 | 15.8 | 15.9 | 17.6
26 | -165 | 16.6 | 15.7 | 15.9 | 17.6
27 | -164 | 16.6 | 15.7 | 15.9 | 17.6
28 | -163 | 16.6 | 15.7 | 15.9 | 17.6
29 | -162 | 16.6 | 15.7 | 15.9 | 17.6
30 | -161 | 16.6 | 15.7 | 15.9 | 17.6
31 | -160 | 16.6 | 15.7 | 15.8 | 17.6
32 | -159 | 16.6 | 15.7 | 15.8 | 17.6
33 | -158 | 16.6 | 15.7 | 15.9 | 17.6
34 | -157 | 16.6 | 15.7 | 15.9 | 17.6
35 | -156 | 16.6 | 15.7 | 15.9 | 17.6
36 | -155 | 16.6 | 15.7 | 15.9 | 17.6
37 | -154 | 16.6 | 15.7 | 15.9 | 17.6
38 | -153 | 16.6 | 15.7 | 15.9 | 17.6
39 | -152 | 16.6 | 15.7 | 15.9 | 17.6
40 | -151 | 16.6 | 15.7 | 15.9 | 17.6
41 | -150 | 16.6 | 15.7 | 15.9 | 17.6
42 | -149 | 16.6 | 15.7 | 15.9 | 17.6
43 | -148 | 16.6 | 15.7 | 15.9 | 17.6
44 | -147 | 16.6 | 15.7 | 15.9 | 17.6
45 | -146 | 16.6 | 15.7 | 15.9 | 17.6
46 | -145 | 16.6 | 15.8 | 15.9 | 17.6
47 | -144 | 16.6 | 15.8 | 15.9 | 17.6
48 | -143 | 16.6 | 15.8 | 15.9 | 17.6
49 | -142 | 16.6 | 15.8 | 15.9 | 17.6
50 | -141 | 16.6 | 15.8 | 15.9 | 17.6
51 | -140 | 16.6 | 15.8 | 15.9 | 17.6
52 | -139 | 16.6 | 15.8 | 15.9 | 17.6
53 | -138 | 16.6 | 15.8 | 15.9 | 17.6
54 | -137 | 16.6 | 15.8 | 15.9 | 17.6
55 | -136 | 16.6 | 15.8 | 15.9 | 17.6
56 | -135 | 16.6 | 15.8 | 15.9 | 17.6
57 | -134 | 16.6 | 15.8 | 15.9 | 17.6
58 | -133 | 16.6 | 15.8 | 15.9 | 17.6
59 | -132 | 16.6 | 15.8 | 15.9 | 17.6
60 | -131 | 16.6 | 15.8 | 15.9 | 17.6
61 | -130 | 16.6 | 15.8 | 15.9 | 17.6
62 | -129 | 16.6 | 15.8 | 15.9 | 17.6
63 | -128 | 16.6 | 15.8 | 15.9 | 17.6
64 | -127 | 16.6 | 15.8 | 15.9 | 17.6
65 | -126 | 16.6 | 15.8 | 16 | 17.6
66 | -125 | 16.6 | 15.8 | 16 | 17.6
67 | -124 | 16.6 | 15.8 | 16 | 17.6
68 | -123 | 16.6 | 15.8 | 16 | 17.6
69 | -122 | 16.6 | 15.8 | 16 | 17.6
70 | -121 | 16.6 | 15.8 | 16 | 17.6
71 | -120 | 16.6 | 15.8 | 16 | 17.6
72 | -119 | 16.6 | 15.8 | 16 | 17.6
73 | -118 | 16.6 | 15.8 | 16 | 17.6
74 | -117 | 16.6 | 15.8 | 16 | 17.6
75 | -116 | 16.6 | 15.8 | 16 | 17.6
76 | -115 | 16.6 | 15.8 | 16 | 17.6
77 | -114 | 16.6 | 15.8 | 16 | 17.6
78 | -113 | 16.6 | 15.8 | 16 | 17.6
79 | -112 | 16.6 | 15.8 | 16 | 17.6
80 | -111 | 16.6 | 15.8 | 16 | 17.6
81 | -110 | 16.6 | 15.8 | 16 | 17.6
82 | -109 | 16.6 | 15.8 | 16 | 17.6
83 | -108 | 16.6 | 15.8 | 16 | 17.6
84 | -107 | 16.6 | 15.8 | 16 | 17.6
85 | -106 | 16.6 | 15.8 | 16 | 17.6
86 | -105 | 16.6 | 15.8 | 16 | 17.6
87 | -104 | 16.6 | 15.8 | 16 | 17.6
88 | -103 | 16.6 | 15.8 | 16 | 17.6
89 | -102 | 16.6 | 15.8 | 16 | 17.6
90 | -101 | 16.6 | 15.8 | 16 | 17.6
91 | -100 | 16.6 | 15.8 | 16 | 17.6
92 | -99 | 16.6 | 15.8 | 16 | 17.6
93 | -98 | 16.6 | 15.8 | 16 | 17.6
94 | -97 | 16.6 | 15.8 | 16 | 17.6
95 | -96 | 16.6 | 15.8 | 16 | 17.6
96 | -95 | 16.6 | 15.8 | 16 | 17.6
97 | -94 | 16.6 | 15.8 | 16 | 17.6
98 | -93 | 16.6 | 15.8 | 16 | 17.6
99 | -92 | 16.6 | 15.8 | 16.1 | 17.6
100 | -91 | 16.6 | 15.9 | 16.1 | 17.6
101 | -90 | 16.6 | 15.9 | 16.1 | 17.7
102 | -89 | 16.6 | 15.9 | 16.1 | 17.7
103 | -88 | 16.6 | 15.9 | 16.1 | 17.6
104 | -87 | 16.6 | 15.9 | 16.1 | 17.7
105 | -86 | 16.7 | 15.9 | 16.1 | 17.7
106 | -85 | 16.6 | 15.9 | 16 | 17.7
107 | -84 | 16.6 | 15.9 | 16 | 17.6
108 | -83 | 16.6 | 15.9 | 16 | 17.7
109 | -82 | 16.6 | 15.9 | 16 | 17.6
110 | -81 | 16.6 | 15.9 | 16 | 17.6
111 | -80 | 16.6 | 15.9 | 16 | 17.6
112 | -79 | 16.7 | 15.9 | 16 | 17.6
113 | -78 | 16.6 | 15.9 | 16 | 17.6
114 | -77 | 16.7 | 15.9 | 16 | 17.6
115 | -76 | 16.7 | 15.9 | 16 | 17.6
116 | -75 | 16.7 | 15.9 | 16 | 17.6
117 | -74 | 16.7 | 15.9 | 16 | 17.6
118 | -73 | 16.6 | 15.8 | 16 | 17.6
119 | -72 | 16.6 | 15.8 | 16 | 17.6
120 | -71 | 16.6 | 15.8 | 16 | 17.6
121 | -70 | 16.6 | 15.8 | 16 | 17.6
122 | -69 | 16.6 | 15.8 | 16 | 17.6
123 | -68 | 16.7 | 15.9 | 16 | 17.6
124 | -67 | 16.6 | 15.9 | 16 | 17.6
125 | -66 | 16.7 | 15.8 | 16 | 17.6
126 | -65 | 16.7 | 15.9 | 16 | 17.7
127 | -64 | 16.7 | 15.8 | 16 | 17.6
128 | -63 | 16.6 | 15.8 | 16 | 17.6
129 | -62 | 16.6 | 15.9 | 16 | 17.6
130 | -61 | 16.6 | 15.9 | 16 | 17.6
131 | -60 | 16.7 | 15.9 | 16 | 17.6
132 | -59 | 16.7 | 15.9 | 16 | 17.6
133 | -58 | 16.7 | 15.9 | 16 | 17.7
134 | -57 | 16.6 | 15.9 | 16 | 17.6
135 | -56 | 16.7 | 15.9 | 16 | 17.7
136 | -55 | 16.7 | 15.9 | 16 | 17.7
137 | -54 | 16.6 | 15.9 | 16 | 17.7
138 | -53 | 16.6 | 15.9 | 16 | 17.7
139 | -52 | 16.6 | 15.9 | 16 | 17.7
140 | -51 | 16.7 | 15.9 | 16 | 17.7
141 | -50 | 16.6 | 15.9 | 16 | 17.7
142 | -49 | 16.6 | 15.9 | 16 | 17.6
143 | -48 | 16.7 | 15.9 | 16 | 17.7
144 | -47 | 16.7 | 15.9 | 16 | 17.6
145 | -46 | 16.7 | 15.9 | 16 | 17.7
146 | -45 | 16.7 | 15.9 | 16 | 17.6
147 | -44 | 16.7 | 15.8 | 16 | 17.7
148 | -43 | 16.7 | 15.9 | 16 | 17.7
149 | -42 | 16.7 | 15.8 | 16 | 17.7
150 | -41 | 16.7 | 15.8 | 16 | 17.7
151 | -40 | 16.7 | 15.8 | 16 | 17.7
152 | -39 | 16.7 | 15.8 | 16 | 17.7
153 | -38 | 16.7 | 15.8 | 16 | 17.7
154 | -37 | 16.7 | 15.9 | 16 | 17.7
155 | -36 | 16.7 | 15.9 | 16 | 17.7
156 | -35 | 16.7 | 15.9 | 16 | 17.7
157 | -34 | 16.7 | 15.9 | 16 | 17.7
158 | -33 | 16.7 | 15.9 | 16 | 17.7
159 | -32 | 16.7 | 15.9 | 16 | 17.6
160 | -31 | 16.7 | 15.9 | 16 | 17.6
161 | -30 | 16.7 | 15.9 | 16 | 17.6
162 | -29 | 16.7 | 15.9 | 16 | 17.7
163 | -28 | 16.7 | 15.9 | 16 | 17.6
164 | -27 | 16.7 | 15.9 | 16 | 17.6
165 | -26 | 16.7 | 15.9 | 16 | 17.6
166 | -25 | 16.6 | 15.9 | 16 | 17.6
167 | -24 | 16.7 | 15.9 | 16 | 17.6
168 | -23 | 16.7 | 15.9 | 16 | 17.6
169 | -22 | 16.7 | 15.9 | 16 | 17.6
170 | -21 | 16.7 | 15.9 | 16 | 17.6
171 | -20 | 16.7 | 15.9 | 16 | 17.6
172 | -19 | 16.7 | 15.9 | 16 | 17.7
173 | -18 | 16.7 | 15.9 | 16 | 17.6
174 | -17 | 16.7 | 15.9 | 16 | 17.7
175 | -16 | 16.7 | 15.9 | 16 | 17.7
176 | -15 | 16.7 | 15.9 | 16 | 17.7
177 | -14 | 16.7 | 15.9 | 16 | 17.7
178 | -13 | 16.7 | 15.9 | 16 | 17.7
179 | -12 | 16.7 | 15.9 | 16 | 17.7
180 | -11 | 16.7 | 15.9 | 16 | 17.7
181 | -10 | 16.7 | 15.9 | 16 | 17.7
182 | -9 | 16.7 | 15.9 | 16 | 17.7
183 | -8 | 16.7 | 15.9 | 16 | 17.7
184 | -7 | 16.7 | 15.9 | 16 | 17.7
185 | -6 | 16.7 | 15.9 | 16 | 17.7
186 | -5 | 16.7 | 15.9 | 16 | 17.7
187 | -4 | 16.7 | 15.9 | 16 | 17.7
188 | -3 | 16.7 | 15.9 | 16 | 17.7
189 | -2 | 16.7 | 15.9 | 16.1 | 17.7
190 | -1 | 16.7 | 15.9 | 16.1 | 17.7
191 | 0 | 16.7 | 15.9 | 16.1 | 17.7
192 | 1 | 16.7 | 15.9 | 16.1 | 17.7
193 | 2 | 16.7 | 15.9 | 16.1 | 17.7
194 | 3 | 16.7 | 15.9 | 16.1 | 17.8
195 | 4 | 16.7 | 16.1 | 16.2 | 18
196 | 5 | 16.7 | 18.1 | 19.4 | 20.3
197 | 6 | 16.7 | 26.6 | 26.9 | 25.4
198 | 7 | 16.7 | 40.9 | 42.4 | 30.2
199 | 8 | 16.7 | 57.6 | 51.3 | 34.8
200 | 9 | 16.8 | 71.8 | 69.2 | 45.8
201 | 10 | 17.1 | 87.8 | 89.9 | 57.1
202 | 11 | 17.5 | 124 | 110.6 | 65.1
203 | 12 | 18 | 158.8 | 134.4 | 71.2
204 | 13 | 18.9 | 198.3 | 153.8 | 77.2
205 | 14 | 20.1 | 249.9 | 181.3 | 86.7
206 | 15 | 21.5 | 287 | 209.1 | 94.8
207 | 16 | 23.2 | 317.4 | 220.4 | 102.4
208 | 17 | 25.2 | 351 | 236.7 | 117.8
209 | 18 | 27.6 | 370.6 | 255.5 | 132.9
210 | 19 | 30.2 | 386.4 | 271.6 | 137.4
211 | 20 | 33.1 | 401.8 | 305.7 | 147.9
212 | 21 | 36.3 | 422 | 337.3 | 164.7
213 | 22 | 39.6 | 445.2 | 355.6 | 167.5
214 | 23 | 43 | 477.3 | 381.1 | 174.9
215 | 24 | 46.7 | 511.9 | 398.9 | 185.8
216 | 25 | 50.4 | 533.5 | 414.7 | 188.2
217 | 26 | 53.5 | 558.3 | 435.1 | 194.9
218 | 27 | 56.8 | 574.4 | 453.2 | 207.7
219 | 28 | 60.8 | 592.8 | 475.5 | 213.2
220 | 29 | 65 | 617 | 488.7 | 209.2
221 | 30 | 69.5 | 622.9 | 477 | 206
222 | 31 | 74.3 | 634.7 | 464.3 | 200.2
223 | 32 | 79.4 | 656.2 | 457.6 | 204.2
224 | 33 | 84.6 | 664.5 | 457.3 | 208.1
225 | 34 | 89.8 | 672.8 | 449.2 | 207
226 | 35 | 95.2 | 677.8 | 464.8 | 213.2
227 | 36 | 100.6 | 684.6 | 475.5 | 219.3
228 | 37 | 106.1 | 690.7 | 471.4 | 220.9
229 | 38 | 111.6 | 701.5 | 465 | 226.5
230 | 39 | 117.5 | 707.7 | 460.5 | 237.6
231 | 40 | 123.1 | 707.6 | 466.4 | 243.2
232 | 41 | 128.5 | 711.9 | 474.6 | 252.4
233 | 42 | 133.9 | 712.7 | 473.5 | 253.2
234 | 43 | 139.1 | 707.8 | 477.6 | 254.7
235 | 44 | 144 | 711.5 | 484.5 | 263.8
236 | 45 | 148.4 | 710.5 | 493.3 | 273.8
237 | 46 | 152.4 | 716.3 | 498.1 | 279.3
238 | 47 | 156 | 722.4 | 498 | 282.1
239 | 48 | 159.4 | 731.3 | 491.2 | 280.9
240 | 49 | 162.6 | 737.4 | 503.1 | 282.1
241 | 50 | 165.7 | 743.3 | 508.6 | 285.2
242 | 51 | 168.6 | 737.1 | 501.4 | 286.4
243 | 52 | 171.6 | 743.4 | 496.9 | 287.4
244 | 53 | 174.8 | 744.5 | 512.4 | 292.2
245 | 54 | 178.1 | 748.1 | 523.2 | 298.5
246 | 55 | 181.3 | 749.9 | 523.9 | 303.3
247 | 56 | 184.4 | 753.8 | 516.7 | 309.1
248 | 57 | 188.7 | 747.5 | 522.4 | 323.5
249 | 58 | 192.4 | 749.4 | 537.2 | 328.6
250 | 59 | 193.9 | 752.7 | 552.6 | 332.6
251 | 60 | 195.1 | 750.8 | 559 | 336.3
252 | 61 | 197 | 752.9 | 564.3 | 342.8
253 | 62 | 199.1 | 756.1 | 558.5 | 350.8
254 | 63 | 201.5 | 757.4 | 574.1 | 352.7
255 | 64 | 203.6 | 757.3 | 600 | 360.4
256 | 65 | 206.3 | 752.4 | 615.8 | 365.1
257 | 66 | 209.2 | 737.1 | 629.9 | 360.9
258 | 67 | 212 | 727.8 | 628.1 | 359.5
259 | 68 | 214.8 | 742.7 | 628.2 | 364.9
260 | 69 | 217.7 | 735.7 | 623.5 | 367.4
261 | 70 | 221.6 | 737.6 | 634 | 363.9
262 | 71 | 226.8 | 734.7 | 631.8 | 363.7
263 | 72 | 231.7 | 742 | 635.9 | 364.6
264 | 73 | 236.2 | 748.1 | 623.6 | 368.9
265 | 74 | 241 | 745.9 | 609.3 | 374.8
266 | 75 | 245.2 | 743.3 | 606.5 | 381.1
267 | 76 | 248.7 | 746.4 | 607.1 | 385.4
268 | 77 | 251.4 | 747.3 | 603.7 | 391.2
269 | 78 | 252.9 | 746.2 | 617.7 | 399.4
270 | 79 | 253.6 | 750.9 | 644.6 | 409
271 | 80 | 254.1 | 766.8 | 661.8 | 421.8
272 | 81 | 255.2 | 772.5 | 650.2 | 431.2
273 | 82 | 256.2 | 767 | 637.8 | 426.8
274 | 83 | 255.6 | 771.6 | 629.9 | 424.1
275 | 84 | 252.5 | 778.8 | 620.3 | 429.8
276 | 85 | 249.2 | 784.4 | 609.8 | 426.2
277 | 86 | 248.2 | 788.9 | 606.2 | 425.6
278 | 87 | 248.4 | 797.9 | 601.9 | 426.4
279 | 88 | 249.5 | 807.8 | 600.3 | 431.9
280 | 89 | 249.8 | 810.8 | 600.8 | 433.5
281 | 90 | 250.4 | 817 | 607.2 | 434.6
282 | 91 | 252.2 | 821.6 | 606.5 | 442.7
283 | 92 | 254.1 | 810.7 | 598 | 443.5
284 | 93 | 256.7 | 815.4 | 586.8 | 450.3
285 | 94 | 259.3 | 815.3 | 581.1 | 449.6
286 | 95 | 260.9 | 815.9 | 577.2 | 451
287 | 96 | 262.4 | 814.2 | 570.9 | 451.8
288 | 97 | 263.7 | 820.2 | 568.7 | 453.7
289 | 98 | 265.3 | 824.9 | 562.7 | 458.5
290 | 99 | 266 | 833.7 | 553.4 | 453.3
291 | 100 | 268.8 | 837.1 | 549.7 | 447.9
292 | 101 | 272.8 | 841 | 538.2 | 448.2
293 | 102 | 275.9 | 849.7 | 535.1 | 450.6
294 | 103 | 278.2 | 856.8 | 542.9 | 454
295 | 104 | 282.1 | 861.8 | 566.5 | 465.1
296 | 105 | 285.2 | 854.7 | 594.9 | 482.2
297 | 106 | 287.2 | 858.5 | 614.8 | 489.3
298 | 107 | 289.6 | 848 | 630.6 | 489.5
299 | 108 | 292 | 845.8 | 620.4 | 485.8
300 | 109 | 297.1 | 824.4 | 600.6 | 479.4
301 | 110 | 301.9 | 826.7 | 601.8 | 483.1
302 | 111 | 305.5 | 837.9 | 584.7 | 482.9
303 | 112 | 307.1 | 832.4 | 579.7 | 486.8
304 | 113 | 308.2 | 829.5 | 599.3 | 487.6
305 | 114 | 309.6 | 825.7 | 609.4 | 494
306 | 115 | 312.6 | 821.2 | 618.2 | 504.2
307 | 116 | 316 | 807.3 | 622.2 | 502.5
308 | 117 | 319.3 | 812.9 | 627.1 | 501.8
309 | 118 | 322.5 | 815.6 | 631.4 | 503.8
310 | 119 | 325.3 | 820.4 | 633.8 | 510.5
311 | 120 | 328.6 | 819.9 | 642.2 | 519
312 | 121 | 332.1 | 806.5 | 645.9 | 518.8
313 | 122 | 335 | 800.1 | 654.1 | 510.9
314 | 123 | 337.2 | 801.3 | 656.2 | 506.4
315 | 124 | 339.6 | 800.7 | 649.9 | 507.5
316 | 125 | 341.9 | 812.3 | 641.5 | 507.9
317 | 126 | 343.9 | 820.2 | 629 | 506.2
318 | 127 | 346.3 | 829.9 | 627.8 | 509.9
319 | 128 | 348.9 | 840.5 | 626.7 | 515.1
320 | 129 | 351.3 | 854.2 | 618.6 | 517.1
321 | 130 | 354.1 | 864.3 | 617.5 | 519.9
322 | 131 | 356.6 | 867.2 | 634.5 | 528.7
323 | 132 | 358.8 | 869.6 | 649.9 | 533.7
324 | 133 | 361.5 | 866.9 | 657.8 | 537.5
325 | 134 | 364.6 | 871.3 | 663.6 | 534.1
326 | 135 | 367.8 | 876.6 | 650.3 | 533.2
327 | 136 | 371.1 | 863.6 | 633.9 | 532.6
328 | 137 | 373.9 | 860.8 | 628.2 | 537.6
329 | 138 | 376.5 | 863.8 | 625.3 | 536.5
330 | 139 | 378.9 | 867.1 | 633.3 | 536.9
331 | 140 | 381.5 | 866.1 | 626.6 | 532.9
332 | 141 | 384.2 | 866.6 | 612.1 | 529.2
333 | 142 | 387.3 | 860.6 | 597.3 | 526.4
334 | 143 | 390.4 | 869.1 | 588.1 | 524.4
335 | 144 | 393 | 865.4 | 581.3 | 531.4
336 | 145 | 395.3 | 863.1 | 588.5 | 535.9
337 | 146 | 397.4 | 854.2 | 604.3 | 544.3
338 | 147 | 399.6 | 850.5 | 604.4 | 546.8
339 | 148 | 401.9 | 852.6 | 606.1 | 552.9
340 | 149 | 404.3 | 858.5 | 597.8 | 555.6
341 | 150 | 406.7 | 863.9 | 587.8 | 558.1
342 | 151 | 409.3 | 877.4 | 587.2 | 555.8
343 | 152 | 412.1 | 884.6 | 584.5 | 557.2
344 | 153 | 415 | 895.2 | 595 | 557.2
345 | 154 | 418.2 | 893.7 | 587.2 | 559.5
346 | 155 | 421.7 | 887 | 592.8 | 569.4
347 | 156 | 425 | 881.4 | 594.4 | 571.1
348 | 157 | 428.2 | 871.8 | 582.8 | 577
349 | 158 | 431.4 | 869.6 | 575.7 | 583
350 | 159 | 434.6 | 876.9 | 566.9 | 577.4
351 | 160 | 438 | 883 | 563.2 | 574.6
352 | 161 | 441.6 | 879.5 | 565.9 | 576.1
353 | 162 | 444.8 | 876.5 | 560.7 | 579.9
354 | 163 | 448.3 | 872.5 | 560.1 | 579.8
355 | 164 | 451.2 | 869.9 | 563.8 | 585.3
356 | 165 | 453.9 | 868.8 | 570 | 586.6
357 | 166 | 456.9 | 871.2 | 579.9 | 583.1
358 | 167 | 460 | 861.3 | 589.9 | 589.8
359 | 168 | 462.8 | 848 | 602.2 | 598.1
360 | 169 | 465.6 | 855.8 | 599.7 | 610.3
361 | 170 | 468.9 | 869.5 | 609.1 | 610.2
362 | 171 | 472.6 | 877.4 | 613.2 | 606.7
363 | 172 | 476.7 | 867.2 | 616.1 | 610.1
364 | 173 | 480.9 | 873.7 | 608.6 | 603.5
365 | 174 | 485.7 | 872.1 | 605.9 | 601.7
366 | 175 | 490.3 | 874 | 603.4 | 594
367 | 176 | 494.4 | 878.1 | 607.3 | 594.6
368 | 177 | 498.3 | 886.2 | 609 | 592.5
369 | 178 | 502 | 885.5 | 621.2 | 592.4
370 | 179 | 505.7 | 885.3 | 622.9 | 598.2
371 | 180 | 509.5 | 880.1 | 624.5 | 593.6
372 | 181 | 513.4 | 870.5 | 625.6 | 590.6
373 | 182 | 517.2 | 861.5 | 637 | 592.7
374 | 183 | 521.2 | 863 | 646.8 | 595.4
375 | 184 | 526.1 | 846.8 | 656.1 | 601.8
376 | 185 | 531 | 848.2 | 670.8 | 600.5
377 | 186 | 535.6 | 854.4 | 678.8 | 604.7
378 | 187 | 539.7 | 847.8 | 670.3 | 607.8
379 | 188 | 543.7 | 848.1 | 675.9 | 610.5
380 | 189 | 547.4 | 856 | 684 | 612.9
381 | 190 | 551 | 864.2 | 683.1 | 602.6
382 | 191 | 554.8 | 865.2 | 679.1 | 600.3
383 | 192 | 559 | 856.8 | 680.8 | 598.3
384 | 193 | 562.8 | 850.3 | 696.3 | 603.5
385 | 194 | 566.5 | 853.3 | 702.2 | 609.3
386 | 195 | 570.5 | 854.7 | 710.5 | 616.2
387 | 196 | 574.7 | 852 | 705.9 | 612.1
388 | 197 | 579.1 | 851.5 | 693 | 603.7
389 | 198 | 583 | 846.9 | 685.1 | 609.5
390 | 199 | 586.5 | 838 | 672.5 | 609.3
391 | 200 | 589.9 | 834.4 | 665.6 | 604.7
392 | 201 | 593 | 845.5 | 652.6 | 604.2
393 | 202 | 596.3 | 854.5 | 642.9 | 603.2
394 | 203 | 599.3 | 857.3 | 642.6 | 602.7
395 | 204 | 602.3 | 851.5 | 646.1 | 597.1
396 | 205 | 605 | 858.7 | 664.2 | 600.5
397 | 206 | 607.6 | 869.5 | 676.8 | 611.9
398 | 207 | 610.6 | 869.9 | 673.8 | 615.6
399 | 208 | 614 | 870.7 | 678.3 | 616.6
400 | 209 | 617.5 | 866.9 | 674.9 | 619.2
401 | 210 | 621.1 | 862.5 | 663 | 608.8
402 | 211 | 624.8 | 859.6 | 660.5 | 607
403 | 212 | 628.1 | 851.6 | 673.2 | 609.2
404 | 213 | 631.3 | 843 | 674.4 | 607.3
405 | 214 | 634.5 | 847.4 | 676.7 | 607.8
406 | 215 | 638 | 852.8 | 661.9 | 606.2
407 | 216 | 641.8 | 840.1 | 633.9 | 598.8
408 | 217 | 645.8 | 833.3 | 625.8 | 595.7
409 | 218 | 649.4 | 823.5 | 607.2 | 588.3
410 | 219 | 653.1 | 800.1 | 584.8 | 582
411 | 220 | 656.5 | 803.1 | 569.8 | 581.1
412 | 221 | 659.2 | 804 | 563.3 | 580.1
413 | 222 | 661.2 | 806.2 | 563.7 | 580.9
414 | 223 | 662.6 | 802.1 | 556.5 | 582.8
415 | 224 | 663.7 | 811.5 | 577.3 | 583
416 | 225 | 665 | 820.8 | 587.8 | 584.3
417 | 226 | 666.8 | 817.2 | 583.1 | 580.4
418 | 227 | 668.7 | 832.4 | 579.2 | 577.1
419 | 228 | 670.9 | 844.3 | 567.8 | 577
420 | 229 | 673.1 | 855.5 | 557.9 | 578.7
421 | 230 | 675.2 | 848.2 | 564.8 | 576.3
422 | 231 | 677.7 | 841 | 566.2 | 574.4
423 | 232 | 679.8 | 838.9 | 572.3 | 574.1
424 | 233 | 681.9 | 838.7 | 574.3 | 574.6
425 | 234 | 684.3 | 824.8 | 578.2 | 575
426 | 235 | 686.7 | 822.2 | 571.3 | 571.9
427 | 236 | 688.8 | 829.9 | 579.7 | 572.4
428 | 237 | 690.6 | 838.4 | 587.2 | 573.9
429 | 238 | 692.5 | 846.7 | 603.8 | 573.7
430 | 239 | 694.3 | 846.5 | 616.4 | 578.2
431 | 240 | 696.3 | 850.9 | 622.3 | 581.4
432 | 241 | 698.8 | 846.8 | 622.5 | 576.8
433 | 242 | 701.5 | 836.6 | 621.5 | 576.3
434 | 243 | 704.1 | 827 | 619.3 | 575.1
435 | 244 | 706.4 | 827.1 | 618.5 | 576.4
436 | 245 | 708.6 | 841.7 | 612.1 | 577.6
437 | 246 | 710.8 | 850.9 | 605.7 | 578.9
438 | 247 | 712.7 | 853.5 | 610.5 | 579
439 | 248 | 714.3 | 862.1 | 612 | 580.7
440 | 249 | 715.7 | 874.6 | 610.9 | 583.2
441 | 250 | 717.3 | 872.1 | 606 | 581.2
442 | 251 | 719.1 | 868.1 | 599.2 | 576.1
443 | 252 | 721.5 | 851.6 | 592.6 | 573.2
444 | 253 | 723.5 | 851.4 | 592 | 573.6
445 | 254 | 724.6 | 858 | 612.6 | 576.5
446 | 255 | 726 | 850.6 | 608 | 576.3
447 | 256 | 727.2 | 862.7 | 620.2 | 580.2
448 | 257 | 728.8 | 860.1 | 626.9 | 581.1
449 | 258 | 730.7 | 838.3 | 623 | 582.3
450 | 259 | 733 | 826.9 | 615.1 | 577.5
451 | 260 | 735 | 817.2 | 616.4 | 572.6
452 | 261 | 736.3 | 812.1 | 610.3 | 568.4
453 | 262 | 737.7 | 804.8 | 596 | 567.7
454 | 263 | 739.1 | 807.1 | 594.6 | 567.3
455 | 264 | 740.4 | 802.6 | 584.1 | 569.3
456 | 265 | 741.8 | 787.9 | 577.1 | 565.7
457 | 266 | 742.6 | 767.3 | 568.7 | 563.3
458 | 267 | 743.3 | 767.1 | 561.5 | 561
459 | 268 | 743.9 | 750.1 | 556 | 559.5
460 | 269 | 744.7 | 713.1 | 535.2 | 551.1
461 | 270 | 744.9 | 664.3 | 509.4 | 542.4
462 | 271 | 744.4 | 621.3 | 485.9 | 538
463 | 272 | 743.4 | 586 | 464.2 | 533.2
464 | 273 | 741.9 | 555.8 | 444.2 | 528.3
465 | 274 | 740.3 | 528.4 | 426.5 | 523.5
466 | 275 | 738.6 | 504.2 | 409.8 | 520.1
467 | 276 | 736.7 | 483.2 | 394 | 516.1
468 | 277 | 734.8 | 460.3 | 379.5 | 512
469 | 278 | 732.8 | 441.4 | 366.7 | 508.3
470 | 279 | 730.8 | 425.4 | 354.3 | 505.4
471 | 280 | 728.5 | 409.5 | 342.6 | 502.3
472 | 281 | 726.1 | 396.4 | 331.8 | 498.2
473 | 282 | 723.9 | 382.1 | 321.2 | 493.8
474 | 283 | 721.6 | 368.1 | 311.3 | 490.9
475 | 284 | 719.3 | 354.9 | 302.6 | 488.4
476 | 285 | 716.7 | 343.6 | 293.4 | 485
477 | 286 | 714.2 | 331.4 | 285 | 482
478 | 287 | 711.6 | 320.7 | 277.5 | 478.1
479 | 288 | 708.9 | 310.7 | 270.7 | 473.9
480 | 289 | 706.4 | 300.3 | 263.7 | 470.6
481 | 290 | 703.8 | 290.8 | 257.3 | 467.7
482 | 291 | 701.1 | 283 | 251.5 | 465.2
483 | 292 | 698.4 | 275.9 | 245.2 | 462.1
484 | 293 | 695.5 | 268.5 | 239.7 | 460.1
485 | 294 | 692.6 | 261.5 | 234.1 | 457.2
486 | 295 | 689.6 | 255.8 | 228.5 | 454.8
487 | 296 | 686.5 | 250.7 | 222.9 | 453.3
488 | 297 | 683.5 | 245.4 | 218 | 450
489 | 298 | 680.5 | 238.9 | 213.7 | 446.1
490 | 299 | 677.5 | 232.7 | 209.3 | 442.7
491 | 300 | 674.8 | 226.9 | 205.4 | 440.1
492 | 301 | 671.9 | 221.6 | 201.3 | 437.6
493 | 302 | 669.1 | 216.6 | 197.2 | 434.9
494 | 303 | 666.4 | 212.1 | 193.2 | 433.1
495 | 304 | 663.6 | 208.6 | 189.4 | 430.3
496 | 305 | 660.8 | 204.8 | 185.7 | 427.9
497 | 306 | 657.9 | 201.6 | 182.4 | 426.2
498 | 307 | 655.1 | 197.8 | 179.2 | 423.7
499 | 308 | 652.5 | 193.8 | 175.9 | 421
500 | 309 | 649.8 | 189.3 | 172.9 | 418.3
501 | 310 | 647 | 185.5 | 170.3 | 416
502 | 311 | 644 | 181.6 | 167.5 | 413.4
503 | 312 | 641.2 | 177.4 | 164.7 | 410.8
504 | 313 | 638.2 | 173.8 | 162.2 | 408.4
505 | 314 | 635.3 | 171.3 | 159.7 | 405.8
506 | 315 | 632.4 | 168.7 | 157.2 | 403.6
507 | 316 | 629.7 | 165.1 | 154.5 | 400.2
508 | 317 | 626.9 | 161.6 | 151.7 | 396.2
509 | 318 | 623.9 | 158.2 | 149 | 392.7
510 | 319 | 620.9 | 154.9 | 146.4 | 390.7
511 | 320 | 618 | 152.5 | 144.1 | 388
512 | 321 | 615.1 | 150.1 | 142 | 387.3
513 | 322 | 612 | 147.7 | 139.3 | 385.8
514 | 323 | 608.8 | 146.3 | 137 | 383.1
515 | 324 | 605.5 | 144.8 | 134.8 | 380
516 | 325 | 602.2 | 142 | 133.1 | 378.3
517 | 326 | 598.9 | 139.8 | 131.6 | 377.2
518 | 327 | 595.4 | 137.9 | 129.4 | 375.6
519 | 328 | 591.9 | 136.2 | 127.7 | 374
520 | 329 | 588.2 | 134.8 | 126.2 | 371.9
521 | 330 | 584.6 | 133.7 | 124.9 | 370.3
522 | 331 | 581 | 132.8 | 123.5 | 368.2
523 | 332 | 577.5 | 132 | 121.9 | 366.6
524 | 333 | 573.9 | 131.1 | 120.5 | 365.3
525 | 334 | 570.5 | 130.3 | 119.2 | 363.4
526 | 335 | 567 | 129.6 | 118 | 361.1
527 | 336 | 563.7 | 128.8 | 116.8 | 359.5
528 | 337 | 560.3 | 127.6 | 115.5 | 357.8
529 | 338 | 557.1 | 126.4 | 114.4 | 356.3
530 | 339 | 554 | 125 | 112.8 | 353.7
531 | 340 | 550.9 | 123.4 | 111.3 | 350.7
532 | 341 | 547.8 | 121.9 | 110 | 349.1
533 | 342 | 544.8 | 120.1 | 108.9 | 347.7
534 | 343 | 541.7 | 118.2 | 107.8 | 346.1
535 | 344 | 538.7 | 116.8 | 106.6 | 345.3
536 | 345 | 535.6 | 115.9 | 105.4 | 344.3
537 | 346 | 532.5 | 115.2 | 104.4 | 342.8
538 | 347 | 529.4 | 114.3 | 103.4 | 341.7
539 | 348 | 526.3 | 113.8 | 102.4 | 340.1
540 | 349 | 523.2 | 112.8 | 101.5 | 337.9
541 | 350 | 520.1 | 111.9 | 100.5 | 336.4
542 | 351 | 517 | 111.2 | 99.5 | 335.3
543 | 352 | 513.9 | 110.4 | 98.4 | 333.8
544 | 353 | 510.8 | 109.7 | 97.4 | 332.7
545 | 354 | 507.8 | 109.2 | 96.4 | 331.6
546 | 355 | 504.7 | 108.5 | 95.4 | 330.5
547 | 356 | 501.7 | 107.7 | 94.4 | 329.1
548 | 357 | 498.9 | 106.9 | 93.5 | 327.6
549 | 358 | 495.9 | 106.1 | 92.7 | 326.5
550 | 359 | 493 | 105.4 | 91.9 | 325.1
551 | 360 | 490 | 104.7 | 91.1 | 323.6
552 | 361 | 487.1 | 104.1 | 90.2 | 322.1
553 | 362 | 484.3 | 103.6 | 89.4 | 321
554 | 363 | 481.4 | 103.2 | 88.5 | 319.8
555 | 364 | 478.6 | 102.7 | 87.7 | 318.7
556 | 365 | 475.9 | 101.7 | 86.8 | 317.4
557 | 366 | 473.1 | 100.8 | 86 | 315.9
558 | 367 | 470.5 | 99.8 | 85.2 | 315.2
559 | 368 | 467.8 | 99.2 | 84.5 | 314.1
560 | 369 | 465.1 | 98.5 | 83.9 | 312.5
561 | 370 | 462.6 | 97.7 | 83.3 | 311.1
562 | 371 | 460 | 96.7 | 82.7 | 309.7
563 | 372 | 457.5 | 95.8 | 82 | 308.6
564 | 373 | 454.9 | 94.9 | 81.4 | 307.4
565 | 374 | 452.3 | 94.1 | 80.8 | 306
566 | 375 | 450 | 93.5 | 80.1 | 304.8
567 | 376 | 447.6 | 92.6 | 79.3 | 303.6
568 | 377 | 445.2 | 92 | 78.5 | 302.4
569 | 378 | 442.9 | 91.6 | 77.9 | 301.5
570 | 379 | 440 | 91.3 | 77.3 | 300.3
571 | 380 | 438.3 | 91.3 | 76.8 | 298.8
572 | 381 | 435.8 | 90.6 | 76.2 | 297.7
573 | 382 | 429.7 | 90.2 | 75.6 | 296
574 | 383 | 431.7 | 89.8 | 75.1 | 294.4
575 | 384 | 426.1 | 89.1 | 74.6 | 292.9
576 | 385 | 420.5 | 88.5 | 74.1 | 291.9
577 | 386 | 425.3 | 87.7 | 73.8 | 290.4
578 | 387 | 415.5 | 86.5 | 72.9 | 289.4
579 | 388 | 415.8 | 85.5 | 72.3 | 288.5
580 | 389 | 419.1 | 84.8 | 72.4 | 287.6
581 | 390 | 417 | 84.2 | 71.9 | 286.9
582 | 391 | 415 | 83.9 | 71.4 | 285.9
583 | 392 | 410.6 | 83.5 | 70.7 | 285
584 | 393 | 397 | 83.1 | 69.3 | 284.1

## Test Facts
Last row in IRMS data sheets: | 9
Time when gas burner was ignited: | 191