## Test Conditions
CAROLFIRE Intermediate Scale Preliminary Test Number IP-4
Test Date: | 2006-10-17
Ignition Time Relative to Thermal Data: | 877 | s
Ignition Time Relative to Electrical Data: | 191 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
Gas Burner Heat Release Rate Calculation Parameters: |  | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
3/C cable temperatures and IRMS data
7/C cable temperatures and IRMS data

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 3/C PVC Cable |  |  | Location A - 7/C PVC Cable |  |  | Location A - Tray
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | Cable Temp | Temp Above Cable | Temp Below Cable | Cable Temp | Temp Above Cable | Temp Below Cable | Tray Rung Temp
0 | -877 | -5.9 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.3 | 269.3 | 12.9 | 16.6 | 16.1 | 16 | 16.8 | 15.9 | 16 | 17.7
1 | -876 | -5.3 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 3.1 | 269.6 | 12.4 | 16.6 | 16.1 | 16 | 16.8 | 15.9 | 16 | 17.7
2 | -875 | -6.2 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 3.1 | 261.2 | 12.4 | 16.6 | 16.1 | 16 | 16.8 | 15.9 | 15.9 | 17.7
3 | -874 | -6.4 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 3 | 268.8 | 10.7 | 16.6 | 16.1 | 16 | 16.8 | 15.9 | 16 | 17.7
4 | -873 | -5.9 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.5 | 254.3 | 9.7 | 16.6 | 16.1 | 16 | 16.8 | 15.9 | 15.9 | 17.7
5 | -872 | -6 | 0 | 0 | 17.6 | 17.9 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 2.2 | 268.6 | 9.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
6 | -871 | -6.3 | 0 | 0 | 17.6 | 17.9 | 17.6 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.4 | 273.4 | 10.1 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
7 | -870 | -6.5 | 0 | 0 | 17.6 | 17.9 | 17.5 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 2.7 | 225.4 | 8.8 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
8 | -869 | -5.3 | 0 | 0 | 17.6 | 17.9 | 17.5 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 3.2 | 255.7 | 8.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
9 | -868 | -5.6 | 0 | 0 | 17.6 | 17.9 | 17.5 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2.8 | 235.6 | 9.3 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
10 | -867 | -5.9 | 0 | 0 | 17.6 | 17.9 | 17.5 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2.3 | 236.9 | 8.7 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
11 | -866 | -6.5 | 0 | 0 | 17.6 | 17.9 | 17.5 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2 | 251.2 | 8.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
12 | -865 | -6.7 | 0 | 0 | 17.4 | 18 | 17.6 | 17.5 | 18.4 | 16.4 | 21.9 | 16.6 | 2.1 | 253.2 | 11.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
13 | -864 | -6.2 | 0 | 0 | 17.4 | 18 | 17.5 | 17.5 | 18.4 | 16.4 | 21.9 | 16.6 | 2.7 | 253 | 13.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
14 | -863 | -5.8 | 0 | 0 | 17.4 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.8 | 256.4 | 13.7 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 16 | 17.7
15 | -862 | -5.5 | 0 | 0 | 17.4 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.5 | 261.3 | 12.4 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 16 | 17.7
16 | -861 | -5.6 | 0 | 0 | 17.4 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.2 | 262.3 | 11.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 16 | 17.7
17 | -860 | -5.7 | 0 | 0 | 17.4 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.1 | 260.4 | 11.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 16 | 17.7
18 | -859 | -5.9 | 0 | 0 | 17.4 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.7 | 252.8 | 12.7 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 16 | 17.7
19 | -858 | -6.3 | 0 | 0 | 17.3 | 18 | 17.6 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.9 | 251.9 | 14.1 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 16 | 17.7
20 | -857 | -6.7 | 0 | 0 | 17.4 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 3.3 | 260.2 | 13.6 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 16 | 17.7
21 | -856 | -6.7 | 0 | 0 | 17.4 | 17.9 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 3 | 260.6 | 13.8 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
22 | -855 | -6.5 | 0 | 0 | 17.3 | 18 | 17.5 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.4 | 263.7 | 13.4 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
23 | -854 | -6.1 | 0 | 0 | 17.3 | 17.9 | 17.6 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.2 | 263.4 | 12.5 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
24 | -853 | -6.5 | 0 | 0 | 17.4 | 17.9 | 17.5 | 17.3 | 18.4 | 16.3 | 21.9 | 16.6 | 2.4 | 268.1 | 11.3 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
25 | -852 | -5.8 | 0 | 0 | 17.4 | 17.9 | 17.6 | 17.3 | 18.4 | 16.3 | 21.9 | 16.6 | 2.4 | 292.7 | 10.4 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
26 | -851 | -4.1 | 0 | 0 | 17.3 | 17.9 | 17.6 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.3 | 264.6 | 9.8 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
27 | -850 | -4.7 | 0 | 0 | 17.4 | 17.9 | 17.6 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.7 | 274.3 | 10.7 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
28 | -849 | -6 | 0 | 0 | 17.4 | 17.9 | 17.6 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.9 | 272.7 | 10.6 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
29 | -848 | -5.6 | 0 | 0 | 17.4 | 17.9 | 17.6 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 3.1 | 257.8 | 10.7 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
30 | -847 | -5.8 | 0 | 0 | 17.4 | 17.9 | 17.7 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.8 | 241.4 | 10.5 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
31 | -846 | -6.2 | 0 | 0 | 17.5 | 17.9 | 17.7 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 2.8 | 257.4 | 9.2 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
32 | -845 | -6.6 | 0 | 0 | 17.5 | 17.9 | 17.7 | 17.4 | 18.4 | 16.3 | 21.9 | 16.6 | 3.2 | 261.9 | 9.1 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
33 | -844 | -6.8 | 0 | 0 | 17.4 | 17.9 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3.3 | 235.5 | 8.6 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
34 | -843 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3.3 | 248.7 | 7.8 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
35 | -842 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 3.2 | 228.6 | 8.5 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
36 | -841 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.8 | 17.4 | 18.4 | 16.2 | 21.9 | 16.6 | 3.3 | 244.7 | 8 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
37 | -840 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.9 | 16.6 | 2.7 | 237.7 | 8.2 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
38 | -839 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 3.3 | 235.9 | 8.5 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
39 | -838 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 3.4 | 232.3 | 11.6 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
40 | -837 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.8 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 3 | 253.5 | 11.1 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
41 | -836 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 2.8 | 235.4 | 9.7 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
42 | -835 | -6.1 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 3.2 | 247.1 | 10.1 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
43 | -834 | -5.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 3.3 | 225.2 | 12.2 | 16.6 | 16 | 16.1 | 16.8 | 15.9 | 16 | 17.7
44 | -833 | -5.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.2 | 21.8 | 16.6 | 2.6 | 227.4 | 10.8 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
45 | -832 | -6.1 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3 | 245.9 | 9.6 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
46 | -831 | -6.4 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3.6 | 246.8 | 9.8 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
47 | -830 | -6.5 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 4.1 | 227.6 | 8.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
48 | -829 | -6.3 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3.7 | 242.3 | 9.2 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
49 | -828 | -6.6 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3.5 | 246.5 | 10.7 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
50 | -827 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 3.6 | 246.7 | 12 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
51 | -826 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 2.7 | 239 | 12.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
52 | -825 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 2.2 | 240.9 | 13.1 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
53 | -824 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.6 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 2.3 | 238.4 | 13.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
54 | -823 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 2.3 | 243.3 | 14.3 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
55 | -822 | -6.8 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 2.5 | 243.8 | 13.5 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
56 | -821 | -6.7 | 0 | 0 | 17.6 | 17.8 | 17.7 | 17.4 | 18.4 | 16.3 | 21.8 | 16.6 | 2.4 | 241.5 | 13.1 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
57 | -820 | -6.5 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.5 | 18.4 | 16.3 | 21.8 | 16.6 | 2 | 247.7 | 12.5 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
58 | -819 | -6.1 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.5 | 18.4 | 16.3 | 21.8 | 16.6 | 1.7 | 253.2 | 11.3 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
59 | -818 | -6.5 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.5 | 18.4 | 16.3 | 21.8 | 16.6 | 1.7 | 253 | 11.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 16 | 17.7
60 | -817 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.5 | 18.4 | 16.3 | 21.8 | 16.6 | 2 | 253.2 | 11 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
61 | -816 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.7 | 17.5 | 18.4 | 16.3 | 21.8 | 16.6 | 1.8 | 251.3 | 10.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
62 | -815 | -6.4 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.5 | 18.4 | 16.3 | 21.8 | 16.6 | 1.8 | 248 | 10.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
63 | -814 | -6.5 | 0 | 0 | 17.5 | 17.8 | 17.7 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 1.7 | 245.3 | 10.1 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
64 | -813 | -6.7 | 0 | 0 | 17.4 | 17.9 | 17.8 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 1.9 | 256.2 | 10.8 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
65 | -812 | -6.6 | 0 | 0 | 17.4 | 17.9 | 17.8 | 17.5 | 18.4 | 16.4 | 21.9 | 16.6 | 1.8 | 253.5 | 11.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
66 | -811 | -6.7 | 0 | 0 | 17.4 | 17.9 | 17.8 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2 | 255.8 | 11.3 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
67 | -810 | -6.8 | 0 | 0 | 17.4 | 17.9 | 17.8 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 1.8 | 269.6 | 10.9 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
68 | -809 | -6.7 | 0 | 0 | 17.3 | 17.9 | 17.8 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 1.8 | 267.4 | 10.2 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
69 | -808 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.7 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 2.2 | 259.8 | 11 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
70 | -807 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.7 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 2.2 | 270.6 | 11.2 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
71 | -806 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.7 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 2 | 256.5 | 10.6 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
72 | -805 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.7 | 17.4 | 18.4 | 16.4 | 21.8 | 16.6 | 1.9 | 257.3 | 10.2 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
73 | -804 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.6 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2 | 251.6 | 10.5 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
74 | -803 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.6 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2 | 248.1 | 10.8 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
75 | -802 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 255.6 | 11.1 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
76 | -801 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 2 | 262.2 | 10.3 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
77 | -800 | -6.6 | 0 | 0 | 17.3 | 17.8 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 244.6 | 9.1 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
78 | -799 | -6 | 0 | 0 | 17.3 | 17.8 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 259.4 | 7.4 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
79 | -798 | -6 | 0 | 0 | 17.3 | 17.8 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 2 | 255 | 6.3 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
80 | -797 | -6.3 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 1.8 | 263.5 | 7.1 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
81 | -796 | -6.4 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 269.5 | 7.7 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
82 | -795 | -6.5 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 1.8 | 260.2 | 8.7 | 16.6 | 16 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
83 | -794 | -6.7 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 1.8 | 252.4 | 9.3 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
84 | -793 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.5 | 1.9 | 260.9 | 8 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
85 | -792 | -6.6 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 1.7 | 259.7 | 7.1 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
86 | -791 | -6.3 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 1.6 | 261.7 | 7.4 | 16.6 | 16.1 | 16.1 | 16.8 | 15.9 | 15.9 | 17.7
87 | -790 | -6.7 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.9 | 16.5 | 1.6 | 242.3 | 7.8 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
88 | -789 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.9 | 16.5 | 1.6 | 257.7 | 7.1 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
89 | -788 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.9 | 16.5 | 2 | 254.3 | 8 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
90 | -787 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.9 | 16.5 | 1.6 | 255.1 | 8.6 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
91 | -786 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.8 | 16.5 | 1.7 | 255.9 | 9.1 | 16.6 | 16.1 | 16.1 | 16.8 | 15.8 | 15.9 | 17.7
92 | -785 | -6.8 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.8 | 16.5 | 1.7 | 244.8 | 8.4 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
93 | -784 | -6.2 | 0 | 0 | 17.4 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.8 | 16.5 | 1.7 | 259.4 | 8.6 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
94 | -783 | -6.7 | 0 | 0 | 17.5 | 17.8 | 17.5 | 17.6 | 18.4 | 16.5 | 21.9 | 16.5 | 1.8 | 248.4 | 8.3 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
95 | -782 | -6.8 | 0 | 0 | 17.5 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.5 | 1.7 | 256.1 | 8.6 | 16.6 | 16.1 | 16 | 16.8 | 15.8 | 15.9 | 17.7
96 | -781 | -6.8 | 0 | 0 | 17.4 | 17.9 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.5 | 1.9 | 251.4 | 7.9 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
97 | -780 | -6.5 | 0 | 0 | 17.4 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.5 | 2 | 247.5 | 7 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
98 | -779 | -6.7 | 0 | 0 | 17.4 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.2 | 277.9 | 6.3 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
99 | -778 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.2 | 270.9 | 6 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
100 | -777 | -6.4 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.4 | 250.3 | 7 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
101 | -776 | -6.3 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.3 | 257.8 | 8 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
102 | -775 | -6.4 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2.2 | 261.7 | 8.3 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
103 | -774 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2 | 261.4 | 8.3 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
104 | -773 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2 | 258.7 | 8.9 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
105 | -772 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 243.9 | 9.7 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
106 | -771 | -6.5 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 251 | 9.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
107 | -770 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.5 | 18.4 | 16.5 | 21.9 | 16.6 | 2 | 235.9 | 8.8 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
108 | -769 | -6.6 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 2.1 | 236.4 | 8.1 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
109 | -768 | -6.6 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.4 | 18.4 | 16.5 | 21.9 | 16.6 | 1.9 | 249.1 | 6.9 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
110 | -767 | -6.5 | 0 | 0 | 17.1 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 254.4 | 7 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
111 | -766 | -6.1 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.9 | 240.5 | 6.8 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
112 | -765 | -6.4 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 241.1 | 6.5 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
113 | -764 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.8 | 249.8 | 6.6 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
114 | -763 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.6 | 254.1 | 6.6 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
115 | -762 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.6 | 249.7 | 7 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
116 | -761 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.6 | 243.3 | 6.9 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
117 | -760 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.5 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.9 | 247.1 | 7.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
118 | -759 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.9 | 246.6 | 8.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
119 | -758 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.9 | 264.5 | 9.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
120 | -757 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 258.1 | 9 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
121 | -756 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.7 | 259.6 | 9.4 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
122 | -755 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.7 | 259.1 | 10.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
123 | -754 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.7 | 259.9 | 9.5 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
124 | -753 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.7 | 264.1 | 9.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
125 | -752 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.5 | 248.6 | 9.2 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
126 | -751 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.6 | 263.8 | 8.5 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
127 | -750 | -6.7 | 0 | 0 | 17.1 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.8 | 226.3 | 7.8 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
128 | -749 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 1.9 | 246.3 | 7.9 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
129 | -748 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 232.1 | 8.6 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
130 | -747 | -6.7 | 0 | 0 | 17.2 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 248.6 | 8.7 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.9 | 17.7
131 | -746 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2.1 | 236.7 | 9.1 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
132 | -745 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2.2 | 244.3 | 9.3 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
133 | -744 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 1.9 | 257 | 8.3 | 16.6 | 16 | 16 | 16.8 | 15.8 | 15.8 | 17.7
134 | -743 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.2 | 257.9 | 7.4 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
135 | -742 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.3 | 251.8 | 7.9 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
136 | -741 | -6.6 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.7 | 244.4 | 7.5 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
137 | -740 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 239.4 | 7.1 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
138 | -739 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.5 | 236.3 | 6.7 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
139 | -738 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 264.5 | 5.6 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
140 | -737 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.4 | 264.6 | 4.9 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
141 | -736 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 3 | 244.3 | 4.3 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
142 | -735 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 245.5 | 4.3 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
143 | -734 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 242.2 | 4.2 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
144 | -733 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.7 | 2.6 | 245.3 | 4.1 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
145 | -732 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.4 | 18.3 | 16.4 | 21.9 | 16.7 | 2.6 | 267.8 | 4.7 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
146 | -731 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.3 | 18.3 | 16.4 | 21.9 | 16.7 | 2.4 | 256.4 | 4.9 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
147 | -730 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.3 | 18.3 | 16.4 | 21.9 | 16.7 | 2.5 | 222.8 | 5.5 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
148 | -729 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.3 | 18.3 | 16.4 | 21.9 | 16.7 | 2.2 | 226.5 | 5.7 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
149 | -728 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.3 | 18.3 | 16.4 | 21.9 | 16.7 | 3.1 | 254.9 | 7.5 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
150 | -727 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.3 | 18.3 | 16.5 | 21.9 | 16.7 | 3.1 | 232.1 | 8.7 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
151 | -726 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.7 | 17.4 | 18.3 | 16.5 | 21.9 | 16.7 | 3.5 | 247.9 | 11.2 | 16.6 | 16 | 15.9 | 16.8 | 15.8 | 15.8 | 17.7
152 | -725 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.7 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 3.6 | 248.8 | 12 | 16.6 | 16 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
153 | -724 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.4 | 18.3 | 16.5 | 21.9 | 16.7 | 2.9 | 241.5 | 12.7 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
154 | -723 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.4 | 18.4 | 16.4 | 21.9 | 16.7 | 2.3 | 234.3 | 13.5 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
155 | -722 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.4 | 18.4 | 16.5 | 21.9 | 16.7 | 1.9 | 239.2 | 14.3 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
156 | -721 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.4 | 18.3 | 16.5 | 21.9 | 16.7 | 1.8 | 239.2 | 14 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
157 | -720 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.3 | 18.4 | 16.5 | 21.9 | 16.7 | 2 | 252.1 | 13.2 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
158 | -719 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.3 | 18.4 | 16.5 | 21.9 | 16.7 | 2.5 | 233.6 | 11.4 | 16.6 | 16 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
159 | -718 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.3 | 18.3 | 16.5 | 21.9 | 16.7 | 2.3 | 246 | 10.4 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
160 | -717 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.3 | 18.4 | 16.4 | 21.9 | 16.7 | 1.9 | 247.9 | 10.7 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
161 | -716 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.3 | 18.4 | 16.4 | 21.9 | 16.7 | 1.6 | 237.3 | 11.4 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
162 | -715 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.6 | 17.3 | 18.4 | 16.4 | 21.9 | 16.7 | 1.8 | 229.8 | 10.8 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
163 | -714 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.3 | 18.4 | 16.4 | 21.9 | 16.7 | 1.7 | 246.7 | 10.8 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
164 | -713 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 1.5 | 247.9 | 12.2 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
165 | -712 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 1.4 | 247.4 | 11.6 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
166 | -711 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 1.5 | 251.4 | 11.3 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
167 | -710 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 1.5 | 248.2 | 9.4 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
168 | -709 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 1.6 | 211.9 | 8.9 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
169 | -708 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 1.8 | 224.6 | 8.2 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
170 | -707 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 2 | 241.3 | 7.6 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
171 | -706 | -6.7 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 2.4 | 245.2 | 7.2 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
172 | -705 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 2.9 | 245.9 | 6.8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
173 | -704 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 3.1 | 244.4 | 7.4 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
174 | -703 | -6.7 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.4 | 16.4 | 21.9 | 16.7 | 3.1 | 229.2 | 7.3 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
175 | -702 | -6.5 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.3 | 18.4 | 16.4 | 21.9 | 16.6 | 2.7 | 251.9 | 6.8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
176 | -701 | -6.6 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.3 | 18.4 | 16.4 | 21.9 | 16.6 | 3 | 252 | 6.6 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
177 | -700 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.3 | 18.4 | 16.4 | 21.9 | 16.6 | 3.4 | 243.3 | 9.1 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
178 | -699 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.3 | 18.4 | 16.4 | 21.9 | 16.6 | 3.6 | 236.6 | 11.4 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
179 | -698 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 3.3 | 241.1 | 12.6 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
180 | -697 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2.6 | 249.1 | 12.9 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
181 | -696 | -6.5 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2.4 | 237.6 | 12.4 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
182 | -695 | -6.1 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2.5 | 232.6 | 11.7 | 16.6 | 15.9 | 15.9 | 16.8 | 15.7 | 15.8 | 17.7
183 | -694 | -6.4 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.4 | 18.4 | 16.4 | 21.9 | 16.7 | 2.5 | 241.6 | 10.4 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
184 | -693 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.4 | 18.4 | 16.4 | 21.9 | 16.7 | 2.9 | 243 | 12.2 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
185 | -692 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.6 | 250.6 | 13.6 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
186 | -691 | -6.6 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.4 | 18.4 | 16.4 | 21.9 | 16.6 | 2.5 | 250.1 | 14.1 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
187 | -690 | -6.5 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.8 | 248.4 | 14.1 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
188 | -689 | -6.2 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 1.8 | 270.5 | 12.1 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
189 | -688 | -6.4 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 231 | 9.5 | 16.6 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
190 | -687 | -6.5 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 243.3 | 8.7 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
191 | -686 | -6.7 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 3.4 | 244.8 | 11.9 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
192 | -685 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 3.7 | 250.4 | 12.7 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
193 | -684 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 3.7 | 262.9 | 12.9 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
194 | -683 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 3.2 | 253.8 | 12.9 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
195 | -682 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.5 | 261.3 | 13 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
196 | -681 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.5 | 252.7 | 11.8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
197 | -680 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 262.8 | 11.1 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
198 | -679 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 3.3 | 259.9 | 10.4 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
199 | -678 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.8 | 253.1 | 9.1 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
200 | -677 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 251.4 | 8.6 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
201 | -676 | -5.9 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2 | 254.1 | 8.2 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
202 | -675 | -3.2 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 240.3 | 7.7 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
203 | -674 | -2.4 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 2.2 | 270.3 | 7.2 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
204 | -673 | -3.9 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 2.1 | 237.8 | 8.4 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
205 | -672 | -5.6 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 2.3 | 243.4 | 7.8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
206 | -671 | -6.4 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 2.2 | 236.9 | 7.8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
207 | -670 | -6.7 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 1.7 | 243.9 | 10 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
208 | -669 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 1.9 | 234.3 | 11.6 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
209 | -668 | -6.4 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2.2 | 237.5 | 11.1 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.9 | 17.7
210 | -667 | -5.3 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2.2 | 227.2 | 10 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.9 | 17.7
211 | -666 | -5.1 | 0 | 0 | 17.1 | 17.8 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.6 | 212.5 | 8.8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.9 | 17.7
212 | -665 | -5.6 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.6 | 220.9 | 8 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
213 | -664 | -6 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 1.4 | 248.7 | 7 | 16.6 | 15.9 | 15.9 | 16.7 | 15.7 | 15.9 | 17.7
214 | -663 | -6.6 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 1.4 | 228.3 | 6.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
215 | -662 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2 | 233.1 | 7.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
216 | -661 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.4 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 224.7 | 8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
217 | -660 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 3.1 | 196.8 | 7.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
218 | -659 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 3.3 | 213.2 | 7.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
219 | -658 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2.9 | 183.2 | 6.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
220 | -657 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2.4 | 211.2 | 5.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
221 | -656 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2.3 | 236.8 | 5.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
222 | -655 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2 | 212.2 | 5.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
223 | -654 | -6.8 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.8 | 229.4 | 5.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
224 | -653 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.8 | 245.2 | 4.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
225 | -652 | -6.5 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.9 | 254.8 | 6.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
226 | -651 | -6.1 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.7 | 242.1 | 6.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
227 | -650 | -6.1 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.5 | 175.3 | 5.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
228 | -649 | -6.3 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.6 | 203.7 | 4.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
229 | -648 | -6.1 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2 | 220.9 | 6.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
230 | -647 | -6.4 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2.6 | 201.5 | 8.2 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
231 | -646 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 2.6 | 205.9 | 9.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
232 | -645 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.3 | 18.3 | 16.3 | 21.9 | 16.7 | 2.7 | 210.3 | 10.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
233 | -644 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.3 | 18.3 | 16.3 | 21.9 | 16.7 | 2.6 | 217 | 11.2 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
234 | -643 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 2.3 | 220.1 | 11.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
235 | -642 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.3 | 18.3 | 16.3 | 21.9 | 16.7 | 2.4 | 226.4 | 9.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
236 | -641 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.7 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.6 | 254.8 | 7.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
237 | -640 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.7 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.6 | 255.7 | 7.2 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
238 | -639 | -6.5 | 0 | 0 | 17.3 | 17.7 | 17.7 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 251.2 | 8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
239 | -638 | -6.3 | 0 | 0 | 17.3 | 17.7 | 17.7 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.5 | 243.9 | 10.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
240 | -637 | -6.5 | 0 | 0 | 17.3 | 17.7 | 17.7 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 245.6 | 11.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
241 | -636 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.1 | 244.7 | 11.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
242 | -635 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 1.9 | 233.3 | 11.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
243 | -634 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.6 | 241 | 11 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
244 | -633 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 1.6 | 238 | 10.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
245 | -632 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.4 | 232.2 | 9.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
246 | -631 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.6 | 239.4 | 9.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
247 | -630 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.7 | 241.6 | 9.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
248 | -629 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.7 | 248.6 | 8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
249 | -628 | -6.6 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.7 | 1.8 | 230.8 | 7.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
250 | -627 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.5 | 221.1 | 7.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
251 | -626 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.7 | 1.5 | 208 | 6.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
252 | -625 | -6.1 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.7 | 1.6 | 244.3 | 5.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
253 | -624 | -6.1 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.8 | 246.7 | 5.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
254 | -623 | -6.5 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.9 | 246.8 | 4.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
255 | -622 | -6.1 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 2.1 | 205 | 5.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
256 | -621 | -6 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.9 | 186.2 | 6.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
257 | -620 | -5.8 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.6 | 240.9 | 6.4 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
258 | -619 | -6 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.4 | 222.6 | 7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
259 | -618 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.4 | 221.9 | 9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
260 | -617 | -6.7 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.5 | 209.2 | 9.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
261 | -616 | -6.2 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.1 | 18.3 | 16.4 | 21.9 | 16.7 | 1.8 | 212.3 | 9.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
262 | -615 | -6.1 | 0 | 0 | 17.3 | 17.8 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 1.8 | 212.7 | 8.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
263 | -614 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.4 | 16.3 | 21.9 | 16.6 | 1.8 | 221.3 | 8.2 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
264 | -613 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.4 | 16.3 | 21.9 | 16.6 | 1.8 | 225.1 | 7.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
265 | -612 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.4 | 16.3 | 21.9 | 16.6 | 1.6 | 222.9 | 6.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
266 | -611 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.4 | 16.3 | 21.9 | 16.6 | 1.7 | 215.6 | 6.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
267 | -610 | -6.4 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.3 | 18.4 | 16.3 | 21.9 | 16.6 | 1.6 | 224.2 | 6.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
268 | -609 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 237.9 | 6.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
269 | -608 | -6.3 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.3 | 18.4 | 16.3 | 21.9 | 16.7 | 1.7 | 259.5 | 5.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
270 | -607 | -5 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.3 | 18.3 | 16.3 | 21.9 | 16.7 | 1.6 | 271.4 | 4.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
271 | -606 | -5.2 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 1.7 | 220 | 3.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
272 | -605 | -6.1 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.4 | 18.3 | 16.3 | 21.9 | 16.7 | 1.5 | 206.4 | 4.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
273 | -604 | -3.8 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 1.4 | 251.3 | 4.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
274 | -603 | -2.9 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 1.6 | 280.9 | 4.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
275 | -602 | -4.5 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 1.6 | 244.2 | 3.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
276 | -601 | -5.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 1.6 | 208.3 | 4 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
277 | -600 | -5.6 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 1.5 | 225.9 | 4.4 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
278 | -599 | -6.4 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.4 | 241.3 | 4.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
279 | -598 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 1.4 | 249 | 5.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
280 | -597 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 1.5 | 246.2 | 6.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
281 | -596 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 245.7 | 7.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
282 | -595 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 248 | 8.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
283 | -594 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 1.6 | 248.4 | 7.7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
284 | -593 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 1.9 | 257.6 | 6.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
285 | -592 | -6 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.1 | 262.3 | 6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
286 | -591 | -6.1 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.1 | 257.8 | 5.4 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
287 | -590 | -6.3 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2 | 254.3 | 4.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
288 | -589 | -6.4 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.1 | 247.9 | 4.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
289 | -588 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 250.1 | 4.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
290 | -587 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.4 | 249.4 | 4.6 | 16.5 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
291 | -586 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 241 | 4.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
292 | -585 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.5 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 234.5 | 5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
293 | -584 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.9 | 257.5 | 5.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
294 | -583 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.9 | 263.9 | 6.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
295 | -582 | -5.8 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.8 | 256.8 | 7.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
296 | -581 | -5.3 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 256.5 | 8.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
297 | -580 | -5.5 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 248.5 | 7.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
298 | -579 | -5.9 | 0 | 0 | 17.3 | 17.6 | 17.5 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 261.5 | 6.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
299 | -578 | -5.5 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.7 | 267 | 5.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
300 | -577 | -6.3 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 1.9 | 259.2 | 4.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
301 | -576 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.1 | 253.9 | 4.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
302 | -575 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.4 | 252.1 | 5.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
303 | -574 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.8 | 221.7 | 4.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
304 | -573 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.6 | 238.3 | 4.2 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
305 | -572 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 278.1 | 5.9 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
306 | -571 | -6.2 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.4 | 253.3 | 6.8 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
307 | -570 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 246.4 | 7.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
308 | -569 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.1 | 241.4 | 7.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
309 | -568 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.4 | 18.3 | 16.5 | 21.9 | 16.6 | 2.1 | 235.8 | 9.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
310 | -567 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2.2 | 241.1 | 9.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
311 | -566 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 243.1 | 8.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
312 | -565 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.5 | 21.9 | 16.6 | 2 | 256.4 | 7.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
313 | -564 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2 | 248.2 | 7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
314 | -563 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 238 | 6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
315 | -562 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2.5 | 239.3 | 6.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
316 | -561 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 243.4 | 7.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
317 | -560 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 3.7 | 246.6 | 6.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
318 | -559 | -6.1 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 4.2 | 262.7 | 5.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
319 | -558 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 3.7 | 271.2 | 5.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
320 | -557 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 3.1 | 253.3 | 7.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
321 | -556 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 248.8 | 10.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
322 | -555 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 3.3 | 239.5 | 11.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
323 | -554 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 3.4 | 242.9 | 11.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
324 | -553 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 3.1 | 242.1 | 12.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
325 | -552 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 3.4 | 239.7 | 13.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
326 | -551 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 3.1 | 235.6 | 12.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
327 | -550 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.9 | 241.5 | 11.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
328 | -549 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.2 | 243.9 | 12.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
329 | -548 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.5 | 245.9 | 13.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
330 | -547 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 237.1 | 12.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
331 | -546 | -5.8 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.2 | 256.8 | 11 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
332 | -545 | -5.9 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.3 | 276.9 | 10.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
333 | -544 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.7 | 265.4 | 12.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
334 | -543 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 4 | 269 | 12.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
335 | -542 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 4.1 | 256.2 | 10.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
336 | -541 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3.4 | 274.9 | 11.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
337 | -540 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3 | 255.1 | 11.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
338 | -539 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.8 | 253.5 | 11.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
339 | -538 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.8 | 253.8 | 11.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
340 | -537 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3.1 | 250.9 | 10 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
341 | -536 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3.3 | 266.9 | 9.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
342 | -535 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3.5 | 259.4 | 12 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
343 | -534 | -6.6 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3.5 | 254.9 | 14.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
344 | -533 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 4.5 | 255.8 | 15.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
345 | -532 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 4.4 | 261.4 | 15.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
346 | -531 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 4.2 | 254.9 | 14.7 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
347 | -530 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 3.3 | 256.9 | 14 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
348 | -529 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.8 | 258.2 | 13.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
349 | -528 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.7 | 256.6 | 13.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
350 | -527 | -6.2 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.5 | 249.5 | 13.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
351 | -526 | -5.9 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 249.8 | 12.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
352 | -525 | -6 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.3 | 246.4 | 13.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
353 | -524 | -6.2 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.7 | 254.1 | 13.2 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
354 | -523 | -6.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.3 | 261.4 | 12.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
355 | -522 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.9 | 258.9 | 12.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
356 | -521 | -6.4 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2.1 | 263.1 | 11.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
357 | -520 | -5.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2 | 262.1 | 10 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
358 | -519 | -5.2 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 1.8 | 241.2 | 10.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
359 | -518 | -5.7 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.7 | 1.5 | 258.8 | 11.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
360 | -517 | -6.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.2 | 18.3 | 16.2 | 21.9 | 16.7 | 1.4 | 253.7 | 12.7 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
361 | -516 | -6.4 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 1.6 | 245.7 | 11.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
362 | -515 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 1.7 | 251.4 | 9.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
363 | -514 | -6.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 1.9 | 248.3 | 8.3 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
364 | -513 | -6.4 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 1.9 | 268.5 | 7.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
365 | -512 | -5.9 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2 | 259.1 | 6.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
366 | -511 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 2.3 | 240.6 | 6.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
367 | -510 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.9 | 239.7 | 6.1 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
368 | -509 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.7 | 246 | 6.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
369 | -508 | -6.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.6 | 272.9 | 6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
370 | -507 | -5.7 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.4 | 248.6 | 5.4 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
371 | -506 | -5.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.7 | 268.3 | 5.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
372 | -505 | -5.3 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.5 | 244.5 | 5.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
373 | -504 | -5.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.7 | 246.2 | 6.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
374 | -503 | -5.4 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.1 | 244.2 | 6.7 | 16.5 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
375 | -502 | -5.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.1 | 18.3 | 16.2 | 21.9 | 16.6 | 2.3 | 242.2 | 7 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
376 | -501 | -5.4 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 2.2 | 248.4 | 8.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
377 | -500 | -6.2 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 2.1 | 259.2 | 10.2 | 16.5 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
378 | -499 | -6.5 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 2.5 | 243.1 | 10.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
379 | -498 | -5.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 4.1 | 249.8 | 10.5 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
380 | -497 | -5.7 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 6 | 266.7 | 9.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
381 | -496 | -6.1 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 5.7 | 271.2 | 7.3 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
382 | -495 | -6.5 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 4.2 | 239.9 | 6.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
383 | -494 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 3.7 | 230.2 | 8.1 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
384 | -493 | -6.8 | 0 | 0 | 17.2 | 17.8 | 17.5 | 17.1 | 18.3 | 16.3 | 21.9 | 16.6 | 3.1 | 243 | 10.6 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
385 | -492 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.5 | 257.7 | 11.2 | 16.6 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
386 | -491 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 3.4 | 239.6 | 12.8 | 16.5 | 16 | 16 | 16.7 | 15.8 | 15.9 | 17.7
387 | -490 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.9 | 227.3 | 12.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
388 | -489 | -6.6 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.6 | 253.9 | 12.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
389 | -488 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.8 | 231.6 | 14.8 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
390 | -487 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.1 | 238.4 | 14.6 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
391 | -486 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 241.5 | 14.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
392 | -485 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 248.9 | 12.9 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.9 | 17.7
393 | -484 | -6.5 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 3.3 | 250.1 | 11.9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
394 | -483 | -6.1 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 3.6 | 235.3 | 11.4 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
395 | -482 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 3.2 | 241.6 | 11.6 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
396 | -481 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.5 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 2.9 | 237.3 | 12.5 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
397 | -480 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 2.2 | 237.6 | 13.4 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
398 | -479 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2.1 | 247.9 | 14.1 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
399 | -478 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2.1 | 251 | 13.6 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
400 | -477 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2.4 | 260.9 | 13.8 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.6
401 | -476 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 2.6 | 268.8 | 13.7 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
402 | -475 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 2.9 | 254.2 | 13.2 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
403 | -474 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 3 | 242.1 | 11.5 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
404 | -473 | -6.3 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 2.6 | 237.8 | 9 | 16.6 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
405 | -472 | -5.7 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 2.3 | 252.4 | 9.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
406 | -471 | -6.4 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 2.3 | 253.3 | 12 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
407 | -470 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 2.2 | 261.6 | 14.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
408 | -469 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.5 | 2.2 | 239.8 | 13.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
409 | -468 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.5 | 2.5 | 241.8 | 12.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
410 | -467 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.6 | 2.6 | 258.4 | 10.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
411 | -466 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.2 | 21.9 | 16.5 | 2.8 | 245.7 | 10.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
412 | -465 | -6.2 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.5 | 3.4 | 254.4 | 10.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
413 | -464 | -6.4 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.3 | 18.3 | 16.3 | 21.9 | 16.5 | 3.7 | 262.1 | 11.8 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.7
414 | -463 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.3 | 18.3 | 16.3 | 21.9 | 16.5 | 3.7 | 256 | 11.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
415 | -462 | -5.3 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.3 | 18.3 | 16.3 | 21.9 | 16.5 | 3.1 | 260.4 | 10.5 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
416 | -461 | -4.9 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.5 | 3 | 241.6 | 9.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
417 | -460 | -5.2 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.5 | 3.1 | 256.1 | 10.5 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
418 | -459 | -5.7 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.3 | 18.3 | 16.3 | 21.9 | 16.5 | 3.7 | 262.5 | 14.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
419 | -458 | -6 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 4.1 | 249.3 | 15.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
420 | -457 | -6.6 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 4.2 | 250.1 | 15.2 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
421 | -456 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 3.4 | 243.2 | 14.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
422 | -455 | -6.4 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 4.3 | 255.8 | 13.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
423 | -454 | -6 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 4.3 | 242.9 | 16 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
424 | -453 | -5.1 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 4 | 247.2 | 16.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
425 | -452 | -5.5 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.4 | 21.9 | 16.6 | 4.1 | 266 | 15.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
426 | -451 | -6.2 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 4.8 | 274.7 | 14 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
427 | -450 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 4 | 227.7 | 12.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
428 | -449 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3 | 256.2 | 11.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
429 | -448 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.1 | 241.9 | 10.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
430 | -447 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.5 | 261.5 | 13 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
431 | -446 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 4.4 | 263 | 15.5 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
432 | -445 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 4.6 | 246.7 | 14.8 | 16.5 | 16 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
433 | -444 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 4.5 | 250.6 | 16.4 | 16.5 | 16 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
434 | -443 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 5.3 | 260.4 | 15.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
435 | -442 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 6 | 260.2 | 13.9 | 16.5 | 16 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
436 | -441 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 6.9 | 249.7 | 14.2 | 16.5 | 16 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
437 | -440 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 6.3 | 239.9 | 14.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
438 | -439 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 6.8 | 240.6 | 13.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
439 | -438 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 5.5 | 258.1 | 16.5 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
440 | -437 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 4.4 | 253.6 | 20.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
441 | -436 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 6.1 | 239.9 | 20.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
442 | -435 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 7.7 | 250 | 18.1 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
443 | -434 | -5.2 | 0 | 0 | 17.2 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 6.3 | 244.1 | 15.6 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
444 | -433 | -2.7 | 0 | 0 | 17.1 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 4.4 | 250.9 | 15.8 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
445 | -432 | -3.9 | 0 | 0 | 17.1 | 17.7 | 17.4 | 17.3 | 18.3 | 16.3 | 21.9 | 16.6 | 4.8 | 239.7 | 17 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
446 | -431 | -4.8 | 0 | 0 | 17.1 | 17.7 | 17.4 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.5 | 242.9 | 17.9 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
447 | -430 | -5.5 | 0 | 0 | 17.1 | 17.7 | 17.4 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.3 | 241.7 | 17.9 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
448 | -429 | -5 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 2.9 | 235.3 | 14.3 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
449 | -428 | -5.8 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 2.9 | 283 | 10.8 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
450 | -427 | -6.2 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 2.6 | 220.8 | 8.5 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
451 | -426 | -5.8 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3 | 254 | 8.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
452 | -425 | -5.5 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.1 | 255.9 | 9.7 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
453 | -424 | -5.1 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 2.7 | 267.2 | 10.8 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
454 | -423 | -4.8 | 0 | 0 | 17.1 | 17.7 | 17.3 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 2.9 | 261.3 | 11.2 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
455 | -422 | -4.8 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 2.7 | 257.6 | 11.8 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
456 | -421 | -6 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 2.6 | 250.6 | 11.9 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.7 | 17.6
457 | -420 | -6.6 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 2.2 | 249.7 | 13.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
458 | -419 | -6.4 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 1.8 | 255 | 13.4 | 16.5 | 15.9 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
459 | -418 | -6.8 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 1.7 | 244.4 | 12.7 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
460 | -417 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 2.4 | 243.3 | 11.9 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
461 | -416 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 3.6 | 258.7 | 11.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
462 | -415 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 4.4 | 263.6 | 12.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
463 | -414 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 4.2 | 255.5 | 12.5 | 16.5 | 16 | 15.8 | 16.7 | 15.7 | 15.8 | 17.6
464 | -413 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 3.1 | 249.1 | 14.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
465 | -412 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.2 | 21.9 | 16.6 | 3.4 | 268.8 | 12.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.7
466 | -411 | -6.8 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.5 | 18.3 | 16.3 | 21.9 | 16.6 | 3.3 | 256.2 | 11.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
467 | -410 | -6.5 | 0 | 0 | 17.1 | 17.8 | 17.2 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.3 | 245 | 13.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
468 | -409 | -6.7 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.4 | 251.1 | 15.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
469 | -408 | -6.8 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 4.1 | 254 | 15.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
470 | -407 | -6.6 | 0 | 0 | 17 | 17.7 | 17.2 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.9 | 265.6 | 17.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
471 | -406 | -6.7 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.9 | 259.9 | 17.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
472 | -405 | -6.7 | 0 | 0 | 17 | 17.7 | 17.2 | 17.4 | 18.3 | 16.3 | 21.9 | 16.6 | 3.6 | 248.6 | 18.4 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
473 | -404 | -6.5 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 3.5 | 237.6 | 16.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
474 | -403 | -6.7 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 4 | 237.5 | 14.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
475 | -402 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 4.4 | 235.9 | 12.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
476 | -401 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 3.6 | 253.8 | 12 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
477 | -400 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 3 | 249.3 | 10.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
478 | -399 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.9 | 246.9 | 11.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
479 | -398 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 2.6 | 239.5 | 14.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
480 | -397 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 3.2 | 230.3 | 12.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
481 | -396 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 3.5 | 240.5 | 9.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
482 | -395 | -6.8 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 4 | 224.6 | 7.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
483 | -394 | -6.6 | 0 | 0 | 17 | 17.7 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 3.7 | 218.7 | 7.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
484 | -393 | -5.7 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 3.1 | 246.8 | 8.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
485 | -392 | -5.8 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 3.5 | 245.8 | 10.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
486 | -391 | -6.6 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.8 | 245.3 | 11.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
487 | -390 | -6.8 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 2.3 | 243.2 | 12.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
488 | -389 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.2 | 21.9 | 16.6 | 2.5 | 255.1 | 13.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
489 | -388 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 3.1 | 244.8 | 12 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
490 | -387 | -5.9 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 3.2 | 236.6 | 9.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
491 | -386 | -5.1 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.3 | 16.2 | 21.9 | 16.6 | 4.5 | 230.8 | 7.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
492 | -385 | -6 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 5.3 | 266.5 | 6.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
493 | -384 | -6.4 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 4.5 | 264.2 | 9.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
494 | -383 | -6.7 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 3.1 | 269 | 10.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
495 | -382 | -6.8 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 3 | 259.7 | 9.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
496 | -381 | -6.8 | 0 | 0 | 17 | 17.6 | 17.2 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 2.5 | 236.1 | 9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
497 | -380 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 2.6 | 228.3 | 12.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
498 | -379 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.3 | 16.1 | 21.9 | 16.6 | 3.4 | 229.9 | 13.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
499 | -378 | -6 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.1 | 21.9 | 16.6 | 4.3 | 235.5 | 11.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
500 | -377 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.1 | 21.9 | 16.6 | 4.5 | 274.5 | 11.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
501 | -376 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4.5 | 250.6 | 11.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
502 | -375 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4 | 246.3 | 13.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
503 | -374 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 3.2 | 234.2 | 13.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
504 | -373 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 2.7 | 263.4 | 11.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
505 | -372 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 3.2 | 246 | 13.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
506 | -371 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4.1 | 247.5 | 13.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
507 | -370 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4.4 | 261.8 | 12.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
508 | -369 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4.7 | 278.3 | 11.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
509 | -368 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4 | 257 | 10.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
510 | -367 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 3.9 | 244.2 | 11.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
511 | -366 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.4 | 248.1 | 11.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
512 | -365 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.4 | 248.2 | 12.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
513 | -364 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.2 | 245.8 | 10.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
514 | -363 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.7 | 253 | 9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
515 | -362 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.5 | 270.5 | 9.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
516 | -361 | -6.8 | 0 | 0 | 17.2 | 17.5 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.7 | 248 | 9.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
517 | -360 | -6.5 | 0 | 0 | 17.2 | 17.5 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 4.5 | 248.2 | 11 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
518 | -359 | -6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 4.7 | 246.7 | 11.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
519 | -358 | -5.9 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 4.1 | 217.6 | 9.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
520 | -357 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.2 | 21.9 | 16.6 | 3.6 | 242.8 | 7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
521 | -356 | -6.4 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 3.1 | 265.2 | 8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
522 | -355 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 240.6 | 9.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
523 | -354 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.7 | 245.7 | 9.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
524 | -353 | -6.4 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.1 | 239.9 | 7.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
525 | -352 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.1 | 255.7 | 8.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
526 | -351 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.1 | 247.6 | 8.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
527 | -350 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2 | 253.1 | 7.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
528 | -349 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 237.6 | 7.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
529 | -348 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.2 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 231.3 | 8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
530 | -347 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 242.4 | 7.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
531 | -346 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.8 | 230.2 | 6.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
532 | -345 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 1.9 | 220.4 | 5.6 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
533 | -344 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.2 | 217.2 | 5.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
534 | -343 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.5 | 222.6 | 4.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
535 | -342 | -6.5 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.5 | 247.3 | 4.4 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
536 | -341 | -6.2 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.5 | 215.3 | 4.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
537 | -340 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.5 | 216 | 5.2 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
538 | -339 | -6.8 | 0 | 0 | 17.3 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.6 | 220.6 | 7.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
539 | -338 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.3 | 21.9 | 16.6 | 2.7 | 213.5 | 8.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
540 | -337 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.7 | 205.2 | 9.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
541 | -336 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.3 | 207.4 | 8.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
542 | -335 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.2 | 223.4 | 7.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
543 | -334 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2.1 | 247.3 | 6.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
544 | -333 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.3 | 16.4 | 21.9 | 16.6 | 2 | 223.4 | 6.4 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
545 | -332 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 222.7 | 6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
546 | -331 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2 | 249.8 | 6.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
547 | -330 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.7 | 239.1 | 7.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
548 | -329 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 238.8 | 6.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
549 | -328 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.5 | 2.6 | 208.1 | 5.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
550 | -327 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.9 | 193.4 | 5.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
551 | -326 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.2 | 18.2 | 16.4 | 21.9 | 16.5 | 3.1 | 217.7 | 5.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
552 | -325 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.8 | 198.8 | 6.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
553 | -324 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.7 | 199.2 | 6.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
554 | -323 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 226.5 | 6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
555 | -322 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 3 | 248.5 | 6.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
556 | -321 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 246 | 7.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
557 | -320 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.4 | 233.7 | 7.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
558 | -319 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 233.6 | 5.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
559 | -318 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.3 | 251.7 | 5.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
560 | -317 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.3 | 256.2 | 7.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
561 | -316 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 240.2 | 8.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
562 | -315 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.1 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 230.8 | 8.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
563 | -314 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 245.1 | 7.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
564 | -313 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 227.2 | 6.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
565 | -312 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 254.9 | 7.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
566 | -311 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 239 | 7.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.9 | 17.6
567 | -310 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 243.1 | 7.4 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
568 | -309 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 1.6 | 248.1 | 7.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
569 | -308 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 233.5 | 7.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
570 | -307 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 232.7 | 7 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
571 | -306 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 233.3 | 7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
572 | -305 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 220.8 | 6.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
573 | -304 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.5 | 1.9 | 222.6 | 7.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
574 | -303 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.5 | 1.7 | 224.3 | 8.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
575 | -302 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.5 | 1.8 | 227.1 | 9.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
576 | -301 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.5 | 2.1 | 218.3 | 9.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
577 | -300 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.5 | 1.8 | 210.4 | 8.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
578 | -299 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 1.9 | 218.5 | 8.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
579 | -298 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 1.9 | 224.4 | 7.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
580 | -297 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 212 | 7.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
581 | -296 | -6.1 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 209.7 | 7.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
582 | -295 | -5.6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 221.1 | 7.6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
583 | -294 | -5.4 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 212 | 8.8 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
584 | -293 | -5.5 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2 | 221.8 | 9.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
585 | -292 | -6.1 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.3 | 210.3 | 9.5 | 16.5 | 15.9 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
586 | -291 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.5 | 208.1 | 9.6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
587 | -290 | -6.4 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.5 | 210.6 | 10.5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
588 | -289 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 206.1 | 10.5 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
589 | -288 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 202.3 | 10.3 | 16.5 | 15.9 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
590 | -287 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.4 | 226.6 | 9.3 | 16.5 | 15.9 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
591 | -286 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 215.2 | 8.3 | 16.5 | 15.9 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
592 | -285 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.3 | 209.2 | 9 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
593 | -284 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 226.3 | 8.6 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
594 | -283 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 232.3 | 6.7 | 16.5 | 15.9 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
595 | -282 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 246.4 | 5.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
596 | -281 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 250.5 | 6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
597 | -280 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 214.3 | 7.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
598 | -279 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2 | 220.8 | 7.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
599 | -278 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 229.7 | 7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
600 | -277 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 230.3 | 6.7 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
601 | -276 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 211.1 | 6.5 | 16.5 | 15.9 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
602 | -275 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 221.9 | 6.7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
603 | -274 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 262.4 | 6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
604 | -273 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 257.8 | 5.4 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
605 | -272 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.5 | 245.9 | 6.4 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
606 | -271 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.6 | 263.8 | 5.9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
607 | -270 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.5 | 234.7 | 5.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
608 | -269 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 260.3 | 7.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
609 | -268 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 255.7 | 8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
610 | -267 | -5.9 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 1.6 | 254.2 | 8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
611 | -266 | -5.2 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 258.7 | 7.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
612 | -265 | -5.9 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 1.8 | 257.5 | 8.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
613 | -264 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 1.8 | 259.5 | 10.4 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
614 | -263 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 1.8 | 260.3 | 11 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
615 | -262 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2 | 250.8 | 10.5 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
616 | -261 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 239.2 | 9.8 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
617 | -260 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 236.6 | 8.6 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
618 | -259 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 243.3 | 7.9 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
619 | -258 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.1 | 18.2 | 16.4 | 21.9 | 16.6 | 2.9 | 253 | 7.9 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
620 | -257 | -6.4 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 252.3 | 7.6 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
621 | -256 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 248 | 7.1 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
622 | -255 | -6.4 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 234.6 | 6.9 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
623 | -254 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 266.8 | 7.1 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
624 | -253 | -6.6 | 0 | 0 | 17.3 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 257.8 | 9.3 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
625 | -252 | -6.4 | 0 | 0 | 17.3 | 17.6 | 17.3 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 247 | 10.9 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
626 | -251 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 253.3 | 11.2 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
627 | -250 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 241.8 | 10.6 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
628 | -249 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.4 | 241.7 | 11.3 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
629 | -248 | -6.7 | 0 | 0 | 17.3 | 17.6 | 17.4 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 254.6 | 12.3 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
630 | -247 | -6.4 | 0 | 0 | 17.3 | 17.6 | 17.4 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.6 | 230.5 | 11.4 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.9 | 17.6
631 | -246 | -5.7 | 0 | 0 | 17.3 | 17.6 | 17.4 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.8 | 238.8 | 9.9 | 16.5 | 16 | 16 | 16.7 | 15.7 | 15.8 | 17.6
632 | -245 | -5.8 | 0 | 0 | 17.3 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 226.1 | 8.4 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.8 | 17.6
633 | -244 | -6.1 | 0 | 0 | 17.3 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 245.3 | 7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
634 | -243 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 241.4 | 9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
635 | -242 | -6.7 | 0 | 0 | 17.3 | 17.7 | 17.4 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 2.1 | 245.5 | 10.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
636 | -241 | -6.8 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 2.2 | 242.8 | 11 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
637 | -240 | -6.3 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.9 | 243.8 | 11.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
638 | -239 | -6.6 | 0 | 0 | 17.3 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.5 | 245.5 | 11.5 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
639 | -238 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.9 | 241.9 | 11.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
640 | -237 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.6 | 236.8 | 11.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
641 | -236 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.6 | 240.2 | 10 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
642 | -235 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.5 | 241 | 9 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
643 | -234 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.5 | 247.8 | 8.1 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.6
644 | -233 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.6 | 249.7 | 7.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
645 | -232 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.1 | 16.4 | 21.9 | 16.6 | 1.9 | 252.2 | 7 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
646 | -231 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.1 | 16.4 | 21.9 | 16.6 | 2 | 252 | 6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
647 | -230 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.1 | 16.4 | 21.9 | 16.6 | 2.1 | 263.9 | 5.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
648 | -229 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 258.1 | 5.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
649 | -228 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.4 | 251 | 5.3 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
650 | -227 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 1.8 | 243.6 | 5.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
651 | -226 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 219.7 | 5.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
652 | -225 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 210.3 | 5.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
653 | -224 | -6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 1.8 | 235.9 | 5.4 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
654 | -223 | -6.4 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 261.5 | 5.1 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
655 | -222 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 224.3 | 4.6 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
656 | -221 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 1.7 | 188.2 | 4.4 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.6
657 | -220 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2 | 231.4 | 4.2 | 16.5 | 16 | 15.9 | 16.7 | 15.7 | 15.8 | 17.6
658 | -219 | -6.3 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.1 | 234.9 | 4.6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
659 | -218 | -5.5 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.7 | 228.7 | 5 | 16.5 | 16 | 15.9 | 16.7 | 15.8 | 15.8 | 17.6
660 | -217 | -6.2 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.8 | 265.5 | 5.9 | 16.5 | 16 | 15.9 | 16.6 | 15.8 | 15.9 | 17.6
661 | -216 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.3 | 18.2 | 16.3 | 21.9 | 16.6 | 2.4 | 245 | 6.4 | 16.5 | 16 | 15.9 | 16.6 | 15.8 | 15.8 | 17.6
662 | -215 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 242.6 | 6.8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
663 | -214 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 239.5 | 7.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
664 | -213 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.1 | 239 | 6.5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
665 | -212 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 203.7 | 6.3 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
666 | -211 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.7 | 187.3 | 5.9 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
667 | -210 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 22 | 16.6 | 2.6 | 256.3 | 5.5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
668 | -209 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.3 | 258.8 | 6.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
669 | -208 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 1.6 | 221.9 | 6.2 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
670 | -207 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2 | 227.2 | 6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
671 | -206 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.6 | 230.8 | 5.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
672 | -205 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 3.1 | 176.4 | 5.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
673 | -204 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.7 | 206 | 4.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
674 | -203 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.3 | 21.9 | 16.6 | 2.6 | 228 | 5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
675 | -202 | -6.6 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 2.3 | 211 | 6.7 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
676 | -201 | -6.1 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 2.2 | 214.7 | 8.5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
677 | -200 | -6.5 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 2.1 | 221.1 | 8.8 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
678 | -199 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.3 | 17.2 | 18.2 | 16.2 | 21.9 | 16.7 | 2.1 | 232.5 | 9.3 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
679 | -198 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.7 | 2.3 | 235.7 | 8.8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
680 | -197 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 2.1 | 229.2 | 8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
681 | -196 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.2 | 16.2 | 21.9 | 16.6 | 1.9 | 229.1 | 7.6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
682 | -195 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2 | 232.4 | 7.1 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
683 | -194 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 248.4 | 6.4 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
684 | -193 | -6.1 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.5 | 239.1 | 6.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
685 | -192 | -6.4 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 215.9 | 6.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
686 | -191 | -6.4 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 221.3 | 5.7 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
687 | -190 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 231.3 | 5.8 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
688 | -189 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.5 | 242.9 | 7.4 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
689 | -188 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2.4 | 234.1 | 8.3 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
690 | -187 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2.1 | 210 | 8.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
691 | -186 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 1.9 | 230.9 | 7.5 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
692 | -185 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 1.9 | 224.4 | 6.6 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
693 | -184 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2.1 | 245 | 5.6 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
694 | -183 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2.2 | 246.4 | 5.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
695 | -182 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2.5 | 234.4 | 4.9 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
696 | -181 | -6.4 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.2 | 16.2 | 21.9 | 16.6 | 2.3 | 230.7 | 4.8 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
697 | -180 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.2 | 225.8 | 5.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
698 | -179 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 239 | 6.2 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
699 | -178 | -6.4 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 235.1 | 8.2 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
700 | -177 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2 | 250.2 | 7.9 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
701 | -176 | -6.3 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 245.8 | 7.4 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
702 | -175 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 235.5 | 6.9 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
703 | -174 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.9 | 248.7 | 6.9 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
704 | -173 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 22 | 16.6 | 1.7 | 243.5 | 6.9 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
705 | -172 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 22 | 16.6 | 1.5 | 251.5 | 7 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
706 | -171 | -6.4 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 22 | 16.6 | 1.6 | 249.2 | 6.9 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
707 | -170 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 222.1 | 6.4 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
708 | -169 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 251.4 | 6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
709 | -168 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 249.7 | 6.1 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
710 | -167 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.7 | 252.4 | 6.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
711 | -166 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 250.3 | 6.1 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
712 | -165 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 1.8 | 252.8 | 7 | 16.5 | 16 | 15.9 | 16.6 | 15.8 | 15.9 | 17.6
713 | -164 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.1 | 245 | 8.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
714 | -163 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.2 | 16.3 | 21.9 | 16.6 | 2.3 | 235.8 | 8.8 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
715 | -162 | -6.8 | 0 | 0 | 17 | 17.6 | 17.4 | 17.2 | 18.1 | 16.3 | 21.9 | 16.6 | 2 | 254 | 8.2 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
716 | -161 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 2.2 | 242.7 | 8.5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
717 | -160 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 2.2 | 241.2 | 9.6 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
718 | -159 | -6.8 | 0 | 0 | 17 | 17.6 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.9 | 241.6 | 8.8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
719 | -158 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.8 | 257.9 | 7.3 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.8 | 17.6
720 | -157 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.7 | 251.6 | 6.5 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
721 | -156 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.7 | 227.3 | 5.9 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
722 | -155 | -6.8 | 0 | 0 | 17 | 17.6 | 17.4 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.9 | 221.7 | 5.8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
723 | -154 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.4 | 21.9 | 16.6 | 2.3 | 207.8 | 7 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
724 | -153 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.4 | 21.9 | 16.6 | 2.1 | 207.3 | 7.8 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
725 | -152 | -6.2 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.4 | 21.9 | 16.6 | 1.7 | 220.5 | 7.2 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
726 | -151 | -6.3 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.4 | 21.9 | 16.6 | 1.5 | 214.5 | 7.1 | 16.5 | 16 | 15.9 | 16.6 | 15.7 | 15.9 | 17.6
727 | -150 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.4 | 21.9 | 16.6 | 1.4 | 235.9 | 6.9 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
728 | -149 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.4 | 21.9 | 16.6 | 1.6 | 224.1 | 7.4 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
729 | -148 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.3 | 21.9 | 16.6 | 1.8 | 227.1 | 7.8 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
730 | -147 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.3 | 21.9 | 16.6 | 2.6 | 233.7 | 7.8 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
731 | -146 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.3 | 21.9 | 16.6 | 2.7 | 204 | 8.1 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
732 | -145 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.3 | 22 | 16.7 | 2.3 | 213.2 | 8.4 | 16.5 | 16 | 16 | 16.6 | 15.7 | 15.9 | 17.6
733 | -144 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.1 | 18.1 | 16.3 | 21.9 | 16.7 | 1.6 | 205.9 | 7.6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
734 | -143 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.1 | 16.3 | 21.9 | 16.7 | 2 | 205.8 | 6.9 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
735 | -142 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.1 | 16.3 | 21.9 | 16.7 | 1.8 | 216.2 | 7.3 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
736 | -141 | -5.2 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.1 | 16.4 | 21.9 | 16.7 | 1.6 | 247.1 | 6.6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
737 | -140 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.1 | 16.3 | 21.9 | 16.7 | 1.3 | 249.4 | 5.6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
738 | -139 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.1 | 16.3 | 21.9 | 16.7 | 1.3 | 233.8 | 5.5 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
739 | -138 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.1 | 18.1 | 16.3 | 22 | 16.7 | 1.7 | 258.8 | 5.2 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
740 | -137 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.1 | 16.4 | 22 | 16.7 | 2.3 | 218.8 | 6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
741 | -136 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.1 | 16.4 | 22 | 16.7 | 3.2 | 215.8 | 6.6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
742 | -135 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.1 | 18.1 | 16.4 | 22 | 16.7 | 3.1 | 222.9 | 7.5 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
743 | -134 | -6.8 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 2.4 | 213.3 | 8 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
744 | -133 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.7 | 2.2 | 237 | 7.7 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
745 | -132 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.7 | 1.9 | 267.4 | 6.4 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
746 | -131 | -6.8 | 0 | 0 | 17.1 | 17.7 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.7 | 1.6 | 228.6 | 6.1 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
747 | -130 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.7 | 241.6 | 5.7 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
748 | -129 | -5.2 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.8 | 262.6 | 5 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
749 | -128 | -3.9 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.8 | 228.2 | 6.2 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
750 | -127 | -4.1 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 2.1 | 217 | 7.4 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
751 | -126 | -5 | 0 | 0 | 17.2 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 21.9 | 16.6 | 1.9 | 228 | 6.8 | 16.5 | 16 | 16 | 16.6 | 15.8 | 15.9 | 17.6
752 | -125 | -5.9 | 0 | 0 | 17.1 | 17.6 | 17.2 | 17.2 | 18.1 | 16.4 | 22 | 16.6 | 2 | 253.9 | 7.6 | 16.5 | 16 | 16 | 16.6 | 15.8 | 16 | 17.6
753 | -124 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.3 | 18.1 | 16.4 | 22 | 16.6 | 2 | 245.7 | 8 | 16.5 | 16 | 16 | 16.6 | 15.8 | 16 | 17.6
754 | -123 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.2 | 239.4 | 7.5 | 16.5 | 16 | 16 | 16.6 | 15.8 | 16 | 17.6
755 | -122 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.8 | 249.8 | 6.4 | 16.5 | 16 | 16 | 16.6 | 15.8 | 16 | 17.6
756 | -121 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 269 | 5.7 | 16.5 | 16 | 16 | 16.6 | 15.8 | 16 | 17.6
757 | -120 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.6 | 275.4 | 6.1 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
758 | -119 | -6.6 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.5 | 246.8 | 5.2 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
759 | -118 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.7 | 235.5 | 5.3 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
760 | -117 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.3 | 242.6 | 6 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
761 | -116 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.6 | 252.8 | 7.5 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
762 | -115 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.3 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.8 | 251.4 | 8.7 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
763 | -114 | -6.1 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 255.6 | 8.9 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
764 | -113 | -6.3 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.7 | 294.5 | 8.4 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
765 | -112 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 3 | 250.4 | 7 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
766 | -111 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.9 | 228.5 | 6.6 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
767 | -110 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 3.6 | 247.5 | 7.9 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
768 | -109 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 3.5 | 248.2 | 10.8 | 16.5 | 16 | 16.1 | 16.6 | 15.8 | 16 | 17.6
769 | -108 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.6 | 251.4 | 11.7 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
770 | -107 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.3 | 18.2 | 16.4 | 21.9 | 16.6 | 2.3 | 236.5 | 10.8 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
771 | -106 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.3 | 18.2 | 16.5 | 21.9 | 16.6 | 2.5 | 244.6 | 10 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
772 | -105 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.5 | 21.9 | 16.6 | 3 | 236.1 | 9.4 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
773 | -104 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.5 | 21.9 | 16.6 | 3.7 | 244.2 | 11.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
774 | -103 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.5 | 21.9 | 16.6 | 2.6 | 243.1 | 12.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
775 | -102 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.5 | 21.9 | 16.6 | 2.3 | 239.6 | 11.8 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
776 | -101 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.5 | 243.1 | 11.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
777 | -100 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 245.3 | 12.3 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
778 | -99 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.9 | 243.7 | 14.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
779 | -98 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 1.8 | 245.8 | 14.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
780 | -97 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.4 | 17.2 | 18.2 | 16.5 | 21.9 | 16.6 | 2 | 246.3 | 13.8 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
781 | -96 | -6.7 | 0 | 0 | 17.1 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 21.9 | 16.6 | 2.6 | 247.8 | 12.6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
782 | -95 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.6 | 247.8 | 12.3 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
783 | -94 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.3 | 249.3 | 11.6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
784 | -93 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.2 | 243.6 | 10.8 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
785 | -92 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2 | 232.8 | 10.3 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
786 | -91 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.3 | 245.3 | 9.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16.1 | 17.6
787 | -90 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.8 | 239.9 | 8.7 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16.1 | 17.6
788 | -89 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.2 | 234 | 8.3 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16.1 | 17.7
789 | -88 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.7 | 245.4 | 9.9 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16.1 | 17.7
790 | -87 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.9 | 266 | 11.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16.1 | 17.6
791 | -86 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.5 | 22 | 16.6 | 3.2 | 260.5 | 9.8 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16.1 | 17.7
792 | -85 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.3 | 253.2 | 11.4 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16.1 | 17.7
793 | -84 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.5 | 249.6 | 12.7 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.7
794 | -83 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.3 | 240.9 | 12.3 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
795 | -82 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3 | 242.3 | 12.6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.7
796 | -81 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.2 | 236.8 | 13 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
797 | -80 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 3.1 | 231.9 | 12.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
798 | -79 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.6 | 230.8 | 10.6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
799 | -78 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.5 | 202.7 | 7.5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
800 | -77 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.7 | 2.4 | 226.1 | 6.9 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
801 | -76 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 236.2 | 10.4 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
802 | -75 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2 | 259.3 | 10.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
803 | -74 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.4 | 234.6 | 10.5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
804 | -73 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 244 | 10.2 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
805 | -72 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2 | 226.8 | 9.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
806 | -71 | -5.9 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 226.3 | 8.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
807 | -70 | -6.2 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.7 | 232 | 6.4 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
808 | -69 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 222.1 | 6.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
809 | -68 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2 | 248.5 | 6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
810 | -67 | -6.8 | 0 | 0 | 17.1 | 17.6 | 17.5 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 220.6 | 5.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
811 | -66 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 245.4 | 5.6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
812 | -65 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 259.3 | 5.6 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.6
813 | -64 | -6.5 | 0 | 0 | 17.1 | 17.6 | 17.5 | 17.3 | 18.1 | 16.4 | 22 | 16.7 | 2.6 | 234.2 | 5.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
814 | -63 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.2 | 16.5 | 22 | 16.7 | 2.3 | 238.5 | 6.3 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.6
815 | -62 | -6.6 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 3.1 | 231.1 | 6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.8 | 16 | 17.6
816 | -61 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 2.5 | 255.8 | 6.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
817 | -60 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 2.3 | 238.1 | 5.6 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
818 | -59 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 2.4 | 204 | 4.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
819 | -58 | -6.7 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 1.7 | 232.8 | 4.7 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
820 | -57 | -6.8 | 0 | 0 | 17.1 | 17.7 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 1.5 | 254.3 | 5.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
821 | -56 | -6.5 | 0 | 0 | 17.2 | 17.6 | 17.5 | 17.2 | 18.1 | 16.4 | 22 | 16.7 | 1.5 | 235.4 | 6.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
822 | -55 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.1 | 16.3 | 22 | 16.7 | 1.9 | 231.3 | 7.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
823 | -54 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.1 | 16.3 | 22 | 16.7 | 2 | 191.9 | 7.3 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
824 | -53 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.1 | 16.3 | 22 | 16.7 | 1.9 | 216.1 | 7.4 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.7
825 | -52 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.1 | 16.3 | 22 | 16.7 | 2.3 | 251.5 | 6.4 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.7
826 | -51 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 22 | 16.7 | 2 | 248.1 | 6.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.7
827 | -50 | -6.8 | 0 | 0 | 17.1 | 17.7 | 17.5 | 17.2 | 18.1 | 16.3 | 22 | 16.7 | 1.8 | 229.6 | 6.6 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
828 | -49 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 22 | 16.7 | 1.8 | 205.4 | 6.1 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.7
829 | -48 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 21.9 | 16.7 | 1.4 | 258.1 | 5.5 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
830 | -47 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 22 | 16.7 | 1.2 | 235 | 5.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
831 | -46 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.3 | 22 | 16.7 | 1.3 | 221.6 | 6.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
832 | -45 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.7 | 1.6 | 232.7 | 6 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
833 | -44 | -6.8 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.2 | 18.2 | 16.4 | 22 | 16.7 | 1.8 | 237.2 | 6.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
834 | -43 | -6.7 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 1.9 | 242.6 | 6.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.7
835 | -42 | -6.4 | 0 | 0 | 17.2 | 17.7 | 17.5 | 17.3 | 18.2 | 16.3 | 22 | 16.7 | 1.8 | 240.3 | 7.6 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
836 | -41 | -6 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.3 | 22 | 16.7 | 1.7 | 224.5 | 7.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.7
837 | -40 | -5 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.3 | 22 | 16.7 | 1.8 | 211.8 | 6.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.7
838 | -39 | -5.6 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.3 | 22 | 16.6 | 1.8 | 246.1 | 6.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.7
839 | -38 | -3.1 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.2 | 16.3 | 22 | 16.6 | 1.6 | 244.1 | 6.2 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.7
840 | -37 | -6.9 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.5 | 206.2 | 5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.8 | 16 | 17.7
841 | -36 | -6.9 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.4 | 218.3 | 4.2 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
842 | -35 | -6.9 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.2 | 246.6 | 5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
843 | -34 | -6.9 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.5 | 239.9 | 5.9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
844 | -33 | -6.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.9 | 264.2 | 5.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
845 | -32 | -6.3 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 243.9 | 6.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
846 | -31 | -5.9 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.2 | 18.1 | 16.4 | 22 | 16.6 | 2.5 | 234.1 | 7 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
847 | -30 | -5.9 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.2 | 18.1 | 16.4 | 22 | 16.6 | 2.2 | 204.3 | 6.3 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
848 | -29 | -6.1 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.3 | 18.1 | 16.4 | 22 | 16.6 | 1.7 | 211.5 | 5.3 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
849 | -28 | -5.4 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.2 | 268.2 | 5.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
850 | -27 | -4.8 | 0 | 0 | 17.3 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.6 | 255 | 6.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
851 | -26 | -3.1 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.9 | 244.2 | 7 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
852 | -25 | -1.1 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 238.8 | 8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
853 | -24 | 0 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.9 | 248.2 | 8.8 | 16.5 | 16.1 | 16.1 | 16.6 | 15.9 | 16 | 17.6
854 | -23 | -0.2 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 2 | 266.4 | 9.5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
855 | -22 | -0.7 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.5 | 236.8 | 9 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
856 | -21 | -1.3 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.1 | 16.4 | 22 | 16.6 | 1.7 | 223.9 | 8.3 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
857 | -20 | -1.9 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.8 | 213.9 | 8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
858 | -19 | -2.1 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.8 | 206.6 | 7.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
859 | -18 | -1.3 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.5 | 209.5 | 5.8 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
860 | -17 | -0.6 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.5 | 243.6 | 6.3 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.6
861 | -16 | -0.1 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.4 | 238.1 | 6.5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
862 | -15 | -1 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.4 | 223.5 | 7.5 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
863 | -14 | -1.7 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.4 | 222.2 | 8.6 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
864 | -13 | -1.7 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.2 | 18.2 | 16.4 | 22 | 16.6 | 1.5 | 230.6 | 8.7 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
865 | -12 | -1.2 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.7 | 235.8 | 7.4 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
866 | -11 | -2.3 | 0 | 0 | 17.2 | 17.6 | 17.7 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.9 | 246.9 | 7.1 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
867 | -10 | -2.1 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.2 | 226.5 | 6.2 | 16.5 | 16.1 | 16.1 | 16.7 | 15.9 | 16 | 17.7
868 | -9 | -2.2 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.2 | 210.9 | 5.5 | 16.5 | 16.1 | 16.2 | 16.7 | 15.9 | 16 | 17.7
869 | -8 | -1.4 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.2 | 228.6 | 5.1 | 16.5 | 16.1 | 16.2 | 16.7 | 15.9 | 16 | 17.7
870 | -7 | -2.2 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2 | 262.2 | 5.1 | 16.5 | 16.1 | 16.2 | 16.7 | 15.9 | 16 | 17.7
871 | -6 | -1.9 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2 | 249.1 | 5.2 | 16.5 | 16.1 | 16.2 | 16.7 | 15.9 | 16 | 17.7
872 | -5 | -2.7 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.5 | 22 | 16.6 | 1.9 | 240.2 | 5.5 | 16.5 | 16.1 | 16.2 | 16.7 | 15.9 | 16 | 17.7
873 | -4 | -3.3 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.5 | 22 | 16.6 | 1.7 | 258 | 6.1 | 16.5 | 16.2 | 16.3 | 16.7 | 15.9 | 16 | 17.7
874 | -3 | -2.8 | 0 | 0 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.5 | 22 | 16.6 | 1.8 | 241.1 | 6.2 | 16.5 | 16.2 | 16.3 | 16.7 | 15.9 | 16 | 17.7
875 | -2 | -2.2 | 0 | 0 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.5 | 22 | 16.6 | 2 | 273.7 | 5.4 | 16.5 | 16.2 | 16.3 | 16.7 | 15.9 | 16 | 17.7
876 | -1 | -2.8 | 0 | 0 | 17.1 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 277.4 | 4.5 | 16.5 | 16.3 | 16.3 | 16.7 | 15.9 | 16.1 | 17.7
877 | 0 | 3.5 | 1.4 | 1.6365 | 17.2 | 17.6 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 252.2 | 4.1 | 16.5 | 16.3 | 16.3 | 16.7 | 15.9 | 16.1 | 17.7
878 | 1 | 195.3 | 78.12 | 91.3178 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 244.2 | 5 | 16.5 | 16.3 | 16.3 | 16.7 | 15.9 | 16.1 | 17.7
879 | 2 | 377.3 | 150.92 | 176.4168 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 257.5 | 6 | 16.5 | 16.3 | 16.3 | 16.7 | 15.9 | 16.1 | 17.7
880 | 3 | 416 | 166.4 | 194.512 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 1.8 | 249.9 | 7.1 | 16.5 | 16.3 | 16.3 | 16.7 | 15.9 | 16.1 | 17.7
881 | 4 | 413.3 | 165.32 | 193.2496 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.6 | 2.1 | 254.4 | 7.7 | 16.5 | 16.3 | 16.3 | 16.7 | 15.9 | 16.1 | 17.8
882 | 5 | 398.6 | 159.44 | 186.3762 | 17.2 | 17.7 | 17.6 | 17.3 | 18.2 | 16.4 | 22 | 16.7 | 2.3 | 262.6 | 7.4 | 16.5 | 17.1 | 17.5 | 16.7 | 16.1 | 16.2 | 18
883 | 6 | 383.8 | 153.52 | 179.456 | 17.2 | 17.7 | 17.6 | 17.4 | 18.3 | 16.4 | 22 | 16.7 | 2.1 | 257.1 | 7.2 | 16.5 | 21.6 | 22.5 | 16.7 | 18.1 | 19.4 | 20.3
884 | 7 | 378.4 | 151.36 | 176.9311 | 17.4 | 17.8 | 17.7 | 17.5 | 21.4 | 16.5 | 22 | 16.7 | 2.4 | 248.4 | 7.3 | 16.5 | 32.6 | 29.7 | 16.7 | 26.6 | 26.9 | 25.4
885 | 8 | 376.2 | 150.48 | 175.9024 | 17.5 | 17.9 | 17.8 | 17.6 | 28.9 | 16.5 | 22 | 16.7 | 2.3 | 245.8 | 7.8 | 16.5 | 49.8 | 35.4 | 16.7 | 40.9 | 42.4 | 30.2
886 | 9 | 366.8 | 146.72 | 171.5072 | 17.8 | 18 | 18 | 17.8 | 37.2 | 16.5 | 22 | 16.7 | 2.2 | 246.2 | 8.4 | 16.5 | 71.9 | 46.1 | 16.7 | 57.6 | 51.3 | 34.8
887 | 10 | 361.8 | 144.72 | 169.1693 | 18.4 | 18.3 | 18.3 | 18.2 | 46.1 | 16.5 | 22 | 16.6 | 2.3 | 243.5 | 8.4 | 16.6 | 97 | 66.3 | 16.8 | 71.8 | 69.2 | 45.8
888 | 11 | 358.1 | 143.24 | 167.4393 | 19.2 | 18.7 | 19.3 | 19.2 | 54.9 | 16.5 | 22 | 16.6 | 2.5 | 258.1 | 7.5 | 16.6 | 116.7 | 80 | 17.1 | 87.8 | 89.9 | 57.1
889 | 12 | 355.9 | 142.36 | 166.4106 | 20 | 19.1 | 20.9 | 20.6 | 62.8 | 16.6 | 22 | 16.6 | 3 | 270 | 8.4 | 16.7 | 135.5 | 99.7 | 17.5 | 124 | 110.6 | 65.1
890 | 13 | 355 | 142 | 165.9898 | 20.9 | 19.7 | 23 | 22.2 | 77.9 | 16.6 | 22 | 16.6 | 3.2 | 263.9 | 8.7 | 16.7 | 157.4 | 109.9 | 18 | 158.8 | 134.4 | 71.2
891 | 14 | 354.3 | 141.72 | 165.6625 | 21.8 | 20.4 | 25.6 | 24 | 88 | 16.6 | 22 | 16.6 | 3.1 | 260.9 | 8 | 16.9 | 187.7 | 124.4 | 18.9 | 198.3 | 153.8 | 77.2
892 | 15 | 353.8 | 141.52 | 165.4287 | 23.3 | 21.4 | 27.6 | 26.4 | 98.1 | 16.7 | 22 | 16.6 | 3.4 | 248.5 | 7.6 | 17.1 | 226.3 | 155.6 | 20.1 | 249.9 | 181.3 | 86.7
893 | 16 | 353.2 | 141.28 | 165.1482 | 25.2 | 23.4 | 30.3 | 29.7 | 111.7 | 16.7 | 22 | 16.6 | 3.9 | 240.2 | 8.2 | 17.3 | 261.4 | 171.3 | 21.5 | 287 | 209.1 | 94.8
894 | 17 | 353.2 | 141.28 | 165.1482 | 27.5 | 25.9 | 33 | 33.1 | 123 | 16.7 | 22 | 16.6 | 3.6 | 248.5 | 10.3 | 17.7 | 294 | 199.3 | 23.2 | 317.4 | 220.4 | 102.4
895 | 18 | 354 | 141.6 | 165.5222 | 30.2 | 28 | 36.2 | 36.5 | 140 | 16.8 | 22 | 16.7 | 3.8 | 252.9 | 11 | 18.1 | 327.2 | 227 | 25.2 | 351 | 236.7 | 117.8
896 | 19 | 355.1 | 142.04 | 166.0366 | 32.8 | 30.1 | 41.1 | 40.3 | 149.8 | 16.8 | 22 | 16.7 | 3.6 | 244.3 | 10.5 | 18.7 | 362.6 | 253.7 | 27.6 | 370.6 | 255.5 | 132.9
897 | 20 | 356.6 | 142.64 | 166.7379 | 36.1 | 32.7 | 45.7 | 44.6 | 158.4 | 16.9 | 22 | 16.7 | 3 | 243.4 | 10 | 19.3 | 386.1 | 269.5 | 30.2 | 386.4 | 271.6 | 137.4
898 | 21 | 356.8 | 142.72 | 166.8315 | 39.5 | 35.9 | 50.1 | 48.6 | 165.7 | 16.9 | 22 | 16.7 | 3.2 | 241.3 | 9.6 | 20 | 407.9 | 295.1 | 33.1 | 401.8 | 305.7 | 147.9
899 | 22 | 357.4 | 142.96 | 167.112 | 43 | 39.6 | 54.6 | 52.6 | 175.5 | 17 | 22 | 16.7 | 2.7 | 250.1 | 9 | 20.9 | 426.7 | 323 | 36.3 | 422 | 337.3 | 164.7
900 | 23 | 357.9 | 143.16 | 167.3458 | 47.2 | 43.4 | 58.8 | 56.8 | 184.4 | 17 | 22 | 16.7 | 2.5 | 249.9 | 8.3 | 21.8 | 439.1 | 349.1 | 39.6 | 445.2 | 355.6 | 167.5
901 | 24 | 358.4 | 143.36 | 167.5796 | 51.9 | 47.2 | 62.8 | 61.1 | 197 | 17 | 22 | 16.7 | 2.6 | 260.7 | 9.6 | 22.9 | 456.7 | 364.9 | 43 | 477.3 | 381.1 | 174.9
902 | 25 | 359.4 | 143.76 | 168.0472 | 56.4 | 50.1 | 66.7 | 65 | 215.3 | 17.1 | 22 | 16.7 | 3.1 | 247.6 | 12.4 | 24.1 | 469.7 | 372.9 | 46.7 | 511.9 | 398.9 | 185.8
903 | 26 | 360.8 | 144.32 | 168.7018 | 60.3 | 53.4 | 71 | 69.1 | 225.3 | 17.1 | 22 | 16.8 | 3.2 | 259.2 | 12.8 | 25.5 | 486.2 | 384 | 50.4 | 533.5 | 414.7 | 188.2
904 | 27 | 360.5 | 144.2 | 168.5615 | 63.9 | 57.3 | 75.9 | 73.6 | 232 | 17.1 | 22 | 17 | 3.5 | 265.4 | 11.9 | 27 | 495 | 394.1 | 53.5 | 558.3 | 435.1 | 194.9
905 | 28 | 360.7 | 144.28 | 168.655 | 67.6 | 60.8 | 79.6 | 77.3 | 237.4 | 17.1 | 22 | 17.3 | 4.1 | 270.1 | 10.7 | 28.6 | 501.2 | 424.9 | 56.8 | 574.4 | 453.2 | 207.7
906 | 29 | 360.7 | 144.28 | 168.655 | 71.7 | 65.2 | 83.4 | 81.7 | 239.6 | 17.1 | 22 | 17.9 | 4.3 | 257.3 | 9.8 | 30.2 | 514.1 | 429.2 | 60.8 | 592.8 | 475.5 | 213.2
907 | 30 | 362.3 | 144.92 | 169.4031 | 75.8 | 68.8 | 87.6 | 86.4 | 248.7 | 17.2 | 22 | 18.5 | 3.6 | 254.9 | 9.8 | 31.9 | 530 | 424.8 | 65 | 617 | 488.7 | 209.2
908 | 31 | 363.3 | 145.32 | 169.8707 | 79.8 | 72.1 | 91.9 | 91 | 261.3 | 17.2 | 22 | 19.2 | 3.1 | 244.4 | 10.1 | 33.7 | 530.2 | 423.2 | 69.5 | 622.9 | 477 | 206
909 | 32 | 363.5 | 145.4 | 169.9642 | 83.9 | 75.9 | 95.6 | 95.1 | 263.1 | 17.2 | 22 | 19.9 | 3.6 | 252.2 | 10.4 | 35.6 | 524.7 | 417.4 | 74.3 | 634.7 | 464.3 | 200.2
910 | 33 | 363.9 | 145.56 | 170.1513 | 87.6 | 80 | 99.1 | 99.5 | 270.6 | 17.2 | 22 | 20.6 | 3.7 | 245.7 | 10 | 37.6 | 534.3 | 424.2 | 79.4 | 656.2 | 457.6 | 204.2
911 | 34 | 364.1 | 145.64 | 170.2448 | 91.1 | 84 | 102.7 | 104.1 | 277.8 | 17.2 | 22 | 21.4 | 4 | 234.9 | 9.8 | 39.6 | 546 | 418.3 | 84.6 | 664.5 | 457.3 | 208.1
912 | 35 | 364.8 | 145.92 | 170.5721 | 94.9 | 88.5 | 106.8 | 108.2 | 283.2 | 17.2 | 22 | 22.1 | 3.4 | 242.6 | 9.3 | 41.7 | 551.3 | 417.8 | 89.8 | 672.8 | 449.2 | 207
913 | 36 | 364.9 | 145.96 | 170.6188 | 99.1 | 92.8 | 110.5 | 112.5 | 286.5 | 17.2 | 22 | 22.7 | 3.1 | 254.2 | 10.7 | 43.9 | 541 | 433.6 | 95.2 | 677.8 | 464.8 | 213.2
914 | 37 | 365.9 | 146.36 | 171.0864 | 102.5 | 96.3 | 114.3 | 116.1 | 292.4 | 17.2 | 21.9 | 23.4 | 2.6 | 243.5 | 11.6 | 46.1 | 533.8 | 430.7 | 100.6 | 684.6 | 475.5 | 219.3
915 | 38 | 365.5 | 146.2 | 170.8994 | 105.7 | 99.4 | 117.5 | 119.6 | 292.6 | 17.2 | 21.9 | 24 | 2.6 | 247.5 | 10.9 | 48.3 | 532.2 | 428.8 | 106.1 | 690.7 | 471.4 | 220.9
916 | 39 | 365.6 | 146.24 | 170.9461 | 108.8 | 102.9 | 120.5 | 123.7 | 291.5 | 17.3 | 21.9 | 24.5 | 2.5 | 250.2 | 10.1 | 50.6 | 537.2 | 436.3 | 111.6 | 701.5 | 465 | 226.5
917 | 40 | 367.5 | 147 | 171.8345 | 111.4 | 106.2 | 123.8 | 127.7 | 294.3 | 17.5 | 21.9 | 25.1 | 2.9 | 245.2 | 10.5 | 52.8 | 541.3 | 451.9 | 117.5 | 707.7 | 460.5 | 237.6
918 | 41 | 369 | 147.6 | 172.5359 | 113.8 | 109.6 | 126.7 | 130.5 | 294.8 | 17.6 | 21.9 | 25.7 | 3.1 | 244.2 | 10.6 | 55.1 | 554.1 | 462.4 | 123.1 | 707.6 | 466.4 | 243.2
919 | 42 | 368.6 | 147.44 | 172.3489 | 117.2 | 113.2 | 129.2 | 132.9 | 299.8 | 17.7 | 21.9 | 26.2 | 3.3 | 264.5 | 10.4 | 57.4 | 560.7 | 474.5 | 128.5 | 711.9 | 474.6 | 252.4
920 | 43 | 368.4 | 147.36 | 172.2553 | 120.2 | 116.7 | 131.8 | 135.8 | 298.8 | 17.7 | 21.9 | 26.7 | 3.4 | 262.9 | 11.1 | 59.6 | 557 | 473.4 | 133.9 | 712.7 | 473.5 | 253.2
921 | 44 | 368.4 | 147.36 | 172.2553 | 122.6 | 119.8 | 134.1 | 138.8 | 298.3 | 17.7 | 21.9 | 27.2 | 4.4 | 266.9 | 13 | 61.8 | 538.1 | 477.9 | 139.1 | 707.8 | 477.6 | 254.7
922 | 45 | 369.5 | 147.8 | 172.7697 | 124.4 | 122.6 | 136.6 | 141.2 | 296.4 | 17.7 | 21.9 | 27.8 | 4.1 | 267.9 | 13.1 | 64.1 | 535.4 | 490.1 | 144 | 711.5 | 484.5 | 263.8
923 | 46 | 369.4 | 147.76 | 172.7229 | 127 | 125 | 138.9 | 143.3 | 299 | 17.8 | 21.9 | 28.2 | 3.5 | 261.9 | 10.2 | 66.4 | 531.7 | 501 | 148.4 | 710.5 | 493.3 | 273.8
924 | 47 | 371.9 | 148.76 | 173.8919 | 129.7 | 127.5 | 141.5 | 145.6 | 301.1 | 17.8 | 21.9 | 28.7 | 3 | 259.4 | 10.6 | 68.7 | 540 | 505.6 | 152.4 | 716.3 | 498.1 | 279.3
925 | 48 | 372.6 | 149.04 | 174.2192 | 132.3 | 130.1 | 144.6 | 147.7 | 303.9 | 17.8 | 21.9 | 29.2 | 4.1 | 266 | 11 | 71 | 548.6 | 518.3 | 156 | 722.4 | 498 | 282.1
926 | 49 | 372.2 | 148.88 | 174.0321 | 134.8 | 131.9 | 146.6 | 149.5 | 308.9 | 17.8 | 21.9 | 29.6 | 4.2 | 250.6 | 13.1 | 73.4 | 558.9 | 525.4 | 159.4 | 731.3 | 491.2 | 280.9
927 | 50 | 370.7 | 148.28 | 173.3308 | 136.1 | 133.8 | 148.6 | 151.2 | 310.4 | 17.9 | 21.9 | 29.9 | 3.7 | 255.8 | 14 | 75.8 | 566.9 | 532.4 | 162.6 | 737.4 | 503.1 | 282.1
928 | 51 | 372.1 | 148.84 | 173.9854 | 137.2 | 135.7 | 150.1 | 153 | 314.3 | 17.8 | 21.9 | 30.1 | 3.3 | 254.3 | 14.2 | 78.4 | 566.3 | 526.3 | 165.7 | 743.3 | 508.6 | 285.2
929 | 52 | 372 | 148.8 | 173.9386 | 138.2 | 137.3 | 151.8 | 154.7 | 313.9 | 17.8 | 21.9 | 30.3 | 4 | 252.3 | 15.2 | 81 | 565.2 | 522.9 | 168.6 | 737.1 | 501.4 | 286.4
930 | 53 | 371.2 | 148.48 | 173.5646 | 139.9 | 139.3 | 153.3 | 156.5 | 316.3 | 17.8 | 21.9 | 30.6 | 3.6 | 254.4 | 12.9 | 83.7 | 570.6 | 511.8 | 171.6 | 743.4 | 496.9 | 287.4
931 | 54 | 372.6 | 149.04 | 174.2192 | 141.9 | 141.4 | 155.1 | 158.6 | 324 | 17.8 | 21.9 | 30.8 | 3.2 | 245.4 | 11.3 | 86.6 | 574.2 | 502 | 174.8 | 744.5 | 512.4 | 292.2
932 | 55 | 373.1 | 149.24 | 174.453 | 143.9 | 143.1 | 156.6 | 160.3 | 329.8 | 17.8 | 21.9 | 31 | 3.1 | 247.9 | 10 | 89.5 | 570.8 | 507.9 | 178.1 | 748.1 | 523.2 | 298.5
933 | 56 | 373.6 | 149.44 | 174.6867 | 145.2 | 145.3 | 157.5 | 161.7 | 326 | 17.8 | 21.9 | 31.1 | 2.7 | 287.6 | 7.8 | 92.6 | 579.8 | 509.6 | 181.3 | 749.9 | 523.9 | 303.3
934 | 57 | 373.3 | 149.32 | 174.5465 | 147 | 147.6 | 158.7 | 163.6 | 323.4 | 17.9 | 21.9 | 31.2 | 3.6 | 255.3 | 7.1 | 95.7 | 591 | 524.1 | 184.4 | 753.8 | 516.7 | 309.1
935 | 58 | 373.8 | 149.52 | 174.7803 | 148.4 | 149.1 | 159.5 | 164.9 | 323.1 | 17.9 | 21.9 | 31.3 | 4 | 264.6 | 9.4 | 99 | 595.3 | 540.9 | 188.7 | 747.5 | 522.4 | 323.5
936 | 59 | 373.8 | 149.52 | 174.7803 | 150.2 | 150.8 | 160.5 | 166.5 | 326.9 | 18 | 21.9 | 31.4 | 4.1 | 249.7 | 9.4 | 102.9 | 591.6 | 550.8 | 192.4 | 749.4 | 537.2 | 328.6
937 | 60 | 374.2 | 149.68 | 174.9673 | 151.4 | 152.1 | 161.8 | 168.1 | 327.1 | 18 | 21.9 | 31.6 | 3.2 | 269.5 | 8.1 | 109.1 | 585.8 | 554.2 | 193.9 | 752.7 | 552.6 | 332.6
938 | 61 | 375.1 | 150.04 | 175.3881 | 152 | 152.9 | 163.2 | 170 | 323.3 | 18 | 21.9 | 31.8 | 3.1 | 264.4 | 9.8 | 115.5 | 579.3 | 564.9 | 195.1 | 750.8 | 559 | 336.3
939 | 62 | 375.1 | 150.04 | 175.3881 | 152.8 | 154.6 | 164.3 | 171 | 321.9 | 18.1 | 21.9 | 32.1 | 3.4 | 253.8 | 11.6 | 121 | 566.4 | 574.5 | 197 | 752.9 | 564.3 | 342.8
940 | 63 | 375.4 | 150.16 | 175.5284 | 154.6 | 156.2 | 165.4 | 171.9 | 325.8 | 18.1 | 21.9 | 32.3 | 3.9 | 246.9 | 13.2 | 125.7 | 556.2 | 578.8 | 199.1 | 756.1 | 558.5 | 350.8
941 | 64 | 375.2 | 150.08 | 175.4349 | 156.1 | 157.1 | 166.5 | 173.6 | 329.3 | 18.1 | 21.9 | 32.6 | 3.7 | 251.9 | 12.4 | 130.2 | 544.7 | 572.6 | 201.5 | 757.4 | 574.1 | 352.7
942 | 65 | 375.4 | 150.16 | 175.5284 | 157.3 | 158.5 | 167.5 | 174.7 | 330.2 | 18.1 | 21.9 | 32.9 | 3.4 | 256.3 | 11.7 | 134.8 | 541.5 | 577.4 | 203.6 | 757.3 | 600 | 360.4
943 | 66 | 376.5 | 150.6 | 176.0427 | 158.2 | 160.1 | 168.3 | 175.8 | 335 | 18.2 | 21.9 | 33.1 | 3.6 | 264.3 | 11.5 | 139 | 531.2 | 572.1 | 206.3 | 752.4 | 615.8 | 365.1
944 | 67 | 377.5 | 151 | 176.5103 | 159.1 | 161.9 | 169.4 | 176.4 | 335.9 | 18.2 | 21.9 | 33.4 | 4 | 247.4 | 12.3 | 143 | 502.1 | 556.9 | 209.2 | 737.1 | 629.9 | 360.9
945 | 68 | 376.5 | 150.6 | 176.0427 | 159.3 | 163.6 | 170.5 | 177.1 | 335.1 | 18.2 | 21.9 | 33.7 | 4 | 244.2 | 12.7 | 146.9 | 476.7 | 554.2 | 212 | 727.8 | 628.1 | 359.5
946 | 69 | 377.5 | 151 | 176.5103 | 159.9 | 163.9 | 171.5 | 178.4 | 331 | 18.2 | 21.9 | 34 | 3.5 | 260 | 13.6 | 150.2 | 507.6 | 548.7 | 214.8 | 742.7 | 628.2 | 364.9
947 | 70 | 379.8 | 151.92 | 177.5857 | 161.1 | 163.3 | 172.3 | 179.2 | 330.2 | 18.3 | 21.9 | 34.3 | 3.1 | 245.5 | 13.5 | 153.2 | 420 | 539.3 | 217.7 | 735.7 | 623.5 | 367.4
948 | 71 | 379.7 | 151.88 | 177.539 | 162.2 | 163.7 | 172.3 | 179.5 | 330.6 | 18.3 | 21.9 | 34.5 | 3.4 | 248.5 | 13.2 | 155.9 | 437.4 | 525.7 | 221.6 | 737.6 | 634 | 363.9
949 | 72 | 379.2 | 151.68 | 177.3052 | 162.8 | 165.4 | 172.9 | 180 | 331.1 | 18.3 | 21.9 | 34.7 | 3.6 | 243.5 | 13.8 | 158.3 | 487.6 | 511.6 | 226.8 | 734.7 | 631.8 | 363.7
950 | 73 | 378.7 | 151.48 | 177.0714 | 164.1 | 166.4 | 174.5 | 181.3 | 333.1 | 18.4 | 21.9 | 35 | 3.9 | 242.8 | 13.7 | 160.7 | 338.6 | 507.7 | 231.7 | 742 | 635.9 | 364.6
951 | 74 | 379.9 | 151.96 | 177.6325 | 165.4 | 166.9 | 175.7 | 182.2 | 335.7 | 18.4 | 21.8 | 35.2 | 4.2 | 253.9 | 14 | 162.8 | 457.2 | 504.5 | 236.2 | 748.1 | 623.6 | 368.9
952 | 75 | 379.3 | 151.72 | 177.3519 | 166.9 | 167.5 | 177.1 | 183.2 | 336.2 | 18.4 | 21.8 | 35.4 | 4.1 | 254.3 | 13.5 | 164.9 | 502.1 | 511.5 | 241 | 745.9 | 609.3 | 374.8
953 | 76 | 379.7 | 151.88 | 177.539 | 168.2 | 168.1 | 178.4 | 184.7 | 334.7 | 18.5 | 21.8 | 35.8 | 4.5 | 263.4 | 13.8 | 167 | 282.3 | 516.2 | 245.2 | 743.3 | 606.5 | 381.1
954 | 77 | 379.3 | 151.72 | 177.3519 | 168.9 | 169 | 179.5 | 186 | 330.2 | 18.5 | 21.8 | 36 | 5.2 | 253.5 | 13.8 | 168.7 | 500 | 521.2 | 248.7 | 746.4 | 607.1 | 385.4
955 | 78 | 379.2 | 151.68 | 177.3052 | 169.2 | 169.6 | 180.2 | 186.9 | 325.7 | 18.6 | 21.8 | 36.1 | 4.5 | 250 | 12.8 | 170.5 | 458.4 | 531.9 | 251.4 | 747.3 | 603.7 | 391.2
956 | 79 | 379.1 | 151.64 | 177.2584 | 168.8 | 170.3 | 181 | 187.5 | 322.6 | 18.6 | 21.8 | 36.3 | 5.2 | 240.4 | 11.6 | 171.9 | 300.8 | 534.7 | 252.9 | 746.2 | 617.7 | 399.4
957 | 80 | 375.5 | 150.2 | 175.5751 | 168.7 | 170.6 | 181.7 | 188.1 | 319.5 | 18.7 | 21.8 | 36.4 | 3.6 | 246.4 | 11.6 | 173.1 | 491.8 | 544.8 | 253.6 | 750.9 | 644.6 | 409
958 | 81 | 376.5 | 150.6 | 176.0427 | 168.8 | 171.8 | 182.2 | 188.3 | 327.3 | 18.7 | 21.8 | 36.6 | 3.9 | 249.3 | 12.6 | 174.5 | 405.8 | 565.2 | 254.1 | 766.8 | 661.8 | 421.8
959 | 82 | 377.7 | 151.08 | 176.6038 | 169 | 173.8 | 182.6 | 188.1 | 343.2 | 18.8 | 21.8 | 36.9 | 3.9 | 258.3 | 11.1 | 175.7 | 357.9 | 582 | 255.2 | 772.5 | 650.2 | 431.2
960 | 83 | 377.8 | 151.12 | 176.6506 | 169.6 | 175.5 | 184.1 | 188.6 | 341.6 | 18.9 | 21.8 | 37.1 | 3.7 | 248.9 | 12.2 | 176.7 | 526.4 | 577 | 256.2 | 767 | 637.8 | 426.8
961 | 84 | 377.9 | 151.16 | 176.6973 | 172.3 | 175.6 | 183.9 | 189 | 335.6 | 18.9 | 21.8 | 37.3 | 3.8 | 266.1 | 11.7 | 178 | 347.2 | 578.9 | 255.6 | 771.6 | 629.9 | 424.1
962 | 85 | 379.2 | 151.68 | 177.3052 | 172.1 | 176.2 | 184.8 | 190.1 | 331.4 | 18.9 | 21.8 | 37.4 | 3.7 | 255 | 10.8 | 179.2 | 424.2 | 583.4 | 252.5 | 778.8 | 620.3 | 429.8
963 | 86 | 381.9 | 152.76 | 178.5676 | 171.5 | 176.6 | 184.8 | 190.7 | 335.5 | 18.9 | 21.8 | 37.5 | 3.4 | 269.9 | 9.5 | 180.2 | 578.9 | 576.1 | 249.2 | 784.4 | 609.8 | 426.2
964 | 87 | 382.7 | 153.08 | 178.9417 | 171.9 | 177.4 | 185.5 | 191.1 | 342.3 | 19 | 21.8 | 37.5 | 4.1 | 255.4 | 10.3 | 181.4 | 602.3 | 574.2 | 248.2 | 788.9 | 606.2 | 425.6
965 | 88 | 381.4 | 152.56 | 178.3339 | 173.1 | 178.5 | 186.6 | 191.6 | 344.3 | 19 | 21.8 | 37.6 | 4 | 247.4 | 11 | 182.5 | 614 | 574.3 | 248.4 | 797.9 | 601.9 | 426.4
966 | 89 | 379.8 | 151.92 | 177.5857 | 174.4 | 179.6 | 187.5 | 192.2 | 342.1 | 19.1 | 21.8 | 37.6 | 4 | 261 | 10.2 | 183.7 | 627.6 | 583.5 | 249.5 | 807.8 | 600.3 | 431.9
967 | 90 | 380.6 | 152.24 | 177.9598 | 175.8 | 180.3 | 188.6 | 192.9 | 346.4 | 19.1 | 21.8 | 37.6 | 3.7 | 254 | 10.7 | 184.9 | 631.7 | 576.9 | 249.8 | 810.8 | 600.8 | 433.5
968 | 91 | 381.1 | 152.44 | 178.1936 | 176.9 | 180.7 | 189.8 | 193.9 | 351.9 | 19.2 | 21.8 | 37.8 | 3.7 | 254.5 | 11.5 | 186.1 | 637 | 578.3 | 250.4 | 817 | 607.2 | 434.6
969 | 92 | 380.3 | 152.12 | 177.8195 | 176.3 | 182.5 | 192.1 | 195.4 | 364.6 | 19.4 | 21.8 | 38 | 4.3 | 262.9 | 10.6 | 187.4 | 637.3 | 581 | 252.2 | 821.6 | 606.5 | 442.7
970 | 93 | 379.7 | 151.88 | 177.539 | 178.9 | 183.5 | 192.8 | 196 | 366.3 | 19.2 | 21.8 | 38 | 4.4 | 268.3 | 10.6 | 188.7 | 641.2 | 586 | 254.1 | 810.7 | 598 | 443.5
971 | 94 | 379.2 | 151.68 | 177.3052 | 179.7 | 184.5 | 194.2 | 197.3 | 357.2 | 19.2 | 21.8 | 38.1 | 4.7 | 275.7 | 9.3 | 190 | 651.8 | 591.7 | 256.7 | 815.4 | 586.8 | 450.3
972 | 95 | 380 | 152 | 177.6792 | 180.7 | 185.8 | 195.2 | 198.8 | 354.7 | 19.3 | 21.8 | 38.1 | 4.6 | 247.8 | 8.1 | 191.3 | 668 | 590.5 | 259.3 | 815.3 | 581.1 | 449.6
973 | 96 | 379.6 | 151.84 | 177.4922 | 183.6 | 186.4 | 195.6 | 199.6 | 358.2 | 19.3 | 21.8 | 38.2 | 5 | 263.3 | 9.7 | 192.6 | 672.3 | 585.6 | 260.9 | 815.9 | 577.2 | 451
974 | 97 | 380 | 152 | 177.6792 | 185.4 | 186.9 | 196.2 | 200.9 | 359.7 | 19.4 | 21.8 | 38.3 | 4.4 | 248.5 | 13.4 | 194 | 678.6 | 581.9 | 262.4 | 814.2 | 570.9 | 451.8
975 | 98 | 380.5 | 152.2 | 177.913 | 184.1 | 188.6 | 198.4 | 202.9 | 358.2 | 19.5 | 21.8 | 38.4 | 3.7 | 250.1 | 15.2 | 195.3 | 674.4 | 581.2 | 263.7 | 820.2 | 568.7 | 453.7
976 | 99 | 379.3 | 151.72 | 177.3519 | 181.6 | 189.8 | 201.7 | 204.6 | 356.2 | 19.9 | 21.8 | 38.5 | 4.5 | 253 | 13.2 | 196.7 | 666.2 | 580.9 | 265.3 | 824.9 | 562.7 | 458.5
977 | 100 | 379.7 | 151.88 | 177.539 | 185 | 188.6 | 201 | 204.7 | 356.1 | 19.5 | 21.8 | 38.6 | 5 | 247.2 | 12.9 | 198.3 | 660.1 | 564.6 | 266 | 833.7 | 553.4 | 453.3
978 | 101 | 379.8 | 151.92 | 177.5857 | 187.4 | 188.3 | 200.8 | 205.6 | 358.6 | 19.4 | 21.8 | 38.6 | 4.7 | 256.7 | 14.3 | 200.1 | 641.3 | 553.7 | 268.8 | 837.1 | 549.7 | 447.9
979 | 102 | 379.3 | 151.72 | 177.3519 | 188.2 | 189.6 | 202.4 | 206.8 | 367.2 | 19.5 | 21.8 | 38.7 | 5 | 247.6 | 15.3 | 201.9 | 634.6 | 545.6 | 272.8 | 841 | 538.2 | 448.2
980 | 103 | 379.5 | 151.8 | 177.4455 | 189.4 | 191.6 | 204.1 | 207.7 | 370.6 | 19.5 | 21.7 | 38.7 | 7 | 248.3 | 14.1 | 203.8 | 639 | 534.1 | 275.9 | 849.7 | 535.1 | 450.6
981 | 104 | 379.8 | 151.92 | 177.5857 | 192.2 | 192.5 | 204.1 | 207.9 | 373.2 | 19.4 | 21.7 | 38.8 | 7.3 | 250.3 | 13.3 | 205.7 | 632.6 | 533 | 278.2 | 856.8 | 542.9 | 454
982 | 105 | 379 | 151.6 | 177.2117 | 193.1 | 194 | 205.8 | 208.8 | 376.3 | 19.5 | 21.7 | 38.8 | 6 | 257 | 13.6 | 207.8 | 619.7 | 545.2 | 282.1 | 861.8 | 566.5 | 465.1
983 | 106 | 379.3 | 151.72 | 177.3519 | 193.9 | 194.8 | 207.2 | 210.1 | 378.5 | 19.5 | 21.7 | 38.8 | 5.3 | 253.3 | 14.9 | 209.5 | 613.6 | 577.2 | 285.2 | 854.7 | 594.9 | 482.2
984 | 107 | 379.3 | 151.72 | 177.3519 | 194.7 | 196.1 | 208.2 | 211.2 | 380.5 | 19.7 | 21.7 | 38.8 | 5.3 | 261.6 | 14.8 | 211.1 | 610.3 | 587.4 | 287.2 | 858.5 | 614.8 | 489.3
985 | 108 | 380 | 152 | 177.6792 | 196.2 | 197.9 | 209 | 212.2 | 385.5 | 19.8 | 21.7 | 38.9 | 4.2 | 260.1 | 15.6 | 212.9 | 599.1 | 589.9 | 289.6 | 848 | 630.6 | 489.5
986 | 109 | 380.7 | 152.28 | 178.0065 | 196.7 | 198.6 | 209.9 | 213.6 | 385.4 | 19.8 | 21.7 | 38.9 | 5 | 268.3 | 17 | 214.9 | 593.7 | 578.2 | 292 | 845.8 | 620.4 | 485.8
987 | 110 | 380.9 | 152.36 | 178.1001 | 197 | 198 | 210.5 | 214.2 | 381.6 | 19.8 | 21.7 | 39 | 5.4 | 263.7 | 14.8 | 217 | 608.8 | 570.5 | 297.1 | 824.4 | 600.6 | 479.4
988 | 111 | 380.5 | 152.2 | 177.913 | 198.5 | 198.9 | 211.3 | 214.7 | 376.3 | 19.8 | 21.7 | 39.1 | 5.7 | 271 | 12.6 | 219.2 | 616 | 571.2 | 301.9 | 826.7 | 601.8 | 483.1
989 | 112 | 379.7 | 151.88 | 177.539 | 199.2 | 199.5 | 211.8 | 215.5 | 372.6 | 19.8 | 21.7 | 39.4 | 4.6 | 262.4 | 11.4 | 222.2 | 627.7 | 562.9 | 305.5 | 837.9 | 584.7 | 482.9
990 | 113 | 378.9 | 151.56 | 177.1649 | 199.3 | 200.2 | 212 | 215.9 | 372.5 | 19.8 | 21.7 | 39.5 | 5 | 246.2 | 12.4 | 224.9 | 637.4 | 563.8 | 307.1 | 832.4 | 579.7 | 486.8
991 | 114 | 380.1 | 152.04 | 177.726 | 199.1 | 200.5 | 212.5 | 216 | 369.4 | 19.8 | 21.7 | 39.8 | 6.1 | 252.1 | 11.9 | 227.3 | 646.3 | 567.4 | 308.2 | 829.5 | 599.3 | 487.6
992 | 115 | 379.9 | 151.96 | 177.6325 | 199.9 | 200.9 | 213.7 | 216.6 | 368.6 | 19.9 | 21.7 | 40 | 6.7 | 246.3 | 10.9 | 229.4 | 644.8 | 577.1 | 309.6 | 825.7 | 609.4 | 494
993 | 116 | 380.1 | 152.04 | 177.726 | 200.3 | 200.9 | 214.2 | 217.8 | 376.4 | 20 | 21.7 | 40 | 5.1 | 279.1 | 10.1 | 231.4 | 640.7 | 590.5 | 312.6 | 821.2 | 618.2 | 504.2
994 | 117 | 380.1 | 152.04 | 177.726 | 199.8 | 200.9 | 214.7 | 218.1 | 383.3 | 20.1 | 21.7 | 40.1 | 4.9 | 257 | 9 | 233.6 | 635 | 587.3 | 316 | 807.3 | 622.2 | 502.5
995 | 118 | 380.4 | 152.16 | 177.8663 | 200.1 | 201.6 | 214.9 | 218.6 | 386.9 | 20.2 | 21.7 | 40.4 | 4.7 | 266.7 | 8.9 | 236.8 | 639.6 | 582.7 | 319.3 | 812.9 | 627.1 | 501.8
996 | 119 | 380.6 | 152.24 | 177.9598 | 200.2 | 203.2 | 214.9 | 218.7 | 391.8 | 20.3 | 21.7 | 40.6 | 5.4 | 222.5 | 9.4 | 240.6 | 638.6 | 584.6 | 322.5 | 815.6 | 631.4 | 503.8
997 | 120 | 380.2 | 152.08 | 177.7728 | 200.4 | 204.5 | 214.9 | 219.1 | 394.1 | 20.3 | 21.7 | 40.8 | 3.6 | 244.9 | 9.8 | 244.1 | 636 | 597.3 | 325.3 | 820.4 | 633.8 | 510.5
998 | 121 | 380.7 | 152.28 | 178.0065 | 199.4 | 205.2 | 215.7 | 219.6 | 397 | 20.4 | 21.7 | 40.8 | 3.8 | 239.8 | 9.9 | 246.3 | 645.7 | 605.9 | 328.6 | 819.9 | 642.2 | 519
999 | 122 | 379.8 | 151.92 | 177.5857 | 199.1 | 205.4 | 216.2 | 220.2 | 395.5 | 20.5 | 21.7 | 40.9 | 4.2 | 251.9 | 10.7 | 247.8 | 643.5 | 607.4 | 332.1 | 806.5 | 645.9 | 518.8
1000 | 123 | 380.3 | 152.12 | 177.8195 | 199.5 | 204.7 | 216.4 | 219.6 | 388.3 | 20.5 | 21.7 | 41.1 | 4.4 | 248.3 | 11.2 | 249.6 | 620.9 | 592.3 | 335 | 800.1 | 654.1 | 510.9
1001 | 124 | 379.7 | 151.88 | 177.539 | 200.1 | 204.1 | 216.9 | 219.6 | 385.1 | 20.6 | 21.7 | 41.3 | 4.1 | 240.8 | 10.7 | 252 | 615.9 | 576.3 | 337.2 | 801.3 | 656.2 | 506.4
1002 | 125 | 379.7 | 151.88 | 177.539 | 200.8 | 204.4 | 217.1 | 219.3 | 384 | 20.6 | 21.7 | 41.5 | 5 | 230.4 | 11.8 | 254.9 | 611.2 | 575.2 | 339.6 | 800.7 | 649.9 | 507.5
1003 | 126 | 379.3 | 151.72 | 177.3519 | 202.3 | 205.4 | 216.8 | 219 | 383 | 20.6 | 21.7 | 41.7 | 4.7 | 226.8 | 11.7 | 258.1 | 613.8 | 565.5 | 341.9 | 812.3 | 641.5 | 507.9
1004 | 127 | 379.7 | 151.88 | 177.539 | 202.5 | 205.5 | 216.4 | 218.5 | 384.2 | 20.6 | 21.7 | 41.9 | 4.6 | 230.1 | 11.1 | 261.4 | 613.4 | 558.4 | 343.9 | 820.2 | 629 | 506.2
1005 | 128 | 379.9 | 151.96 | 177.6325 | 203.1 | 204.5 | 216.7 | 217.8 | 394.4 | 20.6 | 21.7 | 42.1 | 4 | 200.4 | 10.1 | 264.5 | 627.8 | 557.8 | 346.3 | 829.9 | 627.8 | 509.9
1006 | 129 | 376.6 | 150.64 | 176.0895 | 202.5 | 204.6 | 218.1 | 218.1 | 393.4 | 20.8 | 21.7 | 42.2 | 3.5 | 217.1 | 9.3 | 266.6 | 637.4 | 566.4 | 348.9 | 840.5 | 626.7 | 515.1
1007 | 130 | 379.8 | 151.92 | 177.5857 | 203.4 | 204.6 | 218.5 | 218.2 | 395.1 | 20.7 | 21.7 | 42.3 | 4.1 | 222.6 | 8.8 | 268.3 | 647.1 | 574 | 351.3 | 854.2 | 618.6 | 517.1
1008 | 131 | 379.2 | 151.68 | 177.3052 | 203.6 | 204.6 | 218.9 | 218.5 | 402.8 | 20.8 | 21.6 | 42.4 | 3.6 | 230.5 | 7.7 | 269.7 | 667.4 | 577 | 354.1 | 864.3 | 617.5 | 519.9
1009 | 132 | 378.4 | 151.36 | 176.9311 | 203.2 | 205.2 | 219 | 219.3 | 410.1 | 20.8 | 21.6 | 42.5 | 3.8 | 229.8 | 7.4 | 270.7 | 653.9 | 592 | 356.6 | 867.2 | 634.5 | 528.7
1010 | 133 | 378.9 | 151.56 | 177.1649 | 203.5 | 206 | 219.7 | 219.7 | 406.1 | 20.9 | 21.6 | 42.6 | 4.4 | 200.7 | 7.6 | 271.2 | 653.3 | 606 | 358.8 | 869.6 | 649.9 | 533.7
1011 | 134 | 379.4 | 151.76 | 177.3987 | 203.8 | 206.7 | 220.3 | 219.9 | 406.1 | 21 | 21.6 | 42.7 | 4.4 | 208 | 6.4 | 273 | 651.1 | 613.9 | 361.5 | 866.9 | 657.8 | 537.5
1012 | 135 | 380.2 | 152.08 | 177.7728 | 204.1 | 207.1 | 220.8 | 220.9 | 408.3 | 21 | 21.6 | 42.7 | 4.5 | 240.5 | 6.1 | 275.5 | 655.2 | 613.4 | 364.6 | 871.3 | 663.6 | 534.1
1013 | 136 | 381 | 152.4 | 178.1468 | 205.4 | 207.6 | 221.2 | 221.4 | 412.2 | 21 | 21.6 | 42.7 | 4.9 | 220.3 | 6.7 | 278.7 | 672.7 | 610 | 367.8 | 876.6 | 650.3 | 533.2
1014 | 137 | 380.1 | 152.04 | 177.726 | 206.2 | 208.1 | 221.3 | 222 | 405.5 | 21 | 21.6 | 42.9 | 5.1 | 225.9 | 7.7 | 282.5 | 686.6 | 607.5 | 371.1 | 863.6 | 633.9 | 532.6
1015 | 138 | 380.7 | 152.28 | 178.0065 | 206.6 | 208.5 | 221.9 | 222.6 | 404.9 | 21 | 21.6 | 42.9 | 3.9 | 211.5 | 8.6 | 285.2 | 695.8 | 606.9 | 373.9 | 860.8 | 628.2 | 537.6
1016 | 139 | 380.4 | 152.16 | 177.8663 | 207.4 | 208.1 | 222 | 223.3 | 403.6 | 21 | 21.6 | 43 | 4.5 | 234.6 | 8.1 | 287.8 | 705.1 | 603.4 | 376.5 | 863.8 | 625.3 | 536.5
1017 | 140 | 379.4 | 151.76 | 177.3987 | 208.4 | 208.4 | 221.7 | 223.5 | 405.1 | 21 | 21.6 | 43.2 | 4.7 | 236.9 | 8.2 | 289.4 | 696 | 606.6 | 378.9 | 867.1 | 633.3 | 536.9
1018 | 141 | 379.9 | 151.96 | 177.6325 | 208.5 | 208.6 | 223.1 | 224.2 | 404.2 | 21 | 21.6 | 43.3 | 4.4 | 203.4 | 10.4 | 290.3 | 696 | 594.8 | 381.5 | 866.1 | 626.6 | 532.9
1019 | 142 | 380 | 152 | 177.6792 | 207.6 | 208.9 | 223.9 | 225.2 | 402.5 | 21 | 21.6 | 43.4 | 4.7 | 201.2 | 9.4 | 291.1 | 694.5 | 583.9 | 384.2 | 866.6 | 612.1 | 529.2
1020 | 143 | 380.8 | 152.32 | 178.0533 | 208.8 | 208.9 | 224.7 | 225.9 | 398.4 | 21.1 | 21.6 | 43.4 | 4.4 | 239.2 | 8.9 | 288.3 | 691 | 570.8 | 387.3 | 860.6 | 597.3 | 526.4
1021 | 144 | 380.2 | 152.08 | 177.7728 | 209.9 | 208.6 | 225.8 | 226.7 | 396.5 | 21.1 | 21.6 | 43.5 | 3.9 | 226.8 | 9.2 | 287.3 | 687.1 | 564.7 | 390.4 | 869.1 | 588.1 | 524.4
1022 | 145 | 380.1 | 152.04 | 177.726 | 209.3 | 208.1 | 226.6 | 226.8 | 395.4 | 21.2 | 21.6 | 43.5 | 4.4 | 227.8 | 9.6 | 287.8 | 681.6 | 571.9 | 393 | 865.4 | 581.3 | 531.4
1023 | 146 | 380.2 | 152.08 | 177.7728 | 209 | 208.5 | 226.9 | 227.1 | 397.6 | 21.2 | 21.6 | 43.6 | 3.8 | 232.6 | 10.8 | 289 | 680.1 | 578.3 | 395.3 | 863.1 | 588.5 | 535.9
1024 | 147 | 381.3 | 152.52 | 178.2871 | 208.7 | 208.9 | 226.8 | 227.8 | 397 | 21.2 | 21.6 | 43.7 | 3.4 | 231.1 | 11.4 | 289.9 | 670.6 | 592.7 | 397.4 | 854.2 | 604.3 | 544.3
1025 | 148 | 379.8 | 151.92 | 177.5857 | 209.7 | 209.9 | 227.1 | 228.9 | 391.4 | 21.2 | 21.6 | 43.8 | 3.5 | 245.4 | 12.3 | 290.9 | 673 | 605.8 | 399.6 | 850.5 | 604.4 | 546.8
1026 | 149 | 380.4 | 152.16 | 177.8663 | 210 | 210.8 | 227.3 | 229.3 | 389.2 | 21.3 | 21.6 | 43.8 | 3.2 | 238.7 | 11.9 | 292.1 | 679.5 | 617.2 | 401.9 | 852.6 | 606.1 | 552.9
1027 | 150 | 379.8 | 151.92 | 177.5857 | 209.7 | 211.3 | 227.5 | 229.6 | 386.8 | 21.3 | 21.6 | 44 | 3.9 | 245.1 | 10.1 | 292.6 | 692.3 | 622.3 | 404.3 | 858.5 | 597.8 | 555.6
1028 | 151 | 379.7 | 151.88 | 177.539 | 210 | 211 | 227.5 | 229.7 | 389 | 21.3 | 21.6 | 44.2 | 4.4 | 232 | 8.7 | 293.7 | 701 | 626.7 | 406.7 | 863.9 | 587.8 | 558.1
1029 | 152 | 378.2 | 151.28 | 176.8376 | 209.6 | 211.7 | 227.9 | 229.4 | 395.3 | 21.4 | 21.6 | 44.5 | 4.2 | 228.8 | 9 | 294.5 | 706.2 | 626.5 | 409.3 | 877.4 | 587.2 | 555.8
1030 | 153 | 376.9 | 150.76 | 176.2298 | 210.7 | 212.7 | 228.4 | 229.1 | 404.7 | 21.4 | 21.6 | 44.6 | 4.2 | 242.1 | 9.5 | 295 | 711.8 | 627.1 | 412.1 | 884.6 | 584.5 | 557.2
1031 | 154 | 379.5 | 151.8 | 177.4455 | 212 | 213.1 | 228.6 | 229 | 413.5 | 21.4 | 21.6 | 44.7 | 3.4 | 236.6 | 9.4 | 296 | 710.1 | 625.2 | 415 | 895.2 | 595 | 557.2
1032 | 155 | 379 | 151.6 | 177.2117 | 211.7 | 213.4 | 229.1 | 228.9 | 421.9 | 21.4 | 21.6 | 44.9 | 3.6 | 251.1 | 9.6 | 298.2 | 703.2 | 628 | 418.2 | 893.7 | 587.2 | 559.5
1033 | 156 | 379.5 | 151.8 | 177.4455 | 211.1 | 214.1 | 229.6 | 229 | 415.9 | 21.4 | 21.6 | 45 | 3.1 | 239.5 | 9.1 | 302.1 | 707.8 | 641.2 | 421.7 | 887 | 592.8 | 569.4
1034 | 157 | 379.3 | 151.72 | 177.3519 | 211.3 | 214.6 | 230.1 | 229.6 | 408.2 | 21.5 | 21.6 | 45.1 | 3 | 239.4 | 9.1 | 305.2 | 709.7 | 647.1 | 425 | 881.4 | 594.4 | 571.1
1035 | 158 | 379.7 | 151.88 | 177.539 | 211.2 | 215.7 | 230.5 | 229 | 401.8 | 21.5 | 21.6 | 45 | 3.1 | 240.6 | 10.4 | 308.6 | 721.5 | 654.8 | 428.2 | 871.8 | 582.8 | 577
1036 | 159 | 379 | 151.6 | 177.2117 | 210.4 | 216.1 | 231 | 228.7 | 401.9 | 21.5 | 21.6 | 45 | 3.1 | 246.6 | 10.2 | 311.7 | 727.2 | 660.4 | 431.4 | 869.6 | 575.7 | 583
1037 | 160 | 378.7 | 151.48 | 177.0714 | 210.7 | 216 | 230.9 | 228.4 | 403.8 | 21.5 | 21.5 | 45.1 | 3.4 | 229.4 | 8.3 | 314.5 | 736.7 | 646.8 | 434.6 | 876.9 | 566.9 | 577.4
1038 | 161 | 378.7 | 151.48 | 177.0714 | 210.3 | 216.3 | 230.3 | 228.5 | 404.9 | 21.5 | 21.5 | 45.1 | 3.2 | 219.9 | 7.5 | 317.7 | 744.7 | 643.5 | 438 | 883 | 563.2 | 574.6
1039 | 162 | 378.6 | 151.44 | 177.0246 | 210.1 | 216.6 | 230.2 | 229.1 | 407.9 | 21.5 | 21.5 | 45.1 | 3.1 | 227.7 | 7.7 | 320.7 | 747.6 | 641.6 | 441.6 | 879.5 | 565.9 | 576.1
1040 | 163 | 379.3 | 151.72 | 177.3519 | 210 | 217.3 | 230.5 | 229.3 | 405.1 | 21.5 | 21.5 | 45.2 | 3.6 | 237.7 | 7.4 | 323.7 | 751.3 | 640.3 | 444.8 | 876.5 | 560.7 | 579.9
1041 | 164 | 380.4 | 152.16 | 177.8663 | 211.1 | 218 | 230.6 | 228.8 | 406.1 | 21.6 | 21.5 | 45.2 | 3.5 | 239.4 | 6.6 | 326 | 751.4 | 640 | 448.3 | 872.5 | 560.1 | 579.8
1042 | 165 | 379.8 | 151.92 | 177.5857 | 211.6 | 218.3 | 231.2 | 228.4 | 412.8 | 21.7 | 21.5 | 45.2 | 3.6 | 216 | 7.1 | 327.1 | 750 | 651.4 | 451.2 | 869.9 | 563.8 | 585.3
1043 | 166 | 378.8 | 151.52 | 177.1181 | 210.9 | 218.5 | 231.7 | 228.4 | 410 | 21.7 | 21.5 | 45.3 | 3.7 | 221.2 | 6.5 | 328.6 | 753.8 | 649.1 | 453.9 | 868.8 | 570 | 586.6
1044 | 167 | 379.7 | 151.88 | 177.539 | 211 | 218.5 | 231.8 | 229.5 | 405 | 21.8 | 21.5 | 45.4 | 3.8 | 186.9 | 6.4 | 332.4 | 757.5 | 646.1 | 456.9 | 871.2 | 579.9 | 583.1
1045 | 168 | 380.5 | 152.2 | 177.913 | 210.9 | 218.9 | 232.7 | 230 | 404.7 | 21.8 | 21.5 | 45.6 | 3.8 | 224.7 | 7.8 | 335.8 | 747.9 | 656.5 | 460 | 861.3 | 589.9 | 589.8
1046 | 169 | 380.7 | 152.28 | 178.0065 | 211.5 | 218.3 | 233 | 230.6 | 404.3 | 21.8 | 21.5 | 45.8 | 3.5 | 201 | 7.3 | 338.6 | 736.7 | 664.1 | 462.8 | 848 | 602.2 | 598.1
1047 | 170 | 380 | 152 | 177.6792 | 212.8 | 218.2 | 233 | 230.9 | 404.9 | 21.9 | 21.5 | 45.9 | 3.6 | 199.7 | 7.4 | 341.2 | 745.6 | 678.1 | 465.6 | 855.8 | 599.7 | 610.3
1048 | 171 | 378.8 | 151.52 | 177.1181 | 213 | 218.7 | 233.4 | 230.8 | 408.1 | 21.9 | 21.5 | 46 | 3.4 | 205.8 | 8.9 | 344.2 | 749.1 | 672.9 | 468.9 | 869.5 | 609.1 | 610.2
1049 | 172 | 377.7 | 151.08 | 176.6038 | 212.7 | 219.5 | 234 | 231.2 | 418.6 | 21.9 | 21.5 | 46.2 | 3.8 | 197.2 | 8.8 | 346.6 | 745.2 | 670.2 | 472.6 | 877.4 | 613.2 | 606.7
1050 | 173 | 378 | 151.2 | 176.7441 | 214.3 | 220.5 | 234.4 | 231.7 | 426.4 | 22 | 21.5 | 46.3 | 3.8 | 166.7 | 7 | 347.9 | 747.6 | 666.4 | 476.7 | 867.2 | 616.1 | 610.1
1051 | 174 | 376.9 | 150.76 | 176.2298 | 215.6 | 221.3 | 234.5 | 232.3 | 419.9 | 22 | 21.5 | 46.3 | 3.5 | 210 | 5.5 | 351.4 | 746.7 | 657.5 | 480.9 | 873.7 | 608.6 | 603.5
1052 | 175 | 378.6 | 151.44 | 177.0246 | 215 | 221.2 | 234.5 | 232.4 | 419.9 | 22.1 | 21.5 | 46.4 | 3.6 | 237.3 | 4.5 | 354.9 | 751.5 | 651.6 | 485.7 | 872.1 | 605.9 | 601.7
1053 | 176 | 378.8 | 151.52 | 177.1181 | 214.4 | 221 | 234.8 | 232.4 | 419.1 | 22.1 | 21.5 | 46.4 | 3.4 | 241.5 | 5.1 | 357 | 758.1 | 632.3 | 490.3 | 874 | 603.4 | 594
1054 | 177 | 379.8 | 151.92 | 177.5857 | 213.8 | 221.2 | 234.7 | 232.6 | 419.1 | 22.1 | 21.5 | 46.4 | 4.2 | 243.8 | 5.9 | 358.5 | 752.5 | 629.3 | 494.4 | 878.1 | 607.3 | 594.6
1055 | 178 | 378.1 | 151.24 | 176.7908 | 214.2 | 221.6 | 234.7 | 233.3 | 420.2 | 22.2 | 21.5 | 46.5 | 4.2 | 263.8 | 6.1 | 360.9 | 739.5 | 617.9 | 498.3 | 886.2 | 609 | 592.5
1056 | 179 | 378.8 | 151.52 | 177.1181 | 215.2 | 221.5 | 233.9 | 233.6 | 418.8 | 22.2 | 21.5 | 46.5 | 4.5 | 251.6 | 6.2 | 363.7 | 730.6 | 617.8 | 502 | 885.5 | 621.2 | 592.4
1057 | 180 | 378.9 | 151.56 | 177.1649 | 215.8 | 222.1 | 233.4 | 234.2 | 413.2 | 22.2 | 21.5 | 46.5 | 4.5 | 234.6 | 7.3 | 366.4 | 722.2 | 619.4 | 505.7 | 885.3 | 622.9 | 598.2
1058 | 181 | 379.9 | 151.96 | 177.6325 | 215.9 | 223.2 | 233.3 | 234.5 | 409.2 | 22.3 | 21.5 | 46.6 | 3.9 | 199.8 | 5.8 | 368.5 | 710.4 | 612.5 | 509.5 | 880.1 | 624.5 | 593.6
1059 | 182 | 379.3 | 151.72 | 177.3519 | 215.8 | 224.2 | 233.5 | 234.5 | 408.2 | 22.3 | 21.5 | 46.6 | 3.5 | 204.6 | 4.2 | 370.7 | 696.4 | 612.7 | 513.4 | 870.5 | 625.6 | 590.6
1060 | 183 | 379.1 | 151.64 | 177.2584 | 215.3 | 224.5 | 233.9 | 234.7 | 407.1 | 22.3 | 21.5 | 46.7 | 3.5 | 255.7 | 5.9 | 373.3 | 689 | 618.6 | 517.2 | 861.5 | 637 | 592.7
1061 | 184 | 378.6 | 151.44 | 177.0246 | 215.9 | 224.3 | 234.5 | 234.8 | 406.9 | 22.4 | 21.5 | 46.7 | 3.1 | 234.4 | 7.4 | 375.8 | 686.6 | 625 | 521.2 | 863 | 646.8 | 595.4
1062 | 185 | 379.7 | 151.88 | 177.539 | 216.6 | 224.6 | 234.7 | 235.4 | 407.6 | 22.4 | 21.5 | 46.7 | 2.9 | 234.8 | 8 | 379.5 | 683.9 | 633.4 | 526.1 | 846.8 | 656.1 | 601.8
1063 | 186 | 378.8 | 151.52 | 177.1181 | 217 | 224.7 | 234.4 | 235.4 | 408.3 | 22.4 | 21.5 | 46.8 | 3.4 | 260.4 | 8.1 | 383 | 671 | 629.1 | 531 | 848.2 | 670.8 | 600.5
1064 | 187 | 379.7 | 151.88 | 177.539 | 217.1 | 224.6 | 234.2 | 235.4 | 408.2 | 22.4 | 21.5 | 47 | 3.8 | 231 | 8.6 | 386.3 | 670.3 | 641.6 | 535.6 | 854.4 | 678.8 | 604.7
1065 | 188 | 380.4 | 152.16 | 177.8663 | 217.9 | 224.9 | 234.5 | 236 | 407 | 22.4 | 21.5 | 47.2 | 3.6 | 207.8 | 8.5 | 388.3 | 676.6 | 645.8 | 539.7 | 847.8 | 670.3 | 607.8
1066 | 189 | 378.7 | 151.48 | 177.0714 | 217.4 | 225.5 | 235.2 | 236.5 | 404.2 | 22.5 | 21.5 | 47.3 | 3.5 | 221.9 | 7 | 390.1 | 663.6 | 649.6 | 543.7 | 848.1 | 675.9 | 610.5
1067 | 190 | 379.1 | 151.64 | 177.2584 | 217.6 | 225 | 235 | 236.3 | 404.6 | 22.5 | 21.5 | 47.5 | 3.6 | 244.6 | 6.6 | 392.8 | 651.7 | 648.4 | 547.4 | 856 | 684 | 612.9
1068 | 191 | 379.7 | 151.88 | 177.539 | 218.2 | 224.6 | 234.8 | 236.1 | 404.7 | 22.5 | 21.5 | 47.6 | 3.9 | 255.7 | 6.6 | 394.9 | 647.7 | 631.4 | 551 | 864.2 | 683.1 | 602.6
1069 | 192 | 379.4 | 151.76 | 177.3987 | 219.2 | 225.4 | 235.2 | 236.5 | 409.6 | 22.6 | 21.5 | 47.7 | 4 | 277.9 | 6.6 | 396.8 | 636.8 | 623.4 | 554.8 | 865.2 | 679.1 | 600.3
1070 | 193 | 379.4 | 151.76 | 177.3987 | 219.6 | 226 | 235.9 | 236.4 | 406.9 | 22.6 | 21.5 | 47.7 | 3.8 | 254.5 | 6.6 | 401 | 636.2 | 625.4 | 559 | 856.8 | 680.8 | 598.3
1071 | 194 | 379.8 | 151.92 | 177.5857 | 219.6 | 226.2 | 236.1 | 236.4 | 403.4 | 22.6 | 21.5 | 47.8 | 3.6 | 255.7 | 6.2 | 405.6 | 632.2 | 623.6 | 562.8 | 850.3 | 696.3 | 603.5
1072 | 195 | 378.8 | 151.52 | 177.1181 | 219.4 | 226.1 | 236.2 | 236.6 | 401 | 22.7 | 21.5 | 47.9 | 4.1 | 266.3 | 5.9 | 409.4 | 621.3 | 629.8 | 566.5 | 853.3 | 702.2 | 609.3
1073 | 196 | 378.8 | 151.52 | 177.1181 | 218.8 | 225.5 | 236 | 236.3 | 405.3 | 22.7 | 21.5 | 48.1 | 3.7 | 274.7 | 5.3 | 414.6 | 618 | 638.8 | 570.5 | 854.7 | 710.5 | 616.2
1074 | 197 | 378.7 | 151.48 | 177.0714 | 218 | 225.4 | 235.7 | 236.1 | 401 | 22.8 | 21.5 | 48.1 | 3.4 | 237.6 | 4.9 | 418.7 | 615.4 | 628 | 574.7 | 852 | 705.9 | 612.1
1075 | 198 | 377.5 | 151 | 176.5103 | 217.9 | 225.7 | 235 | 235.7 | 395.9 | 22.8 | 21.5 | 48.2 | 3.6 | 231.6 | 5.3 | 420.6 | 615.4 | 624.1 | 579.1 | 851.5 | 693 | 603.7
1076 | 199 | 378 | 151.2 | 176.7441 | 218.6 | 226.8 | 235.2 | 235.4 | 395.8 | 22.9 | 21.5 | 48.3 | 3.3 | 253.2 | 6.1 | 422.4 | 619.3 | 631.1 | 583 | 846.9 | 685.1 | 609.5
1077 | 200 | 378.2 | 151.28 | 176.8376 | 220.1 | 227 | 235.2 | 235.1 | 401.9 | 22.9 | 21.4 | 48.4 | 3.9 | 238.8 | 6.3 | 424.4 | 621.5 | 625.7 | 586.5 | 838 | 672.5 | 609.3
1078 | 201 | 377.3 | 150.92 | 176.4168 | 220.6 | 227 | 235.9 | 234.8 | 401.4 | 23 | 21.4 | 48.5 | 3.8 | 234.4 | 6.8 | 426.9 | 625.7 | 621.4 | 589.9 | 834.4 | 665.6 | 604.7
1079 | 202 | 378.4 | 151.36 | 176.9311 | 219.8 | 227 | 235.8 | 235.7 | 403.8 | 23 | 21.4 | 48.7 | 3.9 | 267.2 | 9.5 | 430.3 | 632.8 | 623.8 | 593 | 845.5 | 652.6 | 604.2
1080 | 203 | 379 | 151.6 | 177.2117 | 219.2 | 227.1 | 236.5 | 236.4 | 404.7 | 23.1 | 21.4 | 48.9 | 4 | 264.8 | 9.5 | 434.2 | 632.6 | 623.5 | 596.3 | 854.5 | 642.9 | 603.2
1081 | 204 | 379.1 | 151.64 | 177.2584 | 219.5 | 226.7 | 236.5 | 236.1 | 405.2 | 23.1 | 21.4 | 49 | 3.5 | 255.3 | 9.4 | 438.5 | 633 | 617.1 | 599.3 | 857.3 | 642.6 | 602.7
1082 | 205 | 378.7 | 151.48 | 177.0714 | 220 | 226.2 | 236.1 | 236.6 | 407.3 | 23.2 | 21.4 | 49.2 | 3.5 | 259.8 | 9.7 | 443.5 | 622.9 | 601.2 | 602.3 | 851.5 | 646.1 | 597.1
1083 | 206 | 378.9 | 151.56 | 177.1649 | 221.4 | 226.1 | 235.1 | 237.7 | 413.7 | 23.2 | 21.4 | 49.5 | 3.8 | 249.7 | 9.8 | 449.3 | 618.7 | 604.1 | 605 | 858.7 | 664.2 | 600.5
1084 | 207 | 378.2 | 151.28 | 176.8376 | 222.7 | 226.1 | 234.6 | 238.4 | 415.4 | 23.2 | 21.4 | 49.6 | 4.4 | 243.7 | 10 | 455 | 635.6 | 614.6 | 607.6 | 869.5 | 676.8 | 611.9
1085 | 208 | 379.1 | 151.64 | 177.2584 | 222.9 | 227 | 234.6 | 237.7 | 415.9 | 23.2 | 21.4 | 49.7 | 4.5 | 236 | 8.5 | 458.3 | 635 | 623.8 | 610.6 | 869.9 | 673.8 | 615.6
1086 | 209 | 378.4 | 151.36 | 176.9311 | 222.9 | 227.9 | 234.6 | 237.6 | 418.2 | 23.3 | 21.4 | 49.8 | 5 | 241.1 | 8.3 | 461.2 | 629.3 | 633.5 | 614 | 870.7 | 678.3 | 616.6
1087 | 210 | 378.1 | 151.24 | 176.7908 | 222.8 | 228.8 | 235 | 238.2 | 419.5 | 23.3 | 21.4 | 50 | 4.7 | 237.2 | 7.8 | 463.3 | 623.1 | 636.6 | 617.5 | 866.9 | 674.9 | 619.2
1088 | 211 | 379.3 | 151.72 | 177.3519 | 223.1 | 229.6 | 235 | 238.6 | 414 | 23.3 | 21.4 | 50.1 | 5.5 | 259.8 | 7.6 | 465.2 | 622.2 | 625.9 | 621.1 | 862.5 | 663 | 608.8
1089 | 212 | 380.3 | 152.12 | 177.8195 | 223.1 | 229.3 | 235.3 | 239 | 408.9 | 23.3 | 21.4 | 50.2 | 5.1 | 241.6 | 7.3 | 466.6 | 619.6 | 624.7 | 624.8 | 859.6 | 660.5 | 607
1090 | 213 | 380.5 | 152.2 | 177.913 | 223.9 | 229.4 | 235.2 | 238.5 | 408 | 23.3 | 21.4 | 50.3 | 3.9 | 242.1 | 7.5 | 468.4 | 615.7 | 624.2 | 628.1 | 851.6 | 673.2 | 609.2
1091 | 214 | 380.5 | 152.2 | 177.913 | 224 | 229.7 | 235.7 | 238.5 | 411.4 | 23.3 | 21.4 | 50.3 | 3.4 | 244.2 | 8 | 470.9 | 606.4 | 621.8 | 631.3 | 843 | 674.4 | 607.3
1092 | 215 | 379.6 | 151.84 | 177.4922 | 223.8 | 229.8 | 235.9 | 238.8 | 412.9 | 23.4 | 21.4 | 50.4 | 3.5 | 242 | 8.3 | 473.7 | 604.6 | 615.4 | 634.5 | 847.4 | 676.7 | 607.8
1093 | 216 | 379 | 151.6 | 177.2117 | 224.1 | 229.5 | 236.4 | 239 | 410.7 | 23.4 | 21.4 | 50.5 | 3.8 | 231 | 7.6 | 476.4 | 611 | 612.5 | 638 | 852.8 | 661.9 | 606.2
1094 | 217 | 379.8 | 151.92 | 177.5857 | 223.8 | 229.7 | 236.6 | 238.7 | 408 | 23.4 | 21.4 | 50.6 | 3.9 | 257.8 | 8.9 | 478.9 | 618.5 | 602 | 641.8 | 840.1 | 633.9 | 598.8
1095 | 218 | 380 | 152 | 177.6792 | 223.4 | 229.5 | 237.2 | 238.6 | 401.7 | 23.5 | 21.4 | 50.7 | 3.8 | 246.6 | 8.1 | 483 | 622.8 | 594.5 | 645.8 | 833.3 | 625.8 | 595.7
1096 | 219 | 379.6 | 151.84 | 177.4922 | 223 | 229.6 | 237.3 | 238.4 | 396.8 | 23.5 | 21.4 | 50.9 | 3.6 | 238.5 | 7.7 | 486.5 | 631.6 | 577 | 649.4 | 823.5 | 607.2 | 588.3
1097 | 220 | 380 | 152 | 177.6792 | 222.9 | 229.1 | 237.3 | 237.8 | 393.5 | 23.6 | 21.4 | 51 | 3.3 | 241.9 | 9 | 490 | 635.6 | 557.8 | 653.1 | 800.1 | 584.8 | 582
1098 | 221 | 379.6 | 151.84 | 177.4922 | 223.7 | 228.6 | 237.5 | 238.1 | 386 | 23.7 | 21.4 | 51 | 3.3 | 249.7 | 8.5 | 494.5 | 637.2 | 545.8 | 656.5 | 803.1 | 569.8 | 581.1
1099 | 222 | 378.2 | 151.28 | 176.8376 | 224.7 | 227.8 | 237.4 | 237.9 | 380 | 23.8 | 21.4 | 51 | 3.3 | 232.4 | 8.5 | 498 | 633.4 | 533.5 | 659.2 | 804 | 563.3 | 580.1
1100 | 223 | 376.7 | 150.68 | 176.1362 | 225.6 | 226.8 | 236.8 | 237.6 | 378 | 23.9 | 21.4 | 51 | 3.5 | 222.9 | 8.8 | 501.9 | 624.7 | 534.1 | 661.2 | 806.2 | 563.7 | 580.9
1101 | 224 | 376.5 | 150.6 | 176.0427 | 226.2 | 226 | 237.2 | 236.9 | 378.2 | 24 | 21.4 | 51.1 | 3.3 | 224 | 8.6 | 505.7 | 616.2 | 534.5 | 662.6 | 802.1 | 556.5 | 582.8
1102 | 225 | 377.5 | 151 | 176.5103 | 227.3 | 225.7 | 237.5 | 236.9 | 374.2 | 24.1 | 21.4 | 51.2 | 3.9 | 201.3 | 7.7 | 508.8 | 612.1 | 532.5 | 663.7 | 811.5 | 577.3 | 583
1103 | 226 | 377.6 | 151.04 | 176.5571 | 227.2 | 225.9 | 237.4 | 236.8 | 373.8 | 24.2 | 21.4 | 51.4 | 4.5 | 230.5 | 6.1 | 511.7 | 608.8 | 532.5 | 665 | 820.8 | 587.8 | 584.3
1104 | 227 | 377.4 | 150.96 | 176.4635 | 227.6 | 226.2 | 237.6 | 236.9 | 370.5 | 24.2 | 21.4 | 51.5 | 4.7 | 259.7 | 6.5 | 516.5 | 603.8 | 527.2 | 666.8 | 817.2 | 583.1 | 580.4
1105 | 228 | 379.3 | 151.72 | 177.3519 | 229 | 226.6 | 237.6 | 236.8 | 370.4 | 24.3 | 21.4 | 51.5 | 5.1 | 234.5 | 6.9 | 529.3 | 603.5 | 524 | 668.7 | 832.4 | 579.2 | 577.1
1106 | 229 | 378.5 | 151.4 | 176.9779 | 229.6 | 227.4 | 237.6 | 236.9 | 373.2 | 24.4 | 21.4 | 51.5 | 4.4 | 230 | 6.3 | 539.7 | 610.5 | 525.8 | 670.9 | 844.3 | 567.8 | 577
1107 | 230 | 379.2 | 151.68 | 177.3052 | 229.5 | 228 | 236.9 | 237.2 | 376.7 | 24.4 | 21.4 | 51.6 | 4 | 249.7 | 7 | 548.3 | 617 | 530.1 | 673.1 | 855.5 | 557.9 | 578.7
1108 | 231 | 378.4 | 151.36 | 176.9311 | 229.2 | 228 | 236.5 | 237.1 | 377.2 | 24.5 | 21.4 | 51.7 | 3.7 | 240.2 | 8.3 | 555.9 | 615.2 | 524.2 | 675.2 | 848.2 | 564.8 | 576.3
1109 | 232 | 378.7 | 151.48 | 177.0714 | 228.5 | 227.3 | 237.3 | 237.8 | 377.3 | 24.5 | 21.3 | 51.7 | 3.9 | 242.3 | 9.4 | 562.2 | 611.8 | 520.1 | 677.7 | 841 | 566.2 | 574.4
1110 | 233 | 379 | 151.6 | 177.2117 | 228 | 227.5 | 237.7 | 238.4 | 373.2 | 24.6 | 21.3 | 51.8 | 3.8 | 251.2 | 9.7 | 567.7 | 610.3 | 527.6 | 679.8 | 838.9 | 572.3 | 574.1
1111 | 234 | 379.6 | 151.84 | 177.4922 | 228.2 | 228 | 238.2 | 238.9 | 373.6 | 24.7 | 21.3 | 51.9 | 4.1 | 253.7 | 8.4 | 572.3 | 608.3 | 526.5 | 681.9 | 838.7 | 574.3 | 574.6
1112 | 235 | 379 | 151.6 | 177.2117 | 228.6 | 228.7 | 238 | 239.4 | 376.2 | 24.8 | 21.3 | 52 | 4.5 | 271.4 | 7 | 576.3 | 606 | 523.6 | 684.3 | 824.8 | 578.2 | 575
1113 | 236 | 378.5 | 151.4 | 176.9779 | 228.7 | 229 | 237.6 | 240.1 | 374.6 | 24.9 | 21.3 | 52.1 | 4.6 | 286.4 | 5.9 | 579.7 | 605.2 | 515.7 | 686.7 | 822.2 | 571.3 | 571.9
1114 | 237 | 378.6 | 151.44 | 177.0246 | 228.6 | 228.7 | 237 | 240 | 372.9 | 24.9 | 21.3 | 52.2 | 4.1 | 272.7 | 5.7 | 582.6 | 603.4 | 517.7 | 688.8 | 829.9 | 579.7 | 572.4
1115 | 238 | 379.5 | 151.8 | 177.4455 | 228.6 | 229 | 236.8 | 239.9 | 376.2 | 25 | 21.3 | 52.3 | 4.1 | 251.6 | 5.6 | 585.3 | 600.7 | 519.6 | 690.6 | 838.4 | 587.2 | 573.9
1116 | 239 | 379.2 | 151.68 | 177.3052 | 228.6 | 229.7 | 237 | 239.7 | 382.8 | 25 | 21.3 | 52.4 | 4 | 267.9 | 8.4 | 588.4 | 600.3 | 528.9 | 692.5 | 846.7 | 603.8 | 573.7
1117 | 240 | 379.1 | 151.64 | 177.2584 | 228.1 | 229.8 | 237.1 | 240.1 | 386.8 | 25 | 21.3 | 52.4 | 3.6 | 270.9 | 11 | 591 | 602 | 537.4 | 694.3 | 846.5 | 616.4 | 578.2
1118 | 241 | 380.2 | 152.08 | 177.7728 | 228.2 | 230.3 | 237.5 | 240.2 | 386 | 25 | 21.3 | 52.5 | 3.9 | 260.4 | 11 | 593.7 | 604.5 | 538.1 | 696.3 | 850.9 | 622.3 | 581.4
1119 | 242 | 380.4 | 152.16 | 177.8663 | 228.5 | 229.7 | 238 | 240.5 | 388.6 | 25 | 21.3 | 52.6 | 4.1 | 239.5 | 9.4 | 597.1 | 610.8 | 534.6 | 698.8 | 846.8 | 622.5 | 576.8
1120 | 243 | 380.1 | 152.04 | 177.726 | 229 | 229.4 | 238.4 | 240.7 | 385.4 | 25.1 | 21.3 | 52.7 | 4.1 | 230.1 | 8 | 599.7 | 613.8 | 537.7 | 701.5 | 836.6 | 621.5 | 576.3
1121 | 244 | 379.8 | 151.92 | 177.5857 | 229.4 | 229.6 | 238.2 | 240.9 | 378.3 | 25.2 | 21.3 | 52.7 | 3.4 | 257.8 | 8.2 | 601.1 | 616.9 | 537.3 | 704.1 | 827 | 619.3 | 575.1
1122 | 245 | 380.1 | 152.04 | 177.726 | 229.1 | 228.9 | 238.1 | 241.3 | 377.4 | 25.3 | 21.3 | 52.7 | 3.5 | 251.6 | 10.1 | 603.8 | 617.1 | 542.9 | 706.4 | 827.1 | 618.5 | 576.4
1123 | 246 | 379.9 | 151.96 | 177.6325 | 228.5 | 228.8 | 237.4 | 240.8 | 380.2 | 25.3 | 21.3 | 52.8 | 4.6 | 251.9 | 10.3 | 607.3 | 617.4 | 547.1 | 708.6 | 841.7 | 612.1 | 577.6
1124 | 247 | 379.9 | 151.96 | 177.6325 | 228.2 | 229.4 | 236.4 | 240.3 | 381.2 | 25.4 | 21.3 | 52.9 | 5.2 | 248.4 | 10.1 | 610.9 | 623.1 | 554.8 | 710.8 | 850.9 | 605.7 | 578.9
1125 | 248 | 379.4 | 151.76 | 177.3987 | 228.4 | 230.2 | 235.2 | 240 | 383.6 | 25.4 | 21.3 | 53.1 | 6.1 | 251.1 | 9.2 | 613.9 | 621.9 | 557.7 | 712.7 | 853.5 | 610.5 | 579
1126 | 249 | 379.2 | 151.68 | 177.3052 | 228.5 | 230.2 | 235 | 239.7 | 388.7 | 25.5 | 21.3 | 53.2 | 5.9 | 258.8 | 11.1 | 616.8 | 623.7 | 557.9 | 714.3 | 862.1 | 612 | 580.7
1127 | 250 | 378.2 | 151.28 | 176.8376 | 228.4 | 230.3 | 235.6 | 239.9 | 397.5 | 25.5 | 21.3 | 53.3 | 5.5 | 253.9 | 14.3 | 619.2 | 630.4 | 571 | 715.7 | 874.6 | 610.9 | 583.2
1128 | 251 | 379.3 | 151.72 | 177.3519 | 228.4 | 230.6 | 236.5 | 240.3 | 401.8 | 25.5 | 21.3 | 53.3 | 4.7 | 257.2 | 15.5 | 620.9 | 633 | 572.8 | 717.3 | 872.1 | 606 | 581.2
1129 | 252 | 378.5 | 151.4 | 176.9779 | 227.9 | 230.2 | 237.3 | 240.3 | 401.8 | 25.6 | 21.3 | 53.4 | 4.6 | 260.5 | 14.9 | 622.8 | 634.4 | 572.7 | 719.1 | 868.1 | 599.2 | 576.1
1130 | 253 | 379.7 | 151.88 | 177.539 | 227.5 | 229.3 | 237.2 | 241 | 397.1 | 25.6 | 21.3 | 53.5 | 4.2 | 255.9 | 14.6 | 624.3 | 631.4 | 570.3 | 721.5 | 851.6 | 592.6 | 573.2
1131 | 254 | 379.3 | 151.72 | 177.3519 | 227.8 | 228.6 | 237.5 | 241.5 | 394.3 | 25.7 | 21.3 | 53.5 | 4.3 | 255.6 | 13.8 | 626.1 | 631.1 | 569.6 | 723.5 | 851.4 | 592 | 573.6
1132 | 255 | 379.9 | 151.96 | 177.6325 | 228.3 | 229 | 238 | 241.7 | 394.4 | 25.7 | 21.3 | 53.5 | 5.2 | 257.9 | 14.3 | 628.4 | 633.4 | 574 | 724.6 | 858 | 612.6 | 576.5
1133 | 256 | 378.9 | 151.56 | 177.1649 | 228.4 | 229.7 | 238.2 | 241 | 396.8 | 25.8 | 21.3 | 53.6 | 5 | 257.1 | 12.3 | 629.8 | 634.8 | 574.2 | 726 | 850.6 | 608 | 576.3
1134 | 257 | 379.5 | 151.8 | 177.4455 | 228.3 | 230.5 | 238.5 | 240.9 | 396.7 | 25.8 | 21.3 | 53.6 | 4.6 | 251.4 | 12.3 | 632.1 | 636.4 | 580.1 | 727.2 | 862.7 | 620.2 | 580.2
1135 | 258 | 379.4 | 151.76 | 177.3987 | 228.3 | 231.5 | 238.6 | 241.2 | 399.5 | 25.8 | 21.3 | 53.5 | 4.4 | 248.9 | 12.1 | 633.9 | 635.5 | 581.7 | 728.8 | 860.1 | 626.9 | 581.1
1136 | 259 | 379.3 | 151.72 | 177.3519 | 228.7 | 232.1 | 238.6 | 241.3 | 397.9 | 25.8 | 21.3 | 53.3 | 4 | 252 | 11.6 | 634.3 | 632.5 | 587 | 730.7 | 838.3 | 623 | 582.3
1137 | 260 | 378.9 | 151.56 | 177.1649 | 229.1 | 233 | 239.1 | 241.4 | 395.2 | 25.9 | 21.3 | 53.3 | 4.5 | 267.4 | 12.2 | 635.1 | 630.3 | 578 | 733 | 826.9 | 615.1 | 577.5
1138 | 261 | 377.8 | 151.12 | 176.6506 | 229.7 | 232.5 | 239.4 | 241.6 | 390.8 | 25.9 | 21.3 | 53.4 | 4.6 | 249.8 | 12.3 | 635 | 624.3 | 564.1 | 735 | 817.2 | 616.4 | 572.6
1139 | 262 | 379.2 | 151.68 | 177.3052 | 229.4 | 232 | 239.8 | 241.7 | 386.1 | 26 | 21.3 | 53.4 | 5.3 | 257.1 | 12.4 | 634.7 | 614.9 | 551.2 | 736.3 | 812.1 | 610.3 | 568.4
1140 | 263 | 378.5 | 151.4 | 176.9779 | 229.4 | 231.8 | 240.4 | 241.6 | 379.1 | 26 | 21.3 | 53.4 | 5.7 | 252.9 | 12.1 | 634.7 | 606.4 | 541.8 | 737.7 | 804.8 | 596 | 567.7
1141 | 264 | 379.4 | 151.76 | 177.3987 | 229.9 | 232.2 | 240.5 | 241.5 | 375.8 | 26.1 | 21.3 | 53.6 | 5.4 | 233.2 | 10.7 | 635.5 | 603.1 | 538.3 | 739.1 | 807.1 | 594.6 | 567.3
1142 | 265 | 378.5 | 151.4 | 176.9779 | 229.9 | 232.7 | 240.4 | 241.1 | 373.4 | 26.1 | 21.3 | 53.7 | 5.1 | 255.7 | 9.3 | 636.1 | 606.9 | 541.7 | 740.4 | 802.6 | 584.1 | 569.3
1143 | 266 | 378.8 | 151.52 | 177.1181 | 230.6 | 232.8 | 240.2 | 240.8 | 373 | 26.1 | 21.3 | 53.8 | 5.8 | 248.2 | 9.6 | 636 | 609 | 533.5 | 741.8 | 787.9 | 577.1 | 565.7
1144 | 267 | 378.9 | 151.56 | 177.1649 | 231.1 | 232.4 | 239.9 | 240.9 | 371.5 | 26.2 | 21.3 | 53.9 | 5.7 | 265.2 | 9.5 | 635.4 | 605.7 | 522.6 | 742.6 | 767.3 | 568.7 | 563.3
1145 | 268 | 368 | 147.2 | 172.0683 | 231.1 | 232.3 | 239.6 | 240.7 | 369 | 26.2 | 21.3 | 53.9 | 5.5 | 235.7 | 9.2 | 635.6 | 604.4 | 516.2 | 743.3 | 767.1 | 561.5 | 561
1146 | 269 | 76.1 | 30.44 | 35.5826 | 231.3 | 232.1 | 238.9 | 240.3 | 369.2 | 26.3 | 21.3 | 54 | 4.8 | 239.8 | 9.1 | 635.4 | 605.3 | 511.9 | 743.9 | 750.1 | 556 | 559.5
1147 | 270 | -6.9 | 0 | 0 | 231.1 | 231.3 | 238.1 | 239.7 | 364.6 | 26.3 | 21.3 | 54 | 5.1 | 241.5 | 10.7 | 633.6 | 599.5 | 500 | 744.7 | 713.1 | 535.2 | 551.1
1148 | 271 | -6.9 | 0 | 0 | 230 | 230.6 | 237.2 | 239.1 | 354.3 | 26.3 | 21.3 | 54.1 | 5.4 | 243 | 12 | 631.2 | 589.8 | 479.3 | 744.9 | 664.3 | 509.4 | 542.4
1149 | 272 | -6.9 | 0 | 0 | 228.5 | 229 | 235.8 | 238.2 | 342.8 | 26.4 | 21.3 | 54.3 | 5.5 | 238.3 | 12.7 | 628.5 | 578.3 | 459.7 | 744.4 | 621.3 | 485.9 | 538
1150 | 273 | -6.9 | 0 | 0 | 226.6 | 227.1 | 233.8 | 236.8 | 332.4 | 26.4 | 21.2 | 54.3 | 4.7 | 253.9 | 11.2 | 625.2 | 566.4 | 440.7 | 743.4 | 586 | 464.2 | 533.2
1151 | 274 | -6.9 | 0 | 0 | 224.5 | 225.5 | 231.7 | 235.1 | 323.4 | 26.4 | 21.2 | 54.3 | 5.3 | 257.2 | 9.3 | 621 | 556.4 | 423 | 741.9 | 555.8 | 444.2 | 528.3
1152 | 275 | -6.9 | 0 | 0 | 221.7 | 223.4 | 229.4 | 232.8 | 315 | 26.4 | 21.2 | 54.2 | 4.3 | 272.1 | 8.6 | 617 | 546 | 406.9 | 740.3 | 528.4 | 426.5 | 523.5
1153 | 276 | -6.9 | 0 | 0 | 218.9 | 221.1 | 226.9 | 230.2 | 307.4 | 26.5 | 21.3 | 53.9 | 4.1 | 223.4 | 8.1 | 613 | 536.5 | 392.1 | 738.6 | 504.2 | 409.8 | 520.1
1154 | 277 | -6.9 | 0 | 0 | 215.9 | 219.1 | 223.9 | 227.3 | 300.3 | 26.6 | 21.2 | 53.5 | 3.1 | 249.4 | 7.3 | 608.6 | 527.8 | 378.2 | 736.7 | 483.2 | 394 | 516.1
1155 | 278 | -6.9 | 0 | 0 | 213.3 | 217 | 221.2 | 224.1 | 294 | 26.7 | 21.2 | 53 | 3.4 | 234.5 | 8.6 | 605 | 518.2 | 365.1 | 734.8 | 460.3 | 379.5 | 512
1156 | 279 | -6.9 | 0 | 0 | 211.6 | 214.7 | 218.5 | 221.1 | 288.4 | 26.7 | 21.2 | 52.5 | 3.7 | 247.5 | 9.2 | 601.8 | 508.3 | 353 | 732.8 | 441.4 | 366.7 | 508.3
1157 | 280 | -6.9 | 0 | 0 | 209.5 | 212.1 | 216.1 | 218.3 | 283.2 | 26.8 | 21.2 | 52 | 2.8 | 245.6 | 8.2 | 598.8 | 498.4 | 341.2 | 730.8 | 425.4 | 354.3 | 505.4
1158 | 281 | -6.9 | 0 | 0 | 206.7 | 209.5 | 213.8 | 215.6 | 277.9 | 26.8 | 21.2 | 51.5 | 2.9 | 222.9 | 7.4 | 595.5 | 489.7 | 330.2 | 728.5 | 409.5 | 342.6 | 502.3
1159 | 282 | -6.9 | 0 | 0 | 203.3 | 207 | 211.4 | 212.9 | 272.9 | 26.9 | 21.2 | 51 | 3 | 256.4 | 7 | 592.3 | 481.4 | 319.9 | 726.1 | 396.4 | 331.8 | 498.2
1160 | 283 | -6.9 | 0 | 0 | 201.1 | 204.5 | 208.9 | 210.3 | 268.1 | 26.9 | 21.2 | 50.6 | 3.2 | 226.1 | 6.6 | 589.2 | 473.7 | 310.5 | 723.9 | 382.1 | 321.2 | 493.8
1161 | 284 | -6.9 | 0 | 0 | 199.3 | 201.9 | 206.5 | 207.6 | 263.1 | 26.8 | 21.2 | 50.3 | 3.2 | 235.8 | 5.5 | 586.5 | 466.1 | 301.6 | 721.6 | 368.1 | 311.3 | 490.9
1162 | 285 | -6.9 | 0 | 0 | 197 | 199.5 | 204.3 | 205 | 258.4 | 26.8 | 21.2 | 49.9 | 2.6 | 267.7 | 4.7 | 584.1 | 458.6 | 293.8 | 719.3 | 354.9 | 302.6 | 488.4
1163 | 286 | -6.9 | 0 | 0 | 194.7 | 197.1 | 202.1 | 202.6 | 253.5 | 26.8 | 21.2 | 49.6 | 2.8 | 246.6 | 5.1 | 581.7 | 452 | 285.8 | 716.7 | 343.6 | 293.4 | 485
1164 | 287 | -6.9 | 0 | 0 | 192.1 | 194.9 | 200 | 199.9 | 248.8 | 26.8 | 21.2 | 49.2 | 3.3 | 242.1 | 7.2 | 579.7 | 445 | 278.7 | 714.2 | 331.4 | 285 | 482
1165 | 288 | -6.9 | 0 | 0 | 189.6 | 192.5 | 197.7 | 197.4 | 244.5 | 26.9 | 21.2 | 49 | 3.3 | 231 | 7.6 | 577.7 | 438.6 | 271.3 | 711.6 | 320.7 | 277.5 | 478.1
1166 | 289 | -6.9 | 0 | 0 | 187.5 | 190.4 | 195.4 | 194.9 | 240.6 | 26.8 | 21.2 | 48.7 | 3.2 | 252.3 | 8 | 575.8 | 432.7 | 264.4 | 708.9 | 310.7 | 270.7 | 473.9
1167 | 290 | -6.8 | 0 | 0 | 185.6 | 188.1 | 193.1 | 192.5 | 236.7 | 26.8 | 21.2 | 48.4 | 2.9 | 243.5 | 8.8 | 573.9 | 426.4 | 258 | 706.4 | 300.3 | 263.7 | 470.6
1168 | 291 | -6.9 | 0 | 0 | 183.7 | 185.9 | 190.7 | 190.1 | 233.2 | 26.8 | 21.2 | 48.2 | 3.1 | 241.8 | 8.9 | 572 | 418.7 | 252.3 | 703.8 | 290.8 | 257.3 | 467.7
1169 | 292 | -6.8 | 0 | 0 | 181.4 | 183.6 | 188.4 | 187.9 | 229.8 | 26.8 | 21.2 | 47.9 | 3.9 | 241.2 | 8.2 | 570.1 | 412.6 | 247 | 701.1 | 283 | 251.5 | 465.2
1170 | 293 | -6.8 | 0 | 0 | 179.4 | 181.5 | 186.2 | 185.8 | 226.7 | 26.8 | 21.2 | 47.6 | 4.5 | 260.7 | 8.1 | 568.5 | 406.1 | 241.9 | 698.4 | 275.9 | 245.2 | 462.1
1171 | 294 | -6.9 | 0 | 0 | 177.7 | 179.4 | 183.9 | 183.7 | 223.6 | 26.8 | 21.2 | 47.3 | 4 | 246.2 | 11 | 567 | 400.2 | 237.3 | 695.5 | 268.5 | 239.7 | 460.1
1172 | 295 | -6.9 | 0 | 0 | 176.2 | 177.5 | 181.8 | 181.5 | 220.5 | 26.8 | 21.2 | 47 | 3.5 | 258.1 | 11.3 | 565.3 | 393.6 | 232.6 | 692.6 | 261.5 | 234.1 | 457.2
1173 | 296 | -6.9 | 0 | 0 | 174.7 | 175.6 | 179.7 | 179.6 | 217.5 | 26.8 | 21.2 | 46.7 | 2.6 | 259.6 | 10.5 | 563.7 | 388.5 | 228.4 | 689.6 | 255.8 | 228.5 | 454.8
1174 | 297 | -6.9 | 0 | 0 | 173.1 | 173.6 | 177.8 | 177.6 | 214.6 | 26.8 | 21.2 | 46.4 | 2.2 | 241.9 | 11.9 | 562.1 | 384.2 | 224 | 686.5 | 250.7 | 222.9 | 453.3
1175 | 298 | -6.9 | 0 | 0 | 171.1 | 171.7 | 175.8 | 175.7 | 212 | 26.8 | 21.2 | 46.1 | 2.6 | 249.1 | 12.1 | 560.7 | 380.3 | 219.6 | 683.5 | 245.4 | 218 | 450
1176 | 299 | -6.9 | 0 | 0 | 169.1 | 170 | 173.8 | 173.9 | 209.3 | 26.8 | 21.2 | 45.8 | 2.6 | 257.6 | 11.7 | 559.2 | 376.3 | 215 | 680.5 | 238.9 | 213.7 | 446.1
1177 | 300 | -6.9 | 0 | 0 | 167.3 | 168.4 | 172 | 172.1 | 206.8 | 26.8 | 21.2 | 45.5 | 2.3 | 264.2 | 10.6 | 557.9 | 371.5 | 210.7 | 677.5 | 232.7 | 209.3 | 442.7
1178 | 301 | -6.9 | 0 | 0 | 165.6 | 166.8 | 170.2 | 170.4 | 204.6 | 26.8 | 21.2 | 45.3 | 2.7 | 262.8 | 9.6 | 556.5 | 367.4 | 206.8 | 674.8 | 226.9 | 205.4 | 440.1
1179 | 302 | -6.8 | 0 | 0 | 163.9 | 165.3 | 168.4 | 168.7 | 202.1 | 26.8 | 21.2 | 45 | 3.2 | 289.4 | 8.4 | 555 | 363.1 | 203.2 | 671.9 | 221.6 | 201.3 | 437.6
1180 | 303 | -6.8 | 0 | 0 | 162 | 163.9 | 166.8 | 167.1 | 199.9 | 26.9 | 21.2 | 44.8 | 2.7 | 237.2 | 6.5 | 553.4 | 358.1 | 199.7 | 669.1 | 216.6 | 197.2 | 434.9
1181 | 304 | -6.8 | 0 | 0 | 160.4 | 162.6 | 165.4 | 165.5 | 197.8 | 26.9 | 21.2 | 44.6 | 2.4 | 278.6 | 5.9 | 551.9 | 353.2 | 196.4 | 666.4 | 212.1 | 193.2 | 433.1
1182 | 305 | -6.8 | 0 | 0 | 158.9 | 161.2 | 164 | 164 | 195.9 | 26.9 | 21.2 | 44.3 | 2.3 | 233.9 | 5.3 | 550.1 | 348.4 | 193.3 | 663.6 | 208.6 | 189.4 | 430.3
1183 | 306 | -6.8 | 0 | 0 | 157.3 | 159.8 | 162.6 | 162.5 | 194 | 26.9 | 21.2 | 44.1 | 2.3 | 203.3 | 5.9 | 548.3 | 343.9 | 190.3 | 660.8 | 204.8 | 185.7 | 427.9
1184 | 307 | -6.8 | 0 | 0 | 156 | 158.4 | 161.2 | 161.1 | 192.2 | 26.8 | 21.2 | 43.9 | 3 | 229.5 | 5.9 | 546.5 | 340 | 187.4 | 657.9 | 201.6 | 182.4 | 426.2
1185 | 308 | -6.8 | 0 | 0 | 154.7 | 156.9 | 159.8 | 159.7 | 190.2 | 26.8 | 21.2 | 43.7 | 2.8 | 229.6 | 5.5 | 544.6 | 335.8 | 184.8 | 655.1 | 197.8 | 179.2 | 423.7
1186 | 309 | -6.8 | 0 | 0 | 153.6 | 155.6 | 158.4 | 158.4 | 188.4 | 26.8 | 21.2 | 43.5 | 2.5 | 199.8 | 7.1 | 542.6 | 331.9 | 182.2 | 652.5 | 193.8 | 175.9 | 421
1187 | 310 | -6.8 | 0 | 0 | 152.5 | 154.4 | 157.2 | 157 | 186.4 | 26.8 | 21.2 | 43.2 | 2.4 | 225.8 | 8.3 | 540.5 | 328 | 179.3 | 649.8 | 189.3 | 172.9 | 418.3
1188 | 311 | -6.8 | 0 | 0 | 151.4 | 153.2 | 155.8 | 155.6 | 184.6 | 26.7 | 21.2 | 43 | 2.6 | 238.9 | 7.6 | 538.3 | 324.4 | 176.4 | 647 | 185.5 | 170.3 | 416
1189 | 312 | -6.8 | 0 | 0 | 150.4 | 151.9 | 154.5 | 154.1 | 182.9 | 26.7 | 21.2 | 42.9 | 2.3 | 222.1 | 6.5 | 536 | 321.6 | 173.6 | 644 | 181.6 | 167.5 | 413.4
1190 | 313 | -6.8 | 0 | 0 | 149.4 | 150.7 | 153.3 | 152.7 | 181.3 | 26.7 | 21.2 | 42.7 | 2.4 | 235.2 | 6.4 | 533.6 | 318.5 | 170.9 | 641.2 | 177.4 | 164.7 | 410.8
1191 | 314 | -6.8 | 0 | 0 | 148.3 | 149.5 | 152.2 | 151.4 | 179.7 | 26.7 | 21.2 | 42.5 | 2.5 | 206.2 | 6.1 | 531 | 315.4 | 168.4 | 638.2 | 173.8 | 162.2 | 408.4
1192 | 315 | -6.8 | 0 | 0 | 147.1 | 148.3 | 151 | 150.1 | 178 | 26.7 | 21.2 | 42.3 | 2.4 | 201.5 | 6.8 | 528.4 | 312 | 166.2 | 635.3 | 171.3 | 159.7 | 405.8
1193 | 316 | -6.8 | 0 | 0 | 146.1 | 147.1 | 149.9 | 149 | 176.7 | 26.7 | 21.2 | 42.1 | 2.5 | 220.9 | 6.5 | 525.3 | 308.2 | 164 | 632.4 | 168.7 | 157.2 | 403.6
1194 | 317 | -6.8 | 0 | 0 | 145.1 | 146 | 148.7 | 147.8 | 175.4 | 26.7 | 21.2 | 41.8 | 2.4 | 262.9 | 5.7 | 522 | 304.8 | 161.4 | 629.7 | 165.1 | 154.5 | 400.2
1195 | 318 | -6.8 | 0 | 0 | 144.2 | 144.8 | 147.7 | 146.8 | 174.2 | 26.7 | 21.2 | 41.6 | 2.2 | 247.9 | 4.5 | 518.4 | 301.5 | 158.7 | 626.9 | 161.6 | 151.7 | 396.2
1196 | 319 | -6.8 | 0 | 0 | 143.4 | 143.8 | 146.6 | 145.8 | 173 | 26.7 | 21.2 | 41.5 | 2.3 | 220.4 | 3.9 | 514.6 | 298.5 | 156.3 | 623.9 | 158.2 | 149 | 392.7
1197 | 320 | -6.8 | 0 | 0 | 142.5 | 142.7 | 145.6 | 144.7 | 171.6 | 26.7 | 21.2 | 41.3 | 2.1 | 225.9 | 3.5 | 510.4 | 296.1 | 154 | 620.9 | 154.9 | 146.4 | 390.7
1198 | 321 | -6.8 | 0 | 0 | 141.6 | 141.6 | 144.6 | 143.7 | 170.1 | 26.7 | 21.2 | 41.1 | 2.4 | 236.4 | 3.5 | 506.3 | 293.8 | 151.6 | 618 | 152.5 | 144.1 | 388
1199 | 322 | -6.8 | 0 | 0 | 140.7 | 140.6 | 143.6 | 142.8 | 168.7 | 26.6 | 21.2 | 40.9 | 2.8 | 242.9 | 3.8 | 502.2 | 291.5 | 149.7 | 615.1 | 150.1 | 142 | 387.3
1200 | 323 | -6.8 | 0 | 0 | 139.9 | 139.7 | 142.6 | 141.9 | 167.5 | 26.6 | 21.2 | 40.7 | 2.8 | 255.7 | 4.6 | 498 | 288.6 | 147.8 | 612 | 147.7 | 139.3 | 385.8
1201 | 324 | -6.8 | 0 | 0 | 138.9 | 138.9 | 141.6 | 140.9 | 166.2 | 26.6 | 21.2 | 40.5 | 2.8 | 259.1 | 5.3 | 493.6 | 285.8 | 145.3 | 608.8 | 146.3 | 137 | 383.1
1202 | 325 | -6.8 | 0 | 0 | 137.8 | 138 | 140.6 | 139.9 | 165 | 26.6 | 21.2 | 40.4 | 2.5 | 267 | 6.7 | 489.1 | 282.1 | 143.2 | 605.5 | 144.8 | 134.8 | 380
1203 | 326 | -6.8 | 0 | 0 | 136.9 | 137.2 | 139.6 | 139 | 163.6 | 26.5 | 21.2 | 40.2 | 2.7 | 264 | 7.6 | 484.5 | 279.8 | 141.3 | 602.2 | 142 | 133.1 | 378.3
1204 | 327 | -6.8 | 0 | 0 | 136.1 | 136.3 | 138.7 | 138 | 162.4 | 26.5 | 21.2 | 40 | 3.4 | 264.7 | 7.5 | 480.1 | 277.7 | 139.5 | 598.9 | 139.8 | 131.6 | 377.2
1205 | 328 | -6.8 | 0 | 0 | 135.2 | 135.6 | 137.8 | 137.1 | 161.2 | 26.5 | 21.2 | 39.8 | 3.9 | 271.5 | 6.8 | 475.6 | 275.7 | 137.8 | 595.4 | 137.9 | 129.4 | 375.6
1206 | 329 | -6.7 | 0 | 0 | 134.4 | 134.7 | 136.9 | 136.3 | 160.1 | 26.5 | 21.2 | 39.6 | 3.9 | 259 | 6.3 | 471.1 | 273.4 | 135.9 | 591.9 | 136.2 | 127.7 | 374
1207 | 330 | -6 | 0 | 0 | 133.7 | 133.8 | 136 | 135.5 | 159.1 | 26.5 | 21.2 | 39.4 | 3.1 | 248.8 | 6.3 | 466.7 | 271.4 | 134.1 | 588.2 | 134.8 | 126.2 | 371.9
1208 | 331 | -6.4 | 0 | 0 | 132.9 | 133.1 | 135.2 | 134.7 | 158.2 | 26.4 | 21.2 | 39.2 | 3.4 | 242.1 | 5.7 | 462.4 | 269.8 | 132.3 | 584.6 | 133.7 | 124.9 | 370.3
1209 | 332 | -6.4 | 0 | 0 | 132.3 | 132.4 | 134.4 | 133.9 | 157.2 | 26.4 | 21.2 | 39.1 | 3.4 | 242.2 | 5.1 | 458.1 | 268 | 130.6 | 581 | 132.8 | 123.5 | 368.2
1210 | 333 | -6 | 0 | 0 | 131.6 | 131.8 | 133.7 | 133.1 | 156.4 | 26.4 | 21.2 | 38.9 | 3 | 222.8 | 5.4 | 453.9 | 266.6 | 128.9 | 577.5 | 132 | 121.9 | 366.6
1211 | 334 | -6.7 | 0 | 0 | 131 | 131.2 | 133 | 132.3 | 155.5 | 26.4 | 21.2 | 38.8 | 2.5 | 242.6 | 6.1 | 449.8 | 265.6 | 127.3 | 573.9 | 131.1 | 120.5 | 365.3
1212 | 335 | -6.8 | 0 | 0 | 130.3 | 130.6 | 132.3 | 131.6 | 154.6 | 26.4 | 21.2 | 38.6 | 2.8 | 241 | 7.6 | 445.8 | 264.9 | 125.6 | 570.5 | 130.3 | 119.2 | 363.4
1213 | 336 | -6.8 | 0 | 0 | 129.7 | 130 | 131.5 | 130.9 | 153.7 | 26.4 | 21.2 | 38.5 | 2.2 | 225.4 | 8.5 | 442 | 264.4 | 123.9 | 567 | 129.6 | 118 | 361.1
1214 | 337 | -6.8 | 0 | 0 | 129.2 | 129.3 | 130.8 | 130.2 | 152.9 | 26.4 | 21.2 | 38.3 | 1.9 | 221.3 | 9 | 438.2 | 264.1 | 122.2 | 563.7 | 128.8 | 116.8 | 359.5
1215 | 338 | -6.8 | 0 | 0 | 128.6 | 128.6 | 130.2 | 129.5 | 152.1 | 26.4 | 21.2 | 38.2 | 1.8 | 226.5 | 9.1 | 434.6 | 263.2 | 120.4 | 560.3 | 127.6 | 115.5 | 357.8
1216 | 339 | -6.7 | 0 | 0 | 128 | 128 | 129.5 | 128.8 | 151.3 | 26.4 | 21.2 | 38 | 2.3 | 232.2 | 9 | 431 | 261.6 | 119 | 557.1 | 126.4 | 114.4 | 356.3
1217 | 340 | -6.7 | 0 | 0 | 127.5 | 127.3 | 128.8 | 128.1 | 150.5 | 26.4 | 21.2 | 37.9 | 2.2 | 245.9 | 8 | 427.5 | 259.6 | 117.3 | 554 | 125 | 112.8 | 353.7
1218 | 341 | -6.7 | 0 | 0 | 126.9 | 126.7 | 128.2 | 127.5 | 149.6 | 26.4 | 21.2 | 37.7 | 2.3 | 244.4 | 6.9 | 424 | 257 | 115.6 | 550.9 | 123.4 | 111.3 | 350.7
1219 | 342 | -5.7 | 0 | 0 | 126.4 | 126.1 | 127.5 | 126.9 | 148.8 | 26.4 | 21.2 | 37.6 | 2 | 244.9 | 6.8 | 420.6 | 254.3 | 114.4 | 547.8 | 121.9 | 110 | 349.1
1220 | 343 | -6.3 | 0 | 0 | 125.9 | 125.4 | 126.8 | 126.3 | 148 | 26.4 | 21.2 | 37.5 | 2.3 | 236.9 | 6.9 | 417.2 | 251.6 | 113 | 544.8 | 120.1 | 108.9 | 347.7
1221 | 344 | -6.3 | 0 | 0 | 125.4 | 124.7 | 126.2 | 125.7 | 147.2 | 26.3 | 21.2 | 37.3 | 2.5 | 232.1 | 6.6 | 413.9 | 249.1 | 111.6 | 541.7 | 118.2 | 107.8 | 346.1
1222 | 345 | -6.4 | 0 | 0 | 124.9 | 124.1 | 125.6 | 125 | 146.5 | 26.3 | 21.2 | 37.2 | 2.6 | 245.8 | 5.9 | 410.6 | 247.5 | 110.2 | 538.7 | 116.8 | 106.6 | 345.3
1223 | 346 | -6.6 | 0 | 0 | 124.5 | 123.5 | 124.9 | 124.5 | 145.8 | 26.3 | 21.2 | 37.1 | 2.9 | 260.1 | 5.9 | 407.5 | 245.8 | 108.9 | 535.6 | 115.9 | 105.4 | 344.3
1224 | 347 | -6.8 | 0 | 0 | 124 | 123 | 124.3 | 124 | 145.1 | 26.2 | 21.2 | 37 | 2.6 | 249.1 | 5.9 | 404.4 | 244.3 | 107.5 | 532.5 | 115.2 | 104.4 | 342.8
1225 | 348 | -6.8 | 0 | 0 | 123.6 | 122.5 | 123.8 | 123.4 | 144.4 | 26.2 | 21.2 | 36.9 | 2.3 | 229.1 | 5.3 | 401.3 | 242.8 | 106.3 | 529.4 | 114.3 | 103.4 | 341.7
1226 | 349 | -6.8 | 0 | 0 | 123.1 | 121.9 | 123.2 | 122.9 | 143.7 | 26.2 | 21.2 | 36.8 | 2.7 | 227.6 | 5.3 | 398.4 | 241.1 | 105 | 526.3 | 113.8 | 102.4 | 340.1
1227 | 350 | -6.7 | 0 | 0 | 122.6 | 121.4 | 122.7 | 122.4 | 143 | 26.2 | 21.2 | 36.6 | 2.5 | 236.7 | 5.4 | 395.4 | 239.4 | 103.8 | 523.2 | 112.8 | 101.5 | 337.9
1228 | 351 | -6.5 | 0 | 0 | 122.2 | 121 | 122.1 | 121.9 | 142.4 | 26.1 | 21.2 | 36.5 | 2.4 | 244.4 | 5.7 | 392.6 | 237.7 | 102.6 | 520.1 | 111.9 | 100.5 | 336.4
1229 | 352 | -6.7 | 0 | 0 | 121.7 | 120.6 | 121.6 | 121.3 | 141.8 | 26.1 | 21.2 | 36.4 | 2.6 | 251.1 | 5.8 | 389.8 | 236.3 | 101.5 | 517 | 111.2 | 99.5 | 335.3
1230 | 353 | -6.8 | 0 | 0 | 121.3 | 120.1 | 121.1 | 120.8 | 141.1 | 26 | 21.3 | 36.3 | 2.5 | 270.3 | 6.1 | 387.1 | 234.8 | 100.5 | 513.9 | 110.4 | 98.4 | 333.8
1231 | 354 | -5 | 0 | 0 | 120.9 | 119.7 | 120.6 | 120.3 | 140.5 | 26 | 21.3 | 36.2 | 2.4 | 252.2 | 5.9 | 384.4 | 233.3 | 99.6 | 510.8 | 109.7 | 97.4 | 332.7
1232 | 355 | -3.3 | 0 | 0 | 120.4 | 119.2 | 120.2 | 119.8 | 139.9 | 26 | 21.3 | 36.1 | 2.5 | 231.9 | 5.5 | 381.7 | 231.9 | 98.6 | 507.8 | 109.2 | 96.4 | 331.6
1233 | 356 | -4.7 | 0 | 0 | 120 | 118.8 | 119.8 | 119.3 | 139.3 | 26 | 21.3 | 36.1 | 2.7 | 257.5 | 5.8 | 379.1 | 230.7 | 97.7 | 504.7 | 108.5 | 95.4 | 330.5
1234 | 357 | -5.5 | 0 | 0 | 119.6 | 118.2 | 119.3 | 118.9 | 138.8 | 26 | 21.3 | 36 | 2.6 | 249.9 | 6.7 | 376.6 | 229.4 | 96.9 | 501.7 | 107.7 | 94.4 | 329.1
1235 | 358 | -5.4 | 0 | 0 | 119.1 | 117.7 | 118.9 | 118.5 | 138.3 | 26 | 21.3 | 35.9 | 2.6 | 241.4 | 7 | 374 | 228.1 | 96.3 | 498.9 | 106.9 | 93.5 | 327.6
1236 | 359 | -5.4 | 0 | 0 | 118.7 | 117.3 | 118.5 | 118.1 | 137.7 | 26 | 21.3 | 35.9 | 2.4 | 234.6 | 7.9 | 371.6 | 226.9 | 95.7 | 495.9 | 106.1 | 92.7 | 326.5
1237 | 360 | -5.3 | 0 | 0 | 118.3 | 116.8 | 118 | 117.7 | 137.1 | 25.9 | 21.3 | 35.8 | 2.5 | 246.5 | 9 | 369.1 | 225.6 | 95 | 493 | 105.4 | 91.9 | 325.1
1238 | 361 | -5.1 | 0 | 0 | 117.9 | 116.4 | 117.6 | 117.3 | 136.6 | 25.9 | 21.3 | 35.7 | 2.7 | 257.7 | 9.1 | 366.7 | 224.4 | 94.3 | 490 | 104.7 | 91.1 | 323.6
1239 | 362 | -3.8 | 0 | 0 | 117.5 | 116 | 117.1 | 116.8 | 136.1 | 25.9 | 21.3 | 35.6 | 2.8 | 248.9 | 9.4 | 364.4 | 223.1 | 93.6 | 487.1 | 104.1 | 90.2 | 322.1
1240 | 363 | -4.3 | 0 | 0 | 117 | 115.7 | 116.7 | 116.4 | 135.6 | 25.9 | 21.3 | 35.6 | 2.7 | 256.8 | 10.3 | 362.1 | 221.8 | 92.8 | 484.3 | 103.6 | 89.4 | 321
1241 | 364 | -6.3 | 0 | 0 | 116.6 | 115.3 | 116.3 | 116 | 135.2 | 25.9 | 21.3 | 35.5 | 2.6 | 256.4 | 9.7 | 359.8 | 220.4 | 92 | 481.4 | 103.2 | 88.5 | 319.8
1242 | 365 | -6.8 | 0 | 0 | 116.2 | 114.9 | 115.9 | 115.6 | 134.7 | 25.9 | 21.3 | 35.4 | 2.8 | 243.2 | 8.7 | 357.7 | 219.1 | 91.1 | 478.6 | 102.7 | 87.7 | 318.7
1243 | 366 | -6.8 | 0 | 0 | 115.8 | 114.6 | 115.5 | 115.2 | 134.3 | 25.8 | 21.3 | 35.3 | 3.8 | 230.7 | 7.2 | 355.5 | 217.7 | 90.2 | 475.9 | 101.7 | 86.8 | 317.4
1244 | 367 | -6.6 | 0 | 0 | 115.4 | 114.2 | 115.1 | 114.9 | 133.8 | 25.8 | 21.3 | 35.2 | 3.5 | 256.5 | 6.3 | 353.3 | 216.3 | 89.4 | 473.1 | 100.8 | 86 | 315.9
1245 | 368 | -6.3 | 0 | 0 | 115.1 | 113.9 | 114.7 | 114.5 | 133.4 | 25.8 | 21.3 | 35.1 | 3.2 | 255.5 | 6.1 | 351.2 | 214.9 | 88.6 | 470.5 | 99.8 | 85.2 | 315.2
1246 | 369 | -6.4 | 0 | 0 | 114.7 | 113.5 | 114.3 | 114.2 | 132.9 | 25.8 | 21.3 | 35 | 3.1 | 246.2 | 5.4 | 349.1 | 213.5 | 87.9 | 467.8 | 99.2 | 84.5 | 314.1
1247 | 370 | -6.7 | 0 | 0 | 114.4 | 113.2 | 114 | 113.9 | 132.5 | 25.7 | 21.3 | 35 | 2.6 | 234.5 | 4.7 | 347 | 212.2 | 87.3 | 465.1 | 98.5 | 83.9 | 312.5
1248 | 371 | -6.8 | 0 | 0 | 114.1 | 112.9 | 113.7 | 113.4 | 132 | 25.7 | 21.3 | 34.9 | 3.1 | 228.2 | 4.5 | 345 | 210.9 | 86.7 | 462.6 | 97.7 | 83.3 | 311.1
1249 | 372 | -6.8 | 0 | 0 | 113.8 | 112.7 | 113.3 | 113 | 131.6 | 25.7 | 21.3 | 34.8 | 3.5 | 247.6 | 4.3 | 343 | 209.5 | 86.1 | 460 | 96.7 | 82.7 | 309.7
1250 | 373 | -6.8 | 0 | 0 | 113.4 | 112.4 | 113 | 112.6 | 131.1 | 25.6 | 21.3 | 34.8 | 3.4 | 244.9 | 4.2 | 341.1 | 208.1 | 85.5 | 457.5 | 95.8 | 82 | 308.6
1251 | 374 | -6.7 | 0 | 0 | 113.1 | 112.1 | 112.7 | 112.2 | 130.6 | 25.6 | 21.3 | 34.7 | 2.9 | 226.7 | 4.2 | 339.2 | 206.8 | 84.9 | 454.9 | 94.9 | 81.4 | 307.4
1252 | 375 | -6.4 | 0 | 0 | 112.8 | 111.8 | 112.3 | 111.8 | 130.2 | 25.6 | 21.3 | 34.6 | 2.6 | 216.4 | 5 | 337.4 | 205.6 | 84.3 | 452.3 | 94.1 | 80.8 | 306
1253 | 376 | -5.3 | 0 | 0 | 112.5 | 111.4 | 112 | 111.5 | 129.7 | 25.5 | 21.3 | 34.5 | 3.5 | 222.2 | 7.3 | 335.6 | 204.4 | 83.4 | 450 | 93.5 | 80.1 | 304.8
1254 | 377 | -5.6 | 0 | 0 | 112.2 | 111.1 | 111.7 | 111.2 | 129.3 | 25.5 | 21.3 | 34.4 | 4.3 | 206.9 | 9.8 | 333.7 | 203.1 | 82.6 | 447.6 | 92.6 | 79.3 | 303.6
1255 | 378 | -6 | 0 | 0 | 112 | 110.8 | 111.4 | 110.8 | 128.8 | 25.5 | 21.3 | 34.3 | 3.9 | 227.2 | 10.8 | 331.9 | 202.3 | 81.9 | 445.2 | 92 | 78.5 | 302.4
1256 | 379 | -6.5 | 0 | 0 | 111.7 | 110.4 | 111.1 | 110.4 | 128.4 | 25.4 | 21.3 | 34.3 | 3.5 | 269.7 | 8.5 | 330.1 | 201.9 | 81.2 | 442.9 | 91.6 | 77.9 | 301.5
1257 | 380 | -6.4 | 0 | 0 | 111.4 | 110.1 | 110.7 | 110.1 | 128 | 25.4 | 21.3 | 34.2 | 4 | 255.4 | 6.8 | 328.4 | 201.6 | 80.4 | 440 | 91.3 | 77.3 | 300.3
1258 | 381 | -5.9 | 0 | 0 | 111.2 | 109.8 | 110.4 | 109.7 | 127.7 | 25.4 | 21.3 | 34.1 | 4.1 | 230 | 6.7 | 326.8 | 201.4 | 79.7 | 438.3 | 91.3 | 76.8 | 298.8
1259 | 382 | -5.5 | 0 | 0 | 110.9 | 109.5 | 110.1 | 109.4 | 127.3 | 25.3 | 21.3 | 34.1 | 5.6 | 243.1 | 7.5 | 325.1 | 201.4 | 79 | 435.8 | 90.6 | 76.2 | 297.7
1260 | 383 | -5.9 | 0 | 0 | 110.6 | 109.2 | 109.7 | 109.1 | 126.9 | 25.3 | 21.3 | 34 | 5.8 | 230.8 | 7.9 | 323.5 | 201.1 | 78.4 | 429.7 | 90.2 | 75.6 | 296
1261 | 384 | -6.1 | 0 | 0 | 110.3 | 109 | 109.4 | 108.8 | 126.6 | 25.3 | 21.3 | 33.9 | 4.8 | 236.2 | 8 | 321.9 | 200.4 | 77.8 | 431.7 | 89.8 | 75.1 | 294.4
1262 | 385 | -5.2 | 0 | 0 | 110.1 | 108.7 | 109.1 | 108.5 | 126.2 | 25.2 | 21.3 | 33.8 | 4.6 | 240.6 | 9 | 320.3 | 199.5 | 77.3 | 426.1 | 89.1 | 74.6 | 292.9
1263 | 386 | -5 | 0 | 0 | 109.8 | 108.4 | 108.8 | 108.2 | 125.9 | 25.2 | 21.3 | 33.7 | 4 | 253.9 | 11.1 | 318.7 | 197.9 | 76.7 | 420.5 | 88.5 | 74.1 | 291.9
1264 | 387 | -5.2 | 0 | 0 | 109.5 | 108.2 | 108.5 | 107.9 | 125.5 | 25.2 | 21.3 | 33.6 | 4.4 | 234.5 | 13.2 | 317 | 196.9 | 76.1 | 425.3 | 87.7 | 73.8 | 290.4
1265 | 388 | -5 | 0 | 0 | 109.2 | 107.9 | 108.2 | 107.7 | 125.1 | 25.1 | 21.3 | 33.5 | 5.2 | 243.8 | 16.7 | 315.3 | 195.8 | 75.6 | 415.5 | 86.5 | 72.9 | 289.4
1266 | 389 | -5.6 | 0 | 0 | 109 | 107.7 | 107.9 | 107.5 | 124.8 | 25.1 | 21.3 | 33.4 | 4.4 | 241.7 | 15.3 | 313.7 | 194.7 | 75 | 415.8 | 85.5 | 72.3 | 288.5
1267 | 390 | -6.1 | 0 | 0 | 108.7 | 107.4 | 107.6 | 107.3 | 124.4 | 25.1 | 21.3 | 33.3 | 4.8 | 244.8 | 13.5 | 312.1 | 193.7 | 74.4 | 419.1 | 84.8 | 72.4 | 287.6
1268 | 391 | -6.4 | 0 | 0 | 108.4 | 107.2 | 107.3 | 107 | 124.1 | 25.1 | 21.3 | 33.2 | 5.4 | 248.8 | 13.2 | 310.6 | 193 | 73.7 | 417 | 84.2 | 71.9 | 286.9
1269 | 392 | -6.8 | 0 | 0 | 108.1 | 107 | 107 | 106.7 | 123.7 | 25 | 21.3 | 33.1 | 5.2 | 250 | 12.6 | 309.1 | 192.3 | 73.2 | 415 | 83.9 | 71.4 | 285.9
1270 | 393 | -6.8 | 0 | 0 | 107.8 | 106.8 | 106.7 | 106.4 | 123.4 | 25 | 21.3 | 33 | 5.4 | 247.9 | 13.7 | 307.6 | 191.4 | 72.7 | 410.6 | 83.5 | 70.7 | 285
1271 | 394 | -6.8 | 0 | 0 | 107.6 | 106.5 | 106.4 | 106.1 | 123.1 | 25 | 21.3 | 33 | 5.2 | 246.6 | 13.7 | 306.2 | 190.2 | 72.2 | 397 | 83.1 | 69.3 | 284.1

## First Electrical Failures
First electrical failures observed for the two cables present extracted from the corresponding IRMS data files
3/C Cable |  |  | 7/C IRMS Cable
Time | Offset Time (s) | C1-G | Time | Offset Time (s) | C2-G
3.3333 | -187.6667 | 223238 | 114.3333 | -76.6667 | 240638
157.3333 | -33.6667 | 223238 | 268.3333 | 77.3333 | 99.3355
311.3333 | 120.3333 | 0.64235 | 422.25 | 231.25 | 0.62831
465.3333 | 274.3333 | 0.62187 | 576.3333 | 385.3333 | 4.3093