## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Preliminary Test 1, 7/C Cable in Location A
Test conditions: Cable: 7-conductor, 12 AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III control cable. (Item #10) Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 100 kW heat release rate and increased to ~250 kW during the test run. Electrical repsonse monitoring: IRMS system using seven channels - one for each insulated conductor, cable tray was grounded. Thermal response monitoring: One cable temperature (see thermocouple map), air temperatures above and below the cable, and the cable tray rung temperature. Gas burner initiated: Following 1700 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
1700 | 0 | Ignited Gas Burner
3078 | 1378 | Conductor 6 shorts to conductor 7 at less than 1000 ohms (807) | Initial failure is by shorting between conductors
3176-3190 | 1476-1490 | Conductor 1 shorts to conductors 2, 4, 5, 6 & 7 at less than 100 ohms (17, 14, 30, 1 & 16 ohms, respectively) | Failures progress to additional conductor-to-conductor shorts and shorts to ground
3183 | 1483 | Conductor 1 shorts to ground at less than 100 ohms (1)
3193-3204 | 1493-1504 | Conductor 2 shorts to conductors 3, 4, 5, 6 & 7 at less than 100 ohms (8, 22, 7, 1 & 11)
3194-3202 | 1494-1502 | Conductors 2 & 3 both short to ground at less than 100 ohms (1 & 1)
3207-3215 | 1507-1515 | Conductor 3 shorts to conductors 4, 5, 6 & 7 (38, 1, 134 & 138)
3208-3215 | 1508-1515 | Conductors 4, 5, 6 & 7 all short to ground at less than 100 ohms (5, 3, 11 & 15) | All conductors have shorted to external ground.
3218-3224 | 1518-1524 | Conductor 4 shorts to conductors 5 & 7 (172 & 7)
3226 | 1526 | Conductor 5 shorts to conductor 6 at less than 100 ohms (7)
3333 | 1633 | Conductors 1 & 3 short together at less than 100 ohms (15)
3366-3369 | 1666-1669 | The existing shorts between conductor 3 and conductors 6 & 7 decrease to less than 100 ohms (22 & 14)
3372-3375 | 1672-1675 | The existing short between conductors 4 & 5 decreases to less than 100 ohms (14) and conductor 4 shorts to conductor 6 at less than 100 ohms (20)
3383 | 1683 | Conductors 5 & 7 short together at less than 100 ohms (14)
3386 | 1686 | The existing short between conductors 6 & 7 decreases to less than 100 ohms (10) | All conductors have shorted together at less than 100 ohms
4305 | 2605 | Extinguished Gas Burner
Additional Observations

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable = | XLPE, 7/C | (Item #10)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| A4 | = | Within cable just below cable jacket, center position
| A5 | = | Air temperature above cable
| A6 | = | Air temperature below cable

## C-C Individuals
Conductor to Conductor Resistances
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24
XLPE | 7-C | Tray A
0 | 250 kW
Burner Time | C1-2 | Burner Time | C1-3 | Burner Time | C1-4 | Burner Time | C1-5 | Burner Time | C1-6 | Burner Time | C1-7 | Burner Time | C2-3 | Burner Time | C2-4 | Burner Time | C2-5 | Burner Time | C2-6 | Burner Time | C2-7 | Burner Time | C3-4 | Burner Time | C3-5 | Burner Time | C3-6 | Burner Time | C3-7 | Burner Time | C4-5 | Burner Time | C4-6 | Burner Time | C4-7 | Burner Time | C5-6 | Burner Time | C5-7 | Burner Time | C6-7 | Burner Time | Minimums
-1604 | 241537.9994 | -1601 | 244937.9994 | -1598.5 | 250637.9994 | -1595.5 | 253437.9994 | -1592.5 | 249137.9994 | -1590 | 248837.9994 | -1587 | 247537.9994 | -1584.5 | 248137.9994 | -1581.5 | 252037.9994 | -1578.5 | 254237.9994 | -1576 | 239737.9994 | -1573 | 253637.9994 | -1570.5 | 244437.9994 | -1567.5 | 498975.9997 | -1564.5 | 249237.9994 | -1562 | 248737.9994 | -1559 | 245137.9994 | -1556.5 | 248637.9994 | -1553.5 | 246537.9994 | -1550.5 | 241037.9994 | -1548 | 252537.9994 | -1604 | 239737.9994
-1450 | 241537.9994 | -1447 | 244937.9994 | -1444.5 | 250637.9994 | -1441.5 | 253437.9994 | -1438.5 | 249137.9994 | -1436 | 248837.9994 | -1433 | 247537.9994 | -1430.5 | 248137.9994 | -1427.5 | 252037.9994 | -1424.5 | 254237.9994 | -1422 | 239737.9994 | -1419 | 507375.9997 | -1416.5 | 244437.9994 | -1413.5 | 249437.9994 | -1410.5 | 249237.9994 | -1408 | 248737.9994 | -1405 | 245137.9994 | -1402.5 | 497375.9997 | -1399.5 | 246537.9994 | -1396.5 | 241037.9994 | -1394 | 252537.9994 | -1450 | 239737.9994
-1296 | 241537.9994 | -1293.5 | 244937.9994 | -1290.5 | 250637.9994 | -1287.5 | 253437.9994 | -1284.5 | 249137.9994 | -1282 | 248837.9994 | -1279 | 247537.9994 | -1276.5 | 248137.9994 | -1273.5 | 252037.9994 | -1270.5 | 254237.9994 | -1268 | 239737.9994 | -1265 | 253637.9994 | -1262 | 244437.9994 | -1259.5 | 249437.9994 | -1256.5 | 498575.9997 | -1254 | 248737.9994 | -1251 | 245137.9994 | -1248.5 | 248637.9994 | -1245.5 | 246537.9994 | -1242.5 | 241037.9994 | -1240 | 252537.9994 | -1296 | 239737.9994
-1142 | 241537.9994 | -1139.5 | 489975.9997 | -1136.5 | 250637.9994 | -1133.5 | 506975.9997 | -1131 | 249137.9994 | -1128 | 248837.9994 | -1125.5 | 247537.9994 | -1122.5 | 496375.9997 | -1119.5 | 504175.9997 | -1116.5 | 254237.9994 | -1114 | 239737.9994 | -1111 | 253637.9994 | -1108.5 | 244437.9994 | -1105.5 | 249437.9994 | -1102.5 | 249237.9994 | -1100 | 248737.9994 | -1097 | 245137.9994 | -1094.5 | 248637.9994 | -1091.5 | 246537.9994 | -1088.5 | 241037.9994 | -1086 | 252537.9994 | -1142 | 239737.9994
-988 | 241537.9994 | -985.5 | 244937.9994 | -982.5 | 250637.9994 | -979.5 | 253437.9994 | -977 | 249137.9994 | -974 | 248837.9994 | -971 | 247537.9994 | -968.5 | 248137.9994 | -965.5 | 252037.9994 | -962.5 | 254237.9994 | -960 | 239737.9994 | -957.5 | 253637.9994 | -954.5 | 244437.9994 | -951.5 | 249437.9994 | -949 | 249237.9994 | -946 | 248737.9994 | -943.5 | 245137.9994 | -940.5 | 497375.9997 | -937.5 | 246537.9994 | -935 | 482175.9997 | -932 | 252537.9994 | -988 | 239737.9994
-834 | 241537.9994 | -831.5 | 244937.9994 | -828.5 | 250637.9994 | -825.5 | 253437.9994 | -822.5 | 249137.9994 | -820 | 248837.9994 | -817 | 247537.9994 | -814.5 | 248137.9994 | -811.5 | 252037.9994 | -808.5 | 254237.9994 | -806 | 239737.9994 | -803.5 | 253637.9994 | -800.5 | 244437.9994 | -797.5 | 249437.9994 | -795 | 249237.9994 | -792 | 248737.9994 | -789.5 | 245137.9994 | -786.5 | 248637.9994 | -783.5 | 493175.9997 | -780.5 | 241037.9994 | -778 | 505175.9997 | -834 | 239737.9994
-680 | 241537.9994 | -677.5 | 244937.9994 | -674.5 | 250637.9994 | -671.5 | 253437.9994 | -669 | 249137.9994 | -666 | 497775.9997 | -663.5 | 247537.9994 | -660.5 | 248137.9994 | -657.5 | 252037.9994 | -655 | 254237.9994 | -652 | 239737.9994 | -649.5 | 253637.9994 | -646.5 | 244437.9994 | -643.5 | 249437.9994 | -641 | 249237.9994 | -638 | 248737.9994 | -635.5 | 245137.9994 | -632.5 | 248637.9994 | -629.5 | 246537.9994 | -627 | 241037.9994 | -624 | 252537.9994 | -680 | 239737.9994
-526 | 483175.9997 | -523.5 | 244937.9994 | -520.5 | 250637.9994 | -517.5 | 253437.9994 | -515 | 249137.9994 | -512 | 248837.9994 | -509.5 | 247537.9994 | -506.5 | 248137.9994 | -503.5 | 252037.9994 | -501 | 254237.9994 | -498 | 239737.9994 | -495.5 | 253637.9994 | -492.5 | 244437.9994 | -489.5 | 249437.9994 | -487 | 249237.9994 | -484 | 248737.9994 | -481.5 | 245137.9994 | -478.5 | 497375.9997 | -475.5 | 246537.9994 | -473 | 241037.9994 | -470 | 252537.9994 | -526 | 239737.9994
-372 | 241537.9994 | -369.5 | 489975.9997 | -366.5 | 250637.9994 | -364 | 253437.9994 | -361 | 249137.9994 | -358 | 248837.9994 | -355.5 | 247537.9994 | -352.5 | 248137.9994 | -349.5 | 252037.9994 | -347 | 254237.9994 | -344 | 239737.9994 | -341.5 | 253637.9994 | -338.5 | 244437.9994 | -335.5 | 249437.9994 | -333 | 249237.9994 | -330 | 248737.9994 | -327.5 | 245137.9994 | -324.5 | 248637.9994 | -321.5 | 246537.9994 | -319 | 241037.9994 | -316 | 252537.9994 | -372 | 239737.9994
-218 | 241537.9994 | -215.5 | 244937.9994 | -212.5 | 250637.9994 | -209.5 | 253437.9994 | -207 | 249137.9994 | -204 | 248837.9994 | -201.5 | 247537.9994 | -198.5 | 248137.9994 | -195.5 | 252037.9994 | -193 | 254237.9994 | -190 | 239737.9994 | -187.5 | 253637.9994 | -184.5 | 244437.9994 | -181.5 | 249437.9994 | -179 | 498575.9997 | -176 | 497575.9997 | -173.5 | 245137.9994 | -170.5 | 248637.9994 | -167.5 | 246537.9994 | -165 | 241037.9994 | -162 | 252537.9994 | -218 | 239737.9994
-64.5 | 241537.9994 | -61.5 | 244937.9994 | -58.5 | 250637.9994 | -55.5 | 253437.9994 | -53 | 249137.9994 | -50 | 248837.9994 | -47.5 | 247537.9994 | -44.5 | 248137.9994 | -41.5 | 252037.9994 | -39 | 508575.9997 | -36 | 239737.9994 | -33.5 | 253637.9994 | -30.5 | 244437.9994 | -27.5 | 498975.9997 | -25 | 249237.9994 | -22 | 248737.9994 | -19.5 | 245137.9994 | -16.5 | 248637.9994 | -13.5 | 246537.9994 | -11 | 241037.9994 | -8 | 252537.9994 | -64.5 | 239737.9994
89.5 | 241537.9994 | 92.5 | 244937.9994 | 95.5 | 250637.9994 | 98 | 253437.9994 | 101 | 249137.9994 | 103.5 | 248837.9994 | 106.5 | 247537.9994 | 109.5 | 248137.9994 | 112 | 252037.9994 | 115 | 254237.9994 | 118 | 239737.9994 | 120.5 | 253637.9994 | 123.5 | 244437.9994 | 126.5 | 249437.9994 | 129 | 249237.9994 | 132 | 248737.9994 | 134.5 | 245137.9994 | 137.5 | 497375.9997 | 140.5 | 246537.9994 | 143 | 241037.9994 | 145.5 | 252537.9994 | 89.5 | 239737.9994
243.5 | 241537.9994 | 246.5 | 244937.9994 | 249.5 | 250637.9994 | 252.5 | 253437.9994 | 255 | 249137.9994 | 258 | 248837.9994 | 260.5 | 247537.9994 | 263.5 | 248137.9994 | 266.5 | 504175.9997 | 269 | 254237.9994 | 271.5 | 239737.9994 | 274.5 | 253637.9994 | 277.5 | 244437.9994 | 280.5 | 249437.9994 | 283 | 249237.9994 | 285.5 | 248737.9994 | 288.5 | 245137.9994 | 291.5 | 248637.9994 | 294 | 246537.9994 | 297 | 241037.9994 | 300 | 252537.9994 | 243.5 | 239737.9994
398 | 241537.9994 | 400.5 | 244937.9994 | 403.5 | 250637.9994 | 406.5 | 253437.9994 | 409 | 249137.9994 | 412 | 248837.9994 | 414.5 | 247537.9994 | 417.5 | 248137.9994 | 420.5 | 252037.9994 | 423 | 508575.9997 | 426 | 479575.9997 | 428.5 | 253637.9994 | 431.5 | 244437.9994 | 434 | 249437.9994 | 437 | 249237.9994 | 439.5 | 248737.9994 | 442.5 | 490375.9997 | 445.5 | 248637.9994 | 448 | 246537.9994 | 451 | 241037.9994 | 453.5 | 252537.9994 | 398 | 241037.9994
551.5 | 241537.9994 | 554.5 | 244937.9994 | 557.5 | 250637.9994 | 560.5 | 253437.9994 | 563 | 249137.9994 | 565.5 | 248837.9994 | 568.5 | 247537.9994 | 571.5 | 248137.9994 | 574 | 252037.9994 | 577 | 254237.9994 | 579.5 | 239737.9994 | 582.5 | 253637.9994 | 585.5 | 244437.9994 | 588 | 249437.9994 | 591 | 249237.9994 | 593.5 | 248737.9994 | 596.5 | 245137.9994 | 599.5 | 248637.9994 | 602.5 | 246537.9994 | 605 | 241037.9994 | 608 | 252537.9994 | 551.5 | 239737.9994
705.5 | 241537.9994 | 708.5 | 244937.9994 | 711.5 | 250637.9994 | 714 | 253437.9994 | 717 | 249137.9994 | 719.5 | 248837.9994 | 722.5 | 247537.9994 | 725.5 | 248137.9994 | 728 | 252037.9994 | 731 | 254237.9994 | 733.5 | 239737.9994 | 736.5 | 253637.9994 | 739.5 | 244437.9994 | 742 | 249437.9994 | 745 | 249237.9994 | 747.5 | 248737.9994 | 750.5 | 245137.9994 | 753.5 | 497375.9997 | 756 | 246537.9994 | 759 | 241037.9994 | 761.5 | 252537.9994 | 705.5 | 239737.9994
859.5 | 241537.9994 | 862.5 | 244937.9994 | 865.5 | 250637.9994 | 868 | 253437.9994 | 871 | 249137.9994 | 873.5 | 248837.9994 | 876.5 | 247537.9994 | 879.5 | 248137.9994 | 882 | 252037.9994 | 885 | 254237.9994 | 887.5 | 239737.9994 | 890.5 | 253637.9994 | 893.5 | 244437.9994 | 896 | 249437.9994 | 899 | 249237.9994 | 901.5 | 248737.9994 | 904.5 | 245137.9994 | 907.5 | 248637.9994 | 910 | 246537.9994 | 913 | 241037.9994 | 915.5 | 252537.9994 | 859.5 | 239737.9994
1013.5 | 241537.9994 | 1016.5 | 244937.9994 | 1019.5 | 250637.9994 | 1022 | 253437.9994 | 1025 | 249137.9994 | 1027.5 | 248837.9994 | 1030.5 | 247537.9994 | 1033.5 | 248137.9994 | 1036 | 252037.9994 | 1039 | 254237.9994 | 1041.5 | 239737.9994 | 1044.5 | 253637.9994 | 1047.5 | 244437.9994 | 1050 | 249437.9994 | 1053 | 249237.9994 | 1055.5 | 248737.9994 | 1058.5 | 245137.9994 | 1061.5 | 248637.9994 | 1064 | 246537.9994 | 1067 | 241037.9994 | 1069.5 | 252537.9994 | 1013.5 | 239737.9994
1167.5 | 241537.9994 | 1170.5 | 244937.9994 | 1173.5 | 250637.9994 | 1176 | 506975.9997 | 1179 | 249137.9994 | 1181.5 | 248837.9994 | 1184.5 | 247537.9994 | 1187.5 | 248137.9994 | 1190 | 252037.9994 | 1193 | 254237.9994 | 1195.5 | 239737.9994 | 1198.5 | 253637.9994 | 1201.5 | 244437.9994 | 1204 | 249437.9994 | 1207 | 249237.9994 | 1209.5 | 248737.9994 | 1212.5 | 245137.9994 | 1215.5 | 248637.9994 | 1218 | 246537.9994 | 1221 | 241037.9994 | 1223.5 | 252537.9994 | 1167.5 | 239737.9994
1321.5 | 241537.9994 | 1324.5 | 244937.9994 | 1327.5 | 250637.9994 | 1330 | 253437.9994 | 1333 | 249137.9994 | 1335.5 | 248837.9994 | 1338.5 | 247537.9994 | 1341.5 | 248137.9994 | 1344 | 7425.5971 | 1347 | 3804.6042 | 1349.5 | 26415.6569 | 1352.5 | 63184.5887 | 1355.5 | 7941.3756 | 1358 | 12891.809 | 1361 | 49627.4554 | 1363.5 | 16336.231 | 1366.5 | 3287.9432 | 1369.5 | 2202.8485 | 1372 | 1325.7317 | 1375 | 1090.573 | 1377.5 | 807.2527 | 1321.5 | 807.2527
1475.5 | 17.4987 | 1478.5 | 1428.1387 | 1481.5 | 13.6865 | 1484 | 30.2573 | 1487 | 0.85005 | 1489.5 | 15.6274 | 1492.5 | 8.0965 | 1495.5 | 21.9649 | 1498 | 6.6034 | 1501 | 0.89454 | 1503.5 | 11.4603 | 1506.5 | 38.1975 | 1509.5 | 0.80855 | 1512 | 134.394 | 1515 | 137.7614 | 1517.5 | 172.3116 | 1520.5 | 7979.0662 | 1523.5 | 7.3655 | 1526 | 6.5429 | 1528.5 | 5365.9054 | 1531.5 | 286.2354 | 1475.5 | 0.80855
1629.5 | 0.68489 | 1632.5 | 15.4589 | 1635.5 | 0.86319 | 1638 | 0.88759 | 1640.5 | 26.3598 | 1643.5 | 3.0983 | 1646.5 | 1.413 | 1649 | 18.9514 | 1652 | 18.7259 | 1654.5 | 16.7066 | 1657.5 | 2.0978 | 1660.5 | 0.88933 | 1663 | 24.2786 | 1666 | 21.5026 | 1668.5 | 14.4952 | 1671.5 | 14.3172 | 1674.5 | 19.8689 | 1677 | 0.84566 | 1680 | 21.9736 | 1682.5 | 14.4369 | 1685.5 | 9.7597 | 1629.5 | 0.68489
1783.5 | 5.6837 | 1786.5 | 0.13707 | 1789 | 14.7094 | 1792 | 28.4934 | 1794.5 | 0.82727 | 1797.5 | 6409.3543 | 1800.5 | 1705.4231 | 1803 | 2018.4542 | 1806 | 4435.4017 | 1809 | 1.6324 | 1811.5 | 603.6877 | 1814.5 | 5.1142 | 1817 | 2530.5909 | 1820 | 0.85268 | 1822.5 | 0.85093 | 1825.5 | 6.8817 | 1828.5 | 26.4218 | 1831 | 3.461 | 1834 | 0.82716 | 1836.5 | 18.6216 | 1839.5 | 85.9789 | 1783.5 | 0.13707
1937.5 | 4.0274 | 1940.5 | 21.4839 | 1943 | 0.82215 | 1946 | 15.133 | 1948.5 | 7.8259 | 1951.5 | 22.2504 | 1954.5 | 20.0256 | 1957 | 15.2433 | 1960 | 0.87541 | 1962.5 | 5.1393 | 1965.5 | 22.9603 | 1968.5 | 23.1976 | 1971 | 6658.6782 | 1974 | 956.5743 | 1976.5 | 981.638 | 1979.5 | 24.5953 | 1982.5 | 5.9778 | 1985 | 2534.3222 | 1988 | 3746.1472 | 1990.5 | 24.8844 | 1993.5 | 466.1213 | 1937.5 | 0.82215
2091.5 | 64.8116 | 2094.5 | 632.7787 | 2097 | 586.8358 | 2100 | 15.622 | 2102.5 | 423.2214 | 2105.5 | 10573.5382 | 2108.5 | 135.8081 | 2111 | 0.50875 | 2114 | 4566.1822 | 2116.5 | 1.6324 | 2119.5 | 2301.5134 | 2122.5 | 25.2012 | 2125 | 872.4261 | 2128 | 6373.9853 | 2130.5 | 18.0823 | 2133.5 | 1336.3845 | 2136.5 | 0.81477 | 2139 | 11710.9748 | 2142 | 6808.9947 | 2144.5 | 2915.5639 | 2147.5 | 1377.7633 | 2091.5 | 0.50875
2245.5 | 484.1536 | 2248.5 | 42.0253 | 2251 | 1622.5623 | 2254 | 543.4303 | 2256.5 | 1286.7981 | 2259.5 | 87.267 | 2262.5 | 497.7333 | 2265 | 90.5437 | 2268 | 1997.5708 | 2270.5 | 542.9601 | 2273.5 | 2199.518 | 2276.5 | 1848.3261 | 2279 | 929.2675 | 2282 | 706.8884 | 2284.5 | 1349.4304 | 2287.5 | 446.9561 | 2290.5 | 1566.176 | 2293 | 843.7509 | 2296 | 233.0669 | 2298.5 | 1150.0142 | 2301.5 | 865.3595 | 2245.5 | 42.0253
2399.5 | 88.4382 | 2402.5 | 21.4189 | 2405 | 39.8539 | 2408 | 42.6883 | 2410.5 | 74.1833 | 2413.5 | 18.3751 | 2416.5 | 118.7397 | 2419 | 16.644 | 2422 | 80.8826 | 2424.5 | 27.2922 | 2427.5 | 3.8589 | 2430.5 | 65.9729 | 2433 | 1.5459 | 2436 | 5.0582 | 2438.5 | 16.9283 | 2441.5 | 0.053281 | 2444.5 | 3.2032 | 2447 | 22.7088 | 2450 | 1.962 | 2452.5 | 57.4468 | 2455.5 | 16.1668 | 2399.5 | 0.053281
2553.5 | 30.848 | 2556.5 | 161.8892 | 2559 | 66.6839 | 2562 | 895.0483 | 2564.5 | 378.0124 | 2567.5 | 396.605 | 2570.5 | 166.8666 | 2573 | 131.8285 | 2576 | 1196.8129 | 2578.5 | 354.1118 | 2581.5 | 23.4173 | 2584.5 | 1211.8643 | 2587 | 47.9798 | 2590 | 73.895 | 2592.5 | 339.8791 | 2595.5 | 117.8217 | 2598.5 | 296.3712 | 2601 | 274.8354 | 2604 | 1377.2749 | 2606.5 | 1898.823 | 2609.5 | 810.061 | 2553.5 | 23.4173
2707.5 | 224.0938 | 2710.5 | 196.4369 | 2713 | 371.015 | 2716 | 49.7312 | 2718.5 | 328.3003 | 2721.5 | 50.7872 | 2724.5 | 249.7404 | 2727 | 140.5572 | 2730 | 29.5601 | 2732.5 | 60.4537 | 2735.5 | 119818.9988 | 2738.5 | 253637.9994 | 2741 | 244437.9994 | 2744 | 249437.9994 | 2746.5 | 249237.9994 | 2749.5 | 248737.9994 | 2752.5 | 245137.9994 | 2755 | 248637.9994 | 2758 | 246537.9994 | 2760.5 | 241037.9994 | 2763.5 | 252537.9994 | 2707.5 | 29.5601

## C-G Min
Average Conductor to Ground Resistances
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24
XLPE | 7-C | Tray A
0 | 250 kW
Burner Time | C1-G |  | Burner Time | C2-G | Burner Time | C3-G | Burner Time | C4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | C7-G | Burner Time | Minimums Overall
-1596.9167 | 241538 |  | -1585.25 | 239738 | -1577.25 | 244438 | -1572.25 | 245138 | -1568.9167 | 241038 | -1566.5 | 245138 | -1564.25 | 239738 | -1596.9167 | 239738
-1442.9167 | 241538 |  | -1431.25 | 239738 | -1423.25 | 244438 | -1418.25 | 245138 | -1414.9167 | 241038 | -1412.5 | 245138 | -1410.25 | 239738 | -1442.9167 | 239738
-1289 | 241538 |  | -1277.25 | 239738 | -1269.25 | 244438 | -1264.25 | 245138 | -1260.8333 | 241038 | -1258.5 | 245138 | -1256.25 | 239738 | -1289 | 239738
-1135.0833 | 241538 |  | -1123.3333 | 239738 | -1115.4167 | 244438 | -1110.25 | 245138 | -1106.9167 | 241038 | -1104.5833 | 245138 | -1102.25 | 239738 | -1135.0833 | 239738
-981.0833 | 241538 |  | -969.25 | 239738 | -961.5 | 244438 | -956.4167 | 245138 | -953 | 244438 | -950.6667 | 245138 | -948.4167 | 239738 | -981.0833 | 239738
-827 | 241538 |  | -815.25 | 239738 | -807.5 | 244438 | -802.4167 | 245138 | -798.9167 | 241038 | -796.5833 | 245138 | -794.3333 | 241038 | -827 | 239738
-673.0833 | 241538 |  | -661.4167 | 239738 | -653.5833 | 244438 | -648.4167 | 245138 | -645 | 241038 | -642.75 | 245138 | -640.4167 | 239738 | -673.0833 | 239738
-519.0833 | 244938 |  | -507.4167 | 239738 | -499.5833 | 244438 | -494.4167 | 245138 | -491 | 241038 | -488.75 | 245138 | -486.4167 | 239738 | -519.0833 | 239738
-365.1667 | 241538 |  | -353.4167 | 239738 | -345.5833 | 244438 | -340.4167 | 245138 | -337.0833 | 241038 | -334.75 | 245138 | -332.4167 | 239738 | -365.1667 | 239738
-211.0833 | 241538 |  | -199.4167 | 239738 | -191.5833 | 244438 | -186.4167 | 245138 | -183 | 241038 | -180.75 | 245138 | -178.4167 | 239738 | -211.0833 | 239738
-57.1667 | 241538 |  | -45.5 | 239738 | -37.5833 | 244438 | -32.4167 | 245138 | -29 | 241038 | -26.75 | 245138 | -24.4167 | 239738 | -57.1667 | 239738
96.6667 | 241538 |  | 108.4167 | 239738 | 116.4167 | 244438 | 121.5833 | 245138 | 124.8333 | 241038 | 127.1667 | 245138 | 129.4167 | 239738 | 96.6667 | 239738
250.8333 | 241538 |  | 262.4167 | 239738 | 270.4167 | 244438 | 275.5 | 245138 | 278.8333 | 241038 | 281.1667 | 245138 | 283.5 | 239738 | 250.8333 | 239738
404.9167 | 241538 |  | 416.5833 | 241538 | 424.3333 | 244438 | 429.5 | 248138 | 432.8333 | 241038 | 435 | 245138 | 437.5 | 239738 | 404.9167 | 239738
558.75 | 241538 |  | 570.3333 | 239738 | 578.3333 | 244438 | 583.5 | 245138 | 586.8333 | 241038 | 589.1667 | 245138 | 591.4167 | 239738 | 558.75 | 239738
712.6667 | 241538 |  | 724.3333 | 239738 | 732.3333 | 244438 | 737.5 | 245138 | 740.6667 | 241038 | 743 | 245138 | 745.3333 | 239738 | 712.6667 | 239738
866.6667 | 241538 |  | 878.3333 | 239738 | 886.3333 | 244438 | 891.5 | 245138 | 894.6667 | 241038 | 897 | 245138 | 899.3333 | 239738 | 866.6667 | 239738
1020.6667 | 241538 |  | 1032.3333 | 239738 | 1040.3333 | 244438 | 1045.5 | 245138 | 1048.6667 | 241038 | 1051 | 245138 | 1053.3333 | 239738 | 1020.6667 | 239738
1174.6667 | 241538 |  | 1186.3333 | 239738 | 1194.3333 | 244438 | 1199.5 | 245138 | 1202.6667 | 241038 | 1205 | 245138 | 1207.3333 | 239738 | 1174.6667 | 239738
1328.6667 | 241538 |  | 1340.3333 | 62305.2051 | 1348.3333 | 35313.4955 | 1353.5 | 35205.9861 | 1356.6667 | 28675.0745 | 1359 | 6698.8904 | 1361.3333 | 2137.873 | 1328.6667 | 2137.873
1482.6667 | 0.66155 |  | 1494.3333 | 0.6482 | 1502.3333 | 0.67435 | 1507.5 | 5.3292 | 1510.5833 | 2.7471 | 1513 | 11.0461 | 1515.25 | 16.9425 | 1482.6667 | 0.6482
1636.5833 | 0.65026 |  | 1648.1667 | 2.8824 | 1656.1667 | 0.64974 | 1661.3333 | 0.66289 | 1664.5 | 0.66262 | 1666.8333 | 3.5859 | 1669.0833 | 0.65259 | 1636.5833 | 0.64974
1790.5 | 1.3391 |  | 1802.25 | 3.1379 | 1810.1667 | 0.66075 | 1815.25 | 4.9085 | 1818.5 | 0.66857 | 1820.9167 | 3.8698 | 1823.0833 | 2.657 | 1790.5 | 0.66075
1944.5 | 0.69799 |  | 1956.1667 | 0.65389 | 1964.1667 | 0.87088 | 1969.25 | 7.3722 | 1972.5 | 1.9863 | 1974.8333 | 10.9674 | 1977.0833 | 0.68392 | 1944.5 | 0.65389
2098.5 | 2.1412 |  | 2110.1667 | 0.66893 | 2118.1667 | 9.6854 | 2123.25 | 0.67241 | 2126.5 | 1.6853 | 2128.8333 | 1.2543 | 2131.0833 | 8.2196 | 2098.5 | 0.66893
2252.5 | 0.67987 |  | 2264.1667 | 3.5375 | 2272.1667 | 10.1672 | 2277.25 | 0.6696 | 2280.5 | 3.5297 | 2282.8333 | 3.0615 | 2285.0833 | 17.37 | 2252.5 | 0.6696
2406.5 | 5.2103 |  | 2418.1667 | 16.9072 | 2426.1667 | 14.5492 | 2431.25 | 0.41969 | 2434.5 | 0.47866 | 2436.8333 | 26.8467 | 2439.0833 | 57.4628 | 2406.5 | 0.41969
2560.5 | 4.1246 |  | 2572.1667 | 0.69561 | 2580.1667 | 12.8195 | 2585.25 | 3.1583 | 2588.5 | 0.97912 | 2590.8333 | 1.8864 | 2593.0833 | 9.7671 | 2560.5 | 0.69561
2714.5 | 5.1736 |  | 2726.1667 | 12.1358 | 2734.1667 | 18.0903 | 2739.25 | 19.3211 | 2742.5 | 10.1553 | 2744.8333 | 10.4763 | 2747.0833 | 23.2776 | 2714.5 | 5.1736

## C6-7
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 154.2357 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 6 & 7
Time-109 | N11 | N12 | Time-110 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
39002.4354 | 1 | 0 | 39002.4354 | 1 | 0 | -1548 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4372 | 1 | 0 | 39002.4372 | 1 | 0 | -1394 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.439 | 1 | 0 | 39002.439 | 1 | 0 | -1240 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4408 | 1 | 0 | 39002.4408 | 1 | 0 | -1086 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4425 | 1 | 0 | 39002.4426 | 1 | 0 | -932 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4443 | 0 | 0 | 39002.4444 | 1 | 0 | -778 | 922 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 505176 | 252538 | 505175.9997
39002.4461 | 1 | 0 | 39002.4461 | 1 | 0 | -624 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4479 | 1 | 0 | 39002.4479 | 1 | 0 | -470 | 1230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4497 | 1 | 0 | 39002.4497 | 1 | 0 | -316 | 1384 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4515 | 1 | 0 | 39002.4515 | 1 | 0 | -162 | 1538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4532 | 1 | 0 | 39002.4533 | 1 | 0 | -8 | 1692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.455 | 1 | 0 | 39002.455 | 1 | 0 | 145.5 | 1845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4568 | 1 | 0 | 39002.4568 | 1 | 0 | 300 | 2000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4586 | 1 | 0 | 39002.4586 | 1 | 0 | 453.5 | 2153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4604 | 1 | 0 | 39002.4604 | 1 | 0 | 608 | 2308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4622 | 1 | 0 | 39002.4622 | 1 | 0 | 761.5 | 2461.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4639 | 1 | 0 | 39002.4639 | 1 | 0 | 915.5 | 2615.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4657 | 1 | 0 | 39002.4657 | 1 | 0 | 1069.5 | 2769.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4675 | 1 | 0 | 39002.4675 | 1 | 0 | 1223.5 | 2923.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252538 | 252538 | 252537.9994
39002.4693 | 230 | 243 | 39002.4693 | 895 | 972 | 1377.5 | 3077.5 | 14.0415 | 14.8352 | 54.6398 | 59.3407 | 0.14042 | 0.14835 | 0.5464 | 0.59341 | 0.0079365 | 0.047009 | 140574.9599 | 2137.873 | 807.2527
39002.4711 | 2132 | 19 | 39002.4711 | 2163 | 3 | 1531.5 | 3231.5 | 130.1587 | 1.16 | 132.0513 | 0.18315 | 1.3016 | 0.0116 | 1.3205 | 0.0018315 | 1.29 | 1.3187 | 19.7106 | 16.9425 | 286.2354
39002.4728 | 2273 | 0 | 39002.4729 | 2510 | 0 | 1685.5 | 3385.5 | 138.7668 | 0 | 153.2357 | 0 | 1.3877 | 0 | 1.5324 | 0 | 1.3877 | 1.5324 | 11.1474 | 0.65259 | 9.7597
39002.4746 | 2436 | 4 | 39002.4746 | 2429 | 3 | 1839.5 | 3539.5 | 148.7179 | 0.2442 | 148.2906 | 0.18315 | 1.4872 | 0.002442 | 1.4829 | 0.0018315 | 1.4847 | 1.4811 | 3.8698 | 4.1465 | 85.9789
39002.4764 | 2048 | 19 | 39002.4764 | 2054 | 15 | 1993.5 | 3693.5 | 125.0305 | 1.16 | 125.3968 | 0.91575 | 1.2503 | 0.0116 | 1.254 | 0.0091575 | 1.2387 | 1.2448 | 24.5393 | 23.8832 | 466.1213
39002.4782 | 2036 | 4 | 39002.4782 | 2243 | 5 | 2147.5 | 3847.5 | 124.2979 | 0.2442 | 136.9353 | 0.30525 | 1.243 | 0.002442 | 1.3694 | 0.0030525 | 1.2405 | 1.3663 | 24.5104 | 12.7787 | 1377.7633
39002.48 | 2359 | 4 | 39002.48 | 2007 | 5 | 2301.5 | 4001.5 | 144.0171 | 0.2442 | 122.5275 | 0.30525 | 1.4402 | 0.002442 | 1.2253 | 0.0030525 | 1.4377 | 1.2222 | 7.1526 | 26.8817 | 865.3595
39002.4818 | 1562 | 790 | 39002.4818 | 1671 | 625 | 2455.5 | 4155.5 | 95.3602 | 48.2295 | 102.0147 | 38.1563 | 0.9536 | 0.4823 | 1.0201 | 0.38156 | 0.47131 | 0.63858 | 199.5109 | 273.7089 | 16.1668
39002.4835 | 2205 | 6 | 39002.4836 | 2143 | 5 | 2609.5 | 4309.5 | 134.6154 | 0.3663 | 130.8303 | 0.30525 | 1.3462 | 0.003663 | 1.3083 | 0.0030525 | 1.3425 | 1.3053 | 14.837 | 18.2189 | 810.061
39002.4853 | 1 | 0 | 39002.4853 | 0 | 0 | 2763.5 | 4463.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 252538 | 505176 | 252537.9994

## C5-7
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 147.2149 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 5 & 7
Time-107 | N11 | N12 | Time-108 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
39002.4354 | 1 | 0 | 39002.4354 | 1 | 0 | -1550.5 | 149.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4372 | 1 | 0 | 39002.4372 | 1 | 0 | -1396.5 | 303.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.439 | 1 | 0 | 39002.439 | 1 | 0 | -1242.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4407 | 1 | 0 | 39002.4408 | 1 | 0 | -1088.5 | 611.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4425 | 0 | 0 | 39002.4425 | 1 | 0 | -935 | 765 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 482176 | 241038 | 482175.9997
39002.4443 | 1 | 0 | 39002.4443 | 1 | 0 | -780.5 | 919.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4461 | 1 | 0 | 39002.4461 | 1 | 0 | -627 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4479 | 1 | 0 | 39002.4479 | 1 | 0 | -473 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4496 | 1 | 0 | 39002.4497 | 1 | 0 | -319 | 1381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4514 | 1 | 0 | 39002.4514 | 1 | 0 | -165 | 1535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4532 | 1 | 0 | 39002.4532 | 1 | 0 | -11 | 1689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.455 | 1 | 0 | 39002.455 | 1 | 0 | 143 | 1843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4568 | 1 | 0 | 39002.4568 | 1 | 0 | 297 | 1997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4586 | 1 | 0 | 39002.4586 | 1 | 0 | 451 | 2151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4603 | 1 | 0 | 39002.4604 | 1 | 0 | 605 | 2305 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4621 | 1 | 0 | 39002.4621 | 1 | 0 | 759 | 2459 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4639 | 1 | 0 | 39002.4639 | 1 | 0 | 913 | 2613 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4657 | 1 | 0 | 39002.4657 | 1 | 0 | 1067 | 2767 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4675 | 1 | 0 | 39002.4675 | 1 | 0 | 1221 | 2921 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994
39002.4692 | 194 | 186 | 39002.4693 | 268 | 264 | 1375 | 3075 | 11.8437 | 11.3553 | 16.3614 | 16.1172 | 0.11844 | 0.11355 | 0.16361 | 0.16117 | 0.004884 | 0.002442 | 28675.0745 | 69605.1798 | 1090.573
39002.471 | 1844 | 3 | 39002.471 | 1726 | 2 | 1528.5 | 3228.5 | 112.5763 | 0.18315 | 105.3724 | 0.1221 | 1.1258 | 0.0018315 | 1.0537 | 0.001221 | 1.1239 | 1.0525 | 30.9455 | 39.9048 | 5365.9054
39002.4728 | 2084 | 0 | 39002.4728 | 2154 | 0 | 1682.5 | 3382.5 | 127.2283 | 0 | 131.5018 | 0 | 1.2723 | 0 | 1.315 | 0 | 1.2723 | 1.315 | 15.7092 | 11.9489 | 14.4369
39002.4746 | 2012 | 0 | 39002.4746 | 2202 | 0 | 1836.5 | 3536.5 | 122.8327 | 0 | 134.4322 | 0 | 1.2283 | 0 | 1.3443 | 0 | 1.2283 | 1.3443 | 19.8499 | 9.5086 | 18.6216
39002.4764 | 1913 | 0 | 39002.4764 | 2395 | 0 | 1990.5 | 3690.5 | 116.7888 | 0 | 146.2149 | 0 | 1.1679 | 0 | 1.4621 | 0 | 1.1679 | 1.4621 | 26.0523 | 0.68392 | 24.8844
39002.4782 | 2258 | 1 | 39002.4782 | 1953 | 1 | 2144.5 | 3844.5 | 137.851 | 0.06105 | 119.2308 | 0.06105 | 1.3785 | 0.0006105 | 1.1923 | 0.0006105 | 1.3779 | 1.1917 | 6.8085 | 23.6606 | 2915.5639
39002.4799 | 2201 | 3 | 39002.48 | 2014 | 2 | 2298.5 | 3998.5 | 134.3712 | 0.18315 | 122.9548 | 0.1221 | 1.3437 | 0.0018315 | 1.2295 | 0.001221 | 1.3419 | 1.2283 | 9.6373 | 19.9563 | 1150.0142
39002.4817 | 1665 | 416 | 39002.4817 | 1742 | 604 | 2452.5 | 4152.5 | 101.6484 | 25.3968 | 106.3492 | 36.8742 | 1.0165 | 0.25397 | 1.0635 | 0.36874 | 0.76252 | 0.69475 | 68.4819 | 261.4616 | 57.4468
39002.4835 | 1903 | 5 | 39002.4835 | 1961 | 5 | 2606.5 | 4306.5 | 116.1783 | 0.30525 | 119.7192 | 0.30525 | 1.1618 | 0.0030525 | 1.1972 | 0.0030525 | 1.1587 | 1.1941 | 27.0921 | 23.2449 | 1898.823
39002.4853 | 1 | 0 | 39002.4853 | 1 | 0 | 2760.5 | 4460.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241038 | 241038 | 241037.9994

## C5-6
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 150.5726 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 5 & 6
Time-105 | N11 | N12 | Time-106 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39002.4354 | 1 | 0 | 39002.4354 | 1 | 0 | -1553.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4371 | 1 | 0 | 39002.4372 | 1 | 0 | -1399.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4389 | 1 | 0 | 39002.4389 | 0 | 0 | -1245.5 | 454.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 246538 | 493176 | 246537.9994
39002.4407 | 1 | 0 | 39002.4407 | 1 | 0 | -1091.5 | 608.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4425 | 1 | 0 | 39002.4425 | 1 | 0 | -937.5 | 762.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4443 | 0 | 0 | 39002.4443 | 1 | 0 | -783.5 | 916.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 493176 | 246538 | 493175.9997
39002.4461 | 1 | 0 | 39002.4461 | 1 | 0 | -629.5 | 1070.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4478 | 1 | 0 | 39002.4478 | 1 | 0 | -475.5 | 1224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4496 | 1 | 0 | 39002.4496 | 1 | 0 | -321.5 | 1378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4514 | 1 | 0 | 39002.4514 | 1 | 0 | -167.5 | 1532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4532 | 1 | 0 | 39002.4532 | 1 | 0 | -13.5 | 1686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.455 | 1 | 0 | 39002.455 | 1 | 0 | 140.5 | 1840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4567 | 1 | 0 | 39002.4568 | 1 | 0 | 294 | 1994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4585 | 1 | 0 | 39002.4585 | 1 | 0 | 448 | 2148 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4603 | 1 | 0 | 39002.4603 | 1 | 0 | 602.5 | 2302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4621 | 1 | 0 | 39002.4621 | 1 | 0 | 756 | 2456 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4639 | 1 | 0 | 39002.4639 | 1 | 0 | 910 | 2610 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4656 | 1 | 0 | 39002.4657 | 1 | 0 | 1064 | 2764 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4674 | 1 | 0 | 39002.4675 | 1 | 0 | 1218 | 2918 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994
39002.4692 | 168 | 159 | 39002.4692 | 656 | 685 | 1372 | 3072 | 10.2564 | 9.707 | 40.0488 | 41.8193 | 0.10256 | 0.09707 | 0.40049 | 0.41819 | 0.0054945 | 0.017705 | 34684.8186 | 6698.8904 | 1325.7317
39002.471 | 2285 | 0 | 39002.471 | 2202 | 1 | 1526 | 3226 | 139.4994 | 0 | 134.4322 | 0.06105 | 1.395 | 0 | 1.3443 | 0.0006105 | 1.395 | 1.3437 | 7.9379 | 12.0572 | 6.5429
39002.4728 | 2002 | 0 | 39002.4728 | 2381 | 0 | 1680 | 3380 | 122.2222 | 0 | 145.3602 | 0 | 1.2222 | 0 | 1.4536 | 0 | 1.2222 | 1.4536 | 23.1958 | 3.5859 | 21.9736
39002.4746 | 2450 | 0 | 39002.4746 | 1896 | 0 | 1834 | 3534 | 149.5726 | 0 | 115.7509 | 0 | 1.4957 | 0 | 1.1575 | 0 | 1.4957 | 1.1575 | 0.66857 | 30.0833 | 0.82716
39002.4763 | 2209 | 1 | 39002.4764 | 2106 | 0 | 1988 | 3688 | 134.8596 | 0.06105 | 128.5714 | 0 | 1.3486 | 0.0006105 | 1.2857 | 0 | 1.348 | 1.2857 | 11.6876 | 17.1121 | 3746.1472
39002.4781 | 1973 | 1 | 39002.4781 | 2126 | 1 | 2142 | 3842 | 120.4518 | 0.06105 | 129.7924 | 0.06105 | 1.2045 | 0.0006105 | 1.2979 | 0.0006105 | 1.2039 | 1.2973 | 25.0986 | 16.048 | 6808.9947
39002.4799 | 2228 | 3 | 39002.4799 | 2394 | 3 | 2296 | 3996 | 136.0195 | 0.18315 | 146.1538 | 0.18315 | 1.3602 | 0.0018315 | 1.4615 | 0.0018315 | 1.3584 | 1.4597 | 11.2073 | 3.0615 | 233.0669
39002.4817 | 1922 | 600 | 39002.4817 | 1555 | 657 | 2450 | 4150 | 117.3382 | 36.63 | 94.9328 | 40.1099 | 1.1734 | 0.3663 | 0.94933 | 0.4011 | 0.80708 | 0.54823 | 15.3048 | 26.8467 | 1.962
39002.4835 | 2099 | 5 | 39002.4835 | 2004 | 5 | 2604 | 4304 | 128.1441 | 0.30525 | 122.3443 | 0.30525 | 1.2814 | 0.0030525 | 1.2234 | 0.0030525 | 1.2784 | 1.2204 | 17.7248 | 23.4616 | 1377.2749
39002.4853 | 1 | 0 | 39002.4853 | 1 | 0 | 2758 | 4458 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 246538 | 246538 | 246537.9994

## C4-7
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 151.8547 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 7
Time-103 | N11 | N12 | Time-104 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39002.4353 | 1 | 0 | 39002.4353 | 1 | 0 | -1556.5 | 143.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4371 | 0 | 0 | 39002.4371 | 1 | 0 | -1402.5 | 297.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497376 | 248638 | 497375.9997
39002.4389 | 1 | 0 | 39002.4389 | 1 | 0 | -1248.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4407 | 1 | 0 | 39002.4407 | 1 | 0 | -1094.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4425 | 0 | 0 | 39002.4425 | 1 | 0 | -940.5 | 759.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497376 | 248638 | 497375.9997
39002.4442 | 1 | 0 | 39002.4442 | 1 | 0 | -786.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.446 | 1 | 0 | 39002.446 | 1 | 0 | -632.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4478 | 0 | 0 | 39002.4478 | 1 | 0 | -478.5 | 1221.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497376 | 248638 | 497375.9997
39002.4496 | 1 | 0 | 39002.4496 | 1 | 0 | -324.5 | 1375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4514 | 1 | 0 | 39002.4514 | 1 | 0 | -170.5 | 1529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4531 | 1 | 0 | 39002.4532 | 1 | 0 | -16.5 | 1683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4549 | 0 | 0 | 39002.4549 | 1 | 0 | 137.5 | 1837.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497376 | 248638 | 497375.9997
39002.4567 | 1 | 0 | 39002.4567 | 1 | 0 | 291.5 | 1991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4585 | 1 | 0 | 39002.4585 | 1 | 0 | 445.5 | 2145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4603 | 1 | 0 | 39002.4603 | 1 | 0 | 599.5 | 2299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4621 | 0 | 0 | 39002.4621 | 1 | 0 | 753.5 | 2453.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497376 | 248638 | 497375.9997
39002.4638 | 1 | 0 | 39002.4639 | 1 | 0 | 907.5 | 2607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4656 | 1 | 0 | 39002.4656 | 1 | 0 | 1061.5 | 2761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4674 | 1 | 0 | 39002.4674 | 1 | 0 | 1215.5 | 2915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994
39002.4692 | 110 | 103 | 39002.4692 | 106 | 100 | 1369.5 | 3069.5 | 6.7155 | 6.2882 | 6.4713 | 6.105 | 0.067155 | 0.062882 | 0.064713 | 0.06105 | 0.0042735 | 0.003663 | 35205.9861 | 41661.962 | 2202.8485
39002.471 | 2287 | 0 | 39002.471 | 2005 | 1 | 1523.5 | 3223.5 | 139.6215 | 0 | 122.4054 | 0.06105 | 1.3962 | 0 | 1.2241 | 0.0006105 | 1.3962 | 1.2234 | 8.7617 | 24.1208 | 7.3655
39002.4727 | 2471 | 0 | 39002.4728 | 2459 | 0 | 1677 | 3377 | 150.8547 | 0 | 150.1221 | 0 | 1.5085 | 0 | 1.5012 | 0 | 1.5085 | 1.5012 | 0.66289 | 1.1541 | 0.84566
39002.4745 | 2371 | 0 | 39002.4745 | 2423 | 0 | 1831 | 3531 | 144.7497 | 0 | 147.9243 | 0 | 1.4475 | 0 | 1.4792 | 0 | 1.4475 | 1.4792 | 4.9085 | 2.657 | 3.461
39002.4763 | 2168 | 1 | 39002.4763 | 2290 | 1 | 1985 | 3685 | 132.3565 | 0.06105 | 139.8046 | 0.06105 | 1.3236 | 0.0006105 | 1.398 | 0.0006105 | 1.323 | 1.3974 | 14.8174 | 8.6485 | 2534.3222
39002.4781 | 2002 | 1 | 39002.4781 | 1886 | 0 | 2139 | 3839 | 122.2222 | 0.06105 | 115.1404 | 0 | 1.2222 | 0.0006105 | 1.1514 | 0 | 1.2216 | 1.1514 | 24.2949 | 31.8865 | 11710.9748
39002.4799 | 2413 | 2 | 39002.4799 | 1923 | 2 | 2293 | 3993 | 147.3138 | 0.1221 | 117.3993 | 0.1221 | 1.4731 | 0.001221 | 1.174 | 0.001221 | 1.4719 | 1.1728 | 3.0935 | 30.4027 | 843.7509
39002.4817 | 1639 | 620 | 39002.4817 | 1727 | 718 | 2447 | 4147 | 100.0611 | 37.851 | 105.4335 | 43.8339 | 1.0006 | 0.37851 | 1.0543 | 0.43834 | 0.6221 | 0.616 | 133.9597 | 160.7507 | 22.7088
39002.4834 | 2412 | 6 | 39002.4835 | 1935 | 5 | 2601 | 4301 | 147.2527 | 0.3663 | 118.1319 | 0.30525 | 1.4725 | 0.003663 | 1.1813 | 0.0030525 | 1.4689 | 1.1783 | 3.1583 | 31.1782 | 274.8354
39002.4852 | 1 | 0 | 39002.4852 | 1 | 0 | 2755 | 4455 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248638 | 248638 | 248637.9994

## C4-6
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 149.7179 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 6
Time-101 | N11 | N12 | Time-102 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39002.4353 | 1 | 0 | 39002.4353 | 1 | 0 | -1559 | 141 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4371 | 1 | 0 | 39002.4371 | 1 | 0 | -1405 | 295 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4389 | 1 | 0 | 39002.4389 | 1 | 0 | -1251 | 449 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4406 | 1 | 0 | 39002.4407 | 1 | 0 | -1097 | 603 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4424 | 1 | 0 | 39002.4424 | 1 | 0 | -943.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4442 | 1 | 0 | 39002.4442 | 1 | 0 | -789.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.446 | 1 | 0 | 39002.446 | 1 | 0 | -635.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4478 | 1 | 0 | 39002.4478 | 1 | 0 | -481.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4495 | 1 | 0 | 39002.4496 | 1 | 0 | -327.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4513 | 1 | 0 | 39002.4513 | 1 | 0 | -173.5 | 1526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4531 | 1 | 0 | 39002.4531 | 1 | 0 | -19.5 | 1680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4549 | 1 | 0 | 39002.4549 | 1 | 0 | 134.5 | 1834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4567 | 1 | 0 | 39002.4567 | 1 | 0 | 288.5 | 1988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4585 | 0 | 0 | 39002.4585 | 1 | 0 | 442.5 | 2142.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 490376 | 245138 | 490375.9997
39002.4602 | 1 | 0 | 39002.4603 | 1 | 0 | 596.5 | 2296.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.462 | 1 | 0 | 39002.462 | 1 | 0 | 750.5 | 2450.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4638 | 1 | 0 | 39002.4638 | 1 | 0 | 904.5 | 2604.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4656 | 1 | 0 | 39002.4656 | 1 | 0 | 1058.5 | 2758.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4674 | 1 | 0 | 39002.4674 | 1 | 0 | 1212.5 | 2912.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994
39002.4692 | 72 | 70 | 39002.4692 | 126 | 117 | 1366.5 | 3066.5 | 4.3956 | 4.2735 | 7.6923 | 7.1429 | 0.043956 | 0.042735 | 0.076923 | 0.071429 | 0.001221 | 0.0054945 | 137454.8426 | 26095.4685 | 3287.9432
39002.4709 | 2126 | 1 | 39002.4709 | 1851 | 0 | 1520.5 | 3220.5 | 129.7924 | 0.06105 | 113.0037 | 0 | 1.2979 | 0.0006105 | 1.13 | 0 | 1.2973 | 1.13 | 15.3813 | 32.4895 | 7979.0662
39002.4727 | 2025 | 0 | 39002.4727 | 2207 | 0 | 1674.5 | 3374.5 | 123.6264 | 0 | 134.7375 | 0 | 1.2363 | 0 | 1.3474 | 0 | 1.2363 | 1.3474 | 21.1052 | 11.1183 | 19.8689
39002.4745 | 1922 | 0 | 39002.4745 | 2050 | 0 | 1828.5 | 3528.5 | 117.3382 | 0 | 125.1526 | 0 | 1.1734 | 0 | 1.2515 | 0 | 1.1734 | 1.2515 | 27.5952 | 19.6283 | 26.4218
39002.4763 | 2284 | 0 | 39002.4763 | 2210 | 0 | 1982.5 | 3682.5 | 139.4383 | 0 | 134.9206 | 0 | 1.3944 | 0 | 1.3492 | 0 | 1.3944 | 1.3492 | 7.3722 | 10.9674 | 5.9778
39002.4781 | 2436 | 0 | 39002.4781 | 2422 | 0 | 2136.5 | 3836.5 | 148.7179 | 0 | 147.8632 | 0 | 1.4872 | 0 | 1.4786 | 0 | 1.4872 | 1.4786 | 0.67241 | 1.2543 | 0.81477
39002.4798 | 1970 | 3 | 39002.4799 | 2213 | 2 | 2290.5 | 3990.5 | 120.2686 | 0.18315 | 135.1038 | 0.1221 | 1.2027 | 0.0018315 | 1.351 | 0.001221 | 1.2009 | 1.3498 | 24.8727 | 10.8663 | 1566.176
39002.4816 | 1850 | 669 | 39002.4816 | 1570 | 647 | 2444.5 | 4144.5 | 112.9426 | 40.8425 | 95.8486 | 39.4994 | 1.1294 | 0.40842 | 0.95849 | 0.39499 | 0.721 | 0.56349 | 23.2417 | 47.4196 | 3.2032
39002.4834 | 2353 | 7 | 39002.4834 | 1929 | 5 | 2598.5 | 4298.5 | 143.6508 | 0.42735 | 117.7656 | 0.30525 | 1.4365 | 0.0042735 | 1.1777 | 0.0030525 | 1.4322 | 1.1746 | 4.2802 | 28.9611 | 296.3712
39002.4852 | 1 | 0 | 39002.4852 | 1 | 0 | 2752.5 | 4452.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245138 | 245138 | 245137.9994

## C4-5
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 151.9158 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 4 & 5
Time-99 | N11 | N12 | Time-100 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39002.4353 | 1 | 0 | 39002.4353 | 1 | 0 | -1562 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.437 | 1 | 0 | 39002.4371 | 1 | 0 | -1408 | 292 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4388 | 1 | 0 | 39002.4388 | 1 | 0 | -1254 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4406 | 1 | 0 | 39002.4406 | 1 | 0 | -1100 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4424 | 1 | 0 | 39002.4424 | 0 | 0 | -946 | 754 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248738 | 497576 | 248737.9994
39002.4442 | 1 | 0 | 39002.4442 | 1 | 0 | -792 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4459 | 1 | 0 | 39002.446 | 0 | 0 | -638 | 1062 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248738 | 497576 | 248737.9994
39002.4477 | 1 | 0 | 39002.4478 | 1 | 0 | -484 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4495 | 1 | 0 | 39002.4495 | 1 | 0 | -330 | 1370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4513 | 0 | 0 | 39002.4513 | 1 | 0 | -176 | 1524 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497576 | 248738 | 497575.9997
39002.4531 | 1 | 0 | 39002.4531 | 0 | 0 | -22 | 1678 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248738 | 497576 | 248737.9994
39002.4549 | 1 | 0 | 39002.4549 | 1 | 0 | 132 | 1832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4566 | 1 | 0 | 39002.4567 | 0 | 0 | 285.5 | 1985.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248738 | 497576 | 248737.9994
39002.4584 | 1 | 0 | 39002.4584 | 1 | 0 | 439.5 | 2139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4602 | 1 | 0 | 39002.4602 | 1 | 0 | 593.5 | 2293.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.462 | 1 | 0 | 39002.462 | 1 | 0 | 747.5 | 2447.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4638 | 1 | 0 | 39002.4638 | 1 | 0 | 901.5 | 2601.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4656 | 1 | 0 | 39002.4656 | 1 | 0 | 1055.5 | 2755.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4673 | 1 | 0 | 39002.4673 | 1 | 0 | 1209.5 | 2909.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994
39002.4691 | 19 | 15 | 39002.4691 | 43 | 39 | 1363.5 | 3063.5 | 1.16 | 0.91575 | 2.6252 | 2.381 | 0.0116 | 0.0091575 | 0.026252 | 0.02381 | 0.002442 | 0.002442 | 62109.5 | 62109.5 | 16336.231
39002.4709 | 1982 | 30 | 39002.4709 | 2234 | 33 | 1517.5 | 3217.5 | 121.0012 | 1.8315 | 136.3858 | 2.0147 | 1.21 | 0.018315 | 1.3639 | 0.020147 | 1.1917 | 1.3437 | 29.6904 | 12.1721 | 172.3116
39002.4727 | 2152 | 0 | 39002.4727 | 2472 | 0 | 1671.5 | 3371.5 | 131.3797 | 0 | 150.9158 | 0 | 1.3138 | 0 | 1.5092 | 0 | 1.3138 | 1.5092 | 15.631 | 0.66262 | 14.3172
39002.4745 | 2298 | 0 | 39002.4745 | 2057 | 0 | 1825.5 | 3525.5 | 140.293 | 0 | 125.58 | 0 | 1.4029 | 0 | 1.2558 | 0 | 1.4029 | 1.2558 | 8.2846 | 20.9713 | 6.8817
39002.4762 | 1978 | 0 | 39002.4763 | 2180 | 0 | 1979.5 | 3679.5 | 120.757 | 0 | 133.0891 | 0 | 1.2076 | 0 | 1.3309 | 0 | 1.2076 | 1.3309 | 25.8028 | 14.1459 | 24.5953
39002.478 | 2411 | 1 | 39002.478 | 2053 | 0 | 2133.5 | 3833.5 | 147.1917 | 0.06105 | 125.3358 | 0 | 1.4719 | 0.0006105 | 1.2534 | 0 | 1.4713 | 1.2534 | 3.2171 | 21.207 | 1336.3845
39002.4798 | 1960 | 4 | 39002.4798 | 2404 | 3 | 2287.5 | 3987.5 | 119.6581 | 0.2442 | 146.7643 | 0.18315 | 1.1966 | 0.002442 | 1.4676 | 0.0018315 | 1.1941 | 1.4658 | 28.6746 | 3.5297 | 446.9561
39002.4816 | 2007 | 542 | 39002.4816 | 1849 | 566 | 2441.5 | 4141.5 | 122.5275 | 33.0891 | 112.8816 | 34.5543 | 1.2253 | 0.33089 | 1.1288 | 0.34554 | 0.89438 | 0.78327 | 0.41969 | 0.47866 | 0.053281
39002.4834 | 1991 | 6 | 39002.4834 | 2453 | 7 | 2595.5 | 4295.5 | 121.5507 | 0.3663 | 149.7558 | 0.42735 | 1.2155 | 0.003663 | 1.4976 | 0.0042735 | 1.2118 | 1.4933 | 31.6008 | 1.4597 | 117.8217
39002.4852 | 1 | 0 | 39002.4852 | 1 | 0 | 2749.5 | 4449.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248738 | 248738 | 248737.9994

## C3-7
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 152.221 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 7
Time-97 | N11 | N12 | Time-98 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39002.4352 | 1 | 0 | 39002.4352 | 1 | 0 | -1564.5 | 135.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.437 | 1 | 0 | 39002.437 | 1 | 0 | -1410.5 | 289.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4388 | 0 | 0 | 39002.4388 | 1 | 0 | -1256.5 | 443.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 498576 | 249238 | 498575.9997
39002.4406 | 1 | 0 | 39002.4406 | 1 | 0 | -1102.5 | 597.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4423 | 1 | 0 | 39002.4424 | 1 | 0 | -949 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4441 | 1 | 0 | 39002.4442 | 1 | 0 | -795 | 905 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4459 | 1 | 0 | 39002.4459 | 1 | 0 | -641 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4477 | 1 | 0 | 39002.4477 | 1 | 0 | -487 | 1213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4495 | 1 | 0 | 39002.4495 | 1 | 0 | -333 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4513 | 0 | 0 | 39002.4513 | 1 | 0 | -179 | 1521 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 498576 | 249238 | 498575.9997
39002.453 | 1 | 0 | 39002.4531 | 1 | 0 | -25 | 1675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4548 | 1 | 0 | 39002.4548 | 1 | 0 | 129 | 1829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4566 | 1 | 0 | 39002.4566 | 1 | 0 | 283 | 1983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4584 | 1 | 0 | 39002.4584 | 1 | 0 | 437 | 2137 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4602 | 1 | 0 | 39002.4602 | 1 | 0 | 591 | 2291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.462 | 1 | 0 | 39002.462 | 1 | 0 | 745 | 2445 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4637 | 1 | 0 | 39002.4638 | 1 | 0 | 899 | 2599 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4655 | 1 | 0 | 39002.4655 | 1 | 0 | 1053 | 2753 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4673 | 1 | 0 | 39002.4673 | 1 | 0 | 1207 | 2907 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994
39002.4691 | 7 | 5 | 39002.4691 | 9 | 9 | 1361 | 3061 | 0.42735 | 0.30525 | 0.54945 | 0.54945 | 0.0042735 | 0.0030525 | 0.0054945 | 0.0054945 | 0.001221 | 0 | 124318.0943 | 34317043.0246 | 49627.4554
39002.4709 | 2349 | 18 | 39002.4709 | 2027 | 7 | 1515 | 3215 | 143.4066 | 1.0989 | 123.7485 | 0.42735 | 1.4341 | 0.010989 | 1.2375 | 0.0042735 | 1.4231 | 1.2332 | 6.3962 | 24.4106 | 137.7614
39002.4727 | 2153 | 0 | 39002.4727 | 1986 | 0 | 1668.5 | 3368.5 | 131.4408 | 0 | 121.2454 | 0 | 1.3144 | 0 | 1.2125 | 0 | 1.3144 | 1.2125 | 15.8096 | 25.5478 | 14.4952
39002.4744 | 2477 | 0 | 39002.4744 | 1958 | 0 | 1822.5 | 3522.5 | 151.221 | 0 | 119.536 | 0 | 1.5122 | 0 | 1.1954 | 0 | 1.5122 | 1.1954 | 0.66128 | 27.3432 | 0.85093
39002.4762 | 2428 | 1 | 39002.4762 | 2119 | 1 | 1976.5 | 3676.5 | 148.2295 | 0.06105 | 129.3651 | 0.06105 | 1.4823 | 0.0006105 | 1.2937 | 0.0006105 | 1.4817 | 1.293 | 2.7 | 17.9907 | 981.638
39002.478 | 2089 | 0 | 39002.478 | 2305 | 1 | 2130.5 | 3830.5 | 127.5336 | 0 | 140.7204 | 0.06105 | 1.2753 | 0 | 1.4072 | 0.0006105 | 1.2753 | 1.4066 | 19.3576 | 8.2196 | 18.0823
39002.4798 | 2125 | 4 | 39002.4798 | 2127 | 3 | 2284.5 | 3984.5 | 129.7314 | 0.2442 | 129.8535 | 0.18315 | 1.2973 | 0.002442 | 1.2985 | 0.0018315 | 1.2949 | 1.2967 | 17.5586 | 17.3894 | 1349.4304
39002.4816 | 1678 | 557 | 39002.4816 | 1856 | 491 | 2438.5 | 4138.5 | 102.442 | 34.0049 | 113.3089 | 29.9756 | 1.0244 | 0.34005 | 1.1331 | 0.29976 | 0.68437 | 0.83333 | 537.5743 | 57.4628 | 16.9283
39002.4833 | 2219 | 7 | 39002.4834 | 2277 | 7 | 2592.5 | 4292.5 | 135.4701 | 0.42735 | 139.011 | 0.42735 | 1.3547 | 0.0042735 | 1.3901 | 0.0042735 | 1.3504 | 1.3858 | 12.8195 | 9.7671 | 339.8791
39002.4851 | 1 | 0 | 39002.4851 | 1 | 0 | 2746.5 | 4446.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249238 | 249238 | 249237.9994

## C3-6
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 152.3431 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 6
Time-95 | N11 | N12 | Time-96 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39002.4352 | 0 | 0 | 39002.4352 | 1 | 0 | -1567.5 | 132.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 498976 | 249438 | 498975.9997
39002.437 | 1 | 0 | 39002.437 | 1 | 0 | -1413.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4388 | 1 | 0 | 39002.4388 | 1 | 0 | -1259.5 | 440.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4405 | 1 | 0 | 39002.4406 | 1 | 0 | -1105.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4423 | 1 | 0 | 39002.4423 | 1 | 0 | -951.5 | 748.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4441 | 1 | 0 | 39002.4441 | 1 | 0 | -797.5 | 902.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4459 | 1 | 0 | 39002.4459 | 1 | 0 | -643.5 | 1056.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4477 | 1 | 0 | 39002.4477 | 1 | 0 | -489.5 | 1210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4495 | 1 | 0 | 39002.4495 | 1 | 0 | -335.5 | 1364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4512 | 1 | 0 | 39002.4512 | 1 | 0 | -181.5 | 1518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.453 | 0 | 0 | 39002.453 | 1 | 0 | -27.5 | 1672.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 498976 | 249438 | 498975.9997
39002.4548 | 1 | 0 | 39002.4548 | 1 | 0 | 126.5 | 1826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4566 | 1 | 0 | 39002.4566 | 1 | 0 | 280.5 | 1980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4584 | 1 | 0 | 39002.4584 | 1 | 0 | 434 | 2134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4601 | 1 | 0 | 39002.4602 | 1 | 0 | 588 | 2288 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4619 | 1 | 0 | 39002.4619 | 1 | 0 | 742 | 2442 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4637 | 1 | 0 | 39002.4637 | 1 | 0 | 896 | 2596 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4655 | 1 | 0 | 39002.4655 | 1 | 0 | 1050 | 2750 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4673 | 1 | 0 | 39002.4673 | 1 | 0 | 1204 | 2904 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39002.4691 | 26 | 19 | 39002.4691 | 20 | 19 | 1358 | 3058 | 1.5873 | 1.16 | 1.221 | 1.16 | 0.015873 | 0.0116 | 0.01221 | 0.0116 | 0.0042735 | 0.0006105 | 35313.4955 | 261613.8156 | 12891.809
39002.4708 | 1973 | 36 | 39002.4709 | 2250 | 7 | 1512 | 3212 | 120.4518 | 2.1978 | 137.3626 | 0.42735 | 1.2045 | 0.021978 | 1.3736 | 0.0042735 | 1.1825 | 1.3694 | 32.4239 | 11.0461 | 134.394
39002.4726 | 2033 | 0 | 39002.4726 | 1959 | 0 | 1666 | 3366 | 124.1148 | 0 | 119.5971 | 0 | 1.2411 | 0 | 1.196 | 0 | 1.2411 | 1.196 | 22.7437 | 27.3803 | 21.5026
39002.4744 | 2479 | 0 | 39002.4744 | 2327 | 0 | 1820 | 3520 | 151.3431 | 0 | 142.0635 | 0 | 1.5134 | 0 | 1.4206 | 0 | 1.5134 | 1.4206 | 0.66075 | 7.2359 | 0.85268
39002.4762 | 2438 | 1 | 39002.4762 | 2072 | 0 | 1974 | 3674 | 148.84 | 0.06105 | 126.4957 | 0 | 1.4884 | 0.0006105 | 1.265 | 0 | 1.4878 | 1.265 | 2.3593 | 20.4334 | 956.5743
39002.478 | 2003 | 1 | 39002.478 | 2173 | 2 | 2128 | 3828 | 122.2833 | 0.06105 | 132.6618 | 0.1221 | 1.2228 | 0.0006105 | 1.3266 | 0.001221 | 1.2222 | 1.3254 | 24.6771 | 14.905 | 6373.9853
39002.4797 | 2268 | 4 | 39002.4798 | 2185 | 4 | 2282 | 3982 | 138.4615 | 0.2442 | 133.3944 | 0.2442 | 1.3846 | 0.002442 | 1.3339 | 0.002442 | 1.3822 | 1.3315 | 10.1672 | 14.4925 | 706.8884
39002.4815 | 1759 | 628 | 39002.4816 | 1947 | 521 | 2436 | 4136 | 107.3871 | 38.3394 | 118.8645 | 31.8071 | 1.0739 | 0.38339 | 1.1886 | 0.31807 | 0.69048 | 0.87057 | 27.8334 | 41.461 | 5.0582
39002.4833 | 2209 | 7 | 39002.4833 | 2450 | 6 | 2590 | 4290 | 134.8596 | 0.42735 | 149.5726 | 0.3663 | 1.3486 | 0.0042735 | 1.4957 | 0.003663 | 1.3443 | 1.4921 | 15.6413 | 1.8864 | 73.895
39002.4851 | 1 | 0 | 39002.4851 | 1 | 0 | 2744 | 4444 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994

## C3-5
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 149.2906 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 5
Time-93 | N11 | N12 | Time-94 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39002.4352 | 1 | 0 | 39002.4352 | 1 | 0 | -1570.5 | 129.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4369 | 1 | 0 | 39002.437 | 1 | 0 | -1416.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
| 1 | 0 | 39002.4387 | 1 | 0 | -1262 | 438 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4405 | 1 | 0 | 39002.4405 | 1 | 0 | -1108.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4423 | 1 | 0 | 39002.4423 | 1 | 0 | -954.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4441 | 1 | 0 | 39002.4441 | 1 | 0 | -800.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4459 | 1 | 0 | 39002.4459 | 1 | 0 | -646.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4476 | 1 | 0 | 39002.4477 | 1 | 0 | -492.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4494 | 1 | 0 | 39002.4494 | 1 | 0 | -338.5 | 1361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4512 | 1 | 0 | 39002.4512 | 1 | 0 | -184.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.453 | 1 | 0 | 39002.453 | 1 | 0 | -30.5 | 1669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4548 | 1 | 0 | 39002.4548 | 1 | 0 | 123.5 | 1823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4566 | 1 | 0 | 39002.4566 | 1 | 0 | 277.5 | 1977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4583 | 1 | 0 | 39002.4583 | 1 | 0 | 431.5 | 2131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4601 | 1 | 0 | 39002.4601 | 1 | 0 | 585.5 | 2285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4619 | 1 | 0 | 39002.4619 | 1 | 0 | 739.5 | 2439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4637 | 1 | 0 | 39002.4637 | 1 | 0 | 893.5 | 2593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4655 | 1 | 0 | 39002.4655 | 1 | 0 | 1047.5 | 2747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.4672 | 1 | 0 | 39002.4673 | 1 | 0 | 1201.5 | 2901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244438 | 244438 | 244437.9994
39002.469 | 32 | 30 | 39002.469 | 19 | 18 | 1355.5 | 3055.5 | 1.9536 | 1.8315 | 1.16 | 1.0989 | 0.019536 | 0.018315 | 0.0116 | 0.010989 | 0.001221 | 0.0006105 | 121408.4251 | 246289.4852 | 7941.3756
39002.4708 | 2429 | 0 | 39002.4708 | 2380 | 0 | 1509.5 | 3209.5 | 148.2906 | 0 | 145.2991 | 0 | 1.4829 | 0 | 1.453 | 0 | 1.4829 | 1.453 | 0.67435 | 2.7471 | 0.80855
39002.4726 | 1949 | 0 | 39002.4726 | 2140 | 0 | 1663 | 3363 | 118.9866 | 0 | 130.6471 | 0 | 1.1899 | 0 | 1.3065 | 0 | 1.1899 | 1.3065 | 25.4684 | 14.2701 | 24.2786
39002.4744 | 2135 | 1 | 39002.4744 | 2246 | 1 | 1817 | 3517 | 130.3419 | 0.06105 | 137.1184 | 0.06105 | 1.3034 | 0.0006105 | 1.3712 | 0.0006105 | 1.3028 | 1.3706 | 14.6214 | 8.9082 | 2530.5909
39002.4761 | 1967 | 1 | 39002.4762 | 2105 | 1 | 1971 | 3671 | 120.0855 | 0.06105 | 128.5104 | 0.06105 | 1.2009 | 0.0006105 | 1.2851 | 0.0006105 | 1.2002 | 1.2845 | 24.4093 | 16.2093 | 6658.6782
39002.4779 | 1918 | 1 | 39002.478 | 2405 | 2 | 2125 | 3825 | 117.094 | 0.06105 | 146.8254 | 0.1221 | 1.1709 | 0.0006105 | 1.4683 | 0.001221 | 1.1703 | 1.467 | 28.3894 | 1.6853 | 872.4261
39002.4797 | 2065 | 4 | 39002.4797 | 2207 | 5 | 2279 | 3979 | 126.0684 | 0.2442 | 134.7375 | 0.30525 | 1.2607 | 0.002442 | 1.3474 | 0.0030525 | 1.2582 | 1.3443 | 18.7889 | 10.958 | 929.2675
39002.4815 | 1979 | 434 | 39002.4815 | 1823 | 534 | 2433 | 4133 | 120.8181 | 26.4957 | 111.2943 | 32.6007 | 1.2082 | 0.26496 | 1.1129 | 0.32601 | 0.94322 | 0.78694 | 14.5492 | 26.136 | 1.5459
39002.4833 | 2092 | 7 | 39002.4833 | 2422 | 7 | 2587 | 4287 | 127.7167 | 0.42735 | 147.8632 | 0.42735 | 1.2772 | 0.0042735 | 1.4786 | 0.0042735 | 1.2729 | 1.4744 | 25.7928 | 0.97912 | 47.9798
39002.4851 | 1 | 0 | 39002.4851 | 0 | 0 | 2741 | 4441 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 244438 | 488976 | 244437.9994

## C3-4
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 154.9072 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 3 & 4
Time-91 | N11 | N12 | Time-92 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39002.4351 | 1 | 0 | 39002.4352 | 1 | 0 | -1573 | 127 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4369 | 0 | 0 | 39002.4369 | 1 | 0 | -1419 | 281 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 507376 | 253638 | 507375.9997
39002.4387 | 1 | 0 | 39002.4387 | 1 | 0 | -1265 | 435 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4405 | 1 | 0 | 39002.4405 | 1 | 0 | -1111 | 589 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4423 | 1 | 0 | 39002.4423 | 1 | 0 | -957.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.444 | 1 | 0 | 39002.4441 | 1 | 0 | -803.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4458 | 1 | 0 | 39002.4458 | 1 | 0 | -649.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4476 | 1 | 0 | 39002.4476 | 1 | 0 | -495.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4494 | 1 | 0 | 39002.4494 | 1 | 0 | -341.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4512 | 1 | 0 | 39002.4512 | 1 | 0 | -187.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.453 | 1 | 0 | 39002.453 | 1 | 0 | -33.5 | 1666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4547 | 1 | 0 | 39002.4547 | 1 | 0 | 120.5 | 1820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4565 | 1 | 0 | 39002.4565 | 1 | 0 | 274.5 | 1974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4583 | 1 | 0 | 39002.4583 | 1 | 0 | 428.5 | 2128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4601 | 1 | 0 | 39002.4601 | 1 | 0 | 582.5 | 2282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4619 | 1 | 0 | 39002.4619 | 0 | 0 | 736.5 | 2436.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 253638 | 507376 | 253637.9994
39002.4636 | 1 | 0 | 39002.4637 | 0 | 0 | 890.5 | 2590.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 253638 | 507376 | 253637.9994
39002.4654 | 1 | 0 | 39002.4654 | 1 | 0 | 1044.5 | 2744.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.4672 | 1 | 0 | 39002.4672 | 1 | 0 | 1198.5 | 2898.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39002.469 | 5 | 4 | 39002.469 | 9 | 8 | 1352.5 | 3052.5 | 0.30525 | 0.2442 | 0.54945 | 0.4884 | 0.0030525 | 0.002442 | 0.0054945 | 0.004884 | 0.0006105 | 0.0006105 | 253638 | 253638 | 63184.5887
39002.4708 | 2127 | 48 | 39002.4708 | 2409 | 0 | 1506.5 | 3206.5 | 129.8535 | 2.9304 | 147.0696 | 0 | 1.2985 | 0.029304 | 1.4707 | 0 | 1.2692 | 1.4707 | 34.8282 | 5.3292 | 38.1975
39002.4726 | 2521 | 0 | 39002.4726 | 2502 | 0 | 1660.5 | 3360.5 | 153.9072 | 0 | 152.7473 | 0 | 1.5391 | 0 | 1.5275 | 0 | 1.5391 | 1.5275 | 0.64974 | 1.4141 | 0.88933
39002.4743 | 2381 | 0 | 39002.4744 | 1925 | 0 | 1814.5 | 3514.5 | 145.3602 | 0 | 117.5214 | 0 | 1.4536 | 0 | 1.1752 | 0 | 1.4536 | 1.1752 | 6.5678 | 31.8119 | 5.1142
39002.4761 | 2039 | 0 | 39002.4761 | 2157 | 0 | 1968.5 | 3668.5 | 124.4811 | 0 | 131.685 | 0 | 1.2448 | 0 | 1.3168 | 0 | 1.2448 | 1.3168 | 24.4424 | 17.6347 | 23.1976
39002.4779 | 2007 | 0 | 39002.4779 | 2004 | 0 | 2122.5 | 3822.5 | 122.5275 | 0 | 122.3443 | 0 | 1.2253 | 0 | 1.2234 | 0 | 1.2253 | 1.2234 | 26.4265 | 26.6158 | 25.2012
39002.4797 | 1929 | 4 | 39002.4797 | 2229 | 4 | 2276.5 | 3976.5 | 117.7656 | 0.2442 | 136.0806 | 0.2442 | 1.1777 | 0.002442 | 1.3608 | 0.002442 | 1.1752 | 1.3584 | 32.0825 | 13.9379 | 1848.3261
39002.4815 | 1546 | 475 | 39002.4815 | 1671 | 627 | 2430.5 | 4130.5 | 94.3834 | 28.9988 | 102.0147 | 38.2784 | 0.94383 | 0.28999 | 1.0201 | 0.38278 | 0.65385 | 0.63736 | 129.8833 | 154.3637 | 65.9729
39002.4833 | 2121 | 8 | 39002.4833 | 1945 | 7 | 2584.5 | 4284.5 | 129.4872 | 0.4884 | 118.7424 | 0.42735 | 1.2949 | 0.004884 | 1.1874 | 0.0042735 | 1.29 | 1.1832 | 19.9482 | 31.1302 | 1211.8643
39002.485 | 1 | 0 | 39002.485 | 1 | 0 | 2738.5 | 4438.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994

## C2-7
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 146.4212 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 7
Time-89 | N11 | N12 | Time-90 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R7-G | R2-7
39002.4351 | 1 | 0 | 39002.4351 | 1 | 0 | -1576 | 124 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4369 | 1 | 0 | 39002.4369 | 1 | 0 | -1422 | 278 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4387 | 1 | 0 | 39002.4387 | 1 | 0 | -1268 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4404 | 1 | 0 | 39002.4405 | 1 | 0 | -1114 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4422 | 1 | 0 | 39002.4422 | 1 | 0 | -960 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.444 | 1 | 0 | 39002.444 | 0 | 0 | -806 | 894 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 239738 | 479576 | 239737.9994
39002.4458 | 1 | 0 | 39002.4458 | 1 | 0 | -652 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4476 | 1 | 0 | 39002.4476 | 1 | 0 | -498 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4494 | 1 | 0 | 39002.4494 | 1 | 0 | -344 | 1356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4511 | 1 | 0 | 39002.4512 | 1 | 0 | -190 | 1510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4529 | 1 | 0 | 39002.4529 | 1 | 0 | -36 | 1664 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
| 1 | 0 | 39002.4547 | 1 | 0 | 118 | 1818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4565 | 1 | 0 | 39002.4565 | 1 | 0 | 271.5 | 1971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4583 | 0 | 0 | 39002.4583 | 1 | 0 | 426 | 2126 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 479576 | 239738 | 479575.9997
39002.46 | 1 | 0 | 39002.4601 | 1 | 0 | 579.5 | 2279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4618 | 1 | 0 | 39002.4618 | 1 | 0 | 733.5 | 2433.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4636 | 1 | 0 | 39002.4636 | 1 | 0 | 887.5 | 2587.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4654 | 1 | 0 | 39002.4654 | 1 | 0 | 1041.5 | 2741.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.4672 | 1 | 0 | 39002.4672 | 1 | 0 | 1195.5 | 2895.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239738 | 239738 | 239737.9994
39002.469 | 11 | 9 | 39002.469 | 50 | 49 | 1349.5 | 3049.5 | 0.67155 | 0.54945 | 3.0525 | 2.9915 | 0.0067155 | 0.0054945 | 0.030525 | 0.029915 | 0.001221 | 0.0006105 | 119588.7683 | 244871.2946 | 26415.6569
39002.4707 | 2127 | 0 | 39002.4708 | 2165 | 126 | 1503.5 | 3203.5 | 129.8535 | 0 | 132.1734 | 7.6923 | 1.2985 | 0 | 1.3217 | 0.076923 | 1.2985 | 1.2448 | 12.7588 | 17.6253 | 11.4603
39002.4725 | 2317 | 0 | 39002.4725 | 2101 | 0 | 1657.5 | 3357.5 | 141.453 | 0 | 128.2662 | 0 | 1.4145 | 0 | 1.2827 | 0 | 1.4145 | 1.2827 | 3.5123 | 14.1542 | 2.0978
39002.4743 | 2289 | 1 | 39002.4743 | 2266 | 1 | 1811.5 | 3511.5 | 139.7436 | 0.06105 | 138.3394 | 0.06105 | 1.3974 | 0.0006105 | 1.3834 | 0.0006105 | 1.3968 | 1.3828 | 4.8163 | 5.8987 | 603.6877
39002.4761 | 1932 | 0 | 39002.4761 | 1915 | 1 | 1965.5 | 3665.5 | 117.9487 | 0 | 116.9109 | 0.06105 | 1.1795 | 0 | 1.1691 | 0.0006105 | 1.1795 | 1.1685 | 24.1398 | 25.3072 | 22.9603
39002.4779 | 2136 | 2 | 39002.4779 | 1976 | 1 | 2119.5 | 3819.5 | 130.4029 | 0.1221 | 120.6349 | 0.06105 | 1.304 | 0.001221 | 1.2063 | 0.0006105 | 1.3028 | 1.2057 | 12.3491 | 21.4744 | 2301.5134
39002.4797 | 2008 | 3 | 39002.4797 | 1994 | 4 | 2273.5 | 3973.5 | 122.5885 | 0.18315 | 121.7338 | 0.2442 | 1.2259 | 0.0018315 | 1.2173 | 0.002442 | 1.2241 | 1.2149 | 19.6133 | 20.531 | 2199.518
39002.4814 | 1848 | 524 | 39002.4814 | 1606 | 438 | 2427.5 | 4127.5 | 112.8205 | 31.9902 | 98.0464 | 26.7399 | 1.1282 | 0.3199 | 0.98046 | 0.2674 | 0.8083 | 0.71306 | 47.2679 | 328.2887 | 3.8589
39002.4832 | 2382 | 10 | 39002.4832 | 1890 | 7 | 2581.5 | 4281.5 | 145.4212 | 0.6105 | 115.3846 | 0.42735 | 1.4542 | 0.006105 | 1.1538 | 0.0042735 | 1.4481 | 1.1496 | 0.69561 | 57.9883 | 23.4173
39002.485 | 2 | 0 | 39002.485 | 1 | 0 | 2735.5 | 4435.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 119819 | 239738 | 119818.9988

## C2-6
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 155.2735 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 6
Time-87 | N11 | N12 | Time-88 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39002.4351 | 1 | 0 | 39002.4351 | 1 | 0 | -1578.5 | 121.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4369 | 1 | 0 | 39002.4369 | 1 | 0 | -1424.5 | 275.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4386 | 1 | 0 | 39002.4386 | 1 | 0 | -1270.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4404 | 1 | 0 | 39002.4404 | 1 | 0 | -1116.5 | 583.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4422 | 1 | 0 | 39002.4422 | 1 | 0 | -962.5 | 737.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.444 | 1 | 0 | 39002.444 | 0 | 0 | -808.5 | 891.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 254238 | 508576 | 254237.9994
39002.4458 | 1 | 0 | 39002.4458 | 1 | 0 | -655 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4475 | 1 | 0 | 39002.4476 | 1 | 0 | -501 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4493 | 1 | 0 | 39002.4493 | 1 | 0 | -347 | 1353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4511 | 1 | 0 | 39002.4511 | 1 | 0 | -193 | 1507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4529 | 0 | 0 | 39002.4529 | 1 | 0 | -39 | 1661 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 508576 | 254238 | 508575.9997
39002.4547 | 1 | 0 | 39002.4547 | 1 | 0 | 115 | 1815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4564 | 1 | 0 | 39002.4565 | 1 | 0 | 269 | 1969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4582 | 0 | 0 | 39002.4583 | 1 | 0 | 423 | 2123 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 508576 | 254238 | 508575.9997
39002.46 | 1 | 0 | 39002.46 | 1 | 0 | 577 | 2277 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4618 | 1 | 0 | 39002.4618 | 1 | 0 | 731 | 2431 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4636 | 1 | 0 | 39002.4636 | 1 | 0 | 885 | 2585 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4654 | 1 | 0 | 39002.4654 | 1 | 0 | 1039 | 2739 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4671 | 1 | 0 | 39002.4672 | 1 | 0 | 1193 | 2893 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39002.4689 | 67 | 63 | 39002.4689 | 85 | 68 | 1347 | 3047 | 4.0904 | 3.8462 | 5.1893 | 4.1514 | 0.040904 | 0.038462 | 0.051893 | 0.041514 | 0.002442 | 0.010379 | 69427.5056 | 14544.8576 | 3804.6042
39002.4707 | 2527 | 0 | 39002.4707 | 2132 | 0 | 1501 | 3201 | 154.2735 | 0 | 130.1587 | 0 | 1.5427 | 0 | 1.3016 | 0 | 1.5427 | 1.3016 | 0.6482 | 19.2955 | 0.89454
39002.4725 | 2155 | 0 | 39002.4725 | 2280 | 0 | 1654.5 | 3354.5 | 131.5629 | 0 | 139.1941 | 0 | 1.3156 | 0 | 1.3919 | 0 | 1.3156 | 1.3919 | 18.0223 | 11.5518 | 16.7066
39002.4743 | 2466 | 0 | 39002.4743 | 2075 | 0 | 1809 | 3509 | 150.5495 | 0 | 126.6789 | 0 | 1.5055 | 0 | 1.2668 | 0 | 1.5055 | 1.2668 | 3.1379 | 22.5725 | 1.6324
39002.4761 | 2386 | 0 | 39002.4761 | 1957 | 0 | 1962.5 | 3662.5 | 145.6654 | 0 | 119.475 | 0 | 1.4567 | 0 | 1.1947 | 0 | 1.4567 | 1.1947 | 6.596 | 29.9632 | 5.1393
39002.4778 | 2466 | 0 | 39002.4778 | 1947 | 1 | 2116.5 | 3816.5 | 150.5495 | 0 | 118.8645 | 0.06105 | 1.5055 | 0 | 1.1886 | 0.0006105 | 1.5055 | 1.188 | 3.1379 | 30.6978 | 1.6324
39002.4796 | 2457 | 4 | 39002.4796 | 1896 | 3 | 2270.5 | 3970.5 | 150 | 0.2442 | 115.7509 | 0.18315 | 1.5 | 0.002442 | 1.1575 | 0.0018315 | 1.4976 | 1.1557 | 3.5375 | 35.8026 | 542.9601
39002.4814 | 2153 | 225 | 39002.4814 | 1983 | 424 | 2424.5 | 4124.5 | 131.4408 | 13.7363 | 121.0623 | 25.8852 | 1.3144 | 0.13736 | 1.2106 | 0.25885 | 1.177 | 0.95177 | 16.9072 | 59.0613 | 27.2922
39002.4832 | 2275 | 11 | 39002.4832 | 2171 | 9 | 2578.5 | 4278.5 | 138.8889 | 0.67155 | 132.5397 | 0.54945 | 1.3889 | 0.0067155 | 1.3254 | 0.0054945 | 1.3822 | 1.3199 | 12.1863 | 17.833 | 354.1118
39002.485 | 2005 | 73 | 39002.485 | 2325 | 73 | 2732.5 | 4432.5 | 122.4054 | 4.4567 | 141.9414 | 4.4567 | 1.2241 | 0.044567 | 1.4194 | 0.044567 | 1.1795 | 1.3748 | 43.5869 | 10.4763 | 60.4537

## C2-5
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 153.9304 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 5
Time-85 | N11 | N12 | Time-86 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39002.435 | 1 | 0 | 39002.435 | 1 | 0 | -1581.5 | 118.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4368 | 1 | 0 | 39002.4368 | 1 | 0 | -1427.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4386 | 1 | 0 | 39002.4386 | 0 | 0 | -1273.5 | 426.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 252038 | 504176 | 252037.9994
39002.4404 | 0 | 0 | 39002.4404 | 1 | 0 | -1119.5 | 580.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 504176 | 252038 | 504175.9997
39002.4422 | 1 | 0 | 39002.4422 | 1 | 0 | -965.5 | 734.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4439 | 1 | 0 | 39002.444 | 1 | 0 | -811.5 | 888.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4457 | 1 | 0 | 39002.4457 | 1 | 0 | -657.5 | 1042.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4475 | 1 | 0 | 39002.4475 | 1 | 0 | -503.5 | 1196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4493 | 1 | 0 | 39002.4493 | 1 | 0 | -349.5 | 1350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4511 | 1 | 0 | 39002.4511 | 1 | 0 | -195.5 | 1504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4529 | 1 | 0 | 39002.4529 | 0 | 0 | -41.5 | 1658.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 252038 | 504176 | 252037.9994
39002.4546 | 1 | 0 | 39002.4547 | 1 | 0 | 112 | 1812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4564 | 0 | 0 | 39002.4564 | 1 | 0 | 266.5 | 1966.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 504176 | 252038 | 504175.9997
39002.4582 | 1 | 0 | 39002.4582 | 1 | 0 | 420.5 | 2120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.46 | 1 | 0 | 39002.46 | 1 | 0 | 574 | 2274 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4618 | 1 | 0 | 39002.4618 | 1 | 0 | 728 | 2428 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4635 | 1 | 0 | 39002.4636 | 1 | 0 | 882 | 2582 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4653 | 1 | 0 | 39002.4653 | 1 | 0 | 1036 | 2736 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252038 | 252038 | 252037.9994
39002.4671 | 1 | 0 | 39002.4671 | 0 | 0 | 1190 | 2890 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 252038 | 504176 | 252037.9994
39002.4689 | 37 | 33 | 39002.4689 | 34 | 33 | 1344 | 3044 | 2.2589 | 2.0147 | 2.0757 | 2.0147 | 0.022589 | 0.020147 | 0.020757 | 0.020147 | 0.002442 | 0.0006105 | 62305.2051 | 262649.2371 | 7425.5971
39002.4707 | 2334 | 0 | 39002.4707 | 1725 | 0 | 1498 | 3198 | 142.4908 | 0 | 105.3114 | 0 | 1.4249 | 0 | 1.0531 | 0 | 1.4249 | 1.0531 | 8.0283 | 46.167 | 6.6034
39002.4725 | 2101 | 0 | 39002.4725 | 2387 | 0 | 1652 | 3352 | 128.2662 | 0 | 145.7265 | 0 | 1.2827 | 0 | 1.4573 | 0 | 1.2827 | 1.4573 | 20.0086 | 5.6297 | 18.7259
39002.4742 | 2107 | 2 | 39002.4743 | 1979 | 0 | 1806 | 3506 | 128.6325 | 0.1221 | 120.8181 | 0 | 1.2863 | 0.001221 | 1.2082 | 0 | 1.2851 | 1.2082 | 19.754 | 27.4068 | 4435.4017
39002.476 | 2505 | 0 | 39002.476 | 2046 | 0 | 1960 | 3660 | 152.9304 | 0 | 124.9084 | 0 | 1.5293 | 0 | 1.2491 | 0 | 1.5293 | 1.2491 | 0.65389 | 23.2346 | 0.87541
39002.4778 | 2066 | 1 | 39002.4778 | 2268 | 0 | 2114 | 3814 | 126.1294 | 0.06105 | 138.4615 | 0 | 1.2613 | 0.0006105 | 1.3846 | 0 | 1.2607 | 1.3846 | 22.1483 | 11.172 | 4566.1822
39002.4796 | 1914 | 3 | 39002.4796 | 2273 | 4 | 2268 | 3968 | 116.8498 | 0.18315 | 138.7668 | 0.2442 | 1.1685 | 0.0018315 | 1.3877 | 0.002442 | 1.1667 | 1.3852 | 32.2432 | 11.0069 | 1997.5708
39002.4814 | 1543 | 411 | 39002.4814 | 1613 | 522 | 2422 | 4122 | 94.2002 | 25.0916 | 98.4737 | 31.8681 | 0.942 | 0.25092 | 0.98474 | 0.31868 | 0.69109 | 0.66606 | 116.2642 | 141.4872 | 80.8826
39002.4831 | 1993 | 10 | 39002.4832 | 1949 | 9 | 2576 | 4276 | 121.6728 | 0.6105 | 118.9866 | 0.54945 | 1.2167 | 0.006105 | 1.1899 | 0.0054945 | 1.2106 | 1.1844 | 27.1008 | 30.018 | 1196.8129
39002.4849 | 2301 | 77 | 39002.485 | 2259 | 94 | 2730 | 4430 | 140.4762 | 4.7009 | 137.9121 | 5.7387 | 1.4048 | 0.047009 | 1.3791 | 0.057387 | 1.3578 | 1.3217 | 12.1358 | 18.8704 | 29.5601

## C2-4
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 151.5495 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 4
Time-83 | N11 | N12 | Time-84 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39002.435 | 1 | 0 | 39002.435 | 1 | 0 | -1584.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4368 | 1 | 0 | 39002.4368 | 1 | 0 | -1430.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4386 | 1 | 0 | 39002.4386 | 1 | 0 | -1276.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4403 | 0 | 0 | 39002.4404 | 1 | 0 | -1122.5 | 577.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 496376 | 248138 | 496375.9997
39002.4421 | 1 | 0 | 39002.4421 | 1 | 0 | -968.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4439 | 1 | 0 | 39002.4439 | 1 | 0 | -814.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4457 | 1 | 0 | 39002.4457 | 1 | 0 | -660.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4475 | 1 | 0 | 39002.4475 | 1 | 0 | -506.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4493 | 1 | 0 | 39002.4493 | 1 | 0 | -352.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.451 | 1 | 0 | 39002.4511 | 1 | 0 | -198.5 | 1501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4528 | 1 | 0 | 39002.4528 | 1 | 0 | -44.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4546 | 1 | 0 | 39002.4546 | 1 | 0 | 109.5 | 1809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4564 | 1 | 0 | 39002.4564 | 1 | 0 | 263.5 | 1963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4582 | 1 | 0 | 39002.4582 | 1 | 0 | 417.5 | 2117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.46 | 1 | 0 | 39002.46 | 1 | 0 | 571.5 | 2271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4617 | 1 | 0 | 39002.4617 | 1 | 0 | 725.5 | 2425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4635 | 1 | 0 | 39002.4635 | 1 | 0 | 879.5 | 2579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4653 | 1 | 0 | 39002.4653 | 1 | 0 | 1033.5 | 2733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4671 | 1 | 0 | 39002.4671 | 1 | 0 | 1187.5 | 2887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4689 | 1 | 0 | 39002.4689 | 8 | 7 | 1341.5 | 3041.5 | 0.06105 | 0 | 0.4884 | 0.42735 | 0.0006105 | 0 | 0.004884 | 0.0042735 | 0.0006105 | 0.0006105 | 248138 | 248138 | 248137.9994
39002.4706 | 2015 | 0 | 39002.4707 | 2092 | 0 | 1495.5 | 3195.5 | 123.0159 | 0 | 127.7167 | 0 | 1.2302 | 0 | 1.2772 | 0 | 1.2302 | 1.2772 | 23.195 | 18.6606 | 21.9649
39002.4724 | 2065 | 0 | 39002.4724 | 2315 | 0 | 1649 | 3349 | 126.0684 | 0 | 141.3309 | 0 | 1.2607 | 0 | 1.4133 | 0 | 1.2607 | 1.4133 | 20.2121 | 7.2302 | 18.9514
39002.4742 | 2350 | 1 | 39002.4742 | 2101 | 0 | 1803 | 3503 | 143.4676 | 0.06105 | 128.2662 | 0 | 1.4347 | 0.0006105 | 1.2827 | 0 | 1.4341 | 1.2827 | 5.6488 | 18.1523 | 2018.4542
39002.476 | 2130 | 0 | 39002.476 | 2199 | 0 | 1957 | 3657 | 130.0366 | 0 | 134.2491 | 0 | 1.3004 | 0 | 1.3425 | 0 | 1.3004 | 1.3425 | 16.5437 | 12.8868 | 15.2433
39002.4778 | 2458 | 0 | 39002.4778 | 2016 | 0 | 2111 | 3811 | 150.0611 | 0 | 123.0769 | 0 | 1.5006 | 0 | 1.2308 | 0 | 1.5006 | 1.2308 | 0.99186 | 23.1339 | 0.50875
39002.4795 | 2071 | 3 | 39002.4796 | 2466 | 4 | 2265 | 3965 | 126.4347 | 0.18315 | 150.5495 | 0.2442 | 1.2643 | 0.0018315 | 1.5055 | 0.002442 | 1.2625 | 1.5031 | 25.3943 | 0.6696 | 90.5437
39002.4813 | 2010 | 347 | 39002.4814 | 1864 | 481 | 2419 | 4119 | 122.7106 | 21.1844 | 113.7973 | 29.3651 | 1.2271 | 0.21184 | 1.138 | 0.29365 | 1.0153 | 0.84432 | 22.828 | 85.4039 | 16.644
39002.4831 | 2265 | 13 | 39002.4831 | 2285 | 12 | 2573 | 4273 | 138.2784 | 0.79365 | 139.4994 | 0.7326 | 1.3828 | 0.0079365 | 1.395 | 0.007326 | 1.3748 | 1.3877 | 10.3025 | 9.1527 | 131.8285
39002.4849 | 1979 | 52 | 39002.4849 | 2127 | 67 | 2727 | 4427 | 120.8181 | 3.1746 | 129.8535 | 4.0904 | 1.2082 | 0.031746 | 1.2985 | 0.040904 | 1.1764 | 1.2576 | 30.3632 | 19.3211 | 140.5572

## C2-3
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 151.1832 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 2 & 3
Time-81 | N11 | N12 | Time-82 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39002.435 | 1 | 0 | 39002.435 | 1 | 0 | -1587 | 113 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4367 | 1 | 0 | 39002.4368 | 1 | 0 | -1433 | 267 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4385 | 1 | 0 | 39002.4386 | 1 | 0 | -1279 | 421 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4403 | 1 | 0 | 39002.4403 | 1 | 0 | -1125.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4421 | 1 | 0 | 39002.4421 | 1 | 0 | -971 | 729 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4439 | 1 | 0 | 39002.4439 | 0 | 0 | -817 | 883 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 247538 | 495176 | 247537.9994
39002.4457 | 1 | 0 | 39002.4457 | 0 | 0 | -663.5 | 1036.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 247538 | 495176 | 247537.9994
39002.4474 | 1 | 0 | 39002.4475 | 1 | 0 | -509.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4492 | 1 | 0 | 39002.4492 | 1 | 0 | -355.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.451 | 1 | 0 | 39002.451 | 0 | 0 | -201.5 | 1498.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 247538 | 495176 | 247537.9994
39002.4528 | 1 | 0 | 39002.4528 | 1 | 0 | -47.5 | 1652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4546 | 1 | 0 | 39002.4546 | 1 | 0 | 106.5 | 1806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4564 | 1 | 0 | 39002.4564 | 1 | 0 | 260.5 | 1960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4581 | 1 | 0 | 39002.4581 | 1 | 0 | 414.5 | 2114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4599 | 1 | 0 | 39002.4599 | 1 | 0 | 568.5 | 2268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4617 | 1 | 0 | 39002.4617 | 1 | 0 | 722.5 | 2422.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4635 | 1 | 0 | 39002.4635 | 1 | 0 | 876.5 | 2576.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4653 | 1 | 0 | 39002.4653 | 1 | 0 | 1030.5 | 2730.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.467 | 1 | 0 | 39002.4671 | 1 | 0 | 1184.5 | 2884.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4688 | 1 | 0 | 39002.4688 | 10 | 9 | 1338.5 | 3038.5 | 0.06105 | 0 | 0.6105 | 0.54945 | 0.0006105 | 0 | 0.006105 | 0.0054945 | 0.0006105 | 0.0006105 | 247538 | 247538 | 247537.9994
39002.4706 | 2262 | 0 | 39002.4706 | 2435 | 0 | 1492.5 | 3192.5 | 138.0952 | 0 | 148.6569 | 0 | 1.381 | 0 | 1.4866 | 0 | 1.381 | 1.4866 | 9.4775 | 1.6994 | 8.0965
39002.4724 | 2407 | 0 | 39002.4724 | 2229 | 0 | 1646.5 | 3346.5 | 146.9475 | 0 | 136.0806 | 0 | 1.4695 | 0 | 1.3608 | 0 | 1.4695 | 1.3608 | 2.8824 | 11.0983 | 1.413
39002.4742 | 2019 | 4 | 39002.4742 | 2107 | 4 | 1800.5 | 3500.5 | 123.2601 | 0.2442 | 128.6325 | 0.2442 | 1.2326 | 0.002442 | 1.2863 | 0.002442 | 1.2302 | 1.2839 | 22.9561 | 17.7112 | 1705.4231
39002.476 | 2042 | 0 | 39002.476 | 2455 | 0 | 1954.5 | 3654.5 | 124.6642 | 0 | 149.8779 | 0 | 1.2466 | 0 | 1.4988 | 0 | 1.2466 | 1.4988 | 21.2723 | 0.87088 | 20.0256
39002.4777 | 2460 | 1 | 39002.4778 | 2271 | 1 | 2108.5 | 3808.5 | 150.1832 | 0.06105 | 138.6447 | 0.06105 | 1.5018 | 0.0006105 | 1.3864 | 0.0006105 | 1.5012 | 1.3858 | 0.66893 | 9.6854 | 135.8081
39002.4795 | 2376 | 4 | 39002.4795 | 1980 | 3 | 2262.5 | 3962.5 | 145.0549 | 0.2442 | 120.8791 | 0.18315 | 1.4505 | 0.002442 | 1.2088 | 0.0018315 | 1.4481 | 1.207 | 4.2595 | 26.0353 | 497.7333
39002.4813 | 1736 | 200 | 39002.4813 | 1874 | 405 | 2416.5 | 4116.5 | 105.9829 | 12.21 | 114.4078 | 24.7253 | 1.0598 | 0.1221 | 1.1441 | 0.24725 | 0.93773 | 0.89683 | 57.8014 | 78.4017 | 118.7397
39002.4831 | 2296 | 16 | 39002.4831 | 2102 | 13 | 2570.5 | 4270.5 | 140.1709 | 0.9768 | 128.3272 | 0.79365 | 1.4017 | 0.009768 | 1.2833 | 0.0079365 | 1.3919 | 1.2753 | 8.2085 | 19.3916 | 166.8666
39002.4849 | 1940 | 31 | 39002.4849 | 2123 | 40 | 2724.5 | 4424.5 | 118.4371 | 1.8926 | 129.6093 | 2.442 | 1.1844 | 0.018926 | 1.2961 | 0.02442 | 1.1654 | 1.2717 | 30.8683 | 18.0903 | 249.7404

## C1-7
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 151.9768 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 7
Time-79 | N11 | N12 | Time-80 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R7-G | R1-7
39002.4349 | 1 | 0 | 39002.435 | 0 | 0 | -1590 | 110 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248838 | 497776 | 248837.9994
39002.4367 | 1 | 0 | 39002.4367 | 1 | 0 | -1436 | 264 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4385 | 1 | 0 | 39002.4385 | 1 | 0 | -1282 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4403 | 1 | 0 | 39002.4403 | 1 | 0 | -1128 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4421 | 1 | 0 | 39002.4421 | 1 | 0 | -974 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4438 | 1 | 0 | 39002.4439 | 1 | 0 | -820 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4456 | 0 | 0 | 39002.4456 | 1 | 0 | -666 | 1034 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 497776 | 248838 | 497775.9997
39002.4474 | 1 | 0 | 39002.4474 | 0 | 0 | -512 | 1188 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248838 | 497776 | 248837.9994
39002.4492 | 1 | 0 | 39002.4492 | 1 | 0 | -358 | 1342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.451 | 1 | 0 | 39002.451 | 1 | 0 | -204 | 1496 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4528 | 1 | 0 | 39002.4528 | 0 | 0 | -50 | 1650 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 248838 | 497776 | 248837.9994
39002.4545 | 1 | 0 | 39002.4545 | 1 | 0 | 103.5 | 1803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4563 | 1 | 0 | 39002.4563 | 1 | 0 | 258 | 1958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4581 | 1 | 0 | 39002.4581 | 1 | 0 | 412 | 2112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4599 | 1 | 0 | 39002.4599 | 1 | 0 | 565.5 | 2265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4617 | 1 | 0 | 39002.4617 | 1 | 0 | 719.5 | 2419.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4634 | 1 | 0 | 39002.4635 | 1 | 0 | 873.5 | 2573.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4652 | 1 | 0 | 39002.4652 | 1 | 0 | 1027.5 | 2727.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.467 | 1 | 0 | 39002.467 | 1 | 0 | 1181.5 | 2881.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4688 | 1 | 0 | 39002.4688 | 1 | 0 | 1335.5 | 3035.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248838 | 248838 | 248837.9994
39002.4706 | 2129 | 0 | 39002.4706 | 2040 | 0 | 1489.5 | 3189.5 | 129.9756 | 0 | 124.5421 | 0 | 1.2998 | 0 | 1.2454 | 0 | 1.2998 | 1.2454 | 16.9272 | 22.0284 | 15.6274
39002.4724 | 2381 | 0 | 39002.4724 | 2473 | 0 | 1643.5 | 3343.5 | 145.3602 | 0 | 150.9768 | 0 | 1.4536 | 0 | 1.5098 | 0 | 1.4536 | 1.5098 | 4.5519 | 0.66235 | 3.0983
39002.4741 | 2022 | 1 | 39002.4742 | 2148 | 1 | 1797.5 | 3497.5 | 123.4432 | 0.06105 | 131.1355 | 0.06105 | 1.2344 | 0.0006105 | 1.3114 | 0.0006105 | 1.2338 | 1.3107 | 23.1982 | 15.9323 | 6409.3543
39002.4759 | 2016 | 0 | 39002.4759 | 2470 | 0 | 1951.5 | 3651.5 | 123.0769 | 0 | 150.7937 | 0 | 1.2308 | 0 | 1.5079 | 0 | 1.2308 | 1.5079 | 23.4812 | 0.78462 | 22.2504
39002.4777 | 2022 | 1 | 39002.4777 | 1925 | 0 | 2105.5 | 3805.5 | 123.4432 | 0.06105 | 117.5214 | 0 | 1.2344 | 0.0006105 | 1.1752 | 0 | 1.2338 | 1.1752 | 23.1653 | 29.3184 | 10573.5382
39002.4795 | 2448 | 6 | 39002.4795 | 2156 | 4 | 2259.5 | 3959.5 | 149.4505 | 0.3663 | 131.6239 | 0.2442 | 1.4945 | 0.003663 | 1.3162 | 0.002442 | 1.4908 | 1.3138 | 1.7188 | 17.37 | 87.267
39002.4813 | 2062 | 352 | 39002.4813 | 1614 | 302 | 2413.5 | 4113.5 | 125.8852 | 21.4896 | 98.5348 | 18.4371 | 1.2589 | 0.2149 | 0.98535 | 0.18437 | 1.044 | 0.80098 | 25.874 | 604.5156 | 18.3751
39002.4831 | 2190 | 17 | 39002.4831 | 1922 | 14 | 2567.5 | 4267.5 | 133.6996 | 1.0379 | 117.3382 | 0.8547 | 1.337 | 0.010379 | 1.1734 | 0.008547 | 1.3266 | 1.1648 | 14.1297 | 31.3657 | 396.605
39002.4848 | 2375 | 31 | 39002.4848 | 2146 | 33 | 2721.5 | 4421.5 | 144.9939 | 1.8926 | 131.0134 | 2.0147 | 1.4499 | 0.018926 | 1.3101 | 0.020147 | 1.431 | 1.29 | 5.1736 | 23.2776 | 50.7872

## C1-6
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 152.16 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 6
Time-77 | N11 | N12 | Time-78 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39002.4349 | 1 | 0 | 39002.4349 | 1 | 0 | -1592.5 | 107.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4367 | 1 | 0 | 39002.4367 | 1 | 0 | -1438.5 | 261.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4385 | 1 | 0 | 39002.4385 | 1 | 0 | -1284.5 | 415.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4402 | 1 | 0 | 39002.4403 | 1 | 0 | -1131 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.442 | 1 | 0 | 39002.442 | 1 | 0 | -977 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4438 | 1 | 0 | 39002.4438 | 0 | 0 | -822.5 | 877.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 249138 | 498376 | 249137.9994
39002.4456 | 1 | 0 | 39002.4456 | 1 | 0 | -669 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4474 | 1 | 0 | 39002.4474 | 1 | 0 | -515 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4492 | 1 | 0 | 39002.4492 | 1 | 0 | -361 | 1339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4509 | 1 | 0 | 39002.451 | 1 | 0 | -207 | 1493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4527 | 1 | 0 | 39002.4527 | 1 | 0 | -53 | 1647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4545 | 1 | 0 | 39002.4545 | 1 | 0 | 101 | 1801 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4563 | 1 | 0 | 39002.4563 | 1 | 0 | 255 | 1955 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4581 | 1 | 0 | 39002.4581 | 1 | 0 | 409 | 2109 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4598 | 1 | 0 | 39002.4599 | 1 | 0 | 563 | 2263 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4616 | 1 | 0 | 39002.4617 | 1 | 0 | 717 | 2417 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4634 | 1 | 0 | 39002.4634 | 1 | 0 | 871 | 2571 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4652 | 1 | 0 | 39002.4652 | 1 | 0 | 1025 | 2725 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.467 | 1 | 0 | 39002.467 | 1 | 0 | 1179 | 2879 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4688 | 1 | 0 | 39002.4688 | 1 | 0 | 1333 | 3033 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39002.4705 | 2476 | 0 | 39002.4706 | 1319 | 0 | 1487 | 3187 | 151.16 | 0 | 80.525 | 0 | 1.5116 | 0 | 0.80525 | 0 | 1.5116 | 0.80525 | 0.66155 | 88.9598 | 0.85005
39002.4723 | 1954 | 0 | 39002.4723 | 2018 | 0 | 1640.5 | 3340.5 | 119.2918 | 0 | 123.199 | 0 | 1.1929 | 0 | 1.232 | 0 | 1.1929 | 1.232 | 27.5527 | 23.5074 | 26.3598
39002.4741 | 2436 | 0 | 39002.4741 | 2335 | 2 | 1794.5 | 3494.5 | 148.7179 | 0 | 142.5519 | 0.1221 | 1.4872 | 0 | 1.4255 | 0.001221 | 1.4872 | 1.4243 | 2.3144 | 6.8315 | 0.82727
39002.4759 | 2282 | 0 | 39002.4759 | 2137 | 0 | 1948.5 | 3648.5 | 139.3162 | 0 | 130.464 | 0 | 1.3932 | 0 | 1.3046 | 0 | 1.3932 | 1.3046 | 9.2191 | 16.6299 | 7.8259
39002.4777 | 2439 | 1 | 39002.4777 | 2291 | 0 | 2102.5 | 3802.5 | 148.9011 | 0.06105 | 139.8657 | 0 | 1.489 | 0.0006105 | 1.3987 | 0 | 1.4884 | 1.3987 | 2.1998 | 8.79 | 423.2214
39002.4795 | 1962 | 7 | 39002.4795 | 2069 | 7 | 2256.5 | 3956.5 | 119.7802 | 0.42735 | 126.3126 | 0.42735 | 1.1978 | 0.0042735 | 1.2631 | 0.0042735 | 1.1935 | 1.2589 | 27.6049 | 20.7881 | 1286.7981
39002.4812 | 1831 | 248 | 39002.4812 | 1654 | 208 | 2410.5 | 4110.5 | 111.7827 | 15.1404 | 100.9768 | 12.6984 | 1.1178 | 0.1514 | 1.0098 | 0.12698 | 0.96642 | 0.88278 | 51.9235 | 80.1962 | 74.1833
39002.483 | 2202 | 18 | 39002.483 | 1901 | 15 | 2564.5 | 4264.5 | 134.4322 | 1.0989 | 116.0562 | 0.91575 | 1.3443 | 0.010989 | 1.1606 | 0.0091575 | 1.3333 | 1.1514 | 13.6332 | 33.2989 | 378.0124
39002.4848 | 1882 | 36 | 39002.4848 | 2010 | 39 | 2718.5 | 4418.5 | 114.8962 | 2.1978 | 122.7106 | 2.381 | 1.149 | 0.021978 | 1.2271 | 0.02381 | 1.127 | 1.2033 | 35.7565 | 25.9075 | 328.3003

## C1-5
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 154.7851 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 5
Time-75 | N11 | N12 | Time-76 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39002.4349 | 1 | 0 | 39002.4349 | 1 | 0 | -1595.5 | 104.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4367 | 1 | 0 | 39002.4367 | 0 | 0 | -1441.5 | 258.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 253438 | 506976 | 253437.9994
39002.4384 | 1 | 0 | 39002.4384 | 1 | 0 | -1287.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4402 | 0 | 0 | 39002.4402 | 1 | 0 | -1133.5 | 566.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 506976 | 253438 | 506975.9997
39002.442 | 1 | 0 | 39002.442 | 1 | 0 | -979.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4438 | 1 | 0 | 39002.4438 | 1 | 0 | -825.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4456 | 1 | 0 | 39002.4456 | 1 | 0 | -671.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4473 | 1 | 0 | 39002.4474 | 1 | 0 | -517.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4491 | 1 | 0 |  | 1 | 0 | -364 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4509 | 1 | 0 | 39002.4509 | 1 | 0 | -209.5 | 1490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4527 | 1 | 0 | 39002.4527 | 0 | 0 | -55.5 | 1644.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 253438 | 506976 | 253437.9994
39002.4545 | 1 | 0 | 39002.4545 | 1 | 0 | 98 | 1798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4563 | 1 | 0 | 39002.4563 | 1 | 0 | 252.5 | 1952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.458 | 1 | 0 | 39002.4581 | 1 | 0 | 406.5 | 2106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4598 | 1 | 0 | 39002.4598 | 1 | 0 | 560.5 | 2260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4616 | 1 | 0 | 39002.4616 | 1 | 0 | 714 | 2414 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4634 | 1 | 0 | 39002.4634 | 1 | 0 | 868 | 2568 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4652 | 1 | 0 | 39002.4652 | 1 | 0 | 1022 | 2722 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4669 | 0 | 0 | 39002.467 | 1 | 0 | 1176 | 2876 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 506976 | 253438 | 506975.9997
39002.4687 | 1 | 0 | 39002.4688 | 1 | 0 | 1330 | 3030 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253438 | 253438 | 253437.9994
39002.4705 | 1929 | 0 | 39002.4705 | 1736 | 0 | 1484 | 3184 | 117.7656 | 0 | 105.9829 | 0 | 1.1777 | 0 | 1.0598 | 0 | 1.1777 | 1.0598 | 31.4349 | 46.0472 | 30.2573
39002.4723 | 2519 | 0 | 39002.4723 | 1990 | 0 | 1638 | 3338 | 153.7851 | 0 | 121.4896 | 0 | 1.5379 | 0 | 1.2149 | 0 | 1.5379 | 1.2149 | 0.65026 | 27.406 | 0.88759
39002.4741 | 1955 | 0 | 39002.4741 | 2166 | 1 | 1792 | 3492 | 119.3529 | 0 | 132.2344 | 0.06105 | 1.1935 | 0 | 1.3223 | 0.0006105 | 1.1935 | 1.3217 | 29.687 | 17.1076 | 28.4934
39002.4759 | 2177 | 0 | 39002.4759 | 2486 | 0 | 1946 | 3646 | 132.906 | 0 | 151.7705 | 0 | 1.3291 | 0 | 1.5177 | 0 | 1.3291 | 1.5177 | 16.4621 | 1.9863 | 15.133
39002.4776 | 2168 | 0 | 39002.4777 | 2320 | 1 | 2100 | 3800 | 132.3565 | 0 | 141.6361 | 0.06105 | 1.3236 | 0 | 1.4164 | 0.0006105 | 1.3236 | 1.4158 | 16.9456 | 9.3307 | 15.622
39002.4794 | 1970 | 7 | 39002.4794 | 2365 | 8 | 2254 | 3954 | 120.2686 | 0.42735 | 144.3834 | 0.4884 | 1.2027 | 0.0042735 | 1.4438 | 0.004884 | 1.1984 | 1.4389 | 30.2788 | 7.3106 | 543.4303
39002.4812 | 1428 | 561 | 39002.4812 | 1683 | 521 | 2408 | 4108 | 87.1795 | 34.2491 | 102.7473 | 31.8071 | 0.87179 | 0.34249 | 1.0275 | 0.31807 | 0.5293 | 0.7094 | 747.8671 | 78.0328 | 42.6883
39002.483 | 1920 | 18 | 39002.483 | 1870 | 17 | 2562 | 4262 | 117.2161 | 1.0989 | 114.1636 | 1.0379 | 1.1722 | 0.010989 | 1.1416 | 0.010379 | 1.1612 | 1.1313 | 33.2053 | 36.9286 | 895.0483
39002.4848 | 2286 | 39 | 39002.4848 | 2336 | 44 | 2716 | 4416 | 139.5604 | 2.381 | 142.6129 | 2.6862 | 1.3956 | 0.02381 | 1.4261 | 0.026862 | 1.3718 | 1.3993 | 13.3862 | 10.1553 | 49.7312

## C1-4
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 153.0757 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 4
Time-73 | N11 | N12 | Time-74 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39002.4348 | 1 | 0 | 39002.4348 | 1 | 0 | -1598.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4366 | 1 | 0 | 39002.4366 | 1 | 0 | -1444.5 | 255.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4384 | 1 | 0 | 39002.4384 | 1 | 0 | -1290.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4402 | 1 | 0 | 39002.4402 | 0 | 0 | -1136.5 | 563.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 250638 | 501376 | 250637.9994
39002.442 | 1 | 0 | 39002.442 | 1 | 0 | -982.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4437 | 1 | 0 | 39002.4438 | 1 | 0 | -828.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4455 | 1 | 0 | 39002.4455 | 1 | 0 | -674.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4473 | 1 | 0 | 39002.4473 | 1 | 0 | -520.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4491 | 1 | 0 | 39002.4491 | 1 | 0 | -366.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4509 | 1 | 0 | 39002.4509 | 1 | 0 | -212.5 | 1487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4527 | 1 | 0 | 39002.4527 | 1 | 0 | -58.5 | 1641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4544 | 1 | 0 | 39002.4545 | 1 | 0 | 95.5 | 1795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4562 | 1 | 0 | 39002.4562 | 1 | 0 | 249.5 | 1949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.458 | 1 | 0 | 39002.458 | 1 | 0 | 403.5 | 2103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4598 | 1 | 0 | 39002.4598 | 0 | 0 | 557.5 | 2257.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 250638 | 501376 | 250637.9994
39002.4616 | 1 | 0 | 39002.4616 | 1 | 0 | 711.5 | 2411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4634 | 1 | 0 | 39002.4634 | 1 | 0 | 865.5 | 2565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4651 | 1 | 0 | 39002.4652 | 1 | 0 | 1019.5 | 2719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4669 | 1 | 0 | 39002.4669 | 1 | 0 | 1173.5 | 2873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4687 | 1 | 0 | 39002.4687 | 1 | 0 | 1327.5 | 3027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250638 | 250638 | 250637.9994
39002.4705 | 2180 | 0 | 39002.4705 | 2094 | 0 | 1481.5 | 3181.5 | 133.0891 | 0 | 127.8388 | 0 | 1.3309 | 0 | 1.2784 | 0 | 1.3309 | 1.2784 | 15.0174 | 19.7412 | 13.6865
39002.4723 | 2491 | 0 | 39002.4723 | 2198 | 0 | 1635.5 | 3335.5 | 152.0757 | 0 | 134.188 | 0 | 1.5208 | 0 | 1.3419 | 0 | 1.5208 | 1.3419 | 0.65757 | 14.0755 | 0.86319
39002.474 | 2161 | 0 | 39002.4741 | 2071 | 0 | 1789 | 3489 | 131.9292 | 0 | 126.4347 | 0 | 1.3193 | 0 | 1.2643 | 0 | 1.3193 | 1.2643 | 16.0287 | 21.071 | 14.7094
39002.4758 | 2490 | 0 | 39002.4758 | 1951 | 0 | 1943 | 3643 | 152.0147 | 0 | 119.1087 | 0 | 1.5201 | 0 | 1.1911 | 0 | 1.5201 | 1.1911 | 0.69799 | 28.5177 | 0.82215
39002.4776 | 2455 | 1 | 39002.4776 | 2221 | 0 | 2097 | 3797 | 149.8779 | 0.06105 | 135.5922 | 0 | 1.4988 | 0.0006105 | 1.3559 | 0 | 1.4982 | 1.3559 | 2.1412 | 12.8942 | 586.8358
39002.4794 | 1930 | 6 | 39002.4794 | 2086 | 8 | 2251 | 3951 | 117.8266 | 0.3663 | 127.3504 | 0.4884 | 1.1783 | 0.003663 | 1.2735 | 0.004884 | 1.1746 | 1.2686 | 30.4721 | 20.5376 | 1622.5623
39002.4812 | 1489 | 542 | 39002.4812 | 1690 | 547 | 2405 | 4105 | 90.9035 | 33.0891 | 103.1746 | 33.3944 | 0.90904 | 0.33089 | 1.0317 | 0.33394 | 0.57814 | 0.6978 | 346.7613 | 82.9613 | 39.8539
39002.483 | 2412 | 29 | 39002.483 | 1924 | 20 | 2559 | 4259 | 147.2527 | 1.7705 | 117.4603 | 1.221 | 1.4725 | 0.017705 | 1.1746 | 0.01221 | 1.4548 | 1.1624 | 4.1246 | 41.109 | 66.6839
39002.4847 | 1981 | 36 | 39002.4848 | 1865 | 33 | 2713 | 4413 | 120.9402 | 2.1978 | 113.8584 | 2.0147 | 1.2094 | 0.021978 | 1.1386 | 0.020147 | 1.1874 | 1.1184 | 28.471 | 37.4327 | 371.015

## C1-3
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 149.5958 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 3
Time-71 | N11 | N12 | Time-72 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39002.4348 | 1 | 0 | 39002.4348 | 0 | 0 | -1601 | 99 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 244938 | 489976 | 244937.9994
39002.4366 | 1 | 0 | 39002.4366 | 1 | 0 | -1447 | 253 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4384 | 1 | 0 | 39002.4384 | 1 | 0 | -1293.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4402 | 0 | 0 | 39002.4402 | 1 | 0 | -1139.5 | 560.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 489976 | 244938 | 489975.9997
39002.4419 | 1 | 0 | 39002.4419 | 1 | 0 | -985.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4437 | 1 | 0 | 39002.4437 | 0 | 0 | -831.5 | 868.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 244938 | 489976 | 244937.9994
39002.4455 | 1 | 0 | 39002.4455 | 1 | 0 | -677.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4473 | 1 | 0 | 39002.4473 | 1 | 0 | -523.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4491 | 0 | 0 | 39002.4491 | 1 | 0 | -369.5 | 1330.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 489976 | 244938 | 489975.9997
39002.4508 | 1 | 0 | 39002.4509 | 1 | 0 | -215.5 | 1484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4526 | 1 | 0 | 39002.4526 | 1 | 0 | -61.5 | 1638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4544 | 1 | 0 | 39002.4544 | 1 | 0 | 92.5 | 1792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4562 | 1 | 0 | 39002.4562 | 1 | 0 | 246.5 | 1946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.458 | 1 | 0 | 39002.458 | 1 | 0 | 400.5 | 2100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4598 | 1 | 0 | 39002.4598 | 1 | 0 | 554.5 | 2254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4615 | 1 | 0 | 39002.4616 | 1 | 0 | 708.5 | 2408.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4633 | 1 | 0 | 39002.4633 | 1 | 0 | 862.5 | 2562.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4651 | 1 | 0 | 39002.4651 | 1 | 0 | 1016.5 | 2716.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4669 | 1 | 0 | 39002.4669 | 1 | 0 | 1170.5 | 2870.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4687 | 1 | 0 | 39002.4687 | 1 | 0 | 1324.5 | 3024.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 244938 | 244938 | 244937.9994
39002.4705 | 1931 | 1 | 39002.4705 | 2383 | 1 | 1478.5 | 3178.5 | 117.8877 | 0.06105 | 145.4823 | 0.06105 | 1.1789 | 0.0006105 | 1.4548 | 0.0006105 | 1.1783 | 1.4542 | 27.4122 | 2.8331 | 1428.1387
39002.4722 | 2099 | 0 | 39002.4722 | 2144 | 0 | 1632.5 | 3332.5 | 128.1441 | 0 | 130.8913 | 0 | 1.2814 | 0 | 1.3089 | 0 | 1.2814 | 1.3089 | 16.7404 | 14.2901 | 15.4589
39002.474 | 2418 | 0 | 39002.474 | 2331 | 0 | 1786.5 | 3486.5 | 147.619 | 0 | 142.3077 | 0 | 1.4762 | 0 | 1.4231 | 0 | 1.4762 | 1.4231 | 1.3391 | 5.1214 | 0.13707
39002.4758 | 1997 | 0 | 39002.4758 | 2253 | 0 | 1940.5 | 3640.5 | 121.917 | 0 | 137.5458 | 0 | 1.2192 | 0 | 1.3755 | 0 | 1.2192 | 1.3755 | 22.7031 | 8.7608 | 21.4839
39002.4776 | 2385 | 2 | 39002.4776 | 1976 | 2 | 2094.5 | 3794.5 | 145.6044 | 0.1221 | 120.6349 | 0.1221 | 1.456 | 0.001221 | 1.2063 | 0.001221 | 1.4548 | 1.2051 | 2.7529 | 24.9497 | 632.7787
39002.4794 | 2434 | 6 | 39002.4794 | 2035 | 5 | 2248.5 | 3948.5 | 148.5958 | 0.3663 | 124.2369 | 0.30525 | 1.486 | 0.003663 | 1.2424 | 0.0030525 | 1.4823 | 1.2393 | 0.67987 | 32.0866 | 42.0253
39002.4811 | 1698 | 555 | 39002.4812 | 1704 | 596 | 2402.5 | 4102.5 | 103.663 | 33.8828 | 104.0293 | 36.3858 | 1.0366 | 0.33883 | 1.0403 | 0.36386 | 0.6978 | 0.67643 | 96.8968 | 151.4224 | 21.4189
39002.4829 | 2223 | 31 | 39002.4829 | 1887 | 24 | 2556.5 | 4256.5 | 135.7143 | 1.8926 | 115.2015 | 1.4652 | 1.3571 | 0.018926 | 1.152 | 0.014652 | 1.3382 | 1.1374 | 10.8189 | 34.328 | 161.8892
39002.4847 | 1971 | 44 | 39002.4847 | 1999 | 38 | 2710.5 | 4410.5 | 120.3297 | 2.6862 | 122.0391 | 2.3199 | 1.2033 | 0.026862 | 1.2204 | 0.023199 | 1.1764 | 1.1972 | 27.4031 | 24.7694 | 196.4369

## C1-2
OB Prelim Test 1 |  |  | 2006-10-12 | 10:24 |  | Vs = |  | 147.5201 |  | R = | 100
XLPE | 7-C | Tray A
0 | 250 kW |  | Cable | 1 & 2
Time-69 | N11 | N12 | Time-70 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39002.4348 | 1 | 0 | 39002.4348 | 1 | 0 | -1604 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4366 | 1 | 0 | 39002.4366 | 1 | 0 | -1450 | 250 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4383 | 1 | 0 | 39002.4384 | 1 | 0 | -1296 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4401 | 1 | 0 | 39002.4401 | 1 | 0 | -1142 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4419 | 1 | 0 | 39002.4419 | 1 | 0 | -988 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4437 | 1 | 0 | 39002.4437 | 0 | 0 | -834 | 866 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 241538 | 483176 | 241537.9994
39002.4455 | 1 | 0 | 39002.4455 | 1 | 0 | -680 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4472 | 0 | 0 | 39002.4473 | 0 | 0 | -526 | 1174 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 483176 | 483176 | 483175.9997
39002.449 | 1 | 0 | 39002.4491 | 1 | 0 | -372 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4508 | 1 | 0 | 39002.4508 | 1 | 0 | -218 | 1482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4526 | 1 | 0 | 39002.4526 | 1 | 0 | -64.5 | 1635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4544 | 1 | 0 | 39002.4544 | 1 | 0 | 89.5 | 1789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4562 | 1 | 0 | 39002.4562 | 1 | 0 | 243.5 | 1943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4579 | 1 | 0 | 39002.458 | 1 | 0 | 398 | 2098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4597 | 1 | 0 | 39002.4597 | 1 | 0 | 551.5 | 2251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4615 | 1 | 0 | 39002.4615 | 1 | 0 | 705.5 | 2405.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4633 | 1 | 0 | 39002.4633 | 1 | 0 | 859.5 | 2559.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4651 | 1 | 0 | 39002.4651 | 1 | 0 | 1013.5 | 2713.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4669 | 1 | 0 | 39002.4669 | 1 | 0 | 1167.5 | 2867.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4686 | 1 | 0 | 39002.4686 | 1 | 0 | 1321.5 | 3021.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 241538 | 241538 | 241537.9994
39002.4704 | 2035 | 0 | 39002.4704 | 2071 | 0 | 1475.5 | 3175.5 | 124.2369 | 0 | 126.4347 | 0 | 1.2424 | 0 | 1.2643 | 0 | 1.2424 | 1.2643 | 18.741 | 16.677 | 17.4987
39002.4722 | 2366 | 0 | 39002.4722 | 2125 | 0 | 1629.5 | 3329.5 | 144.4444 | 0 | 129.7314 | 0 | 1.4444 | 0 | 1.2973 | 0 | 1.4444 | 1.2973 | 2.1293 | 13.712 | 0.68489
39002.474 | 2257 | 0 | 39002.474 | 2177 | 1 | 1783.5 | 3483.5 | 137.79 | 0 | 132.906 | 0.06105 | 1.3779 | 0 | 1.3291 | 0.0006105 | 1.3779 | 1.3284 | 7.0616 | 11.0469 | 5.6837
39002.4758 | 2292 | 0 | 39002.4758 | 1936 | 0 | 1937.5 | 3637.5 | 139.9267 | 0 | 118.1929 | 0 | 1.3993 | 0 | 1.1819 | 0 | 1.3993 | 1.1819 | 5.4267 | 24.813 | 4.0274
39002.4775 | 2129 | 3 | 39002.4776 | 2400 | 3 | 2091.5 | 3791.5 | 129.9756 | 0.18315 | 146.5201 | 0.18315 | 1.2998 | 0.0018315 | 1.4652 | 0.0018315 | 1.2979 | 1.4634 | 17.0025 | 0.68842 | 64.8116
39002.4793 | 2267 | 6 | 39002.4793 | 1943 | 5 | 2245.5 | 3945.5 | 138.4005 | 0.3663 | 118.6203 | 0.30525 | 1.384 | 0.003663 | 1.1862 | 0.0030525 | 1.3803 | 1.1832 | 6.6765 | 25.408 | 484.1536
39002.4811 | 2302 | 20 | 39002.4811 | 2043 | 21 | 2399.5 | 4099.5 | 140.5372 | 1.221 | 124.7253 | 1.2821 | 1.4054 | 0.01221 | 1.2473 | 0.012821 | 1.3932 | 1.2344 | 5.2103 | 23.0631 | 88.4382
39002.4829 | 2083 | 36 | 39002.4829 | 2332 | 36 | 2553.5 | 4253.5 | 127.1673 | 2.1978 | 142.3687 | 2.1978 | 1.2717 | 0.021978 | 1.4237 | 0.021978 | 1.2497 | 1.4017 | 29.7931 | 3.8792 | 30.848
39002.4847 | 1860 | 55 | 39002.4847 | 1865 | 44 | 2707.5 | 4407.5 | 113.5531 | 3.3578 | 113.8584 | 2.6862 | 1.1355 | 0.033578 | 1.1386 | 0.026862 | 1.102 | 1.1117 | 34.0031 | 32.5952 | 224.0938

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | OB Prelim Test 1 |  |  | 2006-10-12 | 10:24
39002.4337 | 1 | 0 | 1 | XLPE | 7-C | Tray A | IRMS | 1
39002.4355 | 1 | 0 | 1 |  | 250 kW |  | Cable
39002.4372 | 1 | 0 | 1
39002.439 | 1 | 0 | 1
39002.4408 | 1 | 0 | 1
39002.4426 | 1 | 0 | 1
39002.4444 | 1 | 0 | 1
39002.4461 | 1 | 0 | 1
39002.4479 | 1 | 0 | 1
39002.4497 | 0 | 0 | 1
39002.4515 | 0 | 0 | 1
39002.4533 | 1 | 0 | 1
39002.4551 | 1 | 0 | 1
39002.4568 | 1 | 0 | 1
39002.4586 | 1 | 0 | 1
39002.4604 | 1 | 0 | 1
39002.4622 | 1 | 0 | 1
39002.464 | 1 | 0 | 1
39002.4658 | 1 | 0 | 1
39002.4675 | 1 | 0 | 1
39002.4693 | 1 | 0 | 1
39002.4711 | 1947 | 0 | 1
39002.4729 | 2249 | 0 | 1
39002.4747 | 2580 | 0 | 1
39002.4764 | 2452 | 0 | 1
39002.4782 | 2055 | 0 | 1
39002.48 | 1798 | 471 | 1
39002.4818 | 1825 | 95 | 1
39002.4836 | 1823 | 395 | 1
1
39002.4337 | 1 | 0 | 2
39002.4355 | 1 | 0 | 2
39002.4373 | 1 | 0 | 2
39002.439 | 1 | 0 | 2
39002.4408 | 0 | 0 | 2
39002.4426 | 1 | 0 | 2
39002.4444 | 1 | 0 | 2
39002.4462 | 1 | 0 | 2
39002.4479 | 1 | 0 | 2
39002.4497 | 1 | 0 | 2
39002.4515 | 1 | 0 | 2
39002.4533 | 1 | 0 | 2
39002.4551 | 1 | 0 | 2
39002.4569 | 1 | 0 | 2
39002.4586 | 0 | 0 | 2
39002.4604 | 1 | 0 | 2
39002.4622 | 1 | 0 | 2
39002.464 | 1 | 0 | 2
39002.4658 | 1 | 0 | 2
39002.4675 | 1 | 0 | 2
39002.4693 | 49 | 38 | 2
39002.4711 | 1984 | 0 | 2
39002.4729 | 2542 | 0 | 2
39002.4747 | 2117 | 0 | 2
39002.4765 | 2132 | 0 | 2
39002.4782 | 2328 | 0 | 2
39002.48 | 1433 | 860 | 2
39002.4818 | 1969 | 93 | 2
39002.4836 | 1762 | 685 | 2
2
39002.4337 | 1 | 0 | 3
39002.4355 | 1 | 0 | 3
39002.4373 | 1 | 0 | 3
39002.4391 | 1 | 0 | 3
39002.4408 | 1 | 0 | 3
39002.4426 | 1 | 0 | 3
39002.4444 | 1 | 0 | 3
39002.4462 | 0 | 0 | 3
39002.448 | 0 | 0 | 3
39002.4497 | 0 | 0 | 3
39002.4515 | 1 | 0 | 3
39002.4533 | 1 | 0 | 3
39002.4551 | 0 | 0 | 3
39002.4569 | 1 | 0 | 3
39002.4587 | 1 | 0 | 3
39002.4604 | 1 | 0 | 3
39002.4622 | 1 | 0 | 3
39002.464 | 1 | 0 | 3
39002.4658 | 1 | 0 | 3
39002.4676 | 1 | 0 | 3
39002.4694 | 11 | 0 | 3
39002.4711 | 2374 | 0 | 3
39002.4729 | 2143 | 0 | 3
39002.4747 | 2184 | 0 | 3
39002.4765 | 2135 | 0 | 3
39002.4783 | 2188 | 0 | 3
39002.48 | 1457 | 762 | 3
39002.4818 | 2200 | 93 | 3
39002.4836 | 1239 | 646 | 3
3
39002.4337 | 1 | 0 | 4
39002.4355 | 1 | 0 | 4
39002.4373 | 1 | 0 | 4
39002.4391 | 1 | 0 | 4
39002.4408 | 0 | 0 | 4
39002.4426 | 1 | 0 | 4
39002.4444 | 1 | 0 | 4
39002.4462 | 0 | 0 | 4
39002.448 | 1 | 0 | 4
39002.4498 | 1 | 0 | 4
39002.4515 | 0 | 0 | 4
39002.4533 | 1 | 0 | 4
39002.4551 | 1 | 0 | 4
39002.4569 | 1 | 0 | 4
39002.4587 | 0 | 0 | 4
39002.4605 | 1 | 0 | 4
39002.4622 | 1 | 0 | 4
39002.464 | 1 | 0 | 4
39002.4658 | 1 | 0 | 4
39002.4676 | 1 | 0 | 4
39002.4694 | 1 | 0 | 4
39002.4711 | 2353 | 0 | 4
39002.4729 | 2247 | 0 | 4
39002.4747 | 2077 | 0 | 4
39002.4765 | 2038 | 0 | 4
39002.4783 | 2513 | 0 | 4
39002.4801 | 1432 | 639 | 4
39002.4818 | 2272 | 82 | 4
39002.4836 | 1415 | 712 | 4
4
39002.4337 | 1 | 0 | 5
39002.4355 | 1 | 0 | 5
39002.4373 | 1 | 0 | 5
39002.4391 | 1 | 0 | 5
39002.4409 | 0 | 0 | 5
39002.4427 | 1 | 0 | 5
39002.4444 | 1 | 0 | 5
39002.4462 | 1 | 0 | 5
39002.448 | 1 | 0 | 5
39002.4498 | 0 | 0 | 5
39002.4516 | 1 | 0 | 5
39002.4533 | 1 | 0 | 5
39002.4551 | 1 | 0 | 5
39002.4569 | 1 | 0 | 5
39002.4587 | 1 | 0 | 5
39002.4605 | 1 | 0 | 5
39002.4622 | 1 | 0 | 5
39002.464 | 1 | 0 | 5
39002.4658 | 1 | 0 | 5
39002.4676 | 1 | 0 | 5
39002.4694 | 166 | 163 | 5
39002.4712 | 2192 | 0 | 5
39002.4729 | 2409 | 0 | 5
39002.4747 | 2316 | 0 | 5
39002.4765 | 2592 | 0 | 5
39002.4783 | 2005 | 0 | 5
39002.4801 | 1416 | 510 | 5
39002.4819 | 1857 | 60 | 5
39002.4836 | 1613 | 323 | 5
5
39002.4337 | 1 | 0 | 6
39002.4355 | 1 | 0 | 6
39002.4373 | 1 | 0 | 6
39002.4391 | 1 | 0 | 6
39002.4409 | 0 | 0 | 6
39002.4427 | 1 | 0 | 6
39002.4444 | 0 | 0 | 6
39002.4462 | 1 | 0 | 6
39002.448 | 1 | 0 | 6
39002.4498 | 1 | 0 | 6
39002.4516 | 0 | 0 | 6
39002.4534 | 1 | 0 | 6
39002.4551 | 1 | 0 | 6
39002.4569 | 1 | 0 | 6
39002.4587 | 1 | 0 | 6
39002.4605 | 1 | 0 | 6
39002.4623 | 1 | 0 | 6
39002.4641 | 1 | 0 | 6
39002.4658 | 1 | 0 | 6
39002.4676 | 1 | 0 | 6
39002.4694 | 308 | 177 | 6
39002.4712 | 2007 | 0 | 6
39002.473 | 2257 | 0 | 6
39002.4747 | 2576 | 0 | 6
39002.4765 | 2506 | 0 | 6
39002.4783 | 2506 | 0 | 6
39002.4801 | 1548 | 457 | 6
39002.4819 | 2212 | 65 | 6
39002.4837 | 1460 | 547 | 6
6
39002.4338 | 1 | 0 | 7
39002.4356 | 1 | 0 | 7
39002.4373 | 1 | 0 | 7
39002.4391 | 1 | 0 | 7
39002.4409 | 1 | 0 | 7
39002.4427 | 1 | 0 | 7
39002.4445 | 1 | 0 | 7
39002.4462 | 1 | 0 | 7
39002.448 | 1 | 0 | 7
39002.4498 | 1 | 0 | 7
39002.4516 | 1 | 0 | 7
39002.4534 | 1 | 0 | 7
39002.4552 | 1 | 0 | 7
39002.4569 | 1 | 0 | 7
39002.4587 | 1 | 0 | 7
39002.4605 | 1 | 0 | 7
39002.4623 | 1 | 0 | 7
39002.4641 | 1 | 0 | 7
39002.4658 | 1 | 0 | 7
39002.4676 | 1 | 0 | 7
39002.4694 | 238 | 0 | 7
39002.4712 | 2011 | 0 | 7
39002.473 | 2062 | 0 | 7
39002.4748 | 2113 | 0 | 7
39002.4765 | 2131 | 0 | 7
39002.4783 | 2494 | 0 | 7
39002.4801 | 1750 | 0 | 7
39002.4819 | 2028 | 0 | 7
39002.4837 | 1553 | 0 | 7
7
39002.4338 | 1 | 0 | 8
39002.4356 | 1 | 0 | 8
39002.4373 | 1 | 0 | 8
39002.4391 | 1 | 0 | 8
39002.4409 | 1 | 0 | 8
39002.4427 | 1 | 0 | 8
39002.4445 | 0 | 0 | 8
39002.4463 | 1 | 0 | 8
39002.448 | 1 | 0 | 8
39002.4498 | 1 | 0 | 8
39002.4516 | 1 | 0 | 8
39002.4534 | 0 | 0 | 8
39002.4552 | 1 | 0 | 8
39002.457 | 1 | 0 | 8
39002.4587 | 1 | 0 | 8
39002.4605 | 1 | 0 | 8
39002.4623 | 1 | 0 | 8
39002.4641 | 1 | 0 | 8
39002.4659 | 1 | 0 | 8
39002.4677 | 1 | 0 | 8
39002.4694 | 1 | 0 | 8
39002.4712 | 2308 | 0 | 8
39002.473 | 2320 | 0 | 8
39002.4748 | 1957 | 0 | 8
39002.4766 | 2315 | 0 | 8
39002.4783 | 2033 | 0 | 8
39002.4801 | 2109 | 0 | 8
39002.4819 | 1776 | 0 | 8
39002.4837 | 2052 | 0 | 8
8
39002.4338 | 1 | 0 | 9
39002.4356 | 1 | 0 | 9
39002.4374 | 1 | 0 | 9
39002.4391 | 1 | 0 | 9
39002.4409 | 1 | 0 | 9
39002.4427 | 1 | 0 | 9
39002.4445 | 1 | 0 | 9
39002.4463 | 1 | 0 | 9
39002.4481 | 1 | 0 | 9
39002.4498 | 1 | 0 | 9
39002.4516 | 1 | 0 | 9
39002.4534 | 1 | 0 | 9
39002.4552 | 1 | 0 | 9
39002.457 | 0 | 0 | 9
39002.4587 | 1 | 0 | 9
39002.4605 | 1 | 0 | 9
39002.4623 | 1 | 0 | 9
39002.4641 | 1 | 0 | 9
39002.4659 | 1 | 0 | 9
39002.4677 | 1 | 0 | 9
39002.4694 | 878 | 0 | 9
39002.4712 | 2283 | 0 | 9
39002.473 | 2569 | 0 | 9
39002.4748 | 2578 | 0 | 9
39002.4766 | 2023 | 0 | 9
39002.4784 | 2281 | 0 | 9
39002.4801 | 1864 | 0 | 9
39002.4819 | 2039 | 0 | 9
39002.4837 | 1935 | 0 | 9
9
39002.4338 | 1 | 0 | 10
39002.4356 | 1 | 0 | 10
39002.4374 | 0 | 0 | 10
39002.4392 | 1 | 0 | 10
39002.4409 | 0 | 0 | 10
39002.4427 | 1 | 0 | 10
39002.4445 | 1 | 0 | 10
39002.4463 | 1 | 0 | 10
39002.4481 | 1 | 0 | 10
39002.4499 | 1 | 0 | 10
39002.4516 | 1 | 0 | 10
39002.4534 | 1 | 0 | 10
39002.4552 | 1 | 0 | 10
39002.457 | 1 | 0 | 10
39002.4588 | 1 | 0 | 10
39002.4605 | 1 | 0 | 10
39002.4623 | 1 | 0 | 10
39002.4641 | 1 | 0 | 10
39002.4659 | 0 | 0 | 10
39002.4677 | 1 | 0 | 10
39002.4695 | 1 | 0 | 10
39002.4712 | 2194 | 0 | 10
39002.473 | 2349 | 0 | 10
39002.4748 | 1941 | 0 | 10
39002.4766 | 1994 | 0 | 10
39002.4784 | 2118 | 0 | 10
39002.4802 | 2109 | 0 | 10
39002.4819 | 1354 | 0 | 10
39002.4837 | 2190 | 0 | 10
10
39002.4338 | 1 | 0 | 11
39002.4356 | 1 | 0 | 11
39002.4374 | 1 | 0 | 11
39002.4392 | 1 | 0 | 11
39002.441 | 1 | 0 | 11
39002.4427 | 1 | 0 | 11
39002.4445 | 1 | 0 | 11
39002.4463 | 1 | 0 | 11
39002.4481 | 1 | 0 | 11
39002.4499 | 1 | 0 | 11
39002.4517 | 1 | 0 | 11
39002.4534 | 1 | 0 | 11
39002.4552 | 0 | 0 | 11
39002.457 | 0 | 0 | 11
39002.4588 | 1 | 0 | 11
39002.4606 | 1 | 0 | 11
39002.4623 | 1 | 0 | 11
39002.4641 | 1 | 0 | 11
39002.4659 | 1 | 0 | 11
39002.4677 | 1 | 0 | 11
39002.4695 | 1330 | 0 | 11
39002.4713 | 2397 | 0 | 11
39002.473 | 2268 | 0 | 11
39002.4748 | 2584 | 0 | 11
39002.4766 | 2326 | 0 | 11
39002.4784 | 2181 | 0 | 11
39002.4802 | 1845 | 0 | 11
39002.482 | 1835 | 0 | 11
39002.4837 | 1890 | 0 | 11
11
39002.4339 | 1 | 0 | 12
39002.4356 | 1 | 0 | 12
39002.4374 | 1 | 0 | 12
39002.4392 | 1 | 0 | 12
39002.441 | 1 | 0 | 12
39002.4428 | 1 | 0 | 12
39002.4445 | 1 | 0 | 12
39002.4463 | 1 | 0 | 12
39002.4481 | 1 | 0 | 12
39002.4499 | 1 | 0 | 12
39002.4517 | 1 | 0 | 12
39002.4534 | 1 | 0 | 12
39002.4552 | 1 | 0 | 12
39002.457 | 1 | 0 | 12
39002.4588 | 1 | 0 | 12
39002.4606 | 1 | 0 | 12
39002.4624 | 1 | 0 | 12
39002.4641 | 1 | 0 | 12
39002.4659 | 1 | 0 | 12
39002.4677 | 1 | 0 | 12
39002.4695 | 1 | 0 | 12
39002.4713 | 2274 | 0 | 12
39002.4731 | 2491 | 0 | 12
39002.4748 | 2031 | 0 | 12
39002.4766 | 2037 | 0 | 12
39002.4784 | 1996 | 0 | 12
39002.4802 | 1981 | 0 | 12
39002.482 | 1577 | 0 | 12
39002.4837 | 2217 | 0 | 12
12
39002.4339 | 1 | 0 | 13
39002.4356 | 1 | 0 | 13
39002.4374 | 1 | 0 | 13
39002.4392 | 1 | 0 | 13
39002.441 | 1 | 0 | 13
39002.4428 | 1 | 0 | 13
39002.4446 | 1 | 0 | 13
39002.4463 | 1 | 0 | 13
39002.4481 | 1 | 0 | 13
39002.4499 | 0 | 0 | 13
39002.4517 | 1 | 0 | 13
39002.4535 | 1 | 0 | 13
39002.4553 | 1 | 0 | 13
39002.457 | 1 | 0 | 13
39002.4588 | 1 | 0 | 13
39002.4606 | 1 | 0 | 13
39002.4624 | 1 | 0 | 13
39002.4642 | 1 | 0 | 13
39002.4659 | 1 | 0 | 13
39002.4677 | 1 | 0 | 13
39002.4695 | 169 | 0 | 13
39002.4713 | 2108 | 0 | 13
39002.4731 | 2359 | 0 | 13
39002.4748 | 2005 | 0 | 13
39002.4766 | 2118 | 0 | 13
39002.4784 | 2582 | 0 | 13
39002.4802 | 2011 | 0 | 13
39002.482 | 2103 | 0 | 13
39002.4838 | 2093 | 0 | 13
13
39002.4339 | 1 | 0 | 14
39002.4357 | 1 | 0 | 14
39002.4374 | 1 | 0 | 14
39002.4392 | 1 | 0 | 14
39002.441 | 1 | 0 | 14
39002.4428 | 1 | 0 | 14
39002.4446 | 1 | 0 | 14
39002.4464 | 1 | 0 | 14
39002.4481 | 1 | 0 | 14
39002.4499 | 1 | 0 | 14
39002.4517 | 0 | 0 | 14
39002.4535 | 1 | 0 | 14
39002.4553 | 1 | 0 | 14
39002.457 | 1 | 0 | 14
39002.4588 | 1 | 0 | 14
39002.4606 | 1 | 0 | 14
39002.4624 | 1 | 0 | 14
39002.4642 | 1 | 0 | 14
39002.466 | 0 | 0 | 14
39002.4677 | 1 | 0 | 14
39002.4695 | 1 | 0 | 14
39002.4713 | 1978 | 0 | 14
39002.4731 | 2469 | 0 | 14
39002.4749 | 2126 | 0 | 14
39002.4767 | 2129 | 0 | 14
39002.4784 | 2368 | 0 | 14
39002.4802 | 1924 | 0 | 14
39002.482 | 1929 | 0 | 14
39002.4838 | 2046 | 0 | 14
14
39002.4339 | 1 | 0 | 15
39002.4357 | 1 | 0 | 15
39002.4375 | 1 | 0 | 15
39002.4392 | 1 | 0 | 15
39002.441 | 1 | 0 | 15
39002.4428 | 1 | 0 | 15
39002.4446 | 1 | 0 | 15
39002.4464 | 1 | 0 | 15
39002.4482 | 1 | 0 | 15
39002.4499 | 1 | 0 | 15
39002.4517 | 1 | 0 | 15
39002.4535 | 1 | 0 | 15
39002.4553 | 0 | 0 | 15
39002.4571 | 1 | 0 | 15
39002.4588 | 1 | 0 | 15
39002.4606 | 1 | 0 | 15
39002.4624 | 1 | 0 | 15
39002.4642 | 1 | 0 | 15
39002.466 | 1 | 0 | 15
39002.4678 | 1 | 0 | 15
39002.4695 | 1423 | 0 | 15
39002.4713 | 2195 | 0 | 15
39002.4731 | 2299 | 0 | 15
39002.4749 | 2555 | 0 | 15
39002.4767 | 2589 | 0 | 15
39002.4784 | 2282 | 0 | 15
39002.4802 | 1846 | 0 | 15
39002.482 | 1833 | 0 | 15
39002.4838 | 1457 | 0 | 15
15
39002.4339 | 1 | 0 | 16
39002.4357 | 1 | 0 | 16
39002.4375 | 1 | 0 | 16
39002.4393 | 1 | 0 | 16
39002.441 | 1 | 0 | 16
39002.4428 | 1 | 0 | 16
39002.4446 | 1 | 0 | 16
39002.4464 | 1 | 0 | 16
39002.4482 | 1 | 0 | 16
39002.45 | 1 | 0 | 16
39002.4517 | 1 | 0 | 16
39002.4535 | 1 | 0 | 16
39002.4553 | 1 | 0 | 16
39002.4571 | 1 | 0 | 16
39002.4589 | 1 | 0 | 16
39002.4606 | 1 | 0 | 16
39002.4624 | 1 | 0 | 16
39002.4642 | 1 | 0 | 16
39002.466 | 1 | 0 | 16
39002.4678 | 1 | 0 | 16
39002.4696 | 6 | 0 | 16
39002.4713 | 2201 | 0 | 16
39002.4731 | 2225 | 0 | 16
39002.4749 | 2303 | 0 | 16
39002.4767 | 2125 | 0 | 16
39002.4785 | 2379 | 0 | 16
39002.4803 | 2442 | 0 | 16
39002.482 | 1612 | 0 | 16
39002.4838 | 2255 | 0 | 16
16
39002.4339 | 1 | 0 | 17
39002.4357 | 1 | 0 | 17
39002.4375 | 1 | 0 | 17
39002.4393 | 1 | 0 | 17
39002.4411 | 1 | 0 | 17
39002.4428 | 1 | 0 | 17
39002.4446 | 1 | 0 | 17
39002.4464 | 1 | 0 | 17
39002.4482 | 0 | 0 | 17
39002.45 | 1 | 0 | 17
39002.4517 | 1 | 0 | 17
39002.4535 | 1 | 0 | 17
39002.4553 | 1 | 0 | 17
39002.4571 | 0 | 0 | 17
39002.4589 | 1 | 0 | 17
39002.4607 | 1 | 0 | 17
39002.4624 | 1 | 0 | 17
39002.4642 | 1 | 0 | 17
39002.466 | 1 | 0 | 17
39002.4678 | 1 | 0 | 17
39002.4696 | 1927 | 0 | 17
39002.4714 | 2219 | 0 | 17
39002.4731 | 2529 | 0 | 17
39002.4749 | 2578 | 0 | 17
39002.4767 | 2588 | 0 | 17
39002.4785 | 2283 | 0 | 17
39002.4803 | 1666 | 0 | 17
39002.482 | 1813 | 0 | 17
39002.4838 | 1966 | 0 | 17
17
39002.4339 | 1 | 0 | 18
39002.4357 | 1 | 0 | 18
39002.4375 | 1 | 0 | 18
39002.4393 | 1 | 0 | 18
39002.4411 | 1 | 0 | 18
39002.4429 | 1 | 0 | 18
39002.4446 | 1 | 0 | 18
39002.4464 | 1 | 0 | 18
39002.4482 | 1 | 0 | 18
39002.45 | 1 | 0 | 18
39002.4518 | 1 | 0 | 18
39002.4536 | 1 | 0 | 18
39002.4553 | 1 | 0 | 18
39002.4571 | 0 | 0 | 18
39002.4589 | 1 | 0 | 18
39002.4607 | 1 | 0 | 18
39002.4625 | 1 | 0 | 18
39002.4642 | 1 | 0 | 18
39002.466 | 1 | 0 | 18
39002.4678 | 1 | 0 | 18
39002.4696 | 7 | 0 | 18
39002.4714 | 2145 | 0 | 18
39002.4732 | 1970 | 0 | 18
39002.4749 | 1892 | 0 | 18
39002.4767 | 1916 | 0 | 18
39002.4785 | 2104 | 0 | 18
39002.4803 | 2440 | 0 | 18
39002.4821 | 2049 | 0 | 18
39002.4838 | 2387 | 0 | 18
18
39002.434 | 1 | 0 | 19
39002.4357 | 1 | 0 | 19
39002.4375 | 1 | 0 | 19
39002.4393 | 1 | 0 | 19
39002.4411 | 1 | 0 | 19
39002.4429 | 1 | 0 | 19
39002.4447 | 1 | 0 | 19
39002.4464 | 1 | 0 | 19
39002.4482 | 1 | 0 | 19
39002.45 | 1 | 0 | 19
39002.4518 | 0 | 0 | 19
39002.4536 | 1 | 0 | 19
39002.4553 | 1 | 0 | 19
39002.4571 | 1 | 0 | 19
39002.4589 | 1 | 0 | 19
39002.4607 | 1 | 0 | 19
39002.4625 | 1 | 0 | 19
39002.4643 | 1 | 0 | 19
39002.466 | 1 | 0 | 19
39002.4678 | 1 | 0 | 19
39002.4696 | 2336 | 0 | 19
39002.4714 | 2501 | 0 | 19
39002.4732 | 2582 | 0 | 19
39002.475 | 2507 | 0 | 19
39002.4767 | 2583 | 0 | 19
39002.4785 | 2288 | 0 | 19
39002.4803 | 2004 | 0 | 19
39002.4821 | 1886 | 0 | 19
39002.4839 | 1370 | 0 | 19
19
39002.434 | 1 | 0 | 20
39002.4358 | 1 | 0 | 20
39002.4375 | 1 | 0 | 20
39002.4393 | 1 | 0 | 20
39002.4411 | 1 | 0 | 20
39002.4429 | 1 | 0 | 20
39002.4447 | 0 | 0 | 20
39002.4465 | 1 | 0 | 20
39002.4482 | 1 | 0 | 20
39002.45 | 1 | 0 | 20
39002.4518 | 1 | 0 | 20
39002.4536 | 1 | 0 | 20
39002.4554 | 1 | 0 | 20
39002.4572 | 1 | 0 | 20
39002.4589 | 1 | 0 | 20
39002.4607 | 1 | 0 | 20
39002.4625 | 1 | 0 | 20
39002.4643 | 1 | 0 | 20
39002.4661 | 1 | 0 | 20
39002.4678 | 1 | 0 | 20
39002.4696 | 3 | 0 | 20
39002.4714 | 2346 | 0 | 20
39002.4732 | 1977 | 0 | 20
39002.475 | 1972 | 0 | 20
39002.4767 | 1926 | 0 | 20
39002.4785 | 2422 | 0 | 20
39002.4803 | 2169 | 0 | 20
39002.4821 | 1765 | 0 | 20
39002.4839 | 1982 | 0 | 20
20
39002.434 | 1 | 0 | 21
39002.4358 | 1 | 0 | 21
39002.4376 | 1 | 0 | 21
39002.4393 | 1 | 0 | 21
39002.4411 | 1 | 0 | 21
39002.4429 | 1 | 0 | 21
39002.4447 | 1 | 0 | 21
39002.4465 | 1 | 0 | 21
39002.4483 | 1 | 0 | 21
39002.45 | 1 | 0 | 21
39002.4518 | 0 | 0 | 21
39002.4536 | 1 | 0 | 21
39002.4554 | 1 | 0 | 21
39002.4572 | 0 | 0 | 21
39002.4589 | 1 | 0 | 21
39002.4607 | 1 | 0 | 21
39002.4625 | 1 | 0 | 21
39002.4643 | 1 | 0 | 21
39002.4661 | 1 | 0 | 21
39002.4679 | 1 | 0 | 21
39002.4696 | 1076 | 0 | 21
39002.4714 | 2165 | 0 | 21
39002.4732 | 2562 | 0 | 21
39002.475 | 2240 | 0 | 21
39002.4768 | 2106 | 0 | 21
39002.4786 | 2055 | 0 | 21
39002.4803 | 1927 | 156 | 21
39002.4821 | 2132 | 60 | 21
39002.4839 | 1125 | 857 | 21
21
39002.434 | 1 | 0 | 22
39002.4358 | 1 | 0 | 22
39002.4376 | 1 | 0 | 22
39002.4394 | 1 | 0 | 22
39002.4411 | 1 | 0 | 22
39002.4429 | 1 | 0 | 22
39002.4447 | 1 | 0 | 22
39002.4465 | 1 | 0 | 22
39002.4483 | 1 | 0 | 22
39002.45 | 1 | 0 | 22
39002.4518 | 1 | 0 | 22
39002.4536 | 1 | 0 | 22
39002.4554 | 1 | 0 | 22
39002.4572 | 1 | 0 | 22
39002.459 | 1 | 0 | 22
39002.4607 | 1 | 0 | 22
39002.4625 | 1 | 0 | 22
39002.4643 | 1 | 0 | 22
39002.4661 | 1 | 0 | 22
39002.4679 | 1 | 0 | 22
39002.4697 | 1 | 0 | 22
39002.4714 | 2408 | 0 | 22
39002.4732 | 2426 | 0 | 22
39002.475 | 2448 | 0 | 22
39002.4768 | 2293 | 0 | 22
39002.4786 | 2136 | 0 | 22
39002.4803 | 2259 | 158 | 22
39002.4821 | 2367 | 50 | 22
39002.4839 | 1207 | 1088 | 22
22
39002.434 | 1 | 0 | 23
39002.4358 | 1 | 0 | 23
39002.4376 | 1 | 0 | 23
39002.4394 | 1 | 0 | 23
39002.4412 | 1 | 0 | 23
39002.4429 | 1 | 0 | 23
39002.4447 | 1 | 0 | 23
39002.4465 | 1 | 0 | 23
39002.4483 | 0 | 0 | 23
39002.4501 | 1 | 0 | 23
39002.4519 | 1 | 0 | 23
39002.4536 | 1 | 0 | 23
39002.4554 | 1 | 0 | 23
39002.4572 | 1 | 0 | 23
39002.459 | 1 | 0 | 23
39002.4608 | 1 | 0 | 23
39002.4625 | 1 | 0 | 23
39002.4643 | 1 | 0 | 23
39002.4661 | 1 | 0 | 23
39002.4679 | 1 | 0 | 23
39002.4697 | 1873 | 0 | 23
39002.4715 | 1964 | 0 | 23
39002.4732 | 2212 | 0 | 23
39002.475 | 2161 | 0 | 23
39002.4768 | 2572 | 0 | 23
39002.4786 | 2162 | 0 | 23
39002.4804 | 2133 | 135 | 23
39002.4821 | 1934 | 54 | 23
39002.4839 | 1194 | 1170 | 23
23
39002.434 | 1 | 0 | 24
39002.4358 | 0 | 0 | 24
39002.4376 | 1 | 0 | 24
39002.4394 | 1 | 0 | 24
39002.4412 | 1 | 0 | 24
39002.443 | 0 | 0 | 24
39002.4447 | 1 | 0 | 24
39002.4465 | 1 | 0 | 24
39002.4483 | 0 | 0 | 24
39002.4501 | 1 | 0 | 24
39002.4519 | 1 | 0 | 24
39002.4536 | 1 | 0 | 24
39002.4554 | 1 | 0 | 24
39002.4572 | 1 | 0 | 24
39002.459 | 1 | 0 | 24
39002.4608 | 1 | 0 | 24
39002.4626 | 1 | 0 | 24
39002.4643 | 0 | 0 | 24
39002.4661 | 1 | 0 | 24
39002.4679 | 1 | 0 | 24
39002.4697 | 2213 | 0 | 24
39002.4715 | 2138 | 0 | 24
39002.4733 | 2217 | 0 | 24
39002.475 | 2108 | 0 | 24
39002.4768 | 2112 | 0 | 24
39002.4786 | 2217 | 0 | 24
39002.4804 | 2217 | 129 | 24
39002.4822 | 2260 | 48 | 24
39002.4839 | 1155 | 1079 | 24
24
39002.4341 | 1 | 0 | 25
39002.4358 | 1 | 0 | 25
39002.4376 | 0 | 0 | 25
39002.4394 | 1 | 0 | 25
39002.4412 | 1 | 0 | 25
39002.443 | 1 | 0 | 25
39002.4448 | 1 | 0 | 25
39002.4465 | 1 | 0 | 25
39002.4483 | 1 | 0 | 25
39002.4501 | 0 | 0 | 25
39002.4519 | 1 | 0 | 25
39002.4537 | 1 | 0 | 25
39002.4554 | 0 | 0 | 25
39002.4572 | 1 | 0 | 25
39002.459 | 1 | 0 | 25
39002.4608 | 1 | 0 | 25
39002.4626 | 0 | 0 | 25
39002.4644 | 1 | 0 | 25
39002.4661 | 0 | 0 | 25
39002.4679 | 1 | 0 | 25
39002.4697 | 1934 | 0 | 25
39002.4715 | 2130 | 0 | 25
39002.4733 | 2364 | 0 | 25
39002.475 | 2075 | 0 | 25
39002.4768 | 2213 | 0 | 25
39002.4786 | 2576 | 0 | 25
39002.4822 | 2320 | 0 | 25
39002.484 | 1203 | 0 | 25
25
39002.4341 | 1 | 0 | 26
39002.4359 | 1 | 0 | 26
39002.4376 | 1 | 0 | 26
39002.4394 | 1 | 0 | 26
39002.4412 | 1 | 0 | 26
39002.443 | 1 | 0 | 26
39002.4448 | 1 | 0 | 26
39002.4466 | 1 | 0 | 26
39002.4483 | 1 | 0 | 26
39002.4501 | 1 | 0 | 26
39002.4519 | 1 | 0 | 26
39002.4537 | 1 | 0 | 26
39002.4555 | 1 | 0 | 26
39002.4572 | 1 | 0 | 26
39002.459 | 1 | 0 | 26
39002.4608 | 1 | 0 | 26
39002.4626 | 1 | 0 | 26
39002.4644 | 1 | 0 | 26
39002.4662 | 1 | 0 | 26
39002.4679 | 1 | 0 | 26
39002.4697 | 15 | 0 | 26
39002.4715 | 2232 | 0 | 26
39002.4733 | 2118 | 0 | 26
39002.4751 | 2060 | 0 | 26
39002.4769 | 2426 | 0 | 26
39002.4786 | 1910 | 0 | 26
39002.4804 | 2467 | 0 | 26
39002.4822 | 1402 | 0 | 26
39002.484 | 1882 | 0 | 26
26
39002.4341 | 1 | 0 | 27
39002.4359 | 1 | 0 | 27
39002.4377 | 1 | 0 | 27
39002.4394 | 0 | 0 | 27
39002.4412 | 1 | 0 | 27
39002.443 | 1 | 0 | 27
39002.4448 | 1 | 0 | 27
39002.4466 | 1 | 0 | 27
39002.4483 | 1 | 0 | 27
39002.4501 | 1 | 0 | 27
39002.4519 | 1 | 0 | 27
39002.4537 | 1 | 0 | 27
39002.4555 | 1 | 0 | 27
39002.4573 | 1 | 0 | 27
39002.459 | 1 | 0 | 27
39002.4608 | 1 | 0 | 27
39002.4626 | 0 | 0 | 27
39002.4644 | 1 | 0 | 27
39002.4662 | 1 | 0 | 27
39002.468 | 1 | 0 | 27
39002.4697 | 2404 | 0 | 27
39002.4715 | 2407 | 0 | 27
39002.4733 | 2186 | 0 | 27
39002.4751 | 2028 | 0 | 27
39002.4769 | 2589 | 0 | 27
39002.4786 | 2188 | 0 | 27
39002.4804 | 1879 | 0 | 27
39002.4822 | 2335 | 0 | 27
39002.484 | 1348 | 0 | 27
27
39002.4341 | 0 | 0 | 28
39002.4359 | 1 | 0 | 28
39002.4377 | 1 | 0 | 28
39002.4395 | 1 | 0 | 28
39002.4412 | 1 | 0 | 28
39002.443 | 1 | 0 | 28
39002.4448 | 1 | 0 | 28
39002.4466 | 1 | 0 | 28
39002.4484 | 1 | 0 | 28
39002.4502 | 1 | 0 | 28
39002.4519 | 1 | 0 | 28
39002.4537 | 1 | 0 | 28
39002.4555 | 1 | 0 | 28
39002.4573 | 1 | 0 | 28
39002.4591 | 1 | 0 | 28
39002.4608 | 1 | 0 | 28
39002.4626 | 1 | 0 | 28
39002.4644 | 1 | 0 | 28
39002.4662 | 1 | 0 | 28
39002.468 | 1 | 0 | 28
39002.4698 | 135 | 0 | 28
39002.4715 | 2224 | 0 | 28
39002.4733 | 2175 | 0 | 28
39002.4751 | 2071 | 0 | 28
39002.4769 | 1936 | 0 | 28
39002.4787 | 1929 | 0 | 28
39002.4804 | 2401 | 0 | 28
39002.4822 | 1387 | 0 | 28
39002.484 | 1974 | 0 | 28
28
39002.4341 | 1 | 0 | 29
39002.4359 | 1 | 0 | 29
39002.4377 | 1 | 0 | 29
39002.4395 | 1 | 0 | 29
39002.4413 | 1 | 0 | 29
39002.443 | 1 | 0 | 29
39002.4448 | 1 | 0 | 29
39002.4466 | 1 | 0 | 29
39002.4484 | 1 | 0 | 29
39002.4502 | 0 | 0 | 29
39002.4519 | 1 | 0 | 29
39002.4537 | 1 | 0 | 29
39002.4555 | 1 | 0 | 29
39002.4573 | 1 | 0 | 29
39002.4591 | 1 | 0 | 29
39002.4609 | 1 | 0 | 29
39002.4626 | 1 | 0 | 29
39002.4662 | 1 | 0 | 29
39002.468 | 1 | 0 | 29
39002.4698 | 1927 | 0 | 29
39002.4716 | 2229 | 0 | 29
39002.4733 | 2581 | 0 | 29
39002.4751 | 2024 | 0 | 29
39002.4769 | 2386 | 0 | 29
39002.4787 | 2349 | 0 | 29
39002.4805 | 2214 | 0 | 29
39002.4822 | 1935 | 0 | 29
39002.484 | 1969 | 0 | 29
29
39002.4341 | 1 | 0 | 30
39002.4359 | 1 | 0 | 30
39002.4377 | 1 | 0 | 30
39002.4395 | 1 | 0 | 30
39002.4413 | 1 | 0 | 30
39002.4431 | 1 | 0 | 30
39002.4448 | 1 | 0 | 30
39002.4466 | 1 | 0 | 30
39002.4484 | 1 | 0 | 30
39002.4502 | 1 | 0 | 30
39002.452 | 1 | 0 | 30
39002.4538 | 1 | 0 | 30
39002.4555 | 1 | 0 | 30
39002.4573 | 1 | 0 | 30
39002.4591 | 1 | 0 | 30
39002.4609 | 1 | 0 | 30
39002.4627 | 1 | 0 | 30
39002.4644 | 1 | 0 | 30
39002.4662 | 1 | 0 | 30
39002.468 | 1 | 0 | 30
39002.4698 | 37 | 0 | 30
39002.4716 | 2167 | 0 | 30
39002.4733 | 2073 | 0 | 30
39002.4751 | 2102 | 0 | 30
39002.4769 | 1919 | 0 | 30
39002.4787 | 2221 | 0 | 30
39002.4805 | 2472 | 0 | 30
39002.4823 | 1376 | 0 | 30
39002.484 | 2039 | 0 | 30
30
39002.4342 | 1 | 0 | 31
39002.4359 | 1 | 0 | 31
39002.4377 | 1 | 0 | 31
39002.4395 | 1 | 0 | 31
39002.4413 | 1 | 0 | 31
39002.4431 | 1 | 0 | 31
39002.4448 | 1 | 0 | 31
39002.4466 | 1 | 0 | 31
39002.4484 | 1 | 0 | 31
39002.4502 | 1 | 0 | 31
39002.452 | 1 | 0 | 31
39002.4538 | 1 | 0 | 31
39002.4555 | 1 | 0 | 31
39002.4573 | 1 | 0 | 31
39002.4591 | 1 | 0 | 31
39002.4609 | 1 | 0 | 31
39002.4627 | 1 | 0 | 31
39002.4645 | 1 | 0 | 31
39002.4662 | 1 | 0 | 31
39002.468 | 1 | 0 | 31
39002.4698 | 2176 | 0 | 31
39002.4716 | 1999 | 0 | 31
39002.4734 | 2177 | 0 | 31
39002.4752 | 2451 | 0 | 31
39002.4769 | 2233 | 0 | 31
39002.4787 | 2561 | 0 | 31
39002.4805 | 2246 | 0 | 31
39002.4823 | 2352 | 0 | 31
39002.4841 | 1720 | 0 | 31
31
39002.4342 | 1 | 0 | 32
39002.436 | 1 | 0 | 32
39002.4377 | 1 | 0 | 32
39002.4395 | 0 | 0 | 32
39002.4413 | 1 | 0 | 32
39002.4431 | 1 | 0 | 32
39002.4449 | 1 | 0 | 32
39002.4466 | 1 | 0 | 32
39002.4484 | 0 | 0 | 32
39002.4502 | 1 | 0 | 32
39002.452 | 1 | 0 | 32
39002.4538 | 1 | 0 | 32
39002.4556 | 1 | 0 | 32
39002.4573 | 1 | 0 | 32
39002.4591 | 1 | 0 | 32
39002.4609 | 1 | 0 | 32
39002.4627 | 1 | 0 | 32
39002.4645 | 1 | 0 | 32
39002.4662 | 1 | 0 | 32
39002.468 | 1 | 0 | 32
39002.4698 | 107 | 0 | 32
39002.4716 | 1904 | 0 | 32
39002.4734 | 2367 | 0 | 32
39002.4752 | 2333 | 0 | 32
39002.4769 | 1974 | 0 | 32
39002.4787 | 2334 | 0 | 32
39002.4805 | 2011 | 0 | 32
39002.4823 | 1514 | 0 | 32
39002.4841 | 2274 | 0 | 32
32
39002.4342 | 1 | 0 | 33
39002.436 | 1 | 0 | 33
39002.4378 | 1 | 0 | 33
39002.4395 | 1 | 0 | 33
39002.4413 | 1 | 0 | 33
39002.4431 | 0 | 0 | 33
39002.4449 | 1 | 0 | 33
39002.4467 | 1 | 0 | 33
39002.4484 | 0 | 0 | 33
39002.4502 | 2 | 0 | 33
39002.452 | 1 | 0 | 33
39002.4538 | 1 | 0 | 33
39002.4556 | 1 | 0 | 33
39002.4574 | 0 | 0 | 33
39002.4591 | 1 | 0 | 33
39002.4609 | 1 | 0 | 33
39002.4627 | 2 | 0 | 33
39002.4645 | 1 | 0 | 33
39002.4663 | 1 | 0 | 33
39002.4681 | 1 | 0 | 33
39002.4698 | 1903 | 0 | 33
39002.4716 | 2483 | 0 | 33
39002.4734 | 2569 | 0 | 33
39002.4752 | 2526 | 0 | 33
39002.477 | 1999 | 0 | 33
39002.4787 | 2105 | 0 | 33
39002.4805 | 2262 | 0 | 33
39002.4823 | 1819 | 0 | 33
39002.4841 | 2098 | 0 | 33
33
39002.4342 | 1 | 0 | 34
39002.436 | 1 | 0 | 34
39002.4378 | 1 | 0 | 34
39002.4395 | 1 | 0 | 34
39002.4413 | 1 | 0 | 34
39002.4431 | 1 | 0 | 34
39002.4449 | 1 | 0 | 34
39002.4467 | 1 | 0 | 34
39002.4485 | 1 | 0 | 34
39002.4502 | 1 | 0 | 34
39002.452 | 1 | 0 | 34
39002.4538 | 1 | 0 | 34
39002.4556 | 1 | 0 | 34
39002.4574 | 1 | 0 | 34
39002.4592 | 1 | 0 | 34
39002.4609 | 1 | 0 | 34
39002.4627 | 1 | 0 | 34
39002.4645 | 1 | 0 | 34
39002.4663 | 1 | 0 | 34
39002.4681 | 1 | 0 | 34
39002.4698 | 280 | 0 | 34
39002.4716 | 2228 | 0 | 34
39002.4734 | 2069 | 0 | 34
39002.4752 | 1918 | 0 | 34
39002.477 | 2032 | 0 | 34
39002.4788 | 2445 | 0 | 34
39002.4805 | 2070 | 0 | 34
39002.4823 | 1695 | 0 | 34
39002.4841 | 2224 | 0 | 34
34
39002.4342 | 1 | 0 | 35
39002.436 | 1 | 0 | 35
39002.4378 | 1 | 0 | 35
39002.4396 | 1 | 0 | 35
39002.4414 | 1 | 0 | 35
39002.4431 | 1 | 0 | 35
39002.4449 | 1 | 0 | 35
39002.4467 | 1 | 0 | 35
39002.4485 | 1 | 0 | 35
39002.4503 | 1 | 0 | 35
39002.452 | 1 | 0 | 35
39002.4538 | 1 | 0 | 35
39002.4556 | 1 | 0 | 35
39002.4574 | 1 | 0 | 35
39002.4592 | 1 | 0 | 35
39002.4609 | 1 | 0 | 35
39002.4627 | 1 | 0 | 35
39002.4645 | 0 | 0 | 35
39002.4663 | 1 | 0 | 35
39002.4681 | 1 | 0 | 35
39002.4699 | 2440 | 0 | 35
39002.4716 | 2247 | 0 | 35
39002.4734 | 2318 | 0 | 35
39002.4752 | 2210 | 0 | 35
39002.477 | 2409 | 0 | 35
39002.4788 | 2189 | 0 | 35
39002.4806 | 2173 | 0 | 35
39002.4823 | 2090 | 0 | 35
39002.4841 | 1666 | 0 | 35
35
39002.4342 | 1 | 0 | 36
39002.436 | 1 | 0 | 36
39002.4378 | 1 | 0 | 36
39002.4396 | 1 | 0 | 36
39002.4414 | 1 | 0 | 36
39002.4431 | 1 | 0 | 36
39002.4449 | 1 | 0 | 36
39002.4467 | 1 | 0 | 36
39002.4485 | 1 | 0 | 36
39002.4503 | 1 | 0 | 36
39002.4521 | 1 | 0 | 36
39002.4538 | 1 | 0 | 36
39002.4556 | 1 | 0 | 36
39002.4574 | 1 | 0 | 36
39002.4592 | 1 | 0 | 36
39002.461 | 1 | 0 | 36
39002.4628 | 1 | 0 | 36
39002.4645 | 1 | 0 | 36
39002.4663 | 1 | 0 | 36
39002.4681 | 1 | 0 | 36
39002.4699 | 160 | 0 | 36
39002.4717 | 2263 | 0 | 36
39002.4734 | 2043 | 0 | 36
39002.4752 | 2262 | 0 | 36
39002.477 | 2115 | 0 | 36
39002.4788 | 2181 | 0 | 36
39002.4806 | 2049 | 0 | 36
39002.4824 | 1949 | 0 | 36
39002.4841 | 1952 | 0 | 36
36
39002.4343 | 1 | 0 | 37
39002.436 | 1 | 0 | 37
39002.4378 | 1 | 0 | 37
39002.4396 | 1 | 0 | 37
39002.4414 | 0 | 0 | 37
39002.4432 | 1 | 0 | 37
39002.445 | 1 | 0 | 37
39002.4467 | 1 | 0 | 37
39002.4485 | 1 | 0 | 37
39002.4503 | 1 | 0 | 37
39002.4521 | 1 | 0 | 37
39002.4539 | 0 | 0 | 37
39002.4556 | 1 | 0 | 37
39002.4574 | 1 | 0 | 37
39002.4592 | 1 | 0 | 37
39002.461 | 1 | 0 | 37
39002.4628 | 1 | 0 | 37
39002.4645 | 1 | 0 | 37
39002.4663 | 1 | 0 | 37
39002.4681 | 1 | 0 | 37
39002.4699 | 2450 | 0 | 37
39002.4717 | 2292 | 0 | 37
39002.4735 | 2064 | 0 | 37
39002.4752 | 2419 | 0 | 37
39002.477 | 2122 | 0 | 37
39002.4788 | 2375 | 0 | 37
39002.4806 | 2220 | 0 | 37
39002.4824 | 1866 | 0 | 37
39002.4842 | 1321 | 0 | 37
37
39002.4343 | 1 | 0 | 38
39002.4361 | 1 | 0 | 38
39002.4378 | 1 | 0 | 38
39002.4396 | 1 | 0 | 38
39002.4414 | 1 | 0 | 38
39002.4432 | 1 | 0 | 38
39002.445 | 1 | 0 | 38
39002.4467 | 1 | 0 | 38
39002.4485 | 1 | 0 | 38
39002.4503 | 0 | 0 | 38
39002.4521 | 1 | 0 | 38
39002.4539 | 1 | 0 | 38
39002.4557 | 1 | 0 | 38
39002.4574 | 0 | 0 | 38
39002.4592 | 1 | 0 | 38
39002.461 | 0 | 0 | 38
39002.4628 | 1 | 0 | 38
39002.4646 | 1 | 0 | 38
39002.4664 | 1 | 0 | 38
39002.4681 | 1 | 0 | 38
39002.4699 | 158 | 0 | 38
39002.4717 | 1987 | 0 | 38
39002.4735 | 2101 | 0 | 38
39002.4753 | 2381 | 0 | 38
39002.477 | 2236 | 0 | 38
39002.4788 | 1868 | 0 | 38
39002.4806 | 2083 | 0 | 38
39002.4824 | 1946 | 0 | 38
39002.4842 | 2395 | 0 | 38
38
39002.4343 | 1 | 0 | 39
39002.4361 | 1 | 0 | 39
39002.4378 | 1 | 0 | 39
39002.4396 | 1 | 0 | 39
39002.4414 | 1 | 0 | 39
39002.4432 | 1 | 0 | 39
39002.445 | 1 | 0 | 39
39002.4468 | 1 | 0 | 39
39002.4485 | 1 | 0 | 39
39002.4503 | 1 | 0 | 39
39002.4521 | 1 | 0 | 39
39002.4539 | 1 | 0 | 39
39002.4557 | 1 | 0 | 39
39002.4575 | 1 | 0 | 39
39002.4592 | 1 | 0 | 39
39002.461 | 1 | 0 | 39
39002.4628 | 1 | 0 | 39
39002.4646 | 1 | 0 | 39
39002.4664 | 1 | 0 | 39
39002.4681 | 1 | 0 | 39
39002.4699 | 1352 | 0 | 39
39002.4717 | 2563 | 0 | 39
39002.4735 | 2593 | 0 | 39
39002.4753 | 2568 | 0 | 39
39002.4771 | 2560 | 0 | 39
39002.4788 | 2582 | 0 | 39
39002.4806 | 1853 | 88 | 39
39002.4824 | 2264 | 54 | 39
39002.4842 | 1208 | 1191 | 39
39
39002.4343 | 1 | 0 | 40
39002.4361 | 1 | 0 | 40
39002.4379 | 1 | 0 | 40
39002.4397 | 1 | 0 | 40
39002.4414 | 1 | 0 | 40
39002.4432 | 1 | 0 | 40
39002.445 | 1 | 0 | 40
39002.4468 | 0 | 0 | 40
39002.4486 | 1 | 0 | 40
39002.4503 | 1 | 0 | 40
39002.4521 | 1 | 0 | 40
39002.4539 | 1 | 0 | 40
39002.4557 | 1 | 0 | 40
39002.4575 | 1 | 0 | 40
39002.4592 | 1 | 0 | 40
39002.461 | 1 | 0 | 40
39002.4628 | 2 | 0 | 40
39002.4646 | 1 | 0 | 40
39002.4664 | 1 | 0 | 40
39002.4682 | 1 | 0 | 40
39002.4699 | 1990 | 0 | 40
39002.4717 | 2566 | 0 | 40
39002.4735 | 2459 | 0 | 40
39002.4753 | 2047 | 0 | 40
39002.4771 | 2510 | 0 | 40
39002.4789 | 2514 | 0 | 40
39002.4806 | 2235 | 103 | 40
39002.4824 | 2005 | 46 | 40
39002.4842 | 1026 | 988 | 40
40
39002.4343 | 1 | 0 | 41
39002.4361 | 0 | 0 | 41
39002.4379 | 1 | 0 | 41
39002.4397 | 1 | 0 | 41
39002.4414 | 0 | 0 | 41
39002.4432 | 1 | 0 | 41
39002.445 | 1 | 0 | 41
39002.4468 | 1 | 0 | 41
39002.4486 | 1 | 0 | 41
39002.4504 | 1 | 0 | 41
39002.4521 | 1 | 0 | 41
39002.4539 | 1 | 0 | 41
39002.4557 | 1 | 0 | 41
39002.4575 | 1 | 0 | 41
39002.4593 | 1 | 0 | 41
39002.4611 | 1 | 0 | 41
39002.4628 | 1 | 0 | 41
39002.4646 | 1 | 0 | 41
39002.4664 | 1 | 0 | 41
39002.4682 | 1 | 0 | 41
39002.47 | 2470 | 0 | 41
39002.4717 | 1978 | 0 | 41
39002.4735 | 2213 | 0 | 41
39002.4753 | 2120 | 0 | 41
39002.4771 | 2059 | 0 | 41
39002.4789 | 2569 | 0 | 41
39002.4807 | 2170 | 0 | 41
39002.4824 | 1863 | 0 | 41
39002.4842 | 1331 | 0 | 41
41
39002.4343 | 1 | 0 | 42
39002.4361 | 1 | 0 | 42
39002.4379 | 1 | 0 | 42
39002.4397 | 1 | 0 | 42
39002.4415 | 1 | 0 | 42
39002.4432 | 1 | 0 | 42
39002.445 | 1 | 0 | 42
39002.4468 | 0 | 0 | 42
39002.4486 | 1 | 0 | 42
39002.4504 | 1 | 0 | 42
39002.4522 | 1 | 0 | 42
39002.4539 | 1 | 0 | 42
39002.4557 | 1 | 0 | 42
39002.4575 | 1 | 0 | 42
39002.4593 | 1 | 0 | 42
39002.4611 | 1 | 0 | 42
39002.4628 | 1 | 0 | 42
39002.4646 | 1 | 0 | 42
39002.4664 | 1 | 0 | 42
39002.4682 | 1 | 0 | 42
39002.4718 | 2322 | 0 | 42
39002.4735 | 2108 | 0 | 42
39002.4753 | 2110 | 0 | 42
39002.4771 | 2298 | 0 | 42
39002.4789 | 2033 | 0 | 42
39002.4807 | 2323 | 0 | 42
39002.4825 | 1795 | 0 | 42
39002.4842 | 1991 | 0 | 42
42
39002.4344 | 1 | 0 | 43
39002.4361 | 1 | 0 | 43
39002.4379 | 1 | 0 | 43
39002.4397 | 0 | 0 | 43
39002.4415 | 1 | 0 | 43
39002.4433 | 1 | 0 | 43
39002.445 | 1 | 0 | 43
39002.4468 | 1 | 0 | 43
39002.4486 | 1 | 0 | 43
39002.4504 | 1 | 0 | 43
39002.4522 | 0 | 0 | 43
39002.454 | 1 | 0 | 43
39002.4557 | 1 | 0 | 43
39002.4575 | 1 | 0 | 43
39002.4593 | 1 | 0 | 43
39002.4611 | 1 | 0 | 43
39002.4629 | 1 | 0 | 43
39002.4647 | 1 | 0 | 43
39002.4664 | 1 | 0 | 43
39002.4682 | 1 | 0 | 43
39002.47 | 2447 | 0 | 43
39002.4718 | 2302 | 0 | 43
39002.4736 | 2275 | 0 | 43
39002.4753 | 2271 | 0 | 43
39002.4771 | 2353 | 0 | 43
39002.4789 | 2344 | 0 | 43
39002.4807 | 1838 | 0 | 43
39002.4825 | 2182 | 0 | 43
39002.4842 | 1137 | 0 | 43
43
39002.4344 | 1 | 0 | 44
39002.4361 | 1 | 0 | 44
39002.4379 | 1 | 0 | 44
39002.4397 | 1 | 0 | 44
39002.4415 | 1 | 0 | 44
39002.4433 | 1 | 0 | 44
39002.4451 | 1 | 0 | 44
39002.4468 | 1 | 0 | 44
39002.4486 | 1 | 0 | 44
39002.4504 | 1 | 0 | 44
39002.4522 | 1 | 0 | 44
39002.454 | 1 | 0 | 44
39002.4558 | 1 | 0 | 44
39002.4575 | 0 | 0 | 44
39002.4593 | 1 | 0 | 44
39002.4611 | 1 | 0 | 44
39002.4629 | 1 | 0 | 44
39002.4647 | 1 | 0 | 44
39002.4664 | 1 | 0 | 44
39002.4682 | 1 | 0 | 44
39002.47 | 1057 | 0 | 44
39002.4718 | 2136 | 0 | 44
39002.4736 | 2493 | 0 | 44
39002.4754 | 2020 | 0 | 44
39002.4771 | 2373 | 0 | 44
39002.4789 | 2439 | 0 | 44
39002.4807 | 2131 | 0 | 44
39002.4825 | 2050 | 0 | 44
39002.4843 | 1864 | 0 | 44
44
39002.4344 | 1 | 0 | 45
39002.4362 | 1 | 0 | 45
39002.438 | 1 | 0 | 45
39002.4397 | 1 | 0 | 45
39002.4415 | 1 | 0 | 45
39002.4433 | 1 | 0 | 45
39002.4451 | 1 | 0 | 45
39002.4469 | 0 | 0 | 45
39002.4486 | 1 | 0 | 45
39002.4504 | 1 | 0 | 45
39002.4522 | 0 | 0 | 45
39002.454 | 1 | 0 | 45
39002.4558 | 1 | 0 | 45
39002.4575 | 1 | 0 | 45
39002.4593 | 1 | 0 | 45
39002.4611 | 1 | 0 | 45
39002.4629 | 1 | 0 | 45
39002.4647 | 1 | 0 | 45
39002.4665 | 1 | 0 | 45
39002.4682 | 1 | 0 | 45
39002.47 | 1929 | 0 | 45
39002.4718 | 2242 | 0 | 45
39002.4736 | 2069 | 0 | 45
39002.4754 | 2260 | 0 | 45
39002.4772 | 2331 | 0 | 45
39002.4789 | 2036 | 0 | 45
39002.4807 | 2310 | 0 | 45
39002.4825 | 2189 | 0 | 45
39002.4843 | 2032 | 0 | 45
45
39002.4344 | 1 | 0 | 46
39002.4362 | 1 | 0 | 46
39002.438 | 1 | 0 | 46
39002.4397 | 0 | 0 | 46
39002.4415 | 1 | 0 | 46
39002.4433 | 1 | 0 | 46
39002.4451 | 1 | 0 | 46
39002.4469 | 1 | 0 | 46
39002.4487 | 1 | 0 | 46
39002.4504 | 1 | 0 | 46
39002.4522 | 0 | 0 | 46
39002.454 | 1 | 0 | 46
39002.4558 | 1 | 0 | 46
39002.4576 | 0 | 0 | 46
39002.4594 | 1 | 0 | 46
39002.4611 | 1 | 0 | 46
39002.4629 | 1 | 0 | 46
39002.4647 | 1 | 0 | 46
39002.4665 | 1 | 0 | 46
39002.4683 | 0 | 0 | 46
39002.47 | 2147 | 0 | 46
39002.4718 | 2254 | 0 | 46
39002.4736 | 2116 | 0 | 46
39002.4754 | 2480 | 0 | 46
39002.4772 | 2379 | 0 | 46
39002.479 | 2389 | 0 | 46
39002.4807 | 2141 | 0 | 46
39002.4825 | 2300 | 0 | 46
39002.4843 | 1847 | 0 | 46
46
39002.4344 | 1 | 0 | 47
39002.4362 | 1 | 0 | 47
39002.438 | 1 | 0 | 47
39002.4398 | 1 | 0 | 47
39002.4415 | 1 | 0 | 47
39002.4433 | 1 | 0 | 47
39002.4451 | 1 | 0 | 47
39002.4469 | 1 | 0 | 47
39002.4487 | 1 | 0 | 47
39002.4505 | 1 | 0 | 47
39002.4522 | 1 | 0 | 47
39002.454 | 0 | 0 | 47
39002.4558 | 1 | 0 | 47
39002.4576 | 1 | 0 | 47
39002.4594 | 1 | 0 | 47
39002.4611 | 1 | 0 | 47
39002.4629 | 1 | 0 | 47
39002.4647 | 1 | 0 | 47
39002.4665 | 1 | 0 | 47
39002.4683 | 1 | 0 | 47
39002.4701 | 2374 | 0 | 47
39002.4718 | 2047 | 0 | 47
39002.4736 | 2491 | 0 | 47
39002.4754 | 2475 | 0 | 47
39002.4772 | 2318 | 0 | 47
39002.479 | 2494 | 0 | 47
39002.4808 | 2256 | 0 | 47
39002.4825 | 1936 | 0 | 47
39002.4843 | 1627 | 0 | 47
47
39002.4344 | 1 | 0 | 48
39002.4362 | 1 | 0 | 48
39002.438 | 1 | 0 | 48
39002.4398 | 1 | 0 | 48
39002.4416 | 0 | 0 | 48
39002.4433 | 1 | 0 | 48
39002.4451 | 1 | 0 | 48
39002.4469 | 1 | 0 | 48
39002.4487 | 1 | 0 | 48
39002.4505 | 1 | 0 | 48
39002.4523 | 1 | 0 | 48
39002.454 | 1 | 0 | 48
39002.4558 | 1 | 0 | 48
39002.4576 | 1 | 0 | 48
39002.4594 | 1 | 0 | 48
39002.4612 | 1 | 0 | 48
39002.463 | 1 | 0 | 48
39002.4647 | 1 | 0 | 48
39002.4665 | 1 | 0 | 48
39002.4683 | 1 | 0 | 48
39002.4701 | 800 | 0 | 48
39002.4719 | 2122 | 0 | 48
39002.4736 | 2070 | 0 | 48
39002.4754 | 2322 | 0 | 48
39002.4772 | 2403 | 0 | 48
39002.479 | 2121 | 0 | 48
39002.4808 | 2132 | 0 | 48
39002.4825 | 1988 | 0 | 48
39002.4843 | 1913 | 0 | 48
48
39002.4344 | 1 | 0 | 49
39002.4362 | 1 | 0 | 49
39002.438 | 1 | 0 | 49
39002.4398 | 1 | 0 | 49
39002.4416 | 1 | 0 | 49
39002.4434 | 1 | 0 | 49
39002.4451 | 1 | 0 | 49
39002.4469 | 1 | 0 | 49
39002.4487 | 1 | 0 | 49
39002.4505 | 0 | 0 | 49
39002.4523 | 1 | 0 | 49
39002.4541 | 1 | 0 | 49
39002.4558 | 1 | 0 | 49
39002.4576 | 1 | 0 | 49
39002.4594 | 1 | 0 | 49
39002.4612 | 1 | 0 | 49
39002.463 | 1 | 0 | 49
39002.4647 | 1 | 0 | 49
39002.4665 | 1 | 0 | 49
39002.4683 | 1 | 0 | 49
39002.4701 | 2232 | 0 | 49
39002.4719 | 2555 | 0 | 49
39002.4737 | 2035 | 0 | 49
39002.4754 | 2500 | 0 | 49
39002.4772 | 2010 | 0 | 49
39002.479 | 2507 | 0 | 49
39002.4808 | 2070 | 0 | 49
39002.4826 | 2316 | 0 | 49
39002.4844 | 1658 | 0 | 49
49
39002.4345 | 1 | 0 | 50
39002.4362 | 1 | 0 | 50
39002.438 | 1 | 0 | 50
39002.4398 | 1 | 0 | 50
39002.4416 | 0 | 0 | 50
39002.4434 | 1 | 0 | 50
39002.4452 | 1 | 0 | 50
39002.4469 | 1 | 0 | 50
39002.4487 | 1 | 0 | 50
39002.4505 | 1 | 0 | 50
39002.4523 | 1 | 0 | 50
39002.4541 | 1 | 0 | 50
39002.4558 | 1 | 0 | 50
39002.4576 | 1 | 0 | 50
39002.4594 | 1 | 0 | 50
39002.4612 | 1 | 0 | 50
39002.463 | 1 | 0 | 50
39002.4648 | 0 | 0 | 50
39002.4665 | 1 | 0 | 50
39002.4683 | 1 | 0 | 50
39002.4701 | 798 | 0 | 50
39002.4719 | 2233 | 0 | 50
39002.4737 | 2000 | 0 | 50
39002.4755 | 2008 | 0 | 50
39002.4772 | 2462 | 0 | 50
39002.479 | 2111 | 0 | 50
39002.4808 | 2028 | 0 | 50
39002.4826 | 2112 | 0 | 50
39002.4844 | 2187 | 0 | 50
50
39002.4345 | 0 | 0 | 51
39002.4363 | 1 | 0 | 51
39002.438 | 1 | 0 | 51
39002.4398 | 1 | 0 | 51
39002.4416 | 1 | 0 | 51
39002.4434 | 1 | 0 | 51
39002.4452 | 1 | 0 | 51
39002.447 | 1 | 0 | 51
39002.4487 | 1 | 0 | 51
39002.4505 | 1 | 0 | 51
39002.4523 | 1 | 0 | 51
39002.4541 | 1 | 0 | 51
39002.4559 | 1 | 0 | 51
39002.4577 | 1 | 0 | 51
39002.4594 | 1 | 0 | 51
39002.4612 | 1 | 0 | 51
39002.463 | 1 | 0 | 51
39002.4648 | 1 | 0 | 51
39002.4666 | 1 | 0 | 51
39002.4683 | 1 | 0 | 51
39002.4701 | 2362 | 0 | 51
39002.4719 | 2546 | 0 | 51
39002.4737 | 2576 | 0 | 51
39002.4755 | 2330 | 0 | 51
39002.4773 | 2587 | 0 | 51
39002.479 | 2440 | 0 | 51
39002.4808 | 1785 | 0 | 51
39002.4826 | 1897 | 0 | 51
39002.4844 | 1777 | 0 | 51
51
39002.4345 | 1 | 0 | 52
39002.4363 | 1 | 0 | 52
39002.4381 | 1 | 0 | 52
39002.4398 | 1 | 0 | 52
39002.4416 | 1 | 0 | 52
39002.4434 | 1 | 0 | 52
39002.4452 | 1 | 0 | 52
39002.447 | 1 | 0 | 52
39002.4488 | 1 | 0 | 52
39002.4505 | 1 | 0 | 52
39002.4523 | 1 | 0 | 52
39002.4541 | 1 | 0 | 52
39002.4559 | 1 | 0 | 52
39002.4577 | 1 | 0 | 52
39002.4594 | 0 | 0 | 52
39002.4612 | 1 | 0 | 52
39002.463 | 1 | 0 | 52
39002.4648 | 1 | 0 | 52
39002.4666 | 1 | 0 | 52
39002.4684 | 0 | 0 | 52
39002.4701 | 1058 | 0 | 52
39002.4719 | 1907 | 0 | 52
39002.4737 | 1999 | 0 | 52
39002.4755 | 2187 | 0 | 52
39002.4773 | 2128 | 0 | 52
39002.4791 | 1978 | 0 | 52
39002.4808 | 2091 | 0 | 52
39002.4826 | 1821 | 0 | 52
39002.4844 | 2124 | 0 | 52
52
39002.4345 | 1 | 0 | 53
39002.4363 | 1 | 0 | 53
39002.4381 | 0 | 0 | 53
39002.4399 | 1 | 0 | 53
39002.4416 | 1 | 0 | 53
39002.4434 | 0 | 0 | 53
39002.4452 | 1 | 0 | 53
39002.447 | 1 | 0 | 53
39002.4488 | 1 | 0 | 53
39002.4506 | 1 | 0 | 53
39002.4523 | 1 | 0 | 53
39002.4541 | 1 | 0 | 53
39002.4559 | 0 | 0 | 53
39002.4577 | 1 | 0 | 53
39002.4595 | 1 | 0 | 53
39002.4613 | 1 | 0 | 53
39002.463 | 1 | 0 | 53
39002.4648 | 1 | 0 | 53
39002.4666 | 1 | 0 | 53
39002.4684 | 1 | 0 | 53
39002.4702 | 2481 | 0 | 53
39002.4719 | 2558 | 0 | 53
39002.4737 | 2034 | 0 | 53
39002.4755 | 2403 | 0 | 53
39002.4773 | 2584 | 0 | 53
39002.4791 | 2100 | 0 | 53
39002.4808 | 2071 | 0 | 53
39002.4826 | 2089 | 0 | 53
39002.4844 | 1440 | 0 | 53
53
39002.4345 | 1 | 0 | 54
39002.4363 | 0 | 0 | 54
39002.4381 | 1 | 0 | 54
39002.4399 | 1 | 0 | 54
39002.4417 | 1 | 0 | 54
39002.4434 | 1 | 0 | 54
39002.4452 | 1 | 0 | 54
39002.447 | 1 | 0 | 54
39002.4488 | 1 | 0 | 54
39002.4506 | 1 | 0 | 54
39002.4523 | 1 | 0 | 54
39002.4541 | 1 | 0 | 54
39002.4559 | 1 | 0 | 54
39002.4577 | 1 | 0 | 54
39002.4595 | 1 | 0 | 54
39002.4613 | 1 | 0 | 54
39002.463 | 1 | 0 | 54
39002.4648 | 1 | 0 | 54
39002.4666 | 1 | 0 | 54
39002.4684 | 1 | 0 | 54
39002.4702 | 660 | 0 | 54
39002.472 | 2035 | 0 | 54
39002.4737 | 1966 | 0 | 54
39002.4755 | 2247 | 0 | 54
39002.4773 | 2261 | 0 | 54
39002.4791 | 2208 | 0 | 54
39002.4809 | 2164 | 0 | 54
39002.4827 | 1844 | 0 | 54
39002.4844 | 2214 | 0 | 54
54
39002.4345 | 1 | 0 | 55
39002.4363 | 1 | 0 | 55
39002.4381 | 1 | 0 | 55
39002.4399 | 1 | 0 | 55
39002.4417 | 1 | 0 | 55
39002.4435 | 1 | 0 | 55
39002.4452 | 1 | 0 | 55
39002.447 | 1 | 0 | 55
39002.4488 | 1 | 0 | 55
39002.4506 | 1 | 0 | 55
39002.4524 | 1 | 0 | 55
39002.4542 | 1 | 0 | 55
39002.4559 | 1 | 0 | 55
39002.4577 | 1 | 0 | 55
39002.4595 | 1 | 0 | 55
39002.4613 | 1 | 0 | 55
39002.4631 | 1 | 0 | 55
39002.4648 | 1 | 0 | 55
39002.4666 | 1 | 0 | 55
39002.4684 | 1 | 0 | 55
39002.4702 | 2377 | 0 | 55
39002.472 | 2275 | 0 | 55
39002.4737 | 2457 | 0 | 55
39002.4755 | 2047 | 0 | 55
39002.4773 | 2495 | 0 | 55
39002.4791 | 2375 | 0 | 55
39002.4809 | 1939 | 0 | 55
39002.4827 | 2247 | 0 | 55
39002.4844 | 1349 | 0 | 55
55
39002.4346 | 1 | 0 | 56
39002.4363 | 1 | 0 | 56
39002.4381 | 1 | 0 | 56
39002.4399 | 1 | 0 | 56
39002.4417 | 1 | 0 | 56
39002.4435 | 1 | 0 | 56
39002.4453 | 1 | 0 | 56
39002.447 | 1 | 0 | 56
39002.4488 | 1 | 0 | 56
39002.4506 | 1 | 0 | 56
39002.4524 | 1 | 0 | 56
39002.4542 | 0 | 0 | 56
39002.4559 | 1 | 0 | 56
39002.4577 | 1 | 0 | 56
39002.4595 | 1 | 0 | 56
39002.4613 | 1 | 0 | 56
39002.4631 | 0 | 0 | 56
39002.4649 | 1 | 0 | 56
39002.4666 | 1 | 0 | 56
39002.4684 | 1 | 0 | 56
39002.4702 | 1512 | 0 | 56
39002.472 | 2478 | 0 | 56
39002.4738 | 2402 | 0 | 56
39002.4756 | 2494 | 0 | 56
39002.4773 | 2016 | 0 | 56
39002.4791 | 2181 | 0 | 56
39002.4809 | 2417 | 0 | 56
39002.4827 | 2196 | 0 | 56
39002.4845 | 1761 | 0 | 56
56
39002.4346 | 1 | 0 | 57
39002.4364 | 1 | 0 | 57
39002.4381 | 1 | 0 | 57
39002.4399 | 1 | 0 | 57
39002.4417 | 1 | 0 | 57
39002.4435 | 1 | 0 | 57
39002.4453 | 1 | 0 | 57
39002.447 | 1 | 0 | 57
39002.4488 | 1 | 0 | 57
39002.4506 | 1 | 0 | 57
39002.4524 | 1 | 0 | 57
39002.4542 | 1 | 0 | 57
39002.456 | 1 | 0 | 57
39002.4577 | 0 | 0 | 57
39002.4595 | 1 | 0 | 57
39002.4613 | 1 | 0 | 57
39002.4631 | 1 | 0 | 57
39002.4649 | 1 | 0 | 57
39002.4667 | 0 | 0 | 57
39002.4684 | 1 | 0 | 57
39002.4702 | 2409 | 0 | 57
39002.472 | 1992 | 0 | 57
39002.4738 | 2346 | 0 | 57
39002.4756 | 2517 | 0 | 57
39002.4773 | 2341 | 0 | 57
39002.4791 | 2171 | 0 | 57
39002.4809 | 1845 | 0 | 57
39002.4827 | 2186 | 0 | 57
39002.4845 | 1449 | 0 | 57
57
39002.4346 | 1 | 0 | 58
39002.4364 | 0 | 0 | 58
39002.4382 | 1 | 0 | 58
39002.4399 | 0 | 0 | 58
39002.4417 | 1 | 0 | 58
39002.4435 | 1 | 0 | 58
39002.4453 | 1 | 0 | 58
39002.4471 | 1 | 0 | 58
39002.4489 | 1 | 0 | 58
39002.4506 | 0 | 0 | 58
39002.4524 | 1 | 0 | 58
39002.4542 | 1 | 0 | 58
39002.456 | 1 | 0 | 58
39002.4578 | 1 | 0 | 58
39002.4595 | 1 | 0 | 58
39002.4613 | 1 | 0 | 58
39002.4631 | 1 | 0 | 58
39002.4649 | 1 | 0 | 58
39002.4667 | 1 | 0 | 58
39002.4685 | 1 | 0 | 58
39002.4702 | 1993 | 0 | 58
39002.472 | 2115 | 0 | 58
39002.4738 | 2138 | 0 | 58
39002.4756 | 2297 | 0 | 58
39002.4774 | 2235 | 0 | 58
39002.4791 | 1984 | 0 | 58
39002.4809 | 2186 | 0 | 58
39002.4827 | 1887 | 0 | 58
39002.4845 | 2266 | 0 | 58
58
39002.4346 | 1 | 0 | 59
39002.4364 | 1 | 0 | 59
39002.4382 | 1 | 0 | 59
39002.44 | 1 | 0 | 59
39002.4417 | 1 | 0 | 59
39002.4435 | 1 | 0 | 59
39002.4453 | 1 | 0 | 59
39002.4471 | 1 | 0 | 59
39002.4489 | 1 | 0 | 59
39002.4506 | 1 | 0 | 59
39002.4524 | 1 | 0 | 59
39002.4542 | 1 | 0 | 59
39002.456 | 1 | 0 | 59
39002.4578 | 1 | 0 | 59
39002.4596 | 1 | 0 | 59
39002.4613 | 1 | 0 | 59
39002.4631 | 1 | 0 | 59
39002.4649 | 1 | 0 | 59
39002.4667 | 1 | 0 | 59
39002.4685 | 1 | 0 | 59
39002.4703 | 2504 | 0 | 59
39002.472 | 2073 | 0 | 59
39002.4738 | 2519 | 0 | 59
39002.4756 | 2272 | 0 | 59
39002.4774 | 2024 | 0 | 59
39002.4792 | 2538 | 0 | 59
39002.4809 | 1863 | 0 | 59
39002.4827 | 2152 | 0 | 59
39002.4845 | 1656 | 0 | 59
59
39002.4346 | 1 | 0 | 60
39002.4364 | 1 | 0 | 60
39002.4382 | 1 | 0 | 60
39002.44 | 1 | 0 | 60
39002.4418 | 1 | 0 | 60
39002.4435 | 1 | 0 | 60
39002.4453 | 1 | 0 | 60
39002.4471 | 1 | 0 | 60
39002.4489 | 1 | 0 | 60
39002.4507 | 1 | 0 | 60
39002.4525 | 0 | 0 | 60
39002.4542 | 1 | 0 | 60
39002.456 | 1 | 0 | 60
39002.4578 | 1 | 0 | 60
39002.4596 | 1 | 0 | 60
39002.4614 | 1 | 0 | 60
39002.4631 | 1 | 0 | 60
39002.4649 | 0 | 0 | 60
39002.4667 | 1 | 0 | 60
39002.4685 | 1 | 0 | 60
39002.4703 | 1995 | 0 | 60
39002.472 | 1950 | 0 | 60
39002.4738 | 1937 | 0 | 60
39002.4756 | 2476 | 0 | 60
39002.4774 | 2350 | 0 | 60
39002.4792 | 2266 | 0 | 60
39002.481 | 2268 | 0 | 60
39002.4827 | 1935 | 0 | 60
39002.4845 | 2032 | 0 | 60
60
39002.4346 | 1 | 0 | 61
39002.4364 | 1 | 0 | 61
39002.4382 | 1 | 0 | 61
39002.44 | 1 | 0 | 61
39002.4418 | 1 | 0 | 61
39002.4436 | 1 | 0 | 61
39002.4453 | 0 | 0 | 61
39002.4471 | 1 | 0 | 61
39002.4489 | 1 | 0 | 61
39002.4507 | 1 | 0 | 61
39002.4525 | 1 | 0 | 61
39002.4542 | 1 | 0 | 61
39002.456 | 1 | 0 | 61
39002.4578 | 1 | 0 | 61
39002.4596 | 1 | 0 | 61
39002.4614 | 1 | 0 | 61
39002.4632 | 1 | 0 | 61
39002.4649 | 0 | 0 | 61
39002.4667 | 1 | 0 | 61
39002.4685 | 1 | 0 | 61
39002.4703 | 2196 | 0 | 61
39002.4721 | 2116 | 0 | 61
39002.4739 | 2123 | 0 | 61
39002.4756 | 2330 | 0 | 61
39002.4774 | 2427 | 0 | 61
39002.4792 | 2185 | 0 | 61
39002.481 | 2313 | 0 | 61
39002.4828 | 2144 | 0 | 61
39002.4845 | 1679 | 0 | 61
61
39002.4347 | 1 | 0 | 62
39002.4364 | 1 | 0 | 62
39002.4382 | 1 | 0 | 62
39002.44 | 1 | 0 | 62
39002.4418 | 1 | 0 | 62
39002.4436 | 1 | 0 | 62
39002.4453 | 1 | 0 | 62
39002.4471 | 1 | 0 | 62
39002.4489 | 1 | 0 | 62
39002.4507 | 1 | 0 | 62
39002.4525 | 1 | 0 | 62
39002.4543 | 1 | 0 | 62
39002.456 | 1 | 0 | 62
39002.4578 | 1 | 0 | 62
39002.4596 | 1 | 0 | 62
39002.4614 | 1 | 0 | 62
39002.4632 | 1 | 0 | 62
39002.465 | 1 | 0 | 62
39002.4667 | 1 | 0 | 62
39002.4685 | 1 | 0 | 62
39002.4703 | 1810 | 0 | 62
39002.4721 | 2489 | 0 | 62
39002.4739 | 2077 | 0 | 62
39002.4756 | 2468 | 0 | 62
39002.4774 | 2364 | 0 | 62
39002.4792 | 2042 | 0 | 62
39002.481 | 1861 | 0 | 62
39002.4828 | 2194 | 0 | 62
39002.4846 | 1982 | 0 | 62
62
39002.4347 | 1 | 0 | 63
39002.4365 | 1 | 0 | 63
39002.4382 | 0 | 0 | 63
39002.44 | 1 | 0 | 63
39002.4418 | 1 | 0 | 63
39002.4436 | 1 | 0 | 63
39002.4454 | 1 | 0 | 63
39002.4472 | 1 | 0 | 63
39002.4489 | 1 | 0 | 63
39002.4507 | 1 | 0 | 63
39002.4525 | 1 | 0 | 63
39002.4543 | 1 | 0 | 63
39002.4561 | 1 | 0 | 63
39002.4578 | 1 | 0 | 63
39002.4596 | 1 | 0 | 63
39002.4614 | 1 | 0 | 63
39002.4632 | 1 | 0 | 63
39002.465 | 1 | 0 | 63
39002.4668 | 1 | 0 | 63
39002.4685 | 1 | 0 | 63
39002.4703 | 2314 | 0 | 63
39002.4721 | 2474 | 0 | 63
39002.4739 | 2272 | 0 | 63
39002.4757 | 2162 | 0 | 63
39002.4774 | 2007 | 0 | 63
39002.4792 | 2162 | 0 | 63
39002.481 | 2008 | 0 | 63
39002.4828 | 2175 | 0 | 63
39002.4846 | 1804 | 0 | 63
63
39002.4347 | 1 | 0 | 64
39002.4365 | 1 | 0 | 64
39002.4383 | 1 | 0 | 64
39002.44 | 1 | 0 | 64
39002.4418 | 1 | 0 | 64
39002.4436 | 1 | 0 | 64
39002.4454 | 1 | 0 | 64
39002.4472 | 1 | 0 | 64
39002.4489 | 1 | 0 | 64
39002.4507 | 1 | 0 | 64
39002.4525 | 1 | 0 | 64
39002.4543 | 1 | 0 | 64
39002.4561 | 1 | 0 | 64
39002.4579 | 1 | 0 | 64
39002.4596 | 1 | 0 | 64
39002.4614 | 1 | 0 | 64
39002.4632 | 1 | 0 | 64
39002.465 | 1 | 0 | 64
39002.4668 | 1 | 0 | 64
39002.4686 | 1 | 0 | 64
39002.4703 | 737 | 0 | 64
39002.4721 | 1986 | 0 | 64
39002.4739 | 2309 | 0 | 64
39002.4757 | 2189 | 0 | 64
39002.4775 | 1964 | 0 | 64
39002.4792 | 2426 | 0 | 64
39002.481 | 2403 | 0 | 64
39002.4828 | 2053 | 0 | 64
39002.4846 | 1991 | 0 | 64
64
39002.4347 | 1 | 0 | 65
39002.4365 | 1 | 0 | 65
39002.4383 | 1 | 0 | 65
39002.4401 | 1 | 0 | 65
39002.4418 | 0 | 0 | 65
39002.4436 | 1 | 0 | 65
39002.4454 | 1 | 0 | 65
39002.4472 | 1 | 0 | 65
39002.449 | 1 | 0 | 65
39002.4508 | 0 | 0 | 65
39002.4525 | 0 | 0 | 65
39002.4543 | 1 | 0 | 65
39002.4561 | 1 | 0 | 65
39002.4579 | 1 | 0 | 65
39002.4597 | 1 | 0 | 65
39002.4614 | 1 | 0 | 65
39002.4632 | 1 | 0 | 65
39002.465 | 0 | 0 | 65
39002.4668 | 1 | 0 | 65
39002.4686 | 1 | 0 | 65
39002.4703 | 2512 | 0 | 65
39002.4721 | 2119 | 0 | 65
39002.4739 | 2550 | 0 | 65
39002.4757 | 2548 | 0 | 65
39002.4775 | 2068 | 0 | 65
39002.4793 | 2064 | 0 | 65
39002.481 | 1836 | 0 | 65
39002.4828 | 1845 | 0 | 65
39002.4846 | 1896 | 0 | 65
65
39002.4347 | 1 | 0 | 66
39002.4365 | 1 | 0 | 66
39002.4383 | 1 | 0 | 66
39002.4401 | 1 | 0 | 66
39002.4419 | 1 | 0 | 66
39002.4436 | 1 | 0 | 66
39002.4454 | 0 | 0 | 66
39002.4472 | 1 | 0 | 66
39002.449 | 1 | 0 | 66
39002.4508 | 1 | 0 | 66
39002.4525 | 0 | 0 | 66
39002.4543 | 1 | 0 | 66
39002.4561 | 0 | 0 | 66
39002.4579 | 0 | 0 | 66
39002.4597 | 1 | 0 | 66
39002.4615 | 1 | 0 | 66
39002.4632 | 1 | 0 | 66
39002.465 | 1 | 0 | 66
39002.4668 | 1 | 0 | 66
39002.4686 | 1 | 0 | 66
39002.4704 | 2431 | 0 | 66
39002.4722 | 2367 | 0 | 66
39002.4739 | 2428 | 0 | 66
39002.4757 | 2412 | 0 | 66
39002.4775 | 1956 | 0 | 66
39002.4793 | 2144 | 0 | 66
39002.4811 | 2016 | 0 | 66
39002.4828 | 1836 | 0 | 66
39002.4846 | 1990 | 0 | 66
66
39002.4347 | 1 | 0 | 67
39002.4365 | 1 | 0 | 67
39002.4383 | 0 | 0 | 67
39002.4401 | 1 | 0 | 67
39002.4419 | 0 | 0 | 67
39002.4436 | 1 | 0 | 67
39002.4454 | 1 | 0 | 67
39002.4472 | 1 | 0 | 67
39002.449 | 1 | 0 | 67
39002.4508 | 1 | 0 | 67
39002.4526 | 1 | 0 | 67
39002.4543 | 1 | 0 | 67
39002.4561 | 1 | 0 | 67
39002.4579 | 1 | 0 | 67
39002.4597 | 1 | 0 | 67
39002.4615 | 1 | 0 | 67
39002.4633 | 1 | 0 | 67
39002.465 | 0 | 0 | 67
39002.4668 | 1 | 0 | 67
39002.4686 | 1 | 0 | 67
39002.4704 | 1988 | 0 | 67
39002.4722 | 2450 | 0 | 67
39002.4739 | 2572 | 0 | 67
39002.4757 | 2368 | 0 | 67
39002.4775 | 2157 | 0 | 67
39002.4793 | 2496 | 0 | 67
39002.4811 | 2309 | 0 | 67
39002.4829 | 2218 | 0 | 67
39002.4846 | 2021 | 0 | 67
67
39002.4348 | 1 | 0 | 68
39002.4365 | 1 | 0 | 68
39002.4383 | 1 | 0 | 68
39002.4401 | 1 | 0 | 68
39002.4419 | 1 | 0 | 68
39002.4437 | 1 | 0 | 68
39002.4455 | 1 | 0 | 68
39002.4472 | 1 | 0 | 68
39002.449 | 1 | 0 | 68
39002.4508 | 1 | 0 | 68
39002.4526 | 1 | 0 | 68
39002.4544 | 1 | 0 | 68
39002.4561 | 1 | 0 | 68
39002.4579 | 1 | 0 | 68
39002.4597 | 1 | 0 | 68
39002.4615 | 1 | 0 | 68
39002.4633 | 1 | 0 | 68
39002.4651 | 1 | 0 | 68
39002.4668 | 0 | 0 | 68
39002.4686 | 1 | 0 | 68
39002.4704 | 2266 | 0 | 68
39002.4722 | 2404 | 0 | 68
39002.474 | 2197 | 0 | 68
39002.4757 | 2413 | 0 | 68
39002.4775 | 1922 | 0 | 68
39002.4793 | 2376 | 0 | 68
39002.4811 | 2315 | 0 | 68
39002.4829 | 1851 | 0 | 68
39002.4847 | 2011 | 0 | 68
68
39002.4348 | 1 | 0 | 69
39002.4366 | 1 | 0 | 69
39002.4383 | 1 | 0 | 69
39002.4401 | 1 | 0 | 69
39002.4419 | 1 | 0 | 69
39002.4437 | 1 | 0 | 69
39002.4455 | 1 | 0 | 69
39002.4472 | 0 | 0 | 69
39002.449 | 1 | 0 | 69
39002.4508 | 1 | 0 | 69
39002.4526 | 1 | 0 | 69
39002.4544 | 1 | 0 | 69
39002.4562 | 1 | 0 | 69
39002.4579 | 1 | 0 | 69
39002.4597 | 1 | 0 | 69
39002.4615 | 1 | 0 | 69
39002.4633 | 1 | 0 | 69
39002.4651 | 1 | 0 | 69
39002.4669 | 1 | 0 | 69
39002.4686 | 1 | 0 | 69
39002.4704 | 2035 | 0 | 69
39002.4722 | 2366 | 0 | 69
39002.474 | 2257 | 0 | 69
39002.4758 | 2292 | 0 | 69
39002.4775 | 2129 | 3 | 69
39002.4793 | 2267 | 6 | 69
39002.4811 | 2302 | 20 | 69
39002.4829 | 2083 | 36 | 69
39002.4847 | 1860 | 55 | 69
69
39002.4348 | 1 | 0 | 70
39002.4366 | 1 | 0 | 70
39002.4384 | 1 | 0 | 70
39002.4401 | 1 | 0 | 70
39002.4419 | 1 | 0 | 70
39002.4437 | 0 | 0 | 70
39002.4455 | 1 | 0 | 70
39002.4473 | 0 | 0 | 70
39002.4491 | 1 | 0 | 70
39002.4508 | 1 | 0 | 70
39002.4526 | 1 | 0 | 70
39002.4544 | 1 | 0 | 70
39002.4562 | 1 | 0 | 70
39002.458 | 1 | 0 | 70
39002.4597 | 1 | 0 | 70
39002.4615 | 1 | 0 | 70
39002.4633 | 1 | 0 | 70
39002.4651 | 1 | 0 | 70
39002.4669 | 1 | 0 | 70
39002.4686 | 1 | 0 | 70
39002.4704 | 2071 | 0 | 70
39002.4722 | 2125 | 0 | 70
39002.474 | 2177 | 1 | 70
39002.4758 | 1936 | 0 | 70
39002.4776 | 2400 | 3 | 70
39002.4793 | 1943 | 5 | 70
39002.4811 | 2043 | 21 | 70
39002.4829 | 2332 | 36 | 70
39002.4847 | 1865 | 44 | 70
70
39002.4348 | 1 | 0 | 71
39002.4366 | 1 | 0 | 71
39002.4384 | 1 | 0 | 71
39002.4402 | 0 | 0 | 71
39002.4419 | 1 | 0 | 71
39002.4437 | 1 | 0 | 71
39002.4455 | 1 | 0 | 71
39002.4473 | 1 | 0 | 71
39002.4491 | 0 | 0 | 71
39002.4508 | 1 | 0 | 71
39002.4526 | 1 | 0 | 71
39002.4544 | 1 | 0 | 71
39002.4562 | 1 | 0 | 71
39002.458 | 1 | 0 | 71
39002.4598 | 1 | 0 | 71
39002.4615 | 1 | 0 | 71
39002.4633 | 1 | 0 | 71
39002.4651 | 1 | 0 | 71
39002.4669 | 1 | 0 | 71
39002.4687 | 1 | 0 | 71
39002.4705 | 1931 | 1 | 71
39002.4722 | 2099 | 0 | 71
39002.474 | 2418 | 0 | 71
39002.4758 | 1997 | 0 | 71
39002.4776 | 2385 | 2 | 71
39002.4794 | 2434 | 6 | 71
39002.4811 | 1698 | 555 | 71
39002.4829 | 2223 | 31 | 71
39002.4847 | 1971 | 44 | 71
71
39002.4348 | 0 | 0 | 72
39002.4366 | 1 | 0 | 72
39002.4384 | 1 | 0 | 72
39002.4402 | 1 | 0 | 72
39002.4419 | 1 | 0 | 72
39002.4437 | 0 | 0 | 72
39002.4455 | 1 | 0 | 72
39002.4473 | 1 | 0 | 72
39002.4491 | 1 | 0 | 72
39002.4509 | 1 | 0 | 72
39002.4526 | 1 | 0 | 72
39002.4544 | 1 | 0 | 72
39002.4562 | 1 | 0 | 72
39002.458 | 1 | 0 | 72
39002.4598 | 1 | 0 | 72
39002.4616 | 1 | 0 | 72
39002.4633 | 1 | 0 | 72
39002.4651 | 1 | 0 | 72
39002.4669 | 1 | 0 | 72
39002.4687 | 1 | 0 | 72
39002.4705 | 2383 | 1 | 72
39002.4722 | 2144 | 0 | 72
39002.474 | 2331 | 0 | 72
39002.4758 | 2253 | 0 | 72
39002.4776 | 1976 | 2 | 72
39002.4794 | 2035 | 5 | 72
39002.4812 | 1704 | 596 | 72
39002.4829 | 1887 | 24 | 72
39002.4847 | 1999 | 38 | 72
72
39002.4348 | 1 | 0 | 73
39002.4366 | 1 | 0 | 73
39002.4384 | 1 | 0 | 73
39002.4402 | 1 | 0 | 73
39002.442 | 1 | 0 | 73
39002.4437 | 1 | 0 | 73
39002.4455 | 1 | 0 | 73
39002.4473 | 1 | 0 | 73
39002.4491 | 1 | 0 | 73
39002.4509 | 1 | 0 | 73
39002.4527 | 1 | 0 | 73
39002.4544 | 1 | 0 | 73
39002.4562 | 1 | 0 | 73
39002.458 | 1 | 0 | 73
39002.4598 | 1 | 0 | 73
39002.4616 | 1 | 0 | 73
39002.4634 | 1 | 0 | 73
39002.4651 | 1 | 0 | 73
39002.4669 | 1 | 0 | 73
39002.4687 | 1 | 0 | 73
39002.4705 | 2180 | 0 | 73
39002.4723 | 2491 | 0 | 73
39002.474 | 2161 | 0 | 73
39002.4758 | 2490 | 0 | 73
39002.4776 | 2455 | 1 | 73
39002.4794 | 1930 | 6 | 73
39002.4812 | 1489 | 542 | 73
39002.483 | 2412 | 29 | 73
39002.4847 | 1981 | 36 | 73
73
39002.4348 | 1 | 0 | 74
39002.4366 | 1 | 0 | 74
39002.4384 | 1 | 0 | 74
39002.4402 | 0 | 0 | 74
39002.442 | 1 | 0 | 74
39002.4438 | 1 | 0 | 74
39002.4455 | 1 | 0 | 74
39002.4473 | 1 | 0 | 74
39002.4491 | 1 | 0 | 74
39002.4509 | 1 | 0 | 74
39002.4527 | 1 | 0 | 74
39002.4545 | 1 | 0 | 74
39002.4562 | 1 | 0 | 74
39002.458 | 1 | 0 | 74
39002.4598 | 0 | 0 | 74
39002.4616 | 1 | 0 | 74
39002.4634 | 1 | 0 | 74
39002.4652 | 1 | 0 | 74
39002.4669 | 1 | 0 | 74
39002.4687 | 1 | 0 | 74
39002.4705 | 2094 | 0 | 74
39002.4723 | 2198 | 0 | 74
39002.4741 | 2071 | 0 | 74
39002.4758 | 1951 | 0 | 74
39002.4776 | 2221 | 0 | 74
39002.4794 | 2086 | 8 | 74
39002.4812 | 1690 | 547 | 74
39002.483 | 1924 | 20 | 74
39002.4848 | 1865 | 33 | 74
74
39002.4349 | 1 | 0 | 75
39002.4367 | 1 | 0 | 75
39002.4384 | 1 | 0 | 75
39002.4402 | 0 | 0 | 75
39002.442 | 1 | 0 | 75
39002.4438 | 1 | 0 | 75
39002.4456 | 1 | 0 | 75
39002.4473 | 1 | 0 | 75
39002.4491 | 1 | 0 | 75
39002.4509 | 1 | 0 | 75
39002.4527 | 1 | 0 | 75
39002.4545 | 1 | 0 | 75
39002.4563 | 1 | 0 | 75
39002.458 | 1 | 0 | 75
39002.4598 | 1 | 0 | 75
39002.4616 | 1 | 0 | 75
39002.4634 | 1 | 0 | 75
39002.4652 | 1 | 0 | 75
39002.4669 | 0 | 0 | 75
39002.4687 | 1 | 0 | 75
39002.4705 | 1929 | 0 | 75
39002.4723 | 2519 | 0 | 75
39002.4741 | 1955 | 0 | 75
39002.4759 | 2177 | 0 | 75
39002.4776 | 2168 | 0 | 75
39002.4794 | 1970 | 7 | 75
39002.4812 | 1428 | 561 | 75
39002.483 | 1920 | 18 | 75
39002.4848 | 2286 | 39 | 75
75
39002.4349 | 1 | 0 | 76
39002.4367 | 0 | 0 | 76
39002.4384 | 1 | 0 | 76
39002.4402 | 1 | 0 | 76
39002.442 | 1 | 0 | 76
39002.4438 | 1 | 0 | 76
39002.4456 | 1 | 0 | 76
39002.4474 | 1 | 0 | 76
39002.4509 | 1 | 0 | 76
39002.4527 | 0 | 0 | 76
39002.4545 | 1 | 0 | 76
39002.4563 | 1 | 0 | 76
39002.4581 | 1 | 0 | 76
39002.4598 | 1 | 0 | 76
39002.4616 | 1 | 0 | 76
39002.4634 | 1 | 0 | 76
39002.4652 | 1 | 0 | 76
39002.467 | 1 | 0 | 76
39002.4688 | 1 | 0 | 76
39002.4705 | 1736 | 0 | 76
39002.4723 | 1990 | 0 | 76
39002.4741 | 2166 | 1 | 76
39002.4759 | 2486 | 0 | 76
39002.4777 | 2320 | 1 | 76
39002.4794 | 2365 | 8 | 76
39002.4812 | 1683 | 521 | 76
39002.483 | 1870 | 17 | 76
39002.4848 | 2336 | 44 | 76
76
39002.4349 | 1 | 0 | 77
39002.4367 | 1 | 0 | 77
39002.4385 | 1 | 0 | 77
39002.4402 | 1 | 0 | 77
39002.442 | 1 | 0 | 77
39002.4438 | 1 | 0 | 77
39002.4456 | 1 | 0 | 77
39002.4474 | 1 | 0 | 77
39002.4492 | 1 | 0 | 77
39002.4509 | 1 | 0 | 77
39002.4527 | 1 | 0 | 77
39002.4545 | 1 | 0 | 77
39002.4563 | 1 | 0 | 77
39002.4581 | 1 | 0 | 77
39002.4598 | 1 | 0 | 77
39002.4616 | 1 | 0 | 77
39002.4634 | 1 | 0 | 77
39002.4652 | 1 | 0 | 77
39002.467 | 1 | 0 | 77
39002.4688 | 1 | 0 | 77
39002.4705 | 2476 | 0 | 77
39002.4723 | 1954 | 0 | 77
39002.4741 | 2436 | 0 | 77
39002.4759 | 2282 | 0 | 77
39002.4777 | 2439 | 1 | 77
39002.4795 | 1962 | 7 | 77
39002.4812 | 1831 | 248 | 77
39002.483 | 2202 | 18 | 77
39002.4848 | 1882 | 36 | 77
77
39002.4349 | 1 | 0 | 78
39002.4367 | 1 | 0 | 78
39002.4385 | 1 | 0 | 78
39002.4403 | 1 | 0 | 78
39002.442 | 1 | 0 | 78
39002.4438 | 0 | 0 | 78
39002.4456 | 1 | 0 | 78
39002.4474 | 1 | 0 | 78
39002.4492 | 1 | 0 | 78
39002.451 | 1 | 0 | 78
39002.4527 | 1 | 0 | 78
39002.4545 | 1 | 0 | 78
39002.4563 | 1 | 0 | 78
39002.4581 | 1 | 0 | 78
39002.4599 | 1 | 0 | 78
39002.4617 | 1 | 0 | 78
39002.4634 | 1 | 0 | 78
39002.4652 | 1 | 0 | 78
39002.467 | 1 | 0 | 78
39002.4688 | 1 | 0 | 78
39002.4706 | 1319 | 0 | 78
39002.4723 | 2018 | 0 | 78
39002.4741 | 2335 | 2 | 78
39002.4759 | 2137 | 0 | 78
39002.4777 | 2291 | 0 | 78
39002.4795 | 2069 | 7 | 78
39002.4812 | 1654 | 208 | 78
39002.483 | 1901 | 15 | 78
39002.4848 | 2010 | 39 | 78
78
39002.4349 | 1 | 0 | 79
39002.4367 | 1 | 0 | 79
39002.4385 | 1 | 0 | 79
39002.4403 | 1 | 0 | 79
39002.4421 | 1 | 0 | 79
39002.4438 | 1 | 0 | 79
39002.4456 | 0 | 0 | 79
39002.4474 | 1 | 0 | 79
39002.4492 | 1 | 0 | 79
39002.451 | 1 | 0 | 79
39002.4528 | 1 | 0 | 79
39002.4545 | 1 | 0 | 79
39002.4563 | 1 | 0 | 79
39002.4581 | 1 | 0 | 79
39002.4599 | 1 | 0 | 79
39002.4617 | 1 | 0 | 79
39002.4634 | 1 | 0 | 79
39002.4652 | 1 | 0 | 79
39002.467 | 1 | 0 | 79
39002.4688 | 1 | 0 | 79
39002.4706 | 2129 | 0 | 79
39002.4724 | 2381 | 0 | 79
39002.4741 | 2022 | 1 | 79
39002.4759 | 2016 | 0 | 79
39002.4777 | 2022 | 1 | 79
39002.4795 | 2448 | 6 | 79
39002.4813 | 2062 | 352 | 79
39002.4831 | 2190 | 17 | 79
39002.4848 | 2375 | 31 | 79
79
39002.435 | 0 | 0 | 80
39002.4367 | 1 | 0 | 80
39002.4385 | 1 | 0 | 80
39002.4403 | 1 | 0 | 80
39002.4421 | 1 | 0 | 80
39002.4439 | 1 | 0 | 80
39002.4456 | 1 | 0 | 80
39002.4474 | 0 | 0 | 80
39002.4492 | 1 | 0 | 80
39002.451 | 1 | 0 | 80
39002.4528 | 0 | 0 | 80
39002.4545 | 1 | 0 | 80
39002.4563 | 1 | 0 | 80
39002.4581 | 1 | 0 | 80
39002.4599 | 1 | 0 | 80
39002.4617 | 1 | 0 | 80
39002.4635 | 1 | 0 | 80
39002.4652 | 1 | 0 | 80
39002.467 | 1 | 0 | 80
39002.4688 | 1 | 0 | 80
39002.4706 | 2040 | 0 | 80
39002.4724 | 2473 | 0 | 80
39002.4742 | 2148 | 1 | 80
39002.4759 | 2470 | 0 | 80
39002.4777 | 1925 | 0 | 80
39002.4795 | 2156 | 4 | 80
39002.4813 | 1614 | 302 | 80
39002.4831 | 1922 | 14 | 80
39002.4848 | 2146 | 33 | 80
80
39002.435 | 1 | 0 | 81
39002.4367 | 1 | 0 | 81
39002.4385 | 1 | 0 | 81
39002.4403 | 1 | 0 | 81
39002.4421 | 1 | 0 | 81
39002.4439 | 1 | 0 | 81
39002.4457 | 1 | 0 | 81
39002.4474 | 1 | 0 | 81
39002.4492 | 1 | 0 | 81
39002.451 | 1 | 0 | 81
39002.4528 | 1 | 0 | 81
39002.4546 | 1 | 0 | 81
39002.4564 | 1 | 0 | 81
39002.4581 | 1 | 0 | 81
39002.4599 | 1 | 0 | 81
39002.4617 | 1 | 0 | 81
39002.4635 | 1 | 0 | 81
39002.4653 | 1 | 0 | 81
39002.467 | 1 | 0 | 81
39002.4688 | 1 | 0 | 81
39002.4706 | 2262 | 0 | 81
39002.4724 | 2407 | 0 | 81
39002.4742 | 2019 | 4 | 81
39002.476 | 2042 | 0 | 81
39002.4777 | 2460 | 1 | 81
39002.4795 | 2376 | 4 | 81
39002.4813 | 1736 | 200 | 81
39002.4831 | 2296 | 16 | 81
39002.4849 | 1940 | 31 | 81
81
39002.435 | 1 | 0 | 82
39002.4368 | 1 | 0 | 82
39002.4386 | 1 | 0 | 82
39002.4403 | 1 | 0 | 82
39002.4421 | 1 | 0 | 82
39002.4439 | 0 | 0 | 82
39002.4457 | 0 | 0 | 82
39002.4475 | 1 | 0 | 82
39002.4492 | 1 | 0 | 82
39002.451 | 0 | 0 | 82
39002.4528 | 1 | 0 | 82
39002.4546 | 1 | 0 | 82
39002.4564 | 1 | 0 | 82
39002.4581 | 1 | 0 | 82
39002.4599 | 1 | 0 | 82
39002.4617 | 1 | 0 | 82
39002.4635 | 1 | 0 | 82
39002.4653 | 1 | 0 | 82
39002.4671 | 1 | 0 | 82
39002.4688 | 10 | 9 | 82
39002.4706 | 2435 | 0 | 82
39002.4724 | 2229 | 0 | 82
39002.4742 | 2107 | 4 | 82
39002.476 | 2455 | 0 | 82
39002.4778 | 2271 | 1 | 82
39002.4795 | 1980 | 3 | 82
39002.4813 | 1874 | 405 | 82
39002.4831 | 2102 | 13 | 82
39002.4849 | 2123 | 40 | 82
82
39002.435 | 1 | 0 | 83
39002.4368 | 1 | 0 | 83
39002.4386 | 1 | 0 | 83
39002.4403 | 0 | 0 | 83
39002.4421 | 1 | 0 | 83
39002.4439 | 1 | 0 | 83
39002.4457 | 1 | 0 | 83
39002.4475 | 1 | 0 | 83
39002.4493 | 1 | 0 | 83
39002.451 | 1 | 0 | 83
39002.4528 | 1 | 0 | 83
39002.4546 | 1 | 0 | 83
39002.4564 | 1 | 0 | 83
39002.4582 | 1 | 0 | 83
39002.46 | 1 | 0 | 83
39002.4617 | 1 | 0 | 83
39002.4635 | 1 | 0 | 83
39002.4653 | 1 | 0 | 83
39002.4671 | 1 | 0 | 83
39002.4689 | 1 | 0 | 83
39002.4706 | 2015 | 0 | 83
39002.4724 | 2065 | 0 | 83
39002.4742 | 2350 | 1 | 83
39002.476 | 2130 | 0 | 83
39002.4778 | 2458 | 0 | 83
39002.4795 | 2071 | 3 | 83
39002.4813 | 2010 | 347 | 83
39002.4831 | 2265 | 13 | 83
39002.4849 | 1979 | 52 | 83
83
39002.435 | 1 | 0 | 84
39002.4368 | 1 | 0 | 84
39002.4386 | 1 | 0 | 84
39002.4404 | 1 | 0 | 84
39002.4421 | 1 | 0 | 84
39002.4439 | 1 | 0 | 84
39002.4457 | 1 | 0 | 84
39002.4475 | 1 | 0 | 84
39002.4493 | 1 | 0 | 84
39002.4511 | 1 | 0 | 84
39002.4528 | 1 | 0 | 84
39002.4546 | 1 | 0 | 84
39002.4564 | 1 | 0 | 84
39002.4582 | 1 | 0 | 84
39002.46 | 1 | 0 | 84
39002.4617 | 1 | 0 | 84
39002.4635 | 1 | 0 | 84
39002.4653 | 1 | 0 | 84
39002.4671 | 1 | 0 | 84
39002.4689 | 8 | 7 | 84
39002.4707 | 2092 | 0 | 84
39002.4724 | 2315 | 0 | 84
39002.4742 | 2101 | 0 | 84
39002.476 | 2199 | 0 | 84
39002.4778 | 2016 | 0 | 84
39002.4796 | 2466 | 4 | 84
39002.4814 | 1864 | 481 | 84
39002.4831 | 2285 | 12 | 84
39002.4849 | 2127 | 67 | 84
84
39002.435 | 1 | 0 | 85
39002.4368 | 1 | 0 | 85
39002.4386 | 1 | 0 | 85
39002.4404 | 0 | 0 | 85
39002.4422 | 1 | 0 | 85
39002.4439 | 1 | 0 | 85
39002.4457 | 1 | 0 | 85
39002.4475 | 1 | 0 | 85
39002.4493 | 1 | 0 | 85
39002.4511 | 1 | 0 | 85
39002.4529 | 1 | 0 | 85
39002.4546 | 1 | 0 | 85
39002.4564 | 0 | 0 | 85
39002.4582 | 1 | 0 | 85
39002.46 | 1 | 0 | 85
39002.4618 | 1 | 0 | 85
39002.4635 | 1 | 0 | 85
39002.4653 | 1 | 0 | 85
39002.4671 | 1 | 0 | 85
39002.4689 | 37 | 33 | 85
39002.4707 | 2334 | 0 | 85
39002.4725 | 2101 | 0 | 85
39002.4742 | 2107 | 2 | 85
39002.476 | 2505 | 0 | 85
39002.4778 | 2066 | 1 | 85
39002.4796 | 1914 | 3 | 85
39002.4814 | 1543 | 411 | 85
39002.4831 | 1993 | 10 | 85
39002.4849 | 2301 | 77 | 85
85
39002.435 | 1 | 0 | 86
39002.4368 | 1 | 0 | 86
39002.4386 | 0 | 0 | 86
39002.4404 | 1 | 0 | 86
39002.4422 | 1 | 0 | 86
39002.444 | 1 | 0 | 86
39002.4457 | 1 | 0 | 86
39002.4475 | 1 | 0 | 86
39002.4493 | 1 | 0 | 86
39002.4511 | 1 | 0 | 86
39002.4529 | 0 | 0 | 86
39002.4547 | 1 | 0 | 86
39002.4564 | 1 | 0 | 86
39002.4582 | 1 | 0 | 86
39002.46 | 1 | 0 | 86
39002.4618 | 1 | 0 | 86
39002.4636 | 1 | 0 | 86
39002.4653 | 1 | 0 | 86
39002.4671 | 0 | 0 | 86
39002.4689 | 34 | 33 | 86
39002.4707 | 1725 | 0 | 86
39002.4725 | 2387 | 0 | 86
39002.4743 | 1979 | 0 | 86
39002.476 | 2046 | 0 | 86
39002.4778 | 2268 | 0 | 86
39002.4796 | 2273 | 4 | 86
39002.4814 | 1613 | 522 | 86
39002.4832 | 1949 | 9 | 86
39002.485 | 2259 | 94 | 86
86
39002.4351 | 1 | 0 | 87
39002.4369 | 1 | 0 | 87
39002.4386 | 1 | 0 | 87
39002.4404 | 1 | 0 | 87
39002.4422 | 1 | 0 | 87
39002.444 | 1 | 0 | 87
39002.4458 | 1 | 0 | 87
39002.4475 | 1 | 0 | 87
39002.4493 | 1 | 0 | 87
39002.4511 | 1 | 0 | 87
39002.4529 | 0 | 0 | 87
39002.4547 | 1 | 0 | 87
39002.4564 | 1 | 0 | 87
39002.4582 | 0 | 0 | 87
39002.46 | 1 | 0 | 87
39002.4618 | 1 | 0 | 87
39002.4636 | 1 | 0 | 87
39002.4654 | 1 | 0 | 87
39002.4671 | 1 | 0 | 87
39002.4689 | 67 | 63 | 87
39002.4707 | 2527 | 0 | 87
39002.4725 | 2155 | 0 | 87
39002.4743 | 2466 | 0 | 87
39002.4761 | 2386 | 0 | 87
39002.4778 | 2466 | 0 | 87
39002.4796 | 2457 | 4 | 87
39002.4814 | 2153 | 225 | 87
39002.4832 | 2275 | 11 | 87
39002.485 | 2005 | 73 | 87
87
39002.4351 | 1 | 0 | 88
39002.4369 | 1 | 0 | 88
39002.4386 | 1 | 0 | 88
39002.4404 | 1 | 0 | 88
39002.4422 | 1 | 0 | 88
39002.444 | 0 | 0 | 88
39002.4458 | 1 | 0 | 88
39002.4476 | 1 | 0 | 88
39002.4493 | 1 | 0 | 88
39002.4511 | 1 | 0 | 88
39002.4529 | 1 | 0 | 88
39002.4547 | 1 | 0 | 88
39002.4565 | 1 | 0 | 88
39002.4583 | 1 | 0 | 88
39002.46 | 1 | 0 | 88
39002.4618 | 1 | 0 | 88
39002.4636 | 1 | 0 | 88
39002.4654 | 1 | 0 | 88
39002.4672 | 1 | 0 | 88
39002.4689 | 85 | 68 | 88
39002.4707 | 2132 | 0 | 88
39002.4725 | 2280 | 0 | 88
39002.4743 | 2075 | 0 | 88
39002.4761 | 1957 | 0 | 88
39002.4778 | 1947 | 1 | 88
39002.4796 | 1896 | 3 | 88
39002.4814 | 1983 | 424 | 88
39002.4832 | 2171 | 9 | 88
39002.485 | 2325 | 73 | 88
88
39002.4351 | 1 | 0 | 89
39002.4369 | 1 | 0 | 89
39002.4387 | 1 | 0 | 89
39002.4404 | 1 | 0 | 89
39002.4422 | 1 | 0 | 89
39002.444 | 1 | 0 | 89
39002.4458 | 1 | 0 | 89
39002.4476 | 1 | 0 | 89
39002.4494 | 1 | 0 | 89
39002.4511 | 1 | 0 | 89
39002.4529 | 1 | 0 | 89
39002.4565 | 1 | 0 | 89
39002.4583 | 0 | 0 | 89
39002.46 | 1 | 0 | 89
39002.4618 | 1 | 0 | 89
39002.4636 | 1 | 0 | 89
39002.4654 | 1 | 0 | 89
39002.4672 | 1 | 0 | 89
39002.469 | 11 | 9 | 89
39002.4707 | 2127 | 0 | 89
39002.4725 | 2317 | 0 | 89
39002.4743 | 2289 | 1 | 89
39002.4761 | 1932 | 0 | 89
39002.4779 | 2136 | 2 | 89
39002.4797 | 2008 | 3 | 89
39002.4814 | 1848 | 524 | 89
39002.4832 | 2382 | 10 | 89
39002.485 | 2 | 0 | 89
89
39002.4351 | 1 | 0 | 90
39002.4369 | 1 | 0 | 90
39002.4387 | 1 | 0 | 90
39002.4405 | 1 | 0 | 90
39002.4422 | 1 | 0 | 90
39002.444 | 0 | 0 | 90
39002.4458 | 1 | 0 | 90
39002.4476 | 1 | 0 | 90
39002.4494 | 1 | 0 | 90
39002.4512 | 1 | 0 | 90
39002.4529 | 1 | 0 | 90
39002.4547 | 1 | 0 | 90
39002.4565 | 1 | 0 | 90
39002.4583 | 1 | 0 | 90
39002.4601 | 1 | 0 | 90
39002.4618 | 1 | 0 | 90
39002.4636 | 1 | 0 | 90
39002.4654 | 1 | 0 | 90
39002.4672 | 1 | 0 | 90
39002.469 | 50 | 49 | 90
39002.4708 | 2165 | 126 | 90
39002.4725 | 2101 | 0 | 90
39002.4743 | 2266 | 1 | 90
39002.4761 | 1915 | 1 | 90
39002.4779 | 1976 | 1 | 90
39002.4797 | 1994 | 4 | 90
39002.4814 | 1606 | 438 | 90
39002.4832 | 1890 | 7 | 90
39002.485 | 1 | 0 | 90
90
39002.4351 | 1 | 0 | 91
39002.4369 | 0 | 0 | 91
39002.4387 | 1 | 0 | 91
39002.4405 | 1 | 0 | 91
39002.4423 | 1 | 0 | 91
39002.444 | 1 | 0 | 91
39002.4458 | 1 | 0 | 91
39002.4476 | 1 | 0 | 91
39002.4494 | 1 | 0 | 91
39002.4512 | 1 | 0 | 91
39002.453 | 1 | 0 | 91
39002.4547 | 1 | 0 | 91
39002.4565 | 1 | 0 | 91
39002.4583 | 1 | 0 | 91
39002.4601 | 1 | 0 | 91
39002.4619 | 1 | 0 | 91
39002.4636 | 1 | 0 | 91
39002.4654 | 1 | 0 | 91
39002.4672 | 1 | 0 | 91
39002.469 | 5 | 4 | 91
39002.4708 | 2127 | 48 | 91
39002.4726 | 2521 | 0 | 91
39002.4743 | 2381 | 0 | 91
39002.4761 | 2039 | 0 | 91
39002.4779 | 2007 | 0 | 91
39002.4797 | 1929 | 4 | 91
39002.4815 | 1546 | 475 | 91
39002.4833 | 2121 | 8 | 91
39002.485 | 1 | 0 | 91
91
39002.4352 | 1 | 0 | 92
39002.4369 | 1 | 0 | 92
39002.4387 | 1 | 0 | 92
39002.4405 | 1 | 0 | 92
39002.4423 | 1 | 0 | 92
39002.4441 | 1 | 0 | 92
39002.4458 | 1 | 0 | 92
39002.4476 | 1 | 0 | 92
39002.4494 | 1 | 0 | 92
39002.4512 | 1 | 0 | 92
39002.453 | 1 | 0 | 92
39002.4547 | 1 | 0 | 92
39002.4565 | 1 | 0 | 92
39002.4583 | 1 | 0 | 92
39002.4601 | 1 | 0 | 92
39002.4619 | 0 | 0 | 92
39002.4637 | 0 | 0 | 92
39002.4654 | 1 | 0 | 92
39002.4672 | 1 | 0 | 92
39002.469 | 9 | 8 | 92
39002.4708 | 2409 | 0 | 92
39002.4726 | 2502 | 0 | 92
39002.4744 | 1925 | 0 | 92
39002.4761 | 2157 | 0 | 92
39002.4779 | 2004 | 0 | 92
39002.4797 | 2229 | 4 | 92
39002.4815 | 1671 | 627 | 92
39002.4833 | 1945 | 7 | 92
39002.485 | 1 | 0 | 92
92
39002.4352 | 1 | 0 | 93
39002.4369 | 1 | 0 | 93
39002.4405 | 1 | 0 | 93
39002.4423 | 1 | 0 | 93
39002.4441 | 1 | 0 | 93
39002.4459 | 1 | 0 | 93
39002.4476 | 1 | 0 | 93
39002.4494 | 1 | 0 | 93
39002.4512 | 1 | 0 | 93
39002.453 | 1 | 0 | 93
39002.4548 | 1 | 0 | 93
39002.4566 | 1 | 0 | 93
39002.4583 | 1 | 0 | 93
39002.4601 | 1 | 0 | 93
39002.4619 | 1 | 0 | 93
39002.4637 | 1 | 0 | 93
39002.4655 | 1 | 0 | 93
39002.4672 | 1 | 0 | 93
39002.469 | 32 | 30 | 93
39002.4708 | 2429 | 0 | 93
39002.4726 | 1949 | 0 | 93
39002.4744 | 2135 | 1 | 93
39002.4761 | 1967 | 1 | 93
39002.4779 | 1918 | 1 | 93
39002.4797 | 2065 | 4 | 93
39002.4815 | 1979 | 434 | 93
39002.4833 | 2092 | 7 | 93
39002.4851 | 1 | 0 | 93
93
39002.4352 | 1 | 0 | 94
39002.437 | 1 | 0 | 94
39002.4387 | 1 | 0 | 94
39002.4405 | 1 | 0 | 94
39002.4423 | 1 | 0 | 94
39002.4441 | 1 | 0 | 94
39002.4459 | 1 | 0 | 94
39002.4477 | 1 | 0 | 94
39002.4494 | 1 | 0 | 94
39002.4512 | 1 | 0 | 94
39002.453 | 1 | 0 | 94
39002.4548 | 1 | 0 | 94
39002.4566 | 1 | 0 | 94
39002.4583 | 1 | 0 | 94
39002.4601 | 1 | 0 | 94
39002.4619 | 1 | 0 | 94
39002.4637 | 1 | 0 | 94
39002.4655 | 1 | 0 | 94
39002.4673 | 1 | 0 | 94
39002.469 | 19 | 18 | 94
39002.4708 | 2380 | 0 | 94
39002.4726 | 2140 | 0 | 94
39002.4744 | 2246 | 1 | 94
39002.4762 | 2105 | 1 | 94
39002.478 | 2405 | 2 | 94
39002.4797 | 2207 | 5 | 94
39002.4815 | 1823 | 534 | 94
39002.4833 | 2422 | 7 | 94
39002.4851 | 0 | 0 | 94
94
39002.4352 | 0 | 0 | 95
39002.437 | 1 | 0 | 95
39002.4388 | 1 | 0 | 95
39002.4405 | 1 | 0 | 95
39002.4423 | 1 | 0 | 95
39002.4441 | 1 | 0 | 95
39002.4459 | 1 | 0 | 95
39002.4477 | 1 | 0 | 95
39002.4495 | 1 | 0 | 95
39002.4512 | 1 | 0 | 95
39002.453 | 0 | 0 | 95
39002.4548 | 1 | 0 | 95
39002.4566 | 1 | 0 | 95
39002.4584 | 1 | 0 | 95
39002.4601 | 1 | 0 | 95
39002.4619 | 1 | 0 | 95
39002.4637 | 1 | 0 | 95
39002.4655 | 1 | 0 | 95
39002.4673 | 1 | 0 | 95
39002.4691 | 26 | 19 | 95
39002.4708 | 1973 | 36 | 95
39002.4726 | 2033 | 0 | 95
39002.4744 | 2479 | 0 | 95
39002.4762 | 2438 | 1 | 95
39002.478 | 2003 | 1 | 95
39002.4797 | 2268 | 4 | 95
39002.4815 | 1759 | 628 | 95
39002.4833 | 2209 | 7 | 95
39002.4851 | 1 | 0 | 95
95
39002.4352 | 1 | 0 | 96
39002.437 | 1 | 0 | 96
39002.4388 | 1 | 0 | 96
39002.4406 | 1 | 0 | 96
39002.4423 | 1 | 0 | 96
39002.4441 | 1 | 0 | 96
39002.4459 | 1 | 0 | 96
39002.4477 | 1 | 0 | 96
39002.4495 | 1 | 0 | 96
39002.4512 | 1 | 0 | 96
39002.453 | 1 | 0 | 96
39002.4548 | 1 | 0 | 96
39002.4566 | 1 | 0 | 96
39002.4584 | 1 | 0 | 96
39002.4602 | 1 | 0 | 96
39002.4619 | 1 | 0 | 96
39002.4637 | 1 | 0 | 96
39002.4655 | 1 | 0 | 96
39002.4673 | 1 | 0 | 96
39002.4691 | 20 | 19 | 96
39002.4709 | 2250 | 7 | 96
39002.4726 | 1959 | 0 | 96
39002.4744 | 2327 | 0 | 96
39002.4762 | 2072 | 0 | 96
39002.478 | 2173 | 2 | 96
39002.4798 | 2185 | 4 | 96
39002.4816 | 1947 | 521 | 96
39002.4833 | 2450 | 6 | 96
39002.4851 | 1 | 0 | 96
96
39002.4352 | 1 | 0 | 97
39002.437 | 1 | 0 | 97
39002.4388 | 0 | 0 | 97
39002.4406 | 1 | 0 | 97
39002.4423 | 1 | 0 | 97
39002.4441 | 1 | 0 | 97
39002.4459 | 1 | 0 | 97
39002.4477 | 1 | 0 | 97
39002.4495 | 1 | 0 | 97
39002.4513 | 0 | 0 | 97
39002.453 | 1 | 0 | 97
39002.4548 | 1 | 0 | 97
39002.4566 | 1 | 0 | 97
39002.4584 | 1 | 0 | 97
39002.4602 | 1 | 0 | 97
39002.462 | 1 | 0 | 97
39002.4637 | 1 | 0 | 97
39002.4655 | 1 | 0 | 97
39002.4673 | 1 | 0 | 97
39002.4691 | 7 | 5 | 97
39002.4709 | 2349 | 18 | 97
39002.4727 | 2153 | 0 | 97
39002.4744 | 2477 | 0 | 97
39002.4762 | 2428 | 1 | 97
39002.478 | 2089 | 0 | 97
39002.4798 | 2125 | 4 | 97
39002.4816 | 1678 | 557 | 97
39002.4833 | 2219 | 7 | 97
39002.4851 | 1 | 0 | 97
97
39002.4352 | 1 | 0 | 98
39002.437 | 1 | 0 | 98
39002.4388 | 1 | 0 | 98
39002.4406 | 1 | 0 | 98
39002.4424 | 1 | 0 | 98
39002.4442 | 1 | 0 | 98
39002.4459 | 1 | 0 | 98
39002.4477 | 1 | 0 | 98
39002.4495 | 1 | 0 | 98
39002.4513 | 1 | 0 | 98
39002.4531 | 1 | 0 | 98
39002.4548 | 1 | 0 | 98
39002.4566 | 1 | 0 | 98
39002.4584 | 1 | 0 | 98
39002.4602 | 1 | 0 | 98
39002.462 | 1 | 0 | 98
39002.4638 | 1 | 0 | 98
39002.4655 | 1 | 0 | 98
39002.4673 | 1 | 0 | 98
39002.4691 | 9 | 9 | 98
39002.4709 | 2027 | 7 | 98
39002.4727 | 1986 | 0 | 98
39002.4744 | 1958 | 0 | 98
39002.4762 | 2119 | 1 | 98
39002.478 | 2305 | 1 | 98
39002.4798 | 2127 | 3 | 98
39002.4816 | 1856 | 491 | 98
39002.4834 | 2277 | 7 | 98
39002.4851 | 1 | 0 | 98
98
39002.4353 | 1 | 0 | 99
39002.437 | 1 | 0 | 99
39002.4388 | 1 | 0 | 99
39002.4406 | 1 | 0 | 99
39002.4424 | 1 | 0 | 99
39002.4442 | 1 | 0 | 99
39002.4459 | 1 | 0 | 99
39002.4477 | 1 | 0 | 99
39002.4495 | 1 | 0 | 99
39002.4513 | 0 | 0 | 99
39002.4531 | 1 | 0 | 99
39002.4549 | 1 | 0 | 99
39002.4566 | 1 | 0 | 99
39002.4584 | 1 | 0 | 99
39002.4602 | 1 | 0 | 99
39002.462 | 1 | 0 | 99
39002.4638 | 1 | 0 | 99
39002.4656 | 1 | 0 | 99
39002.4673 | 1 | 0 | 99
39002.4691 | 19 | 15 | 99
39002.4709 | 1982 | 30 | 99
39002.4727 | 2152 | 0 | 99
39002.4745 | 2298 | 0 | 99
39002.4762 | 1978 | 0 | 99
39002.478 | 2411 | 1 | 99
39002.4798 | 1960 | 4 | 99
39002.4816 | 2007 | 542 | 99
39002.4834 | 1991 | 6 | 99
39002.4852 | 1 | 0 | 99
99
39002.4353 | 1 | 0 | 100
39002.4371 | 1 | 0 | 100
39002.4388 | 1 | 0 | 100
39002.4406 | 1 | 0 | 100
39002.4424 | 0 | 0 | 100
39002.4442 | 1 | 0 | 100
39002.446 | 0 | 0 | 100
39002.4478 | 1 | 0 | 100
39002.4495 | 1 | 0 | 100
39002.4513 | 1 | 0 | 100
39002.4531 | 0 | 0 | 100
39002.4549 | 1 | 0 | 100
39002.4567 | 0 | 0 | 100
39002.4584 | 1 | 0 | 100
39002.4602 | 1 | 0 | 100
39002.462 | 1 | 0 | 100
39002.4638 | 1 | 0 | 100
39002.4656 | 1 | 0 | 100
39002.4673 | 1 | 0 | 100
39002.4691 | 43 | 39 | 100
39002.4709 | 2234 | 33 | 100
39002.4727 | 2472 | 0 | 100
39002.4745 | 2057 | 0 | 100
39002.4763 | 2180 | 0 | 100
39002.478 | 2053 | 0 | 100
39002.4798 | 2404 | 3 | 100
39002.4816 | 1849 | 566 | 100
39002.4834 | 2453 | 7 | 100
39002.4852 | 1 | 0 | 100
100
39002.4353 | 1 | 0 | 101
39002.4371 | 1 | 0 | 101
39002.4389 | 1 | 0 | 101
39002.4406 | 1 | 0 | 101
39002.4424 | 1 | 0 | 101
39002.4442 | 1 | 0 | 101
39002.446 | 1 | 0 | 101
39002.4478 | 1 | 0 | 101
39002.4495 | 1 | 0 | 101
39002.4513 | 1 | 0 | 101
39002.4531 | 1 | 0 | 101
39002.4549 | 1 | 0 | 101
39002.4567 | 1 | 0 | 101
39002.4585 | 0 | 0 | 101
39002.4602 | 1 | 0 | 101
39002.462 | 1 | 0 | 101
39002.4638 | 1 | 0 | 101
39002.4656 | 1 | 0 | 101
39002.4674 | 1 | 0 | 101
39002.4692 | 72 | 70 | 101
39002.4709 | 2126 | 1 | 101
39002.4727 | 2025 | 0 | 101
39002.4745 | 1922 | 0 | 101
39002.4763 | 2284 | 0 | 101
39002.4781 | 2436 | 0 | 101
39002.4798 | 1970 | 3 | 101
39002.4816 | 1850 | 669 | 101
39002.4834 | 2353 | 7 | 101
39002.4852 | 1 | 0 | 101
101
39002.4353 | 1 | 0 | 102
39002.4371 | 1 | 0 | 102
39002.4389 | 1 | 0 | 102
39002.4407 | 1 | 0 | 102
39002.4424 | 1 | 0 | 102
39002.4442 | 1 | 0 | 102
39002.446 | 1 | 0 | 102
39002.4478 | 1 | 0 | 102
39002.4496 | 1 | 0 | 102
39002.4513 | 1 | 0 | 102
39002.4531 | 1 | 0 | 102
39002.4549 | 1 | 0 | 102
39002.4567 | 1 | 0 | 102
39002.4585 | 1 | 0 | 102
39002.4603 | 1 | 0 | 102
39002.462 | 1 | 0 | 102
39002.4638 | 1 | 0 | 102
39002.4656 | 1 | 0 | 102
39002.4674 | 1 | 0 | 102
39002.4692 | 126 | 117 | 102
39002.4709 | 1851 | 0 | 102
39002.4727 | 2207 | 0 | 102
39002.4745 | 2050 | 0 | 102
39002.4763 | 2210 | 0 | 102
39002.4781 | 2422 | 0 | 102
39002.4799 | 2213 | 2 | 102
39002.4816 | 1570 | 647 | 102
39002.4834 | 1929 | 5 | 102
39002.4852 | 1 | 0 | 102
102
39002.4353 | 1 | 0 | 103
39002.4371 | 0 | 0 | 103
39002.4389 | 1 | 0 | 103
39002.4407 | 1 | 0 | 103
39002.4425 | 0 | 0 | 103
39002.4442 | 1 | 0 | 103
39002.446 | 1 | 0 | 103
39002.4478 | 0 | 0 | 103
39002.4496 | 1 | 0 | 103
39002.4514 | 1 | 0 | 103
39002.4531 | 1 | 0 | 103
39002.4549 | 0 | 0 | 103
39002.4567 | 1 | 0 | 103
39002.4585 | 1 | 0 | 103
39002.4603 | 1 | 0 | 103
39002.4621 | 0 | 0 | 103
39002.4638 | 1 | 0 | 103
39002.4656 | 1 | 0 | 103
39002.4674 | 1 | 0 | 103
39002.4692 | 110 | 103 | 103
39002.471 | 2287 | 0 | 103
39002.4727 | 2471 | 0 | 103
39002.4745 | 2371 | 0 | 103
39002.4763 | 2168 | 1 | 103
39002.4781 | 2002 | 1 | 103
39002.4799 | 2413 | 2 | 103
39002.4817 | 1639 | 620 | 103
39002.4834 | 2412 | 6 | 103
39002.4852 | 1 | 0 | 103
103
39002.4353 | 1 | 0 | 104
39002.4371 | 1 | 0 | 104
39002.4389 | 1 | 0 | 104
39002.4407 | 1 | 0 | 104
39002.4425 | 1 | 0 | 104
39002.4442 | 1 | 0 | 104
39002.446 | 1 | 0 | 104
39002.4478 | 1 | 0 | 104
39002.4496 | 1 | 0 | 104
39002.4514 | 1 | 0 | 104
39002.4532 | 1 | 0 | 104
39002.4549 | 1 | 0 | 104
39002.4567 | 1 | 0 | 104
39002.4585 | 1 | 0 | 104
39002.4603 | 1 | 0 | 104
39002.4621 | 1 | 0 | 104
39002.4639 | 1 | 0 | 104
39002.4656 | 1 | 0 | 104
39002.4674 | 1 | 0 | 104
39002.4692 | 106 | 100 | 104
39002.471 | 2005 | 1 | 104
39002.4728 | 2459 | 0 | 104
39002.4745 | 2423 | 0 | 104
39002.4763 | 2290 | 1 | 104
39002.4781 | 1886 | 0 | 104
39002.4799 | 1923 | 2 | 104
39002.4817 | 1727 | 718 | 104
39002.4835 | 1935 | 5 | 104
39002.4852 | 1 | 0 | 104
104
39002.4354 | 1 | 0 | 105
39002.4371 | 1 | 0 | 105
39002.4389 | 1 | 0 | 105
39002.4407 | 1 | 0 | 105
39002.4425 | 1 | 0 | 105
39002.4443 | 0 | 0 | 105
39002.4461 | 1 | 0 | 105
39002.4478 | 1 | 0 | 105
39002.4496 | 1 | 0 | 105
39002.4514 | 1 | 0 | 105
39002.4532 | 1 | 0 | 105
39002.455 | 1 | 0 | 105
39002.4567 | 1 | 0 | 105
39002.4585 | 1 | 0 | 105
39002.4603 | 1 | 0 | 105
39002.4621 | 1 | 0 | 105
39002.4639 | 1 | 0 | 105
39002.4656 | 1 | 0 | 105
39002.4674 | 1 | 0 | 105
39002.4692 | 168 | 159 | 105
39002.471 | 2285 | 0 | 105
39002.4728 | 2002 | 0 | 105
39002.4746 | 2450 | 0 | 105
39002.4763 | 2209 | 1 | 105
39002.4781 | 1973 | 1 | 105
39002.4799 | 2228 | 3 | 105
39002.4817 | 1922 | 600 | 105
39002.4835 | 2099 | 5 | 105
39002.4853 | 1 | 0 | 105
105
39002.4354 | 1 | 0 | 106
39002.4372 | 1 | 0 | 106
39002.4389 | 0 | 0 | 106
39002.4407 | 1 | 0 | 106
39002.4425 | 1 | 0 | 106
39002.4443 | 1 | 0 | 106
39002.4461 | 1 | 0 | 106
39002.4478 | 1 | 0 | 106
39002.4496 | 1 | 0 | 106
39002.4514 | 1 | 0 | 106
39002.4532 | 1 | 0 | 106
39002.455 | 1 | 0 | 106
39002.4568 | 1 | 0 | 106
39002.4585 | 1 | 0 | 106
39002.4603 | 1 | 0 | 106
39002.4621 | 1 | 0 | 106
39002.4639 | 1 | 0 | 106
39002.4657 | 1 | 0 | 106
39002.4675 | 1 | 0 | 106
39002.4692 | 656 | 685 | 106
39002.471 | 2202 | 1 | 106
39002.4728 | 2381 | 0 | 106
39002.4746 | 1896 | 0 | 106
39002.4764 | 2106 | 0 | 106
39002.4781 | 2126 | 1 | 106
39002.4799 | 2394 | 3 | 106
39002.4817 | 1555 | 657 | 106
39002.4835 | 2004 | 5 | 106
39002.4853 | 1 | 0 | 106
106
39002.4354 | 1 | 0 | 107
39002.4372 | 1 | 0 | 107
39002.439 | 1 | 0 | 107
39002.4407 | 1 | 0 | 107
39002.4425 | 0 | 0 | 107
39002.4443 | 1 | 0 | 107
39002.4461 | 1 | 0 | 107
39002.4479 | 1 | 0 | 107
39002.4496 | 1 | 0 | 107
39002.4514 | 1 | 0 | 107
39002.4532 | 1 | 0 | 107
39002.455 | 1 | 0 | 107
39002.4568 | 1 | 0 | 107
39002.4586 | 1 | 0 | 107
39002.4603 | 1 | 0 | 107
39002.4621 | 1 | 0 | 107
39002.4639 | 1 | 0 | 107
39002.4657 | 1 | 0 | 107
39002.4675 | 1 | 0 | 107
39002.4692 | 194 | 186 | 107
39002.471 | 1844 | 3 | 107
39002.4728 | 2084 | 0 | 107
39002.4746 | 2012 | 0 | 107
39002.4764 | 1913 | 0 | 107
39002.4782 | 2258 | 1 | 107
39002.4799 | 2201 | 3 | 107
39002.4817 | 1665 | 416 | 107
39002.4835 | 1903 | 5 | 107
39002.4853 | 1 | 0 | 107
107
39002.4354 | 1 | 0 | 108
39002.4372 | 1 | 0 | 108
39002.439 | 1 | 0 | 108
39002.4408 | 1 | 0 | 108
39002.4425 | 1 | 0 | 108
39002.4443 | 1 | 0 | 108
39002.4461 | 1 | 0 | 108
39002.4479 | 1 | 0 | 108
39002.4497 | 1 | 0 | 108
39002.4514 | 1 | 0 | 108
39002.4532 | 1 | 0 | 108
39002.455 | 1 | 0 | 108
39002.4568 | 1 | 0 | 108
39002.4586 | 1 | 0 | 108
39002.4604 | 1 | 0 | 108
39002.4621 | 1 | 0 | 108
39002.4639 | 1 | 0 | 108
39002.4657 | 1 | 0 | 108
39002.4675 | 1 | 0 | 108
39002.4693 | 268 | 264 | 108
39002.471 | 1726 | 2 | 108
39002.4728 | 2154 | 0 | 108
39002.4746 | 2202 | 0 | 108
39002.4764 | 2395 | 0 | 108
39002.4782 | 1953 | 1 | 108
39002.48 | 2014 | 2 | 108
39002.4817 | 1742 | 604 | 108
39002.4835 | 1961 | 5 | 108
39002.4853 | 1 | 0 | 108
108
39002.4354 | 1 | 0 | 109
39002.4372 | 1 | 0 | 109
39002.439 | 1 | 0 | 109
39002.4408 | 1 | 0 | 109
39002.4425 | 1 | 0 | 109
39002.4443 | 0 | 0 | 109
39002.4461 | 1 | 0 | 109
39002.4479 | 1 | 0 | 109
39002.4497 | 1 | 0 | 109
39002.4515 | 1 | 0 | 109
39002.4532 | 1 | 0 | 109
39002.455 | 1 | 0 | 109
39002.4568 | 1 | 0 | 109
39002.4586 | 1 | 0 | 109
39002.4604 | 1 | 0 | 109
39002.4622 | 1 | 0 | 109
39002.4639 | 1 | 0 | 109
39002.4657 | 1 | 0 | 109
39002.4675 | 1 | 0 | 109
39002.4693 | 230 | 243 | 109
39002.4711 | 2132 | 19 | 109
39002.4728 | 2273 | 0 | 109
39002.4746 | 2436 | 4 | 109
39002.4764 | 2048 | 19 | 109
39002.4782 | 2036 | 4 | 109
39002.48 | 2359 | 4 | 109
39002.4818 | 1562 | 790 | 109
39002.4835 | 2205 | 6 | 109
39002.4853 | 1 | 0 | 109
109
39002.4354 | 1 | 0 | 110
39002.4372 | 1 | 0 | 110
39002.439 | 1 | 0 | 110
39002.4408 | 1 | 0 | 110
39002.4426 | 1 | 0 | 110
39002.4444 | 1 | 0 | 110
39002.4461 | 1 | 0 | 110
39002.4479 | 1 | 0 | 110
39002.4497 | 1 | 0 | 110
39002.4515 | 1 | 0 | 110
39002.4533 | 1 | 0 | 110
39002.455 | 1 | 0 | 110
39002.4568 | 1 | 0 | 110
39002.4586 | 1 | 0 | 110
39002.4604 | 1 | 0 | 110
39002.4622 | 1 | 0 | 110
39002.4639 | 1 | 0 | 110
39002.4657 | 1 | 0 | 110
39002.4675 | 1 | 0 | 110
39002.4693 | 895 | 972 | 110
39002.4711 | 2163 | 3 | 110
39002.4729 | 2510 | 0 | 110
39002.4746 | 2429 | 3 | 110
39002.4764 | 2054 | 15 | 110
39002.4782 | 2243 | 5 | 110
39002.48 | 2007 | 5 | 110
39002.4818 | 1671 | 625 | 110
39002.4836 | 2143 | 5 | 110
39002.4853 | 0 | 0 | 110
110

## Temperatures
DAQ Time | Burner Time | Cable center | Air above cable | Air below cable | TRAY A
0 | -1700 | 15.6 | 15.1 | 15.4 | 16.6
1 | -1699 | 15.6 | 15.1 | 15.4 | 16.6
2 | -1698 | 15.6 | 15.1 | 15.4 | 16.6
3 | -1697 | 15.6 | 15.1 | 15.4 | 16.6
4 | -1696 | 15.6 | 15.1 | 15.4 | 16.6
5 | -1695 | 15.6 | 15.1 | 15.4 | 16.6
6 | -1694 | 15.6 | 15.1 | 15.4 | 16.6
7 | -1693 | 15.6 | 15.1 | 15.4 | 16.6
8 | -1692 | 15.6 | 15.1 | 15.4 | 16.6
9 | -1691 | 15.6 | 15.1 | 15.4 | 16.6
10 | -1690 | 15.6 | 15.1 | 15.4 | 16.6
11 | -1689 | 15.6 | 15.1 | 15.4 | 16.6
12.2 | -1687.8 | 15.6 | 15.1 | 15.4 | 16.6
13.2 | -1686.8 | 15.6 | 15.1 | 15.4 | 16.6
14.2 | -1685.8 | 15.6 | 15.1 | 15.4 | 16.6
15.2 | -1684.8 | 15.6 | 15.1 | 15.4 | 16.6
16.2 | -1683.8 | 15.6 | 15.1 | 15.4 | 16.6
17.2 | -1682.8 | 15.6 | 15.1 | 15.4 | 16.6
18.2 | -1681.8 | 15.6 | 15.1 | 15.4 | 16.6
19.2 | -1680.8 | 15.6 | 15.1 | 15.4 | 16.6
20.2 | -1679.8 | 15.6 | 15.1 | 15.4 | 16.6
21.2 | -1678.8 | 15.6 | 15.1 | 15.4 | 16.6
22.2 | -1677.8 | 15.6 | 15.1 | 15.4 | 16.6
23.2 | -1676.8 | 15.6 | 15.1 | 15.4 | 16.6
24.2 | -1675.8 | 15.6 | 15.1 | 15.4 | 16.6
25.2 | -1674.8 | 15.6 | 15.1 | 15.4 | 16.6
26.2 | -1673.8 | 15.6 | 15.1 | 15.4 | 16.6
27.2 | -1672.8 | 15.6 | 15.1 | 15.4 | 16.6
28.2 | -1671.8 | 15.6 | 15.1 | 15.4 | 16.6
29.2 | -1670.8 | 15.6 | 15.1 | 15.4 | 16.6
30.2 | -1669.8 | 15.6 | 15.1 | 15.4 | 16.6
31.2 | -1668.8 | 15.6 | 15.1 | 15.4 | 16.6
32.2 | -1667.8 | 15.6 | 15.1 | 15.4 | 16.6
33.2 | -1666.8 | 15.6 | 15.1 | 15.4 | 16.6
34.2 | -1665.8 | 15.6 | 15.1 | 15.4 | 16.6
35.2 | -1664.8 | 15.6 | 15.1 | 15.4 | 16.6
36.2 | -1663.8 | 15.6 | 15.1 | 15.4 | 16.6
37.2 | -1662.8 | 15.6 | 15.1 | 15.4 | 16.6
38.2 | -1661.8 | 15.6 | 15.1 | 15.4 | 16.6
39.2 | -1660.8 | 15.6 | 15.1 | 15.4 | 16.6
40.2 | -1659.8 | 15.6 | 15.1 | 15.4 | 16.6
41.2 | -1658.8 | 15.6 | 15.1 | 15.4 | 16.6
42.2 | -1657.8 | 15.6 | 15.1 | 15.4 | 16.6
43.2 | -1656.8 | 15.6 | 15.1 | 15.4 | 16.6
44.2 | -1655.8 | 15.6 | 15.1 | 15.4 | 16.6
45.2 | -1654.8 | 15.6 | 15.1 | 15.4 | 16.6
46.2 | -1653.8 | 15.6 | 15.1 | 15.4 | 16.6
47.2 | -1652.8 | 15.6 | 15.1 | 15.4 | 16.6
48.2 | -1651.8 | 15.6 | 15.1 | 15.4 | 16.6
49.2 | -1650.8 | 15.6 | 15.1 | 15.4 | 16.6
50.2 | -1649.8 | 15.6 | 15.1 | 15.4 | 16.6
51.2 | -1648.8 | 15.6 | 15.1 | 15.4 | 16.6
52.2 | -1647.8 | 15.6 | 15.1 | 15.4 | 16.6
53.2 | -1646.8 | 15.6 | 15.1 | 15.4 | 16.6
54.2 | -1645.8 | 15.7 | 15.1 | 15.4 | 16.6
55.2 | -1644.8 | 15.6 | 15.1 | 15.4 | 16.6
56.2 | -1643.8 | 15.7 | 15.1 | 15.4 | 16.6
57.2 | -1642.8 | 15.6 | 15.1 | 15.4 | 16.6
58.2 | -1641.8 | 15.6 | 15.1 | 15.4 | 16.6
59.2 | -1640.8 | 15.6 | 15.1 | 15.4 | 16.6
60.2 | -1639.8 | 15.6 | 15.1 | 15.4 | 16.6
61.2 | -1638.8 | 15.6 | 15.1 | 15.4 | 16.6
62.2 | -1637.8 | 15.6 | 15.1 | 15.4 | 16.6
63.2 | -1636.8 | 15.6 | 15.1 | 15.4 | 16.6
64.2 | -1635.8 | 15.6 | 15.1 | 15.4 | 16.6
65.2 | -1634.8 | 15.6 | 15.1 | 15.4 | 16.6
66.2 | -1633.8 | 15.6 | 15.1 | 15.4 | 16.6
67.2 | -1632.8 | 15.6 | 15.1 | 15.4 | 16.6
68.2 | -1631.8 | 15.7 | 15.1 | 15.4 | 16.6
69.2 | -1630.8 | 15.6 | 15.1 | 15.4 | 16.6
70.2 | -1629.8 | 15.7 | 15.1 | 15.4 | 16.6
71.2 | -1628.8 | 15.7 | 15.1 | 15.4 | 16.6
72.2 | -1627.8 | 15.6 | 15.1 | 15.4 | 16.6
73.2 | -1626.8 | 15.6 | 15.1 | 15.4 | 16.6
74.2 | -1625.8 | 15.7 | 15.1 | 15.4 | 16.6
75.2 | -1624.8 | 15.7 | 15.1 | 15.4 | 16.6
76.2 | -1623.8 | 15.7 | 15.1 | 15.4 | 16.6
77.2 | -1622.8 | 15.6 | 15.1 | 15.4 | 16.6
78.2 | -1621.8 | 15.7 | 15.1 | 15.4 | 16.6
79.2 | -1620.8 | 15.6 | 15.1 | 15.4 | 16.6
80.2 | -1619.8 | 15.6 | 15.1 | 15.4 | 16.6
81.2 | -1618.8 | 15.7 | 15.1 | 15.4 | 16.6
82.2 | -1617.8 | 15.7 | 15.1 | 15.4 | 16.6
83.2 | -1616.8 | 15.7 | 15.1 | 15.4 | 16.6
84.2 | -1615.8 | 15.7 | 15.1 | 15.4 | 16.6
85.2 | -1614.8 | 15.7 | 15.1 | 15.4 | 16.6
86.2 | -1613.8 | 15.7 | 15.1 | 15.4 | 16.6
87.2 | -1612.8 | 15.7 | 15.1 | 15.4 | 16.6
88.2 | -1611.8 | 15.7 | 15.1 | 15.4 | 16.6
89.2 | -1610.8 | 15.7 | 15.1 | 15.4 | 16.6
90.2 | -1609.8 | 15.6 | 15.1 | 15.4 | 16.6
91.2 | -1608.8 | 15.6 | 15.1 | 15.4 | 16.6
92.2 | -1607.8 | 15.6 | 15.1 | 15.4 | 16.6
93.2 | -1606.8 | 15.7 | 15.1 | 15.4 | 16.6
94.2 | -1605.8 | 15.7 | 15.1 | 15.4 | 16.6
95.2 | -1604.8 | 15.7 | 15.1 | 15.4 | 16.6
96.2 | -1603.8 | 15.7 | 15.1 | 15.4 | 16.6
97.2 | -1602.8 | 15.7 | 15.1 | 15.4 | 16.6
98.2 | -1601.8 | 15.7 | 15.1 | 15.4 | 16.6
99.2 | -1600.8 | 15.7 | 15.1 | 15.4 | 16.6
100.2 | -1599.8 | 15.6 | 15.1 | 15.4 | 16.6
101.2 | -1598.8 | 15.7 | 15.1 | 15.4 | 16.6
102.2 | -1597.8 | 15.7 | 15.1 | 15.4 | 16.6
103.2 | -1596.8 | 15.6 | 15.1 | 15.4 | 16.6
104.2 | -1595.8 | 15.7 | 15.1 | 15.4 | 16.6
105.2 | -1594.8 | 15.7 | 15.1 | 15.5 | 16.6
106.2 | -1593.8 | 15.7 | 15.1 | 15.4 | 16.6
107.2 | -1592.8 | 15.7 | 15.1 | 15.4 | 16.6
108.2 | -1591.8 | 15.7 | 15.1 | 15.4 | 16.6
109.2 | -1590.8 | 15.7 | 15.1 | 15.4 | 16.6
110.2 | -1589.8 | 15.7 | 15.1 | 15.4 | 16.6
111.2 | -1588.8 | 15.6 | 15.1 | 15.4 | 16.6
112.2 | -1587.8 | 15.6 | 15.1 | 15.4 | 16.6
113.2 | -1586.8 | 15.7 | 15.1 | 15.4 | 16.6
114.2 | -1585.8 | 15.6 | 15.1 | 15.4 | 16.6
115.2 | -1584.8 | 15.6 | 15.1 | 15.4 | 16.6
116.2 | -1583.8 | 15.6 | 15.1 | 15.4 | 16.6
117.2 | -1582.8 | 15.7 | 15.1 | 15.4 | 16.6
118.2 | -1581.8 | 15.7 | 15.1 | 15.4 | 16.6
119.2 | -1580.8 | 15.7 | 15.1 | 15.4 | 16.6
120.2 | -1579.8 | 15.7 | 15.1 | 15.4 | 16.6
121.2 | -1578.8 | 15.7 | 15.1 | 15.4 | 16.6
122.2 | -1577.8 | 15.7 | 15.1 | 15.4 | 16.6
123.2 | -1576.8 | 15.7 | 15.1 | 15.4 | 16.6
124.2 | -1575.8 | 15.7 | 15.1 | 15.4 | 16.6
125.2 | -1574.8 | 15.7 | 15.1 | 15.4 | 16.6
126.2 | -1573.8 | 15.7 | 15.1 | 15.4 | 16.6
127.2 | -1572.8 | 15.7 | 15.1 | 15.4 | 16.6
128.2 | -1571.8 | 15.7 | 15.1 | 15.4 | 16.6
129.2 | -1570.8 | 15.6 | 15.1 | 15.4 | 16.6
130.2 | -1569.8 | 15.7 | 15.1 | 15.4 | 16.6
131.2 | -1568.8 | 15.7 | 15.1 | 15.4 | 16.6
132.2 | -1567.8 | 15.7 | 15.1 | 15.4 | 16.6
133.2 | -1566.8 | 15.7 | 15.1 | 15.4 | 16.6
134.2 | -1565.8 | 15.7 | 15.1 | 15.4 | 16.6
135.2 | -1564.8 | 15.7 | 15.1 | 15.4 | 16.6
136.2 | -1563.8 | 15.6 | 15.1 | 15.4 | 16.6
137.2 | -1562.8 | 15.7 | 15.1 | 15.4 | 16.6
138.2 | -1561.8 | 15.7 | 15.1 | 15.4 | 16.6
139.2 | -1560.8 | 15.7 | 15.1 | 15.4 | 16.6
140.2 | -1559.8 | 15.7 | 15.1 | 15.4 | 16.6
141.2 | -1558.8 | 15.7 | 15.1 | 15.4 | 16.6
142.2 | -1557.8 | 15.7 | 15.1 | 15.4 | 16.6
143.2 | -1556.8 | 15.7 | 15.1 | 15.4 | 16.6
144.2 | -1555.8 | 15.7 | 15.1 | 15.4 | 16.6
145.2 | -1554.8 | 15.7 | 15.1 | 15.4 | 16.6
146.2 | -1553.8 | 15.7 | 15.1 | 15.4 | 16.6
147.2 | -1552.8 | 15.7 | 15.1 | 15.4 | 16.6
148.2 | -1551.8 | 15.7 | 15.1 | 15.4 | 16.6
149.2 | -1550.8 | 15.6 | 15.1 | 15.4 | 16.6
150.2 | -1549.8 | 15.7 | 15.1 | 15.4 | 16.6
151.2 | -1548.8 | 15.7 | 15.1 | 15.4 | 16.6
152.2 | -1547.8 | 15.7 | 15.1 | 15.4 | 16.6
153.2 | -1546.8 | 15.7 | 15.1 | 15.4 | 16.6
154.2 | -1545.8 | 15.6 | 15.1 | 15.4 | 16.6
155.2 | -1544.8 | 15.7 | 15.1 | 15.4 | 16.6
156.2 | -1543.8 | 15.6 | 15.1 | 15.4 | 16.6
157.2 | -1542.8 | 15.7 | 15.1 | 15.4 | 16.6
158.2 | -1541.8 | 15.7 | 15.1 | 15.4 | 16.6
159.2 | -1540.8 | 15.7 | 15.1 | 15.4 | 16.6
160.2 | -1539.8 | 15.7 | 15.1 | 15.4 | 16.6
161.2 | -1538.8 | 15.7 | 15.1 | 15.4 | 16.6
162.2 | -1537.8 | 15.7 | 15.1 | 15.4 | 16.6
163.2 | -1536.8 | 15.7 | 15.1 | 15.4 | 16.6
164.2 | -1535.8 | 15.7 | 15.1 | 15.4 | 16.6
165.2 | -1534.8 | 15.6 | 15.1 | 15.4 | 16.6
166.2 | -1533.8 | 15.6 | 15.1 | 15.4 | 16.6
167.2 | -1532.8 | 15.7 | 15.1 | 15.4 | 16.6
168.2 | -1531.8 | 15.6 | 15.1 | 15.4 | 16.6
169.2 | -1530.8 | 15.7 | 15.1 | 15.4 | 16.6
170.2 | -1529.8 | 15.6 | 15.1 | 15.4 | 16.6
171.2 | -1528.8 | 15.7 | 15.1 | 15.4 | 16.6
172.2 | -1527.8 | 15.7 | 15.1 | 15.4 | 16.6
173.2 | -1526.8 | 15.6 | 15.1 | 15.4 | 16.6
174.2 | -1525.8 | 15.6 | 15.1 | 15.4 | 16.6
175.2 | -1524.8 | 15.6 | 15.1 | 15.4 | 16.6
176.2 | -1523.8 | 15.7 | 15.1 | 15.4 | 16.6
177.2 | -1522.8 | 15.6 | 15.1 | 15.4 | 16.6
178.2 | -1521.8 | 15.7 | 15.1 | 15.4 | 16.6
179.2 | -1520.8 | 15.7 | 15.1 | 15.4 | 16.6
180.2 | -1519.8 | 15.7 | 15.1 | 15.4 | 16.6
181.2 | -1518.8 | 15.6 | 15.1 | 15.4 | 16.6
182.2 | -1517.8 | 15.6 | 15.1 | 15.4 | 16.6
183.2 | -1516.8 | 15.6 | 15.1 | 15.4 | 16.6
184.2 | -1515.8 | 15.6 | 15.1 | 15.4 | 16.6
185.2 | -1514.8 | 15.6 | 15.1 | 15.4 | 16.6
186.2 | -1513.8 | 15.6 | 15.1 | 15.4 | 16.6
187.2 | -1512.8 | 15.6 | 15.1 | 15.4 | 16.6
188.2 | -1511.8 | 15.6 | 15.1 | 15.4 | 16.6
189.2 | -1510.8 | 15.6 | 15.1 | 15.4 | 16.6
190.2 | -1509.8 | 15.7 | 15.1 | 15.4 | 16.6
191.2 | -1508.8 | 15.6 | 15.1 | 15.4 | 16.6
192.2 | -1507.8 | 15.7 | 15.1 | 15.4 | 16.6
193.2 | -1506.8 | 15.6 | 15.1 | 15.4 | 16.6
194.2 | -1505.8 | 15.6 | 15.1 | 15.4 | 16.6
195.2 | -1504.8 | 15.6 | 15.1 | 15.4 | 16.6
196.2 | -1503.8 | 15.6 | 15.1 | 15.4 | 16.6
197.2 | -1502.8 | 15.6 | 15.1 | 15.4 | 16.6
198.2 | -1501.8 | 15.7 | 15.1 | 15.4 | 16.6
199.2 | -1500.8 | 15.7 | 15.1 | 15.4 | 16.6
200.2 | -1499.8 | 15.7 | 15.1 | 15.4 | 16.6
201.2 | -1498.8 | 15.7 | 15.1 | 15.4 | 16.6
202.2 | -1497.8 | 15.7 | 15.1 | 15.4 | 16.6
203.2 | -1496.8 | 15.7 | 15.1 | 15.4 | 16.6
204.2 | -1495.8 | 15.7 | 15.1 | 15.4 | 16.6
205.2 | -1494.8 | 15.7 | 15.1 | 15.4 | 16.6
206.2 | -1493.8 | 15.7 | 15.1 | 15.4 | 16.6
207.2 | -1492.8 | 15.7 | 15.1 | 15.4 | 16.6
208.2 | -1491.8 | 15.7 | 15 | 15.4 | 16.6
209.2 | -1490.8 | 15.7 | 15.1 | 15.4 | 16.6
210.2 | -1489.8 | 15.7 | 15.1 | 15.4 | 16.6
211.2 | -1488.8 | 15.7 | 15.1 | 15.4 | 16.6
212.2 | -1487.8 | 15.7 | 15.1 | 15.4 | 16.6
213.2 | -1486.8 | 15.7 | 15.1 | 15.4 | 16.6
214.2 | -1485.8 | 15.7 | 15.1 | 15.4 | 16.6
215.2 | -1484.8 | 15.7 | 15.1 | 15.4 | 16.6
216.2 | -1483.8 | 15.7 | 15.1 | 15.4 | 16.6
217.2 | -1482.8 | 15.7 | 15.1 | 15.4 | 16.6
218.2 | -1481.8 | 15.7 | 15.1 | 15.4 | 16.6
219.2 | -1480.8 | 15.7 | 15.1 | 15.4 | 16.6
220.2 | -1479.8 | 15.7 | 15.1 | 15.4 | 16.6
221.2 | -1478.8 | 15.7 | 15.1 | 15.4 | 16.6
222.2 | -1477.8 | 15.7 | 15.1 | 15.4 | 16.6
223.2 | -1476.8 | 15.7 | 15.1 | 15.4 | 16.6
224.2 | -1475.8 | 15.7 | 15.1 | 15.4 | 16.6
225.2 | -1474.8 | 15.6 | 15.1 | 15.4 | 16.6
226.2 | -1473.8 | 15.7 | 15.1 | 15.4 | 16.6
227.2 | -1472.8 | 15.6 | 15.1 | 15.4 | 16.6
228.2 | -1471.8 | 15.7 | 15.1 | 15.4 | 16.6
229.2 | -1470.8 | 15.7 | 15.1 | 15.4 | 16.6
230.2 | -1469.8 | 15.7 | 15.1 | 15.4 | 16.6
231.2 | -1468.8 | 15.7 | 15.1 | 15.4 | 16.6
232.2 | -1467.8 | 15.7 | 15.1 | 15.4 | 16.6
233.2 | -1466.8 | 15.7 | 15.1 | 15.4 | 16.6
234.2 | -1465.8 | 15.7 | 15.1 | 15.4 | 16.6
235.2 | -1464.8 | 15.7 | 15.1 | 15.4 | 16.6
236.2 | -1463.8 | 15.7 | 15.1 | 15.4 | 16.6
237.2 | -1462.8 | 15.7 | 15.1 | 15.4 | 16.6
238.2 | -1461.8 | 15.7 | 15.1 | 15.4 | 16.6
239.2 | -1460.8 | 15.7 | 15.1 | 15.4 | 16.6
240.2 | -1459.8 | 15.7 | 15.1 | 15.4 | 16.6
241.2 | -1458.8 | 15.7 | 15.1 | 15.4 | 16.6
242.2 | -1457.8 | 15.7 | 15.1 | 15.4 | 16.6
243.2 | -1456.8 | 15.7 | 15.1 | 15.4 | 16.6
244.2 | -1455.8 | 15.7 | 15.1 | 15.4 | 16.6
245.2 | -1454.8 | 15.7 | 15.1 | 15.4 | 16.6
246.2 | -1453.8 | 15.7 | 15.1 | 15.4 | 16.6
247.2 | -1452.8 | 15.7 | 15.1 | 15.4 | 16.6
248.2 | -1451.8 | 15.7 | 15.1 | 15.4 | 16.6
249.2 | -1450.8 | 15.7 | 15.1 | 15.4 | 16.6
250.2 | -1449.8 | 15.7 | 15.1 | 15.4 | 16.6
251.2 | -1448.8 | 15.7 | 15.1 | 15.4 | 16.6
252.2 | -1447.8 | 15.7 | 15.1 | 15.4 | 16.6
253.2 | -1446.8 | 15.7 | 15.1 | 15.4 | 16.6
254.2 | -1445.8 | 15.7 | 15.1 | 15.4 | 16.6
255.2 | -1444.8 | 15.7 | 15.1 | 15.4 | 16.6
256.2 | -1443.8 | 15.7 | 15.1 | 15.4 | 16.6
257.2 | -1442.8 | 15.7 | 15.1 | 15.4 | 16.6
258.2 | -1441.8 | 15.7 | 15.1 | 15.4 | 16.6
259.2 | -1440.8 | 15.7 | 15.1 | 15.4 | 16.6
260.2 | -1439.8 | 15.7 | 15.1 | 15.4 | 16.6
261.2 | -1438.8 | 15.7 | 15.1 | 15.4 | 16.6
262.2 | -1437.8 | 15.7 | 15.1 | 15.4 | 16.6
263.2 | -1436.8 | 15.7 | 15.1 | 15.4 | 16.6
264.2 | -1435.8 | 15.7 | 15.1 | 15.4 | 16.6
265.2 | -1434.8 | 15.7 | 15.1 | 15.4 | 16.6
266.2 | -1433.8 | 15.7 | 15.1 | 15.4 | 16.6
267.2 | -1432.8 | 15.7 | 15.1 | 15.4 | 16.6
268.2 | -1431.8 | 15.7 | 15.1 | 15.4 | 16.6
269.2 | -1430.8 | 15.7 | 15.1 | 15.4 | 16.6
270.2 | -1429.8 | 15.7 | 15.1 | 15.4 | 16.6
271.2 | -1428.8 | 15.7 | 15.1 | 15.4 | 16.6
272.2 | -1427.8 | 15.7 | 15.1 | 15.4 | 16.6
273.2 | -1426.8 | 15.7 | 15.1 | 15.4 | 16.6
274.2 | -1425.8 | 15.7 | 15.1 | 15.4 | 16.6
275.2 | -1424.8 | 15.7 | 15.1 | 15.4 | 16.6
276.2 | -1423.8 | 15.7 | 15.1 | 15.4 | 16.6
277.2 | -1422.8 | 15.7 | 15.1 | 15.4 | 16.6
278.2 | -1421.8 | 15.7 | 15 | 15.4 | 16.6
279.2 | -1420.8 | 15.7 | 15.1 | 15.4 | 16.6
280.2 | -1419.8 | 15.7 | 15.1 | 15.4 | 16.6
281.2 | -1418.8 | 15.7 | 15.1 | 15.4 | 16.6
282.2 | -1417.8 | 15.7 | 15.1 | 15.4 | 16.6
283.2 | -1416.8 | 15.7 | 15.1 | 15.4 | 16.6
284.2 | -1415.8 | 15.7 | 15.1 | 15.4 | 16.6
285.2 | -1414.8 | 15.7 | 15.1 | 15.4 | 16.6
286.2 | -1413.8 | 15.7 | 15.1 | 15.4 | 16.6
287.2 | -1412.8 | 15.7 | 15.1 | 15.4 | 16.6
288.2 | -1411.8 | 15.7 | 15.1 | 15.4 | 16.6
289.2 | -1410.8 | 15.7 | 15.1 | 15.4 | 16.6
290.2 | -1409.8 | 15.7 | 15.1 | 15.4 | 16.6
291.2 | -1408.8 | 15.7 | 15.1 | 15.4 | 16.6
292.2 | -1407.8 | 15.7 | 15.1 | 15.4 | 16.6
293.2 | -1406.8 | 15.7 | 15.1 | 15.4 | 16.6
294.2 | -1405.8 | 15.7 | 15.1 | 15.4 | 16.6
295.2 | -1404.8 | 15.7 | 15.1 | 15.4 | 16.6
296.2 | -1403.8 | 15.7 | 15.1 | 15.4 | 16.6
297.2 | -1402.8 | 15.7 | 15.1 | 15.4 | 16.6
298.2 | -1401.8 | 15.7 | 15.1 | 15.4 | 16.6
299.2 | -1400.8 | 15.7 | 15.1 | 15.4 | 16.6
300.2 | -1399.8 | 15.7 | 15.1 | 15.4 | 16.6
301.2 | -1398.8 | 15.7 | 15.1 | 15.4 | 16.6
302.2 | -1397.8 | 15.7 | 15.1 | 15.4 | 16.6
303.2 | -1396.8 | 15.7 | 15.1 | 15.4 | 16.6
304.2 | -1395.8 | 15.7 | 15.1 | 15.4 | 16.6
305.2 | -1394.8 | 15.7 | 15.1 | 15.4 | 16.6
306.2 | -1393.8 | 15.7 | 15.1 | 15.4 | 16.6
307.2 | -1392.8 | 15.7 | 15.1 | 15.4 | 16.6
308.2 | -1391.8 | 15.7 | 15.1 | 15.4 | 16.6
309.2 | -1390.8 | 15.7 | 15.1 | 15.4 | 16.6
310.2 | -1389.8 | 15.7 | 15.1 | 15.4 | 16.6
311.2 | -1388.8 | 15.7 | 15.1 | 15.4 | 16.6
312.2 | -1387.8 | 15.7 | 15.1 | 15.4 | 16.6
313.2 | -1386.8 | 15.7 | 15.1 | 15.4 | 16.6
314.2 | -1385.8 | 15.7 | 15.1 | 15.4 | 16.6
315.2 | -1384.8 | 15.7 | 15.1 | 15.4 | 16.6
316.2 | -1383.8 | 15.7 | 15.1 | 15.4 | 16.6
317.2 | -1382.8 | 15.7 | 15.1 | 15.4 | 16.6
318.2 | -1381.8 | 15.7 | 15.1 | 15.4 | 16.6
319.2 | -1380.8 | 15.7 | 15.1 | 15.4 | 16.6
320.2 | -1379.8 | 15.7 | 15.1 | 15.4 | 16.6
321.2 | -1378.8 | 15.7 | 15.1 | 15.4 | 16.6
322.2 | -1377.8 | 15.7 | 15.1 | 15.4 | 16.6
323.2 | -1376.8 | 15.7 | 15.1 | 15.4 | 16.6
324.2 | -1375.8 | 15.7 | 15.1 | 15.4 | 16.6
325.2 | -1374.8 | 15.7 | 15.1 | 15.4 | 16.6
326.2 | -1373.8 | 15.7 | 15.1 | 15.4 | 16.6
327.2 | -1372.8 | 15.7 | 15.1 | 15.4 | 16.6
328.2 | -1371.8 | 15.7 | 15.1 | 15.4 | 16.6
329.2 | -1370.8 | 15.7 | 15.1 | 15.4 | 16.6
330.2 | -1369.8 | 15.7 | 15.1 | 15.4 | 16.6
331.2 | -1368.8 | 15.7 | 15.1 | 15.4 | 16.6
332.2 | -1367.8 | 15.7 | 15.1 | 15.4 | 16.6
333.2 | -1366.8 | 15.7 | 15.1 | 15.4 | 16.6
334.2 | -1365.8 | 15.7 | 15.1 | 15.4 | 16.6
335.2 | -1364.8 | 15.7 | 15.1 | 15.4 | 16.6
336.2 | -1363.8 | 15.7 | 15.1 | 15.4 | 16.6
337.2 | -1362.8 | 15.7 | 15.1 | 15.4 | 16.6
338.2 | -1361.8 | 15.7 | 15.1 | 15.4 | 16.6
339.2 | -1360.8 | 15.7 | 15.1 | 15.4 | 16.6
340.2 | -1359.8 | 15.7 | 15.1 | 15.4 | 16.6
341.2 | -1358.8 | 15.7 | 15.1 | 15.4 | 16.6
342.2 | -1357.8 | 15.7 | 15.1 | 15.4 | 16.6
343.2 | -1356.8 | 15.7 | 15.1 | 15.4 | 16.6
344.2 | -1355.8 | 15.7 | 15.1 | 15.4 | 16.6
345.2 | -1354.8 | 15.7 | 15.1 | 15.4 | 16.6
346.2 | -1353.8 | 15.7 | 15.1 | 15.4 | 16.6
347.2 | -1352.8 | 15.7 | 15.1 | 15.4 | 16.6
348.2 | -1351.8 | 15.7 | 15.1 | 15.4 | 16.6
349.2 | -1350.8 | 15.7 | 15.1 | 15.4 | 16.6
350.2 | -1349.8 | 15.7 | 15.1 | 15.4 | 16.6
351.2 | -1348.8 | 15.7 | 15.1 | 15.4 | 16.6
352.2 | -1347.8 | 15.7 | 15.1 | 15.4 | 16.6
353.2 | -1346.8 | 15.7 | 15.1 | 15.4 | 16.6
354.2 | -1345.8 | 15.7 | 15.1 | 15.4 | 16.6
355.2 | -1344.8 | 15.7 | 15.1 | 15.4 | 16.6
356.2 | -1343.8 | 15.7 | 15.1 | 15.4 | 16.6
357.2 | -1342.8 | 15.7 | 15.1 | 15.4 | 16.6
358.2 | -1341.8 | 15.7 | 15.1 | 15.4 | 16.6
359.2 | -1340.8 | 15.7 | 15.1 | 15.4 | 16.6
360.2 | -1339.8 | 15.7 | 15.1 | 15.4 | 16.6
361.2 | -1338.8 | 15.7 | 15.1 | 15.4 | 16.6
362.2 | -1337.8 | 15.7 | 15.1 | 15.4 | 16.6
363.2 | -1336.8 | 15.7 | 15.1 | 15.4 | 16.6
364.2 | -1335.8 | 15.7 | 15.1 | 15.4 | 16.6
365.2 | -1334.8 | 15.7 | 15.1 | 15.4 | 16.6
366.2 | -1333.8 | 15.7 | 15.1 | 15.4 | 16.6
367.2 | -1332.8 | 15.7 | 15.1 | 15.4 | 16.6
368.2 | -1331.8 | 15.7 | 15.1 | 15.4 | 16.6
369.2 | -1330.8 | 15.7 | 15.1 | 15.4 | 16.6
370.2 | -1329.8 | 15.7 | 15.1 | 15.4 | 16.6
371.2 | -1328.8 | 15.7 | 15.1 | 15.4 | 16.6
372.2 | -1327.8 | 15.7 | 15.1 | 15.4 | 16.6
373.2 | -1326.8 | 15.7 | 15.1 | 15.4 | 16.6
374.2 | -1325.8 | 15.7 | 15.1 | 15.4 | 16.6
375.2 | -1324.8 | 15.7 | 15.1 | 15.4 | 16.6
376.2 | -1323.8 | 15.7 | 15.1 | 15.4 | 16.6
377.2 | -1322.8 | 15.7 | 15.1 | 15.4 | 16.6
378.2 | -1321.8 | 15.7 | 15.1 | 15.4 | 16.6
379.2 | -1320.8 | 15.7 | 15.1 | 15.4 | 16.6
380.2 | -1319.8 | 15.7 | 15.1 | 15.4 | 16.6
381.2 | -1318.8 | 15.7 | 15.1 | 15.4 | 16.6
382.2 | -1317.8 | 15.7 | 15.1 | 15.4 | 16.6
383.2 | -1316.8 | 15.7 | 15.1 | 15.4 | 16.6
384.2 | -1315.8 | 15.7 | 15.1 | 15.4 | 16.6
385.2 | -1314.8 | 15.7 | 15.1 | 15.4 | 16.6
386.2 | -1313.8 | 15.7 | 15.1 | 15.4 | 16.6
387.2 | -1312.8 | 15.7 | 15.1 | 15.4 | 16.6
388.2 | -1311.8 | 15.7 | 15.1 | 15.4 | 16.6
389.2 | -1310.8 | 15.7 | 15.1 | 15.4 | 16.6
390.2 | -1309.8 | 15.7 | 15.1 | 15.4 | 16.6
391.2 | -1308.8 | 15.7 | 15.1 | 15.4 | 16.6
392.2 | -1307.8 | 15.7 | 15.1 | 15.4 | 16.6
393.2 | -1306.8 | 15.7 | 15.1 | 15.4 | 16.6
394.2 | -1305.8 | 15.7 | 15.1 | 15.4 | 16.6
395.2 | -1304.8 | 15.7 | 15.1 | 15.4 | 16.6
396.2 | -1303.8 | 15.7 | 15.1 | 15.4 | 16.6
397.2 | -1302.8 | 15.7 | 15.1 | 15.4 | 16.6
398.2 | -1301.8 | 15.7 | 15.1 | 15.4 | 16.6
399.2 | -1300.8 | 15.7 | 15.1 | 15.4 | 16.6
400.2 | -1299.8 | 15.7 | 15.1 | 15.4 | 16.6
401.2 | -1298.8 | 15.7 | 15.1 | 15.4 | 16.6
402.2 | -1297.8 | 15.7 | 15.1 | 15.4 | 16.6
403.2 | -1296.8 | 15.7 | 15.1 | 15.4 | 16.6
404.2 | -1295.8 | 15.7 | 15.1 | 15.4 | 16.6
405.2 | -1294.8 | 15.7 | 15.1 | 15.4 | 16.6
406.2 | -1293.8 | 15.7 | 15.1 | 15.4 | 16.6
407.2 | -1292.8 | 15.7 | 15.1 | 15.4 | 16.6
408.2 | -1291.8 | 15.7 | 15.1 | 15.4 | 16.6
409.2 | -1290.8 | 15.7 | 15.1 | 15.4 | 16.6
410.2 | -1289.8 | 15.7 | 15.1 | 15.4 | 16.6
411.2 | -1288.8 | 15.7 | 15.1 | 15.4 | 16.6
412.2 | -1287.8 | 15.7 | 15.1 | 15.4 | 16.6
413.2 | -1286.8 | 15.7 | 15.1 | 15.4 | 16.6
414.2 | -1285.8 | 15.7 | 15.1 | 15.4 | 16.6
415.2 | -1284.8 | 15.7 | 15.1 | 15.4 | 16.6
416.2 | -1283.8 | 15.7 | 15.1 | 15.4 | 16.6
417.2 | -1282.8 | 15.7 | 15.1 | 15.4 | 16.6
418.2 | -1281.8 | 15.7 | 15.1 | 15.4 | 16.6
419.2 | -1280.8 | 15.7 | 15.1 | 15.4 | 16.6
420.2 | -1279.8 | 15.7 | 15.1 | 15.4 | 16.6
421.2 | -1278.8 | 15.7 | 15.1 | 15.4 | 16.6
422.2 | -1277.8 | 15.7 | 15.1 | 15.4 | 16.6
423.2 | -1276.8 | 15.7 | 15.1 | 15.4 | 16.6
424.2 | -1275.8 | 15.7 | 15.1 | 15.4 | 16.6
425.2 | -1274.8 | 15.7 | 15.1 | 15.4 | 16.6
426.2 | -1273.8 | 15.7 | 15.1 | 15.4 | 16.6
427.2 | -1272.8 | 15.7 | 15.1 | 15.4 | 16.6
428.2 | -1271.8 | 15.7 | 15.1 | 15.4 | 16.6
429.2 | -1270.8 | 15.7 | 15.1 | 15.4 | 16.6
430.2 | -1269.8 | 15.7 | 15.1 | 15.4 | 16.6
431.2 | -1268.8 | 15.7 | 15.1 | 15.4 | 16.6
432.2 | -1267.8 | 15.7 | 15.1 | 15.4 | 16.6
433.2 | -1266.8 | 15.7 | 15.1 | 15.4 | 16.6
434.2 | -1265.8 | 15.7 | 15.1 | 15.4 | 16.6
435.2 | -1264.8 | 15.7 | 15.1 | 15.4 | 16.6
436.2 | -1263.8 | 15.7 | 15.1 | 15.4 | 16.6
437.2 | -1262.8 | 15.7 | 15.1 | 15.4 | 16.6
438.2 | -1261.8 | 15.7 | 15.1 | 15.4 | 16.6
439.2 | -1260.8 | 15.7 | 15.1 | 15.4 | 16.6
440.2 | -1259.8 | 15.7 | 15.1 | 15.4 | 16.6
441.2 | -1258.8 | 15.7 | 15.1 | 15.4 | 16.6
442.2 | -1257.8 | 15.7 | 15.1 | 15.4 | 16.6
443.2 | -1256.8 | 15.7 | 15.1 | 15.4 | 16.6
444.2 | -1255.8 | 15.7 | 15.1 | 15.4 | 16.6
445.2 | -1254.8 | 15.7 | 15.1 | 15.4 | 16.6
446.2 | -1253.8 | 15.7 | 15.1 | 15.4 | 16.6
447.2 | -1252.8 | 15.7 | 15.1 | 15.4 | 16.6
448.2 | -1251.8 | 15.7 | 15.1 | 15.4 | 16.6
449.2 | -1250.8 | 15.7 | 15.1 | 15.4 | 16.6
450.2 | -1249.8 | 15.7 | 15.1 | 15.4 | 16.6
451.2 | -1248.8 | 15.7 | 15.1 | 15.4 | 16.6
452.2 | -1247.8 | 15.7 | 15.1 | 15.5 | 16.6
453.2 | -1246.8 | 15.7 | 15.1 | 15.4 | 16.6
454.2 | -1245.8 | 15.7 | 15.1 | 15.5 | 16.6
455.2 | -1244.8 | 15.7 | 15.1 | 15.4 | 16.6
456.2 | -1243.8 | 15.7 | 15.1 | 15.4 | 16.6
457.2 | -1242.8 | 15.7 | 15.1 | 15.5 | 16.6
458.2 | -1241.8 | 15.7 | 15.1 | 15.5 | 16.6
459.2 | -1240.8 | 15.7 | 15.1 | 15.4 | 16.6
460.2 | -1239.8 | 15.7 | 15.1 | 15.5 | 16.6
461.2 | -1238.8 | 15.7 | 15.1 | 15.5 | 16.6
462.2 | -1237.8 | 15.7 | 15.1 | 15.5 | 16.6
463.2 | -1236.8 | 15.7 | 15.1 | 15.4 | 16.6
464.2 | -1235.8 | 15.7 | 15.1 | 15.4 | 16.6
465.2 | -1234.8 | 15.7 | 15.1 | 15.4 | 16.6
466.2 | -1233.8 | 15.7 | 15.1 | 15.4 | 16.6
467.2 | -1232.8 | 15.7 | 15.1 | 15.4 | 16.6
468.2 | -1231.8 | 15.7 | 15.1 | 15.5 | 16.6
469.2 | -1230.8 | 15.7 | 15.1 | 15.4 | 16.6
470.2 | -1229.8 | 15.7 | 15.1 | 15.5 | 16.6
471.2 | -1228.8 | 15.7 | 15.1 | 15.4 | 16.6
472.2 | -1227.8 | 15.7 | 15.1 | 15.4 | 16.6
473.2 | -1226.8 | 15.7 | 15.1 | 15.4 | 16.6
474.2 | -1225.8 | 15.7 | 15.1 | 15.5 | 16.6
475.2 | -1224.8 | 15.7 | 15.1 | 15.5 | 16.6
476.2 | -1223.8 | 15.7 | 15.1 | 15.4 | 16.6
477.2 | -1222.8 | 15.7 | 15.1 | 15.4 | 16.6
478.2 | -1221.8 | 15.7 | 15.1 | 15.5 | 16.6
479.2 | -1220.8 | 15.7 | 15.1 | 15.5 | 16.6
480.2 | -1219.8 | 15.7 | 15.1 | 15.4 | 16.6
481.2 | -1218.8 | 15.7 | 15.1 | 15.4 | 16.6
482.2 | -1217.8 | 15.7 | 15.1 | 15.4 | 16.6
483.2 | -1216.8 | 15.7 | 15.1 | 15.5 | 16.6
484.2 | -1215.8 | 15.7 | 15.1 | 15.4 | 16.6
485.2 | -1214.8 | 15.7 | 15.1 | 15.4 | 16.6
486.2 | -1213.8 | 15.7 | 15.1 | 15.4 | 16.6
487.2 | -1212.8 | 15.7 | 15.1 | 15.4 | 16.6
488.2 | -1211.8 | 15.7 | 15.1 | 15.4 | 16.6
489.2 | -1210.8 | 15.7 | 15.1 | 15.4 | 16.6
490.2 | -1209.8 | 15.7 | 15.1 | 15.4 | 16.6
491.2 | -1208.8 | 15.7 | 15.1 | 15.4 | 16.6
492.2 | -1207.8 | 15.7 | 15.1 | 15.4 | 16.6
493.2 | -1206.8 | 15.7 | 15.1 | 15.4 | 16.6
494.2 | -1205.8 | 15.7 | 15.1 | 15.4 | 16.6
495.2 | -1204.8 | 15.7 | 15.1 | 15.4 | 16.6
496.2 | -1203.8 | 15.7 | 15.1 | 15.4 | 16.6
497.2 | -1202.8 | 15.7 | 15.1 | 15.4 | 16.6
498.2 | -1201.8 | 15.7 | 15.1 | 15.4 | 16.6
499.2 | -1200.8 | 15.7 | 15.1 | 15.4 | 16.6
500.2 | -1199.8 | 15.7 | 15.1 | 15.4 | 16.6
501.2 | -1198.8 | 15.7 | 15.1 | 15.4 | 16.6
502.2 | -1197.8 | 15.7 | 15.1 | 15.4 | 16.6
503.2 | -1196.8 | 15.7 | 15.1 | 15.4 | 16.6
504.2 | -1195.8 | 15.7 | 15.1 | 15.4 | 16.6
505.2 | -1194.8 | 15.7 | 15.1 | 15.4 | 16.6
506.2 | -1193.8 | 15.7 | 15.1 | 15.4 | 16.6
507.2 | -1192.8 | 15.7 | 15.1 | 15.4 | 16.6
508.2 | -1191.8 | 15.7 | 15.1 | 15.4 | 16.6
509.2 | -1190.8 | 15.7 | 15.1 | 15.4 | 16.6
510.2 | -1189.8 | 15.7 | 15.1 | 15.4 | 16.6
511.2 | -1188.8 | 15.7 | 15.1 | 15.4 | 16.6
512.2 | -1187.8 | 15.7 | 15.1 | 15.4 | 16.6
513.2 | -1186.8 | 15.7 | 15.1 | 15.4 | 16.6
514.2 | -1185.8 | 15.7 | 15.1 | 15.4 | 16.6
515.2 | -1184.8 | 15.7 | 15.1 | 15.4 | 16.6
516.2 | -1183.8 | 15.7 | 15.1 | 15.4 | 16.6
517.2 | -1182.8 | 15.7 | 15.1 | 15.4 | 16.6
518.2 | -1181.8 | 15.7 | 15.1 | 15.4 | 16.6
519.2 | -1180.8 | 15.7 | 15.1 | 15.4 | 16.6
520.2 | -1179.8 | 15.7 | 15.1 | 15.4 | 16.6
521.2 | -1178.8 | 15.7 | 15.1 | 15.4 | 16.6
522.2 | -1177.8 | 15.7 | 15.1 | 15.4 | 16.6
523.2 | -1176.8 | 15.7 | 15.1 | 15.4 | 16.6
524.2 | -1175.8 | 15.7 | 15.1 | 15.4 | 16.6
525.2 | -1174.8 | 15.7 | 15.1 | 15.4 | 16.6
526.2 | -1173.8 | 15.7 | 15.1 | 15.4 | 16.6
527.2 | -1172.8 | 15.7 | 15.1 | 15.4 | 16.6
528.2 | -1171.8 | 15.7 | 15.1 | 15.4 | 16.6
529.2 | -1170.8 | 15.7 | 15.1 | 15.4 | 16.6
530.2 | -1169.8 | 15.7 | 15.1 | 15.4 | 16.6
531.2 | -1168.8 | 15.7 | 15.1 | 15.4 | 16.6
532.2 | -1167.8 | 15.7 | 15.1 | 15.4 | 16.6
533.2 | -1166.8 | 15.7 | 15.1 | 15.4 | 16.6
534.2 | -1165.8 | 15.7 | 15.1 | 15.4 | 16.6
535.2 | -1164.8 | 15.7 | 15.1 | 15.4 | 16.6
536.2 | -1163.8 | 15.7 | 15.1 | 15.4 | 16.6
537.2 | -1162.8 | 15.7 | 15.1 | 15.4 | 16.6
538.2 | -1161.8 | 15.7 | 15.1 | 15.4 | 16.6
539.2 | -1160.8 | 15.7 | 15.1 | 15.4 | 16.6
540.2 | -1159.8 | 15.7 | 15.1 | 15.4 | 16.6
541.2 | -1158.8 | 15.7 | 15.1 | 15.4 | 16.6
542.2 | -1157.8 | 15.7 | 15.1 | 15.4 | 16.6
543.2 | -1156.8 | 15.7 | 15.1 | 15.4 | 16.6
544.2 | -1155.8 | 15.7 | 15.1 | 15.4 | 16.6
545.2 | -1154.8 | 15.7 | 15.1 | 15.4 | 16.6
546.2 | -1153.8 | 15.7 | 15.1 | 15.4 | 16.6
547.2 | -1152.8 | 15.7 | 15.1 | 15.4 | 16.6
548.2 | -1151.8 | 15.7 | 15.1 | 15.4 | 16.6
549.2 | -1150.8 | 15.7 | 15.1 | 15.4 | 16.6
550.2 | -1149.8 | 15.7 | 15.1 | 15.4 | 16.6
551.2 | -1148.8 | 15.7 | 15.1 | 15.4 | 16.6
552.2 | -1147.8 | 15.7 | 15.1 | 15.4 | 16.6
553.2 | -1146.8 | 15.7 | 15.1 | 15.4 | 16.6
554.2 | -1145.8 | 15.7 | 15.1 | 15.4 | 16.6
555.2 | -1144.8 | 15.7 | 15.1 | 15.4 | 16.6
556.2 | -1143.8 | 15.7 | 15.1 | 15.4 | 16.6
557.2 | -1142.8 | 15.7 | 15.1 | 15.4 | 16.6
558.2 | -1141.8 | 15.7 | 15.1 | 15.4 | 16.6
559.2 | -1140.8 | 15.7 | 15.1 | 15.4 | 16.6
560.2 | -1139.8 | 15.7 | 15.1 | 15.4 | 16.6
561.2 | -1138.8 | 15.7 | 15.1 | 15.4 | 16.6
562.2 | -1137.8 | 15.7 | 15.1 | 15.4 | 16.6
563.2 | -1136.8 | 15.7 | 15.1 | 15.4 | 16.6
564.2 | -1135.8 | 15.7 | 15.1 | 15.4 | 16.6
565.2 | -1134.8 | 15.7 | 15.1 | 15.5 | 16.6
566.2 | -1133.8 | 15.7 | 15.1 | 15.4 | 16.6
567.2 | -1132.8 | 15.7 | 15.1 | 15.4 | 16.6
568.2 | -1131.8 | 15.7 | 15.1 | 15.4 | 16.6
569.2 | -1130.8 | 15.7 | 15.1 | 15.5 | 16.6
570.2 | -1129.8 | 15.7 | 15.1 | 15.5 | 16.6
571.2 | -1128.8 | 15.7 | 15.1 | 15.4 | 16.6
572.2 | -1127.8 | 15.7 | 15.1 | 15.4 | 16.6
573.2 | -1126.8 | 15.7 | 15.1 | 15.5 | 16.6
574.2 | -1125.8 | 15.7 | 15.1 | 15.5 | 16.6
575.2 | -1124.8 | 15.7 | 15.1 | 15.4 | 16.6
576.2 | -1123.8 | 15.7 | 15.1 | 15.5 | 16.6
577.2 | -1122.8 | 15.7 | 15.1 | 15.5 | 16.6
578.2 | -1121.8 | 15.7 | 15.1 | 15.5 | 16.6
579.2 | -1120.8 | 15.7 | 15.1 | 15.5 | 16.6
580.2 | -1119.8 | 15.7 | 15.1 | 15.5 | 16.6
581.2 | -1118.8 | 15.7 | 15.1 | 15.5 | 16.6
582.2 | -1117.8 | 15.7 | 15.1 | 15.5 | 16.6
583.2 | -1116.8 | 15.7 | 15.1 | 15.5 | 16.6
584.2 | -1115.8 | 15.7 | 15.1 | 15.4 | 16.6
585.2 | -1114.8 | 15.7 | 15.1 | 15.5 | 16.6
586.2 | -1113.8 | 15.7 | 15.1 | 15.4 | 16.6
587.2 | -1112.8 | 15.7 | 15.1 | 15.5 | 16.6
588.2 | -1111.8 | 15.7 | 15.1 | 15.5 | 16.6
589.2 | -1110.8 | 15.7 | 15.1 | 15.5 | 16.6
590.2 | -1109.8 | 15.7 | 15.1 | 15.5 | 16.6
591.2 | -1108.8 | 15.7 | 15.1 | 15.5 | 16.6
592.2 | -1107.8 | 15.7 | 15.1 | 15.5 | 16.6
593.2 | -1106.8 | 15.7 | 15.1 | 15.5 | 16.6
594.2 | -1105.8 | 15.7 | 15.1 | 15.5 | 16.6
595.2 | -1104.8 | 15.7 | 15.1 | 15.5 | 16.6
596.2 | -1103.8 | 15.7 | 15.1 | 15.5 | 16.6
597.2 | -1102.8 | 15.7 | 15.1 | 15.5 | 16.6
598.2 | -1101.8 | 15.7 | 15.1 | 15.5 | 16.6
599.2 | -1100.8 | 15.7 | 15.1 | 15.5 | 16.6
600.2 | -1099.8 | 15.7 | 15.1 | 15.5 | 16.6
601.2 | -1098.8 | 15.7 | 15.1 | 15.5 | 16.6
602.2 | -1097.8 | 15.7 | 15.1 | 15.5 | 16.6
603.2 | -1096.8 | 15.7 | 15.1 | 15.5 | 16.6
604.2 | -1095.8 | 15.7 | 15.1 | 15.5 | 16.6
605.2 | -1094.8 | 15.7 | 15.1 | 15.5 | 16.6
606.2 | -1093.8 | 15.7 | 15.1 | 15.5 | 16.6
607.2 | -1092.8 | 15.7 | 15.1 | 15.5 | 16.6
608.2 | -1091.8 | 15.7 | 15.1 | 15.5 | 16.6
609.2 | -1090.8 | 15.7 | 15.1 | 15.5 | 16.6
610.2 | -1089.8 | 15.7 | 15.1 | 15.5 | 16.6
611.2 | -1088.8 | 15.7 | 15.1 | 15.5 | 16.6
612.2 | -1087.8 | 15.7 | 15.1 | 15.5 | 16.6
613.2 | -1086.8 | 15.7 | 15.1 | 15.5 | 16.6
614.2 | -1085.8 | 15.7 | 15.1 | 15.5 | 16.6
615.2 | -1084.8 | 15.7 | 15.1 | 15.5 | 16.6
616.2 | -1083.8 | 15.7 | 15.1 | 15.5 | 16.6
617.2 | -1082.8 | 15.7 | 15.1 | 15.5 | 16.6
618.2 | -1081.8 | 15.7 | 15.1 | 15.5 | 16.6
619.2 | -1080.8 | 15.7 | 15.1 | 15.5 | 16.6
620.2 | -1079.8 | 15.7 | 15.1 | 15.5 | 16.6
621.2 | -1078.8 | 15.7 | 15.1 | 15.5 | 16.6
622.2 | -1077.8 | 15.7 | 15.1 | 15.5 | 16.6
623.2 | -1076.8 | 15.7 | 15.1 | 15.5 | 16.6
624.2 | -1075.8 | 15.7 | 15.1 | 15.5 | 16.6
625.2 | -1074.8 | 15.7 | 15.1 | 15.5 | 16.6
626.2 | -1073.8 | 15.7 | 15.1 | 15.5 | 16.6
627.2 | -1072.8 | 15.7 | 15.1 | 15.5 | 16.6
628.2 | -1071.8 | 15.7 | 15.1 | 15.5 | 16.6
629.2 | -1070.8 | 15.7 | 15.1 | 15.5 | 16.6
630.2 | -1069.8 | 15.7 | 15.1 | 15.5 | 16.6
631.2 | -1068.8 | 15.7 | 15.1 | 15.5 | 16.6
632.2 | -1067.8 | 15.7 | 15.1 | 15.5 | 16.6
633.2 | -1066.8 | 15.7 | 15.1 | 15.5 | 16.6
634.2 | -1065.8 | 15.7 | 15.1 | 15.5 | 16.6
635.2 | -1064.8 | 15.7 | 15.1 | 15.5 | 16.6
636.2 | -1063.8 | 15.7 | 15.1 | 15.5 | 16.6
637.2 | -1062.8 | 15.7 | 15.1 | 15.5 | 16.6
638.2 | -1061.8 | 15.7 | 15.1 | 15.5 | 16.6
639.2 | -1060.8 | 15.7 | 15.1 | 15.5 | 16.6
640.2 | -1059.8 | 15.7 | 15.1 | 15.5 | 16.6
641.2 | -1058.8 | 15.7 | 15.1 | 15.5 | 16.6
642.2 | -1057.8 | 15.7 | 15.1 | 15.5 | 16.6
643.2 | -1056.8 | 15.7 | 15.1 | 15.5 | 16.6
644.2 | -1055.8 | 15.7 | 15.1 | 15.5 | 16.6
645.2 | -1054.8 | 15.7 | 15.1 | 15.5 | 16.6
646.2 | -1053.8 | 15.7 | 15.1 | 15.5 | 16.6
647.2 | -1052.8 | 15.7 | 15.1 | 15.5 | 16.6
648.2 | -1051.8 | 15.7 | 15.1 | 15.5 | 16.6
649.2 | -1050.8 | 15.7 | 15.1 | 15.5 | 16.6
650.2 | -1049.8 | 15.7 | 15.1 | 15.5 | 16.6
651.2 | -1048.8 | 15.7 | 15.1 | 15.5 | 16.6
652.2 | -1047.8 | 15.7 | 15.1 | 15.5 | 16.6
653.2 | -1046.8 | 15.7 | 15.1 | 15.4 | 16.6
654.2 | -1045.8 | 15.7 | 15.1 | 15.4 | 16.6
655.2 | -1044.8 | 15.7 | 15.1 | 15.4 | 16.6
656.2 | -1043.8 | 15.7 | 15.1 | 15.4 | 16.6
657.2 | -1042.8 | 15.7 | 15.1 | 15.4 | 16.6
658.2 | -1041.8 | 15.7 | 15.1 | 15.5 | 16.6
659.2 | -1040.8 | 15.7 | 15.1 | 15.4 | 16.6
660.2 | -1039.8 | 15.7 | 15.1 | 15.4 | 16.6
661.2 | -1038.8 | 15.7 | 15.1 | 15.4 | 16.6
662.2 | -1037.8 | 15.7 | 15.1 | 15.4 | 16.6
663.2 | -1036.8 | 15.7 | 15.1 | 15.4 | 16.6
664.2 | -1035.8 | 15.7 | 15.1 | 15.4 | 16.6
665.2 | -1034.8 | 15.7 | 15.1 | 15.4 | 16.6
666.2 | -1033.8 | 15.7 | 15.1 | 15.4 | 16.6
667.2 | -1032.8 | 15.7 | 15.1 | 15.4 | 16.6
668.2 | -1031.8 | 15.7 | 15.1 | 15.4 | 16.6
669.2 | -1030.8 | 15.7 | 15.1 | 15.4 | 16.6
670.2 | -1029.8 | 15.7 | 15.1 | 15.4 | 16.6
671.2 | -1028.8 | 15.7 | 15.1 | 15.4 | 16.6
672.2 | -1027.8 | 15.7 | 15.1 | 15.4 | 16.6
673.2 | -1026.8 | 15.7 | 15.1 | 15.4 | 16.6
674.2 | -1025.8 | 15.7 | 15.1 | 15.4 | 16.6
675.2 | -1024.8 | 15.7 | 15.1 | 15.4 | 16.6
676.2 | -1023.8 | 15.7 | 15.1 | 15.4 | 16.6
677.2 | -1022.8 | 15.7 | 15.1 | 15.4 | 16.6
678.2 | -1021.8 | 15.7 | 15.1 | 15.4 | 16.6
679.2 | -1020.8 | 15.7 | 15.1 | 15.4 | 16.6
680.2 | -1019.8 | 15.7 | 15.1 | 15.4 | 16.6
681.2 | -1018.8 | 15.7 | 15.1 | 15.4 | 16.6
682.2 | -1017.8 | 15.7 | 15.1 | 15.4 | 16.6
683.2 | -1016.8 | 15.7 | 15.1 | 15.4 | 16.6
684.2 | -1015.8 | 15.7 | 15.1 | 15.4 | 16.6
685.2 | -1014.8 | 15.7 | 15.1 | 15.5 | 16.6
686.2 | -1013.8 | 15.7 | 15.1 | 15.5 | 16.6
687.2 | -1012.8 | 15.7 | 15.1 | 15.5 | 16.6
688.2 | -1011.8 | 15.7 | 15.1 | 15.5 | 16.6
689.2 | -1010.8 | 15.7 | 15.1 | 15.5 | 16.6
690.2 | -1009.8 | 15.7 | 15.1 | 15.5 | 16.6
691.2 | -1008.8 | 15.7 | 15.1 | 15.5 | 16.6
692.2 | -1007.8 | 15.7 | 15.1 | 15.5 | 16.6
693.2 | -1006.8 | 15.7 | 15.1 | 15.5 | 16.6
694.2 | -1005.8 | 15.7 | 15.1 | 15.5 | 16.6
695.2 | -1004.8 | 15.7 | 15.1 | 15.5 | 16.6
696.2 | -1003.8 | 15.7 | 15.1 | 15.5 | 16.6
697.2 | -1002.8 | 15.7 | 15.1 | 15.5 | 16.6
698.2 | -1001.8 | 15.7 | 15.1 | 15.5 | 16.6
699.2 | -1000.8 | 15.7 | 15.1 | 15.5 | 16.6
700.2 | -999.8 | 15.7 | 15.1 | 15.5 | 16.6
701.2 | -998.8 | 15.7 | 15.1 | 15.5 | 16.6
702.2 | -997.8 | 15.7 | 15.2 | 15.5 | 16.6
703.2 | -996.8 | 15.7 | 15.1 | 15.5 | 16.6
704.2 | -995.8 | 15.7 | 15.1 | 15.5 | 16.6
705.2 | -994.8 | 15.7 | 15.1 | 15.5 | 16.6
706.2 | -993.8 | 15.7 | 15.1 | 15.5 | 16.6
707.2 | -992.8 | 15.7 | 15.1 | 15.5 | 16.6
708.2 | -991.8 | 15.7 | 15.1 | 15.5 | 16.6
709.2 | -990.8 | 15.7 | 15.1 | 15.5 | 16.6
710.2 | -989.8 | 15.7 | 15.1 | 15.5 | 16.6
711.2 | -988.8 | 15.7 | 15.1 | 15.5 | 16.6
712.2 | -987.8 | 15.7 | 15.1 | 15.5 | 16.6
713.2 | -986.8 | 15.7 | 15.1 | 15.5 | 16.6
714.2 | -985.8 | 15.7 | 15.1 | 15.5 | 16.6
715.2 | -984.8 | 15.7 | 15.1 | 15.5 | 16.6
716.2 | -983.8 | 15.7 | 15.1 | 15.5 | 16.6
717.2 | -982.8 | 15.7 | 15.2 | 15.5 | 16.6
718.2 | -981.8 | 15.7 | 15.1 | 15.5 | 16.6
719.2 | -980.8 | 15.7 | 15.2 | 15.5 | 16.6
720.2 | -979.8 | 15.7 | 15.2 | 15.5 | 16.6
721.2 | -978.8 | 15.7 | 15.1 | 15.5 | 16.6
722.2 | -977.8 | 15.7 | 15.1 | 15.5 | 16.6
723.2 | -976.8 | 15.7 | 15.1 | 15.5 | 16.6
724.2 | -975.8 | 15.7 | 15.1 | 15.5 | 16.6
725.2 | -974.8 | 15.7 | 15.2 | 15.5 | 16.6
726.2 | -973.8 | 15.7 | 15.2 | 15.5 | 16.6
727.2 | -972.8 | 15.7 | 15.2 | 15.5 | 16.6
728.2 | -971.8 | 15.7 | 15.2 | 15.5 | 16.6
729.2 | -970.8 | 15.7 | 15.2 | 15.5 | 16.6
730.2 | -969.8 | 15.7 | 15.2 | 15.5 | 16.6
731.2 | -968.8 | 15.7 | 15.2 | 15.5 | 16.6
732.2 | -967.8 | 15.7 | 15.2 | 15.5 | 16.6
733.2 | -966.8 | 15.7 | 15.2 | 15.5 | 16.6
734.2 | -965.8 | 15.7 | 15.2 | 15.5 | 16.6
735.2 | -964.8 | 15.7 | 15.1 | 15.5 | 16.6
736.2 | -963.8 | 15.7 | 15.1 | 15.5 | 16.6
737.2 | -962.8 | 15.7 | 15.2 | 15.5 | 16.6
738.2 | -961.8 | 15.7 | 15.1 | 15.5 | 16.6
739.2 | -960.8 | 15.7 | 15.1 | 15.5 | 16.6
740.2 | -959.8 | 15.7 | 15.2 | 15.5 | 16.6
741.2 | -958.8 | 15.7 | 15.1 | 15.5 | 16.6
742.2 | -957.8 | 15.7 | 15.1 | 15.5 | 16.6
743.2 | -956.8 | 15.7 | 15.1 | 15.5 | 16.6
744.2 | -955.8 | 15.7 | 15.1 | 15.5 | 16.6
745.2 | -954.8 | 15.7 | 15.1 | 15.5 | 16.6
746.2 | -953.8 | 15.7 | 15.1 | 15.5 | 16.6
747.2 | -952.8 | 15.7 | 15.1 | 15.5 | 16.6
748.2 | -951.8 | 15.7 | 15.1 | 15.5 | 16.6
749.2 | -950.8 | 15.7 | 15.1 | 15.5 | 16.6
750.2 | -949.8 | 15.7 | 15.1 | 15.5 | 16.6
751.2 | -948.8 | 15.7 | 15.1 | 15.5 | 16.6
752.2 | -947.8 | 15.7 | 15.1 | 15.5 | 16.6
753.2 | -946.8 | 15.7 | 15.1 | 15.5 | 16.6
754.2 | -945.8 | 15.7 | 15.1 | 15.5 | 16.6
755.2 | -944.8 | 15.7 | 15.1 | 15.5 | 16.6
756.2 | -943.8 | 15.7 | 15.1 | 15.5 | 16.6
757.2 | -942.8 | 15.7 | 15.1 | 15.5 | 16.6
758.2 | -941.8 | 15.7 | 15.1 | 15.5 | 16.6
759.2 | -940.8 | 15.7 | 15.1 | 15.5 | 16.6
760.2 | -939.8 | 15.7 | 15.1 | 15.5 | 16.6
761.2 | -938.8 | 15.7 | 15.1 | 15.5 | 16.6
762.2 | -937.8 | 15.7 | 15.1 | 15.5 | 16.6
763.2 | -936.8 | 15.7 | 15.1 | 15.5 | 16.6
764.2 | -935.8 | 15.7 | 15.1 | 15.5 | 16.6
765.2 | -934.8 | 15.7 | 15.1 | 15.5 | 16.6
766.2 | -933.8 | 15.7 | 15.1 | 15.5 | 16.6
767.2 | -932.8 | 15.7 | 15.1 | 15.5 | 16.6
768.2 | -931.8 | 15.7 | 15.1 | 15.5 | 16.6
769.2 | -930.8 | 15.7 | 15.1 | 15.5 | 16.6
770.2 | -929.8 | 15.7 | 15.1 | 15.5 | 16.6
771.2 | -928.8 | 15.7 | 15.1 | 15.5 | 16.6
772.2 | -927.8 | 15.7 | 15.1 | 15.5 | 16.6
773.2 | -926.8 | 15.7 | 15.1 | 15.5 | 16.6
774.2 | -925.8 | 15.7 | 15.1 | 15.5 | 16.6
775.2 | -924.8 | 15.7 | 15.1 | 15.5 | 16.6
776.2 | -923.8 | 15.7 | 15.1 | 15.5 | 16.6
777.2 | -922.8 | 15.7 | 15.1 | 15.5 | 16.6
778.2 | -921.8 | 15.7 | 15.1 | 15.5 | 16.6
779.2 | -920.8 | 15.7 | 15.1 | 15.5 | 16.6
780.2 | -919.8 | 15.7 | 15.1 | 15.5 | 16.6
781.2 | -918.8 | 15.7 | 15.1 | 15.5 | 16.6
782.2 | -917.8 | 15.7 | 15.1 | 15.5 | 16.6
783.2 | -916.8 | 15.7 | 15.1 | 15.5 | 16.6
784.2 | -915.8 | 15.7 | 15.1 | 15.5 | 16.6
785.2 | -914.8 | 15.7 | 15.1 | 15.5 | 16.6
786.2 | -913.8 | 15.7 | 15.1 | 15.5 | 16.6
787.2 | -912.8 | 15.7 | 15.1 | 15.5 | 16.6
788.2 | -911.8 | 15.7 | 15.2 | 15.5 | 16.6
789.2 | -910.8 | 15.7 | 15.1 | 15.5 | 16.6
790.2 | -909.8 | 15.7 | 15.1 | 15.5 | 16.6
791.2 | -908.8 | 15.7 | 15.1 | 15.5 | 16.6
792.2 | -907.8 | 15.7 | 15.1 | 15.5 | 16.6
793.2 | -906.8 | 15.7 | 15.1 | 15.5 | 16.6
794.2 | -905.8 | 15.7 | 15.1 | 15.5 | 16.6
795.2 | -904.8 | 15.7 | 15.1 | 15.5 | 16.6
796.2 | -903.8 | 15.7 | 15.1 | 15.5 | 16.6
797.2 | -902.8 | 15.7 | 15.1 | 15.5 | 16.6
798.2 | -901.8 | 15.7 | 15.1 | 15.5 | 16.6
799.2 | -900.8 | 15.7 | 15.1 | 15.5 | 16.6
800.2 | -899.8 | 15.7 | 15.1 | 15.5 | 16.6
801.2 | -898.8 | 15.7 | 15.1 | 15.5 | 16.6
802.2 | -897.8 | 15.7 | 15.1 | 15.5 | 16.6
803.2 | -896.8 | 15.7 | 15.2 | 15.5 | 16.6
804.2 | -895.8 | 15.7 | 15.1 | 15.5 | 16.6
805.2 | -894.8 | 15.7 | 15.1 | 15.5 | 16.6
806.2 | -893.8 | 15.7 | 15.1 | 15.5 | 16.6
807.2 | -892.8 | 15.7 | 15.1 | 15.5 | 16.6
808.2 | -891.8 | 15.7 | 15.1 | 15.5 | 16.6
809.2 | -890.8 | 15.7 | 15.1 | 15.5 | 16.6
810.2 | -889.8 | 15.7 | 15.1 | 15.5 | 16.6
811.2 | -888.8 | 15.7 | 15.1 | 15.5 | 16.6
812.2 | -887.8 | 15.7 | 15.1 | 15.5 | 16.6
813.2 | -886.8 | 15.7 | 15.1 | 15.5 | 16.6
814.2 | -885.8 | 15.7 | 15.1 | 15.5 | 16.6
815.2 | -884.8 | 15.7 | 15.1 | 15.5 | 16.6
816.2 | -883.8 | 15.7 | 15.1 | 15.5 | 16.6
817.2 | -882.8 | 15.7 | 15.1 | 15.5 | 16.6
818.2 | -881.8 | 15.7 | 15.1 | 15.5 | 16.6
819.2 | -880.8 | 15.7 | 15.1 | 15.5 | 16.6
820.2 | -879.8 | 15.7 | 15.1 | 15.5 | 16.6
821.2 | -878.8 | 15.7 | 15.1 | 15.5 | 16.6
822.2 | -877.8 | 15.7 | 15.1 | 15.5 | 16.6
823.2 | -876.8 | 15.7 | 15.1 | 15.5 | 16.6
824.2 | -875.8 | 15.7 | 15.1 | 15.5 | 16.6
825.2 | -874.8 | 15.7 | 15.1 | 15.5 | 16.6
826.2 | -873.8 | 15.7 | 15.1 | 15.5 | 16.6
827.2 | -872.8 | 15.7 | 15.1 | 15.5 | 16.6
828.2 | -871.8 | 15.7 | 15.1 | 15.5 | 16.6
829.2 | -870.8 | 15.7 | 15.1 | 15.5 | 16.6
830.2 | -869.8 | 15.7 | 15.1 | 15.5 | 16.6
831.2 | -868.8 | 15.7 | 15.1 | 15.5 | 16.6
832.2 | -867.8 | 15.7 | 15.1 | 15.5 | 16.6
833.2 | -866.8 | 15.7 | 15.1 | 15.5 | 16.6
834.2 | -865.8 | 15.7 | 15.1 | 15.5 | 16.6
835.2 | -864.8 | 15.7 | 15.1 | 15.5 | 16.6
836.2 | -863.8 | 15.7 | 15.1 | 15.5 | 16.6
837.2 | -862.8 | 15.7 | 15.1 | 15.5 | 16.6
838.2 | -861.8 | 15.7 | 15.1 | 15.5 | 16.6
839.2 | -860.8 | 15.7 | 15.1 | 15.5 | 16.6
840.2 | -859.8 | 15.7 | 15.1 | 15.5 | 16.6
841.2 | -858.8 | 15.7 | 15.1 | 15.5 | 16.6
842.2 | -857.8 | 15.7 | 15.1 | 15.5 | 16.6
843.2 | -856.8 | 15.7 | 15.1 | 15.5 | 16.6
844.2 | -855.8 | 15.7 | 15.1 | 15.5 | 16.6
845.2 | -854.8 | 15.7 | 15.1 | 15.5 | 16.6
846.2 | -853.8 | 15.7 | 15.1 | 15.5 | 16.6
847.2 | -852.8 | 15.7 | 15.1 | 15.5 | 16.6
848.2 | -851.8 | 15.7 | 15.1 | 15.5 | 16.6
849.2 | -850.8 | 15.7 | 15.1 | 15.5 | 16.6
850.2 | -849.8 | 15.7 | 15.1 | 15.5 | 16.6
851.2 | -848.8 | 15.7 | 15.1 | 15.5 | 16.6
852.2 | -847.8 | 15.7 | 15.1 | 15.5 | 16.6
853.2 | -846.8 | 15.7 | 15.1 | 15.5 | 16.6
854.2 | -845.8 | 15.7 | 15.1 | 15.5 | 16.6
855.2 | -844.8 | 15.7 | 15.1 | 15.5 | 16.6
856.2 | -843.8 | 15.7 | 15.1 | 15.5 | 16.6
857.2 | -842.8 | 15.7 | 15.1 | 15.5 | 16.6
858.2 | -841.8 | 15.7 | 15.1 | 15.5 | 16.6
859.2 | -840.8 | 15.7 | 15.1 | 15.5 | 16.6
860.2 | -839.8 | 15.7 | 15.1 | 15.5 | 16.6
861.2 | -838.8 | 15.7 | 15.1 | 15.5 | 16.6
862.2 | -837.8 | 15.7 | 15.1 | 15.5 | 16.6
863.2 | -836.8 | 15.7 | 15.1 | 15.5 | 16.6
864.2 | -835.8 | 15.7 | 15.1 | 15.5 | 16.6
865.2 | -834.8 | 15.7 | 15.1 | 15.5 | 16.6
866.2 | -833.8 | 15.7 | 15.1 | 15.5 | 16.6
867.2 | -832.8 | 15.7 | 15.1 | 15.5 | 16.6
868.2 | -831.8 | 15.7 | 15.1 | 15.5 | 16.6
869.2 | -830.8 | 15.7 | 15.1 | 15.5 | 16.6
870.2 | -829.8 | 15.7 | 15.1 | 15.5 | 16.6
871.2 | -828.8 | 15.7 | 15.1 | 15.5 | 16.6
872.2 | -827.8 | 15.7 | 15.1 | 15.5 | 16.6
873.2 | -826.8 | 15.7 | 15.1 | 15.5 | 16.6
874.2 | -825.8 | 15.7 | 15.1 | 15.5 | 16.6
875.2 | -824.8 | 15.7 | 15.1 | 15.5 | 16.6
876.2 | -823.8 | 15.7 | 15.1 | 15.5 | 16.6
877.2 | -822.8 | 15.7 | 15.1 | 15.5 | 16.6
878.2 | -821.8 | 15.7 | 15.1 | 15.5 | 16.6
879.2 | -820.8 | 15.7 | 15.1 | 15.5 | 16.6
880.2 | -819.8 | 15.7 | 15.1 | 15.5 | 16.6
881.2 | -818.8 | 15.7 | 15.1 | 15.5 | 16.6
882.2 | -817.8 | 15.7 | 15.1 | 15.5 | 16.6
883.2 | -816.8 | 15.7 | 15.1 | 15.5 | 16.6
884.2 | -815.8 | 15.7 | 15.1 | 15.5 | 16.6
885.2 | -814.8 | 15.7 | 15.1 | 15.5 | 16.6
886.2 | -813.8 | 15.7 | 15.1 | 15.5 | 16.6
887.2 | -812.8 | 15.7 | 15.1 | 15.5 | 16.6
888.2 | -811.8 | 15.7 | 15.1 | 15.5 | 16.6
889.2 | -810.8 | 15.7 | 15.1 | 15.5 | 16.6
890.2 | -809.8 | 15.7 | 15.1 | 15.5 | 16.6
891.2 | -808.8 | 15.7 | 15.1 | 15.5 | 16.6
892.2 | -807.8 | 15.7 | 15.1 | 15.5 | 16.6
893.2 | -806.8 | 15.7 | 15.1 | 15.5 | 16.6
894.2 | -805.8 | 15.7 | 15.1 | 15.5 | 16.6
895.2 | -804.8 | 15.7 | 15.1 | 15.5 | 16.6
896.2 | -803.8 | 15.7 | 15.1 | 15.5 | 16.6
897.2 | -802.8 | 15.7 | 15.1 | 15.5 | 16.6
898.2 | -801.8 | 15.7 | 15.1 | 15.5 | 16.6
899.2 | -800.8 | 15.7 | 15.1 | 15.5 | 16.6
900.2 | -799.8 | 15.7 | 15.1 | 15.5 | 16.6
901.2 | -798.8 | 15.7 | 15.1 | 15.5 | 16.7
902.2 | -797.8 | 15.7 | 15.1 | 15.5 | 16.6
903.2 | -796.8 | 15.7 | 15.1 | 15.5 | 16.6
904.2 | -795.8 | 15.7 | 15.1 | 15.5 | 16.6
905.2 | -794.8 | 15.7 | 15.1 | 15.5 | 16.6
906.2 | -793.8 | 15.7 | 15.1 | 15.5 | 16.6
907.2 | -792.8 | 15.7 | 15.1 | 15.5 | 16.6
908.2 | -791.8 | 15.7 | 15.1 | 15.5 | 16.6
909.2 | -790.8 | 15.7 | 15.1 | 15.5 | 16.6
910.2 | -789.8 | 15.7 | 15.1 | 15.5 | 16.6
911.2 | -788.8 | 15.7 | 15.1 | 15.5 | 16.7
912.2 | -787.8 | 15.7 | 15.1 | 15.5 | 16.6
913.2 | -786.8 | 15.7 | 15.1 | 15.5 | 16.6
914.2 | -785.8 | 15.7 | 15.1 | 15.5 | 16.6
915.2 | -784.8 | 15.7 | 15.1 | 15.5 | 16.6
916.2 | -783.8 | 15.7 | 15.1 | 15.5 | 16.6
917.2 | -782.8 | 15.7 | 15.1 | 15.5 | 16.6
918.2 | -781.8 | 15.7 | 15.1 | 15.5 | 16.6
919.2 | -780.8 | 15.7 | 15.1 | 15.5 | 16.6
920.2 | -779.8 | 15.7 | 15.1 | 15.5 | 16.6
921.2 | -778.8 | 15.7 | 15.1 | 15.5 | 16.6
922.2 | -777.8 | 15.7 | 15.1 | 15.5 | 16.6
923.2 | -776.8 | 15.7 | 15.1 | 15.5 | 16.6
924.2 | -775.8 | 15.7 | 15.1 | 15.5 | 16.6
925.2 | -774.8 | 15.7 | 15.1 | 15.5 | 16.6
926.2 | -773.8 | 15.7 | 15.1 | 15.5 | 16.6
927.2 | -772.8 | 15.7 | 15.1 | 15.5 | 16.6
928.2 | -771.8 | 15.7 | 15.1 | 15.5 | 16.6
929.2 | -770.8 | 15.7 | 15.1 | 15.5 | 16.6
930.2 | -769.8 | 15.7 | 15.2 | 15.5 | 16.6
931.2 | -768.8 | 15.7 | 15.2 | 15.5 | 16.6
932.2 | -767.8 | 15.7 | 15.1 | 15.5 | 16.6
933.2 | -766.8 | 15.7 | 15.2 | 15.5 | 16.6
934.2 | -765.8 | 15.7 | 15.2 | 15.5 | 16.6
935.2 | -764.8 | 15.7 | 15.2 | 15.5 | 16.6
936.2 | -763.8 | 15.7 | 15.2 | 15.5 | 16.6
937.2 | -762.8 | 15.7 | 15.2 | 15.5 | 16.6
938.2 | -761.8 | 15.7 | 15.2 | 15.5 | 16.6
939.2 | -760.8 | 15.7 | 15.2 | 15.5 | 16.7
940.2 | -759.8 | 15.7 | 15.2 | 15.5 | 16.6
941.2 | -758.8 | 15.7 | 15.2 | 15.5 | 16.6
942.2 | -757.8 | 15.7 | 15.2 | 15.5 | 16.6
943.2 | -756.8 | 15.7 | 15.2 | 15.5 | 16.7
944.2 | -755.8 | 15.7 | 15.2 | 15.5 | 16.7
945.2 | -754.8 | 15.7 | 15.2 | 15.5 | 16.6
946.2 | -753.8 | 15.7 | 15.2 | 15.5 | 16.7
947.2 | -752.8 | 15.7 | 15.2 | 15.5 | 16.6
948.2 | -751.8 | 15.7 | 15.2 | 15.5 | 16.6
949.2 | -750.8 | 15.7 | 15.2 | 15.5 | 16.7
950.2 | -749.8 | 15.7 | 15.2 | 15.5 | 16.6
951.2 | -748.8 | 15.7 | 15.2 | 15.5 | 16.6
952.2 | -747.8 | 15.7 | 15.2 | 15.5 | 16.6
953.2 | -746.8 | 15.7 | 15.2 | 15.5 | 16.7
954.2 | -745.8 | 15.7 | 15.2 | 15.5 | 16.6
955.2 | -744.8 | 15.7 | 15.2 | 15.5 | 16.6
956.2 | -743.8 | 15.7 | 15.2 | 15.5 | 16.7
957.2 | -742.8 | 15.7 | 15.2 | 15.5 | 16.7
958.2 | -741.8 | 15.7 | 15.2 | 15.5 | 16.7
959.2 | -740.8 | 15.7 | 15.2 | 15.5 | 16.7
960.2 | -739.8 | 15.7 | 15.2 | 15.5 | 16.6
961.2 | -738.8 | 15.7 | 15.2 | 15.5 | 16.7
962.2 | -737.8 | 15.7 | 15.2 | 15.5 | 16.7
963.2 | -736.8 | 15.7 | 15.2 | 15.5 | 16.7
964.2 | -735.8 | 15.7 | 15.2 | 15.5 | 16.7
965.2 | -734.8 | 15.7 | 15.2 | 15.5 | 16.6
966.2 | -733.8 | 15.7 | 15.2 | 15.5 | 16.7
967.2 | -732.8 | 15.7 | 15.2 | 15.5 | 16.7
968.2 | -731.8 | 15.7 | 15.2 | 15.5 | 16.7
969.2 | -730.8 | 15.7 | 15.2 | 15.5 | 16.7
970.2 | -729.8 | 15.7 | 15.2 | 15.5 | 16.7
971.2 | -728.8 | 15.7 | 15.2 | 15.5 | 16.7
972.2 | -727.8 | 15.7 | 15.2 | 15.5 | 16.7
973.2 | -726.8 | 15.7 | 15.2 | 15.5 | 16.6
974.2 | -725.8 | 15.7 | 15.2 | 15.5 | 16.7
975.2 | -724.8 | 15.7 | 15.2 | 15.5 | 16.6
976.2 | -723.8 | 15.7 | 15.2 | 15.5 | 16.6
977.2 | -722.8 | 15.7 | 15.2 | 15.5 | 16.7
978.2 | -721.8 | 15.7 | 15.2 | 15.5 | 16.7
979.2 | -720.8 | 15.7 | 15.2 | 15.5 | 16.7
980.2 | -719.8 | 15.7 | 15.2 | 15.5 | 16.6
981.2 | -718.8 | 15.7 | 15.2 | 15.5 | 16.7
982.2 | -717.8 | 15.7 | 15.2 | 15.5 | 16.7
983.2 | -716.8 | 15.7 | 15.2 | 15.5 | 16.6
984.2 | -715.8 | 15.7 | 15.2 | 15.5 | 16.6
985.2 | -714.8 | 15.7 | 15.2 | 15.5 | 16.7
986.2 | -713.8 | 15.7 | 15.2 | 15.5 | 16.7
987.2 | -712.8 | 15.7 | 15.2 | 15.5 | 16.7
988.2 | -711.8 | 15.7 | 15.2 | 15.5 | 16.7
989.2 | -710.8 | 15.7 | 15.2 | 15.5 | 16.7
990.2 | -709.8 | 15.7 | 15.2 | 15.5 | 16.7
991.2 | -708.8 | 15.7 | 15.2 | 15.5 | 16.7
992.2 | -707.8 | 15.7 | 15.2 | 15.5 | 16.7
993.2 | -706.8 | 15.7 | 15.2 | 15.5 | 16.6
994.2 | -705.8 | 15.7 | 15.2 | 15.5 | 16.7
995.2 | -704.8 | 15.7 | 15.2 | 15.5 | 16.7
996.2 | -703.8 | 15.7 | 15.2 | 15.5 | 16.7
997.2 | -702.8 | 15.7 | 15.2 | 15.5 | 16.7
998.2 | -701.8 | 15.7 | 15.2 | 15.5 | 16.7
999.2 | -700.8 | 15.7 | 15.2 | 15.5 | 16.7
1000.2 | -699.8 | 15.7 | 15.2 | 15.5 | 16.7
1001.2 | -698.8 | 15.7 | 15.2 | 15.5 | 16.6
1002.2 | -697.8 | 15.7 | 15.2 | 15.5 | 16.7
1003.2 | -696.8 | 15.7 | 15.2 | 15.5 | 16.7
1004.2 | -695.8 | 15.7 | 15.2 | 15.5 | 16.7
1005.2 | -694.8 | 15.7 | 15.2 | 15.5 | 16.7
1006.2 | -693.8 | 15.7 | 15.2 | 15.5 | 16.7
1007.2 | -692.8 | 15.7 | 15.2 | 15.5 | 16.7
1008.2 | -691.8 | 15.7 | 15.2 | 15.5 | 16.7
1009.2 | -690.8 | 15.7 | 15.2 | 15.5 | 16.7
1010.2 | -689.8 | 15.7 | 15.2 | 15.5 | 16.7
1011.2 | -688.8 | 15.7 | 15.2 | 15.5 | 16.7
1012.2 | -687.8 | 15.7 | 15.2 | 15.5 | 16.6
1013.2 | -686.8 | 15.7 | 15.2 | 15.5 | 16.7
1014.2 | -685.8 | 15.7 | 15.2 | 15.5 | 16.7
1015.2 | -684.8 | 15.7 | 15.2 | 15.5 | 16.7
1016.2 | -683.8 | 15.7 | 15.2 | 15.5 | 16.7
1017.2 | -682.8 | 15.7 | 15.2 | 15.5 | 16.7
1018.2 | -681.8 | 15.7 | 15.2 | 15.5 | 16.7
1019.2 | -680.8 | 15.7 | 15.2 | 15.5 | 16.7
1020.2 | -679.8 | 15.7 | 15.2 | 15.5 | 16.7
1021.2 | -678.8 | 15.7 | 15.2 | 15.5 | 16.7
1022.2 | -677.8 | 15.7 | 15.2 | 15.5 | 16.7
1023.2 | -676.8 | 15.7 | 15.2 | 15.5 | 16.7
1024.2 | -675.8 | 15.7 | 15.2 | 15.5 | 16.7
1025.2 | -674.8 | 15.7 | 15.2 | 15.5 | 16.7
1026.2 | -673.8 | 15.7 | 15.2 | 15.5 | 16.7
1027.2 | -672.8 | 15.7 | 15.2 | 15.5 | 16.7
1028.2 | -671.8 | 15.7 | 15.2 | 15.5 | 16.6
1029.2 | -670.8 | 15.7 | 15.2 | 15.5 | 16.7
1030.2 | -669.8 | 15.7 | 15.2 | 15.5 | 16.7
1031.2 | -668.8 | 15.7 | 15.2 | 15.5 | 16.7
1032.2 | -667.8 | 15.7 | 15.2 | 15.5 | 16.7
1033.2 | -666.8 | 15.7 | 15.2 | 15.5 | 16.7
1034.2 | -665.8 | 15.7 | 15.2 | 15.5 | 16.7
1035.2 | -664.8 | 15.7 | 15.2 | 15.5 | 16.7
1036.2 | -663.8 | 15.7 | 15.2 | 15.5 | 16.7
1037.2 | -662.8 | 15.7 | 15.2 | 15.5 | 16.7
1038.2 | -661.8 | 15.7 | 15.2 | 15.5 | 16.7
1039.2 | -660.8 | 15.7 | 15.2 | 15.5 | 16.7
1040.2 | -659.8 | 15.7 | 15.2 | 15.5 | 16.7
1041.2 | -658.8 | 15.7 | 15.2 | 15.5 | 16.7
1042.2 | -657.8 | 15.7 | 15.2 | 15.5 | 16.7
1043.2 | -656.8 | 15.7 | 15.2 | 15.5 | 16.7
1044.2 | -655.8 | 15.7 | 15.2 | 15.5 | 16.7
1045.2 | -654.8 | 15.7 | 15.2 | 15.5 | 16.7
1046.2 | -653.8 | 15.7 | 15.2 | 15.5 | 16.7
1047.2 | -652.8 | 15.7 | 15.2 | 15.5 | 16.7
1048.2 | -651.8 | 15.7 | 15.2 | 15.5 | 16.7
1049.2 | -650.8 | 15.7 | 15.2 | 15.5 | 16.7
1050.2 | -649.8 | 15.7 | 15.2 | 15.5 | 16.7
1051.2 | -648.8 | 15.7 | 15.2 | 15.5 | 16.7
1052.2 | -647.8 | 15.7 | 15.2 | 15.5 | 16.7
1053.2 | -646.8 | 15.7 | 15.2 | 15.5 | 16.7
1054.2 | -645.8 | 15.7 | 15.2 | 15.5 | 16.7
1055.2 | -644.8 | 15.7 | 15.2 | 15.5 | 16.7
1056.2 | -643.8 | 15.7 | 15.2 | 15.5 | 16.7
1057.2 | -642.8 | 15.7 | 15.2 | 15.5 | 16.7
1058.2 | -641.8 | 15.7 | 15.2 | 15.5 | 16.7
1059.2 | -640.8 | 15.7 | 15.2 | 15.5 | 16.7
1060.2 | -639.8 | 15.7 | 15.2 | 15.5 | 16.7
1061.2 | -638.8 | 15.7 | 15.2 | 15.5 | 16.7
1062.2 | -637.8 | 15.7 | 15.2 | 15.5 | 16.7
1063.2 | -636.8 | 15.7 | 15.2 | 15.5 | 16.7
1064.2 | -635.8 | 15.7 | 15.2 | 15.5 | 16.7
1065.2 | -634.8 | 15.7 | 15.2 | 15.5 | 16.7
1066.2 | -633.8 | 15.7 | 15.2 | 15.5 | 16.7
1067.2 | -632.8 | 15.7 | 15.2 | 15.5 | 16.7
1068.2 | -631.8 | 15.7 | 15.2 | 15.5 | 16.7
1069.2 | -630.8 | 15.7 | 15.2 | 15.5 | 16.7
1070.2 | -629.8 | 15.7 | 15.2 | 15.5 | 16.7
1071.2 | -628.8 | 15.7 | 15.2 | 15.5 | 16.7
1072.2 | -627.8 | 15.7 | 15.2 | 15.5 | 16.7
1073.2 | -626.8 | 15.7 | 15.2 | 15.5 | 16.7
1074.2 | -625.8 | 15.7 | 15.2 | 15.5 | 16.7
1075.2 | -624.8 | 15.7 | 15.2 | 15.5 | 16.7
1076.2 | -623.8 | 15.7 | 15.2 | 15.5 | 16.7
1077.2 | -622.8 | 15.7 | 15.2 | 15.5 | 16.6
1078.2 | -621.8 | 15.7 | 15.2 | 15.5 | 16.7
1079.2 | -620.8 | 15.7 | 15.2 | 15.5 | 16.7
1080.2 | -619.8 | 15.7 | 15.2 | 15.5 | 16.7
1081.2 | -618.8 | 15.7 | 15.2 | 15.5 | 16.7
1082.2 | -617.8 | 15.7 | 15.2 | 15.5 | 16.7
1083.2 | -616.8 | 15.7 | 15.2 | 15.5 | 16.7
1084.2 | -615.8 | 15.7 | 15.2 | 15.5 | 16.6
1085.2 | -614.8 | 15.7 | 15.2 | 15.5 | 16.7
1086.2 | -613.8 | 15.7 | 15.2 | 15.5 | 16.7
1087.2 | -612.8 | 15.7 | 15.2 | 15.5 | 16.7
1088.2 | -611.8 | 15.7 | 15.2 | 15.5 | 16.7
1089.2 | -610.8 | 15.7 | 15.2 | 15.5 | 16.7
1090.2 | -609.8 | 15.7 | 15.2 | 15.5 | 16.7
1091.2 | -608.8 | 15.7 | 15.2 | 15.5 | 16.7
1092.2 | -607.8 | 15.7 | 15.2 | 15.5 | 16.7
1093.2 | -606.8 | 15.7 | 15.2 | 15.5 | 16.7
1094.2 | -605.8 | 15.7 | 15.2 | 15.5 | 16.7
1095.2 | -604.8 | 15.7 | 15.2 | 15.5 | 16.7
1096.2 | -603.8 | 15.7 | 15.2 | 15.5 | 16.7
1097.2 | -602.8 | 15.7 | 15.2 | 15.5 | 16.7
1098.2 | -601.8 | 15.7 | 15.2 | 15.5 | 16.7
1099.2 | -600.8 | 15.7 | 15.2 | 15.5 | 16.7
1100.2 | -599.8 | 15.7 | 15.2 | 15.5 | 16.7
1101.2 | -598.8 | 15.7 | 15.2 | 15.5 | 16.7
1102.2 | -597.8 | 15.7 | 15.2 | 15.5 | 16.7
1103.2 | -596.8 | 15.7 | 15.2 | 15.5 | 16.7
1104.2 | -595.8 | 15.7 | 15.2 | 15.5 | 16.7
1105.2 | -594.8 | 15.7 | 15.2 | 15.5 | 16.7
1106.2 | -593.8 | 15.7 | 15.2 | 15.5 | 16.7
1107.2 | -592.8 | 15.7 | 15.2 | 15.5 | 16.7
1108.2 | -591.8 | 15.7 | 15.2 | 15.5 | 16.7
1109.2 | -590.8 | 15.7 | 15.2 | 15.5 | 16.7
1110.2 | -589.8 | 15.7 | 15.2 | 15.5 | 16.7
1111.2 | -588.8 | 15.7 | 15.2 | 15.5 | 16.7
1112.2 | -587.8 | 15.7 | 15.2 | 15.5 | 16.7
1113.2 | -586.8 | 15.7 | 15.2 | 15.5 | 16.7
1114.2 | -585.8 | 15.7 | 15.2 | 15.5 | 16.7
1115.2 | -584.8 | 15.7 | 15.2 | 15.5 | 16.7
1116.2 | -583.8 | 15.7 | 15.2 | 15.5 | 16.7
1117.2 | -582.8 | 15.7 | 15.2 | 15.5 | 16.7
1118.2 | -581.8 | 15.7 | 15.2 | 15.5 | 16.7
1119.2 | -580.8 | 15.7 | 15.2 | 15.5 | 16.7
1120.2 | -579.8 | 15.7 | 15.2 | 15.5 | 16.7
1121.2 | -578.8 | 15.7 | 15.2 | 15.5 | 16.7
1122.2 | -577.8 | 15.7 | 15.2 | 15.5 | 16.7
1123.2 | -576.8 | 15.7 | 15.2 | 15.5 | 16.7
1124.2 | -575.8 | 15.7 | 15.2 | 15.5 | 16.7
1125.2 | -574.8 | 15.7 | 15.2 | 15.5 | 16.7
1126.2 | -573.8 | 15.7 | 15.2 | 15.5 | 16.7
1127.2 | -572.8 | 15.7 | 15.2 | 15.5 | 16.7
1128.2 | -571.8 | 15.7 | 15.2 | 15.5 | 16.7
1129.2 | -570.8 | 15.7 | 15.2 | 15.5 | 16.7
1130.2 | -569.8 | 15.7 | 15.2 | 15.5 | 16.7
1131.2 | -568.8 | 15.7 | 15.2 | 15.5 | 16.7
1132.2 | -567.8 | 15.7 | 15.2 | 15.5 | 16.7
1133.2 | -566.8 | 15.7 | 15.2 | 15.5 | 16.7
1134.2 | -565.8 | 15.7 | 15.2 | 15.5 | 16.7
1135.2 | -564.8 | 15.7 | 15.2 | 15.5 | 16.7
1136.2 | -563.8 | 15.7 | 15.2 | 15.5 | 16.7
1137.2 | -562.8 | 15.7 | 15.2 | 15.5 | 16.7
1138.2 | -561.8 | 15.7 | 15.2 | 15.5 | 16.7
1139.2 | -560.8 | 15.7 | 15.2 | 15.5 | 16.7
1140.2 | -559.8 | 15.7 | 15.2 | 15.5 | 16.7
1141.2 | -558.8 | 15.7 | 15.2 | 15.5 | 16.7
1142.2 | -557.8 | 15.7 | 15.2 | 15.5 | 16.7
1143.2 | -556.8 | 15.7 | 15.2 | 15.5 | 16.7
1144.2 | -555.8 | 15.7 | 15.2 | 15.5 | 16.7
1145.2 | -554.8 | 15.7 | 15.2 | 15.5 | 16.7
1146.2 | -553.8 | 15.7 | 15.2 | 15.5 | 16.7
1147.2 | -552.8 | 15.7 | 15.2 | 15.5 | 16.7
1148.2 | -551.8 | 15.7 | 15.2 | 15.5 | 16.7
1149.2 | -550.8 | 15.7 | 15.2 | 15.5 | 16.7
1150.2 | -549.8 | 15.7 | 15.2 | 15.5 | 16.7
1151.2 | -548.8 | 15.7 | 15.2 | 15.5 | 16.7
1152.2 | -547.8 | 15.7 | 15.2 | 15.5 | 16.7
1153.2 | -546.8 | 15.8 | 15.2 | 15.5 | 16.7
1154.2 | -545.8 | 15.7 | 15.2 | 15.5 | 16.7
1155.2 | -544.8 | 15.7 | 15.2 | 15.5 | 16.7
1156.2 | -543.8 | 15.7 | 15.2 | 15.5 | 16.7
1157.2 | -542.8 | 15.7 | 15.2 | 15.5 | 16.7
1158.2 | -541.8 | 15.7 | 15.2 | 15.5 | 16.7
1159.2 | -540.8 | 15.7 | 15.2 | 15.5 | 16.7
1160.2 | -539.8 | 15.7 | 15.2 | 15.5 | 16.7
1161.2 | -538.8 | 15.7 | 15.2 | 15.5 | 16.7
1162.2 | -537.8 | 15.7 | 15.2 | 15.5 | 16.7
1163.2 | -536.8 | 15.7 | 15.2 | 15.5 | 16.7
1164.2 | -535.8 | 15.7 | 15.2 | 15.5 | 16.7
1165.2 | -534.8 | 15.7 | 15.2 | 15.5 | 16.7
1166.2 | -533.8 | 15.7 | 15.2 | 15.5 | 16.7
1167.2 | -532.8 | 15.7 | 15.2 | 15.5 | 16.7
1168.2 | -531.8 | 15.7 | 15.2 | 15.5 | 16.7
1169.2 | -530.8 | 15.7 | 15.2 | 15.6 | 16.7
1170.2 | -529.8 | 15.7 | 15.2 | 15.5 | 16.7
1171.2 | -528.8 | 15.7 | 15.2 | 15.5 | 16.7
1172.2 | -527.8 | 15.7 | 15.2 | 15.5 | 16.7
1173.2 | -526.8 | 15.7 | 15.2 | 15.6 | 16.7
1174.2 | -525.8 | 15.7 | 15.2 | 15.5 | 16.7
1175.2 | -524.8 | 15.7 | 15.2 | 15.5 | 16.7
1176.2 | -523.8 | 15.7 | 15.2 | 15.5 | 16.7
1177.2 | -522.8 | 15.7 | 15.2 | 15.5 | 16.7
1178.2 | -521.8 | 15.7 | 15.2 | 15.5 | 16.7
1179.2 | -520.8 | 15.7 | 15.2 | 15.5 | 16.7
1180.2 | -519.8 | 15.7 | 15.2 | 15.5 | 16.7
1181.2 | -518.8 | 15.7 | 15.2 | 15.5 | 16.7
1182.2 | -517.8 | 15.7 | 15.2 | 15.5 | 16.7
1183.2 | -516.8 | 15.7 | 15.2 | 15.5 | 16.7
1184.2 | -515.8 | 15.7 | 15.2 | 15.5 | 16.7
1185.2 | -514.8 | 15.7 | 15.2 | 15.5 | 16.7
1186.2 | -513.8 | 15.7 | 15.2 | 15.5 | 16.7
1187.2 | -512.8 | 15.7 | 15.2 | 15.5 | 16.7
1188.2 | -511.8 | 15.7 | 15.2 | 15.5 | 16.7
1189.2 | -510.8 | 15.7 | 15.2 | 15.6 | 16.7
1190.2 | -509.8 | 15.7 | 15.2 | 15.5 | 16.7
1191.2 | -508.8 | 15.7 | 15.2 | 15.6 | 16.7
1192.2 | -507.8 | 15.7 | 15.2 | 15.5 | 16.7
1193.2 | -506.8 | 15.7 | 15.2 | 15.5 | 16.7
1194.2 | -505.8 | 15.7 | 15.2 | 15.6 | 16.7
1195.2 | -504.8 | 15.8 | 15.2 | 15.6 | 16.7
1196.2 | -503.8 | 15.7 | 15.2 | 15.6 | 16.7
1197.2 | -502.8 | 15.7 | 15.2 | 15.6 | 16.7
1198.2 | -501.8 | 15.7 | 15.2 | 15.6 | 16.7
1199.2 | -500.8 | 15.7 | 15.2 | 15.5 | 16.7
1200.2 | -499.8 | 15.7 | 15.2 | 15.5 | 16.7
1201.2 | -498.8 | 15.7 | 15.2 | 15.5 | 16.7
1202.2 | -497.8 | 15.7 | 15.2 | 15.6 | 16.7
1203.2 | -496.8 | 15.7 | 15.2 | 15.6 | 16.7
1204.2 | -495.8 | 15.7 | 15.2 | 15.6 | 16.7
1205.2 | -494.8 | 15.7 | 15.2 | 15.5 | 16.7
1206.2 | -493.8 | 15.7 | 15.2 | 15.5 | 16.7
1207.2 | -492.8 | 15.7 | 15.2 | 15.6 | 16.7
1208.2 | -491.8 | 15.7 | 15.2 | 15.6 | 16.7
1209.2 | -490.8 | 15.7 | 15.2 | 15.5 | 16.7
1210.2 | -489.8 | 15.7 | 15.2 | 15.5 | 16.7
1211.2 | -488.8 | 15.7 | 15.2 | 15.5 | 16.7
1212.2 | -487.8 | 15.7 | 15.2 | 15.5 | 16.7
1213.2 | -486.8 | 15.7 | 15.2 | 15.5 | 16.7
1214.2 | -485.8 | 15.7 | 15.2 | 15.6 | 16.7
1215.2 | -484.8 | 15.7 | 15.2 | 15.6 | 16.7
1216.2 | -483.8 | 15.8 | 15.2 | 15.5 | 16.7
1217.2 | -482.8 | 15.7 | 15.2 | 15.6 | 16.7
1218.2 | -481.8 | 15.7 | 15.2 | 15.6 | 16.7
1219.2 | -480.8 | 15.7 | 15.2 | 15.6 | 16.7
1220.2 | -479.8 | 15.7 | 15.2 | 15.6 | 16.7
1221.2 | -478.8 | 15.7 | 15.2 | 15.6 | 16.7
1222.2 | -477.8 | 15.7 | 15.2 | 15.6 | 16.7
1223.2 | -476.8 | 15.7 | 15.2 | 15.6 | 16.7
1224.2 | -475.8 | 15.7 | 15.2 | 15.6 | 16.7
1225.2 | -474.8 | 15.7 | 15.2 | 15.6 | 16.7
1226.2 | -473.8 | 15.7 | 15.2 | 15.6 | 16.7
1227.2 | -472.8 | 15.8 | 15.2 | 15.6 | 16.7
1228.2 | -471.8 | 15.7 | 15.2 | 15.6 | 16.7
1229.2 | -470.8 | 15.7 | 15.2 | 15.6 | 16.7
1230.2 | -469.8 | 15.8 | 15.2 | 15.6 | 16.7
1231.2 | -468.8 | 15.7 | 15.2 | 15.6 | 16.7
1232.2 | -467.8 | 15.7 | 15.2 | 15.6 | 16.7
1233.2 | -466.8 | 15.7 | 15.2 | 15.6 | 16.7
1234.2 | -465.8 | 15.8 | 15.2 | 15.6 | 16.7
1235.2 | -464.8 | 15.7 | 15.2 | 15.6 | 16.7
1236.2 | -463.8 | 15.7 | 15.2 | 15.6 | 16.7
1237.2 | -462.8 | 15.7 | 15.2 | 15.6 | 16.7
1238.2 | -461.8 | 15.7 | 15.2 | 15.6 | 16.7
1239.2 | -460.8 | 15.7 | 15.2 | 15.6 | 16.7
1240.2 | -459.8 | 15.7 | 15.2 | 15.6 | 16.7
1241.2 | -458.8 | 15.7 | 15.2 | 15.6 | 16.7
1242.2 | -457.8 | 15.7 | 15.2 | 15.6 | 16.7
1243.2 | -456.8 | 15.7 | 15.2 | 15.6 | 16.7
1244.2 | -455.8 | 15.8 | 15.2 | 15.6 | 16.7
1245.2 | -454.8 | 15.7 | 15.2 | 15.6 | 16.7
1246.2 | -453.8 | 15.8 | 15.2 | 15.6 | 16.7
1247.2 | -452.8 | 15.8 | 15.2 | 15.6 | 16.7
1248.2 | -451.8 | 15.7 | 15.2 | 15.6 | 16.7
1249.2 | -450.8 | 15.7 | 15.2 | 15.6 | 16.7
1250.2 | -449.8 | 15.7 | 15.2 | 15.6 | 16.7
1251.2 | -448.8 | 15.8 | 15.2 | 15.6 | 16.7
1252.2 | -447.8 | 15.7 | 15.2 | 15.6 | 16.7
1253.2 | -446.8 | 15.7 | 15.2 | 15.6 | 16.7
1254.2 | -445.8 | 15.8 | 15.2 | 15.6 | 16.7
1255.2 | -444.8 | 15.8 | 15.2 | 15.6 | 16.7
1256.2 | -443.8 | 15.7 | 15.2 | 15.5 | 16.7
1257.2 | -442.8 | 15.7 | 15.2 | 15.5 | 16.7
1258.2 | -441.8 | 15.8 | 15.2 | 15.5 | 16.7
1259.2 | -440.8 | 15.7 | 15.2 | 15.5 | 16.7
1260.2 | -439.8 | 15.7 | 15.2 | 15.6 | 16.7
1261.2 | -438.8 | 15.8 | 15.2 | 15.5 | 16.7
1262.2 | -437.8 | 15.7 | 15.2 | 15.5 | 16.7
1263.2 | -436.8 | 15.8 | 15.2 | 15.5 | 16.7
1264.2 | -435.8 | 15.8 | 15.2 | 15.5 | 16.7
1265.2 | -434.8 | 15.8 | 15.2 | 15.6 | 16.7
1266.2 | -433.8 | 15.7 | 15.2 | 15.5 | 16.7
1267.2 | -432.8 | 15.8 | 15.2 | 15.6 | 16.7
1268.2 | -431.8 | 15.8 | 15.2 | 15.6 | 16.7
1269.2 | -430.8 | 15.7 | 15.2 | 15.6 | 16.7
1270.2 | -429.8 | 15.8 | 15.2 | 15.6 | 16.7
1271.2 | -428.8 | 15.7 | 15.2 | 15.6 | 16.7
1272.2 | -427.8 | 15.8 | 15.2 | 15.6 | 16.7
1273.2 | -426.8 | 15.7 | 15.2 | 15.6 | 16.7
1274.2 | -425.8 | 15.7 | 15.2 | 15.6 | 16.7
1275.2 | -424.8 | 15.7 | 15.2 | 15.6 | 16.7
1276.2 | -423.8 | 15.8 | 15.2 | 15.6 | 16.7
1277.2 | -422.8 | 15.8 | 15.2 | 15.6 | 16.7
1278.2 | -421.8 | 15.7 | 15.2 | 15.6 | 16.7
1279.2 | -420.8 | 15.8 | 15.2 | 15.5 | 16.7
1280.2 | -419.8 | 15.7 | 15.2 | 15.5 | 16.7
1281.2 | -418.8 | 15.7 | 15.2 | 15.6 | 16.7
1282.2 | -417.8 | 15.8 | 15.2 | 15.6 | 16.7
1283.2 | -416.8 | 15.8 | 15.2 | 15.6 | 16.7
1284.2 | -415.8 | 15.7 | 15.2 | 15.6 | 16.7
1285.2 | -414.8 | 15.8 | 15.2 | 15.6 | 16.7
1286.2 | -413.8 | 15.8 | 15.2 | 15.6 | 16.7
1287.2 | -412.8 | 15.8 | 15.2 | 15.6 | 16.7
1288.2 | -411.8 | 15.8 | 15.2 | 15.6 | 16.7
1289.2 | -410.8 | 15.7 | 15.2 | 15.6 | 16.7
1290.2 | -409.8 | 15.8 | 15.2 | 15.6 | 16.7
1291.2 | -408.8 | 15.8 | 15.2 | 15.6 | 16.7
1292.2 | -407.8 | 15.8 | 15.2 | 15.6 | 16.7
1293.2 | -406.8 | 15.8 | 15.2 | 15.6 | 16.7
1294.2 | -405.8 | 15.7 | 15.2 | 15.6 | 16.7
1295.2 | -404.8 | 15.8 | 15.2 | 15.6 | 16.7
1296.2 | -403.8 | 15.8 | 15.2 | 15.6 | 16.7
1297.2 | -402.8 | 15.7 | 15.2 | 15.6 | 16.7
1298.2 | -401.8 | 15.7 | 15.2 | 15.6 | 16.7
1299.2 | -400.8 | 15.8 | 15.2 | 15.6 | 16.7
1300.2 | -399.8 | 15.8 | 15.2 | 15.5 | 16.7
1301.2 | -398.8 | 15.8 | 15.2 | 15.6 | 16.7
1302.2 | -397.8 | 15.8 | 15.2 | 15.6 | 16.7
1303.2 | -396.8 | 15.8 | 15.2 | 15.5 | 16.7
1304.2 | -395.8 | 15.8 | 15.2 | 15.6 | 16.7
1305.2 | -394.8 | 15.8 | 15.2 | 15.6 | 16.7
1306.2 | -393.8 | 15.8 | 15.2 | 15.6 | 16.7
1307.2 | -392.8 | 15.8 | 15.2 | 15.6 | 16.7
1308.2 | -391.8 | 15.8 | 15.2 | 15.6 | 16.7
1309.2 | -390.8 | 15.8 | 15.2 | 15.6 | 16.7
1310.2 | -389.8 | 15.8 | 15.2 | 15.6 | 16.7
1311.2 | -388.8 | 15.8 | 15.2 | 15.5 | 16.7
1312.2 | -387.8 | 15.8 | 15.2 | 15.6 | 16.7
1313.2 | -386.8 | 15.7 | 15.2 | 15.6 | 16.7
1314.2 | -385.8 | 15.8 | 15.2 | 15.6 | 16.7
1315.2 | -384.8 | 15.8 | 15.2 | 15.6 | 16.7
1316.2 | -383.8 | 15.8 | 15.2 | 15.6 | 16.7
1317.2 | -382.8 | 15.8 | 15.2 | 15.6 | 16.7
1318.2 | -381.8 | 15.8 | 15.2 | 15.6 | 16.7
1319.2 | -380.8 | 15.8 | 15.2 | 15.6 | 16.7
1320.2 | -379.8 | 15.8 | 15.2 | 15.6 | 16.7
1321.2 | -378.8 | 15.8 | 15.2 | 15.6 | 16.7
1322.2 | -377.8 | 15.8 | 15.2 | 15.6 | 16.7
1323.2 | -376.8 | 15.8 | 15.2 | 15.6 | 16.7
1324.2 | -375.8 | 15.8 | 15.2 | 15.6 | 16.7
1325.2 | -374.8 | 15.8 | 15.2 | 15.6 | 16.7
1326.2 | -373.8 | 15.8 | 15.2 | 15.6 | 16.7
1327.2 | -372.8 | 15.8 | 15.2 | 15.6 | 16.7
1328.2 | -371.8 | 15.8 | 15.2 | 15.6 | 16.7
1329.2 | -370.8 | 15.8 | 15.2 | 15.6 | 16.7
1330.2 | -369.8 | 15.8 | 15.2 | 15.6 | 16.7
1331.2 | -368.8 | 15.8 | 15.2 | 15.6 | 16.7
1332.2 | -367.8 | 15.8 | 15.2 | 15.6 | 16.7
1333.2 | -366.8 | 15.8 | 15.2 | 15.6 | 16.7
1334.2 | -365.8 | 15.8 | 15.2 | 15.6 | 16.7
1335.2 | -364.8 | 15.8 | 15.2 | 15.6 | 16.7
1336.2 | -363.8 | 15.8 | 15.2 | 15.6 | 16.7
1337.2 | -362.8 | 15.8 | 15.2 | 15.6 | 16.7
1338.2 | -361.8 | 15.8 | 15.2 | 15.6 | 16.7
1339.2 | -360.8 | 15.8 | 15.2 | 15.6 | 16.7
1340.2 | -359.8 | 15.8 | 15.2 | 15.6 | 16.7
1341.2 | -358.8 | 15.8 | 15.2 | 15.6 | 16.7
1342.2 | -357.8 | 15.8 | 15.2 | 15.6 | 16.7
1343.2 | -356.8 | 15.8 | 15.2 | 15.6 | 16.7
1344.2 | -355.8 | 15.8 | 15.2 | 15.6 | 16.7
1345.2 | -354.8 | 15.8 | 15.2 | 15.6 | 16.7
1346.2 | -353.8 | 15.8 | 15.2 | 15.6 | 16.7
1347.2 | -352.8 | 15.8 | 15.2 | 15.6 | 16.7
1348.2 | -351.8 | 15.8 | 15.2 | 15.6 | 16.7
1349.2 | -350.8 | 15.8 | 15.2 | 15.6 | 16.7
1350.2 | -349.8 | 15.8 | 15.2 | 15.6 | 16.7
1351.2 | -348.8 | 15.8 | 15.2 | 15.6 | 16.7
1352.2 | -347.8 | 15.7 | 15.2 | 15.6 | 16.7
1353.2 | -346.8 | 15.8 | 15.2 | 15.6 | 16.7
1354.2 | -345.8 | 15.8 | 15.2 | 15.6 | 16.7
1355.2 | -344.8 | 15.8 | 15.2 | 15.6 | 16.7
1356.2 | -343.8 | 15.8 | 15.2 | 15.6 | 16.7
1357.2 | -342.8 | 15.8 | 15.2 | 15.6 | 16.7
1358.2 | -341.8 | 15.8 | 15.2 | 15.6 | 16.7
1359.2 | -340.8 | 15.8 | 15.2 | 15.6 | 16.7
1360.2 | -339.8 | 15.8 | 15.2 | 15.6 | 16.7
1361.2 | -338.8 | 15.8 | 15.2 | 15.6 | 16.7
1362.2 | -337.8 | 15.8 | 15.2 | 15.6 | 16.7
1363.2 | -336.8 | 15.8 | 15.2 | 15.6 | 16.7
1364.2 | -335.8 | 15.8 | 15.2 | 15.6 | 16.7
1365.2 | -334.8 | 15.8 | 15.2 | 15.6 | 16.7
1366.2 | -333.8 | 15.8 | 15.2 | 15.6 | 16.7
1367.2 | -332.8 | 15.8 | 15.2 | 15.6 | 16.7
1368.2 | -331.8 | 15.8 | 15.2 | 15.6 | 16.7
1369.2 | -330.8 | 15.8 | 15.2 | 15.6 | 16.7
1370.2 | -329.8 | 15.8 | 15.2 | 15.6 | 16.7
1371.2 | -328.8 | 15.8 | 15.2 | 15.6 | 16.7
1372.2 | -327.8 | 15.8 | 15.2 | 15.6 | 16.7
1373.2 | -326.8 | 15.8 | 15.2 | 15.6 | 16.7
1374.2 | -325.8 | 15.8 | 15.2 | 15.6 | 16.7
1375.2 | -324.8 | 15.8 | 15.2 | 15.6 | 16.7
1376.2 | -323.8 | 15.8 | 15.2 | 15.6 | 16.7
1377.2 | -322.8 | 15.8 | 15.2 | 15.6 | 16.7
1378.2 | -321.8 | 15.8 | 15.2 | 15.6 | 16.7
1379.2 | -320.8 | 15.8 | 15.2 | 15.6 | 16.7
1380.2 | -319.8 | 15.8 | 15.2 | 15.6 | 16.7
1381.2 | -318.8 | 15.8 | 15.2 | 15.6 | 16.7
1382.2 | -317.8 | 15.8 | 15.2 | 15.6 | 16.7
1383.2 | -316.8 | 15.8 | 15.2 | 15.6 | 16.7
1384.2 | -315.8 | 15.8 | 15.2 | 15.6 | 16.7
1385.2 | -314.8 | 15.8 | 15.2 | 15.6 | 16.7
1386.2 | -313.8 | 15.8 | 15.2 | 15.6 | 16.7
1387.2 | -312.8 | 15.8 | 15.2 | 15.6 | 16.7
1388.2 | -311.8 | 15.8 | 15.2 | 15.6 | 16.7
1389.2 | -310.8 | 15.8 | 15.2 | 15.6 | 16.7
1390.2 | -309.8 | 15.8 | 15.2 | 15.6 | 16.7
1391.2 | -308.8 | 15.8 | 15.2 | 15.6 | 16.7
1392.2 | -307.8 | 15.8 | 15.2 | 15.6 | 16.7
1393.2 | -306.8 | 15.8 | 15.2 | 15.6 | 16.7
1394.2 | -305.8 | 15.8 | 15.2 | 15.6 | 16.7
1395.2 | -304.8 | 15.8 | 15.2 | 15.6 | 16.7
1396.2 | -303.8 | 15.8 | 15.2 | 15.6 | 16.7
1397.2 | -302.8 | 15.8 | 15.3 | 15.6 | 16.7
1398.2 | -301.8 | 15.8 | 15.2 | 15.6 | 16.7
1399.2 | -300.8 | 15.8 | 15.2 | 15.6 | 16.7
1400.2 | -299.8 | 15.8 | 15.2 | 15.6 | 16.7
1401.2 | -298.8 | 15.8 | 15.2 | 15.6 | 16.7
1402.2 | -297.8 | 15.8 | 15.2 | 15.6 | 16.7
1403.2 | -296.8 | 15.8 | 15.2 | 15.6 | 16.7
1404.2 | -295.8 | 15.8 | 15.2 | 15.6 | 16.7
1405.2 | -294.8 | 15.8 | 15.3 | 15.6 | 16.7
1406.2 | -293.8 | 15.8 | 15.3 | 15.6 | 16.7
1407.2 | -292.8 | 15.8 | 15.2 | 15.6 | 16.7
1408.2 | -291.8 | 15.8 | 15.2 | 15.6 | 16.7
1409.2 | -290.8 | 15.8 | 15.2 | 15.6 | 16.7
1410.2 | -289.8 | 15.8 | 15.2 | 15.6 | 16.7
1411.2 | -288.8 | 15.8 | 15.2 | 15.6 | 16.7
1412.2 | -287.8 | 15.8 | 15.2 | 15.6 | 16.7
1413.2 | -286.8 | 15.8 | 15.2 | 15.6 | 16.7
1414.2 | -285.8 | 15.8 | 15.2 | 15.6 | 16.7
1415.2 | -284.8 | 15.8 | 15.2 | 15.6 | 16.7
1416.2 | -283.8 | 15.8 | 15.2 | 15.6 | 16.7
1417.2 | -282.8 | 15.8 | 15.3 | 15.6 | 16.7
1418.2 | -281.8 | 15.8 | 15.2 | 15.6 | 16.7
1419.2 | -280.8 | 15.8 | 15.2 | 15.6 | 16.7
1420.2 | -279.8 | 15.8 | 15.2 | 15.6 | 16.7
1421.2 | -278.8 | 15.8 | 15.2 | 15.6 | 16.7
1422.2 | -277.8 | 15.8 | 15.2 | 15.6 | 16.7
1423.2 | -276.8 | 15.8 | 15.2 | 15.6 | 16.7
1424.2 | -275.8 | 15.8 | 15.2 | 15.6 | 16.7
1425.2 | -274.8 | 15.8 | 15.2 | 15.6 | 16.7
1426.2 | -273.8 | 15.8 | 15.2 | 15.6 | 16.7
1427.2 | -272.8 | 15.8 | 15.2 | 15.6 | 16.7
1428.2 | -271.8 | 15.8 | 15.2 | 15.6 | 16.7
1429.2 | -270.8 | 15.8 | 15.2 | 15.6 | 16.7
1430.2 | -269.8 | 15.8 | 15.2 | 15.6 | 16.7
1431.2 | -268.8 | 15.8 | 15.3 | 15.6 | 16.7
1432.2 | -267.8 | 15.8 | 15.2 | 15.6 | 16.7
1433.2 | -266.8 | 15.8 | 15.2 | 15.6 | 16.7
1434.2 | -265.8 | 15.8 | 15.2 | 15.6 | 16.7
1435.2 | -264.8 | 15.8 | 15.2 | 15.6 | 16.7
1436.2 | -263.8 | 15.8 | 15.2 | 15.6 | 16.7
1437.2 | -262.8 | 15.8 | 15.2 | 15.6 | 16.7
1438.2 | -261.8 | 15.8 | 15.2 | 15.6 | 16.7
1439.2 | -260.8 | 15.8 | 15.2 | 15.6 | 16.7
1440.2 | -259.8 | 15.8 | 15.2 | 15.6 | 16.7
1441.2 | -258.8 | 15.8 | 15.2 | 15.6 | 16.7
1442.2 | -257.8 | 15.8 | 15.2 | 15.6 | 16.7
1443.2 | -256.8 | 15.8 | 15.2 | 15.6 | 16.7
1444.2 | -255.8 | 15.8 | 15.2 | 15.6 | 16.7
1445.2 | -254.8 | 15.8 | 15.2 | 15.6 | 16.7
1446.2 | -253.8 | 15.8 | 15.2 | 15.6 | 16.7
1447.2 | -252.8 | 15.8 | 15.2 | 15.6 | 16.7
1448.2 | -251.8 | 15.8 | 15.2 | 15.6 | 16.7
1449.2 | -250.8 | 15.8 | 15.2 | 15.6 | 16.7
1450.2 | -249.8 | 15.8 | 15.2 | 15.6 | 16.7
1451.2 | -248.8 | 15.8 | 15.2 | 15.6 | 16.7
1452.2 | -247.8 | 15.8 | 15.2 | 15.6 | 16.7
1453.2 | -246.8 | 15.8 | 15.2 | 15.6 | 16.7
1454.2 | -245.8 | 15.8 | 15.2 | 15.6 | 16.7
1455.2 | -244.8 | 15.8 | 15.2 | 15.6 | 16.7
1456.2 | -243.8 | 15.8 | 15.2 | 15.6 | 16.7
1457.2 | -242.8 | 15.8 | 15.2 | 15.6 | 16.7
1458.2 | -241.8 | 15.8 | 15.2 | 15.6 | 16.7
1459.2 | -240.8 | 15.8 | 15.2 | 15.6 | 16.7
1460.2 | -239.8 | 15.8 | 15.2 | 15.6 | 16.7
1461.2 | -238.8 | 15.8 | 15.2 | 15.6 | 16.7
1462.2 | -237.8 | 15.8 | 15.2 | 15.6 | 16.7
1463.2 | -236.8 | 15.8 | 15.2 | 15.6 | 16.7
1464.2 | -235.8 | 15.8 | 15.2 | 15.6 | 16.7
1465.2 | -234.8 | 15.8 | 15.2 | 15.6 | 16.7
1466.2 | -233.8 | 15.8 | 15.2 | 15.6 | 16.7
1467.2 | -232.8 | 15.8 | 15.2 | 15.6 | 16.7
1468.2 | -231.8 | 15.8 | 15.2 | 15.6 | 16.7
1469.2 | -230.8 | 15.8 | 15.2 | 15.6 | 16.7
1470.2 | -229.8 | 15.8 | 15.2 | 15.6 | 16.7
1471.2 | -228.8 | 15.8 | 15.2 | 15.6 | 16.7
1472.2 | -227.8 | 15.8 | 15.2 | 15.6 | 16.7
1473.2 | -226.8 | 15.8 | 15.2 | 15.6 | 16.7
1474.2 | -225.8 | 15.8 | 15.2 | 15.6 | 16.7
1475.2 | -224.8 | 15.8 | 15.2 | 15.6 | 16.7
1476.2 | -223.8 | 15.8 | 15.2 | 15.6 | 16.7
1477.2 | -222.8 | 15.8 | 15.2 | 15.6 | 16.7
1478.2 | -221.8 | 15.8 | 15.2 | 15.6 | 16.7
1479.2 | -220.8 | 15.8 | 15.2 | 15.6 | 16.7
1480.2 | -219.8 | 15.8 | 15.2 | 15.6 | 16.7
1481.2 | -218.8 | 15.8 | 15.2 | 15.6 | 16.7
1482.2 | -217.8 | 15.8 | 15.2 | 15.6 | 16.7
1483.2 | -216.8 | 15.8 | 15.2 | 15.6 | 16.7
1484.2 | -215.8 | 15.8 | 15.2 | 15.6 | 16.7
1485.2 | -214.8 | 15.8 | 15.2 | 15.6 | 16.7
1486.2 | -213.8 | 15.8 | 15.2 | 15.6 | 16.7
1487.2 | -212.8 | 15.8 | 15.2 | 15.6 | 16.7
1488.2 | -211.8 | 15.8 | 15.2 | 15.6 | 16.7
1489.2 | -210.8 | 15.8 | 15.2 | 15.6 | 16.7
1490.2 | -209.8 | 15.8 | 15.2 | 15.6 | 16.7
1491.2 | -208.8 | 15.8 | 15.2 | 15.6 | 16.7
1492.2 | -207.8 | 15.8 | 15.2 | 15.6 | 16.7
1493.2 | -206.8 | 15.8 | 15.2 | 15.6 | 16.7
1494.2 | -205.8 | 15.8 | 15.2 | 15.6 | 16.7
1495.2 | -204.8 | 15.8 | 15.2 | 15.6 | 16.7
1496.2 | -203.8 | 15.8 | 15.2 | 15.6 | 16.7
1497.2 | -202.8 | 15.8 | 15.2 | 15.6 | 16.7
1498.2 | -201.8 | 15.8 | 15.2 | 15.6 | 16.7
1499.2 | -200.8 | 15.8 | 15.2 | 15.6 | 16.7
1500.2 | -199.8 | 15.8 | 15.2 | 15.6 | 16.7
1501.2 | -198.8 | 15.8 | 15.2 | 15.6 | 16.7
1502.2 | -197.8 | 15.8 | 15.2 | 15.6 | 16.7
1503.2 | -196.8 | 15.8 | 15.2 | 15.6 | 16.7
1504.2 | -195.8 | 15.8 | 15.2 | 15.6 | 16.7
1505.2 | -194.8 | 15.8 | 15.2 | 15.6 | 16.7
1506.2 | -193.8 | 15.8 | 15.2 | 15.6 | 16.7
1507.2 | -192.8 | 15.8 | 15.2 | 15.6 | 16.7
1508.2 | -191.8 | 15.8 | 15.2 | 15.6 | 16.7
1509.2 | -190.8 | 15.8 | 15.2 | 15.6 | 16.7
1510.2 | -189.8 | 15.8 | 15.2 | 15.6 | 16.7
1511.2 | -188.8 | 15.8 | 15.2 | 15.6 | 16.7
1512.2 | -187.8 | 15.8 | 15.2 | 15.6 | 16.7
1513.2 | -186.8 | 15.8 | 15.2 | 15.6 | 16.7
1514.2 | -185.8 | 15.8 | 15.2 | 15.6 | 16.7
1515.2 | -184.8 | 15.8 | 15.2 | 15.6 | 16.7
1516.2 | -183.8 | 15.8 | 15.2 | 15.6 | 16.7
1517.2 | -182.8 | 15.8 | 15.2 | 15.6 | 16.7
1518.2 | -181.8 | 15.8 | 15.2 | 15.6 | 16.7
1519.2 | -180.8 | 15.8 | 15.2 | 15.6 | 16.7
1520.2 | -179.8 | 15.8 | 15.2 | 15.6 | 16.7
1521.2 | -178.8 | 15.8 | 15.2 | 15.6 | 16.7
1522.2 | -177.8 | 15.8 | 15.2 | 15.6 | 16.7
1523.2 | -176.8 | 15.8 | 15.2 | 15.6 | 16.7
1524.2 | -175.8 | 15.8 | 15.2 | 15.6 | 16.7
1525.2 | -174.8 | 15.8 | 15.2 | 15.6 | 16.7
1526.2 | -173.8 | 15.8 | 15.2 | 15.6 | 16.7
1527.2 | -172.8 | 15.8 | 15.2 | 15.6 | 16.7
1528.2 | -171.8 | 15.8 | 15.2 | 15.6 | 16.7
1529.2 | -170.8 | 15.8 | 15.2 | 15.6 | 16.7
1530.2 | -169.8 | 15.8 | 15.2 | 15.6 | 16.7
1531.2 | -168.8 | 15.8 | 15.2 | 15.6 | 16.7
1532.2 | -167.8 | 15.8 | 15.2 | 15.6 | 16.7
1533.2 | -166.8 | 15.8 | 15.2 | 15.6 | 16.7
1534.2 | -165.8 | 15.8 | 15.2 | 15.6 | 16.7
1535.2 | -164.8 | 15.8 | 15.2 | 15.6 | 16.7
1536.2 | -163.8 | 15.8 | 15.2 | 15.6 | 16.7
1537.2 | -162.8 | 15.8 | 15.2 | 15.6 | 16.7
1538.2 | -161.8 | 15.8 | 15.2 | 15.6 | 16.7
1539.2 | -160.8 | 15.8 | 15.2 | 15.6 | 16.7
1540.2 | -159.8 | 15.8 | 15.2 | 15.6 | 16.7
1541.2 | -158.8 | 15.8 | 15.2 | 15.6 | 16.7
1542.2 | -157.8 | 15.8 | 15.2 | 15.6 | 16.7
1543.2 | -156.8 | 15.8 | 15.2 | 15.6 | 16.7
1544.2 | -155.8 | 15.8 | 15.3 | 15.6 | 16.7
1545.2 | -154.8 | 15.8 | 15.3 | 15.6 | 16.7
1546.2 | -153.8 | 15.8 | 15.3 | 15.6 | 16.7
1547.2 | -152.8 | 15.8 | 15.3 | 15.6 | 16.7
1548.2 | -151.8 | 15.8 | 15.2 | 15.6 | 16.7
1549.2 | -150.8 | 15.8 | 15.2 | 15.6 | 16.7
1550.2 | -149.8 | 15.8 | 15.3 | 15.6 | 16.7
1551.2 | -148.8 | 15.8 | 15.3 | 15.6 | 16.7
1552.2 | -147.8 | 15.8 | 15.3 | 15.6 | 16.7
1553.2 | -146.8 | 15.8 | 15.3 | 15.6 | 16.7
1554.2 | -145.8 | 15.8 | 15.2 | 15.6 | 16.7
1555.2 | -144.8 | 15.8 | 15.3 | 15.6 | 16.7
1556.2 | -143.8 | 15.8 | 15.3 | 15.6 | 16.7
1557.2 | -142.8 | 15.8 | 15.3 | 15.6 | 16.7
1558.2 | -141.8 | 15.8 | 15.3 | 15.6 | 16.7
1559.2 | -140.8 | 15.8 | 15.2 | 15.6 | 16.7
1560.2 | -139.8 | 15.8 | 15.3 | 15.6 | 16.7
1561.2 | -138.8 | 15.8 | 15.2 | 15.6 | 16.7
1562.2 | -137.8 | 15.8 | 15.3 | 15.6 | 16.7
1563.2 | -136.8 | 15.8 | 15.3 | 15.6 | 16.7
1564.2 | -135.8 | 15.8 | 15.3 | 15.6 | 16.7
1565.2 | -134.8 | 15.8 | 15.3 | 15.6 | 16.7
1566.2 | -133.8 | 15.8 | 15.3 | 15.6 | 16.7
1567.2 | -132.8 | 15.8 | 15.3 | 15.6 | 16.7
1568.2 | -131.8 | 15.8 | 15.3 | 15.6 | 16.7
1569.2 | -130.8 | 15.8 | 15.3 | 15.6 | 16.7
1570.2 | -129.8 | 15.8 | 15.3 | 15.6 | 16.7
1571.2 | -128.8 | 15.8 | 15.3 | 15.6 | 16.7
1572.2 | -127.8 | 15.8 | 15.3 | 15.6 | 16.7
1573.2 | -126.8 | 15.8 | 15.3 | 15.6 | 16.7
1574.2 | -125.8 | 15.8 | 15.3 | 15.6 | 16.7
1575.2 | -124.8 | 15.8 | 15.3 | 15.6 | 16.7
1576.2 | -123.8 | 15.8 | 15.3 | 15.6 | 16.7
1577.2 | -122.8 | 15.8 | 15.3 | 15.6 | 16.7
1578.2 | -121.8 | 15.8 | 15.2 | 15.6 | 16.7
1579.2 | -120.8 | 15.8 | 15.3 | 15.6 | 16.7
1580.2 | -119.8 | 15.8 | 15.2 | 15.6 | 16.7
1581.2 | -118.8 | 15.8 | 15.2 | 15.6 | 16.7
1582.2 | -117.8 | 15.8 | 15.2 | 15.6 | 16.7
1583.2 | -116.8 | 15.8 | 15.3 | 15.6 | 16.7
1584.2 | -115.8 | 15.8 | 15.2 | 15.6 | 16.7
1585.2 | -114.8 | 15.8 | 15.2 | 15.6 | 16.7
1586.2 | -113.8 | 15.8 | 15.2 | 15.6 | 16.7
1587.2 | -112.8 | 15.8 | 15.2 | 15.6 | 16.7
1588.2 | -111.8 | 15.8 | 15.2 | 15.6 | 16.7
1589.2 | -110.8 | 15.8 | 15.2 | 15.6 | 16.7
1590.2 | -109.8 | 15.8 | 15.2 | 15.6 | 16.7
1591.2 | -108.8 | 15.8 | 15.2 | 15.6 | 16.7
1592.2 | -107.8 | 15.8 | 15.2 | 15.6 | 16.7
1593.2 | -106.8 | 15.8 | 15.2 | 15.6 | 16.7
1594.2 | -105.8 | 15.8 | 15.3 | 15.6 | 16.7
1595.2 | -104.8 | 15.8 | 15.3 | 15.6 | 16.7
1596.2 | -103.8 | 15.8 | 15.3 | 15.6 | 16.7
1597.2 | -102.8 | 15.8 | 15.2 | 15.6 | 16.7
1598.2 | -101.8 | 15.8 | 15.3 | 15.6 | 16.7
1599.2 | -100.8 | 15.8 | 15.2 | 15.6 | 16.7
1600.2 | -99.8 | 15.8 | 15.3 | 15.6 | 16.7
1601.2 | -98.8 | 15.8 | 15.3 | 15.6 | 16.7
1602.2 | -97.8 | 15.8 | 15.2 | 15.6 | 16.7
1603.2 | -96.8 | 15.8 | 15.2 | 15.6 | 16.7
1604.2 | -95.8 | 15.8 | 15.3 | 15.6 | 16.7
1605.2 | -94.8 | 15.8 | 15.3 | 15.6 | 16.7
1606.2 | -93.8 | 15.8 | 15.3 | 15.6 | 16.7
1607.2 | -92.8 | 15.8 | 15.2 | 15.6 | 16.7
1608.2 | -91.8 | 15.8 | 15.3 | 15.6 | 16.7
1609.2 | -90.8 | 15.8 | 15.2 | 15.6 | 16.7
1610.2 | -89.8 | 15.8 | 15.2 | 15.6 | 16.7
1611.2 | -88.8 | 15.8 | 15.2 | 15.6 | 16.7
1612.2 | -87.8 | 15.8 | 15.2 | 15.6 | 16.7
1613.2 | -86.8 | 15.8 | 15.2 | 15.6 | 16.7
1614.2 | -85.8 | 15.8 | 15.3 | 15.6 | 16.7
1615.2 | -84.8 | 15.8 | 15.2 | 15.6 | 16.7
1616.2 | -83.8 | 15.8 | 15.2 | 15.6 | 16.7
1617.2 | -82.8 | 15.8 | 15.2 | 15.6 | 16.7
1618.2 | -81.8 | 15.8 | 15.2 | 15.6 | 16.7
1619.2 | -80.8 | 15.8 | 15.2 | 15.6 | 16.7
1620.2 | -79.8 | 15.8 | 15.2 | 15.6 | 16.7
1621.2 | -78.8 | 15.8 | 15.2 | 15.6 | 16.7
1622.2 | -77.8 | 15.8 | 15.2 | 15.6 | 16.7
1623.2 | -76.8 | 15.8 | 15.2 | 15.6 | 16.7
1624.2 | -75.8 | 15.8 | 15.2 | 15.6 | 16.7
1625.2 | -74.8 | 15.8 | 15.2 | 15.6 | 16.7
1626.2 | -73.8 | 15.8 | 15.2 | 15.6 | 16.7
1627.2 | -72.8 | 15.8 | 15.2 | 15.6 | 16.7
1628.2 | -71.8 | 15.8 | 15.2 | 15.6 | 16.7
1629.2 | -70.8 | 15.8 | 15.2 | 15.6 | 16.7
1630.2 | -69.8 | 15.8 | 15.2 | 15.6 | 16.7
1631.2 | -68.8 | 15.8 | 15.2 | 15.6 | 16.7
1632.2 | -67.8 | 15.8 | 15.2 | 15.6 | 16.7
1633.2 | -66.8 | 15.8 | 15.2 | 15.6 | 16.7
1634.2 | -65.8 | 15.8 | 15.2 | 15.6 | 16.7
1635.2 | -64.8 | 15.8 | 15.2 | 15.6 | 16.7
1636.2 | -63.8 | 15.8 | 15.2 | 15.6 | 16.7
1637.2 | -62.8 | 15.8 | 15.2 | 15.6 | 16.7
1638.2 | -61.8 | 15.8 | 15.2 | 15.6 | 16.7
1639.2 | -60.8 | 15.8 | 15.2 | 15.6 | 16.7
1640.2 | -59.8 | 15.8 | 15.2 | 15.6 | 16.7
1641.2 | -58.8 | 15.8 | 15.2 | 15.6 | 16.7
1642.2 | -57.8 | 15.8 | 15.2 | 15.6 | 16.7
1643.2 | -56.8 | 15.8 | 15.2 | 15.6 | 16.7
1644.2 | -55.8 | 15.8 | 15.2 | 15.6 | 16.7
1645.2 | -54.8 | 15.8 | 15.2 | 15.6 | 16.7
1646.2 | -53.8 | 15.8 | 15.2 | 15.6 | 16.7
1647.2 | -52.8 | 15.8 | 15.2 | 15.6 | 16.7
1648.2 | -51.8 | 15.8 | 15.2 | 15.6 | 16.7
1649.2 | -50.8 | 15.8 | 15.2 | 15.6 | 16.7
1650.2 | -49.8 | 15.8 | 15.2 | 15.6 | 16.7
1651.2 | -48.8 | 15.8 | 15.2 | 15.6 | 16.7
1652.2 | -47.8 | 15.8 | 15.3 | 15.6 | 16.7
1653.2 | -46.8 | 15.8 | 15.2 | 15.6 | 16.7
1654.2 | -45.8 | 15.8 | 15.3 | 15.6 | 16.7
1655.2 | -44.8 | 15.8 | 15.3 | 15.6 | 16.7
1656.2 | -43.8 | 15.8 | 15.2 | 15.6 | 16.7
1657.2 | -42.8 | 15.8 | 15.2 | 15.6 | 16.7
1658.2 | -41.8 | 15.8 | 15.2 | 15.6 | 16.7
1659.2 | -40.8 | 15.8 | 15.3 | 15.6 | 16.7
1660.2 | -39.8 | 15.8 | 15.3 | 15.6 | 16.7
1661.2 | -38.8 | 15.8 | 15.2 | 15.6 | 16.7
1662.2 | -37.8 | 15.8 | 15.3 | 15.6 | 16.7
1663.2 | -36.8 | 15.8 | 15.2 | 15.6 | 16.7
1664.2 | -35.8 | 15.8 | 15.2 | 15.6 | 16.7
1665.2 | -34.8 | 15.8 | 15.2 | 15.6 | 16.7
1666.2 | -33.8 | 15.8 | 15.2 | 15.6 | 16.7
1667.2 | -32.8 | 15.8 | 15.2 | 15.6 | 16.7
1668.2 | -31.8 | 15.8 | 15.2 | 15.6 | 16.7
1669.2 | -30.8 | 15.8 | 15.3 | 15.6 | 16.7
1670.2 | -29.8 | 15.8 | 15.3 | 15.6 | 16.7
1671.2 | -28.8 | 15.8 | 15.3 | 15.6 | 16.7
1672.2 | -27.8 | 15.8 | 15.3 | 15.6 | 16.7
1673.2 | -26.8 | 15.8 | 15.3 | 15.6 | 16.7
1674.2 | -25.8 | 15.8 | 15.3 | 15.6 | 16.7
1675.2 | -24.8 | 15.8 | 15.3 | 15.6 | 16.7
1676.2 | -23.8 | 15.8 | 15.3 | 15.6 | 16.7
1677.2 | -22.8 | 15.8 | 15.2 | 15.6 | 16.7
1678.2 | -21.8 | 15.8 | 15.3 | 15.6 | 16.7
1679.2 | -20.8 | 15.8 | 15.3 | 15.6 | 16.7
1680.2 | -19.8 | 15.8 | 15.2 | 15.6 | 16.7
1681.2 | -18.8 | 15.8 | 15.3 | 15.6 | 16.7
1682.2 | -17.8 | 15.8 | 15.3 | 15.6 | 16.7
1683.2 | -16.8 | 15.8 | 15.3 | 15.6 | 16.7
1684.2 | -15.8 | 15.8 | 15.3 | 15.6 | 16.7
1685.2 | -14.8 | 15.8 | 15.3 | 15.6 | 16.8
1686.2 | -13.8 | 15.8 | 15.3 | 15.6 | 16.7
1687.2 | -12.8 | 15.8 | 15.3 | 15.6 | 16.8
1688.2 | -11.8 | 15.8 | 15.3 | 15.6 | 16.7
1689.2 | -10.8 | 15.8 | 15.3 | 15.6 | 16.8
1690.2 | -9.8 | 15.8 | 15.3 | 15.7 | 16.8
1691.2 | -8.8 | 15.8 | 15.3 | 15.7 | 16.8
1692.2 | -7.8 | 15.8 | 15.3 | 15.7 | 16.8
1693.2 | -6.8 | 15.8 | 15.3 | 15.7 | 16.8
1694.2 | -5.8 | 15.8 | 15.3 | 15.7 | 16.9
1695.2 | -4.8 | 15.8 | 15.3 | 15.7 | 16.9
1696.2 | -3.8 | 15.8 | 15.3 | 15.8 | 16.9
1697.2 | -2.8 | 15.8 | 15.3 | 15.8 | 16.9
1698.2 | -1.8 | 15.8 | 15.3 | 15.8 | 16.9
1699.2 | -0.8 | 15.8 | 15.3 | 15.8 | 16.9
1700.2 | 0.2 | 15.8 | 15.3 | 15.8 | 16.9
1701.2 | 1.2 | 15.8 | 15.3 | 15.8 | 16.8
1702.2 | 2.2 | 15.8 | 15.3 | 15.8 | 16.8
1703.2 | 3.2 | 15.8 | 15.3 | 15.8 | 16.8
1704.2 | 4.2 | 15.8 | 15.3 | 15.8 | 16.8
1705.2 | 5.2 | 15.8 | 15.3 | 15.7 | 16.8
1706.2 | 6.2 | 15.8 | 15.3 | 15.8 | 16.8
1707.2 | 7.2 | 15.8 | 16 | 19.2 | 17.6
1708.2 | 8.2 | 15.8 | 19.5 | 28.4 | 20.1
1709.2 | 9.2 | 15.8 | 28.6 | 53.6 | 30
1710.2 | 10.2 | 15.9 | 43.9 | 83.3 | 42.5
1711.2 | 11.2 | 16 | 64.7 | 111.6 | 55.8
1712.2 | 12.2 | 16.3 | 80.1 | 152.5 | 65.3
1713.2 | 13.2 | 16.8 | 96.4 | 211.7 | 85.2
1714.2 | 14.2 | 17.6 | 125.5 | 244.2 | 99.8
1715.2 | 15.2 | 18.7 | 145.9 | 265.4 | 108.4
1716.2 | 16.2 | 20.2 | 164.3 | 277.9 | 111.9
1717.2 | 17.2 | 22 | 178.7 | 294.7 | 119.1
1718.2 | 18.2 | 24.1 | 197.7 | 320.7 | 121.4
1719.2 | 19.2 | 26.2 | 215.1 | 324.7 | 126.4
1720.2 | 20.2 | 28.6 | 228.3 | 336.6 | 132.4
1721.2 | 21.2 | 31.1 | 238.2 | 345.4 | 134.5
1722.2 | 22.2 | 33.7 | 247.1 | 351.4 | 127.7
1723.2 | 23.2 | 36.3 | 257.5 | 354.1 | 122.2
1724.2 | 24.2 | 39 | 268.8 | 353.8 | 119.2
1725.2 | 25.2 | 41.7 | 278.5 | 353.9 | 119
1726.2 | 26.2 | 44.4 | 286.6 | 346.6 | 117.9
1727.2 | 27.2 | 47 | 293.3 | 342.2 | 118.4
1728.2 | 28.2 | 49.6 | 291.3 | 338.6 | 121.5
1729.2 | 29.2 | 52.1 | 287.3 | 331.4 | 123.2
1730.2 | 30.2 | 54.5 | 290.3 | 328.5 | 121.2
1731.2 | 31.2 | 56.8 | 296.2 | 337.9 | 123.2
1732.2 | 32.2 | 59 | 294.3 | 337.6 | 128.9
1733.2 | 33.2 | 61.1 | 298.7 | 344.8 | 134.9
1734.2 | 34.2 | 63.1 | 296.8 | 343.9 | 135.7
1735.2 | 35.2 | 65.1 | 295.4 | 346.4 | 140.4
1736.2 | 36.2 | 67 | 291.8 | 338 | 141.4
1737.2 | 37.2 | 68.9 | 295.2 | 341 | 143.2
1738.2 | 38.2 | 70.7 | 300.6 | 350 | 146.3
1739.2 | 39.2 | 72.5 | 309.8 | 364.6 | 151
1740.2 | 40.2 | 74.2 | 315.1 | 368.5 | 155.4
1741.2 | 41.2 | 75.9 | 312.5 | 355.6 | 156.2
1742.2 | 42.2 | 77.6 | 308.9 | 342.5 | 149.9
1743.2 | 43.2 | 79.3 | 301.6 | 330.8 | 147
1744.2 | 44.2 | 81 | 300.1 | 329.8 | 151.3
1745.2 | 45.2 | 82.6 | 293.5 | 319.6 | 149
1746.2 | 46.2 | 84.2 | 295.4 | 311.8 | 147.3
1747.2 | 47.2 | 85.6 | 287.5 | 300.8 | 145.2
1748.2 | 48.2 | 87 | 277.8 | 294 | 144.6
1749.2 | 49.2 | 88.3 | 274.1 | 290.2 | 146.3
1750.2 | 50.2 | 89.4 | 275.1 | 296.5 | 155.9
1751.2 | 51.2 | 90.5 | 275.5 | 304.6 | 167.3
1752.2 | 52.2 | 91.4 | 282.6 | 302.4 | 167
1753.2 | 53.2 | 92.3 | 278.7 | 295.6 | 167.1
1754.2 | 54.2 | 93.2 | 275.6 | 289.9 | 163.4
1755.2 | 55.2 | 93.9 | 274.3 | 296.2 | 168.4
1756.2 | 56.2 | 94.4 | 271.7 | 304.5 | 175.1
1757.2 | 57.2 | 94.1 | 268.6 | 308 | 178.9
1758.2 | 58.2 | 94.1 | 267.6 | 312.8 | 185.1
1759.2 | 59.2 | 94.2 | 264.4 | 310 | 191.2
1760.2 | 60.2 | 94.4 | 264 | 308 | 192.5
1761.2 | 61.2 | 94.7 | 265.3 | 327.7 | 199.4
1762.2 | 62.2 | 95 | 266.6 | 329.4 | 204.1
1763.2 | 63.2 | 95.4 | 268.3 | 323.7 | 202.7
1764.2 | 64.2 | 95.8 | 264.8 | 319.4 | 200.2
1765.2 | 65.2 | 96.1 | 263.6 | 316.3 | 196.5
1766.2 | 66.2 | 96.3 | 258.5 | 321.1 | 197.7
1767.2 | 67.2 | 96.2 | 255.9 | 322.3 | 203.2
1768.2 | 68.2 | 96.2 | 250.6 | 311.2 | 203.5
1769.2 | 69.2 | 96.4 | 250.4 | 306.3 | 202.3
1770.2 | 70.2 | 96.7 | 250.7 | 311.5 | 205.1
1771.2 | 71.2 | 97.2 | 248.6 | 313.5 | 208.7
1772.2 | 72.2 | 97.7 | 248.9 | 327.6 | 214
1773.2 | 73.2 | 98.7 | 250.7 | 340.9 | 217.2
1774.2 | 74.2 | 99.8 | 250.4 | 344.7 | 220.1
1775.2 | 75.2 | 100.6 | 253.5 | 349.9 | 224.3
1776.2 | 76.2 | 101.4 | 257.1 | 352.4 | 227
1777.2 | 77.2 | 102.2 | 257 | 348.7 | 225.3
1778.2 | 78.2 | 103 | 256.6 | 345.5 | 224.1
1779.2 | 79.2 | 103.8 | 263.2 | 355.4 | 228.5
1780.2 | 80.2 | 104.7 | 268.9 | 350.1 | 228.3
1781.2 | 81.2 | 105.6 | 274.3 | 349.4 | 229.6
1782.2 | 82.2 | 106.4 | 283 | 361.9 | 231.5
1783.2 | 83.2 | 107.2 | 290.4 | 364.1 | 233.4
1784.2 | 84.2 | 108 | 297.1 | 358.8 | 228.6
1785.2 | 85.2 | 108.8 | 297.9 | 351.8 | 224.9
1786.2 | 86.2 | 109.6 | 296.1 | 356.3 | 224.4
1787.2 | 87.2 | 110.3 | 293.1 | 350.8 | 223.8
1788.2 | 88.2 | 111.1 | 295.7 | 350.2 | 223.3
1789.2 | 89.2 | 111.9 | 294.6 | 350.6 | 225.3
1790.2 | 90.2 | 112.6 | 293.7 | 342.9 | 226.4
1791.2 | 91.2 | 113.4 | 292.5 | 339 | 223.8
1792.2 | 92.2 | 114.2 | 296.6 | 341 | 223.2
1793.2 | 93.2 | 115 | 298.9 | 342.4 | 223.4
1794.2 | 94.2 | 115.7 | 298.5 | 337.4 | 221.7
1795.2 | 95.2 | 116.5 | 296.7 | 325.5 | 220.4
1796.2 | 96.2 | 117.2 | 296.8 | 325.1 | 221.3
1797.2 | 97.2 | 117.9 | 299.1 | 320.1 | 224.5
1798.2 | 98.2 | 118.6 | 304.9 | 326.6 | 227.9
1799.2 | 99.2 | 119.3 | 318.3 | 332.6 | 227.8
1800.2 | 100.2 | 119.9 | 318.1 | 328.2 | 223
1801.2 | 101.2 | 120.6 | 320.9 | 328.3 | 224
1802.2 | 102.2 | 121.3 | 322.4 | 325.9 | 223.5
1803.2 | 103.2 | 121.9 | 326 | 325.7 | 223.2
1804.2 | 104.2 | 122.6 | 321.9 | 320 | 220.1
1805.2 | 105.2 | 123.3 | 322.9 | 316.4 | 219.1
1806.2 | 106.2 | 124 | 319.3 | 309.6 | 218
1807.2 | 107.2 | 124.7 | 312 | 303.3 | 216.7
1808.2 | 108.2 | 125.4 | 308.5 | 292.5 | 215.2
1809.2 | 109.2 | 126 | 305.6 | 286.9 | 214.3
1810.2 | 110.2 | 126.6 | 305.3 | 290.6 | 218.2
1811.2 | 111.2 | 127.1 | 301.2 | 286.6 | 219.4
1812.2 | 112.2 | 127.6 | 300.8 | 283.8 | 217.3
1813.2 | 113.2 | 128.1 | 297.6 | 282.1 | 216.3
1814.2 | 114.2 | 128.6 | 299.1 | 293.4 | 224.1
1815.2 | 115.2 | 129 | 297.6 | 296.9 | 226.2
1816.2 | 116.2 | 129.4 | 294.4 | 294.9 | 224.6
1817.2 | 117.2 | 129.8 | 290.9 | 290 | 222.1
1818.2 | 118.2 | 130.3 | 294.9 | 290.3 | 221.3
1819.2 | 119.2 | 130.7 | 299.4 | 293.5 | 221.7
1820.2 | 120.2 | 131.2 | 306.2 | 298.2 | 223.6
1821.2 | 121.2 | 131.6 | 304.8 | 299.7 | 226.9
1822.2 | 122.2 | 132 | 304.7 | 302.7 | 227.7
1823.2 | 123.2 | 132.5 | 300.8 | 305 | 228.1
1824.2 | 124.2 | 132.9 | 302 | 314.3 | 230.8
1825.2 | 125.2 | 133.2 | 304.9 | 319.1 | 232.1
1826.2 | 126.2 | 133.6 | 300.4 | 311.9 | 230.9
1827.2 | 127.2 | 134 | 295.5 | 307.3 | 229.8
1828.2 | 128.2 | 134.5 | 291.9 | 308.1 | 229.4
1829.2 | 129.2 | 135 | 297.9 | 313.1 | 233.3
1830.2 | 130.2 | 135.5 | 303.6 | 317.7 | 237.2
1831.2 | 131.2 | 135.9 | 300.8 | 319.9 | 240.8
1832.2 | 132.2 | 136.4 | 293.7 | 314.2 | 239.5
1833.2 | 133.2 | 136.9 | 289.3 | 312.6 | 234.6
1834.2 | 134.2 | 137.4 | 286.6 | 312.2 | 236.6
1835.2 | 135.2 | 137.9 | 290.5 | 318.2 | 243.4
1836.2 | 136.2 | 138.4 | 290.8 | 317 | 246.3
1837.2 | 137.2 | 139 | 290 | 325.1 | 256.5
1838.2 | 138.2 | 139.5 | 286.6 | 325.6 | 259
1839.2 | 139.2 | 140 | 283.9 | 323.3 | 253.9
1840.2 | 140.2 | 140.5 | 287.7 | 325.5 | 249.7
1841.2 | 141.2 | 141.2 | 289.5 | 332.6 | 248.2
1842.2 | 142.2 | 141.9 | 287.4 | 334.5 | 249.8
1843.2 | 143.2 | 142.5 | 286.6 | 328.6 | 248.5
1844.2 | 144.2 | 143.2 | 285.4 | 326.9 | 244.8
1845.2 | 145.2 | 144 | 287.3 | 325.4 | 245.1
1846.2 | 146.2 | 144.7 | 299.6 | 331.4 | 248.7
1847.2 | 147.2 | 145.5 | 304.3 | 340.3 | 251.7
1848.2 | 148.2 | 146.2 | 303.3 | 332.7 | 251
1849.2 | 149.2 | 147 | 305.2 | 331.6 | 255.1
1850.2 | 150.2 | 147.7 | 305.1 | 323.6 | 254.3
1851.2 | 151.2 | 148.4 | 301.6 | 325.9 | 258.8
1852.2 | 152.2 | 149 | 300.8 | 323.3 | 260.2
1853.2 | 153.2 | 149.7 | 298.2 | 324 | 257.9
1854.2 | 154.2 | 150.3 | 295.1 | 330.8 | 258.3
1855.2 | 155.2 | 150.9 | 297.7 | 333.9 | 260.3
1856.2 | 156.2 | 151.5 | 297.9 | 335.7 | 266
1857.2 | 157.2 | 152 | 291.1 | 341.4 | 269.9
1858.2 | 158.2 | 152.5 | 288.1 | 351.1 | 275.9
1859.2 | 159.2 | 153 | 290.6 | 357.5 | 282.7
1860.2 | 160.2 | 153.5 | 292.8 | 373.5 | 285.2
1861.2 | 161.2 | 154 | 295 | 370.4 | 284.8
1862.2 | 162.2 | 154.5 | 298.8 | 366 | 277.1
1863.2 | 163.2 | 155.1 | 308.7 | 380 | 274
1864.2 | 164.2 | 155.6 | 318.9 | 394.8 | 279.2
1865.2 | 165.2 | 156.3 | 320.9 | 391.9 | 283.3
1866.2 | 166.2 | 156.9 | 314.9 | 384.1 | 281.3
1867.2 | 167.2 | 157.7 | 316.1 | 385.7 | 285.5
1868.2 | 168.2 | 158.4 | 310.1 | 382.7 | 283.1
1869.2 | 169.2 | 159.2 | 310.5 | 386.7 | 282.8
1870.2 | 170.2 | 160 | 308.2 | 392.3 | 280.9
1871.2 | 171.2 | 160.8 | 310.4 | 398.8 | 282.7
1872.2 | 172.2 | 161.5 | 316.5 | 401.3 | 289
1873.2 | 173.2 | 162.3 | 311.2 | 402 | 295.2
1874.2 | 174.2 | 163 | 308.5 | 404.1 | 295.2
1875.2 | 175.2 | 163.8 | 312.1 | 405.4 | 292.6
1876.2 | 176.2 | 164.6 | 308.4 | 403.4 | 293.5
1877.2 | 177.2 | 165.3 | 305.4 | 404.8 | 292.7
1878.2 | 178.2 | 166.1 | 306.9 | 407 | 288.4
1879.2 | 179.2 | 166.8 | 304.5 | 403.3 | 281.8
1880.2 | 180.2 | 167.5 | 303.2 | 393.1 | 278.2
1881.2 | 181.2 | 168.2 | 307.1 | 395.7 | 281.5
1882.2 | 182.2 | 168.9 | 309.9 | 393.6 | 282.8
1883.2 | 183.2 | 169.6 | 308.9 | 384.8 | 280.9
1884.2 | 184.2 | 170.2 | 309.8 | 383.5 | 280.8
1885.2 | 185.2 | 170.9 | 308.4 | 378.4 | 285
1886.2 | 186.2 | 171.6 | 305.2 | 377 | 287.5
1887.2 | 187.2 | 172.2 | 300.2 | 371 | 287.8
1888.2 | 188.2 | 172.8 | 304.5 | 368.7 | 284.6
1889.2 | 189.2 | 173.4 | 311.7 | 380.7 | 290.1
1890.2 | 190.2 | 174 | 317.8 | 375 | 293.5
1891.2 | 191.2 | 174.6 | 317.2 | 370.2 | 290.9
1892.2 | 192.2 | 175.2 | 319 | 367.9 | 290.5
1893.2 | 193.2 | 175.8 | 318.6 | 368.3 | 291.8
1894.2 | 194.2 | 176.5 | 317.6 | 362.9 | 289.6
1895.2 | 195.2 | 177.3 | 320.4 | 358.8 | 286.7
1896.2 | 196.2 | 178 | 320.2 | 352.7 | 286
1897.2 | 197.2 | 178.6 | 318 | 349.5 | 283.1
1898.2 | 198.2 | 179.2 | 318.9 | 345.7 | 283.9
1899.2 | 199.2 | 179.8 | 316.8 | 346 | 284.2
1900.2 | 200.2 | 180.4 | 317.6 | 354.8 | 286.6
1901.2 | 201.2 | 180.9 | 318.8 | 366.2 | 293
1902.2 | 202.2 | 181.4 | 318.6 | 370.9 | 294.8
1903.2 | 203.2 | 181.9 | 318.5 | 374.3 | 296.8
1904.2 | 204.2 | 182.4 | 314.1 | 370.5 | 295
1905.2 | 205.2 | 183 | 312 | 366.7 | 290.7
1906.2 | 206.2 | 183.5 | 319.5 | 362.6 | 288.7
1907.2 | 207.2 | 184.1 | 322.3 | 360.7 | 287.5
1908.2 | 208.2 | 184.7 | 318.5 | 350.3 | 286.9
1909.2 | 209.2 | 185.3 | 320.4 | 347.5 | 286.6
1910.2 | 210.2 | 185.9 | 323.4 | 340.4 | 285.3
1911.2 | 211.2 | 186.4 | 332.5 | 350.1 | 286.3
1912.2 | 212.2 | 186.9 | 327.3 | 349.1 | 284.9
1913.2 | 213.2 | 187.3 | 325.1 | 353 | 287.1
1914.2 | 214.2 | 187.8 | 324.4 | 346.8 | 286.7
1915.2 | 215.2 | 188.4 | 324.4 | 348.9 | 288.9
1916.2 | 216.2 | 188.9 | 328.8 | 351.3 | 288.9
1917.2 | 217.2 | 189.4 | 334.6 | 363.1 | 290.7
1918.2 | 218.2 | 189.9 | 334 | 367 | 292
1919.2 | 219.2 | 190.5 | 341.4 | 368.9 | 293.3
1920.2 | 220.2 | 191 | 339.4 | 372.9 | 297
1921.2 | 221.2 | 191.6 | 336.6 | 387 | 299.8
1922.2 | 222.2 | 192.2 | 332.8 | 395.4 | 300.2
1923.2 | 223.2 | 192.8 | 332.4 | 394.9 | 299.1
1924.2 | 224.2 | 193.3 | 326.9 | 391.3 | 296.8
1925.2 | 225.2 | 193.9 | 323.1 | 384.5 | 294.1
1926.2 | 226.2 | 194.5 | 319.3 | 385.6 | 291.5
1927.2 | 227.2 | 195.1 | 320.1 | 392.2 | 295.4
1928.2 | 228.2 | 195.7 | 316.9 | 388.6 | 297.7
1929.2 | 229.2 | 196.3 | 317.4 | 388.7 | 299.9
1930.2 | 230.2 | 196.8 | 315.9 | 392.6 | 302.6
1931.2 | 231.2 | 197.4 | 312.3 | 390.6 | 299.6
1932.2 | 232.2 | 198 | 306.3 | 389.7 | 298.4
1933.2 | 233.2 | 198.6 | 313.4 | 396.4 | 298.3
1934.2 | 234.2 | 199.1 | 310.8 | 389.9 | 297.9
1935.2 | 235.2 | 199.6 | 315.9 | 381.6 | 296.3
1936.2 | 236.2 | 200.1 | 317 | 382.5 | 293
1937.2 | 237.2 | 200.7 | 322.7 | 381.9 | 296.1
1938.2 | 238.2 | 201.2 | 321.5 | 379.2 | 295.1
1939.2 | 239.2 | 201.8 | 321.3 | 375.2 | 291.2
1940.2 | 240.2 | 202.5 | 326 | 379.3 | 292.4
1941.2 | 241.2 | 203 | 328.6 | 380.9 | 291.4
1942.2 | 242.2 | 203.5 | 334.4 | 386.2 | 293.3
1943.2 | 243.2 | 204 | 338.1 | 386.9 | 293.7
1944.2 | 244.2 | 204.5 | 346 | 384.6 | 292.9
1945.2 | 245.2 | 205 | 348.9 | 386.2 | 291.8
1946.2 | 246.2 | 205.5 | 347 | 387.9 | 293.9
1947.2 | 247.2 | 206 | 348.9 | 390.2 | 295
1948.2 | 248.2 | 206.5 | 346.5 | 388.1 | 293
1949.2 | 249.2 | 207.1 | 344.2 | 395.8 | 294.8
1950.2 | 250.2 | 207.6 | 344.1 | 399.1 | 296
1951.2 | 251.2 | 208.1 | 340.1 | 399 | 299.7
1952.2 | 252.2 | 208.7 | 335.1 | 394.1 | 299.3
1953.2 | 253.2 | 209.3 | 331.4 | 392.5 | 296.2
1954.2 | 254.2 | 209.9 | 330.7 | 392.9 | 296.1
1955.2 | 255.2 | 210.6 | 331.4 | 390.7 | 297.9
1956.2 | 256.2 | 211.1 | 331.4 | 386.9 | 297.3
1957.2 | 257.2 | 211.6 | 329.9 | 377.8 | 294
1958.2 | 258.2 | 212.2 | 332.5 | 376.5 | 293.6
1959.2 | 259.2 | 212.7 | 332.2 | 377.3 | 290.1
1960.2 | 260.2 | 213.1 | 332 | 377.2 | 289.2
1961.2 | 261.2 | 213.7 | 334.5 | 380.4 | 289.8
1962.2 | 262.2 | 214.1 | 333.2 | 378.4 | 289.7
1963.2 | 263.2 | 215.1 | 334.9 | 384.4 | 292
1964.2 | 264.2 | 215.9 | 332 | 384.3 | 295.6
1965.2 | 265.2 | 216.7 | 323.7 | 380.8 | 298.3
1966.2 | 266.2 | 217.4 | 319.6 | 379.9 | 299.9
1967.2 | 267.2 | 217.9 | 317.4 | 374.6 | 297
1968.2 | 268.2 | 218.4 | 316.2 | 375 | 292.6
1969.2 | 269.2 | 218.7 | 318.6 | 370.5 | 291.7
1970.2 | 270.2 | 219.1 | 315.9 | 367.3 | 291.9
1971.2 | 271.2 | 219.6 | 311.5 | 362.9 | 289.5
1972.2 | 272.2 | 220.2 | 318.8 | 371.1 | 290.8
1973.2 | 273.2 | 220.6 | 319.6 | 374.4 | 291.5
1974.2 | 274.2 | 221.2 | 318.6 | 374.3 | 292.3
1975.2 | 275.2 | 223.1 | 318 | 376.1 | 292.9
1976.2 | 276.2 | 224.5 | 315 | 382.8 | 297.3
1977.2 | 277.2 | 225.5 | 314 | 383.5 | 298.2
1978.2 | 278.2 | 226.4 | 317.1 | 383.3 | 296.7
1979.2 | 279.2 | 227.1 | 320.2 | 382.1 | 298.7
1980.2 | 280.2 | 227.9 | 325.4 | 382.4 | 296.9
1981.2 | 281.2 | 228.5 | 329.5 | 378.3 | 294.4
1982.2 | 282.2 | 229.2 | 330.9 | 373.1 | 294.3
1983.2 | 283.2 | 229.8 | 333 | 374.5 | 299.5
1984.2 | 284.2 | 230.3 | 332 | 373.5 | 296.2
1985.2 | 285.2 | 230.8 | 331.3 | 372.7 | 293.8
1986.2 | 286.2 | 231.3 | 331.5 | 374.5 | 296.2
1987.2 | 287.2 | 231.8 | 329.4 | 378.9 | 304.9
1988.2 | 288.2 | 232.2 | 329.7 | 374.6 | 304.1
1989.2 | 289.2 | 232.7 | 333.9 | 371.3 | 300.2
1990.2 | 290.2 | 233.1 | 329.7 | 364 | 297.5
1991.2 | 291.2 | 233.6 | 324.2 | 356.9 | 293.7
1992.2 | 292.2 | 234 | 323.2 | 355 | 292.3
1993.2 | 293.2 | 234.5 | 326.7 | 354.6 | 292.9
1994.2 | 294.2 | 234.8 | 323.1 | 350.7 | 289.7
1995.2 | 295.2 | 235.2 | 320.6 | 350.1 | 290.1
1996.2 | 296.2 | 235.5 | 320 | 345.3 | 287.4
1997.2 | 297.2 | 235.9 | 318.6 | 339.7 | 284.8
1998.2 | 298.2 | 236.2 | 317.9 | 333.4 | 285.4
1999.2 | 299.2 | 236.6 | 317.6 | 335.6 | 284.7
2000.2 | 300.2 | 236.9 | 315.5 | 339.6 | 284.1
2001.2 | 301.2 | 237.2 | 320 | 344.8 | 286.2
2002.2 | 302.2 | 237.4 | 321.2 | 345.2 | 290.1
2003.2 | 303.2 | 237.7 | 319.4 | 341 | 287
2004.2 | 304.2 | 237.9 | 318.1 | 335.8 | 285.1
2005.2 | 305.2 | 238.2 | 316.8 | 337.6 | 290.7
2006.2 | 306.2 | 238.4 | 321.5 | 338.2 | 291.9
2007.2 | 307.2 | 238.6 | 318.6 | 339.3 | 288.8
2008.2 | 308.2 | 238.8 | 317.7 | 340.2 | 290.1
2009.2 | 309.2 | 238.9 | 317.3 | 343.7 | 290.9
2010.2 | 310.2 | 239.1 | 313.5 | 350 | 293.8
2011.2 | 311.2 | 239.3 | 309.5 | 355.7 | 296.6
2012.2 | 312.2 | 239.4 | 305.8 | 362.7 | 298.3
2013.2 | 313.2 | 239.6 | 307.6 | 372 | 299.7
2014.2 | 314.2 | 239.8 | 306 | 371.6 | 297.8
2015.2 | 315.2 | 239.9 | 309.8 | 367.6 | 294.9
2016.2 | 316.2 | 240.1 | 314.4 | 366.1 | 291
2017.2 | 317.2 | 240.3 | 318.1 | 361.7 | 289.1
2018.2 | 318.2 | 240.5 | 317.8 | 353.9 | 286
2019.2 | 319.2 | 240.7 | 314.7 | 349 | 287.7
2020.2 | 320.2 | 240.9 | 316.3 | 355.2 | 291
2021.2 | 321.2 | 241.1 | 317.9 | 362.9 | 297.3
2022.2 | 322.2 | 241.3 | 321.3 | 367 | 300.5
2023.2 | 323.2 | 241.5 | 315.4 | 364.1 | 297.2
2024.2 | 324.2 | 241.7 | 312.6 | 357.7 | 294.2
2025.2 | 325.2 | 241.9 | 313.7 | 363.9 | 295.4
2026.2 | 326.2 | 242.1 | 313.2 | 363.4 | 294.8
2027.2 | 327.2 | 242.3 | 315.2 | 371.8 | 297.3
2028.2 | 328.2 | 242.6 | 318.6 | 378 | 296.7
2029.2 | 329.2 | 242.8 | 318.9 | 385.4 | 300.2
2030.2 | 330.2 | 243 | 323.5 | 389.2 | 302.6
2031.2 | 331.2 | 243.2 | 329.6 | 394.2 | 303.4
2032.2 | 332.2 | 243.5 | 323.7 | 389.5 | 306
2033.3 | 333.3 | 243.8 | 328.7 | 393.1 | 308.7
2034.3 | 334.3 | 244.1 | 332.3 | 396.9 | 307
2035.3 | 335.3 | 244.5 | 334.2 | 391 | 303.4
2036.3 | 336.3 | 244.9 | 337.9 | 387 | 301.5
2037.3 | 337.3 | 245.3 | 338.7 | 381.7 | 302.7
2038.3 | 338.3 | 245.7 | 335.6 | 377.6 | 303
2039.3 | 339.3 | 246.1 | 331.6 | 378.2 | 307.9
2040.3 | 340.3 | 246.6 | 330.7 | 383 | 314.6
2041.3 | 341.3 | 247 | 332.8 | 390.4 | 320.2
2042.3 | 342.3 | 247.4 | 330.1 | 394 | 319
2043.3 | 343.3 | 247.7 | 323.4 | 394.2 | 317.9
2044.3 | 344.3 | 248.1 | 320.6 | 395.7 | 313.8
2045.3 | 345.3 | 248.4 | 320 | 399.4 | 310.9
2046.3 | 346.3 | 248.8 | 319.4 | 400.8 | 307.5
2047.3 | 347.3 | 249.1 | 320.4 | 398.4 | 305.7
2048.3 | 348.3 | 249.4 | 321.8 | 400.3 | 306.5
2049.3 | 349.3 | 249.7 | 321.6 | 410 | 312.8
2050.3 | 350.3 | 250 | 314.5 | 408.7 | 316.6
2051.3 | 351.3 | 250.3 | 313.6 | 405.1 | 319
2052.3 | 352.3 | 250.5 | 315.5 | 407.7 | 317.8
2053.3 | 353.3 | 250.8 | 314.4 | 409.4 | 317.6
2054.3 | 354.3 | 251 | 311 | 411.3 | 319.7
2055.3 | 355.3 | 251.1 | 306.6 | 407 | 318.6
2056.3 | 356.3 | 251.4 | 310.3 | 409.6 | 316.3
2057.3 | 357.3 | 251.6 | 317.2 | 413.2 | 316.1
2058.3 | 358.3 | 251.8 | 329.3 | 410.9 | 315.3
2059.3 | 359.3 | 251.8 | 333.5 | 407.5 | 313.2
2060.3 | 360.3 | 251.7 | 332.9 | 402.2 | 310.5
2061.3 | 361.3 | 251.6 | 332.7 | 400.9 | 307.3
2062.3 | 362.3 | 251.6 | 331.5 | 398.5 | 304.4
2063.3 | 363.3 | 251.6 | 327.6 | 395.1 | 305.3
2064.3 | 364.3 | 252.1 | 324.1 | 393.9 | 304.3
2065.3 | 365.3 | 252.6 | 324.9 | 400.1 | 306.2
2066.3 | 366.3 | 252.6 | 328.1 | 408.7 | 311.1
2067.3 | 367.3 | 252.4 | 325.6 | 406.3 | 309.5
2068.3 | 368.3 | 252.2 | 323.8 | 406.2 | 308.4
2069.3 | 369.3 | 252.2 | 322.9 | 403.8 | 307.4
2070.3 | 370.3 | 252.3 | 327.9 | 403.1 | 313.7
2071.3 | 371.3 | 252.4 | 326.6 | 401 | 316.1
2072.3 | 372.3 | 252.8 | 326 | 403.1 | 318.1
2073.3 | 373.3 | 253.1 | 325.4 | 399.6 | 314.9
2074.3 | 374.3 | 253.4 | 326.5 | 391.4 | 312.4
2075.3 | 375.3 | 253.6 | 325.7 | 387.1 | 310.1
2076.3 | 376.3 | 253.7 | 331.5 | 385.3 | 309.3
2077.3 | 377.3 | 254 | 324.6 | 375.7 | 306.9
2078.3 | 378.3 | 254.2 | 322.2 | 368.3 | 304.1
2079.3 | 379.3 | 254.3 | 326 | 367.5 | 302
2080.3 | 380.3 | 254.5 | 333.3 | 367.5 | 302.7
2081.3 | 381.3 | 254.6 | 337 | 364.8 | 304.7
2082.3 | 382.3 | 254.7 | 335.2 | 362.4 | 304.6
2083.3 | 383.3 | 254.8 | 331.3 | 357.8 | 302.1
2084.3 | 384.3 | 255.4 | 327.7 | 360.2 | 303.1
2085.3 | 385.3 | 256.4 | 330.8 | 360.9 | 305.3
2086.3 | 386.3 | 257.2 | 326 | 358.7 | 302.4
2087.3 | 387.3 | 257.9 | 324.9 | 359.3 | 303
2088.3 | 388.3 | 258.4 | 322.2 | 353.5 | 299
2089.3 | 389.3 | 258.8 | 316.2 | 348.3 | 295.6
2090.3 | 390.3 | 259.2 | 310.8 | 342.3 | 297.1
2091.3 | 391.3 | 259.6 | 310.1 | 339.2 | 301.7
2092.3 | 392.3 | 259.9 | 309.9 | 339.6 | 299.3
2093.3 | 393.3 | 260.1 | 307.5 | 335.7 | 296.5
2094.3 | 394.3 | 260.3 | 307.6 | 340.6 | 299.1
2095.3 | 395.3 | 260.4 | 308.4 | 345.4 | 304.9
2096.3 | 396.3 | 260.5 | 310.1 | 349.4 | 307.5
2097.3 | 397.3 | 260.5 | 307.5 | 352.8 | 305.5
2098.3 | 398.3 | 260.5 | 307.9 | 355.2 | 304.3
2099.3 | 399.3 | 260.4 | 306.2 | 357.2 | 302.7
2100.3 | 400.3 | 260.2 | 302.5 | 357.9 | 299.4
2101.3 | 401.3 | 260 | 304 | 362.6 | 299.8
2102.3 | 402.3 | 259.7 | 300.4 | 363 | 303.1
2103.3 | 403.3 | 259.4 | 300.3 | 360.9 | 302.4
2104.3 | 404.3 | 259.1 | 298.9 | 361 | 299.8
2105.3 | 405.3 | 259.2 | 294 | 353.3 | 298.2
2106.3 | 406.3 | 259.6 | 297.9 | 356.6 | 300.1
2107.3 | 407.3 | 259.9 | 299.8 | 353.3 | 304.4
2108.3 | 408.3 | 260.3 | 299.2 | 345.5 | 302
2109.3 | 409.3 | 260.6 | 302.3 | 336.4 | 297.4
2110.3 | 410.3 | 260.8 | 302.1 | 331.9 | 295.9
2111.3 | 411.3 | 260.8 | 304.8 | 332.5 | 300.9
2112.3 | 412.3 | 260.9 | 302.6 | 329.3 | 304.7
2113.3 | 413.3 | 261 | 298.5 | 327.9 | 303.5
2114.3 | 414.3 | 261.1 | 297 | 329.3 | 304.1
2115.3 | 415.3 | 261.1 | 290.5 | 330.5 | 305.2
2116.3 | 416.3 | 261.1 | 289.1 | 334.9 | 307.6
2117.3 | 417.3 | 261.1 | 284.8 | 343.6 | 306.6
2118.3 | 418.3 | 261 | 287.1 | 346.2 | 307.9
2119.3 | 419.3 | 261 | 291.5 | 348.7 | 310.7
2120.3 | 420.3 | 261.1 | 293.7 | 347.6 | 310.4
2121.3 | 421.3 | 261.2 | 293.3 | 347.4 | 306
2122.3 | 422.3 | 261.4 | 292.8 | 346.8 | 303.1
2123.3 | 423.3 | 261.6 | 293.4 | 347.6 | 301.8
2124.3 | 424.3 | 261.8 | 295.4 | 348.9 | 301.4
2125.3 | 425.3 | 261.9 | 299.9 | 354 | 305
2126.3 | 426.3 | 261.9 | 297.4 | 355.9 | 307.3
2127.3 | 427.3 | 262 | 299 | 357.1 | 304.4
2128.3 | 428.3 | 262 | 298.5 | 356.8 | 305.3
2129.3 | 429.3 | 262 | 298.8 | 354.5 | 303.1
2130.3 | 430.3 | 262.1 | 299.6 | 354.8 | 303.7
2131.3 | 431.3 | 262.2 | 300.5 | 355.6 | 306.3
2132.3 | 432.3 | 262.3 | 303.1 | 359.5 | 307.5
2133.3 | 433.3 | 262.4 | 302 | 360.8 | 305.1
2134.3 | 434.3 | 262.4 | 303.2 | 362.4 | 307.2
2135.3 | 435.3 | 262.5 | 303.3 | 360.2 | 307
2136.3 | 436.3 | 262.6 | 305.8 | 356.5 | 305.1
2137.3 | 437.3 | 262.8 | 310.9 | 360.4 | 306.4
2138.3 | 438.3 | 263.2 | 308.7 | 351.8 | 302.7
2139.3 | 439.3 | 263.7 | 305.2 | 344.6 | 298.9
2140.3 | 440.3 | 264.1 | 304.7 | 350.5 | 299
2141.3 | 441.3 | 264.4 | 302.6 | 353.8 | 298.2
2142.3 | 442.3 | 264.7 | 301.1 | 356.8 | 298.4
2143.3 | 443.3 | 264.9 | 300.6 | 361.2 | 300.4
2144.3 | 444.3 | 265.1 | 305 | 370.7 | 304.9
2145.3 | 445.3 | 265.4 | 304.5 | 373.9 | 311.2
2146.3 | 446.3 | 265.7 | 308.3 | 377.8 | 309.6
2147.3 | 447.3 | 266.2 | 306.1 | 374 | 306.4
2148.3 | 448.3 | 266.6 | 304.9 | 377.1 | 304.6
2149.3 | 449.3 | 267.1 | 307.9 | 374.4 | 302.1
2150.3 | 450.3 | 267.7 | 307.3 | 367 | 298.7
2151.3 | 451.3 | 268.3 | 307.5 | 366.9 | 297.7
2152.3 | 452.3 | 268.8 | 308.7 | 371.1 | 302.2
2153.3 | 453.3 | 269.2 | 304.1 | 373.1 | 304.5
2154.3 | 454.3 | 269.6 | 304.7 | 374.1 | 304.9
2155.3 | 455.3 | 269.9 | 301.9 | 369.7 | 303.6
2156.3 | 456.3 | 270.3 | 302.3 | 369.3 | 302.9
2157.3 | 457.3 | 270.6 | 300.8 | 372.1 | 303.3
2158.3 | 458.3 | 270.9 | 303 | 379.4 | 313
2159.3 | 459.3 | 271.2 | 299.5 | 384 | 317.2
2160.3 | 460.3 | 271.5 | 299.1 | 393 | 319.1
2161.3 | 461.3 | 271.7 | 302.8 | 409.4 | 323.2
2162.3 | 462.3 | 272 | 302.6 | 409.5 | 324.1
2163.3 | 463.3 | 272.3 | 309 | 414.8 | 323.5
2164.3 | 464.3 | 272.6 | 313.8 | 410.5 | 322.6
2165.3 | 465.3 | 273 | 311.5 | 409.1 | 322.4
2166.3 | 466.3 | 273.4 | 307.6 | 406.9 | 321.9
2167.3 | 467.3 | 273.8 | 303.8 | 403.1 | 325.1
2168.3 | 468.3 | 274.2 | 299.9 | 401.3 | 322.3
2169.3 | 469.3 | 274.6 | 300.1 | 399 | 321.2
2170.3 | 470.3 | 275 | 298.6 | 394.4 | 319.1
2171.3 | 471.3 | 275.3 | 300.8 | 394.3 | 319.2
2172.3 | 472.3 | 275.6 | 301.3 | 396.6 | 321.7
2173.3 | 473.3 | 275.8 | 299.5 | 395.3 | 323.9
2174.3 | 474.3 | 276 | 295.7 | 394.5 | 325.7
2175.3 | 475.3 | 276.3 | 292.4 | 395.7 | 325.2
2176.3 | 476.3 | 276.5 | 291.1 | 395.3 | 329.3
2177.3 | 477.3 | 276.7 | 291.1 | 396 | 329.5
2178.3 | 478.3 | 276.9 | 291.8 | 396.7 | 328.2
2179.3 | 479.3 | 277.1 | 294.7 | 389.9 | 325.8
2180.3 | 480.3 | 277.3 | 292.1 | 386.9 | 325.9
2181.3 | 481.3 | 277.4 | 288.9 | 372.2 | 321.1
2182.3 | 482.3 | 277.6 | 286 | 363.1 | 315.6
2183.3 | 483.3 | 277.8 | 284.8 | 353.9 | 313.5
2184.3 | 484.3 | 278 | 284.9 | 346.8 | 312.1
2185.3 | 485.3 | 278.2 | 283.8 | 340.8 | 310.1
2186.3 | 486.3 | 278.2 | 285.4 | 337.4 | 311.3
2187.3 | 487.3 | 278.3 | 284.8 | 335.6 | 310.9
2188.3 | 488.3 | 278.4 | 284.9 | 340.2 | 313.5
2189.3 | 489.3 | 278.4 | 281 | 337.9 | 318.6
2190.3 | 490.3 | 278.4 | 278 | 333.9 | 326.5
2191.3 | 491.3 | 278.3 | 276.8 | 337 | 334.4
2192.3 | 492.3 | 278.3 | 275.4 | 336.7 | 336.5
2193.3 | 493.3 | 278.2 | 273.5 | 334.8 | 331.5
2194.3 | 494.3 | 278.1 | 269.2 | 326.8 | 324.4
2195.3 | 495.3 | 278 | 266.4 | 324.8 | 323.1
2196.3 | 496.3 | 278 | 266.4 | 326.4 | 325.2
2197.3 | 497.3 | 277.9 | 268.5 | 335.5 | 331.5
2198.3 | 498.3 | 277.8 | 268.7 | 332.3 | 333
2199.3 | 499.3 | 277.7 | 265.9 | 330.5 | 331.6
2200.3 | 500.3 | 277.6 | 260.4 | 324.7 | 326.6
2201.3 | 501.3 | 277.5 | 261.5 | 324.9 | 328.3
2202.3 | 502.3 | 277.5 | 259 | 320.9 | 329.7
2203.3 | 503.3 | 277.4 | 259.4 | 320.9 | 325.8
2204.3 | 504.3 | 277.3 | 259.9 | 320.7 | 321.6
2205.3 | 505.3 | 277.2 | 258.4 | 318.2 | 318.4
2206.3 | 506.3 | 277.1 | 262.6 | 317.7 | 318.3
2207.3 | 507.3 | 277 | 263.7 | 312.3 | 314.3
2208.3 | 508.3 | 276.9 | 268.3 | 309.7 | 313.1
2209.3 | 509.3 | 276.8 | 275 | 308.3 | 312.7
2210.3 | 510.3 | 276.7 | 282.9 | 311.2 | 316.2
2211.3 | 511.3 | 276.6 | 287.6 | 318.8 | 320.8
2212.3 | 512.3 | 276.5 | 286 | 322.1 | 326.9
2213.3 | 513.3 | 276.4 | 285.1 | 324.4 | 328
2214.3 | 514.3 | 276.4 | 282.6 | 332.8 | 332.3
2215.3 | 515.3 | 276.4 | 283.2 | 334.8 | 333.6
2216.3 | 516.3 | 276.3 | 282.3 | 334.1 | 328
2217.3 | 517.3 | 276.3 | 278.7 | 332.1 | 329.5
2218.3 | 518.3 | 276.4 | 276.8 | 331.1 | 328.3
2219.3 | 519.3 | 276.4 | 280.7 | 335.8 | 328.7
2220.3 | 520.3 | 276.4 | 278.4 | 336.8 | 333.4
2221.3 | 521.3 | 276.4 | 275.2 | 330.5 | 332.3
2222.3 | 522.3 | 276.5 | 273.9 | 330.4 | 332.4
2223.3 | 523.3 | 276.5 | 273.9 | 337.6 | 337.1
2224.3 | 524.3 | 276.6 | 270.9 | 339 | 338.7
2225.3 | 525.3 | 276.6 | 271.6 | 344.8 | 340.7
2226.3 | 526.3 | 276.6 | 267.6 | 343.2 | 340.1
2227.3 | 527.3 | 276.6 | 263.5 | 343.5 | 338.9
2228.3 | 528.3 | 276.7 | 263.8 | 351.5 | 338.9
2229.3 | 529.3 | 276.7 | 261 | 353.2 | 339.4
2230.3 | 530.3 | 276.6 | 256.3 | 347.4 | 336.6
2231.3 | 531.3 | 276.6 | 251.8 | 342.9 | 334.6
2232.3 | 532.3 | 276.6 | 249.5 | 344.7 | 335.2
2233.3 | 533.3 | 276.6 | 246.4 | 341.2 | 337.5
2234.3 | 534.3 | 276.5 | 242.5 | 335.9 | 335.5
2235.3 | 535.3 | 276.4 | 239.4 | 334.4 | 337.4
2236.3 | 536.3 | 276.3 | 236.6 | 329.3 | 334.9
2237.3 | 537.3 | 276.2 | 237 | 328.9 | 333.9
2238.3 | 538.3 | 276.1 | 233.9 | 324.4 | 334.1
2239.3 | 539.3 | 276 | 232.8 | 325.6 | 335.1
2240.3 | 540.3 | 275.8 | 232 | 327.3 | 333.4
2241.3 | 541.3 | 275.8 | 229.4 | 323.2 | 331.4
2242.3 | 542.3 | 275.6 | 227.7 | 321.7 | 334
2243.3 | 543.3 | 275.4 | 223.8 | 316.2 | 332.9
2244.3 | 544.3 | 275.1 | 221.3 | 315.6 | 331.2
2245.3 | 545.3 | 274.9 | 217 | 311.2 | 328.5
2246.3 | 546.3 | 274.6 | 214.3 | 312.6 | 329.1
2247.3 | 547.3 | 274.3 | 213.2 | 310 | 329.1
2248.3 | 548.3 | 274.1 | 211 | 309.7 | 325.2
2249.3 | 549.3 | 273.8 | 210.1 | 309.3 | 325.6
2250.3 | 550.3 | 273.5 | 207.6 | 305.2 | 325.8
2251.3 | 551.3 | 273.2 | 206.9 | 306 | 330.6
2252.3 | 552.3 | 272.9 | 205.9 | 305.4 | 334.3
2253.3 | 553.3 | 272.5 | 205.1 | 305.7 | 333.9
2254.3 | 554.3 | 272.2 | 203.8 | 302.4 | 334.4
2255.3 | 555.3 | 271.8 | 201.3 | 298.4 | 331.1
2256.3 | 556.3 | 271.6 | 201 | 296.8 | 329.6
2257.3 | 557.3 | 271.2 | 200.2 | 298 | 333.3
2258.3 | 558.3 | 270.9 | 201.5 | 298.2 | 333.8
2259.3 | 559.3 | 270.5 | 199.9 | 297.8 | 332
2260.3 | 560.3 | 270.2 | 201.6 | 299.8 | 333.8
2261.3 | 561.3 | 269.9 | 199.8 | 298.3 | 337.7
2262.3 | 562.3 | 269.5 | 198.1 | 296.6 | 338.3
2263.3 | 563.3 | 269.2 | 201.1 | 299.9 | 340.1
2264.3 | 564.3 | 268.9 | 204.4 | 300.3 | 335.8
2265.3 | 565.3 | 268.5 | 210 | 300.7 | 334.1
2266.3 | 566.3 | 268.3 | 213.7 | 305.9 | 337
2267.3 | 567.3 | 268 | 212.8 | 307.3 | 337.4
2268.3 | 568.3 | 267.8 | 214 | 306.4 | 337.6
2269.3 | 569.3 | 267.6 | 214.6 | 303.5 | 336
2270.3 | 570.3 | 267.4 | 213 | 296.6 | 333.2
2271.3 | 571.3 | 267.1 | 211.8 | 294.7 | 331.8
2272.3 | 572.3 | 266.9 | 210.4 | 295.5 | 333.7
2273.3 | 573.3 | 266.7 | 210 | 295.9 | 336.9
2274.3 | 574.3 | 266.5 | 208.9 | 293 | 335.8
2275.3 | 575.3 | 266.3 | 206.5 | 289.4 | 332.7
2276.3 | 576.3 | 266.1 | 205.7 | 287.3 | 330.1
2277.3 | 577.3 | 265.8 | 203.9 | 280.3 | 325.8
2278.3 | 578.3 | 265.6 | 200.7 | 276.1 | 323.8
2279.3 | 579.3 | 265.3 | 197.7 | 271.7 | 325.4
2280.3 | 580.3 | 265.1 | 197.3 | 270.2 | 323.8
2281.3 | 581.3 | 264.8 | 195.1 | 267.3 | 321.1
2282.3 | 582.3 | 264.5 | 193.5 | 264 | 321.5
2283.3 | 583.3 | 264.3 | 192.6 | 263.7 | 327
2284.3 | 584.3 | 264 | 189.4 | 257.6 | 326.1
2285.3 | 585.3 | 263.7 | 187.8 | 255.3 | 323.3
2286.3 | 586.3 | 263.3 | 188.5 | 254.4 | 322.9
2287.3 | 587.3 | 263 | 186.6 | 250.1 | 322.6
2288.3 | 588.3 | 262.7 | 186.1 | 246.8 | 324.2
2289.3 | 589.3 | 262.3 | 185.7 | 246.4 | 321.9
2290.3 | 590.3 | 262 | 183.9 | 248.2 | 323.8
2291.3 | 591.3 | 261.7 | 181.6 | 244.9 | 327.4
2292.3 | 592.3 | 261.3 | 180.4 | 243.7 | 327.7
2293.3 | 593.3 | 261 | 179.3 | 241.1 | 324.8
2294.3 | 594.3 | 260.7 | 177.2 | 241.3 | 326.3
2295.3 | 595.3 | 260.4 | 174.8 | 238.4 | 324.5
2296.3 | 596.3 | 260 | 172.9 | 242.3 | 326.1
2297.3 | 597.3 | 259.7 | 171.8 | 244.2 | 327.6
2298.3 | 598.3 | 259.4 | 172.3 | 247.2 | 328.4
2299.3 | 599.3 | 259.1 | 174.1 | 250.5 | 330.5
2300.3 | 600.3 | 258.7 | 173.8 | 248.9 | 329
2301.3 | 601.3 | 258.4 | 173.6 | 248.5 | 327.5
2302.3 | 602.3 | 258.1 | 172.7 | 251.6 | 328.6
2303.3 | 603.3 | 257.8 | 172.3 | 251.8 | 325.3
2304.3 | 604.3 | 257.6 | 175.3 | 259.2 | 329
2305.3 | 605.3 | 257.3 | 177.3 | 267.2 | 328.8
2306.3 | 606.3 | 257 | 181.1 | 272.8 | 326.3
2307.3 | 607.3 | 256.7 | 185.6 | 277.1 | 324.6
2308.3 | 608.3 | 256.5 | 191 | 280.1 | 325.8
2309.3 | 609.3 | 256.3 | 194.1 | 286 | 332.1
2310.3 | 610.3 | 256.2 | 200.6 | 294.7 | 334.8
2311.3 | 611.3 | 256.1 | 205.3 | 301.5 | 333.4
2312.3 | 612.3 | 256.1 | 208.9 | 303.4 | 329.3
2313.3 | 613.3 | 256.1 | 211.5 | 301.4 | 326.5
2314.3 | 614.3 | 256 | 210.6 | 300.4 | 324.3
2315.3 | 615.3 | 256.1 | 210.1 | 301.8 | 323.9
2316.3 | 616.3 | 256.2 | 209.9 | 300.4 | 326.7
2317.3 | 617.3 | 256.3 | 209.2 | 299.2 | 328.4
2318.3 | 618.3 | 256.4 | 210.3 | 300.5 | 331.3
2319.3 | 619.3 | 256.4 | 209.3 | 298.1 | 329
2320.3 | 620.3 | 256.5 | 210 | 295.9 | 327.5
2321.3 | 621.3 | 256.5 | 213.6 | 294.8 | 324.4
2322.3 | 622.3 | 256.6 | 215.6 | 292.4 | 324.9
2323.3 | 623.3 | 256.6 | 217.9 | 294.7 | 325.6
2324.3 | 624.3 | 256.7 | 222.9 | 296 | 326.2
2325.3 | 625.3 | 256.7 | 225.9 | 296.4 | 324
2326.3 | 626.3 | 256.7 | 225.6 | 297.7 | 323.1
2327.3 | 627.3 | 256.8 | 229.5 | 294.9 | 320.4
2328.3 | 628.3 | 256.9 | 228 | 293.5 | 319.3
2329.3 | 629.3 | 256.9 | 234 | 293.9 | 321.2
2330.3 | 630.3 | 257 | 236.7 | 297.2 | 322.2
2331.3 | 631.3 | 257.1 | 238.8 | 300.3 | 325.5
2332.3 | 632.3 | 257.2 | 236.7 | 298.3 | 327.2
2333.3 | 633.3 | 257.3 | 234.2 | 298.2 | 329
2334.3 | 634.3 | 257.4 | 232.6 | 295.8 | 325.4
2335.3 | 635.3 | 257.5 | 230.3 | 295.8 | 325.6
2336.3 | 636.3 | 257.6 | 227.9 | 295.4 | 326.5
2337.3 | 637.3 | 257.6 | 225.7 | 293.5 | 329.1
2338.3 | 638.3 | 257.7 | 225.4 | 297.7 | 332
2339.3 | 639.3 | 257.7 | 225.4 | 295.5 | 330.9
2340.3 | 640.3 | 257.8 | 231 | 298.8 | 326.8
2341.3 | 641.3 | 257.8 | 235.4 | 300.4 | 325.5
2342.3 | 642.3 | 257.8 | 240.2 | 301.6 | 325.1
2343.3 | 643.3 | 257.8 | 241.2 | 299.8 | 324
2344.3 | 644.3 | 257.9 | 240 | 296.1 | 323.2
2345.3 | 645.3 | 257.9 | 245.1 | 304.1 | 324.9
2346.3 | 646.3 | 258 | 249.4 | 314.5 | 334.3
2347.3 | 647.3 | 258.1 | 249.3 | 317 | 338.3
2348.3 | 648.3 | 258.3 | 258.8 | 328.1 | 342.8
2349.3 | 649.3 | 258.5 | 262 | 325.7 | 341.9
2350.3 | 650.3 | 258.7 | 259.7 | 318.6 | 336
2351.3 | 651.3 | 258.9 | 260.4 | 320.2 | 336.3
2352.3 | 652.3 | 259.1 | 261.4 | 323.6 | 343.4
2353.3 | 653.3 | 259.3 | 257.2 | 318.5 | 341.9
2354.3 | 654.3 | 259.6 | 251.8 | 312.6 | 339.9
2355.3 | 655.3 | 259.8 | 247.3 | 311 | 341
2356.3 | 656.3 | 260 | 243.2 | 312.3 | 345
2357.3 | 657.3 | 260.2 | 239.2 | 308.8 | 344.1
2358.3 | 658.3 | 260.3 | 234.4 | 304.5 | 339.9
2359.3 | 659.3 | 260.4 | 230.4 | 303.9 | 340.3
2360.3 | 660.3 | 260.4 | 227.8 | 304.7 | 342.2
2361.3 | 661.3 | 260.4 | 225.8 | 307.4 | 345.6
2362.3 | 662.3 | 260.4 | 226 | 309.8 | 346
2363.3 | 663.3 | 260.4 | 229.6 | 312.4 | 344.8
2364.3 | 664.3 | 260.3 | 235.9 | 314.8 | 342.5
2365.3 | 665.3 | 260.3 | 238.6 | 316.8 | 341.9
2366.3 | 666.3 | 260.3 | 235.8 | 315.7 | 341.6
2367.3 | 667.3 | 260.3 | 233.1 | 316.8 | 344.1
2368.3 | 668.3 | 260.3 | 229.8 | 310 | 341.7
2369.3 | 669.3 | 260.3 | 229.1 | 313.4 | 343.9
2370.3 | 670.3 | 260.3 | 228.2 | 311.7 | 349.3
2371.3 | 671.3 | 260.3 | 224.5 | 304.8 | 346.1
2372.3 | 672.3 | 260.3 | 220.2 | 301.2 | 341.7
2373.3 | 673.3 | 260.3 | 217.5 | 300.8 | 340.3
2374.3 | 674.3 | 260.2 | 215.6 | 298.3 | 340.7
2375.3 | 675.3 | 260.1 | 213.5 | 299.5 | 341.4
2376.3 | 676.3 | 260 | 212.3 | 297.6 | 341.1
2377.3 | 677.3 | 259.9 | 209.5 | 294.2 | 339.6
2378.3 | 678.3 | 259.8 | 206.4 | 287.7 | 336
2379.3 | 679.3 | 259.7 | 204.5 | 283.7 | 333.7
2380.3 | 680.3 | 259.6 | 203.5 | 285.3 | 339.2
2381.3 | 681.3 | 259.4 | 203.1 | 288.7 | 344.3
2382.3 | 682.3 | 259.3 | 203.1 | 288.4 | 344.3
2383.3 | 683.3 | 259.1 | 201.7 | 288.1 | 346
2384.3 | 684.3 | 258.9 | 200.6 | 287.2 | 343.6
2385.3 | 685.3 | 258.7 | 201.6 | 287.7 | 341
2386.3 | 686.3 | 258.5 | 201.1 | 287.2 | 340.8
2387.3 | 687.3 | 258.4 | 198.7 | 285.1 | 339.9
2388.3 | 688.3 | 258.2 | 196.1 | 285.7 | 341.3
2389.3 | 689.3 | 258 | 194.6 | 284.7 | 342.1
2390.3 | 690.3 | 257.8 | 193.4 | 279.3 | 339.9
2391.3 | 691.3 | 257.6 | 191.7 | 274.6 | 335.5
2392.3 | 692.3 | 257.5 | 190.8 | 271.9 | 332.8
2393.3 | 693.3 | 257.3 | 188.3 | 268.1 | 331.5
2394.3 | 694.3 | 257 | 188.2 | 267.8 | 330.3
2395.3 | 695.3 | 256.8 | 190.2 | 264.2 | 328
2396.3 | 696.3 | 256.6 | 192.4 | 263.4 | 329.4
2397.3 | 697.3 | 256.4 | 191.7 | 262.5 | 333.4
2398.3 | 698.3 | 256.1 | 188.9 | 257.4 | 332.2
2399.3 | 699.3 | 255.9 | 187 | 254.1 | 330
2400.3 | 700.3 | 255.7 | 185.6 | 250.9 | 327
2401.3 | 701.3 | 255.4 | 186.5 | 250 | 325.7
2402.3 | 702.3 | 255.2 | 186.7 | 251.6 | 326.4
2403.3 | 703.3 | 255 | 185.9 | 252.7 | 330
2404.3 | 704.3 | 254.8 | 183.8 | 249.8 | 329
2405.3 | 705.3 | 254.5 | 182.5 | 248.7 | 331.9
2406.3 | 706.3 | 254.3 | 183 | 251.7 | 336.6
2407.3 | 707.3 | 254.1 | 183.5 | 254.3 | 339.5
2408.3 | 708.3 | 253.8 | 183.7 | 250.4 | 332.8
2409.3 | 709.3 | 253.6 | 185.2 | 248.6 | 329.3
2410.3 | 710.3 | 253.3 | 190.5 | 251 | 326.7
2411.3 | 711.3 | 253.1 | 191.3 | 246.4 | 324.8
2412.3 | 712.3 | 252.9 | 191.2 | 245.4 | 324.2
2413.3 | 713.3 | 252.7 | 196.3 | 252.8 | 329.2
2414.3 | 714.3 | 252.5 | 199.4 | 258.2 | 333.3
2415.3 | 715.3 | 252.4 | 198.4 | 258.5 | 332.9
2416.3 | 716.3 | 252.2 | 197.6 | 256.9 | 329.1
2417.3 | 717.3 | 252.1 | 198 | 266.4 | 332
2418.3 | 718.3 | 252 | 199.3 | 271.8 | 336.9
2419.3 | 719.3 | 251.9 | 198.8 | 272.5 | 341.7
2420.3 | 720.3 | 251.8 | 198.9 | 278.9 | 345.1
2421.3 | 721.3 | 251.7 | 201.7 | 283.5 | 346.6
2422.3 | 722.3 | 251.7 | 200.2 | 286.3 | 345.9
2423.3 | 723.3 | 251.6 | 200.3 | 289 | 348.8
2424.3 | 724.3 | 251.6 | 200.9 | 287.3 | 346.5
2425.3 | 725.3 | 251.6 | 205.1 | 291.4 | 346.5
2426.3 | 726.3 | 251.6 | 210 | 300.2 | 346.5
2427.3 | 727.3 | 251.6 | 215.5 | 310 | 347.9
2428.3 | 728.3 | 251.6 | 219.8 | 322.9 | 351.8
2429.3 | 729.3 | 251.7 | 220.7 | 321.8 | 352.2
2430.3 | 730.3 | 251.8 | 219.2 | 317.2 | 349.4
2431.3 | 731.3 | 251.9 | 216 | 312.1 | 349.6
2432.3 | 732.3 | 252.1 | 213.7 | 307.6 | 351.7
2433.3 | 733.3 | 252.2 | 213.6 | 312.2 | 350.3
2434.3 | 734.3 | 252.4 | 216.1 | 316.3 | 351.6
2435.3 | 735.3 | 252.5 | 221.9 | 326.5 | 355.8
2436.3 | 736.3 | 252.6 | 223.1 | 330.2 | 358.3
2437.3 | 737.3 | 252.7 | 222.6 | 332.4 | 355.2
2438.3 | 738.3 | 252.9 | 219.9 | 331.8 | 356.3
2439.3 | 739.3 | 253 | 218.2 | 333.7 | 358.8
2440.3 | 740.3 | 253.2 | 216.2 | 334.9 | 359.7
2441.3 | 741.3 | 253.3 | 215.8 | 335.8 | 358.2
2442.3 | 742.3 | 253.4 | 220.1 | 343.7 | 357.8
2443.3 | 743.3 | 253.6 | 229.5 | 349.1 | 357.7
2444.3 | 744.3 | 253.7 | 234.7 | 350.2 | 354.6
2445.3 | 745.3 | 253.8 | 247.3 | 358.6 | 357.3
2446.3 | 746.3 | 254 | 247.6 | 360.4 | 358
2447.3 | 747.3 | 254.2 | 247.4 | 357.1 | 355.9
2448.3 | 748.3 | 254.5 | 248.8 | 359.4 | 355.8
2449.3 | 749.3 | 254.8 | 248.9 | 364 | 359.2
2450.3 | 750.3 | 255.2 | 249.1 | 362.2 | 359.4
2451.3 | 751.3 | 255.5 | 247.9 | 359.4 | 356.8
2452.3 | 752.3 | 255.8 | 246.1 | 354.1 | 358
2453.3 | 753.3 | 256.2 | 242.4 | 348.2 | 358.1
2454.3 | 754.3 | 256.4 | 240.2 | 348.4 | 358.5
2455.3 | 755.3 | 256.7 | 238.3 | 349.8 | 359.8
2456.3 | 756.3 | 256.9 | 235.1 | 348.3 | 360.8
2457.3 | 757.3 | 257.1 | 232.3 | 348.7 | 361.1
2458.3 | 758.3 | 257.2 | 231 | 350 | 361.4
2459.3 | 759.3 | 257.3 | 229.4 | 348.9 | 359.2
2460.3 | 760.3 | 257.4 | 232.6 | 357.2 | 364.4
2461.3 | 761.3 | 257.5 | 235.3 | 359.4 | 363.5
2462.3 | 762.3 | 257.6 | 242.9 | 366.4 | 362.7
2463.3 | 763.3 | 257.6 | 244.1 | 362.9 | 362.4
2464.3 | 764.3 | 257.8 | 241.1 | 355.9 | 362.3
2465.3 | 765.3 | 257.9 | 238.7 | 353.2 | 364.8
2466.3 | 766.3 | 258.1 | 235.7 | 348.4 | 364.3
2467.3 | 767.3 | 258.3 | 232.7 | 343.3 | 362.8
2468.3 | 768.3 | 258.4 | 230.9 | 338.6 | 360.9
2469.3 | 769.3 | 258.5 | 229.7 | 333.7 | 359.6
2470.3 | 770.3 | 258.6 | 228.2 | 335.5 | 359.8
2471.3 | 771.3 | 258.7 | 226.1 | 336 | 358.9
2472.3 | 772.3 | 258.8 | 224.4 | 331.5 | 357.6
2473.3 | 773.3 | 258.8 | 221.3 | 323.5 | 352.5
2474.3 | 774.3 | 258.9 | 218 | 316.4 | 349.9
2475.3 | 775.3 | 258.9 | 216.7 | 310.5 | 348.4
2476.3 | 776.3 | 258.9 | 215.5 | 304.9 | 347.9
2477.3 | 777.3 | 258.9 | 212.3 | 299.3 | 348.4
2478.3 | 778.3 | 258.8 | 210 | 293.9 | 346.7
2479.3 | 779.3 | 258.7 | 208.2 | 292.2 | 345.5
2480.3 | 780.3 | 258.6 | 207.2 | 296.2 | 348.7
2481.3 | 781.3 | 258.5 | 206.2 | 302.2 | 352.2
2482.3 | 782.3 | 258.3 | 206.1 | 307 | 355
2483.3 | 783.3 | 258.2 | 203.7 | 304.6 | 352.9
2484.3 | 784.3 | 258 | 204.2 | 312.2 | 355.5
2485.3 | 785.3 | 257.9 | 204.6 | 318.8 | 362.2
2486.3 | 786.3 | 257.7 | 204.9 | 323.1 | 363.8
2487.3 | 787.3 | 257.6 | 203.9 | 323.4 | 361.1
2488.3 | 788.3 | 257.5 | 204.6 | 326.9 | 364.4
2489.3 | 789.3 | 257.3 | 205.8 | 327.7 | 364.2
2490.3 | 790.3 | 257.2 | 204.5 | 322 | 358.6
2491.3 | 791.3 | 257.1 | 202.3 | 316.7 | 354.9
2492.3 | 792.3 | 257 | 201.8 | 314.6 | 354.5
2493.3 | 793.3 | 257 | 201.8 | 312.7 | 355.3
2494.3 | 794.3 | 256.9 | 201.2 | 313.9 | 355
2495.3 | 795.3 | 256.8 | 202.7 | 312.5 | 355.1
2496.3 | 796.3 | 256.7 | 204.4 | 311.6 | 356.4
2497.3 | 797.3 | 256.6 | 204.3 | 308 | 355.6
2498.3 | 798.3 | 256.5 | 205.7 | 305.5 | 351.7
2499.3 | 799.3 | 256.3 | 210.6 | 307.1 | 350.9
2500.3 | 800.3 | 256.2 | 216.1 | 316.3 | 354
2501.3 | 801.3 | 256.1 | 215.9 | 319.9 | 355.3
2502.3 | 802.3 | 256 | 215 | 317.2 | 354.6
2503.3 | 803.3 | 256 | 215.6 | 318.8 | 355.8
2504.3 | 804.3 | 255.9 | 214.6 | 318.4 | 357.5
2505.3 | 805.3 | 255.9 | 213.1 | 316.4 | 356.2
2506.3 | 806.3 | 255.9 | 213 | 311.6 | 352.2
2507.3 | 807.3 | 255.9 | 211.2 | 310.5 | 352.6
2508.3 | 808.3 | 255.9 | 210.1 | 310.2 | 356.7
2509.3 | 809.3 | 255.9 | 209.5 | 310.5 | 356.6
2510.3 | 810.3 | 255.8 | 212.5 | 315.6 | 358.4
2511.3 | 811.3 | 255.8 | 214.5 | 318.4 | 358
2512.3 | 812.3 | 255.8 | 220.6 | 318.5 | 357.2
2513.3 | 813.3 | 255.8 | 223.2 | 317.3 | 354.1
2514.3 | 814.3 | 255.8 | 228 | 322.3 | 356.1
2515.3 | 815.3 | 255.8 | 235.1 | 333.9 | 361.4
2516.3 | 816.3 | 255.8 | 240 | 338.8 | 362.3
2517.3 | 817.3 | 255.9 | 246.4 | 343.5 | 359.4
2518.3 | 818.3 | 256 | 250.4 | 352.5 | 361.6
2519.3 | 819.3 | 256.1 | 254.2 | 355.6 | 367.6
2520.3 | 820.3 | 256.3 | 252.8 | 349.2 | 363.4
2521.3 | 821.3 | 256.5 | 248.9 | 344.5 | 362.4
2522.3 | 822.3 | 256.8 | 246.5 | 342 | 364.9
2523.3 | 823.3 | 257 | 244.6 | 339.9 | 365.9
2524.3 | 824.3 | 257.1 | 242.8 | 334.2 | 362.1
2525.3 | 825.3 | 257.3 | 243.6 | 338.8 | 360.3
2526.3 | 826.3 | 257.5 | 243.8 | 339.1 | 362.1
2527.3 | 827.3 | 257.6 | 241.2 | 334.2 | 359
2528.3 | 828.3 | 257.8 | 238.7 | 326.6 | 354.1
2529.3 | 829.3 | 258 | 240.4 | 325 | 350.9
2530.3 | 830.3 | 258.1 | 243.9 | 330 | 351.8
2531.3 | 831.3 | 258.2 | 246.4 | 329.3 | 351.8
2532.3 | 832.3 | 258.3 | 248.5 | 322.7 | 348.4
2533.3 | 833.3 | 258.5 | 251.5 | 319.8 | 345.3
2534.3 | 834.3 | 258.6 | 254.5 | 314.8 | 342.7
2535.3 | 835.3 | 258.8 | 257.5 | 311.6 | 339.7
2536.3 | 836.3 | 258.9 | 261 | 313.7 | 339.2
2537.3 | 837.3 | 259.1 | 266.2 | 321.2 | 341.7
2538.3 | 838.3 | 259.3 | 268.9 | 323.8 | 344.8
2539.3 | 839.3 | 259.4 | 269.9 | 327.4 | 346.5
2540.3 | 840.3 | 259.6 | 266 | 327.7 | 350.2
2541.3 | 841.3 | 259.8 | 262.5 | 329 | 355
2542.3 | 842.3 | 259.9 | 262.7 | 337.9 | 361.8
2543.3 | 843.3 | 260.1 | 271 | 355.1 | 372.2
2544.3 | 844.3 | 260.3 | 272.4 | 356.7 | 371.2
2545.3 | 845.3 | 260.4 | 271.2 | 353.2 | 367.3
2546.3 | 846.3 | 260.6 | 270.7 | 354.9 | 366.4
2547.3 | 847.3 | 260.8 | 269.8 | 357.9 | 366.7
2548.3 | 848.3 | 261.1 | 268.4 | 360.5 | 369.4
2549.3 | 849.3 | 261.3 | 269.3 | 358.5 | 369.6
2550.3 | 850.3 | 261.6 | 268.9 | 357.4 | 368.9
2551.3 | 851.3 | 261.8 | 266.4 | 359.3 | 372.4
2552.3 | 852.3 | 262 | 267.8 | 364.8 | 375
2553.3 | 853.3 | 262.2 | 271.6 | 372.6 | 383.2
2554.3 | 854.3 | 262.4 | 271.2 | 374.2 | 388
2555.3 | 855.3 | 262.6 | 269 | 374.7 | 387.7
2556.3 | 856.3 | 262.8 | 265.2 | 373.1 | 386.3
2557.3 | 857.3 | 263.1 | 261.5 | 366.5 | 385.1
2558.3 | 858.3 | 263.3 | 259.6 | 365.6 | 386.7
2559.3 | 859.3 | 263.6 | 260.5 | 371.9 | 389.9
2560.3 | 860.3 | 263.8 | 267.2 | 387.9 | 400.1
2561.3 | 861.3 | 264 | 267.4 | 392.2 | 401.2
2562.3 | 862.3 | 264.2 | 267.3 | 400.9 | 407.7
2563.3 | 863.3 | 264.4 | 266.5 | 400.7 | 406.4
2564.3 | 864.3 | 264.7 | 263.1 | 395.8 | 399
2565.3 | 865.3 | 265.1 | 264.3 | 396.1 | 394.5
2566.3 | 866.3 | 265.4 | 269.2 | 398.7 | 395.2
2567.3 | 867.3 | 265.6 | 272.9 | 408.2 | 400.2
2568.3 | 868.3 | 265.9 | 278.9 | 415.2 | 406.7
2569.3 | 869.3 | 266.3 | 282.3 | 423.6 | 411.4
2570.3 | 870.3 | 266.7 | 286.8 | 424.7 | 413.6
2571.3 | 871.3 | 267.1 | 291.2 | 430.2 | 418.3
2572.3 | 872.3 | 267.5 | 290.9 | 428.2 | 415.9
2573.3 | 873.3 | 268 | 294.1 | 433.8 | 420.4
2574.3 | 874.3 | 268.5 | 296.6 | 433.3 | 422
2575.3 | 875.3 | 269.1 | 292.6 | 428.1 | 415.1
2576.3 | 876.3 | 269.7 | 289.9 | 430.3 | 421.5
2577.3 | 877.3 | 270.3 | 290.2 | 427.9 | 426.6
2578.3 | 878.3 | 270.8 | 290.6 | 429 | 423.8
2579.3 | 879.3 | 271.4 | 290.9 | 423.5 | 419.4
2580.3 | 880.3 | 271.9 | 290.1 | 419.9 | 415.1
2581.3 | 881.3 | 272.5 | 288.8 | 421.3 | 422.7
2582.3 | 882.3 | 273 | 284.7 | 419.4 | 425.7
2583.3 | 883.3 | 273.4 | 283.4 | 419.3 | 428.2
2584.3 | 884.3 | 273.9 | 279.6 | 414 | 427.6
2585.3 | 885.3 | 274.3 | 280.4 | 412.7 | 424.6
2586.3 | 886.3 | 274.7 | 278.7 | 414.7 | 427.2
2587.3 | 887.3 | 275.1 | 276.3 | 408.1 | 422.5
2588.3 | 888.3 | 275.5 | 273.8 | 404.3 | 420.2
2589.3 | 889.3 | 275.9 | 277.6 | 408.2 | 423.2
2590.3 | 890.3 | 276.2 | 280.5 | 405.9 | 419.3
2591.3 | 891.3 | 276.5 | 287.3 | 402.9 | 415.1
2592.3 | 892.3 | 276.8 | 288.3 | 397 | 411.7
2593.3 | 893.3 | 277.1 | 286.8 | 393.4 | 408.5
2594.3 | 894.3 | 277.4 | 285.8 | 386.1 | 405.7
2595.3 | 895.3 | 277.7 | 286.1 | 382.1 | 403.6
2596.3 | 896.3 | 278.1 | 283.9 | 380 | 403.2
2597.3 | 897.3 | 278.4 | 286 | 387.9 | 411.9
2598.3 | 898.3 | 278.7 | 286.4 | 390.2 | 419.2
2599.3 | 899.3 | 278.9 | 281.4 | 387.6 | 416
2600.3 | 900.3 | 279 | 277.5 | 387.7 | 413.4
2601.3 | 901.3 | 279.1 | 278.9 | 395.7 | 418.8
2602.3 | 902.3 | 279.3 | 278.6 | 393.8 | 420.4
2603.3 | 903.3 | 279.5 | 275 | 389.9 | 417.2
2604.3 | 904.3 | 279.7 | 271 | 387.8 | 416.1
2605.3 | 905.3 | 279.9 | 270.1 | 387.2 | 418.6
2606.3 | 906.3 | 280.1 | 271.4 | 391.2 | 420.6
2607.3 | 907.3 | 280.2 | 272.5 | 398.6 | 423
2608.3 | 908.3 | 280.4 | 272.1 | 398.3 | 424.4
2609.3 | 909.3 | 280.5 | 271.8 | 402.8 | 426.8
2610.3 | 910.3 | 280.7 | 272.2 | 407.3 | 433.8
2611.3 | 911.3 | 280.8 | 274.4 | 411.7 | 432.9
2612.3 | 912.3 | 281 | 280.2 | 417.9 | 431.2
2613.3 | 913.3 | 281.1 | 283.4 | 421.2 | 435.2
2614.3 | 914.3 | 281.3 | 281.1 | 419 | 436
2615.3 | 915.3 | 281.5 | 284.8 | 419.7 | 436.6
2616.3 | 916.3 | 281.6 | 289.8 | 431.7 | 436.9
2617.3 | 917.3 | 281.7 | 296.1 | 439 | 443.2
2618.3 | 918.3 | 281.9 | 297.6 | 441.5 | 447.1
2619.3 | 919.3 | 282.3 | 303.8 | 442.8 | 444.3
2620.3 | 920.3 | 282.7 | 314.9 | 449.4 | 442.4
2621.3 | 921.3 | 283.1 | 324.8 | 451.8 | 439.8
2622.3 | 922.3 | 283.5 | 324.8 | 451.9 | 435.7
2623.3 | 923.3 | 284.1 | 328.3 | 453.9 | 437.9
2624.3 | 924.3 | 284.7 | 326.2 | 456.5 | 441.2
2625.3 | 925.3 | 285.5 | 325 | 454.5 | 437.6
2626.3 | 926.3 | 286.2 | 326.1 | 454.9 | 439.2
2627.3 | 927.3 | 286.8 | 329.5 | 454.1 | 440.4
2628.3 | 928.3 | 287.5 | 327.4 | 444.5 | 439.3
2629.3 | 929.3 | 288.1 | 329.3 | 442.7 | 436.8
2630.3 | 930.3 | 288.8 | 331.1 | 438.7 | 435.7
2631.3 | 931.3 | 289.5 | 329.6 | 436.6 | 437.9
2632.3 | 932.3 | 290.2 | 324.2 | 431.8 | 441
2633.3 | 933.3 | 290.9 | 317.6 | 429.1 | 443
2634.3 | 934.3 | 291.5 | 310.9 | 423.7 | 441.4
2635.3 | 935.3 | 292 | 311.2 | 426.2 | 441.7
2636.3 | 936.3 | 292.4 | 311.2 | 423.6 | 440.6
2637.3 | 937.3 | 292.9 | 311.7 | 425.2 | 440.1
2638.3 | 938.3 | 293.3 | 317 | 432 | 441.3
2639.3 | 939.3 | 293.7 | 324.6 | 428.7 | 439
2640.3 | 940.3 | 294.1 | 327.7 | 430.2 | 437
2641.3 | 941.3 | 294.5 | 332.2 | 434.5 | 441.2
2642.3 | 942.3 | 294.8 | 337 | 436.7 | 446.2
2643.3 | 943.3 | 295.1 | 337.1 | 440.4 | 446.4
2644.3 | 944.3 | 295.5 | 344.2 | 440.3 | 443.1
2645.3 | 945.3 | 296 | 341.3 | 441.5 | 440.1
2646.3 | 946.3 | 296.4 | 342 | 449 | 441.7
2647.3 | 947.3 | 296.9 | 343 | 457.5 | 451.3
2648.3 | 948.3 | 297.3 | 340 | 456 | 448.3
2649.3 | 949.3 | 297.8 | 342.4 | 461.2 | 452.4
2650.3 | 950.3 | 298.1 | 341.1 | 465.9 | 455.6
2651.3 | 951.3 | 298.6 | 341.6 | 469.3 | 454.5
2652.3 | 952.3 | 299.1 | 343.2 | 471.7 | 455.1
2653.3 | 953.3 | 299.5 | 343.4 | 473.1 | 452.4
2654.3 | 954.3 | 299.9 | 348.7 | 475 | 447.1
2655.3 | 955.3 | 300.4 | 349.5 | 474.1 | 443.4
2656.3 | 956.3 | 300.8 | 351.6 | 474 | 444.1
2657.3 | 957.3 | 301.3 | 351.4 | 474.9 | 446.1
2658.3 | 958.3 | 301.8 | 346 | 471.3 | 447.7
2659.3 | 959.3 | 302.2 | 351.3 | 476.2 | 450.5
2660.3 | 960.3 | 302.7 | 353.8 | 476.2 | 453.1
2661.3 | 961.3 | 303.3 | 348.7 | 466.8 | 450.1
2662.3 | 962.3 | 303.7 | 341.2 | 458.3 | 448.3
2663.3 | 963.3 | 304.2 | 333 | 446.8 | 445.6
2664.3 | 964.3 | 304.7 | 325.3 | 437.8 | 445.1
2665.3 | 965.3 | 305 | 318.7 | 433.3 | 445.5
2666.3 | 966.3 | 305.2 | 317 | 434.5 | 451.7
2667.3 | 967.3 | 305.5 | 312.4 | 432.2 | 451.8
2668.3 | 968.3 | 305.8 | 315.4 | 434 | 453.2
2669.3 | 969.3 | 305.9 | 317.1 | 436.2 | 451.2
2670.3 | 970.3 | 305.8 | 324.2 | 445.1 | 448.9
2671.3 | 971.3 | 305.8 | 329.6 | 450 | 448.1
2672.3 | 972.3 | 305.9 | 336.1 | 458.9 | 450.6
2673.3 | 973.3 | 306 | 341.9 | 464.2 | 447.8
2674.3 | 974.3 | 306.2 | 348.5 | 466.8 | 444.3
2675.3 | 975.3 | 306.4 | 352.6 | 463.2 | 441.9
2676.3 | 976.3 | 306.7 | 360.3 | 462.2 | 438.6
2677.3 | 977.3 | 307.1 | 369.3 | 462.8 | 436.8
2678.3 | 978.3 | 307.5 | 368.6 | 461.1 | 434.7
2679.3 | 979.3 | 308 | 369.6 | 461.2 | 431.6
2680.3 | 980.3 | 308.4 | 373.8 | 465.4 | 429.7
2681.3 | 981.3 | 308.9 | 379.6 | 476.6 | 432.9
2682.3 | 982.3 | 309.4 | 381 | 476.5 | 436.5
2683.3 | 983.3 | 310 | 380.5 | 482.9 | 440
2684.3 | 984.3 | 310.5 | 389 | 491.8 | 445.1
2685.3 | 985.3 | 311.1 | 385.7 | 488.1 | 447.2
2686.3 | 986.3 | 311.7 | 379.8 | 490.2 | 453
2687.3 | 987.3 | 312.2 | 371.4 | 485.3 | 455.1
2688.3 | 988.3 | 312.8 | 363.5 | 480.7 | 452.3
2689.3 | 989.3 | 313.4 | 363.1 | 483.5 | 451.7
2690.3 | 990.3 | 314 | 361.5 | 483.5 | 453.1
2691.3 | 991.3 | 314.7 | 358.2 | 482.9 | 453.1
2692.3 | 992.3 | 315.2 | 352.7 | 483.3 | 458.2
2693.3 | 993.3 | 315.7 | 349.4 | 485.2 | 461.7
2694.3 | 994.3 | 316.2 | 349.4 | 489.4 | 462.9
2695.3 | 995.3 | 316.7 | 346.5 | 489.5 | 463.1
2696.3 | 996.3 | 316.9 | 352.1 | 495.1 | 463.9
2697.3 | 997.3 | 317.2 | 363.1 | 503.3 | 467.3
2698.3 | 998.3 | 317.6 | 362.5 | 499.7 | 463.9
2699.3 | 999.3 | 318 | 358.7 | 493.9 | 458.3
2700.3 | 1000.3 | 318.4 | 359.1 | 492.7 | 451.8
2701.3 | 1001.3 | 318.7 | 366.2 | 492.8 | 449.8
2702.3 | 1002.3 | 319.2 | 377.6 | 494.9 | 450.5
2703.3 | 1003.3 | 319.7 | 379.5 | 490.4 | 446.2
2704.3 | 1004.3 | 320.3 | 380.2 | 489.7 | 440.9
2705.3 | 1005.3 | 320.9 | 380.1 | 493.6 | 447.2
2706.3 | 1006.3 | 321.2 | 379.4 | 497.4 | 449.1
2707.3 | 1007.3 | 321.6 | 375.6 | 500.2 | 452.1
2708.3 | 1008.3 | 322 | 373.5 | 504.7 | 454.2
2709.3 | 1009.3 | 322.5 | 369.8 | 502.4 | 453.2
2710.3 | 1010.3 | 323.1 | 380.3 | 503.7 | 451
2711.3 | 1011.3 | 323.7 | 387.2 | 497 | 445.2
2712.3 | 1012.3 | 324.2 | 387.4 | 490.6 | 439.6
2713.3 | 1013.3 | 324.8 | 390.8 | 490.7 | 439.8
2714.3 | 1014.3 | 325.2 | 396.3 | 495.8 | 445.1
2715.3 | 1015.3 | 325.6 | 397.3 | 499.4 | 452.2
2716.3 | 1016.3 | 326.2 | 393.6 | 496.9 | 452.7
2717.3 | 1017.3 | 326.9 | 391.6 | 495.4 | 457.5
2718.3 | 1018.3 | 327.5 | 383 | 486.9 | 458.6
2719.3 | 1019.3 | 328.1 | 374.2 | 477.9 | 458
2720.3 | 1020.3 | 328.6 | 367.1 | 472.6 | 460.1
2721.3 | 1021.3 | 329.2 | 359.7 | 464.7 | 458
2722.3 | 1022.3 | 329.8 | 355.4 | 461.4 | 456.7
2723.3 | 1023.3 | 330.2 | 348.2 | 456.6 | 456.7
2724.3 | 1024.3 | 330.5 | 341.6 | 451.9 | 456.9
2725.3 | 1025.3 | 330.8 | 337.2 | 454.4 | 459.8
2726.3 | 1026.3 | 331.1 | 332 | 455.1 | 462.5
2727.3 | 1027.3 | 331.3 | 326.3 | 450 | 461.7
2728.3 | 1028.3 | 331.3 | 322.6 | 449.9 | 460.1
2729.3 | 1029.3 | 331.3 | 321.7 | 449.4 | 459.3
2730.3 | 1030.3 | 331.2 | 319.6 | 447.3 | 457.4
2731.3 | 1031.3 | 331.1 | 320.6 | 447 | 455.4
2732.3 | 1032.3 | 330.9 | 316.2 | 444.2 | 452.8
2733.3 | 1033.3 | 330.8 | 315.1 | 445.8 | 457.5
2734.3 | 1034.3 | 330.8 | 320.7 | 451.4 | 467
2735.3 | 1035.3 | 330.7 | 320.9 | 452.6 | 466.7
2736.3 | 1036.3 | 330.6 | 327.9 | 455.8 | 466.5
2737.3 | 1037.3 | 330.7 | 326.4 | 450 | 459.2
2738.3 | 1038.3 | 330.7 | 325.3 | 447 | 453.9
2739.3 | 1039.3 | 330.8 | 323.3 | 446 | 454.9
2740.3 | 1040.3 | 330.9 | 325.3 | 447.5 | 458.8
2741.3 | 1041.3 | 330.8 | 325.2 | 447 | 459.4
2742.3 | 1042.3 | 330.9 | 325 | 443.3 | 457.5
2743.3 | 1043.3 | 330.9 | 333.6 | 446.8 | 454.8
2744.3 | 1044.3 | 330.9 | 337.6 | 449.4 | 453.3
2745.3 | 1045.3 | 331 | 344.2 | 452.4 | 450.5
2746.3 | 1046.3 | 331.1 | 350.8 | 453.5 | 451.1
2747.3 | 1047.3 | 331.2 | 351.4 | 449 | 451.7
2748.3 | 1048.3 | 331.3 | 350.3 | 442.4 | 446.2
2749.3 | 1049.3 | 331.6 | 343.8 | 432.3 | 441.4
2750.3 | 1050.3 | 331.8 | 340.6 | 427.5 | 443.4
2751.3 | 1051.3 | 331.9 | 340.9 | 436.7 | 453.3
2752.3 | 1052.3 | 332.1 | 336.1 | 436.9 | 460.6
2753.3 | 1053.3 | 332.1 | 330.5 | 436.4 | 459.8
2754.3 | 1054.3 | 332.3 | 326.4 | 440 | 456.9
2755.3 | 1055.3 | 332.3 | 328.9 | 445.3 | 461.1
2756.3 | 1056.3 | 332.4 | 336.6 | 459.4 | 467.1
2757.3 | 1057.3 | 332.5 | 333.4 | 462.1 | 468.2
2758.3 | 1058.3 | 332.5 | 330.9 | 461.3 | 465.9
2759.3 | 1059.3 | 332.6 | 327.2 | 457.9 | 462.5
2760.3 | 1060.3 | 332.7 | 323.7 | 456.4 | 459.8
2761.3 | 1061.3 | 332.8 | 324.3 | 460.5 | 460.8
2762.3 | 1062.3 | 332.9 | 332.7 | 472.1 | 468.5
2763.3 | 1063.3 | 333 | 335.3 | 474.6 | 477
2764.3 | 1064.3 | 333.1 | 335.7 | 477.1 | 473.3
2765.3 | 1065.3 | 333 | 335.9 | 478.7 | 473.7
2766.3 | 1066.3 | 333.2 | 332.6 | 477.3 | 476.3
2767.3 | 1067.3 | 333.3 | 330.1 | 468.2 | 473.1
2768.3 | 1068.3 | 333.5 | 325.8 | 467.2 | 473
2769.3 | 1069.3 | 333.8 | 322 | 463.7 | 471
2770.3 | 1070.3 | 333.9 | 323 | 466 | 471.8
2771.3 | 1071.3 | 334 | 323.6 | 463.6 | 471.1
2772.3 | 1072.3 | 334.1 | 318.9 | 459 | 471.6
2773.3 | 1073.3 | 334.1 | 314.9 | 455.8 | 471.3
2774.3 | 1074.3 | 334.3 | 310.5 | 449.6 | 471.3
2775.3 | 1075.3 | 334.3 | 307.3 | 445.4 | 469.7
2776.3 | 1076.3 | 334.3 | 303.9 | 444.9 | 470.3
2777.3 | 1077.3 | 334.4 | 301.6 | 444.2 | 470.9
2778.3 | 1078.3 | 334.4 | 301.2 | 445.6 | 472.4
2779.3 | 1079.3 | 334.3 | 301.4 | 451.4 | 478.5
2780.3 | 1080.3 | 334.1 | 302.5 | 454.9 | 484.3
2781.3 | 1081.3 | 334 | 304.1 | 462.4 | 487.7
2782.3 | 1082.3 | 334 | 306.2 | 467.7 | 490.1
2783.3 | 1083.3 | 334 | 312.3 | 476.7 | 493.9
2784.3 | 1084.3 | 334 | 318.2 | 477.7 | 493
2785.3 | 1085.3 | 334 | 315.8 | 474.2 | 489.3
2786.3 | 1086.3 | 334.1 | 311.6 | 464.1 | 482.3
2787.3 | 1087.3 | 334.4 | 306.4 | 454.5 | 476.1
2788.3 | 1088.3 | 334.6 | 301.6 | 449.2 | 477.4
2789.3 | 1089.3 | 334.8 | 299.6 | 450.2 | 481.8
2790.3 | 1090.3 | 334.9 | 298.1 | 447 | 482.6
2791.3 | 1091.3 | 335.1 | 297.8 | 445.9 | 480.2
2792.3 | 1092.3 | 335.1 | 298.3 | 445.8 | 477.4
2793.3 | 1093.3 | 335.1 | 302.7 | 450.7 | 478.3
2794.3 | 1094.3 | 335.1 | 309.7 | 460.6 | 478.1
2795.3 | 1095.3 | 335.2 | 318.2 | 471.1 | 478
2796.3 | 1096.3 | 335.3 | 324.8 | 482.4 | 478.2
2797.3 | 1097.3 | 335.5 | 326 | 486.8 | 481.6
2798.3 | 1098.3 | 335.7 | 323.1 | 482.8 | 487.6
2799.3 | 1099.3 | 336 | 323.5 | 482.7 | 487.6
2800.3 | 1100.3 | 336.3 | 324 | 481.8 | 487.9
2801.3 | 1101.3 | 336.6 | 324.8 | 480.3 | 486.3
2802.3 | 1102.3 | 336.8 | 328.6 | 478.9 | 485.2
2803.3 | 1103.3 | 337.2 | 325.9 | 474.9 | 481.3
2804.3 | 1104.3 | 337.5 | 327 | 473.8 | 476.5
2805.3 | 1105.3 | 337.8 | 329.8 | 473 | 474.8
2806.3 | 1106.3 | 338.1 | 333.7 | 466.5 | 469.9
2807.3 | 1107.3 | 338.4 | 335.9 | 458.4 | 466.7
2808.3 | 1108.3 | 338.6 | 332.4 | 452.5 | 467.9
2809.3 | 1109.3 | 338.8 | 327.7 | 447.3 | 472.2
2810.3 | 1110.3 | 339 | 322.2 | 440.3 | 474
2811.3 | 1111.3 | 339.2 | 317.8 | 430.8 | 468.8
2812.3 | 1112.3 | 339.4 | 312.8 | 423.8 | 469.4
2813.3 | 1113.3 | 339.5 | 309.5 | 419.1 | 468.2
2814.3 | 1114.3 | 339.5 | 308.2 | 419.7 | 472.7
2815.3 | 1115.3 | 339.6 | 308.3 | 416.9 | 469.9
2816.3 | 1116.3 | 339.6 | 307.2 | 413.1 | 467.2
2817.3 | 1117.3 | 339.6 | 304.8 | 408.5 | 462.6
2818.3 | 1118.3 | 339.6 | 302.4 | 405.7 | 459.3
2819.3 | 1119.3 | 339.5 | 299 | 398.3 | 454.2
2820.3 | 1120.3 | 339.5 | 294.9 | 389.1 | 450.2
2821.3 | 1121.3 | 339.4 | 290.9 | 385.1 | 448.9
2822.3 | 1122.3 | 339.3 | 286.5 | 381.8 | 447.5
2823.3 | 1123.3 | 339.1 | 284.5 | 378.9 | 446.5
2824.3 | 1124.3 | 338.9 | 285.2 | 379.9 | 447.4
2825.3 | 1125.3 | 338.7 | 281.9 | 375.5 | 445.2
2826.3 | 1126.3 | 338.5 | 279.9 | 370.5 | 442.3
2827.3 | 1127.3 | 338.2 | 285.5 | 380.7 | 448.9
2828.3 | 1128.3 | 338 | 286.9 | 385.5 | 456.4
2829.3 | 1129.3 | 337.8 | 283.2 | 381.8 | 454.5
2830.3 | 1130.3 | 337.6 | 279.4 | 379.5 | 450.1
2831.3 | 1131.3 | 337.3 | 276.8 | 382.8 | 451.2
2832.3 | 1132.3 | 337.1 | 277.9 | 385.4 | 449
2833.3 | 1133.3 | 336.9 | 279.1 | 389.6 | 451.9
2834.3 | 1134.3 | 336.6 | 280.4 | 395.1 | 460.5
2835.3 | 1135.3 | 336.4 | 283.7 | 405.5 | 461.5
2836.3 | 1136.3 | 336.2 | 287.1 | 412.9 | 463.7
2837.3 | 1137.3 | 336 | 289.3 | 416.6 | 463.5
2838.3 | 1138.3 | 335.8 | 290.1 | 419.8 | 464.7
2839.3 | 1139.3 | 335.7 | 291.3 | 424 | 466.8
2840.3 | 1140.3 | 335.6 | 288.4 | 422 | 463.5
2841.3 | 1141.3 | 335.6 | 287 | 421 | 463.4
2842.3 | 1142.3 | 335.6 | 285 | 418.1 | 461.3
2843.3 | 1143.3 | 335.6 | 282.8 | 417.1 | 459.8
2844.3 | 1144.3 | 335.5 | 282.5 | 413.7 | 458.4
2845.3 | 1145.3 | 335.5 | 282.5 | 409.9 | 453
2846.3 | 1146.3 | 335.5 | 285.4 | 406.8 | 451.5
2847.3 | 1147.3 | 335.4 | 292.2 | 406.3 | 449.1
2848.3 | 1148.3 | 335.4 | 297.8 | 407.7 | 447.6
2849.3 | 1149.3 | 335.4 | 309.6 | 413.8 | 448.3
2850.3 | 1150.3 | 335.4 | 317.2 | 424 | 451.4
2851.3 | 1151.3 | 335.4 | 326.2 | 435.6 | 451.3
2852.3 | 1152.3 | 335.4 | 328.2 | 443.5 | 453.2
2853.3 | 1153.3 | 335.5 | 327.6 | 445.8 | 459.4
2854.3 | 1154.3 | 335.7 | 326.9 | 451.6 | 466.3
2855.3 | 1155.3 | 335.9 | 330.5 | 456.1 | 473
2856.3 | 1156.3 | 336.2 | 333.2 | 458.9 | 475.7
2857.3 | 1157.3 | 336.5 | 333.7 | 459.6 | 468.4
2858.3 | 1158.3 | 336.8 | 333.9 | 460.4 | 467.6
2859.3 | 1159.3 | 337.1 | 338 | 463.3 | 469.1
2860.3 | 1160.3 | 337.5 | 348.1 | 470.3 | 470.6
2861.3 | 1161.3 | 337.9 | 356.5 | 473.2 | 470
2862.3 | 1162.3 | 338.3 | 359.5 | 469.3 | 463.9
2863.3 | 1163.3 | 338.8 | 362.1 | 466.6 | 458.8
2864.3 | 1164.3 | 339.3 | 367.1 | 467.4 | 457.6
2865.3 | 1165.3 | 339.8 | 364.1 | 461.1 | 454.8
2866.3 | 1166.3 | 340.4 | 366.7 | 463.7 | 456
2867.3 | 1167.3 | 340.9 | 366.4 | 462.9 | 455
2868.3 | 1168.3 | 341.4 | 368.1 | 469.9 | 459
2869.3 | 1169.3 | 342 | 369.2 | 476.7 | 463.8
2870.3 | 1170.3 | 342.5 | 370.5 | 484.3 | 464.9
2871.3 | 1171.3 | 343 | 379.1 | 489 | 462.3
2872.3 | 1172.3 | 343.5 | 384.5 | 490.5 | 458.3
2873.3 | 1173.3 | 344 | 388.5 | 489.9 | 457.9
2874.3 | 1174.3 | 344.6 | 388.2 | 485.3 | 457.4
2875.3 | 1175.3 | 345.1 | 390.8 | 481.9 | 454.8
2876.3 | 1176.3 | 345.7 | 388.8 | 472.9 | 449.3
2877.3 | 1177.3 | 346.3 | 392.7 | 475.5 | 451.8
2878.3 | 1178.3 | 346.8 | 398 | 479.2 | 455
2879.3 | 1179.3 | 347.4 | 399.2 | 486.5 | 458.2
2880.3 | 1180.3 | 347.9 | 399.3 | 491.1 | 460.6
2881.3 | 1181.3 | 348.4 | 407.7 | 496 | 456.2
2882.3 | 1182.3 | 349 | 411.4 | 501.7 | 453.8
2883.3 | 1183.3 | 349.5 | 418.9 | 502.2 | 452.3
2884.3 | 1184.3 | 350.1 | 430.2 | 504.2 | 452.8
2885.3 | 1185.3 | 350.7 | 429 | 504.5 | 452.4
2886.3 | 1186.3 | 351.3 | 437.1 | 504.1 | 450.9
2887.3 | 1187.3 | 351.9 | 432.6 | 496.2 | 448.2
2888.3 | 1188.3 | 352.5 | 427.1 | 489.7 | 446.2
2889.3 | 1189.3 | 353.2 | 427.4 | 492.1 | 449.1
2890.3 | 1190.3 | 353.9 | 434.7 | 495.5 | 452.1
2891.3 | 1191.3 | 354.5 | 436.8 | 498.2 | 455.6
2892.3 | 1192.3 | 355.1 | 438 | 502.5 | 459.1
2893.3 | 1193.3 | 355.8 | 432.6 | 496.3 | 456.4
2894.3 | 1194.3 | 356.4 | 426.2 | 487.4 | 453.1
2895.3 | 1195.3 | 357 | 419.9 | 483.5 | 454.6
2896.3 | 1196.3 | 357.7 | 415.7 | 485.8 | 462.3
2897.3 | 1197.3 | 358.3 | 405.8 | 482.5 | 464.1
2898.3 | 1198.3 | 358.9 | 397.8 | 480 | 464
2899.3 | 1199.3 | 359.4 | 393.7 | 478.7 | 463
2900.3 | 1200.3 | 359.8 | 385.1 | 476 | 462.4
2901.3 | 1201.3 | 360.2 | 376.8 | 469.5 | 461.4
2902.3 | 1202.3 | 360.5 | 369.5 | 463.3 | 457.4
2903.3 | 1203.3 | 360.8 | 362.4 | 454 | 452.8
2904.3 | 1204.3 | 361 | 355.4 | 447 | 450.6
2905.3 | 1205.3 | 361.2 | 347.5 | 437.4 | 450.5
2906.3 | 1206.3 | 361.2 | 339.5 | 433 | 449.9
2907.3 | 1207.3 | 361.2 | 333.9 | 430.9 | 455.5
2908.3 | 1208.3 | 361.1 | 331.7 | 436.3 | 457.3
2909.3 | 1209.3 | 360.9 | 333.3 | 444.5 | 460.2
2910.3 | 1210.3 | 360.7 | 337.3 | 453 | 462.6
2911.3 | 1211.3 | 360.5 | 338.9 | 460.3 | 466.4
2912.3 | 1212.3 | 360.3 | 338.1 | 462.9 | 465.9
2913.3 | 1213.3 | 360.2 | 341 | 459.2 | 457.7
2914.3 | 1214.3 | 360.1 | 344.8 | 460.3 | 456.8
2915.3 | 1215.3 | 360.1 | 346.9 | 458.9 | 456.9
2916.3 | 1216.3 | 360 | 345.3 | 456.4 | 455.5
2917.3 | 1217.3 | 360.1 | 342.5 | 449.9 | 451.6
2918.3 | 1218.3 | 360.2 | 338.1 | 444.9 | 450.4
2919.3 | 1219.3 | 360.4 | 334.2 | 442.5 | 451
2920.3 | 1220.3 | 360.5 | 330.4 | 440.8 | 452.7
2921.3 | 1221.3 | 360.5 | 331.6 | 442.9 | 455.9
2922.3 | 1222.3 | 360.6 | 334.1 | 446.4 | 456.4
2923.3 | 1223.3 | 360.6 | 336.7 | 444.5 | 453.1
2924.3 | 1224.3 | 360.7 | 336.9 | 438.7 | 447.2
2925.3 | 1225.3 | 360.8 | 336.6 | 435.5 | 445.9
2926.3 | 1226.3 | 360.9 | 332 | 430.3 | 447.8
2927.3 | 1227.3 | 361 | 331.5 | 434 | 452.7
2928.3 | 1228.3 | 361 | 324.9 | 431.9 | 453.4
2929.3 | 1229.3 | 361.1 | 321.3 | 430.3 | 455.2
2930.3 | 1230.3 | 361.1 | 325.9 | 432.5 | 456.5
2931.3 | 1231.3 | 361.2 | 326.7 | 432.2 | 450.9
2932.3 | 1232.3 | 361.2 | 329.9 | 433.4 | 446.9
2933.3 | 1233.3 | 361.2 | 326.4 | 430.7 | 447.8
2934.3 | 1234.3 | 361.3 | 331.1 | 436.1 | 448.6
2935.3 | 1235.3 | 361.3 | 332.7 | 436.8 | 450.2
2936.3 | 1236.3 | 361.4 | 332.3 | 434.2 | 449.3
2937.3 | 1237.3 | 361.5 | 331.2 | 430.2 | 447
2938.3 | 1238.3 | 361.6 | 328.7 | 432.6 | 450.9
2939.3 | 1239.3 | 361.8 | 325.1 | 434.6 | 456.1
2940.3 | 1240.3 | 361.9 | 327.8 | 438.4 | 455.9
2941.3 | 1241.3 | 362 | 332.5 | 444.2 | 454.5
2942.3 | 1242.3 | 362 | 336.9 | 444.4 | 452.2
2943.3 | 1243.3 | 362.1 | 338.5 | 445.2 | 454.7
2944.3 | 1244.3 | 362.2 | 339.5 | 446.9 | 453.9
2945.3 | 1245.3 | 362.4 | 344.2 | 451.5 | 454.6
2946.3 | 1246.3 | 362.6 | 344.1 | 449.3 | 454
2947.3 | 1247.3 | 362.8 | 350.4 | 455.4 | 454.6
2948.3 | 1248.3 | 363.1 | 347.2 | 455.7 | 453.9
2949.3 | 1249.3 | 363.3 | 355.1 | 460.5 | 452.2
2950.3 | 1250.3 | 363.6 | 369.8 | 471.7 | 452.7
2951.3 | 1251.3 | 363.9 | 378.7 | 473.6 | 452.8
2952.3 | 1252.3 | 364.3 | 384.9 | 480 | 457
2953.3 | 1253.3 | 364.7 | 393 | 484.1 | 458.3
2954.3 | 1254.3 | 365.2 | 393.9 | 483.3 | 458.6
2955.3 | 1255.3 | 365.8 | 395.1 | 483.3 | 455.8
2956.3 | 1256.3 | 366.5 | 395 | 473.9 | 449
2957.3 | 1257.3 | 367.1 | 398 | 471.8 | 448.7
2958.3 | 1258.3 | 367.8 | 395.5 | 472.2 | 451.1
2959.3 | 1259.3 | 368.4 | 400.8 | 479.2 | 451.9
2960.3 | 1260.3 | 369.1 | 406.9 | 485.8 | 454.5
2961.3 | 1261.3 | 369.7 | 413.5 | 493.1 | 458.6
2962.3 | 1262.3 | 370.3 | 416.4 | 495.6 | 459.1
2963.3 | 1263.3 | 371 | 420.1 | 499.6 | 462.4
2964.3 | 1264.3 | 371.8 | 418 | 494.5 | 462.7
2965.3 | 1265.3 | 372.6 | 418.3 | 493.4 | 466
2966.3 | 1266.3 | 373.4 | 417.1 | 498.5 | 467.3
2967.3 | 1267.3 | 374.3 | 418.6 | 498.4 | 464.7
2968.3 | 1268.3 | 375.2 | 431 | 501.5 | 463.1
2969.3 | 1269.3 | 376.1 | 437.9 | 503.8 | 462.2
2970.3 | 1270.3 | 377 | 439.4 | 509.1 | 460.3
2971.3 | 1271.3 | 377.9 | 436.6 | 507.9 | 461.9
2972.3 | 1272.3 | 378.8 | 435.2 | 511.6 | 466.7
2973.3 | 1273.3 | 379.7 | 434 | 523.1 | 477.1
2974.3 | 1274.3 | 380.6 | 434.1 | 523.9 | 476.8
2975.3 | 1275.3 | 381.5 | 432.7 | 515.1 | 467.7
2976.3 | 1276.3 | 382.4 | 440.4 | 511 | 464.7
2977.3 | 1277.3 | 383.3 | 445.1 | 508.7 | 461.4
2978.3 | 1278.3 | 384.2 | 438.9 | 510.9 | 465.4
2979.3 | 1279.3 | 385 | 430.9 | 506.7 | 468.7
2980.3 | 1280.3 | 385.8 | 420.8 | 493.3 | 465.4
2981.3 | 1281.3 | 386.6 | 410.2 | 486.7 | 465.3
2982.3 | 1282.3 | 387.3 | 405.1 | 486.1 | 465.7
2983.3 | 1283.3 | 387.9 | 399.4 | 483.9 | 467.5
2984.3 | 1284.3 | 388.4 | 391.1 | 478 | 466.2
2985.3 | 1285.3 | 388.9 | 385.4 | 471.6 | 462.9
2986.3 | 1286.3 | 389.3 | 377.9 | 464.7 | 459.4
2987.3 | 1287.3 | 389.6 | 370.6 | 458.8 | 461.8
2988.3 | 1288.3 | 389.8 | 361.9 | 451.7 | 459.2
2989.3 | 1289.3 | 390.1 | 357.3 | 456.1 | 463.9
2990.3 | 1290.3 | 390.2 | 350.3 | 458.1 | 469.8
2991.3 | 1291.3 | 390.4 | 345.1 | 457.2 | 472.1
2992.3 | 1292.3 | 390.4 | 343 | 461 | 473.6
2993.3 | 1293.3 | 390.4 | 342.4 | 462.4 | 473.1
2994.3 | 1294.3 | 390.5 | 344.6 | 464.2 | 472.2
2995.3 | 1295.3 | 390.6 | 344.7 | 469.3 | 469.6
2996.3 | 1296.3 | 390.6 | 344.4 | 471.8 | 471.3
2997.3 | 1297.3 | 390.8 | 342.3 | 471.6 | 470.8
2998.3 | 1298.3 | 390.9 | 338.6 | 471.6 | 472.3
2999.3 | 1299.3 | 391.1 | 338.9 | 474.9 | 470
3000.3 | 1300.3 | 391.3 | 346.9 | 487.9 | 472.4
3001.3 | 1301.3 | 391.6 | 360.6 | 488.8 | 469.4
3002.3 | 1302.3 | 391.9 | 369.2 | 490.4 | 463.9
3003.3 | 1303.3 | 392.3 | 371.8 | 491.2 | 460.9
3004.3 | 1304.3 | 392.9 | 380.5 | 491.1 | 457.6
3005.3 | 1305.3 | 393.4 | 391.1 | 488.1 | 456.1
3006.3 | 1306.3 | 394 | 389.9 | 482.1 | 455.1
3007.3 | 1307.3 | 394.6 | 387.4 | 477.8 | 453.5
3008.3 | 1308.3 | 395.3 | 387.7 | 481.2 | 455.1
3009.3 | 1309.3 | 395.9 | 393.6 | 483.8 | 456.1
3010.3 | 1310.3 | 396.6 | 402.5 | 483.6 | 457.3
3011.3 | 1311.3 | 397.2 | 406.7 | 483.8 | 457.5
3012.3 | 1312.3 | 397.9 | 408 | 483.5 | 459
3013.3 | 1313.3 | 398.5 | 410.3 | 477.9 | 453.5
3014.3 | 1314.3 | 399 | 406.6 | 469.1 | 447.7
3015.3 | 1315.3 | 399.5 | 400.4 | 459.4 | 441.9
3016.3 | 1316.3 | 400 | 398.4 | 455.2 | 440.9
3017.3 | 1317.3 | 400.5 | 403.1 | 453.9 | 440.9
3018.3 | 1318.3 | 401 | 408 | 455.3 | 440.8
3019.3 | 1319.3 | 401.5 | 409.9 | 452.9 | 438.1
3020.3 | 1320.3 | 401.9 | 412.1 | 451.8 | 438.5
3021.3 | 1321.3 | 402.2 | 409.4 | 448.4 | 437.6
3022.3 | 1322.3 | 402.6 | 405.3 | 444.8 | 436.3
3023.3 | 1323.3 | 403 | 396.6 | 438.1 | 432.7
3024.3 | 1324.3 | 403.3 | 390 | 435.2 | 433.5
3025.3 | 1325.3 | 403.7 | 390.7 | 436 | 436.8
3026.3 | 1326.3 | 404.1 | 388.4 | 432.8 | 434.7
3027.3 | 1327.3 | 404.4 | 390.9 | 432.9 | 435.4
3028.3 | 1328.3 | 404.8 | 393.9 | 437.3 | 435.6
3029.3 | 1329.3 | 405.3 | 393.9 | 438.8 | 432.9
3030.3 | 1330.3 | 405.6 | 389.6 | 437.9 | 431.1
3031.3 | 1331.3 | 406 | 389.7 | 437 | 429.9
3032.3 | 1332.3 | 406.3 | 386.6 | 433.1 | 427.5
3033.3 | 1333.3 | 406.5 | 383.7 | 432.7 | 427.6
3034.3 | 1334.3 | 406.9 | 385.8 | 437.9 | 434.5
3035.3 | 1335.3 | 407.2 | 385.1 | 442.1 | 438.3
3036.3 | 1336.3 | 407.6 | 383.1 | 444.9 | 441.6
3037.3 | 1337.3 | 407.8 | 381.8 | 443.2 | 441.9
3038.3 | 1338.3 | 408.1 | 382.5 | 445.1 | 441.3
3039.3 | 1339.3 | 408.5 | 382.4 | 446.9 | 445.7
3040.3 | 1340.3 | 408.8 | 381.3 | 448.5 | 446.4
3041.3 | 1341.3 | 409.1 | 376.3 | 441.8 | 440.3
3042.3 | 1342.3 | 409.2 | 373.4 | 435.9 | 433.4
3043.3 | 1343.3 | 409.5 | 371.5 | 430.5 | 428.9
3044.3 | 1344.3 | 409.7 | 372 | 429.9 | 427.9
3045.3 | 1345.3 | 410 | 370.2 | 433 | 431.3
3046.3 | 1346.3 | 410.3 | 369 | 433.2 | 434.8
3047.3 | 1347.3 | 410.6 | 370.2 | 446.7 | 439.3
3048.3 | 1348.3 | 411 | 377.6 | 455.2 | 444.1
3049.3 | 1349.3 | 411.4 | 379.1 | 456.5 | 445
3050.3 | 1350.3 | 411.6 | 371.6 | 452.7 | 445.1
3051.3 | 1351.3 | 411.8 | 366.9 | 449.7 | 444.4
3052.3 | 1352.3 | 412 | 364.4 | 450.7 | 447.5
3053.3 | 1353.3 | 412.2 | 368.5 | 453.3 | 448.8
3054.3 | 1354.3 | 412.5 | 363.4 | 452.7 | 450.1
3055.3 | 1355.3 | 412.5 | 358.5 | 453.4 | 452.2
3056.3 | 1356.3 | 412.7 | 359.4 | 461.2 | 460.8
3057.3 | 1357.3 | 413 | 362.2 | 461.5 | 460.1
3058.3 | 1358.3 | 413.3 | 364.2 | 460.4 | 455.1
3059.3 | 1359.3 | 413.6 | 367.5 | 459.1 | 453.5
3060.3 | 1360.3 | 414 | 368.6 | 461.2 | 453
3061.3 | 1361.3 | 414.5 | 377.5 | 465.2 | 454.3
3062.3 | 1362.3 | 415.1 | 386.8 | 473.1 | 454.3
3063.3 | 1363.3 | 415.8 | 397.3 | 478.4 | 454.7
3064.3 | 1364.3 | 416.5 | 405.5 | 476.5 | 449.7
3065.3 | 1365.3 | 416.9 | 408.5 | 472.3 | 445.1
3066.3 | 1366.3 | 417.3 | 408 | 466 | 439.6
3067.3 | 1367.3 | 417.7 | 403 | 461.2 | 437
3068.3 | 1368.3 | 418.1 | 400.8 | 460 | 438.8
3069.3 | 1369.3 | 418.6 | 405.8 | 461.3 | 438.7
3070.3 | 1370.3 | 419.2 | 405.4 | 460.3 | 438.5
3071.3 | 1371.3 | 419.8 | 403.5 | 465.8 | 441.9
3072.3 | 1372.3 | 420.3 | 396.7 | 461 | 441.5
3073.3 | 1373.3 | 420.8 | 392.7 | 465.7 | 445.9
3074.3 | 1374.3 | 421.3 | 392.5 | 471 | 452.3
3075.3 | 1375.3 | 422.2 | 407.4 | 480.5 | 455.2
3076.3 | 1376.3 | 423.1 | 420 | 489.8 | 454.1
3077.3 | 1377.3 | 423.9 | 426.4 | 489.3 | 450.5
3078.3 | 1378.3 | 424.4 | 421.7 | 480.2 | 443.6
3079.3 | 1379.3 | 424.9 | 418.6 | 474.4 | 439.8
3080.3 | 1380.3 | 425.5 | 417.5 | 471.2 | 443.1
3081.3 | 1381.3 | 426.1 | 408.7 | 463.7 | 445.1
3082.3 | 1382.3 | 426.3 | 402.9 | 459.9 | 449.3
3083.3 | 1383.3 | 426.5 | 401.1 | 465.2 | 459.6
3084.3 | 1384.3 | 426.9 | 398.7 | 472.7 | 464.9
3085.3 | 1385.3 | 427.3 | 393.6 | 476 | 469.1
3086.3 | 1386.3 | 427.7 | 388.8 | 483.4 | 473.4
3087.3 | 1387.3 | 428.4 | 390.6 | 492.4 | 476.5
3088.3 | 1388.3 | 429.2 | 397.2 | 502.1 | 480.4
3089.3 | 1389.3 | 430.2 | 404.9 | 508 | 480.9
3090.3 | 1390.3 | 431 | 410.1 | 510.6 | 480.9
3091.3 | 1391.3 | 431.8 | 408.3 | 509.6 | 479.9
3092.3 | 1392.3 | 432.5 | 405.9 | 506.8 | 477.8
3093.3 | 1393.3 | 433.3 | 400 | 506.4 | 479.8
3094.3 | 1394.3 | 433.7 | 391.4 | 501.5 | 481
3095.3 | 1395.3 | 434.2 | 386.4 | 503.2 | 488.4
3096.3 | 1396.3 | 434.8 | 388.2 | 511.7 | 493.9
3097.3 | 1397.3 | 435.6 | 405.7 | 528.8 | 502.8
3098.3 | 1398.3 | 436.7 | 429.5 | 534.8 | 501.7
3099.3 | 1399.3 | 437.8 | 443.1 | 543.7 | 502.2
3100.3 | 1400.3 | 439 | 455.6 | 546.8 | 502.2
3101.3 | 1401.3 | 440.1 | 460.3 | 550.9 | 501.1
3102.3 | 1402.3 | 441.1 | 462.8 | 554.5 | 497.9
3103.3 | 1403.3 | 442.4 | 467.2 | 565.3 | 506.8
3104.3 | 1404.3 | 443.5 | 469.4 | 568.3 | 517.1
3105.3 | 1405.3 | 444.5 | 478.7 | 573.3 | 518.8
3106.3 | 1406.3 | 445.7 | 486.4 | 576.6 | 519.3
3107.3 | 1407.3 | 447.2 | 504.3 | 579 | 518.1
3108.3 | 1408.3 | 448.7 | 517.5 | 580.1 | 513.3
3109.3 | 1409.3 | 450.4 | 537.2 | 586.5 | 516.1
3110.3 | 1410.3 | 452 | 554.3 | 582.3 | 513.5
3111.3 | 1411.3 | 453.4 | 565.3 | 572.8 | 506.3
3112.3 | 1412.3 | 455 | 578.6 | 572.1 | 509.7
3113.3 | 1413.3 | 457 | 593.8 | 578 | 519.9
3114.3 | 1414.3 | 459.3 | 616.4 | 586 | 524.3
3115.3 | 1415.3 | 461.3 | 640.3 | 588.8 | 528.5
3116.3 | 1416.3 | 463.1 | 657.1 | 588.5 | 528.2
3117.3 | 1417.3 | 464.8 | 671.3 | 593.6 | 528.1
3118.3 | 1418.3 | 466.5 | 682.7 | 595.2 | 532
3119.3 | 1419.3 | 468.1 | 695.3 | 598.2 | 535.7
3120.3 | 1420.3 | 469.4 | 692 | 591.5 | 534.1
3121.3 | 1421.3 | 470.5 | 679.8 | 582.8 | 534.5
3122.3 | 1422.3 | 471.6 | 680.2 | 590.8 | 543.6
3123.3 | 1423.3 | 472.3 | 678.9 | 595.5 | 549.9
3124.3 | 1424.3 | 472.6 | 674.5 | 592.6 | 552.3
3125.3 | 1425.3 | 473 | 683.5 | 595 | 551.6
3126.3 | 1426.3 | 473.7 | 701.1 | 601.4 | 547.4
3127.3 | 1427.3 | 474.6 | 707 | 607.3 | 546.4
3128.3 | 1428.3 | 474.9 | 708.7 | 606.3 | 546.1
3129.3 | 1429.3 | 475 | 710.8 | 610.8 | 545.7
3130.3 | 1430.3 | 475.2 | 717.2 | 616.8 | 546.4
3131.3 | 1431.3 | 475.3 | 720.8 | 623.1 | 549.9
3132.3 | 1432.3 | 475.2 | 717.3 | 626.1 | 554.7
3133.3 | 1433.3 | 475.1 | 712.6 | 626.8 | 556.5
3134.3 | 1434.3 | 475.6 | 715.8 | 629.6 | 558.5
3135.3 | 1435.3 | 476.2 | 721.9 | 626.4 | 556.8
3136.3 | 1436.3 | 477.1 | 724 | 627.8 | 558.1
3137.3 | 1437.3 | 478 | 721.4 | 635.5 | 563.4
3138.3 | 1438.3 | 478.8 | 722.7 | 634.6 | 564.4
3139.3 | 1439.3 | 479.5 | 726.2 | 638.9 | 571.2
3140.3 | 1440.3 | 480.6 | 725.3 | 639.1 | 577.9
3141.3 | 1441.3 | 481 | 718.9 | 637.2 | 578.8
3142.3 | 1442.3 | 481.2 | 721.4 | 640.1 | 581.9
3143.3 | 1443.3 | 481.7 | 730.5 | 643.9 | 579.4
3144.3 | 1444.3 | 482.3 | 740 | 649.2 | 578.9
3145.3 | 1445.3 | 482.9 | 741.4 | 646.3 | 576.5
3146.3 | 1446.3 | 483.3 | 741.5 | 647 | 576
3147.3 | 1447.3 | 483.9 | 738.9 | 645 | 578.6
3148.3 | 1448.3 | 484 | 734.1 | 639 | 577.6
3149.3 | 1449.3 | 484.2 | 727.4 | 635.4 | 578.9
3150.3 | 1450.3 | 484.5 | 721 | 628.5 | 582.3
3151.3 | 1451.3 | 484.5 | 714.5 | 620.8 | 584
3152.3 | 1452.3 | 484.4 | 704.9 | 609.1 | 586
3153.3 | 1453.3 | 483.8 | 690.3 | 595.5 | 582.3
3154.3 | 1454.3 | 483.1 | 684.1 | 586.6 | 582.2
3155.3 | 1455.3 | 482.3 | 676.6 | 574.7 | 578.8
3156.3 | 1456.3 | 481.9 | 669.4 | 563.4 | 573.5
3157.3 | 1457.3 | 481.4 | 661.3 | 555.6 | 570.9
3158.3 | 1458.3 | 480 | 650.3 | 547.5 | 567.4
3159.3 | 1459.3 | 479 | 639 | 539.6 | 567.5
3160.3 | 1460.3 | 478.1 | 632.1 | 539.6 | 572.7
3161.3 | 1461.3 | 477.4 | 630.3 | 541 | 574.3
3162.3 | 1462.3 | 477 | 633.5 | 543.4 | 575.6
3163.3 | 1463.3 | 477 | 645.2 | 552.4 | 576.9
3164.3 | 1464.3 | 477.6 | 654.2 | 560.6 | 576
3165.3 | 1465.3 | 478.1 | 651.6 | 558.2 | 574.2
3166.3 | 1466.3 | 477.9 | 646.2 | 566.1 | 581.8
3167.3 | 1467.3 | 478.3 | 653.5 | 585.1 | 590.2
3168.3 | 1468.3 | 478.9 | 661 | 591.3 | 592.5
3169.3 | 1469.3 | 479.3 | 661.6 | 592.7 | 589.2
3170.3 | 1470.3 | 479.6 | 665.6 | 592.4 | 583.7
3171.3 | 1471.3 | 479.7 | 669.2 | 599 | 583.9
3172.3 | 1472.3 | 480.2 | 677.5 | 604.8 | 584.2
3173.3 | 1473.3 | 481.2 | 684 | 607.8 | 585.7
3174.3 | 1474.3 | 481.9 | 680.7 | 610.1 | 584.4
3175.3 | 1475.3 | 482.8 | 683.3 | 618.1 | 586.8
3176.3 | 1476.3 | 483.7 | 676.2 | 619.4 | 590.3
3177.3 | 1477.3 | 484.5 | 669.2 | 619.1 | 594.4
3178.3 | 1478.3 | 485.2 | 663.6 | 611.7 | 587.3
3179.3 | 1479.3 | 485.7 | 656.6 | 606.4 | 584.4
3180.3 | 1480.3 | 486.8 | 651.4 | 596.8 | 581.6
3181.3 | 1481.3 | 487.9 | 662.6 | 600.1 | 583.5
3182.3 | 1482.3 | 489 | 673.8 | 613.3 | 594.5
3183.3 | 1483.3 | 489.5 | 678.2 | 623 | 601.3
3184.3 | 1484.3 | 489.9 | 684.7 | 627 | 598
3185.3 | 1485.3 | 490.9 | 702.2 | 635.8 | 597.2
3186.3 | 1486.3 | 492.1 | 706.8 | 639.5 | 598.2
3187.3 | 1487.3 | 493 | 701 | 637.7 | 598.2
3188.3 | 1488.3 | 494.1 | 698.1 | 636 | 600.4
3189.3 | 1489.3 | 495.7 | 709.6 | 633.2 | 594.2
3190.3 | 1490.3 | 497.1 | 709.7 | 638 | 595.6
3191.3 | 1491.3 | 498 | 712.4 | 646.6 | 602.2
3192.3 | 1492.3 | 498.8 | 714 | 650.4 | 606.8
3193.3 | 1493.3 | 499.6 | 712.1 | 649.8 | 608.6
3194.3 | 1494.3 | 500.8 | 714 | 645.9 | 603.6
3195.3 | 1495.3 | 502.1 | 725.1 | 642.7 | 596.8
3196.3 | 1496.3 | 502.9 | 736.4 | 637.8 | 591.5
3197.3 | 1497.3 | 503.5 | 739 | 630.5 | 586.2
3198.3 | 1498.3 | 504.1 | 737.3 | 619 | 582.6
3199.3 | 1499.3 | 504.4 | 733.8 | 612.6 | 580.1
3200.3 | 1500.3 | 504.9 | 742 | 619.5 | 584.2
3201.3 | 1501.3 | 506.4 | 750.9 | 626.6 | 590.7
3202.3 | 1502.3 | 507.5 | 747.9 | 635.5 | 600.6
3203.3 | 1503.3 | 507.8 | 743.4 | 637.2 | 605.4
3204.3 | 1504.3 | 508 | 740.7 | 627.6 | 602
3205.3 | 1505.3 | 508.3 | 739.2 | 619.4 | 595.2
3206.3 | 1506.3 | 508.7 | 736.4 | 613.6 | 595.7
3207.3 | 1507.3 | 509.3 | 736.8 | 611.8 | 596.5
3208.3 | 1508.3 | 511 | 746.3 | 613.1 | 594.3
3209.3 | 1509.3 | 512.6 | 750 | 609.3 | 590.4
3210.3 | 1510.3 | 514.2 | 752.7 | 607.3 | 587.2
3211.3 | 1511.3 | 516 | 749.1 | 603.1 | 586.9
3212.3 | 1512.3 | 517.6 | 752.4 | 605.2 | 591.7
3213.3 | 1513.3 | 519.1 | 749.6 | 618.1 | 598.1
3214.3 | 1514.3 | 520.9 | 746.9 | 622.2 | 603.2
3215.3 | 1515.3 | 522.4 | 748.3 | 623.9 | 602
3216.3 | 1516.3 | 524.1 | 747.4 | 625 | 598.9
3217.3 | 1517.3 | 525.9 | 746.6 | 624.3 | 601.2
3218.3 | 1518.3 | 527.6 | 745.1 | 621.6 | 603.5
3219.3 | 1519.3 | 529.3 | 749.7 | 625.3 | 603.1
3220.3 | 1520.3 | 530.6 | 758.8 | 632.2 | 600.6
3221.3 | 1521.3 | 532.4 | 764.4 | 639.4 | 601.3
3222.3 | 1522.3 | 534.4 | 773 | 642.9 | 604.2
3223.3 | 1523.3 | 536 | 776.7 | 637.4 | 603
3224.3 | 1524.3 | 537.1 | 784.6 | 631.4 | 599
3225.3 | 1525.3 | 537.7 | 795.6 | 640.3 | 599.5
3226.3 | 1526.3 | 538.9 | 800.2 | 643 | 602.9
3227.3 | 1527.3 | 539.7 | 804.2 | 641.4 | 602.3
3228.3 | 1528.3 | 540.9 | 803.7 | 636 | 600.3
3229.3 | 1529.3 | 540.9 | 799.7 | 624.1 | 595.2
3230.3 | 1530.3 | 540.2 | 787.7 | 607.7 | 589.6
3231.3 | 1531.3 | 540 | 789 | 604.8 | 587.5
3232.3 | 1532.3 | 541.8 | 783.3 | 609.9 | 591.2
3233.3 | 1533.3 | 544 | 780.1 | 608.4 | 592.8
3234.3 | 1534.3 | 546.4 | 772.7 | 602.7 | 592.1
3235.3 | 1535.3 | 548.8 | 771.3 | 608.9 | 592.5
3236.3 | 1536.3 | 551 | 769.9 | 599 | 587.8
3237.3 | 1537.3 | 552.6 | 769.8 | 589 | 584
3238.3 | 1538.3 | 553.7 | 771.7 | 581.3 | 579.3
3239.3 | 1539.3 | 555.4 | 778.7 | 579 | 580.2
3240.3 | 1540.3 | 556.9 | 776.4 | 572.9 | 579.9
3241.3 | 1541.3 | 559.6 | 774.5 | 575.5 | 583.4
3242.3 | 1542.3 | 561.4 | 767.5 | 574 | 584.3
3243.3 | 1543.3 | 561.5 | 762.4 | 565.6 | 580.3
3244.3 | 1544.3 | 560.7 | 766.9 | 559 | 574.5
3245.3 | 1545.3 | 560.4 | 769.2 | 553.5 | 572.9
3246.3 | 1546.3 | 562 | 767.2 | 562.9 | 579.2
3247.3 | 1547.3 | 564.4 | 764.4 | 563.4 | 577.7
3248.3 | 1548.3 | 565.3 | 771 | 571.6 | 580.4
3249.3 | 1549.3 | 567.2 | 776.3 | 584.7 | 581.3
3250.3 | 1550.3 | 570 | 778.8 | 596.4 | 584.1
3251.3 | 1551.3 | 572.8 | 781 | 607.6 | 587.1
3252.3 | 1552.3 | 575.4 | 781.1 | 617.3 | 593.1
3253.3 | 1553.3 | 577.5 | 787.9 | 628.9 | 597.6
3254.3 | 1554.3 | 578.5 | 784 | 624.5 | 593
3255.3 | 1555.3 | 579.4 | 771.6 | 607.9 | 584
3256.3 | 1556.3 | 579.7 | 764 | 594.7 | 579
3257.3 | 1557.3 | 579.3 | 746.9 | 581 | 574.3
3258.3 | 1558.3 | 578.8 | 740.9 | 575.8 | 572
3259.3 | 1559.3 | 578.2 | 742.5 | 565.5 | 570.7
3260.3 | 1560.3 | 578.5 | 736.7 | 556.3 | 569.6
3261.3 | 1561.3 | 579.8 | 734.7 | 561 | 573.8
3262.3 | 1562.3 | 583 | 737.5 | 576.3 | 582.3
3263.3 | 1563.3 | 585.8 | 722.4 | 581.4 | 586.2
3264.3 | 1564.3 | 588.6 | 715.6 | 590.4 | 590.1
3265.3 | 1565.3 | 590.7 | 721 | 599.4 | 591.5
3266.3 | 1566.3 | 592.6 | 727.8 | 608 | 592.1
3267.3 | 1567.3 | 591.9 | 720.9 | 601.2 | 585
3268.3 | 1568.3 | 590.2 | 714.9 | 584.7 | 577
3269.3 | 1569.3 | 588.5 | 702.7 | 568.5 | 572.2
3270.3 | 1570.3 | 587.9 | 687.7 | 554.2 | 571.1
3271.3 | 1571.3 | 592.6 | 671.4 | 554 | 578.1
3272.3 | 1572.3 | 595.3 | 670.7 | 558 | 580.5
3273.3 | 1573.3 | 596 | 658.3 | 556.2 | 578.4
3274.3 | 1574.3 | 597.4 | 652.9 | 557 | 579.5
3275.3 | 1575.3 | 597.6 | 651.3 | 555.9 | 580.6
3276.3 | 1576.3 | 598.8 | 654.6 | 563.1 | 585.5
3277.3 | 1577.3 | 600.7 | 655.4 | 565.1 | 581.7
3278.3 | 1578.3 | 602.8 | 654 | 565.9 | 579
3279.3 | 1579.3 | 606.3 | 656.6 | 573.6 | 578.9
3280.3 | 1580.3 | 609.3 | 648.4 | 575.9 | 581
3281.3 | 1581.3 | 612.2 | 638.2 | 572.2 | 581.4
3282.3 | 1582.3 | 613.8 | 628.3 | 569.7 | 581.8
3283.3 | 1583.3 | 615.7 | 623.6 | 570.3 | 583.6
3284.3 | 1584.3 | 618.3 | 624.3 | 567.3 | 584.8
3285.3 | 1585.3 | 618.9 | 620.7 | 563.8 | 586.1
3286.3 | 1586.3 | 618.9 | 610.7 | 560.6 | 589.1
3287.3 | 1587.3 | 618 | 604.3 | 557.3 | 586.9
3288.3 | 1588.3 | 618.8 | 595.9 | 557.9 | 590.8
3289.3 | 1589.3 | 619.6 | 587.1 | 555 | 595
3290.3 | 1590.3 | 619.7 | 577.5 | 545.7 | 593.1
3291.3 | 1591.3 | 619 | 573.4 | 544.8 | 594.5
3292.3 | 1592.3 | 619.1 | 571.1 | 553 | 598.5
3293.3 | 1593.3 | 620.1 | 576.5 | 561.9 | 600.6
3294.3 | 1594.3 | 621.7 | 564.2 | 558.8 | 596.9
3295.3 | 1595.3 | 621.9 | 558.9 | 550.2 | 596.4
3296.3 | 1596.3 | 622.4 | 555.9 | 558.2 | 600.8
3297.3 | 1597.3 | 623.1 | 560.8 | 562.1 | 599.8
3298.3 | 1598.3 | 621.3 | 562.3 | 563.3 | 597.1
3299.3 | 1599.3 | 620.6 | 568.8 | 564.9 | 595.5
3300.3 | 1600.3 | 619.7 | 575.4 | 553 | 585.3
3301.3 | 1601.3 | 616.7 | 584.6 | 548.7 | 580.3
3302.3 | 1602.3 | 615 | 590.6 | 549.2 | 579.5
3303.3 | 1603.3 | 614.8 | 593.1 | 552.7 | 584.4
3304.3 | 1604.3 | 614.5 | 595.2 | 554.4 | 589.4
3305.3 | 1605.3 | 616 | 595.6 | 547.7 | 585.2
3306.3 | 1606.3 | 617.2 | 605 | 550.9 | 581.4
3307.3 | 1607.3 | 617 | 615.3 | 552.4 | 578.6
3308.3 | 1608.3 | 616.1 | 620.7 | 551.3 | 574.9
3309.3 | 1609.3 | 613.5 | 620.7 | 546.8 | 573.3
3310.3 | 1610.3 | 612.7 | 609.2 | 541.3 | 571.9
3311.3 | 1611.3 | 612.3 | 606.1 | 537.4 | 568.7
3312.3 | 1612.3 | 614.1 | 618.1 | 546.6 | 570.7
3313.3 | 1613.3 | 615.9 | 623.4 | 561.4 | 579.1
3314.3 | 1614.3 | 618.2 | 621.7 | 575.2 | 587.2
3315.3 | 1615.3 | 620.2 | 631.8 | 594.5 | 591.8
3316.3 | 1616.3 | 621.6 | 632.2 | 602.2 | 591.4
3317.3 | 1617.3 | 622.5 | 623.4 | 593.4 | 583.4
3318.3 | 1618.3 | 623.5 | 612.9 | 582.6 | 579.2
3319.3 | 1619.3 | 623.6 | 605.5 | 577.8 | 576.9
3320.3 | 1620.3 | 624.4 | 601.1 | 575.4 | 580
3321.3 | 1621.3 | 625.6 | 600.2 | 574.2 | 580.7
3322.3 | 1622.3 | 626.6 | 600.8 | 581.2 | 585.5
3323.3 | 1623.3 | 628.3 | 604.5 | 586.9 | 587.6
3324.3 | 1624.3 | 629.1 | 614.8 | 588.6 | 586.6
3325.3 | 1625.3 | 629.1 | 616 | 588.7 | 584.5
3326.3 | 1626.3 | 630 | 614.6 | 584 | 579.3
3327.3 | 1627.3 | 631.6 | 609.6 | 578 | 574
3328.3 | 1628.3 | 632.6 | 609.2 | 577.2 | 571.7
3329.3 | 1629.3 | 633.8 | 605.4 | 570.5 | 568.7
3330.3 | 1630.3 | 634.1 | 608.7 | 565.9 | 567.2
3331.3 | 1631.3 | 635.3 | 606.9 | 571.4 | 568
3332.3 | 1632.3 | 638.1 | 612.3 | 579.1 | 573.5
3333.3 | 1633.3 | 640.6 | 603 | 581.7 | 579
3334.3 | 1634.3 | 642.9 | 593.2 | 576.3 | 581.1
3335.3 | 1635.3 | 645.5 | 600 | 578.4 | 582.7
3336.3 | 1636.3 | 646.9 | 595.8 | 572.5 | 579.7
3337.3 | 1637.3 | 648.7 | 592.2 | 564.8 | 572.8
3338.3 | 1638.3 | 648.1 | 584.6 | 554 | 564.3
3339.3 | 1639.3 | 647.6 | 578.4 | 551.7 | 563.1
3340.3 | 1640.3 | 647.3 | 586.5 | 553.1 | 565.1
3341.3 | 1641.3 | 646.5 | 587.6 | 550.4 | 563.5
3342.3 | 1642.3 | 646.9 | 582.2 | 547 | 563.4
3343.3 | 1643.3 | 648 | 583.5 | 553.2 | 562.3
3344.3 | 1644.3 | 648.6 | 583.5 | 553.8 | 560.1
3345.3 | 1645.3 | 649 | 583.7 | 552 | 556.6
3346.3 | 1646.3 | 648.5 | 587.9 | 547.2 | 554.7
3347.3 | 1647.3 | 648.6 | 604.5 | 557.9 | 559.8
3348.3 | 1648.3 | 649.9 | 604.4 | 565.2 | 563.2
3349.3 | 1649.3 | 651.4 | 606.5 | 575 | 564.9
3350.3 | 1650.3 | 653.1 | 610.9 | 587 | 567.5
3351.3 | 1651.3 | 655.2 | 614.9 | 593.4 | 570.2
3352.3 | 1652.3 | 656.2 | 628.8 | 604.3 | 572.9
3353.3 | 1653.3 | 658.1 | 633.3 | 609.7 | 576.5
3354.3 | 1654.3 | 660.3 | 631.5 | 620.5 | 579.2
3355.3 | 1655.3 | 662.5 | 639.5 | 632.5 | 582.8
3356.3 | 1656.3 | 664.6 | 639.7 | 636 | 579.6
3357.3 | 1657.3 | 666.4 | 621.9 | 626.3 | 578.1
3358.3 | 1658.3 | 668.4 | 618.8 | 622.4 | 576.3
3359.3 | 1659.3 | 668.9 | 609.9 | 620.5 | 581
3360.3 | 1660.3 | 670 | 601.4 | 613.3 | 578.8
3361.3 | 1661.3 | 671.1 | 588.3 | 603.2 | 576
3362.3 | 1662.3 | 673.3 | 572 | 594.3 | 576.2
3363.3 | 1663.3 | 674.9 | 568.3 | 588.8 | 575.3
3364.3 | 1664.3 | 676.4 | 567.4 | 594.4 | 579.5
3365.3 | 1665.3 | 677.7 | 565.7 | 601.4 | 585.4
3366.3 | 1666.3 | 678.2 | 560.9 | 599.3 | 580.5
3367.3 | 1667.3 | 677.4 | 549 | 587.1 | 573.6
3368.3 | 1668.3 | 678.9 | 542 | 589.5 | 575.1
3369.3 | 1669.3 | 680.4 | 558.3 | 600.9 | 581.7
3370.3 | 1670.3 | 680.7 | 578.7 | 611.7 | 584.3
3371.3 | 1671.3 | 681.1 | 583.6 | 621.4 | 587.3
3372.3 | 1672.3 | 682.1 | 573.8 | 616.6 | 585.1
3373.3 | 1673.3 | 681.8 | 555.4 | 596.3 | 577.4
3374.3 | 1674.3 | 681.9 | 541 | 581.6 | 571.1
3375.3 | 1675.3 | 684.6 | 529 | 571.1 | 570
3376.3 | 1676.3 | 685.6 | 523.3 | 569.4 | 573.3
3377.3 | 1677.3 | 685.8 | 526.5 | 574.2 | 575.6
3378.3 | 1678.3 | 685.5 | 518.9 | 570.5 | 575.7
3379.3 | 1679.3 | 686 | 513.6 | 566.2 | 572.9
3380.3 | 1680.3 | 686.2 | 521.7 | 569.7 | 569.1
3381.3 | 1681.3 | 685.8 | 537.8 | 580.3 | 570.3
3382.3 | 1682.3 | 685.9 | 565.9 | 599.6 | 575.2
3383.3 | 1683.3 | 686.5 | 582.3 | 609.7 | 579.6
3384.3 | 1684.3 | 686.9 | 582.1 | 608.9 | 579.7
3385.3 | 1685.3 | 686.6 | 583.5 | 610.4 | 581
3386.3 | 1686.3 | 687.4 | 576.5 | 611.9 | 578.4
3387.3 | 1687.3 | 688.4 | 571.5 | 604.7 | 576.8
3388.3 | 1688.3 | 689.6 | 568.6 | 606.2 | 575.9
3389.3 | 1689.3 | 690.5 | 572.9 | 611 | 577
3390.3 | 1690.3 | 690.9 | 562.9 | 610.3 | 578.2
3391.3 | 1691.3 | 691.6 | 562.7 | 617.3 | 583.2
3392.3 | 1692.3 | 692.3 | 571.8 | 623.3 | 580.5
3393.3 | 1693.3 | 693 | 581.4 | 623.7 | 576.4
3394.3 | 1694.3 | 694 | 577.8 | 620 | 575.4
3395.3 | 1695.3 | 695.1 | 572.3 | 608.5 | 570.6
3396.3 | 1696.3 | 696.4 | 572.9 | 604 | 567.3
3397.3 | 1697.3 | 697.4 | 581 | 606.5 | 568.7
3398.3 | 1698.3 | 698 | 581.5 | 599 | 566.7
3399.3 | 1699.3 | 698.5 | 581 | 592.4 | 565.5
3400.3 | 1700.3 | 699.5 | 568.9 | 584.1 | 563.1
3401.3 | 1701.3 | 699.7 | 565.3 | 574.7 | 557.3
3402.3 | 1702.3 | 699.7 | 568.9 | 568 | 552.9
3403.3 | 1703.3 | 700.5 | 572.7 | 560 | 548.9
3404.3 | 1704.3 | 701.4 | 585.1 | 567.1 | 547.2
3405.3 | 1705.3 | 702.7 | 596.4 | 573.7 | 553.2
3406.3 | 1706.3 | 704.5 | 588.9 | 576.7 | 554.6
3407.3 | 1707.3 | 706.4 | 574.3 | 582.4 | 560.1
3408.3 | 1708.3 | 708.2 | 573.2 | 590.7 | 563.4
3409.3 | 1709.3 | 709.8 | 592.7 | 598.8 | 565.8
3410.3 | 1710.3 | 711.5 | 604.2 | 609.6 | 568.1
3411.3 | 1711.3 | 712.9 | 605 | 609.8 | 565.2
3412.3 | 1712.3 | 713.7 | 591 | 600.8 | 559.6
3413.3 | 1713.3 | 713.8 | 578.5 | 586.7 | 553.4
3414.3 | 1714.3 | 713.6 | 564.8 | 576.2 | 551.1
3415.3 | 1715.3 | 714.2 | 552 | 560.9 | 546.9
3416.3 | 1716.3 | 715 | 540.2 | 548.2 | 542.3
3417.3 | 1717.3 | 715.1 | 534.5 | 549.7 | 548.4
3418.3 | 1718.3 | 715.7 | 539.7 | 562.7 | 557.4
3419.3 | 1719.3 | 717.6 | 547.1 | 566.1 | 556.6
3420.3 | 1720.3 | 718.3 | 539.7 | 567.7 | 557.2
3421.3 | 1721.3 | 719.6 | 537.7 | 566 | 554.5
3422.3 | 1722.3 | 721.2 | 532.2 | 566.5 | 554.7
3423.3 | 1723.3 | 722.1 | 532.8 | 567.6 | 554.5
3424.3 | 1724.3 | 722.6 | 540 | 570 | 556.4
3425.3 | 1725.3 | 723.4 | 528 | 568.5 | 558.4
3426.3 | 1726.3 | 723.2 | 521.4 | 561.1 | 554.9
3427.3 | 1727.3 | 722.1 | 526.3 | 555.7 | 549.5
3428.3 | 1728.3 | 722.5 | 532.6 | 563.3 | 550.7
3429.3 | 1729.3 | 724 | 528.2 | 565 | 554
3430.3 | 1730.3 | 725.4 | 520.3 | 557.7 | 556.3
3431.3 | 1731.3 | 726.7 | 528.6 | 560.8 | 556
3432.3 | 1732.3 | 727.4 | 550.2 | 572.4 | 558
3433.3 | 1733.3 | 727.7 | 552.6 | 575.8 | 558.5
3434.3 | 1734.3 | 728.8 | 550.7 | 585.7 | 560.8
3435.3 | 1735.3 | 730.1 | 539.6 | 585.2 | 562.2
3436.3 | 1736.3 | 732 | 536.5 | 584.7 | 563
3437.3 | 1737.3 | 732.2 | 543.1 | 586.9 | 560.7
3438.3 | 1738.3 | 733.2 | 549.4 | 597.4 | 563
3439.3 | 1739.3 | 734.7 | 553.2 | 604.9 | 568.4
3440.3 | 1740.3 | 736 | 561.4 | 605.1 | 574.5
3441.3 | 1741.3 | 737.3 | 557.9 | 606 | 577.5
3442.3 | 1742.3 | 739.3 | 565.1 | 629.7 | 588.7
3443.3 | 1743.3 | 740.2 | 568.8 | 643.5 | 599.4
3444.3 | 1744.3 | 741.8 | 561.1 | 648 | 602.2
3445.3 | 1745.3 | 743.8 | 576 | 662 | 610.2
3446.3 | 1746.3 | 745 | 600.6 | 666.2 | 607.1
3447.3 | 1747.3 | 746.4 | 612.3 | 667.5 | 604
3448.3 | 1748.3 | 748.3 | 604.1 | 664.7 | 606.9
3449.3 | 1749.3 | 750.3 | 583.2 | 656.5 | 610.7
3450.3 | 1750.3 | 752.2 | 562.6 | 649.4 | 612.6
3451.3 | 1751.3 | 753.7 | 557.4 | 658.6 | 620.1
3452.3 | 1752.3 | 755.7 | 570 | 679.3 | 629.2
3453.3 | 1753.3 | 756.7 | 571.7 | 681.8 | 632.3
3454.3 | 1754.3 | 757.6 | 566.7 | 681.4 | 631.6
3455.3 | 1755.3 | 758.6 | 557.5 | 679.1 | 636
3456.3 | 1756.3 | 759.2 | 559.1 | 681.2 | 642.5
3457.3 | 1757.3 | 759.1 | 572.4 | 677.5 | 636.7
3458.3 | 1758.3 | 758.8 | 564.8 | 655.1 | 624.9
3459.3 | 1759.3 | 760.3 | 563.1 | 650.4 | 620.6
3460.3 | 1760.3 | 761.8 | 575.1 | 650.4 | 617.9
3461.3 | 1761.3 | 762.6 | 595.9 | 652.7 | 618.5
3462.3 | 1762.3 | 763.2 | 613.7 | 657.1 | 619.8
3463.3 | 1763.3 | 764.4 | 616.8 | 650 | 615.9
3464.3 | 1764.3 | 765.9 | 620.8 | 651.9 | 615.8
3465.3 | 1765.3 | 767.3 | 653.1 | 670.7 | 620.4
3466.3 | 1766.3 | 768.1 | 672.9 | 686 | 626
3467.3 | 1767.3 | 769.2 | 663.9 | 682.1 | 625.2
3468.3 | 1768.3 | 771.5 | 649.7 | 680.2 | 627.3
3469.3 | 1769.3 | 774.6 | 646.7 | 684.7 | 632.1
3470.3 | 1770.3 | 775.4 | 654.2 | 688.1 | 630.5
3471.3 | 1771.3 | 775.3 | 665.8 | 698.2 | 633.8
3472.3 | 1772.3 | 775 | 679.8 | 699.7 | 631.8
3473.3 | 1773.3 | 775 | 672.2 | 693.6 | 629.9
3474.3 | 1774.3 | 775.9 | 675.8 | 686.2 | 624.2
3475.3 | 1775.3 | 777.3 | 670.9 | 679.9 | 618.3
3476.3 | 1776.3 | 778.1 | 656.5 | 664.6 | 614
3477.3 | 1777.3 | 779.6 | 648.3 | 655.1 | 611.3
3478.3 | 1778.3 | 781.6 | 631.6 | 647.3 | 613.6
3479.3 | 1779.3 | 783.4 | 621.7 | 653.6 | 618
3480.3 | 1780.3 | 785.1 | 613.9 | 651.4 | 621
3481.3 | 1781.3 | 785.6 | 629.2 | 669.7 | 629.8
3482.3 | 1782.3 | 785 | 654 | 701.5 | 640.6
3483.3 | 1783.3 | 785.2 | 659.8 | 718.1 | 644.4
3484.3 | 1784.3 | 785.9 | 675.1 | 723.9 | 644.5
3485.3 | 1785.3 | 787.2 | 685.8 | 729.2 | 643.1
3486.3 | 1786.3 | 788.3 | 685.1 | 723.7 | 643.8
3487.3 | 1787.3 | 789.7 | 681.2 | 705.9 | 642.2
3488.3 | 1788.3 | 790.8 | 677.2 | 698.6 | 637.5
3489.3 | 1789.3 | 791.8 | 679.7 | 690.6 | 635.3
3490.3 | 1790.3 | 792.7 | 674.2 | 695.8 | 636.7
3491.3 | 1791.3 | 795.1 | 678.1 | 692.5 | 632.2
3492.3 | 1792.3 | 797.5 | 661.9 | 679.9 | 632.5
3493.3 | 1793.3 | 797.4 | 644.4 | 672.3 | 629
3494.3 | 1794.3 | 797.5 | 644.9 | 671.9 | 629.1
3495.3 | 1795.3 | 797.8 | 665.9 | 689.6 | 631.2
3496.3 | 1796.3 | 798.5 | 682.1 | 705.3 | 639.5
3497.3 | 1797.3 | 798.6 | 677.8 | 702.9 | 645
3498.3 | 1798.3 | 798.8 | 665.9 | 686.4 | 641.7
3499.3 | 1799.3 | 798.4 | 650.6 | 680.4 | 636.1
3500.3 | 1800.3 | 797.8 | 642.4 | 679.6 | 634.7
3501.3 | 1801.3 | 797.1 | 641.1 | 667.2 | 631.4
3502.3 | 1802.3 | 796.4 | 630.1 | 652 | 628.1
3503.3 | 1803.3 | 794.8 | 610.8 | 635.3 | 624.3
3504.3 | 1804.3 | 793.3 | 594.6 | 628.8 | 629.6
3505.3 | 1805.3 | 793.3 | 597.3 | 621.5 | 631.4
3506.3 | 1806.3 | 792.7 | 591.3 | 598.1 | 623.1
3507.3 | 1807.3 | 792.3 | 581.9 | 589.1 | 618.4
3508.3 | 1808.3 | 791.8 | 569.6 | 578.7 | 615.7
3509.3 | 1809.3 | 790.5 | 575.2 | 583 | 616.1
3510.3 | 1810.3 | 788.5 | 567.9 | 572.9 | 612
3511.3 | 1811.3 | 786.5 | 555 | 559.6 | 606.3
3512.3 | 1812.3 | 786.4 | 543.9 | 561.5 | 608
3513.3 | 1813.3 | 787.8 | 529.9 | 565.9 | 613.8
3514.3 | 1814.3 | 789.3 | 529.2 | 582.6 | 620.9
3515.3 | 1815.3 | 790.4 | 538.3 | 593.6 | 629
3516.3 | 1816.3 | 791.1 | 553.1 | 613.8 | 627.2
3517.3 | 1817.3 | 791.2 | 553.8 | 613.8 | 624.3
3518.3 | 1818.3 | 790.7 | 565.6 | 618.7 | 623.4
3519.3 | 1819.3 | 790.7 | 574.7 | 625.5 | 627.2
3520.3 | 1820.3 | 789.4 | 574.9 | 609.3 | 621.1
3521.3 | 1821.3 | 788.5 | 562.4 | 585.2 | 611.3
3522.3 | 1822.3 | 788.2 | 557.5 | 582 | 609.4
3523.3 | 1823.3 | 787.9 | 554 | 579.9 | 609.9
3524.3 | 1824.3 | 789.5 | 555.7 | 585.1 | 613.8
3525.3 | 1825.3 | 791.1 | 546.6 | 582.4 | 614.1
3526.3 | 1826.3 | 791.6 | 541.7 | 574.2 | 608.3
3527.3 | 1827.3 | 791.4 | 548.3 | 588 | 605.4
3528.3 | 1828.3 | 791.5 | 560.5 | 595.7 | 606.4
3529.3 | 1829.3 | 791.7 | 568.8 | 597 | 607
3530.3 | 1830.3 | 790.9 | 566.7 | 588.8 | 601.6
3531.3 | 1831.3 | 791.7 | 558.9 | 580.4 | 598.2
3532.3 | 1832.3 | 791.5 | 558.1 | 586.7 | 599.2
3533.3 | 1833.3 | 793.1 | 587.3 | 608.5 | 605.8
3534.3 | 1834.3 | 794.2 | 587.4 | 618 | 609.9
3535.3 | 1835.3 | 796 | 589 | 625.1 | 610.9
3536.3 | 1836.3 | 796.5 | 582.4 | 614.3 | 613
3537.3 | 1837.3 | 794.9 | 573.5 | 601.2 | 608.5
3538.3 | 1838.3 | 794.6 | 563.5 | 590.8 | 600.7
3539.3 | 1839.3 | 794 | 564.9 | 584.8 | 597.3
3540.3 | 1840.3 | 793.9 | 561.8 | 578.9 | 597.1
3541.3 | 1841.3 | 794.1 | 551.7 | 577.5 | 597.7
3542.3 | 1842.3 | 794.8 | 557.9 | 584.7 | 598
3543.3 | 1843.3 | 796.3 | 570.3 | 593.8 | 598.1
3544.3 | 1844.3 | 796.5 | 572.5 | 588 | 596.3
3545.3 | 1845.3 | 796.3 | 575.9 | 593.1 | 595.8
3546.3 | 1846.3 | 797.2 | 588.9 | 593.1 | 594
3547.3 | 1847.3 | 797.8 | 597.6 | 579.2 | 589.5
3548.3 | 1848.3 | 798.6 | 604.5 | 581 | 586.9
3549.3 | 1849.3 | 799.9 | 596.2 | 574.9 | 586.3
3550.3 | 1850.3 | 801 | 586.9 | 561.7 | 581.6
3551.3 | 1851.3 | 800.6 | 586.3 | 557.6 | 578.1
3552.3 | 1852.3 | 800.1 | 596.6 | 562.8 | 582.5
3553.3 | 1853.3 | 800.2 | 599.8 | 566 | 587.5
3554.3 | 1854.3 | 800.2 | 604.9 | 577.7 | 594.8
3555.3 | 1855.3 | 799.7 | 609.3 | 577.5 | 591.8
3556.3 | 1856.3 | 798.6 | 616.5 | 577.8 | 587.5
3557.3 | 1857.3 | 798.9 | 623.1 | 580.3 | 585
3558.3 | 1858.3 | 799.3 | 617.9 | 570.4 | 579.8
3559.3 | 1859.3 | 799.1 | 604 | 550.9 | 572.9
3560.3 | 1860.3 | 797.5 | 589.7 | 536.5 | 567.4
3561.3 | 1861.3 | 796.2 | 580.1 | 539.3 | 567.5
3562.3 | 1862.3 | 795.6 | 588.8 | 549 | 567.8
3563.3 | 1863.3 | 796.7 | 601.7 | 551.6 | 565
3564.3 | 1864.3 | 797.6 | 592.5 | 549.5 | 562.4
3565.3 | 1865.3 | 797.9 | 581.6 | 546.2 | 565.2
3566.3 | 1866.3 | 800.8 | 582.5 | 564.5 | 576.8
3567.3 | 1867.3 | 801.4 | 584.7 | 584.3 | 590.3
3568.3 | 1868.3 | 800.4 | 569.7 | 578.1 | 590.2
3569.3 | 1869.3 | 798.7 | 549.5 | 561.4 | 582.5
3570.3 | 1870.3 | 798.8 | 530.4 | 548.5 | 575.8
3571.3 | 1871.3 | 800.4 | 520.6 | 557 | 580.6
3572.3 | 1872.3 | 802.2 | 521.3 | 559.2 | 589.3
3573.3 | 1873.3 | 801.9 | 520.7 | 561.8 | 588.8
3574.3 | 1874.3 | 801.3 | 521.5 | 570.9 | 586.7
3575.3 | 1875.3 | 802.9 | 521.6 | 567.7 | 585.2
3576.3 | 1876.3 | 802.4 | 525.7 | 566.7 | 581.9
3577.3 | 1877.3 | 800.9 | 517.1 | 556 | 575.7
3578.3 | 1878.3 | 799.7 | 515.5 | 560.6 | 577.3
3579.3 | 1879.3 | 796.8 | 507.1 | 547.5 | 574
3580.3 | 1880.3 | 793.9 | 501.9 | 540.2 | 568.5
3581.3 | 1881.3 | 793.2 | 509 | 553.4 | 572.3
3582.3 | 1882.3 | 792.3 | 519 | 547.9 | 569.2
3583.3 | 1883.3 | 792 | 521.4 | 549.7 | 567
3584.3 | 1884.3 | 792.4 | 532.2 | 551.1 | 568.5
3585.3 | 1885.3 | 791.7 | 556.9 | 572.4 | 570.7
3586.3 | 1886.3 | 790.3 | 580.8 | 578.9 | 572.8
3587.3 | 1887.3 | 789.4 | 598 | 592.9 | 579.1
3588.3 | 1888.3 | 788.7 | 617.1 | 609.9 | 581.8
3589.3 | 1889.3 | 791.3 | 615.9 | 599.9 | 576.6
3590.3 | 1890.3 | 792.4 | 622 | 593.8 | 571.4
3591.3 | 1891.3 | 793.6 | 617.9 | 608.1 | 575.8
3592.3 | 1892.3 | 792.7 | 632.2 | 627.4 | 582.9
3593.3 | 1893.3 | 792.5 | 653.8 | 640 | 584.5
3594.3 | 1894.3 | 793.2 | 642.1 | 637.1 | 586.4
3595.3 | 1895.3 | 795 | 631.8 | 643.3 | 589.6
3596.3 | 1896.3 | 796.7 | 624.8 | 646.8 | 592.5
3597.3 | 1897.3 | 796.6 | 633.6 | 666.9 | 600.9
3598.3 | 1898.3 | 795.5 | 660.3 | 698.3 | 620.1
3599.3 | 1899.3 | 795.3 | 684.1 | 710.3 | 625.1
3600.3 | 1900.3 | 795 | 706.6 | 725.2 | 626.6
3601.3 | 1901.3 | 794.7 | 732 | 730.5 | 624.6
3602.3 | 1902.3 | 797.3 | 741.9 | 732.4 | 619.2
3603.3 | 1903.3 | 800.8 | 735.9 | 728.7 | 615.6
3604.3 | 1904.3 | 804.3 | 724.8 | 734.7 | 623.5
3605.3 | 1905.3 | 806.5 | 720.9 | 737.6 | 626.3
3606.3 | 1906.3 | 808.8 | 719.8 | 744.4 | 631.6
3607.3 | 1907.3 | 808.7 | 738.6 | 762.2 | 638.2
3608.3 | 1908.3 | 808.7 | 733.1 | 761.8 | 644.4
3609.3 | 1909.3 | 809.1 | 724.7 | 764.5 | 642.7
3610.3 | 1910.3 | 810.8 | 706.4 | 752.2 | 639.7
3611.3 | 1911.3 | 813.4 | 697.1 | 739.4 | 638.2
3612.3 | 1912.3 | 814.5 | 691.6 | 731.7 | 636.1
3613.3 | 1913.3 | 814.8 | 686.8 | 733.1 | 633.2
3614.3 | 1914.3 | 814.6 | 680.5 | 711.2 | 628.6
3615.3 | 1915.3 | 813.9 | 671.1 | 701.8 | 622.9
3616.3 | 1916.3 | 814.3 | 669 | 694.4 | 625.6
3617.3 | 1917.3 | 816.6 | 658.2 | 681.5 | 622.9
3618.3 | 1918.3 | 819.1 | 648.9 | 665.9 | 623
3619.3 | 1919.3 | 818.3 | 650.9 | 666.3 | 624.3
3620.3 | 1920.3 | 816.1 | 653 | 670.5 | 626.3
3621.3 | 1921.3 | 814.8 | 644.6 | 672.9 | 627.2
3622.3 | 1922.3 | 813.6 | 647 | 678.1 | 630.3
3623.3 | 1923.3 | 812.4 | 650.3 | 667.9 | 628.1
3624.3 | 1924.3 | 811 | 644.4 | 659.1 | 622.3
3625.3 | 1925.3 | 809.6 | 646.5 | 649.2 | 618.9
3626.3 | 1926.3 | 808.3 | 651.3 | 659.7 | 621
3627.3 | 1927.3 | 807.7 | 669.8 | 663.7 | 617.1
3628.3 | 1928.3 | 807.9 | 679.7 | 661.5 | 614.7
3629.3 | 1929.3 | 807.9 | 687.5 | 652.8 | 613.6
3630.3 | 1930.3 | 809.4 | 686.3 | 651 | 612.6
3631.3 | 1931.3 | 811 | 686.2 | 652.5 | 610.3
3632.3 | 1932.3 | 811.4 | 685.3 | 656.3 | 609.4
3633.3 | 1933.3 | 811.3 | 681.5 | 662.6 | 613.8
3634.3 | 1934.3 | 811.5 | 692.7 | 673.6 | 619.1
3635.3 | 1935.3 | 813.1 | 692.6 | 686.2 | 625.5
3636.3 | 1936.3 | 814.5 | 699.6 | 690.4 | 633.6
3637.3 | 1937.3 | 815.4 | 695.4 | 698.4 | 641.9
3638.3 | 1938.3 | 816.3 | 684.5 | 694 | 640.5
3639.3 | 1939.3 | 816.8 | 671.3 | 681.2 | 631.8
3640.3 | 1940.3 | 815.9 | 676.2 | 680.4 | 620.9
3641.3 | 1941.3 | 815.7 | 676.2 | 671.5 | 616.7
3642.3 | 1942.3 | 815.3 | 677 | 669.1 | 615.6
3643.3 | 1943.3 | 814.3 | 695.4 | 686.9 | 613.8
3644.3 | 1944.3 | 813.9 | 689.6 | 683.5 | 611
3645.3 | 1945.3 | 813.9 | 692.3 | 695.1 | 618.1
3646.3 | 1946.3 | 815 | 675.2 | 699.7 | 636.7
3647.3 | 1947.3 | 815.7 | 659.1 | 699 | 641.5
3648.3 | 1948.3 | 814.9 | 640.6 | 684.3 | 638.2
3649.3 | 1949.3 | 814.6 | 629.1 | 707.3 | 651.3
3650.3 | 1950.3 | 813.3 | 622.6 | 724.3 | 669.3
3651.3 | 1951.3 | 815 | 604.1 | 724.9 | 672.3
3652.3 | 1952.3 | 816.5 | 588 | 721.2 | 671.3
3653.3 | 1953.3 | 816.6 | 576.3 | 727.8 | 677.5
3654.3 | 1954.3 | 815.4 | 577.2 | 730.7 | 686.6
3655.3 | 1955.3 | 814 | 575.7 | 720.1 | 686.5
3656.3 | 1956.3 | 814.8 | 556.5 | 707 | 683.7
3657.3 | 1957.3 | 815.1 | 538.5 | 686.4 | 680
3658.3 | 1958.3 | 814.4 | 528.4 | 674.5 | 680.8
3659.3 | 1959.3 | 813.6 | 520.7 | 670.3 | 680.6
3660.3 | 1960.3 | 811.1 | 516.7 | 666.6 | 682.3
3661.3 | 1961.3 | 810.7 | 509.6 | 660.7 | 681.9
3662.3 | 1962.3 | 808.5 | 500.6 | 669.4 | 682.2
3663.3 | 1963.3 | 806.6 | 486.2 | 649.4 | 674
3664.3 | 1964.3 | 805.1 | 472.9 | 641.2 | 666.4
3665.3 | 1965.3 | 803.9 | 466.1 | 657.6 | 675.6
3666.3 | 1966.3 | 800.9 | 472.6 | 677.6 | 688.9
3667.3 | 1967.3 | 798.3 | 507.5 | 716.8 | 700.6
3668.3 | 1968.3 | 796.2 | 546.5 | 736 | 698.3
3669.3 | 1969.3 | 796 | 564.3 | 744 | 695.3
3670.3 | 1970.3 | 796.9 | 552.5 | 738.3 | 692.4
3671.3 | 1971.3 | 797 | 534.1 | 723.9 | 692.7
3672.3 | 1972.3 | 797.5 | 520.5 | 719.1 | 701.6
3673.3 | 1973.3 | 796.2 | 527.6 | 711.5 | 697.1
3674.3 | 1974.3 | 794.3 | 545.9 | 708.9 | 689.8
3675.3 | 1975.3 | 792.6 | 564.8 | 706.5 | 676.4
3676.3 | 1976.3 | 791.6 | 576.4 | 683.7 | 661.7
3677.3 | 1977.3 | 791.2 | 583.9 | 670.1 | 652.6
3678.3 | 1978.3 | 791.5 | 573.1 | 667.6 | 654.4
3679.3 | 1979.3 | 790.3 | 576.6 | 678.2 | 661.4
3680.3 | 1980.3 | 789.8 | 590 | 711 | 685
3681.3 | 1981.3 | 790.5 | 586.9 | 707.1 | 692.3
3682.3 | 1982.3 | 790 | 573.6 | 685.5 | 688.8
3683.3 | 1983.3 | 788.6 | 574.1 | 690.9 | 684.5
3684.3 | 1984.3 | 787.4 | 587 | 682.6 | 683.2
3685.3 | 1985.3 | 786.7 | 583.4 | 663.7 | 670
3686.3 | 1986.3 | 784.9 | 561.9 | 642.1 | 662.8
3687.3 | 1987.3 | 782 | 543 | 629.4 | 659
3688.3 | 1988.3 | 779.7 | 527.9 | 621 | 653.8
3689.3 | 1989.3 | 776.9 | 511 | 595.8 | 645.6
3690.3 | 1990.3 | 774.1 | 499.6 | 577.6 | 643.5
3691.3 | 1991.3 | 771.3 | 489.2 | 569.1 | 644.9
3692.3 | 1992.3 | 769 | 488.4 | 591 | 649.3
3693.3 | 1993.3 | 767.1 | 495.2 | 615.8 | 654.3
3694.3 | 1994.3 | 765.8 | 499.6 | 645.3 | 665.2
3695.3 | 1995.3 | 765.5 | 493.4 | 639.5 | 671.7
3696.3 | 1996.3 | 764.3 | 480.3 | 620.1 | 661.9
3697.3 | 1997.3 | 763.1 | 469.2 | 606.6 | 657.5
3698.3 | 1998.3 | 761.4 | 471.3 | 612.2 | 661.9
3699.3 | 1999.3 | 759.6 | 462.6 | 604.5 | 664.2
3700.3 | 2000.3 | 756.9 | 450.8 | 598.2 | 661.2
3701.3 | 2001.3 | 754.3 | 445.1 | 599.8 | 660.8
3702.3 | 2002.3 | 753 | 443.6 | 605.3 | 670.1
3703.3 | 2003.3 | 752.2 | 444.8 | 631.2 | 685.1
3704.3 | 2004.3 | 751.7 | 442.1 | 623.6 | 679.6
3705.3 | 2005.3 | 750.9 | 443.5 | 622.4 | 673.6
3706.3 | 2006.3 | 750.2 | 447.2 | 632.5 | 673.7
3707.3 | 2007.3 | 750 | 466.7 | 656.8 | 676.9
3708.3 | 2008.3 | 749.1 | 496.2 | 650.3 | 667.3
3709.3 | 2009.3 | 747.9 | 503.5 | 639.1 | 657.6
3710.3 | 2010.3 | 747.2 | 501 | 638.1 | 652.9
3711.3 | 2011.3 | 746.5 | 516.8 | 637.3 | 658.1
3712.3 | 2012.3 | 745.8 | 529.4 | 649.6 | 654.7
3713.3 | 2013.3 | 746 | 570.1 | 676.8 | 659.9
3714.3 | 2014.3 | 747.3 | 606.1 | 696 | 669
3715.3 | 2015.3 | 749.1 | 629.4 | 715 | 678.3
3716.3 | 2016.3 | 750.7 | 645 | 731.4 | 684.1
3717.3 | 2017.3 | 752.1 | 671.3 | 744.5 | 691.5
3718.3 | 2018.3 | 753.9 | 672.6 | 746.8 | 692.2
3719.3 | 2019.3 | 755.8 | 655.7 | 747.8 | 700.8
3720.3 | 2020.3 | 757.9 | 635.2 | 742.2 | 709.4
3721.3 | 2021.3 | 758.7 | 628.1 | 744.2 | 707
3722.3 | 2022.3 | 759.4 | 616.7 | 745.7 | 702.8
3723.3 | 2023.3 | 759.8 | 628.8 | 742.2 | 694.4
3724.3 | 2024.3 | 760.4 | 624.5 | 746.6 | 694.7
3725.3 | 2025.3 | 760.9 | 606.3 | 735.8 | 692.9
3726.3 | 2026.3 | 760.9 | 593.7 | 730.4 | 692.7
3727.3 | 2027.3 | 760.3 | 596 | 733.6 | 694.4
3728.3 | 2028.3 | 759.8 | 618.2 | 738.2 | 693.5
3729.3 | 2029.3 | 759.8 | 626.4 | 752.3 | 694.9
3730.3 | 2030.3 | 760.3 | 625.1 | 773.2 | 706.1
3731.3 | 2031.3 | 761.7 | 622.8 | 786 | 718.8
3732.3 | 2032.3 | 763.1 | 637.2 | 799 | 725.3
3733.3 | 2033.3 | 764.5 | 670.9 | 805.5 | 720.9
3734.3 | 2034.3 | 766.8 | 689.4 | 801.4 | 710.3
3735.3 | 2035.3 | 769 | 701.9 | 782.7 | 694.9
3736.3 | 2036.3 | 770.2 | 725.3 | 784.3 | 690.3
3737.3 | 2037.3 | 772 | 712.6 | 777.4 | 690.1
3738.3 | 2038.3 | 773.4 | 701.3 | 772.9 | 697.3
3739.3 | 2039.3 | 774.4 | 686.1 | 763.5 | 707.5
3740.3 | 2040.3 | 774.9 | 668.3 | 756.6 | 714
3741.3 | 2041.3 | 774.5 | 655.9 | 737.4 | 702.4
3742.3 | 2042.3 | 773.6 | 635.1 | 718.8 | 692
3743.3 | 2043.3 | 772.5 | 616.3 | 696.9 | 686.4
3744.3 | 2044.3 | 770.9 | 597.7 | 679.2 | 679.5
3745.3 | 2045.3 | 769 | 594.1 | 678.3 | 681.7
3746.3 | 2046.3 | 767.9 | 586.5 | 678.2 | 693.5
3747.3 | 2047.3 | 766.7 | 587.4 | 698.3 | 705.9
3748.3 | 2048.3 | 766.1 | 580.5 | 704.5 | 713.5
3749.3 | 2049.3 | 765.5 | 571.6 | 709.2 | 718.8
3750.3 | 2050.3 | 764.7 | 559.3 | 701.9 | 719.2
3751.3 | 2051.3 | 763.8 | 547.1 | 693.5 | 719
3752.3 | 2052.3 | 762.9 | 542.8 | 702.4 | 720
3753.3 | 2053.3 | 761.9 | 543.4 | 685.5 | 711.9
3754.3 | 2054.3 | 761.1 | 543 | 694.2 | 703
3755.3 | 2055.3 | 760.5 | 546.7 | 710.8 | 715.8
3756.3 | 2056.3 | 760 | 554.4 | 723.3 | 721.7
3757.3 | 2057.3 | 759.5 | 561.5 | 745.2 | 735.6
3758.3 | 2058.3 | 760.1 | 588.1 | 762.7 | 735.9
3759.3 | 2059.3 | 761.3 | 617.2 | 757.1 | 722.7
3760.3 | 2060.3 | 762.1 | 640.9 | 745.2 | 710
3761.3 | 2061.3 | 763.5 | 664.7 | 763.5 | 714.9
3762.3 | 2062.3 | 765.5 | 682.9 | 781.3 | 719
3763.3 | 2063.3 | 766.9 | 676.6 | 794.2 | 727
3764.3 | 2064.3 | 767.5 | 653.3 | 788.4 | 731.4
3765.3 | 2065.3 | 768.4 | 653.9 | 796.5 | 734.2
3766.3 | 2066.3 | 769.5 | 653.5 | 803.3 | 737.6
3767.3 | 2067.3 | 769.9 | 635.7 | 801.9 | 747.9
3768.3 | 2068.3 | 769.9 | 623.1 | 792.8 | 743.4
3769.3 | 2069.3 | 770.4 | 639.5 | 803.3 | 748.3
3770.3 | 2070.3 | 771.5 | 641.8 | 806.3 | 752.8
3771.3 | 2071.3 | 772.4 | 638.2 | 809.2 | 754.4
3772.3 | 2072.3 | 772.3 | 620.2 | 795 | 749.9
3773.3 | 2073.3 | 772.1 | 621.3 | 795.8 | 752.6
3774.3 | 2074.3 | 772.4 | 631.9 | 801.6 | 751.1
3775.3 | 2075.3 | 773.1 | 640.5 | 801.5 | 747.9
3776.3 | 2076.3 | 773.3 | 651 | 803.8 | 740.5
3777.3 | 2077.3 | 773.5 | 676.4 | 801.9 | 730.5
3778.3 | 2078.3 | 774 | 706.8 | 807.7 | 726.3
3779.3 | 2079.3 | 775 | 706.5 | 818.7 | 739.3
3780.3 | 2080.3 | 776.1 | 706.7 | 819.8 | 744.4
3781.3 | 2081.3 | 776.7 | 718 | 804.6 | 730.8
3782.3 | 2082.3 | 777.3 | 724.5 | 793.1 | 729.2
3783.3 | 2083.3 | 777.5 | 722.9 | 782.1 | 724.1
3784.3 | 2084.3 | 777.4 | 705.9 | 771.9 | 723.2
3785.3 | 2085.3 | 776.4 | 681 | 755.8 | 717.5
3786.3 | 2086.3 | 774.7 | 657.2 | 729 | 710.9
3787.3 | 2087.3 | 774 | 657.1 | 756.1 | 715.9
3788.3 | 2088.3 | 773.7 | 643.4 | 737.6 | 708.7
3789.3 | 2089.3 | 772.2 | 622.9 | 720.5 | 704.1
3790.3 | 2090.3 | 769.9 | 602 | 708.9 | 706.5
3791.3 | 2091.3 | 767.8 | 592.6 | 707.5 | 718.9
3792.3 | 2092.3 | 766.2 | 584.1 | 693.8 | 719
3793.3 | 2093.3 | 764.4 | 573.5 | 693.1 | 718.2
3794.3 | 2094.3 | 762.2 | 563.9 | 677.7 | 719.3
3795.3 | 2095.3 | 759.9 | 564.7 | 696 | 722.9
3796.3 | 2096.3 | 758.4 | 560.2 | 711.4 | 730.6
3797.3 | 2097.3 | 757.7 | 564.2 | 710.1 | 729.8
3798.3 | 2098.3 | 757.4 | 570 | 716.3 | 729.7
3799.3 | 2099.3 | 757 | 575.6 | 710.5 | 725.3
3800.3 | 2100.3 | 756.1 | 580 | 706.9 | 721
3801.3 | 2101.3 | 755.4 | 577.9 | 708.4 | 722
3802.3 | 2102.3 | 755.3 | 592 | 729.5 | 725.6
3803.3 | 2103.3 | 755.9 | 606.9 | 748.1 | 736.9
3804.3 | 2104.3 | 756.5 | 617.3 | 741 | 732.6
3805.3 | 2105.3 | 757.1 | 629.8 | 741.8 | 726.5
3806.3 | 2106.3 | 757.6 | 629.5 | 749.3 | 730.8
3807.3 | 2107.3 | 758.5 | 635.3 | 757.1 | 741.4
3808.3 | 2108.3 | 759.6 | 628 | 762 | 745.7
3809.3 | 2109.3 | 759.6 | 615.7 | 755.3 | 744.2
3810.3 | 2110.3 | 759.8 | 616.9 | 759.7 | 744.5
3811.3 | 2111.3 | 760.6 | 631.2 | 772.3 | 745.9
3812.3 | 2112.3 | 761.8 | 629.1 | 782.3 | 754.7
3813.3 | 2113.3 | 761.5 | 609.9 | 763.3 | 755
3814.3 | 2114.3 | 759.8 | 585.6 | 739 | 748.8
3815.3 | 2115.3 | 758.6 | 585.3 | 751.5 | 753.8
3816.3 | 2116.3 | 759.5 | 612.2 | 779.9 | 756.1
3817.3 | 2117.3 | 761.4 | 651.2 | 797.1 | 751.1
3818.3 | 2118.3 | 763.5 | 668.2 | 805 | 759.8
3819.3 | 2119.3 | 765 | 674.4 | 801.3 | 766.2
3820.3 | 2120.3 | 765.3 | 676.2 | 784.1 | 761.7
3821.3 | 2121.3 | 765.7 | 699.1 | 774.4 | 745
3822.3 | 2122.3 | 766.2 | 725.9 | 770.7 | 735.9
3823.3 | 2123.3 | 767.9 | 754.8 | 789 | 737.4
3824.3 | 2124.3 | 770.4 | 776.2 | 808.3 | 748.3
3825.3 | 2125.3 | 772.6 | 780.3 | 818.2 | 752.9
3826.3 | 2126.3 | 774.7 | 779.8 | 825.1 | 757.3
3827.3 | 2127.3 | 775.9 | 750.8 | 807.2 | 761.8
3828.3 | 2128.3 | 775.8 | 735.1 | 798.1 | 758
3829.3 | 2129.3 | 776.6 | 742.6 | 798.1 | 751.7
3830.3 | 2130.3 | 777.1 | 743.5 | 793 | 744.8
3831.3 | 2131.3 | 777.2 | 730.7 | 791.6 | 743.6
3832.3 | 2132.3 | 776.6 | 718.6 | 781 | 737.7
3833.3 | 2133.3 | 776.1 | 721.5 | 786.3 | 738.5
3834.3 | 2134.3 | 775.8 | 740.2 | 774.1 | 730.8
3835.3 | 2135.3 | 775.9 | 759.6 | 762.3 | 718.1
3836.3 | 2136.3 | 775.7 | 766.7 | 750 | 711.4
3837.3 | 2137.3 | 776.6 | 776.4 | 756.8 | 711.6
3838.3 | 2138.3 | 777.4 | 786.9 | 762.3 | 709.3
3839.3 | 2139.3 | 778.8 | 780.6 | 780.9 | 720.7
3840.3 | 2140.3 | 779.6 | 756.9 | 781.8 | 734.5
3841.3 | 2141.3 | 778.6 | 723 | 779.4 | 742.7
3842.3 | 2142.3 | 776.8 | 695.5 | 764 | 745.1
3843.3 | 2143.3 | 775.5 | 673.6 | 770.9 | 756.7
3844.3 | 2144.3 | 774.9 | 650.7 | 773.3 | 766.5
3845.3 | 2145.3 | 774.1 | 634 | 778.3 | 763.2
3846.3 | 2146.3 | 774.3 | 637 | 783.9 | 757.8
3847.3 | 2147.3 | 775 | 665 | 789.7 | 742.8
3848.3 | 2148.3 | 776.6 | 685.2 | 812.8 | 747.2
3849.3 | 2149.3 | 778.6 | 695.1 | 822.8 | 754.6
3850.3 | 2150.3 | 779.5 | 693.6 | 815.7 | 744
3851.3 | 2151.3 | 780.9 | 697.8 | 812.9 | 743
3852.3 | 2152.3 | 781.5 | 685.1 | 806.2 | 752.9
3853.3 | 2153.3 | 781.6 | 669.4 | 798.3 | 753.2
3854.3 | 2154.3 | 781.4 | 661.7 | 791.1 | 752.2
3855.3 | 2155.3 | 781.4 | 655.6 | 787.7 | 753.9
3856.3 | 2156.3 | 781.3 | 655.4 | 785.2 | 753.6
3857.3 | 2157.3 | 782 | 676.1 | 795.6 | 755.3
3858.3 | 2158.3 | 782.2 | 682.8 | 797.7 | 755.6
3859.3 | 2159.3 | 782.2 | 700.4 | 790.9 | 750.4
3860.3 | 2160.3 | 782.4 | 702.4 | 775.4 | 739.2
3861.3 | 2161.3 | 781.4 | 709.7 | 759.7 | 723.7
3862.3 | 2162.3 | 780.9 | 719.7 | 768 | 724.7
3863.3 | 2163.3 | 780.1 | 725.5 | 747.5 | 717.5
3864.3 | 2164.3 | 779.9 | 751.1 | 760.4 | 720.5
3865.3 | 2165.3 | 781.9 | 770.5 | 773.4 | 721.1
3866.3 | 2166.3 | 784.2 | 784.2 | 772.3 | 718.3
3867.3 | 2167.3 | 784.5 | 797.7 | 766.3 | 720.2
3868.3 | 2168.3 | 784.2 | 782.8 | 751.8 | 715.5
3869.3 | 2169.3 | 782.8 | 758.6 | 738.1 | 709.2
3870.3 | 2170.3 | 780.4 | 730.5 | 737.3 | 708.4
3871.3 | 2171.3 | 779.3 | 727.1 | 746.5 | 710.9
3872.3 | 2172.3 | 779.2 | 727.9 | 770.1 | 722.1
3873.3 | 2173.3 | 779 | 724.2 | 778.1 | 729.7
3874.3 | 2174.3 | 779.9 | 725.6 | 792.4 | 735.9
3875.3 | 2175.3 | 781.7 | 748.5 | 792.9 | 730.7
3876.3 | 2176.3 | 783 | 757.9 | 794.5 | 719.5
3877.3 | 2177.3 | 784.5 | 757.3 | 794.9 | 713.3
3878.3 | 2178.3 | 784.3 | 747.7 | 793.2 | 718.2
3879.3 | 2179.3 | 785.5 | 746.6 | 799.5 | 724.4
3880.3 | 2180.3 | 785.9 | 728 | 794.7 | 735.5
3881.3 | 2181.3 | 784 | 711.4 | 792.2 | 740.5
3882.3 | 2182.3 | 784 | 722.5 | 793.8 | 745.9
3883.3 | 2183.3 | 784.6 | 732.5 | 799.8 | 743
3884.3 | 2184.3 | 782.5 | 707.4 | 756.6 | 722.4
3885.3 | 2185.3 | 779 | 680.2 | 731.9 | 711.4
3886.3 | 2186.3 | 776.3 | 662.8 | 714.8 | 705.4
3887.3 | 2187.3 | 772.7 | 649.2 | 694.6 | 703.1
3888.3 | 2188.3 | 769.2 | 628.5 | 682.9 | 708.9
3889.3 | 2189.3 | 765.1 | 603 | 669.1 | 708.1
3890.3 | 2190.3 | 761.3 | 592.2 | 663.4 | 706.7
3891.3 | 2191.3 | 758.5 | 580.5 | 666.7 | 707.8
3892.3 | 2192.3 | 755.5 | 569.3 | 638.7 | 696.7
3893.3 | 2193.3 | 751.6 | 545.9 | 605.8 | 683.5
3894.3 | 2194.3 | 747.3 | 526.4 | 587.9 | 675.3
3895.3 | 2195.3 | 742.5 | 520.9 | 587.7 | 675.2
3896.3 | 2196.3 | 739.7 | 538.9 | 619.8 | 685.1
3897.3 | 2197.3 | 740.3 | 560.3 | 666.7 | 703.1
3898.3 | 2198.3 | 740.7 | 563.2 | 686.3 | 714.9
3899.3 | 2199.3 | 738.9 | 566 | 689.1 | 715.7
3900.3 | 2200.3 | 737.6 | 570 | 702.4 | 718.5
3901.3 | 2201.3 | 738.6 | 580.3 | 717.9 | 719.3
3902.3 | 2202.3 | 739.3 | 587.5 | 717.5 | 715.5
3903.3 | 2203.3 | 742.4 | 617.6 | 749.3 | 726.3
3904.3 | 2204.3 | 747.1 | 659.3 | 770.8 | 728.5
3905.3 | 2205.3 | 750.8 | 685.4 | 786.9 | 737.9
3906.3 | 2206.3 | 751.8 | 685.5 | 777 | 738.4
3907.3 | 2207.3 | 751.9 | 670.5 | 764.1 | 733.4
3908.3 | 2208.3 | 752.3 | 663.7 | 764.7 | 732.4
3909.3 | 2209.3 | 752.4 | 657.8 | 760.7 | 729
3910.3 | 2210.3 | 752.3 | 643.4 | 738 | 717.9
3911.3 | 2211.3 | 750.8 | 634.9 | 711.5 | 704.4
3912.3 | 2212.3 | 749.5 | 619 | 711.6 | 702.7
3913.3 | 2213.3 | 747.7 | 611.1 | 697.2 | 700.6
3914.3 | 2214.3 | 744 | 588.9 | 663 | 691.2
3915.3 | 2215.3 | 740.5 | 581.3 | 653.5 | 685.3
3916.3 | 2216.3 | 737.1 | 566.8 | 643.4 | 681.5
3917.3 | 2217.3 | 733.5 | 554.1 | 632.5 | 682.9
3918.3 | 2218.3 | 730.2 | 563.5 | 654.9 | 692
3919.3 | 2219.3 | 730.8 | 580.2 | 699.5 | 711
3920.3 | 2220.3 | 731.1 | 589.6 | 699.6 | 707
3921.3 | 2221.3 | 729.6 | 574.7 | 689.8 | 698.9
3922.3 | 2222.3 | 727.8 | 556.7 | 661.8 | 697.6
3923.3 | 2223.3 | 725.4 | 534.7 | 638.7 | 691.9
3924.3 | 2224.3 | 722.4 | 518.7 | 626 | 689.7
3925.3 | 2225.3 | 718.8 | 499.4 | 609.9 | 688.1
3926.3 | 2226.3 | 714.5 | 484.4 | 600.7 | 683.1
3927.3 | 2227.3 | 710.9 | 472.9 | 586.8 | 674.7
3928.3 | 2228.3 | 707.7 | 471.8 | 589.4 | 676.7
3929.3 | 2229.3 | 704.7 | 470.2 | 603.6 | 682.2
3930.3 | 2230.3 | 701.4 | 472.9 | 618.3 | 684.7
3931.3 | 2231.3 | 700.3 | 504.2 | 654.9 | 694.1
3932.3 | 2232.3 | 703.8 | 545.3 | 688.8 | 702.6
3933.3 | 2233.3 | 705.3 | 569.2 | 693.1 | 699.1
3934.3 | 2234.3 | 705.2 | 560.3 | 676.2 | 691.3
3935.3 | 2235.3 | 705.7 | 575 | 687.2 | 696.3
3936.3 | 2236.3 | 708.8 | 595.6 | 712.6 | 704.3
3937.3 | 2237.3 | 713.2 | 634.7 | 726.9 | 702
3938.3 | 2238.3 | 714.2 | 626 | 733.1 | 708
3939.3 | 2239.3 | 713.9 | 622.4 | 741 | 711.5
3940.3 | 2240.3 | 716.3 | 624.4 | 768.1 | 721.3
3941.3 | 2241.3 | 720.7 | 640.1 | 782.5 | 725.8
3942.3 | 2242.3 | 722.7 | 631.5 | 773.4 | 734.3
3943.3 | 2243.3 | 724.5 | 631.7 | 778 | 738.1
3944.3 | 2244.3 | 726.2 | 629.3 | 776.4 | 734.9
3945.3 | 2245.3 | 725.8 | 618.9 | 768.9 | 728.9
3946.3 | 2246.3 | 725 | 618 | 768.2 | 729.6
3947.3 | 2247.3 | 725.4 | 621.1 | 771.1 | 728.5
3948.3 | 2248.3 | 724.7 | 621.4 | 767.1 | 726.1
3949.3 | 2249.3 | 724 | 645.6 | 751.7 | 713
3950.3 | 2250.3 | 723.6 | 662 | 751.7 | 715.2
3951.3 | 2251.3 | 722.9 | 666 | 754.3 | 721.3
3952.3 | 2252.3 | 722.8 | 672.7 | 764.8 | 727.9
3953.3 | 2253.3 | 723.3 | 677.5 | 762.8 | 723.3
3954.3 | 2254.3 | 725.6 | 685.1 | 776 | 724.4
3955.3 | 2255.3 | 729.9 | 694.6 | 793.8 | 730.1
3956.3 | 2256.3 | 731.5 | 705.3 | 794.7 | 723.8
3957.3 | 2257.3 | 735.1 | 729.1 | 803.3 | 722.7
3958.3 | 2258.3 | 736.6 | 728.4 | 788.8 | 717.2
3959.3 | 2259.3 | 737.1 | 727.5 | 784.3 | 716.1
3960.3 | 2260.3 | 740 | 738 | 789.9 | 726.1
3961.3 | 2261.3 | 741.8 | 745.3 | 797.8 | 731.1
3962.3 | 2262.3 | 740.9 | 734.5 | 771.7 | 721.2
3963.3 | 2263.3 | 739.6 | 718.2 | 765 | 724.1
3964.3 | 2264.3 | 738.4 | 697 | 764.1 | 732.1
3965.3 | 2265.3 | 738.9 | 699.3 | 782.5 | 742.7
3966.3 | 2266.3 | 741 | 728.1 | 785.7 | 735
3967.3 | 2267.3 | 744.3 | 758 | 791.3 | 728.2
3968.3 | 2268.3 | 748.6 | 777.6 | 811.6 | 733.8
3969.3 | 2269.3 | 750.6 | 765.7 | 806.1 | 736.7
3970.3 | 2270.3 | 748.9 | 747.5 | 777.6 | 726.3
3971.3 | 2271.3 | 745.9 | 713.6 | 755.3 | 717.3
3972.3 | 2272.3 | 742.7 | 687.6 | 746.7 | 729.2
3973.3 | 2273.3 | 739.6 | 669.2 | 750.3 | 735.8
3974.3 | 2274.3 | 738.6 | 682.9 | 761.5 | 735.2
3975.3 | 2275.3 | 740.2 | 701.5 | 775.7 | 730.6
3976.3 | 2276.3 | 741.7 | 710.5 | 791.1 | 739.9
3977.3 | 2277.3 | 741 | 692.7 | 773.4 | 744.4
3978.3 | 2278.3 | 738.7 | 673.4 | 770.4 | 736.7
3979.3 | 2279.3 | 736.7 | 662.9 | 774.4 | 737
3980.3 | 2280.3 | 735.5 | 664.9 | 775.8 | 740.3
3981.3 | 2281.3 | 734.1 | 657.2 | 770.9 | 741.2
3982.3 | 2282.3 | 734.3 | 665.9 | 781.5 | 753.2
3983.3 | 2283.3 | 734.6 | 656.2 | 792.1 | 763.3
3984.3 | 2284.3 | 734.9 | 653.1 | 799.8 | 770
3985.3 | 2285.3 | 735.5 | 650 | 799.4 | 770.5
3986.3 | 2286.3 | 734.1 | 631.1 | 794.7 | 771.4
3987.3 | 2287.3 | 734.3 | 648.3 | 797.6 | 769.1
3988.3 | 2288.3 | 735.2 | 677.1 | 773.4 | 755.8
3989.3 | 2289.3 | 734.9 | 687.1 | 769.2 | 743.8
3990.3 | 2290.3 | 736.9 | 701.4 | 784.3 | 740.7
3991.3 | 2291.3 | 737.1 | 707.4 | 759.3 | 729.5
3992.3 | 2292.3 | 734.2 | 698.8 | 732.1 | 716.2
3993.3 | 2293.3 | 730.2 | 681.6 | 710.6 | 706.3
3994.3 | 2294.3 | 729.4 | 701.7 | 720.1 | 705.6
3995.3 | 2295.3 | 729.2 | 707.9 | 726.9 | 716.5
3996.3 | 2296.3 | 729.9 | 715.4 | 750.8 | 737.2
3997.3 | 2297.3 | 731.5 | 735.3 | 763.5 | 734.4
3998.3 | 2298.3 | 731.6 | 746.4 | 753.2 | 721
3999.3 | 2299.3 | 733.2 | 757.4 | 761.1 | 721.3
4000.3 | 2300.3 | 735.6 | 764.7 | 772.3 | 724.6
4001.3 | 2301.3 | 738.7 | 772.1 | 786.8 | 729.5
4002.3 | 2302.3 | 741.8 | 775 | 787.7 | 734.4
4003.3 | 2303.3 | 741 | 759.7 | 760 | 716.2
4004.3 | 2304.3 | 739 | 747.5 | 738.5 | 704.6
4005.3 | 2305.3 | 736.2 | 730.3 | 711.3 | 698.3
4006.3 | 2306.3 | 733.1 | 707.2 | 676.9 | 688.7
4007.3 | 2307.3 | 729.6 | 671.6 | 646.5 | 680.7
4008.3 | 2308.3 | 725.4 | 648.2 | 633.9 | 676.9
4009.3 | 2309.3 | 721.4 | 643.8 | 630 | 676.3
4010.3 | 2310.3 | 716.7 | 633.2 | 609.2 | 668.8
4011.3 | 2311.3 | 711.7 | 625.5 | 602.2 | 665
4012.3 | 2312.3 | 707.3 | 618.2 | 587.6 | 662.1
4013.3 | 2313.3 | 703.2 | 625.3 | 593.9 | 661.7
4014.3 | 2314.3 | 698.6 | 626.9 | 597.4 | 657.7
4015.3 | 2315.3 | 696.5 | 642 | 599.6 | 655.6
4016.3 | 2316.3 | 697.1 | 659.7 | 623.3 | 660
4017.3 | 2317.3 | 699.1 | 670.1 | 655.7 | 671.8
4018.3 | 2318.3 | 702.4 | 687.3 | 687.3 | 690.5
4019.3 | 2319.3 | 704.4 | 698.9 | 702.6 | 702
4020.3 | 2320.3 | 706.5 | 717.8 | 717.1 | 706.8
4021.3 | 2321.3 | 707.1 | 701.3 | 699.6 | 698.7
4022.3 | 2322.3 | 706.7 | 691 | 696.3 | 689.8
4023.3 | 2323.3 | 706.4 | 686.1 | 709.4 | 691.7
4024.3 | 2324.3 | 706.2 | 687.8 | 706 | 687.4
4025.3 | 2325.3 | 705.1 | 690.7 | 697.4 | 676.6
4026.3 | 2326.3 | 704.7 | 688.9 | 686.4 | 667.4
4027.3 | 2327.3 | 706.8 | 713 | 710.8 | 679.5
4028.3 | 2328.3 | 710.7 | 738.4 | 725.2 | 690.6
4029.3 | 2329.3 | 712.5 | 761 | 730.2 | 693.1
4030.3 | 2330.3 | 713.9 | 743.9 | 738 | 691
4031.3 | 2331.3 | 713.9 | 714.9 | 728.9 | 686.8
4032.3 | 2332.3 | 712.6 | 696.5 | 713.1 | 677.6
4033.3 | 2333.3 | 709.9 | 678.6 | 690.3 | 671.1
4034.3 | 2334.3 | 706.1 | 652 | 676.7 | 668.4
4035.3 | 2335.3 | 701.7 | 639.4 | 651 | 665.1
4036.3 | 2336.3 | 697.7 | 622.5 | 635.5 | 657.3
4037.3 | 2337.3 | 692.6 | 606.6 | 623.1 | 654.4
4038.3 | 2338.3 | 691.6 | 637.3 | 644.4 | 660
4039.3 | 2339.3 | 693.6 | 662.3 | 672.9 | 677
4040.3 | 2340.3 | 695.8 | 687.3 | 701.2 | 686.4
4041.3 | 2341.3 | 698.7 | 692.1 | 729.6 | 704.4
4042.3 | 2342.3 | 699.8 | 689.6 | 735.2 | 714.8
4043.3 | 2343.3 | 699.8 | 677.4 | 726 | 705.6
4044.3 | 2344.3 | 699 | 658.3 | 707.8 | 691.8
4045.3 | 2345.3 | 697.5 | 661.7 | 712.8 | 695
4046.3 | 2346.3 | 696 | 649.7 | 699.9 | 681.2
4047.3 | 2347.3 | 697.3 | 653.2 | 727.9 | 691.9
4048.3 | 2348.3 | 699.9 | 649 | 739.1 | 699.2
4049.3 | 2349.3 | 698.4 | 647.8 | 714.7 | 691.2
4050.3 | 2350.3 | 696.6 | 632.5 | 690.2 | 678.1
4051.3 | 2351.3 | 693.9 | 624.6 | 672.9 | 668.1
4052.3 | 2352.3 | 691.6 | 638.6 | 666.6 | 660.8
4053.3 | 2353.3 | 690.1 | 666.8 | 660.5 | 654.1
4054.3 | 2354.3 | 690.8 | 695.6 | 660.2 | 651.5
4055.3 | 2355.3 | 692.5 | 712.8 | 665 | 655.4
4056.3 | 2356.3 | 691.4 | 708.9 | 665.5 | 655.8
4057.3 | 2357.3 | 691.3 | 705.4 | 684.5 | 663.4
4058.3 | 2358.3 | 692.6 | 709.8 | 694 | 670.7
4059.3 | 2359.3 | 694.9 | 715 | 716.2 | 682.8
4060.3 | 2360.3 | 699 | 724.4 | 742.1 | 690.8
4061.3 | 2361.3 | 700.1 | 695.5 | 737.2 | 696.6
4062.3 | 2362.3 | 701.7 | 685.6 | 734.5 | 698.7
4063.3 | 2363.3 | 702.2 | 692.3 | 726.3 | 685.1
4064.3 | 2364.3 | 703.9 | 707.1 | 750.1 | 686.5
4065.3 | 2365.3 | 706.9 | 705.7 | 767.4 | 704.6
4066.3 | 2366.3 | 708.2 | 709 | 782.1 | 715.6
4067.3 | 2367.3 | 711.5 | 728.7 | 789.6 | 713.7
4068.3 | 2368.3 | 712.4 | 716.3 | 762.9 | 702.6
4069.3 | 2369.3 | 711.5 | 691.1 | 740.2 | 693.3
4070.3 | 2370.3 | 709.8 | 671 | 729 | 690.6
4071.3 | 2371.3 | 707.3 | 655.9 | 735.8 | 696
4072.3 | 2372.3 | 703.7 | 637.1 | 721.3 | 697.1
4073.3 | 2373.3 | 700.7 | 627.1 | 718.3 | 694.5
4074.3 | 2374.3 | 700.1 | 646.3 | 731.1 | 692.5
4075.3 | 2375.3 | 702.4 | 658 | 752.2 | 699.5
4076.3 | 2376.3 | 702.1 | 638.1 | 736.8 | 703.5
4077.3 | 2377.3 | 701.4 | 633 | 732.4 | 690.8
4078.3 | 2378.3 | 700 | 629 | 713.1 | 680.2
4079.3 | 2379.3 | 697.4 | 619.4 | 686.3 | 672.1
4080.3 | 2380.3 | 693.4 | 600 | 661.8 | 665.7
4081.3 | 2381.3 | 688.9 | 594 | 660.5 | 663.6
4082.3 | 2382.3 | 686.2 | 586.9 | 658.8 | 667.2
4083.3 | 2383.3 | 683.3 | 567.9 | 637.7 | 664.1
4084.3 | 2384.3 | 679.4 | 546.3 | 626.8 | 664.6
4085.3 | 2385.3 | 675.8 | 543.4 | 642.9 | 676.3
4086.3 | 2386.3 | 675.1 | 561.6 | 666.6 | 684.3
4087.3 | 2387.3 | 673.7 | 578.9 | 663 | 676.3
4088.3 | 2388.3 | 672.5 | 579.3 | 653 | 680.9
4089.3 | 2389.3 | 670.5 | 558.1 | 640.7 | 686.3
4090.3 | 2390.3 | 669.5 | 551.4 | 653 | 699.2
4091.3 | 2391.3 | 667.4 | 533 | 641.4 | 703.5
4092.3 | 2392.3 | 665.2 | 531.1 | 643.7 | 702.9
4093.3 | 2393.3 | 663.2 | 525.4 | 639 | 695.4
4094.3 | 2394.3 | 661.1 | 515.8 | 637.4 | 701.5
4095.3 | 2395.3 | 659.2 | 522.1 | 660.6 | 711
4096.3 | 2396.3 | 657.7 | 514.4 | 647 | 702.8
4097.3 | 2397.3 | 655.3 | 497.7 | 616.4 | 682.5
4098.3 | 2398.3 | 652.8 | 480.7 | 590.2 | 672.6
4099.3 | 2399.3 | 650 | 465.8 | 588.5 | 676.3
4100.3 | 2400.3 | 647 | 453.1 | 587 | 689
4101.3 | 2401.3 | 643.8 | 457 | 617.1 | 695.9
4102.3 | 2402.3 | 644.4 | 496.2 | 668.9 | 712.7
4103.3 | 2403.3 | 646 | 511.3 | 682.4 | 707
4104.3 | 2404.3 | 647.3 | 529.9 | 687.5 | 694.3
4105.3 | 2405.3 | 648.9 | 564 | 695.8 | 687.5
4106.3 | 2406.3 | 653.6 | 616 | 708.3 | 683.4
4107.3 | 2407.3 | 656.4 | 642.3 | 695.2 | 678.1
4108.3 | 2408.3 | 660.1 | 671.2 | 709.2 | 682.1
4109.3 | 2409.3 | 662.7 | 657.7 | 707.7 | 687.5
4110.3 | 2410.3 | 661.4 | 630.8 | 699.5 | 681.5
4111.3 | 2411.3 | 662.3 | 613.6 | 706.4 | 690.3
4112.3 | 2412.3 | 661.6 | 587.6 | 677.6 | 682.6
4113.3 | 2413.3 | 659.5 | 564.8 | 658.1 | 680.7
4114.3 | 2414.3 | 656 | 559.3 | 655.5 | 676
4115.3 | 2415.3 | 654 | 564.4 | 648.8 | 672.5
4116.3 | 2416.3 | 652.9 | 582.3 | 649.1 | 674.4
4117.3 | 2417.3 | 652.7 | 584.4 | 644.3 | 680.9
4118.3 | 2418.3 | 651.9 | 571 | 642.8 | 681.2
4119.3 | 2419.3 | 650.5 | 552 | 632.2 | 672.2
4120.3 | 2420.3 | 648.9 | 539.7 | 614.6 | 667.5
4121.3 | 2421.3 | 646.6 | 526.7 | 590.2 | 659.8
4122.3 | 2422.3 | 644 | 534 | 595.1 | 659.4
4123.3 | 2423.3 | 643.3 | 568.4 | 636.7 | 678
4124.3 | 2424.3 | 645.3 | 579.6 | 672.7 | 695.2
4125.3 | 2425.3 | 647.2 | 595.6 | 691.8 | 696.2
4126.3 | 2426.3 | 647.8 | 599.8 | 698.3 | 693.9
4127.3 | 2427.3 | 648 | 603.1 | 690.7 | 680.6
4128.3 | 2428.3 | 648.8 | 619.9 | 694.2 | 676.8
4129.3 | 2429.3 | 652.5 | 629 | 721.4 | 692.1
4130.3 | 2430.3 | 656.2 | 636.9 | 751.7 | 710.8
4131.3 | 2431.3 | 659.8 | 665.2 | 759.4 | 707.8
4132.3 | 2432.3 | 662.1 | 685 | 756.7 | 697
4133.3 | 2433.3 | 662.9 | 701.4 | 738.1 | 682.9
4134.3 | 2434.3 | 664.6 | 711.2 | 724.1 | 677.5
4135.3 | 2435.3 | 666.1 | 709.7 | 724.5 | 673.8
4136.3 | 2436.3 | 668.1 | 717.1 | 731.6 | 672.3
4137.3 | 2437.3 | 672.4 | 723.3 | 758.2 | 683.6
4138.3 | 2438.3 | 678.1 | 734.3 | 793.3 | 703.7
4139.3 | 2439.3 | 683.9 | 739.2 | 808.6 | 714.4
4140.3 | 2440.3 | 687.6 | 731.1 | 798.9 | 718.6
4141.3 | 2441.3 | 688 | 715 | 775.7 | 715.1
4142.3 | 2442.3 | 688 | 703.7 | 769.8 | 710.1
4143.3 | 2443.3 | 689.3 | 695.5 | 768.6 | 711.3
4144.3 | 2444.3 | 693.1 | 716.4 | 790 | 717.4
4145.3 | 2445.3 | 697.5 | 732.3 | 805.9 | 719.5
4146.3 | 2446.3 | 701.9 | 742.1 | 811 | 716
4147.3 | 2447.3 | 704.9 | 742.1 | 801.8 | 720.8
4148.3 | 2448.3 | 704.2 | 720.5 | 778.5 | 717.6
4149.3 | 2449.3 | 702.7 | 704.4 | 760.4 | 711.5
4150.3 | 2450.3 | 702 | 708.9 | 772.3 | 713.9
4151.3 | 2451.3 | 704.2 | 714.6 | 793.1 | 723.9
4152.3 | 2452.3 | 704.7 | 697.2 | 784.8 | 734.1
4153.3 | 2453.3 | 702.9 | 665.1 | 760.8 | 729.7
4154.3 | 2454.3 | 701 | 636 | 745.6 | 725.9
4155.3 | 2455.3 | 699.6 | 638 | 753.6 | 725.5
4156.3 | 2456.3 | 699 | 655.7 | 745.5 | 718.6
4157.3 | 2457.3 | 696.8 | 688.5 | 741.6 | 710.6
4158.3 | 2458.3 | 698.9 | 718.4 | 756.9 | 710.8
4159.3 | 2459.3 | 703.2 | 730.8 | 784.4 | 730.8
4160.3 | 2460.3 | 705.9 | 731.6 | 801.9 | 743.9
4161.3 | 2461.3 | 708.7 | 740.3 | 807 | 738
4162.3 | 2462.3 | 711.1 | 756 | 804.5 | 731.5
4163.3 | 2463.3 | 714.3 | 762 | 817.4 | 737
4164.3 | 2464.3 | 716.7 | 763.9 | 826 | 739.3
4165.3 | 2465.3 | 718.2 | 750.7 | 824.3 | 740.6
4166.3 | 2466.3 | 720.3 | 740.2 | 824.7 | 746.1
4167.3 | 2467.3 | 722.3 | 738 | 826.7 | 746.1
4168.3 | 2468.3 | 723.4 | 729.2 | 826.7 | 742.7
4169.3 | 2469.3 | 722.5 | 710.9 | 813.9 | 739.2
4170.3 | 2470.3 | 721.4 | 690.2 | 813.8 | 750.3
4171.3 | 2471.3 | 719.3 | 672.5 | 805.5 | 756.9
4172.3 | 2472.3 | 719.3 | 675 | 819.2 | 764.5
4173.3 | 2473.3 | 718.8 | 666.3 | 826.2 | 773.7
4174.3 | 2474.3 | 716.7 | 642.4 | 795.1 | 764.8
4175.3 | 2475.3 | 713.1 | 621.5 | 769.1 | 757.2
4176.3 | 2476.3 | 710.2 | 615.3 | 779.4 | 757.3
4177.3 | 2477.3 | 708.5 | 604.7 | 786.2 | 764.4
4178.3 | 2478.3 | 706.3 | 585.3 | 756 | 756.8
4179.3 | 2479.3 | 702.4 | 571.7 | 734.9 | 744
4180.3 | 2480.3 | 699.3 | 564.4 | 727.9 | 744.7
4181.3 | 2481.3 | 696 | 555.1 | 731.7 | 750.3
4182.3 | 2482.3 | 693.3 | 545 | 725.1 | 751.9
4183.3 | 2483.3 | 691.3 | 536.9 | 724.3 | 756.8
4184.3 | 2484.3 | 687.4 | 537.4 | 718.9 | 750.5
4185.3 | 2485.3 | 685.9 | 542.2 | 723.2 | 748.6
4186.3 | 2486.3 | 683.2 | 538.3 | 695.9 | 731.5
4187.3 | 2487.3 | 680.6 | 553 | 682.7 | 722.8
4188.3 | 2488.3 | 681.3 | 608.3 | 702.6 | 724.2
4189.3 | 2489.3 | 684.2 | 645.9 | 733.3 | 735.7
4190.3 | 2490.3 | 685.9 | 646.2 | 754.2 | 746
4191.3 | 2491.3 | 687.4 | 666.1 | 767 | 750
4192.3 | 2492.3 | 688.4 | 683.9 | 759.1 | 748.3
4193.3 | 2493.3 | 688.2 | 659.7 | 717.4 | 738.9
4194.3 | 2494.3 | 686.7 | 633.9 | 712.5 | 732.6
4195.3 | 2495.3 | 686.1 | 629.8 | 739.2 | 741.4
4196.3 | 2496.3 | 686.7 | 640.9 | 748.4 | 747.4
4197.3 | 2497.3 | 686.4 | 644.9 | 743 | 739.1
4198.3 | 2498.3 | 685.1 | 649.3 | 717.6 | 725
4199.3 | 2499.3 | 684.4 | 656.1 | 701.5 | 722.1
4200.3 | 2500.3 | 683.2 | 650.5 | 699.1 | 727
4201.3 | 2501.3 | 681.2 | 649.2 | 705 | 724.8
4202.3 | 2502.3 | 681.8 | 635 | 727.1 | 735.6
4203.3 | 2503.3 | 684.7 | 663.3 | 746.9 | 747.1
4204.3 | 2504.3 | 686.7 | 682 | 749.3 | 740.9
4205.3 | 2505.3 | 688.2 | 689.5 | 745.4 | 730
4206.3 | 2506.3 | 689.7 | 704.3 | 743 | 726.1
4207.3 | 2507.3 | 689.1 | 696.3 | 716.8 | 716.7
4208.3 | 2508.3 | 686.4 | 692.5 | 704.3 | 708
4209.3 | 2509.3 | 687.5 | 727.1 | 722.1 | 713.3
4210.3 | 2510.3 | 691.3 | 747.5 | 740.4 | 723.4
4211.3 | 2511.3 | 694 | 747.1 | 764.2 | 735.4
4212.3 | 2512.3 | 696.8 | 728 | 788.3 | 753.8
4213.3 | 2513.3 | 697.7 | 714.8 | 787.1 | 757.3
4214.3 | 2514.3 | 696.4 | 685.9 | 775 | 753.6
4215.3 | 2515.3 | 694.8 | 664.8 | 760.7 | 753.5
4216.3 | 2516.3 | 692.3 | 649.8 | 748.1 | 745.4
4217.3 | 2517.3 | 690 | 645 | 755.8 | 744.9
4218.3 | 2518.3 | 689.4 | 655.5 | 754.7 | 734.5
4219.3 | 2519.3 | 691.1 | 664.2 | 748.5 | 725
4220.3 | 2520.3 | 691 | 650.5 | 730 | 727.6
4221.3 | 2521.3 | 687.5 | 632.8 | 716.9 | 732.7
4222.3 | 2522.3 | 684.5 | 615.7 | 706.6 | 726.2
4223.3 | 2523.3 | 682.8 | 613.4 | 720.6 | 733.2
4224.3 | 2524.3 | 683.7 | 620.5 | 732.8 | 733.5
4225.3 | 2525.3 | 686.3 | 633.8 | 762 | 752.3
4226.3 | 2526.3 | 686.1 | 616.7 | 752.8 | 756.4
4227.3 | 2527.3 | 685 | 593.7 | 721.5 | 737.2
4228.3 | 2528.3 | 681.2 | 575.6 | 691.7 | 720.5
4229.3 | 2529.3 | 677.4 | 555.5 | 656.8 | 707.2
4230.3 | 2530.3 | 674.7 | 537.2 | 639.3 | 707.1
4231.3 | 2531.3 | 670.4 | 520 | 623.1 | 709.6
4232.3 | 2532.3 | 665.9 | 503.2 | 595 | 697.5
4233.3 | 2533.3 | 661.3 | 492.3 | 596.6 | 701.5
4234.3 | 2534.3 | 658.1 | 482 | 594.3 | 705
4235.3 | 2535.3 | 653.9 | 478 | 598.2 | 705.5
4236.3 | 2536.3 | 649.2 | 470.4 | 587.7 | 693
4237.3 | 2537.3 | 645.3 | 461.2 | 580.7 | 684
4238.3 | 2538.3 | 642 | 468.1 | 611.1 | 696.8
4239.3 | 2539.3 | 642.9 | 505 | 651.7 | 701.9
4240.3 | 2540.3 | 645.4 | 562.3 | 676.6 | 698.6
4241.3 | 2541.3 | 647.2 | 583.6 | 679.1 | 701.7
4242.3 | 2542.3 | 646.6 | 571 | 657.3 | 695.6
4243.3 | 2543.3 | 645.1 | 554.5 | 648.2 | 696.3
4244.3 | 2544.3 | 644.6 | 541.7 | 655.1 | 698
4245.3 | 2545.3 | 642.8 | 522.1 | 626.7 | 685.8
4246.3 | 2546.3 | 640.5 | 519.2 | 629.7 | 680.3
4247.3 | 2547.3 | 638.7 | 531.5 | 625.7 | 674.1
4248.3 | 2548.3 | 637 | 563.2 | 632.4 | 670.4
4249.3 | 2549.3 | 635.7 | 593.8 | 636.2 | 667.8
4250.3 | 2550.3 | 637.5 | 630.4 | 641.9 | 665.9
4251.3 | 2551.3 | 638.4 | 641.5 | 651.5 | 669.1
4252.3 | 2552.3 | 638.6 | 622.5 | 634.8 | 661.3
4253.3 | 2553.3 | 636.9 | 610 | 635.8 | 664.9
4254.3 | 2554.3 | 635.5 | 607.2 | 650.3 | 669.1
4255.3 | 2555.3 | 635 | 588.8 | 650.8 | 675.9
4256.3 | 2556.3 | 633.6 | 570 | 673.9 | 692.6
4257.3 | 2557.3 | 632.6 | 568.9 | 674 | 696.3
4258.3 | 2558.3 | 634.7 | 579.2 | 708.3 | 712.4
4259.3 | 2559.3 | 639.4 | 614.4 | 737.3 | 725.8
4260.3 | 2560.3 | 644.7 | 643.2 | 755 | 723.2
4261.3 | 2561.3 | 647.3 | 640.6 | 752.1 | 718.9
4262.3 | 2562.3 | 649.3 | 632.1 | 751.8 | 716.5
4263.3 | 2563.3 | 649.6 | 612.1 | 720 | 703
4264.3 | 2564.3 | 649.2 | 585.1 | 686.2 | 689.1
4265.3 | 2565.3 | 647.6 | 560.8 | 667.8 | 691.3
4266.3 | 2566.3 | 644.8 | 547.9 | 671.9 | 706.6
4267.3 | 2567.3 | 642.8 | 544.6 | 687.3 | 718.5
4268.3 | 2568.3 | 643.5 | 568.2 | 715.3 | 723.3
4269.3 | 2569.3 | 645.5 | 581 | 728.2 | 715.3
4270.3 | 2570.3 | 645.3 | 564.3 | 689 | 695.8
4271.3 | 2571.3 | 643.5 | 541.5 | 661.5 | 686
4272.3 | 2572.3 | 641.5 | 520 | 640.7 | 687
4273.3 | 2573.3 | 638.6 | 502.9 | 630.9 | 690
4274.3 | 2574.3 | 635.2 | 499.1 | 636.7 | 688.8
4275.3 | 2575.3 | 631.4 | 500 | 624.4 | 685.6
4276.3 | 2576.3 | 631.6 | 532.1 | 657.1 | 687.6
4277.3 | 2577.3 | 631.6 | 534.1 | 672.3 | 703.2
4278.3 | 2578.3 | 628.8 | 528.6 | 656.1 | 698.3
4279.3 | 2579.3 | 627.4 | 520.8 | 647.4 | 691.1
4280.3 | 2580.3 | 625.8 | 506.8 | 628.5 | 681.2
4281.3 | 2581.3 | 623.3 | 496.2 | 622.6 | 679.1
4282.3 | 2582.3 | 623.8 | 514.4 | 650.7 | 698.3
4283.3 | 2583.3 | 626.9 | 542.8 | 696.6 | 712.1
4284.3 | 2584.3 | 629.9 | 572.2 | 711.5 | 713.3
4285.3 | 2585.3 | 630.2 | 567.7 | 681 | 693.7
4286.3 | 2586.3 | 629.4 | 554.5 | 653.5 | 680.1
4287.3 | 2587.3 | 627.7 | 549.2 | 631 | 676.2
4288.3 | 2588.3 | 626.4 | 534.9 | 607 | 668.4
4289.3 | 2589.3 | 624.4 | 538.2 | 622.5 | 673
4290.3 | 2590.3 | 625.3 | 565 | 658.8 | 685.6
4291.3 | 2591.3 | 627.5 | 572.3 | 681.2 | 697.6
4292.3 | 2592.3 | 627.9 | 570.9 | 669.2 | 694.7
4293.3 | 2593.3 | 627.5 | 565.8 | 659.5 | 687.2
4294.3 | 2594.3 | 626.4 | 569.2 | 664.4 | 682.9
4295.3 | 2595.3 | 625.7 | 551.2 | 647.3 | 681.9
4296.3 | 2596.3 | 624.3 | 536.6 | 639.4 | 678.4
4297.3 | 2597.3 | 622.7 | 527.4 | 643.3 | 680.1
4298.3 | 2598.3 | 621 | 511.6 | 617.8 | 675.1
4299.3 | 2599.3 | 619.3 | 494.9 | 595.5 | 664.2
4300.3 | 2600.3 | 616.5 | 484.7 | 583.7 | 660.8
4301.3 | 2601.3 | 614.4 | 471.7 | 579.7 | 657.8
4302.3 | 2602.3 | 612.3 | 470.1 | 565.3 | 652.1
4303.3 | 2603.3 | 610.7 | 497.4 | 590.7 | 652.9
4304.3 | 2604.3 | 612.3 | 528.5 | 639.8 | 667.2
4305.3 | 2605.3 | 614.1 | 552.5 | 658.6 | 675.5
4306.3 | 2606.3 | 611.1 | 530 | 620 | 658.3
4307.3 | 2607.3 | 607.3 | 506.8 | 575.2 | 637.6
4308.3 | 2608.3 | 604.7 | 486.8 | 539.4 | 626
4309.3 | 2609.3 | 601.1 | 464.6 | 505.3 | 616.6
4310.3 | 2610.3 | 596.6 | 445.5 | 476.9 | 607.8
4311.3 | 2611.3 | 591.6 | 428.4 | 452 | 600.9
4312.3 | 2612.3 | 584.5 | 411.4 | 428.5 | 592.7
4313.3 | 2613.3 | 577.7 | 396.6 | 408 | 586.4
4314.3 | 2614.3 | 572.1 | 382.7 | 389.6 | 579.8
4315.3 | 2615.3 | 567.1 | 369.5 | 374.8 | 576.9
4316.3 | 2616.3 | 561.9 | 357.6 | 360.2 | 575.5
4317.3 | 2617.3 | 556.6 | 346.4 | 346.9 | 572.3
4318.3 | 2618.3 | 551.3 | 336.5 | 335.2 | 568.4
4319.3 | 2619.3 | 546 | 326.7 | 324.3 | 564.2
4320.3 | 2620.3 | 540.8 | 317.8 | 313.9 | 560.7
4321.3 | 2621.3 | 535.6 | 308.5 | 303.7 | 556.3
4322.3 | 2622.3 | 530.5 | 299.7 | 293.9 | 550
4323.3 | 2623.3 | 525.5 | 292.4 | 285.2 | 543.6
4324.3 | 2624.3 | 520.5 | 285 | 277 | 538.4
4325.3 | 2625.3 | 515.7 | 279.1 | 269.7 | 534.9
4326.3 | 2626.3 | 510.9 | 273.3 | 262.1 | 531.1
4327.3 | 2627.3 | 506.3 | 267.5 | 255.1 | 526.6
4328.3 | 2628.3 | 501.8 | 264 | 247.8 | 522.8
4329.3 | 2629.3 | 497.4 | 260.7 | 240.8 | 519.2
4330.3 | 2630.3 | 493.1 | 257.5 | 234.3 | 515.3
4331.3 | 2631.3 | 488.8 | 254.3 | 228.4 | 511.2
4332.3 | 2632.3 | 484.6 | 251 | 223.1 | 506
4333.3 | 2633.3 | 480.5 | 247.5 | 218.5 | 499.6
4334.3 | 2634.3 | 476.4 | 244 | 213.7 | 495.4
4335.3 | 2635.3 | 472.5 | 240.2 | 209.3 | 491.5
4336.3 | 2636.3 | 468.5 | 236.5 | 205.5 | 488
4337.3 | 2637.3 | 464.7 | 233.2 | 201.3 | 484.6
4338.3 | 2638.3 | 461 | 230.5 | 196.7 | 480.2
4339.3 | 2639.3 | 457.3 | 227.9 | 192.5 | 476.2
4340.3 | 2640.3 | 453.7 | 225.8 | 189 | 472.4
4341.3 | 2641.3 | 450.2 | 222.8 | 185.5 | 468.5
4342.3 | 2642.3 | 446.7 | 219.7 | 182.1 | 465.1
4343.3 | 2643.3 | 443.3 | 218 | 179.2 | 461.9
4344.3 | 2644.3 | 440 | 215.1 | 176.4 | 456.9
4345.3 | 2645.3 | 436.7 | 211.7 | 173.6 | 452.9
4346.3 | 2646.3 | 433.5 | 208 | 170.8 | 448.9
4347.3 | 2647.3 | 430.3 | 204.4 | 168.6 | 444.9
4348.3 | 2648.3 | 427.2 | 201.2 | 166.3 | 443.1
4349.3 | 2649.3 | 424.1 | 197.9 | 164 | 440.9
4350.3 | 2650.3 | 421.1 | 194.5 | 161.7 | 438.1
4351.3 | 2651.3 | 418.1 | 191.4 | 159.4 | 435.4
4352.3 | 2652.3 | 415.2 | 188.2 | 157 | 432.2
4353.3 | 2653.3 | 412.4 | 185.2 | 154.5 | 428.8
4354.3 | 2654.3 | 409.7 | 182.2 | 152.1 | 425.2
4355.3 | 2655.3 | 407 | 179.6 | 149.9 | 422.1
4356.3 | 2656.3 | 404.3 | 178.2 | 147.6 | 419.2
4357.3 | 2657.3 | 401.7 | 175.9 | 145.2 | 416.1
4358.3 | 2658.3 | 399.1 | 173.3 | 143 | 413.5
4359.3 | 2659.3 | 396.6 | 171.2 | 141.1 | 410.9
4360.3 | 2660.3 | 394.1 | 169.5 | 139.3 | 407.7
4361.3 | 2661.3 | 391.6 | 167.9 | 137.8 | 404.8
4362.3 | 2662.3 | 389.2 | 166 | 135.8 | 402.8
4363.3 | 2663.3 | 386.8 | 164.3 | 134.2 | 400.9
4364.3 | 2664.3 | 384.4 | 163 | 132.4 | 398.6
4365.3 | 2665.3 | 382.1 | 162.4 | 130.5 | 395.8
4366.3 | 2666.3 | 379.8 | 161.4 | 128.7 | 393
4367.3 | 2667.3 | 377.5 | 160.3 | 126.9 | 390
4368.3 | 2668.3 | 375.2 | 158.9 | 125.2 | 387
4369.3 | 2669.3 | 373 | 157.5 | 123.7 | 383.7
4370.3 | 2670.3 | 370.8 | 156.9 | 122 | 381.4
4371.3 | 2671.3 | 368.6 | 155.6 | 120.4 | 379.2
4372.3 | 2672.3 | 366.5 | 154.7 | 118.9 | 377.2
4373.3 | 2673.3 | 364.4 | 153.8 | 117.1 | 375.4
4374.3 | 2674.3 | 362.3 | 152 | 115.4 | 372.6
4375.3 | 2675.3 | 360.2 | 150.2 | 114.2 | 371
4376.3 | 2676.3 | 358.1 | 148.1 | 112.9 | 369.2
4377.3 | 2677.3 | 356.1 | 146.2 | 111.4 | 366.7
4378.3 | 2678.3 | 354.1 | 144.5 | 110.2 | 364.7
4379.3 | 2679.3 | 352.1 | 143.3 | 109.2 | 363.1
4380.3 | 2680.3 | 350.1 | 142.5 | 108.2 | 361.2
4381.3 | 2681.3 | 348.2 | 141 | 107 | 359.3
4382.3 | 2682.3 | 346.3 | 140.3 | 105.9 | 357.1
4383.3 | 2683.3 | 344.4 | 139.1 | 104.9 | 355
4384.3 | 2684.3 | 342.5 | 138 | 103.9 | 353.3
4385.3 | 2685.3 | 340.7 | 137.1 | 102.6 | 351.5
4386.3 | 2686.3 | 338.9 | 136 | 101.4 | 349.1
4387.3 | 2687.3 | 337.1 | 135.2 | 100.4 | 346.2
4388.3 | 2688.3 | 335.3 | 134.1 | 99.5 | 344.4
4389.3 | 2689.3 | 333.6 | 133.1 | 98.6 | 343.5
4390.3 | 2690.3 | 331.9 | 132.6 | 97.6 | 341.7
4391.3 | 2691.3 | 330.1 | 131.5 | 96.4 | 340.5
4392.3 | 2692.3 | 328.4 | 130.2 | 95.7 | 338.6
4393.3 | 2693.3 | 326.7 | 129 | 95.1 | 337.1
4394.3 | 2694.3 | 325 | 127.9 | 94.7 | 336
4395.3 | 2695.3 | 323.3 | 126.6 | 94 | 333.9
4396.3 | 2696.3 | 321.6 | 125.1 | 93.2 | 331.9
4397.3 | 2697.3 | 320 | 123.8 | 92.7 | 330.5
4398.3 | 2698.3 | 318.4 | 122.7 | 92.1 | 328.5
4399.3 | 2699.3 | 316.8 | 121.8 | 91.5 | 326.5
4400.3 | 2700.3 | 315.2 | 121.1 | 90.9 | 324.8
4401.3 | 2701.3 | 313.6 | 120 | 90.4 | 323.4
4402.3 | 2702.3 | 312.1 | 119.1 | 89.9 | 321.9
4403.3 | 2703.3 | 310.5 | 118.2 | 89.2 | 320.2
4404.3 | 2704.3 | 309 | 118.2 | 88.7 | 318
4405.3 | 2705.3 | 307.5 | 117.4 | 88.1 | 316.1
4406.3 | 2706.3 | 306 | 116.8 | 87.7 | 315
4407.3 | 2707.3 | 304.5 | 116.1 | 87.3 | 313.8
4408.3 | 2708.3 | 303 | 115.5 | 86.8 | 312.6
4409.3 | 2709.3 | 301.6 | 115.4 | 86.4 | 311.1
4410.3 | 2710.3 | 300.1 | 115.4 | 86 | 309.8
4411.3 | 2711.3 | 298.7 | 114.8 | 85.5 | 308.2
4412.3 | 2712.3 | 297.3 | 114.2 | 85 | 306.7
4413.3 | 2713.3 | 295.9 | 114.2 | 84.6 | 305.2
4414.3 | 2714.3 | 294.5 | 113.2 | 84.2 | 302.9
4415.3 | 2715.3 | 293.2 | 112.3 | 83.6 | 301.6
4416.3 | 2716.3 | 291.8 | 111.5 | 82.9 | 300.3
4417.3 | 2717.3 | 290.4 | 110.9 | 82.2 | 298.6
4418.3 | 2718.3 | 289.1 | 111 | 81.6 | 297.3
4419.3 | 2719.3 | 287.8 | 110.3 | 81 | 295.5
4420.3 | 2720.3 | 286.4 | 109.9 | 80.6 | 294.3
4421.3 | 2721.3 | 285.1 | 109.5 | 80.3 | 293
4422.3 | 2722.3 | 283.9 | 108.9 | 79.8 | 291.6
4423.3 | 2723.3 | 282.6 | 108.8 | 79.2 | 289.9
4424.3 | 2724.3 | 281.3 | 108.6 | 78.8 | 288.3
4425.3 | 2725.3 | 280 | 109.1 | 78.3 | 287.2
4426.3 | 2726.3 | 278.8 | 109.6 | 77.7 | 286.2
4427.3 | 2727.3 | 277.5 | 109.4 | 77.1 | 284.8
4428.3 | 2728.3 | 276.2 | 108.8 | 76.6 | 283.4
4429.3 | 2729.3 | 275 | 109.3 | 76 | 281.9
4430.3 | 2730.3 | 273.8 | 109 | 75.4 | 280.9
4431.3 | 2731.3 | 272.6 | 109.2 | 74.9 | 280.2
4432.3 | 2732.3 | 271.4 | 108.7 | 74.4 | 279.1
4433.3 | 2733.3 | 270.3 | 107.8 | 73.9 | 277.6
4434.3 | 2734.3 | 269.1 | 107 | 73.4 | 275.4
4435.3 | 2735.3 | 268 | 105.9 | 72.9 | 272.7
4436.3 | 2736.3 | 266.9 | 105 | 72.4 | 271.1
4437.3 | 2737.3 | 265.8 | 104 | 71.9 | 270.3
4438.3 | 2738.3 | 264.7 | 102.8 | 71.4 | 269.7
4439.3 | 2739.3 | 263.6 | 102 | 71 | 268.5
4440.3 | 2740.3 | 262.5 | 101.1 | 70.6 | 267.1
4441.3 | 2741.3 | 261.3 | 100.2 | 70.2 | 266.4
4442.3 | 2742.3 | 260.2 | 99.3 | 69.7 | 265.7
4443.3 | 2743.3 | 259.2 | 99.1 | 69.3 | 264.8
4444.3 | 2744.3 | 258.1 | 99.1 | 69.1 | 263.8
4445.3 | 2745.3 | 257.1 | 99 | 68.9 | 262.9
4446.3 | 2746.3 | 256 | 99 | 68.6 | 261.8
4447.3 | 2747.3 | 254.9 | 98.3 | 68.2 | 260.8
4448.3 | 2748.3 | 253.8 | 97.6 | 67.9 | 259.7
4449.3 | 2749.3 | 252.8 | 96.9 | 67.6 | 258.5
4450.3 | 2750.3 | 251.7 | 96.1 | 67.3 | 257
4451.3 | 2751.3 | 250.6 | 95.5 | 67 | 255.6
4452.3 | 2752.3 | 249.6 | 94.9 | 66.8 | 254.6
4453.3 | 2753.3 | 248.6 | 94.4 | 66.5 | 253.2
4454.3 | 2754.3 | 247.5 | 94 | 66.2 | 252
4455.3 | 2755.3 | 246.5 | 93.9 | 65.9 | 251.3
4456.3 | 2756.3 | 245.5 | 93.2 | 65.7 | 250.5
4457.3 | 2757.3 | 244.5 | 92.9 | 65.4 | 249.8
4458.3 | 2758.3 | 243.5 | 92.6 | 65.2 | 249.3
4459.3 | 2759.3 | 242.6 | 92.4 | 65 | 248.5
4460.3 | 2760.3 | 241.6 | 91.9 | 64.8 | 247.5
4461.3 | 2761.3 | 240.6 | 91.4 | 64.6 | 246.2
4462.3 | 2762.3 | 239.7 | 90.9 | 64.4 | 245.6
4463.3 | 2763.3 | 238.7 | 90.5 | 64.2 | 244.7
4464.3 | 2764.3 | 237.7 | 90.1 | 63.9 | 243.6
4465.3 | 2765.3 | 236.8 | 89.7 | 63.7 | 243.5
4466.3 | 2766.3 | 235.8 | 89.2 | 63.6 | 242.7
4467.3 | 2767.3 | 234.9 | 88.6 | 63.3 | 241.4
4468.3 | 2768.3 | 234 | 88.2 | 63.1 | 240.3
4469.3 | 2769.3 | 233.1 | 87.7 | 62.8 | 239
4470.3 | 2770.3 | 232.2 | 87.2 | 62.6 | 237.8
4471.3 | 2771.3 | 231.3 | 86.7 | 62.4 | 236.6
4472.3 | 2772.3 | 230.4 | 86.3 | 62.2 | 236
4473.3 | 2773.3 | 229.5 | 85.8 | 62 | 235.4
4474.3 | 2774.3 | 228.6 | 85.4 | 61.8 | 234.6
4475.3 | 2775.3 | 227.7 | 85.1 | 61.7 | 233.8
4476.3 | 2776.3 | 226.8 | 84.8 | 61.6 | 233.3
4477.3 | 2777.3 | 226 | 84.4 | 61.5 | 232.5
4478.3 | 2778.3 | 225.1 | 84.2 | 61.4 | 231.3
4479.3 | 2779.3 | 224.4 | 84.1 | 61.2 | 230.7
4480.3 | 2780.3 | 223.5 | 83.9 | 61.1 | 229.6
4481.3 | 2781.3 | 222.6 | 84.2 | 61 | 228.4
4482.3 | 2782.3 | 221.9 | 84.5 | 60.8 | 227.4
4483.3 | 2783.3 | 221.1 | 84.5 | 60.5 | 226.3
4484.3 | 2784.3 | 220.3 | 84.2 | 60.4 | 225.2
4485.3 | 2785.3 | 219.4 | 83.8 | 60.3 | 224.4
4486.3 | 2786.3 | 218.7 | 84 | 60 | 223.8
4487.3 | 2787.3 | 217.8 | 84 | 59.9 | 223.1
4488.3 | 2788.3 | 217 | 84.6 | 59.7 | 222.4
4489.3 | 2789.3 | 216.3 | 84.9 | 59.4 | 221.7
4490.3 | 2790.3 | 215.5 | 84.6 | 59.2 | 220.6
4491.3 | 2791.3 | 214.7 | 84.2 | 59 | 219.3
4492.3 | 2792.3 | 213.9 | 84.1 | 58.8 | 218.2
4493.3 | 2793.3 | 213.2 | 84 | 58.5 | 217.6
4494.3 | 2794.3 | 212.5 | 84.1 | 58.3 | 216.8
4495.3 | 2795.3 | 211.7 | 83.9 | 58.1 | 216.1
4496.3 | 2796.3 | 211 | 83.8 | 57.8 | 215.3
4497.3 | 2797.3 | 210.3 | 83.3 | 57.7 | 214.3
4498.3 | 2798.3 | 209.6 | 82.9 | 57.6 | 213.9
4499.3 | 2799.3 | 208.9 | 82.4 | 57.5 | 213.2
4500.3 | 2800.3 | 208.2 | 82 | 57.3 | 212.3
4501.3 | 2801.3 | 207.5 | 81.7 | 57.1 | 211.3
4502.3 | 2802.3 | 206.8 | 81.4 | 57 | 210.2
4503.3 | 2803.3 | 206.2 | 80.9 | 56.8 | 209.2
4504.3 | 2804.3 | 205.5 | 80.5 | 56.5 | 208.3
4505.3 | 2805.3 | 204.8 | 80.6 | 56.3 | 207.8
4506.3 | 2806.3 | 204.1 | 80.3 | 56.1 | 207.6
4507.3 | 2807.3 | 203.5 | 80.1 | 55.9 | 206.7
4508.3 | 2808.3 | 202.8 | 80 | 55.8 | 205.6
4509.3 | 2809.3 | 202.1 | 79.9 | 55.7 | 204.7
4510.3 | 2810.3 | 201.4 | 79.5 | 55.6 | 203.7
4511.3 | 2811.3 | 200.7 | 79.2 | 55.6 | 203.1
4512.3 | 2812.3 | 200 | 79.5 | 55.5 | 202.9
4513.3 | 2813.3 | 199.4 | 79.5 | 55.4 | 202.4
4514.3 | 2814.3 | 198.7 | 79.3 | 55.2 | 201.9
4515.3 | 2815.3 | 198.1 | 79.3 | 55 | 201.4
4516.3 | 2816.3 | 197.4 | 79.6 | 54.9 | 200.9
4517.3 | 2817.3 | 196.8 | 79.8 | 54.7 | 200.6
4518.3 | 2818.3 | 196.1 | 80.1 | 54.6 | 199.9
4519.3 | 2819.3 | 195.5 | 80.9 | 54.3 | 199.1
4520.3 | 2820.3 | 194.9 | 81.3 | 54.2 | 198.3
4521.3 | 2821.3 | 194.3 | 81.5 | 54 | 197.5
4522.3 | 2822.3 | 193.7 | 81.8 | 53.9 | 196.7
4523.3 | 2823.3 | 193 | 82.2 | 53.8 | 196.3
4524.3 | 2824.3 | 192.5 | 82.6 | 53.6 | 195.3
4525.3 | 2825.3 | 191.9 | 83 | 53.4 | 194.1
4526.3 | 2826.3 | 191.3 | 83.4 | 53.2 | 193.3
4527.3 | 2827.3 | 190.7 | 83.7 | 52.9 | 192.6
4528.3 | 2828.3 | 190.1 | 84 | 52.7 | 191.9
4529.3 | 2829.3 | 189.5 | 84.1 | 52.5 | 191.1
4530.3 | 2830.3 | 188.9 | 83.8 | 52.3 | 190.6
4531.3 | 2831.3 | 188.3 | 83.8 | 52.1 | 190.4
4532.3 | 2832.3 | 187.8 | 83.9 | 52 | 189.9
4533.3 | 2833.3 | 187.2 | 84 | 51.8 | 189.4
4534.3 | 2834.3 | 186.6 | 83.4 | 51.7 | 188.6
4535.3 | 2835.3 | 186.1 | 83.3 | 51.6 | 188
4536.3 | 2836.3 | 185.5 | 83.3 | 51.6 | 187.4
4537.3 | 2837.3 | 184.9 | 83.3 | 51.4 | 186.7
4538.3 | 2838.3 | 184.4 | 83.5 | 51.3 | 185.6
4539.3 | 2839.3 | 183.9 | 83.4 | 51.2 | 184.6
4540.3 | 2840.3 | 183.4 | 83.2 | 51.2 | 183.8
4541.3 | 2841.3 | 182.8 | 83.6 | 51.1 | 183.4
4542.3 | 2842.3 | 182.3 | 83.2 | 51 | 182.9
4543.3 | 2843.3 | 181.8 | 83.1 | 51 | 182.3
4544.3 | 2844.3 | 181.3 | 82.8 | 50.9 | 181.7
4545.3 | 2845.3 | 180.8 | 82.5 | 50.8 | 181.1
4546.3 | 2846.3 | 180.3 | 81.9 | 50.8 | 180.6
4547.3 | 2847.3 | 179.8 | 81.8 | 50.7 | 180
4548.3 | 2848.3 | 179.2 | 81.3 | 50.6 | 179.4
4549.3 | 2849.3 | 178.7 | 80.9 | 50.5 | 178.9
4550.3 | 2850.3 | 178.2 | 80.6 | 50.3 | 178.3
4551.3 | 2851.3 | 177.7 | 80.4 | 50.3 | 177.8
4552.3 | 2852.3 | 177.3 | 80.1 | 50.2 | 177.1
4553.3 | 2853.3 | 176.8 | 79.8 | 50.1 | 176.4
4554.3 | 2854.3 | 176.3 | 79.6 | 50 | 175.9
4555.3 | 2855.3 | 175.8 | 79.3 | 49.9 | 175.3
4556.3 | 2856.3 | 175.3 | 79 | 49.8 | 174.6
4557.3 | 2857.3 | 174.9 | 78.6 | 49.9 | 173.7
4558.3 | 2858.3 | 174.4 | 78.3 | 50 | 172.5
4559.3 | 2859.3 | 173.9 | 78.2 | 49.9 | 172.2
4560.3 | 2860.3 | 173.5 | 77.9 | 49.8 | 172.1
4561.3 | 2861.3 | 173 | 77.6 | 49.7 | 171.5
4562.3 | 2862.3 | 172.5 | 77.5 | 49.6 | 170.9
4563.3 | 2863.3 | 172 | 77.2 | 49.5 | 170.4
4564.3 | 2864.3 | 171.6 | 76.8 | 49.5 | 170.3
4565.3 | 2865.3 | 171.1 | 77 | 49.5 | 170
4566.3 | 2866.3 | 170.6 | 77.3 | 49.4 | 169.4
4567.3 | 2867.3 | 170.2 | 77.1 | 49.4 | 168.7
4568.3 | 2868.3 | 169.7 | 76.8 | 49.3 | 167.8
4569.3 | 2869.3 | 169.2 | 76.3 | 49.3 | 167.4
4570.3 | 2870.3 | 168.8 | 75.8 | 49.2 | 167.1
4571.3 | 2871.3 | 168.3 | 75.7 | 49.2 | 166.7
4572.3 | 2872.3 | 167.9 | 75.6 | 49 | 166.3
4573.3 | 2873.3 | 167.4 | 75.7 | 48.9 | 165.7
4574.3 | 2874.3 | 166.9 | 75.8 | 48.8 | 165.1
4575.3 | 2875.3 | 166.5 | 75.6 | 48.7 | 164.5
4576.3 | 2876.3 | 166 | 75.6 | 48.5 | 163.9
4577.3 | 2877.3 | 165.6 | 75.2 | 48.4 | 163.4
4578.3 | 2878.3 | 165.2 | 75.1 | 48.3 | 163
4579.3 | 2879.3 | 164.7 | 75.1 | 48.2 | 162.4
4580.3 | 2880.3 | 164.3 | 75.1 | 48.1 | 162
4581.3 | 2881.3 | 163.8 | 75.3 | 48 | 161.6
4582.3 | 2882.3 | 163.4 | 75.4 | 47.9 | 161.4
4583.3 | 2883.3 | 163 | 75.5 | 47.9 | 161.4
4584.3 | 2884.3 | 162.6 | 75.7 | 47.8 | 161.1
4585.3 | 2885.3 | 162.2 | 75.5 | 47.8 | 160.2
4586.3 | 2886.3 | 161.8 | 75.2 | 47.7 | 159.4
4587.3 | 2887.3 | 161.3 | 74.8 | 47.6 | 158.6
4588.3 | 2888.3 | 160.9 | 75 | 47.6 | 157.9
4589.3 | 2889.3 | 160.5 | 75.2 | 47.5 | 157.4
4590.3 | 2890.3 | 160.1 | 75.3 | 47.4 | 156.9
4591.3 | 2891.3 | 159.7 | 75.2 | 47.3 | 156.5
4592.3 | 2892.3 | 159.3 | 74.8 | 47.2 | 156
4593.3 | 2893.3 | 159 | 74.3 | 47.2 | 155.8
4594.3 | 2894.3 | 158.6 | 74.2 | 47 | 155.6
4595.3 | 2895.3 | 158.2 | 74.3 | 46.9 | 155.1
4596.3 | 2896.3 | 157.9 | 74.4 | 46.8 | 154.6
4597.3 | 2897.3 | 157.5 | 74.4 | 46.7 | 154.1
4598.3 | 2898.3 | 157.1 | 74.2 | 46.6 | 153.8
4599.3 | 2899.3 | 156.8 | 74.4 | 46.5 | 153.9
4600.3 | 2900.3 | 156.4 | 74.3 | 46.5 | 153.8
4601.3 | 2901.3 | 156.1 | 73.9 | 46.4 | 153.1
4602.3 | 2902.3 | 155.7 | 73.6 | 46.4 | 152
4603.3 | 2903.3 | 155.4 | 73.3 | 46.3 | 151.3
4604.3 | 2904.3 | 155 | 73 | 46.3 | 151.1
4605.3 | 2905.3 | 154.6 | 72.7 | 46.3 | 150.8
4606.3 | 2906.3 | 154.3 | 72.7 | 46.3 | 150.1
4607.3 | 2907.3 | 153.9 | 72.6 | 46.4 | 149.4
4608.3 | 2908.3 | 153.5 | 72.5 | 46.3 | 149.2
4609.3 | 2909.3 | 153.1 | 72.2 | 46.3 | 148.8
4610.3 | 2910.3 | 152.8 | 72.3 | 46.2 | 148.2
4611.3 | 2911.3 | 152.5 | 72.4 | 46.1 | 147.8
4612.3 | 2912.3 | 152.1 | 72.3 | 46 | 147.2
4613.3 | 2913.3 | 151.7 | 72.5 | 45.9 | 146.8
4614.3 | 2914.3 | 151.4 | 72.5 | 45.8 | 146.6
4615.3 | 2915.3 | 151 | 72.6 | 45.6 | 146.3
4616.3 | 2916.3 | 150.7 | 72.6 | 45.5 | 145.9
4617.3 | 2917.3 | 150.4 | 72.7 | 45.4 | 145.5
4618.3 | 2918.3 | 150 | 72.8 | 45.3 | 145
4619.3 | 2919.3 | 149.7 | 72.7 | 45.2 | 144.3
4620.3 | 2920.3 | 149.3 | 72.5 | 45.1 | 143.8
4621.3 | 2921.3 | 149 | 72.1 | 44.9 | 143.3
4622.3 | 2922.3 | 148.7 | 71.9 | 44.8 | 142.8
4623.3 | 2923.3 | 148.4 | 71.6 | 44.7 | 142.4
4624.3 | 2924.3 | 148 | 71.5 | 44.6 | 142.3
4625.3 | 2925.3 | 147.7 | 71.4 | 44.5 | 142.2
4626.3 | 2926.3 | 147.3 | 71.2 | 44.5 | 142.2
4627.3 | 2927.3 | 147 | 71.2 | 44.4 | 141.9
4628.3 | 2928.3 | 146.7 | 71.1 | 44.4 | 141.6
4629.3 | 2929.3 | 146.4 | 71 | 44.3 | 141.3
4630.3 | 2930.3 | 146 | 70.8 | 44.3 | 140.6
4631.3 | 2931.3 | 145.7 | 70.7 | 44.2 | 140.2
4632.3 | 2932.3 | 145.4 | 70.5 | 44.1 | 139.9
4633.3 | 2933.3 | 145 | 70.6 | 44.1 | 140
4634.3 | 2934.3 | 144.7 | 70.6 | 44.1 | 139.7
4635.3 | 2935.3 | 144.4 | 70.8 | 44 | 138.9
4636.3 | 2936.3 | 144 | 70.7 | 43.9 | 138.2
4637.3 | 2937.3 | 143.7 | 70.8 | 43.9 | 137.6
4638.3 | 2938.3 | 143.4 | 70.5 | 43.8 | 137.2
4639.3 | 2939.3 | 143.1 | 70.5 | 43.7 | 136.8
4640.3 | 2940.3 | 142.7 | 70.5 | 43.6 | 136.6
4641.3 | 2941.3 | 142.4 | 70.4 | 43.6 | 136.2
4642.3 | 2942.3 | 142.1 | 70.1 | 43.5 | 135.9
4643.3 | 2943.3 | 141.8 | 70.2 | 43.5 | 135.4
4644.3 | 2944.3 | 141.5 | 70.5 | 43.4 | 135
4645.3 | 2945.3 | 141.1 | 70.6 | 43.4 | 134.5
4646.3 | 2946.3 | 140.8 | 70.5 | 43.3 | 134.2
4647.3 | 2947.3 | 140.5 | 70.3 | 43.2 | 133.8
4648.3 | 2948.3 | 140.2 | 70.1 | 43 | 133.5
4649.3 | 2949.3 | 139.9 | 70.1 | 42.9 | 133
4650.3 | 2950.3 | 139.6 | 69.8 | 42.9 | 132.5
4651.3 | 2951.3 | 139.3 | 69.5 | 42.9 | 132
4652.3 | 2952.3 | 138.9 | 69.1 | 42.8 | 131.6
4653.3 | 2953.3 | 138.6 | 69.1 | 42.8 | 131.2
4654.3 | 2954.3 | 138.3 | 69.2 | 42.8 | 130.8
4655.3 | 2955.3 | 138 | 69.2 | 42.7 | 130.5
4656.3 | 2956.3 | 137.7 | 69 | 42.6 | 130.2
4657.3 | 2957.3 | 137.4 | 69 | 42.5 | 129.6
4658.3 | 2958.3 | 137.1 | 68.9 | 42.5 | 129.2
4659.3 | 2959.3 | 136.8 | 68.8 | 42.4 | 129
4660.3 | 2960.3 | 136.5 | 68.7 | 42.4 | 128.9
4661.3 | 2961.3 | 136.2 | 68.5 | 42.3 | 128.5
4662.3 | 2962.3 | 136 | 68.4 | 42.2 | 128
4663.3 | 2963.3 | 135.7 | 68.4 | 42.1 | 127.7
4664.3 | 2964.3 | 135.4 | 68.4 | 42.1 | 127.5
4665.3 | 2965.3 | 135.1 | 68.3 | 42 | 127.2
4666.3 | 2966.3 | 134.8 | 68 | 42 | 127
4667.3 | 2967.3 | 134.5 | 67.7 | 42 | 126.8
4668.3 | 2968.3 | 134.2 | 67.3 | 41.9 | 126.5
4669.3 | 2969.3 | 134 | 67.1 | 41.9 | 126.2
4670.3 | 2970.3 | 133.7 | 66.8 | 41.9 | 126.1
4671.3 | 2971.3 | 133.4 | 66.6 | 41.9 | 126.1
4672.3 | 2972.3 | 133.1 | 66.7 | 42 | 126.2
4673.3 | 2973.3 | 132.9 | 66.8 | 41.9 | 126.1
4674.3 | 2974.3 | 132.6 | 67 | 41.8 | 125.8
4675.3 | 2975.3 | 132.3 | 66.5 | 41.8 | 125.4
4676.3 | 2976.3 | 132.1 | 66.5 | 41.8 | 125.1
4677.3 | 2977.3 | 131.8 | 66.8 | 41.8 | 124.8
4678.3 | 2978.3 | 131.6 | 66.6 | 41.7 | 124.4
4679.3 | 2979.3 | 131.3 | 66.6 | 41.7 | 124
4680.3 | 2980.3 | 131 | 66.7 | 41.7 | 123.4
4681.3 | 2981.3 | 130.8 | 66.6 | 41.6 | 122.8
4682.3 | 2982.3 | 130.5 | 66.6 | 41.6 | 122.3
4683.3 | 2983.3 | 130.3 | 66.2 | 41.6 | 122.2
4684.3 | 2984.3 | 130 | 66 | 41.6 | 121.6
4685.3 | 2985.3 | 129.8 | 65.8 | 41.5 | 121
4686.3 | 2986.3 | 129.5 | 65.4 | 41.6 | 120.5
4687.3 | 2987.3 | 129.2 | 65.2 | 41.6 | 120.2
4688.3 | 2988.3 | 129 | 64.8 | 41.6 | 119.8
4689.3 | 2989.3 | 128.7 | 64.6 | 41.6 | 119.6
4690.3 | 2990.3 | 128.5 | 64 | 41.6 | 118.9
4691.3 | 2991.3 | 128.2 | 63.5 | 41.5 | 118.3
4692.3 | 2992.3 | 127.9 | 63 | 41.4 | 118
4693.3 | 2993.3 | 127.7 | 62.7 | 41.4 | 117.9
4694.3 | 2994.3 | 127.4 | 62.3 | 41.3 | 117.7
4695.3 | 2995.3 | 127.1 | 61.9 | 41.2 | 117.3
4696.3 | 2996.3 | 126.9 | 61.6 | 41.2 | 117.2
4697.3 | 2997.3 | 126.6 | 61.4 | 41.1 | 117.2
4698.3 | 2998.3 | 126.3 | 61.2 | 41 | 117.1
4699.3 | 2999.3 | 126 | 60.7 | 41 | 116.8
4700.3 | 3000.3 | 125.8 | 60.4 | 41 | 116.5
4701.3 | 3001.3 | 125.5 | 60.1 | 40.9 | 116.5
4702.3 | 3002.3 | 125.3 | 60 | 40.9 | 116.3
4703.3 | 3003.3 | 125 | 59.9 | 40.8 | 116
4704.3 | 3004.3 | 124.7 | 59.9 | 40.7 | 115.6
4705.3 | 3005.3 | 124.5 | 59.6 | 40.6 | 115.3
4706.3 | 3006.3 | 124.2 | 59.6 | 40.6 | 114.9
4707.3 | 3007.3 | 124 | 59.7 | 40.5 | 114.7
4708.3 | 3008.3 | 123.7 | 59.9 | 40.5 | 114.7
4709.3 | 3009.3 | 123.5 | 59.7 | 40.5 | 114.2
4710.3 | 3010.3 | 123.2 | 59.8 | 40.4 | 113.8
4711.3 | 3011.3 | 123 | 59.9 | 40.4 | 113.6
4712.3 | 3012.3 | 122.7 | 59.7 | 40.3 | 113.2
4713.3 | 3013.3 | 122.5 | 59.7 | 40.2 | 112.9
4714.3 | 3014.3 | 122.2 | 59.6 | 40.1 | 112.9
4715.3 | 3015.3 | 122 | 59.5 | 40 | 112.7
4716.3 | 3016.3 | 121.8 | 59.3 | 40 | 112.3
4717.3 | 3017.3 | 121.5 | 59.1 | 39.9 | 111.8
4718.3 | 3018.3 | 121.2 | 59.2 | 39.8 | 111.7
4719.3 | 3019.3 | 121 | 59 | 39.8 | 111.2
4720.3 | 3020.3 | 120.8 | 58.5 | 39.9 | 110.4
4721.3 | 3021.3 | 120.6 | 58.1 | 39.9 | 110
4722.3 | 3022.3 | 120.4 | 57.7 | 39.8 | 109.8
4723.3 | 3023.3 | 120.1 | 57.4 | 39.8 | 109.7
4724.3 | 3024.3 | 119.9 | 57 | 39.7 | 109.7
4725.3 | 3025.3 | 119.6 | 56.9 | 39.7 | 109.8
4726.3 | 3026.3 | 119.4 | 56.7 | 39.6 | 109.4
4727.3 | 3027.3 | 119.2 | 56.5 | 39.7 | 108.9
4728.3 | 3028.3 | 118.9 | 56.4 | 39.9 | 108.3
4729.3 | 3029.3 | 118.7 | 56.2 | 40 | 108
4730.3 | 3030.3 | 118.4 | 56 | 40 | 108
4731.3 | 3031.3 | 118.2 | 55.9 | 40.1 | 107.7
4732.3 | 3032.3 | 118 | 55.8 | 40 | 107.5
4733.3 | 3033.3 | 117.7 | 55.7 | 40 | 107.4
4734.3 | 3034.3 | 117.5 | 55.7 | 39.9 | 107.3
4735.3 | 3035.3 | 117.2 | 55.5 | 39.8 | 107.1
4736.3 | 3036.3 | 117 | 55.3 | 39.7 | 106.8
4737.3 | 3037.3 | 116.8 | 55.2 | 39.7 | 106.6
4738.3 | 3038.3 | 116.5 | 55.2 | 39.6 | 106.4
4739.3 | 3039.3 | 116.3 | 54.9 | 39.5 | 106
4740.3 | 3040.3 | 116 | 54.5 | 39.6 | 105.4
4741.3 | 3041.3 | 115.8 | 54.2 | 39.5 | 104.9
4742.3 | 3042.3 | 115.5 | 53.9 | 39.4 | 104.3
4743.3 | 3043.3 | 115.3 | 53.7 | 39.3 | 104.2
4744.3 | 3044.3 | 115.1 | 53.7 | 39.3 | 103.9
4745.3 | 3045.3 | 114.9 | 53.4 | 39.3 | 103.8
4746.3 | 3046.3 | 114.6 | 53.1 | 39.2 | 103.5
4747.3 | 3047.3 | 114.4 | 52.9 | 39.1 | 103
4748.3 | 3048.3 | 114.1 | 52.8 | 39 | 102.8
4749.3 | 3049.3 | 113.9 | 52.6 | 39 | 102.7
4750.3 | 3050.3 | 113.6 | 52.4 | 38.9 | 102.5
4751.3 | 3051.3 | 113.4 | 52.4 | 38.8 | 102.4
4752.3 | 3052.3 | 113.1 | 52.3 | 38.8 | 102.5
4753.3 | 3053.3 | 112.9 | 52.3 | 38.8 | 102.3
4754.3 | 3054.3 | 112.6 | 52.3 | 38.7 | 102.2
4755.3 | 3055.3 | 112.4 | 52.7 | 38.6 | 102
4756.3 | 3056.3 | 112.1 | 52.8 | 38.6 | 102
4757.3 | 3057.3 | 111.9 | 52.6 | 38.5 | 101.9
4758.3 | 3058.3 | 111.6 | 52.6 | 38.4 | 101.7
4759.3 | 3059.3 | 111.4 | 52.5 | 38.4 | 101.3
4760.3 | 3060.3 | 111.2 | 52.4 | 38.4 | 100.9
4761.3 | 3061.3 | 110.9 | 52.5 | 38.3 | 100.6
4762.3 | 3062.3 | 110.7 | 52.4 | 38.2 | 100.3
4763.3 | 3063.3 | 110.5 | 52.3 | 38.2 | 99.8
4764.3 | 3064.3 | 110.2 | 52.4 | 38.1 | 99.6
4765.3 | 3065.3 | 110 | 52.7 | 38.1 | 99.6
4766.3 | 3066.3 | 109.8 | 52.9 | 38.1 | 99.5
4767.3 | 3067.3 | 109.6 | 53 | 38 | 99.4
4768.3 | 3068.3 | 109.4 | 52.9 | 38 | 99.3
4769.3 | 3069.3 | 109.2 | 53 | 37.9 | 99.1
4770.3 | 3070.3 | 108.9 | 53.1 | 37.9 | 98.9
4771.3 | 3071.3 | 108.7 | 53.1 | 37.8 | 98.8
4772.3 | 3072.3 | 108.5 | 53.1 | 37.8 | 98.7
4773.3 | 3073.3 | 108.3 | 53.2 | 37.7 | 98.4
4774.3 | 3074.3 | 108.1 | 53.2 | 37.7 | 98.1
4775.3 | 3075.3 | 107.9 | 53.1 | 37.6 | 97.8
4776.3 | 3076.3 | 107.8 | 53 | 37.7 | 97.7
4777.3 | 3077.3 | 107.6 | 52.9 | 37.6 | 97.4
4778.3 | 3078.3 | 107.4 | 52.8 | 37.6 | 97
4779.3 | 3079.3 | 107.2 | 52.7 | 37.6 | 96.6
4780.3 | 3080.3 | 107 | 52.6 | 37.6 | 96.5
4781.3 | 3081.3 | 106.8 | 52.6 | 37.5 | 96.5
4782.3 | 3082.3 | 106.6 | 52.7 | 37.6 | 96.4
4783.3 | 3083.3 | 106.4 | 52.7 | 37.5 | 96
4784.3 | 3084.3 | 106.2 | 52.5 | 37.5 | 95.9
4785.3 | 3085.3 | 106 | 52.4 | 37.5 | 95.2
4786.3 | 3086.3 | 105.8 | 52.3 | 37.5 | 94.8
4787.3 | 3087.3 | 105.6 | 52.1 | 37.5 | 94.4
4788.3 | 3088.3 | 105.4 | 52 | 37.6 | 94.1
4789.3 | 3089.3 | 105.2 | 51.8 | 37.6 | 94.1
4790.3 | 3090.3 | 105 | 51.7 | 37.5 | 94.4
4791.3 | 3091.3 | 104.8 | 51.6 | 37.5 | 94.4
4792.3 | 3092.3 | 104.6 | 51.8 | 37.4 | 94.2
4793.3 | 3093.3 | 104.4 | 52 | 37.3 | 94.1
4794.3 | 3094.3 | 104.2 | 52.2 | 37.3 | 93.9
4795.3 | 3095.3 | 104 | 52.3 | 37.2 | 93.7
4796.3 | 3096.3 | 103.8 | 52.4 | 37.2 | 93.6
4797.3 | 3097.3 | 103.6 | 52.2 | 37.2 | 93.3
4798.3 | 3098.3 | 103.4 | 51.9 | 37.2 | 93.2
4799.3 | 3099.3 | 103.2 | 51.7 | 37.1 | 92.8
4800.3 | 3100.3 | 103 | 51.6 | 37.1 | 92.5
4801.3 | 3101.3 | 102.8 | 51.7 | 37.1 | 92.5
4802.3 | 3102.3 | 102.6 | 51.8 | 37.2 | 92.3
4803.3 | 3103.3 | 102.4 | 52.1 | 37.3 | 92.1
4804.3 | 3104.3 | 102.2 | 52.2 | 37.4 | 92.1
4805.3 | 3105.3 | 102 | 52.3 | 37.3 | 92.1
4806.3 | 3106.3 | 101.8 | 52.3 | 37.3 | 92.1
4807.3 | 3107.3 | 101.7 | 52.4 | 37.2 | 91.9
4808.3 | 3108.3 | 101.5 | 52.3 | 37.2 | 91.7
4809.3 | 3109.3 | 101.3 | 52.3 | 37.1 | 91.5
4810.3 | 3110.3 | 101.1 | 52.2 | 37.1 | 91.4
4811.3 | 3111.3 | 101 | 52.2 | 37.1 | 91.3
4812.3 | 3112.3 | 100.8 | 52.3 | 37.1 | 91.3
4813.3 | 3113.3 | 100.6 | 52.3 | 37.1 | 91.2
4814.3 | 3114.3 | 100.5 | 52.1 | 37.1 | 91

## Test Facts
Last row in IRMS data sheets: | 34
Time when gas burner was ignited: | 1700