## Test Conditions
CAROLFIRE Intermediate Scale Preliminary Test Number IP-1
Test Date: | 2006-10-12
Ignition Time Relative to Thermal Data: | 1700 | s
Ignition Time Relative to Electrical Data: | 1700 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
3/C cable:
7/C cable:

## Thermal Data
Time (s) |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 3/C cable |  |  | Location A - 7/C cable |  |  | Tray
Recorded time (s) | Offset Time (s) | Gas Flow Controller Flow Rate Reading | Actual Gas Flow Rate (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | Oxygen concentration (%) | Outlet stack Temperature | Differential pressure at stack *10 | Wind Direction | Wind Speed | Cable Temp | Temp Above Cable | Temp Below Cable | Cable Temp | Temp Above Cable | Temp Below Cable | Cable Tray Rung Temp
0 | -1700 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16 | 1 | n/a | n/a | 15.4 | 15.2 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
1 | -1699 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 1.1 |  |  | 15.4 | 15.2 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
2 | -1698 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 1.4 |  |  | 15.4 | 15.2 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
3 | -1697 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 1.6 |  |  | 15.4 | 15.3 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
4 | -1696 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 1.9 |  |  | 15.4 | 15.3 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
5 | -1695 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 2.1 |  |  | 15.4 | 15.2 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
6 | -1694 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 1.9 |  |  | 15.4 | 15.3 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
7 | -1693 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 2.4 |  |  | 15.4 | 15.2 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
8 | -1692 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 2.9 |  |  | 15.4 | 15.3 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
9 | -1691 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 2.3 |  |  | 15.4 | 15.3 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
10 | -1690 | -6.7 | 0 | 0 | 16.5 | 16.5 | 16.4 | 16.3 | 16.3 | 15.8 | 22 | 16.1 | 2.2 |  |  | 15.4 | 15.3 | 15.5 | 15.6 | 15.1 | 15.4 | 16.6
1697.2 | -2.8 | -6.7 | 0 | 0 | 16.6 | 16.8 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.3 | 0.9 |  |  | 15.6 | 15.5 | 16.2 | 15.8 | 15.3 | 15.8 | 16.9
1698.2 | -1.8 | -6.7 | 0 | 0 | 16.6 | 16.8 | 16.7 | 16.5 | 16.6 | 16.1 | 22 | 16.3 | 0.8 |  |  | 15.6 | 15.5 | 16.2 | 15.8 | 15.3 | 15.8 | 16.9
1699.2 | -0.8 | -6.4 | 0 | 0 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 22 | 16.3 | 0.5 |  |  | 15.6 | 15.5 | 16.2 | 15.8 | 15.3 | 15.8 | 16.9
1700.2 | 0.2 | 11.4 | 4.56 | 5.3304 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.3 | 0.4 |  |  | 15.6 | 15.5 | 16.2 | 15.8 | 15.3 | 15.8 | 16.9
1701.2 | 1.2 | 36.3 | 14.52 | 16.973 | 16.6 | 16.9 | 16.7 | 16.5 | 16.5 | 16.1 | 21.9 | 16.4 | 0.4 |  |  | 15.6 | 15.5 | 16.2 | 15.8 | 15.3 | 15.8 | 16.8
1702.2 | 2.2 | 57.8 | 23.12 | 27.0259 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.4 | 0.6 |  |  | 15.6 | 15.5 | 16.1 | 15.8 | 15.3 | 15.8 | 16.8
1703.2 | 3.2 | 71.2 | 28.48 | 33.2915 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.3 | 0.8 |  |  | 15.6 | 15.5 | 16.1 | 15.8 | 15.3 | 15.8 | 16.8
1704.2 | 4.2 | 71.8 | 28.72 | 33.572 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.3 | 0.8 |  |  | 15.6 | 15.5 | 16.1 | 15.8 | 15.3 | 15.8 | 16.8
1705.2 | 5.2 | 72.2 | 28.88 | 33.7591 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 22 | 16.3 | 0.6 |  |  | 15.6 | 15.5 | 16.1 | 15.8 | 15.3 | 15.7 | 16.8
1706.2 | 6.2 | 81.6 | 32.64 | 38.1543 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.4 | 0.5 |  |  | 15.6 | 15.5 | 16.1 | 15.8 | 15.3 | 15.8 | 16.8
1707.2 | 7.2 | 101.2 | 40.48 | 47.3188 | 16.6 | 16.9 | 16.7 | 16.5 | 16.6 | 16.1 | 21.9 | 16.4 | 0.5 |  |  | 15.6 | 15.8 | 17.2 | 15.8 | 16 | 19.2 | 17.6
1708.2 | 8.2 | 123.4 | 49.36 | 57.699 | 16.6 | 16.9 | 16.7 | 16.5 | 16.7 | 16.1 | 22 | 16.4 | 0.5 |  |  | 15.6 | 18.1 | 21.7 | 15.8 | 19.5 | 28.4 | 20.1
1709.2 | 9.2 | 132.1 | 52.84 | 61.7669 | 16.6 | 17 | 16.8 | 16.6 | 19.3 | 16.1 | 22 | 16.4 | 0.5 |  |  | 15.6 | 26.7 | 41.2 | 15.8 | 28.6 | 53.6 | 30
1710.2 | 10.2 | 146.6 | 58.64 | 68.5468 | 16.7 | 17 | 16.8 | 16.7 | 28.8 | 16.1 | 22 | 16.4 | 0.5 |  |  | 15.6 | 39.1 | 59 | 15.9 | 43.9 | 83.3 | 42.5
1711.2 | 11.2 | 190 | 76 | 88.8396 | 16.9 | 17.2 | 16.9 | 16.7 | 36.4 | 16.1 | 22 | 16.4 | 0.4 |  |  | 15.6 | 52.1 | 84.1 | 16 | 64.7 | 111.6 | 55.8
1712.2 | 12.2 | 223.3 | 89.32 | 104.4099 | 17.3 | 17.8 | 17 | 17.2 | 46.2 | 16.2 | 22 | 16.4 | 0.4 |  |  | 15.6 | 65.1 | 112.1 | 16.3 | 80.1 | 152.5 | 65.3
1713.2 | 13.2 | 222.1 | 88.84 | 103.8488 | 17.6 | 18.8 | 18.5 | 18.8 | 57.1 | 16.2 | 21.9 | 16.4 | 0.6 |  |  | 15.8 | 77.1 | 143.9 | 16.8 | 96.4 | 211.7 | 85.2
1714.2 | 14.2 | 200.2 | 80.08 | 93.6089 | 18 | 19.6 | 21.1 | 20.5 | 64.8 | 16.2 | 21.9 | 16.4 | 0.6 |  |  | 16 | 104.8 | 173.1 | 17.6 | 125.5 | 244.2 | 99.8
1715.2 | 15.2 | 184.9 | 73.96 | 86.455 | 18.5 | 20.4 | 23.5 | 23.3 | 72 | 16.2 | 21.9 | 16.4 | 0.9 |  |  | 16.4 | 128.3 | 204.9 | 18.7 | 145.9 | 265.4 | 108.4
1716.2 | 16.2 | 181.9 | 72.76 | 85.0522 | 19.1 | 21.2 | 25.6 | 26.4 | 80.2 | 16.2 | 21.9 | 16.4 | 1.2 |  |  | 16.9 | 151.3 | 240 | 20.2 | 164.3 | 277.9 | 111.9
1717.2 | 17.2 | 181.9 | 72.76 | 85.0522 | 20.4 | 22.2 | 27.4 | 28.5 | 85.7 | 16.2 | 21.9 | 16.4 | 1.2 |  |  | 17.7 | 169.2 | 272.5 | 22 | 178.7 | 294.7 | 119.1
1718.2 | 18.2 | 182.8 | 73.12 | 85.4731 | 22.5 | 24.2 | 30.3 | 31.3 | 95.7 | 16.2 | 21.9 | 16.4 | 1.1 |  |  | 18.6 | 182.6 | 286.4 | 24.1 | 197.7 | 320.7 | 121.4
1719.2 | 19.2 | 182.1 | 72.84 | 85.1458 | 23.9 | 27 | 33.4 | 34.2 | 105.8 | 16.3 | 21.9 | 16.4 | 0.9 |  |  | 19.8 | 206.2 | 292.7 | 26.2 | 215.1 | 324.7 | 126.4
1720.2 | 20.2 | 181.1 | 72.44 | 84.6782 | 25.3 | 29.5 | 36.4 | 37.1 | 112.1 | 16.3 | 22 | 16.4 | 0.9 |  |  | 21.1 | 219.6 | 298.7 | 28.6 | 228.3 | 336.6 | 132.4
1721.2 | 21.2 | 179 | 71.6 | 83.6963 | 27.2 | 31.7 | 39.9 | 40.5 | 114.8 | 16.3 | 21.9 | 16.4 | 1 |  |  | 22.6 | 228.9 | 303.7 | 31.1 | 238.2 | 345.4 | 134.5
1722.2 | 22.2 | 176.8 | 70.72 | 82.6676 | 29.5 | 33.6 | 42.9 | 43.5 | 115.1 | 16.3 | 21.9 | 16.4 | 1.1 |  |  | 24.2 | 239.1 | 309.7 | 33.7 | 247.1 | 351.4 | 127.7
1723.2 | 23.2 | 173.8 | 69.52 | 81.2649 | 31.9 | 36.1 | 45.5 | 47 | 116.6 | 16.3 | 21.9 | 16.4 | 1.6 |  |  | 26 | 252.7 | 305.4 | 36.3 | 257.5 | 354.1 | 122.2
1724.2 | 24.2 | 171.9 | 68.76 | 80.3765 | 34.2 | 39.2 | 47.6 | 49.8 | 122.7 | 16.3 | 21.9 | 16.4 | 1.9 |  |  | 27.9 | 266.1 | 301.5 | 39 | 268.8 | 353.8 | 119.2
1725.2 | 25.2 | 169.9 | 67.96 | 79.4413 | 36.3 | 42.3 | 49.9 | 52.5 | 127.7 | 16.3 | 21.9 | 16.4 | 1.7 |  |  | 29.8 | 273.9 | 299.5 | 41.7 | 278.5 | 353.9 | 119
1726.2 | 26.2 | 168.2 | 67.28 | 78.6464 | 38.3 | 44.9 | 52.7 | 55.1 | 130.1 | 16.3 | 21.9 | 16.4 | 1.9 |  |  | 31.8 | 283.6 | 302.7 | 44.4 | 286.6 | 346.6 | 117.9
1727.2 | 27.2 | 168 | 67.2 | 78.5529 | 40.5 | 47.2 | 55.4 | 57.2 | 132.5 | 16.3 | 21.9 | 16.4 | 1.7 |  |  | 33.8 | 293.5 | 301.2 | 47 | 293.3 | 342.2 | 118.4
1728.2 | 28.2 | 165.4 | 66.16 | 77.3372 | 42.8 | 50.5 | 58.5 | 60 | 133.4 | 16.3 | 21.9 | 16.4 | 1.9 |  |  | 35.8 | 298.5 | 308.1 | 49.6 | 291.3 | 338.6 | 121.5
1729.2 | 29.2 | 163.8 | 65.52 | 76.5891 | 45.3 | 53.5 | 61.3 | 62.6 | 133.8 | 16.3 | 21.9 | 16.4 | 1.8 |  |  | 37.8 | 298.6 | 314 | 52.1 | 287.3 | 331.4 | 123.2
1730.2 | 30.2 | 162.6 | 65.04 | 76.028 | 47.9 | 55.7 | 63.8 | 64.8 | 134.2 | 16.3 | 21.9 | 16.4 | 2 |  |  | 39.8 | 301.9 | 311.8 | 54.5 | 290.3 | 328.5 | 121.2
1731.2 | 31.2 | 161.4 | 64.56 | 75.4669 | 49.2 | 57.5 | 66.6 | 66.8 | 135.6 | 16.3 | 21.9 | 16.5 | 2.2 |  |  | 41.8 | 310.7 | 317.6 | 56.8 | 296.2 | 337.9 | 123.2
1732.2 | 32.2 | 160.7 | 64.28 | 75.1396 | 50.5 | 59.6 | 68.8 | 69 | 137.8 | 16.3 | 21.9 | 16.6 | 2.2 |  |  | 43.8 | 312.3 | 322 | 59 | 294.3 | 337.6 | 128.9
1733.2 | 33.2 | 159.5 | 63.8 | 74.5785 | 52.9 | 61.9 | 70.7 | 71.1 | 139.2 | 16.3 | 21.9 | 16.9 | 1.7 |  |  | 45.8 | 316.7 | 334.3 | 61.1 | 298.7 | 344.8 | 134.9
1734.2 | 34.2 | 159.6 | 63.84 | 74.6253 | 55.3 | 64.5 | 72.8 | 73 | 142.1 | 16.4 | 21.9 | 17.1 | 1.3 |  |  | 47.8 | 316.9 | 335.3 | 63.1 | 296.8 | 343.9 | 135.7
1735.2 | 35.2 | 158.7 | 63.48 | 74.2045 | 56.7 | 67.2 | 74.7 | 74.7 | 141.5 | 16.4 | 21.9 | 17.5 | 1.3 |  |  | 49.8 | 317.4 | 334.8 | 65.1 | 295.4 | 346.4 | 140.4
1736.2 | 36.2 | 157.5 | 63 | 73.6434 | 58.5 | 69.3 | 76.5 | 77 | 141.3 | 16.4 | 21.9 | 17.9 | 1.3 |  |  | 51.9 | 315.5 | 331.6 | 67 | 291.8 | 338 | 141.4
1737.2 | 37.2 | 157.4 | 62.96 | 73.5966 | 59.9 | 71.3 | 77.9 | 79.3 | 140.7 | 16.4 | 21.9 | 18.4 | 1.4 |  |  | 53.9 | 317.5 | 340.9 | 68.9 | 295.2 | 341 | 143.2
1738.2 | 38.2 | 156.3 | 62.52 | 73.0823 | 61.5 | 73.4 | 79 | 81 | 143.7 | 16.4 | 21.9 | 18.9 | 1.7 |  |  | 56 | 319.6 | 348.1 | 70.7 | 300.6 | 350 | 146.3
1739.2 | 39.2 | 154.6 | 61.84 | 72.2874 | 63 | 75.5 | 80.8 | 82.1 | 146.1 | 16.4 | 21.9 | 19.2 | 1.4 |  |  | 58.1 | 325.8 | 353.7 | 72.5 | 309.8 | 364.6 | 151
1740.2 | 40.2 | 153.5 | 61.4 | 71.7731 | 65.1 | 77.3 | 82.4 | 83.3 | 151.5 | 16.4 | 21.9 | 19.6 | 1.3 |  |  | 60.1 | 330.7 | 353.8 | 74.2 | 315.1 | 368.5 | 155.4
1741.2 | 41.2 | 153.4 | 61.36 | 71.7263 | 66.8 | 78.6 | 83.6 | 84.4 | 155.1 | 16.4 | 21.9 | 19.9 | 1.1 |  |  | 62.1 | 332.6 | 351.3 | 75.9 | 312.5 | 355.6 | 156.2
1742.2 | 42.2 | 152.5 | 61 | 71.3055 | 69.2 | 79.5 | 85.6 | 85.6 | 154.5 | 16.4 | 21.9 | 20.2 | 1.2 |  |  | 64.1 | 331.1 | 347.8 | 77.6 | 308.9 | 342.5 | 149.9
1743.2 | 43.2 | 151.8 | 60.72 | 70.9782 | 71.2 | 80.6 | 87.3 | 87 | 155.1 | 16.4 | 21.9 | 20.5 | 1.1 |  |  | 66.1 | 327 | 344.6 | 79.3 | 301.6 | 330.8 | 147
1744.2 | 44.2 | 149.6 | 59.84 | 69.9495 | 73.4 | 81.5 | 88.7 | 88.6 | 153.3 | 16.4 | 21.9 | 20.8 | 1 |  |  | 68.2 | 327.4 | 341.4 | 81 | 300.1 | 329.8 | 151.3
1745.2 | 45.2 | 150 | 60 | 70.1365 | 74.2 | 82.4 | 89.9 | 90.2 | 153.2 | 16.5 | 21.9 | 21 | 0.9 |  |  | 70.2 | 321.6 | 339.5 | 82.6 | 293.5 | 319.6 | 149
1746.2 | 46.2 | 149.8 | 59.92 | 70.043 | 74.9 | 84 | 91.2 | 91.1 | 152.2 | 16.5 | 21.9 | 21.3 | 0.9 |  |  | 72.1 | 324.1 | 336.9 | 84.2 | 295.4 | 311.8 | 147.3
1747.2 | 47.2 | 149.4 | 59.76 | 69.856 | 76.2 | 85.4 | 92.7 | 91.8 | 151.5 | 16.5 | 21.9 | 21.5 | 0.6 |  |  | 74.1 | 318.6 | 331.1 | 85.6 | 287.5 | 300.8 | 145.2
1748.2 | 48.2 | 149.6 | 59.84 | 69.9495 | 77.5 | 86.4 | 93.9 | 92.4 | 149.1 | 16.6 | 21.9 | 21.6 | 0.5 |  |  | 76 | 310.2 | 328.2 | 87 | 277.8 | 294 | 144.6
1749.2 | 49.2 | 149 | 59.6 | 69.669 | 78.8 | 87.6 | 95 | 93.1 | 147.5 | 16.6 | 21.9 | 21.8 | 0.6 |  |  | 78 | 308.9 | 326.8 | 88.3 | 274.1 | 290.2 | 146.3
1750.2 | 50.2 | 146.1 | 58.44 | 68.313 | 79.8 | 88.3 | 96.4 | 93.9 | 147.3 | 16.6 | 21.9 | 21.9 | 0.6 |  |  | 79.9 | 310.5 | 340.3 | 89.4 | 275.1 | 296.5 | 155.9
1751.2 | 51.2 | 145.6 | 58.24 | 68.0792 | 81.1 | 89.2 | 97.5 | 94.8 | 149.1 | 16.7 | 21.9 | 22.1 | 0.7 |  |  | 81.8 | 313 | 344 | 90.5 | 275.5 | 304.6 | 167.3
1752.2 | 52.2 | 146 | 58.4 | 68.2662 | 82.4 | 90.3 | 98.5 | 95.5 | 151.3 | 16.8 | 21.9 | 22.3 | 0.9 |  |  | 83.6 | 322.1 | 351.4 | 91.4 | 282.6 | 302.4 | 167
1753.2 | 53.2 | 145.4 | 58.16 | 67.9857 | 83.5 | 91.8 | 99.7 | 96.2 | 152.6 | 17 | 21.9 | 22.5 | 1.1 |  |  | 85.5 | 319.9 | 346.6 | 92.3 | 278.7 | 295.6 | 167.1
1754.2 | 54.2 | 144.7 | 57.88 | 67.6584 | 84.5 | 93 | 100.6 | 97 | 152.7 | 17.1 | 21.9 | 22.7 | 1.2 |  |  | 87.3 | 319.1 | 341.7 | 93.2 | 275.6 | 289.9 | 163.4
1755.2 | 55.2 | 144.7 | 57.88 | 67.6584 | 85.1 | 93.8 | 101 | 98.3 | 152 | 17.2 | 21.9 | 23 | 1.2 |  |  | 89.1 | 318.1 | 353.6 | 93.9 | 274.3 | 296.2 | 168.4
1756.2 | 56.2 | 145 | 58 | 67.7987 | 85.3 | 94.8 | 101.6 | 99.3 | 149.9 | 17.3 | 21.9 | 23.2 | 1.2 |  |  | 90.9 | 311.9 | 353.1 | 94.4 | 271.7 | 304.5 | 175.1
1757.2 | 57.2 | 144.2 | 57.68 | 67.4246 | 85.9 | 95.1 | 101.6 | 99.8 | 149.2 | 17.4 | 21.9 | 23.5 | 1 |  |  | 92.6 | 305.6 | 356.1 | 94.1 | 268.6 | 308 | 178.9
1758.2 | 58.2 | 142.5 | 57 | 66.6297 | 85.8 | 95.5 | 101.7 | 100.3 | 148.6 | 17.5 | 21.9 | 23.7 | 1 |  |  | 94.4 | 300.8 | 365.3 | 94.1 | 267.6 | 312.8 | 185.1
1759.2 | 59.2 | 142.7 | 57.08 | 66.7232 | 86.1 | 96.1 | 102 | 101 | 148 | 17.6 | 21.9 | 23.9 | 1 |  |  | 96.2 | 296.4 | 369.4 | 94.2 | 264.4 | 310 | 191.2
1760.2 | 60.2 | 142.5 | 57 | 66.6297 | 87 | 96 | 101.9 | 101.4 | 148.7 | 17.6 | 21.9 | 23.9 | 1.3 |  |  | 97.9 | 298.4 | 376.2 | 94.4 | 264 | 308 | 192.5
1761.2 | 61.2 | 142.3 | 56.92 | 66.5362 | 87.4 | 96.3 | 102 | 102.2 | 151.4 | 17.7 | 21.9 | 24 | 1.2 |  |  | 99.6 | 300.3 | 381.2 | 94.7 | 265.3 | 327.7 | 199.4
1762.2 | 62.2 | 142.4 | 56.96 | 66.583 | 88.1 | 96.8 | 102 | 103.3 | 152.9 | 17.7 | 21.9 | 24.2 | 1 |  |  | 101.3 | 300.6 | 400.9 | 95 | 266.6 | 329.4 | 204.1
1763.2 | 63.2 | 141.2 | 56.48 | 66.0219 | 89.6 | 97.3 | 101.4 | 104 | 156.1 | 17.8 | 21.9 | 24.3 | 1.1 |  |  | 103 | 304 | 409.8 | 95.4 | 268.3 | 323.7 | 202.7
1764.2 | 64.2 | 141 | 56.4 | 65.9284 | 90.5 | 97.9 | 101.2 | 104.5 | 154.9 | 17.9 | 21.9 | 24.4 | 1.2 |  |  | 104.6 | 299.7 | 407.7 | 95.8 | 264.8 | 319.4 | 200.2
1765.2 | 65.2 | 141.1 | 56.44 | 65.9751 | 89.5 | 98.2 | 101.1 | 105 | 155.7 | 17.9 | 21.9 | 24.6 | 1.4 |  |  | 106.3 | 299.4 | 401.3 | 96.1 | 263.6 | 316.3 | 196.5
1766.2 | 66.2 | 141.5 | 56.6 | 66.1621 | 89.2 | 98.2 | 101.3 | 105.6 | 156.2 | 17.9 | 21.9 | 24.9 | 1.3 |  |  | 108 | 291.8 | 397 | 96.3 | 258.5 | 321.1 | 197.7
1767.2 | 67.2 | 140.3 | 56.12 | 65.601 | 89.5 | 98.6 | 101.8 | 106.2 | 155.2 | 18 | 21.9 | 25 | 1 |  |  | 109.7 | 285.2 | 403.5 | 96.2 | 255.9 | 322.3 | 203.2
1768.2 | 68.2 | 141.2 | 56.48 | 66.0219 | 89.1 | 99.1 | 102.1 | 106.6 | 155.7 | 18 | 21.9 | 25.1 | 0.6 |  |  | 111.4 | 277 | 401.9 | 96.2 | 250.6 | 311.2 | 203.5
1769.2 | 69.2 | 141.1 | 56.44 | 65.9751 | 88.8 | 100.1 | 102.4 | 107 | 156.3 | 17.9 | 21.9 | 25.1 | 0.4 |  |  | 113.1 | 277 | 394.7 | 96.4 | 250.4 | 306.3 | 202.3
1770.2 | 70.2 | 142.6 | 57.04 | 66.6765 | 89.7 | 100.7 | 102.8 | 107.2 | 156.8 | 17.8 | 21.9 | 25.1 | 0.4 |  |  | 114.7 | 275.7 | 394.6 | 96.7 | 250.7 | 311.5 | 205.1
1771.2 | 71.2 | 140 | 56 | 65.4608 | 90.6 | 100.8 | 103.4 | 107.1 | 156.5 | 17.8 | 21.9 | 25.1 | 0.5 |  |  | 116.3 | 272.3 | 391.1 | 97.2 | 248.6 | 313.5 | 208.7
1772.2 | 72.2 | 140 | 56 | 65.4608 | 91 | 100.9 | 103.7 | 107.1 | 154.8 | 17.8 | 21.9 | 25.1 | 0.6 |  |  | 117.9 | 271.4 | 389.9 | 97.7 | 248.9 | 327.6 | 214
1773.2 | 73.2 | 139.5 | 55.8 | 65.227 | 91.4 | 101.3 | 103.8 | 107 | 152.2 | 17.8 | 21.9 | 25.2 | 0.8 |  |  | 119.5 | 268.7 | 380.8 | 98.7 | 250.7 | 340.9 | 217.2
1774.2 | 74.2 | 140.7 | 56.28 | 65.7881 | 91.2 | 101.8 | 104.3 | 107.3 | 150 | 17.8 | 21.9 | 25.5 | 1.3 |  |  | 121 | 265.9 | 380.9 | 99.8 | 250.4 | 344.7 | 220.1
1775.2 | 75.2 | 142 | 56.8 | 66.3959 | 90 | 101.8 | 105.1 | 107.8 | 150.3 | 17.8 | 21.9 | 25.6 | 1.6 |  |  | 122.5 | 264.6 | 385.1 | 100.6 | 253.5 | 349.9 | 224.3
1776.2 | 76.2 | 142.2 | 56.88 | 66.4894 | 89.2 | 101.6 | 105.8 | 108.1 | 152.6 | 17.8 | 21.9 | 25.7 | 2 |  |  | 123.9 | 270.7 | 383.7 | 101.4 | 257.1 | 352.4 | 227
1777.2 | 77.2 | 141.6 | 56.64 | 66.2089 | 89.7 | 101.6 | 105.9 | 108.4 | 151.5 | 17.8 | 21.9 | 25.9 | 2.1 |  |  | 125.3 | 274.7 | 388.4 | 102.2 | 257 | 348.7 | 225.3
1778.2 | 78.2 | 141.5 | 56.6 | 66.1621 | 90 | 101.8 | 105.8 | 108.8 | 149.9 | 17.8 | 21.9 | 26 | 2.4 |  |  | 126.6 | 274.4 | 386.4 | 103 | 256.6 | 345.5 | 224.1
1779.2 | 79.2 | 140.4 | 56.16 | 65.6478 | 90.4 | 101.5 | 105.8 | 108.9 | 149.1 | 17.8 | 21.9 | 26.1 | 2.4 |  |  | 127.9 | 279.3 | 390.7 | 103.8 | 263.2 | 355.4 | 228.5
1780.2 | 80.2 | 141.1 | 56.44 | 65.9751 | 90.4 | 101.5 | 105.6 | 108.9 | 151.5 | 17.8 | 21.9 | 26.2 | 2.8 |  |  | 129.2 | 286.5 | 392.6 | 104.7 | 268.9 | 350.1 | 228.3
1781.2 | 81.2 | 141 | 56.4 | 65.9284 | 90.9 | 102.1 | 105.6 | 108.9 | 152.3 | 17.8 | 21.9 | 26.2 | 2.5 |  |  | 130.4 | 292.7 | 397.2 | 105.6 | 274.3 | 349.4 | 229.6
1782.2 | 82.2 | 141.6 | 56.64 | 66.2089 | 91.6 | 102.5 | 105.8 | 109.1 | 153.6 | 17.8 | 21.9 | 26.3 | 2.3 |  |  | 131.6 | 301.8 | 394.2 | 106.4 | 283 | 361.9 | 231.5
1783.2 | 83.2 | 141.3 | 56.52 | 66.0686 | 91.1 | 102.3 | 106 | 109.5 | 158.1 | 17.8 | 21.9 | 26.4 | 2.3 |  |  | 132.8 | 313 | 393.8 | 107.2 | 290.4 | 364.1 | 233.4
1784.2 | 84.2 | 139 | 55.6 | 64.9932 | 90.5 | 102.4 | 106.1 | 109.7 | 161.3 | 17.8 | 21.9 | 26.3 | 2.3 |  |  | 134 | 324.9 | 384.8 | 108 | 297.1 | 358.8 | 228.6
1785.2 | 85.2 | 139.3 | 55.72 | 65.1335 | 90.9 | 102.7 | 106.1 | 109.7 | 161.2 | 17.8 | 21.9 | 26.3 | 2.3 |  |  | 135.2 | 325.8 | 379.8 | 108.8 | 297.9 | 351.8 | 224.9
1786.2 | 86.2 | 139.3 | 55.72 | 65.1335 | 91.8 | 103.4 | 106.4 | 109.8 | 158.9 | 17.8 | 21.9 | 26.3 | 2.6 |  |  | 136.4 | 322.9 | 376.3 | 109.6 | 296.1 | 356.3 | 224.4
1787.2 | 87.2 | 138.4 | 55.36 | 64.7127 | 92 | 103.7 | 106.4 | 110 | 156.6 | 17.8 | 21.8 | 26.3 | 2.5 |  |  | 137.6 | 318.5 | 367.6 | 110.3 | 293.1 | 350.8 | 223.8
1788.2 | 88.2 | 140.7 | 56.28 | 65.7881 | 92.4 | 103.1 | 106.2 | 110 | 157.3 | 17.8 | 21.8 | 26.4 | 2.2 |  |  | 138.9 | 323.7 | 360.7 | 111.1 | 295.7 | 350.2 | 223.3
1789.2 | 89.2 | 139.8 | 55.92 | 65.3673 | 92.2 | 103.1 | 106.4 | 110.2 | 159.5 | 17.8 | 21.9 | 26.4 | 1.9 |  |  | 140.2 | 320 | 355.1 | 111.9 | 294.6 | 350.6 | 225.3
1790.2 | 90.2 | 138.2 | 55.28 | 64.6191 | 91.7 | 102.9 | 106.3 | 110.4 | 159.8 | 17.8 | 21.8 | 26.4 | 2.1 |  |  | 141.4 | 322.4 | 352.9 | 112.6 | 293.7 | 342.9 | 226.4
1791.2 | 91.2 | 140.3 | 56.12 | 65.601 | 91.2 | 103 | 106.6 | 110.2 | 160.1 | 17.8 | 21.8 | 26.4 | 2.3 |  |  | 142.7 | 320.6 | 348.8 | 113.4 | 292.5 | 339 | 223.8
1792.2 | 92.2 | 139.2 | 55.68 | 65.0867 | 90.9 | 102.6 | 106.8 | 110.1 | 160.4 | 17.8 | 21.8 | 26.5 | 2.1 |  |  | 143.9 | 319.8 | 346.3 | 114.2 | 296.6 | 341 | 223.2
1793.2 | 93.2 | 138.1 | 55.24 | 64.5724 | 91.6 | 102.3 | 106.9 | 110.3 | 161.3 | 17.8 | 21.8 | 26.6 | 1.9 |  |  | 145 | 318 | 338.9 | 115 | 298.9 | 342.4 | 223.4
1794.2 | 94.2 | 138.8 | 55.52 | 64.8997 | 91.8 | 101.9 | 107.1 | 110 | 159.8 | 17.8 | 21.8 | 26.7 | 1.7 |  |  | 146.1 | 312.9 | 327.5 | 115.7 | 298.5 | 337.4 | 221.7
1795.2 | 95.2 | 137.7 | 55.08 | 64.3853 | 91.8 | 102 | 107.2 | 110.2 | 157.6 | 17.8 | 21.8 | 26.7 | 1.8 |  |  | 147.2 | 309.1 | 322.2 | 116.5 | 296.7 | 325.5 | 220.4
1796.2 | 96.2 | 138.7 | 55.48 | 64.8529 | 91.5 | 101.7 | 107.4 | 110.5 | 156.3 | 17.7 | 21.8 | 26.9 | 1.7 |  |  | 148.3 | 306.9 | 318.5 | 117.2 | 296.8 | 325.1 | 221.3
1797.2 | 97.2 | 139.1 | 55.64 | 65.04 | 91.3 | 100.6 | 107.8 | 110.5 | 156.4 | 17.7 | 21.8 | 27 | 1.9 |  |  | 149.3 | 307.1 | 314.4 | 117.9 | 299.1 | 320.1 | 224.5
1798.2 | 98.2 | 139.1 | 55.64 | 65.04 | 91.9 | 99.3 | 107.8 | 110.4 | 155.7 | 17.7 | 21.8 | 27.1 | 1.7 |  |  | 150.3 | 311.3 | 312.2 | 118.6 | 304.9 | 326.6 | 227.9
1799.2 | 99.2 | 136.9 | 54.76 | 64.0113 | 91.9 | 98.9 | 107.8 | 110.2 | 156.7 | 17.7 | 21.8 | 27.1 | 1.8 |  |  | 151.1 | 323.3 | 305.5 | 119.3 | 318.3 | 332.6 | 227.8
1800.2 | 100.2 | 138 | 55.2 | 64.5256 | 92.3 | 99.2 | 107.8 | 110.4 | 159.6 | 17.7 | 21.8 | 27.2 | 1.7 |  |  | 152 | 327.5 | 296.7 | 119.9 | 318.1 | 328.2 | 223
1801.2 | 101.2 | 138.6 | 55.44 | 64.8062 | 92.5 | 99.7 | 107.7 | 110.7 | 158.6 | 17.7 | 21.8 | 27.1 | 1.2 |  |  | 152.7 | 333 | 294 | 120.6 | 320.9 | 328.3 | 224
1802.2 | 102.2 | 138.1 | 55.24 | 64.5724 | 92.8 | 100.1 | 107.8 | 110.6 | 159.1 | 17.7 | 21.8 | 27.1 | 1.2 |  |  | 153.4 | 334.5 | 293.3 | 121.3 | 322.4 | 325.9 | 223.5
1803.2 | 103.2 | 141.7 | 56.68 | 66.2557 | 92.7 | 100.3 | 108 | 110.6 | 157.1 | 17.7 | 21.8 | 27.2 | 1.4 |  |  | 154.1 | 336.8 | 293.2 | 121.9 | 326 | 325.7 | 223.2
1804.2 | 104.2 | 139.4 | 55.76 | 65.1802 | 92.5 | 100 | 108.2 | 110.6 | 157.4 | 17.6 | 21.8 | 27.2 | 1.2 |  |  | 154.8 | 333.5 | 288.2 | 122.6 | 321.9 | 320 | 220.1
1805.2 | 105.2 | 138.5 | 55.4 | 64.7594 | 91.9 | 100.3 | 108.5 | 110.5 | 157.2 | 17.6 | 21.8 | 27.3 | 1 |  |  | 155.4 | 333.6 | 283.2 | 123.3 | 322.9 | 316.4 | 219.1
1806.2 | 106.2 | 139.2 | 55.68 | 65.0867 | 92.2 | 100.2 | 108.8 | 110.5 | 157.5 | 17.7 | 21.8 | 27.4 | 1 |  |  | 155.9 | 330.6 | 277.6 | 124 | 319.3 | 309.6 | 218
1807.2 | 107.2 | 139 | 55.6 | 64.9932 | 92.1 | 100.1 | 109.2 | 110.5 | 155.8 | 17.7 | 21.8 | 27.4 | 0.9 |  |  | 156.5 | 323 | 270.7 | 124.7 | 312 | 303.3 | 216.7
1808.2 | 108.2 | 141.2 | 56.48 | 66.0219 | 92 | 100.2 | 109.6 | 110.7 | 153.4 | 17.8 | 21.8 | 27.5 | 1.2 |  |  | 157 | 317.7 | 268 | 125.4 | 308.5 | 292.5 | 215.2
1809.2 | 109.2 | 137 | 54.8 | 64.058 | 91.5 | 100.3 | 109.5 | 110.6 | 151 | 17.8 | 21.8 | 27.6 | 1.6 |  |  | 157.5 | 316.3 | 262.5 | 126 | 305.6 | 286.9 | 214.3
1810.2 | 110.2 | 139.8 | 55.92 | 65.3673 | 90.9 | 100.1 | 109.5 | 110.4 | 149.6 | 17.8 | 21.8 | 27.6 | 1.6 |  |  | 158 | 312.6 | 265.1 | 126.6 | 305.3 | 290.6 | 218.2
1811.2 | 111.2 | 135.9 | 54.36 | 63.5437 | 90.6 | 99.4 | 109.6 | 110.4 | 150 | 17.8 | 21.8 | 27.6 | 1.5 |  |  | 158.4 | 308.4 | 262.9 | 127.1 | 301.2 | 286.6 | 219.4
1812.2 | 112.2 | 139.4 | 55.76 | 65.1802 | 91.1 | 99.6 | 109.7 | 110.3 | 148.6 | 17.8 | 21.8 | 27.5 | 1.5 |  |  | 158.8 | 308.8 | 259.2 | 127.6 | 300.8 | 283.8 | 217.3
1813.2 | 113.2 | 139.1 | 55.64 | 65.04 | 91.7 | 99.3 | 109.6 | 110.3 | 147.6 | 17.8 | 21.8 | 27.5 | 1.3 |  |  | 159.1 | 311.7 | 265.1 | 128.1 | 297.6 | 282.1 | 216.3
1814.2 | 114.2 | 138.4 | 55.36 | 64.7127 | 92.2 | 99.5 | 109.5 | 110.4 | 145.7 | 17.8 | 21.8 | 27.5 | 1 |  |  | 159.4 | 312.9 | 277.9 | 128.6 | 299.1 | 293.4 | 224.1
1815.2 | 115.2 | 134.2 | 53.68 | 62.7488 | 91.7 | 99.9 | 109.4 | 110.2 | 146.3 | 17.8 | 21.8 | 27.5 | 0.9 |  |  | 159.7 | 310.8 | 280.5 | 129 | 297.6 | 296.9 | 226.2
1816.2 | 116.2 | 138 | 55.2 | 64.5256 | 90.8 | 100.1 | 109.5 | 110.3 | 148 | 17.8 | 21.8 | 27.4 | 0.8 |  |  | 159.9 | 307.9 | 284 | 129.4 | 294.4 | 294.9 | 224.6
1817.2 | 117.2 | 135.3 | 54.12 | 63.2632 | 90.1 | 100.9 | 109.6 | 110.5 | 148.9 | 17.9 | 21.8 | 27.4 | 0.8 |  |  | 160.2 | 305.4 | 280.2 | 129.8 | 290.9 | 290 | 222.1
1818.2 | 118.2 | 136.5 | 54.6 | 63.8243 | 90.7 | 101.4 | 109.8 | 110.6 | 149.6 | 17.9 | 21.8 | 27.4 | 1 |  |  | 160.5 | 308.1 | 277.7 | 130.3 | 294.9 | 290.3 | 221.3
1819.2 | 119.2 | 138.8 | 55.52 | 64.8997 | 91.5 | 101.3 | 109.8 | 110.5 | 151.6 | 17.9 | 21.8 | 27.6 | 1.3 |  |  | 160.8 | 310.9 | 277.5 | 130.7 | 299.4 | 293.5 | 221.7
1820.2 | 120.2 | 139.1 | 55.64 | 65.04 | 91.6 | 101.3 | 109.7 | 110.5 | 152 | 17.9 | 21.8 | 27.6 | 1.4 |  |  | 161.1 | 315.7 | 284.7 | 131.2 | 306.2 | 298.2 | 223.6
1821.2 | 121.2 | 138.2 | 55.28 | 64.6191 | 91.7 | 101.7 | 109.6 | 110.3 | 152 | 18 | 21.8 | 27.6 | 1.8 |  |  | 161.4 | 317 | 291.8 | 131.6 | 304.8 | 299.7 | 226.9
1822.2 | 122.2 | 138.8 | 55.52 | 64.8997 | 92 | 102 | 109.5 | 110.3 | 152.5 | 18 | 21.8 | 27.7 | 1.9 |  |  | 161.7 | 318.5 | 297 | 132 | 304.7 | 302.7 | 227.7
1823.2 | 123.2 | 136.1 | 54.44 | 63.6372 | 92.5 | 102.3 | 109.4 | 110.4 | 152.9 | 18 | 21.8 | 27.7 | 2 |  |  | 162 | 319.2 | 296.6 | 132.5 | 300.8 | 305 | 228.1
1824.2 | 124.2 | 137.8 | 55.12 | 64.4321 | 92.6 | 102.3 | 109.5 | 110.7 | 152.3 | 18 | 21.8 | 27.8 | 1.8 |  |  | 162.4 | 318.7 | 303.2 | 132.9 | 302 | 314.3 | 230.8
1825.2 | 125.2 | 134.6 | 53.84 | 62.9359 | 92.9 | 102.6 | 109.7 | 110.9 | 152.3 | 18 | 21.8 | 27.9 | 2.2 |  |  | 162.7 | 322.4 | 308.1 | 133.2 | 304.9 | 319.1 | 232.1
1826.2 | 126.2 | 139.1 | 55.64 | 65.04 | 93.7 | 102.6 | 110.2 | 110.9 | 153 | 18 | 21.8 | 27.9 | 1.7 |  |  | 163.1 | 320.1 | 305.8 | 133.6 | 300.4 | 311.9 | 230.9
1827.2 | 127.2 | 138.8 | 55.52 | 64.8997 | 94.1 | 103 | 110.5 | 110.8 | 151.2 | 18 | 21.8 | 27.8 | 1.5 |  |  | 163.5 | 316.3 | 303.5 | 134 | 295.5 | 307.3 | 229.8
1828.2 | 128.2 | 139 | 55.6 | 64.9932 | 94.5 | 102.8 | 110.7 | 111.1 | 149.4 | 18 | 21.8 | 27.8 | 1.6 |  |  | 163.9 | 313.9 | 299.9 | 134.5 | 291.9 | 308.1 | 229.4
1829.2 | 129.2 | 137.6 | 55.04 | 64.3386 | 94.3 | 102.3 | 110.7 | 111.4 | 148.7 | 17.9 | 21.8 | 27.8 | 2 |  |  | 164.3 | 317.5 | 300.4 | 135 | 297.9 | 313.1 | 233.3
1830.2 | 130.2 | 137.7 | 55.08 | 64.3853 | 93.6 | 102.5 | 110.6 | 111.4 | 150.4 | 17.9 | 21.8 | 27.9 | 2.3 |  |  | 164.8 | 320.5 | 304.5 | 135.5 | 303.6 | 317.7 | 237.2
1831.2 | 131.2 | 140.7 | 56.28 | 65.7881 | 93.8 | 102.7 | 110.7 | 111.2 | 153 | 17.9 | 21.8 | 28 | 2.6 |  |  | 165.2 | 317.6 | 302.7 | 135.9 | 300.8 | 319.9 | 240.8
1832.2 | 132.2 | 138.4 | 55.36 | 64.7127 | 93.5 | 103 | 110.5 | 111.3 | 152.2 | 17.9 | 21.8 | 28 | 1.9 |  |  | 165.6 | 312.2 | 301.2 | 136.4 | 293.7 | 314.2 | 239.5
1833.2 | 133.2 | 139.2 | 55.68 | 65.0867 | 94.4 | 103.1 | 110.4 | 111.5 | 150.2 | 17.8 | 21.8 | 28 | 1.6 |  |  | 165.9 | 307.6 | 296.6 | 136.9 | 289.3 | 312.6 | 234.6
1834.2 | 134.2 | 140.3 | 56.12 | 65.601 | 94.4 | 103.1 | 110 | 111 | 150 | 17.8 | 21.8 | 28 | 1.6 |  |  | 166.3 | 305.7 | 305 | 137.4 | 286.6 | 312.2 | 236.6
1835.2 | 135.2 | 140 | 56 | 65.4608 | 93.4 | 103 | 109 | 111 | 152.4 | 17.8 | 21.8 | 28 | 1.8 |  |  | 166.7 | 307.6 | 312 | 137.9 | 290.5 | 318.2 | 243.4
1836.2 | 136.2 | 137.8 | 55.12 | 64.4321 | 93.4 | 102.9 | 108.1 | 110.8 | 153.3 | 17.8 | 21.8 | 28 | 2.1 |  |  | 167 | 307.2 | 320.5 | 138.4 | 290.8 | 317 | 246.3
1837.2 | 137.2 | 140.8 | 56.32 | 65.8348 | 93.5 | 102.7 | 107.6 | 110.7 | 152.7 | 17.9 | 21.8 | 27.9 | 2.4 |  |  | 167.3 | 311 | 330.3 | 139 | 290 | 325.1 | 256.5
1838.2 | 138.2 | 142.2 | 56.88 | 66.4894 | 93.5 | 103.2 | 107.6 | 110.6 | 153.2 | 17.9 | 21.8 | 28 | 1.8 |  |  | 167.6 | 308 | 330.8 | 139.5 | 286.6 | 325.6 | 259
1839.2 | 139.2 | 143.2 | 57.28 | 66.957 | 93.5 | 103.7 | 107.9 | 110.9 | 151.3 | 18 | 21.8 | 28 | 1.4 |  |  | 167.9 | 305 | 329 | 140 | 283.9 | 323.3 | 253.9
1840.2 | 140.2 | 142.6 | 57.04 | 66.6765 | 94.1 | 104.2 | 108.3 | 111.2 | 149.5 | 18 | 21.8 | 28.1 | 1.4 |  |  | 168.2 | 303.8 | 329.7 | 140.5 | 287.7 | 325.5 | 249.7
1841.2 | 141.2 | 141.6 | 56.64 | 66.2089 | 95 | 104.2 | 108.5 | 111.6 | 150.7 | 18 | 21.8 | 28.2 | 2 |  |  | 168.6 | 305 | 328.6 | 141.2 | 289.5 | 332.6 | 248.2
1842.2 | 142.2 | 140.7 | 56.28 | 65.7881 | 95.1 | 103.8 | 108.6 | 111.6 | 151.3 | 18.1 | 21.8 | 28.3 | 2 |  |  | 168.9 | 305.1 | 334.9 | 141.9 | 287.4 | 334.5 | 249.8
1843.2 | 143.2 | 141.1 | 56.44 | 65.9751 | 94.4 | 103.9 | 108.6 | 111.8 | 152.1 | 18.1 | 21.8 | 28.3 | 1.8 |  |  | 169.3 | 308.6 | 342.6 | 142.5 | 286.6 | 328.6 | 248.5
1844.2 | 144.2 | 141.3 | 56.52 | 66.0686 | 95.3 | 104.1 | 108.3 | 112 | 152.9 | 18.2 | 21.8 | 28.4 | 2 |  |  | 169.7 | 307.2 | 336.9 | 143.2 | 285.4 | 326.9 | 244.8
1845.2 | 145.2 | 140.4 | 56.16 | 65.6478 | 95.6 | 104.8 | 108.5 | 112 | 153.2 | 18.2 | 21.8 | 28.6 | 2.8 |  |  | 170.1 | 308 | 340.8 | 144 | 287.3 | 325.4 | 245.1
1846.2 | 146.2 | 139.9 | 55.96 | 65.414 | 95.5 | 105.3 | 108.2 | 112.1 | 155.9 | 18.2 | 21.8 | 28.7 | 3.8 |  |  | 170.5 | 312.9 | 345.3 | 144.7 | 299.6 | 331.4 | 248.7
1847.2 | 147.2 | 138.5 | 55.4 | 64.7594 | 95.7 | 105.7 | 107.7 | 112.1 | 158.8 | 18.2 | 21.8 | 28.8 | 4.6 |  |  | 171 | 317.1 | 348 | 145.5 | 304.3 | 340.3 | 251.7
1848.2 | 148.2 | 137.4 | 54.96 | 64.2451 | 95.2 | 106 | 107.6 | 112 | 159.5 | 18.2 | 21.8 | 28.9 | 4.2 |  |  | 171.5 | 320.1 | 343.4 | 146.2 | 303.3 | 332.7 | 251
1849.2 | 149.2 | 137.2 | 54.88 | 64.1516 | 94.9 | 106.1 | 107.3 | 112.1 | 159 | 18.3 | 21.8 | 28.9 | 4.8 |  |  | 172 | 324.6 | 345.8 | 147 | 305.2 | 331.6 | 255.1
1850.2 | 150.2 | 140.3 | 56.12 | 65.601 | 95.2 | 106 | 106.5 | 112.3 | 160 | 18.3 | 21.8 | 28.9 | 4.3 |  |  | 172.5 | 326.4 | 340.1 | 147.7 | 305.1 | 323.6 | 254.3
1851.2 | 151.2 | 138.7 | 55.48 | 64.8529 | 95.7 | 106.2 | 106.3 | 112.7 | 160.4 | 18.3 | 21.8 | 29 | 4.3 |  |  | 173 | 322.9 | 349.5 | 148.4 | 301.6 | 325.9 | 258.8
1852.2 | 152.2 | 136.9 | 54.76 | 64.0113 | 95.5 | 106.2 | 106.8 | 113.1 | 159.9 | 18.3 | 21.8 | 29.1 | 3.6 |  |  | 173.5 | 321.4 | 354.4 | 149 | 300.8 | 323.3 | 260.2
1853.2 | 153.2 | 138.7 | 55.48 | 64.8529 | 95.1 | 106.1 | 107.2 | 113.2 | 159.6 | 18.3 | 21.8 | 29 | 3 |  |  | 174 | 319 | 351 | 149.7 | 298.2 | 324 | 257.9
1854.2 | 154.2 | 136.7 | 54.68 | 63.9178 | 95.4 | 105.8 | 107.4 | 113.4 | 159.3 | 18.3 | 21.8 | 29 | 2.8 |  |  | 174.5 | 314.5 | 349.7 | 150.3 | 295.1 | 330.8 | 258.3
1855.2 | 155.2 | 136.4 | 54.56 | 63.7775 | 96.4 | 106.1 | 107.8 | 113.8 | 158.6 | 18.3 | 21.8 | 29 | 2.7 |  |  | 175 | 314.3 | 348.1 | 150.9 | 297.7 | 333.9 | 260.3
1856.2 | 156.2 | 140 | 56 | 65.4608 | 96.9 | 106.2 | 108.1 | 114.2 | 157.7 | 18.3 | 21.8 | 29.1 | 2.4 |  |  | 175.5 | 312.6 | 345.3 | 151.5 | 297.9 | 335.7 | 266
1857.2 | 157.2 | 140.3 | 56.12 | 65.601 | 97.3 | 106 | 108.2 | 114.4 | 156.7 | 18.3 | 21.8 | 29.1 | 2.4 |  |  | 176.1 | 305.5 | 341.3 | 152 | 291.1 | 341.4 | 269.9
1858.2 | 158.2 | 139.6 | 55.84 | 65.2737 | 97.4 | 105.8 | 108.4 | 114.5 | 154.8 | 18.3 | 21.8 | 29.1 | 2.4 |  |  | 176.6 | 299.7 | 343.7 | 152.5 | 288.1 | 351.1 | 275.9
1859.2 | 159.2 | 138.8 | 55.52 | 64.8997 | 97.5 | 106 | 108.8 | 114.7 | 154.6 | 18.3 | 21.7 | 29.2 | 3 |  |  | 177 | 299.7 | 346.2 | 153 | 290.6 | 357.5 | 282.7
1860.2 | 160.2 | 134.9 | 53.96 | 63.0761 | 97.5 | 106.5 | 109.1 | 114.9 | 155.7 | 18.3 | 21.7 | 29.2 | 3.2 |  |  | 177.5 | 302.8 | 349.2 | 153.5 | 292.8 | 373.5 | 285.2
1861.2 | 161.2 | 139.4 | 55.76 | 65.1802 | 96.9 | 106.7 | 109.3 | 114.8 | 159.5 | 18.3 | 21.7 | 29.2 | 3.4 |  |  | 177.9 | 303.1 | 351.2 | 154 | 295 | 370.4 | 284.8
1862.2 | 162.2 | 139.4 | 55.76 | 65.1802 | 96.6 | 106.8 | 109.1 | 114.8 | 159.2 | 18.4 | 21.8 | 29.2 | 3.6 |  |  | 178.3 | 301.2 | 342.6 | 154.5 | 298.8 | 366 | 277.1
1863.2 | 163.2 | 138.8 | 55.52 | 64.8997 | 96.9 | 106.4 | 109 | 114.8 | 158.3 | 18.4 | 21.7 | 29.3 | 3.5 |  |  | 178.7 | 305.7 | 338.9 | 155.1 | 308.7 | 380 | 274
1864.2 | 164.2 | 137.7 | 55.08 | 64.3853 | 97.1 | 106 | 109.3 | 114.9 | 160.4 | 18.4 | 21.7 | 29.3 | 3 |  |  | 179.1 | 313.7 | 347.7 | 155.6 | 318.9 | 394.8 | 279.2
1865.2 | 165.2 | 139.3 | 55.72 | 65.1335 | 97.2 | 105.8 | 109.5 | 115 | 163.6 | 18.5 | 21.7 | 29.3 | 2 |  |  | 179.4 | 313.6 | 349.5 | 156.3 | 320.9 | 391.9 | 283.3
1866.2 | 166.2 | 138.6 | 55.44 | 64.8062 | 96.8 | 105.4 | 109.6 | 115.2 | 162.3 | 18.5 | 21.7 | 29.4 | 3.1 |  |  | 179.7 | 309.1 | 356.4 | 156.9 | 314.9 | 384.1 | 281.3
1867.2 | 167.2 | 138.3 | 55.32 | 64.6659 | 96.8 | 105.6 | 109.6 | 115.3 | 161.1 | 18.6 | 21.7 | 29.6 | 3.9 |  |  | 180 | 309.3 | 361.3 | 157.7 | 316.1 | 385.7 | 285.5
1868.2 | 168.2 | 139.5 | 55.8 | 65.227 | 97.1 | 105.8 | 110.2 | 115.5 | 160.6 | 18.6 | 21.7 | 29.6 | 3.5 |  |  | 180.3 | 307.7 | 362 | 158.4 | 310.1 | 382.7 | 283.1
1869.2 | 169.2 | 138.8 | 55.52 | 64.8997 | 96.7 | 105.8 | 110.6 | 115.5 | 159.7 | 18.7 | 21.7 | 29.7 | 3.4 |  |  | 180.6 | 308.5 | 364.8 | 159.2 | 310.5 | 386.7 | 282.8
1870.2 | 170.2 | 138.6 | 55.44 | 64.8062 | 96.4 | 106 | 110.4 | 115.7 | 159.5 | 18.7 | 21.7 | 29.9 | 3 |  |  | 180.8 | 305.1 | 367.4 | 160 | 308.2 | 392.3 | 280.9
1871.2 | 171.2 | 133.9 | 53.56 | 62.6086 | 96.6 | 106.3 | 110.2 | 115.9 | 158.6 | 18.8 | 21.7 | 29.9 | 2.9 |  |  | 181.1 | 305.8 | 368.9 | 160.8 | 310.4 | 398.8 | 282.7
1872.2 | 172.2 | 140.5 | 56.2 | 65.6946 | 96.5 | 106.2 | 109.9 | 116.2 | 159.3 | 18.8 | 21.7 | 30 | 3.1 |  |  | 181.4 | 312.5 | 371.8 | 161.5 | 316.5 | 401.3 | 289
1873.2 | 173.2 | 140.2 | 56.08 | 65.5543 | 97.1 | 106.1 | 109.8 | 116 | 160.3 | 18.8 | 21.7 | 29.9 | 2.7 |  |  | 181.6 | 313.6 | 380.5 | 162.3 | 311.2 | 402 | 295.2
1874.2 | 174.2 | 137.9 | 55.16 | 64.4789 | 97.9 | 106 | 109.3 | 115.9 | 162.3 | 18.8 | 21.7 | 29.8 | 3.6 |  |  | 181.9 | 312.3 | 380.1 | 163 | 308.5 | 404.1 | 295.2
1875.2 | 175.2 | 140.2 | 56.08 | 65.5543 | 98.3 | 106.2 | 109.5 | 115.7 | 161 | 18.8 | 21.7 | 29.9 | 3.2 |  |  | 182.2 | 314.1 | 379 | 163.8 | 312.1 | 405.4 | 292.6
1876.2 | 176.2 | 139.7 | 55.88 | 65.3205 | 98.3 | 106.2 | 109.9 | 115.7 | 159.3 | 18.7 | 21.7 | 29.8 | 2.7 |  |  | 182.5 | 313 | 374.7 | 164.6 | 308.4 | 403.4 | 293.5
1877.2 | 177.2 | 141.6 | 56.64 | 66.2089 | 98.4 | 105.7 | 110.5 | 115.9 | 157.8 | 18.7 | 21.7 | 29.8 | 3.3 |  |  | 182.9 | 311.4 | 371.6 | 165.3 | 305.4 | 404.8 | 292.7
1878.2 | 178.2 | 142.9 | 57.16 | 66.8167 | 98.3 | 105.3 | 110.9 | 116.2 | 156.4 | 18.7 | 21.7 | 29.9 | 4 |  |  | 183.2 | 309.2 | 365.6 | 166.1 | 306.9 | 407 | 288.4
1879.2 | 179.2 | 142.3 | 56.92 | 66.5362 | 97.8 | 104.9 | 110.9 | 116.3 | 155.9 | 18.7 | 21.7 | 30 | 4.5 |  |  | 183.6 | 307.8 | 354.6 | 166.8 | 304.5 | 403.3 | 281.8
1880.2 | 180.2 | 140.7 | 56.28 | 65.7881 | 98 | 105.3 | 110.9 | 116.3 | 156.1 | 18.7 | 21.7 | 30 | 4 |  |  | 184 | 307.3 | 348.3 | 167.5 | 303.2 | 393.1 | 278.2
1881.2 | 181.2 | 138.9 | 55.56 | 64.9464 | 97.2 | 105.8 | 111.1 | 115.8 | 157.4 | 18.7 | 21.7 | 30 | 4.1 |  |  | 184.3 | 307.6 | 349 | 168.2 | 307.1 | 395.7 | 281.5
1882.2 | 182.2 | 139.5 | 55.8 | 65.227 | 96.8 | 106.3 | 111.2 | 114.9 | 157.9 | 18.8 | 21.7 | 30 | 3.7 |  |  | 184.7 | 306.3 | 345.5 | 168.9 | 309.9 | 393.6 | 282.8
1883.2 | 183.2 | 141 | 56.4 | 65.9284 | 96.8 | 106.1 | 111.1 | 114.5 | 157.6 | 18.9 | 21.7 | 30 | 4 |  |  | 185 | 303.3 | 346.3 | 169.6 | 308.9 | 384.8 | 280.9
1884.2 | 184.2 | 139.8 | 55.92 | 65.3673 | 96.4 | 106.3 | 111.2 | 114.2 | 156.1 | 19 | 21.7 | 30 | 3.3 |  |  | 185.3 | 302.5 | 344.2 | 170.2 | 309.8 | 383.5 | 280.8
1885.2 | 185.2 | 140.1 | 56.04 | 65.5075 | 96.8 | 105.9 | 111.4 | 114 | 156.1 | 19 | 21.7 | 30.1 | 3.4 |  |  | 185.6 | 302.3 | 351.9 | 170.9 | 308.4 | 378.4 | 285
1886.2 | 186.2 | 141.3 | 56.52 | 66.0686 | 97.7 | 105.3 | 111.3 | 114.1 | 157 | 19.1 | 21.7 | 30.1 | 2.8 |  |  | 185.8 | 300.1 | 348.9 | 171.6 | 305.2 | 377 | 287.5
1887.2 | 187.2 | 141 | 56.4 | 65.9284 | 98.1 | 105.7 | 111.2 | 114.2 | 156.7 | 19.1 | 21.7 | 30.1 | 2.6 |  |  | 186.1 | 296.1 | 346.4 | 172.2 | 300.2 | 371 | 287.8
1888.2 | 188.2 | 139.5 | 55.8 | 65.227 | 98.1 | 106.3 | 111.3 | 114.4 | 155.8 | 19.1 | 21.7 | 30 | 2.5 |  |  | 186.3 | 299.2 | 340 | 172.8 | 304.5 | 368.7 | 284.6
1889.2 | 189.2 | 140 | 56 | 65.4608 | 98 | 106.6 | 111.2 | 114.8 | 157.5 | 19.1 | 21.7 | 30 | 2.6 |  |  | 186.5 | 304.5 | 345.9 | 173.4 | 311.7 | 380.7 | 290.1
1890.2 | 190.2 | 139.3 | 55.72 | 65.1335 | 98.2 | 106.5 | 111.2 | 115 | 159.1 | 19.1 | 21.7 | 30 | 3.5 |  |  | 186.7 | 312.7 | 354.2 | 174 | 317.8 | 375 | 293.5
1891.2 | 191.2 | 140.5 | 56.2 | 65.6946 | 98.2 | 106.2 | 111.2 | 115 | 159.3 | 19.1 | 21.7 | 30.1 | 3.4 |  |  | 186.9 | 311 | 356.5 | 174.6 | 317.2 | 370.2 | 290.9
1892.2 | 192.2 | 141.2 | 56.48 | 66.0219 | 98.4 | 106.6 | 111.2 | 115.1 | 158.2 | 19.1 | 21.7 | 30.2 | 3.1 |  |  | 187.1 | 310.6 | 359.1 | 175.2 | 319 | 367.9 | 290.5
1893.2 | 193.2 | 139.1 | 55.64 | 65.04 | 98.9 | 107.3 | 111.2 | 115.2 | 156.4 | 19 | 21.7 | 30.3 | 2.8 |  |  | 187.3 | 311.1 | 363.3 | 175.8 | 318.6 | 368.3 | 291.8
1894.2 | 194.2 | 139.9 | 55.96 | 65.414 | 99.4 | 107.6 | 111.5 | 115.1 | 155.9 | 19 | 21.7 | 30.3 | 2.4 |  |  | 187.5 | 312.4 | 353.3 | 176.5 | 317.6 | 362.9 | 289.6
1895.2 | 195.2 | 139.7 | 55.88 | 65.3205 | 99.3 | 107.8 | 111.3 | 115.3 | 155 | 19 | 21.7 | 30.4 | 2.7 |  |  | 187.7 | 315.5 | 348 | 177.3 | 320.4 | 358.8 | 286.7
1896.2 | 196.2 | 138.2 | 55.28 | 64.6191 | 98.7 | 107.7 | 111.2 | 115.4 | 155.4 | 18.9 | 21.7 | 30.4 | 2.3 |  |  | 188 | 313.6 | 343.4 | 178 | 320.2 | 352.7 | 286
1897.2 | 197.2 | 140.8 | 56.32 | 65.8348 | 98.4 | 107.7 | 111.1 | 115.7 | 157.4 | 19 | 21.7 | 30.4 | 2.9 |  |  | 188.3 | 315.7 | 341.9 | 178.6 | 318 | 349.5 | 283.1
1898.2 | 198.2 | 141.5 | 56.6 | 66.1621 | 97.9 | 108.3 | 111.1 | 115.8 | 157.2 | 19 | 21.7 | 30.4 | 3.6 |  |  | 188.6 | 315.3 | 346.3 | 179.2 | 318.9 | 345.7 | 283.9
1899.2 | 199.2 | 140.7 | 56.28 | 65.7881 | 97.5 | 107.9 | 111.1 | 115.5 | 157.9 | 19 | 21.7 | 30.4 | 3.7 |  |  | 188.9 | 316.6 | 347.9 | 179.8 | 316.8 | 346 | 284.2
1900.2 | 200.2 | 140.9 | 56.36 | 65.8816 | 97.6 | 107.6 | 111.2 | 115.7 | 157.1 | 19.1 | 21.7 | 30.5 | 4.2 |  |  | 189.2 | 312.1 | 348 | 180.4 | 317.6 | 354.8 | 286.6
1901.2 | 201.2 | 139.3 | 55.72 | 65.1335 | 98 | 107.8 | 111.9 | 115.5 | 157 | 19.1 | 21.7 | 30.5 | 4.6 |  |  | 189.5 | 309.8 | 347.8 | 180.9 | 318.8 | 366.2 | 293
1902.2 | 202.2 | 142 | 56.8 | 66.3959 | 98.5 | 107.5 | 112.2 | 115.5 | 157.6 | 19.2 | 21.7 | 30.5 | 4.1 |  |  | 189.8 | 313.6 | 344.9 | 181.4 | 318.6 | 370.9 | 294.8
1903.2 | 203.2 | 140.4 | 56.16 | 65.6478 | 97.9 | 106.8 | 112.1 | 115.6 | 158.3 | 19.2 | 21.7 | 30.6 | 4.6 |  |  | 190.1 | 316.1 | 351.6 | 181.9 | 318.5 | 374.3 | 296.8
1904.2 | 204.2 | 140.6 | 56.24 | 65.7413 | 98.1 | 106.7 | 112.2 | 115.8 | 160.3 | 19.2 | 21.7 | 30.6 | 3.8 |  |  | 190.3 | 313.4 | 344 | 182.4 | 314.1 | 370.5 | 295
1905.2 | 205.2 | 141.7 | 56.68 | 66.2557 | 98.3 | 106.9 | 112.6 | 115.9 | 158.1 | 19.2 | 21.7 | 30.5 | 3.4 |  |  | 190.7 | 311.5 | 333.4 | 183 | 312 | 366.7 | 290.7
1906.2 | 206.2 | 140.7 | 56.28 | 65.7881 | 98.3 | 106.7 | 112.6 | 115.9 | 157.1 | 19.2 | 21.7 | 30.5 | 2.3 |  |  | 191 | 316.3 | 334.8 | 183.5 | 319.5 | 362.6 | 288.7
1907.2 | 207.2 | 140.2 | 56.08 | 65.5543 | 97.7 | 106.5 | 112.7 | 115.6 | 157.7 | 19.2 | 21.7 | 30.4 | 2.2 |  |  | 191.4 | 318.1 | 328.9 | 184.1 | 322.3 | 360.7 | 287.5
1908.2 | 208.2 | 141.2 | 56.48 | 66.0219 | 97.5 | 106.4 | 112.6 | 115.5 | 156.7 | 19.2 | 21.7 | 30.4 | 2.8 |  |  | 191.8 | 315.3 | 324.5 | 184.7 | 318.5 | 350.3 | 286.9
1909.2 | 209.2 | 140.7 | 56.28 | 65.7881 | 97.4 | 106.3 | 113.1 | 115.5 | 155.7 | 19.2 | 21.7 | 30.5 | 2.6 |  |  | 192.2 | 320 | 322.4 | 185.3 | 320.4 | 347.5 | 286.6
1910.2 | 210.2 | 143.4 | 57.36 | 67.0505 | 98.2 | 106.5 | 113.8 | 115.3 | 157.4 | 19.2 | 21.7 | 30.6 | 2.7 |  |  | 192.6 | 325.7 | 323.3 | 185.9 | 323.4 | 340.4 | 285.3
1911.2 | 211.2 | 143.4 | 57.36 | 67.0505 | 98.6 | 106.7 | 113.9 | 115.1 | 161.4 | 19.2 | 21.7 | 30.6 | 2.7 |  |  | 192.9 | 335.4 | 330.9 | 186.4 | 332.5 | 350.1 | 286.3
1912.2 | 212.2 | 142.2 | 56.88 | 66.4894 | 99.2 | 106.5 | 114 | 114.7 | 163.1 | 19.2 | 21.7 | 30.6 | 2 |  |  | 193.3 | 331.1 | 328.6 | 186.9 | 327.3 | 349.1 | 284.9
1913.2 | 213.2 | 141.9 | 56.76 | 66.3492 | 99.8 | 107 | 113.7 | 114.8 | 163.6 | 19.3 | 21.7 | 30.6 | 1.6 |  |  | 193.6 | 327.6 | 329.5 | 187.3 | 325.1 | 353 | 287.1
1914.2 | 214.2 | 142.2 | 56.88 | 66.4894 | 100.1 | 107.8 | 113.6 | 114.9 | 163.5 | 19.3 | 21.7 | 30.6 | 1.9 |  |  | 193.9 | 326.9 | 329.2 | 187.8 | 324.4 | 346.8 | 286.7
1915.2 | 215.2 | 140.8 | 56.32 | 65.8348 | 100.1 | 107.7 | 113.9 | 115.1 | 163.1 | 19.3 | 21.7 | 30.6 | 2.6 |  |  | 194.2 | 323.9 | 333.4 | 188.4 | 324.4 | 348.9 | 288.9
1916.2 | 216.2 | 140.1 | 56.04 | 65.5075 | 100.4 | 107.5 | 114 | 115.2 | 162.4 | 19.3 | 21.7 | 30.7 | 2.6 |  |  | 194.5 | 324.1 | 328.4 | 188.9 | 328.8 | 351.3 | 288.9
1917.2 | 217.2 | 140.6 | 56.24 | 65.7413 | 100.8 | 107.2 | 114.1 | 115.4 | 166.2 | 19.3 | 21.7 | 30.7 | 2.3 |  |  | 194.9 | 325.3 | 328.2 | 189.4 | 334.6 | 363.1 | 290.7
1918.2 | 218.2 | 140.9 | 56.36 | 65.8816 | 100.9 | 107 | 114.3 | 115.7 | 166.1 | 19.3 | 21.7 | 30.7 | 3 |  |  | 195.2 | 322.9 | 323.7 | 189.9 | 334 | 367 | 292
1919.2 | 219.2 | 140.4 | 56.16 | 65.6478 | 100.4 | 106.9 | 114.5 | 116.1 | 166.6 | 19.3 | 21.7 | 30.7 | 3.2 |  |  | 195.6 | 326.9 | 324.3 | 190.5 | 341.4 | 368.9 | 293.3
1920.2 | 220.2 | 138.9 | 55.56 | 64.9464 | 99.9 | 107.1 | 114.4 | 116.1 | 167.3 | 19.3 | 21.7 | 30.7 | 3.5 |  |  | 195.9 | 325.9 | 325.1 | 191 | 339.4 | 372.9 | 297
1921.2 | 221.2 | 139.8 | 55.92 | 65.3673 | 100.4 | 107.4 | 114.5 | 116.2 | 166.4 | 19.3 | 21.7 | 30.8 | 3 |  |  | 196.3 | 319 | 324.1 | 191.6 | 336.6 | 387 | 299.8
1922.2 | 222.2 | 139.5 | 55.8 | 65.227 | 100.9 | 107.2 | 115 | 116.4 | 166 | 19.3 | 21.7 | 30.9 | 2.8 |  |  | 196.6 | 314.5 | 324 | 192.2 | 332.8 | 395.4 | 300.2
1923.2 | 223.2 | 139.5 | 55.8 | 65.227 | 100.8 | 107.6 | 115.4 | 116.4 | 165.9 | 19.3 | 21.7 | 30.9 | 2.3 |  |  | 196.9 | 312.3 | 324 | 192.8 | 332.4 | 394.9 | 299.1
1924.2 | 224.2 | 140.8 | 56.32 | 65.8348 | 100.1 | 108.2 | 115.5 | 116.5 | 165.2 | 19.3 | 21.7 | 30.9 | 2.7 |  |  | 197.2 | 305.9 | 318.2 | 193.3 | 326.9 | 391.3 | 296.8
1925.2 | 225.2 | 139.1 | 55.64 | 65.04 | 99.2 | 108.3 | 115.2 | 116.5 | 163.5 | 19.4 | 21.7 | 31.1 | 2.9 |  |  | 197.4 | 302 | 312.2 | 193.9 | 323.1 | 384.5 | 294.1
1926.2 | 226.2 | 138.5 | 55.4 | 64.7594 | 99.2 | 108.4 | 115.3 | 116.3 | 162.4 | 19.4 | 21.7 | 31.1 | 2.7 |  |  | 197.7 | 297.2 | 308.6 | 194.5 | 319.3 | 385.6 | 291.5
1927.2 | 227.2 | 140 | 56 | 65.4608 | 98.6 | 108.1 | 115.6 | 116.4 | 160.6 | 19.4 | 21.7 | 31.1 | 2.6 |  |  | 197.9 | 297.8 | 310.6 | 195.1 | 320.1 | 392.2 | 295.4
1928.2 | 228.2 | 134.6 | 53.84 | 62.9359 | 98.5 | 107.7 | 115.9 | 116.6 | 161.3 | 19.4 | 21.7 | 31 | 2.3 |  |  | 198.2 | 293.3 | 313.5 | 195.7 | 316.9 | 388.6 | 297.7
1929.2 | 229.2 | 141.1 | 56.44 | 65.9751 | 98.4 | 108.1 | 115.9 | 116.9 | 159.5 | 19.5 | 21.7 | 30.9 | 2.3 |  |  | 198.4 | 293.6 | 317.8 | 196.3 | 317.4 | 388.7 | 299.9
1930.2 | 230.2 | 138.7 | 55.48 | 64.8529 | 97.9 | 108.5 | 115.7 | 117.1 | 158.3 | 19.5 | 21.7 | 30.9 | 2.6 |  |  | 198.5 | 292.5 | 317.1 | 196.8 | 315.9 | 392.6 | 302.6
1931.2 | 231.2 | 139 | 55.6 | 64.9932 | 97.5 | 108.8 | 115.8 | 117.1 | 157.1 | 19.5 | 21.7 | 30.9 | 2.6 |  |  | 198.7 | 289.5 | 312.6 | 197.4 | 312.3 | 390.6 | 299.6
1932.2 | 232.2 | 137.5 | 55 | 64.2918 | 97.9 | 108.9 | 115.7 | 117.7 | 155.1 | 19.5 | 21.7 | 30.9 | 2.9 |  |  | 198.9 | 283.6 | 315.5 | 198 | 306.3 | 389.7 | 298.4
1933.2 | 233.2 | 139.9 | 55.96 | 65.414 | 98.2 | 109.3 | 115.7 | 118.2 | 154.9 | 19.6 | 21.7 | 31 | 3.2 |  |  | 199 | 287.5 | 312.9 | 198.6 | 313.4 | 396.4 | 298.3
1934.2 | 234.2 | 140.4 | 56.16 | 65.6478 | 99 | 109.6 | 115.5 | 118.5 | 155.2 | 19.6 | 21.7 | 31 | 3.4 |  |  | 199.1 | 290.7 | 310.5 | 199.1 | 310.8 | 389.9 | 297.9
1935.2 | 235.2 | 136.7 | 54.68 | 63.9178 | 99.7 | 109.7 | 115.2 | 118.6 | 154.6 | 19.6 | 21.7 | 31 | 3.2 |  |  | 199.2 | 299.5 | 313.3 | 199.6 | 315.9 | 381.6 | 296.3
1936.2 | 236.2 | 138.3 | 55.32 | 64.6659 | 100 | 109.4 | 115.1 | 118.5 | 155.7 | 19.6 | 21.7 | 31 | 2.6 |  |  | 199.3 | 299.3 | 312.6 | 200.1 | 317 | 382.5 | 293
1937.2 | 237.2 | 138.2 | 55.28 | 64.6191 | 99.8 | 109 | 114.9 | 118.5 | 156.2 | 19.6 | 21.7 | 31 | 2.5 |  |  | 199.4 | 304.6 | 315.8 | 200.7 | 322.7 | 381.9 | 296.1
1938.2 | 238.2 | 139.5 | 55.8 | 65.227 | 99.7 | 109 | 114.8 | 118.4 | 158.8 | 19.5 | 21.7 | 31.1 | 2.2 |  |  | 199.4 | 304.5 | 312.8 | 201.2 | 321.5 | 379.2 | 295.1
1939.2 | 239.2 | 136.8 | 54.72 | 63.9645 | 99.9 | 109.2 | 115.1 | 118.1 | 157.3 | 19.5 | 21.7 | 31.1 | 2.8 |  |  | 199.5 | 306 | 312.1 | 201.8 | 321.3 | 375.2 | 291.2
1940.2 | 240.2 | 138.8 | 55.52 | 64.8997 | 100.3 | 109.4 | 115.1 | 117.8 | 157.3 | 19.5 | 21.7 | 31.2 | 3.1 |  |  | 199.6 | 311.5 | 315.5 | 202.5 | 326 | 379.3 | 292.4
1941.2 | 241.2 | 139.1 | 55.64 | 65.04 | 100.6 | 109.2 | 114.8 | 117.5 | 157.9 | 19.5 | 21.7 | 31.2 | 3.4 |  |  | 199.7 | 316.1 | 315.4 | 203 | 328.6 | 380.9 | 291.4
1942.2 | 242.2 | 134.5 | 53.8 | 62.8891 | 100.4 | 109 | 114.8 | 117.3 | 159 | 19.5 | 21.7 | 31.3 | 2.7 |  |  | 199.7 | 319.8 | 316.1 | 203.5 | 334.4 | 386.2 | 293.3
1943.2 | 243.2 | 139.1 | 55.64 | 65.04 | 100.8 | 109.1 | 114.5 | 117.2 | 160.8 | 19.5 | 21.7 | 31.4 | 2.9 |  |  | 199.8 | 325 | 313.4 | 204 | 338.1 | 386.9 | 293.7
1944.2 | 244.2 | 140.7 | 56.28 | 65.7881 | 101.2 | 109.3 | 114.7 | 117.3 | 161.9 | 19.4 | 21.7 | 31.4 | 2.8 |  |  | 199.9 | 331.1 | 310.2 | 204.5 | 346 | 384.6 | 292.9
1945.2 | 245.2 | 139.7 | 55.88 | 65.3205 | 101.7 | 109.6 | 115 | 117.1 | 162.1 | 19.4 | 21.7 | 31.4 | 3.4 |  |  | 200.1 | 328.4 | 308.2 | 205 | 348.9 | 386.2 | 291.8
1946.2 | 246.2 | 140 | 56 | 65.4608 | 102.6 | 109.7 | 115.3 | 116.6 | 162.1 | 19.5 | 21.7 | 31.5 | 3.4 |  |  | 200.2 | 326 | 311.1 | 205.5 | 347 | 387.9 | 293.9
1947.2 | 247.2 | 138.2 | 55.28 | 64.6191 | 102.7 | 109.6 | 115.8 | 116.8 | 162.3 | 19.5 | 21.7 | 31.4 | 3.1 |  |  | 200.3 | 325.8 | 310 | 206 | 348.9 | 390.2 | 295
1948.2 | 248.2 | 140.3 | 56.12 | 65.601 | 102.5 | 109.7 | 116.2 | 116.9 | 162.3 | 19.5 | 21.7 | 31.4 | 3.5 |  |  | 200.5 | 324.4 | 304.6 | 206.5 | 346.5 | 388.1 | 293
1949.2 | 249.2 | 139.3 | 55.72 | 65.1335 | 102.7 | 110 | 116.3 | 116.9 | 161.8 | 19.6 | 21.7 | 31.4 | 2.8 |  |  | 200.7 | 321.3 | 302.7 | 207.1 | 344.2 | 395.8 | 294.8
1950.2 | 250.2 | 138.3 | 55.32 | 64.6659 | 102.5 | 110.1 | 116.1 | 116.8 | 162.3 | 19.7 | 21.7 | 31.3 | 1.7 |  |  | 200.9 | 321 | 307.5 | 207.6 | 344.1 | 399.1 | 296
1951.2 | 251.2 | 137.9 | 55.16 | 64.4789 | 102.5 | 109.7 | 116.1 | 116.6 | 162 | 19.8 | 21.7 | 31.3 | 2.9 |  |  | 201 | 318.8 | 308.1 | 208.1 | 340.1 | 399 | 299.7
1952.2 | 252.2 | 139.8 | 55.92 | 65.3673 | 101.8 | 109.2 | 116.1 | 116.5 | 161.7 | 19.8 | 21.6 | 31.3 | 2.8 |  |  | 201.2 | 316 | 302.3 | 208.7 | 335.1 | 394.1 | 299.3
1953.2 | 253.2 | 142.1 | 56.84 | 66.4427 | 101.3 | 108.9 | 116 | 116.5 | 160.7 | 19.9 | 21.6 | 31.3 | 2.3 |  |  | 201.4 | 313.6 | 296 | 209.3 | 331.4 | 392.5 | 296.2
1954.2 | 254.2 | 142.7 | 57.08 | 66.7232 | 101.2 | 108.9 | 116.3 | 116.4 | 161.8 | 20 | 21.6 | 31.2 | 2 |  |  | 201.6 | 315.4 | 298.3 | 209.9 | 330.7 | 392.9 | 296.1
1955.2 | 255.2 | 141.5 | 56.6 | 66.1621 | 100.4 | 109 | 115.8 | 116.1 | 162.5 | 20 | 21.6 | 31.3 | 1.6 |  |  | 201.7 | 317.2 | 304.2 | 210.6 | 331.4 | 390.7 | 297.9
1956.2 | 256.2 | 141.5 | 56.6 | 66.1621 | 99.5 | 109.2 | 115.6 | 116.1 | 165.2 | 20.1 | 21.6 | 31.3 | 1.5 |  |  | 201.8 | 317.5 | 302.8 | 211.1 | 331.4 | 386.9 | 297.3
1957.2 | 257.2 | 141.9 | 56.76 | 66.3492 | 98.9 | 109.4 | 115.3 | 116 | 165.4 | 20.1 | 21.6 | 31.3 | 1.7 |  |  | 201.9 | 317.9 | 300.9 | 211.6 | 329.9 | 377.8 | 294
1958.2 | 258.2 | 140.7 | 56.28 | 65.7881 | 99.1 | 109.5 | 115.5 | 115.6 | 165 | 20.1 | 21.7 | 31.4 | 2 |  |  | 202 | 322.9 | 299 | 212.2 | 332.5 | 376.5 | 293.6
1959.2 | 259.2 | 139.6 | 55.84 | 65.2737 | 99.4 | 109.7 | 115.8 | 116.3 | 164 | 20.1 | 21.6 | 31.5 | 2.1 |  |  | 202.1 | 323.4 | 292.3 | 212.7 | 332.2 | 377.3 | 290.1
1960.2 | 260.2 | 139.4 | 55.76 | 65.1802 | 99.7 | 109.9 | 115.9 | 116.5 | 163.8 | 20.1 | 21.6 | 31.5 | 1.7 |  |  | 202.3 | 320.7 | 294.1 | 213.1 | 332 | 377.2 | 289.2
1961.2 | 261.2 | 139.6 | 55.84 | 65.2737 | 99.8 | 110 | 116 | 116.8 | 165.5 | 20.1 | 21.6 | 31.6 | 1.7 |  |  | 202.4 | 322.2 | 293.8 | 213.7 | 334.5 | 380.4 | 289.8
1962.2 | 262.2 | 138.8 | 55.52 | 64.8997 | 100.2 | 109.9 | 115.9 | 117.1 | 164.4 | 20.1 | 21.6 | 31.6 | 1.7 |  |  | 202.6 | 322.2 | 291.7 | 214.1 | 333.2 | 378.4 | 289.7
1963.2 | 263.2 | 139 | 55.6 | 64.9932 | 101.1 | 110 | 115.8 | 117.2 | 162.3 | 20.1 | 21.6 | 31.7 | 2 |  |  | 202.7 | 321.2 | 294.6 | 215.1 | 334.9 | 384.4 | 292
1964.2 | 264.2 | 139.7 | 55.88 | 65.3205 | 101.4 | 109.9 | 116 | 117.2 | 161.7 | 20.1 | 21.6 | 31.8 | 2 |  |  | 202.8 | 319.2 | 303.4 | 215.9 | 332 | 384.3 | 295.6
1965.2 | 265.2 | 140.5 | 56.2 | 65.6946 | 101.3 | 109.8 | 116.1 | 117.1 | 160 | 20.1 | 21.6 | 31.8 | 1.7 |  |  | 202.9 | 313.1 | 309.4 | 216.7 | 323.7 | 380.8 | 298.3
1966.2 | 266.2 | 138.7 | 55.48 | 64.8529 | 101.2 | 109.7 | 115.9 | 117 | 158.2 | 20.1 | 21.6 | 31.8 | 1.8 |  |  | 203.1 | 309.8 | 310.4 | 217.4 | 319.6 | 379.9 | 299.9
1967.2 | 267.2 | 139 | 55.6 | 64.9932 | 101 | 109.7 | 115.7 | 116.9 | 157.2 | 20.1 | 21.6 | 31.9 | 2.1 |  |  | 203.2 | 308.1 | 310.4 | 217.9 | 317.4 | 374.6 | 297
1968.2 | 268.2 | 137.6 | 55.04 | 64.3386 | 101.1 | 110 | 115.8 | 116.6 | 156.2 | 20.2 | 21.6 | 32 | 2.2 |  |  | 203.4 | 303.9 | 310.7 | 218.4 | 316.2 | 375 | 292.6
1969.2 | 269.2 | 138.9 | 55.56 | 64.9464 | 101 | 110.3 | 115.6 | 116.4 | 154.8 | 20.2 | 21.6 | 32.1 | 2.4 |  |  | 203.6 | 305.3 | 313.4 | 218.7 | 318.6 | 370.5 | 291.7
1970.2 | 270.2 | 136.5 | 54.6 | 63.8243 | 100.5 | 110.3 | 115 | 116 | 155.4 | 20.2 | 21.6 | 32.1 | 2.3 |  |  | 203.7 | 303.1 | 311 | 219.1 | 315.9 | 367.3 | 291.9
1971.2 | 271.2 | 136.6 | 54.64 | 63.871 | 101.2 | 110.4 | 114.3 | 116.1 | 154 | 20.2 | 21.6 | 32.2 | 2.1 |  |  | 203.9 | 298.9 | 308.1 | 219.6 | 311.5 | 362.9 | 289.5
1972.2 | 272.2 | 138.3 | 55.32 | 64.6659 | 101 | 110.5 | 113.8 | 116 | 153 | 20.3 | 21.6 | 32.3 | 2.4 |  |  | 204.1 | 306.3 | 310.1 | 220.2 | 318.8 | 371.1 | 290.8
1973.2 | 273.2 | 134.8 | 53.92 | 63.0294 | 100.8 | 110.2 | 113.4 | 115.8 | 154.9 | 20.2 | 21.6 | 32.3 | 2.3 |  |  | 204.3 | 309 | 312.6 | 220.6 | 319.6 | 374.4 | 291.5
1974.2 | 274.2 | 138.2 | 55.28 | 64.6191 | 100.7 | 109.7 | 113.1 | 115.7 | 156.5 | 20.2 | 21.6 | 32.4 | 2 |  |  | 204.5 | 308.2 | 309 | 221.2 | 318.6 | 374.3 | 292.3
1975.2 | 275.2 | 137 | 54.8 | 64.058 | 101 | 109.3 | 112.9 | 115.7 | 156.7 | 20.2 | 21.6 | 32.4 | 1.5 |  |  | 204.7 | 306.4 | 312.6 | 223.1 | 318 | 376.1 | 292.9
1976.2 | 276.2 | 140.4 | 56.16 | 65.6478 | 101.1 | 108.8 | 112.9 | 115.2 | 155.2 | 20.2 | 21.6 | 32.5 | 2.3 |  |  | 204.8 | 307.5 | 316 | 224.5 | 315 | 382.8 | 297.3
1977.2 | 277.2 | 140 | 56 | 65.4608 | 100.9 | 108.3 | 113 | 114.5 | 155.7 | 20.2 | 21.6 | 32.6 | 2.5 |  |  | 205 | 305.6 | 312.1 | 225.5 | 314 | 383.5 | 298.2
1978.2 | 278.2 | 139.6 | 55.84 | 65.2737 | 101 | 108.3 | 113.2 | 114.6 | 155.3 | 20.2 | 21.6 | 32.6 | 2.1 |  |  | 205.2 | 305.5 | 310.9 | 226.4 | 317.1 | 383.3 | 296.7
1979.2 | 279.2 | 138.1 | 55.24 | 64.5724 | 101.4 | 108.6 | 113.3 | 115 | 157 | 20.3 | 21.6 | 32.6 | 1.9 |  |  | 205.4 | 307.1 | 311.5 | 227.1 | 320.2 | 382.1 | 298.7
1980.2 | 280.2 | 138.8 | 55.52 | 64.8997 | 101.9 | 109 | 113.1 | 115 | 159.4 | 20.3 | 21.6 | 32.6 | 2 |  |  | 205.6 | 308.8 | 310.9 | 227.9 | 325.4 | 382.4 | 296.9
1981.2 | 281.2 | 139.2 | 55.68 | 65.0867 | 101.8 | 109.4 | 112.8 | 114.9 | 160.6 | 20.3 | 21.6 | 32.6 | 1.8 |  |  | 205.8 | 308.6 | 308 | 228.5 | 329.5 | 378.3 | 294.4
1982.2 | 282.2 | 139.4 | 55.76 | 65.1802 | 101.4 | 109.6 | 112.5 | 115.2 | 160.4 | 20.3 | 21.6 | 32.7 | 2 |  |  | 206 | 311.6 | 312.6 | 229.2 | 330.9 | 373.1 | 294.3
1983.2 | 283.2 | 138.6 | 55.44 | 64.8062 | 101.5 | 109.6 | 112.7 | 115.4 | 160.8 | 20.3 | 21.6 | 32.7 | 2.5 |  |  | 206.2 | 313.2 | 318.7 | 229.8 | 333 | 374.5 | 299.5
1984.2 | 284.2 | 139.4 | 55.76 | 65.1802 | 102.1 | 109.3 | 113 | 115.6 | 160.3 | 20.3 | 21.6 | 32.7 | 2.5 |  |  | 206.4 | 313.7 | 313.8 | 230.3 | 332 | 373.5 | 296.2
1985.2 | 285.2 | 141.2 | 56.48 | 66.0219 | 102.2 | 109.1 | 113.1 | 115.8 | 161.1 | 20.3 | 21.6 | 32.7 | 2.3 |  |  | 206.6 | 315.4 | 313.2 | 230.8 | 331.3 | 372.7 | 293.8
1986.2 | 286.2 | 138 | 55.2 | 64.5256 | 102.3 | 109.5 | 113.3 | 115.6 | 161.7 | 20.2 | 21.6 | 32.6 | 2.4 |  |  | 206.8 | 319 | 321.9 | 231.3 | 331.5 | 374.5 | 296.2
1987.2 | 287.2 | 138.4 | 55.36 | 64.7127 | 102.2 | 109.3 | 113.4 | 116 | 162.1 | 20.2 | 21.6 | 32.6 | 2.2 |  |  | 207 | 316.2 | 331.6 | 231.8 | 329.4 | 378.9 | 304.9
1988.2 | 288.2 | 139.2 | 55.68 | 65.0867 | 101.7 | 109 | 113.3 | 116.1 | 161.3 | 20.3 | 21.6 | 32.6 | 2.4 |  |  | 207.2 | 315.5 | 329.4 | 232.2 | 329.7 | 374.6 | 304.1
1989.2 | 289.2 | 138.8 | 55.52 | 64.8997 | 102 | 109.1 | 113.3 | 116.5 | 160.3 | 20.3 | 21.6 | 32.7 | 2.3 |  |  | 207.4 | 319.4 | 325.4 | 232.7 | 333.9 | 371.3 | 300.2
1990.2 | 290.2 | 137.2 | 54.88 | 64.1516 | 102 | 109.9 | 113.3 | 116.8 | 160.1 | 20.3 | 21.6 | 32.8 | 2.3 |  |  | 207.7 | 317.9 | 324.4 | 233.1 | 329.7 | 364 | 297.5
1991.2 | 291.2 | 137.9 | 55.16 | 64.4789 | 102 | 110.3 | 112.9 | 117 | 161.1 | 20.3 | 21.6 | 32.8 | 2.3 |  |  | 207.9 | 315.2 | 321.1 | 233.6 | 324.2 | 356.9 | 293.7
1992.2 | 292.2 | 138.3 | 55.32 | 64.6659 | 102 | 110.4 | 113 | 117.5 | 159.7 | 20.3 | 21.6 | 32.7 | 2.3 |  |  | 208.2 | 314.1 | 316.8 | 234 | 323.2 | 355 | 292.3
1993.2 | 293.2 | 136.4 | 54.56 | 63.7775 | 102.3 | 110.9 | 113.2 | 118.3 | 160.2 | 20.3 | 21.6 | 32.7 | 2.1 |  |  | 208.5 | 318.9 | 313.6 | 234.5 | 326.7 | 354.6 | 292.9
1994.2 | 294.2 | 132 | 52.8 | 61.7202 | 102.4 | 111 | 113.1 | 118.9 | 161.6 | 20.4 | 21.6 | 32.7 | 2.4 |  |  | 208.8 | 317.9 | 308.5 | 234.8 | 323.1 | 350.7 | 289.7
1995.2 | 295.2 | 135.7 | 54.28 | 63.4502 | 102.4 | 110.9 | 112.9 | 119 | 161.4 | 20.3 | 21.6 | 32.8 | 1.7 |  |  | 209.1 | 314.7 | 306.8 | 235.2 | 320.6 | 350.1 | 290.1
1996.2 | 296.2 | 134.7 | 53.88 | 62.9826 | 102.7 | 110.9 | 112.9 | 119.1 | 159.6 | 20.3 | 21.6 | 32.7 | 1.5 |  |  | 209.4 | 313.4 | 297.7 | 235.5 | 320 | 345.3 | 287.4
1997.2 | 297.2 | 132.5 | 53 | 61.9539 | 103.2 | 110.9 | 112.8 | 119.4 | 157.6 | 20.3 | 21.6 | 32.7 | 1.5 |  |  | 209.7 | 312 | 292.8 | 235.9 | 318.6 | 339.7 | 284.8
1998.2 | 298.2 | 136.7 | 54.68 | 63.9178 | 103.1 | 110.9 | 112.7 | 119.5 | 156.4 | 20.3 | 21.6 | 32.7 | 1.6 |  |  | 210 | 311.2 | 289.9 | 236.2 | 317.9 | 333.4 | 285.4
1999.2 | 299.2 | 136.4 | 54.56 | 63.7775 | 102.3 | 110.9 | 112.8 | 119.8 | 156.8 | 20.3 | 21.6 | 32.7 | 1.6 |  |  | 210.2 | 307.5 | 284 | 236.6 | 317.6 | 335.6 | 284.7
2000.2 | 300.2 | 137.5 | 55 | 64.2918 | 102.7 | 110.4 | 113.2 | 119.8 | 156.4 | 20.3 | 21.6 | 32.7 | 1.6 |  |  | 210.5 | 304.9 | 281.7 | 236.9 | 315.5 | 339.6 | 284.1
2001.2 | 301.2 | 136.8 | 54.72 | 63.9645 | 102.9 | 109.9 | 113.7 | 119.9 | 157.5 | 20.3 | 21.6 | 32.7 | 1.9 |  |  | 210.6 | 305.3 | 284.2 | 237.2 | 320 | 344.8 | 286.2
2002.2 | 302.2 | 135.7 | 54.28 | 63.4502 | 102.9 | 109.6 | 113.9 | 119.6 | 159.2 | 20.4 | 21.6 | 32.8 | 2.4 |  |  | 210.8 | 305.8 | 283 | 237.4 | 321.2 | 345.2 | 290.1
2003.2 | 303.2 | 137.1 | 54.84 | 64.1048 | 102.3 | 109.6 | 114 | 119.3 | 159.7 | 20.4 | 21.6 | 32.8 | 2.3 |  |  | 210.9 | 303.3 | 276.2 | 237.7 | 319.4 | 341 | 287
2004.2 | 304.2 | 137.8 | 55.12 | 64.4321 | 102.2 | 109.2 | 114.3 | 119.1 | 159.9 | 20.4 | 21.6 | 32.9 | 2.5 |  |  | 211.1 | 303.5 | 274.1 | 237.9 | 318.1 | 335.8 | 285.1
2005.2 | 305.2 | 136.8 | 54.72 | 63.9645 | 102.3 | 109 | 114.4 | 119.2 | 159.5 | 20.4 | 21.6 | 32.9 | 3.3 |  |  | 211.2 | 302.9 | 284.9 | 238.2 | 316.8 | 337.6 | 290.7
2006.2 | 306.2 | 138.9 | 55.56 | 64.9464 | 101.6 | 109 | 114.4 | 119.1 | 162.1 | 20.5 | 21.6 | 33 | 3 |  |  | 211.3 | 306.7 | 283.8 | 238.4 | 321.5 | 338.2 | 291.9
2007.2 | 307.2 | 135.7 | 54.28 | 63.4502 | 101.9 | 109.1 | 114.3 | 118.9 | 161.9 | 20.5 | 21.6 | 33 | 2.1 |  |  | 211.4 | 303.7 | 280.4 | 238.6 | 318.6 | 339.3 | 288.8
2008.2 | 308.2 | 139.2 | 55.68 | 65.0867 | 101.5 | 109.2 | 114.3 | 118.9 | 160.8 | 20.6 | 21.6 | 32.9 | 2 |  |  | 211.4 | 301.4 | 278.8 | 238.8 | 317.7 | 340.2 | 290.1
2009.2 | 309.2 | 138.6 | 55.44 | 64.8062 | 101 | 108.8 | 114.7 | 118.9 | 161.2 | 20.6 | 21.6 | 33 | 3 |  |  | 211.5 | 298.4 | 277.3 | 238.9 | 317.3 | 343.7 | 290.9
2010.2 | 310.2 | 136.1 | 54.44 | 63.6372 | 101.5 | 108.9 | 115 | 119.2 | 160.6 | 20.7 | 21.6 | 33.1 | 3.1 |  |  | 211.6 | 295.7 | 280.2 | 239.1 | 313.5 | 350 | 293.8
2011.2 | 311.2 | 139.2 | 55.68 | 65.0867 | 101.5 | 109.4 | 115.1 | 119.3 | 159.6 | 20.8 | 21.6 | 33.1 | 2.3 |  |  | 211.7 | 291.9 | 282.4 | 239.3 | 309.5 | 355.7 | 296.6
2012.2 | 312.2 | 137 | 54.8 | 64.058 | 101.5 | 109.9 | 115.3 | 119.5 | 159 | 20.8 | 21.6 | 33.1 | 2.6 |  |  | 211.8 | 289 | 285.7 | 239.4 | 305.8 | 362.7 | 298.3
2013.2 | 313.2 | 136.5 | 54.6 | 63.8243 | 101.7 | 109.6 | 115.5 | 119.5 | 159.2 | 20.8 | 21.6 | 33.2 | 1.8 |  |  | 211.9 | 288.4 | 290.4 | 239.6 | 307.6 | 372 | 299.7
2014.2 | 314.2 | 138.5 | 55.4 | 64.7594 | 102.1 | 109.9 | 115.8 | 119.1 | 159.2 | 20.8 | 21.6 | 33.1 | 2.3 |  |  | 211.9 | 287.3 | 287.8 | 239.8 | 306 | 371.6 | 297.8
2015.2 | 315.2 | 140.1 | 56.04 | 65.5075 | 101.9 | 110.3 | 116.1 | 119.1 | 159.6 | 20.8 | 21.6 | 33.2 | 2.5 |  |  | 212 | 292.7 | 287.9 | 239.9 | 309.8 | 367.6 | 294.9
2016.2 | 316.2 | 137.7 | 55.08 | 64.3853 | 101.5 | 110.6 | 116.2 | 119.1 | 159.7 | 20.8 | 21.6 | 33.3 | 2.2 |  |  | 212 | 296.7 | 286.2 | 240.1 | 314.4 | 366.1 | 291
2017.2 | 317.2 | 138.2 | 55.28 | 64.6191 | 101.1 | 110.7 | 116.2 | 118.9 | 161.6 | 20.8 | 21.6 | 33.2 | 2 |  |  | 212.1 | 301.6 | 282.2 | 240.3 | 318.1 | 361.7 | 289.1
2018.2 | 318.2 | 134.1 | 53.64 | 62.7021 | 101 | 110.9 | 116 | 118.8 | 161.6 | 20.8 | 21.6 | 33.2 | 2.3 |  |  | 212.1 | 303.5 | 278.6 | 240.5 | 317.8 | 353.9 | 286
2019.2 | 319.2 | 134.1 | 53.64 | 62.7021 | 101.8 | 111.2 | 116.2 | 118.7 | 159.5 | 20.8 | 21.6 | 33.3 | 2.3 |  |  | 212.2 | 302.8 | 279.3 | 240.7 | 314.7 | 349 | 287.7
2020.2 | 320.2 | 135 | 54 | 63.1229 | 102.8 | 111.5 | 116.5 | 118.5 | 158.9 | 20.8 | 21.6 | 33.3 | 2.2 |  |  | 212.2 | 302.3 | 285.5 | 240.9 | 316.3 | 355.2 | 291
2021.2 | 321.2 | 139.5 | 55.8 | 65.227 | 103.3 | 111.7 | 117 | 118.2 | 160.6 | 20.8 | 21.6 | 33.3 | 1.9 |  |  | 212.3 | 302.7 | 293.2 | 241.1 | 317.9 | 362.9 | 297.3
2022.2 | 322.2 | 136.2 | 54.48 | 63.684 | 103 | 111.6 | 117 | 118.1 | 160.2 | 20.8 | 21.6 | 33.3 | 1.9 |  |  | 212.3 | 303.5 | 297.7 | 241.3 | 321.3 | 367 | 300.5
2023.2 | 323.2 | 136.3 | 54.52 | 63.7307 | 103.3 | 111.8 | 117 | 118.1 | 159.2 | 20.8 | 21.6 | 33.4 | 1.7 |  |  | 212.4 | 303.4 | 294.9 | 241.5 | 315.4 | 364.1 | 297.2
2024.2 | 324.2 | 139 | 55.6 | 64.9932 | 103.7 | 112.3 | 116.8 | 118.3 | 157.3 | 20.9 | 21.6 | 33.4 | 1.3 |  |  | 212.5 | 304.1 | 293.3 | 241.7 | 312.6 | 357.7 | 294.2
2025.2 | 325.2 | 138.5 | 55.4 | 64.7594 | 104.1 | 112 | 116.7 | 118.6 | 156.5 | 20.9 | 21.6 | 33.4 | 1.4 |  |  | 212.6 | 303.4 | 290.8 | 241.9 | 313.7 | 363.9 | 295.4
2026.2 | 326.2 | 137.7 | 55.08 | 64.3853 | 104.3 | 111.4 | 117 | 118.7 | 157.8 | 20.9 | 21.6 | 33.3 | 1.1 |  |  | 212.7 | 302.5 | 289.2 | 242.1 | 313.2 | 363.4 | 294.8
2027.2 | 327.2 | 137.5 | 55 | 64.2918 | 104.2 | 111.3 | 117 | 118.8 | 158.8 | 21 | 21.6 | 33.4 | 1 |  |  | 212.8 | 302.5 | 288.9 | 242.3 | 315.2 | 371.8 | 297.3
2028.2 | 328.2 | 137.6 | 55.04 | 64.3386 | 103.6 | 111.2 | 117.2 | 118.7 | 161.9 | 21 | 21.6 | 33.5 | 0.8 |  |  | 212.9 | 304 | 291.2 | 242.6 | 318.6 | 378 | 296.7
2029.2 | 329.2 | 136 | 54.4 | 63.5905 | 103.2 | 111.3 | 117.1 | 118.6 | 164 | 21 | 21.6 | 33.5 | 0.7 |  |  | 213 | 302.7 | 294.7 | 242.8 | 318.9 | 385.4 | 300.2
2030.2 | 330.2 | 139.8 | 55.92 | 65.3673 | 103.3 | 111.1 | 117 | 118.5 | 164.2 | 21 | 21.6 | 33.7 | 1.1 |  |  | 213.1 | 303.5 | 300.2 | 243 | 323.5 | 389.2 | 302.6
2031.2 | 331.2 | 141.8 | 56.72 | 66.3024 | 103.5 | 111 | 116.6 | 118.6 | 164.1 | 21 | 21.6 | 33.8 | 1.4 |  |  | 213.2 | 305.8 | 305.6 | 243.2 | 329.6 | 394.2 | 303.4
2032.2 | 332.2 | 140.8 | 56.32 | 65.8348 | 103.8 | 111 | 116.5 | 118.5 | 164.1 | 21 | 21.6 | 34 | 1.5 |  |  | 213.3 | 301.7 | 310.9 | 243.5 | 323.7 | 389.5 | 306
2033.3 | 333.3 | 139.1 | 55.64 | 65.04 | 104 | 111 | 117 | 118.5 | 164.1 | 21.1 | 21.6 | 34.1 | 2 |  |  | 213.5 | 310.3 | 314.5 | 243.8 | 328.7 | 393.1 | 308.7
2034.3 | 334.3 | 140.5 | 56.2 | 65.6946 | 103.5 | 110.9 | 117.4 | 119 | 166.2 | 21.2 | 21.6 | 34.1 | 1.8 |  |  | 213.6 | 312.1 | 317.6 | 244.1 | 332.3 | 396.9 | 307
2035.3 | 335.3 | 137.1 | 54.84 | 64.1048 | 103.4 | 111 | 117.5 | 119.8 | 166.1 | 21.3 | 21.6 | 34.1 | 1.5 |  |  | 213.7 | 313.2 | 314.7 | 244.5 | 334.2 | 391 | 303.4
2036.3 | 336.3 | 140 | 56 | 65.4608 | 103.7 | 111.3 | 117.2 | 120.2 | 166 | 21.4 | 21.6 | 34 | 1.7 |  |  | 213.9 | 316.9 | 317.1 | 244.9 | 337.9 | 387 | 301.5
2037.3 | 337.3 | 138.3 | 55.32 | 64.6659 | 103.9 | 111.3 | 117.3 | 120.2 | 165.2 | 21.4 | 21.6 | 34.1 | 2 |  |  | 214 | 317 | 323.6 | 245.3 | 338.7 | 381.7 | 302.7
2038.3 | 338.3 | 138.4 | 55.36 | 64.7127 | 103.5 | 111.3 | 117.7 | 120.3 | 165.7 | 21.4 | 21.6 | 34.1 | 2.1 |  |  | 214.2 | 316.3 | 331 | 245.7 | 335.6 | 377.6 | 303
2039.3 | 339.3 | 140.1 | 56.04 | 65.5075 | 103.5 | 111.9 | 118 | 120.5 | 165.8 | 21.5 | 21.6 | 34.1 | 2.1 |  |  | 214.4 | 316.1 | 341.9 | 246.1 | 331.6 | 378.2 | 307.9
2040.3 | 340.3 | 140.4 | 56.16 | 65.6478 | 103.8 | 112.3 | 118.5 | 120.9 | 169.4 | 21.5 | 21.6 | 34.2 | 2 |  |  | 214.6 | 315.9 | 354.7 | 246.6 | 330.7 | 383 | 314.6
2041.3 | 341.3 | 140.6 | 56.24 | 65.7413 | 104.1 | 112 | 118.6 | 121.2 | 171.2 | 21.5 | 21.6 | 34.2 | 1.8 |  |  | 214.8 | 315.6 | 354.5 | 247 | 332.8 | 390.4 | 320.2
2042.3 | 342.3 | 139.6 | 55.84 | 65.2737 | 104.2 | 111.6 | 118.8 | 121.4 | 169.9 | 21.5 | 21.6 | 34.2 | 2.1 |  |  | 215.1 | 309.6 | 352.3 | 247.4 | 330.1 | 394 | 319
2043.3 | 343.3 | 139.3 | 55.72 | 65.1335 | 104.7 | 111.6 | 118.9 | 121.6 | 168 | 21.5 | 21.6 | 34.3 | 2.3 |  |  | 215.4 | 302.9 | 347.7 | 247.7 | 323.4 | 394.2 | 317.9
2044.3 | 344.3 | 138.1 | 55.24 | 64.5724 | 105.2 | 111.6 | 119.4 | 122.3 | 164.8 | 21.5 | 21.6 | 34.3 | 2 |  |  | 215.8 | 299.7 | 342.6 | 248.1 | 320.6 | 395.7 | 313.8
2045.3 | 345.3 | 138.7 | 55.48 | 64.8529 | 105 | 112.1 | 119.4 | 122.5 | 165.2 | 21.5 | 21.6 | 34.3 | 2.3 |  |  | 216.1 | 297.9 | 334.7 | 248.4 | 320 | 399.4 | 310.9
2046.3 | 346.3 | 137.8 | 55.12 | 64.4321 | 104 | 112.3 | 119.1 | 122.5 | 165.6 | 21.5 | 21.6 | 34.3 | 1.9 |  |  | 216.5 | 296.6 | 325 | 248.8 | 319.4 | 400.8 | 307.5
2047.3 | 347.3 | 137.7 | 55.08 | 64.3853 | 103.3 | 112.4 | 118.6 | 122.8 | 167.3 | 21.5 | 21.6 | 34.4 | 2 |  |  | 216.9 | 299.3 | 324.2 | 249.1 | 320.4 | 398.4 | 305.7
2048.3 | 348.3 | 140.4 | 56.16 | 65.6478 | 102.7 | 112.5 | 118 | 122.9 | 167.2 | 21.5 | 21.6 | 34.4 | 1.9 |  |  | 217.2 | 301.5 | 325 | 249.4 | 321.8 | 400.3 | 306.5
2049.3 | 349.3 | 138.6 | 55.44 | 64.8062 | 103 | 113.1 | 117.9 | 122.5 | 167.5 | 21.5 | 21.6 | 34.3 | 1.8 |  |  | 217.6 | 299.6 | 330.9 | 249.7 | 321.6 | 410 | 312.8
2050.3 | 350.3 | 137 | 54.8 | 64.058 | 103.5 | 113.2 | 118.1 | 122.4 | 166.2 | 21.4 | 21.6 | 34.3 | 1.7 |  |  | 217.8 | 295.2 | 334.7 | 250 | 314.5 | 408.7 | 316.6
2051.3 | 351.3 | 140.5 | 56.2 | 65.6946 | 103.4 | 113.2 | 118.3 | 122.2 | 163.9 | 21.4 | 21.6 | 34.3 | 2 |  |  | 218.1 | 294.7 | 337.6 | 250.3 | 313.6 | 405.1 | 319
2052.3 | 352.3 | 141.2 | 56.48 | 66.0219 | 103.8 | 113.3 | 118.8 | 122.2 | 163.3 | 21.4 | 21.6 | 34.4 | 2.2 |  |  | 218.4 | 295.6 | 335.9 | 250.5 | 315.5 | 407.7 | 317.8
2053.3 | 353.3 | 139.5 | 55.8 | 65.227 | 103.3 | 113.5 | 119.3 | 122.1 | 161.6 | 21.4 | 21.6 | 34.6 | 3.1 |  |  | 218.7 | 293.7 | 333.5 | 250.8 | 314.4 | 409.4 | 317.6
2054.3 | 354.3 | 140 | 56 | 65.4608 | 103.3 | 113.8 | 119.5 | 122.3 | 161.2 | 21.4 | 21.6 | 34.6 | 3 |  |  | 218.9 | 291.1 | 334.4 | 251 | 311 | 411.3 | 319.7
2055.3 | 355.3 | 139.8 | 55.92 | 65.3673 | 103.3 | 114.2 | 119.7 | 122.3 | 160.7 | 21.3 | 21.6 | 34.6 | 2.3 |  |  | 219.1 | 287.5 | 328.7 | 251.1 | 306.6 | 407 | 318.6
2056.3 | 356.3 | 138.2 | 55.28 | 64.6191 | 102.9 | 114.6 | 119.6 | 122.4 | 159.8 | 21.3 | 21.6 | 34.6 | 2.2 |  |  | 219.4 | 290.4 | 324.4 | 251.4 | 310.3 | 409.6 | 316.3
2057.3 | 357.3 | 138.2 | 55.28 | 64.6191 | 103.2 | 114.9 | 120 | 122.6 | 161.4 | 21.3 | 21.6 | 34.7 | 1.9 |  |  | 219.6 | 295.8 | 320.2 | 251.6 | 317.2 | 413.2 | 316.1
2058.3 | 358.3 | 136.5 | 54.6 | 63.8243 | 103 | 114.9 | 120.4 | 122.7 | 163.9 | 21.3 | 21.6 | 34.7 | 1.8 |  |  | 219.8 | 310.7 | 325 | 251.8 | 329.3 | 410.9 | 315.3
2059.3 | 359.3 | 139.9 | 55.96 | 65.414 | 102.2 | 114.6 | 120.7 | 122.7 | 166.1 | 21.3 | 21.6 | 34.7 | 1.8 |  |  | 220.1 | 314.7 | 329.2 | 251.8 | 333.5 | 407.5 | 313.2
2060.3 | 360.3 | 139.2 | 55.68 | 65.0867 | 102.2 | 114.7 | 121.1 | 122.9 | 169.8 | 21.3 | 21.6 | 34.8 | 1.9 |  |  | 220.3 | 314 | 325.2 | 251.7 | 332.9 | 402.2 | 310.5
2061.3 | 361.3 | 137.8 | 55.12 | 64.4321 | 103.1 | 115 | 121.3 | 122.9 | 169.6 | 21.2 | 21.6 | 34.8 | 1.5 |  |  | 220.5 | 316.1 | 321 | 251.6 | 332.7 | 400.9 | 307.3
2062.3 | 362.3 | 137.4 | 54.96 | 64.2451 | 103.9 | 114.8 | 121.3 | 123 | 170.7 | 21.2 | 21.6 | 34.8 | 1.5 |  |  | 220.7 | 315.7 | 316.8 | 251.6 | 331.5 | 398.5 | 304.4
2063.3 | 363.3 | 139.7 | 55.88 | 65.3205 | 104.6 | 114.7 | 121.4 | 123.1 | 172.1 | 21.2 | 21.6 | 34.8 | 1.8 |  |  | 220.9 | 310.9 | 312.5 | 251.6 | 327.6 | 395.1 | 305.3
2064.3 | 364.3 | 141 | 56.4 | 65.9284 | 104.6 | 114.7 | 121 | 123.4 | 171.3 | 21.2 | 21.6 | 34.9 | 2.3 |  |  | 221.1 | 307.8 | 307.7 | 252.1 | 324.1 | 393.9 | 304.3
2065.3 | 365.3 | 141.8 | 56.72 | 66.3024 | 104.6 | 114.7 | 120.8 | 123.6 | 170.1 | 21.2 | 21.6 | 35 | 2.7 |  |  | 221.4 | 307.6 | 304.7 | 252.6 | 324.9 | 400.1 | 306.2
2066.3 | 366.3 | 142.1 | 56.84 | 66.4427 | 104.9 | 114.8 | 120.9 | 123.5 | 170.4 | 21.2 | 21.6 | 35.1 | 3.3 |  |  | 221.6 | 309.4 | 307.4 | 252.6 | 328.1 | 408.7 | 311.1
2067.3 | 367.3 | 141.8 | 56.72 | 66.3024 | 105.3 | 115.4 | 121 | 123.4 | 170.2 | 21.3 | 21.6 | 35.1 | 3.4 |  |  | 221.8 | 307.3 | 301.7 | 252.4 | 325.6 | 406.3 | 309.5
2068.3 | 368.3 | 141.3 | 56.52 | 66.0686 | 105.8 | 115.7 | 120.9 | 123.2 | 168.2 | 21.4 | 21.6 | 35.2 | 3.3 |  |  | 222 | 305.2 | 297.1 | 252.2 | 323.8 | 406.2 | 308.4
2069.3 | 369.3 | 141.8 | 56.72 | 66.3024 | 106.3 | 115.9 | 121.1 | 122.6 | 168.3 | 21.5 | 21.6 | 35.2 | 3.8 |  |  | 222.3 | 303.6 | 296.7 | 252.2 | 322.9 | 403.8 | 307.4
2070.3 | 370.3 | 141.4 | 56.56 | 66.1154 | 106.2 | 115.9 | 121.2 | 122.5 | 167.8 | 21.5 | 21.6 | 35.2 | 3.1 |  |  | 222.5 | 311.2 | 304.1 | 252.3 | 327.9 | 403.1 | 313.7
2071.3 | 371.3 | 139 | 55.6 | 64.9932 | 105.6 | 115.7 | 121.3 | 122.4 | 167.2 | 21.6 | 21.6 | 35.3 | 3.1 |  |  | 222.7 | 311.4 | 307.9 | 252.4 | 326.6 | 401 | 316.1
2072.3 | 372.3 | 136.6 | 54.64 | 63.871 | 105.3 | 115.4 | 121.4 | 122.2 | 166.2 | 21.6 | 21.6 | 35.3 | 3.3 |  |  | 222.9 | 312.7 | 312 | 252.8 | 326 | 403.1 | 318.1
2073.3 | 373.3 | 140.1 | 56.04 | 65.5075 | 105.2 | 114.8 | 121.5 | 121.5 | 168 | 21.7 | 21.5 | 35.3 | 2.9 |  |  | 223.2 | 310.7 | 312.4 | 253.1 | 325.4 | 399.6 | 314.9
2074.3 | 374.3 | 139.4 | 55.76 | 65.1802 | 105.1 | 114 | 121.6 | 121.4 | 167.8 | 21.7 | 21.6 | 35.3 | 2 |  |  | 223.4 | 311 | 311.6 | 253.4 | 326.5 | 391.4 | 312.4
2075.3 | 375.3 | 140 | 56 | 65.4608 | 104.8 | 113.8 | 121.4 | 121.4 | 167.6 | 21.7 | 21.6 | 35.2 | 1.6 |  |  | 223.6 | 310.1 | 303.7 | 253.6 | 325.7 | 387.1 | 310.1
2076.3 | 376.3 | 138.5 | 55.4 | 64.7594 | 104.5 | 113.7 | 121.4 | 121.4 | 167.2 | 21.7 | 21.6 | 35.2 | 1.5 |  |  | 223.8 | 318.3 | 300.7 | 253.7 | 331.5 | 385.3 | 309.3
2077.3 | 377.3 | 141.4 | 56.56 | 66.1154 | 104 | 113 | 121.5 | 121.4 | 167 | 21.7 | 21.6 | 35.2 | 1.4 |  |  | 224.1 | 316.2 | 297.7 | 254 | 324.6 | 375.7 | 306.9
2078.3 | 378.3 | 137.4 | 54.96 | 64.2451 | 104.2 | 112.7 | 121.5 | 121.4 | 164.7 | 21.7 | 21.6 | 35.1 | 1.2 |  |  | 224.3 | 316.8 | 295.9 | 254.2 | 322.2 | 368.3 | 304.1
2079.3 | 379.3 | 139.8 | 55.92 | 65.3673 | 104.5 | 112.8 | 121.6 | 121.5 | 163.9 | 21.7 | 21.5 | 35.1 | 1.4 |  |  | 224.6 | 319.7 | 295.5 | 254.3 | 326 | 367.5 | 302
2080.3 | 380.3 | 140 | 56 | 65.4608 | 104.7 | 112.8 | 122.1 | 121.6 | 166.5 | 21.6 | 21.5 | 35.1 | 1.9 |  |  | 224.8 | 324.1 | 298.4 | 254.5 | 333.3 | 367.5 | 302.7
2081.3 | 381.3 | 138.1 | 55.24 | 64.5724 | 105.5 | 113.3 | 122.4 | 121.6 | 168.7 | 21.6 | 21.5 | 35.1 | 1.6 |  |  | 225 | 327.9 | 301.6 | 254.6 | 337 | 364.8 | 304.7
2082.3 | 382.3 | 138.6 | 55.44 | 64.8062 | 106.2 | 113.9 | 122.3 | 121.4 | 168.3 | 21.6 | 21.5 | 35.2 | 1.6 |  |  | 225.3 | 326.7 | 302 | 254.7 | 335.2 | 362.4 | 304.6
2083.3 | 383.3 | 137.1 | 54.84 | 64.1048 | 106.2 | 114.7 | 122.2 | 121.4 | 167.1 | 21.6 | 21.5 | 35.3 | 2.1 |  |  | 225.5 | 322 | 296.5 | 254.8 | 331.3 | 357.8 | 302.1
2084.3 | 384.3 | 138 | 55.2 | 64.5256 | 105.9 | 115 | 122.3 | 121.6 | 164.9 | 21.6 | 21.5 | 35.3 | 1.9 |  |  | 225.8 | 319.5 | 297.4 | 255.4 | 327.7 | 360.2 | 303.1
2085.3 | 385.3 | 139.5 | 55.8 | 65.227 | 105.8 | 115.3 | 122.1 | 121.7 | 164.7 | 21.6 | 21.5 | 35.3 | 1.4 |  |  | 226 | 324 | 302.8 | 256.4 | 330.8 | 360.9 | 305.3
2086.3 | 386.3 | 141 | 56.4 | 65.9284 | 105.7 | 115.5 | 121.7 | 121.9 | 165.2 | 21.7 | 21.5 | 35.3 | 1.3 |  |  | 226.3 | 321.8 | 299.4 | 257.2 | 326 | 358.7 | 302.4
2087.3 | 387.3 | 140.2 | 56.08 | 65.5543 | 105.7 | 115.8 | 121.6 | 122 | 165.2 | 21.8 | 21.5 | 35.4 | 1.7 |  |  | 226.6 | 321.4 | 301.1 | 257.9 | 324.9 | 359.3 | 303
2088.3 | 388.3 | 138.8 | 55.52 | 64.8997 | 106 | 115.8 | 121.3 | 121.9 | 164.9 | 21.9 | 21.5 | 35.5 | 1.9 |  |  | 226.9 | 322.6 | 298.3 | 258.4 | 322.2 | 353.5 | 299
2089.3 | 389.3 | 139.5 | 55.8 | 65.227 | 106.5 | 115.8 | 120.9 | 122 | 163.5 | 21.9 | 21.5 | 35.6 | 1.6 |  |  | 227.2 | 320.7 | 295.6 | 258.8 | 316.2 | 348.3 | 295.6
2090.3 | 390.3 | 139 | 55.6 | 64.9932 | 106.6 | 115.6 | 120.6 | 122.4 | 161.5 | 21.9 | 21.5 | 35.6 | 1.5 |  |  | 227.5 | 315.3 | 296.4 | 259.2 | 310.8 | 342.3 | 297.1
2091.3 | 391.3 | 140 | 56 | 65.4608 | 105.8 | 114.9 | 120.3 | 122.5 | 159.8 | 22 | 21.5 | 35.5 | 1.6 |  |  | 227.8 | 316.5 | 297.3 | 259.6 | 310.1 | 339.2 | 301.7
2092.3 | 392.3 | 139.7 | 55.88 | 65.3205 | 105.1 | 114.4 | 120 | 122.2 | 160.2 | 22.1 | 21.5 | 35.6 | 1.5 |  |  | 228.1 | 313 | 294.3 | 259.9 | 309.9 | 339.6 | 299.3
2093.3 | 393.3 | 137.6 | 55.04 | 64.3386 | 104.8 | 113.8 | 119.9 | 122.2 | 160.3 | 22.2 | 21.5 | 35.5 | 1.5 |  |  | 228.4 | 310.1 | 292.9 | 260.1 | 307.5 | 335.7 | 296.5
2094.3 | 394.3 | 136.9 | 54.76 | 64.0113 | 104.7 | 113.7 | 120.2 | 122 | 157.6 | 22.2 | 21.5 | 35.5 | 1.2 |  |  | 228.7 | 307.5 | 294.5 | 260.3 | 307.6 | 340.6 | 299.1
2095.3 | 395.3 | 139.2 | 55.68 | 65.0867 | 105.2 | 113.7 | 120.2 | 121.8 | 156.7 | 22.3 | 21.5 | 35.5 | 1.2 |  |  | 228.9 | 307.7 | 303.2 | 260.4 | 308.4 | 345.4 | 304.9
2096.3 | 396.3 | 139.9 | 55.96 | 65.414 | 105.3 | 113.5 | 119.5 | 121.6 | 158.5 | 22.4 | 21.5 | 35.6 | 1.3 |  |  | 229.2 | 310.4 | 305.3 | 260.5 | 310.1 | 349.4 | 307.5
2097.3 | 397.3 | 138.9 | 55.56 | 64.9464 | 105.3 | 113.3 | 119.1 | 121.4 | 159.1 | 22.4 | 21.5 | 35.7 | 1.7 |  |  | 229.4 | 308.4 | 304.1 | 260.5 | 307.5 | 352.8 | 305.5
2098.3 | 398.3 | 138.9 | 55.56 | 64.9464 | 105.9 | 113.6 | 119 | 121.2 | 158.2 | 22.4 | 21.5 | 35.8 | 1.8 |  |  | 229.7 | 310.4 | 305.3 | 260.5 | 307.9 | 355.2 | 304.3
2099.3 | 399.3 | 139.9 | 55.96 | 65.414 | 106.2 | 113.7 | 118.8 | 121 | 157.5 | 22.4 | 21.5 | 36 | 2 |  |  | 229.9 | 305.6 | 302.2 | 260.4 | 306.2 | 357.2 | 302.7
2100.3 | 400.3 | 140.6 | 56.24 | 65.7413 | 106.8 | 113.4 | 118.2 | 120.9 | 158.6 | 22.4 | 21.5 | 36.1 | 1.6 |  |  | 230.2 | 299.8 | 300.9 | 260.2 | 302.5 | 357.9 | 299.4
2101.3 | 401.3 | 135.8 | 54.32 | 63.497 | 106.6 | 112.8 | 118.3 | 120.8 | 159.3 | 22.4 | 21.5 | 36.1 | 1.4 |  |  | 230.4 | 298.8 | 304.3 | 260 | 304 | 362.6 | 299.8
2102.3 | 402.3 | 138.7 | 55.48 | 64.8529 | 106.3 | 112.7 | 118.1 | 120.5 | 160.2 | 22.4 | 21.5 | 36.1 | 1.5 |  |  | 230.7 | 294.8 | 306.3 | 259.7 | 300.4 | 363 | 303.1
2103.3 | 403.3 | 137.7 | 55.08 | 64.3853 | 106.4 | 112.2 | 118 | 120.5 | 160 | 22.4 | 21.5 | 36.1 | 1.7 |  |  | 230.9 | 294 | 306.5 | 259.4 | 300.3 | 360.9 | 302.4
2104.3 | 404.3 | 140.5 | 56.2 | 65.6946 | 105.9 | 111.8 | 117.9 | 120.2 | 159.4 | 22.3 | 21.5 | 36 | 1.4 |  |  | 231.1 | 294.1 | 300.8 | 259.1 | 298.9 | 361 | 299.8
2105.3 | 405.3 | 137.8 | 55.12 | 64.4321 | 105.3 | 111.8 | 117.9 | 119.9 | 158.6 | 22.3 | 21.5 | 36 | 1.3 |  |  | 231.3 | 292 | 298.7 | 259.2 | 294 | 353.3 | 298.2
2106.3 | 406.3 | 137.7 | 55.08 | 64.3853 | 105.3 | 111.5 | 117.9 | 119.9 | 158.5 | 22.3 | 21.5 | 36 | 1.3 |  |  | 231.5 | 294.6 | 305.1 | 259.6 | 297.9 | 356.6 | 300.1
2107.3 | 407.3 | 137.5 | 55 | 64.2918 | 105.4 | 111.6 | 117.9 | 120.2 | 159.5 | 22.3 | 21.5 | 36 | 1.1 |  |  | 231.7 | 300.9 | 305.7 | 259.9 | 299.8 | 353.3 | 304.4
2108.3 | 408.3 | 140.5 | 56.2 | 65.6946 | 105.2 | 111.9 | 117.9 | 120.4 | 159.8 | 22.4 | 21.5 | 36 | 1 |  |  | 231.9 | 301.5 | 302.4 | 260.3 | 299.2 | 345.5 | 302
2109.3 | 409.3 | 140 | 56 | 65.4608 | 105.2 | 112.3 | 117.9 | 120.5 | 158.3 | 22.5 | 21.5 | 36 | 1.1 |  |  | 232.1 | 303.1 | 297.4 | 260.6 | 302.3 | 336.4 | 297.4
2110.3 | 410.3 | 136.9 | 54.76 | 64.0113 | 105 | 112.7 | 117.9 | 120.5 | 158 | 22.6 | 21.5 | 36.1 | 1.6 |  |  | 232.2 | 305.3 | 299.4 | 260.8 | 302.1 | 331.9 | 295.9
2111.3 | 411.3 | 139.3 | 55.72 | 65.1335 | 104.8 | 112.8 | 117.8 | 120.5 | 157.6 | 22.6 | 21.5 | 36.2 | 1.4 |  |  | 232.4 | 307.8 | 307.7 | 260.8 | 304.8 | 332.5 | 300.9
2112.3 | 412.3 | 138.3 | 55.32 | 64.6659 | 104.7 | 112.6 | 117.9 | 120.5 | 157.1 | 22.7 | 21.5 | 36.2 | 1.7 |  |  | 232.6 | 305.6 | 314.6 | 260.9 | 302.6 | 329.3 | 304.7
2113.3 | 413.3 | 137.8 | 55.12 | 64.4321 | 105.4 | 112.7 | 117.9 | 120.5 | 156.6 | 22.7 | 21.5 | 36.3 | 1.6 |  |  | 232.8 | 302.2 | 311.2 | 261 | 298.5 | 327.9 | 303.5
2114.3 | 414.3 | 138.4 | 55.36 | 64.7127 | 106.5 | 112.7 | 118 | 120.5 | 155.5 | 22.7 | 21.5 | 36.4 | 1.7 |  |  | 233 | 301.5 | 312.3 | 261.1 | 297 | 329.3 | 304.1
2115.3 | 415.3 | 134.9 | 53.96 | 63.0761 | 106.9 | 112.9 | 117.7 | 120.5 | 155.4 | 22.7 | 21.5 | 36.4 | 1.4 |  |  | 233.2 | 296 | 311.8 | 261.1 | 290.5 | 330.5 | 305.2
2116.3 | 416.3 | 136 | 54.4 | 63.5905 | 107 | 112.9 | 117.7 | 120.4 | 154.4 | 22.7 | 21.5 | 36.5 | 1.9 |  |  | 233.5 | 293.5 | 309.8 | 261.1 | 289.1 | 334.9 | 307.6
2117.3 | 417.3 | 136 | 54.4 | 63.5905 | 106.9 | 112.9 | 117.7 | 120.5 | 154.1 | 22.7 | 21.5 | 36.6 | 1.8 |  |  | 233.7 | 288.6 | 309 | 261.1 | 284.8 | 343.6 | 306.6
2118.3 | 418.3 | 137.6 | 55.04 | 64.3386 | 106.4 | 112.7 | 117.5 | 120.7 | 154.7 | 22.7 | 21.5 | 36.5 | 1.5 |  |  | 234 | 287.8 | 313.7 | 261 | 287.1 | 346.2 | 307.9
2119.3 | 419.3 | 133.7 | 53.48 | 62.515 | 105.4 | 112.7 | 117.3 | 120.8 | 156.4 | 22.7 | 21.5 | 36.5 | 1.3 |  |  | 234.2 | 291.4 | 319.5 | 261 | 291.5 | 348.7 | 310.7
2120.3 | 420.3 | 135.9 | 54.36 | 63.5437 | 104.8 | 113 | 117.2 | 120.8 | 156.7 | 22.8 | 21.5 | 36.6 | 1.4 |  |  | 234.5 | 292.4 | 320.4 | 261.1 | 293.7 | 347.6 | 310.4
2121.3 | 421.3 | 139.6 | 55.84 | 65.2737 | 104.8 | 113.5 | 117.2 | 120.7 | 155.8 | 22.8 | 21.5 | 36.6 | 1.5 |  |  | 234.8 | 294.7 | 318.7 | 261.2 | 293.3 | 347.4 | 306
2122.3 | 422.3 | 135.6 | 54.24 | 63.4034 | 105.3 | 113.6 | 117.4 | 120.7 | 156.6 | 22.8 | 21.5 | 36.7 | 1.5 |  |  | 235 | 294.1 | 319.5 | 261.4 | 292.8 | 346.8 | 303.1
2123.3 | 423.3 | 136.6 | 54.64 | 63.871 | 105.4 | 113.4 | 117.4 | 120.7 | 156.2 | 22.7 | 21.5 | 36.7 | 1.3 |  |  | 235.3 | 296 | 319.1 | 261.6 | 293.4 | 347.6 | 301.8
2124.3 | 424.3 | 139.8 | 55.92 | 65.3673 | 105.1 | 112.6 | 117.5 | 120.5 | 155.7 | 22.6 | 21.5 | 36.8 | 1.4 |  |  | 235.5 | 297.4 | 320.1 | 261.8 | 295.4 | 348.9 | 301.4
2125.3 | 425.3 | 136.6 | 54.64 | 63.871 | 105.1 | 112 | 117.6 | 120.4 | 156 | 22.7 | 21.5 | 36.9 | 1.7 |  |  | 235.7 | 299.7 | 322.3 | 261.9 | 299.9 | 354 | 305
2126.3 | 426.3 | 138.4 | 55.36 | 64.7127 | 105.2 | 112.1 | 117.6 | 120.6 | 157.6 | 22.8 | 21.5 | 36.9 | 1.7 |  |  | 235.9 | 297.1 | 321.1 | 261.9 | 297.4 | 355.9 | 307.3
2127.3 | 427.3 | 137.7 | 55.08 | 64.3853 | 105 | 111.9 | 117.8 | 120.5 | 157.8 | 22.9 | 21.5 | 36.9 | 1.4 |  |  | 236.2 | 296.6 | 317.4 | 262 | 299 | 357.1 | 304.4
2128.3 | 428.3 | 138 | 55.2 | 64.5256 | 104.7 | 112 | 117.7 | 120.2 | 158.9 | 23 | 21.5 | 36.8 | 1.6 |  |  | 236.4 | 296.4 | 316 | 262 | 298.5 | 356.8 | 305.3
2129.3 | 429.3 | 139.1 | 55.64 | 65.04 | 105.3 | 112.2 | 117.7 | 120.3 | 158.6 | 23.1 | 21.5 | 36.8 | 1.8 |  |  | 236.7 | 299.2 | 317.5 | 262 | 298.8 | 354.5 | 303.1
2130.3 | 430.3 | 139.3 | 55.72 | 65.1335 | 106 | 112.3 | 117.4 | 120.6 | 159.3 | 23.1 | 21.5 | 36.8 | 1.6 |  |  | 236.9 | 302 | 327.3 | 262.1 | 299.6 | 354.8 | 303.7
2131.3 | 431.3 | 138.6 | 55.44 | 64.8062 | 106.4 | 112.3 | 117.2 | 120.7 | 159.2 | 23.1 | 21.5 | 36.7 | 1.5 |  |  | 237.2 | 301.2 | 331.3 | 262.2 | 300.5 | 355.6 | 306.3
2132.3 | 432.3 | 139.1 | 55.64 | 65.04 | 106.7 | 112.1 | 117.2 | 120.7 | 158.6 | 23.1 | 21.5 | 36.8 | 1.5 |  |  | 237.4 | 304.2 | 330.6 | 262.3 | 303.1 | 359.5 | 307.5
2133.3 | 433.3 | 140.7 | 56.28 | 65.7881 | 107 | 112.2 | 117.7 | 120.7 | 158.5 | 23.1 | 21.5 | 36.8 | 1.5 |  |  | 237.7 | 300.8 | 326.4 | 262.4 | 302 | 360.8 | 305.1
2134.3 | 434.3 | 138 | 55.2 | 64.5256 | 107.2 | 112.5 | 117.9 | 120.9 | 157.8 | 23.1 | 21.5 | 36.8 | 1.9 |  |  | 237.9 | 300 | 328.3 | 262.4 | 303.2 | 362.4 | 307.2
2135.3 | 435.3 | 140.7 | 56.28 | 65.7881 | 107.6 | 112.9 | 118 | 121 | 157.3 | 23.1 | 21.5 | 37 | 1.8 |  |  | 238.2 | 299.4 | 323.6 | 262.5 | 303.3 | 360.2 | 307
2136.3 | 436.3 | 139.8 | 55.92 | 65.3673 | 107.6 | 113.2 | 118.1 | 120.9 | 157.9 | 23.2 | 21.5 | 37 | 1.9 |  |  | 238.5 | 304.3 | 321.3 | 262.6 | 305.8 | 356.5 | 305.1
2137.3 | 437.3 | 138.7 | 55.48 | 64.8529 | 107.7 | 113.2 | 118.2 | 120.6 | 159 | 23.2 | 21.5 | 37.1 | 1.7 |  |  | 238.7 | 313.3 | 320.9 | 262.8 | 310.9 | 360.4 | 306.4
2138.3 | 438.3 | 140.4 | 56.16 | 65.6478 | 108 | 112.8 | 118.4 | 120.6 | 158.7 | 23.2 | 21.5 | 37.2 | 1.7 |  |  | 239 | 310.4 | 316 | 263.2 | 308.7 | 351.8 | 302.7
2139.3 | 439.3 | 139 | 55.6 | 64.9932 | 107.9 | 112.1 | 118.5 | 120.5 | 158.1 | 23.1 | 21.5 | 37.2 | 1.6 |  |  | 239.2 | 307.3 | 310.9 | 263.7 | 305.2 | 344.6 | 298.9
2140.3 | 440.3 | 139.1 | 55.64 | 65.04 | 107.7 | 111.5 | 118.6 | 120.4 | 158.9 | 23 | 21.5 | 37.2 | 1.3 |  |  | 239.4 | 305.8 | 309.7 | 264.1 | 304.7 | 350.5 | 299
2141.3 | 441.3 | 138 | 55.2 | 64.5256 | 107.9 | 111.8 | 118.9 | 120.2 | 160.8 | 22.9 | 21.5 | 37.2 | 1.5 |  |  | 239.7 | 302.9 | 308 | 264.4 | 302.6 | 353.8 | 298.2
2142.3 | 442.3 | 139.9 | 55.96 | 65.414 | 107.5 | 112.2 | 119.2 | 119.8 | 161.1 | 22.8 | 21.5 | 37.2 | 1.5 |  |  | 239.9 | 301.6 | 309.2 | 264.7 | 301.1 | 356.8 | 298.4
2143.3 | 443.3 | 138.2 | 55.28 | 64.6191 | 107.1 | 112.4 | 119.4 | 119.7 | 161.2 | 22.8 | 21.5 | 37.2 | 1.5 |  |  | 240.1 | 299.3 | 307.5 | 264.9 | 300.6 | 361.2 | 300.4
2144.3 | 444.3 | 141.5 | 56.6 | 66.1621 | 106.5 | 112.4 | 119.3 | 119.6 | 161.7 | 22.7 | 21.5 | 37.1 | 1.1 |  |  | 240.3 | 298 | 309.8 | 265.1 | 305 | 370.7 | 304.9
2145.3 | 445.3 | 139.8 | 55.92 | 65.3673 | 106.1 | 112.4 | 118.9 | 119.5 | 162.5 | 22.7 | 21.5 | 37.1 | 1 |  |  | 240.4 | 297.5 | 312.1 | 265.4 | 304.5 | 373.9 | 311.2
2146.3 | 446.3 | 140.8 | 56.32 | 65.8348 | 105.8 | 112.1 | 118.6 | 119.6 | 163.3 | 22.6 | 21.5 | 37.1 | 1.4 |  |  | 240.6 | 299.5 | 311.6 | 265.7 | 308.3 | 377.8 | 309.6
2147.3 | 447.3 | 141.9 | 56.76 | 66.3492 | 105.2 | 112.3 | 118.5 | 119.8 | 164.7 | 22.6 | 21.5 | 37.2 | 1.5 |  |  | 240.9 | 300.2 | 310.9 | 266.2 | 306.1 | 374 | 306.4
2148.3 | 448.3 | 140.2 | 56.08 | 65.5543 | 104.6 | 112.7 | 118.5 | 120.2 | 162.6 | 22.7 | 21.5 | 37.3 | 1.7 |  |  | 241 | 299.6 | 311.1 | 266.6 | 304.9 | 377.1 | 304.6
2149.3 | 449.3 | 139.5 | 55.8 | 65.227 | 103.9 | 112.8 | 118.5 | 120.4 | 161.2 | 22.7 | 21.5 | 37.4 | 2 |  |  | 241.1 | 302.2 | 308.3 | 267.1 | 307.9 | 374.4 | 302.1
2150.3 | 450.3 | 139.5 | 55.8 | 65.227 | 103.4 | 112.9 | 118.7 | 120.6 | 162 | 22.8 | 21.5 | 37.4 | 2 |  |  | 241.3 | 303.4 | 305.1 | 267.7 | 307.3 | 367 | 298.7
2151.3 | 451.3 | 142.8 | 57.12 | 66.77 | 103 | 113.4 | 119 | 120.9 | 162.3 | 22.8 | 21.5 | 37.4 | 2.9 |  |  | 241.4 | 304.8 | 303.4 | 268.3 | 307.5 | 366.9 | 297.7
2152.3 | 452.3 | 143.6 | 57.44 | 67.1441 | 104 | 113.4 | 119.5 | 121 | 162.4 | 22.9 | 21.5 | 37.4 | 2.6 |  |  | 241.5 | 306.4 | 307.5 | 268.8 | 308.7 | 371.1 | 302.2
2153.3 | 453.3 | 143.8 | 57.52 | 67.2376 | 104.7 | 113 | 119.4 | 121.2 | 161.8 | 22.9 | 21.5 | 37.5 | 2.5 |  |  | 241.7 | 302.1 | 311.8 | 269.2 | 304.1 | 373.1 | 304.5
2154.3 | 454.3 | 142.6 | 57.04 | 66.6765 | 104.6 | 113.1 | 119.4 | 121.5 | 160.2 | 23 | 21.5 | 37.5 | 2.5 |  |  | 241.8 | 302.8 | 317.1 | 269.6 | 304.7 | 374.1 | 304.9
2155.3 | 455.3 | 142 | 56.8 | 66.3959 | 105.2 | 113.4 | 119.5 | 121.6 | 159.7 | 22.9 | 21.5 | 37.5 | 2.1 |  |  | 241.9 | 303.1 | 319.1 | 269.9 | 301.9 | 369.7 | 303.6
2156.3 | 456.3 | 141.8 | 56.72 | 66.3024 | 105.9 | 113.5 | 119.8 | 121.8 | 159.9 | 22.9 | 21.5 | 37.4 | 1.8 |  |  | 242 | 303.4 | 318.2 | 270.3 | 302.3 | 369.3 | 302.9
2157.3 | 457.3 | 140.8 | 56.32 | 65.8348 | 106 | 114 | 119.7 | 121.7 | 160.3 | 22.9 | 21.5 | 37.4 | 1.7 |  |  | 242 | 301.5 | 318.2 | 270.6 | 300.8 | 372.1 | 303.3
2158.3 | 458.3 | 139.8 | 55.92 | 65.3673 | 105.8 | 114 | 119.3 | 121.7 | 161.8 | 22.9 | 21.5 | 37.5 | 1.6 |  |  | 242.2 | 299.7 | 323.9 | 270.9 | 303 | 379.4 | 313
2159.3 | 459.3 | 139 | 55.6 | 64.9932 | 105.8 | 113.8 | 118.8 | 122.1 | 162.6 | 22.9 | 21.5 | 37.5 | 1.8 |  |  | 242.4 | 294.6 | 325.8 | 271.2 | 299.5 | 384 | 317.2
2160.3 | 460.3 | 141.1 | 56.44 | 65.9751 | 105.9 | 113.6 | 118.6 | 122.4 | 163.3 | 22.9 | 21.5 | 37.4 | 1.7 |  |  | 242.6 | 292.8 | 324.5 | 271.5 | 299.1 | 393 | 319.1
2161.3 | 461.3 | 138.5 | 55.4 | 64.7594 | 106.1 | 113.8 | 118.7 | 122.7 | 163.4 | 23 | 21.5 | 37.4 | 1.6 |  |  | 242.8 | 292.9 | 327.2 | 271.7 | 302.8 | 409.4 | 323.2
2162.3 | 462.3 | 143.5 | 57.4 | 67.0973 | 105.5 | 114.6 | 119 | 123 | 165.2 | 23 | 21.5 | 37.4 | 1.5 |  |  | 243.1 | 292.3 | 327.3 | 272 | 302.6 | 409.5 | 324.1
2163.3 | 463.3 | 139.9 | 55.96 | 65.414 | 105 | 115 | 119.5 | 123 | 167 | 23 | 21.5 | 37.4 | 1.5 |  |  | 243.4 | 300.1 | 331.3 | 272.3 | 309 | 414.8 | 323.5
2164.3 | 464.3 | 141.2 | 56.48 | 66.0219 | 105.3 | 115.3 | 119.8 | 123.2 | 169.5 | 23.1 | 21.5 | 37.4 | 1.4 |  |  | 243.6 | 304.7 | 332.5 | 272.6 | 313.8 | 410.5 | 322.6
2165.3 | 465.3 | 140.1 | 56.04 | 65.5075 | 106.1 | 115.7 | 120.2 | 123.2 | 171.7 | 23.1 | 21.5 | 37.6 | 1.6 |  |  | 243.8 | 303.8 | 336.4 | 273 | 311.5 | 409.1 | 322.4
2166.3 | 466.3 | 141.3 | 56.52 | 66.0686 | 106.8 | 115.5 | 120.4 | 123.1 | 170.1 | 23.1 | 21.5 | 37.6 | 1.6 |  |  | 243.9 | 301.2 | 341.6 | 273.4 | 307.6 | 406.9 | 321.9
2167.3 | 467.3 | 142.4 | 56.96 | 66.583 | 107.1 | 115.2 | 120.8 | 123 | 168.6 | 23.1 | 21.5 | 37.6 | 1.9 |  |  | 244.1 | 299.1 | 347.8 | 273.8 | 303.8 | 403.1 | 325.1
2168.3 | 468.3 | 137.2 | 54.88 | 64.1516 | 106.8 | 114.8 | 121.2 | 122.9 | 168.2 | 23.2 | 21.5 | 37.6 | 2.4 |  |  | 244.4 | 298 | 344.5 | 274.2 | 299.9 | 401.3 | 322.3
2169.3 | 469.3 | 140.3 | 56.12 | 65.601 | 106.3 | 114.6 | 121.2 | 123 | 166.3 | 23.2 | 21.5 | 37.6 | 2.8 |  |  | 244.7 | 299.2 | 344.1 | 274.6 | 300.1 | 399 | 321.2
2170.3 | 470.3 | 139.8 | 55.92 | 65.3673 | 106.2 | 114.6 | 121 | 123.2 | 164 | 23.2 | 21.5 | 37.6 | 3 |  |  | 244.9 | 301.9 | 339.1 | 275 | 298.6 | 394.4 | 319.1
2171.3 | 471.3 | 140.6 | 56.24 | 65.7413 | 106.3 | 115.3 | 121.3 | 123.8 | 163.8 | 23.2 | 21.5 | 37.7 | 3.4 |  |  | 245.2 | 304.4 | 345.1 | 275.3 | 300.8 | 394.3 | 319.2
2172.3 | 472.3 | 138.8 | 55.52 | 64.8997 | 106.6 | 115.9 | 121.7 | 124.2 | 164 | 23.3 | 21.5 | 37.7 | 3.2 |  |  | 245.5 | 304.4 | 349.1 | 275.6 | 301.3 | 396.6 | 321.7
2173.3 | 473.3 | 135.3 | 54.12 | 63.2632 | 106.6 | 115.8 | 121.7 | 124.4 | 163.9 | 23.4 | 21.5 | 37.7 | 2.6 |  |  | 245.8 | 300.5 | 351.5 | 275.8 | 299.5 | 395.3 | 323.9
2174.3 | 474.3 | 137.9 | 55.16 | 64.4789 | 107.1 | 115.5 | 121.9 | 124.4 | 164 | 23.4 | 21.5 | 37.7 | 2.6 |  |  | 246 | 294.8 | 354.5 | 276 | 295.7 | 394.5 | 325.7
2175.3 | 475.3 | 138.6 | 55.44 | 64.8062 | 106.9 | 116.4 | 122.1 | 124.3 | 162.5 | 23.5 | 21.5 | 37.8 | 2.5 |  |  | 246.3 | 290.4 | 353 | 276.3 | 292.4 | 395.7 | 325.2
2176.3 | 476.3 | 138.3 | 55.32 | 64.6659 | 106.6 | 116.9 | 122 | 124.3 | 161.8 | 23.5 | 21.5 | 37.8 | 2.1 |  |  | 246.6 | 287.7 | 358.9 | 276.5 | 291.1 | 395.3 | 329.3
2177.3 | 477.3 | 135.3 | 54.12 | 63.2632 | 105.8 | 117.2 | 121.6 | 124.9 | 165 | 23.5 | 21.5 | 37.8 | 1.6 |  |  | 246.8 | 289 | 358.5 | 276.7 | 291.1 | 396 | 329.5
2178.3 | 478.3 | 136.7 | 54.68 | 63.9178 | 105.9 | 117.5 | 121.4 | 125.4 | 166.5 | 23.5 | 21.5 | 37.8 | 1.9 |  |  | 247.1 | 291.3 | 360 | 276.9 | 291.8 | 396.7 | 328.2
2179.3 | 479.3 | 135.1 | 54.04 | 63.1696 | 106.3 | 117.9 | 121.5 | 125.6 | 167.6 | 23.5 | 21.5 | 37.9 | 1.7 |  |  | 247.3 | 294.5 | 363.5 | 277.1 | 294.7 | 389.9 | 325.8
2180.3 | 480.3 | 138.9 | 55.56 | 64.9464 | 106.9 | 118.2 | 121.2 | 125.7 | 169.4 | 23.5 | 21.5 | 37.9 | 1.7 |  |  | 247.6 | 294.3 | 366.6 | 277.3 | 292.1 | 386.9 | 325.9
2181.3 | 481.3 | 139.8 | 55.92 | 65.3673 | 107.4 | 118.3 | 121.1 | 125.8 | 169.6 | 23.6 | 21.5 | 38.1 | 1.7 |  |  | 247.8 | 293.1 | 357.9 | 277.4 | 288.9 | 372.2 | 321.1
2182.3 | 482.3 | 140 | 56 | 65.4608 | 107.4 | 118.6 | 121.5 | 125.7 | 167.5 | 23.6 | 21.5 | 38 | 1.6 |  |  | 248 | 293.1 | 349.3 | 277.6 | 286 | 363.1 | 315.6
2183.3 | 483.3 | 140.2 | 56.08 | 65.5543 | 108.2 | 119.1 | 121.7 | 125.4 | 165.9 | 23.6 | 21.5 | 38 | 1.6 |  |  | 248.2 | 292.9 | 344.1 | 277.8 | 284.8 | 353.9 | 313.5
2184.3 | 484.3 | 137.8 | 55.12 | 64.4321 | 108.7 | 119.1 | 121.8 | 125 | 165.7 | 23.7 | 21.5 | 38 | 1.7 |  |  | 248.5 | 297.1 | 340.5 | 278 | 284.9 | 346.8 | 312.1
2185.3 | 485.3 | 138.7 | 55.48 | 64.8529 | 108.8 | 119.2 | 122 | 124.8 | 165.8 | 23.7 | 21.5 | 38 | 1.8 |  |  | 248.8 | 298.6 | 336 | 278.2 | 283.8 | 340.8 | 310.1
2186.3 | 486.3 | 135.8 | 54.32 | 63.497 | 108.8 | 119.7 | 122.1 | 124.6 | 165.8 | 23.7 | 21.5 | 38.1 | 2.1 |  |  | 249.1 | 304.1 | 337.8 | 278.2 | 285.4 | 337.4 | 311.3
2187.3 | 487.3 | 140.8 | 56.32 | 65.8348 | 108.8 | 120.2 | 122 | 124.6 | 167.2 | 23.7 | 21.5 | 38.1 | 2.2 |  |  | 249.4 | 305.6 | 337.3 | 278.3 | 284.8 | 335.6 | 310.9
2188.3 | 488.3 | 140.7 | 56.28 | 65.7881 | 109.1 | 120.6 | 122.3 | 124.9 | 168.3 | 23.7 | 21.5 | 38.1 | 2.1 |  |  | 249.6 | 305.6 | 343.4 | 278.4 | 284.9 | 340.2 | 313.5
2189.3 | 489.3 | 138.8 | 55.52 | 64.8997 | 109.2 | 120.8 | 122.4 | 125.1 | 167.8 | 23.7 | 21.5 | 38.1 | 2.3 |  |  | 249.9 | 300.4 | 352.4 | 278.4 | 281 | 337.9 | 318.6
2190.3 | 490.3 | 139.1 | 55.64 | 65.04 | 108.7 | 120.5 | 122.5 | 125.4 | 167 | 23.8 | 21.5 | 38.1 | 1.8 |  |  | 250.2 | 298.4 | 364.5 | 278.4 | 278 | 333.9 | 326.5
2191.3 | 491.3 | 137.4 | 54.96 | 64.2451 | 108.4 | 120.8 | 122.1 | 125.4 | 167.4 | 23.8 | 21.5 | 38.1 | 1.8 |  |  | 250.4 | 299.3 | 373 | 278.3 | 276.8 | 337 | 334.4
2192.3 | 492.3 | 136.8 | 54.72 | 63.9645 | 108.4 | 121.3 | 122 | 125.6 | 168.1 | 23.8 | 21.5 | 38.1 | 2 |  |  | 250.7 | 298.7 | 378.9 | 278.3 | 275.4 | 336.7 | 336.5
2193.3 | 493.3 | 139.2 | 55.68 | 65.0867 | 108.6 | 121.6 | 122 | 126 | 168 | 23.8 | 21.5 | 38.1 | 1.7 |  |  | 251 | 297.2 | 374.3 | 278.2 | 273.5 | 334.8 | 331.5
2194.3 | 494.3 | 138.5 | 55.4 | 64.7594 | 108.7 | 121.8 | 122 | 126.3 | 167.4 | 23.8 | 21.5 | 38.1 | 1.4 |  |  | 251.2 | 294.8 | 369.6 | 278.1 | 269.2 | 326.8 | 324.4
2195.3 | 495.3 | 138.1 | 55.24 | 64.5724 | 108.4 | 121.9 | 122.3 | 126.8 | 167.3 | 23.9 | 21.5 | 38.1 | 1.5 |  |  | 251.4 | 292.7 | 374 | 278 | 266.4 | 324.8 | 323.1
2196.3 | 496.3 | 140.2 | 56.08 | 65.5543 | 108.6 | 122 | 122.5 | 127.1 | 167.8 | 23.9 | 21.5 | 38.1 | 1.3 |  |  | 251.7 | 295.2 | 379.3 | 278 | 266.4 | 326.4 | 325.2
2197.3 | 497.3 | 141.1 | 56.44 | 65.9751 | 108.6 | 122.1 | 123 | 127.4 | 169.4 | 23.9 | 21.5 | 38.2 | 2 |  |  | 252 | 297.4 | 386.7 | 277.9 | 268.5 | 335.5 | 331.5
2198.3 | 498.3 | 140.9 | 56.36 | 65.8816 | 108.2 | 122.2 | 123.1 | 127.4 | 169.8 | 23.9 | 21.5 | 38.3 | 2.4 |  |  | 252.2 | 296.5 | 391.4 | 277.8 | 268.7 | 332.3 | 333
2199.3 | 499.3 | 141.1 | 56.44 | 65.9751 | 108.3 | 122.3 | 123 | 127.2 | 168.3 | 23.9 | 21.5 | 38.4 | 2.4 |  |  | 252.4 | 292.8 | 389.6 | 277.7 | 265.9 | 330.5 | 331.6
2200.3 | 500.3 | 139.8 | 55.92 | 65.3673 | 108.9 | 122.1 | 122.7 | 127.5 | 165.8 | 23.9 | 21.5 | 38.4 | 2.3 |  |  | 252.6 | 286.3 | 387.7 | 277.6 | 260.4 | 324.7 | 326.6
2201.3 | 501.3 | 141.2 | 56.48 | 66.0219 | 108.8 | 121.6 | 122.9 | 127.8 | 164.2 | 23.9 | 21.5 | 38.4 | 2 |  |  | 252.9 | 286.9 | 392.6 | 277.5 | 261.5 | 324.9 | 328.3
2202.3 | 502.3 | 140 | 56 | 65.4608 | 108.6 | 121.3 | 123.2 | 128.3 | 165.4 | 23.9 | 21.5 | 38.3 | 2.2 |  |  | 253.1 | 283.7 | 390.6 | 277.5 | 259 | 320.9 | 329.7
2203.3 | 503.3 | 137.5 | 55 | 64.2918 | 108.6 | 121.3 | 123.1 | 128.7 | 166.5 | 23.9 | 21.5 | 38.3 | 2.2 |  |  | 253.4 | 287.4 | 388.8 | 277.4 | 259.4 | 320.9 | 325.8
2204.3 | 504.3 | 137.7 | 55.08 | 64.3853 | 108.4 | 121.4 | 123 | 128.8 | 166.8 | 23.8 | 21.5 | 38.2 | 2.2 |  |  | 253.6 | 291.5 | 383.7 | 277.3 | 259.9 | 320.7 | 321.6
2205.3 | 505.3 | 137.8 | 55.12 | 64.4321 | 108.4 | 121.3 | 123.1 | 128.3 | 166.8 | 23.8 | 21.5 | 38.2 | 2.7 |  |  | 253.9 | 295.2 | 375.8 | 277.2 | 258.4 | 318.2 | 318.4
2206.3 | 506.3 | 139.6 | 55.84 | 65.2737 | 109.5 | 121.4 | 123.4 | 128.1 | 167.4 | 23.8 | 21.5 | 38.3 | 3.1 |  |  | 254.1 | 301.9 | 371.1 | 277.1 | 262.6 | 317.7 | 318.3
2207.3 | 507.3 | 140 | 56 | 65.4608 | 109.4 | 121.5 | 123.8 | 127.9 | 167.4 | 23.8 | 21.5 | 38.5 | 3 |  |  | 254.4 | 306.6 | 362 | 277 | 263.7 | 312.3 | 314.3
2208.3 | 508.3 | 139.9 | 55.96 | 65.414 | 109.7 | 121.9 | 123.9 | 127.5 | 167.6 | 23.8 | 21.5 | 38.5 | 3.1 |  |  | 254.7 | 310.6 | 356.2 | 276.9 | 268.3 | 309.7 | 313.1
2209.3 | 509.3 | 138.6 | 55.44 | 64.8062 | 110.4 | 122.3 | 124 | 127.6 | 168.8 | 23.8 | 21.5 | 38.7 | 2.7 |  |  | 255 | 316.4 | 351.8 | 276.8 | 275 | 308.3 | 312.7
2210.3 | 510.3 | 138 | 55.2 | 64.5256 | 110.1 | 122.5 | 124.1 | 127.7 | 169.1 | 23.8 | 21.5 | 38.7 | 1.8 |  |  | 255.3 | 322.8 | 349.8 | 276.7 | 282.9 | 311.2 | 316.2
2211.3 | 511.3 | 137.3 | 54.92 | 64.1983 | 110.6 | 122.5 | 124 | 127.7 | 168.9 | 23.9 | 21.5 | 38.7 | 1.7 |  |  | 255.6 | 322.4 | 354.2 | 276.6 | 287.6 | 318.8 | 320.8
2212.3 | 512.3 | 135.5 | 54.2 | 63.3567 | 111.4 | 121.8 | 123.8 | 127.8 | 167.8 | 23.8 | 21.5 | 38.7 | 2.4 |  |  | 255.9 | 317.5 | 357.1 | 276.5 | 286 | 322.1 | 326.9
2213.3 | 513.3 | 137.3 | 54.92 | 64.1983 | 111.8 | 121 | 123.7 | 128.2 | 166.6 | 23.8 | 21.5 | 38.9 | 2.9 |  |  | 256.2 | 314.9 | 362.1 | 276.4 | 285.1 | 324.4 | 328
2214.3 | 514.3 | 139 | 55.6 | 64.9932 | 112.2 | 120.7 | 123.3 | 128.3 | 166.6 | 23.8 | 21.5 | 38.9 | 2.3 |  |  | 256.5 | 311.3 | 365.9 | 276.4 | 282.6 | 332.8 | 332.3
2215.3 | 515.3 | 139.3 | 55.72 | 65.1335 | 112.5 | 120.6 | 123.6 | 128.3 | 166.2 | 23.8 | 21.5 | 38.9 | 2.3 |  |  | 256.7 | 310 | 365.5 | 276.4 | 283.2 | 334.8 | 333.6
2216.3 | 516.3 | 138.2 | 55.28 | 64.6191 | 112.3 | 120.7 | 123.7 | 128.3 | 166 | 23.8 | 21.5 | 39 | 2.4 |  |  | 256.9 | 309.1 | 366.1 | 276.3 | 282.3 | 334.1 | 328
2217.3 | 517.3 | 139.8 | 55.92 | 65.3673 | 112.3 | 120.4 | 123.7 | 128.3 | 166.2 | 23.8 | 21.5 | 39.1 | 2.3 |  |  | 257.1 | 304.7 | 369.2 | 276.3 | 278.7 | 332.1 | 329.5
2218.3 | 518.3 | 140.2 | 56.08 | 65.5543 | 112.8 | 119.7 | 123.6 | 128.2 | 166.6 | 23.8 | 21.5 | 39 | 2.2 |  |  | 257.2 | 304.1 | 367 | 276.4 | 276.8 | 331.1 | 328.3
2219.3 | 519.3 | 139.7 | 55.88 | 65.3205 | 113.4 | 119.7 | 123.9 | 128.4 | 167.5 | 23.9 | 21.5 | 39 | 2.1 |  |  | 257.4 | 307.5 | 372.9 | 276.4 | 280.7 | 335.8 | 328.7
2220.3 | 520.3 | 137.9 | 55.16 | 64.4789 | 113.7 | 119.4 | 123.9 | 128.3 | 168.3 | 23.9 | 21.5 | 38.9 | 2.1 |  |  | 257.6 | 304.8 | 380.1 | 276.4 | 278.4 | 336.8 | 333.4
2221.3 | 521.3 | 139.8 | 55.92 | 65.3673 | 113.4 | 119.2 | 123.5 | 128.1 | 168.5 | 23.9 | 21.5 | 38.9 | 2 |  |  | 257.8 | 300.1 | 385.3 | 276.4 | 275.2 | 330.5 | 332.3
2222.3 | 522.3 | 141.3 | 56.52 | 66.0686 | 112.7 | 119 | 123.1 | 128 | 167.8 | 23.8 | 21.5 | 38.9 | 2 |  |  | 257.9 | 299 | 388.1 | 276.5 | 273.9 | 330.4 | 332.4
2223.3 | 523.3 | 141 | 56.4 | 65.9284 | 112.4 | 119.3 | 122.9 | 128 | 168.1 | 23.8 | 21.5 | 38.8 | 2.1 |  |  | 258 | 300 | 393.7 | 276.5 | 273.9 | 337.6 | 337.1
2224.3 | 524.3 | 140.9 | 56.36 | 65.8816 | 111.9 | 120.1 | 123 | 128.4 | 167.9 | 23.8 | 21.4 | 38.9 | 1.8 |  |  | 258.1 | 296.9 | 391.3 | 276.6 | 270.9 | 339 | 338.7
2225.3 | 525.3 | 140.7 | 56.28 | 65.7881 | 112 | 120.9 | 123.1 | 128.7 | 167.1 | 23.7 | 21.4 | 38.9 | 1.6 |  |  | 258.2 | 297.1 | 393.6 | 276.6 | 271.6 | 344.8 | 340.7
2226.3 | 526.3 | 140 | 56 | 65.4608 | 112.8 | 121.2 | 123.2 | 128.5 | 166.8 | 23.7 | 21.4 | 39.1 | 1.5 |  |  | 258.4 | 293.4 | 393.5 | 276.6 | 267.6 | 343.2 | 340.1
2227.3 | 527.3 | 139 | 55.6 | 64.9932 | 113.3 | 120.8 | 123.3 | 128.7 | 164.8 | 23.9 | 21.4 | 39.1 | 1.5 |  |  | 258.6 | 288.5 | 389.2 | 276.6 | 263.5 | 343.5 | 338.9
2228.3 | 528.3 | 138.3 | 55.32 | 64.6659 | 113.8 | 120.6 | 123.1 | 129 | 162.7 | 24 | 21.5 | 39.1 | 1.5 |  |  | 258.9 | 289.9 | 388.7 | 276.7 | 263.8 | 351.5 | 338.9
2229.3 | 529.3 | 140.7 | 56.28 | 65.7881 | 114.2 | 120.5 | 123.2 | 129.1 | 162.1 | 24.2 | 21.5 | 39.2 | 1.6 |  |  | 259.1 | 284.9 | 386.1 | 276.7 | 261 | 353.2 | 339.4
2230.3 | 530.3 | 140.5 | 56.2 | 65.6946 | 114 | 120.4 | 123.3 | 129.4 | 162.4 | 24.4 | 21.5 | 39.2 | 1.6 |  |  | 259.4 | 279.5 | 379.6 | 276.6 | 256.3 | 347.4 | 336.6
2231.3 | 531.3 | 140.2 | 56.08 | 65.5543 | 113.7 | 120.4 | 123.3 | 129.4 | 161.9 | 24.6 | 21.5 | 39.2 | 1.8 |  |  | 259.7 | 273.6 | 376 | 276.6 | 251.8 | 342.9 | 334.6
2232.3 | 532.3 | 140.6 | 56.24 | 65.7413 | 113.2 | 120.3 | 123 | 129.8 | 160 | 24.7 | 21.5 | 39.3 | 2 |  |  | 259.9 | 268.9 | 373.5 | 276.6 | 249.5 | 344.7 | 335.2
2233.3 | 533.3 | 140.4 | 56.16 | 65.6478 | 112.5 | 120.4 | 122.9 | 130 | 160.1 | 24.8 | 21.5 | 39.3 | 2.3 |  |  | 260.2 | 265 | 373.1 | 276.6 | 246.4 | 341.2 | 337.5
2234.3 | 534.3 | 141 | 56.4 | 65.9284 | 112.4 | 120.3 | 122.8 | 129.7 | 159.8 | 24.6 | 21.5 | 39.3 | 2.4 |  |  | 260.4 | 260.4 | 368 | 276.5 | 242.5 | 335.9 | 335.5
2235.3 | 535.3 | 138 | 55.2 | 64.5256 | 112.4 | 120.5 | 122.7 | 129.2 | 158.6 | 24.5 | 21.5 | 39.3 | 2.8 |  |  | 260.6 | 258.3 | 368.3 | 276.4 | 239.4 | 334.4 | 337.4
2236.3 | 536.3 | 141.2 | 56.48 | 66.0219 | 112.1 | 120.7 | 122.7 | 128.6 | 157.7 | 24.6 | 21.5 | 39.1 | 2.9 |  |  | 260.8 | 254.7 | 365.8 | 276.3 | 236.6 | 329.3 | 334.9
2237.3 | 537.3 | 137.8 | 55.12 | 64.4321 | 111.4 | 121 | 122.7 | 128.2 | 157.1 | 24.7 | 21.4 | 39 | 2.4 |  |  | 261 | 256.5 | 370.1 | 276.2 | 237 | 328.9 | 333.9
2238.3 | 538.3 | 140.1 | 56.04 | 65.5075 | 111.3 | 121.1 | 122.7 | 128 | 157 | 24.7 | 21.4 | 38.9 | 2.9 |  |  | 261.1 | 254 | 372.4 | 276.1 | 233.9 | 324.4 | 334.1
2239.3 | 539.3 | 139.3 | 55.72 | 65.1335 | 111.5 | 121 | 122.7 | 127.7 | 157.3 | 24.8 | 21.5 | 38.8 | 3 |  |  | 261.3 | 253.8 | 374 | 276 | 232.8 | 325.6 | 335.1
2240.3 | 540.3 | 138 | 55.2 | 64.5256 | 111.7 | 121.1 | 122.7 | 127.2 | 156.7 | 24.9 | 21.5 | 38.8 | 3 |  |  | 261.4 | 252 | 373.6 | 275.8 | 232 | 327.3 | 333.4
2241.3 | 541.3 | 139.1 | 55.64 | 65.04 | 112.1 | 120.9 | 122.6 | 127.2 | 155.9 | 25 | 21.4 | 38.9 | 2.6 |  |  | 261.4 | 247.6 | 366.9 | 275.8 | 229.4 | 323.2 | 331.4
2242.3 | 542.3 | 139.7 | 55.88 | 65.3205 | 112.4 | 120.8 | 122.3 | 126.8 | 153.9 | 25.1 | 21.4 | 38.9 | 2.3 |  |  | 261.5 | 244 | 366.8 | 275.6 | 227.7 | 321.7 | 334
2243.3 | 543.3 | 139.2 | 55.68 | 65.0867 | 112.6 | 120.5 | 122.1 | 126.8 | 153.2 | 25.2 | 21.5 | 38.8 | 1.8 |  |  | 261.6 | 239.5 | 360.6 | 275.4 | 223.8 | 316.2 | 332.9
2244.3 | 544.3 | 139.1 | 55.64 | 65.04 | 112.7 | 120.2 | 121.9 | 127.2 | 151.7 | 25.3 | 21.4 | 38.8 | 1.6 |  |  | 261.7 | 236.2 | 353.2 | 275.1 | 221.3 | 315.6 | 331.2
2245.3 | 545.3 | 138.3 | 55.32 | 64.6659 | 112.5 | 120 | 121.5 | 127.5 | 149.9 | 25.4 | 21.4 | 38.8 | 1.5 |  |  | 261.8 | 231 | 343.3 | 274.9 | 217 | 311.2 | 328.5
2246.3 | 546.3 | 138.1 | 55.24 | 64.5724 | 112 | 120.1 | 120.7 | 127.3 | 149.9 | 25.4 | 21.4 | 38.8 | 1.4 |  |  | 261.9 | 227.3 | 337.2 | 274.6 | 214.3 | 312.6 | 329.1
2247.3 | 547.3 | 137.7 | 55.08 | 64.3853 | 111.6 | 120.3 | 120.3 | 127.1 | 148.9 | 25.5 | 21.4 | 38.8 | 1.3 |  |  | 261.9 | 224.8 | 332 | 274.3 | 213.2 | 310 | 329.1
2248.3 | 548.3 | 135.5 | 54.2 | 63.3567 | 110.8 | 121 | 120.3 | 127.4 | 148.3 | 25.6 | 21.4 | 38.8 | 1.3 |  |  | 262 | 221.1 | 326 | 274.1 | 211 | 309.7 | 325.2
2249.3 | 549.3 | 137.5 | 55 | 64.2918 | 110.2 | 120.6 | 120.2 | 127.7 | 147.5 | 25.7 | 21.4 | 38.9 | 1.3 |  |  | 262 | 219.9 | 324 | 273.8 | 210.1 | 309.3 | 325.6
2250.3 | 550.3 | 137.3 | 54.92 | 64.1983 | 110.3 | 120.2 | 119.7 | 128 | 146.1 | 25.7 | 21.4 | 38.9 | 1.5 |  |  | 262 | 217.6 | 323.3 | 273.5 | 207.6 | 305.2 | 325.8
2251.3 | 551.3 | 139.3 | 55.72 | 65.1335 | 110.1 | 120.2 | 118.9 | 127.9 | 145.2 | 25.7 | 21.4 | 38.9 | 1.4 |  |  | 261.9 | 216.2 | 326 | 273.2 | 206.9 | 306 | 330.6
2252.3 | 552.3 | 137.3 | 54.92 | 64.1983 | 110.1 | 120.4 | 118.3 | 127.5 | 145.3 | 25.6 | 21.4 | 38.9 | 1.4 |  |  | 261.8 | 214.6 | 327 | 272.9 | 205.9 | 305.4 | 334.3
2253.3 | 553.3 | 138.5 | 55.4 | 64.7594 | 109.7 | 120.1 | 118.1 | 127.4 | 145 | 25.5 | 21.4 | 38.8 | 1.3 |  |  | 261.7 | 213.3 | 327.9 | 272.5 | 205.1 | 305.7 | 333.9
2254.3 | 554.3 | 139.1 | 55.64 | 65.04 | 109 | 119.7 | 118 | 127.1 | 145.2 | 25.4 | 21.4 | 38.8 | 1.2 |  |  | 261.5 | 210.6 | 326.8 | 272.2 | 203.8 | 302.4 | 334.4
2255.3 | 555.3 | 137.6 | 55.04 | 64.3386 | 108.1 | 119.6 | 118.1 | 127 | 145.2 | 25.4 | 21.4 | 38.8 | 1.4 |  |  | 261.4 | 207.1 | 323.1 | 271.8 | 201.3 | 298.4 | 331.1
2256.3 | 556.3 | 138.5 | 55.4 | 64.7594 | 107.7 | 119.8 | 118.1 | 126.8 | 143.9 | 25.6 | 21.4 | 38.7 | 1.5 |  |  | 261.2 | 206.6 | 322.3 | 271.6 | 201 | 296.8 | 329.6
2257.3 | 557.3 | 139.6 | 55.84 | 65.2737 | 108.4 | 119.8 | 117.7 | 126.6 | 143 | 25.6 | 21.4 | 38.7 | 1.1 |  |  | 261.1 | 205.8 | 323 | 271.2 | 200.2 | 298 | 333.3
2258.3 | 558.3 | 139.3 | 55.72 | 65.1335 | 108.5 | 119.8 | 117.1 | 126.6 | 143.1 | 25.7 | 21.4 | 38.9 | 1 |  |  | 260.9 | 204.6 | 319.9 | 270.9 | 201.5 | 298.2 | 333.8
2259.3 | 559.3 | 140 | 56 | 65.4608 | 107.9 | 119.9 | 116.8 | 126.9 | 144.2 | 25.8 | 21.4 | 39 | 1.6 |  |  | 260.8 | 202.1 | 320.3 | 270.5 | 199.9 | 297.8 | 332
2260.3 | 560.3 | 140.1 | 56.04 | 65.5075 | 107.7 | 120.4 | 116.6 | 127.2 | 143.9 | 25.8 | 21.4 | 39.2 | 1.4 |  |  | 260.6 | 202.2 | 328.3 | 270.2 | 201.6 | 299.8 | 333.8
2261.3 | 561.3 | 140.1 | 56.04 | 65.5075 | 107.9 | 120.4 | 116.4 | 127.4 | 145 | 25.8 | 21.4 | 39.4 | 1.3 |  |  | 260.4 | 201 | 338.2 | 269.9 | 199.8 | 298.3 | 337.7
2262.3 | 562.3 | 139.8 | 55.92 | 65.3673 | 107.2 | 120.6 | 116 | 127.7 | 146.8 | 25.9 | 21.4 | 39.5 | 1.2 |  |  | 260.2 | 200.2 | 341.1 | 269.5 | 198.1 | 296.6 | 338.3
2263.3 | 563.3 | 137.8 | 55.12 | 64.4321 | 106.6 | 120.8 | 116.2 | 127.9 | 147.2 | 25.9 | 21.4 | 39.5 | 1.3 |  |  | 260 | 204.9 | 344.3 | 269.2 | 201.1 | 299.9 | 340.1
2264.3 | 564.3 | 140.6 | 56.24 | 65.7413 | 106.5 | 120.7 | 116.8 | 127.7 | 149.7 | 25.9 | 21.4 | 39.6 | 1.2 |  |  | 259.9 | 211.5 | 345.2 | 268.9 | 204.4 | 300.3 | 335.8
2265.3 | 565.3 | 138.4 | 55.36 | 64.7127 | 106.7 | 120.3 | 117.3 | 127.9 | 151.7 | 25.9 | 21.4 | 39.7 | 1.4 |  |  | 259.7 | 219.1 | 349.7 | 268.5 | 210 | 300.7 | 334.1
2266.3 | 566.3 | 140.2 | 56.08 | 65.5543 | 106.3 | 120.3 | 117.5 | 128.1 | 154.2 | 25.8 | 21.4 | 39.8 | 1.3 |  |  | 259.6 | 222.4 | 357.3 | 268.3 | 213.7 | 305.9 | 337
2267.3 | 567.3 | 139 | 55.6 | 64.9932 | 106.2 | 120.5 | 117.6 | 128.4 | 154.4 | 25.6 | 21.4 | 39.9 | 1.5 |  |  | 259.4 | 220.3 | 361.1 | 268 | 212.8 | 307.3 | 337.4
2268.3 | 568.3 | 138.9 | 55.56 | 64.9464 | 106.4 | 120.3 | 117.7 | 128.6 | 154.2 | 25.4 | 21.4 | 39.9 | 1.6 |  |  | 259.4 | 219.7 | 363.9 | 267.8 | 214 | 306.4 | 337.6
2269.3 | 569.3 | 137.9 | 55.16 | 64.4789 | 106.3 | 119.7 | 117.9 | 128.5 | 154.4 | 25.2 | 21.4 | 40 | 1.4 |  |  | 259.3 | 218.9 | 359.7 | 267.6 | 214.6 | 303.5 | 336
2270.3 | 570.3 | 139.8 | 55.92 | 65.3673 | 106 | 119.8 | 118.4 | 128.2 | 153.5 | 25.1 | 21.4 | 40 | 1.4 |  |  | 259.3 | 216.8 | 357.1 | 267.4 | 213 | 296.6 | 333.2
2271.3 | 571.3 | 137.6 | 55.04 | 64.3386 | 106.1 | 120.5 | 118.9 | 127.8 | 152.5 | 25.1 | 21.4 | 40 | 1.5 |  |  | 259.3 | 217.2 | 358.7 | 267.1 | 211.8 | 294.7 | 331.8
2272.3 | 572.3 | 138.4 | 55.36 | 64.7127 | 106.2 | 120.5 | 119.2 | 127.8 | 151.9 | 25.3 | 21.4 | 40 | 1.5 |  |  | 259.3 | 216.3 | 361.2 | 266.9 | 210.4 | 295.5 | 333.7
2273.3 | 573.3 | 138.7 | 55.48 | 64.8529 | 105.8 | 120.5 | 119.3 | 128 | 151.4 | 25.3 | 21.4 | 39.8 | 1.6 |  |  | 259.4 | 216 | 360.9 | 266.7 | 210 | 295.9 | 336.9
2274.3 | 574.3 | 138.2 | 55.28 | 64.6191 | 105.8 | 120.3 | 119.4 | 128 | 151.9 | 25.5 | 21.4 | 39.7 | 1.5 |  |  | 259.5 | 214.9 | 360.3 | 266.5 | 208.9 | 293 | 335.8
2275.3 | 575.3 | 138.5 | 55.4 | 64.7594 | 105.6 | 119.9 | 120.2 | 127.7 | 153.6 | 25.7 | 21.4 | 39.6 | 1.4 |  |  | 259.6 | 213.2 | 359.3 | 266.3 | 206.5 | 289.4 | 332.7
2276.3 | 576.3 | 138.5 | 55.4 | 64.7594 | 105.3 | 119.5 | 120.6 | 127.3 | 153.4 | 25.8 | 21.4 | 39.6 | 1.2 |  |  | 259.6 | 214 | 359.4 | 266.1 | 205.7 | 287.3 | 330.1
2277.3 | 577.3 | 138 | 55.2 | 64.5256 | 105 | 119.4 | 120.4 | 127.3 | 152.5 | 25.8 | 21.4 | 39.6 | 1.2 |  |  | 259.7 | 213.2 | 355.7 | 265.8 | 203.9 | 280.3 | 325.8
2278.3 | 578.3 | 135.6 | 54.24 | 63.4034 | 105.8 | 119.8 | 120.4 | 127.4 | 152.7 | 25.9 | 21.4 | 39.7 | 1.3 |  |  | 259.8 | 210.5 | 351.5 | 265.6 | 200.7 | 276.1 | 323.8
2279.3 | 579.3 | 138.8 | 55.52 | 64.8997 | 106.1 | 119.8 | 120.6 | 127.3 | 152.3 | 25.8 | 21.4 | 39.9 | 1.6 |  |  | 259.8 | 208.1 | 348.2 | 265.3 | 197.7 | 271.7 | 325.4
2280.3 | 580.3 | 139.8 | 55.92 | 65.3673 | 106.1 | 119.7 | 120.8 | 127 | 151.3 | 25.8 | 21.4 | 40 | 1.2 |  |  | 259.9 | 207.9 | 346 | 265.1 | 197.3 | 270.2 | 323.8
2281.3 | 581.3 | 138.6 | 55.44 | 64.8062 | 106.8 | 119.9 | 120.3 | 126.8 | 150.9 | 25.8 | 21.4 | 40 | 1.2 |  |  | 260 | 206.5 | 341 | 264.8 | 195.1 | 267.3 | 321.1
2282.3 | 582.3 | 140.7 | 56.28 | 65.7881 | 108 | 119.8 | 120.2 | 126.5 | 150.5 | 25.8 | 21.4 | 40.1 | 1.2 |  |  | 260 | 206 | 340.8 | 264.5 | 193.5 | 264 | 321.5
2283.3 | 583.3 | 141.5 | 56.6 | 66.1621 | 108.1 | 119.5 | 120.5 | 125.8 | 149.9 | 25.8 | 21.4 | 40.2 | 1.6 |  |  | 260.1 | 204.5 | 338.1 | 264.3 | 192.6 | 263.7 | 327
2284.3 | 584.3 | 140.3 | 56.12 | 65.601 | 107.8 | 119.3 | 120.4 | 125.7 | 149.3 | 25.7 | 21.4 | 40.3 | 1.6 |  |  | 260.1 | 202 | 337.9 | 264 | 189.4 | 257.6 | 326.1
2285.3 | 585.3 | 138.5 | 55.4 | 64.7594 | 108.4 | 119.6 | 120.4 | 125.8 | 148.1 | 25.7 | 21.4 | 40.2 | 1.4 |  |  | 260.1 | 200.5 | 335.3 | 263.7 | 187.8 | 255.3 | 323.3
2286.3 | 586.3 | 139.5 | 55.8 | 65.227 | 108.8 | 120.1 | 120.3 | 125.8 | 147.8 | 25.8 | 21.4 | 40.2 | 1.6 |  |  | 260.2 | 201.9 | 335.5 | 263.3 | 188.5 | 254.4 | 322.9
2287.3 | 587.3 | 139.6 | 55.84 | 65.2737 | 108.6 | 120.5 | 120 | 125.6 | 147.7 | 25.9 | 21.4 | 40.2 | 1.3 |  |  | 260.1 | 200.4 | 333.6 | 263 | 186.6 | 250.1 | 322.6
2288.3 | 588.3 | 140 | 56 | 65.4608 | 108.2 | 120.7 | 119.7 | 125.6 | 147.6 | 26 | 21.4 | 40.2 | 1.2 |  |  | 260.1 | 201.6 | 336.9 | 262.7 | 186.1 | 246.8 | 324.2
2289.3 | 589.3 | 138.7 | 55.48 | 64.8529 | 108.3 | 121.3 | 119.9 | 125.7 | 148.3 | 26 | 21.4 | 40.3 | 1.4 |  |  | 260.1 | 201 | 342.7 | 262.3 | 185.7 | 246.4 | 321.9
2290.3 | 590.3 | 137.5 | 55 | 64.2918 | 108.9 | 121.4 | 120.5 | 125.8 | 149.1 | 25.9 | 21.4 | 40.4 | 1.2 |  |  | 260.1 | 200 | 349.1 | 262 | 183.9 | 248.2 | 323.8
2291.3 | 591.3 | 137.7 | 55.08 | 64.3853 | 109.2 | 121 | 120.7 | 126 | 148.8 | 25.8 | 21.4 | 40.4 | 1.3 |  |  | 260.1 | 197.5 | 350.7 | 261.7 | 181.6 | 244.9 | 327.4
2292.3 | 592.3 | 138.3 | 55.32 | 64.6659 | 109 | 120.7 | 120.6 | 126.1 | 148 | 25.9 | 21.4 | 40.5 | 1.1 |  |  | 260.1 | 197.1 | 349.8 | 261.3 | 180.4 | 243.7 | 327.7
2293.3 | 593.3 | 137.8 | 55.12 | 64.4321 | 108.6 | 120.4 | 120.7 | 126.3 | 147.5 | 26 | 21.4 | 40.6 | 1.2 |  |  | 260 | 195.9 | 348.5 | 261 | 179.3 | 241.1 | 324.8
2294.3 | 594.3 | 137.5 | 55 | 64.2918 | 108.2 | 120.3 | 120.9 | 126.6 | 146.9 | 26 | 21.4 | 40.7 | 1.1 |  |  | 260 | 194.2 | 348.4 | 260.7 | 177.2 | 241.3 | 326.3
2295.3 | 595.3 | 140 | 56 | 65.4608 | 108 | 120.1 | 120.9 | 127 | 146.3 | 26.1 | 21.4 | 40.8 | 1.3 |  |  | 259.9 | 191.4 | 341.5 | 260.4 | 174.8 | 238.4 | 324.5
2296.3 | 596.3 | 139.9 | 55.96 | 65.414 | 108.1 | 120 | 120.6 | 127.1 | 145.9 | 26.2 | 21.4 | 40.9 | 1 |  |  | 259.9 | 189.4 | 341.8 | 260 | 172.9 | 242.3 | 326.1
2297.3 | 597.3 | 138.5 | 55.4 | 64.7594 | 108.7 | 120.1 | 120.2 | 127.3 | 145.3 | 26.2 | 21.4 | 40.9 | 1 |  |  | 259.9 | 188.3 | 341.8 | 259.7 | 171.8 | 244.2 | 327.6
2298.3 | 598.3 | 138.9 | 55.56 | 64.9464 | 109.1 | 120.1 | 120.1 | 127.4 | 145.3 | 26.2 | 21.4 | 40.9 | 1.2 |  |  | 259.9 | 189.1 | 343.9 | 259.4 | 172.3 | 247.2 | 328.4
2299.3 | 599.3 | 138.7 | 55.48 | 64.8529 | 109.3 | 119.9 | 120.3 | 126.8 | 145.8 | 26.2 | 21.4 | 40.9 | 1.3 |  |  | 259.8 | 191.3 | 343.4 | 259.1 | 174.1 | 250.5 | 330.5
2300.3 | 600.3 | 138.3 | 55.32 | 64.6659 | 108.6 | 119.6 | 120.3 | 126.7 | 146.9 | 26.3 | 21.4 | 40.9 | 1.6 |  |  | 259.7 | 192.9 | 342.3 | 258.7 | 173.8 | 248.9 | 329
2301.3 | 601.3 | 137.9 | 55.16 | 64.4789 | 108.3 | 119.1 | 120.4 | 126.7 | 146.6 | 26.5 | 21.4 | 40.9 | 1.3 |  |  | 259.6 | 191.6 | 339.1 | 258.4 | 173.6 | 248.5 | 327.5
2302.3 | 602.3 | 137.4 | 54.96 | 64.2451 | 108 | 119 | 120.2 | 127 | 146 | 26.7 | 21.4 | 40.9 | 1.7 |  |  | 259.6 | 190.7 | 337.2 | 258.1 | 172.7 | 251.6 | 328.6
2303.3 | 603.3 | 137.4 | 54.96 | 64.2451 | 107.9 | 119.3 | 119.8 | 127.2 | 144.9 | 26.8 | 21.4 | 41 | 1.7 |  |  | 259.5 | 190.5 | 332.7 | 257.8 | 172.3 | 251.8 | 325.3
2304.3 | 604.3 | 138.5 | 55.4 | 64.7594 | 107.8 | 119.5 | 119.8 | 127.1 | 144.3 | 27 | 21.4 | 41.2 | 1.7 |  |  | 259.4 | 193.2 | 337.9 | 257.6 | 175.3 | 259.2 | 329
2305.3 | 605.3 | 139.4 | 55.76 | 65.1802 | 108.1 | 119.9 | 119.8 | 127.1 | 145 | 27 | 21.4 | 41.3 | 1.9 |  |  | 259.3 | 197.1 | 342.5 | 257.3 | 177.3 | 267.2 | 328.8
2306.3 | 606.3 | 136.8 | 54.72 | 63.9645 | 108 | 119.8 | 119.2 | 127.2 | 147.3 | 27 | 21.4 | 41.5 | 1.9 |  |  | 259.2 | 205 | 348.1 | 257 | 181.1 | 272.8 | 326.3
2307.3 | 607.3 | 139.4 | 55.76 | 65.1802 | 107.7 | 119.7 | 118.7 | 127.2 | 150.6 | 27.1 | 21.4 | 41.6 | 1.6 |  |  | 259.1 | 211.2 | 347.7 | 256.7 | 185.6 | 277.1 | 324.6
2308.3 | 608.3 | 138.9 | 55.56 | 64.9464 | 106.7 | 119.4 | 118.5 | 127.2 | 151.9 | 27 | 21.4 | 41.6 | 1.6 |  |  | 259 | 220.5 | 352.2 | 256.5 | 191 | 280.1 | 325.8
2309.3 | 609.3 | 138.6 | 55.44 | 64.8062 | 106.7 | 119.3 | 118.4 | 126.8 | 155.6 | 26.9 | 21.4 | 41.7 | 2.2 |  |  | 258.9 | 224.6 | 358.8 | 256.3 | 194.1 | 286 | 332.1
2310.3 | 610.3 | 140 | 56 | 65.4608 | 107.3 | 119.4 | 118.2 | 126.7 | 156.8 | 26.8 | 21.4 | 41.7 | 1.8 |  |  | 258.8 | 233.7 | 360.7 | 256.2 | 200.6 | 294.7 | 334.8
2311.3 | 611.3 | 140.5 | 56.2 | 65.6946 | 107.3 | 119.6 | 118.2 | 127.2 | 158.6 | 26.7 | 21.4 | 41.7 | 1.5 |  |  | 258.8 | 241.1 | 359.7 | 256.1 | 205.3 | 301.5 | 333.4
2312.3 | 612.3 | 139.2 | 55.68 | 65.0867 | 107.3 | 119.8 | 118.2 | 127.8 | 160.8 | 26.6 | 21.4 | 41.6 | 1.7 |  |  | 258.7 | 247.7 | 362.5 | 256.1 | 208.9 | 303.4 | 329.3
2313.3 | 613.3 | 138.2 | 55.28 | 64.6191 | 107.1 | 119.2 | 118.5 | 128.1 | 164.5 | 26.5 | 21.4 | 41.6 | 1.7 |  |  | 258.7 | 256.2 | 364.5 | 256.1 | 211.5 | 301.4 | 326.5
2314.3 | 614.3 | 141.1 | 56.44 | 65.9751 | 107.6 | 119 | 119.3 | 128.5 | 164.9 | 26.4 | 21.4 | 41.5 | 1.9 |  |  | 258.7 | 256 | 362.8 | 256 | 210.6 | 300.4 | 324.3
2315.3 | 615.3 | 141.8 | 56.72 | 66.3024 | 108.2 | 118.9 | 120.1 | 129.1 | 164.2 | 26.4 | 21.4 | 41.5 | 1.9 |  |  | 258.8 | 253.5 | 364.6 | 256.1 | 210.1 | 301.8 | 323.9
2316.3 | 616.3 | 140.9 | 56.36 | 65.8816 | 109 | 119 | 120.8 | 129.1 | 163.5 | 26.4 | 21.4 | 41.5 | 1.8 |  |  | 258.9 | 250.2 | 367.5 | 256.2 | 209.9 | 300.4 | 326.7
2317.3 | 617.3 | 140.9 | 56.36 | 65.8816 | 109.6 | 119.2 | 121.8 | 128.9 | 161.9 | 26.3 | 21.4 | 41.5 | 1.7 |  |  | 259 | 247.2 | 371.6 | 256.3 | 209.2 | 299.2 | 328.4
2318.3 | 618.3 | 141.8 | 56.72 | 66.3024 | 109.9 | 119.2 | 122.6 | 128.9 | 161.8 | 26.3 | 21.4 | 41.4 | 1.6 |  |  | 259.1 | 246.2 | 374.6 | 256.4 | 210.3 | 300.5 | 331.3
2319.3 | 619.3 | 140.8 | 56.32 | 65.8348 | 109.9 | 119.5 | 123.1 | 128.8 | 162.4 | 26.3 | 21.4 | 41.3 | 1.3 |  |  | 259.2 | 244.5 | 372.4 | 256.4 | 209.3 | 298.1 | 329
2320.3 | 620.3 | 139.8 | 55.92 | 65.3673 | 109.9 | 120 | 123.2 | 128.6 | 161.9 | 26.2 | 21.4 | 41.2 | 1.2 |  |  | 259.4 | 245.1 | 370.9 | 256.5 | 210 | 295.9 | 327.5
2321.3 | 621.3 | 139.7 | 55.88 | 65.3205 | 109.5 | 120.4 | 123.3 | 128.4 | 161.2 | 26.3 | 21.4 | 41.1 | 1.2 |  |  | 259.6 | 249.6 | 366.9 | 256.5 | 213.6 | 294.8 | 324.4
2322.3 | 622.3 | 141.2 | 56.48 | 66.0219 | 109.8 | 120.4 | 123.3 | 128.5 | 161.4 | 26.3 | 21.4 | 40.9 | 1 |  |  | 259.8 | 252.6 | 366.2 | 256.6 | 215.6 | 292.4 | 324.9
2323.3 | 623.3 | 141.9 | 56.76 | 66.3492 | 110.3 | 120.7 | 123.2 | 128.4 | 161 | 26.4 | 21.4 | 40.9 | 1 |  |  | 260 | 254.4 | 365.5 | 256.6 | 217.9 | 294.7 | 325.6
2324.3 | 624.3 | 140.9 | 56.36 | 65.8816 | 110.5 | 121.1 | 123 | 128.1 | 162.6 | 26.4 | 21.4 | 40.8 | 1 |  |  | 260.1 | 262 | 368.2 | 256.7 | 222.9 | 296 | 326.2
2325.3 | 625.3 | 139.2 | 55.68 | 65.0867 | 111.1 | 121.1 | 123.2 | 127.9 | 164.7 | 26.5 | 21.4 | 40.8 | 0.9 |  |  | 260.3 | 264.6 | 366 | 256.7 | 225.9 | 296.4 | 324
2326.3 | 626.3 | 139.7 | 55.88 | 65.3205 | 111.1 | 121.1 | 123.3 | 127.7 | 165.1 | 26.5 | 21.4 | 40.7 | 1.3 |  |  | 260.5 | 263.8 | 359.8 | 256.7 | 225.6 | 297.7 | 323.1
2327.3 | 627.3 | 137.3 | 54.92 | 64.1983 | 111 | 121.4 | 123.4 | 127.9 | 164.5 | 26.4 | 21.4 | 40.7 | 1.6 |  |  | 260.7 | 266.8 | 352.3 | 256.8 | 229.5 | 294.9 | 320.4
2328.3 | 628.3 | 139.8 | 55.92 | 65.3673 | 111.4 | 121.6 | 123.3 | 128.1 | 164.6 | 26.4 | 21.4 | 40.7 | 1.5 |  |  | 260.9 | 266.4 | 349.1 | 256.9 | 228 | 293.5 | 319.3
2329.3 | 629.3 | 139.1 | 55.64 | 65.04 | 111.8 | 121.7 | 123.4 | 128.2 | 165.6 | 26.3 | 21.4 | 40.7 | 1.2 |  |  | 261.1 | 276.4 | 349 | 256.9 | 234 | 293.9 | 321.2
2330.3 | 630.3 | 139.2 | 55.68 | 65.0867 | 112.1 | 122.2 | 123.4 | 128.1 | 166.4 | 26.3 | 21.4 | 40.7 | 1.6 |  |  | 261.2 | 280.1 | 348.9 | 257 | 236.7 | 297.2 | 322.2
2331.3 | 631.3 | 138.1 | 55.24 | 64.5724 | 112.2 | 122.3 | 123.3 | 128.1 | 167.1 | 26.3 | 21.4 | 40.7 | 1.8 |  |  | 261.4 | 281.7 | 355.7 | 257.1 | 238.8 | 300.3 | 325.5
2332.3 | 632.3 | 137.4 | 54.96 | 64.2451 | 112.7 | 121.9 | 123.2 | 128.4 | 167.6 | 26.3 | 21.4 | 40.7 | 2.2 |  |  | 261.6 | 278.2 | 358.6 | 257.2 | 236.7 | 298.3 | 327.2
2333.3 | 633.3 | 137.4 | 54.96 | 64.2451 | 112.6 | 121.2 | 123.6 | 128.8 | 165.5 | 26.3 | 21.4 | 40.8 | 2.2 |  |  | 261.8 | 273.5 | 360.8 | 257.3 | 234.2 | 298.2 | 329
2334.3 | 634.3 | 138.2 | 55.28 | 64.6191 | 112.7 | 120.9 | 123.8 | 129.1 | 164.3 | 26.3 | 21.4 | 40.7 | 2.3 |  |  | 262 | 269.4 | 359 | 257.4 | 232.6 | 295.8 | 325.4
2335.3 | 635.3 | 138.5 | 55.4 | 64.7594 | 112.8 | 121.2 | 124 | 129.1 | 162.1 | 26.2 | 21.4 | 40.7 | 2.2 |  |  | 262.2 | 265.2 | 358.6 | 257.5 | 230.3 | 295.8 | 325.6
2336.3 | 636.3 | 138.2 | 55.28 | 64.6191 | 112.7 | 121.9 | 124 | 129.1 | 159.9 | 26.2 | 21.4 | 40.6 | 2.3 |  |  | 262.5 | 260.6 | 359.8 | 257.6 | 227.9 | 295.4 | 326.5
2337.3 | 637.3 | 138.3 | 55.32 | 64.6659 | 113 | 122.2 | 123.8 | 129.3 | 158.9 | 26.1 | 21.4 | 40.6 | 2.4 |  |  | 262.7 | 258.6 | 362.1 | 257.6 | 225.7 | 293.5 | 329.1
2338.3 | 638.3 | 138.4 | 55.36 | 64.7127 | 113.2 | 122.6 | 123.6 | 129.4 | 158.9 | 26.1 | 21.4 | 40.7 | 2.4 |  |  | 262.9 | 256.7 | 366.8 | 257.7 | 225.4 | 297.7 | 332
2339.3 | 639.3 | 139.1 | 55.64 | 65.04 | 113.3 | 123 | 123.7 | 129.1 | 159.4 | 26.2 | 21.4 | 40.9 | 2.8 |  |  | 263.1 | 257.4 | 369.8 | 257.7 | 225.4 | 295.5 | 330.9
2340.3 | 640.3 | 139 | 55.6 | 64.9932 | 114 | 123.3 | 123.8 | 128.7 | 159.5 | 26.2 | 21.4 | 40.9 | 2.6 |  |  | 263.3 | 266.1 | 363.1 | 257.8 | 231 | 298.8 | 326.8
2341.3 | 641.3 | 140.2 | 56.08 | 65.5543 | 114.8 | 123.4 | 123.8 | 128.5 | 160.3 | 26.4 | 21.4 | 41 | 2.9 |  |  | 263.4 | 272.9 | 362.1 | 257.8 | 235.4 | 300.4 | 325.5
2342.3 | 642.3 | 140.6 | 56.24 | 65.7413 | 115.5 | 123.4 | 123.5 | 128.7 | 164.2 | 26.4 | 21.4 | 41 | 2.5 |  |  | 263.6 | 280.8 | 364.1 | 257.8 | 240.2 | 301.6 | 325.1
2343.3 | 643.3 | 139.4 | 55.76 | 65.1802 | 115.1 | 123.5 | 123.1 | 128.8 | 168.8 | 26.5 | 21.4 | 41 | 2.2 |  |  | 263.7 | 285.5 | 362.2 | 257.8 | 241.2 | 299.8 | 324
2344.3 | 644.3 | 138.8 | 55.52 | 64.8997 | 114.7 | 123.6 | 123.2 | 129 | 169.4 | 26.7 | 21.4 | 40.9 | 1.8 |  |  | 263.9 | 289.1 | 362.8 | 257.9 | 240 | 296.1 | 323.2
2345.3 | 645.3 | 139 | 55.6 | 64.9932 | 115.2 | 123.9 | 123.5 | 129.1 | 168.3 | 27 | 21.4 | 40.8 | 1.2 |  |  | 264 | 299.7 | 365.2 | 257.9 | 245.1 | 304.1 | 324.9
2346.3 | 646.3 | 141.1 | 56.44 | 65.9751 | 115.4 | 123.6 | 123.8 | 129.4 | 171.1 | 27.1 | 21.4 | 40.8 | 1.3 |  |  | 264.2 | 304.4 | 375.7 | 258 | 249.4 | 314.5 | 334.3
2347.3 | 647.3 | 140.9 | 56.36 | 65.8816 | 115 | 123.3 | 124 | 129.7 | 173.8 | 27.1 | 21.4 | 40.8 | 1.4 |  |  | 264.3 | 301.4 | 382.3 | 258.1 | 249.3 | 317 | 338.3
2348.3 | 648.3 | 140.9 | 56.36 | 65.8816 | 114.9 | 123.2 | 123.5 | 129.8 | 173.4 | 27.1 | 21.4 | 40.9 | 1.9 |  |  | 264.5 | 305.9 | 385.6 | 258.3 | 258.8 | 328.1 | 342.8
2349.3 | 649.3 | 141.3 | 56.52 | 66.0686 | 115.3 | 122.9 | 123.5 | 129.8 | 174.9 | 27 | 21.4 | 40.9 | 2.8 |  |  | 264.7 | 307.2 | 382 | 258.5 | 262 | 325.7 | 341.9
2350.3 | 650.3 | 141.1 | 56.44 | 65.9751 | 115.7 | 122.5 | 123.6 | 129.9 | 173.8 | 27 | 21.4 | 40.9 | 2.9 |  |  | 264.9 | 305.5 | 376.9 | 258.7 | 259.7 | 318.6 | 336
2351.3 | 651.3 | 139.8 | 55.92 | 65.3673 | 116.4 | 122.2 | 123.5 | 130.3 | 172.3 | 27 | 21.4 | 40.8 | 3 |  |  | 265.1 | 307.1 | 382.4 | 258.9 | 260.4 | 320.2 | 336.3
2352.3 | 652.3 | 139.2 | 55.68 | 65.0867 | 116.2 | 122.5 | 123.8 | 130.8 | 172.7 | 26.9 | 21.4 | 40.8 | 2.7 |  |  | 265.4 | 304.3 | 388.9 | 259.1 | 261.4 | 323.6 | 343.4
2353.3 | 653.3 | 137.3 | 54.92 | 64.1983 | 115.9 | 122.9 | 123.8 | 130.8 | 171.9 | 26.9 | 21.4 | 40.7 | 2.7 |  |  | 265.6 | 298.1 | 388.1 | 259.3 | 257.2 | 318.5 | 341.9
2354.3 | 654.3 | 139 | 55.6 | 64.9932 | 115.9 | 122.8 | 123.7 | 130.7 | 171 | 26.8 | 21.4 | 40.7 | 2.4 |  |  | 265.9 | 291 | 383.3 | 259.6 | 251.8 | 312.6 | 339.9
2355.3 | 655.3 | 138 | 55.2 | 64.5256 | 116 | 122.5 | 123.4 | 130.6 | 169.1 | 26.6 | 21.4 | 40.6 | 2.5 |  |  | 266.2 | 285.5 | 382.8 | 259.8 | 247.3 | 311 | 341
2356.3 | 656.3 | 140.2 | 56.08 | 65.5543 | 116.1 | 122.8 | 123.3 | 130.7 | 167.8 | 26.7 | 21.4 | 40.6 | 2.7 |  |  | 266.4 | 280.1 | 382 | 260 | 243.2 | 312.3 | 345
2357.3 | 657.3 | 138.1 | 55.24 | 64.5724 | 116.2 | 123.5 | 123.5 | 130.8 | 166.3 | 26.7 | 21.4 | 40.5 | 2.8 |  |  | 266.7 | 273.9 | 378.9 | 260.2 | 239.2 | 308.8 | 344.1
2358.3 | 658.3 | 138.9 | 55.56 | 64.9464 | 116 | 123.8 | 123.8 | 130.7 | 165.7 | 26.7 | 21.4 | 40.5 | 3.1 |  |  | 266.9 | 267.4 | 372.6 | 260.3 | 234.4 | 304.5 | 339.9
2359.3 | 659.3 | 140.2 | 56.08 | 65.5543 | 116.4 | 123.7 | 123.9 | 130.7 | 164 | 26.7 | 21.4 | 40.5 | 3.2 |  |  | 267.2 | 261.9 | 371 | 260.4 | 230.4 | 303.9 | 340.3
2360.3 | 660.3 | 138.3 | 55.32 | 64.6659 | 116.4 | 123.5 | 123.9 | 130.9 | 162 | 26.7 | 21.4 | 40.6 | 3.7 |  |  | 267.4 | 256.9 | 368.9 | 260.4 | 227.8 | 304.7 | 342.2
2361.3 | 661.3 | 140 | 56 | 65.4608 | 116.2 | 123.5 | 123.4 | 130.8 | 160.8 | 26.7 | 21.3 | 40.7 | 3.9 |  |  | 267.6 | 254.3 | 368.1 | 260.4 | 225.8 | 307.4 | 345.6
2362.3 | 662.3 | 139.1 | 55.64 | 65.04 | 116.3 | 123.3 | 122.9 | 130.5 | 159.6 | 26.6 | 21.4 | 40.8 | 3.8 |  |  | 267.8 | 253.9 | 369.3 | 260.4 | 226 | 309.8 | 346
2363.3 | 663.3 | 140.2 | 56.08 | 65.5543 | 116.4 | 123.2 | 122.3 | 130.7 | 159.3 | 26.5 | 21.4 | 40.8 | 3.3 |  |  | 267.9 | 256.3 | 368.8 | 260.4 | 229.6 | 312.4 | 344.8
2364.3 | 664.3 | 140.6 | 56.24 | 65.7413 | 115.9 | 123 | 122.2 | 131 | 160.3 | 26.5 | 21.4 | 40.8 | 2.9 |  |  | 268.1 | 264.2 | 369.7 | 260.3 | 235.9 | 314.8 | 342.5
2365.3 | 665.3 | 139.1 | 55.64 | 65.04 | 115.5 | 123.1 | 122.3 | 131.4 | 163.6 | 26.6 | 21.4 | 40.9 | 2.5 |  |  | 268.2 | 267.6 | 366.6 | 260.3 | 238.6 | 316.8 | 341.9
2366.3 | 666.3 | 139.4 | 55.76 | 65.1802 | 115.3 | 123.2 | 122 | 131.6 | 166.4 | 26.7 | 21.3 | 41 | 2.7 |  |  | 268.3 | 264.6 | 371 | 260.3 | 235.8 | 315.7 | 341.6
2367.3 | 667.3 | 142.3 | 56.92 | 66.5362 | 115.6 | 123.1 | 122.4 | 131.8 | 165.9 | 26.7 | 21.3 | 41.1 | 2.6 |  |  | 268.4 | 261.2 | 377.7 | 260.3 | 233.1 | 316.8 | 344.1
2368.3 | 668.3 | 139.2 | 55.68 | 65.0867 | 115.8 | 123.2 | 122.8 | 131.8 | 164.8 | 26.8 | 21.3 | 41.1 | 2.9 |  |  | 268.4 | 257.4 | 377.2 | 260.3 | 229.8 | 310 | 341.7
2369.3 | 669.3 | 137.5 | 55 | 64.2918 | 115.8 | 124.1 | 123.1 | 131.9 | 163.7 | 26.8 | 21.3 | 41 | 2.9 |  |  | 268.5 | 255.4 | 381.2 | 260.3 | 229.1 | 313.4 | 343.9
2370.3 | 670.3 | 139.4 | 55.76 | 65.1802 | 116.2 | 124.2 | 123.2 | 132.2 | 163.5 | 26.8 | 21.3 | 41 | 2.7 |  |  | 268.6 | 253.1 | 381.3 | 260.3 | 228.2 | 311.7 | 349.3
2371.3 | 671.3 | 140.2 | 56.08 | 65.5543 | 116.3 | 123.7 | 123.5 | 132.6 | 161.6 | 26.7 | 21.4 | 40.9 | 2.3 |  |  | 268.7 | 248.4 | 378.6 | 260.3 | 224.5 | 304.8 | 346.1
2372.3 | 672.3 | 140.5 | 56.2 | 65.6946 | 116.3 | 123.4 | 123.8 | 132.6 | 159.7 | 26.7 | 21.4 | 40.8 | 2.1 |  |  | 268.8 | 242.5 | 370 | 260.3 | 220.2 | 301.2 | 341.7
2373.3 | 673.3 | 139.5 | 55.8 | 65.227 | 116 | 123.3 | 123.7 | 132.7 | 157.8 | 26.6 | 21.3 | 40.7 | 2.6 |  |  | 268.9 | 238 | 366.1 | 260.3 | 217.5 | 300.8 | 340.3
2374.3 | 674.3 | 139.2 | 55.68 | 65.0867 | 115.6 | 123.4 | 123.3 | 132.6 | 156.3 | 26.6 | 21.4 | 40.7 | 2.8 |  |  | 269 | 234.3 | 360.7 | 260.2 | 215.6 | 298.3 | 340.7
2375.3 | 675.3 | 139.6 | 55.84 | 65.2737 | 114.7 | 123.3 | 122.7 | 132.7 | 155.3 | 26.6 | 21.3 | 40.7 | 3.2 |  |  | 269.1 | 231.8 | 357.4 | 260.1 | 213.5 | 299.5 | 341.4
2376.3 | 676.3 | 139.9 | 55.96 | 65.414 | 114.1 | 122.9 | 122.6 | 132.8 | 154.5 | 26.5 | 21.4 | 40.6 | 2.7 |  |  | 269.2 | 230.2 | 355.3 | 260 | 212.3 | 297.6 | 341.1
2377.3 | 677.3 | 141.2 | 56.48 | 66.0219 | 113.2 | 122.9 | 122.4 | 132.7 | 153.7 | 26.4 | 21.4 | 40.6 | 3.1 |  |  | 269.3 | 226.7 | 349.2 | 259.9 | 209.5 | 294.2 | 339.6
2378.3 | 678.3 | 140.9 | 56.36 | 65.8816 | 112.8 | 123.1 | 121.7 | 132.5 | 153.9 | 26.3 | 21.4 | 40.6 | 3 |  |  | 269.3 | 222.3 | 343.4 | 259.8 | 206.4 | 287.7 | 336
2379.3 | 679.3 | 140.9 | 56.36 | 65.8816 | 112.5 | 123.4 | 121.4 | 132.6 | 152.7 | 26.3 | 21.4 | 40.7 | 3.2 |  |  | 269.3 | 219.2 | 340.5 | 259.7 | 204.5 | 283.7 | 333.7
2380.3 | 680.3 | 140 | 56 | 65.4608 | 112.5 | 123.1 | 121.5 | 132.6 | 152.2 | 26.3 | 21.4 | 40.7 | 3.2 |  |  | 269.3 | 218 | 342 | 259.6 | 203.5 | 285.3 | 339.2
2381.3 | 681.3 | 140.5 | 56.2 | 65.6946 | 112.4 | 123.1 | 121.1 | 132.3 | 153.2 | 26.4 | 21.3 | 40.8 | 2.7 |  |  | 269.2 | 218.1 | 346.4 | 259.4 | 203.1 | 288.7 | 344.3
2382.3 | 682.3 | 139.5 | 55.8 | 65.227 | 112.8 | 123.1 | 121.4 | 131.9 | 154.1 | 26.5 | 21.3 | 40.9 | 2.8 |  |  | 269.2 | 219.2 | 353.6 | 259.3 | 203.1 | 288.4 | 344.3
2383.3 | 683.3 | 139.8 | 55.92 | 65.3673 | 113.5 | 122.5 | 121.7 | 131.5 | 156.4 | 26.6 | 21.3 | 41.1 | 3.4 |  |  | 269.1 | 217.8 | 356.2 | 259.1 | 201.7 | 288.1 | 346
2384.3 | 684.3 | 138.8 | 55.52 | 64.8997 | 113.4 | 122.3 | 121.5 | 131.3 | 156.7 | 26.7 | 21.4 | 41.2 | 3 |  |  | 269.1 | 216.1 | 358.9 | 258.9 | 200.6 | 287.2 | 343.6
2385.3 | 685.3 | 137.9 | 55.16 | 64.4789 | 113 | 122.3 | 121.1 | 131.3 | 156.8 | 26.7 | 21.4 | 41.4 | 3.8 |  |  | 269 | 214.9 | 355.6 | 258.7 | 201.6 | 287.7 | 341
2386.3 | 686.3 | 139.9 | 55.96 | 65.414 | 113 | 122.5 | 121.3 | 131.2 | 156.5 | 26.7 | 21.3 | 41.4 | 3.6 |  |  | 268.9 | 213.6 | 356.7 | 258.5 | 201.1 | 287.2 | 340.8
2387.3 | 687.3 | 140.6 | 56.24 | 65.7413 | 112.8 | 122.9 | 121.6 | 131 | 156.3 | 26.8 | 21.3 | 41.4 | 4.2 |  |  | 268.8 | 213 | 357 | 258.4 | 198.7 | 285.1 | 339.9
2388.3 | 688.3 | 138.1 | 55.24 | 64.5724 | 113.4 | 122.5 | 121.9 | 130.8 | 156.2 | 26.9 | 21.3 | 41.4 | 4.8 |  |  | 268.7 | 211.2 | 356.1 | 258.2 | 196.1 | 285.7 | 341.3
2389.3 | 689.3 | 139.1 | 55.64 | 65.04 | 113.7 | 122.7 | 122.1 | 130.8 | 154.7 | 26.9 | 21.3 | 41.4 | 4.4 |  |  | 268.7 | 209.4 | 356.4 | 258 | 194.6 | 284.7 | 342.1
2390.3 | 690.3 | 138.3 | 55.32 | 64.6659 | 113.8 | 122.6 | 122.2 | 131 | 153.4 | 26.9 | 21.3 | 41.3 | 4.5 |  |  | 268.6 | 208.3 | 358.7 | 257.8 | 193.4 | 279.3 | 339.9
2391.3 | 691.3 | 138.9 | 55.56 | 64.9464 | 113.6 | 122.5 | 122 | 131 | 152.9 | 26.8 | 21.3 | 41.2 | 4.6 |  |  | 268.5 | 207.4 | 351.7 | 257.6 | 191.7 | 274.6 | 335.5
2392.3 | 692.3 | 137.3 | 54.92 | 64.1983 | 113.7 | 122.8 | 122 | 131.1 | 153.1 | 26.8 | 21.3 | 41.2 | 4.3 |  |  | 268.5 | 207.5 | 352 | 257.5 | 190.8 | 271.9 | 332.8
2393.3 | 693.3 | 137.7 | 55.08 | 64.3853 | 113.7 | 123 | 121.8 | 131.1 | 155 | 26.9 | 21.3 | 41.2 | 3.8 |  |  | 268.5 | 206.1 | 349.5 | 257.3 | 188.3 | 268.1 | 331.5
2394.3 | 694.3 | 137.1 | 54.84 | 64.1048 | 113.7 | 123.1 | 121.7 | 130.7 | 154.6 | 27 | 21.3 | 41.2 | 3.6 |  |  | 268.4 | 207.3 | 345.5 | 257 | 188.2 | 267.8 | 330.3
2395.3 | 695.3 | 137.1 | 54.84 | 64.1048 | 113.6 | 123.1 | 121.7 | 130.4 | 154.1 | 27 | 21.3 | 41 | 2.5 |  |  | 268.4 | 209.6 | 343.5 | 256.8 | 190.2 | 264.2 | 328
2396.3 | 696.3 | 138.2 | 55.28 | 64.6191 | 114 | 123 | 122.5 | 130.5 | 154.4 | 27 | 21.3 | 41 | 2.6 |  |  | 268.3 | 215.3 | 344.6 | 256.6 | 192.4 | 263.4 | 329.4
2397.3 | 697.3 | 138.5 | 55.4 | 64.7594 | 114.3 | 123.1 | 122.8 | 130.4 | 155.4 | 27 | 21.3 | 41 | 2.8 |  |  | 268.2 | 217.3 | 347.4 | 256.4 | 191.7 | 262.5 | 333.4
2398.3 | 698.3 | 137.4 | 54.96 | 64.2451 | 114.2 | 123.9 | 123.1 | 130 | 156.2 | 27 | 21.3 | 41 | 3.1 |  |  | 268.2 | 213.8 | 347.5 | 256.1 | 188.9 | 257.4 | 332.2
2399.3 | 699.3 | 137.9 | 55.16 | 64.4789 | 114 | 124.8 | 123.2 | 129.2 | 155.5 | 27 | 21.3 | 41 | 4.2 |  |  | 268.1 | 211.4 | 348 | 255.9 | 187 | 254.1 | 330
2400.3 | 700.3 | 139.7 | 55.88 | 65.3205 | 114 | 124.7 | 123.3 | 128.6 | 154.3 | 27.1 | 21.3 | 41 | 4.6 |  |  | 268 | 211.4 | 347.2 | 255.7 | 185.6 | 250.9 | 327
2401.3 | 701.3 | 137.5 | 55 | 64.2918 | 114.1 | 124.6 | 123.3 | 128.4 | 154.4 | 27 | 21.3 | 41 | 4.3 |  |  | 268 | 212.1 | 349.2 | 255.4 | 186.5 | 250 | 325.7
2402.3 | 702.3 | 138.8 | 55.52 | 64.8997 | 113.8 | 124.3 | 122.9 | 128.4 | 154.3 | 26.9 | 21.3 | 40.9 | 4.4 |  |  | 268 | 211 | 349 | 255.2 | 186.7 | 251.6 | 326.4
2403.3 | 703.3 | 137.9 | 55.16 | 64.4789 | 113.5 | 123.3 | 121.8 | 128.2 | 153.6 | 26.9 | 21.3 | 40.9 | 4.1 |  |  | 268 | 209.4 | 350.9 | 255 | 185.9 | 252.7 | 330
2404.3 | 704.3 | 140.4 | 56.16 | 65.6478 | 113.7 | 122.3 | 120.9 | 128.1 | 152.6 | 27 | 21.3 | 40.9 | 4 |  |  | 268 | 206.6 | 347 | 254.8 | 183.8 | 249.8 | 329
2405.3 | 705.3 | 140.9 | 56.36 | 65.8816 | 114.3 | 122.2 | 120.2 | 128.4 | 151.2 | 27 | 21.3 | 40.9 | 4.7 |  |  | 268 | 206.4 | 348.9 | 254.5 | 182.5 | 248.7 | 331.9
2406.3 | 706.3 | 140.8 | 56.32 | 65.8348 | 113.8 | 122.4 | 120 | 128.5 | 150.9 | 27 | 21.3 | 40.9 | 4.5 |  |  | 268 | 207.4 | 354.6 | 254.3 | 183 | 251.7 | 336.6
2407.3 | 707.3 | 140.3 | 56.12 | 65.601 | 113.3 | 121.9 | 120.1 | 128.3 | 151.8 | 27 | 21.3 | 41 | 3.7 |  |  | 268 | 207.4 | 358.9 | 254.1 | 183.5 | 254.3 | 339.5
2408.3 | 708.3 | 140.2 | 56.08 | 65.5543 | 113.5 | 122 | 120.3 | 128.4 | 152.6 | 27 | 21.3 | 41 | 4 |  |  | 268 | 208 | 354.8 | 253.8 | 183.7 | 250.4 | 332.8
2409.3 | 709.3 | 138.5 | 55.4 | 64.7594 | 114.1 | 122.3 | 120.4 | 128.7 | 153.3 | 27 | 21.3 | 41.1 | 2.8 |  |  | 267.9 | 211 | 353.4 | 253.6 | 185.2 | 248.6 | 329.3
2410.3 | 710.3 | 139 | 55.6 | 64.9932 | 114.7 | 122 | 120.2 | 129.2 | 155.7 | 26.9 | 21.3 | 41.1 | 2.1 |  |  | 267.9 | 218.9 | 356.3 | 253.3 | 190.5 | 251 | 326.7
2411.3 | 711.3 | 139.1 | 55.64 | 65.04 | 114.9 | 121.9 | 120.1 | 129.3 | 156.8 | 26.9 | 21.3 | 41.1 | 2 |  |  | 267.9 | 221.5 | 354.8 | 253.1 | 191.3 | 246.4 | 324.8
2412.3 | 712.3 | 138.7 | 55.48 | 64.8529 | 114.8 | 122.3 | 120.5 | 129.4 | 157.8 | 27.1 | 21.3 | 41 | 2.3 |  |  | 267.9 | 221.8 | 354.8 | 252.9 | 191.2 | 245.4 | 324.2
2413.3 | 713.3 | 140.2 | 56.08 | 65.5543 | 115.2 | 122.7 | 120.9 | 129.3 | 158.8 | 27.1 | 21.3 | 41 | 3 |  |  | 267.9 | 229.2 | 366.3 | 252.7 | 196.3 | 252.8 | 329.2
2414.3 | 714.3 | 140.2 | 56.08 | 65.5543 | 115.4 | 122.7 | 121.6 | 129.5 | 161.4 | 27 | 21.3 | 41 | 4.2 |  |  | 268 | 233.7 | 373.6 | 252.5 | 199.4 | 258.2 | 333.3
2415.3 | 715.3 | 137 | 54.8 | 64.058 | 115.5 | 122.3 | 122.1 | 129.5 | 162.7 | 27.1 | 21.3 | 40.9 | 4.7 |  |  | 268 | 231.6 | 371.9 | 252.4 | 198.4 | 258.5 | 332.9
2416.3 | 716.3 | 139.9 | 55.96 | 65.414 | 115.6 | 121.9 | 122.4 | 130.1 | 161.2 | 27 | 21.3 | 40.9 | 5.1 |  |  | 268.1 | 230.8 | 368.1 | 252.2 | 197.6 | 256.9 | 329.1
2417.3 | 717.3 | 136.3 | 54.52 | 63.7307 | 115.9 | 122.1 | 122.8 | 130.4 | 160.4 | 26.9 | 21.3 | 40.8 | 5.7 |  |  | 268.1 | 232.3 | 372.7 | 252.1 | 198 | 266.4 | 332
2418.3 | 718.3 | 139.3 | 55.72 | 65.1335 | 116 | 122 | 123.4 | 130.8 | 161 | 26.8 | 21.3 | 40.8 | 4.9 |  |  | 268.2 | 230.4 | 378.1 | 252 | 199.3 | 271.8 | 336.9
2419.3 | 719.3 | 139.1 | 55.64 | 65.04 | 116 | 122 | 124 | 131 | 160.4 | 26.7 | 21.3 | 40.7 | 3.7 |  |  | 268.3 | 228.6 | 383.2 | 251.9 | 198.8 | 272.5 | 341.7
2420.3 | 720.3 | 138.6 | 55.44 | 64.8062 | 115.7 | 121.7 | 124 | 131 | 159.7 | 26.8 | 21.3 | 40.7 | 3 |  |  | 268.4 | 228.7 | 386 | 251.8 | 198.9 | 278.9 | 345.1
2421.3 | 721.3 | 138.2 | 55.28 | 64.6191 | 115.6 | 121.9 | 123.4 | 131.1 | 158.9 | 26.9 | 21.3 | 40.7 | 3.6 |  |  | 268.6 | 229.7 | 387.9 | 251.7 | 201.7 | 283.5 | 346.6
2422.3 | 722.3 | 138.5 | 55.4 | 64.7594 | 115.5 | 121.8 | 123.2 | 131.2 | 158.6 | 26.9 | 21.3 | 40.6 | 5.1 |  |  | 268.8 | 228.1 | 390.9 | 251.7 | 200.2 | 286.3 | 345.9
2423.3 | 723.3 | 139.7 | 55.88 | 65.3205 | 115.4 | 122 | 123.4 | 131.6 | 158.4 | 26.9 | 21.3 | 40.6 | 4.7 |  |  | 269 | 227 | 393 | 251.6 | 200.3 | 289 | 348.8
2424.3 | 724.3 | 139.4 | 55.76 | 65.1802 | 115.1 | 122.3 | 123.5 | 132.1 | 157.8 | 26.8 | 21.3 | 40.6 | 4.3 |  |  | 269.1 | 228.4 | 394.1 | 251.6 | 200.9 | 287.3 | 346.5
2425.3 | 725.3 | 138.4 | 55.36 | 64.7127 | 114.6 | 122.9 | 123.5 | 132.5 | 158.2 | 26.8 | 21.3 | 40.6 | 4.1 |  |  | 269.3 | 231.6 | 395.9 | 251.6 | 205.1 | 291.4 | 346.5
2426.3 | 726.3 | 137.9 | 55.16 | 64.4789 | 114 | 123.6 | 124 | 132.6 | 159.6 | 26.8 | 21.3 | 40.7 | 4.7 |  |  | 269.4 | 238 | 396.3 | 251.6 | 210 | 300.2 | 346.5
2427.3 | 727.3 | 139.7 | 55.88 | 65.3205 | 114 | 123.9 | 124.3 | 132.8 | 159.8 | 26.8 | 21.3 | 40.8 | 4.2 |  |  | 269.5 | 242.9 | 395.7 | 251.6 | 215.5 | 310 | 347.9
2428.3 | 728.3 | 138.7 | 55.48 | 64.8529 | 114.3 | 124.1 | 124.5 | 132.9 | 161.5 | 26.8 | 21.3 | 40.7 | 3.4 |  |  | 269.6 | 246.1 | 397.2 | 251.6 | 219.8 | 322.9 | 351.8
2429.3 | 729.3 | 141.6 | 56.64 | 66.2089 | 114.3 | 123.9 | 124.8 | 133 | 162.8 | 26.9 | 21.3 | 40.7 | 2.8 |  |  | 269.7 | 248.3 | 398.4 | 251.7 | 220.7 | 321.8 | 352.2
2430.3 | 730.3 | 140 | 56 | 65.4608 | 114.2 | 124 | 125.2 | 132.9 | 162.2 | 27.1 | 21.3 | 40.7 | 2.6 |  |  | 269.9 | 245.8 | 400.8 | 251.8 | 219.2 | 317.2 | 349.4
2431.3 | 731.3 | 138.5 | 55.4 | 64.7594 | 114.2 | 124.3 | 125.4 | 133.5 | 162.4 | 27.2 | 21.3 | 40.7 | 2.5 |  |  | 270 | 241.4 | 402.5 | 251.9 | 216 | 312.1 | 349.6
2432.3 | 732.3 | 140.1 | 56.04 | 65.5075 | 114 | 124.7 | 125.4 | 133.9 | 161.3 | 27.3 | 21.3 | 40.7 | 2.7 |  |  | 270.2 | 237.9 | 398.4 | 252.1 | 213.7 | 307.6 | 351.7
2433.3 | 733.3 | 140.5 | 56.2 | 65.6946 | 113.8 | 124.8 | 125.4 | 133.8 | 159.8 | 27.4 | 21.3 | 40.7 | 2.3 |  |  | 270.4 | 237.5 | 398.8 | 252.2 | 213.6 | 312.2 | 350.3
2434.3 | 734.3 | 141 | 56.4 | 65.9284 | 113.9 | 125 | 125.3 | 134 | 160.1 | 27.4 | 21.3 | 40.8 | 2.8 |  |  | 270.4 | 241.7 | 398.9 | 252.4 | 216.1 | 316.3 | 351.6
2435.3 | 735.3 | 141.2 | 56.48 | 66.0219 | 114 | 125.4 | 125.5 | 134.3 | 160.4 | 27.5 | 21.3 | 40.9 | 3.7 |  |  | 270.5 | 245.6 | 400.2 | 252.5 | 221.9 | 326.5 | 355.8
2436.3 | 736.3 | 141.1 | 56.44 | 65.9751 | 113.7 | 126 | 125.6 | 134.2 | 160.4 | 27.5 | 21.3 | 41 | 3.8 |  |  | 270.6 | 246.6 | 400.4 | 252.6 | 223.1 | 330.2 | 358.3
2437.3 | 737.3 | 139.7 | 55.88 | 65.3205 | 113.8 | 126.4 | 125.6 | 134.4 | 160.2 | 27.4 | 21.3 | 41.1 | 3.7 |  |  | 270.7 | 245.7 | 398.9 | 252.7 | 222.6 | 332.4 | 355.2
2438.3 | 738.3 | 139.3 | 55.72 | 65.1335 | 113.7 | 126.7 | 125.7 | 134.7 | 160 | 27.4 | 21.3 | 41.1 | 3.6 |  |  | 270.8 | 242.6 | 397.6 | 252.9 | 219.9 | 331.8 | 356.3
2439.3 | 739.3 | 139.8 | 55.92 | 65.3673 | 113.7 | 126.5 | 125.8 | 135.1 | 158.7 | 27.4 | 21.3 | 41.1 | 3.4 |  |  | 271 | 239 | 394.3 | 253 | 218.2 | 333.7 | 358.8
2440.3 | 740.3 | 140.1 | 56.04 | 65.5075 | 113.9 | 126.3 | 125.6 | 135.5 | 159.5 | 27.3 | 21.3 | 41.1 | 3.7 |  |  | 271.1 | 235.3 | 389.8 | 253.2 | 216.2 | 334.9 | 359.7
2441.3 | 741.3 | 139.5 | 55.8 | 65.227 | 113.8 | 126.5 | 125.3 | 135.8 | 159.5 | 27.3 | 21.3 | 41.1 | 3.5 |  |  | 271.2 | 235.1 | 387.4 | 253.3 | 215.8 | 335.8 | 358.2
2442.3 | 742.3 | 141.5 | 56.6 | 66.1621 | 114 | 127.3 | 125 | 136 | 159 | 27.3 | 21.3 | 41.1 | 2.3 |  |  | 271.4 | 235.7 | 388.7 | 253.4 | 220.1 | 343.7 | 357.8
2443.3 | 743.3 | 138.3 | 55.32 | 64.6659 | 113.7 | 127.6 | 125 | 136.3 | 160.2 | 27.3 | 21.3 | 41.1 | 3.1 |  |  | 271.5 | 243.2 | 391.6 | 253.6 | 229.5 | 349.1 | 357.7
2444.3 | 744.3 | 139.5 | 55.8 | 65.227 | 114 | 127.4 | 125.6 | 136.1 | 162.6 | 27.3 | 21.3 | 41.2 | 3.9 |  |  | 271.6 | 250.7 | 388.6 | 253.7 | 234.7 | 350.2 | 354.6
2445.3 | 745.3 | 138.3 | 55.32 | 64.6659 | 114.3 | 127 | 125.5 | 135.7 | 163.3 | 27.3 | 21.3 | 41.2 | 4 |  |  | 271.6 | 262.2 | 392.7 | 253.8 | 247.3 | 358.6 | 357.3
2446.3 | 746.3 | 136.5 | 54.6 | 63.8243 | 114.1 | 126.4 | 125.4 | 135.3 | 164.7 | 27.4 | 21.3 | 41.2 | 3.1 |  |  | 271.6 | 262.4 | 390.6 | 254 | 247.6 | 360.4 | 358
2447.3 | 747.3 | 138.5 | 55.4 | 64.7594 | 113.6 | 126.5 | 125.6 | 135 | 163.7 | 27.6 | 21.3 | 41.2 | 2.8 |  |  | 271.7 | 260 | 384.9 | 254.2 | 247.4 | 357.1 | 355.9
2448.3 | 748.3 | 138.5 | 55.4 | 64.7594 | 114 | 127.2 | 125.9 | 134.8 | 161.7 | 27.6 | 21.3 | 41.3 | 3.6 |  |  | 271.7 | 258.1 | 382.3 | 254.5 | 248.8 | 359.4 | 355.8
2449.3 | 749.3 | 140.1 | 56.04 | 65.5075 | 114.2 | 126.9 | 126 | 134.4 | 161.4 | 27.6 | 21.3 | 41.4 | 3.2 |  |  | 271.8 | 258.3 | 384.4 | 254.8 | 248.9 | 364 | 359.2
2450.3 | 750.3 | 138.6 | 55.44 | 64.8062 | 114.4 | 126.6 | 126.3 | 134 | 161.5 | 27.6 | 21.3 | 41.5 | 3.2 |  |  | 271.9 | 258.4 | 382.2 | 255.2 | 249.1 | 362.2 | 359.4
2451.3 | 751.3 | 137 | 54.8 | 64.058 | 114.6 | 126.3 | 126.2 | 134.1 | 162.8 | 27.6 | 21.3 | 41.5 | 2.6 |  |  | 272 | 257.7 | 383.1 | 255.5 | 247.9 | 359.4 | 356.8
2452.3 | 752.3 | 136.7 | 54.68 | 63.9178 | 114.8 | 125.7 | 126.1 | 134.5 | 163.5 | 27.6 | 21.3 | 41.5 | 2.6 |  |  | 272.1 | 254.9 | 384.9 | 255.8 | 246.1 | 354.1 | 358
2453.3 | 753.3 | 136.9 | 54.76 | 64.0113 | 115 | 125.2 | 126.2 | 134.7 | 162.8 | 27.5 | 21.3 | 41.5 | 2.2 |  |  | 272.3 | 251.5 | 382.3 | 256.2 | 242.4 | 348.2 | 358.1
2454.3 | 754.3 | 138.4 | 55.36 | 64.7127 | 115.1 | 124.8 | 126.4 | 134.5 | 161.1 | 27.4 | 21.3 | 41.5 | 1.9 |  |  | 272.4 | 249.1 | 378.4 | 256.4 | 240.2 | 348.4 | 358.5
2455.3 | 755.3 | 139.2 | 55.68 | 65.0867 | 115.2 | 124.4 | 126.5 | 134.4 | 160.2 | 27.4 | 21.3 | 41.5 | 2.4 |  |  | 272.5 | 247.4 | 378.9 | 256.7 | 238.3 | 349.8 | 359.8
2456.3 | 756.3 | 139.1 | 55.64 | 65.04 | 115.1 | 124.1 | 126.2 | 134.2 | 160.4 | 27.4 | 21.3 | 41.5 | 2 |  |  | 272.7 | 242.9 | 378 | 256.9 | 235.1 | 348.3 | 360.8
2457.3 | 757.3 | 139.5 | 55.8 | 65.227 | 114.9 | 124.1 | 126.1 | 133.8 | 159.2 | 27.4 | 21.3 | 41.4 | 1.7 |  |  | 272.8 | 240.5 | 379 | 257.1 | 232.3 | 348.7 | 361.1
2458.3 | 758.3 | 140.6 | 56.24 | 65.7413 | 114.5 | 123.8 | 126 | 133.3 | 158.3 | 27.4 | 21.3 | 41.2 | 1.9 |  |  | 273 | 238.2 | 377.2 | 257.2 | 231 | 350 | 361.4
2459.3 | 759.3 | 140.8 | 56.32 | 65.8348 | 114.4 | 123.7 | 125.5 | 133.3 | 156.8 | 27.4 | 21.3 | 41.2 | 1.9 |  |  | 273.1 | 237.2 | 376.6 | 257.3 | 229.4 | 348.9 | 359.2
2460.3 | 760.3 | 140.8 | 56.32 | 65.8348 | 113.9 | 123.9 | 124.9 | 133.7 | 157.2 | 27.4 | 21.3 | 41.3 | 2.1 |  |  | 273.1 | 240.4 | 378.7 | 257.4 | 232.6 | 357.2 | 364.4
2461.3 | 761.3 | 139.7 | 55.88 | 65.3205 | 113.5 | 124.1 | 124.9 | 133.9 | 159.4 | 27.4 | 21.3 | 41.3 | 2 |  |  | 273.2 | 246 | 377.6 | 257.5 | 235.3 | 359.4 | 363.5
2462.3 | 762.3 | 135.8 | 54.32 | 63.497 | 113.3 | 124.1 | 124.8 | 134 | 160.8 | 27.3 | 21.3 | 41.4 | 1.9 |  |  | 273.2 | 251.7 | 375.2 | 257.6 | 242.9 | 366.4 | 362.7
2463.3 | 763.3 | 135.2 | 54.08 | 63.2164 | 113 | 123.8 | 124.9 | 133.8 | 162.1 | 27.2 | 21.3 | 41.5 | 1.9 |  |  | 273.2 | 251.3 | 376.3 | 257.6 | 244.1 | 362.9 | 362.4
2464.3 | 764.3 | 136.6 | 54.64 | 63.871 | 112.6 | 123.7 | 125 | 133.9 | 162.7 | 27.1 | 21.3 | 41.5 | 2.3 |  |  | 273.3 | 247.8 | 375.5 | 257.8 | 241.1 | 355.9 | 362.3
2465.3 | 765.3 | 138.6 | 55.44 | 64.8062 | 112.8 | 123.7 | 125.4 | 134.3 | 161.6 | 27 | 21.3 | 41.6 | 1.9 |  |  | 273.3 | 245.7 | 377.8 | 257.9 | 238.7 | 353.2 | 364.8
2466.3 | 766.3 | 137 | 54.8 | 64.058 | 113 | 124.1 | 125.7 | 134.2 | 160.5 | 27.1 | 21.3 | 41.7 | 2.3 |  |  | 273.4 | 244 | 379.2 | 258.1 | 235.7 | 348.4 | 364.3
2467.3 | 767.3 | 137.8 | 55.12 | 64.4321 | 113 | 124.2 | 125.7 | 134.3 | 159.8 | 27.1 | 21.3 | 41.8 | 2.7 |  |  | 273.4 | 242.9 | 378.2 | 258.3 | 232.7 | 343.3 | 362.8
2468.3 | 768.3 | 138.5 | 55.4 | 64.7594 | 112.8 | 124.5 | 125.9 | 134.4 | 159 | 27.1 | 21.3 | 41.9 | 3.1 |  |  | 273.4 | 240.5 | 376.4 | 258.4 | 230.9 | 338.6 | 360.9
2469.3 | 769.3 | 136.8 | 54.72 | 63.9645 | 113 | 124.7 | 126 | 134.6 | 158.5 | 27.1 | 21.3 | 41.9 | 2.9 |  |  | 273.5 | 237.9 | 371.7 | 258.5 | 229.7 | 333.7 | 359.6
2470.3 | 770.3 | 136.5 | 54.6 | 63.8243 | 112.8 | 124.8 | 125.3 | 134.8 | 157.3 | 27 | 21.3 | 41.9 | 2.6 |  |  | 273.5 | 236.6 | 371 | 258.6 | 228.2 | 335.5 | 359.8
2471.3 | 771.3 | 137 | 54.8 | 64.058 | 112.7 | 124.7 | 124.7 | 135.1 | 157.3 | 26.9 | 21.3 | 41.9 | 2.5 |  |  | 273.6 | 235.1 | 371 | 258.7 | 226.1 | 336 | 358.9
2472.3 | 772.3 | 139.5 | 55.8 | 65.227 | 112.7 | 124.3 | 124.6 | 135.2 | 157.5 | 26.9 | 21.3 | 41.9 | 2.7 |  |  | 273.6 | 235.8 | 367.8 | 258.8 | 224.4 | 331.5 | 357.6
2473.3 | 773.3 | 137.2 | 54.88 | 64.1516 | 112.6 | 124 | 124.7 | 135 | 157.3 | 26.8 | 21.3 | 42 | 2.2 |  |  | 273.7 | 233.3 | 362.4 | 258.8 | 221.3 | 323.5 | 352.5
2474.3 | 774.3 | 139.1 | 55.64 | 65.04 | 113.3 | 124.4 | 125 | 135 | 157.2 | 26.7 | 21.3 | 41.9 | 2 |  |  | 273.7 | 230.9 | 358.5 | 258.9 | 218 | 316.4 | 349.9
2475.3 | 775.3 | 139.4 | 55.76 | 65.1802 | 114.2 | 124.8 | 125.1 | 134.7 | 157 | 26.7 | 21.3 | 42 | 2 |  |  | 273.8 | 231.6 | 359 | 258.9 | 216.7 | 310.5 | 348.4
2476.3 | 776.3 | 139.9 | 55.96 | 65.414 | 114.9 | 125.3 | 125 | 134 | 157.1 | 26.8 | 21.3 | 42.1 | 1.7 |  |  | 273.8 | 232 | 355.8 | 258.9 | 215.5 | 304.9 | 347.9
2477.3 | 777.3 | 139.3 | 55.72 | 65.1335 | 115.2 | 126 | 124.5 | 133.7 | 156.9 | 26.8 | 21.3 | 42.1 | 1.7 |  |  | 273.8 | 228.4 | 350.6 | 258.9 | 212.3 | 299.3 | 348.4
2478.3 | 778.3 | 137.5 | 55 | 64.2918 | 115.4 | 126.5 | 124.1 | 133.3 | 155.1 | 26.8 | 21.3 | 42.1 | 1.8 |  |  | 273.9 | 227.6 | 347.2 | 258.8 | 210 | 293.9 | 346.7
2479.3 | 779.3 | 139.8 | 55.92 | 65.3673 | 115.4 | 126.6 | 123.6 | 133.4 | 153.5 | 26.7 | 21.3 | 42.1 | 2 |  |  | 274 | 224.9 | 343.6 | 258.7 | 208.2 | 292.2 | 345.5
2480.3 | 780.3 | 139.8 | 55.92 | 65.3673 | 115.6 | 126.3 | 123.5 | 133.6 | 153.2 | 26.7 | 21.3 | 42.3 | 2.1 |  |  | 274 | 223 | 341.3 | 258.6 | 207.2 | 296.2 | 348.7
2481.3 | 781.3 | 138.2 | 55.28 | 64.6191 | 115.5 | 125.5 | 123.2 | 133.6 | 152.8 | 26.6 | 21.3 | 42.3 | 1.8 |  |  | 274 | 221.1 | 339.9 | 258.5 | 206.2 | 302.2 | 352.2
2482.3 | 782.3 | 141 | 56.4 | 65.9284 | 115.2 | 125.4 | 122.8 | 133.4 | 152.5 | 26.5 | 21.3 | 42.4 | 2.3 |  |  | 274 | 221.6 | 339.6 | 258.3 | 206.1 | 307 | 355
2483.3 | 783.3 | 139.7 | 55.88 | 65.3205 | 114.9 | 125.3 | 122.3 | 133.1 | 153.7 | 26.5 | 21.3 | 42.5 | 2.7 |  |  | 274 | 219 | 333.7 | 258.2 | 203.7 | 304.6 | 352.9
2484.3 | 784.3 | 139.6 | 55.84 | 65.2737 | 114.6 | 125.3 | 122.6 | 132.7 | 153.4 | 26.5 | 21.3 | 42.5 | 2.4 |  |  | 273.9 | 218.5 | 336.5 | 258 | 204.2 | 312.2 | 355.5
2485.3 | 785.3 | 139.8 | 55.92 | 65.3673 | 115 | 125.5 | 122.7 | 132.5 | 155 | 26.5 | 21.3 | 42.6 | 2.7 |  |  | 273.9 | 219.7 | 343.1 | 257.9 | 204.6 | 318.8 | 362.2
2486.3 | 786.3 | 141.9 | 56.76 | 66.3492 | 114.8 | 125.7 | 122.6 | 132.5 | 157 | 26.5 | 21.3 | 42.6 | 2.5 |  |  | 273.9 | 218.6 | 346.3 | 257.7 | 204.9 | 323.1 | 363.8
2487.3 | 787.3 | 137.6 | 55.04 | 64.3386 | 114.4 | 125.7 | 123 | 132.8 | 156.7 | 26.6 | 21.3 | 42.5 | 2.4 |  |  | 273.8 | 217.3 | 347.9 | 257.6 | 203.9 | 323.4 | 361.1
2488.3 | 788.3 | 139.1 | 55.64 | 65.04 | 114.4 | 125.5 | 123.2 | 133.2 | 156.1 | 26.6 | 21.3 | 42.4 | 2.6 |  |  | 273.7 | 215.7 | 350.4 | 257.5 | 204.6 | 326.9 | 364.4
2489.3 | 789.3 | 138 | 55.2 | 64.5256 | 114.2 | 125.7 | 123.3 | 133.2 | 156.2 | 26.6 | 21.3 | 42.5 | 2.8 |  |  | 273.6 | 216.6 | 353.8 | 257.3 | 205.8 | 327.7 | 364.2
2490.3 | 790.3 | 138.2 | 55.28 | 64.6191 | 114.1 | 125.7 | 123.6 | 133.2 | 155.8 | 26.6 | 21.3 | 42.5 | 2.9 |  |  | 273.5 | 215.7 | 354.8 | 257.2 | 204.5 | 322 | 358.6
2491.3 | 791.3 | 140.9 | 56.36 | 65.8816 | 114.4 | 126 | 123.8 | 133.5 | 155.6 | 26.5 | 21.3 | 42.5 | 3.4 |  |  | 273.4 | 212.6 | 353 | 257.1 | 202.3 | 316.7 | 354.9
2492.3 | 792.3 | 135.8 | 54.32 | 63.497 | 114.3 | 126.2 | 124 | 133.8 | 154.9 | 26.4 | 21.3 | 42.5 | 2.6 |  |  | 273.3 | 213.7 | 355.8 | 257 | 201.8 | 314.6 | 354.5
2493.3 | 793.3 | 138.1 | 55.24 | 64.5724 | 114.3 | 126.3 | 124.2 | 133.6 | 156.1 | 26.5 | 21.3 | 42.4 | 1.8 |  |  | 273.3 | 215.5 | 356.9 | 257 | 201.8 | 312.7 | 355.3
2494.3 | 794.3 | 139 | 55.6 | 64.9932 | 114.2 | 126.2 | 124.5 | 133.6 | 156.7 | 26.5 | 21.3 | 42.4 | 2 |  |  | 273.2 | 216 | 358.1 | 256.9 | 201.2 | 313.9 | 355
2495.3 | 795.3 | 137.9 | 55.16 | 64.4789 | 114.2 | 126.4 | 124.4 | 133.5 | 156 | 26.6 | 21.3 | 42.3 | 2.8 |  |  | 273.1 | 219.6 | 360.6 | 256.8 | 202.7 | 312.5 | 355.1
2496.3 | 796.3 | 136.6 | 54.64 | 63.871 | 114 | 126.7 | 124.1 | 133.5 | 157 | 26.7 | 21.3 | 42.3 | 4.4 |  |  | 273.1 | 226.4 | 361.3 | 256.7 | 204.4 | 311.6 | 356.4
2497.3 | 797.3 | 138.7 | 55.48 | 64.8529 | 114.1 | 126.7 | 123.9 | 133.5 | 157.5 | 26.8 | 21.3 | 42.3 | 3.8 |  |  | 273 | 228.3 | 365.9 | 256.6 | 204.3 | 308 | 355.6
2498.3 | 798.3 | 137.5 | 55 | 64.2918 | 114.1 | 126 | 123.7 | 133.4 | 158.4 | 26.8 | 21.3 | 42.3 | 2.6 |  |  | 272.9 | 230.7 | 364.6 | 256.5 | 205.7 | 305.5 | 351.7
2499.3 | 799.3 | 137.7 | 55.08 | 64.3853 | 113.8 | 125.4 | 123.4 | 132.9 | 159.9 | 26.8 | 21.3 | 42.3 | 2.3 |  |  | 272.9 | 236.1 | 366.3 | 256.3 | 210.6 | 307.1 | 350.9
2500.3 | 800.3 | 138.2 | 55.28 | 64.6191 | 113.8 | 125.3 | 123.7 | 132.9 | 161.3 | 26.8 | 21.3 | 42.3 | 3 |  |  | 272.8 | 244 | 371.1 | 256.2 | 216.1 | 316.3 | 354
2501.3 | 801.3 | 137 | 54.8 | 64.058 | 113.9 | 125.3 | 123.9 | 132.9 | 162.2 | 26.8 | 21.3 | 42.4 | 4.2 |  |  | 272.7 | 240.8 | 370 | 256.1 | 215.9 | 319.9 | 355.3
2502.3 | 802.3 | 138.5 | 55.4 | 64.7594 | 114.3 | 125.4 | 124 | 132.7 | 161.1 | 26.8 | 21.3 | 42.4 | 6 |  |  | 272.7 | 240.4 | 369.1 | 256 | 215 | 317.2 | 354.6
2503.3 | 803.3 | 139.1 | 55.64 | 65.04 | 114.6 | 125.8 | 124 | 132.7 | 160.8 | 26.8 | 21.3 | 42.3 | 6.4 |  |  | 272.8 | 243.5 | 374.6 | 256 | 215.6 | 318.8 | 355.8
2504.3 | 804.3 | 137.2 | 54.88 | 64.1516 | 115.2 | 125.9 | 124.2 | 132.6 | 163.2 | 26.8 | 21.3 | 42.2 | 7.1 |  |  | 272.8 | 241.5 | 374.6 | 255.9 | 214.6 | 318.4 | 357.5
2505.3 | 805.3 | 138 | 55.2 | 64.5256 | 115.7 | 125.6 | 124.3 | 132.6 | 162.8 | 26.7 | 21.3 | 42.1 | 6.4 |  |  | 272.8 | 240 | 374.7 | 255.9 | 213.1 | 316.4 | 356.2
2506.3 | 806.3 | 137.6 | 55.04 | 64.3386 | 116.1 | 125.4 | 124.5 | 132.8 | 162.6 | 26.7 | 21.3 | 42.1 | 6.8 |  |  | 272.9 | 238.6 | 368.6 | 255.9 | 213 | 311.6 | 352.2
2507.3 | 807.3 | 137.4 | 54.96 | 64.2451 | 116.4 | 125.7 | 124.5 | 133.2 | 161.8 | 26.8 | 21.3 | 42.2 | 6.6 |  |  | 273.1 | 235.2 | 368.9 | 255.9 | 211.2 | 310.5 | 352.6
2508.3 | 808.3 | 138.3 | 55.32 | 64.6659 | 116.4 | 125.5 | 124.3 | 133.7 | 160.5 | 26.8 | 21.3 | 42.2 | 4.3 |  |  | 273.2 | 232.8 | 365 | 255.9 | 210.1 | 310.2 | 356.7
2509.3 | 809.3 | 137.5 | 55 | 64.2918 | 116.3 | 125.4 | 124.4 | 133.7 | 159.2 | 26.9 | 21.3 | 42.2 | 4.6 |  |  | 273.4 | 232.7 | 366.1 | 255.9 | 209.5 | 310.5 | 356.6
2510.3 | 810.3 | 138.4 | 55.36 | 64.7127 | 116.3 | 125.3 | 124.7 | 133.6 | 160.3 | 27 | 21.3 | 42.1 | 5.5 |  |  | 273.4 | 235.1 | 372.9 | 255.8 | 212.5 | 315.6 | 358.4
2511.3 | 811.3 | 138.5 | 55.4 | 64.7594 | 115.6 | 125.3 | 125.1 | 133.3 | 162.9 | 27.1 | 21.3 | 42.1 | 5.1 |  |  | 273.4 | 238.7 | 376.4 | 255.8 | 214.5 | 318.4 | 358
2512.3 | 812.3 | 139.8 | 55.92 | 65.3673 | 115 | 125.2 | 125.3 | 132.9 | 165.9 | 27.2 | 21.3 | 42.2 | 6.1 |  |  | 273.5 | 245.1 | 378.5 | 255.8 | 220.6 | 318.5 | 357.2
2513.3 | 813.3 | 139.5 | 55.8 | 65.227 | 115.3 | 125.5 | 124.9 | 133 | 168.3 | 27.2 | 21.3 | 42.2 | 5.2 |  |  | 273.6 | 251.5 | 377.8 | 255.8 | 223.2 | 317.3 | 354.1
2514.3 | 814.3 | 138.7 | 55.48 | 64.8529 | 115.6 | 125.7 | 125 | 133.3 | 169.1 | 27.3 | 21.3 | 42.3 | 5.5 |  |  | 273.7 | 259 | 380.7 | 255.8 | 228 | 322.3 | 356.1
2515.3 | 815.3 | 139.2 | 55.68 | 65.0867 | 115.2 | 125.6 | 125.6 | 133.6 | 170.8 | 27.3 | 21.3 | 42.4 | 5.4 |  |  | 273.8 | 265.2 | 384.3 | 255.8 | 235.1 | 333.9 | 361.4
2516.3 | 816.3 | 138.4 | 55.36 | 64.7127 | 115.1 | 125.4 | 126.1 | 134 | 171.9 | 27.3 | 21.3 | 42.4 | 5.2 |  |  | 273.9 | 272.8 | 385.4 | 255.8 | 240 | 338.8 | 362.3
2517.3 | 817.3 | 138.2 | 55.28 | 64.6191 | 115.3 | 125.2 | 126.6 | 134.1 | 171.9 | 27.3 | 21.3 | 42.4 | 5.9 |  |  | 274 | 276.8 | 384.8 | 255.9 | 246.4 | 343.5 | 359.4
2518.3 | 818.3 | 139.7 | 55.88 | 65.3205 | 115.8 | 125.1 | 127 | 134.3 | 172.3 | 27.3 | 21.3 | 42.4 | 5.5 |  |  | 274.1 | 283.3 | 388 | 256 | 250.4 | 352.5 | 361.6
2519.3 | 819.3 | 139.1 | 55.64 | 65.04 | 116.2 | 125 | 127.2 | 134.5 | 173.4 | 27.3 | 21.3 | 42.4 | 5.6 |  |  | 274.3 | 286.5 | 388.4 | 256.1 | 254.2 | 355.6 | 367.6
2520.3 | 820.3 | 138.4 | 55.36 | 64.7127 | 116.5 | 124.8 | 127.5 | 134.7 | 172.7 | 27.3 | 21.3 | 42.4 | 5 |  |  | 274.5 | 283.4 | 387.2 | 256.3 | 252.8 | 349.2 | 363.4
2521.3 | 821.3 | 138.6 | 55.44 | 64.8062 | 116.2 | 124.4 | 127.6 | 134.6 | 170.9 | 27.3 | 21.3 | 42.3 | 5.4 |  |  | 274.7 | 277.4 | 384.2 | 256.5 | 248.9 | 344.5 | 362.4
2522.3 | 822.3 | 137.8 | 55.12 | 64.4321 | 116 | 124.5 | 127.8 | 134.7 | 170 | 27.3 | 21.3 | 42.3 | 5.5 |  |  | 274.9 | 275.4 | 386.9 | 256.8 | 246.5 | 342 | 364.9
2523.3 | 823.3 | 138.1 | 55.24 | 64.5724 | 116.1 | 125 | 128.2 | 134.8 | 170.9 | 27.2 | 21.3 | 42.2 | 4.3 |  |  | 275.1 | 273.4 | 392.1 | 257 | 244.6 | 339.9 | 365.9
2524.3 | 824.3 | 137.1 | 54.84 | 64.1048 | 116.1 | 125.3 | 128.5 | 135.3 | 171.3 | 27.2 | 21.3 | 42.1 | 3.7 |  |  | 275.3 | 271.1 | 392.5 | 257.1 | 242.8 | 334.2 | 362.1
2525.3 | 825.3 | 137.4 | 54.96 | 64.2451 | 116.4 | 125.6 | 128.8 | 135.6 | 171.1 | 27.2 | 21.3 | 42.1 | 4.1 |  |  | 275.5 | 271.9 | 391.6 | 257.3 | 243.6 | 338.8 | 360.3
2526.3 | 826.3 | 138.1 | 55.24 | 64.5724 | 116.7 | 125.6 | 128.9 | 135.7 | 171.1 | 27.1 | 21.3 | 42.1 | 4.2 |  |  | 275.7 | 274.5 | 397 | 257.5 | 243.8 | 339.1 | 362.1
2527.3 | 827.3 | 137.5 | 55 | 64.2918 | 117.1 | 126.1 | 128.8 | 135.8 | 169.8 | 27.1 | 21.3 | 42 | 3.7 |  |  | 275.9 | 270.8 | 394.9 | 257.6 | 241.2 | 334.2 | 359
2528.3 | 828.3 | 138 | 55.2 | 64.5256 | 118 | 127 | 128.8 | 136 | 168.8 | 27 | 21.3 | 42 | 4.4 |  |  | 276.1 | 269.2 | 390 | 257.8 | 238.7 | 326.6 | 354.1
2529.3 | 829.3 | 138.2 | 55.28 | 64.6191 | 118.4 | 127.8 | 128.9 | 136.1 | 169.7 | 27 | 21.3 | 42 | 3.6 |  |  | 276.3 | 272.6 | 386.5 | 258 | 240.4 | 325 | 350.9
2530.3 | 830.3 | 138 | 55.2 | 64.5256 | 117.9 | 127.8 | 128.6 | 136 | 170.3 | 26.9 | 21.3 | 42.1 | 3.3 |  |  | 276.5 | 278.6 | 383 | 258.1 | 243.9 | 330 | 351.8
2531.3 | 831.3 | 137.3 | 54.92 | 64.1983 | 117.7 | 127.6 | 128.9 | 136 | 169.6 | 26.8 | 21.3 | 42.1 | 3.8 |  |  | 276.7 | 281.6 | 382.6 | 258.2 | 246.4 | 329.3 | 351.8
2532.3 | 832.3 | 136.4 | 54.56 | 63.7775 | 118.1 | 127.5 | 129 | 136 | 169.7 | 26.8 | 21.3 | 42.1 | 4.5 |  |  | 277 | 288.3 | 379.1 | 258.3 | 248.5 | 322.7 | 348.4
2533.3 | 833.3 | 136.2 | 54.48 | 63.684 | 118.5 | 127.6 | 128.6 | 136.1 | 169.9 | 26.7 | 21.3 | 42 | 4.3 |  |  | 277.2 | 292.6 | 373.1 | 258.5 | 251.5 | 319.8 | 345.3
2534.3 | 834.3 | 140.9 | 56.36 | 65.8816 | 118.6 | 127.9 | 128.5 | 136.5 | 171.6 | 26.7 | 21.3 | 41.9 | 4 |  |  | 277.5 | 297.2 | 366.8 | 258.6 | 254.5 | 314.8 | 342.7
2535.3 | 835.3 | 140.3 | 56.12 | 65.601 | 118.3 | 127.7 | 128.6 | 136.7 | 173.9 | 26.7 | 21.3 | 41.8 | 3.9 |  |  | 277.7 | 300.8 | 361.1 | 258.8 | 257.5 | 311.6 | 339.7
2536.3 | 836.3 | 143.6 | 57.44 | 67.1441 | 118.4 | 127.2 | 128.6 | 136.7 | 173.5 | 26.7 | 21.3 | 41.7 | 3 |  |  | 277.9 | 305 | 357.6 | 258.9 | 261 | 313.7 | 339.2
2537.3 | 837.3 | 142.3 | 56.92 | 66.5362 | 119 | 126.7 | 128.3 | 136.8 | 173.2 | 26.8 | 21.3 | 41.7 | 2.4 |  |  | 278.2 | 310.6 | 358 | 259.1 | 266.2 | 321.2 | 341.7
2538.3 | 838.3 | 147.5 | 59 | 68.9676 | 118.7 | 126.6 | 128.1 | 137 | 175 | 27.1 | 21.3 | 41.7 | 2.5 |  |  | 278.4 | 313.8 | 359.5 | 259.3 | 268.9 | 323.8 | 344.8
2539.3 | 839.3 | 147.5 | 59 | 68.9676 | 118.6 | 126.6 | 128.4 | 137.5 | 175.3 | 27.3 | 21.3 | 41.6 | 2.4 |  |  | 278.5 | 312.5 | 359.9 | 259.4 | 269.9 | 327.4 | 346.5
2540.3 | 840.3 | 146.2 | 58.48 | 68.3598 | 118.6 | 126.6 | 128.5 | 137.7 | 174 | 27.4 | 21.3 | 41.5 | 2.6 |  |  | 278.8 | 307.2 | 361.7 | 259.6 | 266 | 327.7 | 350.2
2541.3 | 841.3 | 146.9 | 58.76 | 68.6871 | 118.7 | 126.5 | 128.9 | 137.9 | 172 | 27.6 | 21.3 | 41.5 | 3 |  |  | 279.1 | 302.9 | 364.4 | 259.8 | 262.5 | 329 | 355
2542.3 | 842.3 | 147.5 | 59 | 68.9676 | 118.5 | 126.7 | 129.2 | 138.1 | 171.1 | 27.6 | 21.3 | 41.6 | 3.3 |  |  | 279.3 | 300.5 | 371.4 | 259.9 | 262.7 | 337.9 | 361.8
2543.3 | 843.3 | 148.2 | 59.28 | 69.2949 | 118.4 | 126.5 | 129.7 | 138.2 | 171.8 | 27.7 | 21.3 | 41.7 | 3.6 |  |  | 279.5 | 305.3 | 383.1 | 260.1 | 271 | 355.1 | 372.2
2544.3 | 844.3 | 149.2 | 59.68 | 69.7625 | 118 | 126.9 | 130.1 | 138.1 | 174.4 | 27.7 | 21.3 | 41.8 | 3.1 |  |  | 279.7 | 307.5 | 389.7 | 260.3 | 272.4 | 356.7 | 371.2
2545.3 | 845.3 | 150.9 | 60.36 | 70.5574 | 117.7 | 127.4 | 130.4 | 138.2 | 174.8 | 27.7 | 21.3 | 41.7 | 2.9 |  |  | 279.8 | 304.3 | 388.9 | 260.4 | 271.2 | 353.2 | 367.3
2546.3 | 846.3 | 156.1 | 62.44 | 72.9888 | 117.2 | 128.5 | 130.9 | 138.3 | 173.3 | 27.7 | 21.3 | 41.6 | 3.4 |  |  | 280 | 301.3 | 388.8 | 260.6 | 270.7 | 354.9 | 366.4
2547.3 | 847.3 | 161.9 | 64.76 | 75.7007 | 117.5 | 129.1 | 131.2 | 138.3 | 171.8 | 27.6 | 21.3 | 41.7 | 3.7 |  |  | 280.1 | 299.4 | 390.4 | 260.8 | 269.8 | 357.9 | 366.7
2548.3 | 848.3 | 165.7 | 66.28 | 77.4775 | 117.5 | 129.4 | 131.4 | 138.3 | 170.8 | 27.6 | 21.3 | 41.7 | 3 |  |  | 280.2 | 297.1 | 392.1 | 261.1 | 268.4 | 360.5 | 369.4
2549.3 | 849.3 | 169.5 | 67.8 | 79.2543 | 117.3 | 129.4 | 131.7 | 138.8 | 170.1 | 27.5 | 21.3 | 41.8 | 3.4 |  |  | 280.5 | 296.1 | 394.6 | 261.3 | 269.3 | 358.5 | 369.6
2550.3 | 850.3 | 174.8 | 69.92 | 81.7325 | 117.3 | 129.3 | 132.1 | 138.9 | 169.9 | 27.5 | 21.3 | 41.8 | 3.6 |  |  | 280.8 | 294.3 | 393 | 261.6 | 268.9 | 357.4 | 368.9
2551.3 | 851.3 | 183.7 | 73.48 | 85.8939 | 117.8 | 129.3 | 132.4 | 138.7 | 168.9 | 27.4 | 21.3 | 41.9 | 2.8 |  |  | 280.9 | 291.9 | 392.3 | 261.8 | 266.4 | 359.3 | 372.4
2552.3 | 852.3 | 193.7 | 77.48 | 90.5697 | 118.1 | 129.1 | 132.6 | 138.7 | 168 | 27.4 | 21.3 | 41.9 | 2.7 |  |  | 281.1 | 291.8 | 395 | 262 | 267.8 | 364.8 | 375
2553.3 | 853.3 | 200.9 | 80.36 | 93.9362 | 117.5 | 128.8 | 132.6 | 138.9 | 169.3 | 27.4 | 21.3 | 41.9 | 3 |  |  | 281.4 | 290.6 | 400.7 | 262.2 | 271.6 | 372.6 | 383.2
2554.3 | 854.3 | 197.4 | 78.96 | 92.2997 | 117.2 | 128.5 | 132.3 | 138.9 | 170.7 | 27.4 | 21.3 | 41.9 | 4.1 |  |  | 281.7 | 290 | 404.6 | 262.4 | 271.2 | 374.2 | 388
2555.3 | 855.3 | 194.1 | 77.64 | 90.7567 | 117.9 | 128.6 | 132.3 | 139.4 | 170.3 | 27.4 | 21.3 | 41.9 | 4.1 |  |  | 281.9 | 287.1 | 404 | 262.6 | 269 | 374.7 | 387.7
2556.3 | 856.3 | 194.6 | 77.84 | 90.9905 | 118.2 | 128.9 | 132.2 | 140.2 | 170 | 27.3 | 21.3 | 42 | 4.2 |  |  | 282 | 282.2 | 407 | 262.8 | 265.2 | 373.1 | 386.3
2557.3 | 857.3 | 194.4 | 77.76 | 90.897 | 118.5 | 129.4 | 132.7 | 140.7 | 169.6 | 27.3 | 21.3 | 42.1 | 4.5 |  |  | 282.2 | 278.6 | 409.5 | 263.1 | 261.5 | 366.5 | 385.1
2558.3 | 858.3 | 194 | 77.6 | 90.7099 | 118.8 | 129.4 | 133.1 | 141.2 | 169.7 | 27.3 | 21.3 | 42.4 | 5 |  |  | 282.4 | 277 | 413.4 | 263.3 | 259.6 | 365.6 | 386.7
2559.3 | 859.3 | 191.2 | 76.48 | 89.4007 | 119.2 | 130.2 | 133.3 | 141.4 | 170.9 | 27.3 | 21.3 | 42.5 | 3.9 |  |  | 282.7 | 278.6 | 421 | 263.6 | 260.5 | 371.9 | 389.9
2560.3 | 860.3 | 188.7 | 75.48 | 88.2318 | 119.3 | 131.1 | 133.7 | 141 | 173.9 | 27.3 | 21.3 | 42.6 | 4.7 |  |  | 282.8 | 285.3 | 426.5 | 263.8 | 267.2 | 387.9 | 400.1
2561.3 | 861.3 | 187 | 74.8 | 87.4369 | 120.2 | 131.4 | 133.8 | 141 | 175.7 | 27.3 | 21.3 | 42.7 | 5.6 |  |  | 283 | 286.2 | 429.3 | 264 | 267.4 | 392.2 | 401.2
2562.3 | 862.3 | 190.4 | 76.16 | 89.0267 | 121.2 | 131.7 | 133.8 | 141.2 | 176.2 | 27.3 | 21.3 | 42.7 | 5.4 |  |  | 283.1 | 286.5 | 431.2 | 264.2 | 267.3 | 400.9 | 407.7
2563.3 | 863.3 | 192 | 76.8 | 89.7748 | 121.4 | 132.2 | 133.8 | 142.1 | 176.3 | 27.3 | 21.3 | 42.8 | 4.1 |  |  | 283.3 | 282.6 | 428.7 | 264.4 | 266.5 | 400.7 | 406.4
2564.3 | 864.3 | 190.1 | 76.04 | 88.8864 | 120.8 | 132.8 | 134.2 | 143 | 176.3 | 27.4 | 21.3 | 42.9 | 3.9 |  |  | 283.4 | 276.9 | 422.8 | 264.7 | 263.1 | 395.8 | 399
2565.3 | 865.3 | 190.4 | 76.16 | 89.0267 | 120.7 | 132.9 | 134.7 | 144 | 175.8 | 27.4 | 21.3 | 42.9 | 4.4 |  |  | 283.8 | 276.2 | 420.7 | 265.1 | 264.3 | 396.1 | 394.5
2566.3 | 866.3 | 190.5 | 76.2 | 89.0734 | 121.1 | 134 | 135.1 | 145.1 | 177.1 | 27.5 | 21.3 | 43 | 4.7 |  |  | 284.1 | 287.7 | 428.5 | 265.4 | 269.2 | 398.7 | 395.2
2567.3 | 867.3 | 190.3 | 76.12 | 88.9799 | 121.3 | 134.3 | 135.2 | 146 | 181.4 | 27.5 | 21.3 | 43.1 | 6.3 |  |  | 284.4 | 290 | 432.4 | 265.6 | 272.9 | 408.2 | 400.2
2568.3 | 868.3 | 191.6 | 76.64 | 89.5877 | 121.9 | 134.6 | 135.3 | 146.4 | 183.2 | 27.5 | 21.3 | 43.2 | 6.9 |  |  | 284.6 | 296.5 | 441.3 | 265.9 | 278.9 | 415.2 | 406.7
2569.3 | 869.3 | 191.6 | 76.64 | 89.5877 | 122.6 | 135.3 | 135.4 | 146.4 | 186 | 27.5 | 21.3 | 43.3 | 5.4 |  |  | 284.7 | 299.3 | 453.2 | 266.3 | 282.3 | 423.6 | 411.4
2570.3 | 870.3 | 190.9 | 76.36 | 89.2604 | 123.1 | 135.6 | 135.7 | 146.8 | 188.8 | 27.5 | 21.3 | 43.2 | 4 |  |  | 284.9 | 304.3 | 459.8 | 266.7 | 286.8 | 424.7 | 413.6
2571.3 | 871.3 | 190.9 | 76.36 | 89.2604 | 123.9 | 135.7 | 136.2 | 147.6 | 191 | 27.5 | 21.3 | 43.1 | 3.1 |  |  | 285.2 | 309.3 | 465.1 | 267.1 | 291.2 | 430.2 | 418.3
2572.3 | 872.3 | 190.5 | 76.2 | 89.0734 | 125 | 135.7 | 136.1 | 148.6 | 192.3 | 27.5 | 21.3 | 43.2 | 3.7 |  |  | 285.5 | 308 | 464.1 | 267.5 | 290.9 | 428.2 | 415.9
2573.3 | 873.3 | 191.7 | 76.68 | 89.6345 | 126.1 | 135.8 | 136.2 | 149 | 191.8 | 27.4 | 21.3 | 43.3 | 4.7 |  |  | 285.7 | 311.4 | 468.1 | 268 | 294.1 | 433.8 | 420.4
2574.3 | 874.3 | 190.9 | 76.36 | 89.2604 | 126.9 | 135.4 | 136.7 | 149 | 193.2 | 27.4 | 21.3 | 43.3 | 4.3 |  |  | 285.9 | 310.8 | 470.3 | 268.5 | 296.6 | 433.3 | 422
2575.3 | 875.3 | 192 | 76.8 | 89.7748 | 127.4 | 135.6 | 137.3 | 149.1 | 192.8 | 27.4 | 21.3 | 43.3 | 5.4 |  |  | 286.2 | 305.4 | 468.1 | 269.1 | 292.6 | 428.1 | 415.1
2576.3 | 876.3 | 189.8 | 75.92 | 88.7461 | 128.1 | 136.3 | 137.8 | 149.3 | 191.2 | 27.4 | 21.3 | 43.3 | 5 |  |  | 286.4 | 303.5 | 474 | 269.7 | 289.9 | 430.3 | 421.5
2577.3 | 877.3 | 188.7 | 75.48 | 88.2318 | 128.6 | 136.8 | 137.8 | 150 | 192.3 | 27.4 | 21.3 | 43.4 | 4.8 |  |  | 286.8 | 306.2 | 482.7 | 270.3 | 290.2 | 427.9 | 426.6
2578.3 | 878.3 | 191.6 | 76.64 | 89.5877 | 128.5 | 137 | 138.7 | 150.5 | 192.8 | 27.5 | 21.3 | 43.5 | 5.3 |  |  | 286.9 | 312.5 | 483.3 | 270.8 | 290.6 | 429 | 423.8
2579.3 | 879.3 | 191 | 76.4 | 89.3072 | 129.4 | 137.2 | 139.3 | 150.5 | 192.9 | 27.5 | 21.3 | 43.6 | 5.9 |  |  | 287.1 | 316.4 | 482.2 | 271.4 | 290.9 | 423.5 | 419.4
2580.3 | 880.3 | 191 | 76.4 | 89.3072 | 130.2 | 137.9 | 139.6 | 150.5 | 195.3 | 27.5 | 21.3 | 43.7 | 5.2 |  |  | 287.5 | 320.6 | 481.9 | 271.9 | 290.1 | 419.9 | 415.1
2581.3 | 881.3 | 191.2 | 76.48 | 89.4007 | 129.9 | 138.3 | 139.3 | 151.1 | 198.5 | 27.4 | 21.3 | 43.7 | 4.4 |  |  | 287.9 | 318.7 | 485.1 | 272.5 | 288.8 | 421.3 | 422.7
2582.3 | 882.3 | 190.4 | 76.16 | 89.0267 | 129.3 | 139.4 | 139.2 | 151.3 | 196.9 | 27.3 | 21.3 | 43.7 | 5.1 |  |  | 288.4 | 313.3 | 486.3 | 273 | 284.7 | 419.4 | 425.7
2583.3 | 883.3 | 189.6 | 75.84 | 88.6526 | 130.3 | 140 | 138.9 | 151.1 | 196.4 | 27.1 | 21.3 | 43.8 | 4.1 |  |  | 288.9 | 310.5 | 482.3 | 273.4 | 283.4 | 419.3 | 428.2
2584.3 | 884.3 | 189.3 | 75.72 | 88.5123 | 131.1 | 140 | 139.3 | 151.1 | 194.1 | 27.1 | 21.3 | 43.9 | 3.7 |  |  | 289.4 | 307.2 | 480.6 | 273.9 | 279.6 | 414 | 427.6
2585.3 | 885.3 | 189.2 | 75.68 | 88.4656 | 131.3 | 140.4 | 139.9 | 151.2 | 192.7 | 27.1 | 21.3 | 43.9 | 3.6 |  |  | 290.1 | 307.9 | 483.3 | 274.3 | 280.4 | 412.7 | 424.6
2586.3 | 886.3 | 187.9 | 75.16 | 87.8577 | 131.5 | 140.6 | 139.8 | 151.2 | 191.9 | 27 | 21.3 | 43.8 | 3.4 |  |  | 290.8 | 305.9 | 481.9 | 274.7 | 278.7 | 414.7 | 427.2
2587.3 | 887.3 | 190.2 | 76.08 | 88.9331 | 131.4 | 140.6 | 139.7 | 151.4 | 192.9 | 26.9 | 21.3 | 43.7 | 3.4 |  |  | 291.4 | 303.5 | 477.8 | 275.1 | 276.3 | 408.1 | 422.5
2588.3 | 888.3 | 189.5 | 75.8 | 88.6058 | 131.9 | 140.4 | 140.3 | 151.5 | 192.2 | 26.9 | 21.3 | 43.7 | 3.1 |  |  | 291.9 | 298.5 | 472.2 | 275.5 | 273.8 | 404.3 | 420.2
2589.3 | 889.3 | 188.9 | 75.56 | 88.3253 | 131.7 | 140 | 141.2 | 151.6 | 191.1 | 26.9 | 21.3 | 43.6 | 2.7 |  |  | 292.4 | 299 | 473.3 | 275.9 | 277.6 | 408.2 | 423.2
2590.3 | 890.3 | 187.5 | 75 | 87.6707 | 131.6 | 140.1 | 141.1 | 151.8 | 191.7 | 27 | 21.3 | 43.6 | 2.7 |  |  | 292.9 | 302.5 | 469.5 | 276.2 | 280.5 | 405.9 | 419.3
2591.3 | 891.3 | 188.8 | 75.52 | 88.2785 | 131.4 | 140 | 140.5 | 152 | 192.4 | 27.1 | 21.2 | 43.6 | 2.6 |  |  | 293.3 | 310.2 | 465 | 276.5 | 287.3 | 402.9 | 415.1
2592.3 | 892.3 | 189.7 | 75.88 | 88.6993 | 131 | 139.7 | 140.4 | 152.2 | 194.7 | 27 | 21.2 | 43.7 | 2.4 |  |  | 293.7 | 317.8 | 460.2 | 276.8 | 288.3 | 397 | 411.7
2593.3 | 893.3 | 188.6 | 75.44 | 88.185 | 130.8 | 139.5 | 140.7 | 152.2 | 194.3 | 27 | 21.2 | 43.6 | 2 |  |  | 294.1 | 320.4 | 453 | 277.1 | 286.8 | 393.4 | 408.5
2594.3 | 894.3 | 191.4 | 76.56 | 89.4942 | 130.8 | 139.8 | 141.2 | 152.2 | 193 | 26.9 | 21.2 | 43.6 | 2.2 |  |  | 294.4 | 321.3 | 448.7 | 277.4 | 285.8 | 386.1 | 405.7
2595.3 | 895.3 | 188.4 | 75.36 | 88.0915 | 130.7 | 140 | 141.3 | 152.4 | 192.8 | 26.9 | 21.3 | 43.6 | 2.8 |  |  | 294.8 | 325.8 | 443.9 | 277.7 | 286.1 | 382.1 | 403.6
2596.3 | 896.3 | 189.8 | 75.92 | 88.7461 | 130.7 | 140 | 141.3 | 152.6 | 191.8 | 26.9 | 21.3 | 43.6 | 3.5 |  |  | 295.2 | 324.7 | 440.4 | 278.1 | 283.9 | 380 | 403.2
2597.3 | 897.3 | 189.9 | 75.96 | 88.7929 | 131 | 139.6 | 141.6 | 152.6 | 190.8 | 26.9 | 21.3 | 43.7 | 3.8 |  |  | 295.7 | 325 | 442.8 | 278.4 | 286 | 387.9 | 411.9
2598.3 | 898.3 | 190.9 | 76.36 | 89.2604 | 130.9 | 139.7 | 141.7 | 152.5 | 189.7 | 26.9 | 21.2 | 43.7 | 3.5 |  |  | 296.1 | 321.4 | 448.7 | 278.7 | 286.4 | 390.2 | 419.2
2599.3 | 899.3 | 190.2 | 76.08 | 88.9331 | 130.5 | 140 | 142.1 | 152.4 | 188.3 | 26.8 | 21.2 | 43.7 | 3.3 |  |  | 296.5 | 313.9 | 445.8 | 278.9 | 281.4 | 387.6 | 416
2600.3 | 900.3 | 189.5 | 75.8 | 88.6058 | 130 | 140.6 | 142.5 | 152.6 | 185.3 | 26.8 | 21.2 | 43.8 | 2.7 |  |  | 296.9 | 309.4 | 440.6 | 279 | 277.5 | 387.7 | 413.4
2601.3 | 901.3 | 188.7 | 75.48 | 88.2318 | 129.3 | 140.9 | 142.7 | 153 | 184.1 | 26.8 | 21.2 | 43.8 | 3 |  |  | 297.3 | 309.4 | 442.2 | 279.1 | 278.9 | 395.7 | 418.8
2602.3 | 902.3 | 187.6 | 75.04 | 87.7174 | 128.8 | 141.5 | 142.9 | 153.4 | 187 | 26.9 | 21.2 | 43.8 | 2.9 |  |  | 297.8 | 308.1 | 443.2 | 279.3 | 278.6 | 393.8 | 420.4
2603.3 | 903.3 | 189.9 | 75.96 | 88.7929 | 128.4 | 141.8 | 142.9 | 153.4 | 188.3 | 26.9 | 21.2 | 43.7 | 3 |  |  | 298.2 | 305 | 443.3 | 279.5 | 275 | 389.9 | 417.2
2604.3 | 904.3 | 188.4 | 75.36 | 88.0915 | 128.5 | 141.5 | 142.9 | 153.7 | 187.6 | 27 | 21.2 | 43.7 | 3.6 |  |  | 298.4 | 303.3 | 443.1 | 279.7 | 271 | 387.8 | 416.1
2605.3 | 905.3 | 189.9 | 75.96 | 88.7929 | 128.2 | 141.2 | 143 | 153.8 | 185.5 | 27 | 21.2 | 43.8 | 3.6 |  |  | 298.5 | 300.2 | 447.1 | 279.9 | 270.1 | 387.2 | 418.6
2606.3 | 906.3 | 189.3 | 75.72 | 88.5123 | 128 | 141.5 | 143 | 154 | 185.1 | 27.1 | 21.2 | 43.8 | 3.5 |  |  | 298.7 | 302 | 450.6 | 280.1 | 271.4 | 391.2 | 420.6
2607.3 | 907.3 | 188.6 | 75.44 | 88.185 | 127.9 | 141.4 | 143.2 | 153.9 | 186.7 | 27.1 | 21.2 | 43.8 | 3.2 |  |  | 299 | 300.4 | 449 | 280.2 | 272.5 | 398.6 | 423
2608.3 | 908.3 | 189.6 | 75.84 | 88.6526 | 127.6 | 141.5 | 143.4 | 153.9 | 187.6 | 27 | 21.2 | 43.8 | 2.9 |  |  | 299.2 | 298.8 | 451.1 | 280.4 | 272.1 | 398.3 | 424.4
2609.3 | 909.3 | 189.3 | 75.72 | 88.5123 | 127.7 | 141.9 | 143.3 | 154.3 | 188 | 27.1 | 21.2 | 43.9 | 3 |  |  | 299.4 | 300.2 | 454.6 | 280.5 | 271.8 | 402.8 | 426.8
2610.3 | 910.3 | 189.7 | 75.88 | 88.6993 | 128 | 141.9 | 143 | 154.4 | 188.3 | 27.1 | 21.3 | 43.9 | 2.9 |  |  | 299.6 | 299.9 | 460.2 | 280.7 | 272.2 | 407.3 | 433.8
2611.3 | 911.3 | 188 | 75.2 | 87.9045 | 128 | 141.9 | 142.5 | 154.4 | 188 | 27.2 | 21.2 | 44 | 3 |  |  | 299.8 | 300.7 | 459.7 | 280.8 | 274.4 | 411.7 | 432.9
2612.3 | 912.3 | 189.1 | 75.64 | 88.4188 | 128.3 | 141.8 | 141.6 | 154 | 187.9 | 27.2 | 21.2 | 44.1 | 2.7 |  |  | 299.9 | 303.3 | 462.7 | 281 | 280.2 | 417.9 | 431.2
2613.3 | 913.3 | 187.8 | 75.12 | 87.811 | 128.2 | 141.5 | 141.4 | 153.8 | 188.8 | 27.2 | 21.2 | 44.3 | 2.5 |  |  | 300.2 | 304.2 | 469.5 | 281.1 | 283.4 | 421.2 | 435.2
2614.3 | 914.3 | 185.3 | 74.12 | 86.642 | 128.6 | 140.8 | 141.5 | 153.7 | 190.8 | 27.3 | 21.2 | 44.4 | 2.2 |  |  | 300.5 | 301.2 | 471.9 | 281.3 | 281.1 | 419 | 436
2615.3 | 915.3 | 186.7 | 74.68 | 87.2966 | 128.9 | 141.2 | 141.5 | 154 | 188.7 | 27.2 | 21.2 | 44.6 | 2.6 |  |  | 300.7 | 305 | 474.9 | 281.5 | 284.8 | 419.7 | 436.6
2616.3 | 916.3 | 183.5 | 73.4 | 85.8004 | 129.1 | 141.5 | 141.7 | 154.6 | 188.1 | 27.2 | 21.2 | 44.7 | 2.2 |  |  | 301 | 315 | 479.6 | 281.6 | 289.8 | 431.7 | 436.9
2617.3 | 917.3 | 186.6 | 74.64 | 87.2499 | 129.1 | 141.6 | 141.7 | 155.4 | 189.2 | 27.1 | 21.2 | 44.7 | 1.9 |  |  | 301.4 | 322.9 | 489 | 281.7 | 296.1 | 439 | 443.2
2618.3 | 918.3 | 186.3 | 74.52 | 87.1096 | 129.5 | 141.2 | 141.9 | 155.6 | 191 | 27.2 | 21.2 | 44.7 | 1.9 |  |  | 302.1 | 324.8 | 493.5 | 281.9 | 297.6 | 441.5 | 447.1
2619.3 | 919.3 | 186.5 | 74.6 | 87.2031 | 129.8 | 141.7 | 142.1 | 155 | 191.4 | 27.2 | 21.2 | 44.6 | 1.6 |  |  | 302.7 | 330.9 | 492.2 | 282.3 | 303.8 | 442.8 | 444.3
2620.3 | 920.3 | 187.4 | 74.96 | 87.6239 | 129.8 | 142.5 | 142.1 | 154.8 | 192.8 | 27.3 | 21.2 | 44.5 | 1.5 |  |  | 303.1 | 343.9 | 492.3 | 282.7 | 314.9 | 449.4 | 442.4
2621.3 | 921.3 | 186.3 | 74.52 | 87.1096 | 129.8 | 142.7 | 142.5 | 154.8 | 197.5 | 27.3 | 21.2 | 44.5 | 2.2 |  |  | 303.5 | 350.8 | 493.2 | 283.1 | 324.8 | 451.8 | 439.8
2622.3 | 922.3 | 187.5 | 75 | 87.6707 | 129.9 | 142.9 | 142.9 | 155.1 | 198.6 | 27.2 | 21.2 | 44.5 | 2.3 |  |  | 303.9 | 352.9 | 494.9 | 283.5 | 324.8 | 451.9 | 435.7
2623.3 | 923.3 | 187.3 | 74.92 | 87.5772 | 130.1 | 143 | 143.3 | 155.6 | 199.7 | 27.2 | 21.2 | 44.5 | 2.2 |  |  | 304.2 | 357.4 | 496.1 | 284.1 | 328.3 | 453.9 | 437.9
2624.3 | 924.3 | 187.5 | 75 | 87.6707 | 130.8 | 143.3 | 143.8 | 156 | 199.6 | 27.2 | 21.2 | 44.6 | 2.4 |  |  | 304.4 | 351.5 | 498.7 | 284.7 | 326.2 | 456.5 | 441.2
2625.3 | 925.3 | 187.6 | 75.04 | 87.7174 | 131.4 | 143.2 | 144.1 | 156 | 198.8 | 27.2 | 21.2 | 44.7 | 2.7 |  |  | 304.8 | 350.9 | 496.4 | 285.5 | 325 | 454.5 | 437.6
2626.3 | 926.3 | 188.4 | 75.36 | 88.0915 | 132.3 | 142.8 | 145 | 155.8 | 200.5 | 27.3 | 21.2 | 44.7 | 2.8 |  |  | 305.3 | 354.7 | 495.1 | 286.2 | 326.1 | 454.9 | 439.2
2627.3 | 927.3 | 189.4 | 75.76 | 88.5591 | 132.5 | 142.9 | 145.7 | 155.7 | 201.4 | 27.3 | 21.2 | 44.7 | 3.5 |  |  | 305.8 | 359.5 | 490.6 | 286.8 | 329.5 | 454.1 | 440.4
2628.3 | 928.3 | 186.7 | 74.68 | 87.2966 | 132.7 | 142.6 | 145.9 | 155.5 | 202 | 27.4 | 21.2 | 44.8 | 3.7 |  |  | 306.4 | 357.2 | 489.3 | 287.5 | 327.4 | 444.5 | 439.3
2629.3 | 929.3 | 187.3 | 74.92 | 87.5772 | 133.2 | 142.9 | 146 | 155.5 | 201.3 | 27.5 | 21.2 | 44.8 | 3.3 |  |  | 306.7 | 355.3 | 487.7 | 288.1 | 329.3 | 442.7 | 436.8
2630.3 | 930.3 | 187.9 | 75.16 | 87.8577 | 133.4 | 143.3 | 145.9 | 155.7 | 200.1 | 27.5 | 21.2 | 44.8 | 3 |  |  | 307.2 | 359.5 | 487.4 | 288.8 | 331.1 | 438.7 | 435.7
2631.3 | 931.3 | 186.6 | 74.64 | 87.2499 | 133.7 | 143.9 | 145.9 | 155.6 | 200.7 | 27.5 | 21.2 | 44.8 | 2.6 |  |  | 307.8 | 358.6 | 486.4 | 289.5 | 329.6 | 436.6 | 437.9
2632.3 | 932.3 | 189 | 75.6 | 88.372 | 133.9 | 144.6 | 145.9 | 155.4 | 200.7 | 27.5 | 21.2 | 44.7 | 2.9 |  |  | 308.3 | 353.6 | 488 | 290.2 | 324.2 | 431.8 | 441
2633.3 | 933.3 | 189.5 | 75.8 | 88.6058 | 134.4 | 144.8 | 146 | 155.2 | 198.6 | 27.6 | 21.2 | 44.7 | 2.2 |  |  | 308.7 | 344.4 | 485.6 | 290.9 | 317.6 | 429.1 | 443
2634.3 | 934.3 | 188.5 | 75.4 | 88.1383 | 134.6 | 144.8 | 145.3 | 155 | 195.6 | 27.5 | 21.2 | 44.8 | 2 |  |  | 309.1 | 336.8 | 481.6 | 291.5 | 310.9 | 423.7 | 441.4
2635.3 | 935.3 | 187.8 | 75.12 | 87.811 | 134.8 | 144.4 | 145.5 | 154.9 | 192.9 | 27.5 | 21.2 | 44.7 | 2 |  |  | 309.5 | 335.1 | 482.2 | 292 | 311.2 | 426.2 | 441.7
2636.3 | 936.3 | 187.4 | 74.96 | 87.6239 | 134.5 | 144.3 | 145.8 | 155.2 | 193 | 27.5 | 21.2 | 44.7 | 2.3 |  |  | 310 | 332.8 | 481.4 | 292.4 | 311.2 | 423.6 | 440.6
2637.3 | 937.3 | 187.4 | 74.96 | 87.6239 | 134.3 | 144.5 | 146 | 155.7 | 192.7 | 27.5 | 21.2 | 44.7 | 2.8 |  |  | 310.5 | 330.3 | 474.6 | 292.9 | 311.7 | 425.2 | 440.1
2638.3 | 938.3 | 187.8 | 75.12 | 87.811 | 134.6 | 144.6 | 146.1 | 155.8 | 191.7 | 27.5 | 21.2 | 44.7 | 3 |  |  | 310.8 | 335.4 | 473.9 | 293.3 | 317 | 432 | 441.3
2639.3 | 939.3 | 188.6 | 75.44 | 88.185 | 134.8 | 144.3 | 146.3 | 155.6 | 192.2 | 27.5 | 21.2 | 44.7 | 3.3 |  |  | 311.2 | 346.7 | 473.4 | 293.7 | 324.6 | 428.7 | 439
2640.3 | 940.3 | 189.6 | 75.84 | 88.6526 | 135.1 | 143.7 | 146.3 | 155.5 | 192.1 | 27.5 | 21.2 | 44.8 | 3.6 |  |  | 311.7 | 349.6 | 473.7 | 294.1 | 327.7 | 430.2 | 437
2641.3 | 941.3 | 188.5 | 75.4 | 88.1383 | 134.9 | 143.2 | 146.2 | 155.5 | 192.4 | 27.5 | 21.2 | 44.8 | 3.5 |  |  | 312.2 | 352.5 | 476.5 | 294.5 | 332.2 | 434.5 | 441.2
2642.3 | 942.3 | 187.9 | 75.16 | 87.8577 | 135 | 143.5 | 146.2 | 155.7 | 193.5 | 27.5 | 21.2 | 44.9 | 3.6 |  |  | 312.7 | 355.4 | 480.8 | 294.8 | 337 | 436.7 | 446.2
2643.3 | 943.3 | 189 | 75.6 | 88.372 | 135.4 | 143.5 | 146.2 | 155.7 | 193.9 | 27.5 | 21.2 | 44.9 | 3.1 |  |  | 313 | 354.6 | 483.3 | 295.1 | 337.1 | 440.4 | 446.4
2644.3 | 944.3 | 187.6 | 75.04 | 87.7174 | 135.4 | 143.3 | 146.2 | 155.7 | 195.9 | 27.5 | 21.2 | 45 | 2.9 |  |  | 313.3 | 366.3 | 481.4 | 295.5 | 344.2 | 440.3 | 443.1
2645.3 | 945.3 | 186.1 | 74.44 | 87.0161 | 135.9 | 143.3 | 146.4 | 155.5 | 198.8 | 27.6 | 21.2 | 45.1 | 3.1 |  |  | 313.4 | 364.1 | 475.6 | 296 | 341.3 | 441.5 | 440.1
2646.3 | 946.3 | 187.7 | 75.08 | 87.7642 | 135.9 | 143.6 | 146.6 | 155.2 | 197.2 | 27.9 | 21.2 | 45.2 | 2.8 |  |  | 313.5 | 361.6 | 473 | 296.4 | 342 | 449 | 441.7
2647.3 | 947.3 | 186.1 | 74.44 | 87.0161 | 135.9 | 143.7 | 146.8 | 154.7 | 198.5 | 28.1 | 21.2 | 45.3 | 2.7 |  |  | 313.9 | 361.1 | 475.5 | 296.9 | 343 | 457.5 | 451.3
2648.3 | 948.3 | 187.4 | 74.96 | 87.6239 | 136.1 | 143.9 | 146.9 | 154.8 | 199.6 | 28.1 | 21.2 | 45.3 | 2.4 |  |  | 314.5 | 356.1 | 470.7 | 297.3 | 340 | 456 | 448.3
2649.3 | 949.3 | 187.5 | 75 | 87.6707 | 136.7 | 144.1 | 146.7 | 155.2 | 198.3 | 28.2 | 21.2 | 45.3 | 2.5 |  |  | 315 | 355 | 468.7 | 297.8 | 342.4 | 461.2 | 452.4
2650.3 | 950.3 | 187.3 | 74.92 | 87.5772 | 136.9 | 144.4 | 146.8 | 155.5 | 198.3 | 28.2 | 21.2 | 45.3 | 2.1 |  |  | 315.4 | 352.8 | 471.9 | 298.1 | 341.1 | 465.9 | 455.6
2651.3 | 951.3 | 188.1 | 75.24 | 87.9512 | 136.5 | 144.4 | 146.9 | 155.6 | 198.7 | 28.1 | 21.2 | 45.3 | 2.2 |  |  | 315.6 | 353.2 | 476.2 | 298.6 | 341.6 | 469.3 | 454.5
2652.3 | 952.3 | 184.3 | 73.72 | 86.1744 | 136.5 | 144.4 | 146.9 | 155.8 | 198.7 | 28 | 21.2 | 45.2 | 2 |  |  | 315.8 | 354.3 | 479.6 | 299.1 | 343.2 | 471.7 | 455.1
2653.3 | 953.3 | 188.2 | 75.28 | 87.998 | 136.3 | 144.4 | 147.3 | 156 | 198.4 | 27.8 | 21.2 | 45.2 | 2.2 |  |  | 316.2 | 358.9 | 479.3 | 299.5 | 343.4 | 473.1 | 452.4
2654.3 | 954.3 | 188 | 75.2 | 87.9045 | 136.3 | 144.7 | 147.7 | 155.9 | 201.1 | 27.8 | 21.2 | 45.2 | 2 |  |  | 316.6 | 368.2 | 478.1 | 299.9 | 348.7 | 475 | 447.1
2655.3 | 955.3 | 187.6 | 75.04 | 87.7174 | 136.2 | 144.9 | 147.9 | 155.8 | 202.8 | 27.7 | 21.2 | 45.2 | 1.5 |  |  | 317 | 372 | 476.8 | 300.4 | 349.5 | 474.1 | 443.4
2656.3 | 956.3 | 188.7 | 75.48 | 88.2318 | 136.4 | 144.7 | 148 | 155.6 | 204 | 27.7 | 21.2 | 45.1 | 1.4 |  |  | 317.5 | 375.7 | 477.4 | 300.8 | 351.6 | 474 | 444.1
2657.3 | 957.3 | 188.6 | 75.44 | 88.185 | 136.7 | 144.2 | 148.2 | 155.5 | 205.5 | 27.6 | 21.2 | 45 | 1.3 |  |  | 318 | 376.5 | 476.8 | 301.3 | 351.4 | 474.9 | 446.1
2658.3 | 958.3 | 187.8 | 75.12 | 87.811 | 136.9 | 144.3 | 148.1 | 155.5 | 204 | 27.6 | 21.2 | 45 | 1.4 |  |  | 318.2 | 368.8 | 474.3 | 301.8 | 346 | 471.3 | 447.7
2659.3 | 959.3 | 189 | 75.6 | 88.372 | 136.9 | 144.2 | 148 | 155.7 | 200.2 | 27.6 | 21.2 | 45.1 | 1.7 |  |  | 318.5 | 369.5 | 472.9 | 302.2 | 351.3 | 476.2 | 450.5
2660.3 | 960.3 | 188.9 | 75.56 | 88.3253 | 136.9 | 144.2 | 148.3 | 155.9 | 198.4 | 27.6 | 21.2 | 45.2 | 2 |  |  | 318.9 | 366.6 | 473.9 | 302.7 | 353.8 | 476.2 | 453.1
2661.3 | 961.3 | 188.8 | 75.52 | 88.2785 | 136.6 | 144.2 | 148.3 | 156 | 197 | 27.6 | 21.2 | 45.3 | 2 |  |  | 319.4 | 361.5 | 471.3 | 303.3 | 348.7 | 466.8 | 450.1
2662.3 | 962.3 | 188.1 | 75.24 | 87.9512 | 136.3 | 143.9 | 148.1 | 156.4 | 195.7 | 27.6 | 21.2 | 45.4 | 2.4 |  |  | 319.8 | 353.1 | 465 | 303.7 | 341.2 | 458.3 | 448.3
2663.3 | 963.3 | 189.4 | 75.76 | 88.5591 | 136 | 143.5 | 148.2 | 156.9 | 193 | 27.8 | 21.2 | 45.5 | 2.8 |  |  | 320 | 344.2 | 454.9 | 304.2 | 333 | 446.8 | 445.6
2664.3 | 964.3 | 188.9 | 75.56 | 88.3253 | 135.7 | 142.9 | 148.1 | 157.2 | 189.1 | 27.8 | 21.2 | 45.4 | 2.2 |  |  | 320.4 | 335.9 | 449 | 304.7 | 325.3 | 437.8 | 445.1
2665.3 | 965.3 | 186.7 | 74.68 | 87.2966 | 135.1 | 142.4 | 148.1 | 157.3 | 186.2 | 27.9 | 21.2 | 45.4 | 2.5 |  |  | 320.7 | 330.2 | 445.9 | 305 | 318.7 | 433.3 | 445.5
2666.3 | 966.3 | 188.5 | 75.4 | 88.1383 | 134.3 | 142.1 | 147.8 | 157.1 | 185.8 | 27.9 | 21.2 | 45.5 | 2.5 |  |  | 321 | 327.4 | 450.2 | 305.2 | 317 | 434.5 | 451.7
2667.3 | 967.3 | 185.4 | 74.16 | 86.6888 | 133.8 | 142.1 | 147.4 | 157.1 | 188 | 28 | 21.2 | 45.5 | 2.2 |  |  | 321.2 | 323 | 455.4 | 305.5 | 312.4 | 432.2 | 451.8
2668.3 | 968.3 | 187.9 | 75.16 | 87.8577 | 133.6 | 142.3 | 146.8 | 156.9 | 189.6 | 28 | 21.2 | 45.5 | 2.4 |  |  | 321.3 | 326.7 | 463.8 | 305.8 | 315.4 | 434 | 453.2
2669.3 | 969.3 | 188.6 | 75.44 | 88.185 | 133.3 | 143.2 | 146.4 | 156.6 | 190.8 | 27.9 | 21.2 | 45.5 | 2.7 |  |  | 321.5 | 331.1 | 467.8 | 305.9 | 317.1 | 436.2 | 451.2
2670.3 | 970.3 | 187.6 | 75.04 | 87.7174 | 133.4 | 143.7 | 146.2 | 156.5 | 193.2 | 28 | 21.2 | 45.5 | 2.8 |  |  | 321.7 | 335.7 | 466.9 | 305.8 | 324.2 | 445.1 | 448.9
2671.3 | 971.3 | 186.7 | 74.68 | 87.2966 | 134 | 143.2 | 146 | 156.8 | 193.7 | 28.2 | 21.2 | 45.6 | 2.8 |  |  | 322.1 | 339.2 | 465.2 | 305.8 | 329.6 | 450 | 448.1
2672.3 | 972.3 | 187.3 | 74.92 | 87.5772 | 134.5 | 142.5 | 145.8 | 156.9 | 195.3 | 28.2 | 21.2 | 45.8 | 3 |  |  | 322.3 | 345.7 | 466.8 | 305.9 | 336.1 | 458.9 | 450.6
2673.3 | 973.3 | 188.7 | 75.48 | 88.2318 | 135 | 141.9 | 145.7 | 156.9 | 196.4 | 28.3 | 21.2 | 46 | 3.1 |  |  | 322.4 | 352.4 | 461.4 | 306 | 341.9 | 464.2 | 447.8
2674.3 | 974.3 | 188.4 | 75.36 | 88.0915 | 135.6 | 141.7 | 145.9 | 157 | 198.2 | 28.3 | 21.2 | 46.1 | 3.2 |  |  | 322.5 | 355.1 | 458.2 | 306.2 | 348.5 | 466.8 | 444.3
2675.3 | 975.3 | 188.5 | 75.4 | 88.1383 | 135.8 | 141.8 | 146.3 | 156.8 | 198.8 | 28.2 | 21.2 | 46 | 2.8 |  |  | 322.7 | 358.7 | 454.7 | 306.4 | 352.6 | 463.2 | 441.9
2676.3 | 976.3 | 189 | 75.6 | 88.372 | 135.9 | 142.1 | 146.7 | 156.6 | 200.7 | 28.2 | 21.2 | 46 | 2.8 |  |  | 323.1 | 362.2 | 448.9 | 306.7 | 360.3 | 462.2 | 438.6
2677.3 | 977.3 | 187.7 | 75.08 | 87.7642 | 136 | 142.2 | 146.8 | 156.4 | 203.7 | 28.2 | 21.2 | 46 | 2.8 |  |  | 323.4 | 364.6 | 443 | 307.1 | 369.3 | 462.8 | 436.8
2678.3 | 978.3 | 189.1 | 75.64 | 88.4188 | 136.1 | 142.5 | 146.7 | 156.4 | 204.6 | 28.1 | 21.2 | 45.9 | 3.4 |  |  | 323.5 | 357.4 | 434 | 307.5 | 368.6 | 461.1 | 434.7
2679.3 | 979.3 | 187.1 | 74.84 | 87.4836 | 136.3 | 143 | 146.8 | 156.6 | 202.9 | 28.1 | 21.2 | 45.8 | 3 |  |  | 323.6 | 353.3 | 427.9 | 308 | 369.6 | 461.2 | 431.6
2680.3 | 980.3 | 187 | 74.8 | 87.4369 | 136.7 | 142.9 | 147.4 | 156.6 | 200.6 | 28.1 | 21.2 | 45.8 | 3.2 |  |  | 323.9 | 352.8 | 423.3 | 308.4 | 373.8 | 465.4 | 429.7
2681.3 | 981.3 | 183.8 | 73.52 | 85.9406 | 136.9 | 142.8 | 147.7 | 156.6 | 201.3 | 28.2 | 21.2 | 45.9 | 3.2 |  |  | 324.2 | 355.6 | 421 | 308.9 | 379.6 | 476.6 | 432.9
2682.3 | 982.3 | 187.9 | 75.16 | 87.8577 | 136.9 | 142.9 | 147.8 | 156.7 | 202.6 | 28.2 | 21.2 | 45.9 | 2.4 |  |  | 324.5 | 359.9 | 422.1 | 309.4 | 381 | 476.5 | 436.5
2683.3 | 983.3 | 188.1 | 75.24 | 87.9512 | 136.9 | 142.8 | 147.6 | 156.7 | 200.8 | 28.2 | 21.2 | 45.9 | 2.2 |  |  | 324.4 | 359.7 | 426.2 | 310 | 380.5 | 482.9 | 440
2684.3 | 984.3 | 186 | 74.4 | 86.9693 | 137.1 | 143.4 | 147.6 | 156.3 | 200.7 | 28.2 | 21.2 | 45.8 | 1.9 |  |  | 324.7 | 367.5 | 432.5 | 310.5 | 389 | 491.8 | 445.1
2685.3 | 985.3 | 187.7 | 75.08 | 87.7642 | 137.4 | 144.1 | 148 | 156.2 | 203.2 | 28.2 | 21.2 | 45.7 | 2.1 |  |  | 324.9 | 363 | 434.2 | 311.1 | 385.7 | 488.1 | 447.2
2686.3 | 986.3 | 188.9 | 75.56 | 88.3253 | 137.7 | 144.3 | 148.4 | 156.2 | 202 | 28.3 | 21.2 | 45.6 | 1.8 |  |  | 325.2 | 357.5 | 439.2 | 311.7 | 379.8 | 490.2 | 453
2687.3 | 987.3 | 187 | 74.8 | 87.4369 | 137.7 | 144.7 | 148.6 | 156.4 | 201 | 28.4 | 21.2 | 45.6 | 1.6 |  |  | 325.4 | 352.3 | 440.3 | 312.2 | 371.4 | 485.3 | 455.1
2688.3 | 988.3 | 186.7 | 74.68 | 87.2966 | 137.7 | 145.3 | 148.8 | 156.2 | 199 | 28.4 | 21.2 | 45.6 | 2.1 |  |  | 325.2 | 345.1 | 440.7 | 312.8 | 363.5 | 480.7 | 452.3
2689.3 | 989.3 | 187.7 | 75.08 | 87.7642 | 137.3 | 145.3 | 149.1 | 156 | 196.9 | 28.3 | 21.2 | 45.6 | 2 |  |  | 325.5 | 343.6 | 441.5 | 313.4 | 363.1 | 483.5 | 451.7
2690.3 | 990.3 | 188.8 | 75.52 | 88.2785 | 137.1 | 145.2 | 148.8 | 156.1 | 197.9 | 28.3 | 21.2 | 45.6 | 2.1 |  |  | 325.6 | 344.6 | 448.4 | 314 | 361.5 | 483.5 | 453.1
2691.3 | 991.3 | 188.6 | 75.44 | 88.185 | 137.3 | 144.9 | 148.5 | 156.1 | 200.5 | 28.3 | 21.2 | 45.6 | 2 |  |  | 325.8 | 345.3 | 452.9 | 314.7 | 358.2 | 482.9 | 453.1
2692.3 | 992.3 | 187.5 | 75 | 87.6707 | 137.6 | 144.9 | 148.4 | 156.1 | 201.6 | 28.3 | 21.2 | 45.7 | 2.1 |  |  | 325.7 | 341.9 | 459.1 | 315.2 | 352.7 | 483.3 | 458.2
2693.3 | 993.3 | 188.1 | 75.24 | 87.9512 | 137.8 | 145 | 148.7 | 155.8 | 201.5 | 28.2 | 21.2 | 45.8 | 2 |  |  | 325.9 | 339.1 | 461.9 | 315.7 | 349.4 | 485.2 | 461.7
2694.3 | 994.3 | 187.7 | 75.08 | 87.7642 | 137.9 | 145.4 | 148.7 | 155 | 200.6 | 28.2 | 21.2 | 45.9 | 1.8 |  |  | 326 | 338.9 | 461.8 | 316.2 | 349.4 | 489.4 | 462.9
2695.3 | 995.3 | 188.1 | 75.24 | 87.9512 | 137.9 | 145.5 | 148.5 | 154.9 | 202.1 | 28.3 | 21.2 | 46 | 1.8 |  |  | 326.1 | 336.8 | 457.6 | 316.7 | 346.5 | 489.5 | 463.1
2696.3 | 996.3 | 186.6 | 74.64 | 87.2499 | 137.4 | 145.5 | 148.4 | 155.3 | 204.4 | 28.4 | 21.2 | 46.1 | 2 |  |  | 326.3 | 340.7 | 460.4 | 316.9 | 352.1 | 495.1 | 463.9
2697.3 | 997.3 | 187.9 | 75.16 | 87.8577 | 137.2 | 145.1 | 148.3 | 155.6 | 207.5 | 28.7 | 21.2 | 46.3 | 1.6 |  |  | 326.6 | 346.6 | 467.3 | 317.2 | 363.1 | 503.3 | 467.3
2698.3 | 998.3 | 185.1 | 74.04 | 86.5485 | 137.6 | 145 | 148.6 | 155.9 | 208.7 | 28.8 | 21.2 | 46.4 | 1.8 |  |  | 326.8 | 348.8 | 470.1 | 317.6 | 362.5 | 499.7 | 463.9
2699.3 | 999.3 | 187.4 | 74.96 | 87.6239 | 137.6 | 145.2 | 148.8 | 155.8 | 209.2 | 28.8 | 21.2 | 46.4 | 1.8 |  |  | 326.9 | 348.4 | 471 | 318 | 358.7 | 493.9 | 458.3
2700.3 | 1000.3 | 187.3 | 74.92 | 87.5772 | 137.7 | 145.3 | 149.1 | 155.7 | 207.3 | 28.8 | 21.2 | 46.3 | 1.6 |  |  | 327 | 352.3 | 465.6 | 318.4 | 359.1 | 492.7 | 451.8
2701.3 | 1001.3 | 184.5 | 73.8 | 86.2679 | 137.8 | 145.4 | 149.2 | 155.7 | 206.9 | 28.8 | 21.2 | 46.3 | 1.8 |  |  | 327.5 | 357.5 | 461.5 | 318.7 | 366.2 | 492.8 | 449.8
2702.3 | 1002.3 | 187.5 | 75 | 87.6707 | 138.2 | 145.1 | 149.2 | 155.8 | 207.4 | 28.8 | 21.2 | 46.3 | 2 |  |  | 328.1 | 366.4 | 459 | 319.2 | 377.6 | 494.9 | 450.5
2703.3 | 1003.3 | 187.8 | 75.12 | 87.811 | 138.4 | 145.1 | 149.2 | 155.9 | 207.9 | 28.8 | 21.2 | 46.4 | 2.2 |  |  | 328.2 | 365.2 | 451.7 | 319.7 | 379.5 | 490.4 | 446.2
2704.3 | 1004.3 | 188 | 75.2 | 87.9045 | 138.6 | 144.7 | 148.8 | 155.9 | 205.4 | 28.8 | 21.2 | 46.4 | 2.3 |  |  | 328.4 | 360.5 | 444.3 | 320.3 | 380.2 | 489.7 | 440.9
2705.3 | 1005.3 | 187.6 | 75.04 | 87.7174 | 138.6 | 144.2 | 148.8 | 155.9 | 202.4 | 28.8 | 21.2 | 46.4 | 2.3 |  |  | 328.5 | 360.2 | 444.7 | 320.9 | 380.1 | 493.6 | 447.2
2706.3 | 1006.3 | 187.9 | 75.16 | 87.8577 | 138.7 | 143.9 | 148.8 | 155.9 | 201.9 | 28.8 | 21.2 | 46.5 | 2.3 |  |  | 328.9 | 360.1 | 446.2 | 321.2 | 379.4 | 497.4 | 449.1
2707.3 | 1007.3 | 186.7 | 74.68 | 87.2966 | 138.6 | 144.1 | 149.1 | 155.9 | 201.9 | 28.8 | 21.2 | 46.5 | 2.4 |  |  | 328.9 | 357.1 | 450.3 | 321.6 | 375.6 | 500.2 | 452.1
2708.3 | 1008.3 | 187.4 | 74.96 | 87.6239 | 138.8 | 144.6 | 149 | 155.9 | 203.5 | 29.1 | 21.2 | 46.5 | 2.6 |  |  | 329.4 | 354.8 | 450.5 | 322 | 373.5 | 504.7 | 454.2
2709.3 | 1009.3 | 186.2 | 74.48 | 87.0628 | 139 | 144.7 | 149 | 155.7 | 203.4 | 29.2 | 21.2 | 46.5 | 2.4 |  |  | 329.7 | 350.5 | 449.6 | 322.5 | 369.8 | 502.4 | 453.2
2710.3 | 1010.3 | 189.5 | 75.8 | 88.6058 | 139.1 | 144.6 | 148.7 | 155.6 | 203.7 | 29.3 | 21.2 | 46.5 | 2.2 |  |  | 329.8 | 359 | 444.6 | 323.1 | 380.3 | 503.7 | 451
2711.3 | 1011.3 | 192.8 | 77.12 | 90.1488 | 139 | 144.7 | 148.8 | 155.5 | 206.3 | 29.3 | 21.2 | 46.5 | 2.1 |  |  | 330.1 | 371.9 | 440.7 | 323.7 | 387.2 | 497 | 445.2
2712.3 | 1012.3 | 194 | 77.6 | 90.7099 | 139.1 | 144.2 | 149.1 | 155.8 | 207.2 | 29.3 | 21.2 | 46.5 | 1.7 |  |  | 330.4 | 380.3 | 436.2 | 324.2 | 387.4 | 490.6 | 439.6
2713.3 | 1013.3 | 191.5 | 76.6 | 89.541 | 139.2 | 144.4 | 149.5 | 155.9 | 208.9 | 29.3 | 21.2 | 46.5 | 1.9 |  |  | 330.6 | 388.6 | 440.7 | 324.8 | 390.8 | 490.7 | 439.8
2714.3 | 1014.3 | 190.5 | 76.2 | 89.0734 | 139.5 | 144.8 | 150.2 | 156 | 211.6 | 29.3 | 21.2 | 46.5 | 2 |  |  | 331 | 395.9 | 447.3 | 325.2 | 396.3 | 495.8 | 445.1
2715.3 | 1015.3 | 190.4 | 76.16 | 89.0267 | 139.9 | 145.2 | 150.2 | 156.2 | 211.8 | 29.3 | 21.2 | 46.5 | 2.2 |  |  | 331.3 | 400.8 | 457.3 | 325.6 | 397.3 | 499.4 | 452.2
2716.3 | 1016.3 | 188.6 | 75.44 | 88.185 | 140.6 | 145.8 | 150.3 | 156.1 | 210.5 | 29.2 | 21.2 | 46.6 | 2.5 |  |  | 331.8 | 399.4 | 463.1 | 326.2 | 393.6 | 496.9 | 452.7
2717.3 | 1017.3 | 188.1 | 75.24 | 87.9512 | 141.1 | 146 | 150.6 | 156.4 | 211.7 | 29.1 | 21.2 | 46.6 | 2.8 |  |  | 331.8 | 402.9 | 472.3 | 326.9 | 391.6 | 495.4 | 457.5
2718.3 | 1018.3 | 187.8 | 75.12 | 87.811 | 141.9 | 146.3 | 151.3 | 156.7 | 212.7 | 29 | 21.2 | 46.6 | 2.6 |  |  | 332 | 394.4 | 474.6 | 327.5 | 383 | 486.9 | 458.6
2719.3 | 1019.3 | 187.2 | 74.88 | 87.5304 | 142.4 | 146.3 | 151.7 | 156.8 | 211.4 | 28.9 | 21.2 | 46.6 | 2.6 |  |  | 332.6 | 384.6 | 470.4 | 328.1 | 374.2 | 477.9 | 458
2720.3 | 1020.3 | 187.3 | 74.92 | 87.5772 | 142.9 | 146.2 | 151.9 | 156.8 | 210 | 29 | 21.2 | 46.7 | 3 |  |  | 333.1 | 375.6 | 469.5 | 328.6 | 367.1 | 472.6 | 460.1
2721.3 | 1021.3 | 189.4 | 75.76 | 88.5591 | 143.2 | 146.4 | 152.1 | 157.2 | 207.1 | 29 | 21.2 | 46.6 | 3 |  |  | 333.6 | 368 | 467.1 | 329.2 | 359.7 | 464.7 | 458
2722.3 | 1022.3 | 189.7 | 75.88 | 88.6993 | 143.5 | 146.4 | 152 | 157.6 | 204.8 | 29 | 21.2 | 46.5 | 2.9 |  |  | 334 | 363.4 | 468.1 | 329.8 | 355.4 | 461.4 | 456.7
2723.3 | 1023.3 | 189.3 | 75.72 | 88.5123 | 143.7 | 146.1 | 151.7 | 157.8 | 203.4 | 29.1 | 21.2 | 46.5 | 2.8 |  |  | 334.3 | 355.5 | 467.2 | 330.2 | 348.2 | 456.6 | 456.7
2724.3 | 1024.3 | 188 | 75.2 | 87.9045 | 143.8 | 146 | 151.5 | 157.9 | 202.8 | 29 | 21.2 | 46.6 | 2.6 |  |  | 334.7 | 348.8 | 463 | 330.5 | 341.6 | 451.9 | 456.9
2725.3 | 1025.3 | 185.2 | 74.08 | 86.5953 | 143.9 | 146.2 | 151.2 | 158.2 | 201.5 | 29 | 21.2 | 46.7 | 2.6 |  |  | 335.3 | 343.7 | 460.6 | 330.8 | 337.2 | 454.4 | 459.8
2726.3 | 1026.3 | 186.5 | 74.6 | 87.2031 | 144.1 | 146.1 | 150.8 | 158.3 | 200.1 | 28.8 | 21.2 | 46.8 | 2.8 |  |  | 335.9 | 339.8 | 462.9 | 331.1 | 332 | 455.1 | 462.5
2727.3 | 1027.3 | 188.2 | 75.28 | 87.998 | 144 | 146.1 | 150.9 | 158.3 | 197.2 | 28.7 | 21.2 | 46.9 | 2.8 |  |  | 336.3 | 333.5 | 464.5 | 331.3 | 326.3 | 450 | 461.7
2728.3 | 1028.3 | 188.4 | 75.36 | 88.0915 | 143.7 | 146.8 | 150.9 | 158.1 | 195.4 | 28.6 | 21.2 | 46.8 | 2.2 |  |  | 336.7 | 330.7 | 466.5 | 331.3 | 322.6 | 449.9 | 460.1
2729.3 | 1029.3 | 182 | 72.8 | 85.099 | 143.3 | 147.1 | 150.7 | 157.9 | 195 | 28.5 | 21.2 | 46.9 | 2.4 |  |  | 336.8 | 330.8 | 470.8 | 331.3 | 321.7 | 449.4 | 459.3
2730.3 | 1030.3 | 187.2 | 74.88 | 87.5304 | 142.9 | 147.1 | 150.1 | 157.8 | 196.7 | 28.5 | 21.2 | 47 | 2.2 |  |  | 337 | 330.5 | 467.6 | 331.2 | 319.6 | 447.3 | 457.4
2731.3 | 1031.3 | 187.7 | 75.08 | 87.7642 | 142.8 | 147 | 148.9 | 157.4 | 197.3 | 28.5 | 21.2 | 47 | 2.4 |  |  | 337.2 | 332.1 | 465.5 | 331.1 | 320.6 | 447 | 455.4
2732.3 | 1032.3 | 187.7 | 75.08 | 87.7642 | 142.3 | 147 | 148.5 | 156.9 | 198 | 28.4 | 21.2 | 47.2 | 2.7 |  |  | 337.2 | 329 | 467.9 | 330.9 | 316.2 | 444.2 | 452.8
2733.3 | 1033.3 | 187.6 | 75.04 | 87.7174 | 142.1 | 146.8 | 148.6 | 156.6 | 198.3 | 28.4 | 21.2 | 47.3 | 2.8 |  |  | 337.6 | 328.4 | 476.6 | 330.8 | 315.1 | 445.8 | 457.5
2734.3 | 1034.3 | 185.3 | 74.12 | 86.642 | 142.1 | 146.5 | 148 | 156.4 | 199.4 | 28.5 | 21.2 | 47.4 | 2.7 |  |  | 337.9 | 333.5 | 483.4 | 330.8 | 320.7 | 451.4 | 467
2735.3 | 1035.3 | 187.6 | 75.04 | 87.7174 | 142.4 | 146.3 | 146.9 | 156.5 | 199.1 | 28.6 | 21.2 | 47.4 | 2.9 |  |  | 338.1 | 335.5 | 484.5 | 330.7 | 320.9 | 452.6 | 466.7
2736.3 | 1036.3 | 188.2 | 75.28 | 87.998 | 142.3 | 145.9 | 146.8 | 156.5 | 198.3 | 28.6 | 21.2 | 47.4 | 2.8 |  |  | 338.4 | 342.1 | 486.5 | 330.6 | 327.9 | 455.8 | 466.5
2737.3 | 1037.3 | 188.2 | 75.28 | 87.998 | 142 | 146 | 147.1 | 156.4 | 201.2 | 28.6 | 21.2 | 47.5 | 3 |  |  | 338.4 | 342.9 | 480.1 | 330.7 | 326.4 | 450 | 459.2
2738.3 | 1038.3 | 186.7 | 74.68 | 87.2966 | 141.6 | 146 | 147.3 | 156.6 | 203.7 | 28.6 | 21.2 | 47.5 | 2.4 |  |  | 338.5 | 343.6 | 478.8 | 330.7 | 325.3 | 447 | 453.9
2739.3 | 1039.3 | 189 | 75.6 | 88.372 | 141.4 | 146.2 | 147.4 | 156.9 | 204.5 | 28.6 | 21.2 | 47.4 | 2.6 |  |  | 339.1 | 342.2 | 482.2 | 330.8 | 323.3 | 446 | 454.9
2740.3 | 1040.3 | 188.6 | 75.44 | 88.185 | 141.2 | 146.2 | 147.2 | 157.2 | 204.6 | 28.5 | 21.2 | 47.3 | 2.7 |  |  | 339.2 | 344 | 482.9 | 330.9 | 325.3 | 447.5 | 458.8
2741.3 | 1041.3 | 188.9 | 75.56 | 88.3253 | 141.2 | 146.1 | 147.2 | 157.4 | 204.5 | 28.5 | 21.2 | 47.2 | 3.1 |  |  | 339.7 | 344.9 | 486.8 | 330.8 | 325.2 | 447 | 459.4
2742.3 | 1042.3 | 188.7 | 75.48 | 88.2318 | 141.2 | 146.2 | 147.5 | 157.5 | 204.8 | 28.4 | 21.2 | 47.1 | 2.9 |  |  | 340.3 | 346.8 | 487.6 | 330.9 | 325 | 443.3 | 457.5
2743.3 | 1043.3 | 187.8 | 75.12 | 87.811 | 141.1 | 146.2 | 147.8 | 157.5 | 205.1 | 28.4 | 21.2 | 47 | 2.7 |  |  | 340.2 | 354.1 | 486.4 | 330.9 | 333.6 | 446.8 | 454.8
2744.3 | 1044.3 | 189.3 | 75.72 | 88.5123 | 140.9 | 146.2 | 148 | 157.5 | 206.8 | 28.4 | 21.2 | 47 | 3 |  |  | 340.3 | 361.1 | 481.8 | 330.9 | 337.6 | 449.4 | 453.3
2745.3 | 1045.3 | 188.1 | 75.24 | 87.9512 | 141.2 | 146.2 | 147.9 | 157.8 | 206.4 | 28.4 | 21.2 | 47 | 3.1 |  |  | 340.4 | 369.1 | 477.1 | 331 | 344.2 | 452.4 | 450.5
2746.3 | 1046.3 | 187.8 | 75.12 | 87.811 | 141.5 | 146.3 | 147.9 | 158 | 207.5 | 28.5 | 21.2 | 47 | 3.2 |  |  | 340.7 | 379.8 | 481.3 | 331.1 | 350.8 | 453.5 | 451.1
2747.3 | 1047.3 | 188.2 | 75.28 | 87.998 | 141.7 | 146.3 | 147.7 | 157.8 | 208.8 | 28.7 | 21.2 | 47 | 3.1 |  |  | 341 | 382 | 479.9 | 331.2 | 351.4 | 449 | 451.7
2748.3 | 1048.3 | 188.7 | 75.48 | 88.2318 | 141.7 | 146.6 | 148 | 157.7 | 209.4 | 28.9 | 21.2 | 47 | 2.6 |  |  | 341.1 | 383.4 | 472.8 | 331.3 | 350.3 | 442.4 | 446.2
2749.3 | 1049.3 | 188.5 | 75.4 | 88.1383 | 141.8 | 146.9 | 148.4 | 157.7 | 209.1 | 29.1 | 21.2 | 47 | 2.1 |  |  | 341.5 | 379.2 | 465.7 | 331.6 | 343.8 | 432.3 | 441.4
2750.3 | 1050.3 | 187.1 | 74.84 | 87.4836 | 142.1 | 146.9 | 148.5 | 158.1 | 208.6 | 29.2 | 21.2 | 47 | 1.7 |  |  | 342.1 | 378.1 | 469 | 331.8 | 340.6 | 427.5 | 443.4
2751.3 | 1051.3 | 187.1 | 74.84 | 87.4836 | 142.1 | 146.9 | 148.6 | 158.5 | 208.3 | 29.3 | 21.2 | 47 | 1.6 |  |  | 342.6 | 376.4 | 471.4 | 331.9 | 340.9 | 436.7 | 453.3
2752.3 | 1052.3 | 186.2 | 74.48 | 87.0628 | 141.8 | 147.2 | 148.6 | 158.4 | 205.9 | 29.4 | 21.2 | 46.9 | 1.5 |  |  | 342.9 | 372 | 470.9 | 332.1 | 336.1 | 436.9 | 460.6
2753.3 | 1053.3 | 186 | 74.4 | 86.9693 | 141.6 | 147.3 | 148.7 | 157.8 | 203.7 | 29.5 | 21.2 | 46.9 | 1.4 |  |  | 343.1 | 363 | 464.6 | 332.1 | 330.5 | 436.4 | 459.8
2754.3 | 1054.3 | 186.2 | 74.48 | 87.0628 | 141.2 | 147.6 | 148.7 | 157.3 | 201.7 | 29.5 | 21.2 | 46.9 | 1.9 |  |  | 343.7 | 355.9 | 458.9 | 332.3 | 326.4 | 440 | 456.9
2755.3 | 1055.3 | 184.5 | 73.8 | 86.2679 | 140.9 | 147.7 | 149 | 157.4 | 199.3 | 29.4 | 21.2 | 47 | 2.4 |  |  | 344 | 354.8 | 458.9 | 332.3 | 328.9 | 445.3 | 461.1
2756.3 | 1056.3 | 186.9 | 74.76 | 87.3901 | 140.6 | 147.6 | 149 | 157.6 | 198.4 | 29.2 | 21.2 | 47.2 | 2.6 |  |  | 344.3 | 358.4 | 461.4 | 332.4 | 336.6 | 459.4 | 467.1
2757.3 | 1057.3 | 187 | 74.8 | 87.4369 | 139.9 | 147.8 | 148.3 | 157.6 | 202.1 | 29.2 | 21.2 | 47.4 | 2.6 |  |  | 344.9 | 351.7 | 463.9 | 332.5 | 333.4 | 462.1 | 468.2
2758.3 | 1058.3 | 187.6 | 75.04 | 87.7174 | 139.3 | 147.9 | 147.9 | 157.6 | 201.5 | 29.1 | 21.2 | 47.4 | 2 |  |  | 345.3 | 346 | 463 | 332.5 | 330.9 | 461.3 | 465.9
2759.3 | 1059.3 | 184.7 | 73.88 | 86.3615 | 139 | 147.8 | 148 | 157.6 | 200.5 | 29.2 | 21.1 | 47.4 | 1.6 |  |  | 345.4 | 340.9 | 458.8 | 332.6 | 327.2 | 457.9 | 462.5
2760.3 | 1060.3 | 187 | 74.8 | 87.4369 | 138.8 | 147.5 | 148.4 | 158.4 | 198.3 | 29.2 | 21.1 | 47.4 | 1.5 |  |  | 345.4 | 337.2 | 455.1 | 332.7 | 323.7 | 456.4 | 459.8
2761.3 | 1061.3 | 188.3 | 75.32 | 88.0447 | 138.7 | 147.2 | 148.3 | 159 | 196.8 | 29.4 | 21.2 | 47.4 | 1.5 |  |  | 345.5 | 334 | 452.2 | 332.8 | 324.3 | 460.5 | 460.8
2762.3 | 1062.3 | 186.6 | 74.64 | 87.2499 | 138.7 | 147.2 | 148.3 | 159.3 | 198.7 | 29.5 | 21.2 | 47.5 | 1.5 |  |  | 345.7 | 338.1 | 453.5 | 332.9 | 332.7 | 472.1 | 468.5
2763.3 | 1063.3 | 187.8 | 75.12 | 87.811 | 138.6 | 147.2 | 148.2 | 159.5 | 202.9 | 29.6 | 21.2 | 47.4 | 1.8 |  |  | 345.7 | 340.1 | 461.1 | 333 | 335.3 | 474.6 | 477
2764.3 | 1064.3 | 186 | 74.4 | 86.9693 | 138.7 | 147.2 | 147.9 | 159.7 | 204.4 | 29.6 | 21.1 | 47.5 | 2 |  |  | 345.9 | 340.1 | 461.7 | 333.1 | 335.7 | 477.1 | 473.3
2765.3 | 1065.3 | 188.2 | 75.28 | 87.998 | 138.7 | 146.9 | 147.8 | 160.1 | 202.7 | 29.6 | 21.1 | 47.5 | 1.8 |  |  | 345.9 | 338.4 | 463.6 | 333 | 335.9 | 478.7 | 473.7
2766.3 | 1066.3 | 189.6 | 75.84 | 88.6526 | 138.6 | 146.8 | 147.8 | 160.4 | 203 | 29.6 | 21.1 | 47.5 | 1.8 |  |  | 345.8 | 335.8 | 467.6 | 333.2 | 332.6 | 477.3 | 476.3
2767.3 | 1067.3 | 189.6 | 75.84 | 88.6526 | 138.7 | 146.8 | 147.9 | 160.5 | 202.1 | 29.8 | 21.1 | 47.6 | 2 |  |  | 345.8 | 334.2 | 469.6 | 333.3 | 330.1 | 468.2 | 473.1
2768.3 | 1068.3 | 188.6 | 75.44 | 88.185 | 139 | 147.1 | 147.9 | 160.3 | 200.9 | 30 | 21.1 | 47.7 | 1.8 |  |  | 346 | 330.9 | 472.2 | 333.5 | 325.8 | 467.2 | 473
2769.3 | 1069.3 | 187.9 | 75.16 | 87.8577 | 139.2 | 147.4 | 147.9 | 159.9 | 199 | 30.2 | 21.1 | 47.8 | 1.6 |  |  | 346 | 328.1 | 472.6 | 333.8 | 322 | 463.7 | 471
2770.3 | 1070.3 | 187.4 | 74.96 | 87.6239 | 139.1 | 147.3 | 147.8 | 159.9 | 198.4 | 30.2 | 21.1 | 47.9 | 1.5 |  |  | 346.2 | 328.6 | 470.8 | 333.9 | 323 | 466 | 471.8
2771.3 | 1071.3 | 186.8 | 74.72 | 87.3434 | 139 | 147.1 | 148.2 | 159.6 | 198.7 | 30.2 | 21.1 | 47.9 | 1.2 |  |  | 346.4 | 327.7 | 469 | 334 | 323.6 | 463.6 | 471.1
2772.3 | 1072.3 | 186 | 74.4 | 86.9693 | 139 | 147.1 | 148.5 | 159.4 | 199.3 | 30.2 | 21.1 | 47.9 | 1.3 |  |  | 346.2 | 322.9 | 471.8 | 334.1 | 318.9 | 459 | 471.6
2773.3 | 1073.3 | 187.6 | 75.04 | 87.7174 | 138.8 | 147.1 | 148.8 | 158.7 | 199 | 30.2 | 21.1 | 48 | 1.6 |  |  | 346.4 | 319.8 | 473.1 | 334.1 | 314.9 | 455.8 | 471.3
2774.3 | 1074.3 | 190.2 | 76.08 | 88.9331 | 138.6 | 147.1 | 148.8 | 158.1 | 198.2 | 30.1 | 21.1 | 48 | 1.6 |  |  | 346.4 | 315.2 | 472.4 | 334.3 | 310.5 | 449.6 | 471.3
2775.3 | 1075.3 | 188.7 | 75.48 | 88.2318 | 138.9 | 146.7 | 148.9 | 158.1 | 196.9 | 30 | 21.1 | 48 | 1.5 |  |  | 346.4 | 313.7 | 469.5 | 334.3 | 307.3 | 445.4 | 469.7
2776.3 | 1076.3 | 188.8 | 75.52 | 88.2785 | 138.9 | 146.5 | 148.7 | 158.4 | 195.4 | 30 | 21.1 | 48 | 1.3 |  |  | 346.5 | 310.9 | 470 | 334.3 | 303.9 | 444.9 | 470.3
2777.3 | 1077.3 | 187.9 | 75.16 | 87.8577 | 138.9 | 146.6 | 148.5 | 158.5 | 195 | 30 | 21.1 | 48 | 1.5 |  |  | 346.5 | 307.3 | 470.1 | 334.4 | 301.6 | 444.2 | 470.9
2778.3 | 1078.3 | 186.6 | 74.64 | 87.2499 | 138.8 | 146.5 | 148.6 | 158.9 | 194.5 | 30 | 21.1 | 48.1 | 1.8 |  |  | 346.7 | 306.3 | 468.4 | 334.4 | 301.2 | 445.6 | 472.4
2779.3 | 1079.3 | 187.2 | 74.88 | 87.5304 | 138.5 | 147 | 148.7 | 159.1 | 194.5 | 30 | 21.1 | 48.3 | 2.3 |  |  | 347 | 305.8 | 470.2 | 334.3 | 301.4 | 451.4 | 478.5
2780.3 | 1080.3 | 186.6 | 74.64 | 87.2499 | 138.4 | 147.6 | 149 | 159.3 | 194.4 | 30.1 | 21.1 | 48.3 | 2 |  |  | 347 | 305.6 | 474 | 334.1 | 302.5 | 454.9 | 484.3
2781.3 | 1081.3 | 187.5 | 75 | 87.6707 | 138.4 | 147.9 | 149.3 | 159.4 | 196.5 | 30.1 | 21.1 | 48.3 | 2.1 |  |  | 347.2 | 307 | 475.7 | 334 | 304.1 | 462.4 | 487.7
2782.3 | 1082.3 | 186.8 | 74.72 | 87.3434 | 138.2 | 148 | 149.3 | 159.6 | 200.1 | 30.1 | 21.1 | 48.3 | 2 |  |  | 347.4 | 307 | 478.8 | 334 | 306.2 | 467.7 | 490.1
2783.3 | 1083.3 | 186.5 | 74.6 | 87.2031 | 138.3 | 148.3 | 148.8 | 160 | 204 | 30.3 | 21.1 | 48.2 | 2 |  |  | 347.2 | 313.6 | 486.8 | 334 | 312.3 | 476.7 | 493.9
2784.3 | 1084.3 | 188.2 | 75.28 | 87.998 | 138.2 | 148.4 | 149 | 160.9 | 207.8 | 30.4 | 21.1 | 48.3 | 2.1 |  |  | 347.2 | 320.1 | 496.7 | 334 | 318.2 | 477.7 | 493
2785.3 | 1085.3 | 188.2 | 75.28 | 87.998 | 138 | 148.5 | 149.4 | 161.7 | 210.1 | 30.5 | 21.1 | 48.3 | 1.8 |  |  | 347.3 | 316.6 | 491.2 | 334 | 315.8 | 474.2 | 489.3
2786.3 | 1086.3 | 187.8 | 75.12 | 87.811 | 138.2 | 148.6 | 149.8 | 161.9 | 207.8 | 30.5 | 21.1 | 48.2 | 1.6 |  |  | 347.4 | 312.9 | 486.4 | 334.1 | 311.6 | 464.1 | 482.3
2787.3 | 1087.3 | 187.8 | 75.12 | 87.811 | 138.3 | 149.1 | 150.1 | 161.9 | 204.5 | 30.5 | 21.1 | 48.2 | 1.9 |  |  | 347.5 | 307.3 | 478.3 | 334.4 | 306.4 | 454.5 | 476.1
2788.3 | 1088.3 | 187.4 | 74.96 | 87.6239 | 138.5 | 149.3 | 150.3 | 161.8 | 201.4 | 30.6 | 21.1 | 48.2 | 2.1 |  |  | 347.7 | 302.7 | 474.8 | 334.6 | 301.6 | 449.2 | 477.4
2789.3 | 1089.3 | 187.5 | 75 | 87.6707 | 138.5 | 148.9 | 150.4 | 162.1 | 198.9 | 30.6 | 21.1 | 48.3 | 2.3 |  |  | 347.9 | 300 | 474.7 | 334.8 | 299.6 | 450.2 | 481.8
2790.3 | 1090.3 | 186.6 | 74.64 | 87.2499 | 138.5 | 148.9 | 150.3 | 162.1 | 198.8 | 30.4 | 21.1 | 48.3 | 2.3 |  |  | 348.2 | 300 | 475 | 334.9 | 298.1 | 447 | 482.6
2791.3 | 1091.3 | 187.1 | 74.84 | 87.4836 | 138.9 | 149.2 | 150.6 | 161.9 | 199.6 | 30.4 | 21.2 | 48.4 | 1.9 |  |  | 348.3 | 298.8 | 474.6 | 335.1 | 297.8 | 445.9 | 480.2
2792.3 | 1092.3 | 187.4 | 74.96 | 87.6239 | 139.1 | 149.4 | 150.8 | 161.8 | 202.9 | 30.3 | 21.2 | 48.5 | 2.6 |  |  | 348.6 | 299.3 | 476.2 | 335.1 | 298.3 | 445.8 | 477.4
2793.3 | 1093.3 | 187.1 | 74.84 | 87.4836 | 138.9 | 149.6 | 150.8 | 161.5 | 202.4 | 30.2 | 21.1 | 48.6 | 2.5 |  |  | 348.6 | 306.2 | 482.1 | 335.1 | 302.7 | 450.7 | 478.3
2794.3 | 1094.3 | 188.9 | 75.56 | 88.3253 | 138.6 | 149.5 | 150.9 | 160.6 | 202.5 | 30.2 | 21.1 | 48.7 | 2.5 |  |  | 348.6 | 314.5 | 479.1 | 335.1 | 309.7 | 460.6 | 478.1
2795.3 | 1095.3 | 189.2 | 75.68 | 88.4656 | 138.6 | 149 | 150.9 | 160.4 | 203.4 | 30.2 | 21.1 | 48.8 | 3 |  |  | 348.7 | 324.2 | 478.5 | 335.2 | 318.2 | 471.1 | 478
2796.3 | 1096.3 | 188.2 | 75.28 | 87.998 | 138.7 | 148.8 | 150.6 | 160 | 206.7 | 30.2 | 21.1 | 48.9 | 2.9 |  |  | 348.9 | 335.2 | 477.7 | 335.3 | 324.8 | 482.4 | 478.2
2797.3 | 1097.3 | 187.4 | 74.96 | 87.6239 | 138.6 | 149.3 | 150.3 | 159.9 | 208.4 | 30.2 | 21.1 | 48.9 | 2.7 |  |  | 349.1 | 336.5 | 480.1 | 335.5 | 326 | 486.8 | 481.6
2798.3 | 1098.3 | 189.7 | 75.88 | 88.6993 | 139.4 | 149.6 | 150.5 | 159.8 | 208.1 | 30.1 | 21.1 | 48.9 | 2.9 |  |  | 349.5 | 333.9 | 485.9 | 335.7 | 323.1 | 482.8 | 487.6
2799.3 | 1099.3 | 189 | 75.6 | 88.372 | 140.2 | 149.7 | 150.4 | 159.2 | 207.7 | 30.1 | 21.1 | 48.9 | 2.6 |  |  | 349.6 | 334.7 | 485.2 | 336 | 323.5 | 482.7 | 487.6
2800.3 | 1100.3 | 188.1 | 75.24 | 87.9512 | 140.9 | 149.4 | 149.9 | 159 | 207.1 | 30 | 21.1 | 48.9 | 2.4 |  |  | 349.9 | 331.9 | 484.1 | 336.3 | 324 | 481.8 | 487.9
2801.3 | 1101.3 | 189 | 75.6 | 88.372 | 141.5 | 148.9 | 149.9 | 159.3 | 206.4 | 30 | 21.1 | 48.9 | 2.5 |  |  | 350.2 | 333.9 | 483.5 | 336.6 | 324.8 | 480.3 | 486.3
2802.3 | 1102.3 | 188.9 | 75.56 | 88.3253 | 141.9 | 148.7 | 149.9 | 159.8 | 207.1 | 30.1 | 21.1 | 48.9 | 2.1 |  |  | 350.4 | 342.1 | 482.8 | 336.8 | 328.6 | 478.9 | 485.2
2803.3 | 1103.3 | 189.6 | 75.84 | 88.6526 | 142.3 | 148.6 | 150.3 | 160.3 | 206.7 | 30.1 | 21.1 | 48.8 | 2 |  |  | 350.6 | 341.3 | 481.2 | 337.2 | 325.9 | 474.9 | 481.3
2804.3 | 1104.3 | 187.7 | 75.08 | 87.7642 | 142.7 | 148.6 | 150.7 | 160.4 | 205.9 | 30.2 | 21.1 | 48.8 | 1.8 |  |  | 350.9 | 341.5 | 480.5 | 337.5 | 327 | 473.8 | 476.5
2805.3 | 1105.3 | 188.3 | 75.32 | 88.0447 | 142.5 | 148.4 | 151.3 | 160.2 | 205.1 | 30.2 | 21.1 | 48.8 | 2 |  |  | 351.2 | 346.1 | 480.8 | 337.8 | 329.8 | 473 | 474.8
2806.3 | 1106.3 | 187.8 | 75.12 | 87.811 | 142.6 | 148.3 | 151.4 | 160.2 | 206.9 | 30.2 | 21.1 | 48.7 | 1.9 |  |  | 351.4 | 352.3 | 476 | 338.1 | 333.7 | 466.5 | 469.9
2807.3 | 1107.3 | 188 | 75.2 | 87.9045 | 142.9 | 148.4 | 151.2 | 160.1 | 207.8 | 30.2 | 21.1 | 48.6 | 2 |  |  | 351.7 | 359.4 | 473 | 338.4 | 335.9 | 458.4 | 466.7
2808.3 | 1108.3 | 186.4 | 74.56 | 87.1563 | 143.1 | 148.2 | 151.3 | 160.2 | 208.6 | 30.3 | 21.1 | 48.6 | 2.3 |  |  | 351.9 | 359 | 476.8 | 338.6 | 332.4 | 452.5 | 467.9
2809.3 | 1109.3 | 188.8 | 75.52 | 88.2785 | 143.1 | 148.1 | 151.4 | 160.3 | 209.6 | 30.5 | 21.1 | 48.7 | 2.5 |  |  | 352.3 | 358.4 | 485.9 | 338.8 | 327.7 | 447.3 | 472.2
2810.3 | 1110.3 | 187.4 | 74.96 | 87.6239 | 143.2 | 148.2 | 151.5 | 160.3 | 210.4 | 30.6 | 21.1 | 48.9 | 2.8 |  |  | 352.8 | 355.1 | 489.4 | 339 | 322.2 | 440.3 | 474
2811.3 | 1111.3 | 188.4 | 75.36 | 88.0915 | 143.7 | 148.4 | 151.7 | 160.2 | 208 | 30.7 | 21.1 | 49 | 2.8 |  |  | 352.9 | 350.4 | 489.6 | 339.2 | 317.8 | 430.8 | 468.8
2812.3 | 1112.3 | 189.1 | 75.64 | 88.4188 | 143.6 | 148.8 | 151.9 | 160.3 | 206.7 | 30.7 | 21.1 | 49 | 3 |  |  | 353.2 | 344.7 | 491.9 | 339.4 | 312.8 | 423.8 | 469.4
2813.3 | 1113.3 | 188.9 | 75.56 | 88.3253 | 143.1 | 149.3 | 152.1 | 160.6 | 205 | 30.7 | 21.1 | 49.1 | 2.9 |  |  | 353.6 | 340.1 | 491 | 339.5 | 309.5 | 419.1 | 468.2
2814.3 | 1114.3 | 188.7 | 75.48 | 88.2318 | 143 | 149.7 | 151.9 | 160.7 | 203 | 30.7 | 21.1 | 49.1 | 2.7 |  |  | 354.1 | 338 | 490 | 339.5 | 308.2 | 419.7 | 472.7
2815.3 | 1115.3 | 188.3 | 75.32 | 88.0447 | 143.2 | 149.5 | 151.7 | 160.9 | 203 | 30.7 | 21.1 | 49 | 2.8 |  |  | 354.6 | 340.8 | 488.6 | 339.6 | 308.3 | 416.9 | 469.9
2816.3 | 1116.3 | 189.3 | 75.72 | 88.5123 | 143 | 149.4 | 151.4 | 161.2 | 203.1 | 30.7 | 21.1 | 49 | 2.6 |  |  | 355.1 | 342.7 | 485.6 | 339.6 | 307.2 | 413.1 | 467.2
2817.3 | 1117.3 | 188.1 | 75.24 | 87.9512 | 142.9 | 148.9 | 150.9 | 161 | 202.2 | 30.6 | 21.1 | 49 | 2.9 |  |  | 355.7 | 340.6 | 480.2 | 339.6 | 304.8 | 408.5 | 462.6
2818.3 | 1118.3 | 188 | 75.2 | 87.9045 | 142.7 | 148.2 | 150.9 | 160.8 | 200.1 | 30.5 | 21.1 | 48.9 | 2.4 |  |  | 356.3 | 339.7 | 475 | 339.6 | 302.4 | 405.7 | 459.3
2819.3 | 1119.3 | 188.3 | 75.32 | 88.0447 | 142.9 | 148 | 151.5 | 160.6 | 198.8 | 30.5 | 21.1 | 48.8 | 2.5 |  |  | 356.9 | 339.3 | 469.9 | 339.5 | 299 | 398.3 | 454.2
2820.3 | 1120.3 | 187.5 | 75 | 87.6707 | 143.1 | 147.8 | 151.6 | 160.4 | 197.6 | 30.4 | 21.1 | 48.8 | 3.4 |  |  | 357.1 | 336.2 | 461.6 | 339.5 | 294.9 | 389.1 | 450.2
2821.3 | 1121.3 | 185.2 | 74.08 | 86.5953 | 143.5 | 148 | 151.6 | 160.4 | 195.4 | 30.4 | 21.1 | 48.9 | 3.7 |  |  | 357.6 | 333.8 | 453.6 | 339.4 | 290.9 | 385.1 | 448.9
2822.3 | 1122.3 | 187.1 | 74.84 | 87.4836 | 143.8 | 147.8 | 152 | 160.3 | 193.2 | 30.3 | 21.1 | 49.1 | 4.1 |  |  | 358 | 327.4 | 448.3 | 339.3 | 286.5 | 381.8 | 447.5
2823.3 | 1123.3 | 187.8 | 75.12 | 87.811 | 143.9 | 147.6 | 152.2 | 160.1 | 191.1 | 30.3 | 21.1 | 49.2 | 3.6 |  |  | 358.2 | 323.5 | 447 | 339.1 | 284.5 | 378.9 | 446.5
2824.3 | 1124.3 | 187.1 | 74.84 | 87.4836 | 143.9 | 147.8 | 152.2 | 159.7 | 192.4 | 30.3 | 21.1 | 49.2 | 2.9 |  |  | 358.6 | 325 | 450.8 | 338.9 | 285.2 | 379.9 | 447.4
2825.3 | 1125.3 | 188.1 | 75.24 | 87.9512 | 143.9 | 148.3 | 152.1 | 159.2 | 193.9 | 30.2 | 21.1 | 49.2 | 2.6 |  |  | 358.9 | 324.5 | 451.3 | 338.7 | 281.9 | 375.5 | 445.2
2826.3 | 1126.3 | 186.3 | 74.52 | 87.1096 | 144 | 148.9 | 152 | 158.9 | 193.1 | 30.2 | 21.1 | 49.4 | 3 |  |  | 359.2 | 324.3 | 450.4 | 338.5 | 279.9 | 370.5 | 442.3
2827.3 | 1127.3 | 188.6 | 75.44 | 88.185 | 144.1 | 149.2 | 151.8 | 158.5 | 193.7 | 30.2 | 21.1 | 49.4 | 2.7 |  |  | 359.3 | 332.1 | 454.6 | 338.2 | 285.5 | 380.7 | 448.9
2828.3 | 1128.3 | 187.6 | 75.04 | 87.7174 | 144.1 | 148.9 | 151.5 | 158.2 | 196.5 | 30.3 | 21.1 | 49.5 | 3.2 |  |  | 359.7 | 333.2 | 460.8 | 338 | 286.9 | 385.5 | 456.4
2829.3 | 1129.3 | 188 | 75.2 | 87.9045 | 144.2 | 148.9 | 151.5 | 157.4 | 195.6 | 30.5 | 21.1 | 49.7 | 3.9 |  |  | 359.7 | 329 | 457.5 | 337.8 | 283.2 | 381.8 | 454.5
2830.3 | 1130.3 | 187.9 | 75.16 | 87.8577 | 144.2 | 148.8 | 151.1 | 157.1 | 193.2 | 30.6 | 21.1 | 49.8 | 3.9 |  |  | 359.9 | 323.3 | 453.3 | 337.6 | 279.4 | 379.5 | 450.1
2831.3 | 1131.3 | 187.5 | 75 | 87.6707 | 144.5 | 148.8 | 150.7 | 157 | 191.2 | 30.6 | 21.1 | 49.8 | 3.8 |  |  | 360.1 | 318.9 | 450.2 | 337.3 | 276.8 | 382.8 | 451.2
2832.3 | 1132.3 | 188 | 75.2 | 87.9045 | 144.3 | 148.7 | 150.3 | 157.2 | 190.7 | 30.3 | 21.1 | 49.8 | 3.5 |  |  | 360.5 | 318.7 | 446.9 | 337.1 | 277.9 | 385.4 | 449
2833.3 | 1133.3 | 187.3 | 74.92 | 87.5772 | 143.9 | 149.1 | 150.3 | 157.4 | 190.5 | 30.2 | 21.1 | 49.7 | 2.6 |  |  | 360.5 | 319.7 | 447.4 | 336.9 | 279.1 | 389.6 | 451.9
2834.3 | 1134.3 | 186.8 | 74.72 | 87.3434 | 143.5 | 149.2 | 150.3 | 157.6 | 191.3 | 30.3 | 21.1 | 49.5 | 2.3 |  |  | 360.6 | 317.6 | 448.4 | 336.6 | 280.4 | 395.1 | 460.5
2835.3 | 1135.3 | 186.6 | 74.64 | 87.2499 | 143.4 | 149.4 | 149.9 | 157.9 | 191.3 | 30.4 | 21.1 | 49.3 | 2.5 |  |  | 360.6 | 317.1 | 451.8 | 336.4 | 283.7 | 405.5 | 461.5
2836.3 | 1136.3 | 187.9 | 75.16 | 87.8577 | 143.1 | 149.4 | 149.9 | 158 | 191.1 | 30.5 | 21.1 | 49.3 | 2.9 |  |  | 360.6 | 318.9 | 452.2 | 336.2 | 287.1 | 412.9 | 463.7
2837.3 | 1137.3 | 187 | 74.8 | 87.4369 | 142.8 | 149.4 | 149.6 | 158.2 | 191.9 | 30.6 | 21.1 | 49.2 | 3 |  |  | 360.7 | 318 | 451.2 | 336 | 289.3 | 416.6 | 463.5
2838.3 | 1138.3 | 187.5 | 75 | 87.6707 | 142.8 | 149.4 | 149.6 | 158.4 | 192.9 | 30.6 | 21.1 | 49.3 | 3.7 |  |  | 360.8 | 318.5 | 452.9 | 335.8 | 290.1 | 419.8 | 464.7
2839.3 | 1139.3 | 182.9 | 73.16 | 85.5198 | 142.5 | 149.4 | 149.7 | 158.6 | 194.4 | 30.6 | 21.1 | 49.4 | 3.9 |  |  | 360.9 | 319 | 454.7 | 335.7 | 291.3 | 424 | 466.8
2840.3 | 1140.3 | 185.9 | 74.36 | 86.9226 | 142.3 | 149.8 | 150 | 158.8 | 194.5 | 30.6 | 21.1 | 49.4 | 3.9 |  |  | 361.1 | 314.1 | 456.2 | 335.6 | 288.4 | 422 | 463.5
2841.3 | 1141.3 | 187.9 | 75.16 | 87.8577 | 142.2 | 150.2 | 150 | 159.3 | 194 | 30.6 | 21.1 | 49.4 | 4 |  |  | 360.9 | 310.2 | 459.8 | 335.6 | 287 | 421 | 463.4
2842.3 | 1142.3 | 188.2 | 75.28 | 87.998 | 142.1 | 150 | 150.1 | 159.8 | 192.8 | 30.6 | 21.1 | 49.4 | 4.1 |  |  | 361 | 307.3 | 460.3 | 335.6 | 285 | 418.1 | 461.3
2843.3 | 1143.3 | 187.9 | 75.16 | 87.8577 | 141.8 | 149.3 | 150 | 160.1 | 190.9 | 30.4 | 21.1 | 49.4 | 3.8 |  |  | 361.2 | 306.1 | 462.3 | 335.6 | 282.8 | 417.1 | 459.8
2844.3 | 1144.3 | 187.3 | 74.92 | 87.5772 | 141.2 | 149.3 | 150 | 159.9 | 190.1 | 30.2 | 21.1 | 49.3 | 3.2 |  |  | 361.1 | 306.2 | 465 | 335.5 | 282.5 | 413.7 | 458.4
2845.3 | 1145.3 | 184.4 | 73.76 | 86.2212 | 141.2 | 149.2 | 150 | 160 | 189.8 | 30 | 21.1 | 49.2 | 3.4 |  |  | 361 | 307 | 463 | 335.5 | 282.5 | 409.9 | 453
2846.3 | 1146.3 | 188.9 | 75.56 | 88.3253 | 141.3 | 149.1 | 149.9 | 160 | 191.2 | 29.9 | 21.1 | 49.2 | 3.9 |  |  | 361 | 315.4 | 464.3 | 335.5 | 285.4 | 406.8 | 451.5
2847.3 | 1147.3 | 188.5 | 75.4 | 88.1383 | 141.1 | 149 | 149.9 | 159.8 | 192.8 | 29.8 | 21.1 | 49.2 | 4.1 |  |  | 361.1 | 324.6 | 461.4 | 335.4 | 292.2 | 406.3 | 449.1
2848.3 | 1148.3 | 188.4 | 75.36 | 88.0915 | 141.2 | 149 | 149.9 | 159.6 | 193.6 | 29.8 | 21.1 | 49.2 | 4.5 |  |  | 361.2 | 329.2 | 458.9 | 335.4 | 297.8 | 407.7 | 447.6
2849.3 | 1149.3 | 187.1 | 74.84 | 87.4836 | 141.2 | 148.8 | 149.6 | 159.3 | 195.5 | 29.9 | 21.1 | 49.3 | 3.7 |  |  | 361.2 | 340.9 | 458 | 335.4 | 309.6 | 413.8 | 448.3
2850.3 | 1150.3 | 188.1 | 75.24 | 87.9512 | 141 | 148.8 | 149.8 | 158.8 | 199.3 | 30 | 21.1 | 49.4 | 3.5 |  |  | 361.2 | 347 | 457.1 | 335.4 | 317.2 | 424 | 451.4
2851.3 | 1151.3 | 189.5 | 75.8 | 88.6058 | 140.7 | 148.9 | 150 | 158.6 | 199.9 | 30.2 | 21.1 | 49.6 | 4.8 |  |  | 361.6 | 352.2 | 453.2 | 335.4 | 326.2 | 435.6 | 451.3
2852.3 | 1152.3 | 188.9 | 75.56 | 88.3253 | 140.5 | 148.7 | 149.9 | 159 | 199.6 | 30.3 | 21.1 | 49.7 | 4.2 |  |  | 361.9 | 351.6 | 448.7 | 335.4 | 328.2 | 443.5 | 453.2
2853.3 | 1153.3 | 186.6 | 74.64 | 87.2499 | 140.9 | 148.5 | 149.9 | 159.6 | 198.3 | 30.3 | 21.1 | 49.7 | 3.5 |  |  | 361.9 | 348.2 | 455.9 | 335.5 | 327.6 | 445.8 | 459.4
2854.3 | 1154.3 | 189.2 | 75.68 | 88.4656 | 140.8 | 148.5 | 150.4 | 159.9 | 198 | 30.3 | 21.1 | 49.7 | 2.7 |  |  | 362.2 | 347.2 | 464 | 335.7 | 326.9 | 451.6 | 466.3
2855.3 | 1155.3 | 188.9 | 75.56 | 88.3253 | 140.6 | 148.3 | 150.6 | 159.9 | 200.4 | 30.2 | 21.1 | 49.7 | 3 |  |  | 362.4 | 350.6 | 474.1 | 335.9 | 330.5 | 456.1 | 473
2856.3 | 1156.3 | 188.9 | 75.56 | 88.3253 | 140.5 | 148.1 | 150.9 | 160.3 | 203.2 | 30.2 | 21.1 | 49.6 | 3.6 |  |  | 362.3 | 354.1 | 480.1 | 336.2 | 333.2 | 458.9 | 475.7
2857.3 | 1157.3 | 188.2 | 75.28 | 87.998 | 140.5 | 148.1 | 151.3 | 160.9 | 205.2 | 30.3 | 21.1 | 49.6 | 2.8 |  |  | 362.5 | 352 | 479.8 | 336.5 | 333.7 | 459.6 | 468.4
2858.3 | 1158.3 | 189.9 | 75.96 | 88.7929 | 140.6 | 148 | 151.6 | 161.1 | 204 | 30.4 | 21.1 | 49.5 | 2.9 |  |  | 362.7 | 349.6 | 478.3 | 336.8 | 333.9 | 460.4 | 467.6
2859.3 | 1159.3 | 187.5 | 75 | 87.6707 | 141 | 148 | 152 | 161 | 202.3 | 30.5 | 21.1 | 49.4 | 2.8 |  |  | 362.8 | 351.9 | 478.5 | 337.1 | 338 | 463.3 | 469.1
2860.3 | 1160.3 | 188.7 | 75.48 | 88.2318 | 141.2 | 148.2 | 152.4 | 161.1 | 202.9 | 30.5 | 21.1 | 49.5 | 3 |  |  | 363 | 357.3 | 474.2 | 337.5 | 348.1 | 470.3 | 470.6
2861.3 | 1161.3 | 189.1 | 75.64 | 88.4188 | 141.3 | 148.3 | 152.5 | 161.2 | 203.5 | 30.6 | 21.1 | 49.6 | 3.2 |  |  | 363.4 | 369 | 475.4 | 337.9 | 356.5 | 473.2 | 470
2862.3 | 1162.3 | 188.7 | 75.48 | 88.2318 | 141.4 | 148.6 | 152.6 | 160.9 | 205.6 | 30.5 | 21.1 | 49.6 | 2.7 |  |  | 363.6 | 377.1 | 471 | 338.3 | 359.5 | 469.3 | 463.9
2863.3 | 1163.3 | 188.8 | 75.52 | 88.2785 | 141.5 | 149.4 | 152.9 | 161.1 | 205.1 | 30.4 | 21.1 | 49.6 | 2.2 |  |  | 363.8 | 379.6 | 466.1 | 338.8 | 362.1 | 466.6 | 458.8
2864.3 | 1164.3 | 188.5 | 75.4 | 88.1383 | 141.8 | 150.4 | 153 | 161.4 | 204.9 | 30.4 | 21.1 | 49.6 | 2 |  |  | 363.9 | 388.3 | 467.1 | 339.3 | 367.1 | 467.4 | 457.6
2865.3 | 1165.3 | 188.1 | 75.24 | 87.9512 | 142.3 | 150.6 | 153.1 | 161.8 | 205.1 | 30.3 | 21.1 | 49.5 | 2.2 |  |  | 364.2 | 388.4 | 465.5 | 339.8 | 364.1 | 461.1 | 454.8
2866.3 | 1166.3 | 187.2 | 74.88 | 87.5304 | 142.8 | 150.5 | 153.2 | 162.1 | 205.8 | 30.3 | 21.1 | 49.5 | 2.2 |  |  | 364.4 | 389.6 | 466 | 340.4 | 366.7 | 463.7 | 456
2867.3 | 1167.3 | 189.7 | 75.88 | 88.6993 | 143.1 | 150.4 | 153.2 | 161.9 | 206.9 | 30.5 | 21.1 | 49.5 | 2.9 |  |  | 364.7 | 389.4 | 465.5 | 340.9 | 366.4 | 462.9 | 455
2868.3 | 1168.3 | 187.2 | 74.88 | 87.5304 | 143.1 | 150.3 | 153.6 | 162 | 206.6 | 30.7 | 21.1 | 49.5 | 3 |  |  | 365.8 | 388.5 | 467.4 | 341.4 | 368.1 | 469.9 | 459
2869.3 | 1169.3 | 187.8 | 75.12 | 87.811 | 143.3 | 149.9 | 153.9 | 162.1 | 206.2 | 30.7 | 21.1 | 49.4 | 2.9 |  |  | 366.8 | 390.8 | 464.8 | 342 | 369.2 | 476.7 | 463.8
2870.3 | 1170.3 | 187.4 | 74.96 | 87.6239 | 143.7 | 149.6 | 153.9 | 161.7 | 208.2 | 30.6 | 21.1 | 49.4 | 3 |  |  | 367.5 | 388.1 | 463.8 | 342.5 | 370.5 | 484.3 | 464.9
2871.3 | 1171.3 | 187.8 | 75.12 | 87.811 | 144.4 | 149.7 | 153.9 | 161.7 | 207.8 | 30.4 | 21.1 | 49.4 | 2.5 |  |  | 368.2 | 392.4 | 459.7 | 343 | 379.1 | 489 | 462.3
2872.3 | 1172.3 | 187.6 | 75.04 | 87.7174 | 144.8 | 150 | 153.8 | 161.5 | 207.8 | 30.4 | 21.1 | 49.4 | 2.8 |  |  | 368.8 | 397.9 | 456.7 | 343.5 | 384.5 | 490.5 | 458.3
2873.3 | 1173.3 | 186 | 74.4 | 86.9693 | 145.1 | 150.5 | 153.8 | 161.7 | 208.5 | 30.4 | 21.1 | 49.4 | 2.6 |  |  | 369.3 | 400 | 456.5 | 344 | 388.5 | 489.9 | 457.9
2874.3 | 1174.3 | 188.7 | 75.48 | 88.2318 | 144.9 | 150.4 | 154.3 | 161.4 | 208.3 | 30.4 | 21.1 | 49.5 | 1.9 |  |  | 369.7 | 404.3 | 457.4 | 344.6 | 388.2 | 485.3 | 457.4
2875.3 | 1175.3 | 187.7 | 75.08 | 87.7642 | 144.6 | 151 | 155 | 161.4 | 208.3 | 30.4 | 21.1 | 49.5 | 2.3 |  |  | 370.2 | 407.2 | 454.5 | 345.1 | 390.8 | 481.9 | 454.8
2876.3 | 1176.3 | 188.7 | 75.48 | 88.2318 | 144.8 | 151.5 | 155.7 | 161 | 208.9 | 30.3 | 21.1 | 49.7 | 2.3 |  |  | 370.8 | 407.4 | 446.6 | 345.7 | 388.8 | 472.9 | 449.3
2877.3 | 1177.3 | 189.2 | 75.68 | 88.4656 | 145.2 | 150.9 | 155.8 | 160.3 | 208.9 | 30.2 | 21.1 | 49.8 | 2 |  |  | 371.2 | 413.2 | 444.4 | 346.3 | 392.7 | 475.5 | 451.8
2878.3 | 1178.3 | 189.4 | 75.76 | 88.5591 | 145.8 | 150.5 | 155.9 | 159.7 | 211.1 | 30.3 | 21.1 | 49.9 | 1.9 |  |  | 371.5 | 413.2 | 442.5 | 346.8 | 398 | 479.2 | 455
2879.3 | 1179.3 | 186.9 | 74.76 | 87.3901 | 146.3 | 150.5 | 156.2 | 160.2 | 212.2 | 30.5 | 21.1 | 50 | 2.2 |  |  | 372.1 | 416.1 | 442.3 | 347.4 | 399.2 | 486.5 | 458.2
2880.3 | 1180.3 | 187.8 | 75.12 | 87.811 | 146.7 | 150.1 | 156.5 | 160.3 | 214.3 | 30.7 | 21.1 | 50.1 | 2.4 |  |  | 372.5 | 411.3 | 438.2 | 347.9 | 399.3 | 491.1 | 460.6
2881.3 | 1181.3 | 185.1 | 74.04 | 86.5485 | 147.1 | 149.8 | 156.7 | 160.5 | 215.1 | 30.8 | 21.1 | 50.2 | 2.1 |  |  | 372.8 | 408.7 | 434 | 348.4 | 407.7 | 496 | 456.2
2882.3 | 1182.3 | 187.7 | 75.08 | 87.7642 | 147.1 | 150 | 156.8 | 160.7 | 216.9 | 30.7 | 21.1 | 50.2 | 2.4 |  |  | 373.2 | 406.8 | 433 | 349 | 411.4 | 501.7 | 453.8
2883.3 | 1183.3 | 186 | 74.4 | 86.9693 | 146.9 | 150.2 | 157 | 160.8 | 217.7 | 30.6 | 21.1 | 50.1 | 2.8 |  |  | 373.3 | 412.2 | 433.3 | 349.5 | 418.9 | 502.2 | 452.3
2884.3 | 1184.3 | 188.1 | 75.24 | 87.9512 | 146.4 | 149.8 | 157 | 160.7 | 217.7 | 30.6 | 21.1 | 50 | 2.6 |  |  | 373.5 | 424.1 | 434.8 | 350.1 | 430.2 | 504.2 | 452.8
2885.3 | 1185.3 | 188.1 | 75.24 | 87.9512 | 146.5 | 149.5 | 156.8 | 160.8 | 218.2 | 30.7 | 21 | 49.9 | 2.2 |  |  | 373.9 | 424.6 | 435.6 | 350.7 | 429 | 504.5 | 452.4
2886.3 | 1186.3 | 186.8 | 74.72 | 87.3434 | 146.5 | 149.4 | 157 | 161 | 219 | 30.7 | 21.1 | 49.8 | 2.1 |  |  | 374.1 | 429.8 | 435.6 | 351.3 | 437.1 | 504.1 | 450.9
2887.3 | 1187.3 | 186.5 | 74.6 | 87.2031 | 146.1 | 149.6 | 157.5 | 161.7 | 221.6 | 30.8 | 21.1 | 49.8 | 2 |  |  | 374.3 | 430.1 | 432.8 | 351.9 | 432.6 | 496.2 | 448.2
2888.3 | 1188.3 | 187.3 | 74.92 | 87.5772 | 146.1 | 149.8 | 157.8 | 162.2 | 219.2 | 30.9 | 21 | 49.7 | 1.9 |  |  | 374.7 | 426.7 | 432.9 | 352.5 | 427.1 | 489.7 | 446.2
2889.3 | 1189.3 | 186 | 74.4 | 86.9693 | 146.3 | 150 | 157.8 | 162.4 | 217 | 31 | 21 | 49.7 | 2.1 |  |  | 374.9 | 430.3 | 434.6 | 353.2 | 427.4 | 492.1 | 449.1
2890.3 | 1190.3 | 186.7 | 74.68 | 87.2966 | 146.9 | 150.1 | 157.8 | 162.4 | 217.8 | 31.1 | 21 | 49.6 | 2.1 |  |  | 375.3 | 437.9 | 441.8 | 353.9 | 434.7 | 495.5 | 452.1
2891.3 | 1191.3 | 187.5 | 75 | 87.6707 | 146.9 | 150.2 | 158.2 | 162.6 | 220.7 | 31.2 | 21 | 49.6 | 2 |  |  | 375.7 | 443.2 | 447.5 | 354.5 | 436.8 | 498.2 | 455.6
2892.3 | 1192.3 | 188.2 | 75.28 | 87.998 | 146.5 | 150.6 | 158.5 | 162.5 | 222.1 | 31.3 | 21 | 49.5 | 2 |  |  | 376 | 446.2 | 453.8 | 355.1 | 438 | 502.5 | 459.1
2893.3 | 1193.3 | 188.1 | 75.24 | 87.9512 | 146 | 151.1 | 158.7 | 162.8 | 223.7 | 31.4 | 21 | 49.5 | 2.2 |  |  | 376.4 | 446.5 | 455.7 | 355.8 | 432.6 | 496.3 | 456.4
2894.3 | 1194.3 | 187.3 | 74.92 | 87.5772 | 145.9 | 150.9 | 159 | 163.4 | 221.4 | 31.2 | 21 | 49.5 | 2 |  |  | 376.8 | 443.9 | 454.5 | 356.4 | 426.2 | 487.4 | 453.1
2895.3 | 1195.3 | 186.7 | 74.68 | 87.2966 | 146.1 | 150.9 | 159.3 | 163.5 | 218.3 | 31 | 21 | 49.5 | 1.7 |  |  | 377.1 | 440.8 | 459.5 | 357 | 419.9 | 483.5 | 454.6
2896.3 | 1196.3 | 186.8 | 74.72 | 87.3434 | 146.5 | 151.3 | 159.5 | 163.8 | 217.3 | 31 | 21 | 49.6 | 1.9 |  |  | 377.6 | 437.4 | 465.8 | 357.7 | 415.7 | 485.8 | 462.3
2897.3 | 1197.3 | 186.4 | 74.56 | 87.1563 | 147.1 | 151.6 | 159.6 | 164.1 | 217.2 | 31 | 21 | 49.7 | 1.6 |  |  | 378.1 | 426.6 | 463.5 | 358.3 | 405.8 | 482.5 | 464.1
2898.3 | 1198.3 | 186.6 | 74.64 | 87.2499 | 147.3 | 151.6 | 159.5 | 164.1 | 214.1 | 31.2 | 21 | 49.7 | 1.9 |  |  | 378.7 | 418.4 | 463.7 | 358.9 | 397.8 | 480 | 464
2899.3 | 1199.3 | 187.5 | 75 | 87.6707 | 147.6 | 152 | 159.3 | 164 | 212.7 | 31.3 | 21 | 49.7 | 1.6 |  |  | 379.1 | 415 | 460 | 359.4 | 393.7 | 478.7 | 463
2900.3 | 1200.3 | 188.4 | 75.36 | 88.0915 | 147.8 | 152.2 | 159 | 164.1 | 209.6 | 31.3 | 21 | 49.7 | 1.7 |  |  | 379.9 | 405.4 | 461 | 359.8 | 385.1 | 476 | 462.4
2901.3 | 1201.3 | 189 | 75.6 | 88.372 | 147.7 | 152.4 | 158.8 | 163.9 | 208.4 | 31.2 | 21 | 49.8 | 2 |  |  | 380.3 | 395.6 | 458.7 | 360.2 | 376.8 | 469.5 | 461.4
2902.3 | 1202.3 | 188.1 | 75.24 | 87.9512 | 147.2 | 152.7 | 158.7 | 163.5 | 205.5 | 31.2 | 21 | 49.9 | 2.2 |  |  | 380.8 | 386.1 | 453.1 | 360.5 | 369.5 | 463.3 | 457.4
2903.3 | 1203.3 | 187.5 | 75 | 87.6707 | 146.8 | 152.8 | 158.6 | 163.4 | 201.9 | 31.2 | 21 | 49.9 | 2.3 |  |  | 381.3 | 377.6 | 447.3 | 360.8 | 362.4 | 454 | 452.8
2904.3 | 1204.3 | 187.8 | 75.12 | 87.811 | 146.4 | 152.8 | 158.3 | 163.2 | 198.9 | 31.1 | 21 | 50 | 2.4 |  |  | 381.6 | 368.9 | 444.4 | 361 | 355.4 | 447 | 450.6
2905.3 | 1205.3 | 186.6 | 74.64 | 87.2499 | 146.1 | 152.7 | 157.7 | 162.7 | 197.1 | 30.8 | 21 | 50 | 1.9 |  |  | 381.9 | 362.2 | 444.6 | 361.2 | 347.5 | 437.4 | 450.5
2906.3 | 1206.3 | 189.5 | 75.8 | 88.6058 | 145.8 | 152.5 | 157.4 | 162.4 | 195.2 | 30.7 | 21 | 50.1 | 1.7 |  |  | 382.1 | 354.4 | 442.5 | 361.2 | 339.5 | 433 | 449.9
2907.3 | 1207.3 | 189.8 | 75.92 | 88.7461 | 145.3 | 152 | 157.1 | 161.8 | 193.4 | 30.7 | 21 | 50.1 | 1.6 |  |  | 382.3 | 348.8 | 447.6 | 361.2 | 333.9 | 430.9 | 455.5
2908.3 | 1208.3 | 189.4 | 75.76 | 88.5591 | 144.8 | 151.2 | 156.7 | 161.4 | 193.3 | 30.8 | 21 | 50.1 | 1.4 |  |  | 382.5 | 346.4 | 450.9 | 361.1 | 331.7 | 436.3 | 457.3
2909.3 | 1209.3 | 189.5 | 75.8 | 88.6058 | 144.5 | 150.7 | 156.3 | 161 | 194.3 | 31 | 21 | 50.1 | 1.3 |  |  | 382.5 | 346.7 | 453.1 | 360.9 | 333.3 | 444.5 | 460.2
2910.3 | 1210.3 | 185.8 | 74.32 | 86.8758 | 144.4 | 150.8 | 155.8 | 160.9 | 197.3 | 31 | 21 | 50.1 | 1.5 |  |  | 382.4 | 348.9 | 454.8 | 360.7 | 337.3 | 453 | 462.6
2911.3 | 1211.3 | 188.6 | 75.44 | 88.185 | 144.3 | 150.5 | 155.3 | 161.1 | 200.7 | 31 | 21 | 50.2 | 1.5 |  |  | 382.6 | 350.9 | 456.5 | 360.5 | 338.9 | 460.3 | 466.4
2912.3 | 1212.3 | 188.5 | 75.4 | 88.1383 | 144.4 | 150.3 | 154.5 | 161.7 | 200.4 | 30.9 | 21.1 | 50.3 | 1.6 |  |  | 382.6 | 350 | 455.2 | 360.3 | 338.1 | 462.9 | 465.9
2913.3 | 1213.3 | 187.6 | 75.04 | 87.7174 | 144.3 | 149.9 | 153.9 | 162 | 199 | 31 | 21 | 50.4 | 1.7 |  |  | 382.6 | 351 | 449.6 | 360.2 | 341 | 459.2 | 457.7
2914.3 | 1214.3 | 185.5 | 74.2 | 86.7355 | 144.2 | 149.7 | 154 | 162 | 199.6 | 31.1 | 21 | 50.4 | 1.8 |  |  | 382.6 | 360.9 | 454.8 | 360.1 | 344.8 | 460.3 | 456.8
2915.3 | 1215.3 | 187.2 | 74.88 | 87.5304 | 143.8 | 149.4 | 154.1 | 162.1 | 202.2 | 31.1 | 21 | 50.4 | 2.1 |  |  | 382.7 | 364.4 | 457 | 360.1 | 346.9 | 458.9 | 456.9
2916.3 | 1216.3 | 187.1 | 74.84 | 87.4836 | 143.3 | 149.1 | 153.9 | 162.3 | 203 | 31.1 | 21 | 50.5 | 2.9 |  |  | 382.8 | 364.8 | 458 | 360 | 345.3 | 456.4 | 455.5
2917.3 | 1217.3 | 188 | 75.2 | 87.9045 | 143 | 149.2 | 153.7 | 162.5 | 202.3 | 31.1 | 21 | 50.4 | 2.2 |  |  | 382.8 | 367.5 | 457.9 | 360.1 | 342.5 | 449.9 | 451.6
2918.3 | 1218.3 | 187.7 | 75.08 | 87.7642 | 142.9 | 149.5 | 153.8 | 162.6 | 201.1 | 31 | 21 | 50.4 | 2 |  |  | 382.9 | 362.9 | 457.7 | 360.2 | 338.1 | 444.9 | 450.4
2919.3 | 1219.3 | 186.7 | 74.68 | 87.2966 | 143.2 | 149.7 | 154 | 162.6 | 199.2 | 30.9 | 21 | 50.4 | 2.1 |  |  | 382.9 | 362.4 | 458.4 | 360.4 | 334.2 | 442.5 | 451
2920.3 | 1220.3 | 187 | 74.8 | 87.4369 | 143.2 | 149.5 | 154.2 | 162.3 | 197.2 | 30.8 | 21 | 50.4 | 2.3 |  |  | 383.2 | 357.6 | 456.5 | 360.5 | 330.4 | 440.8 | 452.7
2921.3 | 1221.3 | 186.5 | 74.6 | 87.2031 | 143.2 | 149.3 | 154.1 | 162 | 196.2 | 30.7 | 21 | 50.5 | 2.3 |  |  | 383.3 | 359.7 | 455.6 | 360.5 | 331.6 | 442.9 | 455.9
2922.3 | 1222.3 | 188.8 | 75.52 | 88.2785 | 143 | 149 | 153.8 | 161.7 | 197.1 | 30.6 | 21 | 50.6 | 2.3 |  |  | 383.5 | 366.6 | 458.8 | 360.6 | 334.1 | 446.4 | 456.4
2923.3 | 1223.3 | 189.5 | 75.8 | 88.6058 | 143 | 148.8 | 153.5 | 161.7 | 201.8 | 30.5 | 21 | 50.5 | 2.3 |  |  | 383.5 | 375.2 | 459.6 | 360.6 | 336.7 | 444.5 | 453.1
2924.3 | 1224.3 | 189.8 | 75.92 | 88.7461 | 142.9 | 148.9 | 153.1 | 161.8 | 203.6 | 30.6 | 21 | 50.5 | 2.6 |  |  | 383.8 | 380.4 | 456.9 | 360.7 | 336.9 | 438.7 | 447.2
2925.3 | 1225.3 | 190.7 | 76.28 | 89.1669 | 143.5 | 149.3 | 152.9 | 161.7 | 205.3 | 30.8 | 21 | 50.5 | 2.6 |  |  | 383.9 | 384.9 | 455.7 | 360.8 | 336.6 | 435.5 | 445.9
2926.3 | 1226.3 | 191.1 | 76.44 | 89.354 | 144.5 | 149.3 | 153 | 161.5 | 207 | 31.1 | 21 | 50.5 | 2.7 |  |  | 384.2 | 384 | 458 | 360.9 | 332 | 430.3 | 447.8
2927.3 | 1227.3 | 188.9 | 75.56 | 88.3253 | 145.4 | 149.4 | 152.9 | 161.8 | 205.9 | 31.3 | 21 | 50.6 | 3.1 |  |  | 384.6 | 382.9 | 464.3 | 361 | 331.5 | 434 | 452.7
2928.3 | 1228.3 | 187.8 | 75.12 | 87.811 | 145.5 | 149.6 | 153 | 161.8 | 205.1 | 31.2 | 21 | 50.6 | 3 |  |  | 385 | 374.4 | 463.6 | 361 | 324.9 | 431.9 | 453.4
2929.3 | 1229.3 | 187.7 | 75.08 | 87.7642 | 145.6 | 150 | 153 | 161.6 | 202.9 | 31.2 | 21 | 50.7 | 3 |  |  | 385.4 | 369.6 | 465.3 | 361.1 | 321.3 | 430.3 | 455.2
2930.3 | 1230.3 | 187.5 | 75 | 87.6707 | 146 | 151.2 | 152.8 | 161 | 202.2 | 31.3 | 21 | 50.7 | 3.4 |  |  | 385.7 | 374.1 | 465.1 | 361.1 | 325.9 | 432.5 | 456.5
2931.3 | 1231.3 | 186.7 | 74.68 | 87.2966 | 146 | 151.7 | 152.9 | 160.7 | 204.8 | 31.4 | 21 | 50.7 | 3.2 |  |  | 386.3 | 377.4 | 463.4 | 361.2 | 326.7 | 432.2 | 450.9
2932.3 | 1232.3 | 189.1 | 75.64 | 88.4188 | 145.9 | 150.9 | 152.3 | 160.9 | 204.4 | 31.4 | 21 | 50.6 | 3.3 |  |  | 386.8 | 381.1 | 458.1 | 361.2 | 329.9 | 433.4 | 446.9
2933.3 | 1233.3 | 190.4 | 76.16 | 89.0267 | 145.8 | 150.7 | 151.2 | 161 | 203.2 | 31.4 | 21 | 50.7 | 3.6 |  |  | 387.3 | 377.5 | 460.7 | 361.2 | 326.4 | 430.7 | 447.8
2934.3 | 1234.3 | 189.5 | 75.8 | 88.6058 | 146 | 151.1 | 151.2 | 161 | 202.3 | 31.4 | 21 | 50.7 | 4.1 |  |  | 388 | 381.8 | 466 | 361.3 | 331.1 | 436.1 | 448.6
2935.3 | 1235.3 | 187.8 | 75.12 | 87.811 | 145.7 | 151.1 | 151.8 | 160.9 | 204.5 | 31.4 | 21 | 50.8 | 5.2 |  |  | 388.5 | 381.5 | 472.2 | 361.3 | 332.7 | 436.8 | 450.2
2936.3 | 1236.3 | 187.6 | 75.04 | 87.7174 | 145.8 | 150.6 | 151.8 | 160.9 | 205.3 | 31.4 | 21 | 50.9 | 4.7 |  |  | 389.1 | 383.6 | 474.8 | 361.4 | 332.3 | 434.2 | 449.3
2937.3 | 1237.3 | 187.1 | 74.84 | 87.4836 | 145.6 | 150.3 | 151.8 | 161 | 205.7 | 31.4 | 21 | 50.9 | 2.9 |  |  | 389.6 | 382.2 | 473.9 | 361.5 | 331.2 | 430.2 | 447
2938.3 | 1238.3 | 187.4 | 74.96 | 87.6239 | 145.2 | 150.8 | 152.3 | 160.9 | 205.2 | 31.4 | 21 | 51 | 2.5 |  |  | 390.3 | 380.3 | 476.5 | 361.6 | 328.7 | 432.6 | 450.9
2939.3 | 1239.3 | 183.4 | 73.36 | 85.7536 | 145.6 | 151.1 | 152.5 | 160.7 | 204.5 | 31.4 | 21 | 51.1 | 2.5 |  |  | 391.1 | 379.6 | 477.2 | 361.8 | 325.1 | 434.6 | 456.1
2940.3 | 1240.3 | 185.9 | 74.36 | 86.9226 | 146.2 | 151.3 | 152.1 | 160.8 | 204.8 | 31.5 | 21 | 51.2 | 2.4 |  |  | 391.6 | 379.8 | 478.8 | 361.9 | 327.8 | 438.4 | 455.9
2941.3 | 1241.3 | 187.2 | 74.88 | 87.5304 | 146.7 | 151.1 | 152 | 160.6 | 206.2 | 31.4 | 21 | 51.3 | 3 |  |  | 392.2 | 383.5 | 481.7 | 362 | 332.5 | 444.2 | 454.5
2942.3 | 1242.3 | 187.7 | 75.08 | 87.7642 | 146.8 | 151.1 | 152 | 160.9 | 206.8 | 31.4 | 21 | 51.3 | 4.1 |  |  | 392.9 | 386.3 | 482.1 | 362 | 336.9 | 444.4 | 452.2
2943.3 | 1243.3 | 187.2 | 74.88 | 87.5304 | 146.6 | 151.1 | 152.1 | 161.2 | 207.4 | 31.4 | 21 | 51.2 | 4 |  |  | 393.5 | 386.9 | 483.7 | 362.1 | 338.5 | 445.2 | 454.7
2944.3 | 1244.3 | 187.6 | 75.04 | 87.7174 | 146.9 | 151.2 | 152.4 | 161.4 | 206.8 | 31.3 | 21 | 51.1 | 4.7 |  |  | 394.1 | 388.7 | 480.3 | 362.2 | 339.5 | 446.9 | 453.9
2945.3 | 1245.3 | 187.6 | 75.04 | 87.7174 | 147.3 | 151.2 | 152.8 | 161.5 | 205.8 | 31.3 | 21 | 51.1 | 6.3 |  |  | 394.6 | 390.5 | 476.7 | 362.4 | 344.2 | 451.5 | 454.6
2946.3 | 1246.3 | 185 | 74 | 86.5017 | 147.5 | 151.2 | 153 | 161.6 | 205.8 | 31.2 | 21 | 51.2 | 6.1 |  |  | 395.2 | 391.2 | 476.2 | 362.6 | 344.1 | 449.3 | 454
2947.3 | 1247.3 | 187.4 | 74.96 | 87.6239 | 147.6 | 151 | 153.2 | 161.7 | 206.7 | 31.2 | 21 | 51.2 | 4.2 |  |  | 395.7 | 398.5 | 474.4 | 362.8 | 350.4 | 455.4 | 454.6
2948.3 | 1248.3 | 187.3 | 74.92 | 87.5772 | 147.5 | 150.7 | 153.3 | 161.9 | 207.8 | 31.2 | 21 | 51.2 | 3 |  |  | 396.2 | 391.3 | 471 | 363.1 | 347.2 | 455.7 | 453.9
2949.3 | 1249.3 | 186.8 | 74.72 | 87.3434 | 146.9 | 150.3 | 153.3 | 162 | 206.5 | 31.2 | 21 | 51.1 | 3.5 |  |  | 396.6 | 392.8 | 464.5 | 363.3 | 355.1 | 460.5 | 452.2
2950.3 | 1250.3 | 189 | 75.6 | 88.372 | 146.9 | 149.7 | 153.3 | 162.2 | 208.9 | 31.4 | 21 | 50.9 | 4.1 |  |  | 397.1 | 406.9 | 463.6 | 363.6 | 369.8 | 471.7 | 452.7
2951.3 | 1251.3 | 188.7 | 75.48 | 88.2318 | 146.6 | 149.7 | 152.8 | 162.3 | 212.7 | 31.5 | 21 | 50.8 | 6.1 |  |  | 397.5 | 414.7 | 461.9 | 363.9 | 378.7 | 473.6 | 452.8
2952.3 | 1252.3 | 188.3 | 75.32 | 88.0447 | 146.3 | 149.8 | 152.4 | 162.5 | 212.9 | 31.7 | 21 | 50.8 | 6.7 |  |  | 397.9 | 421.1 | 462.6 | 364.3 | 384.9 | 480 | 457
2953.3 | 1253.3 | 188.7 | 75.48 | 88.2318 | 146.4 | 149.7 | 152.7 | 162.6 | 213.7 | 31.7 | 21 | 50.8 | 7.7 |  |  | 398.2 | 436.5 | 466.4 | 364.7 | 393 | 484.1 | 458.3
2954.3 | 1254.3 | 188.5 | 75.4 | 88.1383 | 146.6 | 149.8 | 153.2 | 162.7 | 216.5 | 31.7 | 21 | 50.8 | 7.2 |  |  | 398.3 | 438.7 | 469.9 | 365.2 | 393.9 | 483.3 | 458.6
2955.3 | 1255.3 | 187.1 | 74.84 | 87.4836 | 146.4 | 150.4 | 154.3 | 162.5 | 216.4 | 31.7 | 21 | 50.8 | 4.9 |  |  | 398.7 | 440 | 466.2 | 365.8 | 395.1 | 483.3 | 455.8
2956.3 | 1256.3 | 187.8 | 75.12 | 87.811 | 146.4 | 150.8 | 155.6 | 162.2 | 215.2 | 31.7 | 21 | 50.7 | 4.2 |  |  | 398.8 | 440.1 | 461.8 | 366.5 | 395 | 473.9 | 449
2957.3 | 1257.3 | 186.6 | 74.64 | 87.2499 | 146.5 | 150.6 | 156.2 | 162.2 | 215.4 | 31.6 | 21 | 50.6 | 4.5 |  |  | 399.1 | 441.2 | 461.3 | 367.1 | 398 | 471.8 | 448.7
2958.3 | 1258.3 | 188.4 | 75.36 | 88.0915 | 146.3 | 150.1 | 156.4 | 162 | 213.5 | 31.6 | 21 | 50.5 | 5 |  |  | 399.4 | 436.8 | 463.5 | 367.8 | 395.5 | 472.2 | 451.1
2959.3 | 1259.3 | 187.9 | 75.16 | 87.8577 | 146.9 | 150.2 | 156.8 | 162 | 212.1 | 31.5 | 21 | 50.5 | 5.5 |  |  | 399.8 | 438.7 | 464.7 | 368.4 | 400.8 | 479.2 | 451.9
2960.3 | 1260.3 | 187.7 | 75.08 | 87.7642 | 147.6 | 150.5 | 157.4 | 162.1 | 214 | 31.4 | 21 | 50.5 | 4.4 |  |  | 400.1 | 439 | 465.2 | 369.1 | 406.9 | 485.8 | 454.5
2961.3 | 1261.3 | 187.7 | 75.08 | 87.7642 | 148 | 150.8 | 157.5 | 162 | 216 | 31.3 | 21 | 50.4 | 4.7 |  |  | 400.5 | 443.3 | 466.6 | 369.7 | 413.5 | 493.1 | 458.6
2962.3 | 1262.3 | 188.5 | 75.4 | 88.1383 | 147.8 | 151.3 | 157.7 | 161.9 | 217.6 | 31.3 | 21 | 50.5 | 4.3 |  |  | 401 | 448.4 | 468.1 | 370.3 | 416.4 | 495.6 | 459.1
2963.3 | 1263.3 | 186.6 | 74.64 | 87.2499 | 147.6 | 151.8 | 157.9 | 161.9 | 216.5 | 31.3 | 21 | 50.5 | 4.3 |  |  | 401.3 | 452.3 | 472.9 | 371 | 420.1 | 499.6 | 462.4
2964.3 | 1264.3 | 187 | 74.8 | 87.4369 | 147.7 | 152.3 | 157.7 | 161.8 | 216.4 | 31.3 | 21 | 50.4 | 4.9 |  |  | 401.6 | 452.3 | 480.7 | 371.8 | 418 | 494.5 | 462.7
2965.3 | 1265.3 | 187.1 | 74.84 | 87.4836 | 147.6 | 152.5 | 157.8 | 161.9 | 218.8 | 31.2 | 21 | 50.3 | 5.3 |  |  | 402.1 | 454.4 | 486.7 | 372.6 | 418.3 | 493.4 | 466
2966.3 | 1266.3 | 188.3 | 75.32 | 88.0447 | 147.5 | 152.7 | 157.8 | 161.9 | 220 | 31.3 | 21 | 50.3 | 5.1 |  |  | 402.3 | 458.7 | 487.9 | 373.4 | 417.1 | 498.5 | 467.3
2967.3 | 1267.3 | 187.3 | 74.92 | 87.5772 | 147.7 | 153.2 | 157.6 | 162.2 | 219.6 | 31.2 | 21 | 50.4 | 4.9 |  |  | 402.6 | 464.1 | 485.6 | 374.3 | 418.6 | 498.4 | 464.7
2968.3 | 1268.3 | 186.3 | 74.52 | 87.1096 | 147.9 | 153.5 | 157.3 | 162.4 | 219.3 | 31.2 | 21 | 50.3 | 5.3 |  |  | 403 | 477.5 | 482.5 | 375.2 | 431 | 501.5 | 463.1
2969.3 | 1269.3 | 187.1 | 74.84 | 87.4836 | 148 | 153.6 | 157.2 | 162.5 | 220.5 | 31.2 | 21 | 50.3 | 5.1 |  |  | 403.5 | 481.4 | 478.5 | 376.1 | 437.9 | 503.8 | 462.2
2970.3 | 1270.3 | 184.7 | 73.88 | 86.3615 | 148.3 | 153 | 157.4 | 162.9 | 219.5 | 31.3 | 21 | 50.3 | 6.4 |  |  | 404.3 | 477.9 | 473.1 | 377 | 439.4 | 509.1 | 460.3
2971.3 | 1271.3 | 187.2 | 74.88 | 87.5304 | 148.6 | 152.9 | 157.7 | 163.1 | 220 | 31.3 | 21 | 50.3 | 6 |  |  | 404.9 | 472.8 | 472.5 | 377.9 | 436.6 | 507.9 | 461.9
2972.3 | 1272.3 | 187.3 | 74.92 | 87.5772 | 148.8 | 152.8 | 157.9 | 163.3 | 217.9 | 31.4 | 21 | 50.2 | 4.2 |  |  | 405.6 | 467 | 473.1 | 378.8 | 435.2 | 511.6 | 466.7
2973.3 | 1273.3 | 184.7 | 73.88 | 86.3615 | 148.7 | 152.3 | 158.3 | 163.9 | 218.2 | 31.4 | 21 | 50.1 | 4.8 |  |  | 405.7 | 462.7 | 480.8 | 379.7 | 434 | 523.1 | 477.1
2974.3 | 1274.3 | 187 | 74.8 | 87.4369 | 148.6 | 152.5 | 158.5 | 164.1 | 220.7 | 31.4 | 21 | 50 | 6.3 |  |  | 405.9 | 461.3 | 484.1 | 380.6 | 434.1 | 523.9 | 476.8
2975.3 | 1275.3 | 188.5 | 75.4 | 88.1383 | 148.7 | 152.8 | 159.2 | 164 | 220.4 | 31.5 | 21 | 49.9 | 7.6 |  |  | 405.9 | 459.9 | 480.3 | 381.5 | 432.7 | 515.1 | 467.7
2976.3 | 1276.3 | 188.9 | 75.56 | 88.3253 | 148.5 | 152.7 | 159.7 | 164.2 | 220.8 | 31.5 | 21 | 49.8 | 6.8 |  |  | 406 | 465.2 | 476.4 | 382.4 | 440.4 | 511 | 464.7
2977.3 | 1277.3 | 185.9 | 74.36 | 86.9226 | 147.9 | 152.7 | 160.1 | 164.6 | 222 | 31.6 | 21 | 49.6 | 6.5 |  |  | 406.4 | 465 | 470.9 | 383.3 | 445.1 | 508.7 | 461.4
2978.3 | 1278.3 | 187.8 | 75.12 | 87.811 | 147.9 | 152.6 | 160.1 | 164.7 | 218.8 | 31.6 | 21 | 49.6 | 4.9 |  |  | 406.4 | 455.8 | 469.7 | 384.2 | 438.9 | 510.9 | 465.4
2979.3 | 1279.3 | 185.8 | 74.32 | 86.8758 | 148.6 | 152.7 | 160.2 | 164.6 | 215.9 | 31.5 | 21 | 49.5 | 5.4 |  |  | 406.7 | 446 | 470.7 | 385 | 430.9 | 506.7 | 468.7
2980.3 | 1280.3 | 189.9 | 75.96 | 88.7929 | 149.2 | 152.8 | 159.9 | 164.6 | 213.2 | 31.5 | 21 | 49.5 | 5.1 |  |  | 406.9 | 435.7 | 467.1 | 385.8 | 420.8 | 493.3 | 465.4
2981.3 | 1281.3 | 192.5 | 77 | 90.0086 | 149.5 | 152.9 | 159.8 | 164.7 | 210.3 | 31.2 | 21 | 49.6 | 6.4 |  |  | 406.7 | 428.2 | 467.9 | 386.6 | 410.2 | 486.7 | 465.3
2982.3 | 1282.3 | 191.6 | 76.64 | 89.5877 | 149.6 | 153.4 | 159.7 | 164.5 | 208.8 | 31.1 | 21 | 49.6 | 6.9 |  |  | 407 | 425.2 | 470.5 | 387.3 | 405.1 | 486.1 | 465.7
2983.3 | 1283.3 | 191.6 | 76.64 | 89.5877 | 149.6 | 153.6 | 159.3 | 164.3 | 209.7 | 31 | 21 | 49.7 | 4.9 |  |  | 406.9 | 420.1 | 475.3 | 387.9 | 399.4 | 483.9 | 467.5
2984.3 | 1284.3 | 191.3 | 76.52 | 89.4475 | 149.2 | 153.7 | 158.8 | 164.3 | 209.6 | 30.9 | 21 | 49.7 | 3.5 |  |  | 406.6 | 414.1 | 475.3 | 388.4 | 391.1 | 478 | 466.2
2985.3 | 1285.3 | 190 | 76 | 88.8396 | 148.9 | 153.9 | 158.6 | 163.7 | 207.6 | 31 | 21 | 49.7 | 3.7 |  |  | 406.7 | 408.3 | 472.3 | 388.9 | 385.4 | 471.6 | 462.9
2986.3 | 1286.3 | 189.1 | 75.64 | 88.4188 | 148.8 | 153.6 | 158.8 | 163.4 | 205.4 | 31.1 | 21 | 49.7 | 3.6 |  |  | 406.7 | 400.3 | 468.4 | 389.3 | 377.9 | 464.7 | 459.4
2987.3 | 1287.3 | 187.9 | 75.16 | 87.8577 | 149.1 | 153.1 | 159 | 163.5 | 204.1 | 31.3 | 21 | 49.7 | 4 |  |  | 406.6 | 394.7 | 467.5 | 389.6 | 370.6 | 458.8 | 461.8
2988.3 | 1288.3 | 188.1 | 75.24 | 87.9512 | 149.4 | 153 | 159 | 163.3 | 201.9 | 31.3 | 21 | 49.8 | 4.1 |  |  | 406.5 | 385.8 | 463.2 | 389.8 | 361.9 | 451.7 | 459.2
2989.3 | 1289.3 | 187.6 | 75.04 | 87.7174 | 149.8 | 153.7 | 158.7 | 163.1 | 199.7 | 31.3 | 21 | 49.8 | 4.3 |  |  | 406.5 | 379.6 | 462.5 | 390.1 | 357.3 | 456.1 | 463.9
2990.3 | 1290.3 | 188 | 75.2 | 87.9045 | 150.2 | 154 | 158.2 | 163.2 | 198.7 | 31.4 | 21 | 49.9 | 3.4 |  |  | 406.5 | 374.4 | 462.4 | 390.2 | 350.3 | 458.1 | 469.8
2991.3 | 1291.3 | 188.6 | 75.44 | 88.185 | 150.1 | 154 | 157.5 | 163.4 | 196.9 | 31.4 | 21 | 49.9 | 3.4 |  |  | 406.2 | 369.3 | 462.3 | 390.4 | 345.1 | 457.2 | 472.1
2992.3 | 1292.3 | 189 | 75.6 | 88.372 | 149.7 | 154.1 | 157 | 163.4 | 195.7 | 31.3 | 21 | 50 | 3.3 |  |  | 406 | 363.8 | 461.2 | 390.4 | 343 | 461 | 473.6
2993.3 | 1293.3 | 189.8 | 75.92 | 88.7461 | 149.2 | 154.3 | 157 | 163.3 | 195.7 | 31.3 | 21 | 50 | 3.2 |  |  | 405.6 | 361.6 | 462.9 | 390.4 | 342.4 | 462.4 | 473.1
2994.3 | 1294.3 | 188.8 | 75.52 | 88.2785 | 148.7 | 154.6 | 156.9 | 163.5 | 197.3 | 31.3 | 21 | 50 | 2.6 |  |  | 405.4 | 365.1 | 464.7 | 390.5 | 344.6 | 464.2 | 472.2
2995.3 | 1295.3 | 186.9 | 74.76 | 87.3901 | 148.3 | 154.6 | 157.1 | 163.6 | 198.3 | 31.4 | 21 | 50 | 3 |  |  | 405.2 | 365.3 | 466.7 | 390.6 | 344.7 | 469.3 | 469.6
2996.3 | 1296.3 | 190.1 | 76.04 | 88.8864 | 147.6 | 154.5 | 157.3 | 163.6 | 200.3 | 31.4 | 21 | 49.9 | 3.5 |  |  | 404.8 | 364.5 | 470.5 | 390.6 | 344.4 | 471.8 | 471.3
2997.3 | 1297.3 | 190.5 | 76.2 | 89.0734 | 147.3 | 154.3 | 157.2 | 163.5 | 201.5 | 31.4 | 21 | 50 | 3.9 |  |  | 404.6 | 361.4 | 467.1 | 390.8 | 342.3 | 471.6 | 470.8
2998.3 | 1298.3 | 188.6 | 75.44 | 88.185 | 147.2 | 154.2 | 157.1 | 163.4 | 200.6 | 31.4 | 21 | 50.1 | 3.4 |  |  | 404.2 | 356.6 | 467.6 | 390.9 | 338.6 | 471.6 | 472.3
2999.3 | 1299.3 | 189.6 | 75.84 | 88.6526 | 147.2 | 153.6 | 157.1 | 163.3 | 200 | 31.3 | 21 | 50.1 | 3.1 |  |  | 403.8 | 356.4 | 468.9 | 391.1 | 338.9 | 474.9 | 470
3000.3 | 1300.3 | 189.4 | 75.76 | 88.5591 | 147.3 | 152.9 | 157 | 163.4 | 201.5 | 31.3 | 21 | 50.2 | 3.8 |  |  | 403.6 | 361.2 | 469.2 | 391.3 | 346.9 | 487.9 | 472.4
3001.3 | 1301.3 | 189.6 | 75.84 | 88.6526 | 147.2 | 153.2 | 156.7 | 163.7 | 204.7 | 31.4 | 21 | 50.4 | 3.5 |  |  | 403.3 | 376.6 | 467.8 | 391.6 | 360.6 | 488.8 | 469.4
3002.3 | 1302.3 | 186 | 74.4 | 86.9693 | 147.1 | 153.4 | 156.8 | 163.7 | 207.7 | 31.3 | 21 | 50.4 | 3.5 |  |  | 403.1 | 385.2 | 466.6 | 391.9 | 369.2 | 490.4 | 463.9
3003.3 | 1303.3 | 189 | 75.6 | 88.372 | 147.4 | 153.1 | 156.9 | 163.5 | 208.2 | 31.4 | 21 | 50.3 | 4.4 |  |  | 402.9 | 397 | 464.6 | 392.3 | 371.8 | 491.2 | 460.9
3004.3 | 1304.3 | 187.7 | 75.08 | 87.7642 | 147.7 | 152.7 | 157.2 | 163.2 | 208.7 | 31.5 | 21 | 50.3 | 4.2 |  |  | 402.6 | 414.9 | 463.1 | 392.9 | 380.5 | 491.1 | 457.6
3005.3 | 1305.3 | 188.7 | 75.48 | 88.2318 | 148.1 | 152.8 | 157.4 | 163.2 | 210.6 | 31.5 | 21 | 50.2 | 3.7 |  |  | 402.6 | 432.9 | 460.4 | 393.4 | 391.1 | 488.1 | 456.1
3006.3 | 1306.3 | 188.5 | 75.4 | 88.1383 | 148.1 | 152.6 | 157.7 | 163.1 | 213.2 | 31.4 | 21 | 50.3 | 3.6 |  |  | 402.6 | 433.6 | 459.5 | 394 | 389.9 | 482.1 | 455.1
3007.3 | 1307.3 | 187.1 | 74.84 | 87.4836 | 148.4 | 152 | 157.9 | 163.4 | 212.8 | 31.3 | 21 | 50.3 | 3.3 |  |  | 402.6 | 429.8 | 459 | 394.6 | 387.4 | 477.8 | 453.5
3008.3 | 1308.3 | 187.8 | 75.12 | 87.811 | 149.2 | 151.9 | 158.1 | 163.8 | 211.1 | 31.2 | 21 | 50.4 | 3.1 |  |  | 402.6 | 423.9 | 460.2 | 395.3 | 387.7 | 481.2 | 455.1
3009.3 | 1309.3 | 187 | 74.8 | 87.4369 | 149.6 | 151.4 | 158.2 | 163.8 | 210.5 | 31.2 | 21 | 50.5 | 4.2 |  |  | 402.8 | 428.4 | 461.6 | 395.9 | 393.6 | 483.8 | 456.1
3010.3 | 1310.3 | 183.8 | 73.52 | 85.9406 | 149.7 | 151.3 | 158.2 | 164 | 213.9 | 31.2 | 21 | 50.6 | 4.1 |  |  | 403 | 435.9 | 460.3 | 396.6 | 402.5 | 483.6 | 457.3
3011.3 | 1311.3 | 186.2 | 74.48 | 87.0628 | 149.7 | 151.8 | 158.3 | 164.3 | 215.6 | 31.1 | 21 | 50.7 | 4 |  |  | 403.2 | 436.2 | 459.2 | 397.2 | 406.7 | 483.8 | 457.5
3012.3 | 1312.3 | 186.4 | 74.56 | 87.1563 | 149.7 | 152.4 | 158.2 | 164.7 | 215 | 31 | 21 | 50.9 | 4.8 |  |  | 403.3 | 437.2 | 458.6 | 397.9 | 408 | 483.5 | 459
3013.3 | 1313.3 | 185.3 | 74.12 | 86.642 | 149.9 | 152.8 | 158.3 | 164.9 | 215.1 | 30.9 | 21 | 50.9 | 4.2 |  |  | 403.6 | 442 | 453.2 | 398.5 | 410.3 | 477.9 | 453.5
3014.3 | 1314.3 | 182.6 | 73.04 | 85.3796 | 149.9 | 153.1 | 158.6 | 164.6 | 215.3 | 30.9 | 21 | 50.8 | 3.1 |  |  | 403.8 | 439.5 | 444.5 | 399 | 406.6 | 469.1 | 447.7
3015.3 | 1315.3 | 187 | 74.8 | 87.4369 | 149.3 | 153.1 | 159.1 | 164.3 | 212.3 | 30.8 | 21 | 50.6 | 3.4 |  |  | 404.1 | 437.2 | 435.9 | 399.5 | 400.4 | 459.4 | 441.9
3016.3 | 1316.3 | 187.2 | 74.88 | 87.5304 | 148.8 | 153 | 159.2 | 163.9 | 210.9 | 30.8 | 21 | 50.5 | 3.3 |  |  | 404.1 | 440.7 | 432 | 400 | 398.4 | 455.2 | 440.9
3017.3 | 1317.3 | 185.5 | 74.2 | 86.7355 | 148.6 | 152.9 | 159.3 | 163.8 | 210.7 | 30.8 | 21 | 50.4 | 3.4 |  |  | 404.3 | 447.9 | 430.5 | 400.5 | 403.1 | 453.9 | 440.9
3018.3 | 1318.3 | 187.5 | 75 | 87.6707 | 148.7 | 152.6 | 159.4 | 163.6 | 211.8 | 30.8 | 21 | 50.4 | 3.2 |  |  | 404.6 | 449.4 | 427 | 401 | 408 | 455.3 | 440.8
3019.3 | 1319.3 | 187.5 | 75 | 87.6707 | 149 | 152.4 | 159.6 | 163.6 | 211.1 | 30.8 | 21 | 50.4 | 2.9 |  |  | 404.6 | 448.8 | 422.3 | 401.5 | 409.9 | 452.9 | 438.1
3020.3 | 1320.3 | 188 | 75.2 | 87.9045 | 149.2 | 152.5 | 159.8 | 163.7 | 210.6 | 30.8 | 21 | 50.4 | 3.4 |  |  | 404.6 | 447.7 | 423.5 | 401.9 | 412.1 | 451.8 | 438.5
3021.3 | 1321.3 | 187.8 | 75.12 | 87.811 | 149.1 | 152.4 | 160.2 | 163.8 | 209.6 | 30.7 | 21 | 50.4 | 3.6 |  |  | 404.7 | 446.6 | 423.5 | 402.2 | 409.4 | 448.4 | 437.6
3022.3 | 1322.3 | 186.9 | 74.76 | 87.3901 | 149.3 | 151.6 | 160.8 | 163.6 | 209.5 | 30.6 | 21 | 50.4 | 3.4 |  |  | 404.6 | 450.2 | 420.9 | 402.6 | 405.3 | 444.8 | 436.3
3023.3 | 1323.3 | 187.4 | 74.96 | 87.6239 | 149.6 | 151.4 | 161.2 | 163.6 | 210.6 | 30.6 | 21 | 50.4 | 2.6 |  |  | 404.5 | 450.1 | 421.2 | 403 | 396.6 | 438.1 | 432.7
3024.3 | 1324.3 | 186.6 | 74.64 | 87.2499 | 150 | 151.6 | 161.3 | 163.8 | 211.1 | 30.6 | 21 | 50.3 | 2.6 |  |  | 404.3 | 444.7 | 423.1 | 403.3 | 390 | 435.2 | 433.5
3025.3 | 1325.3 | 187.7 | 75.08 | 87.7642 | 150.3 | 151.9 | 161.3 | 164 | 209.9 | 30.7 | 21 | 50.3 | 3 |  |  | 404.2 | 447.7 | 426.6 | 403.7 | 390.7 | 436 | 436.8
3026.3 | 1326.3 | 187.7 | 75.08 | 87.7642 | 150.4 | 152.3 | 161.1 | 164.1 | 208.8 | 30.8 | 21 | 50.2 | 3.7 |  |  | 404.1 | 448.1 | 426.9 | 404.1 | 388.4 | 432.8 | 434.7
3027.3 | 1327.3 | 187.5 | 75 | 87.6707 | 150.7 | 152.7 | 160.9 | 163.9 | 208.8 | 30.9 | 21 | 50.2 | 3.7 |  |  | 404.1 | 457.7 | 429.7 | 404.4 | 390.9 | 432.9 | 435.4
3028.3 | 1328.3 | 187.2 | 74.88 | 87.5304 | 150.5 | 152.9 | 161.2 | 163.9 | 210.9 | 31 | 21 | 50.3 | 2.9 |  |  | 404.1 | 462.3 | 429.8 | 404.8 | 393.9 | 437.3 | 435.6
3029.3 | 1329.3 | 187.2 | 74.88 | 87.5304 | 150.5 | 153.3 | 161.5 | 163.9 | 211.1 | 31 | 21 | 50.3 | 3 |  |  | 404.1 | 461.6 | 427.7 | 405.3 | 393.9 | 438.8 | 432.9
3030.3 | 1330.3 | 185.8 | 74.32 | 86.8758 | 150.4 | 154.1 | 161.8 | 163.8 | 211.4 | 31 | 21 | 50.3 | 3.2 |  |  | 404.3 | 457.5 | 428.6 | 405.6 | 389.6 | 437.9 | 431.1
3031.3 | 1331.3 | 186.8 | 74.72 | 87.3434 | 150.3 | 154.4 | 162.1 | 163.9 | 209 | 31 | 21 | 50.4 | 3.7 |  |  | 404.3 | 460.4 | 429.4 | 406 | 389.7 | 437 | 429.9
3032.3 | 1332.3 | 185.3 | 74.12 | 86.642 | 150.5 | 154.3 | 162.3 | 164 | 208.4 | 31.1 | 21 | 50.3 | 3.4 |  |  | 404.5 | 461.5 | 429 | 406.3 | 386.6 | 433.1 | 427.5
3033.3 | 1333.3 | 187.4 | 74.96 | 87.6239 | 150.7 | 154 | 162.3 | 163.9 | 208.1 | 31.2 | 21 | 50.3 | 3.4 |  |  | 404.5 | 458.4 | 434.9 | 406.5 | 383.7 | 432.7 | 427.6
3034.3 | 1334.3 | 187.9 | 75.16 | 87.8577 | 151.2 | 153.9 | 162.5 | 163.7 | 207.8 | 31.3 | 21 | 50.3 | 2.9 |  |  | 404.6 | 457.1 | 443.7 | 406.9 | 385.8 | 437.9 | 434.5
3035.3 | 1335.3 | 186.3 | 74.52 | 87.1096 | 151.6 | 154.1 | 162.7 | 163.6 | 207.1 | 31.3 | 21 | 50.3 | 2.7 |  |  | 404.9 | 450.7 | 448.3 | 407.2 | 385.1 | 442.1 | 438.3
3036.3 | 1336.3 | 186.3 | 74.52 | 87.1096 | 151.8 | 154.5 | 162.8 | 163.6 | 206.8 | 31.3 | 21 | 50.3 | 2.9 |  |  | 405.1 | 444.5 | 453.6 | 407.6 | 383.1 | 444.9 | 441.6
3037.3 | 1337.3 | 187.5 | 75 | 87.6707 | 151.9 | 154.8 | 162.8 | 163.4 | 205.8 | 31.4 | 21 | 50.3 | 3.1 |  |  | 405.3 | 440.7 | 454.9 | 407.8 | 381.8 | 443.2 | 441.9
3038.3 | 1338.3 | 186.1 | 74.44 | 87.0161 | 152.1 | 154.8 | 162.7 | 163.3 | 204.5 | 31.3 | 21 | 50.3 | 3.9 |  |  | 405.5 | 441 | 456.9 | 408.1 | 382.5 | 445.1 | 441.3
3039.3 | 1339.3 | 187.5 | 75 | 87.6707 | 152.1 | 155.1 | 162.4 | 163.2 | 204.8 | 31.3 | 21 | 50.4 | 4 |  |  | 405.8 | 436.5 | 461 | 408.5 | 382.4 | 446.9 | 445.7
3040.3 | 1340.3 | 186.8 | 74.72 | 87.3434 | 152.1 | 155.3 | 162.4 | 163.2 | 204.2 | 31.2 | 21 | 50.5 | 3.6 |  |  | 406.1 | 437.8 | 464.5 | 408.8 | 381.3 | 448.5 | 446.4
3041.3 | 1341.3 | 186.6 | 74.64 | 87.2499 | 151.9 | 155.1 | 162.1 | 163 | 203.7 | 31.2 | 21 | 50.5 | 3.3 |  |  | 406.4 | 437.9 | 460.2 | 409.1 | 376.3 | 441.8 | 440.3
3042.3 | 1342.3 | 186.8 | 74.72 | 87.3434 | 151.9 | 154.8 | 162 | 162.9 | 203.5 | 31.3 | 21 | 50.5 | 3.3 |  |  | 406.6 | 438.3 | 452.6 | 409.2 | 373.4 | 435.9 | 433.4
3043.3 | 1343.3 | 185.9 | 74.36 | 86.9226 | 152 | 154.8 | 162 | 162.8 | 203.3 | 31.4 | 21 | 50.4 | 3 |  |  | 406.9 | 438.3 | 444.9 | 409.5 | 371.5 | 430.5 | 428.9
3044.3 | 1344.3 | 190.7 | 76.28 | 89.1669 | 152.2 | 154.7 | 161.8 | 162.7 | 203.2 | 31.5 | 21 | 50.4 | 2.7 |  |  | 407.2 | 442.5 | 443.9 | 409.7 | 372 | 429.9 | 427.9
3045.3 | 1345.3 | 192.7 | 77.08 | 90.1021 | 152 | 154.6 | 161.7 | 162.9 | 203.7 | 31.5 | 21 | 50.4 | 2.6 |  |  | 407.4 | 436.6 | 445.1 | 410 | 370.2 | 433 | 431.3
3046.3 | 1346.3 | 193.5 | 77.4 | 90.4761 | 152.2 | 154.5 | 160.9 | 162.9 | 203.7 | 31.4 | 21 | 50.5 | 2.7 |  |  | 407.5 | 431.3 | 445.2 | 410.3 | 369 | 433.2 | 434.8
3047.3 | 1347.3 | 197 | 78.8 | 92.1127 | 152.4 | 154.5 | 160.2 | 162.9 | 204.2 | 31.2 | 21 | 50.5 | 3.1 |  |  | 407.7 | 428.1 | 446.1 | 410.6 | 370.2 | 446.7 | 439.3
3048.3 | 1348.3 | 191.9 | 76.76 | 89.728 | 152.2 | 154.6 | 160.1 | 162.8 | 205.6 | 31.1 | 21 | 50.6 | 3.3 |  |  | 407.7 | 430.5 | 447.6 | 411 | 377.6 | 455.2 | 444.1
3049.3 | 1349.3 | 190 | 76 | 88.8396 | 152 | 154.5 | 160.1 | 162.8 | 205.7 | 31.1 | 21 | 50.7 | 3.3 |  |  | 407.8 | 427.3 | 449.8 | 411.4 | 379.1 | 456.5 | 445
3050.3 | 1350.3 | 189.9 | 75.96 | 88.7929 | 152 | 154.4 | 160.3 | 162.7 | 204.5 | 31 | 21 | 50.8 | 3.7 |  |  | 407.8 | 417.5 | 449.9 | 411.6 | 371.6 | 452.7 | 445.1
3051.3 | 1351.3 | 190.8 | 76.32 | 89.2137 | 152 | 154.5 | 160.4 | 162.7 | 202.3 | 31.2 | 21 | 50.8 | 3.4 |  |  | 407.7 | 411.9 | 453.2 | 411.8 | 366.9 | 449.7 | 444.4
3052.3 | 1352.3 | 192.4 | 76.96 | 89.9618 | 151.9 | 154.6 | 160.5 | 162.7 | 201.1 | 31.4 | 21 | 50.8 | 3 |  |  | 407.7 | 409.3 | 459.6 | 412 | 364.4 | 450.7 | 447.5
3053.3 | 1353.3 | 193.9 | 77.56 | 90.6632 | 151.5 | 154.6 | 160.7 | 162.7 | 201.1 | 31.5 | 21 | 50.8 | 2.6 |  |  | 407.7 | 416.3 | 465.1 | 412.2 | 368.5 | 453.3 | 448.8
3054.3 | 1354.3 | 194.6 | 77.84 | 90.9905 | 151.3 | 154.7 | 160.5 | 162.9 | 202.2 | 31.5 | 21 | 50.8 | 3.5 |  |  | 407.6 | 407.7 | 466.5 | 412.5 | 363.4 | 452.7 | 450.1
3055.3 | 1355.3 | 195.6 | 78.24 | 91.4581 | 150.8 | 155.2 | 160.3 | 162.6 | 200.3 | 31.5 | 21 | 50.8 | 4 |  |  | 407.5 | 398.5 | 470.7 | 412.5 | 358.5 | 453.4 | 452.2
3056.3 | 1356.3 | 198.1 | 79.24 | 92.627 | 150.1 | 155.4 | 160 | 162.8 | 200.1 | 31.5 | 21 | 50.8 | 3.2 |  |  | 407.3 | 398.1 | 479.9 | 412.7 | 359.4 | 461.2 | 460.8
3057.3 | 1357.3 | 201 | 80.4 | 93.983 | 149.6 | 155.8 | 159.7 | 163 | 202.1 | 31.6 | 21 | 50.9 | 3.2 |  |  | 407.2 | 404 | 480.7 | 413 | 362.2 | 461.5 | 460.1
3058.3 | 1358.3 | 202.6 | 81.04 | 94.7311 | 149.1 | 155.8 | 159 | 162.9 | 203 | 31.6 | 21 | 50.9 | 3.7 |  |  | 407.1 | 404.9 | 482.1 | 413.3 | 364.2 | 460.4 | 455.1
3059.3 | 1359.3 | 205.4 | 82.16 | 96.0403 | 148.7 | 155.7 | 158.2 | 162.7 | 203.1 | 31.6 | 21 | 51 | 3.4 |  |  | 406.9 | 406.7 | 481.5 | 413.6 | 367.5 | 459.1 | 453.5
3060.3 | 1360.3 | 207.3 | 82.92 | 96.9287 | 148.9 | 155.8 | 158.2 | 162.8 | 203 | 31.6 | 21 | 51.1 | 3.5 |  |  | 406.9 | 405.9 | 482.8 | 414 | 368.6 | 461.2 | 453
3061.3 | 1361.3 | 209.1 | 83.64 | 97.7703 | 149 | 156 | 158.7 | 162.8 | 206.3 | 31.3 | 21 | 51.2 | 3.5 |  |  | 406.9 | 413.4 | 484 | 414.5 | 377.5 | 465.2 | 454.3
3062.3 | 1362.3 | 211.8 | 84.72 | 99.0328 | 148.9 | 155.9 | 158.8 | 162.8 | 212.6 | 31.3 | 21 | 51.3 | 3.2 |  |  | 407 | 421.5 | 484.9 | 415.1 | 386.8 | 473.1 | 454.3
3063.3 | 1363.3 | 214.2 | 85.68 | 100.155 | 149.4 | 155.9 | 158.7 | 162.7 | 215.7 | 31.5 | 21 | 51.2 | 3.2 |  |  | 407.1 | 428.3 | 482 | 415.8 | 397.3 | 478.4 | 454.7
3064.3 | 1364.3 | 215.9 | 86.36 | 100.9499 | 149.6 | 155.7 | 158.6 | 162.7 | 216 | 31.8 | 21 | 51.1 | 3.3 |  |  | 407.2 | 435.7 | 475.2 | 416.5 | 405.5 | 476.5 | 449.7
3065.3 | 1365.3 | 216.1 | 86.44 | 101.0434 | 149.6 | 155.4 | 158.5 | 162.8 | 217.1 | 32 | 21 | 51.1 | 3.3 |  |  | 407.4 | 447.4 | 467.4 | 416.9 | 408.5 | 472.3 | 445.1
3066.3 | 1366.3 | 217.4 | 86.96 | 101.6512 | 149.4 | 155.6 | 158.3 | 163.4 | 216.4 | 32 | 21 | 51.2 | 3 |  |  | 407.5 | 456.1 | 459.9 | 417.3 | 408 | 466 | 439.6
3067.3 | 1367.3 | 219.1 | 87.64 | 102.4461 | 149.3 | 155.9 | 158.1 | 163.8 | 215.8 | 32 | 21 | 51.3 | 3.9 |  |  | 407.7 | 456 | 455.8 | 417.7 | 403 | 461.2 | 437
3068.3 | 1368.3 | 220.8 | 88.32 | 103.241 | 149.5 | 156.6 | 158.4 | 164.1 | 214.8 | 31.9 | 21 | 51.3 | 4.5 |  |  | 407.8 | 458.3 | 453.6 | 418.1 | 400.8 | 460 | 438.8
3069.3 | 1369.3 | 222.1 | 88.84 | 103.8488 | 150.4 | 157 | 158.9 | 164.5 | 213.7 | 31.7 | 21 | 51.3 | 4 |  |  | 408 | 462.2 | 450.5 | 418.6 | 405.8 | 461.3 | 438.7
3070.3 | 1370.3 | 223.9 | 89.56 | 104.6905 | 150.7 | 157 | 159.5 | 165.2 | 214.8 | 31.6 | 21 | 51.3 | 4 |  |  | 408.1 | 463.9 | 450.1 | 419.2 | 405.4 | 460.3 | 438.5
3071.3 | 1371.3 | 226.1 | 90.44 | 105.7191 | 150.9 | 156.9 | 160.1 | 165.5 | 215.4 | 31.5 | 21 | 51.3 | 5.5 |  |  | 408.2 | 468 | 455.1 | 419.8 | 403.5 | 465.8 | 441.9
3072.3 | 1372.3 | 228.3 | 91.32 | 106.7478 | 151.2 | 156.7 | 160.6 | 165.8 | 215.7 | 31.5 | 21 | 51.3 | 5.9 |  |  | 408.4 | 462.9 | 458.5 | 420.3 | 396.7 | 461 | 441.5
3073.3 | 1373.3 | 229.8 | 91.92 | 107.4492 | 151.4 | 156.2 | 161.1 | 166.4 | 215.8 | 31.5 | 21 | 51.3 | 3.9 |  |  | 408.5 | 461.7 | 464.2 | 420.8 | 392.7 | 465.7 | 445.9
3074.3 | 1374.3 | 230.6 | 92.24 | 107.8232 | 151.7 | 155.6 | 161.4 | 166.6 | 216.2 | 31.6 | 21 | 51.3 | 4.5 |  |  | 408.7 | 463.3 | 471.6 | 421.3 | 392.5 | 471 | 452.3
3075.3 | 1375.3 | 232.3 | 92.92 | 108.6181 | 151.8 | 155.6 | 161.5 | 166.7 | 217.6 | 31.6 | 21 | 51.4 | 5.3 |  |  | 408.9 | 474.1 | 476.9 | 422.2 | 407.4 | 480.5 | 455.2
3076.3 | 1376.3 | 234.2 | 93.68 | 109.5065 | 152 | 155.7 | 161.6 | 166.8 | 221.8 | 31.6 | 21 | 51.4 | 4.2 |  |  | 409.2 | 489.9 | 475.6 | 423.1 | 420 | 489.8 | 454.1
3077.3 | 1377.3 | 236.7 | 94.68 | 110.6755 | 152 | 156.1 | 161.8 | 167.1 | 224.3 | 31.7 | 21 | 51.4 | 3.7 |  |  | 409.6 | 494.7 | 473.6 | 423.9 | 426.4 | 489.3 | 450.5
3078.3 | 1378.3 | 236.6 | 94.64 | 110.6287 | 152.1 | 156.7 | 162.5 | 167.3 | 222.9 | 31.7 | 21 | 51.5 | 3.8 |  |  | 410.1 | 492.2 | 468 | 424.4 | 421.7 | 480.2 | 443.6
3079.3 | 1379.3 | 236.7 | 94.68 | 110.6755 | 152.1 | 157.3 | 162.8 | 167.8 | 221.1 | 31.8 | 21 | 51.5 | 4.9 |  |  | 410.5 | 489.8 | 465 | 424.9 | 418.6 | 474.4 | 439.8
3080.3 | 1380.3 | 240 | 96 | 112.2185 | 153.1 | 157.6 | 163.2 | 168.2 | 220.9 | 31.8 | 21 | 51.5 | 3.9 |  |  | 411.1 | 488.9 | 472.3 | 425.5 | 417.5 | 471.2 | 443.1
3081.3 | 1381.3 | 241.9 | 96.76 | 113.1069 | 154.4 | 158.1 | 163.7 | 168.5 | 223.5 | 31.8 | 21 | 51.5 | 4 |  |  | 411.7 | 480.2 | 479.3 | 426.1 | 408.7 | 463.7 | 445.1
3082.3 | 1382.3 | 242.9 | 97.16 | 113.5744 | 154.5 | 158 | 164.1 | 168.8 | 223.3 | 31.9 | 21 | 51.4 | 5.6 |  |  | 412.3 | 470.8 | 483.5 | 426.3 | 402.9 | 459.9 | 449.3
3083.3 | 1383.3 | 243.6 | 97.44 | 113.9017 | 154.6 | 157.8 | 164.1 | 169.2 | 221.5 | 31.9 | 21 | 51.3 | 4.5 |  |  | 412.9 | 464.8 | 490.9 | 426.5 | 401.1 | 465.2 | 459.6
3084.3 | 1384.3 | 244.9 | 97.96 | 114.5096 | 154.9 | 157.9 | 164.2 | 169.6 | 218.9 | 31.9 | 21 | 51.2 | 4 |  |  | 413.5 | 456.9 | 491.7 | 426.9 | 398.7 | 472.7 | 464.9
3085.3 | 1385.3 | 247.3 | 98.92 | 115.6318 | 154.9 | 159 | 164.5 | 169.8 | 219.6 | 31.9 | 21 | 51.3 | 4.1 |  |  | 414.2 | 452.1 | 496.9 | 427.3 | 393.6 | 476 | 469.1
3086.3 | 1386.3 | 249.3 | 99.72 | 116.5669 | 154.6 | 160 | 164.1 | 170.1 | 220.3 | 31.8 | 21 | 51.5 | 3.8 |  |  | 414.8 | 447.3 | 500.5 | 427.7 | 388.8 | 483.4 | 473.4
3087.3 | 1387.3 | 251.3 | 100.52 | 117.5021 | 154.6 | 160.4 | 164.6 | 170.5 | 220.2 | 31.7 | 21 | 51.6 | 4.6 |  |  | 415.5 | 446.1 | 510.8 | 428.4 | 390.6 | 492.4 | 476.5
3088.3 | 1388.3 | 254.1 | 101.64 | 118.8113 | 155 | 161.3 | 165.1 | 171 | 222.2 | 31.6 | 21 | 51.7 | 4 |  |  | 416 | 451.5 | 513 | 429.2 | 397.2 | 502.1 | 480.4
3089.3 | 1389.3 | 256.7 | 102.68 | 120.027 | 155.2 | 161.7 | 166.2 | 171.4 | 225.7 | 31.4 | 21 | 51.7 | 3.5 |  |  | 416.7 | 458.8 | 512 | 430.2 | 404.9 | 508 | 480.9
3090.3 | 1390.3 | 259.1 | 103.64 | 121.1492 | 155.1 | 161.3 | 166.9 | 172.3 | 226.8 | 31.2 | 21 | 51.8 | 3.4 |  |  | 417.4 | 456.3 | 512.2 | 431 | 410.1 | 510.6 | 480.9
3091.3 | 1391.3 | 261.2 | 104.48 | 122.1311 | 155.1 | 161.1 | 167.6 | 173 | 225.7 | 31.1 | 21 | 51.9 | 3.6 |  |  | 417.9 | 454.5 | 514.1 | 431.8 | 408.3 | 509.6 | 479.9
3092.3 | 1392.3 | 262.7 | 105.08 | 122.8325 | 155.7 | 160.9 | 168.2 | 173.1 | 225.2 | 31 | 21 | 52 | 2.8 |  |  | 418.6 | 455.4 | 523.1 | 432.5 | 405.9 | 506.8 | 477.8
3093.3 | 1393.3 | 264.3 | 105.72 | 123.5806 | 156.6 | 162 | 168.8 | 173 | 226.5 | 30.9 | 21 | 52 | 3.1 |  |  | 419.1 | 451.1 | 526.4 | 433.3 | 400 | 506.4 | 479.8
3094.3 | 1394.3 | 267.9 | 107.16 | 125.2639 | 156.7 | 163.8 | 169.7 | 173 | 225.2 | 30.8 | 21 | 52.2 | 3.9 |  |  | 419.7 | 439.5 | 521.6 | 433.7 | 391.4 | 501.5 | 481
3095.3 | 1395.3 | 272 | 108.8 | 127.1809 | 156.9 | 165.1 | 170.6 | 173.8 | 222.5 | 30.8 | 21 | 52.3 | 3.6 |  |  | 420.3 | 431.2 | 524.3 | 434.2 | 386.4 | 503.2 | 488.4
3096.3 | 1396.3 | 274.4 | 109.76 | 128.3031 | 157.2 | 165.5 | 171.3 | 174.4 | 222.7 | 30.8 | 21 | 52.4 | 3.2 |  |  | 421 | 436.1 | 529.4 | 434.8 | 388.2 | 511.7 | 493.9
3097.3 | 1397.3 | 277 | 110.8 | 129.5188 | 157.5 | 166.1 | 172.3 | 174.7 | 227.1 | 31 | 21 | 52.3 | 3.1 |  |  | 421.6 | 442.7 | 534.6 | 435.6 | 405.7 | 528.8 | 502.8
3098.3 | 1398.3 | 277.7 | 111.08 | 129.8461 | 157.8 | 166.7 | 172.9 | 175.3 | 230.5 | 31.2 | 21 | 52.2 | 3.4 |  |  | 422.3 | 465.6 | 536.2 | 436.7 | 429.5 | 534.8 | 501.7
3099.3 | 1399.3 | 278.2 | 111.28 | 130.0799 | 158.2 | 167.1 | 173.4 | 175.6 | 235.6 | 31.3 | 21 | 52.1 | 3.6 |  |  | 423 | 478.6 | 543.2 | 437.8 | 443.1 | 543.7 | 502.2
3100.3 | 1400.3 | 277.6 | 111.04 | 129.7994 | 158.7 | 168 | 173.9 | 176 | 237.3 | 31.3 | 21 | 52.1 | 3.4 |  |  | 423.6 | 487.8 | 543.2 | 439 | 455.6 | 546.8 | 502.2
3101.3 | 1401.3 | 277.6 | 111.04 | 129.7994 | 159.1 | 168.7 | 174.4 | 176.8 | 238 | 31.4 | 21 | 52.1 | 4 |  |  | 424.5 | 486.3 | 539.7 | 440.1 | 460.3 | 550.9 | 501.1
3102.3 | 1402.3 | 277.8 | 111.12 | 129.8929 | 160.1 | 168.7 | 174.9 | 178.2 | 239.7 | 31.5 | 21 | 52.2 | 4.1 |  |  | 425.4 | 485.7 | 532.8 | 441.1 | 462.8 | 554.5 | 497.9
3103.3 | 1403.3 | 278.4 | 111.36 | 130.1734 | 161 | 169.1 | 174.8 | 179.5 | 243.4 | 31.7 | 21 | 52.3 | 3.4 |  |  | 426.3 | 492.3 | 535 | 442.4 | 467.2 | 565.3 | 506.8
3104.3 | 1404.3 | 279.5 | 111.8 | 130.6878 | 161.1 | 169.5 | 174.8 | 180.7 | 245.4 | 31.8 | 21 | 52.4 | 3.1 |  |  | 427.2 | 499.3 | 541.6 | 443.5 | 469.4 | 568.3 | 517.1
3105.3 | 1405.3 | 279.9 | 111.96 | 130.8748 | 161.8 | 170.7 | 174.2 | 181.6 | 247.3 | 31.9 | 21 | 52.4 | 3.1 |  |  | 428.3 | 510.6 | 546 | 444.5 | 478.7 | 573.3 | 518.8
3106.3 | 1406.3 | 280 | 112 | 130.9215 | 162.4 | 172.3 | 173.3 | 182.4 | 251.4 | 31.9 | 21 | 52.4 | 3.2 |  |  | 429.3 | 522 | 545.1 | 445.7 | 486.4 | 576.6 | 519.3
3107.3 | 1407.3 | 279.8 | 111.92 | 130.828 | 163 | 173.8 | 172.9 | 182.9 | 255.9 | 32 | 20.9 | 52.4 | 3.7 |  |  | 430.4 | 545.7 | 550 | 447.2 | 504.3 | 579 | 518.1
3108.3 | 1408.3 | 280 | 112 | 130.9215 | 163.9 | 175 | 173.5 | 183.9 | 258.7 | 32 | 20.9 | 52.5 | 3.5 |  |  | 431.5 | 562.7 | 548.3 | 448.7 | 517.5 | 580.1 | 513.3
3109.3 | 1409.3 | 281.3 | 112.52 | 131.5294 | 164.4 | 174.8 | 174.5 | 184.8 | 263.1 | 31.9 | 20.9 | 52.6 | 4.1 |  |  | 432.7 | 587.1 | 552.1 | 450.4 | 537.2 | 586.5 | 516.1
3110.3 | 1410.3 | 281.8 | 112.72 | 131.7632 | 164.6 | 175 | 175.4 | 185.1 | 270.8 | 31.9 | 20.9 | 52.8 | 4.3 |  |  | 434 | 606.5 | 553.7 | 452 | 554.3 | 582.3 | 513.5
3111.3 | 1411.3 | 281.9 | 112.76 | 131.8099 | 165.1 | 175.6 | 175.1 | 185.2 | 274 | 31.9 | 20.9 | 52.9 | 3.7 |  |  | 435.4 | 620.6 | 546.9 | 453.4 | 565.3 | 572.8 | 506.3
3112.3 | 1412.3 | 281.7 | 112.68 | 131.7164 | 165.6 | 176.2 | 175.5 | 185.4 | 275 | 31.8 | 20.9 | 53 | 3.9 |  |  | 436.9 | 634.2 | 548.7 | 455 | 578.6 | 572.1 | 509.7
3113.3 | 1413.3 | 282.3 | 112.92 | 131.997 | 165.9 | 176.9 | 176.3 | 185.9 | 277.4 | 31.7 | 20.9 | 53.2 | 3.5 |  |  | 438.7 | 657.3 | 558.4 | 457 | 593.8 | 578 | 519.9
3114.3 | 1414.3 | 282.7 | 113.08 | 132.184 | 166.9 | 177.6 | 176.5 | 186.5 | 282.4 | 31.7 | 20.9 | 53.4 | 3 |  |  | 440.3 | 678.2 | 569.6 | 459.3 | 616.4 | 586 | 524.3
3115.3 | 1415.3 | 283.3 | 113.32 | 132.4646 | 168.2 | 177.7 | 177.7 | 187.8 | 289.1 | 31.6 | 21 | 53.4 | 2 |  |  | 442 | 697.9 | 576.5 | 461.3 | 640.3 | 588.8 | 528.5
3116.3 | 1416.3 | 283.9 | 113.56 | 132.7451 | 169.1 | 178.8 | 179.2 | 189 | 294 | 31.6 | 21 | 53.5 | 2.1 |  |  | 443.8 | 698.8 | 580.5 | 463.1 | 657.1 | 588.5 | 528.2
3117.3 | 1417.3 | 283.5 | 113.4 | 132.5581 | 169.8 | 179.6 | 180.4 | 190.1 | 296.1 | 31.5 | 21 | 53.6 | 2.4 |  |  | 445.7 | 704.5 | 586.5 | 464.8 | 671.3 | 593.6 | 528.1
3118.3 | 1418.3 | 283.9 | 113.56 | 132.7451 | 170.5 | 180 | 181.7 | 192.1 | 299.6 | 31.5 | 20.9 | 53.7 | 2.9 |  |  | 447.4 | 706.7 | 594 | 466.5 | 682.7 | 595.2 | 532
3119.3 | 1419.3 | 284.2 | 113.68 | 132.8854 | 171.5 | 180.7 | 183 | 193.3 | 302.3 | 31.5 | 20.9 | 53.8 | 3.5 |  |  | 449.3 | 711.5 | 595.9 | 468.1 | 695.3 | 598.2 | 535.7
3120.3 | 1420.3 | 284.5 | 113.8 | 133.0256 | 171.8 | 180.9 | 184.8 | 194.1 | 301.4 | 31.3 | 21 | 53.9 | 3.8 |  |  | 451.3 | 700.7 | 592.4 | 469.4 | 692 | 591.5 | 534.1
3121.3 | 1421.3 | 284.6 | 113.84 | 133.0724 | 172.8 | 180.6 | 186.5 | 195.1 | 302.2 | 31.1 | 20.9 | 54.1 | 3.4 |  |  | 453.1 | 690.9 | 589.8 | 470.5 | 679.8 | 582.8 | 534.5
3122.3 | 1422.3 | 284.8 | 113.92 | 133.1659 | 173.4 | 180.4 | 188 | 196.5 | 298.9 | 31.1 | 20.9 | 54.2 | 3.1 |  |  | 455 | 689.8 | 591.5 | 471.6 | 680.2 | 590.8 | 543.6
3123.3 | 1423.3 | 285.8 | 114.32 | 133.6335 | 173.9 | 180.7 | 189 | 197.8 | 297.5 | 31.4 | 20.9 | 54.2 | 3 |  |  | 456.9 | 682.7 | 591 | 472.3 | 678.9 | 595.5 | 549.9
3124.3 | 1424.3 | 285.6 | 114.24 | 133.54 | 174.3 | 181.3 | 189.8 | 199 | 296.9 | 31.5 | 20.9 | 54.3 | 3 |  |  | 458.4 | 677.6 | 594.4 | 472.6 | 674.5 | 592.6 | 552.3
3125.3 | 1425.3 | 285.9 | 114.36 | 133.6803 | 175.2 | 182.7 | 190.7 | 200 | 298.3 | 31.5 | 20.9 | 54.4 | 3.1 |  |  | 459.7 | 679.6 | 594.9 | 473 | 683.5 | 595 | 551.6
3126.3 | 1426.3 | 286.8 | 114.72 | 134.1011 | 176.4 | 183.5 | 191.7 | 200.3 | 301.8 | 31.6 | 20.9 | 54.5 | 3.3 |  |  | 460.8 | 691.5 | 594.8 | 473.7 | 701.1 | 601.4 | 547.4
3127.3 | 1427.3 | 287 | 114.8 | 134.1946 | 176.9 | 183.4 | 193.2 | 200.8 | 306.3 | 31.6 | 20.9 | 54.7 | 2.7 |  |  | 461.8 | 699.9 | 593.1 | 474.6 | 707 | 607.3 | 546.4
3128.3 | 1428.3 | 287.3 | 114.92 | 134.3349 | 177.6 | 183.1 | 193.8 | 202.1 | 306.3 | 31.7 | 20.9 | 54.7 | 2.2 |  |  | 462.8 | 707.2 | 590.8 | 474.9 | 708.7 | 606.3 | 546.1
3129.3 | 1429.3 | 287.5 | 115 | 134.4284 | 178.2 | 183.9 | 194.4 | 202.7 | 307.5 | 31.8 | 20.9 | 54.8 | 2.3 |  |  | 463.6 | 709.8 | 585.9 | 475 | 710.8 | 610.8 | 545.7
3130.3 | 1430.3 | 287.6 | 115.04 | 134.4751 | 179.2 | 185.1 | 195.7 | 203.3 | 305.2 | 31.8 | 20.9 | 54.9 | 2.4 |  |  | 464.5 | 715.5 | 580.1 | 475.2 | 717.2 | 616.8 | 546.4
3131.3 | 1431.3 | 288.2 | 115.28 | 134.7557 | 180.1 | 185.1 | 196.7 | 204.5 | 307.9 | 31.8 | 20.9 | 55 | 2.3 |  |  | 465.4 | 716.9 | 577.2 | 475.3 | 720.8 | 623.1 | 549.9
3132.3 | 1432.3 | 288.8 | 115.52 | 135.0362 | 180.6 | 184.3 | 197.4 | 205.5 | 312.7 | 32 | 20.9 | 55.1 | 2 |  |  | 466.2 | 710.7 | 579.9 | 475.2 | 717.3 | 626.1 | 554.7
3133.3 | 1433.3 | 289 | 115.6 | 135.1297 | 181 | 184.2 | 199 | 206.2 | 311.3 | 32 | 20.9 | 55.1 | 1.9 |  |  | 466.6 | 708.7 | 581 | 475.1 | 712.6 | 626.8 | 556.5
3134.3 | 1434.3 | 289.1 | 115.64 | 135.1765 | 181.5 | 184.1 | 200.3 | 207.1 | 312.2 | 32 | 20.9 | 55.1 | 1.8 |  |  | 467.2 | 714.2 | 585 | 475.6 | 715.8 | 629.6 | 558.5
3135.3 | 1435.3 | 289.6 | 115.84 | 135.4103 | 182.2 | 185.2 | 200.6 | 207.1 | 316.5 | 32 | 20.9 | 55.2 | 2.6 |  |  | 467.5 | 713.5 | 587.2 | 476.2 | 721.9 | 626.4 | 556.8
3136.3 | 1436.3 | 289.6 | 115.84 | 135.4103 | 182 | 186.4 | 200.9 | 206.9 | 326.8 | 32 | 20.9 | 55.5 | 3.4 |  |  | 467.9 | 723.1 | 588.9 | 477.1 | 724 | 627.8 | 558.1
3137.3 | 1437.3 | 289.8 | 115.92 | 135.5038 | 181.9 | 187.9 | 201.3 | 207.5 | 329.3 | 32 | 20.9 | 55.8 | 2.9 |  |  | 468.2 | 723.9 | 588.8 | 478 | 721.4 | 635.5 | 563.4
3138.3 | 1438.3 | 290.1 | 116.04 | 135.6441 | 183.4 | 189.2 | 201.9 | 208 | 328.4 | 32 | 20.9 | 56 | 2.2 |  |  | 468.7 | 725 | 587.8 | 478.8 | 722.7 | 634.6 | 564.4
3139.3 | 1439.3 | 289.8 | 115.92 | 135.5038 | 185.1 | 189.9 | 202.5 | 208.4 | 328.3 | 32 | 20.9 | 56.1 | 2.6 |  |  | 469 | 727.6 | 596.4 | 479.5 | 726.2 | 638.9 | 571.2
3140.3 | 1440.3 | 288.7 | 115.48 | 134.9895 | 185.9 | 189.8 | 204.2 | 209.2 | 330.7 | 32 | 20.9 | 56.3 | 2.8 |  |  | 469.5 | 725.4 | 605.6 | 480.6 | 725.3 | 639.1 | 577.9
3141.3 | 1441.3 | 284.9 | 113.96 | 133.2127 | 186.8 | 190.8 | 205.3 | 209.9 | 328.9 | 32.1 | 20.9 | 56.3 | 3 |  |  | 469.9 | 724.5 | 602.6 | 481 | 718.9 | 637.2 | 578.8
3142.3 | 1442.3 | 286.7 | 114.68 | 134.0543 | 187.8 | 191.8 | 205.9 | 210.6 | 327.5 | 32.1 | 20.9 | 56.3 | 3.1 |  |  | 470.4 | 720.9 | 601.7 | 481.2 | 721.4 | 640.1 | 581.9
3143.3 | 1443.3 | 287.8 | 115.12 | 134.5686 | 188.5 | 192.8 | 206.7 | 210.7 | 326.6 | 32.2 | 20.9 | 56.3 | 2.6 |  |  | 471 | 722.1 | 597.7 | 481.7 | 730.5 | 643.9 | 579.4
3144.3 | 1444.3 | 289.6 | 115.84 | 135.4103 | 188.9 | 193.5 | 207.2 | 211.2 | 330.7 | 32.3 | 20.9 | 56.2 | 2.7 |  |  | 471.7 | 730 | 602.6 | 482.3 | 740 | 649.2 | 578.9
3145.3 | 1445.3 | 290.2 | 116.08 | 135.6908 | 189 | 194 | 207.8 | 212.1 | 333.3 | 32.5 | 20.9 | 56.2 | 3.3 |  |  | 472.3 | 735.8 | 605.2 | 482.9 | 741.4 | 646.3 | 576.5
3146.3 | 1446.3 | 290.3 | 116.12 | 135.7376 | 189.1 | 195 | 208.2 | 212.6 | 333.9 | 32.6 | 20.9 | 56.2 | 3.2 |  |  | 473 | 741.5 | 608.5 | 483.3 | 741.5 | 647 | 576
3147.3 | 1447.3 | 290.1 | 116.04 | 135.6441 | 189.6 | 195.9 | 208.8 | 213 | 334.6 | 32.7 | 20.9 | 56.3 | 3 |  |  | 473.7 | 742.4 | 610.4 | 483.9 | 738.9 | 645 | 578.6
3148.3 | 1448.3 | 289.9 | 115.96 | 135.5506 | 190.4 | 196.5 | 209.1 | 213.3 | 336.2 | 32.8 | 20.9 | 56.3 | 3 |  |  | 474.5 | 737.8 | 614.2 | 484 | 734.1 | 639 | 577.6
3149.3 | 1449.3 | 288.9 | 115.56 | 135.083 | 191.2 | 197.2 | 209.2 | 213.7 | 337.7 | 32.9 | 20.9 | 56.3 | 3.3 |  |  | 475.3 | 729.2 | 615.9 | 484.2 | 727.4 | 635.4 | 578.9
3150.3 | 1450.3 | 288.5 | 115.4 | 134.896 | 191.4 | 198.2 | 209.7 | 214.5 | 333.8 | 32.8 | 20.9 | 56.5 | 3.2 |  |  | 476.1 | 716.1 | 617.3 | 484.5 | 721 | 628.5 | 582.3
3151.3 | 1451.3 | 288 | 115.2 | 134.6622 | 191.8 | 199.7 | 209.7 | 215.1 | 328 | 32.8 | 20.9 | 56.5 | 3 |  |  | 476.9 | 701.5 | 616.8 | 484.5 | 714.5 | 620.8 | 584
3152.3 | 1452.3 | 289.7 | 115.88 | 135.457 | 192 | 200.5 | 209.9 | 215.2 | 323.3 | 32.7 | 20.9 | 56.6 | 2.7 |  |  | 477.9 | 690.5 | 621.7 | 484.4 | 704.9 | 609.1 | 586
3153.3 | 1453.3 | 289.1 | 115.64 | 135.1765 | 191.9 | 201.2 | 209.4 | 215 | 320 | 32.7 | 20.9 | 56.6 | 2.7 |  |  | 478.7 | 684.6 | 617.3 | 483.8 | 690.3 | 595.5 | 582.3
3154.3 | 1454.3 | 290 | 116 | 135.5973 | 192.2 | 202.3 | 208.2 | 215.6 | 317.5 | 32.6 | 20.9 | 56.7 | 2.3 |  |  | 479.5 | 680.8 | 611.4 | 483.1 | 684.1 | 586.6 | 582.2
3155.3 | 1455.3 | 289.9 | 115.96 | 135.5506 | 192.4 | 202.9 | 207.5 | 215.4 | 311.8 | 32.6 | 20.9 | 56.7 | 2.7 |  |  | 480.3 | 669.3 | 607.3 | 482.3 | 676.6 | 574.7 | 578.8
3156.3 | 1456.3 | 289.8 | 115.92 | 135.5038 | 192.5 | 203 | 207.3 | 214.7 | 309.8 | 32.7 | 20.9 | 57 | 2.7 |  |  | 480.9 | 671.1 | 602.3 | 481.9 | 669.4 | 563.4 | 573.5
3157.3 | 1457.3 | 289.9 | 115.96 | 135.5506 | 192.9 | 202.4 | 206.9 | 214 | 309.3 | 32.7 | 20.9 | 57.2 | 3.1 |  |  | 481.6 | 667.9 | 595 | 481.4 | 661.3 | 555.6 | 570.9
3158.3 | 1458.3 | 290.6 | 116.24 | 135.8779 | 194 | 202.3 | 206.5 | 213.7 | 307.4 | 32.7 | 20.9 | 57.4 | 2.5 |  |  | 482.4 | 661.3 | 591.8 | 480 | 650.3 | 547.5 | 567.4
3159.3 | 1459.3 | 289.2 | 115.68 | 135.2233 | 193.9 | 203.1 | 205.8 | 213.3 | 305 | 32.7 | 20.9 | 57.6 | 2.5 |  |  | 483.2 | 658.5 | 591.4 | 479 | 639 | 539.6 | 567.5
3160.3 | 1460.3 | 288.6 | 115.44 | 134.9427 | 194.4 | 203.6 | 205.2 | 212.8 | 302.6 | 32.7 | 20.9 | 57.8 | 2.8 |  |  | 483.9 | 654.9 | 595.2 | 478.1 | 632.1 | 539.6 | 572.7
3161.3 | 1461.3 | 288.9 | 115.56 | 135.083 | 195.1 | 203.4 | 204.8 | 212 | 302.5 | 32.8 | 20.9 | 58 | 2.8 |  |  | 484.8 | 656.9 | 593.5 | 477.4 | 630.3 | 541 | 574.3
3162.3 | 1462.3 | 288.6 | 115.44 | 134.9427 | 195.2 | 202.7 | 204.8 | 211.9 | 303.3 | 32.8 | 20.9 | 58.2 | 2.6 |  |  | 485.5 | 658.7 | 595.5 | 477 | 633.5 | 543.4 | 575.6
3163.3 | 1463.3 | 287.4 | 114.96 | 134.3816 | 195.2 | 201.7 | 205.7 | 212.6 | 304.8 | 32.9 | 20.9 | 58.4 | 2.7 |  |  | 486.4 | 671.4 | 596.9 | 477 | 645.2 | 552.4 | 576.9
3164.3 | 1464.3 | 289.5 | 115.8 | 135.3635 | 195.2 | 200.4 | 205.8 | 213.2 | 311.2 | 32.8 | 20.9 | 58.5 | 2.6 |  |  | 487.2 | 680.1 | 594 | 477.6 | 654.2 | 560.6 | 576
3165.3 | 1465.3 | 290.1 | 116.04 | 135.6441 | 195.2 | 199.6 | 205.5 | 213.6 | 315.5 | 32.8 | 20.9 | 58.7 | 2.2 |  |  | 487.9 | 684.6 | 594.3 | 478.1 | 651.6 | 558.2 | 574.2
3166.3 | 1466.3 | 290.4 | 116.16 | 135.7843 | 195 | 199.5 | 205.9 | 214.5 | 313.5 | 32.8 | 20.9 | 58.7 | 2.5 |  |  | 488.6 | 676 | 598.5 | 477.9 | 646.2 | 566.1 | 581.8
3167.3 | 1467.3 | 289.5 | 115.8 | 135.3635 | 194.3 | 199.4 | 205.7 | 215.2 | 312.6 | 32.9 | 20.9 | 58.7 | 3.3 |  |  | 489.3 | 678.9 | 606.3 | 478.3 | 653.5 | 585.1 | 590.2
3168.3 | 1468.3 | 289.3 | 115.72 | 135.27 | 193.4 | 199.3 | 205.5 | 215.4 | 317.9 | 33 | 20.9 | 58.7 | 2.8 |  |  | 490 | 687 | 609.8 | 478.9 | 661 | 591.3 | 592.5
3169.3 | 1469.3 | 289.2 | 115.68 | 135.2233 | 192.6 | 199.6 | 206.1 | 215.9 | 318.2 | 33.1 | 20.9 | 58.7 | 2.6 |  |  | 490.6 | 679.8 | 608 | 479.3 | 661.6 | 592.7 | 589.2
3170.3 | 1470.3 | 288.9 | 115.56 | 135.083 | 192.7 | 200.4 | 206.6 | 216.1 | 316.6 | 33.2 | 20.9 | 58.7 | 2.5 |  |  | 491.2 | 675.2 | 597 | 479.6 | 665.6 | 592.4 | 583.7
3171.3 | 1471.3 | 289.6 | 115.84 | 135.4103 | 192.9 | 200.9 | 206.7 | 216.3 | 314.2 | 33.3 | 20.9 | 58.6 | 2.5 |  |  | 491.6 | 677.4 | 592.2 | 479.7 | 669.2 | 599 | 583.9
3172.3 | 1472.3 | 289 | 115.6 | 135.1297 | 192.4 | 200.6 | 206.9 | 216.5 | 314.5 | 33.4 | 20.9 | 58.6 | 2.3 |  |  | 492.1 | 683.1 | 591.4 | 480.2 | 677.5 | 604.8 | 584.2
3173.3 | 1473.3 | 289.9 | 115.96 | 135.5506 | 192.1 | 200.5 | 207 | 216.3 | 314.3 | 33.5 | 20.9 | 58.5 | 2.8 |  |  | 492.6 | 685.6 | 593.4 | 481.2 | 684 | 607.8 | 585.7
3174.3 | 1474.3 | 289.6 | 115.84 | 135.4103 | 192 | 200.7 | 208 | 216 | 313.7 | 33.5 | 20.9 | 58.4 | 3 |  |  | 493.2 | 677.3 | 590 | 481.9 | 680.7 | 610.1 | 584.4
3175.3 | 1475.3 | 290.4 | 116.16 | 135.7843 | 193.2 | 200.9 | 208.1 | 216.2 | 315.4 | 33.3 | 20.9 | 58.4 | 3.1 |  |  | 494 | 678.8 | 597 | 482.8 | 683.3 | 618.1 | 586.8
3176.3 | 1476.3 | 290.1 | 116.04 | 135.6441 | 194.6 | 200.6 | 207.6 | 216.1 | 317.9 | 33.3 | 20.9 | 58.3 | 3.2 |  |  | 494.5 | 675 | 609.8 | 483.7 | 676.2 | 619.4 | 590.3
3177.3 | 1477.3 | 290.2 | 116.08 | 135.6908 | 194.7 | 200.9 | 207.8 | 216 | 318.2 | 33.4 | 20.9 | 58.3 | 3.2 |  |  | 495.3 | 680 | 618.2 | 484.5 | 669.2 | 619.1 | 594.4
3178.3 | 1478.3 | 289.4 | 115.76 | 135.3168 | 195.5 | 202 | 207.8 | 216.4 | 318.2 | 33.2 | 20.9 | 58.4 | 3.7 |  |  | 496 | 679.3 | 611.7 | 485.2 | 663.6 | 611.7 | 587.3
3179.3 | 1479.3 | 289.3 | 115.72 | 135.27 | 196.4 | 202.7 | 208 | 216.2 | 317.6 | 33.1 | 20.9 | 58.5 | 3.2 |  |  | 496.7 | 680 | 608.1 | 485.7 | 656.6 | 606.4 | 584.4
3180.3 | 1480.3 | 289.4 | 115.76 | 135.3168 | 196.5 | 203.1 | 208.2 | 215.5 | 316.5 | 33.1 | 20.9 | 58.5 | 3.4 |  |  | 497.6 | 678.5 | 607.3 | 486.8 | 651.4 | 596.8 | 581.6
3181.3 | 1481.3 | 289.7 | 115.88 | 135.457 | 196.3 | 202.8 | 208 | 215 | 318.4 | 33.3 | 20.9 | 58.6 | 2.8 |  |  | 498.6 | 686.2 | 610.7 | 487.9 | 662.6 | 600.1 | 583.5
3182.3 | 1482.3 | 289.8 | 115.92 | 135.5038 | 196.4 | 202.9 | 208.3 | 214.5 | 324.8 | 33.4 | 20.9 | 58.6 | 2.3 |  |  | 499.7 | 696.7 | 622.8 | 489 | 673.8 | 613.3 | 594.5
3183.3 | 1483.3 | 290.3 | 116.12 | 135.7376 | 196.6 | 202.7 | 208.7 | 214.8 | 325.9 | 33.5 | 20.9 | 58.6 | 3 |  |  | 500.7 | 701.7 | 626.4 | 489.5 | 678.2 | 623 | 601.3
3184.3 | 1484.3 | 289.3 | 115.72 | 135.27 | 196.4 | 202.3 | 208.6 | 214.9 | 325.8 | 33.6 | 20.9 | 58.7 | 2.9 |  |  | 501.6 | 706.8 | 624 | 489.9 | 684.7 | 627 | 598
3185.3 | 1485.3 | 290.9 | 116.36 | 136.0181 | 196.4 | 201.7 | 207.5 | 215.4 | 329 | 33.6 | 20.9 | 58.8 | 3 |  |  | 502.4 | 721.9 | 618.5 | 490.9 | 702.2 | 635.8 | 597.2
3186.3 | 1486.3 | 290.6 | 116.24 | 135.8779 | 196.4 | 200.9 | 207.5 | 215.8 | 335 | 33.6 | 20.9 | 58.8 | 2.3 |  |  | 503.4 | 725.8 | 618.6 | 492.1 | 706.8 | 639.5 | 598.2
3187.3 | 1487.3 | 290.9 | 116.36 | 136.0181 | 196.2 | 199.8 | 208.4 | 216.3 | 335.7 | 33.5 | 20.9 | 58.8 | 2.4 |  |  | 504.4 | 718.7 | 622 | 493 | 701 | 637.7 | 598.2
3188.3 | 1488.3 | 291.4 | 116.56 | 136.2519 | 195.9 | 199.9 | 208.5 | 217.4 | 334 | 33.6 | 20.9 | 58.8 | 2.6 |  |  | 505.5 | 715.8 | 626 | 494.1 | 698.1 | 636 | 600.4
3189.3 | 1489.3 | 291.6 | 116.64 | 136.3454 | 196.2 | 201 | 208.6 | 217.8 | 334.2 | 33.6 | 20.9 | 58.8 | 2.9 |  |  | 506.4 | 720.1 | 613.6 | 495.7 | 709.6 | 633.2 | 594.2
3190.3 | 1490.3 | 290.2 | 116.08 | 135.6908 | 197.2 | 201.6 | 208.9 | 218 | 345.7 | 33.7 | 20.9 | 58.9 | 3.5 |  |  | 507.6 | 714.8 | 608.6 | 497.1 | 709.7 | 638 | 595.6
3191.3 | 1491.3 | 290.1 | 116.04 | 135.6441 | 198.1 | 201.6 | 209 | 217.9 | 344.8 | 33.8 | 20.9 | 58.9 | 3.5 |  |  | 508.9 | 713.6 | 609.1 | 498 | 712.4 | 646.6 | 602.2
3192.3 | 1492.3 | 287.4 | 114.96 | 134.3816 | 198.6 | 201.5 | 209.1 | 218.3 | 341.1 | 33.7 | 20.9 | 58.9 | 3.5 |  |  | 510.1 | 715.6 | 615.5 | 498.8 | 714 | 650.4 | 606.8
3193.3 | 1493.3 | 289.6 | 115.84 | 135.4103 | 198.1 | 201.7 | 209.8 | 218.6 | 337.2 | 33.7 | 20.8 | 58.9 | 2.8 |  |  | 511.5 | 710.8 | 624.9 | 499.6 | 712.1 | 649.8 | 608.6
3194.3 | 1494.3 | 290.1 | 116.04 | 135.6441 | 197.5 | 202.2 | 210.6 | 219.1 | 336.8 | 33.6 | 20.8 | 58.8 | 2.5 |  |  | 513 | 707.4 | 621.8 | 500.8 | 714 | 645.9 | 603.6
3195.3 | 1495.3 | 289.2 | 115.68 | 135.2233 | 197.5 | 202.3 | 211.5 | 219.2 | 333.1 | 33.6 | 20.8 | 58.8 | 3.4 |  |  | 513.9 | 715 | 615.7 | 502.1 | 725.1 | 642.7 | 596.8
3196.3 | 1496.3 | 289.2 | 115.68 | 135.2233 | 198.1 | 202.6 | 212.1 | 218.7 | 331.8 | 33.5 | 20.8 | 58.9 | 4.3 |  |  | 514.6 | 729.7 | 606.9 | 502.9 | 736.4 | 637.8 | 591.5
3197.3 | 1497.3 | 289.6 | 115.84 | 135.4103 | 198.6 | 202 | 211.6 | 218.4 | 331.1 | 33.6 | 20.8 | 59.1 | 4.4 |  |  | 515.4 | 729.9 | 596.2 | 503.5 | 739 | 630.5 | 586.2
3198.3 | 1498.3 | 289.7 | 115.88 | 135.457 | 199.2 | 201.2 | 211.7 | 218.2 | 329.9 | 33.7 | 20.8 | 59.3 | 4.8 |  |  | 516.3 | 724.1 | 587.3 | 504.1 | 737.3 | 619 | 582.6
3199.3 | 1499.3 | 289.9 | 115.96 | 135.5506 | 199.3 | 200.6 | 212 | 218.3 | 329.8 | 33.8 | 20.8 | 59.4 | 4.9 |  |  | 517.1 | 726.3 | 585.8 | 504.4 | 733.8 | 612.6 | 580.1
3200.3 | 1500.3 | 290.2 | 116.08 | 135.6908 | 199.9 | 201 | 211.8 | 218.7 | 334 | 33.7 | 20.8 | 59.5 | 4.8 |  |  | 518.3 | 732 | 587.3 | 504.9 | 742 | 619.5 | 584.2
3201.3 | 1501.3 | 290 | 116 | 135.5973 | 200.6 | 201.6 | 212.2 | 218.9 | 334.8 | 33.6 | 20.8 | 59.5 | 3.6 |  |  | 519.7 | 738.1 | 590.2 | 506.4 | 750.9 | 626.6 | 590.7
3202.3 | 1502.3 | 289.3 | 115.72 | 135.27 | 200.8 | 201.6 | 212.6 | 219.4 | 339.4 | 33.5 | 20.8 | 59.5 | 4.2 |  |  | 521.7 | 729.8 | 598.2 | 507.5 | 747.9 | 635.5 | 600.6
3203.3 | 1503.3 | 289.3 | 115.72 | 135.27 | 200.9 | 201.4 | 213.3 | 219.5 | 337.1 | 33.6 | 20.8 | 59.4 | 2.8 |  |  | 524 | 729.8 | 608 | 507.8 | 743.4 | 637.2 | 605.4
3204.3 | 1504.3 | 289.8 | 115.92 | 135.5038 | 200.7 | 201.6 | 214.3 | 220 | 336.3 | 33.8 | 20.8 | 59.3 | 2.4 |  |  | 526.2 | 733.5 | 611.2 | 508 | 740.7 | 627.6 | 602
3205.3 | 1505.3 | 290.2 | 116.08 | 135.6908 | 200.7 | 201.9 | 215.3 | 219.9 | 331.6 | 34 | 20.8 | 59.3 | 2.5 |  |  | 528 | 727.9 | 606.2 | 508.3 | 739.2 | 619.4 | 595.2
3206.3 | 1506.3 | 289 | 115.6 | 135.1297 | 201 | 202 | 216 | 220.5 | 331.9 | 34.1 | 20.8 | 59.3 | 2.8 |  |  | 530.1 | 731.9 | 610 | 508.7 | 736.4 | 613.6 | 595.7
3207.3 | 1507.3 | 290.4 | 116.16 | 135.7843 | 201.9 | 200.9 | 216.2 | 220.8 | 331.8 | 33.8 | 20.8 | 59.3 | 3.2 |  |  | 533.4 | 733.8 | 613.2 | 509.3 | 736.8 | 611.8 | 596.5
3208.3 | 1508.3 | 290.2 | 116.08 | 135.6908 | 202 | 201.5 | 216.1 | 220.9 | 332.7 | 33.6 | 20.8 | 59.3 | 3 |  |  | 536.5 | 739.4 | 610.5 | 511 | 746.3 | 613.1 | 594.3
3209.3 | 1509.3 | 291.3 | 116.52 | 136.2052 | 202.7 | 202.2 | 215.8 | 221.1 | 335.2 | 33.6 | 20.8 | 59.3 | 2.5 |  |  | 538.8 | 740 | 602.6 | 512.6 | 750 | 609.3 | 590.4
3210.3 | 1510.3 | 290.4 | 116.16 | 135.7843 | 203 | 202.8 | 216.4 | 221.2 | 335.3 | 33.9 | 20.8 | 59.2 | 2.5 |  |  | 540.8 | 740 | 595 | 514.2 | 752.7 | 607.3 | 587.2
3211.3 | 1511.3 | 290.6 | 116.24 | 135.8779 | 203 | 202.5 | 217.1 | 221.3 | 333.9 | 34.1 | 20.8 | 59.1 | 3.7 |  |  | 545.2 | 742.7 | 598.3 | 516 | 749.1 | 603.1 | 586.9
3212.3 | 1512.3 | 290.3 | 116.12 | 135.7376 | 203.6 | 202.9 | 217.4 | 221.5 | 333.7 | 34.1 | 20.8 | 59.1 | 4.6 |  |  | 549.8 | 746.4 | 602.7 | 517.6 | 752.4 | 605.2 | 591.7
3213.3 | 1513.3 | 289.9 | 115.96 | 135.5506 | 203.9 | 203.1 | 217.5 | 222 | 334.2 | 34 | 20.8 | 59.3 | 5 |  |  | 557.2 | 744.2 | 609.5 | 519.1 | 749.6 | 618.1 | 598.1
3214.3 | 1514.3 | 289.6 | 115.84 | 135.4103 | 203.9 | 203.3 | 217.8 | 222.3 | 333.8 | 34 | 20.8 | 59.5 | 4.2 |  |  | 566.3 | 738.8 | 610.5 | 520.9 | 746.9 | 622.2 | 603.2
3215.3 | 1515.3 | 289.8 | 115.92 | 135.5038 | 203.9 | 202.9 | 218.2 | 222.9 | 333.8 | 33.9 | 20.8 | 59.6 | 3.6 |  |  | 575.1 | 740.1 | 609.5 | 522.4 | 748.3 | 623.9 | 602
3216.3 | 1516.3 | 290 | 116 | 135.5973 | 203.8 | 202.3 | 218.8 | 222.8 | 335.7 | 33.9 | 20.8 | 59.5 | 2.5 |  |  | 581.5 | 734.9 | 602.1 | 524.1 | 747.4 | 625 | 598.9
3217.3 | 1517.3 | 290 | 116 | 135.5973 | 203.3 | 202.6 | 219.1 | 223 | 339.6 | 33.8 | 20.8 | 59.3 | 2.5 |  |  | 586.4 | 736.1 | 606.5 | 525.9 | 746.6 | 624.3 | 601.2
3218.3 | 1518.3 | 291.1 | 116.44 | 136.1117 | 202.8 | 203.2 | 219.3 | 222.9 | 343.6 | 33.8 | 20.8 | 59.3 | 2.5 |  |  | 591.8 | 736.5 | 610.4 | 527.6 | 745.1 | 621.6 | 603.5
3219.3 | 1519.3 | 290.5 | 116.2 | 135.8311 | 202.5 | 203.3 | 219.2 | 223.4 | 342.8 | 33.8 | 20.8 | 59.2 | 2.3 |  |  | 596.6 | 733.2 | 608 | 529.3 | 749.7 | 625.3 | 603.1
3220.3 | 1520.3 | 289.7 | 115.88 | 135.457 | 202.4 | 203.6 | 219.7 | 222.8 | 340.9 | 33.9 | 20.8 | 59.1 | 2.2 |  |  | 601.3 | 725.5 | 604.1 | 530.6 | 758.8 | 632.2 | 600.6
3221.3 | 1521.3 | 291 | 116.4 | 136.0649 | 203.4 | 204.3 | 219.7 | 222.4 | 343.1 | 33.9 | 20.8 | 59.2 | 2.3 |  |  | 605.1 | 724.1 | 604.2 | 532.4 | 764.4 | 639.4 | 601.3
3222.3 | 1522.3 | 292.1 | 116.84 | 136.5792 | 203.3 | 204.2 | 219.2 | 222.1 | 344.9 | 33.9 | 20.8 | 59.1 | 2.6 |  |  | 609.9 | 726.3 | 615.3 | 534.4 | 773 | 642.9 | 604.2
3223.3 | 1523.3 | 291 | 116.4 | 136.0649 | 203.7 | 204 | 219.1 | 221.4 | 345 | 33.9 | 20.8 | 59.1 | 3 |  |  | 614.3 | 732.4 | 618.4 | 536 | 776.7 | 637.4 | 603
3224.3 | 1524.3 | 291.1 | 116.44 | 136.1117 | 203.5 | 204.4 | 219.1 | 221 | 343.5 | 33.9 | 20.8 | 59.3 | 3.6 |  |  | 616.9 | 736.6 | 608.5 | 537.1 | 784.6 | 631.4 | 599
3225.3 | 1525.3 | 290.7 | 116.28 | 135.9246 | 203.3 | 205 | 218.9 | 220.8 | 343.8 | 34 | 20.8 | 59.4 | 3.9 |  |  | 619.7 | 741.2 | 603.3 | 537.7 | 795.6 | 640.3 | 599.5
3226.3 | 1526.3 | 290.1 | 116.04 | 135.6441 | 203.3 | 205.4 | 218.8 | 220.6 | 342.5 | 34 | 20.8 | 59.5 | 4.1 |  |  | 622.1 | 740.7 | 602.6 | 538.9 | 800.2 | 643 | 602.9
3227.3 | 1527.3 | 290.5 | 116.2 | 135.8311 | 203.6 | 205.2 | 218.4 | 220.3 | 342.7 | 34 | 20.8 | 59.7 | 4.2 |  |  | 623.8 | 750.1 | 606.2 | 539.7 | 804.2 | 641.4 | 602.3
3228.3 | 1528.3 | 291 | 116.4 | 136.0649 | 203.9 | 204.5 | 218.3 | 220.4 | 346.4 | 34.1 | 20.8 | 59.7 | 3.5 |  |  | 627.7 | 747.9 | 602.8 | 540.9 | 803.7 | 636 | 600.3
3229.3 | 1529.3 | 290.6 | 116.24 | 135.8779 | 203.6 | 204.6 | 218.7 | 220.2 | 343.8 | 34.1 | 20.8 | 59.8 | 3.5 |  |  | 629.7 | 741.2 | 593.2 | 540.9 | 799.7 | 624.1 | 595.2
3230.3 | 1530.3 | 290.2 | 116.08 | 135.6908 | 203.3 | 204.7 | 219.1 | 219.7 | 337.8 | 34.2 | 20.8 | 59.8 | 3.2 |  |  | 628.9 | 728.3 | 580.5 | 540.2 | 787.7 | 607.7 | 589.6
3231.3 | 1531.3 | 290.9 | 116.36 | 136.0181 | 202.6 | 204.4 | 219.4 | 219.7 | 332.3 | 34.2 | 20.8 | 59.9 | 3.1 |  |  | 630.5 | 729.6 | 573.4 | 540 | 789 | 604.8 | 587.5
3232.3 | 1532.3 | 289.9 | 115.96 | 135.5506 | 201.9 | 203.7 | 219.4 | 219.3 | 331.5 | 34.2 | 20.8 | 59.9 | 2.7 |  |  | 634.8 | 727.8 | 576.1 | 541.8 | 783.3 | 609.9 | 591.2
3233.3 | 1533.3 | 290.6 | 116.24 | 135.8779 | 201.7 | 203.9 | 219.1 | 218.9 | 329.8 | 34.2 | 20.8 | 59.8 | 2.4 |  |  | 638.7 | 734.8 | 575.1 | 544 | 780.1 | 608.4 | 592.8
3234.3 | 1534.3 | 289.7 | 115.88 | 135.457 | 201.5 | 204 | 219 | 219.1 | 328.8 | 34.2 | 20.8 | 59.7 | 2.4 |  |  | 642.1 | 726.3 | 574.6 | 546.4 | 772.7 | 602.7 | 592.1
3235.3 | 1535.3 | 290.5 | 116.2 | 135.8311 | 201.7 | 203.2 | 219.2 | 219.3 | 325.8 | 34.2 | 20.8 | 59.7 | 2.8 |  |  | 645.8 | 717 | 575.3 | 548.8 | 771.3 | 608.9 | 592.5
3236.3 | 1536.3 | 291.7 | 116.68 | 136.3922 | 202.1 | 203 | 219.1 | 219.1 | 325.6 | 34.3 | 20.8 | 59.9 | 3 |  |  | 649.8 | 698 | 568.9 | 551 | 769.9 | 599 | 587.8
3237.3 | 1537.3 | 291.6 | 116.64 | 136.3454 | 202.7 | 202.9 | 218.8 | 219.8 | 321.1 | 34.3 | 20.8 | 59.9 | 2.8 |  |  | 653.5 | 696.3 | 566.7 | 552.6 | 769.8 | 589 | 584
3238.3 | 1538.3 | 290.5 | 116.2 | 135.8311 | 202.5 | 203.3 | 219 | 220.5 | 322.3 | 34.2 | 20.8 | 60 | 2.7 |  |  | 654.8 | 713 | 566.6 | 553.7 | 771.7 | 581.3 | 579.3
3239.3 | 1539.3 | 290.2 | 116.08 | 135.6908 | 202.4 | 203.2 | 218.8 | 220.6 | 323.4 | 34.1 | 20.8 | 60.1 | 2.6 |  |  | 656.3 | 722.8 | 571.6 | 555.4 | 778.7 | 579 | 580.2
3240.3 | 1540.3 | 290.4 | 116.16 | 135.7843 | 203.3 | 203.7 | 218.3 | 220.3 | 325.2 | 34 | 20.8 | 60.2 | 2.9 |  |  | 658.7 | 721.8 | 576.2 | 556.9 | 776.4 | 572.9 | 579.9
3241.3 | 1541.3 | 290.2 | 116.08 | 135.6908 | 204.5 | 204.6 | 218 | 219.7 | 323.7 | 34 | 20.8 | 60.3 | 3 |  |  | 663.1 | 724.5 | 578.4 | 559.6 | 774.5 | 575.5 | 583.4
3242.3 | 1542.3 | 290.4 | 116.16 | 135.7843 | 204.9 | 205.1 | 217.9 | 218.8 | 325.1 | 34 | 20.8 | 60.3 | 3.1 |  |  | 665.2 | 726.7 | 582.6 | 561.4 | 767.5 | 574 | 584.3
3243.3 | 1543.3 | 290.3 | 116.12 | 135.7376 | 205.1 | 204.6 | 218.2 | 218.7 | 324.2 | 33.9 | 20.8 | 60.2 | 2.8 |  |  | 665.2 | 724.2 | 575.2 | 561.5 | 762.4 | 565.6 | 580.3
3244.3 | 1544.3 | 290.5 | 116.2 | 135.8311 | 205.3 | 204.9 | 217.9 | 219.4 | 321.2 | 33.9 | 20.8 | 60.3 | 2.8 |  |  | 664 | 720.9 | 559.9 | 560.7 | 766.9 | 559 | 574.5
3245.3 | 1545.3 | 290.7 | 116.28 | 135.9246 | 205.5 | 204.5 | 218.1 | 219.5 | 320 | 34 | 20.8 | 60.4 | 2.8 |  |  | 666.8 | 716.5 | 556.6 | 560.4 | 769.2 | 553.5 | 572.9
3246.3 | 1546.3 | 291 | 116.4 | 136.0649 | 205.2 | 204.9 | 217.9 | 219.5 | 318.6 | 34 | 20.8 | 60.4 | 2.8 |  |  | 672 | 718.7 | 568.2 | 562 | 767.2 | 562.9 | 579.2
3247.3 | 1547.3 | 289.7 | 115.88 | 135.457 | 205 | 204.9 | 217.4 | 220 | 322.4 | 34.1 | 20.8 | 60.4 | 2.3 |  |  | 676.1 | 723 | 570.3 | 564.4 | 764.4 | 563.4 | 577.7
3248.3 | 1548.3 | 290.6 | 116.24 | 135.8779 | 204.6 | 204.6 | 217.5 | 220.2 | 323.5 | 34.2 | 20.8 | 60.4 | 2.8 |  |  | 679.6 | 725.6 | 572.3 | 565.3 | 771 | 571.6 | 580.4
3249.3 | 1549.3 | 290 | 116 | 135.5973 | 204.2 | 204.6 | 218.2 | 220.3 | 324 | 34.2 | 20.8 | 60.4 | 3.1 |  |  | 683.4 | 727.2 | 572.7 | 567.2 | 776.3 | 584.7 | 581.3
3250.3 | 1550.3 | 290 | 116 | 135.5973 | 203.9 | 204.8 | 218.5 | 220.4 | 327.2 | 34.3 | 20.8 | 60.4 | 2.7 |  |  | 687 | 729.2 | 577 | 570 | 778.8 | 596.4 | 584.1
3251.3 | 1551.3 | 290.9 | 116.36 | 136.0181 | 203.7 | 205.1 | 218.4 | 220.3 | 327 | 34.4 | 20.8 | 60.3 | 2.7 |  |  | 690.9 | 727.6 | 577.2 | 572.8 | 781 | 607.6 | 587.1
3252.3 | 1552.3 | 289.7 | 115.88 | 135.457 | 203 | 204.7 | 218.6 | 220.6 | 326.4 | 34.5 | 20.8 | 60.3 | 2.8 |  |  | 693.7 | 725.1 | 581.1 | 575.4 | 781.1 | 617.3 | 593.1
3253.3 | 1553.3 | 290 | 116 | 135.5973 | 203 | 204.7 | 218.6 | 220.6 | 327.3 | 34.6 | 20.8 | 60.2 | 2.9 |  |  | 696.6 | 731 | 585.7 | 577.5 | 787.9 | 628.9 | 597.6
3254.3 | 1554.3 | 291.2 | 116.48 | 136.1584 | 203.1 | 204.9 | 218.5 | 220.8 | 329.8 | 34.6 | 20.8 | 60.1 | 3.1 |  |  | 700.2 | 729.7 | 584.9 | 578.5 | 784 | 624.5 | 593
3255.3 | 1555.3 | 291.6 | 116.64 | 136.3454 | 203.2 | 204.5 | 219 | 221.1 | 326.2 | 34.7 | 20.8 | 60 | 3.2 |  |  | 703.4 | 723.4 | 575.4 | 579.4 | 771.6 | 607.9 | 584
3256.3 | 1556.3 | 292 | 116.8 | 136.5325 | 203.1 | 204.1 | 219.5 | 221.4 | 322.2 | 34.7 | 20.8 | 60.1 | 3.7 |  |  | 705.3 | 715.5 | 572.4 | 579.7 | 764 | 594.7 | 579
3257.3 | 1557.3 | 291.1 | 116.44 | 136.1117 | 202.9 | 203.9 | 219.8 | 221.3 | 318.8 | 34.7 | 20.8 | 60.2 | 3.7 |  |  | 705.6 | 700.4 | 563.8 | 579.3 | 746.9 | 581 | 574.3
3258.3 | 1558.3 | 292 | 116.8 | 136.5325 | 202.6 | 204.8 | 220.4 | 221 | 317.8 | 34.7 | 20.8 | 60.3 | 2.7 |  |  | 707.6 | 702 | 561.1 | 578.8 | 740.9 | 575.8 | 572
3259.3 | 1559.3 | 291.9 | 116.76 | 136.4857 | 202.6 | 205.9 | 220.7 | 220 | 318.2 | 34.7 | 20.7 | 60.2 | 2.8 |  |  | 708.9 | 699.8 | 558 | 578.2 | 742.5 | 565.5 | 570.7
3260.3 | 1560.3 | 291.6 | 116.64 | 136.3454 | 202.8 | 205.1 | 220.4 | 219.4 | 318.9 | 34.7 | 20.7 | 60.1 | 3.1 |  |  | 713.1 | 699.5 | 564 | 578.5 | 736.7 | 556.3 | 569.6
3261.3 | 1561.3 | 291.2 | 116.48 | 136.1584 | 202.7 | 204.1 | 220 | 218.5 | 319 | 34.7 | 20.7 | 60.1 | 2.7 |  |  | 719.9 | 711 | 575.9 | 579.8 | 734.7 | 561 | 573.8
3262.3 | 1562.3 | 290.8 | 116.32 | 135.9714 | 202.9 | 203.8 | 219.3 | 218.5 | 325.8 | 34.7 | 20.7 | 60.2 | 2.9 |  |  | 726.5 | 714.5 | 586.9 | 583 | 737.5 | 576.3 | 582.3
3263.3 | 1563.3 | 289.9 | 115.96 | 135.5506 | 202.7 | 204 | 219.1 | 218.6 | 325.4 | 34.8 | 20.7 | 60.3 | 3.8 |  |  | 731.9 | 695 | 591.9 | 585.8 | 722.4 | 581.4 | 586.2
3264.3 | 1564.3 | 290.3 | 116.12 | 135.7376 | 202.5 | 203.5 | 219.7 | 218.7 | 321.8 | 34.9 | 20.7 | 60.6 | 3.7 |  |  | 736.5 | 695.2 | 596.6 | 588.6 | 715.6 | 590.4 | 590.1
3265.3 | 1565.3 | 290.6 | 116.24 | 135.8779 | 202.1 | 203.8 | 219.5 | 218.8 | 322.7 | 35 | 20.7 | 60.8 | 3.4 |  |  | 741.8 | 698.8 | 597.6 | 590.7 | 721 | 599.4 | 591.5
3266.3 | 1566.3 | 290.8 | 116.32 | 135.9714 | 201.8 | 203.8 | 219.3 | 218.4 | 325.1 | 34.9 | 20.7 | 61 | 2.8 |  |  | 747.4 | 706.2 | 601.8 | 592.6 | 727.8 | 608 | 592.1
3267.3 | 1567.3 | 289 | 115.6 | 135.1297 | 201.7 | 203.7 | 219.3 | 218.4 | 326.1 | 34.8 | 20.7 | 61.1 | 2.5 |  |  | 751 | 700.3 | 594.5 | 591.9 | 720.9 | 601.2 | 585
3268.3 | 1568.3 | 287.9 | 115.16 | 134.6154 | 201.8 | 203.1 | 220 | 219.1 | 322.6 | 34.6 | 20.7 | 61.1 | 2.7 |  |  | 753.4 | 695.2 | 585.2 | 590.2 | 714.9 | 584.7 | 577
3269.3 | 1569.3 | 289.3 | 115.72 | 135.27 | 202.2 | 203 | 220.2 | 219.5 | 318 | 34.4 | 20.7 | 61.1 | 3.1 |  |  | 753.9 | 677.4 | 575.4 | 588.5 | 702.7 | 568.5 | 572.2
3270.3 | 1570.3 | 290.8 | 116.32 | 135.9714 | 202.7 | 204.1 | 220.5 | 219.4 | 313.6 | 34.5 | 20.7 | 61.2 | 3.9 |  |  | 755.3 | 661.3 | 573.1 | 587.9 | 687.7 | 554.2 | 571.1
3271.3 | 1571.3 | 289.3 | 115.72 | 135.27 | 202.8 | 204.9 | 220.1 | 219.1 | 309.7 | 34.5 | 20.7 | 61.4 | 4.6 |  |  | 761.5 | 651.7 | 586.2 | 592.6 | 671.4 | 554 | 578.1
3272.3 | 1572.3 | 289 | 115.6 | 135.1297 | 202.3 | 204.6 | 219.6 | 218.6 | 307.3 | 34.3 | 20.7 | 61.5 | 4.4 |  |  | 766.8 | 659.5 | 598 | 595.3 | 670.7 | 558 | 580.5
3273.3 | 1573.3 | 289.3 | 115.72 | 135.27 | 201.5 | 204.7 | 219.1 | 217.7 | 307.5 | 34.1 | 20.7 | 61.6 | 4.3 |  |  | 771.8 | 660.7 | 597.8 | 596 | 658.3 | 556.2 | 578.4
3274.3 | 1574.3 | 289.5 | 115.8 | 135.3635 | 200.7 | 204 | 218.4 | 216.9 | 310.4 | 33.9 | 20.7 | 61.6 | 4.9 |  |  | 776.9 | 657.4 | 603.8 | 597.4 | 652.9 | 557 | 579.5
3275.3 | 1575.3 | 290.6 | 116.24 | 135.8779 | 200.7 | 204.4 | 218.8 | 217 | 310.3 | 33.9 | 20.7 | 61.6 | 4.9 |  |  | 780.3 | 663.2 | 612.6 | 597.6 | 651.3 | 555.9 | 580.6
3276.3 | 1576.3 | 290.5 | 116.2 | 135.8311 | 200.7 | 204.4 | 218.5 | 216.7 | 312 | 33.9 | 20.7 | 61.7 | 3.7 |  |  | 783.3 | 668.8 | 621.4 | 598.8 | 654.6 | 563.1 | 585.5
3277.3 | 1577.3 | 290.3 | 116.12 | 135.7376 | 200.3 | 203.2 | 217.9 | 216.7 | 311.2 | 34 | 20.7 | 61.7 | 3.2 |  |  | 788.4 | 668.3 | 616.9 | 600.7 | 655.4 | 565.1 | 581.7
3278.3 | 1578.3 | 290.3 | 116.12 | 135.7376 | 200.2 | 202.2 | 217.1 | 216.4 | 312.2 | 34.2 | 20.7 | 61.8 | 3.4 |  |  | 789.5 | 679.6 | 616.8 | 602.8 | 654 | 565.9 | 579
3279.3 | 1579.3 | 289.7 | 115.88 | 135.457 | 200.1 | 201.6 | 217 | 215.8 | 313.2 | 34.4 | 20.7 | 61.9 | 3.5 |  |  | 794.7 | 688.5 | 615.3 | 606.3 | 656.6 | 573.6 | 578.9
3280.3 | 1580.3 | 290.5 | 116.2 | 135.8311 | 200 | 202.1 | 216.5 | 215.5 | 315 | 34.6 | 20.7 | 61.9 | 3.7 |  |  | 801.2 | 683.3 | 620.8 | 609.3 | 648.4 | 575.9 | 581
3281.3 | 1581.3 | 289 | 115.6 | 135.1297 | 199.9 | 202.7 | 216.2 | 215.6 | 314.8 | 34.7 | 20.7 | 61.8 | 3.8 |  |  | 804.8 | 679.3 | 624.7 | 612.2 | 638.2 | 572.2 | 581.4
3282.3 | 1582.3 | 289.3 | 115.72 | 135.27 | 200 | 202.7 | 216.1 | 215.9 | 314.3 | 34.6 | 20.7 | 61.7 | 3.5 |  |  | 807.1 | 675 | 629.6 | 613.8 | 628.3 | 569.7 | 581.8
3283.3 | 1583.3 | 289.1 | 115.64 | 135.1765 | 199.9 | 202.9 | 215.9 | 215.7 | 310.7 | 34.4 | 20.7 | 61.6 | 2.8 |  |  | 809.2 | 664.3 | 633.9 | 615.7 | 623.6 | 570.3 | 583.6
3284.3 | 1584.3 | 290.1 | 116.04 | 135.6441 | 199.6 | 202.5 | 216.1 | 215 | 309.6 | 34.4 | 20.7 | 61.4 | 3.2 |  |  | 812 | 662.2 | 635 | 618.3 | 624.3 | 567.3 | 584.8
3285.3 | 1585.3 | 291.2 | 116.48 | 136.1584 | 199.4 | 202.3 | 215.8 | 214.4 | 307.9 | 34.6 | 20.7 | 61.2 | 3.5 |  |  | 813.9 | 651.9 | 636.5 | 618.9 | 620.7 | 563.8 | 586.1
3286.3 | 1586.3 | 289.8 | 115.92 | 135.5038 | 199.5 | 202.1 | 216.1 | 213.9 | 304.9 | 34.8 | 20.7 | 61.2 | 3.7 |  |  | 814 | 638.5 | 642.7 | 618.9 | 610.7 | 560.6 | 589.1
3287.3 | 1587.3 | 288.8 | 115.52 | 135.0362 | 199.5 | 202.1 | 216.2 | 213.3 | 302.7 | 34.9 | 20.7 | 61.3 | 4.1 |  |  | 812.7 | 624.5 | 638.3 | 618 | 604.3 | 557.3 | 586.9
3288.3 | 1588.3 | 288.2 | 115.28 | 134.7557 | 199.1 | 202.4 | 216.2 | 212.7 | 300.8 | 35 | 20.7 | 61.3 | 4.4 |  |  | 812.3 | 615.3 | 640.4 | 618.8 | 595.9 | 557.9 | 590.8
3289.3 | 1589.3 | 290 | 116 | 135.5973 | 199 | 202.5 | 216.8 | 211.8 | 298.4 | 35.1 | 20.7 | 61.3 | 4.3 |  |  | 812.2 | 604.1 | 636.4 | 619.6 | 587.1 | 555 | 595
3290.3 | 1590.3 | 287.2 | 114.88 | 134.2881 | 199.2 | 201.5 | 216.5 | 211.1 | 295.3 | 35.1 | 20.7 | 61.2 | 3.5 |  |  | 811.6 | 593.1 | 632.5 | 619.7 | 577.5 | 545.7 | 593.1
3291.3 | 1591.3 | 286.1 | 114.44 | 133.7738 | 198.9 | 201.1 | 216.2 | 211 | 291.7 | 35.1 | 20.7 | 61.2 | 4.5 |  |  | 811.6 | 589.3 | 639.1 | 619 | 573.4 | 544.8 | 594.5
3292.3 | 1592.3 | 288.4 | 115.36 | 134.8492 | 198.9 | 202.4 | 215.6 | 210.8 | 288.4 | 35 | 20.7 | 61.3 | 5.1 |  |  | 810.9 | 591.6 | 640.2 | 619.1 | 571.1 | 553 | 598.5
3293.3 | 1593.3 | 285.7 | 114.28 | 133.5867 | 199.1 | 204.3 | 214.4 | 210.3 | 287.5 | 35 | 20.7 | 61.4 | 4.5 |  |  | 810.3 | 595.3 | 637.6 | 620.1 | 576.5 | 561.9 | 600.6
3294.3 | 1594.3 | 286.3 | 114.52 | 133.8673 | 199.1 | 204.4 | 213.2 | 209.5 | 286.6 | 35 | 20.7 | 61.5 | 3.8 |  |  | 809.7 | 590.9 | 637.3 | 621.7 | 564.2 | 558.8 | 596.9
3295.3 | 1595.3 | 288.9 | 115.56 | 135.083 | 198.9 | 203.9 | 212.5 | 209.7 | 283.9 | 34.9 | 20.7 | 61.6 | 3.8 |  |  | 808.5 | 580.1 | 638.7 | 621.9 | 558.9 | 550.2 | 596.4
3296.3 | 1596.3 | 288.2 | 115.28 | 134.7557 | 198.5 | 203.4 | 212 | 209.9 | 281.3 | 34.7 | 20.7 | 61.6 | 4.1 |  |  | 807.7 | 583.2 | 639.2 | 622.4 | 555.9 | 558.2 | 600.8
3297.3 | 1597.3 | 288.2 | 115.28 | 134.7557 | 198.2 | 203.2 | 210.8 | 209.9 | 282.6 | 34.7 | 20.7 | 61.7 | 4.7 |  |  | 806.7 | 591.5 | 636.1 | 623.1 | 560.8 | 562.1 | 599.8
3298.3 | 1598.3 | 288.1 | 115.24 | 134.7089 | 197.5 | 202.7 | 209.5 | 209.5 | 283.8 | 34.8 | 20.7 | 61.7 | 4.8 |  |  | 805.9 | 594.5 | 639.4 | 621.3 | 562.3 | 563.3 | 597.1
3299.3 | 1599.3 | 289.7 | 115.88 | 135.457 | 197.1 | 202.6 | 209.1 | 208.9 | 282.6 | 34.8 | 20.7 | 61.7 | 4.2 |  |  | 804.4 | 607.4 | 638.3 | 620.6 | 568.8 | 564.9 | 595.5
3300.3 | 1600.3 | 289.2 | 115.68 | 135.2233 | 197.4 | 203.5 | 209.2 | 208.3 | 283.4 | 34.8 | 20.7 | 61.7 | 4.2 |  |  | 801.9 | 616.1 | 619.5 | 619.7 | 575.4 | 553 | 585.3
3301.3 | 1601.3 | 289.5 | 115.8 | 135.3635 | 197.6 | 203.3 | 209.2 | 207.4 | 284.7 | 35 | 20.7 | 61.6 | 3.6 |  |  | 799.8 | 626 | 605.3 | 616.7 | 584.6 | 548.7 | 580.3
3302.3 | 1602.3 | 290.4 | 116.16 | 135.7843 | 198.3 | 203.3 | 209.5 | 206.4 | 285.3 | 35 | 20.7 | 61.8 | 3.5 |  |  | 798.1 | 634.7 | 600.5 | 615 | 590.6 | 549.2 | 579.5
3303.3 | 1603.3 | 291.4 | 116.56 | 136.2519 | 198.1 | 203 | 209.7 | 205.4 | 286.1 | 35.1 | 20.7 | 61.9 | 3.5 |  |  | 796.5 | 643.8 | 604.8 | 614.8 | 593.1 | 552.7 | 584.4
3304.3 | 1604.3 | 292.2 | 116.88 | 136.626 | 198 | 201.9 | 209.2 | 205.8 | 291.2 | 35.1 | 20.7 | 61.9 | 3.6 |  |  | 795 | 639.6 | 612 | 614.5 | 595.2 | 554.4 | 589.4
3305.3 | 1605.3 | 292.7 | 117.08 | 136.8598 | 197.8 | 200.6 | 208.8 | 207.1 | 295.2 | 35.1 | 20.7 | 61.9 | 3.9 |  |  | 792.3 | 644.3 | 604 | 616 | 595.6 | 547.7 | 585.2
3306.3 | 1606.3 | 291.6 | 116.64 | 136.3454 | 197.7 | 199.4 | 208.5 | 207.6 | 297.7 | 35.1 | 20.7 | 61.9 | 4.1 |  |  | 791.9 | 665 | 604.2 | 617.2 | 605 | 550.9 | 581.4
3307.3 | 1607.3 | 291.9 | 116.76 | 136.4857 | 197.2 | 198 | 208.9 | 207.7 | 299.7 | 35 | 20.7 | 61.9 | 4.1 |  |  | 790.3 | 674.1 | 593.4 | 617 | 615.3 | 552.4 | 578.6
3308.3 | 1608.3 | 291.9 | 116.76 | 136.4857 | 196.5 | 196.7 | 208.9 | 208.5 | 299.8 | 34.9 | 20.7 | 61.9 | 5 |  |  | 787.9 | 681.2 | 583.6 | 616.1 | 620.7 | 551.3 | 574.9
3309.3 | 1609.3 | 291 | 116.4 | 136.0649 | 196.5 | 196.8 | 209.4 | 209.4 | 301.7 | 34.9 | 20.7 | 62 | 5.1 |  |  | 786.7 | 687.2 | 584.7 | 613.5 | 620.7 | 546.8 | 573.3
3310.3 | 1610.3 | 291.3 | 116.52 | 136.2052 | 195.8 | 196.3 | 210.1 | 209.5 | 302.1 | 35 | 20.7 | 62.1 | 4.2 |  |  | 783.8 | 670.6 | 579 | 612.7 | 609.2 | 541.3 | 571.9
3311.3 | 1611.3 | 291.3 | 116.52 | 136.2052 | 196 | 196.5 | 211.1 | 209.7 | 299.2 | 35.2 | 20.7 | 62.1 | 4.5 |  |  | 781.5 | 673.3 | 575.6 | 612.3 | 606.1 | 537.4 | 568.7
3312.3 | 1612.3 | 289.6 | 115.84 | 135.4103 | 196.6 | 195.6 | 211.9 | 209.5 | 300 | 35.4 | 20.7 | 62 | 5.4 |  |  | 780.9 | 673.2 | 578.6 | 614.1 | 618.1 | 546.6 | 570.7
3313.3 | 1613.3 | 289.3 | 115.72 | 135.27 | 196.8 | 195.1 | 211.9 | 209.7 | 302.9 | 35.5 | 20.7 | 62 | 5 |  |  | 780.3 | 664.9 | 584.3 | 615.9 | 623.4 | 561.4 | 579.1
3314.3 | 1614.3 | 290.5 | 116.2 | 135.8311 | 196.9 | 195.3 | 211.6 | 209.7 | 302.2 | 35.6 | 20.7 | 61.9 | 4.8 |  |  | 779.5 | 655.9 | 592.3 | 618.2 | 621.7 | 575.2 | 587.2
3315.3 | 1615.3 | 289.6 | 115.84 | 135.4103 | 196.7 | 195.6 | 211.8 | 210.1 | 301.5 | 35.6 | 20.7 | 61.7 | 4.5 |  |  | 778.8 | 655.1 | 598.8 | 620.2 | 631.8 | 594.5 | 591.8
3316.3 | 1616.3 | 290 | 116 | 135.5973 | 196.3 | 195.9 | 212.1 | 210.5 | 304.4 | 35.5 | 20.7 | 61.7 | 4.5 |  |  | 778.4 | 657.3 | 604.5 | 621.6 | 632.2 | 602.2 | 591.4
3317.3 | 1617.3 | 290.1 | 116.04 | 135.6441 | 195.8 | 195.9 | 211.8 | 210.8 | 302.9 | 35.5 | 20.7 | 61.6 | 4.2 |  |  | 775.8 | 653.5 | 599.4 | 622.5 | 623.4 | 593.4 | 583.4
3318.3 | 1618.3 | 289.6 | 115.84 | 135.4103 | 195.1 | 195.9 | 211.4 | 211.1 | 304.9 | 35.4 | 20.7 | 61.6 | 3.6 |  |  | 774.6 | 648.1 | 604.5 | 623.5 | 612.9 | 582.6 | 579.2
3319.3 | 1619.3 | 291.3 | 116.52 | 136.2052 | 194.1 | 196.6 | 211.4 | 211.3 | 305.5 | 35.4 | 20.7 | 61.5 | 3.4 |  |  | 774.9 | 654.9 | 603.5 | 623.6 | 605.5 | 577.8 | 576.9
3320.3 | 1620.3 | 291.1 | 116.44 | 136.1117 | 194.1 | 198 | 211.8 | 211.6 | 306.2 | 35.3 | 20.7 | 61.5 | 4.1 |  |  | 775.1 | 659.9 | 611.6 | 624.4 | 601.1 | 575.4 | 580
3321.3 | 1621.3 | 288.1 | 115.24 | 134.7089 | 194.3 | 199.2 | 212 | 211.4 | 309.6 | 35.1 | 20.7 | 61.7 | 4.7 |  |  | 772.9 | 654.2 | 606.9 | 625.6 | 600.2 | 574.2 | 580.7
3322.3 | 1622.3 | 289.8 | 115.92 | 135.5038 | 195.1 | 199.7 | 212 | 210.7 | 310.3 | 35 | 20.7 | 61.7 | 5 |  |  | 773.2 | 651.7 | 612.2 | 626.6 | 600.8 | 581.2 | 585.5
3323.3 | 1623.3 | 287.5 | 115 | 134.4284 | 194.9 | 199.5 | 211.9 | 210.1 | 310.3 | 35.1 | 20.7 | 61.7 | 4 |  |  | 774.1 | 664.3 | 619.4 | 628.3 | 604.5 | 586.9 | 587.6
3324.3 | 1624.3 | 288.8 | 115.52 | 135.0362 | 194.8 | 199.4 | 211.1 | 209.5 | 310.4 | 35.4 | 20.7 | 61.7 | 3.7 |  |  | 773.6 | 678.7 | 612.8 | 629.1 | 614.8 | 588.6 | 586.6
3325.3 | 1625.3 | 288.7 | 115.48 | 134.9895 | 194.6 | 198.7 | 211.2 | 209.7 | 312.3 | 35.5 | 20.7 | 61.6 | 2.9 |  |  | 772.4 | 683.3 | 607.8 | 629.1 | 616 | 588.7 | 584.5
3326.3 | 1626.3 | 288.9 | 115.56 | 135.083 | 194.1 | 198.2 | 211.6 | 209.8 | 317.7 | 35.5 | 20.7 | 61.6 | 3 |  |  | 769.3 | 680.8 | 598.2 | 630 | 614.6 | 584 | 579.3
3327.3 | 1627.3 | 289.9 | 115.96 | 135.5506 | 194.4 | 197.7 | 211.3 | 210.2 | 315.8 | 35.3 | 20.7 | 61.6 | 2.7 |  |  | 766.1 | 670.9 | 586.9 | 631.6 | 609.6 | 578 | 574
3328.3 | 1628.3 | 289.4 | 115.76 | 135.3168 | 194.8 | 197.8 | 210.6 | 211 | 310.9 | 35.3 | 20.7 | 61.5 | 2.8 |  |  | 765.5 | 675.8 | 576.1 | 632.6 | 609.2 | 577.2 | 571.7
3329.3 | 1629.3 | 290.1 | 116.04 | 135.6441 | 194.9 | 197.9 | 210.4 | 211.2 | 308.2 | 35.3 | 20.7 | 61.5 | 3.3 |  |  | 763.9 | 679 | 570.5 | 633.8 | 605.4 | 570.5 | 568.7
3330.3 | 1630.3 | 290 | 116 | 135.5973 | 194.6 | 197.8 | 209.9 | 211.8 | 305.8 | 35.1 | 20.7 | 61.5 | 3.3 |  |  | 763.5 | 686.9 | 568.1 | 634.1 | 608.7 | 565.9 | 567.2
3331.3 | 1631.3 | 290.6 | 116.24 | 135.8779 | 194.7 | 198.1 | 210 | 212.2 | 306.2 | 35.1 | 20.7 | 61.5 | 3.1 |  |  | 764.9 | 693.6 | 572.5 | 635.3 | 606.9 | 571.4 | 568
3332.3 | 1632.3 | 289.4 | 115.76 | 135.3168 | 194.7 | 198 | 209.6 | 212 | 310.7 | 35.1 | 20.7 | 61.5 | 3.5 |  |  | 765 | 689.2 | 582.2 | 638.1 | 612.3 | 579.1 | 573.5
3333.3 | 1633.3 | 288.8 | 115.52 | 135.0362 | 194.1 | 198.1 | 209.6 | 212.4 | 310.3 | 35.2 | 20.7 | 61.5 | 3.7 |  |  | 764.2 | 676.1 | 593.7 | 640.6 | 603 | 581.7 | 579
3334.3 | 1634.3 | 289 | 115.6 | 135.1297 | 193.9 | 199.3 | 210 | 212.3 | 309.6 | 35.3 | 20.7 | 61.5 | 3.4 |  |  | 764.8 | 670.5 | 607.6 | 642.9 | 593.2 | 576.3 | 581.1
3335.3 | 1635.3 | 288.9 | 115.56 | 135.083 | 194 | 199.2 | 210.6 | 212.1 | 310.3 | 35.3 | 20.7 | 61.5 | 2.7 |  |  | 765.8 | 676.9 | 616.1 | 645.5 | 600 | 578.4 | 582.7
3336.3 | 1636.3 | 289.9 | 115.96 | 135.5506 | 194.3 | 198.2 | 211.1 | 212.4 | 312.6 | 35.3 | 20.7 | 61.4 | 2.7 |  |  | 765.1 | 675.3 | 622.7 | 646.9 | 595.8 | 572.5 | 579.7
3337.3 | 1637.3 | 290.3 | 116.12 | 135.7376 | 194.5 | 197.5 | 211 | 212.8 | 311.1 | 35.3 | 20.7 | 61.4 | 2.4 |  |  | 762.2 | 679.1 | 610.1 | 648.7 | 592.2 | 564.8 | 572.8
3338.3 | 1638.3 | 289.1 | 115.64 | 135.1765 | 194.9 | 197.5 | 211 | 212.4 | 307.6 | 35.4 | 20.6 | 61.4 | 2.8 |  |  | 758.8 | 671.8 | 594.6 | 648.1 | 584.6 | 554 | 564.3
3339.3 | 1639.3 | 289.6 | 115.84 | 135.4103 | 195.2 | 197.5 | 211.2 | 211.9 | 304.7 | 35.5 | 20.6 | 61.4 | 2.9 |  |  | 757.5 | 663.7 | 590.9 | 647.6 | 578.4 | 551.7 | 563.1
3340.3 | 1640.3 | 290.1 | 116.04 | 135.6441 | 195.2 | 197.7 | 211.6 | 211.5 | 304.1 | 35.6 | 20.6 | 61.5 | 2.2 |  |  | 756.6 | 658 | 583.6 | 647.3 | 586.5 | 553.1 | 565.1
3341.3 | 1641.3 | 289.5 | 115.8 | 135.3635 | 195.3 | 197.7 | 211.3 | 211.7 | 304.7 | 35.7 | 20.6 | 61.7 | 2.7 |  |  | 755.5 | 665.6 | 576.1 | 646.5 | 587.6 | 550.4 | 563.5
3342.3 | 1642.3 | 290.1 | 116.04 | 135.6441 | 195.8 | 196.7 | 210.8 | 212 | 305 | 35.9 | 20.7 | 62 | 2.7 |  |  | 755.4 | 667.1 | 572.4 | 646.9 | 582.2 | 547 | 563.4
3343.3 | 1643.3 | 289.5 | 115.8 | 135.3635 | 195.9 | 197.2 | 210.3 | 212.2 | 306.7 | 35.9 | 20.7 | 62.1 | 2.3 |  |  | 754.7 | 668 | 567.9 | 648 | 583.5 | 553.2 | 562.3
3344.3 | 1644.3 | 291.1 | 116.44 | 136.1117 | 195.4 | 197.8 | 210 | 212.2 | 306.9 | 36.1 | 20.7 | 62 | 2.4 |  |  | 753.4 | 675.4 | 564.3 | 648.6 | 583.5 | 553.8 | 560.1
3345.3 | 1645.3 | 291.3 | 116.52 | 136.2052 | 194.8 | 197.5 | 209.7 | 211.7 | 304.3 | 36.1 | 20.7 | 61.9 | 2.2 |  |  | 750 | 674.8 | 555.1 | 649 | 583.7 | 552 | 556.6
3346.3 | 1646.3 | 290.2 | 116.08 | 135.6908 | 194.8 | 197.6 | 208.7 | 211.8 | 301 | 36.2 | 20.6 | 61.9 | 2.1 |  |  | 747.2 | 672.9 | 547.5 | 648.5 | 587.9 | 547.2 | 554.7
3347.3 | 1647.3 | 289.7 | 115.88 | 135.457 | 194.6 | 196.8 | 208.8 | 212.1 | 299.4 | 36.3 | 20.6 | 61.9 | 2.3 |  |  | 750.5 | 684.1 | 558.5 | 648.6 | 604.5 | 557.9 | 559.8
3348.3 | 1648.3 | 289.3 | 115.72 | 135.27 | 194.8 | 196.7 | 208.9 | 212.3 | 304.2 | 36.3 | 20.6 | 61.8 | 2.4 |  |  | 751.1 | 679.1 | 565.7 | 649.9 | 604.4 | 565.2 | 563.2
3349.3 | 1649.3 | 289.3 | 115.72 | 135.27 | 194.9 | 196.7 | 208.4 | 212.8 | 303.1 | 36.2 | 20.6 | 61.8 | 2.3 |  |  | 749.8 | 674.3 | 567 | 651.4 | 606.5 | 575 | 564.9
3350.3 | 1650.3 | 290.1 | 116.04 | 135.6441 | 194.9 | 197.2 | 208.7 | 213.4 | 303.2 | 36.2 | 20.6 | 61.8 | 2 |  |  | 747.1 | 665.9 | 563.5 | 653.1 | 610.9 | 587 | 567.5
3351.3 | 1651.3 | 290.7 | 116.28 | 135.9246 | 194.5 | 197.2 | 209.8 | 213.3 | 302.1 | 36.1 | 20.6 | 61.8 | 2.1 |  |  | 750.1 | 669.3 | 573.2 | 655.2 | 614.9 | 593.4 | 570.2
3352.3 | 1652.3 | 291 | 116.4 | 136.0649 | 194.5 | 197 | 209.8 | 213.5 | 302.1 | 36.1 | 20.6 | 61.8 | 2.2 |  |  | 752.3 | 691 | 579 | 656.2 | 628.8 | 604.3 | 572.9
3353.3 | 1653.3 | 291.8 | 116.72 | 136.439 | 194.8 | 197 | 209.5 | 213.1 | 300.8 | 36.4 | 20.6 | 61.8 | 2.3 |  |  | 750.5 | 685.6 | 586.9 | 658.1 | 633.3 | 609.7 | 576.5
3354.3 | 1654.3 | 290.4 | 116.16 | 135.7843 | 194.7 | 197.2 | 209.5 | 212.7 | 300.3 | 36.6 | 20.6 | 61.9 | 2.9 |  |  | 751.3 | 681 | 593.7 | 660.3 | 631.5 | 620.5 | 579.2
3355.3 | 1655.3 | 287.4 | 114.96 | 134.3816 | 195 | 197.7 | 208.8 | 213.1 | 301.7 | 36.5 | 20.6 | 62 | 2.8 |  |  | 751.2 | 693 | 591.9 | 662.5 | 639.5 | 632.5 | 582.8
3356.3 | 1656.3 | 285.5 | 114.2 | 133.4932 | 195.7 | 198.1 | 208.1 | 213.2 | 305.6 | 36.4 | 20.6 | 62 | 3.1 |  |  | 750.6 | 694.4 | 595.3 | 664.6 | 639.7 | 636 | 579.6
3357.3 | 1657.3 | 290.2 | 116.08 | 135.6908 | 196.3 | 198.7 | 207.8 | 213.1 | 306.8 | 36.5 | 20.6 | 62.2 | 3.6 |  |  | 751.2 | 674.4 | 604.1 | 666.4 | 621.9 | 626.3 | 578.1
3358.3 | 1658.3 | 288.3 | 115.32 | 134.8024 | 196 | 199.5 | 208.2 | 213.1 | 305.8 | 36.3 | 20.6 | 62.2 | 2.9 |  |  | 753.5 | 675.7 | 609 | 668.4 | 618.8 | 622.4 | 576.3
3359.3 | 1659.3 | 287.6 | 115.04 | 134.4751 | 196 | 200.1 | 208.7 | 212.6 | 306.2 | 36.4 | 20.6 | 62.3 | 3.2 |  |  | 750.6 | 659.1 | 610.7 | 668.9 | 609.9 | 620.5 | 581
3360.3 | 1660.3 | 288.6 | 115.44 | 134.9427 | 196.7 | 200.8 | 208.5 | 212 | 303.3 | 36.6 | 20.6 | 62.3 | 3.3 |  |  | 747.4 | 649.1 | 609.1 | 670 | 601.4 | 613.3 | 578.8
3361.3 | 1661.3 | 288.5 | 115.4 | 134.896 | 196.9 | 200.7 | 208.3 | 211.2 | 301.7 | 36.6 | 20.6 | 62.3 | 3.4 |  |  | 747.4 | 642.9 | 610.1 | 671.1 | 588.3 | 603.2 | 576
3362.3 | 1662.3 | 288.8 | 115.52 | 135.0362 | 196.9 | 199.9 | 208.7 | 210.7 | 300.7 | 36.6 | 20.6 | 62.3 | 3.5 |  |  | 745.4 | 627.7 | 617.4 | 673.3 | 572 | 594.3 | 576.2
3363.3 | 1663.3 | 289.9 | 115.96 | 135.5506 | 196.9 | 199.1 | 209.2 | 210.7 | 299.6 | 36.6 | 20.6 | 62.3 | 3.7 |  |  | 744.2 | 625.7 | 612.2 | 674.9 | 568.3 | 588.8 | 575.3
3364.3 | 1664.3 | 287.6 | 115.04 | 134.4751 | 196.7 | 199.2 | 209.5 | 210 | 299 | 36.7 | 20.6 | 62.3 | 4.1 |  |  | 748.4 | 628 | 625.6 | 676.4 | 567.4 | 594.4 | 579.5
3365.3 | 1665.3 | 288.9 | 115.56 | 135.083 | 196.3 | 199.3 | 209.8 | 209.7 | 302.4 | 36.8 | 20.6 | 62.4 | 3.8 |  |  | 751.1 | 630.4 | 629.8 | 677.7 | 565.7 | 601.4 | 585.4
3366.3 | 1666.3 | 289.4 | 115.76 | 135.3168 | 196.2 | 199.9 | 210.4 | 209.3 | 303.7 | 36.8 | 20.6 | 62.4 | 3.9 |  |  | 748.8 | 646.4 | 620 | 678.2 | 560.9 | 599.3 | 580.5
3367.3 | 1667.3 | 289.6 | 115.84 | 135.4103 | 196.5 | 201.1 | 210.4 | 209.3 | 304.1 | 36.8 | 20.6 | 62.4 | 3.9 |  |  | 745 | 638 | 614.3 | 677.4 | 549 | 587.1 | 573.6
3368.3 | 1668.3 | 289.2 | 115.68 | 135.2233 | 196.4 | 202.2 | 210.7 | 209.5 | 302.3 | 36.9 | 20.6 | 62.6 | 4.4 |  |  | 743.5 | 628.6 | 621.6 | 678.9 | 542 | 589.5 | 575.1
3369.3 | 1669.3 | 289.6 | 115.84 | 135.4103 | 196 | 202.3 | 210.5 | 210.1 | 304.6 | 36.9 | 20.6 | 62.6 | 3.7 |  |  | 744.2 | 637.1 | 620.9 | 680.4 | 558.3 | 600.9 | 581.7
3370.3 | 1670.3 | 290.3 | 116.12 | 135.7376 | 196.5 | 201.5 | 209.7 | 210.3 | 311.1 | 37 | 20.6 | 62.6 | 3.9 |  |  | 748.1 | 663.8 | 613.4 | 680.7 | 578.7 | 611.7 | 584.3
3371.3 | 1671.3 | 289.9 | 115.96 | 135.5506 | 196.3 | 201.3 | 209.8 | 210.1 | 314.5 | 37.1 | 20.6 | 62.6 | 3.5 |  |  | 751.5 | 677.6 | 624.5 | 681.1 | 583.6 | 621.4 | 587.3
3372.3 | 1672.3 | 288.4 | 115.36 | 134.8492 | 196.3 | 201.6 | 210.4 | 209.9 | 315.8 | 37.1 | 20.6 | 62.6 | 3.6 |  |  | 748.8 | 657.8 | 625.4 | 682.1 | 573.8 | 616.6 | 585.1
3373.3 | 1673.3 | 288.4 | 115.36 | 134.8492 | 196.6 | 201.1 | 211.2 | 209.7 | 312.4 | 36.9 | 20.6 | 62.7 | 3.6 |  |  | 743.8 | 634.7 | 614.1 | 681.8 | 555.4 | 596.3 | 577.4
3374.3 | 1674.3 | 288.6 | 115.44 | 134.9427 | 197.7 | 200.3 | 211.4 | 210.2 | 309.4 | 36.9 | 20.6 | 62.8 | 3.6 |  |  | 740.7 | 615 | 606 | 681.9 | 541 | 581.6 | 571.1
3375.3 | 1675.3 | 289.1 | 115.64 | 135.1765 | 197.7 | 199.9 | 211.9 | 210.2 | 308 | 36.9 | 20.6 | 62.8 | 3.2 |  |  | 739.6 | 611.4 | 609.4 | 684.6 | 529 | 571.1 | 570
3376.3 | 1676.3 | 289.4 | 115.76 | 135.3168 | 198.1 | 200.7 | 212.3 | 209.9 | 305.5 | 37 | 20.6 | 62.7 | 2.9 |  |  | 736.6 | 608.1 | 612.6 | 685.6 | 523.3 | 569.4 | 573.3
3377.3 | 1677.3 | 288.6 | 115.44 | 134.9427 | 197.9 | 201.8 | 212.8 | 209.3 | 302.5 | 37.1 | 20.6 | 62.7 | 2.7 |  |  | 735.5 | 613.4 | 610.8 | 685.8 | 526.5 | 574.2 | 575.6
3378.3 | 1678.3 | 289.8 | 115.92 | 135.5038 | 198.2 | 202.6 | 213.8 | 208.7 | 299.7 | 37.1 | 20.6 | 62.8 | 2.7 |  |  | 733.9 | 607.2 | 605.3 | 685.5 | 518.9 | 570.5 | 575.7
3379.3 | 1679.3 | 291 | 116.4 | 136.0649 | 197.9 | 202.4 | 213.8 | 208.6 | 295.9 | 37 | 20.6 | 62.7 | 2.4 |  |  | 732.6 | 600 | 600.3 | 686 | 513.6 | 566.2 | 572.9
3380.3 | 1680.3 | 290.4 | 116.16 | 135.7843 | 197.7 | 201.6 | 213.4 | 208.7 | 294.7 | 37 | 20.6 | 62.7 | 2.6 |  |  | 732.8 | 614.5 | 593.5 | 686.2 | 521.7 | 569.7 | 569.1
3381.3 | 1681.3 | 290.3 | 116.12 | 135.7376 | 197.4 | 201.6 | 213.5 | 208.7 | 296 | 36.9 | 20.6 | 62.7 | 2.5 |  |  | 733.1 | 631.7 | 591.6 | 685.8 | 537.8 | 580.3 | 570.3
3382.3 | 1682.3 | 289.1 | 115.64 | 135.1765 | 197.5 | 202.5 | 213.3 | 208.8 | 300.1 | 37 | 20.6 | 62.7 | 2.6 |  |  | 738.3 | 656.1 | 600.6 | 685.9 | 565.9 | 599.6 | 575.2
3383.3 | 1683.3 | 290.3 | 116.12 | 135.7376 | 197.3 | 203.2 | 212.4 | 208.8 | 302.6 | 36.9 | 20.6 | 62.8 | 2.9 |  |  | 742 | 666.3 | 616.3 | 686.5 | 582.3 | 609.7 | 579.6
3384.3 | 1684.3 | 290.8 | 116.32 | 135.9714 | 196.3 | 202.7 | 212.1 | 209.4 | 302.7 | 37.1 | 20.6 | 62.8 | 3.4 |  |  | 738.6 | 654.4 | 614.6 | 686.9 | 582.1 | 608.9 | 579.7
3385.3 | 1685.3 | 291 | 116.4 | 136.0649 | 196.3 | 201.8 | 212.1 | 210.3 | 301.7 | 37.3 | 20.6 | 62.9 | 3.4 |  |  | 739.4 | 656.3 | 610.5 | 686.6 | 583.5 | 610.4 | 581
3386.3 | 1686.3 | 287.4 | 114.96 | 134.3816 | 196.2 | 201.7 | 211.7 | 210.4 | 298.4 | 37.4 | 20.6 | 62.9 | 3.6 |  |  | 738.8 | 647.1 | 604.8 | 687.4 | 576.5 | 611.9 | 578.4
3387.3 | 1687.3 | 289 | 115.6 | 135.1297 | 196 | 201.2 | 210.8 | 209.8 | 295.4 | 37.4 | 20.6 | 63 | 3.7 |  |  | 735.4 | 640 | 598.9 | 688.4 | 571.5 | 604.7 | 576.8
3388.3 | 1688.3 | 289.1 | 115.64 | 135.1765 | 195.5 | 199.9 | 210.5 | 209.1 | 293.7 | 37.4 | 20.6 | 63.1 | 4 |  |  | 730.5 | 630.6 | 595.6 | 689.6 | 568.6 | 606.2 | 575.9
3389.3 | 1689.3 | 287.1 | 114.84 | 134.2413 | 195 | 199.6 | 210.5 | 208.9 | 293.3 | 37.4 | 20.6 | 63.1 | 3.3 |  |  | 729.8 | 636.3 | 592.3 | 690.5 | 572.9 | 611 | 577
3390.3 | 1690.3 | 286 | 114.4 | 133.727 | 195.2 | 200.4 | 210.2 | 208.8 | 293.2 | 37.5 | 20.6 | 62.9 | 2.6 |  |  | 727.6 | 624.2 | 589.5 | 690.9 | 562.9 | 610.3 | 578.2
3391.3 | 1691.3 | 290 | 116 | 135.5973 | 195.2 | 200.7 | 209.6 | 208.5 | 291.4 | 37.6 | 20.6 | 62.9 | 2.8 |  |  | 728.6 | 621.3 | 592.3 | 691.6 | 562.7 | 617.3 | 583.2
3392.3 | 1692.3 | 288.4 | 115.36 | 134.8492 | 195.3 | 200.5 | 209.1 | 208.3 | 291.4 | 37.6 | 20.6 | 62.9 | 2.6 |  |  | 729.2 | 638.4 | 586.8 | 692.3 | 571.8 | 623.3 | 580.5
3393.3 | 1693.3 | 286.9 | 114.76 | 134.1478 | 195.2 | 200 | 208.2 | 208 | 292.7 | 37.7 | 20.6 | 62.8 | 2.3 |  |  | 729.4 | 651.1 | 583.1 | 693 | 581.4 | 623.7 | 576.4
3394.3 | 1694.3 | 286.5 | 114.6 | 133.9608 | 195.1 | 199.4 | 207.4 | 208.1 | 292.7 | 37.8 | 20.6 | 62.8 | 2.8 |  |  | 726.8 | 658.3 | 581.2 | 694 | 577.8 | 620 | 575.4
3395.3 | 1695.3 | 288.2 | 115.28 | 134.7557 | 195 | 199.9 | 207.8 | 208.1 | 291.6 | 37.7 | 20.6 | 62.8 | 3 |  |  | 721.3 | 656.7 | 574.5 | 695.1 | 572.3 | 608.5 | 570.6
3396.3 | 1696.3 | 289.2 | 115.68 | 135.2233 | 195.5 | 200.1 | 207.7 | 208 | 289 | 37.6 | 20.6 | 62.7 | 3.1 |  |  | 718.6 | 653.2 | 570.9 | 696.4 | 572.9 | 604 | 567.3
3397.3 | 1697.3 | 286.7 | 114.68 | 134.0543 | 195.2 | 199.2 | 207.8 | 208.2 | 290.3 | 37.5 | 20.6 | 62.6 | 2.8 |  |  | 720.1 | 669.1 | 573.7 | 697.4 | 581 | 606.5 | 568.7
3398.3 | 1698.3 | 289.1 | 115.64 | 135.1765 | 194.9 | 199 | 208 | 208.1 | 293.7 | 37.4 | 20.6 | 62.6 | 2.4 |  |  | 719.5 | 681.5 | 569.4 | 698 | 581.5 | 599 | 566.7
3399.3 | 1699.3 | 288.4 | 115.36 | 134.8492 | 194.6 | 199 | 208.2 | 207.8 | 292.9 | 37.5 | 20.6 | 62.6 | 2 |  |  | 715.9 | 677.6 | 565.1 | 698.5 | 581 | 592.4 | 565.5
3400.3 | 1700.3 | 287.6 | 115.04 | 134.4751 | 194.4 | 198.9 | 208.2 | 207.8 | 292.1 | 37.4 | 20.6 | 62.6 | 2.3 |  |  | 712.1 | 666.8 | 552.8 | 699.5 | 568.9 | 584.1 | 563.1
3401.3 | 1701.3 | 289.1 | 115.64 | 135.1765 | 193.8 | 198.5 | 207.8 | 207.7 | 289.4 | 37.3 | 20.6 | 62.5 | 3.2 |  |  | 709.3 | 670.9 | 533.4 | 699.7 | 565.3 | 574.7 | 557.3
3402.3 | 1702.3 | 288.5 | 115.4 | 134.896 | 193.7 | 198 | 208 | 208 | 287.8 | 36.9 | 20.6 | 62.5 | 3.4 |  |  | 708 | 677.5 | 516.8 | 699.7 | 568.9 | 568 | 552.9
3403.3 | 1703.3 | 289.6 | 115.84 | 135.4103 | 193.6 | 197.2 | 208.2 | 208.3 | 285.3 | 36.7 | 20.6 | 62.5 | 3.9 |  |  | 705.8 | 682.8 | 504.5 | 700.5 | 572.7 | 560 | 548.9
3404.3 | 1704.3 | 289.2 | 115.68 | 135.2233 | 194.1 | 196.9 | 208.1 | 207.9 | 285.2 | 36.7 | 20.6 | 62.5 | 3.7 |  |  | 705.8 | 693.2 | 497.9 | 701.4 | 585.1 | 567.1 | 547.2
3405.3 | 1705.3 | 289.5 | 115.8 | 135.3635 | 194.8 | 197.3 | 208.1 | 208 | 289.5 | 36.5 | 20.6 | 62.6 | 3.9 |  |  | 707.2 | 702.3 | 503.8 | 702.7 | 596.4 | 573.7 | 553.2
3406.3 | 1706.3 | 290.2 | 116.08 | 135.6908 | 195.3 | 197.5 | 208.7 | 208.5 | 293.9 | 36.5 | 20.6 | 62.7 | 4 |  |  | 708.5 | 692.4 | 518.5 | 704.5 | 588.9 | 576.7 | 554.6
3407.3 | 1707.3 | 289.4 | 115.76 | 135.3168 | 195.5 | 198.4 | 209.6 | 209 | 295.9 | 36.7 | 20.6 | 62.8 | 3.7 |  |  | 712.2 | 682.3 | 547.5 | 706.4 | 574.3 | 582.4 | 560.1
3408.3 | 1708.3 | 289.7 | 115.88 | 135.457 | 195.6 | 198.7 | 210 | 209.7 | 299.8 | 36.9 | 20.6 | 62.9 | 3.9 |  |  | 715.3 | 680.1 | 569.5 | 708.2 | 573.2 | 590.7 | 563.4
3409.3 | 1709.3 | 289.2 | 115.68 | 135.2233 | 195.7 | 198.8 | 210.2 | 209.5 | 301 | 37 | 20.6 | 63 | 4.6 |  |  | 716.7 | 686.7 | 573.9 | 709.8 | 592.7 | 598.8 | 565.8
3410.3 | 1710.3 | 289.2 | 115.68 | 135.2233 | 195.6 | 198.2 | 210.3 | 209.8 | 302.5 | 37.1 | 20.6 | 63 | 4.3 |  |  | 721.6 | 703.3 | 583 | 711.5 | 604.2 | 609.6 | 568.1
3411.3 | 1711.3 | 289.1 | 115.64 | 135.1765 | 195.5 | 197.7 | 210.9 | 210.2 | 307.3 | 37 | 20.6 | 63 | 4.5 |  |  | 721.4 | 702.1 | 575.9 | 712.9 | 605 | 609.8 | 565.2
3412.3 | 1712.3 | 288.4 | 115.36 | 134.8492 | 195.5 | 196.9 | 210.9 | 210.9 | 307.5 | 37.1 | 20.6 | 63 | 5.1 |  |  | 716.6 | 692.5 | 568.4 | 713.7 | 591 | 600.8 | 559.6
3413.3 | 1713.3 | 290.5 | 116.2 | 135.8311 | 196 | 196.8 | 210.7 | 211.5 | 309 | 37.1 | 20.6 | 63 | 5.3 |  |  | 710.7 | 675.8 | 556.3 | 713.8 | 578.5 | 586.7 | 553.4
3414.3 | 1714.3 | 290.4 | 116.16 | 135.7843 | 196.9 | 197.9 | 211 | 211.4 | 306.9 | 37 | 20.6 | 63.1 | 5 |  |  | 707.9 | 660.9 | 558.7 | 713.6 | 564.8 | 576.2 | 551.1
3415.3 | 1715.3 | 289.6 | 115.84 | 135.4103 | 197.3 | 197.9 | 211.3 | 211.5 | 305.1 | 37 | 20.6 | 63 | 4.7 |  |  | 704.5 | 654.8 | 540.8 | 714.2 | 552 | 560.9 | 546.9
3416.3 | 1716.3 | 290.2 | 116.08 | 135.6908 | 197.4 | 197.8 | 211.6 | 212.1 | 302 | 37 | 20.6 | 62.9 | 4 |  |  | 701.7 | 639.5 | 529.4 | 715 | 540.2 | 548.2 | 542.3
3417.3 | 1717.3 | 290 | 116 | 135.5973 | 196.7 | 198.1 | 212.3 | 212.4 | 298.9 | 37.2 | 20.6 | 62.9 | 3.6 |  |  | 701.9 | 634.4 | 540.8 | 715.1 | 534.5 | 549.7 | 548.4
3418.3 | 1718.3 | 289.2 | 115.68 | 135.2233 | 196.1 | 198.9 | 212.6 | 212.2 | 302 | 37.3 | 20.6 | 62.9 | 3 |  |  | 709.2 | 638.6 | 552.2 | 715.7 | 539.7 | 562.7 | 557.4
3419.3 | 1719.3 | 290.5 | 116.2 | 135.8311 | 196.2 | 199.3 | 212.3 | 211.9 | 303.9 | 37.4 | 20.6 | 62.9 | 3.3 |  |  | 708.2 | 637.1 | 561.9 | 717.6 | 547.1 | 566.1 | 556.6
3420.3 | 1720.3 | 289.1 | 115.64 | 135.1765 | 196.6 | 199.7 | 211.6 | 211.9 | 302.3 | 37.4 | 20.6 | 62.9 | 3.4 |  |  | 708.6 | 642.1 | 567.1 | 718.3 | 539.7 | 567.7 | 557.2
3421.3 | 1721.3 | 289.2 | 115.68 | 135.2233 | 196.1 | 199.5 | 211.4 | 212.3 | 304.7 | 37.3 | 20.6 | 63 | 3.6 |  |  | 709.2 | 642 | 574.7 | 719.6 | 537.7 | 566 | 554.5
3422.3 | 1722.3 | 289.8 | 115.92 | 135.5038 | 195.6 | 200.5 | 211.6 | 212.8 | 309.3 | 37.3 | 20.6 | 63.1 | 3.3 |  |  | 706 | 637.6 | 572.3 | 721.2 | 532.2 | 566.5 | 554.7
3423.3 | 1723.3 | 289.3 | 115.72 | 135.27 | 194.6 | 202 | 211.6 | 213.2 | 307.6 | 37.3 | 20.6 | 63.1 | 3.2 |  |  | 702.6 | 642.5 | 562.9 | 722.1 | 532.8 | 567.6 | 554.5
3424.3 | 1724.3 | 289.1 | 115.64 | 135.1765 | 194.5 | 202.2 | 211.2 | 213.4 | 308 | 37.3 | 20.6 | 63.1 | 3.3 |  |  | 701.1 | 645.9 | 565.7 | 722.6 | 540 | 570 | 556.4
3425.3 | 1725.3 | 290.6 | 116.24 | 135.8779 | 194.5 | 202 | 210.9 | 213.3 | 307.5 | 37.3 | 20.6 | 63.1 | 3.5 |  |  | 701.9 | 634 | 580.5 | 723.4 | 528 | 568.5 | 558.4
3426.3 | 1726.3 | 291 | 116.4 | 136.0649 | 194.8 | 202.1 | 210.8 | 212.7 | 307.1 | 37.3 | 20.6 | 63.1 | 4.1 |  |  | 701.4 | 633 | 571.8 | 723.2 | 521.4 | 561.1 | 554.9
3427.3 | 1727.3 | 290.8 | 116.32 | 135.9714 | 194.9 | 201.7 | 210.6 | 212.2 | 304.6 | 37.4 | 20.6 | 63.2 | 4.4 |  |  | 698.9 | 640.6 | 560.5 | 722.1 | 526.3 | 555.7 | 549.5
3428.3 | 1728.3 | 289.2 | 115.68 | 135.2233 | 194.7 | 201.8 | 210.5 | 212 | 303.2 | 37.5 | 20.6 | 63.3 | 4.4 |  |  | 704.1 | 655 | 575.7 | 722.5 | 532.6 | 563.3 | 550.7
3429.3 | 1729.3 | 289.7 | 115.88 | 135.457 | 194.6 | 202.7 | 210.1 | 211.9 | 307.8 | 37.6 | 20.6 | 63.3 | 4.4 |  |  | 705.1 | 640.4 | 583.8 | 724 | 528.2 | 565 | 554
3430.3 | 1730.3 | 289.7 | 115.88 | 135.457 | 195 | 203.3 | 210.1 | 212.4 | 307.8 | 37.6 | 20.6 | 63.3 | 3.3 |  |  | 702.2 | 621.3 | 598.2 | 725.4 | 520.3 | 557.7 | 556.3
3431.3 | 1731.3 | 294.2 | 117.68 | 137.5611 | 195.4 | 202.9 | 210.2 | 212.8 | 307.8 | 37.6 | 20.6 | 63.3 | 3.1 |  |  | 702.2 | 620.9 | 601.9 | 726.7 | 528.6 | 560.8 | 556
3432.3 | 1732.3 | 295.3 | 118.12 | 138.0755 | 195 | 201.8 | 210.9 | 212.9 | 307.5 | 37.4 | 20.6 | 63.2 | 3.7 |  |  | 702.1 | 636.2 | 587 | 727.4 | 550.2 | 572.4 | 558
3433.3 | 1733.3 | 293.1 | 117.24 | 137.0468 | 194.9 | 201.4 | 211.6 | 212.7 | 305.2 | 37.2 | 20.6 | 63.2 | 4.2 |  |  | 701.5 | 643.6 | 587.1 | 727.7 | 552.6 | 575.8 | 558.5
3434.3 | 1734.3 | 295.5 | 118.2 | 138.169 | 194.4 | 201 | 211.5 | 212.4 | 302.7 | 37.1 | 20.6 | 63.1 | 3.4 |  |  | 702.5 | 637.4 | 587.8 | 728.8 | 550.7 | 585.7 | 560.8
3435.3 | 1735.3 | 301.7 | 120.68 | 141.068 | 194.5 | 200.7 | 211 | 212.2 | 299.1 | 37.2 | 20.6 | 63 | 3.4 |  |  | 702.8 | 636.4 | 599.5 | 730.1 | 539.6 | 585.2 | 562.2
3436.3 | 1736.3 | 310.2 | 124.08 | 145.0424 | 194.4 | 200.7 | 210.5 | 212.3 | 297.4 | 37.2 | 20.6 | 63 | 2.8 |  |  | 702.8 | 633.9 | 596.4 | 732 | 536.5 | 584.7 | 563
3437.3 | 1737.3 | 322.8 | 129.12 | 150.9338 | 193.8 | 201.3 | 210.2 | 212 | 297.4 | 36.9 | 20.6 | 63 | 2.8 |  |  | 702.4 | 651.4 | 591.4 | 732.2 | 543.1 | 586.9 | 560.7
3438.3 | 1738.3 | 338 | 135.2 | 158.041 | 193.5 | 201.1 | 209.9 | 211.6 | 299.6 | 36.8 | 20.6 | 63 | 2.5 |  |  | 709.2 | 664.5 | 609.2 | 733.2 | 549.4 | 597.4 | 563
3439.3 | 1739.3 | 346.4 | 138.56 | 161.9687 | 193.6 | 200.8 | 209.6 | 211.3 | 300.8 | 36.9 | 20.6 | 63 | 2.4 |  |  | 714.2 | 656.7 | 626.7 | 734.7 | 553.2 | 604.9 | 568.4
3440.3 | 1740.3 | 351 | 140.4 | 164.1195 | 194.4 | 201.4 | 209.1 | 211.2 | 301.8 | 37 | 20.6 | 63 | 2.4 |  |  | 717.4 | 659 | 639 | 736 | 561.4 | 605.1 | 574.5
3441.3 | 1741.3 | 351.9 | 140.76 | 164.5403 | 194.4 | 201.9 | 209.1 | 211.4 | 305.5 | 37.1 | 20.6 | 63 | 2.6 |  |  | 720.4 | 653.5 | 650.1 | 737.3 | 557.9 | 606 | 577.5
3442.3 | 1742.3 | 358.3 | 143.32 | 167.5328 | 194.5 | 202.4 | 209.5 | 212.5 | 309.3 | 37.2 | 20.6 | 63 | 2.9 |  |  | 726.3 | 658.7 | 666.4 | 739.3 | 565.1 | 629.7 | 588.7
3443.3 | 1743.3 | 360.8 | 144.32 | 168.7018 | 194.5 | 202.2 | 210.2 | 213.9 | 315 | 37.3 | 20.6 | 63 | 2.7 |  |  | 729.2 | 647.3 | 666.8 | 740.2 | 568.8 | 643.5 | 599.4
3444.3 | 1744.3 | 360.5 | 144.2 | 168.5615 | 194.8 | 202.3 | 211.1 | 215.2 | 314 | 37.4 | 20.5 | 62.9 | 3.1 |  |  | 725.2 | 628.6 | 658.6 | 741.8 | 561.1 | 648 | 602.2
3445.3 | 1745.3 | 359.3 | 143.72 | 168.0004 | 194.9 | 204.6 | 212.1 | 215.8 | 314.2 | 37.4 | 20.5 | 63.1 | 3.8 |  |  | 728 | 645.8 | 665.8 | 743.8 | 576 | 662 | 610.2
3446.3 | 1746.3 | 358 | 143.2 | 167.3925 | 195.5 | 205 | 212.5 | 216.6 | 320.1 | 37.3 | 20.5 | 63.2 | 3.6 |  |  | 731.9 | 683.7 | 657.2 | 745 | 600.6 | 666.2 | 607.1
3447.3 | 1747.3 | 355 | 142 | 165.9898 | 195.8 | 204.3 | 212.9 | 217.6 | 333.8 | 37.3 | 20.5 | 63.2 | 4.6 |  |  | 736.4 | 702.1 | 654.3 | 746.4 | 612.3 | 667.5 | 604
3448.3 | 1748.3 | 353.2 | 141.28 | 165.1482 | 196.6 | 204.2 | 213.6 | 219.6 | 346.3 | 37.3 | 20.5 | 63.3 | 4.4 |  |  | 737.7 | 696 | 658.1 | 748.3 | 604.1 | 664.7 | 606.9
3449.3 | 1749.3 | 351.8 | 140.72 | 164.4936 | 197.3 | 204.7 | 214.1 | 220.6 | 341.9 | 37.3 | 20.5 | 63.4 | 4.2 |  |  | 732.2 | 664.7 | 661.5 | 750.3 | 583.2 | 656.5 | 610.7
3450.3 | 1750.3 | 350.6 | 140.24 | 163.9325 | 198.6 | 205 | 214.7 | 221.4 | 336 | 37.4 | 20.5 | 63.5 | 3.8 |  |  | 725.6 | 631.3 | 676.8 | 752.2 | 562.6 | 649.4 | 612.6
3451.3 | 1751.3 | 350.6 | 140.24 | 163.9325 | 198.7 | 204.9 | 215.6 | 222.2 | 330.9 | 37.5 | 20.5 | 63.6 | 4 |  |  | 725 | 625.6 | 683.4 | 753.7 | 557.4 | 658.6 | 620.1
3452.3 | 1752.3 | 350.6 | 140.24 | 163.9325 | 199.2 | 206.4 | 216.3 | 222.8 | 332.9 | 37.6 | 20.5 | 63.6 | 5.7 |  |  | 732 | 636.6 | 689.2 | 755.7 | 570 | 679.3 | 629.2
3453.3 | 1753.3 | 351.1 | 140.44 | 164.1663 | 198.7 | 208.1 | 216.2 | 222.9 | 334.7 | 37.7 | 20.5 | 63.7 | 6 |  |  | 737.7 | 647.5 | 694.2 | 756.7 | 571.7 | 681.8 | 632.3
3454.3 | 1754.3 | 352 | 140.8 | 164.5871 | 198.8 | 209.6 | 216 | 223.3 | 335.6 | 37.7 | 20.6 | 63.7 | 4.9 |  |  | 743 | 662.9 | 699.6 | 757.6 | 566.7 | 681.4 | 631.6
3455.3 | 1755.3 | 352.8 | 141.12 | 164.9611 | 199.7 | 210.3 | 216.1 | 223.5 | 336.1 | 37.7 | 20.6 | 63.8 | 4.9 |  |  | 748.4 | 661.8 | 715.8 | 758.6 | 557.5 | 679.1 | 636
3456.3 | 1756.3 | 353.3 | 141.32 | 165.1949 | 200.2 | 210.7 | 216.3 | 224.1 | 339.9 | 37.7 | 20.5 | 63.8 | 5.1 |  |  | 754 | 666.8 | 722.5 | 759.2 | 559.1 | 681.2 | 642.5
3457.3 | 1757.3 | 353.6 | 141.44 | 165.3352 | 200.5 | 211.5 | 217 | 225.3 | 344.9 | 37.7 | 20.5 | 63.8 | 5.1 |  |  | 750.7 | 686 | 696.3 | 759.1 | 572.4 | 677.5 | 636.7
3458.3 | 1758.3 | 352.6 | 141.04 | 164.8676 | 200.5 | 212.3 | 217.2 | 225.9 | 347.2 | 37.7 | 20.5 | 63.9 | 5 |  |  | 744.9 | 687.1 | 674.1 | 758.8 | 564.8 | 655.1 | 624.9
3459.3 | 1759.3 | 353.2 | 141.28 | 165.1482 | 200.6 | 212.7 | 217.2 | 225.4 | 347.5 | 37.7 | 20.5 | 64.1 | 4.6 |  |  | 740 | 688.3 | 667.4 | 760.3 | 563.1 | 650.4 | 620.6
3460.3 | 1760.3 | 353.3 | 141.32 | 165.1949 | 201.2 | 212.2 | 217.7 | 225.8 | 343 | 37.8 | 20.5 | 64.2 | 4.5 |  |  | 735.4 | 702.9 | 649.5 | 761.8 | 575.1 | 650.4 | 617.9
3461.3 | 1761.3 | 355 | 142 | 165.9898 | 201.9 | 211.7 | 218.9 | 226.1 | 344.2 | 37.8 | 20.5 | 64.3 | 4.1 |  |  | 736.5 | 715.2 | 643.2 | 762.6 | 595.9 | 652.7 | 618.5
3462.3 | 1762.3 | 357.1 | 142.84 | 166.9717 | 202 | 211.2 | 220.1 | 226.4 | 347.9 | 37.9 | 20.5 | 64.5 | 4.6 |  |  | 737.9 | 735.7 | 640.3 | 763.2 | 613.7 | 657.1 | 619.8
3463.3 | 1763.3 | 357.7 | 143.08 | 167.2523 | 202.9 | 211 | 222 | 227.7 | 350 | 38 | 20.5 | 64.7 | 4.2 |  |  | 736.7 | 734.2 | 641.7 | 764.4 | 616.8 | 650 | 615.9
3464.3 | 1764.3 | 358.6 | 143.44 | 167.6731 | 204.3 | 210.5 | 223.5 | 228.7 | 346.4 | 38 | 20.5 | 64.6 | 4.4 |  |  | 737.5 | 734 | 632.8 | 765.9 | 620.8 | 651.9 | 615.8
3465.3 | 1765.3 | 360.9 | 144.36 | 168.7485 | 205 | 210.3 | 224.2 | 228.6 | 346.4 | 38 | 20.5 | 64.6 | 4.5 |  |  | 740.4 | 742.3 | 626.7 | 767.3 | 653.1 | 670.7 | 620.4
3466.3 | 1766.3 | 362.7 | 145.08 | 169.5902 | 205.4 | 211.5 | 225.1 | 228.4 | 348.9 | 38.1 | 20.5 | 64.7 | 4.1 |  |  | 739.2 | 740.8 | 616.6 | 768.1 | 672.9 | 686 | 626
3467.3 | 1767.3 | 364.7 | 145.88 | 170.5253 | 206.1 | 211.6 | 225.9 | 228.5 | 359.3 | 38.3 | 20.5 | 64.7 | 3.5 |  |  | 737.8 | 725.2 | 624.8 | 769.2 | 663.9 | 682.1 | 625.2
3468.3 | 1768.3 | 366 | 146.4 | 171.1332 | 206.6 | 211.8 | 226.5 | 228.8 | 360.8 | 38.3 | 20.5 | 64.6 | 3.7 |  |  | 739.8 | 715.6 | 632.5 | 771.5 | 649.7 | 680.2 | 627.3
3469.3 | 1769.3 | 366.3 | 146.52 | 171.2734 | 207.7 | 212.3 | 227.3 | 229.7 | 359.4 | 38 | 20.5 | 64.6 | 2.8 |  |  | 737.6 | 707.9 | 633.3 | 774.6 | 646.7 | 684.7 | 632.1
3470.3 | 1770.3 | 367.3 | 146.92 | 171.741 | 208.4 | 214.4 | 228 | 229.9 | 358.8 | 37.8 | 20.5 | 64.6 | 3 |  |  | 735.9 | 707.2 | 630.6 | 775.4 | 654.2 | 688.1 | 630.5
3471.3 | 1771.3 | 368.9 | 147.56 | 172.4891 | 209.2 | 215.5 | 228.8 | 230 | 361.1 | 37.9 | 20.5 | 64.6 | 3.2 |  |  | 738.3 | 716.9 | 631.4 | 775.3 | 665.8 | 698.2 | 633.8
3472.3 | 1772.3 | 370 | 148 | 173.0035 | 210.3 | 216 | 229.6 | 230.6 | 360.6 | 38 | 20.5 | 64.6 | 4.1 |  |  | 741 | 731.4 | 635.6 | 775 | 679.8 | 699.7 | 631.8
3473.3 | 1773.3 | 370.8 | 148.32 | 173.3775 | 211 | 216.5 | 229.3 | 230.8 | 361.6 | 38.1 | 20.5 | 64.9 | 4.9 |  |  | 743.7 | 747.7 | 640.6 | 775 | 672.2 | 693.6 | 629.9
3474.3 | 1774.3 | 371.7 | 148.68 | 173.7984 | 211.3 | 217.5 | 230.5 | 231.2 | 361.8 | 38.2 | 20.5 | 64.9 | 4.1 |  |  | 743.3 | 761.6 | 627.6 | 775.9 | 675.8 | 686.2 | 624.2
3475.3 | 1775.3 | 372.2 | 148.88 | 174.0321 | 212.8 | 217.9 | 231.3 | 231.3 | 366.5 | 38.3 | 20.5 | 64.8 | 4 |  |  | 742 | 768.5 | 612.9 | 777.3 | 670.9 | 679.9 | 618.3
3476.3 | 1776.3 | 371.9 | 148.76 | 173.8919 | 213.6 | 217.3 | 231.3 | 231.5 | 370.7 | 38.3 | 20.5 | 64.9 | 3.6 |  |  | 738.6 | 761.9 | 602.8 | 778.1 | 656.5 | 664.6 | 614
3477.3 | 1777.3 | 371.8 | 148.72 | 173.8451 | 213.8 | 218.2 | 231.3 | 231.9 | 369.5 | 38.3 | 20.5 | 64.9 | 3.7 |  |  | 734.9 | 759.6 | 598.6 | 779.6 | 648.3 | 655.1 | 611.3
3478.3 | 1778.3 | 372.2 | 148.88 | 174.0321 | 214.3 | 219.9 | 231.6 | 232.7 | 371.9 | 38.3 | 20.5 | 64.8 | 3.4 |  |  | 735 | 754.9 | 609.1 | 781.6 | 631.6 | 647.3 | 613.6
3479.3 | 1779.3 | 374.6 | 149.84 | 175.1543 | 214.7 | 220.2 | 232.1 | 233.3 | 374.6 | 38.2 | 20.5 | 64.7 | 4.1 |  |  | 738.3 | 763.8 | 633.7 | 783.4 | 621.7 | 653.6 | 618
3480.3 | 1780.3 | 375.5 | 150.2 | 175.5751 | 215.3 | 220.5 | 232.8 | 233 | 374 | 38.2 | 20.5 | 64.7 | 5.1 |  |  | 739.1 | 754.7 | 666.3 | 785.1 | 613.9 | 651.4 | 621
3481.3 | 1781.3 | 374 | 149.6 | 174.8738 | 215.6 | 220.3 | 234.2 | 233.9 | 371.7 | 38.1 | 20.5 | 64.8 | 4.5 |  |  | 744.7 | 767.5 | 679.1 | 785.6 | 629.2 | 669.7 | 629.8
3482.3 | 1782.3 | 373.7 | 149.48 | 174.7335 | 215.9 | 219.9 | 235.4 | 235.2 | 376.1 | 38.1 | 20.5 | 64.7 | 3.2 |  |  | 751.3 | 777.6 | 676.9 | 785 | 654 | 701.5 | 640.6
3483.3 | 1783.3 | 373.8 | 149.52 | 174.7803 | 216.3 | 219.9 | 236.8 | 235.7 | 374.9 | 38.2 | 20.5 | 64.7 | 2.7 |  |  | 754.8 | 777.3 | 669.8 | 785.2 | 659.8 | 718.1 | 644.4
3484.3 | 1784.3 | 373.6 | 149.44 | 174.6867 | 216.4 | 219.5 | 237.6 | 237 | 377.4 | 38.4 | 20.5 | 64.7 | 3.5 |  |  | 760.7 | 794.8 | 668.3 | 785.9 | 675.1 | 723.9 | 644.5
3485.3 | 1785.3 | 373.1 | 149.24 | 174.453 | 216.4 | 219.7 | 237.5 | 237.1 | 381.9 | 38.4 | 20.5 | 64.8 | 5.1 |  |  | 766.2 | 806.1 | 662.9 | 787.2 | 685.8 | 729.2 | 643.1
3486.3 | 1786.3 | 373.2 | 149.28 | 174.4997 | 216.5 | 220.8 | 238.3 | 238 | 386.4 | 38.5 | 20.5 | 64.9 | 4 |  |  | 768.6 | 808.9 | 667.3 | 788.3 | 685.1 | 723.7 | 643.8
3487.3 | 1787.3 | 373.9 | 149.56 | 174.827 | 218.6 | 222.3 | 238.9 | 238.9 | 387.6 | 38.6 | 20.5 | 64.9 | 3.9 |  |  | 765.4 | 794.6 | 663.3 | 789.7 | 681.2 | 705.9 | 642.2
3488.3 | 1788.3 | 374.4 | 149.76 | 175.0608 | 220.6 | 223.3 | 239 | 238.7 | 389.3 | 38.6 | 20.5 | 65 | 3.5 |  |  | 760.5 | 783.9 | 653.1 | 790.8 | 677.2 | 698.6 | 637.5
3489.3 | 1789.3 | 375 | 150 | 175.3414 | 221.3 | 224.1 | 238.9 | 238.3 | 390.1 | 38.7 | 20.5 | 65.1 | 2.9 |  |  | 758.8 | 788 | 650.8 | 791.8 | 679.7 | 690.6 | 635.3
3490.3 | 1790.3 | 375.7 | 150.28 | 175.6687 | 221.2 | 224.3 | 239.7 | 238.9 | 398.5 | 38.6 | 20.5 | 65.2 | 3.1 |  |  | 760.8 | 799 | 650.5 | 792.7 | 674.2 | 695.8 | 636.7
3491.3 | 1791.3 | 375.3 | 150.12 | 175.4816 | 221.4 | 225.1 | 240.4 | 239.4 | 400.1 | 38.5 | 20.5 | 65.4 | 3.1 |  |  | 760.8 | 788.3 | 648.6 | 795.1 | 678.1 | 692.5 | 632.2
3492.3 | 1792.3 | 375.9 | 150.36 | 175.7622 | 222.2 | 227.2 | 240.6 | 239.1 | 401.8 | 38.4 | 20.5 | 65.6 | 2.8 |  |  | 762 | 770.7 | 660.7 | 797.5 | 661.9 | 679.9 | 632.5
3493.3 | 1793.3 | 375.7 | 150.28 | 175.6687 | 222.2 | 227.7 | 239.8 | 238.7 | 402.4 | 38.3 | 20.5 | 65.7 | 3 |  |  | 759.6 | 760.2 | 656.3 | 797.4 | 644.4 | 672.3 | 629
3494.3 | 1794.3 | 376.4 | 150.56 | 175.996 | 221.7 | 227.4 | 239.4 | 238.7 | 393.8 | 38.3 | 20.5 | 65.9 | 3.6 |  |  | 758.1 | 771.1 | 655.6 | 797.5 | 644.9 | 671.9 | 629.1
3495.3 | 1795.3 | 376.6 | 150.64 | 176.0895 | 220.9 | 227.1 | 239.1 | 239.1 | 396.4 | 38 | 20.5 | 65.9 | 3.5 |  |  | 760.3 | 783.7 | 652.7 | 797.8 | 665.9 | 689.6 | 631.2
3496.3 | 1796.3 | 376.4 | 150.56 | 175.996 | 220.7 | 226.4 | 239.8 | 239.3 | 395.5 | 37.8 | 20.5 | 65.8 | 3.6 |  |  | 763.4 | 773 | 656.4 | 798.5 | 682.1 | 705.3 | 639.5
3497.3 | 1797.3 | 376.8 | 150.72 | 176.183 | 221.2 | 226.8 | 240.4 | 239.3 | 393.6 | 37.8 | 20.5 | 65.6 | 4.2 |  |  | 764.6 | 772.5 | 666.4 | 798.6 | 677.8 | 702.9 | 645
3498.3 | 1798.3 | 376.2 | 150.48 | 175.9024 | 221.3 | 226.4 | 240.6 | 239.5 | 391.9 | 38 | 20.5 | 65.5 | 3.7 |  |  | 763.1 | 765.8 | 677.7 | 798.8 | 665.9 | 686.4 | 641.7
3499.3 | 1799.3 | 376.5 | 150.6 | 176.0427 | 221.7 | 226.4 | 241.3 | 239.5 | 387.4 | 38.1 | 20.5 | 65.4 | 3.7 |  |  | 761.1 | 760.6 | 673.8 | 798.4 | 650.6 | 680.4 | 636.1
3500.3 | 1800.3 | 376.7 | 150.68 | 176.1362 | 221.9 | 226.8 | 241.7 | 239.5 | 391.7 | 38.2 | 20.5 | 65.4 | 4.1 |  |  | 761.7 | 768.1 | 671.2 | 797.8 | 642.4 | 679.6 | 634.7
3501.3 | 1801.3 | 377 | 150.8 | 176.2765 | 221.8 | 227.7 | 241.7 | 240.2 | 389.6 | 38.3 | 20.5 | 65.4 | 4.7 |  |  | 760.3 | 767 | 660.4 | 797.1 | 641.1 | 667.2 | 631.4
3502.3 | 1802.3 | 376.8 | 150.72 | 176.183 | 221.6 | 228.5 | 240.8 | 240.3 | 382.5 | 38.4 | 20.5 | 65.6 | 4.9 |  |  | 758.6 | 757.8 | 659.3 | 796.4 | 630.1 | 652 | 628.1
3503.3 | 1803.3 | 376.7 | 150.68 | 176.1362 | 221.7 | 228.5 | 239.9 | 240 | 377 | 38.4 | 20.5 | 65.7 | 6.3 |  |  | 755.3 | 732.5 | 649.4 | 794.8 | 610.8 | 635.3 | 624.3
3504.3 | 1804.3 | 376.6 | 150.64 | 176.0895 | 222 | 228.3 | 239.6 | 239.9 | 372 | 38.4 | 20.5 | 65.9 | 6.3 |  |  | 752.1 | 717.3 | 663.2 | 793.3 | 594.6 | 628.8 | 629.6
3505.3 | 1805.3 | 377.3 | 150.92 | 176.4168 | 221.4 | 227.7 | 240.2 | 240.2 | 367.2 | 38.4 | 20.5 | 66.2 | 6.5 |  |  | 753.1 | 728.7 | 662.4 | 793.3 | 597.3 | 621.5 | 631.4
3506.3 | 1806.3 | 377.4 | 150.96 | 176.4635 | 220.7 | 226.2 | 239.8 | 240.2 | 363.7 | 38.3 | 20.5 | 66.4 | 5.1 |  |  | 747.6 | 725.6 | 637.7 | 792.7 | 591.3 | 598.1 | 623.1
3507.3 | 1807.3 | 377.7 | 151.08 | 176.6038 | 221.2 | 225.4 | 239.5 | 239.9 | 360.1 | 38.1 | 20.5 | 66.6 | 4.8 |  |  | 743.3 | 719 | 623.4 | 792.3 | 581.9 | 589.1 | 618.4
3508.3 | 1808.3 | 377.4 | 150.96 | 176.4635 | 221.4 | 225.1 | 239.6 | 239.9 | 361.2 | 38.1 | 20.5 | 66.8 | 5.8 |  |  | 740.5 | 705.4 | 624 | 791.8 | 569.6 | 578.7 | 615.7
3509.3 | 1809.3 | 377.9 | 151.16 | 176.6973 | 221.9 | 225.6 | 239.3 | 239.4 | 363.1 | 38 | 20.5 | 67 | 6.3 |  |  | 738.7 | 716.1 | 614.8 | 790.5 | 575.2 | 583 | 616.1
3510.3 | 1810.3 | 378.7 | 151.48 | 177.0714 | 222 | 226.3 | 239.1 | 238.9 | 369.1 | 37.9 | 20.5 | 67 | 6.3 |  |  | 737 | 700.7 | 606.2 | 788.5 | 567.9 | 572.9 | 612
3511.3 | 1811.3 | 378.3 | 151.32 | 176.8844 | 222.1 | 227 | 239.3 | 239.5 | 363.4 | 38 | 20.5 | 67.1 | 5.6 |  |  | 734.9 | 685.1 | 603.3 | 786.5 | 555 | 559.6 | 606.3
3512.3 | 1812.3 | 378.8 | 151.52 | 177.1181 | 222.2 | 227.8 | 239.7 | 241.1 | 358.1 | 38.1 | 20.5 | 67.2 | 4.5 |  |  | 732.1 | 678.3 | 625.8 | 786.4 | 543.9 | 561.5 | 608
3513.3 | 1813.3 | 378.6 | 151.44 | 177.0246 | 222.1 | 228.7 | 239.7 | 241.1 | 359.6 | 38.1 | 20.5 | 67.3 | 4.2 |  |  | 730.3 | 667.8 | 654.2 | 787.8 | 529.9 | 565.9 | 613.8
3514.3 | 1814.3 | 378.3 | 151.32 | 176.8844 | 222 | 229.6 | 239 | 240.6 | 355.6 | 38.1 | 20.5 | 67.2 | 4.1 |  |  | 731.4 | 661.7 | 675 | 789.3 | 529.2 | 582.6 | 620.9
3515.3 | 1815.3 | 379.1 | 151.64 | 177.2584 | 222 | 229.6 | 238.4 | 240.8 | 359 | 38.2 | 20.5 | 67.1 | 4.2 |  |  | 733.4 | 671.6 | 681.6 | 790.4 | 538.3 | 593.6 | 629
3516.3 | 1816.3 | 379 | 151.6 | 177.2117 | 221.6 | 229.4 | 239.5 | 240.8 | 361 | 38.1 | 20.4 | 67 | 4 |  |  | 734.2 | 677.3 | 680.1 | 791.1 | 553.1 | 613.8 | 627.2
3517.3 | 1817.3 | 379.4 | 151.76 | 177.3987 | 221 | 229.1 | 240.5 | 240.9 | 360.3 | 38.2 | 20.5 | 67 | 2.6 |  |  | 734 | 675.7 | 673.2 | 791.2 | 553.8 | 613.8 | 624.3
3518.3 | 1818.3 | 379.6 | 151.84 | 177.4922 | 222.3 | 229.1 | 240.3 | 240.8 | 357.4 | 38.2 | 20.5 | 67 | 2.6 |  |  | 732.2 | 684.4 | 667 | 790.7 | 565.6 | 618.7 | 623.4
3519.3 | 1819.3 | 379.7 | 151.88 | 177.539 | 223.1 | 229.4 | 239.7 | 240.5 | 358.4 | 38.2 | 20.4 | 67 | 3.5 |  |  | 734.9 | 694.8 | 674.9 | 790.7 | 574.7 | 625.5 | 627.2
3520.3 | 1820.3 | 380.6 | 152.24 | 177.9598 | 222.8 | 230.1 | 239.3 | 239.5 | 367.7 | 38.2 | 20.4 | 67.1 | 3.4 |  |  | 737 | 710.4 | 659 | 789.4 | 574.9 | 609.3 | 621.1
3521.3 | 1821.3 | 380.5 | 152.2 | 177.913 | 222.8 | 230.8 | 238.9 | 238.9 | 368.9 | 38.2 | 20.4 | 67.2 | 3.9 |  |  | 735.3 | 708.1 | 645.7 | 788.5 | 562.4 | 585.2 | 611.3
3522.3 | 1822.3 | 380.1 | 152.04 | 177.726 | 223.2 | 230.7 | 240.7 | 238.1 | 365 | 38.1 | 20.4 | 67.3 | 5 |  |  | 733 | 707.8 | 635.6 | 788.2 | 557.5 | 582 | 609.4
3523.3 | 1823.3 | 380.5 | 152.2 | 177.913 | 223.5 | 231 | 242 | 237.4 | 360.2 | 38.2 | 20.4 | 67.5 | 4.3 |  |  | 729.1 | 702.4 | 626 | 787.9 | 554 | 579.9 | 609.9
3524.3 | 1824.3 | 380.6 | 152.24 | 177.9598 | 223.3 | 230.3 | 241.7 | 237.3 | 355.8 | 38.1 | 20.4 | 67.6 | 4.6 |  |  | 723.9 | 700.2 | 625.7 | 789.5 | 555.7 | 585.1 | 613.8
3525.3 | 1825.3 | 380.9 | 152.36 | 178.1001 | 223.5 | 228.8 | 241.4 | 238 | 355.8 | 38.1 | 20.4 | 67.6 | 4.9 |  |  | 718.7 | 694.1 | 623.3 | 791.1 | 546.6 | 582.4 | 614.1
3526.3 | 1826.3 | 381.1 | 152.44 | 178.1936 | 223.2 | 227.9 | 241.5 | 238.2 | 353.5 | 38.2 | 20.4 | 67.5 | 4 |  |  | 714.5 | 693.4 | 608.9 | 791.6 | 541.7 | 574.2 | 608.3
3527.3 | 1827.3 | 380.5 | 152.2 | 177.913 | 222 | 227.4 | 241.3 | 238.6 | 349.8 | 38.2 | 20.4 | 67.5 | 3.9 |  |  | 715.1 | 708.3 | 606.8 | 791.4 | 548.3 | 588 | 605.4
3528.3 | 1828.3 | 381 | 152.4 | 178.1468 | 220.7 | 227.1 | 241.2 | 239.3 | 349.3 | 38.2 | 20.4 | 67.4 | 3.5 |  |  | 720.8 | 724.5 | 617.3 | 791.5 | 560.5 | 595.7 | 606.4
3529.3 | 1829.3 | 381.4 | 152.56 | 178.3339 | 219.8 | 227.5 | 241.1 | 239.5 | 353.8 | 38.2 | 20.4 | 67.4 | 3.4 |  |  | 723.6 | 733.6 | 612.9 | 791.7 | 568.8 | 597 | 607
3530.3 | 1830.3 | 381.7 | 152.68 | 178.4741 | 219.8 | 227.8 | 240.8 | 239.3 | 354.1 | 38.1 | 20.4 | 67.3 | 3.4 |  |  | 722.1 | 738.1 | 601.7 | 790.9 | 566.7 | 588.8 | 601.6
3531.3 | 1831.3 | 382.3 | 152.92 | 178.7547 | 219.9 | 228.2 | 241.3 | 239.9 | 352.7 | 38.1 | 20.4 | 67.2 | 4.2 |  |  | 721.1 | 721.9 | 597.9 | 791.7 | 558.9 | 580.4 | 598.2
3532.3 | 1832.3 | 382 | 152.8 | 178.6144 | 220.1 | 228.5 | 241.2 | 240.1 | 349.1 | 38.2 | 20.4 | 67.2 | 4.1 |  |  | 720.5 | 712.9 | 606.3 | 791.5 | 558.1 | 586.7 | 599.2
3533.3 | 1833.3 | 382 | 152.8 | 178.6144 | 220.2 | 228.1 | 241.1 | 240.3 | 353.2 | 38.3 | 20.4 | 67.2 | 3.9 |  |  | 724.7 | 723.4 | 614.2 | 793.1 | 587.3 | 608.5 | 605.8
3534.3 | 1834.3 | 382.7 | 153.08 | 178.9417 | 220.1 | 228.7 | 241 | 240.4 | 354.4 | 38.4 | 20.4 | 67.4 | 4.8 |  |  | 730.6 | 733.2 | 621.3 | 794.2 | 587.4 | 618 | 609.9
3535.3 | 1835.3 | 382.8 | 153.12 | 178.9885 | 219.6 | 229.8 | 240.5 | 240.3 | 359.6 | 38.5 | 20.4 | 67.5 | 6.1 |  |  | 734.9 | 737.8 | 625.3 | 796 | 589 | 625.1 | 610.9
3536.3 | 1836.3 | 383.1 | 153.24 | 179.1287 | 219.6 | 230.1 | 241.2 | 240.4 | 362.5 | 38.6 | 20.4 | 67.7 | 6.1 |  |  | 735.2 | 722.5 | 640.4 | 796.5 | 582.4 | 614.3 | 613
3537.3 | 1837.3 | 381.7 | 152.68 | 178.4741 | 219.9 | 230.1 | 242 | 241.3 | 362.4 | 38.6 | 20.4 | 67.8 | 5.3 |  |  | 732.5 | 714.3 | 631.5 | 794.9 | 573.5 | 601.2 | 608.5
3538.3 | 1838.3 | 382.1 | 152.84 | 178.6612 | 220.7 | 229.8 | 242.4 | 241.6 | 361.1 | 38.6 | 20.4 | 67.9 | 6 |  |  | 728.5 | 703.3 | 624.6 | 794.6 | 563.5 | 590.8 | 600.7
3539.3 | 1839.3 | 382.4 | 152.96 | 178.8014 | 220.4 | 230.1 | 242.4 | 241.8 | 355.2 | 38.6 | 20.4 | 67.8 | 4.9 |  |  | 725 | 701.8 | 611.9 | 794 | 564.9 | 584.8 | 597.3
3540.3 | 1840.3 | 382.6 | 153.04 | 178.8949 | 219.8 | 230.4 | 242.1 | 241.3 | 349.6 | 38.6 | 20.4 | 67.8 | 3.7 |  |  | 724 | 702.3 | 614.6 | 793.9 | 561.8 | 578.9 | 597.1
3541.3 | 1841.3 | 383.1 | 153.24 | 179.1287 | 220.4 | 230.3 | 241.9 | 240.6 | 348 | 38.5 | 20.4 | 67.8 | 3.3 |  |  | 723.4 | 698.8 | 624 | 794.1 | 551.7 | 577.5 | 597.7
3542.3 | 1842.3 | 382.7 | 153.08 | 178.9417 | 220.3 | 229.7 | 241.4 | 240.3 | 352.4 | 38.5 | 20.4 | 67.9 | 3.5 |  |  | 721.9 | 705.7 | 644.2 | 794.8 | 557.9 | 584.7 | 598
3543.3 | 1843.3 | 383.1 | 153.24 | 179.1287 | 219.5 | 229.6 | 240.6 | 240.4 | 353.2 | 38.5 | 20.4 | 67.8 | 3.2 |  |  | 722.9 | 708.7 | 645.6 | 796.3 | 570.3 | 593.8 | 598.1
3544.3 | 1844.3 | 383.6 | 153.44 | 179.3625 | 218.7 | 229.9 | 240.7 | 240.7 | 352.8 | 38.5 | 20.4 | 67.9 | 3.9 |  |  | 722.3 | 717.6 | 626.5 | 796.5 | 572.5 | 588 | 596.3
3545.3 | 1845.3 | 383.9 | 153.56 | 179.5028 | 219.1 | 229 | 241.5 | 240.6 | 352.4 | 38.6 | 20.4 | 68 | 4.5 |  |  | 722.8 | 736 | 624.6 | 796.3 | 575.9 | 593.1 | 595.8
3546.3 | 1846.3 | 383.6 | 153.44 | 179.3625 | 219.5 | 228 | 241.8 | 240.2 | 351.3 | 38.7 | 20.4 | 68.2 | 4.4 |  |  | 721.4 | 742.1 | 611.3 | 797.2 | 588.9 | 593.1 | 594
3547.3 | 1847.3 | 383.9 | 153.56 | 179.5028 | 219.6 | 227.2 | 241.3 | 240.1 | 352.3 | 38.8 | 20.4 | 68.3 | 4.1 |  |  | 716.6 | 748.5 | 595.9 | 797.8 | 597.6 | 579.2 | 589.5
3548.3 | 1848.3 | 383.7 | 153.48 | 179.4093 | 219.6 | 226.3 | 241.3 | 239.9 | 356.1 | 38.9 | 20.4 | 68.3 | 4.2 |  |  | 713.8 | 759.9 | 593.8 | 798.6 | 604.5 | 581 | 586.9
3549.3 | 1849.3 | 383.4 | 153.36 | 179.269 | 220.3 | 226.7 | 241.2 | 240.2 | 357.5 | 39 | 20.4 | 68.5 | 4.5 |  |  | 712.5 | 747.5 | 587.4 | 799.9 | 596.2 | 574.9 | 586.3
3550.3 | 1850.3 | 384.2 | 153.68 | 179.6431 | 221.2 | 226.9 | 240.8 | 239.8 | 355.2 | 39.1 | 20.4 | 68.8 | 4.5 |  |  | 709.6 | 742.3 | 588.1 | 801 | 586.9 | 561.7 | 581.6
3551.3 | 1851.3 | 384.3 | 153.72 | 179.6898 | 222.3 | 227.1 | 240.3 | 239.8 | 355 | 39 | 20.4 | 69 | 4.1 |  |  | 707.3 | 756.7 | 574 | 800.6 | 586.3 | 557.6 | 578.1
3552.3 | 1852.3 | 384.3 | 153.72 | 179.6898 | 223.9 | 227.2 | 241 | 240 | 364.3 | 39 | 20.4 | 68.7 | 4.2 |  |  | 710.1 | 782 | 579.9 | 800.1 | 596.6 | 562.8 | 582.5
3553.3 | 1853.3 | 383.1 | 153.24 | 179.1287 | 224.3 | 226.5 | 241.6 | 240.3 | 369.1 | 39.1 | 20.4 | 68.9 | 5.5 |  |  | 712.1 | 772.2 | 602.2 | 800.2 | 599.8 | 566 | 587.5
3554.3 | 1854.3 | 383.3 | 153.32 | 179.2222 | 225 | 226.2 | 242 | 241 | 372.1 | 39.2 | 20.4 | 69.1 | 5 |  |  | 716.4 | 770.5 | 622.8 | 800.2 | 604.9 | 577.7 | 594.8
3555.3 | 1855.3 | 383.1 | 153.24 | 179.1287 | 225.1 | 225.8 | 242.2 | 241.7 | 377.8 | 39.3 | 20.4 | 69.1 | 5.3 |  |  | 718.1 | 770.2 | 614.2 | 799.7 | 609.3 | 577.5 | 591.8
3556.3 | 1856.3 | 384 | 153.6 | 179.5496 | 225.6 | 226 | 242.5 | 241.6 | 380.8 | 39.3 | 20.4 | 69.3 | 5.9 |  |  | 715.9 | 762.2 | 601.1 | 798.6 | 616.5 | 577.8 | 587.5
3557.3 | 1857.3 | 383.7 | 153.48 | 179.4093 | 226.2 | 226.8 | 242.9 | 242.1 | 373.6 | 39.3 | 20.4 | 69.4 | 4.8 |  |  | 712.4 | 764.5 | 581.4 | 798.9 | 623.1 | 580.3 | 585
3558.3 | 1858.3 | 384.6 | 153.84 | 179.8301 | 226.6 | 227.4 | 242.8 | 243 | 367.4 | 39.4 | 20.4 | 69.4 | 3.5 |  |  | 708.8 | 764.3 | 559.5 | 799.3 | 617.9 | 570.4 | 579.8
3559.3 | 1859.3 | 384.1 | 153.64 | 179.5963 | 226.8 | 227.1 | 243.1 | 243.3 | 365.5 | 39.7 | 20.4 | 69.4 | 3.1 |  |  | 703.9 | 751.2 | 540 | 799.1 | 604 | 550.9 | 572.9
3560.3 | 1860.3 | 384.6 | 153.84 | 179.8301 | 226.9 | 226.9 | 243 | 243.1 | 360.2 | 39.5 | 20.4 | 69.2 | 4.3 |  |  | 699.1 | 737.7 | 535.2 | 797.5 | 589.7 | 536.5 | 567.4
3561.3 | 1861.3 | 384.3 | 153.72 | 179.6898 | 226.9 | 227.7 | 243.6 | 243.9 | 355.3 | 39.2 | 20.4 | 69 | 5 |  |  | 696.1 | 722.1 | 545.4 | 796.2 | 580.1 | 539.3 | 567.5
3562.3 | 1862.3 | 385.1 | 154.04 | 180.0639 | 226.5 | 228.5 | 243.9 | 244.1 | 350.7 | 39 | 20.4 | 68.9 | 4.4 |  |  | 694.5 | 728.5 | 542.9 | 795.6 | 588.8 | 549 | 567.8
3563.3 | 1863.3 | 385.2 | 154.08 | 180.1106 | 226 | 228.8 | 243.8 | 243.2 | 354.5 | 39 | 20.4 | 68.9 | 4.7 |  |  | 694.6 | 739.8 | 536.9 | 796.7 | 601.7 | 551.6 | 565
3564.3 | 1864.3 | 386 | 154.4 | 180.4847 | 226.1 | 229.2 | 244.1 | 243.1 | 357.9 | 39 | 20.4 | 68.7 | 4 |  |  | 694.2 | 746.8 | 543.9 | 797.6 | 592.5 | 549.5 | 562.4
3565.3 | 1865.3 | 385.2 | 154.08 | 180.1106 | 226 | 230.2 | 243.6 | 244.1 | 362 | 39 | 20.4 | 68.7 | 3.4 |  |  | 695.6 | 740.4 | 574.8 | 797.9 | 581.6 | 546.2 | 565.2
3566.3 | 1866.3 | 385.6 | 154.24 | 180.2977 | 227.2 | 230.2 | 244.2 | 244.7 | 366.5 | 39.1 | 20.4 | 68.7 | 2.9 |  |  | 702.1 | 740.3 | 609.4 | 800.8 | 582.5 | 564.5 | 576.8
3567.3 | 1867.3 | 385.2 | 154.08 | 180.1106 | 226.9 | 230.6 | 244.9 | 244.6 | 369.2 | 39.1 | 20.4 | 68.9 | 3.2 |  |  | 711.1 | 735.7 | 642.2 | 801.4 | 584.7 | 584.3 | 590.3
3568.3 | 1868.3 | 386.1 | 154.44 | 180.5315 | 226.9 | 232.5 | 245.3 | 244.1 | 370.8 | 39.1 | 20.4 | 69 | 4.3 |  |  | 713.4 | 721 | 653.3 | 800.4 | 569.7 | 578.1 | 590.2
3569.3 | 1869.3 | 386 | 154.4 | 180.4847 | 226.6 | 232.4 | 245.4 | 244.8 | 370.4 | 39.2 | 20.4 | 69.2 | 5.2 |  |  | 713.8 | 697.2 | 639.6 | 798.7 | 549.5 | 561.4 | 582.5
3570.3 | 1870.3 | 385.8 | 154.32 | 180.3912 | 226.4 | 233.1 | 245.4 | 245.3 | 365.9 | 39.2 | 20.4 | 69.3 | 5.6 |  |  | 708 | 670.3 | 638.1 | 798.8 | 530.4 | 548.5 | 575.8
3571.3 | 1871.3 | 385.3 | 154.12 | 180.1574 | 226 | 233.7 | 246.4 | 245.8 | 360.1 | 39.1 | 20.4 | 69.3 | 5.8 |  |  | 706 | 660.9 | 650.2 | 800.4 | 520.6 | 557 | 580.6
3572.3 | 1872.3 | 385.2 | 154.08 | 180.1106 | 226 | 234.4 | 246.8 | 245 | 356.1 | 39.1 | 20.4 | 69.1 | 4.5 |  |  | 707.7 | 664.5 | 659.6 | 802.2 | 521.3 | 559.2 | 589.3
3573.3 | 1873.3 | 385.5 | 154.2 | 180.2509 | 226.2 | 234.2 | 246.7 | 244.2 | 358.9 | 39.1 | 20.4 | 68.9 | 4 |  |  | 714.3 | 673.7 | 663.5 | 801.9 | 520.7 | 561.8 | 588.8
3574.3 | 1874.3 | 386.4 | 154.56 | 180.6717 | 225.9 | 233.4 | 246.2 | 244.4 | 367.9 | 39 | 20.4 | 69 | 5.9 |  |  | 720.2 | 682.9 | 668.8 | 801.3 | 521.5 | 570.9 | 586.7
3575.3 | 1875.3 | 386.4 | 154.56 | 180.6717 | 226.1 | 232.9 | 245.9 | 244.4 | 368.3 | 39 | 20.4 | 69.3 | 7.8 |  |  | 723.1 | 692.9 | 667.2 | 802.9 | 521.6 | 567.7 | 585.2
3576.3 | 1876.3 | 386.4 | 154.56 | 180.6717 | 225.9 | 234.2 | 245.9 | 244 | 370.8 | 39 | 20.4 | 69.4 | 7.5 |  |  | 724.5 | 694.5 | 653.3 | 802.4 | 525.7 | 566.7 | 581.9
3577.3 | 1877.3 | 387.1 | 154.84 | 180.999 | 225.6 | 235.8 | 246.7 | 243.5 | 370.8 | 38.9 | 20.4 | 69.5 | 6.7 |  |  | 724.2 | 692.2 | 657.5 | 800.9 | 517.1 | 556 | 575.7
3578.3 | 1878.3 | 387.4 | 154.96 | 181.1393 | 226 | 236.8 | 247.4 | 242.9 | 369.5 | 38.9 | 20.4 | 69.3 | 6.9 |  |  | 725 | 692.1 | 666.2 | 799.7 | 515.5 | 560.6 | 577.3
3579.3 | 1879.3 | 387.6 | 155.04 | 181.2328 | 226.2 | 236.7 | 248.2 | 242 | 365.6 | 38.9 | 20.4 | 69.2 | 7 |  |  | 722.1 | 688.6 | 646.5 | 796.8 | 507.1 | 547.5 | 574
3580.3 | 1880.3 | 385.6 | 154.24 | 180.2977 | 225.3 | 236.6 | 249.4 | 241.8 | 361.8 | 39 | 20.4 | 69.2 | 7.3 |  |  | 717.1 | 669.5 | 624.6 | 793.9 | 501.9 | 540.2 | 568.5
3581.3 | 1881.3 | 385.6 | 154.24 | 180.2977 | 225.1 | 235.9 | 249.8 | 242.1 | 356 | 39 | 20.4 | 69.1 | 7.6 |  |  | 715.3 | 676.4 | 612 | 793.2 | 509 | 553.4 | 572.3
3582.3 | 1882.3 | 386.5 | 154.6 | 180.7185 | 224.8 | 234.9 | 249.7 | 242.9 | 359 | 39.2 | 20.4 | 69 | 7.5 |  |  | 712.2 | 680.2 | 590.2 | 792.3 | 519 | 547.9 | 569.2
3583.3 | 1883.3 | 387.1 | 154.84 | 180.999 | 224.5 | 234.4 | 249.2 | 243.3 | 361.6 | 39.2 | 20.4 | 69 | 7.7 |  |  | 709.1 | 683.7 | 587.7 | 792 | 521.4 | 549.7 | 567
3584.3 | 1884.3 | 387.3 | 154.92 | 181.0926 | 224.5 | 235.3 | 248.1 | 243.7 | 364.9 | 39.1 | 20.4 | 69.2 | 7.6 |  |  | 709.3 | 701.6 | 608.6 | 792.4 | 532.2 | 551.1 | 568.5
3585.3 | 1885.3 | 386.5 | 154.6 | 180.7185 | 224.3 | 235.3 | 247.5 | 244.2 | 364.7 | 39.1 | 20.4 | 69.2 | 7.7 |  |  | 709.5 | 716.7 | 606 | 791.7 | 556.9 | 572.4 | 570.7
3586.3 | 1886.3 | 386.8 | 154.72 | 180.8588 | 224.2 | 235.5 | 247 | 245.1 | 363.8 | 38.9 | 20.4 | 69.2 | 7.7 |  |  | 709.7 | 730.5 | 611 | 790.3 | 580.8 | 578.9 | 572.8
3587.3 | 1887.3 | 386.2 | 154.48 | 180.5782 | 224.8 | 235.6 | 247.1 | 245.8 | 367.6 | 38.7 | 20.4 | 69.2 | 7 |  |  | 715.9 | 748.1 | 619.8 | 789.4 | 598 | 592.9 | 579.1
3588.3 | 1888.3 | 386.7 | 154.68 | 180.812 | 225.2 | 235.8 | 246.8 | 246 | 367.3 | 38.6 | 20.4 | 69.3 | 6.6 |  |  | 721.3 | 766.5 | 615.6 | 788.7 | 617.1 | 609.9 | 581.8
3589.3 | 1889.3 | 386.5 | 154.6 | 180.7185 | 225.1 | 236.2 | 246.7 | 246.2 | 367.5 | 38.6 | 20.4 | 69.3 | 5.4 |  |  | 720 | 763.1 | 606.3 | 791.3 | 615.9 | 599.9 | 576.6
3590.3 | 1890.3 | 387.5 | 155 | 181.1861 | 225 | 237 | 246.2 | 246.8 | 366.6 | 38.7 | 20.4 | 69.6 | 5 |  |  | 718.4 | 755.8 | 591.6 | 792.4 | 622 | 593.8 | 571.4
3591.3 | 1891.3 | 388.3 | 155.32 | 181.5601 | 224.8 | 237.5 | 245.1 | 246.7 | 367.2 | 38.9 | 20.4 | 69.6 | 6.4 |  |  | 719.8 | 755.1 | 611.4 | 793.6 | 617.9 | 608.1 | 575.8
3592.3 | 1892.3 | 387.9 | 155.16 | 181.3731 | 224.8 | 237.6 | 244.5 | 246 | 369.1 | 39.1 | 20.4 | 69.4 | 6.4 |  |  | 723.9 | 764.2 | 609.8 | 792.7 | 632.2 | 627.4 | 582.9
3593.3 | 1893.3 | 388.2 | 155.28 | 181.5134 | 224.4 | 236.5 | 244.6 | 245.7 | 372.6 | 39.2 | 20.4 | 69.2 | 5.7 |  |  | 729.5 | 781.2 | 625.4 | 792.5 | 653.8 | 640 | 584.5
3594.3 | 1894.3 | 387.7 | 155.08 | 181.2796 | 224.6 | 235.7 | 244.5 | 245.5 | 375.5 | 39.2 | 20.4 | 69.1 | 6.1 |  |  | 736.6 | 775.6 | 639.2 | 793.2 | 642.1 | 637.1 | 586.4
3595.3 | 1895.3 | 387.5 | 155 | 181.1861 | 224.8 | 235 | 244.4 | 245.9 | 376.1 | 39.1 | 20.4 | 69.2 | 5.9 |  |  | 740 | 768.1 | 643.6 | 795 | 631.8 | 643.3 | 589.6
3596.3 | 1896.3 | 386.8 | 154.72 | 180.8588 | 224.6 | 234.4 | 244.4 | 246.4 | 376.2 | 39.1 | 20.4 | 69.4 | 6.6 |  |  | 745.3 | 768.3 | 665.2 | 796.7 | 624.8 | 646.8 | 592.5
3597.3 | 1897.3 | 387.7 | 155.08 | 181.2796 | 224.2 | 234.9 | 245.2 | 246.8 | 374.5 | 39.2 | 20.4 | 69.4 | 7.2 |  |  | 749.1 | 760.9 | 674.4 | 796.6 | 633.6 | 666.9 | 600.9
3598.3 | 1898.3 | 388 | 155.2 | 181.4199 | 224.8 | 234.6 | 245.5 | 247.2 | 381.3 | 39.1 | 20.4 | 69.2 | 7 |  |  | 755.1 | 766 | 688.1 | 795.5 | 660.3 | 698.3 | 620.1
3599.3 | 1899.3 | 386.9 | 154.76 | 180.9055 | 225 | 234 | 245.5 | 247 | 387.2 | 39.1 | 20.4 | 69 | 6 |  |  | 759.1 | 775.5 | 704.2 | 795.3 | 684.1 | 710.3 | 625.1
3600.3 | 1900.3 | 386.5 | 154.6 | 180.7185 | 224.8 | 234 | 245 | 247.1 | 390.1 | 39.1 | 20.4 | 69 | 5.6 |  |  | 762.6 | 785.4 | 700.5 | 795 | 706.6 | 725.2 | 626.6
3601.3 | 1901.3 | 386.2 | 154.48 | 180.5782 | 225.9 | 233.8 | 243.6 | 247.4 | 401.2 | 39.2 | 20.4 | 69.1 | 6.4 |  |  | 764.6 | 791.5 | 693.9 | 794.7 | 732 | 730.5 | 624.6
3602.3 | 1902.3 | 387.1 | 154.84 | 180.999 | 225.9 | 233.2 | 244.1 | 247.2 | 406 | 39.3 | 20.4 | 69.1 | 6.2 |  |  | 767 | 807.4 | 676.4 | 797.3 | 741.9 | 732.4 | 619.2
3603.3 | 1903.3 | 387.2 | 154.88 | 181.0458 | 225.3 | 232.4 | 244.9 | 246.9 | 413.6 | 39.4 | 20.4 | 69 | 5.9 |  |  | 768.7 | 802.1 | 674.5 | 800.8 | 735.9 | 728.7 | 615.6
3604.3 | 1904.3 | 388.3 | 155.32 | 181.5601 | 226.8 | 231.4 | 245.5 | 247.7 | 421.4 | 39.3 | 20.4 | 68.9 | 4.7 |  |  | 774.1 | 799.8 | 674.5 | 804.3 | 724.8 | 734.7 | 623.5
3605.3 | 1905.3 | 388.1 | 155.24 | 181.4666 | 226.9 | 232.1 | 245.9 | 248.4 | 417.2 | 39.3 | 20.4 | 68.8 | 4.9 |  |  | 777.6 | 801.5 | 682.1 | 806.5 | 720.9 | 737.6 | 626.3
3606.3 | 1906.3 | 388.3 | 155.32 | 181.5601 | 226.4 | 232.8 | 246.1 | 248.5 | 410.1 | 39.3 | 20.4 | 68.7 | 4.7 |  |  | 780.5 | 792.6 | 692.3 | 808.8 | 719.8 | 744.4 | 631.6
3607.3 | 1907.3 | 389.6 | 155.84 | 182.168 | 225.5 | 232.4 | 246.6 | 248.1 | 407 | 39.2 | 20.4 | 68.5 | 4.5 |  |  | 782.7 | 795.4 | 694.5 | 808.7 | 738.6 | 762.2 | 638.2
3608.3 | 1908.3 | 390.1 | 156.04 | 182.4018 | 224 | 232.1 | 247.6 | 248.4 | 405.9 | 39.2 | 20.4 | 68.6 | 4.7 |  |  | 784 | 786.9 | 697 | 808.7 | 733.1 | 761.8 | 644.4
3609.3 | 1909.3 | 390.1 | 156.04 | 182.4018 | 224.2 | 232.6 | 248 | 248.5 | 398 | 39.1 | 20.4 | 68.5 | 4.2 |  |  | 784.6 | 784.7 | 699 | 809.1 | 724.7 | 764.5 | 642.7
3610.3 | 1910.3 | 390.5 | 156.2 | 182.5888 | 224.4 | 233.6 | 248 | 248.7 | 398.5 | 38.9 | 20.4 | 68.7 | 4.7 |  |  | 780.3 | 772.8 | 708.5 | 810.8 | 706.4 | 752.2 | 639.7
3611.3 | 1911.3 | 389.5 | 155.8 | 182.1212 | 223.4 | 235 | 248.3 | 249.1 | 398.7 | 38.8 | 20.4 | 68.8 | 4.2 |  |  | 775.1 | 759.8 | 707.4 | 813.4 | 697.1 | 739.4 | 638.2
3612.3 | 1912.3 | 390.1 | 156.04 | 182.4018 | 222.8 | 235.7 | 248 | 249.1 | 393.3 | 39 | 20.4 | 68.9 | 3.5 |  |  | 772.2 | 754.9 | 694.5 | 814.5 | 691.6 | 731.7 | 636.1
3613.3 | 1913.3 | 390.5 | 156.2 | 182.5888 | 222.6 | 236.7 | 247.3 | 248.3 | 387.5 | 39.1 | 20.4 | 69 | 3.3 |  |  | 770.7 | 762 | 701.4 | 814.8 | 686.8 | 733.1 | 633.2
3614.3 | 1914.3 | 390.2 | 156.08 | 182.4485 | 223.2 | 237 | 247 | 247.7 | 389.4 | 39.3 | 20.3 | 69.2 | 4.2 |  |  | 767.2 | 759.5 | 693.7 | 814.6 | 680.5 | 711.2 | 628.6
3615.3 | 1915.3 | 390.5 | 156.2 | 182.5888 | 222.9 | 235.7 | 246.8 | 247.2 | 384.8 | 39.3 | 20.4 | 69.3 | 6.1 |  |  | 763.6 | 759.5 | 691 | 813.9 | 671.1 | 701.8 | 622.9
3616.3 | 1916.3 | 390 | 156 | 182.355 | 222.9 | 234.3 | 246.2 | 247 | 383.3 | 39.4 | 20.4 | 69.3 | 5.8 |  |  | 762.5 | 757.3 | 677.8 | 814.3 | 669 | 694.4 | 625.6
3617.3 | 1917.3 | 389.8 | 155.92 | 182.2615 | 222.4 | 234 | 246.4 | 247.2 | 380.9 | 39.6 | 20.3 | 69.4 | 4.9 |  |  | 761 | 756.9 | 680 | 816.6 | 658.2 | 681.5 | 622.9
3618.3 | 1918.3 | 390.4 | 156.16 | 182.542 | 221.7 | 234 | 246.3 | 246.9 | 378.8 | 39.6 | 20.4 | 69.4 | 5.9 |  |  | 760.2 | 745.1 | 688.9 | 819.1 | 648.9 | 665.9 | 623
3619.3 | 1919.3 | 390.4 | 156.16 | 182.542 | 222.1 | 234.7 | 245.7 | 247.4 | 373.7 | 39.7 | 20.3 | 69.4 | 5 |  |  | 763.8 | 746.1 | 698.1 | 818.3 | 650.9 | 666.3 | 624.3
3620.3 | 1920.3 | 390.8 | 156.32 | 182.7291 | 222 | 234.8 | 244.8 | 247.4 | 374.9 | 39.8 | 20.3 | 69.5 | 6.1 |  |  | 767.2 | 763.3 | 696.4 | 816.1 | 653 | 670.5 | 626.3
3621.3 | 1921.3 | 392.2 | 156.88 | 183.3837 | 221.8 | 234.4 | 244.6 | 246.7 | 377.7 | 39.8 | 20.3 | 69.6 | 5.8 |  |  | 770.1 | 751.9 | 696.4 | 814.8 | 644.6 | 672.9 | 627.2
3622.3 | 1922.3 | 391.2 | 156.48 | 182.9161 | 221.7 | 233.7 | 245.6 | 245.9 | 375.1 | 39.8 | 20.3 | 69.6 | 5.2 |  |  | 769.7 | 754.1 | 693.5 | 813.6 | 647 | 678.1 | 630.3
3623.3 | 1923.3 | 390.1 | 156.04 | 182.4018 | 222.1 | 233.1 | 245.4 | 245.4 | 375.1 | 39.9 | 20.3 | 69.8 | 4.8 |  |  | 768.5 | 761 | 687.2 | 812.4 | 650.3 | 667.9 | 628.1
3624.3 | 1924.3 | 390.6 | 156.24 | 182.6356 | 221.9 | 232.8 | 245.3 | 245.5 | 373.6 | 39.8 | 20.3 | 70 | 5.2 |  |  | 764.8 | 746.2 | 672.7 | 811 | 644.4 | 659.1 | 622.3
3625.3 | 1925.3 | 390.8 | 156.32 | 182.7291 | 221.8 | 232.7 | 245.6 | 246.1 | 370.9 | 39.8 | 20.3 | 70 | 4.6 |  |  | 759.1 | 735.4 | 647.7 | 809.6 | 646.5 | 649.2 | 618.9
3626.3 | 1926.3 | 390.8 | 156.32 | 182.7291 | 221.9 | 232.1 | 245.3 | 245.9 | 371.8 | 39.7 | 20.3 | 70 | 4.7 |  |  | 755.1 | 738 | 655.3 | 808.3 | 651.3 | 659.7 | 621
3627.3 | 1927.3 | 391.1 | 156.44 | 182.8693 | 221.6 | 231.2 | 245.1 | 245.9 | 375.8 | 39.6 | 20.3 | 70 | 4.1 |  |  | 751.4 | 746.6 | 636.7 | 807.7 | 669.8 | 663.7 | 617.1
3628.3 | 1928.3 | 391.7 | 156.68 | 183.1499 | 221.7 | 231.1 | 245 | 245.9 | 376.8 | 39.5 | 20.3 | 70.1 | 4.6 |  |  | 751 | 756.1 | 636 | 807.9 | 679.7 | 661.5 | 614.7
3629.3 | 1929.3 | 391.1 | 156.44 | 182.8693 | 222.7 | 231.8 | 245.6 | 245.6 | 378.6 | 39.6 | 20.3 | 70.2 | 5.1 |  |  | 751.2 | 770.7 | 624.1 | 807.9 | 687.5 | 652.8 | 613.6
3630.3 | 1930.3 | 390.9 | 156.36 | 182.7758 | 223.5 | 232.1 | 246.2 | 245.9 | 374.4 | 39.7 | 20.3 | 70.3 | 4.5 |  |  | 747.1 | 771.6 | 611.4 | 809.4 | 686.3 | 651 | 612.6
3631.3 | 1931.3 | 391.2 | 156.48 | 182.9161 | 224 | 231.9 | 246.2 | 246.4 | 373.1 | 39.8 | 20.3 | 70.3 | 4.1 |  |  | 746 | 785.7 | 613.4 | 811 | 686.2 | 652.5 | 610.3
3632.3 | 1932.3 | 391.7 | 156.68 | 183.1499 | 224.3 | 232.3 | 246.4 | 247 | 375.4 | 39.8 | 20.3 | 70.3 | 4 |  |  | 749.7 | 789.9 | 613.2 | 811.4 | 685.3 | 656.3 | 609.4
3633.3 | 1933.3 | 391.6 | 156.64 | 183.1031 | 224.9 | 233.1 | 246.9 | 247.3 | 373 | 39.8 | 20.3 | 70.4 | 4.2 |  |  | 751.9 | 774.6 | 628.6 | 811.3 | 681.5 | 662.6 | 613.8
3634.3 | 1934.3 | 391.8 | 156.72 | 183.1967 | 225 | 233.4 | 248.2 | 247.1 | 369.8 | 39.6 | 20.3 | 70.4 | 4.5 |  |  | 751.6 | 761.3 | 639.7 | 811.5 | 692.7 | 673.6 | 619.1
3635.3 | 1935.3 | 392 | 156.8 | 183.2902 | 225.2 | 234.1 | 249 | 246.9 | 366.5 | 39.6 | 20.3 | 70.4 | 4.3 |  |  | 753.8 | 754.1 | 641 | 813.1 | 692.6 | 686.2 | 625.5
3636.3 | 1936.3 | 392.4 | 156.96 | 183.4772 | 225.9 | 236.1 | 249 | 247.1 | 371.6 | 39.7 | 20.3 | 70.4 | 3.7 |  |  | 754.9 | 758.3 | 635.8 | 814.5 | 699.6 | 690.4 | 633.6
3637.3 | 1937.3 | 391.9 | 156.76 | 183.2434 | 226 | 236.2 | 249.5 | 247.3 | 376 | 39.8 | 20.3 | 70.2 | 4.4 |  |  | 753.3 | 744.5 | 651.3 | 815.4 | 695.4 | 698.4 | 641.9
3638.3 | 1938.3 | 391.3 | 156.52 | 182.9629 | 226.1 | 235.7 | 250.4 | 247.1 | 375.8 | 39.7 | 20.3 | 70.1 | 5 |  |  | 751 | 740.3 | 646 | 816.3 | 684.5 | 694 | 640.5
3639.3 | 1939.3 | 391.9 | 156.76 | 183.2434 | 226.3 | 235.1 | 250.7 | 247.4 | 376 | 39.7 | 20.3 | 69.9 | 4.6 |  |  | 747.7 | 749.9 | 644.9 | 816.8 | 671.3 | 681.2 | 631.8
3640.3 | 1940.3 | 391.6 | 156.64 | 183.1031 | 225.8 | 234.9 | 250.8 | 247.6 | 373.6 | 39.7 | 20.3 | 69.7 | 4.6 |  |  | 745.9 | 771.8 | 620.3 | 815.9 | 676.2 | 680.4 | 620.9
3641.3 | 1941.3 | 392.1 | 156.84 | 183.3369 | 225.4 | 235.3 | 251 | 247.3 | 376.4 | 39.8 | 20.3 | 69.5 | 5 |  |  | 743.8 | 782.1 | 615.1 | 815.7 | 676.2 | 671.5 | 616.7
3642.3 | 1942.3 | 392.4 | 156.96 | 183.4772 | 225.4 | 235.9 | 251 | 247.4 | 383.8 | 40 | 20.3 | 69.4 | 4.8 |  |  | 741.8 | 778.2 | 614.6 | 815.3 | 677 | 669.1 | 615.6
3643.3 | 1943.3 | 391.8 | 156.72 | 183.1967 | 225.7 | 236.6 | 251 | 247.4 | 389.8 | 40 | 20.3 | 69.6 | 4.3 |  |  | 739.6 | 770.6 | 602.2 | 814.3 | 695.4 | 686.9 | 613.8
3644.3 | 1944.3 | 391.9 | 156.76 | 183.2434 | 225.8 | 238.4 | 251.1 | 247.5 | 384.6 | 39.7 | 20.3 | 69.6 | 4.2 |  |  | 738 | 770.2 | 596.3 | 813.9 | 689.6 | 683.5 | 611
3645.3 | 1945.3 | 392.2 | 156.88 | 183.3837 | 226.1 | 238.4 | 251.3 | 247.7 | 384.3 | 39.4 | 20.3 | 69.7 | 4.6 |  |  | 744.3 | 778.4 | 611.5 | 813.9 | 692.3 | 695.1 | 618.1
3646.3 | 1946.3 | 392.6 | 157.04 | 183.5707 | 226.7 | 237.8 | 251.4 | 247.6 | 383.7 | 39.2 | 20.3 | 69.7 | 4.2 |  |  | 752.4 | 769.4 | 644.3 | 815 | 675.2 | 699.7 | 636.7
3647.3 | 1947.3 | 392.6 | 157.04 | 183.5707 | 227 | 237.1 | 251.3 | 247.5 | 386.5 | 39.2 | 20.3 | 69.6 | 3.6 |  |  | 758.9 | 766.9 | 656.8 | 815.7 | 659.1 | 699 | 641.5
3648.3 | 1948.3 | 393.3 | 157.32 | 183.898 | 227.4 | 236.4 | 251.9 | 247.5 | 384.4 | 39.2 | 20.3 | 69.4 | 4 |  |  | 760 | 750.6 | 676.5 | 814.9 | 640.6 | 684.3 | 638.2
3649.3 | 1949.3 | 393.7 | 157.48 | 184.085 | 227.6 | 236.4 | 252 | 248.2 | 380.8 | 39.2 | 20.3 | 69.3 | 4.8 |  |  | 762.7 | 730.7 | 682.2 | 814.6 | 629.1 | 707.3 | 651.3
3650.3 | 1950.3 | 392.9 | 157.16 | 183.711 | 228.1 | 236.4 | 252.3 | 248.8 | 377.2 | 39.1 | 20.3 | 69.2 | 4.6 |  |  | 763.2 | 709 | 687.1 | 813.3 | 622.6 | 724.3 | 669.3
3651.3 | 1951.3 | 392.6 | 157.04 | 183.5707 | 228.2 | 235.9 | 251.7 | 248.7 | 376.2 | 38.9 | 20.3 | 69.1 | 4.1 |  |  | 760.1 | 681.9 | 697.2 | 815 | 604.1 | 724.9 | 672.3
3652.3 | 1952.3 | 393.6 | 157.44 | 184.0383 | 227.8 | 235.3 | 251.1 | 248.2 | 372.7 | 38.9 | 20.3 | 69.2 | 4 |  |  | 753.9 | 659.3 | 700 | 816.5 | 588 | 721.2 | 671.3
3653.3 | 1953.3 | 393.8 | 157.52 | 184.1318 | 226.9 | 235.4 | 250.2 | 247.9 | 367.7 | 39 | 20.3 | 69.4 | 4.3 |  |  | 752.5 | 646.9 | 709.5 | 816.6 | 576.3 | 727.8 | 677.5
3654.3 | 1954.3 | 392.9 | 157.16 | 183.711 | 225.8 | 235.8 | 249.1 | 247.8 | 365.1 | 38.9 | 20.3 | 69.5 | 4.6 |  |  | 756 | 648.5 | 722.5 | 815.4 | 577.2 | 730.7 | 686.6
3655.3 | 1955.3 | 392.2 | 156.88 | 183.3837 | 224.7 | 235.4 | 248.2 | 247.6 | 363.6 | 39 | 20.3 | 69.8 | 4.4 |  |  | 759.4 | 643.6 | 740.2 | 814 | 575.7 | 720.1 | 686.5
3656.3 | 1956.3 | 392.8 | 157.12 | 183.6642 | 223.6 | 235.9 | 248 | 247.6 | 359.3 | 39.2 | 20.3 | 70.1 | 4.6 |  |  | 756.2 | 615.4 | 733.7 | 814.8 | 556.5 | 707 | 683.7
3657.3 | 1957.3 | 392.2 | 156.88 | 183.3837 | 222.9 | 237.2 | 248 | 247.7 | 353.2 | 39.4 | 20.3 | 70.2 | 5 |  |  | 749.5 | 592.9 | 709.1 | 815.1 | 538.5 | 686.4 | 680
3658.3 | 1958.3 | 392.5 | 157 | 183.524 | 221.9 | 240.8 | 247.5 | 247.7 | 346.8 | 39.5 | 20.3 | 70.3 | 6.5 |  |  | 741.7 | 572.3 | 709.9 | 814.4 | 528.4 | 674.5 | 680.8
3659.3 | 1959.3 | 393.1 | 157.24 | 183.8045 | 221 | 243.1 | 247.1 | 247.7 | 343.3 | 39.3 | 20.3 | 70.4 | 6.5 |  |  | 736.2 | 562.6 | 726.1 | 813.6 | 520.7 | 670.3 | 680.6
3660.3 | 1960.3 | 393 | 157.2 | 183.7577 | 221.7 | 243.1 | 246.3 | 248.7 | 342.3 | 39.4 | 20.3 | 70.4 | 5.8 |  |  | 739.4 | 561.8 | 746.8 | 811.1 | 516.7 | 666.6 | 682.3
3661.3 | 1961.3 | 393.2 | 157.28 | 183.8513 | 223 | 242.3 | 244.8 | 248.6 | 344.9 | 39.8 | 20.3 | 70.2 | 4.6 |  |  | 744.8 | 551.8 | 766.4 | 810.7 | 509.6 | 660.7 | 681.9
3662.3 | 1962.3 | 392.9 | 157.16 | 183.711 | 222.5 | 241.9 | 242.9 | 248.4 | 344.7 | 40.4 | 20.3 | 70 | 4.6 |  |  | 750.5 | 546.7 | 779 | 808.5 | 500.6 | 669.4 | 682.2
3663.3 | 1963.3 | 392 | 156.8 | 183.2902 | 222.9 | 242.8 | 241 | 248 | 343.1 | 40.8 | 20.3 | 69.9 | 4.8 |  |  | 744.7 | 535.3 | 766.8 | 806.6 | 486.2 | 649.4 | 674
3664.3 | 1964.3 | 392.5 | 157 | 183.524 | 223.6 | 242.5 | 240.5 | 247.4 | 340.2 | 40.6 | 20.3 | 69.9 | 4.9 |  |  | 736.2 | 525.5 | 753.7 | 805.1 | 472.9 | 641.2 | 666.4
3665.3 | 1965.3 | 393.6 | 157.44 | 184.0383 | 223.8 | 241.8 | 240.9 | 247.2 | 339 | 40.6 | 20.3 | 70.1 | 5 |  |  | 735.9 | 529.1 | 755 | 803.9 | 466.1 | 657.6 | 675.6
3666.3 | 1966.3 | 394.5 | 157.8 | 184.4591 | 224.4 | 240.4 | 240.8 | 247.5 | 339.5 | 40.5 | 20.3 | 70.3 | 5.2 |  |  | 733.9 | 536.1 | 756.3 | 800.9 | 472.6 | 677.6 | 688.9
3667.3 | 1967.3 | 393.8 | 157.52 | 184.1318 | 223.6 | 240.3 | 240 | 247.8 | 342.3 | 40.3 | 20.3 | 70.3 | 5.2 |  |  | 736.5 | 576.4 | 745 | 798.3 | 507.5 | 716.8 | 700.6
3668.3 | 1968.3 | 393.3 | 157.32 | 183.898 | 223.2 | 241.1 | 240.6 | 247.6 | 347.7 | 40.3 | 20.3 | 70.1 | 5 |  |  | 740.4 | 613.6 | 723.3 | 796.2 | 546.5 | 736 | 698.3
3669.3 | 1969.3 | 394 | 157.6 | 184.2253 | 223.1 | 241.7 | 240.7 | 247.7 | 350.4 | 40.2 | 20.3 | 70 | 5.1 |  |  | 744.1 | 630.2 | 708.1 | 796 | 564.3 | 744 | 695.3
3670.3 | 1970.3 | 394.2 | 157.68 | 184.3188 | 222.5 | 241.4 | 240.8 | 249.1 | 351.4 | 40.3 | 20.3 | 70 | 4.7 |  |  | 741.8 | 617.6 | 724.8 | 796.9 | 552.5 | 738.3 | 692.4
3671.3 | 1971.3 | 394.6 | 157.84 | 184.5059 | 222.3 | 240.8 | 241 | 250.9 | 349.7 | 40.1 | 20.3 | 69.9 | 4.6 |  |  | 740.3 | 597.8 | 737.3 | 797 | 534.1 | 723.9 | 692.7
3672.3 | 1972.3 | 395.3 | 158.12 | 184.8332 | 222.4 | 241.4 | 240.9 | 252.2 | 349 | 40 | 20.3 | 69.9 | 4.8 |  |  | 739.9 | 587.1 | 749.4 | 797.5 | 520.5 | 719.1 | 701.6
3673.3 | 1973.3 | 394 | 157.6 | 184.2253 | 221.7 | 241.9 | 240.8 | 252.1 | 346.6 | 39.9 | 20.3 | 70.1 | 4.8 |  |  | 740.5 | 608.6 | 747.2 | 796.2 | 527.6 | 711.5 | 697.1
3674.3 | 1974.3 | 393.7 | 157.48 | 184.085 | 221.8 | 242.6 | 239.9 | 251.6 | 351.3 | 40 | 20.3 | 70.2 | 4.9 |  |  | 740 | 642.9 | 719.8 | 794.3 | 545.9 | 708.9 | 689.8
3675.3 | 1975.3 | 393.6 | 157.44 | 184.0383 | 221.6 | 243.2 | 239.8 | 251.1 | 352.2 | 40.1 | 20.3 | 70.3 | 5.1 |  |  | 734.9 | 657.4 | 688.7 | 792.6 | 564.8 | 706.5 | 676.4
3676.3 | 1976.3 | 394 | 157.6 | 184.2253 | 221.5 | 242.6 | 239.8 | 249.6 | 354.2 | 40.3 | 20.3 | 70.3 | 4 |  |  | 731.3 | 675.9 | 667.9 | 791.6 | 576.4 | 683.7 | 661.7
3677.3 | 1977.3 | 393.8 | 157.52 | 184.1318 | 222.6 | 241.9 | 240.8 | 247.4 | 357.8 | 40.3 | 20.3 | 70.6 | 5.2 |  |  | 730.1 | 695.8 | 664.9 | 791.2 | 583.9 | 670.1 | 652.6
3678.3 | 1978.3 | 393.7 | 157.48 | 184.085 | 224.3 | 241.8 | 241.9 | 245.9 | 363 | 40.3 | 20.3 | 70.9 | 5.2 |  |  | 731.5 | 691.1 | 664.7 | 791.5 | 573.1 | 667.6 | 654.4
3679.3 | 1979.3 | 394.8 | 157.92 | 184.5994 | 224.7 | 241.7 | 243.3 | 245.6 | 373.8 | 40.4 | 20.3 | 71.1 | 5.9 |  |  | 740.8 | 706.1 | 680.9 | 790.3 | 576.6 | 678.2 | 661.4
3680.3 | 1980.3 | 394.3 | 157.72 | 184.3656 | 225.1 | 241.8 | 244.3 | 246 | 400.2 | 40.6 | 20.3 | 71.3 | 6.8 |  |  | 753 | 716.6 | 698.7 | 789.8 | 590 | 711 | 685
3681.3 | 1981.3 | 394 | 157.6 | 184.2253 | 226.1 | 241.3 | 245.6 | 246.2 | 412.8 | 40.7 | 20.3 | 71.3 | 6.1 |  |  | 757.5 | 707.3 | 711.1 | 790.5 | 586.9 | 707.1 | 692.3
3682.3 | 1982.3 | 394.5 | 157.8 | 184.4591 | 226.8 | 241.4 | 247 | 246.9 | 407.9 | 40.7 | 20.3 | 70.9 | 6 |  |  | 756.8 | 679.8 | 711.1 | 790 | 573.6 | 685.5 | 688.8
3683.3 | 1983.3 | 395.1 | 158.04 | 184.7397 | 227.5 | 242.1 | 247.8 | 248.9 | 396.6 | 40.6 | 20.3 | 70.7 | 6.8 |  |  | 756.4 | 675.1 | 711.3 | 788.6 | 574.1 | 690.9 | 684.5
3684.3 | 1984.3 | 395.2 | 158.08 | 184.7864 | 228 | 242 | 248.6 | 249.8 | 390.4 | 40.6 | 20.2 | 70.5 | 5.6 |  |  | 756.9 | 682.4 | 713 | 787.4 | 587 | 682.6 | 683.2
3685.3 | 1985.3 | 393.9 | 157.56 | 184.1786 | 228.2 | 243.2 | 249.5 | 249.2 | 386.8 | 40.7 | 20.2 | 70.2 | 4.9 |  |  | 755.9 | 685.8 | 706.3 | 786.7 | 583.4 | 663.7 | 670
3686.3 | 1986.3 | 394.3 | 157.72 | 184.3656 | 227.7 | 243.9 | 250.6 | 248.6 | 381.3 | 40.5 | 20.3 | 70 | 4.3 |  |  | 751.8 | 661.5 | 705.4 | 784.9 | 561.9 | 642.1 | 662.8
3687.3 | 1987.3 | 394.7 | 157.88 | 184.5526 | 227.6 | 244.9 | 250.8 | 248.6 | 374.6 | 40.1 | 20.3 | 69.8 | 5.1 |  |  | 745.4 | 641.1 | 703.8 | 782 | 543 | 629.4 | 659
3688.3 | 1988.3 | 394.5 | 157.8 | 184.4591 | 228.3 | 246 | 252.3 | 248.4 | 367.6 | 39.9 | 20.2 | 69.6 | 4.9 |  |  | 739.9 | 627.1 | 681.5 | 779.7 | 527.9 | 621 | 653.8
3689.3 | 1989.3 | 394.8 | 157.92 | 184.5994 | 229.5 | 247 | 253.1 | 248.2 | 364.5 | 39.9 | 20.2 | 69.6 | 5.3 |  |  | 732.8 | 611.3 | 658.5 | 776.9 | 511 | 595.8 | 645.6
3690.3 | 1990.3 | 395.1 | 158.04 | 184.7397 | 229.6 | 246.7 | 253 | 247.5 | 358.3 | 40 | 20.2 | 69.7 | 4.8 |  |  | 726.5 | 597.5 | 670 | 774.1 | 499.6 | 577.6 | 643.5
3691.3 | 1991.3 | 395.1 | 158.04 | 184.7397 | 230 | 245.6 | 253 | 246.1 | 354.2 | 40.1 | 20.2 | 69.8 | 5.7 |  |  | 723.6 | 591.7 | 682.9 | 771.3 | 489.2 | 569.1 | 644.9
3692.3 | 1992.3 | 394.7 | 157.88 | 184.5526 | 229.8 | 245.1 | 252.3 | 245.6 | 354.2 | 40.1 | 20.2 | 69.9 | 4.8 |  |  | 720.8 | 603.9 | 693 | 769 | 488.4 | 591 | 649.3
3693.3 | 1993.3 | 394.7 | 157.88 | 184.5526 | 229.2 | 244.9 | 251.8 | 245.6 | 353.5 | 40.1 | 20.2 | 69.8 | 4.6 |  |  | 723.6 | 620.2 | 697.4 | 767.1 | 495.2 | 615.8 | 654.3
3694.3 | 1994.3 | 394.6 | 157.84 | 184.5059 | 228.6 | 244.9 | 250.7 | 244.9 | 355 | 40.1 | 20.2 | 70 | 5.1 |  |  | 729.8 | 626.6 | 702.3 | 765.8 | 499.6 | 645.3 | 665.2
3695.3 | 1995.3 | 394.4 | 157.76 | 184.4124 | 227.7 | 245.5 | 250.2 | 244.6 | 354.6 | 40.1 | 20.2 | 70.3 | 4.1 |  |  | 725.7 | 604.7 | 701 | 765.5 | 493.4 | 639.5 | 671.7
3696.3 | 1996.3 | 394.8 | 157.92 | 184.5994 | 227 | 246.4 | 249.4 | 244.3 | 347.4 | 40 | 20.2 | 70.8 | 3.7 |  |  | 718.1 | 579.3 | 684.7 | 764.3 | 480.3 | 620.1 | 661.9
3697.3 | 1997.3 | 394.6 | 157.84 | 184.5059 | 226.5 | 247.3 | 248.1 | 244.7 | 339.2 | 39.9 | 20.2 | 71.1 | 3.5 |  |  | 709.5 | 560.3 | 675.8 | 763.1 | 469.2 | 606.6 | 657.5
3698.3 | 1998.3 | 395.4 | 158.16 | 184.8799 | 225.9 | 247.8 | 247.1 | 245.1 | 336.1 | 39.8 | 20.2 | 71.3 | 3.7 |  |  | 704.2 | 557.1 | 683.2 | 761.4 | 471.3 | 612.2 | 661.9
3699.3 | 1999.3 | 395.8 | 158.32 | 185.067 | 225.5 | 248.1 | 246.6 | 246.4 | 332.9 | 39.8 | 20.2 | 71.5 | 4.9 |  |  | 701.7 | 540.6 | 689 | 759.6 | 462.6 | 604.5 | 664.2
3700.3 | 2000.3 | 396.1 | 158.44 | 185.2072 | 225.4 | 247.3 | 245.8 | 247.1 | 330.2 | 39.7 | 20.2 | 71.7 | 5 |  |  | 697.6 | 530.3 | 701.3 | 756.9 | 450.8 | 598.2 | 661.2
3701.3 | 2001.3 | 395.8 | 158.32 | 185.067 | 225 | 247.2 | 245.8 | 247.5 | 330.3 | 39.7 | 20.2 | 71.8 | 5.5 |  |  | 696.9 | 526.4 | 719.4 | 754.3 | 445.1 | 599.8 | 660.8
3702.3 | 2002.3 | 395.9 | 158.36 | 185.1137 | 224.7 | 247.7 | 246.1 | 247.7 | 332.9 | 39.7 | 20.2 | 71.8 | 4.9 |  |  | 700 | 525.2 | 728.8 | 753 | 443.6 | 605.3 | 670.1
3703.3 | 2003.3 | 395.2 | 158.08 | 184.7864 | 224.8 | 249.2 | 246.1 | 247.5 | 332.9 | 39.7 | 20.2 | 71.8 | 4.2 |  |  | 705.3 | 529.2 | 738.6 | 752.2 | 444.8 | 631.2 | 685.1
3704.3 | 2004.3 | 395 | 158 | 184.6929 | 225.1 | 249.5 | 245.6 | 247.9 | 334.9 | 39.7 | 20.2 | 71.8 | 4.8 |  |  | 701.2 | 518.2 | 725.8 | 751.7 | 442.1 | 623.6 | 679.6
3705.3 | 2005.3 | 394.8 | 157.92 | 184.5994 | 225.1 | 249.1 | 245.9 | 248.4 | 331.1 | 39.8 | 20.2 | 71.9 | 5.7 |  |  | 702.5 | 530.5 | 734.6 | 750.9 | 443.5 | 622.4 | 673.6
3706.3 | 2006.3 | 395.5 | 158.2 | 184.9267 | 224.5 | 248.9 | 246 | 248.7 | 336.2 | 39.8 | 20.2 | 72 | 5.1 |  |  | 707.5 | 546.4 | 739.6 | 750.2 | 447.2 | 632.5 | 673.7
3707.3 | 2007.3 | 396.2 | 158.48 | 185.254 | 223.7 | 247.7 | 246.7 | 249.1 | 337.1 | 39.9 | 20.2 | 71.9 | 4.4 |  |  | 710.5 | 577.6 | 716.1 | 750 | 466.7 | 656.8 | 676.9
3708.3 | 2008.3 | 395.2 | 158.08 | 184.7864 | 223.4 | 246.9 | 246.2 | 249.6 | 344.7 | 40 | 20.2 | 71.7 | 4.3 |  |  | 712.4 | 616.8 | 696.7 | 749.1 | 496.2 | 650.3 | 667.3
3709.3 | 2009.3 | 395.1 | 158.04 | 184.7397 | 223.4 | 245.6 | 246.8 | 249.5 | 347 | 40.1 | 20.2 | 71.8 | 4.2 |  |  | 708.8 | 633.7 | 680.4 | 747.9 | 503.5 | 639.1 | 657.6
3710.3 | 2010.3 | 395.4 | 158.16 | 184.8799 | 224 | 244.1 | 246.7 | 248.5 | 350.8 | 40.2 | 20.2 | 72.2 | 6.2 |  |  | 712.8 | 654.7 | 692.4 | 747.2 | 501 | 638.1 | 652.9
3711.3 | 2011.3 | 395.4 | 158.16 | 184.8799 | 224.8 | 243.8 | 245.9 | 248.8 | 359.4 | 40.2 | 20.2 | 72.5 | 5.7 |  |  | 719.4 | 674.4 | 692.6 | 746.5 | 516.8 | 637.3 | 658.1
3712.3 | 2012.3 | 395 | 158 | 184.6929 | 224.7 | 243.6 | 245.7 | 249 | 365.7 | 40.1 | 20.2 | 72.6 | 4.6 |  |  | 725.8 | 689.6 | 674.2 | 745.8 | 529.4 | 649.6 | 654.7
3713.3 | 2013.3 | 395.6 | 158.24 | 184.9734 | 224.8 | 243.7 | 245.8 | 249.3 | 368.5 | 40.2 | 20.2 | 72.5 | 3.9 |  |  | 736.5 | 726.1 | 667.1 | 746 | 570.1 | 676.8 | 659.9
3714.3 | 2014.3 | 396.8 | 158.72 | 185.5345 | 225.3 | 242.7 | 245.7 | 249.4 | 376.4 | 40.3 | 20.2 | 72.4 | 4 |  |  | 743.6 | 754.2 | 679.8 | 747.3 | 606.1 | 696 | 669
3715.3 | 2015.3 | 395.9 | 158.36 | 185.1137 | 225.5 | 243 | 246.1 | 249.4 | 384.7 | 40.2 | 20.2 | 72.3 | 4.6 |  |  | 746.8 | 754.7 | 662.7 | 749.1 | 629.4 | 715 | 678.3
3716.3 | 2016.3 | 394.6 | 157.84 | 184.5059 | 225.8 | 244.6 | 246.8 | 249.6 | 394 | 40.2 | 20.2 | 72.2 | 4.7 |  |  | 748.4 | 743.6 | 649 | 750.7 | 645 | 731.4 | 684.1
3717.3 | 2017.3 | 395.6 | 158.24 | 184.9734 | 226.5 | 245.3 | 247 | 249.7 | 400.9 | 40.1 | 20.2 | 72 | 4.5 |  |  | 750.1 | 754 | 639.9 | 752.1 | 671.3 | 744.5 | 691.5
3718.3 | 2018.3 | 396 | 158.4 | 185.1605 | 226.3 | 246.3 | 247.8 | 250 | 407.8 | 40.1 | 20.2 | 71.8 | 4.6 |  |  | 747.5 | 736.4 | 638.7 | 753.9 | 672.6 | 746.8 | 692.2
3719.3 | 2019.3 | 396.6 | 158.64 | 185.441 | 226.6 | 247.6 | 248.2 | 250.6 | 400.5 | 40.3 | 20.2 | 71.6 | 4.5 |  |  | 745.4 | 711.4 | 650.9 | 755.8 | 655.7 | 747.8 | 700.8
3720.3 | 2020.3 | 396.6 | 158.64 | 185.441 | 226.9 | 248.9 | 248.5 | 251.3 | 393.9 | 40.6 | 20.2 | 71.4 | 4.6 |  |  | 741.4 | 690.6 | 659.5 | 757.9 | 635.2 | 742.2 | 709.4
3721.3 | 2021.3 | 396.4 | 158.56 | 185.3475 | 227.3 | 249.2 | 248.4 | 251.1 | 388.3 | 40.9 | 20.2 | 71.2 | 4.4 |  |  | 736.8 | 671.5 | 660.6 | 758.7 | 628.1 | 744.2 | 707
3722.3 | 2022.3 | 396.5 | 158.6 | 185.3943 | 227 | 249.3 | 248.5 | 251.1 | 382.3 | 41.1 | 20.2 | 71.1 | 4.9 |  |  | 731.2 | 661.1 | 649.8 | 759.4 | 616.7 | 745.7 | 702.8
3723.3 | 2023.3 | 396.7 | 158.68 | 185.4878 | 226.3 | 249 | 247.5 | 251.4 | 376.6 | 41.1 | 20.2 | 70.8 | 5.4 |  |  | 725.5 | 658.6 | 631.7 | 759.8 | 628.8 | 742.2 | 694.4
3724.3 | 2024.3 | 396.4 | 158.56 | 185.3475 | 225.4 | 248.6 | 247.3 | 252.4 | 373 | 41.2 | 20.2 | 70.7 | 5.7 |  |  | 720.9 | 648.9 | 616.7 | 760.4 | 624.5 | 746.6 | 694.7
3725.3 | 2025.3 | 396 | 158.4 | 185.1605 | 225.1 | 249.2 | 247.7 | 252.4 | 368.6 | 41.1 | 20.2 | 70.7 | 5.4 |  |  | 713.4 | 621.4 | 597.2 | 760.9 | 606.3 | 735.8 | 692.9
3726.3 | 2026.3 | 396.7 | 158.68 | 185.4878 | 225.4 | 249.9 | 247.6 | 252.7 | 363.9 | 41 | 20.2 | 70.7 | 5.3 |  |  | 704.9 | 601.1 | 587.3 | 760.9 | 593.7 | 730.4 | 692.7
3727.3 | 2027.3 | 397.3 | 158.92 | 185.7683 | 224.8 | 250.2 | 249.1 | 252.8 | 357.5 | 40.9 | 20.2 | 70.8 | 5.3 |  |  | 699.3 | 591.2 | 576.4 | 760.3 | 596 | 733.6 | 694.4
3728.3 | 2028.3 | 396.2 | 158.48 | 185.254 | 224.3 | 252.1 | 250.3 | 252.8 | 355.7 | 41 | 20.2 | 70.9 | 5.2 |  |  | 696.4 | 605.3 | 568.3 | 759.8 | 618.2 | 738.2 | 693.5
3729.3 | 2029.3 | 396.4 | 158.56 | 185.3475 | 223.9 | 252.5 | 251.6 | 252.5 | 360.5 | 41.2 | 20.2 | 71 | 5.4 |  |  | 693 | 611.3 | 565.7 | 759.8 | 626.4 | 752.3 | 694.9
3730.3 | 2030.3 | 396.6 | 158.64 | 185.441 | 223.4 | 251.8 | 252.4 | 252.5 | 374 | 41.5 | 20.2 | 71.1 | 6.5 |  |  | 694.9 | 609.2 | 568.3 | 760.3 | 625.1 | 773.2 | 706.1
3731.3 | 2031.3 | 396.8 | 158.72 | 185.5345 | 223.4 | 251.5 | 252.2 | 252.7 | 385.8 | 41.5 | 20.2 | 71.1 | 5.5 |  |  | 699 | 602.5 | 593.5 | 761.7 | 622.8 | 786 | 718.8
3732.3 | 2032.3 | 400.9 | 160.36 | 187.4516 | 224 | 250.8 | 252.5 | 253.4 | 388.6 | 41.6 | 20.2 | 71.1 | 3.6 |  |  | 701.8 | 608.7 | 606.1 | 763.1 | 637.2 | 799 | 725.3
3733.3 | 2033.3 | 401.5 | 160.6 | 187.7321 | 225.6 | 249.8 | 253.5 | 253.8 | 387 | 41.5 | 20.2 | 71.1 | 3.5 |  |  | 702.5 | 639.2 | 600.3 | 764.5 | 670.9 | 805.5 | 720.9
3734.3 | 2034.3 | 406.7 | 162.68 | 190.1635 | 225.6 | 248.7 | 253.9 | 254.1 | 394 | 41.3 | 20.2 | 71 | 3.7 |  |  | 705.2 | 660.7 | 601.4 | 766.8 | 689.4 | 801.4 | 710.3
3735.3 | 2035.3 | 410.8 | 164.32 | 192.0806 | 225 | 247.7 | 255.2 | 254.9 | 391.7 | 41.2 | 20.2 | 70.8 | 3.8 |  |  | 704 | 677.5 | 598 | 769 | 701.9 | 782.7 | 694.9
3736.3 | 2036.3 | 410.7 | 164.28 | 192.0339 | 224.8 | 246.8 | 257.2 | 255.6 | 391.9 | 41.1 | 20.2 | 70.6 | 3.8 |  |  | 706 | 704.8 | 590.5 | 770.2 | 725.3 | 784.3 | 690.3
3737.3 | 2037.3 | 409.4 | 163.76 | 191.426 | 224.7 | 246.6 | 257.9 | 255.6 | 394.5 | 40.9 | 20.2 | 70.5 | 3.6 |  |  | 711 | 718.7 | 613.4 | 772 | 712.6 | 777.4 | 690.1
3738.3 | 2038.3 | 408.1 | 163.24 | 190.8182 | 225.4 | 246.9 | 258.9 | 254.9 | 396.2 | 40.9 | 20.2 | 70.5 | 3.8 |  |  | 718.4 | 720.7 | 649.5 | 773.4 | 701.3 | 772.9 | 697.3
3739.3 | 2039.3 | 407.4 | 162.96 | 190.4909 | 226 | 248.1 | 259.2 | 254.1 | 398.2 | 40.9 | 20.2 | 70.6 | 3.9 |  |  | 729.2 | 712.9 | 675.6 | 774.4 | 686.1 | 763.5 | 707.5
3740.3 | 2040.3 | 407 | 162.8 | 190.3038 | 226.5 | 249.4 | 258.6 | 254.2 | 403.8 | 41 | 20.2 | 70.6 | 4.3 |  |  | 733.4 | 697.8 | 680 | 774.9 | 668.3 | 756.6 | 714
3741.3 | 2041.3 | 405.9 | 162.36 | 189.7895 | 227.1 | 250.4 | 258.2 | 254.1 | 401.3 | 41.3 | 20.2 | 70.5 | 5.1 |  |  | 730.1 | 699.8 | 674.5 | 774.5 | 655.9 | 737.4 | 702.4
3742.3 | 2042.3 | 405.5 | 162.2 | 189.6025 | 229.3 | 251.3 | 258.8 | 254.1 | 399.3 | 41.4 | 20.2 | 70.5 | 5.3 |  |  | 725.9 | 678.9 | 673.3 | 773.6 | 635.1 | 718.8 | 692
3743.3 | 2043.3 | 405 | 162 | 189.3687 | 230 | 251.1 | 258.8 | 254.3 | 392.1 | 41.5 | 20.2 | 70.6 | 4.8 |  |  | 722.4 | 657 | 675.3 | 772.5 | 616.3 | 696.9 | 686.4
3744.3 | 2044.3 | 405.7 | 162.28 | 189.696 | 232.2 | 251.3 | 258.5 | 254 | 384 | 41.6 | 20.2 | 70.5 | 4.8 |  |  | 718.4 | 646.9 | 673.9 | 770.9 | 597.7 | 679.2 | 679.5
3745.3 | 2045.3 | 405.6 | 162.24 | 189.6492 | 232.5 | 251.2 | 257.1 | 253.8 | 378.5 | 41.5 | 20.2 | 70.6 | 4.6 |  |  | 718.9 | 644.8 | 681.6 | 769 | 594.1 | 678.3 | 681.7
3746.3 | 2046.3 | 404.7 | 161.88 | 189.2284 | 233 | 250.9 | 256.2 | 253.4 | 377.7 | 41.4 | 20.2 | 71 | 4.8 |  |  | 717 | 634 | 679.1 | 767.9 | 586.5 | 678.2 | 693.5
3747.3 | 2047.3 | 404.5 | 161.8 | 189.1349 | 233.1 | 251.1 | 255.9 | 253.8 | 375.1 | 41.3 | 20.2 | 71.4 | 4.7 |  |  | 716.1 | 620.6 | 675.2 | 766.7 | 587.4 | 698.3 | 705.9
3748.3 | 2048.3 | 405.9 | 162.36 | 189.7895 | 233.4 | 251.3 | 255.1 | 254 | 379.6 | 41.2 | 20.2 | 71.7 | 4.1 |  |  | 716.6 | 615 | 670.5 | 766.1 | 580.5 | 704.5 | 713.5
3749.3 | 2049.3 | 404.6 | 161.84 | 189.1816 | 233.7 | 251.8 | 254.2 | 253.6 | 378.2 | 41.2 | 20.2 | 72 | 3.8 |  |  | 720.3 | 622.4 | 696.3 | 765.5 | 571.6 | 709.2 | 718.8
3750.3 | 2050.3 | 404 | 161.6 | 188.9011 | 233.6 | 252.2 | 252.9 | 253.7 | 377.2 | 41.3 | 20.2 | 72.4 | 3.5 |  |  | 727.6 | 624.4 | 714.4 | 764.7 | 559.3 | 701.9 | 719.2
3751.3 | 2051.3 | 403.7 | 161.48 | 188.7608 | 232.9 | 251.6 | 252.4 | 253.8 | 375.2 | 41.3 | 20.2 | 72.4 | 3.2 |  |  | 729.1 | 614.1 | 728.2 | 763.8 | 547.1 | 693.5 | 719
3752.3 | 2052.3 | 405.2 | 162.08 | 189.4622 | 232.5 | 251.7 | 251.7 | 254 | 373.2 | 41.3 | 20.2 | 72.1 | 3.2 |  |  | 730.3 | 617.6 | 725.9 | 762.9 | 542.8 | 702.4 | 720
3753.3 | 2053.3 | 403.7 | 161.48 | 188.7608 | 232.3 | 251.9 | 251.6 | 253.3 | 369.9 | 41.3 | 20.2 | 72 | 3.1 |  |  | 728.9 | 612.8 | 717.9 | 761.9 | 543.4 | 685.5 | 711.9
3754.3 | 2054.3 | 403.8 | 161.52 | 188.8076 | 231.9 | 251.8 | 251.3 | 252.4 | 369.4 | 41.2 | 20.2 | 72.1 | 3.4 |  |  | 729.6 | 626.8 | 715.1 | 761.1 | 543 | 694.2 | 703
3755.3 | 2055.3 | 403.9 | 161.56 | 188.8543 | 231.4 | 251.1 | 250.8 | 252.1 | 372.2 | 41.2 | 20.2 | 72.3 | 4.3 |  |  | 734.2 | 650.2 | 718.5 | 760.5 | 546.7 | 710.8 | 715.8
3756.3 | 2056.3 | 404.5 | 161.8 | 189.1349 | 231.7 | 250.7 | 250.4 | 252.6 | 375.5 | 41.2 | 20.2 | 72.3 | 3.9 |  |  | 737.2 | 659.7 | 720.3 | 760 | 554.4 | 723.3 | 721.7
3757.3 | 2057.3 | 405.1 | 162.04 | 189.4154 | 231.8 | 250.2 | 250.1 | 253.1 | 373.1 | 41.4 | 20.2 | 72.2 | 4.1 |  |  | 739 | 652.3 | 701 | 759.5 | 561.5 | 745.2 | 735.6
3758.3 | 2058.3 | 405.4 | 162.16 | 189.5557 | 232.4 | 249.8 | 249.9 | 253.6 | 371.9 | 41.5 | 20.2 | 72.4 | 4.8 |  |  | 739.6 | 662.9 | 688.3 | 760.1 | 588.1 | 762.7 | 735.9
3759.3 | 2059.3 | 405.8 | 162.32 | 189.7427 | 232.9 | 248.8 | 248.9 | 254 | 372.1 | 41.7 | 20.2 | 72.4 | 3.8 |  |  | 739.6 | 692.7 | 669.3 | 761.3 | 617.2 | 757.1 | 722.7
3760.3 | 2060.3 | 405.8 | 162.32 | 189.7427 | 233.1 | 248.1 | 249 | 253.9 | 376.7 | 41.8 | 20.2 | 72.3 | 3.7 |  |  | 737.6 | 726.2 | 652.4 | 762.1 | 640.9 | 745.2 | 710
3761.3 | 2061.3 | 405.8 | 162.32 | 189.7427 | 232.4 | 247.8 | 249 | 253.6 | 386.3 | 41.8 | 20.2 | 72.2 | 3.7 |  |  | 741.8 | 746.9 | 650.4 | 763.5 | 664.7 | 763.5 | 714.9
3762.3 | 2062.3 | 405.5 | 162.2 | 189.6025 | 232.1 | 248.6 | 248.4 | 253.2 | 395 | 41.8 | 20.2 | 72 | 3.9 |  |  | 739.8 | 740.4 | 644.6 | 765.5 | 682.9 | 781.3 | 719
3763.3 | 2063.3 | 405.2 | 162.08 | 189.4622 | 232.2 | 249 | 248.3 | 253.1 | 400.5 | 41.7 | 20.2 | 72 | 3.9 |  |  | 738.7 | 722.8 | 639.1 | 766.9 | 676.6 | 794.2 | 727
3764.3 | 2064.3 | 405.2 | 162.08 | 189.4622 | 232.5 | 249 | 249.5 | 253.7 | 401.1 | 41.7 | 20.2 | 71.9 | 4 |  |  | 735.2 | 694.5 | 644.5 | 767.5 | 653.3 | 788.4 | 731.4
3765.3 | 2065.3 | 405.2 | 162.08 | 189.4622 | 232.6 | 248.5 | 250.2 | 254.2 | 402 | 41.7 | 20.2 | 71.7 | 3.4 |  |  | 736.1 | 689.7 | 650.7 | 768.4 | 653.9 | 796.5 | 734.2
3766.3 | 2066.3 | 405.2 | 162.08 | 189.4622 | 233 | 248.2 | 250.6 | 254.3 | 406.3 | 41.8 | 20.2 | 71.6 | 2.9 |  |  | 741.4 | 689.5 | 661.8 | 769.5 | 653.5 | 803.3 | 737.6
3767.3 | 2067.3 | 404.1 | 161.64 | 188.9478 | 233.2 | 248.4 | 250.7 | 254.2 | 410.5 | 41.8 | 20.2 | 71.7 | 3.4 |  |  | 746.8 | 666.7 | 679.1 | 769.9 | 635.7 | 801.9 | 747.9
3768.3 | 2068.3 | 404.7 | 161.88 | 189.2284 | 232.8 | 249.1 | 249.9 | 253.9 | 407.1 | 41.8 | 20.2 | 71.8 | 3.6 |  |  | 745.7 | 644.5 | 679 | 769.9 | 623.1 | 792.8 | 743.4
3769.3 | 2069.3 | 404.9 | 161.96 | 189.3219 | 232.4 | 250.8 | 249.4 | 253.9 | 400 | 41.7 | 20.2 | 71.8 | 3.3 |  |  | 748.3 | 659.4 | 681 | 770.4 | 639.5 | 803.3 | 748.3
3770.3 | 2070.3 | 404.6 | 161.84 | 189.1816 | 232.7 | 250.9 | 248.7 | 254 | 403.7 | 41.7 | 20.2 | 71.8 | 3.4 |  |  | 752.2 | 660.2 | 695.2 | 771.5 | 641.8 | 806.3 | 752.8
3771.3 | 2071.3 | 404.9 | 161.96 | 189.3219 | 232.5 | 251 | 248.7 | 254.4 | 404.6 | 41.7 | 20.2 | 71.8 | 3.8 |  |  | 756.8 | 658.9 | 704.5 | 772.4 | 638.2 | 809.2 | 754.4
3772.3 | 2072.3 | 404.7 | 161.88 | 189.2284 | 232.4 | 251 | 248.5 | 254.9 | 399.9 | 41.7 | 20.2 | 71.9 | 4.2 |  |  | 756.2 | 649.6 | 704 | 772.3 | 620.2 | 795 | 749.9
3773.3 | 2073.3 | 404.5 | 161.8 | 189.1349 | 232.1 | 250.9 | 248.5 | 255.1 | 393.8 | 41.7 | 20.2 | 71.9 | 4.1 |  |  | 755.7 | 668.8 | 704.2 | 772.1 | 621.3 | 795.8 | 752.6
3774.3 | 2074.3 | 404.6 | 161.84 | 189.1816 | 233.3 | 250.1 | 249.2 | 255.1 | 396.9 | 41.7 | 20.2 | 71.8 | 3.5 |  |  | 757.8 | 695.5 | 703.5 | 772.4 | 631.9 | 801.6 | 751.1
3775.3 | 2075.3 | 404.3 | 161.72 | 189.0414 | 233.8 | 250.5 | 249.8 | 255.1 | 404 | 41.7 | 20.2 | 71.9 | 3.1 |  |  | 758.5 | 712.4 | 704.9 | 773.1 | 640.5 | 801.5 | 747.9
3776.3 | 2076.3 | 404.1 | 161.64 | 188.9478 | 233.9 | 250.4 | 250.5 | 256 | 401.4 | 41.9 | 20.2 | 72 | 3.9 |  |  | 757.5 | 726.7 | 692.8 | 773.3 | 651 | 803.8 | 740.5
3777.3 | 2077.3 | 404.1 | 161.64 | 188.9478 | 233.9 | 250.7 | 251.1 | 256.8 | 399.7 | 42 | 20.2 | 72.1 | 4.1 |  |  | 754.4 | 740.6 | 664.6 | 773.5 | 676.4 | 801.9 | 730.5
3778.3 | 2078.3 | 404.1 | 161.64 | 188.9478 | 233.6 | 250.7 | 251.9 | 257 | 401.8 | 42 | 20.2 | 72.2 | 3.8 |  |  | 752 | 759.9 | 665.3 | 774 | 706.8 | 807.7 | 726.3
3779.3 | 2079.3 | 404.3 | 161.72 | 189.0414 | 234.1 | 250.3 | 252 | 257.3 | 410.9 | 41.9 | 20.2 | 72.3 | 3.3 |  |  | 755.5 | 747.6 | 678.7 | 775 | 706.5 | 818.7 | 739.3
3780.3 | 2080.3 | 404 | 161.6 | 188.9011 | 234.7 | 250 | 252.3 | 257.7 | 406.9 | 41.8 | 20.2 | 72.3 | 2.7 |  |  | 761.5 | 751.1 | 671.5 | 776.1 | 706.7 | 819.8 | 744.4
3781.3 | 2081.3 | 404.2 | 161.68 | 188.9946 | 234.8 | 250.4 | 252.8 | 258.5 | 407.6 | 41.9 | 20.2 | 72.4 | 3.6 |  |  | 761.1 | 761.9 | 650.1 | 776.7 | 718 | 804.6 | 730.8
3782.3 | 2082.3 | 404.2 | 161.68 | 188.9946 | 234.6 | 251.4 | 253.7 | 259.8 | 421.8 | 41.9 | 20.2 | 72.4 | 3.9 |  |  | 764.9 | 767.8 | 645.1 | 777.3 | 724.5 | 793.1 | 729.2
3783.3 | 2083.3 | 404.1 | 161.64 | 188.9478 | 234.7 | 252.1 | 254.5 | 260.5 | 430.4 | 41.8 | 20.2 | 72.4 | 3.7 |  |  | 763.9 | 763.8 | 646.3 | 777.5 | 722.9 | 782.1 | 724.1
3784.3 | 2084.3 | 404.3 | 161.72 | 189.0414 | 235.2 | 252.9 | 255.2 | 259.6 | 428 | 41.8 | 20.2 | 72.4 | 4.8 |  |  | 760.7 | 753.2 | 647.6 | 777.4 | 705.9 | 771.9 | 723.2
3785.3 | 2085.3 | 404 | 161.6 | 188.9011 | 235.7 | 252.6 | 256.1 | 258.9 | 434.2 | 41.7 | 20.2 | 72.4 | 4.3 |  |  | 758.9 | 743.4 | 655 | 776.4 | 681 | 755.8 | 717.5
3786.3 | 2086.3 | 404.1 | 161.64 | 188.9478 | 236.4 | 252.4 | 256.5 | 258.7 | 438.2 | 41.5 | 20.2 | 72.6 | 4.9 |  |  | 756.8 | 728.4 | 664.3 | 774.7 | 657.2 | 729 | 710.9
3787.3 | 2087.3 | 404 | 161.6 | 188.9011 | 236.7 | 253.3 | 258.6 | 257.9 | 429 | 41.4 | 20.2 | 72.6 | 4.4 |  |  | 766 | 741 | 682.4 | 774 | 657.1 | 756.1 | 715.9
3788.3 | 2088.3 | 404.2 | 161.68 | 188.9946 | 237.3 | 253.8 | 259.7 | 257.3 | 427.3 | 41.4 | 20.2 | 72.6 | 4.4 |  |  | 769 | 729.3 | 689.6 | 773.7 | 643.4 | 737.6 | 708.7
3789.3 | 2089.3 | 404.1 | 161.64 | 188.9478 | 238.7 | 254.1 | 259.4 | 256.1 | 421 | 41.5 | 20.2 | 72.6 | 3.9 |  |  | 768.6 | 714.8 | 699.3 | 772.2 | 622.9 | 720.5 | 704.1
3790.3 | 2090.3 | 404 | 161.6 | 188.9011 | 239.8 | 254.8 | 260 | 255.8 | 417.7 | 41.5 | 20.2 | 72.5 | 3.4 |  |  | 766 | 697.9 | 706.9 | 769.9 | 602 | 708.9 | 706.5
3791.3 | 2091.3 | 403.7 | 161.48 | 188.7608 | 240.6 | 256.6 | 260.2 | 255.5 | 410.5 | 41.4 | 20.2 | 72.3 | 3 |  |  | 766.4 | 690.6 | 712.5 | 767.8 | 592.6 | 707.5 | 718.9
3792.3 | 2092.3 | 403.8 | 161.52 | 188.8076 | 240.4 | 258.1 | 259.8 | 255 | 405.7 | 41.4 | 20.2 | 72.2 | 3.6 |  |  | 764.6 | 676.5 | 716.2 | 766.2 | 584.1 | 693.8 | 719
3793.3 | 2093.3 | 403.9 | 161.56 | 188.8543 | 240.1 | 258 | 259.5 | 255.7 | 399.3 | 41.7 | 20.2 | 72.2 | 3.6 |  |  | 762.7 | 668.3 | 713.2 | 764.4 | 573.5 | 693.1 | 718.2
3794.3 | 2094.3 | 404.1 | 161.64 | 188.9478 | 240.1 | 257.7 | 258.8 | 255.8 | 393.9 | 41.9 | 20.2 | 72.2 | 3 |  |  | 759.1 | 655.7 | 722.7 | 762.2 | 563.9 | 677.7 | 719.3
3795.3 | 2095.3 | 404 | 161.6 | 188.9011 | 239.8 | 258.3 | 258.2 | 255.9 | 386.6 | 42 | 20.2 | 72.2 | 3.5 |  |  | 753.1 | 642.1 | 701 | 759.9 | 564.7 | 696 | 722.9
3796.3 | 2096.3 | 404 | 161.6 | 188.9011 | 239.3 | 257.5 | 257.8 | 256.2 | 382.6 | 42.1 | 20.2 | 72.2 | 3.9 |  |  | 750.6 | 634.6 | 689.3 | 758.4 | 560.2 | 711.4 | 730.6
3797.3 | 2097.3 | 404 | 161.6 | 188.9011 | 239 | 256.8 | 256.9 | 256.6 | 379.3 | 42.3 | 20.1 | 72.2 | 4.5 |  |  | 752 | 650.3 | 687.7 | 757.7 | 564.2 | 710.1 | 729.8
3798.3 | 2098.3 | 403.7 | 161.48 | 188.7608 | 238.5 | 256.9 | 255.7 | 257.3 | 379.5 | 42.3 | 20.2 | 72.3 | 5.3 |  |  | 754.9 | 652.1 | 712 | 757.4 | 570 | 716.3 | 729.7
3799.3 | 2099.3 | 403.9 | 161.56 | 188.8543 | 237.7 | 256.9 | 256 | 258 | 383 | 42.2 | 20.1 | 72.3 | 5 |  |  | 757.7 | 669.4 | 728.1 | 757 | 575.6 | 710.5 | 725.3
3800.3 | 2100.3 | 404 | 161.6 | 188.9011 | 237.2 | 257.5 | 256.8 | 257.2 | 384.9 | 42.2 | 20.1 | 72.2 | 4.6 |  |  | 758.3 | 686.2 | 732.5 | 756.1 | 580 | 706.9 | 721
3801.3 | 2101.3 | 404.1 | 161.64 | 188.9478 | 237.3 | 257.3 | 257.4 | 256.8 | 387.8 | 42.2 | 20.1 | 72.1 | 4 |  |  | 759.1 | 706.1 | 729.7 | 755.4 | 577.9 | 708.4 | 722
3802.3 | 2102.3 | 403.9 | 161.56 | 188.8543 | 236.9 | 256.2 | 257.1 | 256.3 | 391.8 | 42.1 | 20.1 | 72.3 | 3.4 |  |  | 759.4 | 717.4 | 714.1 | 755.3 | 592 | 729.5 | 725.6
3803.3 | 2103.3 | 404 | 161.6 | 188.9011 | 236.9 | 254.7 | 256.8 | 256.1 | 392.5 | 42.2 | 20.1 | 72.4 | 3.3 |  |  | 760.9 | 715.9 | 696.8 | 755.9 | 606.9 | 748.1 | 736.9
3804.3 | 2104.3 | 403.8 | 161.52 | 188.8076 | 237 | 253.3 | 256.6 | 255.8 | 395.6 | 42.2 | 20.1 | 72.6 | 3 |  |  | 761.4 | 730.7 | 684.3 | 756.5 | 617.3 | 741 | 732.6
3805.3 | 2105.3 | 404.1 | 161.64 | 188.9478 | 236.6 | 252.3 | 256.1 | 255.7 | 400.3 | 42.2 | 20.1 | 72.7 | 3.1 |  |  | 762.9 | 737.3 | 684 | 757.1 | 629.8 | 741.8 | 726.5
3806.3 | 2106.3 | 404 | 161.6 | 188.9011 | 236.7 | 251.7 | 255.4 | 255.7 | 400.7 | 42.2 | 20.1 | 72.7 | 4 |  |  | 765.4 | 732.5 | 686 | 757.6 | 629.5 | 749.3 | 730.8
3807.3 | 2107.3 | 403.9 | 161.56 | 188.8543 | 236.9 | 252.5 | 254.9 | 255.3 | 398.2 | 42.1 | 20.1 | 72.5 | 4.3 |  |  | 767 | 738.8 | 703.6 | 758.5 | 635.3 | 757.1 | 741.4
3808.3 | 2108.3 | 403.5 | 161.4 | 188.6673 | 237.7 | 253.3 | 254.9 | 255 | 398.9 | 42.1 | 20.1 | 72.4 | 4.2 |  |  | 768 | 728.1 | 705.8 | 759.6 | 628 | 762 | 745.7
3809.3 | 2109.3 | 403.7 | 161.48 | 188.7608 | 237.7 | 253.9 | 254.1 | 254.6 | 394.1 | 42.2 | 20.1 | 72.4 | 5 |  |  | 767.4 | 709.6 | 698.6 | 759.6 | 615.7 | 755.3 | 744.2
3810.3 | 2110.3 | 404 | 161.6 | 188.9011 | 237.5 | 253.7 | 253 | 254.9 | 393.2 | 42.2 | 20.1 | 72.5 | 4.9 |  |  | 766.4 | 700.2 | 701.3 | 759.8 | 616.9 | 759.7 | 744.5
3811.3 | 2111.3 | 403.5 | 161.4 | 188.6673 | 236.9 | 253.3 | 251.1 | 255.1 | 389.4 | 42.1 | 20.1 | 72.4 | 4.2 |  |  | 765.6 | 705.9 | 690.3 | 760.6 | 631.2 | 772.3 | 745.9
3812.3 | 2112.3 | 404.2 | 161.68 | 188.9946 | 236.7 | 253.1 | 250.8 | 255.3 | 393.3 | 42.2 | 20.1 | 72.3 | 4.6 |  |  | 767.6 | 704.7 | 697.1 | 761.8 | 629.1 | 782.3 | 754.7
3813.3 | 2113.3 | 424.9 | 169.96 | 198.6734 | 236.6 | 253.8 | 250.7 | 254.8 | 390.6 | 42.3 | 20.1 | 72.4 | 4.5 |  |  | 763.5 | 679.6 | 708.8 | 761.5 | 609.9 | 763.3 | 755
3814.3 | 2114.3 | 449.1 | 179.64 | 209.9888 | 236.6 | 255.2 | 251.3 | 254.3 | 384.2 | 42.4 | 20.1 | 72.5 | 4.1 |  |  | 753 | 648.3 | 737.2 | 759.8 | 585.6 | 739 | 748.8
3815.3 | 2115.3 | 478 | 191.2 | 223.5018 | 235.9 | 256.5 | 251.5 | 253.7 | 384.9 | 42.6 | 20.1 | 72.6 | 3.9 |  |  | 748.8 | 640.4 | 733.1 | 758.6 | 585.3 | 751.5 | 753.8
3816.3 | 2116.3 | 490.3 | 196.12 | 229.253 | 235.3 | 256.6 | 251.3 | 253.1 | 386.8 | 42.7 | 20.1 | 72.7 | 4.3 |  |  | 747.2 | 644.4 | 709.8 | 759.5 | 612.2 | 779.9 | 756.1
3817.3 | 2117.3 | 514.1 | 205.64 | 240.3813 | 235.3 | 256.1 | 251.5 | 253.4 | 396.1 | 42.9 | 20.1 | 72.6 | 3.1 |  |  | 748.2 | 677.7 | 684.2 | 761.4 | 651.2 | 797.1 | 751.1
3818.3 | 2118.3 | 521.9 | 208.76 | 244.0284 | 235.7 | 255.7 | 251.7 | 253.2 | 409.2 | 43 | 20.1 | 72.6 | 3.3 |  |  | 751.7 | 698.2 | 692.7 | 763.5 | 668.2 | 805 | 759.8
3819.3 | 2119.3 | 508.3 | 203.32 | 237.6694 | 236.5 | 256.3 | 252.8 | 254.5 | 421.1 | 43.1 | 20.1 | 72.6 | 3.5 |  |  | 756.6 | 704.1 | 710.8 | 765 | 674.4 | 801.3 | 766.2
3820.3 | 2120.3 | 486.6 | 194.64 | 227.5229 | 238.2 | 257.1 | 253.1 | 255.9 | 422 | 43.4 | 20.1 | 72.6 | 3.3 |  |  | 760 | 711.7 | 716.8 | 765.3 | 676.2 | 784.1 | 761.7
3821.3 | 2121.3 | 460.6 | 184.24 | 215.3659 | 238 | 257.5 | 253.1 | 257.5 | 422 | 43.7 | 20.1 | 72.8 | 3.2 |  |  | 757.2 | 731.8 | 680.5 | 765.7 | 699.1 | 774.4 | 745
3822.3 | 2122.3 | 444.7 | 177.88 | 207.9315 | 238.1 | 257.9 | 254.4 | 259.3 | 428.6 | 43.7 | 20.1 | 72.8 | 3.5 |  |  | 758.2 | 763.3 | 671 | 766.2 | 725.9 | 770.7 | 735.9
3823.3 | 2123.3 | 435.9 | 174.36 | 203.8168 | 238.6 | 258 | 255.6 | 260.4 | 440.2 | 43.8 | 20.1 | 72.8 | 3.7 |  |  | 766.4 | 782.1 | 673.2 | 767.9 | 754.8 | 789 | 737.4
3824.3 | 2124.3 | 433.3 | 173.32 | 202.6011 | 239.2 | 257.9 | 256.9 | 260.9 | 453.3 | 43.8 | 20.1 | 73 | 3.5 |  |  | 773.8 | 797.3 | 658.6 | 770.4 | 776.2 | 808.3 | 748.3
3825.3 | 2125.3 | 433 | 173.2 | 202.4608 | 239.8 | 258 | 258.1 | 260.9 | 460.4 | 43.8 | 20.1 | 73.3 | 3.1 |  |  | 772.3 | 793.8 | 639.6 | 772.6 | 780.3 | 818.2 | 752.9
3826.3 | 2126.3 | 434.4 | 173.76 | 203.1154 | 240.3 | 258.5 | 259.2 | 261.9 | 464.1 | 43.8 | 20.1 | 73.5 | 3.4 |  |  | 771.3 | 808.4 | 638.9 | 774.7 | 779.8 | 825.1 | 757.3
3827.3 | 2127.3 | 435.1 | 174.04 | 203.4427 | 241 | 259.7 | 261.2 | 263.5 | 461.2 | 43.7 | 20.1 | 73.7 | 3.4 |  |  | 771.8 | 798.7 | 658.6 | 775.9 | 750.8 | 807.2 | 761.8
3828.3 | 2128.3 | 434.9 | 173.96 | 203.3492 | 241.5 | 260.4 | 262.4 | 265 | 452.4 | 43.6 | 20.1 | 73.7 | 3.6 |  |  | 770 | 797.3 | 675.2 | 775.8 | 735.1 | 798.1 | 758
3829.3 | 2129.3 | 434.4 | 173.76 | 203.1154 | 242.1 | 261 | 264.1 | 266.3 | 445.8 | 43.5 | 20.1 | 73.8 | 3.6 |  |  | 771.3 | 806.4 | 668.1 | 776.6 | 742.6 | 798.1 | 751.7
3830.3 | 2130.3 | 434.7 | 173.88 | 203.2557 | 243.1 | 262.1 | 266 | 265.4 | 443.4 | 43.4 | 20.1 | 73.8 | 3.4 |  |  | 772.3 | 802.8 | 658.6 | 777.1 | 743.5 | 793 | 744.8
3831.3 | 2131.3 | 434.6 | 173.84 | 203.2089 | 244.4 | 262.9 | 266.2 | 264.3 | 442.4 | 43.5 | 20.1 | 73.9 | 4 |  |  | 774.8 | 811 | 659.7 | 777.2 | 730.7 | 791.6 | 743.6
3832.3 | 2132.3 | 434.9 | 173.96 | 203.3492 | 245.4 | 263.4 | 266 | 263.7 | 451.2 | 43.6 | 20.1 | 73.9 | 3.9 |  |  | 779.6 | 802.2 | 668.6 | 776.6 | 718.6 | 781 | 737.7
3833.3 | 2133.3 | 433.4 | 173.36 | 202.6479 | 245.8 | 263.4 | 266.3 | 264.3 | 447.4 | 43.6 | 20.1 | 73.9 | 3.5 |  |  | 779.7 | 798.7 | 660 | 776.1 | 721.5 | 786.3 | 738.5
3834.3 | 2134.3 | 432.8 | 173.12 | 202.3673 | 245.8 | 263.1 | 266.9 | 264 | 444.6 | 43.7 | 20.1 | 73.8 | 3.1 |  |  | 771.4 | 797.4 | 627.8 | 775.8 | 740.2 | 774.1 | 730.8
3835.3 | 2135.3 | 432.2 | 172.88 | 202.0868 | 246.4 | 262.6 | 266.9 | 263.3 | 444.7 | 43.8 | 20.1 | 73.8 | 3 |  |  | 759.4 | 802.9 | 609.7 | 775.9 | 759.6 | 762.3 | 718.1
3836.3 | 2136.3 | 432.4 | 172.96 | 202.1803 | 246.8 | 262.2 | 266.5 | 262.9 | 443.7 | 44 | 20.1 | 73.7 | 2.9 |  |  | 753.2 | 809.9 | 607 | 775.7 | 766.7 | 750 | 711.4
3837.3 | 2137.3 | 431.3 | 172.52 | 201.6659 | 247.2 | 262.5 | 266.4 | 262.3 | 445.9 | 44.2 | 20.1 | 73.8 | 3.7 |  |  | 753 | 822.3 | 588.9 | 776.6 | 776.4 | 756.8 | 711.6
3838.3 | 2138.3 | 430.7 | 172.28 | 201.3854 | 247.4 | 263.1 | 266.9 | 261.7 | 448 | 44.1 | 20.1 | 73.7 | 3.4 |  |  | 755.2 | 825.4 | 582.9 | 777.4 | 786.9 | 762.3 | 709.3
3839.3 | 2139.3 | 430.7 | 172.28 | 201.3854 | 247.9 | 263.3 | 267.2 | 261.6 | 453.4 | 43.9 | 20.1 | 73.6 | 3.4 |  |  | 759.5 | 821.9 | 595.9 | 778.8 | 780.6 | 780.9 | 720.7
3840.3 | 2140.3 | 428.5 | 171.4 | 200.3567 | 248.4 | 264 | 266.7 | 261.7 | 451.3 | 44 | 20.1 | 73.7 | 3.4 |  |  | 765.6 | 800.1 | 622 | 779.6 | 756.9 | 781.8 | 734.5
3841.3 | 2141.3 | 426.9 | 170.76 | 199.6086 | 248.5 | 264.5 | 266.8 | 262.3 | 448.3 | 44 | 20.1 | 73.7 | 3.6 |  |  | 773.3 | 775 | 651 | 778.6 | 723 | 779.4 | 742.7
3842.3 | 2142.3 | 426.9 | 170.76 | 199.6086 | 248.3 | 264.8 | 266.5 | 262.7 | 439.7 | 43.9 | 20.1 | 73.6 | 3.4 |  |  | 773.5 | 744.6 | 673.4 | 776.8 | 695.5 | 764 | 745.1
3843.3 | 2143.3 | 427.6 | 171.04 | 199.9359 | 248.3 | 265.7 | 266.8 | 263.5 | 431.3 | 43.8 | 20.1 | 73.5 | 3.3 |  |  | 774.8 | 713.5 | 694.7 | 775.5 | 673.6 | 770.9 | 756.7
3844.3 | 2144.3 | 426.5 | 170.6 | 199.4216 | 248 | 266.6 | 267 | 264.1 | 422.6 | 43.6 | 20.1 | 73.4 | 3.3 |  |  | 777.9 | 683.9 | 713.9 | 774.9 | 650.7 | 773.3 | 766.5
3845.3 | 2145.3 | 426 | 170.4 | 199.1878 | 247.4 | 267.6 | 266.8 | 263.8 | 418.2 | 43.4 | 20.1 | 73.4 | 3.4 |  |  | 779.5 | 668.3 | 718.1 | 774.1 | 634 | 778.3 | 763.2
3846.3 | 2146.3 | 426 | 170.4 | 199.1878 | 247.9 | 268.8 | 265.7 | 263.9 | 414.7 | 43.4 | 20.1 | 73.5 | 3.7 |  |  | 780.3 | 677.1 | 723 | 774.3 | 637 | 783.9 | 757.8
3847.3 | 2147.3 | 425.5 | 170.2 | 198.954 | 248.1 | 269.4 | 265.1 | 263.6 | 419.1 | 43.3 | 20.1 | 73.6 | 3.8 |  |  | 783.3 | 712.8 | 723.5 | 775 | 665 | 789.7 | 742.8
3848.3 | 2148.3 | 424.9 | 169.96 | 198.6734 | 248.2 | 269.1 | 264.5 | 263.2 | 422.2 | 43.3 | 20.1 | 73.8 | 3.3 |  |  | 785.4 | 731.8 | 726 | 776.6 | 685.2 | 812.8 | 747.2
3849.3 | 2149.3 | 424.8 | 169.92 | 198.6267 | 248 | 268.4 | 263.9 | 263 | 426.3 | 43.1 | 20.1 | 74 | 3.1 |  |  | 782.3 | 737.2 | 714.6 | 778.6 | 695.1 | 822.8 | 754.6
3850.3 | 2150.3 | 421.8 | 168.72 | 197.224 | 248.3 | 267.3 | 263.4 | 263 | 431.3 | 43.1 | 20.1 | 74.1 | 3.3 |  |  | 781.9 | 758.3 | 711.5 | 779.5 | 693.6 | 815.7 | 744
3851.3 | 2151.3 | 416.5 | 166.6 | 194.7458 | 248.8 | 267.3 | 263.1 | 263.4 | 434.4 | 43.5 | 20.1 | 74.3 | 3.1 |  |  | 786.3 | 766.4 | 708.4 | 780.9 | 697.8 | 812.9 | 743
3852.3 | 2152.3 | 411.6 | 164.64 | 192.4547 | 249 | 266.5 | 263.6 | 263.6 | 440.4 | 43.9 | 20.1 | 74.5 | 2.9 |  |  | 789.2 | 754.6 | 705.4 | 781.5 | 685.1 | 806.2 | 752.9
3853.3 | 2153.3 | 406.4 | 162.56 | 190.0233 | 249.1 | 265.7 | 265 | 263.6 | 443.9 | 43.8 | 20.1 | 74.4 | 3.2 |  |  | 792.6 | 751.2 | 717.7 | 781.6 | 669.4 | 798.3 | 753.2
3854.3 | 2154.3 | 405 | 162 | 189.3687 | 249.1 | 265.4 | 265 | 263.9 | 442.3 | 43.7 | 20.1 | 74.4 | 3.8 |  |  | 795.6 | 752.8 | 719.4 | 781.4 | 661.7 | 791.1 | 752.2
3855.3 | 2155.3 | 403.8 | 161.52 | 188.8076 | 248.7 | 265.3 | 264.7 | 264.1 | 437.3 | 43.6 | 20.1 | 74.5 | 3.9 |  |  | 795.7 | 748.7 | 716.6 | 781.4 | 655.6 | 787.7 | 753.9
3856.3 | 2156.3 | 403.8 | 161.52 | 188.8076 | 248.2 | 265.4 | 265.3 | 263.4 | 433.9 | 43.5 | 20.1 | 74.5 | 3.7 |  |  | 799.2 | 749.4 | 722.5 | 781.3 | 655.4 | 785.2 | 753.6
3857.3 | 2157.3 | 404.6 | 161.84 | 189.1816 | 248.3 | 266.3 | 264.8 | 262 | 438.6 | 43.4 | 20.1 | 74.6 | 3.6 |  |  | 798.7 | 749.6 | 708.5 | 782 | 676.1 | 795.6 | 755.3
3858.3 | 2158.3 | 405 | 162 | 189.3687 | 247.8 | 266.8 | 264.2 | 261 | 442.3 | 43.5 | 20.1 | 74.8 | 3.9 |  |  | 791.9 | 745.4 | 696.5 | 782.2 | 682.8 | 797.7 | 755.6
3859.3 | 2159.3 | 405 | 162 | 189.3687 | 247 | 266.4 | 263.2 | 260.7 | 445 | 43.6 | 20.1 | 74.8 | 3.7 |  |  | 789.6 | 765.4 | 689.3 | 782.2 | 700.4 | 790.9 | 750.4
3860.3 | 2160.3 | 405.4 | 162.16 | 189.5557 | 246.8 | 265.9 | 262.7 | 260.4 | 441.1 | 43.6 | 20.1 | 74.8 | 3.6 |  |  | 783.4 | 775.3 | 673.4 | 782.4 | 702.4 | 775.4 | 739.2
3861.3 | 2161.3 | 404.8 | 161.92 | 189.2752 | 246.6 | 265.4 | 263.2 | 260.9 | 434.9 | 43.7 | 20.1 | 74.7 | 3.8 |  |  | 777.9 | 792.3 | 657.3 | 781.4 | 709.7 | 759.7 | 723.7
3862.3 | 2162.3 | 403.7 | 161.48 | 188.7608 | 246.6 | 264.4 | 262.9 | 260.9 | 435.1 | 43.6 | 20.1 | 74.7 | 4.2 |  |  | 777 | 800 | 645.8 | 780.9 | 719.7 | 768 | 724.7
3863.3 | 2163.3 | 403.9 | 161.56 | 188.8543 | 246.7 | 264.5 | 263 | 260.3 | 439.7 | 43.5 | 20.1 | 74.6 | 3.5 |  |  | 772.4 | 814.2 | 638.4 | 780.1 | 725.5 | 747.5 | 717.5
3864.3 | 2164.3 | 405.6 | 162.24 | 189.6492 | 247.1 | 264.3 | 262.7 | 259.3 | 434.7 | 43.4 | 20 | 74.7 | 3.7 |  |  | 774.2 | 822 | 630 | 779.9 | 751.1 | 760.4 | 720.5
3865.3 | 2165.3 | 406.3 | 162.52 | 189.9765 | 247.4 | 263.1 | 262.6 | 258.5 | 436.9 | 43.3 | 20.1 | 74.7 | 3.8 |  |  | 777 | 817.7 | 624.6 | 781.9 | 770.5 | 773.4 | 721.1
3866.3 | 2166.3 | 406.3 | 162.52 | 189.9765 | 247.5 | 262 | 262.4 | 259 | 439.1 | 43.3 | 20.1 | 74.7 | 4.6 |  |  | 771 | 796.7 | 611.5 | 784.2 | 784.2 | 772.3 | 718.3
3867.3 | 2167.3 | 406.1 | 162.44 | 189.883 | 247.6 | 260.8 | 262.4 | 260.8 | 439.6 | 43.3 | 20.1 | 74.8 | 5.5 |  |  | 769.8 | 797.5 | 649.9 | 784.5 | 797.7 | 766.3 | 720.2
3868.3 | 2168.3 | 405.9 | 162.36 | 189.7895 | 247.7 | 260.1 | 262.8 | 261.8 | 438.3 | 43.3 | 20.1 | 74.9 | 5.4 |  |  | 775.8 | 812.7 | 660.4 | 784.2 | 782.8 | 751.8 | 715.5
3869.3 | 2169.3 | 405.7 | 162.28 | 189.696 | 247.7 | 260.5 | 263.5 | 261.6 | 432.4 | 43.3 | 20.1 | 74.9 | 4.5 |  |  | 778.3 | 809.4 | 665.7 | 782.8 | 758.6 | 738.1 | 709.2
3870.3 | 2170.3 | 405.5 | 162.2 | 189.6025 | 247.8 | 261 | 264.7 | 261.1 | 432.6 | 43.3 | 20.1 | 74.8 | 4 |  |  | 778.2 | 784.3 | 673 | 780.4 | 730.5 | 737.3 | 708.4
3871.3 | 2171.3 | 405.5 | 162.2 | 189.6025 | 248.1 | 262.5 | 265.3 | 261.4 | 430.1 | 43.3 | 20.1 | 74.7 | 3.5 |  |  | 778.9 | 771.7 | 664.5 | 779.3 | 727.1 | 746.5 | 710.9
3872.3 | 2172.3 | 405.6 | 162.24 | 189.6492 | 248.4 | 263.7 | 265.5 | 261.2 | 424.2 | 43.4 | 20.1 | 74.5 | 3.3 |  |  | 780.2 | 764.9 | 658 | 779.2 | 727.9 | 770.1 | 722.1
3873.3 | 2173.3 | 405.4 | 162.16 | 189.5557 | 248.6 | 263.6 | 265.2 | 261.2 | 431.7 | 43.4 | 20 | 74.5 | 3.6 |  |  | 781.5 | 769.8 | 660.4 | 779 | 724.2 | 778.1 | 729.7
3874.3 | 2174.3 | 405.5 | 162.2 | 189.6025 | 248.6 | 263.4 | 264.7 | 261 | 432.7 | 43.5 | 20 | 74.5 | 3.4 |  |  | 781.6 | 771.1 | 659.1 | 779.9 | 725.6 | 792.4 | 735.9
3875.3 | 2175.3 | 405.4 | 162.16 | 189.5557 | 249.4 | 263.5 | 263.9 | 261 | 431 | 43.5 | 20 | 74.4 | 3.5 |  |  | 781.1 | 770.4 | 652.8 | 781.7 | 748.5 | 792.9 | 730.7
3876.3 | 2176.3 | 405.2 | 162.08 | 189.4622 | 249.6 | 263.7 | 263.8 | 260.8 | 427.3 | 43.4 | 20 | 74.5 | 3.6 |  |  | 778 | 779.9 | 639.6 | 783 | 757.9 | 794.5 | 719.5
3877.3 | 2177.3 | 405.2 | 162.08 | 189.4622 | 249.7 | 263.6 | 264.2 | 261.2 | 437.3 | 43.3 | 20 | 74.6 | 4.2 |  |  | 786.2 | 792.4 | 640.7 | 784.5 | 757.3 | 794.9 | 713.3
3878.3 | 2178.3 | 405.1 | 162.04 | 189.4154 | 250.4 | 264 | 264.7 | 261.6 | 441.5 | 43.3 | 20 | 74.6 | 4.4 |  |  | 793.6 | 794.1 | 647 | 784.3 | 747.7 | 793.2 | 718.2
3879.3 | 2179.3 | 404.5 | 161.8 | 189.1349 | 251.1 | 264.6 | 265.4 | 261.5 | 442.3 | 43.3 | 20 | 74.6 | 4.4 |  |  | 798.6 | 793.5 | 642.1 | 785.5 | 746.6 | 799.5 | 724.4
3880.3 | 2180.3 | 405.1 | 162.04 | 189.4154 | 251.3 | 264 | 266 | 261.8 | 444.4 | 43.4 | 20 | 74.9 | 4.5 |  |  | 793.4 | 755.3 | 627.9 | 785.9 | 728 | 794.7 | 735.5
3881.3 | 2181.3 | 405.1 | 162.04 | 189.4154 | 251.4 | 263.6 | 265.5 | 262.6 | 432.3 | 43.4 | 20 | 74.9 | 3.5 |  |  | 783.6 | 725.2 | 619.5 | 784 | 711.4 | 792.2 | 740.5
3882.3 | 2182.3 | 405.2 | 162.08 | 189.4622 | 250.6 | 264 | 265.9 | 263.5 | 424.1 | 43.4 | 20 | 75 | 3.6 |  |  | 781 | 714.8 | 628.2 | 784 | 722.5 | 793.8 | 745.9
3883.3 | 2183.3 | 405 | 162 | 189.3687 | 250.2 | 264.2 | 265.8 | 264.2 | 428.9 | 43.4 | 20 | 75 | 3.4 |  |  | 780.8 | 734.1 | 629.6 | 784.6 | 732.5 | 799.8 | 743
3884.3 | 2184.3 | 404.3 | 161.72 | 189.0414 | 249.7 | 264.2 | 265.4 | 264.5 | 430.3 | 43.3 | 20 | 75 | 3.5 |  |  | 772.3 | 728.4 | 625.5 | 782.5 | 707.4 | 756.6 | 722.4
3885.3 | 2185.3 | 403 | 161.2 | 188.4335 | 249.4 | 264.1 | 264.9 | 263.7 | 418 | 43.3 | 20 | 75.1 | 3.9 |  |  | 757.6 | 706 | 631.6 | 779 | 680.2 | 731.9 | 711.4
3886.3 | 2186.3 | 404.4 | 161.76 | 189.0881 | 249.7 | 263.4 | 264.4 | 262.8 | 408.1 | 43.4 | 20 | 75 | 3.4 |  |  | 752.9 | 705.6 | 633.4 | 776.3 | 662.8 | 714.8 | 705.4
3887.3 | 2187.3 | 403.8 | 161.52 | 188.8076 | 250.2 | 262.8 | 263.9 | 261.8 | 404.7 | 43.4 | 20 | 75 | 3.2 |  |  | 749.8 | 691.6 | 641.9 | 772.7 | 649.2 | 694.6 | 703.1
3888.3 | 2188.3 | 403.8 | 161.52 | 188.8076 | 249.5 | 261.9 | 263.2 | 260.6 | 401.1 | 43.4 | 20 | 75.2 | 2.9 |  |  | 744.9 | 663.3 | 670.5 | 769.2 | 628.5 | 682.9 | 708.9
3889.3 | 2189.3 | 403.9 | 161.56 | 188.8543 | 249 | 262 | 263.7 | 260.2 | 391.7 | 43.5 | 20 | 75.4 | 3 |  |  | 738.5 | 637.4 | 694.5 | 765.1 | 603 | 669.1 | 708.1
3890.3 | 2190.3 | 404.2 | 161.68 | 188.9946 | 248.5 | 263 | 263.4 | 259.8 | 382.8 | 43.6 | 20 | 75.5 | 4 |  |  | 739.1 | 633.7 | 692.8 | 761.3 | 592.2 | 663.4 | 706.7
3891.3 | 2191.3 | 404.4 | 161.76 | 189.0881 | 247.9 | 262.8 | 262.5 | 259.6 | 382.8 | 43.7 | 20 | 75.4 | 3.6 |  |  | 744.1 | 645.6 | 696.4 | 758.5 | 580.5 | 666.7 | 707.8
3892.3 | 2192.3 | 404 | 161.6 | 188.9011 | 247.4 | 262 | 261.7 | 259.2 | 381.3 | 43.8 | 20 | 75.5 | 3.6 |  |  | 738.3 | 645.5 | 688.2 | 755.5 | 569.3 | 638.7 | 696.7
3893.3 | 2193.3 | 403.5 | 161.4 | 188.6673 | 248.1 | 260.9 | 261.2 | 259.5 | 377.5 | 43.6 | 20 | 75.8 | 3.7 |  |  | 726.4 | 624.7 | 673.6 | 751.6 | 545.9 | 605.8 | 683.5
3894.3 | 2194.3 | 404.3 | 161.72 | 189.0414 | 248.1 | 260.1 | 260.3 | 258.7 | 374.2 | 43.6 | 20 | 76 | 3.7 |  |  | 717.3 | 604.8 | 672.2 | 747.3 | 526.4 | 587.9 | 675.3
3895.3 | 2195.3 | 404.1 | 161.64 | 188.9478 | 248.1 | 259.1 | 259.3 | 258 | 370.2 | 43.9 | 20 | 76.2 | 4.1 |  |  | 717.6 | 613.9 | 662.6 | 742.5 | 520.9 | 587.7 | 675.2
3896.3 | 2196.3 | 405.1 | 162.04 | 189.4154 | 248.9 | 258.4 | 259.1 | 256.9 | 372.8 | 44.1 | 20 | 76.4 | 4 |  |  | 731 | 640.2 | 668.7 | 739.7 | 538.9 | 619.8 | 685.1
3897.3 | 2197.3 | 404.1 | 161.64 | 188.9478 | 249.1 | 257.9 | 259.1 | 255.4 | 379.9 | 44.2 | 20 | 76.5 | 4.2 |  |  | 742.8 | 662.2 | 668.6 | 740.3 | 560.3 | 666.7 | 703.1
3898.3 | 2198.3 | 403.9 | 161.56 | 188.8543 | 248.7 | 257.6 | 258.9 | 253.9 | 388 | 44.2 | 20 | 76.7 | 4.1 |  |  | 749.5 | 656.2 | 675.6 | 740.7 | 563.2 | 686.3 | 714.9
3899.3 | 2199.3 | 403.4 | 161.36 | 188.6205 | 248.3 | 257.5 | 258.9 | 253 | 390.1 | 44.5 | 20 | 76.8 | 3.8 |  |  | 750.5 | 655.1 | 674.5 | 738.9 | 566 | 689.1 | 715.7
3900.3 | 2200.3 | 402.5 | 161 | 188.1997 | 247.9 | 257.5 | 258.2 | 253.9 | 387.6 | 44.6 | 20 | 76.9 | 3.6 |  |  | 754 | 664.6 | 671.3 | 737.6 | 570 | 702.4 | 718.5
3901.3 | 2201.3 | 404.2 | 161.68 | 188.9946 | 247.6 | 257.4 | 258 | 254.5 | 388.6 | 44.8 | 20 | 77 | 3.7 |  |  | 760.8 | 687 | 668.9 | 738.6 | 580.3 | 717.9 | 719.3
3902.3 | 2202.3 | 405 | 162 | 189.3687 | 246.7 | 257.3 | 257.8 | 254.1 | 385.6 | 44.9 | 20 | 76.9 | 3.9 |  |  | 765.9 | 709 | 668.3 | 739.3 | 587.5 | 717.5 | 715.5
3903.3 | 2203.3 | 411.7 | 164.68 | 192.5014 | 245.9 | 257.3 | 257.9 | 254.1 | 388.7 | 45 | 20 | 76.8 | 3.5 |  |  | 771.3 | 725.5 | 652.9 | 742.4 | 617.6 | 749.3 | 726.3
3904.3 | 2204.3 | 409.1 | 163.64 | 191.2857 | 245.3 | 257.3 | 257.5 | 254.5 | 404.3 | 45 | 20 | 76.8 | 3.6 |  |  | 775.3 | 749.2 | 639 | 747.1 | 659.3 | 770.8 | 728.5
3905.3 | 2205.3 | 407.6 | 163.04 | 190.5844 | 245 | 257.6 | 257.3 | 254.8 | 413.6 | 44.9 | 20 | 76.6 | 3.6 |  |  | 777.9 | 764.2 | 648 | 750.8 | 685.4 | 786.9 | 737.9
3906.3 | 2206.3 | 410.7 | 164.28 | 192.0339 | 245.4 | 257.6 | 257.7 | 255.3 | 416.8 | 45.3 | 20 | 76.5 | 3.5 |  |  | 773.7 | 766.8 | 651.8 | 751.8 | 685.5 | 777 | 738.4
3907.3 | 2207.3 | 416.2 | 166.48 | 194.6055 | 246.4 | 257.5 | 258.3 | 256.5 | 412.5 | 45.7 | 20 | 76.4 | 3.8 |  |  | 771.1 | 760.1 | 665.2 | 751.9 | 670.5 | 764.1 | 733.4
3908.3 | 2208.3 | 420.8 | 168.32 | 196.7564 | 246.9 | 257.9 | 259.3 | 257.9 | 405.2 | 45.8 | 20 | 76.3 | 3.3 |  |  | 779.6 | 764 | 686.5 | 752.3 | 663.7 | 764.7 | 732.4
3909.3 | 2209.3 | 423.7 | 169.48 | 198.1124 | 247 | 258.7 | 260.3 | 258.1 | 409.4 | 45.9 | 20 | 76.1 | 3.1 |  |  | 781.7 | 773.4 | 687.7 | 752.4 | 657.8 | 760.7 | 729
3910.3 | 2210.3 | 427 | 170.8 | 199.6554 | 247.2 | 260 | 260.5 | 257.9 | 410.7 | 46 | 20 | 76 | 3.6 |  |  | 775.9 | 770.2 | 678 | 752.3 | 643.4 | 738 | 717.9
3911.3 | 2211.3 | 428.9 | 171.56 | 200.5438 | 247.7 | 261.3 | 261.1 | 257.3 | 407.8 | 46.1 | 20 | 76 | 3.4 |  |  | 762.6 | 768.8 | 656.2 | 750.8 | 634.9 | 711.5 | 704.4
3912.3 | 2212.3 | 430.2 | 172.08 | 201.1516 | 248.5 | 261.2 | 261.8 | 257 | 403.4 | 46.1 | 20 | 76 | 2.9 |  |  | 763.4 | 762.7 | 662.9 | 749.5 | 619 | 711.6 | 702.7
3913.3 | 2213.3 | 433.2 | 173.28 | 202.5543 | 249.8 | 260.1 | 261.6 | 256.8 | 405.2 | 46.1 | 20 | 75.9 | 2.9 |  |  | 761.6 | 748.7 | 659.8 | 747.7 | 611.1 | 697.2 | 700.6
3914.3 | 2214.3 | 434.2 | 173.68 | 203.0219 | 250.5 | 259.2 | 260.8 | 257.2 | 398.1 | 46.1 | 20 | 75.8 | 2.9 |  |  | 746.5 | 710.9 | 639.5 | 744 | 588.9 | 663 | 691.2
3915.3 | 2215.3 | 434.9 | 173.96 | 203.3492 | 250.4 | 258.6 | 260.6 | 257.3 | 391.9 | 46.2 | 20 | 76 | 3.4 |  |  | 742.5 | 713.3 | 624.3 | 740.5 | 581.3 | 653.5 | 685.3
3916.3 | 2216.3 | 434.9 | 173.96 | 203.3492 | 251.2 | 258.6 | 260.5 | 257.3 | 388.3 | 46.1 | 20 | 76 | 3.1 |  |  | 739.4 | 705.9 | 629.9 | 737.1 | 566.8 | 643.4 | 681.5
3917.3 | 2217.3 | 436.9 | 174.76 | 204.2844 | 251.2 | 259.1 | 260.2 | 257.3 | 389.5 | 46 | 20 | 75.9 | 2.9 |  |  | 739.4 | 691.2 | 645 | 733.5 | 554.1 | 632.5 | 682.9
3918.3 | 2218.3 | 437.3 | 174.92 | 204.4714 | 250.9 | 258.7 | 260 | 257.9 | 384.7 | 45.9 | 20 | 76 | 2.7 |  |  | 740.9 | 708.9 | 654.6 | 730.2 | 563.5 | 654.9 | 692
3919.3 | 2219.3 | 437.4 | 174.96 | 204.5182 | 250.4 | 259 | 259.9 | 257.9 | 389.3 | 45.6 | 20 | 76.3 | 2.9 |  |  | 755.8 | 723.4 | 659.1 | 730.8 | 580.2 | 699.5 | 711
3920.3 | 2220.3 | 438.1 | 175.24 | 204.8455 | 249.5 | 259.4 | 259.5 | 257.9 | 406 | 45.6 | 20 | 76.6 | 3.2 |  |  | 767.3 | 742.5 | 668.5 | 731.1 | 589.6 | 699.6 | 707
3921.3 | 2221.3 | 440.1 | 176.04 | 205.7806 | 248.9 | 259.4 | 260.1 | 258 | 406.4 | 45.9 | 20 | 77 | 3.3 |  |  | 761.7 | 726.1 | 677.2 | 729.6 | 574.7 | 689.8 | 698.9
3922.3 | 2222.3 | 439 | 175.6 | 205.2663 | 248.2 | 260.3 | 260.4 | 258.9 | 394.9 | 46.2 | 20 | 77.4 | 3.7 |  |  | 755.6 | 699.7 | 690.3 | 727.8 | 556.7 | 661.8 | 697.6
3923.3 | 2223.3 | 439.5 | 175.8 | 205.5001 | 248 | 260.9 | 260.2 | 258.7 | 389.1 | 46.2 | 20 | 77.9 | 3.7 |  |  | 750.6 | 671.4 | 698.4 | 725.4 | 534.7 | 638.7 | 691.9
3924.3 | 2224.3 | 439.4 | 175.76 | 205.4533 | 247.8 | 261.5 | 259.8 | 258.4 | 381.8 | 46.2 | 20 | 78.3 | 3.8 |  |  | 744.5 | 650.1 | 722.5 | 722.4 | 518.7 | 626 | 689.7
3925.3 | 2225.3 | 440.5 | 176.2 | 205.9676 | 247.8 | 262.1 | 259.4 | 258.3 | 377.5 | 46.3 | 20 | 78.6 | 4.2 |  |  | 729.9 | 624.8 | 724.7 | 718.8 | 499.4 | 609.9 | 688.1
3926.3 | 2226.3 | 441.1 | 176.44 | 206.2482 | 247.4 | 261.5 | 259.8 | 258.1 | 377 | 46.3 | 20 | 78.8 | 3.4 |  |  | 721.6 | 605.7 | 716.2 | 714.5 | 484.4 | 600.7 | 683.1
3927.3 | 2227.3 | 441.5 | 176.6 | 206.4352 | 246.9 | 260.7 | 260.5 | 258.1 | 372.8 | 46.3 | 20 | 78.9 | 3.1 |  |  | 715.3 | 596.2 | 715.8 | 710.9 | 472.9 | 586.8 | 674.7
3928.3 | 2228.3 | 442 | 176.8 | 206.669 | 247 | 260.7 | 260.5 | 258 | 367 | 46.3 | 20 | 79.1 | 3 |  |  | 716.9 | 602.6 | 723 | 707.7 | 471.8 | 589.4 | 676.7
3929.3 | 2229.3 | 442.8 | 177.12 | 207.0431 | 247.4 | 261.3 | 260.9 | 257.6 | 367.1 | 46.2 | 20 | 79.2 | 3.4 |  |  | 723.7 | 604.4 | 713.4 | 704.7 | 470.2 | 603.6 | 682.2
3930.3 | 2230.3 | 443.3 | 177.32 | 207.2769 | 247.7 | 261.7 | 261.2 | 256.5 | 369.5 | 46.1 | 20 | 79.4 | 3.4 |  |  | 724.9 | 611 | 705 | 701.4 | 472.9 | 618.3 | 684.7
3931.3 | 2231.3 | 443.7 | 177.48 | 207.4639 | 248.4 | 261.8 | 261.1 | 256.4 | 374 | 45.9 | 20 | 79.4 | 3.6 |  |  | 734.5 | 648.2 | 714.4 | 700.3 | 504.2 | 654.9 | 694.1
3932.3 | 2232.3 | 443.8 | 177.52 | 207.5107 | 248.7 | 262.3 | 261.3 | 256.2 | 394.7 | 45.9 | 20 | 79.3 | 3.5 |  |  | 746.2 | 682.7 | 709.5 | 703.8 | 545.3 | 688.8 | 702.6
3933.3 | 2233.3 | 444.5 | 177.8 | 207.838 | 249 | 263.1 | 261.7 | 256.9 | 408.2 | 45.7 | 20 | 79.2 | 3.9 |  |  | 746.6 | 714.1 | 690.2 | 705.3 | 569.2 | 693.1 | 699.1
3934.3 | 2234.3 | 445.6 | 178.24 | 208.3523 | 249.2 | 264 | 261 | 257.8 | 408.2 | 45.5 | 20 | 79 | 3.7 |  |  | 750.8 | 722.8 | 689.1 | 705.2 | 560.3 | 676.2 | 691.3
3935.3 | 2235.3 | 446 | 178.4 | 208.5393 | 249.3 | 264.7 | 261.7 | 259.2 | 414.4 | 45.5 | 20 | 78.7 | 3.6 |  |  | 763.7 | 735.8 | 711.3 | 705.7 | 575 | 687.2 | 696.3
3936.3 | 2236.3 | 445.9 | 178.36 | 208.4926 | 249.5 | 266.2 | 262.6 | 260 | 420.8 | 45.5 | 20 | 78.5 | 3.1 |  |  | 774.4 | 740.3 | 724.8 | 708.8 | 595.6 | 712.6 | 704.3
3937.3 | 2237.3 | 445.9 | 178.36 | 208.4926 | 249.4 | 267 | 262.9 | 260.4 | 435.2 | 45.5 | 20 | 78.4 | 3.6 |  |  | 779.7 | 753.5 | 726.3 | 713.2 | 634.7 | 726.9 | 702
3938.3 | 2238.3 | 446.3 | 178.52 | 208.6796 | 249.4 | 267.1 | 262.8 | 260.7 | 436.9 | 45.4 | 20 | 78.5 | 3.9 |  |  | 786.2 | 742.8 | 733.8 | 714.2 | 626 | 733.1 | 708
3939.3 | 2239.3 | 446.3 | 178.52 | 208.6796 | 249.4 | 267.5 | 264.1 | 261.7 | 433.7 | 45.3 | 20 | 78.3 | 3.5 |  |  | 789.1 | 728.3 | 735.7 | 713.9 | 622.4 | 741 | 711.5
3940.3 | 2240.3 | 446.6 | 178.64 | 208.8199 | 249.7 | 268.3 | 264.7 | 262.1 | 433.6 | 45.2 | 20 | 78 | 3.4 |  |  | 794.7 | 720.5 | 737.1 | 716.3 | 624.4 | 768.1 | 721.3
3941.3 | 2241.3 | 446.6 | 178.64 | 208.8199 | 250.6 | 268.7 | 266 | 262.4 | 432.4 | 45.3 | 20 | 77.6 | 3.2 |  |  | 800.4 | 731.2 | 749.4 | 720.7 | 640.1 | 782.5 | 725.8
3942.3 | 2242.3 | 447.4 | 178.96 | 209.1939 | 251 | 269.1 | 266.6 | 263.2 | 433.5 | 45.3 | 20 | 77.3 | 3.4 |  |  | 807.7 | 733.6 | 759.7 | 722.7 | 631.5 | 773.4 | 734.3
3943.3 | 2243.3 | 447.2 | 178.88 | 209.1004 | 251.3 | 270.2 | 267.2 | 264.3 | 430.5 | 45.4 | 20 | 77.1 | 4.1 |  |  | 816.6 | 735.5 | 763.7 | 724.5 | 631.7 | 778 | 738.1
3944.3 | 2244.3 | 447.4 | 178.96 | 209.1939 | 252.6 | 271.6 | 268 | 264.6 | 432.1 | 45.6 | 20 | 77.1 | 4.1 |  |  | 818.3 | 736.2 | 765.9 | 726.2 | 629.3 | 776.4 | 734.9
3945.3 | 2245.3 | 449.1 | 179.64 | 209.9888 | 253.3 | 272.2 | 267.8 | 264.3 | 430.3 | 45.8 | 20 | 77 | 3.6 |  |  | 816.7 | 728.8 | 771.4 | 725.8 | 618.9 | 768.9 | 728.9
3946.3 | 2246.3 | 449.3 | 179.72 | 210.0823 | 253.7 | 272.3 | 268.1 | 263.9 | 425.2 | 46 | 20 | 76.9 | 3.7 |  |  | 817.8 | 724.2 | 786 | 725 | 618 | 768.2 | 729.6
3947.3 | 2247.3 | 450.6 | 180.24 | 210.6902 | 254.7 | 272.4 | 268.6 | 264 | 427.1 | 46.1 | 20 | 77 | 3.6 |  |  | 820.7 | 750.4 | 781.1 | 725.4 | 621.1 | 771.1 | 728.5
3948.3 | 2248.3 | 451.2 | 180.48 | 210.9707 | 255.4 | 273.7 | 268 | 263.9 | 426.9 | 46.2 | 20 | 77 | 3.7 |  |  | 818.3 | 753 | 763.6 | 724.7 | 621.4 | 767.1 | 726.1
3949.3 | 2249.3 | 451.3 | 180.52 | 211.0175 | 256 | 274.5 | 269 | 264 | 427.8 | 46.3 | 20 | 77 | 3.8 |  |  | 805.9 | 766.9 | 728.6 | 724 | 645.6 | 751.7 | 713
3950.3 | 2250.3 | 451 | 180.4 | 210.8772 | 256.7 | 274.4 | 269.1 | 264.1 | 425.4 | 46.3 | 20 | 77 | 3.3 |  |  | 797.3 | 776.6 | 726.3 | 723.6 | 662 | 751.7 | 715.2
3951.3 | 2251.3 | 451.1 | 180.44 | 210.924 | 257.5 | 274.4 | 269 | 264.3 | 425.5 | 46.2 | 20 | 77 | 3.4 |  |  | 805.2 | 788.5 | 745.1 | 722.9 | 666 | 754.3 | 721.3
3952.3 | 2252.3 | 451.5 | 180.6 | 211.111 | 257.7 | 274.4 | 269.2 | 265.4 | 432.6 | 46.1 | 20 | 77.1 | 3.4 |  |  | 811.1 | 799.5 | 741.4 | 722.8 | 672.7 | 764.8 | 727.9
3953.3 | 2253.3 | 451.5 | 180.6 | 211.111 | 258 | 275 | 269.5 | 265.8 | 441.2 | 46.1 | 20 | 77.1 | 3.4 |  |  | 809.1 | 807.4 | 725.2 | 723.3 | 677.5 | 762.8 | 723.3
3954.3 | 2254.3 | 451.6 | 180.64 | 211.1578 | 258.1 | 274.9 | 269.7 | 266 | 445 | 46 | 20 | 77.1 | 3.2 |  |  | 808.9 | 813.9 | 716.1 | 725.6 | 685.1 | 776 | 724.4
3955.3 | 2255.3 | 451.7 | 180.68 | 211.2045 | 258.3 | 275 | 270.7 | 266.7 | 456.4 | 45.9 | 20 | 77.1 | 3.2 |  |  | 812.5 | 814.3 | 716.1 | 729.9 | 694.6 | 793.8 | 730.1
3956.3 | 2256.3 | 451.7 | 180.68 | 211.2045 | 258.6 | 274.7 | 270.8 | 266.8 | 452.7 | 46.1 | 20 | 77.2 | 3.4 |  |  | 811.4 | 816.6 | 705.4 | 731.5 | 705.3 | 794.7 | 723.8
3957.3 | 2257.3 | 451.8 | 180.72 | 211.2513 | 259.5 | 274.8 | 270.5 | 266.7 | 463 | 46.3 | 20 | 77.2 | 3.5 |  |  | 818.1 | 832.5 | 698.1 | 735.1 | 729.1 | 803.3 | 722.7
3958.3 | 2258.3 | 453 | 181.2 | 211.8124 | 259.9 | 275.3 | 270.4 | 266.9 | 483.8 | 46.5 | 20 | 77.3 | 4 |  |  | 827.7 | 839.3 | 702.1 | 736.6 | 728.4 | 788.8 | 717.2
3959.3 | 2259.3 | 455.4 | 182.16 | 212.9345 | 260.7 | 275.7 | 270.6 | 267.1 | 507.3 | 46.6 | 20 | 77.6 | 4.2 |  |  | 834.5 | 831.6 | 722.4 | 737.1 | 727.5 | 784.3 | 716.1
3960.3 | 2260.3 | 456.3 | 182.52 | 213.3554 | 261.1 | 276 | 271.6 | 268.3 | 508.6 | 46.6 | 19.9 | 77.8 | 4.6 |  |  | 838.5 | 829.9 | 730.2 | 740 | 738 | 789.9 | 726.1
3961.3 | 2261.3 | 456.6 | 182.64 | 213.4956 | 261.7 | 275.8 | 272.8 | 269.2 | 504.8 | 46.6 | 20 | 77.9 | 4.7 |  |  | 839.2 | 827.5 | 710.4 | 741.8 | 745.3 | 797.8 | 731.1
3962.3 | 2262.3 | 456.4 | 182.56 | 213.4021 | 261.8 | 275.1 | 273.5 | 269.9 | 500.7 | 46.7 | 20 | 77.8 | 4.1 |  |  | 836.7 | 832.5 | 708.3 | 740.9 | 734.5 | 771.7 | 721.2
3963.3 | 2263.3 | 456.9 | 182.76 | 213.6359 | 261.7 | 274.4 | 274.4 | 271.3 | 497.7 | 46.8 | 19.9 | 77.6 | 3.8 |  |  | 835.5 | 835.6 | 713 | 739.6 | 718.2 | 765 | 724.1
3964.3 | 2264.3 | 457.6 | 183.04 | 213.9632 | 261.8 | 274.5 | 276 | 272.1 | 487 | 47 | 20 | 77.6 | 3.9 |  |  | 830.4 | 804.3 | 735.1 | 738.4 | 697 | 764.1 | 732.1
3965.3 | 2265.3 | 457.8 | 183.12 | 214.0567 | 262.3 | 275 | 277.1 | 272.3 | 478.4 | 47 | 20 | 77.4 | 4.5 |  |  | 834.7 | 803.2 | 746.1 | 738.9 | 699.3 | 782.5 | 742.7
3966.3 | 2266.3 | 457.5 | 183 | 213.9165 | 262.9 | 275.7 | 277.2 | 272.5 | 467.8 | 46.9 | 20 | 77.3 | 5 |  |  | 827.7 | 809.1 | 730.1 | 741 | 728.1 | 785.7 | 735
3967.3 | 2267.3 | 456.4 | 182.56 | 213.4021 | 263.1 | 275.5 | 276.8 | 273.1 | 472.9 | 47 | 20 | 77.2 | 4.6 |  |  | 821.8 | 815.2 | 722.2 | 744.3 | 758 | 791.3 | 728.2
3968.3 | 2268.3 | 457.9 | 183.16 | 214.1035 | 263.2 | 275.6 | 277.6 | 273.4 | 486.8 | 46.9 | 20 | 77 | 3.5 |  |  | 823 | 835.7 | 716.2 | 748.6 | 777.6 | 811.6 | 733.8
3969.3 | 2269.3 | 457.3 | 182.92 | 213.8229 | 263.3 | 275.7 | 278.2 | 272.9 | 493.8 | 46.9 | 20 | 76.8 | 3.3 |  |  | 831 | 833.1 | 731.9 | 750.6 | 765.7 | 806.1 | 736.7
3970.3 | 2270.3 | 457.4 | 182.96 | 213.8697 | 263.7 | 276.3 | 278.8 | 272.7 | 489.9 | 47.1 | 20 | 76.9 | 3 |  |  | 827.5 | 827.6 | 735.3 | 748.9 | 747.5 | 777.6 | 726.3
3971.3 | 2271.3 | 459.5 | 183.8 | 214.8516 | 264.3 | 276.4 | 279.3 | 273.3 | 478.3 | 46.9 | 20 | 76.9 | 2.3 |  |  | 818.5 | 800 | 737.1 | 745.9 | 713.6 | 755.3 | 717.3
3972.3 | 2272.3 | 459.6 | 183.84 | 214.8984 | 264.9 | 277.1 | 280.4 | 273.5 | 461.4 | 46.7 | 20 | 77 | 2.5 |  |  | 819.9 | 766.1 | 745.7 | 742.7 | 687.6 | 746.7 | 729.2
3973.3 | 2273.3 | 460.5 | 184.2 | 215.3192 | 265.6 | 278.6 | 280.8 | 273.5 | 451.1 | 46.5 | 20 | 77.1 | 3.2 |  |  | 813.3 | 735.7 | 734.8 | 739.6 | 669.2 | 750.3 | 735.8
3974.3 | 2274.3 | 460.3 | 184.12 | 215.2257 | 265.6 | 280.4 | 280.6 | 272.7 | 444.1 | 46.8 | 20 | 77.2 | 3 |  |  | 802.7 | 735.6 | 707.3 | 738.6 | 682.9 | 761.5 | 735.2
3975.3 | 2275.3 | 460.9 | 184.36 | 215.5062 | 264.9 | 280.4 | 279.7 | 272.3 | 438.8 | 47.1 | 20 | 77.4 | 3.6 |  |  | 792 | 740.7 | 684.6 | 740.2 | 701.5 | 775.7 | 730.6
3976.3 | 2276.3 | 460.6 | 184.24 | 215.3659 | 264.3 | 279.3 | 279.2 | 272.7 | 436.9 | 47 | 19.9 | 77.4 | 3.7 |  |  | 790.9 | 751.5 | 692.7 | 741.7 | 710.5 | 791.1 | 739.9
3977.3 | 2277.3 | 460.2 | 184.08 | 215.1789 | 263.6 | 278.6 | 277.9 | 272.9 | 437.9 | 47 | 19.9 | 77.4 | 3.5 |  |  | 791.7 | 751.4 | 721.5 | 741 | 692.7 | 773.4 | 744.4
3978.3 | 2278.3 | 460 | 184 | 215.0854 | 263 | 278.1 | 277.1 | 272.5 | 428.8 | 47 | 19.9 | 77.5 | 4 |  |  | 792.6 | 747 | 716.3 | 738.7 | 673.4 | 770.4 | 736.7
3979.3 | 2279.3 | 461.4 | 184.56 | 215.74 | 262.8 | 277.9 | 275.8 | 272.7 | 426 | 46.9 | 19.9 | 77.5 | 3.2 |  |  | 794.6 | 754.3 | 720.8 | 736.7 | 662.9 | 774.4 | 737
3980.3 | 2280.3 | 460.4 | 184.16 | 215.2724 | 262.7 | 277.4 | 275.4 | 273.3 | 425 | 46.8 | 19.9 | 77.6 | 2.9 |  |  | 799.7 | 760.5 | 731.2 | 735.5 | 664.9 | 775.8 | 740.3
3981.3 | 2281.3 | 459.1 | 183.64 | 214.6646 | 263 | 276.7 | 275.2 | 272.7 | 429.6 | 46.8 | 19.9 | 77.7 | 3 |  |  | 807.1 | 762.5 | 740.4 | 734.1 | 657.2 | 770.9 | 741.2
3982.3 | 2282.3 | 458 | 183.2 | 214.1502 | 263.4 | 276.2 | 274.6 | 272.5 | 435.2 | 46.6 | 19.9 | 77.9 | 3.7 |  |  | 816.9 | 777.4 | 764.2 | 734.3 | 665.9 | 781.5 | 753.2
3983.3 | 2283.3 | 458.8 | 183.52 | 214.5243 | 263.4 | 276.5 | 273.7 | 272 | 436.1 | 47.3 | 19.9 | 78 | 4 |  |  | 819.8 | 776.6 | 769.7 | 734.6 | 656.2 | 792.1 | 763.3
3984.3 | 2284.3 | 457.9 | 183.16 | 214.1035 | 263.2 | 276.9 | 273.8 | 272.2 | 428.5 | 48.1 | 19.9 | 78.3 | 5.2 |  |  | 814.4 | 742.9 | 769.8 | 734.9 | 653.1 | 799.8 | 770
3985.3 | 2285.3 | 458.4 | 183.36 | 214.3373 | 262.5 | 277.7 | 273.7 | 272.3 | 427.6 | 48.3 | 19.9 | 78.8 | 6 |  |  | 803.4 | 722 | 749.7 | 735.5 | 650 | 799.4 | 770.5
3986.3 | 2286.3 | 458.3 | 183.32 | 214.2905 | 261.6 | 277.6 | 273 | 272.4 | 420.9 | 48.3 | 19.9 | 79.1 | 5.6 |  |  | 789 | 692.7 | 741.4 | 734.1 | 631.1 | 794.7 | 771.4
3987.3 | 2287.3 | 458.8 | 183.52 | 214.5243 | 261.1 | 277.3 | 271.6 | 271.7 | 416.1 | 48.2 | 19.9 | 79.2 | 6.2 |  |  | 782.6 | 694.7 | 732.3 | 734.3 | 648.3 | 797.6 | 769.1
3988.3 | 2288.3 | 459.8 | 183.92 | 214.9919 | 260.7 | 278.5 | 270.3 | 271.7 | 425.9 | 48 | 19.9 | 79.2 | 5.6 |  |  | 788.6 | 739.1 | 724 | 735.2 | 677.1 | 773.4 | 755.8
3989.3 | 2289.3 | 460.5 | 184.2 | 215.3192 | 260.8 | 279.6 | 270.3 | 272 | 430.3 | 47.9 | 19.9 | 79.1 | 5.2 |  |  | 784.5 | 765.3 | 715 | 734.9 | 687.1 | 769.2 | 743.8
3990.3 | 2290.3 | 463.5 | 185.4 | 216.7219 | 261 | 279 | 271.1 | 272.4 | 437 | 47.9 | 19.9 | 78.9 | 5.5 |  |  | 790.6 | 783.8 | 711.4 | 736.9 | 701.4 | 784.3 | 740.7
3991.3 | 2291.3 | 465.5 | 186.2 | 217.6571 | 261.3 | 278.2 | 271.7 | 272.1 | 436.8 | 47.8 | 19.9 | 78.8 | 5.6 |  |  | 784.8 | 792 | 700.8 | 737.1 | 707.4 | 759.3 | 729.5
3992.3 | 2292.3 | 466.4 | 186.56 | 218.0779 | 262.2 | 277.4 | 273 | 272.3 | 434.6 | 47.7 | 19.9 | 78.9 | 5.6 |  |  | 777 | 786 | 693.5 | 734.2 | 698.8 | 732.1 | 716.2
3993.3 | 2293.3 | 467 | 186.8 | 218.3584 | 262.8 | 277.4 | 274.5 | 272.9 | 442.3 | 47.5 | 19.9 | 78.8 | 4.8 |  |  | 771.9 | 788.7 | 697.5 | 730.2 | 681.6 | 710.6 | 706.3
3994.3 | 2294.3 | 466.4 | 186.56 | 218.0779 | 264 | 277.7 | 276 | 273.1 | 446.6 | 47.4 | 19.9 | 78.6 | 3.9 |  |  | 775.8 | 799.6 | 704.5 | 729.4 | 701.7 | 720.1 | 705.6
3995.3 | 2295.3 | 465.6 | 186.24 | 217.7038 | 264.8 | 277.8 | 275.8 | 273 | 457.4 | 47.3 | 19.9 | 78.5 | 5.2 |  |  | 782.8 | 798.6 | 708.1 | 729.2 | 707.9 | 726.9 | 716.5
3996.3 | 2296.3 | 466.3 | 186.52 | 218.0311 | 265 | 277.8 | 275.7 | 273.5 | 455.1 | 47.2 | 19.9 | 78.5 | 5.6 |  |  | 792.4 | 795.7 | 716.6 | 729.9 | 715.4 | 750.8 | 737.2
3997.3 | 2297.3 | 465.2 | 186.08 | 217.5168 | 265 | 278 | 276.4 | 273.9 | 466.1 | 47.1 | 19.9 | 78.3 | 4.6 |  |  | 800.9 | 816.1 | 699.4 | 731.5 | 735.3 | 763.5 | 734.4
3998.3 | 2298.3 | 465.1 | 186.04 | 217.47 | 265 | 277.9 | 276.9 | 273.6 | 474.8 | 47 | 19.9 | 78.1 | 4.9 |  |  | 796.3 | 827.8 | 676.4 | 731.6 | 746.4 | 753.2 | 721
3999.3 | 2299.3 | 465 | 186 | 217.4233 | 264.9 | 277.8 | 278 | 273 | 483.2 | 47 | 19.9 | 78.1 | 4.8 |  |  | 803.9 | 828.8 | 667.9 | 733.2 | 757.4 | 761.1 | 721.3
4000.3 | 2300.3 | 465.2 | 186.08 | 217.5168 | 264.9 | 277.9 | 279.7 | 273.2 | 486.6 | 47.1 | 19.9 | 78 | 5.2 |  |  | 808.2 | 826.7 | 655.2 | 735.6 | 764.7 | 772.3 | 724.6
4001.3 | 2301.3 | 464.8 | 185.92 | 217.3298 | 265.5 | 277.9 | 280.3 | 273.4 | 512.3 | 47.5 | 19.9 | 78 | 5.5 |  |  | 815.1 | 830.9 | 654.8 | 738.7 | 772.1 | 786.8 | 729.5
4002.3 | 2302.3 | 464.1 | 185.64 | 217.0025 | 266 | 277.8 | 280.2 | 273.3 | 523.9 | 47.6 | 19.9 | 78 | 4.6 |  |  | 817.4 | 839.6 | 660.6 | 741.8 | 775 | 787.7 | 734.4
4003.3 | 2303.3 | 463.8 | 185.52 | 216.8622 | 267.2 | 277.6 | 280.8 | 273.4 | 516.6 | 47.6 | 19.9 | 78 | 5 |  |  | 809.9 | 850.6 | 642.2 | 741 | 759.7 | 760 | 716.2
4004.3 | 2304.3 | 462 | 184.8 | 216.0206 | 268.1 | 277.4 | 281.9 | 274.1 | 512 | 47.4 | 19.9 | 78.2 | 5.6 |  |  | 799.6 | 848.7 | 631.6 | 739 | 747.5 | 738.5 | 704.6
4005.3 | 2305.3 | 461.4 | 184.56 | 215.74 | 269.4 | 277.7 | 282.6 | 275.1 | 510.5 | 47.2 | 19.9 | 78.2 | 6 |  |  | 794.2 | 842.4 | 631.8 | 736.2 | 730.3 | 711.3 | 698.3
4006.3 | 2306.3 | 461.2 | 184.48 | 215.6465 | 270.6 | 277.5 | 283.5 | 275.7 | 505.1 | 47.3 | 19.9 | 78 | 5.6 |  |  | 780.6 | 817.3 | 625.1 | 733.1 | 707.2 | 676.9 | 688.7
4007.3 | 2307.3 | 461.7 | 184.68 | 215.8803 | 270.4 | 277.5 | 284.9 | 276.8 | 489.2 | 47.5 | 19.9 | 77.9 | 5.1 |  |  | 765.9 | 777.7 | 627.6 | 729.6 | 671.6 | 646.5 | 680.7
4008.3 | 2308.3 | 462.4 | 184.96 | 216.2076 | 270 | 278.2 | 285.7 | 277.5 | 484 | 47.7 | 19.9 | 77.8 | 5.5 |  |  | 765 | 771.6 | 630.1 | 725.4 | 648.2 | 633.9 | 676.9
4009.3 | 2309.3 | 461.4 | 184.56 | 215.74 | 269.8 | 279.6 | 286.4 | 277.3 | 480 | 48 | 19.9 | 77.8 | 5.5 |  |  | 765 | 784.7 | 619.1 | 721.4 | 643.8 | 630 | 676.3
4010.3 | 2310.3 | 462.4 | 184.96 | 216.2076 | 270.2 | 281.1 | 286.8 | 276.1 | 480.9 | 48.2 | 19.9 | 77.7 | 5.3 |  |  | 751.5 | 785.9 | 602.2 | 716.7 | 633.2 | 609.2 | 668.8
4011.3 | 2311.3 | 462.9 | 185.16 | 216.4414 | 272 | 281 | 287.1 | 275.7 | 471 | 48.3 | 19.9 | 77.5 | 4.8 |  |  | 739.1 | 782.4 | 587.2 | 711.7 | 625.5 | 602.2 | 665
4012.3 | 2312.3 | 463.5 | 185.4 | 216.7219 | 274.1 | 280.8 | 286.5 | 275.9 | 468 | 48.1 | 19.9 | 77.3 | 6.2 |  |  | 731.7 | 787.1 | 575.5 | 707.3 | 618.2 | 587.6 | 662.1
4013.3 | 2313.3 | 463.3 | 185.32 | 216.6284 | 274.8 | 280.7 | 285.7 | 275.7 | 462.9 | 47.7 | 19.9 | 77.4 | 6.9 |  |  | 724.9 | 798.2 | 565.8 | 703.2 | 625.3 | 593.9 | 661.7
4014.3 | 2314.3 | 464.5 | 185.8 | 217.1895 | 274.4 | 280.1 | 285.9 | 276.6 | 459.3 | 47.6 | 19.9 | 77.5 | 6.6 |  |  | 723.3 | 807.7 | 558.3 | 698.6 | 626.9 | 597.4 | 657.7
4015.3 | 2315.3 | 465.9 | 186.36 | 217.8441 | 274.3 | 279.7 | 285.6 | 277.6 | 457.1 | 47.7 | 19.9 | 77.7 | 6.3 |  |  | 725.1 | 810.6 | 548.8 | 696.5 | 642 | 599.6 | 655.6
4016.3 | 2316.3 | 465.6 | 186.24 | 217.7038 | 274.8 | 279 | 285.5 | 278.6 | 452.9 | 47.7 | 19.9 | 77.8 | 6.1 |  |  | 734 | 821.4 | 569.6 | 697.1 | 659.7 | 623.3 | 660
4017.3 | 2317.3 | 465.4 | 186.16 | 217.6103 | 275 | 278.1 | 286 | 279.7 | 451.6 | 47.6 | 19.9 | 78.1 | 6.5 |  |  | 748.4 | 816.9 | 592.8 | 699.1 | 670.1 | 655.7 | 671.8
4018.3 | 2318.3 | 464.3 | 185.72 | 217.096 | 274.4 | 278.6 | 286.9 | 280.1 | 453.1 | 47.6 | 19.9 | 78.3 | 7.4 |  |  | 764.2 | 817.9 | 636.9 | 702.4 | 687.3 | 687.3 | 690.5
4019.3 | 2319.3 | 463.8 | 185.52 | 216.8622 | 273.5 | 279.2 | 287.7 | 280.5 | 460.3 | 47.5 | 19.9 | 78.3 | 6.9 |  |  | 777.6 | 809.8 | 663.9 | 704.4 | 698.9 | 702.6 | 702
4020.3 | 2320.3 | 463.9 | 185.56 | 216.9089 | 272.9 | 280 | 287.7 | 280.8 | 464.4 | 47.3 | 19.9 | 78.3 | 6.2 |  |  | 788.2 | 815.3 | 667.9 | 706.5 | 717.8 | 717.1 | 706.8
4021.3 | 2321.3 | 464.6 | 185.84 | 217.2363 | 272.3 | 280.9 | 287.8 | 280.8 | 464.6 | 47.1 | 19.9 | 78.1 | 5.5 |  |  | 797.4 | 812.6 | 690.8 | 707.1 | 701.3 | 699.6 | 698.7
4022.3 | 2322.3 | 464.5 | 185.8 | 217.1895 | 272.1 | 280.9 | 288.5 | 281.1 | 466.6 | 47 | 19.9 | 77.8 | 4.7 |  |  | 806.4 | 823.6 | 698.8 | 706.7 | 691 | 696.3 | 689.8
4023.3 | 2323.3 | 464.8 | 185.92 | 217.3298 | 272.2 | 280.3 | 289.4 | 280.8 | 465.7 | 47 | 19.9 | 77.6 | 6.7 |  |  | 812.3 | 833.3 | 695.7 | 706.4 | 686.1 | 709.4 | 691.7
4024.3 | 2324.3 | 464.3 | 185.72 | 217.096 | 272.6 | 280.6 | 289.9 | 280.5 | 471.4 | 46.9 | 19.9 | 77.6 | 6.4 |  |  | 812.6 | 840.2 | 684.1 | 706.2 | 687.8 | 706 | 687.4
4025.3 | 2325.3 | 464.5 | 185.8 | 217.1895 | 273.9 | 280.9 | 289.9 | 280.3 | 476.8 | 46.6 | 19.9 | 77.6 | 6.3 |  |  | 807.7 | 849 | 662.2 | 705.1 | 690.7 | 697.4 | 676.6
4026.3 | 2326.3 | 464.1 | 185.64 | 217.0025 | 274.3 | 281.5 | 290.4 | 280.5 | 475.7 | 46.5 | 19.9 | 77.5 | 5.5 |  |  | 798.6 | 851 | 644.4 | 704.7 | 688.9 | 686.4 | 667.4
4027.3 | 2327.3 | 464.1 | 185.64 | 217.0025 | 274.8 | 281.5 | 290.1 | 280.7 | 479.8 | 46.5 | 19.9 | 77.4 | 5 |  |  | 807.1 | 859 | 657.8 | 706.8 | 713 | 710.8 | 679.5
4028.3 | 2328.3 | 464 | 185.6 | 216.9557 | 275 | 281 | 290.7 | 280.9 | 498.2 | 46.5 | 19.9 | 77.7 | 5.3 |  |  | 806.6 | 855.1 | 653.2 | 710.7 | 738.4 | 725.2 | 690.6
4029.3 | 2329.3 | 464 | 185.6 | 216.9557 | 274.7 | 280.9 | 291 | 282.4 | 504.1 | 46.6 | 19.9 | 77.7 | 5.5 |  |  | 797.8 | 851.9 | 635.6 | 712.5 | 761 | 730.2 | 693.1
4030.3 | 2330.3 | 464.3 | 185.72 | 217.096 | 274 | 281.5 | 291.7 | 283.9 | 503.3 | 46.6 | 19.9 | 77.7 | 5 |  |  | 794.5 | 838.5 | 638.4 | 713.9 | 743.9 | 738 | 691
4031.3 | 2331.3 | 463.8 | 185.52 | 216.8622 | 273.7 | 282.2 | 291.3 | 284.6 | 487.2 | 46.5 | 19.9 | 77.9 | 4 |  |  | 795.8 | 807.4 | 648.2 | 713.9 | 714.9 | 728.9 | 686.8
4032.3 | 2332.3 | 464.2 | 185.68 | 217.0492 | 274 | 282.2 | 290.3 | 285.2 | 475.3 | 46.6 | 19.9 | 78 | 3.6 |  |  | 790.1 | 791.3 | 637.4 | 712.6 | 696.5 | 713.1 | 677.6
4033.3 | 2333.3 | 464 | 185.6 | 216.9557 | 275.1 | 282.7 | 289.6 | 285.2 | 472 | 46.8 | 19.9 | 78.2 | 4.7 |  |  | 777.2 | 782 | 633.5 | 709.9 | 678.6 | 690.3 | 671.1
4034.3 | 2334.3 | 463.2 | 185.28 | 216.5816 | 276.8 | 283.8 | 289.1 | 284.1 | 460.4 | 47.2 | 19.9 | 78.4 | 6.7 |  |  | 765.4 | 750.6 | 637.7 | 706.1 | 652 | 676.7 | 668.4
4035.3 | 2335.3 | 464 | 185.6 | 216.9557 | 277.9 | 284.4 | 289.3 | 283.1 | 446.6 | 47.1 | 19.9 | 78.4 | 6.4 |  |  | 753.2 | 721.2 | 635.7 | 701.7 | 639.4 | 651 | 665.1
4036.3 | 2336.3 | 464.5 | 185.8 | 217.1895 | 278 | 285.1 | 290.2 | 282.4 | 437.2 | 47 | 19.9 | 78.1 | 5.3 |  |  | 746.4 | 712.3 | 631.2 | 697.7 | 622.5 | 635.5 | 657.3
4037.3 | 2337.3 | 464.2 | 185.68 | 217.0492 | 278.4 | 285.8 | 291.2 | 281.1 | 431.7 | 46.8 | 19.9 | 78 | 4.8 |  |  | 741.5 | 718.6 | 629.1 | 692.6 | 606.6 | 623.1 | 654.4
4038.3 | 2338.3 | 464.9 | 185.96 | 217.3765 | 279.7 | 285.6 | 291.2 | 279.8 | 437.6 | 46.9 | 19.9 | 77.8 | 3.8 |  |  | 747.9 | 758.9 | 646.1 | 691.6 | 637.3 | 644.4 | 660
4039.3 | 2339.3 | 466.8 | 186.72 | 218.2649 | 279.6 | 285.8 | 290.8 | 279.3 | 449.5 | 47 | 19.9 | 77.9 | 4.6 |  |  | 766.2 | 779.7 | 676.3 | 693.6 | 662.3 | 672.9 | 677
4040.3 | 2340.3 | 467.6 | 187.04 | 218.639 | 278.3 | 285 | 289.7 | 279.5 | 454.3 | 47 | 19.9 | 78 | 4.8 |  |  | 768.3 | 786.1 | 671.9 | 695.8 | 687.3 | 701.2 | 686.4
4041.3 | 2341.3 | 468.2 | 187.28 | 218.9195 | 276.9 | 284.6 | 288.9 | 279.6 | 464.5 | 47.1 | 19.9 | 77.9 | 4.2 |  |  | 772.1 | 774.6 | 679.9 | 698.7 | 692.1 | 729.6 | 704.4
4042.3 | 2342.3 | 467.6 | 187.04 | 218.639 | 276 | 284.5 | 288.1 | 279.3 | 464.1 | 47.1 | 19.9 | 77.9 | 4.4 |  |  | 780 | 766.6 | 709.2 | 699.8 | 689.6 | 735.2 | 714.8
4043.3 | 2343.3 | 465.9 | 186.36 | 217.8441 | 275.4 | 284.2 | 287.9 | 279.2 | 461.9 | 47 | 19.9 | 77.8 | 5 |  |  | 782.3 | 757.8 | 709.4 | 699.8 | 677.4 | 726 | 705.6
4044.3 | 2344.3 | 464.5 | 185.8 | 217.1895 | 275.2 | 284.3 | 287.3 | 278.8 | 454.2 | 46.9 | 19.9 | 77.8 | 5.7 |  |  | 777.3 | 740.3 | 715.2 | 699 | 658.3 | 707.8 | 691.8
4045.3 | 2345.3 | 465.8 | 186.32 | 217.7973 | 275.5 | 284.1 | 286.9 | 278.4 | 449.4 | 46.9 | 19.9 | 77.9 | 4.6 |  |  | 781.7 | 742.3 | 697.4 | 697.5 | 661.7 | 712.8 | 695
4046.3 | 2346.3 | 466.8 | 186.72 | 218.2649 | 275.9 | 283.9 | 286.6 | 277.7 | 448.6 | 46.9 | 19.9 | 78.1 | 4.3 |  |  | 781.3 | 748.5 | 692.4 | 696 | 649.7 | 699.9 | 681.2
4047.3 | 2347.3 | 467.3 | 186.92 | 218.4987 | 276 | 283.3 | 285.9 | 276.8 | 452.4 | 46.8 | 19.9 | 78.3 | 4 |  |  | 789.6 | 761.4 | 698.6 | 697.3 | 653.2 | 727.9 | 691.9
4048.3 | 2348.3 | 467 | 186.8 | 218.3584 | 276.3 | 283.7 | 285.7 | 276.9 | 451.4 | 46.7 | 19.9 | 78.4 | 3.9 |  |  | 797.9 | 765.2 | 692.1 | 699.9 | 649 | 739.1 | 699.2
4049.3 | 2349.3 | 466 | 186.4 | 217.8909 | 276.7 | 283.7 | 285.1 | 276.9 | 452.3 | 46.7 | 19.9 | 78.6 | 4.4 |  |  | 797.8 | 774.4 | 684.8 | 698.4 | 647.8 | 714.7 | 691.2
4050.3 | 2350.3 | 466 | 186.4 | 217.8909 | 277.1 | 284.5 | 285.2 | 277.4 | 460.3 | 46.6 | 19.8 | 78.7 | 3.8 |  |  | 787 | 756.6 | 683.2 | 696.6 | 632.5 | 690.2 | 678.1
4051.3 | 2351.3 | 465.5 | 186.2 | 217.6571 | 277.4 | 287.1 | 286.7 | 276.9 | 466.9 | 46.5 | 19.9 | 78.9 | 4.3 |  |  | 779 | 746.3 | 665.8 | 693.9 | 624.6 | 672.9 | 668.1
4052.3 | 2352.3 | 465.8 | 186.32 | 217.7973 | 278.7 | 289.1 | 288.3 | 276.5 | 468.7 | 46.6 | 19.8 | 78.9 | 3.9 |  |  | 770.9 | 777.4 | 639.8 | 691.6 | 638.6 | 666.6 | 660.8
4053.3 | 2353.3 | 466.6 | 186.64 | 218.1714 | 279.7 | 291.2 | 290.1 | 276.5 | 466.2 | 46.5 | 19.8 | 79 | 3.8 |  |  | 763.3 | 798.4 | 619.9 | 690.1 | 666.8 | 660.5 | 654.1
4054.3 | 2354.3 | 466.5 | 186.6 | 218.1246 | 280.1 | 290.9 | 291 | 276.8 | 474.5 | 46.5 | 19.8 | 79.1 | 4.1 |  |  | 765.1 | 821.3 | 620.1 | 690.8 | 695.6 | 660.2 | 651.5
4055.3 | 2355.3 | 465.4 | 186.16 | 217.6103 | 279.6 | 289.4 | 292.3 | 278.1 | 484.9 | 46.5 | 19.8 | 79 | 4 |  |  | 773.4 | 839.3 | 626.7 | 692.5 | 712.8 | 665 | 655.4
4056.3 | 2356.3 | 465.5 | 186.2 | 217.6571 | 279.2 | 287.8 | 293.1 | 279.7 | 485.9 | 46.6 | 19.8 | 79.1 | 4.5 |  |  | 779.4 | 849.4 | 636.2 | 691.4 | 708.9 | 665.5 | 655.8
4057.3 | 2357.3 | 466.2 | 186.48 | 217.9844 | 279.7 | 286.6 | 293.6 | 281 | 486.7 | 46.7 | 19.8 | 79.2 | 4.4 |  |  | 787.8 | 850.8 | 652.6 | 691.3 | 705.4 | 684.5 | 663.4
4058.3 | 2358.3 | 466.2 | 186.48 | 217.9844 | 279.9 | 286.1 | 293.3 | 282.6 | 482.1 | 46.7 | 19.8 | 79.1 | 3.7 |  |  | 794.9 | 852.9 | 691.5 | 692.6 | 709.8 | 694 | 670.7
4059.3 | 2359.3 | 465.1 | 186.04 | 217.47 | 280 | 286 | 293.1 | 283.6 | 491.8 | 46.8 | 19.8 | 79 | 3.2 |  |  | 809 | 857 | 707 | 694.9 | 715 | 716.2 | 682.8
4060.3 | 2360.3 | 465 | 186 | 217.4233 | 280.1 | 286.4 | 293.8 | 284.6 | 496.4 | 46.8 | 19.8 | 78.8 | 3.9 |  |  | 813.9 | 844.6 | 704.1 | 699 | 724.4 | 742.1 | 690.8
4061.3 | 2361.3 | 464.3 | 185.72 | 217.096 | 279.6 | 287 | 293.8 | 285.2 | 492.3 | 46.7 | 19.8 | 78.6 | 4 |  |  | 809.6 | 814.6 | 722.1 | 700.1 | 695.5 | 737.2 | 696.6
4062.3 | 2362.3 | 464.7 | 185.88 | 217.283 | 278.9 | 287.5 | 292.4 | 285.4 | 484.1 | 46.7 | 19.8 | 78.4 | 3.8 |  |  | 808.2 | 807.8 | 722.6 | 701.7 | 685.6 | 734.5 | 698.7
4063.3 | 2363.3 | 465.6 | 186.24 | 217.7038 | 278.5 | 288.2 | 291.3 | 285.9 | 481.6 | 46.8 | 19.8 | 78.3 | 3.5 |  |  | 807.3 | 829.6 | 708.8 | 702.2 | 692.3 | 726.3 | 685.1
4064.3 | 2364.3 | 465 | 186 | 217.4233 | 279 | 288.4 | 290.8 | 285.7 | 496.8 | 46.8 | 19.8 | 78.2 | 3.3 |  |  | 810.9 | 829.2 | 694.2 | 703.9 | 707.1 | 750.1 | 686.5
4065.3 | 2365.3 | 465.6 | 186.24 | 217.7038 | 279.9 | 288.9 | 291.3 | 285.1 | 495.6 | 46.7 | 19.8 | 78.2 | 3.4 |  |  | 803.5 | 787.6 | 684.8 | 706.9 | 705.7 | 767.4 | 704.6
4066.3 | 2366.3 | 465.1 | 186.04 | 217.47 | 280.5 | 288.9 | 291.4 | 285.3 | 491.5 | 46.7 | 19.8 | 78.1 | 3.6 |  |  | 816.3 | 784.5 | 702.7 | 708.2 | 709 | 782.1 | 715.6
4067.3 | 2367.3 | 465.4 | 186.16 | 217.6103 | 280.3 | 289.5 | 292.4 | 285.6 | 506.5 | 46.7 | 19.8 | 78.2 | 3.6 |  |  | 833 | 807.2 | 713.3 | 711.5 | 728.7 | 789.6 | 713.7
4068.3 | 2368.3 | 465.1 | 186.04 | 217.47 | 279.8 | 290.2 | 292.8 | 286.1 | 515.2 | 46.9 | 19.8 | 78.3 | 3.8 |  |  | 829.4 | 800.9 | 726.2 | 712.4 | 716.3 | 762.9 | 702.6
4069.3 | 2369.3 | 464.9 | 185.96 | 217.3765 | 279.4 | 291 | 293.2 | 286.7 | 510.6 | 47.1 | 19.8 | 78.4 | 4.2 |  |  | 821.8 | 786.4 | 735.2 | 711.5 | 691.1 | 740.2 | 693.3
4070.3 | 2370.3 | 463.7 | 185.48 | 216.8154 | 279.1 | 291.6 | 293.1 | 286.4 | 507.3 | 47.3 | 19.8 | 78.4 | 3.8 |  |  | 813.9 | 771.4 | 747.3 | 709.8 | 671 | 729 | 690.6
4071.3 | 2371.3 | 463.6 | 185.44 | 216.7687 | 279 | 291.8 | 292.3 | 285.9 | 493.7 | 47.4 | 19.8 | 78.4 | 4.6 |  |  | 819.4 | 758.9 | 757.3 | 707.3 | 655.9 | 735.8 | 696
4072.3 | 2372.3 | 463.9 | 185.56 | 216.9089 | 279.4 | 292.8 | 291.9 | 285.2 | 486.4 | 47.5 | 19.8 | 78.2 | 4.1 |  |  | 821.7 | 762.2 | 767.7 | 703.7 | 637.1 | 721.3 | 697.1
4073.3 | 2373.3 | 463.9 | 185.56 | 216.9089 | 279.6 | 293.9 | 291.3 | 284.4 | 477.3 | 47.6 | 19.8 | 77.9 | 3.5 |  |  | 822.6 | 765.3 | 753.2 | 700.7 | 627.1 | 718.3 | 694.5
4074.3 | 2374.3 | 463.9 | 185.56 | 216.9089 | 280.2 | 293.9 | 291 | 283.8 | 475.5 | 47.7 | 19.8 | 77.9 | 3.8 |  |  | 823.7 | 787.6 | 727.9 | 700.1 | 646.3 | 731.1 | 692.5
4075.3 | 2375.3 | 461.8 | 184.72 | 215.927 | 280.7 | 293.4 | 291.2 | 282.4 | 486.4 | 47.6 | 19.8 | 78 | 3.6 |  |  | 829.8 | 795.8 | 725.3 | 702.4 | 658 | 752.2 | 699.5
4076.3 | 2376.3 | 462 | 184.8 | 216.0206 | 281.8 | 293 | 290.6 | 281.8 | 492.8 | 47.6 | 19.8 | 78.1 | 4.3 |  |  | 830.1 | 788.3 | 733.5 | 702.1 | 638.1 | 736.8 | 703.5
4077.3 | 2377.3 | 462.2 | 184.88 | 216.1141 | 281.8 | 293.5 | 289.8 | 281.2 | 490 | 47.3 | 19.8 | 78.2 | 4.5 |  |  | 833.8 | 785.2 | 745.1 | 701.4 | 633 | 732.4 | 690.8
4078.3 | 2378.3 | 461.5 | 184.6 | 215.7868 | 282.5 | 294.1 | 290.5 | 280.3 | 491.4 | 47.3 | 19.8 | 78.3 | 4.1 |  |  | 822.9 | 788.2 | 728.8 | 700 | 629 | 713.1 | 680.2
4079.3 | 2379.3 | 461.5 | 184.6 | 215.7868 | 283.6 | 295 | 290.9 | 279.3 | 488.6 | 47.3 | 19.8 | 78.5 | 3.9 |  |  | 806.4 | 786.5 | 717 | 697.4 | 619.4 | 686.3 | 672.1
4080.3 | 2380.3 | 462.2 | 184.88 | 216.1141 | 283.4 | 294.8 | 291.2 | 279 | 486.6 | 47.5 | 19.8 | 78.6 | 4.2 |  |  | 790.3 | 747 | 709.8 | 693.4 | 600 | 661.8 | 665.7
4081.3 | 2381.3 | 463.2 | 185.28 | 216.5816 | 283.3 | 294.7 | 291.4 | 278.8 | 471.8 | 47.7 | 19.8 | 78.5 | 4.1 |  |  | 787.7 | 747.1 | 693.5 | 688.9 | 594 | 660.5 | 663.6
4082.3 | 2382.3 | 464.7 | 185.88 | 217.283 | 283.2 | 294.8 | 291.9 | 278.7 | 467.8 | 47.8 | 19.8 | 78.4 | 3.8 |  |  | 791.2 | 753.1 | 712.3 | 686.2 | 586.9 | 658.8 | 667.2
4083.3 | 2383.3 | 465.3 | 186.12 | 217.5636 | 282.8 | 295.1 | 292.3 | 278.2 | 469.6 | 47.9 | 19.8 | 78.1 | 3.5 |  |  | 781.3 | 725.3 | 711.5 | 683.3 | 567.9 | 637.7 | 664.1
4084.3 | 2384.3 | 464.8 | 185.92 | 217.3298 | 283.1 | 295.8 | 291.9 | 278.2 | 463.3 | 48 | 19.8 | 77.8 | 4 |  |  | 774.5 | 703.6 | 723.9 | 679.4 | 546.3 | 626.8 | 664.6
4085.3 | 2385.3 | 464.9 | 185.96 | 217.3765 | 282.6 | 296.8 | 292 | 278.8 | 456 | 47.9 | 19.8 | 77.8 | 4.1 |  |  | 781.6 | 690.5 | 741.8 | 675.8 | 543.4 | 642.9 | 676.3
4086.3 | 2386.3 | 464.4 | 185.76 | 217.1427 | 282 | 297.6 | 291.5 | 278.6 | 455.7 | 47.7 | 19.8 | 77.7 | 4 |  |  | 800 | 731.4 | 742.9 | 675.1 | 561.6 | 666.6 | 684.3
4087.3 | 2387.3 | 464.1 | 185.64 | 217.0025 | 281.5 | 297.9 | 290.4 | 278.9 | 464.2 | 47.4 | 19.8 | 77.7 | 3.8 |  |  | 802.5 | 761.4 | 712.7 | 673.7 | 578.9 | 663 | 676.3
4088.3 | 2388.3 | 465.2 | 186.08 | 217.5168 | 281.7 | 297.6 | 290.1 | 279.6 | 463.4 | 47.6 | 19.8 | 77.8 | 4.3 |  |  | 798 | 744.2 | 729.8 | 672.5 | 579.3 | 653 | 680.9
4089.3 | 2389.3 | 464.8 | 185.92 | 217.3298 | 282.6 | 297.8 | 289.9 | 280.4 | 460.1 | 48 | 19.8 | 78 | 4.7 |  |  | 784.4 | 708.6 | 752.3 | 670.5 | 558.1 | 640.7 | 686.3
4090.3 | 2390.3 | 464.6 | 185.84 | 217.2363 | 283 | 298.1 | 289.4 | 281.2 | 451.4 | 47.9 | 19.8 | 78.1 | 5.8 |  |  | 783.7 | 702.1 | 775.7 | 669.5 | 551.4 | 653 | 699.2
4091.3 | 2391.3 | 464.3 | 185.72 | 217.096 | 282.3 | 298.4 | 288.3 | 282.7 | 447.1 | 47.7 | 19.8 | 78.2 | 5.7 |  |  | 785.2 | 687.3 | 779.7 | 667.4 | 533 | 641.4 | 703.5
4092.3 | 2392.3 | 464.8 | 185.92 | 217.3298 | 281.8 | 298.1 | 286.8 | 283.6 | 445.1 | 47.6 | 19.8 | 78.4 | 5.2 |  |  | 787.7 | 689.3 | 781.5 | 665.2 | 531.1 | 643.7 | 702.9
4093.3 | 2393.3 | 464.9 | 185.96 | 217.3765 | 281.3 | 297.8 | 285.2 | 284.1 | 443.1 | 47.4 | 19.8 | 78.4 | 4.2 |  |  | 780.1 | 677.9 | 777.1 | 663.2 | 525.4 | 639 | 695.4
4094.3 | 2394.3 | 464.3 | 185.72 | 217.096 | 280.8 | 298.6 | 284.9 | 283.7 | 434.3 | 47.3 | 19.8 | 78.6 | 3.9 |  |  | 776.5 | 660.5 | 787.1 | 661.1 | 515.8 | 637.4 | 701.5
4095.3 | 2395.3 | 464.5 | 185.8 | 217.1895 | 280.5 | 299.6 | 285 | 283.6 | 428.3 | 47.5 | 19.8 | 78.8 | 4.5 |  |  | 779.7 | 665 | 790.3 | 659.2 | 522.1 | 660.6 | 711
4096.3 | 2396.3 | 463.4 | 185.36 | 216.6752 | 280.1 | 300.1 | 284.8 | 283.3 | 427.5 | 47.5 | 19.8 | 79 | 4.9 |  |  | 780.6 | 659.6 | 784 | 657.7 | 514.4 | 647 | 702.8
4097.3 | 2397.3 | 462.9 | 185.16 | 216.4414 | 279.8 | 299.7 | 284.9 | 281.6 | 426.9 | 47.5 | 19.8 | 79.3 | 5.4 |  |  | 759.3 | 633.9 | 760.4 | 655.3 | 497.7 | 616.4 | 682.5
4098.3 | 2398.3 | 461.9 | 184.76 | 215.9738 | 279.5 | 299.8 | 287.1 | 279.9 | 423.4 | 47.8 | 19.8 | 79.3 | 5.4 |  |  | 742.7 | 610.8 | 749.9 | 652.8 | 480.7 | 590.2 | 672.6
4099.3 | 2399.3 | 461.1 | 184.44 | 215.5997 | 279.5 | 299.9 | 289.7 | 278.2 | 417.9 | 47.8 | 19.8 | 79.3 | 5 |  |  | 738 | 589.2 | 766.8 | 650 | 465.8 | 588.5 | 676.3
4100.3 | 2400.3 | 460 | 184 | 215.0854 | 279.4 | 300.1 | 290 | 277.2 | 416.2 | 47.8 | 19.8 | 79.2 | 4.1 |  |  | 736.2 | 571.1 | 787.4 | 647 | 453.1 | 587 | 689
4101.3 | 2401.3 | 460.2 | 184.08 | 215.1789 | 279 | 301.5 | 289.5 | 276.4 | 414 | 47.7 | 19.8 | 79.2 | 3.8 |  |  | 733.1 | 570.6 | 778.4 | 643.8 | 457 | 617.1 | 695.9
4102.3 | 2402.3 | 462.3 | 184.92 | 216.1608 | 278.8 | 302 | 289.2 | 276 | 415.1 | 47.5 | 19.8 | 79.2 | 3.9 |  |  | 757 | 619.1 | 778.3 | 644.4 | 496.2 | 668.9 | 712.7
4103.3 | 2403.3 | 462.7 | 185.08 | 216.3479 | 278.6 | 301.6 | 288.5 | 277 | 434.5 | 47.2 | 19.8 | 79.2 | 5.6 |  |  | 774.3 | 670.2 | 771.2 | 646 | 511.3 | 682.4 | 707
4104.3 | 2404.3 | 462.5 | 185 | 216.2543 | 278.6 | 300.8 | 287.1 | 278.8 | 451.3 | 47.1 | 19.8 | 79.4 | 6.9 |  |  | 779.7 | 710.5 | 754.7 | 647.3 | 529.9 | 687.5 | 694.3
4105.3 | 2405.3 | 461.2 | 184.48 | 215.6465 | 278.9 | 299.6 | 286.4 | 279 | 456.7 | 46.6 | 19.8 | 79.5 | 7.5 |  |  | 784 | 750.3 | 732.5 | 648.9 | 564 | 695.8 | 687.5
4106.3 | 2406.3 | 461.6 | 184.64 | 215.8335 | 279.4 | 298.5 | 286.2 | 278.8 | 476.3 | 46.4 | 19.8 | 79.3 | 6.6 |  |  | 784.2 | 783.3 | 707.5 | 653.6 | 616 | 708.3 | 683.4
4107.3 | 2407.3 | 463.3 | 185.32 | 216.6284 | 279.8 | 297.5 | 287 | 278.8 | 483 | 46.5 | 19.8 | 79 | 6.4 |  |  | 777.5 | 796.2 | 694.2 | 656.4 | 642.3 | 695.2 | 678.1
4108.3 | 2408.3 | 463.3 | 185.32 | 216.6284 | 279.7 | 297 | 287.5 | 280.1 | 480.8 | 46.4 | 19.8 | 78.8 | 5.6 |  |  | 784.6 | 801.6 | 696.6 | 660.1 | 671.2 | 709.2 | 682.1
4109.3 | 2409.3 | 462 | 184.8 | 216.0206 | 280 | 297.4 | 287.5 | 280.6 | 484.6 | 46.4 | 19.8 | 78.7 | 6.1 |  |  | 798.8 | 782.4 | 717.4 | 662.7 | 657.7 | 707.7 | 687.5
4110.3 | 2410.3 | 461.6 | 184.64 | 215.8335 | 280.5 | 298.8 | 288 | 279.9 | 483.2 | 46.3 | 19.8 | 78.5 | 5.2 |  |  | 803.4 | 758.2 | 746.1 | 661.4 | 630.8 | 699.5 | 681.5
4111.3 | 2411.3 | 462 | 184.8 | 216.0206 | 280.3 | 300.7 | 289 | 279.6 | 479.4 | 46.1 | 19.8 | 78.3 | 6.6 |  |  | 808 | 752.6 | 756.3 | 662.3 | 613.6 | 706.4 | 690.3
4112.3 | 2412.3 | 462.8 | 185.12 | 216.3946 | 280.3 | 301.7 | 289.3 | 279.2 | 479.1 | 46 | 19.8 | 78.2 | 7.1 |  |  | 798.4 | 727.1 | 761.3 | 661.6 | 587.6 | 677.6 | 682.6
4113.3 | 2413.3 | 463.1 | 185.24 | 216.5349 | 280.4 | 303.1 | 290.8 | 278.2 | 474.2 | 45.9 | 19.8 | 78.1 | 6.3 |  |  | 785.2 | 712.7 | 760.8 | 659.5 | 564.8 | 658.1 | 680.7
4114.3 | 2414.3 | 462.7 | 185.08 | 216.3479 | 280.6 | 304.8 | 292.3 | 278 | 459.4 | 46 | 19.8 | 77.9 | 5.3 |  |  | 779.4 | 713.1 | 739.5 | 656 | 559.3 | 655.5 | 676
4115.3 | 2415.3 | 461.5 | 184.6 | 215.7868 | 280.8 | 304.6 | 293 | 278.2 | 453.6 | 46.4 | 19.8 | 77.8 | 5.6 |  |  | 782.5 | 722.3 | 737.9 | 654 | 564.4 | 648.8 | 672.5
4116.3 | 2416.3 | 462.6 | 185.04 | 216.3011 | 281.1 | 304.1 | 293.4 | 279 | 462.8 | 46.4 | 19.8 | 78 | 5.5 |  |  | 787 | 733.7 | 750.4 | 652.9 | 582.3 | 649.1 | 674.4
4117.3 | 2417.3 | 462.9 | 185.16 | 216.4414 | 281.7 | 303.9 | 293.6 | 279.8 | 470.6 | 46.3 | 19.8 | 78 | 4.8 |  |  | 787.6 | 739.3 | 770.7 | 652.7 | 584.4 | 644.3 | 680.9
4118.3 | 2418.3 | 462.4 | 184.96 | 216.2076 | 282.3 | 304.1 | 293.3 | 280.4 | 474.3 | 46.2 | 19.8 | 77.9 | 6.1 |  |  | 787.4 | 733.1 | 774.9 | 651.9 | 571 | 642.8 | 681.2
4119.3 | 2419.3 | 461.9 | 184.76 | 215.9738 | 283 | 304.7 | 293.5 | 281.9 | 466.9 | 46.1 | 19.8 | 78 | 6.8 |  |  | 781.3 | 715.9 | 771.5 | 650.5 | 552 | 632.2 | 672.2
4120.3 | 2420.3 | 463 | 185.2 | 216.4881 | 284.3 | 304.3 | 294 | 282.5 | 459.1 | 46.1 | 19.8 | 78.1 | 5.9 |  |  | 774.6 | 704.5 | 763.5 | 648.9 | 539.7 | 614.6 | 667.5
4121.3 | 2421.3 | 463.4 | 185.36 | 216.6752 | 284.9 | 303.3 | 293.5 | 283.1 | 451.6 | 46.2 | 19.8 | 78.1 | 7 |  |  | 761.1 | 692.7 | 728.5 | 646.6 | 526.7 | 590.2 | 659.8
4122.3 | 2422.3 | 462.6 | 185.04 | 216.3011 | 286.8 | 303 | 292.3 | 282.7 | 450.6 | 46.4 | 19.8 | 78.3 | 7.6 |  |  | 757.9 | 713.2 | 704 | 644 | 534 | 595.1 | 659.4
4123.3 | 2423.3 | 462.3 | 184.92 | 216.1608 | 288.2 | 302.4 | 291.2 | 281 | 451.1 | 46.9 | 19.8 | 78.4 | 6.5 |  |  | 773.7 | 739.4 | 723.8 | 643.3 | 568.4 | 636.7 | 678
4124.3 | 2424.3 | 461.5 | 184.6 | 215.7868 | 288.2 | 301.4 | 291.2 | 279.7 | 456.7 | 47 | 19.8 | 78.5 | 7.1 |  |  | 780 | 761 | 735.5 | 645.3 | 579.6 | 672.7 | 695.2
4125.3 | 2425.3 | 463.1 | 185.24 | 216.5349 | 287 | 300.5 | 291.4 | 280.6 | 462.7 | 47 | 19.8 | 78.4 | 5.4 |  |  | 790 | 774.6 | 738.5 | 647.2 | 595.6 | 691.8 | 696.2
4126.3 | 2426.3 | 466.1 | 186.44 | 217.9376 | 286.1 | 300.3 | 292.9 | 281.8 | 461.4 | 47 | 19.8 | 78.3 | 4.6 |  |  | 792.1 | 777.9 | 721.9 | 647.8 | 599.8 | 698.3 | 693.9
4127.3 | 2427.3 | 467.1 | 186.84 | 218.4052 | 285.5 | 301 | 293.5 | 282.8 | 466.4 | 46.9 | 19.8 | 78.2 | 5.3 |  |  | 786.3 | 791.2 | 692.5 | 648 | 603.1 | 690.7 | 680.6
4128.3 | 2428.3 | 467.6 | 187.04 | 218.639 | 285.2 | 300.5 | 293 | 282.9 | 472.6 | 46.9 | 19.8 | 78.2 | 6.9 |  |  | 784.2 | 798.1 | 683.7 | 648.8 | 619.9 | 694.2 | 676.8
4129.3 | 2429.3 | 467.5 | 187 | 218.5922 | 284.6 | 299.7 | 292.9 | 282.6 | 494.5 | 47.1 | 19.8 | 78.2 | 8.3 |  |  | 801.8 | 801.1 | 717.1 | 652.5 | 629 | 721.4 | 692.1
4130.3 | 2430.3 | 467.9 | 187.16 | 218.7793 | 284 | 300.5 | 293.7 | 282.9 | 500.8 | 47.3 | 19.8 | 78.4 | 8 |  |  | 816.1 | 790.5 | 727.4 | 656.2 | 636.9 | 751.7 | 710.8
4131.3 | 2431.3 | 467.4 | 186.96 | 218.5455 | 283.5 | 301.2 | 293.5 | 283.7 | 507.6 | 47.5 | 19.8 | 78.5 | 5.6 |  |  | 820.5 | 813.7 | 718 | 659.8 | 665.2 | 759.4 | 707.8
4132.3 | 2432.3 | 465.1 | 186.04 | 217.47 | 283.3 | 300.3 | 293.2 | 284.2 | 506.9 | 47.5 | 19.8 | 78.5 | 5.2 |  |  | 818.4 | 832.6 | 695.1 | 662.1 | 685 | 756.7 | 697
4133.3 | 2433.3 | 464.5 | 185.8 | 217.1895 | 283.8 | 298.6 | 293.1 | 284.8 | 507.7 | 47.5 | 19.8 | 78.3 | 6.7 |  |  | 803 | 842 | 678.4 | 662.9 | 701.4 | 738.1 | 682.9
4134.3 | 2434.3 | 464.7 | 185.88 | 217.283 | 284.5 | 296.9 | 294.2 | 285.7 | 502 | 47.5 | 19.8 | 78.1 | 5.7 |  |  | 801.3 | 849.1 | 665.3 | 664.6 | 711.2 | 724.1 | 677.5
4135.3 | 2435.3 | 465 | 186 | 217.4233 | 284.6 | 296 | 294.9 | 286.8 | 505.4 | 47.5 | 19.8 | 78.1 | 6.3 |  |  | 797 | 854.4 | 647.9 | 666.1 | 709.7 | 724.5 | 673.8
4136.3 | 2436.3 | 465.7 | 186.28 | 217.7506 | 284.5 | 295.2 | 295.2 | 287.4 | 499.7 | 47.6 | 19.8 | 78.1 | 6.5 |  |  | 805.3 | 863.1 | 634.9 | 668.1 | 717.1 | 731.6 | 672.3
4137.3 | 2437.3 | 466.3 | 186.52 | 218.0311 | 283.9 | 294.7 | 295.2 | 287.5 | 512.7 | 47.6 | 19.8 | 77.9 | 5.9 |  |  | 821.1 | 867 | 644.3 | 672.4 | 723.3 | 758.2 | 683.6
4138.3 | 2438.3 | 465.7 | 186.28 | 217.7506 | 283.5 | 294.7 | 294.8 | 287.3 | 521 | 47.8 | 19.8 | 77.6 | 6.6 |  |  | 826.3 | 851.9 | 659.5 | 678.1 | 734.3 | 793.3 | 703.7
4139.3 | 2439.3 | 466 | 186.4 | 217.8909 | 283.4 | 294.6 | 294.4 | 287.9 | 520.3 | 47.8 | 19.8 | 77.7 | 7.5 |  |  | 829.6 | 847.9 | 671.4 | 683.9 | 739.2 | 808.6 | 714.4
4140.3 | 2440.3 | 465.4 | 186.16 | 217.6103 | 283.8 | 295 | 294.9 | 288.4 | 520.6 | 47.4 | 19.8 | 77.6 | 7.1 |  |  | 832.1 | 836.4 | 688.2 | 687.6 | 731.1 | 798.9 | 718.6
4141.3 | 2441.3 | 464.3 | 185.72 | 217.096 | 284.1 | 295.8 | 295.4 | 288.5 | 512.8 | 47 | 19.8 | 77.4 | 7.5 |  |  | 830.8 | 808.9 | 712.9 | 688 | 715 | 775.7 | 715.1
4142.3 | 2442.3 | 464 | 185.6 | 216.9557 | 284.4 | 297.4 | 295.5 | 287.6 | 503.3 | 46.9 | 19.8 | 77.2 | 8.7 |  |  | 826.3 | 800.5 | 705.6 | 688 | 703.7 | 769.8 | 710.1
4143.3 | 2443.3 | 464.4 | 185.76 | 217.1427 | 284.3 | 299 | 295.1 | 287 | 488.3 | 47 | 19.8 | 76.9 | 7.4 |  |  | 817.7 | 789.3 | 706.3 | 689.3 | 695.5 | 768.6 | 711.3
4144.3 | 2444.3 | 464.6 | 185.84 | 217.2363 | 284.2 | 299.1 | 293.9 | 286.6 | 483.8 | 47.1 | 19.8 | 76.8 | 6.9 |  |  | 827.2 | 804.4 | 696.2 | 693.1 | 716.4 | 790 | 717.4
4145.3 | 2445.3 | 464.2 | 185.68 | 217.0492 | 284.1 | 298.8 | 293.3 | 286.4 | 499.4 | 47.1 | 19.8 | 76.8 | 6.2 |  |  | 837.8 | 816.8 | 697.8 | 697.5 | 732.3 | 805.9 | 719.5
4146.3 | 2446.3 | 464.4 | 185.76 | 217.1427 | 283.7 | 298.6 | 292.8 | 287 | 500.6 | 47.2 | 19.8 | 76.9 | 6 |  |  | 833.5 | 813.7 | 710.6 | 701.9 | 742.1 | 811 | 716
4147.3 | 2447.3 | 465.6 | 186.24 | 217.7038 | 283.6 | 298.4 | 293.2 | 288.1 | 497.9 | 47.2 | 19.8 | 77 | 5.6 |  |  | 837.7 | 815.7 | 720.2 | 704.9 | 742.1 | 801.8 | 720.8
4148.3 | 2448.3 | 466.6 | 186.64 | 218.1714 | 283.4 | 298.4 | 293.4 | 288.4 | 500 | 46.9 | 19.8 | 77.2 | 5.8 |  |  | 832.2 | 805.1 | 732.8 | 704.2 | 720.5 | 778.5 | 717.6
4149.3 | 2449.3 | 466.5 | 186.6 | 218.1246 | 283.5 | 299.1 | 294.8 | 288.2 | 492.7 | 46.5 | 19.8 | 77.6 | 5.3 |  |  | 820.9 | 799.4 | 745.7 | 702.7 | 704.4 | 760.4 | 711.5
4150.3 | 2450.3 | 465.9 | 186.36 | 217.8441 | 284.2 | 298.9 | 295.1 | 288.5 | 483.2 | 46.3 | 19.8 | 77.8 | 4.3 |  |  | 834.1 | 806.1 | 752 | 702 | 708.9 | 772.3 | 713.9
4151.3 | 2451.3 | 465.8 | 186.32 | 217.7973 | 284.4 | 298.4 | 294.4 | 288.4 | 487.4 | 46.4 | 19.8 | 77.9 | 4.8 |  |  | 831.3 | 800.8 | 739.6 | 704.2 | 714.6 | 793.1 | 723.9
4152.3 | 2452.3 | 466.3 | 186.52 | 218.0311 | 284.1 | 297.8 | 294.2 | 288.3 | 483.4 | 46.6 | 19.8 | 77.9 | 5.2 |  |  | 819.1 | 776.2 | 749 | 704.7 | 697.2 | 784.8 | 734.1
4153.3 | 2453.3 | 467.6 | 187.04 | 218.639 | 283.5 | 297.1 | 293.2 | 288.9 | 472.1 | 46.8 | 19.8 | 78 | 5.2 |  |  | 811.7 | 740.1 | 758.5 | 702.9 | 665.1 | 760.8 | 729.7
4154.3 | 2454.3 | 467.6 | 187.04 | 218.639 | 282.7 | 297.5 | 291.6 | 289.5 | 468.9 | 47 | 19.8 | 78 | 4.1 |  |  | 801.4 | 715.5 | 757.5 | 701 | 636 | 745.6 | 725.9
4155.3 | 2455.3 | 467.1 | 186.84 | 218.4052 | 282.2 | 297.7 | 291.2 | 289.4 | 463.5 | 47.1 | 19.8 | 78 | 3.2 |  |  | 806.1 | 739 | 751.3 | 699.6 | 638 | 753.6 | 725.5
4156.3 | 2456.3 | 466.4 | 186.56 | 218.0779 | 282.6 | 297.2 | 290.5 | 289.3 | 477.7 | 47.1 | 19.8 | 77.9 | 3.1 |  |  | 801.8 | 765.9 | 733.5 | 699 | 655.7 | 745.5 | 718.6
4157.3 | 2457.3 | 466.8 | 186.72 | 218.2649 | 283 | 297 | 289.1 | 289.1 | 478.5 | 47 | 19.7 | 77.9 | 3.2 |  |  | 783.6 | 776.4 | 713.9 | 696.8 | 688.5 | 741.6 | 710.6
4158.3 | 2458.3 | 467.2 | 186.88 | 218.452 | 283.7 | 296.7 | 287.8 | 288.9 | 484.4 | 46.7 | 19.8 | 78.2 | 2.8 |  |  | 775.9 | 782.2 | 689.9 | 698.9 | 718.4 | 756.9 | 710.8
4159.3 | 2459.3 | 467.2 | 186.88 | 218.452 | 283.7 | 295.7 | 287.8 | 288.5 | 489.5 | 47 | 19.8 | 78.4 | 2.7 |  |  | 778.2 | 774.1 | 681.2 | 703.2 | 730.8 | 784.4 | 730.8
4160.3 | 2460.3 | 467.6 | 187.04 | 218.639 | 283.5 | 295 | 288.8 | 288.8 | 488.2 | 47.2 | 19.8 | 78.5 | 2.5 |  |  | 792 | 781.3 | 697 | 705.9 | 731.6 | 801.9 | 743.9
4161.3 | 2461.3 | 467.5 | 187 | 218.5922 | 283 | 295.3 | 288.7 | 288.5 | 488.8 | 47.2 | 19.7 | 78.7 | 2.7 |  |  | 802.9 | 797.6 | 697.5 | 708.7 | 740.3 | 807 | 738
4162.3 | 2462.3 | 467.1 | 186.84 | 218.4052 | 282.7 | 295.9 | 289.2 | 288.4 | 498.1 | 47.2 | 19.8 | 79.1 | 2.8 |  |  | 808.3 | 817 | 686.6 | 711.1 | 756 | 804.5 | 731.5
4163.3 | 2463.3 | 467 | 186.8 | 218.3584 | 282.6 | 296.2 | 289.5 | 288.5 | 497.6 | 47.1 | 19.7 | 79.2 | 2.6 |  |  | 820.8 | 822.2 | 680 | 714.3 | 762 | 817.4 | 737
4164.3 | 2464.3 | 467.2 | 186.88 | 218.452 | 282.5 | 296.5 | 289.5 | 288.7 | 493.9 | 46.8 | 19.7 | 79.2 | 3.1 |  |  | 835.2 | 825.9 | 678.6 | 716.7 | 763.9 | 826 | 739.3
4165.3 | 2465.3 | 467.6 | 187.04 | 218.639 | 282.8 | 296.3 | 289.9 | 288.2 | 497.5 | 46.5 | 19.7 | 79.1 | 3.1 |  |  | 846.8 | 827.5 | 691.9 | 718.2 | 750.7 | 824.3 | 740.6
4166.3 | 2466.3 | 467.5 | 187 | 218.5922 | 283.2 | 297.3 | 290 | 288 | 503.2 | 46.2 | 19.7 | 79 | 3.2 |  |  | 856.5 | 829.5 | 705.7 | 720.3 | 740.2 | 824.7 | 746.1
4167.3 | 2467.3 | 467.4 | 186.96 | 218.5455 | 284 | 298.5 | 290.7 | 287.9 | 506.4 | 46.1 | 19.7 | 78.9 | 3 |  |  | 860.2 | 840.8 | 720.8 | 722.3 | 738 | 826.7 | 746.1
4168.3 | 2468.3 | 466.4 | 186.56 | 218.0779 | 284.7 | 299 | 291.2 | 287.9 | 512.2 | 45.8 | 19.7 | 78.8 | 3.5 |  |  | 866.9 | 836.7 | 727.2 | 723.4 | 729.2 | 826.7 | 742.7
4169.3 | 2469.3 | 467.1 | 186.84 | 218.4052 | 284.9 | 299.6 | 291.8 | 287.5 | 515.2 | 45.7 | 19.7 | 78.5 | 2.9 |  |  | 869.6 | 831.6 | 747.3 | 722.5 | 710.9 | 813.9 | 739.2
4170.3 | 2470.3 | 467.8 | 187.12 | 218.7325 | 284.9 | 300.7 | 293 | 287.4 | 511.5 | 45.8 | 19.7 | 78.3 | 2.7 |  |  | 867 | 806.3 | 771.4 | 721.4 | 690.2 | 813.8 | 750.3
4171.3 | 2471.3 | 467.6 | 187.04 | 218.639 | 284.9 | 302.4 | 293.4 | 287.4 | 499.9 | 45.9 | 19.7 | 78.2 | 2.8 |  |  | 861.1 | 789.6 | 791.8 | 719.3 | 672.5 | 805.5 | 756.9
4172.3 | 2472.3 | 467.7 | 187.08 | 218.6857 | 284.9 | 303.1 | 292.9 | 287.8 | 492 | 46.1 | 19.7 | 78.1 | 3 |  |  | 865.5 | 786.3 | 786.2 | 719.3 | 675 | 819.2 | 764.5
4173.3 | 2473.3 | 468 | 187.2 | 218.826 | 284.9 | 303.1 | 292.5 | 287.9 | 494.5 | 46.2 | 19.7 | 78.1 | 3.1 |  |  | 861.1 | 775 | 769.9 | 718.8 | 666.3 | 826.2 | 773.7
4174.3 | 2474.3 | 467 | 186.8 | 218.3584 | 284.4 | 302.4 | 292.4 | 289.1 | 483.4 | 46.2 | 19.7 | 78.2 | 3.6 |  |  | 839.9 | 738.1 | 770 | 716.7 | 642.4 | 795.1 | 764.8
4175.3 | 2475.3 | 465.2 | 186.08 | 217.5168 | 284.3 | 301.5 | 292.7 | 290.3 | 468.6 | 45.9 | 19.7 | 78.5 | 3.5 |  |  | 824 | 715.3 | 771.2 | 713.1 | 621.5 | 769.1 | 757.2
4176.3 | 2476.3 | 465.5 | 186.2 | 217.6571 | 284.2 | 301.1 | 293.1 | 291.3 | 457.7 | 45.8 | 19.7 | 78.6 | 3.1 |  |  | 827.3 | 719 | 766.3 | 710.2 | 615.3 | 779.4 | 757.3
4177.3 | 2477.3 | 465.4 | 186.16 | 217.6103 | 284.1 | 300.4 | 293.1 | 290.7 | 450.8 | 45.8 | 19.7 | 78.5 | 3 |  |  | 833.5 | 718.2 | 780.6 | 708.5 | 604.7 | 786.2 | 764.4
4178.3 | 2478.3 | 465.7 | 186.28 | 217.7506 | 284.4 | 300.8 | 293 | 289 | 448.2 | 45.8 | 19.7 | 78.5 | 3 |  |  | 825.9 | 698.9 | 787.3 | 706.3 | 585.3 | 756 | 756.8
4179.3 | 2479.3 | 466 | 186.4 | 217.8909 | 284.9 | 301.2 | 291.8 | 288.5 | 441.9 | 45.7 | 19.7 | 78.7 | 3.2 |  |  | 818.7 | 684.3 | 789.9 | 702.4 | 571.7 | 734.9 | 744
4180.3 | 2480.3 | 466.3 | 186.52 | 218.0311 | 285.3 | 300.3 | 290.7 | 287.7 | 451.5 | 45.5 | 19.7 | 79 | 3.8 |  |  | 830.1 | 699.4 | 790.6 | 699.3 | 564.4 | 727.9 | 744.7
4181.3 | 2481.3 | 466.2 | 186.48 | 217.9844 | 285.5 | 300.4 | 289.9 | 286.7 | 460.4 | 45.6 | 19.7 | 79.2 | 4.1 |  |  | 832.3 | 697 | 787.2 | 696 | 555.1 | 731.7 | 750.3
4182.3 | 2482.3 | 466.5 | 186.6 | 218.1246 | 285.4 | 301.1 | 288.8 | 286.5 | 455.1 | 45.7 | 19.7 | 79.4 | 3.7 |  |  | 821.4 | 679.3 | 771.1 | 693.3 | 545 | 725.1 | 751.9
4183.3 | 2483.3 | 466.7 | 186.68 | 218.2182 | 285 | 301.9 | 287.4 | 286.1 | 446.5 | 45.9 | 19.7 | 79.5 | 3.5 |  |  | 821 | 683.3 | 769.3 | 691.3 | 536.9 | 724.3 | 756.8
4184.3 | 2484.3 | 466.9 | 186.76 | 218.3117 | 284.3 | 301.3 | 286.4 | 285.9 | 443.6 | 45.7 | 19.7 | 79.6 | 3.5 |  |  | 810.2 | 677.4 | 766.8 | 687.4 | 537.4 | 718.9 | 750.5
4185.3 | 2485.3 | 467 | 186.8 | 218.3584 | 283.1 | 300.5 | 285.1 | 285.5 | 442.5 | 45.6 | 19.7 | 79.7 | 4.3 |  |  | 820.4 | 704.8 | 756.1 | 685.9 | 542.2 | 723.2 | 748.6
4186.3 | 2486.3 | 467.2 | 186.88 | 218.452 | 282.4 | 300.3 | 284.6 | 284.7 | 445.7 | 45.5 | 19.7 | 80 | 4.2 |  |  | 804.1 | 724.2 | 731.5 | 683.2 | 538.3 | 695.9 | 731.5
4187.3 | 2487.3 | 467 | 186.8 | 218.3584 | 281.9 | 299.3 | 285 | 284.2 | 445.5 | 45.4 | 19.7 | 80.1 | 3.8 |  |  | 793.6 | 751.4 | 728 | 680.6 | 553 | 682.7 | 722.8
4188.3 | 2488.3 | 467.1 | 186.84 | 218.4052 | 281.3 | 298.2 | 284.6 | 284.4 | 443.1 | 45.4 | 19.7 | 80.2 | 3.6 |  |  | 791.9 | 783.6 | 709.4 | 681.3 | 608.3 | 702.6 | 724.2
4189.3 | 2489.3 | 467.3 | 186.92 | 218.4987 | 280.9 | 297.4 | 283.9 | 284.7 | 452.5 | 45.4 | 19.7 | 80.3 | 3.5 |  |  | 801.2 | 802.9 | 717.8 | 684.2 | 645.9 | 733.3 | 735.7
4190.3 | 2490.3 | 467.2 | 186.88 | 218.452 | 280.8 | 296.6 | 285.1 | 284.9 | 459.9 | 45.6 | 19.7 | 80.6 | 4.4 |  |  | 818.1 | 814.1 | 735.2 | 685.9 | 646.2 | 754.2 | 746
4191.3 | 2491.3 | 467.2 | 186.88 | 218.452 | 280.7 | 296.8 | 286.5 | 285.8 | 467.8 | 45.8 | 19.7 | 80.9 | 3.9 |  |  | 828.9 | 825.6 | 731.5 | 687.4 | 666.1 | 767 | 750
4192.3 | 2492.3 | 467.2 | 186.88 | 218.452 | 280.4 | 297.4 | 287.8 | 286.6 | 473.6 | 45.9 | 19.7 | 80.8 | 3.7 |  |  | 830.6 | 827.7 | 735.6 | 688.4 | 683.9 | 759.1 | 748.3
4193.3 | 2493.3 | 467.1 | 186.84 | 218.4052 | 280.4 | 297.3 | 288.8 | 287.1 | 466.4 | 45.9 | 19.7 | 80.8 | 4.1 |  |  | 812.6 | 794.9 | 745.4 | 688.2 | 659.7 | 717.4 | 738.9
4194.3 | 2494.3 | 467.4 | 186.96 | 218.5455 | 280.4 | 296.6 | 289.2 | 287.2 | 452 | 45.8 | 19.7 | 80.7 | 3.6 |  |  | 811.6 | 771.7 | 755.5 | 686.7 | 633.9 | 712.5 | 732.6
4195.3 | 2495.3 | 467.4 | 186.96 | 218.5455 | 280.7 | 296.7 | 288.9 | 287 | 445.3 | 45.8 | 19.7 | 80.6 | 3.4 |  |  | 829.5 | 778.5 | 758.2 | 686.1 | 629.8 | 739.2 | 741.4
4196.3 | 2496.3 | 465.9 | 186.36 | 217.8441 | 281.5 | 296.8 | 288.3 | 286.6 | 456.6 | 46 | 19.7 | 80.7 | 4.4 |  |  | 827.8 | 788.8 | 745.9 | 686.7 | 640.9 | 748.4 | 747.4
4197.3 | 2497.3 | 466.6 | 186.64 | 218.1714 | 281.7 | 296.3 | 287.8 | 285.7 | 460 | 46.2 | 19.7 | 80.9 | 4.6 |  |  | 821.2 | 796 | 716.6 | 686.4 | 644.9 | 743 | 739.1
4198.3 | 2498.3 | 468 | 187.2 | 218.826 | 282.2 | 295.9 | 287.3 | 285.1 | 465.4 | 46.2 | 19.7 | 81.1 | 3.9 |  |  | 808.7 | 799.7 | 709.8 | 685.1 | 649.3 | 717.6 | 725
4199.3 | 2499.3 | 468.9 | 187.56 | 219.2468 | 283.1 | 295.2 | 286.6 | 284.6 | 466.4 | 46.2 | 19.7 | 81.3 | 3.4 |  |  | 802.8 | 801.5 | 729.5 | 684.4 | 656.1 | 701.5 | 722.1
4200.3 | 2500.3 | 466.4 | 186.56 | 218.0779 | 283.6 | 295 | 285.5 | 284.2 | 465.2 | 46.2 | 19.7 | 81.5 | 3.7 |  |  | 812.3 | 807 | 747.4 | 683.2 | 650.5 | 699.1 | 727
4201.3 | 2501.3 | 464.3 | 185.72 | 217.096 | 283.6 | 294.8 | 285.2 | 284.2 | 467 | 46.3 | 19.7 | 81.6 | 4 |  |  | 818 | 820.3 | 744.2 | 681.2 | 649.2 | 705 | 724.8
4202.3 | 2502.3 | 463.9 | 185.56 | 216.9089 | 283.2 | 294.3 | 286.2 | 283.7 | 473.1 | 46.5 | 19.7 | 81.6 | 3.8 |  |  | 821.7 | 801 | 739.6 | 681.8 | 635 | 727.1 | 735.6
4203.3 | 2503.3 | 464.6 | 185.84 | 217.2363 | 282.6 | 294.1 | 286.7 | 284.5 | 466.4 | 46.7 | 19.7 | 81.7 | 3.8 |  |  | 810.7 | 797.9 | 719.2 | 684.7 | 663.3 | 746.9 | 747.1
4204.3 | 2504.3 | 465 | 186 | 217.4233 | 282.3 | 294.4 | 286.6 | 285.2 | 471.5 | 46.5 | 19.7 | 81.8 | 4 |  |  | 814.4 | 805.4 | 718.1 | 686.7 | 682 | 749.3 | 740.9
4205.3 | 2505.3 | 464.5 | 185.8 | 217.1895 | 282 | 293.8 | 287 | 285.2 | 473 | 46.4 | 19.7 | 81.8 | 3.7 |  |  | 813.2 | 813.9 | 707.1 | 688.2 | 689.5 | 745.4 | 730
4206.3 | 2506.3 | 465.1 | 186.04 | 217.47 | 281.9 | 293.7 | 287.4 | 285.9 | 475.7 | 46.4 | 19.7 | 81.8 | 3.5 |  |  | 813.5 | 821.9 | 695.2 | 689.7 | 704.3 | 743 | 726.1
4207.3 | 2507.3 | 464.8 | 185.92 | 217.3298 | 281.9 | 294.1 | 287.6 | 286.5 | 472.1 | 46.1 | 19.7 | 81.9 | 3.6 |  |  | 808.3 | 825.2 | 696.1 | 689.1 | 696.3 | 716.8 | 716.7
4208.3 | 2508.3 | 465.1 | 186.04 | 217.47 | 282.3 | 294.1 | 287.9 | 286.9 | 467.5 | 46 | 19.7 | 81.9 | 3 |  |  | 795.7 | 836.2 | 668 | 686.4 | 692.5 | 704.3 | 708
4209.3 | 2509.3 | 464.9 | 185.96 | 217.3765 | 283.1 | 293.8 | 288.9 | 287.2 | 469.2 | 46.1 | 19.7 | 81.9 | 2.7 |  |  | 786.3 | 841.5 | 654.2 | 687.5 | 727.1 | 722.1 | 713.3
4210.3 | 2510.3 | 465.7 | 186.28 | 217.7506 | 283.4 | 294 | 289 | 287.4 | 490.1 | 46.5 | 19.7 | 81.8 | 3.3 |  |  | 795.4 | 844 | 641.6 | 691.3 | 747.5 | 740.4 | 723.4
4211.3 | 2511.3 | 465.3 | 186.12 | 217.5636 | 283.3 | 293.5 | 289.8 | 286.6 | 501.4 | 47 | 19.7 | 81.6 | 3.2 |  |  | 815.3 | 846.2 | 650.1 | 694 | 747.1 | 764.2 | 735.4
4212.3 | 2512.3 | 465.6 | 186.24 | 217.7038 | 283.2 | 293.1 | 290.8 | 287.3 | 515.2 | 47.4 | 19.7 | 81.4 | 3.1 |  |  | 831.5 | 825.9 | 670.5 | 696.8 | 728 | 788.3 | 753.8
4213.3 | 2513.3 | 465.1 | 186.04 | 217.47 | 283.9 | 293 | 291 | 288.1 | 511.4 | 47.5 | 19.7 | 81.3 | 3.4 |  |  | 835.3 | 813.1 | 674.6 | 697.7 | 714.8 | 787.1 | 757.3
4214.3 | 2514.3 | 465.5 | 186.2 | 217.6571 | 283.9 | 293.5 | 291.2 | 288.5 | 501.5 | 47.5 | 19.7 | 81.3 | 3.5 |  |  | 840.2 | 779.8 | 713.3 | 696.4 | 685.9 | 775 | 753.6
4215.3 | 2515.3 | 466.5 | 186.6 | 218.1246 | 284 | 295.5 | 291.3 | 289.3 | 492.3 | 47.4 | 19.7 | 81.3 | 3.8 |  |  | 832.4 | 753 | 747 | 694.8 | 664.8 | 760.7 | 753.5
4216.3 | 2516.3 | 465.8 | 186.32 | 217.7973 | 283.9 | 298.8 | 291.9 | 289.4 | 486.8 | 47.5 | 19.7 | 81.5 | 3.4 |  |  | 823.5 | 746.3 | 744.6 | 692.3 | 649.8 | 748.1 | 745.4
4217.3 | 2517.3 | 465.3 | 186.12 | 217.5636 | 283.5 | 300.9 | 292.3 | 289.2 | 482.8 | 47.6 | 19.7 | 81.5 | 3.6 |  |  | 821.9 | 751.2 | 729.2 | 690 | 645 | 755.8 | 744.9
4218.3 | 2518.3 | 465.6 | 186.24 | 217.7038 | 283.5 | 301 | 292.5 | 289 | 477.8 | 48 | 19.7 | 81.6 | 3.4 |  |  | 824.5 | 777.6 | 720.1 | 689.4 | 655.5 | 754.7 | 734.5
4219.3 | 2519.3 | 466.3 | 186.52 | 218.0311 | 283.8 | 300.8 | 291.7 | 287.9 | 477.5 | 48.4 | 19.7 | 81.5 | 4.2 |  |  | 822.2 | 801.7 | 731.5 | 691.1 | 664.2 | 748.5 | 725
4220.3 | 2520.3 | 466.5 | 186.6 | 218.1246 | 284.7 | 301.5 | 291.7 | 287.3 | 478.3 | 48.6 | 19.7 | 81.4 | 4 |  |  | 818.3 | 783.4 | 753.6 | 691 | 650.5 | 730 | 727.6
4221.3 | 2521.3 | 467 | 186.8 | 218.3584 | 286.1 | 302.1 | 291.9 | 286.7 | 464.2 | 48.6 | 19.7 | 81.1 | 4.3 |  |  | 819.4 | 755.5 | 767.5 | 687.5 | 632.8 | 716.9 | 732.7
4222.3 | 2522.3 | 466.4 | 186.56 | 218.0779 | 286.9 | 301.7 | 291.9 | 286.7 | 453.5 | 48.6 | 19.7 | 80.9 | 4.6 |  |  | 813.6 | 729.3 | 760.4 | 684.5 | 615.7 | 706.6 | 726.2
4223.3 | 2523.3 | 467 | 186.8 | 218.3584 | 286.9 | 300.7 | 291.5 | 286 | 444.3 | 48.7 | 19.7 | 80.8 | 4.7 |  |  | 807.8 | 727.3 | 755.9 | 682.8 | 613.4 | 720.6 | 733.2
4224.3 | 2524.3 | 466.3 | 186.52 | 218.0311 | 287.2 | 301.1 | 290.4 | 285.4 | 445.9 | 48.8 | 19.7 | 81 | 4.6 |  |  | 817.9 | 753.9 | 774.4 | 683.7 | 620.5 | 732.8 | 733.5
4225.3 | 2525.3 | 465.3 | 186.12 | 217.5636 | 288.6 | 301.8 | 290.7 | 284.8 | 456.2 | 48.6 | 19.7 | 81.1 | 4.3 |  |  | 836.4 | 762.9 | 776.7 | 686.3 | 633.8 | 762 | 752.3
4226.3 | 2526.3 | 465.3 | 186.12 | 217.5636 | 289.7 | 303.1 | 290.1 | 283.7 | 461.9 | 48.4 | 19.7 | 81.2 | 4.2 |  |  | 840.1 | 747.1 | 779.7 | 686.1 | 616.7 | 752.8 | 756.4
4227.3 | 2527.3 | 464.9 | 185.96 | 217.3765 | 289.7 | 304.6 | 289.2 | 282.6 | 460.9 | 48.8 | 19.7 | 81.2 | 4.4 |  |  | 824.2 | 727.9 | 767.2 | 685 | 593.7 | 721.5 | 737.2
4228.3 | 2528.3 | 465.7 | 186.28 | 217.7506 | 289.4 | 305.2 | 290.1 | 282.6 | 464.3 | 49.1 | 19.7 | 81.3 | 4.6 |  |  | 799.3 | 705.8 | 740.7 | 681.2 | 575.6 | 691.7 | 720.5
4229.3 | 2529.3 | 466.1 | 186.44 | 217.9376 | 289.8 | 305.6 | 291.9 | 283.2 | 452.2 | 49.1 | 19.7 | 81.3 | 4.4 |  |  | 780 | 686.1 | 737.2 | 677.4 | 555.5 | 656.8 | 707.2
4230.3 | 2530.3 | 466.3 | 186.52 | 218.0311 | 291 | 307.7 | 294.8 | 283.6 | 449.4 | 48.8 | 19.7 | 81.2 | 3.7 |  |  | 773.3 | 669.6 | 743.4 | 674.7 | 537.2 | 639.3 | 707.1
4231.3 | 2531.3 | 466.5 | 186.6 | 218.1246 | 291.4 | 309.5 | 295.5 | 282.7 | 440.4 | 48.7 | 19.7 | 81 | 3.5 |  |  | 758.7 | 643.8 | 754 | 670.4 | 520 | 623.1 | 709.6
4232.3 | 2532.3 | 465.7 | 186.28 | 217.7506 | 292.2 | 309.8 | 296 | 281.3 | 430.9 | 48.7 | 19.7 | 81 | 3.3 |  |  | 736.5 | 615 | 727.2 | 665.9 | 503.2 | 595 | 697.5
4233.3 | 2533.3 | 465.9 | 186.36 | 217.8441 | 292.9 | 309.4 | 296.4 | 281.3 | 425.1 | 48.7 | 19.7 | 80.8 | 3.5 |  |  | 736.3 | 603 | 738.6 | 661.3 | 492.3 | 596.6 | 701.5
4234.3 | 2534.3 | 465.5 | 186.2 | 217.6571 | 293.2 | 309.5 | 296.7 | 281.2 | 432.9 | 48.7 | 19.7 | 80.8 | 3.9 |  |  | 756.6 | 609.5 | 757.8 | 658.1 | 482 | 594.3 | 705
4235.3 | 2535.3 | 467.1 | 186.84 | 218.4052 | 293.2 | 310.4 | 296.7 | 280.5 | 449.5 | 48.8 | 19.7 | 81 | 4.2 |  |  | 768.3 | 615 | 758.4 | 653.9 | 478 | 598.2 | 705.5
4236.3 | 2536.3 | 466.4 | 186.56 | 218.0779 | 293.2 | 310.9 | 296.4 | 279.9 | 455.2 | 48.8 | 19.7 | 81.1 | 3.5 |  |  | 763 | 641.1 | 728 | 649.2 | 470.4 | 587.7 | 693
4237.3 | 2537.3 | 466.9 | 186.76 | 218.3117 | 292.9 | 311.9 | 295.7 | 280.3 | 462.3 | 49 | 19.7 | 81.1 | 3.5 |  |  | 759.7 | 653.2 | 713.6 | 645.3 | 461.2 | 580.7 | 684
4238.3 | 2538.3 | 466.2 | 186.48 | 217.9844 | 292.8 | 313.1 | 295.3 | 280.6 | 457 | 49.2 | 19.7 | 81.3 | 4 |  |  | 764.2 | 659.4 | 728.2 | 642 | 468.1 | 611.1 | 696.8
4239.3 | 2539.3 | 465 | 186 | 217.4233 | 292.4 | 313.8 | 295.9 | 281 | 456.5 | 49.2 | 19.7 | 81.4 | 4.6 |  |  | 771.2 | 692.5 | 714.7 | 642.9 | 505 | 651.7 | 701.9
4240.3 | 2540.3 | 466.5 | 186.6 | 218.1246 | 291.9 | 313.3 | 296.8 | 281.6 | 460.4 | 49.1 | 19.7 | 81.3 | 4.1 |  |  | 783.4 | 737.1 | 712.8 | 645.4 | 562.3 | 676.6 | 698.6
4241.3 | 2541.3 | 467.2 | 186.88 | 218.452 | 291.3 | 311.7 | 297.5 | 283.6 | 465.8 | 49.2 | 19.7 | 81.3 | 4.5 |  |  | 794.1 | 755.8 | 728.6 | 647.2 | 583.6 | 679.1 | 701.7
4242.3 | 2542.3 | 466.3 | 186.52 | 218.0311 | 290.9 | 310.4 | 297.6 | 285 | 464.8 | 49.7 | 19.7 | 81.3 | 4.1 |  |  | 781.6 | 728.9 | 729.2 | 646.6 | 571 | 657.3 | 695.6
4243.3 | 2543.3 | 466.2 | 186.48 | 217.9844 | 291.5 | 310.2 | 298.1 | 286.4 | 455.1 | 50 | 19.7 | 81.4 | 3.9 |  |  | 774.3 | 703.8 | 743.9 | 645.1 | 554.5 | 648.2 | 696.3
4244.3 | 2544.3 | 466.3 | 186.52 | 218.0311 | 292.7 | 310.1 | 298.4 | 286.5 | 451.6 | 49.9 | 19.7 | 81.4 | 4.8 |  |  | 769.3 | 690.8 | 737.7 | 644.6 | 541.7 | 655.1 | 698
4245.3 | 2545.3 | 466.6 | 186.64 | 218.1714 | 294.2 | 311 | 298.4 | 285.8 | 450.3 | 49.4 | 19.7 | 81.4 | 4.7 |  |  | 751.4 | 661.8 | 715.8 | 642.8 | 522.1 | 626.7 | 685.8
4246.3 | 2546.3 | 466.3 | 186.52 | 218.0311 | 296.3 | 311.1 | 298.5 | 284.8 | 443.2 | 49.1 | 19.7 | 81.3 | 4.6 |  |  | 746.8 | 662.2 | 695.5 | 640.5 | 519.2 | 629.7 | 680.3
4247.3 | 2547.3 | 467.1 | 186.84 | 218.4052 | 298.3 | 310 | 299 | 284.2 | 447.7 | 48.9 | 19.7 | 81.3 | 4 |  |  | 743.3 | 696.6 | 672.5 | 638.7 | 531.5 | 625.7 | 674.1
4248.3 | 2548.3 | 468 | 187.2 | 218.826 | 299.4 | 308 | 298.5 | 284 | 457.9 | 48.7 | 19.7 | 81.2 | 3.7 |  |  | 741.3 | 725.8 | 662.6 | 637 | 563.2 | 632.4 | 670.4
4249.3 | 2549.3 | 467 | 186.8 | 218.3584 | 299 | 307.4 | 297.7 | 284.9 | 458.7 | 48.8 | 19.7 | 81.1 | 4 |  |  | 744 | 755.8 | 663.2 | 635.7 | 593.8 | 636.2 | 667.8
4250.3 | 2550.3 | 466.5 | 186.6 | 218.1246 | 298.3 | 307.3 | 297.3 | 285.8 | 467.6 | 49.2 | 19.7 | 81.4 | 5.2 |  |  | 751.3 | 785.3 | 672.4 | 637.5 | 630.4 | 641.9 | 665.9
4251.3 | 2551.3 | 467.5 | 187 | 218.5922 | 297.4 | 307.4 | 296.7 | 286 | 475.7 | 49.2 | 19.7 | 81.7 | 5.4 |  |  | 756.6 | 798.9 | 673.3 | 638.4 | 641.5 | 651.5 | 669.1
4252.3 | 2552.3 | 464.2 | 185.68 | 217.0492 | 296.7 | 307.9 | 296.2 | 287 | 476.1 | 49.4 | 19.7 | 81.7 | 5 |  |  | 752.8 | 791 | 659.7 | 638.6 | 622.5 | 634.8 | 661.3
4253.3 | 2553.3 | 465.3 | 186.12 | 217.5636 | 296.7 | 308 | 296.7 | 288.7 | 470.1 | 49.5 | 19.7 | 81.6 | 4.3 |  |  | 751.7 | 777.1 | 684.3 | 636.9 | 610 | 635.8 | 664.9
4254.3 | 2554.3 | 465.6 | 186.24 | 217.7038 | 296.6 | 308 | 297.1 | 289.2 | 466.4 | 49.5 | 19.7 | 81.3 | 4 |  |  | 768.7 | 780.3 | 709.9 | 635.5 | 607.2 | 650.3 | 669.1
4255.3 | 2555.3 | 465.8 | 186.32 | 217.7973 | 296.9 | 308 | 297.7 | 288.8 | 470.1 | 49.5 | 19.7 | 81.1 | 4.3 |  |  | 771.6 | 757.1 | 738 | 635 | 588.8 | 650.8 | 675.9
4256.3 | 2556.3 | 465.8 | 186.32 | 217.7973 | 297.9 | 308.5 | 298.2 | 287.6 | 462.1 | 49.5 | 19.7 | 81.1 | 4.4 |  |  | 770.7 | 728.7 | 754.3 | 633.6 | 570 | 673.9 | 692.6
4257.3 | 2557.3 | 466.2 | 186.48 | 217.9844 | 298.2 | 309.5 | 297.7 | 286.7 | 451.7 | 49.5 | 19.7 | 81.3 | 3.7 |  |  | 755 | 704.6 | 757 | 632.6 | 568.9 | 674 | 696.3
4258.3 | 2558.3 | 466 | 186.4 | 217.8909 | 297.6 | 310.1 | 296.9 | 286.8 | 443.4 | 49.5 | 19.7 | 81.3 | 4.5 |  |  | 761.3 | 698 | 754.6 | 634.7 | 579.2 | 708.3 | 712.4
4259.3 | 2559.3 | 466.1 | 186.44 | 217.9376 | 296.9 | 309.7 | 296.8 | 287.1 | 450 | 49.5 | 19.7 | 81.1 | 5.3 |  |  | 767 | 715.9 | 740.8 | 639.4 | 614.4 | 737.3 | 725.8
4260.3 | 2560.3 | 466.3 | 186.52 | 218.0311 | 296 | 308.9 | 296.3 | 287.1 | 462.3 | 49.5 | 19.7 | 81 | 6.2 |  |  | 781.4 | 742.8 | 736.1 | 644.7 | 643.2 | 755 | 723.2
4261.3 | 2561.3 | 466.5 | 186.6 | 218.1246 | 295.2 | 308.7 | 295.9 | 287.4 | 473.8 | 49.6 | 19.7 | 81.1 | 5.9 |  |  | 802.3 | 751.2 | 761.1 | 647.3 | 640.6 | 752.1 | 718.9
4262.3 | 2562.3 | 466.3 | 186.52 | 218.0311 | 294.6 | 308.4 | 295.8 | 287.7 | 474 | 49.6 | 19.7 | 81.1 | 5.5 |  |  | 813.1 | 748 | 758.3 | 649.3 | 632.1 | 751.8 | 716.5
4263.3 | 2563.3 | 466.5 | 186.6 | 218.1246 | 293.8 | 308.4 | 296.1 | 288.2 | 471.6 | 49.5 | 19.7 | 81 | 5.2 |  |  | 804.7 | 732.5 | 743 | 649.6 | 612.1 | 720 | 703
4264.3 | 2564.3 | 466.5 | 186.6 | 218.1246 | 293.2 | 309.2 | 296.4 | 288.4 | 464.1 | 49.4 | 19.7 | 81 | 4.9 |  |  | 781.4 | 702.8 | 740.8 | 649.2 | 585.1 | 686.2 | 689.1
4265.3 | 2565.3 | 466.4 | 186.56 | 218.0779 | 292.7 | 310 | 297.7 | 287.7 | 451.7 | 49.1 | 19.7 | 81.2 | 5.6 |  |  | 762 | 666.5 | 759.3 | 647.6 | 560.8 | 667.8 | 691.3
4266.3 | 2566.3 | 466.5 | 186.6 | 218.1246 | 292.5 | 310.8 | 298.5 | 286.6 | 441.8 | 49 | 19.6 | 81.1 | 5.7 |  |  | 760.9 | 651.7 | 781.5 | 644.8 | 547.9 | 671.9 | 706.6
4267.3 | 2567.3 | 466.6 | 186.64 | 218.1714 | 292.5 | 311.9 | 299.1 | 285.4 | 442.3 | 48.7 | 19.7 | 81 | 6.1 |  |  | 775.1 | 649 | 797.9 | 642.8 | 544.6 | 687.3 | 718.5
4268.3 | 2568.3 | 466.7 | 186.68 | 218.2182 | 291.9 | 312 | 298.5 | 284.3 | 440.6 | 48.5 | 19.6 | 81 | 6 |  |  | 785.7 | 664.3 | 778.8 | 643.5 | 568.2 | 715.3 | 723.3
4269.3 | 2569.3 | 466.4 | 186.56 | 218.0779 | 292.3 | 311.4 | 297.7 | 285 | 457.3 | 48.4 | 19.6 | 80.9 | 5.9 |  |  | 794.2 | 706.7 | 754.3 | 645.5 | 581 | 728.2 | 715.3
4270.3 | 2570.3 | 466.7 | 186.68 | 218.2182 | 293.7 | 310.1 | 297.2 | 285.4 | 465.9 | 48.4 | 19.6 | 81 | 5.5 |  |  | 785.4 | 696.1 | 741.7 | 645.3 | 564.3 | 689 | 695.8
4271.3 | 2571.3 | 466.6 | 186.64 | 218.1714 | 294.2 | 311.1 | 297.9 | 286 | 460.9 | 48.6 | 19.6 | 81 | 6.3 |  |  | 770.7 | 668.9 | 746.8 | 643.5 | 541.5 | 661.5 | 686
4272.3 | 2572.3 | 466.9 | 186.76 | 218.3117 | 294.3 | 312.7 | 299.4 | 286.3 | 455.6 | 48.7 | 19.6 | 81 | 5.3 |  |  | 759.4 | 648 | 747.4 | 641.5 | 520 | 640.7 | 687
4273.3 | 2573.3 | 466.5 | 186.6 | 218.1246 | 295 | 313.5 | 300.4 | 286 | 448 | 48.8 | 19.6 | 80.8 | 6.1 |  |  | 753.1 | 629.5 | 760.9 | 638.6 | 502.9 | 630.9 | 690
4274.3 | 2574.3 | 465.3 | 186.12 | 217.5636 | 294.8 | 313.6 | 300.7 | 285.6 | 445.7 | 48.8 | 19.6 | 80.8 | 5.3 |  |  | 755.7 | 645.4 | 742.1 | 635.2 | 499.1 | 636.7 | 688.8
4275.3 | 2575.3 | 466.5 | 186.6 | 218.1246 | 294.2 | 313.2 | 300.6 | 286 | 444.1 | 48.8 | 19.6 | 80.9 | 5.4 |  |  | 755.2 | 665.7 | 736.7 | 631.4 | 500 | 624.4 | 685.6
4276.3 | 2576.3 | 466.7 | 186.68 | 218.2182 | 294.1 | 313.5 | 300.5 | 286.5 | 449.8 | 48.6 | 19.7 | 80.9 | 4.7 |  |  | 771.2 | 701.2 | 729.2 | 631.6 | 532.1 | 657.1 | 687.6
4277.3 | 2577.3 | 466.1 | 186.44 | 217.9376 | 293.8 | 313.7 | 300.2 | 286 | 453.9 | 48.4 | 19.6 | 80.8 | 6 |  |  | 779.6 | 697.5 | 731.1 | 631.6 | 534.1 | 672.3 | 703.2
4278.3 | 2578.3 | 466.8 | 186.72 | 218.2649 | 293.2 | 313.5 | 300.3 | 285.6 | 449.4 | 48.2 | 19.6 | 80.8 | 5.8 |  |  | 779.1 | 691.8 | 738.9 | 628.8 | 528.6 | 656.1 | 698.3
4279.3 | 2579.3 | 468.2 | 187.28 | 218.9195 | 292.9 | 313.1 | 301.1 | 286.1 | 451.9 | 48.1 | 19.6 | 80.9 | 5.6 |  |  | 776.3 | 694.6 | 747.6 | 627.4 | 520.8 | 647.4 | 691.1
4280.3 | 2580.3 | 468.1 | 187.24 | 218.8728 | 292.5 | 312.7 | 301.1 | 286.8 | 450.7 | 48 | 19.6 | 81 | 4.7 |  |  | 762.6 | 673.4 | 742.3 | 625.8 | 506.8 | 628.5 | 681.2
4281.3 | 2581.3 | 466.6 | 186.64 | 218.1714 | 291.8 | 312.4 | 301.5 | 287.6 | 448.8 | 47.9 | 19.6 | 80.9 | 4.5 |  |  | 754.5 | 663.2 | 743.9 | 623.3 | 496.2 | 622.6 | 679.1
4282.3 | 2582.3 | 466.8 | 186.72 | 218.2649 | 291.2 | 313.6 | 302.2 | 287.9 | 443.8 | 48 | 19.6 | 81 | 4.5 |  |  | 753.5 | 657 | 743 | 623.8 | 514.4 | 650.7 | 698.3
4283.3 | 2583.3 | 467 | 186.8 | 218.3584 | 291.3 | 313.4 | 301.7 | 287.4 | 436.8 | 48 | 19.6 | 81.1 | 5.5 |  |  | 767.1 | 667.5 | 736.5 | 626.9 | 542.8 | 696.6 | 712.1
4284.3 | 2584.3 | 466.6 | 186.64 | 218.1714 | 291.4 | 312 | 300.2 | 286.4 | 442.4 | 47.5 | 19.6 | 81.1 | 5.7 |  |  | 788.7 | 696.5 | 729.7 | 629.9 | 572.2 | 711.5 | 713.3
4285.3 | 2585.3 | 466.8 | 186.72 | 218.2649 | 292 | 311.2 | 298.5 | 285.9 | 441.6 | 47.3 | 19.6 | 81.2 | 6 |  |  | 775.6 | 693 | 716.1 | 630.2 | 567.7 | 681 | 693.7
4286.3 | 2586.3 | 466.6 | 186.64 | 218.1714 | 293.3 | 311.2 | 298.2 | 286.3 | 438.8 | 47.4 | 19.6 | 81.1 | 6.3 |  |  | 756 | 675.2 | 711 | 629.4 | 554.5 | 653.5 | 680.1
4287.3 | 2587.3 | 466.7 | 186.68 | 218.2182 | 294.4 | 310.9 | 298.3 | 286.4 | 439.9 | 47.6 | 19.6 | 81.1 | 6.2 |  |  | 749.6 | 675.1 | 714.1 | 627.7 | 549.2 | 631 | 676.2
4288.3 | 2588.3 | 466.8 | 186.72 | 218.2649 | 294.9 | 310.8 | 299 | 285.9 | 448.7 | 47.9 | 19.6 | 81.1 | 5.8 |  |  | 740.1 | 665.2 | 701.4 | 626.4 | 534.9 | 607 | 668.4
4289.3 | 2589.3 | 469.1 | 187.64 | 219.3403 | 294.5 | 310.5 | 300.1 | 285.7 | 448.4 | 48.1 | 19.6 | 81.1 | 5.5 |  |  | 754.7 | 692.2 | 721.1 | 624.4 | 538.2 | 622.5 | 673
4290.3 | 2590.3 | 468.9 | 187.56 | 219.2468 | 294.5 | 309.8 | 300.4 | 285.4 | 459.1 | 47.9 | 19.6 | 81.2 | 5.9 |  |  | 778.4 | 723.7 | 721.6 | 625.3 | 565 | 658.8 | 685.6
4291.3 | 2591.3 | 468.8 | 187.52 | 219.2001 | 294 | 309.6 | 300.4 | 285.3 | 479.2 | 48 | 19.6 | 81.2 | 5.9 |  |  | 799.4 | 736.5 | 741.1 | 627.5 | 572.3 | 681.2 | 697.6
4292.3 | 2592.3 | 468.7 | 187.48 | 219.1533 | 293.2 | 309.9 | 301 | 285.7 | 491.4 | 47.8 | 19.6 | 81.2 | 6 |  |  | 806.1 | 746.1 | 741.8 | 627.9 | 570.9 | 669.2 | 694.7
4293.3 | 2593.3 | 468.2 | 187.28 | 218.9195 | 293.6 | 310.9 | 300.6 | 287.2 | 491.3 | 47.8 | 19.6 | 81.3 | 5.5 |  |  | 802.8 | 742.3 | 739.6 | 627.5 | 565.8 | 659.5 | 687.2
4294.3 | 2594.3 | 468.4 | 187.36 | 219.013 | 295.1 | 311.1 | 300.4 | 287.9 | 484.5 | 48 | 19.6 | 81.3 | 5.5 |  |  | 809.5 | 746.3 | 736.6 | 626.4 | 569.2 | 664.4 | 682.9
4295.3 | 2595.3 | 468 | 187.2 | 218.826 | 295.5 | 311.3 | 300.4 | 288.1 | 486.6 | 48.2 | 19.6 | 81.2 | 5.1 |  |  | 804.7 | 722 | 757.1 | 625.7 | 551.2 | 647.3 | 681.9
4296.3 | 2596.3 | 468.3 | 187.32 | 218.9663 | 295.1 | 312.2 | 300 | 288.1 | 483.3 | 48.2 | 19.6 | 81.1 | 4 |  |  | 794.9 | 691.5 | 749.3 | 624.3 | 536.6 | 639.4 | 678.4
4297.3 | 2597.3 | 468 | 187.2 | 218.826 | 295 | 313.1 | 300.6 | 287.7 | 478.2 | 47.9 | 19.6 | 81 | 3.8 |  |  | 796 | 684.3 | 747.8 | 622.7 | 527.4 | 643.3 | 680.1
4298.3 | 2598.3 | 467.7 | 187.08 | 218.6857 | 295.5 | 314 | 301.6 | 287.7 | 470.6 | 47.8 | 19.6 | 81 | 4.2 |  |  | 777.4 | 660.8 | 737 | 621 | 511.6 | 617.8 | 675.1
4299.3 | 2599.3 | 467.9 | 187.16 | 218.7793 | 295.8 | 314.5 | 302.7 | 288.1 | 463.7 | 48 | 19.6 | 81.1 | 4.6 |  |  | 760.7 | 634.5 | 728.5 | 619.3 | 494.9 | 595.5 | 664.2
4300.3 | 2600.3 | 467.7 | 187.08 | 218.6857 | 296.9 | 314.9 | 303.6 | 287.9 | 457.1 | 48.4 | 19.6 | 81 | 4.4 |  |  | 751.7 | 634.9 | 716.6 | 616.5 | 484.7 | 583.7 | 660.8
4301.3 | 2601.3 | 467.4 | 186.96 | 218.5455 | 297.3 | 314.5 | 303.8 | 287 | 449.7 | 48.6 | 19.6 | 81 | 4.8 |  |  | 741 | 625.6 | 702.2 | 614.4 | 471.7 | 579.7 | 657.8
4302.3 | 2602.3 | 466.9 | 186.76 | 218.3117 | 297.9 | 314.2 | 304.3 | 286.9 | 440.5 | 48.3 | 19.6 | 81.2 | 5 |  |  | 730.6 | 621.7 | 676.1 | 612.3 | 470.1 | 565.3 | 652.1
4303.3 | 2603.3 | 466.3 | 186.52 | 218.0311 | 299.1 | 313.8 | 305.5 | 286.1 | 443.1 | 48.3 | 19.6 | 81.3 | 5.4 |  |  | 741.6 | 669.8 | 665.4 | 610.7 | 497.4 | 590.7 | 652.9
4304.3 | 2604.3 | 391.2 | 156.48 | 182.9161 | 300 | 314.5 | 305.5 | 285.5 | 444.1 | 48.3 | 19.6 | 81.3 | 4.8 |  |  | 761.2 | 709.2 | 668.3 | 612.3 | 528.5 | 639.8 | 667.2
4305.3 | 2605.3 | 32.7 | 13.08 | 15.2898 | 299.4 | 314.5 | 305.4 | 285 | 456.3 | 48.4 | 19.6 | 81.5 | 4.6 |  |  | 789.5 | 744 | 693.5 | 614.1 | 552.5 | 658.6 | 675.5
4306.3 | 2606.3 | -6.8 | 0 | 0 | 298 | 314 | 304.3 | 285.9 | 459.5 | 48.6 | 19.6 | 81.6 | 3.4 |  |  | 769.3 | 704.4 | 653.2 | 611.1 | 530 | 620 | 658.3
4307.3 | 2607.3 | -6.8 | 0 | 0 | 295.9 | 312.1 | 302.2 | 287.5 | 438.9 | 48.8 | 19.6 | 81.7 | 2.7 |  |  | 729.6 | 650.9 | 608.8 | 607.3 | 506.8 | 575.2 | 637.6
4308.3 | 2608.3 | -6.8 | 0 | 0 | 293.5 | 309.2 | 299.5 | 287 | 419.6 | 48.6 | 19.6 | 81.7 | 3.3 |  |  | 696.5 | 607.2 | 573.2 | 604.7 | 486.8 | 539.4 | 626
4309.3 | 2609.3 | -6.8 | 0 | 0 | 290.6 | 305.2 | 296.4 | 284.8 | 405.6 | 48.5 | 19.6 | 81.8 | 3.5 |  |  | 667.3 | 566 | 542.8 | 601.1 | 464.6 | 505.3 | 616.6
4310.3 | 2610.3 | -6.8 | 0 | 0 | 287.6 | 301.2 | 292.9 | 281.8 | 393.9 | 48.2 | 19.6 | 81.6 | 3.4 |  |  | 638 | 529.3 | 512.5 | 596.6 | 445.5 | 476.9 | 607.8
4311.3 | 2611.3 | -6.8 | 0 | 0 | 284.8 | 297.3 | 288.8 | 278.9 | 384.1 | 48.3 | 19.6 | 81.4 | 3.9 |  |  | 612.3 | 500.8 | 487 | 591.6 | 428.4 | 452 | 600.9
4312.3 | 2612.3 | -6.8 | 0 | 0 | 282.2 | 293.4 | 284.8 | 275.7 | 374.5 | 48.5 | 19.6 | 81.2 | 3.5 |  |  | 587.6 | 474.3 | 464.1 | 584.5 | 411.4 | 428.5 | 592.7
4313.3 | 2613.3 | -6.8 | 0 | 0 | 279.2 | 289.5 | 280.8 | 272.7 | 365.8 | 48.5 | 19.6 | 80.7 | 3.9 |  |  | 566 | 450.5 | 443.2 | 577.7 | 396.6 | 408 | 586.4
4314.3 | 2614.3 | -6.8 | 0 | 0 | 276.5 | 285.7 | 276.9 | 269.1 | 358 | 48.3 | 19.6 | 80.2 | 4 |  |  | 545.3 | 428.1 | 423.4 | 572.1 | 382.7 | 389.6 | 579.8
4315.3 | 2615.3 | -6.8 | 0 | 0 | 273.7 | 281.5 | 273.3 | 265.5 | 350.8 | 47.9 | 19.6 | 79.6 | 5 |  |  | 531.4 | 411.2 | 406.4 | 567.1 | 369.5 | 374.8 | 576.9
4316.3 | 2616.3 | -6.8 | 0 | 0 | 270.7 | 277.2 | 269.8 | 262.3 | 344.4 | 47.7 | 19.6 | 78.9 | 4.3 |  |  | 522.3 | 395 | 392.9 | 561.9 | 357.6 | 360.2 | 575.5
4317.3 | 2617.3 | -6.8 | 0 | 0 | 267 | 272.9 | 266.4 | 259.2 | 338.3 | 47.5 | 19.6 | 78.4 | 4.6 |  |  | 513.1 | 380.6 | 380.3 | 556.6 | 346.4 | 346.9 | 572.3
4318.3 | 2618.3 | -6.8 | 0 | 0 | 262.5 | 268.8 | 263.2 | 256 | 332 | 47.3 | 19.6 | 77.9 | 3.8 |  |  | 505.1 | 367.1 | 369.9 | 551.3 | 336.5 | 335.2 | 568.4
4319.3 | 2619.3 | -6.8 | 0 | 0 | 258.9 | 264.9 | 260.3 | 253 | 326.1 | 47 | 19.6 | 77.6 | 4.1 |  |  | 497.2 | 354.9 | 360.5 | 546 | 326.7 | 324.3 | 564.2
4320.3 | 2620.3 | -6.8 | 0 | 0 | 255.6 | 261.2 | 257.1 | 250.3 | 320.7 | 47 | 19.6 | 77.3 | 4.1 |  |  | 489 | 344.3 | 351.5 | 540.8 | 317.8 | 313.9 | 560.7
4321.3 | 2621.3 | -6.8 | 0 | 0 | 252.2 | 257.8 | 253.8 | 247.6 | 315.5 | 47.1 | 19.6 | 76.9 | 3.7 |  |  | 482.3 | 334.3 | 343.4 | 535.6 | 308.5 | 303.7 | 556.3
4322.3 | 2622.3 | -6.8 | 0 | 0 | 249.3 | 254.4 | 250.5 | 244.8 | 310.6 | 47.2 | 19.6 | 76.5 | 4.2 |  |  | 476.6 | 324.8 | 336.3 | 530.5 | 299.7 | 293.9 | 550
4323.3 | 2623.3 | -6.7 | 0 | 0 | 246.6 | 250.8 | 247.5 | 242.2 | 306 | 47.3 | 19.6 | 76.1 | 4.1 |  |  | 467.9 | 314 | 328.6 | 525.5 | 292.4 | 285.2 | 543.6
4324.3 | 2624.3 | -6.7 | 0 | 0 | 243.6 | 247.4 | 244.8 | 239.6 | 301.2 | 47.3 | 19.6 | 75.7 | 3.9 |  |  | 459.1 | 304.6 | 320.5 | 520.5 | 285 | 277 | 538.4
4325.3 | 2625.3 | -6.7 | 0 | 0 | 240.3 | 244.2 | 241.9 | 237.2 | 296.8 | 47.2 | 19.6 | 75.3 | 3.9 |  |  | 450.9 | 296 | 313.2 | 515.7 | 279.1 | 269.7 | 534.9
4326.3 | 2626.3 | -6.7 | 0 | 0 | 237.4 | 241.3 | 238.4 | 235 | 292.8 | 47.1 | 19.6 | 75 | 3.7 |  |  | 445.3 | 288.6 | 307.1 | 510.9 | 273.3 | 262.1 | 531.1
4327.3 | 2627.3 | -6.7 | 0 | 0 | 235 | 238.5 | 235.2 | 232.7 | 289.4 | 46.9 | 19.6 | 74.5 | 4 |  |  | 438.6 | 281.3 | 300.7 | 506.3 | 267.5 | 255.1 | 526.6
4328.3 | 2628.3 | -6.7 | 0 | 0 | 232.8 | 235.8 | 232.3 | 230.3 | 286 | 46.5 | 19.6 | 74.2 | 3.6 |  |  | 430.4 | 272.8 | 293.8 | 501.8 | 264 | 247.8 | 522.8
4329.3 | 2629.3 | -6.7 | 0 | 0 | 230.4 | 233.1 | 229.7 | 227.7 | 282.5 | 46.1 | 19.6 | 74 | 3.8 |  |  | 422 | 265.2 | 286.6 | 497.4 | 260.7 | 240.8 | 519.2
4330.3 | 2630.3 | -6.7 | 0 | 0 | 228.1 | 230.4 | 227.2 | 225.2 | 278.9 | 46.1 | 19.6 | 73.7 | 3.9 |  |  | 413.8 | 258.7 | 279.8 | 493.1 | 257.5 | 234.3 | 515.3
4331.3 | 2631.3 | -6.7 | 0 | 0 | 226 | 228.1 | 224.8 | 222.9 | 275.3 | 46.2 | 19.6 | 73.3 | 3.5 |  |  | 407.6 | 252.4 | 273.6 | 488.8 | 254.3 | 228.4 | 511.2
4332.3 | 2632.3 | -6.7 | 0 | 0 | 223.9 | 225.7 | 222.3 | 220.8 | 271.8 | 46.4 | 19.6 | 72.9 | 3.9 |  |  | 400.4 | 245.9 | 267.4 | 484.6 | 251 | 223.1 | 506
4333.3 | 2633.3 | -6.7 | 0 | 0 | 222.1 | 223.1 | 219.9 | 218.4 | 268.6 | 46.4 | 19.6 | 72.5 | 4.3 |  |  | 394.4 | 240.4 | 262 | 480.5 | 247.5 | 218.5 | 499.6
4334.3 | 2634.3 | -6.7 | 0 | 0 | 220.5 | 220.8 | 217.7 | 215.9 | 265.5 | 46.1 | 19.6 | 72.3 | 4.2 |  |  | 388.5 | 234.9 | 256.6 | 476.4 | 244 | 213.7 | 495.4
4335.3 | 2635.3 | -6.7 | 0 | 0 | 218.8 | 218.6 | 215.6 | 213.7 | 262.7 | 46.1 | 19.6 | 72 | 3.9 |  |  | 382.7 | 230.5 | 251.9 | 472.5 | 240.2 | 209.3 | 491.5
4336.3 | 2636.3 | -6.7 | 0 | 0 | 216.9 | 216.2 | 213.4 | 211.5 | 260.2 | 45.9 | 19.6 | 71.7 | 3.4 |  |  | 378.4 | 226.5 | 248 | 468.5 | 236.5 | 205.5 | 488
4337.3 | 2637.3 | -6.7 | 0 | 0 | 215 | 214.2 | 211.3 | 209.1 | 257.9 | 45.9 | 19.6 | 71.4 | 3.1 |  |  | 374.5 | 222.2 | 244 | 464.7 | 233.2 | 201.3 | 484.6
4338.3 | 2638.3 | -6.7 | 0 | 0 | 213.3 | 212.2 | 209.2 | 206.8 | 255.7 | 45.6 | 19.6 | 71.2 | 2.9 |  |  | 368.9 | 217.8 | 239.4 | 461 | 230.5 | 196.7 | 480.2
4339.3 | 2639.3 | -6.7 | 0 | 0 | 211.7 | 210.4 | 207.1 | 204.7 | 253.3 | 45.4 | 19.6 | 71.1 | 2.9 |  |  | 364.3 | 214.3 | 235.5 | 457.3 | 227.9 | 192.5 | 476.2
4340.3 | 2640.3 | -6.7 | 0 | 0 | 210.2 | 208.7 | 204.9 | 202.6 | 251 | 45.3 | 19.6 | 70.7 | 3.2 |  |  | 360.7 | 210.7 | 231.6 | 453.7 | 225.8 | 189 | 472.4
4341.3 | 2641.3 | -6.7 | 0 | 0 | 208.8 | 207.1 | 203.1 | 200.7 | 248.7 | 45.2 | 19.6 | 70.3 | 3.5 |  |  | 357.4 | 207.5 | 228.1 | 450.2 | 222.8 | 185.5 | 468.5
4342.3 | 2642.3 | -6.7 | 0 | 0 | 207.4 | 205.2 | 201.5 | 198.8 | 246.6 | 44.9 | 19.6 | 70 | 3.8 |  |  | 354 | 204.3 | 224.9 | 446.7 | 219.7 | 182.1 | 465.1
4343.3 | 2643.3 | -6.7 | 0 | 0 | 206 | 203.3 | 199.9 | 196.6 | 244.6 | 44.7 | 19.6 | 69.7 | 3.5 |  |  | 349.8 | 200.8 | 221.1 | 443.3 | 218 | 179.2 | 461.9
4344.3 | 2644.3 | -6.7 | 0 | 0 | 204.5 | 201.4 | 198.4 | 194.8 | 242.7 | 44.6 | 19.6 | 69.5 | 3.4 |  |  | 347 | 198.1 | 217.5 | 440 | 215.1 | 176.4 | 456.9
4345.3 | 2645.3 | -6.7 | 0 | 0 | 202.9 | 199.6 | 197 | 193 | 240.9 | 44.4 | 19.6 | 69.2 | 3.5 |  |  | 346 | 196 | 215.2 | 436.7 | 211.7 | 173.6 | 452.9
4346.3 | 2646.3 | -6.7 | 0 | 0 | 201.1 | 198 | 195.4 | 191.3 | 239.3 | 44.2 | 19.6 | 68.9 | 3.4 |  |  | 344.8 | 193.8 | 212.5 | 433.5 | 208 | 170.8 | 448.9
4347.3 | 2647.3 | -6.7 | 0 | 0 | 199.2 | 196.6 | 193.8 | 189.6 | 237.8 | 44.2 | 19.6 | 68.5 | 3.7 |  |  | 342.7 | 191.5 | 209.9 | 430.3 | 204.4 | 168.6 | 444.9
4348.3 | 2648.3 | -6.7 | 0 | 0 | 197.5 | 195.2 | 192.5 | 188.1 | 236.3 | 44 | 19.6 | 68.1 | 3.6 |  |  | 340.4 | 189.4 | 208.5 | 427.2 | 201.2 | 166.3 | 443.1
4349.3 | 2649.3 | -6.7 | 0 | 0 | 196.2 | 193.8 | 191.5 | 186.7 | 234.9 | 43.8 | 19.6 | 67.8 | 3.4 |  |  | 338.2 | 187.6 | 205.8 | 424.1 | 197.9 | 164 | 440.9
4350.3 | 2650.3 | -6.7 | 0 | 0 | 195.1 | 192.3 | 190.3 | 185.5 | 233.5 | 44 | 19.6 | 67.4 | 4 |  |  | 336.9 | 186.2 | 203.3 | 421.1 | 194.5 | 161.7 | 438.1
4351.3 | 2651.3 | -6.7 | 0 | 0 | 193.8 | 190.9 | 188.7 | 184.3 | 232.1 | 44.1 | 19.6 | 67.1 | 4.3 |  |  | 335.4 | 185.2 | 201 | 418.1 | 191.4 | 159.4 | 435.4
4352.3 | 2652.3 | -6.7 | 0 | 0 | 192.3 | 189.6 | 187.2 | 183 | 230.8 | 43.9 | 19.6 | 66.7 | 4.1 |  |  | 334.8 | 184.4 | 198.4 | 415.2 | 188.2 | 157 | 432.2
4353.3 | 2653.3 | -6.7 | 0 | 0 | 190.8 | 188.4 | 185.9 | 181.9 | 229.5 | 43.6 | 19.6 | 66.6 | 3.5 |  |  | 334.1 | 183.3 | 196 | 412.4 | 185.2 | 154.5 | 428.8
4354.3 | 2654.3 | -6.7 | 0 | 0 | 189.6 | 187.3 | 184.6 | 180.7 | 228.2 | 43.3 | 19.6 | 66.4 | 3.5 |  |  | 333.6 | 181.3 | 193.7 | 409.7 | 182.2 | 152.1 | 425.2
4355.3 | 2655.3 | -6.7 | 0 | 0 | 188.4 | 186.2 | 183.2 | 179.5 | 227.1 | 43.1 | 19.6 | 66.1 | 3.8 |  |  | 332.2 | 178.9 | 191.3 | 407 | 179.6 | 149.9 | 422.1
4356.3 | 2656.3 | -6.7 | 0 | 0 | 187.4 | 184.8 | 181.9 | 178.5 | 226 | 43.3 | 19.6 | 65.7 | 3.7 |  |  | 330.1 | 176.9 | 189.1 | 404.3 | 178.2 | 147.6 | 419.2
4357.3 | 2657.3 | -6.7 | 0 | 0 | 186.6 | 183.4 | 180.6 | 177.5 | 225.1 | 43.4 | 19.6 | 65.3 | 3.5 |  |  | 328.4 | 176.8 | 187 | 401.7 | 175.9 | 145.2 | 416.1
4358.3 | 2658.3 | -6.7 | 0 | 0 | 185.5 | 182.1 | 179.2 | 176.4 | 224.1 | 43.4 | 19.6 | 64.9 | 3.8 |  |  | 326.1 | 174.9 | 184.3 | 399.1 | 173.3 | 143 | 413.5
4359.3 | 2659.3 | -6.7 | 0 | 0 | 184 | 181 | 177.8 | 175.5 | 223.1 | 43.2 | 19.6 | 64.7 | 4 |  |  | 321.8 | 172.6 | 181.4 | 396.6 | 171.2 | 141.1 | 410.9
4360.3 | 2660.3 | -6.7 | 0 | 0 | 182.5 | 179.8 | 176.5 | 174.6 | 221.9 | 43.4 | 19.6 | 64.3 | 4.2 |  |  | 320.8 | 171 | 179.2 | 394.1 | 169.5 | 139.3 | 407.7
4361.3 | 2661.3 | -6.7 | 0 | 0 | 181.6 | 179.1 | 175.2 | 173.5 | 220.8 | 43.5 | 19.6 | 64.1 | 3.6 |  |  | 319.2 | 168.8 | 177.1 | 391.6 | 167.9 | 137.8 | 404.8
4362.3 | 2662.3 | -6.7 | 0 | 0 | 180.3 | 178.2 | 173.9 | 172.3 | 219.7 | 43.4 | 19.6 | 63.9 | 3.5 |  |  | 317 | 166.7 | 175.2 | 389.2 | 166 | 135.8 | 402.8
4363.3 | 2663.3 | -6.7 | 0 | 0 | 178.9 | 177.1 | 173 | 171.2 | 218.6 | 43.2 | 19.6 | 63.7 | 3.5 |  |  | 313.9 | 164.6 | 173.1 | 386.8 | 164.3 | 134.2 | 400.9
4364.3 | 2664.3 | -6.7 | 0 | 0 | 177.5 | 176 | 171.9 | 170.2 | 217.6 | 43.1 | 19.6 | 63.4 | 3.8 |  |  | 313 | 164.1 | 171.6 | 384.4 | 163 | 132.4 | 398.6
4365.3 | 2665.3 | -6.7 | 0 | 0 | 176.3 | 175.2 | 170.8 | 169.1 | 216.6 | 42.9 | 19.6 | 63.2 | 3.3 |  |  | 313.7 | 165 | 169.9 | 382.1 | 162.4 | 130.5 | 395.8
4366.3 | 2666.3 | -6.7 | 0 | 0 | 175.3 | 174.5 | 169.7 | 168 | 215.6 | 42.5 | 19.6 | 63.1 | 3.7 |  |  | 313.6 | 164.5 | 167.7 | 379.8 | 161.4 | 128.7 | 393
4367.3 | 2667.3 | -6.7 | 0 | 0 | 174.1 | 173.6 | 168.8 | 167.1 | 214.6 | 42.3 | 19.7 | 63 | 3.5 |  |  | 312.8 | 163.6 | 165.5 | 377.5 | 160.3 | 126.9 | 390
4368.3 | 2668.3 | -6.7 | 0 | 0 | 173 | 172.6 | 167.8 | 166.4 | 213.7 | 42.3 | 19.7 | 62.9 | 3.2 |  |  | 312 | 163.2 | 163.6 | 375.2 | 158.9 | 125.2 | 387
4369.3 | 2669.3 | -6.7 | 0 | 0 | 171.9 | 171.6 | 166.9 | 165.4 | 212.9 | 42.7 | 19.7 | 62.7 | 3.2 |  |  | 311.4 | 161.7 | 162.1 | 373 | 157.5 | 123.7 | 383.7
4370.3 | 2670.3 | -6.7 | 0 | 0 | 171.1 | 170.8 | 166.3 | 164.3 | 212 | 42.9 | 19.7 | 62.6 | 3.8 |  |  | 311 | 161.2 | 160.6 | 370.8 | 156.9 | 122 | 381.4
4371.3 | 2671.3 | -6.7 | 0 | 0 | 170.6 | 170 | 165.4 | 163.4 | 211.2 | 42.8 | 19.7 | 62.4 | 4.1 |  |  | 310.9 | 161.3 | 159 | 368.6 | 155.6 | 120.4 | 379.2
4372.3 | 2672.3 | -6.7 | 0 | 0 | 170.1 | 169.3 | 164.5 | 162.7 | 210.3 | 42.5 | 19.7 | 62.3 | 4.8 |  |  | 310.7 | 160.3 | 157.5 | 366.5 | 154.7 | 118.9 | 377.2
4373.3 | 2673.3 | -6.7 | 0 | 0 | 169.5 | 168.7 | 163.6 | 161.9 | 209.4 | 42.6 | 19.7 | 62.1 | 4.6 |  |  | 310.7 | 159.6 | 155.9 | 364.4 | 153.8 | 117.1 | 375.4
4374.3 | 2674.3 | -6.7 | 0 | 0 | 168.9 | 168 | 162.7 | 161.2 | 208.6 | 42.5 | 19.7 | 62 | 4 |  |  | 308.7 | 158 | 153.9 | 362.3 | 152 | 115.4 | 372.6
4375.3 | 2675.3 | -6.7 | 0 | 0 | 167.8 | 167.3 | 162 | 160.6 | 207.8 | 42.2 | 19.7 | 61.7 | 3.3 |  |  | 304.2 | 155.9 | 151.3 | 360.2 | 150.2 | 114.2 | 371
4376.3 | 2676.3 | -6.7 | 0 | 0 | 166.8 | 166.5 | 161.4 | 160 | 207.1 | 42 | 19.7 | 61.6 | 3.2 |  |  | 301.3 | 154.5 | 149.4 | 358.1 | 148.1 | 112.9 | 369.2
4377.3 | 2677.3 | -6.7 | 0 | 0 | 166.1 | 165.7 | 160.6 | 159.4 | 206.3 | 41.8 | 19.7 | 61.5 | 3.7 |  |  | 298.9 | 153.6 | 147.8 | 356.1 | 146.2 | 111.4 | 366.7
4378.3 | 2678.3 | -6.7 | 0 | 0 | 165.2 | 165.1 | 159.9 | 158.7 | 205.5 | 41.8 | 19.7 | 61.4 | 3.5 |  |  | 293.8 | 151.1 | 145.7 | 354.1 | 144.5 | 110.2 | 364.7
4379.3 | 2679.3 | -6.7 | 0 | 0 | 164.2 | 164.5 | 159.1 | 158 | 204.7 | 41.9 | 19.7 | 61.3 | 4.1 |  |  | 291.4 | 149.1 | 144.2 | 352.1 | 143.3 | 109.2 | 363.1
4380.3 | 2680.3 | -6.7 | 0 | 0 | 163.5 | 163.8 | 158.3 | 157.3 | 204 | 41.7 | 19.7 | 61.2 | 3.6 |  |  | 290.6 | 147.7 | 143.2 | 350.1 | 142.5 | 108.2 | 361.2
4381.3 | 2681.3 | -6.7 | 0 | 0 | 162.6 | 163.2 | 157.8 | 156.7 | 203.3 | 41.7 | 19.7 | 61.1 | 3.4 |  |  | 288 | 145.7 | 142 | 348.2 | 141 | 107 | 359.3
4382.3 | 2682.3 | -6.7 | 0 | 0 | 162.5 | 162.5 | 157.1 | 155.9 | 202.7 | 41.9 | 19.7 | 61 | 3.7 |  |  | 287.1 | 144.9 | 140.7 | 346.3 | 140.3 | 105.9 | 357.1
4383.3 | 2683.3 | -6.7 | 0 | 0 | 162.2 | 161.9 | 156.7 | 155.3 | 202.2 | 42 | 19.7 | 60.8 | 3.9 |  |  | 286.4 | 144.2 | 139.5 | 344.4 | 139.1 | 104.9 | 355
4384.3 | 2684.3 | -6.7 | 0 | 0 | 161.8 | 161.3 | 156.2 | 154.7 | 201.5 | 41.9 | 19.7 | 60.7 | 3.5 |  |  | 285.1 | 144.3 | 138.2 | 342.5 | 138 | 103.9 | 353.3
4385.3 | 2685.3 | -6.7 | 0 | 0 | 161.2 | 160.6 | 155.7 | 154.1 | 200.9 | 41.9 | 19.7 | 60.5 | 3.2 |  |  | 283.5 | 144.6 | 137 | 340.7 | 137.1 | 102.6 | 351.5
4386.3 | 2686.3 | -6.7 | 0 | 0 | 160.4 | 160 | 155.1 | 153.5 | 200.2 | 41.9 | 19.7 | 60.3 | 3.6 |  |  | 281.1 | 143.4 | 135.3 | 338.9 | 136 | 101.4 | 349.1
4387.3 | 2687.3 | -6.7 | 0 | 0 | 159.6 | 159.5 | 154.5 | 152.9 | 199.5 | 41.7 | 19.7 | 60 | 3.2 |  |  | 276.7 | 141.5 | 133.6 | 337.1 | 135.2 | 100.4 | 346.2
4388.3 | 2688.3 | -6.7 | 0 | 0 | 159 | 159 | 154 | 152.5 | 198.9 | 41.5 | 19.7 | 59.7 | 3.7 |  |  | 271.8 | 139.6 | 131.9 | 335.3 | 134.1 | 99.5 | 344.4
4389.3 | 2689.3 | -6.7 | 0 | 0 | 158.2 | 158.4 | 153.5 | 152 | 198.2 | 41.3 | 19.7 | 59.6 | 3.5 |  |  | 268.5 | 139.5 | 130.2 | 333.6 | 133.1 | 98.6 | 343.5
4390.3 | 2690.3 | -6.7 | 0 | 0 | 157.8 | 157.9 | 152.8 | 151.4 | 197.6 | 41.2 | 19.7 | 59.5 | 3.3 |  |  | 264.1 | 137.2 | 128.4 | 331.9 | 132.6 | 97.6 | 341.7
4391.3 | 2691.3 | -6.7 | 0 | 0 | 157.5 | 157.4 | 152.1 | 150.8 | 197 | 41.3 | 19.7 | 59.4 | 3.5 |  |  | 258.6 | 135 | 126.5 | 330.1 | 131.5 | 96.4 | 340.5
4392.3 | 2692.3 | -6.7 | 0 | 0 | 157.2 | 156.8 | 151.5 | 150.3 | 196.5 | 41.4 | 19.7 | 59.2 | 3.7 |  |  | 253.6 | 133.4 | 124.8 | 328.4 | 130.2 | 95.7 | 338.6
4393.3 | 2693.3 | -6.7 | 0 | 0 | 156.8 | 156.2 | 151 | 149.8 | 195.9 | 41.4 | 19.7 | 59.1 | 3.3 |  |  | 249.9 | 131.8 | 123.5 | 326.7 | 129 | 95.1 | 337.1
4394.3 | 2694.3 | -6.7 | 0 | 0 | 156.2 | 155.7 | 150.5 | 149.5 | 195.3 | 41.3 | 19.7 | 59.1 | 3.1 |  |  | 247.9 | 131.3 | 122.4 | 325 | 127.9 | 94.7 | 336
4395.3 | 2695.3 | -6.7 | 0 | 0 | 155.5 | 155.3 | 150 | 149.1 | 194.7 | 41.2 | 19.7 | 59.2 | 3.5 |  |  | 247.2 | 131.6 | 121.7 | 323.3 | 126.6 | 94 | 333.9
4396.3 | 2696.3 | -6.7 | 0 | 0 | 154.8 | 155 | 149.4 | 148.4 | 194 | 41.4 | 19.7 | 59.1 | 3.2 |  |  | 245.3 | 130 | 120.5 | 321.6 | 125.1 | 93.2 | 331.9
4397.3 | 2697.3 | -6.7 | 0 | 0 | 154.2 | 154.5 | 149 | 147.8 | 193.2 | 41.4 | 19.7 | 59 | 2.7 |  |  | 243.7 | 128.6 | 119.3 | 320 | 123.8 | 92.7 | 330.5
4398.3 | 2698.3 | -6.7 | 0 | 0 | 154.1 | 154 | 148.7 | 147.2 | 192.4 | 41.5 | 19.7 | 58.9 | 2.5 |  |  | 242.8 | 127.5 | 118.5 | 318.4 | 122.7 | 92.1 | 328.5
4399.3 | 2699.3 | -6.7 | 0 | 0 | 154 | 153.5 | 148.2 | 146.8 | 191.7 | 41.5 | 19.7 | 58.8 | 2.5 |  |  | 242.4 | 126.5 | 117.7 | 316.8 | 121.8 | 91.5 | 326.5
4400.3 | 2700.3 | -6.7 | 0 | 0 | 153.7 | 153.1 | 147.6 | 146.3 | 191.1 | 41.4 | 19.7 | 58.6 | 2.7 |  |  | 241.4 | 126.1 | 116.8 | 315.2 | 121.1 | 90.9 | 324.8
4401.3 | 2701.3 | -6.7 | 0 | 0 | 153.2 | 152.6 | 147 | 145.9 | 190.5 | 41.4 | 19.7 | 58.4 | 3 |  |  | 240.4 | 125.3 | 116 | 313.6 | 120 | 90.4 | 323.4
4402.3 | 2702.3 | -6.7 | 0 | 0 | 152.7 | 152.1 | 146.6 | 145.5 | 189.9 | 41.4 | 19.7 | 58.2 | 3.2 |  |  | 239.5 | 124.2 | 115.2 | 312.1 | 119.1 | 89.9 | 321.9
4403.3 | 2703.3 | -6.7 | 0 | 0 | 152.2 | 151.6 | 146.2 | 145 | 189.2 | 41.4 | 19.8 | 58.1 | 3.3 |  |  | 238.2 | 123 | 114.1 | 310.5 | 118.2 | 89.2 | 320.2
4404.3 | 2704.3 | -6.7 | 0 | 0 | 151.6 | 151.2 | 145.9 | 144.5 | 188.5 | 41.6 | 19.8 | 58 | 3.1 |  |  | 236.4 | 122 | 113 | 309 | 118.2 | 88.7 | 318
4405.3 | 2705.3 | -6.7 | 0 | 0 | 151.3 | 150.8 | 145.4 | 144.1 | 188 | 41.7 | 19.8 | 57.9 | 3.1 |  |  | 234 | 120.9 | 111.9 | 307.5 | 117.4 | 88.1 | 316.1
4406.3 | 2706.3 | -6.7 | 0 | 0 | 150.9 | 150.5 | 145.1 | 143.8 | 187.4 | 41.8 | 19.8 | 57.9 | 2.8 |  |  | 231.5 | 120.3 | 110.8 | 306 | 116.8 | 87.7 | 315
4407.3 | 2707.3 | -6.7 | 0 | 0 | 150.7 | 150 | 144.7 | 143.4 | 186.8 | 41.8 | 19.8 | 57.8 | 2.8 |  |  | 230.5 | 119.5 | 110.1 | 304.5 | 116.1 | 87.3 | 313.8
4408.3 | 2708.3 | -6.7 | 0 | 0 | 150.4 | 149.7 | 144.3 | 143 | 186.2 | 41.8 | 19.8 | 57.7 | 3.2 |  |  | 229.3 | 118.5 | 109.2 | 303 | 115.5 | 86.8 | 312.6
4409.3 | 2709.3 | -6.7 | 0 | 0 | 150.1 | 149.3 | 143.9 | 142.7 | 185.6 | 41.7 | 19.8 | 57.6 | 3.1 |  |  | 228.4 | 117.8 | 108.3 | 301.6 | 115.4 | 86.4 | 311.1
4410.3 | 2710.3 | -6.7 | 0 | 0 | 149.9 | 148.9 | 143.4 | 142.4 | 185 | 41.6 | 19.8 | 57.4 | 3.2 |  |  | 227.2 | 117.2 | 107.7 | 300.1 | 115.4 | 86 | 309.8
4411.3 | 2711.3 | -6.7 | 0 | 0 | 149.6 | 148.5 | 143 | 142.1 | 184.4 | 41.5 | 19.8 | 57.2 | 3.7 |  |  | 227.1 | 116.7 | 107.2 | 298.7 | 114.8 | 85.5 | 308.2
4412.3 | 2712.3 | -6.7 | 0 | 0 | 148.8 | 148.1 | 142.6 | 141.9 | 183.8 | 41.4 | 19.8 | 57 | 3.7 |  |  | 225.8 | 115.6 | 106.5 | 297.3 | 114.2 | 85 | 306.7
4413.3 | 2713.3 | -6.7 | 0 | 0 | 148.4 | 147.7 | 142.1 | 141.5 | 183.3 | 41.3 | 19.8 | 56.9 | 3.7 |  |  | 223.6 | 114.9 | 105.7 | 295.9 | 114.2 | 84.6 | 305.2
4414.3 | 2714.3 | -6.7 | 0 | 0 | 148.2 | 147.3 | 141.7 | 141.1 | 182.7 | 41.3 | 19.8 | 56.8 | 3.7 |  |  | 223.5 | 115.1 | 104.9 | 294.5 | 113.2 | 84.2 | 302.9
4415.3 | 2715.3 | -6.7 | 0 | 0 | 147.7 | 147 | 141.5 | 140.6 | 182.2 | 41.3 | 19.8 | 56.7 | 3.9 |  |  | 223.3 | 115.3 | 104.1 | 293.2 | 112.3 | 83.6 | 301.6
4416.3 | 2716.3 | -6.7 | 0 | 0 | 147.5 | 146.6 | 141.1 | 140.1 | 181.7 | 41.3 | 19.8 | 56.6 | 4 |  |  | 221.9 | 115.4 | 103.2 | 291.8 | 111.5 | 82.9 | 300.3
4417.3 | 2717.3 | -6.7 | 0 | 0 | 147.3 | 146.3 | 140.7 | 139.8 | 181.2 | 41 | 19.8 | 56.5 | 3.9 |  |  | 219.9 | 114.7 | 102.2 | 290.4 | 110.9 | 82.2 | 298.6
4418.3 | 2718.3 | -6.7 | 0 | 0 | 147 | 145.9 | 140.2 | 139.7 | 180.7 | 40.8 | 19.8 | 56.4 | 3.5 |  |  | 215.9 | 113.2 | 101 | 289.1 | 111 | 81.6 | 297.3
4419.3 | 2719.3 | -6.7 | 0 | 0 | 146.7 | 145.5 | 139.9 | 139.5 | 180.3 | 40.6 | 19.8 | 56.3 | 3.5 |  |  | 214.2 | 113.1 | 100 | 287.8 | 110.3 | 81 | 295.5
4420.3 | 2720.3 | -6.7 | 0 | 0 | 146.2 | 145.2 | 139.7 | 139.2 | 179.8 | 40.5 | 19.8 | 56.2 | 3.2 |  |  | 212.1 | 113 | 99.1 | 286.4 | 109.9 | 80.6 | 294.3
4421.3 | 2721.3 | -6.7 | 0 | 0 | 146.1 | 144.9 | 139.4 | 138.9 | 179.4 | 40.3 | 19.8 | 56.1 | 3.3 |  |  | 210.8 | 112.7 | 98.3 | 285.1 | 109.5 | 80.3 | 293
4422.3 | 2722.3 | -6.7 | 0 | 0 | 145.9 | 144.6 | 139.2 | 138.6 | 179.1 | 40.2 | 19.8 | 55.9 | 3.2 |  |  | 209.6 | 112.5 | 97.5 | 283.9 | 108.9 | 79.8 | 291.6
4423.3 | 2723.3 | -6.7 | 0 | 0 | 145.4 | 144.4 | 139 | 138.4 | 178.7 | 40.1 | 19.8 | 55.8 | 3.1 |  |  | 209.5 | 111.5 | 96.7 | 282.6 | 108.8 | 79.2 | 289.9
4424.3 | 2724.3 | -6.7 | 0 | 0 | 145.3 | 144 | 138.6 | 138 | 178.4 | 40 | 19.8 | 55.8 | 2.6 |  |  | 210.3 | 111.8 | 96.4 | 281.3 | 108.6 | 78.8 | 288.3
4425.3 | 2725.3 | -6.7 | 0 | 0 | 145.1 | 143.7 | 138.3 | 137.6 | 178 | 39.9 | 19.8 | 55.8 | 2.4 |  |  | 211.2 | 112.4 | 96.2 | 280 | 109.1 | 78.3 | 287.2
4426.3 | 2726.3 | -6.7 | 0 | 0 | 144.6 | 143.5 | 138.1 | 137.4 | 177.5 | 40 | 19.8 | 55.7 | 2.7 |  |  | 212.7 | 113.6 | 95.8 | 278.8 | 109.6 | 77.7 | 286.2
4427.3 | 2727.3 | -6.7 | 0 | 0 | 144.6 | 143.2 | 137.7 | 136.9 | 177.1 | 40 | 19.8 | 55.7 | 2.7 |  |  | 214.3 | 114.4 | 95.3 | 277.5 | 109.4 | 77.1 | 284.8
4428.3 | 2728.3 | -6.7 | 0 | 0 | 144.5 | 142.8 | 137.4 | 136.6 | 176.6 | 39.9 | 19.8 | 55.7 | 2.8 |  |  | 215.4 | 114.5 | 94.9 | 276.2 | 108.8 | 76.6 | 283.4
4429.3 | 2729.3 | -6.7 | 0 | 0 | 144.3 | 142.5 | 137.2 | 136.3 | 176.2 | 39.8 | 19.8 | 55.6 | 3.3 |  |  | 216.9 | 114.9 | 94.5 | 275 | 109.3 | 76 | 281.9
4430.3 | 2730.3 | -6.7 | 0 | 0 | 144.3 | 142.1 | 136.8 | 136 | 175.8 | 39.6 | 19.8 | 55.6 | 3.3 |  |  | 218 | 114.9 | 94 | 273.8 | 109 | 75.4 | 280.9
4431.3 | 2731.3 | -6.7 | 0 | 0 | 143.9 | 141.9 | 136.5 | 135.7 | 175.5 | 39.7 | 19.8 | 55.5 | 3.3 |  |  | 218.4 | 114.8 | 93.3 | 272.6 | 109.2 | 74.9 | 280.2
4432.3 | 2732.3 | -6.7 | 0 | 0 | 143.7 | 141.6 | 136.1 | 135.4 | 175.2 | 39.8 | 19.8 | 55.4 | 3.1 |  |  | 219 | 114.7 | 92.7 | 271.4 | 108.7 | 74.4 | 279.1
4433.3 | 2733.3 | -6.7 | 0 | 0 | 143.3 | 141.3 | 135.9 | 135.1 | 174.8 | 39.7 | 19.8 | 55.4 | 3.4 |  |  | 219.1 | 114.3 | 91.9 | 270.3 | 107.8 | 73.9 | 277.6
4434.3 | 2734.3 | -6.7 | 0 | 0 | 142.7 | 140.9 | 135.8 | 134.8 | 174.4 | 39.6 | 19.8 | 55.3 | 3.8 |  |  | 218.7 | 113.5 | 91.1 | 269.1 | 107 | 73.4 | 275.4
4435.3 | 2735.3 | -6.7 | 0 | 0 | 142.5 | 140.4 | 135.5 | 134.3 | 173.9 | 39.7 | 19.8 | 55.3 | 3.9 |  |  | 218.6 | 113 | 90.3 | 268 | 105.9 | 72.9 | 272.7
4436.3 | 2736.3 | -6.7 | 0 | 0 | 142.4 | 140 | 135 | 133.9 | 173.4 | 39.8 | 19.8 | 55.2 | 3.7 |  |  | 218.9 | 112.4 | 89.5 | 266.9 | 105 | 72.4 | 271.1
4437.3 | 2737.3 | -6.7 | 0 | 0 | 142.2 | 139.7 | 134.6 | 133.7 | 173 | 39.7 | 19.8 | 55 | 3.1 |  |  | 218.5 | 111.4 | 88.9 | 265.8 | 104 | 71.9 | 270.3
4438.3 | 2738.3 | -6.7 | 0 | 0 | 142.2 | 139.3 | 134.2 | 133.4 | 172.5 | 39.8 | 19.8 | 54.8 | 3 |  |  | 218 | 110.5 | 88.3 | 264.7 | 102.8 | 71.4 | 269.7
4439.3 | 2739.3 | -6.7 | 0 | 0 | 142.1 | 139 | 133.9 | 133.2 | 172 | 39.7 | 19.8 | 54.6 | 2.7 |  |  | 217.3 | 109.6 | 87.7 | 263.6 | 102 | 71 | 268.5
4440.3 | 2740.3 | -6.7 | 0 | 0 | 141.9 | 138.7 | 133.7 | 132.9 | 171.6 | 39.5 | 19.8 | 54.5 | 2.6 |  |  | 216.6 | 108.3 | 87.1 | 262.5 | 101.1 | 70.6 | 267.1
4441.3 | 2741.3 | -6.7 | 0 | 0 | 141.6 | 138.4 | 133.5 | 132.5 | 171.1 | 39.5 | 19.8 | 54.4 | 3.1 |  |  | 215.1 | 107.7 | 86.5 | 261.3 | 100.2 | 70.2 | 266.4
4442.3 | 2742.3 | -6.7 | 0 | 0 | 141.3 | 138.2 | 133.3 | 132.2 | 170.8 | 39.4 | 19.9 | 54.2 | 3.7 |  |  | 212.8 | 107 | 86.1 | 260.2 | 99.3 | 69.7 | 265.7
4443.3 | 2743.3 | -6.7 | 0 | 0 | 141 | 137.9 | 133.1 | 131.8 | 170.4 | 39.4 | 19.9 | 54.1 | 4.3 |  |  | 210.5 | 106 | 85.8 | 259.2 | 99.1 | 69.3 | 264.8
4444.3 | 2744.3 | -6.7 | 0 | 0 | 140.6 | 137.7 | 132.8 | 131.5 | 170.1 | 39.2 | 19.9 | 54 | 4 |  |  | 208.7 | 104.7 | 85.5 | 258.1 | 99.1 | 69.1 | 263.8
4445.3 | 2745.3 | -6.7 | 0 | 0 | 140.1 | 137.5 | 132.6 | 131.2 | 169.8 | 39 | 19.9 | 53.9 | 3.9 |  |  | 207.7 | 103.6 | 85.1 | 257.1 | 99 | 68.9 | 262.9
4446.3 | 2746.3 | -6.7 | 0 | 0 | 139.6 | 137.2 | 132.4 | 130.9 | 169.5 | 38.9 | 19.9 | 53.8 | 3.6 |  |  | 206.7 | 103 | 84.7 | 256 | 99 | 68.6 | 261.8
4447.3 | 2747.3 | -6.7 | 0 | 0 | 139.1 | 137 | 132.1 | 130.8 | 169.2 | 38.8 | 19.9 | 53.8 | 3.8 |  |  | 205.9 | 102.7 | 84.3 | 254.9 | 98.3 | 68.2 | 260.8
4448.3 | 2748.3 | -6.7 | 0 | 0 | 138.9 | 136.8 | 131.9 | 130.7 | 168.8 | 38.7 | 19.9 | 53.7 | 4.4 |  |  | 205.2 | 102.4 | 84 | 253.8 | 97.6 | 67.9 | 259.7
4449.3 | 2749.3 | -6.7 | 0 | 0 | 138.7 | 136.6 | 131.7 | 130.4 | 168.5 | 38.6 | 19.9 | 53.6 | 4.7 |  |  | 204.7 | 102 | 83.5 | 252.8 | 96.9 | 67.6 | 258.5
4450.3 | 2750.3 | -6.7 | 0 | 0 | 138.5 | 136.3 | 131.5 | 130.2 | 168.3 | 38.6 | 19.9 | 53.5 | 4.7 |  |  | 203.6 | 101.2 | 83 | 251.7 | 96.1 | 67.3 | 257
4451.3 | 2751.3 | -6.7 | 0 | 0 | 138.4 | 136.1 | 131.3 | 130 | 168 | 38.5 | 19.9 | 53.4 | 5.1 |  |  | 202.2 | 101.1 | 82.5 | 250.6 | 95.5 | 67 | 255.6
4452.3 | 2752.3 | -6.7 | 0 | 0 | 138.1 | 135.9 | 130.9 | 129.8 | 167.8 | 38.4 | 19.9 | 53.3 | 4.4 |  |  | 201.2 | 101 | 82.1 | 249.6 | 94.9 | 66.8 | 254.6
4453.3 | 2753.3 | -6.7 | 0 | 0 | 137.9 | 135.6 | 130.6 | 129.7 | 167.5 | 38.3 | 19.9 | 53.3 | 4.5 |  |  | 200.1 | 100.1 | 81.5 | 248.6 | 94.4 | 66.5 | 253.2
4454.3 | 2754.3 | -6.7 | 0 | 0 | 137.4 | 135.3 | 130.4 | 129.5 | 167.2 | 38.2 | 19.9 | 53.2 | 4.2 |  |  | 198.7 | 99.1 | 81 | 247.5 | 94 | 66.2 | 252
4455.3 | 2755.3 | -6.7 | 0 | 0 | 136.9 | 135.1 | 130.1 | 129.2 | 166.9 | 38.1 | 19.9 | 53.2 | 3.8 |  |  | 197.6 | 98.7 | 80.6 | 246.5 | 93.9 | 65.9 | 251.3
4456.3 | 2756.3 | -6.7 | 0 | 0 | 136.7 | 135 | 129.8 | 128.9 | 166.6 | 38.2 | 19.9 | 53.1 | 3.5 |  |  | 196.4 | 98.3 | 80.3 | 245.5 | 93.2 | 65.7 | 250.5
4457.3 | 2757.3 | -6.7 | 0 | 0 | 136.5 | 134.9 | 129.4 | 128.7 | 166.3 | 38.2 | 19.9 | 53.1 | 3.8 |  |  | 194 | 97.6 | 80 | 244.5 | 92.9 | 65.4 | 249.8
4458.3 | 2758.3 | -6.7 | 0 | 0 | 136.5 | 134.7 | 129.1 | 128.5 | 166 | 38.1 | 19.9 | 53 | 3.9 |  |  | 191.8 | 97 | 79.5 | 243.5 | 92.6 | 65.2 | 249.3
4459.3 | 2759.3 | -6.7 | 0 | 0 | 136.3 | 134.4 | 128.8 | 128.2 | 165.6 | 38.1 | 19.9 | 52.9 | 3.8 |  |  | 190 | 96 | 79.1 | 242.6 | 92.4 | 65 | 248.5
4460.3 | 2760.3 | -6.7 | 0 | 0 | 136.2 | 134.1 | 128.7 | 128 | 165.2 | 38.1 | 19.9 | 52.9 | 4.4 |  |  | 189.4 | 95.5 | 78.8 | 241.6 | 91.9 | 64.8 | 247.5
4461.3 | 2761.3 | -6.7 | 0 | 0 | 136 | 133.7 | 128.5 | 127.8 | 164.8 | 38.1 | 19.9 | 52.9 | 4 |  |  | 188.5 | 95 | 78.4 | 240.6 | 91.4 | 64.6 | 246.2
4462.3 | 2762.3 | -6.7 | 0 | 0 | 135.8 | 133.4 | 128.3 | 127.5 | 164.4 | 38.1 | 19.9 | 52.8 | 4.2 |  |  | 188.4 | 95 | 78.1 | 239.7 | 90.9 | 64.4 | 245.6
4463.3 | 2763.3 | -6.7 | 0 | 0 | 135.7 | 133.1 | 128.2 | 127.1 | 164.2 | 38 | 19.9 | 52.8 | 3.9 |  |  | 188.4 | 95 | 77.8 | 238.7 | 90.5 | 64.2 | 244.7
4464.3 | 2764.3 | -6.7 | 0 | 0 | 135.5 | 132.9 | 128 | 126.8 | 164 | 37.9 | 19.9 | 52.8 | 3.9 |  |  | 187.9 | 95.4 | 77.5 | 237.7 | 90.1 | 63.9 | 243.6
4465.3 | 2765.3 | -6.7 | 0 | 0 | 135.2 | 132.7 | 127.8 | 126.5 | 163.7 | 37.8 | 19.9 | 52.7 | 4 |  |  | 187.6 | 95.7 | 77.3 | 236.8 | 89.7 | 63.7 | 243.5
4466.3 | 2766.3 | -6.7 | 0 | 0 | 134.8 | 132.5 | 127.6 | 126.3 | 163.5 | 37.8 | 19.9 | 52.7 | 4.1 |  |  | 187.5 | 95.3 | 77 | 235.8 | 89.2 | 63.6 | 242.7
4467.3 | 2767.3 | -6.7 | 0 | 0 | 134.3 | 132.3 | 127.4 | 126.1 | 163.4 | 37.7 | 19.9 | 52.7 | 4 |  |  | 187.1 | 94.7 | 76.7 | 234.9 | 88.6 | 63.3 | 241.4
4468.3 | 2768.3 | -6.7 | 0 | 0 | 133.7 | 132 | 127.2 | 125.9 | 163.2 | 37.6 | 19.9 | 52.6 | 3.2 |  |  | 185.5 | 94 | 76.2 | 234 | 88.2 | 63.1 | 240.3
4469.3 | 2769.3 | -6.7 | 0 | 0 | 133.5 | 131.8 | 126.9 | 125.7 | 163 | 37.5 | 19.9 | 52.4 | 3.3 |  |  | 184 | 93.2 | 75.7 | 233.1 | 87.7 | 62.8 | 239
4470.3 | 2770.3 | -6.7 | 0 | 0 | 133.3 | 131.4 | 126.7 | 125.4 | 162.8 | 37.3 | 19.9 | 52.3 | 3.6 |  |  | 182.7 | 92.3 | 75.2 | 232.2 | 87.2 | 62.6 | 237.8
4471.3 | 2771.3 | -6.7 | 0 | 0 | 133.2 | 131.2 | 126.5 | 125.2 | 162.6 | 37.1 | 20 | 52.2 | 3.5 |  |  | 181.4 | 91.9 | 74.9 | 231.3 | 86.7 | 62.4 | 236.6
4472.3 | 2772.3 | -6.7 | 0 | 0 | 133 | 131 | 126.2 | 125.1 | 162.4 | 37 | 20 | 52.1 | 3.1 |  |  | 179.4 | 91.5 | 74.5 | 230.4 | 86.3 | 62.2 | 236
4473.3 | 2773.3 | -6.7 | 0 | 0 | 132.9 | 130.8 | 125.8 | 124.8 | 162.2 | 37 | 19.9 | 52 | 3.1 |  |  | 177 | 91.2 | 74.1 | 229.5 | 85.8 | 62 | 235.4
4474.3 | 2774.3 | -6.7 | 0 | 0 | 132.8 | 130.5 | 125.5 | 124.6 | 162 | 36.9 | 20 | 52 | 3.4 |  |  | 174.8 | 90.5 | 73.8 | 228.6 | 85.4 | 61.8 | 234.6
4475.3 | 2775.3 | -6.7 | 0 | 0 | 132.7 | 130.2 | 125.3 | 124.4 | 161.8 | 36.9 | 20 | 51.9 | 3.4 |  |  | 172.6 | 89.9 | 73.4 | 227.7 | 85.1 | 61.7 | 233.8
4476.3 | 2776.3 | -6.7 | 0 | 0 | 132.5 | 129.8 | 125.2 | 124.3 | 161.6 | 36.7 | 20 | 51.9 | 3.2 |  |  | 170.9 | 89.4 | 73.2 | 226.8 | 84.8 | 61.6 | 233.3
4477.3 | 2777.3 | -6.7 | 0 | 0 | 132.4 | 129.5 | 125 | 124.1 | 161.3 | 36.7 | 20 | 51.9 | 3.3 |  |  | 169.4 | 88.6 | 73 | 226 | 84.4 | 61.5 | 232.5
4478.3 | 2778.3 | -6.7 | 0 | 0 | 132.2 | 129.3 | 124.8 | 123.8 | 161.1 | 36.6 | 20 | 51.9 | 3.5 |  |  | 168.2 | 88 | 72.8 | 225.1 | 84.2 | 61.4 | 231.3
4479.3 | 2779.3 | -6.7 | 0 | 0 | 131.5 | 129.2 | 124.9 | 123.6 | 160.9 | 36.6 | 20 | 51.9 | 3.5 |  |  | 167.4 | 87.6 | 72.5 | 224.4 | 84.1 | 61.2 | 230.7
4480.3 | 2780.3 | -6.7 | 0 | 0 | 131.3 | 129 | 124.5 | 123.3 | 160.6 | 36.5 | 20 | 51.9 | 3.1 |  |  | 167 | 87.8 | 72.4 | 223.5 | 83.9 | 61.1 | 229.6
4481.3 | 2781.3 | -6.7 | 0 | 0 | 130.8 | 128.8 | 124.3 | 123.1 | 160.4 | 36.5 | 20 | 51.7 | 3.2 |  |  | 167.4 | 88.6 | 72.4 | 222.6 | 84.2 | 61 | 228.4
4482.3 | 2782.3 | -6.7 | 0 | 0 | 130.6 | 128.7 | 124.2 | 123 | 160.2 | 36.5 | 20 | 51.5 | 3.8 |  |  | 166.3 | 88.1 | 72 | 221.9 | 84.5 | 60.8 | 227.4
4483.3 | 2783.3 | -6.7 | 0 | 0 | 130.4 | 128.5 | 124 | 122.7 | 160 | 36.6 | 20 | 51.4 | 3.5 |  |  | 164.7 | 87.7 | 71.5 | 221.1 | 84.5 | 60.5 | 226.3
4484.3 | 2784.3 | -6.7 | 0 | 0 | 130.4 | 128.3 | 123.7 | 122.5 | 159.8 | 36.6 | 20 | 51.2 | 3.3 |  |  | 164.5 | 87.9 | 71.1 | 220.3 | 84.2 | 60.4 | 225.2
4485.3 | 2785.3 | -6.7 | 0 | 0 | 130.3 | 128 | 123.5 | 122.3 | 159.6 | 36.6 | 20 | 51.2 | 3.3 |  |  | 164.7 | 87.8 | 70.9 | 219.4 | 83.8 | 60.3 | 224.4
4486.3 | 2786.3 | -6.7 | 0 | 0 | 130.1 | 127.8 | 123.3 | 122.1 | 159.3 | 36.4 | 20 | 51.1 | 3.7 |  |  | 164.7 | 87.8 | 70.7 | 218.7 | 84 | 60 | 223.8
4487.3 | 2787.3 | -6.7 | 0 | 0 | 130.1 | 127.6 | 122.9 | 121.9 | 159.1 | 36.3 | 20 | 50.9 | 4.2 |  |  | 163.5 | 87.4 | 70.4 | 217.8 | 84 | 59.9 | 223.1
4488.3 | 2788.3 | -6.7 | 0 | 0 | 129.9 | 127.4 | 122.7 | 121.7 | 158.8 | 36.5 | 20 | 50.8 | 4.7 |  |  | 161.6 | 86.6 | 70 | 217 | 84.6 | 59.7 | 222.4
4489.3 | 2789.3 | -6.7 | 0 | 0 | 129.8 | 127.2 | 122.7 | 121.5 | 158.6 | 36.7 | 20 | 50.8 | 4 |  |  | 160.1 | 87 | 69.6 | 216.3 | 84.9 | 59.4 | 221.7
4490.3 | 2790.3 | -6.7 | 0 | 0 | 129.6 | 126.9 | 122.6 | 121.3 | 158.4 | 36.9 | 20 | 50.7 | 3.3 |  |  | 159.7 | 88 | 69.3 | 215.5 | 84.6 | 59.2 | 220.6
4491.3 | 2791.3 | -6.7 | 0 | 0 | 129.6 | 126.6 | 122.3 | 121.1 | 158.2 | 36.8 | 20 | 50.8 | 3.4 |  |  | 160.5 | 88.6 | 69.1 | 214.7 | 84.2 | 59 | 219.3
4492.3 | 2792.3 | -6.7 | 0 | 0 | 129.5 | 126.4 | 122.2 | 120.9 | 158 | 36.8 | 20 | 50.7 | 3.3 |  |  | 161.1 | 89.2 | 68.8 | 213.9 | 84.1 | 58.8 | 218.2
4493.3 | 2793.3 | -6.7 | 0 | 0 | 129.3 | 126.3 | 122.2 | 120.7 | 157.7 | 36.8 | 20 | 50.6 | 2.9 |  |  | 159.9 | 89.2 | 68.4 | 213.2 | 84 | 58.5 | 217.6
4494.3 | 2794.3 | -6.7 | 0 | 0 | 129.4 | 126.1 | 121.7 | 120.4 | 157.5 | 36.7 | 20 | 50.5 | 3.1 |  |  | 158 | 88.6 | 68 | 212.5 | 84.1 | 58.3 | 216.8
4495.3 | 2795.3 | -6.7 | 0 | 0 | 129.3 | 125.9 | 121.4 | 120.3 | 157.4 | 36.6 | 20 | 50.4 | 3.2 |  |  | 156.2 | 88.6 | 67.7 | 211.7 | 83.9 | 58.1 | 216.1
4496.3 | 2796.3 | -6.7 | 0 | 0 | 128.9 | 125.8 | 121.3 | 120.2 | 157.2 | 36.6 | 20 | 50.4 | 3.5 |  |  | 155.8 | 88.8 | 67.4 | 211 | 83.8 | 57.8 | 215.3
4497.3 | 2797.3 | -6.7 | 0 | 0 | 128.6 | 125.5 | 121.2 | 120.2 | 157 | 36.5 | 20 | 50.2 | 3.8 |  |  | 155.4 | 89.2 | 67.2 | 210.3 | 83.3 | 57.7 | 214.3
4498.3 | 2798.3 | -6.7 | 0 | 0 | 128.4 | 125.3 | 121 | 119.9 | 156.8 | 36.4 | 20 | 50.1 | 3.4 |  |  | 154.9 | 88.7 | 66.9 | 209.6 | 82.9 | 57.6 | 213.9
4499.3 | 2799.3 | -6.7 | 0 | 0 | 128 | 125.1 | 121 | 119.6 | 156.5 | 36.2 | 20 | 50 | 4 |  |  | 154.7 | 88.1 | 66.6 | 208.9 | 82.4 | 57.5 | 213.2
4500.3 | 2800.3 | -6.7 | 0 | 0 | 127.4 | 125 | 120.9 | 119.4 | 156.2 | 36.1 | 20 | 49.9 | 3.6 |  |  | 155.2 | 87.7 | 66.4 | 208.2 | 82 | 57.3 | 212.3
4501.3 | 2801.3 | -6.7 | 0 | 0 | 127.1 | 124.8 | 120.5 | 119.1 | 155.9 | 35.9 | 20 | 49.8 | 3.4 |  |  | 155.6 | 87.6 | 66.3 | 207.5 | 81.7 | 57.1 | 211.3
4502.3 | 2802.3 | -6.7 | 0 | 0 | 127 | 124.6 | 120.2 | 118.9 | 155.6 | 35.9 | 20 | 49.7 | 3.3 |  |  | 156.5 | 87.6 | 66.1 | 206.8 | 81.4 | 57 | 210.2
4503.3 | 2803.3 | -6.7 | 0 | 0 | 126.9 | 124.5 | 120.1 | 118.8 | 155.4 | 36 | 20 | 49.7 | 4 |  |  | 157.5 | 87.4 | 66 | 206.2 | 80.9 | 56.8 | 209.2
4504.3 | 2804.3 | -6.7 | 0 | 0 | 126.8 | 124.4 | 119.8 | 118.6 | 155.2 | 36.1 | 20 | 49.7 | 4.6 |  |  | 158.1 | 87.3 | 65.7 | 205.5 | 80.5 | 56.5 | 208.3
4505.3 | 2805.3 | -6.7 | 0 | 0 | 126.2 | 124.2 | 119.6 | 118.4 | 155 | 36.2 | 20.1 | 49.7 | 4.1 |  |  | 158.3 | 87 | 65.5 | 204.8 | 80.6 | 56.3 | 207.8
4506.3 | 2806.3 | -6.7 | 0 | 0 | 125.6 | 124.1 | 119.4 | 118.3 | 154.9 | 36.1 | 20 | 49.7 | 3.7 |  |  | 157.8 | 86.7 | 65.3 | 204.1 | 80.3 | 56.1 | 207.6
4507.3 | 2807.3 | -6.7 | 0 | 0 | 125 | 124.1 | 119.3 | 118.3 | 154.6 | 35.9 | 20 | 49.6 | 3.5 |  |  | 157.2 | 86.2 | 65 | 203.5 | 80.1 | 55.9 | 206.7
4508.3 | 2808.3 | -6.7 | 0 | 0 | 125 | 123.9 | 118.8 | 118.1 | 154.4 | 35.8 | 20 | 49.7 | 3.3 |  |  | 156.2 | 85.3 | 64.7 | 202.8 | 80 | 55.8 | 205.6
4509.3 | 2809.3 | -6.7 | 0 | 0 | 124.8 | 123.7 | 118.6 | 117.9 | 154.2 | 35.7 | 20.1 | 49.6 | 3.6 |  |  | 155.5 | 84.8 | 64.4 | 202.1 | 79.9 | 55.7 | 204.7
4510.3 | 2810.3 | -6.7 | 0 | 0 | 124.4 | 123.4 | 118.4 | 117.6 | 154 | 35.6 | 20 | 49.7 | 3.5 |  |  | 155.3 | 84.4 | 64 | 201.4 | 79.5 | 55.6 | 203.7
4511.3 | 2811.3 | -6.7 | 0 | 0 | 123.9 | 123.1 | 118.3 | 117.5 | 153.8 | 35.7 | 20.1 | 49.6 | 3.8 |  |  | 154.4 | 84.1 | 63.8 | 200.7 | 79.2 | 55.6 | 203.1
4512.3 | 2812.3 | -6.7 | 0 | 0 | 123.4 | 122.9 | 118.1 | 117.4 | 153.6 | 35.6 | 20.1 | 49.5 | 3.2 |  |  | 154.4 | 84.5 | 63.7 | 200 | 79.5 | 55.5 | 202.9
4513.3 | 2813.3 | -6.7 | 0 | 0 | 123.2 | 122.6 | 118 | 117.2 | 153.3 | 35.6 | 20.1 | 49.4 | 3.2 |  |  | 154.1 | 84.7 | 63.5 | 199.4 | 79.5 | 55.4 | 202.4
4514.3 | 2814.3 | -6.7 | 0 | 0 | 123.1 | 122.4 | 117.9 | 117.1 | 153 | 35.6 | 20.1 | 49.3 | 3.1 |  |  | 152.7 | 84.4 | 63.2 | 198.7 | 79.3 | 55.2 | 201.9
4515.3 | 2815.3 | -6.7 | 0 | 0 | 123 | 122.2 | 117.8 | 116.9 | 152.8 | 35.6 | 20.1 | 49.1 | 2.7 |  |  | 151.4 | 83.8 | 62.8 | 198.1 | 79.3 | 55 | 201.4
4516.3 | 2816.3 | -6.7 | 0 | 0 | 122.9 | 122.1 | 117.6 | 116.7 | 152.6 | 35.6 | 20.1 | 49.1 | 2.6 |  |  | 150 | 83.4 | 62.6 | 197.4 | 79.6 | 54.9 | 200.9
4517.3 | 2817.3 | -6.7 | 0 | 0 | 122.7 | 122 | 117.4 | 116.5 | 152.4 | 35.7 | 20.1 | 49.1 | 2.6 |  |  | 148.4 | 82.8 | 62.2 | 196.8 | 79.8 | 54.7 | 200.6
4518.3 | 2818.3 | -6.7 | 0 | 0 | 122.6 | 121.9 | 117.4 | 116.3 | 152.1 | 35.8 | 20.1 | 49.1 | 2.3 |  |  | 147 | 82.8 | 61.9 | 196.1 | 80.1 | 54.6 | 199.9
4519.3 | 2819.3 | -6.7 | 0 | 0 | 122.6 | 121.7 | 117.3 | 116.1 | 151.9 | 35.6 | 20.1 | 49.1 | 2 |  |  | 145.5 | 82.7 | 61.5 | 195.5 | 80.9 | 54.3 | 199.1
4520.3 | 2820.3 | -6.7 | 0 | 0 | 122.6 | 121.6 | 117.2 | 115.9 | 151.5 | 35.5 | 20.1 | 49.1 | 2.5 |  |  | 143.9 | 82.1 | 61.2 | 194.9 | 81.3 | 54.2 | 198.3
4521.3 | 2821.3 | -6.7 | 0 | 0 | 122.6 | 121.4 | 116.9 | 115.8 | 151.3 | 35.5 | 20.1 | 49 | 3.3 |  |  | 142.3 | 81.6 | 60.9 | 194.3 | 81.5 | 54 | 197.5
4522.3 | 2822.3 | -6.7 | 0 | 0 | 122.5 | 121.2 | 116.5 | 115.7 | 151 | 35.5 | 20.1 | 49 | 3.3 |  |  | 141.6 | 81.3 | 60.7 | 193.7 | 81.8 | 53.9 | 196.7
4523.3 | 2823.3 | -6.7 | 0 | 0 | 122.1 | 121.1 | 116.3 | 115.5 | 150.8 | 35.5 | 20.1 | 49 | 3.2 |  |  | 141.6 | 81.7 | 60.6 | 193 | 82.2 | 53.8 | 196.3
4524.3 | 2824.3 | -6.7 | 0 | 0 | 121.9 | 121 | 116.1 | 115.3 | 150.6 | 35.5 | 20.1 | 49 | 3.1 |  |  | 142.5 | 82 | 60.5 | 192.5 | 82.6 | 53.6 | 195.3
4525.3 | 2825.3 | -6.7 | 0 | 0 | 121.7 | 120.8 | 115.9 | 115.1 | 150.4 | 35.6 | 20.1 | 49 | 2.8 |  |  | 143 | 82.2 | 60.4 | 191.9 | 83 | 53.4 | 194.1
4526.3 | 2826.3 | -6.7 | 0 | 0 | 121.5 | 120.6 | 115.8 | 114.9 | 150.2 | 35.8 | 20.1 | 49 | 3.1 |  |  | 143.3 | 82.9 | 60.2 | 191.3 | 83.4 | 53.2 | 193.3
4527.3 | 2827.3 | -6.7 | 0 | 0 | 121.2 | 120.5 | 115.7 | 114.8 | 150 | 35.9 | 20.1 | 49 | 3.5 |  |  | 144 | 83.9 | 60.1 | 190.7 | 83.7 | 52.9 | 192.6
4528.3 | 2828.3 | -6.7 | 0 | 0 | 120.9 | 120.3 | 115.5 | 114.6 | 149.8 | 35.9 | 20.1 | 49 | 3.5 |  |  | 143.7 | 84.7 | 59.9 | 190.1 | 84 | 52.7 | 191.9
4529.3 | 2829.3 | -6.7 | 0 | 0 | 120.7 | 120.2 | 115.3 | 114.4 | 149.6 | 36 | 20.1 | 48.9 | 3.7 |  |  | 142.3 | 85 | 59.5 | 189.5 | 84.1 | 52.5 | 191.1
4530.3 | 2830.3 | -6.7 | 0 | 0 | 120.5 | 120 | 115.1 | 114.2 | 149.4 | 36.1 | 20.1 | 48.9 | 4.2 |  |  | 140.3 | 85.4 | 59.1 | 188.9 | 83.8 | 52.3 | 190.6
4531.3 | 2831.3 | -6.7 | 0 | 0 | 120.2 | 119.8 | 114.9 | 114.1 | 149.3 | 36.2 | 20.1 | 48.8 | 3.7 |  |  | 137.9 | 84.6 | 58.7 | 188.3 | 83.8 | 52.1 | 190.4
4532.3 | 2832.3 | -6.7 | 0 | 0 | 120.2 | 119.6 | 114.8 | 114 | 149 | 36.1 | 20.1 | 48.7 | 4 |  |  | 135.4 | 83.7 | 58.4 | 187.8 | 83.9 | 52 | 189.9
4533.3 | 2833.3 | -6.7 | 0 | 0 | 120.3 | 119.4 | 114.6 | 113.9 | 148.8 | 36 | 20.1 | 48.6 | 4.1 |  |  | 133.8 | 84.2 | 58.2 | 187.2 | 84 | 51.8 | 189.4
4534.3 | 2834.3 | -6.7 | 0 | 0 | 120.2 | 119.3 | 114.5 | 113.8 | 148.6 | 35.9 | 20.1 | 48.5 | 3.5 |  |  | 132.5 | 84.6 | 58 | 186.6 | 83.4 | 51.7 | 188.6
4535.3 | 2835.3 | -6.7 | 0 | 0 | 119.9 | 119.1 | 114.3 | 113.7 | 148.5 | 35.9 | 20.1 | 48.4 | 3.3 |  |  | 131.3 | 84.4 | 57.8 | 186.1 | 83.3 | 51.6 | 188
4536.3 | 2836.3 | -6.7 | 0 | 0 | 119.7 | 118.9 | 114.1 | 113.6 | 148.4 | 35.9 | 20.1 | 48.3 | 3.7 |  |  | 130.3 | 84.4 | 57.7 | 185.5 | 83.3 | 51.6 | 187.4
4537.3 | 2837.3 | -6.7 | 0 | 0 | 119.6 | 118.7 | 114 | 113.4 | 148.2 | 35.9 | 20.1 | 48.2 | 3.9 |  |  | 129.5 | 85.1 | 57.4 | 184.9 | 83.3 | 51.4 | 186.7
4538.3 | 2838.3 | -6.7 | 0 | 0 | 119.7 | 118.6 | 114 | 113.2 | 148 | 36 | 20.1 | 48.1 | 4.1 |  |  | 129.1 | 85.6 | 57.2 | 184.4 | 83.5 | 51.3 | 185.6
4539.3 | 2839.3 | -6.7 | 0 | 0 | 119.7 | 118.4 | 114 | 113.1 | 147.9 | 36 | 20.1 | 48 | 4.2 |  |  | 129 | 85.5 | 57 | 183.9 | 83.4 | 51.2 | 184.6
4540.3 | 2840.3 | -6.7 | 0 | 0 | 119.7 | 118.3 | 113.9 | 113 | 147.8 | 36 | 20.1 | 47.9 | 4.1 |  |  | 128.7 | 84.6 | 56.8 | 183.4 | 83.2 | 51.2 | 183.8
4541.3 | 2841.3 | -6.7 | 0 | 0 | 119.6 | 118.2 | 113.7 | 112.9 | 147.7 | 36 | 20.2 | 47.8 | 4.2 |  |  | 127.8 | 83.6 | 56.8 | 182.8 | 83.6 | 51.1 | 183.4
4542.3 | 2842.3 | -6.7 | 0 | 0 | 119.4 | 118 | 113.5 | 112.7 | 147.6 | 36 | 20.2 | 47.7 | 4.3 |  |  | 127.2 | 82.9 | 56.9 | 182.3 | 83.2 | 51 | 182.9
4543.3 | 2843.3 | -6.7 | 0 | 0 | 119.1 | 117.9 | 113.4 | 112.5 | 147.5 | 36 | 20.2 | 47.6 | 4 |  |  | 126.4 | 82.3 | 56.7 | 181.8 | 83.1 | 51 | 182.3
4544.3 | 2844.3 | -6.7 | 0 | 0 | 118.8 | 117.7 | 113.4 | 112.4 | 147.4 | 36.1 | 20.1 | 47.5 | 3.9 |  |  | 125.9 | 82.3 | 56.6 | 181.3 | 82.8 | 50.9 | 181.7
4545.3 | 2845.3 | -6.7 | 0 | 0 | 118.6 | 117.5 | 113.2 | 112.3 | 147.2 | 36 | 20.2 | 47.4 | 4.9 |  |  | 125.9 | 82.6 | 56.4 | 180.8 | 82.5 | 50.8 | 181.1
4546.3 | 2846.3 | -6.7 | 0 | 0 | 118.2 | 117.3 | 113 | 112.2 | 147 | 35.9 | 20.2 | 47.3 | 5.2 |  |  | 125.6 | 82.8 | 56.3 | 180.3 | 81.9 | 50.8 | 180.6
4547.3 | 2847.3 | -6.7 | 0 | 0 | 117.8 | 117.1 | 112.7 | 112 | 146.8 | 35.8 | 20.2 | 47.2 | 4.8 |  |  | 125.2 | 83.2 | 56.1 | 179.8 | 81.8 | 50.7 | 180
4548.3 | 2848.3 | -6.7 | 0 | 0 | 117.6 | 116.9 | 112.5 | 111.9 | 146.7 | 35.7 | 20.2 | 47.1 | 4.2 |  |  | 124.6 | 83.6 | 55.9 | 179.2 | 81.3 | 50.6 | 179.4
4549.3 | 2849.3 | -6.7 | 0 | 0 | 117.7 | 116.7 | 112.4 | 111.9 | 146.5 | 35.6 | 20.2 | 47 | 4.7 |  |  | 123.8 | 83.4 | 55.7 | 178.7 | 80.9 | 50.5 | 178.9
4550.3 | 2850.3 | -6.7 | 0 | 0 | 117.7 | 116.5 | 112.3 | 111.7 | 146.3 | 35.4 | 20.2 | 47 | 4.3 |  |  | 122.9 | 83.2 | 55.5 | 178.2 | 80.6 | 50.3 | 178.3
4551.3 | 2851.3 | -6.7 | 0 | 0 | 117.7 | 116.3 | 112.2 | 111.5 | 146.2 | 35.2 | 20.2 | 47 | 4 |  |  | 121.9 | 82.7 | 55.2 | 177.7 | 80.4 | 50.3 | 177.8
4552.3 | 2852.3 | -6.7 | 0 | 0 | 117.7 | 116.1 | 112.1 | 111.3 | 146 | 35.1 | 20.2 | 47.1 | 3.8 |  |  | 121.4 | 82.1 | 55 | 177.3 | 80.1 | 50.2 | 177.1
4553.3 | 2853.3 | -6.7 | 0 | 0 | 117.6 | 116 | 112.1 | 111.3 | 145.8 | 35.1 | 20.2 | 47.2 | 3.3 |  |  | 120.7 | 81.2 | 54.9 | 176.8 | 79.8 | 50.1 | 176.4
4554.3 | 2854.3 | -6.7 | 0 | 0 | 117.3 | 115.9 | 111.9 | 111.2 | 145.6 | 35.1 | 20.2 | 47.2 | 3 |  |  | 119.8 | 80.7 | 54.7 | 176.3 | 79.6 | 50 | 175.9
4555.3 | 2855.3 | -6.7 | 0 | 0 | 117 | 115.7 | 111.7 | 111 | 145.4 | 35.2 | 20.2 | 47.3 | 3.6 |  |  | 118.9 | 80.1 | 54.5 | 175.8 | 79.3 | 49.9 | 175.3
4556.3 | 2856.3 | -6.7 | 0 | 0 | 116.8 | 115.6 | 111.5 | 110.8 | 145.2 | 35.2 | 20.2 | 47.3 | 3.8 |  |  | 118.3 | 79.7 | 54.4 | 175.3 | 79 | 49.8 | 174.6
4557.3 | 2857.3 | -6.7 | 0 | 0 | 116.9 | 115.5 | 111.4 | 110.6 | 145 | 35.3 | 20.2 | 47.3 | 3.1 |  |  | 118.3 | 79.9 | 54.3 | 174.9 | 78.6 | 49.9 | 173.7
4558.3 | 2858.3 | -6.7 | 0 | 0 | 116.9 | 115.4 | 111.4 | 110.5 | 144.8 | 35.4 | 20.2 | 47.3 | 2.6 |  |  | 117.7 | 79.8 | 54.2 | 174.4 | 78.3 | 50 | 172.5
4559.3 | 2859.3 | -6.7 | 0 | 0 | 116.9 | 115.2 | 111.3 | 110.3 | 144.6 | 35.3 | 20.2 | 47.3 | 2.5 |  |  | 117 | 78.9 | 54 | 173.9 | 78.2 | 49.9 | 172.2
4560.3 | 2860.3 | -6.7 | 0 | 0 | 116.8 | 115 | 111.2 | 110.2 | 144.5 | 35.2 | 20.2 | 47.3 | 2.3 |  |  | 115.8 | 77.9 | 53.8 | 173.5 | 77.9 | 49.8 | 172.1
4561.3 | 2861.3 | -6.7 | 0 | 0 | 116.8 | 114.8 | 111 | 110.1 | 144.4 | 35.1 | 20.2 | 47.3 | 2.6 |  |  | 115.5 | 77.6 | 53.7 | 173 | 77.6 | 49.7 | 171.5
4562.3 | 2862.3 | -6.7 | 0 | 0 | 116.8 | 114.7 | 110.8 | 110 | 144.3 | 35 | 20.2 | 47.2 | 2.7 |  |  | 115.4 | 77.5 | 53.6 | 172.5 | 77.5 | 49.6 | 170.9
4563.3 | 2863.3 | -6.7 | 0 | 0 | 116.9 | 114.5 | 110.7 | 110 | 144.1 | 34.9 | 20.2 | 47.1 | 3.3 |  |  | 114.9 | 77.1 | 53.5 | 172 | 77.2 | 49.5 | 170.4
4564.3 | 2864.3 | -6.7 | 0 | 0 | 116.9 | 114.2 | 110.5 | 109.9 | 144 | 34.7 | 20.2 | 47.1 | 4.8 |  |  | 113.5 | 76.2 | 53.4 | 171.6 | 76.8 | 49.5 | 170.3
4565.3 | 2865.3 | -6.7 | 0 | 0 | 116.9 | 114 | 110.4 | 109.7 | 143.8 | 34.6 | 20.2 | 47 | 6.1 |  |  | 112.9 | 75.7 | 53.4 | 171.1 | 77 | 49.5 | 170
4566.3 | 2866.3 | -6.7 | 0 | 0 | 116.8 | 113.8 | 110.3 | 109.6 | 143.7 | 34.4 | 20.2 | 46.8 | 5.9 |  |  | 113 | 75.5 | 53.3 | 170.6 | 77.3 | 49.4 | 169.4
4567.3 | 2867.3 | -6.7 | 0 | 0 | 116.6 | 113.7 | 110.3 | 109.4 | 143.6 | 34.4 | 20.2 | 46.7 | 5.6 |  |  | 112.7 | 75.5 | 53.3 | 170.2 | 77.1 | 49.4 | 168.7
4568.3 | 2868.3 | -6.7 | 0 | 0 | 116.3 | 113.5 | 110.1 | 109.2 | 143.5 | 34.4 | 20.2 | 46.5 | 5.1 |  |  | 111.7 | 75 | 53.1 | 169.7 | 76.8 | 49.3 | 167.8
4569.3 | 2869.3 | -6.7 | 0 | 0 | 115.9 | 113.2 | 109.9 | 109.1 | 143.3 | 34.3 | 20.2 | 46.4 | 4.1 |  |  | 111.4 | 75 | 53 | 169.2 | 76.3 | 49.3 | 167.4
4570.3 | 2870.3 | -6.7 | 0 | 0 | 115.5 | 113.1 | 109.7 | 109 | 143.1 | 34.2 | 20.2 | 46.3 | 4.5 |  |  | 111.9 | 74.8 | 53 | 168.8 | 75.8 | 49.2 | 167.1
4571.3 | 2871.3 | -6.7 | 0 | 0 | 115.2 | 113.1 | 109.5 | 108.9 | 142.9 | 34.2 | 20.2 | 46.2 | 4.4 |  |  | 111.7 | 74.9 | 53 | 168.3 | 75.7 | 49.2 | 166.7
4572.3 | 2872.3 | -6.7 | 0 | 0 | 114.9 | 113 | 109.3 | 108.9 | 142.6 | 34.2 | 20.2 | 46.2 | 5.2 |  |  | 111.5 | 75.4 | 52.9 | 167.9 | 75.6 | 49 | 166.3
4573.3 | 2873.3 | -6.7 | 0 | 0 | 114.7 | 112.8 | 109.2 | 108.8 | 142.4 | 34.3 | 20.2 | 46.1 | 5.5 |  |  | 111.3 | 76.1 | 52.8 | 167.4 | 75.7 | 48.9 | 165.7
4574.3 | 2874.3 | -6.7 | 0 | 0 | 114.6 | 112.6 | 109.1 | 108.7 | 142.3 | 34.3 | 20.2 | 46 | 6.1 |  |  | 111.6 | 76.8 | 52.6 | 166.9 | 75.8 | 48.8 | 165.1
4575.3 | 2875.3 | -6.7 | 0 | 0 | 114.7 | 112.4 | 109 | 108.7 | 142.1 | 34.3 | 20.2 | 46 | 5.4 |  |  | 111.7 | 77.2 | 52.5 | 166.5 | 75.6 | 48.7 | 164.5
4576.3 | 2876.3 | -6.7 | 0 | 0 | 114.7 | 112.3 | 109 | 108.5 | 141.9 | 34.4 | 20.2 | 45.9 | 5.4 |  |  | 112.2 | 77.8 | 52.4 | 166 | 75.6 | 48.5 | 163.9
4577.3 | 2877.3 | -6.7 | 0 | 0 | 114.7 | 112.2 | 108.8 | 108.4 | 141.7 | 34.5 | 20.2 | 45.9 | 5.7 |  |  | 112.4 | 78.3 | 52.3 | 165.6 | 75.2 | 48.4 | 163.4
4578.3 | 2878.3 | -6.7 | 0 | 0 | 114.7 | 112.1 | 108.7 | 108.3 | 141.6 | 34.5 | 20.2 | 45.9 | 4.3 |  |  | 111.8 | 78.1 | 52.2 | 165.2 | 75.1 | 48.3 | 163
4579.3 | 2879.3 | -6.7 | 0 | 0 | 114.7 | 112 | 108.6 | 108.2 | 141.4 | 34.5 | 20.2 | 45.9 | 3.9 |  |  | 111.2 | 77.5 | 52 | 164.7 | 75.1 | 48.2 | 162.4
4580.3 | 2880.3 | -6.7 | 0 | 0 | 114.7 | 112 | 108.4 | 108.1 | 141.3 | 34.4 | 20.2 | 45.8 | 3.9 |  |  | 110.7 | 77.2 | 51.9 | 164.3 | 75.1 | 48.1 | 162
4581.3 | 2881.3 | -6.7 | 0 | 0 | 114.6 | 111.9 | 108.3 | 107.9 | 141.2 | 34.3 | 20.2 | 45.8 | 3.2 |  |  | 110.2 | 76.2 | 51.7 | 163.8 | 75.3 | 48 | 161.6
4582.3 | 2882.3 | -6.7 | 0 | 0 | 114.5 | 111.9 | 108.2 | 107.7 | 141 | 34.3 | 20.2 | 45.7 | 3.8 |  |  | 109.3 | 75.3 | 51.5 | 163.4 | 75.4 | 47.9 | 161.4
4583.3 | 2883.3 | -6.7 | 0 | 0 | 114.4 | 111.9 | 108.1 | 107.5 | 140.8 | 34.2 | 20.2 | 45.7 | 3.9 |  |  | 108.3 | 74.9 | 51.6 | 163 | 75.5 | 47.9 | 161.4
4584.3 | 2884.3 | -6.7 | 0 | 0 | 114.2 | 111.8 | 108 | 107.3 | 140.7 | 34.2 | 20.2 | 45.6 | 3.1 |  |  | 107.8 | 74.4 | 52.2 | 162.6 | 75.7 | 47.8 | 161.1
4585.3 | 2885.3 | -6.7 | 0 | 0 | 114 | 111.6 | 107.9 | 107.2 | 140.5 | 34.3 | 20.3 | 45.6 | 3.5 |  |  | 108.1 | 75 | 52.4 | 162.2 | 75.5 | 47.8 | 160.2
4586.3 | 2886.3 | -6.7 | 0 | 0 | 113.8 | 111.5 | 107.8 | 106.9 | 140.4 | 34.1 | 20.3 | 45.5 | 4.6 |  |  | 109.1 | 75.7 | 52.3 | 161.8 | 75.2 | 47.7 | 159.4
4587.3 | 2887.3 | -6.7 | 0 | 0 | 113.8 | 111.4 | 107.7 | 106.7 | 140.3 | 33.9 | 20.3 | 45.5 | 5.3 |  |  | 110 | 76.2 | 52.2 | 161.3 | 74.8 | 47.6 | 158.6
4588.3 | 2888.3 | -6.7 | 0 | 0 | 113.7 | 111.3 | 107.5 | 106.7 | 140.2 | 33.8 | 20.3 | 45.4 | 5.7 |  |  | 111.6 | 76.8 | 52 | 160.9 | 75 | 47.6 | 157.9
4589.3 | 2889.3 | -6.7 | 0 | 0 | 113.5 | 111.2 | 107.2 | 106.6 | 140.1 | 33.8 | 20.3 | 45.2 | 5.5 |  |  | 113.1 | 76.9 | 51.9 | 160.5 | 75.2 | 47.5 | 157.4
4590.3 | 2890.3 | -6.7 | 0 | 0 | 113 | 111 | 106.9 | 106.5 | 140 | 33.6 | 20.3 | 45.1 | 6.7 |  |  | 114.5 | 77.1 | 51.9 | 160.1 | 75.3 | 47.4 | 156.9
4591.3 | 2891.3 | -6.7 | 0 | 0 | 112.6 | 110.9 | 106.8 | 106.3 | 139.9 | 33.5 | 20.3 | 45.1 | 7.6 |  |  | 115.4 | 77.1 | 51.8 | 159.7 | 75.2 | 47.3 | 156.5
4592.3 | 2892.3 | -6.7 | 0 | 0 | 112.4 | 110.7 | 106.6 | 106.1 | 139.7 | 33.4 | 20.3 | 45 | 6.2 |  |  | 115.7 | 77 | 51.7 | 159.3 | 74.8 | 47.2 | 156
4593.3 | 2893.3 | -6.7 | 0 | 0 | 112.5 | 110.5 | 106.6 | 106 | 139.6 | 33.4 | 20.3 | 44.9 | 6.8 |  |  | 115.9 | 76.9 | 51.6 | 159 | 74.3 | 47.2 | 155.8
4594.3 | 2894.3 | -6.7 | 0 | 0 | 112.5 | 110.4 | 106.5 | 105.9 | 139.5 | 33.4 | 20.3 | 44.9 | 7.2 |  |  | 115.3 | 76.5 | 51.5 | 158.6 | 74.2 | 47 | 155.6
4595.3 | 2895.3 | -6.7 | 0 | 0 | 112.4 | 110.2 | 106.5 | 105.7 | 139.4 | 33.4 | 20.3 | 44.9 | 6.1 |  |  | 114.5 | 76.1 | 51.3 | 158.2 | 74.3 | 46.9 | 155.1
4596.3 | 2896.3 | -6.7 | 0 | 0 | 112.4 | 110.2 | 106.3 | 105.6 | 139.2 | 33.5 | 20.3 | 44.9 | 6.4 |  |  | 113.8 | 76.3 | 51.1 | 157.9 | 74.4 | 46.8 | 154.6
4597.3 | 2897.3 | -6.7 | 0 | 0 | 112.3 | 110.2 | 106.2 | 105.6 | 139 | 33.6 | 20.3 | 44.9 | 5 |  |  | 113.9 | 75.9 | 51 | 157.5 | 74.4 | 46.7 | 154.1
4598.3 | 2898.3 | -6.7 | 0 | 0 | 112.2 | 110.1 | 106.1 | 105.5 | 138.9 | 33.8 | 20.3 | 44.9 | 4.7 |  |  | 113.4 | 75.2 | 50.8 | 157.1 | 74.2 | 46.6 | 153.8
4599.3 | 2899.3 | -6.7 | 0 | 0 | 112.1 | 109.9 | 106 | 105.3 | 138.7 | 33.8 | 20.3 | 44.9 | 6.1 |  |  | 112.2 | 74.2 | 50.7 | 156.8 | 74.4 | 46.5 | 153.9
4600.3 | 2900.3 | -6.7 | 0 | 0 | 111.9 | 109.7 | 105.9 | 105.1 | 138.5 | 33.9 | 20.3 | 44.8 | 6.8 |  |  | 111.2 | 73.4 | 50.5 | 156.4 | 74.3 | 46.5 | 153.8
4601.3 | 2901.3 | -6.7 | 0 | 0 | 111.7 | 109.5 | 105.7 | 104.9 | 138.2 | 33.7 | 20.3 | 44.7 | 6.1 |  |  | 111 | 72.9 | 50.4 | 156.1 | 73.9 | 46.4 | 153.1
4602.3 | 2902.3 | -6.7 | 0 | 0 | 111.5 | 109.3 | 105.5 | 104.8 | 138 | 33.6 | 20.3 | 44.5 | 6.8 |  |  | 110.7 | 72.6 | 50.2 | 155.7 | 73.6 | 46.4 | 152
4603.3 | 2903.3 | -6.7 | 0 | 0 | 111.3 | 109 | 105.4 | 104.7 | 137.8 | 33.6 | 20.3 | 44.4 | 6.1 |  |  | 110.3 | 72.1 | 50.1 | 155.4 | 73.3 | 46.3 | 151.3
4604.3 | 2904.3 | -6.7 | 0 | 0 | 111.1 | 108.8 | 105.2 | 104.6 | 137.6 | 33.8 | 20.3 | 44.3 | 5.5 |  |  | 110 | 71.8 | 49.9 | 155 | 73 | 46.3 | 151.1
4605.3 | 2905.3 | -6.7 | 0 | 0 | 111.1 | 108.6 | 105 | 104.6 | 137.4 | 33.7 | 20.3 | 44.3 | 5.4 |  |  | 109.6 | 71.2 | 49.9 | 154.6 | 72.7 | 46.3 | 150.8
4606.3 | 2906.3 | -6.7 | 0 | 0 | 111.1 | 108.4 | 104.8 | 104.6 | 137.3 | 33.4 | 20.3 | 44.3 | 5.6 |  |  | 108.3 | 70.6 | 49.7 | 154.3 | 72.7 | 46.3 | 150.1
4607.3 | 2907.3 | -6.7 | 0 | 0 | 111 | 108.2 | 104.6 | 104.5 | 137.1 | 33.3 | 20.3 | 44.2 | 4.9 |  |  | 106.3 | 69.8 | 49.6 | 153.9 | 72.6 | 46.4 | 149.4
4608.3 | 2908.3 | -6.7 | 0 | 0 | 111 | 108 | 104.4 | 104.4 | 137 | 33.2 | 20.3 | 44.2 | 4.3 |  |  | 104.9 | 69.4 | 49.4 | 153.5 | 72.5 | 46.3 | 149.2
4609.3 | 2909.3 | -6.7 | 0 | 0 | 111 | 107.9 | 104.3 | 104.3 | 136.9 | 33.2 | 20.3 | 44.2 | 5.4 |  |  | 105.2 | 69.9 | 49.4 | 153.1 | 72.2 | 46.3 | 148.8
4610.3 | 2910.3 | -6.7 | 0 | 0 | 110.9 | 107.7 | 104.4 | 104.2 | 136.8 | 33.2 | 20.3 | 44.3 | 6.3 |  |  | 105.6 | 70.6 | 49.3 | 152.8 | 72.3 | 46.2 | 148.2
4611.3 | 2911.3 | -6.7 | 0 | 0 | 110.8 | 107.6 | 104.3 | 104.1 | 136.8 | 33.3 | 20.3 | 44.2 | 6.8 |  |  | 106 | 71.2 | 49.1 | 152.5 | 72.4 | 46.1 | 147.8
4612.3 | 2912.3 | -6.7 | 0 | 0 | 110.7 | 107.5 | 104.1 | 104 | 136.7 | 33.2 | 20.3 | 44.2 | 5.1 |  |  | 106.7 | 71.9 | 49.1 | 152.1 | 72.3 | 46 | 147.2
4613.3 | 2913.3 | -6.7 | 0 | 0 | 110.6 | 107.5 | 103.9 | 103.8 | 136.6 | 33.2 | 20.3 | 44.1 | 4.9 |  |  | 107.7 | 72.3 | 49 | 151.7 | 72.5 | 45.9 | 146.8
4614.3 | 2914.3 | -6.7 | 0 | 0 | 110.6 | 107.4 | 103.8 | 103.7 | 136.5 | 33.2 | 20.3 | 44 | 4.1 |  |  | 108.1 | 72.6 | 49 | 151.4 | 72.5 | 45.8 | 146.6
4615.3 | 2915.3 | -6.7 | 0 | 0 | 110.6 | 107.4 | 103.6 | 103.5 | 136.4 | 33.2 | 20.4 | 44 | 4.9 |  |  | 108.4 | 73.1 | 48.9 | 151 | 72.6 | 45.6 | 146.3
4616.3 | 2916.3 | -6.7 | 0 | 0 | 110.5 | 107.3 | 103.5 | 103.4 | 136.2 | 33.2 | 20.4 | 43.9 | 5.3 |  |  | 108.7 | 73.2 | 48.8 | 150.7 | 72.6 | 45.5 | 145.9
4617.3 | 2917.3 | -6.7 | 0 | 0 | 110.4 | 107.1 | 103.3 | 103.2 | 136.1 | 33 | 20.4 | 43.8 | 5.2 |  |  | 109.1 | 73.6 | 48.8 | 150.4 | 72.7 | 45.4 | 145.5
4618.3 | 2918.3 | -6.7 | 0 | 0 | 110.3 | 107 | 103.3 | 103.1 | 136 | 33 | 20.4 | 43.8 | 5.1 |  |  | 109.2 | 74 | 48.8 | 150 | 72.8 | 45.3 | 145
4619.3 | 2919.3 | -6.7 | 0 | 0 | 110.1 | 106.9 | 103.1 | 102.9 | 135.8 | 33 | 20.4 | 43.8 | 4.3 |  |  | 109.6 | 74.3 | 48.7 | 149.7 | 72.7 | 45.2 | 144.3
4620.3 | 2920.3 | -6.7 | 0 | 0 | 109.8 | 106.7 | 103 | 102.7 | 135.7 | 33.2 | 20.4 | 43.7 | 3.6 |  |  | 109.9 | 74.6 | 48.6 | 149.3 | 72.5 | 45.1 | 143.8
4621.3 | 2921.3 | -6.7 | 0 | 0 | 109.6 | 106.5 | 103 | 102.6 | 135.6 | 33.4 | 20.4 | 43.8 | 3.4 |  |  | 110 | 74.6 | 48.5 | 149 | 72.1 | 44.9 | 143.3
4622.3 | 2922.3 | -6.7 | 0 | 0 | 109.4 | 106.3 | 102.9 | 102.4 | 135.5 | 33.5 | 20.4 | 43.8 | 3.6 |  |  | 109 | 73.9 | 48.3 | 148.7 | 71.9 | 44.8 | 142.8
4623.3 | 2923.3 | -6.7 | 0 | 0 | 109.2 | 106.1 | 102.9 | 102.3 | 135.3 | 33.5 | 20.4 | 43.8 | 3.6 |  |  | 107.9 | 73.3 | 48.2 | 148.4 | 71.6 | 44.7 | 142.4
4624.3 | 2924.3 | -6.7 | 0 | 0 | 109 | 106 | 102.7 | 102.2 | 135.2 | 33.3 | 20.4 | 43.7 | 4 |  |  | 106.6 | 72.9 | 48 | 148 | 71.5 | 44.6 | 142.3
4625.3 | 2925.3 | -6.7 | 0 | 0 | 108.5 | 105.8 | 102.5 | 102.2 | 135.1 | 33.2 | 20.4 | 43.6 | 4.1 |  |  | 104.6 | 72.2 | 48 | 147.7 | 71.4 | 44.5 | 142.2
4626.3 | 2926.3 | -6.7 | 0 | 0 | 108.1 | 105.7 | 102.3 | 102.2 | 134.9 | 33.1 | 20.4 | 43.5 | 4.6 |  |  | 103.5 | 71.7 | 48.3 | 147.3 | 71.2 | 44.5 | 142.2
4627.3 | 2927.3 | -6.7 | 0 | 0 | 107.8 | 105.6 | 102.2 | 102.1 | 134.7 | 33 | 20.4 | 43.4 | 4.7 |  |  | 102.7 | 71.1 | 48.3 | 147 | 71.2 | 44.4 | 141.9
4628.3 | 2928.3 | -6.6 | 0 | 0 | 107.5 | 105.5 | 102.1 | 102.1 | 134.6 | 33.1 | 20.4 | 43.3 | 4.5 |  |  | 102 | 70.5 | 48.1 | 146.7 | 71.1 | 44.4 | 141.6
4629.3 | 2929.3 | -6.6 | 0 | 0 | 107.4 | 105.2 | 102.1 | 102.1 | 134.5 | 33.2 | 20.4 | 43.2 | 3.6 |  |  | 101.2 | 69.6 | 48 | 146.4 | 71 | 44.3 | 141.3
4630.3 | 2930.3 | -6.6 | 0 | 0 | 107.3 | 105 | 102 | 102 | 134.4 | 33.3 | 20.4 | 43.2 | 3.7 |  |  | 100 | 68.8 | 47.8 | 146 | 70.8 | 44.3 | 140.6
4631.3 | 2931.3 | -6.6 | 0 | 0 | 107 | 104.9 | 101.9 | 101.8 | 134.3 | 33.4 | 20.4 | 43.2 | 4.3 |  |  | 99 | 68.4 | 47.6 | 145.7 | 70.7 | 44.2 | 140.2
4632.3 | 2932.3 | -6.6 | 0 | 0 | 106.6 | 104.8 | 101.9 | 101.7 | 134.1 | 33.4 | 20.4 | 43.2 | 4.4 |  |  | 98.3 | 68.4 | 47.6 | 145.4 | 70.5 | 44.1 | 139.9
4633.3 | 2933.3 | -6.7 | 0 | 0 | 106.3 | 104.7 | 101.8 | 101.6 | 134 | 33.4 | 20.4 | 43.2 | 3.9 |  |  | 97.5 | 68.6 | 48 | 145 | 70.6 | 44.1 | 140
4634.3 | 2934.3 | -6.7 | 0 | 0 | 106.2 | 104.6 | 101.6 | 101.6 | 133.8 | 33.4 | 20.4 | 43.1 | 4 |  |  | 97 | 68.9 | 48.2 | 144.7 | 70.6 | 44.1 | 139.7
4635.3 | 2935.3 | -6.7 | 0 | 0 | 106.3 | 104.5 | 101.5 | 101.5 | 133.6 | 33.4 | 20.4 | 43.1 | 4.7 |  |  | 96.7 | 69.6 | 48.2 | 144.4 | 70.8 | 44 | 138.9
4636.3 | 2936.3 | -6.7 | 0 | 0 | 106.4 | 104.3 | 101.5 | 101.4 | 133.4 | 33.5 | 20.4 | 43.1 | 5.4 |  |  | 96.4 | 70 | 48.3 | 144 | 70.7 | 43.9 | 138.2
4637.3 | 2937.3 | -6.7 | 0 | 0 | 106.4 | 104.1 | 101.5 | 101.3 | 133.2 | 33.5 | 20.4 | 43.1 | 5 |  |  | 95.8 | 70.2 | 48.4 | 143.7 | 70.8 | 43.9 | 137.6
4638.3 | 2938.3 | -6.7 | 0 | 0 | 106.5 | 103.8 | 101.5 | 101.1 | 133 | 33.5 | 20.4 | 43.1 | 4.3 |  |  | 95.6 | 70.7 | 48.5 | 143.4 | 70.5 | 43.8 | 137.2
4639.3 | 2939.3 | -6.7 | 0 | 0 | 106.5 | 103.7 | 101.5 | 101 | 132.9 | 33.5 | 20.4 | 43.1 | 4.2 |  |  | 95.5 | 71 | 48.6 | 143.1 | 70.5 | 43.7 | 136.8
4640.3 | 2940.3 | -6.7 | 0 | 0 | 106.3 | 103.6 | 101.5 | 100.9 | 132.7 | 33.5 | 20.4 | 43.2 | 4.4 |  |  | 94.8 | 71 | 49.2 | 142.7 | 70.5 | 43.6 | 136.6
4641.3 | 2941.3 | -6.7 | 0 | 0 | 106.2 | 103.5 | 101.5 | 100.8 | 132.5 | 33.3 | 20.4 | 43.2 | 5 |  |  | 94.4 | 71.2 | 49 | 142.4 | 70.4 | 43.6 | 136.2
4642.3 | 2942.3 | -6.7 | 0 | 0 | 106.1 | 103.4 | 101.3 | 100.7 | 132.3 | 33.1 | 20.4 | 43.1 | 4.1 |  |  | 94 | 71.7 | 48.7 | 142.1 | 70.1 | 43.5 | 135.9
4643.3 | 2943.3 | -6.7 | 0 | 0 | 106.1 | 103.2 | 101.1 | 100.7 | 132.2 | 33 | 20.4 | 43.1 | 3.7 |  |  | 93.4 | 71.9 | 48.5 | 141.8 | 70.2 | 43.5 | 135.4
4644.3 | 2944.3 | -6.7 | 0 | 0 | 106.1 | 103 | 100.9 | 100.5 | 132 | 33.1 | 20.4 | 43 | 3.3 |  |  | 92.9 | 72.4 | 48.2 | 141.5 | 70.5 | 43.4 | 135
4645.3 | 2945.3 | -6.7 | 0 | 0 | 106 | 102.9 | 100.6 | 100.3 | 131.9 | 33.3 | 20.4 | 42.9 | 3.3 |  |  | 92.4 | 73 | 47.9 | 141.1 | 70.6 | 43.4 | 134.5
4646.3 | 2946.3 | -6.7 | 0 | 0 | 105.9 | 102.9 | 100.5 | 100.2 | 131.8 | 33.2 | 20.4 | 42.9 | 3.2 |  |  | 91.9 | 73.4 | 47.7 | 140.8 | 70.5 | 43.3 | 134.2
4647.3 | 2947.3 | -6.6 | 0 | 0 | 105.8 | 102.8 | 100.3 | 100 | 131.7 | 33 | 20.4 | 42.9 | 3.2 |  |  | 91.4 | 73.8 | 47.4 | 140.5 | 70.3 | 43.2 | 133.8
4648.3 | 2948.3 | -6.6 | 0 | 0 | 105.6 | 102.8 | 100.2 | 99.7 | 131.6 | 32.9 | 20.4 | 42.8 | 3.2 |  |  | 91 | 74.4 | 47.1 | 140.2 | 70.1 | 43 | 133.5
4649.3 | 2949.3 | -6.6 | 0 | 0 | 105.3 | 102.8 | 100 | 99.6 | 131.5 | 32.9 | 20.4 | 42.7 | 3.1 |  |  | 90.7 | 74.8 | 46.9 | 139.9 | 70.1 | 42.9 | 133
4650.3 | 2950.3 | -6.6 | 0 | 0 | 104.8 | 102.8 | 99.8 | 99.5 | 131.4 | 32.9 | 20.4 | 42.5 | 2.9 |  |  | 90.2 | 75.1 | 46.7 | 139.6 | 69.8 | 42.9 | 132.5
4651.3 | 2951.3 | -6.6 | 0 | 0 | 104.3 | 102.7 | 99.7 | 99.4 | 131.3 | 32.9 | 20.4 | 42.4 | 3.3 |  |  | 90.2 | 74.8 | 46.6 | 139.3 | 69.5 | 42.9 | 132
4652.3 | 2952.3 | -6.6 | 0 | 0 | 103.9 | 102.7 | 99.6 | 99.3 | 131.2 | 32.8 | 20.4 | 42.4 | 3.2 |  |  | 89.9 | 74.1 | 46.5 | 138.9 | 69.1 | 42.8 | 131.6
4653.3 | 2953.3 | -6.6 | 0 | 0 | 103.6 | 102.7 | 99.4 | 99.1 | 131.1 | 32.9 | 20.4 | 42.5 | 2.9 |  |  | 90.2 | 73.6 | 46.5 | 138.6 | 69.1 | 42.8 | 131.2
4654.3 | 2954.3 | -6.6 | 0 | 0 | 103.3 | 102.5 | 99.2 | 99 | 131 | 33 | 20.4 | 42.5 | 2.9 |  |  | 91.1 | 73.3 | 46.4 | 138.3 | 69.2 | 42.8 | 130.8
4655.3 | 2955.3 | -6.6 | 0 | 0 | 102.9 | 102.4 | 99.1 | 98.8 | 130.8 | 33 | 20.4 | 42.6 | 2.8 |  |  | 91.7 | 73.3 | 46.3 | 138 | 69.2 | 42.7 | 130.5
4656.3 | 2956.3 | -6.6 | 0 | 0 | 102.5 | 102.3 | 99.1 | 98.8 | 130.7 | 33 | 20.4 | 42.7 | 3.1 |  |  | 91.9 | 73.2 | 46.2 | 137.7 | 69 | 42.6 | 130.2
4657.3 | 2957.3 | -6.6 | 0 | 0 | 102.3 | 102.2 | 99.2 | 98.9 | 130.5 | 33 | 20.4 | 42.7 | 3.2 |  |  | 92.9 | 73.1 | 46.1 | 137.4 | 69 | 42.5 | 129.6
4658.3 | 2958.3 | -6.6 | 0 | 0 | 102.4 | 102.1 | 99.2 | 98.9 | 130.4 | 32.8 | 20.4 | 42.7 | 3.3 |  |  | 93.5 | 72.7 | 46 | 137.1 | 68.9 | 42.5 | 129.2
4659.3 | 2959.3 | -6.6 | 0 | 0 | 102.5 | 102.1 | 99.1 | 98.7 | 130.3 | 32.8 | 20.4 | 42.6 | 3.3 |  |  | 93.6 | 72.5 | 45.9 | 136.8 | 68.8 | 42.4 | 129
4660.3 | 2960.3 | -6.7 | 0 | 0 | 102.6 | 101.9 | 98.9 | 98.5 | 130.2 | 32.7 | 20.4 | 42.6 | 3.7 |  |  | 94 | 72.7 | 45.9 | 136.5 | 68.7 | 42.4 | 128.9
4661.3 | 2961.3 | -6.6 | 0 | 0 | 102.5 | 101.8 | 98.7 | 98.5 | 130.1 | 32.6 | 20.4 | 42.6 | 3.8 |  |  | 94.2 | 72.7 | 45.8 | 136.2 | 68.5 | 42.3 | 128.5
4662.3 | 2962.3 | -6.6 | 0 | 0 | 102.2 | 101.6 | 98.6 | 98.5 | 130 | 32.5 | 20.4 | 42.6 | 3.9 |  |  | 94.3 | 72.6 | 45.6 | 136 | 68.4 | 42.2 | 128
4663.3 | 2963.3 | -6.6 | 0 | 0 | 102 | 101.5 | 98.5 | 98.5 | 130 | 32.4 | 20.4 | 42.5 | 4 |  |  | 93.8 | 72.3 | 45.5 | 135.7 | 68.4 | 42.1 | 127.7
4664.3 | 2964.3 | -6.6 | 0 | 0 | 101.9 | 101.5 | 98.4 | 98.5 | 129.9 | 32.3 | 20.4 | 42.5 | 4 |  |  | 93 | 72 | 45.3 | 135.4 | 68.4 | 42.1 | 127.5
4665.3 | 2965.3 | -6.6 | 0 | 0 | 101.8 | 101.5 | 98.4 | 98.3 | 129.8 | 32.4 | 20.4 | 42.5 | 3.8 |  |  | 92.3 | 71.9 | 45.2 | 135.1 | 68.3 | 42 | 127.2
4666.3 | 2966.3 | -6.6 | 0 | 0 | 101.8 | 101.5 | 98.5 | 98.1 | 129.7 | 32.4 | 20.5 | 42.6 | 4 |  |  | 91.7 | 71.9 | 45.2 | 134.8 | 68 | 42 | 127
4667.3 | 2967.3 | -6.6 | 0 | 0 | 102 | 101.4 | 98.5 | 98 | 129.5 | 32.5 | 20.5 | 42.6 | 4 |  |  | 91.2 | 72 | 45.2 | 134.5 | 67.7 | 42 | 126.8
4668.3 | 2968.3 | -6.6 | 0 | 0 | 102.1 | 101.3 | 98.3 | 98 | 129.4 | 32.4 | 20.5 | 42.6 | 4.6 |  |  | 90.8 | 72.2 | 45.1 | 134.2 | 67.3 | 41.9 | 126.5
4669.3 | 2969.3 | -6.6 | 0 | 0 | 102.1 | 101.2 | 98.2 | 98 | 129.3 | 32.4 | 20.5 | 42.6 | 5.3 |  |  | 90.4 | 71.9 | 45 | 134 | 67.1 | 41.9 | 126.2
4670.3 | 2970.3 | -6.6 | 0 | 0 | 102.2 | 101.2 | 98.1 | 97.9 | 129.2 | 32.4 | 20.5 | 42.5 | 5.5 |  |  | 89.6 | 71.3 | 45.4 | 133.7 | 66.8 | 41.9 | 126.1
4671.3 | 2971.3 | -6.6 | 0 | 0 | 102.3 | 101.1 | 98 | 97.7 | 129.1 | 32.3 | 20.5 | 42.5 | 4.5 |  |  | 89.4 | 70.9 | 46.2 | 133.4 | 66.6 | 41.9 | 126.1
4672.3 | 2972.3 | -6.7 | 0 | 0 | 102.3 | 101 | 97.8 | 97.5 | 129 | 32.4 | 20.5 | 42.4 | 4.5 |  |  | 89.5 | 70.7 | 46.5 | 133.1 | 66.7 | 42 | 126.2
4673.3 | 2973.3 | -6.7 | 0 | 0 | 102.2 | 100.9 | 97.6 | 97.3 | 128.9 | 32.5 | 20.5 | 42.5 | 4.6 |  |  | 89.3 | 70.6 | 46.8 | 132.9 | 66.8 | 41.9 | 126.1
4674.3 | 2974.3 | -6.7 | 0 | 0 | 102.2 | 100.8 | 97.5 | 97.2 | 128.7 | 32.6 | 20.5 | 42.5 | 4.2 |  |  | 89 | 70.4 | 47.5 | 132.6 | 67 | 41.8 | 125.8
4675.3 | 2975.3 | -6.7 | 0 | 0 | 102.1 | 100.7 | 97.5 | 97.1 | 128.6 | 32.6 | 20.5 | 42.4 | 3.5 |  |  | 88.8 | 70.4 | 47.9 | 132.3 | 66.5 | 41.8 | 125.4
4676.3 | 2976.3 | -6.7 | 0 | 0 | 102.1 | 100.6 | 97.5 | 97 | 128.5 | 32.7 | 20.5 | 42.4 | 3 |  |  | 88.6 | 70.3 | 48.5 | 132.1 | 66.5 | 41.8 | 125.1
4677.3 | 2977.3 | -6.7 | 0 | 0 | 102.2 | 100.5 | 97.5 | 97 | 128.4 | 32.9 | 20.5 | 42.4 | 3.3 |  |  | 88.1 | 70 | 48.9 | 131.8 | 66.8 | 41.8 | 124.8
4678.3 | 2978.3 | -6.6 | 0 | 0 | 102.2 | 100.4 | 97.4 | 97 | 128.3 | 33 | 20.5 | 42.3 | 4 |  |  | 87.4 | 69.6 | 49 | 131.6 | 66.6 | 41.7 | 124.4
4679.3 | 2979.3 | -6.6 | 0 | 0 | 102 | 100.4 | 97.3 | 96.9 | 128.2 | 33.1 | 20.5 | 42.2 | 3.8 |  |  | 87.1 | 69.4 | 48.8 | 131.3 | 66.6 | 41.7 | 124
4680.3 | 2980.3 | -6.6 | 0 | 0 | 101.6 | 100.4 | 97.3 | 96.8 | 128.1 | 33.2 | 20.5 | 42.2 | 4.7 |  |  | 86.8 | 68.9 | 48.5 | 131 | 66.7 | 41.7 | 123.4
4681.3 | 2981.3 | -6.6 | 0 | 0 | 101.3 | 100.4 | 97.3 | 96.6 | 128 | 33.1 | 20.5 | 42.1 | 5.8 |  |  | 86.6 | 68.9 | 48.3 | 130.8 | 66.6 | 41.6 | 122.8
4682.3 | 2982.3 | -6.6 | 0 | 0 | 101.2 | 100.2 | 97.2 | 96.5 | 127.9 | 33 | 20.5 | 42 | 5.6 |  |  | 86.6 | 68.8 | 48 | 130.5 | 66.6 | 41.6 | 122.3
4683.3 | 2983.3 | -6.6 | 0 | 0 | 101.2 | 100.1 | 97.1 | 96.4 | 127.8 | 32.8 | 20.5 | 42 | 4.6 |  |  | 86.8 | 68.7 | 47.7 | 130.3 | 66.2 | 41.6 | 122.2
4684.3 | 2984.3 | -6.6 | 0 | 0 | 101 | 100 | 97.2 | 96.3 | 127.6 | 32.6 | 20.5 | 42 | 4.2 |  |  | 87.2 | 68.5 | 47.5 | 130 | 66 | 41.6 | 121.6
4685.3 | 2985.3 | -6.7 | 0 | 0 | 100.8 | 99.8 | 97.2 | 96.2 | 127.5 | 32.5 | 20.5 | 41.9 | 3.8 |  |  | 87.8 | 68.6 | 47.2 | 129.8 | 65.8 | 41.5 | 121
4686.3 | 2986.3 | -6.7 | 0 | 0 | 100.8 | 99.7 | 97.2 | 96.2 | 127.4 | 32.5 | 20.5 | 41.8 | 3 |  |  | 87.4 | 68.1 | 47 | 129.5 | 65.4 | 41.6 | 120.5
4687.3 | 2987.3 | -6.7 | 0 | 0 | 100.8 | 99.6 | 97.1 | 96.1 | 127.2 | 32.6 | 20.5 | 41.8 | 2.7 |  |  | 86.5 | 67.8 | 46.8 | 129.2 | 65.2 | 41.6 | 120.2
4688.3 | 2988.3 | -6.7 | 0 | 0 | 100.6 | 99.5 | 97 | 96.1 | 127.1 | 32.6 | 20.5 | 41.8 | 3.8 |  |  | 87 | 67.7 | 46.6 | 129 | 64.8 | 41.6 | 119.8
4689.3 | 2989.3 | -6.7 | 0 | 0 | 100.2 | 99.4 | 96.8 | 96 | 126.9 | 32.7 | 20.5 | 41.7 | 4.6 |  |  | 87.5 | 67.5 | 46.4 | 128.7 | 64.6 | 41.6 | 119.6
4690.3 | 2990.3 | -6.6 | 0 | 0 | 99.7 | 99.4 | 96.6 | 96 | 126.8 | 32.8 | 20.5 | 41.7 | 4.1 |  |  | 87.6 | 67.2 | 46.2 | 128.5 | 64 | 41.6 | 118.9
4691.3 | 2991.3 | -6.6 | 0 | 0 | 99.5 | 99.3 | 96.4 | 95.9 | 126.7 | 33 | 20.5 | 41.7 | 3.3 |  |  | 87.9 | 67.1 | 45.9 | 128.2 | 63.5 | 41.5 | 118.3
4692.3 | 2992.3 | -6.6 | 0 | 0 | 99.3 | 99.3 | 96.3 | 95.8 | 126.5 | 33.1 | 20.5 | 41.7 | 3 |  |  | 88.5 | 67.1 | 45.7 | 127.9 | 63 | 41.4 | 118
4693.3 | 2993.3 | -6.6 | 0 | 0 | 99.2 | 99.3 | 96.2 | 95.7 | 126.4 | 33.2 | 20.5 | 41.7 | 2.5 |  |  | 88.9 | 67.1 | 45.5 | 127.7 | 62.7 | 41.4 | 117.9
4694.3 | 2994.3 | -6.6 | 0 | 0 | 99.3 | 99.3 | 96.2 | 95.5 | 126.3 | 33.2 | 20.5 | 41.6 | 2.8 |  |  | 89.2 | 66.9 | 45.3 | 127.4 | 62.3 | 41.3 | 117.7
4695.3 | 2995.3 | -6.6 | 0 | 0 | 99.4 | 99.3 | 96.1 | 95.4 | 126.2 | 33.1 | 20.5 | 41.6 | 3.3 |  |  | 88.6 | 66.3 | 45.2 | 127.1 | 61.9 | 41.2 | 117.3
4696.3 | 2996.3 | -6.6 | 0 | 0 | 99.4 | 99.3 | 96 | 95.4 | 126.1 | 32.8 | 20.5 | 41.5 | 4.2 |  |  | 88.7 | 66 | 45 | 126.9 | 61.6 | 41.2 | 117.2
4697.3 | 2997.3 | -6.6 | 0 | 0 | 99.2 | 99.2 | 95.8 | 95.3 | 126 | 32.6 | 20.5 | 41.4 | 5.4 |  |  | 89.2 | 66 | 44.9 | 126.6 | 61.4 | 41.1 | 117.2
4698.3 | 2998.3 | -6.6 | 0 | 0 | 98.9 | 99.1 | 95.7 | 95.2 | 125.9 | 32.4 | 20.5 | 41.3 | 5.3 |  |  | 90.1 | 66.1 | 44.8 | 126.3 | 61.2 | 41 | 117.1
4699.3 | 2999.3 | -6.6 | 0 | 0 | 98.7 | 98.9 | 95.6 | 95.1 | 125.8 | 32.3 | 20.5 | 41.3 | 4.5 |  |  | 90.6 | 66.3 | 44.7 | 126 | 60.7 | 41 | 116.8
4700.3 | 3000.3 | -6.6 | 0 | 0 | 98.6 | 98.7 | 95.6 | 95 | 125.7 | 32.3 | 20.5 | 41.2 | 3.4 |  |  | 90.6 | 66.1 | 44.5 | 125.8 | 60.4 | 41 | 116.5
4701.3 | 3001.3 | -6.6 | 0 | 0 | 98.5 | 98.5 | 95.5 | 95 | 125.7 | 32.4 | 20.5 | 41.3 | 4 |  |  | 90.8 | 65.8 | 44.4 | 125.5 | 60.1 | 40.9 | 116.5
4702.3 | 3002.3 | -6.6 | 0 | 0 | 98.2 | 98.3 | 95.4 | 94.9 | 125.6 | 32.4 | 20.5 | 41.2 | 4.3 |  |  | 90.8 | 65.7 | 44.3 | 125.3 | 60 | 40.9 | 116.3
4703.3 | 3003.3 | -6.6 | 0 | 0 | 97.7 | 98.1 | 95.3 | 94.8 | 125.5 | 32.3 | 20.5 | 41.2 | 4.9 |  |  | 90.3 | 65.3 | 44.1 | 125 | 59.9 | 40.8 | 116
4704.3 | 3004.3 | -6.6 | 0 | 0 | 97.3 | 98 | 95.1 | 94.7 | 125.3 | 32.3 | 20.5 | 41.1 | 4.5 |  |  | 90.5 | 65.4 | 44.1 | 124.7 | 59.9 | 40.7 | 115.6
4705.3 | 3005.3 | -6.6 | 0 | 0 | 97 | 97.8 | 95 | 94.6 | 125.2 | 32.4 | 20.6 | 41.1 | 3.9 |  |  | 90.9 | 65.2 | 43.9 | 124.5 | 59.6 | 40.6 | 115.3
4706.3 | 3006.3 | -6.6 | 0 | 0 | 97 | 97.7 | 94.9 | 94.6 | 125.1 | 32.3 | 20.6 | 41 | 3.9 |  |  | 90.8 | 65.2 | 43.8 | 124.2 | 59.6 | 40.6 | 114.9
4707.3 | 3007.3 | -6.6 | 0 | 0 | 97 | 97.6 | 94.8 | 94.6 | 125 | 32.3 | 20.6 | 41 | 4.5 |  |  | 90.9 | 65 | 43.7 | 124 | 59.7 | 40.5 | 114.7
4708.3 | 3008.3 | -6.6 | 0 | 0 | 97.3 | 97.5 | 94.6 | 94.5 | 124.9 | 32.3 | 20.6 | 41 | 5.3 |  |  | 91.3 | 64.9 | 43.6 | 123.7 | 59.9 | 40.5 | 114.7
4709.3 | 3009.3 | -6.6 | 0 | 0 | 97.5 | 97.4 | 94.4 | 94.5 | 124.8 | 32.4 | 20.6 | 40.9 | 5 |  |  | 91.6 | 64.7 | 43.6 | 123.5 | 59.7 | 40.5 | 114.2
4710.3 | 3010.3 | -6.6 | 0 | 0 | 97.6 | 97.4 | 94.3 | 94.4 | 124.7 | 32.5 | 20.6 | 40.8 | 4.3 |  |  | 91.9 | 64.5 | 43.6 | 123.2 | 59.8 | 40.4 | 113.8
4711.3 | 3011.3 | -6.6 | 0 | 0 | 97.6 | 97.3 | 94.1 | 94.3 | 124.6 | 32.5 | 20.6 | 40.8 | 4.4 |  |  | 92.6 | 64.3 | 43.6 | 123 | 59.9 | 40.4 | 113.6
4712.3 | 3012.3 | -6.6 | 0 | 0 | 97.6 | 97.3 | 94 | 94.3 | 124.6 | 32.5 | 20.6 | 40.7 | 5.1 |  |  | 93.2 | 64.2 | 43.5 | 122.7 | 59.7 | 40.3 | 113.2
4713.3 | 3013.3 | -6.6 | 0 | 0 | 97.8 | 97.2 | 93.8 | 94.2 | 124.5 | 32.5 | 20.6 | 40.6 | 4.7 |  |  | 93.8 | 64 | 43.4 | 122.5 | 59.7 | 40.2 | 112.9
4714.3 | 3014.3 | -6.6 | 0 | 0 | 97.8 | 97.2 | 93.7 | 94 | 124.4 | 32.5 | 20.6 | 40.5 | 4.5 |  |  | 94 | 64.1 | 43.3 | 122.2 | 59.6 | 40.1 | 112.9
4715.3 | 3015.3 | -6.6 | 0 | 0 | 97.9 | 97.1 | 93.6 | 93.9 | 124.3 | 32.5 | 20.6 | 40.4 | 5.2 |  |  | 94.3 | 64.2 | 43.3 | 122 | 59.5 | 40 | 112.7
4716.3 | 3016.3 | -6.6 | 0 | 0 | 98 | 97 | 93.5 | 93.7 | 124.2 | 32.4 | 20.6 | 40.4 | 6.3 |  |  | 94.8 | 64 | 43.2 | 121.8 | 59.3 | 40 | 112.3
4717.3 | 3017.3 | -6.6 | 0 | 0 | 98.1 | 96.9 | 93.4 | 93.6 | 124 | 32.3 | 20.6 | 40.3 | 5.7 |  |  | 94.7 | 63.8 | 43 | 121.5 | 59.1 | 39.9 | 111.8
4718.3 | 3018.3 | -6.6 | 0 | 0 | 97.8 | 96.8 | 93.5 | 93.6 | 123.9 | 32.3 | 20.6 | 40.3 | 5.3 |  |  | 94.9 | 63.8 | 43 | 121.2 | 59.2 | 39.8 | 111.7
4719.3 | 3019.3 | -6.7 | 0 | 0 | 97.5 | 96.7 | 93.5 | 93.4 | 123.8 | 32.3 | 20.6 | 40.2 | 4.8 |  |  | 94.7 | 63.6 | 43 | 121 | 59 | 39.8 | 111.2
4720.3 | 3020.3 | -6.7 | 0 | 0 | 97.4 | 96.5 | 93.5 | 93.3 | 123.7 | 32.2 | 20.6 | 40.1 | 4.8 |  |  | 93.7 | 63.3 | 42.9 | 120.8 | 58.5 | 39.9 | 110.4
4721.3 | 3021.3 | -6.7 | 0 | 0 | 97.4 | 96.4 | 93.5 | 93.1 | 123.6 | 32.2 | 20.6 | 40 | 3.6 |  |  | 93 | 63 | 42.8 | 120.6 | 58.1 | 39.9 | 110
4722.3 | 3022.3 | -6.7 | 0 | 0 | 97.4 | 96.3 | 93.4 | 93.1 | 123.5 | 32.3 | 20.6 | 39.8 | 3.6 |  |  | 91.7 | 62.7 | 42.6 | 120.4 | 57.7 | 39.8 | 109.8
4723.3 | 3023.3 | -6.7 | 0 | 0 | 97.2 | 96.2 | 93.3 | 93 | 123.4 | 32.3 | 20.6 | 39.8 | 3.3 |  |  | 91.1 | 62.4 | 42.5 | 120.1 | 57.4 | 39.8 | 109.7
4724.3 | 3024.3 | -6.7 | 0 | 0 | 96.9 | 96.1 | 93.3 | 93 | 123.3 | 32.3 | 20.6 | 39.7 | 4.5 |  |  | 91 | 62.4 | 42.4 | 119.9 | 57 | 39.7 | 109.7
4725.3 | 3025.3 | -6.7 | 0 | 0 | 96.7 | 96 | 93.2 | 93 | 123.2 | 32.2 | 20.6 | 39.6 | 5.1 |  |  | 90.6 | 62.5 | 42.4 | 119.6 | 56.9 | 39.7 | 109.8
4726.3 | 3026.3 | -6.7 | 0 | 0 | 96.4 | 96 | 93.1 | 92.9 | 123.2 | 32 | 20.6 | 39.5 | 5 |  |  | 89.7 | 62.1 | 42.3 | 119.4 | 56.7 | 39.6 | 109.4
4727.3 | 3027.3 | -6.6 | 0 | 0 | 96.1 | 95.9 | 93 | 92.9 | 123 | 31.9 | 20.6 | 39.6 | 5.4 |  |  | 88.6 | 61.7 | 42.3 | 119.2 | 56.5 | 39.7 | 108.9
4728.3 | 3028.3 | -6.6 | 0 | 0 | 95.9 | 95.9 | 92.9 | 92.7 | 123 | 31.8 | 20.6 | 39.6 | 4.8 |  |  | 88.3 | 61.5 | 42.3 | 118.9 | 56.4 | 39.9 | 108.3
4729.3 | 3029.3 | -6.6 | 0 | 0 | 95.8 | 95.8 | 92.8 | 92.5 | 122.8 | 31.8 | 20.6 | 39.7 | 4 |  |  | 87.7 | 61.2 | 42.3 | 118.7 | 56.2 | 40 | 108
4730.3 | 3030.3 | -6.6 | 0 | 0 | 95.9 | 95.7 | 92.7 | 92.4 | 122.7 | 31.7 | 20.6 | 39.8 | 3.6 |  |  | 87.1 | 60.9 | 42.3 | 118.4 | 56 | 40 | 108
4731.3 | 3031.3 | -6.6 | 0 | 0 | 95.9 | 95.6 | 92.5 | 92.3 | 122.5 | 31.8 | 20.6 | 39.9 | 3.2 |  |  | 87 | 60.7 | 42.2 | 118.2 | 55.9 | 40.1 | 107.7
4732.3 | 3032.3 | -6.6 | 0 | 0 | 95.9 | 95.5 | 92.4 | 92.2 | 122.4 | 31.9 | 20.6 | 39.9 | 3.4 |  |  | 86.6 | 60.3 | 42.1 | 118 | 55.8 | 40 | 107.5
4733.3 | 3033.3 | -6.6 | 0 | 0 | 95.8 | 95.3 | 92.3 | 92.2 | 122.3 | 32.1 | 20.6 | 39.9 | 3.7 |  |  | 86.9 | 60.4 | 42.1 | 117.7 | 55.7 | 40 | 107.4
4734.3 | 3034.3 | -6.6 | 0 | 0 | 95.7 | 95.1 | 92.2 | 92.1 | 122.2 | 32.1 | 20.6 | 39.9 | 3.7 |  |  | 87.3 | 60.5 | 42.1 | 117.5 | 55.7 | 39.9 | 107.3
4735.3 | 3035.3 | -6.6 | 0 | 0 | 95.7 | 94.9 | 92.1 | 92 | 122.1 | 32.1 | 20.6 | 39.9 | 3.4 |  |  | 87.6 | 60.4 | 42 | 117.2 | 55.5 | 39.8 | 107.1
4736.3 | 3036.3 | -6.7 | 0 | 0 | 95.7 | 94.8 | 92 | 91.9 | 121.9 | 31.9 | 20.6 | 39.9 | 3.5 |  |  | 87.5 | 60.3 | 41.9 | 117 | 55.3 | 39.7 | 106.8
4737.3 | 3037.3 | -6.6 | 0 | 0 | 95.4 | 94.7 | 92 | 91.9 | 121.8 | 31.8 | 20.6 | 39.8 | 3.9 |  |  | 86.9 | 59.9 | 41.9 | 116.8 | 55.2 | 39.7 | 106.6
4738.3 | 3038.3 | -6.6 | 0 | 0 | 95.2 | 94.6 | 92.1 | 91.8 | 121.7 | 31.7 | 20.6 | 39.7 | 3.3 |  |  | 86.8 | 59.7 | 41.9 | 116.5 | 55.2 | 39.6 | 106.4
4739.3 | 3039.3 | -6.6 | 0 | 0 | 95.2 | 94.5 | 92 | 91.8 | 121.7 | 31.6 | 20.7 | 39.7 | 3 |  |  | 86.9 | 59.5 | 41.8 | 116.3 | 54.9 | 39.5 | 106
4740.3 | 3040.3 | -6.6 | 0 | 0 | 95.2 | 94.4 | 91.8 | 91.8 | 121.6 | 31.7 | 20.7 | 39.7 | 2.9 |  |  | 86.6 | 59.2 | 41.7 | 116 | 54.5 | 39.6 | 105.4
4741.3 | 3041.3 | -6.6 | 0 | 0 | 95.2 | 94.3 | 91.7 | 91.6 | 121.5 | 31.7 | 20.7 | 39.7 | 2.9 |  |  | 86.1 | 58.8 | 41.6 | 115.8 | 54.2 | 39.5 | 104.9
4742.3 | 3042.3 | -6.6 | 0 | 0 | 95 | 94.3 | 91.7 | 91.5 | 121.3 | 31.7 | 20.7 | 39.8 | 3.2 |  |  | 85.3 | 58.4 | 41.7 | 115.5 | 53.9 | 39.4 | 104.3
4743.3 | 3043.3 | -6.6 | 0 | 0 | 94.8 | 94.3 | 91.7 | 91.3 | 121.2 | 31.7 | 20.7 | 39.8 | 3.4 |  |  | 84.6 | 58.1 | 41.7 | 115.3 | 53.7 | 39.3 | 104.2
4744.3 | 3044.3 | -6.6 | 0 | 0 | 94.7 | 94.2 | 91.5 | 91.1 | 121.1 | 31.8 | 20.7 | 39.9 | 3.6 |  |  | 83.9 | 57.7 | 41.6 | 115.1 | 53.7 | 39.3 | 103.9
4745.3 | 3045.3 | -6.6 | 0 | 0 | 94.5 | 94.2 | 91.4 | 91.1 | 121 | 31.9 | 20.7 | 39.9 | 3 |  |  | 83.4 | 57.6 | 41.5 | 114.9 | 53.4 | 39.3 | 103.8
4746.3 | 3046.3 | -6.6 | 0 | 0 | 94.1 | 94.1 | 91.3 | 91 | 120.9 | 31.9 | 20.7 | 39.9 | 3.1 |  |  | 83 | 57.4 | 41.5 | 114.6 | 53.1 | 39.2 | 103.5
4747.3 | 3047.3 | -6.6 | 0 | 0 | 93.7 | 94.1 | 91.2 | 90.9 | 120.8 | 32 | 20.7 | 39.9 | 3.1 |  |  | 82.8 | 57.3 | 41.3 | 114.4 | 52.9 | 39.1 | 103
4748.3 | 3048.3 | -6.6 | 0 | 0 | 93.4 | 93.9 | 91.2 | 90.8 | 120.7 | 31.9 | 20.7 | 39.9 | 3 |  |  | 82.8 | 57.2 | 41.3 | 114.1 | 52.8 | 39 | 102.8
4749.3 | 3049.3 | -6.6 | 0 | 0 | 93.1 | 93.7 | 91.2 | 90.8 | 120.6 | 31.9 | 20.7 | 39.9 | 2.8 |  |  | 83 | 57.1 | 41.2 | 113.9 | 52.6 | 39 | 102.7
4750.3 | 3050.3 | -6.6 | 0 | 0 | 92.9 | 93.6 | 91.2 | 90.8 | 120.5 | 31.9 | 20.7 | 39.9 | 3.3 |  |  | 83.2 | 57 | 41.2 | 113.6 | 52.4 | 38.9 | 102.5
4751.3 | 3051.3 | -6.6 | 0 | 0 | 92.8 | 93.5 | 91.1 | 90.8 | 120.4 | 31.8 | 20.7 | 40 | 3 |  |  | 83.4 | 56.9 | 41.1 | 113.4 | 52.4 | 38.8 | 102.4
4752.3 | 3052.3 | -6.6 | 0 | 0 | 92.9 | 93.4 | 91 | 90.8 | 120.3 | 31.7 | 20.7 | 40 | 2.5 |  |  | 83.4 | 57 | 41 | 113.1 | 52.3 | 38.8 | 102.5
4753.3 | 3053.3 | -6.6 | 0 | 0 | 92.8 | 93.3 | 90.8 | 90.7 | 120.2 | 31.7 | 20.7 | 40 | 2.4 |  |  | 83.4 | 57 | 41 | 112.9 | 52.3 | 38.8 | 102.3
4754.3 | 3054.3 | -6.6 | 0 | 0 | 92.6 | 93.2 | 90.7 | 90.6 | 120.1 | 31.6 | 20.7 | 40 | 2.4 |  |  | 83.2 | 56.8 | 40.9 | 112.6 | 52.3 | 38.7 | 102.2
4755.3 | 3055.3 | -6.6 | 0 | 0 | 92.3 | 93.1 | 90.6 | 90.6 | 120 | 31.5 | 20.7 | 40 | 2.2 |  |  | 82.6 | 56.8 | 40.8 | 112.4 | 52.7 | 38.6 | 102
4756.3 | 3056.3 | -6.6 | 0 | 0 | 92.3 | 93 | 90.5 | 90.5 | 119.9 | 31.4 | 20.7 | 40 | 2.3 |  |  | 82.2 | 57.2 | 40.9 | 112.1 | 52.8 | 38.6 | 102
4757.3 | 3057.3 | -6.6 | 0 | 0 | 92.1 | 92.9 | 90.4 | 90.6 | 119.7 | 31.3 | 20.7 | 40.1 | 2.2 |  |  | 82.2 | 57.3 | 40.9 | 111.9 | 52.6 | 38.5 | 101.9
4758.3 | 3058.3 | -6.6 | 0 | 0 | 92.1 | 92.8 | 90.3 | 90.5 | 119.6 | 31.2 | 20.7 | 40.1 | 2.1 |  |  | 82.4 | 57.5 | 40.9 | 111.6 | 52.6 | 38.4 | 101.7
4759.3 | 3059.3 | -6.6 | 0 | 0 | 92 | 92.7 | 90.2 | 90.4 | 119.5 | 31.1 | 20.7 | 40.1 | 2.1 |  |  | 82.4 | 57.4 | 40.8 | 111.4 | 52.5 | 38.4 | 101.3
4760.3 | 3060.3 | -6.6 | 0 | 0 | 92 | 92.6 | 90 | 90.3 | 119.4 | 31.1 | 20.7 | 40 | 2.3 |  |  | 82 | 57 | 40.7 | 111.2 | 52.4 | 38.4 | 100.9
4761.3 | 3061.3 | -6.6 | 0 | 0 | 92 | 92.4 | 89.9 | 90.2 | 119.3 | 31.1 | 20.7 | 40 | 2.2 |  |  | 81.8 | 56.9 | 40.6 | 110.9 | 52.5 | 38.3 | 100.6
4762.3 | 3062.3 | -6.6 | 0 | 0 | 92.1 | 92.2 | 89.8 | 90.2 | 119.2 | 31.1 | 20.7 | 39.9 | 2 |  |  | 81.5 | 57 | 40.5 | 110.7 | 52.4 | 38.2 | 100.3
4763.3 | 3063.3 | -6.6 | 0 | 0 | 92.2 | 92.1 | 89.7 | 90.1 | 119.1 | 31.1 | 20.7 | 39.8 | 2.6 |  |  | 81.3 | 57 | 40.4 | 110.5 | 52.3 | 38.2 | 99.8
4764.3 | 3064.3 | -6.6 | 0 | 0 | 92.1 | 91.9 | 89.6 | 90.1 | 119 | 31.1 | 20.7 | 39.6 | 3 |  |  | 81.5 | 56.9 | 40.4 | 110.2 | 52.4 | 38.1 | 99.6
4765.3 | 3065.3 | -6.6 | 0 | 0 | 91.9 | 91.8 | 89.4 | 90 | 118.9 | 31.1 | 20.7 | 39.5 | 3 |  |  | 82 | 56.9 | 40.3 | 110 | 52.7 | 38.1 | 99.6
4766.3 | 3066.3 | -6.6 | 0 | 0 | 91.6 | 91.8 | 89.2 | 89.8 | 118.8 | 31.1 | 20.7 | 39.5 | 2.8 |  |  | 82.4 | 57.1 | 40.3 | 109.8 | 52.9 | 38.1 | 99.5
4767.3 | 3067.3 | -6.6 | 0 | 0 | 91.3 | 91.7 | 89 | 89.7 | 118.8 | 31.1 | 20.7 | 39.5 | 2.4 |  |  | 82.8 | 57.1 | 40.2 | 109.6 | 53 | 38 | 99.4
4768.3 | 3068.3 | -6.6 | 0 | 0 | 91.1 | 91.6 | 88.9 | 89.6 | 118.7 | 31.1 | 20.7 | 39.5 | 2.5 |  |  | 82.9 | 57.2 | 40.2 | 109.4 | 52.9 | 38 | 99.3
4769.3 | 3069.3 | -6.6 | 0 | 0 | 91 | 91.5 | 88.9 | 89.5 | 118.6 | 31.1 | 20.7 | 39.4 | 2.5 |  |  | 82.9 | 57.3 | 40.1 | 109.2 | 53 | 37.9 | 99.1
4770.3 | 3070.3 | -6.6 | 0 | 0 | 91 | 91.5 | 88.8 | 89.5 | 118.5 | 31.1 | 20.7 | 39.3 | 2.2 |  |  | 83.2 | 57.3 | 40.1 | 108.9 | 53.1 | 37.9 | 98.9
4771.3 | 3071.3 | -6.6 | 0 | 0 | 91 | 91.5 | 88.6 | 89.4 | 118.3 | 31 | 20.7 | 39.3 | 2.2 |  |  | 83.4 | 57.2 | 40 | 108.7 | 53.1 | 37.8 | 98.8
4772.3 | 3072.3 | -6.6 | 0 | 0 | 90.9 | 91.4 | 88.5 | 89.3 | 118.1 | 30.8 | 20.7 | 39.3 | 2.4 |  |  | 83.7 | 57.2 | 40 | 108.5 | 53.1 | 37.8 | 98.7
4773.3 | 3073.3 | -6.6 | 0 | 0 | 90.6 | 91.3 | 88.4 | 89.2 | 118 | 30.7 | 20.7 | 39.2 | 2.6 |  |  | 83.7 | 57.2 | 40 | 108.3 | 53.2 | 37.7 | 98.4
4774.3 | 3074.3 | -6.6 | 0 | 0 | 90.3 | 91.1 | 88.5 | 89.1 | 117.8 | 30.7 | 20.7 | 39.2 | 2.7 |  |  | 83.6 | 57.2 | 39.9 | 108.1 | 53.2 | 37.7 | 98.1
4775.3 | 3075.3 | -6.6 | 0 | 0 | 90 | 91 | 88.6 | 89 | 117.6 | 30.7 | 20.7 | 39.1 | 3.3 |  |  | 83.2 | 57.1 | 39.8 | 107.9 | 53.1 | 37.6 | 97.8
4776.3 | 3076.3 | -6.6 | 0 | 0 | 89.8 | 90.9 | 88.7 | 88.8 | 117.5 | 30.7 | 20.7 | 39.1 | 3.3 |  |  | 82.4 | 56.6 | 39.8 | 107.8 | 53 | 37.7 | 97.7
4777.3 | 3077.3 | -6.6 | 0 | 0 | 89.7 | 90.8 | 88.6 | 88.7 | 117.5 | 30.8 | 20.7 | 39 | 3.2 |  |  | 81.7 | 56.5 | 39.7 | 107.6 | 52.9 | 37.6 | 97.4
4778.3 | 3078.3 | -6.5 | 0 | 0 | 89.7 | 90.6 | 88.4 | 88.6 | 117.4 | 30.8 | 20.7 | 39 | 2.3 |  |  | 81.2 | 56.3 | 39.6 | 107.4 | 52.8 | 37.6 | 97
4779.3 | 3079.3 | -6.5 | 0 | 0 | 89.8 | 90.5 | 88.2 | 88.5 | 117.4 | 30.8 | 20.7 | 39 | 2.3 |  |  | 80.4 | 56.1 | 39.6 | 107.2 | 52.7 | 37.6 | 96.6
4780.3 | 3080.3 | -6.6 | 0 | 0 | 89.7 | 90.4 | 88.1 | 88.5 | 117.3 | 30.9 | 20.7 | 39 | 2.3 |  |  | 80.2 | 56.2 | 39.5 | 107 | 52.6 | 37.6 | 96.5
4781.3 | 3081.3 | -6.6 | 0 | 0 | 89.4 | 90.3 | 88.2 | 88.4 | 117.2 | 30.9 | 20.7 | 39 | 1.8 |  |  | 79.7 | 56.2 | 39.5 | 106.8 | 52.6 | 37.5 | 96.5
4782.3 | 3082.3 | -6.6 | 0 | 0 | 89.2 | 90.3 | 88.2 | 88.3 | 117.1 | 31 | 20.7 | 39.1 | 2.2 |  |  | 79.2 | 56.2 | 39.5 | 106.6 | 52.7 | 37.6 | 96.4
4783.3 | 3083.3 | -6.5 | 0 | 0 | 89.1 | 90.3 | 88.1 | 88.2 | 117 | 31.1 | 20.7 | 39.2 | 2.3 |  |  | 79 | 56.3 | 39.4 | 106.4 | 52.7 | 37.5 | 96
4784.3 | 3084.3 | -6.6 | 0 | 0 | 89.3 | 90.1 | 88 | 88.1 | 116.9 | 31 | 20.7 | 39.2 | 2.7 |  |  | 78.9 | 56.4 | 39.4 | 106.2 | 52.5 | 37.5 | 95.9
4785.3 | 3085.3 | -6.6 | 0 | 0 | 89.4 | 90 | 87.9 | 88 | 116.7 | 30.9 | 20.7 | 39.3 | 3 |  |  | 78.7 | 56.1 | 39.4 | 106 | 52.4 | 37.5 | 95.2
4786.3 | 3086.3 | -6.5 | 0 | 0 | 89.5 | 89.7 | 87.8 | 87.9 | 116.7 | 30.8 | 20.7 | 39.2 | 3.5 |  |  | 78.4 | 56 | 39.3 | 105.8 | 52.3 | 37.5 | 94.8
4787.3 | 3087.3 | -6.6 | 0 | 0 | 89.2 | 89.6 | 87.6 | 88 | 116.6 | 30.7 | 20.7 | 39.2 | 3.3 |  |  | 77.8 | 55.6 | 39.2 | 105.6 | 52.1 | 37.5 | 94.4
4788.3 | 3088.3 | -6.6 | 0 | 0 | 89 | 89.5 | 87.5 | 87.9 | 116.5 | 30.6 | 20.7 | 39.3 | 3.2 |  |  | 77 | 55.3 | 39.3 | 105.4 | 52 | 37.6 | 94.1
4789.3 | 3089.3 | -6.6 | 0 | 0 | 88.8 | 89.5 | 87.4 | 87.7 | 116.4 | 30.6 | 20.7 | 39.3 | 3.2 |  |  | 76.3 | 55.1 | 39.3 | 105.2 | 51.8 | 37.6 | 94.1
4790.3 | 3090.3 | -6.6 | 0 | 0 | 88.6 | 89.4 | 87.3 | 87.5 | 116.3 | 30.6 | 20.7 | 39.3 | 3 |  |  | 75.8 | 55.1 | 39.3 | 105 | 51.7 | 37.5 | 94.4
4791.3 | 3091.3 | -6.6 | 0 | 0 | 88.6 | 89.4 | 87.2 | 87.3 | 116.3 | 30.6 | 20.7 | 39.3 | 3.3 |  |  | 76 | 55.1 | 39.3 | 104.8 | 51.6 | 37.5 | 94.4
4792.3 | 3092.3 | -6.6 | 0 | 0 | 88.7 | 89.3 | 87.2 | 87.2 | 116.2 | 30.6 | 20.7 | 39.4 | 3.3 |  |  | 76.2 | 55.2 | 39.2 | 104.6 | 51.8 | 37.4 | 94.2
4793.3 | 3093.3 | -6.6 | 0 | 0 | 88.6 | 89.3 | 87.2 | 87.1 | 116.1 | 30.5 | 20.7 | 39.4 | 3.5 |  |  | 76.7 | 55.2 | 39.2 | 104.4 | 52 | 37.3 | 94.1
4794.3 | 3094.3 | -6.5 | 0 | 0 | 88.4 | 89.1 | 87.3 | 87.1 | 116.1 | 30.5 | 20.7 | 39.4 | 3.5 |  |  | 77.3 | 55.3 | 39.1 | 104.2 | 52.2 | 37.3 | 93.9
4795.3 | 3095.3 | -6.5 | 0 | 0 | 88.2 | 88.9 | 87.2 | 87.2 | 116 | 30.5 | 20.7 | 39.5 | 4 |  |  | 77.9 | 55.3 | 39.1 | 104 | 52.3 | 37.2 | 93.7
4796.3 | 3096.3 | -6.6 | 0 | 0 | 88 | 88.8 | 87.1 | 87.2 | 115.9 | 30.4 | 20.7 | 39.5 | 3.7 |  |  | 78.4 | 55.5 | 39 | 103.8 | 52.4 | 37.2 | 93.6
4797.3 | 3097.3 | -6.5 | 0 | 0 | 87.8 | 88.7 | 87 | 87.1 | 115.8 | 30.6 | 20.7 | 39.5 | 3.7 |  |  | 78.8 | 55.5 | 39 | 103.6 | 52.2 | 37.2 | 93.3
4798.3 | 3098.3 | -6.6 | 0 | 0 | 87.7 | 88.6 | 86.9 | 86.9 | 115.7 | 30.5 | 20.7 | 39.6 | 3 |  |  | 78.8 | 55.3 | 38.9 | 103.4 | 51.9 | 37.2 | 93.2
4799.3 | 3099.3 | -6.6 | 0 | 0 | 87.7 | 88.6 | 86.8 | 86.7 | 115.6 | 30.5 | 20.7 | 39.7 | 3.1 |  |  | 78.4 | 55.2 | 38.9 | 103.2 | 51.7 | 37.1 | 92.8
4800.3 | 3100.3 | -6.6 | 0 | 0 | 87.7 | 88.5 | 86.6 | 86.6 | 115.5 | 30.6 | 20.7 | 39.7 | 3.2 |  |  | 77.7 | 55 | 38.8 | 103 | 51.6 | 37.1 | 92.5
4801.3 | 3101.3 | -6.6 | 0 | 0 | 87.5 | 88.3 | 86.5 | 86.5 | 115.5 | 30.7 | 20.7 | 39.7 | 3.5 |  |  | 77.3 | 54.9 | 38.7 | 102.8 | 51.7 | 37.1 | 92.5
4802.3 | 3102.3 | -6.6 | 0 | 0 | 87.4 | 88.2 | 86.4 | 86.5 | 115.4 | 30.8 | 20.7 | 39.7 | 3.6 |  |  | 77.4 | 55 | 38.7 | 102.6 | 51.8 | 37.2 | 92.3
4803.3 | 3103.3 | -6.6 | 0 | 0 | 87.2 | 88.2 | 86.4 | 86.4 | 115.3 | 30.9 | 20.7 | 39.7 | 3.9 |  |  | 77.3 | 55.4 | 38.7 | 102.4 | 52.1 | 37.3 | 92.1
4804.3 | 3104.3 | -6.6 | 0 | 0 | 87.2 | 88.2 | 86.4 | 86.4 | 115.2 | 30.8 | 20.7 | 39.7 | 4.3 |  |  | 76.9 | 55.6 | 38.7 | 102.2 | 52.2 | 37.4 | 92.1
4805.3 | 3105.3 | -6.6 | 0 | 0 | 87.2 | 88.2 | 86.4 | 86.3 | 115.1 | 30.6 | 20.8 | 39.6 | 4.7 |  |  | 76.5 | 55.8 | 38.6 | 102 | 52.3 | 37.3 | 92.1
4806.3 | 3106.3 | -6.6 | 0 | 0 | 87.2 | 88.1 | 86.3 | 86.2 | 115 | 30.5 | 20.8 | 39.5 | 5 |  |  | 76.1 | 56.2 | 38.6 | 101.8 | 52.3 | 37.3 | 92.1
4807.3 | 3107.3 | -6.6 | 0 | 0 | 87 | 87.9 | 86.2 | 86.2 | 115 | 30.4 | 20.8 | 39.4 | 5.6 |  |  | 75.8 | 56.5 | 38.5 | 101.7 | 52.4 | 37.2 | 91.9
4808.3 | 3108.3 | -6.6 | 0 | 0 | 86.7 | 87.8 | 86.1 | 86 | 114.9 | 30.6 | 20.8 | 39.3 | 5.7 |  |  | 75.6 | 56.8 | 38.5 | 101.5 | 52.3 | 37.2 | 91.7
4809.3 | 3109.3 | -6.6 | 0 | 0 | 86.6 | 87.7 | 86 | 86 | 114.8 | 30.7 | 20.8 | 39.2 | 5.2 |  |  | 75.4 | 57 | 38.5 | 101.3 | 52.3 | 37.1 | 91.5
4810.3 | 3110.3 | -6.6 | 0 | 0 | 86.5 | 87.6 | 85.9 | 85.9 | 114.7 | 30.8 | 20.8 | 39.1 | 4.2 |  |  | 75.1 | 57.3 | 38.5 | 101.1 | 52.2 | 37.1 | 91.4
4811.3 | 3111.3 | -6.7 | 0 | 0 | 86.3 | 87.4 | 85.8 | 85.9 | 114.7 | 30.9 | 20.8 | 39 | 4.4 |  |  | 74.7 | 57.6 | 38.5 | 101 | 52.2 | 37.1 | 91.3
4812.3 | 3112.3 | -6.7 | 0 | 0 | 86.2 | 87.4 | 85.6 | 85.9 | 114.6 | 30.9 | 20.8 | 38.9 | 4.6 |  |  | 74.1 | 57.7 | 38.5 | 100.8 | 52.3 | 37.1 | 91.3
4813.3 | 3113.3 | -6.7 | 0 | 0 | 86 | 87.3 | 85.5 | 85.8 | 114.5 | 31 | 20.8 | 38.8 | 4.8 |  |  | 73.7 | 57.8 | 38.5 | 100.6 | 52.3 | 37.1 | 91.2
4814.3 | 3114.3 | -6.7 | 0 | 0 | 85.8 | 87.3 | 85.5 | 85.8 | 114.5 | 31 | 20.8 | 38.7 | 5.1 |  |  | 73.3 | 57.9 | 38.5 | 100.5 | 52.1 | 37.1 | 91

## First Electrical Failures
First electrical failures observed for the two cables present extracted from the corresponding IRMS files
3/C Cable |  |  | 7/C Cable
Time (s) | Offset time | C2-Grnd | Time (s) | Offset time | C6-C7
20.5 | -1679.5 | 257738 | 152 | -1548 | 252537.9994
174.5 | -1525.5 | 257738 | 306 | -1394 | 252537.9994
328.5 | -1371.5 | 257738 | 460 | -1240 | 252537.9994
482.3333 | -1217.6667 | 257738 | 614 | -1086 | 252537.9994
636.5 | -1063.5 | 257738 | 768 | -932 | 252537.9994
790.1667 | -909.8333 | 257738 | 922 | -778 | 505175.9997
944.5 | -755.5 | 257738 | 1076 | -624 | 252537.9994
1098.1667 | -601.8333 | 257738 | 1230 | -470 | 252537.9994
1252.1667 | -447.8333 | 257738 | 1384 | -316 | 252537.9994
1406.1667 | -293.8333 | 257738 | 1538 | -162 | 252537.9994
1560.1667 | -139.8333 | 258738 | 1692 | -8 | 252537.9994
1714.1667 | 14.1667 | 257738 | 1845.5 | 145.5 | 252537.9994
1868.1667 | 168.1667 | 257738 | 2000 | 300 | 252537.9994
2022.1667 | 322.1667 | 258738 | 2153.5 | 453.5 | 252537.9994
2176.1667 | 476.1667 | 257738 | 2308 | 608 | 252537.9994
2330.1667 | 630.1667 | 257738 | 2461.5 | 761.5 | 252537.9994
2484.1667 | 784.1667 | 257738 | 2615.5 | 915.5 | 252537.9994
2638.1667 | 938.1667 | 257738 | 2769.5 | 1069.5 | 252537.9994
2792.1667 | 1092.1667 | 257738 | 2923.5 | 1223.5 | 252537.9994
2946.1667 | 1246.1667 | 257738 | 3077.5 | 1377.5 | 807.2527
3100.1667 | 1400.1667 | 38.1943 | 3231.5 | 1531.5 | 286.2354
3254.1667 | 1554.1667 | 19.0938 | 3385.5 | 1685.5 | 9.7597
3408 | 1708 | 0.63934 | 3539.5 | 1839.5 | 85.9789
3562 | 1862 | 15.1062 | 3693.5 | 1993.5 | 466.1213
3716 | 2016 | 0.63686 | 3847.5 | 2147.5 | 1377.7633
3870 | 2170 | 11.5284 | 4001.5 | 2301.5 | 865.3595
4024 | 2324 | 32.9693 | 4155.5 | 2455.5 | 16.1668
4178 | 2478 | 30.5579 | 4309.5 | 2609.5 | 810.061
4332 | 2632 | 257.9817 | 4463.5 | 2763.5 | 252537.9994