## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 7, Location C, IRMS #2
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, PVC, EPR, XLPO, PE, TS/TP, & Tefzel control cables (Items 1, 2, 8, 15, 3, & 12). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 200 kW heat release rate and increased to ~300 kW during the test. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 152 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
152 | 0 | Ignited Gas Burner
490-495 | 338-343 | Conductors D7 & D8 both short to ground at less than 100 ohms (1 & 4) | Cable D shorts to ground
507-510 | 355-358 | Conductors E9 & E10 both short to ground at less than 100 ohms (4 & 1) | Cable E shorts to ground
514 | 362 | Conductors D7 & D8 short together at less than 100 ohms (25) | Cable D shorted internally
528-530 | 376-378 | Conductors F11 & F12 both short to ground at less than 100 ohms (1 & 1) | Cable F shorts to ground
539 | 387 | Conductors E9 & E10 short together at less than 100 ohms (2) | Cable E shorted internally
553 | 401 | Conductors F11 & F12 short together at less than 100 ohms (12) | Cable F shorted internally
556 | 404 | Conductors A1 & A2 short together at less than 100 ohms (31) | Cable A shorted internally
561 | 409 | Conductor A1 shorts to ground at less than 1000 ohms (363)
612 | 460 | Conductor B3 shorts to ground at less than 1000 ohms (119)
617 | 465 | Conductor B3 shorts to conductor C5 at less than 1000 ohms (126) | Possible cable to cable interaction
627 | 475 | Conductor B4 shorts to ground at less than 100 ohms (45) | Cable B shorts to ground
641-650 | 489-498 | Conductors C5 & C6 both short to ground at less than 100 ohms (2 & 3) | Cable C shorts to ground
662 | 510 | Conductors C5 & C6 short together at less than 1000 ohms (155) | Cable C shorted internally
746-768 | 594-616 | The existing ground fault on conductor A1 decreases to less than 100 ohms (30) and conductor A2 shorts to ground at less than 100 ohms (8) | Cable A shorts to ground
796 | 644 | The existing ground fault on conductor B3 decreases to less than 100 ohms (2)
799 | 647 | Conductors B3 & B4 short together at less than 100 ohms (23) | Cable B shorted internally
847 | 695 | The existing internal fault between conductors C5 & C6 decreases to less than 100 ohms (69)
1551 | 1399 | Gas burner is shut off
Additional Observations
Observation 1 | The progression of cable failure generally started with the bottom cables and worked up to the top cable group during the test.
Observation 2 | One possible cable to cable interaction occurred during this test (between cables B & C).

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | PVC | (Item #1)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | XLPO | (Item #8)
|  |  |  | Cable D = | PE | (Item #15)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | Tefzel | (Item #12)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | PVC | (Item #1)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | XLPO | (Item #8)
|  |  |  | Cable D = | PE | (Item #15)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | Tefzel | (Item #12)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 7 |  |  | 2006-11-08 | 8:39
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-151 | 479975.9997 | -148 | 485575.9997 | -145.5 | 499375.9997 | -142.5 | 498375.9997 | -139.5 | 500575.9997 | -120 | 471175.9997 | -117.5 | 505775.9997 | -114.5 | 516575.9997 | -111.5 | 507975.9997 | -92 | 429575.9997 | -89.5 | 504575.9997 | -86.5 | 495775.9997 | -83.5 | 510175.9997 | -80.5 | 515975.9997 | -78 | 500775.9997 | -75 | 510775.9997 | -66.5 | 497975.9997 | -64 | 500975.9997 | -61.5 | 524175.9997 | -58.5 | 524775.9997 | -55.5 | 491575.9997 | -52.5 | 492775.9997 | -44.5 | 490375.9997 | -36 | 519575.9997 | -33.5 | 523375.9997 | -30.5 | 522775.9997 | -27.5 | 517775.9997 | -19.5 | 515175.9997 | -16.5 | 497375.9997 | -13.5 | 521175.9997 | -11 | 502775.9997 | -8 | 526775.9997 | -5.5 | 523775.9997 | -2.5 | 498375.9997 | 6 | 512575.9997 | 9 | 522375.9997 | 17 | 508375.9997 | 20 | 525175.9997 | 23 | 506975.9997 | 25.5 | 485775.9997 | 28.5 | 504975.9997 | 31.5 | 524375.9997
34 | 479975.9997 | 36.5 | 485575.9997 | 39.5 | 499375.9997 | 42.5 | 498375.9997 | 45 | 500575.9997 | 64.5 | 471175.9997 | 67.5 | 505775.9997 | 70.5 | 516575.9997 | 73.5 | 507975.9997 | 93 | 429575.9997 | 95.5 | 504575.9997 | 98.5 | 495775.9997 | 101.5 | 510175.9997 | 104 | 515975.9997 | 106.5 | 500775.9997 | 109.5 | 510775.9997 | 118 | 497975.9997 | 120.5 | 500975.9997 | 123.5 | 524175.9997 | 126.5 | 524775.9997 | 129 | 491575.9997 | 132 | 492775.9997 | 140.5 | 490375.9997 | 148.5 | 519575.9997 | 151.5 | 523375.9997 | 154.5 | 522775.9997 | 157.5 | 517775.9997 | 165.5 | 515175.9997 | 168.5 | 497375.9997 | 171 | 521175.9997 | 174 | 502775.9997 | 177 | 526775.9997 | 179.5 | 523775.9997 | 182.5 | 498375.9997 | 190.5 | 512575.9997 | 193.5 | 522375.9997 | 202 | 508375.9997 | 204.5 | 525175.9997 | 207.5 | 506975.9997 | 210.5 | 485775.9997 | 213 | 504975.9997 | 216 | 524375.9997
218.5 | 479975.9997 | 221.5 | 485575.9997 | 224.5 | 499375.9997 | 227 | 498375.9997 | 230 | 500575.9997 | 249.5 | 471175.9997 | 252.5 | 505775.9997 | 255 | 516575.9997 | 258 | 507975.9997 | 277.5 | 214737.9994 | 280.5 | 252237.9994 | 283 | 247837.9994 | 286 | 255037.9994 | 288.5 | 64409.4976 | 291.5 | 62509.4976 | 294.5 | 255337.9994 | 302.5 | 62159.4976 | 305.5 | 250437.9994 | 308.5 | 262037.9994 | 311 | 65509.4976 | 314 | 49067.5969 | 316.5 | 123118.9988 | 325 | 48947.5969 | 333.5 | 51867.5969 | 336.5 | 87145.9982 | 339 | 65259.4976 | 342 | 64634.4976 | 350.5 | 64309.4976 | 353 | 62084.4976 | 356 | 65059.4976 | 358.5 | 62759.4976 | 361.5 | 25.0151 | 364.5 | 23.2706 | 367 | 14.6121 | 375.5 | 13.6405 | 378.5 | 32.2943 | 386.5 | 2.0177 | 389.5 | 16.8424 | 392.5 | 6.0367 | 395 | 12686.1989 | 398 | 8317.915 | 400.5 | 12.0133
403.5 | 31.4007 | 406.5 | 60609.4976 | 409 | 248838.8008 | 412 | 82979.3315 | 414.5 | 83345.9982 | 434.5 | 58809.4976 | 437 | 84212.6648 | 440 | 86012.6648 | 442.5 | 84579.3315 | 462.5 | 4271.0596 | 465 | 126.0393 | 468 | 324.1948 | 470.5 | 539.2 | 473.5 | 125.8525 | 476.5 | 117.8327 | 479 | 275.229 | 487.5 | 77.5417 | 490.5 | 68.0346 | 493 | 103.0547 | 496 | 114.015 | 498.5 | 115.1413 | 501.5 | 103.607 | 510 | 154.6022 | 518.5 | 31.9909 | 521 | 19.743 | 524 | 23.935 | 526.5 | 0.80247 | 535 | 22.5946 | 538 | 18.1417 | 540.5 | 6.5863 | 543.5 | 1.4731 | 546.5 | 15.5522 | 549 | 0.95986 | 552 | 4.1232 | 560.5 | 23.6683 | 563 | 18.2258 | 571.5 | 6.4725 | 574.5 | 4.8232 | 577 | 24.4692 | 580 | 14.7939 | 582.5 | 26.2707 | 585.5 | 15.334
588.5 | 31.5929 | 591 | 28.4386 | 594 | 55.2077 | 596.5 | 48.948 | 599.5 | 74.682 | 619 | 12.1279 | 622 | 31.8947 | 624.5 | 6.2666 | 627.5 | 11.9911 | 647 | 23.4265 | 650 | 35.4929 | 652.5 | 37.2642 | 655.5 | 27.5175 | 658.5 | 11.8329 | 661 | 21.9453 | 664 | 18.4531 | 672.5 | 26.5875 | 675 | 22.5479 | 678 | 23.1266 | 680.5 | 24.9636 | 683.5 | 21.9468 | 686.5 | 25.188 | 694.5 | 68.6032 | 703 | 23.4101 | 706 | 23.7159 | 708.5 | 13.9393 | 711.5 | 31.0508 | 720 | 9.683 | 722.5 | 0.84566 | 725.5 | 18.953 | 728.5 | 22.8688 | 731 | 27.3181 | 734 | 10.3656 | 736.5 | 20.2681 | 745 | 14.1649 | 748 | 24.2644 | 756.5 | 0.89367 | 759 | 6.7334 | 762 | 14.2203 | 764.5 | 18.5538 | 767.5 | 8.3467 | 770.5 | 0.067544
773 | 7083.0562 | 776 | 12.4919 | 778.5 | 0.85443 | 781.5 | 4.5783 | 784.5 | 2.6224 | 804 | 0.15807 | 806.5 | 0.88238 | 809.5 | 25.3282 | 812.5 | 7.323 | 832 | 4551.7327 | 834.5 | 51.7384 | 837.5 | 104.1687 | 840.5 | 43.3117 | 843 | 71.8041 | 846 | 90.2279 | 848.5 | 65.9092 | 857 | 32.3939 | 860 | 75.9437 | 862.5 | 95.1009 | 865.5 | 60.5082 | 868.5 | 49.6397 | 871 | 72.191 | 879.5 | 4729.9596 | 888 | 3.4741 | 890.5 | 9.2276 | 893.5 | 15.5042 | 896.5 | 21.844 | 904.5 | 22.5946 | 907.5 | 7.2212 | 910 | 4.1003 | 913 | 0.79312 | 916 | 27.7632 | 918.5 | 0.83787 | 921.5 | 6.8648 | 930 | 24.4727 | 932.5 | 21.6382 | 941 | 13.3231 | 943.5 | 11.7403 | 946.5 | 0.88759 | 949.5 | 4.0816 | 952 | 18.1692 | 955 | 11.0771
958 | 49.1336 | 960.5 | 18.0883 | 963.5 | 16.3384 | 966.5 | 23.2095 | 969 | 19.3193 | 988.5 | 0.68491 | 991.5 | 27.3899 | 994.5 | 34.3041 | 997 | 26.055 | 1016.5 | 4.1939 | 1019.5 | 35.0468 | 1022.5 | 46.4681 | 1025 | 70.3239 | 1028 | 41.1406 | 1030.5 | 35.5083 | 1033.5 | 68.468 | 1042 | 29.5656 | 1044.5 | 43.3431 | 1047.5 | 41.0315 | 1050.5 | 84.7365 | 1053 | 58.2789 | 1056 | 38.0707 | 1064.5 | 26.0877 | 1072.5 | 17.585 | 1075.5 | 21.9321 | 1078.5 | 27.612 | 1081 | 1.2147 | 1089.5 | 1.6546 | 1092 | 13.0877 | 1095 | 29.6263 | 1097.5 | 5.1923 | 1100.5 | 8.8595 | 1103.5 | 21.792 | 1106 | 4.6698 | 1114.5 | 22.9347 | 1117.5 | 29.5961 | 1125.5 | 2806.9665 | 1128.5 | 8.4313 | 1131.5 | 39.7555 | 1134 | 11.4166 | 1137 | 50.4748 | 1139.5 | 2.1068
1142.5 | 3797.8464 | 1145.5 | 0.79342 | 1148.5 | 10.3245 | 1151 | 23.4609 | 1153.5 | 7.9199 | 1173.5 | 3.3544 | 1176.5 | 22.6824 | 1179 | 2.5268 | 1181.5 | 15.9621 | 1201.5 | 14.2327 | 1204.5 | 124.0143 | 1207 | 110.2937 | 1210 | 82.3068 | 1212.5 | 72.0369 | 1215.5 | 127.4153 | 1218.5 | 57.7735 | 1226.5 | 110.1494 | 1229.5 | 87.7048 | 1232 | 308.5603 | 1235 | 76.6606 | 1237.5 | 255.3495 | 1240.5 | 39.5914 | 1249 | 145.0549 | 1257.5 | 4.7365 | 1260 | 33.3125 | 1263 | 37.766 | 1265.5 | 28.5099 | 1274 | 14.9629 | 1277 | 0.11415 | 1279.5 | 11.0749 | 1282.5 | 10.9323 | 1285.5 | 23.6238 | 1288 | 13.3403 | 1291 | 18.965 | 1299.5 | 3.7419 | 1302 | 0.95389 | 1310.5 | 0.086436 | 1313.5 | 13.0886 | 1316 | 16.2251 | 1319 | 0.79431 | 1321.5 | 7.9136 | 1324.5 | 5.8512
1327.5 | 12.802 | 1330 | 23.0203 | 1333 | 20.9936 | 1335.5 | 10.5061 | 1338.5 | 0.85969 | 1358 | 18.965 | 1361 | 28.3202 | 1363.5 | 0.92906 | 1366.5 | 24.9065 | 1386 | 7.9496 | 1389 | 27371.6675 | 1391.5 | 50.3663 | 1394.5 | 741.8546 | 1397.5 | 1164.7676 | 1400 | 649.6105 | 1403 | 165.7732 | 1411.5 | 721.7226 | 1414 | 687.6612 | 1417 | 756.4733 | 1419.5 | 496.1814 | 1422.5 | 406.5864 | 1425.5 | 486.5007 | 1433.5 | 1508.0024 | 1442 | 37.4356 | 1445 | 37.5539 | 1447.5 | 7.5133 | 1450.5 | 12.8366 | 1459 | 27.2737 | 1461.5 | 11.0989 | 1464.5 | 24.7713 | 1467.5 | 20.9195 | 1470 | 17.4729 | 1473 | 8.7927 | 1475.5 | 1.8165 | 1484 | 4.8036 | 1487 | 28.2219 | 1495.5 | 4.9614 | 1498 | 183.6762 | 1501 | 62.8392 | 1503.5 | 59.5367 | 1506.5 | 137.8218 | 1509.5 | 4.7049
1512 | 558.9142 | 1515 | 5.4482 | 1517.5 | 15.0636 | 1520.5 | 23.1468 | 1523.5 | 26.3955 | 1543 | 0.72857 | 1545.5 | 0.71947 | 1548.5 | 33.6622 | 1551.5 | 17.9097 | 1571 | 3.3808 | 1573.5 | 1640.1735 | 1576.5 | 11169.8957 | 1579.5 | 5446.4502 | 1582 | 17102.5242 | 1585 | 41639.663 | 1587.5 | 255337.9994 | 1596 | 124418.9988 | 1599 | 9536.0611 | 1601.5 | 7843.5556 | 1604.5 | 5483.7585 | 1607.5 | 3682.0834 | 1610 | 4549.7412 | 1618.5 | 15.4477 | 1627 | 25.6863 | 1629.5 | 36.5238 | 1632.5 | 41.8238 | 1635.5 | 741.8975 | 1644 | 66.0301 | 1646.5 | 7962.7787 | 1649.5 | 43.3765 | 1652 | 42.1981 | 1655 | 29.3121 | 1657.5 | 5.9513 | 1660.5 | 23.84 | 1669 | 0.91184 | 1672 | 21.4048 | 1680 | 42.7871 | 1683 | 72.6639 | 1685.5 | 95.9066 | 1688.5 | 9.8505 | 1691.5 | 62.0873 | 1694.5 | 13.8806
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 7 |  |  | 2006-11-08 | 8:39
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-145.3 | 479976 |  | -122.9 | 471176 | -94.7778 | 429576 | -79.2778 | 429576 | -65 | 490376 | -56.2778 | 490376 | -32.2 | 498376 | -26.4 | 512576 | -14.2778 | 491576 | -11.1111 | 485776 | 6.6 | 485776 | 8.9 | 502776
39.5 | 479976 |  | 62 | 471176 | 89.9444 | 429576 | 105.5 | 429576 | 119.8889 | 490376 | 128.5556 | 490376 | 152.8 | 498376 | 158.3 | 512576 | 170.3889 | 491576 | 173.6667 | 485776 | 191.3 | 485776 | 193.6 | 502776
224.3 | 479976 |  | 246.7 | 471176 | 274.7222 | 62509.5 | 290.2778 | 49067.6 | 304.5556 | 48947.6 | 313.2778 | 62084.5 | 337.5 | 0.62879 | 343 | 3.6076 | 355.3333 | 3.5171 | 358.3889 | 0.62976 | 376 | 1.4046 | 378.3 | 0.63661
409.1 | 363.2962 |  | 431.5 | 5182.4111 | 459.5556 | 118.5323 | 475.0556 | 45.0628 | 489.3889 | 2.347 | 498.0556 | 2.964 | 522.2 | 0.62927 | 527.9 | 1.43 | 540.1111 | 0.9949 | 543.1667 | 0.64539 | 560.9 | 1.5203 | 563 | 0.62855
593.9 | 29.5827 |  | 616.3 | 7.7306 | 644.2778 | 2.3721 | 659.8889 | 5.8761 | 674.1111 | 0.66209 | 682.8333 | 0.66289 | 707 | 0.64615 | 712.6 | 0.62567 | 724.8889 | 0.64846 | 728 | 6.9841 | 745.6 | 1.6426 | 748 | 0.65285
778.7 | 0.66022 |  | 801.1 | 0.65181 | 829.1111 | 38.3913 | 844.6111 | 3.0717 | 858.9444 | 0.65337 | 867.6667 | 0.66504 | 891.8 | 2.3995 | 897.4 | 2.2743 | 909.6111 | 0.63984 | 912.6667 | 1.7276 | 930.3 | 4.1719 | 932.6 | 0.65026
963.5 | 12.4453 |  | 985.9 | 0.69233 | 1013.8333 | 11.8567 | 1029.4444 | 5.2802 | 1043.8333 | 2.7532 | 1052.3889 | 0.64897 | 1076.5 | 6.1039 | 1082.2 | 1.1322 | 1094.3333 | 2.8495 | 1097.4444 | 5.046 | 1115.1 | 2.5649 | 1117.3 | 3.6118
1148.2 | 0.6791 |  | 1170.6 | 4.0427 | 1198.7222 | 14.0085 | 1214.1667 | 23.8678 | 1228.4444 | 6.2298 | 1237.0556 | 1.6087 | 1261.3 | 4.3083 | 1266.9 | 0.63097 | 1279.1111 | 0.63439 | 1282.2222 | 0.66155 | 1299.9 | 0.62759 | 1302 | 1.5432
1332.9 | 0.65862 |  | 1355.3 | 0.6381 | 1383.2778 | 51.3663 | 1398.8889 | 13.5779 | 1413.1111 | 8.6367 | 1421.8333 | 0.6581 | 1446 | 3.2897 | 1451.6 | 0.62807 | 1463.8889 | 0.65836 | 1467 | 3.3787 | 1484.6 | 0.63048 | 1487 | 1.2111
1517.7 | 6.089 |  | 1540.1 | 0.7 | 1568.1111 | 306.073 | 1583.6111 | 30.0452 | 1597.9444 | 26.5168 | 1606.7778 | 13.8107 | 1630.8 | 7.4397 | 1636.5 | 0.63885 | 1648.7222 | 10.7644 | 1651.7778 | 11.1844 | 1669.6 | 3.7985 | 1671.8 | 0.65572
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## F11-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.0965 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39029.3576 | 0 | 0 | 39029.3576 | 0 | 0 |  | 31.5 | 183.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39029.3597 | 0 | 0 | 39029.3598 | 0 | 0 |  | 216 | 368 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39029.3619 | 2312 | 0 | 39029.3619 | 1973 | 0 |  | 400.5 | 552.5 | 141.1477 | 0 | 120.4518 | 0 | 1.4115 | 0 | 1.2045 | 0 | 1.4115 | 1.2045 | 13.4247 | 32.9133 | 12.0133
39029.364 | 2247 | 0 | 39029.364 | 2606 | 0 |  | 585.5 | 737.5 | 137.1795 | 0 | 159.0965 | 0 | 1.3718 | 0 | 1.591 | 0 | 1.3718 | 1.591 | 16.7058 | 0.62855 | 15.334
39029.3662 | 2580 | 0 | 39029.3662 | 2162 | 0 |  | 770.5 | 922.5 | 157.5092 | 0 | 131.9902 | 0 | 1.5751 | 0 | 1.3199 | 0 | 1.5751 | 1.3199 | 1.6426 | 21.2942 | 0.067544
39029.3683 | 2331 | 0 | 39029.3683 | 2435 | 0 |  | 955 | 1107 | 142.3077 | 0 | 148.6569 | 0 | 1.4231 | 0 | 1.4866 | 0 | 1.4231 | 1.4866 | 12.5002 | 7.6953 | 11.0771
39029.3704 | 2530 | 0 | 39029.3705 | 2261 | 0 |  | 1139.5 | 1291.5 | 154.4567 | 0 | 138.0342 | 0 | 1.5446 | 0 | 1.3803 | 0 | 1.5446 | 1.3803 | 3.6514 | 15.9832 | 2.1068
39029.3726 | 2443 | 0 | 39029.3726 | 2345 | 0 |  | 1324.5 | 1476.5 | 149.1453 | 0 | 143.1624 | 0 | 1.4915 | 0 | 1.4316 | 0 | 1.4915 | 1.4316 | 7.3426 | 11.8286 | 5.8512
39029.3747 | 2469 | 0 | 39029.3747 | 2591 | 0 |  | 1509.5 | 1661.5 | 150.7326 | 0 | 158.1807 | 0 | 1.5073 | 0 | 1.5818 | 0 | 1.5073 | 1.5818 | 6.2122 | 1.2111 | 4.7049
39029.3769 | 2275 | 0 | 39029.3769 | 2564 | 0 |  | 1694.5 | 1846.5 | 138.8889 | 0 | 156.5324 | 0 | 1.3889 | 0 | 1.5653 | 0 | 1.3889 | 1.5653 | 15.2695 | 2.2769 | 13.8806

## E10-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 154.1746 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39029.3576 | 0 | 0 | 39029.3576 | 0 | 0 |  | 28.5 | 180.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504976 | 504976 | 504975.9997
39029.3597 | 0 | 0 | 39029.3597 | 0 | 0 |  | 213 | 365 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504976 | 504976 | 504975.9997
39029.3619 | 30 | 0 | 39029.3619 | 2462 | 0 |  | 398 | 550 | 1.8315 | 0 | 150.3053 | 0 | 0.018315 | 0 | 1.5031 | 0 | 0.018315 | 1.5031 | 8317.9333 | 2.5743 | 8317.915
39029.364 | 1981 | 0 | 39029.364 | 2351 | 0 |  | 582.5 | 734.5 | 120.9402 | 0 | 143.5287 | 0 | 1.2094 | 0 | 1.4353 | 0 | 1.2094 | 1.4353 | 27.4801 | 7.4173 | 26.2707
39029.3661 | 2301 | 0 | 39029.3661 | 2509 | 0 |  | 767.5 | 919.5 | 140.4762 | 0 | 153.1746 | 0 | 1.4048 | 0 | 1.5317 | 0 | 1.4048 | 1.5317 | 9.7514 | 0.65285 | 8.3467
39029.3683 | 2114 | 0 | 39029.3683 | 2112 | 0 |  | 952 | 1104 | 129.0598 | 0 | 128.9377 | 0 | 1.2906 | 0 | 1.2894 | 0 | 1.2906 | 1.2894 | 19.4598 | 19.5729 | 18.1692
39029.3704 | 1667 | 0 | 39029.3704 | 2062 | 0 |  | 1137 | 1289 | 101.7705 | 0 | 125.8852 | 0 | 1.0177 | 0 | 1.2589 | 0 | 1.0177 | 1.2589 | 51.4925 | 22.4724 | 50.4748
39029.3725 | 2310 | 0 | 39029.3726 | 2487 | 0 |  | 1321.5 | 1473.5 | 141.0256 | 0 | 151.8315 | 0 | 1.4103 | 0 | 1.5183 | 0 | 1.4103 | 1.5183 | 9.3238 | 1.5432 | 7.9136
39029.3747 | 1059 | 0 | 39029.3747 | 2382 | 0 |  | 1506.5 | 1658.5 | 64.652 | 0 | 145.4212 | 0 | 0.64652 | 0 | 1.4542 | 0 | 0.64652 | 1.4542 | 138.4684 | 6.0193 | 137.8218
39029.3768 | 1549 | 0 | 39029.3768 | 1944 | 0 |  | 1691.5 | 1843.5 | 94.5665 | 0 | 118.6813 | 0 | 0.94567 | 0 | 1.1868 | 0 | 0.94567 | 1.1868 | 63.0329 | 29.9064 | 62.0873

## E10-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 148.3138 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39029.3575 | 0 | 0 | 39029.3576 | 0 | 0 |  | 25.5 | 177.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 485776 | 485776 | 485775.9997
39029.3597 | 0 | 0 | 39029.3597 | 0 | 0 |  | 210.5 | 362.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 485776 | 485776 | 485775.9997
39029.3618 | 19 | 0 | 39029.3618 | 2341 | 0 |  | 395 | 547 | 1.16 | 0 | 142.9182 | 0 | 0.0116 | 0 | 1.4292 | 0 | 0.0116 | 1.4292 | 12686.2105 | 3.7753 | 12686.1989
39029.364 | 2093 | 0 | 39029.364 | 2393 | 0 |  | 580 | 732 | 127.7778 | 0 | 146.0928 | 0 | 1.2778 | 0 | 1.4609 | 0 | 1.2778 | 1.4609 | 16.0717 | 1.5203 | 14.7939
39029.3661 | 2028 | 0 | 39029.3661 | 2027 | 0 |  | 764.5 | 916.5 | 123.8095 | 0 | 123.7485 | 0 | 1.2381 | 0 | 1.2375 | 0 | 1.2381 | 1.2375 | 19.7919 | 19.851 | 18.5538
39029.3682 | 2303 | 0 | 39029.3683 | 2305 | 0 |  | 949.5 | 1101.5 | 140.5983 | 0 | 140.7204 | 0 | 1.406 | 0 | 1.4072 | 0 | 1.406 | 1.4072 | 5.4876 | 5.3961 | 4.0816
39029.3704 | 2155 | 0 | 39029.3704 | 1986 | 0 |  | 1134 | 1286 | 131.5629 | 0 | 121.2454 | 0 | 1.3156 | 0 | 1.2125 | 0 | 1.3156 | 1.2125 | 12.7323 | 22.3253 | 11.4166
39029.3725 | 2413 | 0 | 39029.3725 | 2210 | 0 |  | 1319 | 1471 | 147.3138 | 0 | 134.9206 | 0 | 1.4731 | 0 | 1.3492 | 0 | 1.4731 | 1.3492 | 0.67882 | 9.9267 | 0.79431
39029.3747 | 1514 | 0 | 39029.3747 | 2033 | 0 |  | 1503.5 | 1655.5 | 92.4298 | 0 | 124.1148 | 0 | 0.9243 | 0 | 1.2411 | 0 | 0.9243 | 1.2411 | 60.461 | 19.4973 | 59.5367
39029.3768 | 2185 | 0 | 39029.3768 | 2266 | 0 |  | 1688.5 | 1840.5 | 133.3944 | 0 | 138.3394 | 0 | 1.3339 | 0 | 1.3834 | 0 | 1.3339 | 1.3834 | 11.1844 | 7.2101 | 9.8505

## E9-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 154.7851 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39029.3575 | 0 | 0 | 39029.3575 | 0 | 0 |  | 23 | 175 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 506976 | 506976 | 506975.9997
39029.3597 | 0 | 0 | 39029.3597 | 0 | 0 |  | 207.5 | 359.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 506976 | 506976 | 506975.9997
39029.3618 | 2359 | 0 | 39029.3618 | 1989 | 0 |  | 392.5 | 544.5 | 144.0171 | 0 | 121.4286 | 0 | 1.4402 | 0 | 1.2143 | 0 | 1.4402 | 1.2143 | 7.4769 | 27.4701 | 6.0367
39029.3639 | 2017 | 0 | 39029.3639 | 2357 | 0 |  | 577 | 729 | 123.138 | 0 | 143.895 | 0 | 1.2314 | 0 | 1.4389 | 0 | 1.2314 | 1.4389 | 25.7005 | 7.5681 | 24.4692
39029.3661 | 2194 | 0 | 39029.3661 | 2430 | 0 |  | 762 | 914 | 133.9438 | 0 | 148.3516 | 0 | 1.3394 | 0 | 1.4835 | 0 | 1.3394 | 1.4835 | 15.5597 | 4.3366 | 14.2203
39029.3682 | 2519 | 0 | 39029.3682 | 2519 | 0 |  | 946.5 | 1098.5 | 153.7851 | 0 | 153.7851 | 0 | 1.5379 | 0 | 1.5379 | 0 | 1.5379 | 1.5379 | 0.65026 | 0.65026 | 0.88759
39029.3703 | 1800 | 0 | 39029.3704 | 2447 | 0 |  | 1131.5 | 1283.5 | 109.8901 | 0 | 149.3895 | 0 | 1.0989 | 0 | 1.4939 | 0 | 1.0989 | 1.4939 | 40.8544 | 3.6118 | 39.7555
39029.3725 | 2157 | 0 | 39029.3725 | 2044 | 0 |  | 1316 | 1468 | 131.685 | 0 | 124.7863 | 0 | 1.3168 | 0 | 1.2479 | 0 | 1.3168 | 1.2479 | 17.542 | 24.0401 | 16.2251
39029.3746 | 1548 | 0 | 39029.3746 | 1993 | 0 |  | 1501 | 1653 | 94.5055 | 0 | 121.6728 | 0 | 0.94505 | 0 | 1.2167 | 0 | 0.94505 | 1.2167 | 63.7842 | 27.2142 | 62.8392
39029.3768 | 1289 | 0 | 39029.3768 | 2210 | 0 |  | 1685.5 | 1837.5 | 78.6935 | 0 | 134.9206 | 0 | 0.78694 | 0 | 1.3492 | 0 | 0.78694 | 1.3492 | 96.6936 | 14.7231 | 95.9066

## E9-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.3407 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39029.3575 | 0 | 0 | 39029.3575 | 0 | 0 |  | 20 | 172 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525176 | 525176 | 525175.9997
39029.3596 | 0 | 0 | 39029.3596 | 0 | 0 |  | 204.5 | 356.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525176 | 525176 | 525175.9997
39029.3618 | 2222 | 0 | 39029.3618 | 2590 | 0 |  | 389.5 | 541.5 | 135.6532 | 0 | 158.1197 | 0 | 1.3565 | 0 | 1.5812 | 0 | 1.3565 | 1.5812 | 18.1989 | 1.4046 | 16.8424
39029.3639 | 2470 | 0 | 39029.3639 | 2050 | 0 |  | 574.5 | 726.5 | 150.7937 | 0 | 125.1526 | 0 | 1.5079 | 0 | 1.2515 | 0 | 1.5079 | 1.2515 | 6.3312 | 28.1161 | 4.8232
39029.366 | 2427 | 0 | 39029.3661 | 2194 | 0 |  | 759 | 911 | 148.1685 | 0 | 133.9438 | 0 | 1.4817 | 0 | 1.3394 | 0 | 1.4817 | 1.3394 | 8.2151 | 19.7074 | 6.7334
39029.3682 | 2321 | 0 | 39029.3682 | 2223 | 0 |  | 943.5 | 1095.5 | 141.6972 | 0 | 135.7143 | 0 | 1.417 | 0 | 1.3571 | 0 | 1.417 | 1.3571 | 13.1573 | 18.1457 | 11.7403
39029.3703 | 2390 | 0 | 39029.3703 | 2312 | 0 |  | 1128.5 | 1280.5 | 145.9096 | 0 | 141.1477 | 0 | 1.4591 | 0 | 1.4115 | 0 | 1.4591 | 1.4115 | 9.8904 | 13.5978 | 8.4313
39029.3725 | 2294 | 0 | 39029.3725 | 2610 | 0 |  | 1313.5 | 1465.5 | 140.0488 | 0 | 159.3407 | 0 | 1.4005 | 0 | 1.5934 | 0 | 1.4005 | 1.5934 | 14.4891 | 0.62759 | 13.0886
39029.3746 | 924 | 0 | 39029.3746 | 2216 | 0 |  | 1498 | 1650 | 56.4103 | 0 | 135.2869 | 0 | 0.5641 | 0 | 1.3529 | 0 | 0.5641 | 1.3529 | 184.2403 | 18.519 | 183.6762
39029.3767 | 1513 | 0 | 39029.3767 | 2325 | 1 |  | 1683 | 1835 | 92.3687 | 0 | 141.9414 | 0.06105 | 0.92369 | 0 | 1.4194 | 0.0006105 | 0.92369 | 1.4188 | 73.5876 | 13.0112 | 72.6639

## E9-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 155.2125 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39029.3574 | 0 | 0 | 39029.3575 | 0 | 0 |  | 17 | 169 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508376 | 508376 | 508375.9997
39029.3596 | 0 | 0 | 39029.3596 | 0 | 0 |  | 202 | 354 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508376 | 508376 | 508375.9997
39029.3617 | 2456 | 0 | 39029.3617 | 37 | 0 |  | 386.5 | 538.5 | 149.9389 | 0 | 2.2589 | 0 | 1.4994 | 0 | 0.022589 | 0 | 1.4994 | 0.022589 | 3.5171 | 6771.2973 | 2.0177
39029.3639 | 2356 | 0 | 39029.3639 | 1917 | 0 |  | 571.5 | 723.5 | 143.8339 | 0 | 117.033 | 0 | 1.4383 | 0 | 1.1703 | 0 | 1.4383 | 1.1703 | 7.9109 | 32.6228 | 6.4725
39029.366 | 2526 | 0 | 39029.366 | 2195 | 0 |  | 756.5 | 908.5 | 154.2125 | 0 | 134.0049 | 0 | 1.5421 | 0 | 1.34 | 0 | 1.5421 | 1.34 | 0.64846 | 15.826 | 0.89367
39029.3681 | 2217 | 0 | 39029.3682 | 2384 | 0 |  | 941 | 1093 | 135.348 | 0 | 145.5433 | 0 | 1.3535 | 0 | 1.4554 | 0 | 1.3535 | 1.4554 | 14.6766 | 6.6435 | 13.3231
39029.3703 | 2102 | 4 | 39029.3703 | 1903 | 10 |  | 1125.5 | 1277.5 | 128.3272 | 0.2442 | 116.1783 | 0.6105 | 1.2833 | 0.002442 | 1.1618 | 0.006105 | 1.2808 | 1.1557 | 21.1066 | 34.6431 | 2806.9665
39029.3724 | 2502 | 0 | 39029.3724 | 1871 | 0 |  | 1310.5 | 1462.5 | 152.7473 | 0 | 114.2247 | 0 | 1.5275 | 0 | 1.1422 | 0 | 1.5275 | 1.1422 | 1.6139 | 35.8835 | 0.086436
39029.3746 | 2526 | 101 | 39029.3746 | 1273 | 805 |  | 1495.5 | 1647.5 | 154.2125 | 6.1661 | 77.7167 | 49.1453 | 1.5421 | 0.061661 | 0.77717 | 0.49145 | 1.4805 | 0.28571 | 1.9965 | 6.2946 | 4.9614
39029.3767 | 1160 | 940 | 39029.3767 | 1077 | 997 |  | 1680 | 1832 | 70.8181 | 57.3871 | 65.7509 | 60.8669 | 0.70818 | 0.57387 | 0.65751 | 0.60867 | 0.13431 | 0.04884 | 440.3739 | 1000.9527 | 42.7871

## D8-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.486 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39029.3573 | 0 | 0 | 39029.3574 | 0 | 0 |  | 9 | 161 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39029.3595 | 0 | 0 | 39029.3595 | 0 | 0 |  | 193.5 | 345.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522376 | 522376 | 522375.9997
39029.3616 | 1957 | 0 | 39029.3616 | 1622 | 0 |  | 378.5 | 530.5 | 119.475 | 0 | 99.0232 | 0 | 1.1947 | 0 | 0.99023 | 0 | 1.1947 | 0.99023 | 33.489 | 61.0592 | 32.2943
39029.3638 | 2185 | 0 | 39029.3638 | 2468 | 0 |  | 563 | 715 | 133.3944 | 0 | 150.6716 | 0 | 1.3339 | 0 | 1.5067 | 0 | 1.3339 | 1.5067 | 19.5597 | 5.8501 | 18.2258
39029.3659 | 2081 | 0 | 39029.3659 | 2059 | 0 |  | 748 | 900 | 127.0452 | 0 | 125.7021 | 0 | 1.2705 | 0 | 1.257 | 0 | 1.2705 | 1.257 | 25.5348 | 26.8762 | 24.2644
39029.368 | 2125 | 0 | 39029.3681 | 2508 | 0 |  | 932.5 | 1084.5 | 129.7314 | 0 | 153.1136 | 0 | 1.2973 | 0 | 1.5311 | 0 | 1.2973 | 1.5311 | 22.9355 | 4.1619 | 21.6382
39029.3702 | 1997 | 0 | 39029.3702 | 2127 | 0 |  | 1117.5 | 1269.5 | 121.917 | 0 | 129.8535 | 0 | 1.2192 | 0 | 1.2985 | 0 | 1.2192 | 1.2985 | 30.8152 | 22.8199 | 29.5961
39029.3723 | 2596 | 0 | 39029.3723 | 2396 | 0 |  | 1302 | 1454 | 158.486 | 0 | 146.2759 | 0 | 1.5849 | 0 | 1.4628 | 0 | 1.5849 | 1.4628 | 0.63097 | 9.0309 | 0.95389
39029.3745 | 2018 | 0 | 39029.3745 | 2527 | 0 |  | 1487 | 1639 | 123.199 | 0 | 154.2735 | 0 | 1.232 | 0 | 1.5427 | 0 | 1.232 | 1.5427 | 29.4539 | 3.3787 | 28.2219
39029.3766 | 2129 | 0 | 39029.3766 | 2213 | 0 |  | 1672 | 1824 | 129.9756 | 0 | 135.1038 | 0 | 1.2998 | 0 | 1.351 | 0 | 1.2998 | 1.351 | 22.7046 | 18.047 | 21.4048

## D8-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 156.4945 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39029.3573 | 0 | 0 | 39029.3573 | 0 | 0 |  | 6 | 158 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
39029.3595 | 0 | 0 | 39029.3595 | 0 | 0 |  | 190.5 | 342.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512576 | 512576 | 512575.9997
39029.3616 | 2229 | 0 | 39029.3616 | 2073 | 0 |  | 375.5 | 527.5 | 136.0806 | 0 | 126.5568 | 0 | 1.3608 | 0 | 1.2656 | 0 | 1.3608 | 1.2656 | 15.0013 | 23.6556 | 13.6405
39029.3637 | 2052 | 0 | 39029.3637 | 2173 | 0 |  | 560.5 | 712.5 | 125.2747 | 0 | 132.6618 | 0 | 1.2527 | 0 | 1.3266 | 0 | 1.2527 | 1.3266 | 24.9211 | 17.965 | 23.6683
39029.3659 | 2219 | 0 | 39029.3659 | 2464 | 0 |  | 745 | 897 | 135.4701 | 0 | 150.4274 | 0 | 1.3547 | 0 | 1.5043 | 0 | 1.3547 | 1.5043 | 15.5196 | 4.0333 | 14.1649
39029.368 | 2039 | 0 | 39029.368 | 2256 | 0 |  | 930 | 1082 | 124.4811 | 0 | 137.7289 | 0 | 1.2448 | 0 | 1.3773 | 0 | 1.2448 | 1.3773 | 25.7175 | 13.625 | 24.4727
39029.3702 | 2064 | 0 | 39029.3702 | 2122 | 0 |  | 1114.5 | 1266.5 | 126.0073 | 0 | 129.5482 | 0 | 1.2601 | 0 | 1.2955 | 0 | 1.2601 | 1.2955 | 24.1948 | 20.8002 | 22.9347
39029.3723 | 2436 | 0 | 39029.3723 | 2402 | 0 |  | 1299.5 | 1451.5 | 148.7179 | 0 | 146.6422 | 0 | 1.4872 | 0 | 1.4664 | 0 | 1.4872 | 1.4664 | 5.2291 | 6.7186 | 3.7419
39029.3744 | 2412 | 0 | 39029.3744 | 1653 | 0 |  | 1484 | 1636 | 147.2527 | 0 | 100.9158 | 0 | 1.4725 | 0 | 1.0092 | 0 | 1.4725 | 1.0092 | 6.2761 | 55.0744 | 4.8036
39029.3766 | 2547 | 0 | 39029.3766 | 1789 | 0 |  | 1669 | 1821 | 155.4945 | 0 | 109.2186 | 0 | 1.5549 | 0 | 1.0922 | 0 | 1.5549 | 1.0922 | 0.64311 | 43.2856 | 0.91184

## D7-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.16 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39029.3572 | 0 | 0 | 39029.3572 | 0 | 0 |  | -2.5 | 149.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39029.3594 | 0 | 0 | 39029.3594 | 0 | 0 |  | 182.5 | 334.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39029.3615 | 2150 | 0 | 39029.3615 | 2211 | 0 |  | 367 | 519 | 131.2576 | 0 | 134.9817 | 0 | 1.3126 | 0 | 1.3498 | 0 | 1.3126 | 1.3498 | 15.9247 | 12.7264 | 14.6121
39029.3636 | 2361 | 0 | 39029.3637 | 2230 | 0 |  | 552 | 704 | 144.1392 | 0 | 136.1416 | 0 | 1.4414 | 0 | 1.3614 | 0 | 1.4414 | 1.3614 | 5.5646 | 11.7659 | 4.1232
39029.3658 | 2051 | 0 | 39029.3658 | 2230 | 0 |  | 736.5 | 888.5 | 125.2137 | 0 | 136.1416 | 0 | 1.2521 | 0 | 1.3614 | 0 | 1.2521 | 1.3614 | 21.5202 | 11.7659 | 20.2681
39029.3679 | 2302 | 0 | 39029.3679 | 2001 | 0 |  | 921.5 | 1073.5 | 140.5372 | 0 | 122.1612 | 0 | 1.4054 | 0 | 1.2216 | 0 | 1.4054 | 1.2216 | 8.2702 | 24.5567 | 6.8648
39029.37 | 2349 | 0 | 39029.3701 | 2155 | 0 |  | 1106 | 1258 | 143.4066 | 0 | 131.5629 | 0 | 1.4341 | 0 | 1.3156 | 0 | 1.4341 | 1.3156 | 6.1039 | 15.6557 | 4.6698
39029.3722 | 2073 | 0 | 39029.3722 | 2476 | 0 |  | 1291 | 1443 | 126.5568 | 0 | 151.16 | 0 | 1.2656 | 0 | 1.5116 | 0 | 1.2656 | 1.5116 | 20.2306 | 0.66155 | 18.965
39029.3743 | 2413 | 0 | 39029.3743 | 1736 | 0 |  | 1475.5 | 1627.5 | 147.3138 | 0 | 105.9829 | 0 | 1.4731 | 0 | 1.0598 | 0 | 1.4731 | 1.0598 | 3.2897 | 43.5703 | 1.8165
39029.3765 | 1993 | 0 | 39029.3765 | 1810 | 0 |  | 1660.5 | 1812.5 | 121.6728 | 0 | 110.5006 | 0 | 1.2167 | 0 | 1.105 | 0 | 1.2167 | 1.105 | 25.0567 | 37.7006 | 23.84

## D7-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.9133 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39029.3572 | 0 | 0 | 39029.3572 | 0 | 0 |  | -5.5 | 146.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523776 | 523776 | 523775.9997
39029.3593 | 0 | 0 | 39029.3593 | 0 | 0 |  | 179.5 | 331.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523776 | 523776 | 523775.9997
39029.3615 | 2103 | 0 | 39029.3615 | 2479 | 0 |  | 364.5 | 516.5 | 128.3883 | 0 | 151.3431 | 0 | 1.2839 | 0 | 1.5134 | 0 | 1.2839 | 1.5134 | 24.5544 | 5.6628 | 23.2706
39029.3636 | 2603 | 0 | 39029.3636 | 2141 | 0 |  | 549 | 701 | 158.9133 | 0 | 130.7082 | 0 | 1.5891 | 0 | 1.3071 | 0 | 1.5891 | 1.3071 | 0.62927 | 22.3438 | 0.95986
39029.3657 | 2343 | 0 | 39029.3658 | 2514 | 0 |  | 734 | 886 | 143.0403 | 0 | 153.4799 | 0 | 1.4304 | 0 | 1.5348 | 0 | 1.4304 | 1.5348 | 11.796 | 4.1917 | 10.3656
39029.3679 | 2558 | 0 | 39029.3679 | 2485 | 0 |  | 918.5 | 1070.5 | 156.1661 | 0 | 151.7094 | 0 | 1.5617 | 0 | 1.5171 | 0 | 1.5617 | 1.5171 | 2.3995 | 5.4076 | 0.83787
39029.37 | 2128 | 0 | 39029.37 | 2077 | 0 |  | 1103.5 | 1255.5 | 129.9145 | 0 | 126.801 | 0 | 1.2991 | 0 | 1.268 | 0 | 1.2991 | 1.268 | 23.0912 | 26.1136 | 21.792
39029.3722 | 2283 | 0 | 39029.3722 | 1986 | 0 |  | 1288 | 1440 | 139.3773 | 0 | 121.2454 | 0 | 1.3938 | 0 | 1.2125 | 0 | 1.3938 | 1.2125 | 14.7341 | 31.8922 | 13.3403
39029.3743 | 2376 | 0 | 39029.3743 | 1284 | 0 |  | 1473 | 1625 | 145.0549 | 0 | 78.3883 | 0 | 1.4505 | 0 | 0.78388 | 0 | 1.4505 | 0.78388 | 10.2433 | 104.0016 | 8.7927
39029.3764 | 2438 | 0 | 39029.3764 | 2186 | 0 |  | 1657.5 | 1809.5 | 148.84 | 0 | 133.4554 | 0 | 1.4884 | 0 | 1.3346 | 0 | 1.4884 | 1.3346 | 7.4397 | 19.8253 | 5.9513

## D7-D8
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.8291 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39029.3572 | 0 | 0 | 39029.3572 | 0 | 0 |  | -8 | 144 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526776 | 526776 | 526775.9997
39029.3593 | 0 | 0 | 39029.3593 | 0 | 0 |  | 177 | 329 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 526776 | 526776 | 526775.9997
39029.3614 | 2086 | 0 | 39029.3614 | 2433 | 0 |  | 361.5 | 513.5 | 127.3504 | 0 | 148.5348 | 0 | 1.2735 | 0 | 1.4853 | 0 | 1.2735 | 1.4853 | 26.2886 | 8.277 | 25.0151
39029.3636 | 2253 | 0 | 39029.3636 | 2131 | 0 |  | 546.5 | 698.5 | 137.5458 | 0 | 130.0977 | 0 | 1.3755 | 0 | 1.301 | 0 | 1.3755 | 1.301 | 16.9277 | 23.6218 | 15.5522
39029.3657 | 2049 | 0 | 39029.3657 | 2618 | 0 |  | 731 | 883 | 125.0916 | 0 | 159.8291 | 0 | 1.2509 | 0 | 1.5983 | 0 | 1.2509 | 1.5983 | 28.5691 | 0.62567 | 27.3181
39029.3678 | 2042 | 0 | 39029.3679 | 2398 | 0 |  | 916 | 1068 | 124.6642 | 0 | 146.398 | 0 | 1.2466 | 0 | 1.464 | 0 | 1.2466 | 1.464 | 29.0098 | 9.8574 | 27.7632
39029.37 | 2388 | 0 | 39029.37 | 2529 | 0 |  | 1100.5 | 1252.5 | 145.7875 | 0 | 154.3956 | 0 | 1.4579 | 0 | 1.544 | 0 | 1.4579 | 1.544 | 10.3174 | 4.1669 | 8.8595
39029.3721 | 2109 | 0 | 39029.3721 | 2614 | 0 |  | 1285.5 | 1437.5 | 128.7546 | 0 | 159.5849 | 0 | 1.2875 | 0 | 1.5958 | 0 | 1.2875 | 1.5958 | 24.9113 | 0.77965 | 23.6238
39029.3743 | 2217 | 0 | 39029.3743 | 2597 | 0 |  | 1470 | 1622 | 135.348 | 0 | 158.547 | 0 | 1.3535 | 0 | 1.5855 | 0 | 1.3535 | 1.5855 | 18.8263 | 1.4394 | 17.4729
39029.3764 | 2018 | 0 | 39029.3764 | 2137 | 0 |  | 1655 | 1807 | 123.199 | 0 | 130.464 | 0 | 1.232 | 0 | 1.3046 | 0 | 1.232 | 1.3046 | 30.5441 | 23.2747 | 29.3121

## C6-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 153.5031 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39029.3571 | 0 | 0 | 39029.3571 | 0 | 0 |  | -11 | 141 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502776 | 502776 | 502775.9997
39029.3593 | 0 | 0 | 39029.3593 | 0 | 0 |  | 174 | 326 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 502776 | 502776 | 502775.9997
39029.3614 | 4 | 0 | 39029.3614 | 2156 | 0 |  | 358.5 | 510.5 | 0.2442 | 0 | 131.6239 | 0 | 0.002442 | 0 | 1.3162 | 0 | 0.002442 | 1.3162 | 62759.5 | 16.6224 | 62759.4976
39029.3635 | 2442 | 0 | 39029.3636 | 2284 | 0 |  | 543.5 | 695.5 | 149.0842 | 0 | 139.4383 | 0 | 1.4908 | 0 | 1.3944 | 0 | 1.4908 | 1.3944 | 2.964 | 10.0867 | 1.4731
39029.3657 | 2026 | 0 | 39029.3657 | 2119 | 0 |  | 728.5 | 880.5 | 123.6874 | 0 | 129.3651 | 0 | 1.2369 | 0 | 1.2937 | 0 | 1.2369 | 1.2937 | 24.1056 | 18.6588 | 22.8688
39029.3678 | 2458 | 0 | 39029.3678 | 2276 | 0 |  | 913 | 1065 | 150.0611 | 0 | 138.9499 | 0 | 1.5006 | 0 | 1.3895 | 0 | 1.5006 | 1.3895 | 2.2937 | 10.4736 | 0.79312
39029.37 | 2358 | 0 | 39029.37 | 2274 | 0 |  | 1097.5 | 1249.5 | 143.956 | 0 | 138.8278 | 0 | 1.4396 | 0 | 1.3883 | 0 | 1.4396 | 1.3883 | 6.6319 | 10.5708 | 5.1923
39029.3721 | 2239 | 0 | 39029.3721 | 2113 | 0 |  | 1282.5 | 1434.5 | 136.6911 | 0 | 128.9988 | 0 | 1.3669 | 0 | 1.29 | 0 | 1.3669 | 1.29 | 12.2992 | 18.9957 | 10.9323
39029.3742 | 2058 | 0 | 39029.3742 | 2167 | 0 |  | 1467.5 | 1619.5 | 125.641 | 0 | 132.2955 | 0 | 1.2564 | 0 | 1.323 | 0 | 1.2564 | 1.323 | 22.1759 | 16.0305 | 20.9195
39029.3764 | 1755 | 0 | 39029.3764 | 2498 | 0 |  | 1652 | 1804 | 107.1429 | 0 | 152.5031 | 0 | 1.0714 | 0 | 1.525 | 0 | 1.0714 | 1.525 | 43.2695 | 0.65572 | 42.1981

## C6-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.1197 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39029.3571 | 0 | 0 | 39029.3571 | 0 | 0 |  | -13.5 | 138.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39029.3592 | 0 | 0 | 39029.3592 | 0 | 0 |  | 171 | 323 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521176 | 521176 | 521175.9997
39029.3614 | 4 | 0 | 39029.3614 | 1814 | 3 |  | 356 | 508 | 0.2442 | 0 | 110.7448 | 0.18315 | 0.002442 | 0 | 1.1074 | 0.0018315 | 0.002442 | 1.1056 | 65059.5 | 43.9194 | 65059.4976
39029.3635 | 2412 | 0 | 39029.3635 | 1998 | 0 |  | 540.5 | 692.5 | 147.2527 | 0 | 121.978 | 0 | 1.4725 | 0 | 1.2198 | 0 | 1.4725 | 1.2198 | 8.0589 | 30.4494 | 6.5863
39029.3656 | 2167 | 0 | 39029.3657 | 2222 | 0 |  | 725.5 | 877.5 | 132.2955 | 0 | 135.6532 | 0 | 1.323 | 0 | 1.3565 | 0 | 1.323 | 1.3565 | 20.276 | 17.2988 | 18.953
39029.3678 | 2468 | 0 | 39029.3678 | 2502 | 0 |  | 910 | 1062 | 150.6716 | 0 | 152.7473 | 0 | 1.5067 | 0 | 1.5275 | 0 | 1.5067 | 1.5275 | 5.607 | 4.1719 | 4.1003
39029.3699 | 1992 | 0 | 39029.3699 | 2065 | 0 |  | 1095 | 1247 | 121.6117 | 0 | 126.0684 | 0 | 1.2161 | 0 | 1.2607 | 0 | 1.2161 | 1.2607 | 30.8424 | 26.2169 | 29.6263
39029.3721 | 2317 | 0 | 39029.3721 | 2110 | 0 |  | 1279.5 | 1431.5 | 141.453 | 0 | 128.8156 | 0 | 1.4145 | 0 | 1.2882 | 0 | 1.4145 | 1.2882 | 12.4894 | 23.5251 | 11.0749
39029.3742 | 2068 | 0 | 39029.3742 | 2590 | 0 |  | 1464.5 | 1616.5 | 126.2515 | 0 | 158.1197 | 0 | 1.2625 | 0 | 1.5812 | 0 | 1.2625 | 1.5812 | 26.0338 | 0.63243 | 24.7713
39029.3763 | 1804 | 0 | 39029.3764 | 2511 | 0 |  | 1649.5 | 1801.5 | 110.1343 | 0 | 153.2967 | 0 | 1.1013 | 0 | 1.533 | 0 | 1.1013 | 1.533 | 44.4778 | 3.7985 | 43.3765

## C6-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 151.8547 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39029.3571 | 0 | 0 | 39029.3571 | 0 | 0 |  | -16.5 | 135.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497376 | 497376 | 497375.9997
39029.3592 | 0 | 0 | 39029.3592 | 0 | 0 |  | 168.5 | 320.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497376 | 497376 | 497375.9997
39029.3613 | 4 | 0 | 39029.3614 | 2320 | 0 |  | 353 | 505 | 0.2442 | 0 | 141.6361 | 0 | 0.002442 | 0 | 1.4164 | 0 | 0.002442 | 1.4164 | 62084.5 | 7.2147 | 62084.4976
39029.3635 | 2083 | 0 | 39029.3635 | 1975 | 0 |  | 538 | 690 | 127.1673 | 0 | 120.5739 | 0 | 1.2717 | 0 | 1.2057 | 0 | 1.2717 | 1.2057 | 19.4133 | 25.9433 | 18.1417
39029.3656 | 2471 | 0 | 39029.3656 | 2325 | 0 |  | 722.5 | 874.5 | 150.8547 | 0 | 141.9414 | 0 | 1.5085 | 0 | 1.4194 | 0 | 1.5085 | 1.4194 | 0.66289 | 6.9841 | 0.84566
39029.3678 | 2290 | 0 | 39029.3678 | 2004 | 0 |  | 907.5 | 1059.5 | 139.8046 | 0 | 122.3443 | 0 | 1.398 | 0 | 1.2234 | 0 | 1.398 | 1.2234 | 8.6192 | 24.1208 | 7.2212
39029.3699 | 2174 | 0 | 39029.3699 | 2295 | 0 |  | 1092 | 1244 | 132.7228 | 0 | 140.1099 | 0 | 1.3272 | 0 | 1.4011 | 0 | 1.3272 | 1.4011 | 14.4149 | 8.3826 | 13.0877
39029.372 | 2448 | 0 | 39029.372 | 1974 | 0 |  | 1277 | 1429 | 149.4505 | 0 | 120.5128 | 0 | 1.4945 | 0 | 1.2051 | 0 | 1.4945 | 1.2051 | 1.6087 | 26.0071 | 0.11415
39029.3742 | 2212 | 0 | 39029.3742 | 2240 | 2 |  | 1461.5 | 1613.5 | 135.0427 | 0 | 136.7521 | 0.1221 | 1.3504 | 0 | 1.3675 | 0.001221 | 1.3504 | 1.3663 | 12.4494 | 11.143 | 11.0989
39029.3763 | 2186 | 1 | 39029.3763 | 1828 | 0 |  | 1646.5 | 1798.5 | 133.4554 | 0.06105 | 111.5995 | 0 | 1.3346 | 0.0006105 | 1.116 | 0 | 1.3339 | 1.116 | 13.8107 | 36.0711 | 7962.7787

## C6-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 157.2882 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39029.357 | 0 | 0 | 39029.357 | 0 | 0 |  | -19.5 | 132.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39029.3592 | 0 | 0 | 39029.3592 | 0 | 0 |  | 165.5 | 317.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39029.3613 | 4 | 0 | 39029.3613 | 2210 | 0 |  | 350.5 | 502.5 | 0.2442 | 0 | 134.9206 | 0 | 0.002442 | 0 | 1.3492 | 0 | 0.002442 | 1.3492 | 64309.5 | 16.5783 | 64309.4976
39029.3634 | 2080 | 0 | 39029.3635 | 2551 | 0 |  | 535 | 687 | 126.9841 | 0 | 155.7387 | 0 | 1.2698 | 0 | 1.5574 | 0 | 1.2698 | 1.5574 | 23.8644 | 0.9949 | 22.5946
39029.3656 | 2319 | 0 | 39029.3656 | 2431 | 0 |  | 720 | 872 | 141.5751 | 0 | 148.4127 | 0 | 1.4158 | 0 | 1.4841 | 0 | 1.4158 | 1.4841 | 11.0987 | 5.9803 | 9.683
39029.3677 | 2080 | 0 | 39029.3677 | 2560 | 0 |  | 904.5 | 1056.5 | 126.9841 | 0 | 156.2882 | 0 | 1.2698 | 0 | 1.5629 | 0 | 1.2698 | 1.5629 | 23.8644 | 0.63984 | 22.5946
39029.3699 | 2497 | 0 | 39029.3699 | 2505 | 0 |  | 1089.5 | 1241.5 | 152.442 | 0 | 152.9304 | 0 | 1.5244 | 0 | 1.5293 | 0 | 1.5244 | 1.5293 | 3.179 | 2.8495 | 1.6546
39029.372 | 2215 | 0 | 39029.372 | 2391 | 0 |  | 1274 | 1426 | 135.2259 | 0 | 145.9707 | 0 | 1.3523 | 0 | 1.4597 | 0 | 1.3523 | 1.4597 | 16.3151 | 7.7532 | 14.9629
39029.3741 | 2005 | 0 | 39029.3742 | 1252 | 0 |  | 1459 | 1611 | 122.4054 | 0 | 76.4347 | 0 | 1.2241 | 0 | 0.76435 | 0 | 1.2241 | 0.76435 | 28.4978 | 105.7812 | 27.2737
39029.3763 | 1543 | 0 | 39029.3763 | 2326 | 0 |  | 1644 | 1796 | 94.2002 | 0 | 142.0024 | 0 | 0.942 | 0 | 1.42 | 0 | 0.942 | 1.42 | 66.9721 | 10.7644 | 66.0301

## C5-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39029.3569 | 0 | 0 | 39029.3569 | 0 | 0 |  | -27.5 | 124.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39029.3591 | 0 | 0 | 39029.3591 | 0 | 0 |  | 157.5 | 309.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517776 | 517776 | 517775.9997
39029.3612 | 4 | 0 | 39029.3612 | 2573 | 0 |  | 342 | 494 | 0.2442 | 0 | 157.0818 | 0 | 0.002442 | 0 | 1.5708 | 0 | 0.002442 | 1.5708 | 64634.5 | 0.63661 | 64634.4976
39029.3633 | 2530 | 0 | 39029.3634 | 2053 | 0 |  | 526.5 | 678.5 | 154.4567 | 0 | 125.3358 | 0 | 1.5446 | 0 | 1.2534 | 0 | 1.5446 | 1.2534 | 2.347 | 26.1266 | 0.80247
39029.3655 | 1958 | 0 | 39029.3655 | 2079 | 0 |  | 711.5 | 863.5 | 119.536 | 0 | 126.9231 | 0 | 1.1954 | 0 | 1.2692 | 0 | 1.1954 | 1.2692 | 32.2462 | 24.5493 | 31.0508
39029.3676 | 2103 | 0 | 39029.3676 | 2374 | 0 |  | 896.5 | 1048.5 | 128.3883 | 0 | 144.9328 | 0 | 1.2839 | 0 | 1.4493 | 0 | 1.2839 | 1.4493 | 23.1279 | 9.0725 | 21.844
39029.3698 | 2520 | 0 | 39029.3698 | 2354 | 0 |  | 1081 | 1233 | 153.8462 | 0 | 143.7118 | 0 | 1.5385 | 0 | 1.4371 | 0 | 1.5385 | 1.4371 | 2.7532 | 9.9992 | 1.2147
39029.3719 | 1996 | 0 | 39029.3719 | 2324 | 0 |  | 1265.5 | 1417.5 | 121.8559 | 0 | 141.8803 | 0 | 1.2186 | 0 | 1.4188 | 0 | 1.2186 | 1.4188 | 29.7285 | 11.4191 | 28.5099
39029.374 | 2267 | 0 | 39029.3741 | 2277 | 0 |  | 1450.5 | 1602.5 | 138.4005 | 0 | 139.011 | 0 | 1.384 | 0 | 1.3901 | 0 | 1.384 | 1.3901 | 14.2206 | 13.7189 | 12.8366
39029.3762 | 1730 | 1 | 39029.3762 | 2567 | 0 |  | 1635.5 | 1787.5 | 105.6166 | 0.06105 | 156.7155 | 0 | 1.0562 | 0.0006105 | 1.5672 | 0 | 1.0556 | 1.5672 | 53.2355 | 0.87183 | 741.8975

## C5-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.6081 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39029.3569 | 0 | 0 | 39029.3569 | 0 | 0 |  | -30.5 | 121.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522776 | 522776 | 522775.9997
39029.359 | 0 | 0 | 39029.3591 | 0 | 0 |  | 154.5 | 306.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 522776 | 522776 | 522775.9997
39029.3612 | 4 | 0 | 39029.3612 | 2062 | 0 |  | 339 | 491 | 0.2442 | 0 | 125.8852 | 0 | 0.002442 | 0 | 1.2589 | 0 | 0.002442 | 1.2589 | 65259.5 | 26.7886 | 65259.4976
39029.3633 | 2088 | 0 | 39029.3633 | 2251 | 0 |  | 524 | 676 | 127.4725 | 0 | 137.4237 | 0 | 1.2747 | 0 | 1.3742 | 0 | 1.2747 | 1.3742 | 25.2098 | 16.143 | 23.935
39029.3655 | 2267 | 0 | 39029.3655 | 1973 | 0 |  | 708.5 | 860.5 | 138.4005 | 0 | 120.4518 | 0 | 1.384 | 0 | 1.2045 | 0 | 1.384 | 1.2045 | 15.3233 | 32.5079 | 13.9393
39029.3676 | 2237 | 0 | 39029.3676 | 2273 | 0 |  | 893.5 | 1045.5 | 136.569 | 0 | 138.7668 | 0 | 1.3657 | 0 | 1.3877 | 0 | 1.3657 | 1.3877 | 16.8699 | 15.0189 | 15.5042
39029.3697 | 2029 | 0 | 39029.3697 | 2549 | 0 |  | 1078.5 | 1230.5 | 123.8706 | 0 | 155.6166 | 0 | 1.2387 | 0 | 1.5562 | 0 | 1.2387 | 1.5562 | 28.8507 | 2.5649 | 27.612
39029.3719 | 1882 | 0 | 39029.3719 | 2570 | 0 |  | 1263 | 1415 | 114.8962 | 0 | 156.8987 | 0 | 1.149 | 0 | 1.569 | 0 | 1.149 | 1.569 | 38.915 | 1.7268 | 37.766
39029.374 | 2399 | 0 | 39029.374 | 2598 | 0 |  | 1447.5 | 1599.5 | 146.4591 | 0 | 158.6081 | 0 | 1.4646 | 0 | 1.5861 | 0 | 1.4646 | 1.5861 | 8.9779 | 0.63048 | 7.5133
39029.3761 | 1829 | 0 | 39029.3762 | 2318 | 0 |  | 1632.5 | 1784.5 | 111.6606 | 0 | 141.514 | 0 | 1.1166 | 0 | 1.4151 | 0 | 1.1166 | 1.4151 | 42.9404 | 12.786 | 41.8238

## C5-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.7912 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39029.3569 | 0 | 0 | 39029.3569 | 0 | 0 |  | -33.5 | 118.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523376 | 523376 | 523375.9997
39029.359 | 0 | 0 | 39029.359 | 0 | 0 |  | 151.5 | 303.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523376 | 523376 | 523375.9997
39029.3611 | 3 | 0 | 39029.3612 | 2601 | 0 |  | 336.5 | 488.5 | 0.18315 | 0 | 158.7912 | 0 | 0.0018315 | 0 | 1.5879 | 0 | 0.0018315 | 1.5879 | 87146 | 0.62976 | 87145.9982
39029.3633 | 2162 | 0 | 39029.3633 | 2036 | 0 |  | 521 | 673 | 131.9902 | 0 | 124.2979 | 0 | 1.3199 | 0 | 1.243 | 0 | 1.3199 | 1.243 | 21.0629 | 28.555 | 19.743
39029.3654 | 2094 | 0 | 39029.3654 | 2196 | 0 |  | 706 | 858 | 127.8388 | 0 | 134.0659 | 0 | 1.2784 | 0 | 1.3407 | 0 | 1.2784 | 1.3407 | 24.9943 | 19.1885 | 23.7159
39029.3676 | 2365 | 0 | 39029.3676 | 2231 | 0 |  | 890.5 | 1042.5 | 144.3834 | 0 | 136.2027 | 0 | 1.4438 | 0 | 1.362 | 0 | 1.4438 | 1.362 | 10.6715 | 17.3187 | 9.2276
39029.3697 | 2124 | 0 | 39029.3697 | 2296 | 0 |  | 1075.5 | 1227.5 | 129.6703 | 0 | 140.1709 | 0 | 1.2967 | 0 | 1.4017 | 0 | 1.2967 | 1.4017 | 23.2288 | 13.9974 | 21.9321
39029.3718 | 1946 | 0 | 39029.3719 | 2451 | 0 |  | 1260 | 1412 | 118.8034 | 0 | 149.6337 | 0 | 1.188 | 0 | 1.4963 | 0 | 1.188 | 1.4963 | 34.5005 | 6.7882 | 33.3125
39029.374 | 1887 | 0 | 39029.374 | 1436 | 0 |  | 1445 | 1597 | 115.2015 | 0 | 87.6679 | 0 | 1.152 | 0 | 0.87668 | 0 | 1.152 | 0.87668 | 38.7059 | 82.2688 | 37.5539
39029.3761 | 1901 | 0 | 39029.3761 | 2213 | 0 |  | 1629.5 | 1781.5 | 116.0562 | 0 | 135.1038 | 0 | 1.1606 | 0 | 1.351 | 0 | 1.1606 | 1.351 | 37.6844 | 18.2729 | 36.5238

## C5-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.6313 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39029.3568 | 0 | 0 | 39029.3569 | 0 | 0 |  | -36 | 116 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519576 | 519576 | 519575.9997
39029.359 | 0 | 0 | 39029.359 | 0 | 0 |  | 148.5 | 300.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519576 | 519576 | 519575.9997
39029.3611 | 5 | 0 | 39029.3611 | 3 | 0 |  | 333.5 | 485.5 | 0.30525 | 0 | 0.18315 | 0 | 0.0030525 | 0 | 0.0018315 | 0 | 0.0030525 | 0.0018315 | 51867.6 | 86512.6667 | 51867.5969
39029.3633 | 1951 | 0 | 39029.3633 | 2257 | 0 |  | 518.5 | 670.5 | 119.1087 | 0 | 137.79 | 0 | 1.1911 | 0 | 1.3779 | 0 | 1.1911 | 1.3779 | 33.182 | 15.1254 | 31.9909
39029.3654 | 2084 | 0 | 39029.3654 | 2515 | 0 |  | 703 | 855 | 127.2283 | 0 | 153.5409 | 0 | 1.2723 | 0 | 1.5354 | 0 | 1.2723 | 1.5354 | 24.6823 | 3.3153 | 23.4101
39029.3675 | 2475 | 0 | 39029.3675 | 2386 | 0 |  | 888 | 1040 | 151.0989 | 0 | 145.6654 | 0 | 1.511 | 0 | 1.4567 | 0 | 1.511 | 1.4567 | 4.9851 | 8.9011 | 3.4741
39029.3697 | 2185 | 0 | 39029.3697 | 2432 | 0 |  | 1072.5 | 1224.5 | 133.3944 | 0 | 148.4737 | 0 | 1.3339 | 0 | 1.4847 | 0 | 1.3339 | 1.4847 | 18.919 | 6.8413 | 17.585
39029.3718 | 2446 | 0 | 39029.3718 | 2582 | 0 |  | 1257.5 | 1409.5 | 149.3284 | 0 | 157.6313 | 0 | 1.4933 | 0 | 1.5763 | 0 | 1.4933 | 1.5763 | 6.2298 | 0.63439 | 4.7365
39029.3739 | 1875 | 0 | 39029.374 | 1672 | 0 |  | 1442 | 1594 | 114.4689 | 0 | 102.0757 | 0 | 1.1447 | 0 | 1.0208 | 0 | 1.1447 | 1.0208 | 38.5803 | 55.4055 | 37.4356
39029.3761 | 2047 | 0 | 39029.3761 | 2012 | 0 |  | 1627 | 1779 | 124.9695 | 0 | 122.8327 | 0 | 1.2497 | 0 | 1.2283 | 0 | 1.2497 | 1.2283 | 26.936 | 29.1441 | 25.6863

## C5-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 149.7179 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39029.3567 | 0 | 0 | 39029.3567 | 0 | 0 |  | -44.5 | 107.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
39029.3589 | 0 | 0 | 39029.3589 | 0 | 0 |  | 140.5 | 292.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 490376 | 490376 | 490375.9997
39029.361 | 5 | 0 | 39029.361 | 3 | 0 |  | 325 | 477 | 0.30525 | 0 | 0.18315 | 0 | 0.0030525 | 0 | 0.0018315 | 0 | 0.0030525 | 0.0018315 | 48947.6 | 81646 | 48947.5969
39029.3631 | 1515 | 182 | 39029.3632 | 1542 | 4 |  | 510 | 662 | 92.4908 | 11.1111 | 94.1392 | 0.2442 | 0.92491 | 0.11111 | 0.94139 | 0.002442 | 0.8138 | 0.93895 | 91.3266 | 59.3615 | 154.6022
39029.3653 | 1938 | 5 | 39029.3653 | 2436 | 6 |  | 694.5 | 846.5 | 118.315 | 0.30525 | 148.7179 | 0.3663 | 1.1832 | 0.0030525 | 1.4872 | 0.003663 | 1.1801 | 1.4835 | 43.0264 | 0.67796 | 68.6032
39029.3674 | 2158 | 1 | 39029.3674 | 2057 | 0 |  | 879.5 | 1031.5 | 131.746 | 0.06105 | 125.58 | 0 | 1.3175 | 0.0006105 | 1.2558 | 0 | 1.3168 | 1.2558 | 13.6807 | 19.2212 | 4729.9596
39029.3696 | 1927 | 0 | 39029.3696 | 2122 | 1 |  | 1064.5 | 1216.5 | 117.6435 | 0 | 129.5482 | 0.06105 | 1.1764 | 0 | 1.2955 | 0.0006105 | 1.1764 | 1.2949 | 27.2641 | 15.6238 | 26.0877
39029.3717 | 2146 | 8 | 39029.3717 | 2359 | 7 |  | 1249 | 1401 | 131.0134 | 0.4884 | 144.0171 | 0.42735 | 1.3101 | 0.004884 | 1.4402 | 0.0042735 | 1.3053 | 1.4359 | 15.7904 | 4.0465 | 145.0549
39029.3738 | 1989 | 5 | 39029.3739 | 2055 | 7 |  | 1433.5 | 1585.5 | 121.4286 | 0.30525 | 125.4579 | 0.42735 | 1.2143 | 0.0030525 | 1.2546 | 0.0042735 | 1.2112 | 1.2503 | 23.6587 | 19.6877 | 1508.0024
39029.376 | 1557 | 633 | 39029.376 | 1161 | 1035 |  | 1618.5 | 1770.5 | 95.0549 | 38.6447 | 70.8791 | 63.1868 | 0.95055 | 0.38645 | 0.70879 | 0.63187 | 0.5641 | 0.076923 | 45.005 | 59.4081 | 15.4477

## B4-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 150.4505 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39029.3566 | 0 | 0 | 39029.3567 | 0 | 0 |  | -52.5 | 99.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492776 | 492776 | 492775.9997
39029.3588 | 0 | 0 | 39029.3588 | 0 | 0 |  | 132 | 284 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492776 | 492776 | 492775.9997
39029.3609 | 2 | 0 | 39029.3609 | 2448 | 0 |  | 316.5 | 468.5 | 0.1221 | 0 | 149.4505 | 0 | 0.001221 | 0 | 1.4945 | 0 | 0.001221 | 1.4945 | 123119 | 0.66912 | 123118.9988
39029.3631 | 1206 | 0 | 39029.3631 | 2402 | 0 |  | 501.5 | 653.5 | 73.6264 | 0 | 146.6422 | 0 | 0.73626 | 0 | 1.4664 | 0 | 0.73626 | 1.4664 | 104.3433 | 2.597 | 103.607
39029.3652 | 1950 | 0 | 39029.3652 | 2281 | 0 |  | 686.5 | 838.5 | 119.0476 | 0 | 139.2552 | 0 | 1.1905 | 0 | 1.3926 | 0 | 1.1905 | 1.3926 | 26.3785 | 8.0395 | 25.188
39029.3673 | 1424 | 0 | 39029.3673 | 2285 | 0 |  | 871 | 1023 | 86.9353 | 0 | 139.4994 | 0 | 0.86935 | 0 | 1.395 | 0 | 0.86935 | 1.395 | 73.0604 | 7.8503 | 72.191
39029.3695 | 1771 | 0 | 39029.3695 | 2346 | 0 |  | 1056 | 1208 | 108.1197 | 0 | 143.2234 | 0 | 1.0812 | 0 | 1.4322 | 0 | 1.0812 | 1.4322 | 39.1519 | 5.046 | 38.0707
39029.3716 | 1752 | 0 | 39029.3716 | 1955 | 0 |  | 1240.5 | 1392.5 | 106.9597 | 0 | 119.3529 | 0 | 1.0696 | 0 | 1.1935 | 0 | 1.0696 | 1.1935 | 40.661 | 26.0552 | 39.5914
39029.3737 | 420 | 0 | 39029.3738 | 1659 | 0 |  | 1425.5 | 1577.5 | 25.641 | 0 | 101.2821 | 0 | 0.25641 | 0 | 1.0128 | 0 | 0.25641 | 1.0128 | 486.7571 | 48.5461 | 486.5007
39029.3759 | 53 | 0 | 39029.3759 | 2140 | 0 |  | 1610 | 1762 | 3.2357 | 0 | 130.6471 | 0 | 0.032357 | 0 | 1.3065 | 0 | 0.032357 | 1.3065 | 4549.7736 | 15.1579 | 4549.7412

## B4-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 150.0842 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39029.3566 | 0 | 0 | 39029.3566 | 0 | 0 |  | -55.5 | 96.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 491576 | 491576 | 491575.9997
39029.3587 | 0 | 0 | 39029.3588 | 0 | 0 |  | 129 | 281 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 491576 | 491576 | 491575.9997
39029.3609 | 5 | 0 | 39029.3609 | 3 | 0 |  | 314 | 466 | 0.30525 | 0 | 0.18315 | 0 | 0.0030525 | 0 | 0.0018315 | 0 | 0.0030525 | 0.0018315 | 49067.6 | 81846 | 49067.5969
39029.363 | 1139 | 0 | 39029.363 | 2091 | 0 |  | 498.5 | 650.5 | 69.536 | 0 | 127.6557 | 0 | 0.69536 | 0 | 1.2766 | 0 | 0.69536 | 1.2766 | 115.8367 | 17.5696 | 115.1413
39029.3652 | 1996 | 0 | 39029.3652 | 2442 | 0 |  | 683.5 | 835.5 | 121.8559 | 0 | 149.0842 | 0 | 1.2186 | 0 | 1.4908 | 0 | 1.2186 | 1.4908 | 23.1653 | 0.67076 | 21.9468
39029.3673 | 1632 | 0 | 39029.3673 | 2207 | 0 |  | 868.5 | 1020.5 | 99.6337 | 0 | 134.7375 | 0 | 0.99634 | 0 | 1.3474 | 0 | 0.99634 | 1.3474 | 50.636 | 11.3901 | 49.6397
39029.3694 | 1544 | 0 | 39029.3695 | 2049 | 0 |  | 1053 | 1205 | 94.2613 | 0 | 125.0916 | 0 | 0.94261 | 0 | 1.2509 | 0 | 0.94261 | 1.2509 | 59.2215 | 19.9795 | 58.2789
39029.3716 | 691 | 0 | 39029.3716 | 2339 | 0 |  | 1237.5 | 1389.5 | 42.1856 | 0 | 142.7961 | 0 | 0.42186 | 0 | 1.428 | 0 | 0.42186 | 1.428 | 255.7713 | 5.1039 | 255.3495
39029.3737 | 485 | 0 | 39029.3737 | 2239 | 0 |  | 1422.5 | 1574.5 | 29.6093 | 0 | 136.6911 | 0 | 0.29609 | 0 | 1.3669 | 0 | 0.29609 | 1.3669 | 406.8825 | 9.7981 | 406.5864
39029.3759 | 65 | 0 | 39029.3759 | 1854 | 0 |  | 1607.5 | 1759.5 | 3.9683 | 0 | 113.1868 | 0 | 0.039683 | 0 | 1.1319 | 0 | 0.039683 | 1.1319 | 3682.1231 | 32.5987 | 3682.0834

## B4-D8
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.2186 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39029.3566 | 0 | 0 | 39029.3566 | 0 | 0 |  | -58.5 | 93.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39029.3587 | 0 | 0 | 39029.3587 | 0 | 0 |  | 126.5 | 278.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524776 | 524776 | 524775.9997
39029.3608 | 4 | 0 | 39029.3609 | 2533 | 0 |  | 311 | 463 | 0.2442 | 0 | 154.6398 | 0 | 0.002442 | 0 | 1.5464 | 0 | 0.002442 | 1.5464 | 65509.5 | 3.6076 | 65509.4976
39029.363 | 1222 | 0 | 39029.363 | 2261 | 0 |  | 496 | 648 | 74.6032 | 0 | 138.0342 | 0 | 0.74603 | 0 | 1.3803 | 0 | 0.74603 | 1.3803 | 114.761 | 16.0716 | 114.015
39029.3651 | 2079 | 0 | 39029.3651 | 2179 | 0 |  | 680.5 | 832.5 | 126.9231 | 0 | 133.0281 | 0 | 1.2692 | 0 | 1.3303 | 0 | 1.2692 | 1.3303 | 26.2328 | 20.4397 | 24.9636
39029.3673 | 1625 | 0 | 39029.3673 | 2060 | 0 |  | 865.5 | 1017.5 | 99.2063 | 0 | 125.7631 | 0 | 0.99206 | 0 | 1.2576 | 0 | 0.99206 | 1.2576 | 61.5003 | 27.3971 | 60.5082
39029.3694 | 1414 | 0 | 39029.3694 | 2595 | 0 |  | 1050.5 | 1202.5 | 86.3248 | 0 | 158.4249 | 0 | 0.86325 | 0 | 1.5842 | 0 | 0.86325 | 1.5842 | 85.5997 | 1.1322 | 84.7365
39029.3715 | 1478 | 0 | 39029.3716 | 2506 | 0 |  | 1235 | 1387 | 90.232 | 0 | 152.9915 | 0 | 0.90232 | 0 | 1.5299 | 0 | 0.90232 | 1.5299 | 77.5629 | 4.7239 | 76.6606
39029.3737 | 440 | 0 | 39029.3737 | 2608 | 0 |  | 1419.5 | 1571.5 | 26.862 | 0 | 159.2186 | 0 | 0.26862 | 0 | 1.5922 | 0 | 0.26862 | 1.5922 | 496.45 | 0.62807 | 496.1814
39029.3758 | 47 | 0 | 39029.3758 | 2600 | 0 |  | 1604.5 | 1756.5 | 2.8694 | 0 | 158.7302 | 0 | 0.028694 | 0 | 1.5873 | 0 | 0.028694 | 1.5873 | 5483.7872 | 0.93769 | 5483.7585

## B4-D7
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.0354 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39029.3565 | 0 | 0 | 39029.3566 | 0 | 0 |  | -61.5 | 90.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524176 | 524176 | 524175.9997
39029.3587 | 0 | 0 | 39029.3587 | 0 | 0 |  | 123.5 | 275.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524176 | 524176 | 524175.9997
39029.3608 | 1 | 0 | 39029.3608 | 2605 | 0 |  | 308.5 | 460.5 | 0.06105 | 0 | 159.0354 | 0 | 0.0006105 | 0 | 1.5904 | 0 | 0.0006105 | 1.5904 | 262038 | 0.62879 | 262037.9994
39029.363 | 1286 | 0 | 39029.363 | 2542 | 0 |  | 493 | 645 | 78.5104 | 0 | 155.1893 | 0 | 0.7851 | 0 | 1.5519 | 0 | 0.7851 | 1.5519 | 103.8398 | 3.1227 | 103.0547
39029.3651 | 2107 | 0 | 39029.3651 | 1995 | 0 |  | 678 | 830 | 128.6325 | 0 | 121.7949 | 0 | 1.2863 | 0 | 1.2179 | 0 | 1.2863 | 1.2179 | 24.4129 | 31.3975 | 23.1266
39029.3672 | 1338 | 0 | 39029.3672 | 2184 | 0 |  | 862.5 | 1014.5 | 81.685 | 0 | 133.3333 | 0 | 0.81685 | 0 | 1.3333 | 0 | 0.81685 | 1.3333 | 95.9178 | 20.0266 | 95.1009
39029.3694 | 1844 | 0 | 39029.3694 | 2412 | 0 |  | 1047.5 | 1199.5 | 112.5763 | 0 | 147.2527 | 0 | 1.1258 | 0 | 1.4725 | 0 | 1.1258 | 1.4725 | 42.1573 | 8.6808 | 41.0315
39029.3715 | 641 | 0 | 39029.3715 | 2406 | 0 |  | 1232 | 1384 | 39.1331 | 0 | 146.8864 | 0 | 0.39133 | 0 | 1.4689 | 0 | 0.39133 | 1.4689 | 308.9516 | 8.9518 | 308.5603
39029.3736 | 306 | 0 | 39029.3737 | 2267 | 0 |  | 1417 | 1569 | 18.6813 | 0 | 138.4005 | 0 | 0.18681 | 0 | 1.384 | 0 | 0.18681 | 1.384 | 756.6601 | 15.6321 | 756.4733
39029.3758 | 33 | 0 | 39029.3758 | 2060 | 0 |  | 1601.5 | 1753.5 | 2.0147 | 0 | 125.7631 | 0 | 0.020147 | 0 | 1.2576 | 0 | 0.020147 | 1.2576 | 7843.5758 | 27.2515 | 7843.5556

## B4-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.9536 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39029.3565 | 0 | 0 | 39029.3565 | 0 | 0 |  | -64 | 88 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39029.3586 | 0 | 0 | 39029.3587 | 0 | 0 |  | 120.5 | 272.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500976 | 500976 | 500975.9997
39029.3608 | 1 | 0 | 39029.3608 | 1 | 0 |  | 305.5 | 457.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 250438 | 250438 | 250437.9994
39029.3629 | 1483 | 0 | 39029.3629 | 4 | 0 |  | 490.5 | 642.5 | 90.5372 | 0 | 0.2442 | 0 | 0.90537 | 0 | 0.002442 | 0 | 0.90537 | 0.002442 | 68.94 | 62534.5 | 68.0346
39029.3651 | 2024 | 0 | 39029.3651 | 2425 | 0 |  | 675 | 827 | 123.5653 | 0 | 148.0464 | 0 | 1.2357 | 0 | 1.4805 | 0 | 1.2357 | 1.4805 | 23.7836 | 3.3146 | 22.5479
39029.3672 | 1417 | 0 | 39029.3672 | 2325 | 0 |  | 860 | 1012 | 86.5079 | 0 | 141.9414 | 0 | 0.86508 | 0 | 1.4194 | 0 | 0.86508 | 1.4194 | 76.8088 | 7.7583 | 75.9437
39029.3693 | 1735 | 0 | 39029.3694 | 2487 | 0 |  | 1044.5 | 1196.5 | 105.9219 | 0 | 151.8315 | 0 | 1.0592 | 0 | 1.5183 | 0 | 1.0592 | 1.5183 | 44.4023 | 0.73904 | 43.3431
39029.3715 | 1329 | 0 | 39029.3715 | 2113 | 0 |  | 1229.5 | 1381.5 | 81.1355 | 0 | 128.9988 | 0 | 0.81136 | 0 | 1.29 | 0 | 0.81136 | 1.29 | 88.5162 | 18.5698 | 87.7048
39029.3736 | 318 | 0 | 39029.3736 | 2489 | 0 |  | 1414 | 1566 | 19.4139 | 0 | 151.9536 | 0 | 0.19414 | 0 | 1.5195 | 0 | 0.19414 | 1.5195 | 687.8553 | 0.6581 | 687.6612
39029.3758 | 26 | 0 | 39029.3758 | 1988 | 0 |  | 1599 | 1751 | 1.5873 | 0 | 121.3675 | 0 | 0.015873 | 0 | 1.2137 | 0 | 0.015873 | 1.2137 | 9536.0769 | 26.0252 | 9536.0611

## B4-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.0379 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39029.3565 | 0 | 0 | 39029.3565 | 0 | 0 |  | -66.5 | 85.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497976 | 497976 | 497975.9997
39029.3586 | 0 | 0 | 39029.3586 | 0 | 0 |  | 118 | 270 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 497976 | 497976 | 497975.9997
39029.3608 | 4 | 0 | 39029.3608 | 2 | 0 |  | 302.5 | 454.5 | 0.2442 | 0 | 0.1221 | 0 | 0.002442 | 0 | 0.001221 | 0 | 0.002442 | 0.001221 | 62159.5 | 124419 | 62159.4976
39029.3629 | 1396 | 0 | 39029.3629 | 4 | 0 |  | 487.5 | 639.5 | 85.2259 | 0 | 0.2442 | 0 | 0.85226 | 0 | 0.002442 | 0 | 0.85226 | 0.002442 | 78.394 | 62159.5 | 77.5417
39029.365 | 1949 | 0 | 39029.365 | 2474 | 0 |  | 672.5 | 824.5 | 118.9866 | 0 | 151.0379 | 0 | 1.1899 | 0 | 1.5104 | 0 | 1.1899 | 1.5104 | 27.7773 | 0.66209 | 26.5875
39029.3672 | 1865 | 0 | 39029.3672 | 2422 | 0 |  | 857 | 1009 | 113.8584 | 0 | 147.8632 | 0 | 1.1386 | 0 | 1.4786 | 0 | 1.1386 | 1.4786 | 33.5324 | 2.8233 | 32.3939
39029.3693 | 1905 | 0 | 39029.3693 | 2233 | 0 |  | 1042 | 1194 | 116.3004 | 0 | 136.3248 | 0 | 1.163 | 0 | 1.3632 | 0 | 1.163 | 1.3632 | 30.7286 | 11.5262 | 29.5656
39029.3714 | 1181 | 0 | 39029.3715 | 2008 | 0 |  | 1226.5 | 1378.5 | 72.1001 | 0 | 122.5885 | 0 | 0.721 | 0 | 1.2259 | 0 | 0.721 | 1.2259 | 110.8704 | 24.0229 | 110.1494
39029.3736 | 303 | 0 | 39029.3736 | 2057 | 0 |  | 1411.5 | 1563.5 | 18.4982 | 0 | 125.58 | 0 | 0.18498 | 0 | 1.2558 | 0 | 0.18498 | 1.2558 | 721.9076 | 21.0685 | 721.7226
39029.3757 | 2 | 0 | 39029.3757 | 1776 | 0 |  | 1596 | 1748 | 0.1221 | 0 | 108.4249 | 0 | 0.001221 | 0 | 1.0842 | 0 | 0.001221 | 1.0842 | 124419 | 40.2241 | 124418.9988

## B3-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 155.9451 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39029.3564 | 0 | 0 | 39029.3564 | 0 | 0 |  | -75 | 77 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39029.3585 | 0 | 0 | 39029.3585 | 0 | 0 |  | 109.5 | 261.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510776 | 510776 | 510775.9997
39029.3607 | 1 | 0 | 39029.3607 | 2072 | 0 |  | 294.5 | 446.5 | 0.06105 | 0 | 126.4957 | 0 | 0.0006105 | 0 | 1.265 | 0 | 0.0006105 | 1.265 | 255338 | 23.2809 | 255337.9994
39029.3628 | 680 | 0 | 39029.3628 | 2538 | 0 |  | 479 | 631 | 41.514 | 0 | 154.9451 | 0 | 0.41514 | 0 | 1.5495 | 0 | 0.41514 | 1.5495 | 275.6441 | 0.64539 | 275.229
39029.3649 | 2133 | 0 | 39029.365 | 2220 | 0 |  | 664 | 816 | 130.2198 | 0 | 135.5311 | 0 | 1.3022 | 0 | 1.3553 | 0 | 1.3022 | 1.3553 | 19.7553 | 15.0622 | 18.4531
39029.3671 | 1531 | 0 | 39029.3671 | 2511 | 0 |  | 848.5 | 1000.5 | 93.4676 | 0 | 153.2967 | 0 | 0.93468 | 0 | 1.533 | 0 | 0.93468 | 1.533 | 66.8439 | 1.7276 | 65.9092
39029.3692 | 1508 | 0 | 39029.3692 | 2114 | 0 |  | 1033.5 | 1185.5 | 92.0635 | 0 | 129.0598 | 0 | 0.92063 | 0 | 1.2906 | 0 | 0.92063 | 1.2906 | 69.3886 | 20.8316 | 68.468
39029.3714 | 1609 | 0 | 39029.3714 | 2320 | 0 |  | 1218.5 | 1370.5 | 98.2295 | 0 | 141.6361 | 0 | 0.9823 | 0 | 1.4164 | 0 | 0.9823 | 1.4164 | 58.7557 | 10.1026 | 57.7735
39029.3735 | 959 | 0 | 39029.3735 | 1956 | 0 |  | 1403 | 1555 | 58.547 | 0 | 119.4139 | 0 | 0.58547 | 0 | 1.1941 | 0 | 0.58547 | 1.1941 | 166.3587 | 30.592 | 165.7732
39029.3756 | 1 | 0 | 39029.3756 | 1754 | 0 |  | 1587.5 | 1739.5 | 0.06105 | 0 | 107.0818 | 0 | 0.0006105 | 0 | 1.0708 | 0 | 0.0006105 | 1.0708 | 255338 | 45.6317 | 255337.9994

## B3-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.8926 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39029.3563 | 0 | 0 | 39029.3564 | 0 | 0 |  | -78 | 74 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39029.3585 | 0 | 0 | 39029.3585 | 0 | 0 |  | 106.5 | 258.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500776 | 500776 | 500775.9997
39029.3606 | 4 | 0 | 39029.3606 | 3 | 0 |  | 291.5 | 443.5 | 0.2442 | 0 | 0.18315 | 0 | 0.002442 | 0 | 0.0018315 | 0 | 0.002442 | 0.0018315 | 62509.5 | 83379.3333 | 62509.4976
39029.3628 | 1146 | 0 | 39029.3628 | 2382 | 0 |  | 476.5 | 628.5 | 69.9634 | 0 | 145.4212 | 0 | 0.69963 | 0 | 1.4542 | 0 | 0.69963 | 1.4542 | 118.5323 | 5.1377 | 117.8327
39029.3649 | 2033 | 0 | 39029.3649 | 2125 | 0 |  | 661 | 813 | 124.1148 | 0 | 129.7314 | 0 | 1.2411 | 0 | 1.2973 | 0 | 1.2411 | 1.2973 | 23.1864 | 17.8532 | 21.9453
39029.367 | 1311 | 0 | 39029.3671 | 2082 | 0 |  | 846 | 998 | 80.0366 | 0 | 127.1062 | 0 | 0.80037 | 0 | 1.2711 | 0 | 0.80037 | 1.2711 | 91.0282 | 20.2872 | 90.2279
39029.3692 | 1833 | 0 | 39029.3692 | 1922 | 0 |  | 1030.5 | 1182.5 | 111.9048 | 0 | 117.3382 | 0 | 1.119 | 0 | 1.1734 | 0 | 1.119 | 1.1734 | 36.6274 | 30.3007 | 35.5083
39029.3713 | 1098 | 0 | 39029.3713 | 2203 | 0 |  | 1215.5 | 1367.5 | 67.033 | 0 | 134.4933 | 0 | 0.67033 | 0 | 1.3449 | 0 | 0.67033 | 1.3449 | 128.0856 | 13.6804 | 127.4153
39029.3734 | 334 | 0 | 39029.3735 | 2488 | 0 |  | 1400 | 1552 | 20.3907 | 0 | 151.8926 | 0 | 0.20391 | 0 | 1.5189 | 0 | 0.20391 | 1.5189 | 649.8144 | 0.65836 | 649.6105
39029.3756 | 6 | 0 | 39029.3756 | 2223 | 0 |  | 1585 | 1737 | 0.3663 | 0 | 135.7143 | 0 | 0.003663 | 0 | 1.3571 | 0 | 0.003663 | 1.3571 | 41639.6667 | 12.6577 | 41639.663

## B3-D8
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 157.5324 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39029.3563 | 0 | 0 | 39029.3563 | 0 | 0 |  | -80.5 | 71.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
39029.3584 | 0 | 0 | 39029.3585 | 0 | 0 |  | 104 | 256 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515976 | 515976 | 515975.9997
39029.3606 | 4 | 0 | 39029.3606 | 2002 | 0 |  | 288.5 | 440.5 | 0.2442 | 0 | 122.2222 | 0 | 0.002442 | 0 | 1.2222 | 0 | 0.002442 | 1.2222 | 64409.5 | 28.8901 | 64409.4976
39029.3627 | 1139 | 0 | 39029.3627 | 2544 | 0 |  | 473.5 | 625.5 | 69.536 | 0 | 155.3114 | 0 | 0.69536 | 0 | 1.5531 | 0 | 0.69536 | 1.5531 | 126.5478 | 1.43 | 125.8525
39029.3649 | 2279 | 0 | 39029.3649 | 2006 | 0 |  | 658.5 | 810.5 | 139.1331 | 0 | 122.4664 | 0 | 1.3913 | 0 | 1.2247 | 0 | 1.3913 | 1.2247 | 13.2242 | 28.6331 | 11.8329
39029.367 | 1494 | 0 | 39029.367 | 2523 | 0 |  | 843 | 995 | 91.2088 | 0 | 154.0293 | 0 | 0.91209 | 0 | 1.5403 | 0 | 0.91209 | 1.5403 | 72.7162 | 2.2743 | 71.8041
39029.3691 | 1814 | 0 | 39029.3692 | 2082 | 0 |  | 1028 | 1180 | 110.7448 | 0 | 127.1062 | 0 | 1.1074 | 0 | 1.2711 | 0 | 1.1074 | 1.2711 | 42.2481 | 23.9376 | 41.1406
39029.3713 | 1492 | 0 | 39029.3713 | 2497 | 0 |  | 1212.5 | 1364.5 | 91.0867 | 0 | 152.442 | 0 | 0.91087 | 0 | 1.5244 | 0 | 0.91087 | 1.5244 | 72.9477 | 3.3392 | 72.0369
39029.3734 | 204 | 0 | 39029.3734 | 2142 | 0 |  | 1397.5 | 1549.5 | 12.4542 | 0 | 130.7692 | 0 | 0.12454 | 0 | 1.3077 | 0 | 0.12454 | 1.3077 | 1164.8922 | 20.4659 | 1164.7676
39029.3756 | 15 | 0 | 39029.3756 | 2564 | 0 |  | 1582 | 1734 | 0.91575 | 0 | 156.5324 | 0 | 0.0091575 | 0 | 1.5653 | 0 | 0.0091575 | 1.5653 | 17102.5333 | 0.63885 | 17102.5242

## B3-D7
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 155.7619 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39029.3563 | 0 | 0 | 39029.3563 | 0 | 0 |  | -83.5 | 68.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39029.3584 | 0 | 0 | 39029.3584 | 0 | 0 |  | 101.5 | 253.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 510176 | 510176 | 510175.9997
39029.3606 | 1 | 0 | 39029.3606 | 2532 | 0 |  | 286 | 438 | 0.06105 | 0 | 154.5788 | 0 | 0.0006105 | 0 | 1.5458 | 0 | 0.0006105 | 1.5458 | 255038 | 0.7654 | 255037.9994
39029.3627 | 399 | 0 | 39029.3627 | 2172 | 0 |  | 470.5 | 622.5 | 24.359 | 0 | 132.6007 | 0 | 0.24359 | 0 | 1.326 | 0 | 0.24359 | 1.326 | 539.4436 | 17.4669 | 539.2
39029.3648 | 1982 | 0 | 39029.3648 | 2535 | 0 |  | 655.5 | 807.5 | 121.0012 | 0 | 154.7619 | 0 | 1.21 | 0 | 1.5476 | 0 | 1.21 | 1.5476 | 28.7275 | 0.64615 | 27.5175
39029.367 | 1767 | 0 | 39029.367 | 2223 | 0 |  | 840.5 | 992.5 | 107.8755 | 0 | 135.7143 | 0 | 1.0788 | 0 | 1.3571 | 0 | 1.0788 | 1.3571 | 44.3905 | 14.7719 | 43.3117
39029.3691 | 1490 | 0 | 39029.3691 | 2099 | 0 |  | 1025 | 1177 | 90.9646 | 0 | 128.1441 | 0 | 0.90965 | 0 | 1.2814 | 0 | 0.90965 | 1.2814 | 71.2336 | 21.5522 | 70.3239
39029.3712 | 1393 | 0 | 39029.3713 | 2446 | 0 |  | 1210 | 1362 | 85.0427 | 0 | 149.3284 | 0 | 0.85043 | 0 | 1.4933 | 0 | 0.85043 | 1.4933 | 83.1572 | 4.3083 | 82.3068
39029.3734 | 303 | 0 | 39029.3734 | 2426 | 0 |  | 1394.5 | 1546.5 | 18.4982 | 0 | 148.1074 | 0 | 0.18498 | 0 | 1.4811 | 0 | 0.18498 | 1.4811 | 742.0396 | 5.1682 | 741.8546
39029.3755 | 46 | 0 | 39029.3755 | 2062 | 0 |  | 1579.5 | 1731.5 | 2.8083 | 0 | 125.8852 | 0 | 0.028083 | 0 | 1.2589 | 0 | 0.028083 | 1.2589 | 5446.4783 | 23.7333 | 5446.4502

## B3-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 151.3663 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39029.3562 | 0 | 0 | 39029.3563 | 0 | 0 |  | -86.5 | 65.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 495776 | 495776 | 495775.9997
39029.3584 | 0 | 0 | 39029.3584 | 0 | 0 |  | 98.5 | 250.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 495776 | 495776 | 495775.9997
39029.3605 | 1 | 0 | 39029.3605 | 0 | 0 |  | 283 | 435 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 247838 | 495776 | 247837.9994
39029.3627 | 584 | 0 | 39029.3627 | 3 | 0 |  | 468 | 620 | 35.6532 | 0 | 0.18315 | 0 | 0.35653 | 0 | 0.0018315 | 0 | 0.35653 | 0.0018315 | 324.5514 | 82546 | 324.1948
39029.3648 | 1792 | 0 | 39029.3648 | 2131 | 0 |  | 652.5 | 804.5 | 109.4017 | 0 | 130.0977 | 0 | 1.094 | 0 | 1.301 | 0 | 1.094 | 1.301 | 38.3583 | 16.3482 | 37.2642
39029.3669 | 1210 | 0 | 39029.367 | 2463 | 0 |  | 837.5 | 989.5 | 73.8706 | 0 | 150.3663 | 0 | 0.73871 | 0 | 1.5037 | 0 | 0.73871 | 1.5037 | 104.9074 | 0.66504 | 104.1687
39029.3691 | 1681 | 0 | 39029.3691 | 1940 | 0 |  | 1022.5 | 1174.5 | 102.6252 | 0 | 118.4371 | 0 | 1.0263 | 0 | 1.1844 | 0 | 1.0263 | 1.1844 | 47.4943 | 27.8031 | 46.4681
39029.3712 | 1175 | 0 | 39029.3712 | 1979 | 0 |  | 1207 | 1359 | 71.7338 | 0 | 120.8181 | 0 | 0.71734 | 0 | 1.2082 | 0 | 0.71734 | 1.2082 | 111.0111 | 25.2845 | 110.2937
39029.3734 | 1638 | 0 | 39029.3734 | 2270 | 0 |  | 1391.5 | 1543.5 | 100 | 0 | 138.5836 | 0 | 1 | 0 | 1.3858 | 0 | 1 | 1.3858 | 51.3663 | 9.2238 | 50.3663
39029.3755 | 22 | 0 | 39029.3755 | 1327 | 0 |  | 1576.5 | 1728.5 | 1.3431 | 0 | 81.0134 | 0 | 0.013431 | 0 | 0.81013 | 0 | 0.013431 | 0.81013 | 11169.9091 | 86.841 | 11169.8957

## B3-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 154.0525 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39029.3562 | 0 | 0 | 39029.3562 | 0 | 0 |  | -89.5 | 62.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504576 | 504576 | 504575.9997
39029.3584 | 0 | 0 | 39029.3584 | 0 | 0 |  | 95.5 | 247.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 504576 | 504576 | 504575.9997
39029.3605 | 1 | 0 | 39029.3605 | 1 | 0 |  | 280.5 | 432.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 252238 | 252238 | 252237.9994
39029.3626 | 1113 | 0 | 39029.3627 | 3 | 0 |  | 465 | 617 | 67.9487 | 0 | 0.18315 | 0 | 0.67949 | 0 | 0.0018315 | 0 | 0.67949 | 0.0018315 | 126.7188 | 84012.6667 | 126.0393
39029.3648 | 1847 | 0 | 39029.3648 | 2319 | 0 |  | 650 | 802 | 112.7595 | 0 | 141.5751 | 0 | 1.1276 | 0 | 1.4158 | 0 | 1.1276 | 1.4158 | 36.6205 | 8.8133 | 35.4929
39029.3669 | 1652 | 0 | 39029.3669 | 2507 | 0 |  | 834.5 | 986.5 | 100.8547 | 0 | 153.0525 | 0 | 1.0085 | 0 | 1.5305 | 0 | 1.0085 | 1.5305 | 52.747 | 0.65337 | 51.7384
39029.3691 | 1853 | 0 | 39029.3691 | 2081 | 0 |  | 1019.5 | 1171.5 | 113.1258 | 0 | 127.0452 | 0 | 1.1313 | 0 | 1.2705 | 0 | 1.1313 | 1.2705 | 36.1781 | 21.258 | 35.0468
39029.3712 | 1123 | 0 | 39029.3712 | 2227 | 0 |  | 1204.5 | 1356.5 | 68.5592 | 0 | 135.9585 | 0 | 0.68559 | 0 | 1.3596 | 0 | 0.68559 | 1.3596 | 124.6999 | 13.3085 | 124.0143
39029.3733 | 1177 | 1 | 39029.3733 | 2010 | 0 |  | 1389 | 1541 | 71.8559 | 0.06105 | 122.7106 | 0 | 0.71856 | 0.0006105 | 1.2271 | 0 | 0.71795 | 1.2271 | 114.8705 | 25.5413 | 27371.6675
39029.3755 | 145 | 0 | 39029.3755 | 1772 | 0 |  | 1573.5 | 1725.5 | 8.8523 | 0 | 108.1807 | 0 | 0.088523 | 0 | 1.0818 | 0 | 0.088523 | 1.0818 | 1640.2621 | 42.4029 | 1640.1735

## B3-B4
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 131.1587 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39029.3562 | 0 | 0 | 39029.3562 | 0 | 0 |  | -92 | 60 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 429576 | 429576 | 429575.9997
39029.3583 | 0 | 0 | 39029.3583 | 0 | 0 |  | 93 | 245 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 429576 | 429576 | 429575.9997
39029.3605 | 1 | 0 | 39029.3605 | 1 | 0 |  | 277.5 | 429.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 214738 | 214738 | 214737.9994
39029.3626 | 348 | 13 | 39029.3626 | 1481 | 0 |  | 462.5 | 614.5 | 21.2454 | 0.79365 | 90.4151 | 0 | 0.21245 | 0.0079365 | 0.90415 | 0 | 0.20452 | 0.90415 | 588.0686 | 45.0628 | 4271.0596
39029.3647 | 2102 | 12 | 39029.3648 | 2008 | 10 |  | 647 | 799 | 128.3272 | 0.7326 | 122.5885 | 0.6105 | 1.2833 | 0.007326 | 1.2259 | 0.006105 | 1.2759 | 1.2198 | 2.3721 | 8.9049 | 23.4265
39029.3669 | 1556 | 1 | 39029.3669 | 2003 | 72 |  | 832 | 984 | 94.9939 | 0.06105 | 122.2833 | 4.3956 | 0.94994 | 0.0006105 | 1.2228 | 0.043956 | 0.94933 | 1.1789 | 38.3913 | 8.3386 | 4551.7327
39029.369 | 2132 | 100 | 39029.369 | 1965 | 271 |  | 1016.5 | 1168.5 | 130.1587 | 6.105 | 119.9634 | 16.5446 | 1.3016 | 0.06105 | 1.1996 | 0.16545 | 1.2405 | 1.0342 | 11.8567 | 5.2802 | 4.1939
39029.3712 | 1516 | 451 | 39029.3712 | 1661 | 558 |  | 1201.5 | 1353.5 | 92.5519 | 27.5336 | 101.4042 | 34.0659 | 0.92552 | 0.27534 | 1.014 | 0.34066 | 0.65018 | 0.67338 | 261.7307 | 54.7739 | 14.2327
39029.3733 | 1134 | 843 | 39029.3733 | 1108 | 1057 |  | 1386 | 1538 | 69.2308 | 51.4652 | 67.6435 | 64.5299 | 0.69231 | 0.51465 | 0.67643 | 0.6453 | 0.17766 | 0.031136 | 63.2473 | 64.2124 | 7.9496
39029.3754 | 1039 | 1062 | 39029.3755 | 992 | 850 |  | 1571 | 1723 | 63.431 | 64.8352 | 60.5617 | 51.8926 | 0.63431 | 0.64835 | 0.60562 | 0.51893 | 0.014042 | 0.086691 | 306.073 | 312.8535 | 3.3808

## A2-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 155.0904 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39029.356 | 0 | 0 | 39029.356 | 0 | 0 |  | -111.5 | 40.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39029.3581 | 0 | 0 | 39029.3581 | 0 | 0 |  | 73.5 | 225.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39029.3602 | 0 | 0 | 39029.3603 | 0 | 0 |  | 258 | 410 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507976 | 507976 | 507975.9997
39029.3624 | 3 | 0 | 39029.3624 | 3 | 0 |  | 442.5 | 594.5 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 84579.3333 | 84579.3333 | 84579.3315
39029.3645 | 2241 | 0 | 39029.3645 | 1897 | 0 |  | 627.5 | 779.5 | 136.8132 | 0 | 115.812 | 0 | 1.3681 | 0 | 1.1581 | 0 | 1.3681 | 1.1581 | 13.3592 | 33.9157 | 11.9911
39029.3667 | 2336 | 0 | 39029.3667 | 1957 | 0 |  | 812.5 | 964.5 | 142.6129 | 0 | 119.475 | 0 | 1.4261 | 0 | 1.1947 | 0 | 1.4261 | 1.1947 | 8.7491 | 29.8099 | 7.323
39029.3688 | 1996 | 0 | 39029.3688 | 2524 | 0 |  | 997 | 1149 | 121.8559 | 0 | 154.0904 | 0 | 1.2186 | 0 | 1.5409 | 0 | 1.2186 | 1.5409 | 27.2735 | 0.64897 | 26.055
39029.3709 | 2166 | 0 | 39029.3709 | 2371 | 0 |  | 1181.5 | 1333.5 | 132.2344 | 0 | 144.7497 | 0 | 1.3223 | 0 | 1.4475 | 0 | 1.3223 | 1.4475 | 17.2844 | 7.1438 | 15.9621
39029.3731 | 2014 | 0 | 39029.3731 | 2082 | 0 |  | 1366.5 | 1518.5 | 122.9548 | 0 | 127.1062 | 0 | 1.2295 | 0 | 1.2711 | 0 | 1.2295 | 1.2711 | 26.136 | 22.0163 | 24.9065
39029.3752 | 2131 | 0 | 39029.3752 | 1665 | 0 |  | 1551.5 | 1703.5 | 130.0977 | 0 | 101.6484 | 0 | 1.301 | 0 | 1.0165 | 0 | 1.301 | 1.0165 | 19.2107 | 52.5754 | 17.9097

## A2-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 157.7155 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39029.3559 | 0 | 0 | 39029.3559 | 0 | 0 |  | -114.5 | 37.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
39029.3581 | 0 | 0 | 39029.3581 | 0 | 0 |  | 70.5 | 222.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
39029.3602 | 0 | 0 | 39029.3602 | 0 | 0 |  | 255 | 407 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516576 | 516576 | 516575.9997
39029.3623 | 3 | 0 | 39029.3624 | 3 | 0 |  | 440 | 592 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 86012.6667 | 86012.6667 | 86012.6648
39029.3645 | 2398 | 0 | 39029.3645 | 2485 | 0 |  | 624.5 | 776.5 | 146.398 | 0 | 151.7094 | 0 | 1.464 | 0 | 1.5171 | 0 | 1.464 | 1.5171 | 7.7306 | 3.959 | 6.2666
39029.3666 | 2041 | 0 | 39029.3666 | 1941 | 0 |  | 809.5 | 961.5 | 124.6032 | 0 | 118.4982 | 0 | 1.246 | 0 | 1.185 | 0 | 1.246 | 1.185 | 26.5742 | 33.0953 | 25.3282
39029.3688 | 1907 | 0 | 39029.3688 | 2254 | 0 |  | 994.5 | 1146.5 | 116.4225 | 0 | 137.6068 | 0 | 1.1642 | 0 | 1.3761 | 0 | 1.1642 | 1.3761 | 35.4683 | 14.6131 | 34.3041
39029.3709 | 2483 | 0 | 39029.3709 | 2175 | 0 |  | 1179 | 1331 | 151.5873 | 0 | 132.7839 | 0 | 1.5159 | 0 | 1.3278 | 0 | 1.5159 | 1.3278 | 4.0427 | 18.7761 | 2.5268
39029.373 | 2567 | 0 | 39029.373 | 2378 | 0 |  | 1363.5 | 1515.5 | 156.7155 | 0 | 145.177 | 0 | 1.5672 | 0 | 1.4518 | 0 | 1.5672 | 1.4518 | 0.6381 | 8.6367 | 0.92906
39029.3752 | 1916 | 0 | 39029.3752 | 1803 | 0 |  | 1548.5 | 1700.5 | 116.9719 | 0 | 110.0733 | 0 | 1.1697 | 0 | 1.1007 | 0 | 1.1697 | 1.1007 | 34.8319 | 43.2823 | 33.6622

## A2-B4
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 154.4188 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39029.3559 | 0 | 0 | 39029.3559 | 0 | 0 |  | -117.5 | 34.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39029.358 | 0 | 0 | 39029.358 | 0 | 0 |  | 67.5 | 219.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39029.3602 | 0 | 0 | 39029.3602 | 0 | 0 |  | 252.5 | 404.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 505776 | 505776 | 505775.9997
39029.3623 | 3 | 0 | 39029.3623 | 3 | 0 |  | 437 | 589 | 0.18315 | 0 | 0.18315 | 0 | 0.0018315 | 0 | 0.0018315 | 0 | 0.0018315 | 0.0018315 | 84212.6667 | 84212.6667 | 84212.6648
39029.3644 | 1901 | 0 | 39029.3645 | 2389 | 0 |  | 622 | 774 | 116.0562 | 0 | 145.8486 | 0 | 1.1606 | 0 | 1.4585 | 0 | 1.1606 | 1.4585 | 33.0552 | 5.8761 | 31.8947
39029.3666 | 2513 | 0 | 39029.3666 | 2454 | 0 |  | 806.5 | 958.5 | 153.4188 | 0 | 149.8168 | 0 | 1.5342 | 0 | 1.4982 | 0 | 1.5342 | 1.4982 | 0.65181 | 3.0717 | 0.88238
39029.3687 | 1967 | 0 | 39029.3687 | 2183 | 0 |  | 991.5 | 1143.5 | 120.0855 | 0 | 133.2723 | 0 | 1.2009 | 0 | 1.3327 | 0 | 1.2009 | 1.3327 | 28.5907 | 15.8672 | 27.3899
39029.3709 | 2041 | 0 | 39029.3709 | 2042 | 0 |  | 1176.5 | 1328.5 | 124.6032 | 0 | 124.6642 | 0 | 1.246 | 0 | 1.2466 | 0 | 1.246 | 1.2466 | 23.9285 | 23.8678 | 22.6824
39029.373 | 1953 | 0 | 39029.373 | 2227 | 0 |  | 1361 | 1513 | 119.2308 | 0 | 135.9585 | 0 | 1.1923 | 0 | 1.3596 | 0 | 1.1923 | 1.3596 | 29.5125 | 13.5779 | 28.3202
39029.3751 | 2509 | 0 | 39029.3752 | 1945 | 0 |  | 1545.5 | 1697.5 | 153.1746 | 0 | 118.7424 | 0 | 1.5317 | 0 | 1.1874 | 0 | 1.5317 | 1.1874 | 0.81228 | 30.0452 | 0.71947

## A2-B3
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 143.8571 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39029.3559 | 0 | 0 | 39029.3559 | 0 | 0 |  | -120 | 32 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 471176 | 471176 | 471175.9997
39029.358 | 0 | 0 | 39029.358 | 0 | 0 |  | 64.5 | 216.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 471176 | 471176 | 471175.9997
39029.3601 | 0 | 0 | 39029.3602 | 0 | 0 |  | 249.5 | 401.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 471176 | 471176 | 471175.9997
39029.3623 | 4 | 0 | 39029.3623 | 4 | 0 |  | 434.5 | 586.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 58809.5 | 58809.5 | 58809.4976
39029.3644 | 2078 | 0 | 39029.3644 | 1853 | 0 |  | 619 | 771 | 126.862 | 0 | 113.1258 | 0 | 1.2686 | 0 | 1.1313 | 0 | 1.2686 | 1.1313 | 13.3965 | 27.1657 | 12.1279
39029.3666 | 2327 | 0 | 39029.3666 | 1411 | 0 |  | 804 | 956 | 142.0635 | 0 | 86.1416 | 0 | 1.4206 | 0 | 0.86142 | 0 | 1.4206 | 0.86142 | 1.2626 | 67.0007 | 0.15807
39029.3687 | 2339 | 0 | 39029.3687 | 1749 | 0 |  | 988.5 | 1140.5 | 142.7961 | 0 | 106.7766 | 0 | 1.428 | 0 | 1.0678 | 0 | 1.428 | 1.0678 | 0.74305 | 34.7273 | 0.68491
39029.3708 | 2250 | 0 | 39029.3708 | 1327 | 0 |  | 1173.5 | 1325.5 | 137.3626 | 0 | 81.0134 | 0 | 1.3736 | 0 | 0.81013 | 0 | 1.3736 | 0.81013 | 4.728 | 77.572 | 3.3544
39029.373 | 1961 | 0 | 39029.373 | 412 | 0 |  | 1358 | 1510 | 119.7192 | 0 | 25.1526 | 0 | 1.1972 | 0 | 0.25153 | 0 | 1.1972 | 0.25153 | 20.1622 | 471.9369 | 18.965
39029.3751 | 2340 | 0 | 39029.3751 | 289 | 0 |  | 1543 | 1695 | 142.8571 | 0 | 17.6435 | 0 | 1.4286 | 0 | 0.17643 | 0 | 1.4286 | 0.17643 | 0.7 | 715.3564 | 0.72857

## A1-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.8315 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39029.3556 | 0 | 0 | 39029.3556 | 0 | 0 |  | -139.5 | 12.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39029.3578 | 0 | 0 | 39029.3578 | 0 | 0 |  | 45 | 197 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39029.3599 | 0 | 0 | 39029.3599 | 0 | 0 |  | 230 | 382 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 500576 | 500576 | 500575.9997
39029.362 | 3 | 0 | 39029.3621 | 4 | 0 |  | 414.5 | 566.5 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 83346 | 62484.5 | 83345.9982
39029.3642 | 1426 | 0 | 39029.3642 | 1976 | 0 |  | 599.5 | 751.5 | 87.0574 | 0 | 120.6349 | 0 | 0.87057 | 0 | 1.2063 | 0 | 0.87057 | 1.2063 | 75.5526 | 26.6893 | 74.682
39029.3663 | 2405 | 0 | 39029.3663 | 2081 | 0 |  | 784.5 | 936.5 | 146.8254 | 0 | 127.0452 | 0 | 1.4683 | 0 | 1.2705 | 0 | 1.4683 | 1.2705 | 4.0906 | 20.297 | 2.6224
39029.3685 | 2076 | 0 | 39029.3685 | 2458 | 0 |  | 969 | 1121 | 126.7399 | 0 | 150.0611 | 0 | 1.2674 | 0 | 1.5006 | 0 | 1.2674 | 1.5006 | 20.5867 | 1.8462 | 19.3193
39029.3706 | 2290 | 0 | 39029.3706 | 2187 | 0 |  | 1153.5 | 1305.5 | 139.8046 | 0 | 133.5165 | 0 | 1.398 | 0 | 1.3352 | 0 | 1.398 | 1.3352 | 9.3179 | 14.4664 | 7.9199
39029.3727 | 2487 | 0 | 39029.3728 | 1936 | 0 |  | 1338.5 | 1490.5 | 151.8315 | 0 | 118.1929 | 0 | 1.5183 | 0 | 1.1819 | 0 | 1.5183 | 1.1819 | 0.65862 | 29.3068 | 0.85969
39029.3749 | 1962 | 0 | 39029.3749 | 1585 | 0 |  | 1523.5 | 1675.5 | 119.7802 | 0 | 96.7643 | 0 | 1.1978 | 0 | 0.96764 | 0 | 1.1978 | 0.96764 | 27.5933 | 57.942 | 26.3955

## A1-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.16 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39029.3556 | 0 | 0 | 39029.3556 | 0 | 0 |  | -142.5 | 9.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39029.3577 | 0 | 0 | 39029.3578 | 0 | 0 |  | 42.5 | 194.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39029.3599 | 0 | 0 | 39029.3599 | 0 | 0 |  | 227 | 379 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498376 | 498376 | 498375.9997
39029.362 | 3 | 0 | 39029.362 | 4 | 0 |  | 412 | 564 | 0.18315 | 0 | 0.2442 | 0 | 0.0018315 | 0 | 0.002442 | 0 | 0.0018315 | 0.002442 | 82979.3333 | 62209.5 | 82979.3315
39029.3642 | 1662 | 0 | 39029.3642 | 2191 | 0 |  | 596.5 | 748.5 | 101.4652 | 0 | 133.7607 | 0 | 1.0147 | 0 | 1.3376 | 0 | 1.0147 | 1.3376 | 49.9627 | 13.7554 | 48.948
39029.3663 | 2351 | 0 | 39029.3663 | 2476 | 0 |  | 781.5 | 933.5 | 143.5287 | 0 | 151.16 | 0 | 1.4353 | 0 | 1.5116 | 0 | 1.4353 | 1.5116 | 6.0136 | 0.66155 | 4.5783
39029.3684 | 2003 | 0 | 39029.3684 | 2114 | 0 |  | 966.5 | 1118.5 | 122.2833 | 0 | 129.0598 | 0 | 1.2228 | 0 | 1.2906 | 0 | 1.2228 | 1.2906 | 24.4324 | 17.8988 | 23.2095
39029.3706 | 1999 | 0 | 39029.3706 | 2032 | 0 |  | 1151 | 1303 | 122.0391 | 0 | 124.0537 | 0 | 1.2204 | 0 | 1.2405 | 0 | 1.2204 | 1.2405 | 24.6813 | 22.6565 | 23.4609
39029.3727 | 2228 | 0 | 39029.3727 | 2046 | 0 |  | 1335.5 | 1487.5 | 136.0195 | 0 | 124.9084 | 0 | 1.3602 | 0 | 1.2491 | 0 | 1.3602 | 1.2491 | 11.8662 | 21.8172 | 10.5061
39029.3748 | 2004 | 0 | 39029.3749 | 1970 | 0 |  | 1520.5 | 1672.5 | 122.3443 | 0 | 120.2686 | 0 | 1.2234 | 0 | 1.2027 | 0 | 1.2234 | 1.2027 | 24.3703 | 26.5168 | 23.1468

## A1-B4
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 152.4652 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39029.3556 | 0 | 0 | 39029.3556 | 0 | 0 |  | -145.5 | 6.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 499376 | 499376 | 499375.9997
39029.3577 | 0 | 0 | 39029.3577 | 0 | 0 |  | 39.5 | 191.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 499376 | 499376 | 499375.9997
39029.3598 | 0 | 0 | 39029.3599 | 0 | 0 |  | 224.5 | 376.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 499376 | 499376 | 499375.9997
39029.362 | 4 | 1 | 39029.362 | 4 | 0 |  | 409 | 561 | 0.2442 | 0.06105 | 0.2442 | 0 | 0.002442 | 0.0006105 | 0.002442 | 0 | 0.0018315 | 0.002442 | 83157.1349 | 62334.5 | 248838.8008
39029.3641 | 1599 | 0 | 39029.3641 | 1771 | 0 |  | 594 | 746 | 97.619 | 0 | 108.1197 | 0 | 0.97619 | 0 | 1.0812 | 0 | 0.97619 | 1.0812 | 56.1839 | 41.0152 | 55.2077
39029.3663 | 2481 | 0 | 39029.3663 | 1853 | 0 |  | 778.5 | 930.5 | 151.4652 | 0 | 113.1258 | 0 | 1.5147 | 0 | 1.1313 | 0 | 1.5147 | 1.1313 | 0.66022 | 34.775 | 0.85443
39029.3684 | 2123 | 0 | 39029.3684 | 1972 | 0 |  | 963.5 | 1115.5 | 129.6093 | 0 | 120.3907 | 0 | 1.2961 | 0 | 1.2039 | 0 | 1.2961 | 1.2039 | 17.6345 | 26.642 | 16.3384
39029.3705 | 2236 | 0 | 39029.3706 | 1921 | 0 |  | 1148.5 | 1300.5 | 136.5079 | 0 | 117.2772 | 0 | 1.3651 | 0 | 1.1728 | 0 | 1.3651 | 1.1728 | 11.6896 | 30.0042 | 10.3245
39029.3727 | 2043 | 0 | 39029.3727 | 314 | 0 |  | 1333 | 1485 | 124.7253 | 0 | 19.1697 | 0 | 1.2473 | 0 | 0.1917 | 0 | 1.2473 | 0.1917 | 22.2408 | 695.3439 | 20.9936
39029.3748 | 2146 | 0 | 39029.3748 | 422 | 0 |  | 1517.5 | 1669.5 | 131.0134 | 0 | 25.7631 | 0 | 1.3101 | 0 | 0.25763 | 0 | 1.3101 | 0.25763 | 16.3737 | 491.7962 | 15.0636

## A1-B3
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 148.2527 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39029.3555 | 0 | 0 | 39029.3556 | 0 | 0 |  | -148 | 4 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 485576 | 485576 | 485575.9997
39029.3577 | 0 | 0 | 39029.3577 | 0 | 0 |  | 36.5 | 188.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 485576 | 485576 | 485575.9997
39029.3598 | 0 | 0 | 39029.3598 | 0 | 0 |  | 221.5 | 373.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 485576 | 485576 | 485575.9997
39029.362 | 4 | 0 | 39029.362 | 4 | 0 |  | 406.5 | 558.5 | 0.2442 | 0 | 0.2442 | 0 | 0.002442 | 0 | 0.002442 | 0 | 0.002442 | 0.002442 | 60609.5 | 60609.5 | 60609.4976
39029.3641 | 1874 | 0 | 39029.3641 | 2048 | 0 |  | 591 | 743 | 114.4078 | 0 | 125.0305 | 0 | 1.1441 | 0 | 1.2503 | 0 | 1.1441 | 1.2503 | 29.5827 | 18.5732 | 28.4386
39029.3662 | 2134 | 0 | 39029.3662 | 1658 | 0 |  | 776 | 928 | 130.2808 | 0 | 101.221 | 0 | 1.3028 | 0 | 1.0122 | 0 | 1.3028 | 1.0122 | 13.7948 | 46.4644 | 12.4919
39029.3684 | 2035 | 0 | 39029.3684 | 1533 | 0 |  | 960.5 | 1112.5 | 124.2369 | 0 | 93.5897 | 0 | 1.2424 | 0 | 0.9359 | 0 | 1.2424 | 0.9359 | 19.3307 | 58.407 | 18.0883
39029.3705 | 2412 | 0 | 39029.3705 | 2130 | 0 |  | 1145.5 | 1297.5 | 147.2527 | 0 | 130.0366 | 0 | 1.4725 | 0 | 1.3004 | 0 | 1.4725 | 1.3004 | 0.6791 | 14.0085 | 0.79342
39029.3726 | 1955 | 0 | 39029.3727 | 1306 | 0 |  | 1330 | 1482 | 119.3529 | 0 | 79.7314 | 0 | 1.1935 | 0 | 0.79731 | 0 | 1.1935 | 0.79731 | 24.2138 | 85.9403 | 23.0203
39029.3748 | 2273 | 0 | 39029.3748 | 529 | 0 |  | 1515 | 1667 | 138.7668 | 0 | 32.2955 | 0 | 1.3877 | 0 | 0.32295 | 0 | 1.3877 | 0.32295 | 6.8359 | 359.051 | 5.4482

## A1-A2
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 146.5433 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 200 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39029.3555 | 0 | 0 | 39029.3555 | 0 | 0 |  | -151 | 1 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 479976 | 479976 | 479975.9997
39029.3576 | 0 | 0 | 39029.3577 | 0 | 0 |  | 34 | 186 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 479976 | 479976 | 479975.9997
39029.3598 | 0 | 0 | 39029.3598 | 0 | 0 |  | 218.5 | 370.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 479976 | 479976 | 479975.9997
39029.3619 | 1211 | 901 | 39029.3619 | 1179 | 943 |  | 403.5 | 555.5 | 73.9316 | 55.0061 | 71.978 | 57.5702 | 0.73932 | 0.55006 | 0.71978 | 0.5757 | 0.18926 | 0.14408 | 363.2962 | 5182.4111 | 31.4007
39029.3641 | 1461 | 559 | 39029.3641 | 1539 | 428 |  | 588.5 | 740.5 | 89.1941 | 34.127 | 93.956 | 26.1294 | 0.89194 | 0.34127 | 0.93956 | 0.26129 | 0.55067 | 0.67827 | 365.525 | 86.666 | 31.5929
39029.3662 | 1982 | 1 | 39029.3662 | 1994 | 1 |  | 773 | 925 | 121.0012 | 0.06105 | 121.7338 | 0.06105 | 1.21 | 0.0006105 | 1.2173 | 0.0006105 | 1.2094 | 1.2167 | 21.1719 | 20.4388 | 7083.0562
39029.3683 | 2183 | 3 | 39029.3684 | 2384 | 2 |  | 958 | 1110 | 133.2723 | 0.18315 | 145.5433 | 0.1221 | 1.3327 | 0.0018315 | 1.4554 | 0.001221 | 1.3309 | 1.4542 | 12.4453 | 0.69233 | 49.1336
39029.3705 | 2211 | 1 | 39029.3705 | 1919 | 1 |  | 1142.5 | 1294.5 | 134.9817 | 0.06105 | 117.1551 | 0.06105 | 1.3498 | 0.0006105 | 1.1716 | 0.0006105 | 1.3492 | 1.1709 | 8.5846 | 25.2514 | 3797.8464
39029.3726 | 2104 | 0 | 39029.3726 | 2033 | 0 |  | 1327.5 | 1479.5 | 128.4493 | 0 | 124.1148 | 0 | 1.2845 | 0 | 1.2411 | 0 | 1.2845 | 1.2411 | 14.0865 | 18.0708 | 12.802
39029.3747 | 2264 | 1 | 39029.3748 | 2302 | 1 |  | 1512 | 1664 | 138.2173 | 0.06105 | 140.5372 | 0.06105 | 1.3822 | 0.0006105 | 1.4054 | 0.0006105 | 1.3816 | 1.4048 | 6.089 | 4.3063 | 558.9142

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 7 |  |  | 2006-11-08 | 8:39
39029.3555 | 0 | 0 | 1 | Mix | 7-C | Tray C | IRMS | 2
39029.3576 | 0 | 0 | 1 |  | 200 kW |  | Bundle
39029.3598 | 0 | 0 | 1
39029.3619 | 1211 | 901 | 1
39029.3641 | 1461 | 559 | 1
39029.3662 | 1982 | 1 | 1
39029.3683 | 2183 | 3 | 1
39029.3705 | 2211 | 1 | 1
39029.3726 | 2104 | 0 | 1
39029.3747 | 2264 | 1 | 1
1
39029.3555 | 0 | 0 | 2
39029.3577 | 0 | 0 | 2
39029.3598 | 0 | 0 | 2
39029.3619 | 1179 | 943 | 2
39029.3641 | 1539 | 428 | 2
39029.3662 | 1994 | 1 | 2
39029.3684 | 2384 | 2 | 2
39029.3705 | 1919 | 1 | 2
39029.3726 | 2033 | 0 | 2
39029.3748 | 2302 | 1 | 2
2
39029.3555 | 0 | 0 | 3
39029.3577 | 0 | 0 | 3
39029.3598 | 0 | 0 | 3
39029.362 | 4 | 0 | 3
39029.3641 | 1874 | 0 | 3
39029.3662 | 2134 | 0 | 3
39029.3684 | 2035 | 0 | 3
39029.3705 | 2412 | 0 | 3
39029.3726 | 1955 | 0 | 3
39029.3748 | 2273 | 0 | 3
3
39029.3556 | 0 | 0 | 4
39029.3577 | 0 | 0 | 4
39029.3598 | 0 | 0 | 4
39029.362 | 4 | 0 | 4
39029.3641 | 2048 | 0 | 4
39029.3662 | 1658 | 0 | 4
39029.3684 | 1533 | 0 | 4
39029.3705 | 2130 | 0 | 4
39029.3727 | 1306 | 0 | 4
39029.3748 | 529 | 0 | 4
4
39029.3556 | 0 | 0 | 5
39029.3577 | 0 | 0 | 5
39029.3598 | 0 | 0 | 5
39029.362 | 4 | 1 | 5
39029.3641 | 1599 | 0 | 5
39029.3663 | 2481 | 0 | 5
39029.3684 | 2123 | 0 | 5
39029.3705 | 2236 | 0 | 5
39029.3727 | 2043 | 0 | 5
39029.3748 | 2146 | 0 | 5
5
39029.3556 | 0 | 0 | 6
39029.3577 | 0 | 0 | 6
39029.3599 | 0 | 0 | 6
39029.362 | 4 | 0 | 6
39029.3641 | 1771 | 0 | 6
39029.3663 | 1853 | 0 | 6
39029.3684 | 1972 | 0 | 6
39029.3706 | 1921 | 0 | 6
39029.3727 | 314 | 0 | 6
39029.3748 | 422 | 0 | 6
6
39029.3556 | 0 | 0 | 7
39029.3577 | 0 | 0 | 7
39029.3599 | 0 | 0 | 7
39029.362 | 3 | 0 | 7
39029.3642 | 1662 | 0 | 7
39029.3663 | 2351 | 0 | 7
39029.3684 | 2003 | 0 | 7
39029.3706 | 1999 | 0 | 7
39029.3727 | 2228 | 0 | 7
39029.3748 | 2004 | 0 | 7
7
39029.3556 | 0 | 0 | 8
39029.3578 | 0 | 0 | 8
39029.3599 | 0 | 0 | 8
39029.362 | 4 | 0 | 8
39029.3642 | 2191 | 0 | 8
39029.3663 | 2476 | 0 | 8
39029.3684 | 2114 | 0 | 8
39029.3706 | 2032 | 0 | 8
39029.3727 | 2046 | 0 | 8
39029.3749 | 1970 | 0 | 8
8
39029.3556 | 0 | 0 | 9
39029.3578 | 0 | 0 | 9
39029.3599 | 0 | 0 | 9
39029.362 | 3 | 0 | 9
39029.3642 | 1426 | 0 | 9
39029.3663 | 2405 | 0 | 9
39029.3685 | 2076 | 0 | 9
39029.3706 | 2290 | 0 | 9
39029.3727 | 2487 | 0 | 9
39029.3749 | 1962 | 0 | 9
9
39029.3556 | 0 | 0 | 10
39029.3578 | 0 | 0 | 10
39029.3599 | 0 | 0 | 10
39029.3621 | 4 | 0 | 10
39029.3642 | 1976 | 0 | 10
39029.3663 | 2081 | 0 | 10
39029.3685 | 2458 | 0 | 10
39029.3706 | 2187 | 0 | 10
39029.3728 | 1936 | 0 | 10
39029.3749 | 1585 | 0 | 10
10
39029.3557 | 0 | 0 | 11
39029.3578 | 0 | 0 | 11
39029.3599 | 0 | 0 | 11
39029.3621 | 4 | 0 | 11
39029.3642 | 1360 | 0 | 11
39029.3664 | 2226 | 0 | 11
39029.3685 | 2400 | 0 | 11
39029.3706 | 2194 | 0 | 11
39029.3728 | 1992 | 0 | 11
39029.3749 | 2059 | 0 | 11
11
39029.3557 | 0 | 0 | 12
39029.3578 | 0 | 0 | 12
39029.36 | 2202 | 0 | 12
39029.3621 | 2029 | 0 | 12
39029.3642 | 2031 | 0 | 12
39029.3664 | 2260 | 0 | 12
39029.3685 | 2102 | 0 | 12
39029.3706 | 2616 | 0 | 12
39029.3728 | 2344 | 0 | 12
39029.3749 | 2273 | 0 | 12
12
39029.3557 | 0 | 0 | 13
39029.3578 | 0 | 0 | 13
39029.36 | 4 | 0 | 13
39029.3621 | 4 | 0 | 13
39029.3642 | 1262 | 0 | 13
39029.3664 | 2074 | 0 | 13
39029.3685 | 2231 | 0 | 13
39029.3707 | 2379 | 0 | 13
39029.3728 | 2545 | 0 | 13
39029.3749 | 2343 | 0 | 13
13
39029.3557 | 0 | 0 | 14
39029.3578 | 0 | 0 | 14
39029.36 | 1805 | 0 | 14
39029.3621 | 2119 | 0 | 14
39029.3643 | 2016 | 0 | 14
39029.3664 | 2551 | 0 | 14
39029.3685 | 2029 | 0 | 14
39029.3707 | 2031 | 0 | 14
39029.3728 | 2242 | 0 | 14
39029.375 | 2137 | 0 | 14
14
39029.3557 | 0 | 0 | 15
39029.3579 | 0 | 0 | 15
39029.36 | 4 | 0 | 15
39029.3621 | 4 | 0 | 15
39029.3643 | 1905 | 0 | 15
39029.3664 | 2015 | 0 | 15
39029.3686 | 2463 | 0 | 15
39029.3707 | 2151 | 0 | 15
39029.3728 | 2180 | 0 | 15
39029.375 | 2047 | 0 | 15
15
39029.3557 | 0 | 0 | 16
39029.3579 | 0 | 0 | 16
39029.36 | 2 | 0 | 16
39029.3622 | 2549 | 0 | 16
39029.3643 | 2002 | 0 | 16
39029.3664 | 2183 | 0 | 16
39029.3686 | 2040 | 0 | 16
39029.3707 | 2316 | 0 | 16
39029.3729 | 2283 | 0 | 16
39029.375 | 1757 | 0 | 16
16
39029.3558 | 0 | 0 | 17
39029.3579 | 0 | 0 | 17
39029.36 | 1 | 0 | 17
39029.3622 | 4 | 0 | 17
39029.3643 | 1841 | 0 | 17
39029.3665 | 1962 | 0 | 17
39029.3686 | 2487 | 0 | 17
39029.3707 | 2296 | 0 | 17
39029.3729 | 2079 | 0 | 17
39029.375 | 2130 | 0 | 17
17
39029.3558 | 0 | 0 | 18
39029.3579 | 0 | 0 | 18
39029.3601 | 1070 | 15 | 18
39029.3622 | 2299 | 0 | 18
39029.3643 | 2106 | 0 | 18
39029.3665 | 2338 | 0 | 18
39029.3686 | 2046 | 0 | 18
39029.3708 | 1956 | 0 | 18
39029.3729 | 2519 | 0 | 18
39029.375 | 1599 | 0 | 18
18
39029.3558 | 0 | 0 | 19
39029.3579 | 0 | 0 | 19
39029.3601 | 1 | 0 | 19
39029.3622 | 3 | 0 | 19
39029.3644 | 2191 | 0 | 19
39029.3665 | 2070 | 0 | 19
39029.3686 | 2186 | 0 | 19
39029.3708 | 2375 | 0 | 19
39029.3729 | 2310 | 0 | 19
39029.375 | 1968 | 0 | 19
19
39029.3558 | 0 | 0 | 20
39029.358 | 0 | 0 | 20
39029.3601 | 1 | 0 | 20
39029.3622 | 2589 | 0 | 20
39029.3644 | 1978 | 0 | 20
39029.3665 | 2608 | 0 | 20
39029.3686 | 2291 | 0 | 20
39029.3708 | 2206 | 0 | 20
39029.3729 | 2476 | 0 | 20
39029.3751 | 2590 | 0 | 20
20
39029.3558 | 0 | 0 | 21
39029.358 | 0 | 0 | 21
39029.3601 | 1 | 0 | 21
39029.3622 | 4 | 0 | 21
39029.3644 | 1850 | 0 | 21
39029.3665 | 2004 | 0 | 21
39029.3687 | 1969 | 0 | 21
39029.3708 | 2525 | 0 | 21
39029.3729 | 2391 | 0 | 21
39029.3751 | 2199 | 0 | 21
21
39029.3558 | 0 | 0 | 22
39029.358 | 0 | 0 | 22
39029.3601 | 1 | 0 | 22
39029.3623 | 2087 | 0 | 22
39029.3644 | 2295 | 0 | 22
39029.3665 | 2055 | 0 | 22
39029.3687 | 2030 | 0 | 22
39029.3708 | 2229 | 0 | 22
39029.373 | 2595 | 0 | 22
39029.3751 | 2225 | 0 | 22
22
39029.3559 | 0 | 0 | 23
39029.358 | 0 | 0 | 23
39029.3601 | 0 | 0 | 23
39029.3623 | 4 | 0 | 23
39029.3644 | 2078 | 0 | 23
39029.3666 | 2327 | 0 | 23
39029.3687 | 2339 | 0 | 23
39029.3708 | 2250 | 0 | 23
39029.373 | 1961 | 0 | 23
39029.3751 | 2340 | 0 | 23
23
39029.3559 | 0 | 0 | 24
39029.358 | 0 | 0 | 24
39029.3602 | 0 | 0 | 24
39029.3623 | 4 | 0 | 24
39029.3644 | 1853 | 0 | 24
39029.3666 | 1411 | 0 | 24
39029.3687 | 1749 | 0 | 24
39029.3708 | 1327 | 0 | 24
39029.373 | 412 | 0 | 24
39029.3751 | 289 | 0 | 24
24
39029.3559 | 0 | 0 | 25
39029.358 | 0 | 0 | 25
39029.3602 | 0 | 0 | 25
39029.3623 | 3 | 0 | 25
39029.3644 | 1901 | 0 | 25
39029.3666 | 2513 | 0 | 25
39029.3687 | 1967 | 0 | 25
39029.3709 | 2041 | 0 | 25
39029.373 | 1953 | 0 | 25
39029.3751 | 2509 | 0 | 25
25
39029.3559 | 0 | 0 | 26
39029.358 | 0 | 0 | 26
39029.3602 | 0 | 0 | 26
39029.3623 | 3 | 0 | 26
39029.3645 | 2389 | 0 | 26
39029.3666 | 2454 | 0 | 26
39029.3687 | 2183 | 0 | 26
39029.3709 | 2042 | 0 | 26
39029.373 | 2227 | 0 | 26
39029.3752 | 1945 | 0 | 26
26
39029.3559 | 0 | 0 | 27
39029.3581 | 0 | 0 | 27
39029.3602 | 0 | 0 | 27
39029.3623 | 3 | 0 | 27
39029.3645 | 2398 | 0 | 27
39029.3666 | 2041 | 0 | 27
39029.3688 | 1907 | 0 | 27
39029.3709 | 2483 | 0 | 27
39029.373 | 2567 | 0 | 27
39029.3752 | 1916 | 0 | 27
27
39029.3559 | 0 | 0 | 28
39029.3581 | 0 | 0 | 28
39029.3602 | 0 | 0 | 28
39029.3624 | 3 | 0 | 28
39029.3645 | 2485 | 0 | 28
39029.3666 | 1941 | 0 | 28
39029.3688 | 2254 | 0 | 28
39029.3709 | 2175 | 0 | 28
39029.373 | 2378 | 0 | 28
39029.3752 | 1803 | 0 | 28
28
39029.356 | 0 | 0 | 29
39029.3581 | 0 | 0 | 29
39029.3602 | 0 | 0 | 29
39029.3624 | 3 | 0 | 29
39029.3645 | 2241 | 0 | 29
39029.3667 | 2336 | 0 | 29
39029.3688 | 1996 | 0 | 29
39029.3709 | 2166 | 0 | 29
39029.3731 | 2014 | 0 | 29
39029.3752 | 2131 | 0 | 29
29
39029.356 | 0 | 0 | 30
39029.3581 | 0 | 0 | 30
39029.3603 | 0 | 0 | 30
39029.3624 | 3 | 0 | 30
39029.3645 | 1897 | 0 | 30
39029.3667 | 1957 | 0 | 30
39029.3688 | 2524 | 0 | 30
39029.3709 | 2371 | 0 | 30
39029.3731 | 2082 | 0 | 30
39029.3752 | 1665 | 0 | 30
30
39029.356 | 0 | 0 | 31
39029.3581 | 0 | 0 | 31
39029.3603 | 0 | 0 | 31
39029.3624 | 3 | 0 | 31
39029.3645 | 2398 | 0 | 31
39029.3667 | 2128 | 0 | 31
39029.3688 | 1969 | 0 | 31
39029.371 | 2100 | 0 | 31
39029.3731 | 2470 | 0 | 31
39029.3752 | 2414 | 0 | 31
31
39029.356 | 0 | 0 | 32
39029.3581 | 0 | 0 | 32
39029.3603 | 2420 | 0 | 32
39029.3624 | 2488 | 0 | 32
39029.3646 | 2051 | 0 | 32
39029.3667 | 2106 | 0 | 32
39029.3688 | 2427 | 0 | 32
39029.371 | 2064 | 0 | 32
39029.3731 | 2455 | 0 | 32
39029.3753 | 2396 | 0 | 32
32
39029.356 | 0 | 0 | 33
39029.3582 | 0 | 0 | 33
39029.3603 | 4 | 0 | 33
39029.3624 | 4 | 0 | 33
39029.3646 | 2346 | 0 | 33
39029.3667 | 2445 | 0 | 33
39029.3689 | 2198 | 0 | 33
39029.371 | 2466 | 0 | 33
39029.3731 | 2254 | 0 | 33
39029.3753 | 2357 | 0 | 33
33
39029.356 | 0 | 0 | 34
39029.3582 | 0 | 0 | 34
39029.3603 | 2567 | 0 | 34
39029.3625 | 2052 | 0 | 34
39029.3646 | 2396 | 0 | 34
39029.3667 | 2027 | 0 | 34
39029.3689 | 2034 | 0 | 34
39029.371 | 2028 | 0 | 34
39029.3731 | 2605 | 0 | 34
39029.3753 | 2031 | 0 | 34
34
39029.3561 | 0 | 0 | 35
39029.3582 | 0 | 0 | 35
39029.3603 | 4 | 0 | 35
39029.3625 | 4 | 0 | 35
39029.3646 | 2109 | 0 | 35
39029.3667 | 1985 | 0 | 35
39029.3689 | 2408 | 0 | 35
39029.371 | 1928 | 0 | 35
39029.3732 | 2527 | 0 | 35
39029.3753 | 1965 | 0 | 35
35
39029.3561 | 0 | 0 | 36
39029.3582 | 0 | 0 | 36
39029.3603 | 3 | 0 | 36
39029.3625 | 1950 | 0 | 36
39029.3646 | 2103 | 0 | 36
39029.3668 | 2124 | 0 | 36
39029.3689 | 2168 | 0 | 36
39029.371 | 2401 | 0 | 36
39029.3732 | 1967 | 0 | 36
39029.3753 | 1973 | 0 | 36
36
39029.3561 | 0 | 0 | 37
39029.3582 | 0 | 0 | 37
39029.3604 | 1 | 0 | 37
39029.3625 | 4 | 0 | 37
39029.3646 | 2325 | 0 | 37
39029.3668 | 2458 | 0 | 37
39029.3689 | 1923 | 0 | 37
39029.3711 | 2024 | 0 | 37
39029.3732 | 2101 | 0 | 37
39029.3753 | 2463 | 0 | 37
37
39029.3561 | 0 | 0 | 38
39029.3582 | 0 | 0 | 38
39029.3604 | 2146 | 0 | 38
39029.3625 | 2540 | 0 | 38
39029.3647 | 2531 | 0 | 38
39029.3668 | 2479 | 0 | 38
39029.3689 | 2079 | 0 | 38
39029.3711 | 2193 | 0 | 38
39029.3732 | 2505 | 0 | 38
39029.3753 | 1605 | 0 | 38
38
39029.3561 | 0 | 0 | 39
39029.3583 | 0 | 0 | 39
39029.3604 | 4 | 0 | 39
39029.3625 | 4 | 0 | 39
39029.3647 | 2343 | 0 | 39
39029.3668 | 2126 | 0 | 39
39029.3689 | 2017 | 0 | 39
39029.3711 | 2221 | 0 | 39
39029.3732 | 2167 | 0 | 39
39029.3754 | 2502 | 0 | 39
39
39029.3561 | 0 | 0 | 40
39029.3583 | 0 | 0 | 40
39029.3604 | 3 | 0 | 40
39029.3625 | 2018 | 0 | 40
39029.3647 | 2412 | 0 | 40
39029.3668 | 2091 | 0 | 40
39029.369 | 2446 | 0 | 40
39029.3711 | 2000 | 0 | 40
39029.3732 | 2561 | 0 | 40
39029.3754 | 1975 | 0 | 40
40
39029.3561 | 0 | 0 | 41
39029.3583 | 0 | 0 | 41
39029.3604 | 2 | 0 | 41
39029.3626 | 4 | 0 | 41
39029.3647 | 2399 | 0 | 41
39029.3668 | 1994 | 0 | 41
39029.369 | 2258 | 0 | 41
39029.3711 | 2484 | 0 | 41
39029.3733 | 2254 | 0 | 41
39029.3754 | 2252 | 0 | 41
41
39029.3562 | 0 | 0 | 42
39029.3583 | 0 | 0 | 42
39029.3605 | 1 | 0 | 42
39029.3626 | 1974 | 0 | 42
39029.3647 | 2144 | 0 | 42
39029.3669 | 2067 | 0 | 42
39029.369 | 1983 | 0 | 42
39029.3711 | 2247 | 0 | 42
39029.3733 | 2066 | 0 | 42
39029.3754 | 2204 | 0 | 42
42
39029.3562 | 0 | 0 | 43
39029.3583 | 0 | 0 | 43
39029.3605 | 1 | 0 | 43
39029.3626 | 348 | 13 | 43
39029.3647 | 2102 | 12 | 43
39029.3669 | 1556 | 1 | 43
39029.369 | 2132 | 100 | 43
39029.3712 | 1516 | 451 | 43
39029.3733 | 1134 | 843 | 43
39029.3754 | 1039 | 1062 | 43
43
39029.3562 | 0 | 0 | 44
39029.3583 | 0 | 0 | 44
39029.3605 | 1 | 0 | 44
39029.3626 | 1481 | 0 | 44
39029.3648 | 2008 | 10 | 44
39029.3669 | 2003 | 72 | 44
39029.369 | 1965 | 271 | 44
39029.3712 | 1661 | 558 | 44
39029.3733 | 1108 | 1057 | 44
39029.3755 | 992 | 850 | 44
44
39029.3562 | 0 | 0 | 45
39029.3584 | 0 | 0 | 45
39029.3605 | 1 | 0 | 45
39029.3626 | 1113 | 0 | 45
39029.3648 | 1847 | 0 | 45
39029.3669 | 1652 | 0 | 45
39029.3691 | 1853 | 0 | 45
39029.3712 | 1123 | 0 | 45
39029.3733 | 1177 | 1 | 45
39029.3755 | 145 | 0 | 45
45
39029.3562 | 0 | 0 | 46
39029.3584 | 0 | 0 | 46
39029.3605 | 1 | 0 | 46
39029.3627 | 3 | 0 | 46
39029.3648 | 2319 | 0 | 46
39029.3669 | 2507 | 0 | 46
39029.3691 | 2081 | 0 | 46
39029.3712 | 2227 | 0 | 46
39029.3733 | 2010 | 0 | 46
39029.3755 | 1772 | 0 | 46
46
39029.3562 | 0 | 0 | 47
39029.3584 | 0 | 0 | 47
39029.3605 | 1 | 0 | 47
39029.3627 | 584 | 0 | 47
39029.3648 | 1792 | 0 | 47
39029.3669 | 1210 | 0 | 47
39029.3691 | 1681 | 0 | 47
39029.3712 | 1175 | 0 | 47
39029.3734 | 1638 | 0 | 47
39029.3755 | 22 | 0 | 47
47
39029.3563 | 0 | 0 | 48
39029.3584 | 0 | 0 | 48
39029.3605 | 0 | 0 | 48
39029.3627 | 3 | 0 | 48
39029.3648 | 2131 | 0 | 48
39029.367 | 2463 | 0 | 48
39029.3691 | 1940 | 0 | 48
39029.3712 | 1979 | 0 | 48
39029.3734 | 2270 | 0 | 48
39029.3755 | 1327 | 0 | 48
48
39029.3563 | 0 | 0 | 49
39029.3584 | 0 | 0 | 49
39029.3606 | 1 | 0 | 49
39029.3627 | 399 | 0 | 49
39029.3648 | 1982 | 0 | 49
39029.367 | 1767 | 0 | 49
39029.3691 | 1490 | 0 | 49
39029.3712 | 1393 | 0 | 49
39029.3734 | 303 | 0 | 49
39029.3755 | 46 | 0 | 49
49
39029.3563 | 0 | 0 | 50
39029.3584 | 0 | 0 | 50
39029.3606 | 2532 | 0 | 50
39029.3627 | 2172 | 0 | 50
39029.3648 | 2535 | 0 | 50
39029.367 | 2223 | 0 | 50
39029.3691 | 2099 | 0 | 50
39029.3713 | 2446 | 0 | 50
39029.3734 | 2426 | 0 | 50
39029.3755 | 2062 | 0 | 50
50
39029.3563 | 0 | 0 | 51
39029.3584 | 0 | 0 | 51
39029.3606 | 4 | 0 | 51
39029.3627 | 1139 | 0 | 51
39029.3649 | 2279 | 0 | 51
39029.367 | 1494 | 0 | 51
39029.3691 | 1814 | 0 | 51
39029.3713 | 1492 | 0 | 51
39029.3734 | 204 | 0 | 51
39029.3756 | 15 | 0 | 51
51
39029.3563 | 0 | 0 | 52
39029.3585 | 0 | 0 | 52
39029.3606 | 2002 | 0 | 52
39029.3627 | 2544 | 0 | 52
39029.3649 | 2006 | 0 | 52
39029.367 | 2523 | 0 | 52
39029.3692 | 2082 | 0 | 52
39029.3713 | 2497 | 0 | 52
39029.3734 | 2142 | 0 | 52
39029.3756 | 2564 | 0 | 52
52
39029.3563 | 0 | 0 | 53
39029.3585 | 0 | 0 | 53
39029.3606 | 4 | 0 | 53
39029.3628 | 1146 | 0 | 53
39029.3649 | 2033 | 0 | 53
39029.367 | 1311 | 0 | 53
39029.3692 | 1833 | 0 | 53
39029.3713 | 1098 | 0 | 53
39029.3734 | 334 | 0 | 53
39029.3756 | 6 | 0 | 53
53
39029.3564 | 0 | 0 | 54
39029.3585 | 0 | 0 | 54
39029.3606 | 3 | 0 | 54
39029.3628 | 2382 | 0 | 54
39029.3649 | 2125 | 0 | 54
39029.3671 | 2082 | 0 | 54
39029.3692 | 1922 | 0 | 54
39029.3713 | 2203 | 0 | 54
39029.3735 | 2488 | 0 | 54
39029.3756 | 2223 | 0 | 54
54
39029.3564 | 0 | 0 | 55
39029.3585 | 0 | 0 | 55
39029.3607 | 1 | 0 | 55
39029.3628 | 680 | 0 | 55
39029.3649 | 2133 | 0 | 55
39029.3671 | 1531 | 0 | 55
39029.3692 | 1508 | 0 | 55
39029.3714 | 1609 | 0 | 55
39029.3735 | 959 | 0 | 55
39029.3756 | 1 | 0 | 55
55
39029.3564 | 0 | 0 | 56
39029.3585 | 0 | 0 | 56
39029.3607 | 2072 | 0 | 56
39029.3628 | 2538 | 0 | 56
39029.365 | 2220 | 0 | 56
39029.3671 | 2511 | 0 | 56
39029.3692 | 2114 | 0 | 56
39029.3714 | 2320 | 0 | 56
39029.3735 | 1956 | 0 | 56
39029.3756 | 1754 | 0 | 56
56
39029.3564 | 0 | 0 | 57
39029.3586 | 0 | 0 | 57
39029.3607 | 5 | 0 | 57
39029.3628 | 682 | 0 | 57
39029.365 | 1782 | 0 | 57
39029.3671 | 1240 | 0 | 57
39029.3692 | 1515 | 0 | 57
39029.3714 | 1651 | 0 | 57
39029.3735 | 433 | 0 | 57
39029.3757 | 2 | 0 | 57
57
39029.3564 | 0 | 0 | 58
39029.3586 | 0 | 0 | 58
39029.3607 | 3 | 0 | 58
39029.3628 | 2592 | 0 | 58
39029.365 | 1973 | 0 | 58
39029.3671 | 2549 | 0 | 58
39029.3693 | 2587 | 0 | 58
39029.3714 | 2074 | 0 | 58
39029.3735 | 2255 | 0 | 58
39029.3757 | 2334 | 0 | 58
58
39029.3564 | 0 | 0 | 59
39029.3586 | 0 | 0 | 59
39029.3607 | 2 | 0 | 59
39029.3629 | 1002 | 0 | 59
39029.365 | 1906 | 0 | 59
39029.3671 | 1337 | 0 | 59
39029.3693 | 1669 | 0 | 59
39029.3714 | 1348 | 0 | 59
39029.3736 | 343 | 0 | 59
39029.3757 | 1 | 0 | 59
59
39029.3565 | 0 | 0 | 60
39029.3586 | 0 | 0 | 60
39029.3607 | 2207 | 0 | 60
39029.3629 | 2392 | 0 | 60
39029.365 | 2177 | 0 | 60
39029.3672 | 2301 | 0 | 60
39029.3693 | 2447 | 0 | 60
39029.3714 | 2341 | 0 | 60
39029.3736 | 2408 | 0 | 60
39029.3757 | 2218 | 0 | 60
60
39029.3565 | 0 | 0 | 61
39029.3586 | 0 | 0 | 61
39029.3608 | 4 | 0 | 61
39029.3629 | 1396 | 0 | 61
39029.365 | 1949 | 0 | 61
39029.3672 | 1865 | 0 | 61
39029.3693 | 1905 | 0 | 61
39029.3714 | 1181 | 0 | 61
39029.3736 | 303 | 0 | 61
39029.3757 | 2 | 0 | 61
61
39029.3565 | 0 | 0 | 62
39029.3586 | 0 | 0 | 62
39029.3608 | 2 | 0 | 62
39029.3629 | 4 | 0 | 62
39029.365 | 2474 | 0 | 62
39029.3672 | 2422 | 0 | 62
39029.3693 | 2233 | 0 | 62
39029.3715 | 2008 | 0 | 62
39029.3736 | 2057 | 0 | 62
39029.3757 | 1776 | 0 | 62
62
39029.3565 | 0 | 0 | 63
39029.3586 | 0 | 0 | 63
39029.3608 | 1 | 0 | 63
39029.3629 | 1483 | 0 | 63
39029.3651 | 2024 | 0 | 63
39029.3672 | 1417 | 0 | 63
39029.3693 | 1735 | 0 | 63
39029.3715 | 1329 | 0 | 63
39029.3736 | 318 | 0 | 63
39029.3758 | 26 | 0 | 63
63
39029.3565 | 0 | 0 | 64
39029.3587 | 0 | 0 | 64
39029.3608 | 1 | 0 | 64
39029.3629 | 4 | 0 | 64
39029.3651 | 2425 | 0 | 64
39029.3672 | 2325 | 0 | 64
39029.3694 | 2487 | 0 | 64
39029.3715 | 2113 | 0 | 64
39029.3736 | 2489 | 0 | 64
39029.3758 | 1988 | 0 | 64
64
39029.3565 | 0 | 0 | 65
39029.3587 | 0 | 0 | 65
39029.3608 | 1 | 0 | 65
39029.363 | 1286 | 0 | 65
39029.3651 | 2107 | 0 | 65
39029.3672 | 1338 | 0 | 65
39029.3694 | 1844 | 0 | 65
39029.3715 | 641 | 0 | 65
39029.3736 | 306 | 0 | 65
39029.3758 | 33 | 0 | 65
65
39029.3566 | 0 | 0 | 66
39029.3587 | 0 | 0 | 66
39029.3608 | 2605 | 0 | 66
39029.363 | 2542 | 0 | 66
39029.3651 | 1995 | 0 | 66
39029.3672 | 2184 | 0 | 66
39029.3694 | 2412 | 0 | 66
39029.3715 | 2406 | 0 | 66
39029.3737 | 2267 | 0 | 66
39029.3758 | 2060 | 0 | 66
66
39029.3566 | 0 | 0 | 67
39029.3587 | 0 | 0 | 67
39029.3608 | 4 | 0 | 67
39029.363 | 1222 | 0 | 67
39029.3651 | 2079 | 0 | 67
39029.3673 | 1625 | 0 | 67
39029.3694 | 1414 | 0 | 67
39029.3715 | 1478 | 0 | 67
39029.3737 | 440 | 0 | 67
39029.3758 | 47 | 0 | 67
67
39029.3566 | 0 | 0 | 68
39029.3587 | 0 | 0 | 68
39029.3609 | 2533 | 0 | 68
39029.363 | 2261 | 0 | 68
39029.3651 | 2179 | 0 | 68
39029.3673 | 2060 | 0 | 68
39029.3694 | 2595 | 0 | 68
39029.3716 | 2506 | 0 | 68
39029.3737 | 2608 | 0 | 68
39029.3758 | 2600 | 0 | 68
68
39029.3566 | 0 | 0 | 69
39029.3587 | 0 | 0 | 69
39029.3609 | 5 | 0 | 69
39029.363 | 1139 | 0 | 69
39029.3652 | 1996 | 0 | 69
39029.3673 | 1632 | 0 | 69
39029.3694 | 1544 | 0 | 69
39029.3716 | 691 | 0 | 69
39029.3737 | 485 | 0 | 69
39029.3759 | 65 | 0 | 69
69
39029.3566 | 0 | 0 | 70
39029.3588 | 0 | 0 | 70
39029.3609 | 3 | 0 | 70
39029.363 | 2091 | 0 | 70
39029.3652 | 2442 | 0 | 70
39029.3673 | 2207 | 0 | 70
39029.3695 | 2049 | 0 | 70
39029.3716 | 2339 | 0 | 70
39029.3737 | 2239 | 0 | 70
39029.3759 | 1854 | 0 | 70
70
39029.3566 | 0 | 0 | 71
39029.3588 | 0 | 0 | 71
39029.3609 | 2 | 0 | 71
39029.3631 | 1206 | 0 | 71
39029.3652 | 1950 | 0 | 71
39029.3673 | 1424 | 0 | 71
39029.3695 | 1771 | 0 | 71
39029.3716 | 1752 | 0 | 71
39029.3737 | 420 | 0 | 71
39029.3759 | 53 | 0 | 71
71
39029.3567 | 0 | 0 | 72
39029.3588 | 0 | 0 | 72
39029.3609 | 2448 | 0 | 72
39029.3631 | 2402 | 0 | 72
39029.3652 | 2281 | 0 | 72
39029.3673 | 2285 | 0 | 72
39029.3695 | 2346 | 0 | 72
39029.3716 | 1955 | 0 | 72
39029.3738 | 1659 | 0 | 72
39029.3759 | 2140 | 0 | 72
72
39029.3567 | 0 | 0 | 73
39029.3588 | 0 | 0 | 73
39029.3609 | 4 | 0 | 73
39029.3631 | 1443 | 0 | 73
39029.3652 | 1972 | 0 | 73
39029.3674 | 1753 | 0 | 73
39029.3695 | 1718 | 0 | 73
39029.3716 | 1153 | 0 | 73
39029.3738 | 441 | 0 | 73
39029.3759 | 352 | 0 | 73
73
39029.3567 | 0 | 0 | 74
39029.3588 | 0 | 0 | 74
39029.361 | 2072 | 0 | 74
39029.3631 | 2220 | 0 | 74
39029.3652 | 2465 | 0 | 74
39029.3674 | 2019 | 0 | 74
39029.3695 | 2569 | 0 | 74
39029.3717 | 1988 | 0 | 74
39029.3738 | 2385 | 0 | 74
39029.3759 | 2129 | 0 | 74
74
39029.3567 | 0 | 0 | 75
39029.3588 | 0 | 0 | 75
39029.361 | 5 | 0 | 75
39029.3631 | 1839 | 0 | 75
39029.3653 | 1915 | 0 | 75
39029.3674 | 1584 | 0 | 75
39029.3695 | 1819 | 0 | 75
39029.3717 | 977 | 0 | 75
39029.3738 | 491 | 0 | 75
39029.3759 | 1 | 0 | 75
75
39029.3567 | 0 | 0 | 76
39029.3589 | 0 | 0 | 76
39029.361 | 2136 | 0 | 76
39029.3631 | 2040 | 0 | 76
39029.3653 | 2507 | 0 | 76
39029.3674 | 2169 | 0 | 76
39029.3695 | 2053 | 0 | 76
39029.3717 | 2501 | 0 | 76
39029.3738 | 2333 | 0 | 76
39029.376 | 2075 | 0 | 76
76
39029.3567 | 0 | 0 | 77
39029.3589 | 0 | 0 | 77
39029.361 | 5 | 0 | 77
39029.3631 | 1515 | 182 | 77
39029.3653 | 1938 | 5 | 77
39029.3674 | 2158 | 1 | 77
39029.3696 | 1927 | 0 | 77
39029.3717 | 2146 | 8 | 77
39029.3738 | 1989 | 5 | 77
39029.376 | 1557 | 633 | 77
77
39029.3567 | 0 | 0 | 78
39029.3589 | 0 | 0 | 78
39029.361 | 3 | 0 | 78
39029.3632 | 1542 | 4 | 78
39029.3653 | 2436 | 6 | 78
39029.3674 | 2057 | 0 | 78
39029.3696 | 2122 | 1 | 78
39029.3717 | 2359 | 7 | 78
39029.3739 | 2055 | 7 | 78
39029.376 | 1161 | 1035 | 78
78
39029.3568 | 0 | 0 | 79
39029.3589 | 0 | 0 | 79
39029.361 | 3 | 0 | 79
39029.3632 | 2306 | 0 | 79
39029.3653 | 2059 | 0 | 79
39029.3675 | 2259 | 0 | 79
39029.3696 | 2249 | 0 | 79
39029.3717 | 2131 | 0 | 79
39029.3739 | 2113 | 0 | 79
39029.376 | 1702 | 0 | 79
79
39029.3568 | 0 | 0 | 80
39029.3589 | 0 | 0 | 80
39029.3611 | 2552 | 0 | 80
39029.3632 | 2502 | 0 | 80
39029.3653 | 2209 | 0 | 80
39029.3675 | 2318 | 0 | 80
39029.3696 | 2001 | 0 | 80
39029.3717 | 2123 | 0 | 80
39029.3739 | 2506 | 0 | 80
39029.376 | 2594 | 0 | 80
80
39029.3568 | 0 | 0 | 81
39029.3589 | 0 | 0 | 81
39029.3611 | 4 | 0 | 81
39029.3632 | 2493 | 0 | 81
39029.3654 | 2274 | 0 | 81
39029.3675 | 2348 | 0 | 81
39029.3696 | 2012 | 0 | 81
39029.3718 | 2355 | 0 | 81
39029.3739 | 1946 | 0 | 81
39029.376 | 2183 | 0 | 81
81
39029.3568 | 0 | 0 | 82
39029.359 | 0 | 0 | 82
39029.3611 | 2234 | 0 | 82
39029.3632 | 2495 | 0 | 82
39029.3654 | 2479 | 0 | 82
39029.3675 | 2218 | 0 | 82
39029.3697 | 2010 | 0 | 82
39029.3718 | 2424 | 0 | 82
39029.3739 | 2050 | 0 | 82
39029.3761 | 2201 | 0 | 82
82
39029.3568 | 0 | 0 | 83
39029.359 | 0 | 0 | 83
39029.3611 | 5 | 0 | 83
39029.3633 | 1951 | 0 | 83
39029.3654 | 2084 | 0 | 83
39029.3675 | 2475 | 0 | 83
39029.3697 | 2185 | 0 | 83
39029.3718 | 2446 | 0 | 83
39029.3739 | 1875 | 0 | 83
39029.3761 | 2047 | 0 | 83
83
39029.3569 | 0 | 0 | 84
39029.359 | 0 | 0 | 84
39029.3611 | 3 | 0 | 84
39029.3633 | 2257 | 0 | 84
39029.3654 | 2515 | 0 | 84
39029.3675 | 2386 | 0 | 84
39029.3697 | 2432 | 0 | 84
39029.3718 | 2582 | 0 | 84
39029.374 | 1672 | 0 | 84
39029.3761 | 2012 | 0 | 84
84
39029.3569 | 0 | 0 | 85
39029.359 | 0 | 0 | 85
39029.3611 | 3 | 0 | 85
39029.3633 | 2162 | 0 | 85
39029.3654 | 2094 | 0 | 85
39029.3676 | 2365 | 0 | 85
39029.3697 | 2124 | 0 | 85
39029.3718 | 1946 | 0 | 85
39029.374 | 1887 | 0 | 85
39029.3761 | 1901 | 0 | 85
85
39029.3569 | 0 | 0 | 86
39029.359 | 0 | 0 | 86
39029.3612 | 2601 | 0 | 86
39029.3633 | 2036 | 0 | 86
39029.3654 | 2196 | 0 | 86
39029.3676 | 2231 | 0 | 86
39029.3697 | 2296 | 0 | 86
39029.3719 | 2451 | 0 | 86
39029.374 | 1436 | 0 | 86
39029.3761 | 2213 | 0 | 86
86
39029.3569 | 0 | 0 | 87
39029.359 | 0 | 0 | 87
39029.3612 | 4 | 0 | 87
39029.3633 | 2088 | 0 | 87
39029.3655 | 2267 | 0 | 87
39029.3676 | 2237 | 0 | 87
39029.3697 | 2029 | 0 | 87
39029.3719 | 1882 | 0 | 87
39029.374 | 2399 | 0 | 87
39029.3761 | 1829 | 0 | 87
87
39029.3569 | 0 | 0 | 88
39029.3591 | 0 | 0 | 88
39029.3612 | 2062 | 0 | 88
39029.3633 | 2251 | 0 | 88
39029.3655 | 1973 | 0 | 88
39029.3676 | 2273 | 0 | 88
39029.3697 | 2549 | 0 | 88
39029.3719 | 2570 | 0 | 88
39029.374 | 2598 | 0 | 88
39029.3762 | 2318 | 0 | 88
88
39029.3569 | 0 | 0 | 89
39029.3591 | 0 | 0 | 89
39029.3612 | 4 | 0 | 89
39029.3633 | 2530 | 0 | 89
39029.3655 | 1958 | 0 | 89
39029.3676 | 2103 | 0 | 89
39029.3698 | 2520 | 0 | 89
39029.3719 | 1996 | 0 | 89
39029.374 | 2267 | 0 | 89
39029.3762 | 1730 | 1 | 89
89
39029.3569 | 0 | 0 | 90
39029.3591 | 0 | 0 | 90
39029.3612 | 2573 | 0 | 90
39029.3634 | 2053 | 0 | 90
39029.3655 | 2079 | 0 | 90
39029.3676 | 2374 | 0 | 90
39029.3698 | 2354 | 0 | 90
39029.3719 | 2324 | 0 | 90
39029.3741 | 2277 | 0 | 90
39029.3762 | 2567 | 0 | 90
90
39029.357 | 0 | 0 | 91
39029.3591 | 0 | 0 | 91
39029.3612 | 4 | 0 | 91
39029.3634 | 2434 | 0 | 91
39029.3655 | 2257 | 0 | 91
39029.3677 | 1933 | 0 | 91
39029.3698 | 2157 | 0 | 91
39029.3719 | 2013 | 0 | 91
39029.3741 | 1814 | 0 | 91
39029.3762 | 1409 | 0 | 91
91
39029.357 | 0 | 0 | 92
39029.3591 | 0 | 0 | 92
39029.3613 | 2107 | 0 | 92
39029.3634 | 2088 | 0 | 92
39029.3655 | 2192 | 0 | 92
39029.3677 | 2509 | 0 | 92
39029.3698 | 2230 | 0 | 92
39029.3719 | 2613 | 0 | 92
39029.3741 | 2069 | 0 | 92
39029.3762 | 2274 | 0 | 92
92
39029.357 | 0 | 0 | 93
39029.3591 | 0 | 0 | 93
39029.3613 | 5 | 0 | 93
39029.3634 | 1930 | 0 | 93
39029.3655 | 2058 | 0 | 93
39029.3677 | 2490 | 0 | 93
39029.3698 | 2475 | 0 | 93
39029.372 | 2457 | 0 | 93
39029.3741 | 2259 | 0 | 93
39029.3762 | 1769 | 0 | 93
93
39029.357 | 0 | 0 | 94
39029.3591 | 0 | 0 | 94
39029.3613 | 2347 | 0 | 94
39029.3634 | 2022 | 0 | 94
39029.3656 | 2384 | 0 | 94
39029.3677 | 2618 | 0 | 94
39029.3698 | 2520 | 0 | 94
39029.372 | 2044 | 0 | 94
39029.3741 | 2489 | 0 | 94
39029.3763 | 2511 | 0 | 94
94
39029.357 | 0 | 0 | 95
39029.3592 | 0 | 0 | 95
39029.3613 | 4 | 0 | 95
39029.3634 | 2080 | 0 | 95
39029.3656 | 2319 | 0 | 95
39029.3677 | 2080 | 0 | 95
39029.3699 | 2497 | 0 | 95
39029.372 | 2215 | 0 | 95
39029.3741 | 2005 | 0 | 95
39029.3763 | 1543 | 0 | 95
95
39029.357 | 0 | 0 | 96
39029.3592 | 0 | 0 | 96
39029.3613 | 2210 | 0 | 96
39029.3635 | 2551 | 0 | 96
39029.3656 | 2431 | 0 | 96
39029.3677 | 2560 | 0 | 96
39029.3699 | 2505 | 0 | 96
39029.372 | 2391 | 0 | 96
39029.3742 | 1252 | 0 | 96
39029.3763 | 2326 | 0 | 96
96
39029.3571 | 0 | 0 | 97
39029.3592 | 0 | 0 | 97
39029.3613 | 4 | 0 | 97
39029.3635 | 2083 | 0 | 97
39029.3656 | 2471 | 0 | 97
39029.3678 | 2290 | 0 | 97
39029.3699 | 2174 | 0 | 97
39029.372 | 2448 | 0 | 97
39029.3742 | 2212 | 0 | 97
39029.3763 | 2186 | 1 | 97
97
39029.3571 | 0 | 0 | 98
39029.3592 | 0 | 0 | 98
39029.3614 | 2320 | 0 | 98
39029.3635 | 1975 | 0 | 98
39029.3656 | 2325 | 0 | 98
39029.3678 | 2004 | 0 | 98
39029.3699 | 2295 | 0 | 98
39029.372 | 1974 | 0 | 98
39029.3742 | 2240 | 2 | 98
39029.3763 | 1828 | 0 | 98
98
39029.3571 | 0 | 0 | 99
39029.3592 | 0 | 0 | 99
39029.3614 | 4 | 0 | 99
39029.3635 | 2412 | 0 | 99
39029.3656 | 2167 | 0 | 99
39029.3678 | 2468 | 0 | 99
39029.3699 | 1992 | 0 | 99
39029.3721 | 2317 | 0 | 99
39029.3742 | 2068 | 0 | 99
39029.3763 | 1804 | 0 | 99
99
39029.3571 | 0 | 0 | 100
39029.3592 | 0 | 0 | 100
39029.3614 | 1814 | 3 | 100
39029.3635 | 1998 | 0 | 100
39029.3657 | 2222 | 0 | 100
39029.3678 | 2502 | 0 | 100
39029.3699 | 2065 | 0 | 100
39029.3721 | 2110 | 0 | 100
39029.3742 | 2590 | 0 | 100
39029.3764 | 2511 | 0 | 100
100
39029.3571 | 0 | 0 | 101
39029.3593 | 0 | 0 | 101
39029.3614 | 4 | 0 | 101
39029.3635 | 2442 | 0 | 101
39029.3657 | 2026 | 0 | 101
39029.3678 | 2458 | 0 | 101
39029.37 | 2358 | 0 | 101
39029.3721 | 2239 | 0 | 101
39029.3742 | 2058 | 0 | 101
39029.3764 | 1755 | 0 | 101
101
39029.3571 | 0 | 0 | 102
39029.3593 | 0 | 0 | 102
39029.3614 | 2156 | 0 | 102
39029.3636 | 2284 | 0 | 102
39029.3657 | 2119 | 0 | 102
39029.3678 | 2276 | 0 | 102
39029.37 | 2274 | 0 | 102
39029.3721 | 2113 | 0 | 102
39029.3742 | 2167 | 0 | 102
39029.3764 | 2498 | 0 | 102
102
39029.3572 | 0 | 0 | 103
39029.3593 | 0 | 0 | 103
39029.3614 | 2086 | 0 | 103
39029.3636 | 2253 | 0 | 103
39029.3657 | 2049 | 0 | 103
39029.3678 | 2042 | 0 | 103
39029.37 | 2388 | 0 | 103
39029.3721 | 2109 | 0 | 103
39029.3743 | 2217 | 0 | 103
39029.3764 | 2018 | 0 | 103
103
39029.3572 | 0 | 0 | 104
39029.3593 | 0 | 0 | 104
39029.3614 | 2433 | 0 | 104
39029.3636 | 2131 | 0 | 104
39029.3657 | 2618 | 0 | 104
39029.3679 | 2398 | 0 | 104
39029.37 | 2529 | 0 | 104
39029.3721 | 2614 | 0 | 104
39029.3743 | 2597 | 0 | 104
39029.3764 | 2137 | 0 | 104
104
39029.3572 | 0 | 0 | 105
39029.3593 | 0 | 0 | 105
39029.3615 | 2103 | 0 | 105
39029.3636 | 2603 | 0 | 105
39029.3657 | 2343 | 0 | 105
39029.3679 | 2558 | 0 | 105
39029.37 | 2128 | 0 | 105
39029.3722 | 2283 | 0 | 105
39029.3743 | 2376 | 0 | 105
39029.3764 | 2438 | 0 | 105
105
39029.3572 | 0 | 0 | 106
39029.3593 | 0 | 0 | 106
39029.3615 | 2479 | 0 | 106
39029.3636 | 2141 | 0 | 106
39029.3658 | 2514 | 0 | 106
39029.3679 | 2485 | 0 | 106
39029.37 | 2077 | 0 | 106
39029.3722 | 1986 | 0 | 106
39029.3743 | 1284 | 0 | 106
39029.3764 | 2186 | 0 | 106
106
39029.3572 | 0 | 0 | 107
39029.3594 | 0 | 0 | 107
39029.3615 | 2150 | 0 | 107
39029.3636 | 2361 | 0 | 107
39029.3658 | 2051 | 0 | 107
39029.3679 | 2302 | 0 | 107
39029.37 | 2349 | 0 | 107
39029.3722 | 2073 | 0 | 107
39029.3743 | 2413 | 0 | 107
39029.3765 | 1993 | 0 | 107
107
39029.3572 | 0 | 0 | 108
39029.3594 | 0 | 0 | 108
39029.3615 | 2211 | 0 | 108
39029.3637 | 2230 | 0 | 108
39029.3658 | 2230 | 0 | 108
39029.3679 | 2001 | 0 | 108
39029.3701 | 2155 | 0 | 108
39029.3722 | 2476 | 0 | 108
39029.3743 | 1736 | 0 | 108
39029.3765 | 1810 | 0 | 108
108
39029.3573 | 0 | 0 | 109
39029.3594 | 0 | 0 | 109
39029.3615 | 2226 | 0 | 109
39029.3637 | 2597 | 0 | 109
39029.3658 | 2265 | 0 | 109
39029.368 | 2219 | 0 | 109
39029.3701 | 2608 | 0 | 109
39029.3722 | 2116 | 0 | 109
39029.3744 | 2465 | 0 | 109
39029.3765 | 2550 | 0 | 109
109
39029.3573 | 0 | 0 | 110
39029.3594 | 0 | 0 | 110
39029.3616 | 2547 | 0 | 110
39029.3637 | 2157 | 0 | 110
39029.3658 | 2042 | 0 | 110
39029.368 | 2615 | 0 | 110
39029.3701 | 2175 | 0 | 110
39029.3722 | 2411 | 0 | 110
39029.3744 | 2153 | 0 | 110
39029.3765 | 2475 | 0 | 110
110
39029.3573 | 0 | 0 | 111
39029.3594 | 0 | 0 | 111
39029.3616 | 2006 | 0 | 111
39029.3637 | 2029 | 0 | 111
39029.3658 | 2568 | 0 | 111
39029.368 | 2080 | 0 | 111
39029.3701 | 2110 | 0 | 111
39029.3723 | 2240 | 0 | 111
39029.3744 | 2614 | 0 | 111
39029.3765 | 2057 | 0 | 111
111
39029.3573 | 0 | 0 | 112
39029.3594 | 0 | 0 | 112
39029.3616 | 2360 | 0 | 112
39029.3637 | 2391 | 0 | 112
39029.3659 | 2283 | 0 | 112
39029.368 | 2546 | 0 | 112
39029.3701 | 2478 | 0 | 112
39029.3723 | 2064 | 1 | 112
39029.3744 | 2143 | 0 | 112
39029.3766 | 2222 | 0 | 112
112
39029.3573 | 0 | 0 | 113
39029.3595 | 0 | 0 | 113
39029.3616 | 2229 | 0 | 113
39029.3637 | 2052 | 0 | 113
39029.3659 | 2219 | 0 | 113
39029.368 | 2039 | 0 | 113
39029.3702 | 2064 | 0 | 113
39029.3723 | 2436 | 0 | 113
39029.3744 | 2412 | 0 | 113
39029.3766 | 2547 | 0 | 113
113
39029.3573 | 0 | 0 | 114
39029.3595 | 0 | 0 | 114
39029.3616 | 2073 | 0 | 114
39029.3637 | 2173 | 0 | 114
39029.3659 | 2464 | 0 | 114
39029.368 | 2256 | 0 | 114
39029.3702 | 2122 | 0 | 114
39029.3723 | 2402 | 0 | 114
39029.3744 | 1653 | 0 | 114
39029.3766 | 1789 | 0 | 114
114
39029.3573 | 0 | 0 | 115
39029.3595 | 0 | 0 | 115
39029.3616 | 1957 | 0 | 115
39029.3638 | 2185 | 0 | 115
39029.3659 | 2081 | 0 | 115
39029.368 | 2125 | 0 | 115
39029.3702 | 1997 | 0 | 115
39029.3723 | 2596 | 0 | 115
39029.3745 | 2018 | 0 | 115
39029.3766 | 2129 | 0 | 115
115
39029.3574 | 0 | 0 | 116
39029.3595 | 0 | 0 | 116
39029.3616 | 1622 | 0 | 116
39029.3638 | 2468 | 0 | 116
39029.3659 | 2059 | 0 | 116
39029.3681 | 2508 | 0 | 116
39029.3702 | 2127 | 0 | 116
39029.3723 | 2396 | 0 | 116
39029.3745 | 2527 | 0 | 116
39029.3766 | 2213 | 0 | 116
116
39029.3574 | 0 | 0 | 117
39029.3595 | 0 | 0 | 117
39029.3617 | 2374 | 0 | 117
39029.3638 | 2094 | 0 | 117
39029.3659 | 2228 | 0 | 117
39029.3681 | 2043 | 0 | 117
39029.3702 | 2053 | 0 | 117
39029.3723 | 2241 | 0 | 117
39029.3745 | 2109 | 0 | 117
39029.3766 | 2045 | 0 | 117
117
39029.3574 | 0 | 0 | 118
39029.3595 | 0 | 0 | 118
39029.3617 | 2524 | 0 | 118
39029.3638 | 2344 | 0 | 118
39029.3659 | 2495 | 0 | 118
39029.3681 | 1982 | 0 | 118
39029.3702 | 2538 | 0 | 118
39029.3724 | 2390 | 0 | 118
39029.3745 | 2330 | 0 | 118
39029.3766 | 2078 | 0 | 118
118
39029.3574 | 0 | 0 | 119
39029.3596 | 0 | 0 | 119
39029.3617 | 2563 | 0 | 119
39029.3638 | 2323 | 0 | 119
39029.366 | 2602 | 0 | 119
39029.3681 | 2170 | 0 | 119
39029.3702 | 2216 | 0 | 119
39029.3724 | 2347 | 0 | 119
39029.3745 | 2329 | 0 | 119
39029.3767 | 2304 | 0 | 119
119
39029.3574 | 0 | 0 | 120
39029.3596 | 0 | 0 | 120
39029.3617 | 2512 | 0 | 120
39029.3638 | 2094 | 0 | 120
39029.366 | 2596 | 0 | 120
39029.3681 | 2163 | 0 | 120
39029.3703 | 1992 | 0 | 120
39029.3724 | 2129 | 0 | 120
39029.3745 | 2187 | 0 | 120
39029.3767 | 2562 | 0 | 120
120
39029.3574 | 0 | 0 | 121
39029.3596 | 0 | 0 | 121
39029.3617 | 2456 | 0 | 121
39029.3639 | 2356 | 0 | 121
39029.366 | 2526 | 0 | 121
39029.3681 | 2217 | 0 | 121
39029.3703 | 2102 | 4 | 121
39029.3724 | 2502 | 0 | 121
39029.3746 | 2526 | 101 | 121
39029.3767 | 1160 | 940 | 121
121
39029.3575 | 0 | 0 | 122
39029.3596 | 0 | 0 | 122
39029.3617 | 37 | 0 | 122
39029.3639 | 1917 | 0 | 122
39029.366 | 2195 | 0 | 122
39029.3682 | 2384 | 0 | 122
39029.3703 | 1903 | 10 | 122
39029.3724 | 1871 | 0 | 122
39029.3746 | 1273 | 805 | 122
39029.3767 | 1077 | 997 | 122
122
39029.3575 | 0 | 0 | 123
39029.3596 | 0 | 0 | 123
39029.3618 | 2222 | 0 | 123
39029.3639 | 2470 | 0 | 123
39029.366 | 2427 | 0 | 123
39029.3682 | 2321 | 0 | 123
39029.3703 | 2390 | 0 | 123
39029.3725 | 2294 | 0 | 123
39029.3746 | 924 | 0 | 123
39029.3767 | 1513 | 0 | 123
123
39029.3575 | 0 | 0 | 124
39029.3596 | 0 | 0 | 124
39029.3618 | 2590 | 0 | 124
39029.3639 | 2050 | 0 | 124
39029.3661 | 2194 | 0 | 124
39029.3682 | 2223 | 0 | 124
39029.3703 | 2312 | 0 | 124
39029.3725 | 2610 | 0 | 124
39029.3746 | 2216 | 0 | 124
39029.3767 | 2325 | 1 | 124
124
39029.3575 | 0 | 0 | 125
39029.3597 | 0 | 0 | 125
39029.3618 | 2359 | 0 | 125
39029.3639 | 2017 | 0 | 125
39029.3661 | 2194 | 0 | 125
39029.3682 | 2519 | 0 | 125
39029.3703 | 1800 | 0 | 125
39029.3725 | 2157 | 0 | 125
39029.3746 | 1548 | 0 | 125
39029.3768 | 1289 | 0 | 125
125
39029.3575 | 0 | 0 | 126
39029.3597 | 0 | 0 | 126
39029.3618 | 1989 | 0 | 126
39029.3639 | 2357 | 0 | 126
39029.3661 | 2430 | 0 | 126
39029.3682 | 2519 | 0 | 126
39029.3704 | 2447 | 0 | 126
39029.3725 | 2044 | 0 | 126
39029.3746 | 1993 | 0 | 126
39029.3768 | 2210 | 0 | 126
126
39029.3575 | 0 | 0 | 127
39029.3597 | 0 | 0 | 127
39029.3618 | 19 | 0 | 127
39029.364 | 2093 | 0 | 127
39029.3661 | 2028 | 0 | 127
39029.3682 | 2303 | 0 | 127
39029.3704 | 2155 | 0 | 127
39029.3725 | 2413 | 0 | 127
39029.3747 | 1514 | 0 | 127
39029.3768 | 2185 | 0 | 127
127
39029.3576 | 0 | 0 | 128
39029.3597 | 0 | 0 | 128
39029.3618 | 2341 | 0 | 128
39029.364 | 2393 | 0 | 128
39029.3661 | 2027 | 0 | 128
39029.3683 | 2305 | 0 | 128
39029.3704 | 1986 | 0 | 128
39029.3725 | 2210 | 0 | 128
39029.3747 | 2033 | 0 | 128
39029.3768 | 2266 | 0 | 128
128
39029.3576 | 0 | 0 | 129
39029.3597 | 0 | 0 | 129
39029.3619 | 30 | 0 | 129
39029.364 | 1981 | 0 | 129
39029.3661 | 2301 | 0 | 129
39029.3683 | 2114 | 0 | 129
39029.3704 | 1667 | 0 | 129
39029.3725 | 2310 | 0 | 129
39029.3747 | 1059 | 0 | 129
39029.3768 | 1549 | 0 | 129
129
39029.3576 | 0 | 0 | 130
39029.3597 | 0 | 0 | 130
39029.3619 | 2462 | 0 | 130
39029.364 | 2351 | 0 | 130
39029.3661 | 2509 | 0 | 130
39029.3683 | 2112 | 0 | 130
39029.3704 | 2062 | 0 | 130
39029.3726 | 2487 | 0 | 130
39029.3747 | 2382 | 0 | 130
39029.3768 | 1944 | 0 | 130
130
39029.3576 | 0 | 0 | 131
39029.3597 | 0 | 0 | 131
39029.3619 | 2312 | 0 | 131
39029.364 | 2247 | 0 | 131
39029.3662 | 2580 | 0 | 131
39029.3683 | 2331 | 0 | 131
39029.3704 | 2530 | 0 | 131
39029.3726 | 2443 | 0 | 131
39029.3747 | 2469 | 0 | 131
39029.3769 | 2275 | 0 | 131
131
39029.3576 | 0 | 0 | 132
39029.3598 | 0 | 0 | 132
39029.3619 | 1973 | 0 | 132
39029.364 | 2606 | 0 | 132
39029.3662 | 2162 | 0 | 132
39029.3683 | 2435 | 0 | 132
39029.3705 | 2261 | 0 | 132
39029.3726 | 2345 | 0 | 132
39029.3747 | 2591 | 0 | 132
39029.3769 | 2564 | 0 | 132
132

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -152 | 16.2 | 15.7 | 16.4 | 16.1 | 17
1 | -151 | 16.2 | 15.7 | 16.4 | 16.1 | 17
2 | -150 | 16.2 | 15.7 | 16.4 | 16.1 | 17
3 | -149 | 16.2 | 15.7 | 16.4 | 16.1 | 17
4 | -148 | 16.2 | 15.7 | 16.4 | 16.1 | 17
5 | -147 | 16.2 | 15.7 | 16.4 | 16.1 | 17
6 | -146 | 16.2 | 15.7 | 16.5 | 16.1 | 17
7 | -145 | 16.2 | 15.7 | 16.4 | 16.1 | 17
8 | -144 | 16.2 | 15.7 | 16.4 | 16.1 | 17
9 | -143 | 16.2 | 15.7 | 16.4 | 16.1 | 17
10 | -142 | 16.2 | 15.7 | 16.4 | 16.1 | 17
11 | -141 | 16.2 | 15.7 | 16.4 | 16.1 | 17
12 | -140 | 16.2 | 15.7 | 16.4 | 16.1 | 17
13 | -139 | 16.2 | 15.7 | 16.4 | 16.1 | 17
14 | -138 | 16.2 | 15.7 | 16.4 | 16.1 | 17
15 | -137 | 16.2 | 15.7 | 16.4 | 16.1 | 17
16 | -136 | 16.2 | 15.7 | 16.4 | 16.1 | 17
17 | -135 | 16.2 | 15.7 | 16.4 | 16.1 | 17
18 | -134 | 16.2 | 15.7 | 16.5 | 16.1 | 17
19 | -133 | 16.2 | 15.7 | 16.4 | 16.1 | 17
20 | -132 | 16.2 | 15.7 | 16.4 | 16.1 | 17
21 | -131 | 16.2 | 15.7 | 16.4 | 16.1 | 17
22 | -130 | 16.2 | 15.7 | 16.4 | 16.1 | 17
23 | -129 | 16.2 | 15.7 | 16.4 | 16.1 | 17
24 | -128 | 16.2 | 15.7 | 16.4 | 16.1 | 17
25 | -127 | 16.2 | 15.7 | 16.4 | 16.1 | 17
26 | -126 | 16.2 | 15.7 | 16.4 | 16.1 | 17
27 | -125 | 16.2 | 15.7 | 16.4 | 16.1 | 17
28 | -124 | 16.2 | 15.7 | 16.4 | 16.1 | 17
29 | -123 | 16.2 | 15.7 | 16.4 | 16.1 | 17
30 | -122 | 16.2 | 15.7 | 16.4 | 16.1 | 17
31 | -121 | 16.2 | 15.7 | 16.4 | 16.1 | 17
32 | -120 | 16.2 | 15.7 | 16.4 | 16.1 | 17
33 | -119 | 16.2 | 15.7 | 16.4 | 16.1 | 17
34 | -118 | 16.2 | 15.7 | 16.4 | 16.1 | 17
35 | -117 | 16.2 | 15.7 | 16.4 | 16.1 | 17
36 | -116 | 16.2 | 15.7 | 16.4 | 16.1 | 17
37 | -115 | 16.2 | 15.7 | 16.4 | 16.1 | 17
38 | -114 | 16.2 | 15.7 | 16.4 | 16.1 | 17
39 | -113 | 16.2 | 15.7 | 16.4 | 16.1 | 17
40 | -112 | 16.2 | 15.7 | 16.4 | 16.1 | 17
41 | -111 | 16.2 | 15.7 | 16.4 | 16.1 | 17
42 | -110 | 16.2 | 15.7 | 16.4 | 16.1 | 17
43 | -109 | 16.2 | 15.7 | 16.4 | 16.1 | 17
44 | -108 | 16.2 | 15.7 | 16.4 | 16.1 | 17
45 | -107 | 16.2 | 15.7 | 16.4 | 16.1 | 17
46 | -106 | 16.2 | 15.7 | 16.4 | 16.1 | 17
47 | -105 | 16.2 | 15.7 | 16.4 | 16.1 | 17
48 | -104 | 16.2 | 15.7 | 16.4 | 16.1 | 17
49 | -103 | 16.2 | 15.7 | 16.4 | 16.1 | 17
50 | -102 | 16.2 | 15.7 | 16.4 | 16.1 | 17
51 | -101 | 16.2 | 15.7 | 16.4 | 16.1 | 17
52 | -100 | 16.2 | 15.7 | 16.4 | 16.1 | 17
53 | -99 | 16.2 | 15.7 | 16.4 | 16.1 | 17
54 | -98 | 16.2 | 15.7 | 16.4 | 16.1 | 17
55 | -97 | 16.2 | 15.7 | 16.4 | 16.1 | 17
56 | -96 | 16.2 | 15.7 | 16.4 | 16.1 | 17
57 | -95 | 16.2 | 15.7 | 16.4 | 16.1 | 17
58 | -94 | 16.2 | 15.7 | 16.4 | 16.1 | 17
59 | -93 | 16.2 | 15.7 | 16.4 | 16.1 | 17
60 | -92 | 16.2 | 15.7 | 16.4 | 16.1 | 17
61 | -91 | 16.2 | 15.7 | 16.4 | 16.1 | 17
62 | -90 | 16.2 | 15.7 | 16.4 | 16.1 | 17
63 | -89 | 16.2 | 15.7 | 16.4 | 16.1 | 17
64 | -88 | 16.2 | 15.7 | 16.4 | 16.1 | 17
65 | -87 | 16.2 | 15.7 | 16.4 | 16.1 | 17
66 | -86 | 16.2 | 15.7 | 16.4 | 16.1 | 17
67 | -85 | 16.2 | 15.7 | 16.4 | 16.1 | 17
68 | -84 | 16.2 | 15.7 | 16.4 | 16.1 | 17
69 | -83 | 16.2 | 15.7 | 16.4 | 16.1 | 17
70 | -82 | 16.2 | 15.7 | 16.4 | 16.1 | 17
71 | -81 | 16.2 | 15.7 | 16.4 | 16.1 | 17
72 | -80 | 16.2 | 15.7 | 16.4 | 16.1 | 17
73 | -79 | 16.2 | 15.7 | 16.4 | 16.1 | 17
74 | -78 | 16.2 | 15.7 | 16.4 | 16.1 | 17
75 | -77 | 16.2 | 15.6 | 16.4 | 16.1 | 17
76 | -76 | 16.2 | 15.7 | 16.4 | 16.1 | 17
77 | -75 | 16.2 | 15.7 | 16.4 | 16.1 | 17
78 | -74 | 16.2 | 15.6 | 16.4 | 16.1 | 17
79 | -73 | 16.2 | 15.6 | 16.4 | 16.1 | 17
80 | -72 | 16.2 | 15.6 | 16.4 | 16.1 | 17
81 | -71 | 16.2 | 15.6 | 16.4 | 16.1 | 17
82 | -70 | 16.2 | 15.6 | 16.4 | 16.1 | 17
83 | -69 | 16.2 | 15.6 | 16.4 | 16.1 | 17
84 | -68 | 16.2 | 15.6 | 16.4 | 16.1 | 17
85 | -67 | 16.2 | 15.6 | 16.4 | 16.1 | 17
86 | -66 | 16.2 | 15.6 | 16.4 | 16.1 | 17
87 | -65 | 16.2 | 15.6 | 16.4 | 16.1 | 17
88 | -64 | 16.2 | 15.6 | 16.4 | 16.1 | 17
89 | -63 | 16.2 | 15.6 | 16.4 | 16.1 | 17
90 | -62 | 16.2 | 15.6 | 16.4 | 16.1 | 17
91 | -61 | 16.2 | 15.6 | 16.4 | 16.1 | 17
92 | -60 | 16.2 | 15.6 | 16.5 | 16.1 | 17
93 | -59 | 16.2 | 15.6 | 16.4 | 16.1 | 17
94 | -58 | 16.2 | 15.6 | 16.5 | 16.1 | 17
95 | -57 | 16.2 | 15.6 | 16.5 | 16.1 | 17
96 | -56 | 16.2 | 15.6 | 16.4 | 16.1 | 17
97 | -55 | 16.2 | 15.6 | 16.5 | 16.1 | 17
98 | -54 | 16.2 | 15.6 | 16.4 | 16.1 | 17
99 | -53 | 16.2 | 15.6 | 16.4 | 16.1 | 17
100 | -52 | 16.2 | 15.6 | 16.4 | 16.1 | 17
101 | -51 | 16.2 | 15.6 | 16.4 | 16.1 | 17
102 | -50 | 16.2 | 15.6 | 16.4 | 16.1 | 17
103 | -49 | 16.2 | 15.6 | 16.5 | 16.1 | 17
104 | -48 | 16.2 | 15.6 | 16.4 | 16.1 | 17
105 | -47 | 16.2 | 15.6 | 16.5 | 16.1 | 17
106 | -46 | 16.2 | 15.6 | 16.5 | 16.1 | 17
107 | -45 | 16.2 | 15.6 | 16.4 | 16.1 | 17
108 | -44 | 16.2 | 15.6 | 16.5 | 16.1 | 17
109 | -43 | 16.2 | 15.6 | 16.5 | 16.1 | 17
110 | -42 | 16.2 | 15.6 | 16.5 | 16.1 | 17
111 | -41 | 16.2 | 15.6 | 16.5 | 16.1 | 17
112 | -40 | 16.2 | 15.6 | 16.5 | 16.1 | 17
113 | -39 | 16.2 | 15.6 | 16.5 | 16.1 | 17
114 | -38 | 16.2 | 15.7 | 16.5 | 16.1 | 17
115 | -37 | 16.2 | 15.7 | 16.5 | 16.1 | 17
116 | -36 | 16.2 | 15.7 | 16.5 | 16.1 | 17
117 | -35 | 16.2 | 15.7 | 16.5 | 16.1 | 17
118 | -34 | 16.2 | 15.7 | 16.5 | 16.1 | 17
119 | -33 | 16.2 | 15.7 | 16.4 | 16.1 | 17
120 | -32 | 16.2 | 15.7 | 16.5 | 16.1 | 17
121 | -31 | 16.2 | 15.7 | 16.5 | 16.1 | 17
122 | -30 | 16.2 | 15.7 | 16.5 | 16.1 | 17
123 | -29 | 16.2 | 15.7 | 16.5 | 16.1 | 17
124 | -28 | 16.2 | 15.7 | 16.5 | 16.1 | 17
125 | -27 | 16.2 | 15.7 | 16.5 | 16.1 | 17
126 | -26 | 16.2 | 15.7 | 16.5 | 16.1 | 17
127 | -25 | 16.2 | 15.7 | 16.5 | 16.1 | 17
128 | -24 | 16.2 | 15.7 | 16.5 | 16.1 | 17
129 | -23 | 16.2 | 15.7 | 16.5 | 16.1 | 17
130 | -22 | 16.2 | 15.7 | 16.5 | 16.1 | 17
131 | -21 | 16.2 | 15.6 | 16.5 | 16.1 | 17
132 | -20 | 16.2 | 15.7 | 16.5 | 16.1 | 17
133 | -19 | 16.2 | 15.6 | 16.5 | 16.1 | 17
134 | -18 | 16.2 | 15.7 | 16.4 | 16.1 | 17
135 | -17 | 16.2 | 15.7 | 16.5 | 16.1 | 17
136 | -16 | 16.2 | 15.7 | 16.5 | 16.1 | 17
137 | -15 | 16.2 | 15.7 | 16.5 | 16.1 | 17
138 | -14 | 16.2 | 15.7 | 16.5 | 16.1 | 17
139 | -13 | 16.2 | 15.7 | 16.5 | 16.1 | 17
140 | -12 | 16.2 | 15.7 | 16.5 | 16.1 | 17
141 | -11 | 16.2 | 15.7 | 16.5 | 16.1 | 17
142 | -10 | 16.2 | 15.7 | 16.5 | 16.1 | 17
143 | -9 | 16.2 | 15.7 | 16.5 | 16.1 | 17
144 | -8 | 16.2 | 15.7 | 16.4 | 16.1 | 17
145 | -7 | 16.2 | 15.7 | 16.5 | 16.1 | 17
146 | -6 | 16.2 | 15.7 | 16.4 | 16.1 | 17
147 | -5 | 16.1 | 15.7 | 16.4 | 16.1 | 17
148 | -4 | 16.2 | 15.7 | 16.5 | 16.1 | 17
149 | -3 | 16.2 | 15.7 | 16.5 | 16.1 | 17
150 | -2 | 16.2 | 15.7 | 16.5 | 16.1 | 17
151 | -1 | 16.2 | 15.7 | 16.5 | 16.1 | 17
152 | 0 | 16.2 | 15.7 | 16.5 | 16.1 | 17
153 | 1 | 16.2 | 15.7 | 16.4 | 16.1 | 17
154 | 2 | 16.2 | 15.7 | 16.5 | 16.1 | 17
155 | 3 | 16.2 | 15.7 | 16.5 | 16.1 | 17
156 | 4 | 16.2 | 15.7 | 16.5 | 16.1 | 17
157 | 5 | 16.2 | 15.7 | 17 | 16.1 | 17
158 | 6 | 16.2 | 17 | 21.7 | 16.1 | 17.7
159 | 7 | 16.2 | 21.3 | 31.9 | 16.2 | 19
160 | 8 | 16.2 | 29.7 | 47 | 16.5 | 21.4
161 | 9 | 16.2 | 38.4 | 62 | 17 | 23.9
162 | 10 | 16.2 | 48.8 | 84.5 | 17.7 | 27.3
163 | 11 | 16.2 | 56.2 | 96 | 18.1 | 28.8
164 | 12 | 16.2 | 64.1 | 108.9 | 18.7 | 31.4
165 | 13 | 16.3 | 76.4 | 143.2 | 19.4 | 37.1
166 | 14 | 16.3 | 88.9 | 165.4 | 20.2 | 41
167 | 15 | 16.4 | 104.7 | 192.4 | 20.9 | 47
168 | 16 | 16.5 | 115.4 | 206.5 | 21.7 | 51.5
169 | 17 | 16.5 | 130.3 | 244.7 | 22.5 | 56.6
170 | 18 | 16.7 | 152.2 | 291.2 | 23.7 | 63.8
171 | 19 | 16.8 | 171.8 | 327.5 | 25.1 | 71.3
172 | 20 | 16.9 | 196.9 | 364 | 26.5 | 80.4
173 | 21 | 17.1 | 219.5 | 409.2 | 28.2 | 88.8
174 | 22 | 17.3 | 243.5 | 445.2 | 30.3 | 98.1
175 | 23 | 17.5 | 258.8 | 456.6 | 31.5 | 103.8
176 | 24 | 17.7 | 273.7 | 480.4 | 31.6 | 111.8
177 | 25 | 18.1 | 288 | 484.4 | 32 | 119.4
178 | 26 | 18.4 | 304.8 | 510.9 | 33 | 127.3
179 | 27 | 18.8 | 314 | 517 | 33.2 | 133.9
180 | 28 | 19.3 | 318.8 | 511.5 | 33.7 | 138
181 | 29 | 19.7 | 330.4 | 528.9 | 34.1 | 147
182 | 30 | 20.2 | 335.5 | 531.5 | 34.6 | 152
183 | 31 | 20.7 | 345 | 554.1 | 35.2 | 159
184 | 32 | 21.2 | 348 | 557.1 | 36.6 | 165.5
185 | 33 | 21.8 | 349.9 | 547.2 | 37.7 | 168
186 | 34 | 22.3 | 350.7 | 542 | 38.9 | 171.1
187 | 35 | 22.9 | 354.9 | 533.8 | 39.9 | 174.8
188 | 36 | 23.5 | 357.5 | 548.7 | 40.6 | 179
189 | 37 | 24.1 | 359.4 | 538.6 | 42.3 | 181.7
190 | 38 | 24.8 | 356.2 | 529.3 | 42.8 | 183.7
191 | 39 | 25.5 | 353.3 | 516.8 | 44 | 185.4
192 | 40 | 26.2 | 353.5 | 513.6 | 45.6 | 189.7
193 | 41 | 27 | 352.4 | 503.7 | 46.5 | 191.4
194 | 42 | 27.7 | 350.6 | 505 | 47.3 | 194.4
195 | 43 | 28.5 | 347.2 | 493.1 | 48.7 | 196.7
196 | 44 | 29.2 | 341.1 | 477 | 49.2 | 196.1
197 | 45 | 30 | 338.3 | 474.2 | 49.8 | 197.5
198 | 46 | 30.8 | 336.5 | 475 | 51 | 199.4
199 | 47 | 31.7 | 341.4 | 494.3 | 51.8 | 205.4
200 | 48 | 32.5 | 348.3 | 505 | 53 | 210.8
201 | 49 | 33.3 | 350 | 505.5 | 53.9 | 214.8
202 | 50 | 34.2 | 352.9 | 513.9 | 55 | 219.1
203 | 51 | 35.1 | 351.8 | 506.7 | 56.1 | 220.4
204 | 52 | 36 | 345.8 | 488.2 | 57.2 | 220.6
205 | 53 | 36.9 | 347 | 497.6 | 58.9 | 223.5
206 | 54 | 37.9 | 355.7 | 521.6 | 60.3 | 229.8
207 | 55 | 38.9 | 357.9 | 511.5 | 61.1 | 232.3
208 | 56 | 39.9 | 352.5 | 490.2 | 61.7 | 231.4
209 | 57 | 40.9 | 347.4 | 480.7 | 62.5 | 231.5
210 | 58 | 41.9 | 343.7 | 474.7 | 63.7 | 232.3
211 | 59 | 43 | 341.4 | 474.1 | 65 | 233.5
212 | 60 | 44 | 338 | 474.1 | 65.3 | 234.8
213 | 61 | 45 | 346.7 | 502.6 | 66.5 | 239.5
214 | 62 | 46.1 | 350.3 | 506.2 | 67.5 | 243.5
215 | 63 | 47.1 | 352.4 | 512 | 68.1 | 245.5
216 | 64 | 48.1 | 359.3 | 536.9 | 69 | 251.6
217 | 65 | 49.1 | 358 | 525 | 70.6 | 253.5
218 | 66 | 50.1 | 356.9 | 518.8 | 73.3 | 255.1
219 | 67 | 51.2 | 359 | 531.9 | 74.3 | 257.5
220 | 68 | 52.2 | 367.1 | 548.1 | 75.1 | 263.4
221 | 69 | 53.3 | 372.4 | 557.1 | 77.1 | 266.7
222 | 70 | 54.3 | 380.3 | 575.3 | 78.9 | 270.6
223 | 71 | 55.4 | 387.1 | 574.9 | 80.9 | 275.8
224 | 72 | 56.5 | 388.8 | 584.8 | 83.5 | 279.8
225 | 73 | 57.5 | 388.2 | 575.6 | 85.7 | 283
226 | 74 | 58.6 | 391 | 582.9 | 87.6 | 287.2
227 | 75 | 59.7 | 389.2 | 587.3 | 89.7 | 289.1
228 | 76 | 60.9 | 396.3 | 605.2 | 91.6 | 295.6
229 | 77 | 62 | 394.1 | 603.1 | 93.6 | 298.5
230 | 78 | 63.1 | 391.1 | 593.7 | 96.4 | 300.5
231 | 79 | 64.3 | 388.4 | 581.2 | 98.1 | 301.7
232 | 80 | 65.5 | 386.4 | 584.1 | 99.9 | 303.2
233 | 81 | 66.7 | 387.7 | 584.7 | 101.5 | 305.5
234 | 82 | 67.8 | 391.7 | 595.8 | 104.5 | 309.2
235 | 83 | 69 | 396.4 | 598.8 | 107.1 | 313
236 | 84 | 70 | 396.8 | 601.5 | 108.8 | 315.4
237 | 85 | 71.1 | 403.9 | 615.9 | 111.2 | 321.2
238 | 86 | 72.2 | 410.3 | 630.8 | 114.2 | 327.6
239 | 87 | 73.2 | 410.1 | 631.8 | 117 | 330.6
240 | 88 | 74.2 | 413.4 | 640 | 120.3 | 335.5
241 | 89 | 75.2 | 417.8 | 655.3 | 124.1 | 341.3
242 | 90 | 76.3 | 418.8 | 648.5 | 129.1 | 343.7
243 | 91 | 77.4 | 420.5 | 653.5 | 132.9 | 347.5
244 | 92 | 78.5 | 421.5 | 652.3 | 135.8 | 352
245 | 93 | 79.6 | 430.4 | 677.1 | 140.4 | 359.3
246 | 94 | 80.7 | 438 | 704.2 | 146.3 | 367.4
247 | 95 | 81.8 | 446.2 | 720.3 | 152.1 | 374.9
248 | 96 | 82.8 | 449.7 | 730.2 | 157.2 | 379.3
249 | 97 | 83.9 | 458.9 | 740.9 | 161.3 | 387.8
250 | 98 | 85 | 466.6 | 749 | 166.7 | 395.9
251 | 99 | 86.3 | 471.8 | 749.3 | 173.3 | 403.1
252 | 100 | 87.6 | 482 | 759.7 | 176.4 | 414.7
253 | 101 | 88.9 | 490.1 | 761.6 | 178.5 | 421.3
254 | 102 | 90.3 | 490.7 | 745.9 | 180.7 | 424.4
255 | 103 | 91.7 | 485.3 | 738.6 | 181.5 | 425
256 | 104 | 93.2 | 480.2 | 743.5 | 182.8 | 425.5
257 | 105 | 94.8 | 479.7 | 746.1 | 186.4 | 429.4
258 | 106 | 96.4 | 477.2 | 742.6 | 188.1 | 431.3
259 | 107 | 98 | 474.2 | 742.3 | 191.2 | 433.4
260 | 108 | 99.7 | 472.4 | 744.9 | 195.2 | 436.3
261 | 109 | 101.5 | 473.9 | 755.9 | 199.6 | 440.3
262 | 110 | 103.2 | 476.5 | 761.1 | 203 | 444.6
263 | 111 | 105 | 471.4 | 750.3 | 205.8 | 445.2
264 | 112 | 106.9 | 469.3 | 748 | 210.4 | 447
265 | 113 | 108.8 | 470.1 | 753.5 | 215.3 | 452.1
266 | 114 | 110.6 | 468.9 | 755.7 | 220 | 454.8
267 | 115 | 112.5 | 470.2 | 751.6 | 225.2 | 457
268 | 116 | 114.4 | 466.1 | 740.7 | 227.2 | 457.9
269 | 117 | 116.3 | 466.4 | 743.2 | 229.7 | 460.2
270 | 118 | 118.3 | 467.4 | 741.8 | 230.9 | 462.2
271 | 119 | 120.3 | 466.2 | 735.6 | 231.7 | 465.1
272 | 120 | 122.3 | 464.9 | 728.5 | 233.6 | 467.4
273 | 121 | 124.3 | 461.8 | 719.2 | 234.7 | 467.8
274 | 122 | 126.3 | 463.2 | 722.2 | 237.6 | 471.5
275 | 123 | 128.3 | 466.2 | 734.2 | 241.4 | 475.5
276 | 124 | 130.1 | 466.9 | 736.6 | 245.2 | 480
277 | 125 | 131.9 | 469.8 | 740.1 | 247.9 | 483.2
278 | 126 | 133.7 | 476.7 | 745.8 | 251.9 | 489.7
279 | 127 | 135.4 | 475.3 | 743.6 | 252.6 | 490.3
280 | 128 | 137 | 469 | 727.6 | 249.9 | 488.9
281 | 129 | 138.7 | 461.9 | 710.5 | 247.6 | 487.8
282 | 130 | 140.2 | 457.4 | 707.8 | 246.4 | 487.2
283 | 131 | 141.8 | 455.5 | 714.8 | 246.5 | 489.8
284 | 132 | 143.4 | 451.9 | 706.3 | 245.4 | 488.6
285 | 133 | 145 | 449.4 | 705.7 | 245.3 | 489.5
286 | 134 | 146.5 | 451.6 | 700.5 | 246 | 490.1
287 | 135 | 147.9 | 452 | 697.4 | 247.8 | 491.9
288 | 136 | 149.4 | 455 | 696.3 | 249 | 493.5
289 | 137 | 150.8 | 459.1 | 694.7 | 251.6 | 497.1
290 | 138 | 152.2 | 458.1 | 693 | 253 | 496.4
291 | 139 | 153.6 | 453.8 | 681.2 | 253.2 | 495.7
292 | 140 | 155.1 | 455.6 | 688.1 | 254.3 | 498.2
293 | 141 | 156.5 | 456.8 | 694.6 | 254.5 | 499.6
294 | 142 | 157.9 | 457.5 | 693.3 | 255.2 | 501.4
295 | 143 | 159.2 | 457.1 | 686.4 | 255.9 | 503.2
296 | 144 | 160.5 | 459.4 | 688.8 | 256.4 | 505.2
297 | 145 | 161.8 | 458.7 | 698.6 | 256.6 | 506.2
298 | 146 | 163.2 | 460.8 | 696.1 | 258.5 | 509.7
299 | 147 | 164.5 | 461.7 | 688.8 | 260.2 | 510.9
300 | 148 | 165.8 | 465.8 | 698.5 | 262.1 | 514.9
301 | 149 | 167.2 | 478.2 | 696.7 | 265.2 | 521.2
302 | 150 | 168.5 | 483.9 | 695.6 | 268.5 | 523.1
303 | 151 | 169.9 | 487.5 | 681.2 | 270.6 | 525.7
304 | 152 | 171.2 | 488.8 | 675.2 | 272.2 | 525.9
305 | 153 | 172.6 | 494.3 | 690.6 | 274.8 | 529.7
306 | 154 | 173.9 | 497.2 | 701.5 | 278.1 | 532.4
307 | 155 | 175.3 | 496 | 710 | 280.3 | 533.9
308 | 156 | 176.7 | 498.7 | 724.2 | 282.8 | 537.6
309 | 157 | 178.1 | 500.2 | 725 | 285.1 | 540
310 | 158 | 179.4 | 501.5 | 725.7 | 287.2 | 541.6
311 | 159 | 180.6 | 499 | 722.1 | 288.6 | 540.8
312 | 160 | 181.8 | 495.1 | 717.1 | 288.9 | 540
313 | 161 | 183 | 491.2 | 710.7 | 289.3 | 540.7
314 | 162 | 184.1 | 488.9 | 709.3 | 290.6 | 539.8
315 | 163 | 185.3 | 487.7 | 714.7 | 292.1 | 542
316 | 164 | 186.4 | 482.4 | 701.3 | 292.7 | 540.4
317 | 165 | 187.4 | 481.9 | 700.2 | 294.7 | 540.7
318 | 166 | 188.5 | 491.1 | 710.5 | 299.4 | 545.7
319 | 167 | 189.3 | 498.6 | 717.4 | 303.7 | 549.4
320 | 168 | 190.3 | 499.2 | 708.4 | 306.1 | 549.1
321 | 169 | 191.5 | 500.1 | 702.9 | 308.8 | 549.1
322 | 170 | 192.8 | 502.4 | 715.4 | 312.2 | 551.6
323 | 171 | 194.3 | 508.5 | 724.3 | 315.9 | 557
324 | 172 | 195.9 | 509.8 | 716.6 | 318.3 | 558.1
325 | 173 | 197.4 | 506.5 | 722.8 | 320.7 | 558
326 | 174 | 198.9 | 503.6 | 717.6 | 323.2 | 558.1
327 | 175 | 200.1 | 501.2 | 713.5 | 325.8 | 557.4
328 | 176 | 201.2 | 504 | 720.9 | 329.5 | 560.4
329 | 177 | 202.3 | 507.5 | 740.3 | 334.1 | 566
330 | 178 | 203.2 | 506.8 | 744.2 | 337.1 | 567.8
331 | 179 | 204.2 | 509.7 | 752.7 | 340.2 | 571.3
332 | 180 | 205.3 | 510.7 | 746.6 | 342.8 | 573.5
333 | 181 | 206.3 | 511.9 | 753.7 | 346.2 | 575
334 | 182 | 207.3 | 509.8 | 754.3 | 349.1 | 576.4
335 | 183 | 208.4 | 513.1 | 765 | 353.8 | 579.8
336 | 184 | 209.4 | 511.8 | 752.3 | 355.2 | 580.2
337 | 185 | 210.3 | 507.1 | 750.1 | 358.4 | 580.2
338 | 186 | 211.3 | 502.8 | 748.1 | 361.2 | 580.7
339 | 187 | 212.3 | 499.6 | 748.6 | 364.3 | 580.4
340 | 188 | 213.5 | 500.8 | 746.6 | 368 | 580.1
341 | 189 | 214.7 | 497.9 | 743.7 | 370.2 | 580.1
342 | 190 | 216 | 497.6 | 738 | 374.4 | 579.5
343 | 191 | 217.3 | 496.2 | 740.7 | 377.1 | 579
344 | 192 | 218.6 | 494.2 | 750.7 | 379 | 579.1
345 | 193 | 219.9 | 492 | 746.5 | 379.9 | 579.4
346 | 194 | 221.2 | 491 | 751.5 | 382.8 | 579.9
347 | 195 | 222.5 | 487.7 | 743.5 | 384.2 | 579.8
348 | 196 | 223.7 | 487.9 | 740.9 | 387.6 | 579.6
349 | 197 | 224.9 | 487 | 741.5 | 389.3 | 578.8
350 | 198 | 226.1 | 481.9 | 732.7 | 388.4 | 577.3
351 | 199 | 227.3 | 479.4 | 730 | 388.8 | 576.5
352 | 200 | 228.6 | 479.3 | 734.2 | 390.8 | 576.5
353 | 201 | 229.8 | 482.7 | 739.5 | 393.4 | 578.7
354 | 202 | 231.1 | 483.6 | 739.6 | 395.8 | 579.5
355 | 203 | 232.4 | 482.4 | 733.1 | 397.1 | 578.6
356 | 204 | 233.6 | 479.6 | 740.7 | 399.5 | 580.2
357 | 205 | 234.8 | 481.8 | 745.4 | 403.3 | 580.9
358 | 206 | 236 | 478.9 | 741.1 | 404.5 | 579.7
359 | 207 | 237.2 | 475.5 | 723.9 | 404.3 | 579.1
360 | 208 | 238.2 | 476 | 727.1 | 407.4 | 579.4
361 | 209 | 239.3 | 480.2 | 744.7 | 411.4 | 582.6
362 | 210 | 240.4 | 487.6 | 754.3 | 416.5 | 586.3
363 | 211 | 241.4 | 489.5 | 756.5 | 417.9 | 587.5
364 | 212 | 242.3 | 488.6 | 751.1 | 418 | 589.1
365 | 213 | 243.2 | 488.3 | 760.2 | 420.5 | 591.1
366 | 214 | 244.2 | 490.7 | 757.6 | 421.7 | 591.5
367 | 215 | 245.1 | 490.7 | 754.1 | 422.9 | 592.7
368 | 216 | 246.1 | 494.8 | 762.1 | 427.7 | 596.5
369 | 217 | 247 | 494 | 765.1 | 427.6 | 596.1
370 | 218 | 247.8 | 492.8 | 765.5 | 428.1 | 596.6
371 | 219 | 248.6 | 493.1 | 764.4 | 429.2 | 598.3
372 | 220 | 249.4 | 493.1 | 764.6 | 430.4 | 599.3
373 | 221 | 250.2 | 494.5 | 771.6 | 431.9 | 601.4
374 | 222 | 251.1 | 497.6 | 766.3 | 431.6 | 602.9
375 | 223 | 252 | 497.8 | 760.4 | 429.8 | 604
376 | 224 | 253 | 497.1 | 761.3 | 428.8 | 605.5
377 | 225 | 254 | 497.3 | 761.3 | 427.9 | 605
378 | 226 | 255.1 | 499.4 | 760.9 | 427.9 | 605.6
379 | 227 | 256.2 | 497.2 | 759.4 | 428 | 608.1
380 | 228 | 257.2 | 498.4 | 755.1 | 427.6 | 609.4
381 | 229 | 258.3 | 501.5 | 758.2 | 428.8 | 610.5
382 | 230 | 259.3 | 503.9 | 761.5 | 428.2 | 612.3
383 | 231 | 260.4 | 507.5 | 767.7 | 428.8 | 613.4
384 | 232 | 261.5 | 508.6 | 771.5 | 429.1 | 614.6
385 | 233 | 262.7 | 509.1 | 766.7 | 428.8 | 614.1
386 | 234 | 263.9 | 511 | 772.5 | 429.8 | 616.1
387 | 235 | 265.2 | 514.8 | 777.1 | 431.6 | 618.9
388 | 236 | 266.5 | 515.5 | 776.2 | 432.3 | 619
389 | 237 | 267.8 | 514.8 | 772.2 | 432.6 | 618.5
390 | 238 | 269 | 517.5 | 773.8 | 433.7 | 620.3
391 | 239 | 270.1 | 521.3 | 778.9 | 436 | 623.2
392 | 240 | 271.2 | 524.5 | 777.1 | 437.8 | 624
393 | 241 | 272.3 | 528.3 | 774.6 | 440.1 | 625.9
394 | 242 | 273.4 | 532.3 | 782.4 | 442.4 | 628.4
395 | 243 | 274.5 | 533.8 | 783.2 | 444.3 | 630.6
396 | 244 | 275.6 | 532.1 | 782 | 446.3 | 630.7
397 | 245 | 276.7 | 529.7 | 775.3 | 447.5 | 630.2
398 | 246 | 277.9 | 528.2 | 781.6 | 449.4 | 631.8
399 | 247 | 279.2 | 524.4 | 779.6 | 451.1 | 632.4
400 | 248 | 280.3 | 524.2 | 784.6 | 453.8 | 635.5
401 | 249 | 281.3 | 528.9 | 784.5 | 456.6 | 637.8
402 | 250 | 282.3 | 531.4 | 786.6 | 459 | 639.1
403 | 251 | 283.3 | 541.4 | 778.5 | 462.3 | 641.6
404 | 252 | 284.3 | 553.5 | 770.4 | 465.1 | 645.1
405 | 253 | 285.4 | 555.8 | 770.9 | 467 | 646
406 | 254 | 286.7 | 550.9 | 759.3 | 467.9 | 645.7
407 | 255 | 288 | 547.2 | 756.9 | 469 | 646.5
408 | 256 | 289.4 | 546.3 | 765 | 471.3 | 648.1
409 | 257 | 290.9 | 541.5 | 766.1 | 472.5 | 647.8
410 | 258 | 292.3 | 537.4 | 770.9 | 473.9 | 647.9
411 | 259 | 293.7 | 533.6 | 771.1 | 475.4 | 647.2
412 | 260 | 295.4 | 530 | 773.4 | 475.8 | 646.8
413 | 261 | 296.9 | 527.1 | 769.6 | 476.5 | 646.4
414 | 262 | 298.4 | 522.9 | 766.9 | 476.7 | 645.9
415 | 263 | 299.7 | 517.4 | 772.2 | 476.9 | 644.7
416 | 264 | 301.1 | 516.9 | 780.6 | 478.5 | 646.3
417 | 265 | 302.5 | 516.3 | 781.9 | 479.7 | 645.8
418 | 266 | 303.8 | 513.6 | 771 | 479.5 | 644.7
419 | 267 | 305.1 | 511.2 | 759.7 | 478.6 | 643.5
420 | 268 | 306.5 | 510 | 766.3 | 478.9 | 643.9
421 | 269 | 307.9 | 509.9 | 760.5 | 479.3 | 644
422 | 270 | 309.4 | 512.3 | 759.4 | 480.4 | 647.2
423 | 271 | 311 | 514.8 | 772.5 | 482.5 | 649.2
424 | 272 | 312.7 | 514.8 | 783 | 484.3 | 650.8
425 | 273 | 314.3 | 512.3 | 783.5 | 485.4 | 651
426 | 274 | 315.9 | 511.8 | 780.9 | 486.5 | 650.3
427 | 275 | 317.6 | 512.3 | 781.8 | 488 | 650.4
428 | 276 | 319.3 | 514 | 784.7 | 489.6 | 651.2
429 | 277 | 321.1 | 515.6 | 773.7 | 490 | 652.1
430 | 278 | 322.9 | 517.6 | 770.7 | 491.2 | 653.1
431 | 279 | 324.7 | 519.1 | 779.4 | 493.2 | 653.7
432 | 280 | 326.6 | 515 | 776.1 | 494.4 | 653.1
433 | 281 | 328.5 | 512.9 | 769 | 495.6 | 652.1
434 | 282 | 330.5 | 511.1 | 761.8 | 497.5 | 652.2
435 | 283 | 332.6 | 512.3 | 769.6 | 500 | 653.3
436 | 284 | 334.8 | 514.7 | 783.9 | 503.3 | 655.7
437 | 285 | 337 | 516.2 | 779.4 | 505.3 | 655.5
438 | 286 | 339.3 | 512 | 776.7 | 505.6 | 654.9
439 | 287 | 341.5 | 509.4 | 781.3 | 506.8 | 654.6
440 | 288 | 343.8 | 509 | 777 | 507.2 | 652.6
441 | 289 | 346 | 506.7 | 772.3 | 508 | 651.1
442 | 290 | 348.2 | 502 | 764.1 | 508.5 | 649.5
443 | 291 | 350.4 | 501.4 | 756.2 | 508.7 | 648.5
444 | 292 | 352.7 | 500.7 | 759.5 | 509.3 | 648.2
445 | 293 | 354.9 | 501.9 | 771.8 | 510.9 | 649.7
446 | 294 | 357.2 | 501.7 | 767.3 | 512.1 | 648.4
447 | 295 | 359.5 | 500.6 | 766.2 | 513.2 | 647.9
448 | 296 | 361.8 | 499 | 773 | 514.4 | 647.9
449 | 297 | 364.2 | 498.3 | 775.4 | 515.7 | 647.7
450 | 298 | 366.6 | 497.5 | 776.1 | 516.7 | 648.3
451 | 299 | 368.9 | 498.6 | 767 | 517.6 | 647.3
452 | 300 | 371.1 | 497.4 | 760.6 | 517.7 | 646
453 | 301 | 373.3 | 500.5 | 762.7 | 519 | 646.6
454 | 302 | 375.6 | 502.3 | 765 | 519.9 | 646.7
455 | 303 | 377.8 | 504.2 | 770.8 | 521.2 | 647.3
456 | 304 | 380 | 507.4 | 772.2 | 522.5 | 650.1
457 | 305 | 382.3 | 508.4 | 758.5 | 523.2 | 650.2
458 | 306 | 384.4 | 510 | 746.6 | 523.6 | 648.3
459 | 307 | 386.5 | 514.8 | 750.9 | 524.7 | 650.5
460 | 308 | 388.4 | 524.1 | 745.3 | 525.3 | 652.5
461 | 309 | 390.3 | 527.8 | 730.9 | 526.5 | 653.3
462 | 310 | 392.2 | 534.3 | 738.5 | 528.3 | 656.2
463 | 311 | 394.3 | 535.4 | 742.5 | 529.6 | 656.6
464 | 312 | 396.6 | 534.8 | 747.5 | 530.9 | 658.7
465 | 313 | 399 | 541.1 | 744.1 | 532.6 | 659.6
466 | 314 | 401.4 | 543.8 | 749.9 | 534.8 | 661.2
467 | 315 | 403.8 | 545.2 | 762.7 | 536.8 | 663.3
468 | 316 | 406.2 | 549.1 | 761.4 | 538.3 | 665.7
469 | 317 | 406.7 | 548 | 759.9 | 539.6 | 665
470 | 318 | 411.2 | 546.1 | 763.3 | 541.6 | 666.8
471 | 319 | 414.6 | 548.6 | 765.4 | 543.3 | 668
472 | 320 | 419.1 | 552.7 | 763.1 | 545.2 | 668.7
473 | 321 | 424.4 | 556.9 | 756.4 | 547.2 | 669.8
474 | 322 | 429.8 | 560 | 763.4 | 549 | 672.6
475 | 323 | 435 | 558 | 773.2 | 550.5 | 673.2
476 | 324 | 439.9 | 557.9 | 772.7 | 552 | 671.6
477 | 325 | 444.8 | 556 | 764.5 | 553 | 670.6
478 | 326 | 449.4 | 552.5 | 761.2 | 554 | 669.9
479 | 327 | 453.9 | 552.1 | 760.6 | 555 | 671.5
480 | 328 | 458.1 | 561.8 | 731.3 | 556.3 | 671.8
481 | 329 | 462.1 | 566.6 | 722.8 | 558.3 | 669.9
482 | 330 | 466.1 | 569 | 711.2 | 560.1 | 669.9
483 | 331 | 470.1 | 571.9 | 709.4 | 562.3 | 669.9
484 | 332 | 474.1 | 573.5 | 690.9 | 564 | 668.9
485 | 333 | 478.3 | 568 | 681.3 | 565.3 | 666
486 | 334 | 482.5 | 561.7 | 678.4 | 566.3 | 664.4
487 | 335 | 486.5 | 556.6 | 689.5 | 566.7 | 664.5
488 | 336 | 489.8 | 561.4 | 673.9 | 567.2 | 663.1
489 | 337 | 493.8 | 566.1 | 678.8 | 567.9 | 662.9
490 | 338 | 497.7 | 570.1 | 702 | 568.7 | 663.8
491 | 339 | 501.2 | 569.5 | 715.7 | 569.3 | 663.9
492 | 340 | 504.7 | 569.8 | 722.3 | 569.8 | 662.6
493 | 341 | 508.1 | 568.6 | 735.1 | 570.3 | 663.3
494 | 342 | 511.7 | 567.1 | 720.7 | 571 | 661.9
495 | 343 | 515.5 | 566.4 | 720.6 | 571.9 | 662.9
496 | 344 | 519.6 | 565.8 | 733.8 | 573.2 | 663.7
497 | 345 | 524 | 567.5 | 729.1 | 574.4 | 664
498 | 346 | 528.3 | 567 | 716.2 | 574.3 | 663
499 | 347 | 533 | 564.7 | 700.9 | 574.5 | 662.6
500 | 348 | 537.9 | 561.5 | 684.7 | 574.5 | 660.6
501 | 349 | 543.2 | 554.2 | 669 | 574.9 | 657.2
502 | 350 | 548.6 | 548.5 | 671.2 | 575 | 655.6
503 | 351 | 553.9 | 545 | 668.2 | 575.2 | 654.3
504 | 352 | 559.1 | 543 | 662.8 | 575.5 | 653.3
505 | 353 | 564.5 | 546.8 | 669.3 | 576.2 | 654.7
506 | 354 | 569.7 | 549.1 | 684.1 | 577.2 | 658.5
507 | 355 | 575 | 550 | 702.7 | 578.2 | 658.6
508 | 356 | 580.3 | 548.7 | 714.9 | 578.7 | 658.2
509 | 357 | 585.4 | 553.1 | 701.7 | 578.5 | 659.4
510 | 358 | 590.1 | 551.2 | 692.9 | 578.6 | 658.1
511 | 359 | 595.3 | 549.3 | 686.9 | 578.7 | 658.1
512 | 360 | 601 | 550.7 | 692.2 | 579.3 | 658.6
513 | 361 | 606.4 | 553.2 | 677.7 | 579.5 | 658.2
514 | 362 | 611.5 | 552.8 | 663.9 | 579.9 | 656.4
515 | 363 | 617.2 | 552.5 | 659.3 | 580.8 | 654.8
516 | 364 | 623.6 | 560.9 | 665.8 | 582.3 | 655.4
517 | 365 | 629.6 | 557.4 | 665 | 583.6 | 655.3
518 | 366 | 635.2 | 563.2 | 656.9 | 584.7 | 656.2
519 | 367 | 640.2 | 558 | 641 | 585.7 | 653.3
520 | 368 | 646 | 554.1 | 626.2 | 587.2 | 649.8
521 | 369 | 652.2 | 550 | 615.4 | 588.5 | 648.2
522 | 370 | 657.8 | 548.2 | 610.4 | 589.4 | 647.6
523 | 371 | 663 | 546.4 | 620.9 | 590.5 | 647
524 | 372 | 667.1 | 546.7 | 626.4 | 590.9 | 647.6
525 | 373 | 671.4 | 550.9 | 639 | 591.9 | 648.2
526 | 374 | 676.6 | 552 | 674.2 | 592.6 | 651.3
527 | 375 | 679.4 | 553.4 | 697.3 | 592.9 | 654
528 | 376 | 680.5 | 560.6 | 721.6 | 593.1 | 657.7
529 | 377 | 681.1 | 563.5 | 738.9 | 594 | 661.7
530 | 378 | 682 | 565.5 | 743.3 | 595 | 663.1
531 | 379 | 684.2 | 570.4 | 726.4 | 596.5 | 663.8
532 | 380 | 687.8 | 572.7 | 719.4 | 597.5 | 664.8
533 | 381 | 690.6 | 576.1 | 709 | 598.4 | 666.2
534 | 382 | 694.1 | 577.1 | 696.7 | 600.2 | 664.5
535 | 383 | 697.6 | 577.6 | 701.8 | 601.7 | 665.5
536 | 384 | 700.1 | 576.6 | 703.1 | 602.6 | 666.4
537 | 385 | 702.2 | 573.8 | 716.7 | 604 | 666.7
538 | 386 | 704.1 | 579 | 747.6 | 605.2 | 668.2
539 | 387 | 705.3 | 580.4 | 771.9 | 606.4 | 670.7
540 | 388 | 706 | 586.6 | 784.5 | 607 | 674.1
541 | 389 | 705.8 | 587.1 | 785.9 | 608.3 | 676.4
542 | 390 | 706.4 | 584.3 | 789.6 | 609.9 | 677.5
543 | 391 | 706.9 | 586.2 | 793.7 | 611.3 | 680.5
544 | 392 | 707 | 584.8 | 797.2 | 613.2 | 682.1
545 | 393 | 707.1 | 585.1 | 804.5 | 614.9 | 683.7
546 | 394 | 707 | 581.2 | 804.4 | 616.8 | 683.8
547 | 395 | 707.4 | 577.5 | 797.5 | 618.9 | 683
548 | 396 | 708 | 574.3 | 778.2 | 621.1 | 681.2
549 | 397 | 708.9 | 569.8 | 753.6 | 623.6 | 678.3
550 | 398 | 710.3 | 566.6 | 738.1 | 625.7 | 676.2
551 | 399 | 711.8 | 562.9 | 718.7 | 627.5 | 674.2
552 | 400 | 713.5 | 559.9 | 705.3 | 629.5 | 672.2
553 | 401 | 715.6 | 558 | 694.3 | 632.1 | 670.8
554 | 402 | 717.6 | 555.6 | 687.9 | 634.3 | 669.5
555 | 403 | 719.6 | 554 | 684.1 | 636.6 | 669.1
556 | 404 | 721.4 | 556.7 | 668.4 | 639.2 | 668.7
557 | 405 | 723.8 | 556.7 | 675.2 | 641.7 | 669.9
558 | 406 | 725.8 | 555.7 | 685 | 643.6 | 671.3
559 | 407 | 727 | 557.5 | 690.3 | 645.5 | 672.4
560 | 408 | 728 | 564.5 | 684.4 | 647.1 | 674.8
561 | 409 | 728.5 | 568.9 | 693.3 | 648.8 | 678.1
562 | 410 | 729.4 | 570.6 | 681.5 | 651.5 | 677
563 | 411 | 731.2 | 570.8 | 671.5 | 654.6 | 675.9
564 | 412 | 733.5 | 566.9 | 676.5 | 657.4 | 675.6
565 | 413 | 735.2 | 564 | 680.2 | 659 | 675.1
566 | 414 | 736.5 | 563.3 | 672.7 | 660.9 | 673.2
567 | 415 | 737.3 | 563.4 | 670.5 | 662.2 | 673
568 | 416 | 738.3 | 563 | 674.5 | 664.3 | 672.1
569 | 417 | 739.5 | 562.1 | 678.8 | 666.4 | 672.2
570 | 418 | 740.4 | 561.5 | 674.6 | 668.6 | 671.5
571 | 419 | 742.3 | 562.5 | 658 | 671.6 | 670.4
572 | 420 | 744.4 | 568.7 | 654.3 | 673 | 672.6
573 | 421 | 745 | 574.3 | 671.1 | 673.8 | 675.5
574 | 422 | 745.2 | 572.2 | 669.1 | 675.6 | 674.8
575 | 423 | 746.3 | 571 | 676.4 | 677.6 | 675.4
576 | 424 | 747.8 | 569.7 | 692.9 | 680.1 | 676.2
577 | 425 | 748.9 | 566.5 | 701.2 | 682.9 | 676.7
578 | 426 | 750.1 | 564.3 | 711.8 | 685.7 | 677.6
579 | 427 | 750.8 | 565.7 | 734.6 | 688 | 681
580 | 428 | 751.8 | 566 | 746.4 | 690 | 683
581 | 429 | 753 | 565 | 765.9 | 692.6 | 685.2
582 | 430 | 754.2 | 564.4 | 766.6 | 694 | 686.3
583 | 431 | 754.4 | 564.8 | 769.8 | 694.9 | 688.1
584 | 432 | 754.3 | 571.9 | 778.3 | 695.4 | 690.8
585 | 433 | 753.3 | 574 | 786.6 | 696.1 | 692.2
586 | 434 | 752.5 | 576.1 | 792.2 | 696.8 | 694.6
587 | 435 | 752.4 | 576.6 | 787.2 | 699.2 | 695.4
588 | 436 | 753.7 | 578.2 | 778.6 | 703.1 | 696
589 | 437 | 755.7 | 576.5 | 776.8 | 706.6 | 696.3
590 | 438 | 758.3 | 576.3 | 775.9 | 710.2 | 696.1
591 | 439 | 761 | 575.5 | 783.6 | 713.8 | 697.2
592 | 440 | 762.3 | 580.8 | 779.3 | 714.2 | 700.1
593 | 441 | 762.7 | 589 | 776.2 | 715.6 | 701.1
594 | 442 | 764 | 593.9 | 764.8 | 718.2 | 701.9
595 | 443 | 765 | 600.6 | 751.2 | 719.5 | 703.6
596 | 444 | 765.2 | 604.9 | 745 | 720.3 | 705.5
597 | 445 | 765.4 | 611 | 747.9 | 721.2 | 706.7
598 | 446 | 765.4 | 612 | 745.3 | 722.2 | 707.2
599 | 447 | 765.6 | 610.4 | 762 | 722.5 | 708.9
600 | 448 | 765.7 | 605.3 | 770.9 | 723.4 | 709.5
601 | 449 | 766.3 | 602.3 | 764.1 | 723.9 | 710.7
602 | 450 | 766.2 | 601.1 | 779.4 | 724.2 | 712.4
603 | 451 | 765.9 | 597.3 | 783.8 | 724.5 | 712.8
604 | 452 | 766.2 | 594.2 | 784.7 | 726.1 | 713.1
605 | 453 | 766.1 | 595.7 | 796.5 | 726.7 | 715.6
606 | 454 | 765.5 | 595.1 | 806.2 | 726.8 | 716.9
607 | 455 | 764.8 | 597.3 | 811 | 726.2 | 718.2
608 | 456 | 763.5 | 598.9 | 813.6 | 726.1 | 720
609 | 457 | 763.4 | 594.8 | 806.8 | 727.5 | 719
610 | 458 | 764.1 | 592.7 | 807.2 | 728.8 | 719.3
611 | 459 | 765.1 | 588.2 | 799.4 | 730.3 | 717.8
612 | 460 | 766.6 | 585.8 | 799.4 | 731.8 | 717.2
613 | 461 | 767.1 | 588.5 | 789.9 | 732.8 | 717.8
614 | 462 | 767 | 590.2 | 774 | 733.4 | 717.2
615 | 463 | 767.5 | 587.4 | 770.3 | 734.3 | 717.2
616 | 464 | 768 | 590 | 762.8 | 735.6 | 717.5
617 | 465 | 768.9 | 587.6 | 764.9 | 736.9 | 717.2
618 | 466 | 770.3 | 583.4 | 764.1 | 738.5 | 716.4
619 | 467 | 771.7 | 582.5 | 748 | 740.2 | 715.4
620 | 468 | 773.1 | 583.6 | 723 | 741.7 | 714.4
621 | 469 | 775 | 581.4 | 707.1 | 743.6 | 712.3
622 | 470 | 777.8 | 581.4 | 711 | 745.9 | 712.8
623 | 471 | 779 | 580.3 | 732.6 | 746.5 | 714.2
624 | 472 | 781.2 | 582.8 | 740.8 | 747.8 | 714.1
625 | 473 | 783.3 | 582.4 | 758.8 | 749 | 714.2
626 | 474 | 784 | 582.3 | 766.5 | 749.3 | 715.6
627 | 475 | 785 | 583.6 | 762.7 | 750 | 716.8
628 | 476 | 786.1 | 586.4 | 764.5 | 751.1 | 718.3
629 | 477 | 787.8 | 586.5 | 746 | 751.6 | 717.1
630 | 478 | 789.5 | 587.4 | 755.1 | 752.9 | 718.1
631 | 479 | 790.1 | 584.3 | 761.2 | 753.1 | 718.8
632 | 480 | 790.7 | 585.9 | 754.2 | 754 | 718.9
633 | 481 | 790.9 | 588.4 | 746.1 | 754.9 | 719.7
634 | 482 | 791.5 | 592.5 | 727.3 | 755 | 718.5
635 | 483 | 792.5 | 591.7 | 724.2 | 756 | 718.1
636 | 484 | 793 | 592.7 | 730.7 | 757.1 | 720.4
637 | 485 | 792.9 | 595.3 | 724.2 | 758 | 721.4
638 | 486 | 792 | 594.9 | 715.8 | 758.1 | 720.8
639 | 487 | 791.5 | 596.6 | 715.4 | 758.6 | 720.1
640 | 488 | 791.7 | 594.9 | 719.3 | 758.6 | 720
641 | 489 | 792.2 | 595.3 | 726.6 | 759.8 | 720.8
642 | 490 | 793.5 | 590 | 742.7 | 760.5 | 720.9
643 | 491 | 794.6 | 588.3 | 755.1 | 761.6 | 721.2
644 | 492 | 793.9 | 588.5 | 765.2 | 762.5 | 723.1
645 | 493 | 792.8 | 593.3 | 767 | 763.7 | 725.4
646 | 494 | 791.3 | 596.6 | 761.9 | 763.9 | 726.7
647 | 495 | 790.2 | 599 | 757.9 | 763.6 | 727.7
648 | 496 | 790.2 | 603.7 | 752.5 | 764.1 | 728.3
649 | 497 | 789.9 | 606.1 | 745.8 | 764.4 | 728.7
650 | 498 | 790.7 | 603.7 | 744.5 | 764.4 | 727.6
651 | 499 | 792.5 | 603.6 | 742.7 | 765.3 | 728.2
652 | 500 | 793.8 | 604.6 | 743 | 766.8 | 729.3
653 | 501 | 792.6 | 604.8 | 746.9 | 767.2 | 729.8
654 | 502 | 791 | 604.1 | 757 | 766.8 | 729.5
655 | 503 | 790.7 | 601.4 | 764.9 | 766.3 | 729.3
656 | 504 | 791.4 | 599.9 | 760.9 | 767 | 730.2
657 | 505 | 790.7 | 603.5 | 760.1 | 767.8 | 731.8
658 | 506 | 789.7 | 609.9 | 760 | 768.9 | 733.7
659 | 507 | 789.4 | 612.3 | 755.4 | 769.7 | 732.5
660 | 508 | 789.7 | 611.6 | 753.8 | 770.4 | 732.1
661 | 509 | 789.3 | 610 | 753.3 | 770.8 | 732.2
662 | 510 | 788.7 | 610.4 | 752.8 | 771 | 732.9
663 | 511 | 788.2 | 612 | 746.7 | 771.2 | 733.1
664 | 512 | 788.5 | 612.2 | 731.4 | 770.9 | 732.2
665 | 513 | 789.3 | 612.6 | 721.2 | 771.1 | 730.4
666 | 514 | 789.8 | 610.9 | 722.8 | 771.7 | 731.6
667 | 515 | 790.6 | 609.2 | 722.3 | 771.9 | 731.1
668 | 516 | 790.2 | 607.7 | 735.5 | 772.1 | 731.2
669 | 517 | 790.9 | 605.8 | 742.8 | 773.1 | 731
670 | 518 | 792.3 | 602.8 | 750.6 | 774.3 | 730.9
671 | 519 | 794 | 599.2 | 747.4 | 774.2 | 728.7
672 | 520 | 795.9 | 597.8 | 749.8 | 775.2 | 729
673 | 521 | 796.5 | 601.3 | 735.1 | 775.6 | 727.8
674 | 522 | 797.5 | 602.3 | 723.9 | 776 | 726.3
675 | 523 | 797 | 602.8 | 728 | 777.4 | 726.8
676 | 524 | 795.8 | 601.6 | 746.4 | 777.7 | 727.2
677 | 525 | 795.1 | 605.2 | 749.7 | 777.7 | 727.3
678 | 526 | 794.7 | 605.9 | 745.7 | 777.9 | 728.1
679 | 527 | 793.9 | 606.7 | 750.8 | 778.4 | 728.8
680 | 528 | 792.6 | 607.7 | 762.4 | 779.2 | 730.2
681 | 529 | 792.1 | 608.2 | 748.6 | 779.2 | 730.1
682 | 530 | 792.6 | 608.4 | 736.3 | 778.1 | 727.7
683 | 531 | 793.8 | 610.8 | 730.2 | 778.1 | 728
684 | 532 | 795.1 | 609.2 | 724.9 | 777.8 | 725.3
685 | 533 | 796.6 | 606.7 | 727.6 | 778.1 | 724
686 | 534 | 797.4 | 608.2 | 733.8 | 779.5 | 724.7
687 | 535 | 797.1 | 609.6 | 744.4 | 780.6 | 725.7
688 | 536 | 797.2 | 610.5 | 754.5 | 781.4 | 727.2
689 | 537 | 796.9 | 611 | 768.2 | 782.5 | 727.7
690 | 538 | 795.3 | 610.7 | 775.3 | 782.9 | 729.7
691 | 539 | 794.9 | 608.7 | 772.9 | 782.1 | 729.4
692 | 540 | 795.3 | 609.3 | 772.5 | 782.6 | 728.1
693 | 541 | 795.3 | 610.1 | 765.8 | 782.9 | 728.3
694 | 542 | 795.9 | 610.1 | 759.5 | 782.2 | 727.8
695 | 543 | 797 | 606.9 | 756.7 | 781.4 | 725.2
696 | 544 | 798.9 | 603.2 | 752.5 | 779.9 | 720.9
697 | 545 | 799.9 | 603.9 | 753.1 | 780.2 | 720.9
698 | 546 | 799.8 | 604.7 | 752.1 | 781.2 | 721.2
699 | 547 | 798.5 | 607.2 | 747.1 | 782.2 | 720.8
700 | 548 | 796.9 | 608.9 | 757.4 | 782.8 | 721.8
701 | 549 | 796.2 | 610.4 | 759.3 | 783.2 | 723.4
702 | 550 | 796.3 | 612.1 | 758.4 | 783.9 | 724.8
703 | 551 | 795.8 | 615.3 | 744.2 | 783.8 | 723.5
704 | 552 | 796.3 | 618.8 | 739 | 783.9 | 721.9
705 | 553 | 795.2 | 619.9 | 747.7 | 784 | 721.6
706 | 554 | 793.8 | 621.2 | 747.2 | 784.2 | 721.8
707 | 555 | 793 | 620.3 | 749 | 784.1 | 721.8
708 | 556 | 793.8 | 617.9 | 759.6 | 783.1 | 720.4
709 | 557 | 795 | 613.7 | 762.3 | 781.9 | 717.4
710 | 558 | 796.3 | 616 | 769 | 781.1 | 715
711 | 559 | 796.7 | 621.9 | 765.9 | 782 | 715.2
712 | 560 | 796.5 | 620.5 | 772.4 | 782.7 | 715.4
713 | 561 | 797.3 | 618.6 | 777.5 | 781.6 | 713.2
714 | 562 | 797.3 | 619.2 | 785 | 782.2 | 714.5
715 | 563 | 797.3 | 617.8 | 789.5 | 781.4 | 714.2
716 | 564 | 798.5 | 616.7 | 790.6 | 781 | 714
717 | 565 | 798.2 | 619.6 | 789.1 | 783.2 | 716
718 | 566 | 797.5 | 618.5 | 790.2 | 783.3 | 715.5
719 | 567 | 798.6 | 617.2 | 788.2 | 781.7 | 713.5
720 | 568 | 800 | 618.8 | 779.8 | 781 | 710.8
721 | 569 | 801.2 | 624.1 | 780.1 | 781.7 | 710.3
722 | 570 | 801.5 | 622.8 | 780.4 | 782.3 | 711.1
723 | 571 | 802.5 | 621.8 | 771.5 | 782 | 709
724 | 572 | 803.6 | 619.4 | 766.6 | 780.6 | 706.9
725 | 573 | 805.7 | 624.5 | 758.8 | 779.1 | 702.9
726 | 574 | 807.4 | 624 | 756.2 | 779.1 | 701
727 | 575 | 808.7 | 621.6 | 746.3 | 778.6 | 698.4
728 | 576 | 810.1 | 628.2 | 747.9 | 778.1 | 696.5
729 | 577 | 811.5 | 634.1 | 749.3 | 778.9 | 694.6
730 | 578 | 811.6 | 635 | 748.7 | 780 | 693.8
731 | 579 | 811.4 | 632.1 | 750.3 | 780.3 | 693.3
732 | 580 | 809.8 | 629.1 | 757.4 | 781.7 | 694.5
733 | 581 | 809.1 | 629.2 | 767.6 | 782 | 695.5
734 | 582 | 808.9 | 626 | 773.3 | 782.6 | 696.6
735 | 583 | 808.2 | 625.5 | 767.1 | 783 | 696.7
736 | 584 | 807.4 | 623.3 | 776.8 | 783.6 | 697.3
737 | 585 | 806.6 | 625 | 775.2 | 784.3 | 698.5
738 | 586 | 805.1 | 629.3 | 776 | 786.3 | 700.3
739 | 587 | 803 | 634.6 | 781.2 | 787.8 | 703.8
740 | 588 | 802.5 | 634.5 | 785.8 | 787.4 | 704.1
741 | 589 | 802.6 | 632.9 | 785.3 | 787.3 | 704.2
742 | 590 | 802.1 | 632.8 | 782.8 | 788.1 | 706.3
743 | 591 | 800.1 | 639.3 | 778.5 | 789.3 | 708.5
744 | 592 | 798.4 | 638.2 | 779.4 | 789.3 | 709.5
745 | 593 | 797.5 | 638.7 | 788.3 | 789.8 | 711.4
746 | 594 | 797.1 | 639.8 | 785.2 | 790.1 | 713.7
747 | 595 | 796.4 | 641.9 | 777.3 | 790.7 | 714.3
748 | 596 | 795.2 | 644.3 | 775.6 | 791.4 | 716
749 | 597 | 793.8 | 645.3 | 779.8 | 791.4 | 716.3
750 | 598 | 792.9 | 645.7 | 779.2 | 791.1 | 716.8
751 | 599 | 792.6 | 644.3 | 783.3 | 791.1 | 717.8
752 | 600 | 791.7 | 648.2 | 784.4 | 792.2 | 720.9
753 | 601 | 790.9 | 650.1 | 783.4 | 792.8 | 723
754 | 602 | 790.6 | 650.2 | 785.6 | 793 | 725
755 | 603 | 790.9 | 650.1 | 786.8 | 792.4 | 724.2
756 | 604 | 790.7 | 645.7 | 789.3 | 792.2 | 724
757 | 605 | 791.5 | 643.2 | 780.7 | 791.7 | 725.2
758 | 606 | 792.8 | 642.5 | 772 | 791.4 | 724.5
759 | 607 | 793.4 | 641.5 | 772.9 | 791.8 | 723.8
760 | 608 | 793.7 | 637.6 | 785.6 | 791.8 | 723.2
761 | 609 | 796.3 | 630.9 | 784 | 790 | 720.5
762 | 610 | 797.6 | 627.5 | 783.9 | 790.6 | 719.6
763 | 611 | 798.5 | 624.7 | 791.1 | 790.3 | 718.7
764 | 612 | 799.7 | 619.3 | 789.6 | 789.5 | 716.8
765 | 613 | 801.3 | 614.7 | 791.5 | 788.5 | 716.2
766 | 614 | 803.1 | 606.8 | 789.9 | 787.7 | 715
767 | 615 | 804.7 | 605.9 | 788.1 | 787.8 | 714.4
768 | 616 | 806.4 | 602.8 | 778.3 | 786.4 | 711.7
769 | 617 | 807.3 | 601.6 | 779.8 | 786.6 | 710.6
770 | 618 | 807.1 | 601.3 | 780.6 | 787 | 710.7
771 | 619 | 807.8 | 599.1 | 786.3 | 787.1 | 710.3
772 | 620 | 808 | 601.6 | 786.7 | 787.9 | 712
773 | 621 | 808.7 | 602.7 | 787 | 788 | 711.4
774 | 622 | 808.7 | 606.1 | 790.9 | 789.2 | 713.5
775 | 623 | 807.2 | 606.8 | 794.9 | 790.7 | 715
776 | 624 | 806.3 | 607 | 787.1 | 790.8 | 715.5
777 | 625 | 806.3 | 605.9 | 777.2 | 789.5 | 712.9
778 | 626 | 805.9 | 604.6 | 775.3 | 788.8 | 711.4
779 | 627 | 805.4 | 602.6 | 773.8 | 788.1 | 710
780 | 628 | 805.5 | 602.5 | 764.7 | 786.9 | 707.9
781 | 629 | 805.5 | 598.4 | 760.9 | 785.5 | 705
782 | 630 | 805.5 | 597 | 769 | 785.1 | 705.5
783 | 631 | 804.9 | 597.1 | 773.4 | 785.5 | 705.6
784 | 632 | 803 | 600.5 | 783.1 | 786.5 | 707.5
785 | 633 | 801.9 | 600.4 | 792 | 786.6 | 709.4
786 | 634 | 801.1 | 598.8 | 795.7 | 787.2 | 711.5
787 | 635 | 800 | 599 | 799.9 | 787.8 | 712.2
788 | 636 | 799.1 | 597.6 | 804.4 | 788.1 | 714.3
789 | 637 | 798 | 595.8 | 805 | 788.7 | 715.6
790 | 638 | 797.7 | 598.3 | 793.1 | 788.4 | 715.5
791 | 639 | 797 | 599.5 | 781.4 | 787.2 | 713
792 | 640 | 797.1 | 599.2 | 772.9 | 785.8 | 710.5
793 | 641 | 797.8 | 593.5 | 771.4 | 784.1 | 709.2
794 | 642 | 798.2 | 592.5 | 775 | 783.7 | 707.8
795 | 643 | 798.4 | 590 | 770.3 | 782.9 | 706
796 | 644 | 799.2 | 586.5 | 759.6 | 781.4 | 703.2
797 | 645 | 799.3 | 584.9 | 766.8 | 781.1 | 703.5
798 | 646 | 800 | 583.5 | 769.8 | 780.2 | 703.5
799 | 647 | 800.2 | 582.4 | 774.5 | 780 | 703
800 | 648 | 799.6 | 583.5 | 778.7 | 780.5 | 704.3
801 | 649 | 798.5 | 588 | 779.4 | 781.6 | 707.5
802 | 650 | 797 | 594.7 | 774.9 | 782.3 | 708.7
803 | 651 | 794.8 | 600.7 | 770.7 | 782.5 | 709.2
804 | 652 | 793.1 | 605.1 | 771.1 | 782.8 | 709.5
805 | 653 | 791.3 | 604.2 | 776.8 | 783.6 | 712.8
806 | 654 | 789.9 | 605.1 | 782.7 | 784.1 | 714.8
807 | 655 | 789 | 606.6 | 782.5 | 783.8 | 714.3
808 | 656 | 788.2 | 606.7 | 782.5 | 783.5 | 714.7
809 | 657 | 788.4 | 603.2 | 776.8 | 781.8 | 712.8
810 | 658 | 789.2 | 596.6 | 769.2 | 780 | 710.1
811 | 659 | 790.3 | 592.1 | 765 | 778.3 | 707.4
812 | 660 | 791.6 | 587.3 | 763.6 | 776.7 | 705.3
813 | 661 | 792.4 | 583.5 | 753.9 | 775.3 | 702.5
814 | 662 | 792.8 | 579.7 | 750.1 | 774.2 | 700.1
815 | 663 | 792.7 | 579.4 | 746.3 | 773.6 | 699
816 | 664 | 792.5 | 577.4 | 742.9 | 772.4 | 696.2
817 | 665 | 792.2 | 575.2 | 752.4 | 771.9 | 695.6
818 | 666 | 792 | 571.8 | 753.8 | 770.8 | 694.3
819 | 667 | 791.7 | 571 | 752.8 | 770.3 | 694.2
820 | 668 | 791.1 | 571.2 | 757.1 | 770.1 | 694.6
821 | 669 | 790.6 | 569.3 | 752.6 | 769.4 | 693.8
822 | 670 | 789.7 | 571.1 | 755.4 | 769.9 | 695.5
823 | 671 | 788.4 | 573.9 | 758.9 | 770.5 | 695.9
824 | 672 | 787.1 | 578.4 | 752.1 | 770 | 695.6
825 | 673 | 785.8 | 580.9 | 746.1 | 769.7 | 695.7
826 | 674 | 784.1 | 588.5 | 752.9 | 770.4 | 699.1
827 | 675 | 782.2 | 594.9 | 751 | 770.7 | 701.1
828 | 676 | 780.5 | 601 | 747.5 | 770.8 | 701.9
829 | 677 | 779.2 | 602 | 746.5 | 770.5 | 702.7
830 | 678 | 778.5 | 601.2 | 741.8 | 770 | 702.8
831 | 679 | 778 | 599.6 | 747.2 | 769.7 | 702.3
832 | 680 | 777.4 | 596.7 | 762.1 | 769.6 | 703.2
833 | 681 | 777.1 | 594.1 | 769.2 | 769.8 | 705.4
834 | 682 | 776.3 | 595.1 | 775.3 | 770.8 | 709.5
835 | 683 | 775.4 | 596.7 | 772.8 | 770.9 | 709.2
836 | 684 | 774.1 | 602.5 | 779.2 | 771.8 | 712
837 | 685 | 772.6 | 604.9 | 786.1 | 772.5 | 715.1
838 | 686 | 772.2 | 601.8 | 791 | 772.1 | 715.8
839 | 687 | 772.1 | 598.8 | 790.6 | 771.7 | 714.8
840 | 688 | 772.3 | 597.3 | 797.4 | 771.9 | 714.7
841 | 689 | 772.2 | 596.8 | 802.1 | 772.3 | 716.1
842 | 690 | 772.3 | 597.3 | 801.7 | 772.3 | 718.4
843 | 691 | 772.6 | 597.2 | 800.4 | 772.6 | 719
844 | 692 | 773.1 | 593.7 | 805 | 772.4 | 719.5
845 | 693 | 773.2 | 592.5 | 811.7 | 773.2 | 721.8
846 | 694 | 772.9 | 589.2 | 814.2 | 773.5 | 724.6
847 | 695 | 772.8 | 590.5 | 813.6 | 774 | 727.3
848 | 696 | 772.3 | 591.9 | 816.2 | 774.7 | 728.1
849 | 697 | 772 | 593.1 | 816.5 | 775 | 729.4
850 | 698 | 771.4 | 598.9 | 813.7 | 775.5 | 731
851 | 699 | 770.8 | 604.5 | 814.6 | 776.2 | 732.8
852 | 700 | 770.2 | 608.2 | 814.2 | 777.4 | 735.7
853 | 701 | 769.6 | 612.2 | 815.8 | 777.9 | 737
854 | 702 | 769 | 617.2 | 816.5 | 778.3 | 739.7
855 | 703 | 768.3 | 618.9 | 815.4 | 778.8 | 741.9
856 | 704 | 767.7 | 621.3 | 815.5 | 779.2 | 743.9
857 | 705 | 767.4 | 627.4 | 810.3 | 779.1 | 745.7
858 | 706 | 766.9 | 629.5 | 812.6 | 779.9 | 746.1
859 | 707 | 766.7 | 629.7 | 816.4 | 780.4 | 747.6
860 | 708 | 767 | 626.4 | 816.3 | 780.4 | 747.7
861 | 709 | 768.1 | 618.4 | 813.2 | 779 | 744.9
862 | 710 | 769.9 | 613.4 | 817.5 | 778.9 | 746.1
863 | 711 | 771 | 611.2 | 821.9 | 779.4 | 747.5
864 | 712 | 772.1 | 609.6 | 823.9 | 779.5 | 747.2
865 | 713 | 772.6 | 613.2 | 827.1 | 780.9 | 751.1
866 | 714 | 772.8 | 617.6 | 826.4 | 781.5 | 751.8
867 | 715 | 772.6 | 626 | 819.9 | 782.4 | 754
868 | 716 | 772.3 | 633.7 | 813.1 | 782.8 | 755
869 | 717 | 772.2 | 636.3 | 810.3 | 783.2 | 755.7
870 | 718 | 772.5 | 634.4 | 812.2 | 783.3 | 755.9
871 | 719 | 773.8 | 627.9 | 811.5 | 782.8 | 755.6
872 | 720 | 774.8 | 628.1 | 811.5 | 783.1 | 756.9
873 | 721 | 775.1 | 627.8 | 816.6 | 783.7 | 758.3
874 | 722 | 775.5 | 625.3 | 820.5 | 784 | 759.4
875 | 723 | 777 | 619.9 | 823 | 783.8 | 759.1
876 | 724 | 778.5 | 614.3 | 821 | 783.3 | 757.7
877 | 725 | 780 | 610.5 | 824.4 | 783.1 | 757.9
878 | 726 | 781.1 | 608.7 | 826.9 | 782.8 | 756.9
879 | 727 | 782.6 | 607 | 815 | 781.8 | 755.2
880 | 728 | 783.8 | 605.8 | 808 | 781.2 | 753.3
881 | 729 | 784.6 | 606.3 | 806.6 | 780.8 | 753
882 | 730 | 785.1 | 609.4 | 800.9 | 780.5 | 752.4
883 | 731 | 785.5 | 611.3 | 804.6 | 780.4 | 751.8
884 | 732 | 785.6 | 609.8 | 809.8 | 780.2 | 752.6
885 | 733 | 786.3 | 605.9 | 802.2 | 778.6 | 748.9
886 | 734 | 787.3 | 602 | 804.6 | 777.6 | 748.6
887 | 735 | 788.1 | 600.2 | 807.8 | 777.9 | 749.5
888 | 736 | 787.9 | 601.3 | 817 | 779.1 | 752.3
889 | 737 | 788 | 599 | 821.7 | 779.4 | 752.3
890 | 738 | 788.4 | 599.1 | 828 | 779.5 | 753.9
891 | 739 | 788.6 | 598.9 | 831.6 | 779.5 | 755.1
892 | 740 | 788.2 | 600 | 830.5 | 779.4 | 755.4
893 | 741 | 788.2 | 597.4 | 816.1 | 778 | 752.1
894 | 742 | 789.1 | 594.6 | 800.4 | 776 | 747.8
895 | 743 | 789.9 | 591 | 793.1 | 774.4 | 745.5
896 | 744 | 790.7 | 589.8 | 798.3 | 773.1 | 743.6
897 | 745 | 791.4 | 586.9 | 807.3 | 772.5 | 742.6
898 | 746 | 792.2 | 584.8 | 810.2 | 771.9 | 743.5
899 | 747 | 792.9 | 582.8 | 808.6 | 771.2 | 742.8
900 | 748 | 793.7 | 581.5 | 810.5 | 770.3 | 740.8
901 | 749 | 794.2 | 581.8 | 814.4 | 770.2 | 740.7
902 | 750 | 794.1 | 586.5 | 818.3 | 770.8 | 742
903 | 751 | 793.2 | 597.9 | 819.6 | 772.4 | 745.9
904 | 752 | 791.7 | 605 | 821.7 | 773.7 | 747
905 | 753 | 789.9 | 614.5 | 812.1 | 774.8 | 748.9
906 | 754 | 788.3 | 623.8 | 797.8 | 775.5 | 749.5
907 | 755 | 787.1 | 629.9 | 790.3 | 775.9 | 749.6
908 | 756 | 786.3 | 632.4 | 793 | 776.3 | 749.9
909 | 757 | 785.3 | 631.6 | 800.4 | 776.6 | 751.5
910 | 758 | 784.9 | 628 | 804.8 | 776.5 | 752
911 | 759 | 784.9 | 624.2 | 797.7 | 775.8 | 749.9
912 | 760 | 785.4 | 619 | 793.2 | 774 | 746.3
913 | 761 | 785.8 | 616.1 | 792 | 773.4 | 745.7
914 | 762 | 785.9 | 612.7 | 788.8 | 772.3 | 744.2
915 | 763 | 786.3 | 608.8 | 780.2 | 770.6 | 741
916 | 764 | 786.7 | 603.7 | 776.7 | 768.9 | 738.5
917 | 765 | 787.2 | 598.5 | 771.8 | 767.1 | 736.2
918 | 766 | 787.6 | 594.5 | 761.9 | 765.3 | 732.8
919 | 767 | 787.5 | 591.2 | 761 | 764.2 | 731.3
920 | 768 | 787.1 | 588 | 759.3 | 763.2 | 729.2
921 | 769 | 786.7 | 585.5 | 755.9 | 762.2 | 727.3
922 | 770 | 785.7 | 586.9 | 757.9 | 762.1 | 727.7
923 | 771 | 784.9 | 583.9 | 755 | 761 | 725.4
924 | 772 | 784.2 | 581.3 | 742.5 | 759.6 | 722.2
925 | 773 | 783.3 | 580.6 | 741.2 | 758.7 | 721
926 | 774 | 782.6 | 580.7 | 749.8 | 758.5 | 721.7
927 | 775 | 781.4 | 583 | 766.3 | 759.5 | 724.5
928 | 776 | 780.1 | 587 | 784.2 | 760.9 | 727.6
929 | 777 | 778.7 | 592 | 795.4 | 762.6 | 730.5
930 | 778 | 777.5 | 594.4 | 806.9 | 764 | 733.4
931 | 779 | 776.1 | 597.5 | 813.3 | 765.7 | 737.1
932 | 780 | 774.6 | 604.5 | 809.7 | 767.1 | 739.8
933 | 781 | 773.1 | 616.4 | 809.5 | 768.9 | 742.7
934 | 782 | 772.1 | 624.4 | 803.1 | 770.2 | 746
935 | 783 | 771.3 | 627.9 | 811 | 771.5 | 747.9
936 | 784 | 770.7 | 625.2 | 816.3 | 772.3 | 748.4
937 | 785 | 770.4 | 625.6 | 818.6 | 773.5 | 750.3
938 | 786 | 770.4 | 629.6 | 818.9 | 774.8 | 752.3
939 | 787 | 770.3 | 635 | 818.3 | 776 | 754.9
940 | 788 | 770.1 | 639.6 | 811.9 | 776.8 | 756.3
941 | 789 | 770.2 | 640.2 | 812.1 | 777.6 | 757
942 | 790 | 770.6 | 637.8 | 815.2 | 778.4 | 757.7
943 | 791 | 771.6 | 633 | 814.5 | 778.2 | 756.4
944 | 792 | 772.6 | 630 | 816.1 | 778.7 | 757.3
945 | 793 | 773.5 | 629.3 | 818.5 | 779.4 | 759.6
946 | 794 | 774.7 | 624.1 | 807.7 | 778.5 | 755.4
947 | 795 | 775.8 | 619.7 | 810.7 | 778.3 | 754.8
948 | 796 | 777.1 | 615.4 | 801.1 | 777.2 | 752.2
949 | 797 | 778.3 | 609.7 | 789.1 | 775.8 | 749.5
950 | 798 | 779.6 | 605 | 765.9 | 773.7 | 744.2
951 | 799 | 780.8 | 600.2 | 752.7 | 771.7 | 740.2
952 | 800 | 781.8 | 592.7 | 742.9 | 769.6 | 736.5
953 | 801 | 782.8 | 586.1 | 721.9 | 767.4 | 731.3
954 | 802 | 783.6 | 578.8 | 713.7 | 765.2 | 727.2
955 | 803 | 784.1 | 575.6 | 715.3 | 763.3 | 724.4
956 | 804 | 784.3 | 572.3 | 725.3 | 762.2 | 722.6
957 | 805 | 784.4 | 570.2 | 727.6 | 760.8 | 719.9
958 | 806 | 784.4 | 567.9 | 722.2 | 759.2 | 717.2
959 | 807 | 784.3 | 564.4 | 711.7 | 757.3 | 713.6
960 | 808 | 783.7 | 564.9 | 707.2 | 756 | 711
961 | 809 | 782.8 | 569.3 | 712.3 | 755.5 | 710.3
962 | 810 | 781.5 | 572.9 | 714.5 | 755.4 | 709.6
963 | 811 | 780.2 | 576.5 | 736.5 | 756.5 | 712.6
964 | 812 | 778.9 | 575.3 | 745.7 | 756.1 | 712.4
965 | 813 | 777.8 | 574.9 | 749.6 | 755.7 | 712
966 | 814 | 777.1 | 572 | 751.5 | 754.1 | 709.7
967 | 815 | 776.1 | 575.3 | 766.6 | 754.6 | 712.3
968 | 816 | 775.3 | 574.5 | 764.3 | 753.9 | 711.4
969 | 817 | 774.5 | 572.1 | 758.1 | 753 | 710
970 | 818 | 773.4 | 572.9 | 763.1 | 753.1 | 712.3
971 | 819 | 772.5 | 571.1 | 765.5 | 753.2 | 712.4
972 | 820 | 771.2 | 573.6 | 778.9 | 754.6 | 716.4
973 | 821 | 770.1 | 575.8 | 774.6 | 755.1 | 717.7
974 | 822 | 768.9 | 579 | 780 | 755.4 | 717.8
975 | 823 | 767.7 | 579.6 | 780.3 | 755.6 | 717.6
976 | 824 | 766.6 | 581 | 783.2 | 756 | 719.3
977 | 825 | 765.4 | 589.1 | 789.2 | 757.7 | 723
978 | 826 | 764.1 | 597.4 | 793.1 | 759.9 | 726.7
979 | 827 | 762.8 | 607.1 | 795.6 | 761.6 | 729.3
980 | 828 | 761.6 | 614.9 | 793.5 | 763.5 | 732.3
981 | 829 | 760.5 | 623.4 | 789.3 | 765.3 | 735.3
982 | 830 | 759.6 | 629.9 | 790.7 | 767.4 | 737.7
983 | 831 | 758.8 | 635.6 | 785.8 | 768.9 | 739.7
984 | 832 | 758.1 | 638.1 | 794.2 | 770 | 741.2
985 | 833 | 757.8 | 636.4 | 799.3 | 771.2 | 743.7
986 | 834 | 757.9 | 630.2 | 808.7 | 770.2 | 743.4
987 | 835 | 758.2 | 627.1 | 811.3 | 770 | 744.3
988 | 836 | 759 | 620.6 | 801 | 767.4 | 740.9
989 | 837 | 760.3 | 610.9 | 787.6 | 762.9 | 736.5
990 | 838 | 761.4 | 604.5 | 794.7 | 761 | 736
991 | 839 | 762.3 | 601.5 | 806.1 | 761.4 | 738.1
992 | 840 | 762.8 | 602.6 | 809.4 | 763.6 | 741.4
993 | 841 | 762.9 | 610 | 814.6 | 767.1 | 744.8
994 | 842 | 762.8 | 614.4 | 818.5 | 769.8 | 747.3
995 | 843 | 762.9 | 616.2 | 821.4 | 771.9 | 748.7
996 | 844 | 763.3 | 622.4 | 825.7 | 773.8 | 750.9
997 | 845 | 764 | 620.5 | 831 | 774.7 | 752.3
998 | 846 | 765.4 | 614.9 | 831.8 | 772.6 | 752.7
999 | 847 | 766.5 | 616.2 | 831.7 | 774.1 | 755.1
1000 | 848 | 767.2 | 618.2 | 830.5 | 775.5 | 756.1
1001 | 849 | 768.1 | 613.1 | 824.4 | 772.4 | 753.6
1002 | 850 | 769.4 | 604.7 | 808 | 768.3 | 749.8
1003 | 851 | 770.9 | 598.1 | 810 | 765 | 747.6
1004 | 852 | 771.8 | 601.5 | 814.5 | 766.8 | 751
1005 | 853 | 771.9 | 605.4 | 814.8 | 769.6 | 751.8
1006 | 854 | 771.9 | 605.6 | 823.2 | 771.7 | 753.9
1007 | 855 | 772.3 | 603.7 | 827.9 | 772.2 | 754.1
1008 | 856 | 772.5 | 608.1 | 831.4 | 774.2 | 756
1009 | 857 | 772.6 | 613.1 | 831.4 | 776.5 | 759
1010 | 858 | 772.6 | 612.9 | 833.5 | 777.5 | 757.9
1011 | 859 | 772.9 | 606.9 | 817.4 | 774.1 | 752.4
1012 | 860 | 773.7 | 602.4 | 816.7 | 771.3 | 750.7
1013 | 861 | 774.6 | 599.2 | 809.7 | 768.3 | 747.8
1014 | 862 | 775.3 | 594.2 | 791.2 | 764.8 | 743.6
1015 | 863 | 776.1 | 588.6 | 788.4 | 761.4 | 740.2
1016 | 864 | 776.3 | 588 | 797.6 | 760.9 | 740.9
1017 | 865 | 776.8 | 587.1 | 799.1 | 760.1 | 739.3
1018 | 866 | 777.2 | 583 | 785.5 | 757.6 | 736.5
1019 | 867 | 777.2 | 581.3 | 778.5 | 755.7 | 733.8
1020 | 868 | 777 | 579 | 766.3 | 754 | 730.4
1021 | 869 | 776.6 | 575.4 | 752.8 | 751.4 | 727
1022 | 870 | 776.1 | 574.3 | 749.1 | 750.8 | 725.5
1023 | 871 | 775.3 | 573.6 | 756.9 | 751.7 | 725.9
1024 | 872 | 774.7 | 575.5 | 747.2 | 751.6 | 724.8
1025 | 873 | 774.2 | 577.1 | 762.4 | 752.4 | 725.8
1026 | 874 | 773.3 | 575.7 | 752.7 | 750.6 | 722.5
1027 | 875 | 773 | 571.8 | 742.3 | 746.6 | 718.7
1028 | 876 | 772.9 | 568.5 | 743 | 743.9 | 716
1029 | 877 | 772.7 | 564.6 | 735.3 | 741.7 | 713.5
1030 | 878 | 772.6 | 559 | 726.1 | 738.4 | 709.6
1031 | 879 | 772 | 555.5 | 725.8 | 735.8 | 707.5
1032 | 880 | 771.5 | 555.1 | 725.3 | 735 | 705.6
1033 | 881 | 770.6 | 556.5 | 731.5 | 734.7 | 705.4
1034 | 882 | 769.8 | 557.2 | 736.7 | 733.9 | 703.9
1035 | 883 | 768.6 | 558.7 | 741.7 | 733.9 | 704.5
1036 | 884 | 767.4 | 561.7 | 753.6 | 734.4 | 706.9
1037 | 885 | 766.2 | 562.4 | 761.7 | 734.9 | 707.3
1038 | 886 | 765.2 | 562.2 | 772 | 734.3 | 707.5
1039 | 887 | 764.1 | 562.2 | 774 | 734.3 | 708.5
1040 | 888 | 763.5 | 559 | 772.7 | 731.6 | 706.3
1041 | 889 | 763 | 558.5 | 772 | 729.7 | 706.1
1042 | 890 | 762.5 | 556 | 778 | 728.2 | 705.8
1043 | 891 | 762.4 | 554.3 | 780.2 | 727.6 | 706.3
1044 | 892 | 762 | 553.4 | 773.9 | 726.9 | 705
1045 | 893 | 761.9 | 552.1 | 770.2 | 725.6 | 703.8
1046 | 894 | 761.6 | 550.3 | 777.5 | 724.5 | 703.8
1047 | 895 | 761 | 551.4 | 781 | 725.1 | 703.4
1048 | 896 | 760.6 | 550.6 | 768.7 | 723.9 | 701.7
1049 | 897 | 760.1 | 549.3 | 754.3 | 721.7 | 698.3
1050 | 898 | 759.6 | 548.4 | 745.9 | 720.3 | 697.6
1051 | 899 | 759 | 547.3 | 746 | 719.5 | 695.5
1052 | 900 | 758.2 | 546.5 | 749.9 | 719.5 | 695.1
1053 | 901 | 757.4 | 551.8 | 753.6 | 720.9 | 696.5
1054 | 902 | 756.2 | 560.6 | 758.5 | 724.2 | 698.5
1055 | 903 | 755.2 | 570.5 | 763.9 | 727.5 | 701.9
1056 | 904 | 754.3 | 573.2 | 768.3 | 729.4 | 703.2
1057 | 905 | 753.6 | 569.5 | 757.2 | 727.3 | 699.9
1058 | 906 | 753 | 560.5 | 737.8 | 724.2 | 695.9
1059 | 907 | 752.4 | 552.5 | 710.5 | 720 | 691.2
1060 | 908 | 751.8 | 551.3 | 705.6 | 717.7 | 689.8
1061 | 909 | 751 | 554.2 | 717.7 | 718.4 | 690.2
1062 | 910 | 750.4 | 552.9 | 714.8 | 717.6 | 688.2
1063 | 911 | 749.6 | 553.9 | 726.4 | 717.6 | 689.7
1064 | 912 | 748.8 | 556.3 | 726.4 | 719 | 690.1
1065 | 913 | 747.8 | 561.6 | 744.9 | 721.9 | 693.5
1066 | 914 | 747.1 | 562.6 | 738.6 | 722.4 | 692.1
1067 | 915 | 746.3 | 562.7 | 733.2 | 722.4 | 691.7
1068 | 916 | 745.8 | 562.3 | 733.1 | 721.8 | 691.2
1069 | 917 | 745.6 | 558.9 | 718.8 | 719.5 | 687.3
1070 | 918 | 745.4 | 557 | 704.2 | 717.6 | 684.5
1071 | 919 | 745.3 | 557.1 | 702.9 | 716 | 682.9
1072 | 920 | 745.5 | 556.5 | 719.4 | 714.7 | 682.6
1073 | 921 | 745 | 563.6 | 733.1 | 717.7 | 686.8
1074 | 922 | 744.7 | 568.5 | 731.7 | 721.1 | 689.4
1075 | 923 | 744.3 | 569.4 | 752.5 | 723.7 | 692.2
1076 | 924 | 744.3 | 568.2 | 754.2 | 723.3 | 690.2
1077 | 925 | 744.5 | 565.8 | 733.8 | 720.8 | 686.6
1078 | 926 | 744.8 | 557.9 | 712.9 | 716.8 | 683.1
1079 | 927 | 744.9 | 556.2 | 727.4 | 714.9 | 684.1
1080 | 928 | 745.1 | 554.9 | 737.6 | 714.1 | 684.5
1081 | 929 | 745.4 | 553.4 | 744.4 | 712.8 | 683.5
1082 | 930 | 745.6 | 550.7 | 743.5 | 711.4 | 681.8
1083 | 931 | 746 | 547.8 | 740.9 | 709.1 | 680.2
1084 | 932 | 746.1 | 543.8 | 741.8 | 707.2 | 678.4
1085 | 933 | 745.9 | 542.5 | 751.4 | 706.5 | 677.8
1086 | 934 | 745.6 | 546.9 | 760.9 | 708.2 | 680.5
1087 | 935 | 745.5 | 548.5 | 740.3 | 707.1 | 679.3
1088 | 936 | 744.9 | 544.7 | 729.7 | 705.3 | 676.5
1089 | 937 | 743.9 | 545.9 | 720.6 | 704.8 | 675.5
1090 | 938 | 742.9 | 548.9 | 729.9 | 706.3 | 677.4
1091 | 939 | 742 | 545.3 | 729.9 | 705.1 | 675.7
1092 | 940 | 741.3 | 541.3 | 714 | 702 | 672.4
1093 | 941 | 740.6 | 538.7 | 706.7 | 699.8 | 670.5
1094 | 942 | 739.9 | 539.3 | 723.2 | 699.9 | 672.4
1095 | 943 | 739.1 | 541 | 737.5 | 701.4 | 673.7
1096 | 944 | 738.4 | 541.8 | 745.7 | 702.2 | 674.9
1097 | 945 | 737.6 | 542.8 | 762.2 | 703.3 | 677.3
1098 | 946 | 736.9 | 552.6 | 772.7 | 707.2 | 682.9
1099 | 947 | 736.1 | 558.7 | 766.7 | 709.7 | 683.7
1100 | 948 | 735.1 | 557.6 | 743.7 | 708.4 | 679.9
1101 | 949 | 734.2 | 554.7 | 711.7 | 705.5 | 675.9
1102 | 950 | 733.3 | 553.5 | 705 | 703.4 | 674.2
1103 | 951 | 732.5 | 558.6 | 705.9 | 703.8 | 674.2
1104 | 952 | 731.8 | 559.8 | 709.5 | 704.1 | 674.1
1105 | 953 | 731.3 | 559 | 703.5 | 704.4 | 673.1
1106 | 954 | 730.6 | 559.1 | 702.2 | 704.4 | 672.5
1107 | 955 | 730 | 555.8 | 687.6 | 701.8 | 668.6
1108 | 956 | 729.4 | 550.9 | 665.4 | 698.5 | 665.3
1109 | 957 | 728.7 | 547.9 | 650.3 | 696 | 662
1110 | 958 | 728 | 545.6 | 656.4 | 694.6 | 660.6
1111 | 959 | 727.3 | 543.1 | 656.3 | 693.3 | 659.2
1112 | 960 | 726.6 | 538.4 | 662.5 | 691.2 | 657.8
1113 | 961 | 726.1 | 535.6 | 684.9 | 689.6 | 657.6
1114 | 962 | 725.7 | 536.5 | 709.7 | 690.2 | 659.8
1115 | 963 | 725.3 | 537.2 | 705.7 | 689.9 | 658.8
1116 | 964 | 724.8 | 535.1 | 710.5 | 689.2 | 658.7
1117 | 965 | 724.3 | 540.2 | 719.8 | 691 | 662.1
1118 | 966 | 723.8 | 543.8 | 728.3 | 692.6 | 664.2
1119 | 967 | 723.2 | 543.8 | 738.5 | 693 | 664.5
1120 | 968 | 722.7 | 543.4 | 725.8 | 692.8 | 662.5
1121 | 969 | 722.1 | 543.4 | 717.6 | 692.4 | 661.9
1122 | 970 | 721.4 | 543 | 711.6 | 692.3 | 661.7
1123 | 971 | 720.8 | 539.3 | 706.9 | 691.1 | 660.2
1124 | 972 | 720.1 | 539.9 | 701.1 | 690.5 | 659.1
1125 | 973 | 719.5 | 543.3 | 703.3 | 691.2 | 659
1126 | 974 | 719 | 542.6 | 722.1 | 693 | 660.9
1127 | 975 | 718.5 | 544.6 | 727.7 | 693.5 | 662.7
1128 | 976 | 718.3 | 548.6 | 733.2 | 695.5 | 665.1
1129 | 977 | 717.8 | 549 | 723.7 | 695.3 | 663.7
1130 | 978 | 717.5 | 551 | 717.1 | 696.1 | 663.5
1131 | 979 | 717 | 550.6 | 714 | 696.5 | 662.4
1132 | 980 | 716.4 | 554.8 | 703.5 | 698 | 662.9
1133 | 981 | 715.9 | 558.6 | 704 | 700.1 | 663.9
1134 | 982 | 715.5 | 560 | 697.7 | 700.9 | 664.5
1135 | 983 | 715 | 560.4 | 705.6 | 700.7 | 664
1136 | 984 | 714.8 | 561.3 | 718.5 | 701 | 665.4
1137 | 985 | 714.6 | 559.7 | 713 | 699.8 | 663.8
1138 | 986 | 714.2 | 555.5 | 696.1 | 697.7 | 660.6
1139 | 987 | 714 | 550.4 | 704.3 | 695.8 | 660.2
1140 | 988 | 713.7 | 548.3 | 690.7 | 694 | 657.9
1141 | 989 | 713.4 | 543.6 | 670.5 | 691.1 | 654.2
1142 | 990 | 713 | 538.9 | 661.2 | 688.5 | 651.9
1143 | 991 | 712.6 | 539.4 | 674.5 | 688.4 | 653.1
1144 | 992 | 712.3 | 541.9 | 678.9 | 689.2 | 652.1
1145 | 993 | 712 | 544.1 | 691.7 | 690.2 | 652.5
1146 | 994 | 711.6 | 539.7 | 668.5 | 687.8 | 648.6
1147 | 995 | 711.1 | 537.7 | 648 | 685.7 | 645.2
1148 | 996 | 710.5 | 534.3 | 628.8 | 683.4 | 642.2
1149 | 997 | 709.7 | 530.5 | 634.3 | 681.8 | 640.3
1150 | 998 | 709.1 | 532.1 | 658.1 | 682 | 641.3
1151 | 999 | 708.5 | 534.3 | 649 | 682.1 | 640
1152 | 1000 | 707.7 | 533.2 | 626.5 | 680 | 637.2
1153 | 1001 | 706.9 | 536.4 | 623.1 | 678.9 | 637.4
1154 | 1002 | 706.1 | 543.7 | 615.8 | 680.2 | 637.9
1155 | 1003 | 705.3 | 547.8 | 612.5 | 680.7 | 637.2
1156 | 1004 | 704.4 | 546.8 | 602.7 | 680.1 | 635.1
1157 | 1005 | 703.5 | 541 | 597.1 | 677.5 | 632.3
1158 | 1006 | 702.7 | 543 | 629.2 | 677.7 | 635.7
1159 | 1007 | 702.2 | 547.2 | 663.5 | 680.9 | 641.7
1160 | 1008 | 701.9 | 552 | 692.5 | 685.6 | 647.4
1161 | 1009 | 701.8 | 554.8 | 693.2 | 687.8 | 648
1162 | 1010 | 701.4 | 559.6 | 677.4 | 688.5 | 648.4
1163 | 1011 | 701.3 | 570.9 | 673.3 | 690.8 | 653.3
1164 | 1012 | 701.6 | 582.2 | 695.6 | 695.5 | 658.4
1165 | 1013 | 701.9 | 590.8 | 723.4 | 699.4 | 663
1166 | 1014 | 702.4 | 599.1 | 744.4 | 704.2 | 668.5
1167 | 1015 | 702.9 | 599.3 | 762.7 | 707.3 | 672.4
1168 | 1016 | 703.3 | 593 | 772.6 | 706.9 | 671.5
1169 | 1017 | 703.8 | 585.8 | 760.8 | 705.5 | 669.8
1170 | 1018 | 704.4 | 584.8 | 758.3 | 706.3 | 671.4
1171 | 1019 | 704.9 | 590.8 | 751.4 | 708.3 | 673.9
1172 | 1020 | 705.4 | 589.2 | 749.5 | 708.8 | 672.5
1173 | 1021 | 705.8 | 589.9 | 747.4 | 708.7 | 674.4
1174 | 1022 | 706.4 | 584.2 | 736.2 | 707.1 | 671.6
1175 | 1023 | 706.7 | 574 | 706.5 | 703 | 666.9
1176 | 1024 | 707 | 567.5 | 710.6 | 700.4 | 664.9
1177 | 1025 | 707.2 | 566.6 | 719.1 | 700 | 664.4
1178 | 1026 | 707.6 | 564.6 | 711.9 | 698.4 | 662.5
1179 | 1027 | 707.8 | 560.6 | 700.2 | 695.7 | 659.2
1180 | 1028 | 708 | 557.7 | 718.3 | 694.4 | 659.1
1181 | 1029 | 708.4 | 556.4 | 731.1 | 694.7 | 659.2
1182 | 1030 | 708.7 | 557.3 | 752.6 | 696.4 | 660.6
1183 | 1031 | 709.1 | 559.3 | 764.5 | 697.7 | 664.2
1184 | 1032 | 709.4 | 563.3 | 766.3 | 699.9 | 666.7
1185 | 1033 | 709.6 | 567.4 | 758.1 | 702.6 | 666.5
1186 | 1034 | 709.8 | 567.2 | 758.3 | 703.6 | 666
1187 | 1035 | 710.1 | 566.7 | 764.2 | 704.2 | 665.8
1188 | 1036 | 710.4 | 566.8 | 779.9 | 705.7 | 667.7
1189 | 1037 | 710.9 | 566.1 | 773.1 | 705.3 | 667.5
1190 | 1038 | 711.1 | 560.9 | 753.4 | 702.2 | 664.9
1191 | 1039 | 711.3 | 557.8 | 741.1 | 699.8 | 662.8
1192 | 1040 | 711.3 | 555.9 | 727.5 | 697.8 | 661.1
1193 | 1041 | 711.2 | 551.4 | 726.6 | 695.5 | 659.6
1194 | 1042 | 711.3 | 556.2 | 748.6 | 698.4 | 665.4
1195 | 1043 | 711.5 | 554 | 751.7 | 699 | 665.7
1196 | 1044 | 711.6 | 553.5 | 762.4 | 699.7 | 666.3
1197 | 1045 | 711.8 | 553.8 | 767.5 | 700.2 | 667.3
1198 | 1046 | 711.9 | 554.6 | 774.7 | 701.1 | 667.8
1199 | 1047 | 712.3 | 560.5 | 788.9 | 705 | 671.3
1200 | 1048 | 713.3 | 571.9 | 802.8 | 710.9 | 677.6
1201 | 1049 | 714.1 | 582.4 | 808.5 | 716.9 | 683.1
1202 | 1050 | 714.8 | 587.3 | 807.7 | 720.8 | 686.5
1203 | 1051 | 715.2 | 582.7 | 771.6 | 718.1 | 681.3
1204 | 1052 | 715.2 | 573.8 | 747.7 | 713.1 | 677
1205 | 1053 | 715.5 | 571 | 743.7 | 710.9 | 675.9
1206 | 1054 | 715.9 | 568.1 | 734.4 | 708.3 | 673.5
1207 | 1055 | 716 | 564 | 723.1 | 706 | 671.3
1208 | 1056 | 716.1 | 563.6 | 718.9 | 705.1 | 671.4
1209 | 1057 | 716 | 567.9 | 730.9 | 706.9 | 673.2
1210 | 1058 | 716.2 | 568.4 | 748.1 | 708.5 | 674.3
1211 | 1059 | 716.4 | 562.7 | 743.8 | 706.1 | 671.7
1212 | 1060 | 716.5 | 556.4 | 711.9 | 702.1 | 667.6
1213 | 1061 | 716.3 | 551 | 693.2 | 697.3 | 664.7
1214 | 1062 | 716.1 | 547.2 | 692.3 | 694.2 | 662.6
1215 | 1063 | 716 | 549.2 | 718.4 | 695.7 | 665.7
1216 | 1064 | 715.9 | 550 | 731.6 | 697.1 | 667.1
1217 | 1065 | 715.7 | 552.9 | 744.7 | 698.8 | 668.8
1218 | 1066 | 715.7 | 556.1 | 752.6 | 700.4 | 670
1219 | 1067 | 715.6 | 560.3 | 767.6 | 703.1 | 673.2
1220 | 1068 | 715.7 | 560.6 | 784.7 | 704.4 | 675.9
1221 | 1069 | 715.8 | 562.8 | 790.7 | 705.2 | 677
1222 | 1070 | 715.9 | 561.7 | 780.4 | 704 | 675.9
1223 | 1071 | 716 | 559.9 | 761.1 | 702.3 | 673.4
1224 | 1072 | 716 | 561.3 | 764.9 | 703.5 | 674.3
1225 | 1073 | 716.1 | 562.8 | 772.8 | 706.3 | 676
1226 | 1074 | 716.6 | 566.8 | 783.9 | 709.6 | 680.1
1227 | 1075 | 716.9 | 567.6 | 777.3 | 710 | 679.4
1228 | 1076 | 717 | 561.2 | 755.1 | 706.6 | 675.5
1229 | 1077 | 717.1 | 557.4 | 756.8 | 704.6 | 675
1230 | 1078 | 717.1 | 553.9 | 748.3 | 701.7 | 672.8
1231 | 1079 | 717.2 | 555.6 | 765.9 | 701.5 | 674.7
1232 | 1080 | 717.3 | 554.7 | 765.8 | 701 | 673.8
1233 | 1081 | 717.4 | 554.5 | 759.7 | 700.5 | 672.8
1234 | 1082 | 717.1 | 549.3 | 740 | 698.1 | 669.3
1235 | 1083 | 716.8 | 547 | 726.8 | 695.8 | 667.2
1236 | 1084 | 716.6 | 550.5 | 747.1 | 697.5 | 670
1237 | 1085 | 716.5 | 558.1 | 756.1 | 701.4 | 673.9
1238 | 1086 | 716.4 | 559.3 | 775.8 | 702.3 | 674.6
1239 | 1087 | 716.5 | 558 | 786.7 | 701.1 | 674.4
1240 | 1088 | 716.9 | 559.5 | 791.1 | 701.5 | 676.3
1241 | 1089 | 717.1 | 557.3 | 784 | 700.9 | 675
1242 | 1090 | 717.3 | 555 | 789.1 | 700.1 | 673.8
1243 | 1091 | 717.8 | 555.7 | 801.9 | 702 | 677.3
1244 | 1092 | 718.5 | 564.9 | 807.9 | 706.4 | 682.2
1245 | 1093 | 719.4 | 573.3 | 818.5 | 710.7 | 686.4
1246 | 1094 | 720.2 | 575.2 | 825.2 | 712 | 687.7
1247 | 1095 | 720.8 | 573.1 | 815.5 | 711.5 | 686.2
1248 | 1096 | 721.3 | 566.9 | 807.4 | 709 | 683.9
1249 | 1097 | 722.1 | 564.7 | 817.9 | 708.3 | 684.2
1250 | 1098 | 722.9 | 562.7 | 812.6 | 707.8 | 685.9
1251 | 1099 | 723.4 | 556.7 | 787.6 | 704.5 | 681.3
1252 | 1100 | 723.7 | 551.3 | 764.9 | 700.9 | 678.8
1253 | 1101 | 724 | 549.6 | 772.3 | 699 | 679.3
1254 | 1102 | 724.4 | 552.8 | 796.2 | 700.9 | 684
1255 | 1103 | 724.5 | 559.8 | 796.8 | 703.4 | 686.2
1256 | 1104 | 724.8 | 564.8 | 810.1 | 706.3 | 689.4
1257 | 1105 | 725.2 | 563.4 | 810.8 | 707.5 | 689.8
1258 | 1106 | 725.6 | 561.6 | 815.8 | 707.4 | 690.2
1259 | 1107 | 726 | 560.2 | 817.3 | 707.1 | 689.8
1260 | 1108 | 726.6 | 560.9 | 822.6 | 706.7 | 690.6
1261 | 1109 | 727 | 560.5 | 797 | 705.3 | 688.8
1262 | 1110 | 727.1 | 554.1 | 767.4 | 701.5 | 683.6
1263 | 1111 | 726.7 | 549 | 743.9 | 698 | 680.7
1264 | 1112 | 726 | 542 | 720.8 | 693.9 | 676.9
1265 | 1113 | 725.3 | 538.3 | 716 | 690.8 | 674.3
1266 | 1114 | 724.6 | 537.1 | 716.1 | 688.8 | 672.8
1267 | 1115 | 723.9 | 535.6 | 718.9 | 686.3 | 671.2
1268 | 1116 | 723.1 | 534.7 | 725.8 | 684.3 | 670.2
1269 | 1117 | 722.2 | 533.9 | 738.5 | 682.8 | 669.1
1270 | 1118 | 721.6 | 535.2 | 769 | 683.9 | 671.3
1271 | 1119 | 721.2 | 535.1 | 782.4 | 684.6 | 673.4
1272 | 1120 | 720.7 | 534.4 | 787 | 684.6 | 675.2
1273 | 1121 | 720.3 | 534.2 | 799 | 684.6 | 676.7
1274 | 1122 | 720.3 | 540 | 813.2 | 687.6 | 680.4
1275 | 1123 | 720.2 | 540.8 | 818.4 | 688.3 | 681.9
1276 | 1124 | 720.4 | 546.7 | 828.8 | 691.9 | 686.4
1277 | 1125 | 720.4 | 550 | 834.1 | 695.3 | 689.2
1278 | 1126 | 720.6 | 552.5 | 840.2 | 697.7 | 692.1
1279 | 1127 | 720.8 | 553.4 | 843.9 | 698.7 | 694.3
1280 | 1128 | 721 | 553.7 | 842.1 | 698.3 | 695
1281 | 1129 | 721.6 | 556.3 | 838.5 | 698.9 | 696.7
1282 | 1130 | 722.1 | 561.6 | 841.1 | 701.2 | 699.1
1283 | 1131 | 722.9 | 570.7 | 843.8 | 706 | 703.1
1284 | 1132 | 723.6 | 580.4 | 847.3 | 711.6 | 706.4
1285 | 1133 | 724.2 | 584.5 | 847.8 | 715 | 708.7
1286 | 1134 | 724.9 | 593.8 | 847.2 | 718.7 | 712.9
1287 | 1135 | 725.7 | 600.7 | 846.5 | 723 | 715.4
1288 | 1136 | 726.5 | 600 | 843.3 | 725.2 | 716.6
1289 | 1137 | 727.3 | 598.3 | 843.1 | 725.4 | 716.5
1290 | 1138 | 728.2 | 595.3 | 841.5 | 724.6 | 715.8
1291 | 1139 | 729 | 589.4 | 820.4 | 721.8 | 712.4
1292 | 1140 | 729.6 | 585.6 | 811.7 | 720 | 709
1293 | 1141 | 730 | 579.4 | 787.2 | 717 | 706.2
1294 | 1142 | 730.1 | 574.7 | 763.4 | 714.3 | 702.6
1295 | 1143 | 730.2 | 577.1 | 770.5 | 714.9 | 703.3
1296 | 1144 | 730.6 | 581 | 788.4 | 718 | 706.9
1297 | 1145 | 731 | 580.1 | 786.9 | 718.9 | 704.5
1298 | 1146 | 731.2 | 577.5 | 792.4 | 717.9 | 704
1299 | 1147 | 731.7 | 583 | 805.8 | 720.5 | 708.5
1300 | 1148 | 732.6 | 591.6 | 814.1 | 725.8 | 713.1
1301 | 1149 | 733.2 | 592.6 | 809.5 | 727.3 | 712
1302 | 1150 | 733.6 | 592 | 811.4 | 727.9 | 711.3
1303 | 1151 | 734.5 | 592.8 | 817.8 | 730 | 712.9
1304 | 1152 | 735.5 | 589.8 | 828 | 730.3 | 713.8
1305 | 1153 | 736.2 | 585.7 | 813.7 | 727.8 | 710.6
1306 | 1154 | 736.9 | 581.3 | 806.4 | 725.3 | 709.5
1307 | 1155 | 737.4 | 578.3 | 805.1 | 722.8 | 708.6
1308 | 1156 | 738 | 575.2 | 803.2 | 720.1 | 707.9
1309 | 1157 | 738.3 | 571.5 | 786.4 | 717.1 | 705
1310 | 1158 | 738.2 | 566.6 | 762.8 | 713.4 | 700.8
1311 | 1159 | 737.8 | 561.3 | 740.5 | 709.5 | 696.7
1312 | 1160 | 737.3 | 558 | 741 | 707.4 | 694.4
1313 | 1161 | 737 | 561.1 | 763.7 | 709.5 | 696.1
1314 | 1162 | 737.2 | 568.2 | 786.7 | 713.6 | 700.8
1315 | 1163 | 737.4 | 568.4 | 796.1 | 715.2 | 700.2
1316 | 1164 | 737.8 | 577.3 | 806.7 | 718.8 | 704.2
1317 | 1165 | 737.9 | 578.4 | 815.1 | 720.3 | 705.9
1318 | 1166 | 737.8 | 574.4 | 808.5 | 718.4 | 703.9
1319 | 1167 | 737.5 | 572.2 | 797.2 | 716 | 703.6
1320 | 1168 | 737.4 | 573.9 | 809 | 716.7 | 704.9
1321 | 1169 | 737.2 | 575.3 | 802.5 | 717.4 | 703.8
1322 | 1170 | 736.7 | 574.4 | 787.5 | 716.7 | 701.8
1323 | 1171 | 736.2 | 570.3 | 773 | 713.4 | 700.1
1324 | 1172 | 735.6 | 564.7 | 758.9 | 709.4 | 695.8
1325 | 1173 | 735 | 561.8 | 749.9 | 706.9 | 694.3
1326 | 1174 | 734.8 | 563.7 | 771.6 | 707.5 | 696.1
1327 | 1175 | 735.2 | 567.7 | 788.7 | 710.2 | 698.4
1328 | 1176 | 735.2 | 570.6 | 797.1 | 712.7 | 699
1329 | 1177 | 735.1 | 569.4 | 793 | 713.4 | 697.9
1330 | 1178 | 734.9 | 563.7 | 783.9 | 712.3 | 695.6
1331 | 1179 | 735 | 564.2 | 785 | 712.8 | 697.5
1332 | 1180 | 735.3 | 562.5 | 790.8 | 712.7 | 698
1333 | 1181 | 735.2 | 560.6 | 780.2 | 711.1 | 694.9
1334 | 1182 | 735 | 559.1 | 772.3 | 708.6 | 692.3
1335 | 1183 | 734.7 | 558.2 | 768.8 | 706.4 | 691.9
1336 | 1184 | 734.3 | 557.9 | 754.3 | 705.2 | 689.8
1337 | 1185 | 733.7 | 558.6 | 761.1 | 704.9 | 691
1338 | 1186 | 733.1 | 559.2 | 769.2 | 705.2 | 691.2
1339 | 1187 | 732.7 | 558.6 | 765.4 | 705.3 | 689.9
1340 | 1188 | 732.2 | 558.2 | 746.4 | 704.7 | 688.6
1341 | 1189 | 731.4 | 556.4 | 718.9 | 702.3 | 684.7
1342 | 1190 | 730.6 | 556 | 719.1 | 700.1 | 683.8
1343 | 1191 | 730.2 | 555.6 | 721.1 | 699 | 683
1344 | 1192 | 728.7 | 554 | 711.7 | 697.2 | 680.2
1345 | 1193 | 727.9 | 555 | 728.8 | 697.9 | 681.2
1346 | 1194 | 727.7 | 561.4 | 761.3 | 701.7 | 686.5
1347 | 1195 | 727.9 | 566.5 | 774.5 | 704.9 | 689.8
1348 | 1196 | 727.5 | 566.9 | 744 | 704.3 | 686.4
1349 | 1197 | 726.8 | 563.5 | 730.5 | 701.3 | 683.3
1350 | 1198 | 726.5 | 569.2 | 747.1 | 703.5 | 686
1351 | 1199 | 727 | 578.4 | 777.7 | 708.2 | 690.1
1352 | 1200 | 727.3 | 578.1 | 763.7 | 709.8 | 688.9
1353 | 1201 | 726.8 | 572.9 | 740.8 | 707.4 | 685.6
1354 | 1202 | 726.1 | 568.7 | 725.5 | 704.3 | 683.5
1355 | 1203 | 725.3 | 562 | 712.1 | 700.3 | 680.6
1356 | 1204 | 724.5 | 560.1 | 721.9 | 699 | 680
1357 | 1205 | 724.9 | 573.7 | 754.8 | 704.3 | 687.2
1358 | 1206 | 725.4 | 587.4 | 751 | 709.9 | 691
1359 | 1207 | 725.5 | 597.8 | 767.4 | 714 | 693.6
1360 | 1208 | 726.1 | 603.3 | 788.2 | 718.4 | 698
1361 | 1209 | 726.8 | 603.9 | 804.4 | 720.9 | 699.8
1362 | 1210 | 727.4 | 606.3 | 809.1 | 723.7 | 702.7
1363 | 1211 | 728.1 | 612.5 | 805.7 | 726.9 | 705.8
1364 | 1212 | 728.6 | 614.8 | 811.2 | 729.7 | 708.1
1365 | 1213 | 729.4 | 623.8 | 818.8 | 733.1 | 711.6
1366 | 1214 | 731 | 632.6 | 815.8 | 736.7 | 715.1
1367 | 1215 | 732.2 | 625.4 | 820.2 | 737.6 | 713.4
1368 | 1216 | 733.4 | 619.5 | 823 | 736.2 | 712.7
1369 | 1217 | 735 | 611.9 | 811.2 | 734 | 709.4
1370 | 1218 | 734.9 | 605.1 | 790.7 | 730.1 | 706.7
1371 | 1219 | 735.7 | 603.8 | 802.4 | 729.4 | 709.1
1372 | 1220 | 737.2 | 613.7 | 817.4 | 733.4 | 714.1
1373 | 1221 | 738.3 | 622.8 | 825 | 736.8 | 717
1374 | 1222 | 739.2 | 624.6 | 828.6 | 738.1 | 719.2
1375 | 1223 | 745.7 | 618.7 | 837.2 | 730.1 | 721.1
1376 | 1224 | 741.7 | 623.7 | 842.4 | 741.8 | 723.2
1377 | 1225 | 742.5 | 616.6 | 831.4 | 739 | 721.5
1378 | 1226 | 743.3 | 613.7 | 833.6 | 737.9 | 720.6
1379 | 1227 | 744.1 | 612.3 | 841.4 | 738.3 | 721.7
1380 | 1228 | 745 | 611.5 | 836.4 | 739.7 | 722.3
1381 | 1229 | 746 | 606.8 | 832.6 | 739 | 722.6
1382 | 1230 | 746.8 | 606.2 | 841.1 | 738.7 | 723.7
1383 | 1231 | 747.6 | 605.8 | 851.3 | 739.7 | 726.8
1384 | 1232 | 748.6 | 602.9 | 849.6 | 739.9 | 727.5
1385 | 1233 | 749.5 | 600.1 | 853 | 738.8 | 727.8
1386 | 1234 | 754.1 | 565.8 | 837.5 | 696.4 | 727.1
1387 | 1235 | 749.9 | 592.5 | 833.3 | 733.9 | 726.8
1388 | 1236 | 750.3 | 591.4 | 833.3 | 732.8 | 726.4
1389 | 1237 | 750.2 | 590.8 | 827.2 | 732.7 | 725.1
1390 | 1238 | 750.2 | 589.9 | 830.1 | 731.8 | 725.5
1391 | 1239 | 750.6 | 593.9 | 836.7 | 734 | 726.6
1392 | 1240 | 751.2 | 605.3 | 841.8 | 738.4 | 729.8
1393 | 1241 | 752.1 | 616.8 | 845.9 | 742 | 732.5
1394 | 1242 | 753 | 627.6 | 848.1 | 745.4 | 735.4
1395 | 1243 | 753.9 | 631.4 | 854.9 | 748.8 | 737.2
1396 | 1244 | 754.7 | 626.4 | 834.4 | 747.9 | 733.6
1397 | 1245 | 755.8 | 612.1 | 798.3 | 737.8 | 728.2
1398 | 1246 | 754.2 | 607.7 | 773.2 | 737.8 | 724.2
1399 | 1247 | 753.9 | 606.4 | 785.5 | 736.7 | 725.1
1400 | 1248 | 754 | 611.7 | 803.1 | 739.3 | 728.6
1401 | 1249 | 754.6 | 613.4 | 790.2 | 740.5 | 726.4
1402 | 1250 | 754.7 | 615.8 | 799.3 | 742.1 | 728.1
1403 | 1251 | 755.7 | 620.1 | 820.7 | 746.1 | 731.8
1404 | 1252 | 756.9 | 618 | 834.5 | 747.8 | 732.1
1405 | 1253 | 758 | 611.5 | 825.8 | 743.7 | 730.6
1406 | 1254 | 768.2 | 496.6 | 787.3 | 601.9 | 724.8
1407 | 1255 | 757.7 | 597.1 | 772.1 | 736.7 | 721.6
1408 | 1256 | 757.1 | 593 | 761.7 | 732.3 | 720.5
1409 | 1257 | 757.1 | 592.6 | 777.3 | 730.9 | 721.1
1410 | 1258 | 757.1 | 591.2 | 787.7 | 729.7 | 720.3
1411 | 1259 | 755.9 | 589.6 | 783.3 | 727.3 | 718
1412 | 1260 | 756.4 | 586.8 | 770.1 | 725.4 | 716.5
1413 | 1261 | 755.5 | 581.9 | 740.1 | 721.1 | 711.7
1414 | 1262 | 754.2 | 578.6 | 738.8 | 717.8 | 709.2
1415 | 1263 | 753.1 | 573.5 | 731.9 | 714.6 | 706
1416 | 1264 | 752.3 | 574.7 | 746.1 | 714.2 | 706.2
1417 | 1265 | 751.5 | 575.9 | 746.8 | 714.5 | 705.7
1418 | 1266 | 750.6 | 575.1 | 734.9 | 713.1 | 703.5
1419 | 1267 | 749.2 | 571.5 | 712.7 | 710.2 | 699.6
1420 | 1268 | 747.7 | 569.7 | 721.3 | 708.3 | 698
1421 | 1269 | 746.8 | 571.8 | 750.9 | 709.8 | 700.8
1422 | 1270 | 746.3 | 576.9 | 761.6 | 712.4 | 702.6
1423 | 1271 | 746 | 582.1 | 743.8 | 713.2 | 700.6
1424 | 1272 | 744.6 | 587.3 | 752.4 | 714.4 | 701.8
1425 | 1273 | 744.1 | 590.8 | 782.1 | 717.1 | 705.7
1426 | 1274 | 743.3 | 587.8 | 759.3 | 715.4 | 701.5
1427 | 1275 | 741.5 | 579.1 | 718.6 | 710.1 | 695.8
1428 | 1276 | 739.5 | 573.5 | 694.4 | 705.8 | 692
1429 | 1277 | 737.9 | 576 | 696.7 | 705.4 | 692.2
1430 | 1278 | 736.8 | 586.6 | 717.8 | 707.4 | 694.9
1431 | 1279 | 735.9 | 593.6 | 719.8 | 709.7 | 697.1
1432 | 1280 | 735.2 | 597.5 | 735.1 | 711.5 | 698.4
1433 | 1281 | 734.6 | 599.3 | 758.1 | 713.1 | 700.2
1434 | 1282 | 733.8 | 602.1 | 775.9 | 715 | 702.9
1435 | 1283 | 733.4 | 607.5 | 776.1 | 716.6 | 704
1436 | 1284 | 732.7 | 603.9 | 773.5 | 716.7 | 703
1437 | 1285 | 732.4 | 602.5 | 790.7 | 717.2 | 704.2
1438 | 1286 | 732.1 | 598.6 | 778.8 | 715.6 | 702.1
1439 | 1287 | 731.5 | 594.3 | 759 | 713.5 | 699.3
1440 | 1288 | 731 | 592.1 | 762.9 | 711.9 | 698.5
1441 | 1289 | 730.7 | 589.9 | 777.5 | 711.5 | 698.6
1442 | 1290 | 731 | 592.6 | 797.8 | 713 | 701.8
1443 | 1291 | 731.7 | 595 | 810.9 | 714.7 | 704.5
1444 | 1292 | 733 | 605.9 | 818.4 | 719.2 | 710.5
1445 | 1293 | 734.4 | 611.8 | 833.2 | 723.9 | 714.8
1446 | 1294 | 735.9 | 612.1 | 841.5 | 725.9 | 717.8
1447 | 1295 | 736.5 | 606.8 | 832.4 | 723.5 | 714.9
1448 | 1296 | 737 | 603.5 | 824.9 | 720.7 | 712.9
1449 | 1297 | 736.9 | 598.1 | 796.6 | 717.5 | 709.7
1450 | 1298 | 736.2 | 591.6 | 768.8 | 713.8 | 705.4
1451 | 1299 | 736 | 590.6 | 788.9 | 712.9 | 706.7
1452 | 1300 | 736.1 | 591.2 | 784.6 | 713.3 | 705.9
1453 | 1301 | 735.7 | 587.2 | 756.8 | 710 | 701.1
1454 | 1302 | 734.5 | 582 | 722.7 | 705.4 | 696.2
1455 | 1303 | 733.2 | 576.9 | 703 | 702.1 | 692.5
1456 | 1304 | 732.2 | 576.6 | 720.8 | 701.7 | 692.3
1457 | 1305 | 731.9 | 578.3 | 750.4 | 703.3 | 695.6
1458 | 1306 | 731.3 | 575.8 | 751.6 | 702.2 | 693.2
1459 | 1307 | 730.5 | 571 | 730.7 | 699.7 | 689.8
1460 | 1308 | 729.4 | 572.2 | 723.5 | 698.8 | 689.4
1461 | 1309 | 728.8 | 579.6 | 747.4 | 701.9 | 692.2
1462 | 1310 | 728.8 | 586.2 | 759.2 | 705.1 | 695
1463 | 1311 | 728.4 | 582 | 751.3 | 703.9 | 691.7
1464 | 1312 | 727.7 | 581 | 752 | 701.8 | 690.2
1465 | 1313 | 726.9 | 581.9 | 750 | 701.2 | 689.6
1466 | 1314 | 725.8 | 579.6 | 744.6 | 699.8 | 687.6
1467 | 1315 | 725.6 | 587.2 | 764.4 | 703 | 692
1468 | 1316 | 725.5 | 590.1 | 768.7 | 705.7 | 694.3
1469 | 1317 | 725.8 | 592.7 | 785.8 | 709.1 | 697.1
1470 | 1318 | 726.1 | 592.1 | 794.5 | 710.5 | 697.9
1471 | 1319 | 726.1 | 591.6 | 794.6 | 710.8 | 698.2
1472 | 1320 | 726.2 | 596.7 | 790.6 | 712.4 | 699.6
1473 | 1321 | 726.6 | 595.4 | 800.9 | 712.4 | 700.6
1474 | 1322 | 727.2 | 594 | 816.7 | 712.8 | 701.8
1475 | 1323 | 727.8 | 593.3 | 823 | 712.5 | 702.7
1476 | 1324 | 728.4 | 596.1 | 820.3 | 713.6 | 704.8
1477 | 1325 | 728.3 | 591.9 | 793.9 | 711.3 | 701.6
1478 | 1326 | 728 | 592.8 | 779.3 | 710.8 | 700.7
1479 | 1327 | 727.7 | 598.3 | 763.8 | 711.7 | 701.7
1480 | 1328 | 727.1 | 604.6 | 750.3 | 712 | 701.3
1481 | 1329 | 726.8 | 613.5 | 740.3 | 712.7 | 702.4
1482 | 1330 | 727 | 623.8 | 750 | 715.8 | 706.6
1483 | 1331 | 727.3 | 631.8 | 759.8 | 719.2 | 710.6
1484 | 1332 | 728.2 | 636 | 783.5 | 721.8 | 713.8
1485 | 1333 | 729.5 | 634.8 | 794.8 | 723.8 | 715.4
1486 | 1334 | 730.1 | 633 | 809.2 | 725.4 | 717.3
1487 | 1335 | 731.4 | 636.4 | 823.9 | 728.6 | 721.7
1488 | 1336 | 732.7 | 641.1 | 828.2 | 731.6 | 725.7
1489 | 1337 | 734 | 645.2 | 828.8 | 734.6 | 728.2
1490 | 1338 | 735.4 | 648 | 836.2 | 737.1 | 730.9
1491 | 1339 | 736.8 | 651.2 | 839.3 | 739.4 | 733.7
1492 | 1340 | 738.4 | 651.6 | 848.7 | 741.9 | 736.9
1493 | 1341 | 740.1 | 652.6 | 849.7 | 744.3 | 738.7
1494 | 1342 | 741.6 | 647 | 851.5 | 743.4 | 737.2
1495.1 | 1343.1 | 743.2 | 643.8 | 852 | 742.5 | 739.3
1496.1 | 1344.1 | 744.3 | 639.7 | 835.5 | 741.1 | 736.8
1497.1 | 1345.1 | 745.1 | 639.5 | 828.6 | 741.6 | 737.8
1498.1 | 1346.1 | 746.4 | 648.8 | 828.8 | 743.6 | 741.3
1499.1 | 1347.1 | 758.7 | 638.8 | 831.4 | 731.1 | 741.8
1500.1 | 1348.1 | 748.6 | 642.1 | 829.9 | 744.2 | 740.3
1501.1 | 1349.1 | 749.3 | 635.6 | 825.9 | 741.6 | 737.4
1502.1 | 1350.1 | 749.8 | 630.9 | 806.3 | 739.1 | 735.1
1503.1 | 1351.1 | 750.2 | 626.9 | 790.7 | 736.3 | 732.2
1504.1 | 1352.1 | 750.4 | 622.3 | 792.3 | 733.8 | 731.2
1505.1 | 1353.1 | 751.3 | 620.8 | 808.3 | 733.2 | 733.2
1506.1 | 1354.1 | 752 | 617.9 | 815.2 | 732.4 | 732.7
1507.1 | 1355.1 | 753.1 | 619.2 | 827.3 | 733.9 | 735.2
1508.1 | 1356.1 | 754.2 | 622.1 | 832.4 | 735.8 | 736.7
1509.1 | 1357.1 | 755.2 | 622.7 | 839.5 | 736.8 | 737.7
1510.1 | 1358.1 | 755.9 | 621 | 839 | 736.2 | 737.3
1511.1 | 1359.1 | 756.2 | 617.8 | 821.2 | 734 | 734.1
1512.1 | 1360.1 | 756.5 | 615 | 817.9 | 731.9 | 734.2
1513.1 | 1361.1 | 757.3 | 617.1 | 828.5 | 732.6 | 736.8
1514.1 | 1362.1 | 758.1 | 616.2 | 832.9 | 732.8 | 737.7
1515.1 | 1363.1 | 758.4 | 612.8 | 821.2 | 730.5 | 735.5
1516.1 | 1364.1 | 758.3 | 607.8 | 799.5 | 727.2 | 730.9
1517.1 | 1365.1 | 757.2 | 601.8 | 773.2 | 723.4 | 726.6
1518.1 | 1366.1 | 756 | 594.7 | 757.5 | 719.8 | 723.2
1519.1 | 1367.1 | 754.8 | 587.7 | 741.2 | 717.1 | 719.4
1520.1 | 1368.1 | 754.1 | 589.6 | 760.3 | 718.1 | 720.7
1521.1 | 1369.1 | 754 | 591.6 | 785 | 719.9 | 722.8
1522.1 | 1370.1 | 754.4 | 594.5 | 797.6 | 721.3 | 724.4
1523.1 | 1371.1 | 754.6 | 593.1 | 801.2 | 720.3 | 722.5
1524.1 | 1372.1 | 754.1 | 587.6 | 771.8 | 717 | 717.7
1525.1 | 1373.1 | 752.3 | 584.3 | 740.1 | 713.1 | 713.7
1526.1 | 1374.1 | 751.4 | 589.8 | 757 | 714 | 715.9
1527.1 | 1375.1 | 748.5 | 591.4 | 781.4 | 711.8 | 717.6
1528.1 | 1376.1 | 748.7 | 596.1 | 791.4 | 714.7 | 717.1
1529.1 | 1377.1 | 749.9 | 593.2 | 764.2 | 712.4 | 712.8
1530.1 | 1378.1 | 748.6 | 588.3 | 739.1 | 708.6 | 708.6
1531.1 | 1379.1 | 747.6 | 587.3 | 748.5 | 707.4 | 708.4
1532.1 | 1380.1 | 747 | 592 | 738.7 | 707.8 | 708
1533.1 | 1381.1 | 747.4 | 591.9 | 744.9 | 707.6 | 709.4
1534.1 | 1382.1 | 747.3 | 590.1 | 741.5 | 705.4 | 706.3
1535.1 | 1383.1 | 747.1 | 589.1 | 754.2 | 704.4 | 706.4
1536.1 | 1384.1 | 746.2 | 589.4 | 752.8 | 703.4 | 704.7
1537.1 | 1385.1 | 745.5 | 587.7 | 744.2 | 701.4 | 702.6
1538.1 | 1386.1 | 744.2 | 587.7 | 734.2 | 699.2 | 701.3
1539.1 | 1387.1 | 743.4 | 588.3 | 740.4 | 698.8 | 701
1540.1 | 1388.1 | 741.8 | 587.8 | 731.8 | 698.2 | 699.9
1541.1 | 1389.1 | 739.5 | 586.2 | 710 | 696.1 | 697.4
1542.1 | 1390.1 | 736.4 | 585.7 | 702.1 | 694.4 | 695.2
1543.1 | 1391.1 | 735 | 586.6 | 724.5 | 694.4 | 696.8
1544.1 | 1392.1 | 733.7 | 596 | 729.1 | 697.3 | 701.1
1545.1 | 1393.1 | 732.9 | 602.1 | 750.9 | 700.3 | 705.7
1546.1 | 1394.1 | 732.7 | 602.2 | 761.4 | 701.3 | 706.1
1547.1 | 1395.1 | 732.9 | 601 | 776.3 | 701.6 | 707.3
1548.1 | 1396.1 | 732.7 | 598.9 | 767.6 | 700.1 | 704.5
1549.1 | 1397.1 | 732.1 | 596.2 | 751.7 | 697.7 | 702.5
1550.1 | 1398.1 | 731.8 | 601.4 | 763.2 | 698.5 | 705
1551.1 | 1399.1 | 731.4 | 598.6 | 764.7 | 698.2 | 703.8
1552.1 | 1400.1 | 730.7 | 597.2 | 757.6 | 696.9 | 703
1553.1 | 1401.1 | 729.1 | 590.8 | 715.1 | 692 | 696.6
1554.1 | 1402.1 | 726.6 | 581.6 | 674.4 | 687.3 | 690.1
1555.1 | 1403.1 | 723.6 | 573.8 | 637.8 | 682.5 | 684.2
1556.1 | 1404.1 | 720.7 | 566.2 | 607.2 | 678.8 | 678
1557.1 | 1405.1 | 728.1 | 522.5 | 584.3 | 627.2 | 672.2
1558.1 | 1406.1 | 714.1 | 551.5 | 555.4 | 670.1 | 666.4
1559.1 | 1407.1 | 710.2 | 544.4 | 532.6 | 665.5 | 660.9
1560.1 | 1408.1 | 706.2 | 538.4 | 514.2 | 661.2 | 655.7
1561.1 | 1409.1 | 702.8 | 533.2 | 496 | 656.9 | 650.3
1562.1 | 1410.1 | 696.7 | 526.1 | 479.8 | 649.7 | 645.1
1563.1 | 1411.1 | 696.8 | 522.9 | 467.4 | 648.6 | 640.3
1564.1 | 1412.1 | 693.5 | 518.2 | 454.8 | 645.2 | 635.5
1565.1 | 1413.1 | 689.5 | 514.4 | 442.4 | 642.1 | 630.7
1566.1 | 1414.1 | 686.3 | 509.8 | 430.4 | 638.6 | 626
1567.1 | 1415.1 | 682.5 | 505.5 | 421.9 | 634.8 | 622
1568.1 | 1416.1 | 678.6 | 500.9 | 414.4 | 630.7 | 617.6
1569.1 | 1417.1 | 675.1 | 497.3 | 405.2 | 627.2 | 613.1
1570.1 | 1418.1 | 671.4 | 494 | 396.1 | 623.6 | 609.2
1571.1 | 1419.1 | 667.8 | 491.4 | 387.7 | 619.8 | 605.2
1572.1 | 1420.1 | 664.2 | 487.7 | 381.6 | 616.8 | 601.1
1573.1 | 1421.1 | 661 | 484.4 | 373.8 | 613.2 | 597.1
1574.1 | 1422.1 | 657.7 | 480.4 | 368.9 | 608.4 | 593.5
1575.1 | 1423.1 | 655.2 | 478.1 | 362.3 | 606.3 | 589.8
1576.1 | 1424.1 | 651.9 | 474.7 | 355.6 | 603.5 | 586.1
1577.1 | 1425.1 | 648.5 | 471.9 | 352 | 600 | 582.9
1578.1 | 1426.1 | 645.2 | 469.6 | 346.5 | 596.7 | 579.6
1579.1 | 1427.1 | 641.9 | 466.5 | 343.2 | 593.5 | 576
1580.1 | 1428.1 | 638.7 | 464.5 | 340.1 | 590.1 | 572.9
1581.1 | 1429.1 | 635.8 | 461.9 | 333.7 | 587.1 | 569.3
1582.1 | 1430.1 | 632.9 | 459.8 | 330.2 | 584.2 | 566
1583.1 | 1431.1 | 629.7 | 457.4 | 326.3 | 581.8 | 562.6
1584.1 | 1432.1 | 626.6 | 454.4 | 321.1 | 579 | 559.3
1585.1 | 1433.1 | 623.6 | 451 | 318.7 | 576.2 | 556.4
1586.1 | 1434.1 | 620.5 | 448.8 | 314.2 | 573.1 | 553.5
1587.1 | 1435.1 | 617.5 | 446.6 | 310.8 | 570.4 | 550.8
1588.1 | 1436.1 | 614.6 | 443.3 | 307.1 | 568 | 547.7
1589.1 | 1437.1 | 611.6 | 439.9 | 305.9 | 565.3 | 545
1590.1 | 1438.1 | 608.5 | 437.5 | 301.4 | 563.1 | 542.4
1591.1 | 1439.1 | 605.6 | 435 | 297.4 | 561.2 | 539.5
1592.1 | 1440.1 | 602.8 | 432.8 | 293.7 | 558.9 | 536.7
1593.1 | 1441.1 | 600 | 431.1 | 290.9 | 556.8 | 534.5
1594.1 | 1442.1 | 597.2 | 429.3 | 287.6 | 554.1 | 532.2
1595.1 | 1443.1 | 594.4 | 426.9 | 284.5 | 551.7 | 529.4
1596.1 | 1444.1 | 591.6 | 425.3 | 282.1 | 550.4 | 527
1597.1 | 1445.1 | 588.9 | 423.1 | 279.4 | 548.9 | 524.9
1598.1 | 1446.1 | 586.2 | 420.1 | 276.6 | 546.8 | 522.5
1599.1 | 1447.1 | 583.6 | 416 | 273.3 | 544.3 | 519.9
1600.1 | 1448.1 | 581 | 413.1 | 270.8 | 541.6 | 517.4
1601.1 | 1449.1 | 578.3 | 411.3 | 269 | 538.9 | 514.6
1602.1 | 1450.1 | 575.8 | 409.1 | 267.5 | 536.3 | 512.2
1603.1 | 1451.1 | 573.2 | 407.7 | 265.7 | 533.4 | 509.8
1604.1 | 1452.1 | 570.6 | 406.8 | 264.8 | 530.5 | 507.8
1605.1 | 1453.1 | 568 | 404 | 263 | 528.3 | 505.3
1606.1 | 1454.1 | 565.4 | 401.8 | 260.3 | 526.5 | 503.5
1607.1 | 1455.1 | 563 | 399.1 | 258.1 | 524.7 | 501.3
1608.1 | 1456.1 | 560.7 | 395.7 | 255.6 | 523.3 | 499.2
1609.1 | 1457.1 | 558.4 | 392.1 | 253.7 | 521.5 | 497.4
1610.1 | 1458.1 | 556.1 | 389.7 | 252.2 | 520 | 495.2
1611.1 | 1459.1 | 553.8 | 388 | 250.4 | 518.1 | 493.2
1612.1 | 1460.1 | 551.5 | 385.9 | 248.2 | 516.6 | 491.4
1613.1 | 1461.1 | 549.2 | 383.9 | 246.1 | 515.5 | 489.9
1614.1 | 1462.1 | 547 | 381.4 | 243.8 | 513.4 | 487.8
1615.1 | 1463.1 | 544.8 | 379 | 241.4 | 512.1 | 485.4
1616.1 | 1464.1 | 542.5 | 376.8 | 240.8 | 511.2 | 484.3
1617.1 | 1465.1 | 540.3 | 375.1 | 239.9 | 509.9 | 482.6
1618.1 | 1466.1 | 538.3 | 373.7 | 238.4 | 508.3 | 480.5
1619.1 | 1467.1 | 536.3 | 370.4 | 236.8 | 506.7 | 478.7
1620.1 | 1468.1 | 534.1 | 369.2 | 234.8 | 505.5 | 476.9
1621.1 | 1469.1 | 531.9 | 367.6 | 232.8 | 504.2 | 475.3
1622.1 | 1470.1 | 529.9 | 364.4 | 231.4 | 502.2 | 473.4
1623.1 | 1471.1 | 527.9 | 362.3 | 229.9 | 500 | 470.8
1624.1 | 1472.1 | 525.8 | 359.4 | 228.3 | 497.7 | 468.3
1625.1 | 1473.1 | 523.7 | 356.9 | 226.5 | 495.3 | 466.6
1626.1 | 1474.1 | 521.7 | 355.9 | 225.8 | 492.7 | 464.7
1627.1 | 1475.1 | 519.6 | 355.8 | 224.9 | 490.7 | 462.6
1628.1 | 1476.1 | 517.5 | 353.6 | 224.8 | 489.1 | 460.5
1629.1 | 1477.1 | 515.7 | 351.2 | 224.3 | 487.1 | 459.1
1630.1 | 1478.1 | 513.7 | 350.6 | 223.5 | 485.5 | 457.3
1631.1 | 1479.1 | 511.7 | 348.8 | 222.3 | 484 | 455.9
1632.1 | 1480.1 | 509.6 | 347.1 | 222 | 482.7 | 454.4
1633.1 | 1481.1 | 507.6 | 344.8 | 220.4 | 481.5 | 453
1634.1 | 1482.1 | 505.7 | 343.2 | 218.8 | 480.1 | 451.3
1635.1 | 1483.1 | 503.8 | 342 | 217.7 | 478.3 | 449.7
1636.1 | 1484.1 | 501.9 | 341.5 | 217.4 | 476.7 | 447.8
1637.1 | 1485.1 | 500.1 | 339.9 | 216.8 | 474.8 | 446.3
1638.1 | 1486.1 | 498.5 | 337 | 215.4 | 472.6 | 444.6
1639.1 | 1487.1 | 496.7 | 335.7 | 214.1 | 470.6 | 442.8
1640.1 | 1488.1 | 495 | 334.8 | 212.7 | 468.7 | 440.9
1641.1 | 1489.1 | 493 | 333.8 | 211.1 | 467.5 | 439.4
1642.1 | 1490.1 | 491.2 | 331.1 | 210 | 465.9 | 437.6
1643.1 | 1491.1 | 489.4 | 330.5 | 208.6 | 464.4 | 436
1644.1 | 1492.1 | 487.7 | 328.6 | 208.3 | 463.6 | 434.9
1645.1 | 1493.1 | 486.2 | 327.3 | 207.5 | 462.3 | 433.5
1646.1 | 1494.1 | 484.7 | 325.4 | 206.7 | 460.8 | 431.9
1647.1 | 1495.1 | 483 | 323.3 | 205.8 | 459.5 | 430.2
1648.1 | 1496.1 | 481.4 | 320.4 | 203.3 | 458.2 | 429
1649.1 | 1497.1 | 479.9 | 319 | 201.7 | 457.2 | 427.9
1650.1 | 1498.1 | 478.3 | 317.7 | 200.8 | 455.4 | 426.2
1651.1 | 1499.1 | 476.8 | 318.5 | 200.2 | 453.5 | 424.5
1652.1 | 1500.1 | 475.3 | 317.8 | 199.2 | 451.4 | 422.8
1653.1 | 1501.1 | 473.8 | 316.6 | 197.9 | 449.2 | 421.2
1654.1 | 1502.1 | 472.2 | 314.6 | 196.1 | 447.3 | 419.6
1655.1 | 1503.1 | 470.7 | 313.1 | 194.9 | 445.2 | 417.8
1656.1 | 1504.1 | 469.3 | 311.4 | 194.4 | 443.7 | 416.5
1657.1 | 1505.1 | 467.8 | 309.9 | 193.9 | 442.2 | 414.9
1658.1 | 1506.1 | 466.3 | 310.6 | 193.1 | 441 | 413.6
1659.1 | 1507.1 | 464.7 | 309.6 | 192.7 | 440 | 412.6
1660.1 | 1508.1 | 463.2 | 308.4 | 192.9 | 439 | 411.2
1661.1 | 1509.1 | 461.6 | 307 | 192.1 | 438 | 409.5
1662.1 | 1510.1 | 460.1 | 305.4 | 190.8 | 436.2 | 408.2
1663.1 | 1511.1 | 458.7 | 304.9 | 190.6 | 435.3 | 407.1
1664.1 | 1512.1 | 457.3 | 304.2 | 191.9 | 434.6 | 406.1
1665.1 | 1513.1 | 455.8 | 302.9 | 191.8 | 433.9 | 404.9
1666.1 | 1514.1 | 454.4 | 301.1 | 190.4 | 432.8 | 403.3
1667.1 | 1515.1 | 453.2 | 299.6 | 189 | 431.2 | 401.9
1668.1 | 1516.1 | 451.9 | 299.7 | 187.8 | 429.6 | 400.4
1669.1 | 1517.1 | 450.6 | 299.6 | 186.5 | 428.2 | 398.9
1670.1 | 1518.1 | 449.1 | 298.9 | 185.8 | 426.5 | 397.5
1671.1 | 1519.1 | 447.7 | 298.6 | 185.1 | 425.2 | 395.9
1672.1 | 1520.1 | 446.1 | 298.5 | 184.1 | 423.9 | 394.9
1673.1 | 1521.1 | 444.7 | 296.9 | 184.1 | 422.7 | 393.7
1674.1 | 1522.1 | 443.4 | 296.1 | 184.6 | 422 | 392.7
1675.1 | 1523.1 | 442.1 | 294.8 | 184.6 | 421.1 | 391.3
1676.1 | 1524.1 | 440.7 | 294.1 | 183.4 | 419.8 | 389.9
1677.1 | 1525.1 | 439.4 | 293.8 | 182.1 | 418.3 | 388.7
1678.1 | 1526.1 | 438.1 | 291.9 | 181.2 | 417 | 387.4
1679.1 | 1527.1 | 436.8 | 290.8 | 180.3 | 414.9 | 386
1680.1 | 1528.1 | 435.5 | 290.7 | 179.9 | 413.1 | 384.7
1681.1 | 1529.1 | 434.2 | 290.5 | 179.7 | 411.6 | 383.4
1682.1 | 1530.1 | 432.9 | 290.7 | 179.3 | 409.8 | 381.9
1683.1 | 1531.1 | 431.5 | 290 | 178.9 | 407.9 | 380.5
1684.1 | 1532.1 | 430.3 | 289 | 177.5 | 406.1 | 378.8
1685.1 | 1533.1 | 428.9 | 288.7 | 176.7 | 404.3 | 377.3
1686.1 | 1534.1 | 427.7 | 288.9 | 176.2 | 402.8 | 375.8
1687.1 | 1535.1 | 426.4 | 288.5 | 176.3 | 401.5 | 374.5
1688.1 | 1536.1 | 425.4 | 287.8 | 177.3 | 399.9 | 373.4
1689.1 | 1537.1 | 424.1 | 287.8 | 177.6 | 398.4 | 372.1
1690.1 | 1538.1 | 422.8 | 287.1 | 177.6 | 396.9 | 371
1691.1 | 1539.1 | 421.6 | 287.4 | 176.8 | 395.4 | 369.8
1692.1 | 1540.1 | 420.3 | 285.5 | 175.7 | 393.9 | 368.5
1693.1 | 1541.1 | 419 | 285.5 | 175.1 | 393.3 | 367.7
1694.1 | 1542.1 | 417.8 | 285.3 | 173.7 | 392.5 | 366.7
1695.1 | 1543.1 | 416.4 | 285.2 | 172 | 391.7 | 365.3
1696.1 | 1544.1 | 415.1 | 284.3 | 170.7 | 390.3 | 364
1697.1 | 1545.1 | 413.9 | 281.7 | 169.6 | 389.2 | 362.7
1698.1 | 1546.1 | 412.6 | 280.6 | 168.6 | 388.7 | 361.8
1699.1 | 1547.1 | 411.3 | 279.8 | 167.7 | 388.4 | 361
1700.1 | 1548.1 | 409.9 | 278.7 | 167.3 | 388 | 360.3
1701.1 | 1549.1 | 408.6 | 277.2 | 166.7 | 387.1 | 359.7
1702.1 | 1550.1 | 407.4 | 277.5 | 165.6 | 386.5 | 358.4
1703.1 | 1551.1 | 406.2 | 277 | 164.8 | 385.8 | 357.4
1704.1 | 1552.1 | 405.1 | 276.3 | 164.6 | 384.6 | 356.1
1705.1 | 1553.1 | 404 | 275.8 | 164 | 383.3 | 354.8
1706.1 | 1554.1 | 402.9 | 274.1 | 163.7 | 381.7 | 353.7
1707.1 | 1555.1 | 401.8 | 273.3 | 163.4 | 380.6 | 352.7
1708.1 | 1556.1 | 400.7 | 271.8 | 162.5 | 379.5 | 351.4
1709.1 | 1557.1 | 399.6 | 270.5 | 162.4 | 378.2 | 350
1710.1 | 1558.1 | 398.6 | 269.5 | 161.4 | 376.7 | 349.1
1711.1 | 1559.1 | 397.5 | 269.2 | 160.2 | 375.4 | 348.1
1712.1 | 1560.1 | 396.3 | 268.5 | 159.3 | 374.2 | 346.8
1713.1 | 1561.1 | 395 | 266.8 | 158.5 | 372.8 | 345.6
1714.1 | 1562.1 | 393.9 | 266.4 | 157.4 | 371.5 | 344.4
1715.1 | 1563.1 | 392.8 | 266.2 | 156.8 | 370.7 | 343.2
1716.1 | 1564.1 | 391.7 | 265.6 | 156.8 | 369.9 | 342
1717.1 | 1565.1 | 390.6 | 265.4 | 156 | 368.9 | 341
1718.1 | 1566.1 | 389.5 | 265 | 155.2 | 368 | 339.8
1719.1 | 1567.1 | 388.3 | 263.6 | 154.9 | 367.2 | 338.8
1720.1 | 1568.1 | 387.2 | 262.2 | 154.5 | 366 | 337.7
1721.1 | 1569.1 | 386.1 | 262.1 | 154.3 | 364.9 | 336.6
1722.1 | 1570.1 | 385.1 | 262.4 | 154 | 364.2 | 335.8
1723.1 | 1571.1 | 384 | 262.3 | 154.1 | 363.6 | 334.8
1724.1 | 1572.1 | 382.9 | 261.6 | 153.6 | 362.4 | 333.6
1725.1 | 1573.1 | 382.1 | 260.6 | 153.2 | 361.3 | 332.5
1726.1 | 1574.1 | 381 | 261 | 152.8 | 360.5 | 331.3
1727.1 | 1575.1 | 380 | 260.3 | 152.3 | 359.4 | 330.3
1728.1 | 1576.1 | 379 | 260.6 | 151.5 | 358.6 | 329.2
1729.1 | 1577.1 | 378 | 260.9 | 150.7 | 357.8 | 328.1
1730.1 | 1578.1 | 377 | 260.6 | 150.6 | 356.6 | 327.1
1731.1 | 1579.1 | 376 | 259.2 | 150.3 | 355.5 | 326.4
1732.1 | 1580.1 | 374.9 | 258.5 | 150.2 | 354.8 | 325.8
1733.1 | 1581.1 | 373.9 | 258.6 | 149.7 | 354.2 | 325
1734.1 | 1582.1 | 372.8 | 257.3 | 149.9 | 353.4 | 323.8
1735.1 | 1583.1 | 371.8 | 256.3 | 149.2 | 352.5 | 322.8
1736.1 | 1584.1 | 370.7 | 256.9 | 149.6 | 351.9 | 322
1737.1 | 1585.1 | 369.7 | 256.3 | 149.1 | 351 | 321.6
1738.1 | 1586.1 | 368.8 | 254.1 | 148.3 | 349.6 | 320.6
1739.1 | 1587.1 | 367.8 | 254.5 | 148.2 | 348.6 | 319.3
1740.1 | 1588.1 | 366.8 | 254.6 | 147.7 | 347.6 | 318.2
1741.1 | 1589.1 | 365.8 | 254 | 147.1 | 346.5 | 317.4
1742.1 | 1590.1 | 364.8 | 251.7 | 146.1 | 345.1 | 316.2
1743.1 | 1591.1 | 363.8 | 250.6 | 145.6 | 343.9 | 315.5
1744.1 | 1592.1 | 362.8 | 250.8 | 145.2 | 343.1 | 314.6
1745.1 | 1593.1 | 361.9 | 250.8 | 144.9 | 342.3 | 313.8
1746.1 | 1594.1 | 361 | 248.5 | 144.6 | 341 | 312.9
1747.1 | 1595.1 | 360.1 | 248.1 | 144.4 | 340.2 | 312.2
1748.1 | 1596.1 | 359.2 | 246.7 | 144 | 339.1 | 311.3
1749.1 | 1597.1 | 358.2 | 246.6 | 143.3 | 338.3 | 310.2
1750.1 | 1598.1 | 357.3 | 245.7 | 143.1 | 337.3 | 309.4
1751.1 | 1599.1 | 356.3 | 245.2 | 142.6 | 336.6 | 308.7
1752.1 | 1600.1 | 355.4 | 244.6 | 142.6 | 336 | 308.1
1753.1 | 1601.1 | 354.4 | 244.2 | 142 | 335.2 | 307.3
1754.1 | 1602.1 | 353.5 | 243.6 | 142.2 | 334.5 | 306.5
1755.1 | 1603.1 | 352.6 | 242.9 | 141.7 | 333.9 | 305.9
1756.1 | 1604.1 | 351.6 | 243.1 | 141.1 | 333.2 | 305.3
1757.1 | 1605.1 | 350.6 | 241.2 | 141.4 | 332.6 | 304.8
1758.1 | 1606.1 | 349.7 | 240.3 | 141.3 | 332 | 304.2
1759.1 | 1607.1 | 348.9 | 238.7 | 141 | 331.4 | 303.8
1760.1 | 1608.1 | 348 | 237.7 | 140.7 | 330.8 | 302.8
1761.1 | 1609.1 | 347.1 | 236.3 | 140 | 329.8 | 301.8
1762.1 | 1610.1 | 346.3 | 236.4 | 140.3 | 328.8 | 301
1763.1 | 1611.1 | 345.5 | 235.3 | 140.3 | 327.8 | 300.2
1764.1 | 1612.1 | 344.5 | 234.7 | 139.9 | 326.9 | 299.3
1765.1 | 1613.1 | 343.6 | 233.6 | 139.6 | 326.3 | 298.5
1766.1 | 1614.1 | 342.6 | 232.5 | 139.2 | 325.7 | 297.5
1767.1 | 1615.1 | 341.7 | 232.2 | 138.8 | 325.1 | 297.1
1768.1 | 1616.1 | 340.8 | 230.9 | 138.8 | 324.2 | 296.1
1769.1 | 1617.1 | 339.9 | 229.3 | 139 | 323.5 | 295.4
1770.1 | 1618.1 | 339.1 | 228.1 | 138.5 | 322.9 | 294.5
1771.1 | 1619.1 | 338.3 | 227.1 | 137.3 | 322.1 | 293.8
1772.1 | 1620.1 | 337.4 | 226.1 | 136.5 | 321.4 | 293
1773.1 | 1621.1 | 336.5 | 224.6 | 136.8 | 320.9 | 292.8
1774.1 | 1622.1 | 335.6 | 223 | 136.8 | 320.2 | 291.9
1775.1 | 1623.1 | 334.7 | 221.3 | 136.2 | 319.2 | 291
1776.1 | 1624.1 | 333.9 | 220.6 | 135.4 | 318.2 | 290.2
1777.1 | 1625.1 | 333 | 220.2 | 135.3 | 317.3 | 289.6
1778.1 | 1626.1 | 332.3 | 219.9 | 135.6 | 316.2 | 288.6
1779.1 | 1627.1 | 331.5 | 218.7 | 135.2 | 314.9 | 287.7
1780.1 | 1628.1 | 330.7 | 218.4 | 134.4 | 313.9 | 286.9
1781.1 | 1629.1 | 329.9 | 218.8 | 134.1 | 313 | 286.3
1782.1 | 1630.1 | 329.1 | 218.6 | 133.5 | 312 | 285.3
1783.1 | 1631.1 | 328.3 | 218.2 | 132.8 | 310.9 | 284.5
1784.1 | 1632.1 | 327.3 | 217.6 | 132.4 | 309.7 | 283.5
1785.1 | 1633.1 | 326.5 | 216.8 | 132.3 | 308.7 | 282.7
1786.1 | 1634.1 | 325.6 | 215.8 | 131.7 | 307.9 | 282
1787.1 | 1635.1 | 324.9 | 215.2 | 131.5 | 306.8 | 281.2
1788.1 | 1636.1 | 324.2 | 214.3 | 130.8 | 305.9 | 280.5
1789.1 | 1637.1 | 323.2 | 214.4 | 130.2 | 305.3 | 280.3
1790.1 | 1638.1 | 322.3 | 214.3 | 129.7 | 304.6 | 279.4
1791.1 | 1639.1 | 321.5 | 214.4 | 129.3 | 303.9 | 278.6
1792.1 | 1640.1 | 320.5 | 214.1 | 129.1 | 303.1 | 278.2
1793.1 | 1641.1 | 319.7 | 214 | 128.6 | 302.3 | 277.3
1794.1 | 1642.1 | 319 | 213.4 | 128.7 | 301.6 | 276.7
1795.1 | 1643.1 | 318.1 | 211.9 | 128.4 | 300.6 | 275.9
1796.1 | 1644.1 | 317.3 | 211.4 | 127.9 | 299.6 | 275.3
1797.1 | 1645.1 | 316.5 | 210 | 127.8 | 298.6 | 274.5
1798.1 | 1646.1 | 315.8 | 209.4 | 127.8 | 297.9 | 273.9
1799.1 | 1647.1 | 315.1 | 209.6 | 127.3 | 297.1 | 273.3
1800.1 | 1648.1 | 314.2 | 210.2 | 126.7 | 296.1 | 272.5
1801.1 | 1649.1 | 313.6 | 209.9 | 126 | 295.3 | 271.6
1802.1 | 1650.1 | 312.8 | 209.6 | 125.8 | 294.7 | 271
1803.1 | 1651.1 | 312 | 209.6 | 126.2 | 294.3 | 270.6
1804.1 | 1652.1 | 311.3 | 210 | 126.1 | 293.9 | 270
1805.1 | 1653.1 | 310.5 | 210 | 125.6 | 293.1 | 269.2
1806.1 | 1654.1 | 309.8 | 210.1 | 124.8 | 292.3 | 268.3
1807.1 | 1655.1 | 309.2 | 210.1 | 124.5 | 291.7 | 267.8
1808.1 | 1656.1 | 308.5 | 209.1 | 124.3 | 290.9 | 266.9
1809.1 | 1657.1 | 307.7 | 208 | 123.8 | 290.1 | 266.2
1810.1 | 1658.1 | 307.1 | 207.9 | 123.7 | 289.5 | 265.8
1811.1 | 1659.1 | 306.4 | 207.2 | 123.1 | 289 | 265
1812.1 | 1660.1 | 305.6 | 206.9 | 122.8 | 288.5 | 264.3
1813.1 | 1661.1 | 305 | 205.3 | 122.6 | 288 | 263.6
1814.1 | 1662.1 | 304.4 | 204.8 | 122.9 | 287.5 | 263.2
1815.1 | 1663.1 | 303.8 | 204.1 | 122.3 | 286.7 | 262.5
1816.1 | 1664.1 | 303.1 | 203.4 | 121.9 | 286.2 | 262.1
1817.1 | 1665.1 | 302.5 | 202.7 | 121.7 | 285.6 | 261.5
1818.1 | 1666.1 | 301.8 | 202.3 | 121.1 | 284.7 | 260.6
1819.1 | 1667.1 | 301.1 | 201.7 | 120.3 | 284.1 | 260.1
1820.1 | 1668.1 | 300.5 | 200.9 | 119.8 | 283.5 | 259.4
1821.1 | 1669.1 | 299.8 | 199.8 | 120.1 | 283.1 | 259.1
1822.1 | 1670.1 | 299.2 | 199.4 | 119.4 | 282.6 | 258.7
1823.1 | 1671.1 | 298.5 | 199.5 | 118.9 | 282.3 | 258.1
1824.1 | 1672.1 | 297.8 | 199.3 | 118.6 | 282 | 257.8
1825.1 | 1673.1 | 297.1 | 198.9 | 119.2 | 281.7 | 257.6

## Test Facts
Last row in IRMS data sheets: | 12
Time when Penlight power was initiated: | 162