## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 1, Location G
Test conditions: Cable: Bundle of 12, 7-conductor, 12 AWG, XLPE insulated, CSPE jacketed Rockbestos Firewall III control cables (Item 10). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, E, H & L [See Elect. Conn. Map]), a second bundle of 12 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position G in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 200 kW heat release rate, increased to ~350 kW during test run. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Two cable bundle temperatures (see thermocouple map), air temperatures above and below the cable bundle, and the cable tray rung temperature. Gas burner initiated: Following 632 seconds of baseline data monitoring. Special Note: Data for conductor L12 was not collected during this test run.
DAQ Time | Burner Time | Event | Interpretation
632 | 0 | Ignited Gas Burner
1180 | 548 | Conductors B4 & C5 short together at less than 100 ohms (76) | Evidence of cable-to-cable shorting (B & C)
1354 | 722 | Conductor E7 shorts to ground at less than 100 ohms (12) | Cable E is partially shorted to ground
1446-1477 | 814-845 | Conductors A2 & B4 short to ground at less than 100 ohms (3 & 1) | Cables A & B are partially shorted to ground
1617 | 985 | Conductor B3 shorts to ground at less than 100 ohms (2) | Cable B shorted to ground
2190 | 1558 | Conductors A1 & C5 short together at less than 100 ohms (84) | Evidence of cable-to-cable shorting (A & C)
2255-2257 | 1623-1625 | Conductors H9 & H10 short to ground at less than 100 ohms (23 & 5) | Cable H shorted to ground
2308-2328 | 1676-1696 | Conductors E7 & E8 short together (6); conductors H9 & H10 short together (22) | Cables E & H are shorted internally
2336 | 1704 | Conductors A1 & A2 short together at less than 1000 ohms (315) | Cable A shorts internally
2389 | 1757 | Conductors B3 & B4 short together at less than 100 ohms (70) | Cable B shorts internally
2408-2414 | 1776-1782 | Conductors C5, C6 & L11 all short to ground at less than 100 ohms (<1, 5 & 3) | Cables C & L short to ground
2431 | 1799 | Conductors C5 & C6 short together at less than 100 ohms (2) | Cable C shorts internally
2434 | 1802 | Conductor E8 shorts to ground at less than 100 ohms (4) | Cable E is shorted to ground
2490 | 1858 | The existing short between conductors A1 & A2 decreases to less than 100 ohms (13)
2502 | 1870 | Conductor A1 shorts to ground at less than 100 ohms (10) | Cable A shorted to ground
3307 | 2675 | Extinguished Gas Burner
Additional Observations
Observation 1 | This test showed evidence of two cases of cable-to-cable shorting.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
All Cables = XLPE, 7/C (Item 10)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| G1 | = | Center of bundle
| G2 | = | One layer into bundle
| G3 | = | Air above bundle
| G4 | = | Air below bundle

## Elect Conn Map
Electrical connection map within the cables
All Cables = XLPE, item #10
Tray rung under D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 1 |  |  | 2006-10-19 | 9:13
XLPE | 7-C | Tray G
0 | 200 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A1-H9 | Burner Time | A1-H10 | Burner Time | A1-L11 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | A2-H9 | Burner Time | A2-H10 | Burner Time | A2-L11 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-E7 | Burner Time | B3-E8 | Burner Time | B3-H9 | Burner Time | B3-H10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-E7 | Burner Time | B4-E8 | Burner Time | B4-H9 | Burner Time | B4-H10 | Burner Time | C5-C6 | Burner Time | C5-E7 | Burner Time | C5-E8 | Burner Time | C5-L11 | Burner Time | C6-E7 | Burner Time | C6-E8 | Burner Time | C6-L11 | Burner Time | E7-E8 | Burner Time | H9-H10 | Burner Time | A-B MIN IR | Burner Time | A-C MIN IR | Burner Time | B-C MIN IR | Burner Time | B-D MIN IR | Burner Time | B-E MIN IR | Burner Time | D-E MIN IR | Burner Time | C-E MIN IR | Burner Time | C-F MIN IR | Burner Time | E-F MIN IR
-631.5 | 265237.9994 | -629 | 265137.9994 | -626 | 262937.9994 | -623 | 262837.9994 | -620.5 | 264837.9994 | -612 | 263737.9994 | -609 | 256937.9994 | -606.5 | 255137.9994 | -603.5 | 265337.9994 | -601 | 263637.9994 | -598 | 257437.9994 | -595.5 | 262237.9994 | -586.5 | 263537.9994 | -584 | 261837.9994 | -581 | 260637.9994 | -578.5 | 264637.9994 | -575.5 | 259837.9994 | -572.5 | 265437.9994 | -570 | 266137.9994 | -567 | 264937.9994 | -564.5 | 262337.9994 | -561.5 | 264137.9994 | -556 | 264837.9994 | -553 | 263037.9994 | -550.5 | 264737.9994 | -547.5 | 263037.9994 | -544.5 | 265537.9994 | -542 | 263637.9994 | -536.5 | 264037.9994 | -533.5 | 262537.9994 | -530.5 | 263837.9994 | -522.5 | 259637.9994 | -519.5 | 264237.9994 | -516.5 | 262337.9994 | -508.5 | 262237.9994 | -505.5 | 263337.9994 | -486 | 255537.9994 | -614.875 | 262937.9994 | -609.25 | 257437.9994 | -564.25 | 259837.9994 | -558.75 | 263037.9994 | -553.125 | 262337.9994 | #REF! | #REF! | -525 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
-477.5 | 265237.9994 | -474.5 | 265137.9994 | -472 | 262937.9994 | -470 | 262837.9994 | -466.5 | 264837.9994 | -458 | 263737.9994 | -455.5 | 256937.9994 | -452.5 | 255137.9994 | -449.5 | 265337.9994 | -446.5 | 263637.9994 | -444 | 257437.9994 | -441 | 262237.9994 | -433 | 263537.9994 | -430 | 261837.9994 | -427 | 260637.9994 | -424.5 | 264637.9994 | -421.5 | 259837.9994 | -419 | 265437.9994 | -416 | 266137.9994 | -413.5 | 264937.9994 | -410.5 | 262337.9994 | -407.5 | 264137.9994 | -402 | 264837.9994 | -399 | 263037.9994 | -396.5 | 264737.9994 | -393.5 | 263037.9994 | -391 | 265537.9994 | -388 | 263637.9994 | -382.5 | 264037.9994 | -379.5 | 262537.9994 | -377 | 263837.9994 | -368.5 | 259637.9994 | -365.5 | 264237.9994 | -362.5 | 262337.9994 | -354.5 | 262237.9994 | -351.5 | 263337.9994 | -332 | 255537.9994 | -460.625 | 262937.9994 | -455.375 | 257437.9994 | -410.375 | 259837.9994 | -404.875 | 263037.9994 | -399.25 | 262337.9994 | #REF! | #REF! | -371.125 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
-298 | 265237.9994 | -295.5 | 265137.9994 | -292.5 | 262937.9994 | -289.5 | 262837.9994 | -287 | 264837.9994 | -278.5 | 263737.9994 | -275.5 | 256937.9994 | -272.5 | 255137.9994 | -270 | 265337.9994 | -267.5 | 263637.9994 | -264.5 | 257437.9994 | -261.5 | 262237.9994 | -253.5 | 263537.9994 | -250.5 | 261837.9994 | -247.5 | 260637.9994 | -245 | 264637.9994 | -242 | 259837.9994 | -239.5 | 265437.9994 | -236.5 | 266137.9994 | -233.5 | 264937.9994 | -231 | 262337.9994 | -228 | 264137.9994 | -222.5 | 264837.9994 | -219.5 | 263037.9994 | -217 | 264737.9994 | -214 | 263037.9994 | -211.5 | 265537.9994 | -208.5 | 263637.9994 | -203 | 264037.9994 | -200 | 262537.9994 | -197.5 | 263837.9994 | -189 | 259637.9994 | -186 | 264237.9994 | -183.5 | 262337.9994 | -175 | 262237.9994 | -172 | 263337.9994 | -152.5 | 255537.9994 | -281.375 | 262937.9994 | -275.625 | 257437.9994 | -230.875 | 259837.9994 | -225.25 | 263037.9994 | -219.75 | 262337.9994 | #REF! | #REF! | -191.75 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
-144 | 265237.9994 | -141.5 | 265137.9994 | -138.5 | 262937.9994 | -135.5 | 262837.9994 | -133 | 264837.9994 | -124.5 | 263737.9994 | -121.5 | 256937.9994 | -119 | 255137.9994 | -116 | 265337.9994 | -113.5 | 263637.9994 | -110.5 | 257437.9994 | -107.5 | 262237.9994 | -99.5 | 263537.9994 | -96.5 | 261837.9994 | -93.5 | 260637.9994 | -91 | 264637.9994 | -88 | 259837.9994 | -85.5 | 265437.9994 | -82.5 | 266137.9994 | -79.5 | 264937.9994 | -77 | 262337.9994 | -74 | 264137.9994 | -68.5 | 264837.9994 | -65.5 | 263037.9994 | -63 | 264737.9994 | -60 | 263037.9994 | -57.5 | 265537.9994 | -54.5 | 263637.9994 | -49 | 264037.9994 | -46 | 262537.9994 | -43.5 | 263837.9994 | -35 | 259637.9994 | -32 | 264237.9994 | -29.5 | 262337.9994 | -21 | 262237.9994 | -18 | 263337.9994 | 1.5 | 255537.9994 | -127.375 | 262937.9994 | -121.625 | 257437.9994 | -76.875 | 259837.9994 | -71.25 | 263037.9994 | -65.75 | 262337.9994 | #REF! | #REF! | -37.75 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
10 | 265237.9994 | 12.5 | 265137.9994 | 15.5 | 262937.9994 | 18.5 | 262837.9994 | 21 | 264837.9994 | 29.5 | 263737.9994 | 32.5 | 256937.9994 | 35 | 255137.9994 | 38 | 265337.9994 | 40.5 | 263637.9994 | 43.5 | 257437.9994 | 46.5 | 262237.9994 | 54.5 | 263537.9994 | 57.5 | 261837.9994 | 60.5 | 260637.9994 | 63 | 264637.9994 | 66 | 259837.9994 | 68.5 | 265437.9994 | 71.5 | 266137.9994 | 74.5 | 264937.9994 | 77 | 262337.9994 | 80 | 264137.9994 | 85.5 | 264837.9994 | 88.5 | 263037.9994 | 91 | 264737.9994 | 94 | 263037.9994 | 96.5 | 265537.9994 | 99.5 | 263637.9994 | 105 | 264037.9994 | 108 | 262537.9994 | 110.5 | 263837.9994 | 119 | 259637.9994 | 122 | 264237.9994 | 124.5 | 262337.9994 | 133 | 262237.9994 | 136 | 263337.9994 | 155.5 | 255537.9994 | 26.625 | 262937.9994 | 32.375 | 257437.9994 | 77.125 | 259837.9994 | 82.75 | 263037.9994 | 88.25 | 262337.9994 | #REF! | #REF! | 116.25 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
164 | 265237.9994 | 166.5 | 265137.9994 | 169.5 | 262937.9994 | 172.5 | 262837.9994 | 175 | 264837.9994 | 183.5 | 263737.9994 | 186.5 | 256937.9994 | 189 | 255137.9994 | 192 | 265337.9994 | 194.5 | 263637.9994 | 197.5 | 257437.9994 | 200.5 | 262237.9994 | 208.5 | 263537.9994 | 211.5 | 261837.9994 | 214.5 | 260637.9994 | 217 | 264637.9994 | 220 | 259837.9994 | 222.5 | 265437.9994 | 225.5 | 266137.9994 | 228.5 | 264937.9994 | 231 | 262337.9994 | 234 | 264137.9994 | 239.5 | 264837.9994 | 242.5 | 263037.9994 | 245 | 264737.9994 | 248 | 263037.9994 | 250.5 | 265537.9994 | 253.5 | 263637.9994 | 259 | 264037.9994 | 262 | 262537.9994 | 264.5 | 263837.9994 | 273 | 259637.9994 | 276 | 264237.9994 | 278.5 | 262337.9994 | 287 | 262237.9994 | 290 | 263337.9994 | 309.5 | 255537.9994 | 180.625 | 262937.9994 | 186.375 | 257437.9994 | 231.125 | 259837.9994 | 236.75 | 263037.9994 | 242.25 | 262337.9994 | #REF! | #REF! | 270.25 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
318 | 265237.9994 | 320.5 | 265137.9994 | 323.5 | 262937.9994 | 326.5 | 262837.9994 | 329 | 264837.9994 | 337.5 | 263737.9994 | 340.5 | 256937.9994 | 343 | 255137.9994 | 346 | 265337.9994 | 348.5 | 263637.9994 | 351.5 | 257437.9994 | 354.5 | 262237.9994 | 362.5 | 263537.9994 | 365.5 | 261837.9994 | 368.5 | 260637.9994 | 371 | 264637.9994 | 374 | 259837.9994 | 376.5 | 265437.9994 | 379.5 | 266137.9994 | 382.5 | 264937.9994 | 385 | 262337.9994 | 388 | 264137.9994 | 393.5 | 264837.9994 | 396.5 | 263037.9994 | 399 | 264737.9994 | 402 | 263037.9994 | 404.5 | 265537.9994 | 407.5 | 263637.9994 | 413 | 264037.9994 | 416 | 262537.9994 | 418.5 | 263837.9994 | 427 | 259637.9994 | 429.5 | 264237.9994 | 432.5 | 262337.9994 | 441 | 262237.9994 | 444 | 263337.9994 | 463.5 | 255537.9994 | 334.625 | 262937.9994 | 340.375 | 257437.9994 | 385.125 | 259837.9994 | 390.75 | 263037.9994 | 396.25 | 262337.9994 | #REF! | #REF! | 424.125 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
472 | 265237.9994 | 474.5 | 265137.9994 | 477.5 | 262937.9994 | 480.5 | 262837.9994 | 483 | 264837.9994 | 491.5 | 263737.9994 | 494.5 | 256937.9994 | 497 | 255137.9994 | 499.5 | 265337.9994 | 502.5 | 263637.9994 | 505.5 | 257437.9994 | 508 | 262237.9994 | 516.5 | 263537.9994 | 519.5 | 261837.9994 | 522.5 | 260637.9994 | 525 | 264637.9994 | 528 | 259837.9994 | 530.5 | 265437.9994 | 533.5 | 266137.9994 | 536.5 | 264937.9994 | 539 | 262337.9994 | 542 | 264137.9994 | 547.5 | 75.8741 | 550.5 | 263037.9994 | 553 | 264737.9994 | 556 | 263037.9994 | 558.5 | 265537.9994 | 561.5 | 263637.9994 | 567 | 264037.9994 | 570 | 262537.9994 | 572.5 | 263837.9994 | 581 | 259637.9994 | 584 | 264237.9994 | 586.5 | 262337.9994 | 595 | 262237.9994 | 597.5 | 263337.9994 | 617.5 | 255537.9994 | 488.5 | 262937.9994 | 494.25 | 257437.9994 | 539.125 | 75.8741 | 544.75 | 263037.9994 | 550.25 | 262337.9994 | #REF! | #REF! | 578.25 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
625.5 | 265237.9994 | 628.5 | 265137.9994 | 631.5 | 262937.9994 | 634 | 262837.9994 | 637 | 264837.9994 | 645.5 | 263737.9994 | 648.5 | 256937.9994 | 651 | 255137.9994 | 653.5 | 265337.9994 | 656.5 | 263637.9994 | 659.5 | 257437.9994 | 662 | 262237.9994 | 670.5 | 263537.9994 | 673.5 | 261837.9994 | 676 | 260637.9994 | 679 | 264637.9994 | 682 | 259837.9994 | 684.5 | 265437.9994 | 687.5 | 266137.9994 | 690.5 | 264937.9994 | 693 | 262337.9994 | 696 | 264137.9994 | 701.5 | 21.7332 | 704 | 263037.9994 | 707 | 264737.9994 | 710 | 131468.9988 | 712.5 | 265537.9994 | 715.5 | 263637.9994 | 721 | 264037.9994 | 723.5 | 262537.9994 | 726.5 | 263837.9994 | 735 | 259637.9994 | 738 | 264237.9994 | 740.5 | 262337.9994 | 749 | 262237.9994 | 752 | 41722.1564 | 771 | 255537.9994 | 642.5 | 262937.9994 | 648.125 | 257437.9994 | 693 | 21.7332 | 698.75 | 131468.9988 | 704.25 | 262337.9994 | #REF! | #REF! | 732.125 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
780 | 265237.9994 | 782.5 | 265137.9994 | 785.5 | 262937.9994 | 788.5 | 262837.9994 | 791 | 264837.9994 | 799.5 | 263737.9994 | 802 | 256937.9994 | 805 | 255137.9994 | 807.5 | 61314.8918 | 810.5 | 263637.9994 | 813.5 | 7635.0342 | 816 | 55216.944 | 824.5 | 48119.7409 | 827.5 | 37923.5164 | 830.5 | 44503.837 | 833 | 264637.9994 | 835.5 | 259837.9994 | 838.5 | 265437.9994 | 841.5 | 266137.9994 | 844 | 264937.9994 | 847 | 262337.9994 | 850 | 264137.9994 | 855.5 | 35.4868 | 858 | 263037.9994 | 861 | 264737.9994 | 863.5 | 263037.9994 | 866.5 | 265537.9994 | 869.5 | 263637.9994 | 875 | 264037.9994 | 877.5 | 262537.9994 | 880.5 | 263837.9994 | 889 | 259637.9994 | 892 | 264237.9994 | 894.5 | 262337.9994 | 903 | 262237.9994 | 905.5 | 32425.6867 | 925.5 | 255537.9994 | 796.5 | 61314.8918 | 802.25 | 7635.0342 | 846.875 | 35.4868 | 852.5 | 263037.9994 | 858.25 | 262337.9994 | #REF! | #REF! | 886.125 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
933.5 | 265237.9994 | 936.5 | 265137.9994 | 939.5 | 262937.9994 | 942.5 | 262837.9994 | 945 | 264837.9994 | 953.5 | 263737.9994 | 956 | 256937.9994 | 959 | 255137.9994 | 962 | 40222.8409 | 964.5 | 263637.9994 | 967.5 | 29926.3753 | 970 | 42721.7088 | 978.5 | 63214.0133 | 981.5 | 1537.4128 | 984.5 | 44121.0719 | 987 | 264637.9994 | 989.5 | 7035.2924 | 992.5 | 41322.4324 | 995.5 | 21.5946 | 998 | 3936.5142 | 1001 | 14632.4223 | 1003.5 | 5835.7906 | 1009.5 | 30.3638 | 1012.5 | 263037.9994 | 1015 | 264737.9994 | 1017.5 | 263037.9994 | 1020.5 | 265537.9994 | 1023.5 | 263637.9994 | 1029 | 264037.9994 | 1031.5 | 262537.9994 | 1034.5 | 263837.9994 | 1043 | 259637.9994 | 1045.5 | 264237.9994 | 1048.5 | 262337.9994 | 1057 | 262237.9994 | 1059.5 | 39722.9156 | 1079.5 | 255537.9994 | 950.625 | 40222.8409 | 956.25 | 29926.3753 | 1001 | 30.3638 | 1006.5 | 21.5946 | 1012.125 | 5835.7906 | #REF! | #REF! | 1040 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
1087.5 | 265237.9994 | 1090.5 | 265137.9994 | 1093.5 | 262937.9994 | 1096 | 262837.9994 | 1099 | 264837.9994 | 1107.5 | 263737.9994 | 1110 | 256937.9994 | 1113 | 255137.9994 | 1115.5 | 31.2974 | 1118.5 | 131768.9988 | 1121.5 | 11333.5975 | 1124 | 21729.7137 | 1132.5 | 40022.8133 | 1135.5 | 41522.142 | 1138 | 1537.4101 | 1141 | 28427.2581 | 1144 | 9934.1768 | 1146.5 | 65013.5071 | 1149.5 | 17.9196 | 1152 | 62414.4419 | 1155 | 52218.0951 | 1158 | 57194.6769 | 1163.5 | 29.9847 | 1166 | 263037.9994 | 1169 | 264737.9994 | 1171.5 | 263037.9994 | 1174.5 | 265537.9994 | 1177.5 | 263637.9994 | 1183 | 264037.9994 | 1185.5 | 262537.9994 | 1188.5 | 263837.9994 | 1197 | 259637.9994 | 1199.5 | 264237.9994 | 1202.5 | 262337.9994 | 1211 | 262237.9994 | 1213.5 | 32525.6487 | 1233.5 | 255537.9994 | 1104.5 | 31.2974 | 1110.125 | 11333.5975 | 1155 | 29.9847 | 1160.5 | 17.9196 | 1166.25 | 52218.0951 | #REF! | #REF! | 1194 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
1241.5 | 265237.9994 | 1244.5 | 265137.9994 | 1247.5 | 262937.9994 | 1250 | 262837.9994 | 1253 | 264837.9994 | 1261.5 | 263737.9994 | 1264 | 256937.9994 | 1267 | 255137.9994 | 1269.5 | 26.9047 | 1272.5 | 263637.9994 | 1275.5 | 28726.8413 | 1278 | 61414.5806 | 1286.5 | 8834.6477 | 1289.5 | 56616.3773 | 1292 | 30126.4413 | 1295 | 12433.3018 | 1297.5 | 8734.6384 | 1300.5 | 49219.4573 | 1303.5 | 26.605 | 1306 | 47320.1392 | 1309 | 35510.917 | 1311.5 | 55117.1332 | 1317.5 | 71.8743 | 1320 | 263037.9994 | 1323 | 264737.9994 | 1325.5 | 263037.9994 | 1328.5 | 265537.9994 | 1331.5 | 263637.9994 | 1337 | 264037.9994 | 1339.5 | 262537.9994 | 1342.5 | 263837.9994 | 1351 | 259637.9994 | 1353.5 | 264237.9994 | 1356.5 | 262337.9994 | 1365 | 262237.9994 | 1367.5 | 56116.6902 | 1387.5 | 255537.9994 | 1258.5 | 26.9047 | 1264.125 | 28726.8413 | 1308.875 | 71.8743 | 1314.5 | 26.605 | 1320.125 | 35510.917 | #REF! | #REF! | 1348 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
1395.5 | 265237.9994 | 1398.5 | 265137.9994 | 1401.5 | 262937.9994 | 1404 | 262837.9994 | 1407 | 264837.9994 | 1415.5 | 263737.9994 | 1418 | 256738.0778 | 1421 | 255137.9994 | 1423.5 | 32.1034 | 1426.5 | 263637.9994 | 1429.5 | 3936.4709 | 1432 | 7835.0123 | 1440.5 | 13033.0546 | 1443.5 | 54417.2172 | 1446 | 10433.9967 | 1449 | 55417.0593 | 1451.5 | 8134.8693 | 1454.5 | 9034.5963 | 1457.5 | 3.3932 | 1460 | 4336.3633 | 1463 | 1537.414 | 1465.5 | 43821.4097 | 1471.5 | 50.4849 | 1474 | 263037.9994 | 1477 | 264737.9994 | 1479.5 | 263037.9994 | 1482.5 | 265537.9994 | 1485.5 | 263637.9994 | 1491 | 264037.9994 | 1493.5 | 262537.9994 | 1496.5 | 263837.9994 | 1505 | 86479.3315 | 1507.5 | 264237.9994 | 1510.5 | 262337.9994 | 1519 | 262237.9994 | 1521.5 | 62214.3747 | 1541.5 | 31655.1412 | 1412.5 | 32.1034 | 1418.125 | 3936.4709 | 1462.875 | 50.4849 | 1468.5 | 3.3932 | 1474.125 | 1537.414 | #REF! | #REF! | 1502 | 262337.9994 | #REF! | #REF! | #REF! | #REF!
1549.5 | 8126.9102 | 1552.5 | 10101.4457 | 1555.5 | 75.8138 | 1558 | 83.8793 | 1561 | 255441.548 | 1569.5 | 259339.6677 | 1572 | 252339.7896 | 1575 | 250139.959 | 1577.5 | 55.0395 | 1580.5 | 23.6137 | 1583.5 | 5901.4756 | 1586 | 262237.9994 | 1594.5 | 263537.9994 | 1597.5 | 261837.9994 | 1600 | 260637.9994 | 1603 | 4040.0475 | 1605.5 | 2911.9929 | 1608.5 | 265437.9994 | 1611.5 | 266137.9994 | 1614 | 264937.9994 | 1617 | 262337.9994 | 1619.5 | 264137.9994 | 1625.5 | 86.5307 | 1628 | 263037.9994 | 1631 | 264737.9994 | 1633.5 | 263037.9994 | 1636.5 | 265537.9994 | 1639.5 | 263637.9994 | 1645 | 65934.4976 | 1648 | 262537.9994 | 1650.5 | 131868.9988 | 1659 | 259637.9994 | 1661.5 | 264237.9994 | 1664.5 | 262337.9994 | 1674 | 262237.9994 | 1675.5 | 6.4768 | 1695.5 | 21.8124 | 1566.5 | 23.6137 | 1572.125 | 83.8793 | 1616.875 | 86.5307 | 1622.5 | 263037.9994 | 1628.125 | 262337.9994 | #REF! | #REF! | 1656.125 | 131868.9988 | #REF! | #REF! | #REF! | #REF!
1703.5 | 314.5549 | 1706.5 | 17206.3518 | 1709.5 | 38.9151 | 1712 | 60.4594 | 1715 | 15058.9084 | 1723.5 | 5284.4191 | 1726 | 256937.9994 | 1729 | 255137.9994 | 1731.5 | 84.1811 | 1734.5 | 62.3487 | 1737.5 | 23.6318 | 1740 | 3437.1865 | 1748.5 | 263537.9994 | 1751.5 | 261837.9994 | 1754 | 260637.9994 | 1757 | 70.1273 | 1759.5 | 37.8688 | 1762.5 | 57.1765 | 1765.5 | 266137.9994 | 1768 | 16464.8652 | 1771 | 262337.9994 | 1773.5 | 264137.9994 | 1779.5 | 75.2813 | 1782 | 45.1719 | 1785 | 10493.5047 | 1787.5 | 7639.3322 | 1790.5 | 34525.1841 | 1793.5 | 269.4637 | 1799 | 2.1919 | 1801.5 | 19.4253 | 1804.5 | 5.79 | 1812.5 | 0.82213 | 1815.5 | 3.5692 | 1818.5 | 29.2081 | 1827 | 22.7457 | 1829.5 | 23.6238 | 1849.5 | 17.2543 | 1720.5 | 38.9151 | 1726.125 | 23.6318 | 1770.875 | 37.8688 | 1776.5 | 7639.3322 | 1782.125 | 269.4637 | #REF! | #REF! | 1810 | 3.5692 | #REF! | #REF! | #REF! | #REF!
1857.5 | 31.2475 | 1860.5 | 21.0758 | 1863.5 | 21.2035 | 1866 | 14.8085 | 1868.5 | 20.4261 | 1877 | 16.099 | 1880 | 8.8943 | 1883 | 26.6562 | 1885.5 | 15.0282 | 1888.5 | 17.1756 | 1891 | 7.0797 | 1894 | 20.7051 | 1902.5 | 23.0633 | 1905.5 | 19.5529 | 1908 | 29.0822 | 1911 | 27.193 | 1913.5 | 13.1754 | 1916.5 | 17.8762 | 1919.5 | 30.6337 | 1922 | 12.0319 | 1925 | 29.7336 | 1927.5 | 0.20174 | 1933 | 5.975 | 1936 | 28.579 | 1938.5 | 0.83347 | 1941.5 | 13.5602 | 1944.5 | 16.1592 | 1947 | 16.4259 | 1952.5 | 22.2976 | 1955.5 | 22.3558 | 1958.5 | 26.0562 | 1966.5 | 28.3863 | 1969.5 | 21.9831 | 1972.5 | 24.7187 | 1980.5 | 21.2814 | 1983.5 | 30.1004 | 2003 | 0.81204 | 1874.5 | 15.0282 | 1879.875 | 7.0797 | 1924.75 | 5.975 | 1930.375 | 0.83347 | 1936 | 0.20174 | #REF! | #REF! | 1964 | 21.9831 | #REF! | #REF! | #REF! | #REF!
2011.5 | 4.5229 | 2014.5 | 2.9155 | 2017 | 18.055 | 2020 | 20.3549 | 2023 | 14.0403 | 2031.5 | 26.1321 | 2034 | 8.1321 | 2036.5 | 6.5255 | 2039.5 | 13.8515 | 2042.5 | 0.66221 | 2045 | 13.1908 | 2048 | 17.5735 | 2056.5 | 26.722 | 2059.5 | 18.8242 | 2062 | 26.8209 | 2065 | 0.31888 | 2067.5 | 4.3823 | 2070.5 | 21.2714 | 2073.5 | 15.2238 | 2076 | 1.2337 | 2078.5 | 20.1236 | 2081.5 | 1.8601 | 2087.5 | 3.174 | 2090 | 5.1132 | 2092.5 | 12.3903 | 2095.5 | 6.5783 | 2098.5 | 12.8335 | 2101 | 0.070299 | 2107 | 1.5751 | 2109.5 | 6.1489 | 2112.5 | 29.2336 | 2120.5 | 21.4577 | 2123.5 | 28.9117 | 2126.5 | 12.4988 | 2134.5 | 1.239 | 2137.5 | 0.14612 | 2157 | 25.5738 | 2028.375 | 0.66221 | 2034 | 13.1908 | 2078.875 | 3.174 | 2084.375 | 1.2337 | 2089.875 | 0.070299 | #REF! | #REF! | 2118 | 6.1489 | #REF! | #REF! | #REF! | #REF!
2165.5 | 0.14785 | 2168.5 | 20.0564 | 2171 | 11.127 | 2174 | 29.0643 | 2177 | 6.9564 | 2185.5 | 28.023 | 2188 | 17.2917 | 2191 | 20.553 | 2193.5 | 12.1539 | 2196.5 | 14.3854 | 2199 | 27.0946 | 2202 | 29.948 | 2210.5 | 29.8702 | 2213 | 26.4602 | 2216 | 5.8609 | 2219 | 0.036517 | 2221.5 | 4.4698 | 2224.5 | 13.3903 | 2227.5 | 4.3673 | 2230 | 29.712 | 2232.5 | 8.7682 | 2235.5 | 23.2869 | 2241 | 25.9189 | 2244 | 8.0369 | 2246.5 | 487.9075 | 2249.5 | 6.9847 | 2252.5 | 0.94154 | 2255 | 0.97517 | 2260.5 | 28.9427 | 2263.5 | 10.9071 | 2266.5 | 12.5489 | 2274.5 | 16.1793 | 2277.5 | 0.98026 | 2280.5 | 18.1116 | 2289 | 3.8794 | 2291.5 | 20.1318 | 2311 | 9.7918 | 2182.375 | 11.127 | 2188 | 6.9564 | 2232.75 | 4.4698 | 2238.375 | 4.3673 | 2243.875 | 0.94154 | #REF! | #REF! | 2272 | 0.98026 | #REF! | #REF! | #REF! | #REF!
2319.5 | 16.2371 | 2322.5 | 28.3883 | 2325 | 5.8667 | 2328 | 5.7815 | 2330.5 | 27.7324 | 2339.5 | 23.7535 | 2342 | 14.4276 | 2344.5 | 17.9636 | 2347.5 | 9.9333 | 2350.5 | 19.7622 | 2353 | 23.945 | 2356 | 5.9367 | 2364.5 | 22.0636 | 2367 | 1.2459 | 2370 | 14.9808 | 2373 | 6.5606 | 2375.5 | 7.8112 | 2378.5 | 30.3527 | 2381 | 30.2393 | 2384 | 20.5854 | 2387 | 23.869 | 2389.5 | 27.8358 | 2395 | 29.8587 | 2398 | 1.0626 | 2401 | 26.5526 | 2403.5 | 24.9936 | 2406.5 | 9.1706 | 2409 | 24.671 | 2414.5 | 23.5967 | 2417.5 | 4.9544 | 2420.5 | 0.85982 | 2428.5 | 4842.7848 | 2431.5 | 17.7701 | 2434.5 | 0.96412 | 2442.5 | 8.3523 | 2445.5 | 24.044 | 2465 | 13.3786 | 2336.375 | 5.8667 | 2341.875 | 5.7815 | 2386.75 | 1.0626 | 2392.375 | 20.5854 | 2398 | 9.1706 | #REF! | #REF! | 2426 | 0.85982 | #REF! | #REF! | #REF! | #REF!
2473.5 | 28.5012 | 2476.5 | 9.2844 | 2479 | 17.8908 | 2482 | 0.96837 | 2484.5 | 11.9891 | 2493 | 0.80858 | 2496 | 17.6247 | 2498.5 | 0.90233 | 2501.5 | 17.8313 | 2504.5 | 0.97517 | 2507 | 24.9987 | 2510 | 29.0277 | 2518.5 | 2.2853 | 2521 | 0.0087579 | 2524 | 6.3559 | 2526.5 | 0.11582 | 2529.5 | 26.9365 | 2532.5 | 13.7431 | 2535 | 15.5348 | 2538 | 16.3681 | 2540.5 | 14.0712 | 2543.5 | 0.62787 | 2549 | 14.9122 | 2552 | 26.1046 | 2554.5 | 4.1089 | 2557.5 | 27.4254 | 2560.5 | 5.5981 | 2563 | 28.1019 | 2568.5 | 2.6488 | 2571.5 | 21.3636 | 2574.5 | 19.6855 | 2582.5 | 5.0046 | 2585.5 | 1.5715 | 2588.5 | 27.4644 | 2596.5 | 27.9912 | 2599.5 | 0.97262 | 2619 | 2.3304 | 2490.375 | 0.97517 | 2495.875 | 0.96837 | 2540.75 | 13.7431 | 2546.25 | 4.1089 | 2551.875 | 0.62787 | #REF! | #REF! | 2580 | 1.5715 | #REF! | #REF! | #REF! | #REF!
2627.5 | 20.2147 | 2630.5 | 2.3754 | 2633 | 0.96922 | 2636 | 17.4099 | 2638.5 | 0.35175 | 2647 | 4.4389 | 2650 | 0.91787 | 2652.5 | 1.5732 | 2655.5 | 8.1618 | 2658.5 | 27.8462 | 2661 | 0.03603 | 2664 | 25.7795 | 2672.5 | 7.0548 | 2675 | 19.2716 | 2678 | 18.1075 | 2680.5 | 7.2807 | 2683.5 | 4.164 | 2686.5 | 18.7488 | 2689 | 1.2537 | 2692 | 21.6718 | 2694.5 | 21.5602 | 2697.5 | 24.7274 | 2703 | 5.0108 | 2706 | 22.7683 | 2708.5 | 8.0056 | 2711.5 | 0.97007 | 2714.5 | 23.1172 | 2717 | 20.8966 | 2722.5 | 13.8442 | 2725.5 | 18.0927 | 2728.5 | 0.85982 | 2736.5 | 6.988 | 2739.5 | 3.0627 | 2742.5 | 24.7187 | 2750.5 | 21.1657 | 2753.5 | 0.77434 | 2773 | 1.3553 | 2644.375 | 0.96922 | 2649.875 | 0.03603 | 2694.75 | 4.164 | 2700.25 | 0.97007 | 2705.875 | 20.8966 | #REF! | #REF! | 2734 | 0.85982 | #REF! | #REF! | #REF! | #REF!
2781.5 | 17.7323 | 2784.5 | 1.9226 | 2787 | 2.632 | 2790 | 20.3549 | 2792.5 | 0.98534 | 2801 | 0.70239 | 2804 | 19.1461 | 2806.5 | 15.9684 | 2809.5 | 22.73 | 2812.5 | 0.85803 | 2815 | 0.92218 | 2818 | 26.5294 | 2826.5 | 25.2335 | 2829 | 23.8114 | 2832 | 22.7595 | 2834.5 | 24.8443 | 2837.5 | 26.7453 | 2840.5 | 0.091718 | 2843 | 0.257 | 2846 | 1.2337 | 2848.5 | 0.13445 | 2851.5 | 14.8631 | 2857 | 0.63132 | 2860 | 2.047 | 2862.5 | 0.9845 | 2865.5 | 28.9031 | 2868.5 | 0.99127 | 2871 | 5.8415 | 2876.5 | 4.9932 | 2879.5 | 6.1042 | 2882.5 | 14.6278 | 2890.5 | 19.5526 | 2893.5 | 15.5316 | 2896.5 | 11.8023 | 2904.5 | 7.0176 | 2907.5 | 1.1389 | 2927 | 0.90579 | 2798.375 | 0.85803 | 2803.875 | 0.92218 | 2848.75 | 0.091718 | 2854.25 | 0.257 | 2859.875 | 0.13445 | #REF! | #REF! | 2888 | 6.1042 | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [6 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 1 |  |  | 2006-10-19 | 9:13
XLPE | 7-C | Tray G
0 | 200 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | E7-G | Burner Time | E8-G | Burner Time | H9-G | Burner Time | H10-G | Burner Time | L11-G | Burner Time | A-B to Gnd Min | Burner Time | A-C to Gnd Min | Burner Time | B-C to Gnd Min | Burner Time | B-D to Gnd Min | Burner Time | B-E to Gnd Min | Burner Time | D-E to Gnd Min | Burner Time | C-E to Gnd Min | Burner Time | C-F to Gnd Min | Burner Time | E-F to Gnd Min | Burner Time | A to Gnd Min | Burner Time | B to Gnd Min | Burner Time | C to Gnd Min | Burner Time | D to Gnd Min | Burner Time | E to Gnd Min | Burner Time | F to Gnd Min
-619.6875 | 255138 |  | -597.625 | 257438 | -580.2222 | 259838 | -566.5556 | 262938 | -559.4375 | 257438 | -552.8125 | 262238 | -535.8 | 262538 | -533.4 | 262338 | -558.7 | 255538 | -556.5 | 255538 | -554.625 | 255138 | -591.0226 | 255138 | -582.3906 | 255138 | -564.7569 | 257438 | -553.9944 | 259838 | -565.4944 | 255538 | -546.1 | 255538 | -556.8625 | 255538 | #REF! | #REF! | #REF! | #REF! | -608.6563 | 255138 | -573.3889 | 259838 | -556.125 | 257438 | -534.6 | 262338 | -557.6 | 255538 | #REF! | #REF!
-465.8125 | 255138 |  | -443.5625 | 257438 | -426.2778 | 259838 | -412.5556 | 262938 | -405.625 | 257438 | -398.8125 | 262238 | -381.8 | 262538 | -379.6 | 262338 | -404.9 | 255538 | -402.6 | 255538 | -400.625 | 255138 | -437.0521 | 255138 | -428.4531 | 255138 | -410.8177 | 257438 | -400.0583 | 259838 | -411.5833 | 255538 | -392.225 | 255538 | -402.9844 | 255538 | #REF! | #REF! | #REF! | #REF! | -454.6875 | 255138 | -419.4167 | 259838 | -402.2188 | 257438 | -380.7 | 262338 | -403.75 | 255538 | #REF! | #REF!
-286.125 | 255138 |  | -264.125 | 257438 | -246.7778 | 259838 | -233.1111 | 262938 | -226 | 257438 | -219.375 | 262238 | -202.3 | 262538 | -200.1 | 262338 | -225.4 | 255538 | -223 | 255538 | -221 | 255138 | -257.5347 | 255138 | -248.9063 | 255138 | -231.316 | 257438 | -220.5722 | 259838 | -232.0722 | 255538 | -212.7 | 255538 | -223.4438 | 255538 | #REF! | #REF! | #REF! | #REF! | -275.125 | 255138 | -239.9444 | 259838 | -222.6875 | 257438 | -201.2 | 262338 | -224.2 | 255538 | #REF! | #REF!
-132.1875 | 255138 |  | -110.125 | 257438 | -92.7778 | 259838 | -79.1111 | 262938 | -72 | 257438 | -65.375 | 262238 | -48.3 | 262538 | -46.1 | 262338 | -71.4 | 255538 | -69 | 255538 | -67.125 | 255138 | -103.5503 | 255138 | -94.9219 | 255138 | -77.316 | 257438 | -66.5722 | 259838 | -78.0722 | 255538 | -58.7 | 255538 | -69.4438 | 255538 | #REF! | #REF! | #REF! | #REF! | -121.1563 | 255138 | -85.9444 | 259838 | -68.6875 | 257438 | -47.2 | 262338 | -70.2 | 255538 | #REF! | #REF!
21.8125 | 255138 |  | 43.875 | 257438 | 61.2222 | 259838 | 74.8889 | 262938 | 82 | 257438 | 88.625 | 262238 | 105.7 | 262538 | 107.9 | 262338 | 82.6 | 255538 | 85 | 255538 | 86.875 | 255138 | 50.4497 | 255138 | 59.0781 | 255138 | 76.684 | 257438 | 87.4278 | 259838 | 75.9278 | 255538 | 95.3 | 255538 | 84.5562 | 255538 | #REF! | #REF! | #REF! | #REF! | 32.8437 | 255138 | 68.0556 | 259838 | 85.3125 | 257438 | 106.8 | 262338 | 83.8 | 255538 | #REF! | #REF!
175.8125 | 255138 |  | 197.875 | 257438 | 215.2222 | 259838 | 228.8889 | 262938 | 236 | 257438 | 242.625 | 262238 | 259.7 | 262538 | 261.9 | 262338 | 236.6 | 255538 | 239 | 255538 | 240.875 | 255138 | 204.4497 | 255138 | 213.0781 | 255138 | 230.684 | 257438 | 241.4278 | 259838 | 229.9278 | 255538 | 249.3 | 255538 | 238.5562 | 255538 | #REF! | #REF! | #REF! | #REF! | 186.8437 | 255138 | 222.0556 | 259838 | 239.3125 | 257438 | 260.8 | 262338 | 237.8 | 255538 | #REF! | #REF!
329.8125 | 255138 |  | 351.875 | 257438 | 369.2222 | 259838 | 382.8889 | 262938 | 390 | 257438 | 396.5625 | 262238 | 413.6 | 262538 | 415.9 | 262338 | 390.6 | 255538 | 393 | 255538 | 394.875 | 255138 | 358.4497 | 255138 | 367.0625 | 255138 | 384.6684 | 257438 | 395.4028 | 259838 | 383.9278 | 255538 | 403.275 | 255538 | 392.5406 | 255538 | #REF! | #REF! | #REF! | #REF! | 340.8437 | 255138 | 376.0556 | 259838 | 393.2812 | 257438 | 414.75 | 262338 | 391.8 | 255538 | #REF! | #REF!
483.8125 | 255138 |  | 505.75 | 257438 | 523.1667 | 259838 | 536.8889 | 4350.8755 | 544 | 6826.0792 | 550.5625 | 262238 | 567.6 | 262538 | 569.8 | 262338 | 544.6 | 255538 | 547 | 255538 | 548.875 | 255138 | 512.4045 | 4350.8755 | 521.0312 | 6826.0792 | 538.6545 | 4350.8755 | 549.3639 | 4350.8755 | 537.9139 | 4350.8755 | 557.25 | 255538 | 546.5406 | 6826.0792 | #REF! | #REF! | #REF! | #REF! | 494.7812 | 255138 | 530.0278 | 4350.8755 | 547.2812 | 6826.0792 | 568.7 | 262338 | 545.8 | 255538 | #REF! | #REF!
637.6875 | 255138 |  | 659.625 | 257438 | 677.1667 | 259838 | 690.8333 | 96471.244 | 697.875 | 7757.8873 | 704.5 | 262238 | 721.6 | 12.2385 | 723.9 | 262338 | 698.5 | 255538 | 700.9 | 255538 | 702.75 | 255138 | 666.3281 | 96471.244 | 674.9219 | 7757.8873 | 692.5937 | 7757.8873 | 703.375 | 12.2385 | 691.85 | 96471.244 | 711.225 | 12.2385 | 700.4437 | 7757.8873 | #REF! | #REF! | #REF! | #REF! | 648.6562 | 255138 | 684 | 96471.244 | 701.1875 | 7757.8873 | 722.75 | 12.2385 | 699.7 | 255538 | #REF! | #REF!
791.75 | 255138 |  | 813.75 | 3.0439 | 831.0556 | 259838 | 844.7778 | 1.4377 | 851.875 | 7297.5416 | 858.5 | 262238 | 875.5 | 0.62759 | 877.6 | 262338 | 852.6 | 255538 | 854.9 | 255538 | 856.875 | 130268.9999 | 820.3333 | 1.4377 | 828.9687 | 3.0439 | 846.5521 | 1.4377 | 857.2333 | 0.62759 | 845.8333 | 1.4377 | 865.15 | 0.62759 | 854.4687 | 7297.5416 | #REF! | #REF! | #REF! | #REF! | 802.75 | 3.0439 | 837.9167 | 1.4377 | 855.1875 | 7297.5416 | 876.55 | 0.62759 | 853.75 | 255538 | #REF! | #REF!
945.6875 | 255138 |  | 967.75 | 0.62952 | 985.0556 | 1.5477 | 998.8333 | 30.8873 | 1005.875 | 3620.6128 | 1012.5 | 262238 | 1029.4 | 9.8904 | 1031.6 | 262338 | 1006.6 | 255538 | 1008.8 | 255538 | 1010.875 | 255138 | 974.3316 | 0.62952 | 982.9531 | 0.62952 | 1000.566 | 1.5477 | 1011.2222 | 1.5477 | 999.8222 | 1.5477 | 1019.1 | 9.8904 | 1008.4437 | 3620.6128 | #REF! | #REF! | #REF! | #REF! | 956.7187 | 0.62952 | 991.9444 | 1.5477 | 1009.1875 | 3620.6128 | 1030.5 | 9.8904 | 1007.7 | 255538 | #REF! | #REF!
1099.625 | 255138 |  | 1121.625 | 0.63243 | 1139.1111 | 4.0184 | 1152.7778 | 11.0476 | 1159.875 | 11515.2521 | 1166.4375 | 262238 | 1183.4 | 2.1399 | 1185.6 | 262338 | 1160.6 | 255538 | 1162.9 | 132018.9999 | 1164.75 | 255138 | 1128.2847 | 0.63243 | 1136.8906 | 0.63243 | 1154.5503 | 4.0184 | 1165.2222 | 2.1399 | 1153.8472 | 4.0184 | 1173.125 | 2.1399 | 1162.4531 | 11515.2521 | #REF! | #REF! | #REF! | #REF! | 1110.625 | 0.63243 | 1145.9444 | 4.0184 | 1163.1562 | 11515.2521 | 1184.5 | 2.1399 | 1161.75 | 132018.9999 | #REF! | #REF!
1253.625 | 255138 |  | 1275.625 | 3.5106 | 1293 | 3.5211 | 1306.7778 | 4.2855 | 1313.8125 | 10640.008 | 1320.4375 | 262238 | 1337.4 | 11.9349 | 1339.6 | 262338 | 1314.6 | 131119 | 1316.8 | 255538 | 1318.75 | 255138 | 1282.2569 | 3.5106 | 1290.875 | 3.5106 | 1308.5069 | 3.5211 | 1319.1944 | 3.5211 | 1307.7944 | 3.5211 | 1327.1 | 11.9349 | 1316.4125 | 10640.008 | #REF! | #REF! | #REF! | #REF! | 1264.625 | 3.5106 | 1299.8889 | 3.5211 | 1317.125 | 10640.008 | 1338.5 | 11.9349 | 1315.7 | 131119 | #REF! | #REF!
1407.625 | 255138 |  | 1429.625 | 1.5935 | 1447 | 0.62831 | 1460.7778 | 1.6331 | 1467.8125 | 4973.4525 | 1474.4375 | 262238 | 1491.4 | 12.5266 | 1493.6 | 262338 | 1468.6 | 63809.5 | 1470.8 | 63809.5 | 1472.75 | 255138 | 1436.2569 | 0.62831 | 1444.875 | 1.5935 | 1462.5069 | 0.62831 | 1473.1944 | 0.62831 | 1461.7944 | 0.62831 | 1481.1 | 12.5266 | 1470.4125 | 4973.4525 | #REF! | #REF! | #REF! | #REF! | 1418.625 | 1.5935 | 1453.8889 | 0.62831 | 1471.125 | 4973.4525 | 1492.5 | 12.5266 | 1469.7 | 63809.5 | #REF! | #REF!
1561.625 | 1227.7379 |  | 1583.625 | 32.7826 | 1601 | 1.9362 | 1614.7778 | 4051.6209 | 1621.875 | 1820.2699 | 1628.5625 | 262238 | 1645.5 | 4.6533 | 1647.6 | 2644.1458 | 1622.6 | 23.0804 | 1624.8 | 5.2008 | 1627 | 255138 | 1590.2569 | 1.9362 | 1598.9219 | 32.7826 | 1616.5538 | 1.9362 | 1627.2194 | 1.9362 | 1615.7944 | 1.9362 | 1635.125 | 4.6533 | 1624.4594 | 5.2008 | #REF! | #REF! | #REF! | #REF! | 1572.625 | 32.7826 | 1607.8889 | 1.9362 | 1625.2187 | 1820.2699 | 1646.55 | 4.6533 | 1623.7 | 5.2008 | #REF! | #REF!
1715.625 | 2293.399 |  | 1737.625 | 2279.4196 | 1755 | 1250.9979 | 1768.7778 | 269.899 | 1775.75 | 0.75175 | 1782.4375 | 5.1046 | 1799.4 | 10.8335 | 1801.6 | 4.3046 | 1776.6 | 3.3848 | 1778.8 | 7.7491 | 1780.625 | 3.3577 | 1744.2569 | 269.899 | 1752.8594 | 0.75175 | 1770.4913 | 0.75175 | 1781.1944 | 4.3046 | 1769.7944 | 3.3848 | 1789.1 | 3.3848 | 1778.3969 | 0.75175 | #REF! | #REF! | #REF! | #REF! | 1726.625 | 2279.4196 | 1761.8889 | 269.899 | 1779.0937 | 0.75175 | 1800.5 | 4.3046 | 1777.7 | 3.3848 | #REF! | #REF!
1869.5 | 10.3167 |  | 1891.5625 | 8.5284 | 1909 | 1.7866 | 1922.6111 | 2.4122 | 1929.5625 | 15.178 | 1936.25 | 0.62831 | 1953.3 | 6.4173 | 1955.6 | 3.0665 | 1930.4 | 2.3371 | 1932.6 | 17.6483 | 1934.5 | 2.9771 | 1898.1684 | 1.7866 | 1906.7187 | 0.62831 | 1924.3559 | 0.62831 | 1935.1278 | 1.7866 | 1923.6528 | 1.7866 | 1942.975 | 2.3371 | 1932.2031 | 0.62831 | #REF! | #REF! | #REF! | #REF! | 1880.5312 | 8.5284 | 1915.8056 | 1.7866 | 1932.9062 | 0.62831 | 1954.45 | 3.0665 | 1931.5 | 2.3371 | #REF! | #REF!
2023.5 | 4.4655 |  | 2045.5625 | 0.93303 | 2062.9444 | 1.277 | 2076.6111 | 1.5158 | 2083.6875 | 3.1288 | 2090.375 | 2.797 | 2107.3 | 1.4394 | 2109.6 | 4.1421 | 2084.4 | 8.2029 | 2086.6 | 1.6051 | 2088.375 | 2.2188 | 2052.1545 | 0.93303 | 2060.7812 | 0.93303 | 2078.4045 | 1.277 | 2089.1139 | 1.277 | 2077.6389 | 1.277 | 2096.975 | 1.4394 | 2086.2656 | 1.6051 | #REF! | #REF! | #REF! | #REF! | 2034.5312 | 0.93303 | 2069.7778 | 1.277 | 2087.0312 | 2.797 | 2108.45 | 1.4394 | 2085.5 | 1.6051 | #REF! | #REF!
2177.5625 | 1.74 |  | 2199.5 | 7.3438 | 2216.9444 | 1.6269 | 2230.5556 | 0.62495 | 2237.5625 | 12.3345 | 2244.375 | 0.62352 | 2261.3 | 0.81386 | 2263.6 | 1.1712 | 2238.4 | 2.6228 | 2240.5 | 19.2752 | 2242.625 | 9.5017 | 2206.1406 | 0.62495 | 2214.75 | 0.62352 | 2232.3594 | 0.62352 | 2243.1 | 0.62495 | 2231.6 | 0.62495 | 2250.95 | 0.81386 | 2240.2094 | 0.62352 | #REF! | #REF! | #REF! | #REF! | 2188.5312 | 1.74 | 2223.75 | 0.62495 | 2240.9687 | 0.62352 | 2262.45 | 0.81386 | 2239.45 | 2.6228 | #REF! | #REF!
2331.4375 | 7.2778 |  | 2353.5 | 2.8014 | 2370.9444 | 0.6214 | 2384.6111 | 2.6279 | 2391.5625 | 0.73969 | 2398.25 | 0.62639 | 2415.3 | 9.7985 | 2417.6 | 0.62187 | 2392.5 | 0.62471 | 2394.5 | 0.62376 | 2396.375 | 11.5063 | 2360.1233 | 0.6214 | 2368.6875 | 0.62639 | 2386.342 | 0.6214 | 2397.1139 | 0.6214 | 2385.6389 | 0.6214 | 2404.975 | 0.62187 | 2394.2031 | 0.62376 | #REF! | #REF! | #REF! | #REF! | 2342.4687 | 2.8014 | 2377.7778 | 0.6214 | 2394.9062 | 0.62639 | 2416.45 | 0.62187 | 2393.5 | 0.62376 | #REF! | #REF!
2485.375 | 0.62687 |  | 2507.5 | 0.62495 | 2524.8333 | 0.96981 | 2538.5 | 5.6394 | 2545.5625 | 0.92876 | 2552.25 | 3.1362 | 2569.2 | 0.62567 | 2571.6 | 11.8381 | 2546.3 | 3.8335 | 2548.5 | 2.4464 | 2550.375 | 3.4813 | 2514.0521 | 0.62495 | 2522.6719 | 0.62495 | 2540.2865 | 0.92876 | 2551.0333 | 0.62567 | 2539.5333 | 0.96981 | 2558.9 | 0.62567 | 2548.1531 | 0.92876 | #REF! | #REF! | #REF! | #REF! | 2496.4375 | 0.62495 | 2531.6667 | 0.96981 | 2548.9062 | 0.92876 | 2570.4 | 0.62567 | 2547.4 | 2.4464 | #REF! | #REF!
2639.375 | 0.62663 |  | 2661.5 | 1.5128 | 2678.8333 | 0.62092 | 2692.5 | 0.62258 | 2699.5625 | 0.63415 | 2706.25 | 4.6055 | 2723.2 | 2.3458 | 2725.6 | 0.62448 | 2700.3 | 0.62519 | 2702.5 | 8.0451 | 2704.375 | 0.63464 | 2668.0521 | 0.62092 | 2676.6719 | 0.62663 | 2694.2865 | 0.62092 | 2705.0333 | 0.62092 | 2693.5333 | 0.62092 | 2712.9 | 0.62448 | 2702.1531 | 0.62519 | #REF! | #REF! | #REF! | #REF! | 2650.4375 | 0.62663 | 2685.6667 | 0.62092 | 2702.9062 | 0.63415 | 2724.4 | 0.62448 | 2701.4 | 0.62519 | #REF! | #REF!
2793.375 | 0.6221 |  | 2815.5 | 0.62116 | 2832.8333 | 1.3468 | 2846.5 | 0.62045 | 2853.5625 | 0.6221 | 2860.25 | 0.62069 | 2877.2 | 0.61905 | 2879.6 | 1.0115 | 2854.3 | 0.64488 | 2856.5 | 23.0695 | 2858.375 | 0.62831 | 2822.0521 | 0.62045 | 2830.6719 | 0.62069 | 2848.2865 | 0.62045 | 2859.0333 | 0.61905 | 2847.5333 | 0.62045 | 2866.9 | 0.61905 | 2856.1531 | 0.62069 | #REF! | #REF! | #REF! | #REF! | 2804.4375 | 0.62116 | 2839.6667 | 0.62045 | 2856.9062 | 0.62069 | 2878.4 | 0.61905 | 2855.4 | 0.64488 | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## H9-H10
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 156.0672 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 9 & 10 | Cable H | Odd -Even
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39009.3785 | 1 | 0 | 39009.3785 | 1 | 0 |  | -486 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3803 | 1 | 0 | 39009.3803 | 1 | 0 |  | -332 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3824 | 1 | 0 | 39009.3824 | 1 | 0 |  | -152.5 | 479.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3841 | 1 | 0 | 39009.3842 | 1 | 0 |  | 1.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3859 | 1 | 0 | 39009.3859 | 1 | 0 |  | 155.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3877 | 1 | 0 | 39009.3877 | 1 | 0 |  | 309.5 | 941.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3895 | 1 | 0 | 39009.3895 | 1 | 0 |  | 463.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3913 | 1 | 0 | 39009.3913 | 1 | 0 |  | 617.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3931 | 1 | 0 |  | 1 | 0 |  | 771 | 1403 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3948 | 1 | 0 | 39009.3948 | 1 | 0 |  | 925.5 | 1557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3966 | 1 | 0 | 39009.3966 | 1 | 0 |  | 1079.5 | 1711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.3984 | 1 | 0 | 39009.3984 | 1 | 0 |  | 1233.5 | 1865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.4002 | 1 | 0 | 39009.4002 | 1 | 0 |  | 1387.5 | 2019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39009.402 | 12 | 8 | 39009.402 | 12 | 8 |  | 1541.5 | 2173.5 | 0.7326 | 0.4884 | 0.7326 | 0.4884 | 0.007326 | 0.004884 | 0.007326 | 0.004884 | 0.002442 | 0.002442 | 63809.5 | 63809.5 | 31655.1412
39009.4037 | 2077 | 0 | 39009.4038 | 2430 | 0 |  | 1695.5 | 2327.5 | 126.801 | 0 | 148.3516 | 0 | 1.268 | 0 | 1.4835 | 0 | 1.268 | 1.4835 | 23.0804 | 5.2008 | 21.8124
39009.4055 | 2156 | 0 | 39009.4055 | 2054 | 0 |  | 1849.5 | 2481.5 | 131.6239 | 0 | 125.3968 | 0 | 1.3162 | 0 | 1.254 | 0 | 1.3162 | 1.254 | 18.5705 | 24.4586 | 17.2543
39009.4073 | 2498 | 0 | 39009.4073 | 2009 | 0 |  | 2003 | 2635 | 152.5031 | 0 | 122.6496 | 0 | 1.525 | 0 | 1.2265 | 0 | 1.525 | 1.2265 | 2.3371 | 27.2464 | 0.81204
39009.4091 | 2016 | 0 | 39009.4091 | 2094 | 0 |  | 2157 | 2789 | 123.0769 | 0 | 127.8388 | 0 | 1.2308 | 0 | 1.2784 | 0 | 1.2308 | 1.2784 | 26.8046 | 22.0812 | 25.5738
39009.4109 | 2299 | 0 | 39009.4109 | 2058 | 0 |  | 2311 | 2943 | 140.3541 | 0 | 125.641 | 0 | 1.4035 | 0 | 1.2564 | 0 | 1.4035 | 1.2564 | 11.1953 | 24.2167 | 9.7918
39009.4127 | 2228 | 0 | 39009.4127 | 2530 | 0 |  | 2465 | 3097 | 136.0195 | 0 | 154.4567 | 0 | 1.3602 | 0 | 1.5446 | 0 | 1.3602 | 1.5446 | 14.7388 | 1.0427 | 13.3786
39009.4144 | 2462 | 0 | 39009.4145 | 2022 | 0 |  | 2619 | 3251 | 150.3053 | 0 | 123.4432 | 0 | 1.5031 | 0 | 1.2344 | 0 | 1.5031 | 1.2344 | 3.8335 | 26.4283 | 2.3304
39009.4162 | 2485 | 0 | 39009.4162 | 2089 | 0 |  | 2773 | 3405 | 151.7094 | 0 | 127.5336 | 0 | 1.5171 | 0 | 1.2753 | 0 | 1.5171 | 1.2753 | 2.8724 | 22.3734 | 1.3553
39009.418 | 2540 | 0 | 39009.418 | 2018 | 0 |  | 2927 | 3559 | 155.0672 | 0 | 123.199 | 0 | 1.5507 | 0 | 1.232 | 0 | 1.5507 | 1.232 | 0.64488 | 26.6789 | 0.90579

## E7-E8
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.8291 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 7 & 8 | Cable E | Odd -Even
Time-91 | N11 | N12 | Time-92 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39009.3783 | 1 | 0 | 39009.3783 | 1 | 0 |  | -505.5 | 126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3801 | 1 | 0 | 39009.3801 | 1 | 0 |  | -351.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3821 | 1 | 0 | 39009.3822 | 1 | 0 |  | -172 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3839 | 1 | 0 | 39009.3839 | 1 | 0 |  | -18 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3857 | 1 | 0 | 39009.3857 | 1 | 0 |  | 136 | 768 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3875 | 1 | 0 | 39009.3875 | 1 | 0 |  | 290 | 922 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3893 | 1 | 0 | 39009.3893 | 1 | 0 |  | 444 | 1076 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.391 | 1 | 0 | 39009.3911 | 1 | 0 |  | 597.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263338 | 263338 | 263337.9994
39009.3928 | 2216 | 1 | 39009.3928 | 1 | 0 |  | 752 | 1384 | 135.2869 | 0.06105 | 0.06105 | 0 | 1.3529 | 0.0006105 | 0.0006105 | 0 | 1.3523 | 0.0006105 | 18.8885 | 263338.0001 | 41722.1564
39009.3946 | 2309 | 1 | 39009.3946 | 1 | 0 |  | 905.5 | 1537.5 | 140.9646 | 0.06105 | 0.06105 | 0 | 1.4096 | 0.0006105 | 0.0006105 | 0 | 1.409 | 0.0006105 | 14.0979 | 263338.0001 | 32425.6867
39009.3964 | 2236 | 1 | 39009.3964 | 1 | 0 |  | 1059.5 | 1691.5 | 136.5079 | 0.06105 | 0.06105 | 0 | 1.3651 | 0.0006105 | 0.0006105 | 0 | 1.3645 | 0.0006105 | 17.8246 | 263338.0001 | 39722.9156
39009.3982 | 2308 | 1 | 39009.3982 | 1 | 0 |  | 1213.5 | 1845.5 | 140.9035 | 0.06105 | 0.06105 | 0 | 1.409 | 0.0006105 | 0.0006105 | 0 | 1.4084 | 0.0006105 | 14.1474 | 263338.0001 | 32525.6487
39009.4 | 2072 | 1 | 39009.4 | 1 | 0 |  | 1367.5 | 1999.5 | 126.4957 | 0.06105 | 0.06105 | 0 | 1.265 | 0.0006105 | 0.0006105 | 0 | 1.2643 | 0.0006105 | 27.155 | 263338.0001 | 56116.6902
39009.4017 | 2011 | 1 | 39009.4017 | 1 | 0 |  | 1521.5 | 2153.5 | 122.7717 | 0.06105 | 0.06105 | 0 | 1.2277 | 0.0006105 | 0.0006105 | 0 | 1.2271 | 0.0006105 | 31.0139 | 263338.0001 | 62214.3747
39009.4035 | 2440 | 0 | 39009.4035 | 96 | 0 |  | 1675.5 | 2307.5 | 148.9621 | 0 | 5.8608 | 0 | 1.4896 | 0 | 0.058608 | 0 | 1.4896 | 0.058608 | 7.9664 | 2644.1458 | 6.4768
39009.4053 | 2109 | 0 | 39009.4053 | 2011 | 0 |  | 1829.5 | 2461.5 | 128.7546 | 0 | 122.7717 | 0 | 1.2875 | 0 | 1.2277 | 0 | 1.2875 | 1.2277 | 24.9113 | 30.9985 | 23.6238
39009.4071 | 2006 | 0 | 39009.4071 | 2556 | 0 |  | 1983.5 | 2615.5 | 122.4664 | 0 | 156.044 | 0 | 1.2247 | 0 | 1.5604 | 0 | 1.2247 | 1.5604 | 31.325 | 3.0665 | 30.1004
39009.4089 | 2597 | 0 | 39009.4089 | 2055 | 0 |  | 2137.5 | 2769.5 | 158.547 | 0 | 125.4579 | 0 | 1.5855 | 0 | 1.2546 | 0 | 1.5855 | 1.2546 | 1.4394 | 28.1937 | 0.14612
39009.4106 | 2169 | 0 | 39009.4107 | 2402 | 0 |  | 2291.5 | 2923.5 | 132.4176 | 0 | 146.6422 | 0 | 1.3242 | 0 | 1.4664 | 0 | 1.3242 | 1.4664 | 21.456 | 9.6744 | 20.1318
39009.4124 | 2102 | 0 | 39009.4124 | 2126 | 0 |  | 2445.5 | 3077.5 | 128.3272 | 0 | 129.7924 | 0 | 1.2833 | 0 | 1.2979 | 0 | 1.2833 | 1.2979 | 25.3273 | 23.9125 | 24.044
39009.4142 | 2618 | 0 | 39009.4142 | 2105 | 0 |  | 2599.5 | 3231.5 | 159.8291 | 0 | 128.5104 | 0 | 1.5983 | 0 | 1.2851 | 0 | 1.5983 | 1.2851 | 0.62567 | 25.1487 | 0.97262
39009.416 | 2574 | 0 | 39009.416 | 2617 | 0 |  | 2753.5 | 3385.5 | 157.1429 | 0 | 159.768 | 0 | 1.5714 | 0 | 1.5977 | 0 | 1.5714 | 1.5977 | 2.3458 | 0.66412 | 0.77434
39009.4178 | 2565 | 0 | 39009.4178 | 2608 | 0 |  | 2907.5 | 3539.5 | 156.5934 | 0 | 159.2186 | 0 | 1.5659 | 0 | 1.5922 | 0 | 1.5659 | 1.5922 | 2.7049 | 1.0115 | 1.1389

## C6-L11
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.1575 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable L |  | Odd
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39009.3782 | 1 | 0 | 39009.3783 | 1 | 0 |  | -508.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.38 | 1 | 0 | 39009.38 | 1 | 0 |  | -354.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3821 | 1 | 0 | 39009.3821 | 1 | 0 |  | -175 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3839 | 1 | 0 | 39009.3839 | 1 | 0 |  | -21 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3857 | 1 | 0 | 39009.3857 | 1 | 0 |  | 133 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3874 | 1 | 0 | 39009.3875 | 1 | 0 |  | 287 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3892 | 1 | 0 | 39009.3892 | 1 | 0 |  | 441 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.391 | 1 | 0 | 39009.391 | 1 | 0 |  | 595 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3928 | 1 | 0 | 39009.3928 | 1 | 0 |  | 749 | 1381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3946 | 1 | 0 | 39009.3946 | 1 | 0 |  | 903 | 1535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3964 | 1 | 0 | 39009.3964 | 1 | 0 |  | 1057 | 1689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3981 | 1 | 0 | 39009.3982 | 1 | 0 |  | 1211 | 1843 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3999 | 1 | 0 | 39009.3999 | 1 | 0 |  | 1365 | 1997 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.4017 | 1 | 0 | 39009.4017 | 1 | 0 |  | 1519 | 2151 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
| 1 | 0 | 39009.4035 | 1 | 0 |  | 1674 | 2306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.4053 | 2115 | 0 | 39009.4053 | 2347 | 0 |  | 1827 | 2459 | 129.1209 | 0 | 143.2845 | 0 | 1.2912 | 0 | 1.4328 | 0 | 1.2912 | 1.4328 | 24.0369 | 11.7759 | 22.7457
39009.407 | 2140 | 0 | 39009.4071 | 2016 | 0 |  | 1980.5 | 2612.5 | 130.6471 | 0 | 123.0769 | 0 | 1.3065 | 0 | 1.2308 | 0 | 1.3065 | 1.2308 | 22.5879 | 30.128 | 21.2814
39009.4088 | 2552 | 0 | 39009.4088 | 2323 | 0 |  | 2134.5 | 2766.5 | 155.7998 | 0 | 141.8193 | 0 | 1.558 | 0 | 1.4182 | 0 | 1.558 | 1.4182 | 2.797 | 12.9307 | 1.239
39009.4106 | 2489 | 0 | 39009.4106 | 2044 | 0 |  | 2289 | 2921 | 151.9536 | 0 | 124.7863 | 0 | 1.5195 | 0 | 1.2479 | 0 | 1.5195 | 1.2479 | 5.399 | 28.3454 | 3.8794
39009.4124 | 2389 | 0 | 39009.4124 | 2106 | 0 |  | 2442.5 | 3074.5 | 145.8486 | 0 | 128.5714 | 0 | 1.4585 | 0 | 1.2857 | 0 | 1.4585 | 1.2857 | 9.8108 | 24.567 | 8.3523
39009.4142 | 2030 | 0 | 39009.4142 | 2184 | 0 |  | 2596.5 | 3228.5 | 123.9316 | 0 | 133.3333 | 0 | 1.2393 | 0 | 1.3333 | 0 | 1.2393 | 1.3333 | 29.2305 | 20.1181 | 27.9912
39009.416 | 2142 | 0 | 39009.416 | 2306 | 0 |  | 2750.5 | 3382.5 | 130.7692 | 0 | 140.7814 | 0 | 1.3077 | 0 | 1.4078 | 0 | 1.3077 | 1.4078 | 22.4734 | 13.7632 | 21.1657
39009.4177 | 2418 | 0 | 39009.4178 | 2607 | 0 |  | 2904.5 | 3536.5 | 147.619 | 0 | 159.1575 | 0 | 1.4762 | 0 | 1.5916 | 0 | 1.4762 | 1.5916 | 8.4938 | 0.62831 | 7.0176

## C6-E8
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.2186 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 6 & 8 | Cable C | Even - | Cable E |  | Even
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R8-G | R6-8
39009.3781 | 1 | 0 | 39009.3782 | 1 | 0 |  | -516.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3799 | 1 | 0 | 39009.3799 | 1 | 0 |  | -362.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.382 | 1 | 0 | 39009.382 | 1 | 0 |  | -183.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3838 | 1 | 0 | 39009.3838 | 1 | 0 |  | -29.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3856 | 1 | 0 | 39009.3856 | 1 | 0 |  | 124.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3873 | 1 | 0 | 39009.3874 | 1 | 0 |  | 278.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3891 | 1 | 0 | 39009.3891 | 1 | 0 |  | 432.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3909 | 1 | 0 | 39009.3909 | 1 | 0 |  | 586.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3927 | 1 | 0 | 39009.3927 | 1 | 0 |  | 740.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3945 | 1 | 0 | 39009.3945 | 1 | 0 |  | 894.5 | 1526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3963 | 1 | 0 | 39009.3963 | 1 | 0 |  | 1048.5 | 1680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.398 | 1 | 0 | 39009.3981 | 1 | 0 |  | 1202.5 | 1834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3998 | 1 | 0 | 39009.3998 | 1 | 0 |  | 1356.5 | 1988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.4016 | 1 | 0 | 39009.4016 | 1 | 0 |  | 1510.5 | 2142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.4034 | 1 | 0 | 39009.4034 | 26 | 0 |  | 1664.5 | 2296.5 | 0.06105 | 0 | 1.5873 | 0 | 0.0006105 | 0 | 0.015873 | 0 | 0.0006105 | 0.015873 | 262338 | 9993.7692 | 262337.9994
39009.4052 | 2012 | 0 | 39009.4052 | 2261 | 0 |  | 1818.5 | 2450.5 | 122.8327 | 0 | 138.0342 | 0 | 1.2283 | 0 | 1.3803 | 0 | 1.2283 | 1.3803 | 30.4364 | 16.0716 | 29.2081
39009.407 | 2083 | 0 | 39009.407 | 2031 | 0 |  | 1972.5 | 2604.5 | 127.1673 | 0 | 123.9927 | 0 | 1.2717 | 0 | 1.2399 | 0 | 1.2717 | 1.2399 | 25.9904 | 29.2161 | 24.7187
39009.4087 | 2304 | 0 | 39009.4088 | 2520 | 0 |  | 2126.5 | 2758.5 | 140.6593 | 0 | 153.8462 | 0 | 1.4066 | 0 | 1.5385 | 0 | 1.4066 | 1.5385 | 13.9054 | 4.1421 | 12.4988
39009.4105 | 2197 | 0 | 39009.4105 | 2594 | 0 |  | 2280.5 | 2912.5 | 134.127 | 0 | 158.3639 | 0 | 1.3413 | 0 | 1.5836 | 0 | 1.3413 | 1.5836 | 19.4529 | 1.1712 | 18.1116
39009.4123 | 2608 | 0 | 39009.4123 | 2537 | 0 |  | 2434.5 | 3066.5 | 159.2186 | 0 | 154.884 | 0 | 1.5922 | 0 | 1.5488 | 0 | 1.5922 | 1.5488 | 0.62807 | 3.4442 | 0.96412
39009.4141 | 2039 | 0 | 39009.4141 | 2233 | 0 |  | 2588.5 | 3220.5 | 124.4811 | 0 | 136.3248 | 0 | 1.2448 | 0 | 1.3632 | 0 | 1.2448 | 1.3632 | 28.7092 | 17.5271 | 27.4644
39009.4159 | 2083 | 0 | 39009.4159 | 2075 | 0 |  | 2742.5 | 3374.5 | 127.1673 | 0 | 126.6789 | 0 | 1.2717 | 0 | 1.2668 | 0 | 1.2717 | 1.2668 | 25.9904 | 26.4761 | 24.7187
39009.4177 | 2318 | 0 | 39009.4177 | 2273 | 0 |  | 2896.5 | 3528.5 | 141.514 | 0 | 138.7668 | 0 | 1.4151 | 0 | 1.3877 | 0 | 1.4151 | 1.3877 | 13.2174 | 15.4589 | 11.8023

## C6-E7
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.3785 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 6 & 7 | Cable C | Even - | Cable E |  | Odd
Time-81 | N11 | N12 | Time-82 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R7-G | R6-7
39009.3781 | 1 | 0 | 39009.3781 | 1 | 0 |  | -519.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3799 | 1 | 0 | 39009.3799 | 1 | 0 |  | -365.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.382 | 1 | 0 | 39009.382 | 1 | 0 |  | -186 | 446 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3838 | 1 | 0 | 39009.3838 | 1 | 0 |  | -32 | 600 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3855 | 1 | 0 | 39009.3856 | 1 | 0 |  | 122 | 754 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3873 | 1 | 0 | 39009.3873 | 1 | 0 |  | 276 | 908 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3891 | 1 | 0 | 39009.3891 | 1 | 0 |  | 429.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3909 | 1 | 0 | 39009.3909 | 1 | 0 |  | 584 | 1216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39009.3927 | 1 | 0 | 39009.3927 | 2030 | 0 |  | 738 | 1370 | 0.06105 | 0 | 123.9316 | 0 | 0.0006105 | 0 | 1.2393 | 0 | 0.0006105 | 1.2393 | 264238 | 30.2158 | 264237.9994
39009.3944 | 1 | 0 | 39009.3945 | 2125 | 0 |  | 892 | 1524 | 0.06105 | 0 | 129.7314 | 0 | 0.0006105 | 0 | 1.2973 | 0 | 0.0006105 | 1.2973 | 264238 | 24.3944 | 264237.9994
39009.3962 | 1 | 0 | 39009.3962 | 2155 | 0 |  | 1045.5 | 1677.5 | 0.06105 | 0 | 131.5629 | 0 | 0.0006105 | 0 | 1.3156 | 0 | 0.0006105 | 1.3156 | 264238 | 22.6626 | 264237.9994
39009.398 | 1 | 0 | 39009.398 | 2588 | 0 |  | 1199.5 | 1831.5 | 0.06105 | 0 | 157.9976 | 0 | 0.0006105 | 0 | 1.58 | 0 | 0.0006105 | 1.58 | 264238 | 2.1399 | 264237.9994
39009.3998 | 1 | 0 | 39009.3998 | 2085 | 0 |  | 1353.5 | 1985.5 | 0.06105 | 0 | 127.2894 | 0 | 0.0006105 | 0 | 1.2729 | 0 | 0.0006105 | 1.2729 | 264238 | 26.7808 | 264237.9994
39009.4016 | 1 | 0 | 39009.4016 | 2187 | 0 |  | 1507.5 | 2139.5 | 0.06105 | 0 | 133.5165 | 0 | 0.0006105 | 0 | 1.3352 | 0 | 0.0006105 | 1.3352 | 264238 | 20.8679 | 264237.9994
39009.4034 | 1 | 0 | 39009.4034 | 2436 | 0 |  | 1661.5 | 2293.5 | 0.06105 | 0 | 148.7179 | 0 | 0.0006105 | 0 | 1.4872 | 0 | 0.0006105 | 1.4872 | 264238 | 8.5131 | 264237.9994
39009.4051 | 2515 | 0 | 39009.4052 | 2385 | 0 |  | 1815.5 | 2447.5 | 153.5409 | 0 | 145.6044 | 0 | 1.5354 | 0 | 1.456 | 0 | 1.5354 | 1.456 | 5.1046 | 10.8335 | 3.5692
39009.4069 | 2144 | 0 | 39009.4069 | 2417 | 0 |  | 1969.5 | 2601.5 | 130.8913 | 0 | 147.558 | 0 | 1.3089 | 0 | 1.4756 | 0 | 1.3089 | 1.4756 | 23.292 | 9.3662 | 21.9831
39009.4087 | 2031 | 0 | 39009.4087 | 2293 | 0 |  | 2123.5 | 2755.5 | 123.9927 | 0 | 139.9878 | 0 | 1.2399 | 0 | 1.3999 | 0 | 1.2399 | 1.3999 | 30.1516 | 15.2804 | 28.9117
39009.4105 | 2627 | 0 | 39009.4105 | 2547 | 0 |  | 2277.5 | 2909.5 | 160.3785 | 0 | 155.4945 | 0 | 1.6038 | 0 | 1.5549 | 0 | 1.6038 | 1.5549 | 0.62352 | 3.7841 | 0.98026
39009.4123 | 2219 | 0 | 39009.4123 | 2052 | 0 |  | 2431.5 | 3063.5 | 135.4701 | 0 | 125.2747 | 0 | 1.3547 | 0 | 1.2527 | 0 | 1.3547 | 1.2527 | 19.1248 | 28.8197 | 17.7701
39009.4141 | 2563 | 0 | 39009.4141 | 2238 | 0 |  | 2585.5 | 3217.5 | 156.4713 | 0 | 136.63 | 0 | 1.5647 | 0 | 1.3663 | 0 | 1.5647 | 1.3663 | 3.1362 | 18.1135 | 1.5715
39009.4158 | 2527 | 0 | 39009.4158 | 2333 | 0 |  | 2739.5 | 3371.5 | 154.2735 | 0 | 142.4298 | 0 | 1.5427 | 0 | 1.4243 | 0 | 1.5427 | 1.4243 | 4.6055 | 13.3039 | 3.0627
39009.4176 | 2261 | 0 | 39009.4176 | 2213 | 0 |  | 2893.5 | 3525.5 | 138.0342 | 0 | 135.1038 | 0 | 1.3803 | 0 | 1.351 | 0 | 1.3803 | 1.351 | 16.912 | 19.4478 | 15.5316

## C5-L11
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 158.5702 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable L |  | Odd
Time-79 | N11 | N12 | Time-80 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39009.3781 | 1 | 0 | 39009.3781 | 1 | 0 |  | -522.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3799 | 1 | 0 | 39009.3799 | 1 | 0 |  | -368.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3819 | 1 | 0 | 39009.382 | 1 | 0 |  | -189 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3837 | 1 | 0 | 39009.3837 | 1 | 0 |  | -35 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3855 | 1 | 0 | 39009.3855 | 1 | 0 |  | 119 | 751 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3873 | 1 | 0 | 39009.3873 | 1 | 0 |  | 273 | 905 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3891 | 1 | 0 | 39009.3891 | 1 | 0 |  | 427 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3908 | 1 | 0 | 39009.3909 | 1 | 0 |  | 581 | 1213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3926 | 1 | 0 | 39009.3927 | 1 | 0 |  | 735 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3944 | 1 | 0 | 39009.3944 | 1 | 0 |  | 889 | 1521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3962 | 1 | 0 | 39009.3962 | 1 | 0 |  | 1043 | 1675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.398 | 1 | 0 | 39009.398 | 1 | 0 |  | 1197 | 1829 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.3998 | 1 | 0 | 39009.3998 | 1 | 0 |  | 1351 | 1983 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.4015 | 3 | 0 | 39009.4016 | 1 | 0 |  | 1505 | 2137 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 86479.3333 | 259638 | 86479.3315
39009.4033 | 1 | 0 | 39009.4033 | 1 | 0 |  | 1659 | 2291 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259638 | 259638 | 259637.9994
39009.4051 | 2578 | 0 | 39009.4051 | 2513 | 0 |  | 1812.5 | 2444.5 | 157.3871 | 0 | 153.4188 | 0 | 1.5739 | 0 | 1.5342 | 0 | 1.5739 | 1.5342 | 0.75175 | 3.3577 | 0.82213
39009.4069 | 2004 | 0 | 39009.4069 | 2216 | 0 |  | 1966.5 | 2598.5 | 122.3443 | 0 | 135.2869 | 0 | 1.2234 | 0 | 1.3529 | 0 | 1.2234 | 1.3529 | 29.6098 | 17.2103 | 28.3863
39009.4087 | 2116 | 0 | 39009.4087 | 2541 | 0 |  | 2120.5 | 2752.5 | 129.1819 | 0 | 155.1282 | 0 | 1.2918 | 0 | 1.5513 | 0 | 1.2918 | 1.5513 | 22.7495 | 2.2188 | 21.4577
39009.4105 | 2210 | 0 | 39009.4105 | 2372 | 0 |  | 2274.5 | 2906.5 | 134.9206 | 0 | 144.8107 | 0 | 1.3492 | 0 | 1.4481 | 0 | 1.3492 | 1.4481 | 17.5285 | 9.5017 | 16.1793
39009.4122 | 2345 | 1 | 39009.4122 | 2097 | 0 |  | 2428.5 | 3060.5 | 143.1624 | 0.06105 | 128.022 | 0 | 1.4316 | 0.0006105 | 1.2802 | 0 | 1.431 | 1.2802 | 10.7863 | 23.8617 | 4842.7848
39009.414 | 2439 | 0 | 39009.414 | 2510 | 0 |  | 2582.5 | 3214.5 | 148.9011 | 0 | 153.2357 | 0 | 1.489 | 0 | 1.5324 | 0 | 1.489 | 1.5324 | 6.4936 | 3.4813 | 5.0046
39009.4158 | 2395 | 0 | 39009.4158 | 2581 | 0 |  | 2736.5 | 3368.5 | 146.2149 | 0 | 157.5702 | 0 | 1.4621 | 0 | 1.5757 | 0 | 1.4621 | 1.5757 | 8.4501 | 0.63464 | 6.988
39009.4176 | 2149 | 0 | 39009.4176 | 2329 | 0 |  | 2890.5 | 3522.5 | 131.1966 | 0 | 142.1856 | 0 | 1.312 | 0 | 1.4219 | 0 | 1.312 | 1.4219 | 20.8646 | 11.5234 | 19.5526

## C5-E8
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.1343 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 5 & 8 | Cable C | Odd - | Cable E |  | Even
Time-73 | N11 | N12 | Time-74 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R8-G | R5-8
39009.378 | 1 | 0 | 39009.378 | 1 | 0 |  | -530.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3798 | 1 | 0 | 39009.3798 | 1 | 0 |  | -377 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3818 | 1 | 0 | 39009.3819 | 1 | 0 |  | -197.5 | 434.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3836 | 1 | 0 | 39009.3836 | 1 | 0 |  | -43.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3854 | 1 | 0 | 39009.3854 | 1 | 0 |  | 110.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3872 | 1 | 0 | 39009.3872 | 1 | 0 |  | 264.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.389 | 1 | 0 | 39009.389 | 1 | 0 |  | 418.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3908 | 1 | 0 | 39009.3908 | 1 | 0 |  | 572.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3925 | 1 | 0 | 39009.3925 | 1 | 0 |  | 726.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3943 | 1 | 0 | 39009.3943 | 1 | 0 |  | 880.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3961 | 1 | 0 | 39009.3961 | 1 | 0 |  | 1034.5 | 1666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3979 | 1 | 0 | 39009.3979 | 1 | 0 |  | 1188.5 | 1820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.3997 | 1 | 0 | 39009.3997 | 1 | 0 |  | 1342.5 | 1974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.4014 | 1 | 0 | 39009.4015 | 1 | 0 |  | 1496.5 | 2128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39009.4032 | 2 | 0 | 39009.4032 | 7 | 0 |  | 1650.5 | 2282.5 | 0.1221 | 0 | 0.42735 | 0 | 0.001221 | 0 | 0.0042735 | 0 | 0.001221 | 0.0042735 | 131869 | 37605.4286 | 131868.9988
39009.405 | 2460 | 0 | 39009.405 | 1994 | 0 |  | 1804.5 | 2436.5 | 150.1832 | 0 | 121.7338 | 0 | 1.5018 | 0 | 1.2173 | 0 | 1.5018 | 1.2173 | 7.2919 | 32.3661 | 5.79
39009.4068 | 2073 | 0 | 39009.4068 | 2043 | 0 |  | 1958.5 | 2590.5 | 126.5568 | 0 | 124.7253 | 0 | 1.2656 | 0 | 1.2473 | 0 | 1.2656 | 1.2473 | 27.3218 | 29.1914 | 26.0562
39009.4086 | 2023 | 0 | 39009.4086 | 2488 | 0 |  | 2112.5 | 2744.5 | 123.5043 | 0 | 151.8926 | 0 | 1.235 | 0 | 1.5189 | 0 | 1.235 | 1.5189 | 30.4686 | 6.0844 | 29.2336
39009.4104 | 2316 | 0 | 39009.4104 | 2187 | 0 |  | 2266.5 | 2898.5 | 141.3919 | 0 | 133.5165 | 0 | 1.4139 | 0 | 1.3352 | 0 | 1.4139 | 1.3352 | 13.9629 | 20.685 | 12.5489
39009.4121 | 2620 | 0 | 39009.4122 | 2114 | 0 |  | 2420.5 | 3052.5 | 159.9512 | 0 | 129.0598 | 0 | 1.5995 | 0 | 1.2906 | 0 | 1.5995 | 1.2906 | 0.73969 | 24.8524 | 0.85982
39009.4139 | 2181 | 0 | 39009.4139 | 2360 | 0 |  | 2574.5 | 3206.5 | 133.1502 | 0 | 144.0781 | 0 | 1.3315 | 0 | 1.4408 | 0 | 1.3315 | 1.4408 | 21.017 | 11.8381 | 19.6855
39009.4157 | 2620 | 0 | 39009.4157 | 2623 | 0 |  | 2728.5 | 3360.5 | 159.9512 | 0 | 160.1343 | 0 | 1.5995 | 0 | 1.6013 | 0 | 1.5995 | 1.6013 | 0.73969 | 0.62448 | 0.85982
39009.4175 | 2275 | 0 | 39009.4175 | 2341 | 0 |  | 2882.5 | 3514.5 | 138.8889 | 0 | 142.9182 | 0 | 1.3889 | 0 | 1.4292 | 0 | 1.3889 | 1.4292 | 16.0167 | 12.7458 | 14.6278

## C5-E7
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.3407 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 5 & 7 | Cable C | Odd - | Cable E |  | Odd
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R7-G | R5-7
39009.378 | 1 | 0 | 39009.378 | 1 | 0 |  | -533.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3797 | 1 | 0 | 39009.3797 | 1 | 0 |  | -379.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3818 | 1 | 0 | 39009.3818 | 1 | 0 |  | -200 | 432 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3836 | 1 | 0 | 39009.3836 | 1 | 0 |  | -46 | 586 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3854 | 1 | 0 | 39009.3854 | 1 | 0 |  | 108 | 740 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3872 | 1 | 0 | 39009.3872 | 1 | 0 |  | 262 | 894 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3889 | 1 | 0 | 39009.389 | 1 | 0 |  | 416 | 1048 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3907 | 1 | 0 | 39009.3907 | 1 | 0 |  | 570 | 1202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262538 | 262538 | 262537.9994
39009.3925 | 1 | 0 | 39009.3925 | 2340 | 0 |  | 723.5 | 1355.5 | 0.06105 | 0 | 142.8571 | 0 | 0.0006105 | 0 | 1.4286 | 0 | 0.0006105 | 1.4286 | 262538 | 12.2385 | 262537.9994
39009.3943 | 1 | 0 | 39009.3943 | 2610 | 0 |  | 877.5 | 1509.5 | 0.06105 | 0 | 159.3407 | 0 | 0.0006105 | 0 | 1.5934 | 0 | 0.0006105 | 1.5934 | 262538 | 0.62759 | 262537.9994
39009.3961 | 1 | 0 | 39009.3961 | 2390 | 0 |  | 1031.5 | 1663.5 | 0.06105 | 0 | 145.9096 | 0 | 0.0006105 | 0 | 1.4591 | 0 | 0.0006105 | 1.4591 | 262538 | 9.8904 | 262537.9994
39009.3978 | 1 | 0 | 39009.3979 | 2032 | 0 |  | 1185.5 | 1817.5 | 0.06105 | 0 | 124.0537 | 0 | 0.0006105 | 0 | 1.2405 | 0 | 0.0006105 | 1.2405 | 262538 | 29.251 | 262537.9994
39009.3996 | 1 | 0 | 39009.3996 | 2075 | 0 |  | 1339.5 | 1971.5 | 0.06105 | 0 | 126.6789 | 0 | 0.0006105 | 0 | 1.2668 | 0 | 0.0006105 | 1.2668 | 262538 | 26.5725 | 262537.9994
39009.4014 | 1 | 0 | 39009.4014 | 2028 | 0 |  | 1493.5 | 2125.5 | 0.06105 | 0 | 123.8095 | 0 | 0.0006105 | 0 | 1.2381 | 0 | 0.0006105 | 1.2381 | 262538 | 29.5059 | 262537.9994
39009.4032 | 1 | 0 | 39009.4032 | 2477 | 0 |  | 1648 | 2280 | 0.06105 | 0 | 151.221 | 0 | 0.0006105 | 0 | 1.5122 | 0 | 0.0006105 | 1.5122 | 262538 | 6.0307 | 262537.9994
39009.405 | 2175 | 0 | 39009.405 | 2233 | 0 |  | 1801.5 | 2433.5 | 132.7839 | 0 | 136.3248 | 0 | 1.3278 | 0 | 1.3632 | 0 | 1.3278 | 1.3632 | 20.7531 | 17.6167 | 19.4253
39009.4068 | 2124 | 0 | 39009.4068 | 2468 | 0 |  | 1955.5 | 2587.5 | 129.6703 | 0 | 150.6716 | 0 | 1.2967 | 0 | 1.5067 | 0 | 1.2967 | 1.5067 | 23.6525 | 6.4173 | 22.3558
39009.4085 | 2440 | 0 | 39009.4086 | 2464 | 0 |  | 2109.5 | 2741.5 | 148.9621 | 0 | 150.4274 | 0 | 1.4896 | 0 | 1.5043 | 0 | 1.4896 | 1.5043 | 7.6385 | 6.5901 | 6.1489
39009.4103 | 2338 | 0 | 39009.4103 | 2279 | 1 |  | 2263.5 | 2895.5 | 142.735 | 0 | 139.1331 | 0.06105 | 1.4274 | 0 | 1.3913 | 0.0006105 | 1.4274 | 1.3907 | 12.3345 | 15.2932 | 10.9071
39009.4121 | 2467 | 0 | 39009.4121 | 2393 | 1 |  | 2417.5 | 3049.5 | 150.6105 | 0 | 146.0928 | 0.06105 | 1.5061 | 0 | 1.4609 | 0.0006105 | 1.5061 | 1.4603 | 6.4605 | 9.7985 | 4.9544
39009.4139 | 2141 | 0 | 39009.4139 | 2055 | 0 |  | 2571.5 | 3203.5 | 130.7082 | 0 | 125.4579 | 0 | 1.3071 | 0 | 1.2546 | 0 | 1.3071 | 1.2546 | 22.6707 | 27.8044 | 21.3636
39009.4157 | 2199 | 0 | 39009.4157 | 2168 | 0 |  | 2725.5 | 3357.5 | 134.2491 | 0 | 132.3565 | 0 | 1.3425 | 0 | 1.3236 | 0 | 1.3425 | 1.3236 | 19.4352 | 21.143 | 18.0927
39009.4175 | 2441 | 0 | 39009.4175 | 2139 | 0 |  | 2879.5 | 3511.5 | 149.0232 | 0 | 130.5861 | 0 | 1.4902 | 0 | 1.3059 | 0 | 1.4902 | 1.3059 | 7.5944 | 22.7854 | 6.1042

## C5-C6
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.2564 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39009.3779 | 1 | 0 | 39009.3779 | 1 | 0 |  | -536.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3797 | 1 | 0 | 39009.3797 | 1 | 0 |  | -382.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3818 | 1 | 0 | 39009.3818 | 1 | 0 |  | -203 | 429 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3836 | 1 | 0 | 39009.3836 | 1 | 0 |  | -49 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3853 | 1 | 0 | 39009.3854 | 1 | 0 |  | 105 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3871 | 1 | 0 | 39009.3871 | 1 | 0 |  | 259 | 891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3889 | 1 | 0 | 39009.3889 | 1 | 0 |  | 413 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3907 | 1 | 0 | 39009.3907 | 1 | 0 |  | 567 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3925 | 1 | 0 | 39009.3925 | 1 | 0 |  | 721 | 1353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3942 | 1 | 0 | 39009.3943 | 1 | 0 |  | 875 | 1507 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.396 | 1 | 0 | 39009.3961 | 1 | 0 |  | 1029 | 1661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3978 | 1 | 0 | 39009.3978 | 1 | 0 |  | 1183 | 1815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.3996 | 1 | 0 | 39009.3996 | 1 | 0 |  | 1337 | 1969 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.4014 | 1 | 0 | 39009.4014 | 1 | 0 |  | 1491 | 2123 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264038 | 264038 | 264037.9994
39009.4032 | 4 | 0 | 39009.4032 | 2 | 1 |  | 1645 | 2277 | 0.2442 | 0 | 0.1221 | 0.06105 | 0.002442 | 0 | 0.001221 | 0.0006105 | 0.002442 | 0.0006105 | 65934.5 | 264038 | 65934.4976
39009.4049 | 2546 | 0 | 39009.405 | 2338 | 0 |  | 1799 | 2431 | 155.4335 | 0 | 142.735 | 0 | 1.5543 | 0 | 1.4274 | 0 | 1.5543 | 1.4274 | 3.7463 | 12.976 | 2.1919
39009.4067 | 2137 | 0 | 39009.4067 | 2605 | 0 |  | 1952.5 | 2584.5 | 130.464 | 0 | 159.0354 | 0 | 1.3046 | 0 | 1.5904 | 0 | 1.3046 | 1.5904 | 23.6022 | 1.3965 | 22.2976
39009.4085 | 2561 | 0 | 39009.4085 | 2408 | 0 |  | 2107 | 2739 | 156.3492 | 0 | 147.0085 | 0 | 1.5635 | 0 | 1.4701 | 0 | 1.5635 | 1.4701 | 3.1386 | 9.6919 | 1.5751
39009.4103 | 2029 | 0 | 39009.4103 | 2392 | 0 |  | 2260.5 | 2892.5 | 123.8706 | 0 | 146.0317 | 0 | 1.2387 | 0 | 1.4603 | 0 | 1.2387 | 1.4603 | 30.1814 | 10.4256 | 28.9427
39009.4121 | 2115 | 0 | 39009.4121 | 2090 | 0 |  | 2414.5 | 3046.5 | 129.1209 | 0 | 127.5946 | 0 | 1.2912 | 0 | 1.2759 | 0 | 1.2912 | 1.2759 | 24.8879 | 26.3818 | 23.5967
39009.4139 | 2535 | 0 | 39009.4139 | 2345 | 0 |  | 2568.5 | 3200.5 | 154.7619 | 0 | 143.1624 | 0 | 1.5476 | 0 | 1.4316 | 0 | 1.5476 | 1.4316 | 4.1964 | 12.6388 | 2.6488
39009.4156 | 2292 | 0 | 39009.4156 | 2131 | 0 |  | 2722.5 | 3354.5 | 139.9267 | 0 | 130.0977 | 0 | 1.3993 | 0 | 1.301 | 0 | 1.3993 | 1.301 | 15.2435 | 23.9503 | 13.8442
39009.4174 | 2480 | 0 | 39009.4174 | 2625 | 0 |  | 2876.5 | 3508.5 | 151.4042 | 0 | 160.2564 | 0 | 1.514 | 0 | 1.6026 | 0 | 1.514 | 1.6026 | 6.5073 | 0.624 | 4.9932

## B4-H10
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.0122 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable H |  | Even
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39009.3778 | 1 | 0 | 39009.3779 | 1 | 0 |  | -542 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3796 | 1 | 0 | 39009.3797 | 1 | 0 |  | -388 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3817 | 1 | 0 | 39009.3817 | 1 | 0 |  | -208.5 | 423.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3835 | 1 | 0 | 39009.3835 | 1 | 0 |  | -54.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3853 | 1 | 0 | 39009.3853 | 1 | 0 |  | 99.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3871 | 1 | 0 | 39009.3871 | 1 | 0 |  | 253.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3888 | 1 | 0 | 39009.3889 | 1 | 0 |  | 407.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3906 | 1 | 0 | 39009.3906 | 1 | 0 |  | 561.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3924 | 1 | 0 | 39009.3924 | 1 | 0 |  | 715.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3942 | 1 | 0 | 39009.3942 | 1 | 0 |  | 869.5 | 1501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.396 | 1 | 0 | 39009.396 | 1 | 0 |  | 1023.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3978 | 1 | 0 | 39009.3978 | 1 | 0 |  | 1177.5 | 1809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3995 | 1 | 0 | 39009.3995 | 1 | 0 |  | 1331.5 | 1963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.4013 | 1 | 0 | 39009.4013 | 1 | 0 |  | 1485.5 | 2117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.4031 | 1 | 0 | 39009.4031 | 1 | 0 |  | 1639.5 | 2271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.4049 | 713 | 0 | 39009.4049 | 1960 | 0 |  | 1793.5 | 2425.5 | 43.5287 | 0 | 119.6581 | 0 | 0.43529 | 0 | 1.1966 | 0 | 0.43529 | 1.1966 | 269.899 | 34.5602 | 269.4637
39009.4067 | 2239 | 0 | 39009.4067 | 2171 | 0 |  | 1947 | 2579 | 136.6911 | 0 | 132.5397 | 0 | 1.3669 | 0 | 1.3254 | 0 | 1.3669 | 1.3254 | 17.7928 | 21.4823 | 16.4259
39009.4084 | 2598 | 0 | 39009.4085 | 2073 | 0 |  | 2101 | 2733 | 158.6081 | 0 | 126.5568 | 0 | 1.5861 | 0 | 1.2656 | 0 | 1.5861 | 1.2656 | 1.5158 | 27.2253 | 0.070299
39009.4102 | 2621 | 0 | 39009.4102 | 2088 | 0 |  | 2255 | 2887 | 160.0122 | 0 | 127.4725 | 0 | 1.6001 | 0 | 1.2747 | 0 | 1.6001 | 1.2747 | 0.62495 | 26.3113 | 0.97517
39009.412 | 2094 | 0 | 39009.412 | 2572 | 0 |  | 2409 | 3041 | 127.8388 | 0 | 157.0208 | 0 | 1.2784 | 0 | 1.5702 | 0 | 1.2784 | 1.5702 | 25.9494 | 2.542 | 24.671
39009.4138 | 2039 | 0 | 39009.4138 | 2010 | 0 |  | 2563 | 3195 | 124.4811 | 0 | 122.7106 | 0 | 1.2448 | 0 | 1.2271 | 0 | 1.2448 | 1.2271 | 29.3467 | 31.2129 | 28.1019
39009.4156 | 2158 | 0 | 39009.4156 | 2441 | 0 |  | 2717 | 3349 | 131.746 | 0 | 149.0232 | 0 | 1.3175 | 0 | 1.4902 | 0 | 1.3175 | 1.4902 | 22.2141 | 8.0451 | 20.8966
39009.4173 | 2457 | 0 | 39009.4174 | 2143 | 0 |  | 2871 | 3503 | 150 | 0 | 130.8303 | 0 | 1.5 | 0 | 1.3083 | 0 | 1.5 | 1.3083 | 7.3415 | 23.0695 | 5.8415

## B4-H9
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 162.1722 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable H |  | Odd
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39009.3778 | 1 | 0 | 39009.3778 | 1 | 0 |  | -544.5 | 87.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3796 | 1 | 0 | 39009.3796 | 1 | 0 |  | -391 | 241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3817 | 1 | 0 | 39009.3817 | 1 | 0 |  | -211.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3835 | 1 | 0 | 39009.3835 | 1 | 0 |  | -57.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3852 | 1 | 0 | 39009.3853 | 1 | 0 |  | 96.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.387 | 1 | 0 | 39009.387 | 1 | 0 |  | 250.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3888 | 1 | 0 | 39009.3888 | 1 | 0 |  | 404.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3906 | 1 | 0 | 39009.3906 | 1 | 0 |  | 558.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3924 | 1 | 0 | 39009.3924 | 1 | 0 |  | 712.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3942 | 1 | 0 | 39009.3942 | 1 | 0 |  | 866.5 | 1498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3959 | 1 | 0 | 39009.3959 | 1 | 0 |  | 1020.5 | 1652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3977 | 1 | 0 | 39009.3977 | 1 | 0 |  | 1174.5 | 1806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.3995 | 1 | 0 | 39009.3995 | 1 | 0 |  | 1328.5 | 1960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.4013 | 1 | 0 | 39009.4013 | 1 | 0 |  | 1482.5 | 2114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.4031 | 1 | 0 | 39009.4031 | 1 | 0 |  | 1636.5 | 2268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265538 | 265538 | 265537.9994
39009.4048 | 159 | 1 | 39009.4049 | 2289 | 0 |  | 1790.5 | 2422.5 | 9.707 | 0.06105 | 139.7436 | 0 | 0.09707 | 0.0006105 | 1.3974 | 0 | 0.096459 | 1.3974 | 1645.5096 | 16.0498 | 34525.1841
39009.4066 | 2260 | 0 | 39009.4066 | 2098 | 0 |  | 1944.5 | 2576.5 | 137.9731 | 0 | 128.083 | 0 | 1.3797 | 0 | 1.2808 | 0 | 1.3797 | 1.2808 | 17.5389 | 26.6149 | 16.1592
39009.4084 | 2325 | 0 | 39009.4084 | 2455 | 0 |  | 2098.5 | 2730.5 | 141.9414 | 0 | 149.8779 | 0 | 1.4194 | 0 | 1.4988 | 0 | 1.4194 | 1.4988 | 14.2529 | 8.2029 | 12.8335
39009.4102 | 2591 | 0 | 39009.4102 | 2422 | 0 |  | 2252.5 | 2884.5 | 158.1807 | 0 | 147.8632 | 0 | 1.5818 | 0 | 1.4786 | 0 | 1.5818 | 1.4786 | 2.5234 | 9.6771 | 0.94154
39009.412 | 2401 | 0 | 39009.412 | 2144 | 0 |  | 2406.5 | 3038.5 | 146.5812 | 0 | 130.8913 | 0 | 1.4658 | 0 | 1.3089 | 0 | 1.4658 | 1.3089 | 10.6364 | 23.8983 | 9.1706
39009.4138 | 2480 | 0 | 39009.4138 | 2280 | 0 |  | 2560.5 | 3192.5 | 151.4042 | 0 | 139.1941 | 0 | 1.514 | 0 | 1.3919 | 0 | 1.514 | 1.3919 | 7.1121 | 16.5079 | 5.5981
39009.4155 | 2135 | 0 | 39009.4156 | 2337 | 0 |  | 2714.5 | 3346.5 | 130.3419 | 0 | 142.674 | 0 | 1.3034 | 0 | 1.4267 | 0 | 1.3034 | 1.4267 | 24.4206 | 13.6662 | 23.1172
39009.4173 | 2640 | 0 | 39009.4173 | 2031 | 0 |  | 2868.5 | 3500.5 | 161.1722 | 0 | 123.9927 | 0 | 1.6117 | 0 | 1.2399 | 0 | 1.6117 | 1.2399 | 0.62045 | 30.7917 | 0.99127

## B4-E8
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.6459 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable E |  | Even
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39009.3778 | 1 | 0 | 39009.3778 | 1 | 0 |  | -547.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3796 | 1 | 0 | 39009.3796 | 1 | 0 |  | -393.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3816 | 1 | 0 | 39009.3817 | 1 | 0 |  | -214 | 418 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3834 | 1 | 0 | 39009.3834 | 1 | 0 |  | -60 | 572 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3852 | 1 | 0 | 39009.3852 | 1 | 0 |  | 94 | 726 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.387 | 1 | 0 | 39009.387 | 1 | 0 |  | 248 | 880 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3888 | 1 | 0 | 39009.3888 | 1 | 0 |  | 402 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3906 | 1 | 0 | 39009.3906 | 1 | 0 |  | 556 | 1188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3923 | 2 | 0 | 39009.3924 | 1 | 0 |  | 710 | 1342 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 131469 | 263038 | 131468.9988
39009.3941 | 1 | 0 | 39009.3941 | 1 | 0 |  | 863.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3959 | 1 | 0 | 39009.3959 | 1 | 0 |  | 1017.5 | 1649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3977 | 1 | 0 | 39009.3977 | 1 | 0 |  | 1171.5 | 1803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3995 | 1 | 0 | 39009.3995 | 1 | 0 |  | 1325.5 | 1957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.4013 | 1 | 0 | 39009.4013 | 1 | 0 |  | 1479.5 | 2111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.403 | 1 | 0 | 39009.403 | 3 | 0 |  | 1633.5 | 2265.5 | 0.06105 | 0 | 0.18315 | 0 | 0.0006105 | 0 | 0.0018315 | 0 | 0.0006105 | 0.0018315 | 263038 | 87612.6667 | 263037.9994
39009.4048 | 34 | 0 | 39009.4048 | 2044 | 0 |  | 1787.5 | 2419.5 | 2.0757 | 0 | 124.7863 | 0 | 0.020757 | 0 | 1.2479 | 0 | 0.020757 | 1.2479 | 7639.3529 | 28.7368 | 7639.3322
39009.4066 | 2289 | 0 | 39009.4066 | 2046 | 0 |  | 1941.5 | 2573.5 | 139.7436 | 0 | 124.9084 | 0 | 1.3974 | 0 | 1.2491 | 0 | 1.3974 | 1.2491 | 14.9576 | 28.6109 | 13.5602
39009.4084 | 2435 | 0 | 39009.4084 | 2234 | 0 |  | 2095.5 | 2727.5 | 148.6569 | 0 | 136.3858 | 0 | 1.4866 | 0 | 1.3639 | 0 | 1.4866 | 1.3639 | 8.0649 | 17.7878 | 6.5783
39009.4102 | 2426 | 0 | 39009.4102 | 2093 | 0 |  | 2249.5 | 2881.5 | 148.1074 | 0 | 127.7778 | 0 | 1.4811 | 0 | 1.2778 | 0 | 1.4811 | 1.2778 | 8.4658 | 25.7229 | 6.9847
39009.4119 | 2084 | 0 | 39009.412 | 2257 | 0 |  | 2403.5 | 3035.5 | 127.2283 | 0 | 137.79 | 0 | 1.2723 | 0 | 1.3779 | 0 | 1.2723 | 1.3779 | 26.2658 | 16.5875 | 24.9936
39009.4137 | 2045 | 0 | 39009.4137 | 2315 | 0 |  | 2557.5 | 3189.5 | 124.8474 | 0 | 141.3309 | 0 | 1.2485 | 0 | 1.4133 | 0 | 1.2485 | 1.4133 | 28.6738 | 13.6665 | 27.4254
39009.4155 | 2615 | 0 | 39009.4155 | 2074 | 0 |  | 2711.5 | 3343.5 | 159.6459 | 0 | 126.6178 | 0 | 1.5965 | 0 | 1.2662 | 0 | 1.5965 | 1.2662 | 0.62639 | 26.8746 | 0.97007
39009.4173 | 2022 | 0 | 39009.4173 | 2334 | 0 |  | 2865.5 | 3497.5 | 123.4432 | 0 | 142.4908 | 0 | 1.2344 | 0 | 1.4249 | 0 | 1.2344 | 1.4249 | 30.1375 | 12.7412 | 28.9031

## B4-E7
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.6838 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable E |  | Odd
Time-59 | N11 | N12 | Time-60 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39009.3778 | 1 | 0 | 39009.3778 | 1 | 0 |  | -550.5 | 81.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3795 | 1 | 0 | 39009.3795 | 1 | 0 |  | -396.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3816 | 1 | 0 | 39009.3816 | 1 | 0 |  | -217 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3834 | 1 | 0 | 39009.3834 | 1 | 0 |  | -63 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3852 | 1 | 0 | 39009.3852 | 1 | 0 |  | 91 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.387 | 1 | 0 | 39009.387 | 1 | 0 |  | 245 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3887 | 1 | 0 | 39009.3888 | 1 | 0 |  | 399 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3905 | 1 | 0 | 39009.3905 | 1 | 0 |  | 553 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39009.3923 | 1 | 0 | 39009.3923 | 2005 | 0 |  | 707 | 1339 | 0.06105 | 0 | 122.4054 | 0 | 0.0006105 | 0 | 1.2241 | 0 | 0.0006105 | 1.2241 | 264738 | 32.0888 | 264737.9994
39009.3941 | 1 | 0 | 39009.3941 | 2224 | 0 |  | 861 | 1493 | 0.06105 | 0 | 135.7753 | 0 | 0.0006105 | 0 | 1.3578 | 0 | 0.0006105 | 1.3578 | 264738 | 19.0818 | 264737.9994
39009.3959 | 1 | 0 | 39009.3959 | 2311 | 0 |  | 1015 | 1647 | 0.06105 | 0 | 141.0867 | 0 | 0.0006105 | 0 | 1.4109 | 0 | 0.0006105 | 1.4109 | 264738 | 14.5989 | 264737.9994
39009.3977 | 1 | 0 | 39009.3977 | 2545 | 0 |  | 1169 | 1801 | 0.06105 | 0 | 155.3724 | 0 | 0.0006105 | 0 | 1.5537 | 0 | 0.0006105 | 1.5537 | 264738 | 4.0621 | 264737.9994
39009.3994 | 1 | 0 | 39009.3995 | 2366 | 0 |  | 1323 | 1955 | 0.06105 | 0 | 144.4444 | 0 | 0.0006105 | 0 | 1.4444 | 0 | 0.0006105 | 1.4444 | 264738 | 11.9349 | 264737.9994
39009.4012 | 1 | 0 | 39009.4012 | 2203 | 0 |  | 1477 | 2109 | 0.06105 | 0 | 134.4933 | 0 | 0.0006105 | 0 | 1.3449 | 0 | 0.0006105 | 1.3449 | 264738 | 20.217 | 264737.9994
39009.403 | 1 | 0 | 39009.403 | 2275 | 0 |  | 1631 | 2263 | 0.06105 | 0 | 138.8889 | 0 | 0.0006105 | 0 | 1.3889 | 0 | 0.0006105 | 1.3889 | 264738 | 16.4123 | 264737.9994
39009.4048 | 25 | 0 | 39009.4048 | 2365 | 0 |  | 1785 | 2417 | 1.5263 | 0 | 144.3834 | 0 | 0.015263 | 0 | 1.4438 | 0 | 0.015263 | 1.4438 | 10493.52 | 11.9822 | 10493.5047
39009.4066 | 2586 | 0 | 39009.4066 | 2377 | 0 |  | 1938.5 | 2570.5 | 157.8755 | 0 | 145.116 | 0 | 1.5788 | 0 | 1.4512 | 0 | 1.5788 | 1.4512 | 2.4122 | 11.4169 | 0.83347
39009.4083 | 2327 | 0 | 39009.4084 | 2559 | 0 |  | 2092.5 | 2724.5 | 142.0635 | 0 | 156.2271 | 0 | 1.4206 | 0 | 1.5623 | 0 | 1.4206 | 1.5623 | 13.8109 | 3.4928 | 12.3903
39009.4101 | 2043 | 1 | 39009.4101 | 2627 | 0 |  | 2246.5 | 2878.5 | 124.7253 | 0.06105 | 160.3785 | 0 | 1.2473 | 0.0006105 | 1.6038 | 0 | 1.2466 | 1.6038 | 31.5445 | 0.81386 | 487.9075
39009.4119 | 2072 | 0 | 39009.4119 | 2282 | 0 |  | 2401 | 3033 | 126.4957 | 0 | 139.3162 | 0 | 1.265 | 0 | 1.3932 | 0 | 1.265 | 1.3932 | 27.8176 | 16.0552 | 26.5526
39009.4137 | 2507 | 0 | 39009.4137 | 2073 | 0 |  | 2554.5 | 3186.5 | 153.0525 | 0 | 126.5568 | 0 | 1.5305 | 0 | 1.2656 | 0 | 1.5305 | 1.2656 | 5.6394 | 27.7559 | 4.1089
39009.4155 | 2419 | 0 | 39009.4155 | 2370 | 0 |  | 2708.5 | 3340.5 | 147.6801 | 0 | 144.6886 | 0 | 1.4768 | 0 | 1.4469 | 0 | 1.4768 | 1.4469 | 9.4824 | 11.746 | 8.0056
39009.4173 | 2632 | 0 | 39009.4173 | 2613 | 0 |  | 2862.5 | 3494.5 | 160.6838 | 0 | 159.5238 | 0 | 1.6068 | 0 | 1.5952 | 0 | 1.6068 | 1.5952 | 0.62234 | 1.354 | 0.9845

## B4-C6
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.6459 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-57 | N11 | N12 | Time-58 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39009.3777 | 1 | 0 | 39009.3777 | 1 | 0 |  | -553 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3795 | 1 | 0 | 39009.3795 | 1 | 0 |  | -399 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3816 | 1 | 0 | 39009.3816 | 1 | 0 |  | -219.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3834 | 1 | 0 | 39009.3834 | 1 | 0 |  | -65.5 | 566.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3852 | 1 | 0 | 39009.3852 | 1 | 0 |  | 88.5 | 720.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3869 | 1 | 0 | 39009.3869 | 1 | 0 |  | 242.5 | 874.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3887 | 1 | 0 | 39009.3887 | 1 | 0 |  | 396.5 | 1028.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3905 | 1 | 0 | 39009.3905 | 1 | 0 |  | 550.5 | 1182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3923 | 1 | 0 | 39009.3923 | 1 | 0 |  | 704 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3941 | 1 | 0 | 39009.3941 | 1 | 0 |  | 858 | 1490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3958 | 1 | 0 | 39009.3959 | 1 | 0 |  | 1012.5 | 1644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3976 | 1 | 0 | 39009.3976 | 1 | 0 |  | 1166 | 1798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.3994 | 1 | 0 | 39009.3994 | 1 | 0 |  | 1320 | 1952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.4012 | 1 | 0 | 39009.4012 | 1 | 0 |  | 1474 | 2106 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.403 | 1 | 0 | 39009.403 | 1 | 0 |  | 1628 | 2260 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263038 | 263038 | 263037.9994
39009.4047 | 1160 | 1000 | 39009.4048 | 1068 | 998 |  | 1782 | 2414 | 70.8181 | 61.0501 | 65.2015 | 60.928 | 0.70818 | 0.6105 | 0.65201 | 0.60928 | 0.09768 | 0.042735 | 722.949 | 2297.544 | 45.1719
39009.4065 | 2027 | 0 | 39009.4066 | 2282 | 0 |  | 1936 | 2568 | 123.7485 | 0 | 139.3162 | 0 | 1.2375 | 0 | 1.3932 | 0 | 1.2375 | 1.3932 | 29.8165 | 15.3103 | 28.579
39009.4083 | 2468 | 0 | 39009.4083 | 2275 | 0 |  | 2090 | 2722 | 150.6716 | 0 | 138.8889 | 0 | 1.5067 | 0 | 1.3889 | 0 | 1.5067 | 1.3889 | 6.6199 | 15.6651 | 5.1132
39009.4101 | 2403 | 0 | 39009.4101 | 2018 | 0 |  | 2244 | 2876 | 146.7033 | 0 | 123.199 | 0 | 1.467 | 0 | 1.232 | 0 | 1.467 | 1.232 | 9.504 | 30.3954 | 8.0369
39009.4119 | 2564 | 0 | 39009.4119 | 2615 | 0 |  | 2398 | 3030 | 156.5324 | 0 | 159.6459 | 0 | 1.5653 | 0 | 1.5965 | 0 | 1.5653 | 1.5965 | 2.6279 | 0.62639 | 1.0626
39009.4137 | 2066 | 0 | 39009.4137 | 2216 | 0 |  | 2552 | 3184 | 126.1294 | 0 | 135.2869 | 0 | 1.2613 | 0 | 1.3529 | 0 | 1.2613 | 1.3529 | 27.3659 | 18.7446 | 26.1046
39009.4154 | 2121 | 0 | 39009.4155 | 2418 | 0 |  | 2706 | 3338 | 129.4872 | 0 | 147.619 | 0 | 1.2949 | 0 | 1.4762 | 0 | 1.2949 | 1.4762 | 24.0632 | 8.8246 | 22.7683
39009.4172 | 2540 | 0 | 39009.4172 | 2028 | 0 |  | 2860 | 3492 | 155.0672 | 0 | 123.8095 | 0 | 1.5507 | 0 | 1.2381 | 0 | 1.5507 | 1.2381 | 3.5976 | 29.7525 | 2.047

## B4-C5
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.7448 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39009.3777 | 1 | 0 | 39009.3777 | 1 | 0 |  | -556 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3795 | 1 | 0 | 39009.3795 | 1 | 0 |  | -402 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3816 | 1 | 0 | 39009.3816 | 1 | 0 |  | -222.5 | 409.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3833 | 1 | 0 | 39009.3833 | 1 | 0 |  | -68.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3851 | 1 | 0 | 39009.3851 | 1 | 0 |  | 85.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3869 | 1 | 0 | 39009.3869 | 1 | 0 |  | 239.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3887 | 1 | 0 | 39009.3887 | 1 | 0 |  | 393.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3905 | 922 | 976 | 39009.3905 | 970 | 1018 |  | 547.5 | 1179.5 | 56.2882 | 59.5849 | 59.2186 | 62.149 | 0.56288 | 0.59585 | 0.59219 | 0.62149 | 0.032967 | 0.029304 | 4350.8755 | 6826.0792 | 75.8741
39009.3922 | 1184 | 1201 | 39009.3923 | 1147 | 1125 |  | 701.5 | 1333.5 | 72.2833 | 73.3211 | 70.0244 | 68.6813 | 0.72283 | 0.73321 | 0.70024 | 0.68681 | 0.010379 | 0.013431 | 96471.244 | 7757.8873 | 21.7332
39009.394 | 1136 | 1113 | 39009.394 | 946 | 988 |  | 855.5 | 1487.5 | 69.3529 | 67.9487 | 57.7534 | 60.3175 | 0.69353 | 0.67949 | 0.57753 | 0.60317 | 0.014042 | 0.025641 | 19531.7976 | 7297.5416 | 35.4868
39009.3958 | 1113 | 1171 | 39009.3958 | 1104 | 1083 |  | 1009.5 | 1641.5 | 67.9487 | 71.4896 | 67.3993 | 66.1172 | 0.67949 | 0.7149 | 0.67399 | 0.66117 | 0.035409 | 0.012821 | 1700.6154 | 3620.6128 | 30.3638
39009.3976 | 1119 | 1175 | 39009.3976 | 972 | 1017 |  | 1163.5 | 1795.5 | 68.315 | 71.7338 | 59.3407 | 62.0879 | 0.68315 | 0.71734 | 0.59341 | 0.62088 | 0.034188 | 0.027473 | 3341.7226 | 11515.2521 | 29.9847
39009.3994 | 986 | 964 | 39009.3994 | 1063 | 1040 |  | 1317.5 | 1949.5 | 60.1954 | 58.8523 | 64.8962 | 63.4921 | 0.60195 | 0.58852 | 0.64896 | 0.63492 | 0.013431 | 0.014042 | 12854.7021 | 10640.008 | 71.8743
39009.4012 | 995 | 1092 | 39009.4012 | 1010 | 973 |  | 1471.5 | 2103.5 | 60.7448 | 66.6667 | 61.6606 | 59.4017 | 0.60745 | 0.66667 | 0.61661 | 0.59402 | 0.059219 | 0.022589 | 1390.7428 | 4973.4525 | 50.4849
39009.4029 | 935 | 911 | 39009.403 | 1089 | 1137 |  | 1625.5 | 2257.5 | 57.0818 | 55.6166 | 66.4835 | 69.4139 | 0.57082 | 0.55617 | 0.66484 | 0.69414 | 0.014652 | 0.029304 | 26107.7973 | 5225.5846 | 86.5307
39009.4047 | 992 | 931 | 39009.4047 | 1070 | 1074 |  | 1779.5 | 2411.5 | 60.5617 | 56.8376 | 65.3236 | 65.5678 | 0.60562 | 0.56838 | 0.65324 | 0.65568 | 0.037241 | 0.002442 | 1746.6752 | 2747.3093 | 75.2813
39009.4065 | 2465 | 0 | 39009.4065 | 2293 | 0 |  | 1933 | 2565 | 150.4884 | 0 | 139.9878 | 0 | 1.5049 | 0 | 1.3999 | 0 | 1.5049 | 1.3999 | 7.4799 | 15.5421 | 5.975
39009.4083 | 2530 | 0 | 39009.4083 | 2569 | 0 |  | 2087.5 | 2719.5 | 154.4567 | 0 | 156.8376 | 0 | 1.5446 | 0 | 1.5684 | 0 | 1.5446 | 1.5684 | 4.7186 | 3.1288 | 3.174
39009.4101 | 2083 | 0 | 39009.4101 | 2325 | 0 |  | 2241 | 2873 | 127.1673 | 0 | 141.9414 | 0 | 1.2717 | 0 | 1.4194 | 0 | 1.2717 | 1.4194 | 27.1906 | 13.9518 | 25.9189
39009.4118 | 2021 | 0 | 39009.4119 | 2253 | 0 |  | 2395 | 3027 | 123.3822 | 0 | 137.5458 | 0 | 1.2338 | 0 | 1.3755 | 0 | 1.2338 | 1.3755 | 31.0925 | 17.5934 | 29.8587
39009.4136 | 2278 | 0 | 39009.4136 | 2625 | 0 |  | 2549 | 3181 | 139.072 | 0 | 160.2564 | 0 | 1.3907 | 0 | 1.6026 | 0 | 1.3907 | 1.6026 | 16.3029 | 0.92876 | 14.9122
39009.4154 | 2487 | 0 | 39009.4154 | 2209 | 0 |  | 2703 | 3335 | 151.8315 | 0 | 134.8596 | 0 | 1.5183 | 0 | 1.3486 | 0 | 1.5183 | 1.3486 | 6.5292 | 19.9357 | 5.0108
39009.4172 | 2592 | 0 | 39009.4172 | 2633 | 0 |  | 2857 | 3489 | 158.2418 | 0 | 160.7448 | 0 | 1.5824 | 0 | 1.6074 | 0 | 1.5824 | 1.6074 | 2.2137 | 0.6221 | 0.63132

## B3-H10
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.3175 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 10 | Cable B | Odd - | Cable H |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39009.3776 | 1 | 0 | 39009.3776 | 1 | 0 |  | -561.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3794 | 1 | 0 | 39009.3794 | 1 | 0 |  | -407.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3815 | 1 | 0 | 39009.3815 | 1 | 0 |  | -228 | 404 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3833 | 1 | 0 | 39009.3833 | 1 | 0 |  | -74 | 558 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.385 | 1 | 0 | 39009.3851 | 1 | 0 |  | 80 | 712 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3868 | 1 | 0 | 39009.3869 | 1 | 0 |  | 234 | 866 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3886 | 1 | 0 | 39009.3886 | 1 | 0 |  | 388 | 1020 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3904 | 1 | 0 | 39009.3904 | 1 | 0 |  | 542 | 1174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3922 | 1 | 0 | 39009.3922 | 1 | 0 |  | 696 | 1328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.394 | 1 | 0 | 39009.394 | 1 | 0 |  | 850 | 1482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.3957 | 2583 | 1 | 39009.3958 | 1 | 0 |  | 1003.5 | 1635.5 | 157.6923 | 0.06105 | 0.06105 | 0 | 1.5769 | 0.0006105 | 0.0006105 | 0 | 1.5763 | 0.0006105 | 2.2998 | 264138.0002 | 5835.7906
39009.3975 | 2069 | 1 | 39009.3975 | 2 | 0 |  | 1158 | 1790 | 126.3126 | 0.06105 | 0.1221 | 0 | 1.2631 | 0.0006105 | 0.001221 | 0 | 1.2625 | 0.001221 | 27.7263 | 132018.9999 | 57194.6769
39009.3993 | 2090 | 1 | 39009.3993 | 1 | 0 |  | 1311.5 | 1943.5 | 127.5946 | 0.06105 | 0.06105 | 0 | 1.2759 | 0.0006105 | 0.0006105 | 0 | 1.2753 | 0.0006105 | 26.4423 | 264138 | 55117.1332
39009.4011 | 2203 | 1 | 39009.4011 | 1 | 0 |  | 1465.5 | 2097.5 | 134.4933 | 0.06105 | 0.06105 | 0 | 1.3449 | 0.0006105 | 0.0006105 | 0 | 1.3443 | 0.0006105 | 19.9537 | 264138 | 43821.4097
39009.4029 | 1 | 0 | 39009.4029 | 1 | 0 |  | 1619.5 | 2251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264138 | 264138 | 264137.9994
39009.4047 | 1 | 0 | 39009.4047 | 2346 | 0 |  | 1773.5 | 2405.5 | 0.06105 | 0 | 143.2234 | 0 | 0.0006105 | 0 | 1.4322 | 0 | 0.0006105 | 1.4322 | 264138 | 12.6334 | 264137.9994
39009.4064 | 2596 | 0 | 39009.4064 | 2246 | 0 |  | 1927.5 | 2559.5 | 158.486 | 0 | 137.1184 | 0 | 1.5849 | 0 | 1.3712 | 0 | 1.5849 | 1.3712 | 1.7866 | 17.6483 | 0.20174
39009.4082 | 2555 | 0 | 39009.4082 | 2564 | 0 |  | 2081.5 | 2713.5 | 155.9829 | 0 | 156.5324 | 0 | 1.5598 | 0 | 1.5653 | 0 | 1.5598 | 1.5653 | 3.42 | 3.0569 | 1.8601
39009.41 | 2121 | 0 | 39009.41 | 2090 | 0 |  | 2235.5 | 2867.5 | 129.4872 | 0 | 127.5946 | 0 | 1.2949 | 0 | 1.2759 | 0 | 1.2949 | 1.2759 | 24.5818 | 26.4297 | 23.2869
39009.4118 | 2047 | 0 | 39009.4118 | 2626 | 0 |  | 2389.5 | 3021.5 | 124.9695 | 0 | 160.3175 | 0 | 1.2497 | 0 | 1.6032 | 0 | 1.2497 | 1.6032 | 29.0855 | 0.62376 | 27.8358
39009.4136 | 2617 | 0 | 39009.4136 | 2115 | 0 |  | 2543.5 | 3175.5 | 159.768 | 0 | 129.1209 | 0 | 1.5977 | 0 | 1.2912 | 0 | 1.5977 | 1.2912 | 0.96981 | 24.9352 | 0.62787
39009.4153 | 2097 | 0 | 39009.4154 | 2359 | 0 |  | 2697.5 | 3329.5 | 128.022 | 0 | 144.0171 | 0 | 1.2802 | 0 | 1.4402 | 0 | 1.2802 | 1.4402 | 26.0076 | 12.0127 | 24.7274
39009.4171 | 2273 | 0 | 39009.4171 | 2061 | 0 |  | 2851.5 | 3483.5 | 138.7668 | 0 | 125.8242 | 0 | 1.3877 | 0 | 1.2582 | 0 | 1.3877 | 1.2582 | 16.2508 | 28.2086 | 14.8631

## B3-H9
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.2186 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable H |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39009.3776 | 1 | 0 | 39009.3776 | 1 | 0 |  | -564.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3794 | 1 | 0 | 39009.3794 | 1 | 0 |  | -410.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3814 | 1 | 0 | 39009.3815 | 1 | 0 |  | -231 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3832 | 1 | 0 | 39009.3833 | 1 | 0 |  | -77 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.385 | 1 | 0 | 39009.385 | 1 | 0 |  | 77 | 709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3868 | 1 | 0 | 39009.3868 | 1 | 0 |  | 231 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3886 | 1 | 0 | 39009.3886 | 1 | 0 |  | 385 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3904 | 1 | 0 | 39009.3904 | 1 | 0 |  | 539 | 1171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3921 | 1 | 0 | 39009.3922 | 1 | 0 |  | 693 | 1325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3939 | 1 | 0 | 39009.3939 | 1 | 0 |  | 847 | 1479 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.3957 | 2477 | 1 | 39009.3957 | 1 | 0 |  | 1001 | 1633 | 151.221 | 0.06105 | 0.06105 | 0 | 1.5122 | 0.0006105 | 0.0006105 | 0 | 1.5116 | 0.0006105 | 5.9523 | 262338 | 14632.4223
39009.3975 | 2101 | 1 | 39009.3975 | 1 | 0 |  | 1155 | 1787 | 128.2662 | 0.06105 | 0.06105 | 0 | 1.2827 | 0.0006105 | 0.0006105 | 0 | 1.2821 | 0.0006105 | 24.9229 | 262338 | 52218.0951
39009.3993 | 2268 | 1 | 39009.3993 | 2 | 0 |  | 1309 | 1941 | 138.4615 | 0.06105 | 0.1221 | 0 | 1.3846 | 0.0006105 | 0.001221 | 0 | 1.384 | 0.001221 | 15.7203 | 131119 | 35510.917
39009.4011 | 2608 | 1 | 39009.4011 | 1 | 0 |  | 1463 | 2095 | 159.2186 | 0.06105 | 0.06105 | 0 | 1.5922 | 0.0006105 | 0.0006105 | 0 | 1.5916 | 0.0006105 | 0.62831 | 262338.0003 | 1537.414
39009.4028 | 1 | 0 | 39009.4029 | 1 | 0 |  | 1617 | 2249 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262338 | 262338 | 262337.9994
39009.4046 | 1 | 0 | 39009.4046 | 2124 | 0 |  | 1771 | 2403 | 0.06105 | 0 | 129.6703 | 0 | 0.0006105 | 0 | 1.2967 | 0 | 0.0006105 | 1.2967 | 262338 | 23.5584 | 262337.9994
39009.4064 | 2004 | 0 | 39009.4064 | 2253 | 0 |  | 1925 | 2557 | 122.3443 | 0 | 137.5458 | 0 | 1.2234 | 0 | 1.3755 | 0 | 1.2234 | 1.3755 | 30.9571 | 16.4838 | 29.7336
39009.4082 | 2161 | 0 | 39009.4082 | 2266 | 0 |  | 2078.5 | 2710.5 | 131.9292 | 0 | 138.3394 | 0 | 1.3193 | 0 | 1.3834 | 0 | 1.3193 | 1.3834 | 21.4429 | 15.8155 | 20.1236
39009.41 | 2381 | 0 | 39009.41 | 2351 | 0 |  | 2232.5 | 2864.5 | 145.3602 | 0 | 143.5287 | 0 | 1.4536 | 0 | 1.4353 | 0 | 1.4536 | 1.4353 | 10.2218 | 11.6282 | 8.7682
39009.4117 | 2097 | 0 | 39009.4118 | 2349 | 0 |  | 2387 | 3019 | 128.022 | 0 | 143.4066 | 0 | 1.2802 | 0 | 1.4341 | 0 | 1.2802 | 1.4341 | 25.1493 | 11.7233 | 23.869
39009.4135 | 2273 | 0 | 39009.4135 | 2135 | 0 |  | 2540.5 | 3172.5 | 138.7668 | 0 | 130.3419 | 0 | 1.3877 | 0 | 1.3034 | 0 | 1.3877 | 1.3034 | 15.4589 | 22.9218 | 14.0712
39009.4153 | 2136 | 0 | 39009.4153 | 2145 | 0 |  | 2694.5 | 3326.5 | 130.4029 | 0 | 130.9524 | 0 | 1.304 | 0 | 1.3095 | 0 | 1.304 | 1.3095 | 22.8642 | 22.3487 | 21.5602
39009.4171 | 2587 | 0 | 39009.4171 | 2089 | 0 |  | 2848.5 | 3480.5 | 157.9365 | 0 | 127.5336 | 0 | 1.5794 | 0 | 1.2753 | 0 | 1.5794 | 1.2753 | 1.4449 | 25.6285 | 0.13445

## B3-E8
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.8059 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable E |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39009.3776 | 1 | 0 | 39009.3776 | 1 | 0 |  | -567 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3793 | 1 | 0 | 39009.3794 | 1 | 0 |  | -413.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3814 | 1 | 0 | 39009.3814 | 1 | 0 |  | -233.5 | 398.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3832 | 1 | 0 | 39009.3832 | 1 | 0 |  | -79.5 | 552.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.385 | 1 | 0 | 39009.385 | 1 | 0 |  | 74.5 | 706.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3868 | 1 | 0 | 39009.3868 | 1 | 0 |  | 228.5 | 860.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3886 | 1 | 0 | 39009.3886 | 1 | 0 |  | 382.5 | 1014.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3903 | 1 | 0 | 39009.3903 | 1 | 0 |  | 536.5 | 1168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3921 | 1 | 0 | 39009.3921 | 1 | 0 |  | 690.5 | 1322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3939 | 1 | 0 | 39009.3939 | 1 | 0 |  | 844 | 1476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39009.3957 | 2610 | 1 | 39009.3957 | 1 | 0 |  | 998 | 1630 | 159.3407 | 0.06105 | 0.06105 | 0 | 1.5934 | 0.0006105 | 0.0006105 | 0 | 1.5928 | 0.0006105 | 1.5477 | 264937.9999 | 3936.5142
39009.3975 | 2025 | 1 | 39009.3975 | 1 | 0 |  | 1152 | 1784 | 123.6264 | 0.06105 | 0.06105 | 0 | 1.2363 | 0.0006105 | 0.0006105 | 0 | 1.2357 | 0.0006105 | 30.8982 | 264938.0002 | 62414.4419
39009.3992 | 2176 | 1 | 39009.3993 | 1 | 0 |  | 1306 | 1938 | 132.8449 | 0.06105 | 0.06105 | 0 | 1.3284 | 0.0006105 | 0.0006105 | 0 | 1.3278 | 0.0006105 | 21.8106 | 264938.0002 | 47320.1392
39009.401 | 2606 | 1 | 39009.401 | 1 | 0 |  | 1460 | 2092 | 159.0965 | 0.06105 | 0.06105 | 0 | 1.591 | 0.0006105 | 0.0006105 | 0 | 1.5904 | 0.0006105 | 1.7036 | 264938.0002 | 4336.3633
39009.4028 | 1 | 0 | 39009.4028 | 2 | 0 |  | 1614 | 2246 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 264938 | 132419 | 264937.9994
39009.4046 | 16 | 0 | 39009.4046 | 2541 | 0 |  | 1768 | 2400 | 0.9768 | 0 | 155.1282 | 0 | 0.009768 | 0 | 1.5513 | 0 | 0.009768 | 1.5513 | 16464.875 | 4.3046 | 16464.8652
39009.4064 | 2336 | 0 | 39009.4064 | 2266 | 0 |  | 1922 | 2554 | 142.6129 | 0 | 138.3394 | 0 | 1.4261 | 0 | 1.3834 | 0 | 1.4261 | 1.3834 | 13.458 | 16.9629 | 12.0319
39009.4081 | 2578 | 0 | 39009.4082 | 2085 | 0 |  | 2076 | 2708 | 157.3871 | 0 | 127.2894 | 0 | 1.5739 | 0 | 1.2729 | 0 | 1.5739 | 1.2729 | 2.8076 | 27.1165 | 1.2337
39009.4099 | 2024 | 0 | 39009.41 | 2018 | 0 |  | 2230 | 2862 | 123.5653 | 0 | 123.199 | 0 | 1.2357 | 0 | 1.232 | 0 | 1.2357 | 1.232 | 30.9476 | 31.337 | 29.712
39009.4117 | 2174 | 0 | 39009.4117 | 2634 | 0 |  | 2384 | 3016 | 132.7228 | 0 | 160.8059 | 0 | 1.3272 | 0 | 1.6081 | 0 | 1.3272 | 1.6081 | 21.9126 | 0.62187 | 20.5854
39009.4135 | 2251 | 0 | 39009.4135 | 2072 | 0 |  | 2538 | 3170 | 137.4237 | 0 | 126.4957 | 0 | 1.3742 | 0 | 1.265 | 0 | 1.3742 | 1.265 | 17.7423 | 27.9141 | 16.3681
39009.4153 | 2155 | 0 | 39009.4153 | 2297 | 0 |  | 2692 | 3324 | 131.5629 | 0 | 140.232 | 0 | 1.3156 | 0 | 1.4023 | 0 | 1.3156 | 1.4023 | 22.9875 | 15.3844 | 21.6718
39009.4171 | 2578 | 0 | 39009.4171 | 2573 | 0 |  | 2846 | 3478 | 157.3871 | 0 | 157.0818 | 0 | 1.5739 | 0 | 1.5708 | 0 | 1.5739 | 1.5708 | 2.8076 | 3.0074 | 1.2337

## B3-E7
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 162.5385 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable E |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39009.3775 | 1 | 0 | 39009.3775 | 1 | 0 |  | -570 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3793 | 1 | 0 | 39009.3793 | 1 | 0 |  | -416 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3814 | 1 | 0 | 39009.3814 | 1 | 0 |  | -236.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3832 | 1 | 0 | 39009.3832 | 1 | 0 |  | -82.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.385 | 1 | 0 | 39009.385 | 1 | 0 |  | 71.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3867 | 1 | 0 | 39009.3867 | 1 | 0 |  | 225.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3885 | 1 | 0 | 39009.3885 | 1 | 0 |  | 379.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3903 | 1 | 0 | 39009.3903 | 1 | 0 |  | 533.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 266138 | 266138 | 266137.9994
39009.3921 | 1 | 0 | 39009.3921 | 2123 | 0 |  | 687.5 | 1319.5 | 0.06105 | 0 | 129.6093 | 0 | 0.0006105 | 0 | 1.2961 | 0 | 0.0006105 | 1.2961 | 266138 | 25.4065 | 266137.9994
39009.3939 | 1 | 0 | 39009.3939 | 2412 | 0 |  | 841.5 | 1473.5 | 0.06105 | 0 | 147.2527 | 0 | 0.0006105 | 0 | 1.4725 | 0 | 0.0006105 | 1.4725 | 266138 | 10.3806 | 266137.9994
39009.3956 | 2166 | 0 | 39009.3957 | 2084 | 0 |  | 995.5 | 1627.5 | 132.2344 | 0 | 127.2283 | 0 | 1.3223 | 0 | 1.2723 | 0 | 1.3223 | 1.2723 | 22.9169 | 27.7534 | 21.5946
39009.3974 | 2232 | 0 | 39009.3974 | 2259 | 0 |  | 1149.5 | 1781.5 | 136.2637 | 0 | 137.9121 | 0 | 1.3626 | 0 | 1.3791 | 0 | 1.3626 | 1.3791 | 19.2823 | 17.8566 | 17.9196
39009.3992 | 2082 | 0 | 39009.3992 | 2103 | 0 |  | 1303.5 | 1935.5 | 127.1062 | 0 | 128.3883 | 0 | 1.2711 | 0 | 1.2839 | 0 | 1.2711 | 1.2839 | 27.8761 | 26.5991 | 26.605
39009.401 | 2537 | 0 | 39009.401 | 2366 | 0 |  | 1457.5 | 2089.5 | 154.884 | 0 | 144.4444 | 0 | 1.5488 | 0 | 1.4444 | 0 | 1.5488 | 1.4444 | 4.9421 | 12.5266 | 3.3932
39009.4028 | 1 | 0 | 39009.4028 | 2544 | 0 |  | 1611.5 | 2243.5 | 0.06105 | 0 | 155.3114 | 0 | 0.0006105 | 0 | 1.5531 | 0 | 0.0006105 | 1.5531 | 266138 | 4.6533 | 266137.9994
39009.4046 | 1 | 0 | 39009.4046 | 1996 | 0 |  | 1765.5 | 2397.5 | 0.06105 | 0 | 121.8559 | 0 | 0.0006105 | 0 | 1.2186 | 0 | 0.0006105 | 1.2186 | 266138 | 33.3858 | 266137.9994
39009.4063 | 2019 | 0 | 39009.4064 | 2279 | 0 |  | 1919.5 | 2551.5 | 123.2601 | 0 | 139.1331 | 0 | 1.2326 | 0 | 1.3913 | 0 | 1.2326 | 1.3913 | 31.8663 | 16.8223 | 30.6337
39009.4081 | 2283 | 0 | 39009.4081 | 2241 | 0 |  | 2073.5 | 2705.5 | 139.3773 | 0 | 136.8132 | 0 | 1.3938 | 0 | 1.3681 | 0 | 1.3938 | 1.3681 | 16.6176 | 18.8032 | 15.2238
39009.4099 | 2514 | 0 | 39009.4099 | 2135 | 0 |  | 2227.5 | 2859.5 | 153.4799 | 0 | 130.3419 | 0 | 1.5348 | 0 | 1.3034 | 0 | 1.5348 | 1.3034 | 5.9021 | 24.7016 | 4.3673
39009.4117 | 2025 | 0 | 39009.4117 | 2272 | 0 |  | 2381 | 3013 | 123.6264 | 0 | 138.7057 | 0 | 1.2363 | 0 | 1.3871 | 0 | 1.2363 | 1.3871 | 31.4756 | 17.1822 | 30.2393
39009.4135 | 2277 | 0 | 39009.4135 | 2494 | 0 |  | 2535 | 3167 | 139.011 | 0 | 152.2589 | 0 | 1.3901 | 0 | 1.5226 | 0 | 1.3901 | 1.5226 | 16.9249 | 6.7514 | 15.5348
39009.4152 | 2589 | 0 | 39009.4153 | 2211 | 0 |  | 2689 | 3321 | 158.0586 | 0 | 134.9817 | 0 | 1.5806 | 0 | 1.3498 | 0 | 1.5806 | 1.3498 | 2.8343 | 20.4152 | 1.2537
39009.417 | 2627 | 0 | 39009.417 | 2646 | 0 |  | 2843 | 3475 | 160.3785 | 0 | 161.5385 | 0 | 1.6038 | 0 | 1.6154 | 0 | 1.6038 | 1.6154 | 1.3468 | 0.61905 | 0.257

## B3-C6
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 162.1111 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39009.3775 | 1 | 0 | 39009.3775 | 1 | 0 |  | -572.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3793 | 1 | 0 | 39009.3793 | 1 | 0 |  | -419 | 213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3814 | 1 | 0 | 39009.3814 | 1 | 0 |  | -239.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3831 | 1 | 0 | 39009.3831 | 1 | 0 |  | -85.5 | 546.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3849 | 1 | 0 | 39009.3849 | 1 | 0 |  | 68.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3867 | 1 | 0 | 39009.3867 | 1 | 0 |  | 222.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3885 | 1 | 0 | 39009.3885 | 1 | 0 |  | 376.5 | 1008.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3903 | 1 | 0 | 39009.3903 | 1 | 0 |  | 530.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.392 | 1 | 0 | 39009.3921 | 1 | 0 |  | 684.5 | 1316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3938 | 1 | 0 | 39009.3938 | 1 | 0 |  | 838.5 | 1470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.3956 | 2241 | 1 | 39009.3956 | 1 | 0 |  | 992.5 | 1624.5 | 136.8132 | 0.06105 | 0.06105 | 0 | 1.3681 | 0.0006105 | 0.0006105 | 0 | 1.3675 | 0.0006105 | 18.4991 | 265437.9997 | 41322.4324
39009.3974 | 2004 | 1 | 39009.3974 | 1 | 0 |  | 1146.5 | 1778.5 | 122.3443 | 0.06105 | 0.06105 | 0 | 1.2234 | 0.0006105 | 0.0006105 | 0 | 1.2228 | 0.0006105 | 32.5202 | 265438.0002 | 65013.5071
39009.3992 | 2162 | 1 | 39009.3992 | 1 | 0 |  | 1300.5 | 1932.5 | 131.9902 | 0.06105 | 0.06105 | 0 | 1.3199 | 0.0006105 | 0.0006105 | 0 | 1.3193 | 0.0006105 | 22.8311 | 265438.0002 | 49219.4573
39009.401 | 2564 | 1 | 39009.401 | 1 | 0 |  | 1454.5 | 2086.5 | 156.5324 | 0.06105 | 0.06105 | 0 | 1.5653 | 0.0006105 | 0.0006105 | 0 | 1.5647 | 0.0006105 | 3.5654 | 265437.9999 | 9034.5963
39009.4027 | 1 | 0 | 39009.4028 | 1 | 0 |  | 1608.5 | 2240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265438 | 265438 | 265437.9994
39009.4045 | 1063 | 1002 | 39009.4045 | 1116 | 1049 |  | 1762.5 | 2394.5 | 64.8962 | 61.1722 | 68.1319 | 64.0415 | 0.64896 | 0.61172 | 0.68132 | 0.64042 | 0.037241 | 0.040904 | 5230.7625 | 3279.0746 | 57.1765
39009.4063 | 2227 | 0 | 39009.4063 | 2552 | 0 |  | 1916.5 | 2548.5 | 135.9585 | 0 | 155.7998 | 0 | 1.3596 | 0 | 1.558 | 0 | 1.3596 | 1.558 | 19.2357 | 4.0509 | 17.8762
39009.4081 | 2166 | 0 | 39009.4081 | 2268 | 0 |  | 2070.5 | 2702.5 | 132.2344 | 0 | 138.4615 | 0 | 1.3223 | 0 | 1.3846 | 0 | 1.3223 | 1.3846 | 22.5937 | 17.0802 | 21.2714
39009.4099 | 2313 | 0 | 39009.4099 | 2024 | 0 |  | 2224.5 | 2856.5 | 141.2088 | 0 | 123.5653 | 0 | 1.4121 | 0 | 1.2357 | 0 | 1.4121 | 1.2357 | 14.8024 | 31.1947 | 13.3903
39009.4117 | 2018 | 0 | 39009.4117 | 2228 | 0 |  | 2378.5 | 3010.5 | 123.199 | 0 | 136.0195 | 0 | 1.232 | 0 | 1.3602 | 0 | 1.232 | 1.3602 | 31.5847 | 19.1822 | 30.3527
39009.4134 | 2306 | 0 | 39009.4134 | 2147 | 0 |  | 2532.5 | 3164.5 | 140.7814 | 0 | 131.0745 | 0 | 1.4078 | 0 | 1.3107 | 0 | 1.4078 | 1.3107 | 15.1509 | 23.6786 | 13.7431
39009.4152 | 2211 | 0 | 39009.4152 | 2286 | 0 |  | 2686.5 | 3318.5 | 134.9817 | 0 | 139.5604 | 0 | 1.3498 | 0 | 1.3956 | 0 | 1.3498 | 1.3956 | 20.0986 | 16.1584 | 18.7488
39009.417 | 2616 | 0 | 39009.417 | 2639 | 0 |  | 2840.5 | 3472.5 | 159.707 | 0 | 161.1111 | 0 | 1.5971 | 0 | 1.6111 | 0 | 1.5971 | 1.6111 | 1.5054 | 0.62069 | 0.091718

## B3-C5
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 158.6923 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-41 | N11 | N12 | Time-42 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39009.3775 | 1 | 0 | 39009.3775 | 1 | 0 |  | -575.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3792 | 1 | 0 | 39009.3793 | 1 | 0 |  | -421.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3813 | 1 | 0 | 39009.3813 | 1 | 0 |  | -242 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3831 | 1 | 0 | 39009.3831 | 1 | 0 |  | -88 | 544 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3849 | 1 | 0 | 39009.3849 | 1 | 0 |  | 66 | 698 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3867 | 1 | 0 | 39009.3867 | 1 | 0 |  | 220 | 852 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3884 | 1 | 0 | 39009.3885 | 1 | 0 |  | 374 | 1006 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3902 | 1 | 0 | 39009.3903 | 1 | 0 |  | 528 | 1160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.392 | 1 | 0 | 39009.392 | 1 | 0 |  | 682 | 1314 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3938 | 1 | 0 | 39009.3938 | 1 | 0 |  | 835.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259838 | 259838 | 259837.9994
39009.3956 | 2528 | 1 | 39009.3956 | 1 | 0 |  | 989.5 | 1621.5 | 154.3346 | 0.06105 | 0.06105 | 0 | 1.5433 | 0.0006105 | 0.0006105 | 0 | 1.5427 | 0.0006105 | 2.8247 | 259838 | 7035.2924
39009.3974 | 2499 | 1 | 39009.3974 | 1 | 0 |  | 1144 | 1776 | 152.5641 | 0.06105 | 0.06105 | 0 | 1.5256 | 0.0006105 | 0.0006105 | 0 | 1.525 | 0.0006105 | 4.0184 | 259838 | 9934.1768
39009.3991 | 2511 | 1 | 39009.3992 | 1 | 0 |  | 1297.5 | 1929.5 | 153.2967 | 0.06105 | 0.06105 | 0 | 1.533 | 0.0006105 | 0.0006105 | 0 | 1.5324 | 0.0006105 | 3.5211 | 259838.0002 | 8734.6384
39009.4009 | 2517 | 1 | 39009.4009 | 1 | 0 |  | 1451.5 | 2083.5 | 153.663 | 0.06105 | 0.06105 | 0 | 1.5366 | 0.0006105 | 0.0006105 | 0 | 1.536 | 0.0006105 | 3.2742 | 259838 | 8134.8693
39009.4027 | 92 | 83 | 39009.4027 | 100 | 92 |  | 1605.5 | 2237.5 | 5.6166 | 5.0672 | 6.105 | 5.6166 | 0.056166 | 0.050672 | 0.06105 | 0.056166 | 0.0054945 | 0.004884 | 28672.1897 | 32547.6907 | 2911.9929
39009.4045 | 1122 | 1057 | 39009.4045 | 1095 | 1108 |  | 1759.5 | 2391.5 | 68.4982 | 64.5299 | 66.8498 | 67.6435 | 0.68498 | 0.6453 | 0.6685 | 0.67643 | 0.039683 | 0.0079365 | 1250.9979 | 1990.7292 | 37.8688
39009.4063 | 2269 | 0 | 39009.4063 | 2157 | 0 |  | 1913.5 | 2545.5 | 138.5226 | 0 | 131.685 | 0 | 1.3852 | 0 | 1.3168 | 0 | 1.3852 | 1.3168 | 14.5606 | 20.509 | 13.1754
39009.4081 | 2455 | 0 | 39009.4081 | 2004 | 0 |  | 2067.5 | 2699.5 | 149.8779 | 0 | 122.3443 | 0 | 1.4988 | 0 | 1.2234 | 0 | 1.4988 | 1.2234 | 5.8811 | 29.7096 | 4.3823
39009.4098 | 2453 | 0 | 39009.4098 | 2265 | 0 |  | 2221.5 | 2853.5 | 149.7558 | 0 | 138.2784 | 0 | 1.4976 | 0 | 1.3828 | 0 | 1.4976 | 1.3828 | 5.9674 | 14.7629 | 4.4698
39009.4116 | 2379 | 0 | 39009.4116 | 2194 | 0 |  | 2375.5 | 3007.5 | 145.2381 | 0 | 133.9438 | 0 | 1.4524 | 0 | 1.3394 | 0 | 1.4524 | 1.3394 | 9.2636 | 18.4768 | 7.8112
39009.4134 | 2028 | 0 | 39009.4134 | 2107 | 0 |  | 2529.5 | 3161.5 | 123.8095 | 0 | 128.6325 | 0 | 1.2381 | 0 | 1.2863 | 0 | 1.2381 | 1.2863 | 28.1746 | 23.3688 | 26.9365
39009.4152 | 2460 | 0 | 39009.4152 | 2583 | 0 |  | 2683.5 | 3315.5 | 150.1832 | 0 | 157.6923 | 0 | 1.5018 | 0 | 1.5769 | 0 | 1.5018 | 1.5769 | 5.6659 | 0.63415 | 4.164
39009.417 | 2031 | 0 | 39009.417 | 2500 | 0 |  | 2837.5 | 3469.5 | 123.9927 | 0 | 152.6252 | 0 | 1.2399 | 0 | 1.5263 | 0 | 1.2399 | 1.5263 | 27.9852 | 3.9752 | 26.7453

## B3-B4
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.6227 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-39 | N11 | N12 | Time-40 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39009.3774 | 1 | 0 | 39009.3774 | 1 | 0 |  | -578.5 | 53.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3792 | 1 | 0 | 39009.3792 | 1 | 0 |  | -424.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3813 | 1 | 0 | 39009.3813 | 1 | 0 |  | -245 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3831 | 1 | 0 | 39009.3831 | 1 | 0 |  | -91 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3848 | 1 | 0 | 39009.3849 | 1 | 0 |  | 63 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3866 | 1 | 0 | 39009.3867 | 1 | 0 |  | 217 | 849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3884 | 1 | 0 | 39009.3884 | 1 | 0 |  | 371 | 1003 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3902 | 1 | 0 | 39009.3902 | 1 | 0 |  | 525 | 1157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.392 | 1 | 0 | 39009.392 | 1 | 0 |  | 679 | 1311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3938 | 1 | 0 | 39009.3938 | 1 | 0 |  | 833 | 1465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3955 | 1 | 0 | 39009.3956 | 1 | 0 |  | 987 | 1619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39009.3973 | 2362 | 1 | 39009.3973 | 1 | 0 |  | 1141 | 1773 | 144.2002 | 0.06105 | 0.06105 | 0 | 1.442 | 0.0006105 | 0.0006105 | 0 | 1.4414 | 0.0006105 | 12.0873 | 264638 | 28427.2581
39009.3991 | 2522 | 1 | 39009.3991 | 1 | 0 |  | 1295 | 1927 | 153.9683 | 0.06105 | 0.06105 | 0 | 1.5397 | 0.0006105 | 0.0006105 | 0 | 1.5391 | 0.0006105 | 4.9734 | 264638.0003 | 12433.3018
39009.4009 | 2092 | 1 | 39009.4009 | 1 | 0 |  | 1449 | 2081 | 127.7167 | 0.06105 | 0.06105 | 0 | 1.2772 | 0.0006105 | 0.0006105 | 0 | 1.2766 | 0.0006105 | 26.5605 | 264638.0003 | 55417.0593
39009.4027 | 69 | 62 | 39009.4027 | 88 | 76 |  | 1603 | 2235 | 4.2125 | 3.7851 | 5.3724 | 4.6398 | 0.042125 | 0.037851 | 0.053724 | 0.046398 | 0.0042735 | 0.007326 | 38402.4736 | 21685.8089 | 4040.0475
39009.4045 | 940 | 994 | 39009.4045 | 972 | 977 |  | 1757 | 2389 | 57.3871 | 60.6838 | 59.3407 | 59.6459 | 0.57387 | 0.60684 | 0.59341 | 0.59646 | 0.032967 | 0.0030525 | 2209.7787 | 4272.5584 | 70.1273
39009.4062 | 2061 | 0 | 39009.4063 | 2580 | 0 |  | 1911 | 2543 | 125.8242 | 0 | 157.5092 | 0 | 1.2582 | 0 | 1.5751 | 0 | 1.2582 | 1.5751 | 28.4512 | 2.6116 | 27.193
39009.408 | 2614 | 0 | 39009.408 | 2516 | 0 |  | 2065 | 2697 | 159.5849 | 0 | 153.602 | 0 | 1.5958 | 0 | 1.536 | 0 | 1.5958 | 1.536 | 1.277 | 5.2218 | 0.31888
39009.4098 | 2605 | 0 | 39009.4098 | 2140 | 0 |  | 2219 | 2851 | 159.0354 | 0 | 130.6471 | 0 | 1.5904 | 0 | 1.3065 | 0 | 1.5904 | 1.3065 | 1.6269 | 23.7093 | 0.036517
39009.4116 | 2450 | 0 | 39009.4116 | 2361 | 0 |  | 2373 | 3005 | 149.5726 | 0 | 144.1392 | 0 | 1.4957 | 0 | 1.4414 | 0 | 1.4957 | 1.4414 | 8.0563 | 12.1296 | 6.5606
39009.4134 | 2603 | 0 | 39009.4134 | 2104 | 0 |  | 2526.5 | 3158.5 | 158.9133 | 0 | 128.4493 | 0 | 1.5891 | 0 | 1.2845 | 0 | 1.5891 | 1.2845 | 1.705 | 25.826 | 0.11582
39009.4152 | 2434 | 0 | 39009.4152 | 2631 | 0 |  | 2680.5 | 3312.5 | 148.5958 | 0 | 160.6227 | 0 | 1.486 | 0 | 1.6062 | 0 | 1.486 | 1.6062 | 8.7666 | 0.62258 | 7.2807
39009.4169 | 2099 | 0 | 39009.4169 | 2130 | 0 |  | 2834.5 | 3466.5 | 128.1441 | 0 | 130.0366 | 0 | 1.2814 | 0 | 1.3004 | 0 | 1.2814 | 1.3004 | 26.1258 | 24.2901 | 24.8443

## A2-L11
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 159.1807 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 11 | Cable A | Even - | Cable L |  | Odd
Time-37 | N11 | N12 | Time-38 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R11-G | R2-11
39009.3774 | 1 | 0 | 39009.3774 | 1 | 0 |  | -581 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3792 | 1 | 0 | 39009.3792 | 1 | 0 |  | -427 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3813 | 1 | 0 | 39009.3813 | 1 | 0 |  | -247.5 | 384.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.383 | 1 | 0 | 39009.3831 | 1 | 0 |  | -93.5 | 538.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3848 | 1 | 0 | 39009.3848 | 1 | 0 |  | 60.5 | 692.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3866 | 1 | 0 | 39009.3866 | 1 | 0 |  | 214.5 | 846.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3884 | 1 | 0 | 39009.3884 | 1 | 0 |  | 368.5 | 1000.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3902 | 1 | 0 | 39009.3902 | 1 | 0 |  | 522.5 | 1154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3919 | 1 | 0 | 39009.392 | 1 | 0 |  | 676 | 1308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.3937 | 2161 | 1 | 39009.3938 | 2 | 0 |  | 830.5 | 1462.5 | 131.9292 | 0.06105 | 0.1221 | 0 | 1.3193 | 0.0006105 | 0.001221 | 0 | 1.3187 | 0.001221 | 20.6657 | 130268.9999 | 44503.837
39009.3955 | 2165 | 1 | 39009.3955 | 1 | 0 |  | 984.5 | 1616.5 | 132.1734 | 0.06105 | 0.06105 | 0 | 1.3217 | 0.0006105 | 0.0006105 | 0 | 1.3211 | 0.0006105 | 20.4427 | 260637.9999 | 44121.0719
39009.3973 | 2591 | 1 | 39009.3973 | 1 | 0 |  | 1138 | 1770 | 158.1807 | 0.06105 | 0.06105 | 0 | 1.5818 | 0.0006105 | 0.0006105 | 0 | 1.5812 | 0.0006105 | 0.63243 | 260638.0001 | 1537.4101
39009.3991 | 2305 | 1 | 39009.3991 | 1 | 0 |  | 1292 | 1924 | 140.7204 | 0.06105 | 0.06105 | 0 | 1.4072 | 0.0006105 | 0.0006105 | 0 | 1.4066 | 0.0006105 | 13.1241 | 260637.9999 | 30126.4413
39009.4009 | 2502 | 1 | 39009.4009 | 1 | 0 |  | 1446 | 2078 | 152.7473 | 0.06105 | 0.06105 | 0 | 1.5275 | 0.0006105 | 0.0006105 | 0 | 1.5269 | 0.0006105 | 4.2135 | 260638.0001 | 10433.9967
39009.4026 | 1 | 0 | 39009.4027 | 1 | 0 |  | 1600 | 2232 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.4044 | 1 | 0 | 39009.4044 | 1 | 0 |  | 1754 | 2386 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39009.4062 | 2001 | 0 | 39009.4062 | 2532 | 0 |  | 1908 | 2540 | 122.1612 | 0 | 154.5788 | 0 | 1.2216 | 0 | 1.5458 | 0 | 1.2216 | 1.5458 | 30.3038 | 2.9771 | 29.0822
39009.408 | 2036 | 0 | 39009.408 | 2518 | 0 |  | 2062 | 2694 | 124.2979 | 0 | 153.7241 | 0 | 1.243 | 0 | 1.5372 | 0 | 1.243 | 1.5372 | 28.0639 | 3.5496 | 26.8209
39009.4098 | 2429 | 0 | 39009.4098 | 2374 | 0 |  | 2216 | 2848 | 148.2906 | 0 | 144.9328 | 0 | 1.4829 | 0 | 1.4493 | 0 | 1.4829 | 1.4493 | 7.3438 | 9.8307 | 5.8609
39009.4116 | 2241 | 0 | 39009.4116 | 2189 | 0 |  | 2370 | 3002 | 136.8132 | 0 | 133.6386 | 0 | 1.3681 | 0 | 1.3364 | 0 | 1.3681 | 1.3364 | 16.349 | 19.1128 | 14.9808
39009.4133 | 2418 | 0 | 39009.4134 | 2053 | 0 |  | 2524 | 3156 | 147.619 | 0 | 125.3358 | 0 | 1.4762 | 0 | 1.2534 | 0 | 1.4762 | 1.2534 | 7.8321 | 27.0034 | 6.3559
39009.4151 | 2183 | 0 | 39009.4151 | 2180 | 0 |  | 2678 | 3310 | 133.2723 | 0 | 133.0891 | 0 | 1.3327 | 0 | 1.3309 | 0 | 1.3327 | 1.3309 | 19.4402 | 19.6046 | 18.1075
39009.4169 | 2102 | 0 | 39009.4169 | 2165 | 0 |  | 2832 | 3464 | 128.3272 | 0 | 132.1734 | 0 | 1.2833 | 0 | 1.3217 | 0 | 1.2833 | 1.3217 | 24.0428 | 20.4333 | 22.7595

## A2-H10
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 159.9133 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 10 | Cable A | Even - | Cable H |  | Even
Time-35 | N11 | N12 | Time-36 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R10-G | R2-10
39009.3774 | 1 | 0 | 39009.3774 | 1 | 0 |  | -584 | 48 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3791 | 1 | 0 | 39009.3792 | 1 | 0 |  | -430 | 202 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3812 | 1 | 0 | 39009.3812 | 1 | 0 |  | -250.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.383 | 1 | 0 | 39009.383 | 1 | 0 |  | -96.5 | 535.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3848 | 1 | 0 | 39009.3848 | 1 | 0 |  | 57.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3866 | 1 | 0 | 39009.3866 | 1 | 0 |  | 211.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3884 | 1 | 0 | 39009.3884 | 1 | 0 |  | 365.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3901 | 1 | 0 | 39009.3902 | 1 | 0 |  | 519.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3919 | 1 | 0 | 39009.3919 | 1 | 0 |  | 673.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.3937 | 2239 | 1 | 39009.3937 | 1 | 0 |  | 827.5 | 1459.5 | 136.6911 | 0.06105 | 0.06105 | 0 | 1.3669 | 0.0006105 | 0.0006105 | 0 | 1.3663 | 0.0006105 | 16.9964 | 261838.0001 | 37923.5164
39009.3955 | 2603 | 1 | 39009.3955 | 1 | 0 |  | 981.5 | 1613.5 | 158.9133 | 0.06105 | 0.06105 | 0 | 1.5891 | 0.0006105 | 0.0006105 | 0 | 1.5885 | 0.0006105 | 0.62952 | 261838.0001 | 1537.4128
39009.3973 | 2203 | 1 | 39009.3973 | 1 | 0 |  | 1135.5 | 1767.5 | 134.4933 | 0.06105 | 0.06105 | 0 | 1.3449 | 0.0006105 | 0.0006105 | 0 | 1.3443 | 0.0006105 | 18.9092 | 261838.0003 | 41522.142
39009.3991 | 2052 | 1 | 39009.3991 | 1 | 0 |  | 1289.5 | 1921.5 | 125.2747 | 0.06105 | 0.06105 | 0 | 1.2527 | 0.0006105 | 0.0006105 | 0 | 1.2521 | 0.0006105 | 27.6636 | 261838.0001 | 56616.3773
39009.4008 | 2074 | 1 | 39009.4008 | 1 | 0 |  | 1443.5 | 2075.5 | 126.6178 | 0.06105 | 0.06105 | 0 | 1.2662 | 0.0006105 | 0.0006105 | 0 | 1.2656 | 0.0006105 | 26.3087 | 261838.0001 | 54417.2172
39009.4026 | 1 | 0 | 39009.4026 | 1 | 0 |  | 1597.5 | 2229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39009.4044 | 1 | 0 | 39009.4044 | 2431 | 0 |  | 1751.5 | 2383.5 | 0.06105 | 0 | 148.4127 | 0 | 0.0006105 | 0 | 1.4841 | 0 | 0.0006105 | 1.4841 | 261838 | 7.7491 | 261837.9994
39009.4062 | 2167 | 0 | 39009.4062 | 2154 | 0 |  | 1905.5 | 2537.5 | 132.2955 | 0 | 131.5018 | 0 | 1.323 | 0 | 1.315 | 0 | 1.323 | 1.315 | 20.8759 | 21.6054 | 19.5529
39009.408 | 2180 | 0 | 39009.408 | 2578 | 0 |  | 2059.5 | 2691.5 | 133.0891 | 0 | 157.3871 | 0 | 1.3309 | 0 | 1.5739 | 0 | 1.3309 | 1.5739 | 20.155 | 1.6051 | 18.8242
39009.4097 | 2051 | 0 | 39009.4098 | 2185 | 0 |  | 2213 | 2845 | 125.2137 | 0 | 133.3944 | 0 | 1.2521 | 0 | 1.3339 | 0 | 1.2521 | 1.3339 | 27.7123 | 19.8801 | 26.4602
39009.4115 | 2548 | 0 | 39009.4115 | 2567 | 0 |  | 2367 | 2999 | 155.5556 | 0 | 156.7155 | 0 | 1.5556 | 0 | 1.5672 | 0 | 1.5556 | 1.5672 | 2.8014 | 2.0405 | 1.2459
39009.4133 | 2579 | 0 | 39009.4133 | 2051 | 0 |  | 2521 | 3153 | 157.4481 | 0 | 125.2137 | 0 | 1.5745 | 0 | 1.2521 | 0 | 1.5745 | 1.2521 | 1.5657 | 27.7123 | 0.0087579
39009.4151 | 2172 | 0 | 39009.4151 | 2316 | 0 |  | 2675 | 3307 | 132.6007 | 0 | 141.3919 | 0 | 1.326 | 0 | 1.4139 | 0 | 1.326 | 1.4139 | 20.5976 | 13.0993 | 19.2716
39009.4169 | 2094 | 0 | 39009.4169 | 2097 | 0 |  | 2829 | 3461 | 127.8388 | 0 | 128.022 | 0 | 1.2784 | 0 | 1.2802 | 0 | 1.2784 | 1.2802 | 25.0898 | 24.9108 | 23.8114

## A2-H9
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.9512 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 9 | Cable A | Even - | Cable H |  | Odd
Time-33 | N11 | N12 | Time-34 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R9-G | R2-9
39009.3773 | 1 | 0 | 39009.3773 | 1 | 0 |  | -586.5 | 45.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3791 | 1 | 0 | 39009.3791 | 1 | 0 |  | -433 | 199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3812 | 1 | 0 | 39009.3812 | 1 | 0 |  | -253.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.383 | 1 | 0 | 39009.383 | 1 | 0 |  | -99.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3848 | 1 | 0 | 39009.3848 | 1 | 0 |  | 54.5 | 686.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3865 | 1 | 0 | 39009.3866 | 1 | 0 |  | 208.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3883 | 1 | 0 | 39009.3883 | 1 | 0 |  | 362.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3901 | 1 | 0 | 39009.3901 | 1 | 0 |  | 516.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3919 | 1 | 0 | 39009.3919 | 1 | 0 |  | 670.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.3937 | 2154 | 1 | 39009.3937 | 1 | 0 |  | 824.5 | 1456.5 | 131.5018 | 0.06105 | 0.06105 | 0 | 1.315 | 0.0006105 | 0.0006105 | 0 | 1.3144 | 0.0006105 | 22.405 | 263538.0002 | 48119.7409
39009.3955 | 2003 | 1 | 39009.3955 | 1 | 0 |  | 978.5 | 1610.5 | 122.2833 | 0.06105 | 0.06105 | 0 | 1.2228 | 0.0006105 | 0.0006105 | 0 | 1.2222 | 0.0006105 | 31.6374 | 263537.9999 | 63214.0133
39009.3972 | 2235 | 1 | 39009.3972 | 1 | 0 |  | 1132.5 | 1764.5 | 136.4469 | 0.06105 | 0.06105 | 0 | 1.3645 | 0.0006105 | 0.0006105 | 0 | 1.3639 | 0.0006105 | 17.9669 | 263538.0002 | 40022.8133
39009.399 | 2547 | 1 | 39009.399 | 1 | 0 |  | 1286.5 | 1918.5 | 155.4945 | 0.06105 | 0.06105 | 0 | 1.5549 | 0.0006105 | 0.0006105 | 0 | 1.5543 | 0.0006105 | 3.5106 | 263537.9999 | 8834.6477
39009.4008 | 2505 | 1 | 39009.4008 | 1 | 0 |  | 1440.5 | 2072.5 | 152.9304 | 0.06105 | 0.06105 | 0 | 1.5293 | 0.0006105 | 0.0006105 | 0 | 1.5287 | 0.0006105 | 5.2468 | 263537.9999 | 13033.0546
39009.4026 | 1 | 0 | 39009.4026 | 1 | 0 |  | 1594.5 | 2226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39009.4044 | 1 | 0 | 39009.4044 | 2108 | 0 |  | 1748.5 | 2380.5 | 0.06105 | 0 | 128.6935 | 0 | 0.0006105 | 0 | 1.2869 | 0 | 0.0006105 | 1.2869 | 263538 | 25.0655 | 263537.9994
39009.4061 | 2120 | 0 | 39009.4062 | 2295 | 0 |  | 1902.5 | 2534.5 | 129.4261 | 0 | 140.1099 | 0 | 1.2943 | 0 | 1.4011 | 0 | 1.2943 | 1.4011 | 24.3575 | 14.8749 | 23.0633
39009.4079 | 2060 | 0 | 39009.4079 | 2314 | 0 |  | 2056.5 | 2688.5 | 125.7631 | 0 | 141.2698 | 0 | 1.2576 | 0 | 1.4127 | 0 | 1.2576 | 1.4127 | 27.9796 | 13.9317 | 26.722
39009.4097 | 2011 | 0 | 39009.4097 | 2569 | 0 |  | 2210.5 | 2842.5 | 122.7717 | 0 | 156.8376 | 0 | 1.2277 | 0 | 1.5684 | 0 | 1.2277 | 1.5684 | 31.098 | 2.6228 | 29.8702
39009.4115 | 2137 | 0 | 39009.4115 | 2461 | 0 |  | 2364.5 | 2996.5 | 130.464 | 0 | 150.2442 | 0 | 1.3046 | 0 | 1.5024 | 0 | 1.3046 | 1.5024 | 23.3683 | 7.1264 | 22.0636
39009.4133 | 2539 | 0 | 39009.4133 | 2060 | 0 |  | 2518.5 | 3150.5 | 155.0061 | 0 | 125.7631 | 0 | 1.5501 | 0 | 1.2576 | 0 | 1.5501 | 1.2576 | 3.8354 | 27.9796 | 2.2853
39009.4151 | 2429 | 0 | 39009.4151 | 2620 | 0 |  | 2672.5 | 3304.5 | 148.2906 | 0 | 159.9512 | 0 | 1.4829 | 0 | 1.5995 | 0 | 1.4829 | 1.5995 | 8.5377 | 0.62519 | 7.0548
39009.4168 | 2084 | 0 | 39009.4169 | 2237 | 0 |  | 2826.5 | 3458.5 | 127.2283 | 0 | 136.569 | 0 | 1.2723 | 0 | 1.3657 | 0 | 1.2723 | 1.3657 | 26.5058 | 17.8534 | 25.2335

## A2-C6
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.1575 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39009.3772 | 1 | 0 | 39009.3772 | 1 | 0 |  | -595.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.379 | 1 | 0 | 39009.379 | 1 | 0 |  | -441 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3811 | 1 | 0 | 39009.3811 | 1 | 0 |  | -261.5 | 370.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3829 | 1 | 0 | 39009.3829 | 1 | 0 |  | -107.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3847 | 1 | 0 | 39009.3847 | 1 | 0 |  | 46.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3864 | 1 | 0 | 39009.3865 | 1 | 0 |  | 200.5 | 832.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3882 | 1 | 0 | 39009.3882 | 1 | 0 |  | 354.5 | 986.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.39 | 1 | 0 | 39009.39 | 1 | 0 |  | 508 | 1140 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3918 | 1 | 0 | 39009.3918 | 1 | 0 |  | 662 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.3936 | 2070 | 1 | 39009.3936 | 1 | 0 |  | 816 | 1448 | 126.3736 | 0.06105 | 0.06105 | 0 | 1.2637 | 0.0006105 | 0.0006105 | 0 | 1.2631 | 0.0006105 | 26.7463 | 262238.0001 | 55216.944
39009.3953 | 2195 | 1 | 39009.3954 | 1 | 0 |  | 970 | 1602 | 134.0049 | 0.06105 | 0.06105 | 0 | 1.34 | 0.0006105 | 0.0006105 | 0 | 1.3394 | 0.0006105 | 19.5251 | 262238.0001 | 42721.7088
39009.3971 | 2405 | 1 | 39009.3972 | 1 | 0 |  | 1124 | 1756 | 146.8254 | 0.06105 | 0.06105 | 0 | 1.4683 | 0.0006105 | 0.0006105 | 0 | 1.4676 | 0.0006105 | 9.084 | 262238.0001 | 21729.7137
39009.3989 | 2008 | 1 | 39009.3989 | 1 | 0 |  | 1278 | 1910 | 122.5885 | 0.06105 | 0.06105 | 0 | 1.2259 | 0.0006105 | 0.0006105 | 0 | 1.2253 | 0.0006105 | 30.6617 | 262238.0001 | 61414.5806
39009.4007 | 2544 | 1 | 39009.4007 | 1 | 0 |  | 1432 | 2064 | 155.3114 | 0.06105 | 0.06105 | 0 | 1.5531 | 0.0006105 | 0.0006105 | 0 | 1.5525 | 0.0006105 | 3.1215 | 262238.0001 | 7835.0123
39009.4025 | 1 | 0 | 39009.4025 | 1 | 0 |  | 1586 | 2218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39009.4043 | 136 | 70 | 39009.4043 | 92 | 78 |  | 1740 | 2372 | 8.3028 | 4.2735 | 5.6166 | 4.7619 | 0.083028 | 0.042735 | 0.056166 | 0.047619 | 0.040293 | 0.008547 | 3787.7073 | 21199.5826 | 3437.1865
39009.406 | 2150 | 0 | 39009.4061 | 2607 | 0 |  | 1894 | 2526 | 131.2576 | 0 | 159.1575 | 0 | 1.3126 | 0 | 1.5916 | 0 | 1.3126 | 1.5916 | 22.0177 | 0.62831 | 20.7051
39009.4078 | 2206 | 0 | 39009.4078 | 2046 | 1 |  | 2048 | 2680 | 134.6764 | 0 | 124.9084 | 0.06105 | 1.3468 | 0 | 1.2491 | 0.0006105 | 1.3468 | 1.2485 | 18.9202 | 28.2826 | 17.5735
39009.4096 | 2000 | 0 | 39009.4096 | 2484 | 0 |  | 2202 | 2834 | 122.1001 | 0 | 151.6484 | 0 | 1.221 | 0 | 1.5165 | 0 | 1.221 | 1.5165 | 31.169 | 5.6111 | 29.948
39009.4114 | 2442 | 0 | 39009.4114 | 2288 | 0 |  | 2356 | 2988 | 149.0842 | 0 | 139.6825 | 0 | 1.4908 | 0 | 1.3968 | 0 | 1.4908 | 1.3968 | 7.4275 | 14.6582 | 5.9367
39009.4132 | 2014 | 0 | 39009.4132 | 2142 | 0 |  | 2510 | 3142 | 122.9548 | 0 | 130.7692 | 0 | 1.2295 | 0 | 1.3077 | 0 | 1.2295 | 1.3077 | 30.2572 | 22.4734 | 29.0277
39009.415 | 2065 | 0 | 39009.415 | 2506 | 0 |  | 2664 | 3296 | 126.0684 | 0 | 152.9915 | 0 | 1.2607 | 0 | 1.5299 | 0 | 1.2607 | 1.5299 | 27.0402 | 4.684 | 25.7795
39009.4167 | 2053 | 0 | 39009.4168 | 2309 | 0 |  | 2818 | 3450 | 125.3358 | 0 | 140.9646 | 0 | 1.2534 | 0 | 1.4096 | 0 | 1.2534 | 1.4096 | 27.7828 | 13.6154 | 26.5294

## A2-C5
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 157.2271 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39009.3772 | 1 | 0 | 39009.3772 | 1 | 0 |  | -598 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.379 | 1 | 0 | 39009.379 | 1 | 0 |  | -444 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3811 | 1 | 0 | 39009.3811 | 1 | 0 |  | -264.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3828 | 1 | 0 | 39009.3829 | 1 | 0 |  | -110.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3846 | 1 | 0 | 39009.3846 | 1 | 0 |  | 43.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3864 | 1 | 0 | 39009.3864 | 1 | 0 |  | 197.5 | 829.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3882 | 1 | 0 | 39009.3882 | 1 | 0 |  | 351.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.39 | 1 | 0 | 39009.39 | 1 | 0 |  | 505.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3918 | 1 | 0 | 39009.3918 | 1 | 0 |  | 659.5 | 1291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39009.3935 | 2498 | 1 | 39009.3936 | 1 | 0 |  | 813.5 | 1445.5 | 152.5031 | 0.06105 | 0.06105 | 0 | 1.525 | 0.0006105 | 0.0006105 | 0 | 1.5244 | 0.0006105 | 3.0989 | 257437.9999 | 7635.0342
39009.3953 | 2275 | 1 | 39009.3953 | 1 | 0 |  | 967.5 | 1599.5 | 138.8889 | 0.06105 | 0.06105 | 0 | 1.3889 | 0.0006105 | 0.0006105 | 0 | 1.3883 | 0.0006105 | 13.2093 | 257438.0001 | 29926.3753
39009.3971 | 2461 | 1 | 39009.3971 | 1 | 0 |  | 1121.5 | 1753.5 | 150.2442 | 0.06105 | 0.06105 | 0 | 1.5024 | 0.0006105 | 0.0006105 | 0 | 1.5018 | 0.0006105 | 4.6496 | 257438.0001 | 11333.5975
39009.3989 | 2287 | 1 | 39009.3989 | 1 | 0 |  | 1275.5 | 1907.5 | 139.6215 | 0.06105 | 0.06105 | 0 | 1.3962 | 0.0006105 | 0.0006105 | 0 | 1.3956 | 0.0006105 | 12.6151 | 257437.9999 | 28726.8413
39009.4007 | 2535 | 1 | 39009.4007 | 1 | 0 |  | 1429.5 | 2061.5 | 154.7619 | 0.06105 | 0.06105 | 0 | 1.5476 | 0.0006105 | 0.0006105 | 0 | 1.547 | 0.0006105 | 1.5935 | 257437.9999 | 3936.4709
39009.4025 | 46 | 42 | 39009.4025 | 44 | 35 |  | 1583.5 | 2215.5 | 2.8083 | 2.5641 | 2.6862 | 2.1368 | 0.028083 | 0.025641 | 0.026862 | 0.021368 | 0.002442 | 0.0054945 | 65671.5959 | 28293.9936 | 5901.4756
39009.4042 | 1136 | 1156 | 39009.4042 | 1096 | 1035 |  | 1737.5 | 2369.5 | 69.3529 | 70.5739 | 66.9109 | 63.1868 | 0.69353 | 0.70574 | 0.66911 | 0.63187 | 0.01221 | 0.037241 | 2279.4196 | 2679.2269 | 23.6318
39009.406 | 2373 | 0 | 39009.406 | 2236 | 0 |  | 1891 | 2523 | 144.8718 | 0 | 136.5079 | 0 | 1.4487 | 0 | 1.3651 | 0 | 1.4487 | 1.3651 | 8.5284 | 15.178 | 7.0797
39009.4078 | 2248 | 0 | 39009.4078 | 2462 | 0 |  | 2045 | 2677 | 137.2405 | 0 | 150.3053 | 0 | 1.3724 | 0 | 1.5031 | 0 | 1.3724 | 1.5031 | 14.5632 | 4.6052 | 13.1908
39009.4096 | 2007 | 0 | 39009.4096 | 2149 | 0 |  | 2199 | 2831 | 122.5275 | 0 | 131.1966 | 0 | 1.2253 | 0 | 1.312 | 0 | 1.2253 | 1.312 | 28.3199 | 19.8409 | 27.0946
39009.4114 | 2057 | 0 | 39009.4114 | 2345 | 0 |  | 2353 | 2985 | 125.58 | 0 | 143.1624 | 0 | 1.2558 | 0 | 1.4316 | 0 | 1.2558 | 1.4316 | 25.2008 | 9.8243 | 23.945
39009.4131 | 2040 | 0 | 39009.4132 | 2483 | 0 |  | 2507 | 3139 | 124.5421 | 0 | 151.5873 | 0 | 1.2454 | 0 | 1.5159 | 0 | 1.2454 | 1.5159 | 26.2441 | 3.7205 | 24.9987
39009.4149 | 2537 | 0 | 39009.4149 | 2139 | 0 |  | 2661 | 3293 | 154.884 | 0 | 130.5861 | 0 | 1.5488 | 0 | 1.3059 | 0 | 1.5488 | 1.3059 | 1.5128 | 20.4011 | 0.03603
39009.4167 | 2559 | 0 | 39009.4167 | 2558 | 0 |  | 2815 | 3447 | 156.2271 | 0 | 156.1661 | 0 | 1.5623 | 0 | 1.5617 | 0 | 1.5623 | 1.5617 | 0.64009 | 0.67944 | 0.92218

## A2-B4
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.0122 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39009.3772 | 1 | 0 | 39009.3772 | 1 | 0 |  | -601 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.379 | 1 | 0 | 39009.379 | 1 | 0 |  | -446.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.381 | 1 | 0 | 39009.381 | 1 | 0 |  | -267.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3828 | 1 | 0 | 39009.3828 | 1 | 0 |  | -113.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3846 | 1 | 0 | 39009.3846 | 1 | 0 |  | 40.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3864 | 1 | 0 | 39009.3864 | 1 | 0 |  | 194.5 | 826.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3882 | 1 | 0 | 39009.3882 | 1 | 0 |  | 348.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3899 | 1 | 0 | 39009.39 | 1 | 0 |  | 502.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3917 | 1 | 0 | 39009.3917 | 1 | 0 |  | 656.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39009.3935 | 1 | 0 | 39009.3935 | 2600 | 0 |  | 810.5 | 1442.5 | 0.06105 | 0 | 158.7302 | 0 | 0.0006105 | 0 | 1.5873 | 0 | 0.0006105 | 1.5873 | 263638 | 1.4377 | 263637.9994
39009.3953 | 1 | 0 | 39009.3953 | 2015 | 0 |  | 964.5 | 1596.5 | 0.06105 | 0 | 123.0159 | 0 | 0.0006105 | 0 | 1.2302 | 0 | 0.0006105 | 1.2302 | 263638 | 30.8873 | 263637.9994
39009.3971 | 2 | 0 | 39009.3971 | 2375 | 0 |  | 1118.5 | 1750.5 | 0.1221 | 0 | 144.9939 | 0 | 0.001221 | 0 | 1.4499 | 0 | 0.001221 | 1.4499 | 131769 | 11.0476 | 131768.9988
39009.3989 | 1 | 0 | 39009.3989 | 2529 | 0 |  | 1272.5 | 1904.5 | 0.06105 | 0 | 154.3956 | 0 | 0.0006105 | 0 | 1.544 | 0 | 0.0006105 | 1.544 | 263638 | 4.2855 | 263637.9994
39009.4006 | 1 | 0 | 39009.4006 | 2595 | 0 |  | 1426.5 | 2058.5 | 0.06105 | 0 | 158.4249 | 0 | 0.0006105 | 0 | 1.5842 | 0 | 0.0006105 | 1.5842 | 263638 | 1.6331 | 263637.9994
39009.4024 | 1167 | 1186 | 39009.4024 | 982 | 956 |  | 1580.5 | 2212.5 | 71.2454 | 72.4054 | 59.9512 | 58.3639 | 0.71245 | 0.72405 | 0.59951 | 0.58364 | 0.0116 | 0.015873 | 210999.5853 | 6479.7639 | 23.6137
39009.4042 | 1028 | 980 | 39009.4042 | 1166 | 1109 |  | 1734.5 | 2366.5 | 62.7595 | 59.8291 | 71.1844 | 67.7045 | 0.62759 | 0.59829 | 0.71184 | 0.67705 | 0.029304 | 0.034799 | 8676.4779 | 3327.5351 | 62.3487
39009.406 | 2225 | 0 | 39009.406 | 2152 | 0 |  | 1888.5 | 2520.5 | 135.8364 | 0 | 131.3797 | 0 | 1.3584 | 0 | 1.3138 | 0 | 1.3584 | 1.3138 | 18.5339 | 22.5548 | 17.1756
39009.4078 | 2613 | 0 | 39009.4078 | 2042 | 0 |  | 2042.5 | 2674.5 | 159.5238 | 0 | 124.6642 | 0 | 1.5952 | 0 | 1.2466 | 0 | 1.5952 | 1.2466 | 0.93303 | 29.1567 | 0.66221
39009.4095 | 2278 | 0 | 39009.4096 | 2492 | 0 |  | 2196.5 | 2828.5 | 139.072 | 0 | 152.1368 | 0 | 1.3907 | 0 | 1.5214 | 0 | 1.3907 | 1.5214 | 15.7761 | 5.8339 | 14.3854
39009.4113 | 2178 | 0 | 39009.4113 | 2162 | 0 |  | 2350.5 | 2982.5 | 132.967 | 0 | 131.9902 | 0 | 1.3297 | 0 | 1.3199 | 0 | 1.3297 | 1.3199 | 21.0918 | 21.988 | 19.7622
39009.4131 | 2621 | 0 | 39009.4131 | 2124 | 0 |  | 2504.5 | 3136.5 | 160.0122 | 0 | 129.6703 | 0 | 1.6001 | 0 | 1.2967 | 0 | 1.6001 | 1.2967 | 0.62495 | 24.1704 | 0.97517
39009.4149 | 2043 | 0 | 39009.4149 | 2152 | 0 |  | 2658.5 | 3290.5 | 124.7253 | 0 | 131.3797 | 0 | 1.2473 | 0 | 1.3138 | 0 | 1.2473 | 1.3138 | 29.0935 | 22.5548 | 27.8462
39009.4167 | 2618 | 0 | 39009.4167 | 2359 | 0 |  | 2812.5 | 3444.5 | 159.8291 | 0 | 144.0171 | 0 | 1.5983 | 0 | 1.4402 | 0 | 1.5983 | 1.4402 | 0.74026 | 11.8008 | 0.85803

## A2-B3
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 162.0501 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-21 | N11 | N12 | Time-22 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39009.3771 | 1 | 0 | 39009.3772 | 1 | 0 |  | -603.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3789 | 1 | 0 | 39009.3789 | 1 | 0 |  | -449.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.381 | 1 | 0 | 39009.381 | 1 | 0 |  | -270 | 362 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3828 | 1 | 0 | 39009.3828 | 1 | 0 |  | -116 | 516 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3846 | 1 | 0 | 39009.3846 | 1 | 0 |  | 38 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3863 | 1 | 0 | 39009.3864 | 1 | 0 |  | 192 | 824 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3881 | 1 | 0 | 39009.3881 | 1 | 0 |  | 346 | 978 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3899 | 1 | 0 | 39009.3899 | 1 | 0 |  | 499.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3917 | 1 | 0 | 39009.3917 | 1 | 0 |  | 653.5 | 1285.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265338 | 265338 | 265337.9994
39009.3935 | 2040 | 1 | 39009.3935 | 1 | 0 |  | 807.5 | 1439.5 | 124.5421 | 0.06105 | 0.06105 | 0 | 1.2454 | 0.0006105 | 0.0006105 | 0 | 1.2448 | 0.0006105 | 30.1314 | 265338 | 61314.8918
39009.3953 | 2251 | 1 | 39009.3953 | 1 | 0 |  | 962 | 1594 | 137.4237 | 0.06105 | 0.06105 | 0 | 1.3742 | 0.0006105 | 0.0006105 | 0 | 1.3736 | 0.0006105 | 17.928 | 265338 | 40222.8409
39009.397 | 2003 | 0 | 39009.397 | 2474 | 0 |  | 1115.5 | 1747.5 | 122.2833 | 0 | 151.0379 | 0 | 1.2228 | 0 | 1.5104 | 0 | 1.2228 | 1.5104 | 32.5202 | 7.291 | 31.2974
39009.3988 | 2071 | 0 | 39009.3988 | 2479 | 0 |  | 1269.5 | 1901.5 | 126.4347 | 0 | 151.3431 | 0 | 1.2643 | 0 | 1.5134 | 0 | 1.2643 | 1.5134 | 28.169 | 7.0746 | 26.9047
39009.4006 | 1991 | 0 | 39009.4006 | 2410 | 0 |  | 1423.5 | 2055.5 | 121.5507 | 0 | 147.1306 | 0 | 1.2155 | 0 | 1.4713 | 0 | 1.2155 | 1.4713 | 33.3189 | 10.1402 | 32.1034
39009.4024 | 1054 | 1027 | 39009.4024 | 1091 | 1142 |  | 1577.5 | 2209.5 | 64.3468 | 62.6984 | 66.6056 | 69.7192 | 0.64347 | 0.62698 | 0.66606 | 0.69719 | 0.016484 | 0.031136 | 13074.9762 | 6958.0051 | 55.0395
39009.4042 | 958 | 912 | 39009.4042 | 1090 | 1040 |  | 1731.5 | 2363.5 | 58.486 | 55.6777 | 66.5446 | 63.4921 | 0.58486 | 0.55678 | 0.66545 | 0.63492 | 0.028083 | 0.030525 | 6468.9196 | 4611.5442 | 84.1811
39009.4059 | 2280 | 0 | 39009.406 | 2184 | 0 |  | 1885.5 | 2517.5 | 139.1941 | 0 | 133.3333 | 0 | 1.3919 | 0 | 1.3333 | 0 | 1.3919 | 1.3333 | 16.4202 | 21.5375 | 15.0282
39009.4077 | 2303 | 0 | 39009.4077 | 2164 | 0 |  | 2039.5 | 2671.5 | 140.5983 | 0 | 132.1123 | 0 | 1.406 | 0 | 1.3211 | 0 | 1.406 | 1.3211 | 15.2575 | 22.6608 | 13.8515
39009.4095 | 2337 | 0 | 39009.4095 | 2547 | 0 |  | 2193.5 | 2825.5 | 142.674 | 0 | 155.4945 | 0 | 1.4267 | 0 | 1.5549 | 0 | 1.4267 | 1.5549 | 13.5807 | 4.2159 | 12.1539
39009.4113 | 2383 | 0 | 39009.4113 | 2596 | 0 |  | 2347.5 | 2979.5 | 145.4823 | 0 | 158.486 | 0 | 1.4548 | 0 | 1.5849 | 0 | 1.4548 | 1.5849 | 11.3882 | 2.2488 | 9.9333
39009.4131 | 2227 | 0 | 39009.4131 | 2473 | 0 |  | 2501.5 | 3133.5 | 135.9585 | 0 | 150.9768 | 0 | 1.3596 | 0 | 1.5098 | 0 | 1.3596 | 1.5098 | 19.1908 | 7.3344 | 17.8313
39009.4149 | 2421 | 0 | 39009.4149 | 2638 | 0 |  | 2655.5 | 3287.5 | 147.8022 | 0 | 161.0501 | 0 | 1.478 | 0 | 1.6105 | 0 | 1.478 | 1.6105 | 9.6398 | 0.62092 | 8.1618
39009.4166 | 2140 | 0 | 39009.4167 | 2474 | 0 |  | 2809.5 | 3441.5 | 130.6471 | 0 | 151.0379 | 0 | 1.3065 | 0 | 1.5104 | 0 | 1.3065 | 1.5104 | 24.0364 | 7.291 | 22.73

## A1-L11
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 155.823 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 11 | Cable A | Odd - | Cable L |  | Odd
Time-19 | N11 | N12 | Time-20 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R11-G | R1-11
39009.3771 | 1 | 0 | 39009.3771 | 1 | 0 |  | -606.5 | 25.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3789 | 1 | 0 | 39009.3789 | 1 | 0 |  | -452.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.381 | 1 | 0 | 39009.381 | 1 | 0 |  | -272.5 | 359.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3827 | 1 | 0 | 39009.3828 | 1 | 0 |  | -119 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3845 | 1 | 0 | 39009.3845 | 1 | 0 |  | 35 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3863 | 1 | 0 | 39009.3863 | 1 | 0 |  | 189 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3881 | 1 | 0 | 39009.3881 | 1 | 0 |  | 343 | 975 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3899 | 1 | 0 | 39009.3899 | 1 | 0 |  | 497 | 1129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3917 | 1 | 0 | 39009.3917 | 1 | 0 |  | 651 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3934 | 1 | 0 | 39009.3935 | 1 | 0 |  | 805 | 1437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3952 | 1 | 0 | 39009.3952 | 1 | 0 |  | 959 | 1591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.397 | 1 | 0 | 39009.397 | 1 | 0 |  | 1113 | 1745 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.3988 | 1 | 0 | 39009.3988 | 1 | 0 |  | 1267 | 1899 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.4006 | 1 | 0 | 39009.4006 | 1 | 0 |  | 1421 | 2053 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.4023 | 49 | 1 | 39009.4024 | 1 | 0 |  | 1575 | 2207 | 2.9915 | 0.06105 | 0.06105 | 0 | 0.029915 | 0.0006105 | 0.0006105 | 0 | 0.029304 | 0.0006105 | 5215.4176 | 255138 | 250139.959
39009.4041 | 1 | 0 | 39009.4042 | 1 | 0 |  | 1729 | 2361 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39009.4059 | 1996 | 0 | 39009.4059 | 2476 | 0 |  | 1883 | 2515 | 121.8559 | 0 | 151.16 | 0 | 1.2186 | 0 | 1.5116 | 0 | 1.2186 | 1.5116 | 27.8747 | 3.0848 | 26.6562
39009.4077 | 2364 | 0 | 39009.4077 | 2440 | 0 |  | 2036.5 | 2668.5 | 144.3223 | 0 | 148.9621 | 0 | 1.4432 | 0 | 1.4896 | 0 | 1.4432 | 1.4896 | 7.9687 | 4.6057 | 6.5255
39009.4095 | 2095 | 0 | 39009.4095 | 2222 | 0 |  | 2191 | 2823 | 127.8999 | 0 | 135.6532 | 0 | 1.279 | 0 | 1.3565 | 0 | 1.279 | 1.3565 | 21.832 | 14.8686 | 20.553
39009.4113 | 2140 | 0 | 39009.4113 | 2289 | 0 |  | 2344.5 | 2976.5 | 130.6471 | 0 | 139.7436 | 0 | 1.3065 | 0 | 1.3974 | 0 | 1.3065 | 1.3974 | 19.2701 | 11.5063 | 17.9636
39009.413 | 2536 | 0 | 39009.4131 | 2401 | 0 |  | 2498.5 | 3130.5 | 154.823 | 0 | 146.5812 | 0 | 1.5482 | 0 | 1.4658 | 0 | 1.5482 | 1.4658 | 0.6459 | 6.3049 | 0.90233
39009.4148 | 2476 | 0 | 39009.4148 | 2211 | 0 |  | 2652.5 | 3284.5 | 151.16 | 0 | 134.9817 | 0 | 1.5116 | 0 | 1.3498 | 0 | 1.5116 | 1.3498 | 3.0848 | 15.4401 | 1.5732
39009.4166 | 2176 | 0 | 39009.4166 | 2108 | 0 |  | 2806.5 | 3438.5 | 132.8449 | 0 | 128.6935 | 0 | 1.3284 | 0 | 1.2869 | 0 | 1.3284 | 1.2869 | 17.2969 | 21.0806 | 15.9684

## A1-H10
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 156.9219 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 10 | Cable A | Odd - | Cable H |  | Even
Time-17 | N11 | N12 | Time-18 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R10-G | R1-10
39009.3771 | 1 | 0 | 39009.3771 | 1 | 0 |  | -609 | 23 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3789 | 1 | 0 | 39009.3789 | 1 | 0 |  | -455.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3809 | 1 | 0 | 39009.3809 | 1 | 0 |  | -275.5 | 356.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3827 | 1 | 0 | 39009.3827 | 1 | 0 |  | -121.5 | 510.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3845 | 1 | 0 | 39009.3845 | 1 | 0 |  | 32.5 | 664.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3863 | 1 | 0 | 39009.3863 | 1 | 0 |  | 186.5 | 818.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3881 | 1 | 0 | 39009.3881 | 1 | 0 |  | 340.5 | 972.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3898 | 1 | 0 | 39009.3899 | 1 | 0 |  | 494.5 | 1126.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3916 | 1 | 0 | 39009.3916 | 1 | 0 |  | 648.5 | 1280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3934 | 1 | 0 | 39009.3934 | 1 | 0 |  | 802 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3952 | 1 | 0 | 39009.3952 | 1 | 0 |  | 956 | 1588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.397 | 1 | 0 | 39009.397 | 1 | 0 |  | 1110 | 1742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.3988 | 1 | 0 | 39009.3988 | 1 | 0 |  | 1264 | 1896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256938 | 256938 | 256937.9994
39009.4005 | 1 | 1 | 39009.4006 | 1 | 0 |  | 1418 | 2050 | 0.06105 | 0.06105 | 0.06105 | 0 | 0.0006105 | 0.0006105 | 0.0006105 | 0 | 0 | 0.0006105 | 660171358.44 | 256938 | 256738.0778
39009.4023 | 45 | 1 | 39009.4023 | 1 | 0 |  | 1572 | 2204 | 2.7473 | 0.06105 | 0.06105 | 0 | 0.027473 | 0.0006105 | 0.0006105 | 0 | 0.026862 | 0.0006105 | 5739.5508 | 256938 | 252339.7896
39009.4041 | 1 | 0 | 39009.4041 | 2091 | 0 |  | 1726 | 2358 | 0.06105 | 0 | 127.6557 | 0 | 0.0006105 | 0 | 1.2766 | 0 | 0.0006105 | 1.2766 | 256938 | 22.9259 | 256937.9994
39009.4059 | 2330 | 0 | 39009.4059 | 2022 | 0 |  | 1880 | 2512 | 142.2466 | 0 | 123.4432 | 0 | 1.4225 | 0 | 1.2344 | 0 | 1.4225 | 1.2344 | 10.3167 | 27.1207 | 8.8943
39009.4077 | 2346 | 0 | 39009.4077 | 2479 | 0 |  | 2034 | 2666 | 143.2234 | 0 | 151.3431 | 0 | 1.4322 | 0 | 1.5134 | 0 | 1.4322 | 1.5134 | 9.5644 | 3.6862 | 8.1321
39009.4094 | 2167 | 0 | 39009.4095 | 2155 | 0 |  | 2188 | 2820 | 132.2955 | 0 | 131.5629 | 0 | 1.323 | 0 | 1.3156 | 0 | 1.323 | 1.3156 | 18.6147 | 19.2752 | 17.2917
39009.4112 | 2220 | 0 | 39009.4112 | 2184 | 0 |  | 2342 | 2974 | 135.5311 | 0 | 133.3333 | 0 | 1.3553 | 0 | 1.3333 | 0 | 1.3553 | 1.3333 | 15.7829 | 17.6914 | 14.4276
39009.413 | 2161 | 0 | 39009.413 | 2509 | 0 |  | 2496 | 3128 | 131.9292 | 0 | 153.1746 | 0 | 1.3193 | 0 | 1.5317 | 0 | 1.3193 | 1.5317 | 18.944 | 2.4464 | 17.6247
39009.4148 | 2554 | 0 | 39009.4148 | 2210 | 0 |  | 2650 | 3282 | 155.9219 | 0 | 134.9206 | 0 | 1.5592 | 0 | 1.3492 | 0 | 1.5592 | 1.3492 | 0.64135 | 16.3068 | 0.91787
39009.4166 | 2134 | 0 | 39009.4166 | 2007 | 0 |  | 2804 | 3436 | 130.2808 | 0 | 122.5275 | 0 | 1.3028 | 0 | 1.2253 | 0 | 1.3028 | 1.2253 | 20.4489 | 28.0708 | 19.1461

## A1-H9
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.0733 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 9 | Cable A | Odd - | Cable H |  | Odd
Time-15 | N11 | N12 | Time-16 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R9-G | R1-9
39009.377 | 1 | 0 | 39009.3771 | 1 | 0 |  | -612 | 20 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3788 | 1 | 0 | 39009.3788 | 1 | 0 |  | -458 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3809 | 1 | 0 | 39009.3809 | 1 | 0 |  | -278.5 | 353.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3827 | 1 | 0 | 39009.3827 | 1 | 0 |  | -124.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3845 | 1 | 0 | 39009.3845 | 1 | 0 |  | 29.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3863 | 1 | 0 | 39009.3863 | 1 | 0 |  | 183.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.388 | 1 | 0 | 39009.388 | 1 | 0 |  | 337.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3898 | 1 | 0 | 39009.3898 | 1 | 0 |  | 491.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3916 | 1 | 0 | 39009.3916 | 1 | 0 |  | 645.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3934 | 1 | 0 | 39009.3934 | 1 | 0 |  | 799.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3952 | 1 | 0 | 39009.3952 | 1 | 0 |  | 953.5 | 1585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3969 | 1 | 0 | 39009.397 | 1 | 0 |  | 1107.5 | 1739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.3987 | 1 | 0 | 39009.3987 | 1 | 0 |  | 1261.5 | 1893.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.4005 | 1 | 0 | 39009.4005 | 1 | 0 |  | 1415.5 | 2047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263738 | 263738 | 263737.9994
39009.4023 | 43 | 1 | 39009.4023 | 1 | 0 |  | 1569.5 | 2201.5 | 2.6252 | 0.06105 | 0.06105 | 0 | 0.026252 | 0.0006105 | 0.0006105 | 0 | 0.025641 | 0.0006105 | 6179.532 | 263738 | 259339.6677
39009.4041 | 49 | 0 | 39009.4041 | 2552 | 0 |  | 1723.5 | 2355.5 | 2.9915 | 0 | 155.7998 | 0 | 0.029915 | 0 | 1.558 | 0 | 0.029915 | 1.558 | 5284.449 | 3.3848 | 5284.4191
39009.4058 | 2246 | 0 | 39009.4059 | 2482 | 0 |  | 1877 | 2509 | 137.1184 | 0 | 151.5263 | 0 | 1.3712 | 0 | 1.5153 | 0 | 1.3712 | 1.5153 | 17.4702 | 6.3006 | 16.099
39009.4076 | 2071 | 0 | 39009.4077 | 2274 | 0 |  | 2031.5 | 2663.5 | 126.4347 | 0 | 138.8278 | 0 | 1.2643 | 0 | 1.3883 | 0 | 1.2643 | 1.3883 | 27.3964 | 16.0237 | 26.1321
39009.4094 | 2041 | 0 | 39009.4094 | 2106 | 0 |  | 2185.5 | 2817.5 | 124.6032 | 0 | 128.5714 | 0 | 1.246 | 0 | 1.2857 | 0 | 1.246 | 1.2857 | 29.269 | 25.2792 | 28.023
39009.4112 | 2110 | 0 | 39009.4112 | 2622 | 0 |  | 2339.5 | 2971.5 | 128.8156 | 0 | 160.0733 | 0 | 1.2882 | 0 | 1.6007 | 0 | 1.2882 | 1.6007 | 25.0417 | 0.62471 | 23.7535
39009.413 | 2577 | 0 | 39009.413 | 2260 | 0 |  | 2493 | 3125 | 157.326 | 0 | 137.9731 | 0 | 1.5733 | 0 | 1.3797 | 0 | 1.5733 | 1.3797 | 2.3818 | 16.7425 | 0.80858
39009.4148 | 2490 | 0 | 39009.4148 | 2483 | 0 |  | 2647 | 3279 | 152.0147 | 0 | 151.5873 | 0 | 1.5201 | 0 | 1.5159 | 0 | 1.5201 | 1.5159 | 5.959 | 6.2578 | 4.4389
39009.4165 | 2615 | 0 | 39009.4166 | 2447 | 0 |  | 2801 | 3433 | 159.6459 | 0 | 149.3895 | 0 | 1.5965 | 0 | 1.4939 | 0 | 1.5965 | 1.4939 | 0.89407 | 7.821 | 0.70239

## A1-C6
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.7448 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39009.3769 | 1 | 0 | 39009.377 | 1 | 0 |  | -620.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3787 | 1 | 0 | 39009.3787 | 1 | 0 |  | -466.5 | 165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3808 | 1 | 0 | 39009.3808 | 1 | 0 |  | -287 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3826 | 1 | 0 | 39009.3826 | 1 | 0 |  | -133 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3844 | 1 | 0 | 39009.3844 | 1 | 0 |  | 21 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3861 | 1 | 0 | 39009.3862 | 1 | 0 |  | 175 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3879 | 1 | 0 | 39009.388 | 1 | 0 |  | 329 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3897 | 1 | 0 | 39009.3897 | 1 | 0 |  | 483 | 1115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3915 | 1 | 0 | 39009.3915 | 1 | 0 |  | 637 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3933 | 1 | 0 | 39009.3933 | 1 | 0 |  | 791 | 1423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3951 | 1 | 0 | 39009.3951 | 1 | 0 |  | 945 | 1577 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3968 | 1 | 0 | 39009.3969 | 1 | 0 |  | 1099 | 1731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.3986 | 1 | 0 | 39009.3986 | 1 | 0 |  | 1253 | 1885 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.4004 | 1 | 0 | 39009.4004 | 1 | 0 |  | 1407 | 2039 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264838 | 264838 | 264837.9994
39009.4022 | 93 | 1 | 39009.4022 | 1 | 0 |  | 1561 | 2193 | 5.6777 | 0.06105 | 0.06105 | 0 | 0.056777 | 0.0006105 | 0.0006105 | 0 | 0.056166 | 0.0006105 | 2778.6853 | 264838 | 255441.548
39009.404 | 50 | 17 | 39009.404 | 37 | 14 |  | 1715 | 2347 | 3.0525 | 1.0379 | 2.2589 | 0.8547 | 0.030525 | 0.010379 | 0.022589 | 0.008547 | 0.020147 | 0.014042 | 7912.5204 | 11446.2276 | 15058.9084
39009.4058 | 2176 | 0 | 39009.4058 | 2264 | 0 |  | 1868.5 | 2500.5 | 132.8449 | 0 | 138.2173 | 0 | 1.3284 | 0 | 1.3822 | 0 | 1.3284 | 1.3822 | 21.7546 | 17.0221 | 20.4261
39009.4075 | 2295 | 0 | 39009.4076 | 2140 | 0 |  | 2023 | 2655 | 140.1099 | 0 | 130.6471 | 0 | 1.4011 | 0 | 1.3065 | 0 | 1.4011 | 1.3065 | 15.4414 | 23.8028 | 14.0403
39009.4093 | 2443 | 0 | 39009.4093 | 2518 | 0 |  | 2177 | 2809 | 149.1453 | 0 | 153.7241 | 0 | 1.4915 | 0 | 1.5372 | 0 | 1.4915 | 1.5372 | 8.4478 | 5.2176 | 6.9564
39009.4111 | 2054 | 0 | 39009.4111 | 2376 | 0 |  | 2330.5 | 2962.5 | 125.3968 | 0 | 145.0549 | 0 | 1.254 | 0 | 1.4505 | 0 | 1.254 | 1.4505 | 28.9864 | 11.5059 | 27.7324
39009.4129 | 2336 | 0 | 39009.4129 | 2163 | 0 |  | 2484.5 | 3116.5 | 142.6129 | 0 | 132.0513 | 0 | 1.4261 | 0 | 1.3205 | 0 | 1.4261 | 1.3205 | 13.4152 | 22.4864 | 11.9891
39009.4147 | 2599 | 0 | 39009.4147 | 2058 | 0 |  | 2638.5 | 3270.5 | 158.6691 | 0 | 125.641 | 0 | 1.5867 | 0 | 1.2564 | 0 | 1.5867 | 1.2564 | 1.9384 | 28.7357 | 0.35175
39009.4164 | 2633 | 0 | 39009.4165 | 2517 | 0 |  | 2792.5 | 3424.5 | 160.7448 | 0 | 153.663 | 0 | 1.6074 | 0 | 1.5366 | 0 | 1.6074 | 1.5366 | 0.6221 | 5.2594 | 0.98534

## A1-C5
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.5238 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39009.3769 | 1 | 0 | 39009.3769 | 1 | 0 |  | -623 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3787 | 1 | 0 |  | 1 | 0 |  | -470 | 162 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3808 | 1 | 0 | 39009.3808 | 1 | 0 |  | -289.5 | 342.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3826 | 1 | 0 | 39009.3826 | 1 | 0 |  | -135.5 | 496.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3843 | 1 | 0 | 39009.3844 | 1 | 0 |  | 18.5 | 650.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3861 | 1 | 0 | 39009.3861 | 1 | 0 |  | 172.5 | 804.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3879 | 1 | 0 | 39009.3879 | 1 | 0 |  | 326.5 | 958.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3897 | 1 | 0 | 39009.3897 | 1 | 0 |  | 480.5 | 1112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3915 | 1 | 0 | 39009.3915 | 1 | 0 |  | 634 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3933 | 1 | 0 | 39009.3933 | 1 | 0 |  | 788.5 | 1420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.395 | 1 | 0 | 39009.395 | 1 | 0 |  | 942.5 | 1574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3968 | 1 | 0 | 39009.3968 | 1 | 0 |  | 1096 | 1728 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.3986 | 1 | 0 | 39009.3986 | 1 | 0 |  | 1250 | 1882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.4004 | 1 | 0 | 39009.4004 | 1 | 0 |  | 1404 | 2036 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39009.4022 | 982 | 874 | 39009.4022 | 1084 | 964 |  | 1558 | 2190 | 59.9512 | 53.3578 | 66.1783 | 58.8523 | 0.59951 | 0.53358 | 0.66178 | 0.58852 | 0.065934 | 0.07326 | 2746.3134 | 1820.2699 | 83.8793
39009.4039 | 1036 | 987 | 39009.404 | 973 | 927 |  | 1712 | 2344 | 63.2479 | 60.2564 | 59.4017 | 56.5934 | 0.63248 | 0.60256 | 0.59402 | 0.56593 | 0.029915 | 0.028083 | 4821.767 | 6186.3665 | 60.4594
39009.4057 | 2263 | 0 | 39009.4057 | 2049 | 0 |  | 1866 | 2498 | 138.1563 | 0 | 125.0916 | 0 | 1.3816 | 0 | 1.2509 | 0 | 1.3816 | 1.2509 | 16.19 | 28.325 | 14.8085
39009.4075 | 2161 | 0 | 39009.4075 | 2531 | 0 |  | 2020 | 2652 | 131.9292 | 0 | 154.5177 | 0 | 1.3193 | 0 | 1.5452 | 0 | 1.3193 | 1.5452 | 21.6742 | 3.887 | 20.3549
39009.4093 | 2018 | 0 | 39009.4093 | 2205 | 0 |  | 2174 | 2806 | 123.199 | 0 | 134.6154 | 0 | 1.232 | 0 | 1.3462 | 0 | 1.232 | 1.3462 | 30.2963 | 19.2463 | 29.0643
39009.4111 | 2451 | 0 | 39009.4111 | 2233 | 0 |  | 2328 | 2960 | 149.6337 | 0 | 136.3248 | 0 | 1.4963 | 0 | 1.3632 | 0 | 1.4963 | 1.3632 | 7.2778 | 17.751 | 5.7815
39009.4128 | 2613 | 0 | 39009.4129 | 2379 | 0 |  | 2482 | 3114 | 159.5238 | 0 | 145.2381 | 0 | 1.5952 | 0 | 1.4524 | 0 | 1.5952 | 1.4524 | 0.62687 | 10.5246 | 0.96837
39009.4146 | 2214 | 0 | 39009.4147 | 2047 | 0 |  | 2636 | 3268 | 135.1648 | 0 | 124.9695 | 0 | 1.3516 | 0 | 1.2497 | 0 | 1.3516 | 1.2497 | 18.7615 | 28.4504 | 17.4099
39009.4164 | 2161 | 0 | 39009.4164 | 2261 | 0 |  | 2790 | 3422 | 131.9292 | 0 | 138.0342 | 0 | 1.3193 | 0 | 1.3803 | 0 | 1.3193 | 1.3803 | 21.6742 | 16.2928 | 20.3549

## A1-B4
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 160.5849 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39009.3769 | 1 | 0 | 39009.3769 | 1 | 0 |  | -626 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3787 | 1 | 0 | 39009.3787 | 1 | 0 |  | -472 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3807 | 1 | 0 | 39009.3808 | 1 | 0 |  | -292.5 | 339.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3825 | 1 | 0 | 39009.3825 | 1 | 0 |  | -138.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3843 | 1 | 0 | 39009.3843 | 1 | 0 |  | 15.5 | 647.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3861 | 1 | 0 | 39009.3861 | 1 | 0 |  | 169.5 | 801.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3879 | 1 | 0 | 39009.3879 | 1 | 0 |  | 323.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3897 | 1 | 0 | 39009.3897 | 1 | 0 |  | 477.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3914 | 1 | 0 | 39009.3914 | 1 | 0 |  | 631.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3932 | 1 | 0 | 39009.3932 | 1 | 0 |  | 785.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.395 | 1 | 0 | 39009.395 | 1 | 0 |  | 939.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3968 | 1 | 0 | 39009.3968 | 1 | 0 |  | 1093.5 | 1725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.3986 | 1 | 0 | 39009.3986 | 1 | 0 |  | 1247.5 | 1879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.4003 | 1 | 0 | 39009.4004 | 1 | 0 |  | 1401.5 | 2033.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262938 | 262938 | 262937.9994
39009.4021 | 1017 | 908 | 39009.4021 | 1111 | 1062 |  | 1555.5 | 2187.5 | 62.0879 | 55.4335 | 67.8266 | 64.8352 | 0.62088 | 0.55433 | 0.67827 | 0.64835 | 0.066545 | 0.029915 | 1227.7379 | 4051.6209 | 75.8138
39009.4039 | 1066 | 1123 | 39009.4039 | 938 | 915 |  | 1709.5 | 2341.5 | 65.0794 | 68.5592 | 57.265 | 55.8608 | 0.65079 | 0.68559 | 0.57265 | 0.55861 | 0.034799 | 0.014042 | 2293.399 | 10015.7931 | 38.9151
39009.4057 | 2147 | 0 | 39009.4057 | 2001 | 0 |  | 1863.5 | 2495.5 | 131.0745 | 0 | 122.1612 | 0 | 1.3107 | 0 | 1.2216 | 0 | 1.3107 | 1.2216 | 22.5142 | 31.4533 | 21.2035
39009.4075 | 2203 | 0 | 39009.4075 | 2582 | 0 |  | 2017 | 2649 | 134.4933 | 0 | 157.6313 | 0 | 1.3449 | 0 | 1.5763 | 0 | 1.3449 | 1.5763 | 19.3999 | 1.8737 | 18.055
39009.4092 | 2337 | 0 | 39009.4093 | 2249 | 0 |  | 2171 | 2803 | 142.674 | 0 | 137.3016 | 0 | 1.4267 | 0 | 1.373 | 0 | 1.4267 | 1.373 | 12.5537 | 16.9578 | 11.127
39009.411 | 2450 | 0 | 39009.4111 | 2327 | 0 |  | 2325 | 2957 | 149.5726 | 0 | 142.0635 | 0 | 1.4957 | 0 | 1.4206 | 0 | 1.4957 | 1.4206 | 7.3624 | 13.0374 | 5.8667
39009.4128 | 2206 | 0 | 39009.4128 | 2475 | 0 |  | 2479 | 3111 | 134.6764 | 0 | 151.0989 | 0 | 1.3468 | 0 | 1.511 | 0 | 1.3468 | 1.511 | 19.2375 | 6.278 | 17.8908
39009.4146 | 2614 | 0 | 39009.4146 | 2224 | 0 |  | 2633 | 3265 | 159.5849 | 0 | 135.7753 | 0 | 1.5958 | 0 | 1.3578 | 0 | 1.5958 | 1.3578 | 0.62663 | 18.2725 | 0.96922
39009.4164 | 2525 | 0 | 39009.4164 | 2253 | 0 |  | 2787 | 3419 | 154.1514 | 0 | 137.5458 | 0 | 1.5415 | 0 | 1.3755 | 0 | 1.5415 | 1.3755 | 4.1735 | 16.7501 | 2.632

## A1-B3
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.928 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39009.3768 | 1 | 0 | 39009.3769 | 1 | 0 |  | -629 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3786 | 1 | 0 | 39009.3786 | 1 | 0 |  | -474.5 | 157.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3807 | 1 | 0 | 39009.3807 | 1 | 0 |  | -295.5 | 336.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3825 | 1 | 0 | 39009.3825 | 1 | 0 |  | -141.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3843 | 1 | 0 | 39009.3843 | 1 | 0 |  | 12.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3861 | 1 | 0 | 39009.3861 | 1 | 0 |  | 166.5 | 798.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3878 | 1 | 0 | 39009.3878 | 1 | 0 |  | 320.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3896 | 1 | 0 | 39009.3896 | 1 | 0 |  | 474.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3914 | 1 | 0 | 39009.3914 | 1 | 0 |  | 628.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3932 | 1 | 0 | 39009.3932 | 1 | 0 |  | 782.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.395 | 1 | 0 | 39009.395 | 1 | 0 |  | 936.5 | 1568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39009.3967 | 1 | 0 | 39009.3968 | 2073 | 0 |  | 1090.5 | 1722.5 | 0.06105 | 0 | 126.5568 | 0 | 0.0006105 | 0 | 1.2656 | 0 | 0.0006105 | 1.2656 | 265138 | 27.9489 | 265137.9994
39009.3985 | 1 | 0 | 39009.3985 | 2346 | 0 |  | 1244.5 | 1876.5 | 0.06105 | 0 | 143.2234 | 0 | 0.0006105 | 0 | 1.4322 | 0 | 0.0006105 | 1.4322 | 265138 | 13.0597 | 265137.9994
39009.4003 | 1 | 0 | 39009.4003 | 2 | 0 |  | 1398.5 | 2030.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 265138 | 132519 | 265137.9994
39009.4021 | 26 | 0 | 39009.4021 | 2602 | 0 |  | 1552.5 | 2184.5 | 1.5873 | 0 | 158.8523 | 0 | 0.015873 | 0 | 1.5885 | 0 | 0.015873 | 1.5885 | 10101.4615 | 1.9362 | 10101.4457
39009.4039 | 55 | 15 | 39009.4039 | 38 | 36 |  | 1706.5 | 2338.5 | 3.3578 | 0.91575 | 2.3199 | 2.1978 | 0.033578 | 0.0091575 | 0.023199 | 0.021978 | 0.02442 | 0.001221 | 6494.7968 | 180837.0795 | 17206.3518
39009.4057 | 2167 | 0 | 39009.4057 | 2433 | 0 |  | 1860.5 | 2492.5 | 132.2955 | 0 | 148.5348 | 0 | 1.323 | 0 | 1.4853 | 0 | 1.323 | 1.4853 | 22.3987 | 9.0169 | 21.0758
39009.4074 | 2539 | 0 | 39009.4075 | 2156 | 0 |  | 2014.5 | 2646.5 | 155.0061 | 0 | 131.6239 | 0 | 1.5501 | 0 | 1.3162 | 0 | 1.5501 | 1.3162 | 4.4655 | 23.0232 | 2.9155
39009.4092 | 2185 | 0 | 39009.4092 | 2515 | 0 |  | 2168.5 | 2800.5 | 133.3944 | 0 | 153.5409 | 0 | 1.3339 | 0 | 1.5354 | 0 | 1.3339 | 1.5354 | 21.3904 | 5.4624 | 20.0564
39009.411 | 2046 | 0 | 39009.411 | 2636 | 0 |  | 2322.5 | 2954.5 | 124.9084 | 0 | 160.928 | 0 | 1.2491 | 0 | 1.6093 | 0 | 1.2491 | 1.6093 | 29.6373 | 0.6214 | 28.3883
39009.4128 | 2395 | 0 | 39009.4128 | 2217 | 0 |  | 2476.5 | 3108.5 | 146.2149 | 0 | 135.348 | 0 | 1.4621 | 0 | 1.3535 | 0 | 1.4621 | 1.3535 | 10.7466 | 19.6382 | 9.2844
39009.4146 | 2552 | 0 | 39009.4146 | 2454 | 0 |  | 2630.5 | 3262.5 | 155.7998 | 0 | 149.8168 | 0 | 1.558 | 0 | 1.4982 | 0 | 1.558 | 1.4982 | 3.9334 | 8.0839 | 2.3754
39009.4164 | 2563 | 0 | 39009.4164 | 2569 | 0 |  | 2784.5 | 3416.5 | 156.4713 | 0 | 156.8376 | 0 | 1.5647 | 0 | 1.5684 | 0 | 1.5647 | 1.5684 | 3.4873 | 3.2456 | 1.9226

## A1-A2
Open Burn Test 1 |  |  | 2006-10-19 | 9:13 |  |  | Vs = |  | 161.989 |  | R = | 100
XLPE | 7-C | Tray G
0 | 200 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39009.3768 | 1 | 0 | 39009.3768 | 1 | 0 |  | -631.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3786 | 1 | 0 | 39009.3786 | 1 | 0 |  | -477.5 | 154.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3807 | 1 | 0 | 39009.3807 | 1 | 0 |  | -298 | 334 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3825 | 1 | 0 | 39009.3825 | 1 | 0 |  | -144 | 488 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3842 | 1 | 0 | 39009.3843 | 1 | 0 |  | 10 | 642 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.386 | 1 | 0 | 39009.386 | 1 | 0 |  | 164 | 796 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3878 | 1 | 0 | 39009.3878 | 1 | 0 |  | 318 | 950 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3896 | 1 | 0 | 39009.3896 | 1 | 0 |  | 472 | 1104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3914 | 1 | 0 | 39009.3914 | 1 | 0 |  | 625.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265238 | 265238 | 265237.9994
39009.3931 | 1 | 0 | 39009.3932 | 2575 | 0 |  | 780 | 1412 | 0.06105 | 0 | 157.2039 | 0 | 0.0006105 | 0 | 1.572 | 0 | 0.0006105 | 1.572 | 265238 | 3.0439 | 265237.9994
39009.3949 | 1 | 0 | 39009.3949 | 2200 | 0 |  | 933.5 | 1565.5 | 0.06105 | 0 | 134.3101 | 0 | 0.0006105 | 0 | 1.3431 | 0 | 0.0006105 | 1.3431 | 265238 | 20.6082 | 265237.9994
39009.3967 | 1 | 0 | 39009.3967 | 2093 | 0 |  | 1087.5 | 1719.5 | 0.06105 | 0 | 127.7778 | 0 | 0.0006105 | 0 | 1.2778 | 0 | 0.0006105 | 1.2778 | 265238 | 26.774 | 265237.9994
39009.3985 | 1 | 0 | 39009.3985 | 2036 | 0 |  | 1241.5 | 1873.5 | 0.06105 | 0 | 124.2979 | 0 | 0.0006105 | 0 | 1.243 | 0 | 0.0006105 | 1.243 | 265238 | 30.3232 | 265237.9994
39009.4003 | 1 | 0 | 39009.4003 | 5 | 3 |  | 1395.5 | 2027.5 | 0.06105 | 0 | 0.30525 | 0.18315 | 0.0006105 | 0 | 0.0030525 | 0.0018315 | 0.0006105 | 0.001221 | 265238 | 132569 | 265237.9994
39009.4021 | 12 | 8 | 39009.4021 | 2128 | 0 |  | 1549.5 | 2181.5 | 0.7326 | 0.4884 | 129.9145 | 0 | 0.007326 | 0.004884 | 1.2991 | 0 | 0.002442 | 1.2991 | 9299.5817 | 32.7826 | 8126.9102
39009.4038 | 545 | 508 | 39009.4039 | 934 | 953 |  | 1703.5 | 2335.5 | 33.2723 | 31.0134 | 57.0208 | 58.1807 | 0.33272 | 0.31013 | 0.57021 | 0.58181 | 0.022589 | 0.0116 | 5820.4001 | 65461.4087 | 314.5549
39009.4056 | 2003 | 0 | 39009.4056 | 2361 | 0 |  | 1857.5 | 2489.5 | 122.2833 | 0 | 144.1392 | 0 | 1.2228 | 0 | 1.4414 | 0 | 1.2228 | 1.4414 | 32.4703 | 12.3837 | 31.2475
39009.4074 | 2502 | 0 | 39009.4074 | 2359 | 0 |  | 2011.5 | 2643.5 | 152.7473 | 0 | 144.0171 | 0 | 1.5275 | 0 | 1.4402 | 0 | 1.5275 | 1.4402 | 6.0504 | 12.479 | 4.5229
39009.4092 | 2608 | 0 | 39009.4092 | 2469 | 0 |  | 2165.5 | 2797.5 | 159.2186 | 0 | 150.7326 | 0 | 1.5922 | 0 | 1.5073 | 0 | 1.5922 | 1.5073 | 1.74 | 7.4678 | 0.14785
39009.411 | 2256 | 0 | 39009.411 | 2504 | 0 |  | 2319.5 | 2951.5 | 137.7289 | 0 | 152.8694 | 0 | 1.3773 | 0 | 1.5287 | 0 | 1.3773 | 1.5287 | 17.6144 | 5.9657 | 16.2371
39009.4128 | 2045 | 0 | 39009.4128 | 2430 | 0 |  | 2473.5 | 3105.5 | 124.8474 | 0 | 148.3516 | 0 | 1.2485 | 0 | 1.4835 | 0 | 1.2485 | 1.4835 | 29.7496 | 9.1926 | 28.5012
39009.4145 | 2183 | 0 | 39009.4145 | 2500 | 0 |  | 2627.5 | 3259.5 | 133.2723 | 0 | 152.6252 | 0 | 1.3327 | 0 | 1.5263 | 0 | 1.3327 | 1.5263 | 21.5474 | 6.1352 | 20.2147
39009.4163 | 2228 | 0 | 39009.4163 | 2637 | 0 |  | 2781.5 | 3413.5 | 136.0195 | 0 | 160.989 | 0 | 1.3602 | 0 | 1.6099 | 0 | 1.3602 | 1.6099 | 19.0925 | 0.62116 | 17.7323

## Temperatures
DAQ Time | Burner Time | Bundle Center | Bundle, 1-Layer In | Air Above Bundle | Air Below Bundle | TRAY G
0 | -632 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
1 | -631 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
2 | -630 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
3 | -629 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
4 | -628 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
5 | -627 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
6 | -626 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
7 | -625 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
8 | -624 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
9 | -623 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
10 | -622 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
11 | -621 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
12 | -620 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
13 | -619 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
14 | -618 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
15 | -617 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
16 | -616 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
17 | -615 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
18 | -614 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
19 | -613 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
20 | -612 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
21 | -611 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
22 | -610 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
23 | -609 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
24 | -608 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
25 | -607 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
26 | -606 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
27 | -605 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
28 | -604 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
29 | -603 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
30 | -602 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
31 | -601 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
32 | -600 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
33 | -599 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
34 | -598 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
35 | -597 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
36 | -596 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
37 | -595 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
38 | -594 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
39 | -593 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
40 | -592 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
41 | -591 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
42 | -590 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
43 | -589 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
44 | -588 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
45 | -587 | 16.7 | 16.3 | 15.8 | 15.2 | 17.5
46 | -586 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
47 | -585 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
48 | -584 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
49 | -583 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
50 | -582 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
51 | -581 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
52 | -580 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
53 | -579 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
54 | -578 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
55 | -577 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
56 | -576 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
57 | -575 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
58 | -574 | 16.7 | 16.3 | 15.8 | 15.3 | 17.5
59 | -573 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
60 | -572 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
61 | -571 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
62 | -570 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
63 | -569 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
64 | -568 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
65 | -567 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
66 | -566 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
67 | -565 | 16.7 | 16.3 | 15.7 | 15.2 | 17.5
68 | -564 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
69 | -563 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
70 | -562 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
71 | -561 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
72 | -560 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
73 | -559 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
74 | -558 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
75 | -557 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
76 | -556 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
77 | -555 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
78 | -554 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
79 | -553 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
80 | -552 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
81 | -551 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
82 | -550 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
83 | -549 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
84 | -548 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
85 | -547 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
86 | -546 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
87 | -545 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
88 | -544 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
89 | -543 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
90 | -542 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
91 | -541 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
92 | -540 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
93 | -539 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
94 | -538 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
95 | -537 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
96 | -536 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
97 | -535 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
98 | -534 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
99 | -533 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
100 | -532 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
101 | -531 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
102 | -530 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
103 | -529 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
104 | -528 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
105 | -527 | 16.7 | 16.3 | 15.7 | 15.1 | 17.5
106 | -526 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
107 | -525 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
108 | -524 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
109 | -523 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
110 | -522 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
111 | -521 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
112 | -520 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
113 | -519 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
114 | -518 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
115 | -517 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
116 | -516 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
117 | -515 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
118 | -514 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
119 | -513 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
120 | -512 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
121 | -511 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
122 | -510 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
123 | -509 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
124 | -508 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
125 | -507 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
126 | -506 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
127 | -505 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
128 | -504 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
129 | -503 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
130 | -502 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
131 | -501 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
132 | -500 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
133 | -499 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
134 | -498 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
135 | -497 | 16.7 | 16.3 | 15.6 | 15.1 | 17.5
136 | -496 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
137 | -495 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
138 | -494 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
139 | -493 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
140 | -492 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
141 | -491 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
142 | -490 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
143 | -489 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
144 | -488 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
145 | -487 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
146 | -486 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
147 | -485 | 16.7 | 16.3 | 15.6 | 15.1 | 17.4
148 | -484 | 16.7 | 16.3 | 15.6 | 15 | 17.4
149 | -483 | 16.7 | 16.3 | 15.6 | 15 | 17.4
150 | -482 | 16.7 | 16.3 | 15.6 | 15 | 17.4
151 | -481 | 16.7 | 16.3 | 15.6 | 15 | 17.4
152 | -480 | 16.7 | 16.3 | 15.6 | 15 | 17.4
153 | -479 | 16.7 | 16.3 | 15.6 | 15 | 17.4
154 | -478 | 16.7 | 16.3 | 15.6 | 15 | 17.4
155 | -477 | 16.7 | 16.3 | 15.6 | 15 | 17.4
156 | -476 | 16.7 | 16.3 | 15.6 | 15 | 17.4
157 | -475 | 16.7 | 16.3 | 15.6 | 15 | 17.4
158 | -474 | 16.7 | 16.3 | 15.6 | 15 | 17.4
159 | -473 | 16.7 | 16.3 | 15.6 | 15 | 17.4
160 | -472 | 16.7 | 16.3 | 15.6 | 15 | 17.4
161 | -471 | 16.7 | 16.3 | 15.6 | 15 | 17.4
162 | -470 | 16.7 | 16.3 | 15.6 | 15 | 17.4
163 | -469 | 16.7 | 16.3 | 15.6 | 15 | 17.4
164 | -468 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
165 | -467 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
166 | -466 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
167 | -465 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
168 | -464 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
169 | -463 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
170 | -462 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
171 | -461 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
172 | -460 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
173 | -459 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
174 | -458 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
175 | -457 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
176 | -456 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
177 | -455 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
178 | -454 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
179 | -453 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
180 | -452 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
181 | -451 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
182 | -450 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
183 | -449 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
184 | -448 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
185 | -447 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
186 | -446 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
187 | -445 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
188 | -444 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
189 | -443 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
190 | -442 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
191 | -441 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
192 | -440 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
193 | -439 | 16.7 | 16.3 | 15.6 | 15 | 17.4
194 | -438 | 16.7 | 16.3 | 15.6 | 15 | 17.4
195 | -437 | 16.7 | 16.3 | 15.6 | 15 | 17.4
196 | -436 | 16.7 | 16.3 | 15.6 | 15 | 17.4
197 | -435 | 16.7 | 16.3 | 15.6 | 15 | 17.4
198 | -434 | 16.7 | 16.3 | 15.6 | 15 | 17.4
199 | -433 | 16.7 | 16.3 | 15.6 | 15 | 17.4
200 | -432 | 16.7 | 16.3 | 15.6 | 15 | 17.4
201 | -431 | 16.7 | 16.3 | 15.6 | 15 | 17.4
202 | -430 | 16.7 | 16.3 | 15.6 | 15 | 17.4
203 | -429 | 16.7 | 16.3 | 15.6 | 15 | 17.4
204 | -428 | 16.7 | 16.3 | 15.6 | 15 | 17.4
205 | -427 | 16.7 | 16.3 | 15.6 | 15 | 17.4
206 | -426 | 16.7 | 16.3 | 15.6 | 15 | 17.4
207 | -425 | 16.7 | 16.3 | 15.6 | 15 | 17.4
208 | -424 | 16.7 | 16.3 | 15.6 | 15 | 17.4
209 | -423 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
210 | -422 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
211 | -421 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
212 | -420 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
213 | -419 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
214 | -418 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
215 | -417 | 16.7 | 16.3 | 15.6 | 14.9 | 17.4
216 | -416 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
217 | -415 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
218 | -414 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
219 | -413 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
220 | -412 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
221 | -411 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
222 | -410 | 16.7 | 16.3 | 15.5 | 15 | 17.4
223 | -409 | 16.7 | 16.3 | 15.5 | 15 | 17.4
224 | -408 | 16.7 | 16.3 | 15.5 | 15 | 17.4
225 | -407 | 16.7 | 16.3 | 15.5 | 15 | 17.4
226 | -406 | 16.7 | 16.3 | 15.5 | 15 | 17.4
227 | -405 | 16.7 | 16.3 | 15.5 | 15 | 17.4
228 | -404 | 16.7 | 16.3 | 15.5 | 15 | 17.4
229 | -403 | 16.7 | 16.3 | 15.5 | 15 | 17.4
230 | -402 | 16.7 | 16.3 | 15.5 | 15 | 17.4
231 | -401 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
232 | -400 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
233 | -399 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
234 | -398 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
235 | -397 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
236 | -396 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
237 | -395 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
238 | -394 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
239 | -393 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
240 | -392 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
241 | -391 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
242 | -390 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
243 | -389 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
244 | -388 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
245 | -387 | 16.7 | 16.3 | 15.5 | 14.9 | 17.3
246 | -386 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
247 | -385 | 16.7 | 16.3 | 15.5 | 14.9 | 17.4
248 | -384 | 16.7 | 16.3 | 15.5 | 14.8 | 17.4
249 | -383 | 16.7 | 16.3 | 15.5 | 14.8 | 17.4
250 | -382 | 16.7 | 16.3 | 15.5 | 14.8 | 17.4
251 | -381 | 16.7 | 16.3 | 15.5 | 14.8 | 17.4
252 | -380 | 16.7 | 16.3 | 15.5 | 14.8 | 17.3
253 | -379 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
254 | -378 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
255 | -377 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
256 | -376 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
257 | -375 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
258 | -374 | 16.7 | 16.3 | 15.4 | 14.7 | 17.4
259 | -373 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
260 | -372 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
261 | -371 | 16.7 | 16.3 | 15.4 | 14.7 | 17.4
262 | -370 | 16.7 | 16.3 | 15.4 | 14.7 | 17.4
263 | -369 | 16.7 | 16.3 | 15.4 | 14.7 | 17.4
264 | -368 | 16.7 | 16.3 | 15.4 | 14.7 | 17.4
265 | -367 | 16.7 | 16.3 | 15.4 | 14.7 | 17.4
266 | -366 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
267 | -365 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
268 | -364 | 16.7 | 16.3 | 15.4 | 14.8 | 17.4
269 | -363 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
270 | -362 | 16.7 | 16.3 | 15.4 | 14.8 | 17.4
271 | -361 | 16.7 | 16.3 | 15.4 | 14.8 | 17.4
272 | -360 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
273 | -359 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
274 | -358 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
275 | -357 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
276 | -356 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
277 | -355 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
278 | -354 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
279 | -353 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
280 | -352 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
281 | -351 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
282 | -350 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
283 | -349 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
284 | -348 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
285 | -347 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
286 | -346 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
287 | -345 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
288 | -344 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
289 | -343 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
290 | -342 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
291 | -341 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
292 | -340 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
293 | -339 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
294 | -338 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
295 | -337 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
296 | -336 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
297 | -335 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
298 | -334 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
299 | -333 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
300 | -332 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
301 | -331 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
302 | -330 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
303 | -329 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
304 | -328 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
305 | -327 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
306 | -326 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
307 | -325 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
308 | -324 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
309 | -323 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
310 | -322 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
311 | -321 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
312 | -320 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
313 | -319 | 16.7 | 16.3 | 15.4 | 14.6 | 17.3
314 | -318 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
315 | -317 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
316 | -316 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
317 | -315 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
318 | -314 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
319 | -313 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
320 | -312 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
321 | -311 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
322 | -310 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
323 | -309 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
324 | -308 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
325 | -307 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
326 | -306 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
327 | -305 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
328 | -304 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
329 | -303 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
330 | -302 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
331 | -301 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
332 | -300 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
333 | -299 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
334 | -298 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
335 | -297 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
336 | -296 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
337 | -295 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
338 | -294 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
339 | -293 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
340 | -292 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
341 | -291 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
342 | -290 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
343 | -289 | 16.7 | 16.3 | 15.4 | 14.8 | 17.3
344 | -288 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
345 | -287 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
346 | -286 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
347 | -285 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
348 | -284 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
349 | -283 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
350 | -282 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
351 | -281 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
352 | -280 | 16.7 | 16.3 | 15.4 | 14.7 | 17.3
353 | -279 | 16.7 | 16.3 | 15.3 | 14.7 | 17.3
354 | -278 | 16.7 | 16.3 | 15.3 | 14.7 | 17.3
355 | -277 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
356 | -276 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
357 | -275 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
358 | -274 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
359 | -273 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
360 | -272 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
361 | -271 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
362 | -270 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
363 | -269 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
364 | -268 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
365 | -267 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
366 | -266 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
367 | -265 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
368 | -264 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
369 | -263 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
370 | -262 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
371 | -261 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
372 | -260 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
373 | -259 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
374 | -258 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
375 | -257 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
376 | -256 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
377 | -255 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
378 | -254 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
379 | -253 | 16.7 | 16.3 | 15.3 | 14.6 | 17.3
380 | -252 | 16.7 | 16.3 | 15.3 | 14.5 | 17.3
381 | -251 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
382 | -250 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
383 | -249 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
384 | -248 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
385 | -247 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
386 | -246 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
387 | -245 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
388 | -244 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
389 | -243 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
390 | -242 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
391 | -241 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
392 | -240 | 16.7 | 16.3 | 15.3 | 14.5 | 17.2
393 | -239 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
394 | -238 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
395 | -237 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
396 | -236 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
397 | -235 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
398 | -234 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
399 | -233 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
400 | -232 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
401 | -231 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
402 | -230 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
403 | -229 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
404 | -228 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
405 | -227 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
406 | -226 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
407 | -225 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
408 | -224 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
409 | -223 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
410 | -222 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
411 | -221 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
412 | -220 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
413 | -219 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
414 | -218 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
415 | -217 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
416 | -216 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
417 | -215 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
418 | -214 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
419 | -213 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
420 | -212 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
421 | -211 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
422 | -210 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
423 | -209 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
424 | -208 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
425 | -207 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
426 | -206 | 16.7 | 16.3 | 15.2 | 14.7 | 17.2
427 | -205 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
428 | -204 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
429 | -203 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
430 | -202 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
431 | -201 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
432 | -200 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
433 | -199 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
434 | -198 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
435 | -197 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
436 | -196 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
437 | -195 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
438 | -194 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
439 | -193 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
440 | -192 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
441 | -191 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
442 | -190 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
443 | -189 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
444 | -188 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
445 | -187 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
446 | -186 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
447 | -185 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
448 | -184 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
449 | -183 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
450 | -182 | 16.7 | 16.3 | 15.3 | 14.7 | 17.2
451 | -181 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
452 | -180 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
453 | -179 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
454 | -178 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
455 | -177 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
456 | -176 | 16.7 | 16.3 | 15.3 | 14.6 | 17.2
457 | -175 | 16.7 | 16.3 | 15.2 | 14.7 | 17.2
458 | -174 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
459 | -173 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
460 | -172 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
461 | -171 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
462 | -170 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
463 | -169 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
464 | -168 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
465 | -167 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
466 | -166 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
467 | -165 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
468 | -164 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
469 | -163 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
470 | -162 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
471 | -161 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
472 | -160 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
473 | -159 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
474 | -158 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
475 | -157 | 16.7 | 16.3 | 15.1 | 14.6 | 17.2
476 | -156 | 16.7 | 16.3 | 15.1 | 14.6 | 17.2
477 | -155 | 16.7 | 16.3 | 15.1 | 14.6 | 17.2
478 | -154 | 16.7 | 16.3 | 15.1 | 14.6 | 17.2
479 | -153 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
480 | -152 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
481 | -151 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
482 | -150 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
483 | -149 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
484 | -148 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
485 | -147 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
486 | -146 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
487 | -145 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
488 | -144 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
489 | -143 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
490 | -142 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
491 | -141 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
492 | -140 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
493 | -139 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
494 | -138 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
495 | -137 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
496 | -136 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
497 | -135 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
498 | -134 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
499 | -133 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
500 | -132 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
501 | -131 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
502 | -130 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
503 | -129 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
504 | -128 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
505 | -127 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
506 | -126 | 16.7 | 16.3 | 15.2 | 14.6 | 17.2
507 | -125 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
508 | -124 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
509 | -123 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
510 | -122 | 16.6 | 16.3 | 15.2 | 14.6 | 17.1
511 | -121 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
512 | -120 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
513 | -119 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
514 | -118 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
515 | -117 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
516 | -116 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
517 | -115 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
518 | -114 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
519 | -113 | 16.7 | 16.3 | 15.2 | 14.5 | 17.2
520 | -112 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
521 | -111 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
522 | -110 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
523 | -109 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
524 | -108 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
525 | -107 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
526 | -106 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
527 | -105 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
528 | -104 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
529 | -103 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
530 | -102 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
531 | -101 | 16.6 | 16.3 | 15.3 | 14.5 | 17.1
532 | -100 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
533 | -99 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
534 | -98 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
535 | -97 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
536 | -96 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
537 | -95 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
538 | -94 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
539 | -93 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
540 | -92 | 16.6 | 16.3 | 15.3 | 14.6 | 17.1
541 | -91 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
542 | -90 | 16.7 | 16.3 | 15.3 | 14.6 | 17.1
543 | -89 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
544 | -88 | 16.7 | 16.3 | 15.3 | 14.6 | 17.1
545 | -87 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
546 | -86 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
547 | -85 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
548 | -84 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
549 | -83 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
550 | -82 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
551 | -81 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
552 | -80 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
553 | -79 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
554 | -78 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
555 | -77 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
556 | -76 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
557 | -75 | 16.6 | 16.3 | 15.2 | 14.6 | 17.1
558 | -74 | 16.7 | 16.3 | 15.2 | 14.6 | 17.1
559 | -73 | 16.6 | 16.3 | 15.2 | 14.6 | 17.1
560 | -72 | 16.6 | 16.3 | 15.2 | 14.6 | 17.1
561 | -71 | 16.6 | 16.3 | 15.2 | 14.6 | 17.1
562 | -70 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
563 | -69 | 16.6 | 16.3 | 15.2 | 14.5 | 17.1
564 | -68 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
565 | -67 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
566 | -66 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
567 | -65 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
568 | -64 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
569 | -63 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
570 | -62 | 16.7 | 16.3 | 15.2 | 14.5 | 17.1
571 | -61 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
572 | -60 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
573 | -59 | 16.6 | 16.3 | 15.3 | 14.5 | 17.1
574 | -58 | 16.6 | 16.3 | 15.3 | 14.5 | 17.1
575 | -57 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
576 | -56 | 16.6 | 16.3 | 15.3 | 14.5 | 17.1
577 | -55 | 16.7 | 16.3 | 15.3 | 14.5 | 17.1
578 | -54 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
579 | -53 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
580 | -52 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
581 | -51 | 16.7 | 16.3 | 15.3 | 14.4 | 17.1
582 | -50 | 16.7 | 16.2 | 15.2 | 14.4 | 17.1
583 | -49 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
584 | -48 | 16.7 | 16.3 | 15.3 | 14.4 | 17.1
585 | -47 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
586 | -46 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
587 | -45 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
588 | -44 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
589 | -43 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
590 | -42 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
591 | -41 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
592 | -40 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
593 | -39 | 16.7 | 16.2 | 15.2 | 14.4 | 17.1
594 | -38 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
595 | -37 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
596 | -36 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
597 | -35 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
598 | -34 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
599 | -33 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
600 | -32 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
601 | -31 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
602 | -30 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
603 | -29 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
604 | -28 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
605 | -27 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
606 | -26 | 16.7 | 16.2 | 15.2 | 14.4 | 17.1
607 | -25 | 16.7 | 16.2 | 15.2 | 14.4 | 17.1
608 | -24 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
609 | -23 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
610 | -22 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
611 | -21 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
612 | -20 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
613 | -19 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
614 | -18 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
615 | -17 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
616 | -16 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
617 | -15 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
618 | -14 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
619 | -13 | 16.7 | 16.2 | 15.2 | 14.4 | 17.1
620 | -12 | 16.7 | 16.2 | 15.2 | 14.4 | 17.1
621 | -11 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
622 | -10 | 16.6 | 16.2 | 15.2 | 14.5 | 17.1
623 | -9 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
624 | -8 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
625 | -7 | 16.7 | 16.3 | 15.2 | 14.4 | 17.1
626 | -6 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
627 | -5 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
628 | -4 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
629 | -3 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
630 | -2 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
631 | -1 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
632 | 0 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
633 | 1 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
634 | 2 | 16.6 | 16.3 | 15.2 | 14.4 | 17.1
635 | 3 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
636 | 4 | 16.6 | 16.2 | 15.2 | 14.4 | 17.1
637 | 5 | 16.6 | 16.2 | 15.3 | 14.5 | 17.1
638 | 6 | 16.6 | 16.3 | 15.6 | 15.1 | 17.1
639 | 7 | 16.6 | 16.3 | 16 | 16.1 | 17.2
640 | 8 | 16.6 | 16.3 | 16.4 | 16.4 | 17.3
641 | 9 | 16.6 | 16.3 | 17 | 16.7 | 17.3
642 | 10 | 16.6 | 16.2 | 17.4 | 16.9 | 17.4
643 | 11 | 16.6 | 16.3 | 17.5 | 17 | 17.4
644 | 12 | 16.6 | 16.3 | 17.7 | 17.2 | 17.5
645 | 13 | 16.6 | 16.3 | 17.9 | 17.7 | 17.6
646 | 14 | 16.6 | 16.3 | 18.6 | 18.2 | 17.7
647 | 15 | 16.6 | 16.3 | 19.5 | 19 | 17.8
648 | 16 | 16.6 | 16.3 | 20.7 | 19.8 | 17.9
649 | 17 | 16.6 | 16.3 | 22.2 | 20.7 | 18.1
650 | 18 | 16.6 | 16.3 | 24.4 | 22 | 18.3
651 | 19 | 16.6 | 16.3 | 26.6 | 23.5 | 18.5
652 | 20 | 16.6 | 16.2 | 28.7 | 24.8 | 18.7
653 | 21 | 16.6 | 16.3 | 30.7 | 26 | 18.9
654 | 22 | 16.6 | 16.3 | 33 | 27.9 | 19.2
655 | 23 | 16.6 | 16.3 | 35.3 | 29.9 | 19.5
656 | 24 | 16.6 | 16.3 | 37.9 | 31.2 | 19.6
657 | 25 | 16.6 | 16.2 | 40.3 | 32.9 | 19.8
658 | 26 | 16.6 | 16.3 | 42.4 | 34.7 | 20
659 | 27 | 16.6 | 16.3 | 44.5 | 37.2 | 20.3
660 | 28 | 16.6 | 16.3 | 46.8 | 39.9 | 20.7
661 | 29 | 16.6 | 16.3 | 49.2 | 42.3 | 20.8
662 | 30 | 16.6 | 16.3 | 52 | 43.9 | 21.1
663 | 31 | 16.6 | 16.3 | 55 | 45.4 | 21.5
664 | 32 | 16.6 | 16.3 | 58.7 | 47.2 | 21.9
665 | 33 | 16.6 | 16.3 | 62.6 | 48.6 | 22.4
666 | 34 | 16.6 | 16.3 | 65.7 | 51.1 | 22.9
667 | 35 | 16.6 | 16.2 | 68.9 | 52.7 | 23.4
668 | 36 | 16.6 | 16.3 | 72.4 | 54.3 | 23.6
669 | 37 | 16.6 | 16.3 | 75 | 56.1 | 23.9
670 | 38 | 16.6 | 16.3 | 78 | 58.8 | 24.2
671 | 39 | 16.6 | 16.3 | 80.8 | 60.5 | 24.5
672 | 40 | 16.6 | 16.3 | 83.2 | 62.1 | 24.7
673 | 41 | 16.6 | 16.3 | 85.1 | 64.5 | 25.2
674 | 42 | 16.6 | 16.3 | 87.1 | 66.2 | 25.5
675 | 43 | 16.6 | 16.2 | 88.9 | 68 | 25.9
676 | 44 | 16.6 | 16.3 | 90.4 | 69.6 | 26.2
677 | 45 | 16.6 | 16.3 | 92.4 | 71.6 | 26.3
678 | 46 | 16.6 | 16.3 | 94.5 | 73.7 | 26.7
679 | 47 | 16.6 | 16.3 | 96.8 | 75.4 | 27.4
680 | 48 | 16.6 | 16.3 | 98.9 | 77.1 | 27.7
681 | 49 | 16.6 | 16.3 | 101.3 | 78.8 | 28
682 | 50 | 16.6 | 16.2 | 103.8 | 80.8 | 28.2
683 | 51 | 16.6 | 16.3 | 105.8 | 82.9 | 28.4
684 | 52 | 16.6 | 16.2 | 107.8 | 84.8 | 29.1
685 | 53 | 16.6 | 16.3 | 109.9 | 86 | 29.4
686 | 54 | 16.6 | 16.3 | 111.5 | 87.2 | 29.6
687 | 55 | 16.6 | 16.3 | 113.4 | 88.5 | 30
688 | 56 | 16.6 | 16.3 | 115.3 | 89.8 | 30.4
689 | 57 | 16.6 | 16.3 | 117.2 | 91.3 | 30.7
690 | 58 | 16.6 | 16.3 | 119 | 92.7 | 31.1
691 | 59 | 16.6 | 16.3 | 120.5 | 94.7 | 31.7
692 | 60 | 16.6 | 16.3 | 121.9 | 95.7 | 32.1
693 | 61 | 16.6 | 16.3 | 123.7 | 97.1 | 32.4
694 | 62 | 16.6 | 16.3 | 125.8 | 98.1 | 32.9
695 | 63 | 16.6 | 16.3 | 127.6 | 99.6 | 33.3
696 | 64 | 16.6 | 16.3 | 129.1 | 101.1 | 33.7
697 | 65 | 16.6 | 16.3 | 131.6 | 102.5 | 34.1
698 | 66 | 16.6 | 16.3 | 133.5 | 103.7 | 34.3
699 | 67 | 16.6 | 16.3 | 134.9 | 104.7 | 34.6
700 | 68 | 16.6 | 16.3 | 136.3 | 105.7 | 35.1
701 | 69 | 16.6 | 16.3 | 137.5 | 106.5 | 35.5
702 | 70 | 16.6 | 16.3 | 138.8 | 107.2 | 35.9
703 | 71 | 16.6 | 16.3 | 139.7 | 108.8 | 36.1
704 | 72 | 16.6 | 16.3 | 140.6 | 109.9 | 36.5
705 | 73 | 16.6 | 16.3 | 141.5 | 110.6 | 36.9
706 | 74 | 16.6 | 16.3 | 142.2 | 111.4 | 37.6
707 | 75 | 16.6 | 16.3 | 143.1 | 112.6 | 37.9
708 | 76 | 16.6 | 16.3 | 144 | 113.7 | 38.3
709 | 77 | 16.6 | 16.3 | 144.9 | 115 | 38.8
710 | 78 | 16.7 | 16.3 | 145.7 | 116.8 | 39.2
711 | 79 | 16.6 | 16.3 | 146.9 | 118.5 | 39.5
712 | 80 | 16.7 | 16.3 | 147.2 | 119.5 | 39.9
713 | 81 | 16.7 | 16.3 | 147.4 | 119.7 | 40.2
714 | 82 | 16.7 | 16.3 | 148.3 | 119.8 | 40.6
715 | 83 | 16.7 | 16.3 | 149.3 | 120.6 | 41
716 | 84 | 16.7 | 16.3 | 150.6 | 121.3 | 41.5
717 | 85 | 16.7 | 16.3 | 151.7 | 121.9 | 42.1
718 | 86 | 16.7 | 16.3 | 152.4 | 122.9 | 42.5
719 | 87 | 16.7 | 16.3 | 152.7 | 123.6 | 42.7
720 | 88 | 16.7 | 16.3 | 153.2 | 124.1 | 42.9
721 | 89 | 16.7 | 16.3 | 153.7 | 124.1 | 43.4
722 | 90 | 16.7 | 16.3 | 154.1 | 124.8 | 43.6
723 | 91 | 16.7 | 16.3 | 154.4 | 125.1 | 44
724 | 92 | 16.7 | 16.3 | 154.7 | 125.8 | 44.3
725 | 93 | 16.7 | 16.3 | 155.2 | 126.4 | 44.8
726 | 94 | 16.7 | 16.3 | 156.1 | 127.4 | 45.3
727 | 95 | 16.7 | 16.4 | 156.8 | 128.3 | 45.7
728 | 96 | 16.7 | 16.4 | 157.2 | 128.9 | 46.1
729 | 97 | 16.7 | 16.4 | 158 | 129.4 | 46.4
730 | 98 | 16.7 | 16.4 | 158.5 | 130.8 | 47
731 | 99 | 16.7 | 16.4 | 159.2 | 131.9 | 47.4
732 | 100 | 16.7 | 16.4 | 160.1 | 132.6 | 47.8
733 | 101 | 16.7 | 16.4 | 160.4 | 133.4 | 48.2
734 | 102 | 16.7 | 16.4 | 161.1 | 134.1 | 48.5
735 | 103 | 16.7 | 16.4 | 161.5 | 134.6 | 49
736 | 104 | 16.7 | 16.4 | 161.9 | 135 | 49.2
737 | 105 | 16.7 | 16.4 | 162.1 | 135.4 | 49.6
738 | 106 | 16.7 | 16.4 | 162.4 | 135.9 | 50
739 | 107 | 16.7 | 16.4 | 162.6 | 136.2 | 50.4
740 | 108 | 16.8 | 16.4 | 162.9 | 136.9 | 50.8
741 | 109 | 16.8 | 16.4 | 163.1 | 137.2 | 51.1
742 | 110 | 16.8 | 16.5 | 163.3 | 137.5 | 51.5
743 | 111 | 16.8 | 16.5 | 163.8 | 138 | 51.8
744 | 112 | 16.8 | 16.5 | 163.9 | 138.6 | 52.2
745 | 113 | 16.8 | 16.5 | 164.4 | 139.3 | 52.6
746 | 114 | 16.8 | 16.5 | 165.1 | 139.4 | 53.2
747 | 115 | 16.8 | 16.5 | 165.6 | 139.1 | 53.9
748 | 116 | 16.8 | 16.5 | 166.5 | 139.3 | 54.4
749 | 117 | 16.8 | 16.5 | 167 | 139.9 | 54.9
750 | 118 | 16.8 | 16.5 | 167.9 | 140.9 | 55.1
751 | 119 | 16.8 | 16.5 | 168.3 | 141.2 | 55.1
752 | 120 | 16.8 | 16.5 | 169 | 141.9 | 55.4
753 | 121 | 16.8 | 16.6 | 170.1 | 142.6 | 55.8
754 | 122 | 16.8 | 16.6 | 170.6 | 143.4 | 56.1
755 | 123 | 16.8 | 16.6 | 170.8 | 143.8 | 56.3
756 | 124 | 16.8 | 16.6 | 170.7 | 144.6 | 57
757 | 125 | 16.8 | 16.6 | 171.1 | 145 | 57.4
758 | 126 | 16.8 | 16.6 | 171.1 | 144.9 | 57.8
759 | 127 | 16.9 | 16.6 | 171.5 | 145 | 58.3
760 | 128 | 16.9 | 16.6 | 171.7 | 145 | 58.8
761 | 129 | 16.9 | 16.6 | 171.9 | 145.2 | 59.3
762 | 130 | 16.9 | 16.7 | 172.3 | 145.6 | 59.7
763 | 131 | 16.9 | 16.7 | 172.6 | 145.9 | 60.2
764 | 132 | 16.9 | 16.7 | 172.9 | 146.1 | 60.6
765 | 133 | 16.9 | 16.7 | 173 | 146.3 | 61.1
766 | 134 | 16.9 | 16.7 | 173.3 | 146.9 | 61.6
767 | 135 | 16.9 | 16.7 | 173.6 | 147.7 | 62.1
768 | 136 | 16.9 | 16.7 | 173.8 | 148.1 | 62.5
769 | 137 | 16.9 | 16.8 | 173.8 | 148.2 | 62.8
770 | 138 | 16.9 | 16.8 | 173.9 | 148.1 | 63.1
771 | 139 | 16.9 | 16.8 | 173.9 | 148.2 | 63.2
772 | 140 | 17 | 16.8 | 173.9 | 149.3 | 63.7
773 | 141 | 17 | 16.8 | 174.3 | 149.5 | 64.2
774 | 142 | 17 | 16.8 | 174.5 | 149.5 | 64.3
775 | 143 | 17 | 16.8 | 174.2 | 150.7 | 64.7
776 | 144 | 17 | 16.8 | 173.9 | 150.8 | 65.1
777 | 145 | 17 | 16.9 | 173.7 | 151 | 65.5
778 | 146 | 17 | 16.9 | 173.6 | 151.4 | 65.7
779 | 147 | 17 | 16.9 | 173.6 | 151.7 | 66.3
780 | 148 | 17 | 16.9 | 173.7 | 151.6 | 66.7
781 | 149 | 17 | 16.9 | 173.9 | 151.6 | 66.8
782 | 150 | 17 | 16.9 | 174.2 | 151.3 | 66.9
783 | 151 | 17.1 | 16.9 | 174.2 | 151.4 | 67
784 | 152 | 17.1 | 17 | 174.5 | 151.6 | 67.2
785 | 153 | 17.1 | 17 | 175.3 | 152.2 | 67.7
786 | 154 | 17.1 | 17 | 176 | 152.5 | 68.1
787 | 155 | 17.1 | 17 | 176.7 | 152.8 | 68.6
788 | 156 | 17.1 | 17 | 176.8 | 153.1 | 68.7
789 | 157 | 17.1 | 17.1 | 176.8 | 152.9 | 69
790 | 158 | 17.1 | 17.1 | 177.1 | 153 | 69.3
791 | 159 | 17.1 | 17.1 | 177.2 | 152.6 | 69.5
792 | 160 | 17.2 | 17.1 | 177.2 | 153.4 | 69.8
793 | 161 | 17.2 | 17.1 | 177.2 | 153.8 | 70.2
794 | 162 | 17.2 | 17.1 | 177 | 153.8 | 70.6
795 | 163 | 17.2 | 17.2 | 176.9 | 153.9 | 71
796 | 164 | 17.2 | 17.2 | 176.8 | 154.3 | 71.4
797 | 165 | 17.2 | 17.2 | 176.6 | 154.7 | 71.7
798 | 166 | 17.2 | 17.2 | 176.6 | 154.6 | 72.1
799 | 167 | 17.2 | 17.2 | 176.6 | 154.6 | 72.4
800 | 168 | 17.3 | 17.2 | 176.6 | 154.3 | 72.7
801 | 169 | 17.3 | 17.3 | 176.5 | 154.3 | 72.8
802 | 170 | 17.3 | 17.3 | 176.4 | 154.1 | 72.9
803 | 171 | 17.3 | 17.3 | 176.3 | 154.5 | 73.2
804 | 172 | 17.3 | 17.3 | 176.5 | 154.4 | 73.5
805 | 173 | 17.3 | 17.4 | 176.3 | 154.1 | 74
806 | 174 | 17.3 | 17.4 | 176.4 | 153.9 | 74.1
807 | 175 | 17.4 | 17.4 | 176.5 | 154 | 74.3
808 | 176 | 17.4 | 17.4 | 176.5 | 153.9 | 74.5
809 | 177 | 17.4 | 17.4 | 176.4 | 154.1 | 74.8
810 | 178 | 17.4 | 17.5 | 176.5 | 154.3 | 75.1
811 | 179 | 17.4 | 17.5 | 177.4 | 154.2 | 75.5
812 | 180 | 17.4 | 17.5 | 178.6 | 154.4 | 75.9
813 | 181 | 17.4 | 17.5 | 179.7 | 154.1 | 76.2
814 | 182 | 17.5 | 17.6 | 180.4 | 153.7 | 76.5
815 | 183 | 17.5 | 17.6 | 180.7 | 154.3 | 76.9
816 | 184 | 17.5 | 17.6 | 180.8 | 154.9 | 77.3
817 | 185 | 17.5 | 17.6 | 180.8 | 155.3 | 77.6
818 | 186 | 17.5 | 17.6 | 180.9 | 155.7 | 77.9
819 | 187 | 17.5 | 17.7 | 180.9 | 156.2 | 78.2
820 | 188 | 17.6 | 17.7 | 180.8 | 156.4 | 78.8
821 | 189 | 17.6 | 17.7 | 180.8 | 156.1 | 79.1
822 | 190 | 17.6 | 17.7 | 180.6 | 156.4 | 79.4
823 | 191 | 17.6 | 17.7 | 180.4 | 156.5 | 79.6
824 | 192 | 17.6 | 17.8 | 180.3 | 156.4 | 79.9
825 | 193 | 17.6 | 17.8 | 180.2 | 156.9 | 80.1
826 | 194 | 17.6 | 17.8 | 180.1 | 157.5 | 80.4
827 | 195 | 17.7 | 17.8 | 180.2 | 158 | 80.7
828 | 196 | 17.7 | 17.8 | 180.4 | 158.2 | 81.1
829 | 197 | 17.7 | 17.9 | 180.2 | 158.4 | 81.4
830 | 198 | 17.7 | 17.9 | 180.6 | 158.4 | 81.7
831 | 199 | 17.7 | 17.9 | 180.8 | 158.6 | 82.1
832 | 200 | 17.7 | 17.9 | 180.6 | 158.7 | 82.2
833 | 201 | 17.8 | 17.9 | 180.6 | 158.6 | 82.4
834 | 202 | 17.8 | 18 | 180.8 | 158.8 | 82.8
835 | 203 | 17.8 | 18 | 181.4 | 158.8 | 83
836 | 204 | 17.8 | 18 | 182 | 159.5 | 83.4
837 | 205 | 17.9 | 18 | 182.5 | 159.4 | 83.5
838 | 206 | 17.9 | 18 | 182.9 | 159.4 | 83.7
839 | 207 | 17.9 | 18.1 | 183.7 | 159.2 | 84.2
840 | 208 | 17.9 | 18.1 | 184.2 | 159 | 84.5
841 | 209 | 17.9 | 18.1 | 184.6 | 159.2 | 84.7
842 | 210 | 17.9 | 18.1 | 184.6 | 159.5 | 85.2
843 | 211 | 18 | 18.2 | 184.8 | 160.1 | 85.7
844 | 212 | 18 | 18.2 | 184.7 | 160.3 | 85.8
845 | 213 | 18 | 18.2 | 184.7 | 160.5 | 86
846 | 214 | 18 | 18.2 | 184.8 | 160.8 | 86.3
847 | 215 | 18 | 18.3 | 184.8 | 161 | 86.6
848 | 216 | 18.1 | 18.3 | 184.3 | 160.8 | 87
849 | 217 | 18.1 | 18.3 | 183.7 | 161 | 87.3
850 | 218 | 18.1 | 18.3 | 183.4 | 161.1 | 87.6
851 | 219 | 18.1 | 18.4 | 183.6 | 161.5 | 87.9
852 | 220 | 18.1 | 18.4 | 183.4 | 161.4 | 88
853 | 221 | 18.2 | 18.4 | 183.6 | 161.3 | 88.1
854 | 222 | 18.2 | 18.4 | 183.5 | 161 | 88.5
855 | 223 | 18.2 | 18.4 | 183.8 | 160.7 | 88.7
856 | 224 | 18.2 | 18.5 | 184.4 | 160.4 | 88.9
857 | 225 | 18.2 | 18.5 | 184.8 | 160.7 | 89.3
858 | 226 | 18.3 | 18.5 | 184.7 | 160.7 | 89.7
859 | 227 | 18.3 | 18.5 | 184.6 | 160.8 | 90
860 | 228 | 18.3 | 18.6 | 184.6 | 160.7 | 90.1
861 | 229 | 18.3 | 18.6 | 184.8 | 160.6 | 90.3
862 | 230 | 18.3 | 18.6 | 184.9 | 160.9 | 90.5
863 | 231 | 18.4 | 18.6 | 185 | 161.1 | 90.8
864 | 232 | 18.4 | 18.7 | 185.4 | 161 | 91.1
865 | 233 | 18.4 | 18.7 | 185.8 | 161.3 | 91.5
866 | 234 | 18.4 | 18.7 | 186 | 161.6 | 91.7
867 | 235 | 18.5 | 18.7 | 186.2 | 161.8 | 92.1
868 | 236 | 18.5 | 18.8 | 186.6 | 162 | 92.4
869 | 237 | 18.5 | 18.8 | 186.6 | 161.7 | 92.7
870 | 238 | 18.5 | 18.8 | 186.5 | 161.6 | 92.7
871 | 239 | 18.6 | 18.8 | 186.4 | 161.4 | 92.9
872 | 240 | 18.6 | 18.9 | 186.4 | 161.3 | 93.1
873 | 241 | 18.6 | 18.9 | 186.7 | 161.7 | 93.4
874 | 242 | 18.6 | 18.9 | 186.7 | 162.4 | 93.7
875 | 243 | 18.6 | 18.9 | 186.7 | 162.9 | 94
876 | 244 | 18.7 | 19 | 186.7 | 163.3 | 94.1
877 | 245 | 18.7 | 19 | 186.7 | 163.1 | 94.2
878 | 246 | 18.7 | 19 | 186.8 | 163.2 | 94.5
879 | 247 | 18.7 | 19.1 | 186.8 | 163 | 94.8
880 | 248 | 18.8 | 19.1 | 186.9 | 162.7 | 95
881 | 249 | 18.8 | 19.1 | 187.1 | 162.8 | 95.3
882 | 250 | 18.8 | 19.1 | 187.8 | 162.2 | 95.6
883 | 251 | 18.8 | 19.2 | 188 | 162.1 | 95.8
884 | 252 | 18.9 | 19.2 | 188.3 | 162.3 | 96.1
885 | 253 | 18.9 | 19.2 | 188.9 | 162.4 | 96.4
886 | 254 | 18.9 | 19.2 | 189 | 162.4 | 96.5
887 | 255 | 18.9 | 19.3 | 189.1 | 162.8 | 96.7
888 | 256 | 19 | 19.3 | 189.2 | 162.7 | 96.9
889 | 257 | 19 | 19.3 | 189.7 | 162.3 | 97.2
890 | 258 | 19 | 19.4 | 189.7 | 161.8 | 97.6
891 | 259 | 19.1 | 19.4 | 189.7 | 161.8 | 98
892 | 260 | 19.1 | 19.4 | 189.7 | 161.8 | 98
893 | 261 | 19.1 | 19.4 | 189.7 | 162.5 | 98.2
894 | 262 | 19.1 | 19.5 | 190 | 162.9 | 98.5
895 | 263 | 19.1 | 19.5 | 190.1 | 163.3 | 98.7
896 | 264 | 19.2 | 19.5 | 190.7 | 163.5 | 98.9
897 | 265 | 19.2 | 19.6 | 190.7 | 163.8 | 99.3
898 | 266 | 19.2 | 19.6 | 190.7 | 164.4 | 99.6
899 | 267 | 19.2 | 19.6 | 191 | 164.8 | 99.8
900 | 268 | 19.3 | 19.7 | 192.2 | 165 | 99.9
901 | 269 | 19.3 | 19.7 | 192.4 | 165.3 | 100.2
902 | 270 | 19.3 | 19.7 | 192.3 | 165.5 | 100.5
903 | 271 | 19.4 | 19.8 | 192.2 | 165.6 | 100.7
904 | 272 | 19.4 | 19.8 | 192.2 | 166 | 100.8
905 | 273 | 19.4 | 19.8 | 192.4 | 166.5 | 101
906 | 274 | 19.4 | 19.9 | 192.3 | 167 | 101.3
907 | 275 | 19.5 | 19.9 | 192.4 | 167.6 | 101.6
908 | 276 | 19.5 | 19.9 | 192.5 | 167.8 | 102.1
909 | 277 | 19.5 | 20 | 192.7 | 168 | 102.2
910 | 278 | 19.5 | 20 | 193.2 | 168 | 102.5
911 | 279 | 19.6 | 20 | 194.2 | 167.9 | 102.8
912 | 280 | 19.6 | 20 | 194.7 | 167.9 | 103
913 | 281 | 19.6 | 20.1 | 194.8 | 167.8 | 103.1
914 | 282 | 19.6 | 20.1 | 195.2 | 168 | 103.4
915 | 283 | 19.7 | 20.2 | 195.1 | 168.9 | 103.5
916 | 284 | 19.7 | 20.2 | 195.1 | 169.6 | 103.7
917 | 285 | 19.7 | 20.2 | 195.1 | 169.7 | 104.1
918 | 286 | 19.7 | 20.2 | 195.5 | 170 | 104.4
919 | 287 | 19.8 | 20.3 | 196.3 | 170.3 | 104.5
920 | 288 | 19.8 | 20.3 | 196.4 | 171.6 | 104.7
921 | 289 | 19.8 | 20.3 | 196.5 | 172.4 | 105.1
922 | 290 | 19.9 | 20.4 | 196.4 | 172.7 | 105.5
923 | 291 | 19.9 | 20.4 | 196.6 | 173 | 105.8
924 | 292 | 19.9 | 20.4 | 196.9 | 173.2 | 106
925 | 293 | 20 | 20.5 | 197.5 | 172.7 | 106.4
926 | 294 | 20 | 20.5 | 198.2 | 172.7 | 106.6
927 | 295 | 20 | 20.6 | 199 | 172.8 | 106.7
928 | 296 | 20 | 20.6 | 199.5 | 173.2 | 107
929 | 297 | 20.1 | 20.6 | 200.5 | 174 | 107.4
930 | 298 | 20.1 | 20.7 | 200.8 | 174.7 | 107.8
931 | 299 | 20.1 | 20.7 | 201.5 | 175.2 | 108.2
932 | 300 | 20.2 | 20.7 | 202.4 | 176.2 | 108.7
933 | 301 | 20.2 | 20.8 | 203.3 | 177.2 | 109.1
934 | 302 | 20.2 | 20.8 | 204.5 | 177.9 | 109.5
935 | 303 | 20.2 | 20.8 | 205.5 | 178.4 | 110
936 | 304 | 20.3 | 20.9 | 206.2 | 178.9 | 110.3
937 | 305 | 20.3 | 20.9 | 206.9 | 179.3 | 110.5
938 | 306 | 20.3 | 20.9 | 207.1 | 180.2 | 110.7
939 | 307 | 20.4 | 21 | 207.6 | 180.7 | 111
940 | 308 | 20.4 | 21 | 208.8 | 181 | 111.2
941 | 309 | 20.4 | 21.1 | 209.1 | 181.5 | 111.6
942 | 310 | 20.5 | 21.1 | 211 | 181.9 | 112.1
943 | 311 | 20.5 | 21.1 | 211.4 | 182.4 | 112.4
944 | 312 | 20.5 | 21.2 | 212.1 | 182.8 | 112.8
945 | 313 | 20.6 | 21.2 | 212.8 | 183.4 | 113.2
946 | 314 | 20.6 | 21.3 | 213.7 | 183.9 | 113.5
947 | 315 | 20.6 | 21.3 | 214.7 | 185.8 | 113.9
948 | 316 | 20.7 | 21.3 | 215.9 | 186.5 | 114
949 | 317 | 20.7 | 21.4 | 216.6 | 186.9 | 114.5
950 | 318 | 20.7 | 21.4 | 217.2 | 187.7 | 114.9
951 | 319 | 20.7 | 21.5 | 217.7 | 188.5 | 115.2
952 | 320 | 20.8 | 21.5 | 217.8 | 189.1 | 115.4
953 | 321 | 20.8 | 21.5 | 218.3 | 189.2 | 115.9
954 | 322 | 20.8 | 21.6 | 218.8 | 189.1 | 116.1
955 | 323 | 20.9 | 21.6 | 218.9 | 189.5 | 116.3
956 | 324 | 20.9 | 21.7 | 218.7 | 189.6 | 116.7
957 | 325 | 21 | 21.7 | 218.6 | 189.9 | 117
958 | 326 | 21 | 21.7 | 218.7 | 189.8 | 117.1
959 | 327 | 21 | 21.8 | 218.6 | 189.6 | 117.4
960 | 328 | 21 | 21.8 | 218.7 | 189.8 | 117.5
961 | 329 | 21.1 | 21.8 | 218.8 | 189.7 | 117.7
962 | 330 | 21.1 | 21.9 | 219.1 | 189.8 | 117.9
963 | 331 | 21.1 | 21.9 | 219.3 | 189.8 | 118.2
964 | 332 | 21.2 | 22 | 219.4 | 189.7 | 118.6
965 | 333 | 21.2 | 22 | 219.3 | 190.3 | 118.9
966 | 334 | 21.2 | 22.1 | 219.5 | 191.6 | 119.4
967 | 335 | 21.3 | 22.1 | 219.6 | 192.6 | 119.9
968 | 336 | 21.3 | 22.1 | 220 | 193.5 | 120.3
969 | 337 | 21.3 | 22.2 | 220.9 | 194.2 | 120.5
970 | 338 | 21.4 | 22.2 | 223 | 195.3 | 120.9
971 | 339 | 21.4 | 22.3 | 223.6 | 196.1 | 121.3
972 | 340 | 21.4 | 22.3 | 224.2 | 196.4 | 122
973 | 341 | 21.5 | 22.3 | 225 | 198 | 122.7
974 | 342 | 21.5 | 22.4 | 225.4 | 199.4 | 123
975 | 343 | 21.6 | 22.4 | 225.6 | 200.9 | 123.3
976 | 344 | 21.6 | 22.4 | 226 | 201.2 | 123.4
977 | 345 | 21.6 | 22.5 | 226.2 | 201.4 | 123.7
978 | 346 | 21.7 | 22.5 | 226.7 | 201.6 | 124
979 | 347 | 21.7 | 22.6 | 226.8 | 201.7 | 124.3
980 | 348 | 21.7 | 22.6 | 227.2 | 201.5 | 124.7
981 | 349 | 21.8 | 22.7 | 227.4 | 201.3 | 124.8
982 | 350 | 21.8 | 22.7 | 227.5 | 200.9 | 125.1
983 | 351 | 21.8 | 22.7 | 227.7 | 200.6 | 125.4
984 | 352 | 21.9 | 22.8 | 227.9 | 200.6 | 125.7
985 | 353 | 21.9 | 22.8 | 227.9 | 201 | 126
986 | 354 | 21.9 | 22.9 | 228.1 | 201 | 126.3
987 | 355 | 22 | 22.9 | 228.2 | 201.6 | 126.6
988 | 356 | 22 | 22.9 | 228.2 | 201.6 | 127
989 | 357 | 22.1 | 23 | 228.3 | 202 | 127.4
990 | 358 | 22.1 | 23 | 228.2 | 202 | 127.8
991 | 359 | 22.1 | 23.1 | 228.1 | 202.3 | 128
992 | 360 | 22.2 | 23.1 | 228.1 | 202.4 | 128.2
993 | 361 | 22.2 | 23.1 | 228 | 202.6 | 128.5
994 | 362 | 22.2 | 23.2 | 227.7 | 202.7 | 128.8
995 | 363 | 22.3 | 23.2 | 227.6 | 202.3 | 129
996 | 364 | 22.3 | 23.3 | 227.9 | 202.6 | 129.5
997 | 365 | 22.3 | 23.3 | 228.2 | 202.8 | 129.9
998 | 366 | 22.4 | 23.4 | 228.3 | 203.1 | 130.3
999 | 367 | 22.4 | 23.4 | 228.6 | 203.7 | 130.6
1000 | 368 | 22.4 | 23.4 | 228.3 | 205.2 | 130.8
1001 | 369 | 22.5 | 23.5 | 228.2 | 207.1 | 131.2
1002 | 370 | 22.5 | 23.5 | 228.3 | 209 | 131.7
1003 | 371 | 22.6 | 23.6 | 229 | 210.1 | 132.1
1004 | 372 | 22.6 | 23.6 | 229.8 | 210.4 | 132.5
1005 | 373 | 22.6 | 23.6 | 230.5 | 211.4 | 132.8
1006 | 374 | 22.7 | 23.7 | 231.2 | 212 | 133.3
1007 | 375 | 22.7 | 23.7 | 231.8 | 211.9 | 133.6
1008 | 376 | 22.8 | 23.8 | 232.8 | 212.1 | 134.2
1009 | 377 | 22.8 | 23.8 | 234.5 | 212.7 | 134.6
1010 | 378 | 22.8 | 23.8 | 235.5 | 214.4 | 134.8
1011 | 379 | 22.9 | 23.9 | 236.1 | 216.4 | 135.2
1012 | 380 | 22.9 | 23.9 | 237.6 | 217.2 | 135.7
1013 | 381 | 23 | 24 | 238 | 217.9 | 136.2
1014 | 382 | 23 | 24 | 238.2 | 219 | 136.5
1015 | 383 | 23 | 24.1 | 238.9 | 221.4 | 136.7
1016 | 384 | 23.1 | 24.1 | 240.1 | 221.4 | 137.3
1017 | 385 | 23.1 | 24.2 | 241 | 221.6 | 137.8
1018 | 386 | 23.2 | 24.2 | 241.7 | 221.6 | 138.4
1019 | 387 | 23.2 | 24.2 | 241.9 | 222.3 | 138.7
1020 | 388 | 23.3 | 24.3 | 241.8 | 221.7 | 138.8
1021 | 389 | 23.3 | 24.3 | 242.1 | 221 | 139
1022 | 390 | 23.3 | 24.4 | 242.4 | 220.7 | 139.4
1023 | 391 | 23.4 | 24.4 | 242.9 | 220.4 | 139.6
1024 | 392 | 23.4 | 24.5 | 243.2 | 220.3 | 139.9
1025 | 393 | 23.4 | 24.5 | 243.3 | 220.2 | 140.1
1026 | 394 | 23.5 | 24.6 | 244 | 219.7 | 140.6
1027 | 395 | 23.5 | 24.6 | 243.9 | 219.6 | 140.9
1028 | 396 | 23.6 | 24.6 | 244.2 | 219.2 | 141.2
1029 | 397 | 23.6 | 24.7 | 244.7 | 219.7 | 141.6
1030 | 398 | 23.7 | 24.7 | 244.8 | 220.5 | 142.1
1031 | 399 | 23.7 | 24.8 | 244.7 | 221 | 142.4
1032 | 400 | 23.7 | 24.8 | 244.7 | 221.4 | 142.5
1033 | 401 | 23.8 | 24.9 | 244.6 | 221.5 | 142.6
1034 | 402 | 23.8 | 24.9 | 244.9 | 221.8 | 142.9
1035 | 403 | 23.9 | 25 | 245.2 | 222.6 | 143.2
1036 | 404 | 23.9 | 25 | 245.6 | 222.7 | 143.6
1037 | 405 | 23.9 | 25.1 | 245.7 | 223.6 | 144
1038 | 406 | 24 | 25.1 | 246.6 | 224.5 | 144.5
1039 | 407 | 24 | 25.2 | 247.1 | 224.4 | 144.7
1040 | 408 | 24.1 | 25.2 | 247.2 | 224.3 | 144.9
1041 | 409 | 24.1 | 25.3 | 246.9 | 224.5 | 145.2
1042 | 410 | 24.2 | 25.3 | 246.7 | 224.4 | 145.6
1043 | 411 | 24.2 | 25.4 | 246.5 | 224 | 145.8
1044 | 412 | 24.3 | 25.4 | 246.2 | 223.8 | 146
1045 | 413 | 24.3 | 25.4 | 246 | 224.2 | 146.3
1046 | 414 | 24.3 | 25.5 | 246.1 | 224.6 | 146.7
1047 | 415 | 24.4 | 25.5 | 246.4 | 224.2 | 146.9
1048 | 416 | 24.4 | 25.6 | 246.5 | 224.6 | 147.2
1049 | 417 | 24.5 | 25.6 | 247.4 | 224.9 | 147.5
1050 | 418 | 24.5 | 25.7 | 247.7 | 225.1 | 147.9
1051 | 419 | 24.6 | 25.7 | 248.1 | 225 | 148.3
1052 | 420 | 24.6 | 25.8 | 248.4 | 224.9 | 148.7
1053 | 421 | 24.7 | 25.8 | 248.5 | 224.6 | 149.1
1054 | 422 | 24.7 | 25.9 | 248.8 | 224.3 | 149.2
1055 | 423 | 24.7 | 25.9 | 249.2 | 224.7 | 149.5
1056 | 424 | 24.8 | 26 | 249.6 | 225.9 | 149.7
1057 | 425 | 24.8 | 26 | 249.8 | 226.8 | 150.2
1058 | 426 | 24.9 | 26.1 | 250.1 | 227.9 | 150.7
1059 | 427 | 24.9 | 26.1 | 250.2 | 228.6 | 151.2
1060 | 428 | 25 | 26.2 | 249.9 | 229.4 | 151.6
1061 | 429 | 25 | 26.2 | 250 | 230.5 | 152
1062 | 430 | 25 | 26.3 | 250 | 230.8 | 152.3
1063 | 431 | 25.1 | 26.3 | 249.7 | 230.4 | 152.5
1064 | 432 | 25.2 | 26.4 | 250.4 | 230.2 | 152.7
1065 | 433 | 25.2 | 26.4 | 250.5 | 229.6 | 153.1
1066 | 434 | 25.2 | 26.5 | 251 | 229.4 | 153.4
1067 | 435 | 25.3 | 26.5 | 251.1 | 228.4 | 153.6
1068 | 436 | 25.3 | 26.6 | 251.2 | 227.8 | 153.8
1069 | 437 | 25.4 | 26.6 | 250.9 | 227.2 | 154.1
1070 | 438 | 25.4 | 26.7 | 251.2 | 227.1 | 154.3
1071 | 439 | 25.5 | 26.7 | 251.6 | 226.8 | 154.7
1072 | 440 | 25.5 | 26.8 | 251.7 | 226.7 | 155
1073 | 441 | 25.6 | 26.8 | 251.5 | 227.4 | 155.2
1074 | 442 | 25.6 | 26.9 | 252.5 | 228.1 | 155.6
1075 | 443 | 25.7 | 26.9 | 252.7 | 228.6 | 155.9
1076 | 444 | 25.7 | 27 | 253.1 | 229.2 | 156.3
1077 | 445 | 25.8 | 27 | 253.2 | 229.6 | 157
1078 | 446 | 25.8 | 27.1 | 252.9 | 230.2 | 157.4
1079 | 447 | 25.9 | 27.1 | 252.6 | 230.3 | 157.7
1080 | 448 | 25.9 | 27.2 | 252.2 | 231.3 | 157.9
1081 | 449 | 25.9 | 27.2 | 252.2 | 231.4 | 158.3
1082 | 450 | 26 | 27.3 | 252 | 231.7 | 158.4
1083 | 451 | 26 | 27.3 | 251.5 | 231.6 | 158.8
1084 | 452 | 26.1 | 27.4 | 251 | 231.3 | 159.1
1085 | 453 | 26.1 | 27.5 | 250.9 | 230.8 | 159.6
1086 | 454 | 26.2 | 27.5 | 251.1 | 230.7 | 159.9
1087 | 455 | 26.3 | 27.5 | 251.3 | 230.9 | 160.2
1088 | 456 | 26.3 | 27.6 | 251.2 | 231.2 | 160.5
1089 | 457 | 26.3 | 27.7 | 251.7 | 232.5 | 161.1
1090 | 458 | 26.4 | 27.7 | 253 | 235.6 | 161.8
1091 | 459 | 26.4 | 27.8 | 253.4 | 236.8 | 162.5
1092 | 460 | 26.5 | 27.8 | 253.9 | 238 | 162.9
1093 | 461 | 26.5 | 27.8 | 254.5 | 238.9 | 163.3
1094 | 462 | 26.6 | 27.9 | 255.3 | 240 | 163.8
1095 | 463 | 26.6 | 27.9 | 255.8 | 241.3 | 164.5
1096 | 464 | 26.7 | 28 | 256.1 | 242.7 | 164.8
1097 | 465 | 26.7 | 28 | 256.3 | 244 | 165.5
1098 | 466 | 26.8 | 28.1 | 255.9 | 244 | 165.8
1099 | 467 | 26.8 | 28.1 | 255.7 | 244.2 | 166
1100.1 | 468.1 | 26.9 | 28.2 | 255.3 | 244.5 | 166.3
1101.1 | 469.1 | 26.9 | 28.2 | 255.3 | 245.2 | 166.7
1102.1 | 470.1 | 27 | 28.3 | 255.3 | 244.8 | 166.9
1103.1 | 471.1 | 27 | 28.3 | 255.7 | 244.3 | 167.1
1104.1 | 472.1 | 27.1 | 28.4 | 256.3 | 243.7 | 167.4
1105.1 | 473.1 | 27.2 | 28.4 | 256.6 | 243.4 | 167.5
1106.1 | 474.1 | 27.2 | 28.5 | 257 | 243.8 | 167.8
1107.1 | 475.1 | 27.2 | 28.5 | 256.7 | 243.3 | 168.1
1108.1 | 476.1 | 27.3 | 28.6 | 256.7 | 242 | 168.2
1109.1 | 477.1 | 27.3 | 28.6 | 256.4 | 241.6 | 168.3
1110.1 | 478.1 | 27.4 | 28.7 | 255.8 | 241.5 | 168.5
1111.1 | 479.1 | 27.4 | 28.7 | 255.8 | 241.1 | 168.8
1112.1 | 480.1 | 27.5 | 28.8 | 255.7 | 240.2 | 169
1113.1 | 481.1 | 27.6 | 28.8 | 255.5 | 239.3 | 169.2
1114.1 | 482.1 | 27.6 | 28.9 | 255.4 | 238.9 | 169.4
1115.1 | 483.1 | 27.7 | 28.9 | 256 | 239.6 | 169.6
1116.1 | 484.1 | 27.7 | 29 | 257 | 240.7 | 170
1117.1 | 485.1 | 27.7 | 29.1 | 258.2 | 241.3 | 170.5
1118.1 | 486.1 | 27.8 | 29.1 | 258.9 | 242.9 | 171.1
1119.1 | 487.1 | 27.9 | 29.2 | 259.6 | 243.7 | 171.5
1120.1 | 488.1 | 27.9 | 29.2 | 259.8 | 245.3 | 171.9
1121.1 | 489.1 | 28 | 29.3 | 260.2 | 246.4 | 172.2
1122.1 | 490.1 | 28 | 29.3 | 260.6 | 246.9 | 172.5
1123.1 | 491.1 | 28.1 | 29.4 | 260.6 | 247.1 | 172.6
1124.1 | 492.1 | 28.1 | 29.4 | 260.9 | 247.9 | 172.8
1125.1 | 493.1 | 28.2 | 29.5 | 260.8 | 248.6 | 173.1
1126.1 | 494.1 | 28.3 | 29.5 | 260.7 | 248.9 | 173.5
1127.1 | 495.1 | 28.3 | 29.6 | 260.7 | 248.6 | 173.6
1128.1 | 496.1 | 28.3 | 29.7 | 260.3 | 248.5 | 173.7
1129.1 | 497.1 | 28.4 | 29.7 | 259.9 | 248.6 | 173.8
1130.1 | 498.1 | 28.5 | 29.8 | 259.8 | 248.9 | 174
1131.1 | 499.1 | 28.5 | 29.8 | 259.6 | 249.3 | 174.2
1132.1 | 500.1 | 28.6 | 29.9 | 259.6 | 249.9 | 174.4
1133.1 | 501.1 | 28.6 | 29.9 | 259.8 | 250.4 | 175
1134.1 | 502.1 | 28.7 | 30 | 260.3 | 251.1 | 175.2
1135.1 | 503.1 | 28.7 | 30 | 260.2 | 251.2 | 175.7
1136.1 | 504.1 | 28.8 | 30.1 | 260.3 | 250.5 | 176
1137.1 | 505.1 | 28.8 | 30.2 | 260.3 | 249.7 | 176.1
1138.1 | 506.1 | 28.9 | 30.2 | 259.9 | 249.5 | 176.2
1139.1 | 507.1 | 29 | 30.3 | 259.8 | 249.5 | 176.4
1140.1 | 508.1 | 29 | 30.3 | 259.9 | 250.1 | 176.8
1141.1 | 509.1 | 29.1 | 30.4 | 260.4 | 250.7 | 177.4
1142.1 | 510.1 | 29.1 | 30.4 | 260.5 | 251.3 | 177.9
1143.1 | 511.1 | 29.2 | 30.5 | 260.8 | 251.9 | 178.6
1144.1 | 512.1 | 29.2 | 30.5 | 261 | 252.9 | 179.1
1145.1 | 513.1 | 29.3 | 30.6 | 261.2 | 253.5 | 179.6
1146.1 | 514.1 | 29.4 | 30.6 | 261.4 | 253.7 | 179.8
1147.1 | 515.1 | 29.4 | 30.7 | 262 | 253.6 | 180
1148.1 | 516.1 | 29.5 | 30.7 | 261.9 | 253.8 | 180.3
1149.1 | 517.1 | 29.5 | 30.8 | 261.4 | 253.8 | 180.7
1150.1 | 518.1 | 29.6 | 30.8 | 261.3 | 253.2 | 180.9
1151.1 | 519.1 | 29.6 | 30.9 | 261 | 252.1 | 180.9
1152.1 | 520.1 | 29.7 | 30.9 | 260.8 | 251.1 | 180.9
1153.1 | 521.1 | 29.7 | 31 | 260.5 | 250.3 | 181
1154.1 | 522.1 | 29.8 | 31 | 260 | 250.2 | 181.1
1155.1 | 523.1 | 29.9 | 31.1 | 259.6 | 249.4 | 181.3
1156.1 | 524.1 | 29.9 | 31.2 | 260 | 249 | 181.4
1157.1 | 525.1 | 30 | 31.2 | 260.4 | 247.8 | 181.7
1158.1 | 526.1 | 30 | 31.3 | 260.6 | 247.1 | 181.9
1159.1 | 527.1 | 30.1 | 31.3 | 260.7 | 246.7 | 182
1160.1 | 528.1 | 30.2 | 31.4 | 260.8 | 246.1 | 182.1
1161.1 | 529.1 | 30.2 | 31.4 | 261 | 245.6 | 182.2
1162.1 | 530.1 | 30.3 | 31.5 | 260.9 | 245 | 182.4
1163.1 | 531.1 | 30.3 | 31.5 | 260.6 | 244.6 | 182.7
1164.1 | 532.1 | 30.4 | 31.6 | 260.5 | 244.1 | 182.9
1165.1 | 533.1 | 30.5 | 31.7 | 260.4 | 243.4 | 182.9
1166.1 | 534.1 | 30.5 | 31.7 | 260.4 | 242.7 | 183.1
1167.1 | 535.1 | 30.6 | 31.8 | 260.7 | 242.7 | 183.2
1168.1 | 536.1 | 30.6 | 31.8 | 260.7 | 243.3 | 183.4
1169.1 | 537.1 | 30.7 | 31.9 | 260.3 | 243.9 | 183.6
1170.1 | 538.1 | 30.8 | 31.9 | 260.9 | 244.4 | 184.2
1171.1 | 539.1 | 30.8 | 32 | 260.8 | 244.7 | 184.6
1172.1 | 540.1 | 30.9 | 32 | 260.9 | 244.6 | 184.7
1173.1 | 541.1 | 30.9 | 32.1 | 261.2 | 244.5 | 184.8
1174.1 | 542.1 | 31 | 32.1 | 261.6 | 244.2 | 185
1175.1 | 543.1 | 31.1 | 32.2 | 262 | 244.1 | 185.1
1176.1 | 544.1 | 31.1 | 32.2 | 262.4 | 244.1 | 185.3
1177.1 | 545.1 | 31.2 | 32.3 | 262.6 | 244.6 | 185.9
1178.1 | 546.1 | 31.2 | 32.4 | 262.8 | 244.9 | 186.1
1179.1 | 547.1 | 31.3 | 32.4 | 262.7 | 245 | 186.4
1180.1 | 548.1 | 31.4 | 32.5 | 262.6 | 245.3 | 186.5
1181.1 | 549.1 | 31.4 | 32.5 | 262.8 | 245.6 | 186.7
1182.1 | 550.1 | 31.5 | 32.6 | 263.1 | 246.2 | 187.1
1183.1 | 551.1 | 31.5 | 32.6 | 263.4 | 247.3 | 187.4
1184.1 | 552.1 | 31.6 | 32.7 | 263.6 | 247.9 | 187.8
1185.1 | 553.1 | 31.7 | 32.7 | 263.6 | 248.7 | 188.2
1186.1 | 554.1 | 31.7 | 32.8 | 263.5 | 249.6 | 188.6
1187.1 | 555.1 | 31.8 | 32.9 | 263.4 | 249.7 | 188.8
1188.1 | 556.1 | 31.9 | 32.9 | 263.4 | 249.8 | 189
1189.1 | 557.1 | 31.9 | 33 | 263.3 | 249.7 | 189.2
1190.1 | 558.1 | 32 | 33 | 263.1 | 249.2 | 189.3
1191.1 | 559.1 | 32 | 33.1 | 262.6 | 248.4 | 189.4
1192.1 | 560.1 | 32.1 | 33.1 | 262 | 247.6 | 189.6
1193.1 | 561.1 | 32.2 | 33.2 | 261.7 | 246.6 | 190
1194.1 | 562.1 | 32.2 | 33.2 | 261.9 | 245.9 | 190.1
1195.1 | 563.1 | 32.3 | 33.3 | 261.9 | 245.2 | 190.2
1196.1 | 564.1 | 32.4 | 33.4 | 261.6 | 244.4 | 190.2
1197.1 | 565.1 | 32.4 | 33.4 | 261.5 | 243.9 | 190.4
1198.1 | 566.1 | 32.5 | 33.5 | 261.4 | 243.8 | 190.5
1199.1 | 567.1 | 32.5 | 33.5 | 261.1 | 243.4 | 190.6
1200.1 | 568.1 | 32.6 | 33.6 | 261.2 | 242.9 | 190.7
1201.1 | 569.1 | 32.7 | 33.6 | 261.6 | 242.6 | 190.8
1202.1 | 570.1 | 32.7 | 33.7 | 261.7 | 242.3 | 191.1
1203.1 | 571.1 | 32.8 | 33.8 | 261.5 | 242 | 191.3
1204.1 | 572.1 | 32.9 | 33.8 | 261.6 | 241.8 | 191.5
1205.1 | 573.1 | 32.9 | 33.9 | 261.5 | 241.8 | 191.6
1206.1 | 574.1 | 33 | 33.9 | 262.2 | 242.2 | 191.8
1207.1 | 575.1 | 33.1 | 34 | 262.6 | 242.8 | 192.1
1208.1 | 576.1 | 33.1 | 34 | 262.8 | 243.6 | 192.4
1209.1 | 577.1 | 33.2 | 34.1 | 262.7 | 243.8 | 192.9
1210.1 | 578.1 | 33.3 | 34.1 | 262.9 | 244.1 | 193
1211.1 | 579.1 | 33.3 | 34.2 | 262.9 | 244.5 | 193.2
1212.1 | 580.1 | 33.4 | 34.3 | 263.4 | 245.2 | 193.6
1213.1 | 581.1 | 33.4 | 34.3 | 264.3 | 246 | 193.8
1214.1 | 582.1 | 33.5 | 34.4 | 265.3 | 246.4 | 193.9
1215.1 | 583.1 | 33.6 | 34.4 | 266 | 246.3 | 194.1
1216.1 | 584.1 | 33.6 | 34.5 | 266.5 | 246.2 | 194.3
1217.1 | 585.1 | 33.7 | 34.6 | 267.1 | 246.7 | 194.3
1218.1 | 586.1 | 33.8 | 34.6 | 267.7 | 246.5 | 194.4
1219.1 | 587.1 | 33.8 | 34.7 | 267.5 | 246.4 | 194.6
1220.1 | 588.1 | 33.9 | 34.7 | 267.4 | 246.7 | 194.8
1221.1 | 589.1 | 34 | 34.8 | 267.3 | 246.7 | 194.9
1222.1 | 590.1 | 34 | 34.9 | 266.8 | 246.3 | 195.1
1223.1 | 591.1 | 34.1 | 34.9 | 266.8 | 246.2 | 195.2
1224.1 | 592.1 | 34.2 | 35 | 266.9 | 246.2 | 195.3
1225.1 | 593.1 | 34.2 | 35 | 266.8 | 246 | 195.4
1226.1 | 594.1 | 34.3 | 35.1 | 267 | 246.7 | 195.5
1227.1 | 595.1 | 34.4 | 35.2 | 266.7 | 247.5 | 195.7
1228.1 | 596.1 | 34.4 | 35.2 | 266.9 | 247.2 | 195.9
1229.1 | 597.1 | 34.5 | 35.3 | 266.8 | 246.3 | 195.8
1230.1 | 598.1 | 34.6 | 35.3 | 266.6 | 246.2 | 195.8
1231.1 | 599.1 | 34.6 | 35.4 | 266.3 | 246.4 | 195.9
1232.1 | 600.1 | 34.7 | 35.5 | 266.3 | 246.4 | 196.2
1233.1 | 601.1 | 34.8 | 35.5 | 266.4 | 246.4 | 196.5
1234.1 | 602.1 | 34.8 | 35.6 | 266.3 | 246.6 | 196.8
1235.1 | 603.1 | 34.9 | 35.6 | 266 | 247.1 | 196.9
1236.1 | 604.1 | 35 | 35.7 | 265.7 | 247.1 | 197.2
1237.1 | 605.1 | 35 | 35.8 | 266.1 | 247.6 | 197.4
1238.1 | 606.1 | 35.1 | 35.8 | 267.4 | 248 | 197.7
1239.1 | 607.1 | 35.2 | 35.9 | 269 | 248.4 | 197.8
1240.1 | 608.1 | 35.3 | 36 | 270.2 | 248.9 | 198.1
1241.1 | 609.1 | 35.3 | 36 | 271.6 | 249.8 | 198.3
1242.1 | 610.1 | 35.4 | 36.1 | 273.1 | 251.8 | 198.6
1243.1 | 611.1 | 35.4 | 36.2 | 274 | 254.6 | 199.2
1244.1 | 612.1 | 35.5 | 36.2 | 275.2 | 256.8 | 200
1245.1 | 613.1 | 35.6 | 36.3 | 276.5 | 258.1 | 200.5
1246.1 | 614.1 | 35.7 | 36.3 | 276.9 | 258.8 | 200.9
1247.1 | 615.1 | 35.7 | 36.4 | 277 | 259.5 | 201
1248.1 | 616.1 | 35.8 | 36.5 | 277.1 | 260.3 | 201.3
1249.1 | 617.1 | 35.8 | 36.5 | 277.4 | 261.3 | 201.7
1250.1 | 618.1 | 35.9 | 36.6 | 277.2 | 261.9 | 202.1
1251.1 | 619.1 | 36 | 36.6 | 276.8 | 262.2 | 202.5
1252.1 | 620.1 | 36.1 | 36.7 | 276.5 | 262.2 | 202.7
1253.1 | 621.1 | 36.1 | 36.8 | 276 | 261.9 | 203
1254.1 | 622.1 | 36.2 | 36.8 | 275.6 | 261.5 | 203.1
1255.1 | 623.1 | 36.3 | 36.9 | 275.3 | 261.7 | 203.3
1256.1 | 624.1 | 36.3 | 37 | 275.1 | 261.2 | 203.4
1257.1 | 625.1 | 36.4 | 37 | 274.9 | 260.8 | 203.4
1258.1 | 626.1 | 36.5 | 37.1 | 274.8 | 260.4 | 203.6
1259.1 | 627.1 | 36.6 | 37.2 | 274.7 | 259.8 | 203.8
1260.1 | 628.1 | 36.6 | 37.2 | 274.3 | 259.5 | 203.9
1261.1 | 629.1 | 36.7 | 37.3 | 273.9 | 258.7 | 203.9
1262.1 | 630.1 | 36.8 | 37.3 | 273.5 | 258.1 | 203.9
1263.1 | 631.1 | 36.8 | 37.4 | 273.4 | 257.1 | 203.9
1264.1 | 632.1 | 36.9 | 37.5 | 273.1 | 256.2 | 203.9
1265.1 | 633.1 | 37 | 37.5 | 273 | 255.7 | 204.1
1266.1 | 634.1 | 37 | 37.6 | 273.1 | 256.4 | 204.5
1267.1 | 635.1 | 37.1 | 37.6 | 273.1 | 257 | 204.8
1268.1 | 636.1 | 37.2 | 37.7 | 272.5 | 257.3 | 205.2
1269.1 | 637.1 | 37.2 | 37.8 | 272.9 | 257.6 | 205.3
1270.1 | 638.1 | 37.3 | 37.8 | 273.2 | 257.9 | 205.7
1271.1 | 639.1 | 37.4 | 37.9 | 273.5 | 258.7 | 206.1
1272.1 | 640.1 | 37.4 | 37.9 | 273.8 | 259.7 | 206.3
1273.1 | 641.1 | 37.5 | 38 | 273.8 | 259.7 | 206.5
1274.1 | 642.1 | 37.6 | 38.1 | 274.2 | 260.1 | 206.8
1275.1 | 643.1 | 37.6 | 38.1 | 274.7 | 260.4 | 207.1
1276.1 | 644.1 | 37.7 | 38.2 | 275.3 | 260.6 | 207.2
1277.1 | 645.1 | 37.8 | 38.3 | 275.6 | 261.9 | 207.6
1278.1 | 646.1 | 37.9 | 38.3 | 275.7 | 262.5 | 208
1279.1 | 647.1 | 37.9 | 38.4 | 275.7 | 262.8 | 208.2
1280.1 | 648.1 | 38 | 38.4 | 276 | 263.2 | 208.3
1281.1 | 649.1 | 38.1 | 38.5 | 276.1 | 263.5 | 208.5
1282.1 | 650.1 | 38.1 | 38.6 | 276 | 263.4 | 208.7
1283.1 | 651.1 | 38.2 | 38.6 | 275.8 | 263.2 | 208.7
1284.1 | 652.1 | 38.3 | 38.7 | 276.9 | 263 | 208.9
1285.1 | 653.1 | 38.3 | 38.8 | 276.9 | 263.2 | 209.2
1286.1 | 654.1 | 38.4 | 38.8 | 276.5 | 262.9 | 209.2
1287.1 | 655.1 | 38.5 | 38.9 | 276.4 | 262.4 | 209.3
1288.1 | 656.1 | 38.6 | 38.9 | 276.7 | 261.8 | 209.5
1289.1 | 657.1 | 38.6 | 39 | 277 | 261.9 | 209.7
1290.1 | 658.1 | 38.7 | 39 | 277.8 | 262.6 | 210
1291.1 | 659.1 | 38.8 | 39.1 | 279.1 | 263.2 | 210.2
1292.1 | 660.1 | 38.8 | 39.2 | 278.8 | 263.8 | 210.5
1293.1 | 661.1 | 38.9 | 39.3 | 279.1 | 264.8 | 211
1294.1 | 662.1 | 39 | 39.3 | 280.2 | 266.1 | 211.6
1295.1 | 663.1 | 39.1 | 39.4 | 280.5 | 266.5 | 211.9
1296.1 | 664.1 | 39.1 | 39.4 | 280.8 | 266.8 | 212.2
1297.1 | 665.1 | 39.2 | 39.5 | 280.3 | 266.9 | 212.3
1298.1 | 666.1 | 39.3 | 39.6 | 280.1 | 266.8 | 212.5
1299.1 | 667.1 | 39.3 | 39.6 | 279.8 | 266.8 | 212.8
1300.1 | 668.1 | 39.4 | 39.7 | 279.8 | 267.5 | 213
1301.1 | 669.1 | 39.5 | 39.8 | 279.9 | 267.6 | 213.2
1302.1 | 670.1 | 39.6 | 39.8 | 279.8 | 267.9 | 213.4
1303.1 | 671.1 | 39.6 | 39.9 | 280.5 | 268.1 | 213.7
1304.1 | 672.1 | 39.7 | 40 | 280.9 | 268.9 | 214.1
1305.1 | 673.1 | 39.8 | 40 | 281.7 | 269.7 | 214.6
1306.1 | 674.1 | 39.9 | 40.1 | 282.4 | 269.5 | 214.9
1307.1 | 675.1 | 39.9 | 40.1 | 283.4 | 269.6 | 215.2
1308.1 | 676.1 | 40 | 40.2 | 283.9 | 269.8 | 215.4
1309.1 | 677.1 | 40.1 | 40.3 | 284.1 | 269.7 | 215.7
1310.1 | 678.1 | 40.1 | 40.3 | 284.1 | 269.7 | 216
1311.1 | 679.1 | 40.2 | 40.4 | 284.1 | 270.2 | 216.3
1312.1 | 680.1 | 40.3 | 40.5 | 284.2 | 270.1 | 216.4
1313.1 | 681.1 | 40.4 | 40.5 | 284.7 | 269.9 | 216.6
1314.1 | 682.1 | 40.4 | 40.6 | 285.6 | 270.1 | 216.9
1315.1 | 683.1 | 40.5 | 40.7 | 286.7 | 270.4 | 217.2
1316.1 | 684.1 | 40.6 | 40.7 | 287.6 | 270.9 | 217.4
1317.1 | 685.1 | 40.7 | 40.8 | 288.6 | 272.3 | 217.6
1318.1 | 686.1 | 40.7 | 40.8 | 289.3 | 272.9 | 217.9
1319.1 | 687.1 | 40.8 | 40.9 | 290.1 | 273.9 | 218.5
1320.1 | 688.1 | 40.9 | 41 | 291 | 275 | 218.9
1321.1 | 689.1 | 41 | 41 | 291.7 | 276 | 219.3
1322.1 | 690.1 | 41 | 41.1 | 292 | 276.9 | 219.7
1323.1 | 691.1 | 41.1 | 41.2 | 292.1 | 277.6 | 220.1
1324.1 | 692.1 | 41.2 | 41.2 | 291.8 | 277.6 | 220.4
1325.1 | 693.1 | 41.2 | 41.3 | 291.5 | 277.6 | 220.8
1326.1 | 694.1 | 41.3 | 41.4 | 291.3 | 276.9 | 221
1327.1 | 695.1 | 41.4 | 41.4 | 291.8 | 276.5 | 221.1
1328.1 | 696.1 | 41.5 | 41.5 | 291.8 | 276 | 221.2
1329.1 | 697.1 | 41.5 | 41.5 | 292.2 | 275.8 | 221.3
1330.1 | 698.1 | 41.6 | 41.6 | 292.6 | 275.4 | 221.3
1331.1 | 699.1 | 41.7 | 41.7 | 292.8 | 274.9 | 221.3
1332.1 | 700.1 | 41.8 | 41.7 | 293.3 | 274.5 | 221.3
1333.1 | 701.1 | 41.8 | 41.8 | 293.8 | 275.5 | 221.5
1334.1 | 702.1 | 41.9 | 41.9 | 294.2 | 276.7 | 221.8
1335.1 | 703.1 | 42 | 41.9 | 294.1 | 277.2 | 222
1336.1 | 704.1 | 42 | 42 | 294.1 | 277.7 | 222.2
1337.1 | 705.1 | 42.1 | 42.1 | 294.3 | 278.1 | 222.4
1338.1 | 706.1 | 42.2 | 42.1 | 293.9 | 278 | 222.6
1339.1 | 707.1 | 42.3 | 42.2 | 293.7 | 277.4 | 222.7
1340.1 | 708.1 | 42.4 | 42.3 | 293.6 | 276.5 | 222.7
1341.1 | 709.1 | 42.4 | 42.3 | 293.4 | 275.9 | 222.7
1342.1 | 710.1 | 42.5 | 42.4 | 293.8 | 275.9 | 222.9
1343.1 | 711.1 | 42.6 | 42.5 | 294.4 | 276 | 223.3
1344.1 | 712.1 | 42.6 | 42.5 | 294.9 | 275.9 | 223.3
1345.1 | 713.1 | 42.7 | 42.6 | 295.7 | 276.1 | 223.5
1346.1 | 714.1 | 42.8 | 42.7 | 297.3 | 277.2 | 223.7
1347.1 | 715.1 | 42.9 | 42.7 | 298.2 | 278.4 | 224
1348.1 | 716.1 | 42.9 | 42.8 | 298.8 | 279.6 | 224.2
1349.1 | 717.1 | 43 | 42.9 | 299.2 | 280.7 | 224.5
1350.1 | 718.1 | 43.1 | 42.9 | 299.7 | 281 | 224.6
1351.1 | 719.1 | 43.2 | 43 | 300.2 | 280.8 | 224.9
1352.1 | 720.1 | 43.2 | 43.1 | 300.2 | 281.1 | 224.9
1353.1 | 721.1 | 43.3 | 43.1 | 300.1 | 281.7 | 225
1354.1 | 722.1 | 43.4 | 43.2 | 299.9 | 282.3 | 225.3
1355.1 | 723.1 | 43.5 | 43.3 | 299.9 | 282.1 | 225.3
1356.1 | 724.1 | 43.5 | 43.3 | 299.6 | 282.1 | 225.3
1357.1 | 725.1 | 43.6 | 43.4 | 299.5 | 282.7 | 225.4
1358.1 | 726.1 | 43.7 | 43.5 | 299.7 | 283.6 | 225.7
1359.1 | 727.1 | 43.8 | 43.5 | 299.8 | 283.7 | 226.1
1360.1 | 728.1 | 43.8 | 43.6 | 300.8 | 284.9 | 226.4
1361.1 | 729.1 | 43.9 | 43.7 | 302 | 286.3 | 226.9
1362.1 | 730.1 | 44 | 43.7 | 302.7 | 287.6 | 227.4
1363.1 | 731.1 | 44.1 | 43.8 | 303 | 288.6 | 227.9
1364.1 | 732.1 | 44.2 | 43.9 | 303 | 289.3 | 228.1
1365.1 | 733.1 | 44.2 | 43.9 | 303.3 | 289.8 | 228.5
1366.1 | 734.1 | 44.3 | 44 | 303.5 | 290.8 | 228.7
1367.1 | 735.1 | 44.4 | 44.1 | 303.7 | 291.3 | 228.9
1368.1 | 736.1 | 44.5 | 44.2 | 304.1 | 291.9 | 229.1
1369.1 | 737.1 | 44.5 | 44.2 | 305.2 | 292.6 | 229.4
1370.1 | 738.1 | 44.6 | 44.3 | 306.1 | 293.2 | 229.7
1371.1 | 739.1 | 44.7 | 44.4 | 307.2 | 293.8 | 230.2
1372.1 | 740.1 | 44.8 | 44.4 | 308.1 | 294.5 | 230.6
1373.1 | 741.1 | 44.8 | 44.5 | 308.7 | 295.2 | 230.6
1374.1 | 742.1 | 44.9 | 44.6 | 309 | 295.3 | 230.9
1375.1 | 743.1 | 45 | 44.7 | 308.9 | 295.1 | 231.2
1376.1 | 744.1 | 45.1 | 44.7 | 309.3 | 295.2 | 231.4
1377.1 | 745.1 | 45.2 | 44.8 | 309.8 | 295.8 | 231.6
1378.1 | 746.1 | 45.2 | 44.9 | 310.4 | 297.1 | 231.7
1379.1 | 747.1 | 45.3 | 44.9 | 311.2 | 298.2 | 232.2
1380.1 | 748.1 | 45.4 | 45 | 312.4 | 299.6 | 232.7
1381.1 | 749.1 | 45.5 | 45.1 | 313.9 | 300.8 | 233.2
1382.1 | 750.1 | 45.5 | 45.2 | 316.3 | 303.1 | 233.9
1383.1 | 751.1 | 45.6 | 45.2 | 318.7 | 305.5 | 234.7
1384.1 | 752.1 | 45.7 | 45.3 | 319.8 | 306.5 | 235.4
1385.1 | 753.1 | 45.8 | 45.4 | 321 | 306.6 | 235.8
1386.1 | 754.1 | 45.8 | 45.4 | 323.1 | 308.6 | 236.2
1387.1 | 755.1 | 45.9 | 45.5 | 324.7 | 309.5 | 236.7
1388.1 | 756.1 | 46 | 45.6 | 325.6 | 310.5 | 237.1
1389.1 | 757.1 | 46.1 | 45.6 | 326.6 | 311.1 | 237.6
1390.1 | 758.1 | 46.2 | 45.7 | 327.3 | 312 | 238.1
1391.1 | 759.1 | 46.2 | 45.8 | 328.2 | 312.6 | 238.5
1392.1 | 760.1 | 46.3 | 45.9 | 328.2 | 313 | 238.9
1393.1 | 761.1 | 46.4 | 45.9 | 328.2 | 313.1 | 239.2
1394.1 | 762.1 | 46.5 | 46 | 327.9 | 313.1 | 239.5
1395.1 | 763.1 | 46.6 | 46.1 | 327.5 | 312.9 | 239.8
1396.1 | 764.1 | 46.6 | 46.1 | 327 | 312.7 | 240
1397.1 | 765.1 | 46.7 | 46.2 | 326.7 | 313 | 240.2
1398.1 | 766.1 | 46.8 | 46.3 | 326.4 | 312.8 | 240.5
1399.1 | 767.1 | 46.9 | 46.4 | 325.7 | 312.3 | 240.7
1400.1 | 768.1 | 46.9 | 46.4 | 325 | 311.8 | 240.9
1401.1 | 769.1 | 47 | 46.5 | 324.3 | 311.4 | 241.1
1402.1 | 770.1 | 47.1 | 46.6 | 324.9 | 311.5 | 241.4
1403.1 | 771.1 | 47.2 | 46.6 | 325 | 312.7 | 241.8
1404.1 | 772.1 | 47.3 | 46.7 | 324.8 | 312.6 | 242.2
1405.1 | 773.1 | 47.3 | 46.8 | 324.9 | 312.4 | 242.3
1406.1 | 774.1 | 47.4 | 46.9 | 324.9 | 312.7 | 242.6
1407.1 | 775.1 | 47.5 | 46.9 | 324.5 | 312.2 | 242.8
1408.1 | 776.1 | 47.6 | 47 | 324.5 | 311.7 | 243
1409.1 | 777.1 | 47.7 | 47.1 | 324.3 | 310.8 | 243.1
1410.1 | 778.1 | 47.7 | 47.2 | 324.2 | 310.7 | 243.2
1411.1 | 779.1 | 47.8 | 47.2 | 324.3 | 310.4 | 243.5
1412.1 | 780.1 | 47.9 | 47.3 | 324.8 | 310.2 | 243.7
1413.1 | 781.1 | 48 | 47.4 | 325.1 | 310.4 | 243.9
1414.1 | 782.1 | 48.1 | 47.4 | 326.3 | 311.2 | 244.3
1415.1 | 783.1 | 48.1 | 47.5 | 327 | 311.6 | 244.8
1416.1 | 784.1 | 48.2 | 47.6 | 327.7 | 312.3 | 245.3
1417.1 | 785.1 | 48.3 | 47.7 | 329.8 | 313.8 | 245.7
1418.1 | 786.1 | 48.4 | 47.8 | 332.1 | 315.1 | 246.2
1419.1 | 787.1 | 48.5 | 47.8 | 334.3 | 317.1 | 246.7
1420.1 | 788.1 | 48.6 | 47.9 | 336.3 | 320.9 | 247.5
1421.1 | 789.1 | 48.6 | 48 | 338.3 | 323.3 | 248.3
1422.1 | 790.1 | 48.7 | 48.1 | 339.7 | 325.3 | 248.8
1423.1 | 791.1 | 48.8 | 48.2 | 342.2 | 328.2 | 249.7
1424.1 | 792.1 | 48.9 | 48.2 | 344.5 | 329.1 | 250.3
1425.1 | 793.1 | 49 | 48.3 | 345.3 | 330 | 250.8
1426.1 | 794.1 | 49.1 | 48.4 | 346.2 | 331.1 | 251.4
1427.1 | 795.1 | 49.1 | 48.5 | 346.6 | 331.6 | 251.8
1428.1 | 796.1 | 49.2 | 48.6 | 346.6 | 332.1 | 252.5
1429.1 | 797.1 | 49.3 | 48.6 | 346.5 | 332.4 | 252.8
1430.1 | 798.1 | 49.4 | 48.7 | 346.7 | 332.3 | 253.1
1431.1 | 799.1 | 49.4 | 48.8 | 347.5 | 332.1 | 253.4
1432.1 | 800.1 | 49.5 | 48.9 | 347.5 | 331.6 | 253.6
1433.1 | 801.1 | 49.6 | 49 | 348.1 | 332 | 253.9
1434.1 | 802.1 | 49.7 | 49 | 349.6 | 333 | 254.6
1435.1 | 803.1 | 49.8 | 49.1 | 350.3 | 333.8 | 255.1
1436.1 | 804.1 | 49.9 | 49.2 | 350.4 | 333.5 | 255.5
1437.1 | 805.1 | 49.9 | 49.3 | 350 | 332.9 | 255.6
1438.1 | 806.1 | 50 | 49.4 | 349.4 | 332.7 | 255.9
1439.1 | 807.1 | 50.1 | 49.4 | 348.8 | 332.1 | 256.1
1440.1 | 808.1 | 50.2 | 49.5 | 347.9 | 331 | 256.1
1441.1 | 809.1 | 50.3 | 49.6 | 347.4 | 329.8 | 256.2
1442.1 | 810.1 | 50.4 | 49.7 | 346.5 | 328.6 | 256.4
1443.1 | 811.1 | 50.4 | 49.8 | 345.5 | 327.6 | 256.4
1444.1 | 812.1 | 50.5 | 49.8 | 345 | 327.1 | 256.6
1445.1 | 813.1 | 50.6 | 49.9 | 344.8 | 327.1 | 256.8
1446.1 | 814.1 | 50.7 | 50 | 344.7 | 327.3 | 257.2
1447.1 | 815.1 | 50.7 | 50.1 | 344.7 | 327.6 | 257.7
1448.1 | 816.1 | 50.8 | 50.2 | 344.8 | 327.8 | 257.9
1449.1 | 817.1 | 50.9 | 50.3 | 344.8 | 328.3 | 258.3
1450.1 | 818.1 | 51 | 50.3 | 344.7 | 328.4 | 258.5
1451.1 | 819.1 | 51.1 | 50.4 | 345 | 329.1 | 258.8
1452.1 | 820.1 | 51.2 | 50.5 | 345.4 | 330 | 259.3
1453.1 | 821.1 | 51.2 | 50.6 | 347.1 | 332.2 | 259.7
1454.1 | 822.1 | 51.3 | 50.7 | 347.7 | 332.6 | 260.1
1455.1 | 823.1 | 51.4 | 50.7 | 347.7 | 332.6 | 260.2
1456.1 | 824.1 | 51.5 | 50.8 | 347.9 | 333.3 | 260.6
1457.1 | 825.1 | 51.6 | 50.9 | 348.8 | 334.3 | 261
1458.1 | 826.1 | 51.6 | 51 | 349.9 | 335.3 | 261.4
1459.1 | 827.1 | 51.7 | 51.1 | 351.1 | 335.1 | 261.6
1460.1 | 828.1 | 51.8 | 51.2 | 351.1 | 334.9 | 261.7
1461.1 | 829.1 | 51.9 | 51.2 | 351 | 334.3 | 261.8
1462.1 | 830.1 | 52 | 51.3 | 350 | 333.9 | 261.9
1463.1 | 831.1 | 52 | 51.4 | 349.1 | 333 | 262
1464.1 | 832.1 | 52.1 | 51.5 | 348.3 | 331.9 | 262.2
1465.1 | 833.1 | 52.2 | 51.6 | 347.6 | 330.9 | 262.1
1466.1 | 834.1 | 52.3 | 51.7 | 347.3 | 330.1 | 262.1
1467.1 | 835.1 | 52.4 | 51.8 | 347.1 | 329 | 262
1468.1 | 836.1 | 52.4 | 51.8 | 346.5 | 328.4 | 262
1469.1 | 837.1 | 52.5 | 51.9 | 346.2 | 328.6 | 262.1
1470.1 | 838.1 | 52.6 | 52 | 346.1 | 328.1 | 262.2
1471.1 | 839.1 | 52.7 | 52.1 | 346.6 | 328.5 | 262.2
1472.1 | 840.1 | 52.7 | 52.2 | 347.7 | 329 | 262.5
1473.1 | 841.1 | 52.8 | 52.3 | 348.2 | 330.3 | 262.7
1474.1 | 842.1 | 52.9 | 52.3 | 348.9 | 330.8 | 263
1475.1 | 843.1 | 53 | 52.4 | 348.9 | 330.9 | 263.2
1476.1 | 844.1 | 53 | 52.5 | 349 | 331 | 263.5
1477.1 | 845.1 | 53.1 | 52.6 | 349.3 | 330.8 | 263.8
1478.1 | 846.1 | 53.2 | 52.7 | 349.5 | 330.3 | 263.9
1479.1 | 847.1 | 53.3 | 52.8 | 349.3 | 330 | 263.9
1480.1 | 848.1 | 53.4 | 52.8 | 348.9 | 329.2 | 263.9
1481.1 | 849.1 | 53.5 | 52.9 | 348.8 | 329.1 | 264
1482.1 | 850.1 | 53.6 | 52.9 | 348.5 | 328.9 | 264.3
1483.1 | 851.1 | 53.7 | 53.1 | 348.7 | 329.1 | 264.6
1484.1 | 852.1 | 53.7 | 53.2 | 348.7 | 329.1 | 265
1485.1 | 853.1 | 53.8 | 53.2 | 348.5 | 329.3 | 265.3
1486.1 | 854.1 | 53.9 | 53.3 | 348.5 | 328.9 | 265.5
1487.1 | 855.1 | 54 | 53.4 | 348.2 | 328.9 | 265.6
1488.1 | 856.1 | 54.1 | 53.5 | 348 | 329.2 | 265.9
1489.1 | 857.1 | 54.2 | 53.5 | 347.6 | 329.3 | 266
1490.1 | 858.1 | 54.2 | 53.7 | 348.1 | 329.1 | 266.3
1491.1 | 859.1 | 54.3 | 53.8 | 348.4 | 329.5 | 266.6
1492.1 | 860.1 | 54.4 | 53.8 | 348.7 | 329.6 | 266.9
1493.1 | 861.1 | 54.5 | 53.9 | 348.9 | 329.5 | 266.9
1494.1 | 862.1 | 54.6 | 54 | 348.7 | 329.2 | 266.8
1495.1 | 863.1 | 54.7 | 54.1 | 348.8 | 329.3 | 266.8
1496.1 | 864.1 | 54.8 | 54.2 | 349.7 | 330 | 267
1497.1 | 865.1 | 54.8 | 54.3 | 350.1 | 330.5 | 267
1498.1 | 866.1 | 54.9 | 54.4 | 350.7 | 331.5 | 267.3
1499.1 | 867.1 | 55 | 54.5 | 352 | 332.5 | 267.7
1500.1 | 868.1 | 55.1 | 54.6 | 352.9 | 333.1 | 268
1501.1 | 869.1 | 55.2 | 54.7 | 353.2 | 332.8 | 268
1502.1 | 870.1 | 55.3 | 54.8 | 352.9 | 332.4 | 267.9
1503.1 | 871.1 | 55.4 | 54.9 | 353.6 | 332.3 | 268.1
1504.1 | 872.1 | 55.4 | 55 | 354.7 | 332 | 268.4
1505.1 | 873.1 | 55.5 | 55.1 | 356.1 | 332.7 | 268.7
1506.1 | 874.1 | 55.6 | 55.1 | 357.3 | 333.1 | 268.8
1507.1 | 875.1 | 55.7 | 55.2 | 357.9 | 333.7 | 268.9
1508.1 | 876.1 | 55.8 | 55.4 | 358.2 | 333.6 | 269
1509.1 | 877.1 | 55.9 | 55.5 | 358.8 | 333.6 | 269.1
1510.1 | 878.1 | 56 | 55.5 | 359.1 | 333.2 | 269.2
1511.1 | 879.1 | 56 | 55.6 | 359.4 | 333.9 | 269.4
1512.1 | 880.1 | 56.1 | 55.7 | 359.6 | 334.5 | 269.6
1513.1 | 881.1 | 56.2 | 55.8 | 359.2 | 334.5 | 269.9
1514.1 | 882.1 | 56.3 | 55.9 | 358.8 | 334.7 | 269.9
1515.1 | 883.1 | 56.4 | 56 | 359.1 | 334.7 | 270.1
1516.1 | 884.1 | 56.5 | 56.1 | 359.5 | 334.4 | 270.1
1517.1 | 885.1 | 56.6 | 56.2 | 359.6 | 334.6 | 270.2
1518.1 | 886.1 | 56.6 | 56.3 | 360.8 | 335.7 | 270.5
1519.1 | 887.1 | 56.7 | 56.4 | 361.1 | 337 | 270.9
1520.1 | 888.1 | 56.8 | 56.5 | 364 | 340.1 | 271.5
1521.1 | 889.1 | 56.9 | 56.6 | 365.8 | 340.9 | 271.7
1522.1 | 890.1 | 57 | 56.7 | 366.9 | 340.9 | 271.8
1523.1 | 891.1 | 57.1 | 56.8 | 367 | 340.8 | 271.8
1524.1 | 892.1 | 57.2 | 56.9 | 366.4 | 340.5 | 271.9
1525.1 | 893.1 | 57.3 | 57 | 367 | 340.3 | 272.3
1526.1 | 894.1 | 57.4 | 57.1 | 367.1 | 340.9 | 272.7
1527.1 | 895.1 | 57.5 | 57.2 | 367.4 | 341.3 | 273
1528.1 | 896.1 | 57.6 | 57.3 | 367.3 | 341.5 | 273.4
1529.1 | 897.1 | 57.7 | 57.4 | 367.4 | 342.1 | 273.7
1530.1 | 898.1 | 57.7 | 57.5 | 366.9 | 342 | 274
1531.1 | 899.1 | 57.9 | 57.6 | 367.4 | 342.6 | 274.4
1532.1 | 900.1 | 57.9 | 57.7 | 369.6 | 344 | 274.8
1533.1 | 901.1 | 58 | 57.8 | 371.5 | 345.5 | 275.2
1534.1 | 902.1 | 58.1 | 57.9 | 372.8 | 345.8 | 275.5
1535.1 | 903.1 | 58.2 | 58 | 373.2 | 346.1 | 275.7
1536.1 | 904.1 | 58.3 | 58.1 | 374.7 | 347 | 275.9
1537.1 | 905.1 | 58.4 | 58.2 | 375.8 | 348.2 | 276.4
1538.1 | 906.1 | 58.5 | 58.3 | 377.5 | 350.2 | 277
1539.1 | 907.1 | 58.6 | 58.4 | 378.5 | 351.7 | 277.5
1540.1 | 908.1 | 58.7 | 58.5 | 379 | 352.7 | 277.9
1541.1 | 909.1 | 58.8 | 58.6 | 380.8 | 355 | 278.6
1542.1 | 910.1 | 58.9 | 58.7 | 382.8 | 356.7 | 279.3
1543.1 | 911.1 | 59 | 58.8 | 384 | 357.7 | 279.6
1544.1 | 912.1 | 59.1 | 58.9 | 385.2 | 358.5 | 280.1
1545.1 | 913.1 | 59.2 | 59 | 385.9 | 359.2 | 280.5
1546.1 | 914.1 | 59.3 | 59.1 | 387 | 359.7 | 280.6
1547.1 | 915.1 | 59.4 | 59.3 | 386.9 | 359.6 | 280.8
1548.1 | 916.1 | 59.5 | 59.4 | 386.4 | 359.5 | 281
1549.1 | 917.1 | 59.6 | 59.4 | 386.4 | 359.5 | 281.3
1550.1 | 918.1 | 59.6 | 59.6 | 386.7 | 359.8 | 281.7
1551.1 | 919.1 | 59.7 | 59.7 | 387.1 | 360.4 | 282
1552.1 | 920.1 | 59.9 | 59.8 | 386.7 | 359.4 | 282.3
1553.1 | 921.1 | 59.9 | 59.9 | 385.9 | 359.2 | 282.3
1554.1 | 922.1 | 60 | 60 | 385.9 | 358.9 | 282.4
1555.1 | 923.1 | 60.1 | 60.1 | 385.6 | 359.2 | 282.7
1556.1 | 924.1 | 60.2 | 60.2 | 385.7 | 359.4 | 282.9
1557.1 | 925.1 | 60.3 | 60.3 | 386.4 | 359.9 | 283.3
1558.1 | 926.1 | 60.4 | 60.4 | 386.2 | 359.2 | 283.4
1559.1 | 927.1 | 60.6 | 60.5 | 386.2 | 358.5 | 283.7
1560.1 | 928.1 | 60.6 | 60.6 | 385.8 | 357.2 | 283.7
1561.1 | 929.1 | 60.7 | 60.7 | 384.9 | 356.6 | 283.8
1562.1 | 930.1 | 60.8 | 60.8 | 384.3 | 356.4 | 284
1563.1 | 931.1 | 60.9 | 60.9 | 384 | 355.9 | 284.2
1564.1 | 932.1 | 61 | 61.1 | 383.6 | 355.3 | 284.2
1565.1 | 933.1 | 61.1 | 61.2 | 383.6 | 355.4 | 284.2
1566.1 | 934.1 | 61.2 | 61.3 | 383.5 | 355.5 | 284.6
1567.1 | 935.1 | 61.3 | 61.4 | 383.2 | 355.5 | 284.8
1568.1 | 936.1 | 61.4 | 61.5 | 382.8 | 355 | 284.9
1569.1 | 937.1 | 61.5 | 61.6 | 382 | 354.4 | 285.1
1570.1 | 938.1 | 61.6 | 61.7 | 382 | 354 | 285.1
1571.1 | 939.1 | 61.7 | 61.9 | 382 | 353.2 | 285
1572.1 | 940.1 | 61.8 | 62 | 381.6 | 352.7 | 285.2
1573.1 | 941.1 | 61.9 | 62 | 381.2 | 352.7 | 285.5
1574.1 | 942.1 | 62 | 62.2 | 381.1 | 352.4 | 285.4
1575.1 | 943.1 | 62.1 | 62.3 | 381.5 | 352.9 | 285.5
1576.1 | 944.1 | 62.2 | 62.4 | 381.1 | 352.4 | 285.6
1577.1 | 945.1 | 62.3 | 62.5 | 381.4 | 352.7 | 285.7
1578.1 | 946.1 | 62.4 | 62.6 | 382 | 353 | 286.1
1579.1 | 947.1 | 62.5 | 62.7 | 383.6 | 354.5 | 286.5
1580.1 | 948.1 | 62.6 | 62.8 | 386.9 | 357.5 | 287.4
1581.1 | 949.1 | 62.7 | 62.9 | 389 | 359.4 | 287.9
1582.1 | 950.1 | 62.8 | 63.1 | 390.9 | 361.4 | 288.5
1583.1 | 951.1 | 62.9 | 63.2 | 393.6 | 364.1 | 289.1
1584.1 | 952.1 | 63 | 63.2 | 395.8 | 366.3 | 289.6
1585.1 | 953.1 | 63 | 63.4 | 397.2 | 367.9 | 290
1586.1 | 954.1 | 63.1 | 63.5 | 397.7 | 368.8 | 290.5
1587.1 | 955.1 | 63.3 | 63.6 | 398 | 369.6 | 291
1588.1 | 956.1 | 63.4 | 63.7 | 398.4 | 369.6 | 291.3
1589.1 | 957.1 | 63.5 | 63.9 | 398.9 | 370.6 | 291.6
1590.1 | 958.1 | 63.6 | 64 | 399.9 | 372 | 292
1591.1 | 959.1 | 63.7 | 64.1 | 400.8 | 372.9 | 292.4
1592.1 | 960.1 | 63.7 | 64.2 | 403.7 | 376.1 | 293
1593.1 | 961.1 | 63.9 | 64.3 | 407.8 | 380.9 | 293.8
1594.1 | 962.1 | 64 | 64.4 | 409.7 | 381.5 | 294.4
1595.1 | 963.1 | 64.1 | 64.5 | 411.3 | 382.5 | 294.9
1596.1 | 964.1 | 64.2 | 64.7 | 412.1 | 385.8 | 295.3
1597.1 | 965.1 | 64.3 | 64.8 | 413.2 | 388.3 | 296.3
1598.1 | 966.1 | 64.4 | 64.8 | 414 | 388.4 | 296.7
1599.1 | 967.1 | 64.5 | 65 | 415.2 | 390.3 | 297.1
1600.1 | 968.1 | 64.6 | 65.1 | 417.4 | 391.7 | 297.9
1601.1 | 969.1 | 64.7 | 65.2 | 418.9 | 392.3 | 298.5
1602.1 | 970.1 | 64.8 | 65.3 | 419.2 | 392.4 | 298.7
1603.1 | 971.1 | 64.9 | 65.5 | 418.5 | 391.6 | 298.9
1604.1 | 972.1 | 65 | 65.6 | 417.3 | 390.6 | 299
1605.1 | 973.1 | 65.1 | 65.6 | 417 | 389.4 | 299.2
1606.1 | 974.1 | 65.2 | 65.8 | 416.1 | 388.5 | 299.5
1607.1 | 975.1 | 65.3 | 65.9 | 415.9 | 388.1 | 299.8
1608.1 | 976.1 | 65.4 | 66 | 415.9 | 387.7 | 300
1609.1 | 977.1 | 65.5 | 66.1 | 415.1 | 386.9 | 299.9
1610.1 | 978.1 | 65.6 | 66.2 | 413.7 | 385.3 | 299.8
1611.1 | 979.1 | 65.7 | 66.4 | 413.2 | 384.5 | 300.1
1612.1 | 980.1 | 65.8 | 66.5 | 412.8 | 383.8 | 300.4
1613.1 | 981.1 | 65.9 | 66.6 | 412.5 | 382.7 | 300.6
1614.1 | 982.1 | 66 | 66.7 | 411.7 | 381.7 | 300.8
1615.1 | 983.1 | 66.1 | 66.8 | 410.9 | 380.9 | 301
1616.1 | 984.1 | 66.2 | 67 | 409.9 | 380 | 301.1
1617.1 | 985.1 | 66.3 | 67.1 | 409 | 379.1 | 301.2
1618.1 | 986.1 | 66.5 | 67.2 | 408.1 | 377.7 | 301.3
1619.1 | 987.1 | 66.6 | 67.3 | 407.2 | 377.4 | 301.6
1620.1 | 988.1 | 66.7 | 67.4 | 406.7 | 377.2 | 301.7
1621.1 | 989.1 | 66.8 | 67.5 | 406.5 | 376.7 | 301.8
1622.1 | 990.1 | 66.9 | 67.7 | 406 | 375.9 | 302
1623.1 | 991.1 | 67 | 67.8 | 405.7 | 376 | 302.3
1624.1 | 992.1 | 67.1 | 67.9 | 405.7 | 375.9 | 302.6
1625.1 | 993.1 | 67.2 | 68 | 404.5 | 374.8 | 302.6
1626.1 | 994.1 | 67.3 | 68.1 | 403.6 | 374.2 | 302.6
1627.1 | 995.1 | 67.4 | 68.3 | 402.7 | 373.7 | 302.7
1628.1 | 996.1 | 67.5 | 68.4 | 402 | 373.4 | 302.8
1629.1 | 997.1 | 67.7 | 68.5 | 402.4 | 373.3 | 303
1630.1 | 998.1 | 67.8 | 68.6 | 403 | 374 | 303.1
1631.1 | 999.1 | 67.8 | 68.7 | 403.5 | 374.1 | 303.3
1632.1 | 1000.1 | 68 | 68.8 | 403.1 | 373.4 | 303.5
1633.1 | 1001.1 | 68.1 | 69 | 402.5 | 372.9 | 303.7
1634.1 | 1002.1 | 68.2 | 69.1 | 402.8 | 373.2 | 303.8
1635.1 | 1003.1 | 68.3 | 69.2 | 403 | 373.6 | 304
1636.1 | 1004.1 | 68.4 | 69.3 | 402.8 | 373.7 | 304.4
1637.1 | 1005.1 | 68.5 | 69.5 | 402.1 | 373.6 | 304.7
1638.1 | 1006.1 | 68.6 | 69.6 | 402.3 | 373.9 | 305
1639.1 | 1007.1 | 68.7 | 69.7 | 402.3 | 373.5 | 305.1
1640.1 | 1008.1 | 68.9 | 69.8 | 401.5 | 372.5 | 305.2
1641.1 | 1009.1 | 69 | 70 | 400.3 | 371.8 | 305.3
1642.1 | 1010.1 | 69.1 | 70.1 | 399.7 | 371.3 | 305.4
1643.1 | 1011.1 | 69.2 | 70.1 | 399.1 | 370.5 | 305.5
1644.1 | 1012.1 | 69.3 | 70.3 | 398.5 | 370.1 | 305.4
1645.1 | 1013.1 | 69.4 | 70.4 | 398.4 | 370 | 305.4
1646.1 | 1014.1 | 69.6 | 70.5 | 397.9 | 369.6 | 305.5
1647.1 | 1015.1 | 69.7 | 70.6 | 397.6 | 369.1 | 305.6
1648.1 | 1016.1 | 69.8 | 70.8 | 396.9 | 368.4 | 305.6
1649.1 | 1017.1 | 69.9 | 70.9 | 396.4 | 367.7 | 305.5
1650.1 | 1018.1 | 70 | 71 | 396.3 | 367 | 305.6
1651.1 | 1019.1 | 70.1 | 71.2 | 396 | 366.8 | 305.6
1652.1 | 1020.1 | 70.2 | 71.3 | 395.9 | 367.1 | 305.7
1653.1 | 1021.1 | 70.3 | 71.4 | 396.2 | 367.5 | 305.8
1654.1 | 1022.1 | 70.5 | 71.5 | 397.3 | 368.6 | 306.2
1655.1 | 1023.1 | 70.5 | 71.7 | 397.8 | 369.2 | 306.3
1656.1 | 1024.1 | 70.6 | 71.8 | 398.6 | 370.4 | 306.6
1657.1 | 1025.1 | 70.8 | 71.9 | 400.3 | 372 | 307.1
1658.1 | 1026.1 | 70.9 | 72 | 400.8 | 372.5 | 307.3
1659.1 | 1027.1 | 71 | 72.2 | 401.2 | 374 | 307.6
1660.1 | 1028.1 | 71.1 | 72.3 | 402.9 | 375 | 308
1661.1 | 1029.1 | 71.3 | 72.4 | 404.8 | 376.9 | 308.6
1662.1 | 1030.1 | 71.3 | 72.5 | 406.1 | 378.2 | 308.9
1663.1 | 1031.1 | 71.4 | 72.7 | 407 | 379 | 309.2
1664.1 | 1032.1 | 71.6 | 72.8 | 406.9 | 379.2 | 309.5
1665.1 | 1033.1 | 71.7 | 72.9 | 408.6 | 381.2 | 309.9
1666.1 | 1034.1 | 71.8 | 73.1 | 411 | 383.3 | 310.5
1667.1 | 1035.1 | 71.9 | 73.2 | 412 | 384.2 | 311
1668.1 | 1036.1 | 72 | 73.3 | 413.9 | 385.1 | 311.2
1669.1 | 1037.1 | 72.1 | 73.4 | 414.9 | 385.9 | 311.4
1670.1 | 1038.1 | 72.2 | 73.6 | 416.4 | 387.1 | 311.8
1671.1 | 1039.1 | 72.4 | 73.6 | 418.1 | 388.8 | 312.5
1672.1 | 1040.1 | 72.5 | 73.8 | 419.2 | 389.9 | 313
1673.1 | 1041.1 | 72.6 | 73.9 | 420.8 | 391 | 313.3
1674.1 | 1042.1 | 72.7 | 74 | 422.6 | 392.5 | 313.7
1675.1 | 1043.1 | 72.9 | 74.2 | 423.5 | 392.4 | 313.8
1676.1 | 1044.1 | 72.9 | 74.3 | 423.9 | 392 | 313.9
1677.1 | 1045.1 | 73.1 | 74.4 | 423.9 | 392.3 | 314.3
1678.1 | 1046.1 | 73.2 | 74.5 | 424.6 | 393.9 | 315
1679.1 | 1047.1 | 73.3 | 74.7 | 426.5 | 395.2 | 315.4
1680.1 | 1048.1 | 73.4 | 74.8 | 427.7 | 396.2 | 315.7
1681.1 | 1049.1 | 73.6 | 75 | 428 | 396.5 | 316
1682.1 | 1050.1 | 73.7 | 75.1 | 427.9 | 396.1 | 316.2
1683.1 | 1051.1 | 73.8 | 75.2 | 428.3 | 396.3 | 316.5
1684.1 | 1052.1 | 73.9 | 75.4 | 429.3 | 397.5 | 316.8
1685.1 | 1053.1 | 74 | 75.5 | 430.6 | 398.2 | 317.1
1686.1 | 1054.1 | 74.2 | 75.6 | 431.5 | 399.7 | 317.6
1687.1 | 1055.1 | 74.3 | 75.8 | 431 | 398.9 | 317.8
1688.1 | 1056.1 | 74.4 | 75.9 | 430.4 | 397.7 | 317.9
1689.1 | 1057.1 | 74.5 | 76 | 429.5 | 397.3 | 318
1690.1 | 1058.1 | 74.6 | 76.2 | 429.2 | 396.9 | 318.2
1691.1 | 1059.1 | 74.7 | 76.3 | 428.5 | 395.9 | 318.4
1692.1 | 1060.1 | 74.9 | 76.4 | 427.2 | 394.6 | 318.3
1693.1 | 1061.1 | 75 | 76.6 | 427.7 | 395.1 | 318.7
1694.1 | 1062.1 | 75.1 | 76.7 | 427.7 | 395.6 | 318.8
1695.1 | 1063.1 | 75.3 | 76.8 | 428.3 | 395.7 | 319
1696.1 | 1064.1 | 75.4 | 76.9 | 427.6 | 395.1 | 319.1
1697.1 | 1065.1 | 75.5 | 77.1 | 426.4 | 394.1 | 319.2
1698.1 | 1066.1 | 75.6 | 77.3 | 426.7 | 393.5 | 319.4
1699.1 | 1067.1 | 75.8 | 77.4 | 426.2 | 392.4 | 319.5
1700.1 | 1068.1 | 75.9 | 77.5 | 426.1 | 392 | 319.6
1701.1 | 1069.1 | 76 | 77.7 | 425.7 | 391.7 | 319.8
1702.1 | 1070.1 | 76.1 | 77.8 | 425 | 391.3 | 319.9
1703.1 | 1071.1 | 76.2 | 77.9 | 425.3 | 391.6 | 320.2
1704.1 | 1072.1 | 76.3 | 78.1 | 425.4 | 391.4 | 320.5
1705.1 | 1073.1 | 76.4 | 78.2 | 426 | 392 | 320.8
1706.1 | 1074.1 | 76.6 | 78.3 | 427.5 | 394.6 | 321.3
1707.1 | 1075.1 | 76.7 | 78.5 | 428.3 | 396.6 | 321.9
1708.1 | 1076.1 | 76.8 | 78.6 | 427.9 | 396 | 322
1709.1 | 1077.1 | 77 | 78.8 | 426.8 | 395.1 | 322
1710.1 | 1078.1 | 77.1 | 78.9 | 425.7 | 394.1 | 322
1711.1 | 1079.1 | 77.2 | 79.1 | 424.2 | 392.7 | 322
1712.1 | 1080.1 | 77.3 | 79.2 | 422.7 | 390.9 | 321.9
1713.1 | 1081.1 | 77.5 | 79.3 | 421.5 | 390.2 | 322
1714.1 | 1082.1 | 77.6 | 79.5 | 420.9 | 389.5 | 322.2
1715.1 | 1083.1 | 77.7 | 79.6 | 420.1 | 388.3 | 322.3
1716.1 | 1084.1 | 77.8 | 79.8 | 419.3 | 387.3 | 322.4
1717.1 | 1085.1 | 78 | 79.9 | 418.2 | 386.6 | 322.6
1718.1 | 1086.1 | 78.1 | 80.1 | 417.6 | 386.4 | 322.6
1719.1 | 1087.1 | 78.2 | 80.2 | 418.4 | 387.1 | 322.7
1720.1 | 1088.1 | 78.3 | 80.3 | 420 | 389 | 323.3
1721.1 | 1089.1 | 78.5 | 80.5 | 420.4 | 389.3 | 323.5
1722.1 | 1090.1 | 78.6 | 80.6 | 420.8 | 389.8 | 323.6
1723.1 | 1091.1 | 78.7 | 80.8 | 421.5 | 390.5 | 323.7
1724.1 | 1092.1 | 78.9 | 80.9 | 422.4 | 391 | 324.1
1725.1 | 1093.1 | 79 | 81.1 | 421.6 | 390.5 | 324.2
1726.1 | 1094.1 | 79.1 | 81.2 | 420.4 | 389.3 | 324.1
1727.1 | 1095.1 | 79.3 | 81.3 | 420 | 388.7 | 324.1
1728.1 | 1096.1 | 79.4 | 81.5 | 419.1 | 387.8 | 324.2
1729.1 | 1097.1 | 79.5 | 81.7 | 418.5 | 387.5 | 324.3
1730.1 | 1098.1 | 79.6 | 81.8 | 417.9 | 387.3 | 324.5
1731.1 | 1099.1 | 79.7 | 81.9 | 417.2 | 386.8 | 324.6
1732.1 | 1100.1 | 79.9 | 82.1 | 416.7 | 386.3 | 324.7
1733.1 | 1101.1 | 80 | 82.2 | 417.1 | 386.2 | 324.9
1734.1 | 1102.1 | 80.2 | 82.4 | 417.5 | 386.5 | 325.2
1735.1 | 1103.1 | 80.3 | 82.5 | 417.5 | 386.5 | 325.4
1736.1 | 1104.1 | 80.4 | 82.7 | 417 | 385.7 | 325.3
1737.1 | 1105.1 | 80.5 | 82.8 | 416.1 | 384.7 | 325.3
1738.1 | 1106.1 | 80.7 | 82.9 | 416.5 | 385.2 | 325.6
1739.1 | 1107.1 | 80.8 | 83.1 | 418.1 | 386.4 | 325.9
1740.1 | 1108.1 | 80.9 | 83.3 | 418.8 | 387.3 | 326.1
1741.1 | 1109.1 | 81.1 | 83.4 | 419.7 | 387.5 | 326.4
1742.1 | 1110.1 | 81.2 | 83.5 | 419.6 | 386.9 | 326.4
1743.1 | 1111.1 | 81.3 | 83.7 | 418.8 | 385.8 | 326.3
1744.1 | 1112.1 | 81.5 | 83.8 | 417.1 | 384.2 | 326.2
1745.1 | 1113.1 | 81.6 | 84 | 415.4 | 383.1 | 326.1
1746.1 | 1114.1 | 81.7 | 84.1 | 414.5 | 382.6 | 326.1
1747.1 | 1115.1 | 81.9 | 84.3 | 414 | 381.9 | 326.1
1748.1 | 1116.1 | 82.1 | 84.4 | 412.8 | 381.4 | 326.2
1749.1 | 1117.1 | 82.2 | 84.6 | 412.1 | 381.4 | 326.4
1750.1 | 1118.1 | 82.3 | 84.8 | 412.7 | 381.8 | 326.6
1751.1 | 1119.1 | 82.5 | 84.9 | 414.8 | 382.9 | 326.9
1752.1 | 1120.1 | 82.6 | 85 | 417.4 | 385.7 | 327.3
1753.1 | 1121.1 | 82.7 | 85.2 | 422.3 | 389.2 | 327.8
1754.1 | 1122.1 | 82.8 | 85.4 | 424.3 | 391.3 | 328.3
1755.1 | 1123.1 | 83 | 85.5 | 425.1 | 391.6 | 328.7
1756.1 | 1124.1 | 83.1 | 85.7 | 425.8 | 391.7 | 328.7
1757.1 | 1125.1 | 83.3 | 85.8 | 426.4 | 392.1 | 328.8
1758.1 | 1126.1 | 83.4 | 86 | 428.8 | 393.2 | 329
1759.1 | 1127.1 | 83.6 | 86.1 | 430.4 | 394 | 329.2
1760.1 | 1128.1 | 83.7 | 86.3 | 430.9 | 394.2 | 329.5
1761.1 | 1129.1 | 83.9 | 86.4 | 430.6 | 394.3 | 329.7
1762.1 | 1130.1 | 84 | 86.6 | 429.8 | 393.7 | 329.7
1763.1 | 1131.1 | 84.1 | 86.7 | 429 | 393.1 | 329.9
1764.1 | 1132.1 | 84.3 | 86.9 | 427.9 | 392.1 | 330
1765.1 | 1133.1 | 84.4 | 87 | 427.3 | 391.9 | 330.1
1766.1 | 1134.1 | 84.6 | 87.2 | 427 | 392 | 330.4
1767.1 | 1135.1 | 84.7 | 87.3 | 427.3 | 392.6 | 330.5
1768.1 | 1136.1 | 84.9 | 87.5 | 427.9 | 393.2 | 330.8
1769.1 | 1137.1 | 85 | 87.6 | 428 | 393.4 | 331
1770.1 | 1138.1 | 85.1 | 87.8 | 427.8 | 393.6 | 331.2
1771.1 | 1139.1 | 85.3 | 88 | 429.1 | 395.7 | 331.4
1772.1 | 1140.1 | 85.4 | 88.1 | 430.3 | 397.4 | 331.8
1773.1 | 1141.1 | 85.6 | 88.2 | 430.7 | 397.9 | 332.1
1774.1 | 1142.1 | 85.7 | 88.4 | 429.4 | 396.8 | 331.9
1775.1 | 1143.1 | 85.9 | 88.6 | 427.8 | 395.5 | 331.8
1776.1 | 1144.1 | 86 | 88.7 | 426.3 | 393.8 | 331.8
1777.1 | 1145.1 | 86.2 | 88.8 | 424.9 | 392.6 | 331.7
1778.1 | 1146.1 | 86.3 | 89 | 423.7 | 391.6 | 331.6
1779.1 | 1147.1 | 86.5 | 89.1 | 423.2 | 391 | 331.6
1780.1 | 1148.1 | 86.6 | 89.3 | 422.3 | 390 | 331.6
1781.1 | 1149.1 | 86.8 | 89.5 | 421.9 | 389.4 | 331.7
1782.1 | 1150.1 | 86.9 | 89.6 | 422.7 | 389.8 | 332
1783.1 | 1151.1 | 87.3 | 89.5 | 422.7 | 390 | 332.4
1784.1 | 1152.1 | 87.2 | 89.9 | 422.4 | 390 | 332.2
1785.1 | 1153.1 | 87.4 | 90 | 422.1 | 390.2 | 332.5
1786.1 | 1154.1 | 87.5 | 90.3 | 421.8 | 389.9 | 332.6
1787.1 | 1155.1 | 87.7 | 90.4 | 421 | 389.4 | 332.6
1788.1 | 1156.1 | 87.8 | 90.6 | 419.9 | 388.9 | 332.6
1789.1 | 1157.1 | 87.9 | 90.7 | 419.3 | 388.5 | 332.7
1790.1 | 1158.1 | 88.1 | 90.8 | 419.9 | 388.8 | 332.9
1791.1 | 1159.1 | 88.3 | 91 | 420.4 | 388.9 | 333
1792.1 | 1160.1 | 88.4 | 91.2 | 420.7 | 389.1 | 333.2
1793.1 | 1161.1 | 88.5 | 91.3 | 420.9 | 389.4 | 333.4
1794.1 | 1162.1 | 88.7 | 91.5 | 421.8 | 390.1 | 333.7
1795.1 | 1163.1 | 88.9 | 91.7 | 421.2 | 389.6 | 333.6
1796.1 | 1164.1 | 89 | 91.8 | 420.3 | 389 | 333.6
1797.1 | 1165.1 | 89.2 | 92 | 419.3 | 388.2 | 333.7
1798.1 | 1166.1 | 89.3 | 92.1 | 418.9 | 388.1 | 333.7
1799.1 | 1167.1 | 89.4 | 92.3 | 418.7 | 387.8 | 333.6
1800.1 | 1168.1 | 89.6 | 92.4 | 418.6 | 387.7 | 333.7
1801.1 | 1169.1 | 89.8 | 92.6 | 420.5 | 388.2 | 334
1802.1 | 1170.1 | 89.9 | 92.8 | 420.9 | 388.6 | 334.1
1803.1 | 1171.1 | 90.1 | 92.9 | 420.6 | 388.5 | 334.2
1804.1 | 1172.1 | 90.2 | 93.1 | 419.7 | 387.9 | 334.3
1805.1 | 1173.1 | 90.4 | 93.2 | 419.2 | 387.4 | 334.3
1806.1 | 1174.1 | 90.5 | 93.4 | 420 | 388.3 | 334.6
1807.1 | 1175.1 | 90.7 | 93.6 | 421.1 | 389.3 | 334.9
1808.1 | 1176.1 | 90.9 | 93.7 | 420.8 | 389.5 | 335
1809.1 | 1177.1 | 91 | 93.9 | 421.3 | 389.8 | 335.2
1810.1 | 1178.1 | 91.2 | 94 | 423 | 390.6 | 335.5
1811.1 | 1179.1 | 91.3 | 94.2 | 425 | 391.9 | 336
1812.1 | 1180.1 | 91.5 | 94.3 | 426.1 | 392.7 | 336.2
1813.1 | 1181.1 | 91.6 | 94.5 | 426 | 392.6 | 336.3
1814.1 | 1182.1 | 91.8 | 94.6 | 424.8 | 391.8 | 336.2
1815.1 | 1183.1 | 92 | 94.8 | 423.8 | 391.1 | 336.3
1816.1 | 1184.1 | 92.1 | 94.9 | 422.7 | 390 | 336.2
1817.1 | 1185.1 | 92.2 | 95.1 | 421.4 | 389.3 | 336.2
1818.1 | 1186.1 | 92.4 | 95.2 | 420.6 | 389.3 | 336.4
1819.1 | 1187.1 | 92.5 | 95.4 | 420 | 388.6 | 336.5
1820.1 | 1188.1 | 92.7 | 95.6 | 419.2 | 387.9 | 336.5
1821.1 | 1189.1 | 92.9 | 95.7 | 418.1 | 387 | 336.5
1822.1 | 1190.1 | 93 | 95.9 | 417.4 | 386.4 | 336.6
1823.1 | 1191.1 | 93.2 | 96 | 416.5 | 385.9 | 336.7
1824.1 | 1192.1 | 93.3 | 96.2 | 416.2 | 385.9 | 336.8
1825.1 | 1193.1 | 93.5 | 96.3 | 416 | 385.5 | 336.9
1826.1 | 1194.1 | 93.6 | 96.5 | 415.3 | 384.9 | 336.9
1827.1 | 1195.1 | 93.8 | 96.7 | 415.1 | 385 | 337.1
1828.1 | 1196.1 | 93.9 | 96.8 | 414.9 | 384.5 | 337.1
1829.1 | 1197.1 | 94.1 | 97 | 415.1 | 385.4 | 337.3
1830.1 | 1198.1 | 94.3 | 97.1 | 417 | 387.8 | 337.8
1831.1 | 1199.1 | 94.4 | 97.3 | 418.4 | 389 | 338.2
1832.1 | 1200.1 | 94.6 | 97.4 | 420.4 | 390.1 | 338.4
1833.1 | 1201.1 | 94.7 | 97.6 | 421.6 | 390.9 | 338.6
1834.1 | 1202.1 | 94.9 | 97.8 | 423.9 | 393.9 | 339.1
1835.1 | 1203.1 | 95.1 | 97.9 | 427.6 | 398.2 | 340
1836.1 | 1204.1 | 95.2 | 98.1 | 430.6 | 400.7 | 340.7
1837.1 | 1205.1 | 95.4 | 98.3 | 433 | 402.1 | 340.9
1838.1 | 1206.1 | 95.5 | 98.4 | 434 | 402.6 | 341
1839.1 | 1207.1 | 95.7 | 98.6 | 434.7 | 402.5 | 341.2
1840.1 | 1208.1 | 95.9 | 98.7 | 433.9 | 401.9 | 341.1
1841.1 | 1209.1 | 96 | 98.9 | 432.4 | 400.9 | 341.1
1842.1 | 1210.1 | 96.2 | 99 | 430.8 | 399.8 | 341.1
1843.1 | 1211.1 | 96.3 | 99.2 | 429.5 | 398.5 | 341.1
1844.1 | 1212.1 | 96.5 | 99.4 | 428.3 | 397.2 | 341
1845.1 | 1213.1 | 96.6 | 99.5 | 427.2 | 396.2 | 341.1
1846.1 | 1214.1 | 96.8 | 99.7 | 426.2 | 395.1 | 341.1
1847.1 | 1215.1 | 97 | 99.8 | 425.2 | 393.8 | 340.9
1848.1 | 1216.1 | 97.1 | 100 | 424.3 | 392.8 | 340.9
1849.1 | 1217.1 | 97.3 | 100.2 | 424.5 | 391.7 | 340.8
1850.1 | 1218.1 | 97.5 | 100.3 | 423.7 | 390.9 | 340.8
1851.1 | 1219.1 | 97.6 | 100.5 | 423 | 390.1 | 340.6
1852.1 | 1220.1 | 97.8 | 100.7 | 422.1 | 389.2 | 340.5
1853.1 | 1221.1 | 98 | 100.8 | 421.2 | 388.4 | 340.5
1854.1 | 1222.1 | 98.1 | 101 | 422.1 | 388.7 | 340.6
1855.1 | 1223.1 | 98.2 | 101.2 | 424.2 | 389.5 | 340.7
1856.1 | 1224.1 | 98.4 | 101.3 | 425.8 | 390.7 | 340.9
1857.1 | 1225.1 | 98.6 | 101.5 | 427.2 | 392 | 341.1
1858.1 | 1226.1 | 98.7 | 101.7 | 429.7 | 393.7 | 341.3
1859.1 | 1227.1 | 98.9 | 101.8 | 430.4 | 394.5 | 341.5
1860.1 | 1228.1 | 99.1 | 102 | 430.7 | 395.7 | 341.7
1861.1 | 1229.1 | 99.2 | 102.2 | 433.1 | 398.6 | 342.2
1862.1 | 1230.1 | 99.3 | 102.4 | 436.4 | 402 | 342.7
1863.1 | 1231.1 | 99.5 | 102.5 | 441.9 | 405.9 | 343.4
1864.1 | 1232.1 | 99.7 | 102.7 | 445.6 | 409.5 | 344
1865.1 | 1233.1 | 99.8 | 102.9 | 449.2 | 412.5 | 344.6
1866.1 | 1234.1 | 100 | 103 | 451.4 | 414.1 | 345.1
1867.1 | 1235.1 | 100.2 | 103.2 | 453.2 | 414.6 | 345.5
1868.1 | 1236.1 | 100.3 | 103.3 | 454 | 415.2 | 345.7
1869.1 | 1237.1 | 100.5 | 103.5 | 453.8 | 415.5 | 345.9
1870.1 | 1238.1 | 100.6 | 103.7 | 454 | 415.9 | 346.3
1871.1 | 1239.1 | 100.8 | 103.8 | 454.7 | 417.2 | 346.7
1872.1 | 1240.1 | 100.9 | 104 | 456.6 | 419.6 | 347.3
1873.1 | 1241.1 | 101.1 | 104.2 | 458.4 | 420.8 | 347.8
1874.1 | 1242.1 | 101.3 | 104.3 | 458.9 | 420.9 | 348.1
1875.1 | 1243.1 | 101.4 | 104.5 | 458.5 | 420.7 | 348.3
1876.1 | 1244.1 | 101.6 | 104.7 | 458.4 | 420.3 | 348.5
1877.1 | 1245.1 | 101.7 | 104.9 | 459.1 | 420.8 | 348.9
1878.1 | 1246.1 | 101.9 | 105 | 459.9 | 421.5 | 349.3
1879.1 | 1247.1 | 102.1 | 105.2 | 460.7 | 421.8 | 349.5
1880.1 | 1248.1 | 102.2 | 105.3 | 461.3 | 422.5 | 349.8
1881.1 | 1249.1 | 102.4 | 105.5 | 462.3 | 423.1 | 350.2
1882.1 | 1250.1 | 102.5 | 105.6 | 462.1 | 423.5 | 350.6
1883.1 | 1251.1 | 102.7 | 105.8 | 461.7 | 423.2 | 351
1884.1 | 1252.1 | 102.9 | 106 | 461.5 | 423.7 | 351.4
1885.1 | 1253.1 | 103 | 106.2 | 461.6 | 424.1 | 351.9
1886.1 | 1254.1 | 103.2 | 106.3 | 462 | 424.9 | 352.2
1887.1 | 1255.1 | 103.3 | 106.5 | 461.1 | 423.7 | 352.3
1888.1 | 1256.1 | 103.5 | 106.6 | 460.3 | 423.3 | 352.5
1889.1 | 1257.1 | 103.7 | 106.8 | 460.9 | 424.2 | 352.8
1890.1 | 1258.1 | 103.8 | 106.9 | 462.5 | 426.1 | 353.3
1891.1 | 1259.1 | 104 | 107.1 | 464.8 | 429.7 | 354
1892.1 | 1260.1 | 104.2 | 107.3 | 465.6 | 429.9 | 354.6
1893.1 | 1261.1 | 104.3 | 107.5 | 467.8 | 432.9 | 355
1894.1 | 1262.1 | 104.4 | 107.6 | 469.6 | 433.7 | 355.3
1895.1 | 1263.1 | 104.6 | 107.7 | 469.8 | 433.9 | 355.7
1896.1 | 1264.1 | 104.8 | 107.9 | 471.3 | 434.3 | 356.3
1897.1 | 1265.1 | 104.9 | 108.1 | 472.4 | 436.4 | 356.8
1898.1 | 1266.1 | 105.1 | 108.2 | 472.2 | 436 | 357.3
1899.1 | 1267.1 | 105.2 | 108.4 | 472.1 | 436.8 | 357.5
1900.1 | 1268.1 | 105.4 | 108.6 | 472.6 | 438.4 | 358
1901.1 | 1269.1 | 105.6 | 108.7 | 475.3 | 439.9 | 358.7
1902.1 | 1270.1 | 105.7 | 108.9 | 474.8 | 438.3 | 358.9
1903.1 | 1271.1 | 105.9 | 109 | 473 | 436.6 | 358.9
1904.1 | 1272.1 | 106 | 109.2 | 474 | 439.1 | 359.4
1905.1 | 1273.1 | 106.2 | 109.4 | 480.4 | 440.9 | 360.4
1906.1 | 1274.1 | 106.4 | 109.5 | 486.7 | 441.9 | 360.7
1907.1 | 1275.1 | 106.5 | 109.7 | 500.2 | 443 | 361.1
1908.1 | 1276.1 | 106.7 | 109.8 | 502.4 | 441.6 | 361.3
1909.1 | 1277.1 | 106.9 | 110 | 507.9 | 442.5 | 361.7
1910.1 | 1278.1 | 107 | 110.2 | 517.7 | 443 | 362.3
1911.1 | 1279.1 | 107.2 | 110.3 | 518.5 | 442.1 | 362.6
1912.1 | 1280.1 | 107.3 | 110.5 | 522.4 | 441 | 362.9
1913.1 | 1281.1 | 107.5 | 110.6 | 526.2 | 440.8 | 363.3
1914.1 | 1282.1 | 107.7 | 110.8 | 531.8 | 441 | 363.7
1915.1 | 1283.1 | 107.8 | 111 | 546.5 | 445.6 | 365.2
1916.1 | 1284.1 | 108 | 111.2 | 564.6 | 451 | 367.8
1917.1 | 1285.1 | 108.1 | 111.3 | 567.6 | 451.1 | 367.7
1918.1 | 1286.1 | 108.3 | 111.5 | 572.2 | 450 | 367.9
1919.1 | 1287.1 | 108.5 | 111.7 | 573.9 | 449.9 | 368.5
1920.1 | 1288.1 | 108.6 | 111.8 | 580.2 | 451.1 | 369.1
1921.1 | 1289.1 | 108.8 | 112 | 597.1 | 453.1 | 369.7
1922.1 | 1290.1 | 109 | 112.2 | 604.4 | 454.3 | 370.3
1923.1 | 1291.1 | 109.1 | 112.4 | 606.6 | 455.4 | 370.9
1924.1 | 1292.1 | 109.3 | 112.6 | 603.9 | 457.2 | 373.8
1925.1 | 1293.1 | 109.5 | 112.8 | 605.4 | 466.7 | 379.7
1926.1 | 1294.1 | 109.6 | 112.9 | 602.5 | 467.8 | 379.7
1927.1 | 1295.1 | 109.8 | 113.1 | 599.1 | 466.8 | 379
1928.1 | 1296.1 | 109.9 | 113.3 | 603.5 | 465.8 | 379
1929.1 | 1297.1 | 110.1 | 113.5 | 601.5 | 464 | 379.1
1930.1 | 1298.1 | 110.3 | 113.6 | 595.8 | 462.2 | 379.2
1931.1 | 1299.1 | 110.5 | 113.8 | 590 | 461.4 | 379.2
1932.1 | 1300.1 | 110.6 | 114 | 582.9 | 461.8 | 379.8
1933.1 | 1301.1 | 110.8 | 114.1 | 577.9 | 463.2 | 380.4
1934.1 | 1302.1 | 111 | 114.3 | 576 | 466.9 | 381
1935.1 | 1303.1 | 111.1 | 114.5 | 572.5 | 470.2 | 381.4
1936.1 | 1304.1 | 111.3 | 114.7 | 568.4 | 468 | 381.7
1937.1 | 1305.1 | 111.5 | 114.8 | 569.7 | 467.6 | 382
1938.1 | 1306.1 | 111.7 | 115 | 579.2 | 474 | 383.1
1939.1 | 1307.1 | 111.8 | 115.2 | 584.8 | 474.7 | 383.8
1940.1 | 1308.1 | 112 | 115.3 | 584.1 | 473.4 | 384.2
1941.1 | 1309.1 | 112.2 | 115.5 | 579.1 | 472.3 | 384.4
1942.1 | 1310.1 | 112.3 | 115.6 | 576.5 | 472.4 | 384.8
1943.1 | 1311.1 | 112.5 | 115.8 | 576.8 | 471.5 | 385.4
1944.1 | 1312.1 | 112.7 | 115.9 | 579.5 | 470.1 | 385.7
1945.1 | 1313.1 | 112.8 | 116.1 | 575.9 | 468.4 | 385.9
1946.1 | 1314.1 | 113 | 116.3 | 572.1 | 466.3 | 386
1947.1 | 1315.1 | 113.2 | 116.4 | 568 | 464.8 | 386.2
1948.1 | 1316.1 | 113.4 | 116.6 | 561.7 | 462.9 | 386.4
1949.1 | 1317.1 | 113.5 | 116.7 | 555.3 | 461 | 386.6
1950.1 | 1318.1 | 113.7 | 116.9 | 549.8 | 459.7 | 386.8
1951.1 | 1319.1 | 113.9 | 117 | 544.6 | 458.4 | 386.9
1952.1 | 1320.1 | 114.1 | 117.1 | 539.7 | 457.4 | 387
1953.1 | 1321.1 | 114.2 | 117.3 | 535.3 | 455.7 | 387.1
1954.1 | 1322.1 | 114.4 | 117.5 | 531.4 | 455 | 387.3
1955.1 | 1323.1 | 114.6 | 117.6 | 528 | 454.4 | 387.6
1956.1 | 1324.1 | 114.7 | 117.8 | 524.8 | 452.7 | 387.7
1957.1 | 1325.1 | 114.9 | 117.9 | 523.4 | 459.7 | 388.1
1958.1 | 1326.1 | 115.1 | 118 | 528.2 | 466.1 | 391
1959.1 | 1327.1 | 115.3 | 118.2 | 533.7 | 464.5 | 390.7
1960.1 | 1328.1 | 115.4 | 118.4 | 534.2 | 462.7 | 390.5
1961.1 | 1329.1 | 115.6 | 118.5 | 533.4 | 465.3 | 391.1
1962.1 | 1330.1 | 115.8 | 118.6 | 532.3 | 464.4 | 391.5
1963.1 | 1331.1 | 116 | 118.8 | 538.7 | 463.8 | 391.5
1964.1 | 1332.1 | 116.1 | 118.9 | 548.2 | 467.2 | 392.4
1965.1 | 1333.1 | 116.3 | 119.1 | 557.6 | 468.6 | 393.3
1966.1 | 1334.1 | 116.5 | 119.2 | 558.8 | 467.3 | 393.5
1967.1 | 1335.1 | 116.6 | 119.4 | 556.4 | 465.3 | 395.5
1968.1 | 1336.1 | 116.8 | 119.5 | 553.8 | 464.1 | 396
1969.1 | 1337.1 | 117 | 119.6 | 553.9 | 464 | 396.1
1970.1 | 1338.1 | 117.2 | 119.8 | 555.9 | 463.9 | 396.3
1971.1 | 1339.1 | 117.3 | 120 | 559.6 | 464.6 | 396.6
1972.1 | 1340.1 | 117.5 | 120.1 | 559.7 | 466.7 | 396.9
1973.1 | 1341.1 | 117.7 | 120.2 | 559.2 | 466.6 | 397.1
1974.1 | 1342.1 | 117.9 | 120.4 | 562.4 | 464.3 | 396.9
1975.1 | 1343.1 | 118.1 | 120.5 | 558.6 | 462.4 | 396.7
1976.1 | 1344.1 | 118.3 | 120.6 | 555.4 | 460.5 | 396.5
1977.1 | 1345.1 | 118.4 | 120.8 | 551.5 | 460.4 | 396.5
1978.1 | 1346.1 | 118.6 | 120.9 | 548.4 | 460.9 | 396.8
1979.1 | 1347.1 | 118.8 | 121 | 544.9 | 461.3 | 397
1980.1 | 1348.1 | 118.9 | 121.2 | 544.4 | 462.9 | 397.3
1981.1 | 1349.1 | 119.1 | 121.3 | 541.8 | 462.4 | 397.6
1982.1 | 1350.1 | 119.3 | 121.5 | 537 | 459.4 | 397.6
1983.1 | 1351.1 | 119.4 | 121.6 | 532.1 | 458 | 397.5
1984.1 | 1352.1 | 119.6 | 121.8 | 529 | 457.5 | 397.5
1985.1 | 1353.1 | 119.8 | 121.9 | 527.5 | 458.2 | 397.8
1986.1 | 1354.1 | 120 | 122 | 525.9 | 458.3 | 398
1987.1 | 1355.1 | 120.1 | 122.2 | 524.3 | 458.6 | 398.2
1988.1 | 1356.1 | 120.2 | 122.3 | 523.5 | 459 | 398.4
1989.1 | 1357.1 | 120.4 | 122.5 | 522.2 | 459.2 | 398.6
1990.1 | 1358.1 | 120.6 | 122.6 | 520.4 | 458.2 | 398.7
1991.1 | 1359.1 | 120.7 | 122.8 | 518.7 | 457.1 | 398.7
1992.1 | 1360.1 | 120.9 | 122.9 | 516.6 | 456.3 | 398.7
1993.1 | 1361.1 | 121.1 | 123 | 514.6 | 455.5 | 398.8
1994.1 | 1362.1 | 121.2 | 123.2 | 513.6 | 456 | 398.9
1995.1 | 1363.1 | 121.4 | 123.3 | 513.7 | 458.8 | 399.5
1996.1 | 1364.1 | 121.5 | 123.5 | 517.7 | 461.2 | 400.2
1997.1 | 1365.1 | 121.7 | 123.6 | 525.7 | 465.8 | 400.9
1998.1 | 1366.1 | 121.8 | 123.8 | 532.7 | 467.9 | 401.5
1999.1 | 1367.1 | 122 | 123.9 | 538.8 | 465.8 | 401.5
2000.1 | 1368.1 | 122.2 | 124.1 | 538.9 | 464.2 | 401.5
2001.1 | 1369.1 | 122.4 | 124.2 | 538.2 | 464.6 | 401.6
2002.1 | 1370.1 | 122.5 | 124.4 | 547.4 | 475.5 | 402.3
2003.1 | 1371.1 | 122.7 | 124.5 | 558.8 | 478.7 | 403
2004.1 | 1372.1 | 122.9 | 124.6 | 562.7 | 479.3 | 403.6
2005.1 | 1373.1 | 123 | 124.8 | 562.6 | 478.6 | 403.6
2006.1 | 1374.1 | 123.1 | 125 | 558.4 | 476.7 | 403.6
2007.1 | 1375.1 | 123.3 | 125.1 | 555.2 | 474.4 | 403.6
2008.1 | 1376.1 | 123.5 | 125.3 | 551.6 | 473.4 | 403.7
2009.1 | 1377.1 | 123.6 | 125.5 | 548.8 | 472.6 | 403.9
2010.1 | 1378.1 | 123.8 | 125.6 | 546.2 | 471.6 | 404
2011.1 | 1379.1 | 124 | 125.8 | 542.6 | 470.8 | 404.2
2012.1 | 1380.1 | 124.1 | 126 | 539.9 | 469.7 | 404.4
2013.1 | 1381.1 | 124.3 | 126.1 | 537.1 | 468.1 | 404.4
2014.1 | 1382.1 | 124.4 | 126.3 | 536.7 | 468.4 | 404.7
2015.1 | 1383.1 | 124.6 | 126.5 | 536 | 469 | 405.1
2016.1 | 1384.1 | 124.7 | 126.7 | 534.5 | 469.2 | 405.3
2017.1 | 1385.1 | 124.9 | 126.8 | 534.2 | 469.8 | 405.8
2018.1 | 1386.1 | 125.1 | 127 | 532.1 | 468.3 | 405.9
2019.1 | 1387.1 | 125.2 | 127.2 | 529.4 | 466.2 | 405.7
2020.1 | 1388.1 | 125.4 | 127.3 | 525.6 | 464.3 | 405.6
2021.1 | 1389.1 | 125.6 | 127.5 | 521.6 | 461.5 | 405.6
2022.1 | 1390.1 | 125.7 | 127.7 | 518.1 | 459.6 | 405.5
2023.1 | 1391.1 | 125.8 | 127.9 | 516 | 459.3 | 405.7
2024.1 | 1392.1 | 126 | 128.1 | 514.9 | 460.6 | 406
2025.1 | 1393.1 | 126.2 | 128.2 | 513.9 | 461.4 | 406.4
2026.1 | 1394.1 | 126.3 | 128.4 | 512 | 460.1 | 406.2
2027.1 | 1395.1 | 126.5 | 128.6 | 509.3 | 458.2 | 406.1
2028.1 | 1396.1 | 126.6 | 128.8 | 508.7 | 457.6 | 406.2
2029.1 | 1397.1 | 126.8 | 129 | 507.4 | 456.3 | 406.2
2030.1 | 1398.1 | 126.9 | 129.2 | 506 | 455.7 | 406.2
2031.1 | 1399.1 | 127.1 | 129.4 | 505.4 | 454.9 | 406.2
2032.1 | 1400.1 | 127.3 | 129.5 | 505.7 | 456.8 | 406.5
2033.1 | 1401.1 | 127.4 | 129.8 | 509.8 | 460.6 | 407
2034.1 | 1402.1 | 127.6 | 130 | 515.7 | 467 | 407.7
2035.1 | 1403.1 | 127.8 | 130.1 | 517.1 | 466.9 | 407.9
2036.1 | 1404.1 | 127.9 | 130.3 | 518.2 | 468 | 408
2037.1 | 1405.1 | 128.1 | 130.6 | 518.1 | 468.2 | 408.2
2038.1 | 1406.1 | 128.2 | 130.8 | 517.8 | 468 | 408.4
2039.1 | 1407.1 | 128.4 | 131 | 516.4 | 467.4 | 408.3
2040.1 | 1408.1 | 128.5 | 131.2 | 514.8 | 467.1 | 408.6
2041.1 | 1409.1 | 128.7 | 131.4 | 515.8 | 467.4 | 408.9
2042.1 | 1410.1 | 128.9 | 131.6 | 514.5 | 466.8 | 409
2043.1 | 1411.1 | 129 | 131.7 | 514.8 | 466.9 | 409.2
2044.1 | 1412.1 | 129.2 | 132 | 513.1 | 465.3 | 409.1
2045.1 | 1413.1 | 129.3 | 132.2 | 512.4 | 464.6 | 409.1
2046.1 | 1414.1 | 129.5 | 132.3 | 510.6 | 462.8 | 409.1
2047.1 | 1415.1 | 129.7 | 132.6 | 509 | 461.3 | 408.9
2048.1 | 1416.1 | 129.8 | 132.8 | 508.3 | 460.3 | 408.8
2049.1 | 1417.1 | 130 | 133 | 508 | 459.6 | 409
2050.1 | 1418.1 | 130.1 | 133.2 | 507.8 | 459.2 | 409
2051.1 | 1419.1 | 130.3 | 133.4 | 508.4 | 459.6 | 409.4
2052.1 | 1420.1 | 130.5 | 133.6 | 508.4 | 459.6 | 409.5
2053.1 | 1421.1 | 130.6 | 133.9 | 508.8 | 460.3 | 409.6
2054.1 | 1422.1 | 130.8 | 134.1 | 508.3 | 460.3 | 409.7
2055.1 | 1423.1 | 130.9 | 134.3 | 506.9 | 459.2 | 409.6
2056.1 | 1424.1 | 131.1 | 134.5 | 504.6 | 457.6 | 409.5
2057.1 | 1425.1 | 131.3 | 134.7 | 503.2 | 457 | 409.5
2058.1 | 1426.1 | 131.4 | 135 | 503.6 | 457.6 | 409.7
2059.1 | 1427.1 | 131.6 | 135.2 | 503.1 | 457.2 | 409.9
2060.1 | 1428.1 | 131.7 | 135.4 | 504.1 | 458.1 | 410
2061.1 | 1429.1 | 131.9 | 135.7 | 506.2 | 460.3 | 410.2
2062.1 | 1430.1 | 132 | 135.9 | 507.2 | 461.2 | 410.4
2063.1 | 1431.1 | 132.2 | 136.1 | 507.6 | 463 | 410.7
2064.1 | 1432.1 | 132.4 | 136.4 | 508.3 | 463.1 | 410.7
2065.1 | 1433.1 | 132.5 | 136.7 | 509.5 | 463.9 | 410.8
2066.1 | 1434.1 | 132.7 | 136.9 | 512.2 | 466.7 | 411.2
2067.1 | 1435.1 | 132.8 | 137.2 | 513.6 | 467.3 | 411.6
2068.1 | 1436.1 | 133 | 137.4 | 513.7 | 466.4 | 411.4
2069.1 | 1437.1 | 133.1 | 137.7 | 512.3 | 465.2 | 411.3
2070.1 | 1438.1 | 133.3 | 138 | 511.8 | 464.6 | 411.4
2071.1 | 1439.1 | 133.4 | 138.2 | 511.4 | 464.4 | 411.6
2072.1 | 1440.1 | 133.6 | 138.5 | 511.3 | 464.1 | 411.7
2073.1 | 1441.1 | 133.8 | 138.7 | 514.6 | 466.9 | 412.2
2074.1 | 1442.1 | 133.9 | 139 | 516.8 | 469.1 | 412.6
2075.1 | 1443.1 | 134.1 | 139.3 | 518.9 | 470.2 | 413
2076.1 | 1444.1 | 134.2 | 139.5 | 518.4 | 469.5 | 413.1
2077.1 | 1445.1 | 134.4 | 139.8 | 517.8 | 469.2 | 413.2
2078.1 | 1446.1 | 134.5 | 140.1 | 517.1 | 468.2 | 413.1
2079.1 | 1447.1 | 134.7 | 140.4 | 515.3 | 465.9 | 413
2080.1 | 1448.1 | 134.9 | 140.6 | 514.9 | 467.3 | 413.2
2081.1 | 1449.1 | 135.1 | 140.8 | 515.8 | 468.6 | 413.9
2082.1 | 1450.1 | 135.2 | 141.2 | 514.8 | 468.4 | 414
2083.1 | 1451.1 | 135.4 | 141.5 | 512 | 465.9 | 413.9
2084.1 | 1452.1 | 135.6 | 141.7 | 508.5 | 463.4 | 413.7
2085.1 | 1453.1 | 135.7 | 142 | 506.1 | 461.6 | 413.5
2086.1 | 1454.1 | 135.9 | 142.3 | 504.6 | 461.3 | 413.6
2087.1 | 1455.1 | 136.1 | 142.6 | 504.2 | 462 | 413.9
2088.1 | 1456.1 | 136.3 | 142.9 | 504 | 460.2 | 414.1
2089.1 | 1457.1 | 136.4 | 143.1 | 504.1 | 459.3 | 413.9
2090.1 | 1458.1 | 136.6 | 143.4 | 504.5 | 458.3 | 413.8
2091.1 | 1459.1 | 136.8 | 143.7 | 504.1 | 457.2 | 413.6
2092.1 | 1460.1 | 137 | 144 | 504.2 | 457.3 | 413.6
2093.1 | 1461.1 | 137.2 | 144.3 | 505.2 | 458.3 | 413.7
2094.1 | 1462.1 | 137.4 | 144.6 | 508.1 | 462.3 | 414.3
2095.1 | 1463.1 | 137.6 | 144.9 | 510.1 | 463.8 | 414.8
2096.1 | 1464.1 | 137.8 | 145.2 | 512.1 | 464.6 | 415
2097.1 | 1465.1 | 138 | 145.5 | 512 | 464.6 | 415.2
2098.1 | 1466.1 | 138.2 | 145.8 | 510.5 | 463.9 | 415.2
2099.1 | 1467.1 | 138.4 | 146.1 | 509.9 | 464.1 | 415.3
2100.1 | 1468.1 | 138.6 | 146.4 | 508.5 | 464.1 | 415.3
2101.1 | 1469.1 | 138.8 | 146.7 | 508.1 | 463.9 | 415.4
2102.1 | 1470.1 | 139.1 | 147 | 508 | 463.7 | 415.4
2103.1 | 1471.1 | 139.3 | 147.3 | 509.1 | 463.8 | 415.5
2104.1 | 1472.1 | 139.5 | 147.6 | 508.9 | 463.7 | 415.8
2105.1 | 1473.1 | 139.7 | 147.9 | 509.2 | 463.9 | 415.9
2106.1 | 1474.1 | 140 | 148.2 | 510.2 | 465.2 | 416.1
2107.1 | 1475.1 | 140.1 | 148.6 | 510.5 | 466.2 | 416.3
2108.1 | 1476.1 | 140.4 | 148.9 | 513 | 470.2 | 416.7
2109.1 | 1477.1 | 140.6 | 149.2 | 512.9 | 470.3 | 416.9
2110.1 | 1478.1 | 140.8 | 149.5 | 514.1 | 473.1 | 417.2
2111.1 | 1479.1 | 141 | 149.8 | 515.2 | 472.9 | 417.3
2112.1 | 1480.1 | 141.3 | 150.1 | 515.8 | 473 | 417.5
2113.1 | 1481.1 | 141.5 | 150.4 | 515.3 | 471.9 | 417.6
2114.1 | 1482.1 | 141.7 | 150.7 | 514 | 471.1 | 417.5
2115.1 | 1483.1 | 142 | 151.1 | 513.6 | 470.7 | 417.7
2116.1 | 1484.1 | 142.2 | 151.3 | 514 | 470.5 | 418
2117.1 | 1485.1 | 142.5 | 151.7 | 514.8 | 470.3 | 418
2118.1 | 1486.1 | 142.7 | 152 | 515.4 | 470.3 | 418.1
2119.1 | 1487.1 | 142.9 | 152.3 | 515.6 | 470.1 | 418.3
2120.1 | 1488.1 | 143.2 | 152.6 | 515.1 | 470 | 418.4
2121.1 | 1489.1 | 143.4 | 153 | 514.5 | 469.5 | 418.4
2122.1 | 1490.1 | 143.6 | 153.3 | 515.3 | 470.2 | 418.6
2123.1 | 1491.1 | 143.9 | 153.6 | 516.4 | 470.6 | 418.8
2124.1 | 1492.1 | 144.1 | 153.9 | 516.5 | 470.9 | 418.8
2125.1 | 1493.1 | 144.3 | 154.3 | 516.8 | 471.7 | 419.1
2126.1 | 1494.1 | 144.6 | 154.6 | 516.6 | 471.7 | 419.2
2127.1 | 1495.1 | 144.8 | 154.9 | 516.7 | 471.2 | 419.2
2128.1 | 1496.1 | 145.1 | 155.3 | 515.3 | 470.5 | 419.1
2129.1 | 1497.1 | 145.3 | 155.6 | 515 | 470 | 419.2
2130.1 | 1498.1 | 145.5 | 155.9 | 515 | 468.6 | 419.3
2131.1 | 1499.1 | 145.8 | 156.3 | 514.9 | 468.6 | 419.4
2132.1 | 1500.1 | 146 | 156.6 | 514.9 | 468.6 | 419.6
2133.1 | 1501.1 | 146.3 | 157 | 515.4 | 468.1 | 419.6
2134.1 | 1502.1 | 146.5 | 157.3 | 516.1 | 468.2 | 419.7
2135.1 | 1503.1 | 146.7 | 157.6 | 516.1 | 467.8 | 419.7
2136.1 | 1504.1 | 147 | 158 | 516 | 466.8 | 419.6
2137.1 | 1505.1 | 147.2 | 158.3 | 514.7 | 465.7 | 419.4
2138.1 | 1506.1 | 147.5 | 158.6 | 513.5 | 464.9 | 419.3
2139.1 | 1507.1 | 147.7 | 159 | 511.5 | 463.6 | 419.1
2140.1 | 1508.1 | 148 | 159.3 | 509.8 | 462.6 | 419.1
2141.1 | 1509.1 | 148.2 | 159.6 | 509.4 | 463.8 | 419.3
2142.1 | 1510.1 | 148.4 | 160 | 511.6 | 465.9 | 419.7
2143.1 | 1511.1 | 148.7 | 160.3 | 513.6 | 466.6 | 419.7
2144.1 | 1512.1 | 149 | 160.6 | 515.6 | 470.2 | 420.2
2145.1 | 1513.1 | 149.2 | 161 | 519.4 | 474.7 | 421
2146.1 | 1514.1 | 149.4 | 161.3 | 523.7 | 481.9 | 421.3
2147.1 | 1515.1 | 149.7 | 161.7 | 526.8 | 484.2 | 421.8
2148.1 | 1516.1 | 150 | 162 | 526.2 | 483.2 | 422.2
2149.1 | 1517.1 | 150.2 | 162.3 | 523 | 480.3 | 421.9
2150.1 | 1518.1 | 150.4 | 162.7 | 521.3 | 479.3 | 421.9
2151.1 | 1519.1 | 150.7 | 163 | 521.5 | 479.3 | 422.2
2152.1 | 1520.1 | 150.9 | 163.3 | 522.5 | 478.6 | 422.3
2153.1 | 1521.1 | 151.2 | 163.6 | 521.4 | 477.5 | 422.3
2154.1 | 1522.1 | 151.5 | 163.9 | 520.3 | 476.1 | 422.3
2155.1 | 1523.1 | 151.7 | 164.2 | 517.9 | 473.8 | 422.1
2156.1 | 1524.1 | 151.9 | 164.6 | 517.3 | 473 | 422.2
2157.1 | 1525.1 | 152.2 | 164.9 | 517.2 | 471.7 | 422.2
2158.1 | 1526.1 | 152.5 | 165.2 | 516.5 | 470.7 | 422.2
2159.1 | 1527.1 | 152.7 | 165.6 | 517 | 471 | 422.3
2160.1 | 1528.1 | 153 | 165.9 | 519.1 | 472.4 | 422.5
2161.1 | 1529.1 | 153.2 | 166.2 | 520.9 | 473.1 | 422.7
2162.1 | 1530.1 | 153.5 | 166.5 | 525.1 | 480.4 | 423.3
2163.1 | 1531.1 | 153.7 | 166.8 | 529.1 | 485.2 | 423.9
2164.1 | 1532.1 | 154 | 167.2 | 530.6 | 484.7 | 424.2
2165.1 | 1533.1 | 154.3 | 167.5 | 533.3 | 486.4 | 424.6
2166.1 | 1534.1 | 154.5 | 167.8 | 536.1 | 490.6 | 425.4
2167.1 | 1535.1 | 154.8 | 168.1 | 535.8 | 489.5 | 425.5
2168.1 | 1536.1 | 155 | 168.4 | 536.8 | 490 | 425.8
2169.1 | 1537.1 | 155.3 | 168.7 | 535.6 | 490.6 | 425.9
2170.1 | 1538.1 | 155.5 | 169.1 | 537.7 | 491.7 | 426.3
2171.1 | 1539.1 | 155.8 | 169.4 | 537 | 491.6 | 426.6
2172.1 | 1540.1 | 156.1 | 169.7 | 536.3 | 490.4 | 426.7
2173.1 | 1541.1 | 156.3 | 170 | 536.3 | 490.7 | 426.8
2174.1 | 1542.1 | 156.5 | 170.3 | 539 | 494.2 | 427.3
2175.1 | 1543.1 | 156.8 | 170.6 | 538.5 | 493.9 | 427.6
2176.1 | 1544.1 | 157.1 | 170.9 | 538 | 493.3 | 427.8
2177.1 | 1545.1 | 157.3 | 171.3 | 537.7 | 493.9 | 428.2
2178.1 | 1546.1 | 157.6 | 171.5 | 537.1 | 492.6 | 428.6
2179.1 | 1547.1 | 157.9 | 171.8 | 535.5 | 488.8 | 428.5
2180.1 | 1548.1 | 158.1 | 172.1 | 539.9 | 492.4 | 428.7
2181.1 | 1549.1 | 158.4 | 172.5 | 554.2 | 497.4 | 429.6
2182.1 | 1550.1 | 158.6 | 172.7 | 574.1 | 505.2 | 431.1
2183.1 | 1551.1 | 158.9 | 173 | 575.6 | 505 | 431.4
2184.1 | 1552.1 | 159.2 | 173.3 | 577.5 | 508.7 | 431.9
2185.1 | 1553.1 | 159.4 | 173.6 | 578.9 | 510.2 | 432.6
2186.1 | 1554.1 | 159.7 | 173.9 | 578.5 | 511 | 433.6
2187.1 | 1555.1 | 160 | 174.2 | 575.8 | 509 | 433.7
2188.1 | 1556.1 | 160.2 | 174.6 | 574.5 | 507.7 | 433.8
2189.1 | 1557.1 | 160.5 | 174.8 | 572.2 | 506 | 434.2
2190.1 | 1558.1 | 160.8 | 175.1 | 569 | 504 | 434.3
2191.1 | 1559.1 | 161 | 175.4 | 565.9 | 503.3 | 434.6
2192.1 | 1560.1 | 161.3 | 175.7 | 563.6 | 501.9 | 434.8
2193.1 | 1561.1 | 161.9 | 175.7 | 563.1 | 501.3 | 435.3
2194.1 | 1562.1 | 161.9 | 176.3 | 563 | 499.6 | 435
2195.1 | 1563.1 | 162.3 | 176.4 | 560.6 | 498 | 435.2
2196.1 | 1564.1 | 162.5 | 176.8 | 558.2 | 496.6 | 435.2
2197.1 | 1565.1 | 162.7 | 177.2 | 555.3 | 495 | 435.3
2198.1 | 1566.1 | 162.9 | 177.5 | 553.1 | 493.4 | 435.4
2199.1 | 1567.1 | 163.2 | 177.8 | 552.5 | 493.3 | 435.6
2200.1 | 1568.1 | 163.5 | 178 | 550.8 | 491.3 | 435.8
2201.1 | 1569.1 | 163.7 | 178.3 | 547.8 | 490.6 | 435.6
2202.1 | 1570.1 | 164 | 178.6 | 548.1 | 490.8 | 435.8
2203.1 | 1571.1 | 164.3 | 178.9 | 550.5 | 491.1 | 436.1
2204.1 | 1572.1 | 164.6 | 179.2 | 549.2 | 489.8 | 435.9
2205.1 | 1573.1 | 164.8 | 179.5 | 547.9 | 490.1 | 435.9
2206.1 | 1574.1 | 165.1 | 179.8 | 545.2 | 489.5 | 435.9
2207.1 | 1575.1 | 165.4 | 180.1 | 542.2 | 487.4 | 435.8
2208.1 | 1576.1 | 165.6 | 180.4 | 539.5 | 486.3 | 435.7
2209.1 | 1577.1 | 165.9 | 180.7 | 538.9 | 487.4 | 436
2210.1 | 1578.1 | 166.2 | 180.9 | 539.7 | 488.2 | 436.4
2211.1 | 1579.1 | 166.5 | 181.2 | 539.5 | 487.7 | 436.5
2212.1 | 1580.1 | 166.7 | 181.6 | 540.9 | 488.2 | 436.7
2213.1 | 1581.1 | 167 | 181.9 | 541.9 | 491.2 | 437.5
2214.1 | 1582.1 | 167.3 | 182.1 | 542.8 | 492.1 | 437.8
2215.1 | 1583.1 | 167.6 | 182.5 | 546 | 495.2 | 438.2
2216.1 | 1584.1 | 167.8 | 182.8 | 551.8 | 498.9 | 438.9
2217.1 | 1585.1 | 168.1 | 183.1 | 552.6 | 499.4 | 439.5
2218.1 | 1586.1 | 168.4 | 183.4 | 552.2 | 498.6 | 439.6
2219.1 | 1587.1 | 168.7 | 183.7 | 550.6 | 496.9 | 439.5
2220.1 | 1588.1 | 168.9 | 184 | 553.8 | 498.6 | 440
2221.1 | 1589.1 | 169.2 | 184.3 | 556.1 | 498 | 440.2
2222.1 | 1590.1 | 169.5 | 184.6 | 552.9 | 495.6 | 440
2223.1 | 1591.1 | 169.8 | 184.9 | 548.8 | 493.2 | 439.8
2224.1 | 1592.1 | 170 | 185.2 | 547.5 | 493.4 | 439.9
2225.1 | 1593.1 | 170.3 | 185.6 | 546.4 | 492.5 | 439.8
2226.1 | 1594.1 | 170.6 | 185.9 | 545.6 | 493.3 | 440.1
2227.1 | 1595.1 | 170.8 | 186.2 | 545.3 | 494.5 | 440.4
2228.1 | 1596.1 | 171.1 | 186.5 | 548.1 | 497.5 | 440.9
2229.1 | 1597.1 | 171.4 | 186.8 | 546.3 | 494.8 | 440.7
2230.1 | 1598.1 | 171.7 | 187.2 | 544.8 | 493.1 | 440.4
2231.1 | 1599.1 | 172 | 187.5 | 543.9 | 492 | 440.3
2232.1 | 1600.1 | 172.3 | 187.8 | 542.4 | 490.4 | 440.2
2233.1 | 1601.1 | 172.6 | 188.1 | 540.4 | 489.3 | 440.2
2234.1 | 1602.1 | 172.9 | 188.4 | 541.1 | 488.9 | 440.2
2235.1 | 1603.1 | 173.2 | 188.7 | 543.1 | 490.4 | 440.4
2236.1 | 1604.1 | 173.4 | 189 | 547.1 | 493.9 | 440.6
2237.1 | 1605.1 | 173.7 | 189.4 | 548.6 | 494.4 | 440.9
2238.1 | 1606.1 | 174 | 189.6 | 548.2 | 494.1 | 440.8
2239.1 | 1607.1 | 174.3 | 190 | 549.5 | 496 | 441.3
2240.1 | 1608.1 | 174.6 | 190.3 | 554.3 | 496.5 | 442.1
2241.1 | 1609.1 | 174.9 | 190.6 | 554.1 | 495.1 | 441.8
2242.1 | 1610.1 | 175.2 | 190.9 | 552.5 | 494.3 | 441.8
2243.1 | 1611.1 | 175.4 | 191.2 | 552 | 494.3 | 442
2244.1 | 1612.1 | 175.7 | 191.5 | 550.6 | 493 | 442
2245.1 | 1613.1 | 176 | 191.8 | 552.1 | 495.2 | 442.4
2246.1 | 1614.1 | 176.3 | 192.1 | 553.2 | 496.9 | 442.9
2247.1 | 1615.1 | 176.5 | 192.4 | 551.9 | 496.4 | 442.9
2248.1 | 1616.1 | 176.8 | 192.7 | 554.4 | 499.1 | 443.4
2249.1 | 1617.1 | 177.1 | 193 | 557.2 | 499.1 | 443.9
2250.1 | 1618.1 | 177.4 | 193.3 | 555.3 | 497.2 | 443.7
2251.1 | 1619.1 | 177.7 | 193.6 | 553 | 496 | 443.5
2252.1 | 1620.1 | 178 | 193.9 | 551.1 | 495.8 | 443.5
2253.1 | 1621.1 | 178.2 | 194.2 | 550 | 495.8 | 443.8
2254.1 | 1622.1 | 178.5 | 194.5 | 552.1 | 495.6 | 444
2255.1 | 1623.1 | 178.8 | 194.8 | 552.6 | 495.6 | 444
2256.1 | 1624.1 | 179.2 | 195.1 | 552.9 | 491.4 | 443.7
2257.1 | 1625.1 | 179.4 | 195.4 | 549.6 | 488.1 | 443.3
2258.1 | 1626.1 | 179.7 | 195.7 | 545.4 | 490.8 | 443.8
2259.1 | 1627.1 | 180 | 196 | 542.7 | 496.6 | 448.2
2260.1 | 1628.1 | 180.3 | 196.3 | 543 | 495.1 | 447.5
2261.1 | 1629.1 | 180.5 | 196.6 | 541.5 | 492.1 | 446.6
2262.1 | 1630.1 | 180.8 | 196.9 | 539.7 | 490.9 | 446.3
2263.1 | 1631.1 | 181.2 | 197.2 | 538.5 | 489.7 | 446.3
2264.1 | 1632.1 | 181.4 | 197.5 | 537 | 486.9 | 446.1
2265.1 | 1633.1 | 181.7 | 197.8 | 536.8 | 484.4 | 446
2266.1 | 1634.1 | 182 | 198 | 536.1 | 481.7 | 445.6
2267.1 | 1635.1 | 182.3 | 198.3 | 535.9 | 481.7 | 445.4
2268.1 | 1636.1 | 182.6 | 198.6 | 537.9 | 482.6 | 445.3
2269.1 | 1637.1 | 182.9 | 198.9 | 540.9 | 483.4 | 445.3
2270.1 | 1638.1 | 183.2 | 199.2 | 543.2 | 483.5 | 445.3
2271.1 | 1639.1 | 183.5 | 199.5 | 545.7 | 483.3 | 445.3
2272.1 | 1640.1 | 183.8 | 199.9 | 546.5 | 483.7 | 445.2
2273.1 | 1641.1 | 184.1 | 200.2 | 546.7 | 483.8 | 445.1
2274.1 | 1642.1 | 184.4 | 200.5 | 546.1 | 484.7 | 445.2
2275.1 | 1643.1 | 184.7 | 200.8 | 547 | 486.2 | 445.3
2276.1 | 1644.1 | 184.9 | 201.1 | 548.8 | 487.5 | 445.5
2277.1 | 1645.1 | 185.3 | 201.3 | 547.2 | 487 | 445.6
2278.1 | 1646.1 | 185.5 | 201.7 | 546.4 | 486.6 | 445.5
2279.1 | 1647.1 | 185.8 | 202 | 544.9 | 485.5 | 445.5
2280.1 | 1648.1 | 186.1 | 202.3 | 543.7 | 485.7 | 445.5
2281.1 | 1649.1 | 186.3 | 202.6 | 543.6 | 485.2 | 445.5
2282.1 | 1650.1 | 186.6 | 202.9 | 542.9 | 484.3 | 445.4
2283.1 | 1651.1 | 186.9 | 203.2 | 541.4 | 483.7 | 445.4
2284.1 | 1652.1 | 187.2 | 203.5 | 539.7 | 483.6 | 445.4
2285.1 | 1653.1 | 187.5 | 203.8 | 538.9 | 481.9 | 445.2
2286.1 | 1654.1 | 187.7 | 204.1 | 538.3 | 481.5 | 445.2
2287.1 | 1655.1 | 188 | 204.4 | 539.3 | 481.7 | 445.3
2288.1 | 1656.1 | 188.4 | 204.7 | 539.4 | 481.7 | 445.3
2289.1 | 1657.1 | 188.6 | 205 | 539.8 | 483 | 445.2
2290.1 | 1658.1 | 188.9 | 205.3 | 539.3 | 483 | 445.2
2291.1 | 1659.1 | 189.2 | 205.6 | 537.2 | 481.4 | 444.9
2292.1 | 1660.1 | 189.5 | 205.9 | 534.9 | 479.8 | 444.6
2293.1 | 1661.1 | 189.8 | 206.2 | 535.2 | 480.9 | 444.4
2294.1 | 1662.1 | 190.1 | 206.5 | 538.3 | 482.9 | 444.7
2295.1 | 1663.1 | 190.4 | 206.9 | 541 | 483.7 | 444.8
2296.1 | 1664.1 | 190.7 | 207.2 | 542.5 | 485.2 | 444.9
2297.1 | 1665.1 | 190.9 | 207.5 | 545.9 | 487.4 | 445.1
2298.1 | 1666.1 | 191.2 | 207.7 | 545.9 | 488 | 445.3
2299.1 | 1667.1 | 191.5 | 208.1 | 545.2 | 488.4 | 445.4
2300.1 | 1668.1 | 191.8 | 208.4 | 543.4 | 486.8 | 445.5
2301.1 | 1669.1 | 192.4 | 208.3 | 541.5 | 485 | 445.8
2302.1 | 1670.1 | 192.3 | 209 | 540 | 484 | 445.2
2303.1 | 1671.1 | 192.6 | 209.3 | 539.1 | 485.6 | 445.3
2304.1 | 1672.1 | 192.9 | 209.6 | 541.4 | 487.3 | 445.3
2305.1 | 1673.1 | 193.2 | 209.9 | 542.1 | 487.5 | 445.3
2306.1 | 1674.1 | 193.5 | 210.2 | 542.5 | 487.9 | 445.4
2307.1 | 1675.1 | 193.8 | 210.5 | 542.9 | 487.9 | 445.5
2308.1 | 1676.1 | 194 | 210.8 | 542.5 | 487.4 | 445.6
2309.1 | 1677.1 | 194.3 | 211.1 | 544 | 487.2 | 445.7
2310.1 | 1678.1 | 194.6 | 211.4 | 542.8 | 485 | 445.3
2311.1 | 1679.1 | 194.9 | 211.7 | 539.8 | 483.2 | 445.1
2312.1 | 1680.1 | 195.2 | 212 | 537.7 | 482 | 445.1
2313.1 | 1681.1 | 195.4 | 212.3 | 536.2 | 482.1 | 445.1
2314.1 | 1682.1 | 195.7 | 212.6 | 536.4 | 482.6 | 445.1
2315.1 | 1683.1 | 196 | 212.9 | 538.5 | 483.2 | 445.2
2316.1 | 1684.1 | 196.3 | 213.2 | 540.5 | 483.7 | 445.3
2317.1 | 1685.1 | 196.6 | 213.5 | 541.3 | 484.6 | 445.2
2318.1 | 1686.1 | 196.9 | 213.8 | 541.7 | 485.7 | 445.3
2319.1 | 1687.1 | 197.2 | 214.1 | 539.7 | 484.2 | 445.3
2320.1 | 1688.1 | 197.4 | 214.4 | 536 | 482.4 | 445.2
2321.1 | 1689.1 | 197.7 | 214.7 | 534.9 | 481.7 | 445.2
2322.1 | 1690.1 | 198 | 214.9 | 535.8 | 482.5 | 445.4
2323.1 | 1691.1 | 198.3 | 215.3 | 539 | 485.9 | 446
2324.1 | 1692.1 | 198.6 | 215.6 | 543.1 | 487.3 | 446.4
2325.1 | 1693.1 | 198.8 | 215.9 | 544.2 | 489.4 | 446.7
2326.1 | 1694.1 | 199.1 | 216.1 | 542 | 488.1 | 446.6
2327.1 | 1695.1 | 199.4 | 216.5 | 543.2 | 488.2 | 446.8
2328.1 | 1696.1 | 199.7 | 216.8 | 545.8 | 488.8 | 447
2329.1 | 1697.1 | 200 | 217 | 546 | 488.4 | 447
2330.1 | 1698.1 | 200.3 | 217.3 | 547.6 | 489.3 | 447.2
2331.1 | 1699.1 | 200.5 | 217.6 | 549.3 | 490 | 447.6
2332.1 | 1700.1 | 200.8 | 217.9 | 549.9 | 491.7 | 448
2333.1 | 1701.1 | 201.1 | 218.1 | 552.1 | 494 | 448.4
2334.1 | 1702.1 | 201.4 | 218.4 | 552.6 | 493.5 | 448.4
2335.1 | 1703.1 | 201.7 | 218.7 | 554.9 | 494.8 | 448.5
2336.1 | 1704.1 | 201.9 | 219 | 555.8 | 495 | 449.1
2337.1 | 1705.1 | 202.2 | 219.3 | 555.4 | 495 | 448.9
2338.1 | 1706.1 | 202.5 | 219.6 | 555.2 | 493.8 | 448.8
2339.1 | 1707.1 | 202.8 | 219.8 | 553.6 | 492.3 | 448.6
2340.1 | 1708.1 | 203.1 | 220.1 | 551 | 491.1 | 448.9
2341.1 | 1709.1 | 203.3 | 220.4 | 548.2 | 489.6 | 449.2
2342.1 | 1710.1 | 203.6 | 220.7 | 547.1 | 490.6 | 449.9
2343.1 | 1711.1 | 203.9 | 220.9 | 545.4 | 490.5 | 450.2
2344.1 | 1712.1 | 204.2 | 221.2 | 545.8 | 492.3 | 450.8
2345.1 | 1713.1 | 204.4 | 221.5 | 547.7 | 492.9 | 450.6
2346.1 | 1714.1 | 204.7 | 221.8 | 547 | 492.3 | 450.6
2347.1 | 1715.1 | 205 | 222.1 | 550.9 | 494 | 450.8
2348.1 | 1716.1 | 205.3 | 222.4 | 553 | 495.1 | 450.9
2349.1 | 1717.1 | 205.6 | 222.7 | 553.9 | 499.9 | 451.1
2350.1 | 1718.1 | 205.9 | 223 | 554.1 | 500.7 | 451.2
2351.1 | 1719.1 | 206.2 | 223.3 | 554.2 | 499.4 | 451.3
2352.1 | 1720.1 | 206.4 | 223.7 | 555.7 | 498.5 | 451.2
2353.1 | 1721.1 | 206.7 | 224 | 554.2 | 496.9 | 451.2
2354.1 | 1722.1 | 207 | 224.3 | 551.9 | 495.1 | 451.3
2355.1 | 1723.1 | 207.2 | 224.6 | 551.5 | 494.9 | 451.6
2356.1 | 1724.1 | 207.5 | 224.9 | 553.1 | 493.4 | 451.4
2357.1 | 1725.1 | 207.9 | 225.3 | 551.4 | 491.2 | 451
2358.1 | 1726.1 | 208.1 | 225.6 | 546.8 | 487.2 | 450.6
2359.1 | 1727.1 | 208.4 | 226 | 544.6 | 491.9 | 450.6
2360.1 | 1728.1 | 208.6 | 226.3 | 546.5 | 493.3 | 451
2361.1 | 1729.1 | 208.9 | 226.6 | 546.6 | 493.6 | 450.9
2362.1 | 1730.1 | 209.2 | 227 | 545.9 | 493.2 | 450.8
2363.1 | 1731.1 | 209.4 | 227.3 | 547 | 497.4 | 450.8
2364.1 | 1732.1 | 209.8 | 227.7 | 547.7 | 497.2 | 450.7
2365.1 | 1733.1 | 210 | 228.1 | 547.6 | 497.8 | 450.9
2366.1 | 1734.1 | 210.3 | 228.4 | 550.4 | 501.9 | 451.3
2367.1 | 1735.1 | 210.6 | 228.8 | 555.1 | 505.9 | 451.8
2368.1 | 1736.1 | 210.9 | 229.2 | 560 | 504.9 | 451.9
2369.1 | 1737.1 | 211.1 | 229.5 | 564.8 | 504.6 | 451.9
2370.1 | 1738.1 | 211.4 | 229.9 | 568.2 | 503.3 | 452
2371.1 | 1739.1 | 211.6 | 230.3 | 568 | 503 | 452.8
2372.1 | 1740.1 | 211.9 | 230.6 | 571 | 507.5 | 455.9
2373.1 | 1741.1 | 212.1 | 231 | 571.3 | 504.9 | 455.2
2374.1 | 1742.1 | 212.4 | 231.3 | 570 | 503.8 | 455
2375.1 | 1743.1 | 212.7 | 231.6 | 568.1 | 504.1 | 456.4
2376.1 | 1744.1 | 212.9 | 232 | 567 | 502.8 | 456.5
2377.1 | 1745.1 | 213.3 | 232.4 | 566.6 | 502.1 | 456.1
2378.1 | 1746.1 | 213.5 | 232.7 | 565.8 | 501.4 | 456
2379.1 | 1747.1 | 213.8 | 233 | 564 | 500.2 | 455.8
2380.1 | 1748.1 | 214.1 | 233.4 | 563.1 | 499.5 | 456.3
2381.1 | 1749.1 | 214.4 | 233.8 | 561.5 | 500 | 456.9
2382.1 | 1750.1 | 214.7 | 234.1 | 561.9 | 498.3 | 456.9
2383.1 | 1751.1 | 215 | 234.4 | 562 | 495.1 | 456.4
2384.1 | 1752.1 | 215.3 | 234.8 | 560.2 | 490.5 | 455.7
2385.1 | 1753.1 | 215.6 | 235 | 556.3 | 486.9 | 455.7
2386.1 | 1754.1 | 215.8 | 235.4 | 558.3 | 490.2 | 459
2387.1 | 1755.1 | 216 | 235.7 | 558.1 | 488.1 | 458.7
2388.1 | 1756.1 | 216.3 | 236.1 | 559.1 | 487.6 | 458.3
2389.1 | 1757.1 | 216.6 | 236.6 | 557 | 486.5 | 459.7
2390.1 | 1758.1 | 216.8 | 237.2 | 553.3 | 485.8 | 459.8
2391.1 | 1759.1 | 217.1 | 237.8 | 549 | 485.2 | 459
2392.1 | 1760.1 | 217.3 | 238.3 | 549.2 | 486.2 | 458.9
2393.1 | 1761.1 | 217.6 | 238.9 | 550.4 | 485.7 | 458.6
2394.1 | 1762.1 | 217.9 | 239.4 | 549 | 485.9 | 458.3
2395.1 | 1763.1 | 218.1 | 239.9 | 550.1 | 487.7 | 458.9
2396.1 | 1764.1 | 218.4 | 240.3 | 551.5 | 487.1 | 458.8
2397.1 | 1765.1 | 218.6 | 240.7 | 552.7 | 488.9 | 458.6
2398.1 | 1766.1 | 218.9 | 241.1 | 554.2 | 493.6 | 458.7
2399.1 | 1767.1 | 219.2 | 241.5 | 554.2 | 494.2 | 459
2400.1 | 1768.1 | 219.4 | 241.8 | 555.8 | 496.2 | 459.7
2401.1 | 1769.1 | 219.7 | 242.2 | 557.8 | 497.2 | 459.4
2402.1 | 1770.1 | 219.9 | 242.5 | 556.9 | 497.5 | 459.3
2403.1 | 1771.1 | 220.2 | 242.9 | 558.1 | 499 | 459.7
2404.1 | 1772.1 | 220.4 | 243.2 | 560.6 | 497.4 | 459.4
2405.1 | 1773.1 | 220.7 | 243.6 | 560.1 | 497 | 459.5
2406.1 | 1774.1 | 221 | 243.8 | 563.2 | 504.4 | 460.7
2407.1 | 1775.1 | 221.2 | 244.2 | 565.9 | 507.8 | 462.9
2408.1 | 1776.1 | 221.5 | 244.5 | 564.8 | 507.2 | 463
2409.1 | 1777.1 | 221.8 | 244.8 | 564.1 | 507 | 463.6
2410.1 | 1778.1 | 222 | 245.1 | 568 | 507.9 | 464.2
2411.1 | 1779.1 | 222.3 | 245.5 | 569.8 | 505.7 | 464.1
2412.1 | 1780.1 | 222.6 | 245.8 | 566.1 | 502.7 | 463.3
2413.1 | 1781.1 | 222.9 | 246.2 | 565.8 | 501 | 462.8
2414.1 | 1782.1 | 223.1 | 246.5 | 566.5 | 499.1 | 462.5
2415.1 | 1783.1 | 223.4 | 246.8 | 567.7 | 497.4 | 462
2416.1 | 1784.1 | 223.6 | 247.1 | 570.3 | 496.1 | 461.7
2417.1 | 1785.1 | 223.9 | 247.4 | 571.8 | 497.2 | 461.6
2418.1 | 1786.1 | 224.1 | 247.7 | 572.9 | 499.8 | 462.3
2419.1 | 1787.1 | 224.4 | 248 | 571.4 | 499.2 | 462.2
2420.1 | 1788.1 | 224.7 | 248.4 | 570.3 | 498.7 | 462
2421.1 | 1789.1 | 225 | 248.7 | 569.3 | 498.6 | 462
2422.1 | 1790.1 | 225.3 | 249 | 566.9 | 497.7 | 461.8
2423.1 | 1791.1 | 225.5 | 249.3 | 566.2 | 507.8 | 463.4
2424.1 | 1792.1 | 225.8 | 249.7 | 566.7 | 511.9 | 465.7
2425.1 | 1793.1 | 226 | 250.1 | 569.1 | 509.6 | 465.2
2426.1 | 1794.1 | 226.3 | 250.4 | 567.7 | 509.7 | 465
2427.1 | 1795.1 | 226.5 | 250.8 | 572.7 | 508.4 | 464.9
2428.1 | 1796.1 | 226.9 | 251.1 | 572.5 | 508 | 464.9
2429.1 | 1797.1 | 227.1 | 251.4 | 571.3 | 508.2 | 465.1
2430.1 | 1798.1 | 227.4 | 251.6 | 569 | 506.4 | 464.9
2431.1 | 1799.1 | 227.7 | 251.9 | 567.6 | 505.4 | 464.8
2432.1 | 1800.1 | 227.9 | 252.1 | 571.6 | 505.6 | 464.6
2433.1 | 1801.1 | 228.1 | 252.3 | 569.6 | 500.2 | 464.2
2434.1 | 1802.1 | 228.4 | 252.5 | 568.9 | 495.5 | 463.4
2435.1 | 1803.1 | 228.7 | 252.7 | 565.8 | 493.6 | 464.1
2436.1 | 1804.1 | 228.9 | 252.9 | 565.3 | 500.5 | 467.6
2437.1 | 1805.1 | 229.2 | 253.1 | 567.1 | 500.3 | 467.6
2438.1 | 1806.1 | 229.5 | 253.3 | 567.8 | 502.8 | 469
2439.1 | 1807.1 | 229.8 | 253.5 | 580.4 | 512 | 470.8
2440.1 | 1808.1 | 230 | 253.7 | 585.3 | 514.1 | 472.5
2441.1 | 1809.1 | 230.3 | 253.9 | 585.3 | 514.2 | 471.7
2442.1 | 1810.1 | 230.6 | 254 | 587.8 | 514.6 | 471.7
2443.1 | 1811.1 | 230.9 | 254.2 | 590.3 | 514.4 | 471.7
2444.1 | 1812.1 | 231.2 | 254.3 | 588.9 | 512.8 | 471
2445.1 | 1813.1 | 231.6 | 254.3 | 587 | 509.9 | 470.5
2446.1 | 1814.1 | 231.9 | 254.5 | 583.4 | 506.5 | 471.1
2447.1 | 1815.1 | 232.1 | 254.6 | 580.9 | 512.7 | 474.6
2448.1 | 1816.1 | 232.4 | 254.7 | 580.5 | 511.5 | 473.7
2449.1 | 1817.1 | 232.7 | 254.9 | 585 | 517.7 | 474.8
2450.1 | 1818.1 | 233 | 255 | 583.6 | 516.7 | 474.4
2451.1 | 1819.1 | 233.1 | 255.1 | 589.3 | 529.6 | 475.3
2452.1 | 1820.1 | 233.5 | 255.2 | 587.8 | 527.3 | 475.4
2453.1 | 1821.1 | 233.7 | 255.3 | 587.9 | 526.8 | 475.1
2454.1 | 1822.1 | 233.9 | 255.3 | 588.5 | 525.3 | 474.9
2455.1 | 1823.1 | 234.2 | 255.4 | 589.7 | 521.5 | 474.2
2456.1 | 1824.1 | 234.4 | 255.4 | 589.7 | 522.7 | 473.7
2457.1 | 1825.1 | 234.7 | 255.4 | 588.2 | 523.5 | 473.7
2458.1 | 1826.1 | 234.9 | 255.5 | 585 | 520.4 | 473.2
2459.1 | 1827.1 | 235.2 | 255.6 | 582.8 | 528.7 | 473.7
2460.1 | 1828.1 | 235.4 | 255.7 | 581.7 | 527 | 473.5
2461.1 | 1829.1 | 235.7 | 255.8 | 580 | 528.7 | 473
2462.1 | 1830.1 | 235.9 | 256 | 585.6 | 531.6 | 472.8
2463.1 | 1831.1 | 236.3 | 256.2 | 586.3 | 530.6 | 472.7
2464.1 | 1832.1 | 236.6 | 256.5 | 584.7 | 526.7 | 472.8
2465.1 | 1833.1 | 236.9 | 256.6 | 583.6 | 532 | 473.5
2466.1 | 1834.1 | 237.1 | 256.6 | 582.4 | 530.1 | 473.3
2467.1 | 1835.1 | 237.3 | 256.7 | 579 | 526.5 | 472.5
2468.1 | 1836.1 | 237.6 | 256.8 | 578.8 | 522.9 | 471.7
2469.1 | 1837.1 | 237.9 | 257 | 577.1 | 520 | 471.2
2470.1 | 1838.1 | 238.1 | 257.1 | 576.1 | 525.1 | 471.3
2471.1 | 1839.1 | 238.3 | 257.2 | 577.7 | 526.6 | 471.8
2472.1 | 1840.1 | 238.6 | 257.3 | 575.9 | 523.4 | 471.2
2473.1 | 1841.1 | 238.9 | 257.4 | 576.6 | 522.6 | 471.1
2474.1 | 1842.1 | 239 | 257.6 | 575.6 | 521.7 | 470.8
2475.1 | 1843.1 | 239.4 | 257.8 | 576.6 | 530.5 | 472.5
2476.1 | 1844.1 | 240.3 | 257.4 | 573.5 | 527.2 | 472.9
2477.1 | 1845.1 | 239.9 | 258.3 | 571.8 | 528.6 | 473.2
2478.1 | 1846.1 | 240.2 | 258.4 | 571.1 | 532.8 | 474.2
2479.1 | 1847.1 | 240.6 | 258.5 | 568.8 | 529.9 | 474
2480.1 | 1848.1 | 240.7 | 258.8 | 570.4 | 530.6 | 475.6
2481.1 | 1849.1 | 240.9 | 259 | 570.8 | 529.5 | 475.9
2482.1 | 1850.1 | 241.3 | 259.2 | 573.4 | 531.4 | 476.1
2483.1 | 1851.1 | 241.6 | 259.3 | 576.4 | 531.8 | 476.4
2484.1 | 1852.1 | 241.8 | 259.5 | 577.5 | 531.5 | 476.1
2485.1 | 1853.1 | 242 | 259.6 | 578.3 | 531.3 | 476.2
2486.1 | 1854.1 | 242.2 | 259.8 | 579.3 | 530.5 | 476.3
2487.1 | 1855.1 | 242.5 | 260 | 578.1 | 530.1 | 476.5
2488.1 | 1856.1 | 242.7 | 260.1 | 578.2 | 530 | 476.8
2489.1 | 1857.1 | 243 | 260.3 | 577.7 | 529.6 | 476.5
2490.1 | 1858.1 | 243.3 | 260.5 | 580.9 | 527.1 | 476.4
2491.1 | 1859.1 | 243.5 | 260.6 | 581.2 | 539.1 | 477.8
2492.1 | 1860.1 | 243.7 | 260.7 | 584.5 | 539.2 | 478.8
2493.1 | 1861.1 | 243.9 | 260.9 | 585.7 | 537.9 | 478.7
2494.1 | 1862.1 | 244.3 | 261 | 585.9 | 537.5 | 478.9
2495.1 | 1863.1 | 244.5 | 261.2 | 586.3 | 536.1 | 479.4
2496.1 | 1864.1 | 244.8 | 261.4 | 583.4 | 535.2 | 481
2497.1 | 1865.1 | 245 | 261.6 | 582.9 | 531.4 | 480.1
2498.1 | 1866.1 | 245.3 | 261.8 | 582.9 | 530.6 | 480.3
2499.1 | 1867.1 | 245.5 | 262.1 | 580.8 | 530.6 | 480.4
2500.1 | 1868.1 | 245.8 | 262.3 | 580.6 | 529.7 | 480.4
2501.1 | 1869.1 | 246.1 | 262.6 | 581.4 | 526.7 | 480.4
2502.1 | 1870.1 | 246.4 | 262.9 | 590 | 528.7 | 483
2503.1 | 1871.1 | 246.6 | 263.3 | 589.8 | 528.3 | 482.8
2504.1 | 1872.1 | 247 | 263.6 | 589 | 530.7 | 483.2
2505.1 | 1873.1 | 247.1 | 263.9 | 590.1 | 543.6 | 484.6
2506.1 | 1874.1 | 247.4 | 264.3 | 590.1 | 541.2 | 483.7
2507.1 | 1875.1 | 247.6 | 264.5 | 592.1 | 541.6 | 483.4
2508.1 | 1876.1 | 247.9 | 264.6 | 593 | 543.6 | 484.1
2509.1 | 1877.1 | 248.1 | 264.8 | 592.8 | 543.8 | 484.4
2510.1 | 1878.1 | 248.4 | 265.1 | 596.3 | 547.5 | 484.7
2511.1 | 1879.1 | 248.7 | 265.5 | 593.9 | 544.2 | 484.7
2512.1 | 1880.1 | 248.9 | 265.8 | 591.2 | 540.5 | 484.4
2513.1 | 1881.1 | 249.1 | 266 | 593.9 | 550.4 | 486.7
2514.1 | 1882.1 | 249.4 | 266.2 | 592.7 | 549.2 | 487.1
2515.1 | 1883.1 | 249.6 | 266.4 | 591 | 544.2 | 486.1
2516.1 | 1884.1 | 250 | 266.7 | 587.6 | 542 | 486.2
2517.1 | 1885.1 | 250.2 | 266.8 | 587.3 | 542.5 | 486.4
2518.1 | 1886.1 | 250.4 | 266.9 | 586.5 | 540.7 | 486.1
2519.1 | 1887.1 | 250.7 | 267 | 583.5 | 538.3 | 486.7
2520.1 | 1888.1 | 250.8 | 267.1 | 579.9 | 535.2 | 486.8
2521.1 | 1889.1 | 251.1 | 267.1 | 580.9 | 534.1 | 486.4
2522.1 | 1890.1 | 251.4 | 267.2 | 581.7 | 532.8 | 486.2
2523.1 | 1891.1 | 251.5 | 267.2 | 580.1 | 530.4 | 486.2
2524.1 | 1892.1 | 251.8 | 267.3 | 578.4 | 530.6 | 485.9
2525.1 | 1893.1 | 252 | 267.3 | 577.5 | 532 | 485.9
2526.1 | 1894.1 | 252.2 | 267.4 | 574.9 | 530.2 | 486
2527.1 | 1895.1 | 252.4 | 267.5 | 571.5 | 527.9 | 485.4
2528.1 | 1896.1 | 252.6 | 267.6 | 566.8 | 525.8 | 484.8
2529.1 | 1897.1 | 252.8 | 267.6 | 567.1 | 526.9 | 484.4
2530.1 | 1898.1 | 253 | 267.7 | 567.3 | 528.5 | 484.5
2531.1 | 1899.1 | 253.3 | 267.8 | 566.9 | 525.7 | 484.1
2532.1 | 1900.1 | 253.6 | 267.9 | 566 | 527 | 484.9
2533.1 | 1901.1 | 253.8 | 267.9 | 565.6 | 526.1 | 484.8
2534.1 | 1902.1 | 253.9 | 268 | 562.9 | 521.3 | 484
2535.1 | 1903.1 | 254.1 | 268.1 | 561.8 | 519.2 | 483.8
2536.1 | 1904.1 | 254.3 | 268.2 | 563.5 | 519.9 | 484.6
2537.1 | 1905.1 | 254.4 | 268.4 | 562.8 | 518.9 | 484.7
2538.1 | 1906.1 | 254.8 | 268.6 | 562.7 | 518.3 | 484.5
2539.1 | 1907.1 | 255 | 268.8 | 564 | 521.3 | 484.9
2540.1 | 1908.1 | 255.2 | 268.9 | 565.5 | 524 | 485
2541.1 | 1909.1 | 255.4 | 269.1 | 568.4 | 524 | 486.7
2542.1 | 1910.1 | 255.8 | 269.4 | 571.3 | 525.4 | 487.8
2543.1 | 1911.1 | 256.1 | 269.5 | 568.6 | 524.9 | 486.8
2544.1 | 1912.1 | 256.3 | 269.6 | 571 | 530.3 | 487.5
2545.1 | 1913.1 | 256.5 | 269.8 | 575.6 | 533.1 | 487.4
2546.1 | 1914.1 | 256.7 | 269.9 | 572.4 | 531.3 | 487.1
2547.1 | 1915.1 | 256.9 | 270.1 | 571.7 | 529 | 486.7
2548.1 | 1916.1 | 257.2 | 270.3 | 571.9 | 527.2 | 486.2
2549.1 | 1917.1 | 257.4 | 270.5 | 569.5 | 527.4 | 486
2550.1 | 1918.1 | 257.6 | 270.6 | 569.6 | 529.5 | 486.6
2551.1 | 1919.1 | 257.7 | 270.8 | 569.2 | 528.6 | 486.4
2552.1 | 1920.1 | 258.1 | 271.1 | 568.1 | 530.3 | 486.4
2553.1 | 1921.1 | 258.3 | 271.3 | 571.5 | 530.1 | 486.7
2554.1 | 1922.1 | 258.5 | 271.5 | 573.1 | 528.4 | 486.4
2555.1 | 1923.1 | 258.7 | 271.6 | 572 | 525.8 | 486.5
2556.1 | 1924.1 | 258.9 | 271.8 | 572.3 | 525 | 487.8
2557.1 | 1925.1 | 259.2 | 272 | 577.4 | 536.5 | 488.8
2558.1 | 1926.1 | 259.4 | 272.2 | 578.4 | 534.5 | 488.1
2559.1 | 1927.1 | 259.6 | 272.4 | 578.8 | 533.4 | 490
2560.1 | 1928.1 | 259.9 | 272.6 | 575.5 | 531.4 | 489.5
2561.1 | 1929.1 | 260.1 | 272.8 | 574.9 | 529.3 | 489
2562.1 | 1930.1 | 260.4 | 273 | 577.7 | 528.4 | 489.2
2563.1 | 1931.1 | 260.7 | 273.1 | 575.8 | 525.3 | 488.8
2564.1 | 1932.1 | 260.8 | 273.1 | 572 | 522.7 | 489
2565.1 | 1933.1 | 261 | 273.2 | 572.8 | 535.1 | 490.3
2566.1 | 1934.1 | 261.2 | 273.3 | 577.1 | 535.3 | 489.8
2567.1 | 1935.1 | 261.4 | 273.6 | 576.5 | 536.7 | 489.9
2568.1 | 1936.1 | 261.7 | 274 | 579.8 | 538.8 | 489.8
2569.1 | 1937.1 | 261.9 | 274.3 | 578.3 | 539.8 | 489.8
2570.1 | 1938.1 | 262.2 | 274.6 | 582.5 | 537.6 | 490.2
2571.1 | 1939.1 | 262.4 | 275 | 589.2 | 539 | 490.6
2572.1 | 1940.1 | 262.7 | 275.3 | 595.4 | 542.2 | 490.9
2573.1 | 1941.1 | 262.9 | 275.7 | 597.4 | 538 | 490.8
2574.1 | 1942.1 | 263.1 | 276 | 591.2 | 533.5 | 490.9
2575.1 | 1943.1 | 263.4 | 276.4 | 588.9 | 531.4 | 494.3
2576.1 | 1944.1 | 263.6 | 276.7 | 598 | 534.4 | 494.2
2577.1 | 1945.1 | 263.8 | 277.1 | 593.9 | 532.2 | 493.7
2578.1 | 1946.1 | 264.1 | 277.4 | 595.5 | 532.6 | 493.3
2579.1 | 1947.1 | 264.3 | 277.7 | 591.2 | 529.7 | 493
2580.1 | 1948.1 | 264.4 | 277.9 | 593 | 536.4 | 493.5
2581.1 | 1949.1 | 264.7 | 278.2 | 603.5 | 549.8 | 495.5
2582.1 | 1950.1 | 264.9 | 278.5 | 599 | 546.6 | 494.9
2583.1 | 1951.1 | 265.1 | 278.8 | 593.9 | 543 | 494.4
2584.1 | 1952.1 | 265.3 | 279 | 594.2 | 544.5 | 495.9
2585.1 | 1953.1 | 265.5 | 279.2 | 592.3 | 539.8 | 495.3
2586.1 | 1954.1 | 265.7 | 279.5 | 590.5 | 541.1 | 494.8
2587.1 | 1955.1 | 265.9 | 279.7 | 594.3 | 545.4 | 495.5
2588.1 | 1956.1 | 266.1 | 280 | 595 | 543.3 | 495.7
2589.1 | 1957.1 | 266.4 | 280.3 | 592.3 | 539.2 | 495.4
2590.1 | 1958.1 | 266.6 | 280.6 | 592.9 | 554.2 | 496.4
2591.1 | 1959.1 | 266.8 | 280.8 | 597 | 551.9 | 496.3
2592.1 | 1960.1 | 267 | 281 | 593.2 | 550.1 | 495.7
2593.1 | 1961.1 | 267.2 | 281.1 | 588.8 | 548.8 | 495.3
2594.1 | 1962.1 | 267.4 | 281.3 | 583.2 | 549.8 | 494.9
2595.1 | 1963.1 | 267.6 | 281.5 | 585.6 | 553.1 | 495.6
2596.1 | 1964.1 | 267.9 | 281.8 | 582.1 | 549.3 | 495.1
2597.1 | 1965.1 | 268 | 282.1 | 581.5 | 550.4 | 494.6
2598.1 | 1966.1 | 268.2 | 282.3 | 582.7 | 549.3 | 494.8
2599.1 | 1967.1 | 268.4 | 282.5 | 592.2 | 549.1 | 494.5
2600.1 | 1968.1 | 268.5 | 282.8 | 591.4 | 548.3 | 494.2
2601.1 | 1969.1 | 268.6 | 283.1 | 587.8 | 546.2 | 494
2602.1 | 1970.1 | 268.7 | 283.2 | 590.3 | 547.2 | 493.9
2603.1 | 1971.1 | 268.9 | 283.6 | 593.3 | 546.2 | 494
2604.1 | 1972.1 | 269 | 283.9 | 589.3 | 550.4 | 495.2
2605.1 | 1973.1 | 269.2 | 284.2 | 591.6 | 548.6 | 495.4
2606.1 | 1974.1 | 269.3 | 284.4 | 587.9 | 546.2 | 494.9
2607.1 | 1975.1 | 269.3 | 284.7 | 587.2 | 544.9 | 495.9
2608.1 | 1976.1 | 269.3 | 285.1 | 589 | 547 | 497.5
2609.1 | 1977.1 | 269.3 | 285.4 | 592.3 | 548.8 | 499.5
2610.1 | 1978.1 | 269.3 | 285.7 | 594.7 | 548.6 | 498.6
2611.1 | 1979.1 | 269.4 | 285.9 | 594.8 | 545.1 | 498.3
2612.1 | 1980.1 | 269.5 | 286.1 | 594.2 | 540.6 | 498.1
2613.1 | 1981.1 | 269.6 | 286.4 | 600.8 | 544.4 | 499.6
2614.1 | 1982.1 | 269.7 | 286.6 | 601.1 | 548.6 | 500.5
2615.1 | 1983.1 | 269.9 | 286.9 | 599.7 | 543.1 | 499.9
2616.1 | 1984.1 | 270 | 287.1 | 599.5 | 547 | 500.4
2617.1 | 1985.1 | 270.1 | 287.3 | 601.3 | 548.9 | 500.7
2618.1 | 1986.1 | 270.3 | 287.5 | 596.2 | 543.6 | 500
2619.1 | 1987.1 | 270.5 | 287.8 | 598 | 551.7 | 502.1
2620.1 | 1988.1 | 270.7 | 288.1 | 601.6 | 551.8 | 501.9
2621.1 | 1989.1 | 270.8 | 288.4 | 600.1 | 552.4 | 501
2622.1 | 1990.1 | 270.9 | 288.5 | 599.5 | 553.1 | 501.6
2623.1 | 1991.1 | 271.2 | 288.9 | 598.9 | 555.5 | 501.9
2624.1 | 1992.1 | 271.3 | 289.1 | 596.5 | 552.4 | 501.3
2625.1 | 1993.1 | 271.4 | 289.3 | 597 | 553.7 | 501.5
2626.1 | 1994.1 | 271.5 | 289.5 | 596.2 | 551.6 | 500.5
2627.1 | 1995.1 | 271.6 | 289.7 | 595.2 | 550.8 | 499.8
2628.1 | 1996.1 | 271.9 | 290 | 596.7 | 549.1 | 499.1
2629.1 | 1997.1 | 272 | 290.2 | 596 | 545.8 | 498.7
2630.1 | 1998.1 | 272.2 | 290.4 | 604.6 | 542.4 | 498.8
2631.1 | 1999.1 | 272.3 | 290.6 | 606.9 | 545 | 499.6
2632.1 | 2000.1 | 272.5 | 290.8 | 609 | 546.1 | 500.7
2633.1 | 2001.1 | 272.7 | 291.1 | 618.1 | 559.3 | 500.9
2634.1 | 2002.1 | 272.8 | 291.3 | 616.5 | 559.1 | 501.2
2635.1 | 2003.1 | 273 | 291.5 | 615.2 | 556.6 | 501.3
2636.1 | 2004.1 | 273.1 | 291.7 | 613.9 | 554.4 | 502.3
2637.1 | 2005.1 | 273.4 | 291.9 | 610.1 | 550.5 | 501.7
2638.1 | 2006.1 | 273.5 | 292.1 | 607 | 547.3 | 501.7
2639.1 | 2007.1 | 273.7 | 292.3 | 611.2 | 545.4 | 501.8
2640.1 | 2008.1 | 273.8 | 292.5 | 615.2 | 544.9 | 501
2641.1 | 2009.1 | 274 | 292.6 | 612.7 | 545.8 | 500.4
2642.1 | 2010.1 | 274.2 | 292.8 | 610.6 | 545.2 | 500.7
2643.1 | 2011.1 | 274.4 | 293.1 | 608.6 | 546.2 | 501.4
2644.1 | 2012.1 | 274.5 | 293.2 | 602.7 | 545.8 | 501.5
2645.1 | 2013.1 | 274.7 | 293.3 | 598.1 | 544.2 | 500.3
2646.1 | 2014.1 | 274.9 | 293.6 | 600.3 | 543.6 | 499.6
2647.1 | 2015.1 | 275 | 293.7 | 594.5 | 539.2 | 499
2648.1 | 2016.1 | 275.2 | 293.8 | 603.1 | 548.8 | 499.4
2649.1 | 2017.1 | 275.4 | 294 | 608.8 | 553.2 | 500
2650.1 | 2018.1 | 275.5 | 294.1 | 602.7 | 545.5 | 499.2
2651.1 | 2019.1 | 275.8 | 294.4 | 598.8 | 549.3 | 501.5
2652.1 | 2020.1 | 275.9 | 294.6 | 599.4 | 552.4 | 504.4
2653.1 | 2021.1 | 276.8 | 294.2 | 598.1 | 555.5 | 506.3
2654.1 | 2022.1 | 276.7 | 294.7 | 597.8 | 552.7 | 505.1
2655.1 | 2023.1 | 276.9 | 294.8 | 598.4 | 551.9 | 505.1
2656.1 | 2024.1 | 277.1 | 295 | 597.9 | 553.7 | 505.3
2657.1 | 2025.1 | 277.3 | 295.2 | 596.3 | 552.7 | 504.7
2658.1 | 2026.1 | 277.5 | 295.4 | 595.8 | 550 | 504.2
2659.1 | 2027.1 | 277.7 | 295.6 | 594.9 | 549 | 504.1
2660.1 | 2028.1 | 277.9 | 295.9 | 596.6 | 550.1 | 504.1
2661.1 | 2029.1 | 278.1 | 296 | 599.4 | 555.8 | 505.6
2662.1 | 2030.1 | 278.3 | 296.2 | 598.5 | 553.4 | 505.1
2663.1 | 2031.1 | 278.4 | 296.6 | 599.2 | 556.1 | 505.8
2664.1 | 2032.1 | 278.7 | 296.7 | 598.3 | 553 | 505.5
2665.1 | 2033.1 | 279 | 296.9 | 595.9 | 550.3 | 504.6
2666.1 | 2034.1 | 279.2 | 297.1 | 595.2 | 555 | 504
2667.1 | 2035.1 | 279.3 | 297.5 | 606.2 | 556.8 | 503.3
2668.1 | 2036.1 | 279.5 | 297.7 | 605 | 553 | 502.5
2669.1 | 2037.1 | 279.8 | 297.8 | 601.9 | 552.2 | 502.4
2670.1 | 2038.1 | 280 | 297.9 | 601.3 | 550.7 | 502.4
2671.1 | 2039.1 | 280.2 | 298 | 602.7 | 546.2 | 501.5
2672.1 | 2040.1 | 280.4 | 298.2 | 612.5 | 550.7 | 501.3
2673.1 | 2041.1 | 280.7 | 298.2 | 617.4 | 560.1 | 504.6
2674.1 | 2042.1 | 280.8 | 298.4 | 617.6 | 563.5 | 504.7
2675.1 | 2043.1 | 281 | 298.5 | 611 | 558.1 | 504.3
2676.1 | 2044.1 | 281.2 | 298.6 | 609.3 | 558.6 | 504.2
2677.1 | 2045.1 | 281.3 | 298.8 | 609.2 | 558.7 | 504.6
2678.1 | 2046.1 | 281.6 | 299.1 | 608 | 556.4 | 504.5
2679.1 | 2047.1 | 281.8 | 299.2 | 603.1 | 552.7 | 504
2680.1 | 2048.1 | 281.9 | 299.3 | 605.1 | 555.2 | 503.9
2681.1 | 2049.1 | 281.9 | 299.5 | 609.9 | 563.6 | 505.3
2682.1 | 2050.1 | 282.1 | 299.7 | 610.5 | 563.7 | 506.8
2683.1 | 2051.1 | 282.2 | 299.8 | 609.4 | 565.7 | 506.3
2684.1 | 2052.1 | 282.2 | 300.1 | 607.2 | 562.7 | 506.3
2685.1 | 2053.1 | 282.3 | 300.3 | 603.4 | 556.2 | 505.2
2686.1 | 2054.1 | 282.4 | 300.4 | 608.3 | 555 | 504.3
2687.1 | 2055.1 | 282.5 | 300.6 | 609.6 | 551.8 | 503.3
2688.1 | 2056.1 | 282.6 | 300.8 | 611.3 | 548.3 | 502.5
2689.1 | 2057.1 | 282.7 | 301 | 622.3 | 548.4 | 503.1
2690.1 | 2058.1 | 282.8 | 301.2 | 629.5 | 561.6 | 505.8
2691.1 | 2059.1 | 282.9 | 301.4 | 627 | 561.7 | 506.1
2692.1 | 2060.1 | 283 | 301.6 | 619.6 | 567.4 | 505.9
2693.1 | 2061.1 | 283.2 | 301.8 | 614.8 | 572.4 | 506.3
2694.1 | 2062.1 | 283.2 | 302 | 608.5 | 566.3 | 505.1
2695.1 | 2063.1 | 283.3 | 302.2 | 599.6 | 560.9 | 504.6
2696.1 | 2064.1 | 283.4 | 302.5 | 595 | 560.6 | 504.5
2697.1 | 2065.1 | 283.6 | 302.8 | 593.8 | 559.6 | 504.4
2698.1 | 2066.1 | 283.6 | 303.3 | 592 | 554.9 | 503.3
2699.1 | 2067.1 | 283.8 | 303.8 | 590.2 | 555.7 | 503
2700.1 | 2068.1 | 283.9 | 304.2 | 593 | 556.8 | 502.9
2701.1 | 2069.1 | 284 | 304.7 | 594.2 | 554.8 | 502
2702.1 | 2070.1 | 284.1 | 305.1 | 594.4 | 560.5 | 501.9
2703.1 | 2071.1 | 284.2 | 305.5 | 595.4 | 563.7 | 502.6
2704.1 | 2072.1 | 284.4 | 305.9 | 597 | 562.5 | 502.4
2705.1 | 2073.1 | 284.5 | 306.3 | 594.4 | 556.4 | 501.9
2706.1 | 2074.1 | 284.6 | 306.7 | 591.7 | 554.5 | 501.6
2707.1 | 2075.1 | 284.8 | 307.1 | 592.6 | 555.7 | 501.4
2708.1 | 2076.1 | 284.9 | 307.4 | 591.8 | 554.3 | 501.2
2709.1 | 2077.1 | 285 | 307.9 | 603.5 | 557.6 | 501.3
2710.1 | 2078.1 | 285.1 | 308.3 | 610.3 | 568.5 | 502.5
2711.1 | 2079.1 | 285.3 | 308.7 | 611.4 | 564.2 | 501.6
2712.1 | 2080.1 | 285.4 | 309.1 | 611.1 | 563.8 | 502.1
2713.1 | 2081.1 | 285.6 | 309.5 | 611.2 | 567.5 | 504
2714.1 | 2082.1 | 285.8 | 309.8 | 607.2 | 563.8 | 504
2715.1 | 2083.1 | 285.9 | 310.1 | 606.5 | 561.6 | 503.5
2716.1 | 2084.1 | 286 | 310.5 | 602.5 | 559.5 | 503.2
2717.1 | 2085.1 | 286.2 | 310.9 | 600.5 | 555.8 | 503.2
2718.1 | 2086.1 | 286.3 | 311.2 | 597.6 | 556 | 503.2
2719.1 | 2087.1 | 286.4 | 311.7 | 597.1 | 554.4 | 502.8
2720.1 | 2088.1 | 286.5 | 312 | 598.1 | 552.6 | 501.9
2721.1 | 2089.1 | 286.7 | 312.4 | 602.2 | 554 | 501.4
2722.1 | 2090.1 | 286.9 | 312.8 | 609.7 | 563.7 | 501.9
2723.1 | 2091.1 | 287 | 313.2 | 613.5 | 569.2 | 502.9
2724.1 | 2092.1 | 287.1 | 313.7 | 619 | 571.1 | 503.6
2725.1 | 2093.1 | 287.4 | 314 | 616.8 | 571 | 503.8
2726.1 | 2094.1 | 287.5 | 314.4 | 624.6 | 577.3 | 505.8
2727.1 | 2095.1 | 287.7 | 314.8 | 623.9 | 575.8 | 506.1
2728.1 | 2096.1 | 287.8 | 315.1 | 618.5 | 571.9 | 504.6
2729.1 | 2097.1 | 288 | 315.5 | 624.6 | 570.6 | 503.9
2730.1 | 2098.1 | 288.2 | 315.9 | 635 | 568.4 | 503.6
2731.1 | 2099.1 | 288.4 | 316.3 | 639.2 | 568.5 | 504.1
2732.1 | 2100.1 | 288.7 | 316.6 | 636.6 | 572.4 | 505.9
2733.1 | 2101.1 | 288.8 | 317 | 630.8 | 577.8 | 505.5
2734.1 | 2102.1 | 289 | 317.5 | 631.8 | 577.5 | 506.4
2735.1 | 2103.1 | 289.2 | 317.9 | 628.7 | 582.9 | 506.8
2736.1 | 2104.1 | 289.6 | 318.3 | 627.7 | 576.5 | 506.4
2737.1 | 2105.1 | 289.8 | 318.7 | 633.4 | 581 | 509
2738.1 | 2106.1 | 289.9 | 319 | 628.1 | 585.4 | 508.4
2739.1 | 2107.1 | 290.2 | 319.2 | 622.2 | 582.7 | 508
2740.1 | 2108.1 | 290.3 | 319.6 | 618 | 580.9 | 507.4
2741.1 | 2109.1 | 290.4 | 320 | 619.3 | 575.6 | 506.3
2742.1 | 2110.1 | 290.6 | 320.2 | 617.9 | 571 | 505.3
2743.1 | 2111.1 | 290.8 | 320.5 | 619 | 567 | 504.4
2744.1 | 2112.1 | 290.9 | 320.9 | 617.3 | 564.4 | 503.9
2745.1 | 2113.1 | 291.1 | 321.2 | 611.6 | 561.6 | 503.5
2746.1 | 2114.1 | 291.3 | 321.4 | 606.4 | 559.8 | 503
2747.1 | 2115.1 | 291.4 | 321.8 | 604.6 | 559 | 502.5
2748.1 | 2116.1 | 291.6 | 322.2 | 607.8 | 559.6 | 502.4
2749.1 | 2117.1 | 291.8 | 322.5 | 609.2 | 554.6 | 502.3
2750.1 | 2118.1 | 291.9 | 322.8 | 620.8 | 553.9 | 504.9
2751.1 | 2119.1 | 292.1 | 323.2 | 631.1 | 569.5 | 507.9
2752.1 | 2120.1 | 292.4 | 323.5 | 630.4 | 578.4 | 509.2
2753.1 | 2121.1 | 292.6 | 323.8 | 626.5 | 573.7 | 508.8
2754.1 | 2122.1 | 292.8 | 324.2 | 628.2 | 568.3 | 508.2
2755.1 | 2123.1 | 293.1 | 324.6 | 633.7 | 563 | 507.7
2756.1 | 2124.1 | 293.2 | 324.8 | 638.6 | 559.1 | 507.7
2757.1 | 2125.1 | 293.4 | 325.2 | 634.4 | 553.5 | 507.3
2758.1 | 2126.1 | 293.7 | 325.6 | 625 | 549 | 507.1
2759.1 | 2127.1 | 293.9 | 326 | 620.1 | 560.7 | 508.5
2760.1 | 2128.1 | 294.2 | 326.4 | 617.9 | 562 | 510.6
2761.1 | 2129.1 | 294.4 | 327 | 619.6 | 583.9 | 509.7
2762.1 | 2130.1 | 294.5 | 327.5 | 617.8 | 586.2 | 510.5
2763.1 | 2131.1 | 294.7 | 327.9 | 614.3 | 581.9 | 509.3
2764.1 | 2132.1 | 294.9 | 328.4 | 622.2 | 586.6 | 509.8
2765.1 | 2133.1 | 295.1 | 328.9 | 628.9 | 584.2 | 511.9
2766.1 | 2134.1 | 295.4 | 329.3 | 631.6 | 590.9 | 514.7
2767.1 | 2135.1 | 295.6 | 329.6 | 631.4 | 596.9 | 514.8
2768.1 | 2136.1 | 295.8 | 330 | 629.1 | 606.3 | 516.6
2769.1 | 2137.1 | 296.1 | 330.4 | 628.7 | 598.6 | 516.1
2770.1 | 2138.1 | 296.2 | 330.7 | 624.1 | 599.4 | 515.6
2771.1 | 2139.1 | 296.4 | 331.1 | 628 | 606.7 | 517.1
2772.1 | 2140.1 | 296.6 | 331.5 | 632.1 | 597.2 | 515.2
2773.1 | 2141.1 | 296.8 | 331.9 | 625.9 | 593 | 514.1
2774.1 | 2142.1 | 297.1 | 332.2 | 623.8 | 591.8 | 514.1
2775.1 | 2143.1 | 297.4 | 332.6 | 618.6 | 585.7 | 513.6
2776.1 | 2144.1 | 297.5 | 332.9 | 612.8 | 580.9 | 512.9
2777.1 | 2145.1 | 297.7 | 333.2 | 613.3 | 580.7 | 514.6
2778.1 | 2146.1 | 297.9 | 333.5 | 612.6 | 589.4 | 515.9
2779.1 | 2147.1 | 298.1 | 333.8 | 610.6 | 588.6 | 515.9
2780.1 | 2148.1 | 298.3 | 334.1 | 610.9 | 582.8 | 514.4
2781.1 | 2149.1 | 298.5 | 334.4 | 614.5 | 581.3 | 513.6
2782.1 | 2150.1 | 298.7 | 334.7 | 620 | 585.8 | 513.4
2783.1 | 2151.1 | 298.9 | 335 | 618.5 | 581.4 | 512.8
2784.1 | 2152.1 | 299.2 | 335.3 | 612.2 | 580.1 | 513.1
2785.1 | 2153.1 | 299.5 | 335.6 | 612 | 586.8 | 514.8
2786.1 | 2154.1 | 299.6 | 335.9 | 605 | 581.1 | 514.5
2787.1 | 2155.1 | 299.8 | 336.2 | 611.4 | 592.8 | 518.6
2788.1 | 2156.1 | 300.1 | 336.4 | 615.1 | 588 | 517.9
2789.1 | 2157.1 | 300.3 | 336.7 | 618.4 | 581.5 | 516.4
2790.1 | 2158.1 | 300.5 | 337 | 617.9 | 578.3 | 515.9
2791.1 | 2159.1 | 300.8 | 337.2 | 617.1 | 578.7 | 516.4
2792.1 | 2160.1 | 301.1 | 337.5 | 616.5 | 576.2 | 516.2
2793.1 | 2161.1 | 301.3 | 337.8 | 623.6 | 574.4 | 516
2794.1 | 2162.1 | 301.4 | 338.1 | 620.2 | 571.5 | 515.7
2795.1 | 2163.1 | 301.7 | 338.3 | 623.6 | 572 | 515.5
2796.1 | 2164.1 | 302 | 338.5 | 628.7 | 576.2 | 515.8
2797.1 | 2165.1 | 302.2 | 338.7 | 633 | 577.1 | 516.9
2798.1 | 2166.1 | 302.5 | 338.9 | 637.4 | 578.5 | 517
2799.1 | 2167.1 | 302.8 | 339.1 | 641.8 | 576.9 | 518.3
2800.1 | 2168.1 | 303 | 339.3 | 637.3 | 573.7 | 518.4
2801.1 | 2169.1 | 303.2 | 339.5 | 635.6 | 578 | 519
2802.1 | 2170.1 | 303.5 | 339.7 | 637.9 | 583.2 | 520.2
2803.1 | 2171.1 | 303.7 | 339.9 | 631.7 | 580.7 | 519.8
2804.1 | 2172.1 | 303.9 | 340.1 | 633.9 | 576.6 | 522.7
2805.1 | 2173.1 | 304.3 | 340.3 | 629.9 | 571.8 | 523
2806.1 | 2174.1 | 304.5 | 340.5 | 630.2 | 569.2 | 522
2807.1 | 2175.1 | 304.7 | 340.8 | 634.8 | 573.8 | 522.8
2808.1 | 2176.1 | 305 | 341 | 636 | 576.4 | 524.9
2809.1 | 2177.1 | 305.3 | 341.2 | 632 | 572.5 | 524.1
2810.1 | 2178.1 | 305.5 | 341.5 | 629.9 | 575.2 | 523.9
2811.1 | 2179.1 | 305.7 | 341.7 | 632.8 | 579.6 | 524.7
2812.1 | 2180.1 | 306 | 341.9 | 635.4 | 579.4 | 524.9
2813.1 | 2181.1 | 306.2 | 342.2 | 635.8 | 584.7 | 526
2814.1 | 2182.1 | 306.5 | 342.5 | 636 | 587.9 | 527
2815.1 | 2183.1 | 306.8 | 342.7 | 629.4 | 586 | 526.5
2816.1 | 2184.1 | 307.1 | 342.9 | 630.9 | 584.4 | 525.3
2817.1 | 2185.1 | 307.3 | 343.1 | 641 | 581.4 | 524.1
2818.1 | 2186.1 | 307.5 | 343.3 | 644.7 | 580.4 | 523.3
2819.1 | 2187.1 | 307.8 | 343.5 | 649.4 | 578.6 | 522.9
2820.1 | 2188.1 | 308.1 | 343.6 | 653.2 | 581.8 | 522.6
2821.1 | 2189.1 | 308.4 | 343.8 | 648.2 | 576.6 | 521.8
2822.1 | 2190.1 | 308.7 | 343.9 | 647.9 | 579 | 521.1
2823.1 | 2191.1 | 308.9 | 344.2 | 645.4 | 583.1 | 521.1
2824.1 | 2192.1 | 309.1 | 344.4 | 641.3 | 579.9 | 520.1
2825.1 | 2193.1 | 309.4 | 344.7 | 636.8 | 573.9 | 518.7
2826.1 | 2194.1 | 309.6 | 344.8 | 632.4 | 568.2 | 517.6
2827.1 | 2195.1 | 309.9 | 345.1 | 628.6 | 564.6 | 516.6
2828.1 | 2196.1 | 310.1 | 345.4 | 627 | 563.8 | 515.8
2829.1 | 2197.1 | 310.4 | 345.7 | 622.6 | 560.4 | 515
2830.1 | 2198.1 | 310.7 | 345.9 | 618.9 | 556.7 | 514
2831.1 | 2199.1 | 310.9 | 346.1 | 615.9 | 552.3 | 512.8
2832.1 | 2200.1 | 311.2 | 346.4 | 615.7 | 549.9 | 511.9
2833.1 | 2201.1 | 311.4 | 346.6 | 613.5 | 548.1 | 511.1
2834.1 | 2202.1 | 311.7 | 346.8 | 611.8 | 546.7 | 510.2
2835.1 | 2203.1 | 311.9 | 347.2 | 608.1 | 545 | 509.3
2836.1 | 2204.1 | 312.1 | 347.4 | 604.6 | 547 | 509
2837.1 | 2205.1 | 312.3 | 347.6 | 599.3 | 547.3 | 508.7
2838.1 | 2206.1 | 312.6 | 347.9 | 596.4 | 545.8 | 507.9
2839.1 | 2207.1 | 312.9 | 348.2 | 593.4 | 541.6 | 507.3
2840.1 | 2208.1 | 313.2 | 348.5 | 590.2 | 540.1 | 507.1
2841.1 | 2209.1 | 313.4 | 348.8 | 589.9 | 542 | 507.2
2842.1 | 2210.1 | 313.7 | 349.1 | 590.2 | 540 | 506.6
2843.1 | 2211.1 | 314 | 349.4 | 593.1 | 539.3 | 506.3
2844.1 | 2212.1 | 314.4 | 349.7 | 607.1 | 548.5 | 507.1
2845.1 | 2213.1 | 314.7 | 350 | 621.5 | 552.1 | 506.9
2846.1 | 2214.1 | 314.9 | 350.3 | 627.5 | 553.4 | 506.3
2847.1 | 2215.1 | 315.2 | 350.6 | 634.6 | 552.7 | 505.7
2848.1 | 2216.1 | 315.5 | 350.9 | 648.7 | 559.6 | 506
2849.1 | 2217.1 | 315.8 | 351.3 | 649.2 | 560.1 | 505.6
2850.1 | 2218.1 | 316.1 | 351.6 | 644.6 | 559.6 | 505.1
2851.1 | 2219.1 | 316.4 | 351.9 | 648 | 558.2 | 504.5
2852.1 | 2220.1 | 316.7 | 352.2 | 639.9 | 555 | 503.9
2853.1 | 2221.1 | 317 | 352.6 | 644.6 | 563.7 | 504.2
2854.1 | 2222.1 | 317.3 | 352.8 | 643 | 568.6 | 504.6
2855.1 | 2223.1 | 317.6 | 353.1 | 636.6 | 564.4 | 503.8
2856.1 | 2224.1 | 317.8 | 353.5 | 631.1 | 561.1 | 503.1
2857.1 | 2225.1 | 318.1 | 353.8 | 624.5 | 557.8 | 502.6
2858.1 | 2226.1 | 318.5 | 354.1 | 619.2 | 555.2 | 502.8
2859.1 | 2227.1 | 318.8 | 354.4 | 625 | 548.8 | 504.2
2860.1 | 2228.1 | 319.1 | 354.8 | 625.5 | 552.2 | 504
2861.1 | 2229.1 | 319.4 | 355 | 622.1 | 549 | 503.4
2862.1 | 2230.1 | 319.6 | 355.3 | 617.9 | 548.1 | 503.3
2863.1 | 2231.1 | 319.9 | 355.6 | 612.9 | 547 | 503.2
2864.1 | 2232.1 | 320.2 | 355.9 | 608.2 | 544.6 | 503.1
2865.1 | 2233.1 | 320.5 | 356.1 | 605 | 541.9 | 502.6
2866.1 | 2234.1 | 320.8 | 356.4 | 598.6 | 539.3 | 501.8
2867.1 | 2235.1 | 321.1 | 356.7 | 595.6 | 538.8 | 501.3
2868.1 | 2236.1 | 321.4 | 357 | 592.7 | 536.3 | 500.7
2869.1 | 2237.1 | 321.6 | 357.3 | 587.3 | 534.2 | 500.7
2870.1 | 2238.1 | 321.8 | 357.6 | 584.2 | 534 | 500.7
2871.1 | 2239.1 | 322.1 | 357.9 | 583 | 534.5 | 500.1
2872.1 | 2240.1 | 322.5 | 358.2 | 585.3 | 539.4 | 500
2873.1 | 2241.1 | 322.8 | 358.5 | 589 | 539.6 | 499.8
2874.1 | 2242.1 | 323.1 | 358.8 | 595.5 | 539.5 | 499.6
2875.1 | 2243.1 | 323.4 | 359.2 | 607.4 | 539.3 | 499.1
2876.1 | 2244.1 | 323.7 | 359.4 | 618.8 | 542.8 | 498.7
2877.1 | 2245.1 | 324 | 359.8 | 627.2 | 544.8 | 498.4
2878.1 | 2246.1 | 324.4 | 360.1 | 635.7 | 547.1 | 498.2
2879.1 | 2247.1 | 324.7 | 360.3 | 637.2 | 546.2 | 497.9
2880.1 | 2248.1 | 325 | 360.6 | 635.2 | 544.3 | 497.6
2881.1 | 2249.1 | 325.3 | 360.9 | 638.2 | 551.7 | 500.1
2882.1 | 2250.1 | 325.7 | 361.2 | 635.9 | 561.6 | 502.1
2883.1 | 2251.1 | 326 | 361.4 | 634.7 | 573.9 | 504.1
2884.1 | 2252.1 | 326.3 | 361.8 | 633.4 | 572.3 | 504.4
2885.1 | 2253.1 | 326.6 | 362 | 630.3 | 575.8 | 506.6
2886.1 | 2254.1 | 327 | 362.3 | 632.6 | 575.7 | 506.7
2887.1 | 2255.1 | 327.3 | 362.6 | 631.4 | 571 | 505.8
2888.1 | 2256.1 | 327.6 | 362.9 | 625.4 | 564.8 | 504.9
2889.1 | 2257.1 | 327.9 | 363.1 | 617.9 | 564.7 | 505.7
2890.1 | 2258.1 | 328.2 | 363.4 | 613.6 | 571.1 | 507.3
2891.1 | 2259.1 | 328.5 | 363.7 | 610.8 | 566.7 | 506.1
2892.1 | 2260.1 | 328.8 | 363.9 | 609.5 | 560.7 | 504.8
2893.1 | 2261.1 | 329.1 | 364.2 | 614.7 | 555.8 | 503.8
2894.1 | 2262.1 | 329.4 | 364.5 | 611.8 | 553.1 | 503.1
2895.1 | 2263.1 | 329.7 | 364.7 | 610.1 | 549.3 | 502.9
2896.1 | 2264.1 | 330 | 364.9 | 611 | 547.7 | 502.8
2897.1 | 2265.1 | 330.3 | 365.2 | 612.1 | 548.8 | 503.9
2898.1 | 2266.1 | 330.6 | 365.5 | 618 | 552.6 | 504.9
2899.1 | 2267.1 | 331 | 365.7 | 623.7 | 550.3 | 503.9
2900.1 | 2268.1 | 331.3 | 365.9 | 628.8 | 552.1 | 503.9
2901.1 | 2269.1 | 331.6 | 366.2 | 628.7 | 553.7 | 503.4
2902.1 | 2270.1 | 332 | 366.4 | 624.5 | 559.1 | 503.9
2903.1 | 2271.1 | 332.3 | 366.6 | 622.2 | 554.8 | 503.8
2904.1 | 2272.1 | 332.7 | 366.9 | 621.7 | 554.2 | 503.8
2905.1 | 2273.1 | 333.1 | 367.3 | 626 | 559.4 | 504.9
2906.1 | 2274.1 | 333.5 | 367.5 | 629.6 | 557.3 | 504.2
2907.1 | 2275.1 | 333.9 | 367.8 | 631.5 | 554.2 | 503.6
2908.1 | 2276.1 | 334.2 | 368.1 | 630.9 | 549.8 | 502.9
2909.1 | 2277.1 | 334.5 | 368.4 | 633.7 | 549.2 | 505.2
2910.1 | 2278.1 | 334.9 | 368.6 | 631.5 | 547.1 | 506
2911.1 | 2279.1 | 335.2 | 368.9 | 635.4 | 554 | 505.1
2912.1 | 2280.1 | 335.5 | 369.2 | 634.9 | 556.6 | 504.9
2913.1 | 2281.1 | 335.9 | 369.5 | 634.4 | 559.8 | 507.4
2914.1 | 2282.1 | 336.3 | 369.7 | 631.5 | 559.4 | 507.7
2915.1 | 2283.1 | 336.6 | 370 | 635.2 | 558.3 | 506.9
2916.1 | 2284.1 | 336.9 | 370.3 | 636 | 556.7 | 506.8
2917.1 | 2285.1 | 337.2 | 370.6 | 638 | 559.6 | 508.6
2918.1 | 2286.1 | 337.6 | 370.9 | 640.7 | 558.8 | 508.1
2919.1 | 2287.1 | 337.9 | 371.2 | 642.7 | 560.8 | 511.6
2920.1 | 2288.1 | 338.2 | 371.5 | 640.6 | 563.4 | 513.3
2921.1 | 2289.1 | 338.6 | 371.7 | 639.3 | 556.4 | 514.2
2922.1 | 2290.1 | 338.8 | 372 | 644.3 | 553.7 | 516.2
2923.1 | 2291.1 | 339.2 | 372.4 | 635.7 | 550.1 | 516.3
2924.1 | 2292.1 | 339.5 | 372.6 | 632 | 554.4 | 517.4
2925.1 | 2293.1 | 339.8 | 372.9 | 630.7 | 560.5 | 517.6
2926.1 | 2294.1 | 339.9 | 373.2 | 636.9 | 569.8 | 518.1
2927.1 | 2295.1 | 340.3 | 373.5 | 638.9 | 569.7 | 517.6
2928.1 | 2296.1 | 340.7 | 373.7 | 645.5 | 580.1 | 519.1
2929.1 | 2297.1 | 341 | 374 | 640.3 | 574 | 519.7
2930.1 | 2298.1 | 341.3 | 374.4 | 642.5 | 579.1 | 520.6
2931.1 | 2299.1 | 341.7 | 374.6 | 640.2 | 575.1 | 519.4
2932.1 | 2300.1 | 341.9 | 374.9 | 641.2 | 572 | 518.1
2933.1 | 2301.1 | 342.2 | 375.3 | 636.5 | 579.8 | 517.5
2934.1 | 2302.1 | 342.4 | 375.6 | 635.3 | 576.4 | 517.3
2935.1 | 2303.1 | 342.8 | 375.8 | 638.9 | 573.4 | 516.7
2936.1 | 2304.1 | 343 | 376.1 | 633.7 | 582 | 516.9
2937.1 | 2305.1 | 343.3 | 376.4 | 633.6 | 581.6 | 516.7
2938.1 | 2306.1 | 343.6 | 376.7 | 633.6 | 578 | 516.5
2939.1 | 2307.1 | 343.9 | 376.9 | 629.9 | 576.6 | 516.1
2940.1 | 2308.1 | 344.2 | 377.2 | 626.9 | 571.7 | 515.3
2941.1 | 2309.1 | 344.4 | 377.5 | 627.3 | 568.3 | 514.5
2942.1 | 2310.1 | 344.7 | 377.8 | 623.4 | 565.2 | 513.7
2943.1 | 2311.1 | 345 | 378.1 | 629.1 | 563.4 | 512.9
2944.1 | 2312.1 | 345.3 | 378.4 | 634.3 | 562.4 | 512.5
2945.1 | 2313.1 | 345.6 | 378.7 | 631.4 | 568.7 | 513.8
2946.1 | 2314.1 | 345.9 | 378.9 | 630.6 | 578.5 | 515.2
2947.1 | 2315.1 | 346.2 | 379.3 | 631.4 | 574.9 | 513.8
2948.1 | 2316.1 | 346.5 | 379.5 | 630.6 | 570.3 | 512.8
2949.1 | 2317.1 | 346.9 | 379.7 | 628.2 | 575.9 | 514.3
2950.1 | 2318.1 | 347.1 | 380 | 622.9 | 571.6 | 513.5
2951.1 | 2319.1 | 347.4 | 380.3 | 614.8 | 586.5 | 512.8
2952.1 | 2320.1 | 347.7 | 380.6 | 621.1 | 583.1 | 513.5
2953.1 | 2321.1 | 348 | 380.8 | 626.1 | 576.6 | 512.6
2954.1 | 2322.1 | 348.3 | 381.1 | 628.4 | 576.3 | 512.6
2955.1 | 2323.1 | 348.5 | 381.3 | 630.4 | 587.4 | 514.7
2956.1 | 2324.1 | 348.9 | 381.6 | 626.2 | 584.2 | 514.4
2957.1 | 2325.1 | 349.2 | 381.9 | 628.7 | 577.3 | 515
2958.1 | 2326.1 | 349.5 | 382.2 | 623.5 | 574.2 | 516.5
2959.1 | 2327.1 | 349.8 | 382.4 | 634.6 | 587 | 519.4
2960.1 | 2328.1 | 350.1 | 382.6 | 633.5 | 586.6 | 519.8
2961.1 | 2329.1 | 350.4 | 382.9 | 630 | 582.4 | 518.7
2962.1 | 2330.1 | 350.7 | 383.2 | 634.9 | 577.9 | 517.9
2963.1 | 2331.1 | 351 | 383.3 | 636.9 | 574.2 | 517.6
2964.1 | 2332.1 | 351.3 | 383.6 | 638.5 | 571.1 | 516.5
2965.1 | 2333.1 | 351.5 | 383.8 | 644.4 | 570.3 | 515.9
2966.1 | 2334.1 | 351.8 | 384 | 641.5 | 568.5 | 515.5
2967.1 | 2335.1 | 352.1 | 384.2 | 640 | 569.6 | 516
2968.1 | 2336.1 | 352.4 | 384.4 | 633.7 | 564.6 | 515.4
2969.1 | 2337.1 | 352.7 | 384.6 | 637.7 | 565.8 | 515.1
2970.1 | 2338.1 | 353.1 | 384.8 | 646.4 | 574.8 | 516.3
2971.1 | 2339.1 | 353.4 | 385 | 638 | 571.4 | 515.7
2972.1 | 2340.1 | 353.7 | 385.3 | 636.8 | 575.4 | 515
2973.1 | 2341.1 | 353.9 | 385.5 | 633.1 | 584.7 | 515.7
2974.1 | 2342.1 | 354.2 | 385.7 | 632.8 | 585.9 | 516
2975.1 | 2343.1 | 354.5 | 386 | 627.2 | 582.6 | 516.2
2976.1 | 2344.1 | 354.8 | 386.2 | 620.5 | 575.4 | 516.9
2977.1 | 2345.1 | 355.2 | 386.4 | 616.9 | 579.5 | 519.5
2978.1 | 2346.1 | 355.4 | 386.6 | 616.5 | 579.7 | 518.7
2979.1 | 2347.1 | 355.8 | 386.9 | 612.5 | 575.1 | 517.8
2980.1 | 2348.1 | 356.1 | 387 | 620.3 | 578.5 | 517.6
2981.1 | 2349.1 | 356.3 | 387.3 | 618.6 | 574.5 | 517.2
2982.1 | 2350.1 | 356.6 | 387.5 | 618.9 | 571 | 516.3
2983.1 | 2351.1 | 356.8 | 387.7 | 627.9 | 571.2 | 515.5
2984.1 | 2352.1 | 357.1 | 387.8 | 635.4 | 579.1 | 515.5
2985.1 | 2353.1 | 357.4 | 388 | 635 | 581.4 | 515.7
2986.1 | 2354.1 | 357.7 | 388.2 | 633.1 | 583.9 | 516.1
2987.1 | 2355.1 | 358 | 388.4 | 634.4 | 585.1 | 516.2
2988.1 | 2356.1 | 358.3 | 388.5 | 630.6 | 583.1 | 516.2
2989.1 | 2357.1 | 358.6 | 388.8 | 631.2 | 586.6 | 517.7
2990.1 | 2358.1 | 358.9 | 389 | 628.6 | 591.5 | 517
2991.1 | 2359.1 | 359.2 | 389.1 | 627.7 | 604.3 | 516.8
2992.1 | 2360.1 | 359.4 | 389.4 | 623.2 | 597.4 | 516.6
2993.1 | 2361.1 | 359.7 | 389.6 | 624.6 | 591.4 | 516.2
2994.1 | 2362.1 | 360 | 389.8 | 625.1 | 586 | 515.2
2995.1 | 2363.1 | 360.3 | 390 | 623.4 | 583.1 | 514.5
2996.1 | 2364.1 | 360.6 | 390.2 | 617.2 | 578.7 | 513.9
2997.1 | 2365.1 | 360.9 | 390.4 | 618.2 | 581.3 | 513.5
2998.1 | 2366.1 | 361.1 | 390.5 | 624.7 | 586.6 | 512.7
2999.1 | 2367.1 | 361.4 | 390.8 | 626.6 | 594.3 | 513.4
3000.1 | 2368.1 | 361.7 | 391 | 628.5 | 589 | 512.9
3001.1 | 2369.1 | 362 | 391.3 | 621.4 | 583 | 511.7
3002.1 | 2370.1 | 362.4 | 391.5 | 620.4 | 580.6 | 511.1
3003.1 | 2371.1 | 362.7 | 391.8 | 622.2 | 578.7 | 511
3004.1 | 2372.1 | 363 | 392 | 618.7 | 586.6 | 511.5
3005.1 | 2373.1 | 363.3 | 392.3 | 623 | 588.5 | 512.7
3006.1 | 2374.1 | 363.5 | 392.6 | 625.6 | 584.6 | 511.8
3007.1 | 2375.1 | 363.8 | 392.8 | 623.4 | 579.6 | 510.9
3008.1 | 2376.1 | 364.2 | 393 | 623 | 574 | 510.2
3009.1 | 2377.1 | 364.5 | 393.3 | 627.3 | 569 | 509.4
3010.1 | 2378.1 | 364.7 | 393.5 | 621.1 | 565.3 | 508.2
3011.1 | 2379.1 | 365 | 393.8 | 614.3 | 560.3 | 507.1
3012.1 | 2380.1 | 365.3 | 394 | 609.8 | 556.7 | 506.6
3013.1 | 2381.1 | 365.5 | 394.2 | 608.9 | 553.5 | 506.1
3014.1 | 2382.1 | 365.7 | 394.4 | 615.5 | 552.5 | 506.3
3015.1 | 2383.1 | 365.9 | 394.6 | 611.7 | 554.4 | 505.4
3016.1 | 2384.1 | 366.2 | 394.8 | 611.5 | 552.2 | 504.6
3017.1 | 2385.1 | 366.4 | 395.1 | 603.2 | 548.6 | 504.2
3018.1 | 2386.1 | 366.6 | 395.4 | 607.6 | 548.7 | 504.3
3019.1 | 2387.1 | 366.9 | 395.5 | 610.8 | 546.4 | 503.5
3020.1 | 2388.1 | 367.1 | 395.7 | 603.5 | 544.5 | 502.8
3021.1 | 2389.1 | 367.3 | 396 | 600.1 | 545 | 502.2
3022.1 | 2390.1 | 367.6 | 396.1 | 607 | 545.6 | 501.7
3023.1 | 2391.1 | 367.8 | 396.3 | 609.3 | 546.5 | 501.4
3024.1 | 2392.1 | 368 | 396.6 | 613.7 | 547 | 501
3025.1 | 2393.1 | 368.3 | 396.8 | 615.1 | 557.8 | 501.4
3026.1 | 2394.1 | 368.5 | 397 | 616.5 | 559.9 | 502.4
3027.1 | 2395.1 | 368.7 | 397.3 | 616 | 560.4 | 502.2
3028.1 | 2396.1 | 369 | 397.5 | 617.4 | 582.7 | 503.6
3029.1 | 2397.1 | 369.2 | 397.7 | 618.8 | 583.4 | 504.2
3030.1 | 2398.1 | 369.5 | 397.9 | 625.8 | 582.1 | 504.2
3031.1 | 2399.1 | 369.8 | 398.2 | 625.5 | 581.3 | 504.3
3032.1 | 2400.1 | 370 | 398.4 | 627.4 | 583.2 | 505
3033.1 | 2401.1 | 370.4 | 398.6 | 634.6 | 584.6 | 506.1
3034.1 | 2402.1 | 370.6 | 398.8 | 636.2 | 578.9 | 506.4
3035.1 | 2403.1 | 370.8 | 399 | 631 | 574.9 | 506.6
3036.1 | 2404.1 | 371.1 | 399.2 | 634.6 | 575.5 | 508.1
3037.1 | 2405.1 | 371.4 | 399.4 | 637.6 | 576.9 | 509
3038.1 | 2406.1 | 371.5 | 399.6 | 640.4 | 574.8 | 508.3
3039.1 | 2407.1 | 371.7 | 399.8 | 639.5 | 571.6 | 507.9
3040.1 | 2408.1 | 372 | 400 | 641.1 | 568.6 | 507.4
3041.1 | 2409.1 | 372.2 | 400.2 | 637.7 | 573.8 | 507.8
3042.1 | 2410.1 | 372.5 | 400.5 | 635.4 | 572.8 | 509.7
3043.1 | 2411.1 | 372.7 | 400.7 | 631.9 | 572.8 | 510.3
3044.1 | 2412.1 | 373.1 | 400.8 | 627.5 | 570.7 | 512.1
3045.1 | 2413.1 | 373.2 | 401.2 | 626.4 | 568.4 | 513.1
3046.1 | 2414.1 | 373.5 | 401.4 | 626.8 | 572.4 | 513.8
3047.1 | 2415.1 | 373.8 | 401.6 | 629.4 | 571.7 | 513.2
3048.1 | 2416.1 | 373.9 | 401.8 | 634.2 | 573.1 | 512.6
3049.1 | 2417.1 | 374.1 | 402.1 | 640.9 | 578.8 | 512.7
3050.1 | 2418.1 | 374.4 | 402.3 | 641.3 | 593 | 513.2
3051.1 | 2419.1 | 374.7 | 402.6 | 642.4 | 596.6 | 514.6
3052.1 | 2420.1 | 374.9 | 402.8 | 643.7 | 593 | 516.5
3053.1 | 2421.1 | 375 | 402.9 | 641 | 590 | 516.6
3054.1 | 2422.1 | 375.2 | 403 | 636.8 | 597 | 518.3
3055.1 | 2423.1 | 375.5 | 403.3 | 636.4 | 596.9 | 519.3
3056.1 | 2424.1 | 375.6 | 403.4 | 640.6 | 596.4 | 519.3
3057.1 | 2425.1 | 375.8 | 403.6 | 641.8 | 596.7 | 520
3058.1 | 2426.1 | 376 | 403.7 | 643.2 | 601.4 | 521.2
3059.1 | 2427.1 | 376.1 | 403.9 | 645.9 | 597.8 | 521.1
3060.1 | 2428.1 | 376.3 | 404.1 | 640.6 | 594.6 | 521.7
3061.1 | 2429.1 | 376.6 | 404.3 | 640.4 | 601 | 522.6
3062.1 | 2430.1 | 376.8 | 404.6 | 643.6 | 593.6 | 523.6
3063.1 | 2431.1 | 377 | 404.8 | 636.6 | 589.6 | 524.5
3064.1 | 2432.1 | 377.3 | 405 | 633.5 | 593.8 | 524.5
3065.1 | 2433.1 | 377.4 | 405.1 | 633.5 | 588.1 | 523.3
3066.1 | 2434.1 | 377.6 | 405.4 | 650.5 | 583 | 522.5
3067.1 | 2435.1 | 377.9 | 405.7 | 653.2 | 583.2 | 522.2
3068.1 | 2436.1 | 378.1 | 406 | 655.4 | 588.1 | 522.2
3069.1 | 2437.1 | 378.3 | 406.3 | 652.8 | 592.5 | 523.8
3070.1 | 2438.1 | 378.6 | 406.6 | 648.3 | 592.2 | 524.7
3071.1 | 2439.1 | 378.9 | 406.9 | 650 | 593.1 | 523.2
3072.1 | 2440.1 | 379.2 | 407.3 | 648.8 | 595.5 | 522.2
3073.1 | 2441.1 | 379.4 | 407.6 | 652.1 | 596.5 | 522.1
3074.1 | 2442.1 | 379.6 | 407.9 | 656 | 604.3 | 522.8
3075.1 | 2443.1 | 379.9 | 408.1 | 655.8 | 606.9 | 524.9
3076.1 | 2444.1 | 380 | 408.4 | 651.9 | 613.8 | 526
3077.1 | 2445.1 | 380.1 | 408.6 | 649.1 | 617.6 | 525.9
3078.1 | 2446.1 | 380.3 | 408.6 | 647.3 | 611.2 | 525.1
3079.1 | 2447.1 | 380.4 | 408.7 | 648 | 610.7 | 524.5
3080.1 | 2448.1 | 380.5 | 408.9 | 650.9 | 612.1 | 524.9
3081.1 | 2449.1 | 380.7 | 409.1 | 646.3 | 619.8 | 525.9
3082.1 | 2450.1 | 380.9 | 409.2 | 643.3 | 622 | 525.7
3083.1 | 2451.1 | 381 | 409.4 | 647.9 | 622.3 | 526.6
3084.1 | 2452.1 | 381.2 | 409.6 | 639 | 619.3 | 527.6
3085.1 | 2453.1 | 381.2 | 409.6 | 637.3 | 627 | 528.5
3086.1 | 2454.1 | 381.4 | 409.7 | 637.5 | 627.4 | 528
3087.1 | 2455.1 | 381.6 | 410 | 632.8 | 620.3 | 527.1
3088.1 | 2456.1 | 381.7 | 410.2 | 628.7 | 613.4 | 525.9
3089.1 | 2457.1 | 382 | 410.5 | 630.7 | 609.2 | 525.5
3090.1 | 2458.1 | 382.3 | 410.9 | 639 | 605.1 | 525.3
3091.1 | 2459.1 | 382.5 | 411.2 | 645.3 | 603.6 | 524.5
3092.1 | 2460.1 | 382.8 | 411.4 | 651.1 | 613.9 | 525.1
3093.1 | 2461.1 | 382.8 | 411.5 | 654.9 | 617.8 | 525.1
3094.1 | 2462.1 | 382.9 | 411.5 | 657.9 | 618.9 | 527.2
3095.1 | 2463.1 | 383.1 | 411.8 | 653.1 | 622.5 | 530
3096.1 | 2464.1 | 383.4 | 412 | 652.8 | 624.5 | 530.5
3097.1 | 2465.1 | 383.6 | 412.3 | 653.4 | 627.4 | 530.3
3098.1 | 2466.1 | 383.7 | 412.6 | 650.4 | 622.8 | 530.3
3099.1 | 2467.1 | 383.8 | 412.7 | 650.4 | 610 | 531.2
3100.1 | 2468.1 | 383.9 | 412.7 | 645.2 | 600.9 | 532.7
3101.1 | 2469.1 | 384.1 | 413 | 644.5 | 600.1 | 532.7
3102.1 | 2470.1 | 384.2 | 413.2 | 646.9 | 604.1 | 531.7
3103.1 | 2471.1 | 384.4 | 413.3 | 647.5 | 607.8 | 531.2
3104.1 | 2472.1 | 384.5 | 413.4 | 648.3 | 604.3 | 531.2
3105.1 | 2473.1 | 384.6 | 413.5 | 651.2 | 605.3 | 531.3
3106.1 | 2474.1 | 384.8 | 413.8 | 644.6 | 602.9 | 529.7
3107.1 | 2475.1 | 385.1 | 414.1 | 646 | 601.7 | 528.6
3108.1 | 2476.1 | 385.3 | 414.2 | 651.5 | 607.3 | 528.5
3109.1 | 2477.1 | 385.4 | 414.5 | 652.6 | 617.7 | 529.2
3110.1 | 2478.1 | 385.7 | 414.8 | 650.3 | 611.5 | 531
3111.1 | 2479.1 | 386 | 415 | 645.8 | 615 | 532
3112.1 | 2480.1 | 386.1 | 415.2 | 651.9 | 614.6 | 533.3
3113.1 | 2481.1 | 386.3 | 415.4 | 652.7 | 612.8 | 533.5
3114.1 | 2482.1 | 386.5 | 415.6 | 646.8 | 607.7 | 532
3115.1 | 2483.1 | 386.5 | 415.7 | 639.4 | 600.5 | 530.6
3116.1 | 2484.1 | 386.7 | 415.8 | 641.8 | 596 | 529.5
3117.1 | 2485.1 | 386.9 | 416 | 644.5 | 593.1 | 529.9
3118.1 | 2486.1 | 387 | 416.3 | 642.8 | 590.6 | 529
3119.1 | 2487.1 | 387.3 | 416.7 | 642.2 | 588.4 | 528.3
3120.1 | 2488.1 | 387.5 | 416.8 | 640.9 | 587.6 | 528.2
3121.1 | 2489.1 | 387.7 | 417 | 638.1 | 592.4 | 530
3122.1 | 2490.1 | 387.9 | 417.2 | 634.7 | 587.9 | 529.4
3123.1 | 2491.1 | 388.1 | 417.4 | 638.7 | 591.5 | 528.4
3124.1 | 2492.1 | 388.3 | 417.6 | 639.5 | 588.9 | 527.4
3125.1 | 2493.1 | 388.4 | 417.7 | 643.5 | 599.2 | 527.4
3126.1 | 2494.1 | 388.6 | 418 | 643.8 | 605 | 530.1
3127.1 | 2495.1 | 388.8 | 418.2 | 642.6 | 609.3 | 531.5
3128.1 | 2496.1 | 389.1 | 418.4 | 640.7 | 605.2 | 530.9
3129.1 | 2497.1 | 389.2 | 418.7 | 638.8 | 599.9 | 530.4
3130.1 | 2498.1 | 389.4 | 418.9 | 637.6 | 599.6 | 532.1
3131.1 | 2499.1 | 389.7 | 419 | 637.4 | 605.5 | 533
3132.1 | 2500.1 | 389.7 | 419.1 | 635.5 | 600.7 | 531.9
3133.1 | 2501.1 | 389.8 | 419.1 | 641 | 601.2 | 530.9
3134.1 | 2502.1 | 390.1 | 419.3 | 637.7 | 596.8 | 530
3135.1 | 2503.1 | 390.4 | 419.6 | 632.4 | 591.3 | 528.8
3136.1 | 2504.1 | 390.4 | 419.8 | 639 | 589.7 | 528.5
3137.1 | 2505.1 | 390.6 | 420 | 639.5 | 594.4 | 527.3
3138.1 | 2506.1 | 391 | 420.2 | 636 | 594.4 | 526.3
3139.1 | 2507.1 | 391.1 | 420.4 | 632 | 591.3 | 526.2
3140.1 | 2508.1 | 391.3 | 420.6 | 634.2 | 591.2 | 525.7
3141.1 | 2509.1 | 391.5 | 420.8 | 633.8 | 589.1 | 524.7
3142.1 | 2510.1 | 391.9 | 421.3 | 628 | 589.5 | 525.2
3143.1 | 2511.1 | 391.9 | 421.3 | 624.6 | 591.7 | 525.7
3144.1 | 2512.1 | 392.1 | 421.5 | 631.2 | 589.7 | 524.9
3145.1 | 2513.1 | 392.4 | 421.7 | 637.9 | 595.5 | 525.8
3146.1 | 2514.1 | 392.6 | 421.9 | 637.7 | 599.9 | 528.2
3147.1 | 2515.1 | 392.8 | 422.1 | 633.7 | 600.2 | 529.7
3148.1 | 2516.1 | 393 | 422.2 | 633.6 | 597.2 | 529.3
3149.1 | 2517.1 | 393.3 | 422.5 | 636.2 | 603 | 529.1
3150.1 | 2518.1 | 393.5 | 422.7 | 639.2 | 603.1 | 529.9
3151.1 | 2519.1 | 393.6 | 422.8 | 636.8 | 599.3 | 529.1
3152.1 | 2520.1 | 393.9 | 423 | 634.8 | 594.3 | 528.3
3153.1 | 2521.1 | 394.2 | 423.1 | 633 | 586.2 | 527
3154.1 | 2522.1 | 394.3 | 423.2 | 631 | 596.9 | 527.4
3155.1 | 2523.1 | 394.6 | 423.4 | 631.7 | 601.6 | 530.5
3156.1 | 2524.1 | 394.7 | 423.7 | 635.2 | 597.1 | 533.1
3157.1 | 2525.1 | 394.9 | 423.8 | 636.8 | 594 | 533.9
3158.1 | 2526.1 | 395.1 | 424 | 632.3 | 594.6 | 533
3159.1 | 2527.1 | 395.4 | 424.3 | 634.4 | 595.5 | 533.6
3160.1 | 2528.1 | 395.6 | 424.5 | 635.3 | 594.1 | 533.1
3161.1 | 2529.1 | 395.7 | 424.6 | 636.3 | 599.4 | 532.5
3162.1 | 2530.1 | 395.9 | 424.6 | 633.3 | 595.3 | 531.9
3163.1 | 2531.1 | 396 | 424.6 | 632.1 | 595.4 | 532.7
3164.1 | 2532.1 | 396.2 | 424.9 | 632.5 | 598.9 | 533.1
3165.1 | 2533.1 | 396.4 | 425.2 | 631.3 | 602.2 | 534.4
3166.1 | 2534.1 | 396.7 | 425.4 | 629.4 | 604.4 | 534.2
3167.1 | 2535.1 | 396.9 | 425.7 | 630 | 603.8 | 534.5
3168.1 | 2536.1 | 397.3 | 426.1 | 630.8 | 601.4 | 534.1
3169.1 | 2537.1 | 397.5 | 426.1 | 633.4 | 610.9 | 534.7
3170.1 | 2538.1 | 397.7 | 426.3 | 636.8 | 614.6 | 535.9
3171.1 | 2539.1 | 397.9 | 426.5 | 638.2 | 613.6 | 537
3172.1 | 2540.1 | 398.1 | 426.5 | 635.5 | 611 | 539.4
3173.1 | 2541.1 | 398.2 | 426.6 | 632 | 605.7 | 540.9
3174.1 | 2542.1 | 398.4 | 426.7 | 629.8 | 599.1 | 541.6
3175.1 | 2543.1 | 398.6 | 427 | 632.3 | 593.1 | 541.7
3176.1 | 2544.1 | 398.7 | 426.9 | 633.7 | 590.6 | 541.7
3177.1 | 2545.1 | 398.8 | 427 | 633.8 | 585.5 | 542.6
3178.1 | 2546.1 | 398.8 | 426.9 | 638.6 | 583.8 | 544.5
3179.1 | 2547.1 | 398.9 | 426.9 | 641.6 | 585.9 | 544.9
3180.1 | 2548.1 | 399.2 | 427.1 | 639.1 | 592.1 | 545.1
3181.1 | 2549.1 | 399.4 | 427.4 | 641.3 | 590.5 | 544.6
3182.1 | 2550.1 | 399.7 | 427.7 | 641.3 | 583.7 | 545.2
3183.1 | 2551.1 | 399.9 | 427.9 | 639.4 | 588.1 | 545.8
3184.1 | 2552.1 | 400.1 | 428 | 636 | 585.3 | 546.9
3185.1 | 2553.1 | 400.3 | 428.1 | 634 | 586 | 548
3186.1 | 2554.1 | 400.5 | 428.3 | 635.3 | 587.8 | 548.2
3187.1 | 2555.1 | 400.6 | 428.5 | 634.1 | 593 | 550.2
3188.1 | 2556.1 | 401 | 428.7 | 626.4 | 594.3 | 550.5
3189.1 | 2557.1 | 401.1 | 428.8 | 626.2 | 594.6 | 549.9
3190.1 | 2558.1 | 401.1 | 428.9 | 628.4 | 598.6 | 549.8
3191.1 | 2559.1 | 401.4 | 429.1 | 626 | 593.2 | 549
3192.1 | 2560.1 | 401.7 | 429.4 | 620.5 | 597.7 | 549.8
3193.1 | 2561.1 | 402 | 429.7 | 617.8 | 599.4 | 550.5
3194.1 | 2562.1 | 402.3 | 429.7 | 617.3 | 599.3 | 549.7
3195.1 | 2563.1 | 402.6 | 429.9 | 619.1 | 596.7 | 548.9
3196.1 | 2564.1 | 402.8 | 430.2 | 622 | 594.8 | 549.6
3197.1 | 2565.1 | 403.1 | 430.5 | 624.2 | 589.3 | 549.8
3198.1 | 2566.1 | 403.5 | 430.6 | 620.2 | 582.5 | 549.8
3199.1 | 2567.1 | 403.9 | 430.9 | 617 | 586.4 | 550.4
3200.1 | 2568.1 | 404.2 | 431.2 | 620.4 | 602 | 550.8
3201.1 | 2569.1 | 404.5 | 431.2 | 624 | 609.5 | 550.6
3202.1 | 2570.1 | 404.6 | 431.2 | 627.9 | 617.4 | 550.3
3203.1 | 2571.1 | 404.7 | 431.5 | 632.7 | 623.3 | 550.9
3204.1 | 2572.1 | 405 | 431.7 | 634.9 | 623.2 | 552
3205.1 | 2573.1 | 405.3 | 432 | 631.3 | 617.9 | 552.3
3206.1 | 2574.1 | 405.5 | 432.2 | 627.6 | 618.2 | 553.5
3207.1 | 2575.1 | 405.5 | 432.2 | 627.4 | 618.5 | 553.1
3208.1 | 2576.1 | 405.8 | 432.3 | 629.2 | 613.3 | 552.8
3209.1 | 2577.1 | 406.1 | 432.5 | 627.1 | 605.5 | 553.6
3210.1 | 2578.1 | 406.5 | 432.8 | 628.2 | 606 | 555.8
3211.1 | 2579.1 | 406.7 | 432.8 | 625.8 | 600.7 | 557.6
3212.1 | 2580.1 | 406.8 | 432.9 | 625.7 | 602.1 | 558.2
3213.1 | 2581.1 | 407.1 | 432.9 | 624.7 | 612.6 | 558.7
3214.1 | 2582.1 | 407 | 432.8 | 623 | 615 | 557.8
3215.1 | 2583.1 | 407.4 | 432.9 | 624.3 | 624.5 | 557.6
3216.1 | 2584.1 | 407.4 | 433.1 | 625.8 | 636.5 | 557.8
3217.1 | 2585.1 | 407.8 | 433.2 | 626.2 | 639.6 | 559.1
3218.1 | 2586.1 | 408.2 | 433.3 | 626.1 | 644.3 | 559.5
3219.1 | 2587.1 | 408.2 | 433.3 | 625.8 | 649 | 560.1
3220.1 | 2588.1 | 408.1 | 433.3 | 624.8 | 641.7 | 559.5
3221.1 | 2589.1 | 408.4 | 433.5 | 624.4 | 640.1 | 559.5
3222.1 | 2590.1 | 408.7 | 433.6 | 624.5 | 640.2 | 559.8
3223.1 | 2591.1 | 409 | 433.9 | 622.3 | 640.1 | 559.3
3224.1 | 2592.1 | 409.3 | 434 | 619.8 | 641.7 | 559.5
3225.1 | 2593.1 | 409 | 433.9 | 621.5 | 635.9 | 560
3226.1 | 2594.1 | 409.2 | 433.9 | 621 | 634 | 559.6
3227.1 | 2595.1 | 409.4 | 434.1 | 620.2 | 635.3 | 559.6
3228.1 | 2596.1 | 409.7 | 434.2 | 622.9 | 635.1 | 561
3229.1 | 2597.1 | 410 | 434.2 | 624.7 | 632 | 561.1
3230.1 | 2598.1 | 410.2 | 434.4 | 624.7 | 631.8 | 561.9
3231.1 | 2599.1 | 410.6 | 434.7 | 623.9 | 626.7 | 562.1
3232.1 | 2600.1 | 410.9 | 434.7 | 622.9 | 621.9 | 561.7
3233.1 | 2601.1 | 411.2 | 434.8 | 620.2 | 621.9 | 560.9
3234.1 | 2602.1 | 411.5 | 435 | 619.4 | 620.5 | 560.1
3235.1 | 2603.1 | 411.6 | 435.1 | 617.1 | 620.6 | 559.9
3236.1 | 2604.1 | 411.9 | 435.3 | 615.8 | 618.9 | 559.3
3237.1 | 2605.1 | 412.2 | 435.4 | 616.3 | 615.8 | 559.1
3238.1 | 2606.1 | 412.4 | 435.5 | 614.6 | 610.5 | 558.4
3239.1 | 2607.1 | 412.3 | 435.5 | 613.4 | 607 | 557.7
3240.1 | 2608.1 | 412.5 | 435.6 | 616.3 | 611.4 | 556.7
3241.1 | 2609.1 | 412.7 | 435.7 | 618.5 | 622.2 | 557.3
3242.1 | 2610.1 | 412.6 | 435.8 | 618.7 | 620.8 | 557.1
3243.1 | 2611.1 | 413.2 | 436.1 | 625.3 | 614.1 | 557.3
3244.1 | 2612.1 | 413.4 | 436.3 | 623.8 | 609.5 | 557.7
3245.1 | 2613.1 | 413.4 | 436.5 | 623 | 612.5 | 557.4
3246.1 | 2614.1 | 414 | 436.8 | 620.6 | 609.8 | 556.7
3247.1 | 2615.1 | 414.2 | 436.8 | 618.1 | 606.3 | 557
3248.1 | 2616.1 | 414.2 | 436.8 | 617 | 601.4 | 555.6
3249.1 | 2617.1 | 414.1 | 436.8 | 624.8 | 604.4 | 554.5
3250.1 | 2618.1 | 414.5 | 436.8 | 625.9 | 607.2 | 555
3251.1 | 2619.1 | 414.7 | 437 | 624.8 | 606.1 | 555.9
3252.1 | 2620.1 | 415.2 | 437.3 | 626 | 615.1 | 556.7
3253.1 | 2621.1 | 415.3 | 437.4 | 624.4 | 619.3 | 555.8
3254.1 | 2622.1 | 415.5 | 437.5 | 622.5 | 623.3 | 555.5
3255.1 | 2623.1 | 415.6 | 437.5 | 623.1 | 619.8 | 554.5
3256.1 | 2624.1 | 415.9 | 437.6 | 622 | 621.6 | 556.3
3257.1 | 2625.1 | 416.2 | 437.6 | 624.3 | 617.8 | 556.3
3258.1 | 2626.1 | 416.4 | 437.6 | 623.6 | 620.1 | 556.3
3259.1 | 2627.1 | 416.8 | 437.8 | 625.1 | 622.7 | 556.9
3260.1 | 2628.1 | 416.6 | 437.9 | 621.8 | 633 | 557.2
3261.1 | 2629.1 | 416.9 | 438 | 622.3 | 629.5 | 557.8
3262.1 | 2630.1 | 417.2 | 438.3 | 624 | 632.6 | 557.6
3263.1 | 2631.1 | 417.5 | 438.5 | 624.4 | 643.9 | 557.3
3264.1 | 2632.1 | 417.8 | 438.5 | 624.3 | 638.2 | 558.3
3265.1 | 2633.1 | 417.8 | 438.7 | 623.2 | 635.9 | 558.2
3266.1 | 2634.1 | 418 | 438.9 | 621.9 | 634.2 | 558.7
3267.1 | 2635.1 | 418.4 | 439.2 | 619.8 | 625 | 559.4
3268.1 | 2636.1 | 418.9 | 439.4 | 620.4 | 624.4 | 559.8
3269.1 | 2637.1 | 419.2 | 439.6 | 617.1 | 613.7 | 559.5
3270.1 | 2638.1 | 419.6 | 439.6 | 615.1 | 616.7 | 559.9
3271.1 | 2639.1 | 419.7 | 439.6 | 617.4 | 623.6 | 560.4
3272.1 | 2640.1 | 420.1 | 439.7 | 615.7 | 617.7 | 560.8
3273.1 | 2641.1 | 420.4 | 439.7 | 611.1 | 607.4 | 561.5
3274.1 | 2642.1 | 420 | 439.8 | 608.8 | 607.9 | 561
3275.1 | 2643.1 | 420.4 | 439.8 | 609.8 | 605.8 | 560.8
3276.1 | 2644.1 | 420.8 | 439.9 | 607.2 | 604.6 | 560.7
3277.1 | 2645.1 | 421 | 439.8 | 607.6 | 614.6 | 560.6
3278.1 | 2646.1 | 421 | 439.7 | 604.7 | 610.2 | 560.1
3279.1 | 2647.1 | 420.9 | 439.8 | 605.4 | 615.3 | 560
3280.1 | 2648.1 | 421.3 | 440 | 606.4 | 611.4 | 559.1
3281.1 | 2649.1 | 421.4 | 440.2 | 605.6 | 610.8 | 559.1
3282.1 | 2650.1 | 421.5 | 440.2 | 604.8 | 609 | 558.7
3283.1 | 2651.1 | 421.7 | 440.3 | 608.9 | 616.3 | 558.4
3284.1 | 2652.1 | 422 | 440.3 | 610 | 617.1 | 557.9
3285.1 | 2653.1 | 422.2 | 440.4 | 608.1 | 619.1 | 557.1
3286.1 | 2654.1 | 422.5 | 440.5 | 608.6 | 623.9 | 557.4
3287.1 | 2655.1 | 422.7 | 440.7 | 607.8 | 615.8 | 557
3288.1 | 2656.1 | 423.1 | 440.7 | 607.1 | 616.2 | 556.4
3289.1 | 2657.1 | 423.2 | 440.7 | 608.3 | 619.9 | 555.9
3290.1 | 2658.1 | 423 | 441 | 608.3 | 613.6 | 556.6
3291.1 | 2659.1 | 423.7 | 441.1 | 609 | 626.7 | 557.5
3292.1 | 2660.1 | 424.2 | 441.2 | 611.5 | 617.1 | 558.5
3293.1 | 2661.1 | 424.5 | 441.4 | 607.8 | 610.3 | 557.7
3294.1 | 2662.1 | 424.6 | 441.5 | 606.2 | 612.9 | 557.3
3295.1 | 2663.1 | 424.6 | 441.6 | 606.4 | 620.6 | 557.1
3296.1 | 2664.1 | 424.8 | 441.6 | 606.6 | 616.4 | 556.6
3297.1 | 2665.1 | 425.3 | 441.7 | 606.7 | 623.4 | 557.4
3298.1 | 2666.1 | 425.5 | 441.9 | 605.2 | 634.7 | 557.7
3299.1 | 2667.1 | 425.8 | 442 | 605.1 | 640 | 557.6
3300.1 | 2668.1 | 426 | 442.2 | 606.6 | 638 | 557
3301.1 | 2669.1 | 426.1 | 442.3 | 605.4 | 633.9 | 556.3
3302.1 | 2670.1 | 426.3 | 442.4 | 603.2 | 627.1 | 555.7
3303.1 | 2671.1 | 426.2 | 442.2 | 600.2 | 631.8 | 555.5
3304.1 | 2672.1 | 426.1 | 442.4 | 598.3 | 627.7 | 554.7
3305.1 | 2673.1 | 426.3 | 442.2 | 599.4 | 619 | 553.7
3306.1 | 2674.1 | 426.5 | 442.1 | 600.7 | 621.6 | 553.7
3307.1 | 2675.1 | 426.7 | 442.3 | 601.8 | 617.8 | 554.6
3308.1 | 2676.1 | 427.3 | 442.5 | 600.9 | 613.6 | 555.3
3309.1 | 2677.1 | 427.9 | 442.6 | 598.8 | 605.3 | 555.9
3310.1 | 2678.1 | 428.3 | 442.6 | 593.9 | 609.7 | 555.4
3311.1 | 2679.1 | 428.6 | 442.7 | 591.6 | 613.9 | 554.6
3312.1 | 2680.1 | 428.3 | 442.3 | 590.2 | 612 | 554.3
3313.1 | 2681.1 | 428.2 | 442.2 | 586.6 | 606.5 | 552.6
3314.1 | 2682.1 | 428.5 | 442.3 | 584 | 611.5 | 550.9
3315.1 | 2683.1 | 428.7 | 442.2 | 581.1 | 605 | 549.6
3316.1 | 2684.1 | 428.5 | 442.1 | 577.4 | 591.5 | 548.7
3317.1 | 2685.1 | 428.4 | 442 | 572 | 582.1 | 548.9
3318.1 | 2686.1 | 428.5 | 442.1 | 569.6 | 581.9 | 549.4
3319.1 | 2687.1 | 428.9 | 442.2 | 565.9 | 574.3 | 548
3320.1 | 2688.1 | 429.2 | 442.1 | 562.9 | 569 | 548
3321.1 | 2689.1 | 429.5 | 442.2 | 561.1 | 563 | 546.8
3322.1 | 2690.1 | 429.6 | 442.1 | 559 | 556.1 | 546
3323.1 | 2691.1 | 430 | 442.1 | 555.6 | 548.2 | 544.8
3324.1 | 2692.1 | 430.2 | 442.2 | 552.7 | 541.1 | 544
3325.1 | 2693.1 | 430.4 | 442.2 | 550.2 | 535 | 543.6
3326.1 | 2694.1 | 430.6 | 442.3 | 549.1 | 536.2 | 542.6
3327.1 | 2695.1 | 430.8 | 442.3 | 549.3 | 547.3 | 543.1
3328.1 | 2696.1 | 431 | 442.4 | 547.9 | 544.4 | 542
3329.1 | 2697.1 | 431.2 | 442.5 | 546.2 | 541.7 | 541.1
3330.1 | 2698.1 | 431.1 | 442.5 | 545.3 | 539.4 | 540.3
3331.1 | 2699.1 | 431.2 | 442.6 | 544.5 | 537.7 | 539.7
3332.1 | 2700.1 | 431.5 | 442.7 | 543.7 | 535.8 | 539.2
3333.1 | 2701.1 | 431.6 | 442.8 | 542.2 | 532.5 | 538.5
3334.1 | 2702.1 | 431.5 | 442.8 | 540.3 | 534.9 | 538.2
3335.1 | 2703.1 | 431.8 | 442.9 | 539.4 | 538.3 | 538.4
3336.1 | 2704.1 | 432 | 443 | 537.5 | 535.3 | 538.1
3337.1 | 2705.1 | 432 | 443.1 | 536 | 532.8 | 537.2
3338.1 | 2706.1 | 432.1 | 443.2 | 534.3 | 529.9 | 536.4
3339.1 | 2707.1 | 432.2 | 443.3 | 533.8 | 531.7 | 536.4
3340.1 | 2708.1 | 432.3 | 443.5 | 533.8 | 539.6 | 535.8
3341.1 | 2709.1 | 432.5 | 443.5 | 534.3 | 535.8 | 535.2
3342.1 | 2710.1 | 432.2 | 443.6 | 534.2 | 536.9 | 534.7
3343.1 | 2711.1 | 432.6 | 443.6 | 533.8 | 539.9 | 534.3
3344.1 | 2712.1 | 433.1 | 443.7 | 533.8 | 546.7 | 533.9
3345.1 | 2713.1 | 433.2 | 443.8 | 533.7 | 543.3 | 532.9
3346.1 | 2714.1 | 433.5 | 443.9 | 532.1 | 539.4 | 531.8
3347.1 | 2715.1 | 433.6 | 443.9 | 530.5 | 538.6 | 531.3
3348.1 | 2716.1 | 433.6 | 444 | 529.6 | 544.4 | 531
3349.1 | 2717.1 | 433.9 | 444 | 529 | 542.3 | 530.3
3350.1 | 2718.1 | 433.8 | 443.9 | 528.3 | 537.5 | 529.5
3351.1 | 2719.1 | 434 | 444 | 527.6 | 531.9 | 528.9
3352.1 | 2720.1 | 434.3 | 444 | 526.3 | 528.2 | 529.5
3353.1 | 2721.1 | 434.4 | 444 | 525.9 | 524.4 | 528.8
3354.1 | 2722.1 | 434.8 | 444.1 | 524.8 | 520.8 | 528.3
3355.1 | 2723.1 | 434.5 | 444.2 | 523.6 | 517.1 | 527.9
3356.1 | 2724.1 | 434.6 | 444.2 | 522.6 | 515.1 | 528
3357.1 | 2725.1 | 434.7 | 444.2 | 521.9 | 512.6 | 527.6
3358.1 | 2726.1 | 434.4 | 444.1 | 521.5 | 510.1 | 528.5
3359.1 | 2727.1 | 434.5 | 444 | 520.3 | 506.8 | 528.2
3360.1 | 2728.1 | 434.9 | 444.1 | 519.8 | 503 | 526.8
3361.1 | 2729.1 | 435.3 | 444.1 | 518.6 | 499.3 | 525.6
3362.1 | 2730.1 | 435.2 | 444.1 | 517 | 496.5 | 526.1
3363.1 | 2731.1 | 434.9 | 444 | 516 | 493.9 | 527.1
3364.1 | 2732.1 | 435.2 | 444 | 514.7 | 490.6 | 525.4
3365.1 | 2733.1 | 434.9 | 443.9 | 513.8 | 490.1 | 526.3
3366.1 | 2734.1 | 435.2 | 443.8 | 512.3 | 486.9 | 525.4
3367.1 | 2735.1 | 435.4 | 443.8 | 511.4 | 483.9 | 523.6
3368.1 | 2736.1 | 435.9 | 443.7 | 510.6 | 480.8 | 522.2
3369.1 | 2737.1 | 435.9 | 443.7 | 509.3 | 478 | 521.1
3370.1 | 2738.1 | 436.1 | 443.7 | 507.8 | 475.4 | 519.8
3371.1 | 2739.1 | 436.4 | 443.5 | 506.5 | 472.9 | 518.4
3372.1 | 2740.1 | 435.4 | 443.3 | 505.3 | 471 | 517.3
3373.1 | 2741.1 | 435.9 | 443.2 | 503.9 | 469 | 516.3
3374.1 | 2742.1 | 436.5 | 443.1 | 503.4 | 467.1 | 515.3
3375.1 | 2743.1 | 436.3 | 442.9 | 502.7 | 465.5 | 514.6
3376.1 | 2744.1 | 436.4 | 442.6 | 501.6 | 463.9 | 513.6
3377.1 | 2745.1 | 436.8 | 442.6 | 500.6 | 462.5 | 512.5
3378.1 | 2746.1 | 437 | 442.7 | 499.3 | 461.2 | 511.6
3379.1 | 2747.1 | 436.7 | 442.6 | 498.5 | 459.9 | 510.7
3380.1 | 2748.1 | 436.3 | 442.4 | 497.1 | 458.6 | 509.9
3381.1 | 2749.1 | 436.1 | 442.3 | 496 | 458.2 | 509
3382.1 | 2750.1 | 436.6 | 442.3 | 495.3 | 459.3 | 508.2
3383.1 | 2751.1 | 436.5 | 442 | 495.6 | 459.9 | 507.3
3384.1 | 2752.1 | 436.8 | 441.9 | 496.2 | 459.9 | 506.4
3385.1 | 2753.1 | 436.7 | 441.9 | 495.6 | 458.5 | 505.5
3386.1 | 2754.1 | 436.9 | 441.8 | 494.4 | 457.1 | 504.8
3387.1 | 2755.1 | 437.7 | 441.7 | 493.4 | 456.8 | 503.9
3388.1 | 2756.1 | 437.4 | 441.8 | 492.4 | 456.8 | 503.1
3389.1 | 2757.1 | 437.4 | 441.8 | 491.8 | 456.4 | 502.3
3390.1 | 2758.1 | 437.8 | 441.8 | 490.7 | 456.3 | 501.6
3391.1 | 2759.1 | 438.1 | 441.6 | 490.1 | 455.3 | 500.8
3392.1 | 2760.1 | 438 | 441.5 | 489.5 | 454.6 | 500.1
3393.1 | 2761.1 | 437.7 | 441.4 | 489.2 | 454.1 | 499.7
3394.1 | 2762.1 | 437.5 | 441.4 | 488.5 | 453.2 | 499.1
3395.1 | 2763.1 | 437.7 | 441.4 | 488.1 | 453.5 | 498.5
3396.1 | 2764.1 | 437.6 | 441.4 | 487.2 | 452.9 | 497.9
3397.1 | 2765.1 | 437.6 | 441.5 | 486.7 | 451.6 | 497.2
3398.1 | 2766.1 | 437.9 | 441.6 | 486 | 450.3 | 496.4
3399.1 | 2767.1 | 438.1 | 441.5 | 485.3 | 448.9 | 495.8
3400.1 | 2768.1 | 438.2 | 441.4 | 485.6 | 447.6 | 495.1
3401.1 | 2769.1 | 437.7 | 441.3 | 485.1 | 448 | 494.3
3402.1 | 2770.1 | 437.7 | 441.3 | 485.3 | 448.4 | 493.5
3403.1 | 2771.1 | 437.9 | 441.4 | 485.1 | 448.1 | 492.8
3404.1 | 2772.1 | 438.2 | 441.4 | 484.3 | 446.9 | 492.1
3405.1 | 2773.1 | 437.8 | 441.4 | 483.5 | 446.5 | 491.5
3406.1 | 2774.1 | 438.1 | 441.6 | 482.8 | 446.7 | 490.8
3407.1 | 2775.1 | 438 | 441.5 | 482.3 | 445.9 | 490.1
3408.1 | 2776.1 | 437.6 | 441.5 | 481.4 | 445.3 | 489.4
3409.1 | 2777.1 | 437.4 | 441.3 | 480.5 | 444.6 | 488.8
3410.1 | 2778.1 | 437.5 | 441.2 | 480.2 | 444.9 | 488.1
3411.1 | 2779.1 | 437.5 | 441.1 | 480.4 | 445.6 | 487.5
3412.1 | 2780.1 | 437.6 | 441.3 | 479.7 | 444.7 | 486.9
3413.1 | 2781.1 | 437.8 | 441.5 | 479.4 | 443.8 | 486.2
3414.1 | 2782.1 | 438 | 441.6 | 478.9 | 443 | 485.6
3415.1 | 2783.1 | 438.4 | 441.8 | 478.4 | 442.1 | 485
3416.1 | 2784.1 | 438 | 441.9 | 477.8 | 441.5 | 484.3
3417.1 | 2785.1 | 438.1 | 441.8 | 477.2 | 442.4 | 483.8
3418.1 | 2786.1 | 438.5 | 441.9 | 477.2 | 443.3 | 483.2
3419.1 | 2787.1 | 438.2 | 441.9 | 477.7 | 443.4 | 482.6
3420.1 | 2788.1 | 437.9 | 441.7 | 477.4 | 443.3 | 482
3421.1 | 2789.1 | 437.9 | 441.6 | 477.1 | 443.5 | 481.5
3422.1 | 2790.1 | 438.1 | 441.6 | 476.8 | 443.3 | 480.9
3423.1 | 2791.1 | 438.1 | 441.8 | 476.3 | 442.6 | 480.2
3424.1 | 2792.1 | 438.6 | 442.1 | 476.2 | 442.1 | 479.6
3425.1 | 2793.1 | 438.7 | 442.2 | 475.9 | 441.7 | 479.1
3426.1 | 2794.1 | 438.4 | 442.2 | 476.1 | 441.1 | 478.5
3427.1 | 2795.1 | 438.3 | 442.3 | 475.9 | 440.6 | 477.9
3428.1 | 2796.1 | 438.2 | 442.4 | 475.5 | 440 | 477.3
3429.1 | 2797.1 | 438.5 | 442.7 | 475.2 | 439.9 | 476.8
3430.1 | 2798.1 | 438.6 | 442.9 | 475.2 | 440.5 | 476.2
3431.1 | 2799.1 | 438.7 | 443 | 474.7 | 439.8 | 475.7
3432.1 | 2800.1 | 438.9 | 443.2 | 474 | 438.9 | 475.2
3433.1 | 2801.1 | 438.7 | 443.3 | 473.3 | 438.1 | 474.6
3434.1 | 2802.1 | 438.7 | 443.5 | 473.2 | 437.6 | 474
3435.1 | 2803.1 | 438.7 | 443.6 | 473 | 436.9 | 473.3
3436.1 | 2804.1 | 438.8 | 443.7 | 473.5 | 436 | 472.7
3437.1 | 2805.1 | 438.9 | 443.8 | 473.6 | 435.3 | 472
3438.1 | 2806.1 | 439.3 | 444.1 | 473.7 | 434.4 | 471.4
3439.1 | 2807.1 | 439.2 | 444.3 | 474.3 | 433.3 | 470.8
3440.1 | 2808.1 | 439.1 | 444.4 | 474 | 433.1 | 470.2
3441.1 | 2809.1 | 439.1 | 444.5 | 473.5 | 432.7 | 469.5
3442.1 | 2810.1 | 439 | 444.6 | 473.3 | 431.4 | 468.9
3443.1 | 2811.1 | 438.9 | 444.8 | 473.1 | 429.9 | 468.4
3444.1 | 2812.1 | 438.8 | 445.1 | 472.9 | 428.4 | 467.7
3445.1 | 2813.1 | 439 | 445.3 | 472.3 | 427.4 | 467.2
3446.1 | 2814.1 | 439.1 | 445.5 | 471.3 | 426.4 | 466.7
3447.1 | 2815.1 | 438.9 | 445.6 | 470.5 | 425.8 | 466.1
3448.1 | 2816.1 | 438.6 | 445.5 | 470.1 | 425.9 | 465.6
3449.1 | 2817.1 | 438.7 | 445.5 | 469.5 | 426.3 | 465.2
3450.1 | 2818.1 | 438.8 | 445.7 | 468.7 | 426.3 | 464.7
3451.1 | 2819.1 | 439 | 446 | 468.1 | 426.2 | 464.2
3452.1 | 2820.1 | 438.8 | 446.1 | 467.6 | 425.7 | 463.7
3453.1 | 2821.1 | 438.9 | 446.2 | 467 | 425.3 | 463.3
3454.1 | 2822.1 | 439 | 446.2 | 466.4 | 424.8 | 462.7
3455.1 | 2823.1 | 439.1 | 446.4 | 466.1 | 424.4 | 462.2
3456.1 | 2824.1 | 439.3 | 446.6 | 466.3 | 424 | 461.7
3457.1 | 2825.1 | 439.6 | 446.8 | 465.9 | 423.2 | 461.2
3458.1 | 2826.1 | 439.8 | 447 | 465.3 | 422.5 | 460.6
3459.1 | 2827.1 | 439.8 | 447 | 464.9 | 421.7 | 460
3460.1 | 2828.1 | 439.8 | 447 | 464.7 | 421 | 459.5
3461.1 | 2829.1 | 439.9 | 447.1 | 464.4 | 419.9 | 458.9
3462.1 | 2830.1 | 439.9 | 447.2 | 464.2 | 418.8 | 458.4
3463.1 | 2831.1 | 439.7 | 447.2 | 464.2 | 418.1 | 457.9
3464.1 | 2832.1 | 439.7 | 447.2 | 464.1 | 417.6 | 457.5
3465.1 | 2833.1 | 439.5 | 447.2 | 463.8 | 417.9 | 457
3466.1 | 2834.1 | 439.7 | 447.3 | 463.3 | 418.5 | 456.5
3467.1 | 2835.1 | 439.9 | 447.4 | 462.9 | 418.5 | 456.1
3468.1 | 2836.1 | 440 | 447.4 | 462.7 | 418 | 455.6
3469.1 | 2837.1 | 439.8 | 447.4 | 462.2 | 417.4 | 455.1
3470.1 | 2838.1 | 439.9 | 447.5 | 461.7 | 417 | 454.7
3471.1 | 2839.1 | 440 | 447.6 | 461.3 | 416.7 | 454.2
3472.1 | 2840.1 | 440.1 | 447.7 | 461.2 | 416.2 | 453.8
3473.1 | 2841.1 | 440 | 447.7 | 461 | 415.5 | 453.3
3474.1 | 2842.1 | 439.9 | 447.7 | 461 | 415.3 | 452.9
3475.1 | 2843.1 | 440.1 | 447.8 | 460.6 | 415.3 | 452.5
3476.1 | 2844.1 | 440.3 | 447.9 | 460.3 | 415 | 452
3477.1 | 2845.1 | 440.4 | 447.9 | 459.9 | 414.9 | 451.6
3478.1 | 2846.1 | 440.6 | 447.9 | 459.5 | 414.5 | 451.2
3479.1 | 2847.1 | 440.7 | 448 | 459.1 | 413.7 | 450.7
3480.1 | 2848.1 | 440.8 | 448.1 | 459 | 412.8 | 450.3
3481.1 | 2849.1 | 440.9 | 448.1 | 459.2 | 412.5 | 449.9
3482.1 | 2850.1 | 441 | 448.2 | 459 | 412.4 | 449.5
3483.1 | 2851.1 | 440.9 | 448.2 | 458.9 | 412.2 | 449
3484.1 | 2852.1 | 440.9 | 448.3 | 458.6 | 411.7 | 448.6
3485.1 | 2853.1 | 441 | 448.3 | 458.3 | 410.8 | 448.2
3486.1 | 2854.1 | 440.8 | 448.2 | 458 | 410 | 447.7
3487.1 | 2855.1 | 440.7 | 448.2 | 457.7 | 409.2 | 447.3
3488.1 | 2856.1 | 440.9 | 448.2 | 457.5 | 408.6 | 446.9
3489.1 | 2857.1 | 441 | 448.3 | 457.4 | 408 | 446.5
3490.1 | 2858.1 | 441.1 | 448.4 | 457 | 407.4 | 446
3491.1 | 2859.1 | 441.2 | 448.4 | 456.7 | 406.9 | 445.6
3492.1 | 2860.1 | 441.3 | 448.5 | 456.5 | 406.3 | 445.3
3493.1 | 2861.1 | 441.3 | 448.6 | 456.3 | 405.8 | 444.8
3494.1 | 2862.1 | 441.3 | 448.7 | 456.1 | 405.5 | 444.4
3495.1 | 2863.1 | 441.4 | 448.7 | 455.7 | 405.1 | 444
3496.1 | 2864.1 | 441.4 | 448.7 | 455.6 | 405 | 443.6
3497.1 | 2865.1 | 441.3 | 448.7 | 455.5 | 404.3 | 443.2
3498.1 | 2866.1 | 441.2 | 448.7 | 455.2 | 403.8 | 442.8
3499.1 | 2867.1 | 441.3 | 448.7 | 454.9 | 403.1 | 442.4
3500.1 | 2868.1 | 441.1 | 448.8 | 454.6 | 402.4 | 441.9
3501.1 | 2869.1 | 440.9 | 448.7 | 454.5 | 401.8 | 441.5
3502.1 | 2870.1 | 441 | 448.8 | 454.3 | 401.6 | 441.2
3503.1 | 2871.1 | 441.1 | 448.8 | 454 | 401.3 | 440.8
3504.1 | 2872.1 | 441.1 | 448.8 | 453.5 | 401.2 | 440.4
3505.1 | 2873.1 | 440.8 | 448.8 | 453.3 | 401.2 | 440
3506.1 | 2874.1 | 440.9 | 448.8 | 452.8 | 401 | 439.6
3507.1 | 2875.1 | 440.8 | 448.9 | 452.5 | 400.5 | 439.1
3508.1 | 2876.1 | 440.8 | 449 | 451.9 | 400 | 438.8
3509.1 | 2877.1 | 441 | 449 | 451.4 | 400 | 438.4
3510.1 | 2878.1 | 441.2 | 449 | 450.9 | 399.9 | 438
3511.1 | 2879.1 | 441.4 | 449.1 | 450.4 | 399.5 | 437.6
3512.1 | 2880.1 | 441.5 | 449.2 | 449.9 | 399 | 437.3
3513.1 | 2881.1 | 441.5 | 449.2 | 449.7 | 399 | 436.9
3514.1 | 2882.1 | 441.6 | 449.3 | 449.6 | 399.1 | 436.5
3515.1 | 2883.1 | 441.5 | 449.3 | 449.3 | 399 | 436.1
3516.1 | 2884.1 | 441.6 | 449.3 | 448.9 | 398.5 | 435.7
3517.1 | 2885.1 | 441.6 | 449.3 | 448.6 | 397.8 | 435.3
3518.1 | 2886.1 | 441.6 | 449.3 | 448.3 | 397.2 | 434.9
3519.1 | 2887.1 | 441.4 | 449.3 | 448.1 | 396.9 | 434.5
3520.1 | 2888.1 | 441.3 | 449.3 | 447.8 | 396.5 | 434.2
3521.1 | 2889.1 | 441.3 | 449.3 | 447.8 | 396 | 433.8
3522.1 | 2890.1 | 441.4 | 449.3 | 447.9 | 396 | 433.4
3523.1 | 2891.1 | 441.5 | 449.3 | 447.7 | 395.3 | 433.1
3524.1 | 2892.1 | 441.6 | 449.4 | 447.5 | 394.6 | 432.7
3525.1 | 2893.1 | 441.6 | 449.4 | 447.2 | 394.1 | 432.3
3526.1 | 2894.1 | 441.7 | 449.4 | 447.1 | 393.5 | 431.9
3527.1 | 2895.1 | 441.7 | 449.4 | 447 | 393.3 | 431.6
3528.1 | 2896.1 | 441.7 | 449.4 | 446.5 | 393.1 | 431.1
3529.1 | 2897.1 | 441.8 | 449.5 | 446.1 | 392.6 | 430.8
3530.1 | 2898.1 | 441.5 | 449.5 | 446 | 392.5 | 430.4
3531.1 | 2899.1 | 441.4 | 449.4 | 445.7 | 392.5 | 430
3532.1 | 2900.1 | 441.6 | 449.4 | 445.2 | 392.4 | 429.7
3533.1 | 2901.1 | 441.5 | 449.4 | 444.8 | 391.8 | 429.3
3534.1 | 2902.1 | 441.5 | 449.4 | 444.3 | 391.1 | 429
3535.1 | 2903.1 | 441.6 | 449.4 | 444.1 | 390.4 | 428.7
3536.1 | 2904.1 | 441.7 | 449.4 | 443.8 | 389.7 | 428.3
3537.1 | 2905.1 | 441.9 | 449.4 | 443.3 | 389.1 | 427.9
3538.1 | 2906.1 | 441.8 | 449.5 | 442.9 | 389 | 427.5
3539.1 | 2907.1 | 441.9 | 449.5 | 442.6 | 388.4 | 427.1
3540.1 | 2908.1 | 441.9 | 449.4 | 442.4 | 388 | 426.8
3541.1 | 2909.1 | 441.8 | 449.3 | 442.1 | 387.6 | 426.4
3542.1 | 2910.1 | 441.7 | 449.3 | 442.2 | 387.4 | 426.1
3543.1 | 2911.1 | 441.8 | 449.3 | 441.9 | 387.1 | 425.8
3544.1 | 2912.1 | 441.9 | 449.3 | 441.5 | 387.1 | 425.4
3545.1 | 2913.1 | 441.9 | 449.3 | 441.5 | 386.9 | 425
3546.1 | 2914.1 | 441.8 | 449.2 | 441.4 | 386.5 | 424.6
3547.1 | 2915.1 | 441.9 | 449.2 | 441 | 386.2 | 424.3
3548.1 | 2916.1 | 441.9 | 449.2 | 440.6 | 386.5 | 424
3549.1 | 2917.1 | 442 | 449.2 | 440.4 | 386.7 | 423.6
3550.1 | 2918.1 | 441.9 | 449.3 | 440.1 | 386.8 | 423.2
3551.1 | 2919.1 | 441.9 | 449.2 | 439.6 | 386.2 | 422.9
3552.1 | 2920.1 | 441.9 | 449.3 | 439.3 | 385.8 | 422.6
3553.1 | 2921.1 | 441.8 | 449.2 | 438.8 | 385.8 | 422.2
3554.1 | 2922.1 | 441.7 | 449.2 | 438.4 | 386.3 | 421.9
3555.1 | 2923.1 | 441.6 | 449.1 | 438.1 | 386.1 | 421.5
3556.1 | 2924.1 | 441.7 | 449.1 | 437.7 | 385.6 | 421.2
3557.1 | 2925.1 | 441.8 | 449.1 | 437.5 | 385.3 | 420.9
3558.1 | 2926.1 | 441.9 | 449.1 | 437.3 | 384.7 | 420.6
3559.1 | 2927.1 | 441.9 | 449.1 | 437.1 | 384.1 | 420.2
3560.1 | 2928.1 | 441.9 | 449.1 | 437 | 383.6 | 419.8
3561.1 | 2929.1 | 441.9 | 449 | 436.8 | 382.9 | 419.5
3562.1 | 2930.1 | 442 | 449.1 | 436.4 | 383 | 419.2
3563.1 | 2931.1 | 441.9 | 449.1 | 436 | 383.1 | 418.8
3564.1 | 2932.1 | 442 | 449.1 | 435.8 | 383.8 | 418.5
3565.1 | 2933.1 | 441.8 | 449.1 | 435.5 | 383.3 | 418.2
3566.1 | 2934.1 | 441.9 | 449.1 | 435.2 | 382.7 | 417.8
3567.1 | 2935.1 | 441.7 | 449.1 | 435.1 | 382.7 | 417.4
3568.1 | 2936.1 | 441.6 | 449.1 | 434.8 | 383 | 417.1
3569.1 | 2937.1 | 441.7 | 449.1 | 434.5 | 383.2 | 416.8
3570.1 | 2938.1 | 441.8 | 449.1 | 434.1 | 382.8 | 416.5
3571.1 | 2939.1 | 441.8 | 449.1 | 433.7 | 382.5 | 416.2
3572.1 | 2940.1 | 441.8 | 449.1 | 433.6 | 382.6 | 415.8
3573.1 | 2941.1 | 441.8 | 449.1 | 433.4 | 382.1 | 415.5
3574.1 | 2942.1 | 441.6 | 449.1 | 433.1 | 382.5 | 415.2
3575.1 | 2943.1 | 441.3 | 449 | 432.8 | 382 | 414.9
3576.1 | 2944.1 | 441.5 | 449 | 432.3 | 382.4 | 414.6
3577.1 | 2945.1 | 441.7 | 449 | 432 | 382.4 | 414.2
3578.1 | 2946.1 | 441.7 | 449 | 431.7 | 382.4 | 413.9
3579.1 | 2947.1 | 441.8 | 449 | 431.2 | 383.2 | 413.6
3580.1 | 2948.1 | 441.9 | 449 | 430.8 | 383.7 | 413.2
3581.1 | 2949.1 | 441.8 | 449 | 430.2 | 383.7 | 412.9
3582.1 | 2950.1 | 441.8 | 449 | 429.6 | 384.2 | 412.6
3583.1 | 2951.1 | 441.9 | 448.9 | 429 | 384.3 | 412.3
3584.1 | 2952.1 | 441.9 | 448.9 | 428.8 | 384.4 | 412
3585.1 | 2953.1 | 441.8 | 448.8 | 428.6 | 384.8 | 411.7
3586.1 | 2954.1 | 441.9 | 448.9 | 428.4 | 385.3 | 411.4
3587.1 | 2955.1 | 442 | 448.9 | 428.2 | 385.6 | 411.1
3588.1 | 2956.1 | 441.6 | 448.9 | 427.8 | 385.5 | 410.8
3589.1 | 2957.1 | 441.7 | 448.9 | 427.5 | 385.3 | 410.5
3590.1 | 2958.1 | 441.7 | 448.9 | 427 | 385.1 | 410.2
3591.1 | 2959.1 | 441.4 | 449 | 426.8 | 384.6 | 409.8
3592.1 | 2960.1 | 441.3 | 449 | 426.5 | 384.8 | 409.5
3593.1 | 2961.1 | 441.6 | 448.9 | 426.1 | 385 | 409.3
3594.1 | 2962.1 | 441.7 | 448.9 | 425.7 | 383.7 | 408.9
3595.1 | 2963.1 | 441.8 | 448.9 | 425.5 | 382.3 | 408.6
3596.1 | 2964.1 | 441.9 | 448.8 | 425.3 | 382.3 | 408.2
3597.1 | 2965.1 | 441.9 | 448.8 | 425 | 382.1 | 408
3598.1 | 2966.1 | 441.9 | 448.8 | 424.6 | 381.1 | 407.7
3599.1 | 2967.1 | 441.7 | 448.7 | 424.3 | 380.8 | 407.3
3600.1 | 2968.1 | 441.5 | 448.7 | 423.9 | 381 | 407
3601.1 | 2969.1 | 441.5 | 448.7 | 423.6 | 381.3 | 406.7
3602.1 | 2970.1 | 441.5 | 448.6 | 423.1 | 380.3 | 406.4
3603.1 | 2971.1 | 441.5 | 448.6 | 422.9 | 380.1 | 406.1
3604.1 | 2972.1 | 441.6 | 448.5 | 422.5 | 380.4 | 405.8
3605.1 | 2973.1 | 441.8 | 448.5 | 422.2 | 380.1 | 405.5
3606.1 | 2974.1 | 441.7 | 448.5 | 421.9 | 379.7 | 405.2
3607.1 | 2975.1 | 441.7 | 448.4 | 421.3 | 380.3 | 404.9
3608.1 | 2976.1 | 441.7 | 448.4 | 421.2 | 380.5 | 404.5
3609.1 | 2977.1 | 441.6 | 448.4 | 420.8 | 380.7 | 404.2
3610.1 | 2978.1 | 441.6 | 448.3 | 420.6 | 379.6 | 403.9
3611.1 | 2979.1 | 441.5 | 448.3 | 420.4 | 379.2 | 403.7
3612.1 | 2980.1 | 441.4 | 448.3 | 420.3 | 378.6 | 403.3
3613.1 | 2981.1 | 441.5 | 448.2 | 420.1 | 379.2 | 403
3614.1 | 2982.1 | 441.5 | 448.2 | 419.8 | 379.3 | 402.7
3615.1 | 2983.1 | 441.4 | 448.2 | 419.5 | 378.7 | 402.5
3616.1 | 2984.1 | 441.3 | 448.2 | 419.5 | 378.7 | 402.1
3617.1 | 2985.1 | 441.2 | 448.1 | 419.3 | 378.2 | 401.8
3618.1 | 2986.1 | 441.3 | 448.1 | 419 | 377.9 | 401.5
3619.1 | 2987.1 | 441.3 | 448.1 | 418.6 | 377.6 | 401.2
3620.1 | 2988.1 | 441.3 | 448.1 | 418.2 | 377.1 | 400.9
3621.1 | 2989.1 | 441.2 | 448 | 417.9 | 376.8 | 400.6
3622.1 | 2990.1 | 441.2 | 448 | 417.8 | 377.1 | 400.3
3623.1 | 2991.1 | 441.3 | 448 | 417.7 | 377.8 | 400
3624.1 | 2992.1 | 441.3 | 448 | 417.2 | 378.5 | 399.6
3625.1 | 2993.1 | 441.3 | 447.9 | 416.9 | 378.2 | 399.4
3626.1 | 2994.1 | 441.2 | 447.9 | 416.4 | 378.1 | 399.1
3627.1 | 2995.1 | 441.1 | 447.9 | 416.2 | 378.5 | 398.8
3628.1 | 2996.1 | 441.1 | 447.8 | 416.2 | 377.6 | 398.6
3629.1 | 2997.1 | 441 | 447.8 | 416 | 376.7 | 398.3
3630.1 | 2998.1 | 440.8 | 447.9 | 415.9 | 375.6 | 397.9
3631.1 | 2999.1 | 440.7 | 447.8 | 415.6 | 375 | 397.6
3632.1 | 3000.1 | 440.8 | 447.8 | 415.2 | 374.4 | 397.4
3633.1 | 3001.1 | 440.7 | 447.8 | 414.9 | 373.3 | 397.1
3634.1 | 3002.1 | 440.7 | 447.8 | 414.6 | 372.9 | 396.8
3635.1 | 3003.1 | 440.9 | 447.7 | 414.1 | 372.6 | 396.5
3636.1 | 3004.1 | 441 | 447.7 | 414 | 372.7 | 396.3
3637.1 | 3005.1 | 440.8 | 447.7 | 413.9 | 372.3 | 396
3638.1 | 3006.1 | 440.6 | 447.7 | 413.8 | 372.9 | 395.7
3639.1 | 3007.1 | 440.7 | 447.7 | 413.3 | 371.7 | 395.5
3640.1 | 3008.1 | 440.7 | 447.7 | 413.2 | 371.9 | 395.2
3641.1 | 3009.1 | 440.6 | 447.7 | 412.9 | 372.6 | 394.9
3642.1 | 3010.1 | 440.6 | 447.6 | 412.7 | 372.4 | 394.7
3643.1 | 3011.1 | 440.4 | 447.6 | 412.5 | 372.2 | 394.4
3644.1 | 3012.1 | 440.5 | 447.6 | 412.1 | 373 | 394.1
3645.1 | 3013.1 | 440.6 | 447.5 | 411.5 | 372.7 | 393.8
3646.1 | 3014.1 | 440.7 | 447.5 | 411.1 | 372.2 | 393.6
3647.1 | 3015.1 | 440.4 | 447.5 | 410.8 | 370.9 | 393.2
3648.1 | 3016.1 | 440.2 | 447.5 | 410.3 | 370 | 393
3649.1 | 3017.1 | 440.4 | 447.5 | 410 | 369 | 392.8
3650.1 | 3018.1 | 440.3 | 447.5 | 409.6 | 368.1 | 392.5
3651.1 | 3019.1 | 440.3 | 447.5 | 409.1 | 368.2 | 392.2
3652.1 | 3020.1 | 440.3 | 447.5 | 408.8 | 368.6 | 392
3653.1 | 3021.1 | 440.1 | 447.4 | 408.7 | 369.2 | 391.7
3654.1 | 3022.1 | 440.1 | 447.4 | 408.7 | 369.7 | 391.4
3655.1 | 3023.1 | 440.2 | 447.4 | 408.6 | 369.8 | 391.1
3656.1 | 3024.1 | 440.2 | 447.3 | 408.7 | 371.2 | 390.9
3657.1 | 3025.1 | 440.3 | 447.3 | 408.3 | 372.2 | 390.6
3658.1 | 3026.1 | 440.2 | 447.3 | 407.9 | 372.9 | 390.3
3659.1 | 3027.1 | 439.9 | 447.3 | 407.5 | 373.4 | 390.1
3660.1 | 3028.1 | 439.9 | 447.3 | 407.4 | 372.8 | 389.8
3661.1 | 3029.1 | 440 | 447.3 | 407.2 | 373 | 389.5
3662.1 | 3030.1 | 439.6 | 447.2 | 406.7 | 372 | 389.3
3663.1 | 3031.1 | 439.6 | 447.2 | 406.1 | 371.3 | 389.1
3664.1 | 3032.1 | 439.7 | 447.1 | 405.6 | 370.7 | 388.8
3665.1 | 3033.1 | 439.7 | 447.1 | 405.1 | 370 | 388.6
3666.1 | 3034.1 | 439.7 | 447.1 | 404.8 | 369.7 | 388.3
3667.1 | 3035.1 | 439.8 | 447 | 404.6 | 370.1 | 388
3668.1 | 3036.1 | 439.7 | 446.9 | 404.5 | 369.7 | 387.8
3669.1 | 3037.1 | 439.7 | 446.9 | 404.2 | 370.1 | 387.5
3670.1 | 3038.1 | 439.7 | 446.8 | 403.9 | 369.7 | 387.3
3671.1 | 3039.1 | 439.3 | 446.8 | 403.7 | 369.6 | 387
3672.1 | 3040.1 | 439.1 | 446.8 | 403.5 | 369.1 | 386.8
3673.1 | 3041.1 | 438.8 | 446.8 | 403.4 | 368.8 | 386.5
3674.1 | 3042.1 | 439.1 | 446.9 | 402.9 | 368.9 | 386.3
3675.1 | 3043.1 | 439.1 | 446.9 | 402.6 | 369.4 | 385.9
3676.1 | 3044.1 | 439.2 | 446.9 | 402.5 | 370.2 | 385.7
3677.1 | 3045.1 | 439.3 | 446.9 | 402.3 | 370.2 | 385.5
3678.1 | 3046.1 | 439.4 | 446.8 | 401.9 | 368.6 | 385.2
3679.1 | 3047.1 | 439.3 | 446.7 | 401.8 | 367.4 | 385
3680.1 | 3048.1 | 439.2 | 446.6 | 401.7 | 367.1 | 384.8
3681.1 | 3049.1 | 439.1 | 446.5 | 401.4 | 365.4 | 384.5
3682.1 | 3050.1 | 439.1 | 446.5 | 401.4 | 365.5 | 384.2
3683.1 | 3051.1 | 439.1 | 446.5 | 401.3 | 367.1 | 384
3684.1 | 3052.1 | 439 | 446.5 | 400.6 | 366.9 | 383.8
3685.1 | 3053.1 | 438.7 | 446.4 | 400 | 366.5 | 383.5
3686.1 | 3054.1 | 438.7 | 446.4 | 399.7 | 365.5 | 383.3
3687.1 | 3055.1 | 438.6 | 446.4 | 399.6 | 365.7 | 383
3688.1 | 3056.1 | 438.7 | 446.4 | 399.3 | 365.1 | 382.8
3689.1 | 3057.1 | 438.7 | 446.5 | 399.1 | 363.5 | 382.6
3690.1 | 3058.1 | 438.6 | 446.5 | 398.8 | 362.2 | 382.4
3691.1 | 3059.1 | 438.5 | 446.4 | 398.5 | 361.9 | 382.2
3692.1 | 3060.1 | 438.2 | 446.5 | 398.2 | 362.1 | 381.9
3693.1 | 3061.1 | 438 | 446.5 | 397.9 | 360.7 | 381.7
3694.1 | 3062.1 | 438.1 | 446.5 | 397.9 | 359.6 | 381.4
3695.1 | 3063.1 | 438.1 | 446.4 | 397.7 | 359.7 | 381.1
3696.1 | 3064.1 | 438.3 | 446.4 | 397.4 | 359.1 | 380.8
3697.1 | 3065.1 | 438.5 | 446.3 | 396.9 | 357.7 | 380.6
3698.1 | 3066.1 | 438.4 | 446.2 | 396.4 | 356.5 | 380.4
3699.1 | 3067.1 | 438.3 | 446.2 | 396.1 | 355 | 380.2
3700.1 | 3068.1 | 438.2 | 446.1 | 396 | 354.4 | 380
3701.1 | 3069.1 | 438.2 | 446.1 | 395.8 | 354.8 | 379.7
3702.1 | 3070.1 | 438.3 | 446 | 395.6 | 355.7 | 379.6
3703.1 | 3071.1 | 438.2 | 446 | 395.2 | 355.7 | 379.3
3704.1 | 3072.1 | 438.2 | 445.9 | 394.8 | 355.3 | 379.1
3705.1 | 3073.1 | 438.1 | 445.9 | 394.6 | 354.2 | 378.9
3706.1 | 3074.1 | 438.1 | 445.8 | 394.7 | 354.1 | 378.6
3707.1 | 3075.1 | 437.8 | 445.8 | 394.4 | 354.6 | 378.3
3708.1 | 3076.1 | 437.8 | 445.8 | 394.2 | 354 | 378.1
3709.1 | 3077.1 | 437.7 | 445.7 | 394 | 352.9 | 378
3710.1 | 3078.1 | 437.6 | 445.8 | 393.6 | 353.6 | 377.6
3711.1 | 3079.1 | 437.8 | 445.7 | 393.2 | 352.8 | 377.4
3712.1 | 3080.1 | 437.6 | 445.7 | 392.9 | 352.8 | 377.2
3713.1 | 3081.1 | 437.4 | 445.7 | 392.8 | 353.1 | 376.9
3714.1 | 3082.1 | 437.4 | 445.7 | 392.9 | 354 | 376.7
3715.1 | 3083.1 | 437.5 | 445.6 | 393 | 353.8 | 376.5
3716.1 | 3084.1 | 437.4 | 445.5 | 393.1 | 353.7 | 376.3
3717.1 | 3085.1 | 437.3 | 445.5 | 393.1 | 353.4 | 376
3718.1 | 3086.1 | 437.3 | 445.4 | 393.1 | 352.7 | 375.8
3719.1 | 3087.1 | 437.3 | 445.4 | 393 | 352.2 | 375.6
3720.1 | 3088.1 | 437.2 | 445.3 | 392.8 | 352 | 375.4
3721.1 | 3089.1 | 437.1 | 445.3 | 392.7 | 353.1 | 375.1
3722.1 | 3090.1 | 436.9 | 445.2 | 392.5 | 352.1 | 374.9
3723.1 | 3091.1 | 436.9 | 445.2 | 391.9 | 353.8 | 374.8
3724.1 | 3092.1 | 436.8 | 445.2 | 391.5 | 354.6 | 374.5
3725.1 | 3093.1 | 436.9 | 445.1 | 390.8 | 353.1 | 374.2
3726.1 | 3094.1 | 436.8 | 445 | 390.5 | 352.4 | 374
3727.1 | 3095.1 | 436.7 | 445 | 390.5 | 351.8 | 373.8
3728.1 | 3096.1 | 436.5 | 445 | 390.8 | 352.3 | 373.5
3729.1 | 3097.1 | 436.4 | 445 | 391 | 352.7 | 373.3
3730.1 | 3098.1 | 436.5 | 444.9 | 390.7 | 353 | 373.2
3731.1 | 3099.1 | 436.4 | 444.9 | 390.4 | 353.9 | 372.9
3732.1 | 3100.1 | 436.4 | 444.9 | 390.2 | 354.7 | 372.7
3733.1 | 3101.1 | 436.4 | 444.8 | 390.1 | 354.2 | 372.4
3734.1 | 3102.1 | 436.3 | 444.8 | 389.7 | 357.2 | 372.2
3735.1 | 3103.1 | 436.2 | 444.7 | 389.4 | 357.2 | 371.9
3736.1 | 3104.1 | 436.2 | 444.7 | 389.2 | 357 | 371.7
3737.1 | 3105.1 | 435.9 | 444.8 | 388.9 | 355.9 | 371.5
3738.1 | 3106.1 | 435.9 | 444.8 | 388.4 | 354.5 | 371.3
3739.1 | 3107.1 | 435.9 | 444.7 | 388 | 353.7 | 371.1
3740.1 | 3108.1 | 435.8 | 444.7 | 387.6 | 352.9 | 370.9
3741.1 | 3109.1 | 435.6 | 444.8 | 387.4 | 352.4 | 370.7
3742.1 | 3110.1 | 435.6 | 444.8 | 387.5 | 352.5 | 370.5
3743.1 | 3111.1 | 435.7 | 444.8 | 387.2 | 352.2 | 370.3
3744.1 | 3112.1 | 435.9 | 444.7 | 386.8 | 352 | 370.1
3745.1 | 3113.1 | 435.9 | 444.6 | 386.6 | 351.2 | 369.9
3746.1 | 3114.1 | 435.8 | 444.5 | 386.5 | 351.2 | 369.6
3747.1 | 3115.1 | 435.7 | 444.5 | 386.2 | 350.3 | 369.4
3748.1 | 3116.1 | 435.7 | 444.4 | 386.1 | 350.5 | 369.2
3749.1 | 3117.1 | 435.6 | 444.4 | 386.1 | 349.5 | 369
3750.1 | 3118.1 | 435.5 | 444.3 | 386.1 | 349.8 | 368.8
3751.1 | 3119.1 | 435.4 | 444.3 | 385.9 | 348.8 | 368.6
3752.1 | 3120.1 | 435.2 | 444.2 | 385.8 | 348 | 368.4
3753.1 | 3121.1 | 435.1 | 444.2 | 385.7 | 347.4 | 368.1
3754.1 | 3122.1 | 435.1 | 444.1 | 385.4 | 346.5 | 367.9
3755.1 | 3123.1 | 435 | 444.1 | 385 | 345.6 | 367.7
3756.1 | 3124.1 | 435 | 444.1 | 384.5 | 345.7 | 367.5
3757.1 | 3125.1 | 434.9 | 444 | 384.2 | 345.9 | 367.3
3758.1 | 3126.1 | 434.9 | 443.9 | 383.9 | 346.7 | 367.1
3759.1 | 3127.1 | 434.9 | 443.9 | 383.6 | 347 | 366.9
3760.1 | 3128.1 | 434.9 | 443.8 | 383.3 | 347.7 | 366.7
3761.1 | 3129.1 | 434.8 | 443.8 | 383.3 | 347.4 | 366.4
3762.1 | 3130.1 | 434.7 | 443.8 | 383 | 347.3 | 366.2
3763.1 | 3131.1 | 434.6 | 443.9 | 382.6 | 347.6 | 366
3764.1 | 3132.1 | 434.6 | 443.8 | 382.1 | 346.9 | 365.8
3765.1 | 3133.1 | 434.6 | 443.7 | 381.5 | 346.3 | 365.6
3766.1 | 3134.1 | 434.4 | 443.7 | 381 | 345.2 | 365.4
3767.1 | 3135.1 | 434.3 | 443.7 | 380.4 | 344.9 | 365.2
3768.1 | 3136.1 | 434.4 | 443.7 | 379.9 | 344.8 | 365
3769.1 | 3137.1 | 434.4 | 443.6 | 379.5 | 344.2 | 364.8
3770.1 | 3138.1 | 434.4 | 443.6 | 379.1 | 343.3 | 364.6
3771.1 | 3139.1 | 434.4 | 443.5 | 378.8 | 342.6 | 364.4
3772.1 | 3140.1 | 434.3 | 443.4 | 378.4 | 342.1 | 364.2
3773.1 | 3141.1 | 434.1 | 443.4 | 378 | 341.5 | 364.1
3774.1 | 3142.1 | 434.1 | 443.3 | 377.7 | 340.5 | 363.9
3775.1 | 3143.1 | 434 | 443.3 | 377.3 | 339.5 | 363.7
3776.1 | 3144.1 | 434 | 443.3 | 376.9 | 339.2 | 363.5
3777.1 | 3145.1 | 434 | 443.2 | 376.8 | 338.5 | 363.3
3778.1 | 3146.1 | 434 | 443.1 | 376.7 | 337.7 | 363.1
3779.1 | 3147.1 | 434.1 | 442.9 | 376.5 | 337.6 | 362.9
3780.1 | 3148.1 | 433.9 | 442.9 | 376.4 | 337 | 362.7
3781.1 | 3149.1 | 433.9 | 442.9 | 376.1 | 336.5 | 362.5
3782.1 | 3150.1 | 433.7 | 442.9 | 375.8 | 337.8 | 362.3
3783.1 | 3151.1 | 433.7 | 442.9 | 375.5 | 337.5 | 362.1
3784.1 | 3152.1 | 433.6 | 442.9 | 375.2 | 337.3 | 361.9
3785.1 | 3153.1 | 433.6 | 442.8 | 375 | 336.7 | 361.7
3786.1 | 3154.1 | 433.5 | 442.7 | 374.6 | 336.4 | 361.5
3787.1 | 3155.1 | 433.5 | 442.6 | 374.3 | 335.5 | 361.4
3788.1 | 3156.1 | 433.3 | 442.5 | 374 | 334.7 | 361.2
3789.1 | 3157.1 | 433.4 | 442.5 | 373.6 | 334.3 | 361
3790.1 | 3158.1 | 433.4 | 442.4 | 373.4 | 333.9 | 360.8
3791.1 | 3159.1 | 433.4 | 442.4 | 373.1 | 334 | 360.6
3792.1 | 3160.1 | 433.1 | 442.4 | 372.8 | 334.3 | 360.4
3793.1 | 3161.1 | 433.1 | 442.4 | 372.4 | 333.5 | 360.3
3794.1 | 3162.1 | 433 | 442.4 | 372.1 | 332.6 | 360.1
3795.1 | 3163.1 | 433 | 442.3 | 371.8 | 331.8 | 359.9
3796.1 | 3164.1 | 433 | 442.2 | 371.5 | 331.3 | 359.7
3797.1 | 3165.1 | 433.1 | 442.1 | 371.2 | 330.5 | 359.6
3798.1 | 3166.1 | 432.9 | 442 | 371 | 329.7 | 359.4
3799.1 | 3167.1 | 432.8 | 441.9 | 370.7 | 329.1 | 359.3
3800.1 | 3168.1 | 432.9 | 441.8 | 370.5 | 328.5 | 359.1
3801.1 | 3169.1 | 432.8 | 441.7 | 370.1 | 327.9 | 359
3802.1 | 3170.1 | 432.6 | 441.7 | 369.8 | 327.4 | 358.9
3803.1 | 3171.1 | 432.6 | 441.6 | 369.7 | 327 | 358.8
3804.1 | 3172.1 | 432.5 | 441.5 | 369.4 | 326.4 | 358.6
3805.1 | 3173.1 | 432.3 | 441.6 | 369.1 | 326.1 | 358.4
3806.1 | 3174.1 | 432.4 | 441.5 | 368.7 | 326.1 | 358.2
3807.1 | 3175.1 | 432.4 | 441.5 | 368.3 | 325.7 | 358
3808.1 | 3176.1 | 432.3 | 441.5 | 368.1 | 325.4 | 357.8
3809.1 | 3177.1 | 432.2 | 441.4 | 368 | 325.1 | 357.6
3810.1 | 3178.1 | 432.2 | 441.5 | 367.7 | 324.6 | 357.4
3811.1 | 3179.1 | 432.2 | 441.4 | 367.3 | 324.3 | 357.3
3812.1 | 3180.1 | 432.1 | 441.3 | 367.1 | 324 | 357.1
3813.1 | 3181.1 | 432.1 | 441.2 | 366.8 | 323.7 | 356.9
3814.1 | 3182.1 | 432 | 441.1 | 366.4 | 323.6 | 356.7
3815.1 | 3183.1 | 432 | 441 | 366.1 | 323.3 | 356.5
3816.1 | 3184.1 | 432 | 440.9 | 365.9 | 323.1 | 356.3
3817.1 | 3185.1 | 431.9 | 440.8 | 365.7 | 322.6 | 356.1
3818.1 | 3186.1 | 431.8 | 440.7 | 365.4 | 322.4 | 356
3819.1 | 3187.1 | 431.7 | 440.8 | 365.3 | 322.4 | 355.8
3820.1 | 3188.1 | 431.7 | 440.6 | 365.1 | 321.9 | 355.6
3821.1 | 3189.1 | 431.6 | 440.6 | 364.9 | 321.9 | 355.4
3822.1 | 3190.1 | 431.6 | 440.5 | 364.7 | 321.9 | 355.2
3823.1 | 3191.1 | 431.4 | 440.6 | 364.6 | 322.4 | 355
3824.1 | 3192.1 | 431.4 | 440.6 | 364.8 | 321.9 | 354.8
3825.1 | 3193.1 | 431.4 | 440.4 | 364.5 | 321.3 | 354.6
3826.1 | 3194.1 | 431.3 | 440.5 | 364.2 | 321 | 354.4
3827.1 | 3195.1 | 431.2 | 440.5 | 363.9 | 320.5 | 354.3
3828.1 | 3196.1 | 431.2 | 440.5 | 363.6 | 320 | 354.1
3829.1 | 3197.1 | 431.2 | 440.3 | 363.5 | 319.6 | 353.9
3830.1 | 3198.1 | 431.2 | 440.2 | 363.7 | 320.1 | 353.7
3831.1 | 3199.1 | 431.1 | 440.1 | 363.6 | 320.2 | 353.5
3832.1 | 3200.1 | 431.1 | 440 | 363.3 | 319.8 | 353.3
3833.1 | 3201.1 | 431 | 439.9 | 363 | 319.3 | 353.1
3834.1 | 3202.1 | 430.9 | 439.8 | 362.7 | 319 | 352.9
3835.1 | 3203.1 | 430.9 | 439.7 | 362.5 | 318.5 | 352.8
3836.1 | 3204.1 | 430.8 | 439.6 | 362.2 | 318 | 352.6
3837.1 | 3205.1 | 430.8 | 439.4 | 362.1 | 318 | 352.4
3838.1 | 3206.1 | 430.7 | 439.4 | 361.9 | 317.7 | 352.2
3839.1 | 3207.1 | 430.5 | 439.4 | 361.6 | 317.7 | 352
3840.1 | 3208.1 | 430.4 | 439.4 | 361.3 | 317.2 | 351.9
3841.1 | 3209.1 | 430.5 | 439.3 | 361.3 | 316.9 | 351.7
3842.1 | 3210.1 | 430.4 | 439.3 | 361.2 | 316.7 | 351.5
3843.1 | 3211.1 | 430.4 | 439.1 | 360.9 | 316.3 | 351.4
3844.1 | 3212.1 | 430.4 | 439 | 360.7 | 315.9 | 351.2
3845.1 | 3213.1 | 430.3 | 439 | 360.8 | 315.6 | 351.1
3846.1 | 3214.1 | 430.2 | 439 | 360.8 | 315.3 | 350.9
3847.1 | 3215.1 | 430 | 439.1 | 360.9 | 315.1 | 350.8
3848.1 | 3216.1 | 430 | 439 | 360.5 | 314.7 | 350.7
3849.1 | 3217.1 | 430 | 438.8 | 360.2 | 314.5 | 350.5
3850.1 | 3218.1 | 430 | 438.8 | 360.2 | 314.2 | 350.3
3851.1 | 3219.1 | 430 | 438.7 | 360.3 | 313.8 | 350.2
3852.1 | 3220.1 | 429.9 | 438.6 | 359.9 | 313.4 | 350
3853.1 | 3221.1 | 429.8 | 438.5 | 359.4 | 313 | 349.9
3854.1 | 3222.1 | 429.6 | 438.5 | 358.8 | 312.8 | 349.7
3855.1 | 3223.1 | 429.6 | 438.4 | 358.3 | 312.5 | 349.5
3856.1 | 3224.1 | 429.5 | 438.5 | 357.8 | 312.3 | 349.3
3857.1 | 3225.1 | 429.5 | 438.5 | 357.4 | 312 | 349.2
3858.1 | 3226.1 | 429.5 | 438.3 | 357 | 311.6 | 349
3859.1 | 3227.1 | 429.4 | 438.2 | 356.7 | 311.1 | 348.8
3860.1 | 3228.1 | 429.5 | 438.1 | 356.4 | 310.7 | 348.6
3861.1 | 3229.1 | 429.4 | 438 | 356.1 | 310.3 | 348.4
3862.1 | 3230.1 | 429.2 | 437.9 | 355.8 | 310.1 | 348.3
3863.1 | 3231.1 | 429.1 | 437.9 | 355.5 | 309.8 | 348.1
3864.1 | 3232.1 | 429.1 | 437.9 | 355.1 | 309.5 | 348
3865.1 | 3233.1 | 429 | 437.9 | 354.7 | 309.1 | 347.9
3866.1 | 3234.1 | 429 | 437.8 | 354.4 | 308.7 | 347.7
3867.1 | 3235.1 | 428.9 | 437.9 | 354 | 308.5 | 347.5
3868.1 | 3236.1 | 428.9 | 437.8 | 353.6 | 308.2 | 347.3
3869.1 | 3237.1 | 428.9 | 437.7 | 353.4 | 307.9 | 347.1
3870.1 | 3238.1 | 428.9 | 437.6 | 353.1 | 307.6 | 347
3871.1 | 3239.1 | 428.9 | 437.5 | 352.8 | 307.4 | 346.8
3872.1 | 3240.1 | 428.8 | 437.4 | 352.6 | 307.2 | 346.6
3873.1 | 3241.1 | 428.7 | 437.5 | 352.3 | 307 | 346.5
3874.1 | 3242.1 | 428.6 | 437.4 | 352 | 306.9 | 346.3
3875.1 | 3243.1 | 428.6 | 437.3 | 351.8 | 306.7 | 346.2
3876.1 | 3244.1 | 428.6 | 437.1 | 351.5 | 306.4 | 346
3877.1 | 3245.1 | 428.6 | 437 | 351.3 | 306.3 | 345.7
3878.1 | 3246.1 | 428.5 | 436.9 | 351.1 | 306.1 | 345.6
3879.1 | 3247.1 | 428.4 | 436.9 | 351 | 306.1 | 345.4
3880.1 | 3248.1 | 428.3 | 436.9 | 351.2 | 305.8 | 345.3
3881.1 | 3249.1 | 428.3 | 437 | 350.9 | 305.6 | 345.1
3882.1 | 3250.1 | 428.3 | 436.8 | 350.6 | 305.5 | 345
3883.1 | 3251.1 | 428.2 | 436.7 | 350.4 | 305.3 | 344.8
3884.1 | 3252.1 | 428 | 436.8 | 350.1 | 305 | 344.6
3885.1 | 3253.1 | 428.1 | 436.7 | 350 | 304.7 | 344.4
3886.1 | 3254.1 | 428.1 | 436.5 | 350 | 304.4 | 344.3
3887.1 | 3255.1 | 428 | 436.4 | 349.8 | 304.2 | 344.1
3888.1 | 3256.1 | 427.9 | 436.2 | 349.5 | 304 | 343.9
3889.1 | 3257.1 | 427.8 | 436.2 | 349.1 | 303.8 | 343.7
3890.1 | 3258.1 | 427.8 | 436.2 | 348.7 | 303.9 | 343.5
3891.1 | 3259.1 | 427.8 | 436.1 | 348.3 | 303.8 | 343.4
3892.1 | 3260.1 | 427.7 | 436.1 | 348.1 | 303.5 | 343.3
3893.1 | 3261.1 | 427.6 | 436.1 | 347.8 | 303.2 | 343.1
3894.1 | 3262.1 | 427.6 | 436 | 347.4 | 303.1 | 342.9
3895.1 | 3263.1 | 427.6 | 435.8 | 347.1 | 302.8 | 342.7
3896.1 | 3264.1 | 427.4 | 435.8 | 346.9 | 302.6 | 342.5
3897.1 | 3265.1 | 427.3 | 436 | 346.8 | 302.3 | 342.3
3898.1 | 3266.1 | 427.3 | 435.9 | 346.7 | 302.1 | 342.2
3899.1 | 3267.1 | 427.3 | 435.9 | 346.6 | 301.9 | 342
3900.1 | 3268.1 | 427.2 | 435.8 | 346.6 | 301.8 | 341.8
3901.1 | 3269.1 | 427.1 | 435.7 | 346.4 | 301.5 | 341.6
3902.1 | 3270.1 | 427.1 | 435.7 | 346.2 | 301.2 | 341.4
3903.1 | 3271.1 | 427.1 | 435.6 | 346.3 | 300.9 | 341.3
3904.1 | 3272.1 | 427.1 | 435.5 | 346.4 | 300.6 | 341.1
3905.1 | 3273.1 | 427 | 435.4 | 346.1 | 300.3 | 340.9
3906.1 | 3274.1 | 426.9 | 435.3 | 345.9 | 300.1 | 340.8
3907.1 | 3275.1 | 426.8 | 435.2 | 345.5 | 299.9 | 340.7
3908.1 | 3276.1 | 426.7 | 435.2 | 345.1 | 299.6 | 340.5
3909.1 | 3277.1 | 426.8 | 435.1 | 344.8 | 299.4 | 340.4
3910.1 | 3278.1 | 426.7 | 434.9 | 344.5 | 299.3 | 340.2
3911.1 | 3279.1 | 426.6 | 434.9 | 344.6 | 299.1 | 340.1
3912.1 | 3280.1 | 426.5 | 434.9 | 345 | 298.9 | 339.9
3913.1 | 3281.1 | 426.4 | 434.7 | 345.1 | 298.8 | 339.7
3914.1 | 3282.1 | 426.4 | 434.6 | 344.9 | 298.6 | 339.5
3915.1 | 3283.1 | 426.4 | 434.6 | 344.5 | 298.3 | 339.3
3916.1 | 3284.1 | 426.2 | 434.7 | 344.2 | 298.1 | 339.2
3917.1 | 3285.1 | 426.2 | 434.7 | 343.8 | 298 | 339
3918.1 | 3286.1 | 426.1 | 434.6 | 343.5 | 297.8 | 338.8
3919.1 | 3287.1 | 426.2 | 434.4 | 343.3 | 297.7 | 338.7
3920.1 | 3288.1 | 426.2 | 434.2 | 343.2 | 297.4 | 338.5
3921.1 | 3289.1 | 426.1 | 434.1 | 343 | 297.3 | 338.3
3922.1 | 3290.1 | 426 | 433.9 | 342.7 | 297 | 338.2
3923.1 | 3291.1 | 426 | 433.9 | 342.7 | 296.9 | 338
3924.1 | 3292.1 | 425.9 | 433.9 | 342.5 | 296.7 | 337.8
3925.1 | 3293.1 | 425.9 | 433.7 | 342.3 | 296.6 | 337.6
3926.1 | 3294.1 | 425.7 | 433.7 | 342 | 296.6 | 337.4
3927.1 | 3295.1 | 425.7 | 433.6 | 341.7 | 296.5 | 337.2
3928.1 | 3296.1 | 425.7 | 433.5 | 341.4 | 296.2 | 337.1
3929.1 | 3297.1 | 425.7 | 433.4 | 341.3 | 295.9 | 336.9
3930.1 | 3298.1 | 425.5 | 433.5 | 341.1 | 295.8 | 336.7
3931.1 | 3299.1 | 425.4 | 433.6 | 340.9 | 295.6 | 336.5
3932.1 | 3300.1 | 425.3 | 433.4 | 340.5 | 295.5 | 336.4
3933.1 | 3301.1 | 425.3 | 433.4 | 340.2 | 295.3 | 336.3
3934.1 | 3302.1 | 425.3 | 433.3 | 340 | 295 | 336.1
3935.1 | 3303.1 | 425.2 | 433.4 | 339.8 | 294.8 | 336
3936.1 | 3304.1 | 425.2 | 433.3 | 339.6 | 294.5 | 335.8
3937.1 | 3305.1 | 425.2 | 433 | 339.2 | 294.4 | 335.7
3938.1 | 3306.1 | 425.1 | 432.9 | 338.7 | 294.1 | 335.5
3939.1 | 3307.1 | 425 | 432.8 | 338.4 | 293.9 | 335.3
3940.1 | 3308.1 | 425 | 432.7 | 338 | 293.8 | 335.2
3941.1 | 3309.1 | 425 | 432.6 | 337.8 | 293.5 | 335
3942.1 | 3310.1 | 424.9 | 432.5 | 337.4 | 293.2 | 334.9
3943.1 | 3311.1 | 424.7 | 432.5 | 337.5 | 293 | 334.7
3944.1 | 3312.1 | 424.7 | 432.4 | 337.2 | 292.8 | 334.6
3945.1 | 3313.1 | 424.7 | 432.3 | 336.9 | 292.7 | 334.4
3946.1 | 3314.1 | 424.5 | 432.2 | 336.7 | 292.6 | 334.2
3947.1 | 3315.1 | 424.5 | 432.1 | 336.2 | 292.4 | 334.1
3948.1 | 3316.1 | 424.3 | 432.1 | 335.9 | 292.2 | 333.9
3949.1 | 3317.1 | 424.3 | 432.1 | 335.8 | 292 | 333.8
3950.1 | 3318.1 | 424.2 | 432.1 | 335.5 | 291.9 | 333.6
3951.1 | 3319.1 | 424.2 | 431.9 | 335.3 | 291.8 | 333.5
3952.1 | 3320.1 | 424.2 | 431.8 | 335.1 | 291.7 | 333.3
3953.1 | 3321.1 | 424.1 | 431.9 | 334.7 | 291.5 | 333.2
3954.1 | 3322.1 | 424 | 431.9 | 334.5 | 291.4 | 333.1
3955.1 | 3323.1 | 424 | 431.8 | 334.2 | 291.2 | 333
3956.1 | 3324.1 | 423.9 | 431.7 | 334 | 291.1 | 332.8
3957.1 | 3325.1 | 423.9 | 431.6 | 333.8 | 291 | 332.7
3958.1 | 3326.1 | 423.8 | 431.6 | 333.5 | 290.8 | 332.5
3959.1 | 3327.1 | 423.8 | 431.5 | 333.3 | 290.5 | 332.3
3960.1 | 3328.1 | 423.7 | 431.4 | 333 | 290.4 | 332.2
3961.1 | 3329.1 | 423.6 | 431.3 | 332.7 | 290.1 | 332
3962.1 | 3330.1 | 423.5 | 431.3 | 332.4 | 289.9 | 331.9
3963.1 | 3331.1 | 423.5 | 431.2 | 332.2 | 289.6 | 331.8
3964.1 | 3332.1 | 423.4 | 431 | 331.8 | 289.4 | 331.6
3965.1 | 3333.1 | 423.4 | 431 | 331.5 | 289.1 | 331.5
3966.1 | 3334.1 | 423.4 | 430.9 | 331 | 288.9 | 331.3
3967.1 | 3335.1 | 423.3 | 430.7 | 330.7 | 288.6 | 331.1
3968.1 | 3336.1 | 423.3 | 430.6 | 330.4 | 288.4 | 330.9
3969.1 | 3337.1 | 423.2 | 430.6 | 330.1 | 288.3 | 330.8
3970.1 | 3338.1 | 423 | 430.5 | 329.8 | 288 | 330.6
3971.1 | 3339.1 | 423 | 430.4 | 329.7 | 287.7 | 330.5
3972.1 | 3340.1 | 422.9 | 430.3 | 329.6 | 287.5 | 330.3
3973.1 | 3341.1 | 422.9 | 430.2 | 329.4 | 287.3 | 330.2
3974.1 | 3342.1 | 422.9 | 430.1 | 329.2 | 287.2 | 330.1
3975.1 | 3343.1 | 422.8 | 430 | 329.1 | 287.1 | 329.9
3976.1 | 3344.1 | 422.7 | 429.9 | 328.9 | 287 | 329.8
3977.1 | 3345.1 | 422.6 | 429.9 | 328.6 | 286.8 | 329.6
3978.1 | 3346.1 | 422.4 | 430.1 | 328.3 | 286.6 | 329.4
3979.1 | 3347.1 | 422.4 | 430 | 328.1 | 286.3 | 329.2
3980.1 | 3348.1 | 422.3 | 430 | 327.9 | 286 | 329.1
3981.1 | 3349.1 | 422.2 | 429.9 | 327.6 | 285.7 | 328.9
3982.1 | 3350.1 | 422.2 | 429.8 | 327.2 | 285.5 | 328.8
3983.1 | 3351.1 | 422.1 | 429.6 | 327.1 | 285.3 | 328.6
3984.1 | 3352.1 | 421.9 | 429.6 | 326.9 | 285.1 | 328.5
3985.1 | 3353.1 | 421.9 | 429.5 | 326.9 | 284.9 | 328.4
3986.1 | 3354.1 | 421.9 | 429.6 | 326.6 | 284.7 | 328.2
3987.1 | 3355.1 | 421.8 | 429.5 | 326.4 | 284.5 | 328.1
3988.1 | 3356.1 | 421.8 | 429.4 | 326.1 | 284.2 | 327.9
3989.1 | 3357.1 | 421.7 | 429.3 | 325.9 | 284 | 327.8
3990.1 | 3358.1 | 421.7 | 429.1 | 325.6 | 283.9 | 327.7
3991.1 | 3359.1 | 421.6 | 429.1 | 325.4 | 283.6 | 327.7
3992.1 | 3360.1 | 421.5 | 429 | 325.4 | 283.3 | 327.6
3993.1 | 3361.1 | 421.5 | 428.8 | 325.3 | 283.1 | 327.5
3994.1 | 3362.1 | 421.4 | 428.6 | 325 | 282.9 | 327.4
3995.1 | 3363.1 | 421.4 | 428.5 | 324.8 | 282.8 | 327.3
3996.1 | 3364.1 | 421.3 | 428.4 | 324.5 | 282.6 | 327.2
3997.1 | 3365.1 | 421.3 | 428.4 | 324.3 | 282.4 | 327.1
3998.1 | 3366.1 | 421.2 | 428.3 | 324 | 282.2 | 326.9
3999.1 | 3367.1 | 421.1 | 428.3 | 323.6 | 282 | 326.8
4000.1 | 3368.1 | 420.9 | 428.3 | 323.4 | 281.7 | 326.7
4001.1 | 3369.1 | 420.8 | 428.5 | 323.1 | 281.4 | 326.6
4002.1 | 3370.1 | 420.8 | 428.3 | 322.9 | 281.1 | 326.5
4003.1 | 3371.1 | 420.8 | 428.2 | 322.6 | 280.8 | 326.4
4004.1 | 3372.1 | 420.7 | 428.1 | 322.5 | 280.6 | 326.3
4005.1 | 3373.1 | 420.6 | 428 | 322.3 | 280.4 | 326.2
4006.1 | 3374.1 | 420.5 | 427.9 | 322.1 | 280.3 | 326
4007.1 | 3375.1 | 420.4 | 427.8 | 321.8 | 280.1 | 325.9
4008.1 | 3376.1 | 420.3 | 427.8 | 321.6 | 279.8 | 325.8
4009.1 | 3377.1 | 420.3 | 427.8 | 321.4 | 279.7 | 325.7
4010.1 | 3378.1 | 420.3 | 427.8 | 321.2 | 279.5 | 325.5
4011.1 | 3379.1 | 420.2 | 427.7 | 320.9 | 279.3 | 325.4
4012.1 | 3380.1 | 420.2 | 427.6 | 320.6 | 279 | 325.3
4013.1 | 3381.1 | 420.2 | 427.4 | 320.3 | 278.7 | 325.2
4014.1 | 3382.1 | 420.1 | 427.3 | 320 | 278.5 | 325.1
4015.1 | 3383.1 | 420.1 | 427.2 | 319.7 | 278.3 | 325
4016.1 | 3384.1 | 419.9 | 427.2 | 319.4 | 278.1 | 324.8
4017.1 | 3385.1 | 419.7 | 427.2 | 319.1 | 278 | 324.7
4018.1 | 3386.1 | 419.6 | 427.1 | 318.7 | 277.8 | 324.6
4019.1 | 3387.1 | 419.6 | 427 | 318.4 | 277.6 | 324.5
4020.1 | 3388.1 | 419.6 | 426.9 | 318.3 | 277.4 | 324.4
4021.1 | 3389.1 | 419.5 | 426.9 | 318.1 | 277.2 | 324.2
4022.1 | 3390.1 | 419.4 | 426.8 | 317.9 | 277.1 | 324.1
4023.1 | 3391.1 | 419.4 | 426.8 | 317.7 | 277 | 324
4024.1 | 3392.1 | 419.3 | 426.7 | 317.4 | 276.9 | 323.9
4025.1 | 3393.1 | 419.2 | 426.6 | 317.2 | 276.7 | 323.7
4026.1 | 3394.1 | 419.1 | 426.5 | 316.9 | 276.3 | 323.6
4027.1 | 3395.1 | 419.1 | 426.3 | 316.8 | 276.1 | 323.5
4028.1 | 3396.1 | 419 | 426.3 | 316.7 | 275.9 | 323.3
4029.1 | 3397.1 | 418.9 | 426.4 | 316.4 | 275.6 | 323.2
4030.1 | 3398.1 | 418.8 | 426.4 | 316.1 | 275.5 | 323.1
4031.1 | 3399.1 | 418.8 | 426.2 | 315.7 | 275.3 | 323
4032.1 | 3400.1 | 418.8 | 426.2 | 315.4 | 275 | 322.8
4033.1 | 3401.1 | 418.7 | 426 | 315.3 | 274.8 | 322.7
4034.1 | 3402.1 | 418.7 | 425.9 | 315.3 | 274.6 | 322.6
4035.1 | 3403.1 | 418.6 | 425.8 | 315.3 | 274.3 | 322.5
4036.1 | 3404.1 | 418.5 | 425.7 | 315.1 | 274.1 | 322.4
4037.1 | 3405.1 | 418.5 | 425.6 | 314.9 | 273.9 | 322.2
4038.1 | 3406.1 | 418.4 | 425.5 | 314.7 | 273.7 | 322.1
4039.1 | 3407.1 | 418.3 | 425.5 | 314.7 | 273.5 | 322
4040.1 | 3408.1 | 418.2 | 425.5 | 314.6 | 273.3 | 321.8
4041.1 | 3409.1 | 418.1 | 425.4 | 314.4 | 272.9 | 321.7
4042.1 | 3410.1 | 418.1 | 425.5 | 314 | 272.7 | 321.6
4043.1 | 3411.1 | 418 | 425.4 | 313.8 | 272.6 | 321.4
4044.1 | 3412.1 | 418 | 425.2 | 313.5 | 272.5 | 321.3
4045.1 | 3413.1 | 417.9 | 425.1 | 313.3 | 272.3 | 321.2
4046.1 | 3414.1 | 417.8 | 425 | 313.1 | 272.2 | 321.1
4047.1 | 3415.1 | 417.7 | 424.9 | 313 | 272.1 | 320.9
4048.1 | 3416.1 | 417.6 | 424.8 | 312.9 | 271.9 | 320.8
4049.1 | 3417.1 | 417.6 | 424.8 | 312.7 | 271.7 | 320.7
4050.1 | 3418.1 | 417.5 | 424.7 | 312.5 | 271.4 | 320.6
4051.1 | 3419.1 | 417.3 | 424.8 | 312.2 | 271.1 | 320.4
4052.1 | 3420.1 | 417.3 | 424.6 | 312 | 271 | 320.3
4053.1 | 3421.1 | 417.2 | 424.5 | 311.7 | 271 | 320.2
4054.1 | 3422.1 | 417.2 | 424.4 | 311.4 | 270.9 | 320
4055.1 | 3423.1 | 417.2 | 424.2 | 311.1 | 270.7 | 319.9
4056.1 | 3424.1 | 417.1 | 424.2 | 310.8 | 270.6 | 319.8
4057.1 | 3425.1 | 416.9 | 424.4 | 310.7 | 270.4 | 319.6
4058.1 | 3426.1 | 416.9 | 424.2 | 310.5 | 270.2 | 319.5
4059.1 | 3427.1 | 416.9 | 424.1 | 310.3 | 269.9 | 319.4
4060.1 | 3428.1 | 416.9 | 424 | 310.1 | 269.6 | 319.2
4061.1 | 3429.1 | 416.7 | 423.9 | 310 | 269.5 | 319.1
4062.1 | 3430.1 | 416.6 | 423.9 | 309.9 | 269.3 | 319
4063.1 | 3431.1 | 416.6 | 423.9 | 309.7 | 269.1 | 318.9
4064.1 | 3432.1 | 416.5 | 423.7 | 309.6 | 268.8 | 318.7
4065.1 | 3433.1 | 416.4 | 423.6 | 309.4 | 268.6 | 318.6
4066.1 | 3434.1 | 416.4 | 423.5 | 309.1 | 268.4 | 318.5
4067.1 | 3435.1 | 416.3 | 423.4 | 308.8 | 268.3 | 318.4
4068.1 | 3436.1 | 416.2 | 423.4 | 308.6 | 268.1 | 318.3
4069.1 | 3437.1 | 416.2 | 423.3 | 308.4 | 267.9 | 318.2
4070.1 | 3438.1 | 416.1 | 423.1 | 308.2 | 267.6 | 318
4071.1 | 3439.1 | 416 | 423.1 | 307.9 | 267.5 | 317.9
4072.1 | 3440.1 | 415.9 | 423.1 | 307.7 | 267.3 | 317.8
4073.1 | 3441.1 | 415.9 | 422.9 | 307.5 | 267.2 | 317.6
4074.1 | 3442.1 | 415.9 | 422.8 | 307.3 | 267.1 | 317.5
4075.1 | 3443.1 | 415.8 | 422.8 | 307 | 266.9 | 317.4
4076.1 | 3444.1 | 415.7 | 422.7 | 306.7 | 266.7 | 317.3
4077.1 | 3445.1 | 415.6 | 422.7 | 306.4 | 266.7 | 317.2
4078.1 | 3446.1 | 415.5 | 422.7 | 306 | 266.8 | 317
4079.1 | 3447.1 | 415.5 | 422.7 | 305.6 | 266.7 | 316.9
4080.1 | 3448.1 | 415.4 | 422.6 | 305.3 | 266.7 | 316.7
4081.1 | 3449.1 | 415.4 | 422.4 | 305 | 266.6 | 316.6
4082.1 | 3450.1 | 415.3 | 422.5 | 304.8 | 266.5 | 316.5
4083.1 | 3451.1 | 415.2 | 422.4 | 304.5 | 266.4 | 316.4
4084.1 | 3452.1 | 415.2 | 422.3 | 304.2 | 266.3 | 316.3
4085.1 | 3453.1 | 415.1 | 422.2 | 304 | 266.3 | 316.2
4086.1 | 3454.1 | 415 | 422.2 | 303.7 | 266 | 316.1
4087.1 | 3455.1 | 414.9 | 422.2 | 303.5 | 265.7 | 315.9
4088.1 | 3456.1 | 414.9 | 422 | 303.3 | 265.5 | 315.8
4089.1 | 3457.1 | 414.9 | 421.9 | 303.1 | 265.2 | 315.7
4090.1 | 3458.1 | 414.8 | 422 | 303 | 265 | 315.6
4091.1 | 3459.1 | 414.7 | 422 | 302.8 | 264.6 | 315.4
4092.1 | 3460.1 | 414.6 | 421.9 | 302.5 | 264.4 | 315.3
4093.1 | 3461.1 | 414.6 | 421.7 | 302.3 | 264.1 | 315.2
4094.1 | 3462.1 | 414.6 | 421.5 | 302.1 | 263.9 | 315.1
4095.1 | 3463.1 | 414.5 | 421.5 | 301.9 | 263.8 | 314.9
4096.1 | 3464.1 | 414.4 | 421.5 | 301.6 | 263.6 | 314.8
4097.1 | 3465.1 | 414.3 | 421.4 | 301.3 | 263.3 | 314.7
4098.1 | 3466.1 | 414.3 | 421.3 | 301.1 | 263.2 | 314.6
4099.1 | 3467.1 | 414.3 | 421.4 | 300.8 | 263.2 | 314.4
4100.1 | 3468.1 | 414.2 | 421.2 | 300.6 | 263.2 | 314.3
4101.1 | 3469.1 | 414.2 | 421.2 | 300.4 | 263.2 | 314.2
4102.1 | 3470.1 | 414.1 | 421 | 300.2 | 263.1 | 314.1
4103.1 | 3471.1 | 414 | 421 | 300 | 262.8 | 314
4104.1 | 3472.1 | 414 | 420.8 | 299.7 | 262.7 | 313.8
4105.1 | 3473.1 | 413.9 | 420.8 | 299.5 | 262.6 | 313.7
4106.1 | 3474.1 | 413.8 | 420.9 | 299.2 | 262.3 | 313.6
4107.1 | 3475.1 | 413.8 | 420.8 | 298.9 | 262.1 | 313.5
4108.1 | 3476.1 | 413.7 | 420.6 | 298.6 | 262 | 313.4
4109.1 | 3477.1 | 413.6 | 420.5 | 298.3 | 261.9 | 313.2
4110.1 | 3478.1 | 413.5 | 420.4 | 298 | 261.8 | 313.1
4111.1 | 3479.1 | 413.5 | 420.4 | 297.7 | 261.5 | 313
4112.1 | 3480.1 | 413.4 | 420.5 | 297.4 | 261.3 | 312.9
4113.1 | 3481.1 | 413.4 | 420.5 | 297.2 | 261.2 | 312.8
4114.1 | 3482.1 | 413.3 | 420.3 | 296.9 | 261 | 312.7
4115.1 | 3483.1 | 413.3 | 420.3 | 296.6 | 260.8 | 312.6
4116.1 | 3484.1 | 413.2 | 420.2 | 296.3 | 260.6 | 312.5
4117.1 | 3485.1 | 413.2 | 420 | 296 | 260.4 | 312.4
4118.1 | 3486.1 | 413.1 | 420 | 295.7 | 260.2 | 312.3
4119.1 | 3487.1 | 413.1 | 419.9 | 295.4 | 260.1 | 312.2
4120.1 | 3488.1 | 413.1 | 419.8 | 295.2 | 259.8 | 312
4121.1 | 3489.1 | 412.9 | 419.8 | 294.9 | 259.6 | 311.9
4122.1 | 3490.1 | 412.9 | 419.7 | 294.8 | 259.3 | 311.8
4123.1 | 3491.1 | 412.8 | 419.7 | 294.5 | 259.1 | 311.7
4124.1 | 3492.1 | 412.8 | 419.9 | 294.3 | 259.1 | 311.5
4125.1 | 3493.1 | 412.7 | 419.7 | 294.1 | 259 | 311.4
4126.1 | 3494.1 | 412.7 | 419.5 | 293.9 | 258.8 | 311.3
4127.1 | 3495.1 | 412.7 | 419.4 | 293.7 | 258.6 | 311.2
4128.1 | 3496.1 | 412.6 | 419.2 | 293.6 | 258.4 | 311.1
4129.1 | 3497.1 | 412.5 | 419.2 | 293.4 | 258.2 | 311
4130.1 | 3498.1 | 412.4 | 419.2 | 293.2 | 258.1 | 310.8
4131.1 | 3499.1 | 412.4 | 419.2 | 292.9 | 257.9 | 310.7
4132.1 | 3500.1 | 412.3 | 419.1 | 292.7 | 257.6 | 310.6
4133.1 | 3501.1 | 412.2 | 419.2 | 292.5 | 257.5 | 310.5
4134.1 | 3502.1 | 412.2 | 419.2 | 292.3 | 257.3 | 310.4
4135.1 | 3503.1 | 412.1 | 419.1 | 292.1 | 257 | 310.3
4136.1 | 3504.1 | 412.1 | 418.8 | 291.9 | 256.7 | 310.2
4137.1 | 3505.1 | 412.1 | 418.7 | 291.6 | 256.4 | 310
4138.1 | 3506.1 | 412 | 418.6 | 291.3 | 256.2 | 309.9
4139.1 | 3507.1 | 411.9 | 418.6 | 291.1 | 256 | 309.8
4140.1 | 3508.1 | 411.9 | 418.5 | 290.9 | 255.8 | 309.7
4141.1 | 3509.1 | 411.8 | 418.4 | 290.7 | 255.6 | 309.5
4142.1 | 3510.1 | 411.8 | 418.4 | 290.5 | 255.5 | 309.4
4143.1 | 3511.1 | 411.7 | 418.4 | 290.3 | 255.2 | 309.3
4144.1 | 3512.1 | 411.7 | 418.3 | 290.4 | 254.8 | 309.2
4145.1 | 3513.1 | 411.6 | 418.2 | 290.1 | 254.6 | 309
4146.1 | 3514.1 | 411.5 | 418.2 | 289.9 | 254.3 | 308.9
4147.1 | 3515.1 | 411.4 | 418.2 | 289.6 | 254 | 308.8
4148.1 | 3516.1 | 411.4 | 418.2 | 289.3 | 253.8 | 308.7
4149.1 | 3517.1 | 411.4 | 418.1 | 289.1 | 253.6 | 308.6
4150.1 | 3518.1 | 411.3 | 418 | 288.9 | 253.6 | 308.4
4151.1 | 3519.1 | 411.2 | 417.9 | 288.7 | 253.5 | 308.3
4152.2 | 3520.2 | 411.2 | 417.8 | 288.5 | 253.5 | 308.2
4153.2 | 3521.2 | 411.1 | 417.8 | 288.2 | 253.3 | 308.1
4154.2 | 3522.2 | 411.1 | 417.6 | 287.9 | 253 | 308
4155.2 | 3523.2 | 411 | 417.7 | 287.7 | 252.7 | 307.9
4156.2 | 3524.2 | 411 | 417.7 | 287.4 | 252.5 | 307.8
4157.2 | 3525.2 | 410.9 | 417.7 | 287.1 | 252.3 | 307.7
4158.2 | 3526.2 | 410.8 | 417.6 | 286.8 | 252 | 307.6
4159.2 | 3527.2 | 410.8 | 417.4 | 286.6 | 251.8 | 307.5
4160.2 | 3528.2 | 410.8 | 417.3 | 286.3 | 251.7 | 307.4
4161.2 | 3529.2 | 410.7 | 417.2 | 286.2 | 251.6 | 307.3
4162.2 | 3530.2 | 410.7 | 417.3 | 285.9 | 251.4 | 307.2
4163.2 | 3531.2 | 410.6 | 417.4 | 285.8 | 251.3 | 307.1
4164.2 | 3532.2 | 410.6 | 417.3 | 285.6 | 251 | 307
4165.2 | 3533.2 | 410.5 | 417.1 | 285.3 | 250.8 | 306.8
4166.2 | 3534.2 | 410.5 | 417 | 285.1 | 250.4 | 306.7
4167.2 | 3535.2 | 410.4 | 417.1 | 284.9 | 250.3 | 306.6
4168.2 | 3536.2 | 410.3 | 417 | 284.7 | 250.2 | 306.5
4169.2 | 3537.2 | 410.3 | 416.9 | 284.4 | 250 | 306.4
4170.2 | 3538.2 | 410.2 | 416.9 | 284.2 | 249.9 | 306.3
4171.2 | 3539.2 | 410.2 | 416.8 | 284.3 | 249.7 | 306.2
4172.2 | 3540.2 | 410.1 | 416.6 | 284.1 | 249.6 | 306.1
4173.2 | 3541.2 | 410.1 | 416.6 | 284.1 | 249.3 | 306
4174.2 | 3542.2 | 410 | 416.7 | 284 | 248.7 | 305.8
4175.2 | 3543.2 | 409.9 | 416.6 | 283.9 | 248.6 | 305.7
4176.2 | 3544.2 | 409.9 | 416.5 | 283.7 | 248.5 | 305.6
4177.2 | 3545.2 | 409.9 | 416.3 | 283.6 | 248.4 | 305.5
4178.2 | 3546.2 | 409.8 | 416.3 | 283.3 | 248.2 | 305.4
4179.2 | 3547.2 | 409.8 | 416.3 | 283.1 | 248 | 305.3
4180.2 | 3548.2 | 409.7 | 416.4 | 282.9 | 247.9 | 305.2
4181.2 | 3549.2 | 409.6 | 416.2 | 282.7 | 247.7 | 305.1
4182.2 | 3550.2 | 409.5 | 416.1 | 282.5 | 247.5 | 305
4183.2 | 3551.2 | 409.5 | 416 | 282.2 | 247.1 | 304.9
4184.2 | 3552.2 | 409.4 | 415.9 | 281.9 | 246.8 | 304.8
4185.2 | 3553.2 | 409.4 | 415.8 | 281.7 | 246.7 | 304.7
4186.2 | 3554.2 | 409.4 | 415.8 | 281.5 | 246.5 | 304.6
4187.2 | 3555.2 | 409.3 | 416 | 281.3 | 246.4 | 304.5
4188.2 | 3556.2 | 409.3 | 416 | 281.3 | 246.1 | 304.4
4189.2 | 3557.2 | 409.2 | 415.7 | 281.1 | 246 | 304.3
4190.2 | 3558.2 | 409.2 | 415.8 | 281 | 245.9 | 304.2
4191.2 | 3559.2 | 409.1 | 415.9 | 280.8 | 245.6 | 304.1
4192.2 | 3560.2 | 409.1 | 415.7 | 280.6 | 245.4 | 304
4193.2 | 3561.2 | 409 | 415.5 | 280.4 | 245 | 303.8
4194.2 | 3562.2 | 409 | 415.5 | 280.1 | 244.7 | 303.7
4195.2 | 3563.2 | 408.9 | 415.5 | 280.1 | 244.5 | 303.7
4196.2 | 3564.2 | 408.9 | 415.4 | 279.9 | 244.4 | 303.5
4197.2 | 3565.2 | 408.8 | 415.4 | 279.7 | 244.1 | 303.4
4198.2 | 3566.2 | 408.8 | 415.3 | 279.6 | 243.9 | 303.3
4199.2 | 3567.2 | 408.7 | 415.1 | 279.5 | 243.7 | 303.2
4200.2 | 3568.2 | 408.7 | 415.1 | 279.3 | 243.5 | 303.1
4201.2 | 3569.2 | 408.6 | 415.1 | 279.1 | 243.2 | 303
4202.2 | 3570.2 | 408.5 | 415 | 278.8 | 243.1 | 302.9
4203.2 | 3571.2 | 408.5 | 415 | 278.5 | 242.9 | 302.8
4204.2 | 3572.2 | 408.5 | 414.9 | 278.3 | 242.5 | 302.7
4205.2 | 3573.2 | 408.4 | 415 | 278.2 | 242.3 | 302.6
4206.2 | 3574.2 | 408.3 | 414.9 | 278 | 242.1 | 302.6
4207.2 | 3575.2 | 408.3 | 414.8 | 277.9 | 241.9 | 302.5
4208.2 | 3576.2 | 408.2 | 414.7 | 277.9 | 241.7 | 302.4
4209.2 | 3577.2 | 408.2 | 414.6 | 277.7 | 241.4 | 302.3
4210.2 | 3578.2 | 408.2 | 414.6 | 277.7 | 241.2 | 302.2
4211.2 | 3579.2 | 408.1 | 414.6 | 277.7 | 241 | 302
4212.2 | 3580.2 | 408.1 | 414.7 | 277.8 | 240.6 | 302
4213.2 | 3581.2 | 408 | 414.7 | 277.6 | 240.3 | 301.9
4214.2 | 3582.2 | 407.9 | 414.4 | 277.6 | 239.9 | 301.7
4215.2 | 3583.2 | 407.9 | 414.3 | 277.4 | 239.7 | 301.6
4216.2 | 3584.2 | 407.9 | 414.3 | 277.2 | 239.4 | 301.6
4217.2 | 3585.2 | 407.8 | 414.4 | 277.1 | 239.3 | 301.4
4218.2 | 3586.2 | 407.8 | 414.3 | 277.1 | 239 | 301.4
4219.2 | 3587.2 | 407.7 | 414.2 | 277.1 | 238.8 | 301.3
4220.2 | 3588.2 | 407.6 | 414.2 | 276.9 | 238.6 | 301.2
4221.2 | 3589.2 | 407.6 | 414.1 | 276.7 | 238.6 | 301.1
4222.2 | 3590.2 | 407.6 | 414 | 276.5 | 238.5 | 301
4223.2 | 3591.2 | 407.5 | 414 | 276.3 | 238.3 | 301
4224.2 | 3592.2 | 407.4 | 413.9 | 276.1 | 238.1 | 300.8
4225.2 | 3593.2 | 407.4 | 414 | 275.9 | 237.9 | 300.8
4226.2 | 3594.2 | 407.4 | 414.1 | 275.7 | 237.7 | 300.7
4227.2 | 3595.2 | 407.3 | 413.9 | 275.6 | 237.5 | 300.6
4228.2 | 3596.2 | 407.2 | 413.9 | 275.6 | 237.3 | 300.5
4229.2 | 3597.2 | 407.2 | 413.8 | 275.6 | 236.9 | 300.4
4230.2 | 3598.2 | 407.1 | 413.6 | 275.3 | 236.7 | 300.3
4231.2 | 3599.2 | 407.1 | 413.5 | 275 | 236.6 | 300.2
4232.2 | 3600.2 | 407.1 | 413.4 | 274.7 | 236.2 | 300.1
4233.2 | 3601.2 | 407 | 413.4 | 274.6 | 235.7 | 300
4234.2 | 3602.2 | 407 | 413.4 | 274.3 | 235.6 | 299.9
4235.2 | 3603.2 | 406.9 | 413.4 | 274.1 | 235.5 | 299.8
4236.2 | 3604.2 | 406.9 | 413.4 | 273.7 | 235.3 | 299.7
4237.2 | 3605.2 | 406.8 | 413.2 | 273.4 | 235 | 299.6
4238.2 | 3606.2 | 406.8 | 413.2 | 273 | 234.8 | 299.5
4239.2 | 3607.2 | 406.7 | 413.1 | 272.8 | 234.5 | 299.4
4240.2 | 3608.2 | 406.7 | 413.1 | 272.6 | 234.4 | 299.3
4241.2 | 3609.2 | 406.6 | 413 | 272.5 | 234.2 | 299.2
4242.2 | 3610.2 | 406.6 | 413 | 272.5 | 233.8 | 299.1
4243.2 | 3611.2 | 406.5 | 413 | 272.4 | 233.7 | 299
4244.2 | 3612.2 | 406.5 | 412.9 | 272.6 | 233.2 | 298.9
4245.2 | 3613.2 | 406.4 | 412.9 | 272.9 | 233.2 | 298.8
4246.2 | 3614.2 | 406.4 | 412.8 | 272.8 | 233.2 | 298.8
4247.2 | 3615.2 | 406.3 | 412.9 | 272.7 | 233.1 | 298.7
4248.2 | 3616.2 | 406.3 | 412.8 | 272.8 | 233 | 298.6
4249.2 | 3617.2 | 406.2 | 412.8 | 272.5 | 232.9 | 298.6
4250.2 | 3618.2 | 406.2 | 412.6 | 272.4 | 232.8 | 298.5
4251.2 | 3619.2 | 406.1 | 412.6 | 272.6 | 232.3 | 298.4
4252.2 | 3620.2 | 406.1 | 412.6 | 272.5 | 232.2 | 298.3
4253.2 | 3621.2 | 406 | 412.7 | 272.4 | 231.9 | 298.2
4254.2 | 3622.2 | 406 | 412.6 | 272.2 | 231.7 | 298.1
4255.2 | 3623.2 | 405.9 | 412.6 | 271.9 | 231.5 | 298
4256.2 | 3624.2 | 405.9 | 412.5 | 271.6 | 231.3 | 297.9
4257.2 | 3625.2 | 405.9 | 412.4 | 271.8 | 230.9 | 297.8
4258.2 | 3626.2 | 405.8 | 412.4 | 271.7 | 230.6 | 297.7
4259.2 | 3627.2 | 405.8 | 412.4 | 271.5 | 230.4 | 297.7
4260.2 | 3628.2 | 405.7 | 412.3 | 271.3 | 230.3 | 297.6
4261.2 | 3629.2 | 405.7 | 412.3 | 271.2 | 230 | 297.6
4262.2 | 3630.2 | 405.6 | 412.4 | 271.1 | 229.8 | 297.5
4263.2 | 3631.2 | 405.6 | 412.3 | 271 | 229.6 | 297.4
4264.2 | 3632.2 | 405.5 | 412.2 | 270.9 | 229.5 | 297.3
4265.2 | 3633.2 | 405.5 | 412.2 | 270.8 | 229.3 | 297.2
4266.2 | 3634.2 | 405.5 | 412.2 | 270.6 | 229.2 | 297.1
4267.2 | 3635.2 | 405.4 | 412 | 270.5 | 229.1 | 297.1
4268.2 | 3636.2 | 405.4 | 411.9 | 270.7 | 228.8 | 297
4269.2 | 3637.2 | 405.3 | 411.8 | 270.7 | 228.4 | 296.9
4270.2 | 3638.2 | 405.3 | 411.8 | 270.8 | 228.2 | 296.8
4271.2 | 3639.2 | 405.2 | 411.9 | 270.5 | 228 | 296.7
4272.2 | 3640.2 | 405.2 | 411.9 | 270.4 | 227.9 | 296.6
4273.2 | 3641.2 | 405.1 | 411.7 | 270.7 | 227.7 | 296.5
4274.2 | 3642.2 | 405.1 | 411.8 | 270.5 | 227.4 | 296.4
4275.2 | 3643.2 | 405.1 | 411.8 | 270.2 | 227.2 | 296.3
4276.2 | 3644.2 | 405 | 411.8 | 270.3 | 227.1 | 296.3
4277.2 | 3645.2 | 405 | 411.6 | 270.8 | 226.6 | 296.2
4278.2 | 3646.2 | 404.9 | 411.5 | 270.5 | 226.3 | 296
4279.2 | 3647.2 | 404.9 | 411.4 | 270.2 | 226.2 | 295.9
4280.2 | 3648.2 | 404.8 | 411.5 | 270 | 226.2 | 295.9
4281.2 | 3649.2 | 404.8 | 411.5 | 270.3 | 225.7 | 295.8
4282.2 | 3650.2 | 404.7 | 411.4 | 269.8 | 225.2 | 295.6
4283.2 | 3651.2 | 404.7 | 411.4 | 269.4 | 225.1 | 295.5
4284.2 | 3652.2 | 404.7 | 411.3 | 269.1 | 225 | 295.4
4285.2 | 3653.2 | 404.6 | 411.2 | 268.7 | 224.9 | 295.3
4286.2 | 3654.2 | 404.6 | 411.3 | 268.2 | 224.8 | 295.3
4287.2 | 3655.2 | 404.5 | 411.4 | 267.8 | 224.5 | 295.2
4288.2 | 3656.2 | 404.5 | 411.3 | 267.5 | 224.3 | 295.1
4289.2 | 3657.2 | 404.4 | 411.2 | 267.2 | 224.2 | 295
4290.2 | 3658.2 | 404.4 | 411.1 | 266.9 | 224.1 | 295
4291.2 | 3659.2 | 404.4 | 411.1 | 266.5 | 223.8 | 294.9
4292.2 | 3660.2 | 404.3 | 411 | 266.1 | 223.6 | 294.8
4293.2 | 3661.2 | 404.3 | 411.1 | 265.6 | 223.4 | 294.7
4294.2 | 3662.2 | 404.2 | 411.1 | 265.2 | 223 | 294.6
4295.2 | 3663.2 | 404.2 | 410.9 | 265 | 222.7 | 294.5
4296.2 | 3664.2 | 404.1 | 411 | 264.8 | 222.6 | 294.5
4297.2 | 3665.2 | 404.1 | 410.9 | 264.6 | 222.4 | 294.4
4298.2 | 3666.2 | 404 | 410.9 | 264.3 | 222.3 | 294.4
4299.2 | 3667.2 | 404 | 410.8 | 264.1 | 222 | 294.3
4300.2 | 3668.2 | 404 | 410.9 | 264 | 221.7 | 294.2
4301.2 | 3669.2 | 403.9 | 410.9 | 263.7 | 221.6 | 294.1
4302.2 | 3670.2 | 403.9 | 410.8 | 263.5 | 221.5 | 294.1
4303.2 | 3671.2 | 403.9 | 410.8 | 263.4 | 221.4 | 294
4304.2 | 3672.2 | 403.8 | 410.6 | 263.2 | 221.2 | 293.9
4305.2 | 3673.2 | 403.8 | 410.6 | 262.9 | 220.8 | 293.8
4306.2 | 3674.2 | 403.8 | 410.8 | 262.6 | 220.6 | 293.7
4307.2 | 3675.2 | 403.7 | 410.6 | 262.3 | 220.5 | 293.6
4308.2 | 3676.2 | 403.7 | 410.6 | 262 | 220.3 | 293.5
4309.2 | 3677.2 | 403.6 | 410.5 | 261.7 | 220.2 | 293.4
4310.2 | 3678.2 | 403.6 | 410.4 | 261.3 | 219.9 | 293.4
4311.2 | 3679.2 | 403.5 | 410.3 | 260.9 | 219.7 | 293.3
4312.2 | 3680.2 | 403.5 | 410.3 | 260.6 | 219.5 | 293.2
4313.2 | 3681.2 | 403.4 | 410.2 | 260.3 | 219.3 | 293.2
4314.2 | 3682.2 | 403.4 | 410.2 | 260 | 218.8 | 293.1
4315.2 | 3683.2 | 403.4 | 410.2 | 259.8 | 218.4 | 292.9
4316.2 | 3684.2 | 403.3 | 410.2 | 259.6 | 218.2 | 292.8
4317.2 | 3685.2 | 403.3 | 410.1 | 259.8 | 217.9 | 292.8
4318.2 | 3686.2 | 403.3 | 410.2 | 260.1 | 217.4 | 292.7
4319.2 | 3687.2 | 403.2 | 410.1 | 259.7 | 217.1 | 292.6
4320.2 | 3688.2 | 403.2 | 410.2 | 259.4 | 216.9 | 292.5
4321.2 | 3689.2 | 403.2 | 410 | 259 | 216.6 | 292.4
4322.2 | 3690.2 | 403.1 | 410 | 258.5 | 216.1 | 292.3
4323.2 | 3691.2 | 403.1 | 410 | 258.2 | 215.9 | 292.2
4324.2 | 3692.2 | 403 | 409.9 | 257.9 | 215.7 | 292.2
4325.2 | 3693.2 | 403 | 410 | 257.4 | 215.5 | 292.1
4326.2 | 3694.2 | 402.9 | 409.9 | 257 | 215 | 292
4327.2 | 3695.2 | 402.9 | 409.8 | 256.6 | 214.4 | 291.8
4328.2 | 3696.2 | 402.9 | 409.8 | 256.4 | 214.1 | 291.7
4329.2 | 3697.2 | 402.9 | 409.7 | 256 | 214.1 | 291.7
4330.2 | 3698.2 | 402.8 | 409.6 | 255.8 | 213.9 | 291.6
4331.2 | 3699.2 | 402.8 | 409.6 | 255.9 | 213.4 | 291.5
4332.2 | 3700.2 | 402.7 | 409.7 | 255.7 | 213 | 291.3
4333.2 | 3701.2 | 402.7 | 409.6 | 255.4 | 212.9 | 291.2
4334.2 | 3702.2 | 402.7 | 409.6 | 255.1 | 212.8 | 291.1
4335.2 | 3703.2 | 402.6 | 409.5 | 254.9 | 212.6 | 291.1
4336.2 | 3704.2 | 402.6 | 409.4 | 254.6 | 212.4 | 291
4337.2 | 3705.2 | 402.5 | 409.5 | 254.5 | 212.4 | 290.9
4338.2 | 3706.2 | 402.5 | 409.5 | 254.4 | 212.2 | 290.8
4339.2 | 3707.2 | 402.5 | 409.4 | 254.2 | 212.1 | 290.7
4340.2 | 3708.2 | 402.5 | 409.4 | 254.1 | 211.9 | 290.6
4341.2 | 3709.2 | 402.4 | 409.4 | 254.2 | 211.9 | 290.6
4342.2 | 3710.2 | 402.4 | 409.4 | 254.2 | 211.9 | 290.6
4343.2 | 3711.2 | 402.4 | 409.3 | 254.4 | 212 | 290.6
4344.2 | 3712.2 | 402.3 | 409.3 | 254.3 | 211.8 | 290.5
4345.2 | 3713.2 | 402.3 | 409.2 | 254.2 | 211.5 | 290.4
4346.2 | 3714.2 | 402.3 | 409.2 | 254 | 210.7 | 290.2
4347.2 | 3715.2 | 402.2 | 409.2 | 253.8 | 210.6 | 290
4348.2 | 3716.2 | 402.2 | 409.2 | 253.7 | 210.6 | 289.9
4349.2 | 3717.2 | 402.2 | 409.3 | 253.6 | 210.5 | 289.9
4350.2 | 3718.2 | 402.1 | 409.1 | 253.4 | 210.3 | 289.8
4351.2 | 3719.2 | 402.1 | 409.1 | 253 | 209.7 | 289.7
4352.2 | 3720.2 | 402.1 | 409.2 | 252.8 | 209.2 | 289.6
4353.2 | 3721.2 | 402.1 | 409.2 | 252.4 | 209.1 | 289.5
4354.2 | 3722.2 | 402 | 409 | 252 | 208.8 | 289.4
4355.2 | 3723.2 | 402 | 408.9 | 251.7 | 208.8 | 289.3
4356.2 | 3724.2 | 401.9 | 409 | 251.3 | 208.7 | 289.2
4357.2 | 3725.2 | 401.9 | 408.9 | 251 | 208.5 | 289.1
4358.2 | 3726.2 | 401.9 | 409 | 250.7 | 208.4 | 289
4359.2 | 3727.2 | 401.8 | 408.9 | 250.4 | 208.2 | 288.9
4360.2 | 3728.2 | 401.8 | 408.9 | 250.1 | 208.1 | 288.9
4361.2 | 3729.2 | 401.8 | 408.8 | 249.7 | 207.9 | 288.8
4362.2 | 3730.2 | 401.8 | 408.9 | 249.5 | 207.7 | 288.7
4363.2 | 3731.2 | 401.7 | 408.8 | 249.2 | 207.7 | 288.6
4364.2 | 3732.2 | 401.8 | 408.8 | 248.9 | 207.5 | 288.6
4365.2 | 3733.2 | 401.7 | 408.8 | 248.5 | 207.3 | 288.5
4366.2 | 3734.2 | 401.6 | 408.7 | 248.2 | 207.1 | 288.4
4367.2 | 3735.2 | 401.6 | 408.6 | 248 | 207 | 288.4
4368.2 | 3736.2 | 401.6 | 408.6 | 247.8 | 206.9 | 288.4
4369.2 | 3737.2 | 401.6 | 408.6 | 247.5 | 206.5 | 288.2
4370.2 | 3738.2 | 401.5 | 408.7 | 247.2 | 206.4 | 288.2
4371.2 | 3739.2 | 401.5 | 408.8 | 246.9 | 206.2 | 288.1
4372.2 | 3740.2 | 401.5 | 408.7 | 246.6 | 206.1 | 288
4373.2 | 3741.2 | 401.5 | 408.6 | 246.3 | 205.9 | 287.9
4374.2 | 3742.2 | 401.5 | 408.6 | 246.2 | 205.7 | 287.9
4375.2 | 3743.2 | 401.4 | 408.5 | 246.6 | 205.5 | 287.8
4376.2 | 3744.2 | 401.4 | 408.6 | 246.5 | 205.2 | 287.7
4377.2 | 3745.2 | 401.4 | 408.5 | 246.2 | 205 | 287.6
4378.2 | 3746.2 | 401.3 | 408.5 | 246.1 | 204.8 | 287.5
4379.2 | 3747.2 | 401.3 | 408.4 | 245.9 | 204.5 | 287.4
4380.2 | 3748.2 | 401.3 | 408.4 | 245.6 | 204.2 | 287.3
4381.2 | 3749.2 | 401.3 | 408.4 | 245.2 | 203.9 | 287.2
4382.2 | 3750.2 | 401.2 | 408.4 | 244.8 | 203.6 | 287.1
4383.2 | 3751.2 | 401.2 | 408.3 | 244.5 | 203.1 | 287.1
4384.2 | 3752.2 | 401.2 | 408.3 | 244.2 | 202.7 | 286.9
4385.2 | 3753.2 | 401.2 | 408.4 | 243.9 | 202.5 | 286.8
4386.2 | 3754.2 | 401.1 | 408.2 | 243.6 | 202.2 | 286.7
4387.2 | 3755.2 | 401.1 | 408.1 | 243.4 | 202 | 286.6
4388.2 | 3756.2 | 401.1 | 408.1 | 243.1 | 201.9 | 286.5
4389.2 | 3757.2 | 401 | 408.1 | 242.8 | 201.9 | 286.4
4390.2 | 3758.2 | 401 | 408.2 | 242.5 | 201.7 | 286.4
4391.2 | 3759.2 | 401 | 408.1 | 242.2 | 201.4 | 286.3
4392.2 | 3760.2 | 401 | 408.1 | 242 | 201.3 | 286.2
4393.2 | 3761.2 | 400.9 | 408.1 | 241.9 | 201.3 | 286.1
4394.2 | 3762.2 | 400.9 | 408 | 241.5 | 201.3 | 286
4395.2 | 3763.2 | 400.9 | 408 | 241.2 | 201.2 | 286
4396.2 | 3764.2 | 400.9 | 407.9 | 241 | 200.9 | 285.8
4397.2 | 3765.2 | 400.9 | 407.9 | 240.8 | 200.7 | 285.8
4398.2 | 3766.2 | 400.8 | 408 | 240.5 | 200.4 | 285.7
4399.2 | 3767.2 | 400.8 | 408.1 | 240.2 | 200.1 | 285.6
4400.2 | 3768.2 | 400.8 | 408 | 240.2 | 200.2 | 285.5
4401.2 | 3769.2 | 400.8 | 407.9 | 240.1 | 200.1 | 285.4
4402.2 | 3770.2 | 400.8 | 407.9 | 239.9 | 199.9 | 285.4
4403.2 | 3771.2 | 400.7 | 407.8 | 239.7 | 199.8 | 285.3
4404.2 | 3772.2 | 400.7 | 407.8 | 239.6 | 199.6 | 285.2
4405.2 | 3773.2 | 400.7 | 407.9 | 239.4 | 199.2 | 285.1
4406.2 | 3774.2 | 400.6 | 407.9 | 239.2 | 199.1 | 285
4407.2 | 3775.2 | 400.6 | 407.8 | 239 | 199 | 284.9
4408.2 | 3776.2 | 400.6 | 407.7 | 238.8 | 199 | 284.9
4409.2 | 3777.2 | 400.6 | 407.7 | 238.8 | 198.9 | 284.8
4410.2 | 3778.2 | 400.5 | 407.8 | 238.5 | 198.7 | 284.8
4411.2 | 3779.2 | 400.5 | 407.7 | 238.4 | 198.5 | 284.7
4412.2 | 3780.2 | 400.5 | 407.8 | 238.4 | 198.3 | 284.6
4413.2 | 3781.2 | 400.5 | 407.8 | 238.4 | 198.1 | 284.6
4414.2 | 3782.2 | 400.5 | 407.7 | 238.3 | 198 | 284.5
4415.2 | 3783.2 | 400.5 | 407.6 | 238 | 198 | 284.4
4416.2 | 3784.2 | 400.4 | 407.7 | 237.7 | 197.8 | 284.4
4417.2 | 3785.2 | 400.4 | 407.6 | 237.4 | 197.6 | 284.2
4418.2 | 3786.2 | 400.4 | 407.6 | 237.3 | 197.5 | 284.1
4419.2 | 3787.2 | 400.3 | 407.5 | 237.1 | 197.4 | 284
4420.2 | 3788.2 | 400.3 | 407.5 | 237 | 197.3 | 284
4421.2 | 3789.2 | 400.4 | 407.6 | 236.9 | 197.3 | 283.9
4422.2 | 3790.2 | 400.3 | 407.6 | 236.8 | 197.2 | 283.9
4423.2 | 3791.2 | 400.3 | 407.6 | 236.7 | 197.1 | 283.8
4424.2 | 3792.2 | 400.3 | 407.7 | 236.7 | 197 | 283.7
4425.2 | 3793.2 | 400.2 | 407.5 | 236.4 | 196.9 | 283.6
4426.2 | 3794.2 | 400.2 | 407.4 | 236 | 196.6 | 283.5
4427.2 | 3795.2 | 400.2 | 407.4 | 235.6 | 196.3 | 283.4
4428.2 | 3796.2 | 400.2 | 407.4 | 235.6 | 196.2 | 283.3
4429.2 | 3797.2 | 400.2 | 407.4 | 235.9 | 195.9 | 283.2
4430.2 | 3798.2 | 400.1 | 407.4 | 235.8 | 195.5 | 283.1
4431.2 | 3799.2 | 400.1 | 407.4 | 235.7 | 195.3 | 283
4432.2 | 3800.2 | 400.1 | 407.4 | 235.6 | 195 | 282.9
4433.2 | 3801.2 | 400.1 | 407.4 | 235.5 | 194.8 | 282.8
4434.2 | 3802.2 | 400.1 | 407.4 | 235.3 | 194.6 | 282.8
4435.2 | 3803.2 | 400.1 | 407.3 | 235 | 194.3 | 282.7
4436.2 | 3804.2 | 400 | 407.3 | 234.9 | 194.1 | 282.6
4437.2 | 3805.2 | 400 | 407.3 | 234.8 | 194 | 282.5
4438.2 | 3806.2 | 400 | 407.3 | 234.6 | 193.9 | 282.4
4439.2 | 3807.2 | 400 | 407.2 | 234.6 | 193.8 | 282.3
4440.2 | 3808.2 | 400 | 407.2 | 235.2 | 193.4 | 282.3
4441.2 | 3809.2 | 399.9 | 407.2 | 235.7 | 193 | 282.1
4442.2 | 3810.2 | 399.9 | 407.2 | 236 | 192.8 | 282
4443.2 | 3811.2 | 399.9 | 407.3 | 236.4 | 192.8 | 281.9
4444.2 | 3812.2 | 399.9 | 407.2 | 237.2 | 192.4 | 281.8
4445.2 | 3813.2 | 399.9 | 407.2 | 237.1 | 192.2 | 281.8
4446.2 | 3814.2 | 399.9 | 407.2 | 237 | 192.1 | 281.7
4447.2 | 3815.2 | 399.8 | 407.2 | 236.7 | 191.7 | 281.6
4448.2 | 3816.2 | 399.8 | 407.2 | 236.3 | 191.6 | 281.5
4449.2 | 3817.2 | 399.8 | 407.2 | 236 | 191.6 | 281.4
4450.2 | 3818.2 | 399.8 | 407.2 | 235.8 | 191.3 | 281.3
4451.2 | 3819.2 | 399.7 | 407.1 | 235.5 | 191.1 | 281.2
4452.2 | 3820.2 | 399.7 | 407.3 | 235.2 | 191 | 281.2
4453.2 | 3821.2 | 399.7 | 407.1 | 234.9 | 190.9 | 281.1
4454.2 | 3822.2 | 399.7 | 407.1 | 234.8 | 190.9 | 281
4455.2 | 3823.2 | 399.7 | 407 | 234.7 | 190.8 | 281
4456.2 | 3824.2 | 399.7 | 407.1 | 234.5 | 190.3 | 280.9
4457.2 | 3825.2 | 399.6 | 407.1 | 234.2 | 190.1 | 280.8
4458.2 | 3826.2 | 399.6 | 407.1 | 234 | 189.9 | 280.7
4459.2 | 3827.2 | 399.6 | 407.1 | 233.9 | 189.6 | 280.6
4460.2 | 3828.2 | 399.6 | 407 | 233.5 | 189.8 | 280.5
4461.2 | 3829.2 | 399.6 | 407 | 233.2 | 189.7 | 280.5
4462.2 | 3830.2 | 399.5 | 407.1 | 233 | 189.6 | 280.5
4463.2 | 3831.2 | 399.5 | 407 | 232.9 | 189.3 | 280.4
4464.2 | 3832.2 | 399.5 | 407 | 232.8 | 189.2 | 280.4
4465.2 | 3833.2 | 399.5 | 407 | 232.6 | 189.1 | 280.3
4466.2 | 3834.2 | 399.5 | 407.1 | 232.4 | 189 | 280.2
4467.2 | 3835.2 | 399.5 | 407.1 | 232.3 | 188.9 | 280.1
4468.2 | 3836.2 | 399.4 | 407 | 232.3 | 188.9 | 280
4469.2 | 3837.2 | 399.4 | 407 | 232.2 | 188.7 | 279.9
4470.2 | 3838.2 | 399.4 | 407 | 232.1 | 188.5 | 279.8
4471.2 | 3839.2 | 399.4 | 406.9 | 232.1 | 188.3 | 279.7
4472.2 | 3840.2 | 399.4 | 406.9 | 232.1 | 188.2 | 279.7
4473.2 | 3841.2 | 399.3 | 406.9 | 232.1 | 187.9 | 279.6
4474.2 | 3842.2 | 399.3 | 406.9 | 232.2 | 187.5 | 279.5
4475.2 | 3843.2 | 399.3 | 407 | 232.6 | 187.4 | 279.4
4476.2 | 3844.2 | 399.3 | 407 | 232.6 | 187.4 | 279.3
4477.2 | 3845.2 | 399.3 | 407 | 232.9 | 187.1 | 279.2
4478.2 | 3846.2 | 399.3 | 406.9 | 232.9 | 187 | 279.1
4479.2 | 3847.2 | 399.2 | 406.9 | 232.7 | 186.9 | 279
4480.2 | 3848.2 | 399.2 | 406.8 | 232.4 | 186.6 | 279
4481.2 | 3849.2 | 399.2 | 406.9 | 232.2 | 186.5 | 278.9
4482.2 | 3850.2 | 399.2 | 406.8 | 231.8 | 186.5 | 278.9
4483.2 | 3851.2 | 399.2 | 406.8 | 231.4 | 186.2 | 278.8
4484.2 | 3852.2 | 399.2 | 406.8 | 231 | 186.1 | 278.7
4485.2 | 3853.2 | 399.2 | 406.9 | 230.7 | 186.1 | 278.6
4486.2 | 3854.2 | 399.1 | 406.9 | 230.4 | 186.1 | 278.6
4487.2 | 3855.2 | 399.1 | 406.8 | 230.2 | 186 | 278.6
4488.2 | 3856.2 | 399.1 | 406.8 | 229.7 | 185.8 | 278.5
4489.2 | 3857.2 | 399 | 406.8 | 229.4 | 185.7 | 278.4
4490.2 | 3858.2 | 399 | 406.7 | 229.2 | 185.5 | 278.3
4491.2 | 3859.2 | 399 | 406.8 | 229 | 185.6 | 278.3
4492.2 | 3860.2 | 399 | 406.7 | 229.5 | 185.4 | 278.2
4493.2 | 3861.2 | 399 | 406.7 | 229.8 | 185.2 | 278.1
4494.2 | 3862.2 | 398.9 | 406.7 | 229.9 | 185 | 278
4495.2 | 3863.2 | 398.9 | 406.7 | 229.9 | 185 | 277.9
4496.2 | 3864.2 | 398.9 | 406.6 | 229.7 | 184.8 | 277.9
4497.2 | 3865.2 | 398.9 | 406.7 | 229.5 | 184.6 | 277.8
4498.2 | 3866.2 | 398.9 | 406.8 | 229.3 | 184.4 | 277.8
4499.2 | 3867.2 | 398.8 | 406.7 | 228.9 | 184 | 277.6
4500.2 | 3868.2 | 398.8 | 406.7 | 228.7 | 183.9 | 277.5
4501.2 | 3869.2 | 398.8 | 406.7 | 228.6 | 183.8 | 277.4
4502.2 | 3870.2 | 398.8 | 406.7 | 228.6 | 183.7 | 277.4
4503.2 | 3871.2 | 398.8 | 406.7 | 228.6 | 183.4 | 277.3
4504.2 | 3872.2 | 398.8 | 406.7 | 228.3 | 183.4 | 277.2
4505.2 | 3873.2 | 398.7 | 406.7 | 227.9 | 183.3 | 277.2
4506.2 | 3874.2 | 398.7 | 406.6 | 227.6 | 183 | 277.1
4507.2 | 3875.2 | 398.7 | 406.6 | 227.3 | 182.8 | 277
4508.2 | 3876.2 | 398.7 | 406.5 | 227 | 182.7 | 276.9
4509.2 | 3877.2 | 398.7 | 406.5 | 226.7 | 182.7 | 276.9
4510.2 | 3878.2 | 398.7 | 406.6 | 226.3 | 182.6 | 276.8
4511.2 | 3879.2 | 398.7 | 406.6 | 225.8 | 182.4 | 276.7
4512.2 | 3880.2 | 398.7 | 406.6 | 225.5 | 182.4 | 276.7
4513.2 | 3881.2 | 398.6 | 406.5 | 225.3 | 182.4 | 276.7
4514.2 | 3882.2 | 398.6 | 406.5 | 225.1 | 182.3 | 276.6
4515.2 | 3883.2 | 398.6 | 406.5 | 224.8 | 182.1 | 276.5
4516.2 | 3884.2 | 398.5 | 406.5 | 224.5 | 181.9 | 276.5
4517.2 | 3885.2 | 398.5 | 406.7 | 224.4 | 181.7 | 276.4
4518.2 | 3886.2 | 398.5 | 406.6 | 224.3 | 181.5 | 276.2
4519.2 | 3887.2 | 398.5 | 406.5 | 224.4 | 181.5 | 276.2
4520.2 | 3888.2 | 398.5 | 406.5 | 224.7 | 181.3 | 276.1
4521.2 | 3889.2 | 398.5 | 406.5 | 224.6 | 181.1 | 276
4522.2 | 3890.2 | 398.4 | 406.4 | 224.4 | 181 | 275.9
4523.2 | 3891.2 | 398.4 | 406.4 | 224.2 | 180.9 | 275.8
4524.2 | 3892.2 | 398.4 | 406.5 | 224 | 180.8 | 275.7
4525.2 | 3893.2 | 398.4 | 406.5 | 223.8 | 180.6 | 275.6
4526.2 | 3894.2 | 398.4 | 406.4 | 223.6 | 180.4 | 275.5
4527.2 | 3895.2 | 398.3 | 406.4 | 223.4 | 180.3 | 275.4
4528.2 | 3896.2 | 398.3 | 406.4 | 223.4 | 180.3 | 275.3
4529.2 | 3897.2 | 398.3 | 406.4 | 223.4 | 180.1 | 275.3
4530.2 | 3898.2 | 398.3 | 406.4 | 223.5 | 179.9 | 275.2
4531.2 | 3899.2 | 398.3 | 406.4 | 223.6 | 179.9 | 275.2
4532.2 | 3900.2 | 398.3 | 406.5 | 224.2 | 179.9 | 275.1
4533.2 | 3901.2 | 398.2 | 406.4 | 224.6 | 179.9 | 275
4534.2 | 3902.2 | 398.2 | 406.4 | 224.4 | 179.8 | 274.9
4535.2 | 3903.2 | 398.2 | 406.4 | 224.2 | 179.6 | 274.8
4536.2 | 3904.2 | 398.2 | 406.3 | 224 | 179.5 | 274.7
4537.2 | 3905.2 | 398.2 | 406.4 | 223.7 | 179.5 | 274.7
4538.2 | 3906.2 | 398.2 | 406.4 | 223.5 | 179.5 | 274.7
4539.2 | 3907.2 | 398.2 | 406.3 | 223.4 | 179.4 | 274.6
4540.2 | 3908.2 | 398.1 | 406.4 | 223.5 | 179.1 | 274.4
4541.2 | 3909.2 | 398.1 | 406.4 | 223.3 | 179 | 274.3
4542.2 | 3910.2 | 398.1 | 406.4 | 223.3 | 179.1 | 274.2
4543.2 | 3911.2 | 398.1 | 406.4 | 223.2 | 178.9 | 274.1
4544.2 | 3912.2 | 398.1 | 406.4 | 223.1 | 178.8 | 274
4545.2 | 3913.2 | 398.1 | 406.4 | 222.9 | 178.7 | 274
4546.2 | 3914.2 | 398 | 406.3 | 222.7 | 178.5 | 273.9
4547.2 | 3915.2 | 398 | 406.3 | 222.6 | 178.4 | 273.9
4548.2 | 3916.2 | 398 | 406.3 | 222.2 | 178.2 | 273.8
4549.2 | 3917.2 | 398 | 406.3 | 222 | 178.1 | 273.7
4550.2 | 3918.2 | 398 | 406.3 | 222.1 | 177.8 | 273.6
4551.2 | 3919.2 | 398 | 406.3 | 221.9 | 177.6 | 273.5
4552.2 | 3920.2 | 398 | 406.3 | 221.6 | 177.7 | 273.5
4553.2 | 3921.2 | 397.9 | 406.2 | 221.6 | 177.8 | 273.5
4554.2 | 3922.2 | 397.9 | 406.2 | 221.9 | 177.5 | 273.5
4555.2 | 3923.2 | 397.9 | 406.2 | 222.1 | 177.3 | 273.4
4556.2 | 3924.2 | 397.9 | 406.2 | 222 | 177 | 273.4
4557.2 | 3925.2 | 397.9 | 406.2 | 221.8 | 176.8 | 273.3
4558.2 | 3926.2 | 397.9 | 406.2 | 221.5 | 176.7 | 273.2
4559.2 | 3927.2 | 397.8 | 406.1 | 221.4 | 176.7 | 273.2
4560.2 | 3928.2 | 397.8 | 406.2 | 221.4 | 176.5 | 273.1
4561.2 | 3929.2 | 397.8 | 406.2 | 221.1 | 176.4 | 273.1
4562.2 | 3930.2 | 397.8 | 406.3 | 220.8 | 176.4 | 273
4563.2 | 3931.2 | 397.8 | 406.2 | 220.5 | 176.4 | 272.9
4564.2 | 3932.2 | 397.8 | 406.2 | 220.2 | 176.3 | 272.8
4565.2 | 3933.2 | 397.8 | 406.1 | 220.1 | 176.1 | 272.7
4566.2 | 3934.2 | 397.7 | 406.1 | 220 | 175.9 | 272.6
4567.2 | 3935.2 | 397.7 | 406.1 | 220 | 175.9 | 272.5
4568.2 | 3936.2 | 397.7 | 406.1 | 220.1 | 175.8 | 272.4
4569.2 | 3937.2 | 397.7 | 406.1 | 220.1 | 175.5 | 272.3
4570.2 | 3938.2 | 397.7 | 406.1 | 219.8 | 175.3 | 272.3
4571.2 | 3939.2 | 397.7 | 406.1 | 219.7 | 175.3 | 272.2
4572.2 | 3940.2 | 397.7 | 406 | 219.6 | 175.1 | 272.1
4573.2 | 3941.2 | 397.7 | 406 | 219.3 | 175 | 272
4574.2 | 3942.2 | 397.6 | 406 | 219 | 174.9 | 272
4575.2 | 3943.2 | 397.6 | 406 | 218.9 | 174.7 | 272
4576.2 | 3944.2 | 397.6 | 406 | 218.6 | 174.7 | 271.9
4577.2 | 3945.2 | 397.5 | 406.1 | 218.2 | 174.6 | 271.9
4578.2 | 3946.2 | 397.6 | 406 | 218 | 174.4 | 271.9
4579.2 | 3947.2 | 397.5 | 406 | 217.9 | 174.3 | 271.8
4580.2 | 3948.2 | 397.5 | 406 | 218 | 174.2 | 271.7
4581.2 | 3949.2 | 397.5 | 406 | 218 | 174.3 | 271.7
4582.2 | 3950.2 | 397.5 | 406 | 218.5 | 174.1 | 271.6
4583.2 | 3951.2 | 397.5 | 406 | 218.4 | 173.9 | 271.6
4584.2 | 3952.2 | 397.4 | 406 | 218.2 | 173.8 | 271.6
4585.2 | 3953.2 | 397.5 | 406 | 217.9 | 173.7 | 271.5
4586.2 | 3954.2 | 397.4 | 405.9 | 217.8 | 173.5 | 271.5
4587.2 | 3955.2 | 397.4 | 406 | 217.5 | 173.4 | 271.5
4588.2 | 3956.2 | 397.4 | 406 | 217.2 | 173.1 | 271.4
4589.2 | 3957.2 | 397.4 | 406.1 | 217 | 172.9 | 271.3
4590.2 | 3958.2 | 397.4 | 406.1 | 216.8 | 172.9 | 271.1
4591.2 | 3959.2 | 397.4 | 406 | 216.8 | 172.8 | 271.1
4592.2 | 3960.2 | 397.3 | 406 | 216.6 | 173 | 271
4593.2 | 3961.2 | 397.3 | 406 | 216.7 | 172.9 | 270.9
4594.2 | 3962.2 | 397.3 | 406 | 216.5 | 172.7 | 270.9
4595.2 | 3963.2 | 397.3 | 406 | 216.3 | 172.7 | 270.7
4596.2 | 3964.2 | 397.3 | 406.1 | 216.2 | 172.6 | 270.7
4597.2 | 3965.2 | 397.2 | 406 | 216.5 | 172.3 | 270.6
4598.2 | 3966.2 | 397.2 | 406 | 216.1 | 172.3 | 270.6
4599.2 | 3967.2 | 397.2 | 406.1 | 215.7 | 172.1 | 270.5
4600.2 | 3968.2 | 397.2 | 406 | 215.3 | 171.8 | 270.4
4601.2 | 3969.2 | 397.2 | 406 | 215 | 171.5 | 270.3
4602.2 | 3970.2 | 397.2 | 406 | 214.8 | 171.3 | 270.2
4603.2 | 3971.2 | 397.2 | 405.9 | 214.6 | 171.2 | 270.1
4604.2 | 3972.2 | 397.2 | 406 | 214.2 | 171 | 270.1
4605.2 | 3973.2 | 397.1 | 406 | 213.7 | 170.9 | 270
4606.2 | 3974.2 | 397.1 | 405.9 | 213.4 | 170.9 | 269.9
4607.2 | 3975.2 | 397.1 | 406 | 213.2 | 170.8 | 269.8
4608.2 | 3976.2 | 397.1 | 406 | 213 | 170.8 | 269.8
4609.2 | 3977.2 | 397.1 | 405.9 | 212.8 | 170.6 | 269.7
4610.2 | 3978.2 | 397 | 405.9 | 212.4 | 170.5 | 269.7
4611.2 | 3979.2 | 397.1 | 405.9 | 212.3 | 170.5 | 269.6
4612.2 | 3980.2 | 397 | 405.9 | 212 | 170.5 | 269.6
4613.2 | 3981.2 | 397 | 406 | 211.7 | 170.3 | 269.6
4614.2 | 3982.2 | 397 | 406 | 211.7 | 170.2 | 269.5
4615.2 | 3983.2 | 397 | 405.9 | 211.6 | 170.1 | 269.4
4616.2 | 3984.2 | 397 | 405.9 | 211.3 | 170 | 269.3
4617.2 | 3985.2 | 397 | 405.9 | 211.2 | 169.8 | 269.2
4618.2 | 3986.2 | 396.9 | 405.9 | 211.1 | 169.7 | 269.1
4619.2 | 3987.2 | 397 | 405.9 | 211.3 | 169.7 | 269.1
4620.2 | 3988.2 | 396.9 | 405.9 | 211.6 | 169.5 | 269
4621.2 | 3989.2 | 396.9 | 405.8 | 211.6 | 169.3 | 268.9
4622.2 | 3990.2 | 396.9 | 405.9 | 211.7 | 169.1 | 268.7
4623.2 | 3991.2 | 396.9 | 405.8 | 211.6 | 169.1 | 268.7
4624.2 | 3992.2 | 396.9 | 405.9 | 211.4 | 169.1 | 268.7
4625.2 | 3993.2 | 396.9 | 405.9 | 211.1 | 168.9 | 268.6
4626.2 | 3994.2 | 396.9 | 405.9 | 210.8 | 168.8 | 268.6
4627.2 | 3995.2 | 396.8 | 405.9 | 210.6 | 168.7 | 268.5
4628.2 | 3996.2 | 396.8 | 406 | 210.9 | 168.5 | 268.5
4629.2 | 3997.2 | 396.8 | 405.9 | 210.9 | 168.3 | 268.4
4630.2 | 3998.2 | 396.8 | 405.9 | 210.8 | 168.2 | 268.3
4631.2 | 3999.2 | 396.8 | 405.9 | 210.7 | 168.2 | 268.2
4632.2 | 4000.2 | 396.7 | 405.9 | 210.5 | 168 | 268.2
4633.2 | 4001.2 | 396.7 | 405.9 | 210.4 | 168.1 | 268.1
4634.2 | 4002.2 | 396.8 | 405.9 | 210.2 | 168 | 268.1
4635.2 | 4003.2 | 396.8 | 405.9 | 210.3 | 167.8 | 268.1
4636.2 | 4004.2 | 396.7 | 405.8 | 210.9 | 167.7 | 268
4637.2 | 4005.2 | 396.7 | 406 | 211 | 167.7 | 268
4638.2 | 4006.2 | 396.7 | 405.9 | 210.9 | 167.6 | 267.9
4639.2 | 4007.2 | 396.7 | 405.8 | 210.7 | 167.4 | 267.9
4640.2 | 4008.2 | 396.7 | 405.8 | 210.7 | 167.4 | 267.8
4641.2 | 4009.2 | 396.6 | 405.9 | 210.6 | 167.4 | 267.7
4642.2 | 4010.2 | 396.6 | 405.9 | 210.7 | 167.2 | 267.6
4643.2 | 4011.2 | 396.6 | 405.8 | 210.5 | 167 | 267.6
4644.2 | 4012.2 | 396.6 | 405.8 | 210.2 | 166.9 | 267.5
4645.2 | 4013.2 | 396.6 | 405.8 | 210 | 166.7 | 267.3
4646.2 | 4014.2 | 396.6 | 405.8 | 209.9 | 166.6 | 267.3
4647.2 | 4015.2 | 396.6 | 405.8 | 209.7 | 166.4 | 267.2
4648.2 | 4016.2 | 396.5 | 405.7 | 209.4 | 166.4 | 267.2
4649.2 | 4017.2 | 396.5 | 405.8 | 209.2 | 166.4 | 267.2
4650.2 | 4018.2 | 396.5 | 405.8 | 208.9 | 166.4 | 267.1
4651.2 | 4019.2 | 396.5 | 405.7 | 208.7 | 166.2 | 267.1
4652.2 | 4020.2 | 396.5 | 405.8 | 208.5 | 166.2 | 267
4653.2 | 4021.2 | 396.5 | 405.8 | 208.2 | 166.1 | 266.9
4654.2 | 4022.2 | 396.5 | 405.8 | 208 | 166.1 | 266.8
4655.2 | 4023.2 | 396.5 | 405.8 | 207.8 | 166.1 | 266.8
4656.2 | 4024.2 | 396.4 | 405.8 | 207.5 | 166.1 | 266.8
4657.2 | 4025.2 | 396.4 | 405.7 | 207.3 | 166 | 266.7
4658.2 | 4026.2 | 396.4 | 405.7 | 207 | 165.9 | 266.7
4659.2 | 4027.2 | 396.4 | 405.8 | 206.9 | 165.8 | 266.6
4660.2 | 4028.2 | 396.4 | 405.8 | 206.6 | 165.7 | 266.5
4661.2 | 4029.2 | 396.3 | 405.7 | 206.5 | 165.8 | 266.4
4662.2 | 4030.2 | 396.4 | 405.7 | 206.5 | 165.7 | 266.3
4663.2 | 4031.2 | 396.3 | 405.8 | 206.6 | 165.6 | 266.2
4664.2 | 4032.2 | 396.3 | 405.8 | 206.4 | 165.4 | 266.1
4665.2 | 4033.2 | 396.3 | 405.8 | 206.1 | 165.4 | 266
4666.2 | 4034.2 | 396.3 | 405.7 | 205.9 | 165.3 | 266
4667.2 | 4035.2 | 396.3 | 405.7 | 205.8 | 165.2 | 265.9
4668.2 | 4036.2 | 396.3 | 405.7 | 205.6 | 165.1 | 265.9
4669.2 | 4037.2 | 396.3 | 405.7 | 205.4 | 164.9 | 265.8
4670.2 | 4038.2 | 396.3 | 405.7 | 205.3 | 164.8 | 265.8
4671.2 | 4039.2 | 396.3 | 405.8 | 205.1 | 164.8 | 265.6
4672.2 | 4040.2 | 396.2 | 405.7 | 205.1 | 164.6 | 265.5
4673.2 | 4041.2 | 396.2 | 405.6 | 204.8 | 164.4 | 265.5
4674.2 | 4042.2 | 396.2 | 405.7 | 204.7 | 164.4 | 265.3
4675.2 | 4043.2 | 396.2 | 405.7 | 204.6 | 164.3 | 265.2
4676.2 | 4044.2 | 396.2 | 405.8 | 204.3 | 164.1 | 265.2
4677.2 | 4045.2 | 396.2 | 405.7 | 204 | 163.9 | 265.1
4678.2 | 4046.2 | 396.2 | 405.6 | 203.8 | 163.9 | 265
4679.2 | 4047.2 | 396.1 | 405.7 | 203.6 | 163.8 | 264.9
4680.2 | 4048.2 | 396.1 | 405.7 | 203.4 | 163.7 | 264.9
4681.2 | 4049.2 | 396.1 | 405.7 | 203.3 | 163.5 | 264.8
4682.2 | 4050.2 | 396.1 | 405.7 | 203.1 | 163.3 | 264.8
4683.2 | 4051.2 | 396.1 | 405.7 | 203 | 163.3 | 264.7
4684.2 | 4052.2 | 396.1 | 405.7 | 202.8 | 163.4 | 264.7
4685.2 | 4053.2 | 396.1 | 405.6 | 202.8 | 163.3 | 264.6
4686.2 | 4054.2 | 396.1 | 405.7 | 202.7 | 163.2 | 264.5
4687.2 | 4055.2 | 396.1 | 405.6 | 202.5 | 163 | 264.5
4688.2 | 4056.2 | 396.1 | 405.6 | 202.4 | 163 | 264.4
4689.2 | 4057.2 | 396.1 | 405.6 | 202.3 | 163 | 264.4
4690.2 | 4058.2 | 396.1 | 405.6 | 202.1 | 162.9 | 264.5
4691.2 | 4059.2 | 396 | 405.6 | 201.9 | 162.7 | 264.4
4692.2 | 4060.2 | 396 | 405.7 | 201.7 | 162.5 | 264.3
4693.2 | 4061.2 | 396 | 405.7 | 201.6 | 162.4 | 264.3
4694.2 | 4062.2 | 396 | 405.7 | 201.5 | 162.5 | 264.2
4695.2 | 4063.2 | 396 | 405.7 | 201.2 | 162.6 | 264.2
4696.2 | 4064.2 | 396 | 405.6 | 200.9 | 162.6 | 264.1
4697.2 | 4065.2 | 396 | 405.7 | 200.7 | 162.6 | 264
4698.2 | 4066.2 | 395.9 | 405.6 | 200.6 | 162.4 | 264
4699.2 | 4067.2 | 395.9 | 405.5 | 200.4 | 162.4 | 263.9
4700.2 | 4068.2 | 395.9 | 405.5 | 200.2 | 162.3 | 263.8
4701.2 | 4069.2 | 395.9 | 405.6 | 200.1 | 162.1 | 263.8
4702.2 | 4070.2 | 395.9 | 405.6 | 200.1 | 162.1 | 263.7
4703.2 | 4071.2 | 395.9 | 405.6 | 200.1 | 162.1 | 263.6
4704.2 | 4072.2 | 395.9 | 405.6 | 200.1 | 162 | 263.6
4705.2 | 4073.2 | 395.9 | 405.6 | 200.2 | 162 | 263.5
4706.2 | 4074.2 | 395.9 | 405.5 | 200 | 162 | 263.5
4707.2 | 4075.2 | 395.9 | 405.5 | 199.9 | 161.9 | 263.5
4708.2 | 4076.2 | 395.9 | 405.5 | 199.7 | 161.7 | 263.4
4709.2 | 4077.2 | 395.9 | 405.5 | 199.8 | 161.6 | 263.4
4710.2 | 4078.2 | 395.8 | 405.5 | 199.8 | 161.6 | 263.4
4711.2 | 4079.2 | 395.8 | 405.6 | 199.7 | 161.5 | 263.3
4712.2 | 4080.2 | 395.8 | 405.5 | 199.6 | 161.3 | 263.2
4713.2 | 4081.2 | 395.8 | 405.5 | 199.5 | 161.2 | 263.1
4714.2 | 4082.2 | 395.8 | 405.5 | 199.3 | 161.1 | 263.1
4715.2 | 4083.2 | 395.8 | 405.5 | 199.2 | 161.1 | 263
4716.2 | 4084.2 | 395.8 | 405.6 | 199.1 | 160.9 | 263
4717.2 | 4085.2 | 395.8 | 405.5 | 199.1 | 160.8 | 262.9
4718.2 | 4086.2 | 395.8 | 405.4 | 199.1 | 160.7 | 262.9
4719.2 | 4087.2 | 395.8 | 405.5 | 199 | 160.7 | 262.8
4720.2 | 4088.2 | 395.8 | 405.5 | 199 | 160.6 | 262.7
4721.2 | 4089.2 | 395.8 | 405.4 | 198.8 | 160.6 | 262.6
4722.2 | 4090.2 | 395.7 | 405.5 | 198.6 | 160.5 | 262.6
4723.2 | 4091.2 | 395.7 | 405.5 | 198.5 | 160.5 | 262.6
4724.2 | 4092.2 | 395.7 | 405.4 | 198.3 | 160.5 | 262.6
4725.2 | 4093.2 | 395.7 | 405.4 | 198.2 | 160.3 | 262.5
4726.2 | 4094.2 | 395.7 | 405.5 | 198.1 | 160.2 | 262.5
4727.2 | 4095.2 | 395.7 | 405.4 | 198 | 160.2 | 262.4
4728.2 | 4096.2 | 395.7 | 405.4 | 197.9 | 160.2 | 262.3
4729.2 | 4097.2 | 395.7 | 405.4 | 197.8 | 160.2 | 262.3
4730.2 | 4098.2 | 395.7 | 405.5 | 197.7 | 160 | 262.2
4731.2 | 4099.2 | 395.7 | 405.4 | 197.6 | 159.9 | 262.1
4732.2 | 4100.2 | 395.7 | 405.4 | 197.5 | 159.8 | 262
4733.2 | 4101.2 | 395.7 | 405.4 | 197.5 | 159.8 | 261.9
4734.2 | 4102.2 | 395.7 | 405.4 | 197.5 | 159.8 | 261.9
4735.2 | 4103.2 | 395.7 | 405.3 | 197.4 | 159.6 | 261.8
4736.2 | 4104.2 | 395.7 | 405.3 | 197.4 | 159.5 | 261.8
4737.2 | 4105.2 | 395.6 | 405.4 | 197.4 | 159.4 | 261.7
4738.2 | 4106.2 | 395.6 | 405.4 | 197.3 | 159.3 | 261.6
4739.2 | 4107.2 | 395.7 | 405.3 | 197.2 | 159.3 | 261.6
4740.2 | 4108.2 | 395.6 | 405.3 | 197.1 | 159.3 | 261.5
4741.2 | 4109.2 | 395.6 | 405.2 | 196.9 | 159.2 | 261.5
4742.2 | 4110.2 | 395.6 | 405.3 | 196.8 | 159.2 | 261.5
4743.2 | 4111.2 | 395.6 | 405.3 | 196.5 | 159.2 | 261.4
4744.2 | 4112.2 | 395.6 | 405.3 | 196.2 | 158.9 | 261.3
4745.2 | 4113.2 | 395.6 | 405.3 | 196.1 | 158.7 | 261.2
4746.2 | 4114.2 | 395.6 | 405.3 | 196 | 158.6 | 261.2
4747.2 | 4115.2 | 395.6 | 405.4 | 195.9 | 158.5 | 261.1
4748.2 | 4116.2 | 395.6 | 405.3 | 195.8 | 158.4 | 261.1
4749.2 | 4117.2 | 395.6 | 405.3 | 195.7 | 158.3 | 261
4750.2 | 4118.2 | 395.6 | 405.3 | 195.6 | 158.3 | 260.9
4751.2 | 4119.2 | 395.6 | 405.3 | 195.6 | 158.4 | 260.9
4752.2 | 4120.2 | 395.6 | 405.3 | 195.5 | 158.2 | 260.8
4753.2 | 4121.2 | 395.6 | 405.3 | 195.5 | 158.1 | 260.8
4754.2 | 4122.2 | 395.6 | 405.3 | 195.4 | 158.1 | 260.7
4755.2 | 4123.2 | 395.6 | 405.3 | 195.5 | 158 | 260.7
4756.2 | 4124.2 | 395.6 | 405.2 | 195.6 | 158 | 260.6
4757.2 | 4125.2 | 395.6 | 405.3 | 195.7 | 157.9 | 260.6
4758.2 | 4126.2 | 395.6 | 405.3 | 195.5 | 157.9 | 260.6
4759.2 | 4127.2 | 395.6 | 405.3 | 195.4 | 157.8 | 260.5
4760.2 | 4128.2 | 395.6 | 405.3 | 195.3 | 157.6 | 260.5
4761.2 | 4129.2 | 395.6 | 405.2 | 195.2 | 157.4 | 260.4
4762.2 | 4130.2 | 395.5 | 405.2 | 195.2 | 157.2 | 260.3
4763.2 | 4131.2 | 395.5 | 405.2 | 195.2 | 157.2 | 260.3
4764.2 | 4132.2 | 395.6 | 405.2 | 195.2 | 157.1 | 260.2
4765.2 | 4133.2 | 395.6 | 405.2 | 195 | 157 | 260.2
4766.2 | 4134.2 | 395.5 | 405.2 | 194.8 | 156.9 | 260.1
4767.2 | 4135.2 | 395.5 | 405.2 | 194.7 | 156.8 | 260
4768.2 | 4136.2 | 395.5 | 405.1 | 194.8 | 156.8 | 260
4769.2 | 4137.2 | 395.5 | 405.2 | 195.3 | 156.6 | 260
4770.2 | 4138.2 | 395.5 | 405.2 | 195.5 | 156.6 | 259.9
4771.2 | 4139.2 | 395.5 | 405.2 | 195.8 | 156.5 | 259.9
4772.2 | 4140.2 | 395.5 | 405.2 | 195.8 | 156.4 | 259.8
4773.2 | 4141.2 | 395.5 | 405.2 | 195.5 | 156.2 | 259.6
4774.2 | 4142.2 | 395.5 | 405.1 | 195.3 | 156 | 259.5
4775.2 | 4143.2 | 395.5 | 405.2 | 195.1 | 156 | 259.4
4776.2 | 4144.2 | 395.5 | 405.2 | 194.9 | 155.9 | 259.4
4777.2 | 4145.2 | 395.5 | 405.1 | 194.7 | 155.8 | 259.4
4778.2 | 4146.2 | 395.5 | 405.1 | 194.5 | 155.7 | 259.2
4779.2 | 4147.2 | 395.4 | 405.1 | 194.3 | 155.6 | 259.2
4780.2 | 4148.2 | 395.4 | 405.2 | 194.2 | 155.6 | 259.1
4781.2 | 4149.2 | 395.4 | 405.1 | 194.1 | 155.6 | 259.1
4782.2 | 4150.2 | 395.4 | 405.1 | 194.1 | 155.6 | 259
4783.2 | 4151.2 | 395.4 | 405.1 | 194 | 155.4 | 259
4784.2 | 4152.2 | 395.4 | 405.1 | 193.9 | 155.3 | 258.9
4785.2 | 4153.2 | 395.4 | 405.1 | 193.9 | 155.2 | 258.9
4786.2 | 4154.2 | 395.4 | 405 | 194.3 | 155.2 | 258.8
4787.2 | 4155.2 | 395.4 | 405 | 194.4 | 155 | 258.8
4788.2 | 4156.2 | 395.4 | 405 | 194.3 | 154.8 | 258.7
4789.2 | 4157.2 | 395.4 | 405 | 194.2 | 154.7 | 258.7
4790.2 | 4158.2 | 395.4 | 405 | 194 | 154.6 | 258.6
4791.2 | 4159.2 | 395.4 | 405 | 193.7 | 154.7 | 258.5
4792.2 | 4160.2 | 395.4 | 405.1 | 193.7 | 154.6 | 258.5
4793.2 | 4161.2 | 395.4 | 405 | 193.5 | 154.5 | 258.5
4794.2 | 4162.2 | 395.4 | 404.9 | 193.5 | 154.3 | 258.4
4795.2 | 4163.2 | 395.3 | 404.9 | 193.3 | 154.2 | 258.3
4796.2 | 4164.2 | 395.4 | 405 | 193.3 | 154.2 | 258.3
4797.2 | 4165.2 | 395.3 | 404.9 | 193.3 | 154.2 | 258.2
4798.2 | 4166.2 | 395.3 | 404.9 | 193 | 154.1 | 258.2
4799.2 | 4167.2 | 395.3 | 404.9 | 192.8 | 153.9 | 258.2
4800.2 | 4168.2 | 395.3 | 405 | 192.5 | 153.9 | 258.1
4801.2 | 4169.2 | 395.3 | 405 | 192.1 | 153.7 | 258
4802.2 | 4170.2 | 395.3 | 404.9 | 191.8 | 153.5 | 257.9
4803.2 | 4171.2 | 395.3 | 404.9 | 191.4 | 153.4 | 257.8
4804.2 | 4172.2 | 395.3 | 404.9 | 191.2 | 153.2 | 257.7
4805.2 | 4173.2 | 395.3 | 404.9 | 191 | 153.2 | 257.6
4806.2 | 4174.2 | 395.3 | 404.9 | 190.8 | 153.3 | 257.6
4807.2 | 4175.2 | 395.3 | 404.9 | 190.6 | 153.3 | 257.5
4808.2 | 4176.2 | 395.3 | 404.8 | 190.3 | 153.3 | 257.5
4809.2 | 4177.2 | 395.2 | 404.9 | 190 | 153 | 257.4
4810.2 | 4178.2 | 395.2 | 404.9 | 189.8 | 152.9 | 257.3
4811.2 | 4179.2 | 395.2 | 404.9 | 189.6 | 153 | 257.2
4812.2 | 4180.2 | 395.2 | 404.8 | 189.5 | 152.9 | 257.2
4813.2 | 4181.2 | 395.2 | 404.9 | 189.3 | 152.8 | 257.1
4814.2 | 4182.2 | 395.2 | 404.8 | 189.4 | 152.9 | 257.1
4815.2 | 4183.2 | 395.2 | 404.9 | 189.5 | 152.8 | 257.1
4816.2 | 4184.2 | 395.2 | 404.9 | 189.3 | 152.6 | 257
4817.2 | 4185.2 | 395.2 | 404.8 | 189.2 | 152.4 | 256.8
4818.2 | 4186.2 | 395.2 | 404.8 | 189.2 | 152.3 | 256.7
4819.2 | 4187.2 | 395.2 | 404.8 | 189.1 | 152.2 | 256.7
4820.2 | 4188.2 | 395.1 | 404.7 | 189 | 152.1 | 256.6
4821.2 | 4189.2 | 395.1 | 404.7 | 188.9 | 151.9 | 256.5
4822.2 | 4190.2 | 395.1 | 404.7 | 189 | 151.7 | 256.4
4823.2 | 4191.2 | 395.1 | 404.7 | 189 | 151.7 | 256.3
4824.2 | 4192.2 | 395.1 | 404.7 | 189 | 151.7 | 256.3
4825.2 | 4193.2 | 395.1 | 404.8 | 188.9 | 151.6 | 256.3
4826.2 | 4194.2 | 395.1 | 404.7 | 188.7 | 151.4 | 256.2
4827.2 | 4195.2 | 395 | 404.7 | 188.5 | 151.3 | 256
4828.2 | 4196.2 | 395 | 404.7 | 188.3 | 151.2 | 255.9
4829.2 | 4197.2 | 395 | 404.7 | 188 | 151.2 | 255.9
4830.2 | 4198.2 | 395 | 404.7 | 188 | 150.9 | 255.8
4831.2 | 4199.2 | 395.1 | 404.7 | 187.9 | 150.7 | 255.8
4832.2 | 4200.2 | 395 | 404.7 | 187.8 | 150.7 | 255.7
4833.2 | 4201.2 | 395 | 404.6 | 187.7 | 150.7 | 255.6
4834.2 | 4202.2 | 395 | 404.6 | 187.6 | 150.7 | 255.6
4835.2 | 4203.2 | 395 | 404.6 | 187.8 | 150.6 | 255.6
4836.2 | 4204.2 | 395 | 404.6 | 187.8 | 150.5 | 255.6
4837.2 | 4205.2 | 395 | 404.6 | 187.7 | 150.5 | 255.5
4838.2 | 4206.2 | 395 | 404.6 | 187.6 | 150.5 | 255.5
4839.2 | 4207.2 | 394.9 | 404.6 | 187.4 | 150.4 | 255.4
4840.2 | 4208.2 | 395 | 404.5 | 187.1 | 150.2 | 255.3
4841.2 | 4209.2 | 395 | 404.6 | 187 | 150.3 | 255.3
4842.2 | 4210.2 | 395 | 404.5 | 186.9 | 150.3 | 255.2
4843.2 | 4211.2 | 395 | 404.5 | 186.7 | 150.3 | 255.2
4844.2 | 4212.2 | 395 | 404.5 | 186.6 | 150.3 | 255.2
4845.2 | 4213.2 | 394.9 | 404.5 | 186.4 | 150.2 | 255.1
4846.2 | 4214.2 | 394.9 | 404.5 | 186.3 | 150.2 | 255.1
4847.2 | 4215.2 | 395 | 404.5 | 186.3 | 150.1 | 255.1
4848.2 | 4216.2 | 395 | 404.5 | 186.5 | 149.9 | 255
4849.2 | 4217.2 | 395 | 404.4 | 186.4 | 149.7 | 255
4850.2 | 4218.2 | 395 | 404.5 | 186.3 | 149.6 | 254.8
4851.2 | 4219.2 | 394.9 | 404.5 | 186.2 | 149.6 | 254.7
4852.2 | 4220.2 | 394.9 | 404.5 | 186.2 | 149.5 | 254.7
4853.2 | 4221.2 | 394.9 | 404.4 | 186.1 | 149.4 | 254.6
4854.2 | 4222.2 | 394.9 | 404.4 | 186 | 149.3 | 254.5
4855.2 | 4223.2 | 394.9 | 404.4 | 185.9 | 149.2 | 254.4
4856.2 | 4224.2 | 394.8 | 404.5 | 185.8 | 149.1 | 254.3
4857.2 | 4225.2 | 394.9 | 404.5 | 185.7 | 149 | 254.2
4858.2 | 4226.2 | 394.9 | 404.4 | 185.5 | 149 | 254.1
4859.2 | 4227.2 | 394.8 | 404.5 | 185.2 | 148.9 | 254.1
4860.2 | 4228.2 | 394.8 | 404.4 | 185.2 | 148.9 | 254
4861.2 | 4229.2 | 394.8 | 404.4 | 185.3 | 148.6 | 253.9
4862.2 | 4230.2 | 394.8 | 404.4 | 185.3 | 148.4 | 253.9
4863.2 | 4231.2 | 394.8 | 404.4 | 185.2 | 148.5 | 253.9
4864.2 | 4232.2 | 394.8 | 404.4 | 185 | 148.5 | 253.9
4865.2 | 4233.2 | 394.8 | 404.3 | 184.7 | 148.5 | 253.9
4866.2 | 4234.2 | 394.8 | 404.3 | 184.4 | 148.4 | 253.8
4867.2 | 4235.2 | 394.7 | 404.4 | 184.3 | 148.4 | 253.8
4868.2 | 4236.2 | 394.7 | 404.5 | 184.2 | 148.4 | 253.7
4869.2 | 4237.2 | 394.8 | 404.4 | 184.3 | 148.2 | 253.6
4870.2 | 4238.2 | 394.8 | 404.4 | 184.2 | 148.1 | 253.5
4871.2 | 4239.2 | 394.7 | 404.4 | 184.3 | 148.1 | 253.4
4872.2 | 4240.2 | 394.7 | 404.4 | 184.2 | 147.9 | 253.4
4873.2 | 4241.2 | 394.7 | 404.4 | 184.2 | 147.9 | 253.3
4874.2 | 4242.2 | 394.7 | 404.3 | 184.3 | 147.8 | 253.3
4875.2 | 4243.2 | 394.7 | 404.3 | 184.2 | 147.7 | 253.2
4876.2 | 4244.2 | 394.7 | 404.3 | 184.2 | 147.8 | 253.2
4877.2 | 4245.2 | 394.7 | 404.4 | 184.1 | 147.8 | 253.1
4878.2 | 4246.2 | 394.7 | 404.4 | 184 | 147.7 | 253.1
4879.2 | 4247.2 | 394.6 | 404.3 | 183.7 | 147.5 | 253
4880.2 | 4248.2 | 394.6 | 404.4 | 183.7 | 147.5 | 252.9
4881.2 | 4249.2 | 394.6 | 404.4 | 183.8 | 147.4 | 252.8
4882.2 | 4250.2 | 394.6 | 404.3 | 183.6 | 147.4 | 252.7
4883.2 | 4251.2 | 394.6 | 404.3 | 183.5 | 147.4 | 252.7
4884.2 | 4252.2 | 394.6 | 404.3 | 183.4 | 147.3 | 252.7
4885.2 | 4253.2 | 394.6 | 404.2 | 183.2 | 147.2 | 252.6
4886.2 | 4254.2 | 394.6 | 404.2 | 182.9 | 147 | 252.6
4887.2 | 4255.2 | 394.6 | 404.3 | 182.7 | 146.8 | 252.5
4888.2 | 4256.2 | 394.5 | 404.3 | 182.6 | 146.8 | 252.4
4889.2 | 4257.2 | 394.5 | 404.3 | 182.4 | 146.8 | 252.3
4890.2 | 4258.2 | 394.6 | 404.2 | 182.3 | 146.6 | 252.2
4891.2 | 4259.2 | 394.5 | 404.2 | 182.3 | 146.6 | 252.2
4892.2 | 4260.2 | 394.5 | 404.2 | 182.2 | 146.5 | 252.1
4893.2 | 4261.2 | 394.5 | 404.2 | 182.2 | 146.5 | 252
4894.2 | 4262.2 | 394.5 | 404.2 | 182 | 146.6 | 251.9
4895.2 | 4263.2 | 394.5 | 404.2 | 181.9 | 146.5 | 251.9
4896.2 | 4264.2 | 394.5 | 404.2 | 181.8 | 146.4 | 251.8
4897.2 | 4265.2 | 394.5 | 404.2 | 181.8 | 146.3 | 251.7
4898.2 | 4266.2 | 394.4 | 404.2 | 181.7 | 146.4 | 251.7
4899.2 | 4267.2 | 394.4 | 404.2 | 181.7 | 146.4 | 251.6
4900.2 | 4268.2 | 394.4 | 404.1 | 181.8 | 146.3 | 251.6
4901.2 | 4269.2 | 394.4 | 404.1 | 181.8 | 146.3 | 251.5
4902.2 | 4270.2 | 394.4 | 404.1 | 181.8 | 146.3 | 251.5
4903.2 | 4271.2 | 394.4 | 404.1 | 181.7 | 146.3 | 251.5
4904.2 | 4272.2 | 394.4 | 404.1 | 181.7 | 146.3 | 251.5
4905.2 | 4273.2 | 394.3 | 404.1 | 181.8 | 146.4 | 251.4
4906.2 | 4274.2 | 394.3 | 404 | 182.2 | 146.4 | 251.3
4907.2 | 4275.2 | 394.3 | 404.1 | 182.5 | 146.5 | 251.3
4908.2 | 4276.2 | 394.3 | 404.1 | 182.5 | 146.5 | 251.3
4909.2 | 4277.2 | 394.3 | 404 | 182.4 | 146.4 | 251.2
4910.2 | 4278.2 | 394.3 | 404 | 182.3 | 146.3 | 251.1
4911.2 | 4279.2 | 394.3 | 404.1 | 182.2 | 146.2 | 251
4912.2 | 4280.2 | 394.3 | 404.1 | 182.2 | 146.2 | 251
4913.2 | 4281.2 | 394.3 | 404.1 | 182.1 | 146.2 | 250.9
4914.2 | 4282.2 | 394.3 | 404 | 182.1 | 146.1 | 250.9
4915.2 | 4283.2 | 394.3 | 404 | 182 | 146 | 250.8
4916.2 | 4284.2 | 394.2 | 404 | 182 | 145.9 | 250.7
4917.2 | 4285.2 | 394.3 | 404 | 181.8 | 145.8 | 250.6
4918.2 | 4286.2 | 394.3 | 404 | 181.6 | 145.8 | 250.5
4919.2 | 4287.2 | 394.3 | 403.9 | 181.4 | 145.8 | 250.4
4920.2 | 4288.2 | 394.2 | 404 | 181.1 | 145.8 | 250.4
4921.2 | 4289.2 | 394.3 | 404 | 180.9 | 145.7 | 250.3
4922.2 | 4290.2 | 394.3 | 403.9 | 180.6 | 145.5 | 250.3
4923.2 | 4291.2 | 394.2 | 403.9 | 180.4 | 145.5 | 250.3
4924.2 | 4292.2 | 394.2 | 403.9 | 180.2 | 145.4 | 250.3
4925.2 | 4293.2 | 394.2 | 403.9 | 180.1 | 145.2 | 250.2
4926.2 | 4294.2 | 394.2 | 403.9 | 180 | 145.2 | 250.1
4927.2 | 4295.2 | 394.2 | 403.9 | 179.9 | 145.1 | 250
4928.2 | 4296.2 | 394.2 | 403.9 | 180.1 | 145 | 249.9
4929.2 | 4297.2 | 394.2 | 403.8 | 179.9 | 144.9 | 249.9
4930.2 | 4298.2 | 394.2 | 403.8 | 179.7 | 144.9 | 249.8
4931.2 | 4299.2 | 394.1 | 403.8 | 179.6 | 144.9 | 249.7
4932.2 | 4300.2 | 394.1 | 403.9 | 179.6 | 144.9 | 249.7
4933.2 | 4301.2 | 394.1 | 403.9 | 179.5 | 144.8 | 249.6
4934.2 | 4302.2 | 394.1 | 403.9 | 179.4 | 144.6 | 249.5
4935.2 | 4303.2 | 394.1 | 403.9 | 179.3 | 144.5 | 249.5
4936.2 | 4304.2 | 394.1 | 403.9 | 179.2 | 144.6 | 249.4
4937.2 | 4305.2 | 394.1 | 403.9 | 179.1 | 144.5 | 249.4
4938.2 | 4306.2 | 394.1 | 403.8 | 179 | 144.5 | 249.3
4939.2 | 4307.2 | 394.1 | 403.8 | 178.8 | 144.5 | 249.3
4940.2 | 4308.2 | 394.1 | 403.9 | 178.6 | 144.3 | 249.2
4941.2 | 4309.2 | 394.1 | 403.8 | 178.4 | 144.3 | 249.1
4942.2 | 4310.2 | 394.1 | 403.8 | 178.3 | 144.3 | 249.1
4943.2 | 4311.2 | 394 | 403.8 | 178.1 | 144.4 | 249.1
4944.2 | 4312.2 | 394 | 403.8 | 178 | 144.5 | 249
4945.2 | 4313.2 | 394 | 403.8 | 177.9 | 144.4 | 248.9
4946.2 | 4314.2 | 394 | 403.8 | 177.8 | 144.3 | 248.9
4947.2 | 4315.2 | 394 | 403.8 | 177.7 | 144.2 | 248.8
4948.2 | 4316.2 | 394 | 403.8 | 177.7 | 144.1 | 248.7
4949.2 | 4317.2 | 394 | 403.8 | 177.7 | 144 | 248.6
4950.2 | 4318.2 | 394 | 403.8 | 177.7 | 143.9 | 248.5
4951.2 | 4319.2 | 394 | 403.8 | 177.6 | 144 | 248.4
4952.2 | 4320.2 | 393.9 | 403.8 | 177.4 | 144 | 248.4
4953.2 | 4321.2 | 394 | 403.8 | 177.3 | 143.9 | 248.3
4954.2 | 4322.2 | 393.9 | 403.8 | 177.1 | 143.7 | 248.2
4955.2 | 4323.2 | 393.9 | 403.8 | 176.9 | 143.4 | 248.1
4956.2 | 4324.2 | 393.9 | 403.8 | 176.8 | 143.3 | 248
4957.2 | 4325.2 | 393.9 | 403.8 | 176.7 | 143.3 | 247.9
4958.2 | 4326.2 | 393.8 | 403.7 | 176.6 | 143.2 | 247.9
4959.2 | 4327.2 | 393.8 | 403.7 | 176.4 | 143 | 247.8
4960.2 | 4328.2 | 393.8 | 403.7 | 176.2 | 142.9 | 247.7
4961.2 | 4329.2 | 393.8 | 403.7 | 176.1 | 142.9 | 247.6
4962.2 | 4330.2 | 393.8 | 403.7 | 176 | 142.8 | 247.5
4963.2 | 4331.2 | 393.8 | 403.7 | 175.9 | 142.6 | 247.4
4964.2 | 4332.2 | 393.8 | 403.7 | 175.9 | 142.5 | 247.4
4965.2 | 4333.2 | 393.8 | 403.7 | 175.9 | 142.4 | 247.3
4966.2 | 4334.2 | 393.8 | 403.7 | 175.8 | 142.3 | 247.2
4967.2 | 4335.2 | 393.8 | 403.7 | 175.7 | 142.2 | 247.2
4968.2 | 4336.2 | 393.8 | 403.7 | 175.5 | 142.1 | 247.2
4969.2 | 4337.2 | 393.7 | 403.7 | 175.4 | 142 | 247.1
4970.2 | 4338.2 | 393.7 | 403.7 | 175.3 | 141.9 | 247
4971.2 | 4339.2 | 393.6 | 403.7 | 175.1 | 141.8 | 246.9
4972.2 | 4340.2 | 393.7 | 403.8 | 175 | 141.6 | 246.8
4973.2 | 4341.2 | 393.7 | 403.8 | 175 | 141.5 | 246.7
4974.2 | 4342.2 | 393.7 | 403.7 | 175.1 | 141.5 | 246.6
4975.2 | 4343.2 | 393.7 | 403.7 | 175.1 | 141.5 | 246.6
4976.2 | 4344.2 | 393.6 | 403.7 | 174.8 | 141.4 | 246.5
4977.2 | 4345.2 | 393.6 | 403.8 | 174.7 | 141.3 | 246.5
4978.2 | 4346.2 | 393.6 | 403.8 | 174.7 | 141.2 | 246.4
4979.2 | 4347.2 | 393.6 | 403.8 | 174.7 | 141.1 | 246.3
4980.2 | 4348.2 | 393.6 | 403.8 | 174.7 | 141.1 | 246.3
4981.2 | 4349.2 | 393.5 | 403.8 | 174.7 | 141.1 | 246.2
4982.2 | 4350.2 | 393.5 | 403.8 | 174.7 | 141 | 246.2
4983.2 | 4351.2 | 393.5 | 403.8 | 174.7 | 140.9 | 246.1
4984.2 | 4352.2 | 393.5 | 403.8 | 174.6 | 140.8 | 246.1
4985.2 | 4353.2 | 393.5 | 403.8 | 174.6 | 140.7 | 246
4986.2 | 4354.2 | 393.5 | 403.8 | 174.5 | 140.7 | 245.9
4987.2 | 4355.2 | 393.4 | 403.8 | 174.7 | 140.8 | 245.9
4988.2 | 4356.2 | 393.5 | 403.8 | 175 | 140.6 | 246
4989.2 | 4357.2 | 393.5 | 403.7 | 175 | 140.3 | 245.8
4990.2 | 4358.2 | 393.4 | 403.8 | 175 | 140.2 | 245.7
4991.2 | 4359.2 | 393.4 | 403.8 | 175.1 | 140 | 245.6
4992.2 | 4360.2 | 393.4 | 403.8 | 175.2 | 139.9 | 245.5
4993.2 | 4361.2 | 393.4 | 403.8 | 175.1 | 139.7 | 245.5
4994.2 | 4362.2 | 393.4 | 403.8 | 175 | 139.5 | 245.4
4995.2 | 4363.2 | 393.4 | 403.8 | 175.1 | 139.5 | 245.3
4996.2 | 4364.2 | 393.3 | 403.8 | 175 | 139.4 | 245.2
4997.2 | 4365.2 | 393.3 | 403.8 | 174.9 | 139.3 | 245.1
4998.2 | 4366.2 | 393.2 | 403.8 | 174.6 | 139.1 | 245
4999.2 | 4367.2 | 393.2 | 403.8 | 174.6 | 138.9 | 244.9
5000.2 | 4368.2 | 393.3 | 403.8 | 175.1 | 138.9 | 244.7
5001.2 | 4369.2 | 393.2 | 403.7 | 175.5 | 138.8 | 244.7
5002.2 | 4370.2 | 393.2 | 403.8 | 175.8 | 138.7 | 244.6
5003.2 | 4371.2 | 393.2 | 403.8 | 175.8 | 138.5 | 244.6
5004.2 | 4372.2 | 393.1 | 403.8 | 175.9 | 138.3 | 244.5
5005.2 | 4373.2 | 393.1 | 403.8 | 175.8 | 138.3 | 244.5
5006.2 | 4374.2 | 393.1 | 403.8 | 175.7 | 138.1 | 244.4
5007.2 | 4375.2 | 393.1 | 403.7 | 175.7 | 137.8 | 244.2
5008.2 | 4376.2 | 393.1 | 403.7 | 175.6 | 137.8 | 244.1
5009.2 | 4377.2 | 393 | 403.7 | 175.3 | 137.7 | 244
5010.2 | 4378.2 | 393 | 403.8 | 175.1 | 137.5 | 243.9
5011.2 | 4379.2 | 393 | 403.8 | 175.1 | 137.4 | 243.7
5012.2 | 4380.2 | 393.1 | 403.8 | 175 | 137.3 | 243.7
5013.2 | 4381.2 | 393 | 403.7 | 175.2 | 137.3 | 243.5
5014.2 | 4382.2 | 393 | 403.7 | 175.5 | 137.1 | 243.4
5015.2 | 4383.2 | 393 | 403.7 | 175.5 | 137 | 243.5
5016.2 | 4384.2 | 392.9 | 403.7 | 175.3 | 136.8 | 243.4
5017.2 | 4385.2 | 392.9 | 403.7 | 175.1 | 136.7 | 243.3
5018.2 | 4386.2 | 392.9 | 403.7 | 174.9 | 136.4 | 243.3
5019.2 | 4387.2 | 392.9 | 403.7 | 174.7 | 136.3 | 243.2
5020.2 | 4388.2 | 392.9 | 403.7 | 174.7 | 136.3 | 243.1
5021.2 | 4389.2 | 392.8 | 403.7 | 174.4 | 136.3 | 243.1
5022.2 | 4390.2 | 392.8 | 403.8 | 174.2 | 136.2 | 243.1
5023.2 | 4391.2 | 392.9 | 403.7 | 174.1 | 136.2 | 243
5024.2 | 4392.2 | 392.8 | 403.7 | 174.1 | 136.2 | 242.9
5025.2 | 4393.2 | 392.8 | 403.7 | 174.5 | 136 | 242.8
5026.2 | 4394.2 | 392.8 | 403.8 | 174.4 | 136 | 242.7
5027.2 | 4395.2 | 392.7 | 403.8 | 174.3 | 135.9 | 242.7
5028.2 | 4396.2 | 392.6 | 403.7 | 173.9 | 135.7 | 242.6
5029.2 | 4397.2 | 392.6 | 403.7 | 173.6 | 135.6 | 242.6
5030.2 | 4398.2 | 392.6 | 403.7 | 173.4 | 135.6 | 242.5
5031.2 | 4399.2 | 392.6 | 403.8 | 173.5 | 135.7 | 242.5
5032.2 | 4400.2 | 392.6 | 403.8 | 173.3 | 135.8 | 242.5
5033.2 | 4401.2 | 392.6 | 403.8 | 173.1 | 135.7 | 242.5
5034.2 | 4402.2 | 392.6 | 403.8 | 172.9 | 135.5 | 242.4
5035.2 | 4403.2 | 392.6 | 403.8 | 172.8 | 135.4 | 242.4
5036.2 | 4404.2 | 392.6 | 403.8 | 172.6 | 135.5 | 242.2
5037.2 | 4405.2 | 392.6 | 403.7 | 172.3 | 135.3 | 242.1
5038.2 | 4406.2 | 392.5 | 403.7 | 172.1 | 135.3 | 242
5039.2 | 4407.2 | 392.5 | 403.8 | 172 | 135.3 | 241.9
5040.2 | 4408.2 | 392.5 | 403.7 | 171.8 | 135.3 | 241.8
5041.2 | 4409.2 | 392.4 | 403.7 | 171.6 | 135.2 | 241.8
5042.2 | 4410.2 | 392.4 | 403.7 | 171.4 | 135.1 | 241.7
5043.2 | 4411.2 | 392.4 | 403.7 | 171.4 | 134.9 | 241.6
5044.2 | 4412.2 | 392.4 | 403.8 | 171.5 | 134.9 | 241.5
5045.2 | 4413.2 | 392.4 | 403.8 | 171.5 | 134.9 | 241.5
5046.2 | 4414.2 | 392.4 | 403.8 | 171.2 | 135 | 241.4
5047.2 | 4415.2 | 392.4 | 403.7 | 171 | 135.1 | 241.4
5048.2 | 4416.2 | 392.4 | 403.7 | 170.7 | 135.2 | 241.4
5049.2 | 4417.2 | 392.3 | 403.7 | 170.3 | 135.3 | 241.4
5050.2 | 4418.2 | 392.3 | 403.7 | 170 | 135.2 | 241.3
5051.2 | 4419.2 | 392.3 | 403.7 | 169.8 | 135.1 | 241.2
5052.2 | 4420.2 | 392.3 | 403.8 | 169.6 | 135 | 241.1
5053.2 | 4421.2 | 392.3 | 403.7 | 169.4 | 135 | 240.9
5054.2 | 4422.2 | 392.3 | 403.7 | 169.9 | 134.9 | 240.8
5055.2 | 4423.2 | 392.3 | 403.7 | 170.1 | 134.8 | 240.7
5056.2 | 4424.2 | 392.2 | 403.7 | 170.2 | 134.8 | 240.6
5057.2 | 4425.2 | 392.2 | 403.7 | 170.5 | 134.7 | 240.6
5058.2 | 4426.2 | 392.2 | 403.7 | 170.8 | 134.7 | 240.5
5059.2 | 4427.2 | 392.2 | 403.7 | 170.8 | 134.7 | 240.5
5060.2 | 4428.2 | 392.1 | 403.7 | 170.7 | 134.7 | 240.5
5061.2 | 4429.2 | 392 | 403.7 | 170.6 | 134.6 | 240.4
5062.2 | 4430.2 | 392 | 403.7 | 170.6 | 134.5 | 240.3
5063.2 | 4431.2 | 392 | 403.7 | 170.6 | 134.6 | 240.3
5064.2 | 4432.2 | 391.9 | 403.7 | 170.4 | 134.6 | 240.2
5065.2 | 4433.2 | 391.9 | 403.7 | 170.2 | 134.7 | 240.2
5066.2 | 4434.2 | 391.9 | 403.7 | 169.9 | 134.5 | 240.1
5067.2 | 4435.2 | 391.9 | 403.7 | 169.6 | 134.2 | 240
5068.2 | 4436.2 | 391.9 | 403.7 | 169.3 | 134 | 240
5069.2 | 4437.2 | 391.9 | 403.7 | 169.1 | 134 | 239.9
5070.2 | 4438.2 | 391.9 | 403.7 | 168.9 | 134.1 | 239.8
5071.2 | 4439.2 | 391.9 | 403.7 | 168.8 | 134.2 | 239.8
5072.2 | 4440.2 | 391.9 | 403.7 | 168.6 | 134 | 239.8
5073.2 | 4441.2 | 391.9 | 403.7 | 168.5 | 133.9 | 239.7
5074.2 | 4442.2 | 391.9 | 403.8 | 168.3 | 133.9 | 239.7
5075.2 | 4443.2 | 391.9 | 403.8 | 168.1 | 133.8 | 239.6
5076.2 | 4444.2 | 391.9 | 403.7 | 168.5 | 133.7 | 239.5
5077.2 | 4445.2 | 391.9 | 403.8 | 168.3 | 133.6 | 239.5
5078.2 | 4446.2 | 391.8 | 403.8 | 168.2 | 133.6 | 239.4
5079.2 | 4447.2 | 391.8 | 403.7 | 168.2 | 133.7 | 239.4
5080.2 | 4448.2 | 391.8 | 403.8 | 168.2 | 133.6 | 239.3
5081.2 | 4449.2 | 391.7 | 403.7 | 168.3 | 133.6 | 239.2
5082.2 | 4450.2 | 391.7 | 403.7 | 168.2 | 133.6 | 239.1
5083.2 | 4451.2 | 391.7 | 403.7 | 168.1 | 133.6 | 239
5084.2 | 4452.2 | 391.7 | 403.7 | 168.1 | 133.6 | 239
5085.2 | 4453.2 | 391.6 | 403.8 | 167.9 | 133.6 | 239
5086.2 | 4454.2 | 391.6 | 403.8 | 167.8 | 133.6 | 238.9
5087.2 | 4455.2 | 391.6 | 403.8 | 167.8 | 133.6 | 238.8
5088.2 | 4456.2 | 391.5 | 403.8 | 167.7 | 133.7 | 238.7
5089.2 | 4457.2 | 391.5 | 403.8 | 167.5 | 133.8 | 238.7
5090.2 | 4458.2 | 391.5 | 403.7 | 167.3 | 133.7 | 238.6
5091.2 | 4459.2 | 391.4 | 403.8 | 167.2 | 133.7 | 238.5
5092.2 | 4460.2 | 391.4 | 403.8 | 167.1 | 133.6 | 238.5
5093.2 | 4461.2 | 391.4 | 403.7 | 167 | 133.5 | 238.5
5094.2 | 4462.2 | 391.4 | 403.7 | 166.7 | 133.5 | 238.5
5095.2 | 4463.2 | 391.3 | 403.7 | 166.6 | 133.5 | 238.4
5096.2 | 4464.2 | 391.3 | 403.7 | 166.6 | 133.5 | 238.3
5097.2 | 4465.2 | 391.4 | 403.7 | 166.5 | 133.5 | 238.2
5098.2 | 4466.2 | 391.3 | 403.7 | 166.5 | 133.6 | 238.1
5099.2 | 4467.2 | 391.3 | 403.7 | 166.4 | 133.5 | 238.1
5100.2 | 4468.2 | 391.3 | 403.7 | 166.2 | 133.6 | 238
5101.2 | 4469.2 | 391.2 | 403.7 | 166 | 133.6 | 237.9
5102.2 | 4470.2 | 391.2 | 403.7 | 165.8 | 133.4 | 237.8
5103.2 | 4471.2 | 391.2 | 403.7 | 166 | 133.4 | 237.7
5104.2 | 4472.2 | 391.2 | 403.7 | 166.2 | 133.3 | 237.6
5105.2 | 4473.2 | 391.1 | 403.7 | 166.1 | 133.3 | 237.5
5106.2 | 4474.2 | 391.1 | 403.7 | 165.9 | 133.2 | 237.4
5107.2 | 4475.2 | 391.1 | 403.7 | 165.5 | 133.2 | 237.4
5108.2 | 4476.2 | 391.1 | 403.7 | 165.2 | 133.1 | 237.3
5109.2 | 4477.2 | 391.1 | 403.7 | 165 | 133.2 | 237.2
5110.2 | 4478.2 | 391.1 | 403.8 | 165 | 133.2 | 237.2
5111.2 | 4479.2 | 391.1 | 403.7 | 164.9 | 133.3 | 237.1
5112.2 | 4480.2 | 391 | 403.7 | 164.7 | 133.3 | 237
5113.2 | 4481.2 | 391 | 403.8 | 164.6 | 133.3 | 236.9
5114.2 | 4482.2 | 390.9 | 403.8 | 164.4 | 133.2 | 236.9
5115.2 | 4483.2 | 391 | 403.8 | 164.2 | 133.1 | 236.8
5116.2 | 4484.2 | 390.9 | 403.8 | 164.1 | 133 | 236.7
5117.2 | 4485.2 | 390.9 | 403.8 | 164 | 133 | 236.7
5118.2 | 4486.2 | 390.9 | 403.8 | 163.8 | 132.9 | 236.6
5119.2 | 4487.2 | 390.9 | 403.8 | 163.8 | 132.9 | 236.5
5120.2 | 4488.2 | 390.9 | 403.8 | 163.8 | 132.9 | 236.4
5121.2 | 4489.2 | 390.8 | 403.8 | 163.8 | 133 | 236.5
5122.2 | 4490.2 | 390.8 | 403.8 | 164 | 132.9 | 236.4
5123.2 | 4491.2 | 390.8 | 403.8 | 164.2 | 132.8 | 236.3
5124.2 | 4492.2 | 390.7 | 403.8 | 164.5 | 132.7 | 236.3
5125.2 | 4493.2 | 390.7 | 403.8 | 164.7 | 132.7 | 236.1
5126.2 | 4494.2 | 390.8 | 403.8 | 164.9 | 132.8 | 236.1
5127.2 | 4495.2 | 390.8 | 403.8 | 164.9 | 132.8 | 236
5128.2 | 4496.2 | 390.7 | 403.8 | 164.8 | 132.6 | 235.9
5129.2 | 4497.2 | 390.8 | 403.8 | 164.8 | 132.5 | 235.8
5130.2 | 4498.2 | 390.7 | 403.8 | 164.8 | 132.4 | 235.7
5131.2 | 4499.2 | 390.7 | 403.8 | 164.8 | 132.3 | 235.7
5132.2 | 4500.2 | 390.6 | 403.8 | 164.8 | 132.1 | 235.7
5133.2 | 4501.2 | 390.6 | 403.8 | 164.8 | 131.9 | 235.6
5134.2 | 4502.2 | 390.6 | 403.8 | 164.9 | 131.6 | 235.5
5135.2 | 4503.2 | 390.6 | 403.7 | 165 | 131.6 | 235.3
5136.2 | 4504.2 | 390.5 | 403.8 | 165.2 | 131.6 | 235.3
5137.2 | 4505.2 | 390.5 | 403.8 | 165.1 | 131.4 | 235.2
5138.2 | 4506.2 | 390.5 | 403.8 | 164.9 | 131.4 | 235.2
5139.2 | 4507.2 | 390.4 | 403.7 | 164.7 | 131.4 | 235.2
5140.2 | 4508.2 | 390.4 | 403.7 | 164.7 | 131.1 | 235.1
5141.2 | 4509.2 | 390.4 | 403.8 | 164.7 | 130.8 | 235
5142.2 | 4510.2 | 390.5 | 403.8 | 164.7 | 130.7 | 234.9
5143.2 | 4511.2 | 390.3 | 403.7 | 164.6 | 130.6 | 234.8
5144.2 | 4512.2 | 390.3 | 403.7 | 164.5 | 130.5 | 234.7
5145.2 | 4513.2 | 390.3 | 403.8 | 164.5 | 130.4 | 234.6
5146.2 | 4514.2 | 390.3 | 403.8 | 164.4 | 130.2 | 234.5
5147.2 | 4515.2 | 390.3 | 403.8 | 164.2 | 129.9 | 234.4
5148.2 | 4516.2 | 390.3 | 403.8 | 164 | 129.7 | 234.3
5149.2 | 4517.2 | 390.2 | 403.8 | 164 | 129.6 | 234.3
5150.2 | 4518.2 | 390.2 | 403.8 | 164 | 129.5 | 234.2
5151.2 | 4519.2 | 390.1 | 403.8 | 163.8 | 129.4 | 234.1
5152.2 | 4520.2 | 390.2 | 403.8 | 163.7 | 129.2 | 234
5153.2 | 4521.2 | 390.2 | 403.8 | 163.6 | 129.2 | 233.9
5154.2 | 4522.2 | 390.1 | 403.8 | 163.5 | 129.2 | 233.8
5155.2 | 4523.2 | 390 | 403.8 | 163.4 | 129.1 | 233.7
5156.2 | 4524.2 | 390 | 403.8 | 163.4 | 129 | 233.6
5157.2 | 4525.2 | 390 | 403.8 | 163.4 | 129 | 233.5
5158.2 | 4526.2 | 390 | 403.9 | 163.3 | 128.9 | 233.4
5159.2 | 4527.2 | 390 | 403.8 | 163.3 | 128.7 | 233.4
5160.2 | 4528.2 | 390.1 | 403.8 | 163.2 | 128.7 | 233.3
5161.2 | 4529.2 | 390 | 403.8 | 163.4 | 128.8 | 233.2
5162.2 | 4530.2 | 390 | 403.8 | 163.4 | 128.8 | 233.1
5163.2 | 4531.2 | 390 | 403.8 | 163.5 | 128.7 | 233
5164.2 | 4532.2 | 389.9 | 403.8 | 163.8 | 128.7 | 233
5165.2 | 4533.2 | 389.9 | 403.8 | 163.7 | 128.6 | 233
5166.2 | 4534.2 | 389.9 | 403.8 | 163.5 | 128.4 | 232.9
5167.2 | 4535.2 | 389.9 | 403.8 | 163.3 | 128.5 | 232.8
5168.2 | 4536.2 | 389.8 | 403.8 | 163.1 | 128.4 | 232.7
5169.2 | 4537.2 | 389.8 | 403.8 | 163 | 128.3 | 232.6
5170.2 | 4538.2 | 389.8 | 403.8 | 162.8 | 128.2 | 232.6
5171.2 | 4539.2 | 389.8 | 403.8 | 162.6 | 128.2 | 232.5
5172.2 | 4540.2 | 389.8 | 403.8 | 162.5 | 128.2 | 232.5
5173.2 | 4541.2 | 389.8 | 403.8 | 162.3 | 128.1 | 232.4
5174.2 | 4542.2 | 389.7 | 403.7 | 162.1 | 128.1 | 232.3
5175.2 | 4543.2 | 389.7 | 403.8 | 161.9 | 128.1 | 232.2
5176.2 | 4544.2 | 389.7 | 403.8 | 161.9 | 128.2 | 232.1
5177.2 | 4545.2 | 389.7 | 403.8 | 161.8 | 128.3 | 232
5178.2 | 4546.2 | 389.6 | 403.7 | 161.7 | 128.4 | 232
5179.2 | 4547.2 | 389.6 | 403.7 | 161.5 | 128.3 | 232
5180.2 | 4548.2 | 389.6 | 403.8 | 161.2 | 128.1 | 231.9
5181.2 | 4549.2 | 389.6 | 403.7 | 160.9 | 128 | 231.8
5182.2 | 4550.2 | 389.6 | 403.7 | 160.7 | 127.9 | 231.7
5183.2 | 4551.2 | 389.6 | 403.7 | 160.5 | 127.8 | 231.7
5184.2 | 4552.2 | 389.6 | 403.7 | 160.4 | 127.9 | 231.6
5185.2 | 4553.2 | 389.5 | 403.7 | 160.4 | 127.9 | 231.6
5186.2 | 4554.2 | 389.5 | 403.6 | 160.5 | 127.9 | 231.5
5187.2 | 4555.2 | 389.5 | 403.6 | 160.4 | 128 | 231.5
5188.2 | 4556.2 | 389.5 | 403.6 | 160.4 | 128.1 | 231.5
5189.2 | 4557.2 | 389.5 | 403.5 | 160.5 | 128.2 | 231.5
5190.2 | 4558.2 | 389.5 | 403.5 | 160.6 | 128.5 | 231.4
5191.2 | 4559.2 | 389.5 | 403.5 | 160.5 | 128.7 | 231.4
5192.2 | 4560.2 | 389.5 | 403.5 | 160.6 | 128.6 | 231.4
5193.2 | 4561.2 | 389.5 | 403.5 | 160.7 | 128.6 | 231.3
5194.2 | 4562.2 | 389.5 | 403.4 | 160.6 | 128.4 | 231.2
5195.2 | 4563.2 | 389.5 | 403.4 | 160.7 | 128.4 | 231.2
5196.2 | 4564.2 | 389.4 | 403.4 | 160.7 | 128.5 | 231.1
5197.2 | 4565.2 | 389.4 | 403.3 | 160.5 | 128.3 | 231
5198.2 | 4566.2 | 389.4 | 403.3 | 160.8 | 128.2 | 230.9
5199.2 | 4567.2 | 389.4 | 403.3 | 161 | 128.1 | 230.8
5200.2 | 4568.2 | 389.4 | 403.2 | 161.1 | 128.1 | 230.7
5201.2 | 4569.2 | 389.3 | 403.2 | 161.4 | 127.9 | 230.7
5202.2 | 4570.2 | 389.4 | 403.2 | 161.9 | 127.7 | 230.6
5203.2 | 4571.2 | 389.3 | 403.2 | 161.9 | 127.6 | 230.5
5204.2 | 4572.2 | 389.3 | 403.1 | 162.1 | 127.7 | 230.4
5205.2 | 4573.2 | 389.3 | 403.1 | 162.1 | 127.6 | 230.4
5206.2 | 4574.2 | 389.3 | 403 | 162.1 | 127.4 | 230.3
5207.2 | 4575.2 | 389.2 | 403 | 162.1 | 127.3 | 230.2
5208.2 | 4576.2 | 389.2 | 403 | 161.9 | 127.2 | 230.1
5209.2 | 4577.2 | 389.2 | 402.9 | 161.6 | 127 | 230
5210.2 | 4578.2 | 389.2 | 402.9 | 161.2 | 126.7 | 230
5211.2 | 4579.2 | 389.2 | 402.9 | 161.1 | 126.6 | 229.8
5212.2 | 4580.2 | 389.2 | 402.9 | 161 | 126.7 | 229.7
5213.2 | 4581.2 | 389.2 | 402.9 | 161.1 | 126.7 | 229.7
5214.2 | 4582.2 | 389.2 | 402.8 | 161.4 | 126.6 | 229.6
5215.2 | 4583.2 | 389.2 | 402.9 | 161.5 | 126.5 | 229.5
5216.2 | 4584.2 | 389.2 | 402.8 | 161.5 | 126.4 | 229.4
5217.2 | 4585.2 | 389.2 | 402.8 | 161.5 | 126.2 | 229.3
5218.2 | 4586.2 | 389.2 | 402.8 | 161.6 | 126.1 | 229.2
5219.2 | 4587.2 | 389.2 | 402.9 | 162.1 | 126.1 | 229.1
5220.2 | 4588.2 | 389.2 | 402.9 | 162 | 126 | 229
5221.2 | 4589.2 | 389.2 | 402.9 | 161.8 | 125.9 | 228.9
5222.2 | 4590.2 | 389.1 | 402.8 | 161.7 | 125.8 | 228.8
5223.2 | 4591.2 | 389.1 | 402.7 | 161.5 | 125.8 | 228.8
5224.2 | 4592.2 | 389.1 | 402.7 | 161.4 | 125.8 | 228.7
5225.2 | 4593.2 | 389.1 | 402.7 | 161.2 | 125.7 | 228.7
5226.2 | 4594.2 | 389.1 | 402.8 | 161.5 | 125.6 | 228.6
5227.2 | 4595.2 | 389.1 | 402.8 | 161.4 | 125.7 | 228.5
5228.2 | 4596.2 | 389 | 402.8 | 161.3 | 125.8 | 228.5
5229.2 | 4597.2 | 389 | 402.8 | 161 | 125.7 | 228.5
5230.2 | 4598.2 | 389.1 | 402.9 | 160.8 | 125.7 | 228.4
5231.2 | 4599.2 | 389 | 402.8 | 160.9 | 125.6 | 228.4
5232.2 | 4600.2 | 389 | 402.8 | 160.8 | 125.5 | 228.3
5233.2 | 4601.2 | 389 | 402.8 | 160.7 | 125.5 | 228.2
5234.2 | 4602.2 | 389 | 402.8 | 160.6 | 125.7 | 228.2
5235.2 | 4603.2 | 389 | 402.7 | 160.4 | 125.8 | 228.1
5236.2 | 4604.2 | 388.9 | 402.7 | 159.9 | 125.6 | 228.1
5237.2 | 4605.2 | 389 | 402.8 | 159.6 | 125.4 | 228
5238.2 | 4606.2 | 389 | 402.8 | 159.3 | 125.3 | 227.9
5239.2 | 4607.2 | 388.9 | 402.8 | 159.1 | 125.3 | 227.9
5240.2 | 4608.2 | 388.9 | 402.8 | 159 | 125.4 | 227.8
5241.2 | 4609.2 | 388.9 | 402.7 | 159 | 125.3 | 227.7
5242.2 | 4610.2 | 388.9 | 402.7 | 159 | 125.1 | 227.6
5243.2 | 4611.2 | 388.9 | 402.7 | 158.9 | 125.1 | 227.6
5244.2 | 4612.2 | 388.9 | 402.7 | 158.7 | 125 | 227.5
5245.2 | 4613.2 | 388.9 | 402.7 | 158.3 | 124.8 | 227.5
5246.2 | 4614.2 | 388.9 | 402.7 | 158.1 | 124.6 | 227.5
5247.2 | 4615.2 | 388.9 | 402.7 | 158.1 | 124.4 | 227.4
5248.2 | 4616.2 | 388.9 | 402.7 | 158 | 124.4 | 227.3
5249.2 | 4617.2 | 388.9 | 402.7 | 158 | 124.3 | 227.2
5250.2 | 4618.2 | 388.9 | 402.7 | 158.2 | 124.3 | 227.1
5251.2 | 4619.2 | 388.9 | 402.7 | 158.4 | 124.2 | 227
5252.2 | 4620.2 | 388.8 | 402.6 | 158.5 | 124.2 | 226.9
5253.2 | 4621.2 | 388.8 | 402.6 | 158.5 | 124.2 | 226.8
5254.2 | 4622.2 | 388.8 | 402.6 | 158.3 | 124.2 | 226.8
5255.2 | 4623.2 | 388.8 | 402.6 | 158.3 | 124.3 | 226.8
5256.2 | 4624.2 | 388.8 | 402.5 | 158.1 | 124.3 | 226.7
5257.2 | 4625.2 | 388.8 | 402.5 | 157.8 | 124.2 | 226.6
5258.2 | 4626.2 | 388.8 | 402.5 | 157.6 | 124.3 | 226.6
5259.2 | 4627.2 | 388.8 | 402.6 | 157.4 | 124.4 | 226.6
5260.2 | 4628.2 | 388.8 | 402.5 | 157.3 | 124.4 | 226.7
5261.2 | 4629.2 | 388.8 | 402.5 | 157.2 | 124.4 | 226.6
5262.2 | 4630.2 | 388.8 | 402.5 | 157 | 124.4 | 226.5
5263.2 | 4631.2 | 388.8 | 402.5 | 156.9 | 124.6 | 226.5
5264.2 | 4632.2 | 388.8 | 402.5 | 156.8 | 124.7 | 226.5
5265.2 | 4633.2 | 388.8 | 402.5 | 156.5 | 124.7 | 226.4
5266.2 | 4634.2 | 388.8 | 402.4 | 156.2 | 124.7 | 226.4
5267.2 | 4635.2 | 388.8 | 402.4 | 156 | 124.6 | 226.3
5268.2 | 4636.2 | 388.8 | 402.4 | 156.1 | 124.4 | 226.2
5269.2 | 4637.2 | 388.8 | 402.4 | 156.2 | 124.3 | 226.1
5270.2 | 4638.2 | 388.8 | 402.4 | 156.7 | 124.3 | 226
5271.2 | 4639.2 | 388.8 | 402.4 | 156.9 | 124.3 | 225.8
5272.2 | 4640.2 | 388.8 | 402.3 | 156.9 | 124.4 | 225.8
5273.2 | 4641.2 | 388.8 | 402.3 | 156.9 | 124.5 | 225.7
5274.2 | 4642.2 | 388.8 | 402.3 | 157 | 124.4 | 225.6
5275.2 | 4643.2 | 388.8 | 402.3 | 156.8 | 124.4 | 225.6
5276.2 | 4644.2 | 388.8 | 402.3 | 156.7 | 124.3 | 225.6
5277.2 | 4645.2 | 388.8 | 402.3 | 156.6 | 124.2 | 225.5
5278.2 | 4646.2 | 388.8 | 402.3 | 156.5 | 124.2 | 225.5
5279.2 | 4647.2 | 388.8 | 402.3 | 156.2 | 124.3 | 225.5
5280.2 | 4648.2 | 388.8 | 402.3 | 155.9 | 124.4 | 225.5
5281.2 | 4649.2 | 388.8 | 402.4 | 155.7 | 124.3 | 225.4
5282.2 | 4650.2 | 388.8 | 402.4 | 155.5 | 124.2 | 225.3
5283.2 | 4651.2 | 388.8 | 402.4 | 155.5 | 124.2 | 225.2
5284.2 | 4652.2 | 388.8 | 402.3 | 155.7 | 124.3 | 225.1
5285.2 | 4653.2 | 388.8 | 402.3 | 156.9 | 124.2 | 225.1
5286.2 | 4654.2 | 388.8 | 402.4 | 158 | 123.9 | 225
5287.2 | 4655.2 | 388.8 | 402.4 | 158.5 | 123.8 | 224.9
5288.2 | 4656.2 | 388.9 | 402.3 | 158.6 | 123.8 | 224.8
5289.2 | 4657.2 | 388.8 | 402.3 | 158.6 | 123.9 | 224.8
5290.2 | 4658.2 | 388.8 | 402.2 | 158.3 | 123.9 | 224.8
5291.2 | 4659.2 | 388.8 | 402.2 | 157.9 | 123.9 | 224.7
5292.2 | 4660.2 | 388.9 | 402.2 | 157.6 | 123.8 | 224.7
5293.2 | 4661.2 | 388.9 | 402.2 | 157.4 | 123.9 | 224.6
5294.2 | 4662.2 | 388.8 | 402.1 | 157.4 | 123.8 | 224.5
5295.2 | 4663.2 | 388.8 | 402.1 | 157.2 | 123.8 | 224.5
5296.2 | 4664.2 | 388.8 | 402.1 | 156.9 | 123.7 | 224.4
5297.2 | 4665.2 | 388.9 | 402.2 | 156.5 | 123.4 | 224.3
5298.2 | 4666.2 | 388.9 | 402.2 | 156.3 | 123.4 | 224.2
5299.2 | 4667.2 | 388.8 | 402.2 | 156.1 | 123.5 | 224.1
5300.2 | 4668.2 | 388.8 | 402.2 | 156 | 123.5 | 224.1
5301.2 | 4669.2 | 388.8 | 402.2 | 155.8 | 123.3 | 224.1
5302.2 | 4670.2 | 388.8 | 402.1 | 155.9 | 123.3 | 224.1
5303.2 | 4671.2 | 388.8 | 402.1 | 156.5 | 123.3 | 224.1
5304.2 | 4672.2 | 388.8 | 402.1 | 156.5 | 123.1 | 224
5305.2 | 4673.2 | 388.8 | 402 | 156.5 | 123 | 223.9
5306.2 | 4674.2 | 388.8 | 402 | 156.6 | 122.8 | 223.7
5307.2 | 4675.2 | 388.8 | 402 | 156.6 | 122.8 | 223.7
5308.2 | 4676.2 | 388.8 | 402 | 156.6 | 122.7 | 223.7
5309.2 | 4677.2 | 388.8 | 402 | 156.4 | 122.7 | 223.6
5310.2 | 4678.2 | 388.8 | 402 | 156.2 | 122.6 | 223.5
5311.2 | 4679.2 | 388.8 | 402 | 156.1 | 122.6 | 223.4
5312.2 | 4680.2 | 388.8 | 402 | 155.9 | 122.6 | 223.3
5313.2 | 4681.2 | 388.8 | 402.1 | 155.6 | 122.6 | 223.2
5314.2 | 4682.2 | 388.8 | 402.1 | 155.4 | 122.5 | 223.1
5315.2 | 4683.2 | 388.7 | 402.1 | 154.9 | 122.5 | 222.9
5316.2 | 4684.2 | 388.8 | 402 | 154.6 | 122.3 | 222.9
5317.2 | 4685.2 | 388.8 | 402 | 154.4 | 122.2 | 223
5318.2 | 4686.2 | 388.8 | 402 | 154.2 | 122.2 | 222.9
5319.2 | 4687.2 | 388.8 | 402 | 154 | 122.3 | 222.9
5320.2 | 4688.2 | 388.8 | 402 | 153.8 | 122.2 | 222.8
5321.2 | 4689.2 | 388.7 | 402 | 153.6 | 122.3 | 222.7
5322.2 | 4690.2 | 388.7 | 402.1 | 153.5 | 122.3 | 222.6
5323.2 | 4691.2 | 388.7 | 402 | 153.4 | 122.3 | 222.6
5324.2 | 4692.2 | 388.7 | 402 | 153.2 | 122.2 | 222.5
5325.2 | 4693.2 | 388.7 | 402 | 153.1 | 122.3 | 222.5
5326.2 | 4694.2 | 388.7 | 401.9 | 153 | 122.3 | 222.4
5327.2 | 4695.2 | 388.7 | 401.9 | 153 | 122.3 | 222.3
5328.2 | 4696.2 | 388.7 | 401.9 | 153 | 122.3 | 222.2
5329.2 | 4697.2 | 388.7 | 402 | 153 | 122.3 | 222.1
5330.2 | 4698.2 | 388.6 | 402 | 152.9 | 122.4 | 222
5331.2 | 4699.2 | 388.7 | 401.9 | 152.9 | 122.6 | 222
5332.2 | 4700.2 | 388.7 | 401.9 | 152.8 | 122.6 | 222
5333.2 | 4701.2 | 388.7 | 401.9 | 152.5 | 122.6 | 222
5334.2 | 4702.2 | 388.7 | 401.9 | 152.2 | 122.6 | 221.9
5335.2 | 4703.2 | 388.7 | 401.8 | 152 | 122.6 | 221.9
5336.2 | 4704.2 | 388.6 | 401.9 | 152 | 122.6 | 221.7
5337.2 | 4705.2 | 388.7 | 401.9 | 151.8 | 122.5 | 221.7
5338.2 | 4706.2 | 388.8 | 401.9 | 151.8 | 122.4 | 221.7
5339.2 | 4707.2 | 388.7 | 402 | 151.8 | 122.4 | 221.6
5340.2 | 4708.2 | 388.7 | 402 | 152.1 | 122.3 | 221.4
5341.2 | 4709.2 | 388.7 | 401.9 | 152.1 | 122.2 | 221.3
5342.2 | 4710.2 | 388.7 | 401.9 | 152.1 | 122.2 | 221.2
5343.2 | 4711.2 | 388.7 | 401.9 | 152 | 122.3 | 221.1
5344.2 | 4712.2 | 388.7 | 401.9 | 152.1 | 122.4 | 221
5345.2 | 4713.2 | 388.7 | 401.9 | 152 | 122.4 | 221
5346.2 | 4714.2 | 388.7 | 401.8 | 152 | 122.4 | 221
5347.2 | 4715.2 | 388.7 | 401.8 | 151.9 | 122.3 | 220.9
5348.2 | 4716.2 | 388.7 | 401.8 | 151.8 | 122.1 | 220.8
5349.2 | 4717.2 | 388.7 | 401.8 | 151.7 | 122.1 | 220.8
5350.2 | 4718.2 | 388.6 | 401.8 | 152.2 | 122 | 220.7
5351.2 | 4719.2 | 388.6 | 401.8 | 152.6 | 122 | 220.6
5352.2 | 4720.2 | 388.7 | 401.8 | 152.8 | 121.9 | 220.6
5353.2 | 4721.2 | 388.7 | 401.8 | 152.9 | 121.8 | 220.6
5354.2 | 4722.2 | 388.7 | 401.7 | 153 | 121.8 | 220.5
5355.2 | 4723.2 | 388.7 | 401.7 | 153.1 | 121.8 | 220.5
5356.2 | 4724.2 | 388.7 | 401.7 | 153.2 | 121.8 | 220.4
5357.2 | 4725.2 | 388.7 | 401.7 | 153.4 | 121.7 | 220.4
5358.2 | 4726.2 | 388.6 | 401.7 | 153.5 | 121.6 | 220.3
5359.2 | 4727.2 | 388.6 | 401.7 | 153.4 | 121.4 | 220.2
5360.2 | 4728.2 | 388.6 | 401.7 | 153.2 | 121.1 | 220.1
5361.2 | 4729.2 | 388.7 | 401.6 | 153 | 120.9 | 220.2
5362.2 | 4730.2 | 388.7 | 401.6 | 152.7 | 120.7 | 220.2
5363.2 | 4731.2 | 388.7 | 401.6 | 152.4 | 120.7 | 220.1
5364.2 | 4732.2 | 388.7 | 401.6 | 152.2 | 120.7 | 220.1
5365.2 | 4733.2 | 388.6 | 401.7 | 152 | 120.8 | 220
5366.2 | 4734.2 | 388.7 | 401.7 | 151.7 | 120.7 | 220
5367.2 | 4735.2 | 388.7 | 401.6 | 151.4 | 120.5 | 220
5368.2 | 4736.2 | 388.7 | 401.6 | 151.3 | 120.5 | 219.9
5369.2 | 4737.2 | 388.7 | 401.7 | 151.1 | 120.5 | 219.8
5370.2 | 4738.2 | 388.6 | 401.7 | 150.8 | 120.5 | 219.6
5371.2 | 4739.2 | 388.7 | 401.8 | 150.6 | 120.4 | 219.5
5372.2 | 4740.2 | 388.7 | 401.8 | 150.5 | 120.4 | 219.4
5373.2 | 4741.2 | 388.6 | 401.8 | 150.5 | 120.4 | 219.3
5374.2 | 4742.2 | 388.6 | 401.7 | 150.5 | 120.3 | 219.3
5375.2 | 4743.2 | 388.6 | 401.7 | 150.5 | 120.3 | 219.3
5376.2 | 4744.2 | 388.7 | 401.6 | 151.1 | 120.2 | 219.2
5377.2 | 4745.2 | 388.7 | 401.7 | 151.5 | 120.1 | 219.1
5378.2 | 4746.2 | 388.7 | 401.6 | 151.7 | 119.9 | 219.1
5379.2 | 4747.2 | 388.7 | 401.6 | 151.6 | 119.9 | 219
5380.2 | 4748.2 | 388.6 | 401.7 | 151.5 | 119.7 | 218.9
5381.2 | 4749.2 | 388.6 | 401.7 | 151.2 | 119.5 | 218.8
5382.2 | 4750.2 | 388.7 | 401.6 | 150.9 | 119.4 | 218.7
5383.2 | 4751.2 | 388.7 | 401.6 | 150.8 | 119.3 | 218.6
5384.2 | 4752.2 | 388.7 | 401.6 | 150.6 | 119.2 | 218.5
5385.2 | 4753.2 | 388.7 | 401.6 | 150.3 | 119.1 | 218.4
5386.2 | 4754.2 | 388.6 | 401.6 | 150 | 119 | 218.3
5387.2 | 4755.2 | 388.6 | 401.6 | 150.3 | 118.7 | 218.1
5388.2 | 4756.2 | 388.6 | 401.7 | 150.3 | 118.5 | 218
5389.2 | 4757.2 | 388.7 | 401.7 | 151.1 | 118.3 | 217.8
5390.2 | 4758.2 | 388.7 | 401.6 | 151.9 | 118.3 | 217.8
5391.2 | 4759.2 | 388.7 | 401.5 | 152.7 | 118.3 | 217.8
5392.2 | 4760.2 | 388.7 | 401.5 | 153.1 | 118.3 | 217.8
5393.2 | 4761.2 | 388.6 | 401.5 | 153.7 | 118.3 | 217.7
5394.2 | 4762.2 | 388.3 | 401.8 | 154.6 | 118.3 | 217.2
5395.2 | 4763.2 | 388.3 | 401.8 | 155.5 | 118.3 | 217.1
5396.2 | 4764.2 | 388.3 | 401.8 | 155.9 | 118.2 | 217
5397.2 | 4765.2 | 388.3 | 401.8 | 155.5 | 118.1 | 217
5398.2 | 4766.2 | 388.3 | 401.8 | 155.2 | 118.1 | 216.9
5399.2 | 4767.2 | 388.3 | 401.8 | 155 | 118.1 | 216.9
5400.2 | 4768.2 | 388.3 | 401.8 | 154.9 | 118.2 | 216.8
5401.2 | 4769.2 | 388.2 | 401.7 | 154.7 | 118.4 | 216.8
5402.2 | 4770.2 | 388.2 | 401.7 | 154.3 | 118.6 | 216.7
5403.2 | 4771.2 | 388.2 | 401.7 | 153.9 | 118.8 | 216.7
5404.2 | 4772.2 | 388.2 | 401.8 | 153.5 | 118.8 | 216.7
5405.2 | 4773.2 | 388.2 | 401.8 | 153.3 | 118.6 | 216.6
5406.2 | 4774.2 | 388.2 | 401.8 | 153 | 118.4 | 216.5
5407.2 | 4775.2 | 388.2 | 401.8 | 152.8 | 118.4 | 216.4
5408.2 | 4776.2 | 388.2 | 401.7 | 152.5 | 118.3 | 216.4
5409.2 | 4777.2 | 388.2 | 401.7 | 152.3 | 118.3 | 216.3
5410.2 | 4778.2 | 388.2 | 401.7 | 151.9 | 118.4 | 216.3
5411.2 | 4779.2 | 388.2 | 401.7 | 151.6 | 118.4 | 216.2
5412.2 | 4780.2 | 388.2 | 401.7 | 151.4 | 118.3 | 216.2
5413.2 | 4781.2 | 388.2 | 401.7 | 151 | 118.3 | 216.2
5414.2 | 4782.2 | 388.2 | 401.8 | 150.7 | 118.3 | 216.1
5415.2 | 4783.2 | 388.2 | 401.7 | 150.4 | 118.4 | 216
5416.2 | 4784.2 | 388.2 | 401.8 | 150.1 | 118.5 | 215.9
5417.2 | 4785.2 | 388.2 | 401.8 | 149.8 | 118.6 | 215.8
5418.2 | 4786.2 | 388.2 | 401.8 | 149.6 | 118.5 | 215.7
5419.2 | 4787.2 | 388.2 | 401.9 | 149.3 | 118.5 | 215.6
5420.2 | 4788.2 | 388.2 | 401.9 | 149.3 | 118.5 | 215.6
5421.2 | 4789.2 | 388.2 | 401.8 | 149.1 | 118.5 | 215.6
5422.2 | 4790.2 | 388.2 | 401.8 | 149 | 118.6 | 215.4
5423.2 | 4791.2 | 388.1 | 401.8 | 149.1 | 118.7 | 215.3
5424.2 | 4792.2 | 388.1 | 401.8 | 148.9 | 118.7 | 215.3
5425.2 | 4793.2 | 388.2 | 401.8 | 148.7 | 118.5 | 215.2
5426.2 | 4794.2 | 388.2 | 401.8 | 148.6 | 118.4 | 215.2
5427.2 | 4795.2 | 388.2 | 401.8 | 148.4 | 118.4 | 215.1
5428.2 | 4796.2 | 388.2 | 401.8 | 148.1 | 118.5 | 215.1
5429.2 | 4797.2 | 388.2 | 401.9 | 147.9 | 118.4 | 215.1
5430.2 | 4798.2 | 388.1 | 401.9 | 147.5 | 118.4 | 215
5431.2 | 4799.2 | 388.2 | 402 | 147.2 | 118.4 | 215
5432.2 | 4800.2 | 388.2 | 401.9 | 147.2 | 118.4 | 215
5433.2 | 4801.2 | 388.2 | 401.9 | 147 | 118.3 | 214.9
5434.2 | 4802.2 | 388.2 | 401.9 | 147.1 | 118.2 | 214.9
5435.2 | 4803.2 | 388.2 | 401.9 | 147.3 | 118.1 | 214.9
5436.2 | 4804.2 | 388.2 | 401.9 | 147.7 | 118 | 214.8
5437.2 | 4805.2 | 388.2 | 401.9 | 147.8 | 117.9 | 214.7
5438.2 | 4806.2 | 388.2 | 401.9 | 147.7 | 117.8 | 214.6
5439.2 | 4807.2 | 388.2 | 401.9 | 147.6 | 117.8 | 214.5
5440.2 | 4808.2 | 388.1 | 401.9 | 147.5 | 117.8 | 214.3
5441.2 | 4809.2 | 388.2 | 401.9 | 147.2 | 117.5 | 214.2
5442.2 | 4810.2 | 388.2 | 402 | 147.1 | 117.3 | 214.1
5443.2 | 4811.2 | 388.2 | 401.9 | 147 | 117.1 | 214
5444.2 | 4812.2 | 388.2 | 402 | 147 | 117.1 | 213.9
5445.2 | 4813.2 | 388.2 | 401.9 | 146.9 | 117 | 213.8
5446.2 | 4814.2 | 388.1 | 401.9 | 146.9 | 116.9 | 213.8
5447.2 | 4815.2 | 388.1 | 401.9 | 146.7 | 116.7 | 213.7
5448.2 | 4816.2 | 388.2 | 401.9 | 146.6 | 116.5 | 213.5
5449.2 | 4817.2 | 388.2 | 401.9 | 146.5 | 116.3 | 213.4
5450.2 | 4818.2 | 388.2 | 401.9 | 146.5 | 116.1 | 213.2
5451.2 | 4819.2 | 388.2 | 401.9 | 146.6 | 116 | 213.2
5452.2 | 4820.2 | 388.2 | 401.9 | 146.5 | 115.9 | 213.1
5453.2 | 4821.2 | 388.1 | 401.9 | 146.4 | 115.8 | 213
5454.2 | 4822.2 | 388.2 | 401.9 | 146.2 | 115.6 | 212.9
5455.2 | 4823.2 | 388.2 | 401.9 | 146.1 | 115.5 | 212.8
5456.2 | 4824.2 | 388.2 | 401.9 | 145.9 | 115.3 | 212.7
5457.2 | 4825.2 | 388.1 | 401.9 | 145.8 | 115.1 | 212.6
5458.2 | 4826.2 | 388.2 | 401.9 | 145.9 | 115.1 | 212.5
5459.2 | 4827.2 | 388.2 | 401.9 | 146 | 115.2 | 212.4
5460.2 | 4828.2 | 388.1 | 401.9 | 146.1 | 115.1 | 212.3
5461.2 | 4829.2 | 388.1 | 401.9 | 146.2 | 115.1 | 212.2
5462.2 | 4830.2 | 388.1 | 401.9 | 146.3 | 115 | 212.1
5463.2 | 4831.2 | 388.1 | 401.9 | 146.5 | 114.8 | 212.1
5464.2 | 4832.2 | 388.1 | 401.9 | 146.5 | 114.7 | 212
5465.2 | 4833.2 | 388.1 | 401.9 | 146.6 | 114.8 | 211.9
5466.2 | 4834.2 | 388.1 | 401.9 | 146.6 | 114.8 | 211.7
5467.2 | 4835.2 | 388.1 | 401.9 | 146.6 | 115 | 211.7
5468.2 | 4836.2 | 388.1 | 401.9 | 146.5 | 115.1 | 211.8
5469.2 | 4837.2 | 388.1 | 401.9 | 146.4 | 115.1 | 211.8
5470.2 | 4838.2 | 388.1 | 401.9 | 146.3 | 115.1 | 211.7
5471.2 | 4839.2 | 388.1 | 401.9 | 146.3 | 115 | 211.6
5472.2 | 4840.2 | 388.1 | 401.9 | 146.3 | 114.8 | 211.5
5473.2 | 4841.2 | 388.1 | 401.9 | 146.1 | 114.8 | 211.5
5474.2 | 4842.2 | 388.1 | 401.9 | 145.8 | 114.9 | 211.5
5475.2 | 4843.2 | 388.1 | 401.9 | 145.6 | 115.1 | 211.4
5476.2 | 4844.2 | 388.1 | 401.9 | 145.9 | 115.1 | 211.4
5477.2 | 4845.2 | 388.1 | 402 | 145.9 | 115.2 | 211.3
5478.2 | 4846.2 | 388.1 | 402 | 145.7 | 115.3 | 211.3
5479.2 | 4847.2 | 388.1 | 402 | 145.4 | 115.3 | 211.3
5480.2 | 4848.2 | 388.1 | 402 | 145.1 | 115.3 | 211.2
5481.2 | 4849.2 | 388.1 | 402 | 144.9 | 115.3 | 211.1
5482.2 | 4850.2 | 388.1 | 402 | 144.8 | 115.5 | 211.1
5483.2 | 4851.2 | 388.1 | 402 | 144.7 | 115.5 | 211.1
5484.2 | 4852.2 | 388.1 | 402.1 | 144.5 | 115.6 | 211
5485.2 | 4853.2 | 388.1 | 402.1 | 144.5 | 115.5 | 211
5486.2 | 4854.2 | 388.1 | 402.1 | 144.4 | 115.4 | 210.9
5487.2 | 4855.2 | 388.1 | 402.1 | 144.3 | 115.4 | 210.8
5488.2 | 4856.2 | 388.1 | 402.1 | 144.2 | 115.3 | 210.8
5489.2 | 4857.2 | 388 | 402.1 | 144.2 | 115.3 | 210.8
5490.2 | 4858.2 | 388.1 | 402.1 | 144 | 115.3 | 210.7
5491.2 | 4859.2 | 388.1 | 402.1 | 143.9 | 115.3 | 210.6
5492.2 | 4860.2 | 388.1 | 402.1 | 143.8 | 115.3 | 210.6
5493.2 | 4861.2 | 388.1 | 402.1 | 143.6 | 115.3 | 210.5
5494.2 | 4862.2 | 388.1 | 402.1 | 143.6 | 115.2 | 210.4
5495.2 | 4863.2 | 388.1 | 402.1 | 143.6 | 115.1 | 210.3
5496.2 | 4864.2 | 388.1 | 402.1 | 144.2 | 115 | 210.2
5497.2 | 4865.2 | 388.1 | 402.1 | 144.4 | 114.9 | 210.1
5498.2 | 4866.2 | 388.1 | 402.1 | 144.4 | 114.9 | 210
5499.2 | 4867.2 | 388.1 | 402.1 | 144.5 | 115 | 209.9
5500.2 | 4868.2 | 388.1 | 402.1 | 144.4 | 115 | 209.8
5501.2 | 4869.2 | 388.1 | 402 | 144.2 | 115.2 | 209.8
5502.2 | 4870.2 | 388.1 | 402 | 144.1 | 115.2 | 209.8
5503.2 | 4871.2 | 388.1 | 402.1 | 143.9 | 115.3 | 209.7
5504.2 | 4872.2 | 388.1 | 402.1 | 143.8 | 115.2 | 209.6
5505.2 | 4873.2 | 388.1 | 402.1 | 143.8 | 115.2 | 209.6
5506.2 | 4874.2 | 388.1 | 402.1 | 143.6 | 115 | 209.5
5507.2 | 4875.2 | 388.1 | 402.1 | 143.4 | 114.9 | 209.5
5508.2 | 4876.2 | 388.1 | 402.1 | 143.2 | 114.7 | 209.4
5509.2 | 4877.2 | 388.1 | 402.1 | 143 | 114.7 | 209.4
5510.2 | 4878.2 | 388.1 | 402.1 | 143.3 | 114.6 | 209.3
5511.2 | 4879.2 | 388.1 | 402 | 143.2 | 114.5 | 209.2
5512.2 | 4880.2 | 388.1 | 402.1 | 143.5 | 114.3 | 209.1
5513.2 | 4881.2 | 388.1 | 402.1 | 143.7 | 114.1 | 209
5514.2 | 4882.2 | 388.1 | 402 | 143.7 | 114 | 208.9
5515.2 | 4883.2 | 388.1 | 402 | 143.5 | 113.9 | 208.8
5516.2 | 4884.2 | 388.1 | 402 | 143.4 | 113.9 | 208.6
5517.2 | 4885.2 | 388.1 | 402.1 | 143.3 | 113.9 | 208.5
5518.2 | 4886.2 | 388.1 | 402.1 | 143.5 | 113.8 | 208.4
5519.2 | 4887.2 | 388.1 | 402 | 143.5 | 113.8 | 208.3
5520.2 | 4888.2 | 388.1 | 402 | 143.6 | 113.8 | 208.2
5521.2 | 4889.2 | 388 | 402 | 144.2 | 113.7 | 208.1
5522.2 | 4890.2 | 388 | 402.1 | 144.6 | 113.6 | 208.1
5523.2 | 4891.2 | 388 | 402 | 144.7 | 113.6 | 208
5524.2 | 4892.2 | 388.1 | 402 | 144.7 | 113.6 | 207.9
5525.2 | 4893.2 | 388.1 | 402 | 144.6 | 113.6 | 207.8
5526.2 | 4894.2 | 388 | 402 | 144.9 | 113.4 | 207.7
5527.2 | 4895.2 | 388 | 402 | 145.4 | 113.4 | 207.7
5528.2 | 4896.2 | 388 | 402 | 146.6 | 113.5 | 207.6
5529.2 | 4897.2 | 388 | 402 | 146.8 | 113.6 | 207.5
5530.2 | 4898.2 | 388 | 402 | 147 | 113.5 | 207.5
5531.2 | 4899.2 | 388 | 402 | 146.8 | 113.5 | 207.4
5532.2 | 4900.2 | 388 | 402 | 146.8 | 113.4 | 207.4
5533.2 | 4901.2 | 388 | 402 | 146.7 | 113.3 | 207.3
5534.2 | 4902.2 | 388 | 402 | 146.5 | 113.3 | 207.2
5535.2 | 4903.2 | 388 | 402 | 146.3 | 113.2 | 207.1
5536.2 | 4904.2 | 388 | 402 | 146 | 113.2 | 207
5537.2 | 4905.2 | 388 | 402 | 145.8 | 113.3 | 206.9
5538.2 | 4906.2 | 388 | 402 | 145.7 | 113.4 | 206.8
5539.2 | 4907.2 | 388 | 402 | 145.7 | 113.5 | 206.8
5540.2 | 4908.2 | 388 | 402 | 145.4 | 113.5 | 206.8
5541.2 | 4909.2 | 388 | 402 | 145.1 | 113.5 | 206.7
5542.2 | 4910.2 | 388 | 402 | 145 | 113.5 | 206.7
5543.2 | 4911.2 | 388 | 402 | 144.7 | 113.5 | 206.6
5544.2 | 4912.2 | 388 | 402 | 144.4 | 113.4 | 206.6
5545.2 | 4913.2 | 388 | 402 | 144.1 | 113.3 | 206.5
5546.2 | 4914.2 | 388 | 402 | 143.8 | 113.3 | 206.5
5547.2 | 4915.2 | 387.9 | 402 | 143.5 | 113.3 | 206.4
5548.2 | 4916.2 | 388 | 402.1 | 143.3 | 113.2 | 206.3
5549.2 | 4917.2 | 387.9 | 402.1 | 143.3 | 113.2 | 206.2
5550.2 | 4918.2 | 388 | 402.1 | 143.3 | 113.1 | 206.1
5551.2 | 4919.2 | 388 | 402.1 | 143.2 | 113.1 | 206.1
5552.2 | 4920.2 | 387.9 | 402 | 143.3 | 113.2 | 206.1
5553.2 | 4921.2 | 387.9 | 402 | 143.4 | 113.2 | 206.1
5554.2 | 4922.2 | 387.9 | 402 | 143.3 | 113.1 | 206
5555.2 | 4923.2 | 387.9 | 402 | 143.1 | 113 | 205.9
5556.2 | 4924.2 | 387.9 | 402.1 | 142.8 | 112.9 | 205.8
5557.2 | 4925.2 | 387.9 | 402 | 142.6 | 112.9 | 205.8
5558.2 | 4926.2 | 387.9 | 402 | 142.4 | 112.8 | 205.7
5559.2 | 4927.2 | 387.9 | 402.1 | 142.3 | 112.8 | 205.6
5560.2 | 4928.2 | 387.9 | 402.1 | 142.3 | 112.8 | 205.6
5561.2 | 4929.2 | 388 | 402.1 | 142.2 | 112.8 | 205.5
5562.2 | 4930.2 | 388 | 402 | 142.2 | 112.8 | 205.4
5563.2 | 4931.2 | 387.9 | 402 | 142.2 | 112.6 | 205.4
5564.2 | 4932.2 | 388 | 402 | 142.5 | 112.6 | 205.3
5565.2 | 4933.2 | 388 | 402 | 142.7 | 112.6 | 205.2
5566.2 | 4934.2 | 387.9 | 402 | 142.9 | 112.6 | 205.1
5567.2 | 4935.2 | 387.9 | 402 | 142.9 | 112.6 | 205.1
5568.2 | 4936.2 | 387.9 | 402 | 143 | 112.7 | 205
5569.2 | 4937.2 | 387.9 | 402 | 142.9 | 112.6 | 205
5570.2 | 4938.2 | 387.9 | 402 | 142.8 | 112.6 | 204.9
5571.2 | 4939.2 | 387.9 | 402 | 142.6 | 112.4 | 204.8
5572.2 | 4940.2 | 387.9 | 402 | 142.4 | 112.4 | 204.7
5573.2 | 4941.2 | 387.9 | 402.1 | 142.1 | 112.4 | 204.6
5574.2 | 4942.2 | 387.9 | 402.1 | 141.7 | 112.3 | 204.5
5575.2 | 4943.2 | 387.9 | 402.1 | 141.3 | 112.2 | 204.5
5576.2 | 4944.2 | 387.9 | 402.1 | 141 | 112.2 | 204.4
5577.2 | 4945.2 | 387.9 | 402.1 | 140.7 | 112.2 | 204.3
5578.2 | 4946.2 | 387.9 | 402.1 | 140.4 | 112.1 | 204.3
5579.2 | 4947.2 | 387.9 | 402.1 | 140.1 | 111.9 | 204.2
5580.2 | 4948.2 | 387.9 | 402.1 | 139.9 | 111.7 | 204.1
5581.2 | 4949.2 | 387.9 | 402.1 | 140.2 | 111.6 | 204
5582.2 | 4950.2 | 387.9 | 402.1 | 140.3 | 111.6 | 204
5583.2 | 4951.2 | 387.9 | 402.1 | 140.2 | 111.7 | 203.9
5584.2 | 4952.2 | 387.8 | 402.1 | 140.1 | 111.6 | 203.8
5585.2 | 4953.2 | 387.9 | 402.1 | 140.3 | 111.5 | 203.7
5586.2 | 4954.2 | 387.8 | 402.1 | 141 | 111.4 | 203.6
5587.2 | 4955.2 | 387.9 | 402.1 | 141.4 | 111.5 | 203.6
5588.2 | 4956.2 | 387.8 | 402 | 141.2 | 111.5 | 203.6
5589.2 | 4957.2 | 387.8 | 402 | 141 | 111.5 | 203.5
5590.2 | 4958.2 | 387.8 | 402.1 | 140.8 | 111.5 | 203.5
5591.2 | 4959.2 | 387.8 | 402.1 | 140.7 | 111.4 | 203.4
5592.2 | 4960.2 | 387.8 | 402.2 | 140.6 | 111.3 | 203.3
5593.2 | 4961.2 | 387.8 | 402.2 | 140.6 | 111.3 | 203.2
5594.2 | 4962.2 | 387.8 | 402.2 | 140.5 | 111.3 | 203.1
5595.2 | 4963.2 | 387.8 | 402.1 | 140.7 | 111.2 | 203
5596.2 | 4964.2 | 387.8 | 402.1 | 140.9 | 111.1 | 203
5597.2 | 4965.2 | 387.8 | 402.1 | 140.9 | 111.1 | 202.9
5598.2 | 4966.2 | 387.8 | 402.1 | 140.7 | 110.8 | 202.8
5599.2 | 4967.2 | 387.8 | 402.1 | 140.6 | 110.7 | 202.7
5600.2 | 4968.2 | 387.8 | 402.1 | 140.5 | 110.5 | 202.6
5601.2 | 4969.2 | 387.8 | 402.1 | 140.6 | 110.5 | 202.4
5602.2 | 4970.2 | 387.8 | 402.1 | 140.5 | 110.4 | 202.3
5603.2 | 4971.2 | 387.8 | 402.1 | 140.4 | 110.4 | 202.2
5604.2 | 4972.2 | 387.8 | 402.1 | 140.1 | 110.5 | 202.1
5605.2 | 4973.2 | 387.8 | 402.1 | 139.7 | 110.5 | 201.9
5606.2 | 4974.2 | 387.8 | 402.1 | 139.4 | 110.5 | 201.9
5607.2 | 4975.2 | 387.8 | 402 | 139.1 | 110.4 | 201.9
5608.2 | 4976.2 | 387.8 | 402 | 138.9 | 110.4 | 201.9
5609.2 | 4977.2 | 387.8 | 402 | 138.8 | 110.5 | 201.9
5610.2 | 4978.2 | 387.7 | 402 | 138.7 | 110.7 | 201.8
5611.2 | 4979.2 | 387.7 | 402.1 | 138.6 | 110.6 | 201.7
5612.2 | 4980.2 | 387.8 | 402.1 | 138.7 | 110.5 | 201.6
5613.2 | 4981.2 | 387.8 | 402.1 | 138.9 | 110.3 | 201.5
5614.2 | 4982.2 | 387.8 | 402.1 | 139 | 110.3 | 201.4
5615.2 | 4983.2 | 387.8 | 402.1 | 139.2 | 110.3 | 201.3
5616.2 | 4984.2 | 387.7 | 402.1 | 139.7 | 110.1 | 201.2
5617.2 | 4985.2 | 387.7 | 402 | 140 | 110 | 201.1
5618.2 | 4986.2 | 387.7 | 402 | 139.9 | 109.9 | 201.1
5619.2 | 4987.2 | 387.7 | 402 | 139.9 | 109.7 | 201
5620.2 | 4988.2 | 387.7 | 402 | 140.1 | 109.7 | 201
5621.2 | 4989.2 | 387.7 | 402 | 140.2 | 109.6 | 201
5622.2 | 4990.2 | 387.7 | 402 | 140 | 109.5 | 201
5623.2 | 4991.2 | 387.7 | 402 | 139.9 | 109.5 | 200.9
5624.2 | 4992.2 | 387.7 | 402 | 139.9 | 109.5 | 200.9
5625.2 | 4993.2 | 387.7 | 402 | 139.7 | 109.6 | 200.8
5626.2 | 4994.2 | 387.7 | 402 | 139.5 | 109.7 | 200.7
5627.2 | 4995.2 | 387.7 | 402 | 139.3 | 109.6 | 200.7
5628.2 | 4996.2 | 387.7 | 402 | 139.1 | 109.6 | 200.6
5629.2 | 4997.2 | 387.7 | 402 | 138.8 | 109.5 | 200.5
5630.2 | 4998.2 | 387.7 | 402.1 | 138.8 | 109.5 | 200.5
5631.2 | 4999.2 | 387.7 | 402 | 138.5 | 109.5 | 200.4
5632.2 | 5000.2 | 387.7 | 402 | 138.3 | 109.5 | 200.3
5633.2 | 5001.2 | 387.7 | 402.1 | 138.2 | 109.4 | 200.3
5634.2 | 5002.2 | 387.7 | 402.1 | 138.1 | 109.3 | 200.2
5635.2 | 5003.2 | 387.7 | 402.1 | 138 | 109.3 | 200.2
5636.2 | 5004.2 | 387.7 | 402.1 | 137.8 | 109.3 | 200
5637.2 | 5005.2 | 387.7 | 402.1 | 137.4 | 109.2 | 200
5638.2 | 5006.2 | 387.7 | 402.1 | 137.3 | 109.2 | 199.9
5639.2 | 5007.2 | 387.7 | 402.1 | 137.2 | 109.1 | 199.8
5640.2 | 5008.2 | 387.7 | 402.1 | 137.8 | 109 | 199.7
5641.2 | 5009.2 | 387.7 | 402.1 | 138.2 | 108.8 | 199.7
5642.2 | 5010.2 | 387.7 | 402 | 138.2 | 108.6 | 199.6
5643.2 | 5011.2 | 387.7 | 402 | 138.3 | 108.7 | 199.5
5644.2 | 5012.2 | 387.6 | 402 | 138.8 | 108.9 | 199.5
5645.2 | 5013.2 | 387.6 | 402 | 139.3 | 108.9 | 199.5
5646.2 | 5014.2 | 387.7 | 402 | 139.5 | 108.7 | 199.4
5647.2 | 5015.2 | 387.7 | 402.1 | 139.5 | 108.6 | 199.4
5648.2 | 5016.2 | 387.7 | 402.1 | 139.5 | 108.6 | 199.3
5649.2 | 5017.2 | 387.7 | 402 | 139.5 | 108.7 | 199.3
5650.2 | 5018.2 | 387.7 | 402 | 140.1 | 108.7 | 199.2
5651.2 | 5019.2 | 387.7 | 402 | 139.8 | 108.7 | 199.1
5652.2 | 5020.2 | 387.7 | 402 | 139.6 | 108.7 | 199
5653.2 | 5021.2 | 387.7 | 402.1 | 139.4 | 108.7 | 199
5654.2 | 5022.2 | 387.7 | 402 | 139.1 | 108.7 | 198.9
5655.2 | 5023.2 | 387.7 | 402 | 138.7 | 108.7 | 198.8
5656.2 | 5024.2 | 387.7 | 402.1 | 138.3 | 108.7 | 198.7
5657.2 | 5025.2 | 387.7 | 402.1 | 138.1 | 108.6 | 198.6
5658.2 | 5026.2 | 387.7 | 402 | 138.3 | 108.4 | 198.4
5659.2 | 5027.2 | 387.7 | 402 | 139.2 | 108.4 | 198.2
5660.2 | 5028.2 | 387.7 | 402.1 | 139.6 | 108.3 | 198.1
5661.2 | 5029.2 | 387.7 | 402 | 139.4 | 108.4 | 198.1
5662.2 | 5030.2 | 387.6 | 402 | 139.1 | 108.4 | 198.1
5663.2 | 5031.2 | 387.7 | 402 | 138.7 | 108.4 | 198.1
5664.2 | 5032.2 | 387.6 | 402.1 | 138.2 | 108.4 | 198.1
5665.2 | 5033.2 | 387.7 | 402.1 | 137.7 | 108.4 | 198
5666.2 | 5034.2 | 387.7 | 402.1 | 137.3 | 108.4 | 198
5667.2 | 5035.2 | 387.7 | 402.1 | 137 | 108.3 | 197.9
5668.2 | 5036.2 | 387.7 | 402.1 | 136.8 | 108.3 | 197.9
5669.2 | 5037.2 | 387.7 | 402.1 | 136.5 | 108.2 | 197.8
5670.2 | 5038.2 | 387.7 | 402.1 | 136.2 | 108.2 | 197.8
5671.2 | 5039.2 | 387.7 | 402.1 | 136 | 108.3 | 197.8
5672.2 | 5040.2 | 387.7 | 402.1 | 135.7 | 108.2 | 197.7
5673.2 | 5041.2 | 387.7 | 402.1 | 135.6 | 108.1 | 197.7
5674.2 | 5042.2 | 387.7 | 402.1 | 135.5 | 108.1 | 197.7
5675.2 | 5043.2 | 387.7 | 402.2 | 135.3 | 108.2 | 197.6
5676.2 | 5044.2 | 387.7 | 402.2 | 135.2 | 108.1 | 197.5
5677.2 | 5045.2 | 387.7 | 402.2 | 135.1 | 108 | 197.4
5678.2 | 5046.2 | 387.7 | 402.2 | 135 | 108.1 | 197.3
5679.2 | 5047.2 | 387.7 | 402.2 | 135.1 | 108 | 197.2
5680.2 | 5048.2 | 387.7 | 402.2 | 135.3 | 107.9 | 197.1
5681.2 | 5049.2 | 387.7 | 402.3 | 135.3 | 107.8 | 197.1
5682.2 | 5050.2 | 387.7 | 402.2 | 135.3 | 107.9 | 197
5683.2 | 5051.2 | 387.7 | 402.2 | 135.1 | 107.8 | 197
5684.2 | 5052.2 | 387.7 | 402.1 | 135 | 107.9 | 197
5685.2 | 5053.2 | 387.7 | 402.1 | 134.9 | 107.9 | 196.9
5686.2 | 5054.2 | 387.7 | 402.2 | 135 | 107.9 | 196.8
5687.2 | 5055.2 | 387.7 | 402.2 | 134.9 | 107.8 | 196.7
5688.2 | 5056.2 | 387.7 | 402.2 | 134.8 | 107.7 | 196.6
5689.2 | 5057.2 | 387.7 | 402.2 | 134.7 | 107.8 | 196.5
5690.2 | 5058.2 | 387.7 | 402.2 | 134.7 | 107.8 | 196.4
5691.2 | 5059.2 | 387.7 | 402.2 | 134.8 | 107.7 | 196.4
5692.2 | 5060.2 | 387.7 | 402.2 | 134.9 | 107.6 | 196.3
5693.2 | 5061.2 | 387.7 | 402.2 | 134.9 | 107.5 | 196.3
5694.2 | 5062.2 | 387.7 | 402.2 | 134.8 | 107.4 | 196.3
5695.2 | 5063.2 | 387.7 | 402.2 | 134.5 | 107.4 | 196.2
5696.2 | 5064.2 | 387.7 | 402.2 | 134.3 | 107.5 | 196.2
5697.2 | 5065.2 | 387.7 | 402.2 | 134.2 | 107.5 | 196.1
5698.2 | 5066.2 | 387.7 | 402.3 | 134.6 | 107.4 | 196
5699.2 | 5067.2 | 387.7 | 402.2 | 134.6 | 107.3 | 196
5700.2 | 5068.2 | 387.7 | 402.2 | 134.6 | 107.2 | 195.9
5701.2 | 5069.2 | 387.7 | 402.2 | 134.4 | 107.2 | 195.8
5702.2 | 5070.2 | 387.7 | 402.2 | 134.3 | 107.1 | 195.7
5703.2 | 5071.2 | 387.7 | 402.2 | 134.2 | 107.1 | 195.6
5704.2 | 5072.2 | 387.7 | 402.2 | 134.1 | 107.1 | 195.5
5705.2 | 5073.2 | 387.7 | 402.2 | 134 | 107.2 | 195.5
5706.2 | 5074.2 | 387.7 | 402.2 | 133.8 | 107.1 | 195.5
5707.2 | 5075.2 | 387.7 | 402.2 | 133.7 | 107 | 195.4
5708.2 | 5076.2 | 387.7 | 402.2 | 134 | 106.9 | 195.3
5709.2 | 5077.2 | 387.7 | 402.2 | 134.4 | 106.9 | 195.2
5710.2 | 5078.2 | 387.7 | 402.1 | 134.3 | 106.9 | 195.2
5711.2 | 5079.2 | 387.7 | 402.1 | 134.1 | 106.9 | 195.2
5712.2 | 5080.2 | 387.7 | 402.1 | 133.8 | 106.8 | 195.1
5713.2 | 5081.2 | 387.7 | 402.1 | 133.5 | 106.7 | 195
5714.2 | 5082.2 | 387.7 | 402.2 | 133.3 | 106.7 | 194.9
5715.2 | 5083.2 | 387.7 | 402.2 | 133 | 106.6 | 194.9
5716.2 | 5084.2 | 387.7 | 402.2 | 132.9 | 106.5 | 194.8
5717.2 | 5085.2 | 387.7 | 402.2 | 132.8 | 106.4 | 194.7
5718.2 | 5086.2 | 387.7 | 402.3 | 132.9 | 106.3 | 194.6
5719.2 | 5087.2 | 387.7 | 402.2 | 132.9 | 106.3 | 194.6
5720.2 | 5088.2 | 387.7 | 402.2 | 132.8 | 106.4 | 194.6
5721.2 | 5089.2 | 387.7 | 402.3 | 132.7 | 106.4 | 194.5
5722.2 | 5090.2 | 387.7 | 402.3 | 132.7 | 106.4 | 194.4
5723.2 | 5091.2 | 387.7 | 402.3 | 132.6 | 106.4 | 194.3
5724.2 | 5092.2 | 387.7 | 402.3 | 132.5 | 106.4 | 194.2
5725.2 | 5093.2 | 387.7 | 402.2 | 132.4 | 106.5 | 194.2
5726.2 | 5094.2 | 387.7 | 402.2 | 132.5 | 106.5 | 194.2
5727.2 | 5095.2 | 387.7 | 402.2 | 132.5 | 106.4 | 194.1
5728.2 | 5096.2 | 387.7 | 402.2 | 132.5 | 106.5 | 194
5729.2 | 5097.2 | 387.7 | 402.2 | 132.9 | 106.5 | 193.9
5730.2 | 5098.2 | 387.7 | 402.2 | 133.2 | 106.5 | 193.9
5731.2 | 5099.2 | 387.7 | 402.3 | 133.2 | 106.5 | 193.9
5732.2 | 5100.2 | 387.7 | 402.2 | 133.2 | 106.5 | 193.8
5733.2 | 5101.2 | 387.7 | 402.2 | 133.2 | 106.5 | 193.8
5734.2 | 5102.2 | 387.7 | 402.2 | 133.2 | 106.4 | 193.8
5735.2 | 5103.2 | 387.7 | 402.2 | 133.1 | 106.4 | 193.7
5736.2 | 5104.2 | 387.7 | 402.2 | 132.9 | 106.3 | 193.6
5737.2 | 5105.2 | 387.7 | 402.2 | 132.7 | 106.2 | 193.4
5738.2 | 5106.2 | 387.7 | 402.2 | 132.7 | 106.1 | 193.3
5739.2 | 5107.2 | 387.7 | 402.2 | 132.7 | 106.1 | 193.2
5740.2 | 5108.2 | 387.7 | 402.3 | 132.7 | 106.1 | 193
5741.2 | 5109.2 | 387.6 | 402.2 | 132.8 | 106.2 | 192.9
5742.2 | 5110.2 | 387.6 | 402.2 | 132.7 | 106.2 | 192.8
5743.2 | 5111.2 | 387.6 | 402.2 | 132.8 | 106.1 | 192.8
5744.2 | 5112.2 | 387.6 | 402.3 | 132.9 | 106 | 192.7
5745.2 | 5113.2 | 387.7 | 402.3 | 132.8 | 105.8 | 192.7
5746.2 | 5114.2 | 387.6 | 402.3 | 132.8 | 105.7 | 192.6
5747.2 | 5115.2 | 387.6 | 402.3 | 132.8 | 105.7 | 192.5
5748.2 | 5116.2 | 387.6 | 402.3 | 132.8 | 105.6 | 192.5
5749.2 | 5117.2 | 387.6 | 402.3 | 132.7 | 105.6 | 192.4
5750.2 | 5118.2 | 387.6 | 402.3 | 132.5 | 105.5 | 192.4
5751.2 | 5119.2 | 387.6 | 402.3 | 132.3 | 105.4 | 192.3
5752.2 | 5120.2 | 387.6 | 402.3 | 132.3 | 105.3 | 192.3
5753.2 | 5121.2 | 387.6 | 402.3 | 132.3 | 105.1 | 192.2
5754.2 | 5122.2 | 387.6 | 402.3 | 132.5 | 105 | 192.2
5755.2 | 5123.2 | 387.6 | 402.3 | 132.3 | 104.8 | 192.1
5756.2 | 5124.2 | 387.6 | 402.3 | 132.5 | 104.8 | 192
5757.2 | 5125.2 | 387.6 | 402.3 | 133 | 104.8 | 191.9
5758.2 | 5126.2 | 387.6 | 402.3 | 133.2 | 104.7 | 191.7
5759.2 | 5127.2 | 387.6 | 402.3 | 133.4 | 104.6 | 191.6
5760.2 | 5128.2 | 387.6 | 402.3 | 133.4 | 104.4 | 191.6
5761.2 | 5129.2 | 387.6 | 402.3 | 133.5 | 104.3 | 191.6
5762.2 | 5130.2 | 387.6 | 402.3 | 133.5 | 104.3 | 191.5
5763.2 | 5131.2 | 387.6 | 402.3 | 133.3 | 104.2 | 191.5
5764.2 | 5132.2 | 387.6 | 402.3 | 133 | 104.1 | 191.4
5765.2 | 5133.2 | 387.6 | 402.3 | 132.5 | 104.1 | 191.3
5766.2 | 5134.2 | 387.6 | 402.4 | 132.2 | 104 | 191
5767.2 | 5135.2 | 387.6 | 402.4 | 131.9 | 103.9 | 190.9
5768.2 | 5136.2 | 387.6 | 402.4 | 131.9 | 103.8 | 190.8
5769.2 | 5137.2 | 387.6 | 402.4 | 131.8 | 103.5 | 190.7
5770.2 | 5138.2 | 387.6 | 402.4 | 131.7 | 103.2 | 190.7
5771.2 | 5139.2 | 387.6 | 402.4 | 132.1 | 102.9 | 190.7
5772.2 | 5140.2 | 387.6 | 402.4 | 132.4 | 102.9 | 190.6
5773.2 | 5141.2 | 387.6 | 402.4 | 132.4 | 103 | 190.5
5774.2 | 5142.2 | 387.6 | 402.4 | 132.4 | 103.1 | 190.5
5775.2 | 5143.2 | 387.6 | 402.4 | 132.8 | 103.1 | 190.5
5776.2 | 5144.2 | 387.6 | 402.4 | 133.6 | 103 | 190.5
5777.2 | 5145.2 | 387.6 | 402.3 | 133.8 | 102.9 | 190.4
5778.2 | 5146.2 | 387.6 | 402.3 | 133.7 | 102.8 | 190.4
5779.2 | 5147.2 | 387.6 | 402.3 | 133.5 | 102.7 | 190.3
5780.2 | 5148.2 | 387.6 | 402.4 | 133.2 | 102.7 | 190.2
5781.2 | 5149.2 | 387.6 | 402.4 | 132.9 | 102.6 | 190.2
5782.2 | 5150.2 | 387.6 | 402.5 | 132.6 | 102.5 | 190.1
5783.2 | 5151.2 | 387.6 | 402.5 | 132.4 | 102.3 | 190
5784.2 | 5152.2 | 387.6 | 402.5 | 132.2 | 102.2 | 189.8
5785.2 | 5153.2 | 387.6 | 402.5 | 132.1 | 102.2 | 189.8
5786.2 | 5154.2 | 387.6 | 402.5 | 132 | 102.2 | 189.7
5787.2 | 5155.2 | 387.6 | 402.5 | 131.9 | 102.3 | 189.6
5788.2 | 5156.2 | 387.6 | 402.5 | 131.8 | 102.2 | 189.5
5789.2 | 5157.2 | 387.6 | 402.5 | 131.7 | 102.2 | 189.4
5790.2 | 5158.2 | 387.6 | 402.5 | 131.6 | 102 | 189.4
5791.2 | 5159.2 | 387.6 | 402.5 | 131.5 | 101.9 | 189.2
5792.2 | 5160.2 | 387.6 | 402.6 | 131.5 | 101.8 | 189.1
5793.2 | 5161.2 | 387.6 | 402.5 | 131.5 | 101.8 | 189.1
5794.2 | 5162.2 | 387.6 | 402.5 | 131.4 | 101.8 | 189
5795.2 | 5163.2 | 387.6 | 402.5 | 131.2 | 101.7 | 188.9
5796.2 | 5164.2 | 387.6 | 402.6 | 131 | 101.6 | 188.9
5797.2 | 5165.2 | 387.6 | 402.6 | 130.7 | 101.5 | 188.8
5798.2 | 5166.2 | 387.6 | 402.6 | 130.3 | 101.4 | 188.7
5799.2 | 5167.2 | 387.6 | 402.6 | 129.9 | 101.3 | 188.6
5800.2 | 5168.2 | 387.6 | 402.6 | 129.7 | 101.2 | 188.6
5801.2 | 5169.2 | 387.6 | 402.6 | 129.4 | 101.2 | 188.6
5802.2 | 5170.2 | 387.6 | 402.6 | 129.3 | 101.3 | 188.6
5803.2 | 5171.2 | 387.6 | 402.6 | 129.2 | 101.3 | 188.5
5804.2 | 5172.2 | 387.6 | 402.6 | 129.1 | 101.2 | 188.4
5805.2 | 5173.2 | 387.6 | 402.6 | 128.9 | 101.2 | 188.4
5806.2 | 5174.2 | 387.6 | 402.6 | 128.9 | 101.1 | 188.3
5807.2 | 5175.2 | 387.6 | 402.6 | 128.8 | 101.1 | 188.3
5808.2 | 5176.2 | 387.6 | 402.6 | 128.7 | 101.1 | 188.2
5809.2 | 5177.2 | 387.6 | 402.6 | 128.7 | 101.1 | 188.2
5810.2 | 5178.2 | 387.6 | 402.6 | 128.6 | 101.2 | 188.1
5811.2 | 5179.2 | 387.6 | 402.6 | 128.5 | 101.4 | 188
5812.2 | 5180.2 | 387.6 | 402.6 | 128.4 | 101.5 | 187.9
5813.2 | 5181.2 | 387.6 | 402.6 | 128.3 | 101.5 | 187.9
5814.2 | 5182.2 | 387.6 | 402.6 | 128.3 | 101.5 | 187.9
5815.2 | 5183.2 | 387.6 | 402.5 | 128.2 | 101.3 | 187.8
5816.2 | 5184.2 | 387.6 | 402.6 | 128 | 101.2 | 187.6
5817.2 | 5185.2 | 387.6 | 402.5 | 128 | 101.2 | 187.5
5818.2 | 5186.2 | 387.6 | 402.5 | 128.1 | 101.1 | 187.4
5819.2 | 5187.2 | 387.6 | 402.6 | 128.4 | 101.1 | 187.3
5820.2 | 5188.2 | 387.6 | 402.6 | 128.5 | 101.1 | 187.2
5821.2 | 5189.2 | 387.6 | 402.6 | 128.4 | 101 | 187.1
5822.2 | 5190.2 | 387.6 | 402.6 | 128.5 | 100.9 | 187
5823.2 | 5191.2 | 387.6 | 402.6 | 128.6 | 100.9 | 186.9
5824.2 | 5192.2 | 387.6 | 402.6 | 128.4 | 100.9 | 186.8
5825.2 | 5193.2 | 387.6 | 402.6 | 128.2 | 100.9 | 186.7
5826.2 | 5194.2 | 387.6 | 402.6 | 128 | 100.9 | 186.7
5827.2 | 5195.2 | 387.6 | 402.6 | 127.8 | 100.9 | 186.6
5828.2 | 5196.2 | 387.6 | 402.6 | 127.9 | 100.9 | 186.6
5829.2 | 5197.2 | 387.6 | 402.6 | 128 | 100.8 | 186.5
5830.2 | 5198.2 | 387.6 | 402.6 | 128.6 | 100.7 | 186.5
5831.2 | 5199.2 | 387.6 | 402.6 | 129.1 | 100.6 | 186.4
5832.2 | 5200.2 | 387.6 | 402.6 | 128.8 | 100.6 | 186.3
5833.2 | 5201.2 | 387.6 | 402.6 | 128.6 | 100.5 | 186.3
5834.2 | 5202.2 | 387.6 | 402.6 | 128.6 | 100.3 | 186.2
5835.2 | 5203.2 | 387.6 | 402.7 | 128.6 | 100.3 | 186
5836.2 | 5204.2 | 387.6 | 402.7 | 128.5 | 100.2 | 186
5837.2 | 5205.2 | 387.6 | 402.6 | 128.3 | 100.1 | 185.9
5838.2 | 5206.2 | 387.6 | 402.6 | 128.3 | 100 | 185.9
5839.2 | 5207.2 | 387.6 | 402.6 | 128.4 | 99.9 | 185.9
5840.2 | 5208.2 | 387.6 | 402.6 | 129 | 99.8 | 185.8
5841.2 | 5209.2 | 387.6 | 402.6 | 129.4 | 99.7 | 185.7
5842.2 | 5210.2 | 387.6 | 402.6 | 129.2 | 99.8 | 185.6
5843.2 | 5211.2 | 387.6 | 402.6 | 129.1 | 99.9 | 185.6
5844.2 | 5212.2 | 387.6 | 402.6 | 128.9 | 99.9 | 185.5
5845.2 | 5213.2 | 387.6 | 402.6 | 128.6 | 99.8 | 185.5
5846.2 | 5214.2 | 387.6 | 402.6 | 128.4 | 99.9 | 185.4
5847.2 | 5215.2 | 387.6 | 402.6 | 128.2 | 99.9 | 185.3
5848.2 | 5216.2 | 387.6 | 402.6 | 127.9 | 99.7 | 185.3
5849.2 | 5217.2 | 387.6 | 402.7 | 127.6 | 99.7 | 185.3
5850.2 | 5218.2 | 387.6 | 402.7 | 127.5 | 99.7 | 185.3
5851.2 | 5219.2 | 387.6 | 402.7 | 127.2 | 99.7 | 185.1
5852.2 | 5220.2 | 387.6 | 402.7 | 126.8 | 99.7 | 185.1
5853.2 | 5221.2 | 387.6 | 402.7 | 126.4 | 99.7 | 185
5854.2 | 5222.2 | 387.6 | 402.8 | 126.1 | 99.7 | 184.9
5855.2 | 5223.2 | 387.6 | 402.8 | 125.8 | 99.7 | 184.8
5856.2 | 5224.2 | 387.5 | 402.8 | 125.7 | 99.7 | 184.7
5857.2 | 5225.2 | 387.6 | 402.8 | 126.7 | 99.7 | 184.6
5858.2 | 5226.2 | 387.6 | 402.8 | 127.7 | 99.6 | 184.6
5859.2 | 5227.2 | 387.6 | 402.8 | 128.6 | 99.5 | 184.5
5860.2 | 5228.2 | 387.5 | 402.8 | 128.9 | 99.5 | 184.5
5861.2 | 5229.2 | 387.5 | 402.7 | 128.6 | 99.4 | 184.4
5862.2 | 5230.2 | 387.5 | 402.7 | 128.3 | 99.5 | 184.4
5863.2 | 5231.2 | 387.5 | 402.7 | 128 | 99.4 | 184.3
5864.2 | 5232.2 | 387.5 | 402.8 | 127.8 | 99.4 | 184.3
5865.2 | 5233.2 | 387.5 | 402.8 | 127.6 | 99.4 | 184.2
5866.2 | 5234.2 | 387.5 | 402.8 | 127.4 | 99.4 | 184.1
5867.2 | 5235.2 | 387.5 | 402.8 | 127.3 | 99.4 | 184.1
5868.2 | 5236.2 | 387.5 | 402.8 | 127.3 | 99.5 | 184.1
5869.2 | 5237.2 | 387.5 | 402.8 | 127.3 | 99.4 | 184.1
5870.2 | 5238.2 | 387.5 | 402.8 | 127.2 | 99.4 | 184
5871.2 | 5239.2 | 387.5 | 402.8 | 127.6 | 99.4 | 183.9
5872.2 | 5240.2 | 387.5 | 402.8 | 128.5 | 99.4 | 183.9
5873.2 | 5241.2 | 387.5 | 402.8 | 128.9 | 99.4 | 183.8
5874.2 | 5242.2 | 387.5 | 402.7 | 128.9 | 99.4 | 183.8
5875.2 | 5243.2 | 387.5 | 402.7 | 128.7 | 99.3 | 183.7
5876.2 | 5244.2 | 387.5 | 402.7 | 128.4 | 99.3 | 183.6
5877.2 | 5245.2 | 387.5 | 402.8 | 128.1 | 99.2 | 183.5
5878.2 | 5246.2 | 387.5 | 402.9 | 127.9 | 99.1 | 183.4
5879.2 | 5247.2 | 387.5 | 403 | 127.8 | 99.1 | 183.3
5880.2 | 5248.2 | 387.5 | 403 | 128 | 99 | 183.2
5881.2 | 5249.2 | 387.5 | 403 | 128.4 | 98.9 | 183.1
5882.2 | 5250.2 | 387.5 | 402.9 | 128.5 | 98.8 | 183
5883.2 | 5251.2 | 387.5 | 403 | 128.3 | 98.7 | 182.9
5884.2 | 5252.2 | 387.5 | 403 | 128 | 98.6 | 182.8
5885.2 | 5253.2 | 387.5 | 403 | 128.2 | 98.5 | 182.7
5886.2 | 5254.2 | 387.5 | 403 | 128 | 98.4 | 182.6
5887.2 | 5255.2 | 387.5 | 403 | 128.1 | 98.2 | 182.5
5888.2 | 5256.2 | 387.5 | 403 | 128.7 | 98.1 | 182.4
5889.2 | 5257.2 | 387.5 | 403 | 129.1 | 98.1 | 182.4
5890.2 | 5258.2 | 387.4 | 403 | 129.3 | 98.1 | 182.3
5891.2 | 5259.2 | 387.4 | 403 | 129.8 | 98.1 | 182.3
5892.2 | 5260.2 | 387.5 | 402.9 | 130 | 98.1 | 182.3
5893.2 | 5261.2 | 387.4 | 403 | 129.9 | 98 | 182.2
5894.2 | 5262.2 | 387.4 | 402.9 | 129.8 | 97.9 | 182.1
5895.2 | 5263.2 | 387.4 | 402.9 | 129.6 | 97.9 | 182
5896.2 | 5264.2 | 387.4 | 402.9 | 129.5 | 97.9 | 181.9
5897.2 | 5265.2 | 387.4 | 402.9 | 129.4 | 97.8 | 181.8
5898.2 | 5266.2 | 387.4 | 402.9 | 129.3 | 97.7 | 181.8
5899.2 | 5267.2 | 387.4 | 402.9 | 129.1 | 97.7 | 181.7
5900.2 | 5268.2 | 387.4 | 402.9 | 128.9 | 97.7 | 181.7
5901.2 | 5269.2 | 387.4 | 402.9 | 128.8 | 97.7 | 181.7
5902.2 | 5270.2 | 387.4 | 402.9 | 128.5 | 97.7 | 181.6
5903.2 | 5271.2 | 387.4 | 403 | 128.1 | 97.8 | 181.6
5904.2 | 5272.2 | 387.4 | 403 | 127.9 | 97.9 | 181.5
5905.2 | 5273.2 | 387.4 | 403 | 127.9 | 97.7 | 181.5
5906.2 | 5274.2 | 387.4 | 403 | 128 | 97.6 | 181.5
5907.2 | 5275.2 | 387.4 | 403 | 128.2 | 97.5 | 181.3
5908.2 | 5276.2 | 387.4 | 403 | 128.1 | 97.4 | 181.1
5909.2 | 5277.2 | 387.4 | 403 | 127.9 | 97.4 | 181.1
5910.2 | 5278.2 | 387.4 | 403 | 127.7 | 97.3 | 181
5911.2 | 5279.2 | 387.4 | 403 | 127.4 | 97.2 | 180.8
5912.2 | 5280.2 | 387.4 | 403 | 127.1 | 97 | 180.7
5913.2 | 5281.2 | 387.4 | 403.1 | 126.9 | 96.9 | 180.6
5914.2 | 5282.2 | 387.4 | 403.1 | 126.6 | 96.8 | 180.5
5915.2 | 5283.2 | 387.4 | 403.1 | 126.2 | 96.7 | 180.4
5916.2 | 5284.2 | 387.4 | 403.1 | 126 | 96.8 | 180.4
5917.2 | 5285.2 | 387.3 | 403.1 | 126 | 96.7 | 180.3
5918.2 | 5286.2 | 387.3 | 403.1 | 125.9 | 96.6 | 180.2
5919.2 | 5287.2 | 387.3 | 403.1 | 126 | 96.5 | 180.2
5920.2 | 5288.2 | 387.3 | 403 | 125.9 | 96.5 | 180.2
5921.2 | 5289.2 | 387.3 | 403 | 125.9 | 96.5 | 180.1
5922.2 | 5290.2 | 387.3 | 403 | 125.8 | 96.4 | 180
5923.2 | 5291.2 | 387.4 | 403.1 | 125.8 | 96.4 | 179.9
5924.2 | 5292.2 | 387.4 | 403.1 | 125.7 | 96.3 | 179.9
5925.2 | 5293.2 | 387.3 | 403.1 | 126.3 | 96.2 | 179.9
5926.2 | 5294.2 | 387.3 | 403.1 | 127 | 96.2 | 179.8
5927.2 | 5295.2 | 387.3 | 403 | 127.6 | 96.1 | 179.7
5928.2 | 5296.2 | 387.3 | 403 | 128.1 | 96.1 | 179.5
5929.2 | 5297.2 | 387.3 | 403 | 128.5 | 96 | 179.4
5930.2 | 5298.2 | 387.3 | 403 | 128.4 | 96 | 179.5
5931.2 | 5299.2 | 387.3 | 403 | 128 | 95.9 | 179.5
5932.2 | 5300.2 | 387.3 | 403.1 | 127.4 | 95.8 | 179.5
5933.2 | 5301.2 | 387.3 | 403.1 | 126.9 | 95.9 | 179.5
5934.2 | 5302.2 | 387.3 | 403.1 | 126.5 | 96 | 179.4
5935.2 | 5303.2 | 387.3 | 403.1 | 126.1 | 95.9 | 179.3
5936.2 | 5304.2 | 387.3 | 403.2 | 126 | 95.9 | 179.3
5937.2 | 5305.2 | 387.3 | 403.1 | 126.3 | 95.9 | 179.2
5938.2 | 5306.2 | 387.3 | 403.2 | 126.6 | 95.8 | 179.1
5939.2 | 5307.2 | 387.3 | 403.2 | 126.5 | 95.7 | 179
5940.2 | 5308.2 | 387.3 | 403.2 | 126.4 | 95.7 | 178.9
5941.2 | 5309.2 | 387.3 | 403.2 | 126.6 | 95.6 | 178.8
5942.2 | 5310.2 | 387.3 | 403.2 | 126.5 | 95.5 | 178.7
5943.2 | 5311.2 | 387.3 | 403.2 | 126.4 | 95.5 | 178.7
5944.2 | 5312.2 | 387.3 | 403.2 | 126.1 | 95.4 | 178.6
5945.2 | 5313.2 | 387.3 | 403.2 | 125.8 | 95.5 | 178.5
5946.2 | 5314.2 | 387.3 | 403.2 | 125.6 | 95.4 | 178.4
5947.2 | 5315.2 | 387.3 | 403.2 | 125.4 | 95.3 | 178.3
5948.2 | 5316.2 | 387.2 | 403.2 | 125.2 | 95.3 | 178.3
5949.2 | 5317.2 | 387.3 | 403.3 | 125.3 | 95.2 | 178.2
5950.2 | 5318.2 | 387.3 | 403.3 | 125.3 | 95.1 | 178.2
5951.2 | 5319.2 | 387.3 | 403.3 | 125.1 | 94.9 | 178.1
5952.2 | 5320.2 | 387.3 | 403.2 | 125 | 94.7 | 178.1
5953.2 | 5321.2 | 387.3 | 403.2 | 125.3 | 94.4 | 177.9
5954.2 | 5322.2 | 387.3 | 403.2 | 125.3 | 94.4 | 177.8
5955.2 | 5323.2 | 387.2 | 403.3 | 125.3 | 94.5 | 177.7
5956.2 | 5324.2 | 387.2 | 403.2 | 125.3 | 94.4 | 177.7
5957.2 | 5325.2 | 387.2 | 403.2 | 125 | 94.4 | 177.8
5958.2 | 5326.2 | 387.2 | 403.3 | 124.6 | 94.4 | 177.8
5959.2 | 5327.2 | 387.2 | 403.3 | 124.2 | 94.4 | 177.7
5960.2 | 5328.2 | 387.2 | 403.3 | 123.9 | 94.3 | 177.5
5961.2 | 5329.2 | 387.2 | 403.4 | 123.7 | 94.1 | 177.4
5962.2 | 5330.2 | 387.2 | 403.5 | 123.7 | 93.9 | 177.2
5963.2 | 5331.2 | 387.2 | 403.4 | 123.9 | 93.9 | 177.1
5964.2 | 5332.2 | 387.2 | 403.4 | 123.7 | 93.9 | 177
5965.2 | 5333.2 | 387.2 | 403.4 | 123.4 | 93.9 | 177
5966.2 | 5334.2 | 387.2 | 403.4 | 123.1 | 93.8 | 176.9
5967.2 | 5335.2 | 387.2 | 403.4 | 122.9 | 93.7 | 176.8
5968.2 | 5336.2 | 387.2 | 403.5 | 122.6 | 93.6 | 176.8
5969.2 | 5337.2 | 387.2 | 403.5 | 122.6 | 93.4 | 176.7
5970.2 | 5338.2 | 387.2 | 403.5 | 122.9 | 93.2 | 176.6
5971.2 | 5339.2 | 387.2 | 403.4 | 123.1 | 93.1 | 176.6
5972.2 | 5340.2 | 387.2 | 403.4 | 123.5 | 93 | 176.5
5973.2 | 5341.2 | 387.2 | 403.4 | 123.4 | 93.1 | 176.4
5974.2 | 5342.2 | 387.2 | 403.4 | 123.3 | 93.1 | 176.3
5975.2 | 5343.2 | 387.2 | 403.4 | 123.2 | 93.2 | 176.3
5976.2 | 5344.2 | 387.2 | 403.4 | 123.1 | 93.3 | 176.2
5977.2 | 5345.2 | 387.2 | 403.4 | 122.8 | 93.4 | 176.2
5978.2 | 5346.2 | 387.2 | 403.4 | 122.7 | 93.3 | 176.1
5979.2 | 5347.2 | 387.2 | 403.4 | 123.5 | 93.3 | 176
5980.2 | 5348.2 | 387.2 | 403.5 | 124.1 | 93.2 | 175.9
5981.2 | 5349.2 | 387.2 | 403.5 | 124.6 | 93 | 175.7
5982.2 | 5350.2 | 387.2 | 403.5 | 124.7 | 92.7 | 175.6
5983.2 | 5351.2 | 387.2 | 403.4 | 124.6 | 92.6 | 175.7
5984.2 | 5352.2 | 387.2 | 403.4 | 125.2 | 92.6 | 175.6
5985.2 | 5353.2 | 387.2 | 403.4 | 125.5 | 92.6 | 175.6
5986.2 | 5354.2 | 387.2 | 403.5 | 125.8 | 92.5 | 175.5
5987.2 | 5355.2 | 387.2 | 403.5 | 125.9 | 92.3 | 175.5
5988.2 | 5356.2 | 387.2 | 403.5 | 125.8 | 92.3 | 175.4
5989.2 | 5357.2 | 387.2 | 403.5 | 125.6 | 92.3 | 175.2
5990.2 | 5358.2 | 387.2 | 403.4 | 125.5 | 92.4 | 175.2
5991.2 | 5359.2 | 387.2 | 403.4 | 125.7 | 92.5 | 175.2
5992.2 | 5360.2 | 387.1 | 403.5 | 125.9 | 92.5 | 175.1
5993.2 | 5361.2 | 387.1 | 403.5 | 126 | 92.4 | 175
5994.2 | 5362.2 | 387.2 | 403.5 | 125.8 | 92.3 | 174.9
5995.2 | 5363.2 | 387.1 | 403.5 | 125.8 | 92.3 | 174.9
5996.2 | 5364.2 | 387.1 | 403.5 | 126.1 | 92.2 | 174.8
5997.2 | 5365.2 | 387.1 | 403.5 | 126 | 92.1 | 174.7
5998.2 | 5366.2 | 387.1 | 403.5 | 125.9 | 92 | 174.7
5999.2 | 5367.2 | 387.1 | 403.5 | 125.7 | 91.9 | 174.7
6000.2 | 5368.2 | 387.1 | 403.4 | 125.8 | 91.9 | 174.6
6001.2 | 5369.2 | 387.1 | 403.4 | 126.7 | 91.8 | 174.5
6002.2 | 5370.2 | 387.1 | 403.4 | 127.2 | 91.8 | 174.4
6003.2 | 5371.2 | 387.1 | 403.4 | 127 | 91.8 | 174.3
6004.2 | 5372.2 | 387.1 | 403.4 | 126.5 | 91.8 | 174.2
6005.2 | 5373.2 | 387.1 | 403.5 | 125.9 | 91.9 | 174.1
6006.2 | 5374.2 | 387.1 | 403.5 | 125.2 | 91.8 | 174
6007.2 | 5375.2 | 387.1 | 403.6 | 124.6 | 91.8 | 173.9
6008.2 | 5376.2 | 387.1 | 403.6 | 124 | 91.8 | 173.8
6009.2 | 5377.2 | 387.1 | 403.6 | 123.4 | 91.9 | 173.7
6010.2 | 5378.2 | 387.1 | 403.6 | 122.9 | 91.9 | 173.6
6011.2 | 5379.2 | 387.1 | 403.6 | 122.4 | 91.9 | 173.5
6012.2 | 5380.2 | 387.1 | 403.6 | 122 | 91.9 | 173.4
6013.2 | 5381.2 | 387.1 | 403.6 | 121.7 | 91.8 | 173.4
6014.2 | 5382.2 | 387.1 | 403.6 | 121.3 | 91.7 | 173.3
6015.2 | 5383.2 | 387.1 | 403.6 | 121 | 91.6 | 173.2
6016.2 | 5384.2 | 387.1 | 403.6 | 120.7 | 91.6 | 173.1
6017.2 | 5385.2 | 387 | 403.6 | 120.7 | 91.6 | 173
6018.2 | 5386.2 | 387 | 403.5 | 120.8 | 91.6 | 172.8
6019.2 | 5387.2 | 387 | 403.5 | 121.1 | 91.5 | 172.8
6020.2 | 5388.2 | 387 | 403.6 | 121.6 | 91.4 | 172.7
6021.2 | 5389.2 | 387 | 403.6 | 121.6 | 91.3 | 172.7
6022.2 | 5390.2 | 387 | 403.6 | 121.3 | 91.3 | 172.5
6023.2 | 5391.2 | 387 | 403.6 | 121.1 | 91.3 | 172.4
6024.2 | 5392.2 | 387 | 403.6 | 120.7 | 91.3 | 172.3
6025.2 | 5393.2 | 387 | 403.6 | 120.7 | 91.2 | 172.2
6026.2 | 5394.2 | 387 | 403.6 | 121.5 | 91.2 | 172.1
6027.2 | 5395.2 | 387 | 403.6 | 121.6 | 91.3 | 172.1
6028.2 | 5396.2 | 387 | 403.7 | 121.5 | 91.2 | 172
6029.2 | 5397.2 | 387 | 403.7 | 121.4 | 91.1 | 172
6030.2 | 5398.2 | 387 | 403.7 | 121 | 91.1 | 171.9
6031.2 | 5399.2 | 386.9 | 403.7 | 120.6 | 91.1 | 171.8
6032.2 | 5400.2 | 386.9 | 403.7 | 120.4 | 91.1 | 171.6
6033.2 | 5401.2 | 386.9 | 403.8 | 120.3 | 91.1 | 171.5
6034.2 | 5402.2 | 386.9 | 403.8 | 120 | 91 | 171.5
6035.2 | 5403.2 | 386.9 | 403.8 | 119.9 | 91 | 171.5
6036.2 | 5404.2 | 386.9 | 403.8 | 119.9 | 91 | 171.4
6037.2 | 5405.2 | 386.9 | 403.8 | 119.7 | 91 | 171.4
6038.2 | 5406.2 | 386.9 | 403.8 | 119.5 | 91 | 171.3
6039.2 | 5407.2 | 386.9 | 403.8 | 119.6 | 91 | 171.3
6040.2 | 5408.2 | 386.9 | 403.9 | 120.2 | 91 | 171.2
6041.2 | 5409.2 | 386.9 | 403.9 | 120.7 | 90.8 | 171.1
6042.2 | 5410.2 | 386.9 | 403.8 | 120.5 | 90.6 | 171
6043.2 | 5411.2 | 386.9 | 403.8 | 120.3 | 90.6 | 170.9
6044.2 | 5412.2 | 386.9 | 403.8 | 120 | 90.6 | 170.8
6045.2 | 5413.2 | 386.9 | 403.8 | 119.7 | 90.6 | 170.8
6046.2 | 5414.2 | 386.9 | 403.9 | 119.4 | 90.6 | 170.8
6047.2 | 5415.2 | 386.9 | 403.9 | 119.5 | 90.6 | 170.7
6048.2 | 5416.2 | 386.9 | 403.9 | 120.2 | 90.6 | 170.7
6049.2 | 5417.2 | 386.9 | 403.9 | 120.8 | 90.5 | 170.6
6050.2 | 5418.2 | 386.8 | 403.9 | 121.2 | 90.4 | 170.5
6051.2 | 5419.2 | 386.8 | 403.9 | 120.8 | 90.4 | 170.4
6052.2 | 5420.2 | 386.8 | 403.9 | 120.7 | 90.4 | 170.4
6053.2 | 5421.2 | 386.8 | 403.9 | 120.8 | 90.3 | 170.4
6054.2 | 5422.2 | 386.8 | 403.9 | 120.9 | 90.3 | 170.3
6055.2 | 5423.2 | 386.8 | 403.9 | 120.9 | 90.4 | 170.2
6056.2 | 5424.2 | 386.8 | 403.9 | 120.7 | 90.3 | 170.2
6057.2 | 5425.2 | 386.8 | 403.9 | 120.3 | 90.2 | 170.1
6058.2 | 5426.2 | 386.8 | 403.9 | 120 | 90.1 | 169.9
6059.2 | 5427.2 | 386.8 | 403.9 | 120.2 | 90.1 | 169.7
6060.2 | 5428.2 | 386.8 | 403.9 | 120.2 | 90.1 | 169.6
6061.2 | 5429.2 | 386.8 | 403.9 | 120.1 | 90.2 | 169.6
6062.2 | 5430.2 | 386.8 | 403.9 | 119.9 | 90.1 | 169.6
6063.2 | 5431.2 | 386.8 | 403.9 | 119.7 | 90.1 | 169.5
6064.2 | 5432.2 | 386.8 | 403.9 | 119.5 | 89.9 | 169.4
6065.2 | 5433.2 | 386.8 | 403.9 | 119.4 | 89.8 | 169.4
6066.2 | 5434.2 | 386.8 | 403.9 | 119.8 | 89.8 | 169.3
6067.2 | 5435.2 | 386.7 | 403.9 | 119.9 | 89.7 | 169.2
6068.2 | 5436.2 | 386.7 | 403.9 | 120.2 | 89.6 | 169.1
6069.2 | 5437.2 | 386.7 | 403.8 | 120.6 | 89.5 | 169
6070.2 | 5438.2 | 386.7 | 403.9 | 120.6 | 89.4 | 168.9
6071.2 | 5439.2 | 386.7 | 403.9 | 120.6 | 89.4 | 168.9
6072.2 | 5440.2 | 386.7 | 403.8 | 120.9 | 89.4 | 168.8
6073.2 | 5441.2 | 386.7 | 403.8 | 120.6 | 89.3 | 168.7
6074.2 | 5442.2 | 386.7 | 403.9 | 120.3 | 89.3 | 168.6
6075.2 | 5443.2 | 386.7 | 403.9 | 120 | 89.3 | 168.6
6076.2 | 5444.2 | 386.7 | 403.9 | 120.1 | 89.2 | 168.5
6077.2 | 5445.2 | 386.7 | 404 | 120.3 | 89.1 | 168.5
6078.2 | 5446.2 | 386.7 | 403.9 | 120.9 | 89 | 168.4
6079.2 | 5447.2 | 386.7 | 403.9 | 121.1 | 89.1 | 168.3
6080.2 | 5448.2 | 386.7 | 403.8 | 121.1 | 89 | 168.3
6081.2 | 5449.2 | 386.7 | 403.8 | 121.1 | 88.9 | 168.3
6082.2 | 5450.2 | 386.7 | 403.8 | 121 | 88.8 | 168.2
6083.2 | 5451.2 | 386.7 | 403.9 | 120.9 | 88.8 | 168.1
6084.2 | 5452.2 | 386.7 | 403.8 | 120.6 | 88.8 | 168
6085.2 | 5453.2 | 386.6 | 403.8 | 120.3 | 88.8 | 167.9
6086.2 | 5454.2 | 386.6 | 403.8 | 120 | 88.8 | 167.8
6087.2 | 5455.2 | 386.6 | 403.9 | 119.9 | 88.7 | 167.8
6088.2 | 5456.2 | 386.6 | 403.9 | 119.9 | 88.7 | 167.7
6089.2 | 5457.2 | 386.6 | 403.9 | 119.8 | 88.6 | 167.7
6090.2 | 5458.2 | 386.6 | 403.9 | 119.9 | 88.6 | 167.6
6091.2 | 5459.2 | 386.6 | 404 | 120.3 | 88.6 | 167.6
6092.2 | 5460.2 | 386.6 | 404 | 120.6 | 88.6 | 167.5
6093.2 | 5461.2 | 386.6 | 404 | 121.1 | 88.6 | 167.5
6094.2 | 5462.2 | 386.6 | 404 | 121.2 | 88.7 | 167.4
6095.2 | 5463.2 | 386.6 | 403.9 | 121.1 | 88.6 | 167.4
6096.2 | 5464.2 | 386.6 | 404 | 120.9 | 88.6 | 167.4
6097.2 | 5465.2 | 386.6 | 403.9 | 120.9 | 88.5 | 167.3
6098.2 | 5466.2 | 386.6 | 403.9 | 121.5 | 88.5 | 167.2
6099.2 | 5467.2 | 386.5 | 403.9 | 122.1 | 88.5 | 167.1
6100.2 | 5468.2 | 386.5 | 403.9 | 122.5 | 88.4 | 167.1
6101.2 | 5469.2 | 386.5 | 403.9 | 122.9 | 88.3 | 167
6102.2 | 5470.2 | 386.5 | 403.9 | 123.4 | 88.3 | 166.9
6103.2 | 5471.2 | 386.5 | 403.9 | 123.7 | 88.3 | 166.8
6104.2 | 5472.2 | 386.5 | 403.9 | 123.5 | 88.2 | 166.7
6105.2 | 5473.2 | 386.5 | 403.9 | 123.1 | 88.1 | 166.6
6106.2 | 5474.2 | 386.5 | 403.9 | 122.7 | 87.9 | 166.6
6107.2 | 5475.2 | 386.5 | 403.9 | 122.2 | 87.9 | 166.5
6108.2 | 5476.2 | 386.5 | 404 | 121.7 | 88 | 166.4
6109.2 | 5477.2 | 386.5 | 404 | 121.4 | 88 | 166.3
6110.2 | 5478.2 | 386.4 | 404 | 121.1 | 88 | 166.2
6111.2 | 5479.2 | 386.4 | 404 | 121 | 87.9 | 166.1
6112.2 | 5480.2 | 386.4 | 404 | 120.7 | 87.9 | 166
6113.2 | 5481.2 | 386.4 | 404.1 | 120.4 | 88 | 165.9
6114.2 | 5482.2 | 386.4 | 404.1 | 120 | 88.1 | 165.8
6115.2 | 5483.2 | 386.4 | 404.1 | 119.9 | 88.1 | 165.7
6116.2 | 5484.2 | 386.4 | 404.1 | 119.6 | 88.2 | 165.7
6117.2 | 5485.2 | 386.4 | 404.1 | 119.3 | 88.2 | 165.6
6118.2 | 5486.2 | 386.4 | 404.1 | 119 | 88.2 | 165.5
6119.2 | 5487.2 | 386.4 | 404.1 | 119.1 | 88.2 | 165.4
6120.2 | 5488.2 | 386.4 | 404.1 | 119.2 | 88.1 | 165.3
6121.2 | 5489.2 | 386.3 | 404.1 | 119.5 | 88 | 165.3
6122.2 | 5490.2 | 386.4 | 404.1 | 119.4 | 87.9 | 165.2
6123.2 | 5491.2 | 386.3 | 404.1 | 119.3 | 87.9 | 165.1
6124.2 | 5492.2 | 386.3 | 404.1 | 119.2 | 87.9 | 164.9
6125.2 | 5493.2 | 386.3 | 404.1 | 119.3 | 87.8 | 164.8
6126.2 | 5494.2 | 386.3 | 404.1 | 119 | 87.8 | 164.7
6127.2 | 5495.2 | 386.3 | 404.1 | 118.8 | 87.8 | 164.7
6128.2 | 5496.2 | 386.3 | 404.2 | 118.6 | 87.7 | 164.6
6129.2 | 5497.2 | 386.3 | 404.2 | 118.4 | 87.6 | 164.4
6130.2 | 5498.2 | 386.3 | 404.2 | 118.7 | 87.6 | 164.4
6131.2 | 5499.2 | 386.3 | 404.2 | 119.1 | 87.5 | 164.3
6132.2 | 5500.2 | 386.3 | 404.2 | 118.8 | 87.3 | 164.2
6133.2 | 5501.2 | 386.3 | 404.2 | 118.8 | 87.3 | 164.1
6134.2 | 5502.2 | 386.3 | 404.2 | 119.1 | 87.2 | 164
6135.2 | 5503.2 | 386.2 | 404.2 | 119.6 | 87.1 | 164
6136.2 | 5504.2 | 386.2 | 404.1 | 119.3 | 87.1 | 164
6137.2 | 5505.2 | 386.2 | 404.1 | 119.6 | 87.1 | 164
6138.2 | 5506.2 | 386.2 | 404.1 | 119.6 | 87 | 164
6139.2 | 5507.2 | 386.2 | 404.2 | 119.2 | 86.8 | 163.9
6140.2 | 5508.2 | 386.2 | 404.2 | 119.1 | 86.7 | 163.9
6141.2 | 5509.2 | 386.2 | 404.2 | 119.4 | 86.7 | 163.7
6142.2 | 5510.2 | 386.2 | 404.2 | 119.5 | 86.7 | 163.6
6143.2 | 5511.2 | 386.2 | 404.1 | 119.3 | 86.7 | 163.6
6144.2 | 5512.2 | 386.2 | 404.2 | 119 | 86.7 | 163.5
6145.2 | 5513.2 | 386.2 | 404.2 | 118.6 | 86.7 | 163.5
6146.2 | 5514.2 | 386.2 | 404.2 | 118.2 | 86.7 | 163.4
6147.2 | 5515.2 | 386.1 | 404.3 | 117.7 | 86.8 | 163.3
6148.2 | 5516.2 | 386.1 | 404.4 | 117.2 | 86.7 | 163.3
6149.2 | 5517.2 | 386.1 | 404.3 | 116.9 | 86.6 | 163.2
6150.2 | 5518.2 | 386.1 | 404.3 | 116.8 | 86.5 | 163.1
6151.2 | 5519.2 | 386.1 | 404.3 | 116.8 | 86.5 | 163
6152.2 | 5520.2 | 386.1 | 404.3 | 116.5 | 86.4 | 162.9
6153.2 | 5521.2 | 386.1 | 404.3 | 116.1 | 86.3 | 162.8
6154.2 | 5522.2 | 386.1 | 404.3 | 115.7 | 86.2 | 162.7
6155.2 | 5523.2 | 386.1 | 404.3 | 115.4 | 86.2 | 162.6
6156.2 | 5524.2 | 386.1 | 404.3 | 115.3 | 86.2 | 162.5
6157.2 | 5525.2 | 386.1 | 404.3 | 115.4 | 86.2 | 162.5
6158.2 | 5526.2 | 386.1 | 404.2 | 115.3 | 86.1 | 162.5
6159.2 | 5527.2 | 386.1 | 404.2 | 115.2 | 85.9 | 162.4
6160.2 | 5528.2 | 386.1 | 404.2 | 115.1 | 85.9 | 162.4
6161.2 | 5529.2 | 386.1 | 404.2 | 115.2 | 85.8 | 162.3
6162.2 | 5530.2 | 386.1 | 404.2 | 115.7 | 85.8 | 162.3
6163.2 | 5531.2 | 386.1 | 404.2 | 116.4 | 85.7 | 162.2
6164.2 | 5532.2 | 386 | 404.2 | 116.8 | 85.7 | 162.1
6165.2 | 5533.2 | 386 | 404.2 | 117.1 | 85.7 | 162
6166.2 | 5534.2 | 386 | 404.2 | 117.2 | 85.6 | 161.9
6167.2 | 5535.2 | 386 | 404.2 | 117.1 | 85.6 | 161.9
6168.2 | 5536.2 | 386 | 404.2 | 116.9 | 85.4 | 161.8
6169.2 | 5537.2 | 386 | 404.2 | 116.7 | 85.4 | 161.8
6170.2 | 5538.2 | 386 | 404.3 | 116.4 | 85.4 | 161.7
6171.2 | 5539.2 | 386 | 404.3 | 116.1 | 85.4 | 161.5
6172.2 | 5540.2 | 386 | 404.3 | 116.1 | 85.3 | 161.3
6173.2 | 5541.2 | 386 | 404.3 | 115.8 | 85.4 | 161.3
6174.2 | 5542.2 | 385.9 | 404.3 | 115.7 | 85.4 | 161.3
6175.2 | 5543.2 | 385.9 | 404.3 | 115.6 | 85.4 | 161.3
6176.2 | 5544.2 | 385.9 | 404.4 | 115.6 | 85.2 | 161.2
6177.2 | 5545.2 | 385.9 | 404.3 | 115.7 | 85.2 | 161.1
6178.2 | 5546.2 | 385.9 | 404.3 | 115.9 | 85.2 | 161.1
6179.2 | 5547.2 | 385.9 | 404.2 | 116.1 | 85.2 | 161
6180.2 | 5548.2 | 385.9 | 404.2 | 116.3 | 85.2 | 161
6181.2 | 5549.2 | 385.9 | 404.3 | 116.3 | 85.1 | 160.9
6182.2 | 5550.2 | 385.9 | 404.3 | 116.1 | 85 | 160.8
6183.2 | 5551.2 | 385.8 | 404.3 | 115.9 | 85 | 160.8
6184.2 | 5552.2 | 385.8 | 404.2 | 115.8 | 84.9 | 160.7
6185.2 | 5553.2 | 385.8 | 404.3 | 115.7 | 84.9 | 160.6
6186.2 | 5554.2 | 385.8 | 404.3 | 115.9 | 84.8 | 160.5
6187.2 | 5555.2 | 385.8 | 404.2 | 116.3 | 84.7 | 160.4
6188.2 | 5556.2 | 385.8 | 404.2 | 116.4 | 84.7 | 160.3
6189.2 | 5557.2 | 385.8 | 404.3 | 116.4 | 84.6 | 160.2
6190.2 | 5558.2 | 385.8 | 404.3 | 116.6 | 84.6 | 160.1
6191.2 | 5559.2 | 385.8 | 404.3 | 116.6 | 84.5 | 160
6192.2 | 5560.2 | 385.8 | 404.3 | 116.4 | 84.4 | 159.8
6193.2 | 5561.2 | 385.7 | 404.3 | 116.3 | 84.2 | 159.7
6194.2 | 5562.2 | 385.7 | 404.3 | 115.9 | 84.1 | 159.7
6195.2 | 5563.2 | 385.7 | 404.3 | 115.7 | 84.1 | 159.6
6196.2 | 5564.2 | 385.7 | 404.3 | 115.7 | 84 | 159.6
6197.2 | 5565.2 | 385.7 | 404.3 | 115.8 | 84 | 159.6
6198.2 | 5566.2 | 385.7 | 404.3 | 116.3 | 84 | 159.4
6199.2 | 5567.2 | 385.6 | 404.3 | 116.4 | 84 | 159.4
6200.2 | 5568.2 | 385.7 | 404.3 | 116.3 | 83.9 | 159.4
6201.2 | 5569.2 | 385.6 | 404.3 | 116.1 | 83.8 | 159.3
6202.2 | 5570.2 | 385.6 | 404.3 | 116.1 | 83.8 | 159.2
6203.2 | 5571.2 | 385.6 | 404.4 | 115.9 | 83.8 | 159.1
6204.2 | 5572.2 | 385.6 | 404.4 | 116 | 83.7 | 159
6205.2 | 5573.2 | 385.6 | 404.3 | 116.1 | 83.6 | 159
6206.2 | 5574.2 | 385.6 | 404.3 | 115.8 | 83.5 | 159
6207.2 | 5575.2 | 385.6 | 404.3 | 115.4 | 83.4 | 158.8
6208.2 | 5576.2 | 385.6 | 404.3 | 115.1 | 83.4 | 158.7
6209.2 | 5577.2 | 385.6 | 404.4 | 114.7 | 83.3 | 158.7
6210.2 | 5578.2 | 385.5 | 404.4 | 114.5 | 83.4 | 158.6
6211.2 | 5579.2 | 385.5 | 404.4 | 114.5 | 83.4 | 158.5
6212.2 | 5580.2 | 385.5 | 404.4 | 115 | 83.4 | 158.4
6213.2 | 5581.2 | 385.5 | 404.4 | 115.6 | 83.3 | 158.3
6214.2 | 5582.2 | 385.5 | 404.4 | 115.4 | 83.3 | 158.2
6215.2 | 5583.2 | 385.5 | 404.4 | 115.2 | 83.2 | 158.1
6216.2 | 5584.2 | 385.5 | 404.4 | 115 | 83 | 158
6217.2 | 5585.2 | 385.5 | 404.4 | 114.6 | 82.9 | 158
6218.2 | 5586.2 | 385.5 | 404.5 | 114.6 | 82.9 | 157.9
6219.2 | 5587.2 | 385.4 | 404.5 | 114.5 | 82.8 | 157.8
6220.2 | 5588.2 | 385.4 | 404.4 | 114.7 | 82.8 | 157.8
6221.2 | 5589.2 | 385.4 | 404.4 | 115.1 | 82.8 | 157.6
6222.2 | 5590.2 | 385.4 | 404.4 | 115.1 | 82.8 | 157.5
6223.2 | 5591.2 | 385.4 | 404.3 | 115 | 82.8 | 157.5
6224.2 | 5592.2 | 385.4 | 404.3 | 115.3 | 82.8 | 157.5
6225.2 | 5593.2 | 385.4 | 404.3 | 116 | 82.7 | 157.5
6226.2 | 5594.2 | 385.4 | 404.3 | 116.7 | 82.7 | 157.4
6227.2 | 5595.2 | 385.4 | 404.3 | 116.9 | 82.7 | 157.4
6228.2 | 5596.2 | 385.3 | 404.3 | 117 | 82.7 | 157.3
6229.2 | 5597.2 | 385.3 | 404.3 | 117.1 | 82.7 | 157.2
6230.2 | 5598.2 | 385.3 | 404.3 | 116.8 | 82.6 | 157.1
6231.2 | 5599.2 | 385.3 | 404.3 | 116.6 | 82.5 | 157.1
6232.2 | 5600.2 | 385.3 | 404.3 | 116.7 | 82.5 | 157.1
6233.2 | 5601.2 | 385.2 | 404.2 | 116.8 | 82.5 | 157
6234.2 | 5602.2 | 385.2 | 404.3 | 116.7 | 82.4 | 157
6235.2 | 5603.2 | 385.2 | 404.3 | 116.6 | 82.4 | 156.9
6236.2 | 5604.2 | 385.2 | 404.3 | 116.6 | 82.3 | 156.8
6237.2 | 5605.2 | 385.2 | 404.3 | 116.9 | 82.3 | 156.7
6238.2 | 5606.2 | 385.2 | 404.3 | 117.4 | 82.3 | 156.6
6239.2 | 5607.2 | 385.2 | 404.3 | 117.8 | 82.2 | 156.5
6240.2 | 5608.2 | 385.2 | 404.2 | 117.7 | 82.1 | 156.5
6241.2 | 5609.2 | 385.1 | 404.2 | 117.5 | 81.9 | 156.5
6242.2 | 5610.2 | 385.1 | 404.2 | 117.1 | 81.7 | 156.4
6243.2 | 5611.2 | 385.1 | 404.2 | 117.2 | 81.7 | 156.4
6244.2 | 5612.2 | 385.1 | 404.2 | 117.3 | 81.7 | 156.3
6245.2 | 5613.2 | 385.1 | 404.2 | 117.7 | 81.7 | 156.2
6246.2 | 5614.2 | 385.1 | 404.2 | 118 | 81.6 | 156
6247.2 | 5615.2 | 385 | 404.2 | 117.9 | 81.6 | 155.9
6248.2 | 5616.2 | 385 | 404.2 | 117.8 | 81.5 | 155.9
6249.2 | 5617.2 | 385 | 404.2 | 117.6 | 81.5 | 155.7
6250.2 | 5618.2 | 385 | 404.2 | 117 | 81.6 | 155.7
6251.2 | 5619.2 | 385 | 404.2 | 116.4 | 81.8 | 155.7
6252.2 | 5620.2 | 385 | 404.3 | 116 | 81.9 | 155.6
6253.2 | 5621.2 | 385 | 404.3 | 116 | 81.9 | 155.6
6254.2 | 5622.2 | 384.9 | 404.3 | 116.1 | 81.9 | 155.5
6255.2 | 5623.2 | 384.9 | 404.3 | 115.8 | 81.9 | 155.4
6256.2 | 5624.2 | 384.9 | 404.3 | 115.4 | 81.8 | 155.4
6257.2 | 5625.2 | 384.9 | 404.3 | 114.9 | 81.8 | 155.3
6258.2 | 5626.2 | 384.9 | 404.4 | 114.5 | 81.8 | 155.2
6259.2 | 5627.2 | 384.9 | 404.5 | 114 | 81.8 | 155.1
6260.2 | 5628.2 | 384.9 | 404.5 | 113.7 | 81.7 | 155
6261.2 | 5629.2 | 384.9 | 404.5 | 113.3 | 81.8 | 154.9
6262.2 | 5630.2 | 384.9 | 404.5 | 113 | 81.8 | 154.8
6263.2 | 5631.2 | 384.9 | 404.5 | 112.7 | 81.7 | 154.7
6264.2 | 5632.2 | 384.8 | 404.5 | 112.5 | 81.7 | 154.6
6265.2 | 5633.2 | 384.8 | 404.5 | 112.7 | 81.7 | 154.5
6266.2 | 5634.2 | 384.8 | 404.4 | 113.3 | 81.7 | 154.3
6267.2 | 5635.2 | 384.8 | 404.4 | 114 | 81.8 | 154.2
6268.2 | 5636.2 | 384.8 | 404.3 | 114.4 | 81.6 | 154
6269.2 | 5637.2 | 384.8 | 404.3 | 114.1 | 81.4 | 154
6270.2 | 5638.2 | 384.8 | 404.3 | 113.6 | 81.2 | 153.9
6271.2 | 5639.2 | 384.8 | 404.3 | 113.1 | 81.1 | 153.9
6272.2 | 5640.2 | 384.7 | 404.3 | 112.8 | 81.1 | 153.9
6273.2 | 5641.2 | 384.7 | 404.3 | 112.6 | 81.1 | 153.8
6274.2 | 5642.2 | 384.7 | 404.3 | 112.6 | 81.1 | 153.8
6275.2 | 5643.2 | 384.7 | 404.3 | 112.4 | 81.1 | 153.7
6276.2 | 5644.2 | 384.7 | 404.4 | 112.2 | 81 | 153.7
6277.2 | 5645.2 | 384.7 | 404.4 | 112.1 | 80.9 | 153.5
6278.2 | 5646.2 | 384.7 | 404.4 | 111.9 | 80.8 | 153.4
6279.2 | 5647.2 | 384.7 | 404.4 | 111.9 | 80.7 | 153.3
6280.2 | 5648.2 | 384.6 | 404.4 | 112.2 | 80.6 | 153.2
6281.2 | 5649.2 | 384.6 | 404.4 | 112.8 | 80.5 | 152.9
6282.2 | 5650.2 | 384.6 | 404.4 | 113.2 | 80.5 | 152.7
6283.2 | 5651.2 | 384.6 | 404.3 | 113.5 | 80.4 | 152.6
6284.2 | 5652.2 | 384.6 | 404.4 | 113.1 | 80.3 | 152.7
6285.2 | 5653.2 | 384.6 | 404.4 | 112.7 | 80.3 | 152.7
6286.2 | 5654.2 | 384.6 | 404.4 | 112.1 | 80.2 | 152.7
6287.2 | 5655.2 | 384.6 | 404.4 | 111.6 | 80.2 | 152.6
6288.2 | 5656.2 | 384.6 | 404.4 | 111.2 | 80.2 | 152.6
6289.2 | 5657.2 | 384.5 | 404.3 | 111 | 80.2 | 152.5
6290.2 | 5658.2 | 384.5 | 404.3 | 111.7 | 80.2 | 152.4
6291.2 | 5659.2 | 384.5 | 404.3 | 112.4 | 80.1 | 152.4
6292.2 | 5660.2 | 384.5 | 404.3 | 112.7 | 80.1 | 152.3
6293.2 | 5661.2 | 384.5 | 404.3 | 112.9 | 80.1 | 152.2
6294.2 | 5662.2 | 384.5 | 404.3 | 113.1 | 80 | 152.1
6295.2 | 5663.2 | 384.5 | 404.3 | 113.6 | 79.9 | 152.1
6296.2 | 5664.2 | 384.5 | 404.2 | 113.8 | 79.8 | 152
6297.2 | 5665.2 | 384.4 | 404.2 | 113.7 | 79.7 | 151.9
6298.2 | 5666.2 | 384.4 | 404.2 | 113.3 | 79.5 | 151.8
6299.2 | 5667.2 | 384.4 | 404.2 | 112.8 | 79.4 | 151.8
6300.2 | 5668.2 | 384.4 | 404.1 | 112.3 | 79.3 | 151.7
6301.2 | 5669.2 | 384.4 | 404.2 | 112.1 | 79.3 | 151.7
6302.2 | 5670.2 | 384.4 | 404.2 | 111.9 | 79.2 | 151.7
6303.2 | 5671.2 | 384.4 | 404.2 | 112.2 | 79.1 | 151.6
6304.2 | 5672.2 | 384.3 | 404.2 | 112.4 | 79 | 151.5
6305.2 | 5673.2 | 384.3 | 404.2 | 112.2 | 79 | 151.4
6306.2 | 5674.2 | 384.3 | 404.2 | 112 | 79.1 | 151.4
6307.2 | 5675.2 | 384.3 | 404.2 | 111.9 | 79.1 | 151.3
6308.2 | 5676.2 | 384.3 | 404.2 | 111.8 | 79.1 | 151.3
6309.2 | 5677.2 | 384.3 | 404.2 | 112 | 79.1 | 151.2
6310.2 | 5678.2 | 384.2 | 404.2 | 112.5 | 79.1 | 151.2
6311.2 | 5679.2 | 384.2 | 404.2 | 112.9 | 79.1 | 151.1
6312.2 | 5680.2 | 384.2 | 404.2 | 112.8 | 79.1 | 151.1
6313.2 | 5681.2 | 384.2 | 404.2 | 113.3 | 79.1 | 151
6314.2 | 5682.2 | 384.2 | 404.2 | 113.7 | 79.1 | 150.9
6315.2 | 5683.2 | 384.2 | 404.2 | 113.6 | 79 | 150.8
6316.2 | 5684.2 | 384.2 | 404.2 | 113.5 | 78.9 | 150.8
6317.2 | 5685.2 | 384.1 | 404.2 | 113.2 | 78.8 | 150.8
6318.2 | 5686.2 | 384.1 | 404.2 | 112.9 | 78.8 | 150.7
6319.2 | 5687.2 | 384.1 | 404.2 | 112.7 | 78.7 | 150.6
6320.2 | 5688.2 | 384.1 | 404.1 | 112.5 | 78.7 | 150.5
6321.2 | 5689.2 | 384.1 | 404.2 | 112.1 | 78.7 | 150.5
6322.2 | 5690.2 | 384.1 | 404.2 | 112.2 | 78.6 | 150.4
6323.2 | 5691.2 | 384 | 404.2 | 112.5 | 78.6 | 150.3
6324.2 | 5692.2 | 384 | 404.1 | 112.6 | 78.6 | 150.2
6325.2 | 5693.2 | 384 | 404.1 | 112.9 | 78.6 | 150.1
6326.2 | 5694.2 | 384 | 404.1 | 113 | 78.6 | 150.1
6327.2 | 5695.2 | 384 | 404.1 | 112.6 | 78.6 | 150
6328.2 | 5696.2 | 383.9 | 404.1 | 112.2 | 78.7 | 149.9
6329.2 | 5697.2 | 383.9 | 404.1 | 111.8 | 78.7 | 149.9
6330.2 | 5698.2 | 383.9 | 404.2 | 112 | 78.6 | 149.8
6331.2 | 5699.2 | 383.9 | 404.2 | 112.1 | 78.6 | 149.6
6332.2 | 5700.2 | 383.9 | 404.1 | 112.2 | 78.5 | 149.6
6333.2 | 5701.2 | 383.9 | 404.1 | 112.1 | 78.5 | 149.6
6334.2 | 5702.2 | 383.9 | 404.1 | 112 | 78.5 | 149.5
6335.2 | 5703.2 | 383.8 | 404.1 | 111.6 | 78.4 | 149.4
6336.2 | 5704.2 | 383.8 | 404.1 | 111.2 | 78.4 | 149.3
6337.2 | 5705.2 | 383.8 | 404.1 | 110.8 | 78.4 | 149.2
6338.2 | 5706.2 | 383.8 | 404.1 | 110.5 | 78.5 | 149.1
6339.2 | 5707.2 | 383.8 | 404.1 | 110.3 | 78.5 | 149
6340.2 | 5708.2 | 383.8 | 404.1 | 110.8 | 78.4 | 149
6341.2 | 5709.2 | 383.7 | 404.1 | 111.1 | 78.3 | 148.9
6342.2 | 5710.2 | 383.7 | 404.1 | 111 | 78.2 | 148.8
6343.2 | 5711.2 | 383.7 | 404.1 | 110.7 | 78.2 | 148.8
6344.2 | 5712.2 | 383.7 | 404.1 | 110.5 | 78.2 | 148.8
6345.2 | 5713.2 | 383.7 | 404.1 | 110.2 | 78.2 | 148.7
6346.2 | 5714.2 | 383.7 | 404.1 | 109.9 | 78.3 | 148.6
6347.2 | 5715.2 | 383.7 | 404.1 | 109.6 | 78.5 | 148.6
6348.2 | 5716.2 | 383.6 | 404.1 | 109.9 | 78.6 | 148.5
6349.2 | 5717.2 | 383.6 | 404.2 | 110.2 | 78.6 | 148.3
6350.2 | 5718.2 | 383.6 | 404.2 | 110.6 | 78.6 | 148.2
6351.2 | 5719.2 | 383.6 | 404.1 | 110.9 | 78.6 | 148.2
6352.2 | 5720.2 | 383.6 | 404.1 | 110.9 | 78.6 | 148.1
6353.2 | 5721.2 | 383.5 | 404.1 | 111.3 | 78.5 | 148.1
6354.2 | 5722.2 | 383.5 | 404 | 111.2 | 78.4 | 148
6355.2 | 5723.2 | 383.5 | 404 | 111 | 78.5 | 148
6356.2 | 5724.2 | 383.5 | 404 | 111 | 78.4 | 147.9
6357.2 | 5725.2 | 383.5 | 404 | 110.9 | 78.4 | 147.8
6358.2 | 5726.2 | 383.5 | 404.1 | 110.7 | 78.5 | 147.8
6359.2 | 5727.2 | 383.4 | 404.1 | 110.3 | 78.5 | 147.8
6360.2 | 5728.2 | 383.4 | 404.1 | 110 | 78.5 | 147.7
6361.2 | 5729.2 | 383.4 | 404.1 | 109.7 | 78.5 | 147.7
6362.2 | 5730.2 | 383.4 | 404.1 | 109.4 | 78.4 | 147.6
6363.2 | 5731.2 | 383.4 | 404 | 109 | 78.4 | 147.6
6364.2 | 5732.2 | 383.4 | 404 | 108.9 | 78.5 | 147.5
6365.2 | 5733.2 | 383.3 | 404 | 109 | 78.4 | 147.4
6366.2 | 5734.2 | 383.3 | 404 | 109.5 | 78.3 | 147.2
6367.2 | 5735.2 | 383.3 | 403.9 | 110 | 78.2 | 147.1
6368.2 | 5736.2 | 383.3 | 403.9 | 110 | 78.1 | 147
6369.2 | 5737.2 | 383.3 | 403.9 | 109.9 | 78.1 | 147
6370.2 | 5738.2 | 383.2 | 403.9 | 109.8 | 78.2 | 146.9
6371.2 | 5739.2 | 383.2 | 403.9 | 109.5 | 78.2 | 146.7
6372.2 | 5740.2 | 383.2 | 403.9 | 109.2 | 78.2 | 146.6
6373.2 | 5741.2 | 383.2 | 403.9 | 109 | 78.2 | 146.6
6374.2 | 5742.2 | 383.1 | 403.8 | 109.3 | 78.2 | 146.6
6375.2 | 5743.2 | 383.1 | 403.8 | 109.1 | 78.3 | 146.5
6376.2 | 5744.2 | 383.1 | 403.8 | 108.8 | 78.3 | 146.5
6377.2 | 5745.2 | 383.1 | 403.8 | 108.5 | 78.2 | 146.4
6378.2 | 5746.2 | 383 | 403.8 | 108.6 | 78.2 | 146.3
6379.2 | 5747.2 | 383 | 403.8 | 109.1 | 78.3 | 146.2
6380.2 | 5748.2 | 383 | 403.8 | 109.8 | 78.2 | 146.2
6381.2 | 5749.2 | 383 | 403.8 | 110.1 | 78.1 | 146.1
6382.2 | 5750.2 | 383 | 403.7 | 110 | 78 | 146
6383.2 | 5751.2 | 382.9 | 403.7 | 110.2 | 77.9 | 146
6384.2 | 5752.2 | 382.9 | 403.7 | 110 | 77.9 | 145.9
6385.2 | 5753.2 | 382.9 | 403.7 | 110.2 | 77.8 | 145.8
6386.2 | 5754.2 | 382.8 | 403.6 | 110.7 | 77.8 | 145.6
6387.2 | 5755.2 | 382.8 | 403.6 | 111.3 | 77.9 | 145.6
6388.2 | 5756.2 | 382.8 | 403.6 | 111.5 | 77.9 | 145.5
6389.2 | 5757.2 | 382.8 | 403.6 | 111.9 | 77.8 | 145.3
6390.2 | 5758.2 | 382.8 | 403.6 | 111.7 | 77.7 | 145.1
6391.2 | 5759.2 | 382.7 | 403.7 | 111.4 | 77.6 | 144.9
6392.2 | 5760.2 | 382.7 | 403.7 | 111.4 | 77.5 | 144.8
6393.2 | 5761.2 | 382.7 | 403.6 | 111.6 | 77.6 | 144.7
6394.2 | 5762.2 | 382.7 | 403.5 | 111 | 77.7 | 144.7
6395.2 | 5763.2 | 382.6 | 403.6 | 110.7 | 77.6 | 144.7
6396.2 | 5764.2 | 382.6 | 403.5 | 110.1 | 77.4 | 144.7
6397.2 | 5765.2 | 382.6 | 403.5 | 109.8 | 77.4 | 144.6
6398.2 | 5766.2 | 382.6 | 403.5 | 109.7 | 77.4 | 144.5
6399.2 | 5767.2 | 382.5 | 403.4 | 110.1 | 77.4 | 144.4
6400.2 | 5768.2 | 382.5 | 403.4 | 110.4 | 77.3 | 144.4
6401.2 | 5769.2 | 382.5 | 403.4 | 110.2 | 77.3 | 144.3
6402.2 | 5770.2 | 382.5 | 403.4 | 109.8 | 77.2 | 144.2
6403.2 | 5771.2 | 382.5 | 403.4 | 109.6 | 77.1 | 144.2
6404.2 | 5772.2 | 382.4 | 403.4 | 109.4 | 77.1 | 144.1
6405.2 | 5773.2 | 382.4 | 403.5 | 109.2 | 77 | 144.1
6406.2 | 5774.2 | 382.4 | 403.5 | 109.1 | 77 | 143.9
6407.2 | 5775.2 | 382.4 | 403.5 | 108.8 | 76.9 | 143.8
6408.2 | 5776.2 | 382.3 | 403.4 | 108.5 | 76.8 | 143.7
6409.2 | 5777.2 | 382.3 | 403.4 | 108.5 | 76.7 | 143.7
6410.2 | 5778.2 | 382.3 | 403.4 | 108.9 | 76.7 | 143.7
6411.2 | 5779.2 | 382.3 | 403.4 | 109.1 | 76.6 | 143.6
6412.2 | 5780.2 | 382.2 | 403.3 | 108.9 | 76.6 | 143.5
6413.2 | 5781.2 | 382.2 | 403.3 | 108.6 | 76.5 | 143.5
6414.2 | 5782.2 | 382.2 | 403.3 | 108.5 | 76.5 | 143.4
6415.2 | 5783.2 | 382.2 | 403.2 | 108.9 | 76.4 | 143.4
6416.2 | 5784.2 | 382.1 | 403.2 | 109 | 76.3 | 143.3
6417.2 | 5785.2 | 382.1 | 403.2 | 108.8 | 76.3 | 143.3
6418.2 | 5786.2 | 382.1 | 403.2 | 108.8 | 76.3 | 143.2
6419.2 | 5787.2 | 382.1 | 403.2 | 108.7 | 76.3 | 143.2
6420.2 | 5788.2 | 382.1 | 403.2 | 109 | 76.4 | 143
6421.2 | 5789.2 | 382.1 | 403.2 | 109.1 | 76.3 | 142.9
6422.2 | 5790.2 | 382 | 403.2 | 109.3 | 76.3 | 142.9
6423.2 | 5791.2 | 382 | 403.2 | 109.2 | 76.3 | 142.8
6424.2 | 5792.2 | 382 | 403.2 | 109.9 | 76.2 | 142.8
6425.2 | 5793.2 | 381.9 | 403.1 | 110.1 | 76.1 | 142.7
6426.2 | 5794.2 | 381.9 | 403.1 | 110.1 | 76 | 142.7
6427.2 | 5795.2 | 381.9 | 403.1 | 109.8 | 75.9 | 142.6
6428.2 | 5796.2 | 381.9 | 403.1 | 109.4 | 75.9 | 142.6
6429.2 | 5797.2 | 381.9 | 403.1 | 109.1 | 75.8 | 142.5
6430.2 | 5798.2 | 381.8 | 403.1 | 108.7 | 75.8 | 142.4
6431.2 | 5799.2 | 381.8 | 403.1 | 108.5 | 75.7 | 142.4
6432.2 | 5800.2 | 381.8 | 403 | 108.6 | 75.7 | 142.3
6433.2 | 5801.2 | 381.8 | 403 | 108.7 | 75.6 | 142.2
6434.2 | 5802.2 | 381.8 | 403 | 108.6 | 75.5 | 142.2
6435.2 | 5803.2 | 381.7 | 403 | 108.4 | 75.5 | 142.2
6436.2 | 5804.2 | 381.7 | 402.9 | 108.1 | 75.4 | 142.1
6437.2 | 5805.2 | 381.7 | 403 | 107.7 | 75.4 | 141.9
6438.2 | 5806.2 | 381.7 | 403 | 107.5 | 75.4 | 141.8
6439.2 | 5807.2 | 381.6 | 402.9 | 107.3 | 75.3 | 141.8
6440.2 | 5808.2 | 381.6 | 402.9 | 107.5 | 75.3 | 141.8
6441.2 | 5809.2 | 381.6 | 402.9 | 107.8 | 75.3 | 141.8
6442.2 | 5810.2 | 381.6 | 402.9 | 107.9 | 75.3 | 141.7
6443.2 | 5811.2 | 381.5 | 402.9 | 107.7 | 75.3 | 141.6
6444.2 | 5812.2 | 381.5 | 402.9 | 107.5 | 75.3 | 141.4
6445.2 | 5813.2 | 381.5 | 402.9 | 107.4 | 75.4 | 141.4
6446.2 | 5814.2 | 381.5 | 402.9 | 107.6 | 75.4 | 141.2
6447.2 | 5815.2 | 381.5 | 402.9 | 107.6 | 75.4 | 141.1
6448.2 | 5816.2 | 381.4 | 402.9 | 107.3 | 75.5 | 141.1
6449.2 | 5817.2 | 381.4 | 402.9 | 107.5 | 75.5 | 141
6450.2 | 5818.2 | 381.4 | 402.9 | 107.7 | 75.6 | 141
6451.2 | 5819.2 | 381.4 | 402.8 | 107.5 | 75.6 | 140.9
6452.2 | 5820.2 | 381.3 | 402.8 | 107.6 | 75.7 | 140.8
6453.2 | 5821.2 | 381.3 | 402.8 | 108.1 | 75.8 | 140.8
6454.2 | 5822.2 | 381.3 | 402.8 | 108.5 | 75.7 | 140.7
6455.2 | 5823.2 | 381.3 | 402.7 | 108.7 | 75.7 | 140.7
6456.2 | 5824.2 | 381.2 | 402.7 | 109 | 75.7 | 140.7
6457.2 | 5825.2 | 381.2 | 402.6 | 108.8 | 75.7 | 140.6
6458.2 | 5826.2 | 381.2 | 402.6 | 108.8 | 75.7 | 140.6
6459.2 | 5827.2 | 381.2 | 402.6 | 108.6 | 75.6 | 140.5
6460.2 | 5828.2 | 381.1 | 402.6 | 108.7 | 75.6 | 140.5
6461.2 | 5829.2 | 381.1 | 402.6 | 108.9 | 75.7 | 140.4
6462.2 | 5830.2 | 381.1 | 402.6 | 109.2 | 75.7 | 140.3
6463.2 | 5831.2 | 381.1 | 402.5 | 109.1 | 75.5 | 140.3
6464.2 | 5832.2 | 381 | 402.5 | 108.7 | 75.4 | 140.2
6465.2 | 5833.2 | 381 | 402.5 | 108.3 | 75.3 | 140.1
6466.2 | 5834.2 | 381 | 402.5 | 108.3 | 75.2 | 140.1
6467.2 | 5835.2 | 381 | 402.5 | 108.3 | 75.1 | 140
6468.2 | 5836.2 | 381 | 402.5 | 108.1 | 75.1 | 139.9
6469.2 | 5837.2 | 380.9 | 402.5 | 107.8 | 75.2 | 139.9
6470.2 | 5838.2 | 380.9 | 402.5 | 107.5 | 75.2 | 139.8
6471.2 | 5839.2 | 380.9 | 402.4 | 107.8 | 75.1 | 139.8
6472.2 | 5840.2 | 380.8 | 402.4 | 108.3 | 75 | 139.7
6473.2 | 5841.2 | 380.8 | 402.4 | 108.6 | 75 | 139.7
6474.2 | 5842.2 | 380.8 | 402.3 | 109 | 75.1 | 139.6
6475.2 | 5843.2 | 380.8 | 402.3 | 109.1 | 75.1 | 139.6
6476.2 | 5844.2 | 380.7 | 402.4 | 109.2 | 75.1 | 139.5
6477.2 | 5845.2 | 380.7 | 402.4 | 109 | 75 | 139.5
6478.2 | 5846.2 | 380.7 | 402.4 | 109 | 74.9 | 139.4
6479.2 | 5847.2 | 380.6 | 402.3 | 109.3 | 74.9 | 139.4
6480.2 | 5848.2 | 380.6 | 402.3 | 109.4 | 74.9 | 139.3
6481.2 | 5849.2 | 380.6 | 402.2 | 109.5 | 74.9 | 139.2
6482.2 | 5850.2 | 380.6 | 402.2 | 109.2 | 74.9 | 139.2
6483.2 | 5851.2 | 380.5 | 402.2 | 108.8 | 74.9 | 139.2
6484.2 | 5852.2 | 380.5 | 402.2 | 108.4 | 74.9 | 139.1
6485.2 | 5853.2 | 380.5 | 402.2 | 108.1 | 74.8 | 139.1
6486.2 | 5854.2 | 380.4 | 402.2 | 107.9 | 74.8 | 139
6487.2 | 5855.2 | 380.4 | 402.2 | 108.1 | 74.8 | 138.9
6488.2 | 5856.2 | 380.4 | 402.2 | 108.2 | 74.7 | 138.9
6489.2 | 5857.2 | 380.4 | 402.2 | 108.5 | 74.7 | 138.8
6490.2 | 5858.2 | 380.3 | 402.2 | 108.5 | 74.6 | 138.8
6491.2 | 5859.2 | 380.3 | 402.2 | 108.3 | 74.6 | 138.7
6492.2 | 5860.2 | 380.3 | 402.1 | 107.9 | 74.4 | 138.6
6493.2 | 5861.2 | 380.2 | 402.1 | 107.4 | 74.3 | 138.5
6494.2 | 5862.2 | 380.2 | 402.1 | 106.9 | 74.3 | 138.4
6495.2 | 5863.2 | 380.2 | 402.2 | 106.9 | 74.3 | 138.3
6496.2 | 5864.2 | 380.2 | 402.2 | 106.5 | 74.2 | 138.2
6497.2 | 5865.2 | 380.2 | 402.2 | 106.3 | 74.2 | 138
6498.2 | 5866.2 | 380.1 | 402.2 | 106.7 | 74.2 | 137.9
6499.2 | 5867.2 | 380.1 | 402.2 | 107.2 | 74.3 | 137.9
6500.2 | 5868.2 | 380.1 | 402.2 | 107.5 | 74.3 | 137.8
6501.2 | 5869.2 | 380.1 | 402.1 | 107.5 | 74.2 | 137.7
6502.2 | 5870.2 | 380 | 402 | 107.5 | 74.1 | 137.7
6503.2 | 5871.2 | 380 | 402 | 107.2 | 74.1 | 137.6
6504.2 | 5872.2 | 380 | 402 | 106.8 | 74.1 | 137.6
6505.2 | 5873.2 | 380 | 402 | 106.7 | 74.1 | 137.6
6506.2 | 5874.2 | 379.9 | 402 | 106.9 | 74.1 | 137.5
6507.2 | 5875.2 | 379.9 | 401.9 | 107.3 | 74.1 | 137.4
6508.2 | 5876.2 | 379.9 | 401.8 | 107.8 | 74.1 | 137.3
6509.2 | 5877.2 | 379.9 | 401.8 | 108.3 | 74.1 | 137.2
6510.2 | 5878.2 | 379.8 | 401.8 | 108.3 | 74 | 137.2
6511.2 | 5879.2 | 379.8 | 401.8 | 108.2 | 74 | 137
6512.2 | 5880.2 | 379.8 | 401.8 | 107.8 | 73.9 | 136.9
6513.2 | 5881.2 | 379.7 | 401.8 | 107.2 | 73.8 | 136.8
6514.2 | 5882.2 | 379.7 | 401.8 | 106.7 | 73.7 | 136.7
6515.2 | 5883.2 | 379.7 | 401.8 | 106.3 | 73.6 | 136.6
6516.2 | 5884.2 | 379.7 | 401.7 | 105.7 | 73.6 | 136.6
6517.2 | 5885.2 | 379.6 | 401.8 | 105.3 | 73.6 | 136.5
6518.2 | 5886.2 | 379.6 | 401.8 | 104.9 | 73.5 | 136.5
6519.2 | 5887.2 | 379.6 | 401.8 | 104.9 | 73.4 | 136.5
6520.2 | 5888.2 | 379.6 | 401.8 | 104.9 | 73.4 | 136.4
6521.2 | 5889.2 | 379.5 | 401.8 | 105.3 | 73.3 | 136.3
6522.2 | 5890.2 | 379.5 | 401.8 | 105.6 | 73.3 | 136.3
6523.2 | 5891.2 | 379.5 | 401.7 | 105.5 | 73.2 | 136.2
6524.2 | 5892.2 | 379.5 | 401.7 | 105.2 | 73.2 | 136.2
6525.2 | 5893.2 | 379.4 | 401.7 | 104.8 | 73.3 | 136.1
6526.2 | 5894.2 | 379.4 | 401.7 | 104.7 | 73.4 | 136.1
6527.2 | 5895.2 | 379.4 | 401.7 | 105.1 | 73.4 | 136
6528.2 | 5896.2 | 379.4 | 401.7 | 105.5 | 73.4 | 135.9
6529.2 | 5897.2 | 379.3 | 401.7 | 105.9 | 73.4 | 135.8
6530.2 | 5898.2 | 379.3 | 401.7 | 105.8 | 73.3 | 135.7
6531.2 | 5899.2 | 379.3 | 401.7 | 105.4 | 73.3 | 135.6
6532.2 | 5900.2 | 379.2 | 401.7 | 105 | 73.3 | 135.5
6533.2 | 5901.2 | 379.2 | 401.7 | 104.7 | 73.3 | 135.4
6534.2 | 5902.2 | 379.2 | 401.7 | 104.6 | 73.2 | 135.3
6535.2 | 5903.2 | 379.2 | 401.7 | 104.2 | 73 | 135.3
6536.2 | 5904.2 | 379.2 | 401.6 | 104.1 | 72.9 | 135.3
6537.2 | 5905.2 | 379.1 | 401.6 | 104 | 72.9 | 135.3
6538.2 | 5906.2 | 379.1 | 401.6 | 103.8 | 72.8 | 135.2
6539.2 | 5907.2 | 379.1 | 401.6 | 103.8 | 72.7 | 135.2
6540.2 | 5908.2 | 379.1 | 401.5 | 103.9 | 72.6 | 135.2
6541.2 | 5909.2 | 379 | 401.5 | 104.2 | 72.5 | 135.1
6542.2 | 5910.2 | 379 | 401.4 | 104 | 72.5 | 135
6543.2 | 5911.2 | 379 | 401.4 | 103.7 | 72.6 | 134.9
6544.2 | 5912.2 | 379 | 401.4 | 103.3 | 72.7 | 134.9
6545.2 | 5913.2 | 378.9 | 401.4 | 103.1 | 72.7 | 134.8
6546.2 | 5914.2 | 378.9 | 401.4 | 102.9 | 72.7 | 134.7
6547.2 | 5915.2 | 378.9 | 401.4 | 103.1 | 72.8 | 134.6
6548.2 | 5916.2 | 378.9 | 401.4 | 103.4 | 72.8 | 134.6
6549.2 | 5917.2 | 378.9 | 401.4 | 103.4 | 72.7 | 134.4
6550.2 | 5918.2 | 378.8 | 401.4 | 103.7 | 72.6 | 134.2
6551.2 | 5919.2 | 378.8 | 401.3 | 103.6 | 72.6 | 134.2
6552.2 | 5920.2 | 378.8 | 401.4 | 103.4 | 72.6 | 134
6553.2 | 5921.2 | 378.7 | 401.4 | 103.4 | 72.6 | 134
6554.2 | 5922.2 | 378.7 | 401.4 | 103.5 | 72.5 | 133.9
6555.2 | 5923.2 | 378.7 | 401.3 | 103.6 | 72.5 | 133.8
6556.2 | 5924.2 | 378.7 | 401.3 | 103.5 | 72.5 | 133.7
6557.2 | 5925.2 | 378.6 | 401.2 | 103.2 | 72.5 | 133.6
6558.2 | 5926.2 | 378.6 | 401.2 | 102.8 | 72.5 | 133.6
6559.2 | 5927.2 | 378.6 | 401.2 | 102.5 | 72.6 | 133.6
6560.2 | 5928.2 | 378.6 | 401.3 | 102.2 | 72.5 | 133.5
6561.2 | 5929.2 | 378.5 | 401.3 | 102.1 | 72.4 | 133.4
6562.2 | 5930.2 | 378.5 | 401.2 | 102.6 | 72.3 | 133.3
6563.2 | 5931.2 | 378.5 | 401.2 | 102.8 | 72.3 | 133.3
6564.2 | 5932.2 | 378.4 | 401.2 | 102.9 | 72.2 | 133.2
6565.2 | 5933.2 | 378.4 | 401.1 | 103.4 | 72.1 | 133.2
6566.2 | 5934.2 | 378.4 | 401.1 | 104 | 71.9 | 133.2
6567.2 | 5935.2 | 378.4 | 401.1 | 104 | 71.8 | 133.1
6568.2 | 5936.2 | 378.3 | 401 | 104.2 | 71.8 | 133
6569.2 | 5937.2 | 378.3 | 401 | 104 | 71.8 | 132.9
6570.2 | 5938.2 | 378.3 | 400.9 | 103.9 | 71.8 | 132.9
6571.2 | 5939.2 | 378.2 | 400.9 | 103.5 | 71.8 | 132.9
6572.2 | 5940.2 | 378.2 | 400.9 | 103.3 | 71.7 | 132.9
6573.2 | 5941.2 | 378.2 | 400.9 | 103.4 | 71.6 | 132.8
6574.2 | 5942.2 | 378.2 | 400.9 | 103.7 | 71.5 | 132.8
6575.2 | 5943.2 | 378.1 | 400.9 | 103.8 | 71.4 | 132.7
6576.2 | 5944.2 | 378.1 | 400.9 | 104.2 | 71.4 | 132.6
6577.2 | 5945.2 | 378.1 | 400.8 | 103.9 | 71.5 | 132.5
6578.2 | 5946.2 | 378.1 | 400.8 | 103.5 | 71.6 | 132.5
6579.2 | 5947.2 | 378 | 400.9 | 103.3 | 71.6 | 132.4
6580.2 | 5948.2 | 378 | 400.9 | 103.5 | 71.6 | 132.2
6581.2 | 5949.2 | 378 | 400.9 | 103.4 | 71.6 | 132.1
6582.2 | 5950.2 | 377.9 | 400.8 | 103.5 | 71.7 | 132
6583.2 | 5951.2 | 377.9 | 400.8 | 103.7 | 71.7 | 132
6584.2 | 5952.2 | 377.9 | 400.7 | 103.6 | 71.6 | 131.9
6585.2 | 5953.2 | 377.9 | 400.7 | 103.1 | 71.4 | 131.9
6586.2 | 5954.2 | 377.8 | 400.7 | 102.6 | 71.3 | 131.8
6587.2 | 5955.2 | 377.8 | 400.7 | 102.1 | 71.2 | 131.8
6588.2 | 5956.2 | 377.8 | 400.7 | 101.9 | 71.1 | 131.7
6589.2 | 5957.2 | 377.7 | 400.7 | 102.2 | 71 | 131.6
6590.2 | 5958.2 | 377.7 | 400.6 | 102.3 | 71.1 | 131.5
6591.2 | 5959.2 | 377.7 | 400.6 | 102.4 | 71.1 | 131.4
6592.2 | 5960.2 | 377.7 | 400.6 | 102.3 | 71.1 | 131.2
6593.2 | 5961.2 | 377.6 | 400.5 | 102.2 | 71.1 | 131.2
6594.2 | 5962.2 | 377.6 | 400.5 | 101.8 | 71 | 131.1
6595.2 | 5963.2 | 377.6 | 400.5 | 101.4 | 71 | 131.1
6596.2 | 5964.2 | 377.6 | 400.6 | 101.1 | 70.9 | 131.1
6597.2 | 5965.2 | 377.5 | 400.6 | 101.6 | 70.9 | 131
6598.2 | 5966.2 | 377.5 | 400.5 | 102.2 | 70.8 | 131
6599.2 | 5967.2 | 377.5 | 400.5 | 102.4 | 70.8 | 130.9
6600.2 | 5968.2 | 377.4 | 400.5 | 102.5 | 70.7 | 130.8
6601.2 | 5969.2 | 377.4 | 400.5 | 102.7 | 70.6 | 130.6
6602.2 | 5970.2 | 377.4 | 400.5 | 103 | 70.7 | 130.5
6603.2 | 5971.2 | 377.4 | 400.5 | 103 | 70.7 | 130.5
6604.2 | 5972.2 | 377.3 | 400.5 | 103.1 | 70.6 | 130.4
6605.2 | 5973.2 | 377.3 | 400.5 | 102.8 | 70.6 | 130.4
6606.2 | 5974.2 | 377.3 | 400.4 | 102.4 | 70.5 | 130.3
6607.2 | 5975.2 | 377.2 | 400.4 | 102.3 | 70.5 | 130.3
6608.2 | 5976.2 | 377.2 | 400.4 | 102.4 | 70.5 | 130.2
6609.2 | 5977.2 | 377.2 | 400.3 | 102.2 | 70.6 | 130.2
6610.2 | 5978.2 | 377.2 | 400.3 | 102 | 70.7 | 130.1
6611.2 | 5979.2 | 377.1 | 400.3 | 101.8 | 70.7 | 130
6612.2 | 5980.2 | 377.1 | 400.3 | 102.2 | 70.7 | 129.9
6613.2 | 5981.2 | 377.1 | 400.3 | 102.4 | 70.7 | 129.9
6614.2 | 5982.2 | 377.1 | 400.3 | 102.5 | 70.6 | 129.8
6615.2 | 5983.2 | 377 | 400.3 | 102.9 | 70.6 | 129.8
6616.2 | 5984.2 | 377 | 400.3 | 102.8 | 70.5 | 129.7
6617.2 | 5985.2 | 376.9 | 400.3 | 102.8 | 70.5 | 129.6
6618.2 | 5986.2 | 376.9 | 400.3 | 103.1 | 70.5 | 129.4
6619.2 | 5987.2 | 376.9 | 400.2 | 103.5 | 70.4 | 129.3
6620.2 | 5988.2 | 376.9 | 400.2 | 103.8 | 70.4 | 129.3
6621.2 | 5989.2 | 376.8 | 400.1 | 103.8 | 70.4 | 129.2
6622.2 | 5990.2 | 376.8 | 400.1 | 103.4 | 70.3 | 129.1
6623.2 | 5991.2 | 376.8 | 400.1 | 103 | 70.3 | 129.1
6624.2 | 5992.2 | 376.7 | 400.1 | 102.5 | 70.3 | 128.9
6625.2 | 5993.2 | 376.7 | 400.1 | 102.1 | 70.3 | 128.9
6626.2 | 5994.2 | 376.7 | 400 | 101.8 | 70.3 | 128.9
6627.2 | 5995.2 | 376.6 | 400 | 101.5 | 70.3 | 128.9
6628.2 | 5996.2 | 376.6 | 400 | 101.3 | 70.2 | 128.9
6629.2 | 5997.2 | 376.6 | 400 | 101.2 | 70.2 | 128.8
6630.2 | 5998.2 | 376.5 | 399.9 | 101.3 | 70.2 | 128.7
6631.2 | 5999.2 | 376.5 | 399.9 | 101.7 | 70.2 | 128.6
6632.2 | 6000.2 | 376.5 | 399.9 | 101.9 | 70.1 | 128.6
6633.2 | 6001.2 | 376.4 | 399.8 | 102.1 | 70 | 128.5
6634.2 | 6002.2 | 376.4 | 399.8 | 102.5 | 70.2 | 128.5
6635.2 | 6003.2 | 376.4 | 399.7 | 102.8 | 70.2 | 128.4
6636.2 | 6004.2 | 376.3 | 399.7 | 103.1 | 70.1 | 128.4
6637.2 | 6005.2 | 376.3 | 399.7 | 103 | 70.1 | 128.3
6638.2 | 6006.2 | 376.3 | 399.7 | 102.9 | 70 | 128.3
6639.2 | 6007.2 | 376.3 | 399.7 | 102.2 | 70 | 128.2
6640.2 | 6008.2 | 376.2 | 399.7 | 101.7 | 70 | 128.1
6641.2 | 6009.2 | 376.2 | 399.7 | 101.2 | 70.1 | 128
6642.2 | 6010.2 | 376.2 | 399.7 | 100.6 | 70.1 | 128
6643.2 | 6011.2 | 376.1 | 399.7 | 100 | 70.1 | 127.9
6644.2 | 6012.2 | 376.1 | 399.7 | 99.5 | 70.2 | 127.8
6645.2 | 6013.2 | 376.1 | 399.7 | 99 | 70.2 | 127.7
6646.2 | 6014.2 | 376 | 399.6 | 98.6 | 70.3 | 127.7
6647.2 | 6015.2 | 376 | 399.6 | 98.3 | 70.4 | 127.6
6648.2 | 6016.2 | 376 | 399.6 | 98.4 | 70.4 | 127.6
6649.2 | 6017.2 | 376 | 399.6 | 98.8 | 70.3 | 127.6
6650.2 | 6018.2 | 375.9 | 399.6 | 99.1 | 70.2 | 127.6
6651.2 | 6019.2 | 375.9 | 399.5 | 99 | 70 | 127.5
6652.2 | 6020.2 | 375.9 | 399.5 | 99 | 69.9 | 127.4
6653.2 | 6021.2 | 375.8 | 399.4 | 99.2 | 69.8 | 127.3
6654.2 | 6022.2 | 375.8 | 399.3 | 99.2 | 69.8 | 127.2
6655.2 | 6023.2 | 375.8 | 399.3 | 99.3 | 69.8 | 127.2
6656.2 | 6024.2 | 375.7 | 399.2 | 99.4 | 69.8 | 127.1
6657.2 | 6025.2 | 375.7 | 399.3 | 99.3 | 69.8 | 127.1
6658.2 | 6026.2 | 375.7 | 399.3 | 99.2 | 69.8 | 127
6659.2 | 6027.2 | 375.7 | 399.3 | 99.4 | 69.7 | 127
6660.2 | 6028.2 | 375.6 | 399.2 | 99.8 | 69.7 | 126.9
6661.2 | 6029.2 | 375.6 | 399.2 | 100 | 69.7 | 126.8
6662.2 | 6030.2 | 375.6 | 399.2 | 100.3 | 69.7 | 126.7
6663.2 | 6031.2 | 375.5 | 399.2 | 100.4 | 69.8 | 126.6
6664.2 | 6032.2 | 375.5 | 399.2 | 100.2 | 69.8 | 126.6
6665.2 | 6033.2 | 375.5 | 399.2 | 99.8 | 69.7 | 126.5
6666.2 | 6034.2 | 375.4 | 399.2 | 99.4 | 69.7 | 126.5
6667.2 | 6035.2 | 375.4 | 399.2 | 99.4 | 69.6 | 126.4
6668.2 | 6036.2 | 375.4 | 399.1 | 99.6 | 69.5 | 126.4
6669.2 | 6037.2 | 375.3 | 399.1 | 99.8 | 69.4 | 126.3
6670.2 | 6038.2 | 375.3 | 399.1 | 100.2 | 69.3 | 126.2
6671.2 | 6039.2 | 375.3 | 399 | 100.7 | 69.2 | 126.1
6672.2 | 6040.2 | 375.2 | 399 | 101 | 69.1 | 126.1
6673.2 | 6041.2 | 375.2 | 398.9 | 101.3 | 69.1 | 126
6674.2 | 6042.2 | 375.2 | 398.9 | 101.7 | 69.1 | 125.8
6675.2 | 6043.2 | 375.1 | 398.8 | 101.8 | 69 | 125.6
6676.2 | 6044.2 | 375.1 | 398.8 | 101.3 | 69 | 125.5
6677.2 | 6045.2 | 375.1 | 398.8 | 100.9 | 69 | 125.5
6678.2 | 6046.2 | 375 | 398.8 | 100.3 | 69 | 125.4
6679.2 | 6047.2 | 375 | 398.7 | 99.9 | 69.2 | 125.4
6680.2 | 6048.2 | 375 | 398.7 | 99.7 | 69.2 | 125.3
6681.2 | 6049.2 | 374.9 | 398.7 | 100.1 | 69.1 | 125.3
6682.2 | 6050.2 | 374.9 | 398.7 | 100.2 | 69.2 | 125.2
6683.2 | 6051.2 | 374.9 | 398.7 | 100.3 | 69.1 | 125.2
6684.2 | 6052.2 | 374.9 | 398.7 | 100.8 | 69.1 | 125.1
6685.2 | 6053.2 | 374.8 | 398.7 | 100.9 | 68.9 | 125.1
6686.2 | 6054.2 | 374.8 | 398.6 | 101.1 | 68.8 | 125
6687.2 | 6055.2 | 374.7 | 398.6 | 100.9 | 68.7 | 124.9
6688.2 | 6056.2 | 374.7 | 398.6 | 100.4 | 68.6 | 124.9
6689.2 | 6057.2 | 374.7 | 398.6 | 99.9 | 68.6 | 124.9
6690.2 | 6058.2 | 374.6 | 398.6 | 99.5 | 68.6 | 124.8
6691.2 | 6059.2 | 374.6 | 398.6 | 99.3 | 68.7 | 124.8
6692.2 | 6060.2 | 374.6 | 398.6 | 99 | 68.7 | 124.7
6693.2 | 6061.2 | 374.6 | 398.6 | 98.7 | 68.7 | 124.7
6694.2 | 6062.2 | 374.5 | 398.5 | 98.4 | 68.5 | 124.6
6695.2 | 6063.2 | 374.5 | 398.5 | 98.7 | 68.5 | 124.5
6696.2 | 6064.2 | 374.5 | 398.5 | 98.7 | 68.4 | 124.4
6697.2 | 6065.2 | 374.4 | 398.5 | 98.7 | 68.2 | 124.4
6698.2 | 6066.2 | 374.4 | 398.5 | 98.7 | 68.1 | 124.3
6699.2 | 6067.2 | 374.4 | 398.4 | 98.7 | 68 | 124.3
6700.2 | 6068.2 | 374.4 | 398.3 | 98.8 | 67.8 | 124.2
6701.2 | 6069.2 | 374.3 | 398.3 | 98.5 | 68 | 124.1
6702.2 | 6070.2 | 374.3 | 398.2 | 98.1 | 68.1 | 124
6703.2 | 6071.2 | 374.3 | 398.3 | 98 | 68.2 | 123.9
6704.2 | 6072.2 | 374.2 | 398.2 | 98.3 | 68.2 | 123.8
6705.2 | 6073.2 | 374.2 | 398.2 | 98.2 | 68.3 | 123.7
6706.2 | 6074.2 | 374.2 | 398.2 | 97.8 | 68.4 | 123.7
6707.2 | 6075.2 | 374.1 | 398.2 | 97.7 | 68.4 | 123.6
6708.2 | 6076.2 | 374.1 | 398.2 | 97.4 | 68.4 | 123.6
6709.2 | 6077.2 | 374.1 | 398.2 | 97.2 | 68.4 | 123.6
6710.2 | 6078.2 | 374.1 | 398.2 | 97.5 | 68.2 | 123.5
6711.2 | 6079.2 | 374 | 398.1 | 97.7 | 68.1 | 123.4
6712.2 | 6080.2 | 374 | 398.1 | 97.8 | 68.1 | 123.3
6713.2 | 6081.2 | 373.9 | 398 | 97.6 | 68.1 | 123.2
6714.2 | 6082.2 | 373.9 | 398 | 97.3 | 68.1 | 123.2
6715.2 | 6083.2 | 373.9 | 398 | 96.9 | 68 | 123.1
6716.2 | 6084.2 | 373.9 | 398 | 96.6 | 68.1 | 123.1
6717.2 | 6085.2 | 373.8 | 397.9 | 96.8 | 68.1 | 123
6718.2 | 6086.2 | 373.8 | 397.9 | 96.7 | 68.1 | 123.1
6719.2 | 6087.2 | 373.7 | 397.9 | 97.1 | 68 | 123
6720.2 | 6088.2 | 373.7 | 397.9 | 97.3 | 67.9 | 122.9
6721.2 | 6089.2 | 373.7 | 397.8 | 97.4 | 67.9 | 122.7
6722.2 | 6090.2 | 373.6 | 397.8 | 97.7 | 67.8 | 122.5
6723.2 | 6091.2 | 373.6 | 397.8 | 98.2 | 67.7 | 122.5
6724.2 | 6092.2 | 373.6 | 397.7 | 98.6 | 67.7 | 122.5
6725.2 | 6093.2 | 373.5 | 397.7 | 98.5 | 67.8 | 122.4
6726.2 | 6094.2 | 373.5 | 397.7 | 98.1 | 67.8 | 122.4
6727.2 | 6095.2 | 373.5 | 397.7 | 97.7 | 67.8 | 122.3
6728.2 | 6096.2 | 373.4 | 397.6 | 97.8 | 67.7 | 122.3
6729.2 | 6097.2 | 373.4 | 397.6 | 97.8 | 67.6 | 122.2
6730.2 | 6098.2 | 373.4 | 397.5 | 97.5 | 67.5 | 122.2
6731.2 | 6099.2 | 373.3 | 397.5 | 97.3 | 67.4 | 122.1
6732.2 | 6100.2 | 373.3 | 397.5 | 97.1 | 67.4 | 122
6733.2 | 6101.2 | 373.2 | 397.5 | 97 | 67.3 | 122
6734.2 | 6102.2 | 373.2 | 397.4 | 97.1 | 67.3 | 121.9
6735.2 | 6103.2 | 373.2 | 397.4 | 96.9 | 67.3 | 121.8
6736.2 | 6104.2 | 373.1 | 397.4 | 96.8 | 67.3 | 121.7
6737.2 | 6105.2 | 373.1 | 397.4 | 96.8 | 67.4 | 121.5
6738.2 | 6106.2 | 373.1 | 397.3 | 96.8 | 67.4 | 121.4
6739.2 | 6107.2 | 373 | 397.3 | 96.8 | 67.4 | 121.3
6740.2 | 6108.2 | 373 | 397.3 | 96.7 | 67.5 | 121.3
6741.2 | 6109.2 | 373 | 397.3 | 96.7 | 67.4 | 121.3
6742.2 | 6110.2 | 372.9 | 397.2 | 96.6 | 67.4 | 121.2
6743.2 | 6111.2 | 372.9 | 397.2 | 96.8 | 67.4 | 121.2
6744.2 | 6112.2 | 372.9 | 397.2 | 97.1 | 67.4 | 121.2
6745.2 | 6113.2 | 372.8 | 397.1 | 96.9 | 67.4 | 121.2
6746.2 | 6114.2 | 372.8 | 397.1 | 96.5 | 67.4 | 121.1
6747.2 | 6115.2 | 372.8 | 397.1 | 96.2 | 67.4 | 121.1
6748.2 | 6116.2 | 372.7 | 397.1 | 95.8 | 67.3 | 121.1
6749.2 | 6117.2 | 372.7 | 397.1 | 95.7 | 67.3 | 121
6750.2 | 6118.2 | 372.7 | 397.1 | 95.7 | 67.3 | 120.9
6751.2 | 6119.2 | 372.6 | 397 | 95.8 | 67.2 | 120.8
6752.2 | 6120.2 | 372.6 | 397 | 95.6 | 67.2 | 120.6
6753.2 | 6121.2 | 372.6 | 397 | 95.5 | 67.2 | 120.6
6754.2 | 6122.2 | 372.5 | 396.9 | 95.5 | 67.2 | 120.5
6755.2 | 6123.2 | 372.5 | 396.9 | 95.4 | 67.2 | 120.5
6756.2 | 6124.2 | 372.5 | 396.9 | 95.1 | 67.1 | 120.4
6757.2 | 6125.2 | 372.4 | 396.9 | 95.4 | 67.1 | 120.4
6758.2 | 6126.2 | 372.4 | 396.9 | 95.7 | 67 | 120.4
6759.2 | 6127.2 | 372.4 | 396.9 | 95.9 | 66.8 | 120.3
6760.2 | 6128.2 | 372.3 | 396.8 | 95.9 | 66.7 | 120.2
6761.2 | 6129.2 | 372.3 | 396.7 | 95.7 | 66.6 | 120.2
6762.2 | 6130.2 | 372.2 | 396.7 | 95.4 | 66.7 | 120.2
6763.2 | 6131.2 | 372.2 | 396.6 | 95 | 66.8 | 120.1
6764.2 | 6132.2 | 372.2 | 396.7 | 94.8 | 66.8 | 120.1
6765.2 | 6133.2 | 372.1 | 396.7 | 94.8 | 66.8 | 120
6766.2 | 6134.2 | 372.1 | 396.6 | 94.9 | 66.7 | 119.9
6767.2 | 6135.2 | 372.1 | 396.6 | 94.9 | 66.6 | 119.8
6768.2 | 6136.2 | 372 | 396.6 | 94.8 | 66.6 | 119.7
6769.2 | 6137.2 | 372 | 396.5 | 94.8 | 66.5 | 119.7
6770.2 | 6138.2 | 372 | 396.5 | 94.7 | 66.5 | 119.6
6771.2 | 6139.2 | 371.9 | 396.4 | 94.8 | 66.5 | 119.5
6772.2 | 6140.2 | 371.9 | 396.4 | 94.8 | 66.5 | 119.4
6773.2 | 6141.2 | 371.9 | 396.3 | 94.8 | 66.6 | 119.4
6774.2 | 6142.2 | 371.8 | 396.2 | 94.7 | 66.6 | 119.3
6775.2 | 6143.2 | 371.8 | 396.2 | 94.3 | 66.6 | 119.3
6776.2 | 6144.2 | 371.7 | 396.2 | 94.2 | 66.6 | 119.2
6777.2 | 6145.2 | 371.7 | 396.2 | 94.1 | 66.6 | 119.2
6778.2 | 6146.2 | 371.7 | 396.2 | 93.8 | 66.5 | 119.1
6779.2 | 6147.2 | 371.6 | 396.2 | 94 | 66.5 | 119
6780.2 | 6148.2 | 371.6 | 396.2 | 94.2 | 66.3 | 119
6781.2 | 6149.2 | 371.6 | 396.2 | 94.2 | 66.2 | 118.9
6782.2 | 6150.2 | 371.5 | 396.1 | 93.9 | 66.1 | 118.8
6783.2 | 6151.2 | 371.5 | 396.1 | 93.6 | 66 | 118.7
6784.2 | 6152.2 | 371.4 | 396 | 93.5 | 66.1 | 118.6
6785.2 | 6153.2 | 371.4 | 396 | 93.9 | 66.2 | 118.5
6786.2 | 6154.2 | 371.4 | 395.9 | 94 | 66.1 | 118.5
6787.2 | 6155.2 | 371.3 | 395.9 | 94.1 | 66.1 | 118.4
6788.2 | 6156.2 | 371.3 | 395.9 | 94 | 66.1 | 118.4
6789.2 | 6157.2 | 371.3 | 395.8 | 93.9 | 66.1 | 118.4
6790.2 | 6158.2 | 371.2 | 395.8 | 93.7 | 66 | 118.3
6791.2 | 6159.2 | 371.2 | 395.7 | 93.4 | 66 | 118.2
6792.2 | 6160.2 | 371.1 | 395.7 | 93.3 | 65.9 | 118.2
6793.2 | 6161.2 | 371.1 | 395.7 | 93.1 | 65.9 | 118.2
6794.2 | 6162.2 | 371.1 | 395.6 | 92.8 | 65.8 | 118.1
6795.2 | 6163.2 | 371 | 395.6 | 92.6 | 65.8 | 118.1
6796.2 | 6164.2 | 371 | 395.5 | 92.5 | 65.8 | 118
6797.2 | 6165.2 | 370.9 | 395.5 | 92.6 | 65.8 | 117.9
6798.2 | 6166.2 | 370.9 | 395.5 | 92.9 | 65.8 | 117.9
6799.2 | 6167.2 | 370.9 | 395.5 | 93 | 65.7 | 117.8
6800.2 | 6168.2 | 370.8 | 395.4 | 93 | 65.7 | 117.8
6801.2 | 6169.2 | 370.8 | 395.4 | 92.9 | 65.6 | 117.7
6802.2 | 6170.2 | 370.8 | 395.4 | 92.8 | 65.6 | 117.6
6803.2 | 6171.2 | 370.7 | 395.3 | 92.4 | 65.6 | 117.4
6804.2 | 6172.2 | 370.7 | 395.3 | 92 | 65.6 | 117.3
6805.2 | 6173.2 | 370.7 | 395.3 | 91.8 | 65.5 | 117.2
6806.2 | 6174.2 | 370.6 | 395.3 | 92.1 | 65.6 | 117.1
6807.2 | 6175.2 | 370.6 | 395.3 | 92.3 | 65.6 | 117
6808.2 | 6176.2 | 370.5 | 395.2 | 92.8 | 65.5 | 116.9
6809.2 | 6177.2 | 370.5 | 395.2 | 93.1 | 65.5 | 116.8
6810.2 | 6178.2 | 370.5 | 395.1 | 93.1 | 65.5 | 116.8
6811.2 | 6179.2 | 370.4 | 395.1 | 92.9 | 65.4 | 116.7
6812.2 | 6180.2 | 370.4 | 395.1 | 92.9 | 65.4 | 116.7
6813.2 | 6181.2 | 370.4 | 395 | 92.6 | 65.4 | 116.5
6814.2 | 6182.2 | 370.3 | 395 | 92.2 | 65.4 | 116.4
6815.2 | 6183.2 | 370.3 | 395 | 91.9 | 65.5 | 116.3
6816.2 | 6184.2 | 370.2 | 395 | 91.7 | 65.6 | 116.2
6817.2 | 6185.2 | 370.2 | 394.9 | 91.6 | 65.6 | 116.2
6818.2 | 6186.2 | 370.2 | 394.9 | 91.8 | 65.5 | 116.1
6819.2 | 6187.2 | 370.1 | 394.8 | 92.2 | 65.4 | 116.1
6820.2 | 6188.2 | 370.1 | 394.8 | 92.9 | 65.3 | 116.1
6821.2 | 6189.2 | 370 | 394.7 | 93.2 | 65.3 | 116
6822.2 | 6190.2 | 370 | 394.7 | 93.6 | 65.2 | 115.9
6823.2 | 6191.2 | 370 | 394.6 | 93.6 | 65.2 | 115.8
6824.2 | 6192.2 | 369.9 | 394.6 | 93.5 | 65.2 | 115.7
6825.2 | 6193.2 | 369.9 | 394.6 | 93.5 | 65.2 | 115.6
6826.2 | 6194.2 | 369.9 | 394.6 | 93.1 | 65.1 | 115.5
6827.2 | 6195.2 | 369.9 | 394.5 | 93.1 | 65 | 115.4
6828.2 | 6196.2 | 369.8 | 394.5 | 93.2 | 64.9 | 115.4
6829.2 | 6197.2 | 369.8 | 394.5 | 93.1 | 64.8 | 115.3
6830.2 | 6198.2 | 369.7 | 394.4 | 93 | 64.7 | 115.3
6831.2 | 6199.2 | 369.7 | 394.4 | 92.7 | 64.6 | 115.1
6832.2 | 6200.2 | 369.7 | 394.3 | 92.6 | 64.5 | 115.1
6833.2 | 6201.2 | 369.6 | 394.3 | 92.6 | 64.5 | 115
6834.2 | 6202.2 | 369.6 | 394.3 | 92.7 | 64.5 | 115
6835.2 | 6203.2 | 369.6 | 394.3 | 92.7 | 64.5 | 114.9
6836.2 | 6204.2 | 369.5 | 394.2 | 92.4 | 64.4 | 114.7
6837.2 | 6205.2 | 369.5 | 394.1 | 92 | 64.3 | 114.7
6838.2 | 6206.2 | 369.5 | 394.1 | 91.6 | 64.2 | 114.6
6839.2 | 6207.2 | 369.4 | 394.1 | 91.3 | 64.1 | 114.5
6840.2 | 6208.2 | 369.4 | 394 | 91.6 | 64.1 | 114.5
6841.2 | 6209.2 | 369.4 | 394 | 92 | 64.1 | 114.4
6842.2 | 6210.2 | 369.3 | 393.9 | 92.2 | 64 | 114.4
6843.2 | 6211.2 | 369.3 | 393.9 | 92.4 | 63.9 | 114.4
6844.2 | 6212.2 | 369.2 | 393.8 | 92.2 | 64 | 114.3
6845.2 | 6213.2 | 369.2 | 393.7 | 92.5 | 63.9 | 114.2
6846.2 | 6214.2 | 369.2 | 393.7 | 92.7 | 63.9 | 114.1
6847.2 | 6215.2 | 369.1 | 393.6 | 92.9 | 63.8 | 114.1
6848.2 | 6216.2 | 369.1 | 393.6 | 92.7 | 63.8 | 114
6849.2 | 6217.2 | 369 | 393.5 | 92.3 | 63.8 | 114
6850.2 | 6218.2 | 369 | 393.5 | 92.2 | 63.8 | 113.9
6851.2 | 6219.2 | 369 | 393.5 | 92 | 63.8 | 113.9
6852.2 | 6220.2 | 368.9 | 393.5 | 92.1 | 63.8 | 113.9
6853.2 | 6221.2 | 368.9 | 393.4 | 92 | 63.8 | 113.8
6854.2 | 6222.2 | 368.9 | 393.4 | 92 | 63.8 | 113.8
6855.2 | 6223.2 | 368.8 | 393.4 | 92.3 | 63.8 | 113.7
6856.2 | 6224.2 | 368.8 | 393.3 | 92.3 | 63.7 | 113.6
6857.2 | 6225.2 | 368.7 | 393.3 | 92.2 | 63.8 | 113.5
6858.2 | 6226.2 | 368.7 | 393.2 | 92.1 | 63.8 | 113.4
6859.2 | 6227.2 | 368.7 | 393.1 | 92.1 | 63.7 | 113.4
6860.2 | 6228.2 | 368.6 | 393.1 | 92.5 | 63.7 | 113.4
6861.2 | 6229.2 | 368.6 | 393.1 | 92.9 | 63.7 | 113.3
6862.2 | 6230.2 | 368.6 | 393 | 92.5 | 63.6 | 113.2
6863.2 | 6231.2 | 368.5 | 393 | 92.3 | 63.5 | 113.2
6864.2 | 6232.2 | 368.5 | 393 | 92 | 63.5 | 113.1
6865.2 | 6233.2 | 368.5 | 392.9 | 91.8 | 63.4 | 113
6866.2 | 6234.2 | 368.4 | 392.8 | 91.3 | 63.4 | 113
6867.2 | 6235.2 | 368.3 | 392.8 | 90.9 | 63.3 | 112.9
6868.2 | 6236.2 | 368.3 | 392.7 | 90.6 | 63.3 | 112.9
6869.2 | 6237.2 | 368.3 | 392.7 | 90.6 | 63.2 | 112.8
6870.2 | 6238.2 | 368.2 | 392.6 | 90.8 | 63.2 | 112.7
6871.2 | 6239.2 | 368.2 | 392.5 | 90.6 | 63.1 | 112.7
6872.2 | 6240.2 | 368.2 | 392.5 | 90.5 | 63 | 112.6
6873.2 | 6241.2 | 368.1 | 392.4 | 90.2 | 63 | 112.6
6874.2 | 6242.2 | 368.1 | 392.4 | 90.1 | 62.9 | 112.5
6875.2 | 6243.2 | 368 | 392.3 | 90.4 | 63 | 112.4
6876.2 | 6244.2 | 368 | 392.2 | 90.8 | 63 | 112.3
6877.2 | 6245.2 | 368 | 392.2 | 90.9 | 63 | 112.2
6878.2 | 6246.2 | 367.9 | 392.1 | 90.9 | 63 | 112.1
6879.2 | 6247.2 | 367.9 | 392 | 90.4 | 63.1 | 112
6880.2 | 6248.2 | 367.8 | 392 | 90 | 63.1 | 112
6881.2 | 6249.2 | 367.8 | 392 | 89.7 | 63 | 112
6882.2 | 6250.2 | 367.8 | 392 | 89.4 | 63 | 111.9
6883.2 | 6251.2 | 367.7 | 391.9 | 88.9 | 62.9 | 111.8
6884.2 | 6252.2 | 367.7 | 391.9 | 88.6 | 63 | 111.7
6885.2 | 6253.2 | 367.6 | 391.8 | 88.9 | 63.1 | 111.6
6886.2 | 6254.2 | 367.6 | 391.8 | 89.2 | 63.1 | 111.6
6887.2 | 6255.2 | 367.5 | 391.7 | 89.3 | 63.2 | 111.5
6888.2 | 6256.2 | 367.5 | 391.7 | 89.3 | 63.2 | 111.5
6889.2 | 6257.2 | 367.5 | 391.7 | 89.2 | 63.1 | 111.4
6890.2 | 6258.2 | 367.4 | 391.6 | 89.5 | 63.1 | 111.3
6891.2 | 6259.2 | 367.4 | 391.6 | 90 | 63 | 111.3
6892.2 | 6260.2 | 367.3 | 391.5 | 90.1 | 63 | 111.2
6893.2 | 6261.2 | 367.3 | 391.4 | 89.9 | 63 | 111.2
6894.2 | 6262.2 | 367.2 | 391.4 | 89.8 | 63.1 | 111.2
6895.2 | 6263.2 | 367.2 | 391.3 | 89.9 | 63.1 | 111.1
6896.2 | 6264.2 | 367.2 | 391.3 | 89.7 | 63.1 | 111.1
6897.2 | 6265.2 | 367.1 | 391.2 | 89.5 | 63.2 | 111
6898.2 | 6266.2 | 367.1 | 391.1 | 89.5 | 63.2 | 111
6899.2 | 6267.2 | 367 | 391.1 | 89.7 | 63.1 | 110.9
6900.2 | 6268.2 | 367 | 391 | 89.7 | 63.1 | 110.9
6901.2 | 6269.2 | 366.9 | 390.9 | 90 | 63.1 | 110.8
6902.2 | 6270.2 | 366.9 | 390.9 | 90.4 | 63.1 | 110.7
6903.2 | 6271.2 | 366.8 | 390.8 | 90.7 | 63 | 110.6
6904.2 | 6272.2 | 366.8 | 390.8 | 90.9 | 63 | 110.5
6905.2 | 6273.2 | 366.7 | 390.7 | 91.4 | 63 | 110.4
6906.2 | 6274.2 | 366.7 | 390.6 | 91.5 | 63 | 110.4
6907.2 | 6275.2 | 366.7 | 390.5 | 91.9 | 62.9 | 110.4
6908.2 | 6276.2 | 366.6 | 390.5 | 91.9 | 62.9 | 110.3
6909.2 | 6277.2 | 366.6 | 390.4 | 91.7 | 62.9 | 110.3
6910.2 | 6278.2 | 366.5 | 390.4 | 91.6 | 62.9 | 110.2
6911.2 | 6279.2 | 366.5 | 390.3 | 91.2 | 62.8 | 110.2
6912.2 | 6280.2 | 366.4 | 390.3 | 91 | 62.7 | 110.1
6913.2 | 6281.2 | 366.4 | 390.2 | 91.1 | 62.6 | 110.1
6914.2 | 6282.2 | 366.4 | 390.2 | 91.3 | 62.6 | 110
6915.2 | 6283.2 | 366.3 | 390.1 | 91.4 | 62.5 | 109.9
6916.2 | 6284.2 | 366.3 | 390 | 91.3 | 62.5 | 109.9
6917.2 | 6285.2 | 366.2 | 390 | 91 | 62.5 | 109.8
6918.2 | 6286.2 | 366.2 | 389.9 | 91.3 | 62.5 | 109.8
6919.2 | 6287.2 | 366.2 | 389.9 | 91.6 | 62.4 | 109.7
6920.2 | 6288.2 | 366.1 | 389.8 | 91.7 | 62.4 | 109.5
6921.2 | 6289.2 | 366.1 | 389.8 | 91.6 | 62.3 | 109.5
6922.2 | 6290.2 | 366 | 389.7 | 91.6 | 62.2 | 109.4
6923.2 | 6291.2 | 366 | 389.7 | 91.6 | 62.1 | 109.3
6924.2 | 6292.2 | 365.9 | 389.6 | 91.5 | 62.1 | 109.2
6925.2 | 6293.2 | 365.9 | 389.5 | 91.2 | 62 | 109.2
6926.2 | 6294.2 | 365.8 | 389.4 | 90.9 | 62.1 | 109.1
6927.2 | 6295.2 | 365.8 | 389.3 | 90.8 | 62.1 | 109.1
6928.2 | 6296.2 | 365.8 | 389.2 | 91 | 62.1 | 109
6929.2 | 6297.2 | 365.7 | 389.2 | 91.1 | 62.1 | 109
6930.2 | 6298.2 | 365.7 | 389.1 | 91.2 | 62 | 109
6931.2 | 6299.2 | 365.6 | 389 | 91 | 62.1 | 108.9
6932.2 | 6300.2 | 365.6 | 389 | 90.6 | 62.1 | 108.8
6933.2 | 6301.2 | 365.5 | 388.9 | 90.5 | 62.1 | 108.6
6934.2 | 6302.2 | 365.4 | 388.9 | 90.4 | 62.1 | 108.5
6935.2 | 6303.2 | 365.4 | 388.8 | 90.5 | 62 | 108.4
6936.2 | 6304.2 | 365.4 | 388.7 | 90.5 | 61.9 | 108.3
6937.2 | 6305.2 | 365.3 | 388.7 | 90.3 | 61.8 | 108.3
6938.2 | 6306.2 | 365.3 | 388.6 | 89.8 | 61.7 | 108.2
6939.2 | 6307.2 | 365.2 | 388.6 | 89.2 | 61.6 | 108.2
6940.2 | 6308.2 | 365.2 | 388.5 | 88.7 | 61.6 | 108.1
6941.2 | 6309.2 | 365.1 | 388.5 | 88.3 | 61.7 | 107.9
6942.2 | 6310.2 | 365.1 | 388.4 | 88.3 | 61.9 | 107.8
6943.2 | 6311.2 | 365.1 | 388.3 | 88.3 | 62.1 | 107.8
6944.2 | 6312.2 | 365 | 388.2 | 88.2 | 62.1 | 107.8
6945.2 | 6313.2 | 364.9 | 388.2 | 88.1 | 62 | 107.8
6946.2 | 6314.2 | 364.9 | 388.1 | 88.2 | 61.9 | 107.7
6947.2 | 6315.2 | 364.9 | 388 | 88.7 | 61.9 | 107.7
6948.2 | 6316.2 | 364.8 | 387.9 | 88.9 | 61.8 | 107.7

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 1 |  |  | 2006-10-19 | 9:13
39009.3768 | 1 | 0 | 1 | XLPE | 7-C | Tray G
39009.3786 | 1 | 0 | 1 |  | 200 kW |  | Bundle
39009.3807 | 1 | 0 | 1
39009.3825 | 1 | 0 | 1
39009.3842 | 0 | 0 | 1
39009.386 | 1 | 0 | 1
39009.3878 | 1 | 0 | 1
39009.3896 | 1 | 0 | 1
39009.3914 | 1 | 0 | 1
39009.3931 | 1 | 0 | 1
39009.3949 | 1 | 0 | 1
39009.3967 | 1 | 0 | 1
39009.3985 | 1 | 0 | 1
39009.4003 | 1 | 0 | 1
39009.4021 | 12 | 8 | 1
39009.4038 | 545 | 508 | 1
39009.4056 | 2003 | 0 | 1
39009.4074 | 2502 | 0 | 1
39009.4092 | 2608 | 0 | 1
39009.411 | 2256 | 0 | 1
39009.4128 | 2045 | 0 | 1
39009.4145 | 2183 | 0 | 1
39009.4163 | 2228 | 0 | 1
1
39009.3768 | 1 | 0 | 2
39009.3786 | 1 | 0 | 2
39009.3807 | 1 | 0 | 2
39009.3825 | 1 | 0 | 2
39009.3843 | 1 | 0 | 2
39009.386 | 1 | 0 | 2
39009.3878 | 1 | 0 | 2
39009.3896 | 1 | 0 | 2
39009.3914 | 1 | 0 | 2
39009.3932 | 2575 | 0 | 2
39009.3949 | 2200 | 0 | 2
39009.3967 | 2093 | 0 | 2
39009.3985 | 2036 | 0 | 2
39009.4003 | 5 | 3 | 2
39009.4021 | 2128 | 0 | 2
39009.4039 | 934 | 953 | 2
39009.4056 | 2361 | 0 | 2
39009.4074 | 2359 | 0 | 2
39009.4092 | 2469 | 0 | 2
39009.411 | 2504 | 0 | 2
39009.4128 | 2430 | 0 | 2
39009.4145 | 2500 | 0 | 2
39009.4163 | 2637 | 0 | 2
2
39009.3768 | 1 | 0 | 3
39009.3786 | 1 | 0 | 3
39009.3807 | 1 | 0 | 3
39009.3825 | 1 | 0 | 3
39009.3843 | 1 | 0 | 3
39009.3861 | 1 | 0 | 3
39009.3878 | 1 | 0 | 3
39009.3896 | 0 | 0 | 3
39009.3914 | 1 | 0 | 3
39009.3932 | 1 | 0 | 3
39009.395 | 1 | 0 | 3
39009.3967 | 1 | 0 | 3
39009.3985 | 1 | 0 | 3
39009.4003 | 1 | 0 | 3
39009.4021 | 26 | 0 | 3
39009.4039 | 55 | 15 | 3
39009.4057 | 2167 | 0 | 3
39009.4074 | 2539 | 0 | 3
39009.4092 | 2185 | 0 | 3
39009.411 | 2046 | 0 | 3
39009.4128 | 2395 | 0 | 3
39009.4146 | 2552 | 0 | 3
39009.4164 | 2563 | 0 | 3
3
39009.3769 | 1 | 0 | 4
39009.3786 | 1 | 0 | 4
39009.3807 | 1 | 0 | 4
39009.3825 | 1 | 0 | 4
39009.3843 | 1 | 0 | 4
39009.3861 | 1 | 0 | 4
39009.3878 | 1 | 0 | 4
39009.3896 | 1 | 0 | 4
39009.3914 | 1 | 0 | 4
39009.3932 | 0 | 0 | 4
39009.395 | 1 | 0 | 4
39009.3968 | 2073 | 0 | 4
39009.3985 | 2346 | 0 | 4
39009.4003 | 2 | 0 | 4
39009.4021 | 2602 | 0 | 4
39009.4039 | 38 | 36 | 4
39009.4057 | 2433 | 0 | 4
39009.4075 | 2156 | 0 | 4
39009.4092 | 2515 | 0 | 4
39009.411 | 2636 | 0 | 4
39009.4128 | 2217 | 0 | 4
39009.4146 | 2454 | 0 | 4
39009.4164 | 2569 | 0 | 4
4
39009.3769 | 1 | 0 | 5
39009.3787 | 1 | 0 | 5
39009.3807 | 1 | 0 | 5
39009.3825 | 1 | 0 | 5
39009.3843 | 1 | 0 | 5
39009.3861 | 1 | 0 | 5
39009.3879 | 1 | 0 | 5
39009.3897 | 1 | 0 | 5
39009.3914 | 0 | 0 | 5
39009.3932 | 1 | 0 | 5
39009.395 | 1 | 0 | 5
39009.3968 | 1 | 0 | 5
39009.3986 | 1 | 0 | 5
39009.4003 | 1 | 0 | 5
39009.4021 | 1017 | 908 | 5
39009.4039 | 1066 | 1123 | 5
39009.4057 | 2147 | 0 | 5
39009.4075 | 2203 | 0 | 5
39009.4092 | 2337 | 0 | 5
39009.411 | 2450 | 0 | 5
39009.4128 | 2206 | 0 | 5
39009.4146 | 2614 | 0 | 5
39009.4164 | 2525 | 0 | 5
5
39009.3769 | 1 | 0 | 6
39009.3787 | 1 | 0 | 6
39009.3808 | 1 | 0 | 6
39009.3825 | 1 | 0 | 6
39009.3843 | 1 | 0 | 6
39009.3861 | 1 | 0 | 6
39009.3879 | 1 | 0 | 6
39009.3897 | 1 | 0 | 6
39009.3914 | 1 | 0 | 6
39009.3932 | 1 | 0 | 6
39009.395 | 1 | 0 | 6
39009.3968 | 1 | 0 | 6
39009.3986 | 1 | 0 | 6
39009.4004 | 1 | 0 | 6
39009.4021 | 1111 | 1062 | 6
39009.4039 | 938 | 915 | 6
39009.4057 | 2001 | 0 | 6
39009.4075 | 2582 | 0 | 6
39009.4093 | 2249 | 0 | 6
39009.4111 | 2327 | 0 | 6
39009.4128 | 2475 | 0 | 6
39009.4146 | 2224 | 0 | 6
39009.4164 | 2253 | 0 | 6
6
39009.3769 | 1 | 0 | 7
39009.3787 | 1 | 0 | 7
39009.3808 | 1 | 0 | 7
39009.3826 | 1 | 0 | 7
39009.3843 | 1 | 0 | 7
39009.3861 | 1 | 0 | 7
39009.3879 | 1 | 0 | 7
39009.3897 | 1 | 0 | 7
39009.3915 | 1 | 0 | 7
39009.3933 | 1 | 0 | 7
39009.395 | 1 | 0 | 7
39009.3968 | 1 | 0 | 7
39009.3986 | 1 | 0 | 7
39009.4004 | 1 | 0 | 7
39009.4022 | 982 | 874 | 7
39009.4039 | 1036 | 987 | 7
39009.4057 | 2263 | 0 | 7
39009.4075 | 2161 | 0 | 7
39009.4093 | 2018 | 0 | 7
39009.4111 | 2451 | 0 | 7
39009.4128 | 2613 | 0 | 7
39009.4146 | 2214 | 0 | 7
39009.4164 | 2161 | 0 | 7
7
39009.3769 | 1 | 0 | 8
39009.3808 | 1 | 0 | 8
39009.3826 | 1 | 0 | 8
39009.3844 | 1 | 0 | 8
39009.3861 | 1 | 0 | 8
39009.3879 | 1 | 0 | 8
39009.3897 | 1 | 0 | 8
39009.3915 | 0 | 0 | 8
39009.3933 | 1 | 0 | 8
39009.395 | 1 | 0 | 8
39009.3968 | 1 | 0 | 8
39009.3986 | 1 | 0 | 8
39009.4004 | 1 | 0 | 8
39009.4022 | 1084 | 964 | 8
39009.404 | 973 | 927 | 8
39009.4057 | 2049 | 0 | 8
39009.4075 | 2531 | 0 | 8
39009.4093 | 2205 | 0 | 8
39009.4111 | 2233 | 0 | 8
39009.4129 | 2379 | 0 | 8
39009.4147 | 2047 | 0 | 8
39009.4164 | 2261 | 0 | 8
8
39009.3769 | 1 | 0 | 9
39009.3787 | 1 | 0 | 9
39009.3808 | 1 | 0 | 9
39009.3826 | 1 | 0 | 9
39009.3844 | 1 | 0 | 9
39009.3861 | 1 | 0 | 9
39009.3879 | 0 | 0 | 9
39009.3897 | 1 | 0 | 9
39009.3915 | 1 | 0 | 9
39009.3933 | 1 | 0 | 9
39009.3951 | 1 | 0 | 9
39009.3968 | 1 | 0 | 9
39009.3986 | 1 | 0 | 9
39009.4004 | 1 | 0 | 9
39009.4022 | 93 | 0 | 9
39009.404 | 50 | 17 | 9
39009.4058 | 2176 | 0 | 9
39009.4075 | 2295 | 0 | 9
39009.4093 | 2443 | 0 | 9
39009.4111 | 2054 | 0 | 9
39009.4129 | 2336 | 0 | 9
39009.4147 | 2599 | 0 | 9
39009.4164 | 2633 | 0 | 9
9
39009.377 | 1 | 0 | 10
39009.3787 | 1 | 0 | 10
39009.3808 | 1 | 0 | 10
39009.3826 | 1 | 0 | 10
39009.3844 | 1 | 0 | 10
39009.3862 | 1 | 0 | 10
39009.388 | 1 | 0 | 10
39009.3897 | 1 | 0 | 10
39009.3915 | 1 | 0 | 10
39009.3933 | 1 | 0 | 10
39009.3951 | 1 | 0 | 10
39009.3969 | 1 | 0 | 10
39009.3986 | 1 | 0 | 10
39009.4004 | 1 | 0 | 10
39009.4022 | 1 | 0 | 10
39009.404 | 37 | 14 | 10
39009.4058 | 2264 | 0 | 10
39009.4076 | 2140 | 0 | 10
39009.4093 | 2518 | 0 | 10
39009.4111 | 2376 | 0 | 10
39009.4129 | 2163 | 0 | 10
39009.4147 | 2058 | 0 | 10
39009.4165 | 2517 | 0 | 10
10
39009.377 | 1 | 0 | 11
39009.3788 | 1 | 0 | 11
39009.3808 | 1 | 0 | 11
39009.3826 | 1 | 0 | 11
39009.3844 | 1 | 0 | 11
39009.3862 | 1 | 0 | 11
39009.388 | 1 | 0 | 11
39009.3897 | 1 | 0 | 11
39009.3915 | 1 | 0 | 11
39009.3933 | 1 | 0 | 11
39009.3951 | 1 | 0 | 11
39009.3969 | 1 | 0 | 11
39009.3987 | 1 | 0 | 11
39009.4004 | 1 | 0 | 11
39009.4022 | 40 | 0 | 11
39009.404 | 13 | 0 | 11
39009.4058 | 2604 | 0 | 11
39009.4076 | 2483 | 0 | 11
39009.4094 | 2008 | 0 | 11
39009.4111 | 2025 | 0 | 11
39009.4129 | 2411 | 0 | 11
39009.4147 | 2160 | 0 | 11
39009.4165 | 2238 | 0 | 11
11
39009.377 | 1 | 0 | 12
39009.3788 | 1 | 0 | 12
39009.3809 | 1 | 0 | 12
39009.3826 | 1 | 0 | 12
39009.3844 | 1 | 0 | 12
39009.3862 | 1 | 0 | 12
39009.388 | 1 | 0 | 12
39009.3898 | 1 | 0 | 12
39009.3915 | 1 | 0 | 12
39009.3933 | 2521 | 0 | 12
39009.3951 | 2364 | 0 | 12
39009.3969 | 2489 | 0 | 12
39009.3987 | 2040 | 0 | 12
39009.4005 | 2555 | 0 | 12
39009.4022 | 2195 | 0 | 12
39009.404 | 2047 | 0 | 12
39009.4058 | 2513 | 0 | 12
39009.4076 | 2539 | 0 | 12
39009.4094 | 2381 | 0 | 12
39009.4111 | 2262 | 0 | 12
39009.4129 | 2458 | 1 | 12
39009.4147 | 2044 | 0 | 12
39009.4165 | 2444 | 0 | 12
12
39009.377 | 1 | 0 | 13
39009.3788 | 1 | 0 | 13
39009.3809 | 1 | 0 | 13
39009.3844 | 1 | 0 | 13
39009.3862 | 1 | 0 | 13
39009.388 | 1 | 0 | 13
39009.3898 | 1 | 0 | 13
39009.3916 | 1 | 0 | 13
39009.3933 | 1 | 0 | 13
39009.3951 | 1 | 0 | 13
39009.3969 | 1 | 0 | 13
39009.3987 | 1 | 0 | 13
39009.4005 | 1 | 0 | 13
39009.4023 | 43 | 0 | 13
39009.404 | 44 | 0 | 13
39009.4058 | 2255 | 0 | 13
39009.4076 | 2088 | 0 | 13
39009.4094 | 2115 | 0 | 13
39009.4112 | 2425 | 0 | 13
39009.413 | 2311 | 0 | 13
39009.4147 | 2214 | 0 | 13
39009.4165 | 2384 | 0 | 13
13
39009.377 | 1 | 0 | 14
39009.3788 | 1 | 0 | 14
39009.3809 | 1 | 0 | 14
39009.3827 | 1 | 0 | 14
39009.3844 | 1 | 0 | 14
39009.3862 | 0 | 0 | 14
39009.388 | 1 | 0 | 14
39009.3898 | 1 | 0 | 14
39009.3916 | 1 | 0 | 14
39009.3934 | 1 | 0 | 14
39009.3951 | 1 | 0 | 14
39009.3969 | 1 | 0 | 14
39009.3987 | 1 | 0 | 14
39009.4005 | 1 | 0 | 14
39009.4023 | 1 | 0 | 14
39009.4041 | 2383 | 0 | 14
39009.4058 | 2574 | 0 | 14
39009.4076 | 2581 | 0 | 14
39009.4094 | 2172 | 0 | 14
39009.4112 | 2298 | 0 | 14
39009.413 | 2182 | 0 | 14
39009.4147 | 2576 | 0 | 14
39009.4165 | 2392 | 0 | 14
14
39009.377 | 1 | 0 | 15
39009.3788 | 1 | 0 | 15
39009.3809 | 1 | 0 | 15
39009.3827 | 1 | 0 | 15
39009.3845 | 1 | 0 | 15
39009.3863 | 1 | 0 | 15
39009.388 | 1 | 0 | 15
39009.3898 | 1 | 0 | 15
39009.3916 | 1 | 0 | 15
39009.3934 | 0 | 0 | 15
39009.3952 | 1 | 0 | 15
39009.3969 | 1 | 0 | 15
39009.3987 | 1 | 0 | 15
39009.4005 | 1 | 0 | 15
39009.4023 | 43 | 0 | 15
39009.4041 | 49 | 0 | 15
39009.4058 | 2246 | 0 | 15
39009.4076 | 2071 | 0 | 15
39009.4094 | 2041 | 0 | 15
39009.4112 | 2110 | 0 | 15
39009.413 | 2577 | 0 | 15
39009.4148 | 2490 | 0 | 15
39009.4165 | 2615 | 0 | 15
15
39009.3771 | 1 | 0 | 16
39009.3788 | 1 | 0 | 16
39009.3809 | 1 | 0 | 16
39009.3827 | 1 | 0 | 16
39009.3845 | 1 | 0 | 16
39009.3863 | 1 | 0 | 16
39009.388 | 1 | 0 | 16
39009.3898 | 1 | 0 | 16
39009.3916 | 1 | 0 | 16
39009.3934 | 1 | 0 | 16
39009.3952 | 1 | 0 | 16
39009.397 | 1 | 0 | 16
39009.3987 | 1 | 0 | 16
39009.4005 | 0 | 0 | 16
39009.4023 | 1 | 0 | 16
39009.4041 | 2552 | 0 | 16
39009.4059 | 2482 | 0 | 16
39009.4077 | 2274 | 0 | 16
39009.4094 | 2106 | 0 | 16
39009.4112 | 2622 | 0 | 16
39009.413 | 2260 | 0 | 16
39009.4148 | 2483 | 0 | 16
39009.4166 | 2447 | 0 | 16
16
39009.3771 | 1 | 0 | 17
39009.3789 | 1 | 0 | 17
39009.3809 | 1 | 0 | 17
39009.3827 | 1 | 0 | 17
39009.3845 | 1 | 0 | 17
39009.3863 | 1 | 0 | 17
39009.3881 | 1 | 0 | 17
39009.3898 | 1 | 0 | 17
39009.3916 | 1 | 0 | 17
39009.3934 | 1 | 0 | 17
39009.3952 | 1 | 0 | 17
39009.397 | 1 | 0 | 17
39009.3988 | 1 | 0 | 17
39009.4005 | 1 | 1 | 17
39009.4023 | 45 | 0 | 17
39009.4041 | 1 | 0 | 17
39009.4059 | 2330 | 0 | 17
39009.4077 | 2346 | 0 | 17
39009.4094 | 2167 | 0 | 17
39009.4112 | 2220 | 0 | 17
39009.413 | 2161 | 0 | 17
39009.4148 | 2554 | 0 | 17
39009.4166 | 2134 | 0 | 17
17
39009.3771 | 1 | 0 | 18
39009.3789 | 1 | 0 | 18
39009.3809 | 1 | 0 | 18
39009.3827 | 1 | 0 | 18
39009.3845 | 1 | 0 | 18
39009.3863 | 1 | 0 | 18
39009.3881 | 1 | 0 | 18
39009.3899 | 1 | 0 | 18
39009.3916 | 1 | 0 | 18
39009.3934 | 1 | 0 | 18
39009.3952 | 1 | 0 | 18
39009.397 | 1 | 0 | 18
39009.3988 | 1 | 0 | 18
39009.4006 | 1 | 0 | 18
39009.4023 | 1 | 0 | 18
39009.4041 | 2091 | 0 | 18
39009.4059 | 2022 | 0 | 18
39009.4077 | 2479 | 0 | 18
39009.4095 | 2155 | 0 | 18
39009.4112 | 2184 | 0 | 18
39009.413 | 2509 | 0 | 18
39009.4148 | 2210 | 0 | 18
39009.4166 | 2007 | 0 | 18
18
39009.3771 | 1 | 0 | 19
39009.3789 | 1 | 0 | 19
39009.381 | 1 | 0 | 19
39009.3827 | 1 | 0 | 19
39009.3845 | 1 | 0 | 19
39009.3863 | 1 | 0 | 19
39009.3881 | 1 | 0 | 19
39009.3899 | 1 | 0 | 19
39009.3917 | 1 | 0 | 19
39009.3934 | 1 | 0 | 19
39009.3952 | 1 | 0 | 19
39009.397 | 1 | 0 | 19
39009.3988 | 1 | 0 | 19
39009.4006 | 1 | 0 | 19
39009.4023 | 49 | 0 | 19
39009.4041 | 1 | 0 | 19
39009.4059 | 1996 | 0 | 19
39009.4077 | 2364 | 0 | 19
39009.4095 | 2095 | 0 | 19
39009.4113 | 2140 | 0 | 19
39009.413 | 2536 | 0 | 19
39009.4148 | 2476 | 0 | 19
39009.4166 | 2176 | 0 | 19
19
39009.3771 | 1 | 0 | 20
39009.3789 | 1 | 0 | 20
39009.381 | 1 | 0 | 20
39009.3828 | 1 | 0 | 20
39009.3845 | 1 | 0 | 20
39009.3863 | 1 | 0 | 20
39009.3881 | 1 | 0 | 20
39009.3899 | 1 | 0 | 20
39009.3917 | 1 | 0 | 20
39009.3935 | 1 | 0 | 20
39009.3952 | 1 | 0 | 20
39009.397 | 1 | 0 | 20
39009.3988 | 1 | 0 | 20
39009.4006 | 1 | 0 | 20
39009.4024 | 1 | 0 | 20
39009.4042 | 1 | 0 | 20
39009.4059 | 2476 | 0 | 20
39009.4077 | 2440 | 0 | 20
39009.4095 | 2222 | 0 | 20
39009.4113 | 2289 | 0 | 20
39009.4131 | 2401 | 0 | 20
39009.4148 | 2211 | 0 | 20
39009.4166 | 2108 | 0 | 20
20
39009.3771 | 1 | 0 | 21
39009.3789 | 1 | 0 | 21
39009.381 | 1 | 0 | 21
39009.3828 | 1 | 0 | 21
39009.3846 | 1 | 0 | 21
39009.3863 | 1 | 0 | 21
39009.3881 | 1 | 0 | 21
39009.3899 | 1 | 0 | 21
39009.3917 | 1 | 0 | 21
39009.3935 | 2040 | 0 | 21
39009.3953 | 2251 | 0 | 21
39009.397 | 2003 | 0 | 21
39009.3988 | 2071 | 0 | 21
39009.4006 | 1991 | 0 | 21
39009.4024 | 1054 | 1027 | 21
39009.4042 | 958 | 912 | 21
39009.4059 | 2280 | 0 | 21
39009.4077 | 2303 | 0 | 21
39009.4095 | 2337 | 0 | 21
39009.4113 | 2383 | 0 | 21
39009.4131 | 2227 | 0 | 21
39009.4149 | 2421 | 0 | 21
39009.4166 | 2140 | 0 | 21
21
39009.3772 | 1 | 0 | 22
39009.3789 | 1 | 0 | 22
39009.381 | 1 | 0 | 22
39009.3828 | 1 | 0 | 22
39009.3846 | 0 | 0 | 22
39009.3864 | 1 | 0 | 22
39009.3881 | 1 | 0 | 22
39009.3899 | 1 | 0 | 22
39009.3917 | 1 | 0 | 22
39009.3935 | 1 | 0 | 22
39009.3953 | 1 | 0 | 22
39009.397 | 2474 | 0 | 22
39009.3988 | 2479 | 0 | 22
39009.4006 | 2410 | 0 | 22
39009.4024 | 1091 | 1142 | 22
39009.4042 | 1090 | 1040 | 22
39009.406 | 2184 | 0 | 22
39009.4077 | 2164 | 0 | 22
39009.4095 | 2547 | 0 | 22
39009.4113 | 2596 | 0 | 22
39009.4131 | 2473 | 0 | 22
39009.4149 | 2638 | 0 | 22
39009.4167 | 2474 | 0 | 22
22
39009.3772 | 1 | 0 | 23
39009.379 | 1 | 0 | 23
39009.381 | 0 | 0 | 23
39009.3828 | 1 | 0 | 23
39009.3846 | 1 | 0 | 23
39009.3864 | 1 | 0 | 23
39009.3882 | 1 | 0 | 23
39009.3899 | 1 | 0 | 23
39009.3917 | 1 | 0 | 23
39009.3935 | 1 | 0 | 23
39009.3953 | 1 | 0 | 23
39009.3971 | 2 | 0 | 23
39009.3989 | 1 | 0 | 23
39009.4006 | 1 | 0 | 23
39009.4024 | 1167 | 1186 | 23
39009.4042 | 1028 | 980 | 23
39009.406 | 2225 | 0 | 23
39009.4078 | 2613 | 0 | 23
39009.4095 | 2278 | 0 | 23
39009.4113 | 2178 | 0 | 23
39009.4131 | 2621 | 0 | 23
39009.4149 | 2043 | 0 | 23
39009.4167 | 2618 | 0 | 23
23
39009.3772 | 1 | 0 | 24
39009.379 | 1 | 0 | 24
39009.381 | 1 | 0 | 24
39009.3828 | 1 | 0 | 24
39009.3846 | 1 | 0 | 24
39009.3864 | 1 | 0 | 24
39009.3882 | 1 | 0 | 24
39009.39 | 1 | 0 | 24
39009.3917 | 1 | 0 | 24
39009.3935 | 2600 | 0 | 24
39009.3953 | 2015 | 0 | 24
39009.3971 | 2375 | 0 | 24
39009.3989 | 2529 | 0 | 24
39009.4006 | 2595 | 0 | 24
39009.4024 | 982 | 956 | 24
39009.4042 | 1166 | 1109 | 24
39009.406 | 2152 | 0 | 24
39009.4078 | 2042 | 0 | 24
39009.4096 | 2492 | 0 | 24
39009.4113 | 2162 | 0 | 24
39009.4131 | 2124 | 0 | 24
39009.4149 | 2152 | 0 | 24
39009.4167 | 2359 | 0 | 24
24
39009.3772 | 1 | 0 | 25
39009.379 | 1 | 0 | 25
39009.3811 | 1 | 0 | 25
39009.3828 | 1 | 0 | 25
39009.3846 | 0 | 0 | 25
39009.3864 | 1 | 0 | 25
39009.3882 | 1 | 0 | 25
39009.39 | 1 | 0 | 25
39009.3918 | 1 | 0 | 25
39009.3935 | 2498 | 0 | 25
39009.3953 | 2275 | 0 | 25
39009.3971 | 2461 | 0 | 25
39009.3989 | 2287 | 0 | 25
39009.4007 | 2535 | 0 | 25
39009.4025 | 46 | 42 | 25
39009.4042 | 1136 | 1156 | 25
39009.406 | 2373 | 0 | 25
39009.4078 | 2248 | 0 | 25
39009.4096 | 2007 | 0 | 25
39009.4114 | 2057 | 0 | 25
39009.4131 | 2040 | 0 | 25
39009.4149 | 2537 | 0 | 25
39009.4167 | 2559 | 0 | 25
25
39009.3772 | 1 | 0 | 26
39009.379 | 1 | 0 | 26
39009.3811 | 1 | 0 | 26
39009.3829 | 1 | 0 | 26
39009.3846 | 1 | 0 | 26
39009.3864 | 0 | 0 | 26
39009.3882 | 1 | 0 | 26
39009.39 | 1 | 0 | 26
39009.3918 | 1 | 0 | 26
39009.3936 | 1 | 0 | 26
39009.3953 | 1 | 0 | 26
39009.3971 | 1 | 0 | 26
39009.3989 | 1 | 0 | 26
39009.4007 | 1 | 0 | 26
39009.4025 | 44 | 35 | 26
39009.4042 | 1096 | 1035 | 26
39009.406 | 2236 | 0 | 26
39009.4078 | 2462 | 0 | 26
39009.4096 | 2149 | 0 | 26
39009.4114 | 2345 | 0 | 26
39009.4132 | 2483 | 0 | 26
39009.4149 | 2139 | 0 | 26
39009.4167 | 2558 | 0 | 26
26
39009.3772 | 0 | 0 | 27
39009.379 | 1 | 0 | 27
39009.3811 | 1 | 0 | 27
39009.3829 | 1 | 0 | 27
39009.3847 | 1 | 0 | 27
39009.3864 | 1 | 0 | 27
39009.3882 | 1 | 0 | 27
39009.39 | 1 | 0 | 27
39009.3918 | 1 | 0 | 27
39009.3936 | 2070 | 0 | 27
39009.3953 | 2195 | 0 | 27
39009.3971 | 2405 | 0 | 27
39009.3989 | 2008 | 0 | 27
39009.4007 | 2544 | 0 | 27
39009.4025 | 1 | 0 | 27
39009.4043 | 136 | 70 | 27
39009.406 | 2150 | 0 | 27
39009.4078 | 2206 | 0 | 27
39009.4096 | 2000 | 0 | 27
39009.4114 | 2442 | 0 | 27
39009.4132 | 2014 | 0 | 27
39009.415 | 2065 | 0 | 27
39009.4167 | 2053 | 0 | 27
27
39009.3772 | 1 | 0 | 28
39009.379 | 1 | 0 | 28
39009.3811 | 1 | 0 | 28
39009.3829 | 1 | 0 | 28
39009.3847 | 1 | 0 | 28
39009.3865 | 1 | 0 | 28
39009.3882 | 1 | 0 | 28
39009.39 | 1 | 0 | 28
39009.3918 | 1 | 0 | 28
39009.3936 | 1 | 0 | 28
39009.3954 | 1 | 0 | 28
39009.3972 | 1 | 0 | 28
39009.3989 | 1 | 0 | 28
39009.4007 | 1 | 0 | 28
39009.4025 | 1 | 0 | 28
39009.4043 | 92 | 78 | 28
39009.4061 | 2607 | 0 | 28
39009.4078 | 2046 | 1 | 28
39009.4096 | 2484 | 0 | 28
39009.4114 | 2288 | 0 | 28
39009.4132 | 2142 | 0 | 28
39009.415 | 2506 | 0 | 28
39009.4168 | 2309 | 0 | 28
28
39009.3773 | 1 | 0 | 29
39009.3791 | 1 | 0 | 29
39009.3811 | 1 | 0 | 29
39009.3829 | 1 | 0 | 29
39009.3847 | 1 | 0 | 29
39009.3865 | 1 | 0 | 29
39009.3883 | 1 | 0 | 29
39009.39 | 1 | 0 | 29
39009.3918 | 1 | 0 | 29
39009.3936 | 2211 | 0 | 29
39009.3954 | 2344 | 0 | 29
39009.3972 | 2569 | 0 | 29
39009.3989 | 2468 | 0 | 29
39009.4007 | 1997 | 0 | 29
39009.4025 | 1 | 0 | 29
39009.4043 | 1 | 0 | 29
39009.4061 | 2148 | 0 | 29
39009.4079 | 2483 | 0 | 29
39009.4096 | 2334 | 0 | 29
39009.4114 | 2426 | 0 | 29
39009.4132 | 2622 | 0 | 29
39009.415 | 2136 | 0 | 29
39009.4168 | 2066 | 0 | 29
29
39009.3773 | 1 | 0 | 30
39009.3791 | 1 | 0 | 30
39009.3811 | 1 | 0 | 30
39009.3829 | 1 | 0 | 30
39009.3847 | 1 | 0 | 30
39009.3865 | 1 | 0 | 30
39009.3883 | 1 | 0 | 30
39009.3901 | 1 | 0 | 30
39009.3918 | 1 | 0 | 30
39009.3936 | 2271 | 0 | 30
39009.3954 | 2549 | 0 | 30
39009.3972 | 2334 | 0 | 30
39009.399 | 2236 | 0 | 30
39009.4008 | 2587 | 0 | 30
39009.4025 | 2508 | 1 | 30
39009.4043 | 2210 | 0 | 30
39009.4061 | 2168 | 0 | 30
39009.4079 | 2467 | 0 | 30
39009.4097 | 2603 | 0 | 30
39009.4114 | 2642 | 0 | 30
39009.4132 | 2077 | 0 | 30
39009.415 | 2339 | 0 | 30
39009.4168 | 2455 | 0 | 30
30
39009.3773 | 1 | 0 | 31
39009.3791 | 1 | 0 | 31
39009.3812 | 1 | 0 | 31
39009.3829 | 1 | 0 | 31
39009.3847 | 1 | 0 | 31
39009.3865 | 1 | 0 | 31
39009.3883 | 1 | 0 | 31
39009.3901 | 1 | 0 | 31
39009.3919 | 1 | 0 | 31
39009.3936 | 2294 | 0 | 31
39009.3954 | 2453 | 0 | 31
39009.3972 | 2340 | 0 | 31
39009.399 | 2472 | 0 | 31
39009.4008 | 2575 | 0 | 31
39009.4025 | 1 | 0 | 31
39009.4043 | 1 | 0 | 31
39009.4061 | 2139 | 0 | 31
39009.4079 | 2098 | 0 | 31
39009.4097 | 2026 | 0 | 31
39009.4115 | 2625 | 0 | 31
39009.4132 | 2197 | 0 | 31
39009.415 | 2639 | 0 | 31
39009.4168 | 2121 | 0 | 31
31
39009.3773 | 1 | 0 | 32
39009.3791 | 1 | 0 | 32
39009.3812 | 1 | 0 | 32
39009.383 | 1 | 0 | 32
39009.3847 | 1 | 0 | 32
39009.3865 | 1 | 0 | 32
39009.3883 | 0 | 0 | 32
39009.3901 | 1 | 0 | 32
39009.3919 | 1 | 0 | 32
39009.3936 | 1 | 0 | 32
39009.3954 | 1 | 0 | 32
39009.3972 | 1 | 0 | 32
39009.399 | 1 | 0 | 32
39009.4008 | 1 | 0 | 32
39009.4026 | 2 | 0 | 32
39009.4043 | 2067 | 0 | 32
39009.4061 | 2331 | 0 | 32
39009.4079 | 2332 | 0 | 32
39009.4097 | 2595 | 0 | 32
39009.4115 | 2207 | 0 | 32
39009.4133 | 2343 | 0 | 32
39009.415 | 2297 | 0 | 32
39009.4168 | 2047 | 0 | 32
32
39009.3773 | 1 | 0 | 33
39009.3791 | 1 | 0 | 33
39009.3812 | 1 | 0 | 33
39009.383 | 1 | 0 | 33
39009.3848 | 1 | 0 | 33
39009.3865 | 1 | 0 | 33
39009.3883 | 1 | 0 | 33
39009.3901 | 1 | 0 | 33
39009.3919 | 1 | 0 | 33
39009.3937 | 2154 | 0 | 33
39009.3955 | 2003 | 0 | 33
39009.3972 | 2235 | 0 | 33
39009.399 | 2547 | 0 | 33
39009.4008 | 2505 | 0 | 33
39009.4026 | 1 | 0 | 33
39009.4044 | 1 | 0 | 33
39009.4061 | 2120 | 0 | 33
39009.4079 | 2060 | 0 | 33
39009.4097 | 2011 | 0 | 33
39009.4115 | 2137 | 0 | 33
39009.4133 | 2539 | 0 | 33
39009.4151 | 2429 | 0 | 33
39009.4168 | 2084 | 0 | 33
33
39009.3773 | 1 | 0 | 34
39009.3791 | 1 | 0 | 34
39009.3812 | 1 | 0 | 34
39009.383 | 1 | 0 | 34
39009.3848 | 1 | 0 | 34
39009.3866 | 1 | 0 | 34
39009.3883 | 1 | 0 | 34
39009.3901 | 1 | 0 | 34
39009.3919 | 1 | 0 | 34
39009.3937 | 1 | 0 | 34
39009.3955 | 1 | 0 | 34
39009.3972 | 1 | 0 | 34
39009.399 | 1 | 0 | 34
39009.4008 | 1 | 0 | 34
39009.4026 | 1 | 0 | 34
39009.4044 | 2108 | 0 | 34
39009.4062 | 2295 | 0 | 34
39009.4079 | 2314 | 0 | 34
39009.4097 | 2569 | 0 | 34
39009.4115 | 2461 | 0 | 34
39009.4133 | 2060 | 0 | 34
39009.4151 | 2620 | 0 | 34
39009.4169 | 2237 | 0 | 34
34
39009.3774 | 1 | 0 | 35
39009.3791 | 1 | 0 | 35
39009.3812 | 1 | 0 | 35
39009.383 | 1 | 0 | 35
39009.3848 | 1 | 0 | 35
39009.3866 | 1 | 0 | 35
39009.3884 | 1 | 0 | 35
39009.3901 | 1 | 0 | 35
39009.3919 | 1 | 0 | 35
39009.3937 | 2239 | 0 | 35
39009.3955 | 2603 | 0 | 35
39009.3973 | 2203 | 0 | 35
39009.3991 | 2052 | 0 | 35
39009.4008 | 2074 | 0 | 35
39009.4026 | 1 | 0 | 35
39009.4044 | 1 | 0 | 35
39009.4062 | 2167 | 0 | 35
39009.408 | 2180 | 0 | 35
39009.4097 | 2051 | 0 | 35
39009.4115 | 2548 | 0 | 35
39009.4133 | 2579 | 0 | 35
39009.4151 | 2172 | 0 | 35
39009.4169 | 2094 | 0 | 35
35
39009.3774 | 1 | 0 | 36
39009.3792 | 1 | 0 | 36
39009.3812 | 1 | 0 | 36
39009.383 | 0 | 0 | 36
39009.3848 | 1 | 0 | 36
39009.3866 | 1 | 0 | 36
39009.3884 | 1 | 0 | 36
39009.3902 | 1 | 0 | 36
39009.3919 | 1 | 0 | 36
39009.3937 | 1 | 0 | 36
39009.3955 | 1 | 0 | 36
39009.3973 | 1 | 0 | 36
39009.3991 | 1 | 0 | 36
39009.4008 | 1 | 0 | 36
39009.4026 | 1 | 0 | 36
39009.4044 | 2431 | 0 | 36
39009.4062 | 2154 | 0 | 36
39009.408 | 2578 | 0 | 36
39009.4098 | 2185 | 0 | 36
39009.4115 | 2567 | 0 | 36
39009.4133 | 2051 | 0 | 36
39009.4151 | 2316 | 0 | 36
39009.4169 | 2097 | 0 | 36
36
39009.3774 | 1 | 0 | 37
39009.3792 | 1 | 0 | 37
39009.3813 | 1 | 0 | 37
39009.383 | 1 | 0 | 37
39009.3848 | 1 | 0 | 37
39009.3866 | 1 | 0 | 37
39009.3884 | 1 | 0 | 37
39009.3902 | 1 | 0 | 37
39009.3919 | 1 | 0 | 37
39009.3937 | 2161 | 0 | 37
39009.3955 | 2165 | 0 | 37
39009.3973 | 2591 | 0 | 37
39009.3991 | 2305 | 0 | 37
39009.4009 | 2502 | 0 | 37
39009.4026 | 1 | 0 | 37
39009.4044 | 1 | 0 | 37
39009.4062 | 2001 | 0 | 37
39009.408 | 2036 | 0 | 37
39009.4098 | 2429 | 0 | 37
39009.4116 | 2241 | 0 | 37
39009.4133 | 2418 | 0 | 37
39009.4151 | 2183 | 0 | 37
39009.4169 | 2102 | 0 | 37
37
39009.3774 | 1 | 0 | 38
39009.3792 | 1 | 0 | 38
39009.3813 | 1 | 0 | 38
39009.3831 | 1 | 0 | 38
39009.3848 | 1 | 0 | 38
39009.3866 | 1 | 0 | 38
39009.3884 | 1 | 0 | 38
39009.3902 | 1 | 0 | 38
39009.392 | 1 | 0 | 38
39009.3938 | 2 | 0 | 38
39009.3955 | 1 | 0 | 38
39009.3973 | 1 | 0 | 38
39009.3991 | 1 | 0 | 38
39009.4009 | 1 | 0 | 38
39009.4027 | 1 | 0 | 38
39009.4044 | 1 | 0 | 38
39009.4062 | 2532 | 0 | 38
39009.408 | 2518 | 0 | 38
39009.4098 | 2374 | 0 | 38
39009.4116 | 2189 | 0 | 38
39009.4134 | 2053 | 0 | 38
39009.4151 | 2180 | 0 | 38
39009.4169 | 2165 | 0 | 38
38
39009.3774 | 1 | 0 | 39
39009.3792 | 1 | 0 | 39
39009.3813 | 1 | 0 | 39
39009.3831 | 1 | 0 | 39
39009.3848 | 1 | 0 | 39
39009.3866 | 1 | 0 | 39
39009.3884 | 1 | 0 | 39
39009.3902 | 0 | 0 | 39
39009.392 | 1 | 0 | 39
39009.3938 | 1 | 0 | 39
39009.3955 | 1 | 0 | 39
39009.3973 | 2362 | 0 | 39
39009.3991 | 2522 | 0 | 39
39009.4009 | 2092 | 0 | 39
39009.4027 | 69 | 62 | 39
39009.4045 | 940 | 994 | 39
39009.4062 | 2061 | 0 | 39
39009.408 | 2614 | 0 | 39
39009.4098 | 2605 | 0 | 39
39009.4116 | 2450 | 0 | 39
39009.4134 | 2603 | 0 | 39
39009.4152 | 2434 | 0 | 39
39009.4169 | 2099 | 0 | 39
39
39009.3774 | 0 | 0 | 40
39009.3792 | 1 | 0 | 40
39009.3813 | 1 | 0 | 40
39009.3831 | 1 | 0 | 40
39009.3849 | 1 | 0 | 40
39009.3867 | 1 | 0 | 40
39009.3884 | 1 | 0 | 40
39009.3902 | 1 | 0 | 40
39009.392 | 1 | 0 | 40
39009.3938 | 1 | 0 | 40
39009.3956 | 1 | 0 | 40
39009.3973 | 1 | 0 | 40
39009.3991 | 1 | 0 | 40
39009.4009 | 1 | 0 | 40
39009.4027 | 88 | 76 | 40
39009.4045 | 972 | 977 | 40
39009.4063 | 2580 | 0 | 40
39009.408 | 2516 | 0 | 40
39009.4098 | 2140 | 0 | 40
39009.4116 | 2361 | 0 | 40
39009.4134 | 2104 | 0 | 40
39009.4152 | 2631 | 0 | 40
39009.4169 | 2130 | 0 | 40
40
39009.3775 | 1 | 0 | 41
39009.3792 | 1 | 0 | 41
39009.3813 | 1 | 0 | 41
39009.3831 | 1 | 0 | 41
39009.3849 | 1 | 0 | 41
39009.3867 | 1 | 0 | 41
39009.3884 | 1 | 0 | 41
39009.3902 | 1 | 0 | 41
39009.392 | 0 | 0 | 41
39009.3938 | 1 | 0 | 41
39009.3956 | 2528 | 0 | 41
39009.3974 | 2499 | 0 | 41
39009.3991 | 2511 | 0 | 41
39009.4009 | 2517 | 0 | 41
39009.4027 | 92 | 83 | 41
39009.4045 | 1122 | 1057 | 41
39009.4063 | 2269 | 0 | 41
39009.4081 | 2455 | 0 | 41
39009.4098 | 2453 | 0 | 41
39009.4116 | 2379 | 0 | 41
39009.4134 | 2028 | 0 | 41
39009.4152 | 2460 | 0 | 41
39009.417 | 2031 | 0 | 41
41
39009.3775 | 1 | 0 | 42
39009.3793 | 1 | 0 | 42
39009.3813 | 1 | 0 | 42
39009.3831 | 1 | 0 | 42
39009.3849 | 1 | 0 | 42
39009.3867 | 1 | 0 | 42
39009.3885 | 1 | 0 | 42
39009.3903 | 1 | 0 | 42
39009.392 | 1 | 0 | 42
39009.3938 | 1 | 0 | 42
39009.3956 | 1 | 0 | 42
39009.3974 | 1 | 0 | 42
39009.3992 | 1 | 0 | 42
39009.4009 | 1 | 0 | 42
39009.4027 | 100 | 92 | 42
39009.4045 | 1095 | 1108 | 42
39009.4063 | 2157 | 0 | 42
39009.4081 | 2004 | 0 | 42
39009.4098 | 2265 | 0 | 42
39009.4116 | 2194 | 0 | 42
39009.4134 | 2107 | 0 | 42
39009.4152 | 2583 | 0 | 42
39009.417 | 2500 | 0 | 42
42
39009.3775 | 1 | 0 | 43
39009.3793 | 1 | 0 | 43
39009.3814 | 1 | 0 | 43
39009.3831 | 1 | 0 | 43
39009.3849 | 1 | 0 | 43
39009.3867 | 1 | 0 | 43
39009.3885 | 1 | 0 | 43
39009.3903 | 0 | 0 | 43
39009.392 | 1 | 0 | 43
39009.3938 | 1 | 0 | 43
39009.3956 | 2241 | 0 | 43
39009.3974 | 2004 | 0 | 43
39009.3992 | 2162 | 0 | 43
39009.401 | 2564 | 0 | 43
39009.4027 | 1 | 0 | 43
39009.4045 | 1063 | 1002 | 43
39009.4063 | 2227 | 0 | 43
39009.4081 | 2166 | 0 | 43
39009.4099 | 2313 | 0 | 43
39009.4117 | 2018 | 0 | 43
39009.4134 | 2306 | 0 | 43
39009.4152 | 2211 | 0 | 43
39009.417 | 2616 | 0 | 43
43
39009.3775 | 1 | 0 | 44
39009.3793 | 1 | 0 | 44
39009.3814 | 1 | 0 | 44
39009.3831 | 1 | 0 | 44
39009.3849 | 1 | 0 | 44
39009.3867 | 1 | 0 | 44
39009.3885 | 1 | 0 | 44
39009.3903 | 1 | 0 | 44
39009.3921 | 1 | 0 | 44
39009.3938 | 1 | 0 | 44
39009.3956 | 1 | 0 | 44
39009.3974 | 1 | 0 | 44
39009.3992 | 1 | 0 | 44
39009.401 | 1 | 0 | 44
39009.4028 | 1 | 0 | 44
39009.4045 | 1116 | 1049 | 44
39009.4063 | 2552 | 0 | 44
39009.4081 | 2268 | 0 | 44
39009.4099 | 2024 | 0 | 44
39009.4117 | 2228 | 0 | 44
39009.4134 | 2147 | 0 | 44
39009.4152 | 2286 | 0 | 44
39009.417 | 2639 | 0 | 44
44
39009.3775 | 1 | 0 | 45
39009.3793 | 1 | 0 | 45
39009.3814 | 1 | 0 | 45
39009.3832 | 1 | 0 | 45
39009.385 | 1 | 0 | 45
39009.3867 | 1 | 0 | 45
39009.3885 | 1 | 0 | 45
39009.3903 | 1 | 0 | 45
39009.3921 | 1 | 0 | 45
39009.3939 | 1 | 0 | 45
39009.3956 | 2166 | 0 | 45
39009.3974 | 2232 | 0 | 45
39009.3992 | 2082 | 0 | 45
39009.401 | 2537 | 0 | 45
39009.4028 | 1 | 0 | 45
39009.4046 | 1 | 0 | 45
39009.4063 | 2019 | 0 | 45
39009.4081 | 2283 | 0 | 45
39009.4099 | 2514 | 0 | 45
39009.4117 | 2025 | 0 | 45
39009.4135 | 2277 | 0 | 45
39009.4152 | 2589 | 0 | 45
39009.417 | 2627 | 0 | 45
45
39009.3775 | 1 | 0 | 46
39009.3793 | 0 | 0 | 46
39009.3814 | 1 | 0 | 46
39009.3832 | 1 | 0 | 46
39009.385 | 1 | 0 | 46
39009.3867 | 1 | 0 | 46
39009.3885 | 1 | 0 | 46
39009.3903 | 1 | 0 | 46
39009.3921 | 2123 | 0 | 46
39009.3939 | 2412 | 0 | 46
39009.3957 | 2084 | 0 | 46
39009.3974 | 2259 | 0 | 46
39009.3992 | 2103 | 0 | 46
39009.401 | 2366 | 0 | 46
39009.4028 | 2544 | 0 | 46
39009.4046 | 1996 | 0 | 46
39009.4064 | 2279 | 0 | 46
39009.4081 | 2241 | 0 | 46
39009.4099 | 2135 | 0 | 46
39009.4117 | 2272 | 0 | 46
39009.4135 | 2494 | 0 | 46
39009.4153 | 2211 | 0 | 46
39009.417 | 2646 | 0 | 46
46
39009.3776 | 1 | 0 | 47
39009.3793 | 1 | 0 | 47
39009.3814 | 1 | 0 | 47
39009.3832 | 1 | 0 | 47
39009.385 | 1 | 0 | 47
39009.3868 | 0 | 0 | 47
39009.3886 | 1 | 0 | 47
39009.3903 | 0 | 0 | 47
39009.3921 | 1 | 0 | 47
39009.3939 | 1 | 0 | 47
39009.3957 | 2610 | 0 | 47
39009.3975 | 2025 | 0 | 47
39009.3992 | 2176 | 0 | 47
39009.401 | 2606 | 0 | 47
39009.4028 | 1 | 0 | 47
39009.4046 | 16 | 0 | 47
39009.4064 | 2336 | 0 | 47
39009.4081 | 2578 | 0 | 47
39009.4099 | 2024 | 0 | 47
39009.4117 | 2174 | 0 | 47
39009.4135 | 2251 | 0 | 47
39009.4153 | 2155 | 0 | 47
39009.4171 | 2578 | 0 | 47
47
39009.3776 | 1 | 0 | 48
39009.3794 | 1 | 0 | 48
39009.3814 | 1 | 0 | 48
39009.3832 | 1 | 0 | 48
39009.385 | 1 | 0 | 48
39009.3868 | 1 | 0 | 48
39009.3886 | 1 | 0 | 48
39009.3903 | 1 | 0 | 48
39009.3921 | 1 | 0 | 48
39009.3939 | 1 | 0 | 48
39009.3957 | 1 | 0 | 48
39009.3975 | 1 | 0 | 48
39009.3993 | 1 | 0 | 48
39009.401 | 1 | 0 | 48
39009.4028 | 2 | 0 | 48
39009.4046 | 2541 | 0 | 48
39009.4064 | 2266 | 0 | 48
39009.4082 | 2085 | 0 | 48
39009.41 | 2018 | 0 | 48
39009.4117 | 2634 | 0 | 48
39009.4135 | 2072 | 0 | 48
39009.4153 | 2297 | 0 | 48
39009.4171 | 2573 | 0 | 48
48
39009.3776 | 1 | 0 | 49
39009.3794 | 1 | 0 | 49
39009.3814 | 1 | 0 | 49
39009.3832 | 1 | 0 | 49
39009.385 | 1 | 0 | 49
39009.3868 | 0 | 0 | 49
39009.3886 | 1 | 0 | 49
39009.3904 | 1 | 0 | 49
39009.3921 | 1 | 0 | 49
39009.3939 | 1 | 0 | 49
39009.3957 | 2477 | 0 | 49
39009.3975 | 2101 | 0 | 49
39009.3993 | 2268 | 0 | 49
39009.4011 | 2608 | 0 | 49
39009.4028 | 1 | 0 | 49
39009.4046 | 1 | 0 | 49
39009.4064 | 2004 | 0 | 49
39009.4082 | 2161 | 0 | 49
39009.41 | 2381 | 0 | 49
39009.4117 | 2097 | 0 | 49
39009.4135 | 2273 | 0 | 49
39009.4153 | 2136 | 0 | 49
39009.4171 | 2587 | 0 | 49
49
39009.3776 | 1 | 0 | 50
39009.3794 | 1 | 0 | 50
39009.3815 | 1 | 0 | 50
39009.3833 | 1 | 0 | 50
39009.385 | 1 | 0 | 50
39009.3868 | 1 | 0 | 50
39009.3886 | 1 | 0 | 50
39009.3904 | 1 | 0 | 50
39009.3922 | 1 | 0 | 50
39009.3939 | 1 | 0 | 50
39009.3957 | 1 | 0 | 50
39009.3975 | 1 | 0 | 50
39009.3993 | 2 | 0 | 50
39009.4011 | 1 | 0 | 50
39009.4029 | 1 | 0 | 50
39009.4046 | 2124 | 0 | 50
39009.4064 | 2253 | 0 | 50
39009.4082 | 2266 | 0 | 50
39009.41 | 2351 | 0 | 50
39009.4118 | 2349 | 0 | 50
39009.4135 | 2135 | 0 | 50
39009.4153 | 2145 | 0 | 50
39009.4171 | 2089 | 0 | 50
50
39009.3776 | 1 | 0 | 51
39009.3794 | 1 | 0 | 51
39009.3815 | 0 | 0 | 51
39009.3833 | 1 | 0 | 51
39009.385 | 1 | 0 | 51
39009.3868 | 1 | 0 | 51
39009.3886 | 1 | 0 | 51
39009.3904 | 1 | 0 | 51
39009.3922 | 1 | 0 | 51
39009.394 | 1 | 0 | 51
39009.3957 | 2583 | 0 | 51
39009.3975 | 2069 | 0 | 51
39009.3993 | 2090 | 0 | 51
39009.4011 | 2203 | 0 | 51
39009.4029 | 1 | 0 | 51
39009.4047 | 1 | 0 | 51
39009.4064 | 2596 | 0 | 51
39009.4082 | 2555 | 0 | 51
39009.41 | 2121 | 0 | 51
39009.4118 | 2047 | 0 | 51
39009.4136 | 2617 | 0 | 51
39009.4153 | 2097 | 0 | 51
39009.4171 | 2273 | 0 | 51
51
39009.3776 | 1 | 0 | 52
39009.3794 | 1 | 0 | 52
39009.3815 | 1 | 0 | 52
39009.3833 | 1 | 0 | 52
39009.3851 | 1 | 0 | 52
39009.3869 | 1 | 0 | 52
39009.3886 | 0 | 0 | 52
39009.3904 | 1 | 0 | 52
39009.3922 | 1 | 0 | 52
39009.394 | 1 | 0 | 52
39009.3958 | 1 | 0 | 52
39009.3975 | 2 | 0 | 52
39009.3993 | 1 | 0 | 52
39009.4011 | 1 | 0 | 52
39009.4029 | 0 | 0 | 52
39009.4047 | 2346 | 0 | 52
39009.4064 | 2246 | 0 | 52
39009.4082 | 2564 | 0 | 52
39009.41 | 2090 | 0 | 52
39009.4118 | 2626 | 0 | 52
39009.4136 | 2115 | 0 | 52
39009.4154 | 2359 | 0 | 52
39009.4171 | 2061 | 0 | 52
52
39009.3777 | 1 | 0 | 53
39009.3794 | 1 | 0 | 53
39009.3815 | 0 | 0 | 53
39009.3833 | 1 | 0 | 53
39009.3851 | 1 | 0 | 53
39009.3869 | 1 | 0 | 53
39009.3886 | 1 | 0 | 53
39009.3904 | 1 | 0 | 53
39009.3922 | 1 | 0 | 53
39009.394 | 1 | 0 | 53
39009.3958 | 2610 | 0 | 53
39009.3976 | 2093 | 0 | 53
39009.3993 | 1 | 0 | 53
39009.4011 | 2381 | 0 | 53
39009.4029 | 1 | 0 | 53
39009.4047 | 6 | 0 | 53
39009.4065 | 2577 | 0 | 53
39009.4083 | 2518 | 0 | 53
39009.41 | 2251 | 0 | 53
39009.4118 | 2583 | 0 | 53
39009.4136 | 2349 | 0 | 53
39009.4154 | 2456 | 0 | 53
39009.4172 | 2078 | 0 | 53
53
39009.3777 | 0 | 0 | 54
39009.3795 | 1 | 0 | 54
39009.3815 | 1 | 0 | 54
39009.3833 | 0 | 0 | 54
39009.3851 | 1 | 0 | 54
39009.3869 | 1 | 0 | 54
39009.3887 | 1 | 0 | 54
39009.3904 | 1 | 0 | 54
39009.3922 | 1 | 0 | 54
39009.394 | 1 | 0 | 54
39009.3958 | 1 | 0 | 54
39009.3976 | 1 | 0 | 54
39009.3994 | 0 | 0 | 54
39009.4011 | 1 | 0 | 54
39009.4029 | 1 | 0 | 54
39009.4047 | 377 | 0 | 54
39009.4065 | 2001 | 0 | 54
39009.4083 | 1976 | 0 | 54
39009.41 | 2255 | 0 | 54
39009.4118 | 1979 | 0 | 54
39009.4136 | 2049 | 0 | 54
39009.4154 | 2635 | 0 | 54
39009.4172 | 2603 | 0 | 54
54
39009.3777 | 1 | 0 | 55
39009.3795 | 0 | 0 | 55
39009.3816 | 1 | 0 | 55
39009.3833 | 1 | 0 | 55
39009.3851 | 1 | 0 | 55
39009.3869 | 1 | 0 | 55
39009.3887 | 1 | 0 | 55
39009.3905 | 922 | 976 | 55
39009.3922 | 1184 | 1201 | 55
39009.394 | 1136 | 1113 | 55
39009.3958 | 1113 | 1171 | 55
39009.3976 | 1119 | 1175 | 55
39009.3994 | 986 | 964 | 55
39009.4012 | 995 | 1092 | 55
39009.4029 | 935 | 911 | 55
39009.4047 | 992 | 931 | 55
39009.4065 | 2465 | 0 | 55
39009.4083 | 2530 | 0 | 55
39009.4101 | 2083 | 0 | 55
39009.4118 | 2021 | 0 | 55
39009.4136 | 2278 | 0 | 55
39009.4154 | 2487 | 0 | 55
39009.4172 | 2592 | 0 | 55
55
39009.3777 | 1 | 0 | 56
39009.3795 | 1 | 0 | 56
39009.3816 | 1 | 0 | 56
39009.3833 | 1 | 0 | 56
39009.3851 | 1 | 0 | 56
39009.3869 | 1 | 0 | 56
39009.3887 | 1 | 0 | 56
39009.3905 | 970 | 1018 | 56
39009.3923 | 1147 | 1125 | 56
39009.394 | 946 | 988 | 56
39009.3958 | 1104 | 1083 | 56
39009.3976 | 972 | 1017 | 56
39009.3994 | 1063 | 1040 | 56
39009.4012 | 1010 | 973 | 56
39009.403 | 1089 | 1137 | 56
39009.4047 | 1070 | 1074 | 56
39009.4065 | 2293 | 0 | 56
39009.4083 | 2569 | 0 | 56
39009.4101 | 2325 | 0 | 56
39009.4119 | 2253 | 0 | 56
39009.4136 | 2625 | 0 | 56
39009.4154 | 2209 | 0 | 56
39009.4172 | 2633 | 0 | 56
56
39009.3777 | 1 | 0 | 57
39009.3795 | 1 | 0 | 57
39009.3816 | 1 | 0 | 57
39009.3834 | 1 | 0 | 57
39009.3852 | 1 | 0 | 57
39009.3869 | 1 | 0 | 57
39009.3887 | 1 | 0 | 57
39009.3905 | 1 | 0 | 57
39009.3923 | 1 | 0 | 57
39009.3941 | 1 | 0 | 57
39009.3958 | 1 | 0 | 57
39009.3976 | 1 | 0 | 57
39009.3994 | 1 | 0 | 57
39009.4012 | 1 | 0 | 57
39009.403 | 1 | 0 | 57
39009.4047 | 1160 | 1000 | 57
39009.4065 | 2027 | 0 | 57
39009.4083 | 2468 | 0 | 57
39009.4101 | 2403 | 0 | 57
39009.4119 | 2564 | 0 | 57
39009.4137 | 2066 | 0 | 57
39009.4154 | 2121 | 0 | 57
39009.4172 | 2540 | 0 | 57
57
39009.3777 | 1 | 0 | 58
39009.3795 | 1 | 0 | 58
39009.3816 | 1 | 0 | 58
39009.3834 | 1 | 0 | 58
39009.3852 | 1 | 0 | 58
39009.3869 | 1 | 0 | 58
39009.3887 | 0 | 0 | 58
39009.3905 | 1 | 0 | 58
39009.3923 | 1 | 0 | 58
39009.3941 | 1 | 0 | 58
39009.3959 | 1 | 0 | 58
39009.3976 | 1 | 0 | 58
39009.3994 | 1 | 0 | 58
39009.4012 | 1 | 0 | 58
39009.403 | 1 | 0 | 58
39009.4048 | 1068 | 998 | 58
39009.4066 | 2282 | 0 | 58
39009.4083 | 2275 | 0 | 58
39009.4101 | 2018 | 0 | 58
39009.4119 | 2615 | 0 | 58
39009.4137 | 2216 | 0 | 58
39009.4155 | 2418 | 0 | 58
39009.4172 | 2028 | 0 | 58
58
39009.3778 | 1 | 0 | 59
39009.3795 | 1 | 0 | 59
39009.3816 | 1 | 0 | 59
39009.3834 | 1 | 0 | 59
39009.3852 | 1 | 0 | 59
39009.387 | 1 | 0 | 59
39009.3887 | 1 | 0 | 59
39009.3905 | 1 | 0 | 59
39009.3923 | 1 | 0 | 59
39009.3941 | 1 | 0 | 59
39009.3959 | 1 | 0 | 59
39009.3977 | 1 | 0 | 59
39009.3994 | 1 | 0 | 59
39009.4012 | 1 | 0 | 59
39009.403 | 0 | 0 | 59
39009.4048 | 25 | 0 | 59
39009.4066 | 2586 | 0 | 59
39009.4083 | 2327 | 0 | 59
39009.4101 | 2043 | 1 | 59
39009.4119 | 2072 | 0 | 59
39009.4137 | 2507 | 0 | 59
39009.4155 | 2419 | 0 | 59
39009.4173 | 2632 | 0 | 59
59
39009.3778 | 1 | 0 | 60
39009.3795 | 1 | 0 | 60
39009.3816 | 1 | 0 | 60
39009.3834 | 1 | 0 | 60
39009.3852 | 1 | 0 | 60
39009.387 | 1 | 0 | 60
39009.3888 | 1 | 0 | 60
39009.3905 | 1 | 0 | 60
39009.3923 | 2005 | 0 | 60
39009.3941 | 2224 | 0 | 60
39009.3959 | 2311 | 0 | 60
39009.3977 | 2545 | 0 | 60
39009.3995 | 2366 | 0 | 60
39009.4012 | 2203 | 0 | 60
39009.403 | 2275 | 0 | 60
39009.4048 | 2365 | 0 | 60
39009.4066 | 2377 | 0 | 60
39009.4084 | 2559 | 0 | 60
39009.4101 | 2627 | 0 | 60
39009.4119 | 2282 | 0 | 60
39009.4137 | 2073 | 0 | 60
39009.4155 | 2370 | 0 | 60
39009.4173 | 2613 | 0 | 60
60
39009.3778 | 1 | 0 | 61
39009.3796 | 1 | 0 | 61
39009.3816 | 1 | 0 | 61
39009.3834 | 1 | 0 | 61
39009.3852 | 1 | 0 | 61
39009.387 | 1 | 0 | 61
39009.3888 | 1 | 0 | 61
39009.3906 | 1 | 0 | 61
39009.3923 | 2 | 0 | 61
39009.3941 | 1 | 0 | 61
39009.3959 | 1 | 0 | 61
39009.3977 | 1 | 0 | 61
39009.3995 | 1 | 0 | 61
39009.4013 | 1 | 0 | 61
39009.403 | 1 | 0 | 61
39009.4048 | 34 | 0 | 61
39009.4066 | 2289 | 0 | 61
39009.4084 | 2435 | 0 | 61
39009.4102 | 2426 | 0 | 61
39009.4119 | 2084 | 0 | 61
39009.4137 | 2045 | 0 | 61
39009.4155 | 2615 | 0 | 61
39009.4173 | 2022 | 0 | 61
61
39009.3778 | 1 | 0 | 62
39009.3796 | 1 | 0 | 62
39009.3817 | 1 | 0 | 62
39009.3834 | 1 | 0 | 62
39009.3852 | 1 | 0 | 62
39009.387 | 1 | 0 | 62
39009.3888 | 1 | 0 | 62
39009.3906 | 1 | 0 | 62
39009.3924 | 1 | 0 | 62
39009.3941 | 1 | 0 | 62
39009.3959 | 1 | 0 | 62
39009.3977 | 1 | 0 | 62
39009.3995 | 1 | 0 | 62
39009.4013 | 1 | 0 | 62
39009.403 | 3 | 0 | 62
39009.4048 | 2044 | 0 | 62
39009.4066 | 2046 | 0 | 62
39009.4084 | 2234 | 0 | 62
39009.4102 | 2093 | 0 | 62
39009.412 | 2257 | 0 | 62
39009.4137 | 2315 | 0 | 62
39009.4155 | 2074 | 0 | 62
39009.4173 | 2334 | 0 | 62
62
39009.3778 | 1 | 0 | 63
39009.3796 | 1 | 0 | 63
39009.3817 | 1 | 0 | 63
39009.3835 | 1 | 0 | 63
39009.3852 | 1 | 0 | 63
39009.387 | 1 | 0 | 63
39009.3888 | 1 | 0 | 63
39009.3906 | 1 | 0 | 63
39009.3924 | 1 | 0 | 63
39009.3942 | 1 | 0 | 63
39009.3959 | 1 | 0 | 63
39009.3977 | 1 | 0 | 63
39009.3995 | 1 | 0 | 63
39009.4013 | 1 | 0 | 63
39009.4031 | 1 | 0 | 63
39009.4048 | 159 | 1 | 63
39009.4066 | 2260 | 0 | 63
39009.4084 | 2325 | 0 | 63
39009.4102 | 2591 | 0 | 63
39009.412 | 2401 | 0 | 63
39009.4138 | 2480 | 0 | 63
39009.4155 | 2135 | 0 | 63
39009.4173 | 2640 | 0 | 63
63
39009.3778 | 1 | 0 | 64
39009.3796 | 1 | 0 | 64
39009.3817 | 1 | 0 | 64
39009.3835 | 1 | 0 | 64
39009.3853 | 0 | 0 | 64
39009.387 | 1 | 0 | 64
39009.3888 | 1 | 0 | 64
39009.3906 | 1 | 0 | 64
39009.3924 | 1 | 0 | 64
39009.3942 | 1 | 0 | 64
39009.3959 | 1 | 0 | 64
39009.3977 | 1 | 0 | 64
39009.3995 | 1 | 0 | 64
39009.4013 | 1 | 0 | 64
39009.4031 | 1 | 0 | 64
39009.4049 | 2289 | 0 | 64
39009.4066 | 2098 | 0 | 64
39009.4084 | 2455 | 0 | 64
39009.4102 | 2422 | 0 | 64
39009.412 | 2144 | 0 | 64
39009.4138 | 2280 | 0 | 64
39009.4156 | 2337 | 0 | 64
39009.4173 | 2031 | 0 | 64
64
39009.3778 | 1 | 0 | 65
39009.3796 | 1 | 0 | 65
39009.3817 | 1 | 0 | 65
39009.3835 | 1 | 0 | 65
39009.3853 | 0 | 0 | 65
39009.3871 | 1 | 0 | 65
39009.3888 | 1 | 0 | 65
39009.3906 | 1 | 0 | 65
39009.3924 | 1 | 0 | 65
39009.3942 | 1 | 0 | 65
39009.396 | 1 | 0 | 65
39009.3978 | 1 | 0 | 65
39009.3995 | 1 | 0 | 65
39009.4013 | 1 | 0 | 65
39009.4031 | 1 | 0 | 65
39009.4049 | 713 | 0 | 65
39009.4067 | 2239 | 0 | 65
39009.4084 | 2598 | 0 | 65
39009.4102 | 2621 | 0 | 65
39009.412 | 2094 | 0 | 65
39009.4138 | 2039 | 0 | 65
39009.4156 | 2158 | 0 | 65
39009.4173 | 2457 | 0 | 65
65
39009.3779 | 1 | 0 | 66
39009.3797 | 1 | 0 | 66
39009.3817 | 1 | 0 | 66
39009.3835 | 1 | 0 | 66
39009.3853 | 0 | 0 | 66
39009.3871 | 1 | 0 | 66
39009.3889 | 1 | 0 | 66
39009.3906 | 1 | 0 | 66
39009.3924 | 1 | 0 | 66
39009.3942 | 1 | 0 | 66
39009.396 | 1 | 0 | 66
39009.3978 | 1 | 0 | 66
39009.3995 | 1 | 0 | 66
39009.4013 | 1 | 0 | 66
39009.4031 | 1 | 0 | 66
39009.4049 | 1960 | 0 | 66
39009.4067 | 2171 | 0 | 66
39009.4085 | 2073 | 0 | 66
39009.4102 | 2088 | 0 | 66
39009.412 | 2572 | 0 | 66
39009.4138 | 2010 | 0 | 66
39009.4156 | 2441 | 0 | 66
39009.4174 | 2143 | 0 | 66
66
39009.3779 | 1 | 0 | 67
39009.3797 | 1 | 0 | 67
39009.3817 | 1 | 0 | 67
39009.3835 | 1 | 0 | 67
39009.3853 | 1 | 0 | 67
39009.3871 | 1 | 0 | 67
39009.3889 | 1 | 0 | 67
39009.3906 | 1 | 0 | 67
39009.3924 | 1 | 0 | 67
39009.3942 | 1 | 0 | 67
39009.396 | 1 | 0 | 67
39009.3978 | 1 | 0 | 67
39009.3996 | 1 | 0 | 67
39009.4013 | 1 | 0 | 67
39009.4031 | 1 | 0 | 67
39009.4049 | 2095 | 0 | 67
39009.4067 | 2470 | 0 | 67
39009.4085 | 2088 | 0 | 67
39009.4103 | 2327 | 0 | 67
39009.412 | 2155 | 0 | 67
39009.4138 | 2472 | 0 | 67
39009.4156 | 2584 | 0 | 67
39009.4174 | 2323 | 0 | 67
67
39009.3779 | 1 | 0 | 68
39009.3797 | 1 | 0 | 68
39009.3818 | 1 | 0 | 68
39009.3835 | 1 | 0 | 68
39009.3853 | 1 | 0 | 68
39009.3871 | 1 | 0 | 68
39009.3889 | 1 | 0 | 68
39009.3907 | 1 | 0 | 68
39009.3925 | 0 | 0 | 68
39009.3942 | 1 | 0 | 68
39009.396 | 1 | 0 | 68
39009.3978 | 1 | 0 | 68
39009.3996 | 1 | 0 | 68
39009.4014 | 1 | 0 | 68
39009.4031 | 1 | 0 | 68
39009.4049 | 2245 | 0 | 68
39009.4067 | 2069 | 0 | 68
39009.4085 | 2011 | 0 | 68
39009.4103 | 2070 | 0 | 68
39009.4121 | 2170 | 0 | 68
39009.4138 | 2382 | 0 | 68
39009.4156 | 2508 | 0 | 68
39009.4174 | 2640 | 0 | 68
68
39009.3779 | 1 | 0 | 69
39009.3797 | 1 | 0 | 69
39009.3818 | 1 | 0 | 69
39009.3836 | 1 | 0 | 69
39009.3853 | 1 | 0 | 69
39009.3871 | 1 | 0 | 69
39009.3889 | 1 | 0 | 69
39009.3907 | 1 | 0 | 69
39009.3925 | 1 | 0 | 69
39009.3942 | 1 | 0 | 69
39009.396 | 1 | 0 | 69
39009.3978 | 1 | 0 | 69
39009.3996 | 1 | 0 | 69
39009.4014 | 1 | 0 | 69
39009.4032 | 4 | 0 | 69
39009.4049 | 2546 | 0 | 69
39009.4067 | 2137 | 0 | 69
39009.4085 | 2561 | 0 | 69
39009.4103 | 2029 | 0 | 69
39009.4121 | 2115 | 0 | 69
39009.4139 | 2535 | 0 | 69
39009.4156 | 2292 | 0 | 69
39009.4174 | 2480 | 0 | 69
69
39009.3779 | 1 | 0 | 70
39009.3797 | 1 | 0 | 70
39009.3818 | 1 | 0 | 70
39009.3836 | 1 | 0 | 70
39009.3854 | 1 | 0 | 70
39009.3871 | 1 | 0 | 70
39009.3889 | 1 | 0 | 70
39009.3907 | 1 | 0 | 70
39009.3925 | 0 | 0 | 70
39009.3943 | 1 | 0 | 70
39009.3961 | 1 | 0 | 70
39009.3978 | 1 | 0 | 70
39009.3996 | 1 | 0 | 70
39009.4014 | 1 | 0 | 70
39009.4032 | 2 | 1 | 70
39009.405 | 2338 | 0 | 70
39009.4067 | 2605 | 0 | 70
39009.4085 | 2408 | 0 | 70
39009.4103 | 2392 | 0 | 70
39009.4121 | 2090 | 0 | 70
39009.4139 | 2345 | 0 | 70
39009.4156 | 2131 | 0 | 70
39009.4174 | 2625 | 0 | 70
70
39009.378 | 0 | 0 | 71
39009.3797 | 1 | 0 | 71
39009.3818 | 1 | 0 | 71
39009.3836 | 1 | 0 | 71
39009.3854 | 1 | 0 | 71
39009.3872 | 1 | 0 | 71
39009.3889 | 1 | 0 | 71
39009.3907 | 1 | 0 | 71
39009.3925 | 1 | 0 | 71
39009.3943 | 1 | 0 | 71
39009.3961 | 1 | 0 | 71
39009.3978 | 1 | 0 | 71
39009.3996 | 1 | 0 | 71
39009.4014 | 1 | 0 | 71
39009.4032 | 1 | 0 | 71
39009.405 | 2175 | 0 | 71
39009.4068 | 2124 | 0 | 71
39009.4085 | 2440 | 0 | 71
39009.4103 | 2338 | 0 | 71
39009.4121 | 2467 | 0 | 71
39009.4139 | 2141 | 0 | 71
39009.4157 | 2199 | 0 | 71
39009.4175 | 2441 | 0 | 71
71
39009.378 | 1 | 0 | 72
39009.3797 | 1 | 0 | 72
39009.3818 | 1 | 0 | 72
39009.3836 | 1 | 0 | 72
39009.3854 | 1 | 0 | 72
39009.3872 | 1 | 0 | 72
39009.389 | 1 | 0 | 72
39009.3907 | 1 | 0 | 72
39009.3925 | 2340 | 0 | 72
39009.3943 | 2610 | 0 | 72
39009.3961 | 2390 | 0 | 72
39009.3979 | 2032 | 0 | 72
39009.3996 | 2075 | 0 | 72
39009.4014 | 2028 | 0 | 72
39009.4032 | 2477 | 0 | 72
39009.405 | 2233 | 0 | 72
39009.4068 | 2468 | 0 | 72
39009.4086 | 2464 | 0 | 72
39009.4103 | 2279 | 1 | 72
39009.4121 | 2393 | 1 | 72
39009.4139 | 2055 | 0 | 72
39009.4157 | 2168 | 0 | 72
39009.4175 | 2139 | 0 | 72
72
39009.378 | 1 | 0 | 73
39009.3798 | 1 | 0 | 73
39009.3818 | 1 | 0 | 73
39009.3836 | 0 | 0 | 73
39009.3854 | 1 | 0 | 73
39009.3872 | 1 | 0 | 73
39009.389 | 1 | 0 | 73
39009.3908 | 1 | 0 | 73
39009.3925 | 1 | 0 | 73
39009.3943 | 1 | 0 | 73
39009.3961 | 1 | 0 | 73
39009.3979 | 1 | 0 | 73
39009.3997 | 1 | 0 | 73
39009.4014 | 1 | 0 | 73
39009.4032 | 2 | 0 | 73
39009.405 | 2460 | 0 | 73
39009.4068 | 2073 | 0 | 73
39009.4086 | 2023 | 0 | 73
39009.4104 | 2316 | 0 | 73
39009.4121 | 2620 | 0 | 73
39009.4139 | 2181 | 0 | 73
39009.4157 | 2620 | 0 | 73
39009.4175 | 2275 | 0 | 73
73
39009.378 | 1 | 0 | 74
39009.3798 | 1 | 0 | 74
39009.3819 | 1 | 0 | 74
39009.3836 | 1 | 0 | 74
39009.3854 | 1 | 0 | 74
39009.3872 | 1 | 0 | 74
39009.389 | 1 | 0 | 74
39009.3908 | 1 | 0 | 74
39009.3925 | 1 | 0 | 74
39009.3943 | 1 | 0 | 74
39009.3961 | 1 | 0 | 74
39009.3979 | 1 | 0 | 74
39009.3997 | 1 | 0 | 74
39009.4015 | 1 | 0 | 74
39009.4032 | 7 | 0 | 74
39009.405 | 1994 | 0 | 74
39009.4068 | 2043 | 0 | 74
39009.4086 | 2488 | 0 | 74
39009.4104 | 2187 | 0 | 74
39009.4122 | 2114 | 0 | 74
39009.4139 | 2360 | 0 | 74
39009.4157 | 2623 | 0 | 74
39009.4175 | 2341 | 0 | 74
74
39009.378 | 1 | 0 | 75
39009.3798 | 1 | 0 | 75
39009.3819 | 1 | 0 | 75
39009.3837 | 1 | 0 | 75
39009.3854 | 0 | 0 | 75
39009.3872 | 0 | 0 | 75
39009.389 | 1 | 0 | 75
39009.3908 | 1 | 0 | 75
39009.3926 | 1 | 0 | 75
39009.3944 | 1 | 0 | 75
39009.3961 | 1 | 0 | 75
39009.3979 | 1 | 1 | 75
39009.3997 | 1 | 0 | 75
39009.4015 | 1 | 0 | 75
39009.4033 | 1 | 0 | 75
39009.405 | 2463 | 0 | 75
39009.4068 | 2564 | 0 | 75
39009.4086 | 2340 | 0 | 75
39009.4104 | 2072 | 0 | 75
39009.4122 | 2630 | 0 | 75
39009.4139 | 2594 | 0 | 75
39009.4157 | 2598 | 0 | 75
39009.4175 | 2181 | 0 | 75
75
39009.378 | 1 | 0 | 76
39009.3798 | 1 | 0 | 76
39009.3819 | 1 | 0 | 76
39009.3837 | 1 | 0 | 76
39009.3855 | 1 | 0 | 76
39009.3872 | 1 | 0 | 76
39009.389 | 1 | 0 | 76
39009.3908 | 1 | 0 | 76
39009.3926 | 1 | 0 | 76
39009.3944 | 1 | 0 | 76
39009.3961 | 1 | 0 | 76
39009.3997 | 1 | 0 | 76
39009.4015 | 1 | 0 | 76
39009.4033 | 1 | 0 | 76
39009.4051 | 2321 | 0 | 76
39009.4068 | 2402 | 0 | 76
39009.4086 | 2217 | 0 | 76
39009.4104 | 2522 | 0 | 76
39009.4122 | 2456 | 0 | 76
39009.414 | 2453 | 0 | 76
39009.4158 | 2557 | 0 | 76
39009.4175 | 2083 | 0 | 76
76
39009.378 | 1 | 0 | 77
39009.3798 | 0 | 0 | 77
39009.3819 | 1 | 0 | 77
39009.3837 | 1 | 0 | 77
39009.3855 | 1 | 0 | 77
39009.3873 | 1 | 0 | 77
39009.389 | 1 | 0 | 77
39009.3908 | 1 | 0 | 77
39009.3926 | 1 | 0 | 77
39009.3944 | 1 | 0 | 77
39009.3962 | 1 | 0 | 77
39009.398 | 1 | 0 | 77
39009.3997 | 0 | 0 | 77
39009.4015 | 1 | 0 | 77
39009.4033 | 1 | 0 | 77
39009.4051 | 2210 | 0 | 77
39009.4069 | 2585 | 0 | 77
39009.4086 | 2402 | 0 | 77
39009.4104 | 2415 | 0 | 77
39009.4122 | 2146 | 0 | 77
39009.414 | 2223 | 0 | 77
39009.4158 | 2068 | 0 | 77
39009.4175 | 2062 | 0 | 77
77
39009.3781 | 1 | 0 | 78
39009.3798 | 1 | 0 | 78
39009.3819 | 0 | 0 | 78
39009.3837 | 1 | 0 | 78
39009.3855 | 1 | 0 | 78
39009.3873 | 1 | 0 | 78
39009.3891 | 1 | 0 | 78
39009.3908 | 1 | 0 | 78
39009.3926 | 1 | 0 | 78
39009.3944 | 1 | 0 | 78
39009.3962 | 1 | 0 | 78
39009.398 | 1 | 0 | 78
39009.3997 | 1 | 0 | 78
39009.4015 | 1 | 0 | 78
39009.4033 | 1 | 0 | 78
39009.4051 | 2129 | 0 | 78
39009.4069 | 2377 | 0 | 78
39009.4087 | 2182 | 0 | 78
39009.4104 | 2062 | 0 | 78
39009.4122 | 2356 | 0 | 78
39009.414 | 2079 | 0 | 78
39009.4158 | 2488 | 0 | 78
39009.4176 | 2121 | 0 | 78
78
39009.3781 | 1 | 0 | 79
39009.3799 | 1 | 0 | 79
39009.3819 | 0 | 0 | 79
39009.3837 | 1 | 0 | 79
39009.3855 | 1 | 0 | 79
39009.3873 | 1 | 0 | 79
39009.3891 | 1 | 0 | 79
39009.3908 | 1 | 0 | 79
39009.3926 | 1 | 0 | 79
39009.3944 | 1 | 0 | 79
39009.3962 | 1 | 0 | 79
39009.398 | 1 | 0 | 79
39009.3998 | 1 | 0 | 79
39009.4015 | 3 | 0 | 79
39009.4033 | 1 | 0 | 79
39009.4051 | 2578 | 0 | 79
39009.4069 | 2004 | 0 | 79
39009.4087 | 2116 | 0 | 79
39009.4105 | 2210 | 0 | 79
39009.4122 | 2345 | 1 | 79
39009.414 | 2439 | 0 | 79
39009.4158 | 2395 | 0 | 79
39009.4176 | 2149 | 0 | 79
79
39009.3781 | 1 | 0 | 80
39009.3799 | 1 | 0 | 80
39009.382 | 1 | 0 | 80
39009.3837 | 1 | 0 | 80
39009.3855 | 1 | 0 | 80
39009.3873 | 1 | 0 | 80
39009.3891 | 1 | 0 | 80
39009.3909 | 1 | 0 | 80
39009.3927 | 0 | 0 | 80
39009.3944 | 1 | 0 | 80
39009.3962 | 1 | 0 | 80
39009.398 | 1 | 0 | 80
39009.3998 | 1 | 0 | 80
39009.4016 | 1 | 0 | 80
39009.4033 | 1 | 0 | 80
39009.4051 | 2513 | 0 | 80
39009.4069 | 2216 | 0 | 80
39009.4087 | 2541 | 0 | 80
39009.4105 | 2372 | 0 | 80
39009.4122 | 2097 | 0 | 80
39009.414 | 2510 | 0 | 80
39009.4158 | 2581 | 0 | 80
39009.4176 | 2329 | 0 | 80
80
39009.3781 | 1 | 0 | 81
39009.3799 | 1 | 0 | 81
39009.382 | 1 | 0 | 81
39009.3838 | 1 | 0 | 81
39009.3855 | 1 | 0 | 81
39009.3873 | 1 | 0 | 81
39009.3891 | 1 | 0 | 81
39009.3909 | 1 | 0 | 81
39009.3927 | 1 | 0 | 81
39009.3944 | 1 | 0 | 81
39009.3962 | 0 | 0 | 81
39009.398 | 1 | 0 | 81
39009.3998 | 1 | 0 | 81
39009.4016 | 1 | 0 | 81
39009.4034 | 1 | 0 | 81
39009.4051 | 2515 | 0 | 81
39009.4069 | 2144 | 0 | 81
39009.4087 | 2031 | 0 | 81
39009.4105 | 2627 | 0 | 81
39009.4123 | 2219 | 0 | 81
39009.4141 | 2563 | 0 | 81
39009.4158 | 2527 | 0 | 81
39009.4176 | 2261 | 0 | 81
81
39009.3781 | 0 | 0 | 82
39009.3799 | 1 | 0 | 82
39009.382 | 1 | 0 | 82
39009.3838 | 1 | 0 | 82
39009.3856 | 1 | 0 | 82
39009.3873 | 1 | 0 | 82
39009.3891 | 1 | 0 | 82
39009.3909 | 1 | 0 | 82
39009.3927 | 2030 | 0 | 82
39009.3945 | 2125 | 0 | 82
39009.3962 | 2155 | 0 | 82
39009.398 | 2588 | 0 | 82
39009.3998 | 2085 | 0 | 82
39009.4016 | 2187 | 0 | 82
39009.4034 | 2436 | 0 | 82
39009.4052 | 2385 | 0 | 82
39009.4069 | 2417 | 0 | 82
39009.4087 | 2293 | 0 | 82
39009.4105 | 2547 | 0 | 82
39009.4123 | 2052 | 0 | 82
39009.4141 | 2238 | 0 | 82
39009.4158 | 2333 | 0 | 82
39009.4176 | 2213 | 0 | 82
82
39009.3781 | 1 | 0 | 83
39009.3799 | 1 | 0 | 83
39009.382 | 1 | 0 | 83
39009.3838 | 1 | 0 | 83
39009.3856 | 1 | 0 | 83
39009.3873 | 1 | 0 | 83
39009.3891 | 1 | 0 | 83
39009.3909 | 1 | 0 | 83
39009.3927 | 1 | 0 | 83
39009.3945 | 1 | 0 | 83
39009.3963 | 1 | 0 | 83
39009.398 | 1 | 0 | 83
39009.3998 | 1 | 0 | 83
39009.4016 | 1 | 0 | 83
39009.4034 | 1 | 0 | 83
39009.4052 | 2012 | 0 | 83
39009.407 | 2083 | 0 | 83
39009.4087 | 2304 | 0 | 83
39009.4105 | 2197 | 0 | 83
39009.4123 | 2608 | 0 | 83
39009.4141 | 2039 | 0 | 83
39009.4159 | 2083 | 0 | 83
39009.4177 | 2318 | 0 | 83
83
39009.3782 | 1 | 0 | 84
39009.3799 | 1 | 0 | 84
39009.382 | 1 | 0 | 84
39009.3838 | 1 | 0 | 84
39009.3856 | 1 | 0 | 84
39009.3874 | 1 | 0 | 84
39009.3891 | 1 | 0 | 84
39009.3909 | 1 | 0 | 84
39009.3927 | 1 | 0 | 84
39009.3945 | 1 | 0 | 84
39009.3963 | 1 | 0 | 84
39009.3981 | 1 | 0 | 84
39009.3998 | 1 | 0 | 84
39009.4016 | 1 | 0 | 84
39009.4034 | 26 | 0 | 84
39009.4052 | 2261 | 0 | 84
39009.407 | 2031 | 0 | 84
39009.4088 | 2520 | 0 | 84
39009.4105 | 2594 | 0 | 84
39009.4123 | 2537 | 0 | 84
39009.4141 | 2233 | 0 | 84
39009.4159 | 2075 | 0 | 84
39009.4177 | 2273 | 0 | 84
84
39009.3782 | 1 | 0 | 85
39009.38 | 1 | 0 | 85
39009.382 | 1 | 0 | 85
39009.3838 | 1 | 0 | 85
39009.3856 | 1 | 0 | 85
39009.3874 | 1 | 0 | 85
39009.3892 | 1 | 0 | 85
39009.3909 | 1 | 0 | 85
39009.3927 | 1 | 0 | 85
39009.3945 | 1 | 0 | 85
39009.3963 | 1 | 0 | 85
39009.3981 | 1 | 0 | 85
39009.3999 | 1 | 0 | 85
39009.4016 | 1 | 0 | 85
39009.4034 | 1 | 0 | 85
39009.4052 | 2509 | 0 | 85
39009.407 | 2068 | 0 | 85
39009.4088 | 2271 | 0 | 85
39009.4105 | 2246 | 0 | 85
39009.4123 | 2338 | 0 | 85
39009.4141 | 2139 | 0 | 85
39009.4159 | 2253 | 0 | 85
39009.4177 | 2433 | 0 | 85
85
39009.3782 | 1 | 0 | 86
39009.38 | 1 | 0 | 86
39009.382 | 1 | 0 | 86
39009.3838 | 1 | 0 | 86
39009.3856 | 1 | 0 | 86
39009.3874 | 0 | 0 | 86
39009.3892 | 1 | 0 | 86
39009.391 | 1 | 0 | 86
39009.3927 | 1 | 0 | 86
39009.3945 | 1 | 0 | 86
39009.3963 | 1 | 0 | 86
39009.3981 | 1 | 0 | 86
39009.3999 | 1 | 0 | 86
39009.4017 | 1 | 0 | 86
39009.4034 | 1 | 0 | 86
39009.4052 | 2124 | 0 | 86
39009.407 | 2223 | 0 | 86
39009.4088 | 2442 | 0 | 86
39009.4106 | 2573 | 0 | 86
39009.4123 | 2183 | 0 | 86
39009.4141 | 2539 | 0 | 86
39009.4159 | 2037 | 0 | 86
39009.4177 | 2446 | 0 | 86
86
39009.3782 | 1 | 0 | 87
39009.38 | 1 | 0 | 87
39009.3821 | 1 | 0 | 87
39009.3839 | 1 | 0 | 87
39009.3856 | 1 | 0 | 87
39009.3874 | 1 | 0 | 87
39009.3892 | 1 | 0 | 87
39009.391 | 1 | 0 | 87
39009.3928 | 1 | 0 | 87
39009.3945 | 1 | 0 | 87
39009.3963 | 1 | 0 | 87
39009.3981 | 1 | 0 | 87
39009.3999 | 1 | 0 | 87
39009.4017 | 1 | 0 | 87
39009.4034 | 1 | 0 | 87
39009.4052 | 2505 | 0 | 87
39009.407 | 2293 | 0 | 87
39009.4088 | 2605 | 0 | 87
39009.4106 | 2059 | 0 | 87
39009.4124 | 2184 | 0 | 87
39009.4141 | 2437 | 0 | 87
39009.4159 | 2593 | 0 | 87
39009.4177 | 2640 | 0 | 87
87
39009.3782 | 1 | 0 | 88
39009.38 | 1 | 0 | 88
39009.3821 | 1 | 0 | 88
39009.3839 | 1 | 0 | 88
39009.3856 | 1 | 0 | 88
39009.3874 | 1 | 0 | 88
39009.3892 | 1 | 0 | 88
39009.391 | 1 | 0 | 88
39009.3928 | 1 | 0 | 88
39009.3946 | 1 | 0 | 88
39009.3963 | 1 | 0 | 88
39009.3981 | 1 | 0 | 88
39009.3999 | 1 | 0 | 88
39009.4017 | 1 | 0 | 88
39009.4035 | 1 | 0 | 88
39009.4053 | 1980 | 0 | 88
39009.407 | 2574 | 0 | 88
39009.4088 | 2146 | 0 | 88
39009.4106 | 2477 | 0 | 88
39009.4124 | 2577 | 0 | 88
39009.4142 | 2434 | 0 | 88
39009.4159 | 2205 | 0 | 88
39009.4177 | 2536 | 0 | 88
88
39009.3782 | 1 | 0 | 89
39009.38 | 1 | 0 | 89
39009.3821 | 1 | 0 | 89
39009.3839 | 1 | 0 | 89
39009.3857 | 1 | 0 | 89
39009.3874 | 1 | 0 | 89
39009.3892 | 1 | 0 | 89
39009.391 | 1 | 0 | 89
39009.3928 | 1 | 0 | 89
39009.3946 | 1 | 0 | 89
39009.3964 | 1 | 0 | 89
39009.3981 | 1 | 0 | 89
39009.3999 | 1 | 0 | 89
39009.4017 | 1 | 0 | 89
39009.4053 | 2115 | 0 | 89
39009.407 | 2140 | 0 | 89
39009.4088 | 2552 | 0 | 89
39009.4106 | 2489 | 0 | 89
39009.4124 | 2389 | 0 | 89
39009.4142 | 2030 | 0 | 89
39009.416 | 2142 | 0 | 89
39009.4177 | 2418 | 0 | 89
89
39009.3783 | 1 | 0 | 90
39009.38 | 1 | 0 | 90
39009.3821 | 1 | 0 | 90
39009.3839 | 1 | 0 | 90
39009.3857 | 1 | 0 | 90
39009.3875 | 1 | 0 | 90
39009.3892 | 1 | 0 | 90
39009.391 | 1 | 0 | 90
39009.3928 | 1 | 0 | 90
39009.3946 | 1 | 0 | 90
39009.3964 | 1 | 0 | 90
39009.3982 | 1 | 0 | 90
39009.3999 | 1 | 0 | 90
39009.4017 | 1 | 0 | 90
39009.4035 | 1 | 0 | 90
39009.4053 | 2347 | 0 | 90
39009.4071 | 2016 | 0 | 90
39009.4088 | 2323 | 0 | 90
39009.4106 | 2044 | 0 | 90
39009.4124 | 2106 | 0 | 90
39009.4142 | 2184 | 0 | 90
39009.416 | 2306 | 0 | 90
39009.4178 | 2607 | 0 | 90
90
39009.3783 | 1 | 0 | 91
39009.3801 | 1 | 0 | 91
39009.3821 | 1 | 0 | 91
39009.3839 | 1 | 0 | 91
39009.3857 | 1 | 0 | 91
39009.3875 | 1 | 0 | 91
39009.3893 | 1 | 0 | 91
39009.391 | 1 | 0 | 91
39009.3928 | 2216 | 0 | 91
39009.3946 | 2309 | 0 | 91
39009.3964 | 2236 | 0 | 91
39009.3982 | 2308 | 0 | 91
39009.4 | 2072 | 0 | 91
39009.4017 | 2011 | 0 | 91
39009.4035 | 2440 | 0 | 91
39009.4053 | 2109 | 0 | 91
39009.4071 | 2006 | 0 | 91
39009.4089 | 2597 | 0 | 91
39009.4106 | 2169 | 0 | 91
39009.4124 | 2102 | 0 | 91
39009.4142 | 2618 | 0 | 91
39009.416 | 2574 | 0 | 91
39009.4178 | 2565 | 0 | 91
91
39009.3783 | 1 | 0 | 92
39009.3801 | 1 | 0 | 92
39009.3822 | 1 | 0 | 92
39009.3839 | 1 | 0 | 92
39009.3857 | 1 | 0 | 92
39009.3875 | 1 | 0 | 92
39009.3893 | 1 | 0 | 92
39009.3911 | 1 | 0 | 92
39009.3928 | 1 | 0 | 92
39009.3946 | 1 | 0 | 92
39009.3964 | 1 | 0 | 92
39009.3982 | 1 | 0 | 92
39009.4 | 1 | 0 | 92
39009.4017 | 1 | 0 | 92
39009.4035 | 96 | 0 | 92
39009.4053 | 2011 | 0 | 92
39009.4071 | 2556 | 0 | 92
39009.4089 | 2055 | 0 | 92
39009.4107 | 2402 | 0 | 92
39009.4124 | 2126 | 0 | 92
39009.4142 | 2105 | 0 | 92
39009.416 | 2617 | 0 | 92
39009.4178 | 2608 | 0 | 92
92
39009.3783 | 1 | 0 | 93
39009.3801 | 1 | 0 | 93
39009.3822 | 1 | 0 | 93
39009.3839 | 1 | 0 | 93
39009.3857 | 1 | 0 | 93
39009.3875 | 0 | 0 | 93
39009.3893 | 1 | 0 | 93
39009.3911 | 1 | 0 | 93
39009.3929 | 2312 | 0 | 93
39009.3946 | 2543 | 0 | 93
39009.3964 | 2542 | 0 | 93
39009.3982 | 2142 | 0 | 93
39009.4 | 2270 | 0 | 93
39009.4018 | 2482 | 0 | 93
39009.4036 | 2174 | 0 | 93
39009.4053 | 2116 | 0 | 93
39009.4071 | 2215 | 0 | 93
39009.4089 | 2096 | 0 | 93
39009.4107 | 2606 | 0 | 93
39009.4125 | 2084 | 1 | 93
39009.4142 | 2268 | 0 | 93
39009.416 | 2099 | 0 | 93
39009.4178 | 2645 | 0 | 93
93
39009.3783 | 1 | 0 | 94
39009.3801 | 1 | 0 | 94
39009.3822 | 1 | 0 | 94
39009.384 | 1 | 0 | 94
39009.3857 | 1 | 0 | 94
39009.3875 | 1 | 0 | 94
39009.3893 | 1 | 0 | 94
39009.3911 | 1 | 0 | 94
39009.3929 | 1 | 0 | 94
39009.3947 | 1 | 0 | 94
39009.3964 | 1 | 0 | 94
39009.3982 | 1 | 0 | 94
39009.4 | 2 | 0 | 94
39009.4018 | 1 | 0 | 94
39009.4036 | 1569 | 0 | 94
39009.4053 | 2318 | 0 | 94
39009.4071 | 2141 | 0 | 94
39009.4089 | 1990 | 0 | 94
39009.4107 | 2040 | 0 | 94
39009.4125 | 2227 | 0 | 94
39009.4143 | 2110 | 0 | 94
39009.416 | 2202 | 0 | 94
39009.4178 | 2005 | 0 | 94
94
39009.3783 | 1 | 0 | 95
39009.3801 | 1 | 0 | 95
39009.3822 | 1 | 0 | 95
39009.384 | 1 | 0 | 95
39009.3858 | 1 | 0 | 95
39009.3875 | 1 | 0 | 95
39009.3893 | 1 | 0 | 95
39009.3911 | 1 | 0 | 95
39009.3929 | 2341 | 0 | 95
39009.3947 | 2162 | 0 | 95
39009.3965 | 2170 | 0 | 95
39009.3982 | 2293 | 0 | 95
39009.4 | 2309 | 1 | 95
39009.4018 | 2401 | 0 | 95
39009.4036 | 2082 | 0 | 95
39009.4054 | 2273 | 0 | 95
39009.4071 | 2274 | 0 | 95
39009.4089 | 2237 | 0 | 95
39009.4107 | 2078 | 0 | 95
39009.4125 | 2632 | 0 | 95
39009.4143 | 2311 | 0 | 95
39009.4161 | 2373 | 0 | 95
39009.4178 | 2232 | 0 | 95
95
39009.3784 | 1 | 0 | 96
39009.3801 | 1 | 0 | 96
39009.3822 | 1 | 0 | 96
39009.384 | 1 | 0 | 96
39009.3858 | 1 | 0 | 96
39009.3876 | 1 | 0 | 96
39009.3893 | 1 | 0 | 96
39009.3911 | 1 | 0 | 96
39009.3929 | 1 | 0 | 96
39009.3947 | 1 | 0 | 96
39009.3965 | 1 | 0 | 96
39009.3983 | 1 | 0 | 96
39009.4 | 1 | 0 | 96
39009.4018 | 1 | 0 | 96
39009.4036 | 1775 | 1 | 96
39009.4054 | 2276 | 0 | 96
39009.4072 | 2088 | 0 | 96
39009.4089 | 2411 | 0 | 96
39009.4107 | 2003 | 0 | 96
39009.4125 | 2075 | 0 | 96
39009.4143 | 2182 | 0 | 96
39009.4161 | 2600 | 0 | 96
39009.4179 | 2392 | 0 | 96
96
39009.3784 | 1 | 0 | 97
39009.3802 | 1 | 0 | 97
39009.3822 | 1 | 0 | 97
39009.384 | 1 | 0 | 97
39009.3858 | 1 | 0 | 97
39009.3876 | 1 | 0 | 97
39009.3894 | 0 | 0 | 97
39009.3911 | 1 | 0 | 97
39009.3929 | 2329 | 0 | 97
39009.3947 | 2106 | 0 | 97
39009.3965 | 2253 | 0 | 97
39009.3983 | 2380 | 0 | 97
39009.4 | 2056 | 0 | 97
39009.4018 | 2556 | 0 | 97
39009.4036 | 2106 | 0 | 97
39009.4054 | 2205 | 0 | 97
39009.4072 | 2286 | 0 | 97
39009.409 | 2269 | 0 | 97
39009.4107 | 2481 | 0 | 97
39009.4125 | 2631 | 0 | 97
39009.4143 | 2278 | 0 | 97
39009.4161 | 2457 | 0 | 97
39009.4179 | 2525 | 0 | 97
97
39009.3784 | 1 | 0 | 98
39009.3802 | 1 | 0 | 98
39009.3822 | 1 | 0 | 98
39009.384 | 1 | 0 | 98
39009.3858 | 1 | 0 | 98
39009.3876 | 1 | 0 | 98
39009.3894 | 1 | 0 | 98
39009.3912 | 1 | 0 | 98
39009.3929 | 1 | 0 | 98
39009.3947 | 2 | 0 | 98
39009.3965 | 1 | 0 | 98
39009.3983 | 1 | 0 | 98
39009.4001 | 1 | 0 | 98
39009.4019 | 1 | 0 | 98
39009.4036 | 1 | 0 | 98
39009.4054 | 2429 | 0 | 98
39009.4072 | 2522 | 0 | 98
39009.409 | 1969 | 0 | 98
39009.4108 | 2571 | 0 | 98
39009.4125 | 2349 | 0 | 98
39009.4143 | 2423 | 0 | 98
39009.4161 | 2629 | 0 | 98
39009.4179 | 2468 | 0 | 98
98
39009.3784 | 1 | 0 | 99
39009.3802 | 1 | 0 | 99
39009.3823 | 0 | 0 | 99
39009.384 | 1 | 0 | 99
39009.3858 | 1 | 0 | 99
39009.3876 | 1 | 0 | 99
39009.3894 | 1 | 0 | 99
39009.3912 | 1 | 0 | 99
39009.393 | 1 | 0 | 99
39009.3947 | 1 | 0 | 99
39009.3965 | 1 | 0 | 99
39009.3983 | 1 | 0 | 99
39009.4001 | 1 | 0 | 99
39009.4019 | 1 | 0 | 99
39009.4036 | 618 | 0 | 99
39009.4054 | 2538 | 0 | 99
39009.4072 | 2326 | 0 | 99
39009.409 | 2521 | 0 | 99
39009.4108 | 2594 | 0 | 99
39009.4126 | 2552 | 0 | 99
39009.4143 | 2280 | 0 | 99
39009.4161 | 2414 | 0 | 99
39009.4179 | 2628 | 0 | 99
99
39009.3784 | 1 | 0 | 100
39009.3802 | 1 | 0 | 100
39009.3823 | 1 | 0 | 100
39009.3841 | 1 | 0 | 100
39009.3858 | 1 | 0 | 100
39009.3876 | 1 | 0 | 100
39009.3894 | 1 | 0 | 100
39009.3912 | 1 | 0 | 100
39009.393 | 1 | 0 | 100
39009.3948 | 1 | 0 | 100
39009.3965 | 1 | 0 | 100
39009.3983 | 1 | 0 | 100
39009.4001 | 1 | 0 | 100
39009.4019 | 1 | 0 | 100
39009.4037 | 2129 | 0 | 100
39009.4055 | 2011 | 0 | 100
39009.4072 | 2521 | 0 | 100
39009.409 | 2097 | 0 | 100
39009.4108 | 2207 | 0 | 100
39009.4126 | 2010 | 0 | 100
39009.4144 | 2022 | 0 | 100
39009.4161 | 2502 | 0 | 100
39009.4179 | 2503 | 0 | 100
100
39009.3784 | 1 | 0 | 101
39009.3802 | 1 | 0 | 101
39009.3823 | 1 | 0 | 101
39009.3841 | 1 | 0 | 101
39009.3859 | 1 | 0 | 101
39009.3876 | 1 | 0 | 101
39009.3894 | 1 | 0 | 101
39009.3912 | 1 | 0 | 101
39009.393 | 1 | 0 | 101
39009.3948 | 1 | 0 | 101
39009.3966 | 1 | 0 | 101
39009.3983 | 1 | 0 | 101
39009.4001 | 1 | 0 | 101
39009.4019 | 1 | 0 | 101
39009.4037 | 2449 | 0 | 101
39009.4055 | 1996 | 0 | 101
39009.4072 | 2021 | 0 | 101
39009.409 | 2001 | 0 | 101
39009.4108 | 2424 | 0 | 101
39009.4126 | 2257 | 0 | 101
39009.4144 | 2055 | 0 | 101
39009.4162 | 2420 | 0 | 101
39009.4179 | 2443 | 0 | 101
101
39009.3784 | 1 | 0 | 102
39009.3802 | 1 | 0 | 102
39009.3823 | 1 | 0 | 102
39009.3841 | 1 | 0 | 102
39009.3859 | 1 | 0 | 102
39009.3877 | 1 | 0 | 102
39009.3894 | 1 | 0 | 102
39009.3912 | 1 | 0 | 102
39009.393 | 1 | 0 | 102
39009.3948 | 1 | 0 | 102
39009.3966 | 1 | 0 | 102
39009.3983 | 1 | 0 | 102
39009.4001 | 1 | 0 | 102
39009.4019 | 1 | 0 | 102
39009.4037 | 2165 | 0 | 102
39009.4055 | 2371 | 0 | 102
39009.4073 | 2189 | 0 | 102
39009.4108 | 2180 | 0 | 102
39009.4126 | 2172 | 0 | 102
39009.4144 | 2577 | 0 | 102
39009.4162 | 2285 | 0 | 102
39009.418 | 2597 | 0 | 102
102
39009.3785 | 1 | 0 | 103
39009.3803 | 1 | 0 | 103
39009.3823 | 1 | 0 | 103
39009.3841 | 1 | 0 | 103
39009.3859 | 1 | 0 | 103
39009.3877 | 1 | 0 | 103
39009.3895 | 1 | 0 | 103
39009.3912 | 1 | 0 | 103
39009.393 | 1 | 0 | 103
39009.3948 | 1 | 0 | 103
39009.3966 | 1 | 0 | 103
39009.3984 | 1 | 0 | 103
39009.4002 | 1 | 0 | 103
39009.4019 | 1 | 0 | 103
39009.4037 | 2507 | 0 | 103
39009.4055 | 2415 | 0 | 103
39009.4073 | 2374 | 0 | 103
39009.4091 | 2377 | 0 | 103
39009.4108 | 2441 | 0 | 103
39009.4126 | 2565 | 0 | 103
39009.4144 | 2068 | 0 | 103
39009.4162 | 2539 | 0 | 103
39009.418 | 2582 | 0 | 103
103
39009.3803 | 1 | 0 | 104
39009.3823 | 1 | 0 | 104
39009.3841 | 1 | 0 | 104
39009.3859 | 1 | 0 | 104
39009.3877 | 1 | 0 | 104
39009.3895 | 1 | 0 | 104
39009.3913 | 1 | 0 | 104
39009.393 | 1 | 0 | 104
39009.3948 | 1 | 0 | 104
39009.3966 | 1 | 0 | 104
39009.3984 | 1 | 0 | 104
39009.4002 | 1 | 0 | 104
39009.4019 | 1 | 0 | 104
39009.4037 | 1 | 0 | 104
39009.4055 | 2499 | 0 | 104
39009.4073 | 2342 | 0 | 104
39009.4091 | 2387 | 0 | 104
39009.4109 | 2132 | 0 | 104
39009.4126 | 2078 | 0 | 104
39009.4144 | 2234 | 0 | 104
39009.4162 | 2218 | 0 | 104
39009.418 | 2480 | 0 | 104
104
39009.3785 | 1 | 0 | 105
39009.3803 | 1 | 0 | 105
39009.3824 | 1 | 0 | 105
39009.3841 | 1 | 0 | 105
39009.3859 | 1 | 0 | 105
39009.3877 | 1 | 0 | 105
39009.3895 | 1 | 0 | 105
39009.3913 | 1 | 0 | 105
39009.3931 | 1 | 0 | 105
39009.3948 | 1 | 0 | 105
39009.3966 | 1 | 0 | 105
39009.3984 | 1 | 0 | 105
39009.4002 | 1 | 0 | 105
39009.402 | 12 | 8 | 105
39009.4037 | 2077 | 0 | 105
39009.4055 | 2156 | 0 | 105
39009.4073 | 2498 | 0 | 105
39009.4091 | 2016 | 0 | 105
39009.4109 | 2299 | 0 | 105
39009.4127 | 2228 | 0 | 105
39009.4144 | 2462 | 0 | 105
39009.4162 | 2485 | 0 | 105
39009.418 | 2540 | 0 | 105
105
39009.3785 | 1 | 0 | 106
39009.3803 | 1 | 0 | 106
39009.3824 | 1 | 0 | 106
39009.3842 | 1 | 0 | 106
39009.3859 | 1 | 0 | 106
39009.3877 | 1 | 0 | 106
39009.3895 | 1 | 0 | 106
39009.3913 | 1 | 0 | 106
39009.3948 | 1 | 0 | 106
39009.3966 | 1 | 0 | 106
39009.3984 | 1 | 0 | 106
39009.4002 | 1 | 0 | 106
39009.402 | 12 | 8 | 106
39009.4038 | 2430 | 0 | 106
39009.4055 | 2054 | 0 | 106
39009.4073 | 2009 | 0 | 106
39009.4091 | 2094 | 0 | 106
39009.4109 | 2058 | 0 | 106
39009.4127 | 2530 | 0 | 106
39009.4145 | 2022 | 0 | 106
39009.4162 | 2089 | 0 | 106
39009.418 | 2018 | 0 | 106
106
39009.3785 | 1 | 0 | 107
39009.3803 | 1 | 0 | 107
39009.3824 | 1 | 0 | 107
39009.3842 | 1 | 0 | 107
39009.386 | 1 | 0 | 107
39009.3877 | 1 | 0 | 107
39009.3895 | 1 | 0 | 107
39009.3913 | 1 | 0 | 107
39009.3931 | 1 | 0 | 107
39009.3949 | 1 | 0 | 107
39009.3967 | 1 | 0 | 107
39009.3984 | 1 | 0 | 107
39009.4002 | 1 | 0 | 107
39009.402 | 1 | 0 | 107
39009.4038 | 2016 | 0 | 107
39009.4056 | 2178 | 0 | 107
39009.4073 | 2132 | 0 | 107
39009.4091 | 2100 | 0 | 107
39009.4109 | 2210 | 0 | 107
39009.4127 | 2339 | 0 | 107
39009.4145 | 2545 | 0 | 107
39009.4163 | 2363 | 0 | 107
39009.418 | 2555 | 0 | 107
107
39009.3785 | 0 | 0 | 108
39009.3803 | 1 | 0 | 108
39009.3824 | 1 | 0 | 108
39009.3842 | 1 | 0 | 108
39009.386 | 0 | 0 | 108
39009.3878 | 1 | 0 | 108
39009.3895 | 1 | 0 | 108
39009.3913 | 1 | 0 | 108
39009.3931 | 1 | 0 | 108
39009.3949 | 1 | 0 | 108
39009.3967 | 1 | 0 | 108
39009.3984 | 1 | 0 | 108
39009.4002 | 1 | 0 | 108
39009.402 | 1 | 0 | 108
39009.4038 | 1 | 0 | 108
39009.4056 | 2173 | 0 | 108
39009.4074 | 2009 | 0 | 108
39009.4091 | 2003 | 0 | 108
39009.4109 | 2506 | 0 | 108
39009.4127 | 2109 | 0 | 108
39009.4145 | 2021 | 0 | 108
39009.4163 | 2248 | 0 | 108
39009.4181 | 2065 | 0 | 108
108
39009.3786 | 1 | 0 | 109
39009.3803 | 1 | 0 | 109
39009.3824 | 1 | 0 | 109
39009.3842 | 0 | 0 | 109
39009.386 | 1 | 0 | 109
39009.3878 | 1 | 0 | 109
39009.3895 | 1 | 0 | 109
39009.3913 | 1 | 0 | 109
39009.3931 | 1 | 0 | 109
39009.3949 | 1 | 0 | 109
39009.3967 | 1 | 0 | 109
39009.3985 | 1 | 0 | 109
39009.4002 | 1 | 0 | 109
39009.402 | 1 | 0 | 109
39009.4038 | 2223 | 0 | 109
39009.4056 | 2485 | 0 | 109
39009.4074 | 2586 | 0 | 109
39009.4092 | 2313 | 0 | 109
39009.4109 | 2011 | 0 | 109
39009.4127 | 2448 | 0 | 109
39009.4145 | 2268 | 0 | 109
39009.4163 | 2459 | 0 | 109
39009.4181 | 2176 | 0 | 109
109
39009.3786 | 1 | 0 | 110
39009.3804 | 1 | 0 | 110
39009.3824 | 1 | 0 | 110
39009.3842 | 1 | 0 | 110
39009.386 | 1 | 0 | 110
39009.3878 | 1 | 0 | 110
39009.3896 | 1 | 0 | 110
39009.3914 | 1 | 0 | 110
39009.3931 | 1 | 0 | 110
39009.3949 | 1 | 0 | 110
39009.3967 | 1 | 0 | 110
39009.3985 | 1 | 0 | 110
39009.4003 | 1 | 0 | 110
39009.402 | 1 | 0 | 110
39009.4038 | 1 | 0 | 110
39009.4056 | 2230 | 0 | 110
39009.4074 | 2300 | 0 | 110
39009.4092 | 2379 | 0 | 110
39009.411 | 2123 | 0 | 110
39009.4127 | 2016 | 0 | 110
39009.4145 | 2018 | 0 | 110
39009.4163 | 2623 | 0 | 110
39009.4181 | 2131 | 0 | 110
110

## Test Facts
Last row in IRMS data sheets: | 28
Time when gas burner was ignited: | 632