## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-2 - Circuit Simulator Data Only
Test Date: | 2006-10-24
Circuit Simulator Configurations and connections:
|  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 150 VA | 150 VA | 200 VA | 100 VA
| CPT Grounding: | NOT Grounded | Grounded | Grounded | Grounded
| General Config. | Inter-Cable Setup | Inter-Cable Setup | MOV-1 | Inter-Cable Setup
| Cable Type VERIFY | TS Bundle of 12 XLPE/CSPE cables (Item #10) in a cable tray at Location A | Mixed Bundle of 6 XLPE/CSPE cables (item #10) and 6 PE/PVC cables (item #15) in a cable tray at location A | Single Cable PVC/PVC (cable Item #1) in a cable tray at location G | Mixed Bundle of XLPE/CSPE cables (item #10) and PE/PVC cables (item #15) (total 6 cables) in a cable tray at Location C
| Wiring Config: | IC-1 with All XLPE (Item 10) cables: 3-cables on Source 1 3-cables on Source 2 1-cable on each of Targets 4, 5, and 6 | IC: 3-cables on Source 1, (1 XLPE and 2 PE) 3-cables on Source 2, (1 XLPE and 2 PE) 1 XLPE cable on Target 5 1 PE cable on each of Targets 4 and 6 | MOV-1 - source centered | IC: 1 XLPE cable on Source 1 1 PE cable on Source 2 1 PE cable with all three targets present (Targets 4, 5, and 6)
| Circuit Path 1: | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source connected to XLPE cable.
| Circuit Path 2: | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source connected to PE cable.
| Circuit Path 3: | Switch open: not connected | Switch open: not connected | Switch open: not connected | Switch open: not connected
| Circuit Path 4: | Passive target connected to all conductors of one 7/C XLPE cable | Passive target connected to all conductors of one 7/C XLPE cable | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation).
| Circuit Path 5: | Active target connected to all conductors of one 7/C XLPE cable | Active target connected to all conductors of one 7/C XLPE cable | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter
| Circuit Path 6: | Active target connected to all conductors of one 7/C XLPE cable | Active target connected to all conductors of one 7/C XLPE cable | Active Target: Connected to Motor Starter | Active Target: Connected to Motor Starter
| Circuit Path 7: | switch open - no connection | switch open - no connection | Switch Closed - Connects conductor to CPT neutral return and to ground (grounded CPT). | switch open - no connection
| Circuit Path 8: | switch open - no connection | switch open - no connection | Switch open - connected to spare conductor | switch open - no connection
| Circuit Path 9: | switch open - no connection | switch open - no connection | switch open - no connection | switch open - no connection
A Note on Data Conversion and Accuracy:
Each of the voltage and current transducers used produces a 4-20mA signal which is routed through 477ohm precision resistors converting the signal to a nominal 2-10 VDC signal. This DC voltage signal was monitored using a National Instruments PCI-6071E data aquisition (DAQ) card. These data as recorded are presented in the "Raw Test Data" worksheet. The raw data were converted to actual values as shown on the "Converted Test Data" worksheet. The conversion is based on the fact that the 4-20 mA signal corresponds to a full scale reading on the voltage transducers of 0-300 VAC and on the current transducers of 0-5A. Nominal zero point readings for each transducer were taken in a separate test run in order to establish more accurately the zero points for current and voltage measurement. The Zero Point values are provided, and the full run is documented in a separate data file (see 'Zero Points' worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Circuit Fault Summary
Summary of Circuit Faulting Behavior for all Tested Circuits
Circuit 1 | This circuit was configured for TS-to-TS inter-cable hot shorts only and is ungrounded. There was no return path present so a fuse blow was not possible. Hot shorts can occur due to concurrent ground faults or direct cable-to-cable interactions. The first hot short observed likely resulted from direct cable-to-cable interactions, although this cannot be definitively established. The fault was sudden and of high qaulity raising the target to full source potential within less than 1s. This behavior would be expected with direct conductor to conductor shorting, but not due to mutual ground faults. This is in contrast to the hot shorts impacting targets 4 and 5 later in the test. Path 4 experiences a prolonged period (1000s) of rising voltage indicating a slowly developing short circuit. Path 5 sees similar shorting over a period of 170s. Neither path 4 or 5 reaches the full energizing source potential, and path 5 in particular fluctuates considerably throughout the remainder of the test. These are both indications of more tenuous faults of somewhat lower quality and are likely due to mutual ground faults.
Circuit 2 | This circuit was set up to detect inter-cable hot shorts in a mixed bundle of TS and TP cables. At 286 seconds, one of the source cables (on Path 1) shorts to ground and causes a fuse blow failure. No cable-to-cable interactions are indicated.
Circuit 3 | The circuit experience a fuse blow and no spurious operations.
Circuit 4 | This circuit was set up in an inter-cable configuration in a mixed bundel of TS and TP cables. The circuit experiences a fuse blow and no detected inter-cable hot shorts. It appears that the energized PE cable shorted to ground causing the fuse blow.
Note:

## Circuit 1 Faulting
Summary of Observed Faulting Behavior for Circuit #1
DAQ Time | Burner Time | Event | Discussion
221 | 0 | Ignited Gas Burner
Summary observations |  | Failure | This circuit was configured for TS-to-TS inter-cable hot shorts only and is ungrounded. There was no return path present so a fuse blow was not possible. Hot shorts can occur due to concurrent ground faults or direct cable-to-cable interactions. The first hot short observed likely resulted from direct cable-to-cable interactions, although this cannot be definitively established. The fault was sudden and of high qaulity raising the target to full source potential within less than 1s. This behavior would be expected with direct conductor to conductor shorting, but not due to mutual ground faults. This is in contrast to the hot shorts impacting targets 4 and 5 later in the test. Path 4 experiences a prolonged period (1000s) of rising voltage indicating a slowly developing short circuit. Path 5 sees similar shorting over a period of 170s. Neither path 4 or 5 reaches the full energizing source potential, and path 5 in particular fluctuates considerably throughout the remainder of the test. These are both indications of more tenuous faults of somewhat lower quality and are likely due to mutual ground faults.

## Converted Data C1
DAQ Time | Burner Time | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6
0 | -221 | 129.8603 | 0.0089549 | 129.4658 | 0.0047816 | 0.18729 | 0.00060315 | 0.23811 | 0.0017265 | 0.28424 | 0.0002934
10 | -211 | 129.7643 | 0.0089549 | 129.4658 | 0.0047816 | 0.18729 | 0.00060315 | 0.23811 | 0.00012733 | 0.28424 | 0.0002934
20 | -201 | 129.7643 | 0.0089549 | 129.4658 | 0.0047816 | 0.18729 | 0.00060315 | 0.23811 | 0.00012733 | 0.18829 | 0.0002934
30 | -191 | 129.6683 | 0.010554 | 129.3698 | 0.0047816 | 0.18729 | 0.00060315 | 0.23811 | 0.00012733 | 0.28424 | 0.0002934
40 | -181 | 129.5724 | 0.010554 | 129.3698 | 0.0063808 | 0.18729 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
50 | -171 | 129.4764 | 0.012154 | 129.1779 | 0.0063808 | 0.18729 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
60 | -161 | 129.4764 | 0.010554 | 129.1779 | 0.0047816 | 0.18729 | 0.00060315 | 0.23811 | 0.00012733 | 0.28424 | 0.0002934
70 | -151 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.18729 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
80 | -141 | 129.2844 | 0.0057559 | 128.9859 | 0.0015826 | 0.18729 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
90 | -131 | 129.1885 | 0.0057559 | 128.89 | 0.0015826 | 0.37923 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
100 | -121 | 129.4764 | 0.0057559 | 129.0819 | 0.0015826 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
110 | -111 | 129.6683 | 0.0057559 | 129.2738 | 0.0015826 | 0.47518 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0018926
120 | -101 | 129.4764 | 0.0057559 | 129.1779 | 0.0015826 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
130 | -91 | 128.4208 | 0.0057559 | 129.7537 | 0.0015826 | 0.47518 | 0.0022023 | 0.526 | 0.0017265 | 0.66813 | 0.0002934
140 | -81 | 129.4764 | 0.0041567 | 129.0819 | 0.0031824 | 0.47518 | 0.0022023 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
150 | -71 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
160 | -61 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
170 | -51 | 129.2844 | 0.012154 | 128.9859 | 0.0063808 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
180 | -41 | 129.3804 | 0.010554 | 129.0819 | 0.0063808 | 0.18729 | 0.00060315 | 0.33406 | 0.0017265 | 0.28424 | 0.0002934
190 | -31 | 129.3804 | 0.010554 | 128.9859 | 0.0047816 | 0.28324 | 0.00060315 | 0.23811 | 0.0017265 | 0.28424 | 0.0002934
200 | -21 | 129.1885 | 0.010554 | 128.89 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
210 | -11 | 129.0925 | 0.010554 | 128.794 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
220 | -1 | 129.0925 | 0.010554 | 128.794 | 0.0047816 | 0.18729 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
230 | 9 | 129.0925 | 0.0089549 | 128.698 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.28424 | 0.0002934
240 | 19 | 129.0925 | 0.0057559 | 128.698 | 0.0015826 | 0.37923 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
250 | 29 | 129.1885 | 0.0073551 | 128.794 | 0.0015826 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934
260 | 39 | 129.6683 | 0.0073551 | 129.1779 | 0.0015826 | 0.57118 | 0.0022023 | 0.71795 | 0.0017265 | 0.66813 | 0.0018926
270 | 49 | 129.7643 | 0.0057559 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.66813 | 0.0018926
270.2 | 49.2 | 129.7643 | 0.0073551 | 129.3698 | 0.0015826 | 0.76308 | 0.0022023 | 0.71795 | 0.0033264 | 0.76408 | 0.0034924
270.4 | 49.4 | 129.7643 | 0.0057559 | 129.3698 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.66813 | 0.0034924
270.6 | 49.6 | 129.7643 | 0.0073551 | 129.3698 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.76408 | 0.0018926
270.8 | 49.8 | 129.6683 | 0.0073551 | 129.3698 | 0.0031824 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.76408 | 0.0034924
271 | 50 | 129.6683 | 0.0057559 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.76408 | 0.0034924
271.2 | 50.2 | 129.7643 | 0.0073551 | 129.2738 | 0.0031824 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.76408 | 0.0034924
271.4 | 50.4 | 129.6683 | 0.0073551 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.76408 | 0.0034924
271.6 | 50.6 | 129.7643 | 0.0057559 | 129.3698 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.76408 | 0.0034924
271.8 | 50.8 | 129.6683 | 0.0073551 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
272 | 51 | 129.6683 | 0.0057559 | 129.1779 | 0.0031824 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0018926
272.2 | 51.2 | 129.6683 | 0.0073551 | 129.2738 | 0.0015826 | 0.57118 | 0.0022023 | 0.62195 | 0.0033264 | 0.76408 | 0.0018926
272.4 | 51.4 | 129.6683 | 0.0073551 | 129.1779 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.76408 | 0.0018926
272.6 | 51.6 | 129.6683 | 0.0073551 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924
272.8 | 51.8 | 129.6683 | 0.0057559 | 129.2738 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
273 | 52 | 129.6683 | 0.0073551 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
273.2 | 52.2 | 129.6683 | 0.0057559 | 129.2738 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0018926
273.4 | 52.4 | 129.6683 | 0.0073551 | 129.1779 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.76408 | 0.0034924
273.6 | 52.6 | 129.6683 | 0.0073551 | 129.2738 | 0.0015826 | 0.66713 | 0.0022023 | 0.71795 | 0.0033264 | 0.66813 | 0.0034924
273.8 | 52.8 | 129.6683 | 0.0057559 | 129.1779 | 0.0031824 | 0.57118 | 0.0022023 | 0.71795 | 0.0033264 | 0.66813 | 0.0034924
274 | 53 | 129.5724 | 0.0073551 | 129.1779 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0018926
274.2 | 53.2 | 129.5724 | 0.0073551 | 129.1779 | 0.0031824 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.66813 | 0.0018926
274.4 | 53.4 | 129.5724 | 0.0073551 | 129.1779 | 0.0015826 | 0.57118 | 0.0022023 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
274.6 | 53.6 | 129.5724 | 0.0057559 | 129.1779 | 0.0015826 | 0.66713 | 0.0022023 | 0.62195 | 0.0017265 | 0.76408 | 0.0018926
274.8 | 53.8 | 129.5724 | 0.0057559 | 129.0819 | 0.0031824 | 0.57118 | 0.0022023 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
275 | 54 | 129.5724 | 0.0073551 | 129.1779 | 0.0015826 | 0.66713 | 0.0038022 | 0.71795 | 0.0033264 | 0.66813 | 0.0034924
275.2 | 54.2 | 129.5724 | 0.0057559 | 129.0819 | 0.0015826 | 0.57118 | 0.0022023 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
275.4 | 54.4 | 129.5724 | 0.0073551 | 129.1779 | 0.0015826 | 0.57118 | 0.0022023 | 0.71795 | 0.0033264 | 0.66813 | 0.0034924
275.6 | 54.6 | 129.4764 | 0.0057559 | 129.0819 | 0.0015826 | 0.66713 | 0.0038022 | 0.62195 | 0.0017265 | 0.66813 | 0.0034924
275.8 | 54.8 | 129.5724 | 0.0057559 | 128.9859 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924
276 | 55 | 129.3804 | 0.0073551 | 128.89 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
276.2 | 55.2 | 129.4764 | 0.0057559 | 128.9859 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0034924
276.4 | 55.4 | 129.4764 | 0.0057559 | 129.0819 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
276.6 | 55.6 | 129.4764 | 0.0073551 | 128.9859 | 0.0015826 | 0.47518 | 0.0038022 | 0.62195 | 0.0033264 | 0.57213 | 0.0018926
276.8 | 55.8 | 129.4764 | 0.0073551 | 128.9859 | 0.0031824 | 0.57118 | 0.0022023 | 0.62195 | 0.0033264 | 0.57213 | 0.0018926
277 | 56 | 129.4764 | 0.0057559 | 128.9859 | 0.0031824 | 0.57118 | 0.0038022 | 0.62195 | 0.0017265 | 0.57213 | 0.0018926
277.2 | 56.2 | 129.4764 | 0.0073551 | 128.9859 | 0.0015826 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0018926
277.4 | 56.4 | 129.3804 | 0.0073551 | 128.9859 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0033264 | 0.66813 | 0.0018926
277.6 | 56.6 | 129.3804 | 0.0073551 | 128.89 | 0.0015826 | 0.57118 | 0.0038022 | 0.526 | 0.0033264 | 0.66813 | 0.0018926
277.8 | 56.8 | 129.3804 | 0.0057559 | 128.9859 | 0.0015826 | 0.47518 | 0.0022023 | 0.62195 | 0.0017265 | 0.57213 | 0.0018926
278 | 57 | 129.3804 | 0.0073551 | 128.89 | 0.0015826 | 0.57118 | 0.0038022 | 0.62195 | 0.0017265 | 0.57213 | 0.0018926
278.2 | 57.2 | 129.3804 | 0.0057559 | 128.89 | 0.0015826 | 0.57118 | 0.0022023 | 0.62195 | 0.0033264 | 0.57213 | 0.0018926
278.4 | 57.4 | 129.3804 | 0.0073551 | 128.89 | 0.0015826 | 0.57118 | 0.0022023 | 0.62195 | 0.0017265 | 0.57213 | 0.0018926
278.6 | 57.6 | 129.3804 | 0.0073551 | 128.9859 | 0.0031824 | 0.47518 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0018926
278.8 | 57.8 | 129.3804 | 0.0073551 | 128.9859 | 0.0015826 | 0.47518 | 0.0022023 | 0.526 | 0.0017265 | 0.66813 | 0.0018926
279 | 58 | 129.2844 | 0.0057559 | 128.794 | 0.0015826 | 0.47518 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0018926
279.2 | 58.2 | 129.2844 | 0.0073551 | 128.89 | 0.0015826 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0018926
279.4 | 58.4 | 129.2844 | 0.0073551 | 128.89 | 0.0015826 | 0.47518 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0018926
279.6 | 58.6 | 129.1885 | 0.0073551 | 128.794 | 0.0015826 | 0.47518 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
279.8 | 58.8 | 129.2844 | 0.0057559 | 128.794 | 0.0015826 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.57213 | 0.0018926
280 | 59 | 129.0925 | 0.0073551 | 128.794 | 0.0015826 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
280.2 | 59.2 | 129.0925 | 0.0073551 | 128.698 | 0.0015826 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.57213 | 0.0018926
280.4 | 59.4 | 129.0925 | 0.0073551 | 128.698 | 0.0015826 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934
280.6 | 59.6 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934
280.8 | 59.8 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.00060315 | 0.526 | 0.00012733 | 0.47618 | 0.0002934
281 | 60 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
281.2 | 60.2 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934
281.4 | 60.4 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.37923 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926
281.6 | 60.6 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
281.8 | 60.8 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934
282 | 61 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.37923 | 0.00060315 | 0.43001 | 0.00012733 | 0.47618 | 0.0002934
282.2 | 61.2 | 129.0925 | 0.0073551 | 128.602 | 0.0031824 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
282.4 | 61.4 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
282.6 | 61.6 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
282.8 | 61.8 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934
283 | 62 | 129.0925 | 0.0073551 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
283.2 | 62.2 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
283.4 | 62.4 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
283.6 | 62.6 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926
283.8 | 62.8 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.18729 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
284 | 63 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.37923 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926
284.2 | 63.2 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
284.4 | 63.4 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926
284.6 | 63.6 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
284.8 | 63.8 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
285 | 64 | 128.9966 | 0.0073551 | 128.698 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
285.2 | 64.2 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
285.4 | 64.4 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
285.6 | 64.6 | 128.9966 | 0.0089549 | 128.602 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
285.8 | 64.8 | 128.9966 | 0.0073551 | 128.602 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
286 | 65 | 128.9006 | 0.0073551 | 128.602 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
286.2 | 65.2 | 125.3498 | 0.0089549 | 125.0513 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.28424 | 0.0018926
286.4 | 65.4 | 128.8046 | 0.0089549 | 128.5061 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
286.6 | 65.6 | 129.0925 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
286.8 | 65.8 | 129.0925 | 0.0073551 | 128.698 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
287 | 66 | 129.0925 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
287.2 | 66.2 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
287.4 | 66.4 | 129.1885 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926
287.6 | 66.6 | 129.0925 | 0.0073551 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934
287.8 | 66.8 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
288 | 67 | 128.9966 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
288.2 | 67.2 | 129.0925 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926
288.4 | 67.4 | 129.0925 | 0.010554 | 128.794 | 0.0047816 | 0.18729 | 0.0022023 | 0.33406 | 0.0017265 | 0.28424 | 0.0002934
288.6 | 67.6 | 129.0925 | 0.0089549 | 128.698 | 0.0031824 | 0.18729 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926
288.8 | 67.8 | 129.0925 | 0.0089549 | 128.698 | 0.0047816 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934
289 | 68 | 129.0925 | 0.0089549 | 128.698 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0018926
289.2 | 68.2 | 128.9966 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
289.4 | 68.4 | 129.0925 | 0.010554 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
289.6 | 68.6 | 128.9966 | 0.0089549 | 128.698 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
289.8 | 68.8 | 129.0925 | 0.0089549 | 128.698 | 0.0047816 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
290 | 69 | 129.0925 | 0.010554 | 128.698 | 0.0047816 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926
300 | 79 | 129.0925 | 0.010554 | 128.794 | 0.0063808 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
310 | 89 | 129.7643 | 0.012154 | 128.698 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934
320 | 99 | 129.1885 | 0.012154 | 128.794 | 0.0047816 | 0.18729 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
330 | 109 | 129.0925 | 0.0089549 | 128.698 | 0.0031824 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934
340 | 119 | 129.2844 | 0.0073551 | 128.794 | 0.0015826 | 0.28324 | 0.00060315 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
350 | 129 | 129.2844 | 0.0073551 | 128.89 | 0.0015826 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
360 | 139 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
370 | 149 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.00012733 | 0.28424 | 0.0002934
380 | 159 | 129.1885 | 0.010554 | 128.794 | 0.0047816 | 0.28324 | 0.0022023 | 0.33406 | 0.00012733 | 0.47618 | -0.0013064
390 | 169 | 129.1885 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.33406 | 0.00012733 | 0.38019 | 0.0002934
400 | 179 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.00060315 | 0.33406 | 0.0017265 | 0.38019 | 0.0002934
410 | 189 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.00012733 | 0.38019 | 0.0002934
420 | 199 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.33406 | 0.0017265 | 0.47618 | 0.0002934
430 | 209 | 129.3804 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0002934
440 | 219 | 129.3804 | 0.0073551 | 128.89 | 0.0015826 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.47618 | 0.0002934
450 | 229 | 129.4764 | 0.0073551 | 128.9859 | 0.0031824 | 0.66713 | 0.0038022 | 0.71795 | 0.0017265 | 0.66813 | 0.0018926
460 | 239 | 129.7643 | 0.0073551 | 129.2738 | 0.0015826 | 0.76308 | 0.0038022 | 0.8139 | 0.0033264 | 0.86003 | 0.0034924
470 | 249 | 129.8603 | 0.0073551 | 129.3698 | 0.0015826 | 0.85907 | 0.0054014 | 0.8139 | 0.0049255 | 0.86003 | 0.0034924
480 | 259 | 129.9562 | 0.0073551 | 129.3698 | 0.0031824 | 0.95502 | 0.0054014 | 0.90985 | 0.0049255 | 1.052 | 0.0034924
490 | 269 | 130.1482 | 0.0073551 | 129.5617 | 0.0031824 | 1.051 | 0.0054014 | 1.0058 | 0.0049255 | 0.95602 | 0.0050916
500 | 279 | 130.3401 | 0.0073551 | 129.7537 | 0.0031824 | 1.2429 | 0.0070012 | 1.1018 | 0.0065247 | 1.148 | 0.0050916
510 | 289 | 130.4361 | 0.0073551 | 129.7537 | 0.0031824 | 1.2429 | 0.0086004 | 1.1978 | 0.0065247 | 1.148 | 0.0066908
520 | 299 | 130.3401 | 0.0073551 | 129.7537 | 0.0031824 | 1.3389 | 0.0086004 | 1.1978 | 0.0065247 | 1.2439 | 0.0050916
530 | 309 | 130.3401 | 0.0073551 | 129.6577 | 0.0031824 | 1.2429 | 0.0086004 | 1.1018 | 0.0065247 | 1.148 | 0.0066908
540 | 319 | 129.9562 | 0.0073551 | 129.3698 | 0.0031824 | 0.95502 | 0.0070012 | 0.90985 | 0.0049255 | 1.052 | 0.0050916
550 | 329 | 129.4764 | 0.0057559 | 129.0819 | 0.0031824 | 0.57118 | 0.0054014 | 0.62195 | 0.0033264 | 0.66813 | 0.0034924
560 | 339 | 129.2844 | 0.0073551 | 128.89 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
570 | 349 | 130.0522 | 0.0073551 | 129.4658 | 0.0031824 | 1.147 | 0.0070012 | 1.1018 | 0.0049255 | 1.148 | 0.0066908
580 | 359 | 130.532 | 0.0073551 | 129.9456 | 0.0031824 | 1.5308 | 0.0086004 | 1.3897 | 0.0081246 | 1.4359 | 0.0066908
590 | 369 | 130.7239 | 0.0073551 | 130.0416 | 0.0031824 | 1.6268 | 0.0086004 | 1.4857 | 0.0081246 | 1.5318 | 0.0082906
600 | 379 | 130.628 | 0.0073551 | 130.0416 | 0.0031824 | 1.5308 | 0.0086004 | 1.2937 | 0.0081246 | 1.4359 | 0.0066908
610 | 389 | 130.9159 | 0.0089549 | 130.2335 | 0.0031824 | 1.7227 | 0.0102 | 1.4857 | 0.0081246 | 1.6278 | 0.0082906
620 | 399 | 130.2441 | 0.0089549 | 129.9456 | 0.0047816 | 1.5308 | 0.0086004 | 1.2937 | 0.0081246 | 1.3399 | 0.0050916
630 | 409 | 130.7239 | 0.0073551 | 130.0416 | 0.0031824 | 1.6268 | 0.0102 | 1.3897 | 0.0081246 | 1.5318 | 0.0082906
640 | 419 | 130.4361 | 0.0089549 | 129.7537 | 0.0031824 | 1.3389 | 0.0086004 | 1.4857 | 0.0081246 | 1.4359 | 0.0066908
650 | 429 | 130.628 | 0.0073551 | 130.0416 | 0.0031824 | 1.6268 | 0.0102 | 1.4857 | 0.0081246 | 1.5318 | 0.0082906
660 | 439 | 130.532 | 0.0073551 | 129.9456 | 0.0031824 | 1.5308 | 0.0086004 | 1.3897 | 0.0081246 | 1.5318 | 0.0082906
670 | 449 | 130.7239 | 0.0073551 | 130.0416 | 0.0031824 | 1.5308 | 0.0086004 | 1.3897 | 0.0081246 | 1.5318 | 0.0082906
680 | 459 | 130.7239 | 0.0073551 | 130.0416 | 0.0031824 | 1.6268 | 0.0102 | 1.3897 | 0.0081246 | 1.5318 | 0.0082906
690 | 469 | 130.2441 | 0.0073551 | 129.6577 | 0.0031824 | 1.2429 | 0.0086004 | 1.1978 | 0.0065247 | 1.2439 | 0.0066908
700 | 479 | 129.8603 | 0.0089549 | 129.3698 | 0.0031824 | 1.147 | 0.0070012 | 0.8139 | 0.0049255 | 0.76408 | 0.0050916
710 | 489 | 130.4361 | 0.0073551 | 129.7537 | 0.0031824 | 1.4349 | 0.0086004 | 1.2937 | 0.0081246 | 1.3399 | 0.0066908
720 | 499 | 130.4361 | 0.0073551 | 129.7537 | 0.0047816 | 1.4349 | 0.0102 | 1.3897 | 0.0081246 | 1.4359 | 0.0082906
730 | 509 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
740 | 519 | 128.7087 | 0.0073551 | 128.4101 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
750 | 529 | 128.8046 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
760 | 539 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
770 | 549 | 128.9966 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
780 | 559 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
790 | 569 | 128.9966 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0022023 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926
790.2 | 569.2 | 129.0925 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926
790.4 | 569.4 | 128.9966 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926
790.6 | 569.6 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
790.8 | 569.8 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.526 | 0.0017265 | 0.38019 | 0.0018926
791 | 570 | 128.9966 | 0.0057559 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
791.2 | 570.2 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
791.4 | 570.4 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
791.6 | 570.6 | 129.1885 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
791.8 | 570.8 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.38019 | 0.0018926
792 | 571 | 128.9966 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
792.2 | 571.2 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
792.4 | 571.4 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
792.6 | 571.6 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
792.8 | 571.8 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
793 | 572 | 129.0925 | 0.0089549 | 128.794 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
793.2 | 572.2 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
793.4 | 572.4 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
793.6 | 572.6 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
793.8 | 572.8 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
794 | 573 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934
794.2 | 573.2 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
794.4 | 573.4 | 129.0925 | 0.0089549 | 128.89 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
794.6 | 573.6 | 129.0925 | 0.0089549 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
794.8 | 573.8 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
795 | 574 | 129.0925 | 0.0089549 | 128.89 | 0.0047816 | 0.37923 | 0.0038022 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926
795.2 | 574.2 | 128.9966 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
795.4 | 574.4 | 129.0925 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
795.6 | 574.6 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
795.8 | 574.8 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
796 | 575 | 128.9966 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
796.2 | 575.2 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
796.4 | 575.4 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
796.6 | 575.6 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
796.8 | 575.8 | 129.0925 | 0.0089549 | 128.89 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
797 | 576 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
797.2 | 576.2 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
797.4 | 576.4 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.526 | 0.0033264 | 0.38019 | 0.0002934
797.6 | 576.6 | 128.9966 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.33406 | 0.0017265 | 0.38019 | 0.0018926
797.8 | 576.8 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0018926
798 | 577 | 128.9966 | 0.0073551 | 128.698 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
798.2 | 577.2 | 128.9966 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
798.4 | 577.4 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
798.6 | 577.6 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.38019 | 0.0018926
798.8 | 577.8 | 128.9966 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
799 | 578 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
799.2 | 578.2 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924
799.4 | 578.4 | 129.0925 | 0.0089549 | 128.794 | 0.0047816 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
799.6 | 578.6 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
799.8 | 578.8 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
800 | 579 | 128.9966 | 0.0073551 | 128.698 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
800.2 | 579.2 | 129.0925 | 0.0089549 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
800.4 | 579.4 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
800.6 | 579.6 | 129.0925 | 0.0089549 | 128.89 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
800.8 | 579.8 | 129.1885 | 0.0073551 | 128.794 | 0.0047816 | 0.28324 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
801 | 580 | 126.0216 | 0.0089549 | 125.723 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
801.2 | 580.2 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 0.37923 | 0.0022023 | 0.33406 | 0.0033264 | 0.47618 | 0.0018926
801.4 | 580.4 | 129.1885 | 0.0073551 | 128.89 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
801.6 | 580.6 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0002934
801.8 | 580.8 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
802 | 581 | 129.0925 | 0.0073551 | 128.794 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
802.2 | 581.2 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
802.4 | 581.4 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924
802.6 | 581.6 | 129.0925 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
802.8 | 581.8 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924
803 | 582 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
803.2 | 582.2 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
803.4 | 582.4 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
803.6 | 582.6 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
803.8 | 582.8 | 129.0925 | 0.0073551 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.33406 | 0.0017265 | 0.47618 | 0.0018926
804 | 583 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
804.2 | 583.2 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
804.4 | 583.4 | 129.1885 | 0.0073551 | 128.89 | 0.0047816 | 0.37923 | 0.0038022 | 0.526 | 0.0017265 | 0.38019 | 0.0002934
804.6 | 583.6 | 129.1885 | 0.0073551 | 128.9859 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
804.8 | 583.8 | 129.1885 | 0.0073551 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
805 | 584 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0022023 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
805.2 | 584.2 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
805.4 | 584.4 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
805.6 | 584.6 | 129.1885 | 0.0073551 | 128.89 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
805.8 | 584.8 | 129.1885 | 0.0089549 | 128.794 | 0.0031824 | 0.28324 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
806 | 585 | 129.0925 | 0.0089549 | 128.794 | 0.0047816 | 0.37923 | 0.0022023 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
806.2 | 585.2 | 129.0925 | 0.0073551 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
806.4 | 585.4 | 129.0925 | 0.0089549 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0034924
806.6 | 585.6 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.38019 | 0.0018926
806.8 | 585.8 | 129.0925 | 0.0073551 | 128.89 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
807 | 586 | 129.1885 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
808 | 587 | 129.0925 | 0.0089549 | 128.89 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0017265 | 0.38019 | 0.0018926
810 | 589 | 129.0925 | 0.0073551 | 128.794 | 0.0031824 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
820 | 599 | 129.1885 | 0.0073551 | 128.9859 | 0.0031824 | 0.28324 | 0.0038022 | 0.43001 | 0.0017265 | 0.47618 | 0.0018926
830 | 609 | 129.2844 | 0.0073551 | 128.9859 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
840 | 619 | 129.6683 | 0.0073551 | 129.2738 | 0.0047816 | 0.76308 | 0.0070012 | 0.8139 | 0.0049255 | 0.86003 | 0.0050916
850 | 629 | 129.9562 | 0.0089549 | 129.3698 | 0.0047816 | 0.95502 | 0.0070012 | 0.90985 | 0.0065247 | 0.95602 | 0.0050916
860 | 639 | 130.2441 | 0.0073551 | 129.5617 | 0.0047816 | 1.2429 | 0.0086004 | 1.1018 | 0.0065247 | 1.2439 | 0.0066908
870 | 649 | 129.9562 | 0.0073551 | 129.4658 | 0.0047816 | 1.2429 | 0.0086004 | 1.0058 | 0.0065247 | 1.052 | 0.0050916
880 | 659 | 129.6683 | 0.0089549 | 129.1779 | 0.0047816 | 0.76308 | 0.0054014 | 0.8139 | 0.0049255 | 0.86003 | 0.0050916
890 | 669 | 130.4361 | 0.0089549 | 129.8496 | 0.0047816 | 1.3389 | 0.0086004 | 1.1978 | 0.0081246 | 1.3399 | 0.0066908
900 | 679 | 130.7239 | 0.0073551 | 130.0416 | 0.0047816 | 1.6268 | 0.011799 | 1.4857 | 0.0097238 | 1.5318 | 0.0098898
910 | 689 | 130.7239 | 0.0089549 | 130.0416 | 0.0047816 | 1.7227 | 0.0102 | 1.4857 | 0.0097238 | 1.6278 | 0.0098898
920 | 699 | 129.9562 | 0.0089549 | 129.4658 | 0.0031824 | 1.051 | 0.0086004 | 1.0058 | 0.0065247 | 1.052 | 0.0066908
930 | 709 | 129.2844 | 0.0089549 | 128.794 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924
940 | 719 | 129.1885 | 0.0073551 | 128.794 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924
950 | 729 | 129.3804 | 0.0089549 | 128.9859 | 0.0047816 | 0.57118 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
960 | 739 | 129.3804 | 0.0089549 | 128.9859 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924
970 | 749 | 129.5724 | 0.0089549 | 129.0819 | 0.0047816 | 0.57118 | 0.0054014 | 0.62195 | 0.0033264 | 0.57213 | 0.0050916
980 | 759 | 129.7643 | 0.0073551 | 129.3698 | 0.0047816 | 0.85907 | 0.0054014 | 0.90985 | 0.0049255 | 0.95602 | 0.0050916
990 | 769 | 130.1482 | 0.0089549 | 129.5617 | 0.0047816 | 1.147 | 0.0086004 | 1.0058 | 0.0081246 | 1.148 | 0.0066908
1000 | 779 | 130.1482 | 0.0073551 | 129.6577 | 0.0047816 | 1.147 | 0.0102 | 1.1018 | 0.0065247 | 1.2439 | 0.0082906
1010 | 789 | 129.5724 | 0.0089549 | 129.0819 | 0.0047816 | 0.66713 | 0.0070012 | 0.71795 | 0.0049255 | 0.76408 | 0.0034924
1020 | 799 | 129.4764 | 0.0089549 | 129.0819 | 0.0047816 | 0.57118 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924
1030 | 809 | 129.4764 | 0.0089549 | 128.9859 | 0.0047816 | 0.66713 | 0.0054014 | 0.71795 | 0.0049255 | 0.76408 | 0.0050916
1040 | 819 | 129.1885 | 0.0089549 | 128.794 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924
1050 | 829 | 128.8046 | 0.0089549 | 128.5061 | 0.0047816 | 0.47518 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924
1060 | 839 | 128.6127 | 0.0089549 | 128.5061 | 0.0047816 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924
1070 | 849 | 128.6127 | 0.0089549 | 128.4101 | 0.0047816 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
1080 | 859 | 128.8046 | 0.0073551 | 128.602 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1090 | 869 | 128.9966 | 0.0073551 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
1100 | 879 | 129.0925 | 0.0089549 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1110 | 889 | 129.0925 | 0.010554 | 128.794 | 0.0047816 | 0.47518 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1120 | 899 | 128.9966 | 0.0089549 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.47618 | 0.0034924
1130 | 909 | 128.9006 | 0.0073551 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1140 | 919 | 128.9006 | 0.0073551 | 128.698 | 0.0047816 | 0.37923 | 0.0038022 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
1150 | 929 | 128.9006 | 0.0073551 | 128.698 | 0.0047816 | 0.37923 | 0.0038022 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1160 | 939 | 129.0925 | 0.0089549 | 128.794 | 0.0047816 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924
1170 | 949 | 129.0925 | 0.010554 | 128.794 | 0.0047816 | 0.37923 | 0.0038022 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924
1180 | 959 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1190 | 969 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 0.47518 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
1200 | 979 | 129.7643 | 0.0089549 | 128.89 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
1210 | 989 | 129.1885 | 0.0089549 | 128.698 | 0.0047816 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924
1220 | 999 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 0.37923 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1230 | 1009 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 0.47518 | 0.0038022 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1240 | 1019 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0018926
1240.2 | 1019.2 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 0.37923 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1250 | 1029 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 0.37923 | 0.0054014 | 0.43001 | 0.0033264 | 0.47618 | 0.0034924
1260 | 1039 | 129.4764 | 0.0089549 | 129.0819 | 0.0047816 | 0.66713 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0034924
1270 | 1049 | 130.2441 | 0.0089549 | 129.6577 | 0.0063808 | 1.3389 | 0.0102 | 1.1978 | 0.0081246 | 1.2439 | 0.0082906
1280 | 1059 | 130.8199 | 0.0089549 | 130.1375 | 0.0047816 | 1.8187 | 0.011799 | 1.5816 | 0.011324 | 1.7237 | 0.01149
1290 | 1069 | 129.8603 | 0.0089549 | 129.8496 | 0.0063808 | 1.4349 | 0.011799 | 2.0615 | 0.011324 | 2.0116 | 0.013089
1300 | 1079 | 130.628 | 0.0089549 | 129.9456 | 0.0047816 | 1.5308 | 0.0102 | 1.3897 | 0.011324 | 1.5318 | 0.0082906
1310 | 1089 | 129.6683 | 0.0089549 | 129.1779 | 0.0047816 | 0.85907 | 0.0070012 | 0.8139 | 0.0065247 | 0.86003 | 0.0066908
1320 | 1099 | 129.6683 | 0.0089549 | 129.1779 | 0.0047816 | 0.95502 | 0.0070012 | 0.90985 | 0.0065247 | 0.95602 | 0.0066908
1330 | 1109 | 130.4361 | 0.010554 | 129.8496 | 0.0047816 | 1.5308 | 0.0102 | 1.3897 | 0.0097238 | 1.4359 | 0.0082906
1340 | 1119 | 130.7239 | 0.0089549 | 130.0416 | 0.0047816 | 1.7227 | 0.011799 | 1.5816 | 0.011324 | 1.6278 | 0.0098898
1350 | 1129 | 130.1482 | 0.0089549 | 129.5617 | 0.0047816 | 1.4349 | 0.0102 | 1.1978 | 0.0097238 | 1.3399 | 0.0082906
1360 | 1139 | 129.6683 | 0.0073551 | 129.2738 | 0.0047816 | 1.051 | 0.0086004 | 0.90985 | 0.0065247 | 0.86003 | 0.0066908
1370 | 1149 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 0.47518 | 0.0038022 | 0.526 | 0.0033264 | 0.47618 | 0.0034924
1380 | 1159 | 128.9966 | 0.0089549 | 128.794 | 0.0063808 | 0.47518 | 0.0054014 | 0.43001 | 0.0049255 | 0.38019 | 0.0034924
1390 | 1169 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 0.66713 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1400 | 1179 | 129.8603 | 0.0089549 | 129.3698 | 0.0063808 | 1.4349 | 0.0070012 | 0.8139 | 0.0065247 | 0.76408 | 0.0066908
1410 | 1189 | 130.2441 | 0.0089549 | 129.7537 | 0.0047816 | 2.0107 | 0.0102 | 1.1018 | 0.0081246 | 1.052 | 0.0066908
1420 | 1199 | 130.1482 | 0.010554 | 129.5617 | 0.0063808 | 2.2986 | 0.0086004 | 1.1018 | 0.0081246 | 1.148 | 0.0082906
1430 | 1209 | 130.2441 | 0.0089549 | 129.4658 | 0.0063808 | 2.5865 | 0.0086004 | 1.1018 | 0.0081246 | 1.2439 | 0.0066908
1440 | 1219 | 130.532 | 0.010554 | 129.9456 | 0.0047816 | 3.2582 | 0.011799 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1450 | 1229 | 130.7239 | 0.010554 | 130.2335 | 0.0063808 | 3.834 | 0.011799 | 1.4857 | 0.0097238 | 1.6278 | 0.0098898
1450.2 | 1229.2 | 130.9159 | 0.0089549 | 130.3295 | 0.0047816 | 3.834 | 0.013399 | 1.4857 | 0.011324 | 1.6278 | 0.01149
1450.4 | 1229.4 | 131.0119 | 0.010554 | 130.4254 | 0.0063808 | 3.834 | 0.011799 | 1.5816 | 0.011324 | 1.6278 | 0.0098898
1450.6 | 1229.6 | 131.0119 | 0.010554 | 130.3295 | 0.0047816 | 3.93 | 0.013399 | 1.5816 | 0.011324 | 1.6278 | 0.0098898
1450.8 | 1229.8 | 131.0119 | 0.0089549 | 130.3295 | 0.0063808 | 3.93 | 0.011799 | 1.5816 | 0.011324 | 1.6278 | 0.0098898
1451 | 1230 | 131.0119 | 0.0089549 | 130.4254 | 0.0063808 | 3.93 | 0.011799 | 1.5816 | 0.011324 | 1.6278 | 0.01149
1451.2 | 1230.2 | 131.0119 | 0.0089549 | 130.4254 | 0.0063808 | 3.93 | 0.011799 | 1.5816 | 0.011324 | 1.6278 | 0.01149
1451.4 | 1230.4 | 131.0119 | 0.0089549 | 130.4254 | 0.0047816 | 3.93 | 0.011799 | 1.5816 | 0.011324 | 1.7237 | 0.0098898
1451.6 | 1230.6 | 131.0119 | 0.010554 | 130.4254 | 0.0063808 | 3.93 | 0.013399 | 1.5816 | 0.011324 | 1.6278 | 0.01149
1451.8 | 1230.8 | 131.1078 | 0.0089549 | 130.5214 | 0.0063808 | 4.026 | 0.013399 | 1.6776 | 0.012923 | 1.6278 | 0.01149
1452 | 1231 | 131.0119 | 0.0089549 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.5816 | 0.011324 | 1.6278 | 0.01149
1452.2 | 1231.2 | 131.0119 | 0.0089549 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.5816 | 0.011324 | 1.7237 | 0.01149
1452.4 | 1231.4 | 131.1078 | 0.0089549 | 130.4254 | 0.0047816 | 4.026 | 0.013399 | 1.6776 | 0.011324 | 1.7237 | 0.0098898
1452.6 | 1231.6 | 131.1078 | 0.010554 | 130.4254 | 0.0047816 | 4.026 | 0.013399 | 1.5816 | 0.011324 | 1.7237 | 0.0098898
1452.8 | 1231.8 | 131.1078 | 0.0089549 | 130.5214 | 0.0063808 | 4.026 | 0.013399 | 1.5816 | 0.012923 | 1.6278 | 0.01149
1453 | 1232 | 131.1078 | 0.0089549 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.6776 | 0.012923 | 1.7237 | 0.01149
1453.2 | 1232.2 | 131.1078 | 0.0089549 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.6776 | 0.012923 | 1.7237 | 0.01149
1453.4 | 1232.4 | 131.0119 | 0.0089549 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.6776 | 0.012923 | 1.7237 | 0.01149
1453.6 | 1232.6 | 131.0119 | 0.0089549 | 130.4254 | 0.0047816 | 4.026 | 0.013399 | 1.5816 | 0.011324 | 1.7237 | 0.01149
1453.8 | 1232.8 | 131.0119 | 0.010554 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.5816 | 0.012923 | 1.7237 | 0.01149
1454 | 1233 | 131.0119 | 0.010554 | 130.3295 | 0.0063808 | 4.026 | 0.013399 | 1.6776 | 0.012923 | 1.8197 | 0.01149
1454.2 | 1233.2 | 131.1078 | 0.010554 | 130.4254 | 0.0063808 | 4.026 | 0.013399 | 1.6776 | 0.011324 | 1.6278 | 0.01149
1454.4 | 1233.4 | 130.9159 | 0.010554 | 130.3295 | 0.0063808 | 4.026 | 0.011799 | 1.6776 | 0.011324 | 1.7237 | 0.01149
1454.6 | 1233.6 | 130.9159 | 0.0089549 | 130.3295 | 0.0063808 | 4.026 | 0.011799 | 1.4857 | 0.011324 | 1.7237 | 0.0098898
1454.8 | 1233.8 | 130.9159 | 0.0089549 | 130.3295 | 0.0047816 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.01149
1455 | 1234 | 130.9159 | 0.010554 | 130.2335 | 0.0047816 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1455.2 | 1234.2 | 130.9159 | 0.0089549 | 130.2335 | 0.0047816 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.01149
1455.4 | 1234.4 | 130.8199 | 0.0089549 | 130.2335 | 0.0063808 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1455.6 | 1234.6 | 130.8199 | 0.0089549 | 130.2335 | 0.0063808 | 4.026 | 0.011799 | 1.4857 | 0.0097238 | 1.6278 | 0.01149
1455.8 | 1234.8 | 130.8199 | 0.0089549 | 130.2335 | 0.0063808 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1456 | 1235 | 130.8199 | 0.010554 | 130.2335 | 0.0047816 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1456.2 | 1235.2 | 130.9159 | 0.0089549 | 130.2335 | 0.0063808 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.5318 | 0.0098898
1456.4 | 1235.4 | 130.8199 | 0.010554 | 130.2335 | 0.0063808 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.5318 | 0.01149
1456.6 | 1235.6 | 130.9159 | 0.010554 | 130.3295 | 0.0063808 | 3.93 | 0.011799 | 1.4857 | 0.011324 | 1.5318 | 0.01149
1456.8 | 1235.8 | 130.8199 | 0.0089549 | 130.2335 | 0.0063808 | 4.026 | 0.011799 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1457 | 1236 | 130.9159 | 0.0089549 | 130.2335 | 0.0047816 | 4.026 | 0.011799 | 1.3897 | 0.011324 | 1.5318 | 0.01149
1457.2 | 1236.2 | 130.9159 | 0.010554 | 130.2335 | 0.0063808 | 4.026 | 0.011799 | 1.4857 | 0.011324 | 1.5318 | 0.01149
1457.4 | 1236.4 | 130.9159 | 0.0089549 | 130.2335 | 0.0063808 | 4.026 | 0.013399 | 1.3897 | 0.011324 | 1.5318 | 0.0098898
1457.6 | 1236.6 | 130.9159 | 0.0089549 | 130.3295 | 0.0063808 | 4.026 | 0.011799 | 1.5816 | 0.011324 | 1.6278 | 0.01149
1457.8 | 1236.8 | 130.8199 | 0.0089549 | 130.2335 | 0.0047816 | 4.026 | 0.011799 | 1.4857 | 0.011324 | 1.5318 | 0.01149
1458 | 1237 | 130.8199 | 0.010554 | 130.2335 | 0.0063808 | 4.026 | 0.011799 | 1.4857 | 0.011324 | 1.5318 | 0.01149
1458.2 | 1237.2 | 130.8199 | 0.010554 | 130.2335 | 0.0047816 | 4.026 | 0.013399 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1458.4 | 1237.4 | 130.8199 | 0.0089549 | 130.2335 | 0.0047816 | 4.122 | 0.013399 | 1.4857 | 0.011324 | 1.6278 | 0.0098898
1458.6 | 1237.6 | 130.7239 | 0.010554 | 130.1375 | 0.0047816 | 4.026 | 0.013399 | 1.3897 | 0.0097238 | 1.5318 | 0.0098898
1458.8 | 1237.8 | 130.628 | 0.010554 | 130.1375 | 0.0063808 | 4.026 | 0.011799 | 1.4857 | 0.0097238 | 1.6278 | 0.0098898
1459 | 1238 | 130.7239 | 0.0089549 | 130.1375 | 0.0047816 | 4.026 | 0.011799 | 1.3897 | 0.0097238 | 1.5318 | 0.01149
1459.2 | 1238.2 | 130.7239 | 0.0089549 | 130.1375 | 0.0047816 | 3.93 | 0.011799 | 1.3897 | 0.011324 | 1.5318 | 0.0098898
1459.4 | 1238.4 | 130.628 | 0.010554 | 130.1375 | 0.0063808 | 3.93 | 0.011799 | 1.3897 | 0.011324 | 1.5318 | 0.0098898
1459.6 | 1238.6 | 130.7239 | 0.0089549 | 130.1375 | 0.0063808 | 4.026 | 0.011799 | 1.3897 | 0.011324 | 1.5318 | 0.01149
1459.8 | 1238.8 | 130.7239 | 0.010554 | 130.0416 | 0.0047816 | 4.026 | 0.011799 | 1.3897 | 0.011324 | 1.5318 | 0.0098898
1460 | 1239 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 3.93 | 0.011799 | 1.3897 | 0.0097238 | 1.5318 | 0.01149
1460.2 | 1239.2 | 130.628 | 0.010554 | 130.0416 | 0.0047816 | 4.026 | 0.0102 | 1.3897 | 0.011324 | 1.5318 | 0.0098898
1460.4 | 1239.4 | 130.7239 | 0.010554 | 130.1375 | 0.0063808 | 4.026 | 0.011799 | 1.3897 | 0.011324 | 1.4359 | 0.0098898
1460.6 | 1239.6 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.026 | 0.011799 | 1.3897 | 0.011324 | 1.4359 | 0.0098898
1460.8 | 1239.8 | 130.628 | 0.010554 | 130.1375 | 0.0063808 | 4.026 | 0.011799 | 1.3897 | 0.011324 | 1.4359 | 0.0098898
1461 | 1240 | 130.628 | 0.0089549 | 130.0416 | 0.0047816 | 4.026 | 0.011799 | 1.3897 | 0.0097238 | 1.5318 | 0.0098898
1461.2 | 1240.2 | 130.628 | 0.010554 | 130.0416 | 0.0063808 | 4.026 | 0.011799 | 1.3897 | 0.0097238 | 1.5318 | 0.0082906
1461.4 | 1240.4 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.026 | 0.011799 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1461.6 | 1240.6 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.026 | 0.011799 | 1.2937 | 0.011324 | 1.4359 | 0.0098898
1461.8 | 1240.8 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.026 | 0.011799 | 1.2937 | 0.0097238 | 1.4359 | 0.0098898
1462 | 1241 | 130.532 | 0.0089549 | 130.0416 | 0.0047816 | 3.93 | 0.011799 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1462.2 | 1241.2 | 130.532 | 0.010554 | 129.9456 | 0.0063808 | 3.93 | 0.0102 | 1.2937 | 0.0097238 | 1.4359 | 0.0098898
1462.4 | 1241.4 | 130.532 | 0.010554 | 130.0416 | 0.0047816 | 4.026 | 0.0102 | 1.1978 | 0.0097238 | 1.3399 | 0.0098898
1462.6 | 1241.6 | 130.532 | 0.0089549 | 129.9456 | 0.0063808 | 3.93 | 0.0102 | 1.2937 | 0.0097238 | 1.4359 | 0.0098898
1462.8 | 1241.8 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.026 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0082906
1463 | 1242 | 130.532 | 0.0089549 | 129.9456 | 0.0063808 | 3.93 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1463.2 | 1242.2 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.026 | 0.011799 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1463.4 | 1242.4 | 130.628 | 0.0089549 | 130.0416 | 0.0047816 | 4.026 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1463.6 | 1242.6 | 130.532 | 0.0089549 | 130.0416 | 0.0047816 | 4.026 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0082906
1463.8 | 1242.8 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.122 | 0.0102 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1464 | 1243 | 130.532 | 0.010554 | 129.9456 | 0.0063808 | 4.122 | 0.0102 | 1.2937 | 0.011324 | 1.4359 | 0.0082906
1464.2 | 1243.2 | 130.628 | 0.010554 | 130.0416 | 0.0047816 | 4.2179 | 0.011799 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1464.4 | 1243.4 | 130.628 | 0.010554 | 130.0416 | 0.0047816 | 4.2179 | 0.011799 | 1.3897 | 0.011324 | 1.4359 | 0.0098898
1464.6 | 1243.6 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.2179 | 0.011799 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1464.8 | 1243.8 | 130.628 | 0.010554 | 130.0416 | 0.0047816 | 4.2179 | 0.011799 | 1.3897 | 0.011324 | 1.5318 | 0.0098898
1465 | 1244 | 130.628 | 0.010554 | 130.0416 | 0.0063808 | 4.122 | 0.011799 | 1.2937 | 0.0097238 | 1.5318 | 0.0098898
1465.2 | 1244.2 | 130.628 | 0.0089549 | 130.0416 | 0.0063808 | 4.122 | 0.011799 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1465.4 | 1244.4 | 130.532 | 0.010554 | 129.9456 | 0.0047816 | 4.122 | 0.0102 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1465.6 | 1244.6 | 130.532 | 0.0089549 | 129.9456 | 0.0063808 | 4.122 | 0.0102 | 1.3897 | 0.0097238 | 1.4359 | 0.0098898
1465.8 | 1244.8 | 130.4361 | 0.0089549 | 129.9456 | 0.0063808 | 4.122 | 0.0102 | 1.3897 | 0.0097238 | 1.4359 | 0.0082906
1466 | 1245 | 130.4361 | 0.0089549 | 129.8496 | 0.0047816 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.4359 | 0.0098898
1466.2 | 1245.2 | 130.4361 | 0.010554 | 129.9456 | 0.0047816 | 4.122 | 0.0102 | 1.3897 | 0.011324 | 1.4359 | 0.0098898
1466.4 | 1245.4 | 130.3401 | 0.0089549 | 129.8496 | 0.0063808 | 4.026 | 0.0102 | 1.2937 | 0.0097238 | 1.4359 | 0.01149
1466.6 | 1245.6 | 130.4361 | 0.0089549 | 129.9456 | 0.0047816 | 4.2179 | 0.0102 | 1.2937 | 0.0097238 | 1.4359 | 0.0098898
1466.8 | 1245.8 | 130.4361 | 0.010554 | 129.8496 | 0.0063808 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1467 | 1246 | 130.532 | 0.0089549 | 129.9456 | 0.0047816 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1467.2 | 1246.2 | 130.4361 | 0.0089549 | 130.0416 | 0.0063808 | 4.2179 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1467.4 | 1246.4 | 130.4361 | 0.0089549 | 129.8496 | 0.0063808 | 4.2179 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1467.6 | 1246.6 | 130.532 | 0.010554 | 129.9456 | 0.0063808 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1467.8 | 1246.8 | 130.4361 | 0.0089549 | 129.8496 | 0.0063808 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.5318 | 0.0098898
1468 | 1247 | 130.3401 | 0.0089549 | 129.8496 | 0.0063808 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1468.2 | 1247.2 | 130.4361 | 0.0089549 | 129.8496 | 0.0063808 | 4.122 | 0.011799 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1468.4 | 1247.4 | 130.3401 | 0.0089549 | 129.7537 | 0.0063808 | 4.122 | 0.0102 | 1.2937 | 0.0097238 | 1.2439 | 0.0098898
1468.6 | 1247.6 | 130.3401 | 0.010554 | 129.8496 | 0.0063808 | 4.122 | 0.0102 | 1.1978 | 0.0097238 | 1.2439 | 0.0082906
1468.8 | 1247.8 | 130.3401 | 0.0089549 | 129.8496 | 0.0047816 | 4.2179 | 0.0102 | 1.2937 | 0.0097238 | 1.2439 | 0.0098898
1469 | 1248 | 130.3401 | 0.0089549 | 129.8496 | 0.0047816 | 4.026 | 0.011799 | 1.2937 | 0.0097238 | 1.2439 | 0.0098898
1469.2 | 1248.2 | 130.2441 | 0.0089549 | 129.7537 | 0.0063808 | 4.2179 | 0.0102 | 1.2937 | 0.0097238 | 1.3399 | 0.0098898
1469.4 | 1248.4 | 130.2441 | 0.0089549 | 129.8496 | 0.0063808 | 4.122 | 0.0102 | 1.1978 | 0.0081246 | 1.3399 | 0.0098898
1469.6 | 1248.6 | 130.2441 | 0.0089549 | 129.7537 | 0.0047816 | 4.2179 | 0.0102 | 1.1978 | 0.0097238 | 1.2439 | 0.0098898
1469.8 | 1248.8 | 130.2441 | 0.0089549 | 129.7537 | 0.0047816 | 4.2179 | 0.0102 | 1.1978 | 0.0097238 | 1.2439 | 0.0082906
1470 | 1249 | 130.2441 | 0.0089549 | 129.7537 | 0.0047816 | 4.2179 | 0.0102 | 1.1978 | 0.0097238 | 1.2439 | 0.0082906
1470.2 | 1249.2 | 130.1482 | 0.010554 | 129.6577 | 0.0063808 | 4.122 | 0.0102 | 1.1978 | 0.0081246 | 1.148 | 0.0082906
1470.4 | 1249.4 | 130.1482 | 0.0089549 | 129.6577 | 0.0063808 | 4.122 | 0.0086004 | 1.1018 | 0.0097238 | 1.148 | 0.0098898
1470.6 | 1249.6 | 130.0522 | 0.0089549 | 129.5617 | 0.0047816 | 4.026 | 0.0086004 | 1.1018 | 0.0081246 | 1.2439 | 0.0082906
1470.8 | 1249.8 | 130.1482 | 0.0089549 | 129.5617 | 0.0063808 | 4.122 | 0.0086004 | 1.1018 | 0.0081246 | 1.148 | 0.0082906
1471 | 1250 | 130.1482 | 0.010554 | 129.6577 | 0.0063808 | 4.122 | 0.0102 | 1.1018 | 0.0081246 | 1.148 | 0.0066908
1471.2 | 1250.2 | 130.1482 | 0.0089549 | 129.5617 | 0.0063808 | 4.122 | 0.0102 | 1.1018 | 0.0081246 | 1.052 | 0.0082906
1471.4 | 1250.4 | 130.1482 | 0.010554 | 129.6577 | 0.0047816 | 4.2179 | 0.0086004 | 1.1978 | 0.0081246 | 1.148 | 0.0082906
1471.6 | 1250.6 | 130.0522 | 0.0089549 | 129.6577 | 0.0063808 | 4.122 | 0.0086004 | 1.1018 | 0.0097238 | 1.2439 | 0.0082906
1471.8 | 1250.8 | 130.0522 | 0.010554 | 129.5617 | 0.0063808 | 4.026 | 0.0102 | 1.1018 | 0.0081246 | 1.2439 | 0.0082906
1472 | 1251 | 129.9562 | 0.0089549 | 129.4658 | 0.0047816 | 4.122 | 0.0102 | 1.1018 | 0.0081246 | 1.148 | 0.0082906
1472.2 | 1251.2 | 129.9562 | 0.0089549 | 129.5617 | 0.0063808 | 4.122 | 0.0102 | 1.1018 | 0.0081246 | 1.052 | 0.0082906
1472.4 | 1251.4 | 129.9562 | 0.0089549 | 129.5617 | 0.0047816 | 4.026 | 0.0086004 | 1.0058 | 0.0081246 | 1.052 | 0.0066908
1472.6 | 1251.6 | 129.9562 | 0.0089549 | 129.5617 | 0.0063808 | 4.026 | 0.0086004 | 1.0058 | 0.0081246 | 1.052 | 0.0066908
1472.8 | 1251.8 | 130.0522 | 0.0089549 | 129.5617 | 0.0063808 | 4.026 | 0.0086004 | 1.0058 | 0.0081246 | 1.052 | 0.0066908
1473 | 1252 | 129.9562 | 0.0089549 | 129.4658 | 0.0047816 | 4.026 | 0.0086004 | 1.0058 | 0.0081246 | 1.052 | 0.0066908
1473.2 | 1252.2 | 129.9562 | 0.010554 | 129.4658 | 0.0047816 | 4.026 | 0.0086004 | 0.90985 | 0.0065247 | 1.052 | 0.0082906
1473.4 | 1252.4 | 129.9562 | 0.010554 | 129.4658 | 0.0063808 | 4.026 | 0.0086004 | 0.90985 | 0.0081246 | 1.052 | 0.0066908
1473.6 | 1252.6 | 129.8603 | 0.0089549 | 129.4658 | 0.0047816 | 4.026 | 0.0086004 | 0.90985 | 0.0065247 | 0.95602 | 0.0066908
1473.8 | 1252.8 | 127.4611 | 0.0089549 | 126.9706 | 0.0047816 | 3.93 | 0.0086004 | 0.90985 | 0.0065247 | 0.95602 | 0.0066908
1474 | 1253 | 129.6683 | 0.010554 | 129.2738 | 0.0047816 | 4.026 | 0.0086004 | 0.8139 | 0.0065247 | 0.95602 | 0.0066908
1474.2 | 1253.2 | 129.8603 | 0.0089549 | 129.3698 | 0.0063808 | 4.026 | 0.0086004 | 0.90985 | 0.0065247 | 0.95602 | 0.0066908
1474.4 | 1253.4 | 129.7643 | 0.0089549 | 129.3698 | 0.0047816 | 4.026 | 0.0070012 | 0.90985 | 0.0065247 | 0.95602 | 0.0066908
1474.6 | 1253.6 | 129.7643 | 0.0089549 | 129.3698 | 0.0047816 | 4.026 | 0.0070012 | 0.90985 | 0.0065247 | 0.95602 | 0.0066908
1474.8 | 1253.8 | 129.7643 | 0.0089549 | 129.3698 | 0.0047816 | 3.93 | 0.0086004 | 0.8139 | 0.0065247 | 0.76408 | 0.0050916
1475 | 1254 | 129.7643 | 0.0089549 | 129.2738 | 0.0047816 | 3.93 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908
1475.2 | 1254.2 | 129.6683 | 0.0089549 | 129.2738 | 0.0063808 | 3.93 | 0.0086004 | 0.71795 | 0.0065247 | 0.76408 | 0.0066908
1475.4 | 1254.4 | 129.5724 | 0.010554 | 129.2738 | 0.0047816 | 3.93 | 0.0070012 | 0.8139 | 0.0065247 | 0.76408 | 0.0050916
1475.6 | 1254.6 | 129.5724 | 0.0089549 | 129.1779 | 0.0047816 | 3.834 | 0.0070012 | 0.8139 | 0.0065247 | 0.76408 | 0.0050916
1475.8 | 1254.8 | 129.5724 | 0.0089549 | 129.2738 | 0.0047816 | 3.834 | 0.0070012 | 0.71795 | 0.0049255 | 0.76408 | 0.0050916
1476 | 1255 | 129.4764 | 0.0089549 | 129.1779 | 0.0047816 | 3.834 | 0.0070012 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916
1476.2 | 1255.2 | 129.5724 | 0.010554 | 129.1779 | 0.0063808 | 3.834 | 0.0086004 | 0.71795 | 0.0065247 | 0.66813 | 0.0050916
1476.4 | 1255.4 | 129.4764 | 0.0089549 | 129.0819 | 0.0047816 | 3.834 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0050916
1476.6 | 1255.6 | 129.5724 | 0.0089549 | 129.1779 | 0.0047816 | 3.834 | 0.0070012 | 0.71795 | 0.0065247 | 0.76408 | 0.0050916
1476.8 | 1255.8 | 129.4764 | 0.0089549 | 129.0819 | 0.0047816 | 3.834 | 0.0070012 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916
1477 | 1256 | 129.4764 | 0.010554 | 129.0819 | 0.0047816 | 3.834 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916
1477.2 | 1256.2 | 129.4764 | 0.0089549 | 129.0819 | 0.0047816 | 3.834 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916
1477.4 | 1256.4 | 129.3804 | 0.0089549 | 129.0819 | 0.0047816 | 3.834 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916
1477.6 | 1256.6 | 129.3804 | 0.0089549 | 129.0819 | 0.0047816 | 3.7381 | 0.0070012 | 0.71795 | 0.0049255 | 0.66813 | 0.0050916
1477.8 | 1256.8 | 129.4764 | 0.0089549 | 129.0819 | 0.0047816 | 3.834 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0034924
1478 | 1257 | 129.3804 | 0.0089549 | 129.0819 | 0.0063808 | 3.834 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1478.2 | 1257.2 | 129.3804 | 0.0089549 | 129.0819 | 0.0063808 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1478.4 | 1257.4 | 129.3804 | 0.0089549 | 128.9859 | 0.0063808 | 3.834 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1478.6 | 1257.6 | 129.3804 | 0.010554 | 128.9859 | 0.0063808 | 3.834 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1478.8 | 1257.8 | 129.3804 | 0.0089549 | 129.0819 | 0.0063808 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1479 | 1258 | 129.3804 | 0.0089549 | 129.0819 | 0.0047816 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1479.2 | 1258.2 | 129.3804 | 0.010554 | 128.9859 | 0.0047816 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924
1479.4 | 1258.4 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 3.834 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1479.6 | 1258.6 | 129.2844 | 0.010554 | 128.89 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1479.8 | 1258.8 | 129.2844 | 0.010554 | 128.89 | 0.0063808 | 3.7381 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1480 | 1259 | 129.2844 | 0.0073551 | 128.89 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1480.2 | 1259.2 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1480.4 | 1259.4 | 129.2844 | 0.010554 | 128.9859 | 0.0047816 | 3.6421 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1480.6 | 1259.6 | 129.3804 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1480.8 | 1259.8 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1481 | 1260 | 129.2844 | 0.010554 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1481.2 | 1260.2 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1481.4 | 1260.4 | 129.2844 | 0.010554 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1481.6 | 1260.6 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1481.8 | 1260.8 | 129.2844 | 0.0089549 | 128.89 | 0.0063808 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1482 | 1261 | 129.1885 | 0.0073551 | 128.9859 | 0.0063808 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1482.2 | 1261.2 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1482.4 | 1261.4 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1482.6 | 1261.6 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.834 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1482.8 | 1261.8 | 129.2844 | 0.0089549 | 128.9859 | 0.0063808 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1483 | 1262 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1483.2 | 1262.2 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1483.4 | 1262.4 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1483.6 | 1262.6 | 129.2844 | 0.010554 | 128.89 | 0.0047816 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1483.8 | 1262.8 | 129.3804 | 0.010554 | 128.9859 | 0.0047816 | 3.7381 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1484 | 1263 | 129.2844 | 0.0089549 | 128.89 | 0.0063808 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1484.2 | 1263.2 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1484.4 | 1263.4 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 3.834 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1484.6 | 1263.6 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.834 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1484.8 | 1263.8 | 129.3804 | 0.0089549 | 128.9859 | 0.0047816 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1485 | 1264 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1485.2 | 1264.2 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1485.4 | 1264.4 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1485.6 | 1264.6 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 3.93 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1485.8 | 1264.8 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 4.026 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1486 | 1265 | 129.1885 | 0.010554 | 128.89 | 0.0063808 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1486.2 | 1265.2 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 4.026 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1486.4 | 1265.4 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1486.6 | 1265.6 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 3.93 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916
1486.8 | 1265.8 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1487 | 1266 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 3.93 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1487.2 | 1266.2 | 129.1885 | 0.010554 | 128.89 | 0.0063808 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1487.4 | 1266.4 | 129.1885 | 0.0089549 | 128.794 | 0.0047816 | 3.93 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1487.6 | 1266.6 | 129.2844 | 0.0089549 | 128.89 | 0.0063808 | 3.93 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924
1487.8 | 1266.8 | 129.2844 | 0.010554 | 128.89 | 0.0047816 | 4.026 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1488 | 1267 | 129.0925 | 0.010554 | 128.89 | 0.0063808 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1488.2 | 1267.2 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 3.93 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924
1488.4 | 1267.4 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1488.6 | 1267.6 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1488.8 | 1267.8 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 4.026 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1489 | 1268 | 129.2844 | 0.010554 | 128.89 | 0.0063808 | 4.026 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1489.2 | 1268.2 | 129.2844 | 0.010554 | 128.89 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1489.4 | 1268.4 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1489.6 | 1268.6 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1489.8 | 1268.8 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1490 | 1269 | 129.1885 | 0.010554 | 128.89 | 0.0063808 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1490.2 | 1269.2 | 129.1885 | 0.0089549 | 128.89 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1490.4 | 1269.4 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1490.6 | 1269.6 | 129.3804 | 0.0089549 | 128.9859 | 0.0047816 | 4.2179 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1490.8 | 1269.8 | 129.3804 | 0.010554 | 128.9859 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1491 | 1270 | 129.2844 | 0.0089549 | 128.9859 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1491.2 | 1270.2 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1491.4 | 1270.4 | 129.1885 | 0.010554 | 128.9859 | 0.0063808 | 4.3139 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1491.6 | 1270.6 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1491.8 | 1270.8 | 129.1885 | 0.010554 | 128.89 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1492 | 1271 | 129.1885 | 0.0089549 | 128.89 | 0.0063808 | 4.2179 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1492.2 | 1271.2 | 129.1885 | 0.0089549 | 128.89 | 0.0063808 | 4.3139 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1492.4 | 1271.4 | 129.1885 | 0.010554 | 128.9859 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1492.6 | 1271.6 | 129.1885 | 0.0089549 | 128.89 | 0.0063808 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1492.8 | 1271.8 | 129.1885 | 0.0089549 | 128.89 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1493 | 1272 | 129.1885 | 0.010554 | 128.89 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1493.2 | 1272.2 | 129.0925 | 0.0089549 | 128.89 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1493.4 | 1272.4 | 129.1885 | 0.0089549 | 128.9859 | 0.0047816 | 4.4099 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1493.6 | 1272.6 | 129.2844 | 0.0089549 | 128.89 | 0.0047816 | 4.3139 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1493.8 | 1272.8 | 129.1885 | 0.0089549 | 128.9859 | 0.0063808 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1494 | 1273 | 129.0925 | 0.0089549 | 128.794 | 0.0047816 | 4.3139 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1494.2 | 1273.2 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1494.4 | 1273.4 | 129.1885 | 0.010554 | 128.794 | 0.0063808 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1494.6 | 1273.6 | 129.0925 | 0.010554 | 128.794 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1494.8 | 1273.8 | 128.9966 | 0.0089549 | 128.698 | 0.0047816 | 4.4099 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924
1495 | 1274 | 128.9966 | 0.0089549 | 128.794 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1495.2 | 1274.2 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1495.4 | 1274.4 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1495.6 | 1274.6 | 128.9006 | 0.0089549 | 128.794 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1495.8 | 1274.8 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1496 | 1275 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1496.2 | 1275.2 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.122 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1496.4 | 1275.4 | 128.9966 | 0.010554 | 128.698 | 0.0047816 | 4.122 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1496.6 | 1275.6 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1496.8 | 1275.8 | 128.9966 | 0.0089549 | 128.794 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916
1497 | 1276 | 128.9966 | 0.0089549 | 128.698 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1497.2 | 1276.2 | 128.9966 | 0.0089549 | 128.698 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1497.4 | 1276.4 | 128.9966 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1497.6 | 1276.6 | 128.9966 | 0.0089549 | 128.698 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1497.8 | 1276.8 | 128.9966 | 0.010554 | 128.794 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1498 | 1277 | 128.9006 | 0.0089549 | 128.698 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1498.2 | 1277.2 | 128.9006 | 0.010554 | 128.698 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1498.4 | 1277.4 | 128.9966 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1498.6 | 1277.6 | 128.9006 | 0.0089549 | 128.698 | 0.0063808 | 4.2179 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1498.8 | 1277.8 | 128.9966 | 0.0089549 | 128.794 | 0.0063808 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1499 | 1278 | 128.9966 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1499.2 | 1278.2 | 128.9006 | 0.0089549 | 128.794 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1499.4 | 1278.4 | 128.9006 | 0.0089549 | 128.698 | 0.0063808 | 4.3139 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1499.6 | 1278.6 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1499.8 | 1278.8 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1500 | 1279 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1500.2 | 1279.2 | 128.9006 | 0.0089549 | 128.698 | 0.0063808 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1500.4 | 1279.4 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1500.6 | 1279.6 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1500.8 | 1279.8 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1501 | 1280 | 128.9006 | 0.0089549 | 128.602 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1501.2 | 1280.2 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1501.4 | 1280.4 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1501.6 | 1280.6 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1501.8 | 1280.8 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1502 | 1281 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1502.2 | 1281.2 | 128.9006 | 0.0089549 | 128.602 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1502.4 | 1281.4 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1502.6 | 1281.6 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1502.8 | 1281.8 | 128.8046 | 0.010554 | 128.602 | 0.0063808 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1503 | 1282 | 128.9006 | 0.010554 | 128.602 | 0.0063808 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1503.2 | 1282.2 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1503.4 | 1282.4 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1503.6 | 1282.6 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1503.8 | 1282.8 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.3139 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1504 | 1283 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1504.2 | 1283.2 | 128.8046 | 0.0089549 | 128.602 | 0.0063808 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1504.4 | 1283.4 | 128.9006 | 0.0089549 | 128.698 | 0.0063808 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1504.6 | 1283.6 | 128.8046 | 0.010554 | 128.698 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1504.8 | 1283.8 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1505 | 1284 | 128.9006 | 0.0089549 | 128.698 | 0.0063808 | 4.5058 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1505.2 | 1284.2 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.6018 | 0.0070012 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1505.4 | 1284.4 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1505.6 | 1284.6 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1505.8 | 1284.8 | 128.8046 | 0.010554 | 128.602 | 0.0047816 | 4.5058 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1506 | 1285 | 128.7087 | 0.0089549 | 128.5061 | 0.0047816 | 4.5058 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1506.2 | 1285.2 | 128.7087 | 0.0073551 | 128.602 | 0.0063808 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1506.4 | 1285.4 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1506.6 | 1285.6 | 128.7087 | 0.010554 | 128.602 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1506.8 | 1285.8 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.5058 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1507 | 1286 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1507.2 | 1286.2 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1507.4 | 1286.4 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1507.6 | 1286.6 | 128.8046 | 0.0089549 | 128.602 | 0.0063808 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1507.8 | 1286.8 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1508 | 1287 | 128.8046 | 0.0089549 | 128.602 | 0.0063808 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1508.2 | 1287.2 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 4.5058 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0034924
1508.4 | 1287.4 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1508.6 | 1287.6 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1508.8 | 1287.8 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 4.6018 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0034924
1509 | 1288 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1509.2 | 1288.2 | 128.7087 | 0.0089549 | 128.602 | 0.0063808 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1509.4 | 1288.4 | 128.7087 | 0.0089549 | 128.602 | 0.0063808 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1509.6 | 1288.6 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1509.8 | 1288.8 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.5058 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1510 | 1289 | 128.6127 | 0.0089549 | 128.4101 | 0.0063808 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1510.2 | 1289.2 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1510.4 | 1289.4 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1510.6 | 1289.6 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1510.8 | 1289.8 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1511 | 1290 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1511.2 | 1290.2 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1511.4 | 1290.4 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0038022 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1511.6 | 1290.6 | 128.7087 | 0.0089549 | 128.698 | 0.0063808 | 4.6018 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1511.8 | 1290.8 | 128.7087 | 0.0073551 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1512 | 1291 | 128.6127 | 0.0089549 | 128.5061 | 0.0063808 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1512.2 | 1291.2 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1512.4 | 1291.4 | 128.7087 | 0.0089549 | 128.5061 | 0.0047816 | 4.6977 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1512.6 | 1291.6 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.6018 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1512.8 | 1291.8 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1513 | 1292 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 4.6977 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1513.2 | 1292.2 | 128.8046 | 0.010554 | 128.602 | 0.0047816 | 4.6018 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1513.4 | 1292.4 | 128.7087 | 0.0089549 | 128.602 | 0.0063808 | 4.6977 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1513.6 | 1292.6 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.6977 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1513.8 | 1292.8 | 128.7087 | 0.0089549 | 128.602 | 0.0063808 | 4.6977 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1514 | 1293 | 128.7087 | 0.0089549 | 128.602 | 0.0063808 | 4.6977 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1514.2 | 1293.2 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.7937 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1514.4 | 1293.4 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.7937 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1514.6 | 1293.6 | 128.8046 | 0.0073551 | 128.602 | 0.0047816 | 4.8897 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1514.8 | 1293.8 | 128.7087 | 0.0089549 | 128.602 | 0.0063808 | 4.8897 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1515 | 1294 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 4.8897 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1515.2 | 1294.2 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.8897 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1515.4 | 1294.4 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 4.8897 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1515.6 | 1294.6 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.8897 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1515.8 | 1294.8 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.8897 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1516 | 1295 | 128.7087 | 0.010554 | 128.602 | 0.0063808 | 4.9856 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1516.2 | 1295.2 | 128.8046 | 0.0089549 | 128.602 | 0.0047816 | 4.8897 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1516.4 | 1295.4 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.9856 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1516.6 | 1295.6 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.9856 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1516.8 | 1295.8 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.8897 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1517 | 1296 | 128.7087 | 0.0073551 | 128.698 | 0.0063808 | 4.9856 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1517.2 | 1296.2 | 128.7087 | 0.0089549 | 128.698 | 0.0047816 | 4.9856 | 0.0070012 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1517.4 | 1296.4 | 128.8046 | 0.0089549 | 128.698 | 0.0047816 | 4.9856 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1517.6 | 1296.6 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 4.9856 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1517.8 | 1296.8 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.0816 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1518 | 1297 | 128.7087 | 0.0089549 | 128.602 | 0.0047816 | 5.0816 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1518.2 | 1297.2 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.0816 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1518.4 | 1297.4 | 128.9006 | 0.0089549 | 128.698 | 0.0047816 | 5.1776 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1518.6 | 1297.6 | 128.8046 | 0.010554 | 128.602 | 0.0047816 | 5.1776 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1518.8 | 1297.8 | 128.8046 | 0.010554 | 128.698 | 0.0047816 | 5.1776 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1519 | 1298 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.1776 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1519.2 | 1298.2 | 128.8046 | 0.0089549 | 128.602 | 0.0063808 | 5.0816 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1519.4 | 1298.4 | 128.8046 | 0.010554 | 128.602 | 0.0063808 | 5.1776 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1519.6 | 1298.6 | 128.8046 | 0.0089549 | 128.5061 | 0.0047816 | 5.0816 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1519.8 | 1298.8 | 128.9966 | 0.0089549 | 128.5061 | 0.0047816 | 5.1776 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1520 | 1299 | 129.3804 | 0.010554 | 128.0263 | 0.0047816 | 5.1776 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1520.2 | 1299.2 | 128.8046 | 0.0089549 | 128.2182 | 0.0047816 | 5.0816 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1520.4 | 1299.4 | 129.4764 | 0.0089549 | 127.6424 | 0.0047816 | 5.0816 | 0.0054014 | 0.62195 | 0.0049255 | 0.66813 | 0.0050916
1520.6 | 1299.6 | 129.7643 | 0.0089549 | 128.5061 | 0.0047816 | 5.2736 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1520.8 | 1299.8 | 129.7643 | 0.0089549 | 129.0819 | 0.0047816 | 4.4099 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916
1521 | 1300 | 129.7643 | 0.0089549 | 129.0819 | 0.0047816 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1521.2 | 1300.2 | 129.6683 | 0.0089549 | 129.0819 | 0.0063808 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1521.4 | 1300.4 | 129.4764 | 0.0089549 | 128.89 | 0.0047816 | 5.5615 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1521.6 | 1300.6 | 129.3804 | 0.0089549 | 128.89 | 0.0047816 | 5.4655 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1521.8 | 1300.8 | 129.1885 | 0.0089549 | 128.794 | 0.0063808 | 5.2736 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1522 | 1301 | 128.9006 | 0.0089549 | 128.794 | 0.0063808 | 5.2736 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1522.2 | 1301.2 | 128.9006 | 0.0089549 | 128.794 | 0.0063808 | 5.2736 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1522.4 | 1301.4 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.2736 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1522.6 | 1301.6 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.3695 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1522.8 | 1301.8 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.2736 | 0.0070012 | 0.526 | 0.0065247 | 0.57213 | 0.0050916
1523 | 1302 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.3695 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1523.2 | 1302.2 | 128.8046 | 0.0089549 | 128.698 | 0.0063808 | 5.3695 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1523.4 | 1302.4 | 128.9006 | 0.0089549 | 128.794 | 0.0079807 | 5.3695 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1523.6 | 1302.6 | 128.9006 | 0.0073551 | 128.794 | 0.0063808 | 5.4655 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1523.8 | 1302.8 | 128.8046 | 0.010554 | 128.698 | 0.0063808 | 5.3695 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1524 | 1303 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.5615 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1524.2 | 1303.2 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.4655 | 0.0054014 | 0.62195 | 0.0049255 | 0.57213 | 0.0050916
1524.4 | 1303.4 | 128.8046 | 0.0089549 | 128.794 | 0.0079807 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1524.6 | 1303.6 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.4655 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1524.8 | 1303.8 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1525 | 1304 | 128.9006 | 0.0089549 | 128.794 | 0.0079807 | 5.4655 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1525.2 | 1304.2 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1525.4 | 1304.4 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.4655 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1525.6 | 1304.6 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.5615 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1525.8 | 1304.8 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.6574 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1526 | 1305 | 128.7087 | 0.0089549 | 128.602 | 0.0079807 | 5.5615 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916
1526.2 | 1305.2 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1526.4 | 1305.4 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.5615 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1526.6 | 1305.6 | 128.8046 | 0.0089549 | 128.698 | 0.0079807 | 5.6574 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1526.8 | 1305.8 | 128.8046 | 0.0073551 | 128.794 | 0.0079807 | 5.5615 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1527 | 1306 | 128.8046 | 0.0089549 | 128.794 | 0.0095798 | 5.6574 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1527.2 | 1306.2 | 128.8046 | 0.010554 | 128.698 | 0.0095798 | 5.6574 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1527.4 | 1306.4 | 128.9006 | 0.0089549 | 128.794 | 0.0095798 | 5.7534 | 0.0054014 | 0.43001 | 0.0049255 | 0.47618 | 0.0034924
1527.6 | 1306.6 | 128.8046 | 0.0089549 | 128.698 | 0.0095798 | 5.6574 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1527.8 | 1306.8 | 128.8046 | 0.0089549 | 128.698 | 0.0095798 | 5.7534 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1528 | 1307 | 128.7087 | 0.0089549 | 128.602 | 0.0095798 | 5.7534 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1528.2 | 1307.2 | 128.7087 | 0.0089549 | 128.698 | 0.01118 | 5.7534 | 0.0054014 | 0.526 | 0.0033264 | 0.57213 | 0.0050916
1528.4 | 1307.4 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 5.7534 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1528.6 | 1307.6 | 128.7087 | 0.010554 | 128.698 | 0.01118 | 5.8494 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1528.8 | 1307.8 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 5.8494 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1529 | 1308 | 128.9006 | 0.0089549 | 128.698 | 0.01118 | 5.8494 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1529.2 | 1308.2 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 5.8494 | 0.0070012 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924
1529.4 | 1308.4 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 5.8494 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1529.6 | 1308.6 | 128.9006 | 0.010554 | 128.698 | 0.01118 | 5.9453 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1529.8 | 1308.8 | 128.9006 | 0.0089549 | 128.794 | 0.01118 | 5.9453 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1530 | 1309 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 5.9453 | 0.0070012 | 0.43001 | 0.0049255 | 0.47618 | 0.0050916
1530.2 | 1309.2 | 128.9006 | 0.0089549 | 128.794 | 0.012779 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1530.4 | 1309.4 | 128.9006 | 0.0089549 | 128.794 | 0.012779 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1530.6 | 1309.6 | 128.8046 | 0.010554 | 128.698 | 0.01118 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1530.8 | 1309.8 | 128.9006 | 0.010554 | 128.698 | 0.01118 | 6.0413 | 0.0054014 | 0.62195 | 0.0049255 | 0.47618 | 0.0050916
1531 | 1310 | 128.9006 | 0.0089549 | 128.698 | 0.01118 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1531.2 | 1310.2 | 128.9006 | 0.010554 | 128.794 | 0.01118 | 5.9453 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1531.4 | 1310.4 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1531.6 | 1310.6 | 128.9006 | 0.0089549 | 128.698 | 0.012779 | 6.1373 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1531.8 | 1310.8 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0050916
1532 | 1311 | 128.7087 | 0.0089549 | 128.602 | 0.01118 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1532.2 | 1311.2 | 128.8046 | 0.0089549 | 128.698 | 0.012779 | 6.1373 | 0.0054014 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1532.4 | 1311.4 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 6.0413 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1532.6 | 1311.6 | 128.8046 | 0.0089549 | 128.698 | 0.012779 | 6.1373 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1532.8 | 1311.8 | 128.8046 | 0.0089549 | 128.698 | 0.012779 | 6.1373 | 0.0054014 | 0.62195 | 0.0065247 | 0.47618 | 0.0050916
1533 | 1312 | 128.7087 | 0.010554 | 128.698 | 0.012779 | 6.1373 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0034924
1533.2 | 1312.2 | 128.8046 | 0.0089549 | 128.698 | 0.01118 | 6.2332 | 0.0070012 | 0.526 | 0.0049255 | 0.47618 | 0.0034924
1533.4 | 1312.4 | 128.7087 | 0.0089549 | 128.602 | 0.012779 | 6.1373 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1533.6 | 1312.6 | 128.8046 | 0.010554 | 128.602 | 0.012779 | 6.2332 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0034924
1533.8 | 1312.8 | 128.7087 | 0.0089549 | 128.602 | 0.012779 | 6.2332 | 0.0038022 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1534 | 1313 | 128.7087 | 0.0089549 | 128.602 | 0.012779 | 6.2332 | 0.0070012 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1534.2 | 1313.2 | 128.8046 | 0.0089549 | 128.698 | 0.012779 | 6.2332 | 0.0054014 | 0.526 | 0.0049255 | 0.57213 | 0.0050916
1534.4 | 1313.4 | 128.8046 | 0.0089549 | 128.698 | 0.014378 | 6.3292 | 0.0054014 | 0.43001 | 0.0049255 | 0.57213 | 0.0050916
1534.6 | 1313.6 | 128.7087 | 0.0089549 | 128.698 | 0.014378 | 6.3292 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924
1534.8 | 1313.8 | 128.8046 | 0.010554 | 128.698 | 0.015978 | 6.3292 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1535 | 1314 | 128.8046 | 0.0089549 | 128.698 | 0.015978 | 6.4251 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924
1535.2 | 1314.2 | 128.8046 | 0.0089549 | 128.698 | 0.014378 | 6.3292 | 0.0054014 | 0.526 | 0.0033264 | 0.66813 | 0.0034924
1535.4 | 1314.4 | 128.8046 | 0.0089549 | 128.698 | 0.015978 | 6.3292 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0034924
1535.6 | 1314.6 | 128.8046 | 0.0089549 | 128.794 | 0.015978 | 6.4251 | 0.0054014 | 0.526 | 0.0049255 | 0.66813 | 0.0050916
1535.8 | 1314.8 | 128.8046 | 0.0089549 | 128.698 | 0.015978 | 6.4251 | 0.0070012 | 0.43001 | 0.0049255 | 0.76408 | 0.0050916
1536 | 1315 | 128.7087 | 0.0089549 | 128.602 | 0.015978 | 6.4251 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0034924
1536.2 | 1315.2 | 128.7087 | 0.0089549 | 128.602 | 0.015978 | 6.5211 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916
1536.4 | 1315.4 | 128.8046 | 0.0089549 | 128.698 | 0.015978 | 6.5211 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916
1536.6 | 1315.6 | 128.8046 | 0.0073551 | 128.602 | 0.015978 | 6.5211 | 0.0054014 | 0.526 | 0.0049255 | 0.76408 | 0.0050916
1536.8 | 1315.8 | 128.7087 | 0.0089549 | 128.698 | 0.017577 | 6.6171 | 0.0054014 | 0.526 | 0.0049255 | 0.95602 | 0.0050916
1537 | 1316 | 128.7087 | 0.0089549 | 128.698 | 0.017577 | 6.5211 | 0.0054014 | 0.62195 | 0.0049255 | 0.86003 | 0.0050916
1537.2 | 1316.2 | 128.8046 | 0.0089549 | 128.602 | 0.017577 | 6.6171 | 0.0054014 | 0.526 | 0.0049255 | 0.95602 | 0.0050916
1537.4 | 1316.4 | 128.8046 | 0.0089549 | 128.698 | 0.017577 | 6.5211 | 0.0054014 | 0.526 | 0.0049255 | 0.95602 | 0.0050916
1537.6 | 1316.6 | 128.8046 | 0.010554 | 128.698 | 0.017577 | 6.7131 | 0.0054014 | 0.526 | 0.0065247 | 0.95602 | 0.0066908
1537.8 | 1316.8 | 128.7087 | 0.0089549 | 128.602 | 0.019177 | 6.6171 | 0.0054014 | 0.526 | 0.0049255 | 1.052 | 0.0050916
1538 | 1317 | 128.7087 | 0.0089549 | 128.698 | 0.019177 | 6.6171 | 0.0070012 | 0.526 | 0.0049255 | 1.052 | 0.0066908
1538.2 | 1317.2 | 128.8046 | 0.010554 | 128.698 | 0.019177 | 6.7131 | 0.0070012 | 0.526 | 0.0049255 | 1.052 | 0.0066908
1538.4 | 1317.4 | 128.7087 | 0.0089549 | 128.602 | 0.019177 | 6.7131 | 0.0054014 | 0.526 | 0.0049255 | 1.052 | 0.0066908
1538.6 | 1317.6 | 128.7087 | 0.010554 | 128.602 | 0.019177 | 6.7131 | 0.0070012 | 0.526 | 0.0049255 | 1.2439 | 0.0066908
1538.8 | 1317.8 | 128.7087 | 0.0089549 | 128.602 | 0.020776 | 6.7131 | 0.0054014 | 0.526 | 0.0049255 | 1.2439 | 0.0066908
1539 | 1318 | 128.8046 | 0.0089549 | 128.698 | 0.020776 | 6.7131 | 0.0054014 | 0.62195 | 0.0049255 | 1.2439 | 0.0082906
1539.2 | 1318.2 | 128.7087 | 0.010554 | 128.602 | 0.020776 | 6.809 | 0.0054014 | 0.62195 | 0.0049255 | 1.2439 | 0.0082906
1539.4 | 1318.4 | 128.7087 | 0.0089549 | 128.602 | 0.020776 | 6.809 | 0.0054014 | 0.526 | 0.0049255 | 1.3399 | 0.0098898
1539.6 | 1318.6 | 128.7087 | 0.0089549 | 128.602 | 0.022375 | 6.809 | 0.0054014 | 0.526 | 0.0049255 | 1.4359 | 0.0098898
1539.8 | 1318.8 | 128.7087 | 0.0089549 | 128.698 | 0.022375 | 6.809 | 0.0054014 | 0.526 | 0.0049255 | 1.4359 | 0.0098898
1540 | 1319 | 128.7087 | 0.0089549 | 128.602 | 0.022375 | 6.905 | 0.0054014 | 0.526 | 0.0049255 | 1.4359 | 0.0098898
1540.2 | 1319.2 | 128.7087 | 0.0089549 | 128.602 | 0.022375 | 6.905 | 0.0070012 | 0.526 | 0.0049255 | 1.6278 | 0.0098898
1540.4 | 1319.4 | 128.7087 | 0.0089549 | 128.602 | 0.023975 | 6.905 | 0.0054014 | 0.62195 | 0.0049255 | 1.6278 | 0.01149
1540.6 | 1319.6 | 128.6127 | 0.0089549 | 128.602 | 0.023975 | 6.905 | 0.0054014 | 0.526 | 0.0049255 | 1.6278 | 0.01149
1540.8 | 1319.8 | 128.7087 | 0.0089549 | 128.602 | 0.023975 | 6.905 | 0.0070012 | 0.43001 | 0.0049255 | 1.6278 | 0.01149
1541 | 1320 | 128.6127 | 0.010554 | 128.602 | 0.025574 | 7.001 | 0.0054014 | 0.526 | 0.0049255 | 1.7237 | 0.013089
1541.2 | 1320.2 | 128.6127 | 0.0089549 | 128.5061 | 0.023975 | 7.001 | 0.0054014 | 0.526 | 0.0049255 | 1.6278 | 0.01149
1541.4 | 1320.4 | 128.7087 | 0.0089549 | 128.602 | 0.027174 | 7.0969 | 0.0054014 | 0.526 | 0.0049255 | 2.0116 | 0.013089
1541.6 | 1320.6 | 126.9813 | 0.0073551 | 127.2585 | 0.18712 | 6.6171 | 0.0038022 | -1.5853 | 0.0097238 | 26.0035 | 0.13145
1541.8 | 1320.8 | 127.4611 | 0.0089549 | 127.2585 | 0.21911 | 7.1929 | 0.0054014 | 0.526 | 0.0049255 | 34.1607 | 0.21142
1542 | 1321 | 127.4611 | 0.0089549 | 127.3545 | 0.19032 | 7.0969 | 0.0054014 | 0.526 | 0.0049255 | 31.0897 | 0.18263
1542.2 | 1321.2 | 126.5014 | 0.0073551 | 126.2029 | 0.33907 | 7.001 | 0.0054014 | 0.526 | 0.0049255 | 52.9702 | 0.32338
1542.4 | 1321.4 | 126.2135 | 0.0089549 | 126.1069 | 0.36146 | 7.0969 | 0.0086004 | 0.526 | 0.0049255 | 55.4654 | 0.35537
1542.6 | 1321.6 | 126.2135 | 0.010554 | 125.6271 | 0.41424 | 6.905 | 0.0102 | 0.8139 | 0.0049255 | 64.3903 | 0.42575
1542.8 | 1321.8 | 128.3248 | 0.0089549 | 128.2182 | 0.12474 | 7.4808 | 0.0054014 | 0.526 | 0.0049255 | 117.2683 | 0.12505
1543 | 1322 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 7.4808 | 0.0054014 | 0.526 | 0.0049255 | 122.2586 | 0.094661
1543.2 | 1322.2 | 128.5167 | 0.0089549 | 128.3142 | 0.09595 | 7.5768 | 0.0054014 | 0.526 | 0.0049255 | 123.0263 | 0.093061
1543.4 | 1322.4 | 128.4208 | 0.0089549 | 128.4101 | 0.09595 | 7.5768 | 0.0054014 | 0.62195 | 0.0049255 | 123.2182 | 0.093061
1543.6 | 1322.6 | 128.4208 | 0.010554 | 128.3142 | 0.09595 | 7.5768 | 0.0054014 | 0.526 | 0.0049255 | 123.4102 | 0.094661
1543.8 | 1322.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.5768 | 0.0054014 | 0.62195 | 0.0049255 | 123.6021 | 0.093061
1544 | 1323 | 128.4208 | 0.0089549 | 128.3142 | 0.09595 | 7.6727 | 0.0054014 | 0.62195 | 0.0049255 | 123.6021 | 0.094661
1544.2 | 1323.2 | 128.5167 | 0.0073551 | 128.4101 | 0.09595 | 7.6727 | 0.0070012 | 0.526 | 0.0049255 | 123.6981 | 0.093061
1544.4 | 1323.4 | 128.5167 | 0.010554 | 128.4101 | 0.09595 | 7.6727 | 0.0054014 | 0.526 | 0.0049255 | 123.7941 | 0.094661
1544.6 | 1323.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.6727 | 0.0054014 | 0.526 | 0.0049255 | 123.89 | 0.094661
1544.8 | 1323.8 | 128.5167 | 0.0089549 | 128.5061 | 0.09755 | 7.6727 | 0.0054014 | 0.62195 | 0.0049255 | 123.89 | 0.094661
1545 | 1324 | 128.5167 | 0.0089549 | 128.5061 | 0.09595 | 7.7687 | 0.0070012 | 0.526 | 0.0065247 | 123.89 | 0.093061
1545.2 | 1324.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.6727 | 0.0054014 | 0.526 | 0.0049255 | 123.7941 | 0.094661
1545.4 | 1324.4 | 128.5167 | 0.010554 | 128.4101 | 0.09595 | 7.7687 | 0.0054014 | 0.526 | 0.0049255 | 123.6981 | 0.094661
1545.6 | 1324.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.7687 | 0.0054014 | 0.62195 | 0.0049255 | 123.7941 | 0.094661
1545.8 | 1324.8 | 128.6127 | 0.0089549 | 128.4101 | 0.09595 | 7.8647 | 0.0070012 | 0.526 | 0.0049255 | 123.89 | 0.094661
1546 | 1325 | 128.4208 | 0.010554 | 128.3142 | 0.09755 | 7.8647 | 0.0070012 | 0.526 | 0.0049255 | 123.89 | 0.094661
1546.2 | 1325.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.9606 | 0.0054014 | 0.526 | 0.0049255 | 123.89 | 0.094661
1546.4 | 1325.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.8647 | 0.0070012 | 0.526 | 0.0049255 | 123.89 | 0.094661
1546.6 | 1325.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.9606 | 0.0070012 | 0.43001 | 0.0049255 | 123.89 | 0.094661
1546.8 | 1325.8 | 128.5167 | 0.010554 | 128.3142 | 0.09595 | 7.9606 | 0.0070012 | 0.526 | 0.0049255 | 123.7941 | 0.094661
1547 | 1326 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 7.9606 | 0.0054014 | 0.62195 | 0.0065247 | 123.6981 | 0.094661
1547.2 | 1326.2 | 128.5167 | 0.010554 | 128.4101 | 0.09595 | 7.9606 | 0.0054014 | 0.526 | 0.0049255 | 123.7941 | 0.094661
1547.4 | 1326.4 | 128.5167 | 0.0089549 | 128.3142 | 0.09595 | 7.9606 | 0.0054014 | 0.526 | 0.0049255 | 123.6981 | 0.094661
1547.6 | 1326.6 | 128.6127 | 0.0073551 | 128.4101 | 0.09755 | 8.0566 | 0.0054014 | 0.526 | 0.0049255 | 123.6981 | 0.094661
1547.8 | 1326.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.0566 | 0.0054014 | 0.526 | 0.0049255 | 123.6981 | 0.094661
1548 | 1327 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.0566 | 0.0054014 | 0.526 | 0.0049255 | 123.6981 | 0.094661
1548.2 | 1327.2 | 128.6127 | 0.0089549 | 128.5061 | 0.09595 | 8.1526 | 0.0054014 | 0.62195 | 0.0049255 | 123.7941 | 0.094661
1548.4 | 1327.4 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 8.1526 | 0.0054014 | 0.526 | 0.0049255 | 123.89 | 0.094661
1548.6 | 1327.6 | 128.6127 | 0.0089549 | 128.5061 | 0.09595 | 8.1526 | 0.0054014 | 0.526 | 0.0049255 | 123.89 | 0.094661
1548.8 | 1327.8 | 128.6127 | 0.0089549 | 128.4101 | 0.09595 | 8.1526 | 0.0038022 | 0.526 | 0.0049255 | 123.7941 | 0.094661
1549 | 1328 | 128.5167 | 0.0089549 | 128.3142 | 0.09595 | 8.2485 | 0.0054014 | 0.62195 | 0.0049255 | 123.7941 | 0.094661
1549.2 | 1328.2 | 128.5167 | 0.010554 | 128.4101 | 0.09595 | 8.1526 | 0.0054014 | 0.526 | 0.0049255 | 123.6981 | 0.094661
1549.4 | 1328.4 | 128.5167 | 0.0089549 | 128.3142 | 0.09755 | 8.3445 | 0.0054014 | 0.526 | 0.0049255 | 123.7941 | 0.094661
1549.6 | 1328.6 | 128.5167 | 0.010554 | 128.4101 | 0.09595 | 8.3445 | 0.0054014 | 0.526 | 0.0049255 | 123.89 | 0.094661
1549.8 | 1328.8 | 128.5167 | 0.0089549 | 128.3142 | 0.09595 | 8.3445 | 0.0054014 | 0.526 | 0.0049255 | 123.986 | 0.094661
1550 | 1329 | 128.4208 | 0.0089549 | 128.4101 | 0.09595 | 8.3445 | 0.0054014 | 0.526 | 0.0049255 | 124.082 | 0.094661
1550.2 | 1329.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.3445 | 0.0070012 | 0.526 | 0.0049255 | 124.2739 | 0.094661
1550.4 | 1329.4 | 128.4208 | 0.0089549 | 128.4101 | 0.09755 | 8.4405 | 0.0054014 | 0.526 | 0.0049255 | 124.4658 | 0.094661
1550.6 | 1329.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.4405 | 0.0054014 | 0.526 | 0.0049255 | 124.6577 | 0.094661
1550.8 | 1329.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 8.5364 | 0.0054014 | 0.526 | 0.0049255 | 124.5618 | 0.094661
1551 | 1330 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 8.5364 | 0.0070012 | 0.526 | 0.0049255 | 124.7537 | 0.094661
1551.2 | 1330.2 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 8.6324 | 0.0054014 | 0.526 | 0.0049255 | 124.6577 | 0.094661
1551.4 | 1330.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.5364 | 0.0054014 | 0.526 | 0.0049255 | 124.6577 | 0.094661
1551.6 | 1330.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.6324 | 0.0054014 | 0.526 | 0.0049255 | 124.6577 | 0.094661
1551.8 | 1330.8 | 128.4208 | 0.010554 | 128.3142 | 0.09595 | 8.6324 | 0.0054014 | 0.526 | 0.0049255 | 124.6577 | 0.094661
1552 | 1331 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 8.6324 | 0.0054014 | 0.526 | 0.0049255 | 124.7537 | 0.094661
1552.2 | 1331.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 8.6324 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.093061
1552.4 | 1331.4 | 128.5167 | 0.0089549 | 128.3142 | 0.09595 | 8.7284 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1552.6 | 1331.6 | 128.5167 | 0.0089549 | 128.3142 | 0.09755 | 8.8244 | 0.0070012 | 0.526 | 0.0049255 | 124.8497 | 0.09626
1552.8 | 1331.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 8.8244 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.09626
1553 | 1332 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.8244 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.09626
1553.2 | 1332.2 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 8.8244 | 0.0054014 | 0.526 | 0.0049255 | 124.7537 | 0.094661
1553.4 | 1332.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.9203 | 0.0054014 | 0.62195 | 0.0049255 | 124.9457 | 0.094661
1553.6 | 1332.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 8.9203 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1553.8 | 1332.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 8.8244 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1554 | 1333 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 8.9203 | 0.0054014 | 0.62195 | 0.0049255 | 124.7537 | 0.093061
1554.2 | 1333.2 | 128.4208 | 0.010554 | 128.3142 | 0.09755 | 9.0163 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1554.4 | 1333.4 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 8.9203 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1554.6 | 1333.6 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 9.0163 | 0.0070012 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1554.8 | 1333.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.1123 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1555 | 1334 | 128.5167 | 0.010554 | 128.3142 | 0.09755 | 9.0163 | 0.0054014 | 0.526 | 0.0049255 | 124.7537 | 0.094661
1555.2 | 1334.2 | 128.4208 | 0.0089549 | 128.3142 | 0.09595 | 9.1123 | 0.0038022 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1555.4 | 1334.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 9.2082 | 0.0054014 | 0.62195 | 0.0049255 | 124.8497 | 0.093061
1555.6 | 1334.6 | 128.4208 | 0.0089549 | 128.3142 | 0.09595 | 9.2082 | 0.0070012 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1555.8 | 1334.8 | 128.5167 | 0.010554 | 128.4101 | 0.09755 | 9.2082 | 0.0054014 | 0.62195 | 0.0049255 | 124.8497 | 0.094661
1556 | 1335 | 128.4208 | 0.0089549 | 128.3142 | 0.09595 | 9.2082 | 0.0070012 | 0.526 | 0.0049255 | 124.7537 | 0.094661
1556.2 | 1335.2 | 128.4208 | 0.0089549 | 128.4101 | 0.09595 | 9.3042 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1556.4 | 1335.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 9.3042 | 0.0054014 | 0.62195 | 0.0065247 | 124.8497 | 0.094661
1556.6 | 1335.6 | 128.4208 | 0.010554 | 128.4101 | 0.09755 | 9.3042 | 0.0054014 | 0.526 | 0.0049255 | 124.8497 | 0.094661
1556.8 | 1335.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.4001 | 0.0054014 | 0.526 | 0.0049255 | 124.9457 | 0.094661
1557 | 1336 | 128.5167 | 0.0089549 | 128.3142 | 0.09755 | 9.3042 | 0.0054014 | 0.62195 | 0.0049255 | 124.8497 | 0.094661
1557.2 | 1336.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.4001 | 0.0054014 | 0.526 | 0.0049255 | 124.9457 | 0.094661
1557.4 | 1336.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.4961 | 0.0070012 | 0.526 | 0.0049255 | 124.9457 | 0.094661
1557.6 | 1336.6 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 9.4961 | 0.0054014 | 0.526 | 0.0049255 | 124.9457 | 0.094661
1557.8 | 1336.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.5921 | 0.0054014 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1558 | 1337 | 128.4208 | 0.0089549 | 128.3142 | 0.09755 | 9.5921 | 0.0070012 | 0.526 | 0.0049255 | 125.0416 | 0.094661
1558.2 | 1337.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.688 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1558.4 | 1337.4 | 128.5167 | 0.010554 | 128.4101 | 0.09755 | 9.5921 | 0.0054014 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1558.6 | 1337.6 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.688 | 0.0054014 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1558.8 | 1337.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.784 | 0.0054014 | 0.526 | 0.0049255 | 125.1376 | 0.093061
1559 | 1338 | 128.5167 | 0.010554 | 128.4101 | 0.09755 | 9.784 | 0.0054014 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1559.2 | 1338.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.784 | 0.0070012 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1559.4 | 1338.4 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 9.88 | 0.0070012 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1559.6 | 1338.6 | 128.5167 | 0.0073551 | 128.4101 | 0.09595 | 9.88 | 0.0070012 | 0.43001 | 0.0049255 | 125.1376 | 0.094661
1559.8 | 1338.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 9.9759 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1560 | 1339 | 128.4208 | 0.010554 | 128.3142 | 0.09755 | 9.9759 | 0.0054014 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1560.2 | 1339.2 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 9.9759 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1560.4 | 1339.4 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 10.0719 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1560.6 | 1339.6 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 10.0719 | 0.0070012 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1560.8 | 1339.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 10.1679 | 0.0070012 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1561 | 1340 | 128.5167 | 0.0089549 | 128.5061 | 0.09755 | 10.2639 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1561.2 | 1340.2 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 10.2639 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1561.4 | 1340.4 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 10.3598 | 0.0070012 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1561.6 | 1340.6 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 10.3598 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1561.8 | 1340.8 | 128.5167 | 0.010554 | 128.4101 | 0.09755 | 10.4558 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1562 | 1341 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 10.4558 | 0.0054014 | 0.526 | 0.0049255 | 125.2336 | 0.093061
1562.2 | 1341.2 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 10.4558 | 0.0070012 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1562.4 | 1341.4 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 10.5518 | 0.0038022 | 0.526 | 0.0049255 | 125.2336 | 0.09626
1562.6 | 1341.6 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 10.6477 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.09626
1562.8 | 1341.8 | 128.6127 | 0.010554 | 128.4101 | 0.09755 | 10.5518 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1563 | 1342 | 128.6127 | 0.0089549 | 128.602 | 0.09755 | 10.6477 | 0.0054014 | 0.43001 | 0.0049255 | 125.3295 | 0.094661
1563.2 | 1342.2 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 10.7437 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1563.4 | 1342.4 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 10.8397 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1563.6 | 1342.6 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 10.8397 | 0.0054014 | 0.43001 | 0.0049255 | 125.3295 | 0.094661
1563.8 | 1342.8 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 10.9356 | 0.0070012 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1564 | 1343 | 128.6127 | 0.010554 | 128.4101 | 0.09755 | 10.9356 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1564.2 | 1343.2 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 11.0316 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1564.4 | 1343.4 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 11.0316 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1564.6 | 1343.6 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 11.1275 | 0.0054014 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1564.8 | 1343.8 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 11.1275 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1565 | 1344 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 11.2235 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1565.2 | 1344.2 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 11.2235 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1565.4 | 1344.4 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 11.4155 | 0.0054014 | 0.43001 | 0.0049255 | 125.4255 | 0.094661
1565.6 | 1344.6 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 11.3195 | 0.0070012 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1565.8 | 1344.8 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 11.5114 | 0.0070012 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1566 | 1345 | 128.5167 | 0.0089549 | 128.4101 | 0.09595 | 11.5114 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1566.2 | 1345.2 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 11.6074 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1566.4 | 1345.4 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 11.6074 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1566.6 | 1345.6 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 11.7034 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.093061
1566.8 | 1345.8 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 11.7034 | 0.0054014 | 0.43001 | 0.0049255 | 125.4255 | 0.093061
1567 | 1346 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 11.7993 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1567.2 | 1346.2 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 11.8953 | 0.0070012 | 0.526 | 0.0049255 | 125.4255 | 0.093061
1567.4 | 1346.4 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 11.8953 | 0.0070012 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1567.6 | 1346.6 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 11.8953 | 0.0054014 | 0.526 | 0.0049255 | 125.4255 | 0.093061
1567.8 | 1346.8 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 12.0872 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1568 | 1347 | 128.6127 | 0.0089549 | 128.4101 | 0.09595 | 11.9913 | 0.0038022 | 0.526 | 0.0049255 | 125.4255 | 0.094661
1568.2 | 1347.2 | 128.7087 | 0.0089549 | 128.602 | 0.09755 | 12.0872 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1568.4 | 1347.4 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 12.567 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1568.6 | 1347.6 | 128.6127 | 0.010554 | 128.5061 | 0.09755 | 12.3751 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1568.8 | 1347.8 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 12.3751 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1569 | 1348 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 12.3751 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1569.2 | 1348.2 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 12.4711 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1569.4 | 1348.4 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 12.567 | 0.0054014 | 0.43001 | 0.0033264 | 125.5215 | 0.094661
1569.6 | 1348.6 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 12.567 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1569.8 | 1348.8 | 128.7087 | 0.0089549 | 128.602 | 0.099149 | 12.663 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.093061
1570 | 1349 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 12.759 | 0.0054014 | 0.43001 | 0.0049255 | 125.5215 | 0.094661
1570.2 | 1349.2 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 12.855 | 0.0054014 | 0.43001 | 0.0049255 | 125.5215 | 0.094661
1570.4 | 1349.4 | 128.7087 | 0.0089549 | 128.5061 | 0.09595 | 12.855 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1570.6 | 1349.6 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 12.855 | 0.0054014 | 0.43001 | 0.0049255 | 125.6175 | 0.094661
1570.8 | 1349.8 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 12.855 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.093061
1571 | 1350 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 13.0469 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1571.2 | 1350.2 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 13.0469 | 0.0038022 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1571.4 | 1350.4 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 13.0469 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1571.6 | 1350.6 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 13.1429 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1571.8 | 1350.8 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 13.2388 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1572 | 1351 | 128.7087 | 0.0073551 | 128.4101 | 0.099149 | 13.3348 | 0.0054014 | 0.43001 | 0.0033264 | 125.5215 | 0.094661
1572.2 | 1351.2 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 13.3348 | 0.0054014 | 0.526 | 0.0033264 | 125.6175 | 0.094661
1572.4 | 1351.4 | 128.7087 | 0.010554 | 128.602 | 0.09755 | 13.4308 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1572.6 | 1351.6 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 13.5267 | 0.0070012 | 0.526 | 0.0049255 | 125.6175 | 0.093061
1572.8 | 1351.8 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 13.5267 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1573 | 1352 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 13.5267 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1573.2 | 1352.2 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 13.6227 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1573.4 | 1352.4 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 13.6227 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1573.6 | 1352.6 | 128.8046 | 0.0089549 | 128.602 | 0.09755 | 13.9106 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1573.8 | 1352.8 | 128.7087 | 0.010554 | 128.5061 | 0.09755 | 13.8147 | 0.0038022 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1574 | 1353 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 13.8147 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1574.2 | 1353.2 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 13.9106 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1574.4 | 1353.4 | 128.6127 | 0.0073551 | 128.5061 | 0.099149 | 14.0066 | 0.0070012 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1574.6 | 1353.6 | 128.7087 | 0.010554 | 128.5061 | 0.09755 | 14.1025 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.093061
1574.8 | 1353.8 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 14.3904 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1575 | 1354 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 14.4864 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1575.2 | 1354.2 | 128.7087 | 0.0089549 | 128.5061 | 0.099149 | 14.4864 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1575.4 | 1354.4 | 128.7087 | 0.0089549 | 128.4101 | 0.099149 | 14.5824 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1575.6 | 1354.6 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 14.5824 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1575.8 | 1354.8 | 128.6127 | 0.0073551 | 128.5061 | 0.099149 | 14.6783 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1576 | 1355 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 14.6783 | 0.0054014 | 0.43001 | 0.0049255 | 125.6175 | 0.093061
1576.2 | 1355.2 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 14.6783 | 0.0070012 | 0.526 | 0.0033264 | 125.6175 | 0.093061
1576.4 | 1355.4 | 128.6127 | 0.0089549 | 128.5061 | 0.09755 | 14.6783 | 0.0054014 | 0.43001 | 0.0049255 | 125.5215 | 0.094661
1576.6 | 1355.6 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 14.8703 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1576.8 | 1355.8 | 128.7087 | 0.0089549 | 128.5061 | 0.09755 | 14.7743 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.093061
1577 | 1356 | 128.7087 | 0.0089549 | 128.4101 | 0.099149 | 15.0622 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1577.2 | 1356.2 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 15.0622 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1577.4 | 1356.4 | 128.7087 | 0.010554 | 128.5061 | 0.099149 | 15.1582 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1577.6 | 1356.6 | 128.7087 | 0.010554 | 128.5061 | 0.099149 | 15.0622 | 0.0070012 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1577.8 | 1356.8 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 15.0622 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1578 | 1357 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 15.0622 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1578.2 | 1357.2 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 15.1582 | 0.0070012 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1578.4 | 1357.4 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 15.2542 | 0.0054014 | 0.43001 | 0.0049255 | 125.6175 | 0.094661
1578.6 | 1357.6 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 15.3501 | 0.0054014 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1578.8 | 1357.8 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 15.3501 | 0.0054014 | 0.43001 | 0.0049255 | 125.6175 | 0.094661
1579 | 1358 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 15.542 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1579.2 | 1358.2 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 15.638 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1579.4 | 1358.4 | 128.7087 | 0.0089549 | 128.4101 | 0.099149 | 15.542 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1579.6 | 1358.6 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 15.638 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1579.8 | 1358.8 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 15.638 | 0.0070012 | 0.43001 | 0.0049255 | 125.6175 | 0.094661
1580 | 1359 | 128.6127 | 0.0089549 | 128.4101 | 0.09755 | 15.638 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1580.2 | 1359.2 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 15.8299 | 0.0054014 | 0.526 | 0.0033264 | 125.7134 | 0.094661
1580.4 | 1359.4 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 16.0219 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1580.6 | 1359.6 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 15.9259 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1580.8 | 1359.8 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 16.0219 | 0.0070012 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1581 | 1360 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 16.2138 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1581.2 | 1360.2 | 128.6127 | 0.0089549 | 128.3142 | 0.099149 | 16.3098 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1581.4 | 1360.4 | 128.5167 | 0.010554 | 128.4101 | 0.099149 | 16.3098 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1581.6 | 1360.6 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 16.4058 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1581.8 | 1360.8 | 128.5167 | 0.0089549 | 128.4101 | 0.09755 | 16.4058 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1582 | 1361 | 128.5167 | 0.0089549 | 128.3142 | 0.099149 | 16.5017 | 0.0038022 | 0.526 | 0.0049255 | 125.6175 | 0.093061
1582.2 | 1361.2 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 16.6937 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1582.4 | 1361.4 | 128.5167 | 0.0089549 | 128.3142 | 0.099149 | 16.6937 | 0.0038022 | 0.526 | 0.0049255 | 125.6175 | 0.093061
1582.6 | 1361.6 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 17.1735 | 0.0054014 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1582.8 | 1361.8 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 17.0775 | 0.0054014 | 0.43001 | 0.0049255 | 125.6175 | 0.094661
1583 | 1362 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 17.2694 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1583.2 | 1362.2 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 17.1735 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1583.4 | 1362.4 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 17.3654 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1583.6 | 1362.6 | 128.6127 | 0.0089549 | 128.3142 | 0.099149 | 17.2694 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1583.8 | 1362.8 | 128.6127 | 0.0089549 | 128.3142 | 0.099149 | 17.4614 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1584 | 1363 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 17.5574 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.093061
1584.2 | 1363.2 | 128.7087 | 0.010554 | 128.5061 | 0.099149 | 17.5574 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.093061
1584.4 | 1363.4 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 17.2694 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1584.6 | 1363.6 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 17.5574 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1584.8 | 1363.8 | 128.7087 | 0.0089549 | 128.4101 | 0.10075 | 17.4614 | 0.0054014 | 0.62195 | 0.0049255 | 125.8094 | 0.094661
1585 | 1364 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 17.6533 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1585.2 | 1364.2 | 128.6127 | 0.0089549 | 128.5061 | 0.099149 | 17.7493 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1585.4 | 1364.4 | 128.6127 | 0.0073551 | 128.5061 | 0.099149 | 17.7493 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1585.6 | 1364.6 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 17.7493 | 0.0054014 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1585.8 | 1364.8 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 17.8453 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1586 | 1365 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 18.2291 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.09626
1586.2 | 1365.2 | 128.5167 | 0.010554 | 128.4101 | 0.10075 | 18.8049 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1586.4 | 1365.4 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 19.0928 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1586.6 | 1365.6 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 19.0928 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1586.8 | 1365.8 | 128.4208 | 0.0089549 | 128.3142 | 0.10075 | 19.0928 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1587 | 1366 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 18.9969 | 0.0054014 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1587.2 | 1366.2 | 128.5167 | 0.010554 | 128.3142 | 0.099149 | 19.0928 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1587.4 | 1366.4 | 128.5167 | 0.0089549 | 128.3142 | 0.099149 | 19.1888 | 0.0054014 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1587.6 | 1366.6 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 19.3807 | 0.0054014 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1587.8 | 1366.8 | 128.5167 | 0.0089549 | 128.3142 | 0.099149 | 19.4767 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1588 | 1367 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 19.5727 | 0.0054014 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1588.2 | 1367.2 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 19.5727 | 0.0070012 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1588.4 | 1367.4 | 128.5167 | 0.010554 | 128.4101 | 0.099149 | 19.7646 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1588.6 | 1367.6 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 19.7646 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1588.8 | 1367.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 19.8606 | 0.0054014 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1589 | 1368 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 19.9566 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1589.2 | 1368.2 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 20.0525 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1589.4 | 1368.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 20.1485 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1589.6 | 1368.6 | 128.5167 | 0.0089549 | 128.3142 | 0.099149 | 20.3404 | 0.0070012 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1589.8 | 1368.8 | 128.6127 | 0.010554 | 128.4101 | 0.10075 | 20.4364 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.09626
1590 | 1369 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 20.5323 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1590.2 | 1369.2 | 128.5167 | 0.010554 | 128.3142 | 0.10075 | 20.6283 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1590.4 | 1369.4 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 20.6283 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1590.6 | 1369.6 | 128.5167 | 0.0089549 | 128.3142 | 0.099149 | 20.8202 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1590.8 | 1369.8 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 20.9162 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1591 | 1370 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 21.1082 | 0.0070012 | 0.43001 | 0.0049255 | 125.7134 | 0.094661
1591.2 | 1370.2 | 128.5167 | 0.0089549 | 128.4101 | 0.099149 | 21.3961 | 0.0054014 | 0.526 | 0.0033264 | 125.8094 | 0.094661
1591.4 | 1370.4 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 21.492 | 0.0070012 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1591.6 | 1370.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 21.3961 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1591.8 | 1370.8 | 128.6127 | 0.010554 | 128.4101 | 0.10075 | 21.588 | 0.0038022 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1592 | 1371 | 128.6127 | 0.010554 | 128.4101 | 0.099149 | 21.684 | 0.0054014 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1592.2 | 1371.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 21.588 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1592.4 | 1371.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 21.7799 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1592.6 | 1371.6 | 128.6127 | 0.010554 | 128.4101 | 0.10075 | 21.9718 | 0.0070012 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1592.8 | 1371.8 | 128.6127 | 0.010554 | 128.4101 | 0.10075 | 22.0678 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1593 | 1372 | 128.4208 | 0.0089549 | 128.3142 | 0.10075 | 22.0678 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1593.2 | 1372.2 | 128.6127 | 0.010554 | 128.3142 | 0.10075 | 22.0678 | 0.0054014 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1593.4 | 1372.4 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 22.0678 | 0.0054014 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1593.6 | 1372.6 | 128.6127 | 0.0089549 | 128.3142 | 0.10075 | 22.2597 | 0.0070012 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1593.8 | 1372.8 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 22.2597 | 0.0070012 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1594 | 1373 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 22.1638 | 0.0070012 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1594.2 | 1373.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 22.4517 | 0.0070012 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1594.4 | 1373.4 | 128.7087 | 0.0089549 | 128.4101 | 0.10075 | 22.6436 | 0.0070012 | 0.43001 | 0.0049255 | 125.8094 | 0.094661
1594.6 | 1373.6 | 128.6127 | 0.0089549 | 128.4101 | 0.099149 | 22.6436 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1594.8 | 1373.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 22.7396 | 0.0070012 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1595 | 1374 | 128.5167 | 0.0089549 | 128.4101 | 0.10075 | 22.7396 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1595.2 | 1374.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 22.7396 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1595.4 | 1374.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 22.8356 | 0.0070012 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1595.6 | 1374.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10075 | 22.9315 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1595.8 | 1374.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10235 | 22.8356 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1596 | 1375 | 128.5167 | 0.0089549 | 128.2182 | 0.10075 | 22.9315 | 0.0070012 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1596.2 | 1375.2 | 128.6127 | 0.0089549 | 128.3142 | 0.10235 | 23.1235 | 0.0070012 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1596.4 | 1375.4 | 128.6127 | 0.0089549 | 128.3142 | 0.10075 | 23.1235 | 0.0086004 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1596.6 | 1375.6 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 23.3154 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1596.8 | 1375.8 | 128.6127 | 0.010554 | 128.4101 | 0.10075 | 23.5073 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1597 | 1376 | 128.7087 | 0.0089549 | 128.5061 | 0.10075 | 23.5073 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1597.2 | 1376.2 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 23.8912 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1597.4 | 1376.4 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 23.9872 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1597.6 | 1376.6 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 23.8912 | 0.0086004 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1597.8 | 1376.8 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 23.9872 | 0.0086004 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1598 | 1377 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 23.9872 | 0.0086004 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1598.2 | 1377.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.1791 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1598.4 | 1377.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.1791 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1598.6 | 1377.6 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 24.371 | 0.0086004 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1598.8 | 1377.8 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.467 | 0.0086004 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1599 | 1378 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 24.467 | 0.0086004 | 0.526 | 0.0033264 | 126.0013 | 0.094661
1599.2 | 1378.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.467 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1599.4 | 1378.4 | 128.6127 | 0.010554 | 128.4101 | 0.10235 | 24.563 | 0.0086004 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1599.6 | 1378.6 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.7549 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1599.8 | 1378.8 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.8509 | 0.0086004 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1600 | 1379 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 24.9468 | 0.0086004 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1600.2 | 1379.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 25.2347 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1600.4 | 1379.4 | 128.6127 | 0.010554 | 128.4101 | 0.10235 | 25.3307 | 0.0086004 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1600.6 | 1379.6 | 128.7087 | 0.010554 | 128.3142 | 0.10235 | 25.4267 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1600.8 | 1379.8 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 25.3307 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1601 | 1380 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 25.3307 | 0.0086004 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1601.2 | 1380.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10075 | 25.3307 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1601.4 | 1380.4 | 128.7087 | 0.0089549 | 128.5061 | 0.10075 | 25.3307 | 0.0086004 | 0.526 | 0.0033264 | 126.0013 | 0.094661
1601.6 | 1380.6 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 25.6186 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1601.8 | 1380.8 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 25.6186 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1602 | 1381 | 128.6127 | 0.0089549 | 128.5061 | 0.10235 | 25.6186 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1602.2 | 1381.2 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 25.7146 | 0.0102 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1602.4 | 1381.4 | 128.8046 | 0.0089549 | 128.5061 | 0.10235 | 25.6186 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1602.6 | 1381.6 | 128.8046 | 0.0089549 | 128.5061 | 0.10235 | 25.7146 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1602.8 | 1381.8 | 128.8046 | 0.0089549 | 128.5061 | 0.10235 | 25.7146 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1603 | 1382 | 128.8046 | 0.0089549 | 128.5061 | 0.10235 | 25.8105 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1603.2 | 1382.2 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 25.9065 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1603.4 | 1382.4 | 128.8046 | 0.0089549 | 128.5061 | 0.10235 | 26.0985 | 0.0102 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1603.6 | 1382.6 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 26.3863 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1603.8 | 1382.8 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 26.3863 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1604 | 1383 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 26.3863 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1604.2 | 1383.2 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 27.1541 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1604.4 | 1383.4 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 27.2501 | 0.0102 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1604.6 | 1383.6 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 27.0581 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1604.8 | 1383.8 | 128.8046 | 0.0089549 | 128.5061 | 0.10235 | 27.1541 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1605 | 1384 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 26.7702 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1605.2 | 1384.2 | 128.7087 | 0.0089549 | 128.5061 | 0.10235 | 27.346 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1605.4 | 1384.4 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 27.6339 | 0.011799 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1605.6 | 1384.6 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 27.538 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1605.8 | 1384.8 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 27.6339 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1606 | 1385 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 27.6339 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1606.2 | 1385.2 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 27.8259 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1606.4 | 1385.4 | 128.7087 | 0.010554 | 128.5061 | 0.10235 | 27.9218 | 0.011799 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1606.6 | 1385.6 | 128.7087 | 0.0089549 | 128.5061 | 0.10395 | 27.9218 | 0.0102 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1606.8 | 1385.8 | 128.7087 | 0.0089549 | 128.5061 | 0.10395 | 28.1137 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1607 | 1386 | 128.7087 | 0.010554 | 128.4101 | 0.10395 | 28.1137 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1607.2 | 1386.2 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 28.2097 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1607.4 | 1386.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 28.3057 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1607.6 | 1386.6 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 28.4016 | 0.011799 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1607.8 | 1386.8 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 28.4976 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1608 | 1387 | 128.6127 | 0.010554 | 128.4101 | 0.10235 | 28.6896 | 0.0102 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1608.2 | 1387.2 | 128.7087 | 0.0073551 | 128.4101 | 0.10395 | 29.0734 | 0.011799 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1608.4 | 1387.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 29.2654 | 0.011799 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1608.6 | 1387.6 | 128.7087 | 0.0089549 | 128.4101 | 0.10235 | 29.1694 | 0.011799 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1608.8 | 1387.8 | 128.6127 | 0.010554 | 128.4101 | 0.10235 | 28.9775 | 0.011799 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1609 | 1388 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 28.8815 | 0.011799 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1609.2 | 1388.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 29.0734 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1609.4 | 1388.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10235 | 29.3613 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1609.6 | 1388.6 | 128.7087 | 0.010554 | 128.4101 | 0.10235 | 29.5533 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1609.8 | 1388.8 | 128.6127 | 0.010554 | 128.4101 | 0.10395 | 29.6492 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1610 | 1389 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 29.7452 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1610.2 | 1389.2 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 30.1291 | 0.011799 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1610.4 | 1389.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 30.417 | 0.011799 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1610.6 | 1389.6 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 30.8968 | 0.011799 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1610.8 | 1389.8 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 31.0887 | 0.013399 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1611 | 1390 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 30.9928 | 0.011799 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1611.2 | 1390.2 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 30.8968 | 0.013399 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1611.4 | 1390.4 | 128.7087 | 0.010554 | 128.3142 | 0.10395 | 30.8968 | 0.011799 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1611.6 | 1390.6 | 128.7087 | 0.0089549 | 128.4101 | 0.10395 | 30.9928 | 0.013399 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1611.8 | 1390.8 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 31.4726 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1612 | 1391 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 31.2807 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1612.2 | 1391.2 | 128.6127 | 0.010554 | 128.3142 | 0.10395 | 31.2807 | 0.013399 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1612.4 | 1391.4 | 128.6127 | 0.010554 | 128.3142 | 0.10395 | 31.4726 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1612.6 | 1391.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10395 | 31.7605 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1612.8 | 1391.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10395 | 31.8565 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1613 | 1392 | 128.5167 | 0.010554 | 128.4101 | 0.10395 | 31.9524 | 0.013399 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1613.2 | 1392.2 | 128.5167 | 0.0089549 | 128.4101 | 0.10395 | 32.2404 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1613.4 | 1392.4 | 128.6127 | 0.0089549 | 128.3142 | 0.10555 | 32.3363 | 0.013399 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1613.6 | 1392.6 | 128.5167 | 0.0089549 | 128.4101 | 0.10395 | 32.6242 | 0.013399 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1613.8 | 1392.8 | 128.4208 | 0.0089549 | 128.3142 | 0.10395 | 32.7202 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1614 | 1393 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 32.9121 | 0.013399 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1614.2 | 1393.2 | 128.5167 | 0.010554 | 128.3142 | 0.10395 | 32.9121 | 0.014998 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1614.4 | 1393.4 | 128.6127 | 0.0089549 | 128.4101 | 0.10395 | 33.104 | 0.013399 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1614.6 | 1393.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 33.2 | 0.013399 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1614.8 | 1393.8 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 33.392 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1615 | 1394 | 128.6127 | 0.010554 | 128.2182 | 0.10395 | 33.392 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1615.2 | 1394.2 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 33.4879 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1615.4 | 1394.4 | 128.5167 | 0.010554 | 128.4101 | 0.10555 | 33.6799 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1615.6 | 1394.6 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 33.8718 | 0.014998 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1615.8 | 1394.8 | 128.6127 | 0.0089549 | 128.3142 | 0.10555 | 33.8718 | 0.014998 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1616 | 1395 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 33.8718 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1616.2 | 1395.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 34.0637 | 0.014998 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1616.4 | 1395.4 | 128.6127 | 0.010554 | 128.4101 | 0.10555 | 34.1597 | 0.014998 | 0.526 | 0.0033264 | 126.0973 | 0.094661
1616.6 | 1395.6 | 128.6127 | 0.0089549 | 128.3142 | 0.10555 | 34.1597 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1616.8 | 1395.8 | 128.6127 | 0.010554 | 128.4101 | 0.10555 | 34.2556 | 0.014998 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1617 | 1396 | 128.6127 | 0.010554 | 128.4101 | 0.10395 | 34.2556 | 0.014998 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1617.2 | 1396.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 34.5435 | 0.014998 | 0.526 | 0.0049255 | 126.0013 | 0.093061
1617.4 | 1396.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 34.7355 | 0.016598 | 0.526 | 0.0049255 | 126.0013 | 0.093061
1617.6 | 1396.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 34.8315 | 0.014998 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1617.8 | 1396.8 | 128.4208 | 0.0089549 | 128.2182 | 0.10555 | 35.0234 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1618 | 1397 | 128.3248 | 0.0089549 | 128.1222 | 0.10555 | 35.2153 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1618.2 | 1397.2 | 128.4208 | 0.0089549 | 128.2182 | 0.10555 | 35.2153 | 0.016598 | 0.526 | 0.0033264 | 125.9054 | 0.094661
1618.4 | 1397.4 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 35.4073 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1618.6 | 1397.6 | 128.5167 | 0.0089549 | 128.2182 | 0.10555 | 35.4073 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1618.8 | 1397.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 35.3113 | 0.016598 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1619 | 1398 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 35.5992 | 0.016598 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1619.2 | 1398.2 | 128.5167 | 0.0089549 | 128.4101 | 0.10555 | 35.6952 | 0.016598 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1619.4 | 1398.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10395 | 35.7911 | 0.014998 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1619.6 | 1398.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 35.9831 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1619.8 | 1398.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 35.9831 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1620 | 1399 | 128.4208 | 0.010554 | 128.2182 | 0.10555 | 36.175 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1620.2 | 1399.2 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 36.271 | 0.016598 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1620.4 | 1399.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 36.4629 | 0.016598 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1620.6 | 1399.6 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 36.5589 | 0.018197 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1620.8 | 1399.8 | 128.5167 | 0.0073551 | 128.3142 | 0.10555 | 36.6548 | 0.016598 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1621 | 1400 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 36.7508 | 0.018197 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1621.2 | 1400.2 | 128.6127 | 0.010554 | 128.4101 | 0.10555 | 36.8468 | 0.018197 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1621.4 | 1400.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 36.9428 | 0.016598 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1621.6 | 1400.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 36.9428 | 0.016598 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1621.8 | 1400.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 37.1347 | 0.018197 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1622 | 1401 | 128.5167 | 0.0089549 | 128.2182 | 0.10555 | 37.1347 | 0.018197 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1622.2 | 1401.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 37.2306 | 0.016598 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1622.4 | 1401.4 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 37.3266 | 0.018197 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1622.6 | 1401.6 | 128.6127 | 0.0089549 | 128.3142 | 0.10555 | 37.3266 | 0.018197 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1622.8 | 1401.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 37.6145 | 0.016598 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1623 | 1402 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 37.4226 | 0.018197 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1623.2 | 1402.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 37.6145 | 0.018197 | 0.526 | 0.0065247 | 126.0013 | 0.094661
1623.4 | 1402.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 37.6145 | 0.018197 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1623.6 | 1402.6 | 128.6127 | 0.0089549 | 128.4101 | 0.10715 | 37.7105 | 0.018197 | 0.62195 | 0.0049255 | 126.0973 | 0.094661
1623.8 | 1402.8 | 128.6127 | 0.0089549 | 128.3142 | 0.10715 | 37.8064 | 0.018197 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1624 | 1403 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 37.9024 | 0.019797 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1624.2 | 1403.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 38.0943 | 0.018197 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1624.4 | 1403.4 | 128.5167 | 0.010554 | 128.3142 | 0.10555 | 38.2863 | 0.018197 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1624.6 | 1403.6 | 128.6127 | 0.0089549 | 128.3142 | 0.10715 | 38.4782 | 0.018197 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1624.8 | 1403.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 38.5742 | 0.018197 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1625 | 1404 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 38.6702 | 0.018197 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1625.2 | 1404.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 38.7661 | 0.019797 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1625.4 | 1404.4 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 38.7661 | 0.019797 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1625.6 | 1404.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 38.7661 | 0.019797 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1625.8 | 1404.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 38.958 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1626 | 1405 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 38.958 | 0.019797 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1626.2 | 1405.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 39.15 | 0.019797 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1626.4 | 1405.4 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 39.2459 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1626.6 | 1405.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 39.2459 | 0.018197 | 0.43001 | 0.0049255 | 126.1932 | 0.094661
1626.8 | 1405.8 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 39.15 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1627 | 1406 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 39.2459 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1627.2 | 1406.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 39.6298 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1627.4 | 1406.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10555 | 39.5339 | 0.019797 | 0.526 | 0.0049255 | 126.2892 | 0.09626
1627.6 | 1406.6 | 128.5167 | 0.010554 | 128.4101 | 0.10715 | 39.6298 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1627.8 | 1406.8 | 128.5167 | 0.010554 | 128.2182 | 0.10715 | 39.7258 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1628 | 1407 | 128.4208 | 0.010554 | 128.2182 | 0.10715 | 39.9177 | 0.019797 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1628.2 | 1407.2 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 40.0137 | 0.019797 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1628.4 | 1407.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 40.1097 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1628.6 | 1407.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 40.2056 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.09626
1628.8 | 1407.8 | 128.4208 | 0.0089549 | 128.2182 | 0.10715 | 40.3016 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1629 | 1408 | 128.5167 | 0.010554 | 128.3142 | 0.10715 | 40.3976 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1629.2 | 1408.2 | 128.4208 | 0.0089549 | 128.2182 | 0.10715 | 40.3976 | 0.019797 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1629.4 | 1408.4 | 128.5167 | 0.0089549 | 128.2182 | 0.10715 | 40.5895 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1629.6 | 1408.6 | 128.5167 | 0.010554 | 128.2182 | 0.10715 | 40.5895 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1629.8 | 1408.8 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 40.5895 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1630 | 1409 | 128.4208 | 0.0089549 | 128.2182 | 0.10715 | 40.6854 | 0.019797 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1630.2 | 1409.2 | 128.4208 | 0.0089549 | 128.3142 | 0.10715 | 40.7814 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1630.4 | 1409.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 41.1653 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1630.6 | 1409.6 | 128.6127 | 0.0089549 | 128.3142 | 0.10715 | 41.5492 | 0.021396 | 0.526 | 0.0033264 | 126.1932 | 0.094661
1630.8 | 1409.8 | 128.7087 | 0.0089549 | 128.4101 | 0.10715 | 41.4532 | 0.021396 | 0.43001 | 0.0049255 | 126.2892 | 0.094661
1631 | 1410 | 128.6127 | 0.0089549 | 128.4101 | 0.10715 | 41.3572 | 0.021396 | 0.43001 | 0.0049255 | 126.1932 | 0.094661
1631.2 | 1410.2 | 128.6127 | 0.0089549 | 128.3142 | 0.10715 | 41.6451 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1631.4 | 1410.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 41.8371 | 0.019797 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1631.6 | 1410.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10875 | 41.933 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1631.8 | 1410.8 | 128.5167 | 0.0089549 | 128.4101 | 0.10715 | 41.933 | 0.021396 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1632 | 1411 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 42.029 | 0.021396 | 0.62195 | 0.0049255 | 126.0973 | 0.094661
1632.2 | 1411.2 | 128.6127 | 0.010554 | 128.3142 | 0.10715 | 42.125 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1632.4 | 1411.4 | 128.6127 | 0.0073551 | 128.4101 | 0.10715 | 42.2209 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1632.6 | 1411.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10875 | 42.4129 | 0.021396 | 0.43001 | 0.0049255 | 126.1932 | 0.094661
1632.8 | 1411.8 | 128.6127 | 0.0089549 | 128.4101 | 0.10715 | 42.4129 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1633 | 1412 | 128.5167 | 0.0089549 | 128.3142 | 0.10875 | 42.4129 | 0.021396 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1633.2 | 1412.2 | 128.6127 | 0.010554 | 128.4101 | 0.10715 | 42.6048 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1633.4 | 1412.4 | 128.6127 | 0.010554 | 128.4101 | 0.10875 | 42.7008 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1633.6 | 1412.6 | 128.6127 | 0.010554 | 128.3142 | 0.10715 | 42.7967 | 0.022996 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1633.8 | 1412.8 | 128.6127 | 0.0089549 | 128.3142 | 0.10715 | 42.7008 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1634 | 1413 | 128.4208 | 0.010554 | 128.2182 | 0.10715 | 42.7967 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1634.2 | 1413.2 | 128.5167 | 0.0089549 | 128.2182 | 0.10875 | 42.9887 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.09626
1634.4 | 1413.4 | 128.3248 | 0.010554 | 128.2182 | 0.10715 | 42.8927 | 0.021396 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1634.6 | 1413.6 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 43.2766 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1634.8 | 1413.8 | 128.4208 | 0.010554 | 128.2182 | 0.10715 | 43.1806 | 0.021396 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1635 | 1414 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 43.2766 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1635.2 | 1414.2 | 128.4208 | 0.0089549 | 128.3142 | 0.10715 | 43.5645 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1635.4 | 1414.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10715 | 43.6604 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1635.6 | 1414.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10875 | 43.6604 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1635.8 | 1414.8 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 44.1403 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1636 | 1415 | 128.5167 | 0.010554 | 128.2182 | 0.10875 | 44.1403 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1636.2 | 1415.2 | 128.5167 | 0.010554 | 128.3142 | 0.10875 | 44.3322 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1636.4 | 1415.4 | 128.5167 | 0.0089549 | 128.3142 | 0.10875 | 44.3322 | 0.022996 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1636.6 | 1415.6 | 128.5167 | 0.0089549 | 128.3142 | 0.10875 | 44.3322 | 0.021396 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1636.8 | 1415.8 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 44.2362 | 0.022996 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1637 | 1416 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 44.4282 | 0.022996 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1637.2 | 1416.2 | 128.4208 | 0.010554 | 128.1222 | 0.10875 | 44.5242 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1637.4 | 1416.4 | 128.3248 | 0.0089549 | 128.2182 | 0.10715 | 44.5242 | 0.021396 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1637.6 | 1416.6 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 44.5242 | 0.021396 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1637.8 | 1416.8 | 128.4208 | 0.0089549 | 128.2182 | 0.10715 | 44.6201 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1638 | 1417 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 44.7161 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1638.2 | 1417.2 | 128.5167 | 0.010554 | 128.2182 | 0.10875 | 44.7161 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1638.4 | 1417.4 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 44.7161 | 0.022996 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1638.6 | 1417.6 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 44.6201 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1638.8 | 1417.8 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 44.8121 | 0.021396 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1639 | 1418 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 45.004 | 0.021396 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1639.2 | 1418.2 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 45.0999 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1639.4 | 1418.4 | 128.2288 | 0.0089549 | 128.2182 | 0.10875 | 45.0999 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1639.6 | 1418.6 | 128.3248 | 0.0089549 | 128.1222 | 0.10875 | 45.0999 | 0.022996 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1639.8 | 1418.8 | 128.2288 | 0.0089549 | 128.1222 | 0.10875 | 45.0999 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1640 | 1419 | 128.3248 | 0.010554 | 128.1222 | 0.10875 | 45.1959 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1640.2 | 1419.2 | 128.3248 | 0.010554 | 128.1222 | 0.10875 | 45.0999 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1640.4 | 1419.4 | 128.4208 | 0.012154 | 128.2182 | 0.10875 | 45.2919 | 0.022996 | 0.62195 | 0.0049255 | 126.1932 | 0.094661
1640.6 | 1419.6 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 45.3878 | 0.022996 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1640.8 | 1419.8 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 45.3878 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1641 | 1420 | 128.4208 | 0.0089549 | 128.3142 | 0.11035 | 45.4838 | 0.022996 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1641.2 | 1420.2 | 128.5167 | 0.0089549 | 128.2182 | 0.10875 | 45.6758 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1641.4 | 1420.4 | 128.5167 | 0.0089549 | 128.4101 | 0.10875 | 45.7717 | 0.022996 | 0.526 | 0.0049255 | 126.1932 | 0.093061
1641.6 | 1420.6 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 45.6758 | 0.022996 | 0.526 | 0.0033264 | 126.1932 | 0.094661
1641.8 | 1420.8 | 128.4208 | 0.010554 | 128.2182 | 0.11035 | 45.7717 | 0.022996 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1642 | 1421 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 45.8677 | 0.022996 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1642.2 | 1421.2 | 128.4208 | 0.010554 | 128.2182 | 0.11035 | 46.1556 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1642.4 | 1421.4 | 128.5167 | 0.0089549 | 128.2182 | 0.10875 | 46.1556 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1642.6 | 1421.6 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 46.1556 | 0.022996 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1642.8 | 1421.8 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 46.2516 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1643 | 1422 | 128.4208 | 0.010554 | 128.2182 | 0.10875 | 46.4435 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1643.2 | 1422.2 | 128.4208 | 0.010554 | 128.1222 | 0.10875 | 46.3475 | 0.024595 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1643.4 | 1422.4 | 128.5167 | 0.0089549 | 128.3142 | 0.11035 | 46.4435 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1643.6 | 1422.6 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 46.4435 | 0.022996 | 0.526 | 0.0033264 | 126.0973 | 0.094661
1643.8 | 1422.8 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 46.4435 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.093061
1644 | 1423 | 128.3248 | 0.010554 | 128.1222 | 0.10875 | 46.5395 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1644.2 | 1423.2 | 128.3248 | 0.010554 | 128.2182 | 0.11035 | 46.5395 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1644.4 | 1423.4 | 128.4208 | 0.0089549 | 128.3142 | 0.11035 | 46.6354 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1644.6 | 1423.6 | 128.3248 | 0.0089549 | 128.3142 | 0.10875 | 46.6354 | 0.024595 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1644.8 | 1423.8 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 46.6354 | 0.022996 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1645 | 1424 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 46.5395 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1645.2 | 1424.2 | 128.4208 | 0.0089549 | 128.2182 | 0.10875 | 46.7314 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1645.4 | 1424.4 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 46.7314 | 0.024595 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1645.6 | 1424.6 | 128.3248 | 0.0089549 | 128.3142 | 0.10875 | 46.7314 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1645.8 | 1424.8 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 46.8273 | 0.024595 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1646 | 1425 | 128.3248 | 0.0089549 | 128.2182 | 0.10875 | 46.9233 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1646.2 | 1425.2 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 47.0193 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1646.4 | 1425.4 | 128.4208 | 0.0089549 | 128.3142 | 0.10875 | 46.9233 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1646.6 | 1425.6 | 128.3248 | 0.0089549 | 128.3142 | 0.10875 | 47.0193 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1646.8 | 1425.8 | 128.4208 | 0.0089549 | 128.2182 | 0.11035 | 47.1153 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1647 | 1426 | 128.3248 | 0.010554 | 128.2182 | 0.11035 | 47.1153 | 0.022996 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1647.2 | 1426.2 | 128.4208 | 0.0089549 | 128.3142 | 0.11035 | 47.4991 | 0.024595 | 0.526 | 0.0033264 | 126.0973 | 0.094661
1647.4 | 1426.4 | 128.4208 | 0.0089549 | 128.2182 | 0.11035 | 47.4991 | 0.024595 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1647.6 | 1426.6 | 128.3248 | 0.0089549 | 128.2182 | 0.11035 | 47.5951 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1647.8 | 1426.8 | 128.3248 | 0.0089549 | 128.2182 | 0.11035 | 47.5951 | 0.022996 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1648 | 1427 | 128.2288 | 0.0089549 | 128.1222 | 0.10875 | 47.6911 | 0.024595 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1648.2 | 1427.2 | 128.2288 | 0.0089549 | 128.2182 | 0.11035 | 47.787 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1648.4 | 1427.4 | 128.2288 | 0.0089549 | 128.2182 | 0.11035 | 47.979 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1648.6 | 1427.6 | 128.2288 | 0.010554 | 128.1222 | 0.11035 | 47.883 | 0.022996 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1648.8 | 1427.8 | 128.2288 | 0.0089549 | 128.1222 | 0.11035 | 47.979 | 0.024595 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1649 | 1428 | 128.2288 | 0.0089549 | 128.1222 | 0.11035 | 47.979 | 0.024595 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1649.2 | 1428.2 | 128.2288 | 0.0073551 | 128.1222 | 0.11035 | 47.979 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1649.4 | 1428.4 | 128.2288 | 0.0089549 | 128.2182 | 0.11035 | 48.1709 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1649.6 | 1428.6 | 128.2288 | 0.0089549 | 128.1222 | 0.11035 | 48.1709 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1649.8 | 1428.8 | 128.2288 | 0.0089549 | 128.1222 | 0.10875 | 48.2669 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1650 | 1429 | 128.0369 | 0.0089549 | 127.9303 | 0.11035 | 48.2669 | 0.024595 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1650.2 | 1429.2 | 128.2288 | 0.010554 | 128.1222 | 0.11035 | 48.4588 | 0.026194 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1650.4 | 1429.4 | 128.2288 | 0.0089549 | 128.1222 | 0.11035 | 48.5548 | 0.024595 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1650.6 | 1429.6 | 128.2288 | 0.0089549 | 128.1222 | 0.11035 | 48.7467 | 0.024595 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1650.8 | 1429.8 | 128.3248 | 0.0089549 | 128.2182 | 0.11035 | 49.0346 | 0.024595 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1651 | 1430 | 128.3248 | 0.0089549 | 128.2182 | 0.11035 | 49.1306 | 0.026194 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1651.2 | 1430.2 | 128.3248 | 0.010554 | 128.2182 | 0.11035 | 49.2266 | 0.026194 | 0.62195 | 0.0049255 | 126.1932 | 0.09626
1651.4 | 1430.4 | 128.3248 | 0.0089549 | 128.1222 | 0.11035 | 49.3225 | 0.024595 | 0.62195 | 0.0049255 | 126.1932 | 0.094661
1651.6 | 1430.6 | 128.2288 | 0.0089549 | 128.2182 | 0.11035 | 49.5145 | 0.026194 | 0.62195 | 0.0049255 | 126.2892 | 0.094661
1651.8 | 1430.8 | 128.3248 | 0.010554 | 128.1222 | 0.11035 | 49.6104 | 0.026194 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1652 | 1431 | 128.4208 | 0.010554 | 128.2182 | 0.11035 | 49.8023 | 0.026194 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1652.2 | 1431.2 | 128.6127 | 0.0089549 | 128.2182 | 0.11035 | 49.8023 | 0.026194 | 0.526 | 0.0049255 | 125.5215 | 0.09626
1652.4 | 1431.4 | 128.6127 | 0.0089549 | 128.2182 | 0.11035 | 49.8983 | 0.027794 | 0.526 | 0.0049255 | 125.5215 | 0.09626
1652.6 | 1431.6 | 128.8046 | 0.010554 | 128.3142 | 0.10875 | 49.9943 | 0.026194 | 0.526 | 0.0065247 | 125.4255 | 0.09626
1652.8 | 1431.8 | 128.9006 | 0.0089549 | 128.2182 | 0.11194 | 50.0902 | 0.027794 | 0.62195 | 0.0049255 | 125.8094 | 0.094661
1653 | 1432 | 128.9966 | 0.0089549 | 128.4101 | 0.11035 | 50.0902 | 0.027794 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1653.2 | 1432.2 | 129.0925 | 0.010554 | 128.4101 | 0.11194 | 50.1862 | 0.027794 | 0.526 | 0.0049255 | 125.1376 | 0.094661
1653.4 | 1432.4 | 129.1885 | 0.0089549 | 128.4101 | 0.11035 | 50.0902 | 0.026194 | 0.62195 | 0.0049255 | 125.7134 | 0.094661
1653.6 | 1432.6 | 129.1885 | 0.0089549 | 128.3142 | 0.11194 | 49.2266 | 0.022996 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1653.8 | 1432.8 | 129.1885 | 0.0089549 | 128.1222 | 0.11035 | 49.5145 | 0.026194 | 0.62195 | 0.0049255 | 125.6175 | 0.094661
1654 | 1433 | 129.0925 | 0.0089549 | 127.4504 | 0.11035 | 50.0902 | 0.026194 | 0.526 | 0.0049255 | 125.7134 | 0.09626
1654.2 | 1433.2 | 128.9006 | 0.0089549 | 127.0666 | 0.11194 | 49.9943 | 0.026194 | 0.62195 | 0.0065247 | 125.9054 | 0.09626
1654.4 | 1433.4 | 128.1329 | 0.010554 | 127.5464 | 0.11194 | 50.1862 | 0.026194 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1654.6 | 1433.6 | 128.7087 | 0.0089549 | 127.6424 | 0.11035 | 50.5701 | 0.026194 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1654.8 | 1433.8 | 128.8046 | 0.0089549 | 127.5464 | 0.11194 | 50.5701 | 0.026194 | 0.526 | 0.0049255 | 125.8094 | 0.093061
1655 | 1434 | 128.2288 | 0.0089549 | 127.7384 | 0.11035 | 50.6661 | 0.026194 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1655.2 | 1434.2 | 128.2288 | 0.0089549 | 127.8343 | 0.11035 | 50.858 | 0.026194 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1655.4 | 1434.4 | 128.2288 | 0.0089549 | 127.8343 | 0.11194 | 50.954 | 0.026194 | 0.526 | 0.0049255 | 125.8094 | 0.09626
1655.6 | 1434.6 | 128.2288 | 0.0089549 | 127.9303 | 0.11035 | 51.1459 | 0.027794 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1655.8 | 1434.8 | 128.2288 | 0.0089549 | 128.0263 | 0.11035 | 51.3378 | 0.026194 | 0.526 | 0.0065247 | 126.0013 | 0.09626
1656 | 1435 | 128.2288 | 0.010554 | 128.0263 | 0.11194 | 51.3378 | 0.026194 | 0.62195 | 0.0065247 | 126.0013 | 0.09626
1656.2 | 1435.2 | 128.1329 | 0.0089549 | 128.0263 | 0.11035 | 51.3378 | 0.027794 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1656.4 | 1435.4 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 51.5297 | 0.027794 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1656.6 | 1435.6 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 51.7217 | 0.026194 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1656.8 | 1435.8 | 128.2288 | 0.0089549 | 128.0263 | 0.11194 | 51.8177 | 0.027794 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1657 | 1436 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 51.9136 | 0.027794 | 0.526 | 0.0065247 | 126.0973 | 0.094661
1657.2 | 1436.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11194 | 52.0096 | 0.027794 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1657.4 | 1436.4 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 52.0096 | 0.027794 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1657.6 | 1436.6 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 52.4894 | 0.027794 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1657.8 | 1436.8 | 128.3248 | 0.0089549 | 128.1222 | 0.11194 | 52.4894 | 0.027794 | 0.62195 | 0.0049255 | 126.0973 | 0.09626
1658 | 1437 | 128.1329 | 0.0089549 | 128.0263 | 0.11194 | 52.4894 | 0.027794 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1658.2 | 1437.2 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 52.5854 | 0.029393 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1658.4 | 1437.4 | 128.2288 | 0.010554 | 128.1222 | 0.11194 | 52.6814 | 0.029393 | 0.526 | 0.0065247 | 126.0013 | 0.09626
1658.6 | 1437.6 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 52.7773 | 0.029393 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1658.8 | 1437.8 | 128.1329 | 0.0089549 | 128.1222 | 0.11194 | 52.9692 | 0.027794 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1659 | 1438 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 53.0652 | 0.027794 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1659.2 | 1438.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11194 | 53.0652 | 0.027794 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1659.4 | 1438.4 | 128.2288 | 0.010554 | 128.1222 | 0.11354 | 53.3531 | 0.027794 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1659.6 | 1438.6 | 128.1329 | 0.010554 | 128.1222 | 0.11194 | 53.4491 | 0.029393 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1659.8 | 1438.8 | 128.2288 | 0.010554 | 128.1222 | 0.11194 | 53.641 | 0.029393 | 0.526 | 0.0065247 | 126.0013 | 0.094661
1660 | 1439 | 128.1329 | 0.0089549 | 128.0263 | 0.11194 | 53.641 | 0.029393 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1660.2 | 1439.2 | 128.1329 | 0.0089549 | 128.0263 | 0.11194 | 53.641 | 0.029393 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1660.4 | 1439.4 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 53.833 | 0.029393 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1660.6 | 1439.6 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 53.833 | 0.029393 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1660.8 | 1439.8 | 128.2288 | 0.010554 | 128.1222 | 0.11194 | 54.0249 | 0.029393 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1661 | 1440 | 128.2288 | 0.0089549 | 128.0263 | 0.11194 | 54.2169 | 0.029393 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1661.2 | 1440.2 | 128.2288 | 0.010554 | 128.1222 | 0.11354 | 54.2169 | 0.029393 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1661.4 | 1440.4 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 54.2169 | 0.029393 | 0.62195 | 0.0049255 | 126.0973 | 0.09626
1661.6 | 1440.6 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 54.3128 | 0.029393 | 0.62195 | 0.0049255 | 126.1932 | 0.094661
1661.8 | 1440.8 | 128.2288 | 0.0089549 | 128.1222 | 0.11194 | 54.4088 | 0.029393 | 0.526 | 0.0065247 | 126.0973 | 0.09626
1662 | 1441 | 128.2288 | 0.0089549 | 128.0263 | 0.11194 | 54.5047 | 0.027794 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1662.2 | 1441.2 | 128.2288 | 0.010554 | 128.1222 | 0.11354 | 54.6007 | 0.029393 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1662.4 | 1441.4 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 54.6967 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1662.6 | 1441.6 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 54.8886 | 0.029393 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1662.8 | 1441.8 | 128.1329 | 0.0089549 | 128.0263 | 0.11194 | 54.9846 | 0.029393 | 0.62195 | 0.0065247 | 126.0013 | 0.094661
1663 | 1442 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 55.2725 | 0.029393 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1663.2 | 1442.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 55.2725 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1663.4 | 1442.4 | 128.1329 | 0.0089549 | 128.0263 | 0.11194 | 55.4644 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1663.6 | 1442.6 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 55.4644 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1663.8 | 1442.8 | 128.2288 | 0.0089549 | 128.1222 | 0.11354 | 55.6564 | 0.029393 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1664 | 1443 | 128.0369 | 0.010554 | 128.0263 | 0.11354 | 55.6564 | 0.029393 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1664.2 | 1443.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 55.7523 | 0.029393 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1664.4 | 1443.4 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 55.8483 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1664.6 | 1443.6 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 55.9442 | 0.029393 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1664.8 | 1443.8 | 128.1329 | 0.0073551 | 127.9303 | 0.11354 | 55.9442 | 0.029393 | 0.62195 | 0.0049255 | 125.9054 | 0.09626
1665 | 1444 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 56.0402 | 0.030993 | 0.526 | 0.0065247 | 125.9054 | 0.094661
1665.2 | 1444.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 56.0402 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1665.4 | 1444.4 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 56.1362 | 0.030993 | 0.526 | 0.0065247 | 126.0973 | 0.094661
1665.6 | 1444.6 | 128.2288 | 0.010554 | 128.0263 | 0.11354 | 56.2321 | 0.030993 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1665.8 | 1444.8 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 56.3281 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1666 | 1445 | 128.1329 | 0.0089549 | 127.9303 | 0.11354 | 56.4241 | 0.030993 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1666.2 | 1445.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 56.616 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1666.4 | 1445.4 | 128.1329 | 0.0089549 | 127.9303 | 0.11354 | 56.712 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1666.6 | 1445.6 | 128.2288 | 0.0089549 | 128.0263 | 0.11354 | 56.712 | 0.030993 | 0.526 | 0.0065247 | 126.0013 | 0.09626
1666.8 | 1445.8 | 128.1329 | 0.010554 | 127.9303 | 0.11354 | 56.808 | 0.030993 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1667 | 1446 | 128.1329 | 0.0089549 | 128.0263 | 0.11354 | 56.9999 | 0.030993 | 0.526 | 0.0065247 | 126.0013 | 0.09626
1667.2 | 1446.2 | 128.1329 | 0.0089549 | 127.9303 | 0.11354 | 56.9999 | 0.030993 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1667.4 | 1446.4 | 128.1329 | 0.0089549 | 127.9303 | 0.11354 | 57.1918 | 0.030993 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1667.6 | 1446.6 | 128.1329 | 0.0089549 | 127.9303 | 0.11354 | 57.2878 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1667.8 | 1446.8 | 128.1329 | 0.0089549 | 127.9303 | 0.11514 | 57.3838 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1668 | 1447 | 128.1329 | 0.010554 | 127.9303 | 0.11354 | 57.3838 | 0.030993 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1668.2 | 1447.2 | 128.2288 | 0.0089549 | 127.9303 | 0.11354 | 57.4797 | 0.032592 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1668.4 | 1447.4 | 128.2288 | 0.010554 | 127.8343 | 0.11514 | 57.5757 | 0.030993 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1668.6 | 1447.6 | 128.1329 | 0.0089549 | 127.8343 | 0.11354 | 57.4797 | 0.032592 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1668.8 | 1447.8 | 128.2288 | 0.010554 | 127.8343 | 0.11514 | 57.6716 | 0.030993 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1669 | 1448 | 128.2288 | 0.0089549 | 127.9303 | 0.11354 | 57.8636 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1669.2 | 1448.2 | 128.2288 | 0.0089549 | 127.9303 | 0.11514 | 57.9596 | 0.030993 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1669.4 | 1448.4 | 128.3248 | 0.010554 | 127.9303 | 0.11354 | 58.1515 | 0.030993 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1669.6 | 1448.6 | 128.4208 | 0.0089549 | 127.9303 | 0.11514 | 58.2475 | 0.032592 | 0.62195 | 0.0049255 | 126.0013 | 0.094661
1669.8 | 1448.8 | 128.3248 | 0.0089549 | 127.9303 | 0.11514 | 58.3434 | 0.030993 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1670 | 1449 | 128.2288 | 0.0089549 | 127.9303 | 0.11354 | 58.3434 | 0.032592 | 0.526 | 0.0065247 | 125.9054 | 0.094661
1670.2 | 1449.2 | 128.2288 | 0.0089549 | 127.8343 | 0.11514 | 58.5354 | 0.032592 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1670.4 | 1449.4 | 128.2288 | 0.0089549 | 127.8343 | 0.11354 | 58.6313 | 0.032592 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1670.6 | 1449.6 | 128.3248 | 0.010554 | 127.8343 | 0.11514 | 58.6313 | 0.032592 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1670.8 | 1449.8 | 128.4208 | 0.0089549 | 127.7384 | 0.11354 | 58.8233 | 0.032592 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1671 | 1450 | 128.3248 | 0.0089549 | 127.7384 | 0.11514 | 58.9192 | 0.032592 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1671.2 | 1450.2 | 128.5167 | 0.0089549 | 127.6424 | 0.11514 | 59.0152 | 0.032592 | 0.62195 | 0.0049255 | 125.9054 | 0.09626
1671.4 | 1450.4 | 128.8046 | 0.010554 | 127.6424 | 0.11354 | 59.1112 | 0.032592 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1671.6 | 1450.6 | 128.8046 | 0.0089549 | 127.5464 | 0.11514 | 59.3991 | 0.032592 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1671.8 | 1450.8 | 128.4208 | 0.0089549 | 127.6424 | 0.11354 | 59.3991 | 0.032592 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1672 | 1451 | 128.1329 | 0.0089549 | 127.4504 | 0.11514 | 59.3031 | 0.032592 | 0.62195 | 0.0049255 | 125.9054 | 0.09626
1672.2 | 1451.2 | 128.6127 | 0.0089549 | 127.0666 | 0.11514 | 59.591 | 0.032592 | 0.526 | 0.0065247 | 125.9054 | 0.09626
1672.4 | 1451.4 | 129.1885 | 0.0089549 | 127.1625 | 0.11514 | 59.8789 | 0.032592 | 0.526 | 0.0065247 | 126.0013 | 0.09626
1672.6 | 1451.6 | 129.2844 | 0.0089549 | 127.4504 | 0.11514 | 59.8789 | 0.034192 | 0.62195 | 0.0049255 | 125.9054 | 0.09626
1672.8 | 1451.8 | 129.1885 | 0.0089549 | 128.0263 | 0.11514 | 59.7829 | 0.034192 | 0.62195 | 0.0049255 | 125.8094 | 0.094661
1673 | 1452 | 129.1885 | 0.0089549 | 128.2182 | 0.11514 | 59.3991 | 0.032592 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1673.2 | 1452.2 | 129.0925 | 0.0089549 | 128.2182 | 0.11514 | 59.687 | 0.030993 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1673.4 | 1452.4 | 129.1885 | 0.0089549 | 128.4101 | 0.11514 | 60.8386 | 0.034192 | 0.526 | 0.0049255 | 125.7134 | 0.094661
1673.6 | 1452.6 | 128.9966 | 0.0089549 | 128.4101 | 0.11514 | 61.0305 | 0.035791 | 0.62195 | 0.0049255 | 125.1376 | 0.09626
1673.8 | 1452.8 | 128.9966 | 0.0089549 | 128.4101 | 0.11514 | 61.4144 | 0.034192 | 0.526 | 0.0049255 | 125.2336 | 0.094661
1674 | 1453 | 128.9006 | 0.010554 | 128.3142 | 0.11674 | 61.4144 | 0.035791 | 0.526 | 0.0049255 | 125.3295 | 0.094661
1674.2 | 1453.2 | 128.9006 | 0.0089549 | 128.3142 | 0.11514 | 61.5104 | 0.035791 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1674.4 | 1453.4 | 128.9006 | 0.0089549 | 128.2182 | 0.11514 | 61.7983 | 0.034192 | 0.526 | 0.0049255 | 125.8094 | 0.094661
1674.6 | 1453.6 | 128.7087 | 0.0089549 | 128.2182 | 0.11674 | 62.0862 | 0.035791 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1674.8 | 1453.8 | 128.7087 | 0.0073551 | 128.2182 | 0.11674 | 61.9902 | 0.034192 | 0.526 | 0.0049255 | 125.5215 | 0.09626
1675 | 1454 | 128.6127 | 0.0089549 | 128.2182 | 0.11514 | 61.9902 | 0.034192 | 0.62195 | 0.0065247 | 125.6175 | 0.09626
1675.2 | 1454.2 | 128.5167 | 0.0089549 | 128.1222 | 0.11514 | 62.1821 | 0.034192 | 0.526 | 0.0049255 | 125.6175 | 0.094661
1675.4 | 1454.4 | 128.4208 | 0.0089549 | 128.2182 | 0.11674 | 62.374 | 0.035791 | 0.526 | 0.0049255 | 125.5215 | 0.094661
1675.6 | 1454.6 | 128.3248 | 0.0089549 | 128.1222 | 0.11674 | 62.566 | 0.034192 | 0.62195 | 0.0049255 | 125.7134 | 0.09626
1675.8 | 1454.8 | 128.2288 | 0.0089549 | 128.1222 | 0.11674 | 62.374 | 0.034192 | 0.526 | 0.0049255 | 125.8094 | 0.09626
1676 | 1455 | 128.2288 | 0.0089549 | 128.0263 | 0.11514 | 62.374 | 0.035791 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1676.2 | 1455.2 | 128.2288 | 0.0089549 | 128.1222 | 0.11514 | 62.6619 | 0.035791 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1676.4 | 1455.4 | 128.1329 | 0.0089549 | 128.0263 | 0.11674 | 62.8539 | 0.035791 | 0.526 | 0.0049255 | 126.2892 | 0.09626
1676.6 | 1455.6 | 128.1329 | 0.010554 | 128.0263 | 0.11674 | 62.9499 | 0.034192 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1676.8 | 1455.8 | 128.1329 | 0.0073551 | 128.0263 | 0.11674 | 63.0458 | 0.035791 | 0.526 | 0.0065247 | 126.1932 | 0.094661
1677 | 1456 | 128.1329 | 0.0089549 | 128.0263 | 0.11514 | 63.0458 | 0.035791 | 0.62195 | 0.0049255 | 126.0973 | 0.094661
1677.2 | 1456.2 | 128.1329 | 0.0089549 | 128.1222 | 0.11674 | 63.1418 | 0.035791 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1677.4 | 1456.4 | 128.1329 | 0.0089549 | 128.0263 | 0.11674 | 63.1418 | 0.035791 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1677.6 | 1456.6 | 128.1329 | 0.0089549 | 128.1222 | 0.11674 | 63.2378 | 0.035791 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1677.8 | 1456.8 | 128.1329 | 0.010554 | 127.9303 | 0.11674 | 63.2378 | 0.035791 | 0.526 | 0.0065247 | 126.0013 | 0.094661
1678 | 1457 | 128.0369 | 0.0089549 | 127.9303 | 0.11514 | 63.4297 | 0.035791 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1678.2 | 1457.2 | 128.1329 | 0.0089549 | 128.0263 | 0.11674 | 63.7176 | 0.035791 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1678.4 | 1457.4 | 128.0369 | 0.0089549 | 128.0263 | 0.11674 | 63.8135 | 0.03739 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1678.6 | 1457.6 | 128.1329 | 0.0089549 | 128.1222 | 0.11674 | 64.1015 | 0.03739 | 0.62195 | 0.0049255 | 126.0013 | 0.09626
1678.8 | 1457.8 | 128.1329 | 0.010554 | 128.0263 | 0.11674 | 64.2934 | 0.035791 | 0.526 | 0.0065247 | 126.0013 | 0.094661
1679 | 1458 | 128.1329 | 0.0089549 | 127.9303 | 0.11674 | 64.1974 | 0.035791 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1679.2 | 1458.2 | 128.0369 | 0.010554 | 127.9303 | 0.11674 | 64.3894 | 0.03739 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1679.4 | 1458.4 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 64.3894 | 0.035791 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1679.6 | 1458.6 | 128.1329 | 0.0089549 | 128.1222 | 0.11674 | 64.3894 | 0.035791 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1679.8 | 1458.8 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 64.4853 | 0.035791 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1680 | 1459 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 64.5813 | 0.03739 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1680.2 | 1459.2 | 128.0369 | 0.010554 | 128.0263 | 0.11674 | 64.9652 | 0.035791 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1680.4 | 1459.4 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 65.0612 | 0.03739 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1680.6 | 1459.6 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 65.0612 | 0.03739 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1680.8 | 1459.8 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 65.349 | 0.03739 | 0.62195 | 0.0049255 | 125.9054 | 0.09626
1681 | 1460 | 128.1329 | 0.0089549 | 128.0263 | 0.11834 | 65.541 | 0.03739 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1681.2 | 1460.2 | 128.0369 | 0.0089549 | 128.0263 | 0.11674 | 65.541 | 0.03739 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1681.4 | 1460.4 | 128.0369 | 0.010554 | 127.9303 | 0.11674 | 65.7329 | 0.03739 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1681.6 | 1460.6 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 65.7329 | 0.035791 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1681.8 | 1460.8 | 128.1329 | 0.0089549 | 127.9303 | 0.11674 | 65.9248 | 0.035791 | 0.526 | 0.0049255 | 125.9054 | 0.094661
1682 | 1461 | 128.0369 | 0.0089549 | 127.9303 | 0.11674 | 65.9248 | 0.035791 | 0.43001 | 0.0049255 | 125.9054 | 0.094661
1682.2 | 1461.2 | 128.0369 | 0.0089549 | 127.9303 | 0.11834 | 66.2127 | 0.03739 | 0.62195 | 0.0049255 | 125.9054 | 0.094661
1682.4 | 1461.4 | 128.2288 | 0.0089549 | 128.0263 | 0.11674 | 66.4047 | 0.03739 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1682.6 | 1461.6 | 128.1329 | 0.010554 | 128.0263 | 0.11834 | 66.6926 | 0.03899 | 0.526 | 0.0049255 | 125.9054 | 0.09626
1682.8 | 1461.8 | 128.1329 | 0.0089549 | 128.0263 | 0.11834 | 66.8845 | 0.03739 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1683 | 1462 | 128.2288 | 0.010554 | 128.0263 | 0.11834 | 67.1724 | 0.03899 | 0.526 | 0.0049255 | 126.0013 | 0.093061
1683.2 | 1462.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 67.4603 | 0.03899 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1683.4 | 1462.4 | 128.1329 | 0.010554 | 128.0263 | 0.11834 | 67.7482 | 0.03899 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1683.6 | 1462.6 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 67.9402 | 0.03899 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1683.8 | 1462.8 | 128.2288 | 0.0089549 | 128.1222 | 0.11834 | 68.0361 | 0.03899 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1684 | 1463 | 128.1329 | 0.010554 | 128.0263 | 0.11834 | 68.1321 | 0.03899 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1684.2 | 1463.2 | 128.2288 | 0.010554 | 128.1222 | 0.11834 | 68.42 | 0.03899 | 0.526 | 0.0049255 | 126.0973 | 0.093061
1684.4 | 1463.4 | 128.2288 | 0.0089549 | 128.1222 | 0.11834 | 68.5159 | 0.03899 | 0.526 | 0.0033264 | 126.0013 | 0.09626
1684.6 | 1463.6 | 128.1329 | 0.0089549 | 127.9303 | 0.11834 | 68.8998 | 0.040589 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1684.8 | 1463.8 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 69.1877 | 0.040589 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1685 | 1464 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 69.2837 | 0.040589 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1685.2 | 1464.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 69.6676 | 0.040589 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1685.4 | 1464.4 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 69.8595 | 0.040589 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1685.6 | 1464.6 | 128.2288 | 0.0089549 | 128.0263 | 0.11994 | 70.0514 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1685.8 | 1464.8 | 128.1329 | 0.0089549 | 128.0263 | 0.11994 | 70.1474 | 0.040589 | 0.62195 | 0.0049255 | 126.0973 | 0.094661
1686 | 1465 | 128.2288 | 0.0089549 | 128.0263 | 0.11994 | 70.3393 | 0.040589 | 0.43001 | 0.0049255 | 126.0013 | 0.094661
1686.2 | 1465.2 | 128.2288 | 0.0089549 | 128.0263 | 0.11994 | 70.7232 | 0.042189 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1686.4 | 1465.4 | 128.2288 | 0.010554 | 128.1222 | 0.11994 | 71.0111 | 0.042189 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1686.6 | 1465.6 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 71.1071 | 0.042189 | 0.43001 | 0.0049255 | 126.0973 | 0.093061
1686.8 | 1465.8 | 128.3248 | 0.0089549 | 128.2182 | 0.11994 | 71.395 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1687 | 1466 | 128.4208 | 0.0089549 | 128.1222 | 0.11994 | 71.395 | 0.042189 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1687.2 | 1466.2 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 70.0514 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.093061
1687.4 | 1466.4 | 128.3248 | 0.0073551 | 128.2182 | 0.11994 | 69.5716 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1687.6 | 1466.6 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 69.3797 | 0.042189 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1687.8 | 1466.8 | 128.3248 | 0.0089549 | 128.2182 | 0.11834 | 69.2837 | 0.040589 | 0.43001 | 0.0049255 | 126.1932 | 0.094661
1688 | 1467 | 128.1329 | 0.010554 | 127.9303 | 0.11834 | 69.2837 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1688.2 | 1467.2 | 128.2288 | 0.0089549 | 128.1222 | 0.11834 | 69.1877 | 0.040589 | 0.43001 | 0.0049255 | 126.1932 | 0.094661
1688.4 | 1467.4 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 69.1877 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1688.6 | 1467.6 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 68.9958 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1688.8 | 1467.8 | 128.1329 | 0.010554 | 128.0263 | 0.11834 | 68.8038 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1689 | 1468 | 127.749 | 0.0089549 | 127.8343 | 0.11354 | 68.324 | 0.03899 | 0.526 | 0.0049255 | 125.9054 | 0.093061
1689.2 | 1468.2 | 128.2288 | 0.010554 | 128.0263 | 0.11834 | 68.7079 | 0.03899 | 0.526 | 0.0049255 | 126.0013 | 0.09626
1689.4 | 1468.4 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 68.7079 | 0.040589 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1689.6 | 1468.6 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 68.9958 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1689.8 | 1468.8 | 128.3248 | 0.0089549 | 128.0263 | 0.11994 | 69.2837 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1690 | 1469 | 128.2288 | 0.0089549 | 128.0263 | 0.11834 | 69.3797 | 0.040589 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1690.2 | 1469.2 | 128.3248 | 0.0089549 | 128.0263 | 0.11994 | 69.6676 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1690.4 | 1469.4 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 69.6676 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.09626
1690.6 | 1469.6 | 128.3248 | 0.0089549 | 128.2182 | 0.11834 | 69.8595 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1690.8 | 1469.8 | 128.2288 | 0.010554 | 128.1222 | 0.11834 | 69.9555 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1691 | 1470 | 128.4208 | 0.0089549 | 128.1222 | 0.11834 | 69.9555 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1691.2 | 1470.2 | 128.1329 | 0.010554 | 128.1222 | 0.11994 | 70.0514 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1691.4 | 1470.4 | 128.1329 | 0.0089549 | 128.1222 | 0.11994 | 70.3393 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1691.6 | 1470.6 | 128.2288 | 0.0089549 | 128.0263 | 0.11994 | 70.4353 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1691.8 | 1470.8 | 128.2288 | 0.0089549 | 128.0263 | 0.11994 | 70.6272 | 0.040589 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1692 | 1471 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 70.6272 | 0.040589 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1692.2 | 1471.2 | 128.3248 | 0.0089549 | 128.2182 | 0.11834 | 70.8192 | 0.042189 | 0.43001 | 0.0049255 | 126.0973 | 0.094661
1692.4 | 1471.4 | 128.3248 | 0.0089549 | 128.2182 | 0.11994 | 70.7232 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1692.6 | 1471.6 | 128.4208 | 0.0089549 | 128.1222 | 0.11994 | 70.8192 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1692.8 | 1471.8 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 70.9151 | 0.042189 | 0.526 | 0.0049255 | 126.0013 | 0.094661
1693 | 1472 | 128.4208 | 0.0089549 | 128.2182 | 0.11994 | 71.1071 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1693.2 | 1472.2 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 70.8192 | 0.042189 | 0.43001 | 0.0049255 | 126.1932 | 0.094661
1693.4 | 1472.4 | 128.4208 | 0.0089549 | 128.2182 | 0.11994 | 71.1071 | 0.040589 | 0.43001 | 0.0049255 | 126.2892 | 0.09626
1693.6 | 1472.6 | 128.4208 | 0.0089549 | 128.2182 | 0.11994 | 71.1071 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1693.8 | 1472.8 | 128.4208 | 0.0089549 | 128.2182 | 0.11994 | 71.1071 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1694 | 1473 | 128.3248 | 0.010554 | 128.1222 | 0.11994 | 71.4909 | 0.042189 | 0.526 | 0.0049255 | 126.0973 | 0.094661
1694.2 | 1473.2 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 71.6829 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1694.4 | 1473.4 | 128.4208 | 0.0089549 | 128.2182 | 0.11994 | 72.4506 | 0.043788 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1694.6 | 1473.6 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 72.6426 | 0.043788 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1694.8 | 1473.8 | 128.3248 | 0.010554 | 128.1222 | 0.11994 | 72.6426 | 0.042189 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1695 | 1474 | 128.3248 | 0.010554 | 128.1222 | 0.11994 | 72.5466 | 0.042189 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1695.2 | 1474.2 | 128.3248 | 0.010554 | 128.1222 | 0.12154 | 72.5466 | 0.043788 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1695.4 | 1474.4 | 128.3248 | 0.0089549 | 128.1222 | 0.12154 | 72.8345 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1695.6 | 1474.6 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 73.0264 | 0.043788 | 0.43001 | 0.0049255 | 126.2892 | 0.094661
1695.8 | 1474.8 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 73.2183 | 0.043788 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1696 | 1475 | 128.3248 | 0.0089549 | 128.1222 | 0.11994 | 73.1224 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.09626
1696.2 | 1475.2 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 73.2183 | 0.043788 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1696.4 | 1475.4 | 128.4208 | 0.010554 | 128.1222 | 0.11994 | 73.3143 | 0.043788 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1696.6 | 1475.6 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 73.3143 | 0.043788 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1696.8 | 1475.8 | 128.4208 | 0.0089549 | 128.2182 | 0.11994 | 73.4103 | 0.042189 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1697 | 1476 | 128.5167 | 0.0089549 | 128.2182 | 0.11994 | 73.5062 | 0.043788 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1697.2 | 1476.2 | 128.4208 | 0.0073551 | 128.2182 | 0.12154 | 73.8901 | 0.045388 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1697.4 | 1476.4 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 73.9861 | 0.043788 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1697.6 | 1476.6 | 128.4208 | 0.0089549 | 128.1222 | 0.12154 | 74.178 | 0.045388 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1697.8 | 1476.8 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 74.178 | 0.043788 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1698 | 1477 | 128.4208 | 0.0089549 | 128.1222 | 0.12154 | 74.178 | 0.045388 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1698.2 | 1477.2 | 128.5167 | 0.010554 | 128.3142 | 0.12154 | 74.5619 | 0.045388 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1698.4 | 1477.4 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 74.6578 | 0.045388 | 0.526 | 0.0049255 | 126.2892 | 0.09626
1698.6 | 1477.6 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 74.6578 | 0.045388 | 0.526 | 0.0049255 | 126.2892 | 0.09626
1698.8 | 1477.8 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 74.6578 | 0.045388 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1699 | 1478 | 128.4208 | 0.010554 | 128.2182 | 0.11994 | 74.7538 | 0.045388 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1699.2 | 1478.2 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 74.8498 | 0.045388 | 0.526 | 0.0065247 | 126.2892 | 0.094661
1699.4 | 1478.4 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 74.9457 | 0.045388 | 0.43001 | 0.0049255 | 126.3852 | 0.094661
1699.6 | 1478.6 | 128.4208 | 0.0089549 | 128.2182 | 0.12154 | 75.2337 | 0.045388 | 0.526 | 0.0049255 | 126.2892 | 0.09626
1699.8 | 1478.8 | 128.3248 | 0.0089549 | 128.1222 | 0.12154 | 75.3296 | 0.045388 | 0.526 | 0.0049255 | 126.1932 | 0.094661
1700 | 1479 | 128.2288 | 0.0089549 | 128.0263 | 0.12154 | 75.6175 | 0.045388 | 0.526 | 0.0049255 | 126.1932 | 0.09626
1720 | 1499 | 128.4208 | 0.0089549 | 128.1222 | 0.12474 | 82.5272 | 0.050186 | 0.526 | 0.0049255 | 126.2892 | 0.094661
1740 | 1519 | 128.9966 | 0.0089549 | 128.602 | 0.13274 | 95.6747 | 0.061382 | 0.90985 | 0.0081246 | 126.865 | 0.094661
1760 | 1539 | 129.9562 | 0.010554 | 129.6577 | 0.13434 | 102.6803 | 0.064581 | 1.5816 | 0.011324 | 127.9206 | 0.09626
1780 | 1559 | 129.9562 | 0.012154 | 129.3698 | 0.14074 | 113.0448 | 0.070979 | 1.5816 | 0.011324 | 127.7287 | 0.094661
1800 | 1579 | 129.6683 | 0.015352 | 128.9859 | 0.14233 | 114.3883 | 0.072578 | 1.5816 | 0.0097238 | 127.4408 | 0.09626
1850 | 1629 | 129.6683 | 0.031347 | 129.2738 | 0.14553 | 117.5552 | 0.075777 | 3.7889 | 0.025718 | 127.7287 | 0.094661
1900 | 1679 | 128.9006 | 0.05214 | 128.4101 | 0.14873 | 118.9947 | 0.075777 | 6.284 | 0.04971 | 126.3852 | 0.09626
1950 | 1729 | 129.1885 | 0.10332 | 128.698 | 0.14553 | 121.7778 | 0.077377 | 123.6519 | 0.092895 | 127.2489 | 0.09626
2000 | 1779 | 128.1329 | 0.10172 | 127.8343 | 0.14393 | 121.3939 | 0.077377 | 121.8286 | 0.089697 | 126.4811 | 0.09626
2050 | 1829 | 127.8449 | 0.10012 | 127.6424 | 0.14553 | 120.8181 | 0.075777 | 121.4447 | 0.089697 | 126.1932 | 0.09626
2100 | 1879 | 129.6683 | 0.10172 | 129.1779 | 0.14553 | 122.4496 | 0.077377 | 123.8439 | 0.091296 | 128.0166 | 0.09626
2150 | 1929 | 129.8603 | 0.056938 | 129.3698 | 0.16153 | 122.2576 | 0.078976 | 93.9981 | 0.067304 | 128.1126 | 0.09786
2200 | 1979 | 129.9562 | 0.047342 | 129.3698 | 0.17592 | 121.8737 | 0.077377 | 98.6045 | 0.070503 | 128.0166 | 0.09786
2250 | 2029 | 127.653 | 0.042543 | 127.6424 | 0.17752 | 119.1867 | 0.075777 | 98.7005 | 0.068904 | 125.9054 | 0.09626
2300 | 2079 | 127.653 | 0.047342 | 127.6424 | 0.17752 | 119.0907 | 0.075777 | 103.4988 | 0.073702 | 125.9054 | 0.09626
2350 | 2129 | 128.7087 | 0.047342 | 128.3142 | 0.18232 | 120.3383 | 0.077377 | 108.2972 | 0.0801 | 126.961 | 0.09786
2400 | 2179 | 127.653 | 0.05054 | 127.5464 | 0.17912 | 119.0907 | 0.077377 | 112.0399 | 0.083299 | 125.8094 | 0.09786
2450 | 2229 | 129.6683 | 0.060137 | 129.1779 | 0.17432 | 121.3939 | 0.078976 | 115.3028 | 0.084898 | 128.0166 | 0.09786
2500 | 2279 | 127.653 | 0.061737 | 127.6424 | 0.17272 | 119.3786 | 0.075777 | 116.1665 | 0.084898 | 125.9054 | 0.09626
2550 | 2329 | 129.6683 | 0.063336 | 129.0819 | 0.17752 | 121.8737 | 0.078976 | 119.9092 | 0.089697 | 127.8247 | 0.09786
2600 | 2379 | 128.0369 | 0.068135 | 127.8343 | 0.17272 | 120.4342 | 0.077377 | 120.0052 | 0.089697 | 126.1932 | 0.09786
2650 | 2429 | 127.749 | 0.066535 | 127.6424 | 0.17432 | 120.4342 | 0.077377 | 121.1568 | 0.091296 | 125.9054 | 0.09626
2700 | 2479 | 128.6127 | 0.069734 | 128.3142 | 0.17272 | 121.6818 | 0.078976 | 122.8842 | 0.092895 | 126.865 | 0.09786
2750 | 2529 | 128.1329 | 0.072933 | 127.9303 | 0.17272 | 121.3939 | 0.078976 | 123.556 | 0.094495 | 126.2892 | 0.09786
2800 | 2579 | 127.653 | 0.072933 | 127.6424 | 0.17112 | 121.2979 | 0.077377 | 123.6519 | 0.092895 | 125.9054 | 0.09786
2850 | 2629 | 127.749 | 0.076132 | 127.6424 | 0.16793 | 121.5858 | 0.078976 | 124.2277 | 0.094495 | 125.9054 | 0.09786
2900 | 2679 | 127.4611 | 0.077731 | 127.4504 | 0.16793 | 121.6818 | 0.078976 | 124.2277 | 0.094495 | 125.7134 | 0.09786
2950 | 2729 | 128.9006 | 0.079331 | 128.5061 | 0.16793 | 123.6011 | 0.080576 | 125.9552 | 0.094495 | 127.1529 | 0.099459
3000 | 2779 | 129.5724 | 0.08093 | 129.1779 | 0.16793 | 124.7527 | 0.078976 | 126.8188 | 0.096094 | 127.8247 | 0.099459
3050 | 2829 | 129.5724 | 0.082529 | 129.1779 | 0.16793 | 125.0407 | 0.080576 | 127.0108 | 0.096094 | 127.9206 | 0.099459
3100 | 2879 | 129.3804 | 0.079331 | 128.89 | 0.16953 | 125.0407 | 0.080576 | 126.7229 | 0.096094 | 127.6327 | 0.099459
3150 | 2929 | 129.4764 | 0.082529 | 128.9859 | 0.16953 | 125.3286 | 0.082175 | 127.0108 | 0.096094 | 127.8247 | 0.099459
3200 | 2979 | 127.749 | 0.079331 | 127.6424 | 0.16793 | 123.5052 | 0.080576 | 125.2834 | 0.096094 | 126.0973 | 0.099459
3250 | 3029 | 127.2692 | 0.079331 | 127.2585 | 0.16793 | 123.0253 | 0.080576 | 124.8995 | 0.096094 | 125.6175 | 0.09786
3300 | 3079 | 129.1885 | 0.079331 | 128.698 | 0.16953 | 125.4245 | 0.082175 | 126.9148 | 0.097694 | 127.6327 | 0.099459
3350 | 3129 | 129.0925 | 0.077731 | 128.698 | 0.17112 | 125.3286 | 0.080576 | 126.6269 | 0.096094 | 127.4408 | 0.099459
3400 | 3179 | 128.4208 | 0.079331 | 128.1222 | 0.17112 | 124.7527 | 0.082175 | 126.0511 | 0.097694 | 126.769 | 0.099459
3450 | 3229 | 127.4611 | 0.076132 | 127.4504 | 0.17272 | 123.6971 | 0.080576 | 125.2834 | 0.096094 | 126.0013 | 0.099459
3500 | 3279 | 128.3248 | 0.074532 | 128.0263 | 0.17272 | 124.7527 | 0.082175 | 125.8592 | 0.097694 | 126.6731 | 0.099459
3550 | 3329 | 127.557 | 0.072933 | 127.5464 | 0.17272 | 123.985 | 0.082175 | 125.2834 | 0.096094 | 126.0013 | 0.09786
3577 | 3356 | 127.557 | 0.072933 | 127.4504 | 0.17272 | 123.7931 | 0.082175 | 124.9955 | 0.096094 | 125.8094 | 0.09786

## Circuit 2 Faulting
Summary of Observed Faulting Behavior for Circuit #2
DAQ Time | Burner Time | Event | Discussion
Summary Observations |  |  | This circuit was set up to detect inter-cable hot shorts in a mixed bundle of TS and TP cables. At 286 seconds, one of the source cables (on Path 1) shorts to ground and causes a fuse blow failure. No cable-to-cable interactions are indicated.

## Converted Data C2
DAQ Time | Burner Time | C2 V1 | C2 A1 | C2 V2 | C2 A2 | C2 V4 | C2 A4 | C2 V5 | C2 A5 | C2 V6 | C2 A6
0 | -221 | 129.8101 | 0.0072281 | 129.1633 | 0.0095362 | 0.075065 | 0.00033201 | 0.019589 | 0.0022303 | 0.017929 | -0.00030988
10 | -211 | 129.7141 | 0.0072281 | 129.0673 | 0.0063372 | 0.075065 | -0.0012672 | 0.019589 | 0.0022303 | 0.11392 | -0.00030988
20 | -201 | 129.7141 | 0.0072281 | 129.0673 | 0.0079364 | 0.075065 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | -0.00030988
30 | -191 | 129.6182 | 0.0072281 | 128.9713 | 0.0079364 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | -0.00030988
40 | -181 | 129.5222 | 0.0088273 | 128.9713 | 0.0095362 | 0.17102 | 0.00033201 | 0.019589 | 0.0022303 | 0.11392 | -0.00030988
50 | -171 | 129.4263 | 0.0072281 | 128.7794 | 0.0079364 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | 0.0012893
60 | -161 | 129.4263 | 0.0072281 | 128.7794 | 0.0079364 | 0.17102 | 0.00033201 | 0.019589 | 0.0022303 | 0.11392 | 0.0012893
70 | -151 | 129.0424 | 0.0056289 | 128.3955 | 0.0063372 | 0.075065 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | -0.00030988
80 | -141 | 129.0424 | 0.00083003 | 128.4915 | 0.0015389 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | -0.00030988
90 | -131 | 128.9464 | 0.0024299 | 128.2995 | 0.0015389 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | 0.0012893
100 | -121 | 129.0424 | 0.00083003 | 128.3955 | 0.0031381 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893
110 | -111 | 129.1384 | 0.0024299 | 128.5874 | 0.0015389 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | 0.0012893
120 | -101 | 129.0424 | 0.00083003 | 128.4915 | 0.0031381 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | 0.0012893
130 | -91 | 129.3303 | 0.0024299 | 128.6834 | 0.0015389 | 0.17102 | 0.0019319 | 0.019589 | 0.0038295 | 0.20987 | 0.0012893
140 | -81 | 129.0424 | 0.0024299 | 128.4915 | 0.0031381 | 0.17102 | 0.0019319 | 0.11554 | 0.0038295 | 0.20987 | 0.0012893
150 | -71 | 128.9464 | 0.0040291 | 128.2995 | 0.004738 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.20987 | -0.00030988
160 | -61 | 128.8504 | 0.0056289 | 128.2995 | 0.004738 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.11392 | 0.0012893
170 | -51 | 129.2343 | 0.0088273 | 128.5874 | 0.0095362 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
180 | -41 | 129.3303 | 0.0088273 | 128.6834 | 0.0095362 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
190 | -31 | 129.3303 | 0.0088273 | 128.6834 | 0.0095362 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0012893
200 | -21 | 129.2343 | 0.0072281 | 128.5874 | 0.0079364 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
210 | -11 | 129.1384 | 0.0072281 | 128.4915 | 0.0063372 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.20987 | 0.0012893
220 | -1 | 129.0424 | 0.0072281 | 128.4915 | 0.0063372 | 0.17102 | 0.00033201 | 0.019589 | 0.0038295 | 0.20987 | 0.0012893
230 | 9 | 128.9464 | 0.0056289 | 128.2995 | 0.004738 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0012893
240 | 19 | 128.6585 | 0.0024299 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.11392 | 0.0028892
250 | 29 | 128.7545 | 0.0024299 | 128.1076 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
260 | 39 | 129.0424 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
270 | 49 | 129.1384 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.11392 | 0.0028892
270.2 | 49.2 | 129.1384 | 0.0024299 | 128.5874 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
270.4 | 49.4 | 129.2343 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.11392 | 0.0028892
270.6 | 49.6 | 129.1384 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
270.8 | 49.8 | 129.1384 | 0.0024299 | 128.5874 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
271 | 50 | 129.1384 | 0.0024299 | 128.5874 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
271.2 | 50.2 | 129.2343 | 0.00083003 | 128.5874 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0038295 | 0.20987 | 0.0012893
271.4 | 50.4 | 129.1384 | 0.0024299 | 128.5874 | 0.0015389 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
271.6 | 50.6 | 129.2343 | 0.00083003 | 128.5874 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
271.8 | 50.8 | 129.1384 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
272 | 51 | 129.0424 | 0.00083003 | 128.4915 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
272.2 | 51.2 | 129.1384 | 0.0024299 | 128.5874 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
272.4 | 51.4 | 129.1384 | 0.0024299 | 128.4915 | 0.0015389 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
272.6 | 51.6 | 129.1384 | 0.0024299 | 128.5874 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
272.8 | 51.8 | 129.1384 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
273 | 52 | 129.1384 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
273.2 | 52.2 | 129.1384 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
273.4 | 52.4 | 129.1384 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
273.6 | 52.6 | 129.1384 | 0.0024299 | 128.5874 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
273.8 | 52.8 | 129.1384 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
274 | 53 | 129.0424 | 0.0024299 | 128.3955 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
274.2 | 53.2 | 129.0424 | 0.0024299 | 128.4915 | 0.0031381 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
274.4 | 53.4 | 129.0424 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0070285 | 0.20987 | 0.0028892
274.6 | 53.6 | 129.1384 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
274.8 | 53.8 | 129.1384 | 0.0024299 | 128.4915 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
275 | 54 | 129.0424 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
275.2 | 54.2 | 129.0424 | 0.0024299 | 128.4915 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
275.4 | 54.4 | 129.0424 | 0.0024299 | 128.3955 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
275.6 | 54.6 | 129.0424 | 0.0024299 | 128.3955 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0028892
275.8 | 54.8 | 129.0424 | 0.00083003 | 128.3955 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
276 | 55 | 128.9464 | 0.0024299 | 128.3955 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
276.2 | 55.2 | 129.0424 | 0.0024299 | 128.3955 | 0.0031381 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
276.4 | 55.4 | 129.0424 | 0.0024299 | 128.3955 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892
276.6 | 55.6 | 129.0424 | 0.0024299 | 128.3955 | 0.0031381 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
276.8 | 55.8 | 129.0424 | 0.0024299 | 128.3955 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
277 | 56 | 129.0424 | 0.0024299 | 128.3955 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
277.2 | 56.2 | 128.9464 | 0.0024299 | 128.2995 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
277.4 | 56.4 | 128.9464 | 0.0024299 | 128.2995 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
277.6 | 56.6 | 128.9464 | 0.0024299 | 128.2995 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0028892
277.8 | 56.8 | 128.9464 | 0.0024299 | 128.2995 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
278 | 57 | 128.9464 | 0.0024299 | 128.2995 | 0.0031381 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
278.2 | 57.2 | 128.9464 | 0.0024299 | 128.2995 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
278.4 | 57.4 | 128.9464 | 0.0024299 | 128.2995 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
278.6 | 57.6 | 128.9464 | 0.0024299 | 128.2995 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892
278.8 | 57.8 | 128.9464 | 0.0024299 | 128.2995 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
279 | 58 | 128.9464 | 0.0024299 | 128.2995 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
279.2 | 58.2 | 128.8504 | 0.0024299 | 128.2995 | 0.0015389 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
279.4 | 58.4 | 128.8504 | 0.0024299 | 128.2995 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
279.6 | 58.6 | 128.8504 | 0.0024299 | 128.2036 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
279.8 | 58.8 | 128.8504 | 0.0024299 | 128.2036 | 0.0015389 | 0.17102 | 0.0019319 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
280 | 59 | 128.7545 | 0.0024299 | 128.1076 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
280.2 | 59.2 | 128.8504 | 0.0024299 | 128.1076 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
280.4 | 59.4 | 128.7545 | 0.0024299 | 128.2036 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0012893
280.6 | 59.6 | 128.7545 | 0.0024299 | 128.1076 | 0.0015389 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
280.8 | 59.8 | 128.7545 | 0.0024299 | 128.2036 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
281 | 60 | 128.8504 | 0.0024299 | 128.2036 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
281.2 | 60.2 | 128.7545 | 0.0040291 | 128.2036 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
281.4 | 60.4 | 128.6585 | 0.0024299 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
281.6 | 60.6 | 128.7545 | 0.0024299 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
281.8 | 60.8 | 128.7545 | 0.0024299 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
282 | 61 | 128.6585 | 0.0024299 | 128.0117 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
282.2 | 61.2 | 128.7545 | 0.0024299 | 128.2036 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892
282.4 | 61.4 | 128.7545 | 0.0024299 | 128.1076 | 0.0031381 | 0.17102 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
282.6 | 61.6 | 128.7545 | 0.0024299 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
282.8 | 61.8 | 128.7545 | 0.0040291 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
283 | 62 | 128.7545 | 0.0024299 | 128.2036 | 0.004738 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
283.2 | 62.2 | 128.7545 | 0.0040291 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.11392 | 0.0028892
283.4 | 62.4 | 128.6585 | 0.0040291 | 128.1076 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
283.6 | 62.6 | 128.6585 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
283.8 | 62.8 | 128.7545 | 0.0040291 | 128.2036 | 0.0031381 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
284 | 63 | 128.7545 | 0.0056289 | 128.1076 | 0.004738 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
284.2 | 63.2 | 128.7545 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
284.4 | 63.4 | 128.7545 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
284.6 | 63.6 | 128.6585 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
284.8 | 63.8 | 128.6585 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
285 | 64 | 128.7545 | 0.0056289 | 128.2036 | 0.004738 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
285.2 | 64.2 | 128.7545 | 0.0056289 | 128.2036 | 0.004738 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
285.4 | 64.4 | 128.7545 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
285.6 | 64.6 | 128.7545 | 0.0040291 | 128.1076 | 0.004738 | 0.17102 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
285.8 | 64.8 | 128.7545 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.11554 | 0.0070285 | 0.20987 | 0.0012893
286 | 65 | 128.7545 | 0.0040291 | 128.1076 | 0.004738 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
286.2 | 65.2 | 68.3911 | 5.3206 | 69.1837 | 0.0031381 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
286.4 | 65.4 | 7.26 | 0.41349 | 7.3808 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
286.6 | 65.6 | 2.0777 | 0.048814 | 2.0067 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
286.8 | 65.8 | 1.1181 | 0.015225 | 0.95104 | 0.0015389 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.30582 | 0.0028892
287 | 66 | 0.83014 | 0.0088273 | 0.7591 | 0.0015389 | 0.17102 | 0.0019319 | 0.019589 | 0.0054293 | 0.20987 | 0.0012893
287.2 | 66.2 | 0.73419 | 0.0056289 | 0.66314 | 0.0015389 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
287.4 | 66.4 | 0.63824 | 0.0040291 | 0.56715 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
287.6 | 66.6 | 0.63824 | 0.0040291 | 0.56715 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
287.8 | 66.8 | 0.54225 | 0.0040291 | 0.56715 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
288 | 67 | 0.54225 | 0.0024299 | 0.4712 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.11392 | 0.0028892
288.2 | 67.2 | 0.54225 | 0.0024299 | 0.4712 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
288.4 | 67.4 | 0.54225 | 0.0040291 | 0.4712 | 0.0015389 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
288.6 | 67.6 | 0.4463 | 0.0024299 | 0.4712 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0038295 | 0.20987 | 0.0028892
288.8 | 67.8 | 0.54225 | 0.0024299 | 0.4712 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
289 | 68 | 0.54225 | 0.0024299 | 0.37521 | 0.0015389 | 0.17102 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
289.2 | 68.2 | 0.4463 | 0.00083003 | 0.4712 | -6.0896e-05 | 0.26697 | 0.00033201 | 0.019589 | 0.0054293 | 0.20987 | 0.0028892
289.4 | 68.4 | 0.4463 | 0.0024299 | 0.37521 | 0.0015389 | 0.26697 | 0.00033201 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
289.6 | 68.6 | 0.4463 | 0.0024299 | 0.37521 | 0.0015389 | 0.17102 | -0.0012672 | 0.11554 | 0.0054293 | 0.20987 | 0.0012893
289.8 | 68.8 | 0.4463 | 0.00083003 | 0.37521 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
290 | 69 | 0.54225 | 0.00083003 | 0.37521 | 0.0015389 | 0.26697 | 0.0019319 | 0.11554 | 0.0054293 | 0.20987 | 0.0028892
300 | 79
310 | 89
320 | 99
330 | 109
340 | 119
350 | 129
360 | 139
370 | 149
380 | 159
390 | 169
400 | 179
410 | 189
420 | 199
430 | 209
440 | 219
450 | 229
460 | 239
470 | 249
480 | 259
490 | 269
500 | 279
510 | 289
520 | 299
530 | 309
540 | 319
550 | 329
560 | 339
570 | 349
580 | 359
590 | 369
600 | 379
610 | 389
620 | 399
630 | 409
640 | 419
650 | 429
660 | 439
670 | 449
680 | 459
690 | 469
700 | 479
710 | 489
720 | 499
730 | 509
740 | 519
750 | 529
760 | 539
770 | 549
780 | 559
790 | 569
790.2 | 569.2
790.4 | 569.4
790.6 | 569.6
790.8 | 569.8
791 | 570
791.2 | 570.2
791.4 | 570.4
791.6 | 570.6
791.8 | 570.8
792 | 571
792.2 | 571.2
792.4 | 571.4
792.6 | 571.6
792.8 | 571.8
793 | 572
793.2 | 572.2
793.4 | 572.4
793.6 | 572.6
793.8 | 572.8
794 | 573
794.2 | 573.2
794.4 | 573.4
794.6 | 573.6
794.8 | 573.8
795 | 574
795.2 | 574.2
795.4 | 574.4
795.6 | 574.6
795.8 | 574.8
796 | 575
796.2 | 575.2
796.4 | 575.4
796.6 | 575.6
796.8 | 575.8
797 | 576
797.2 | 576.2
797.4 | 576.4
797.6 | 576.6
797.8 | 576.8
798 | 577
798.2 | 577.2
798.4 | 577.4
798.6 | 577.6
798.8 | 577.8
799 | 578
799.2 | 578.2
799.4 | 578.4
799.6 | 578.6
799.8 | 578.8
800 | 579
800.2 | 579.2
800.4 | 579.4
800.6 | 579.6
800.8 | 579.8
801 | 580
801.2 | 580.2
801.4 | 580.4
801.6 | 580.6
801.8 | 580.8
802 | 581
802.2 | 581.2
802.4 | 581.4
802.6 | 581.6
802.8 | 581.8
803 | 582
803.2 | 582.2
803.4 | 582.4
803.6 | 582.6
803.8 | 582.8
804 | 583
804.2 | 583.2
804.4 | 583.4
804.6 | 583.6
804.8 | 583.8
805 | 584
805.2 | 584.2
805.4 | 584.4
805.6 | 584.6
805.8 | 584.8
806 | 585
806.2 | 585.2
806.4 | 585.4
806.6 | 585.6
806.8 | 585.8
807 | 586
808 | 587
810 | 589
820 | 599
830 | 609
840 | 619
850 | 629
860 | 639
870 | 649
880 | 659
890 | 669
900 | 679
910 | 689
920 | 699
930 | 709
940 | 719
950 | 729
960 | 739
970 | 749
980 | 759
990 | 769
1000 | 779
1010 | 789
1020 | 799
1030 | 809
1040 | 819
1050 | 829
1060 | 839
1070 | 849
1080 | 859
1090 | 869
1100 | 879
1110 | 889
1120 | 899
1130 | 909
1140 | 919
1150 | 929
1160 | 939
1170 | 949
1180 | 959
1190 | 969
1200 | 979
1210 | 989
1220 | 999
1230 | 1009
1240 | 1019
1240.2 | 1019.2
1250 | 1029
1260 | 1039
1270 | 1049
1280 | 1059
1290 | 1069
1300 | 1079
1310 | 1089
1320 | 1099
1330 | 1109
1340 | 1119
1350 | 1129
1360 | 1139
1370 | 1149
1380 | 1159
1390 | 1169
1400 | 1179
1410 | 1189
1420 | 1199
1430 | 1209
1440 | 1219
1450 | 1229
1450.2 | 1229.2
1450.4 | 1229.4
1450.6 | 1229.6
1450.8 | 1229.8
1451 | 1230
1451.2 | 1230.2
1451.4 | 1230.4
1451.6 | 1230.6
1451.8 | 1230.8
1452 | 1231
1452.2 | 1231.2
1452.4 | 1231.4
1452.6 | 1231.6
1452.8 | 1231.8
1453 | 1232
1453.2 | 1232.2
1453.4 | 1232.4
1453.6 | 1232.6
1453.8 | 1232.8
1454 | 1233
1454.2 | 1233.2
1454.4 | 1233.4
1454.6 | 1233.6
1454.8 | 1233.8
1455 | 1234
1455.2 | 1234.2
1455.4 | 1234.4
1455.6 | 1234.6
1455.8 | 1234.8
1456 | 1235
1456.2 | 1235.2
1456.4 | 1235.4
1456.6 | 1235.6
1456.8 | 1235.8
1457 | 1236
1457.2 | 1236.2
1457.4 | 1236.4
1457.6 | 1236.6
1457.8 | 1236.8
1458 | 1237
1458.2 | 1237.2
1458.4 | 1237.4
1458.6 | 1237.6
1458.8 | 1237.8
1459 | 1238
1459.2 | 1238.2
1459.4 | 1238.4
1459.6 | 1238.6
1459.8 | 1238.8
1460 | 1239
1460.2 | 1239.2
1460.4 | 1239.4
1460.6 | 1239.6
1460.8 | 1239.8
1461 | 1240
1461.2 | 1240.2
1461.4 | 1240.4
1461.6 | 1240.6
1461.8 | 1240.8
1462 | 1241
1462.2 | 1241.2
1462.4 | 1241.4
1462.6 | 1241.6
1462.8 | 1241.8
1463 | 1242
1463.2 | 1242.2
1463.4 | 1242.4
1463.6 | 1242.6
1463.8 | 1242.8
1464 | 1243
1464.2 | 1243.2
1464.4 | 1243.4
1464.6 | 1243.6
1464.8 | 1243.8
1465 | 1244
1465.2 | 1244.2
1465.4 | 1244.4
1465.6 | 1244.6
1465.8 | 1244.8
1466 | 1245
1466.2 | 1245.2
1466.4 | 1245.4
1466.6 | 1245.6
1466.8 | 1245.8
1467 | 1246
1467.2 | 1246.2
1467.4 | 1246.4
1467.6 | 1246.6
1467.8 | 1246.8
1468 | 1247
1468.2 | 1247.2
1468.4 | 1247.4
1468.6 | 1247.6
1468.8 | 1247.8
1469 | 1248
1469.2 | 1248.2
1469.4 | 1248.4
1469.6 | 1248.6
1469.8 | 1248.8
1470 | 1249
1470.2 | 1249.2
1470.4 | 1249.4
1470.6 | 1249.6
1470.8 | 1249.8
1471 | 1250
1471.2 | 1250.2
1471.4 | 1250.4
1471.6 | 1250.6
1471.8 | 1250.8
1472 | 1251
1472.2 | 1251.2
1472.4 | 1251.4
1472.6 | 1251.6
1472.8 | 1251.8
1473 | 1252
1473.2 | 1252.2
1473.4 | 1252.4
1473.6 | 1252.6
1473.8 | 1252.8
1474 | 1253
1474.2 | 1253.2
1474.4 | 1253.4
1474.6 | 1253.6
1474.8 | 1253.8
1475 | 1254
1475.2 | 1254.2
1475.4 | 1254.4
1475.6 | 1254.6
1475.8 | 1254.8
1476 | 1255
1476.2 | 1255.2
1476.4 | 1255.4
1476.6 | 1255.6
1476.8 | 1255.8
1477 | 1256
1477.2 | 1256.2
1477.4 | 1256.4
1477.6 | 1256.6
1477.8 | 1256.8
1478 | 1257
1478.2 | 1257.2
1478.4 | 1257.4
1478.6 | 1257.6
1478.8 | 1257.8
1479 | 1258
1479.2 | 1258.2
1479.4 | 1258.4
1479.6 | 1258.6
1479.8 | 1258.8
1480 | 1259
1480.2 | 1259.2
1480.4 | 1259.4
1480.6 | 1259.6
1480.8 | 1259.8
1481 | 1260
1481.2 | 1260.2
1481.4 | 1260.4
1481.6 | 1260.6
1481.8 | 1260.8
1482 | 1261
1482.2 | 1261.2
1482.4 | 1261.4
1482.6 | 1261.6
1482.8 | 1261.8
1483 | 1262
1483.2 | 1262.2
1483.4 | 1262.4
1483.6 | 1262.6
1483.8 | 1262.8
1484 | 1263
1484.2 | 1263.2
1484.4 | 1263.4
1484.6 | 1263.6
1484.8 | 1263.8
1485 | 1264
1485.2 | 1264.2
1485.4 | 1264.4
1485.6 | 1264.6
1485.8 | 1264.8
1486 | 1265
1486.2 | 1265.2
1486.4 | 1265.4
1486.6 | 1265.6
1486.8 | 1265.8
1487 | 1266
1487.2 | 1266.2
1487.4 | 1266.4
1487.6 | 1266.6
1487.8 | 1266.8
1488 | 1267
1488.2 | 1267.2
1488.4 | 1267.4
1488.6 | 1267.6
1488.8 | 1267.8
1489 | 1268
1489.2 | 1268.2
1489.4 | 1268.4
1489.6 | 1268.6
1489.8 | 1268.8
1490 | 1269
1490.2 | 1269.2
1490.4 | 1269.4
1490.6 | 1269.6
1490.8 | 1269.8
1491 | 1270
1491.2 | 1270.2
1491.4 | 1270.4
1491.6 | 1270.6
1491.8 | 1270.8
1492 | 1271
1492.2 | 1271.2
1492.4 | 1271.4
1492.6 | 1271.6
1492.8 | 1271.8
1493 | 1272
1493.2 | 1272.2
1493.4 | 1272.4
1493.6 | 1272.6
1493.8 | 1272.8
1494 | 1273
1494.2 | 1273.2
1494.4 | 1273.4
1494.6 | 1273.6
1494.8 | 1273.8
1495 | 1274
1495.2 | 1274.2
1495.4 | 1274.4
1495.6 | 1274.6
1495.8 | 1274.8
1496 | 1275
1496.2 | 1275.2
1496.4 | 1275.4
1496.6 | 1275.6
1496.8 | 1275.8
1497 | 1276
1497.2 | 1276.2
1497.4 | 1276.4
1497.6 | 1276.6
1497.8 | 1276.8
1498 | 1277
1498.2 | 1277.2
1498.4 | 1277.4
1498.6 | 1277.6
1498.8 | 1277.8
1499 | 1278
1499.2 | 1278.2
1499.4 | 1278.4
1499.6 | 1278.6
1499.8 | 1278.8
1500 | 1279
1500.2 | 1279.2
1500.4 | 1279.4
1500.6 | 1279.6
1500.8 | 1279.8
1501 | 1280
1501.2 | 1280.2
1501.4 | 1280.4
1501.6 | 1280.6
1501.8 | 1280.8
1502 | 1281
1502.2 | 1281.2
1502.4 | 1281.4
1502.6 | 1281.6
1502.8 | 1281.8
1503 | 1282
1503.2 | 1282.2
1503.4 | 1282.4
1503.6 | 1282.6
1503.8 | 1282.8
1504 | 1283
1504.2 | 1283.2
1504.4 | 1283.4
1504.6 | 1283.6
1504.8 | 1283.8
1505 | 1284
1505.2 | 1284.2
1505.4 | 1284.4
1505.6 | 1284.6
1505.8 | 1284.8
1506 | 1285
1506.2 | 1285.2
1506.4 | 1285.4
1506.6 | 1285.6
1506.8 | 1285.8
1507 | 1286
1507.2 | 1286.2
1507.4 | 1286.4
1507.6 | 1286.6
1507.8 | 1286.8
1508 | 1287
1508.2 | 1287.2
1508.4 | 1287.4
1508.6 | 1287.6
1508.8 | 1287.8
1509 | 1288
1509.2 | 1288.2
1509.4 | 1288.4
1509.6 | 1288.6
1509.8 | 1288.8
1510 | 1289
1510.2 | 1289.2
1510.4 | 1289.4
1510.6 | 1289.6
1510.8 | 1289.8
1511 | 1290
1511.2 | 1290.2
1511.4 | 1290.4
1511.6 | 1290.6
1511.8 | 1290.8
1512 | 1291
1512.2 | 1291.2
1512.4 | 1291.4
1512.6 | 1291.6
1512.8 | 1291.8
1513 | 1292
1513.2 | 1292.2
1513.4 | 1292.4
1513.6 | 1292.6
1513.8 | 1292.8
1514 | 1293
1514.2 | 1293.2
1514.4 | 1293.4
1514.6 | 1293.6
1514.8 | 1293.8
1515 | 1294
1515.2 | 1294.2
1515.4 | 1294.4
1515.6 | 1294.6
1515.8 | 1294.8
1516 | 1295
1516.2 | 1295.2
1516.4 | 1295.4
1516.6 | 1295.6
1516.8 | 1295.8
1517 | 1296
1517.2 | 1296.2
1517.4 | 1296.4
1517.6 | 1296.6
1517.8 | 1296.8
1518 | 1297
1518.2 | 1297.2
1518.4 | 1297.4
1518.6 | 1297.6
1518.8 | 1297.8
1519 | 1298
1519.2 | 1298.2
1519.4 | 1298.4
1519.6 | 1298.6
1519.8 | 1298.8
1520 | 1299
1520.2 | 1299.2
1520.4 | 1299.4
1520.6 | 1299.6
1520.8 | 1299.8
1521 | 1300
1521.2 | 1300.2
1521.4 | 1300.4
1521.6 | 1300.6
1521.8 | 1300.8
1522 | 1301
1522.2 | 1301.2
1522.4 | 1301.4
1522.6 | 1301.6
1522.8 | 1301.8
1523 | 1302
1523.2 | 1302.2
1523.4 | 1302.4
1523.6 | 1302.6
1523.8 | 1302.8
1524 | 1303
1524.2 | 1303.2
1524.4 | 1303.4
1524.6 | 1303.6
1524.8 | 1303.8
1525 | 1304
1525.2 | 1304.2
1525.4 | 1304.4
1525.6 | 1304.6
1525.8 | 1304.8
1526 | 1305
1526.2 | 1305.2
1526.4 | 1305.4
1526.6 | 1305.6
1526.8 | 1305.8
1527 | 1306
1527.2 | 1306.2
1527.4 | 1306.4
1527.6 | 1306.6
1527.8 | 1306.8
1528 | 1307
1528.2 | 1307.2
1528.4 | 1307.4
1528.6 | 1307.6
1528.8 | 1307.8
1529 | 1308
1529.2 | 1308.2
1529.4 | 1308.4
1529.6 | 1308.6
1529.8 | 1308.8
1530 | 1309
1530.2 | 1309.2
1530.4 | 1309.4
1530.6 | 1309.6
1530.8 | 1309.8
1531 | 1310
1531.2 | 1310.2
1531.4 | 1310.4
1531.6 | 1310.6
1531.8 | 1310.8
1532 | 1311
1532.2 | 1311.2
1532.4 | 1311.4
1532.6 | 1311.6
1532.8 | 1311.8
1533 | 1312
1533.2 | 1312.2
1533.4 | 1312.4
1533.6 | 1312.6
1533.8 | 1312.8
1534 | 1313
1534.2 | 1313.2
1534.4 | 1313.4
1534.6 | 1313.6
1534.8 | 1313.8
1535 | 1314
1535.2 | 1314.2
1535.4 | 1314.4
1535.6 | 1314.6
1535.8 | 1314.8
1536 | 1315
1536.2 | 1315.2
1536.4 | 1315.4
1536.6 | 1315.6
1536.8 | 1315.8
1537 | 1316
1537.2 | 1316.2
1537.4 | 1316.4
1537.6 | 1316.6
1537.8 | 1316.8
1538 | 1317
1538.2 | 1317.2
1538.4 | 1317.4
1538.6 | 1317.6
1538.8 | 1317.8
1539 | 1318
1539.2 | 1318.2
1539.4 | 1318.4
1539.6 | 1318.6
1539.8 | 1318.8
1540 | 1319
1540.2 | 1319.2
1540.4 | 1319.4
1540.6 | 1319.6
1540.8 | 1319.8
1541 | 1320
1541.2 | 1320.2
1541.4 | 1320.4
1541.6 | 1320.6
1541.8 | 1320.8
1542 | 1321
1542.2 | 1321.2
1542.4 | 1321.4
1542.6 | 1321.6
1542.8 | 1321.8
1543 | 1322
1543.2 | 1322.2
1543.4 | 1322.4
1543.6 | 1322.6
1543.8 | 1322.8
1544 | 1323
1544.2 | 1323.2
1544.4 | 1323.4
1544.6 | 1323.6
1544.8 | 1323.8
1545 | 1324
1545.2 | 1324.2
1545.4 | 1324.4
1545.6 | 1324.6
1545.8 | 1324.8
1546 | 1325
1546.2 | 1325.2
1546.4 | 1325.4
1546.6 | 1325.6
1546.8 | 1325.8
1547 | 1326
1547.2 | 1326.2
1547.4 | 1326.4
1547.6 | 1326.6
1547.8 | 1326.8
1548 | 1327
1548.2 | 1327.2
1548.4 | 1327.4
1548.6 | 1327.6
1548.8 | 1327.8
1549 | 1328
1549.2 | 1328.2
1549.4 | 1328.4
1549.6 | 1328.6
1549.8 | 1328.8
1550 | 1329
1550.2 | 1329.2
1550.4 | 1329.4
1550.6 | 1329.6
1550.8 | 1329.8
1551 | 1330
1551.2 | 1330.2
1551.4 | 1330.4
1551.6 | 1330.6
1551.8 | 1330.8
1552 | 1331
1552.2 | 1331.2
1552.4 | 1331.4
1552.6 | 1331.6
1552.8 | 1331.8
1553 | 1332
1553.2 | 1332.2
1553.4 | 1332.4
1553.6 | 1332.6
1553.8 | 1332.8
1554 | 1333
1554.2 | 1333.2
1554.4 | 1333.4
1554.6 | 1333.6
1554.8 | 1333.8
1555 | 1334
1555.2 | 1334.2
1555.4 | 1334.4
1555.6 | 1334.6
1555.8 | 1334.8
1556 | 1335
1556.2 | 1335.2
1556.4 | 1335.4
1556.6 | 1335.6
1556.8 | 1335.8
1557 | 1336
1557.2 | 1336.2
1557.4 | 1336.4
1557.6 | 1336.6
1557.8 | 1336.8
1558 | 1337
1558.2 | 1337.2
1558.4 | 1337.4
1558.6 | 1337.6
1558.8 | 1337.8
1559 | 1338
1559.2 | 1338.2
1559.4 | 1338.4
1559.6 | 1338.6
1559.8 | 1338.8
1560 | 1339
1560.2 | 1339.2
1560.4 | 1339.4
1560.6 | 1339.6
1560.8 | 1339.8
1561 | 1340
1561.2 | 1340.2
1561.4 | 1340.4
1561.6 | 1340.6
1561.8 | 1340.8
1562 | 1341
1562.2 | 1341.2
1562.4 | 1341.4
1562.6 | 1341.6
1562.8 | 1341.8
1563 | 1342
1563.2 | 1342.2
1563.4 | 1342.4
1563.6 | 1342.6
1563.8 | 1342.8
1564 | 1343
1564.2 | 1343.2
1564.4 | 1343.4
1564.6 | 1343.6
1564.8 | 1343.8
1565 | 1344
1565.2 | 1344.2
1565.4 | 1344.4
1565.6 | 1344.6
1565.8 | 1344.8
1566 | 1345
1566.2 | 1345.2
1566.4 | 1345.4
1566.6 | 1345.6
1566.8 | 1345.8
1567 | 1346
1567.2 | 1346.2
1567.4 | 1346.4
1567.6 | 1346.6
1567.8 | 1346.8
1568 | 1347
1568.2 | 1347.2
1568.4 | 1347.4
1568.6 | 1347.6
1568.8 | 1347.8
1569 | 1348
1569.2 | 1348.2
1569.4 | 1348.4
1569.6 | 1348.6
1569.8 | 1348.8
1570 | 1349
1570.2 | 1349.2
1570.4 | 1349.4
1570.6 | 1349.6
1570.8 | 1349.8
1571 | 1350
1571.2 | 1350.2
1571.4 | 1350.4
1571.6 | 1350.6
1571.8 | 1350.8
1572 | 1351
1572.2 | 1351.2
1572.4 | 1351.4
1572.6 | 1351.6
1572.8 | 1351.8
1573 | 1352
1573.2 | 1352.2
1573.4 | 1352.4
1573.6 | 1352.6
1573.8 | 1352.8
1574 | 1353
1574.2 | 1353.2
1574.4 | 1353.4
1574.6 | 1353.6
1574.8 | 1353.8
1575 | 1354
1575.2 | 1354.2
1575.4 | 1354.4
1575.6 | 1354.6
1575.8 | 1354.8
1576 | 1355
1576.2 | 1355.2
1576.4 | 1355.4
1576.6 | 1355.6
1576.8 | 1355.8
1577 | 1356
1577.2 | 1356.2
1577.4 | 1356.4
1577.6 | 1356.6
1577.8 | 1356.8
1578 | 1357
1578.2 | 1357.2
1578.4 | 1357.4
1578.6 | 1357.6
1578.8 | 1357.8
1579 | 1358
1579.2 | 1358.2
1579.4 | 1358.4
1579.6 | 1358.6
1579.8 | 1358.8
1580 | 1359
1580.2 | 1359.2
1580.4 | 1359.4
1580.6 | 1359.6
1580.8 | 1359.8
1581 | 1360
1581.2 | 1360.2
1581.4 | 1360.4
1581.6 | 1360.6
1581.8 | 1360.8
1582 | 1361
1582.2 | 1361.2
1582.4 | 1361.4
1582.6 | 1361.6
1582.8 | 1361.8
1583 | 1362
1583.2 | 1362.2
1583.4 | 1362.4
1583.6 | 1362.6
1583.8 | 1362.8
1584 | 1363
1584.2 | 1363.2
1584.4 | 1363.4
1584.6 | 1363.6
1584.8 | 1363.8
1585 | 1364
1585.2 | 1364.2
1585.4 | 1364.4
1585.6 | 1364.6
1585.8 | 1364.8
1586 | 1365
1586.2 | 1365.2
1586.4 | 1365.4
1586.6 | 1365.6
1586.8 | 1365.8
1587 | 1366
1587.2 | 1366.2
1587.4 | 1366.4
1587.6 | 1366.6
1587.8 | 1366.8
1588 | 1367
1588.2 | 1367.2
1588.4 | 1367.4
1588.6 | 1367.6
1588.8 | 1367.8
1589 | 1368
1589.2 | 1368.2
1589.4 | 1368.4
1589.6 | 1368.6
1589.8 | 1368.8
1590 | 1369
1590.2 | 1369.2
1590.4 | 1369.4
1590.6 | 1369.6
1590.8 | 1369.8
1591 | 1370
1591.2 | 1370.2
1591.4 | 1370.4
1591.6 | 1370.6
1591.8 | 1370.8
1592 | 1371
1592.2 | 1371.2
1592.4 | 1371.4
1592.6 | 1371.6
1592.8 | 1371.8
1593 | 1372
1593.2 | 1372.2
1593.4 | 1372.4
1593.6 | 1372.6
1593.8 | 1372.8
1594 | 1373
1594.2 | 1373.2
1594.4 | 1373.4
1594.6 | 1373.6
1594.8 | 1373.8
1595 | 1374
1595.2 | 1374.2
1595.4 | 1374.4
1595.6 | 1374.6
1595.8 | 1374.8
1596 | 1375
1596.2 | 1375.2
1596.4 | 1375.4
1596.6 | 1375.6
1596.8 | 1375.8
1597 | 1376
1597.2 | 1376.2
1597.4 | 1376.4
1597.6 | 1376.6
1597.8 | 1376.8
1598 | 1377
1598.2 | 1377.2
1598.4 | 1377.4
1598.6 | 1377.6
1598.8 | 1377.8
1599 | 1378
1599.2 | 1378.2
1599.4 | 1378.4
1599.6 | 1378.6
1599.8 | 1378.8
1600 | 1379
1600.2 | 1379.2
1600.4 | 1379.4
1600.6 | 1379.6
1600.8 | 1379.8
1601 | 1380
1601.2 | 1380.2
1601.4 | 1380.4
1601.6 | 1380.6
1601.8 | 1380.8
1602 | 1381
1602.2 | 1381.2
1602.4 | 1381.4
1602.6 | 1381.6
1602.8 | 1381.8
1603 | 1382
1603.2 | 1382.2
1603.4 | 1382.4
1603.6 | 1382.6
1603.8 | 1382.8
1604 | 1383
1604.2 | 1383.2
1604.4 | 1383.4
1604.6 | 1383.6
1604.8 | 1383.8
1605 | 1384
1605.2 | 1384.2
1605.4 | 1384.4
1605.6 | 1384.6
1605.8 | 1384.8
1606 | 1385
1606.2 | 1385.2
1606.4 | 1385.4
1606.6 | 1385.6
1606.8 | 1385.8
1607 | 1386
1607.2 | 1386.2
1607.4 | 1386.4
1607.6 | 1386.6
1607.8 | 1386.8
1608 | 1387
1608.2 | 1387.2
1608.4 | 1387.4
1608.6 | 1387.6
1608.8 | 1387.8
1609 | 1388
1609.2 | 1388.2
1609.4 | 1388.4
1609.6 | 1388.6
1609.8 | 1388.8
1610 | 1389
1610.2 | 1389.2
1610.4 | 1389.4
1610.6 | 1389.6
1610.8 | 1389.8
1611 | 1390
1611.2 | 1390.2
1611.4 | 1390.4
1611.6 | 1390.6
1611.8 | 1390.8
1612 | 1391
1612.2 | 1391.2
1612.4 | 1391.4
1612.6 | 1391.6
1612.8 | 1391.8
1613 | 1392
1613.2 | 1392.2
1613.4 | 1392.4
1613.6 | 1392.6
1613.8 | 1392.8
1614 | 1393
1614.2 | 1393.2
1614.4 | 1393.4
1614.6 | 1393.6
1614.8 | 1393.8
1615 | 1394
1615.2 | 1394.2
1615.4 | 1394.4
1615.6 | 1394.6
1615.8 | 1394.8
1616 | 1395
1616.2 | 1395.2
1616.4 | 1395.4
1616.6 | 1395.6
1616.8 | 1395.8
1617 | 1396
1617.2 | 1396.2
1617.4 | 1396.4
1617.6 | 1396.6
1617.8 | 1396.8
1618 | 1397
1618.2 | 1397.2
1618.4 | 1397.4
1618.6 | 1397.6
1618.8 | 1397.8
1619 | 1398
1619.2 | 1398.2
1619.4 | 1398.4
1619.6 | 1398.6
1619.8 | 1398.8
1620 | 1399
1620.2 | 1399.2
1620.4 | 1399.4
1620.6 | 1399.6
1620.8 | 1399.8
1621 | 1400
1621.2 | 1400.2
1621.4 | 1400.4
1621.6 | 1400.6
1621.8 | 1400.8
1622 | 1401
1622.2 | 1401.2
1622.4 | 1401.4
1622.6 | 1401.6
1622.8 | 1401.8
1623 | 1402
1623.2 | 1402.2
1623.4 | 1402.4
1623.6 | 1402.6
1623.8 | 1402.8
1624 | 1403
1624.2 | 1403.2
1624.4 | 1403.4
1624.6 | 1403.6
1624.8 | 1403.8
1625 | 1404
1625.2 | 1404.2
1625.4 | 1404.4
1625.6 | 1404.6
1625.8 | 1404.8
1626 | 1405
1626.2 | 1405.2
1626.4 | 1405.4
1626.6 | 1405.6
1626.8 | 1405.8
1627 | 1406
1627.2 | 1406.2
1627.4 | 1406.4
1627.6 | 1406.6
1627.8 | 1406.8
1628 | 1407
1628.2 | 1407.2
1628.4 | 1407.4
1628.6 | 1407.6
1628.8 | 1407.8
1629 | 1408
1629.2 | 1408.2
1629.4 | 1408.4
1629.6 | 1408.6
1629.8 | 1408.8
1630 | 1409
1630.2 | 1409.2
1630.4 | 1409.4
1630.6 | 1409.6
1630.8 | 1409.8
1631 | 1410
1631.2 | 1410.2
1631.4 | 1410.4
1631.6 | 1410.6
1631.8 | 1410.8
1632 | 1411
1632.2 | 1411.2
1632.4 | 1411.4
1632.6 | 1411.6
1632.8 | 1411.8
1633 | 1412
1633.2 | 1412.2
1633.4 | 1412.4
1633.6 | 1412.6
1633.8 | 1412.8
1634 | 1413
1634.2 | 1413.2
1634.4 | 1413.4
1634.6 | 1413.6
1634.8 | 1413.8
1635 | 1414
1635.2 | 1414.2
1635.4 | 1414.4
1635.6 | 1414.6
1635.8 | 1414.8
1636 | 1415
1636.2 | 1415.2
1636.4 | 1415.4
1636.6 | 1415.6
1636.8 | 1415.8
1637 | 1416
1637.2 | 1416.2
1637.4 | 1416.4
1637.6 | 1416.6
1637.8 | 1416.8
1638 | 1417
1638.2 | 1417.2
1638.4 | 1417.4
1638.6 | 1417.6
1638.8 | 1417.8
1639 | 1418
1639.2 | 1418.2
1639.4 | 1418.4
1639.6 | 1418.6
1639.8 | 1418.8
1640 | 1419
1640.2 | 1419.2
1640.4 | 1419.4
1640.6 | 1419.6
1640.8 | 1419.8
1641 | 1420
1641.2 | 1420.2
1641.4 | 1420.4
1641.6 | 1420.6
1641.8 | 1420.8
1642 | 1421
1642.2 | 1421.2
1642.4 | 1421.4
1642.6 | 1421.6
1642.8 | 1421.8
1643 | 1422
1643.2 | 1422.2
1643.4 | 1422.4
1643.6 | 1422.6
1643.8 | 1422.8
1644 | 1423
1644.2 | 1423.2
1644.4 | 1423.4
1644.6 | 1423.6
1644.8 | 1423.8
1645 | 1424
1645.2 | 1424.2
1645.4 | 1424.4
1645.6 | 1424.6
1645.8 | 1424.8
1646 | 1425
1646.2 | 1425.2
1646.4 | 1425.4
1646.6 | 1425.6
1646.8 | 1425.8
1647 | 1426
1647.2 | 1426.2
1647.4 | 1426.4
1647.6 | 1426.6
1647.8 | 1426.8
1648 | 1427
1648.2 | 1427.2
1648.4 | 1427.4
1648.6 | 1427.6
1648.8 | 1427.8
1649 | 1428
1649.2 | 1428.2
1649.4 | 1428.4
1649.6 | 1428.6
1649.8 | 1428.8
1650 | 1429
1650.2 | 1429.2
1650.4 | 1429.4
1650.6 | 1429.6
1650.8 | 1429.8
1651 | 1430
1651.2 | 1430.2
1651.4 | 1430.4
1651.6 | 1430.6
1651.8 | 1430.8
1652 | 1431
1652.2 | 1431.2
1652.4 | 1431.4
1652.6 | 1431.6
1652.8 | 1431.8
1653 | 1432
1653.2 | 1432.2
1653.4 | 1432.4
1653.6 | 1432.6
1653.8 | 1432.8
1654 | 1433
1654.2 | 1433.2
1654.4 | 1433.4
1654.6 | 1433.6
1654.8 | 1433.8
1655 | 1434
1655.2 | 1434.2
1655.4 | 1434.4
1655.6 | 1434.6
1655.8 | 1434.8
1656 | 1435
1656.2 | 1435.2
1656.4 | 1435.4
1656.6 | 1435.6
1656.8 | 1435.8
1657 | 1436
1657.2 | 1436.2
1657.4 | 1436.4
1657.6 | 1436.6
1657.8 | 1436.8
1658 | 1437
1658.2 | 1437.2
1658.4 | 1437.4
1658.6 | 1437.6
1658.8 | 1437.8
1659 | 1438
1659.2 | 1438.2
1659.4 | 1438.4
1659.6 | 1438.6
1659.8 | 1438.8
1660 | 1439
1660.2 | 1439.2
1660.4 | 1439.4
1660.6 | 1439.6
1660.8 | 1439.8
1661 | 1440
1661.2 | 1440.2
1661.4 | 1440.4
1661.6 | 1440.6
1661.8 | 1440.8
1662 | 1441
1662.2 | 1441.2
1662.4 | 1441.4
1662.6 | 1441.6
1662.8 | 1441.8
1663 | 1442
1663.2 | 1442.2
1663.4 | 1442.4
1663.6 | 1442.6
1663.8 | 1442.8
1664 | 1443
1664.2 | 1443.2
1664.4 | 1443.4
1664.6 | 1443.6
1664.8 | 1443.8
1665 | 1444
1665.2 | 1444.2
1665.4 | 1444.4
1665.6 | 1444.6
1665.8 | 1444.8
1666 | 1445
1666.2 | 1445.2
1666.4 | 1445.4
1666.6 | 1445.6
1666.8 | 1445.8
1667 | 1446
1667.2 | 1446.2
1667.4 | 1446.4
1667.6 | 1446.6
1667.8 | 1446.8
1668 | 1447
1668.2 | 1447.2
1668.4 | 1447.4
1668.6 | 1447.6
1668.8 | 1447.8
1669 | 1448
1669.2 | 1448.2
1669.4 | 1448.4
1669.6 | 1448.6
1669.8 | 1448.8
1670 | 1449
1670.2 | 1449.2
1670.4 | 1449.4
1670.6 | 1449.6
1670.8 | 1449.8
1671 | 1450
1671.2 | 1450.2
1671.4 | 1450.4
1671.6 | 1450.6
1671.8 | 1450.8
1672 | 1451
1672.2 | 1451.2
1672.4 | 1451.4
1672.6 | 1451.6
1672.8 | 1451.8
1673 | 1452
1673.2 | 1452.2
1673.4 | 1452.4
1673.6 | 1452.6
1673.8 | 1452.8
1674 | 1453
1674.2 | 1453.2
1674.4 | 1453.4
1674.6 | 1453.6
1674.8 | 1453.8
1675 | 1454
1675.2 | 1454.2
1675.4 | 1454.4
1675.6 | 1454.6
1675.8 | 1454.8
1676 | 1455
1676.2 | 1455.2
1676.4 | 1455.4
1676.6 | 1455.6
1676.8 | 1455.8
1677 | 1456
1677.2 | 1456.2
1677.4 | 1456.4
1677.6 | 1456.6
1677.8 | 1456.8
1678 | 1457
1678.2 | 1457.2
1678.4 | 1457.4
1678.6 | 1457.6
1678.8 | 1457.8
1679 | 1458
1679.2 | 1458.2
1679.4 | 1458.4
1679.6 | 1458.6
1679.8 | 1458.8
1680 | 1459
1680.2 | 1459.2
1680.4 | 1459.4
1680.6 | 1459.6
1680.8 | 1459.8
1681 | 1460
1681.2 | 1460.2
1681.4 | 1460.4
1681.6 | 1460.6
1681.8 | 1460.8
1682 | 1461
1682.2 | 1461.2
1682.4 | 1461.4
1682.6 | 1461.6
1682.8 | 1461.8
1683 | 1462
1683.2 | 1462.2
1683.4 | 1462.4
1683.6 | 1462.6
1683.8 | 1462.8
1684 | 1463
1684.2 | 1463.2
1684.4 | 1463.4
1684.6 | 1463.6
1684.8 | 1463.8
1685 | 1464
1685.2 | 1464.2
1685.4 | 1464.4
1685.6 | 1464.6
1685.8 | 1464.8
1686 | 1465
1686.2 | 1465.2
1686.4 | 1465.4
1686.6 | 1465.6
1686.8 | 1465.8
1687 | 1466
1687.2 | 1466.2
1687.4 | 1466.4
1687.6 | 1466.6
1687.8 | 1466.8
1688 | 1467
1688.2 | 1467.2
1688.4 | 1467.4
1688.6 | 1467.6
1688.8 | 1467.8
1689 | 1468
1689.2 | 1468.2
1689.4 | 1468.4
1689.6 | 1468.6
1689.8 | 1468.8
1690 | 1469
1690.2 | 1469.2
1690.4 | 1469.4
1690.6 | 1469.6
1690.8 | 1469.8
1691 | 1470
1691.2 | 1470.2
1691.4 | 1470.4
1691.6 | 1470.6
1691.8 | 1470.8
1692 | 1471
1692.2 | 1471.2
1692.4 | 1471.4
1692.6 | 1471.6
1692.8 | 1471.8
1693 | 1472
1693.2 | 1472.2
1693.4 | 1472.4
1693.6 | 1472.6
1693.8 | 1472.8
1694 | 1473
1694.2 | 1473.2
1694.4 | 1473.4
1694.6 | 1473.6
1694.8 | 1473.8
1695 | 1474
1695.2 | 1474.2
1695.4 | 1474.4
1695.6 | 1474.6
1695.8 | 1474.8
1696 | 1475
1696.2 | 1475.2
1696.4 | 1475.4
1696.6 | 1475.6
1696.8 | 1475.8
1697 | 1476
1697.2 | 1476.2
1697.4 | 1476.4
1697.6 | 1476.6
1697.8 | 1476.8
1698 | 1477
1698.2 | 1477.2
1698.4 | 1477.4
1698.6 | 1477.6
1698.8 | 1477.8
1699 | 1478
1699.2 | 1478.2
1699.4 | 1478.4
1699.6 | 1478.6
1699.8 | 1478.8
1700 | 1479
1720 | 1499
1740 | 1519
1760 | 1539
1780 | 1559
1800 | 1579
1850 | 1629
1900 | 1679
1950 | 1729
2000 | 1779
2050 | 1829
2100 | 1879
2150 | 1929
2200 | 1979
2250 | 2029
2300 | 2079
2350 | 2129
2400 | 2179
2450 | 2229
2500 | 2279
2550 | 2329
2600 | 2379
2650 | 2429
2700 | 2479
2750 | 2529
2800 | 2579
2850 | 2629
2900 | 2679
2950 | 2729
3000 | 2779
3050 | 2829
3100 | 2879
3150 | 2929
3200 | 2979
3250 | 3029
3300 | 3079
3350 | 3129
3400 | 3179
3450 | 3229
3500 | 3279
3550 | 3329
3577 | 3356

## Circuit 3 Faulting
Summary of Observed Faulting Behavior for Circuit #3
DAQ Time | Burner Time | Event | Discussion
801 | 580 | Fuse Blow
Summary Observations |  | The circuit experience a fuse blow and no spurious operations.

## Converted Data C3
DAQ Time | Burner Time | C3 V1 | C3 A1 | C3 V2 | C3 A2 | C3 V4 | C3 A4 | C3 V5 | C3 A5 | C3 V6 | C3 A6
0 | -221 | 130.5244 | 0.083028 | 130.1296 | 0.0082241 | 0.29155 | 0.0013944 | 0.17302 | 0.0014885 | -0.010956 | 0.0009739
10 | -211 | 130.4284 | 0.083028 | 130.0336 | 0.0082241 | 0.1956 | 0.0013944 | 0.17302 | -0.00011067 | -0.010956 | -0.00062529
20 | -201 | 130.4284 | 0.083028 | 129.9376 | 0.0082241 | 0.1956 | -0.00020474 | 0.26897 | 0.0014885 | -0.010956 | 0.0009739
30 | -191 | 130.3325 | 0.083028 | 129.9376 | 0.0082241 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0009739
40 | -181 | 130.2365 | 0.084627 | 129.8417 | 0.0082241 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0009739
50 | -171 | 130.1405 | 0.084627 | 129.7457 | 0.0082241 | 0.1956 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0009739
60 | -161 | 130.1405 | 0.083028 | 129.7457 | 0.0082241 | 0.1956 | 0.0013944 | 0.26897 | -0.00011067 | 0.084995 | 0.0009739
70 | -151 | 129.7567 | 0.079829 | 129.4578 | 0.0066249 | 0.29155 | -0.00020474 | 0.26897 | -0.00011067 | -0.010956 | 0.0025737
80 | -141 | 129.7567 | 0.078229 | 129.3618 | 0.0018261 | 0.29155 | 0.0013944 | 0.26897 | -0.00011067 | 0.084995 | 0.0025737
90 | -131 | 129.6607 | 0.07503 | 129.2658 | 0.0018261 | 0.29155 | 0.0013944 | 0.26897 | -0.00011067 | 0.084995 | 0.0009739
100 | -121 | 129.7567 | 0.07503 | 129.2658 | 0.0018261 | 0.1956 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0009739
110 | -111 | 129.8526 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0009739
120 | -101 | 129.8526 | 0.073431 | 129.3618 | 0.0018261 | 0.29155 | 0.0013944 | 0.26897 | -0.00011067 | 0.084995 | 0.0025737
130 | -91 | 130.0446 | 0.071831 | 129.5538 | 0.0018261 | 0.29155 | 0.0013944 | 0.17302 | -0.00011067 | 0.084995 | 0.0009739
140 | -81 | 129.8526 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
150 | -71 | 129.6607 | 0.078229 | 129.2658 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
160 | -61 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
170 | -51 | 129.9486 | 0.084627 | 129.5538 | 0.0082241 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
180 | -41 | 130.1405 | 0.083028 | 129.5538 | 0.0082241 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
190 | -31 | 130.1405 | 0.084627 | 129.6497 | 0.0082241 | 0.29155 | -0.00020474 | 0.26897 | -0.00011067 | 0.084995 | 0.0025737
200 | -21 | 129.9486 | 0.084627 | 129.5538 | 0.0082241 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
210 | -11 | 129.9486 | 0.083028 | 129.4578 | 0.0082241 | 0.3875 | 0.0013944 | 0.26897 | -0.00011067 | 0.084995 | 0.0025737
220 | -1 | 129.8526 | 0.081428 | 129.3618 | 0.0082241 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
230 | 9 | 129.7567 | 0.081428 | 129.2658 | 0.0066249 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
240 | 19 | 129.5647 | 0.078229 | 129.0739 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
250 | 29 | 129.4687 | 0.07663 | 129.0739 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
260 | 39 | 129.7567 | 0.073431 | 129.3618 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
270 | 49 | 129.9486 | 0.071831 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | -0.00011067 | 0.084995 | 0.0025737
270.2 | 49.2 | 129.9486 | 0.071831 | 129.5538 | 0.0034259 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0009739
270.4 | 49.4 | 129.9486 | 0.071831 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
270.6 | 49.6 | 129.9486 | 0.071831 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
270.8 | 49.8 | 129.8526 | 0.071831 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
271 | 50 | 129.9486 | 0.071831 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
271.2 | 50.2 | 129.9486 | 0.071831 | 129.5538 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
271.4 | 50.4 | 129.9486 | 0.071831 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
271.6 | 50.6 | 129.9486 | 0.071831 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
271.8 | 50.8 | 129.9486 | 0.071831 | 129.5538 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
272 | 51 | 129.8526 | 0.071831 | 129.3618 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
272.2 | 51.2 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
272.4 | 51.4 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
272.6 | 51.6 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
272.8 | 51.8 | 129.9486 | 0.073431 | 129.5538 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
273 | 52 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
273.2 | 52.2 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
273.4 | 52.4 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
273.6 | 52.6 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
273.8 | 52.8 | 129.8526 | 0.071831 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
274 | 53 | 129.8526 | 0.073431 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
274.2 | 53.2 | 129.9486 | 0.07503 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.18099 | 0.0025737
274.4 | 53.4 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
274.6 | 53.6 | 129.8526 | 0.07503 | 129.4578 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
274.8 | 53.8 | 129.8526 | 0.073431 | 129.3618 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
275 | 54 | 129.8526 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
275.2 | 54.2 | 129.8526 | 0.07503 | 129.3618 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
275.4 | 54.4 | 129.8526 | 0.07503 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
275.6 | 54.6 | 129.8526 | 0.073431 | 129.3618 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
275.8 | 54.8 | 129.7567 | 0.073431 | 129.3618 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
276 | 55 | 129.7567 | 0.073431 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
276.2 | 55.2 | 129.7567 | 0.073431 | 129.3618 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
276.4 | 55.4 | 129.8526 | 0.07503 | 129.3618 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
276.6 | 55.6 | 129.8526 | 0.07503 | 129.3618 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
276.8 | 55.8 | 129.8526 | 0.07503 | 129.3618 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
277 | 56 | 129.8526 | 0.073431 | 129.3618 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
277.2 | 56.2 | 129.7567 | 0.07503 | 129.2658 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.084995 | 0.0025737
277.4 | 56.4 | 129.7567 | 0.07503 | 129.2658 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
277.6 | 56.6 | 129.7567 | 0.07503 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
277.8 | 56.8 | 129.7567 | 0.07503 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
278 | 57 | 129.6607 | 0.07503 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
278.2 | 57.2 | 129.7567 | 0.07503 | 129.2658 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
278.4 | 57.4 | 129.7567 | 0.07503 | 129.3618 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
278.6 | 57.6 | 129.7567 | 0.07503 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
278.8 | 57.8 | 129.7567 | 0.07503 | 129.3618 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
279 | 58 | 129.7567 | 0.07503 | 129.1699 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
279.2 | 58.2 | 129.6607 | 0.07503 | 129.1699 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
279.4 | 58.4 | 129.6607 | 0.07503 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
279.6 | 58.6 | 129.6607 | 0.07503 | 129.1699 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
279.8 | 58.8 | 129.6607 | 0.07663 | 129.1699 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
280 | 59 | 129.5647 | 0.07663 | 129.1699 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
280.2 | 59.2 | 129.5647 | 0.07663 | 129.1699 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
280.4 | 59.4 | 129.5647 | 0.07663 | 129.0739 | 0.0034259 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.18099 | 0.0041729
280.6 | 59.6 | 129.6607 | 0.07663 | 129.0739 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
280.8 | 59.8 | 129.6607 | 0.07663 | 129.0739 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
281 | 60 | 129.5647 | 0.07663 | 129.0739 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
281.2 | 60.2 | 129.6607 | 0.07663 | 129.1699 | 0.0034259 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
281.4 | 60.4 | 129.5647 | 0.07663 | 129.1699 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
281.6 | 60.6 | 129.5647 | 0.07663 | 129.0739 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
281.8 | 60.8 | 129.5647 | 0.07663 | 129.0739 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
282 | 61 | 129.4687 | 0.078229 | 128.978 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
282.2 | 61.2 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0025737
282.4 | 61.4 | 129.5647 | 0.078229 | 129.0739 | 0.0034259 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
282.6 | 61.6 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
282.8 | 61.8 | 129.5647 | 0.078229 | 129.0739 | 0.0034259 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
283 | 62 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
283.2 | 62.2 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
283.4 | 62.4 | 129.5647 | 0.078229 | 128.978 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
283.6 | 62.6 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
283.8 | 62.8 | 129.4687 | 0.079829 | 129.0739 | 0.0034259 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
284 | 63 | 129.5647 | 0.078229 | 128.978 | 0.0050251 | 0.3875 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0041729
284.2 | 63.2 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
284.4 | 63.4 | 129.5647 | 0.078229 | 129.0739 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
284.6 | 63.6 | 129.4687 | 0.078229 | 129.0739 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
284.8 | 63.8 | 129.4687 | 0.078229 | 129.0739 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
285 | 64 | 129.5647 | 0.079829 | 129.0739 | 0.0034259 | 0.3875 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0041729
285.2 | 64.2 | 129.5647 | 0.079829 | 129.0739 | 0.0050251 | 0.3875 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
285.4 | 64.4 | 129.5647 | 0.079829 | 129.0739 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
285.6 | 64.6 | 129.5647 | 0.079829 | 128.978 | 0.0050251 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0041729
285.8 | 64.8 | 129.5647 | 0.079829 | 128.978 | 0.0050251 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.18099 | 0.0025737
286 | 65 | 129.5647 | 0.079829 | 128.978 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
286.2 | 65.2 | 126.014 | 0.078229 | 125.4272 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
286.4 | 65.4 | 129.3728 | 0.079829 | 128.882 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0025737
286.6 | 65.6 | 129.5647 | 0.079829 | 129.0739 | 0.0066249 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
286.8 | 65.8 | 129.6607 | 0.079829 | 129.0739 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
287 | 66 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
287.2 | 66.2 | 129.5647 | 0.079829 | 129.0739 | 0.0050251 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
287.4 | 66.4 | 129.5647 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0030884 | 0.084995 | 0.0025737
287.6 | 66.6 | 129.5647 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
287.8 | 66.8 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
288 | 67 | 129.6607 | 0.079829 | 129.0739 | 0.0066249 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.18099 | 0.0025737
288.2 | 67.2 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
288.4 | 67.4 | 129.6607 | 0.079829 | 129.2658 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
288.6 | 67.6 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
288.8 | 67.8 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
289 | 68 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
289.2 | 68.2 | 129.7567 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | -0.00011067 | 0.18099 | 0.0025737
289.4 | 68.4 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
289.6 | 68.6 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.3875 | 0.0013944 | 0.26897 | 0.0014885 | 0.084995 | 0.0025737
289.8 | 68.8 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.18099 | 0.0041729
290 | 69 | 129.6607 | 0.079829 | 129.1699 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
300 | 79 | 129.8526 | 0.083028 | 129.3618 | 0.0082241 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
310 | 89 | 130.0446 | 0.084627 | 129.6497 | 0.0098233 | 0.29155 | 0.0013944 | 0.26897 | 0.0014885 | 0.18099 | 0.0041729
320 | 99 | 129.9486 | 0.084627 | 129.5538 | 0.0098233 | 0.3875 | 0.0013944 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
330 | 109 | 129.7567 | 0.081428 | 129.3618 | 0.0082241 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
340 | 119 | 129.7567 | 0.078229 | 129.2658 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
350 | 129 | 129.7567 | 0.078229 | 129.2658 | 0.0034259 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.084995 | 0.0041729
360 | 139 | 129.8526 | 0.081428 | 129.3618 | 0.0066249 | 0.29155 | 0.0013944 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
370 | 149 | 129.9486 | 0.081428 | 129.4578 | 0.0082241 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
380 | 159 | 129.8526 | 0.083028 | 129.4578 | 0.0082241 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
390 | 169 | 129.7567 | 0.081428 | 129.2658 | 0.0082241 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.18099 | 0.0041729
400 | 179 | 129.8526 | 0.081428 | 129.3618 | 0.0066249 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0025737
410 | 189 | 129.8526 | 0.079829 | 129.4578 | 0.0066249 | 0.29155 | 0.0029943 | 0.26897 | 0.0014885 | 0.18099 | 0.0025737
420 | 199 | 129.7567 | 0.081428 | 129.3618 | 0.0066249 | 0.3875 | 0.0013944 | 0.36492 | 0.0030884 | 0.084995 | 0.0025737
430 | 209 | 129.8526 | 0.079829 | 129.2658 | 0.0066249 | 0.29155 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0025737
440 | 219 | 129.7567 | 0.078229 | 129.2658 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0025737
450 | 229 | 129.7567 | 0.07663 | 129.1699 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0025737
460 | 239 | 129.7567 | 0.07503 | 129.3618 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
470 | 249 | 129.8526 | 0.07503 | 129.3618 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
480 | 259 | 129.8526 | 0.073431 | 129.3618 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0041729
490 | 269 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0025737
500 | 279 | 129.9486 | 0.073431 | 129.4578 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.084995 | 0.0041729
510 | 289 | 130.2365 | 0.07503 | 129.7457 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0057728
520 | 299 | 130.0446 | 0.073431 | 129.6497 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
530 | 309 | 130.1405 | 0.073431 | 129.6497 | 0.0050251 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
540 | 319 | 129.9486 | 0.07503 | 129.4578 | 0.0034259 | 0.29155 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
550 | 329 | 129.8526 | 0.07503 | 129.3618 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
560 | 339 | 129.8526 | 0.079829 | 129.4578 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
570 | 349 | 130.0446 | 0.07503 | 129.5538 | 0.0050251 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
580 | 359 | 130.1405 | 0.071831 | 129.6497 | 0.0050251 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
590 | 369 | 130.2365 | 0.073431 | 129.7457 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
600 | 379 | 130.2365 | 0.073431 | 129.7457 | 0.0050251 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
610 | 389 | 130.2365 | 0.073431 | 129.7457 | 0.0050251 | 0.29155 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
620 | 399 | 130.2365 | 0.073431 | 129.7457 | 0.0050251 | 0.29155 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
630 | 409 | 130.1405 | 0.073431 | 129.6497 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0057728
640 | 419 | 129.9486 | 0.07503 | 129.4578 | 0.0050251 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
650 | 429 | 130.0446 | 0.073431 | 129.5538 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
660 | 439 | 130.0446 | 0.071831 | 129.5538 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
670 | 449 | 130.0446 | 0.073431 | 129.6497 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0057728
680 | 459 | 130.0446 | 0.073431 | 129.6497 | 0.0066249 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0025737
690 | 469 | 129.8526 | 0.07503 | 129.3618 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
700 | 479 | 129.8526 | 0.078229 | 129.3618 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
710 | 489 | 129.9486 | 0.07503 | 129.4578 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0014885 | 0.18099 | 0.0057728
720 | 499 | 130.0446 | 0.07503 | 129.6497 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0057728
730 | 509 | 129.7567 | 0.079829 | 129.2658 | 0.0082241 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
740 | 519 | 129.9486 | 0.084627 | 129.4578 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0057728
750 | 529 | 130.2365 | 0.084627 | 129.7457 | 0.0098233 | 0.48349 | 0.0045935 | 0.46091 | 0.0046875 | 0.27694 | 0.0057728
760 | 539 | 130.2365 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
770 | 549 | 130.0446 | 0.083028 | 129.5538 | 0.0082241 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
780 | 559 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.48349 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
790 | 569 | 130.1405 | 0.083028 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0057728
790.2 | 569.2 | 130.2365 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
790.4 | 569.4 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
790.6 | 569.6 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
790.8 | 569.8 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
791 | 570 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
791.2 | 570.2 | 130.1405 | 0.083028 | 129.7457 | 0.0098233 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
791.4 | 570.4 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
791.6 | 570.6 | 130.2365 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
791.8 | 570.8 | 130.2365 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
792 | 571 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
792.2 | 571.2 | 130.1405 | 0.083028 | 129.6497 | 0.0082241 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
792.4 | 571.4 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0057728
792.6 | 571.6 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
792.8 | 571.8 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
793 | 572 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
793.2 | 572.2 | 130.1405 | 0.083028 | 129.7457 | 0.0098233 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.18099 | 0.0057728
793.4 | 572.4 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
793.6 | 572.6 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
793.8 | 572.8 | 130.2365 | 0.084627 | 129.6497 | 0.011423 | 0.48349 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0057728
794 | 573 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
794.2 | 573.2 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
794.4 | 573.4 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
794.6 | 573.6 | 130.1405 | 0.083028 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
794.8 | 573.8 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
795 | 574 | 130.2365 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
795.2 | 574.2 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
795.4 | 574.4 | 130.2365 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.27694 | 0.0041729
795.6 | 574.6 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
795.8 | 574.8 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
796 | 575 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
796.2 | 575.2 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0057728
796.4 | 575.4 | 130.2365 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
796.6 | 575.6 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
796.8 | 575.8 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.46091 | 0.0046875 | 0.27694 | 0.0041729
797 | 576 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.48349 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
797.2 | 576.2 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
797.4 | 576.4 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
797.6 | 576.6 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
797.8 | 576.8 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
798 | 577 | 130.0446 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
798.2 | 577.2 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
798.4 | 577.4 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
798.6 | 577.6 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0057728
798.8 | 577.8 | 130.1405 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
799 | 578 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
799.2 | 578.2 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
799.4 | 578.4 | 130.2365 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0029943 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
799.6 | 578.6 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
799.8 | 578.8 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
800 | 579 | 130.0446 | 0.084627 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
800.2 | 579.2 | 130.2365 | 0.083028 | 129.6497 | 0.0098233 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
800.4 | 579.4 | 130.1405 | 0.084627 | 129.7457 | 0.0098233 | 0.3875 | 0.0029943 | 0.36492 | 0.0046875 | 0.27694 | 0.0041729
800.6 | 579.6 | 130.1405 | 0.084627 | 129.7457 | 0.011423 | 0.29155 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
800.8 | 579.8 | 130.1405 | 0.084627 | 129.6497 | 0.0098233 | 0.48349 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
801 | 580 | 84.3641 | 0.063834 | 82.6258 | 4.9969 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
801.2 | 580.2 | 9.6057 | 0.022249 | 8.6351 | 0.39209 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
801.4 | 580.4 | 2.6001 | 0.012652 | 2.2053 | 0.04821 | 0.3875 | 0.0029943 | 0.36492 | 0.0046875 | 0.27694 | 0.0057728
801.6 | 580.6 | 1.3525 | 0.0094526 | 1.2456 | 0.017821 | 0.3875 | 0.0029943 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
801.8 | 580.8 | 1.0646 | 0.0078534 | 0.95767 | 0.011423 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
802 | 581 | 0.96863 | 0.0078534 | 0.76573 | 0.0098233 | 0.29155 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0057728
802.2 | 581.2 | 0.87268 | 0.0062542 | 0.76573 | 0.0082241 | 0.3875 | 0.0045935 | 0.46091 | 0.0046875 | 0.27694 | 0.0041729
802.4 | 581.4 | 0.77673 | 0.0062542 | 0.66978 | 0.0066249 | 0.3875 | 0.0029943 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
802.6 | 581.6 | 0.77673 | 0.0062542 | 0.66978 | 0.0066249 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0057728
802.8 | 581.8 | 0.77673 | 0.0062542 | 0.57383 | 0.0066249 | 0.48349 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
803 | 582 | 0.68074 | 0.0062542 | 0.57383 | 0.0066249 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
803.2 | 582.2 | 0.68074 | 0.0062542 | 0.47784 | 0.0066249 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
803.4 | 582.4 | 0.68074 | 0.0062542 | 0.47784 | 0.0066249 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
803.6 | 582.6 | 0.58479 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
803.8 | 582.8 | 0.68074 | 0.0046543 | 0.47784 | 0.0066249 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
804 | 583 | 0.58479 | 0.0046543 | 0.47784 | 0.0066249 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0057728
804.2 | 583.2 | 0.58479 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0046875 | 0.27694 | 0.0041729
804.4 | 583.4 | 0.58479 | 0.0062542 | 0.57383 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.18099 | 0.0041729
804.6 | 583.6 | 0.58479 | 0.0062542 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
804.8 | 583.8 | 0.58479 | 0.0062542 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0046875 | 0.27694 | 0.0041729
805 | 584 | 0.58479 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
805.2 | 584.2 | 0.58479 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0041729
805.4 | 584.4 | 0.58479 | 0.0062542 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
805.6 | 584.6 | 0.58479 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.18099 | 0.0057728
805.8 | 584.8 | 0.58479 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
806 | 585 | 0.4888 | 0.0046543 | 0.47784 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
806.2 | 585.2 | 0.58479 | 0.0046543 | 0.47784 | 0.0034259 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
806.4 | 585.4 | 0.58479 | 0.0046543 | 0.38189 | 0.0034259 | 0.3875 | 0.0029943 | 0.36492 | 0.0030884 | 0.18099 | 0.0041729
806.6 | 585.6 | 0.58479 | 0.0046543 | 0.38189 | 0.0050251 | 0.3875 | 0.0029943 | 0.36492 | 0.0046875 | 0.18099 | 0.0041729
806.8 | 585.8 | 0.4888 | 0.0046543 | 0.38189 | 0.0050251 | 0.3875 | 0.0045935 | 0.36492 | 0.0030884 | 0.27694 | 0.0041729
807 | 586 | 0.58479 | 0.0046543 | 0.47784 | 0.0034259 | 0.3875 | 0.0045935 | 0.46091 | 0.0030884 | 0.27694 | 0.0057728
808 | 587
810 | 589
820 | 599
830 | 609
840 | 619
850 | 629
860 | 639
870 | 649
880 | 659
890 | 669
900 | 679
910 | 689
920 | 699
930 | 709
940 | 719
950 | 729
960 | 739
970 | 749
980 | 759
990 | 769
1000 | 779
1010 | 789
1020 | 799
1030 | 809
1040 | 819
1050 | 829
1060 | 839
1070 | 849
1080 | 859
1090 | 869
1100 | 879
1110 | 889
1120 | 899
1130 | 909
1140 | 919
1150 | 929
1160 | 939
1170 | 949
1180 | 959
1190 | 969
1200 | 979
1210 | 989
1220 | 999
1230 | 1009
1240 | 1019
1240.2 | 1019.2
1250 | 1029
1260 | 1039
1270 | 1049
1280 | 1059
1290 | 1069
1300 | 1079
1310 | 1089
1320 | 1099
1330 | 1109
1340 | 1119
1350 | 1129
1360 | 1139
1370 | 1149
1380 | 1159
1390 | 1169
1400 | 1179
1410 | 1189
1420 | 1199
1430 | 1209
1440 | 1219
1450 | 1229
1450.2 | 1229.2
1450.4 | 1229.4
1450.6 | 1229.6
1450.8 | 1229.8
1451 | 1230
1451.2 | 1230.2
1451.4 | 1230.4
1451.6 | 1230.6
1451.8 | 1230.8
1452 | 1231
1452.2 | 1231.2
1452.4 | 1231.4
1452.6 | 1231.6
1452.8 | 1231.8
1453 | 1232
1453.2 | 1232.2
1453.4 | 1232.4
1453.6 | 1232.6
1453.8 | 1232.8
1454 | 1233
1454.2 | 1233.2
1454.4 | 1233.4
1454.6 | 1233.6
1454.8 | 1233.8
1455 | 1234
1455.2 | 1234.2
1455.4 | 1234.4
1455.6 | 1234.6
1455.8 | 1234.8
1456 | 1235
1456.2 | 1235.2
1456.4 | 1235.4
1456.6 | 1235.6
1456.8 | 1235.8
1457 | 1236
1457.2 | 1236.2
1457.4 | 1236.4
1457.6 | 1236.6
1457.8 | 1236.8
1458 | 1237
1458.2 | 1237.2
1458.4 | 1237.4
1458.6 | 1237.6
1458.8 | 1237.8
1459 | 1238
1459.2 | 1238.2
1459.4 | 1238.4
1459.6 | 1238.6
1459.8 | 1238.8
1460 | 1239
1460.2 | 1239.2
1460.4 | 1239.4
1460.6 | 1239.6
1460.8 | 1239.8
1461 | 1240
1461.2 | 1240.2
1461.4 | 1240.4
1461.6 | 1240.6
1461.8 | 1240.8
1462 | 1241
1462.2 | 1241.2
1462.4 | 1241.4
1462.6 | 1241.6
1462.8 | 1241.8
1463 | 1242
1463.2 | 1242.2
1463.4 | 1242.4
1463.6 | 1242.6
1463.8 | 1242.8
1464 | 1243
1464.2 | 1243.2
1464.4 | 1243.4
1464.6 | 1243.6
1464.8 | 1243.8
1465 | 1244
1465.2 | 1244.2
1465.4 | 1244.4
1465.6 | 1244.6
1465.8 | 1244.8
1466 | 1245
1466.2 | 1245.2
1466.4 | 1245.4
1466.6 | 1245.6
1466.8 | 1245.8
1467 | 1246
1467.2 | 1246.2
1467.4 | 1246.4
1467.6 | 1246.6
1467.8 | 1246.8
1468 | 1247
1468.2 | 1247.2
1468.4 | 1247.4
1468.6 | 1247.6
1468.8 | 1247.8
1469 | 1248
1469.2 | 1248.2
1469.4 | 1248.4
1469.6 | 1248.6
1469.8 | 1248.8
1470 | 1249
1470.2 | 1249.2
1470.4 | 1249.4
1470.6 | 1249.6
1470.8 | 1249.8
1471 | 1250
1471.2 | 1250.2
1471.4 | 1250.4
1471.6 | 1250.6
1471.8 | 1250.8
1472 | 1251
1472.2 | 1251.2
1472.4 | 1251.4
1472.6 | 1251.6
1472.8 | 1251.8
1473 | 1252
1473.2 | 1252.2
1473.4 | 1252.4
1473.6 | 1252.6
1473.8 | 1252.8
1474 | 1253
1474.2 | 1253.2
1474.4 | 1253.4
1474.6 | 1253.6
1474.8 | 1253.8
1475 | 1254
1475.2 | 1254.2
1475.4 | 1254.4
1475.6 | 1254.6
1475.8 | 1254.8
1476 | 1255
1476.2 | 1255.2
1476.4 | 1255.4
1476.6 | 1255.6
1476.8 | 1255.8
1477 | 1256
1477.2 | 1256.2
1477.4 | 1256.4
1477.6 | 1256.6
1477.8 | 1256.8
1478 | 1257
1478.2 | 1257.2
1478.4 | 1257.4
1478.6 | 1257.6
1478.8 | 1257.8
1479 | 1258
1479.2 | 1258.2
1479.4 | 1258.4
1479.6 | 1258.6
1479.8 | 1258.8
1480 | 1259
1480.2 | 1259.2
1480.4 | 1259.4
1480.6 | 1259.6
1480.8 | 1259.8
1481 | 1260
1481.2 | 1260.2
1481.4 | 1260.4
1481.6 | 1260.6
1481.8 | 1260.8
1482 | 1261
1482.2 | 1261.2
1482.4 | 1261.4
1482.6 | 1261.6
1482.8 | 1261.8
1483 | 1262
1483.2 | 1262.2
1483.4 | 1262.4
1483.6 | 1262.6
1483.8 | 1262.8
1484 | 1263
1484.2 | 1263.2
1484.4 | 1263.4
1484.6 | 1263.6
1484.8 | 1263.8
1485 | 1264
1485.2 | 1264.2
1485.4 | 1264.4
1485.6 | 1264.6
1485.8 | 1264.8
1486 | 1265
1486.2 | 1265.2
1486.4 | 1265.4
1486.6 | 1265.6
1486.8 | 1265.8
1487 | 1266
1487.2 | 1266.2
1487.4 | 1266.4
1487.6 | 1266.6
1487.8 | 1266.8
1488 | 1267
1488.2 | 1267.2
1488.4 | 1267.4
1488.6 | 1267.6
1488.8 | 1267.8
1489 | 1268
1489.2 | 1268.2
1489.4 | 1268.4
1489.6 | 1268.6
1489.8 | 1268.8
1490 | 1269
1490.2 | 1269.2
1490.4 | 1269.4
1490.6 | 1269.6
1490.8 | 1269.8
1491 | 1270
1491.2 | 1270.2
1491.4 | 1270.4
1491.6 | 1270.6
1491.8 | 1270.8
1492 | 1271
1492.2 | 1271.2
1492.4 | 1271.4
1492.6 | 1271.6
1492.8 | 1271.8
1493 | 1272
1493.2 | 1272.2
1493.4 | 1272.4
1493.6 | 1272.6
1493.8 | 1272.8
1494 | 1273
1494.2 | 1273.2
1494.4 | 1273.4
1494.6 | 1273.6
1494.8 | 1273.8
1495 | 1274
1495.2 | 1274.2
1495.4 | 1274.4
1495.6 | 1274.6
1495.8 | 1274.8
1496 | 1275
1496.2 | 1275.2
1496.4 | 1275.4
1496.6 | 1275.6
1496.8 | 1275.8
1497 | 1276
1497.2 | 1276.2
1497.4 | 1276.4
1497.6 | 1276.6
1497.8 | 1276.8
1498 | 1277
1498.2 | 1277.2
1498.4 | 1277.4
1498.6 | 1277.6
1498.8 | 1277.8
1499 | 1278
1499.2 | 1278.2
1499.4 | 1278.4
1499.6 | 1278.6
1499.8 | 1278.8
1500 | 1279
1500.2 | 1279.2
1500.4 | 1279.4
1500.6 | 1279.6
1500.8 | 1279.8
1501 | 1280
1501.2 | 1280.2
1501.4 | 1280.4
1501.6 | 1280.6
1501.8 | 1280.8
1502 | 1281
1502.2 | 1281.2
1502.4 | 1281.4
1502.6 | 1281.6
1502.8 | 1281.8
1503 | 1282
1503.2 | 1282.2
1503.4 | 1282.4
1503.6 | 1282.6
1503.8 | 1282.8
1504 | 1283
1504.2 | 1283.2
1504.4 | 1283.4
1504.6 | 1283.6
1504.8 | 1283.8
1505 | 1284
1505.2 | 1284.2
1505.4 | 1284.4
1505.6 | 1284.6
1505.8 | 1284.8
1506 | 1285
1506.2 | 1285.2
1506.4 | 1285.4
1506.6 | 1285.6
1506.8 | 1285.8
1507 | 1286
1507.2 | 1286.2
1507.4 | 1286.4
1507.6 | 1286.6
1507.8 | 1286.8
1508 | 1287
1508.2 | 1287.2
1508.4 | 1287.4
1508.6 | 1287.6
1508.8 | 1287.8
1509 | 1288
1509.2 | 1288.2
1509.4 | 1288.4
1509.6 | 1288.6
1509.8 | 1288.8
1510 | 1289
1510.2 | 1289.2
1510.4 | 1289.4
1510.6 | 1289.6
1510.8 | 1289.8
1511 | 1290
1511.2 | 1290.2
1511.4 | 1290.4
1511.6 | 1290.6
1511.8 | 1290.8
1512 | 1291
1512.2 | 1291.2
1512.4 | 1291.4
1512.6 | 1291.6
1512.8 | 1291.8
1513 | 1292
1513.2 | 1292.2
1513.4 | 1292.4
1513.6 | 1292.6
1513.8 | 1292.8
1514 | 1293
1514.2 | 1293.2
1514.4 | 1293.4
1514.6 | 1293.6
1514.8 | 1293.8
1515 | 1294
1515.2 | 1294.2
1515.4 | 1294.4
1515.6 | 1294.6
1515.8 | 1294.8
1516 | 1295
1516.2 | 1295.2
1516.4 | 1295.4
1516.6 | 1295.6
1516.8 | 1295.8
1517 | 1296
1517.2 | 1296.2
1517.4 | 1296.4
1517.6 | 1296.6
1517.8 | 1296.8
1518 | 1297
1518.2 | 1297.2
1518.4 | 1297.4
1518.6 | 1297.6
1518.8 | 1297.8
1519 | 1298
1519.2 | 1298.2
1519.4 | 1298.4
1519.6 | 1298.6
1519.8 | 1298.8
1520 | 1299
1520.2 | 1299.2
1520.4 | 1299.4
1520.6 | 1299.6
1520.8 | 1299.8
1521 | 1300
1521.2 | 1300.2
1521.4 | 1300.4
1521.6 | 1300.6
1521.8 | 1300.8
1522 | 1301
1522.2 | 1301.2
1522.4 | 1301.4
1522.6 | 1301.6
1522.8 | 1301.8
1523 | 1302
1523.2 | 1302.2
1523.4 | 1302.4
1523.6 | 1302.6
1523.8 | 1302.8
1524 | 1303
1524.2 | 1303.2
1524.4 | 1303.4
1524.6 | 1303.6
1524.8 | 1303.8
1525 | 1304
1525.2 | 1304.2
1525.4 | 1304.4
1525.6 | 1304.6
1525.8 | 1304.8
1526 | 1305
1526.2 | 1305.2
1526.4 | 1305.4
1526.6 | 1305.6
1526.8 | 1305.8
1527 | 1306
1527.2 | 1306.2
1527.4 | 1306.4
1527.6 | 1306.6
1527.8 | 1306.8
1528 | 1307
1528.2 | 1307.2
1528.4 | 1307.4
1528.6 | 1307.6
1528.8 | 1307.8
1529 | 1308
1529.2 | 1308.2
1529.4 | 1308.4
1529.6 | 1308.6
1529.8 | 1308.8
1530 | 1309
1530.2 | 1309.2
1530.4 | 1309.4
1530.6 | 1309.6
1530.8 | 1309.8
1531 | 1310
1531.2 | 1310.2
1531.4 | 1310.4
1531.6 | 1310.6
1531.8 | 1310.8
1532 | 1311
1532.2 | 1311.2
1532.4 | 1311.4
1532.6 | 1311.6
1532.8 | 1311.8
1533 | 1312
1533.2 | 1312.2
1533.4 | 1312.4
1533.6 | 1312.6
1533.8 | 1312.8
1534 | 1313
1534.2 | 1313.2
1534.4 | 1313.4
1534.6 | 1313.6
1534.8 | 1313.8
1535 | 1314
1535.2 | 1314.2
1535.4 | 1314.4
1535.6 | 1314.6
1535.8 | 1314.8
1536 | 1315
1536.2 | 1315.2
1536.4 | 1315.4
1536.6 | 1315.6
1536.8 | 1315.8
1537 | 1316
1537.2 | 1316.2
1537.4 | 1316.4
1537.6 | 1316.6
1537.8 | 1316.8
1538 | 1317
1538.2 | 1317.2
1538.4 | 1317.4
1538.6 | 1317.6
1538.8 | 1317.8
1539 | 1318
1539.2 | 1318.2
1539.4 | 1318.4
1539.6 | 1318.6
1539.8 | 1318.8
1540 | 1319
1540.2 | 1319.2
1540.4 | 1319.4
1540.6 | 1319.6
1540.8 | 1319.8
1541 | 1320
1541.2 | 1320.2
1541.4 | 1320.4
1541.6 | 1320.6
1541.8 | 1320.8
1542 | 1321
1542.2 | 1321.2
1542.4 | 1321.4
1542.6 | 1321.6
1542.8 | 1321.8
1543 | 1322
1543.2 | 1322.2
1543.4 | 1322.4
1543.6 | 1322.6
1543.8 | 1322.8
1544 | 1323
1544.2 | 1323.2
1544.4 | 1323.4
1544.6 | 1323.6
1544.8 | 1323.8
1545 | 1324
1545.2 | 1324.2
1545.4 | 1324.4
1545.6 | 1324.6
1545.8 | 1324.8
1546 | 1325
1546.2 | 1325.2
1546.4 | 1325.4
1546.6 | 1325.6
1546.8 | 1325.8
1547 | 1326
1547.2 | 1326.2
1547.4 | 1326.4
1547.6 | 1326.6
1547.8 | 1326.8
1548 | 1327
1548.2 | 1327.2
1548.4 | 1327.4
1548.6 | 1327.6
1548.8 | 1327.8
1549 | 1328
1549.2 | 1328.2
1549.4 | 1328.4
1549.6 | 1328.6
1549.8 | 1328.8
1550 | 1329
1550.2 | 1329.2
1550.4 | 1329.4
1550.6 | 1329.6
1550.8 | 1329.8
1551 | 1330
1551.2 | 1330.2
1551.4 | 1330.4
1551.6 | 1330.6
1551.8 | 1330.8
1552 | 1331
1552.2 | 1331.2
1552.4 | 1331.4
1552.6 | 1331.6
1552.8 | 1331.8
1553 | 1332
1553.2 | 1332.2
1553.4 | 1332.4
1553.6 | 1332.6
1553.8 | 1332.8
1554 | 1333
1554.2 | 1333.2
1554.4 | 1333.4
1554.6 | 1333.6
1554.8 | 1333.8
1555 | 1334
1555.2 | 1334.2
1555.4 | 1334.4
1555.6 | 1334.6
1555.8 | 1334.8
1556 | 1335
1556.2 | 1335.2
1556.4 | 1335.4
1556.6 | 1335.6
1556.8 | 1335.8
1557 | 1336
1557.2 | 1336.2
1557.4 | 1336.4
1557.6 | 1336.6
1557.8 | 1336.8
1558 | 1337
1558.2 | 1337.2
1558.4 | 1337.4
1558.6 | 1337.6
1558.8 | 1337.8
1559 | 1338
1559.2 | 1338.2
1559.4 | 1338.4
1559.6 | 1338.6
1559.8 | 1338.8
1560 | 1339
1560.2 | 1339.2
1560.4 | 1339.4
1560.6 | 1339.6
1560.8 | 1339.8
1561 | 1340
1561.2 | 1340.2
1561.4 | 1340.4
1561.6 | 1340.6
1561.8 | 1340.8
1562 | 1341
1562.2 | 1341.2
1562.4 | 1341.4
1562.6 | 1341.6
1562.8 | 1341.8
1563 | 1342
1563.2 | 1342.2
1563.4 | 1342.4
1563.6 | 1342.6
1563.8 | 1342.8
1564 | 1343
1564.2 | 1343.2
1564.4 | 1343.4
1564.6 | 1343.6
1564.8 | 1343.8
1565 | 1344
1565.2 | 1344.2
1565.4 | 1344.4
1565.6 | 1344.6
1565.8 | 1344.8
1566 | 1345
1566.2 | 1345.2
1566.4 | 1345.4
1566.6 | 1345.6
1566.8 | 1345.8
1567 | 1346
1567.2 | 1346.2
1567.4 | 1346.4
1567.6 | 1346.6
1567.8 | 1346.8
1568 | 1347
1568.2 | 1347.2
1568.4 | 1347.4
1568.6 | 1347.6
1568.8 | 1347.8
1569 | 1348
1569.2 | 1348.2
1569.4 | 1348.4
1569.6 | 1348.6
1569.8 | 1348.8
1570 | 1349
1570.2 | 1349.2
1570.4 | 1349.4
1570.6 | 1349.6
1570.8 | 1349.8
1571 | 1350
1571.2 | 1350.2
1571.4 | 1350.4
1571.6 | 1350.6
1571.8 | 1350.8
1572 | 1351
1572.2 | 1351.2
1572.4 | 1351.4
1572.6 | 1351.6
1572.8 | 1351.8
1573 | 1352
1573.2 | 1352.2
1573.4 | 1352.4
1573.6 | 1352.6
1573.8 | 1352.8
1574 | 1353
1574.2 | 1353.2
1574.4 | 1353.4
1574.6 | 1353.6
1574.8 | 1353.8
1575 | 1354
1575.2 | 1354.2
1575.4 | 1354.4
1575.6 | 1354.6
1575.8 | 1354.8
1576 | 1355
1576.2 | 1355.2
1576.4 | 1355.4
1576.6 | 1355.6
1576.8 | 1355.8
1577 | 1356
1577.2 | 1356.2
1577.4 | 1356.4
1577.6 | 1356.6
1577.8 | 1356.8
1578 | 1357
1578.2 | 1357.2
1578.4 | 1357.4
1578.6 | 1357.6
1578.8 | 1357.8
1579 | 1358
1579.2 | 1358.2
1579.4 | 1358.4
1579.6 | 1358.6
1579.8 | 1358.8
1580 | 1359
1580.2 | 1359.2
1580.4 | 1359.4
1580.6 | 1359.6
1580.8 | 1359.8
1581 | 1360
1581.2 | 1360.2
1581.4 | 1360.4
1581.6 | 1360.6
1581.8 | 1360.8
1582 | 1361
1582.2 | 1361.2
1582.4 | 1361.4
1582.6 | 1361.6
1582.8 | 1361.8
1583 | 1362
1583.2 | 1362.2
1583.4 | 1362.4
1583.6 | 1362.6
1583.8 | 1362.8
1584 | 1363
1584.2 | 1363.2
1584.4 | 1363.4
1584.6 | 1363.6
1584.8 | 1363.8
1585 | 1364
1585.2 | 1364.2
1585.4 | 1364.4
1585.6 | 1364.6
1585.8 | 1364.8
1586 | 1365
1586.2 | 1365.2
1586.4 | 1365.4
1586.6 | 1365.6
1586.8 | 1365.8
1587 | 1366
1587.2 | 1366.2
1587.4 | 1366.4
1587.6 | 1366.6
1587.8 | 1366.8
1588 | 1367
1588.2 | 1367.2
1588.4 | 1367.4
1588.6 | 1367.6
1588.8 | 1367.8
1589 | 1368
1589.2 | 1368.2
1589.4 | 1368.4
1589.6 | 1368.6
1589.8 | 1368.8
1590 | 1369
1590.2 | 1369.2
1590.4 | 1369.4
1590.6 | 1369.6
1590.8 | 1369.8
1591 | 1370
1591.2 | 1370.2
1591.4 | 1370.4
1591.6 | 1370.6
1591.8 | 1370.8
1592 | 1371
1592.2 | 1371.2
1592.4 | 1371.4
1592.6 | 1371.6
1592.8 | 1371.8
1593 | 1372
1593.2 | 1372.2
1593.4 | 1372.4
1593.6 | 1372.6
1593.8 | 1372.8
1594 | 1373
1594.2 | 1373.2
1594.4 | 1373.4
1594.6 | 1373.6
1594.8 | 1373.8
1595 | 1374
1595.2 | 1374.2
1595.4 | 1374.4
1595.6 | 1374.6
1595.8 | 1374.8
1596 | 1375
1596.2 | 1375.2
1596.4 | 1375.4
1596.6 | 1375.6
1596.8 | 1375.8
1597 | 1376
1597.2 | 1376.2
1597.4 | 1376.4
1597.6 | 1376.6
1597.8 | 1376.8
1598 | 1377
1598.2 | 1377.2
1598.4 | 1377.4
1598.6 | 1377.6
1598.8 | 1377.8
1599 | 1378
1599.2 | 1378.2
1599.4 | 1378.4
1599.6 | 1378.6
1599.8 | 1378.8
1600 | 1379
1600.2 | 1379.2
1600.4 | 1379.4
1600.6 | 1379.6
1600.8 | 1379.8
1601 | 1380
1601.2 | 1380.2
1601.4 | 1380.4
1601.6 | 1380.6
1601.8 | 1380.8
1602 | 1381
1602.2 | 1381.2
1602.4 | 1381.4
1602.6 | 1381.6
1602.8 | 1381.8
1603 | 1382
1603.2 | 1382.2
1603.4 | 1382.4
1603.6 | 1382.6
1603.8 | 1382.8
1604 | 1383
1604.2 | 1383.2
1604.4 | 1383.4
1604.6 | 1383.6
1604.8 | 1383.8
1605 | 1384
1605.2 | 1384.2
1605.4 | 1384.4
1605.6 | 1384.6
1605.8 | 1384.8
1606 | 1385
1606.2 | 1385.2
1606.4 | 1385.4
1606.6 | 1385.6
1606.8 | 1385.8
1607 | 1386
1607.2 | 1386.2
1607.4 | 1386.4
1607.6 | 1386.6
1607.8 | 1386.8
1608 | 1387
1608.2 | 1387.2
1608.4 | 1387.4
1608.6 | 1387.6
1608.8 | 1387.8
1609 | 1388
1609.2 | 1388.2
1609.4 | 1388.4
1609.6 | 1388.6
1609.8 | 1388.8
1610 | 1389
1610.2 | 1389.2
1610.4 | 1389.4
1610.6 | 1389.6
1610.8 | 1389.8
1611 | 1390
1611.2 | 1390.2
1611.4 | 1390.4
1611.6 | 1390.6
1611.8 | 1390.8
1612 | 1391
1612.2 | 1391.2
1612.4 | 1391.4
1612.6 | 1391.6
1612.8 | 1391.8
1613 | 1392
1613.2 | 1392.2
1613.4 | 1392.4
1613.6 | 1392.6
1613.8 | 1392.8
1614 | 1393
1614.2 | 1393.2
1614.4 | 1393.4
1614.6 | 1393.6
1614.8 | 1393.8
1615 | 1394
1615.2 | 1394.2
1615.4 | 1394.4
1615.6 | 1394.6
1615.8 | 1394.8
1616 | 1395
1616.2 | 1395.2
1616.4 | 1395.4
1616.6 | 1395.6
1616.8 | 1395.8
1617 | 1396
1617.2 | 1396.2
1617.4 | 1396.4
1617.6 | 1396.6
1617.8 | 1396.8
1618 | 1397
1618.2 | 1397.2
1618.4 | 1397.4
1618.6 | 1397.6
1618.8 | 1397.8
1619 | 1398
1619.2 | 1398.2
1619.4 | 1398.4
1619.6 | 1398.6
1619.8 | 1398.8
1620 | 1399
1620.2 | 1399.2
1620.4 | 1399.4
1620.6 | 1399.6
1620.8 | 1399.8
1621 | 1400
1621.2 | 1400.2
1621.4 | 1400.4
1621.6 | 1400.6
1621.8 | 1400.8
1622 | 1401
1622.2 | 1401.2
1622.4 | 1401.4
1622.6 | 1401.6
1622.8 | 1401.8
1623 | 1402
1623.2 | 1402.2
1623.4 | 1402.4
1623.6 | 1402.6
1623.8 | 1402.8
1624 | 1403
1624.2 | 1403.2
1624.4 | 1403.4
1624.6 | 1403.6
1624.8 | 1403.8
1625 | 1404
1625.2 | 1404.2
1625.4 | 1404.4
1625.6 | 1404.6
1625.8 | 1404.8
1626 | 1405
1626.2 | 1405.2
1626.4 | 1405.4
1626.6 | 1405.6
1626.8 | 1405.8
1627 | 1406
1627.2 | 1406.2
1627.4 | 1406.4
1627.6 | 1406.6
1627.8 | 1406.8
1628 | 1407
1628.2 | 1407.2
1628.4 | 1407.4
1628.6 | 1407.6
1628.8 | 1407.8
1629 | 1408
1629.2 | 1408.2
1629.4 | 1408.4
1629.6 | 1408.6
1629.8 | 1408.8
1630 | 1409
1630.2 | 1409.2
1630.4 | 1409.4
1630.6 | 1409.6
1630.8 | 1409.8
1631 | 1410
1631.2 | 1410.2
1631.4 | 1410.4
1631.6 | 1410.6
1631.8 | 1410.8
1632 | 1411
1632.2 | 1411.2
1632.4 | 1411.4
1632.6 | 1411.6
1632.8 | 1411.8
1633 | 1412
1633.2 | 1412.2
1633.4 | 1412.4
1633.6 | 1412.6
1633.8 | 1412.8
1634 | 1413
1634.2 | 1413.2
1634.4 | 1413.4
1634.6 | 1413.6
1634.8 | 1413.8
1635 | 1414
1635.2 | 1414.2
1635.4 | 1414.4
1635.6 | 1414.6
1635.8 | 1414.8
1636 | 1415
1636.2 | 1415.2
1636.4 | 1415.4
1636.6 | 1415.6
1636.8 | 1415.8
1637 | 1416
1637.2 | 1416.2
1637.4 | 1416.4
1637.6 | 1416.6
1637.8 | 1416.8
1638 | 1417
1638.2 | 1417.2
1638.4 | 1417.4
1638.6 | 1417.6
1638.8 | 1417.8
1639 | 1418
1639.2 | 1418.2
1639.4 | 1418.4
1639.6 | 1418.6
1639.8 | 1418.8
1640 | 1419
1640.2 | 1419.2
1640.4 | 1419.4
1640.6 | 1419.6
1640.8 | 1419.8
1641 | 1420
1641.2 | 1420.2
1641.4 | 1420.4
1641.6 | 1420.6
1641.8 | 1420.8
1642 | 1421
1642.2 | 1421.2
1642.4 | 1421.4
1642.6 | 1421.6
1642.8 | 1421.8
1643 | 1422
1643.2 | 1422.2
1643.4 | 1422.4
1643.6 | 1422.6
1643.8 | 1422.8
1644 | 1423
1644.2 | 1423.2
1644.4 | 1423.4
1644.6 | 1423.6
1644.8 | 1423.8
1645 | 1424
1645.2 | 1424.2
1645.4 | 1424.4
1645.6 | 1424.6
1645.8 | 1424.8
1646 | 1425
1646.2 | 1425.2
1646.4 | 1425.4
1646.6 | 1425.6
1646.8 | 1425.8
1647 | 1426
1647.2 | 1426.2
1647.4 | 1426.4
1647.6 | 1426.6
1647.8 | 1426.8
1648 | 1427
1648.2 | 1427.2
1648.4 | 1427.4
1648.6 | 1427.6
1648.8 | 1427.8
1649 | 1428
1649.2 | 1428.2
1649.4 | 1428.4
1649.6 | 1428.6
1649.8 | 1428.8
1650 | 1429
1650.2 | 1429.2
1650.4 | 1429.4
1650.6 | 1429.6
1650.8 | 1429.8
1651 | 1430
1651.2 | 1430.2
1651.4 | 1430.4
1651.6 | 1430.6
1651.8 | 1430.8
1652 | 1431
1652.2 | 1431.2
1652.4 | 1431.4
1652.6 | 1431.6
1652.8 | 1431.8
1653 | 1432
1653.2 | 1432.2
1653.4 | 1432.4
1653.6 | 1432.6
1653.8 | 1432.8
1654 | 1433
1654.2 | 1433.2
1654.4 | 1433.4
1654.6 | 1433.6
1654.8 | 1433.8
1655 | 1434
1655.2 | 1434.2
1655.4 | 1434.4
1655.6 | 1434.6
1655.8 | 1434.8
1656 | 1435
1656.2 | 1435.2
1656.4 | 1435.4
1656.6 | 1435.6
1656.8 | 1435.8
1657 | 1436
1657.2 | 1436.2
1657.4 | 1436.4
1657.6 | 1436.6
1657.8 | 1436.8
1658 | 1437
1658.2 | 1437.2
1658.4 | 1437.4
1658.6 | 1437.6
1658.8 | 1437.8
1659 | 1438
1659.2 | 1438.2
1659.4 | 1438.4
1659.6 | 1438.6
1659.8 | 1438.8
1660 | 1439
1660.2 | 1439.2
1660.4 | 1439.4
1660.6 | 1439.6
1660.8 | 1439.8
1661 | 1440
1661.2 | 1440.2
1661.4 | 1440.4
1661.6 | 1440.6
1661.8 | 1440.8
1662 | 1441
1662.2 | 1441.2
1662.4 | 1441.4
1662.6 | 1441.6
1662.8 | 1441.8
1663 | 1442
1663.2 | 1442.2
1663.4 | 1442.4
1663.6 | 1442.6
1663.8 | 1442.8
1664 | 1443
1664.2 | 1443.2
1664.4 | 1443.4
1664.6 | 1443.6
1664.8 | 1443.8
1665 | 1444
1665.2 | 1444.2
1665.4 | 1444.4
1665.6 | 1444.6
1665.8 | 1444.8
1666 | 1445
1666.2 | 1445.2
1666.4 | 1445.4
1666.6 | 1445.6
1666.8 | 1445.8
1667 | 1446
1667.2 | 1446.2
1667.4 | 1446.4
1667.6 | 1446.6
1667.8 | 1446.8
1668 | 1447
1668.2 | 1447.2
1668.4 | 1447.4
1668.6 | 1447.6
1668.8 | 1447.8
1669 | 1448
1669.2 | 1448.2
1669.4 | 1448.4
1669.6 | 1448.6
1669.8 | 1448.8
1670 | 1449
1670.2 | 1449.2
1670.4 | 1449.4
1670.6 | 1449.6
1670.8 | 1449.8
1671 | 1450
1671.2 | 1450.2
1671.4 | 1450.4
1671.6 | 1450.6
1671.8 | 1450.8
1672 | 1451
1672.2 | 1451.2
1672.4 | 1451.4
1672.6 | 1451.6
1672.8 | 1451.8
1673 | 1452
1673.2 | 1452.2
1673.4 | 1452.4
1673.6 | 1452.6
1673.8 | 1452.8
1674 | 1453
1674.2 | 1453.2
1674.4 | 1453.4
1674.6 | 1453.6
1674.8 | 1453.8
1675 | 1454
1675.2 | 1454.2
1675.4 | 1454.4
1675.6 | 1454.6
1675.8 | 1454.8
1676 | 1455
1676.2 | 1455.2
1676.4 | 1455.4
1676.6 | 1455.6
1676.8 | 1455.8
1677 | 1456
1677.2 | 1456.2
1677.4 | 1456.4
1677.6 | 1456.6
1677.8 | 1456.8
1678 | 1457
1678.2 | 1457.2
1678.4 | 1457.4
1678.6 | 1457.6
1678.8 | 1457.8
1679 | 1458
1679.2 | 1458.2
1679.4 | 1458.4
1679.6 | 1458.6
1679.8 | 1458.8
1680 | 1459
1680.2 | 1459.2
1680.4 | 1459.4
1680.6 | 1459.6
1680.8 | 1459.8
1681 | 1460
1681.2 | 1460.2
1681.4 | 1460.4
1681.6 | 1460.6
1681.8 | 1460.8
1682 | 1461
1682.2 | 1461.2
1682.4 | 1461.4
1682.6 | 1461.6
1682.8 | 1461.8
1683 | 1462
1683.2 | 1462.2
1683.4 | 1462.4
1683.6 | 1462.6
1683.8 | 1462.8
1684 | 1463
1684.2 | 1463.2
1684.4 | 1463.4
1684.6 | 1463.6
1684.8 | 1463.8
1685 | 1464
1685.2 | 1464.2
1685.4 | 1464.4
1685.6 | 1464.6
1685.8 | 1464.8
1686 | 1465
1686.2 | 1465.2
1686.4 | 1465.4
1686.6 | 1465.6
1686.8 | 1465.8
1687 | 1466
1687.2 | 1466.2
1687.4 | 1466.4
1687.6 | 1466.6
1687.8 | 1466.8
1688 | 1467
1688.2 | 1467.2
1688.4 | 1467.4
1688.6 | 1467.6
1688.8 | 1467.8
1689 | 1468
1689.2 | 1468.2
1689.4 | 1468.4
1689.6 | 1468.6
1689.8 | 1468.8
1690 | 1469
1690.2 | 1469.2
1690.4 | 1469.4
1690.6 | 1469.6
1690.8 | 1469.8
1691 | 1470
1691.2 | 1470.2
1691.4 | 1470.4
1691.6 | 1470.6
1691.8 | 1470.8
1692 | 1471
1692.2 | 1471.2
1692.4 | 1471.4
1692.6 | 1471.6
1692.8 | 1471.8
1693 | 1472
1693.2 | 1472.2
1693.4 | 1472.4
1693.6 | 1472.6
1693.8 | 1472.8
1694 | 1473
1694.2 | 1473.2
1694.4 | 1473.4
1694.6 | 1473.6
1694.8 | 1473.8
1695 | 1474
1695.2 | 1474.2
1695.4 | 1474.4
1695.6 | 1474.6
1695.8 | 1474.8
1696 | 1475
1696.2 | 1475.2
1696.4 | 1475.4
1696.6 | 1475.6
1696.8 | 1475.8
1697 | 1476
1697.2 | 1476.2
1697.4 | 1476.4
1697.6 | 1476.6
1697.8 | 1476.8
1698 | 1477
1698.2 | 1477.2
1698.4 | 1477.4
1698.6 | 1477.6
1698.8 | 1477.8
1699 | 1478
1699.2 | 1478.2
1699.4 | 1478.4
1699.6 | 1478.6
1699.8 | 1478.8
1700 | 1479
1720 | 1499
1740 | 1519
1760 | 1539
1780 | 1559
1800 | 1579
1850 | 1629
1900 | 1679
1950 | 1729
2000 | 1779
2050 | 1829
2100 | 1879
2150 | 1929
2200 | 1979
2250 | 2029
2300 | 2079
2350 | 2129
2400 | 2179
2450 | 2229
2500 | 2279
2550 | 2329
2600 | 2379
2650 | 2429
2700 | 2479
2750 | 2529
2800 | 2579
2850 | 2629
2900 | 2679
2950 | 2729
3000 | 2779
3050 | 2829
3100 | 2879
3150 | 2929
3200 | 2979
3250 | 3029
3300 | 3079
3350 | 3129
3400 | 3179
3450 | 3229
3500 | 3279
3550 | 3329
3577 | 3356

## Circuit 4 Faulting
Summary of Observed Faulting Behavior for Circuit #4
DAQ Time | Burner Time | Event | Discussion
1474 | 1253 | Fuse Blow
Summary Observations |  | This circuit was set up in an inter-cable configuration in a mixed bundel of TS and TP cables. The circuit experiences a fuse blow and no detected inter-cable hot shorts. It appears that the energized PE cable shorted to ground causing the fuse blow.

## Converted Data C4
DAQ Time | Burner Time | C4 V1 | C4 A1 | C4 V2 | C4 A2 | C4 V4 | C4 A4 | C4 V5 | C4 A5 | C4 V6 | C4 A6
0 | -221 | 127.0709 | 0.0094753 | 127.1409 | 0.0089601 | 0.10226 | 0.001151 | 0.25571 | 0.0011344 | 0.20589 | 0.0012561
10 | -211 | 127.0709 | 0.0078755 | 127.045 | 0.0089601 | 0.0063112 | 0.001151 | 0.25571 | 0.0011344 | 0.20589 | 0.0012561
20 | -201 | 126.9749 | 0.0094753 | 127.045 | 0.0089601 | 0.10226 | 0.001151 | 0.25571 | 0.0011344 | 0.20589 | -0.00034306
30 | -191 | 126.9749 | 0.0094753 | 126.8531 | 0.010559 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.20589 | 0.0012561
40 | -181 | 126.879 | 0.0094753 | 126.8531 | 0.0089601 | 0.10226 | -0.00044821 | 0.25571 | 0.0011344 | 0.20589 | 0.0012561
50 | -171 | 126.687 | 0.0094753 | 126.6611 | 0.0089601 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
60 | -161 | 126.687 | 0.0094753 | 126.7571 | 0.0089601 | 0.10226 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
70 | -151 | 126.3032 | 0.0078755 | 126.3732 | 0.0073609 | 0.10226 | 0.001151 | 0.25571 | -0.00046482 | 0.20589 | -0.00034306
80 | -141 | 126.3991 | 0.0046764 | 126.3732 | 0.002562 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
90 | -131 | 126.2072 | 0.0030772 | 126.1813 | 0.002562 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
100 | -121 | 126.3032 | 0.0030772 | 126.2773 | 0.002562 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
110 | -111 | 126.3991 | 0.0046764 | 126.3732 | 0.002562 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | -0.00034306
120 | -101 | 126.3032 | 0.0046764 | 126.2773 | 0.002562 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.20589 | 0.0012561
130 | -91 | 126.4951 | 0.0030772 | 126.4692 | 0.002562 | 0.19825 | 0.001151 | 0.25571 | 0.0011344 | 0.30184 | -0.00034306
140 | -81 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
150 | -71 | 126.3032 | 0.0062763 | 126.1813 | 0.0041619 | 0.19825 | 0.001151 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
160 | -61 | 126.1112 | 0.0062763 | 126.1813 | 0.0057611 | 0.10226 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
170 | -51 | 126.4951 | 0.011074 | 126.4692 | 0.010559 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
180 | -41 | 126.5911 | 0.011074 | 126.4692 | 0.010559 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
190 | -31 | 126.687 | 0.011074 | 126.5652 | 0.010559 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
200 | -21 | 126.5911 | 0.011074 | 126.5652 | 0.010559 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | -0.00034306
210 | -11 | 126.4951 | 0.0094753 | 126.3732 | 0.0089601 | 0.19825 | 0.0027502 | 0.25571 | 0.0011344 | 0.30184 | -0.00034306
220 | -1 | 126.3991 | 0.0094753 | 126.3732 | 0.0089601 | 0.19825 | 0.001151 | 0.35167 | -0.00046482 | 0.30184 | -0.00034306
230 | 9 | 126.3032 | 0.0094753 | 126.2773 | 0.0089601 | 0.19825 | 0.001151 | 0.25571 | -0.00046482 | 0.30184 | -0.00034306
240 | 19 | 126.0153 | 0.0062763 | 125.9894 | 0.0057611 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
250 | 29 | 126.0153 | 0.0046764 | 125.9894 | 0.002562 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
260 | 39 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
270 | 49 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | -0.00034306
270.2 | 49.2 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | -0.00034306
270.4 | 49.4 | 126.3991 | 0.0046764 | 126.4692 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | -0.00034306
270.6 | 49.6 | 126.3991 | 0.0046764 | 126.3732 | 0.002562 | 0.19825 | 0.001151 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
270.8 | 49.8 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.19825 | 0.00435 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
271 | 50 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | -0.00034306
271.2 | 50.2 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
271.4 | 50.4 | 126.4951 | 0.0046764 | 126.3732 | 0.002562 | 0.19825 | 0.001151 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
271.6 | 50.6 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.19825 | 0.00435 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
271.8 | 50.8 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
272 | 51 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
272.2 | 51.2 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
272.4 | 51.4 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
272.6 | 51.6 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
272.8 | 51.8 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
273 | 52 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
273.2 | 52.2 | 126.4951 | 0.0046764 | 126.3732 | 0.002562 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
273.4 | 52.4 | 126.3991 | 0.0046764 | 126.4692 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0011344 | 0.30184 | 0.0012561
273.6 | 52.6 | 126.4951 | 0.0046764 | 126.4692 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
273.8 | 52.8 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
274 | 53 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
274.2 | 53.2 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
274.4 | 53.4 | 126.4951 | 0.0046764 | 126.3732 | 0.0041619 | 0.19825 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
274.6 | 53.6 | 126.4951 | 0.0062763 | 126.4692 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
274.8 | 53.8 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.00435 | 0.44762 | 0.0011344 | 0.30184 | 0.0012561
275 | 54 | 126.3991 | 0.0062763 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
275.2 | 54.2 | 126.4951 | 0.0062763 | 126.3732 | 0.0041619 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
275.4 | 54.4 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0028553
275.6 | 54.6 | 126.3991 | 0.0062763 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0011344 | 0.39783 | 0.0012561
275.8 | 54.8 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.19825 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
276 | 55 | 126.3032 | 0.0062763 | 126.2773 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
276.2 | 55.2 | 126.3991 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
276.4 | 55.4 | 126.3991 | 0.0046764 | 126.3732 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
276.6 | 55.6 | 126.3991 | 0.0062763 | 126.3732 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
276.8 | 55.8 | 126.3991 | 0.0062763 | 126.3732 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
277 | 56 | 126.3991 | 0.0062763 | 126.2773 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
277.2 | 56.2 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
277.4 | 56.4 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
277.6 | 56.6 | 126.3032 | 0.0062763 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
277.8 | 56.8 | 126.3032 | 0.0062763 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
278 | 57 | 126.2072 | 0.0046764 | 126.1813 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
278.2 | 57.2 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
278.4 | 57.4 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
278.6 | 57.6 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
278.8 | 57.8 | 126.3032 | 0.0046764 | 126.2773 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
279 | 58 | 126.2072 | 0.0062763 | 126.1813 | 0.0041619 | 0.2942 | 0.00435 | 0.44762 | 0.0011344 | 0.39783 | 0.0012561
279.2 | 58.2 | 126.2072 | 0.0062763 | 126.1813 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
279.4 | 58.4 | 126.2072 | 0.0046764 | 126.1813 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0028553
279.6 | 58.6 | 126.2072 | 0.0046764 | 126.1813 | 0.0041619 | 0.19825 | 0.0027502 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
279.8 | 58.8 | 126.2072 | 0.0046764 | 126.1813 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
280 | 59 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
280.2 | 59.2 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
280.4 | 59.4 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
280.6 | 59.6 | 126.1112 | 0.0046764 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
280.8 | 59.8 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
281 | 60 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
281.2 | 60.2 | 126.2072 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
281.4 | 60.4 | 126.1112 | 0.0046764 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
281.6 | 60.6 | 126.1112 | 0.0046764 | 126.0853 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
281.8 | 60.8 | 126.1112 | 0.0046764 | 125.9894 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
282 | 61 | 126.0153 | 0.0046764 | 125.9894 | 0.0041619 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
282.2 | 61.2 | 126.1112 | 0.0046764 | 125.9894 | 0.0057611 | 0.19825 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
282.4 | 61.4 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.19825 | 0.0027502 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
282.6 | 61.6 | 126.1112 | 0.0062763 | 126.0853 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
282.8 | 61.8 | 126.1112 | 0.0046764 | 126.0853 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
283 | 62 | 126.1112 | 0.0062763 | 126.0853 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
283.2 | 62.2 | 126.1112 | 0.0062763 | 125.9894 | 0.0057611 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
283.4 | 62.4 | 126.0153 | 0.0062763 | 125.9894 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
283.6 | 62.6 | 126.0153 | 0.0062763 | 125.9894 | 0.0041619 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
283.8 | 62.8 | 126.1112 | 0.0062763 | 125.9894 | 0.0057611 | 0.19825 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
284 | 63 | 126.0153 | 0.0062763 | 126.0853 | 0.0057611 | 0.19825 | 0.0027502 | 0.44762 | 0.0011344 | 0.39783 | -0.00034306
284.2 | 63.2 | 126.0153 | 0.0062763 | 125.9894 | 0.0057611 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
284.4 | 63.4 | 126.1112 | 0.0062763 | 126.0853 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
284.6 | 63.6 | 126.0153 | 0.0062763 | 125.9894 | 0.0057611 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
284.8 | 63.8 | 126.1112 | 0.0062763 | 126.0853 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
285 | 64 | 126.1112 | 0.0062763 | 126.0853 | 0.0057611 | 0.2942 | 0.00435 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
285.2 | 64.2 | 126.0153 | 0.0062763 | 125.9894 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
285.4 | 64.4 | 126.1112 | 0.0062763 | 125.9894 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
285.6 | 64.6 | 126.1112 | 0.0062763 | 125.9894 | 0.0057611 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
285.8 | 64.8 | 126.0153 | 0.0078755 | 125.9894 | 0.0057611 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | -0.00034306
286 | 65 | 126.0153 | 0.0062763 | 125.9894 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
286.2 | 65.2 | 122.6564 | 0.0062763 | 122.6305 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
286.4 | 65.4 | 125.9193 | 0.0062763 | 125.8934 | 0.0057611 | 0.19825 | 0.00435 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
286.6 | 65.6 | 126.1112 | 0.0078755 | 126.0853 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
286.8 | 65.8 | 126.1112 | 0.0078755 | 126.0853 | 0.0073609 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
287 | 66 | 126.1112 | 0.0062763 | 126.0853 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
287.2 | 66.2 | 126.1112 | 0.0078755 | 126.0853 | 0.0073609 | 0.2942 | 0.0027502 | 0.44762 | 0.0011344 | 0.39783 | 0.0012561
287.4 | 66.4 | 126.2072 | 0.0078755 | 126.1813 | 0.0073609 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
287.6 | 66.6 | 126.1112 | 0.0078755 | 126.0853 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
287.8 | 66.8 | 126.2072 | 0.0078755 | 126.1813 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
288 | 67 | 126.1112 | 0.0078755 | 126.0853 | 0.0073609 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
288.2 | 67.2 | 126.2072 | 0.0078755 | 126.0853 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
288.4 | 67.4 | 126.2072 | 0.0078755 | 126.1813 | 0.0073609 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | -0.00034306
288.6 | 67.6 | 126.2072 | 0.0078755 | 126.0853 | 0.0057611 | 0.2942 | 0.00435 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
288.8 | 67.8 | 126.2072 | 0.0062763 | 126.1813 | 0.0073609 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
289 | 68 | 126.2072 | 0.0078755 | 126.0853 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
289.2 | 68.2 | 126.2072 | 0.0078755 | 126.1813 | 0.0073609 | 0.19825 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
289.4 | 68.4 | 126.2072 | 0.0078755 | 126.1813 | 0.0073609 | 0.19825 | 0.0027502 | 0.25571 | 0.0027342 | 0.30184 | 0.0012561
289.6 | 68.6 | 126.2072 | 0.0062763 | 126.0853 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | 0.0012561
289.8 | 68.8 | 126.2072 | 0.0078755 | 126.1813 | 0.0073609 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
290 | 69 | 126.2072 | 0.0078755 | 126.0853 | 0.0073609 | 0.19825 | 0.0027502 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
300 | 79 | 126.3991 | 0.0094753 | 126.2773 | 0.0089601 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
310 | 89 | 126.5911 | 0.011074 | 126.4692 | 0.010559 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
320 | 99 | 126.4951 | 0.011074 | 126.4692 | 0.010559 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
330 | 109 | 126.3032 | 0.0094753 | 126.2773 | 0.0089601 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.20589 | -0.00034306
340 | 119 | 126.3032 | 0.0062763 | 126.1813 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0011344 | 0.39783 | -0.00034306
350 | 129 | 126.2072 | 0.0062763 | 126.1813 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | -0.00034306
360 | 139 | 126.3991 | 0.0094753 | 126.3732 | 0.0089601 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | -0.00034306
370 | 149 | 126.3991 | 0.011074 | 126.3732 | 0.010559 | 0.2942 | 0.00435 | 0.25571 | 0.0011344 | 0.30184 | 0.0012561
380 | 159 | 126.3991 | 0.0094753 | 126.3732 | 0.0089601 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.20589 | -0.00034306
390 | 169 | 126.3032 | 0.0094753 | 126.2773 | 0.0089601 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.39783 | -0.00034306
400 | 179 | 126.3032 | 0.0094753 | 126.2773 | 0.0089601 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
410 | 189 | 126.3991 | 0.0094753 | 126.3732 | 0.0089601 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | -0.00034306
420 | 199 | 126.3991 | 0.0094753 | 126.2773 | 0.0089601 | 0.19825 | 0.0027502 | 0.35167 | 0.0011344 | 0.30184 | 0.0012561
430 | 209 | 126.3032 | 0.0078755 | 126.2773 | 0.0073609 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | -0.00034306
440 | 219 | 126.3032 | 0.0078755 | 126.2773 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
450 | 229 | 126.2072 | 0.0062763 | 126.1813 | 0.0057611 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
460 | 239 | 126.3032 | 0.0062763 | 126.1813 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
470 | 249 | 126.3991 | 0.0062763 | 126.2773 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
480 | 259 | 126.3032 | 0.0062763 | 126.1813 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.30184 | 0.0012561
490 | 269 | 126.3991 | 0.0062763 | 126.3732 | 0.0057611 | 0.2942 | 0.0027502 | 0.35167 | 0.0043334 | 0.30184 | 0.0012561
500 | 279 | 126.4951 | 0.0062763 | 126.3732 | 0.0057611 | 0.2942 | 0.0027502 | 0.44762 | 0.0027342 | 0.39783 | -0.00034306
510 | 289 | 126.879 | 0.0062763 | 126.6611 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
520 | 299 | 126.5911 | 0.0062763 | 126.5652 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | -0.00034306
530 | 309 | 126.687 | 0.0062763 | 126.5652 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
540 | 319 | 126.4951 | 0.0062763 | 126.4692 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
550 | 329 | 126.3991 | 0.0062763 | 126.3732 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
560 | 339 | 126.3991 | 0.0078755 | 126.3732 | 0.0057611 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
570 | 349 | 126.4951 | 0.0062763 | 126.4692 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
580 | 359 | 126.5911 | 0.0062763 | 126.5652 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
590 | 369 | 126.783 | 0.0078755 | 126.6611 | 0.0057611 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
600 | 379 | 126.687 | 0.0062763 | 126.6611 | 0.0041619 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
610 | 389 | 126.783 | 0.0062763 | 126.7571 | 0.0041619 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | -0.00034306
620 | 399 | 126.687 | 0.0062763 | 126.6611 | 0.0057611 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
630 | 409 | 126.5911 | 0.0062763 | 126.4692 | 0.0057611 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
640 | 419 | 126.3991 | 0.0062763 | 126.3732 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
650 | 429 | 126.5911 | 0.0062763 | 126.4692 | 0.0057611 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
660 | 439 | 126.4951 | 0.0062763 | 126.4692 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
670 | 449 | 126.5911 | 0.0078755 | 126.4692 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
680 | 459 | 126.4951 | 0.0062763 | 126.4692 | 0.0057611 | 0.2942 | 0.0059492 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
690 | 469 | 126.3032 | 0.0078755 | 126.2773 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0028553
700 | 479 | 126.2072 | 0.0062763 | 126.2773 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
710 | 489 | 126.3991 | 0.0062763 | 126.2773 | 0.0057611 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
720 | 499 | 126.687 | 0.0078755 | 126.5652 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
730 | 509 | 126.3032 | 0.0078755 | 126.2773 | 0.0089601 | 0.2942 | 0.00435 | 0.54361 | 0.0043334 | 0.49378 | 0.0012561
740 | 519 | 126.4951 | 0.011074 | 126.3732 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
750 | 529 | 126.3991 | 0.012674 | 126.5652 | 0.013758 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.49378 | 0.0028553
760 | 539 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
770 | 549 | 126.5911 | 0.011074 | 126.5652 | 0.010559 | 0.39016 | 0.0059492 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
780 | 559 | 126.5911 | 0.011074 | 126.5652 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
790 | 569 | 126.687 | 0.011074 | 126.5652 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
790.2 | 569.2 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
790.4 | 569.4 | 126.687 | 0.011074 | 126.5652 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
790.6 | 569.6 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.35167 | 0.0043334 | 0.39783 | 0.0012561
790.8 | 569.8 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
791 | 570 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
791.2 | 570.2 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
791.4 | 570.4 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
791.6 | 570.6 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
791.8 | 570.8 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
792 | 571 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
792.2 | 571.2 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
792.4 | 571.4 | 126.5911 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.0059492 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
792.6 | 571.6 | 126.783 | 0.012674 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
792.8 | 571.8 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.35167 | 0.0043334 | 0.39783 | 0.0012561
793 | 572 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
793.2 | 572.2 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
793.4 | 572.4 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0028553
793.6 | 572.6 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
793.8 | 572.8 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
794 | 573 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
794.2 | 573.2 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
794.4 | 573.4 | 126.687 | 0.012674 | 126.7571 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
794.6 | 573.6 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
794.8 | 573.8 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
795 | 574 | 126.783 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.35167 | 0.0043334 | 0.30184 | 0.0028553
795.2 | 574.2 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
795.4 | 574.4 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
795.6 | 574.6 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
795.8 | 574.8 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
796 | 575 | 126.5911 | 0.012674 | 126.5652 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
796.2 | 575.2 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
796.4 | 575.4 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
796.6 | 575.6 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
796.8 | 575.8 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
797 | 576 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
797.2 | 576.2 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
797.4 | 576.4 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
797.6 | 576.6 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
797.8 | 576.8 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.35167 | 0.0043334 | 0.39783 | 0.0012561
798 | 577 | 126.5911 | 0.012674 | 126.5652 | 0.012159 | 0.2942 | 0.0059492 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
798.2 | 577.2 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
798.4 | 577.4 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
798.6 | 577.6 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.30184 | 0.0012561
798.8 | 577.8 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
799 | 578 | 126.687 | 0.012674 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
799.2 | 578.2 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
799.4 | 578.4 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
799.6 | 578.6 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.0059492 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
799.8 | 578.8 | 126.687 | 0.011074 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
800 | 579 | 126.5911 | 0.011074 | 126.5652 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
800.2 | 579.2 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
800.4 | 579.4 | 126.687 | 0.012674 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
800.6 | 579.6 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.39016 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
800.8 | 579.8 | 126.687 | 0.012674 | 126.6611 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
801 | 580 | 123.7121 | 0.011074 | 123.6861 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
801.2 | 580.2 | 126.5911 | 0.012674 | 126.5652 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
801.4 | 580.4 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
801.6 | 580.6 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
801.8 | 580.8 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
802 | 581 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.0059492 | 0.35167 | 0.0043334 | 0.39783 | 0.0012561
802.2 | 581.2 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
802.4 | 581.4 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
802.6 | 581.6 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0028553
802.8 | 581.8 | 126.783 | 0.011074 | 126.7571 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
803 | 582 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
803.2 | 582.2 | 126.879 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
803.4 | 582.4 | 126.783 | 0.012674 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
803.6 | 582.6 | 126.783 | 0.012674 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
803.8 | 582.8 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
804 | 583 | 126.783 | 0.011074 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
804.2 | 583.2 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
804.4 | 583.4 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.0059492 | 0.44762 | 0.0043334 | 0.30184 | 0.0012561
804.6 | 583.6 | 126.879 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
804.8 | 583.8 | 126.783 | 0.012674 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
805 | 584 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.35167 | 0.0043334 | 0.30184 | 0.0012561
805.2 | 584.2 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
805.4 | 584.4 | 126.783 | 0.011074 | 126.7571 | 0.012159 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
805.6 | 584.6 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
805.8 | 584.8 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
806 | 585 | 126.783 | 0.012674 | 126.7571 | 0.012159 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
806.2 | 585.2 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.35167 | 0.0027342 | 0.39783 | 0.0012561
806.4 | 585.4 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
806.6 | 585.6 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
806.8 | 585.8 | 126.783 | 0.012674 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.35167 | 0.0043334 | 0.39783 | 0.0012561
807 | 586 | 126.783 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
808 | 587 | 126.687 | 0.011074 | 126.7571 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
810 | 589 | 126.783 | 0.012674 | 126.6611 | 0.010559 | 0.39016 | 0.00435 | 0.44762 | 0.0027342 | 0.39783 | 0.0012561
820 | 599 | 126.687 | 0.011074 | 126.6611 | 0.010559 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
830 | 609 | 126.5911 | 0.0094753 | 126.5652 | 0.010559 | 0.2942 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
840 | 619 | 126.3032 | 0.0078755 | 126.3732 | 0.0073609 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
850 | 629 | 126.3032 | 0.0078755 | 126.2773 | 0.0057611 | 0.39016 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
860 | 639 | 126.3032 | 0.0078755 | 126.4692 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.39783 | 0.0012561
870 | 649 | 126.3032 | 0.0078755 | 126.2773 | 0.0057611 | 0.2942 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
880 | 659 | 126.3032 | 0.0062763 | 126.2773 | 0.0073609 | 0.2942 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
890 | 669 | 126.4951 | 0.0078755 | 126.4692 | 0.0073609 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
900 | 679 | 126.5911 | 0.0094753 | 126.5652 | 0.0073609 | 0.39016 | 0.00435 | 0.44762 | 0.0043334 | 0.39783 | 0.0012561
910 | 689 | 126.687 | 0.0078755 | 126.6611 | 0.0057611 | 0.2942 | 0.0059492 | 0.35167 | 0.0043334 | 0.39783 | 0.0028553
920 | 699 | 126.4951 | 0.0094753 | 126.4692 | 0.0073609 | 0.2942 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0028553
930 | 709 | 126.3991 | 0.0094753 | 126.3732 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
940 | 719 | 126.3991 | 0.0094753 | 126.3732 | 0.0089601 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.39783 | 0.0028553
950 | 729 | 126.3991 | 0.0094753 | 126.4692 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.49378 | 0.0028553
960 | 739 | 126.3991 | 0.0094753 | 126.4692 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.49378 | 0.0028553
970 | 749 | 126.4951 | 0.0094753 | 126.4692 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
980 | 759 | 126.4951 | 0.0078755 | 126.4692 | 0.0089601 | 0.48615 | 0.0059492 | 0.44762 | 0.0043334 | 0.49378 | 0.0044552
990 | 769 | 126.687 | 0.0078755 | 126.6611 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1000 | 779 | 126.687 | 0.0094753 | 126.5652 | 0.0073609 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
1010 | 789 | 126.3991 | 0.0094753 | 126.3732 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1020 | 799 | 126.3991 | 0.0094753 | 126.3732 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1030 | 809 | 126.3991 | 0.0078755 | 126.3732 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1040 | 819 | 126.3991 | 0.011074 | 126.3732 | 0.010559 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.39783 | 0.0028553
1050 | 829 | 126.3032 | 0.012674 | 126.3732 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0043334 | 0.49378 | 0.0028553
1060 | 839 | 126.4951 | 0.012674 | 126.4692 | 0.013758 | 0.48615 | 0.0059492 | 0.44762 | 0.0043334 | 0.49378 | 0.0028553
1070 | 849 | 126.3032 | 0.012674 | 126.3732 | 0.012159 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1080 | 859 | 126.3991 | 0.012674 | 126.3732 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0028553
1090 | 869 | 126.2072 | 0.011074 | 126.1813 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
1100 | 879 | 126.3032 | 0.011074 | 126.2773 | 0.0089601 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0028553
1110 | 889 | 126.3032 | 0.011074 | 126.2773 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1120 | 899 | 126.3032 | 0.011074 | 126.2773 | 0.010559 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1130 | 909 | 126.3991 | 0.011074 | 126.3732 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1140 | 919 | 126.4951 | 0.012674 | 126.4692 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1150 | 929 | 126.4951 | 0.012674 | 126.5652 | 0.013758 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1160 | 939 | 126.4951 | 0.011074 | 126.4692 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.49378 | 0.0028553
1170 | 949 | 126.3991 | 0.011074 | 126.2773 | 0.0089601 | 0.48615 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0028553
1180 | 959 | 126.4951 | 0.012674 | 126.4692 | 0.012159 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1190 | 969 | 126.687 | 0.014274 | 126.6611 | 0.013758 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.49378 | 0.0028553
1200 | 979 | 126.687 | 0.014274 | 126.7571 | 0.013758 | 0.48615 | 0.0059492 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1210 | 989 | 126.5911 | 0.015873 | 126.5652 | 0.013758 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
1220 | 999 | 126.5911 | 0.015873 | 126.5652 | 0.013758 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1230 | 1009 | 126.5911 | 0.014274 | 126.6611 | 0.013758 | 0.48615 | 0.00435 | 0.54361 | 0.0043334 | 0.39783 | 0.0028553
1240 | 1019 | 126.5911 | 0.012674 | 126.5652 | 0.012159 | 0.39016 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1240.2 | 1019.2 | 126.4951 | 0.012674 | 126.5652 | 0.012159 | 0.39016 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
1250 | 1029 | 126.4951 | 0.014274 | 126.5652 | 0.013758 | 0.39016 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0044552
1260 | 1039 | 126.3991 | 0.011074 | 126.3732 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1270 | 1049 | 126.3032 | 0.0078755 | 126.3732 | 0.0073609 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0028553
1280 | 1059 | 126.4951 | 0.0078755 | 126.4692 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0043334 | 0.49378 | 0.0044552
1290 | 1069 | 126.5911 | 0.0094753 | 126.5652 | 0.0073609 | 0.2942 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
1300 | 1079 | 126.3991 | 0.0094753 | 126.3732 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0044552
1310 | 1089 | 126.2072 | 0.0094753 | 126.2773 | 0.0073609 | 0.48615 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1320 | 1099 | 126.2072 | 0.0094753 | 126.1813 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1330 | 1109 | 126.3991 | 0.0094753 | 126.3732 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1340 | 1119 | 126.3991 | 0.0078755 | 126.3732 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0028553
1350 | 1129 | 126.3032 | 0.0094753 | 126.2773 | 0.0073609 | 0.48615 | 0.0059492 | 0.44762 | 0.0059332 | 0.39783 | 0.0028553
1360 | 1139 | 126.2072 | 0.011074 | 126.2773 | 0.0073609 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1370 | 1149 | 126.4951 | 0.015873 | 126.4692 | 0.012159 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1380 | 1159 | 126.5911 | 0.017473 | 126.5652 | 0.010559 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1390 | 1169 | 126.4951 | 0.017473 | 126.4692 | 0.012159 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.39783 | 0.0044552
1400 | 1179 | 126.4951 | 0.014274 | 126.4692 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.58973 | 0.0028553
1410 | 1189 | 126.4951 | 0.014274 | 126.4692 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1420 | 1199 | 126.3032 | 0.015873 | 126.3732 | 0.0073609 | 0.48615 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1430 | 1209 | 126.3991 | 0.015873 | 126.3732 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1440 | 1219 | 126.3991 | 0.015873 | 126.4692 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1450 | 1229 | 126.687 | 0.019072 | 126.6611 | 0.0089601 | 0.48615 | 0.0059492 | 0.44762 | 0.0043334 | 0.39783 | 0.0028553
1450.2 | 1229.2 | 126.687 | 0.017473 | 126.7571 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1450.4 | 1229.4 | 126.783 | 0.015873 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0028553
1450.6 | 1229.6 | 126.783 | 0.017473 | 126.7571 | 0.0073609 | 0.39016 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1450.8 | 1229.8 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.007549 | 0.44762 | 0.0043334 | 0.49378 | 0.0044552
1451 | 1230 | 126.9749 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1451.2 | 1230.2 | 127.2628 | 0.015873 | 127.045 | 0.0073609 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.58973 | 0.0044552
1451.4 | 1230.4 | 127.2628 | 0.019072 | 127.2369 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1451.6 | 1230.6 | 126.879 | 0.017473 | 126.949 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1451.8 | 1230.8 | 126.879 | 0.019072 | 127.045 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1452 | 1231 | 126.879 | 0.019072 | 126.8531 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0060543
1452.2 | 1231.2 | 126.879 | 0.017473 | 126.8531 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1452.4 | 1231.4 | 126.879 | 0.017473 | 126.8531 | 0.0073609 | 0.39016 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1452.6 | 1231.6 | 126.879 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1452.8 | 1231.8 | 126.783 | 0.017473 | 126.949 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1453 | 1232 | 126.783 | 0.019072 | 126.8531 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1453.2 | 1232.2 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0043334 | 0.49378 | 0.0028553
1453.4 | 1232.4 | 126.783 | 0.019072 | 126.7571 | 0.0089601 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0044552
1453.6 | 1232.6 | 126.783 | 0.017473 | 126.7571 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.39783 | 0.0044552
1453.8 | 1232.8 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1454 | 1233 | 126.783 | 0.019072 | 126.7571 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1454.2 | 1233.2 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0043334 | 0.39783 | 0.0028553
1454.4 | 1233.4 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.5821 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1454.6 | 1233.6 | 126.783 | 0.017473 | 126.8531 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1454.8 | 1233.8 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.0059492 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1455 | 1234 | 126.783 | 0.019072 | 126.7571 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1455.2 | 1234.2 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.39783 | 0.0044552
1455.4 | 1234.4 | 126.687 | 0.019072 | 126.7571 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1455.6 | 1234.6 | 126.783 | 0.017473 | 126.7571 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1455.8 | 1234.8 | 126.687 | 0.017473 | 126.7571 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1456 | 1235 | 126.783 | 0.017473 | 126.7571 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1456.2 | 1235.2 | 126.783 | 0.017473 | 126.7571 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1456.4 | 1235.4 | 126.783 | 0.019072 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.39783 | 0.0044552
1456.6 | 1235.6 | 126.783 | 0.017473 | 126.8531 | 0.0089601 | 0.39016 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1456.8 | 1235.8 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.39016 | 0.007549 | 0.44762 | 0.0059332 | 0.49378 | 0.0044552
1457 | 1236 | 126.783 | 0.019072 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1457.2 | 1236.2 | 126.783 | 0.017473 | 126.8531 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1457.4 | 1236.4 | 126.783 | 0.019072 | 126.7571 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1457.6 | 1236.6 | 126.879 | 0.019072 | 126.8531 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1457.8 | 1236.8 | 126.783 | 0.019072 | 126.8531 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1458 | 1237 | 126.687 | 0.019072 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1458.2 | 1237.2 | 126.783 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1458.4 | 1237.4 | 126.687 | 0.019072 | 126.7571 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1458.6 | 1237.6 | 126.687 | 0.019072 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1458.8 | 1237.8 | 126.687 | 0.019072 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1459 | 1238 | 126.783 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1459.2 | 1238.2 | 126.687 | 0.019072 | 126.7571 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1459.4 | 1238.4 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1459.6 | 1238.6 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1459.8 | 1238.8 | 126.687 | 0.019072 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.58973 | 0.0044552
1460 | 1239 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1460.2 | 1239.2 | 126.783 | 0.020671 | 126.7571 | 0.0089601 | 0.5821 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1460.4 | 1239.4 | 126.783 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1460.6 | 1239.6 | 126.687 | 0.020671 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1460.8 | 1239.8 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0028553
1461 | 1240 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.0091482 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1461.2 | 1240.2 | 126.783 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1461.4 | 1240.4 | 126.783 | 0.020671 | 126.8531 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1461.6 | 1240.6 | 126.783 | 0.022271 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1461.8 | 1240.8 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.0059492 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1462 | 1241 | 126.5911 | 0.020671 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1462.2 | 1241.2 | 126.5911 | 0.019072 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1462.4 | 1241.4 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1462.6 | 1241.6 | 126.687 | 0.020671 | 126.7571 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0075324 | 0.58973 | 0.0060543
1462.8 | 1241.8 | 126.783 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.0091482 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1463 | 1242 | 126.687 | 0.020671 | 126.7571 | 0.0089601 | 0.48615 | 0.0059492 | 0.63956 | 0.0059332 | 0.58973 | 0.0044552
1463.2 | 1242.2 | 126.687 | 0.020671 | 126.6611 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1463.4 | 1242.4 | 126.687 | 0.019072 | 126.6611 | 0.0073609 | 0.39016 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1463.6 | 1242.6 | 126.687 | 0.020671 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1463.8 | 1242.8 | 126.687 | 0.020671 | 126.6611 | 0.0089601 | 0.39016 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1464 | 1243 | 126.5911 | 0.020671 | 126.6611 | 0.0073609 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1464.2 | 1243.2 | 126.5911 | 0.022271 | 126.7571 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1464.4 | 1243.4 | 126.5911 | 0.022271 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1464.6 | 1243.6 | 126.687 | 0.022271 | 126.6611 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1464.8 | 1243.8 | 126.687 | 0.020671 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1465 | 1244 | 126.5911 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1465.2 | 1244.2 | 126.687 | 0.022271 | 126.7571 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1465.4 | 1244.4 | 126.687 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.58973 | 0.0044552
1465.6 | 1244.6 | 126.687 | 0.020671 | 126.6611 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1465.8 | 1244.8 | 126.5911 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.58973 | 0.0044552
1466 | 1245 | 126.4951 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1466.2 | 1245.2 | 126.5911 | 0.02387 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1466.4 | 1245.4 | 126.4951 | 0.02387 | 126.5652 | 0.0089601 | 0.39016 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1466.6 | 1245.6 | 126.5911 | 0.022271 | 126.5652 | 0.0089601 | 0.5821 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1466.8 | 1245.8 | 126.5911 | 0.02387 | 126.6611 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1467 | 1246 | 126.5911 | 0.022271 | 126.6611 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1467.2 | 1246.2 | 126.687 | 0.022271 | 126.6611 | 0.0073609 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1467.4 | 1246.4 | 126.5911 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1467.6 | 1246.6 | 126.5911 | 0.022271 | 126.6611 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1467.8 | 1246.8 | 126.5911 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1468 | 1247 | 126.4951 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1468.2 | 1247.2 | 126.5911 | 0.022271 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1468.4 | 1247.4 | 126.4951 | 0.022271 | 126.6611 | 0.0073609 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1468.6 | 1247.6 | 126.5911 | 0.02387 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.58973 | 0.0060543
1468.8 | 1247.8 | 126.5911 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1469 | 1248 | 126.5911 | 0.02387 | 126.6611 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0060543
1469.2 | 1248.2 | 126.4951 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1469.4 | 1248.4 | 126.5911 | 0.022271 | 126.5652 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1469.6 | 1248.6 | 126.5911 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1469.8 | 1248.8 | 126.4951 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1470 | 1249 | 126.4951 | 0.022271 | 126.5652 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0060543
1470.2 | 1249.2 | 126.4951 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.58973 | 0.0044552
1470.4 | 1249.4 | 126.3991 | 0.022271 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1470.6 | 1249.6 | 126.3991 | 0.02387 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1470.8 | 1249.8 | 126.4951 | 0.022271 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1471 | 1250 | 126.4951 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.0059492 | 0.63956 | 0.0075324 | 0.58973 | 0.0060543
1471.2 | 1250.2 | 126.4951 | 0.022271 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1471.4 | 1250.4 | 126.4951 | 0.02387 | 126.5652 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1471.6 | 1250.6 | 126.4951 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1471.8 | 1250.8 | 126.4951 | 0.02387 | 126.4692 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0060543
1472 | 1251 | 126.3991 | 0.02387 | 126.4692 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1472.2 | 1251.2 | 126.4951 | 0.02387 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1472.4 | 1251.4 | 126.4951 | 0.02387 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1472.6 | 1251.6 | 126.3991 | 0.022271 | 126.5652 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1472.8 | 1251.8 | 126.5911 | 0.02387 | 126.5652 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0060543
1473 | 1252 | 126.4951 | 0.02387 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.58973 | 0.0044552
1473.2 | 1252.2 | 126.4951 | 0.02387 | 126.4692 | 0.0073609 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1473.4 | 1252.4 | 126.3991 | 0.02387 | 126.4692 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1473.6 | 1252.6 | 126.3991 | 0.02387 | 126.4692 | 0.0089601 | 0.5821 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1473.8 | 1252.8 | 28.1287 | 0.019072 | 28.4867 | 4.3547 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1474 | 1253 | 4.3288 | 0.014274 | 4.5908 | 0.28727 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1474.2 | 1253.2 | 1.7377 | 0.012674 | 1.7118 | 0.048946 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1474.4 | 1253.4 | 1.0659 | 0.011074 | 1.136 | 0.023355 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.58973 | 0.0044552
1474.6 | 1253.6 | 0.874 | 0.011074 | 0.94405 | 0.015358 | 0.39016 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1474.8 | 1253.8 | 0.68206 | 0.011074 | 0.8481 | 0.013758 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1475 | 1254 | 0.68206 | 0.011074 | 0.75211 | 0.012159 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1475.2 | 1254.2 | 0.68206 | 0.011074 | 0.65616 | 0.010559 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1475.4 | 1254.4 | 0.58611 | 0.0094753 | 0.65616 | 0.010559 | 0.39016 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0028553
1475.6 | 1254.6 | 0.58611 | 0.011074 | 0.65616 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0060543
1475.8 | 1254.8 | 0.58611 | 0.0094753 | 0.65616 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1476 | 1255 | 0.58611 | 0.0094753 | 0.56021 | 0.010559 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1476.2 | 1255.2 | 0.58611 | 0.0094753 | 0.56021 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1476.4 | 1255.4 | 0.49012 | 0.0094753 | 0.56021 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.58973 | 0.0044552
1476.6 | 1255.6 | 0.58611 | 0.0094753 | 0.56021 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1476.8 | 1255.8 | 0.49012 | 0.0094753 | 0.56021 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1477 | 1256 | 0.49012 | 0.0094753 | 0.65616 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1477.2 | 1256.2 | 0.58611 | 0.0094753 | 0.56021 | 0.0089601 | 0.48615 | 0.007549 | 0.63956 | 0.0075324 | 0.49378 | 0.0044552
1477.4 | 1256.4 | 0.58611 | 0.0094753 | 0.56021 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1477.6 | 1256.6 | 0.49012 | 0.0078755 | 0.46422 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.58973 | 0.0044552
1477.8 | 1256.8 | 0.49012 | 0.0094753 | 0.56021 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1478 | 1257 | 0.49012 | 0.0078755 | 0.46422 | 0.0073609 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0060543
1478.2 | 1257.2 | 0.49012 | 0.0094753 | 0.46422 | 0.0073609 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1478.4 | 1257.4 | 0.49012 | 0.0094753 | 0.46422 | 0.0073609 | 0.48615 | 0.0059492 | 0.63956 | 0.0059332 | 0.49378 | 0.0044552
1478.6 | 1257.6 | 0.49012 | 0.0078755 | 0.46422 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.58973 | 0.0044552
1478.8 | 1257.8 | 0.49012 | 0.0094753 | 0.46422 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1479 | 1258 | 0.49012 | 0.011074 | 0.56021 | 0.0073609 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552
1479.2 | 1258.2 | 0.49012 | 0.0094753 | 0.46422 | 0.0073609 | 0.48615 | 0.007549 | 0.63956 | 0.0059332 | 0.49378 | 0.0028553
1479.4 | 1258.4 | 0.49012 | 0.0094753 | 0.46422 | 0.0073609 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1479.6 | 1258.6 | 0.49012 | 0.0078755 | 0.46422 | 0.0089601 | 0.48615 | 0.0059492 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1479.8 | 1258.8 | 0.39416 | 0.0078755 | 0.46422 | 0.0089601 | 0.39016 | 0.007549 | 0.54361 | 0.0059332 | 0.49378 | 0.0044552
1480 | 1259 | 0.49012 | 0.0094753 | 0.46422 | 0.0089601 | 0.48615 | 0.007549 | 0.54361 | 0.0075324 | 0.49378 | 0.0044552