## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-2
Test Date: | 2006-10-24
Ignition Time Relative to Thermal Data: | 221 | s
Ignition Time Relative to Electrical Data: | 221 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
7/C Cable at Location G.
12-cable XLPE/CSPE bundle at Location A

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A: 12-cable XLPE/CSPE bundle |  |  |  | Location A: 12-Cable XLPE/CSPE and PE/PVC Bundle |  |  |  | Location A | Location C: 6-Cable XLPE/CSPE Bundle |  |  | Location C: 6-Cable XLPE/CSPE and PE/PVC Bundle |  |  | Location C |  | Location E: Single PVC/PVC cable |  |  |  | Location G: Single PVC/PVC Cable
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-4 Bundle Center | TC-1 Cable A | TC-2 Above Bundle | TC3 Below Bundle | TC-4 Bundle Center | TC-1 Cable A | TC-2 Above Bundle | TC3 Below Bundle | Tray Rung | Bundle Center | Air Above | Air Below | Bundle Center | Air Above | Air Below | General air TC among cables | Tray Rung | Cable Temp | Air Above | Air Below | Cable Tray | Cable Temp | Air Above | Air Below | Cable Tray
0 | -221 | -6.6 | 0 | 0 | 18.4 | 18.6 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.5 | 260.5 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
1 | -220 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.4 | 260.7 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
2 | -219 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.4 | 261.8 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
3 | -218 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.4 | 264.3 | 5.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
4 | -217 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.4 | 271.4 | 4.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
5 | -216 | -6.6 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 270.3 | 4.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17.1
6 | -215 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 263.5 | 4.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
7 | -214 | -6 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 254.1 | 4.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17.1
8 | -213 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 258.5 | 4.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17.1
9 | -212 | -6.1 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 263.9 | 4.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
10 | -211 | -5.9 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 264.9 | 4.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
11 | -210 | -5.5 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.4 | 257.2 | 4.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
12 | -209 | -5.8 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.4 | 254.9 | 4.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
13 | -208 | -6.3 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.4 | 253.1 | 4.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
14 | -207 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 251.5 | 4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
15 | -206 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 253.2 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
16 | -205 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 260 | 3.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
17 | -204 | -6.1 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 265.5 | 4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
18 | -203 | -6.1 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 262.4 | 4.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
19 | -202 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.4 | 262.5 | 4.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.4 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17.1
20 | -201 | -5.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 263.6 | 4.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
21 | -200 | -6.2 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 262.3 | 4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
22 | -199 | -6.5 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 261.1 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
23 | -198 | -6.6 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 256 | 3.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
24 | -197 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 247.3 | 4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
25 | -196 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 244.7 | 4.1 | 17.7 | 17.7 | 17.3 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
26 | -195 | -6.6 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 246.4 | 4.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
27 | -194 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 237.5 | 5.2 | 17.7 | 17.7 | 17.3 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
28 | -193 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 231.2 | 5.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
29 | -192 | -5.4 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 241.1 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
30 | -191 | -5.8 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 247.2 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
31 | -190 | -6.3 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 237.4 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
32 | -189 | -6.3 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 233 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
33 | -188 | -6 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 244.4 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
34 | -187 | -5.6 | 0 | 0 | 18.4 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 240.9 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
35 | -186 | -5.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 242.4 | 5.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
36 | -185 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 238.8 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
37 | -184 | -6.6 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.4 | 243 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
38 | -183 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 246.6 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
39 | -182 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 245.2 | 5.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
40 | -181 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.3 | 249.4 | 5.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
41 | -180 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.4 | 257.5 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
42 | -179 | -6.6 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.5 | 242.1 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
43 | -178 | -6.6 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 236.6 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
44 | -177 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.6 | 242.5 | 5.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
45 | -176 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.6 | 244.4 | 5.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
46 | -175 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.7 | 245.5 | 5.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
47 | -174 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.9 | 244.2 | 5.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
48 | -173 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.8 | 234.2 | 4.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
49 | -172 | -6.8 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.5 | 17.7 | 1.5 | 247.9 | 4.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
50 | -171 | -6.7 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.7 | 274.4 | 4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
51 | -170 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.8 | 264.7 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
52 | -169 | -6.4 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.5 | 17.7 | 1.6 | 246.8 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
53 | -168 | -6.5 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.5 | 239.8 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
54 | -167 | -6.2 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.3 | 246.7 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
55 | -166 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.1 | 258.9 | 3.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
56 | -165 | -6.5 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.5 | 17.7 | 1.3 | 256.1 | 4.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
57 | -164 | -6.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.1 | 240.2 | 3.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
58 | -163 | -6.5 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.2 | 232.1 | 4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
59 | -162 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.1 | 249.1 | 4.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
60 | -161 | -6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.2 | 248.8 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
61 | -160 | -5.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.1 | 228.2 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
62 | -159 | -5.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1 | 213.1 | 3.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
63 | -158 | -5.4 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.1 | 214.3 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
64 | -157 | -5.5 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 227.6 | 3.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
65 | -156 | -5.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 233.7 | 3.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
66 | -155 | -5.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 220.4 | 2.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.5 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
67 | -154 | -6.1 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 213.7 | 3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.4 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
68 | -153 | -6.7 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 216 | 3.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
69 | -152 | -6.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.4 | 216.3 | 3.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.7 | 17.6 | 17.7 | 17
70 | -151 | -6.8 | 0 | 0 | 18.2 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 216.1 | 3.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
71 | -150 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 215.2 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
72 | -149 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.2 | 213.1 | 3.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
73 | -148 | -6.3 | 0 | 0 | 18.2 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 210.8 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
74 | -147 | -6.4 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 210.9 | 3.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
75 | -146 | -6.7 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 207.7 | 3.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
76 | -145 | -6.2 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 204.5 | 3.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
77 | -144 | -5 | 0 | 0 | 18.2 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 208.3 | 3.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
78 | -143 | -6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 208.5 | 3.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
79 | -142 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 209.6 | 3.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
80 | -141 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.5 | 212 | 3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
81 | -140 | -6.7 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.5 | 214.6 | 2.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
82 | -139 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 229.1 | 2.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.5 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
83 | -138 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 244.1 | 2.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
84 | -137 | -6.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 237.8 | 2.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
85 | -136 | -6.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 216.5 | 2.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
86 | -135 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.3 | 236.2 | 2.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
87 | -134 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.5 | 277.3 | 2.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
88 | -133 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.5 | 275.9 | 3.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
89 | -132 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 256.4 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
90 | -131 | -6.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 1.4 | 245.5 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
91 | -130 | -6.6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.4 | 241.6 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
92 | -129 | -6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.4 | 251.2 | 3.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
93 | -128 | -5.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.4 | 254.7 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.3 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
94 | -127 | -6.1 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.6 | 242.8 | 3.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
95 | -126 | -6.5 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.5 | 235 | 2.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
96 | -125 | -6.6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.6 | 242.4 | 2.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
97 | -124 | -6.6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.5 | 245.6 | 2.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
98 | -123 | -6.3 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.6 | 250 | 2.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
99 | -122 | -6.1 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.4 | 265.4 | 2.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
100 | -121 | -6.5 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.5 | 269.1 | 3.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
101 | -120 | -6.7 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.6 | 262 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
102 | -119 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.8 | 263.2 | 3.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
103 | -118 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.8 | 256.2 | 3.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.6 | 17.7 | 17
104 | -117 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.9 | 254.3 | 3.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
105 | -116 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.5 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.7 | 265.5 | 3.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
106 | -115 | -6.7 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.7 | 275 | 4.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
107 | -114 | -6.7 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.9 | 262.3 | 4.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
108 | -113 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.5 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.9 | 255.9 | 4.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
109 | -112 | -6.4 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 1.9 | 254.3 | 4.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
110 | -111 | -6 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.5 | 21.6 | 17.7 | 2.2 | 255.2 | 4.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
111 | -110 | -5.9 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 18.9 | 17.4 | 21.6 | 17.7 | 2.5 | 253.6 | 4.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
112 | -109 | -6.2 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 2.6 | 244.6 | 4.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
113 | -108 | -6.1 | 0 | 0 | 18.3 | 18.6 | 18.4 | 18.4 | 19 | 17.5 | 21.6 | 17.7 | 2.6 | 263.2 | 4.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
114 | -107 | -5.5 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.4 | 18.9 | 17.5 | 21.6 | 17.7 | 2.2 | 275.1 | 4.6 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
115 | -106 | -5.3 | 0 | 0 | 18.2 | 18.6 | 18.3 | 18.4 | 18.9 | 17.4 | 21.6 | 17.7 | 2.5 | 277 | 4.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
116 | -105 | -5.7 | 0 | 0 | 18.2 | 18.6 | 18.3 | 18.4 | 18.9 | 17.4 | 21.6 | 17.7 | 2.4 | 258.1 | 4.2 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
117 | -104 | -6.6 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.4 | 18.9 | 17.4 | 21.6 | 17.7 | 2.2 | 249.8 | 4.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
118 | -103 | -6.8 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.9 | 248.9 | 4.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
119 | -102 | -6.7 | 0 | 0 | 18.2 | 18.6 | 18.3 | 18.4 | 18.9 | 17.4 | 21.6 | 17.7 | 2 | 246 | 5.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
120 | -101 | -5 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 2 | 256 | 6.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
121 | -100 | -4.3 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 2.1 | 243.1 | 7.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
122 | -99 | -5.3 | 0 | 0 | 18.2 | 18.6 | 18.2 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 2.1 | 229.7 | 8.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
123 | -98 | -5.6 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 2.2 | 231.1 | 7.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
124 | -97 | -5.7 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.4 | 21.6 | 17.7 | 1.7 | 229.4 | 6.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.7 | 17
125 | -96 | -5.8 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 224.9 | 4.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
126 | -95 | -6 | 0 | 0 | 18.2 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 226 | 4.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
127 | -94 | -6.2 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 229.2 | 5.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
128 | -93 | -6.4 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.6 | 239.5 | 7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
129 | -92 | -6.5 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 240 | 8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
130 | -91 | -6.6 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 245.6 | 7.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
131 | -90 | -6.5 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.3 | 246.8 | 7.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
132 | -89 | -6 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.4 | 256.8 | 7.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
133 | -88 | -6 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.5 | 267.7 | 6.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
134 | -87 | -6.1 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.8 | 1.5 | 257 | 6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
135 | -86 | -6.6 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 19 | 17.3 | 21.6 | 17.8 | 1.4 | 251.5 | 7.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
136 | -85 | -6.7 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 18.9 | 17.3 | 21.6 | 17.8 | 1.4 | 266.3 | 8.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
137 | -84 | -6.8 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.4 | 260 | 9.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
138 | -83 | -6.8 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 262.1 | 9.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
139 | -82 | -6.7 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 263.5 | 9.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
140 | -81 | -6.3 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 2.3 | 264.1 | 9.6 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
141 | -80 | -6.5 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 2.6 | 263.4 | 9.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
142 | -79 | -6.5 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 2.5 | 269.2 | 8.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
143 | -78 | -6.4 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 2.2 | 272 | 8.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
144 | -77 | -6.3 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 263.2 | 9.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
145 | -76 | -6.1 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 261 | 9.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
146 | -75 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 258.3 | 8.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
147 | -74 | -6.2 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 256.1 | 8.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
148 | -73 | -6.3 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 252.9 | 8.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
149 | -72 | -6 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 249.2 | 8 | 17.7 | 17.6 | 17.2 | 17.2 | 17.4 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
150 | -71 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 249.9 | 7.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
151 | -70 | -6.1 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.5 | 246.9 | 7.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
152 | -69 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.5 | 239.5 | 7.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
153 | -68 | -5.3 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 255 | 7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
154 | -67 | -5.5 | 0 | 0 | 18.2 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.4 | 264.2 | 6.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
155 | -66 | -5.5 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.3 | 243.6 | 5.8 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
156 | -65 | -5.2 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.4 | 256.4 | 5.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
157 | -64 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.3 | 266.6 | 6.2 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
158 | -63 | -5.1 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.4 | 264.4 | 6.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
159 | -62 | -5.6 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.4 | 21.6 | 17.7 | 1.7 | 265.8 | 6.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
160 | -61 | -5.4 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 19 | 17.3 | 21.6 | 17.7 | 1.8 | 259.9 | 6.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
161 | -60 | -5.8 | 0 | 0 | 18.2 | 18.5 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 258.4 | 6.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
162 | -59 | -6.4 | 0 | 0 | 18.3 | 18.5 | 18.1 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 272 | 7 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.1 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
163 | -58 | -6.8 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 274.7 | 6.9 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.4 | 18.9 | 17.8 | 17.7 | 17.8 | 17
164 | -57 | -6.7 | 0 | 0 | 18.2 | 18.5 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 268.3 | 6.5 | 17.7 | 17.7 | 17.2 | 17.2 | 17.4 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.7 | 17.7 | 17.8 | 17
165 | -56 | -6.4 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.7 | 253.8 | 6.3 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.7 | 17.7 | 17.8 | 17
166 | -55 | -6.3 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 266.6 | 6.5 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
167 | -54 | -6.5 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.5 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 270.8 | 6.6 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
168 | -53 | -6.6 | 0 | 0 | 18.2 | 18.5 | 18.2 | 18.5 | 18.9 | 17.2 | 21.6 | 17.7 | 1.8 | 257.2 | 7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.7 | 17.7 | 17.8 | 17
169 | -52 | -6.6 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.4 | 18.9 | 17.2 | 21.6 | 17.7 | 1.9 | 255.6 | 7.3 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
170 | -51 | -6.5 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.4 | 18.9 | 17.2 | 21.6 | 17.7 | 1.9 | 257.8 | 7.5 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.7 | 17.8 | 17
171 | -50 | -6.7 | 0 | 0 | 18.2 | 18.5 | 18.2 | 18.4 | 18.9 | 17.2 | 21.6 | 17.7 | 1.9 | 254.7 | 7.3 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.7 | 17
172 | -49 | -6.7 | 0 | 0 | 18.2 | 18.5 | 18.2 | 18.4 | 18.9 | 17.2 | 21.6 | 17.7 | 1.9 | 249.7 | 7.3 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.7 | 17.7 | 17
173 | -48 | -6.4 | 0 | 0 | 18.3 | 18.5 | 18.2 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 260.8 | 8 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 17.9 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
174 | -47 | -5.9 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 2 | 262.9 | 8 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
175 | -46 | -5.4 | 0 | 0 | 18.2 | 18.5 | 18.3 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 2.2 | 270.6 | 7.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
176 | -45 | -5.1 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 2.5 | 262.3 | 8.1 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.8 | 17.7 | 17.8 | 17
177 | -44 | -5.4 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 2.2 | 258.5 | 8.3 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.7 | 17
178 | -43 | -6 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.4 | 18.9 | 17.3 | 21.6 | 17.7 | 2.3 | 272.9 | 8 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.7 | 17
179 | -42 | -3 | 0 | 0 | 18.3 | 18.4 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 2.3 | 257.4 | 8.1 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.7 | 17
180 | -41 | -6.8 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 2.5 | 257.5 | 8.5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.8 | 17
181 | -40 | -5.2 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 2.2 | 250.7 | 8.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.7 | 17
182 | -39 | 1.6 | 0.64 | 0.74812 | 18.3 | 18.5 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 2.3 | 249.3 | 8.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
183 | -38 | 4 | 1.6 | 1.8703 | 18.3 | 18.5 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 2.3 | 251.1 | 8.6 | 17.7 | 17.7 | 17.2 | 17.2 | 17.4 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
184 | -37 | 5.2 | 2.08 | 2.4314 | 18.3 | 18.5 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 2.5 | 253 | 8.4 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.4 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.7 | 17.7 | 17
185 | -36 | 6.2 | 2.48 | 2.899 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 2.3 | 251.7 | 7.8 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
186 | -35 | 3.6 | 1.44 | 1.6833 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 2.4 | 250.9 | 7.6 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
187 | -34 | 2.5 | 1 | 1.1689 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 2.3 | 251 | 7.8 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
188 | -33 | 3.2 | 1.28 | 1.4962 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.9 | 250.1 | 7.6 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.2 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
189 | -32 | 2.1 | 0.84 | 0.98191 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.8 | 244.4 | 7.7 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
190 | -31 | 0.1 | 0.04 | 0.046758 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.8 | 240.9 | 6.7 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
191 | -30 | -2 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 245.5 | 6.1 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
192 | -29 | -3.6 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 244.3 | 6.3 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.8 | 17.6 | 17.7 | 17
193 | -28 | -4.7 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 244.1 | 6.9 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
194 | -27 | -4.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 244.7 | 7.2 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
195 | -26 | -5.2 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 243.8 | 7.2 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
196 | -25 | -5.6 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.4 | 21.6 | 17.7 | 1.6 | 244.8 | 7.4 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
197 | -24 | -5.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 18.9 | 17.4 | 21.6 | 17.7 | 1.6 | 245.6 | 7.6 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.2 | 18.5 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
198 | -23 | -5.7 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.4 | 21.6 | 17.7 | 1.6 | 249.6 | 7.5 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
199 | -22 | -4.9 | 0 | 0 | 18.2 | 18.5 | 18.4 | 18.3 | 18.9 | 17.4 | 21.6 | 17.7 | 1.5 | 249.7 | 7 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.2 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
200 | -21 | -4.3 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 246 | 6.6 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
201 | -20 | -4.7 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.6 | 17.7 | 1.6 | 245.4 | 6.4 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
202 | -19 | -5.4 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.2 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 246.8 | 6.1 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.2 | 18.5 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
203 | -18 | -5.7 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.7 | 254 | 5.6 | 17.7 | 17.7 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.2 | 18.5 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
204 | -17 | -6 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.8 | 253.5 | 5.4 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.5 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
205 | -16 | -6 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.7 | 247.7 | 5.4 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.2 | 18.5 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
206 | -15 | -5.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.5 | 248.1 | 5.3 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
207 | -14 | -5.8 | 0 | 0 | 18.3 | 18.5 | 18.4 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 252.6 | 5.1 | 17.7 | 17.6 | 17.2 | 17.2 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.2 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
208 | -13 | -6 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 268.8 | 4.7 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
209 | -12 | -6.1 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.5 | 270.4 | 4.8 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
210 | -11 | -5.4 | 0 | 0 | 18.4 | 18.5 | 18.3 | 18.3 | 19 | 17.4 | 21.6 | 17.7 | 1.6 | 267.8 | 5 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
211 | -10 | -4.1 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.6 | 261.6 | 5.1 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
212 | -9 | -4 | 0 | 0 | 18.3 | 18.5 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 250.8 | 5.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
213 | -8 | -4.8 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.3 | 18.9 | 17.3 | 21.6 | 17.7 | 1.6 | 249.6 | 5.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
214 | -7 | -5 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.6 | 254.2 | 5.2 | 17.7 | 17.6 | 17.2 | 17.3 | 17.4 | 17.7 | 17.1 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
215 | -6 | -5 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.7 | 258.7 | 5.2 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
216 | -5 | -5 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 256.3 | 5 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.3 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
217 | -4 | -3.9 | 0 | 0 | 18.3 | 18.6 | 18.3 | 18.3 | 19 | 17.3 | 21.6 | 17.7 | 1.5 | 258.6 | 4.6 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
218 | -3 | -3.9 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.3 | 19 | 17.2 | 21.6 | 17.7 | 1.7 | 264.2 | 4.5 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
219 | -2 | -4.4 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.3 | 19 | 17.2 | 21.6 | 17.7 | 1.5 | 274 | 4.3 | 17.7 | 17.7 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
220 | -1 | -4.8 | 0 | 0 | 18.3 | 18.6 | 18.2 | 18.3 | 19 | 17.2 | 21.6 | 17.7 | 1.5 | 277 | 4.2 | 17.7 | 17.6 | 17.2 | 17.3 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
221 | 0 | 63.2 | 25.28 | 29.5509 | 18.4 | 18.5 | 18.2 | 18.3 | 19 | 17.2 | 21.6 | 17.7 | 1.6 | 270.5 | 4.1 | 17.7 | 17.6 | 17.2 | 17.4 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
222 | 1 | 371.6 | 148.64 | 173.7516 | 18.3 | 18.6 | 18.2 | 18.3 | 19 | 17.2 | 21.6 | 17.7 | 1.7 | 277.1 | 3.7 | 17.7 | 17.7 | 17.2 | 17.4 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
223 | 2 | 518.1 | 207.24 | 242.2516 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.8 | 275 | 3.3 | 17.7 | 17.6 | 17.2 | 17.4 | 17.4 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
224 | 3 | 538.9 | 215.56 | 251.9772 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.3 | 21.6 | 17.7 | 1.9 | 256 | 3.2 | 17.7 | 17.6 | 17.2 | 17.4 | 17.5 | 17.7 | 17.2 | 17.3 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.3 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 18.9 | 17.7 | 17.6 | 17.7 | 17
225 | 4 | 519.2 | 207.68 | 242.766 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.2 | 21.6 | 17.7 | 2 | 251 | 3.5 | 17.7 | 17.6 | 17.2 | 17.5 | 17.5 | 17.7 | 17.2 | 18.7 | 18.6 | 17.5 | 17.4 | 17.2 | 17.8 | 17.4 | 17.4 | 18.1 | 18.7 | 18.1 | 18 | 17.5 | 19 | 17.7 | 17.6 | 17.7 | 17
226 | 5 | 498.1 | 199.24 | 232.9001 | 18.3 | 18.6 | 18.2 | 18.4 | 19 | 17.2 | 21.6 | 17.7 | 1.9 | 255.1 | 3.9 | 17.7 | 17.6 | 17.3 | 26.3 | 17.5 | 17.7 | 18.8 | 25.7 | 19.9 | 17.5 | 17.4 | 17.3 | 17.8 | 17.7 | 18.6 | 18.2 | 18.8 | 18.1 | 18 | 17.5 | 19 | 17.7 | 17.7 | 17.7 | 17.1
227 | 6 | 482.6 | 193.04 | 225.6526 | 18.3 | 18.6 | 18.3 | 18.5 | 19.3 | 17.2 | 21.6 | 17.7 | 2.1 | 254.8 | 4.8 | 17.7 | 17.6 | 18.5 | 46.1 | 17.4 | 17.7 | 23 | 43.2 | 23.1 | 17.5 | 18.6 | 21.5 | 17.8 | 19.1 | 22.6 | 18.2 | 19.3 | 18.1 | 18 | 17.8 | 19.2 | 17.7 | 17.7 | 17.8 | 17.1
228 | 7 | 476.1 | 190.44 | 222.6134 | 18.4 | 18.6 | 18.4 | 18.6 | 20.8 | 17.3 | 21.6 | 17.7 | 2.3 | 263.9 | 5.9 | 17.7 | 17.6 | 24.4 | 74.3 | 17.5 | 17.7 | 30.7 | 71.7 | 27.2 | 17.5 | 23.1 | 30.1 | 17.8 | 21.1 | 26.4 | 18.2 | 20.3 | 18.1 | 18.3 | 18.9 | 19.6 | 17.8 | 17.8 | 17.8 | 17.2
229 | 8 | 476.5 | 190.6 | 222.8004 | 18.5 | 18.7 | 18.5 | 18.7 | 27.6 | 17.3 | 21.6 | 17.7 | 2.4 | 278 | 6.8 | 17.7 | 17.6 | 31.9 | 127.3 | 17.5 | 17.7 | 37 | 101.3 | 32.7 | 17.5 | 30.8 | 44.5 | 17.8 | 23.6 | 30.4 | 18.2 | 21.7 | 18.1 | 18.6 | 19.1 | 19.9 | 17.8 | 17.9 | 17.9 | 17.3
230 | 9 | 468.4 | 187.36 | 219.013 | 18.7 | 18.8 | 18.8 | 19 | 40 | 17.3 | 21.6 | 17.7 | 2.4 | 276.9 | 6.9 | 17.7 | 17.6 | 45.6 | 169.4 | 17.5 | 17.7 | 48.2 | 135.7 | 39 | 17.5 | 43.4 | 63.5 | 17.8 | 27 | 36.5 | 18.2 | 23.7 | 18.1 | 18.8 | 19.2 | 20.1 | 17.8 | 18 | 18 | 17.4
231 | 10 | 460.6 | 184.24 | 215.3659 | 18.9 | 19.1 | 20.1 | 20.2 | 49.7 | 17.3 | 21.6 | 17.7 | 2.4 | 259.8 | 6.4 | 17.7 | 17.7 | 61.2 | 214.4 | 17.5 | 17.7 | 72 | 178.6 | 45.8 | 17.6 | 55.4 | 79.8 | 17.8 | 31.5 | 47.9 | 18.2 | 26.3 | 18.1 | 18.9 | 19.3 | 20.4 | 17.8 | 18.2 | 18.1 | 17.5
232 | 11 | 455.9 | 182.36 | 213.1683 | 19.5 | 19.4 | 21.6 | 22.2 | 61.3 | 17.4 | 21.6 | 17.7 | 2.4 | 255.7 | 6.1 | 17.7 | 17.6 | 77.4 | 279.1 | 17.5 | 17.7 | 102.7 | 238.6 | 61 | 17.6 | 72.2 | 107.8 | 17.8 | 37.6 | 66.3 | 18.2 | 31 | 18.1 | 19 | 19.5 | 20.6 | 17.9 | 18.4 | 18.3 | 17.6
233 | 12 | 453.7 | 181.48 | 212.1397 | 20.2 | 20 | 23.5 | 24.7 | 75.9 | 17.4 | 21.6 | 17.7 | 2.6 | 270 | 6.2 | 17.7 | 17.7 | 97.9 | 342.2 | 17.5 | 17.7 | 132.5 | 273.6 | 76.6 | 17.7 | 96.9 | 138.2 | 17.8 | 46.8 | 83.2 | 18.2 | 39.2 | 18.1 | 19.5 | 19.9 | 20.9 | 17.9 | 18.6 | 18.6 | 17.7
234 | 13 | 452.2 | 180.88 | 211.4383 | 20.7 | 20.9 | 25.3 | 27.2 | 97.4 | 17.4 | 21.6 | 17.7 | 2.7 | 266 | 6.6 | 17.7 | 17.7 | 128.1 | 404.6 | 17.5 | 17.7 | 147.5 | 302.1 | 87.3 | 17.8 | 125 | 178.3 | 17.8 | 51.1 | 89.3 | 18.2 | 43.1 | 18.1 | 20.7 | 20.7 | 21.4 | 18 | 19 | 19 | 17.9
235 | 14 | 451 | 180.4 | 210.8772 | 21.5 | 21.4 | 27.8 | 31.2 | 118.3 | 17.5 | 21.6 | 17.7 | 2.6 | 272 | 6.9 | 17.7 | 17.7 | 150.2 | 461.4 | 17.5 | 17.8 | 164.1 | 334.6 | 99.4 | 18 | 143.4 | 202.5 | 17.8 | 56.1 | 100.4 | 18.2 | 46.7 | 18.1 | 22.1 | 21.6 | 21.9 | 18 | 19.5 | 20.1 | 18
236 | 15 | 450.8 | 180.32 | 210.7837 | 24.1 | 23.6 | 30.9 | 35.8 | 136.1 | 17.5 | 21.6 | 17.7 | 2.5 | 271.8 | 6.8 | 17.8 | 17.7 | 173.1 | 498.3 | 17.5 | 17.8 | 173.5 | 370.8 | 107.9 | 18.1 | 156.8 | 222.8 | 17.8 | 59.3 | 110.2 | 18.2 | 49.6 | 18.2 | 23.8 | 22.8 | 22.5 | 18.1 | 20.3 | 22 | 18.2
237 | 16 | 451.2 | 180.48 | 210.9707 | 26.7 | 27.2 | 34.6 | 40.1 | 151.2 | 17.6 | 21.6 | 17.7 | 2.7 | 275.3 | 6.4 | 17.8 | 17.7 | 188.8 | 542.7 | 17.5 | 17.9 | 185.9 | 391.3 | 117.1 | 18.4 | 167 | 233.3 | 17.8 | 66 | 121.2 | 18.2 | 53.1 | 18.2 | 26.1 | 24.2 | 23.1 | 18.2 | 21.4 | 23.7 | 18.4
238 | 17 | 451.2 | 180.48 | 210.9707 | 29.4 | 30.3 | 41.5 | 45.8 | 163.8 | 17.6 | 21.6 | 17.7 | 2.6 | 267.8 | 6.3 | 17.8 | 17.7 | 216.9 | 572.5 | 17.5 | 17.9 | 206 | 429.5 | 128.6 | 18.7 | 181.4 | 255.3 | 17.9 | 70.1 | 128.9 | 18.3 | 55.5 | 18.3 | 28.8 | 26 | 23.6 | 18.3 | 22.8 | 25.9 | 18.6
239 | 18 | 448.4 | 179.36 | 209.6615 | 32 | 32.7 | 47 | 52.9 | 175.2 | 17.6 | 21.6 | 17.8 | 2.5 | 271 | 6.5 | 17.8 | 17.7 | 239.2 | 613.7 | 17.5 | 18.1 | 236.8 | 470.6 | 138.7 | 18.9 | 195 | 271.3 | 17.9 | 80.5 | 160.3 | 18.3 | 61.5 | 18.4 | 32 | 28.1 | 24.2 | 18.4 | 24.5 | 29.8 | 18.9
240 | 19 | 449.4 | 179.76 | 210.1291 | 34.5 | 34.1 | 53.2 | 59.4 | 182.2 | 17.7 | 21.6 | 17.8 | 2.5 | 262.6 | 6.6 | 17.9 | 17.7 | 274.1 | 641.7 | 17.5 | 18.5 | 246.6 | 495.4 | 153.7 | 19.2 | 209 | 296 | 17.9 | 89.3 | 173.6 | 18.3 | 67.2 | 18.6 | 35 | 30.2 | 24.9 | 18.5 | 26.7 | 34.8 | 19.4
241 | 20 | 450.5 | 180.2 | 210.6434 | 38.1 | 36.3 | 58.3 | 63.8 | 189.4 | 17.7 | 21.6 | 17.9 | 2.7 | 266.9 | 6.4 | 17.9 | 17.7 | 305.9 | 673 | 17.5 | 19 | 258.6 | 515.4 | 170.3 | 19.6 | 226.7 | 324.7 | 18 | 97.8 | 193.9 | 18.3 | 73.3 | 18.8 | 37.8 | 32.4 | 25.8 | 18.7 | 28.9 | 38.2 | 19.9
242 | 21 | 451.4 | 180.56 | 211.0642 | 41.4 | 40.1 | 63.8 | 68 | 198.5 | 17.7 | 21.6 | 18.1 | 2.7 | 270.5 | 6.3 | 18 | 17.7 | 328.6 | 698.2 | 17.6 | 19.7 | 275.6 | 550 | 184.1 | 19.9 | 243.8 | 353.1 | 18 | 107.1 | 206.9 | 18.3 | 79 | 19 | 40.8 | 34.8 | 26.3 | 18.9 | 31.4 | 42 | 20.3
243 | 22 | 451.1 | 180.44 | 210.924 | 44.7 | 44 | 68.7 | 73.1 | 208.5 | 17.8 | 21.6 | 18.2 | 2.6 | 278.5 | 5.8 | 18 | 17.7 | 356.9 | 710.5 | 17.7 | 20.5 | 313.2 | 584.7 | 199.6 | 20.2 | 262.2 | 382.7 | 18 | 112.9 | 221.9 | 18.3 | 85.2 | 19.3 | 44.2 | 37.4 | 26.9 | 19.2 | 34.1 | 44.3 | 20.6
244 | 23 | 451.8 | 180.72 | 211.2513 | 49.2 | 47.5 | 72.3 | 78 | 219.9 | 17.8 | 21.6 | 18.4 | 2.3 | 274.7 | 6.2 | 18.1 | 17.7 | 389.2 | 720.4 | 17.8 | 21.3 | 336.3 | 617.1 | 215.2 | 20.6 | 275.4 | 405.9 | 18.1 | 119.2 | 241.1 | 18.3 | 90.5 | 19.6 | 47.9 | 40 | 27.1 | 19.5 | 36.6 | 46.9 | 20.8
245 | 24 | 455.1 | 182.04 | 212.7943 | 54.6 | 50.7 | 76.7 | 82.8 | 226.6 | 17.8 | 21.6 | 18.6 | 2.2 | 269.5 | 6.4 | 18.1 | 17.8 | 399.8 | 733.7 | 17.9 | 22.3 | 367.4 | 631.8 | 224.5 | 21 | 286.9 | 426.9 | 18.2 | 127 | 263 | 18.3 | 98.2 | 19.9 | 51.4 | 42.8 | 27.4 | 19.8 | 39 | 49.7 | 21.1
246 | 25 | 456.6 | 182.64 | 213.4956 | 59.7 | 53.9 | 82.8 | 87 | 236.8 | 17.8 | 21.6 | 18.8 | 2.5 | 265.2 | 6.4 | 18.2 | 17.8 | 435.3 | 738.3 | 18.1 | 23.4 | 389 | 647.5 | 233.5 | 21.4 | 302.3 | 446.5 | 18.3 | 136.2 | 284.1 | 18.4 | 103.8 | 20.2 | 54.7 | 45 | 28.1 | 20.1 | 41.4 | 52.1 | 21.6
247 | 26 | 457.3 | 182.92 | 213.8229 | 63.4 | 58.5 | 88.5 | 91 | 246.2 | 17.8 | 21.6 | 19.1 | 2.5 | 278.8 | 6.7 | 18.3 | 17.9 | 451.5 | 741.4 | 18.3 | 24.6 | 403.5 | 661.4 | 245.8 | 21.8 | 310.6 | 447.8 | 18.3 | 143.5 | 289.4 | 18.4 | 108.1 | 20.5 | 58 | 47.4 | 28.6 | 20.4 | 43.7 | 55.4 | 22
248 | 27 | 458 | 183.2 | 214.1502 | 67.3 | 64.2 | 94 | 94.4 | 247.6 | 17.9 | 21.6 | 19.6 | 2.6 | 278.3 | 6.7 | 18.5 | 17.9 | 465.1 | 743.2 | 18.5 | 25.8 | 417.7 | 681.4 | 259.1 | 22.3 | 314.5 | 454.7 | 18.4 | 147.8 | 294.5 | 18.4 | 111.7 | 20.9 | 61.3 | 50.2 | 28.6 | 20.7 | 45.8 | 58.6 | 22.3
249 | 28 | 457.5 | 183 | 213.9165 | 70.3 | 69.6 | 99.6 | 98 | 251.5 | 17.9 | 21.6 | 20 | 2.6 | 273.2 | 6.3 | 18.6 | 18 | 477.2 | 744.7 | 18.7 | 27.1 | 438.5 | 699.5 | 270.5 | 22.7 | 319.7 | 458.5 | 18.5 | 155.8 | 311.9 | 18.5 | 117.4 | 21.3 | 64.7 | 53.6 | 29.2 | 21 | 48.4 | 62.4 | 22.5
250 | 29 | 458.1 | 183.24 | 214.197 | 72.9 | 74.2 | 105.7 | 102 | 256.4 | 17.9 | 21.6 | 20.5 | 2.7 | 270.6 | 5.8 | 18.8 | 18.1 | 495.5 | 749.8 | 19 | 28.3 | 462.1 | 715.6 | 280.9 | 23.1 | 330.3 | 467.7 | 18.6 | 166.3 | 331.9 | 18.5 | 123.1 | 21.7 | 67.8 | 56.7 | 29.9 | 21.3 | 51 | 66 | 22.9
251 | 30 | 458.7 | 183.48 | 214.4775 | 76.8 | 77.9 | 111 | 107.3 | 262.5 | 18 | 21.6 | 21.1 | 2.4 | 263.3 | 5.3 | 19 | 18.3 | 498.3 | 749.9 | 19.2 | 29.5 | 488 | 733.3 | 293.9 | 23.4 | 334.4 | 480.7 | 18.7 | 176.1 | 351.8 | 18.5 | 128.6 | 22.1 | 71.4 | 59.5 | 30.3 | 21.6 | 54.6 | 69.2 | 23.7
252 | 31 | 460.2 | 184.08 | 215.1789 | 80.7 | 81.9 | 114.7 | 111.6 | 271.9 | 18 | 21.6 | 21.7 | 2.6 | 265.7 | 4.9 | 19.2 | 18.4 | 486.3 | 754 | 19.5 | 30.7 | 510.1 | 744 | 305.7 | 23.7 | 336.1 | 466.1 | 18.8 | 184.9 | 369 | 18.5 | 133.2 | 22.5 | 74.7 | 62.7 | 31.1 | 21.9 | 58 | 72.2 | 24.2
253 | 32 | 460.9 | 184.36 | 215.5062 | 83.7 | 84.9 | 117.8 | 115.1 | 272.9 | 18.1 | 21.6 | 22.3 | 2.6 | 270.8 | 5.1 | 19.4 | 18.6 | 477.9 | 758.7 | 19.9 | 31.9 | 525.2 | 751.9 | 316.8 | 24 | 337.6 | 459.2 | 19 | 190.7 | 378.6 | 18.6 | 135.9 | 22.9 | 78 | 64.8 | 31.6 | 22.2 | 60.2 | 75.6 | 24.5
254 | 33 | 461.7 | 184.68 | 215.8803 | 88.1 | 89.1 | 121.8 | 118.5 | 275 | 18.1 | 21.6 | 22.9 | 2.3 | 275.6 | 5 | 19.7 | 18.7 | 476.8 | 756.4 | 20.2 | 32.9 | 534.6 | 750.7 | 323.6 | 24.3 | 342.7 | 457.9 | 19.1 | 199.1 | 393.6 | 18.8 | 139.6 | 23.3 | 81.1 | 67.7 | 32.4 | 22.5 | 62.7 | 78.6 | 25
255 | 34 | 461.3 | 184.52 | 215.6932 | 92.9 | 93.9 | 126.9 | 122.1 | 281.6 | 18.1 | 21.6 | 23.6 | 2.4 | 276.3 | 5.3 | 19.9 | 18.9 | 474.2 | 760.2 | 20.6 | 33.9 | 540.9 | 752.4 | 331.4 | 24.6 | 346.3 | 461.5 | 19.2 | 203.6 | 406.2 | 19 | 142.5 | 23.7 | 84.3 | 70.5 | 33.1 | 22.8 | 65.6 | 81.8 | 25.3
256 | 35 | 461.8 | 184.72 | 215.927 | 97.8 | 98.8 | 130.8 | 125.7 | 284.7 | 18.1 | 21.6 | 24.2 | 2.2 | 285.6 | 6.1 | 20.2 | 19.1 | 480.3 | 766.2 | 21 | 34.8 | 567.2 | 745.5 | 343.4 | 24.8 | 355.1 | 472.5 | 19.4 | 211.4 | 428.5 | 19.2 | 148.4 | 24.1 | 87.6 | 72.6 | 33.6 | 23.1 | 70.1 | 84.8 | 25.9
257 | 36 | 462.8 | 185.12 | 216.3946 | 101 | 102.8 | 133.5 | 128.9 | 290.8 | 18.1 | 21.6 | 24.8 | 2.5 | 268.9 | 6.6 | 20.6 | 19.3 | 488.4 | 767.9 | 21.4 | 35.7 | 582.4 | 740 | 352.4 | 25.1 | 359.4 | 471.1 | 19.6 | 219.3 | 439.3 | 19.4 | 154.6 | 24.5 | 91.1 | 75.5 | 34.3 | 23.4 | 73.4 | 87.7 | 26.4
258 | 37 | 463.6 | 185.44 | 216.7687 | 103.3 | 107.3 | 137.6 | 131.6 | 294.5 | 18.1 | 21.6 | 25.4 | 2.7 | 269.7 | 7.3 | 20.9 | 19.6 | 490.5 | 773.2 | 21.8 | 36.6 | 582.6 | 746 | 363.3 | 25.4 | 358.7 | 466.3 | 19.7 | 226.9 | 446.5 | 19.7 | 157.5 | 25 | 94.8 | 78.5 | 34.6 | 23.7 | 75.6 | 90.8 | 26.8
259 | 38 | 461.8 | 184.72 | 215.927 | 106.2 | 112.5 | 141.8 | 134.1 | 297.1 | 18.1 | 21.6 | 26 | 2.6 | 273.7 | 7.2 | 21.3 | 19.8 | 503.2 | 779 | 22.2 | 37.5 | 596.9 | 739.6 | 373 | 25.7 | 360.7 | 472.2 | 19.9 | 230.4 | 448.5 | 19.9 | 160.7 | 25.4 | 98.1 | 80.8 | 34.9 | 24.1 | 78.3 | 94.1 | 27.3
260 | 39 | 462.4 | 184.96 | 216.2076 | 109.1 | 116.5 | 145.8 | 136.5 | 295.9 | 18.1 | 21.6 | 26.6 | 2.5 | 260.2 | 7.4 | 21.7 | 20.1 | 510.7 | 782.7 | 22.6 | 38.3 | 607 | 743.5 | 383.1 | 26 | 366.3 | 488.6 | 20.2 | 231.9 | 456.3 | 20.2 | 164.5 | 26 | 100.9 | 83.1 | 35.7 | 24.4 | 81.2 | 96.9 | 27.7
261 | 40 | 465.1 | 186.04 | 217.47 | 112.4 | 119.2 | 148.5 | 138.8 | 299.7 | 18.2 | 21.6 | 27.3 | 2.7 | 271.1 | 7.2 | 22.1 | 20.4 | 518.7 | 788.7 | 23 | 39.1 | 605.9 | 725.2 | 391.8 | 26.3 | 369.7 | 500.8 | 20.4 | 235 | 454.9 | 20.5 | 168.7 | 26.5 | 103.4 | 85.4 | 36.8 | 24.8 | 84.6 | 99 | 28.4
262 | 41 | 467.1 | 186.84 | 218.4052 | 115.9 | 122.6 | 151.9 | 141.3 | 305.7 | 18.3 | 21.6 | 27.9 | 2.6 | 265.2 | 7.1 | 22.5 | 20.6 | 527.2 | 793.2 | 23.4 | 39.8 | 595.7 | 739.7 | 399.8 | 26.7 | 370.3 | 509.6 | 20.7 | 235.1 | 450.9 | 20.9 | 171.5 | 27 | 106.6 | 87.9 | 38 | 25.1 | 87.4 | 101.7 | 28.9
263 | 42 | 467.4 | 186.96 | 218.5455 | 120.4 | 126.4 | 156.2 | 144.2 | 314.4 | 18.4 | 21.6 | 28.4 | 2.8 | 268.4 | 7 | 23 | 20.9 | 526.3 | 795.5 | 23.8 | 40.5 | 601.7 | 733.8 | 411.2 | 27 | 370.5 | 514 | 21 | 237.6 | 452 | 21.3 | 174.6 | 27.5 | 110 | 90.2 | 38.7 | 25.5 | 90.4 | 104.6 | 29.3
264 | 43 | 465.7 | 186.28 | 217.7506 | 124.5 | 129.6 | 159.8 | 146.7 | 313.3 | 18.5 | 21.6 | 28.9 | 2.8 | 265.3 | 6.6 | 23.4 | 21.1 | 538.3 | 806.6 | 24.2 | 41.1 | 617.7 | 729.9 | 421.2 | 27.4 | 373.7 | 529.3 | 21.3 | 242.4 | 457.1 | 21.8 | 181.8 | 28 | 113.1 | 92.5 | 39.4 | 25.8 | 93.9 | 106.5 | 29.8
265 | 44 | 465.9 | 186.36 | 217.8441 | 128 | 133.2 | 164.5 | 149.1 | 321.6 | 18.5 | 21.6 | 29.4 | 3 | 269.2 | 6.2 | 23.9 | 21.4 | 553.9 | 805.6 | 24.6 | 41.7 | 612.9 | 735.3 | 428.9 | 27.9 | 376.3 | 531.1 | 21.7 | 242.2 | 454.5 | 22.3 | 184.9 | 28.5 | 115.9 | 95.2 | 40.6 | 26.2 | 96 | 108.1 | 30.2
266 | 45 | 466.1 | 186.44 | 217.9376 | 129.2 | 136.2 | 169.2 | 150.7 | 319.4 | 18.4 | 21.6 | 30 | 3.2 | 263.8 | 5.9 | 24.4 | 21.6 | 560.1 | 797.4 | 25 | 42.3 | 613.4 | 740.1 | 436.8 | 28.3 | 377.3 | 530.6 | 22 | 243.3 | 453.3 | 22.9 | 187.2 | 29 | 118.9 | 97.6 | 41.2 | 26.6 | 98 | 110.2 | 30.6
267 | 46 | 467.6 | 187.04 | 218.639 | 131 | 138.3 | 171.2 | 151.9 | 314.8 | 18.4 | 21.6 | 30.4 | 2.9 | 252.7 | 5.5 | 24.9 | 21.8 | 576.3 | 809.9 | 25.5 | 42.9 | 621.1 | 729.6 | 443.6 | 28.7 | 380.3 | 543.3 | 22.4 | 246.4 | 454.4 | 23.6 | 190.5 | 29.6 | 122 | 100.4 | 42.4 | 26.9 | 100.2 | 112.7 | 31.2
268 | 47 | 467.2 | 186.88 | 218.452 | 134 | 140.8 | 173.2 | 153.4 | 320.2 | 18.4 | 21.6 | 30.9 | 2.9 | 277 | 5 | 25.4 | 22 | 575.4 | 814.5 | 25.9 | 43.5 | 618.6 | 720.7 | 452 | 29.2 | 380.7 | 541 | 22.8 | 248 | 451.5 | 24.2 | 193.2 | 30.1 | 125.1 | 103.7 | 43.3 | 27.3 | 101.9 | 114.8 | 31.9
269 | 48 | 467 | 186.8 | 218.3584 | 136.6 | 143.4 | 175.2 | 155.1 | 324 | 18.4 | 21.6 | 31.5 | 3.1 | 277 | 4.7 | 25.9 | 22.2 | 582 | 828.1 | 26.3 | 44 | 624.4 | 713 | 459.3 | 29.7 | 383.6 | 547.1 | 23.3 | 249.3 | 457.2 | 25 | 196.8 | 30.6 | 127.4 | 106.8 | 43.8 | 27.7 | 103.8 | 117.1 | 32.2
270 | 49 | 469.5 | 187.8 | 219.5274 | 138.5 | 145 | 179.4 | 156.8 | 329.3 | 18.5 | 21.6 | 32 | 3.2 | 259.1 | 4.5 | 26.4 | 22.4 | 590.1 | 837.9 | 26.8 | 44.6 | 637.5 | 727.7 | 467.6 | 30.2 | 389.4 | 552.8 | 23.7 | 259.5 | 479.1 | 26 | 201.5 | 31.1 | 129.6 | 108.7 | 44.4 | 28 | 105.8 | 119 | 32.6
271 | 50 | 470.1 | 188.04 | 219.8079 | 140.9 | 146.3 | 181.5 | 158.3 | 327.3 | 18.4 | 21.6 | 32.5 | 3.3 | 264.3 | 4.5 | 26.9 | 22.6 | 591.5 | 835.1 | 27.2 | 45.1 | 634 | 746.9 | 477.8 | 30.7 | 389 | 552.5 | 24.2 | 267.3 | 494.2 | 27 | 206.5 | 31.6 | 131.9 | 110.6 | 44.8 | 28.4 | 107.8 | 121.4 | 33.2
272 | 51 | 471 | 188.4 | 220.2287 | 143 | 148.1 | 182.6 | 159.3 | 322 | 18.5 | 21.6 | 33 | 3.3 | 269.9 | 4.9 | 27.3 | 22.8 | 593.8 | 825.5 | 27.6 | 45.7 | 641.3 | 747.8 | 485.3 | 31.3 | 389.1 | 542.7 | 24.7 | 273.8 | 504.8 | 28.1 | 210.3 | 32 | 134.1 | 112.3 | 45.2 | 28.7 | 110.1 | 123.8 | 33.7
273 | 52 | 473.1 | 189.24 | 221.2107 | 144.6 | 149.1 | 183.4 | 161.5 | 317.1 | 18.5 | 21.6 | 33.4 | 2.8 | 265.2 | 5 | 27.8 | 22.9 | 601.2 | 831.5 | 28.1 | 46.2 | 654 | 748.6 | 493.8 | 31.8 | 390.5 | 543.8 | 25.2 | 281.8 | 516.5 | 29.3 | 214.3 | 32.5 | 136.1 | 114.4 | 45.4 | 29.1 | 111.9 | 125.3 | 34.3
274 | 53 | 472.2 | 188.88 | 220.7898 | 145.8 | 149.5 | 184.5 | 164 | 318.7 | 18.5 | 21.6 | 33.7 | 2.6 | 259.8 | 5.1 | 28.2 | 23.1 | 613.3 | 829.4 | 28.5 | 46.7 | 670.7 | 754.5 | 501.3 | 32.4 | 397.7 | 552.6 | 25.8 | 287 | 522.7 | 30.7 | 220.1 | 33 | 138.4 | 115.9 | 45.8 | 29.5 | 114.1 | 126.9 | 34.8
275 | 54 | 470.3 | 188.12 | 219.9014 | 147.7 | 150.9 | 185 | 165.6 | 317.7 | 18.6 | 21.6 | 34 | 2.1 | 263.1 | 5 | 28.6 | 23.2 | 616.2 | 826.3 | 29 | 47.3 | 674.3 | 744.5 | 508 | 33 | 399.6 | 552.8 | 26.3 | 291.3 | 527.9 | 31.9 | 224.2 | 33.5 | 140.1 | 118.1 | 46.8 | 30 | 115.6 | 128.4 | 35.3
276 | 55 | 471.1 | 188.44 | 220.2755 | 149.6 | 151.8 | 186.4 | 167.3 | 317.8 | 18.6 | 21.6 | 34.3 | 2.5 | 261.5 | 5.1 | 29 | 23.4 | 619.1 | 823.8 | 29.4 | 47.9 | 676.6 | 744.7 | 515 | 33.6 | 400.7 | 552.7 | 27 | 298.4 | 539.1 | 33 | 229.9 | 34 | 141.8 | 120.7 | 47.2 | 30.4 | 117.1 | 130.6 | 35.9
277 | 56 | 472 | 188.8 | 220.6963 | 151.7 | 152.9 | 187.4 | 168.6 | 317.2 | 18.7 | 21.5 | 34.5 | 2.5 | 260 | 5.1 | 29.4 | 23.5 | 608.2 | 828.6 | 29.9 | 48.5 | 686.2 | 758.3 | 522.5 | 34.3 | 400.7 | 549 | 27.6 | 306.2 | 542.8 | 34.2 | 233.6 | 34.6 | 143.2 | 122.7 | 47.9 | 30.8 | 118.7 | 132.9 | 36.4
278 | 57 | 470.8 | 188.32 | 220.1352 | 152.6 | 153.1 | 187.9 | 170.2 | 317.4 | 18.7 | 21.5 | 34.7 | 2.9 | 259.3 | 4.7 | 29.8 | 23.7 | 593.5 | 829.9 | 30.3 | 49.2 | 684.6 | 769.2 | 528.3 | 34.9 | 397.1 | 550.3 | 28.3 | 304.6 | 529.5 | 35.1 | 234.6 | 35.1 | 144.6 | 124 | 48.6 | 31.2 | 122.1 | 134.6 | 36.9
279 | 58 | 472.9 | 189.16 | 221.1171 | 154.1 | 154.6 | 188.4 | 172.2 | 318 | 18.8 | 21.5 | 34.9 | 3.2 | 260.1 | 4.3 | 30.1 | 23.9 | 584.6 | 819.3 | 30.8 | 49.8 | 688 | 774.1 | 532.5 | 35.6 | 396.4 | 543.3 | 28.9 | 304.6 | 524.4 | 36 | 236.8 | 35.6 | 145.9 | 126.3 | 49.7 | 31.7 | 125.4 | 136.1 | 37.6
280 | 59 | 472.5 | 189 | 220.9301 | 155.3 | 155.6 | 189.5 | 173.5 | 315.6 | 18.9 | 21.5 | 35.3 | 3.1 | 263.5 | 4.5 | 30.4 | 24 | 572.2 | 799 | 31.2 | 50.5 | 686.1 | 778.7 | 537.6 | 36.3 | 390.8 | 522.7 | 29.6 | 304.1 | 520.5 | 36.9 | 238.1 | 36.2 | 147.4 | 127.8 | 49.9 | 32.1 | 127.6 | 137.6 | 37.9
281 | 60 | 472.2 | 188.88 | 220.7898 | 156.7 | 156.4 | 190.3 | 174.1 | 315.2 | 18.9 | 21.5 | 35.6 | 3.2 | 260.8 | 4.7 | 30.7 | 24.2 | 558.7 | 788.4 | 31.7 | 51.1 | 666.9 | 778.9 | 543.7 | 36.9 | 384.5 | 504.3 | 30.3 | 300 | 511 | 37.4 | 238 | 36.7 | 148.9 | 128.7 | 50.2 | 32.5 | 128.9 | 138.8 | 38.2
282 | 61 | 472.5 | 189 | 220.9301 | 157.9 | 157 | 190.6 | 175.6 | 312 | 18.9 | 21.5 | 36 | 3 | 260 | 4.5 | 31 | 24.3 | 543.8 | 786.5 | 32.1 | 51.6 | 651.1 | 788.9 | 546.2 | 37.6 | 377.8 | 487.7 | 31 | 296.9 | 501.1 | 38.1 | 238.1 | 37.2 | 150.1 | 130.2 | 51.5 | 33 | 129.8 | 140.7 | 38.7
283 | 62 | 474.2 | 189.68 | 221.725 | 159.1 | 157.5 | 190.2 | 177.2 | 311.3 | 19 | 21.5 | 36.3 | 2.9 | 261.3 | 4.3 | 31.2 | 24.5 | 537.4 | 788.7 | 32.5 | 52.2 | 649 | 789.2 | 552.8 | 38.3 | 372.6 | 486.8 | 31.8 | 294.5 | 492.5 | 38.8 | 239.1 | 37.7 | 150.8 | 131.2 | 52 | 33.4 | 131.1 | 142.9 | 39.4
284 | 63 | 475.9 | 190.36 | 222.5199 | 160.2 | 157.4 | 189.5 | 178.6 | 314.5 | 19 | 21.5 | 36.7 | 2.9 | 260.8 | 4.1 | 31.6 | 24.7 | 543.4 | 799.8 | 32.9 | 52.6 | 655.8 | 779.9 | 558.6 | 39 | 373.8 | 505.8 | 32.5 | 292.6 | 494.1 | 39.6 | 241.9 | 38.2 | 151.8 | 132.6 | 52.5 | 33.8 | 132.9 | 144.9 | 40.1
285 | 64 | 475 | 190 | 222.0991 | 161.4 | 158.2 | 189.2 | 180.2 | 327 | 19.1 | 21.5 | 37.1 | 2.7 | 248.5 | 3.9 | 31.8 | 24.9 | 548.8 | 809.2 | 33.3 | 53 | 644.4 | 768 | 564.5 | 39.6 | 377.5 | 529.4 | 33.2 | 291.1 | 490.2 | 40.3 | 246.6 | 38.7 | 152.6 | 134.3 | 53.8 | 34.2 | 135.2 | 146.1 | 40.6
286 | 65 | 474.4 | 189.76 | 221.8185 | 162.8 | 159.9 | 190.2 | 181.8 | 333.4 | 19.2 | 21.5 | 37.5 | 2.5 | 248.2 | 3.5 | 32.1 | 25.2 | 544.9 | 814.9 | 33.7 | 53.5 | 646.3 | 770.6 | 570.2 | 40.3 | 377.1 | 534.1 | 34 | 289.9 | 480.3 | 40.8 | 249.3 | 39.2 | 153.8 | 135.3 | 54.5 | 34.7 | 136.4 | 147.5 | 40.9
287 | 66 | 475.7 | 190.28 | 222.4264 | 163.8 | 161.5 | 190.5 | 182.5 | 330.7 | 19.3 | 21.5 | 37.8 | 2.2 | 254.7 | 3.2 | 32.3 | 25.4 | 534.3 | 818.1 | 34.1 | 54.1 | 644.4 | 760.7 | 575.5 | 41 | 376.7 | 523.4 | 34.8 | 288.1 | 476.5 | 41.4 | 251.2 | 39.7 | 154.8 | 136.5 | 54.5 | 35.1 | 136.9 | 148.6 | 41.1
288 | 67 | 476.9 | 190.76 | 222.9874 | 163.8 | 163.3 | 190.9 | 183.5 | 327.5 | 19.4 | 21.5 | 38 | 2.7 | 251.3 | 3.4 | 32.6 | 25.6 | 539.2 | 822.4 | 34.5 | 54.7 | 657 | 766.9 | 580.1 | 41.6 | 378.5 | 521.7 | 35.6 | 287.9 | 481.6 | 42 | 253.6 | 40.2 | 156.4 | 137.7 | 54.9 | 35.5 | 137.5 | 149.6 | 41.6
289 | 68 | 474.1 | 189.64 | 221.6782 | 163.8 | 164.6 | 192 | 184.3 | 334.4 | 19.5 | 21.5 | 38.4 | 3.2 | 249.8 | 3.8 | 32.8 | 25.8 | 536.7 | 820.6 | 34.9 | 55.4 | 642.8 | 768.4 | 584.1 | 42.3 | 375.9 | 520.3 | 36.4 | 285 | 471.1 | 42.5 | 254.3 | 40.6 | 157.6 | 138.8 | 55.5 | 35.9 | 138.1 | 150.5 | 42.2
290 | 69 | 473.7 | 189.48 | 221.4912 | 163.3 | 165.6 | 194.3 | 185.6 | 335.6 | 19.5 | 21.5 | 38.7 | 2.9 | 240 | 3.7 | 33 | 26 | 521.9 | 790.6 | 35.2 | 56 | 624.1 | 751.4 | 583.7 | 43 | 371.5 | 502.8 | 37.2 | 286.1 | 461.6 | 42.9 | 255 | 41.1 | 159 | 140 | 56.3 | 36.4 | 138.7 | 151.4 | 43
291 | 70 | 474.5 | 189.8 | 221.8653 | 163.7 | 166.8 | 196.6 | 186.4 | 334.9 | 19.6 | 21.5 | 39 | 2.8 | 230 | 3.7 | 33.2 | 26.2 | 507.7 | 791.4 | 35.5 | 56.6 | 603 | 737.2 | 583.7 | 43.7 | 364.7 | 488.1 | 38 | 280.7 | 444.4 | 43.1 | 253.6 | 41.6 | 159.5 | 141.7 | 57 | 36.8 | 139.3 | 152.1 | 43.4
292 | 71 | 473.7 | 189.48 | 221.4912 | 164.4 | 167.9 | 198.7 | 187.2 | 334.9 | 19.6 | 21.5 | 39.3 | 2.5 | 232 | 3.7 | 33.4 | 26.5 | 500.7 | 788.8 | 35.9 | 57.2 | 595.7 | 726.4 | 586.4 | 44.4 | 361.8 | 480.4 | 38.8 | 276.7 | 438.6 | 43.4 | 254.2 | 42.1 | 160.8 | 142.7 | 57.8 | 37.2 | 140 | 153.1 | 43.6
293 | 72 | 475.6 | 190.24 | 222.3796 | 165.9 | 169.1 | 199.9 | 187.7 | 333.2 | 19.6 | 21.5 | 39.5 | 2.6 | 226.6 | 3.7 | 33.6 | 26.7 | 492.8 | 775.8 | 36.2 | 57.6 | 587.9 | 733.5 | 589.4 | 45 | 360.5 | 479.9 | 39.6 | 275.4 | 434.3 | 43.6 | 255.4 | 42.6 | 161.8 | 143.9 | 58.5 | 37.7 | 140.8 | 154.4 | 44
294 | 73 | 475 | 190 | 222.0991 | 167.3 | 169.8 | 201.5 | 188.3 | 329.4 | 19.6 | 21.5 | 39.9 | 2.9 | 233.5 | 3.3 | 33.8 | 27 | 489.5 | 783.8 | 36.5 | 58 | 584.7 | 738.3 | 596.2 | 45.7 | 363.1 | 485.4 | 40.3 | 276.9 | 444 | 44.1 | 258.7 | 43.1 | 162.7 | 145.1 | 58.9 | 38.1 | 141.8 | 155.3 | 44.7
295 | 74 | 475.2 | 190.08 | 222.1926 | 167.6 | 169 | 203 | 188.6 | 329.6 | 19.6 | 21.5 | 40.2 | 3 | 248.8 | 3.1 | 33.9 | 27.2 | 485.1 | 779.6 | 36.8 | 58.3 | 589.3 | 737 | 600 | 46.3 | 361.8 | 485.2 | 41.1 | 280 | 447.3 | 44.5 | 262 | 43.7 | 163.2 | 146.2 | 59.4 | 38.5 | 142.5 | 155.8 | 45.3
296 | 75 | 476 | 190.4 | 222.5666 | 167.6 | 168.3 | 203.6 | 189 | 325.3 | 19.6 | 21.5 | 40.4 | 3.3 | 257.8 | 2.9 | 34.1 | 27.4 | 474.7 | 773.8 | 37.1 | 58.7 | 574 | 756.8 | 603.6 | 47 | 360.7 | 480.8 | 41.9 | 280.2 | 443.7 | 44.9 | 262.9 | 44.2 | 163.5 | 147 | 60 | 38.9 | 143 | 156.5 | 45.5
297 | 76 | 475.8 | 190.32 | 222.4731 | 168.2 | 168.2 | 203.9 | 189.3 | 322.1 | 19.6 | 21.5 | 40.6 | 3.3 | 258.1 | 2.7 | 34.3 | 27.7 | 469.1 | 779.6 | 37.3 | 59 | 570.5 | 769.1 | 608.4 | 47.6 | 359.6 | 474.4 | 42.7 | 285.1 | 454.8 | 45.3 | 265.1 | 44.7 | 164.2 | 147.8 | 60.5 | 39.3 | 143.6 | 157.4 | 45.8
298 | 77 | 475.4 | 190.16 | 222.2861 | 169.3 | 169.3 | 203.3 | 189.7 | 321.6 | 19.6 | 21.5 | 40.8 | 3.2 | 241.8 | 2.6 | 34.4 | 27.9 | 471.9 | 787.9 | 37.6 | 59.2 | 589.9 | 785.2 | 614.4 | 48.2 | 357.7 | 478.7 | 43.5 | 289.7 | 457.5 | 45.8 | 266.3 | 45.2 | 165.1 | 149 | 61.3 | 39.7 | 144.2 | 158.6 | 46.3
299 | 78 | 474.2 | 189.68 | 221.725 | 169.8 | 169.3 | 202.9 | 190.2 | 320 | 19.7 | 21.4 | 40.9 | 3 | 226.5 | 2.8 | 34.6 | 28.2 | 472.2 | 791.5 | 37.9 | 59.5 | 598.7 | 774.9 | 616.8 | 48.8 | 358.3 | 473.3 | 44.3 | 294.7 | 460.2 | 46.2 | 268.6 | 45.8 | 165.6 | 150 | 61.5 | 40.1 | 145 | 159.6 | 46.9
300 | 79 | 473.7 | 189.48 | 221.4912 | 170.2 | 169.6 | 202.9 | 190.5 | 316.7 | 19.7 | 21.4 | 41 | 3 | 243 | 3.1 | 34.8 | 28.4 | 471.4 | 794.8 | 38.1 | 59.8 | 583.8 | 784.1 | 620.2 | 49.4 | 358.9 | 467.4 | 45.1 | 298.7 | 469.4 | 46.7 | 272 | 46.3 | 166.1 | 150.8 | 62.3 | 40.5 | 145.7 | 160.5 | 47.5
301 | 80 | 474.9 | 189.96 | 222.0523 | 170.7 | 171 | 203.1 | 190.4 | 315.8 | 19.7 | 21.4 | 41.2 | 3 | 275 | 3.2 | 34.9 | 28.7 | 470.9 | 796.1 | 38.4 | 60 | 607.1 | 789.3 | 623 | 50 | 360.8 | 479.5 | 45.8 | 306.4 | 484.5 | 47.4 | 276.4 | 46.8 | 166.4 | 151.5 | 63.3 | 40.9 | 146.5 | 161.1 | 48
302 | 81 | 475.6 | 190.24 | 222.3796 | 171.8 | 171.7 | 202.7 | 190 | 315.8 | 19.7 | 21.4 | 41.4 | 3 | 252.9 | 3.5 | 35 | 28.9 | 478.2 | 796.6 | 38.7 | 60.3 | 613.8 | 788.4 | 626.1 | 50.6 | 365 | 492.8 | 46.6 | 310.4 | 500.9 | 48.1 | 279.9 | 47.3 | 166.7 | 152.6 | 64.1 | 41.3 | 147.6 | 161.7 | 48.6
303 | 82 | 474.8 | 189.92 | 222.0055 | 172.8 | 172.8 | 202.3 | 190.2 | 316.4 | 19.7 | 21.4 | 41.7 | 3.2 | 226.5 | 4.1 | 35.2 | 29.2 | 480.8 | 788.1 | 38.9 | 60.5 | 598.5 | 784.2 | 627.1 | 51.2 | 376.5 | 497.1 | 47.4 | 316.1 | 506.1 | 48.9 | 283.3 | 47.7 | 167.2 | 154.2 | 66 | 41.7 | 148.7 | 162.9 | 48.8
304 | 83 | 476.2 | 190.48 | 222.6601 | 173.1 | 173.7 | 202.1 | 190.7 | 321.6 | 19.7 | 21.4 | 41.9 | 3.3 | 234.3 | 4.7 | 35.3 | 29.4 | 485.9 | 782.8 | 39.2 | 60.7 | 580.9 | 780.9 | 628.7 | 51.7 | 381.9 | 492.1 | 48.2 | 320.5 | 510.5 | 49.4 | 284.5 | 48.2 | 167.8 | 155.4 | 67.1 | 42.1 | 150.2 | 163.3 | 49.3
305 | 84 | 474.3 | 189.72 | 221.7717 | 173.7 | 174.9 | 202.1 | 191.4 | 324.7 | 19.8 | 21.4 | 42 | 3.5 | 244.1 | 5.3 | 35.5 | 29.6 | 477.4 | 761.3 | 39.5 | 61 | 563.6 | 779.9 | 632.3 | 52.3 | 379.9 | 481.5 | 48.9 | 328.6 | 507.9 | 49.8 | 286 | 48.6 | 168.3 | 156.4 | 67.8 | 42.5 | 151.3 | 163.9 | 49.9
306 | 85 | 476.5 | 190.6 | 222.8004 | 174.6 | 174.9 | 202.2 | 192.4 | 328.1 | 19.8 | 21.4 | 42.1 | 3.1 | 244.3 | 5.1 | 35.7 | 29.9 | 463.2 | 734.8 | 39.7 | 61.3 | 548.8 | 784.9 | 636.2 | 52.9 | 373.3 | 467 | 49.7 | 335.5 | 501.7 | 50 | 286.8 | 49.1 | 168.8 | 157.7 | 68.1 | 42.9 | 152.1 | 165.1 | 50.6
307 | 86 | 475.9 | 190.36 | 222.5199 | 174.8 | 174.5 | 202 | 193.9 | 329.9 | 19.9 | 21.4 | 42.2 | 3.3 | 228.7 | 5 | 35.8 | 30.1 | 449.3 | 736.4 | 40 | 61.5 | 539.4 | 797.8 | 639.4 | 53.4 | 367.3 | 456.7 | 50.4 | 338.1 | 491.5 | 50.1 | 286.4 | 49.5 | 169.5 | 158.3 | 67.6 | 43.3 | 153.3 | 165.8 | 51
308 | 87 | 476.7 | 190.68 | 222.8939 | 174.4 | 174.4 | 201.7 | 194.5 | 322.2 | 20 | 21.4 | 42.2 | 3.1 | 231.2 | 5 | 35.9 | 30.3 | 455.2 | 751.5 | 40.3 | 61.7 | 540.2 | 809.7 | 645 | 54 | 363.7 | 461.8 | 51.2 | 336.6 | 486.4 | 50.1 | 288.2 | 49.9 | 169.9 | 159.4 | 68.1 | 43.7 | 154.3 | 166.9 | 51.2
309 | 88 | 475.5 | 190.2 | 222.3328 | 174 | 174.2 | 200.7 | 195 | 318 | 20 | 21.4 | 42.5 | 2.7 | 245.5 | 5.4 | 36.1 | 30.6 | 473 | 763.5 | 40.5 | 61.9 | 561.8 | 808 | 650.6 | 54.6 | 362.9 | 467.8 | 51.9 | 343.2 | 492 | 50.3 | 293.1 | 50.4 | 170.4 | 160.2 | 68.9 | 44.2 | 155.1 | 167.9 | 51.7
310 | 89 | 476.4 | 190.56 | 222.7537 | 175.3 | 174.3 | 200.5 | 195.7 | 319 | 20.1 | 21.4 | 42.7 | 2.9 | 231.1 | 5.2 | 36.2 | 30.8 | 490.6 | 778.5 | 40.8 | 62 | 563.9 | 808 | 653 | 55.1 | 366.6 | 486.3 | 52.7 | 346.2 | 496.4 | 50.5 | 297.9 | 50.8 | 170.8 | 160.7 | 69 | 44.6 | 155.8 | 168 | 52.1
311 | 90 | 473.1 | 189.24 | 221.2107 | 176.4 | 174.8 | 200.3 | 195.8 | 324.3 | 20.2 | 21.4 | 42.9 | 3.3 | 232.9 | 5.6 | 36.3 | 31.1 | 497.7 | 785.6 | 41 | 62.2 | 584.1 | 815.6 | 655.8 | 55.7 | 371.2 | 488.2 | 53.4 | 360.2 | 515.3 | 50.8 | 303 | 51.2 | 171.3 | 161.3 | 69.8 | 45 | 156.3 | 168 | 52.7
312 | 91 | 473.6 | 189.44 | 221.4444 | 176.4 | 174.5 | 199.6 | 195.9 | 327.3 | 20.2 | 21.4 | 43 | 2.9 | 244.1 | 6.3 | 36.5 | 31.3 | 511.7 | 790.1 | 41.3 | 62.5 | 602.9 | 813.4 | 659.4 | 56.3 | 370.9 | 485.2 | 54.2 | 368.2 | 523.9 | 51 | 307.2 | 51.6 | 171.7 | 162.8 | 72.3 | 45.5 | 157.4 | 168.4 | 53.3
313 | 92 | 473.6 | 189.44 | 221.4444 | 176.3 | 174.2 | 199.4 | 195.6 | 326.9 | 20.3 | 21.4 | 43.2 | 3 | 239.3 | 6.4 | 36.6 | 31.6 | 515 | 796.9 | 41.6 | 62.8 | 609.9 | 813.2 | 663.8 | 56.8 | 370.5 | 487.9 | 54.9 | 372.7 | 523.5 | 51.2 | 309.5 | 51.9 | 172.4 | 163.5 | 72.8 | 46 | 158.2 | 169 | 53.8
314 | 93 | 472.9 | 189.16 | 221.1171 | 175.9 | 173.6 | 199 | 195.4 | 326.5 | 20.3 | 21.4 | 43.3 | 3.3 | 234.3 | 6.7 | 36.8 | 31.8 | 518.1 | 796.4 | 41.9 | 63.2 | 607 | 815.8 | 665.7 | 57.4 | 369.6 | 487.4 | 55.6 | 373.7 | 522.4 | 51.3 | 313 | 52.4 | 172.9 | 164.8 | 73.7 | 46.5 | 158.8 | 170 | 54.3
315 | 94 | 473.2 | 189.28 | 221.2574 | 176.6 | 172.8 | 198.6 | 195.6 | 326.9 | 20.3 | 21.4 | 43.4 | 3.1 | 241 | 6.8 | 36.9 | 32.1 | 513.3 | 787.3 | 42.1 | 63.5 | 606 | 810.8 | 668.6 | 58 | 368.8 | 492.3 | 56.3 | 374.5 | 521.5 | 51.4 | 315.1 | 52.8 | 173.1 | 165.2 | 74.3 | 46.9 | 159.5 | 170.9 | 54.7
316 | 95 | 474.9 | 189.96 | 222.0523 | 177.3 | 173.5 | 198 | 195.4 | 323.9 | 20.3 | 21.3 | 43.5 | 3 | 241.8 | 6.6 | 37 | 32.3 | 509.4 | 799.6 | 42.4 | 63.8 | 600.2 | 814.7 | 670.5 | 58.6 | 369.5 | 495.8 | 57 | 372.9 | 517.5 | 51.6 | 316.9 | 53.2 | 173.6 | 165.6 | 74.2 | 47.4 | 160.3 | 171.5 | 55
317 | 96 | 474.5 | 189.8 | 221.8653 | 177.1 | 173 | 197.6 | 194.8 | 319.8 | 20.2 | 21.3 | 43.7 | 2.7 | 257 | 6.5 | 37.1 | 32.6 | 496.8 | 804.6 | 42.7 | 64.1 | 587.3 | 825 | 674.7 | 59.3 | 367.5 | 488 | 57.8 | 366.4 | 506.5 | 51.6 | 316.5 | 53.6 | 174.6 | 166.5 | 74.7 | 47.8 | 161.6 | 171.7 | 55.6
318 | 97 | 474.9 | 189.96 | 222.0523 | 178.3 | 172.9 | 198 | 195 | 317.2 | 20.2 | 21.3 | 43.8 | 3.2 | 248.9 | 6.5 | 37.3 | 32.8 | 491.6 | 814.4 | 43.1 | 64.4 | 570.6 | 833.7 | 677.1 | 59.9 | 366.3 | 489 | 58.5 | 362.2 | 503 | 51.7 | 316.3 | 54 | 175 | 167.5 | 75.7 | 48.3 | 162.8 | 171.8 | 56.3
319 | 98 | 475.2 | 190.08 | 222.1926 | 179.3 | 171.9 | 197.9 | 195.1 | 318.7 | 20.2 | 21.3 | 43.9 | 3.5 | 248.2 | 6.6 | 37.4 | 33.1 | 494.3 | 808 | 43.4 | 64.6 | 563.7 | 834.9 | 678 | 60.6 | 369.4 | 489.5 | 59.2 | 361 | 510.4 | 51.9 | 318 | 54.4 | 175.2 | 168.7 | 77.3 | 48.7 | 163.7 | 171.8 | 56.6
320 | 99 | 475.5 | 190.2 | 222.3328 | 180.5 | 172.2 | 197.2 | 194.8 | 321.4 | 20.2 | 21.3 | 44.1 | 3.3 | 273.3 | 6 | 37.5 | 33.3 | 489.9 | 804.4 | 43.7 | 64.9 | 561.9 | 831.8 | 680.6 | 61.3 | 369.6 | 483.9 | 59.9 | 360.1 | 510.2 | 52.1 | 319.1 | 54.8 | 175.4 | 169.3 | 78.2 | 49.2 | 164.2 | 172.1 | 57.4
321 | 100 | 475.2 | 190.08 | 222.1926 | 180.7 | 171.4 | 197.3 | 194.8 | 321.3 | 20.2 | 21.3 | 44.3 | 3.4 | 272.4 | 5.5 | 37.6 | 33.6 | 494.2 | 802.2 | 44 | 65.2 | 557.8 | 842.1 | 683.1 | 62 | 373.6 | 489.9 | 60.6 | 357.2 | 516.5 | 52.4 | 321.6 | 55.2 | 175.8 | 170.6 | 78.9 | 49.6 | 164.7 | 172.5 | 57.8
322 | 101 | 475 | 190 | 222.0991 | 181.1 | 170.3 | 197.7 | 194.8 | 321.9 | 20.3 | 21.3 | 44.5 | 3.3 | 262.4 | 4.9 | 37.7 | 33.8 | 504.2 | 814.1 | 44.4 | 65.5 | 553.3 | 822.3 | 682.5 | 62.8 | 378.2 | 501.6 | 61.2 | 355.6 | 515.8 | 52.6 | 324.4 | 55.6 | 176 | 171.5 | 79.4 | 50.1 | 165.6 | 172.7 | 58.1
323 | 102 | 476.1 | 190.44 | 222.6134 | 181.8 | 170.1 | 197.9 | 194.7 | 322.1 | 20.3 | 21.3 | 44.7 | 3.6 | 245.2 | 4.9 | 37.8 | 34.1 | 499.5 | 819.5 | 44.7 | 65.8 | 547.2 | 800.2 | 682.9 | 63.5 | 380.1 | 504.6 | 61.9 | 349.9 | 501.2 | 52.9 | 325.4 | 55.9 | 176.3 | 171.8 | 79.3 | 50.5 | 165.8 | 172.9 | 58.4
324 | 103 | 476 | 190.4 | 222.5666 | 180.9 | 170.9 | 198.4 | 194.5 | 321.7 | 20.4 | 21.3 | 44.8 | 3.6 | 237.1 | 4.9 | 38 | 34.3 | 505.9 | 828.3 | 45.1 | 66.2 | 537 | 792.4 | 687.5 | 64.4 | 379.8 | 511.9 | 62.6 | 345 | 491.5 | 53 | 325.7 | 56.3 | 176.7 | 172.2 | 79.3 | 50.9 | 165.9 | 173 | 59.1
325 | 104 | 476.4 | 190.56 | 222.7537 | 180.3 | 171.5 | 198.8 | 195 | 318.4 | 20.5 | 21.3 | 44.9 | 3.6 | 240.6 | 5 | 38.1 | 34.6 | 516.5 | 825.4 | 45.4 | 66.5 | 551.2 | 785.7 | 689.2 | 65.3 | 383 | 519.6 | 63.3 | 345.8 | 493.6 | 53.2 | 328.9 | 56.7 | 177.1 | 172.9 | 80 | 51.4 | 166.4 | 173.3 | 59.6
326 | 105 | 475.7 | 190.28 | 222.4264 | 179.5 | 171.3 | 199.8 | 194.6 | 319.6 | 20.5 | 21.3 | 45.1 | 3.4 | 254.8 | 5 | 38.2 | 34.8 | 513.1 | 820.1 | 45.8 | 66.9 | 551.2 | 781.5 | 690 | 66.3 | 382 | 505.8 | 64 | 345.1 | 484 | 53.4 | 329.9 | 57.1 | 177.2 | 172.9 | 80.5 | 51.8 | 167 | 173.5 | 60.1
327 | 106 | 477.3 | 190.92 | 223.1745 | 179.8 | 172.8 | 200.6 | 194.7 | 317.1 | 20.5 | 21.3 | 45.3 | 3 | 254.3 | 4.9 | 38.4 | 35.1 | 506.5 | 820.1 | 46.2 | 67.3 | 542.9 | 776.3 | 691.3 | 67.6 | 381.1 | 501.3 | 64.7 | 343.4 | 484.1 | 53.7 | 330.9 | 57.5 | 177.6 | 173.1 | 81.3 | 52.3 | 167.6 | 173.9 | 60.6
328 | 107 | 476.9 | 190.76 | 222.9874 | 180.4 | 173.7 | 201 | 194.5 | 316.9 | 20.5 | 21.3 | 45.5 | 2.8 | 253.7 | 4.8 | 38.5 | 35.3 | 503.3 | 830.7 | 46.5 | 67.7 | 525.3 | 773.7 | 692.6 | 69.2 | 381.2 | 505.5 | 65.3 | 338.5 | 479.6 | 53.9 | 331.8 | 57.9 | 178.9 | 173.6 | 81.6 | 52.7 | 168 | 174.3 | 61
329 | 108 | 476.7 | 190.68 | 222.8939 | 180.3 | 174.1 | 202.1 | 194.2 | 315.2 | 20.6 | 21.3 | 45.7 | 2.9 | 271.7 | 4.2 | 38.6 | 35.6 | 500.2 | 819.2 | 46.9 | 68.1 | 518.9 | 776.4 | 694.8 | 71.1 | 380.4 | 506.9 | 66 | 338.5 | 486.7 | 54 | 333.2 | 58.3 | 179.2 | 174 | 81.4 | 53.2 | 168.1 | 174.6 | 61.7
330 | 109 | 477.4 | 190.96 | 223.2212 | 180.6 | 174 | 202.9 | 194.3 | 314.8 | 20.7 | 21.3 | 45.9 | 2.8 | 265.9 | 3.8 | 38.8 | 35.8 | 503.4 | 816.2 | 47.3 | 68.4 | 512.6 | 775 | 697.4 | 73.4 | 379.2 | 498.6 | 66.7 | 335.4 | 477.8 | 54.2 | 333.8 | 58.7 | 179.5 | 175.1 | 82.1 | 53.6 | 168.4 | 175.1 | 62.1
331 | 110 | 477.1 | 190.84 | 223.081 | 181 | 174.3 | 202.4 | 193.8 | 313.7 | 20.7 | 21.3 | 46.1 | 2.3 | 243.3 | 4.5 | 38.9 | 36.1 | 501.9 | 807.6 | 47.6 | 68.8 | 509.6 | 789.3 | 698 | 75.8 | 376.7 | 488.4 | 67.3 | 334.6 | 479.4 | 54.4 | 334.9 | 59.1 | 179.9 | 175.4 | 82.4 | 54.1 | 168.6 | 175.2 | 62.5
332 | 111 | 477.3 | 190.92 | 223.1745 | 180.7 | 175.6 | 202.4 | 194.2 | 311.9 | 20.8 | 21.2 | 46.3 | 2.5 | 235.8 | 5.5 | 39 | 36.3 | 493.4 | 811.9 | 48 | 69.2 | 508.9 | 797.6 | 700 | 78.7 | 376.2 | 489.2 | 68 | 334.6 | 478.1 | 54.6 | 336.5 | 59.5 | 180 | 175.9 | 83.3 | 54.5 | 169.1 | 175.7 | 62.8
333 | 112 | 477.1 | 190.84 | 223.081 | 180.8 | 175.9 | 203.9 | 194.6 | 311.9 | 20.9 | 21.2 | 46.5 | 2.1 | 246.3 | 5.4 | 39.1 | 36.6 | 493.8 | 808.1 | 48.4 | 69.5 | 509.9 | 796.9 | 700.2 | 81.2 | 377 | 487.8 | 68.6 | 334.5 | 478.4 | 54.8 | 338.4 | 59.9 | 180.3 | 177.2 | 84.5 | 54.9 | 169.7 | 175.8 | 63.4
334 | 113 | 476.4 | 190.56 | 222.7537 | 180.6 | 175.6 | 204.4 | 195 | 311.6 | 21.1 | 21.2 | 46.6 | 2 | 246.4 | 5.1 | 39.2 | 36.9 | 486.2 | 796.8 | 48.8 | 69.8 | 500.1 | 790.8 | 698.9 | 83 | 374.1 | 478.5 | 69.3 | 330.8 | 466.8 | 55 | 337.4 | 60.3 | 180.6 | 177.6 | 84.6 | 55.4 | 169.9 | 176 | 63.6
335 | 114 | 477.6 | 191.04 | 223.3148 | 179.9 | 175.3 | 206 | 194.9 | 309.6 | 21.2 | 21.2 | 46.6 | 2.1 | 248 | 5.1 | 39.3 | 37.1 | 472.7 | 791.4 | 49.1 | 70.2 | 492.2 | 800.2 | 699.7 | 84.2 | 370.8 | 477.6 | 69.9 | 327.7 | 461.9 | 55.1 | 337.8 | 60.6 | 180.7 | 177.7 | 85.2 | 55.8 | 170.3 | 176.2 | 63.8
336 | 115 | 478.4 | 191.36 | 223.6888 | 179.7 | 175.6 | 206.3 | 195.1 | 306 | 21.2 | 21.2 | 46.8 | 2.8 | 243.1 | 5.6 | 39.5 | 37.4 | 466.6 | 797.5 | 49.5 | 70.5 | 495.7 | 800 | 699.9 | 85 | 368.8 | 477.9 | 70.6 | 326.2 | 457.5 | 55.2 | 339.2 | 61 | 180.5 | 177.6 | 85.6 | 56.2 | 170.6 | 176.5 | 64.4
337 | 116 | 477.3 | 190.92 | 223.1745 | 180.5 | 175.1 | 205.9 | 195.9 | 305.5 | 21.2 | 21.2 | 47 | 3.6 | 252.1 | 5.7 | 39.6 | 37.6 | 463.1 | 785 | 49.9 | 70.7 | 501.2 | 809.4 | 701.1 | 85.4 | 369 | 482.4 | 71.2 | 325.7 | 463.3 | 55.3 | 340.8 | 61.4 | 180.6 | 177.8 | 85.4 | 56.6 | 171.5 | 176.5 | 64.9
338 | 117 | 477.1 | 190.84 | 223.081 | 181.1 | 174.6 | 205.7 | 196.4 | 304.5 | 21.3 | 21.2 | 47.1 | 3.1 | 235.6 | 4.6 | 39.7 | 37.9 | 463.5 | 792.5 | 50.3 | 71 | 496.6 | 820.8 | 701.6 | 85.6 | 367.2 | 475.2 | 71.8 | 325 | 464 | 55.6 | 341.1 | 61.8 | 180.6 | 177.8 | 85.6 | 57 | 171.7 | 176.7 | 65.3
339 | 118 | 477.4 | 190.96 | 223.2212 | 181.5 | 173.9 | 205.2 | 196.3 | 302.3 | 21.3 | 21.2 | 47.2 | 2.8 | 240 | 3.6 | 39.8 | 38.1 | 463.8 | 799.8 | 50.7 | 71.3 | 503.8 | 806.3 | 701.7 | 86 | 364.9 | 474.2 | 72.5 | 324.8 | 474.1 | 55.9 | 342.7 | 62.2 | 180.4 | 177.8 | 86.7 | 57.4 | 172.1 | 177 | 65.9
340 | 119 | 477.2 | 190.88 | 223.1277 | 182.1 | 173.3 | 204.2 | 196.4 | 302.7 | 21.3 | 21.2 | 47.3 | 2.9 | 262.1 | 3.5 | 39.9 | 38.4 | 471.4 | 804.1 | 51.1 | 71.5 | 494.8 | 799.9 | 703.5 | 86.2 | 363 | 468.6 | 73.1 | 325.7 | 476.3 | 56.2 | 344.3 | 62.5 | 180.3 | 178 | 88.2 | 57.8 | 172.6 | 177.3 | 66.2
341 | 120 | 478.1 | 191.24 | 223.5485 | 183.2 | 173.1 | 204.6 | 196.6 | 303.3 | 21.4 | 21.2 | 47.5 | 3.2 | 264.7 | 3.6 | 40 | 38.6 | 468.5 | 801.3 | 51.4 | 71.8 | 498.4 | 793.1 | 704.6 | 86.3 | 362.7 | 467.8 | 73.8 | 324.9 | 470.4 | 56.5 | 344.8 | 62.8 | 180.2 | 178.5 | 89.1 | 58.3 | 172.6 | 177.8 | 66.5
342 | 121 | 478.1 | 191.24 | 223.5485 | 183.7 | 173.5 | 205.2 | 195.8 | 304.2 | 21.4 | 21.2 | 47.7 | 3.6 | 219.4 | 3.3 | 40.1 | 38.9 | 473.9 | 815.2 | 51.8 | 72.1 | 495.2 | 793.8 | 705.6 | 86.4 | 367.2 | 476.4 | 74.4 | 322.3 | 471 | 56.8 | 345.7 | 63.2 | 180.1 | 178.7 | 89.7 | 58.7 | 172.8 | 177.9 | 66.8
343 | 122 | 478.2 | 191.28 | 223.5953 | 184.1 | 174.3 | 205.6 | 194.8 | 309.3 | 21.4 | 21.2 | 47.9 | 3.6 | 210.1 | 3.1 | 40.2 | 39.2 | 484.4 | 821.2 | 52.2 | 72.4 | 496.2 | 794.1 | 707.4 | 86.6 | 371.3 | 488.3 | 75.1 | 322.6 | 475.4 | 57.2 | 348.1 | 63.5 | 180.1 | 179.4 | 90 | 59.1 | 173 | 178 | 67.5
344 | 123 | 477.8 | 191.12 | 223.4083 | 183.6 | 176.3 | 205.5 | 194.6 | 310.6 | 21.4 | 21.2 | 48.1 | 3.4 | 217.9 | 3.2 | 40.4 | 39.4 | 488.2 | 819 | 52.6 | 72.7 | 502.8 | 793.8 | 708.2 | 87.1 | 375.6 | 500.1 | 75.7 | 322.9 | 477.2 | 57.7 | 350.8 | 63.8 | 180.6 | 180.7 | 90.5 | 59.5 | 173.2 | 178.4 | 67.7
345 | 124 | 477.5 | 191 | 223.268 | 182.2 | 178.4 | 205.7 | 195.3 | 315.5 | 21.4 | 21.2 | 48.2 | 3.2 | 229 | 3.5 | 40.5 | 39.7 | 494.6 | 817.6 | 53 | 73 | 499.8 | 787.2 | 708.4 | 88.1 | 379.8 | 517.7 | 76.4 | 321.3 | 474.7 | 58.2 | 352.9 | 64.2 | 181.1 | 181.2 | 90.5 | 59.9 | 173.5 | 178.3 | 68.4
346 | 125 | 477.6 | 191.04 | 223.3148 | 181.8 | 179.1 | 206.5 | 196 | 319.3 | 21.5 | 21.2 | 48.3 | 3.4 | 233.4 | 4 | 40.6 | 39.9 | 496.1 | 816.5 | 53.4 | 73.5 | 491.5 | 759.7 | 707.7 | 89.8 | 382.2 | 518.3 | 77 | 320.8 | 469.3 | 58.7 | 354.8 | 64.5 | 181.3 | 182 | 90.4 | 60.3 | 174 | 178.4 | 68.7
347 | 126 | 477.5 | 191 | 223.268 | 181.9 | 180.3 | 207.3 | 196.2 | 322.1 | 21.5 | 21.2 | 48.4 | 3.4 | 231.5 | 3.8 | 40.7 | 40.2 | 504.4 | 818.7 | 53.7 | 74 | 486.7 | 754.7 | 707.3 | 91.2 | 393.6 | 535.2 | 77.6 | 320.2 | 479.6 | 59.3 | 358.9 | 64.8 | 181.9 | 182.2 | 91.3 | 60.7 | 174.4 | 178.2 | 69
348 | 127 | 477.5 | 191 | 223.268 | 182.4 | 181.6 | 207.8 | 196.2 | 324.9 | 21.5 | 21.2 | 48.5 | 3.4 | 242.7 | 3.7 | 40.8 | 40.4 | 516.3 | 820.7 | 54.1 | 74.6 | 491.7 | 748.5 | 709.8 | 92.4 | 400.4 | 550.7 | 78.3 | 321.8 | 479.6 | 59.9 | 361.9 | 65.1 | 182.3 | 182.3 | 92 | 61.1 | 174.5 | 178.5 | 69.3
349 | 128 | 477.2 | 190.88 | 223.1277 | 183.5 | 181.9 | 207.9 | 196.2 | 329.5 | 21.6 | 21.2 | 48.7 | 2.9 | 265.5 | 3.9 | 41 | 40.7 | 520.7 | 820.6 | 54.5 | 75.2 | 497.8 | 745 | 708 | 93.6 | 414.2 | 557.9 | 78.9 | 326.3 | 488 | 60.6 | 365.8 | 65.5 | 183.2 | 182.8 | 92.9 | 61.6 | 174.5 | 178.9 | 69.6
350 | 129 | 477.8 | 191.12 | 223.4083 | 184.6 | 183 | 209.3 | 196.7 | 332.6 | 21.7 | 21.2 | 48.9 | 3 | 268.4 | 3.8 | 41.1 | 40.9 | 506.6 | 818.3 | 54.9 | 75.9 | 487.9 | 754.9 | 707.6 | 94.7 | 415.4 | 554.7 | 79.6 | 328 | 482.7 | 61.1 | 366.1 | 65.8 | 184 | 183.1 | 93.9 | 62 | 174.6 | 179.5 | 70
351 | 130 | 477.8 | 191.12 | 223.4083 | 184.9 | 185.3 | 210 | 197 | 328.5 | 21.7 | 21.2 | 49 | 3.1 | 231.7 | 3.6 | 41.2 | 41.1 | 501.4 | 827.4 | 55.3 | 76.6 | 496.9 | 761.6 | 708.3 | 95.5 | 420.8 | 557.9 | 80.2 | 329.5 | 479.8 | 61.3 | 366.9 | 66.1 | 184.7 | 183.4 | 94.6 | 62.4 | 174.8 | 180.2 | 70.5
352 | 131 | 477.8 | 191.12 | 223.4083 | 185.2 | 187.1 | 210.9 | 197.3 | 330.1 | 21.8 | 21.2 | 49.1 | 3.4 | 225.5 | 4 | 41.3 | 41.4 | 503.5 | 830.7 | 55.6 | 77.3 | 492.8 | 770.8 | 710.9 | 96.2 | 420.8 | 559.1 | 80.8 | 328.3 | 473 | 61.5 | 367.9 | 66.5 | 185.4 | 183.5 | 94.9 | 62.8 | 175 | 180.8 | 70.9
353 | 132 | 477 | 190.8 | 223.0342 | 184.3 | 188.2 | 211.6 | 197.9 | 331.6 | 21.8 | 21.2 | 49.3 | 3.4 | 258.2 | 4.2 | 41.4 | 41.6 | 505.1 | 830.6 | 56 | 78 | 489.6 | 775.1 | 713.6 | 96.8 | 423.9 | 568.5 | 81.4 | 327.4 | 471.2 | 61.7 | 368.9 | 66.8 | 186.5 | 183.9 | 94.9 | 63.2 | 175.1 | 181.4 | 71.3
354 | 133 | 476.9 | 190.76 | 222.9874 | 184.8 | 188.8 | 211.2 | 198 | 336 | 21.9 | 21.1 | 49.5 | 3.3 | 266.4 | 3.9 | 41.5 | 41.8 | 507.7 | 828.3 | 56.4 | 78.6 | 502 | 788.3 | 713.7 | 97.2 | 422.1 | 560.1 | 82.1 | 330.5 | 475.6 | 62 | 370.7 | 67.2 | 187.5 | 184.2 | 95 | 63.6 | 175.4 | 181.9 | 71.7
355 | 134 | 477.1 | 190.84 | 223.081 | 185.2 | 188.5 | 211.2 | 198.4 | 336.4 | 21.9 | 21.1 | 49.6 | 2.8 | 245.7 | 4 | 41.6 | 42.1 | 520 | 824.5 | 56.8 | 79.3 | 508.3 | 803.6 | 715.3 | 97.4 | 423 | 549.8 | 82.7 | 333.4 | 483.3 | 62.2 | 373.3 | 67.6 | 188.4 | 184.7 | 95 | 63.9 | 175.9 | 182.3 | 72
356 | 135 | 475.1 | 190.04 | 222.1458 | 185.4 | 189 | 211.2 | 197.8 | 337.5 | 22 | 21.1 | 49.7 | 2.9 | 235.5 | 4.7 | 41.7 | 42.3 | 537.2 | 818.7 | 57.1 | 79.9 | 516 | 809.4 | 716.9 | 97.5 | 426.2 | 557.8 | 83.4 | 338.1 | 505.3 | 62.6 | 376.2 | 67.9 | 188.9 | 184.9 | 95.2 | 64.3 | 176.2 | 182.4 | 72.4
357 | 136 | 476.6 | 190.64 | 222.8472 | 186 | 188.6 | 210.6 | 198 | 339 | 22.1 | 21.1 | 49.7 | 2.9 | 242.9 | 5.1 | 41.8 | 42.5 | 543.7 | 814.9 | 57.5 | 80.5 | 551.4 | 807.8 | 718.1 | 97.5 | 428.6 | 566.3 | 84.3 | 340.3 | 520.2 | 63 | 379.9 | 68.3 | 189.3 | 185 | 95.4 | 64.7 | 176.7 | 182.4 | 72.8
358 | 137 | 476.7 | 190.68 | 222.8939 | 185.8 | 188.1 | 210.7 | 198.7 | 337.1 | 22.2 | 21.1 | 49.8 | 2.7 | 246.4 | 5.1 | 41.9 | 42.8 | 544.7 | 813.3 | 57.9 | 81.2 | 570.2 | 794.5 | 717 | 97.4 | 437 | 575.1 | 85.2 | 345.2 | 524.8 | 63.6 | 383.2 | 68.8 | 189.8 | 185.1 | 96 | 65 | 177.8 | 182.5 | 73.4
359 | 138 | 475.6 | 190.24 | 222.3796 | 186.3 | 186.5 | 211.5 | 199.5 | 336.9 | 22.2 | 21.1 | 49.9 | 2.6 | 246.3 | 4.8 | 42 | 43 | 539.7 | 807.1 | 58.3 | 81.9 | 568.1 | 802.5 | 717 | 97.2 | 441.1 | 583 | 85.9 | 346.2 | 522.1 | 64.3 | 386.4 | 69.2 | 190.2 | 185.1 | 96.9 | 65.4 | 178.1 | 182.5 | 73.8
360 | 139 | 476.2 | 190.48 | 222.6601 | 186.6 | 186 | 212.6 | 200.3 | 341 | 22.3 | 21.1 | 49.9 | 2.7 | 257.2 | 4.5 | 42.1 | 43.2 | 535 | 814.5 | 58.7 | 82.6 | 568.5 | 794.3 | 718.3 | 97.1 | 448.9 | 590.1 | 86.7 | 347.5 | 520.5 | 64.9 | 389.3 | 69.6 | 190.7 | 185.6 | 97.5 | 65.8 | 178.1 | 182.7 | 74
361 | 140 | 476.5 | 190.6 | 222.8004 | 187.3 | 186.7 | 212.8 | 200.2 | 340.7 | 22.3 | 21.1 | 50 | 3.3 | 252 | 4.5 | 42.2 | 43.4 | 532.6 | 816.4 | 59.1 | 83.3 | 559.2 | 785.3 | 717.9 | 96.9 | 454.8 | 585.7 | 87.4 | 345.8 | 509.9 | 65.7 | 389.7 | 70 | 191.3 | 186.1 | 98.1 | 66.1 | 178.1 | 182.9 | 74.3
362 | 141 | 476 | 190.4 | 222.5666 | 187.4 | 187.7 | 212.5 | 200.2 | 339.5 | 22.4 | 21.1 | 50.1 | 3.3 | 247.7 | 4.3 | 42.3 | 43.6 | 537.7 | 818.9 | 59.5 | 84.1 | 555.9 | 782.9 | 719.6 | 96.9 | 454.6 | 587.4 | 88.1 | 345.3 | 507.8 | 66.1 | 391.4 | 70.4 | 191.7 | 186.6 | 98.4 | 66.6 | 178.5 | 183.2 | 74.8
363 | 142 | 475.9 | 190.36 | 222.5199 | 188.3 | 189 | 213.1 | 200.2 | 340.3 | 22.5 | 21.1 | 50.2 | 2.9 | 259.5 | 5 | 42.4 | 43.9 | 531 | 819.6 | 59.9 | 84.8 | 541.2 | 783 | 719.7 | 96.8 | 455.3 | 586.5 | 88.7 | 344.8 | 500.5 | 66.4 | 393.1 | 70.8 | 192.2 | 186.9 | 99.6 | 67 | 179.6 | 183.4 | 75.3
364 | 143 | 477.6 | 191.04 | 223.3148 | 189.2 | 190.6 | 213.5 | 200.5 | 339.5 | 22.5 | 21.1 | 50.3 | 3.2 | 259.2 | 5.7 | 42.5 | 44.1 | 517.6 | 815.3 | 60.3 | 85.6 | 524.3 | 787.8 | 721.8 | 96.7 | 454.5 | 578.7 | 89.3 | 342.3 | 495.9 | 66.6 | 393.6 | 71.3 | 192.7 | 187.7 | 101 | 67.4 | 179.7 | 183.6 | 75.6
365 | 144 | 476.2 | 190.48 | 222.6601 | 189.6 | 190.9 | 213.4 | 201.2 | 342.7 | 22.4 | 21.1 | 50.4 | 3.4 | 260.9 | 5.9 | 42.6 | 44.3 | 508.7 | 800.1 | 60.7 | 86.4 | 511.5 | 801.3 | 721.8 | 96.6 | 449.1 | 567.9 | 89.9 | 341.8 | 493.2 | 67 | 394.3 | 71.7 | 192.8 | 187.9 | 101.6 | 67.8 | 179.9 | 184.1 | 75.8
366 | 145 | 476.5 | 190.6 | 222.8004 | 189.4 | 191.3 | 213.1 | 201.6 | 336.1 | 22.5 | 21.1 | 50.5 | 3.2 | 260.2 | 6.1 | 42.7 | 44.5 | 507.2 | 798.5 | 61.1 | 87 | 513.5 | 803.5 | 723 | 96.5 | 442.6 | 556.4 | 90.5 | 341.5 | 493.3 | 67.2 | 395 | 72.2 | 192.7 | 187.8 | 101.9 | 68.2 | 180 | 184.7 | 76.3
367 | 146 | 477.4 | 190.96 | 223.2212 | 189.1 | 189.4 | 212.7 | 202.6 | 333.1 | 22.7 | 21.1 | 50.7 | 3.2 | 260.5 | 6.5 | 42.8 | 44.8 | 498.9 | 780.9 | 61.6 | 87.7 | 512.8 | 803.7 | 721.7 | 96.4 | 435.7 | 538.8 | 91.1 | 339.6 | 485 | 67.3 | 394.1 | 72.6 | 192.5 | 187.8 | 101.9 | 68.6 | 180 | 185.3 | 76.6
368 | 147 | 476.7 | 190.68 | 222.8939 | 189.7 | 187.9 | 211.8 | 203.1 | 331.4 | 22.9 | 21.1 | 50.8 | 3.5 | 258.1 | 6.9 | 42.9 | 45 | 484.4 | 777.1 | 62 | 88.2 | 501.2 | 795.3 | 720.9 | 96.5 | 425.2 | 519.8 | 91.6 | 337.8 | 479.6 | 67.4 | 392.4 | 73 | 192.5 | 188 | 102.3 | 68.9 | 180.3 | 185.7 | 76.9
369 | 148 | 477.7 | 191.08 | 223.3615 | 190.3 | 187.3 | 211.2 | 202.6 | 332 | 23 | 21.1 | 50.9 | 3.6 | 250.7 | 7.1 | 43 | 45.2 | 472.3 | 763.3 | 62.4 | 88.7 | 500.3 | 810.8 | 720.7 | 96.6 | 416.2 | 502 | 92.2 | 334.6 | 473.6 | 67.6 | 391.1 | 73.4 | 192.3 | 188.1 | 102.6 | 69.3 | 180.5 | 186 | 77.4
370 | 149 | 476.9 | 190.76 | 222.9874 | 192.2 | 188.9 | 211.1 | 202.3 | 325.8 | 23.1 | 21.1 | 50.9 | 3.7 | 253.2 | 7.1 | 43.1 | 45.5 | 470.9 | 764.1 | 62.8 | 89.2 | 501.3 | 810.8 | 721.1 | 96.6 | 407.6 | 494.3 | 92.8 | 338.4 | 479 | 67.6 | 391.3 | 73.9 | 192 | 188.8 | 102.4 | 69.7 | 180.8 | 186.1 | 78.1
371 | 150 | 477.7 | 191.08 | 223.3615 | 194.3 | 189 | 210.8 | 203 | 322.7 | 23.1 | 21.1 | 51 | 3.7 | 252.7 | 6.9 | 43.2 | 45.7 | 472.4 | 771.9 | 63.2 | 89.5 | 498.8 | 803 | 721.3 | 96.6 | 401.9 | 491.5 | 93.4 | 332.7 | 467.8 | 67.6 | 390.6 | 74.2 | 192 | 188.8 | 102.9 | 70.1 | 180.8 | 185.9 | 78.4
372 | 151 | 478.1 | 191.24 | 223.5485 | 194.8 | 188 | 210.4 | 203.2 | 323 | 23.1 | 21.1 | 51.1 | 3.7 | 253.9 | 6.6 | 43.4 | 45.9 | 480 | 771.8 | 63.6 | 89.9 | 492.8 | 781.2 | 720.3 | 96.7 | 397.3 | 491.1 | 94 | 328.2 | 459.4 | 67.6 | 389.9 | 74.6 | 192 | 189 | 104.3 | 70.4 | 181.6 | 186 | 78.8
373 | 152 | 477.4 | 190.96 | 223.2212 | 195.7 | 186.8 | 210.2 | 203.3 | 324.2 | 23.2 | 21.1 | 51.2 | 3.5 | 252 | 6.6 | 43.5 | 46.2 | 474.5 | 772.1 | 64 | 90.2 | 502.9 | 765 | 718.8 | 96.8 | 394.7 | 483.4 | 94.6 | 323.4 | 450.4 | 67.9 | 389.3 | 75 | 192 | 189.5 | 105.2 | 70.8 | 182.6 | 186.1 | 79.5
374 | 153 | 477.8 | 191.12 | 223.4083 | 196.1 | 186.1 | 209.9 | 203.3 | 330.4 | 23.2 | 21 | 51.3 | 3.4 | 252.9 | 6.9 | 43.6 | 46.4 | 467.3 | 774.1 | 64.5 | 90.6 | 500.2 | 744.7 | 715.4 | 96.9 | 390.9 | 485.4 | 95.2 | 317.7 | 438.1 | 68.2 | 388.3 | 75.3 | 192.3 | 189.8 | 105.4 | 71.2 | 183.5 | 185.9 | 79.9
375 | 154 | 476.2 | 190.48 | 222.6601 | 196.4 | 186 | 209 | 203.2 | 337.5 | 23.3 | 21.1 | 51.4 | 3.4 | 249.2 | 6.6 | 43.7 | 46.6 | 464.7 | 783.5 | 64.9 | 90.9 | 499.1 | 749.9 | 715.8 | 97.2 | 387.6 | 483.6 | 95.8 | 312.2 | 429.6 | 68.3 | 387.8 | 75.7 | 193 | 190.3 | 105.6 | 71.5 | 183.6 | 186 | 80
376 | 155 | 476.2 | 190.48 | 222.6601 | 196.5 | 185.5 | 210.1 | 204.3 | 337.2 | 23.4 | 21.1 | 51.5 | 3.5 | 252.4 | 6.1 | 43.8 | 46.9 | 464.3 | 798.8 | 65.3 | 91.2 | 498.6 | 732.6 | 715.1 | 97.5 | 384.1 | 479.3 | 96.4 | 307.8 | 420.6 | 68.4 | 386.4 | 76 | 193.5 | 191.2 | 105.9 | 71.9 | 183.4 | 186.3 | 80.2
377 | 156 | 475.9 | 190.36 | 222.5199 | 196.4 | 183.9 | 211 | 204.6 | 337.5 | 23.5 | 21.1 | 51.7 | 3.7 | 243.2 | 6.1 | 43.9 | 47.1 | 470.5 | 802.5 | 65.8 | 91.5 | 492.3 | 719.8 | 715.9 | 97.7 | 381.9 | 487.4 | 97 | 304.4 | 416.3 | 68.5 | 386.1 | 76.4 | 194.1 | 191.3 | 106.1 | 72.3 | 183.2 | 186.5 | 80.6
378 | 157 | 476.2 | 190.48 | 222.6601 | 196.2 | 182.7 | 212.4 | 204.9 | 341.3 | 23.5 | 21 | 51.9 | 3.7 | 239.4 | 6.2 | 44.1 | 47.3 | 477.1 | 812.9 | 66.3 | 91.8 | 492.4 | 721.8 | 716.2 | 97.9 | 382.7 | 503.2 | 97.7 | 302 | 414.9 | 68.7 | 385.8 | 76.8 | 194.5 | 191.4 | 106.4 | 72.7 | 182.8 | 186.6 | 81.1
379 | 158 | 476.2 | 190.48 | 222.6601 | 196 | 183 | 213.5 | 205 | 348 | 23.5 | 21 | 52.1 | 4 | 251 | 6 | 44.2 | 47.6 | 487.8 | 819.7 | 66.7 | 92.1 | 493.4 | 715.3 | 715.5 | 98.1 | 383.6 | 508.1 | 98.3 | 301.3 | 412.4 | 69 | 386.3 | 77.1 | 194.9 | 191.9 | 107.2 | 73 | 182.5 | 186.8 | 81.4
380 | 159 | 475.5 | 190.2 | 222.3328 | 194.8 | 183.8 | 214.5 | 205.6 | 350.7 | 23.6 | 21 | 52.3 | 3.7 | 254 | 6.5 | 44.4 | 47.8 | 492.7 | 825.9 | 67.2 | 92.4 | 493.2 | 724.3 | 717.3 | 98.3 | 384 | 512.8 | 98.9 | 301 | 413.5 | 69.3 | 386.4 | 77.5 | 195 | 192 | 107.7 | 73.4 | 182.4 | 186.9 | 81.8
381 | 160 | 474.7 | 189.88 | 221.9588 | 194.8 | 184.3 | 215.6 | 206.4 | 350.5 | 23.6 | 21 | 52.3 | 3 | 247 | 6.9 | 44.5 | 48 | 490.9 | 826.1 | 67.7 | 92.8 | 504.1 | 740.5 | 718.5 | 98.5 | 387.1 | 528.4 | 99.6 | 303.6 | 425.9 | 69.6 | 388.8 | 77.9 | 195 | 192.2 | 108 | 73.7 | 182.2 | 187 | 82
382 | 161 | 476.4 | 190.56 | 222.7537 | 195.4 | 184.9 | 216.1 | 206 | 350.7 | 23.7 | 21 | 52.5 | 3.3 | 254.1 | 6.9 | 44.6 | 48.3 | 488.7 | 814.3 | 68.1 | 93.1 | 504.7 | 761.8 | 720.9 | 98.6 | 388.4 | 532.3 | 100.2 | 306.7 | 431.1 | 70.1 | 390.7 | 78.3 | 195.2 | 192.4 | 108.2 | 74.1 | 182.1 | 187.3 | 82.4
383 | 162 | 477 | 190.8 | 223.0342 | 196.2 | 186.1 | 217.1 | 206 | 347.1 | 23.7 | 21 | 52.6 | 2.8 | 244.9 | 7 | 44.8 | 48.5 | 488.5 | 811.2 | 68.6 | 93.5 | 502.2 | 754.9 | 719.6 | 98.7 | 396.4 | 538.4 | 100.9 | 309 | 436.1 | 70.5 | 392.2 | 78.7 | 195.7 | 192.6 | 108.7 | 74.4 | 182.3 | 187.4 | 82.9
384 | 163 | 476.4 | 190.56 | 222.7537 | 196.4 | 186.9 | 218.6 | 206.8 | 349.8 | 23.8 | 21 | 52.7 | 2.8 | 244.9 | 7 | 44.9 | 48.7 | 487.8 | 811.8 | 69.1 | 93.9 | 501.5 | 763.8 | 719.2 | 98.8 | 399.7 | 532.6 | 101.6 | 311 | 442.6 | 71 | 393.4 | 79.1 | 195.9 | 192.7 | 109.4 | 74.7 | 182.6 | 187.3 | 83.3
385 | 164 | 477 | 190.8 | 223.0342 | 195.3 | 188.2 | 218.9 | 207.3 | 345.5 | 23.8 | 21 | 52.9 | 3.6 | 240.9 | 6.5 | 45.1 | 48.9 | 485.3 | 814.5 | 69.5 | 94.3 | 507 | 772.1 | 720.4 | 99 | 400.2 | 529.7 | 102.3 | 312.7 | 450.8 | 71.4 | 394.4 | 79.5 | 196.6 | 192.7 | 109.7 | 75.1 | 182.5 | 187.6 | 83.7
386 | 165 | 477.1 | 190.84 | 223.081 | 194.4 | 189.7 | 219.2 | 207.2 | 341.6 | 23.9 | 21 | 52.9 | 3.7 | 239.9 | 5.9 | 45.2 | 49.2 | 488.7 | 814.4 | 70 | 94.8 | 531.2 | 781.5 | 721.5 | 99.2 | 400.2 | 527.3 | 103 | 317.9 | 466.4 | 72.1 | 395.9 | 79.9 | 197 | 193.1 | 109.9 | 75.4 | 182.7 | 187.9 | 84
387 | 166 | 476 | 190.4 | 222.5666 | 192.9 | 189.6 | 219.2 | 207.5 | 341.6 | 23.9 | 21 | 52.8 | 3.5 | 244.2 | 6.1 | 45.4 | 49.4 | 489.1 | 810.1 | 70.5 | 95.2 | 535.2 | 785.1 | 722.6 | 99.4 | 399.1 | 519.1 | 103.8 | 321.9 | 465.9 | 72.6 | 397.4 | 80.3 | 197.3 | 193.2 | 110.4 | 75.7 | 182.9 | 188.3 | 84.5
388 | 167 | 477.4 | 190.96 | 223.2212 | 192.2 | 190.3 | 219.4 | 207.6 | 339.3 | 24 | 21 | 52.9 | 3.7 | 240.2 | 5.9 | 45.6 | 49.6 | 493.2 | 808.5 | 70.9 | 95.8 | 535.8 | 802.4 | 724.1 | 99.7 | 397.6 | 513.1 | 104.7 | 326.4 | 475.5 | 73.2 | 397.9 | 80.7 | 197.6 | 193 | 110.8 | 76 | 183.7 | 188.5 | 84.9
389 | 168 | 477.4 | 190.96 | 223.2212 | 192.6 | 190.8 | 219.7 | 207.8 | 339.5 | 24 | 21 | 53 | 3.7 | 234.3 | 5.6 | 45.7 | 49.8 | 495.2 | 807.4 | 71.4 | 96.3 | 534 | 805.4 | 724 | 99.9 | 397.5 | 513.5 | 105.5 | 329.6 | 485.3 | 73.9 | 399.8 | 81.1 | 197.7 | 193 | 111.1 | 76.3 | 184 | 188.7 | 85.2
390 | 169 | 475.4 | 190.16 | 222.2861 | 193 | 191.4 | 219.1 | 209 | 338 | 24.1 | 21 | 53.1 | 3.1 | 230.5 | 4.8 | 45.8 | 50.1 | 499.9 | 806.5 | 71.8 | 96.8 | 539.2 | 813.2 | 725.7 | 100.1 | 398.8 | 515.5 | 106.4 | 332.8 | 492.8 | 74.6 | 401 | 81.5 | 197.8 | 193.3 | 111.6 | 76.7 | 184.3 | 189 | 85.6
391 | 170 | 476 | 190.4 | 222.5666 | 193.4 | 190.3 | 218.4 | 210 | 336.5 | 24.1 | 21 | 53.1 | 3.4 | 251.8 | 4.3 | 46 | 50.3 | 499.6 | 806.1 | 72.3 | 97.4 | 540.1 | 801.4 | 725.8 | 100.3 | 399.1 | 522 | 107.2 | 333.6 | 497 | 75.6 | 402.4 | 81.9 | 198 | 194.4 | 112.3 | 77 | 184.7 | 189.1 | 85.9
392 | 171 | 477.8 | 191.12 | 223.4083 | 194.2 | 188.9 | 218.7 | 210.1 | 339.5 | 24.2 | 21 | 53.1 | 3.5 | 247.8 | 4.6 | 46.1 | 50.5 | 497.7 | 808.3 | 72.8 | 97.9 | 528.2 | 794.3 | 725.2 | 100.5 | 400.5 | 528.8 | 108.1 | 332 | 488 | 76.6 | 403.7 | 82.3 | 198.3 | 195.1 | 113.8 | 77.3 | 185 | 189.4 | 86.2
393 | 172 | 477.5 | 191 | 223.268 | 193.8 | 188 | 218.5 | 210.5 | 340.1 | 24.2 | 21 | 53.1 | 3.4 | 249.5 | 4.7 | 46.3 | 50.7 | 499.1 | 810.9 | 73.2 | 98.4 | 520 | 794.4 | 724.8 | 100.8 | 397.2 | 520.3 | 109 | 329.3 | 480.5 | 77.4 | 402.6 | 82.7 | 198.7 | 195.9 | 114.5 | 77.7 | 185.4 | 189.7 | 86.7
394 | 173 | 478.1 | 191.24 | 223.5485 | 194.8 | 188.8 | 218.2 | 210.9 | 341 | 24.3 | 21 | 53.1 | 3.5 | 248.5 | 4.9 | 46.4 | 51 | 508.8 | 808.3 | 73.7 | 98.9 | 522.1 | 790.4 | 726.6 | 101.1 | 403.9 | 545.4 | 109.9 | 333.7 | 494.4 | 78.7 | 406.5 | 83.1 | 198.7 | 196.4 | 115.6 | 78 | 186 | 189.7 | 87.2
395 | 174 | 477.9 | 191.16 | 223.455 | 195 | 190.3 | 218.8 | 210.5 | 344.8 | 24.3 | 21 | 53.2 | 3.6 | 239.6 | 5.2 | 46.6 | 51.2 | 510.9 | 810.7 | 74.2 | 99.4 | 530.8 | 781.8 | 726.3 | 101.3 | 405.4 | 544.9 | 110.8 | 341 | 501.5 | 79.9 | 410.3 | 83.5 | 199.1 | 196.9 | 116.2 | 78.4 | 187 | 189.8 | 87.9
396 | 175 | 477.6 | 191.04 | 223.3148 | 195.7 | 190.9 | 218.9 | 209.7 | 342.7 | 24.4 | 21 | 53.4 | 3.7 | 243.2 | 5 | 46.7 | 51.4 | 512 | 808.9 | 74.6 | 100 | 531.3 | 774.1 | 725.1 | 101.6 | 402.6 | 540.5 | 111.8 | 344.2 | 499.4 | 81.2 | 409.8 | 83.9 | 199.2 | 197.3 | 117.1 | 78.7 | 187.7 | 190 | 88.5
397 | 176 | 478 | 191.2 | 223.5018 | 195.8 | 192.1 | 219.1 | 209.3 | 337.8 | 24.5 | 21 | 53.5 | 3.8 | 265.5 | 4.7 | 46.9 | 51.7 | 509.5 | 804.7 | 75.1 | 100.6 | 523.1 | 776.7 | 725.8 | 101.9 | 399.6 | 527 | 112.8 | 346.5 | 500.1 | 82.4 | 409.9 | 84.2 | 199.3 | 197.2 | 117.6 | 79.1 | 188.5 | 190.1 | 89.1
398 | 177 | 476.9 | 190.76 | 222.9874 | 196.5 | 192 | 219.4 | 209.4 | 335.9 | 24.6 | 21 | 53.8 | 3.5 | 271 | 4.9 | 47.1 | 51.9 | 499.6 | 803.7 | 75.5 | 101.2 | 513.5 | 773.7 | 723.4 | 102.1 | 399 | 521.3 | 113.7 | 345.5 | 495.8 | 83.8 | 410.1 | 84.6 | 199.8 | 197.2 | 118 | 79.5 | 189.3 | 190.3 | 89.5
399 | 178 | 479.5 | 191.8 | 224.2031 | 197.2 | 190.8 | 219.2 | 209.6 | 335.3 | 24.7 | 21 | 54 | 3.3 | 261.8 | 4.7 | 47.2 | 52.2 | 496 | 806.9 | 76 | 101.8 | 504 | 765.8 | 723.6 | 102.4 | 399 | 516.3 | 114.7 | 344.7 | 491 | 85 | 409.9 | 84.9 | 200.6 | 197.6 | 118.4 | 79.9 | 189.8 | 190.7 | 89.8
400 | 179 | 479.2 | 191.68 | 224.0629 | 196.8 | 189.2 | 219.4 | 209.8 | 335.1 | 24.7 | 21 | 54.2 | 3.5 | 271.9 | 4.9 | 47.4 | 52.5 | 487.6 | 804.3 | 76.4 | 102.3 | 498.9 | 762.1 | 724.7 | 102.7 | 397.4 | 507.6 | 115.6 | 342.7 | 487.1 | 86 | 409.4 | 85.3 | 200.6 | 197.7 | 118.8 | 80.3 | 190.3 | 191.2 | 90.4
401 | 180 | 477.6 | 191.04 | 223.3148 | 197 | 188.3 | 219.4 | 209.8 | 338.4 | 24.7 | 21 | 54.3 | 3.3 | 270.7 | 5.6 | 47.5 | 52.7 | 480.8 | 811.7 | 76.9 | 102.7 | 498.4 | 775.1 | 726.2 | 102.9 | 395.3 | 505.3 | 116.5 | 340.2 | 486.2 | 87.4 | 409.2 | 85.7 | 200.6 | 198.4 | 119.3 | 80.7 | 190.7 | 191.6 | 90.8
402 | 181 | 477.1 | 190.84 | 223.081 | 197.1 | 189.1 | 219.3 | 209.2 | 337 | 24.7 | 21 | 54.3 | 3.2 | 261.9 | 5.5 | 47.7 | 53 | 491.7 | 812.3 | 77.3 | 103.2 | 503 | 778.7 | 728.5 | 103.3 | 393.5 | 508.7 | 117.4 | 337.1 | 485.5 | 88.7 | 409.9 | 86 | 200.7 | 199.1 | 120.4 | 81.1 | 190.8 | 192 | 91.1
403 | 182 | 477.4 | 190.96 | 223.2212 | 197 | 188.6 | 219 | 209.1 | 334 | 24.7 | 21 | 54.4 | 3.4 | 253.2 | 5.2 | 47.9 | 53.3 | 502.4 | 815.6 | 77.8 | 103.6 | 534.9 | 798.1 | 730.7 | 103.7 | 392.3 | 511.6 | 118.3 | 339.9 | 490.7 | 90.9 | 412.1 | 86.4 | 200.6 | 199.1 | 121 | 81.5 | 190.7 | 192.6 | 91.3
404 | 183 | 478.1 | 191.24 | 223.5485 | 196 | 189.8 | 218.3 | 209 | 333.8 | 24.8 | 20.9 | 54.5 | 3.3 | 257.5 | 5.4 | 48.1 | 53.6 | 515.4 | 821.7 | 78.2 | 104 | 537.2 | 802.5 | 731.7 | 104.1 | 395 | 521.9 | 119.2 | 345.4 | 507.1 | 93.9 | 415.2 | 86.7 | 200.5 | 198.9 | 120.8 | 81.8 | 190.8 | 192.7 | 92
405 | 184 | 478 | 191.2 | 223.5018 | 194.9 | 191.6 | 217.5 | 208.9 | 338.5 | 24.8 | 20.9 | 54.7 | 3 | 265.7 | 5.3 | 48.2 | 53.9 | 515.3 | 813 | 78.7 | 104.5 | 544.2 | 791.4 | 730.6 | 104.6 | 404.1 | 537.2 | 120.2 | 347.3 | 518.7 | 96.5 | 418.2 | 87 | 200.8 | 198.9 | 121.2 | 82.2 | 191.2 | 192.6 | 92.5
406 | 185 | 478.2 | 191.28 | 223.5953 | 192.5 | 192.8 | 217.1 | 209 | 338.4 | 24.8 | 20.9 | 54.8 | 3.7 | 245.2 | 4.9 | 48.4 | 54.2 | 525.1 | 808.8 | 79.1 | 105 | 540.7 | 781.4 | 731.2 | 105 | 406.4 | 547.8 | 121.1 | 345 | 509.3 | 98.5 | 418.6 | 87.4 | 201 | 199.5 | 122.6 | 82.6 | 191.3 | 192.6 | 92.7
407 | 186 | 477.1 | 190.84 | 223.081 | 191.3 | 193.4 | 217.6 | 208.9 | 337.4 | 24.9 | 20.9 | 54.9 | 3.5 | 246.2 | 4.9 | 48.5 | 54.4 | 528.7 | 808.5 | 79.5 | 105.5 | 542.5 | 782.5 | 732.8 | 105.5 | 404.7 | 542.6 | 122 | 345.9 | 503.7 | 100.1 | 418.2 | 87.7 | 201.2 | 199.7 | 123.2 | 83 | 191.2 | 192.4 | 92.9
408 | 187 | 478.5 | 191.4 | 223.7356 | 191.1 | 192.8 | 217.5 | 208.5 | 337.2 | 25 | 21 | 55 | 3.3 | 271.3 | 5.3 | 48.7 | 54.7 | 530.9 | 812.2 | 80 | 106 | 543.4 | 786.8 | 733.5 | 106 | 404.3 | 544.4 | 122.9 | 347.5 | 508.1 | 102 | 418.9 | 88 | 201.2 | 200.4 | 123.9 | 83.3 | 191.4 | 192.4 | 93.7
409 | 188 | 477.5 | 191 | 223.268 | 190.9 | 192.1 | 217 | 209.5 | 340.8 | 25.1 | 21 | 55.1 | 3.2 | 255.2 | 5.4 | 48.9 | 55 | 532.7 | 819 | 80.4 | 106.5 | 539.3 | 790.6 | 734.7 | 106.6 | 410.1 | 548.5 | 123.8 | 347.6 | 509.6 | 104.3 | 420.7 | 88.4 | 201.3 | 200.8 | 123.9 | 83.7 | 192 | 192.3 | 94
410 | 189 | 477 | 190.8 | 223.0342 | 190.4 | 192.8 | 216.4 | 210.6 | 343.4 | 25 | 20.9 | 55.3 | 3.5 | 255.3 | 5.3 | 49 | 55.3 | 530.4 | 822.1 | 80.8 | 107 | 539 | 782.7 | 734.9 | 107.1 | 408.9 | 544.9 | 124.7 | 347.6 | 503.7 | 106.1 | 420.8 | 88.7 | 201.4 | 200.8 | 124 | 84.1 | 192.8 | 192.3 | 94.5
411 | 190 | 476.7 | 190.68 | 222.8939 | 190.6 | 191.4 | 216.5 | 210.7 | 341.9 | 25 | 20.9 | 55.4 | 3.3 | 269.5 | 5.3 | 49.2 | 55.6 | 539.5 | 827.2 | 81.3 | 107.6 | 539.8 | 780.7 | 735.4 | 107.6 | 409 | 553.3 | 125.6 | 350.2 | 502.5 | 107.6 | 421.7 | 89.1 | 201.6 | 201.3 | 124.1 | 84.5 | 193.1 | 192.3 | 94.9
412 | 191 | 476.8 | 190.72 | 222.9407 | 191.2 | 190.7 | 216.7 | 210.4 | 343.7 | 25 | 20.9 | 55.5 | 3.5 | 268.5 | 5.4 | 49.4 | 55.9 | 544.1 | 824.7 | 81.7 | 108.1 | 540.1 | 778.1 | 736.8 | 108 | 413.1 | 561.4 | 126.5 | 352.3 | 500.4 | 109.1 | 423.2 | 89.4 | 202.1 | 201.3 | 124.4 | 84.9 | 193.5 | 192 | 95.4
413 | 192 | 476.3 | 190.52 | 222.7069 | 191.5 | 191.2 | 216.7 | 209.8 | 346.4 | 25 | 20.9 | 55.6 | 3.7 | 264 | 5.4 | 49.5 | 56.2 | 532.5 | 807 | 82.1 | 108.7 | 536.2 | 778.1 | 735.9 | 108.5 | 409.9 | 543.2 | 127.4 | 348.2 | 491.7 | 110.8 | 422.2 | 89.7 | 202.5 | 201.4 | 125.3 | 85.3 | 193.4 | 192.1 | 95.8
414 | 193 | 476.2 | 190.48 | 222.6601 | 192.5 | 192.8 | 217.3 | 209.2 | 346.4 | 25 | 20.9 | 55.7 | 3.8 | 263.2 | 5.4 | 49.7 | 56.5 | 526.7 | 802.8 | 82.5 | 109.3 | 534.1 | 769 | 734.1 | 108.9 | 403.2 | 528.1 | 128.3 | 341.6 | 479.7 | 111.7 | 421 | 90.1 | 202.9 | 201.8 | 126 | 85.6 | 193.7 | 192.2 | 96.1
415 | 194 | 476.2 | 190.48 | 222.6601 | 193.6 | 193.7 | 218 | 209.2 | 344 | 25 | 20.9 | 55.8 | 3.9 | 259 | 5.5 | 49.9 | 56.8 | 519.2 | 800.8 | 83 | 109.8 | 528.9 | 759.4 | 732.7 | 109.2 | 398.7 | 515.3 | 129.2 | 335.8 | 468.6 | 112.6 | 419.6 | 90.4 | 203.4 | 202.3 | 126.6 | 86 | 193.9 | 192.4 | 96.4
416 | 195 | 478.8 | 191.52 | 223.8758 | 193.3 | 193.6 | 218.5 | 210 | 341.4 | 25.1 | 20.9 | 55.9 | 3.7 | 258.7 | 5.3 | 50 | 57.2 | 513.6 | 808.4 | 83.4 | 110.3 | 523.3 | 757.1 | 732.1 | 109.6 | 397.5 | 514 | 130.1 | 332.2 | 465.1 | 114 | 419.3 | 90.8 | 203.9 | 202.6 | 126.7 | 86.4 | 193.9 | 192.5 | 96.8
417 | 196 | 479.6 | 191.84 | 224.2499 | 194.3 | 193.5 | 219.7 | 210.1 | 342.1 | 25.2 | 20.9 | 55.9 | 3.8 | 258.9 | 5.2 | 50.2 | 57.5 | 510.8 | 798.4 | 83.8 | 110.8 | 526.5 | 750.6 | 730.7 | 110 | 398.9 | 512.2 | 131 | 329.9 | 465.5 | 116.4 | 420.1 | 91.2 | 204.3 | 202.6 | 126.8 | 86.7 | 194.3 | 192.6 | 97.4
418 | 197 | 478.1 | 191.24 | 223.5485 | 194.8 | 192.5 | 220.4 | 210.3 | 348.8 | 25.2 | 20.9 | 55.9 | 3.7 | 259.8 | 5.1 | 50.4 | 57.8 | 509.5 | 798.6 | 84.3 | 111.3 | 515.5 | 733.6 | 728.5 | 110.5 | 400.8 | 515.4 | 131.9 | 328.1 | 460.7 | 118.1 | 420 | 91.5 | 204.7 | 202.8 | 127.1 | 87.1 | 194.6 | 192.8 | 97.8
419 | 198 | 477.4 | 190.96 | 223.2212 | 194.5 | 192 | 221.8 | 210.5 | 352.8 | 25.2 | 20.9 | 56 | 3.7 | 266.8 | 5.3 | 50.5 | 58.1 | 517.6 | 816.6 | 84.7 | 111.8 | 516.6 | 720.8 | 730.4 | 110.8 | 403.7 | 518.9 | 132.8 | 325.2 | 454.9 | 119.2 | 420.1 | 91.9 | 205.1 | 202.9 | 127.4 | 87.4 | 194.4 | 193 | 98.1
420 | 199 | 476.5 | 190.6 | 222.8004 | 195.4 | 192.1 | 223.5 | 210.4 | 355.6 | 25.2 | 20.9 | 56.1 | 3.4 | 274.6 | 5.4 | 50.7 | 58.4 | 523.4 | 819.6 | 85.1 | 112.3 | 526.2 | 728.5 | 730.5 | 111.2 | 402.4 | 522 | 133.7 | 323.1 | 454.8 | 120.2 | 420.7 | 92.2 | 205.5 | 203.4 | 127.7 | 87.7 | 194 | 193.5 | 98.3
421 | 200 | 477.3 | 190.92 | 223.1745 | 195.5 | 192.7 | 226.1 | 210.8 | 356.9 | 25.2 | 20.9 | 56.2 | 3.7 | 265.7 | 5.5 | 50.9 | 58.8 | 528.6 | 815.5 | 85.6 | 112.8 | 542.6 | 748.2 | 732.2 | 111.7 | 405.5 | 535.3 | 134.5 | 326.6 | 470 | 121.9 | 422.9 | 92.6 | 205.8 | 203.6 | 127.9 | 88.1 | 193.7 | 194.1 | 98.7
422 | 201 | 477.6 | 191.04 | 223.3148 | 196.2 | 192.7 | 227.2 | 211.4 | 355.5 | 25.3 | 20.9 | 56.2 | 3.5 | 263.8 | 5.6 | 51 | 59.2 | 544.7 | 822.4 | 86 | 113.3 | 551.1 | 756.9 | 732 | 112.1 | 410.4 | 548.8 | 135.4 | 336.7 | 484.4 | 124.1 | 425.7 | 93 | 206.3 | 203.6 | 128.3 | 88.4 | 193.5 | 194.6 | 99
423 | 202 | 477.9 | 191.16 | 223.455 | 196.8 | 193.3 | 227.8 | 212 | 358.4 | 25.4 | 20.9 | 56.3 | 3.3 | 270 | 5.8 | 51.2 | 59.6 | 552.1 | 817.8 | 86.4 | 113.8 | 576 | 765.9 | 732.2 | 112.6 | 410 | 543.8 | 136.3 | 337.5 | 486.6 | 125.8 | 426.5 | 93.4 | 206.6 | 203.7 | 128.9 | 88.7 | 193.4 | 195 | 99.4
424 | 203 | 477.3 | 190.92 | 223.1745 | 197.2 | 194.5 | 228.8 | 212.2 | 357.6 | 25.4 | 20.9 | 56.3 | 3.3 | 276.3 | 5.7 | 51.3 | 59.9 | 547.6 | 804.8 | 86.9 | 114.4 | 581.9 | 769.5 | 732.9 | 113.1 | 409.1 | 542.5 | 137.2 | 346.2 | 501.5 | 127.8 | 428.5 | 93.8 | 207.1 | 203.8 | 129.3 | 89 | 193.5 | 195.3 | 99.9
425 | 204 | 477.1 | 190.84 | 223.081 | 197.5 | 195.8 | 228.6 | 212.7 | 354.7 | 25.5 | 20.9 | 56.3 | 3.3 | 271.8 | 5.6 | 51.5 | 60.2 | 552.3 | 802.8 | 87.3 | 115 | 600.3 | 773.9 | 734.2 | 113.5 | 408.3 | 541.7 | 138.1 | 349.8 | 515.2 | 130.1 | 431.9 | 94.2 | 207.3 | 203.9 | 129.8 | 89.3 | 194.6 | 195.6 | 100.5
426 | 205 | 477.3 | 190.92 | 223.1745 | 197 | 196.9 | 227.8 | 212.7 | 350.8 | 25.6 | 20.9 | 56.2 | 3.2 | 267.8 | 5.5 | 51.6 | 60.6 | 552.3 | 799.2 | 87.8 | 115.7 | 620 | 779.8 | 734.9 | 114 | 407 | 533.6 | 139 | 350.8 | 522.9 | 132.5 | 433.9 | 94.6 | 207.5 | 204.5 | 130.8 | 89.6 | 195.6 | 196 | 101.2
427 | 206 | 476.4 | 190.56 | 222.7537 | 196.9 | 199.4 | 227.3 | 212.9 | 344.6 | 25.6 | 20.9 | 56.3 | 3.2 | 265.2 | 5.5 | 51.8 | 60.9 | 546.2 | 793.1 | 88.2 | 116.3 | 610.8 | 786.3 | 734.5 | 114.4 | 404.7 | 524.5 | 139.9 | 350.1 | 522.7 | 134.6 | 434.6 | 95 | 207.6 | 204.5 | 131.5 | 89.9 | 196.2 | 196.4 | 101.7
428 | 207 | 474.9 | 189.96 | 222.0523 | 195.9 | 199.1 | 226.9 | 212.5 | 341.7 | 25.7 | 20.9 | 56.3 | 3 | 256.5 | 5.6 | 51.9 | 61.3 | 539.7 | 786.7 | 88.7 | 117 | 603.2 | 782.2 | 734.8 | 114.9 | 404.6 | 521 | 140.8 | 357 | 538.6 | 137.1 | 436.6 | 95.4 | 207.6 | 204.4 | 131.7 | 90.3 | 196.9 | 196.8 | 102.1
429 | 208 | 476.9 | 190.76 | 222.9874 | 195.4 | 199.3 | 225.8 | 212.5 | 343 | 25.7 | 20.9 | 56.4 | 3.3 | 257.9 | 5.6 | 52.1 | 61.5 | 537.6 | 789.6 | 89.1 | 117.7 | 599.7 | 782.5 | 736.1 | 115.3 | 405.7 | 522.1 | 141.7 | 358.1 | 542.9 | 139.6 | 438.6 | 95.8 | 207.5 | 204.3 | 132.3 | 90.6 | 197.6 | 197 | 102.6
430 | 209 | 477.3 | 190.92 | 223.1745 | 195.8 | 200 | 225.3 | 212.7 | 343.7 | 25.8 | 20.9 | 56.5 | 3.3 | 263.7 | 5.3 | 52.2 | 61.8 | 543.9 | 793.8 | 89.6 | 118.3 | 592.2 | 783.3 | 736.3 | 115.7 | 407.7 | 517.5 | 142.6 | 360.8 | 540.7 | 141.7 | 438.5 | 96.2 | 207.3 | 204.5 | 132.6 | 91 | 198.3 | 197.2 | 103.3
431 | 210 | 477.1 | 190.84 | 223.081 | 197.2 | 200.5 | 224.9 | 212.4 | 344.2 | 26 | 20.9 | 56.6 | 3.2 | 267.1 | 5.2 | 52.4 | 62.1 | 542.9 | 800.9 | 90 | 119 | 588 | 779.3 | 734.4 | 116.1 | 412.9 | 523 | 143.4 | 362.9 | 536.4 | 143.6 | 439.4 | 96.6 | 207.1 | 204.4 | 133.7 | 91.3 | 198.4 | 197.4 | 103.7
432 | 211 | 477.7 | 191.08 | 223.3615 | 197.9 | 198.8 | 224.9 | 211.7 | 345.3 | 26.1 | 20.9 | 56.6 | 3.4 | 268 | 5 | 52.5 | 62.5 | 538.5 | 804.4 | 90.5 | 119.6 | 582.6 | 770.7 | 735 | 116.6 | 412.4 | 523 | 144.3 | 359.8 | 527.7 | 144.8 | 439.4 | 96.9 | 207 | 205 | 135.1 | 91.7 | 198.4 | 197.9 | 103.9
433 | 212 | 476.1 | 190.44 | 222.6134 | 197.4 | 197.8 | 224.3 | 211.2 | 344.3 | 26.1 | 20.9 | 56.7 | 3.3 | 269 | 5 | 52.7 | 62.7 | 537.3 | 810.6 | 90.9 | 120.2 | 578.5 | 768.3 | 736.4 | 117 | 412.3 | 521.9 | 145.2 | 355.9 | 521 | 145.9 | 439.3 | 97.3 | 207.5 | 205.6 | 136 | 92 | 198.9 | 198.6 | 104.4
434 | 213 | 476.1 | 190.44 | 222.6134 | 196.8 | 196.9 | 224.2 | 211.1 | 342.1 | 26.2 | 20.9 | 56.8 | 3.5 | 267.8 | 4.8 | 52.8 | 63 | 544.4 | 807.9 | 91.4 | 120.8 | 580.6 | 767.6 | 734.9 | 117.5 | 413.6 | 528.6 | 146.1 | 353 | 517.5 | 147.3 | 440.4 | 97.7 | 207.4 | 205.9 | 136.4 | 92.4 | 199.4 | 199 | 104.9
435 | 214 | 475.6 | 190.24 | 222.3796 | 196.4 | 196.6 | 224.4 | 211.5 | 344.5 | 26.3 | 20.9 | 57 | 3.7 | 252.6 | 5.1 | 53 | 63.3 | 541.1 | 801 | 91.8 | 121.4 | 577.2 | 752.6 | 733 | 118 | 412.2 | 525.1 | 146.9 | 349.2 | 511 | 148.2 | 440.2 | 98 | 207.5 | 207.3 | 137.4 | 92.8 | 199.4 | 199.2 | 105.1
436 | 215 | 475.7 | 190.28 | 222.4264 | 197.1 | 197.4 | 223.9 | 211.3 | 342.1 | 26.4 | 20.9 | 57.1 | 3.2 | 246.4 | 5.2 | 53.2 | 63.5 | 538.6 | 790.8 | 92.3 | 121.9 | 570.7 | 743.6 | 732.8 | 118.4 | 409.9 | 527.8 | 147.8 | 345 | 507.3 | 148.8 | 439.8 | 98.4 | 207.7 | 207.8 | 137.8 | 93.1 | 199.3 | 199.3 | 105.6
437 | 216 | 476 | 190.4 | 222.5666 | 198 | 198.8 | 223.5 | 210.7 | 346.9 | 26.4 | 20.9 | 57.2 | 3.6 | 247.5 | 4.9 | 53.3 | 63.6 | 539.7 | 791.4 | 92.8 | 122.5 | 562 | 744.2 | 731.6 | 118.9 | 409 | 525.9 | 148.7 | 341.1 | 498.7 | 149.5 | 439.8 | 98.7 | 207.7 | 207.9 | 138 | 93.5 | 199.2 | 199.2 | 105.8
438 | 217 | 476.2 | 190.48 | 222.6601 | 198.6 | 199.3 | 223.7 | 210.5 | 348.7 | 26.5 | 20.9 | 57.3 | 3.4 | 239.3 | 4.7 | 53.5 | 63.8 | 535.5 | 794.1 | 93.2 | 123 | 562 | 748.3 | 732.6 | 119.5 | 408.7 | 518.8 | 149.6 | 338.7 | 492.1 | 149.7 | 439.7 | 99 | 207.8 | 207.9 | 138.1 | 93.8 | 199.1 | 199.1 | 106.1
439 | 218 | 476 | 190.4 | 222.5666 | 198.8 | 200.5 | 224.2 | 211.1 | 349.1 | 26.5 | 20.9 | 57.4 | 3.6 | 245.8 | 4.5 | 53.7 | 64 | 543.6 | 796 | 93.6 | 123.5 | 566.3 | 760.1 | 734 | 120 | 411.7 | 526.4 | 150.4 | 339.4 | 491.2 | 150.1 | 440.3 | 99.3 | 208 | 207.7 | 138.2 | 94.2 | 198.7 | 199 | 106.4
440 | 219 | 476.2 | 190.48 | 222.6601 | 198.7 | 201 | 225.5 | 212.6 | 348.2 | 26.6 | 20.9 | 57.6 | 3.6 | 261.7 | 4.6 | 53.8 | 64.3 | 540.3 | 793.6 | 94.1 | 124 | 572.6 | 756.2 | 733.2 | 120.5 | 414 | 520.5 | 151.3 | 341 | 491 | 150.8 | 441.3 | 99.7 | 208.2 | 207.6 | 137.8 | 94.5 | 198.3 | 198.9 | 106.7
441 | 220 | 476.4 | 190.56 | 222.7537 | 199.8 | 200.2 | 226.2 | 213.4 | 344.6 | 26.7 | 20.9 | 57.8 | 3.6 | 265.6 | 4.9 | 54 | 64.6 | 542.2 | 795.7 | 94.5 | 124.4 | 584.7 | 763.5 | 734 | 121.1 | 410.2 | 521.1 | 152.2 | 340.1 | 496.3 | 151.2 | 442 | 100 | 208.3 | 207.6 | 137.8 | 94.9 | 198.1 | 199.1 | 107.1
442 | 221 | 476.5 | 190.6 | 222.8004 | 200.3 | 200.6 | 227 | 213.6 | 345.5 | 26.7 | 20.9 | 58 | 3.8 | 271.3 | 5.1 | 54.2 | 64.9 | 549 | 797 | 95 | 124.9 | 600.9 | 779.6 | 734.9 | 121.6 | 412.9 | 532.6 | 153.1 | 347.7 | 511.4 | 151.5 | 445.7 | 100.4 | 208.5 | 207.4 | 137.9 | 95.2 | 198.1 | 199.6 | 107.4
443 | 222 | 476.3 | 190.52 | 222.7069 | 201 | 199.5 | 227 | 214 | 348.2 | 26.9 | 20.9 | 58.1 | 3.6 | 269.5 | 5.6 | 54.3 | 65.4 | 556.8 | 793.5 | 95.4 | 125.4 | 604.5 | 785.3 | 736.2 | 122.2 | 415.3 | 534.7 | 154 | 351.7 | 513.8 | 151.5 | 447.2 | 100.7 | 208.6 | 207.4 | 138.2 | 95.5 | 198.2 | 200.1 | 107.8
444 | 223 | 476.6 | 190.64 | 222.8472 | 202.2 | 199.8 | 228.1 | 215.5 | 349.8 | 27.1 | 20.9 | 58.2 | 3.7 | 275 | 5.9 | 54.5 | 65.8 | 551.2 | 782.6 | 95.8 | 125.9 | 604.6 | 792.8 | 736.4 | 122.8 | 415.6 | 532.4 | 155 | 353.7 | 511.3 | 151.3 | 447.2 | 101 | 209.1 | 207.4 | 138.3 | 95.8 | 198.1 | 200.6 | 108.3
445 | 224 | 476.6 | 190.64 | 222.8472 | 203.4 | 201 | 228.1 | 216.3 | 349.1 | 27.2 | 20.9 | 58.3 | 3.6 | 274.7 | 5.7 | 54.7 | 66.1 | 547.3 | 776.9 | 96.2 | 126.4 | 604.5 | 791.3 | 736.7 | 123.5 | 417 | 530.8 | 155.8 | 355.2 | 512.3 | 150.9 | 448.4 | 101.4 | 209.6 | 207.5 | 138.6 | 96.1 | 198.5 | 201.1 | 108.7
446 | 225 | 475.7 | 190.28 | 222.4264 | 203.5 | 201.9 | 228.2 | 216.6 | 348.2 | 27.3 | 20.8 | 58.5 | 3.5 | 274 | 6 | 54.8 | 66.4 | 541.2 | 767.8 | 96.7 | 126.9 | 596.3 | 796 | 736 | 124.1 | 414.2 | 521.8 | 156.7 | 353.4 | 505 | 150.5 | 447.9 | 101.8 | 209.9 | 207.6 | 138.9 | 96.4 | 198.9 | 201.4 | 109.1
447 | 226 | 476 | 190.4 | 222.5666 | 203 | 200.9 | 227.9 | 217 | 345.6 | 27.4 | 20.8 | 58.6 | 3.3 | 273.4 | 6.4 | 55 | 66.5 | 528.3 | 765.5 | 97.1 | 127.3 | 586.8 | 800.3 | 735.2 | 124.7 | 408.9 | 510.8 | 157.6 | 351 | 499.5 | 150 | 447 | 102.1 | 210.4 | 207.9 | 139.7 | 96.8 | 199.2 | 201.5 | 109.5
448 | 227 | 476.7 | 190.68 | 222.8939 | 202.3 | 199.8 | 227.7 | 217.1 | 340 | 27.5 | 20.8 | 58.7 | 3.6 | 273.4 | 6.4 | 55.2 | 66.8 | 524.1 | 753.2 | 97.5 | 127.7 | 585.3 | 803.3 | 735.1 | 125.3 | 405.4 | 507.4 | 158.5 | 348.6 | 496.3 | 149.2 | 446.8 | 102.5 | 210.6 | 207.9 | 140.1 | 97.1 | 199.8 | 201.6 | 109.9
449 | 228 | 476.9 | 190.76 | 222.9874 | 202.5 | 199.8 | 227.2 | 216.7 | 339.5 | 27.6 | 20.8 | 58.9 | 3.3 | 269.7 | 6.2 | 55.3 | 67 | 521.1 | 752.9 | 98 | 128.1 | 582.3 | 794.3 | 735.4 | 125.9 | 403.3 | 509.7 | 159.3 | 346.6 | 497.9 | 148.7 | 447.2 | 102.9 | 210.8 | 207.8 | 140.4 | 97.4 | 200.1 | 201.6 | 110.4
450 | 229 | 476.2 | 190.48 | 222.6601 | 204.2 | 200.3 | 227.1 | 216.6 | 343.5 | 27.7 | 20.8 | 59 | 3.8 | 255.2 | 7.3 | 55.5 | 67.3 | 521.3 | 765.8 | 98.4 | 128.5 | 584.1 | 799.1 | 736.3 | 126.4 | 404 | 517.8 | 160.2 | 347.8 | 509.4 | 148.6 | 449.2 | 103.2 | 211.3 | 208 | 140.9 | 97.7 | 200.6 | 201.5 | 110.8
451 | 230 | 477 | 190.8 | 223.0342 | 204 | 200.8 | 226.8 | 216.5 | 347.1 | 27.7 | 20.8 | 59.2 | 3.6 | 265.3 | 8.9 | 55.6 | 67.6 | 529.9 | 770.5 | 98.9 | 128.8 | 589.3 | 808.1 | 738.1 | 127 | 410.3 | 533.1 | 161.1 | 354.1 | 520.9 | 148.6 | 451.7 | 103.6 | 211.5 | 208.3 | 141.5 | 98 | 200.9 | 201.4 | 111.4
452 | 231 | 477.9 | 191.16 | 223.455 | 203.8 | 202.6 | 227.1 | 216.9 | 350.7 | 27.8 | 20.8 | 59.4 | 3.6 | 259.9 | 8.3 | 55.8 | 68 | 538.8 | 778.7 | 99.3 | 129.2 | 597 | 815.2 | 739.6 | 127.5 | 410.5 | 539.7 | 162 | 356.9 | 520.4 | 148.4 | 453 | 104 | 212 | 208.3 | 141.7 | 98.3 | 201.3 | 201.6 | 111.9
453 | 232 | 477.4 | 190.96 | 223.2212 | 203.8 | 202.8 | 227.3 | 217.7 | 347.8 | 27.8 | 20.8 | 59.5 | 3.9 | 233.4 | 7.6 | 55.9 | 68.5 | 551 | 776.5 | 99.7 | 129.6 | 609.2 | 825.9 | 740.7 | 128.1 | 408.9 | 548.1 | 162.9 | 359.7 | 523.1 | 148.4 | 455.5 | 104.4 | 212.7 | 208.4 | 142.1 | 98.6 | 201.9 | 201.6 | 112.4
454 | 233 | 477.7 | 191.08 | 223.3615 | 204.2 | 202.6 | 227.3 | 218.2 | 344.6 | 27.9 | 20.8 | 59.7 | 4 | 226.1 | 6.5 | 56.1 | 68.9 | 560.9 | 782.5 | 100.2 | 130.1 | 608.1 | 827.6 | 741.4 | 128.6 | 411.4 | 545 | 163.8 | 358.8 | 519.7 | 148.5 | 456.7 | 104.7 | 213 | 208.8 | 143.1 | 99 | 202.6 | 201.8 | 112.7
455 | 234 | 476.9 | 190.76 | 222.9874 | 206.3 | 204.5 | 227.1 | 219 | 341.1 | 27.9 | 20.8 | 59.8 | 3.6 | 258.5 | 5.8 | 56.3 | 69.2 | 560.5 | 787 | 100.6 | 130.6 | 609.2 | 813 | 741.5 | 129.1 | 411.4 | 548.4 | 164.7 | 357.7 | 515.4 | 148.5 | 456.9 | 105.1 | 213.2 | 209.4 | 144.3 | 99.3 | 202.6 | 202.3 | 113
456 | 235 | 477.2 | 190.88 | 223.1277 | 208.4 | 204.8 | 227 | 219.9 | 338.7 | 27.9 | 20.8 | 59.8 | 3.8 | 269.4 | 5.7 | 56.4 | 69.4 | 551.3 | 787.4 | 101.1 | 131.1 | 608.3 | 819.3 | 743.4 | 129.6 | 409.1 | 542.4 | 165.6 | 355.3 | 514.3 | 148.5 | 456.6 | 105.5 | 213.5 | 210 | 145 | 99.6 | 202.8 | 202.8 | 113.7
457 | 236 | 476.9 | 190.76 | 222.9874 | 208.4 | 202.9 | 227.5 | 220.5 | 338.3 | 28 | 20.8 | 59.8 | 3.6 | 262.4 | 5.3 | 56.6 | 69.8 | 548.2 | 786.1 | 101.5 | 131.6 | 600 | 824.4 | 744.5 | 130.1 | 407.9 | 534.6 | 166.4 | 358.6 | 519.9 | 148.7 | 458 | 105.9 | 213.7 | 210.5 | 145.3 | 99.9 | 203 | 203 | 114.4
458 | 237 | 477.3 | 190.92 | 223.1745 | 207.6 | 201.7 | 227.8 | 220.4 | 339.2 | 28.1 | 20.8 | 59.9 | 3.4 | 260.9 | 5.2 | 56.8 | 70.1 | 550.8 | 779 | 101.9 | 132.1 | 596.7 | 820.5 | 745.3 | 130.7 | 403.9 | 536.3 | 167.3 | 361.2 | 519.2 | 148.4 | 458.5 | 106.3 | 213.7 | 210.6 | 145.7 | 100.3 | 203.6 | 203.2 | 114.8
459 | 238 | 477.7 | 191.08 | 223.3615 | 206.3 | 202.6 | 227.3 | 220.3 | 339.1 | 28.2 | 20.8 | 60 | 3.3 | 265.9 | 5.9 | 56.9 | 70.4 | 562.5 | 781.6 | 102.4 | 132.6 | 589.7 | 813.5 | 745.3 | 131.3 | 406.4 | 552.1 | 168.2 | 363.7 | 520.9 | 148.4 | 459.7 | 106.7 | 213.9 | 211 | 146.2 | 100.6 | 203.8 | 203.5 | 115.3
460 | 239 | 477.3 | 190.92 | 223.1745 | 205.9 | 203 | 227 | 220.4 | 343.8 | 28.2 | 20.8 | 60.1 | 3.6 | 275.8 | 6.9 | 57.1 | 70.8 | 564.2 | 781.8 | 102.8 | 133.1 | 586.6 | 801.5 | 744.5 | 131.8 | 417.1 | 562 | 169 | 365.6 | 517.8 | 148.6 | 460.9 | 107 | 213.9 | 211 | 146.4 | 100.9 | 204.2 | 203.8 | 115.7
461 | 240 | 477.2 | 190.88 | 223.1277 | 205.2 | 204.4 | 226.5 | 220.1 | 347.2 | 28.3 | 20.8 | 60.2 | 3.5 | 278.6 | 7.2 | 57.3 | 71 | 575.1 | 789.6 | 103.3 | 133.6 | 586.8 | 807.1 | 744.1 | 132.3 | 418.6 | 567.5 | 169.9 | 367.3 | 518.6 | 148.4 | 463 | 107.4 | 214.1 | 211.1 | 146.9 | 101.2 | 204.2 | 204.2 | 116.1
462 | 241 | 477.5 | 191 | 223.268 | 204.8 | 205.2 | 226.1 | 219.6 | 344.7 | 28.3 | 20.8 | 60.2 | 3.2 | 269.8 | 8 | 57.4 | 71.3 | 576.9 | 793.6 | 103.7 | 134.1 | 584.7 | 806.7 | 742.8 | 132.8 | 419.7 | 567.5 | 170.8 | 370.1 | 519.2 | 148.3 | 464.3 | 107.8 | 214.1 | 211.7 | 147.4 | 101.6 | 204.2 | 204.6 | 116.5
463 | 242 | 477.5 | 191 | 223.268 | 204.7 | 205.6 | 225.4 | 219.8 | 345.5 | 28.3 | 20.8 | 60.3 | 3.8 | 275 | 8 | 57.6 | 71.6 | 584.8 | 791.4 | 104.1 | 134.7 | 587.4 | 818.2 | 744.7 | 133.4 | 420.2 | 565 | 171.6 | 377.9 | 522.9 | 148.3 | 465.2 | 108.2 | 214.1 | 212 | 147.5 | 101.9 | 204.3 | 204.9 | 116.9
464 | 243 | 477.2 | 190.88 | 223.1277 | 203.9 | 204.5 | 224.7 | 220 | 346.3 | 28.3 | 20.8 | 60.5 | 4.3 | 276.6 | 7.8 | 57.7 | 71.9 | 590.8 | 782.7 | 104.6 | 135.2 | 610 | 827.5 | 744.1 | 133.9 | 420.7 | 569.3 | 172.4 | 385.2 | 528.6 | 148.3 | 467.8 | 108.6 | 214.2 | 212.2 | 147.3 | 102.2 | 204.6 | 205.4 | 117.3
465 | 244 | 476.8 | 190.72 | 222.9407 | 204.1 | 204.6 | 224.4 | 220.3 | 347.2 | 28.4 | 20.8 | 60.6 | 4.4 | 278.2 | 7.5 | 57.9 | 72.2 | 586.1 | 769.9 | 105 | 135.8 | 631.3 | 830.5 | 744 | 134.4 | 416.7 | 553.5 | 173.3 | 391.7 | 534.4 | 148.2 | 468.6 | 108.9 | 214.1 | 212.6 | 148.2 | 102.6 | 204.9 | 206.2 | 117.9
466 | 245 | 477.1 | 190.84 | 223.081 | 205.5 | 204 | 223.5 | 220.9 | 346.9 | 28.5 | 20.8 | 60.6 | 4.4 | 278.5 | 7.5 | 58.1 | 72.4 | 585.5 | 772.1 | 105.5 | 136.3 | 626.1 | 817.9 | 744.8 | 134.9 | 413.2 | 546.9 | 174.1 | 394.4 | 533.5 | 148.5 | 468.5 | 109.3 | 214.3 | 213.3 | 149.3 | 102.9 | 205 | 207.1 | 118.3
467 | 246 | 477.2 | 190.88 | 223.1277 | 205.4 | 202.8 | 222.7 | 221.1 | 344.4 | 28.6 | 20.8 | 60.7 | 4.4 | 277.8 | 7.2 | 58.2 | 72.5 | 582.5 | 765.7 | 105.9 | 136.8 | 615.7 | 806 | 744.1 | 135.4 | 411.7 | 534.9 | 174.9 | 391.7 | 525.6 | 148.4 | 467.5 | 109.7 | 214.4 | 213.1 | 149.4 | 103.2 | 205 | 207.4 | 118.5
468 | 247 | 477.2 | 190.88 | 223.1277 | 205.1 | 201.9 | 221.7 | 221.5 | 343.8 | 28.6 | 20.8 | 60.8 | 4.2 | 276.2 | 6.7 | 58.4 | 72.6 | 584.4 | 768 | 106.3 | 137.4 | 600.2 | 819.9 | 743.7 | 135.9 | 410 | 529.1 | 175.7 | 389.6 | 522.4 | 147.9 | 467.5 | 110 | 214.4 | 213.1 | 149.3 | 103.6 | 205.6 | 207.5 | 118.9
469 | 248 | 476.7 | 190.68 | 222.8939 | 205 | 201.6 | 221.2 | 221.9 | 345 | 28.7 | 20.8 | 60.9 | 4.1 | 276.8 | 6.4 | 58.6 | 72.7 | 579.8 | 776.2 | 106.8 | 137.9 | 592.7 | 816.6 | 743.8 | 136.4 | 408.7 | 523.6 | 176.5 | 386.7 | 518.1 | 147.8 | 467.4 | 110.3 | 214.5 | 213 | 149.3 | 103.9 | 206.4 | 207.5 | 119.5
470 | 249 | 477.1 | 190.84 | 223.081 | 205.6 | 200.9 | 221.4 | 221.9 | 344.8 | 28.8 | 20.8 | 61 | 4.1 | 279.1 | 6.4 | 58.7 | 72.8 | 567.7 | 777.5 | 107.2 | 138.3 | 587.9 | 814.4 | 743.4 | 136.9 | 406.9 | 519.3 | 177.3 | 385 | 522.4 | 147.6 | 467.7 | 110.7 | 214.3 | 213 | 149.6 | 104.2 | 207 | 207.4 | 120.1
471 | 250 | 476.8 | 190.72 | 222.9407 | 206.4 | 199.6 | 221.1 | 221.5 | 344 | 28.9 | 20.8 | 61.1 | 4.1 | 271.2 | 6.3 | 58.9 | 72.9 | 560.7 | 777.6 | 107.7 | 138.7 | 598.6 | 824.2 | 744.3 | 137.4 | 408.5 | 521.6 | 178 | 388.2 | 533.2 | 147.9 | 469.7 | 111 | 214.3 | 213 | 150.1 | 104.6 | 207.1 | 207.5 | 120.4
472 | 251 | 476.6 | 190.64 | 222.8472 | 206.5 | 198 | 221.1 | 221.4 | 342.3 | 29.1 | 20.8 | 61.2 | 4.2 | 275.9 | 6.4 | 59.1 | 73.1 | 560.3 | 771.5 | 108.1 | 139.1 | 608.9 | 820.5 | 744.7 | 138 | 408.9 | 515.9 | 178.8 | 391.4 | 535.8 | 147.9 | 471.4 | 111.4 | 214.5 | 213.2 | 150.8 | 104.9 | 207.2 | 207.7 | 120.9
473 | 252 | 476.9 | 190.76 | 222.9874 | 206 | 197.8 | 221.9 | 221.6 | 340.2 | 29.2 | 20.8 | 61.3 | 4.6 | 268.4 | 6.2 | 59.2 | 73.3 | 552.9 | 764.8 | 108.5 | 139.5 | 600.8 | 810 | 744.5 | 138.5 | 407 | 508.9 | 179.6 | 390.8 | 531.6 | 147.7 | 471.3 | 111.8 | 214.4 | 213.1 | 151.6 | 105.3 | 207 | 207.9 | 121.3
474 | 253 | 476.6 | 190.64 | 222.8472 | 205.9 | 197.9 | 222.1 | 221.9 | 336.8 | 29.3 | 20.8 | 61.4 | 4.2 | 243.9 | 6.4 | 59.4 | 73.5 | 547.7 | 768.6 | 109 | 139.8 | 601.5 | 819.3 | 744.5 | 139 | 403.6 | 502.7 | 180.3 | 387.5 | 527.5 | 147.5 | 470.7 | 112.1 | 214.3 | 213.1 | 152 | 105.6 | 206.7 | 208 | 121.7
475 | 254 | 475.4 | 190.16 | 222.2861 | 206.1 | 198.8 | 222.3 | 222.1 | 335 | 29.2 | 20.8 | 61.5 | 4 | 243.7 | 6.6 | 59.6 | 73.8 | 545.9 | 774.2 | 109.4 | 140.2 | 614.1 | 827.4 | 744.9 | 139.5 | 404.2 | 503 | 181.1 | 388.2 | 532 | 147.6 | 471.9 | 112.4 | 214.2 | 213.1 | 151.9 | 105.9 | 206.6 | 208.3 | 122.1
476 | 255 | 474.9 | 189.96 | 222.0523 | 208.2 | 199.4 | 222.2 | 222.4 | 335.1 | 29.3 | 20.8 | 61.6 | 4.5 | 237.9 | 7 | 59.7 | 74 | 549.8 | 771.9 | 109.8 | 140.5 | 607.9 | 812.2 | 743.5 | 140.1 | 403.4 | 504.4 | 181.8 | 384.1 | 528.2 | 147.6 | 472.4 | 112.8 | 214.3 | 212.9 | 152 | 106.3 | 206.5 | 208.4 | 122.4
477 | 256 | 474.9 | 189.96 | 222.0523 | 209.7 | 198.9 | 221.9 | 221.6 | 337.4 | 29.3 | 20.8 | 61.7 | 4.7 | 223.9 | 6.2 | 59.9 | 74.1 | 535 | 757.6 | 110.3 | 140.9 | 595 | 798.6 | 741.2 | 140.6 | 399 | 491.9 | 182.5 | 380.7 | 516.7 | 147.4 | 471.2 | 113.1 | 214.1 | 212.8 | 152.4 | 106.6 | 206.4 | 208.6 | 122.7
478 | 257 | 477.4 | 190.96 | 223.2212 | 209.7 | 199.1 | 222 | 220.7 | 335.1 | 29.3 | 20.8 | 61.7 | 3.7 | 246.9 | 5.8 | 60.1 | 74.3 | 529.1 | 758.9 | 110.7 | 141.2 | 594.5 | 818.2 | 742.5 | 141.1 | 395.4 | 489.6 | 183.3 | 379.3 | 523.8 | 147.5 | 472.1 | 113.5 | 213.9 | 213.1 | 153.2 | 106.9 | 206.6 | 209.2 | 123.2
479 | 258 | 475.6 | 190.24 | 222.3796 | 210.1 | 199 | 222 | 220.9 | 334 | 29.3 | 20.8 | 61.7 | 4.1 | 240 | 6.6 | 60.2 | 74.4 | 537.4 | 772.4 | 111.2 | 141.5 | 597.3 | 818.2 | 743.6 | 141.6 | 397.7 | 501 | 184 | 382.4 | 541.8 | 147.7 | 474.6 | 113.8 | 213.8 | 213 | 153.2 | 107.3 | 206.6 | 209.5 | 123.6
480 | 259 | 475 | 190 | 222.0991 | 209.2 | 198.7 | 221.3 | 221.1 | 336.3 | 29.2 | 20.8 | 61.6 | 4.1 | 238.8 | 7.4 | 60.4 | 74.7 | 538.4 | 779.4 | 111.6 | 141.8 | 591.7 | 813.9 | 744.3 | 142.1 | 398.6 | 500 | 184.7 | 383.3 | 539.7 | 147.9 | 475.8 | 114.2 | 213.6 | 212.8 | 153 | 107.6 | 207 | 209.5 | 124.1
481 | 260 | 475.9 | 190.36 | 222.5199 | 208 | 199.7 | 221.4 | 221.1 | 338.2 | 29.2 | 20.8 | 61.7 | 4 | 236.8 | 7.7 | 60.6 | 74.9 | 542.2 | 779.3 | 112 | 142.1 | 593.1 | 823.5 | 745.5 | 142.7 | 399.4 | 499.5 | 185.5 | 391.3 | 555.4 | 148.6 | 478.1 | 114.5 | 213.6 | 212.6 | 153.4 | 107.9 | 207.8 | 209.5 | 124.8
482 | 261 | 475.6 | 190.24 | 222.3796 | 207.4 | 200 | 221.8 | 220.4 | 341.3 | 29.3 | 20.8 | 61.7 | 3.6 | 239.7 | 8.4 | 60.7 | 75.2 | 549.2 | 775.6 | 112.5 | 142.5 | 600.9 | 829.3 | 745.3 | 143.2 | 398.4 | 504 | 186.2 | 394.9 | 557.1 | 149.3 | 479.4 | 114.8 | 213.5 | 212.4 | 153.8 | 108.2 | 208.1 | 209.6 | 125.2
483 | 262 | 475.8 | 190.32 | 222.4731 | 206.4 | 202.1 | 221.3 | 219.8 | 340.1 | 29.5 | 20.8 | 61.7 | 3.5 | 241 | 9.1 | 60.9 | 75.5 | 563.5 | 773.5 | 112.9 | 142.8 | 615 | 833.4 | 746 | 143.7 | 397.5 | 510.1 | 186.9 | 398.4 | 560.2 | 150.2 | 481.2 | 115.2 | 213.2 | 212.1 | 153.9 | 108.6 | 208.2 | 209.5 | 125.8
484 | 263 | 476.4 | 190.56 | 222.7537 | 206.5 | 202.1 | 220.6 | 219.7 | 339.8 | 29.6 | 20.8 | 61.7 | 3.6 | 241.1 | 8.8 | 61.1 | 75.7 | 580.2 | 784.9 | 113.4 | 143.2 | 631.7 | 830.5 | 747.1 | 144.2 | 400 | 526.4 | 187.7 | 404.8 | 570.9 | 151.3 | 484.1 | 115.5 | 213.1 | 212 | 154.2 | 108.9 | 208.5 | 209.6 | 126.2
485 | 264 | 480.3 | 192.12 | 224.5772 | 205.5 | 201.7 | 220.1 | 219.7 | 343.1 | 29.6 | 20.8 | 61.8 | 3.5 | 242.5 | 8.1 | 61.3 | 75.9 | 596.2 | 792.8 | 113.8 | 143.6 | 647.5 | 829.7 | 747.3 | 144.7 | 409.1 | 542 | 188.4 | 407.8 | 575 | 152.1 | 486.5 | 115.8 | 213.1 | 212.2 | 155 | 109.2 | 208.6 | 209.8 | 126.6
486 | 265 | 481.9 | 192.76 | 225.3253 | 205 | 202 | 219.7 | 219.9 | 345.6 | 29.6 | 20.8 | 61.9 | 3.6 | 243.3 | 7.7 | 61.4 | 76.1 | 617.5 | 799.7 | 114.3 | 144 | 651.9 | 831 | 747.8 | 145.2 | 415 | 561.8 | 189.2 | 409 | 584.1 | 152.8 | 489.1 | 116.1 | 213.1 | 212.3 | 155.6 | 109.6 | 208.7 | 210 | 127
487 | 266 | 482.3 | 192.92 | 225.5124 | 204.1 | 203.6 | 219.5 | 219.7 | 346.9 | 29.7 | 20.7 | 62 | 3.4 | 239.4 | 7.6 | 61.6 | 76.2 | 623.7 | 800 | 114.7 | 144.5 | 651 | 833.6 | 746.8 | 145.7 | 422.1 | 569.3 | 190 | 414.6 | 593.9 | 153.3 | 493.2 | 116.5 | 213.2 | 212.5 | 156 | 109.9 | 208.7 | 210.2 | 127.2
488 | 267 | 480 | 192 | 224.4369 | 203 | 204.3 | 219.9 | 219.4 | 348.1 | 29.8 | 20.7 | 62.1 | 3.6 | 241 | 7.5 | 61.8 | 76.4 | 628.6 | 802.7 | 115.2 | 145 | 654.6 | 825.1 | 746.3 | 146.2 | 425.1 | 584.1 | 190.8 | 415.5 | 593.9 | 154 | 496.4 | 116.8 | 213.5 | 212.7 | 156.5 | 110.2 | 209 | 210.4 | 127.7
489 | 268 | 479.6 | 191.84 | 224.2499 | 203 | 204.7 | 220.8 | 219.7 | 350 | 29.9 | 20.7 | 62.1 | 3.7 | 237.1 | 7.6 | 61.9 | 76.5 | 632.2 | 802.2 | 115.6 | 145.5 | 653.4 | 804.4 | 745.3 | 146.7 | 429.6 | 595.8 | 191.6 | 415.6 | 597.9 | 154.7 | 498.8 | 117.1 | 213.8 | 213 | 157 | 110.5 | 208.9 | 210.5 | 128
490 | 269 | 476.9 | 190.76 | 222.9874 | 203 | 205.4 | 222.1 | 219.9 | 358.5 | 29.9 | 20.7 | 62.1 | 3.7 | 244.8 | 7.7 | 62.1 | 76.5 | 631.8 | 806.3 | 116.1 | 146.1 | 657.2 | 796.1 | 744.4 | 147.2 | 435 | 610 | 192.4 | 413.2 | 595.8 | 155.5 | 501.2 | 117.4 | 214.3 | 213.6 | 158 | 110.8 | 208.7 | 210.7 | 128.2
491 | 270 | 476.7 | 190.68 | 222.8939 | 203.1 | 206.4 | 223.5 | 220.1 | 369.4 | 30 | 20.7 | 62.2 | 3.9 | 224.5 | 7.3 | 62.3 | 76.7 | 632.6 | 808.2 | 116.6 | 146.7 | 654.9 | 769 | 742.2 | 147.7 | 442.4 | 629 | 193.2 | 412.1 | 591.3 | 156.3 | 504.1 | 117.8 | 215.2 | 214.5 | 159 | 111.2 | 208.6 | 210.9 | 128.6
492 | 271 | 477 | 190.8 | 223.0342 | 203.8 | 208 | 224.9 | 220.3 | 375 | 30 | 20.7 | 62.3 | 4 | 235.7 | 6.4 | 62.5 | 76.9 | 632.3 | 808.2 | 117 | 147.3 | 645.2 | 754.8 | 741.9 | 148.3 | 441.8 | 632.8 | 194 | 409.5 | 585.8 | 156.9 | 506.4 | 118.1 | 216.5 | 215.1 | 159.6 | 111.5 | 208.6 | 211.4 | 128.9
493 | 272 | 478 | 191.2 | 223.5018 | 204.7 | 209.6 | 226.8 | 220.2 | 374.6 | 30 | 20.7 | 62.3 | 3.9 | 246 | 6.2 | 62.6 | 77.1 | 630.1 | 811.3 | 117.5 | 147.9 | 637.5 | 742.7 | 739.8 | 148.8 | 437.6 | 626.5 | 194.9 | 408.2 | 574.3 | 157.2 | 506.3 | 118.4 | 218.1 | 215.7 | 159.9 | 111.8 | 208.8 | 211.8 | 129.2
494 | 273 | 477.6 | 191.04 | 223.3148 | 205.1 | 210.8 | 228.6 | 220 | 369.8 | 30 | 20.7 | 62.3 | 4.3 | 242.3 | 6 | 62.8 | 77.1 | 614.1 | 805.6 | 118 | 148.5 | 618.8 | 738.7 | 739.5 | 149.4 | 431.6 | 609.7 | 195.7 | 404.9 | 563.9 | 157.2 | 505 | 118.8 | 219.1 | 216 | 159.6 | 112.1 | 208.8 | 212.2 | 129.5
495 | 274 | 477.3 | 190.92 | 223.1745 | 206.2 | 211.2 | 229.7 | 220.4 | 363.4 | 30 | 20.7 | 62.3 | 4 | 246.7 | 5.6 | 63 | 77.1 | 605.3 | 800.6 | 118.4 | 149.1 | 608.3 | 744 | 739.1 | 149.9 | 428.7 | 601.3 | 196.5 | 404.3 | 566.2 | 157.5 | 504.9 | 119.1 | 219.8 | 216.3 | 159.4 | 112.3 | 209 | 212.4 | 129.9
496 | 275 | 477.5 | 191 | 223.268 | 208.1 | 211.8 | 231.5 | 220.3 | 361.4 | 30.1 | 20.7 | 62.4 | 3.6 | 265.7 | 5.9 | 63.2 | 77.3 | 600.9 | 785.5 | 118.9 | 149.7 | 605.8 | 760.4 | 737.6 | 150.5 | 425.5 | 589.5 | 197.3 | 403 | 559.1 | 157.7 | 505 | 119.4 | 220.5 | 216.5 | 159.1 | 112.6 | 209.2 | 212.6 | 130.4
497 | 276 | 476.9 | 190.76 | 222.9874 | 209.7 | 213.3 | 231.8 | 219.9 | 357.1 | 30.2 | 20.7 | 62.5 | 3.6 | 254.5 | 6.4 | 63.4 | 77.5 | 601.1 | 784.7 | 119.3 | 150.2 | 616.4 | 772.5 | 738.6 | 151 | 419.6 | 575.7 | 198.1 | 401 | 553.4 | 158.1 | 504.7 | 119.8 | 220.9 | 216.9 | 159.7 | 112.9 | 210.3 | 212.9 | 130.9
498 | 277 | 477.5 | 191 | 223.268 | 210 | 212.9 | 231.1 | 220.2 | 354.6 | 30.3 | 20.7 | 62.6 | 3.8 | 249.5 | 6.5 | 63.5 | 77.7 | 599 | 779.4 | 119.8 | 150.7 | 629.5 | 796.7 | 740.3 | 151.6 | 414.6 | 567 | 199 | 401.2 | 548.5 | 158.3 | 504.8 | 120.2 | 220.7 | 217.1 | 160.1 | 113.2 | 211.2 | 213.3 | 131.4
499 | 278 | 476.8 | 190.72 | 222.9407 | 209.5 | 212.9 | 230.3 | 220.6 | 350.3 | 30.4 | 20.7 | 62.7 | 3.4 | 250.5 | 6.4 | 63.7 | 77.9 | 601.1 | 777.8 | 120.2 | 151.2 | 644.1 | 815.9 | 742.3 | 152.1 | 411.5 | 562.2 | 199.9 | 405.2 | 548.9 | 159 | 506.4 | 120.6 | 220.6 | 217.1 | 160 | 113.6 | 211.6 | 213.6 | 131.7
500 | 279 | 477.1 | 190.84 | 223.081 | 209 | 212.5 | 229.5 | 221 | 350.6 | 30.5 | 20.7 | 62.9 | 3.6 | 245.8 | 6.6 | 63.9 | 77.9 | 610.6 | 781 | 120.7 | 151.7 | 660.7 | 828.7 | 744.5 | 152.6 | 412.2 | 575.2 | 200.7 | 413.5 | 563.8 | 160.2 | 509.4 | 120.9 | 220.5 | 217.1 | 160 | 113.9 | 211.7 | 214 | 132.2
501 | 280 | 476.9 | 190.76 | 222.9874 | 209.5 | 213.6 | 228.5 | 221.5 | 355.1 | 30.6 | 20.7 | 63 | 3.9 | 245.4 | 6.7 | 64.1 | 78.1 | 611.5 | 778.8 | 121.1 | 152.2 | 667.9 | 823.9 | 745.6 | 153.2 | 413.7 | 575.7 | 201.6 | 418 | 562.8 | 161.3 | 511.1 | 121.3 | 220.4 | 217.1 | 160.7 | 114.2 | 212.3 | 214.2 | 132.7
502 | 281 | 477.4 | 190.96 | 223.2212 | 209 | 214.5 | 227.5 | 221.7 | 352.5 | 30.7 | 20.7 | 63.1 | 3.6 | 243.4 | 6.6 | 64.2 | 78.2 | 610.5 | 775.4 | 121.6 | 152.6 | 651.7 | 798.5 | 744.8 | 153.7 | 412.9 | 570.3 | 202.6 | 414.2 | 554.2 | 161.9 | 510.2 | 121.7 | 220.1 | 217.9 | 161.8 | 114.6 | 212.7 | 214.3 | 133
503 | 282 | 477 | 190.8 | 223.0342 | 209.1 | 215.1 | 226.7 | 221.8 | 354 | 30.7 | 20.7 | 63.2 | 4.2 | 245.1 | 6.5 | 64.4 | 78.2 | 600 | 771.7 | 122 | 153.1 | 645.1 | 796.3 | 744 | 154.2 | 413.4 | 569.9 | 203.8 | 408 | 542.8 | 162.6 | 509.8 | 122.1 | 220.1 | 218.3 | 162.8 | 114.9 | 213.4 | 214.3 | 133.5
504 | 283 | 476.7 | 190.68 | 222.8939 | 209.5 | 214.8 | 227 | 222.1 | 353.6 | 30.8 | 20.7 | 63.3 | 4.2 | 242.8 | 6.4 | 64.6 | 78.2 | 598 | 771.5 | 122.5 | 153.5 | 634.5 | 810.6 | 745.1 | 154.7 | 411.3 | 563 | 204.9 | 402.6 | 548.7 | 162.9 | 510 | 122.4 | 220.1 | 218.4 | 163.9 | 115.2 | 213.8 | 214.4 | 133.9
505 | 284 | 477.2 | 190.88 | 223.1277 | 210.8 | 214.2 | 226.9 | 221.5 | 352.9 | 30.8 | 20.7 | 63.5 | 4.1 | 255.1 | 5.9 | 64.7 | 78.3 | 594.7 | 766.7 | 123 | 153.9 | 620.8 | 807.6 | 744.7 | 155.3 | 412.4 | 559.6 | 205.9 | 406 | 551.3 | 163.3 | 511.1 | 122.8 | 220.3 | 218.6 | 164.3 | 115.6 | 214 | 214.6 | 134.3
506 | 285 | 476.8 | 190.72 | 222.9407 | 211.2 | 212.6 | 226.7 | 221 | 351.6 | 30.9 | 20.7 | 63.6 | 3.6 | 260.9 | 5.3 | 64.9 | 78.3 | 581.7 | 763.9 | 123.4 | 154.3 | 611.6 | 817.9 | 745.8 | 155.8 | 411 | 555.9 | 206.8 | 405.8 | 550.2 | 163.7 | 511.3 | 123.1 | 220.6 | 218.5 | 164.5 | 115.9 | 214.6 | 214.7 | 134.9
507 | 286 | 476.8 | 190.72 | 222.9407 | 212.4 | 211.9 | 227.2 | 221.5 | 349.7 | 30.9 | 20.7 | 63.7 | 3.6 | 226.1 | 4.9 | 65 | 78.5 | 576.4 | 759.9 | 123.9 | 154.7 | 619.1 | 837.6 | 746.7 | 156.3 | 409.6 | 547.4 | 207.6 | 409.6 | 552.7 | 164.1 | 511 | 123.5 | 220.8 | 218.4 | 164.3 | 116.3 | 214.9 | 214.9 | 135.4
508 | 287 | 476.8 | 190.72 | 222.9407 | 213.9 | 211.8 | 228 | 222.3 | 349.1 | 31 | 20.7 | 63.7 | 3.6 | 209 | 4.3 | 65.2 | 78.7 | 577.7 | 760.3 | 124.4 | 155 | 617.3 | 846.7 | 747.3 | 156.8 | 409.1 | 542.9 | 208.4 | 415.6 | 562.9 | 164.6 | 511.7 | 123.8 | 221.1 | 218.3 | 164.2 | 116.6 | 215.7 | 214.9 | 136
509 | 288 | 477.7 | 191.08 | 223.3615 | 214.5 | 212.1 | 228 | 222.5 | 350.1 | 31.1 | 20.7 | 63.7 | 3.8 | 236.1 | 4.1 | 65.4 | 78.8 | 579.2 | 758.2 | 124.8 | 155.4 | 621.8 | 860.2 | 748.6 | 157.4 | 408.2 | 539.5 | 209.2 | 417.9 | 560.7 | 164.7 | 511.5 | 124.2 | 221.1 | 218.1 | 164 | 116.9 | 216 | 215.1 | 136.6
510 | 289 | 476.9 | 190.76 | 222.9874 | 214.8 | 211.3 | 227.3 | 223.7 | 352 | 31.2 | 20.7 | 63.8 | 3.7 | 252 | 5.1 | 65.5 | 79 | 576.1 | 755.6 | 125.2 | 155.7 | 642.6 | 873.1 | 751.1 | 157.9 | 406.1 | 539.5 | 210 | 424.4 | 576.4 | 165.2 | 512.9 | 124.5 | 221 | 218 | 164.2 | 117.3 | 216.5 | 215.4 | 137.1
511 | 290 | 477.7 | 191.08 | 223.3615 | 214.7 | 211.4 | 226.3 | 224.6 | 349.3 | 31.3 | 20.7 | 63.8 | 3.6 | 239.3 | 5.8 | 65.7 | 79.3 | 577 | 757.8 | 125.7 | 156 | 655.4 | 868.9 | 751.7 | 158.4 | 405.9 | 538 | 210.6 | 424 | 574.3 | 165.5 | 514.9 | 124.8 | 221 | 218.2 | 164.7 | 117.6 | 216.9 | 215.6 | 137.6
512 | 291 | 477.4 | 190.96 | 223.2212 | 214.5 | 210.6 | 225.3 | 224.6 | 347.2 | 31.5 | 20.7 | 63.9 | 3.8 | 236.5 | 6 | 65.8 | 79.5 | 580.1 | 758.7 | 126.1 | 156.3 | 652.3 | 870 | 751.7 | 159 | 406.5 | 540.7 | 211.3 | 426.6 | 581.7 | 165.9 | 515.8 | 125.1 | 220.7 | 218.6 | 165.3 | 118 | 217.4 | 215.9 | 138
513 | 292 | 477 | 190.8 | 223.0342 | 214.6 | 209.5 | 225.2 | 224.6 | 351 | 31.6 | 20.7 | 64 | 4 | 240.6 | 5.9 | 66 | 79.5 | 593.2 | 763.6 | 126.5 | 156.7 | 657.8 | 866.3 | 751.6 | 159.5 | 412.7 | 547.6 | 212.1 | 427.5 | 589 | 166.4 | 517.9 | 125.5 | 220.6 | 218.5 | 165.8 | 118.4 | 217.7 | 216.1 | 138.4
514 | 293 | 475.6 | 190.24 | 222.3796 | 215.3 | 209.1 | 224.4 | 224.6 | 353.5 | 31.7 | 20.7 | 64.1 | 3.4 | 237.2 | 6 | 66.1 | 79.6 | 604.2 | 770 | 126.9 | 157 | 655.4 | 875 | 753.6 | 160 | 415.3 | 552.6 | 212.9 | 428.7 | 582.9 | 166.8 | 519 | 125.8 | 220.8 | 218.4 | 165.9 | 118.7 | 217.6 | 216.4 | 138.7
515 | 294 | 475.6 | 190.24 | 222.3796 | 216.1 | 209.9 | 224 | 224.6 | 354.8 | 31.8 | 20.7 | 64.2 | 3.1 | 240.4 | 6.3 | 66.3 | 79.7 | 611.4 | 776.4 | 127.3 | 157.3 | 649.1 | 869 | 754.2 | 160.5 | 417.3 | 557.2 | 213.6 | 427.8 | 577.4 | 167.2 | 519.5 | 126.1 | 220.7 | 218.4 | 165.9 | 119.1 | 217.5 | 216.6 | 139.2
516 | 295 | 476.1 | 190.44 | 222.6134 | 216.3 | 209.6 | 223.9 | 224.5 | 354 | 31.8 | 20.7 | 64.3 | 3.2 | 241.6 | 6.2 | 66.4 | 79.8 | 613.6 | 770.2 | 127.7 | 157.6 | 659.4 | 874.1 | 754.7 | 161 | 418.4 | 566 | 214.3 | 430.8 | 580.2 | 167.8 | 521.6 | 126.4 | 220.7 | 218.3 | 165.9 | 119.4 | 217.9 | 216.8 | 139.6
517 | 296 | 475.8 | 190.32 | 222.4731 | 216.6 | 209.4 | 224.1 | 225.1 | 354.9 | 31.9 | 20.7 | 64.3 | 3.3 | 236.6 | 6 | 66.6 | 80.1 | 608.5 | 759.2 | 128.1 | 157.9 | 663.3 | 870.4 | 756.2 | 161.5 | 415.1 | 554.5 | 215.1 | 434.1 | 582.6 | 168.7 | 521.9 | 126.7 | 221 | 218.6 | 166.2 | 119.8 | 218.3 | 217.4 | 140
518 | 297 | 475.8 | 190.32 | 222.4731 | 217.8 | 209.3 | 224.3 | 225.9 | 355.3 | 32 | 20.7 | 64.4 | 3.4 | 237.5 | 5.9 | 66.7 | 80.1 | 613.1 | 761 | 128.5 | 158.2 | 662 | 865 | 756.3 | 162.1 | 414.4 | 550.7 | 215.8 | 437.6 | 596.4 | 169.6 | 523.1 | 127.1 | 221 | 219 | 166.9 | 120.2 | 218.4 | 218 | 140.2
519 | 298 | 476.2 | 190.48 | 222.6601 | 218.3 | 209.5 | 224.6 | 227.2 | 354.8 | 32.1 | 20.7 | 64.5 | 3.5 | 245.1 | 6 | 66.9 | 80.2 | 615 | 769.3 | 128.9 | 158.4 | 662.1 | 863.5 | 756.2 | 162.6 | 415.3 | 559.2 | 216.5 | 435.5 | 592.2 | 170.3 | 524.4 | 127.4 | 221 | 218.9 | 167.4 | 120.5 | 218.5 | 218.6 | 140.5
520 | 299 | 476.2 | 190.48 | 222.6601 | 217.2 | 208.8 | 225.3 | 227.2 | 356.3 | 32.2 | 20.7 | 64.6 | 3.5 | 242.9 | 6.1 | 67.1 | 80.2 | 629.4 | 778.4 | 129.3 | 158.7 | 657.2 | 858 | 755.8 | 163.1 | 418.8 | 565 | 217.1 | 435.9 | 596.4 | 170.9 | 524.8 | 127.7 | 221.2 | 218.9 | 167.6 | 120.9 | 218.9 | 219.2 | 140.8
521 | 300 | 477.9 | 191.16 | 223.455 | 216.7 | 207.6 | 225.4 | 226.6 | 357.9 | 32.2 | 20.7 | 64.6 | 3.8 | 247.9 | 5.9 | 67.2 | 80.3 | 633.5 | 788.5 | 129.7 | 159 | 648.8 | 852.3 | 755.5 | 163.6 | 422.8 | 577.7 | 217.8 | 435.6 | 592.5 | 171.6 | 526 | 128 | 221.4 | 219 | 168.1 | 121.3 | 218.9 | 219.9 | 141.2
522 | 301 | 479.2 | 191.68 | 224.0629 | 216.5 | 205.9 | 225.4 | 226.7 | 357.8 | 32.2 | 20.7 | 64.8 | 3.3 | 246.1 | 5.7 | 67.4 | 80.4 | 629.1 | 791.3 | 130 | 159.3 | 629.6 | 832 | 754.1 | 164.1 | 423.3 | 578.6 | 218.5 | 434 | 583.4 | 171.8 | 526.3 | 128.3 | 221.5 | 219.4 | 169.2 | 121.6 | 219 | 219.9 | 141.5
523 | 302 | 478.7 | 191.48 | 223.8291 | 217.2 | 204.9 | 225.7 | 226.9 | 353.9 | 32.2 | 20.7 | 64.9 | 3.5 | 246.5 | 5.3 | 67.5 | 80.5 | 629.5 | 791.7 | 130.4 | 159.6 | 623.2 | 806.4 | 752.5 | 164.7 | 424.4 | 579.7 | 219.2 | 430.4 | 580.4 | 172 | 526.9 | 128.6 | 222 | 220.2 | 170.1 | 122 | 218.8 | 220.1 | 141.8
524 | 303 | 476.7 | 190.68 | 222.8939 | 217.7 | 204.8 | 226.1 | 227.1 | 352.5 | 32.2 | 20.7 | 65 | 3.5 | 249.2 | 4.9 | 67.7 | 80.7 | 632.8 | 796 | 130.8 | 159.9 | 627.1 | 790.3 | 752.1 | 165.2 | 425.4 | 589.4 | 219.9 | 428.2 | 580.6 | 171.9 | 528.4 | 129 | 222.3 | 220.6 | 170.7 | 122.4 | 218.6 | 220.5 | 142.1
525 | 304 | 476.2 | 190.48 | 222.6601 | 218.7 | 204.1 | 226.5 | 227.2 | 349.7 | 32.2 | 20.7 | 65.1 | 4 | 247.5 | 4.5 | 67.8 | 80.9 | 645.8 | 798.5 | 131.2 | 160.2 | 641.2 | 785.7 | 751.8 | 165.7 | 426.1 | 592.8 | 220.6 | 428.4 | 579.4 | 172.1 | 530.4 | 129.3 | 222.7 | 221.2 | 171.4 | 122.7 | 218.8 | 220.6 | 142.5
526 | 305 | 477.7 | 191.08 | 223.3615 | 218.7 | 203.4 | 226.9 | 227.3 | 347.9 | 32.2 | 20.7 | 65.2 | 4 | 247.4 | 4.6 | 68 | 81 | 649.9 | 793.1 | 131.5 | 160.5 | 633.4 | 781.9 | 750.8 | 166.2 | 429.4 | 593.8 | 221.4 | 432.6 | 588.8 | 172.7 | 531.8 | 129.6 | 222.7 | 221.4 | 171.6 | 123 | 219.2 | 220.6 | 142.9
527 | 306 | 476.6 | 190.64 | 222.8472 | 217.9 | 203.1 | 227.6 | 227.5 | 347.7 | 32.2 | 20.7 | 65.3 | 3.8 | 251 | 4.5 | 68.1 | 81.1 | 647.1 | 789.3 | 131.9 | 160.9 | 626.6 | 772.4 | 750.6 | 166.7 | 429.8 | 597.6 | 222.3 | 430.9 | 583.5 | 172.9 | 532.4 | 129.9 | 222.9 | 221.5 | 171.4 | 123.3 | 219.7 | 220.5 | 143.3
528 | 307 | 477.4 | 190.96 | 223.2212 | 218.4 | 203.1 | 227.4 | 227.2 | 351.5 | 32.2 | 20.7 | 65.3 | 3.6 | 257.4 | 4.2 | 68.3 | 81.4 | 648 | 789.3 | 132.2 | 161.2 | 644.2 | 755.5 | 750.5 | 167.3 | 432.1 | 615.9 | 223 | 429.1 | 581.7 | 173.4 | 534.4 | 130.2 | 223.4 | 221.8 | 171.2 | 123.7 | 219.6 | 220.5 | 143.6
529 | 308 | 477.7 | 191.08 | 223.3615 | 219.6 | 202.9 | 227.6 | 226.9 | 363.3 | 32.3 | 20.7 | 65.4 | 4 | 245.7 | 4.2 | 68.4 | 81.7 | 649.9 | 790.8 | 132.6 | 161.5 | 649.5 | 736.5 | 748.8 | 167.8 | 442 | 623.5 | 223.7 | 426.5 | 573.7 | 174.4 | 535.2 | 130.5 | 223.6 | 222.1 | 171.5 | 124 | 219.3 | 220.3 | 143.8
530 | 309 | 477.4 | 190.96 | 223.2212 | 219.6 | 203.7 | 228.6 | 227.1 | 369.7 | 32.2 | 20.7 | 65.5 | 4 | 238.5 | 4.4 | 68.6 | 81.6 | 645.6 | 792.7 | 132.9 | 161.8 | 645.9 | 748.4 | 748.5 | 168.3 | 447.3 | 631.8 | 224.4 | 422.7 | 569.9 | 174.9 | 535.8 | 130.8 | 223.9 | 223.1 | 172.2 | 124.3 | 219 | 220.4 | 144
531 | 310 | 477.5 | 191 | 223.268 | 218.6 | 204.3 | 230 | 227.3 | 366.3 | 32.2 | 20.7 | 65.6 | 3.4 | 245.9 | 4.5 | 68.8 | 81.8 | 642.2 | 794.7 | 133.3 | 162.1 | 633.6 | 778.7 | 749.9 | 168.8 | 447.5 | 627.8 | 225.3 | 427.3 | 574.7 | 175.3 | 536.8 | 131.1 | 224.2 | 224.2 | 173.1 | 124.7 | 219 | 220.5 | 144.4
532 | 311 | 477.3 | 190.92 | 223.1745 | 218 | 204.6 | 231 | 226.8 | 365.4 | 32.3 | 20.7 | 65.7 | 3.8 | 247.3 | 4.6 | 68.9 | 82.1 | 638.7 | 790.7 | 133.7 | 162.5 | 643.9 | 790.2 | 750.4 | 169.3 | 444.2 | 625.1 | 226.1 | 430.6 | 576.6 | 175.6 | 537.9 | 131.4 | 224.9 | 224.4 | 173.1 | 125 | 218.9 | 220.4 | 144.8
533 | 312 | 477.5 | 191 | 223.268 | 218 | 205.4 | 231 | 226.8 | 367 | 32.3 | 20.7 | 65.8 | 4.1 | 246.7 | 4.6 | 69.1 | 82.4 | 648.8 | 789.6 | 134 | 162.8 | 658.1 | 798.1 | 750.8 | 169.9 | 449.1 | 633.4 | 226.9 | 431.2 | 587.2 | 176.4 | 539.2 | 131.7 | 225.2 | 224.5 | 173.2 | 125.3 | 218.8 | 220.1 | 145
534 | 313 | 477 | 190.8 | 223.0342 | 217.6 | 204.4 | 230.8 | 227.2 | 370.9 | 32.3 | 20.7 | 65.9 | 3.8 | 246.5 | 4.6 | 69.2 | 82.7 | 656.9 | 789.6 | 134.4 | 163.1 | 652.8 | 813 | 751.8 | 170.4 | 458.5 | 653.4 | 227.7 | 435.7 | 593.9 | 177.1 | 541.3 | 132 | 225.6 | 224.6 | 173.4 | 125.6 | 218.7 | 220.2 | 145.3
535 | 314 | 477.1 | 190.84 | 223.081 | 216.9 | 203.8 | 231 | 227.8 | 374 | 32.3 | 20.7 | 66.1 | 3.6 | 248.4 | 4.8 | 69.4 | 82.9 | 660.1 | 784.9 | 134.7 | 163.4 | 663.5 | 829.4 | 753.3 | 170.9 | 458.4 | 650.2 | 228.4 | 438.2 | 594.4 | 177.5 | 543.5 | 132.3 | 226 | 224.6 | 173.3 | 125.9 | 219.6 | 220.5 | 145.7
536 | 315 | 477.1 | 190.84 | 223.081 | 216.7 | 204.8 | 231.3 | 227.9 | 375.1 | 32.3 | 20.7 | 66.2 | 3.6 | 258.3 | 4.8 | 69.5 | 83.1 | 663.8 | 771.3 | 135.1 | 163.8 | 675.2 | 839.5 | 752 | 171.5 | 454.5 | 636 | 229.2 | 440.8 | 591.3 | 177.5 | 544.2 | 132.6 | 226.4 | 225.1 | 174.1 | 126.2 | 220.2 | 220.6 | 146.2
537 | 316 | 477.2 | 190.88 | 223.1277 | 217.4 | 206 | 231.9 | 227.9 | 376.8 | 32.4 | 20.7 | 66.3 | 3.4 | 249.3 | 5.3 | 69.7 | 83.6 | 667.8 | 764.9 | 135.5 | 164.1 | 680.5 | 846.1 | 752.9 | 172 | 448.7 | 625.7 | 229.9 | 443.3 | 587 | 177.4 | 544.2 | 132.9 | 226.6 | 225 | 174.6 | 126.5 | 220.3 | 221 | 146.6
538 | 317 | 477.2 | 190.88 | 223.1277 | 218 | 206.6 | 232.2 | 228.3 | 373.6 | 32.5 | 20.6 | 66.4 | 3.2 | 244.8 | 5.4 | 69.9 | 84 | 667.9 | 759.4 | 135.9 | 164.4 | 677.9 | 848.9 | 753.6 | 172.5 | 444.2 | 614.1 | 230.6 | 445 | 583.8 | 177.4 | 544.1 | 133.2 | 226.6 | 224.9 | 174.4 | 126.8 | 220.8 | 221.4 | 147.1
539 | 318 | 477.3 | 190.92 | 223.1745 | 218.9 | 206.2 | 231.7 | 229.5 | 370.2 | 32.6 | 20.6 | 66.5 | 3.4 | 246.2 | 5.6 | 70 | 84.1 | 661.8 | 755.7 | 136.2 | 164.7 | 660.8 | 851 | 753 | 173.1 | 441.5 | 607.3 | 231.1 | 441.3 | 578.6 | 177.2 | 543.4 | 133.5 | 226.6 | 224.8 | 174.5 | 127.1 | 221.2 | 221.9 | 147.5
540 | 319 | 477.3 | 190.92 | 223.1745 | 219.2 | 205.8 | 230.6 | 230.6 | 365.1 | 32.7 | 20.6 | 66.5 | 3.8 | 241.2 | 6 | 70.2 | 84.1 | 657.3 | 747.3 | 136.6 | 165 | 645.5 | 857.7 | 753 | 173.6 | 437.6 | 590.4 | 231.6 | 436.8 | 568.2 | 176.8 | 542 | 133.8 | 226.5 | 224.6 | 174.4 | 127.4 | 221.4 | 222.5 | 148
541 | 320 | 476.7 | 190.68 | 222.8939 | 219.2 | 205.8 | 229.7 | 230.5 | 361.9 | 32.8 | 20.6 | 66.6 | 4.3 | 241.1 | 6.5 | 70.3 | 84.2 | 650 | 746 | 137 | 165.3 | 643.7 | 851.9 | 754.3 | 174.1 | 434.3 | 582.5 | 232.1 | 432.5 | 564.4 | 176.9 | 540.8 | 134.1 | 226.6 | 224.5 | 174.9 | 127.8 | 221.5 | 222.9 | 148.4
542 | 321 | 476.7 | 190.68 | 222.8939 | 219.4 | 205.8 | 229.6 | 231 | 358.7 | 32.9 | 20.6 | 66.7 | 4.3 | 229.5 | 6.5 | 70.5 | 84.2 | 653.2 | 757.4 | 137.3 | 165.5 | 646.2 | 843.9 | 755 | 174.7 | 433.1 | 579.9 | 232.5 | 430.6 | 563.8 | 176.5 | 540.7 | 134.4 | 226.4 | 224.5 | 175.2 | 128.1 | 221.5 | 223.1 | 148.8
543 | 322 | 476.7 | 190.68 | 222.8939 | 219.1 | 205.6 | 229.3 | 231.2 | 357.8 | 32.9 | 20.6 | 66.8 | 4.3 | 229.8 | 6.3 | 70.7 | 84.4 | 661.4 | 772.5 | 137.7 | 165.7 | 645.6 | 851.6 | 756.7 | 175.2 | 435.4 | 591.6 | 232.9 | 427.9 | 563.5 | 176.6 | 541.5 | 134.7 | 226.3 | 224.4 | 175.3 | 128.4 | 221.5 | 223.2 | 149.1
544 | 323 | 476.6 | 190.64 | 222.8472 | 218.7 | 204.5 | 229.2 | 231.2 | 360.5 | 33 | 20.6 | 66.9 | 3.9 | 253.1 | 6.3 | 70.8 | 84.4 | 656.8 | 780.6 | 138.1 | 165.9 | 630.7 | 834.3 | 756.1 | 175.7 | 436.7 | 592.7 | 233.3 | 425.4 | 558.1 | 176.5 | 541.2 | 135 | 226.4 | 224.4 | 175.6 | 128.8 | 221.7 | 223.1 | 149.4
545 | 324 | 476.4 | 190.56 | 222.7537 | 218.5 | 203.5 | 229.2 | 231.2 | 364.5 | 33 | 20.6 | 66.9 | 4 | 257.3 | 6.1 | 71 | 84.3 | 652.4 | 784.8 | 138.4 | 166.1 | 614.6 | 820.7 | 756 | 176.3 | 439 | 597.9 | 233.9 | 420 | 547.5 | 176.5 | 541.1 | 135.3 | 226.5 | 224.4 | 176.1 | 129.1 | 221.9 | 223 | 149.6
546 | 325 | 476.2 | 190.48 | 222.6601 | 218.7 | 203.3 | 230.5 | 230.9 | 369.9 | 33.1 | 20.6 | 67 | 4.1 | 260.4 | 5.7 | 71.2 | 84.4 | 667.2 | 784.7 | 138.8 | 166.3 | 607.2 | 822.2 | 757.3 | 176.8 | 445.4 | 613.1 | 234.6 | 415.9 | 550.1 | 176.6 | 542 | 135.6 | 226.7 | 224.4 | 176.4 | 129.4 | 221.7 | 222.9 | 149.9
547 | 326 | 475.5 | 190.2 | 222.3328 | 219.8 | 204 | 231.6 | 230.6 | 369.8 | 33.1 | 20.6 | 67 | 3.6 | 255.5 | 5.6 | 71.3 | 84.5 | 671.2 | 780.1 | 139.2 | 166.4 | 608.3 | 825.1 | 757.2 | 177.3 | 447.3 | 601.1 | 235.3 | 413.9 | 549.5 | 176.9 | 542.7 | 135.9 | 227.3 | 224.6 | 176.4 | 129.7 | 221.4 | 222.8 | 150.2
548 | 327 | 477.3 | 190.92 | 223.1745 | 219.7 | 203.8 | 231.9 | 229.8 | 370.3 | 33.2 | 20.6 | 67.1 | 3.9 | 244.4 | 6.1 | 71.5 | 84.5 | 678.6 | 780.7 | 139.5 | 166.6 | 610.1 | 826.1 | 755.8 | 177.9 | 448.7 | 595.2 | 235.8 | 410.1 | 548.3 | 177.2 | 542 | 136.2 | 227.5 | 224.9 | 176.9 | 130 | 221 | 223 | 150.4
549 | 328 | 477.1 | 190.84 | 223.081 | 219.6 | 203.7 | 232.2 | 230 | 367.4 | 33.2 | 20.6 | 67.1 | 3.9 | 245 | 6.5 | 71.7 | 84.4 | 666.4 | 769.7 | 139.9 | 166.7 | 621 | 827.9 | 755.3 | 178.4 | 447.5 | 584.8 | 236.4 | 408.1 | 548.3 | 177.6 | 541.9 | 136.4 | 227.8 | 225 | 177 | 130.3 | 220.7 | 223.2 | 150.7
550 | 329 | 475.3 | 190.12 | 222.2393 | 219.4 | 204.7 | 232.3 | 230.4 | 364.8 | 33.4 | 20.6 | 67.2 | 3.8 | 237.1 | 6.4 | 71.8 | 84.4 | 663.5 | 774.2 | 140.3 | 166.8 | 625 | 833.6 | 755.1 | 179 | 449.6 | 586.4 | 237.1 | 404.3 | 548.8 | 178.1 | 542.2 | 136.7 | 228.1 | 225.4 | 177.4 | 130.7 | 220.6 | 223.4 | 151.1
551 | 330 | 473.6 | 189.44 | 221.4444 | 218.7 | 205.7 | 232.9 | 230 | 364.2 | 33.5 | 20.6 | 67.3 | 3.6 | 235.9 | 6.4 | 72 | 84.5 | 676.6 | 784.4 | 140.6 | 166.9 | 634.1 | 831.5 | 756.3 | 179.5 | 450.4 | 597.3 | 237.7 | 403.3 | 552.2 | 178.5 | 543.6 | 137.1 | 228.6 | 225.7 | 178 | 131 | 220.5 | 223.6 | 151.4
552 | 331 | 475 | 190 | 222.0991 | 217.9 | 205.4 | 233.5 | 229.7 | 364.8 | 33.6 | 20.6 | 67.4 | 3.8 | 222.7 | 6.3 | 72.2 | 84.6 | 673.9 | 786 | 141 | 167 | 653.4 | 835 | 757.1 | 180 | 450.4 | 594.1 | 238.3 | 401.4 | 555.4 | 178.8 | 544.6 | 137.4 | 229.1 | 225.9 | 178.1 | 131.2 | 220.1 | 223.5 | 151.7
553 | 332 | 475.4 | 190.16 | 222.2861 | 216.7 | 206.5 | 234 | 229.1 | 366.6 | 33.7 | 20.6 | 67.6 | 3.6 | 220.1 | 6 | 72.3 | 84.7 | 672.2 | 782.8 | 141.3 | 167.1 | 661.2 | 825.7 | 758.3 | 180.6 | 453.2 | 597 | 238.9 | 401.4 | 567.5 | 179.1 | 545.7 | 137.7 | 229.4 | 226.1 | 178.2 | 131.5 | 220 | 223.4 | 151.9
554 | 333 | 475.9 | 190.36 | 222.5199 | 215.4 | 207.7 | 234.7 | 229.4 | 368.5 | 33.7 | 20.6 | 67.6 | 4.2 | 230.8 | 5.9 | 72.5 | 84.7 | 673.5 | 778.4 | 141.7 | 167.2 | 675.7 | 831.6 | 757.8 | 181.1 | 454.3 | 591.4 | 239.4 | 406.8 | 583.1 | 179.7 | 547.5 | 138 | 229.9 | 226.3 | 178.3 | 131.8 | 220.2 | 223.1 | 152.2
555 | 334 | 476.2 | 190.48 | 222.6601 | 214.4 | 208.4 | 234.8 | 229.9 | 368.8 | 33.8 | 20.6 | 67.6 | 4.2 | 239.6 | 5.8 | 72.7 | 84.8 | 672.9 | 768.3 | 142 | 167.2 | 668.7 | 833 | 757.5 | 181.7 | 455.1 | 595.4 | 239.9 | 407.4 | 581.9 | 180.1 | 548.9 | 138.3 | 230 | 226.2 | 178.5 | 132.1 | 220.6 | 223 | 152.6
556 | 335 | 476 | 190.4 | 222.5666 | 213.8 | 207.7 | 235 | 230.7 | 368.3 | 33.9 | 20.6 | 67.6 | 4 | 241.4 | 5.5 | 72.8 | 84.9 | 667.6 | 765.5 | 142.4 | 167.3 | 667.2 | 851 | 756.9 | 182.3 | 454.7 | 592.3 | 240.5 | 410.7 | 582.1 | 180.6 | 549.6 | 138.6 | 229.8 | 226.2 | 179.1 | 132.5 | 221.6 | 223.2 | 153.3
557 | 336 | 475.6 | 190.24 | 222.3796 | 213.4 | 207.1 | 234.6 | 231.2 | 369.3 | 34.1 | 20.6 | 67.7 | 3.6 | 245 | 5.5 | 73 | 85.1 | 657.6 | 771.3 | 142.7 | 167.4 | 640.8 | 848.4 | 755.7 | 182.8 | 453.5 | 588.5 | 241.1 | 409.8 | 572.9 | 181.1 | 549.4 | 138.9 | 229.5 | 226.7 | 180.4 | 132.8 | 222.2 | 223.5 | 153.7
558 | 337 | 475.6 | 190.24 | 222.3796 | 213.6 | 206.5 | 234.2 | 231.2 | 366.7 | 34.2 | 20.6 | 67.7 | 3.2 | 249.9 | 5.7 | 73.2 | 85.2 | 642.9 | 769.8 | 143.1 | 167.4 | 629.8 | 837.5 | 756.6 | 183.3 | 448.5 | 574.4 | 241.7 | 404.5 | 559.5 | 181.3 | 547.8 | 139.2 | 229.6 | 227.2 | 180.8 | 133.1 | 222.8 | 223.6 | 154
559 | 338 | 476.2 | 190.48 | 222.6601 | 214.2 | 206.5 | 234.1 | 231.1 | 361.7 | 34.3 | 20.6 | 67.7 | 3.5 | 248.4 | 6.2 | 73.3 | 85.3 | 636.5 | 773.6 | 143.4 | 167.4 | 618.2 | 826.7 | 756.2 | 183.9 | 446.4 | 572.1 | 242.2 | 400.5 | 553.9 | 181.3 | 547.7 | 139.5 | 229.6 | 227.3 | 180.8 | 133.4 | 223.1 | 223.7 | 154.3
560 | 339 | 475.6 | 190.24 | 222.3796 | 215.3 | 205.7 | 233.9 | 230.8 | 360 | 34.3 | 20.6 | 67.6 | 3.7 | 249.5 | 7.1 | 73.5 | 85.5 | 636.8 | 763.5 | 143.8 | 167.4 | 606.7 | 830.2 | 755.4 | 184.4 | 444.8 | 559.6 | 242.8 | 400.6 | 547.7 | 181.5 | 546.9 | 139.8 | 229.5 | 227.2 | 180.8 | 133.7 | 223.7 | 223.8 | 154.6
561 | 340 | 474.8 | 189.92 | 222.0055 | 216.1 | 206.5 | 233.9 | 230.6 | 358.9 | 34.3 | 20.6 | 67.6 | 4.2 | 242.6 | 7.3 | 73.7 | 85.7 | 634.4 | 758.6 | 144.2 | 167.4 | 597.4 | 841.4 | 755.9 | 185 | 440.6 | 547 | 243.3 | 399.3 | 545.3 | 181.6 | 546.5 | 140.1 | 229.6 | 227 | 180.7 | 134.1 | 223.7 | 223.7 | 155
562 | 341 | 476.3 | 190.52 | 222.7069 | 215.6 | 206.4 | 233.9 | 231.1 | 355.2 | 34.3 | 20.6 | 67.7 | 4.6 | 246.5 | 7.3 | 73.8 | 85.9 | 629 | 746.9 | 144.6 | 167.4 | 594.6 | 849.4 | 755.1 | 185.5 | 434.7 | 536 | 243.9 | 400.2 | 547.2 | 181.9 | 546.5 | 140.4 | 229.4 | 226.9 | 180.8 | 134.4 | 224.2 | 223.7 | 155.3
563 | 342 | 476.7 | 190.68 | 222.8939 | 216.6 | 205.3 | 233.6 | 231.7 | 354 | 34.3 | 20.6 | 67.8 | 4.5 | 246 | 7.4 | 74 | 86.1 | 618.6 | 735.8 | 144.9 | 167.4 | 587 | 832.9 | 753.4 | 186.1 | 428.9 | 525.2 | 244.5 | 399.8 | 540.1 | 181.9 | 545.5 | 140.6 | 229.2 | 227 | 181.2 | 134.7 | 224.7 | 223.6 | 155.6
564 | 343 | 476.8 | 190.72 | 222.9407 | 218.8 | 204.6 | 232.5 | 231.9 | 350.9 | 34.3 | 20.6 | 67.9 | 4.8 | 252.6 | 7.2 | 74.2 | 86.2 | 603.9 | 727.4 | 145.3 | 167.4 | 583.7 | 817.6 | 753 | 186.7 | 424.9 | 510.3 | 245.1 | 396.3 | 530.8 | 181.9 | 543.6 | 140.9 | 229.2 | 227.1 | 181.8 | 135 | 224.8 | 223.5 | 155.8
565 | 344 | 479.5 | 191.8 | 224.2031 | 218.9 | 204.6 | 231.7 | 231.7 | 350.6 | 34.3 | 20.6 | 67.9 | 4.6 | 255.8 | 6.9 | 74.3 | 86.3 | 593.1 | 718.4 | 145.7 | 167.4 | 589.8 | 828.6 | 752.9 | 187.2 | 418.3 | 496.4 | 245.7 | 392.2 | 533.2 | 182.1 | 542.8 | 141.2 | 229 | 227.1 | 181.9 | 135.4 | 224.6 | 223.4 | 156.4
566 | 345 | 478.9 | 191.56 | 223.9226 | 218.7 | 204.8 | 231.2 | 232.1 | 349.2 | 34.3 | 20.6 | 68 | 4.3 | 259.7 | 6.7 | 74.5 | 86.5 | 600.9 | 729.5 | 146.1 | 167.3 | 611.4 | 844.3 | 753.9 | 187.8 | 415.1 | 500.5 | 246.4 | 394.4 | 537.4 | 182.3 | 542.7 | 141.5 | 228.8 | 226.8 | 181.8 | 135.7 | 224.4 | 223.2 | 156.7
567 | 346 | 476.7 | 190.68 | 222.8939 | 219.7 | 204.7 | 230.3 | 232.6 | 350.3 | 34.3 | 20.6 | 68 | 4.2 | 265.1 | 6.5 | 74.7 | 86.6 | 614.7 | 733.4 | 146.4 | 167.3 | 629.5 | 861 | 754.8 | 188.3 | 418.4 | 513.9 | 247.1 | 401.3 | 557.2 | 183 | 544.6 | 141.7 | 228.6 | 226.6 | 181.9 | 136 | 224 | 223 | 157
568 | 347 | 477.9 | 191.16 | 223.455 | 220.1 | 204.5 | 229.6 | 232.7 | 349.2 | 34.4 | 20.6 | 68.1 | 4.1 | 268.9 | 6.6 | 74.9 | 86.7 | 615 | 732 | 146.8 | 167.3 | 644.3 | 867.4 | 755.3 | 188.9 | 419.6 | 515.3 | 247.8 | 405.4 | 570.1 | 183.5 | 545.6 | 142 | 228.5 | 226.4 | 182.2 | 136.4 | 224.3 | 223 | 157.3
569 | 348 | 477.7 | 191.08 | 223.3615 | 220.9 | 205.1 | 228.9 | 233.6 | 353.6 | 34.5 | 20.6 | 68.2 | 4 | 259.1 | 6.2 | 75 | 86.9 | 609.6 | 730.2 | 147.2 | 167.3 | 648.8 | 865.1 | 755.3 | 189.4 | 417.8 | 509.2 | 248.5 | 411 | 572.7 | 183.8 | 546.5 | 142.3 | 228.5 | 226.2 | 182.3 | 136.7 | 224.8 | 223.6 | 157.6
570 | 349 | 477.6 | 191.04 | 223.3148 | 220.9 | 205.9 | 228.6 | 234.1 | 357.8 | 34.5 | 20.6 | 68.2 | 4.2 | 226.2 | 6.3 | 75.2 | 87 | 601.8 | 737.7 | 147.6 | 167.3 | 643 | 869.8 | 756.7 | 190 | 415.6 | 512.3 | 249.3 | 411.9 | 565.3 | 184.3 | 545.6 | 142.6 | 228.4 | 225.9 | 182.8 | 137.1 | 225.4 | 224 | 158
571 | 350 | 477.4 | 190.96 | 223.2212 | 220 | 207 | 228.6 | 234 | 356.2 | 34.5 | 20.6 | 68.3 | 4.5 | 220.6 | 6.8 | 75.4 | 87.2 | 607.8 | 750.8 | 148 | 167.3 | 640.3 | 872.8 | 757.9 | 190.6 | 420.1 | 530.5 | 250 | 411 | 566.6 | 184.8 | 546.2 | 142.8 | 228.2 | 225.9 | 183.1 | 137.5 | 225.4 | 224.2 | 158.2
572 | 351 | 477 | 190.8 | 223.0342 | 219.5 | 208.1 | 228.7 | 233.9 | 358 | 34.5 | 20.6 | 68.4 | 4.3 | 211.7 | 6.4 | 75.5 | 87.3 | 611.1 | 744.6 | 148.4 | 167.3 | 651.5 | 878.3 | 759.3 | 191.1 | 420.8 | 529.5 | 250.7 | 413.2 | 571.9 | 185.3 | 546.6 | 143.1 | 228.1 | 225.7 | 183.1 | 137.9 | 225.3 | 224.4 | 158.5
573 | 352 | 478.2 | 191.28 | 223.5953 | 219.4 | 209 | 228.6 | 234.2 | 359.6 | 34.6 | 20.6 | 68.5 | 4.4 | 228.5 | 5.9 | 75.7 | 87.5 | 612.4 | 733.2 | 148.8 | 167.3 | 660.4 | 882.6 | 759.8 | 191.7 | 419.5 | 520.6 | 251.5 | 417.3 | 586.5 | 185.6 | 547.4 | 143.4 | 228 | 225.3 | 183.1 | 138.2 | 225.5 | 224.5 | 159
574 | 353 | 476.4 | 190.56 | 222.7537 | 219 | 210.2 | 228.6 | 234.9 | 361.8 | 34.7 | 20.6 | 68.6 | 4.3 | 233 | 5.4 | 75.9 | 87.8 | 620.3 | 734 | 149.2 | 167.3 | 672.1 | 885.4 | 759.8 | 192.3 | 418.1 | 523.3 | 251.8 | 420.6 | 593.3 | 186 | 548.9 | 143.6 | 227.8 | 225.1 | 183.2 | 138.6 | 225.8 | 224.6 | 159.3
575 | 354 | 476.3 | 190.52 | 222.7069 | 218.8 | 211.2 | 228.2 | 235.7 | 361.3 | 34.8 | 20.6 | 68.6 | 4.1 | 231.8 | 5.3 | 76.1 | 87.8 | 621 | 742.6 | 149.6 | 167.3 | 668.9 | 876.8 | 759.1 | 192.8 | 417.6 | 521.3 | 252.3 | 422 | 591.7 | 186.5 | 549.3 | 143.9 | 227.5 | 225 | 183.4 | 138.9 | 226.1 | 225 | 159.6
576 | 355 | 475.2 | 190.08 | 222.1926 | 218.6 | 211.9 | 227.6 | 236 | 360.8 | 34.8 | 20.6 | 68.6 | 4.1 | 250.8 | 5.7 | 76.2 | 87.9 | 616.3 | 758.6 | 150 | 167.4 | 662.4 | 878.2 | 760.2 | 193.4 | 418 | 536 | 252.9 | 417.5 | 589.6 | 186.8 | 549.8 | 144.1 | 227.3 | 225 | 183.8 | 139.3 | 226.6 | 225.4 | 160.1
577 | 356 | 475.9 | 190.36 | 222.5199 | 218.8 | 212.8 | 226.8 | 235.6 | 362 | 34.9 | 20.6 | 68.6 | 4.4 | 262 | 6.3 | 76.4 | 88 | 617.3 | 765.5 | 150.4 | 167.4 | 664.8 | 874.3 | 760.7 | 193.9 | 423 | 553.3 | 253.6 | 416.7 | 583.6 | 187.3 | 550.7 | 144.4 | 227.3 | 225.2 | 184.2 | 139.7 | 226.9 | 225.8 | 160.5
578 | 357 | 476.5 | 190.6 | 222.8004 | 219.5 | 212.2 | 227.6 | 234.6 | 363.7 | 34.9 | 20.6 | 68.6 | 4 | 238.1 | 6.3 | 76.6 | 88.2 | 613.3 | 763.1 | 150.8 | 167.4 | 671.4 | 870.3 | 761.3 | 194.5 | 424.7 | 547.9 | 254.2 | 416.2 | 584.5 | 187.8 | 551.1 | 144.6 | 227.3 | 225.1 | 184.5 | 140.1 | 227 | 226.1 | 160.8
579 | 358 | 478.1 | 191.24 | 223.5485 | 220.6 | 211.2 | 227.8 | 234 | 362.6 | 35 | 20.6 | 68.6 | 4.1 | 230.2 | 6.5 | 76.8 | 88.4 | 609.3 | 759.2 | 151.2 | 167.4 | 674.1 | 867.2 | 761.5 | 195.1 | 421.6 | 534.2 | 254.8 | 419.2 | 584.9 | 188.4 | 551 | 144.9 | 227.3 | 225 | 184.7 | 140.4 | 227.7 | 226.2 | 161.3
580 | 359 | 478.1 | 191.24 | 223.5485 | 220.4 | 210.8 | 227.8 | 233.4 | 364 | 35.1 | 20.6 | 68.6 | 4.4 | 249.5 | 6.1 | 77 | 88.5 | 603.3 | 755.4 | 151.6 | 167.5 | 670.2 | 876.7 | 760.8 | 195.6 | 419.4 | 528.8 | 255.6 | 414.3 | 575.4 | 188.9 | 550 | 145.1 | 227.2 | 225 | 185.1 | 140.8 | 227.9 | 226.4 | 161.8
581 | 360 | 475.5 | 190.2 | 222.3328 | 219.8 | 210.9 | 228.2 | 232.8 | 363.7 | 35.2 | 20.6 | 68.6 | 4.4 | 227.3 | 5.6 | 77.1 | 88.7 | 602.3 | 754.5 | 152 | 167.5 | 667 | 887.6 | 762 | 196.2 | 417.8 | 526.1 | 256.2 | 414.8 | 574.3 | 189.2 | 550.7 | 145.4 | 227 | 225.1 | 185.7 | 141.2 | 228 | 226.5 | 162.2
582 | 361 | 475.4 | 190.16 | 222.2861 | 219.7 | 210.8 | 227.4 | 232.5 | 364.4 | 35.2 | 20.6 | 68.7 | 4.6 | 225.8 | 5.5 | 77.3 | 88.9 | 618 | 761 | 152.4 | 167.6 | 669.1 | 889.7 | 763.2 | 196.7 | 420 | 538 | 256.8 | 417.7 | 587.6 | 189.8 | 551.5 | 145.6 | 226.8 | 225.2 | 185.9 | 141.6 | 227.8 | 226.6 | 162.4
583 | 362 | 475.6 | 190.24 | 222.3796 | 219.2 | 210.4 | 227.1 | 232.3 | 364.3 | 35.3 | 20.6 | 68.8 | 4.5 | 254.2 | 5.8 | 77.5 | 89 | 621.9 | 762.4 | 152.8 | 167.6 | 667.7 | 882.5 | 763.5 | 197.3 | 421 | 542.5 | 257.7 | 419.2 | 588.3 | 190.4 | 552.3 | 145.9 | 226.9 | 225.6 | 186.1 | 141.9 | 227.5 | 226.9 | 162.6
584 | 363 | 476.1 | 190.44 | 222.6134 | 219.2 | 211.5 | 226.6 | 232.2 | 363.8 | 35.4 | 20.6 | 68.8 | 3.7 | 251.8 | 6.3 | 77.7 | 89.2 | 624.2 | 760 | 153.2 | 167.7 | 678 | 888.4 | 763.3 | 197.8 | 419.8 | 534.8 | 258.6 | 422.7 | 589.5 | 190.9 | 552.4 | 146.1 | 226.8 | 225.9 | 186.3 | 142.3 | 227.3 | 226.9 | 163
585 | 364 | 475.5 | 190.2 | 222.3328 | 219.3 | 212.4 | 226.5 | 232.4 | 366.1 | 35.6 | 20.5 | 68.8 | 3.7 | 249.2 | 6.3 | 77.8 | 89.3 | 624.6 | 763.5 | 153.6 | 167.8 | 676.1 | 886.4 | 764.8 | 198.4 | 419.5 | 530.2 | 259.5 | 426.2 | 589.6 | 191.6 | 552 | 146.4 | 226.7 | 225.7 | 186.6 | 142.7 | 227.3 | 227.1 | 163.3
586 | 365 | 477.8 | 191.12 | 223.4083 | 220.4 | 212.5 | 226.7 | 232 | 369.8 | 35.7 | 20.5 | 68.8 | 3.6 | 246.6 | 6.1 | 78 | 89.5 | 633.3 | 762.2 | 154 | 167.8 | 682.5 | 891.7 | 765.9 | 199 | 417.7 | 528.8 | 260.3 | 429.9 | 591.8 | 192.4 | 551.8 | 146.6 | 226.7 | 225.5 | 186.8 | 143 | 227.5 | 227.4 | 163.7
587 | 366 | 480.1 | 192.04 | 224.4837 | 220.1 | 212.1 | 226.4 | 231.7 | 368.6 | 35.8 | 20.5 | 68.8 | 3.7 | 234.8 | 6.6 | 78.2 | 89.7 | 634.5 | 764.6 | 154.4 | 167.9 | 694.9 | 897.1 | 767.5 | 199.5 | 417.9 | 534.9 | 260.8 | 432.6 | 594 | 193.1 | 552.2 | 146.9 | 226.8 | 225.7 | 186.8 | 143.3 | 227.9 | 227.6 | 164
588 | 367 | 477.6 | 191.04 | 223.3148 | 219.5 | 212.2 | 226.4 | 232.4 | 367.4 | 35.8 | 20.5 | 68.9 | 4.6 | 215.3 | 6.9 | 78.4 | 89.9 | 642 | 757.1 | 154.8 | 168 | 713.5 | 898 | 767 | 200.1 | 418.2 | 540.6 | 261.2 | 435.5 | 592.4 | 194 | 552.8 | 147.1 | 226.8 | 225.8 | 187.1 | 143.7 | 228.4 | 227.9 | 164.6
589 | 368 | 477.3 | 190.92 | 223.1745 | 219.5 | 212.5 | 227 | 232.9 | 371 | 35.9 | 20.5 | 69 | 4.4 | 226.8 | 7.1 | 78.5 | 90.1 | 644.9 | 760.1 | 155.2 | 168.1 | 723.8 | 898.8 | 767.1 | 200.6 | 419.9 | 548 | 261.8 | 434.6 | 597.7 | 195.3 | 553.7 | 147.4 | 227 | 226.2 | 187.7 | 144 | 228.9 | 228.2 | 164.9
590 | 369 | 479 | 191.6 | 223.9694 | 218.9 | 213.1 | 227.5 | 234.1 | 369 | 36 | 20.5 | 69 | 4.3 | 240.2 | 7.5 | 78.7 | 90.3 | 649.1 | 758.8 | 155.6 | 168.2 | 723.5 | 879.8 | 768.1 | 201.2 | 422.9 | 572.9 | 262.4 | 434.2 | 605.2 | 196.6 | 555.1 | 147.6 | 227 | 226.3 | 187.8 | 144.3 | 229 | 228.2 | 165.1
591 | 370 | 478 | 191.2 | 223.5018 | 218.1 | 213.6 | 227.8 | 234.2 | 370.4 | 36.1 | 20.5 | 69.1 | 4.3 | 247.1 | 7.5 | 78.9 | 90.6 | 647.2 | 753.6 | 155.9 | 168.3 | 731.3 | 866.5 | 768 | 201.8 | 426.8 | 581.1 | 263 | 436.8 | 608.9 | 198 | 556.5 | 147.8 | 227.3 | 226.6 | 188.1 | 144.6 | 228.9 | 228.2 | 165.4
592 | 371 | 477.2 | 190.88 | 223.1277 | 217.5 | 213.7 | 228.2 | 233.9 | 370.6 | 36.1 | 20.5 | 69.2 | 4.2 | 244.3 | 7.8 | 79.1 | 90.7 | 639.1 | 749.6 | 156.3 | 168.4 | 739.5 | 868.1 | 768.7 | 202.3 | 426.4 | 571.5 | 263.6 | 438.7 | 608.7 | 199.4 | 557.1 | 148 | 227.4 | 226.6 | 188.2 | 144.9 | 228.6 | 228.3 | 165.6
593 | 372 | 476.8 | 190.72 | 222.9407 | 217.6 | 213.3 | 228.2 | 234 | 370.7 | 36.2 | 20.5 | 69.3 | 4.3 | 243.1 | 7.6 | 79.3 | 90.9 | 648.8 | 761.7 | 156.7 | 168.5 | 749.1 | 863.2 | 769 | 202.9 | 428.9 | 577.5 | 264.2 | 441.6 | 618.2 | 201.2 | 558.9 | 148.3 | 227.5 | 226.5 | 188.5 | 145.2 | 228.5 | 228.4 | 165.8
594 | 373 | 477.5 | 191 | 223.268 | 219.1 | 212.8 | 228.7 | 233.9 | 377.8 | 36.3 | 20.5 | 69.3 | 4.1 | 245.9 | 7.1 | 79.5 | 91.1 | 658.2 | 773.3 | 157.1 | 168.7 | 744.8 | 847.7 | 769.1 | 203.4 | 433 | 595 | 264.9 | 435.9 | 606.8 | 202.5 | 559 | 148.5 | 227.8 | 226.7 | 189 | 145.5 | 228.1 | 228.5 | 166
595 | 374 | 477.8 | 191.12 | 223.4083 | 220.3 | 213 | 230.1 | 233.8 | 385.7 | 36.3 | 20.5 | 69.4 | 4.3 | 240.4 | 7.2 | 79.7 | 91.4 | 652.1 | 785.1 | 157.5 | 168.8 | 745.3 | 826 | 768.7 | 204 | 438.1 | 612.8 | 265.5 | 429.9 | 596.3 | 203.7 | 558.9 | 148.7 | 228.2 | 227.1 | 189.8 | 145.8 | 227.8 | 228.8 | 166.2
596 | 375 | 477.6 | 191.04 | 223.3148 | 220 | 213.7 | 232.6 | 233.3 | 391.3 | 36.4 | 20.5 | 69.5 | 4.2 | 241.7 | 7.3 | 79.9 | 91.7 | 634.8 | 784.8 | 157.9 | 168.9 | 750.9 | 831.5 | 768.7 | 204.5 | 440.1 | 615.7 | 266.2 | 425.8 | 592 | 204.8 | 559.3 | 149 | 228.5 | 227.6 | 190.4 | 146.1 | 227.7 | 228.9 | 166.6
597 | 376 | 477.9 | 191.16 | 223.455 | 220.1 | 214.9 | 233.8 | 232.4 | 390.2 | 36.4 | 20.5 | 69.5 | 4.3 | 241.2 | 7.4 | 80.1 | 92.1 | 619.3 | 782.4 | 158.3 | 169 | 756.2 | 835.1 | 768.5 | 205.1 | 440.7 | 620.2 | 266.8 | 426.4 | 597.1 | 205.8 | 561 | 149.2 | 228.9 | 228.1 | 190.8 | 146.4 | 228.1 | 228.7 | 166.9
598 | 377 | 478.3 | 191.32 | 223.6421 | 219.9 | 215.9 | 234.2 | 231.9 | 387.9 | 36.4 | 20.5 | 69.7 | 4.1 | 242.3 | 7.9 | 80.3 | 92.3 | 610.9 | 786.4 | 158.7 | 169.2 | 740 | 841.9 | 769 | 205.6 | 441.7 | 625.5 | 267.4 | 424.1 | 595.8 | 206.3 | 562.2 | 149.4 | 229.5 | 228.5 | 191.2 | 146.6 | 228.1 | 228.6 | 167.1
599 | 378 | 476.1 | 190.44 | 222.6134 | 220.3 | 216.8 | 234.7 | 231.8 | 385.9 | 36.4 | 20.5 | 69.8 | 3.8 | 243.4 | 8.2 | 80.5 | 92.5 | 603.9 | 787.5 | 159.1 | 169.3 | 734.9 | 849.7 | 770 | 206.1 | 444 | 629.4 | 268 | 425.1 | 593.7 | 206.7 | 563.9 | 149.7 | 229.7 | 228.7 | 191.4 | 146.9 | 227.9 | 228.5 | 167.4
600 | 379 | 473.5 | 189.4 | 221.3977 | 221.5 | 217.7 | 234.9 | 231.4 | 382.4 | 36.4 | 20.5 | 69.9 | 3.8 | 244.6 | 8.1 | 80.7 | 92.6 | 603.9 | 784.2 | 159.5 | 169.4 | 738.1 | 849.7 | 770 | 206.7 | 445.3 | 631.9 | 268.6 | 426.3 | 594 | 207.1 | 563.9 | 149.9 | 230 | 229 | 191.8 | 147.2 | 227.7 | 228.4 | 167.7
601 | 380 | 475.1 | 190.04 | 222.1458 | 223.2 | 218 | 234.4 | 230.5 | 380.7 | 36.4 | 20.5 | 70 | 3.9 | 243.8 | 8.1 | 80.8 | 92.8 | 613.9 | 778.1 | 159.9 | 169.6 | 741.7 | 847.3 | 769.3 | 207.2 | 446.4 | 629 | 269.2 | 426.5 | 588.6 | 207.2 | 563.9 | 150.2 | 230.4 | 229.7 | 192.5 | 147.4 | 227.9 | 228.5 | 168.1
602 | 381 | 475.3 | 190.12 | 222.2393 | 223.4 | 217.6 | 235 | 229.8 | 378.9 | 36.5 | 20.5 | 70 | 3.7 | 238.2 | 8.1 | 81 | 93 | 630 | 785.2 | 160.3 | 169.7 | 743.6 | 842.9 | 768.9 | 207.7 | 451 | 649.6 | 269.7 | 424.4 | 585 | 207.3 | 566.3 | 150.4 | 230.9 | 230.2 | 192.4 | 147.6 | 228.1 | 228.7 | 168.4
603 | 382 | 474.7 | 189.88 | 221.9588 | 223 | 217.5 | 235 | 229.8 | 385.8 | 36.5 | 20.5 | 69.9 | 4 | 243.3 | 7.7 | 81.2 | 93.2 | 626.4 | 788.6 | 160.7 | 169.9 | 735.3 | 830.6 | 769.4 | 208.3 | 453.3 | 642.2 | 270.4 | 421.3 | 576.1 | 207.1 | 565.8 | 150.6 | 231.6 | 230.6 | 192.6 | 147.9 | 228 | 228.8 | 168.5
604 | 383 | 476.4 | 190.56 | 222.7537 | 223 | 217.3 | 235.1 | 229.9 | 385.5 | 36.6 | 20.5 | 69.9 | 3.5 | 218 | 6.9 | 81.4 | 93.4 | 635 | 782.7 | 161.1 | 170.1 | 729.1 | 837.2 | 770.2 | 208.8 | 451.3 | 636.3 | 271 | 421.8 | 582.6 | 206.9 | 565.7 | 150.9 | 232.5 | 230.9 | 192.6 | 148.1 | 228.2 | 228.6 | 169
605 | 384 | 477 | 190.8 | 223.0342 | 222.7 | 217.6 | 235.6 | 229.7 | 381.7 | 36.7 | 20.5 | 70 | 4 | 246.5 | 6.4 | 81.6 | 93.6 | 649.1 | 776.4 | 161.4 | 170.2 | 721.8 | 831.9 | 770.3 | 209.3 | 452.7 | 634.9 | 271.8 | 422.4 | 585.1 | 206.9 | 566.6 | 151.1 | 233 | 231.4 | 192.8 | 148.3 | 228.2 | 228.7 | 169.3
606 | 385 | 476.4 | 190.56 | 222.7537 | 221.5 | 217.2 | 235.6 | 229.7 | 375.8 | 36.8 | 20.5 | 70 | 3.8 | 254.9 | 6.4 | 81.8 | 93.6 | 653.3 | 773.6 | 161.8 | 170.4 | 719.5 | 836.8 | 769.2 | 209.8 | 449.7 | 624.6 | 272.7 | 421.6 | 581.7 | 206.7 | 566 | 151.4 | 233.2 | 231.4 | 193.1 | 148.5 | 228.1 | 228.8 | 169.5
607 | 386 | 476.5 | 190.6 | 222.8004 | 221 | 216.7 | 235.4 | 230.3 | 371.8 | 36.8 | 20.5 | 70.1 | 3.8 | 249.2 | 6.1 | 82 | 93.7 | 654.8 | 770.7 | 162.2 | 170.6 | 714.6 | 837.5 | 768.8 | 210.3 | 448.9 | 613.1 | 273.3 | 423.5 | 585.5 | 206.8 | 566.5 | 151.7 | 233.3 | 231.4 | 193 | 148.7 | 227.9 | 229 | 169.8
608 | 387 | 477.7 | 191.08 | 223.3615 | 220.7 | 216.2 | 235.5 | 231.2 | 370.1 | 36.8 | 20.5 | 70.1 | 4.1 | 247.3 | 5.5 | 82.1 | 93.9 | 653.7 | 757.7 | 162.6 | 170.8 | 717.1 | 837.3 | 767.7 | 210.8 | 446.1 | 597.7 | 273.9 | 424 | 583.8 | 206.8 | 567.1 | 151.9 | 233.3 | 231.3 | 193.1 | 149 | 228.4 | 229.1 | 170.2
609 | 388 | 477.9 | 191.16 | 223.455 | 219.4 | 215.2 | 236 | 231.2 | 373.9 | 36.9 | 20.5 | 70.2 | 4.1 | 258.2 | 5.1 | 82.3 | 94 | 649.7 | 748.8 | 163 | 171 | 707.4 | 845.2 | 767.3 | 211.3 | 442.2 | 583 | 274.5 | 425.5 | 582.1 | 207.3 | 566.3 | 152.2 | 233.2 | 231.2 | 193.4 | 149.2 | 228.7 | 229.2 | 170.6
610 | 389 | 477.6 | 191.04 | 223.3148 | 219.4 | 213.8 | 235.5 | 231.2 | 373.8 | 37 | 20.5 | 70.2 | 4 | 244.6 | 5 | 82.5 | 94.1 | 645 | 744.4 | 163.4 | 171.2 | 707.2 | 851.8 | 766.7 | 211.9 | 438.8 | 570.5 | 275.1 | 428.9 | 582.9 | 207.8 | 565.2 | 152.4 | 233.1 | 231 | 193.4 | 149.4 | 228.9 | 229.4 | 170.8
611 | 390 | 476.9 | 190.76 | 222.9874 | 220.8 | 214 | 235 | 231.7 | 373.2 | 37 | 20.5 | 70.2 | 4 | 249.3 | 5.7 | 82.7 | 94.3 | 651 | 750.4 | 163.7 | 171.3 | 716.3 | 848.7 | 767.4 | 212.4 | 435.9 | 572.3 | 275.6 | 429.9 | 591.2 | 208 | 565.5 | 152.6 | 233.1 | 231.1 | 193.5 | 149.7 | 229.3 | 229.7 | 171.1
612 | 391 | 475.4 | 190.16 | 222.2861 | 221.7 | 213.8 | 234.4 | 232.6 | 371.9 | 37 | 20.5 | 70.3 | 4.4 | 255.9 | 6.2 | 82.9 | 94.5 | 662.1 | 766.4 | 164.1 | 171.6 | 714.5 | 834.4 | 767.8 | 212.9 | 441.1 | 585.8 | 276.2 | 426.4 | 588.6 | 208 | 565.4 | 152.9 | 233.1 | 231.3 | 193.9 | 149.9 | 229.6 | 230.2 | 171.3
613 | 392 | 475.8 | 190.32 | 222.4731 | 221.9 | 213.4 | 234.1 | 233 | 377.6 | 37 | 20.5 | 70.3 | 4.2 | 258.9 | 6.4 | 83 | 94.6 | 662.2 | 772.2 | 164.5 | 171.8 | 714.2 | 811 | 766.7 | 213.4 | 448.1 | 599 | 277 | 423.1 | 577.1 | 207.8 | 564.9 | 153.2 | 233.3 | 231.7 | 194.7 | 150.2 | 229.6 | 230.5 | 171.5
614 | 393 | 475.8 | 190.32 | 222.4731 | 222.5 | 212.6 | 235.8 | 233.3 | 386.5 | 36.9 | 20.5 | 70.4 | 4.1 | 253.5 | 6.4 | 83.2 | 94.8 | 665.1 | 768.3 | 164.9 | 172 | 707.4 | 790.8 | 764.8 | 213.9 | 448.8 | 599.1 | 277.7 | 417.6 | 564.5 | 207.5 | 564.1 | 153.4 | 233.7 | 232.1 | 195.3 | 150.4 | 229.3 | 230.3 | 171.6
615 | 394 | 475.4 | 190.16 | 222.2861 | 223.1 | 212.4 | 237.4 | 233.7 | 386.4 | 36.8 | 20.5 | 70.4 | 3.9 | 241.6 | 6.4 | 83.4 | 94.9 | 662.3 | 770.7 | 165.3 | 172.2 | 695.2 | 764.4 | 762.6 | 214.4 | 447.4 | 601.7 | 278.5 | 411.7 | 551.4 | 207.1 | 562.2 | 153.7 | 234.3 | 232.7 | 195.8 | 150.7 | 229 | 230 | 171.8
616 | 395 | 476.3 | 190.52 | 222.7069 | 223.5 | 213.5 | 240.2 | 233.2 | 386.6 | 36.8 | 20.5 | 70.5 | 3.3 | 240.5 | 6.2 | 83.5 | 95.1 | 651.7 | 772.5 | 165.6 | 172.4 | 679.6 | 751.7 | 761.3 | 214.9 | 446.6 | 598 | 279.4 | 407.2 | 539.9 | 206.7 | 560.6 | 153.9 | 235.3 | 233.4 | 196.2 | 150.9 | 228.5 | 229.8 | 172.1
617 | 396 | 475.9 | 190.36 | 222.5199 | 223.8 | 215.1 | 244 | 232.8 | 385.9 | 36.8 | 20.5 | 70.6 | 3.8 | 237.1 | 6.5 | 83.7 | 95.2 | 639.6 | 770.7 | 166 | 172.7 | 671.4 | 743.7 | 761 | 215.4 | 442.4 | 591.3 | 280.2 | 402.3 | 527.7 | 206.1 | 559 | 154.2 | 236 | 234 | 196.5 | 151.1 | 228.1 | 229.6 | 172.3
618 | 397 | 476.5 | 190.6 | 222.8004 | 224.1 | 216.9 | 245 | 232.7 | 387.1 | 36.9 | 20.5 | 70.7 | 3.6 | 241.2 | 6.7 | 83.9 | 95.4 | 631.5 | 774 | 166.4 | 172.9 | 663.6 | 739.2 | 759.3 | 215.9 | 439.9 | 583.3 | 281 | 396 | 514.8 | 205.6 | 557.4 | 154.5 | 236.8 | 234.6 | 196.7 | 151.4 | 228.3 | 229.4 | 172.6
619 | 398 | 475.6 | 190.24 | 222.3796 | 224 | 217.4 | 245.7 | 232.5 | 393.1 | 36.9 | 20.5 | 70.8 | 3.7 | 244.4 | 7 | 84.1 | 95.5 | 622 | 777.9 | 166.8 | 173.1 | 655.3 | 720.7 | 759 | 216.4 | 438.3 | 580.2 | 281.7 | 390.1 | 504.5 | 205.1 | 555.3 | 154.7 | 236.9 | 234.9 | 196.8 | 151.6 | 228 | 229.4 | 172.7
620 | 399 | 476 | 190.4 | 222.5666 | 223.6 | 218 | 246.4 | 232.2 | 397.4 | 37 | 20.5 | 71 | 4.1 | 240.4 | 7.1 | 84.3 | 95.7 | 619 | 778.8 | 167.1 | 173.4 | 644.7 | 707.1 | 757.7 | 216.9 | 436.1 | 584.4 | 282.2 | 385.9 | 496.3 | 204.7 | 553.5 | 155 | 237 | 235.2 | 197.1 | 151.8 | 227.7 | 229.4 | 172.9
621 | 400 | 475.5 | 190.2 | 222.3328 | 223.5 | 218.3 | 246.4 | 231.4 | 400.4 | 37 | 20.5 | 71.1 | 4.1 | 247.3 | 7.1 | 84.4 | 95.8 | 619.5 | 781.7 | 167.5 | 173.6 | 647 | 717.6 | 757.3 | 217.4 | 435.8 | 591.3 | 282.8 | 383.5 | 494.5 | 204.3 | 552.7 | 155.2 | 237 | 235.6 | 197.4 | 152.1 | 227.4 | 229.5 | 173.2
622 | 401 | 477.3 | 190.92 | 223.1745 | 224.1 | 218.7 | 245.9 | 231.1 | 400 | 37.1 | 20.5 | 71.2 | 4 | 247.1 | 7 | 84.6 | 95.9 | 615.3 | 784.5 | 167.9 | 173.9 | 649.3 | 728.5 | 757.6 | 217.9 | 438.4 | 596 | 283.5 | 383.1 | 494.2 | 204.1 | 552.2 | 155.5 | 237 | 236.1 | 197.7 | 152.3 | 227.4 | 229.4 | 173.4
623 | 402 | 477.1 | 190.84 | 223.081 | 223.9 | 220.3 | 245.3 | 230.5 | 399.3 | 37.2 | 20.5 | 71.2 | 4.2 | 246.8 | 7 | 84.8 | 96.1 | 608.5 | 784.6 | 168.3 | 174.2 | 649.1 | 729.2 | 755.6 | 218.4 | 441.2 | 595.9 | 284.3 | 380.1 | 489.1 | 203.8 | 551.5 | 155.8 | 237 | 236.2 | 198 | 152.5 | 227.4 | 229.5 | 173.6
624 | 403 | 476.9 | 190.76 | 222.9874 | 224.5 | 221.5 | 244.9 | 230.7 | 401.1 | 37.2 | 20.5 | 71.3 | 4.2 | 241.3 | 6.9 | 85 | 96.2 | 601.8 | 789.7 | 168.7 | 174.4 | 646.1 | 750.2 | 754.3 | 218.9 | 440.9 | 599.3 | 285.2 | 379.2 | 489.1 | 203.6 | 550.7 | 156.1 | 237 | 236.4 | 198 | 152.7 | 227.1 | 229.4 | 173.8
625 | 404 | 477.4 | 190.96 | 223.2212 | 224.5 | 222.3 | 245.3 | 230.8 | 401.9 | 37.3 | 20.5 | 71.4 | 3.6 | 240.5 | 6.4 | 85.2 | 96.4 | 600.9 | 790.9 | 169 | 174.7 | 637.7 | 755.7 | 755.3 | 219.4 | 441.6 | 597.8 | 286.1 | 377.5 | 484.5 | 203.4 | 550.2 | 156.3 | 237 | 236.4 | 198.1 | 152.9 | 227.1 | 229.4 | 174.1
626 | 405 | 477.5 | 191 | 223.268 | 223.7 | 222.5 | 246.1 | 230.5 | 398.1 | 37.3 | 20.5 | 71.4 | 3.5 | 240.2 | 5.8 | 85.3 | 96.5 | 606.8 | 787 | 169.4 | 175 | 639.7 | 768.1 | 756.4 | 219.9 | 438 | 588.6 | 287 | 377 | 485.5 | 203.3 | 549.5 | 156.6 | 237.5 | 236.3 | 198.1 | 153.1 | 227.4 | 229.3 | 174.4
627 | 406 | 477.2 | 190.88 | 223.1277 | 223 | 222.8 | 246.1 | 230.1 | 395.7 | 37.3 | 20.5 | 71.5 | 3.8 | 240.6 | 5.6 | 85.5 | 96.8 | 616.5 | 788 | 169.8 | 175.3 | 642.7 | 770.6 | 757 | 220.4 | 438.6 | 591 | 287.9 | 378.3 | 490.7 | 203.1 | 549.5 | 156.8 | 237.6 | 236.4 | 198.2 | 153.3 | 227.9 | 229.3 | 174.8
628 | 407 | 477.2 | 190.88 | 223.1277 | 221.5 | 223.2 | 246.5 | 230 | 397.5 | 37.3 | 20.5 | 71.6 | 3.9 | 249 | 5.4 | 85.7 | 97 | 619 | 791.9 | 170.2 | 175.6 | 644.3 | 759.5 | 758 | 220.9 | 440.4 | 595.9 | 288.8 | 377.1 | 490.5 | 203 | 550 | 157.1 | 237.9 | 236.7 | 198.7 | 153.5 | 228 | 229.4 | 175
629 | 408 | 477.1 | 190.84 | 223.081 | 220.1 | 224.1 | 246.8 | 230 | 401.1 | 37.4 | 20.5 | 71.7 | 3.7 | 245.3 | 5.2 | 85.8 | 97.3 | 617.1 | 789.7 | 170.5 | 175.9 | 640.6 | 751 | 758.1 | 221.4 | 441.6 | 602.7 | 289.6 | 374 | 487 | 202.9 | 549.7 | 157.3 | 238.4 | 236.9 | 199.4 | 153.7 | 227.9 | 229.5 | 175.1
630 | 409 | 476.9 | 190.76 | 222.9874 | 219.1 | 224.9 | 247.9 | 230.2 | 403.3 | 37.5 | 20.5 | 71.8 | 4 | 240.3 | 5.1 | 86 | 97.5 | 610.7 | 791.3 | 170.9 | 176.1 | 629.3 | 739 | 757.6 | 221.9 | 441.8 | 603.5 | 290.3 | 372.7 | 487.4 | 202.7 | 548.7 | 157.6 | 239 | 237.1 | 199.9 | 153.9 | 227.7 | 229.5 | 175.2
631 | 410 | 476.2 | 190.48 | 222.6601 | 219 | 225.5 | 249.1 | 229.6 | 408.4 | 37.6 | 20.5 | 71.9 | 4.1 | 235.5 | 5.1 | 86.1 | 97.6 | 608.5 | 792.8 | 171.3 | 176.4 | 625.8 | 717 | 755.2 | 222.4 | 442.7 | 598.4 | 291 | 369.4 | 479.4 | 202.6 | 547 | 157.9 | 240.1 | 237.5 | 200.3 | 154.1 | 227.5 | 229.7 | 175.4
632 | 411 | 476.3 | 190.52 | 222.7069 | 219.7 | 226.7 | 250 | 229.5 | 414.3 | 37.7 | 20.5 | 72 | 4.2 | 239.1 | 5.4 | 86.3 | 97.8 | 598.2 | 788.8 | 171.7 | 176.7 | 632.6 | 721.4 | 753.9 | 222.9 | 444.2 | 593 | 291.6 | 367 | 473.3 | 202.5 | 545.7 | 158.1 | 241.3 | 238.5 | 201 | 154.3 | 227.3 | 229.7 | 175.6
633 | 412 | 476.8 | 190.72 | 222.9407 | 220.4 | 228.1 | 251.1 | 229.6 | 417.9 | 37.8 | 20.5 | 72.1 | 4.3 | 241.7 | 5.4 | 86.5 | 98 | 596.5 | 783.2 | 172.1 | 177 | 628.9 | 701.9 | 751.5 | 223.4 | 446 | 594.2 | 292.2 | 366.1 | 469.7 | 202.4 | 544.8 | 158.4 | 242 | 239.4 | 201.7 | 154.5 | 227.2 | 229.7 | 175.8
634 | 413 | 476 | 190.4 | 222.5666 | 221.3 | 228.6 | 253 | 229.6 | 419.2 | 37.8 | 20.5 | 72.2 | 4.4 | 240.8 | 5.3 | 86.6 | 98.1 | 598.2 | 776.6 | 172.4 | 177.3 | 617.3 | 679 | 750 | 223.9 | 446 | 596.7 | 292.9 | 364.1 | 464.4 | 202.3 | 543.6 | 158.7 | 242.7 | 240.6 | 202.4 | 154.7 | 227.2 | 229.8 | 176.1
635 | 414 | 476.4 | 190.56 | 222.7537 | 222.3 | 228.3 | 255.1 | 229.6 | 416.2 | 37.9 | 20.5 | 72.2 | 4.2 | 243.7 | 5 | 86.8 | 98.3 | 596.4 | 777.6 | 172.8 | 177.6 | 605.9 | 672.8 | 750.3 | 224.4 | 444.7 | 605.5 | 293.5 | 364.5 | 467 | 202.1 | 543.7 | 159 | 243.5 | 241.3 | 202.6 | 154.8 | 227.1 | 229.9 | 176.3
636 | 415 | 475.9 | 190.36 | 222.5199 | 223.4 | 228.7 | 257.7 | 229.6 | 415.5 | 37.9 | 20.5 | 72.3 | 3.9 | 225.3 | 4.6 | 87 | 98.5 | 595 | 776 | 173.2 | 177.9 | 593.5 | 664.9 | 748.8 | 224.9 | 446.1 | 606.3 | 294 | 364.2 | 461.7 | 202.1 | 543.6 | 159.3 | 244.5 | 242 | 202.9 | 155 | 227 | 230.1 | 176.5
637 | 416 | 476.4 | 190.56 | 222.7537 | 226.5 | 228.5 | 258.8 | 230.4 | 421 | 38 | 20.4 | 72.3 | 4.2 | 213.5 | 4.3 | 87.1 | 98.6 | 596.7 | 766.9 | 173.6 | 178.2 | 589.2 | 637.9 | 745.7 | 225.3 | 447.5 | 598.9 | 294.5 | 362.9 | 456.7 | 202 | 542.2 | 159.6 | 245 | 242.6 | 203.2 | 155.2 | 227.2 | 230.2 | 176.7
638 | 417 | 476.3 | 190.52 | 222.7069 | 228.5 | 229 | 260 | 231.4 | 427.4 | 38.1 | 20.4 | 72.4 | 3.9 | 232.7 | 4.5 | 87.3 | 98.7 | 591.9 | 753.1 | 174 | 178.5 | 582.5 | 605 | 742.6 | 225.8 | 447.8 | 591 | 294.9 | 361 | 451.9 | 201.9 | 540.8 | 159.9 | 245.7 | 243.3 | 203.4 | 155.4 | 227.2 | 230.3 | 176.8
639 | 418 | 476.5 | 190.6 | 222.8004 | 229.3 | 229.4 | 260 | 232.2 | 429.4 | 38.1 | 20.4 | 72.5 | 4 | 233.6 | 4.3 | 87.5 | 98.8 | 583.1 | 745.2 | 174.3 | 178.8 | 569.6 | 593.9 | 740.3 | 226.3 | 444 | 578.7 | 295.4 | 357.8 | 444.8 | 201.7 | 539 | 160.1 | 246.4 | 243.9 | 203.7 | 155.5 | 227.1 | 230.5 | 177
640 | 419 | 477.3 | 190.92 | 223.1745 | 229.4 | 229.9 | 260.8 | 233.4 | 426.3 | 38.1 | 20.4 | 72.6 | 3.6 | 244.9 | 3.8 | 87.7 | 99 | 579.4 | 748.3 | 174.7 | 179.1 | 566.5 | 593.3 | 738.4 | 226.8 | 442.6 | 573.5 | 296 | 354.7 | 444.3 | 201.6 | 537.8 | 160.5 | 247.2 | 244.8 | 204.1 | 155.7 | 227.1 | 230.9 | 177.3
641 | 420 | 478.6 | 191.44 | 223.7823 | 229.5 | 230 | 262.2 | 234.9 | 429.3 | 38.1 | 20.4 | 72.7 | 4 | 265.1 | 3.5 | 87.8 | 99.1 | 582.3 | 758.4 | 175.1 | 179.5 | 554.2 | 619.7 | 738.8 | 227.3 | 444.4 | 580.7 | 296.7 | 354.3 | 446.4 | 201.5 | 538.1 | 160.8 | 247.9 | 245.5 | 204.5 | 155.9 | 227.2 | 231.3 | 177.5
642 | 421 | 477.7 | 191.08 | 223.3615 | 231 | 229.5 | 261.9 | 236 | 424.1 | 38.1 | 20.4 | 72.7 | 3.7 | 273.1 | 3.2 | 88 | 99.3 | 589.3 | 759.9 | 175.5 | 179.8 | 553.5 | 647.8 | 739.8 | 227.8 | 441.5 | 581 | 297.3 | 354.7 | 449.5 | 201.3 | 537.7 | 161.1 | 248.9 | 245.9 | 204.6 | 156.1 | 227.3 | 231.5 | 177.7
643 | 422 | 477.5 | 191 | 223.268 | 232 | 229.6 | 261.2 | 236.7 | 416.6 | 38 | 20.4 | 72.8 | 3.8 | 270 | 3.2 | 88.2 | 99.5 | 591.5 | 763.9 | 175.8 | 180.1 | 564.2 | 685 | 740.8 | 228.3 | 440.8 | 592.7 | 297.9 | 358.8 | 470.4 | 201.3 | 539.7 | 161.4 | 249.2 | 246.1 | 204.4 | 156.3 | 227.3 | 231.6 | 178.1
644 | 423 | 477.4 | 190.96 | 223.2212 | 231.9 | 229.1 | 260.5 | 237 | 410.2 | 38 | 20.4 | 72.8 | 4 | 260.8 | 3.5 | 88.3 | 99.6 | 596.9 | 769.1 | 176.2 | 180.4 | 569.3 | 719.9 | 742.6 | 228.8 | 445.7 | 609.7 | 298.5 | 362.6 | 479.9 | 201.2 | 541.4 | 161.8 | 249.8 | 246.4 | 204.5 | 156.5 | 227.5 | 231.7 | 178.2
645 | 424 | 478.3 | 191.32 | 223.6421 | 231.7 | 227.4 | 259.2 | 236.8 | 405.7 | 38 | 20.4 | 72.9 | 4.2 | 256.3 | 3.6 | 88.5 | 99.7 | 613.5 | 767.8 | 176.6 | 180.7 | 579.7 | 723.6 | 742.6 | 229.2 | 448.6 | 608.5 | 299.1 | 364.9 | 478.6 | 201.1 | 541.7 | 162.1 | 250.2 | 246.6 | 204.7 | 156.6 | 227.6 | 231.9 | 178.4
646 | 425 | 478 | 191.2 | 223.5018 | 230.9 | 226.2 | 257.6 | 236.6 | 404.9 | 38 | 20.4 | 73 | 4.7 | 249.2 | 3.2 | 88.7 | 99.9 | 616.1 | 771.7 | 177 | 181 | 590.3 | 717.5 | 742.3 | 229.7 | 451.1 | 612.1 | 299.6 | 366.6 | 485.7 | 201.1 | 542.5 | 162.4 | 250.6 | 246.9 | 205.1 | 156.8 | 227.7 | 232 | 178.8
647 | 426 | 478 | 191.2 | 223.5018 | 231.3 | 224.9 | 256.5 | 236.1 | 406.5 | 38 | 20.4 | 73 | 4.2 | 242 | 3.1 | 88.8 | 100 | 612.7 | 771.8 | 177.3 | 181.4 | 590.8 | 729.7 | 743.5 | 230.2 | 449.7 | 609.8 | 300.1 | 368.1 | 484.5 | 201 | 542 | 162.8 | 250.7 | 246.9 | 205.4 | 157 | 227.8 | 232 | 179
648 | 427 | 476.5 | 190.6 | 222.8004 | 231.2 | 223.6 | 256.4 | 235.6 | 400.5 | 38 | 20.4 | 73 | 3.9 | 234.7 | 3.4 | 89 | 100.1 | 613.6 | 772.6 | 177.7 | 181.7 | 604.3 | 766.7 | 744.9 | 230.7 | 448.5 | 618.7 | 300.6 | 374.8 | 505.7 | 200.9 | 544.2 | 163.2 | 250.4 | 246.7 | 205.3 | 157.2 | 227.9 | 232.4 | 179.2
649 | 428 | 473.3 | 189.32 | 221.3042 | 231.5 | 223.2 | 256 | 235.2 | 396.4 | 38 | 20.4 | 73 | 4.1 | 225.3 | 3.6 | 89.2 | 100.4 | 613.7 | 773.7 | 178.1 | 182 | 624.7 | 799.8 | 746.9 | 231.2 | 448.3 | 617 | 301 | 385.6 | 521.9 | 200.9 | 546 | 163.5 | 250.1 | 246.4 | 205.2 | 157.4 | 228.1 | 232.5 | 179.5
650 | 429 | 474.8 | 189.92 | 222.0055 | 230.7 | 223.4 | 254.7 | 235 | 393 | 37.9 | 20.4 | 73 | 4.6 | 234.7 | 4 | 89.3 | 100.6 | 612.3 | 772.4 | 178.4 | 182.3 | 636.9 | 813.9 | 749.4 | 231.7 | 445.7 | 611.7 | 301.4 | 387.3 | 522.1 | 200.8 | 545.7 | 163.8 | 249.6 | 246.3 | 205.3 | 157.6 | 228.7 | 232.8 | 179.9
651 | 430 | 475 | 190 | 222.0991 | 229.3 | 223.2 | 252.9 | 234.4 | 389 | 37.9 | 20.4 | 73 | 4.2 | 241.7 | 4.6 | 89.5 | 100.7 | 613.2 | 767.9 | 178.8 | 182.7 | 653.3 | 833.8 | 750.4 | 232.1 | 442.9 | 597.7 | 301.9 | 398 | 538.3 | 200.7 | 546.3 | 164.2 | 249.2 | 246.1 | 205.7 | 157.8 | 229.2 | 233.3 | 180.2
652 | 431 | 476.7 | 190.68 | 222.8939 | 228.6 | 222.7 | 251.3 | 233.6 | 388.6 | 37.9 | 20.4 | 73.1 | 4.1 | 246.2 | 5 | 89.6 | 100.8 | 606.9 | 759.1 | 179.1 | 183 | 657.9 | 837.8 | 751.6 | 232.6 | 441.8 | 593.2 | 302.4 | 400.2 | 540.2 | 200.7 | 547.1 | 164.5 | 248.7 | 245.6 | 205.8 | 158 | 229.8 | 233.6 | 180.3
653 | 432 | 477.3 | 190.92 | 223.1745 | 228.8 | 222 | 249.6 | 233.9 | 386.6 | 37.9 | 20.4 | 73.1 | 4.3 | 248.6 | 5.1 | 89.8 | 100.9 | 607.1 | 761.9 | 179.5 | 183.3 | 659.3 | 838.4 | 753.4 | 233.1 | 440.2 | 587 | 302.9 | 399.9 | 536.9 | 200.6 | 546.7 | 164.9 | 248 | 245.1 | 205.8 | 158.2 | 230.2 | 233.7 | 180.6
654 | 433 | 475.6 | 190.24 | 222.3796 | 227.7 | 220.8 | 248.4 | 233.6 | 386.5 | 38 | 20.4 | 73.1 | 4.3 | 242.7 | 5.1 | 90 | 100.9 | 615.8 | 766.5 | 179.9 | 183.7 | 646 | 828.1 | 753.3 | 233.6 | 442.4 | 591.3 | 303.4 | 395.8 | 526.4 | 200.5 | 546.2 | 165.2 | 247.4 | 244.8 | 206 | 158.5 | 230.6 | 233.8 | 181
655 | 434 | 475.4 | 190.16 | 222.2861 | 227.2 | 220.1 | 247.4 | 233 | 386.3 | 38.1 | 20.4 | 73.2 | 4.2 | 251.7 | 4.9 | 90.1 | 101 | 621.5 | 770.6 | 180.2 | 184 | 651.5 | 830 | 754.9 | 234.1 | 445.1 | 596.4 | 303.9 | 393.9 | 528.3 | 200.5 | 546.8 | 165.6 | 247 | 244.7 | 206.3 | 158.7 | 231 | 234 | 181.2
656 | 435 | 475.9 | 190.36 | 222.5199 | 227.2 | 219.3 | 246 | 232.7 | 388.6 | 38.2 | 20.4 | 73.1 | 3.9 | 248.2 | 4.1 | 90.2 | 101.2 | 624.2 | 774.3 | 180.6 | 184.4 | 655.9 | 817.1 | 755.3 | 234.6 | 448.4 | 603.2 | 304.4 | 395.4 | 530 | 200.5 | 547.8 | 165.9 | 246.9 | 244.5 | 206.7 | 158.9 | 231.1 | 233.7 | 181.4
657 | 436 | 476.9 | 190.76 | 222.9874 | 227.2 | 218.4 | 245.3 | 232.9 | 392.4 | 38.4 | 20.4 | 73.1 | 3.9 | 257.8 | 3.8 | 90.4 | 101.3 | 623.2 | 780.3 | 180.9 | 184.7 | 643.9 | 803.9 | 755.3 | 235 | 447.1 | 600.5 | 304.8 | 391.8 | 521.9 | 200.5 | 546.9 | 166.3 | 246.6 | 244.4 | 207.3 | 159.2 | 231.1 | 233.6 | 181.6
658 | 437 | 476.7 | 190.68 | 222.8939 | 228.1 | 217.8 | 245.2 | 232.8 | 389.2 | 38.5 | 20.4 | 73.2 | 3.8 | 257.1 | 4.2 | 90.5 | 101.4 | 615.2 | 778.7 | 181.3 | 185.1 | 641 | 807.4 | 755.8 | 235.5 | 443.6 | 596.4 | 305.3 | 389.8 | 523.9 | 200.5 | 546.1 | 166.6 | 246.5 | 244.3 | 207.7 | 159.4 | 230.9 | 233.3 | 181.8
659 | 438 | 475.3 | 190.12 | 222.2393 | 228.8 | 218.6 | 244.9 | 232.5 | 384.6 | 38.5 | 20.4 | 73.2 | 4.2 | 246.4 | 4.8 | 90.7 | 101.4 | 608.8 | 775.4 | 181.6 | 185.5 | 650.1 | 809.9 | 755.3 | 236 | 439.4 | 588.2 | 305.8 | 389.7 | 527.1 | 200.4 | 545.5 | 166.9 | 246.4 | 244.2 | 207.6 | 159.7 | 230.7 | 233.2 | 182
660 | 439 | 475.3 | 190.12 | 222.2393 | 228.4 | 219.1 | 244.8 | 231.5 | 379.6 | 38.6 | 20.4 | 73.3 | 4.3 | 259.8 | 4.9 | 90.8 | 101.5 | 603.4 | 773.8 | 182 | 185.9 | 659.8 | 816.6 | 756.2 | 236.5 | 436.8 | 588.6 | 306.3 | 391.2 | 532.9 | 200.5 | 545.1 | 167.2 | 246.2 | 243.9 | 207.6 | 159.9 | 230.9 | 233.4 | 182.4
661 | 440 | 475.9 | 190.36 | 222.5199 | 227.2 | 219.5 | 244.8 | 231.3 | 376.4 | 38.7 | 20.4 | 73.4 | 4.4 | 239.8 | 4.9 | 91 | 101.6 | 616.3 | 768.3 | 182.4 | 186.3 | 671.7 | 826.4 | 757.2 | 237 | 436 | 579.1 | 306.8 | 389.8 | 536.6 | 200.5 | 544.6 | 167.6 | 246.2 | 243.5 | 207.6 | 160.1 | 231.4 | 233.4 | 182.7
662 | 441 | 475.6 | 190.24 | 222.3796 | 226.9 | 219.8 | 243.9 | 231.3 | 372.6 | 38.7 | 20.4 | 73.6 | 3.9 | 225.4 | 4.6 | 91.1 | 101.7 | 625.1 | 766.3 | 182.7 | 186.7 | 675.8 | 842 | 758.2 | 237.5 | 434.4 | 574.7 | 307.4 | 391.8 | 546.4 | 200.6 | 545.5 | 167.9 | 246.2 | 243.3 | 207.5 | 160.3 | 232 | 233.3 | 183
663 | 442 | 481.5 | 192.6 | 225.1383 | 227.2 | 219.2 | 243.1 | 232 | 372.4 | 38.8 | 20.4 | 73.7 | 3.9 | 242.4 | 4.9 | 91.3 | 101.8 | 633.3 | 770.9 | 183.1 | 187.1 | 668.5 | 841.5 | 758.5 | 238 | 438 | 586.6 | 307.9 | 391.2 | 539.6 | 200.7 | 546.3 | 168.3 | 246.1 | 243.1 | 207.7 | 160.6 | 232.6 | 233.2 | 183.3
664 | 443 | 482.9 | 193.16 | 225.7929 | 227.1 | 218.4 | 242.8 | 232.9 | 373.3 | 38.9 | 20.4 | 73.8 | 3.7 | 265 | 4.5 | 91.4 | 101.9 | 632.8 | 765.5 | 183.4 | 187.5 | 654.5 | 823.7 | 757.2 | 238.5 | 437.6 | 576.4 | 308.4 | 388 | 532 | 200.8 | 545.2 | 168.5 | 246 | 243.1 | 208 | 160.8 | 233 | 233.1 | 183.5
665 | 444 | 483.3 | 193.32 | 225.9799 | 226.9 | 217.4 | 242.2 | 233.1 | 370.7 | 38.9 | 20.4 | 73.8 | 3.9 | 252.1 | 4.3 | 91.6 | 101.9 | 616.1 | 758 | 183.8 | 187.9 | 636.4 | 806.7 | 756.7 | 239 | 434.8 | 559.5 | 308.9 | 383.1 | 517.3 | 200.9 | 543.4 | 168.9 | 246 | 242.9 | 208.4 | 161 | 233.2 | 232.8 | 183.6
666 | 445 | 482.7 | 193.08 | 225.6994 | 227.1 | 216.6 | 241.5 | 233.5 | 370.1 | 39 | 20.4 | 73.9 | 4.2 | 238.5 | 4.7 | 91.7 | 102 | 604.4 | 753.4 | 184.2 | 188.3 | 616 | 770.7 | 755.3 | 239.5 | 429.4 | 547.6 | 309.5 | 375.3 | 500.5 | 200.9 | 541.3 | 169.2 | 245.8 | 242.9 | 209.1 | 161.3 | 233.3 | 232.6 | 183.9
667 | 446 | 481.3 | 192.52 | 225.0448 | 227.7 | 217.2 | 241.1 | 233.4 | 377.3 | 39 | 20.4 | 73.9 | 4.1 | 247.4 | 5.6 | 91.8 | 102.1 | 590.3 | 747.1 | 184.5 | 188.7 | 595.8 | 737.1 | 753.4 | 240 | 423.6 | 538 | 309.9 | 368.4 | 487.4 | 201 | 539.4 | 169.6 | 246 | 243 | 209.6 | 161.5 | 233.4 | 232.3 | 184.1
668 | 447 | 478.2 | 191.28 | 223.5953 | 229.3 | 217.7 | 242.8 | 232.8 | 377.5 | 39.1 | 20.4 | 74 | 4.2 | 241.8 | 6 | 92 | 102.2 | 587.9 | 753.3 | 184.9 | 189.1 | 592.1 | 730.8 | 751.8 | 240.5 | 420.4 | 536.3 | 310.4 | 363.6 | 480.5 | 201 | 537.5 | 169.9 | 246.5 | 243.5 | 210.1 | 161.8 | 233.2 | 232.1 | 184.2
669 | 448 | 477.9 | 191.16 | 223.455 | 230.9 | 218.1 | 246.1 | 232.9 | 379.9 | 39.2 | 20.4 | 74.1 | 3.7 | 243.3 | 6.1 | 92.1 | 102.4 | 581.7 | 751.7 | 185.3 | 189.6 | 590.9 | 711.5 | 750.7 | 241 | 418.5 | 533 | 310.9 | 360.6 | 471 | 201 | 535.9 | 170.3 | 247.1 | 244.1 | 210.5 | 162 | 233.2 | 232 | 184.4
670 | 449 | 477.3 | 190.92 | 223.1745 | 231.4 | 218.6 | 249 | 234.1 | 382 | 39.3 | 20.4 | 74.1 | 3.8 | 249 | 6.1 | 92.3 | 102.5 | 575.1 | 749.3 | 185.6 | 190 | 584.6 | 712.6 | 749.5 | 241.6 | 417.4 | 535.8 | 311.4 | 356.1 | 462.9 | 201 | 533.9 | 170.6 | 247.4 | 244.8 | 210.7 | 162.3 | 233 | 231.9 | 184.5
671 | 450 | 476 | 190.4 | 222.5666 | 230.7 | 220 | 251.1 | 235.4 | 386.1 | 39.4 | 20.4 | 74.2 | 4 | 246 | 6.3 | 92.4 | 102.6 | 569.8 | 756.4 | 186 | 190.4 | 577.2 | 712.1 | 748.2 | 242.1 | 419.8 | 535.5 | 311.9 | 353.6 | 459.3 | 201.1 | 532.5 | 170.9 | 248 | 245.5 | 211.2 | 162.5 | 233 | 231.7 | 184.7
672 | 451 | 477.9 | 191.16 | 223.455 | 230.8 | 222.3 | 253.2 | 236 | 390.6 | 39.5 | 20.4 | 74.3 | 3.8 | 243.8 | 6.2 | 92.5 | 102.7 | 564 | 755.3 | 186.4 | 190.8 | 569.5 | 701.8 | 747.3 | 242.6 | 421.5 | 546.1 | 312.4 | 350.2 | 453.7 | 201.1 | 532.4 | 171.2 | 248.2 | 246 | 211.7 | 162.7 | 233 | 232 | 184.9
673 | 452 | 478.1 | 191.24 | 223.5485 | 230.4 | 223.2 | 254.4 | 236.3 | 393.2 | 39.5 | 20.4 | 74.4 | 3.9 | 242.6 | 6.1 | 92.6 | 102.9 | 559.7 | 756.5 | 186.7 | 191.2 | 575.3 | 695.3 | 747.2 | 243.1 | 421.4 | 553 | 312.9 | 350.1 | 455.6 | 201.2 | 531.8 | 171.6 | 248.3 | 246.5 | 212.1 | 163 | 232.7 | 232.1 | 185.1
674 | 453 | 478 | 191.2 | 223.5018 | 230.5 | 224 | 256.3 | 236 | 394.4 | 39.4 | 20.4 | 74.5 | 3.9 | 241.7 | 6.1 | 92.8 | 103.1 | 561.7 | 752.2 | 187.1 | 191.6 | 569.2 | 687.8 | 747 | 243.7 | 422.5 | 556.3 | 313.3 | 350 | 452.1 | 201.2 | 530.8 | 171.9 | 248.4 | 246.7 | 212.3 | 163.2 | 232.6 | 232.2 | 185.2
675 | 454 | 477.4 | 190.96 | 223.2212 | 231.8 | 225.5 | 257 | 235.4 | 399 | 39.5 | 20.4 | 74.6 | 4.2 | 242.6 | 5.9 | 92.9 | 103.2 | 564.1 | 750.4 | 187.4 | 192 | 564.9 | 677.2 | 745.9 | 244.2 | 428.6 | 575.1 | 313.8 | 351 | 461.5 | 201.3 | 531.4 | 172.2 | 248.7 | 247 | 212.4 | 163.4 | 232.4 | 232.3 | 185.3
676 | 455 | 478.2 | 191.28 | 223.5953 | 232.3 | 225.6 | 256.4 | 234.5 | 408.7 | 39.5 | 20.4 | 74.7 | 4.1 | 241.9 | 5.7 | 93 | 103.4 | 558.2 | 738.1 | 187.8 | 192.4 | 561.5 | 650.3 | 742.8 | 244.7 | 433.1 | 573.8 | 314.2 | 352.1 | 458.6 | 201.4 | 531.3 | 172.5 | 249.1 | 247.4 | 213 | 163.6 | 232.3 | 232.5 | 185.5
677 | 456 | 477.5 | 191 | 223.268 | 232.3 | 226.4 | 258.1 | 233.7 | 412.6 | 39.6 | 20.4 | 74.8 | 4.1 | 240.8 | 5.5 | 93.1 | 103.5 | 553.9 | 732.6 | 188.2 | 192.8 | 553.6 | 644.9 | 741.8 | 245.2 | 429.4 | 561.5 | 314.7 | 349.5 | 449.2 | 201.4 | 529.9 | 172.8 | 249.4 | 247.6 | 213.2 | 163.8 | 232.3 | 232.6 | 185.7
678 | 457 | 476.4 | 190.56 | 222.7537 | 233.4 | 227.5 | 259.5 | 233.4 | 411.3 | 39.6 | 20.4 | 74.9 | 4.1 | 238.8 | 5.3 | 93.3 | 103.6 | 556.6 | 734.8 | 188.6 | 193.2 | 545.3 | 662.1 | 742 | 245.7 | 430.5 | 571.2 | 315.3 | 348.7 | 445.1 | 201.5 | 529 | 173.1 | 249.6 | 247.7 | 213.5 | 164 | 232.1 | 232.9 | 185.8
679 | 458 | 476.2 | 190.48 | 222.6601 | 234.6 | 227.9 | 259.7 | 233.6 | 412.5 | 39.6 | 20.4 | 74.9 | 3.8 | 238.7 | 5.1 | 93.4 | 103.8 | 555.7 | 742 | 188.9 | 193.7 | 544.2 | 667.5 | 741.2 | 246.2 | 430.4 | 574.1 | 315.8 | 348.8 | 443.7 | 201.6 | 528.5 | 173.4 | 250 | 247.9 | 213.6 | 164.2 | 232 | 233.4 | 186
680 | 459 | 478 | 191.2 | 223.5018 | 234.8 | 227.1 | 259.6 | 234.7 | 412.4 | 39.6 | 20.4 | 75 | 3.5 | 238 | 5 | 93.5 | 103.9 | 551.7 | 731 | 189.1 | 194.1 | 535.1 | 661.8 | 739.8 | 246.7 | 429.6 | 566.2 | 316.3 | 349.2 | 444.2 | 201.6 | 527.3 | 173.7 | 250.3 | 248.2 | 213.8 | 164.4 | 231.9 | 233.6 | 186.1
681 | 460 | 478.7 | 191.48 | 223.8291 | 235.7 | 226.3 | 260 | 234.8 | 411.9 | 39.6 | 20.4 | 75.1 | 3.7 | 237.9 | 4.9 | 93.7 | 104.1 | 539.2 | 721.3 | 189.4 | 194.5 | 528 | 638.6 | 738.2 | 247.2 | 429.4 | 558.3 | 316.7 | 348.9 | 439 | 201.7 | 526.7 | 174 | 250.8 | 248.7 | 214.1 | 164.6 | 231.9 | 233.9 | 186.3
682 | 461 | 477.9 | 191.16 | 223.455 | 235.5 | 226.3 | 260.4 | 235.2 | 418.4 | 39.7 | 20.4 | 75.1 | 4.1 | 238.9 | 5.1 | 93.8 | 104.2 | 528.4 | 722.3 | 189.7 | 194.9 | 520.9 | 636.7 | 736.7 | 247.7 | 427.2 | 550.3 | 317.1 | 347 | 433.6 | 201.7 | 524.8 | 174.3 | 251.7 | 249.1 | 214.4 | 164.8 | 231.7 | 234.1 | 186.4
683 | 462 | 478.4 | 191.36 | 223.6888 | 235.5 | 226.6 | 261.6 | 235.7 | 424.5 | 39.8 | 20.4 | 75.1 | 3.6 | 240 | 5.2 | 93.9 | 104.4 | 524.4 | 717.2 | 190 | 195.3 | 511.3 | 619.3 | 734.6 | 248.3 | 428.4 | 549 | 317.5 | 345.7 | 430.2 | 201.8 | 523.5 | 174.6 | 253.1 | 249.6 | 214.9 | 165 | 231.6 | 234.6 | 186.5
684 | 463 | 476.1 | 190.44 | 222.6134 | 236.2 | 226.6 | 263.3 | 236.4 | 427.4 | 39.9 | 20.4 | 75 | 3.3 | 239.9 | 5.3 | 94.1 | 104.5 | 517.4 | 703.7 | 190.3 | 195.7 | 509.3 | 599.2 | 731.8 | 248.8 | 428 | 541.3 | 317.9 | 343.4 | 424.3 | 201.9 | 522.1 | 174.9 | 254.5 | 250.5 | 215.6 | 165.1 | 231.5 | 234.9 | 186.7
685 | 464 | 475.8 | 190.32 | 222.4731 | 236.4 | 226.5 | 265.7 | 236.8 | 428.8 | 40.1 | 20.4 | 75.1 | 3.6 | 237.3 | 5.3 | 94.2 | 104.7 | 516.2 | 707.3 | 190.7 | 196.2 | 509.8 | 591.3 | 730 | 249.3 | 432.4 | 558.3 | 318.4 | 342.2 | 422.7 | 202 | 521.6 | 175.2 | 255.5 | 251.3 | 216.3 | 165.3 | 232.2 | 235.1 | 186.9
686 | 465 | 476.3 | 190.52 | 222.7069 | 236.8 | 227 | 267.5 | 237.6 | 430.9 | 40.1 | 20.4 | 75.1 | 3.8 | 234.8 | 5.2 | 94.3 | 104.8 | 509.2 | 716.3 | 191 | 196.6 | 510.9 | 613.8 | 728.6 | 249.9 | 435.1 | 561 | 318.9 | 341.3 | 419.8 | 202.1 | 520.5 | 175.6 | 256.1 | 251.9 | 216.8 | 165.5 | 232.4 | 235.5 | 187.2
687 | 466 | 476.4 | 190.56 | 222.7537 | 237.8 | 227.7 | 268.8 | 238.8 | 426 | 40.1 | 20.4 | 75.2 | 3.6 | 218.1 | 4.8 | 94.5 | 105 | 502.1 | 716 | 191.3 | 197 | 507.5 | 624.3 | 726.6 | 250.5 | 434.2 | 564.9 | 319.3 | 340.5 | 417.8 | 202.2 | 519.7 | 175.9 | 256.5 | 254 | 216.8 | 165.7 | 232.8 | 236 | 187.5
688 | 467 | 477.2 | 190.88 | 223.1277 | 238.1 | 227.9 | 269.1 | 239.9 | 418.3 | 40.1 | 20.4 | 75.1 | 3.6 | 224 | 5.1 | 94.6 | 105.1 | 501.4 | 717.6 | 191.6 | 197.5 | 505.4 | 621.1 | 726.4 | 251 | 430.5 | 564.6 | 319.8 | 337.4 | 413.8 | 202.2 | 519 | 176.3 | 257 | 255.2 | 217.5 | 165.8 | 232.8 | 236.3 | 187.6
689 | 468 | 477.1 | 190.84 | 223.081 | 237.5 | 227.1 | 267.3 | 240.7 | 417.7 | 40 | 20.4 | 75.1 | 3.9 | 215.6 | 4.9 | 94.7 | 105.3 | 497.3 | 715.9 | 191.9 | 197.9 | 512.3 | 633.6 | 725.4 | 251.6 | 426.7 | 559.2 | 320.2 | 334.7 | 411 | 202.3 | 517.9 | 176.6 | 257 | 255.6 | 217.8 | 166 | 232.8 | 236.7 | 187.7
690 | 469 | 477 | 190.8 | 223.0342 | 238 | 226.9 | 266.1 | 241.3 | 414 | 40 | 20.4 | 75.1 | 3.6 | 214.1 | 4.7 | 94.8 | 105.4 | 494.5 | 713.2 | 192.2 | 198.3 | 514.2 | 624.6 | 723.4 | 252.1 | 423.4 | 550.7 | 320.6 | 332.7 | 408.6 | 202.4 | 516.2 | 176.9 | 257 | 255.9 | 218 | 166.2 | 233 | 237 | 188
691 | 470 | 476.5 | 190.6 | 222.8004 | 238.3 | 228 | 265 | 241.3 | 411.3 | 40 | 20.4 | 75 | 3.9 | 226.9 | 4.2 | 95 | 105.6 | 491.1 | 713.1 | 192.5 | 198.8 | 517.1 | 607.7 | 722.4 | 252.6 | 421.6 | 548.2 | 321.1 | 331.2 | 407.1 | 202.5 | 515.1 | 177.3 | 257 | 256.2 | 218.5 | 166.4 | 233.1 | 237.2 | 188.2
692 | 471 | 477 | 190.8 | 223.0342 | 239.4 | 229.1 | 264.5 | 241.6 | 410.1 | 40.1 | 20.4 | 75 | 4 | 230.3 | 4.1 | 95.1 | 105.7 | 490.6 | 711.1 | 192.8 | 199.2 | 520.6 | 604.6 | 721.4 | 253.1 | 419.8 | 548.6 | 321.5 | 329 | 403.9 | 202.6 | 513.7 | 177.6 | 257 | 256.2 | 219 | 166.5 | 232.9 | 237.2 | 188.3
693 | 472 | 477.1 | 190.84 | 223.081 | 239.8 | 229.8 | 264.5 | 241.8 | 408.9 | 40.2 | 20.4 | 74.9 | 4.2 | 239.9 | 4.3 | 95.2 | 105.9 | 484.1 | 706.6 | 193.1 | 199.7 | 511.6 | 597 | 719.2 | 253.6 | 419.5 | 544.3 | 321.9 | 327.7 | 400.2 | 202.7 | 512.5 | 177.9 | 256.9 | 256.1 | 219.2 | 166.7 | 232.7 | 237.2 | 188.5
694 | 473 | 477.7 | 191.08 | 223.3615 | 240.3 | 230.1 | 264.7 | 242.1 | 408.6 | 40.2 | 20.4 | 75 | 3.9 | 233.9 | 4.3 | 95.4 | 106.1 | 490 | 707.7 | 193.4 | 200.1 | 515.8 | 600.3 | 718.7 | 254.1 | 420 | 546.9 | 322.4 | 327.1 | 398.5 | 202.8 | 512.1 | 178.3 | 256.8 | 256 | 219.2 | 166.9 | 232.6 | 237.3 | 188.6
695 | 474 | 477.5 | 191 | 223.268 | 240.7 | 230.6 | 264.9 | 242.6 | 409.4 | 40.2 | 20.4 | 75 | 4 | 234.4 | 4.3 | 95.5 | 106.2 | 493.5 | 710.4 | 193.7 | 200.5 | 520.4 | 606 | 717.4 | 254.5 | 420 | 546.9 | 322.8 | 326 | 400 | 202.9 | 511.3 | 178.6 | 256.6 | 255.9 | 219.1 | 167.1 | 232.4 | 237.1 | 188.7
696 | 475 | 477.1 | 190.84 | 223.081 | 240.6 | 231.2 | 264.4 | 243.6 | 409 | 40.3 | 20.4 | 75 | 3.5 | 236.9 | 4.1 | 95.6 | 106.4 | 493.4 | 715.6 | 193.9 | 200.9 | 515.5 | 605.3 | 717.4 | 255 | 419.9 | 547.6 | 323.2 | 326 | 399.9 | 203 | 510.3 | 178.9 | 256.5 | 255.7 | 219.3 | 167.3 | 232.3 | 237.2 | 188.9
697 | 476 | 477.1 | 190.84 | 223.081 | 239.9 | 231.2 | 262.9 | 243.7 | 412.3 | 40.3 | 20.4 | 75 | 3.3 | 243.3 | 3.9 | 95.7 | 106.5 | 497.4 | 719.2 | 194.2 | 201.3 | 510 | 608.9 | 716.3 | 255.5 | 418.3 | 544.6 | 323.7 | 326.6 | 400.8 | 203.1 | 510 | 179.2 | 256.4 | 255.5 | 219.5 | 167.4 | 232.3 | 237.3 | 189.1
698 | 477 | 477.2 | 190.88 | 223.1277 | 239.6 | 231 | 261.8 | 244.1 | 409 | 40.4 | 20.4 | 75 | 3.1 | 244 | 3.8 | 95.8 | 106.7 | 500 | 720.4 | 194.5 | 201.8 | 510 | 617 | 715.5 | 256 | 418 | 548.1 | 324 | 326.2 | 398.7 | 203.2 | 509.4 | 179.5 | 256.3 | 255.4 | 219.8 | 167.6 | 232.3 | 237.3 | 189.3
699 | 478 | 476.7 | 190.68 | 222.8939 | 240.1 | 230 | 261.2 | 244.3 | 411.5 | 40.4 | 20.4 | 75 | 3.4 | 244.4 | 3.8 | 96 | 106.9 | 499.3 | 710.6 | 194.8 | 202.2 | 502.9 | 608.3 | 713.4 | 256.4 | 417.8 | 542.4 | 324.4 | 326.3 | 396.4 | 203.3 | 508.6 | 179.8 | 256.2 | 255.6 | 220.3 | 167.8 | 232.1 | 237.4 | 189.5
700 | 479 | 477 | 190.8 | 223.0342 | 240.4 | 229.2 | 260.5 | 243.4 | 410.5 | 40.5 | 20.4 | 75 | 3.4 | 226.6 | 3.8 | 96.1 | 107 | 491.9 | 708.8 | 195.1 | 202.6 | 497 | 614.2 | 714 | 256.9 | 414.2 | 534.9 | 324.9 | 324.5 | 392.6 | 203.4 | 507.2 | 180.1 | 255.8 | 255.4 | 220.4 | 168 | 232.3 | 237.5 | 189.7
701 | 480 | 477.4 | 190.96 | 223.2212 | 241 | 229.4 | 260.2 | 242.1 | 409.9 | 40.6 | 20.4 | 75 | 3.4 | 227.9 | 3.3 | 96.2 | 107.2 | 498.5 | 710.7 | 195.3 | 203 | 492.8 | 607.9 | 713.6 | 257.3 | 414 | 540 | 325.3 | 323.7 | 392.2 | 203.6 | 506.6 | 180.5 | 255.7 | 255.3 | 220.4 | 168.1 | 232.4 | 237.4 | 189.9
702 | 481 | 476.8 | 190.72 | 222.9407 | 241 | 229.2 | 259.8 | 242.4 | 413.1 | 40.6 | 20.3 | 75.1 | 3.1 | 255.3 | 3.1 | 96.3 | 107.4 | 501.7 | 714 | 195.6 | 203.4 | 493.1 | 613.9 | 713.6 | 257.8 | 416.1 | 548.9 | 325.8 | 323.3 | 394 | 203.7 | 506.9 | 180.7 | 255.6 | 255.2 | 220.5 | 168.3 | 232.2 | 237.1 | 190.1
703 | 482 | 476.9 | 190.76 | 222.9874 | 240.1 | 229.3 | 258.9 | 242.3 | 410 | 40.7 | 20.3 | 75.2 | 3.5 | 267.6 | 2.9 | 96.4 | 107.5 | 502.5 | 717.5 | 195.9 | 203.8 | 502.6 | 625.6 | 714.3 | 258.2 | 415.8 | 547.1 | 326.3 | 323 | 397.3 | 203.9 | 506.7 | 181 | 255.6 | 255 | 220.7 | 168.5 | 232.1 | 237 | 190.2
704 | 483 | 476.9 | 190.76 | 222.9874 | 239.6 | 230 | 258.5 | 242.5 | 406.2 | 40.7 | 20.3 | 75.2 | 3.7 | 251.2 | 2.7 | 96.6 | 107.7 | 499.8 | 717.7 | 196.2 | 204.2 | 505.4 | 647.6 | 714.7 | 258.7 | 417 | 548.5 | 326.7 | 323.9 | 402.9 | 204 | 506.4 | 181.3 | 255.6 | 254.7 | 220.8 | 168.7 | 232 | 237 | 190.3
705 | 484 | 476.7 | 190.68 | 222.8939 | 239.9 | 230.5 | 259.1 | 242.6 | 406.7 | 40.8 | 20.3 | 75.3 | 3.9 | 235.1 | 2.5 | 96.7 | 107.9 | 501.2 | 721.1 | 196.4 | 204.6 | 505.1 | 653.9 | 715.9 | 259.1 | 418.2 | 546.7 | 326.9 | 324.3 | 402.7 | 204.2 | 505.8 | 181.6 | 255.6 | 254.6 | 221 | 168.8 | 231.9 | 237.3 | 190.5
706 | 485 | 477.6 | 191.04 | 223.3148 | 239.3 | 230.7 | 258.7 | 242.1 | 405.8 | 40.8 | 20.3 | 75.4 | 3.6 | 236.6 | 2.4 | 96.8 | 108.1 | 501.3 | 723.9 | 196.7 | 205 | 499.2 | 647.1 | 716.4 | 259.5 | 417.8 | 550.7 | 327.2 | 323 | 401.6 | 204.3 | 505 | 181.9 | 255.2 | 254.4 | 221.1 | 169 | 231.9 | 237.5 | 190.8
707 | 486 | 476.8 | 190.72 | 222.9407 | 238.8 | 230.9 | 258.5 | 241.7 | 404.4 | 40.8 | 20.3 | 75.5 | 4.1 | 244.9 | 2.5 | 96.9 | 108.2 | 504 | 725.2 | 197 | 205.4 | 499.2 | 656.5 | 717.1 | 259.9 | 418.9 | 553.3 | 327.6 | 323.1 | 406.1 | 204.4 | 504.9 | 182.2 | 255 | 254.2 | 221.2 | 169.2 | 232 | 237.5 | 191
708 | 487 | 476.8 | 190.72 | 222.9407 | 238.1 | 231 | 258.1 | 241.2 | 405.5 | 40.8 | 20.3 | 75.6 | 3.8 | 245.8 | 2.8 | 97 | 108.4 | 501.6 | 728 | 197.2 | 205.8 | 516.7 | 677.9 | 718 | 260.4 | 421.5 | 554.3 | 328 | 325.4 | 413.5 | 204.6 | 505.4 | 182.5 | 254.7 | 254 | 221.3 | 169.4 | 232.3 | 237.2 | 191.2
709 | 488 | 477.4 | 190.96 | 223.2212 | 237.7 | 230.3 | 257.5 | 240.1 | 401.6 | 40.8 | 20.3 | 75.6 | 4.1 | 243 | 3.1 | 97.1 | 108.6 | 501.3 | 730.5 | 197.5 | 206.2 | 527 | 709.2 | 720.1 | 260.8 | 421.9 | 557.4 | 328.4 | 329 | 421.8 | 204.7 | 505.8 | 182.8 | 254.3 | 253.7 | 221.3 | 169.6 | 232.5 | 237 | 191.4
710 | 489 | 477.4 | 190.96 | 223.2212 | 236.7 | 230.1 | 256.9 | 238.8 | 398 | 40.9 | 20.3 | 75.7 | 4.2 | 241.8 | 3.2 | 97.2 | 108.7 | 506.6 | 725.7 | 197.7 | 206.5 | 542.1 | 734 | 721.1 | 261.2 | 420.5 | 543.8 | 328.9 | 332.2 | 432.4 | 204.9 | 506 | 183.1 | 253.9 | 253.3 | 221.1 | 169.7 | 233 | 236.9 | 191.6
711 | 490 | 477.3 | 190.92 | 223.1745 | 235.9 | 231.1 | 256 | 238.2 | 392.1 | 40.9 | 20.3 | 75.7 | 4 | 240 | 3.3 | 97.3 | 108.9 | 519.9 | 723 | 198 | 206.9 | 559.7 | 761.1 | 723.6 | 261.6 | 419.6 | 540.6 | 329.3 | 339.5 | 449.4 | 205 | 508.1 | 183.4 | 253.6 | 253 | 221 | 169.9 | 233.6 | 237.1 | 191.9
712 | 491 | 477.3 | 190.92 | 223.1745 | 235.5 | 231.4 | 253.9 | 238 | 389.8 | 40.9 | 20.3 | 75.8 | 4.3 | 237.7 | 3.5 | 97.3 | 109.1 | 531.4 | 734.9 | 198.3 | 207.3 | 559.6 | 780.4 | 725.7 | 262 | 421.4 | 549.9 | 329.7 | 345.9 | 470.2 | 205.2 | 510.1 | 183.6 | 253.3 | 252.5 | 221 | 170.1 | 234.3 | 237.1 | 192.3
713 | 492 | 477.3 | 190.92 | 223.1745 | 234.4 | 230.3 | 251.2 | 238.5 | 386.7 | 41 | 20.3 | 75.9 | 4.1 | 237.5 | 3.4 | 97.4 | 109.3 | 537.5 | 736.7 | 198.5 | 207.6 | 563.6 | 789.5 | 727.6 | 262.4 | 425.9 | 564.3 | 330 | 351.5 | 483 | 205.4 | 512.6 | 183.9 | 253.3 | 252.3 | 221.2 | 170.3 | 235 | 237.2 | 192.6
714 | 493 | 477.2 | 190.88 | 223.1277 | 234 | 229.2 | 249.3 | 239.6 | 384.4 | 41.1 | 20.3 | 75.9 | 4.1 | 246.2 | 3.1 | 97.5 | 109.5 | 539.3 | 738.6 | 198.8 | 208 | 563.1 | 793.3 | 729.5 | 262.9 | 427.8 | 574 | 330.4 | 355.3 | 487.3 | 205.5 | 513.9 | 184.2 | 253 | 251.9 | 221.3 | 170.5 | 235.3 | 237.3 | 192.6
715 | 494 | 476.9 | 190.76 | 222.9874 | 235 | 228.7 | 248.8 | 240.3 | 385.4 | 41.2 | 20.3 | 76 | 4.3 | 262.5 | 3.1 | 97.6 | 109.7 | 540.9 | 741.9 | 199 | 208.4 | 550 | 775.6 | 729.1 | 263.3 | 427.9 | 578 | 330.8 | 353.9 | 478.7 | 205.7 | 513.6 | 184.5 | 253 | 252 | 221.7 | 170.7 | 235.5 | 237.2 | 192.7
716 | 495 | 477 | 190.8 | 223.0342 | 235.5 | 228.8 | 248.6 | 239.9 | 391.8 | 41.2 | 20.3 | 76 | 4.2 | 264.2 | 2.9 | 97.7 | 109.8 | 533.5 | 733.6 | 199.3 | 208.7 | 535 | 746 | 727.3 | 263.7 | 427.3 | 576 | 331.1 | 352.3 | 472.5 | 205.9 | 512.9 | 184.7 | 253.4 | 252.3 | 222.5 | 170.9 | 235.9 | 237.1 | 193.1
717 | 496 | 476.6 | 190.64 | 222.8472 | 235.5 | 229.7 | 250.2 | 239.9 | 395.2 | 41.2 | 20.3 | 76.1 | 3.9 | 256.8 | 2.8 | 97.8 | 110 | 526.7 | 738.8 | 199.5 | 209.1 | 525.3 | 726.8 | 727.4 | 264.1 | 424.2 | 573.1 | 331.5 | 349.1 | 464.7 | 206 | 511.8 | 185 | 253.9 | 252.7 | 223.2 | 171.1 | 236.6 | 237.1 | 193.4
718 | 497 | 477.1 | 190.84 | 223.081 | 235.6 | 230 | 251.3 | 240 | 396.5 | 41.3 | 20.3 | 76.2 | 3.2 | 251.4 | 2.7 | 97.9 | 110.1 | 525.8 | 749.1 | 199.8 | 209.4 | 521 | 740 | 728.8 | 264.5 | 424.4 | 576.6 | 331.9 | 347.8 | 464 | 206.2 | 511.3 | 185.2 | 254.5 | 253.4 | 223.8 | 171.4 | 236.8 | 237.2 | 193.7
719 | 498 | 476.8 | 190.72 | 222.9407 | 234.9 | 231.2 | 252 | 239.8 | 394 | 41.4 | 20.3 | 76.4 | 3.3 | 250.3 | 2.6 | 98 | 110.3 | 525.8 | 749.6 | 200.1 | 209.8 | 530.4 | 768.2 | 730.7 | 265 | 424.4 | 578.1 | 332.3 | 349.8 | 476.7 | 206.4 | 512 | 185.5 | 254.7 | 253.6 | 224 | 171.6 | 236.9 | 237.3 | 193.9
720 | 499 | 476.7 | 190.68 | 222.8939 | 235 | 232.4 | 252.2 | 240.3 | 389.6 | 41.4 | 20.3 | 76.5 | 3.9 | 247.5 | 2.5 | 98.1 | 110.5 | 532.2 | 754.5 | 200.3 | 210.2 | 531.5 | 772 | 731.4 | 265.4 | 427.3 | 579.8 | 332.7 | 351.8 | 482.2 | 206.6 | 512.8 | 185.8 | 254.5 | 253.5 | 224 | 171.9 | 236.7 | 237.3 | 193.9
721 | 500 | 477.2 | 190.88 | 223.1277 | 235.1 | 232.6 | 252.4 | 240.2 | 390 | 41.5 | 20.3 | 76.6 | 4 | 241.4 | 2.5 | 98.2 | 110.7 | 544.2 | 756.4 | 200.6 | 210.5 | 525.5 | 777.3 | 732.6 | 265.8 | 431.7 | 584.1 | 333 | 353.4 | 484.9 | 206.7 | 513.4 | 186.1 | 254.5 | 253.4 | 224 | 172.2 | 236.7 | 237.4 | 194
722 | 501 | 477.1 | 190.84 | 223.081 | 235 | 233.2 | 252 | 240 | 395.1 | 41.5 | 20.3 | 76.7 | 3.9 | 219 | 2.6 | 98.3 | 110.9 | 545.1 | 757.3 | 200.8 | 210.9 | 518.7 | 754.6 | 731.7 | 266.2 | 433.8 | 578.1 | 333.2 | 353.6 | 479.2 | 206.9 | 513.5 | 186.4 | 254.6 | 253.4 | 224.1 | 172.4 | 237.4 | 237.7 | 194.4
723 | 502 | 475.9 | 190.36 | 222.5199 | 235.3 | 234 | 251.6 | 240.5 | 401.3 | 41.6 | 20.3 | 76.7 | 4.6 | 205.3 | 2.7 | 98.4 | 111 | 538.9 | 741.8 | 201.1 | 211.3 | 513.2 | 718.7 | 730.9 | 266.7 | 434.9 | 569.8 | 333.6 | 351.7 | 472.4 | 207.1 | 512.6 | 186.7 | 255.1 | 253.7 | 224.5 | 172.7 | 237.6 | 237.8 | 194.4
724 | 503 | 477 | 190.8 | 223.0342 | 236.8 | 234.9 | 251.9 | 240.8 | 409.3 | 41.6 | 20.3 | 76.7 | 4.5 | 206.6 | 2.8 | 98.5 | 111.2 | 529 | 726.1 | 201.3 | 211.6 | 516.5 | 676.1 | 727.6 | 267.1 | 431.8 | 558.7 | 334 | 348.6 | 464.8 | 207.3 | 511.4 | 187 | 256.1 | 254.2 | 225.2 | 173 | 237.7 | 238 | 194.5
725 | 504 | 476.9 | 190.76 | 222.9874 | 239.8 | 235.7 | 254 | 240.5 | 414.1 | 41.5 | 20.3 | 76.8 | 4.3 | 215.9 | 2.7 | 98.6 | 111.4 | 526.5 | 718.1 | 201.6 | 212 | 515.9 | 648.4 | 726.3 | 267.5 | 430.6 | 560.2 | 334.5 | 346 | 458.7 | 207.5 | 510.3 | 187.3 | 257.4 | 255.1 | 225.9 | 173.2 | 237.5 | 238.2 | 194.6
726 | 505 | 476.3 | 190.52 | 222.7069 | 243 | 236.2 | 256.2 | 241 | 418.3 | 41.4 | 20.3 | 77 | 4.3 | 227 | 2.7 | 98.7 | 111.5 | 521.1 | 717.7 | 201.8 | 212.3 | 504.7 | 634.8 | 724.4 | 267.9 | 431.7 | 568.2 | 335 | 343.8 | 453 | 207.7 | 509.7 | 187.5 | 258.7 | 255.8 | 226.6 | 173.5 | 237.2 | 238.6 | 194.7
727 | 506 | 477.1 | 190.84 | 223.081 | 242.8 | 236.3 | 258.8 | 241.5 | 417 | 41.4 | 20.3 | 77.1 | 3.8 | 240.9 | 2.6 | 98.8 | 111.7 | 522.1 | 727.6 | 202.1 | 212.7 | 496 | 643.4 | 723.9 | 268.3 | 430.4 | 563.2 | 335.4 | 343 | 450.9 | 207.9 | 508.7 | 187.9 | 259.6 | 256.4 | 226.7 | 173.7 | 237.1 | 238.9 | 195
728 | 507 | 477.5 | 191 | 223.268 | 242.5 | 235.7 | 260.2 | 243.2 | 417.9 | 41.4 | 20.3 | 77.2 | 3.8 | 239.9 | 2.8 | 98.9 | 111.9 | 523.4 | 720.9 | 202.3 | 213.1 | 489.1 | 623.2 | 723.6 | 268.8 | 432.4 | 569.1 | 335.9 | 342.2 | 448.1 | 208.1 | 508.3 | 188.2 | 260.4 | 257.1 | 226.9 | 174 | 236.9 | 239.5 | 195.2
729 | 508 | 477.3 | 190.92 | 223.1745 | 242.4 | 234.2 | 262.2 | 244 | 421.9 | 41.5 | 20.3 | 77.2 | 3.8 | 214.5 | 2.8 | 99 | 112.1 | 523.7 | 715.8 | 202.6 | 213.4 | 484 | 600.8 | 720.4 | 269.2 | 436.2 | 567.1 | 336.3 | 340.6 | 442.6 | 208.4 | 507.8 | 188.5 | 261.2 | 257.9 | 227.2 | 174.2 | 236.7 | 239.8 | 195.3
730 | 509 | 477.1 | 190.84 | 223.081 | 243.6 | 233.5 | 264.7 | 243.8 | 429.5 | 41.6 | 20.3 | 77.2 | 3.6 | 212.4 | 2.6 | 99.1 | 112.3 | 518.5 | 712.9 | 202.8 | 213.8 | 476.1 | 581 | 718.8 | 269.6 | 434.9 | 563.7 | 336.6 | 339.3 | 436.6 | 208.6 | 506.9 | 188.9 | 262.2 | 258.6 | 227.6 | 174.5 | 236.8 | 240.4 | 195.5
731 | 510 | 476.9 | 190.76 | 222.9874 | 244.7 | 233.8 | 266.9 | 243.9 | 434.7 | 41.6 | 20.3 | 77.1 | 3.8 | 215.2 | 2.5 | 99.2 | 112.5 | 521.7 | 712 | 203 | 214.1 | 467.7 | 578.3 | 717.8 | 270 | 433.6 | 562.4 | 336.9 | 337.7 | 434 | 208.8 | 505.9 | 189.3 | 262.7 | 259.2 | 228 | 174.7 | 236.8 | 240.7 | 195.7
732 | 511 | 476.2 | 190.48 | 222.6601 | 245.2 | 233.6 | 268.2 | 244.9 | 432.5 | 41.7 | 20.3 | 77 | 4 | 220.5 | 2.3 | 99.3 | 112.7 | 521.3 | 712.5 | 203.3 | 214.5 | 459.4 | 584.9 | 717 | 270.5 | 433.2 | 564.2 | 337.3 | 337.7 | 431.2 | 209 | 505.2 | 189.6 | 263.1 | 259.7 | 228.3 | 174.9 | 236.9 | 241.1 | 195.9
733 | 512 | 477.4 | 190.96 | 223.2212 | 246.4 | 234.2 | 268.3 | 246 | 432.8 | 41.7 | 20.3 | 76.9 | 4.2 | 234.8 | 2.2 | 99.4 | 112.8 | 516.3 | 719.4 | 203.5 | 214.8 | 469.2 | 620.1 | 717.4 | 270.9 | 432.5 | 567.5 | 337.7 | 338.1 | 433.9 | 209.2 | 505.3 | 190 | 263.5 | 259.9 | 228.4 | 175.1 | 237.2 | 241.6 | 196
734 | 513 | 476.4 | 190.56 | 222.7537 | 246.4 | 234.7 | 269.5 | 247.1 | 425.3 | 41.7 | 20.3 | 77 | 4.2 | 245.7 | 2.3 | 99.5 | 113 | 519.5 | 721.6 | 203.8 | 215.2 | 484.4 | 668.1 | 719.2 | 271.3 | 430.8 | 566.1 | 338 | 340.1 | 442.6 | 209.4 | 505.2 | 190.4 | 263.5 | 259.9 | 228.1 | 175.3 | 237.3 | 241.9 | 196.2
735 | 514 | 476.7 | 190.68 | 222.8939 | 246 | 235.3 | 269.3 | 247.8 | 418.2 | 41.7 | 20.3 | 77.1 | 4.4 | 247.2 | 2.3 | 99.7 | 113.2 | 526.2 | 722.8 | 204 | 215.5 | 498.8 | 720.6 | 721.1 | 271.8 | 429.6 | 565.9 | 338.4 | 345.8 | 460 | 209.6 | 505.8 | 190.8 | 263.4 | 259.8 | 227.9 | 175.5 | 237.6 | 242.3 | 196.5
736 | 515 | 477.7 | 191.08 | 223.3615 | 245.8 | 234.7 | 268.1 | 248.1 | 411.2 | 41.8 | 20.3 | 77.1 | 4.2 | 247.3 | 2.5 | 99.8 | 113.5 | 531.9 | 732.4 | 204.3 | 215.9 | 502.3 | 738.2 | 723.4 | 272.2 | 431.1 | 570.3 | 338.7 | 351.2 | 466.2 | 209.7 | 507.4 | 191.1 | 263.2 | 259.8 | 227.9 | 175.7 | 238 | 242.3 | 196.8
737 | 516 | 477.5 | 191 | 223.268 | 245.6 | 233.9 | 266.7 | 248.4 | 408.2 | 41.9 | 20.3 | 77.2 | 4.2 | 238.4 | 2.8 | 99.9 | 113.7 | 542.3 | 736.5 | 204.5 | 216.2 | 513.4 | 744.2 | 724.6 | 272.6 | 432.2 | 578.9 | 339.1 | 353.2 | 468.5 | 209.9 | 508.3 | 191.5 | 263 | 259.7 | 228.1 | 175.9 | 238.1 | 242.3 | 196.9
738 | 517 | 477.4 | 190.96 | 223.2212 | 244.9 | 234.3 | 264.3 | 247.6 | 405.8 | 41.9 | 20.3 | 77.2 | 4 | 226.2 | 3 | 100 | 113.9 | 546.1 | 735.3 | 204.8 | 216.6 | 527.1 | 774.8 | 726.8 | 273 | 431.7 | 573.2 | 339.4 | 354.9 | 475.8 | 210.1 | 508.5 | 191.9 | 262.8 | 259.4 | 228.2 | 176.1 | 238.1 | 242.4 | 197.1
739 | 518 | 477.4 | 190.96 | 223.2212 | 244.5 | 235 | 262.4 | 246.8 | 402 | 41.9 | 20.3 | 77.2 | 3.8 | 228 | 3.1 | 100.1 | 114.1 | 547.9 | 736.5 | 205.1 | 216.9 | 539.9 | 796.8 | 728 | 273.4 | 431 | 570.3 | 339.7 | 361 | 484.8 | 210.3 | 510.1 | 192.2 | 262.7 | 259.1 | 228.1 | 176.3 | 238.1 | 242.6 | 197.3
740 | 519 | 477.7 | 191.08 | 223.3615 | 243.4 | 233.4 | 261.1 | 246.1 | 396.9 | 41.9 | 20.3 | 77.2 | 4 | 227.2 | 3.2 | 100.2 | 114.3 | 568.4 | 733.4 | 205.3 | 217.3 | 549.9 | 785 | 728.3 | 273.9 | 431 | 568.4 | 340.1 | 362.9 | 491.8 | 210.4 | 511.1 | 192.6 | 262.4 | 258.9 | 228.1 | 176.5 | 238.3 | 242.6 | 197.5
741 | 520 | 475.1 | 190.04 | 222.1458 | 241.8 | 232.3 | 259.7 | 245.6 | 391.3 | 42 | 20.3 | 77.2 | 3.9 | 228.8 | 3 | 100.2 | 114.5 | 570.3 | 729.7 | 205.6 | 217.6 | 553.8 | 796.9 | 729.5 | 274.3 | 430.1 | 566.7 | 340.5 | 364 | 497.5 | 210.6 | 511.2 | 192.9 | 262.1 | 258.6 | 228.2 | 176.7 | 238.3 | 242.4 | 197.6
742 | 521 | 474.8 | 189.92 | 222.0055 | 240.3 | 231.7 | 258.3 | 244.8 | 386.7 | 42 | 20.3 | 77.2 | 3.8 | 233.4 | 2.7 | 100.3 | 114.7 | 570.5 | 727.8 | 205.8 | 218 | 561.6 | 800.1 | 730.8 | 274.7 | 429.2 | 562.5 | 340.8 | 366.8 | 501.5 | 210.8 | 512.6 | 193.3 | 261.6 | 258.2 | 228.2 | 177 | 238.7 | 242.2 | 197.9
743 | 522 | 475 | 190 | 222.0991 | 239.1 | 230.9 | 256.5 | 244.2 | 383.2 | 42.1 | 20.3 | 77.2 | 3.9 | 232.6 | 2.5 | 100.4 | 114.9 | 576.7 | 734.8 | 206.1 | 218.4 | 578.7 | 816.7 | 732.5 | 275.1 | 427.9 | 568.8 | 341.1 | 368.9 | 509 | 211 | 513 | 193.6 | 261 | 257.7 | 228.3 | 177.2 | 239.1 | 242.1 | 198.2
744 | 523 | 474.6 | 189.84 | 221.912 | 239.3 | 230.6 | 255.3 | 244.4 | 383.3 | 42.2 | 20.3 | 77.2 | 3.9 | 224.3 | 2.6 | 100.5 | 115.1 | 587.6 | 741.8 | 206.3 | 218.7 | 580.2 | 820.6 | 733.6 | 275.6 | 430.5 | 584.1 | 341.4 | 369.3 | 515.2 | 211.2 | 514.4 | 193.9 | 260.5 | 257.3 | 228.4 | 177.4 | 239.7 | 241.8 | 198.4
745 | 524 | 475.6 | 190.24 | 222.3796 | 240 | 230 | 253.6 | 244.4 | 383.9 | 42.3 | 20.3 | 77.2 | 3.7 | 223 | 2.6 | 100.7 | 115.3 | 584.4 | 738.4 | 206.6 | 219.1 | 586.8 | 832.3 | 734.2 | 276 | 431.5 | 579 | 341.8 | 372.4 | 528.7 | 211.4 | 515.8 | 194.2 | 260 | 256.9 | 228.4 | 177.6 | 240.4 | 241.6 | 198.6
746 | 525 | 475.1 | 190.04 | 222.1458 | 239.5 | 229.2 | 251.5 | 243.7 | 381.9 | 42.5 | 20.3 | 77.2 | 3.7 | 220.5 | 2.9 | 100.8 | 115.6 | 581 | 735.6 | 206.8 | 219.5 | 614.2 | 845.9 | 735.5 | 276.4 | 431.2 | 570.7 | 342.1 | 381.3 | 539.1 | 211.6 | 517.3 | 194.5 | 259.8 | 256.6 | 228.3 | 177.8 | 240.8 | 241.6 | 198.8
747 | 526 | 475.5 | 190.2 | 222.3328 | 238.6 | 228.6 | 249.8 | 243.8 | 381.6 | 42.6 | 20.3 | 77.1 | 3.9 | 219.4 | 3.3 | 100.9 | 115.8 | 586.9 | 740.9 | 207 | 219.9 | 621.9 | 851.3 | 737.7 | 276.9 | 432.2 | 569.2 | 342.4 | 385.2 | 549.5 | 211.8 | 519 | 194.7 | 259.6 | 256.4 | 228.5 | 178.1 | 241 | 241.6 | 199
748 | 527 | 477.3 | 190.92 | 223.1745 | 237.5 | 228.3 | 248.6 | 244 | 379.5 | 42.8 | 20.3 | 77 | 3.6 | 224.4 | 3.3 | 101 | 116 | 608.6 | 744.7 | 207.3 | 220.2 | 634.6 | 838.7 | 738.5 | 277.3 | 434.9 | 584.2 | 342.7 | 389 | 557.1 | 212 | 521.4 | 195 | 259.4 | 256.2 | 228.7 | 178.3 | 241 | 241.7 | 199.1
749 | 528 | 476.3 | 190.52 | 222.7069 | 237.1 | 228.4 | 248.1 | 244.6 | 382 | 42.9 | 20.3 | 77 | 3.8 | 224 | 3.2 | 101.1 | 116.2 | 611.6 | 733.5 | 207.5 | 220.6 | 620.5 | 807.6 | 736.8 | 277.7 | 438.9 | 583.5 | 343.1 | 387.4 | 548 | 212.1 | 522.2 | 195.3 | 259.3 | 256.3 | 229.3 | 178.5 | 240.9 | 241.6 | 199.3
750 | 529 | 475.7 | 190.28 | 222.4264 | 237.8 | 227.8 | 248 | 244.8 | 386.9 | 43 | 20.3 | 77 | 3.8 | 215.1 | 3.2 | 101.3 | 116.4 | 597 | 717.2 | 207.7 | 221 | 599.2 | 759.3 | 733.3 | 278.1 | 436.6 | 566.7 | 343.5 | 382.3 | 532.2 | 212.3 | 520.9 | 195.6 | 259.3 | 256.4 | 229.8 | 178.8 | 240.8 | 241.6 | 199.4
751 | 530 | 475.9 | 190.36 | 222.5199 | 238.8 | 227.9 | 248.1 | 244.4 | 390.3 | 43.1 | 20.3 | 77.1 | 4.1 | 226.2 | 3.4 | 101.4 | 116.6 | 579.3 | 709.2 | 207.9 | 221.4 | 586.7 | 737.5 | 732.1 | 278.5 | 432.9 | 554.6 | 343.8 | 377.1 | 517.9 | 212.5 | 519.5 | 195.9 | 259.7 | 256.6 | 230.1 | 179 | 240.7 | 241.6 | 199.5
752 | 531 | 475.9 | 190.36 | 222.5199 | 239.8 | 228.8 | 250.2 | 244.1 | 390.6 | 43.2 | 20.3 | 77.1 | 3.9 | 242.6 | 3.7 | 101.6 | 116.8 | 564.6 | 706.5 | 208.2 | 221.8 | 574 | 735.3 | 731.8 | 278.9 | 429.2 | 544.6 | 344.2 | 372.6 | 504.3 | 212.7 | 518.2 | 196.1 | 260.1 | 256.8 | 230.3 | 179.2 | 240.5 | 241.6 | 199.6
753 | 532 | 475.8 | 190.32 | 222.4731 | 241 | 229.5 | 252.1 | 244.1 | 390.2 | 43.3 | 20.3 | 77.2 | 4.2 | 240.2 | 3.8 | 101.8 | 117.1 | 563.3 | 707.7 | 208.4 | 222.1 | 557.4 | 722.3 | 730.5 | 279.4 | 426.2 | 546.3 | 344.5 | 368.1 | 494.5 | 212.8 | 517.3 | 196.4 | 260.5 | 256.9 | 230.6 | 179.5 | 240.5 | 241.8 | 199.7
754 | 533 | 475.2 | 190.08 | 222.1926 | 241.3 | 229.5 | 253 | 243.9 | 394.7 | 43.3 | 20.3 | 77.3 | 4.2 | 224.4 | 3.6 | 102 | 117.3 | 569 | 716.8 | 208.7 | 222.5 | 547.1 | 713.8 | 730 | 279.8 | 427.5 | 556.9 | 344.9 | 366.2 | 489.2 | 213 | 517.1 | 196.7 | 260.6 | 257.1 | 230.9 | 179.7 | 240.3 | 241.7 | 199.9
755 | 534 | 478.9 | 191.56 | 223.9226 | 242.4 | 230.2 | 254.6 | 243.8 | 401.9 | 43.3 | 20.3 | 77.3 | 4.5 | 219.1 | 3.4 | 102.1 | 117.5 | 571.8 | 719.7 | 209 | 222.9 | 544.6 | 708.8 | 728.8 | 280.2 | 426.5 | 555.9 | 345.2 | 365.6 | 484.5 | 213.2 | 517 | 197 | 260.8 | 257.3 | 231.3 | 179.9 | 240.1 | 241.7 | 200
756 | 535 | 477.7 | 191.08 | 223.3615 | 241.8 | 230.7 | 256.2 | 243.4 | 402.1 | 43.3 | 20.2 | 77.3 | 4.3 | 237.2 | 3.1 | 102.3 | 117.7 | 567.3 | 723.1 | 209.2 | 223.3 | 535.7 | 701.5 | 728.3 | 280.6 | 426.9 | 555.9 | 345.6 | 365.8 | 482.1 | 213.3 | 517.1 | 197.2 | 260.9 | 257.6 | 231.5 | 180.1 | 240.4 | 241.5 | 200.3
757 | 536 | 477.6 | 191.04 | 223.3148 | 242.8 | 231.5 | 257.2 | 242.9 | 404 | 43.4 | 20.3 | 77.4 | 3.8 | 253.7 | 3.1 | 102.5 | 118 | 562.2 | 722.8 | 209.5 | 223.7 | 532.5 | 713.9 | 729.1 | 281 | 426.5 | 551.4 | 345.9 | 365.3 | 481.7 | 213.4 | 517.3 | 197.5 | 261 | 257.8 | 231.7 | 180.3 | 240.6 | 241.5 | 200.4
758 | 537 | 477.9 | 191.16 | 223.455 | 244.6 | 232.3 | 257.1 | 242.4 | 400.9 | 43.4 | 20.3 | 77.5 | 3.9 | 255.5 | 2.9 | 102.7 | 118.2 | 561.2 | 722.6 | 209.7 | 224.1 | 537 | 730.5 | 729.6 | 281.4 | 425.6 | 546.9 | 346.3 | 365.6 | 483.1 | 213.6 | 516.9 | 197.8 | 261.6 | 257.9 | 231.7 | 180.5 | 240.5 | 241.6 | 200.6
759 | 538 | 475.9 | 190.36 | 222.5199 | 245.3 | 232.8 | 257.7 | 242.3 | 399.7 | 43.4 | 20.3 | 77.6 | 4.1 | 251.5 | 2.6 | 102.9 | 118.5 | 558.4 | 723.8 | 210 | 224.5 | 536.7 | 735.3 | 729.2 | 281.8 | 425.4 | 537.8 | 346.6 | 365.7 | 479.6 | 213.7 | 516.2 | 198.1 | 261.8 | 257.9 | 231.9 | 180.8 | 240.6 | 241.9 | 200.7
760 | 539 | 477.1 | 190.84 | 223.081 | 245.3 | 232.7 | 258.4 | 241.6 | 397.6 | 43.4 | 20.2 | 77.7 | 4.1 | 250 | 2.4 | 103.1 | 118.7 | 551.7 | 714.5 | 210.2 | 224.9 | 532.4 | 723.1 | 728.4 | 282.2 | 423.9 | 532.4 | 347 | 363.1 | 473 | 213.8 | 515.4 | 198.3 | 261.8 | 258.1 | 232.1 | 180.9 | 240.7 | 241.9 | 200.8
761 | 540 | 477.4 | 190.96 | 223.2212 | 245.1 | 232.9 | 258.4 | 241.2 | 396.7 | 43.3 | 20.2 | 77.8 | 3.7 | 249.3 | 2.2 | 103.3 | 118.9 | 539.1 | 695.3 | 210.4 | 225.3 | 518.6 | 695.4 | 725.8 | 282.6 | 421.1 | 523.7 | 347.3 | 359.2 | 463 | 214 | 514.4 | 198.6 | 262.2 | 258.3 | 232.5 | 181.1 | 240.9 | 241.8 | 201
762 | 541 | 476.9 | 190.76 | 222.9874 | 244.6 | 233 | 258.5 | 241.7 | 398.5 | 43.3 | 20.2 | 77.9 | 4.1 | 248.5 | 2.2 | 103.5 | 119.1 | 525.1 | 681.9 | 210.7 | 225.7 | 506.1 | 670 | 724.8 | 283.1 | 416.8 | 513 | 347.7 | 354.9 | 454.2 | 214.1 | 512.8 | 198.9 | 262.7 | 258.6 | 232.9 | 181.3 | 240.9 | 241.9 | 201.1
763 | 542 | 477.1 | 190.84 | 223.081 | 244.5 | 233.4 | 259.4 | 242.2 | 395.5 | 43.2 | 20.2 | 78 | 4 | 248.4 | 2.1 | 103.7 | 119.4 | 513.6 | 675.7 | 210.9 | 226.1 | 511.8 | 673.7 | 724.1 | 283.5 | 412.1 | 502.8 | 348.1 | 351.2 | 450.5 | 214.2 | 511.2 | 199.1 | 263 | 258.6 | 232.9 | 181.5 | 240.9 | 242.1 | 201.3
764 | 543 | 477.1 | 190.84 | 223.081 | 244.8 | 234.1 | 259.3 | 242.8 | 389.4 | 43.2 | 20.2 | 78.2 | 4.4 | 247.6 | 2.1 | 103.9 | 119.6 | 511.2 | 674.3 | 211.2 | 226.6 | 520.7 | 687.9 | 724.3 | 283.9 | 409.7 | 501.3 | 348.5 | 350.8 | 449.8 | 214.4 | 510.4 | 199.4 | 262.7 | 258.5 | 232.7 | 181.7 | 240.9 | 242.3 | 201.5
765 | 544 | 476.8 | 190.72 | 222.9407 | 245.1 | 234.3 | 259 | 242.3 | 386.8 | 43.2 | 20.2 | 78.3 | 4.1 | 245.4 | 2.1 | 104.1 | 119.8 | 506.1 | 672.6 | 211.4 | 227 | 530.4 | 695.6 | 723.9 | 284.3 | 408.7 | 500 | 348.9 | 350.2 | 451 | 214.5 | 509.8 | 199.7 | 262.5 | 258.3 | 232.6 | 181.9 | 240.9 | 242.5 | 201.7
766 | 545 | 477.2 | 190.88 | 223.1277 | 247.4 | 233.5 | 259 | 242 | 385.6 | 43.1 | 20.2 | 78.4 | 4.1 | 243.7 | 2.3 | 104.4 | 120.1 | 497.8 | 664.4 | 211.6 | 227.4 | 531 | 704.5 | 722.4 | 284.7 | 404.7 | 487.5 | 349.3 | 348.9 | 447.9 | 214.7 | 508.4 | 200 | 262.3 | 258 | 232.6 | 182.1 | 241.2 | 242.6 | 202
767 | 546 | 477.7 | 191.08 | 223.3615 | 247.8 | 233 | 258.5 | 243.5 | 380.8 | 43.1 | 20.2 | 78.5 | 4.2 | 242.7 | 2.4 | 104.6 | 120.3 | 491.6 | 664.8 | 211.9 | 227.8 | 523.8 | 715.8 | 720.6 | 285.1 | 399.5 | 474.3 | 349.7 | 347.8 | 448.2 | 214.8 | 507.3 | 200.2 | 262 | 257.7 | 232.5 | 182.3 | 241.2 | 242.6 | 202.2
768 | 547 | 478.3 | 191.32 | 223.6421 | 249.9 | 232.3 | 257.5 | 245 | 375.4 | 43.1 | 20.2 | 78.7 | 4 | 243.2 | 2.6 | 104.8 | 120.5 | 483.1 | 657 | 212.1 | 228.2 | 520.7 | 717.3 | 721.5 | 285.5 | 394.5 | 463.1 | 350.1 | 348.5 | 447.2 | 215 | 505.5 | 200.5 | 261.9 | 257.4 | 232.4 | 182.5 | 241.3 | 243 | 202.3
769 | 548 | 478.4 | 191.36 | 223.6888 | 252.9 | 231.3 | 257.2 | 245.9 | 374.3 | 43 | 20.2 | 78.8 | 4.3 | 244.6 | 3.1 | 105 | 120.8 | 482.5 | 651 | 212.4 | 228.6 | 523.6 | 735.7 | 722.1 | 285.9 | 391.6 | 457.7 | 350.5 | 352 | 461.9 | 215.1 | 504.8 | 200.7 | 261.8 | 257.1 | 232.3 | 182.7 | 242.4 | 243.3 | 202.9
770 | 549 | 477.8 | 191.12 | 223.4083 | 254.1 | 230 | 256.3 | 247.7 | 372.4 | 43 | 20.2 | 79 | 4.1 | 244.3 | 3.4 | 105.2 | 121 | 482.4 | 649.3 | 212.6 | 229 | 529.4 | 739.1 | 722.7 | 286.3 | 389.9 | 457 | 350.9 | 354 | 466.6 | 215.3 | 504.5 | 201 | 261.7 | 256.9 | 232.3 | 182.9 | 243.4 | 243.9 | 203.3
771 | 550 | 478.1 | 191.24 | 223.5485 | 254.9 | 229 | 255.5 | 248.5 | 369.9 | 43.1 | 20.2 | 79.1 | 3.9 | 244.8 | 3.7 | 105.5 | 121.2 | 479.6 | 641.4 | 212.8 | 229.4 | 529.7 | 741.1 | 722.4 | 286.7 | 387.7 | 450.6 | 351.3 | 352.7 | 462.8 | 215.4 | 503.4 | 201.2 | 261.5 | 256.7 | 232.3 | 183.1 | 243.9 | 244.4 | 203.5
772 | 551 | 478.5 | 191.4 | 223.7356 | 255.6 | 227.5 | 255.3 | 249.5 | 367.3 | 43.1 | 20.2 | 79.1 | 4.2 | 236.8 | 3.6 | 105.7 | 121.4 | 477.1 | 641.8 | 213.1 | 229.7 | 526.9 | 728.5 | 721.2 | 287.1 | 385 | 442 | 351.7 | 352.3 | 459.7 | 215.6 | 501.9 | 201.5 | 261.3 | 256.6 | 232.3 | 183.4 | 244.2 | 244.9 | 203.6
773 | 552 | 477.4 | 190.96 | 223.2212 | 255.5 | 226.5 | 254.6 | 250.9 | 366.4 | 43.2 | 20.2 | 79.1 | 4.3 | 234 | 3.2 | 105.9 | 121.7 | 473.3 | 653.9 | 213.3 | 230.1 | 535.1 | 742.4 | 721.3 | 287.5 | 383 | 435.8 | 352.1 | 351.3 | 457.3 | 215.7 | 500.7 | 201.7 | 261 | 256.4 | 232.5 | 183.6 | 244.3 | 245.2 | 203.8
774 | 553 | 478.2 | 191.28 | 223.5953 | 255.4 | 226.2 | 254.5 | 251.2 | 363.7 | 43.2 | 20.2 | 79 | 3.9 | 234 | 2.9 | 106.1 | 121.9 | 474.5 | 668.7 | 213.5 | 230.5 | 535.6 | 747.2 | 721.2 | 288 | 381.3 | 438.4 | 352.4 | 347.5 | 451.7 | 215.8 | 499.4 | 202 | 260.7 | 256.3 | 232.8 | 183.9 | 244.2 | 245.4 | 203.9
775 | 554 | 477 | 190.8 | 223.0342 | 255.3 | 226.3 | 254.1 | 250.8 | 366.2 | 43.3 | 20.2 | 79 | 3.9 | 251.1 | 3 | 106.3 | 122.1 | 475.9 | 668.8 | 213.8 | 230.8 | 532.5 | 720 | 719.1 | 288.4 | 381.1 | 447.3 | 352.7 | 344.3 | 446.4 | 216 | 498.7 | 202.2 | 260.7 | 256.3 | 233.4 | 184.1 | 243.9 | 245.7 | 203.9
776 | 555 | 476.8 | 190.72 | 222.9407 | 256.1 | 226.3 | 254.7 | 249.9 | 371.1 | 43.3 | 20.2 | 79.1 | 4.1 | 263.2 | 3.6 | 106.6 | 122.3 | 475.4 | 680 | 214 | 231.2 | 531.3 | 707.9 | 718 | 288.8 | 381.5 | 455.4 | 353 | 341.4 | 446.6 | 216.1 | 498.4 | 202.4 | 261.8 | 256.8 | 234.3 | 184.4 | 243.8 | 245.8 | 204.1
777 | 556 | 475.7 | 190.28 | 222.4264 | 255.2 | 226.2 | 255.3 | 249.5 | 375 | 43.4 | 20.2 | 79.1 | 3.6 | 240.8 | 4 | 106.8 | 122.5 | 474 | 690.1 | 214.3 | 231.5 | 529.4 | 700.5 | 717.7 | 289.2 | 381.4 | 465.6 | 353.3 | 341.8 | 449.4 | 216.3 | 498.4 | 202.7 | 261.7 | 256.8 | 234.6 | 184.7 | 243.6 | 246 | 204.2
778 | 557 | 476.4 | 190.56 | 222.7537 | 254.2 | 227.2 | 255.4 | 248.9 | 375.6 | 43.4 | 20.2 | 79.2 | 3.8 | 247.6 | 3.9 | 107 | 122.7 | 476.6 | 694.9 | 214.5 | 231.9 | 526.4 | 707.1 | 717.5 | 289.6 | 381.8 | 474.8 | 353.6 | 341.4 | 451.2 | 216.5 | 498.1 | 202.9 | 261.7 | 257.3 | 235 | 184.9 | 243.4 | 246.3 | 204.3
779 | 558 | 476.9 | 190.76 | 222.9874 | 252.5 | 227.8 | 256.3 | 248.8 | 380 | 43.5 | 20.2 | 79.3 | 3.8 | 248.5 | 3.8 | 107.2 | 122.9 | 481.9 | 705.7 | 214.8 | 232.2 | 522.9 | 708.9 | 716.4 | 290.1 | 385.2 | 488.1 | 353.9 | 341.6 | 446.4 | 216.6 | 498.1 | 203.2 | 262.1 | 257.7 | 235.6 | 185.2 | 243.3 | 246.5 | 204.5
780 | 559 | 476.8 | 190.72 | 222.9407 | 251 | 229.4 | 258.7 | 249.5 | 385.7 | 43.5 | 20.2 | 79.3 | 3.6 | 238.5 | 3.9 | 107.4 | 123.1 | 492.5 | 714.6 | 215 | 232.6 | 521.5 | 712.1 | 717.8 | 290.5 | 387.5 | 499.1 | 354.1 | 341.2 | 443.4 | 216.8 | 497.8 | 203.4 | 263.6 | 258.1 | 235.9 | 185.4 | 243.3 | 246.5 | 204.8
781 | 560 | 476.9 | 190.76 | 222.9874 | 249.7 | 231 | 260 | 249.1 | 390.6 | 43.4 | 20.2 | 79.3 | 3.5 | 258.3 | 4.4 | 107.7 | 123.3 | 503.1 | 718.2 | 215.3 | 232.9 | 526.3 | 716.6 | 717.4 | 290.9 | 390.9 | 522.4 | 354.4 | 344.6 | 453.5 | 217 | 498.4 | 203.6 | 263.6 | 258.5 | 236.1 | 185.6 | 243.3 | 246.5 | 204.9
782 | 561 | 476.4 | 190.56 | 222.7537 | 248.5 | 232.3 | 261 | 248.5 | 391.1 | 43.3 | 20.2 | 79.3 | 3.6 | 244.5 | 4.9 | 107.9 | 123.5 | 515.2 | 718.9 | 215.5 | 233.2 | 535.9 | 731.7 | 718.3 | 291.3 | 393.2 | 531.6 | 354.7 | 349.8 | 465.2 | 217.1 | 500 | 203.9 | 263.8 | 258.7 | 235.9 | 185.9 | 243.3 | 246.4 | 205.1
783 | 562 | 476 | 190.4 | 222.5666 | 248.2 | 233.6 | 261.1 | 248.3 | 390.9 | 43.2 | 20.2 | 79.3 | 4.2 | 243.4 | 5.4 | 108.1 | 123.8 | 527.1 | 718.4 | 215.8 | 233.5 | 545.4 | 744.3 | 718.9 | 291.7 | 398.2 | 534.7 | 355 | 354.2 | 479.8 | 217.3 | 502.4 | 204.1 | 263.7 | 259 | 236 | 186.1 | 243.2 | 246.4 | 205.2
784 | 563 | 476.4 | 190.56 | 222.7537 | 247.1 | 234.2 | 260.5 | 247.7 | 390.8 | 43.2 | 20.2 | 79.3 | 4.3 | 255.6 | 5.5 | 108.4 | 124 | 524.3 | 713.1 | 216 | 233.8 | 538.3 | 743.8 | 718.1 | 292.1 | 397.8 | 525.1 | 355.3 | 354.2 | 476.7 | 217.4 | 502.3 | 204.3 | 263.8 | 259.7 | 236.2 | 186.3 | 243 | 246.4 | 205.3
785 | 564 | 476.7 | 190.68 | 222.8939 | 246.1 | 234.6 | 260.6 | 247 | 388.1 | 43.2 | 20.2 | 79.4 | 4.2 | 251.3 | 5.5 | 108.6 | 124.1 | 522.5 | 710.3 | 216.3 | 234.1 | 528 | 743.6 | 717 | 292.5 | 397.2 | 519.8 | 355.6 | 352.3 | 472.8 | 217.6 | 501.8 | 204.6 | 264 | 260.1 | 236.6 | 186.5 | 242.8 | 246.3 | 205.4
786 | 565 | 476.8 | 190.72 | 222.9407 | 246.3 | 234.3 | 260.4 | 246.8 | 387.3 | 43.4 | 20.2 | 79.5 | 4.4 | 246.8 | 5.7 | 108.8 | 124.3 | 527.7 | 706 | 216.5 | 234.4 | 528.2 | 745.5 | 717.4 | 292.9 | 396.1 | 514.5 | 355.9 | 350.7 | 469.4 | 217.7 | 501.1 | 204.8 | 264.3 | 260.4 | 236.9 | 186.7 | 242.9 | 246 | 205.5
787 | 566 | 478 | 191.2 | 223.5018 | 247.4 | 234.3 | 259.8 | 246.1 | 387.4 | 43.5 | 20.2 | 79.6 | 4.4 | 246.2 | 5.8 | 109 | 124.5 | 530 | 705.7 | 216.8 | 234.7 | 532.1 | 765.2 | 719.6 | 293.3 | 395.8 | 519.2 | 356.3 | 352.4 | 470.5 | 217.9 | 501.5 | 205 | 264.4 | 260.3 | 236.8 | 186.9 | 242.9 | 245.8 | 205.7
788 | 567 | 476.7 | 190.68 | 222.8939 | 248.1 | 234.9 | 259.1 | 245.9 | 384.4 | 43.5 | 20.2 | 79.7 | 4.1 | 248 | 5.8 | 109.2 | 124.7 | 541.4 | 704.6 | 217.1 | 235 | 540.1 | 765.3 | 720.1 | 293.7 | 395.3 | 518.8 | 356.6 | 353.1 | 475.6 | 218.1 | 502.3 | 205.2 | 264.4 | 260.1 | 236.7 | 187.2 | 242.8 | 245.6 | 205.9
789 | 568 | 476.3 | 190.52 | 222.7069 | 247.4 | 234.3 | 259.2 | 245.5 | 381.5 | 43.5 | 20.2 | 79.8 | 4.2 | 254.5 | 5.8 | 109.4 | 124.9 | 541.8 | 709.5 | 217.3 | 235.3 | 537.4 | 763.5 | 720.5 | 294.1 | 396 | 520.8 | 356.9 | 353.4 | 476 | 218.2 | 502.2 | 205.5 | 264.7 | 260 | 236.7 | 187.4 | 242.8 | 245.4 | 206.1
790 | 569 | 476.2 | 190.48 | 222.6601 | 247.1 | 234.1 | 259.4 | 245.3 | 383.3 | 43.5 | 20.2 | 79.8 | 4.4 | 261.8 | 5.6 | 109.6 | 125.1 | 543.7 | 721.1 | 217.6 | 235.6 | 532.6 | 753.8 | 720.1 | 294.5 | 398.6 | 537.9 | 357.2 | 353.2 | 472.6 | 218.4 | 502.9 | 205.7 | 264.5 | 260 | 237.1 | 187.6 | 243.6 | 245.2 | 206.4
791 | 570 | 476.7 | 190.68 | 222.8939 | 247.4 | 234.8 | 259.9 | 244.9 | 387.9 | 43.5 | 20.2 | 79.9 | 4.6 | 261.8 | 5.8 | 109.8 | 125.3 | 549.8 | 722.7 | 217.9 | 235.9 | 523.1 | 739.3 | 719.1 | 294.9 | 399.8 | 533.5 | 357.5 | 352.1 | 468.9 | 218.6 | 503.2 | 206 | 264.5 | 260.2 | 237.4 | 187.8 | 243.8 | 245 | 206.5
792 | 571 | 478.1 | 191.24 | 223.5485 | 248.4 | 235.8 | 260.7 | 244.6 | 388.3 | 43.5 | 20.2 | 79.8 | 4.7 | 245.3 | 6 | 110 | 125.5 | 551.5 | 725.7 | 218.2 | 236.2 | 520.7 | 726.2 | 718.4 | 295.3 | 399.3 | 527.9 | 357.8 | 350.6 | 469.3 | 218.7 | 503.3 | 206.2 | 264.7 | 260.4 | 237.7 | 188 | 243.7 | 244.9 | 206.7
793 | 572 | 477.6 | 191.04 | 223.3148 | 248.7 | 236.5 | 260.5 | 244.6 | 394.2 | 43.6 | 20.2 | 79.8 | 4.5 | 258 | 5.8 | 110.2 | 125.7 | 548.9 | 734.7 | 218.4 | 236.5 | 518.1 | 723.4 | 718.7 | 295.7 | 400.7 | 529.4 | 358.2 | 349.5 | 469.6 | 218.9 | 503.7 | 206.4 | 265.4 | 260.9 | 238 | 188.2 | 244.1 | 244.9 | 206.9
794 | 573 | 477 | 190.8 | 223.0342 | 248.7 | 236.9 | 261.4 | 244.2 | 393 | 43.6 | 20.2 | 79.8 | 4.4 | 254.8 | 5.8 | 110.4 | 125.9 | 545.3 | 729.3 | 218.7 | 236.8 | 529.2 | 725.7 | 720.9 | 296.1 | 398.6 | 528.3 | 358.5 | 349.8 | 474.5 | 219 | 503.4 | 206.7 | 265.5 | 261.3 | 238.1 | 188.4 | 244.3 | 245 | 207.1
795 | 574 | 478.2 | 191.28 | 223.5953 | 248.3 | 237.3 | 262.8 | 243.6 | 389.7 | 43.6 | 20.2 | 79.8 | 4.6 | 243.6 | 5.9 | 110.6 | 126.1 | 543.5 | 718.8 | 219 | 237.1 | 537.1 | 747.7 | 722.5 | 296.5 | 396.7 | 527.7 | 358.8 | 349.9 | 474.8 | 219.2 | 503 | 207 | 265.7 | 261.5 | 238 | 188.6 | 244.7 | 245 | 207.3
796 | 575 | 475.4 | 190.16 | 222.2861 | 248.8 | 238.2 | 262.1 | 244 | 386.7 | 43.8 | 20.2 | 79.8 | 4.5 | 250.4 | 6 | 110.8 | 126.3 | 545.1 | 716.4 | 219.2 | 237.4 | 536.4 | 756.9 | 722.8 | 296.9 | 395.2 | 527 | 359.2 | 349.7 | 474.7 | 219.3 | 502.9 | 207.2 | 265.8 | 261.9 | 238.1 | 188.9 | 245.5 | 244.9 | 207.6
797 | 576 | 476.6 | 190.64 | 222.8472 | 249.4 | 237.7 | 260.7 | 244.4 | 385.3 | 43.9 | 20.2 | 79.8 | 4.4 | 253.7 | 5.9 | 111 | 126.5 | 544.2 | 722 | 219.5 | 237.6 | 531.2 | 763.9 | 723.9 | 297.3 | 395.7 | 535.8 | 359.5 | 351.4 | 484.9 | 219.5 | 503.8 | 207.5 | 265.7 | 262.1 | 238.3 | 189.2 | 245.8 | 244.9 | 207.7
798 | 577 | 476.3 | 190.52 | 222.7069 | 249.7 | 236.7 | 259.7 | 244.4 | 387.4 | 44 | 20.2 | 79.7 | 4.2 | 252.4 | 5.7 | 111.1 | 126.7 | 545.2 | 720.9 | 219.8 | 237.9 | 528.7 | 748.2 | 722.6 | 297.7 | 397.8 | 545.3 | 359.9 | 350.9 | 482.1 | 219.6 | 505.8 | 207.8 | 265.6 | 262.2 | 238.6 | 189.5 | 245.7 | 245 | 207.8
799 | 578 | 477.7 | 191.08 | 223.3615 | 251 | 236.2 | 258.9 | 244.6 | 387.8 | 44 | 20.2 | 79.7 | 4.1 | 253.4 | 5.7 | 111.3 | 126.9 | 545.5 | 712.2 | 220 | 238.3 | 529.5 | 742.8 | 722.5 | 298.1 | 398.1 | 535.9 | 360.2 | 350.5 | 476.7 | 219.8 | 505.5 | 208 | 265.8 | 262.5 | 238.7 | 189.8 | 245.8 | 245.2 | 207.9
800 | 579 | 477.9 | 191.16 | 223.455 | 250.9 | 237 | 259.2 | 245.1 | 389.9 | 44.1 | 20.2 | 79.7 | 4 | 256.1 | 5.8 | 111.5 | 127.1 | 541.2 | 711.7 | 220.3 | 238.6 | 537.4 | 747.2 | 723.3 | 298.5 | 396.3 | 531.5 | 360.5 | 349.2 | 470.3 | 219.9 | 504.8 | 208.3 | 266.1 | 262.6 | 239 | 190.1 | 245.9 | 245.2 | 208.1
801 | 580 | 476.2 | 190.48 | 222.6601 | 249.7 | 237.6 | 259.7 | 245.8 | 387.7 | 44.1 | 20.2 | 79.8 | 4 | 260 | 6 | 111.7 | 127.3 | 544.3 | 717.3 | 220.6 | 238.9 | 548.9 | 761.7 | 723.9 | 298.8 | 394.3 | 528.4 | 360.9 | 349.2 | 475.1 | 220.1 | 504.8 | 208.6 | 266.1 | 262.7 | 239.1 | 190.4 | 246.1 | 245.2 | 208.3
802 | 581 | 476.3 | 190.52 | 222.7069 | 249.4 | 237.9 | 259.9 | 246.5 | 388.2 | 44.2 | 20.2 | 79.8 | 3.9 | 259.8 | 6.1 | 111.8 | 127.5 | 548.4 | 729.5 | 220.8 | 239.2 | 564.5 | 769.8 | 724.1 | 299.2 | 396.5 | 535.5 | 361.2 | 350.5 | 482.1 | 220.3 | 505.3 | 208.8 | 266.1 | 262.7 | 239.3 | 190.7 | 246.5 | 245 | 208.4
803 | 582 | 476.1 | 190.44 | 222.6134 | 248.4 | 237.8 | 260.1 | 246.8 | 391.8 | 44.2 | 20.2 | 80 | 3.8 | 258.5 | 6 | 112 | 127.7 | 553.8 | 730.5 | 221.1 | 239.5 | 574.1 | 776.7 | 725 | 299.6 | 399.5 | 545 | 361.5 | 351.5 | 484.9 | 220.4 | 505.9 | 209.1 | 266 | 262.7 | 239.6 | 191 | 246.7 | 244.9 | 208.6
804 | 583 | 476 | 190.4 | 222.5666 | 247.5 | 238.4 | 260.1 | 247.3 | 393.9 | 44.3 | 20.2 | 80.1 | 4.1 | 248.5 | 5.8 | 112.2 | 127.9 | 565.2 | 731 | 221.4 | 239.8 | 588.8 | 788.6 | 727.5 | 300 | 403.5 | 569.9 | 361.8 | 355.6 | 496 | 220.6 | 508.6 | 209.3 | 265.8 | 262.8 | 239.8 | 191.3 | 246.8 | 244.9 | 208.8
805 | 584 | 475.9 | 190.36 | 222.5199 | 247.3 | 237.7 | 260.5 | 247.4 | 394.2 | 44.3 | 20.2 | 80.1 | 3.8 | 249 | 5.7 | 112.4 | 128.1 | 583.9 | 733.4 | 221.7 | 240.2 | 610.3 | 796.8 | 728.3 | 300.4 | 403.7 | 579.7 | 362.1 | 360.1 | 509 | 220.8 | 511.5 | 209.5 | 265.6 | 262.7 | 240 | 191.6 | 247 | 244.9 | 208.9
806 | 585 | 476.2 | 190.48 | 222.6601 | 247.3 | 238.1 | 260.2 | 246.7 | 392.1 | 44.4 | 20.2 | 80.1 | 3.6 | 250.9 | 5.6 | 112.6 | 128.4 | 608.3 | 739.7 | 221.9 | 240.4 | 621.8 | 796.7 | 729.5 | 300.8 | 404.1 | 600.7 | 362.4 | 368.3 | 525 | 221 | 515.1 | 209.7 | 265.7 | 262.6 | 240 | 191.9 | 247 | 244.9 | 209
807 | 586 | 476 | 190.4 | 222.5666 | 247 | 238.3 | 258.7 | 246.7 | 391 | 44.4 | 20.2 | 80.2 | 3.6 | 248.6 | 5.5 | 112.8 | 128.6 | 622.6 | 739.6 | 222.2 | 240.7 | 628.1 | 794.2 | 729.3 | 301.2 | 407.6 | 608.2 | 362.7 | 375.9 | 539.7 | 221.2 | 518.9 | 210 | 265.9 | 262.9 | 240 | 192.2 | 247 | 245.2 | 209.2
808 | 587 | 475.9 | 190.36 | 222.5199 | 246.4 | 239.2 | 257.9 | 246.8 | 392.4 | 44.5 | 20.2 | 80.2 | 3.8 | 248.3 | 5.4 | 113 | 128.8 | 614.7 | 730.9 | 222.4 | 241 | 627.1 | 807.4 | 730.2 | 301.6 | 408.9 | 599.4 | 362.9 | 379.8 | 537.7 | 221.3 | 520 | 210.2 | 266 | 263.1 | 240.3 | 192.6 | 247.1 | 245.4 | 209.3
809 | 588 | 475.9 | 190.36 | 222.5199 | 246.2 | 238.9 | 257.3 | 247.5 | 390.1 | 44.6 | 20.2 | 80.3 | 3.9 | 248.1 | 5.4 | 113.2 | 129 | 610.6 | 723.3 | 222.7 | 241.3 | 636.2 | 806.3 | 730.9 | 302 | 408.5 | 590.8 | 363.2 | 381.6 | 540.5 | 221.5 | 520 | 210.4 | 265.9 | 263.1 | 240.4 | 192.9 | 247.5 | 245.6 | 209.6
810 | 589 | 476.5 | 190.6 | 222.8004 | 246 | 238.6 | 257.1 | 248.7 | 387.2 | 44.6 | 20.2 | 80.3 | 4.1 | 247.7 | 5.2 | 113.4 | 129.2 | 610.1 | 718.4 | 223 | 241.7 | 637.5 | 814.6 | 731.9 | 302.4 | 409.8 | 590.1 | 363.5 | 381.8 | 539.8 | 221.7 | 520.7 | 210.6 | 266 | 263.2 | 240.4 | 193.2 | 247.6 | 245.8 | 209.9
811 | 590 | 476.3 | 190.52 | 222.7069 | 246.2 | 237.9 | 256.6 | 248.8 | 384.4 | 44.7 | 20.2 | 80.4 | 4.1 | 249.1 | 4.9 | 113.6 | 129.4 | 609.4 | 716.3 | 223.2 | 242 | 640.3 | 818 | 732.8 | 302.8 | 409.8 | 583.4 | 363.8 | 381 | 535.3 | 221.9 | 520.5 | 210.8 | 265.8 | 262.9 | 240.4 | 193.6 | 247.5 | 246 | 210
812 | 591 | 476.1 | 190.44 | 222.6134 | 245.4 | 237 | 256.1 | 249 | 384.8 | 44.7 | 20.2 | 80.4 | 4.1 | 244.4 | 4.6 | 113.8 | 129.6 | 603.4 | 714 | 223.5 | 242.5 | 633.1 | 800.3 | 732.6 | 303.2 | 411 | 583.6 | 364 | 379.5 | 532 | 222 | 520 | 211 | 265.7 | 262.6 | 240.4 | 194 | 247.6 | 246.3 | 210.1
813 | 592 | 477.7 | 191.08 | 223.3615 | 247 | 235.8 | 255.1 | 249.5 | 389.1 | 44.8 | 20.2 | 80.4 | 3.8 | 243.4 | 4.4 | 114 | 129.8 | 599.8 | 705.8 | 223.7 | 242.9 | 627.9 | 803.2 | 733.5 | 303.6 | 409.9 | 572.4 | 364.3 | 379.1 | 529.4 | 222.2 | 519.5 | 211.2 | 265.7 | 262.4 | 240.4 | 194.3 | 247.6 | 246.5 | 210.3
814 | 593 | 479 | 191.6 | 223.9694 | 248.9 | 235.5 | 254.7 | 249.5 | 386.9 | 44.9 | 20.1 | 80.4 | 3.9 | 248.6 | 4.3 | 114.2 | 130 | 589.8 | 690.7 | 224 | 243.3 | 638.6 | 799.6 | 733 | 304 | 407.5 | 554.1 | 364.6 | 380.3 | 531.7 | 222.4 | 518.9 | 211.3 | 265.8 | 262.1 | 240.3 | 194.7 | 247.7 | 247 | 210.5
815 | 594 | 478.4 | 191.36 | 223.6888 | 250.2 | 235.6 | 254.9 | 249.8 | 385.1 | 45 | 20.2 | 80.5 | 4.2 | 248.7 | 4.1 | 114.4 | 130.2 | 576.3 | 682.2 | 224.3 | 243.7 | 636.2 | 790.5 | 732.3 | 304.4 | 404.8 | 537.3 | 364.9 | 380.2 | 523.8 | 222.6 | 517.5 | 211.5 | 265.7 | 262 | 240.2 | 195.2 | 248.2 | 247.6 | 210.7
816 | 595 | 477.7 | 191.08 | 223.3615 | 250.5 | 234.3 | 255.2 | 251 | 386.4 | 45 | 20.2 | 80.5 | 4.2 | 246.4 | 3.9 | 114.6 | 130.5 | 561.6 | 684 | 224.5 | 244.1 | 625 | 783.5 | 731 | 304.8 | 401 | 522.8 | 365.2 | 376.9 | 514.7 | 222.7 | 516 | 211.7 | 265.7 | 262.1 | 240.2 | 195.6 | 248.6 | 248.1 | 210.9
817 | 596 | 477.4 | 190.96 | 223.2212 | 250.7 | 232.9 | 255.8 | 252.9 | 381 | 45 | 20.2 | 80.5 | 4.4 | 246.5 | 3.8 | 114.8 | 130.7 | 565.8 | 688.9 | 224.8 | 244.4 | 616.4 | 803.6 | 732.5 | 305.2 | 401.8 | 520.5 | 365.5 | 373.4 | 514.3 | 222.9 | 515.9 | 211.9 | 265.7 | 262.3 | 240.3 | 196.1 | 248.8 | 248.6 | 211.1
818 | 597 | 476.9 | 190.76 | 222.9874 | 250.9 | 232.2 | 255.6 | 253.1 | 378.5 | 45.1 | 20.2 | 80.5 | 3.6 | 245 | 3.5 | 115 | 130.9 | 569 | 692.5 | 225.1 | 244.7 | 604.8 | 798.3 | 732.7 | 305.7 | 405.1 | 518.8 | 365.8 | 372.2 | 509.4 | 223 | 515.4 | 212.1 | 265.6 | 262.6 | 240.8 | 196.7 | 248.9 | 248.9 | 211.3
819 | 598 | 477 | 190.8 | 223.0342 | 249.7 | 231.2 | 255.2 | 252.7 | 380.3 | 45.1 | 20.2 | 80.5 | 4.1 | 245.5 | 3.2 | 115.2 | 131.1 | 568.2 | 707.2 | 225.3 | 245 | 589.9 | 779.7 | 732.9 | 306 | 405.9 | 526.5 | 366.2 | 369.9 | 507.4 | 223.1 | 514.5 | 212.4 | 265.7 | 262.9 | 241.2 | 197.4 | 249.1 | 248.9 | 211.4
820 | 599 | 476.8 | 190.72 | 222.9407 | 249.3 | 231 | 255.2 | 252.2 | 383.3 | 45.1 | 20.2 | 80.5 | 3.9 | 249.2 | 3 | 115.4 | 131.3 | 564.2 | 710.5 | 225.6 | 245.3 | 582 | 755.2 | 729.9 | 306.4 | 408.1 | 530.6 | 366.5 | 369.2 | 505.8 | 223.3 | 515.6 | 212.5 | 266 | 263.4 | 241.6 | 198.3 | 249 | 249.2 | 211.5
821 | 600 | 477.1 | 190.84 | 223.081 | 250.2 | 231.8 | 255 | 251.9 | 386.5 | 45.1 | 20.1 | 80.6 | 4 | 250.6 | 2.8 | 115.6 | 131.5 | 562.6 | 710 | 225.9 | 245.6 | 575.9 | 751.6 | 728 | 306.8 | 405.9 | 526.1 | 366.8 | 367.1 | 499.3 | 223.4 | 514.7 | 212.8 | 266.3 | 263.8 | 242 | 199.1 | 248.8 | 249.2 | 211.6
822 | 601 | 478.3 | 191.32 | 223.6421 | 251.2 | 233 | 257.4 | 251.8 | 386.6 | 45.2 | 20.1 | 80.6 | 3.7 | 250.4 | 2.6 | 115.9 | 131.7 | 562.9 | 714.9 | 226.2 | 245.9 | 572.9 | 754.5 | 727.9 | 307.1 | 404.6 | 528.9 | 367.2 | 367 | 500.8 | 223.6 | 514.6 | 213 | 266.6 | 264.1 | 242.3 | 199.8 | 248.6 | 249.3 | 211.7
823 | 602 | 477.6 | 191.04 | 223.3148 | 252.1 | 233.3 | 258.7 | 251.4 | 389.9 | 45.2 | 20.1 | 80.5 | 4.1 | 250.3 | 2.4 | 116.1 | 131.9 | 560.2 | 717.7 | 226.5 | 246.2 | 571.3 | 747.1 | 728.1 | 307.5 | 404.8 | 528.1 | 367.6 | 366.5 | 500.1 | 223.7 | 514.2 | 213.2 | 266.7 | 264.3 | 242.5 | 200.5 | 248.7 | 249.4 | 211.9
824 | 603 | 477.7 | 191.08 | 223.3615 | 253.3 | 234.5 | 259.4 | 251.1 | 386.7 | 45.2 | 20.1 | 80.5 | 3.4 | 250.3 | 2.2 | 116.3 | 132.1 | 551.8 | 715.9 | 226.8 | 246.5 | 570.9 | 764.3 | 727.8 | 307.9 | 403.6 | 525.2 | 367.9 | 369.1 | 505 | 223.9 | 514.3 | 213.4 | 266.9 | 264.5 | 242.5 | 201.3 | 248.7 | 249.4 | 212.1
825 | 604 | 478 | 191.2 | 223.5018 | 254.7 | 234.5 | 259.4 | 251.3 | 383.9 | 45.3 | 20.1 | 80.5 | 3.4 | 253.2 | 2.1 | 116.5 | 132.3 | 550.4 | 722.7 | 227.1 | 246.8 | 581.1 | 766.5 | 727.8 | 308.3 | 402.7 | 525.4 | 368.3 | 370.3 | 507 | 224.1 | 514 | 213.7 | 266.9 | 264.6 | 242.5 | 202.1 | 249.2 | 249.3 | 212.3
826 | 605 | 477.7 | 191.08 | 223.3615 | 256 | 234.7 | 259.8 | 250.8 | 385.2 | 45.4 | 20.1 | 80.7 | 4 | 256.6 | 2.2 | 116.7 | 132.5 | 551.3 | 726.6 | 227.4 | 247 | 589.5 | 775.5 | 728.2 | 308.7 | 401.8 | 525.9 | 368.6 | 370 | 508.4 | 224.2 | 513.7 | 213.9 | 267.2 | 264.9 | 242.8 | 202.9 | 249.2 | 249.5 | 212.5
827 | 606 | 477.7 | 191.08 | 223.3615 | 257.1 | 234.8 | 259.4 | 250.2 | 386.9 | 45.4 | 20.1 | 80.8 | 3.9 | 262 | 2.3 | 116.9 | 132.8 | 554.1 | 731.3 | 227.7 | 247.3 | 593.5 | 782.5 | 729.6 | 309 | 401.7 | 529 | 369 | 370.1 | 512.7 | 224.4 | 513.8 | 214.1 | 267.5 | 265 | 243.2 | 203.7 | 249.3 | 249.9 | 212.6
828 | 607 | 477.2 | 190.88 | 223.1277 | 257.6 | 235.4 | 259.7 | 250 | 387.5 | 45.4 | 20.1 | 81 | 3.8 | 266.1 | 2.4 | 117.1 | 133 | 555.6 | 733.2 | 228 | 247.6 | 587.7 | 784 | 730.9 | 309.4 | 401.9 | 539.7 | 369.3 | 371.1 | 511 | 224.5 | 514.6 | 214.3 | 267.8 | 265.1 | 243.4 | 204.5 | 249.4 | 250 | 212.8
829 | 608 | 477.5 | 191 | 223.268 | 257.1 | 236.2 | 259.8 | 250.2 | 387.9 | 45.3 | 20.1 | 81.1 | 4.2 | 266.2 | 2.4 | 117.3 | 133.2 | 556.9 | 738 | 228.3 | 247.9 | 581.1 | 767.7 | 731 | 309.8 | 402.3 | 542.3 | 369.7 | 370.8 | 508.4 | 224.7 | 514.1 | 214.6 | 267.8 | 265 | 243.7 | 205.3 | 249.3 | 250.2 | 213
830 | 609 | 477.4 | 190.96 | 223.2212 | 255.4 | 236.6 | 260.9 | 250.1 | 391.6 | 45.3 | 20.1 | 81.1 | 3.7 | 266.5 | 2.5 | 117.5 | 133.4 | 555.1 | 737.7 | 228.7 | 248.2 | 578.2 | 745.1 | 730.3 | 310.2 | 405.6 | 557.8 | 370.1 | 369.1 | 507.5 | 224.8 | 514.6 | 214.8 | 268 | 265 | 244 | 205.9 | 249.2 | 250.3 | 213.1
831 | 610 | 477.4 | 190.96 | 223.2212 | 254.2 | 237.8 | 261.8 | 250 | 394 | 45.3 | 20.1 | 81.2 | 4.1 | 267.3 | 2.5 | 117.7 | 133.6 | 555.7 | 740 | 229 | 248.5 | 578.4 | 758.4 | 731.5 | 310.6 | 410.1 | 566.6 | 370.5 | 369.6 | 505.8 | 225 | 515 | 215 | 268.1 | 265 | 244 | 206.6 | 249.4 | 250.4 | 213.3
832 | 611 | 477.1 | 190.84 | 223.081 | 253.8 | 239.2 | 263 | 249.6 | 400.2 | 45.3 | 20.1 | 81.4 | 4.6 | 268.7 | 2.5 | 117.9 | 133.9 | 573 | 749.6 | 229.3 | 248.8 | 577.9 | 756.1 | 731.9 | 311 | 414.1 | 585 | 370.8 | 372.2 | 512.9 | 225.1 | 516.6 | 215.2 | 268.2 | 265.1 | 244 | 207.1 | 249.7 | 250.4 | 213.4
833 | 612 | 477.7 | 191.08 | 223.3615 | 253.7 | 239.3 | 262.9 | 249.4 | 402.1 | 45.3 | 20.1 | 81.5 | 4.3 | 269.7 | 2.5 | 118.1 | 134.1 | 586.1 | 750.5 | 229.7 | 249.1 | 576.9 | 757.5 | 732.7 | 311.4 | 416.5 | 592.2 | 371.2 | 375.8 | 517.6 | 225.2 | 518.1 | 215.4 | 268.6 | 265.4 | 244.1 | 207.6 | 249.6 | 250.4 | 213.6
834 | 613 | 477.4 | 190.96 | 223.2212 | 254.1 | 239.5 | 262.2 | 249.5 | 401.2 | 45.3 | 20.1 | 81.6 | 4.2 | 277.9 | 2.4 | 118.3 | 134.3 | 590.3 | 747.1 | 230 | 249.4 | 579 | 766.4 | 732.7 | 311.7 | 416.4 | 578.7 | 371.5 | 376.5 | 512.7 | 225.4 | 518.1 | 215.6 | 269.2 | 265.9 | 244.1 | 208.1 | 249.5 | 250.6 | 213.8
835 | 614 | 477.3 | 190.92 | 223.1745 | 253.9 | 239.3 | 261.9 | 249.2 | 396.8 | 45.3 | 20.1 | 81.7 | 3.8 | 288.2 | 2.4 | 118.5 | 134.6 | 596.2 | 748.3 | 230.3 | 249.7 | 576.7 | 780.5 | 734 | 312.1 | 414.1 | 569.6 | 371.8 | 378.6 | 511.2 | 225.5 | 517.6 | 215.9 | 269.4 | 266.1 | 244.3 | 208.6 | 249.6 | 250.7 | 214
836 | 615 | 476.6 | 190.64 | 222.8472 | 254.5 | 239.5 | 261.7 | 249.4 | 393.5 | 45.3 | 20.1 | 81.8 | 3.9 | 290.1 | 2.3 | 118.7 | 134.8 | 590.7 | 738.2 | 230.6 | 250 | 575.5 | 789.9 | 733.7 | 312.6 | 416.9 | 555.4 | 372.1 | 381.4 | 510.7 | 225.7 | 517 | 216.1 | 269.4 | 266.1 | 244.1 | 209.1 | 249.8 | 251.1 | 214.2
837 | 616 | 476.7 | 190.68 | 222.8939 | 253.6 | 238 | 260.6 | 250.8 | 391.3 | 45.3 | 20.1 | 81.9 | 3.7 | 289.9 | 2.2 | 118.9 | 135 | 602 | 734.9 | 230.9 | 250.3 | 587.8 | 810.4 | 735 | 312.9 | 429.2 | 551.8 | 372.4 | 382.3 | 515.2 | 225.8 | 517.2 | 216.3 | 269.2 | 265.9 | 244.1 | 209.5 | 250.2 | 251.5 | 214.4
838 | 617 | 476.4 | 190.56 | 222.7537 | 254 | 236.6 | 259.7 | 252.4 | 389.8 | 45.3 | 20.1 | 82 | 3.9 | 287.6 | 2 | 119.1 | 135.2 | 618.5 | 743.2 | 231.3 | 250.7 | 594.1 | 814.9 | 736.8 | 313.3 | 429.9 | 571 | 372.7 | 386.7 | 526.8 | 226 | 519.7 | 216.6 | 269 | 266.3 | 244.3 | 210 | 250.6 | 252 | 214.6
839 | 618 | 476.3 | 190.52 | 222.7069 | 254.8 | 236.3 | 258.1 | 253 | 390.8 | 45.4 | 20.1 | 82.1 | 3.9 | 280.5 | 1.9 | 119.3 | 135.5 | 621.1 | 742.1 | 231.6 | 251 | 612.6 | 819.8 | 737.1 | 313.7 | 429 | 569.8 | 373 | 391.6 | 537 | 226.1 | 521.8 | 216.7 | 268.9 | 266.5 | 244.7 | 210.6 | 251.1 | 252.6 | 214.8
840 | 619 | 476.9 | 190.76 | 222.9874 | 256.3 | 236.1 | 257.2 | 253.2 | 392 | 45.5 | 20.1 | 82.2 | 4.1 | 272.1 | 1.8 | 119.5 | 135.7 | 618.7 | 736.8 | 231.9 | 251.3 | 611.6 | 806.5 | 736.9 | 314.1 | 427.8 | 553.8 | 373.2 | 394 | 533.2 | 226.3 | 521.9 | 217 | 268.9 | 266.5 | 244.7 | 211.1 | 251.3 | 253 | 215
841 | 620 | 477.1 | 190.84 | 223.081 | 256.1 | 235.9 | 256.8 | 253.4 | 391.6 | 45.7 | 20.1 | 82.3 | 4.3 | 266 | 1.8 | 119.7 | 135.9 | 613.3 | 738.2 | 232.2 | 251.6 | 608.4 | 811.3 | 737.7 | 314.6 | 448.1 | 543.7 | 373.5 | 391.3 | 526.4 | 226.4 | 521.2 | 217.2 | 268.9 | 266.5 | 244.9 | 211.6 | 251.4 | 253.2 | 215.2
842 | 621 | 476.8 | 190.72 | 222.9407 | 256.2 | 236.2 | 257.1 | 252.4 | 389.9 | 45.8 | 20.1 | 82.5 | 4.4 | 259.2 | 1.9 | 119.9 | 136.1 | 613 | 736.4 | 232.6 | 251.9 | 611.1 | 806.1 | 737.5 | 315 | 469 | 545.4 | 373.9 | 393.3 | 533.4 | 226.6 | 522.6 | 217.4 | 269 | 266.5 | 244.9 | 212 | 251.7 | 253.4 | 215.4
843 | 622 | 477 | 190.8 | 223.0342 | 255.8 | 236 | 257.1 | 252.7 | 391.3 | 45.9 | 20.1 | 82.7 | 4.2 | 259.8 | 1.9 | 120.1 | 136.4 | 616.1 | 736.8 | 232.9 | 252.2 | 604 | 808 | 737.5 | 315.4 | 465.2 | 547.8 | 374.2 | 393.4 | 529.6 | 226.7 | 522.8 | 217.6 | 269.2 | 266.6 | 245 | 212.4 | 252.2 | 253.5 | 215.8
844 | 623 | 477 | 190.8 | 223.0342 | 255.7 | 236 | 256.4 | 252.8 | 394.2 | 46 | 20.1 | 82.8 | 4.8 | 260.6 | 1.8 | 120.3 | 136.6 | 623.5 | 738.1 | 233.2 | 252.5 | 596.3 | 787.7 | 738.5 | 315.8 | 464.1 | 555.6 | 374.6 | 391.8 | 526.4 | 226.9 | 523 | 217.8 | 269.6 | 267 | 245.5 | 212.9 | 252.6 | 253.6 | 216
845 | 624 | 477 | 190.8 | 223.0342 | 255.9 | 236.9 | 256.7 | 252.6 | 405.7 | 46.1 | 20.1 | 82.8 | 4.1 | 254.4 | 1.6 | 120.5 | 136.8 | 616.3 | 731.3 | 233.5 | 252.8 | 588.4 | 755.9 | 736.2 | 316.2 | 462.2 | 553.4 | 374.9 | 389.3 | 517.2 | 227.1 | 522.2 | 218 | 270.3 | 267.3 | 246 | 213.4 | 252.6 | 253.6 | 216.1
846 | 625 | 476.8 | 190.72 | 222.9407 | 255.8 | 237.9 | 258.7 | 251.9 | 409.8 | 46.2 | 20.1 | 82.8 | 4.1 | 241.6 | 1.5 | 120.8 | 137 | 606.4 | 729.7 | 233.8 | 253.1 | 577.9 | 729.4 | 733.1 | 316.7 | 463.7 | 553.6 | 375.2 | 386.5 | 507.3 | 227.2 | 521.4 | 218.2 | 270.8 | 267.9 | 246.4 | 213.8 | 252.4 | 253.7 | 216.1
847 | 626 | 476.9 | 190.76 | 222.9874 | 255.7 | 237.8 | 261.8 | 251.8 | 411.8 | 46.3 | 20.1 | 82.8 | 4.1 | 234.5 | 1.6 | 121 | 137.2 | 598.8 | 727.5 | 234 | 253.4 | 574.9 | 729.5 | 732.7 | 317 | 469.4 | 551.7 | 375.5 | 383.4 | 499.4 | 227.4 | 520.2 | 218.4 | 271.4 | 268.4 | 246.8 | 214.1 | 252.4 | 254 | 216.2
848 | 627 | 477 | 190.8 | 223.0342 | 255 | 238.4 | 265.5 | 252.4 | 411.7 | 46.3 | 20.1 | 82.7 | 4.1 | 240.7 | 1.9 | 121.2 | 137.4 | 592.6 | 730.4 | 234.3 | 253.7 | 570.5 | 730.5 | 732.2 | 317.5 | 469.5 | 555.2 | 375.9 | 381.8 | 494.7 | 227.5 | 519.7 | 218.7 | 271.9 | 269.2 | 247 | 214.5 | 252.2 | 254.2 | 216.4
849 | 628 | 475.9 | 190.36 | 222.5199 | 255.2 | 239.3 | 267.6 | 252.6 | 412.6 | 46.3 | 20.1 | 82.7 | 4.7 | 255 | 2.5 | 121.4 | 137.7 | 594.3 | 731.2 | 234.6 | 254 | 564.2 | 705.6 | 730.6 | 317.9 | 468.7 | 563 | 376.2 | 382 | 493.2 | 227.7 | 519.8 | 218.9 | 272.4 | 270 | 247.5 | 214.8 | 252.3 | 254.2 | 216.5
850 | 629 | 475.4 | 190.16 | 222.2861 | 255.9 | 240.8 | 269.1 | 253 | 415.1 | 46.2 | 20.1 | 82.8 | 4.9 | 265.5 | 3 | 121.6 | 137.9 | 589.4 | 732.1 | 234.9 | 254.3 | 565.7 | 709.4 | 730.2 | 318.3 | 476.6 | 559.6 | 376.5 | 381.6 | 488.9 | 227.8 | 519.2 | 219.2 | 272.9 | 270.6 | 248 | 215 | 252.6 | 254.4 | 216.7
851 | 630 | 476.7 | 190.68 | 222.8939 | 256.9 | 241.8 | 270.1 | 254.1 | 421.9 | 46.2 | 20.1 | 82.9 | 4.8 | 267 | 3.2 | 121.8 | 138.1 | 597.4 | 735.8 | 235.1 | 254.6 | 567.5 | 713.4 | 730.1 | 318.7 | 476.1 | 563.4 | 376.8 | 381.8 | 489.2 | 228 | 518.8 | 219.4 | 273.3 | 271.1 | 248.1 | 215.3 | 252.6 | 254.8 | 216.8
852 | 631 | 476.6 | 190.64 | 222.8472 | 258.3 | 242.5 | 270.6 | 253.8 | 431 | 46.2 | 20.1 | 82.9 | 4.6 | 260.9 | 3.3 | 122 | 138.4 | 603.1 | 731.6 | 235.4 | 254.8 | 570.4 | 691 | 728.5 | 319.1 | 478.8 | 573.6 | 377.2 | 383.6 | 492 | 228.1 | 519.6 | 219.7 | 273.7 | 271.7 | 248.6 | 215.6 | 252.5 | 255 | 216.9
853 | 632 | 476.6 | 190.64 | 222.8472 | 260 | 242.8 | 270.8 | 253.2 | 432 | 46.3 | 20.1 | 83 | 4.5 | 261.4 | 3.7 | 122.3 | 138.6 | 606.1 | 734.8 | 235.8 | 255.1 | 565.3 | 680.6 | 727.5 | 319.6 | 482.8 | 587.4 | 377.5 | 384.9 | 495.6 | 228.3 | 520.8 | 219.9 | 273.9 | 272.2 | 248.8 | 215.9 | 252.4 | 255.2 | 217
854 | 633 | 477.1 | 190.84 | 223.081 | 261.2 | 243.9 | 272.3 | 253.8 | 432.6 | 46.3 | 20.1 | 83.2 | 5.1 | 269.7 | 4 | 122.5 | 138.9 | 602.8 | 737 | 236.1 | 255.4 | 554.5 | 682.2 | 727.5 | 320.1 | 487.4 | 604.7 | 377.8 | 386.8 | 499.2 | 228.5 | 521.5 | 220.2 | 274.1 | 272.6 | 248.9 | 216.1 | 252.5 | 255.6 | 217.2
855 | 634 | 476.7 | 190.68 | 222.8939 | 262.2 | 245.9 | 272 | 254.2 | 437.9 | 46.4 | 20.1 | 83.3 | 5 | 265.7 | 4.1 | 122.7 | 139.1 | 606 | 737.2 | 236.5 | 255.7 | 553.6 | 683.6 | 727.7 | 320.5 | 491.1 | 615.1 | 378.2 | 388.1 | 503.2 | 228.6 | 522.3 | 220.4 | 274.4 | 273 | 249.1 | 216.4 | 252.8 | 255.8 | 217.3
856 | 635 | 476.5 | 190.6 | 222.8004 | 262.1 | 247.6 | 271.8 | 254 | 438 | 46.4 | 20.1 | 83.3 | 4.5 | 259.4 | 4.6 | 123 | 139.4 | 615.2 | 732.4 | 236.9 | 256 | 566.7 | 701.4 | 728.2 | 321 | 494.6 | 607.3 | 378.5 | 392.1 | 512.8 | 228.8 | 523.1 | 220.7 | 274.8 | 273.3 | 249.1 | 216.7 | 253.1 | 255.8 | 217.6
857 | 636 | 476.6 | 190.64 | 222.8472 | 261.6 | 248.2 | 272 | 252.9 | 433.8 | 46.5 | 20.1 | 83.4 | 4.5 | 256.6 | 4.7 | 123.2 | 139.6 | 618.1 | 734.5 | 237.3 | 256.3 | 573.3 | 726.7 | 728.9 | 321.4 | 502.2 | 600.1 | 378.8 | 394.9 | 518.3 | 229 | 524.7 | 220.9 | 275 | 273.5 | 249.3 | 217 | 253.4 | 255.8 | 217.8
858 | 637 | 477.2 | 190.88 | 223.1277 | 262 | 248.2 | 271.1 | 253.6 | 432.2 | 46.6 | 20.1 | 83.5 | 4.1 | 271.8 | 4.6 | 123.4 | 139.9 | 614.8 | 732.9 | 237.7 | 256.7 | 569.9 | 731.5 | 728.1 | 321.9 | 502.1 | 598.2 | 379.1 | 395 | 518 | 229.1 | 524.5 | 221.2 | 275 | 273.8 | 249.6 | 217.3 | 253.8 | 255.8 | 217.9
859 | 638 | 476.3 | 190.52 | 222.7069 | 261.9 | 247.9 | 269.7 | 254 | 431.9 | 46.7 | 20.1 | 83.6 | 4.3 | 254.8 | 4.7 | 123.7 | 140.1 | 620.6 | 742.6 | 238 | 257 | 568 | 738.7 | 728.8 | 322.3 | 502.5 | 604.9 | 379.5 | 395.5 | 521.2 | 229.3 | 525.5 | 221.5 | 275.4 | 273.9 | 249.8 | 217.5 | 254.1 | 255.8 | 218.1
860 | 639 | 476.8 | 190.72 | 222.9407 | 261.1 | 247.8 | 269.8 | 254 | 435.6 | 46.8 | 20.1 | 83.6 | 4.8 | 253.4 | 4.8 | 123.9 | 140.4 | 627 | 744 | 238.3 | 257.3 | 564.7 | 736.6 | 729.4 | 322.6 | 506.6 | 612.4 | 379.7 | 397.5 | 524.4 | 229.4 | 526.7 | 221.7 | 275.6 | 274.1 | 250 | 217.8 | 254.4 | 255.7 | 218.3
861 | 640 | 476.8 | 190.72 | 222.9407 | 261.4 | 247.9 | 270.5 | 254.2 | 442.1 | 46.8 | 20.1 | 83.6 | 4.9 | 255.9 | 5.1 | 124.2 | 140.6 | 633.2 | 740.6 | 238.7 | 257.5 | 566.1 | 710.2 | 725.5 | 323.1 | 516 | 612.6 | 380.1 | 399.3 | 527.6 | 229.6 | 527.4 | 222 | 275.7 | 274.3 | 250.4 | 218.1 | 254.6 | 255.6 | 218.6
862 | 641 | 476.5 | 190.6 | 222.8004 | 262.5 | 248.5 | 271.2 | 254 | 444.9 | 46.7 | 20.1 | 83.6 | 4.6 | 248.4 | 5.2 | 124.5 | 140.8 | 639.5 | 739.6 | 239.1 | 257.8 | 560.5 | 692.7 | 724.2 | 323.4 | 519.7 | 621.7 | 380.4 | 400.2 | 529.2 | 229.8 | 528.3 | 222.2 | 276.2 | 274.8 | 250.7 | 218.3 | 254.8 | 255.5 | 218.7
863 | 642 | 475.1 | 190.04 | 222.1458 | 262.9 | 249.6 | 273 | 255 | 444.9 | 46.8 | 20.1 | 83.6 | 4.2 | 243.3 | 5 | 124.7 | 141 | 638.1 | 741.7 | 239.5 | 258.1 | 554.8 | 694.3 | 725.3 | 323.8 | 521.8 | 622.7 | 380.7 | 400.5 | 528.9 | 229.9 | 529.2 | 222.5 | 276.6 | 275.3 | 250.9 | 218.6 | 254.9 | 255.5 | 218.9
864 | 643 | 476.2 | 190.48 | 222.6601 | 263 | 250.4 | 274.7 | 255.6 | 444.2 | 46.8 | 20.1 | 83.6 | 3.9 | 239.1 | 5.3 | 125 | 141.3 | 626.7 | 738.3 | 240 | 258.4 | 548.9 | 696.7 | 725.1 | 324.2 | 518.9 | 617.1 | 381 | 399.7 | 524.5 | 230.1 | 529.1 | 222.9 | 276.8 | 275.6 | 251.1 | 218.8 | 254.9 | 255.9 | 219
865 | 644 | 476.3 | 190.52 | 222.7069 | 263.1 | 250.4 | 275.6 | 256.1 | 438.6 | 46.8 | 20.1 | 83.6 | 4 | 238.9 | 5.7 | 125.2 | 141.5 | 629.2 | 740.6 | 240.4 | 258.7 | 545.5 | 701.3 | 725.6 | 324.7 | 513.1 | 609.7 | 381.3 | 398 | 527.3 | 230.2 | 529.4 | 223.2 | 276.8 | 275.9 | 251.1 | 219.1 | 255.2 | 256.2 | 219.1
866 | 645 | 476.2 | 190.48 | 222.6601 | 263 | 249.5 | 275.4 | 256.5 | 435.9 | 46.9 | 20 | 83.7 | 4.3 | 243.1 | 6 | 125.5 | 141.7 | 626.8 | 748.5 | 240.9 | 259.1 | 548.6 | 707.2 | 725.3 | 325.1 | 511 | 623.2 | 381.6 | 396.9 | 524.1 | 230.4 | 530.1 | 223.4 | 276.9 | 276 | 251.3 | 219.3 | 255.3 | 256.6 | 219.3
867 | 646 | 476.7 | 190.68 | 222.8939 | 262.2 | 248.7 | 275 | 256.3 | 445.2 | 46.9 | 20 | 83.7 | 3.9 | 246.1 | 5.6 | 125.8 | 142 | 625 | 750.8 | 241.4 | 259.4 | 548.3 | 695.3 | 725.4 | 325.6 | 520.6 | 630.8 | 382 | 398.9 | 523 | 230.5 | 531.1 | 223.8 | 277.2 | 276.2 | 251.6 | 219.6 | 255.6 | 256.8 | 219.5
868 | 647 | 476.2 | 190.48 | 222.6601 | 262.6 | 249.4 | 274.6 | 256.2 | 453.7 | 47.1 | 20 | 83.7 | 3.9 | 239 | 5.1 | 126 | 142.2 | 627.3 | 752.6 | 241.8 | 259.7 | 543.3 | 695.6 | 724.7 | 326.1 | 539.9 | 642.4 | 382.3 | 397.5 | 520.8 | 230.7 | 531.2 | 224 | 277.8 | 276.5 | 252.1 | 219.8 | 256.4 | 256.8 | 219.7
869 | 648 | 476.2 | 190.48 | 222.6601 | 263.1 | 250.2 | 274.1 | 256.4 | 456.1 | 47.2 | 20 | 83.8 | 4 | 241.6 | 4.7 | 126.3 | 142.4 | 635.4 | 756.6 | 242.2 | 260.1 | 543.1 | 696 | 723.9 | 326.5 | 544.7 | 653.5 | 382.6 | 398.4 | 528.4 | 230.8 | 532.3 | 224.3 | 278.3 | 277 | 252.4 | 220.1 | 257 | 256.9 | 219.8
870 | 649 | 478.6 | 191.44 | 223.7823 | 262.1 | 251.6 | 274.3 | 256.5 | 458.1 | 47.2 | 20 | 83.8 | 4.1 | 246.5 | 4.4 | 126.6 | 142.7 | 630.8 | 752.1 | 242.6 | 260.4 | 541.9 | 685.4 | 722.4 | 327 | 551.5 | 647.4 | 382.9 | 399.8 | 527.8 | 231 | 534.1 | 224.5 | 278.8 | 277.5 | 252.8 | 220.4 | 257.7 | 257.1 | 220
871 | 650 | 476.9 | 190.76 | 222.9874 | 262.3 | 252.2 | 274.8 | 256.9 | 456.3 | 47.2 | 20 | 83.9 | 3.7 | 248.1 | 4.1 | 126.8 | 142.9 | 625.2 | 743.8 | 242.9 | 260.7 | 543.3 | 686.4 | 721.6 | 327.5 | 556.9 | 634.6 | 383.3 | 399.8 | 524.8 | 231.2 | 533.1 | 224.8 | 279.5 | 277.9 | 253 | 220.7 | 258.6 | 257.3 | 220.1
872 | 651 | 477.9 | 191.16 | 223.455 | 262.5 | 252.4 | 275.7 | 257.5 | 453.4 | 47.3 | 20 | 83.9 | 3.9 | 245.8 | 4.1 | 127.1 | 143.1 | 620.7 | 742.9 | 243.2 | 261.1 | 548.3 | 708.5 | 724.5 | 328 | 561.8 | 634.2 | 383.6 | 399.7 | 523.6 | 231.3 | 533.3 | 225 | 279.8 | 278.1 | 253 | 221.1 | 259.4 | 257.4 | 220.5
873 | 652 | 477.7 | 191.08 | 223.3615 | 262.4 | 252 | 276.2 | 258.2 | 450.7 | 47.3 | 20 | 83.9 | 4.3 | 242.5 | 4.3 | 127.4 | 143.3 | 628.9 | 741 | 243.5 | 261.4 | 556.8 | 719.2 | 725 | 328.4 | 565.9 | 633.1 | 384 | 399.1 | 523.5 | 231.5 | 533.5 | 225.3 | 280 | 278.2 | 253 | 221.4 | 259.9 | 257.6 | 220.6
874 | 653 | 476.4 | 190.56 | 222.7537 | 261.8 | 252.4 | 276.9 | 258.4 | 447.7 | 47.3 | 20 | 83.9 | 3.6 | 240.5 | 4.2 | 127.6 | 143.5 | 636.3 | 743.2 | 243.8 | 261.7 | 553.4 | 727.2 | 725.8 | 328.9 | 565.5 | 637 | 384.3 | 400.7 | 527.5 | 231.7 | 534.9 | 225.5 | 280.1 | 278.2 | 253.1 | 221.7 | 260.4 | 257.6 | 220.8
875 | 654 | 475.9 | 190.36 | 222.5199 | 263.3 | 252.7 | 277 | 258.1 | 445.3 | 47.3 | 20 | 83.9 | 3.2 | 238.5 | 4 | 127.9 | 143.8 | 627.3 | 742.7 | 244.1 | 262 | 545 | 731.1 | 726.8 | 329.5 | 559.8 | 631.8 | 384.7 | 400.7 | 523.1 | 231.9 | 534.5 | 225.7 | 280.3 | 278.4 | 253.2 | 222 | 260.9 | 257.6 | 221
876 | 655 | 476.2 | 190.48 | 222.6601 | 264.8 | 252 | 276.3 | 257.6 | 444.3 | 47.2 | 20 | 83.9 | 3.9 | 241.3 | 4.1 | 128.2 | 144 | 626.1 | 745.6 | 244.3 | 262.4 | 541.9 | 737.2 | 726.8 | 329.9 | 566.6 | 627.2 | 385.1 | 399.4 | 520.2 | 232.1 | 534 | 226 | 280.5 | 278.6 | 253.4 | 222.3 | 261.4 | 257.8 | 221.1
877 | 656 | 477.2 | 190.88 | 223.1277 | 266.4 | 251 | 275.4 | 257.5 | 440.4 | 47.2 | 20 | 84 | 3.9 | 250.5 | 4.1 | 128.5 | 144.2 | 620.9 | 740 | 244.6 | 262.7 | 543.8 | 751.1 | 726.4 | 330.4 | 564.6 | 608.9 | 385.5 | 398.4 | 517.6 | 232.3 | 533.8 | 226.2 | 280.7 | 278.5 | 253.4 | 222.6 | 261.8 | 257.8 | 221.4
878 | 657 | 478.1 | 191.24 | 223.5485 | 266.9 | 250.8 | 275.3 | 257.8 | 432.6 | 47.2 | 20 | 84.2 | 4.2 | 254.2 | 4 | 128.7 | 144.4 | 615.7 | 742.6 | 244.8 | 263 | 543.3 | 773.3 | 728.4 | 330.9 | 558.3 | 597 | 385.8 | 399.4 | 518.1 | 232.5 | 533.5 | 226.4 | 280.9 | 278.2 | 253.2 | 222.9 | 262 | 257.9 | 221.5
879 | 658 | 477.2 | 190.88 | 223.1277 | 266.9 | 250.4 | 274.3 | 258.3 | 428.8 | 47.2 | 20 | 84.3 | 3.6 | 249.9 | 3.9 | 129 | 144.7 | 621.3 | 751.7 | 245.1 | 263.4 | 544 | 787.1 | 729.9 | 331.5 | 563.7 | 605.3 | 386 | 404.9 | 533.9 | 232.7 | 535.8 | 226.7 | 281 | 278.2 | 253.2 | 223.3 | 262.5 | 258 | 221.7
880 | 659 | 476.9 | 190.76 | 222.9874 | 266.7 | 249 | 272.5 | 258.7 | 429.6 | 47.3 | 20 | 84.3 | 4 | 241.6 | 3.8 | 129.3 | 144.9 | 626.7 | 750.9 | 245.3 | 263.7 | 542.4 | 769.8 | 728.5 | 332.2 | 561.5 | 608.5 | 386.3 | 407.7 | 545.9 | 232.9 | 538.6 | 226.9 | 281.2 | 278.2 | 253.5 | 223.7 | 263 | 258.1 | 222
881 | 660 | 474.3 | 189.72 | 221.7717 | 266.7 | 247.7 | 271 | 260.2 | 434.1 | 47.4 | 20 | 84.3 | 4.1 | 237.2 | 3.8 | 129.5 | 145.1 | 607.5 | 740.8 | 245.6 | 264 | 540.4 | 753.4 | 726.2 | 332.8 | 553.9 | 601.4 | 386.6 | 404.6 | 537.3 | 233.1 | 537.5 | 227.1 | 281.4 | 278.1 | 253.9 | 224 | 263.2 | 258.1 | 222.1
882 | 661 | 468.3 | 187.32 | 218.9663 | 265.7 | 247.9 | 270.7 | 261.3 | 432.7 | 47.5 | 20 | 84.4 | 4.4 | 241.2 | 3.8 | 129.8 | 145.3 | 602.7 | 741.2 | 245.8 | 264.4 | 547.5 | 769.1 | 727.4 | 333.3 | 542.6 | 594.3 | 386.8 | 401.1 | 532.1 | 233.2 | 536.8 | 227.3 | 281.6 | 278.1 | 254.1 | 224.2 | 263.8 | 258.3 | 222.3
883 | 662 | 469.4 | 187.76 | 219.4806 | 265.5 | 248.5 | 271.2 | 260.4 | 432.4 | 47.6 | 20 | 84.4 | 4.2 | 245.3 | 4.1 | 130.1 | 145.5 | 598.8 | 743.6 | 246.1 | 264.7 | 543.7 | 774.4 | 728.5 | 333.8 | 535.1 | 594.2 | 387.1 | 400.1 | 528.7 | 233.4 | 536.9 | 227.5 | 282.2 | 278.7 | 254.4 | 224.6 | 263.6 | 258.4 | 222.4
884 | 663 | 470 | 188 | 219.7612 | 267.3 | 248.8 | 272 | 260.2 | 435.7 | 47.6 | 20 | 84.5 | 3.8 | 237.5 | 4.4 | 130.4 | 145.8 | 606 | 750.9 | 246.3 | 265 | 541.6 | 776.7 | 729.4 | 334.5 | 539.7 | 613.7 | 387.4 | 401 | 530.9 | 233.6 | 538.1 | 227.6 | 282.5 | 279 | 254.5 | 224.8 | 263.3 | 258.5 | 222.5
885 | 664 | 469.8 | 187.92 | 219.6677 | 268.6 | 249.1 | 273 | 259.3 | 439.5 | 47.6 | 20 | 84.6 | 3.9 | 227.1 | 4.6 | 130.6 | 146 | 621.8 | 756.8 | 246.5 | 265.4 | 546.6 | 797.9 | 730.6 | 335.2 | 541.8 | 630.3 | 387.7 | 402.7 | 535.5 | 233.8 | 539.6 | 227.8 | 282.4 | 279.2 | 254.6 | 225 | 262.9 | 258.4 | 222.6
886 | 665 | 468.9 | 187.56 | 219.2468 | 269.8 | 248.8 | 273.3 | 259.7 | 438.9 | 47.6 | 20 | 84.6 | 4.4 | 221.5 | 4.8 | 130.9 | 146.3 | 625.8 | 759.9 | 246.7 | 265.7 | 553.7 | 795.2 | 732.2 | 335.8 | 553.3 | 636.8 | 388.1 | 405.8 | 541.5 | 234 | 541.3 | 227.9 | 282.3 | 279.2 | 254.7 | 225.3 | 262.7 | 258.5 | 222.7
887 | 666 | 465.8 | 186.32 | 217.7973 | 270.3 | 249.5 | 273.3 | 260.3 | 439.1 | 47.5 | 20 | 84.7 | 4.4 | 225.8 | 4.5 | 131.1 | 146.5 | 613.5 | 746.6 | 246.9 | 266.1 | 558 | 767.2 | 729.9 | 336.4 | 559.3 | 626.5 | 388.5 | 404.7 | 537.7 | 234.2 | 540.5 | 228 | 282.5 | 279.5 | 255 | 225.5 | 262.9 | 258.6 | 222.8
888 | 667 | 463.6 | 185.44 | 216.7687 | 269.9 | 250.1 | 272.4 | 260 | 437.5 | 47.6 | 20 | 84.8 | 4.2 | 236.4 | 4.2 | 131.4 | 146.7 | 596 | 739.6 | 247 | 266.4 | 546.5 | 742.1 | 727.7 | 337.1 | 551.4 | 609 | 388.9 | 401.6 | 529.3 | 234.3 | 539.4 | 228.1 | 282.8 | 279.7 | 255.3 | 225.8 | 262.8 | 258.9 | 223
889 | 668 | 462.6 | 185.04 | 216.3011 | 270.8 | 249.8 | 272.1 | 259.1 | 433.2 | 47.5 | 20 | 84.9 | 4.5 | 243.6 | 3.8 | 131.7 | 146.9 | 593.4 | 742.5 | 247.2 | 266.8 | 541.7 | 736.5 | 726.7 | 337.8 | 545.4 | 607.7 | 389.3 | 398.4 | 529.3 | 234.5 | 539 | 228.2 | 283.3 | 279.7 | 255.6 | 226.1 | 262.5 | 259.1 | 223.1
890 | 669 | 461.5 | 184.6 | 215.7868 | 271.3 | 249.7 | 273.1 | 256.9 | 436.1 | 47.6 | 20 | 85 | 4.5 | 245.7 | 3.6 | 131.9 | 147.2 | 596.8 | 747.2 | 247.4 | 267.1 | 540 | 725.4 | 724.5 | 338.4 | 542.5 | 614.7 | 389.8 | 398.9 | 536.5 | 234.6 | 540.4 | 228.2 | 283.8 | 280 | 256 | 226.3 | 262.4 | 259 | 223.3
891 | 670 | 459.7 | 183.88 | 214.9451 | 270.6 | 248.5 | 273.7 | 256.2 | 438.4 | 47.5 | 20 | 85 | 4 | 241.3 | 3.5 | 132.2 | 147.4 | 595.1 | 745.7 | 247.6 | 267.4 | 539.5 | 729.4 | 724.8 | 339.1 | 533.2 | 604.7 | 390.3 | 399.1 | 531 | 234.8 | 540.1 | 228.3 | 283.9 | 279.9 | 256.1 | 226.5 | 262.1 | 259 | 223.4
892 | 671 | 459.9 | 183.96 | 215.0386 | 269 | 248.5 | 274.5 | 255.9 | 436.9 | 47.5 | 20 | 85.2 | 3.9 | 236.6 | 3.4 | 132.5 | 147.6 | 590.3 | 741.5 | 247.8 | 267.7 | 550.1 | 741.7 | 725.3 | 339.7 | 531.1 | 591.3 | 390.7 | 397.7 | 524.2 | 235 | 539 | 228.5 | 283.9 | 279.8 | 256.1 | 226.7 | 262.3 | 259 | 223.5
893 | 672 | 459.4 | 183.76 | 214.8049 | 267.2 | 248 | 274.3 | 256.9 | 433.4 | 47.5 | 20 | 85.3 | 3.9 | 236.9 | 3.4 | 132.7 | 147.8 | 579.1 | 728.1 | 247.9 | 268 | 550.9 | 728.2 | 723.6 | 340.4 | 534 | 575.3 | 391.2 | 397.4 | 516.7 | 235.1 | 537.5 | 228.6 | 284.1 | 279.9 | 256 | 227.1 | 262.9 | 259.1 | 223.8
894 | 673 | 458.9 | 183.56 | 214.5711 | 266 | 247.6 | 274.6 | 258.1 | 430.7 | 47.5 | 20 | 85.4 | 3.8 | 225.2 | 3.2 | 133 | 148.1 | 564.8 | 714.1 | 248.2 | 268.4 | 547.1 | 711.5 | 721.3 | 341.1 | 539.9 | 558 | 391.8 | 394.4 | 507.5 | 235.3 | 535.5 | 228.7 | 284.3 | 280 | 256.2 | 227.4 | 263.1 | 259.1 | 224
895 | 674 | 456.1 | 182.44 | 213.2618 | 265.9 | 247.7 | 274.2 | 258.9 | 431.8 | 47.5 | 20 | 85.5 | 3.9 | 221.5 | 2.9 | 133.2 | 148.3 | 556.2 | 707.5 | 248.4 | 268.7 | 550.5 | 710.5 | 720.7 | 341.7 | 541.8 | 544.1 | 392.4 | 393.4 | 501.2 | 235.5 | 534 | 228.9 | 284.2 | 280 | 256.3 | 227.6 | 263.4 | 259.2 | 224.2
896 | 675 | 455.3 | 182.12 | 212.8878 | 264.8 | 248.1 | 274.2 | 258.8 | 428.9 | 47.4 | 20 | 85.7 | 4.4 | 222.8 | 2.6 | 133.5 | 148.5 | 547.3 | 703 | 248.6 | 269.1 | 550.3 | 716.7 | 720.3 | 342.3 | 562.5 | 532.1 | 393 | 394 | 499.3 | 235.8 | 532.3 | 229.1 | 283.9 | 279.6 | 256.2 | 227.8 | 263.5 | 259.3 | 224.4
897 | 676 | 455.9 | 182.36 | 213.1683 | 266 | 249.2 | 273.2 | 258.1 | 423 | 47.4 | 20 | 85.7 | 3.9 | 222.5 | 2.4 | 133.7 | 148.7 | 539.3 | 693.6 | 248.8 | 269.5 | 550.7 | 718.4 | 719.6 | 343 | 571.7 | 521.2 | 393.5 | 391.6 | 493.5 | 236 | 530.4 | 229.2 | 283.6 | 279.3 | 256.1 | 228.1 | 263.4 | 259.3 | 224.5
898 | 677 | 455.6 | 182.24 | 213.0281 | 268.5 | 249.5 | 272.3 | 258.2 | 417.1 | 47.5 | 20 | 85.7 | 4.1 | 230 | 2.4 | 134 | 149 | 528.5 | 694 | 249 | 269.8 | 545.5 | 725.9 | 719.2 | 343.6 | 564.9 | 512.4 | 394.2 | 388.4 | 485.8 | 236.2 | 528.8 | 229.4 | 283.5 | 279.2 | 256.1 | 228.3 | 263.3 | 259.5 | 224.7
899 | 678 | 455 | 182 | 212.7475 | 269.9 | 249.2 | 271.5 | 258.4 | 412.9 | 47.6 | 20 | 85.7 | 3.6 | 233.9 | 2.5 | 134.3 | 149.2 | 522.8 | 698.8 | 249.2 | 270.2 | 548.1 | 741.3 | 718.9 | 344.2 | 548.5 | 505.5 | 394.8 | 386.9 | 481.8 | 236.4 | 527.3 | 229.5 | 283.2 | 278.7 | 256.1 | 228.7 | 264 | 259.8 | 225
900 | 679 | 454.6 | 181.84 | 212.5605 | 269.8 | 248.6 | 269.6 | 258.5 | 408.8 | 47.7 | 20 | 85.7 | 4 | 225.9 | 2.3 | 134.5 | 149.4 | 517.5 | 691.9 | 249.4 | 270.6 | 551.3 | 739 | 718.6 | 344.9 | 533.8 | 495.2 | 395.2 | 387.7 | 483.5 | 236.6 | 526 | 229.6 | 282.9 | 278.1 | 256 | 229.1 | 264.6 | 260.3 | 225.2
901 | 680 | 455.4 | 182.16 | 212.9345 | 271.4 | 248.7 | 267.5 | 259.5 | 404.2 | 47.8 | 20 | 85.8 | 4.2 | 213.6 | 2.5 | 134.8 | 149.6 | 508.5 | 683.8 | 249.6 | 270.9 | 547.2 | 719.6 | 717.6 | 345.6 | 519.8 | 486.8 | 395.7 | 385.3 | 477.7 | 236.9 | 524.3 | 229.8 | 282.5 | 277.7 | 256 | 229.5 | 264.9 | 260.6 | 225.3
902 | 681 | 455.4 | 182.16 | 212.9345 | 273.1 | 248.2 | 266.9 | 259.6 | 398.1 | 47.8 | 20 | 85.9 | 3.8 | 206.6 | 2.8 | 135.1 | 149.9 | 499 | 676.9 | 249.8 | 271.3 | 534.1 | 703.3 | 716.9 | 346.2 | 505.8 | 478.2 | 396.2 | 381.1 | 470 | 237.1 | 522.6 | 229.9 | 282.2 | 277.2 | 255.9 | 229.8 | 265.4 | 260.7 | 225.5
903 | 682 | 455.6 | 182.24 | 213.0281 | 275.2 | 247.9 | 266.2 | 259.3 | 393.3 | 47.9 | 20 | 86 | 3.4 | 205.7 | 3.1 | 135.3 | 150.1 | 493.5 | 680.4 | 250.1 | 271.7 | 534.7 | 705.6 | 716.6 | 346.8 | 493.6 | 473.8 | 396.7 | 377.4 | 469.4 | 237.3 | 521.1 | 230 | 281.8 | 276.8 | 255.8 | 230.1 | 265.3 | 260.7 | 225.6
904 | 683 | 454.8 | 181.92 | 212.654 | 277.5 | 246.4 | 265.5 | 259.1 | 389.9 | 47.9 | 20 | 86 | 3.6 | 209.1 | 3.3 | 135.6 | 150.3 | 497.8 | 692.9 | 250.3 | 272.1 | 533.2 | 719.2 | 717.7 | 347.4 | 485.2 | 482.6 | 397.2 | 377 | 474 | 237.5 | 520.4 | 230.1 | 281.4 | 276.5 | 255.8 | 230.3 | 265 | 260.8 | 225.7
905 | 684 | 455.6 | 182.24 | 213.0281 | 277.6 | 244.9 | 265.4 | 259.5 | 392.2 | 47.9 | 20 | 86 | 3.6 | 213.2 | 3.8 | 135.8 | 150.6 | 508.4 | 700.8 | 250.5 | 272.4 | 551 | 743.7 | 719.2 | 348 | 477.3 | 493.6 | 397.6 | 377.5 | 479.7 | 237.7 | 520.8 | 230.2 | 281 | 276.1 | 255.9 | 230.5 | 264.7 | 260.8 | 225.9
906 | 685 | 455.2 | 182.08 | 212.841 | 276.6 | 243.7 | 265.7 | 259.5 | 390.6 | 47.8 | 20 | 86 | 4.2 | 216.1 | 4 | 136.1 | 150.8 | 511.6 | 696.5 | 250.7 | 272.8 | 551 | 732.1 | 717.7 | 348.6 | 471.4 | 492.6 | 397.9 | 378.1 | 478.5 | 237.9 | 520.5 | 230.3 | 280.7 | 275.8 | 256.1 | 230.8 | 264.5 | 260.9 | 226
907 | 686 | 455.2 | 182.08 | 212.841 | 274.7 | 242.7 | 265.6 | 259.1 | 390.1 | 47.9 | 20 | 86 | 4 | 212.5 | 4.3 | 136.4 | 151.1 | 503.6 | 687.1 | 250.9 | 273.2 | 539.3 | 695.2 | 714.3 | 349.1 | 464.2 | 484.7 | 398.3 | 376 | 473 | 238.2 | 519.1 | 230.4 | 280.6 | 275.6 | 256.3 | 230.9 | 264.2 | 260.9 | 225.9
908 | 687 | 455.5 | 182.2 | 212.9813 | 275 | 242 | 264.6 | 258.7 | 387.9 | 47.9 | 20 | 85.9 | 4 | 215.5 | 4.8 | 136.6 | 151.3 | 490 | 681.6 | 251.2 | 273.6 | 527.1 | 679.2 | 712.6 | 349.7 | 456.5 | 475.8 | 398.7 | 371.8 | 466.6 | 238.4 | 517.2 | 230.5 | 280.3 | 275.5 | 256.6 | 231.1 | 263.7 | 260.8 | 226.1
909 | 688 | 455.2 | 182.08 | 212.841 | 276.2 | 241.2 | 264.5 | 258.8 | 386 | 47.9 | 20 | 85.8 | 3.9 | 221.2 | 4.9 | 136.9 | 151.5 | 482.7 | 680.3 | 251.4 | 274 | 514.2 | 655.4 | 709.4 | 350.3 | 450.9 | 479 | 399.1 | 368.7 | 468.2 | 238.6 | 516.3 | 230.7 | 280.1 | 275.7 | 256.9 | 231.3 | 263.2 | 260.7 | 226.2
910 | 689 | 455.4 | 182.16 | 212.9345 | 277.5 | 240.7 | 266.6 | 258.7 | 389.4 | 47.9 | 20 | 85.7 | 4.4 | 232 | 4.7 | 137.1 | 151.8 | 476.6 | 674.2 | 251.6 | 274.4 | 512.7 | 632.5 | 704.4 | 350.9 | 443.4 | 472.4 | 399.6 | 365.8 | 461.1 | 238.9 | 515 | 230.8 | 280.2 | 276 | 257.2 | 231.4 | 262.8 | 260.7 | 226.3
911 | 690 | 454.7 | 181.88 | 212.6072 | 278.4 | 239.9 | 267.2 | 257.6 | 390.4 | 48.1 | 20 | 85.7 | 4.4 | 231.7 | 4.5 | 137.4 | 152 | 472.7 | 682.8 | 251.9 | 274.8 | 508.3 | 631.2 | 703.6 | 351.4 | 436.8 | 470.1 | 400.1 | 362.6 | 457.9 | 239.1 | 513.6 | 231 | 280.6 | 276.4 | 257.5 | 231.5 | 262.4 | 260.8 | 226.4
912 | 691 | 453.5 | 181.4 | 212.0461 | 277.3 | 239.9 | 267.4 | 257.6 | 392.5 | 48.2 | 20 | 85.8 | 4.3 | 231.1 | 4.2 | 137.7 | 152.3 | 474.3 | 679.2 | 252.1 | 275.1 | 498.5 | 619.3 | 700.8 | 352 | 432.8 | 469.4 | 400.6 | 359.8 | 456.6 | 239.3 | 512.9 | 231.1 | 280.9 | 276.8 | 257.8 | 231.6 | 262 | 260.9 | 226.5
913 | 692 | 455.5 | 182.2 | 212.9813 | 275.7 | 240.4 | 269.1 | 257.4 | 392.1 | 48.3 | 20 | 85.9 | 4.5 | 231.1 | 3.9 | 137.9 | 152.5 | 474.2 | 673.9 | 252.4 | 275.5 | 491.5 | 604.7 | 698.1 | 352.5 | 429.8 | 467 | 401.1 | 357.4 | 457.2 | 239.6 | 512.5 | 231.3 | 281.1 | 277 | 258.2 | 231.7 | 261.6 | 260.8 | 226.5
914 | 693 | 456.4 | 182.56 | 213.4021 | 274.1 | 240.7 | 271 | 256.8 | 391.7 | 48.4 | 19.9 | 85.9 | 4.4 | 232.1 | 3.5 | 138.2 | 152.8 | 470.8 | 667 | 252.6 | 275.9 | 483.8 | 598.4 | 696.1 | 353.1 | 424.6 | 463.3 | 401.6 | 355 | 450.3 | 239.8 | 511.4 | 231.5 | 281.4 | 277.3 | 258.5 | 231.8 | 261.2 | 260.7 | 226.6
915 | 694 | 454.7 | 181.88 | 212.6072 | 272.8 | 240.5 | 273.1 | 256.3 | 390.4 | 48.5 | 19.9 | 86 | 4.1 | 232.5 | 3 | 138.5 | 153 | 465.6 | 658.9 | 252.8 | 276.2 | 478.8 | 596.9 | 694.3 | 353.6 | 420 | 461.6 | 402.1 | 352.6 | 447.6 | 240.1 | 510.6 | 231.8 | 281.6 | 277.7 | 258.7 | 231.9 | 260.8 | 260.7 | 226.7
916 | 695 | 454.7 | 181.88 | 212.6072 | 271.8 | 239.5 | 274.5 | 256.8 | 393.8 | 48.5 | 19.9 | 86.1 | 4.4 | 232.4 | 2.5 | 138.7 | 153.2 | 460.5 | 655.1 | 253 | 276.5 | 480 | 596.6 | 691.9 | 354.1 | 415.5 | 461.2 | 402.7 | 350.5 | 445.9 | 240.3 | 509.9 | 232 | 281.6 | 278 | 259.1 | 232 | 260.3 | 260.7 | 226.8
917 | 696 | 455.1 | 182.04 | 212.7943 | 270.4 | 240.3 | 274.9 | 257.6 | 393.8 | 48.5 | 19.9 | 86.1 | 3.7 | 233.7 | 2.2 | 139 | 153.5 | 457.4 | 652.4 | 253.3 | 276.9 | 480.8 | 583.8 | 689 | 354.6 | 413.1 | 467.8 | 403.2 | 349.1 | 442.5 | 240.5 | 509 | 232.3 | 282.6 | 278.5 | 259.7 | 232.1 | 260 | 260.7 | 226.9
918 | 697 | 455.3 | 182.12 | 212.8878 | 269.2 | 241.7 | 276.1 | 257.3 | 394.4 | 48.5 | 19.9 | 86.1 | 3.8 | 231.9 | 2 | 139.3 | 153.7 | 457.4 | 656.1 | 253.5 | 277.3 | 475.4 | 586.5 | 686.8 | 355.1 | 411.8 | 475.2 | 403.8 | 348.5 | 440.5 | 240.8 | 508.9 | 232.6 | 282.9 | 278.8 | 260 | 232.2 | 259.8 | 260.6 | 227
919 | 698 | 455.4 | 182.16 | 212.9345 | 268.3 | 242.4 | 277.3 | 257.3 | 394.9 | 48.6 | 19.9 | 86.2 | 3.5 | 226.3 | 1.7 | 139.5 | 154 | 461.1 | 661.2 | 253.8 | 277.6 | 478.6 | 599.2 | 685.5 | 355.6 | 411.6 | 482.4 | 404.3 | 348.4 | 440.8 | 241 | 508.3 | 232.9 | 283.1 | 278.9 | 259.9 | 232.2 | 259.5 | 260.5 | 227.1
920 | 699 | 455.5 | 182.2 | 212.9813 | 267.4 | 242.6 | 277.1 | 257.1 | 396.2 | 48.6 | 19.9 | 86.2 | 3.3 | 223.6 | 1.5 | 139.8 | 154.2 | 458.7 | 665.3 | 254 | 278 | 486.4 | 621.3 | 686 | 356.1 | 410.1 | 474.3 | 404.8 | 348.8 | 439.7 | 241.2 | 507.2 | 233.2 | 283.1 | 278.9 | 259.6 | 232.3 | 259.2 | 260.7 | 227.2
921 | 700 | 455 | 182 | 212.7475 | 266.9 | 243.4 | 276.1 | 256.5 | 394.3 | 48.6 | 19.9 | 86.4 | 4 | 223 | 1.4 | 140.1 | 154.5 | 463 | 671.4 | 254.2 | 278.4 | 485.8 | 627.7 | 686.1 | 356.5 | 406.8 | 477.6 | 405.3 | 349 | 440.7 | 241.4 | 506.4 | 233.5 | 282.7 | 278.7 | 259.4 | 232.5 | 259.2 | 261.2 | 227.4
922 | 701 | 454.8 | 181.92 | 212.654 | 266.5 | 243.9 | 275.2 | 255.9 | 395.3 | 48.5 | 19.9 | 86.5 | 4 | 223 | 1.3 | 140.4 | 154.7 | 461.4 | 668.3 | 254.5 | 278.7 | 477.2 | 616.5 | 685.1 | 357 | 407.4 | 480.6 | 405.8 | 349 | 440.8 | 241.6 | 506 | 233.7 | 282.6 | 278.7 | 259.6 | 232.6 | 259.4 | 261.1 | 227.5
923 | 702 | 454.9 | 181.96 | 212.7008 | 266.5 | 244.1 | 273.7 | 255.8 | 400.7 | 48.5 | 19.9 | 86.7 | 3.9 | 222.9 | 1.4 | 140.6 | 154.9 | 459.6 | 663.2 | 254.7 | 279 | 468.4 | 605.1 | 683.2 | 357.4 | 408.5 | 482.7 | 406.3 | 347.8 | 440.6 | 241.9 | 505.3 | 234 | 282.6 | 278.7 | 259.8 | 232.7 | 259.4 | 260.9 | 227.6
924 | 703 | 454.9 | 181.96 | 212.7008 | 266.3 | 244 | 273.1 | 255.6 | 401.1 | 48.5 | 19.9 | 86.8 | 3.7 | 222 | 1.3 | 140.9 | 155.2 | 455.9 | 656.6 | 255 | 279.3 | 465.4 | 578.8 | 679 | 357.8 | 411.1 | 481.1 | 406.7 | 345.9 | 437.4 | 242.1 | 504.6 | 234.3 | 282.7 | 278.7 | 260.1 | 232.8 | 259.4 | 260.7 | 227.7
925 | 704 | 455 | 182 | 212.7475 | 268.7 | 244.1 | 272.7 | 255.7 | 398.5 | 48.4 | 19.9 | 86.9 | 3.9 | 218.9 | 1.2 | 141.2 | 155.4 | 451.8 | 656.4 | 255.2 | 279.6 | 462.7 | 569 | 676.1 | 358.3 | 408.4 | 478.4 | 407.3 | 344.7 | 438.5 | 242.4 | 504.1 | 234.5 | 283.3 | 278.8 | 260.4 | 232.9 | 259.1 | 260.5 | 227.7
926 | 705 | 454.5 | 181.8 | 212.5137 | 270.3 | 244 | 274.3 | 254.8 | 397.8 | 48.5 | 19.9 | 87 | 3.6 | 211 | 0.9 | 141.4 | 155.7 | 453.1 | 659.2 | 255.5 | 280 | 465.1 | 573.6 | 674.1 | 358.7 | 405.8 | 484.4 | 408 | 344 | 437.3 | 242.6 | 503.2 | 234.9 | 283.8 | 278.9 | 260.6 | 233 | 258.8 | 260.3 | 227.7
927 | 706 | 454.9 | 181.96 | 212.7008 | 270.7 | 245 | 276.7 | 255.1 | 399.1 | 48.6 | 19.9 | 87 | 3.7 | 201.2 | 0.9 | 141.7 | 155.9 | 459.1 | 668.3 | 255.8 | 280.3 | 465 | 596.6 | 673.8 | 359 | 404.2 | 489.7 | 408.5 | 344 | 437 | 242.9 | 502 | 235.2 | 283.9 | 278.9 | 260.6 | 233 | 258.5 | 260 | 227.8
928 | 707 | 454.9 | 181.96 | 212.7008 | 271 | 245.6 | 277.4 | 255.1 | 400.3 | 48.7 | 19.9 | 87.1 | 4.1 | 191.4 | 1.2 | 142 | 156.2 | 471 | 682.4 | 256 | 280.7 | 474.7 | 622.6 | 674.7 | 359.4 | 403.5 | 502.9 | 409 | 346.3 | 442.7 | 243.1 | 502.7 | 235.5 | 283.9 | 278.9 | 260.5 | 233.1 | 258.2 | 259.8 | 227.9
929 | 708 | 454.5 | 181.8 | 212.5137 | 270.3 | 247.1 | 277.7 | 255 | 399.5 | 48.7 | 19.9 | 87.2 | 4.1 | 182.7 | 1.4 | 142.3 | 156.5 | 481.2 | 693.5 | 256.3 | 281.1 | 488.3 | 660.1 | 677.2 | 359.8 | 401.4 | 501.6 | 409.6 | 350.1 | 449.5 | 243.4 | 502.5 | 235.8 | 283.9 | 278.9 | 260.4 | 233.3 | 258.2 | 259.7 | 228
930 | 709 | 454.3 | 181.72 | 212.4202 | 269.4 | 248.1 | 278.4 | 254.8 | 395.9 | 48.8 | 19.9 | 87.2 | 4.2 | 180.3 | 1.5 | 142.5 | 156.7 | 483.7 | 701.7 | 256.5 | 281.4 | 497.4 | 684 | 678.7 | 360.2 | 399.6 | 502.1 | 410.2 | 352.1 | 456 | 243.6 | 502.8 | 236.1 | 284.1 | 279.2 | 260.3 | 233.4 | 258.8 | 259.7 | 228.2
931 | 710 | 454.5 | 181.8 | 212.5137 | 268.3 | 248.7 | 277.9 | 254.4 | 394.9 | 48.8 | 19.9 | 87.2 | 4.2 | 179.4 | 1.6 | 142.8 | 157 | 481.4 | 704.3 | 256.8 | 281.8 | 501.3 | 691 | 679.6 | 360.5 | 398.1 | 502.6 | 410.7 | 352.4 | 457.8 | 243.9 | 502.6 | 236.4 | 284 | 279.2 | 260.5 | 233.6 | 259.6 | 259.8 | 228.3
932 | 711 | 453.9 | 181.56 | 212.2332 | 267.2 | 248.8 | 276.8 | 254.1 | 393.7 | 48.9 | 19.9 | 87.2 | 4.3 | 180.6 | 1.8 | 143.1 | 157.2 | 482 | 699.8 | 257.1 | 282.1 | 502.7 | 700.1 | 679.4 | 360.8 | 396.6 | 496.8 | 411.2 | 351.7 | 457.1 | 244.1 | 502 | 236.7 | 283.9 | 279.1 | 260.6 | 233.7 | 259.9 | 259.8 | 228.5
933 | 712 | 453.8 | 181.52 | 212.1864 | 265.7 | 248.4 | 275.7 | 253.8 | 391.7 | 48.9 | 19.9 | 87.2 | 4.5 | 178.9 | 1.9 | 143.4 | 157.5 | 480 | 696 | 257.3 | 282.4 | 505.2 | 707.9 | 680.8 | 361.1 | 393.3 | 490.4 | 411.8 | 351.8 | 456.3 | 244.4 | 501.5 | 237 | 283.6 | 278.7 | 260.6 | 233.9 | 259.8 | 259.7 | 228.5
934 | 713 | 453.8 | 181.52 | 212.1864 | 264.9 | 247.6 | 274.8 | 252.6 | 388.9 | 48.9 | 19.9 | 87.1 | 4.4 | 171.4 | 1.9 | 143.6 | 157.8 | 479.9 | 694.7 | 257.6 | 282.7 | 507.9 | 724.5 | 680.8 | 361.3 | 390.9 | 485.9 | 412.3 | 352.6 | 457.3 | 244.6 | 500.7 | 237.2 | 283.1 | 278.2 | 260.4 | 234 | 260 | 259.5 | 228.7
935 | 714 | 454.2 | 181.68 | 212.3735 | 263.1 | 246.5 | 273.3 | 252 | 384.7 | 48.9 | 19.9 | 87.1 | 4.6 | 159.3 | 1.9 | 143.9 | 158 | 480 | 694.1 | 257.8 | 283.1 | 516.8 | 723.9 | 682.2 | 361.6 | 389.9 | 482.8 | 412.8 | 353.6 | 460.2 | 244.9 | 500.1 | 237.4 | 282.7 | 277.6 | 260.3 | 234.2 | 260.3 | 259.4 | 229
936 | 715 | 454.1 | 181.64 | 212.3267 | 260.7 | 245.2 | 271.5 | 252.2 | 383.6 | 48.9 | 19.9 | 87 | 4.1 | 149.1 | 2 | 144.2 | 158.3 | 485 | 697 | 258.1 | 283.5 | 516.6 | 724.7 | 683.3 | 361.8 | 388.4 | 487.2 | 413.3 | 351.8 | 456.8 | 245.1 | 499.8 | 237.7 | 282.3 | 277 | 260.4 | 234.4 | 260.6 | 259.2 | 229
937 | 716 | 453.5 | 181.4 | 212.0461 | 259.3 | 244.4 | 270.7 | 251.9 | 385.9 | 48.8 | 19.9 | 86.9 | 4.1 | 151.9 | 2.1 | 144.5 | 158.5 | 487.5 | 692.9 | 258.3 | 283.9 | 508.3 | 699 | 680.4 | 362.1 | 386.9 | 492.5 | 413.9 | 351.3 | 457 | 245.4 | 499.6 | 237.9 | 282 | 276.8 | 260.7 | 234.5 | 260.4 | 259 | 229
938 | 717 | 454.4 | 181.76 | 212.467 | 258.7 | 244.5 | 270.8 | 251.6 | 389.7 | 48.8 | 19.9 | 86.9 | 4 | 159.8 | 2.1 | 144.8 | 158.8 | 483.1 | 687.8 | 258.6 | 284.2 | 497.4 | 669.7 | 677.2 | 362.3 | 386.2 | 490.8 | 414.5 | 350.2 | 453 | 245.6 | 499.4 | 238.2 | 282.1 | 277 | 261.2 | 234.6 | 260.4 | 258.8 | 229.1
939 | 718 | 453.5 | 181.4 | 212.0461 | 259.2 | 245.4 | 271.7 | 252.6 | 391.3 | 48.8 | 19.9 | 86.8 | 4 | 162.4 | 2.1 | 145 | 159 | 478.3 | 687.6 | 258.9 | 284.6 | 487.8 | 657.3 | 676.6 | 362.5 | 384.2 | 489.7 | 415.1 | 347.4 | 448.9 | 245.8 | 498.6 | 238.5 | 282.6 | 277.1 | 261.4 | 234.8 | 260.2 | 258.6 | 229.2
940 | 719 | 453.2 | 181.28 | 211.9059 | 259.3 | 245.6 | 272.9 | 253.6 | 391.3 | 48.9 | 19.9 | 86.8 | 4.3 | 162.2 | 2.2 | 145.3 | 159.3 | 480.6 | 698.2 | 259.1 | 285 | 485.5 | 679 | 677.4 | 362.8 | 381.1 | 487.6 | 415.7 | 345.8 | 449.8 | 246.1 | 498 | 238.8 | 282.3 | 276.9 | 261.2 | 234.9 | 260.1 | 258.5 | 229.2
941 | 720 | 455.9 | 182.36 | 213.1683 | 259.8 | 246.1 | 272.7 | 253.8 | 390.5 | 48.9 | 19.9 | 86.9 | 4.1 | 162.3 | 2.2 | 145.6 | 159.6 | 484.5 | 709.5 | 259.5 | 285.3 | 487.1 | 688.8 | 679.2 | 363.1 | 381.5 | 493.3 | 416.3 | 346.9 | 456.4 | 246.3 | 498 | 239 | 282.2 | 276.7 | 261 | 235 | 260.1 | 258.5 | 229.3
942 | 721 | 464.3 | 185.72 | 217.096 | 259.8 | 246 | 272.7 | 254.4 | 391.9 | 48.9 | 19.9 | 87.1 | 4.5 | 162.3 | 2.2 | 145.9 | 159.8 | 498.5 | 720.3 | 259.9 | 285.7 | 494.1 | 714.7 | 682.3 | 363.3 | 383.8 | 505.3 | 417 | 349.4 | 466.3 | 246.5 | 499 | 239.3 | 282.4 | 276.7 | 261 | 235.1 | 260.2 | 258.6 | 229.5
943 | 722 | 460.2 | 184.08 | 215.1789 | 258.8 | 246.1 | 272.4 | 254.3 | 393.4 | 49 | 19.9 | 87.2 | 4.4 | 162.5 | 2.2 | 146.1 | 160.1 | 514.4 | 723.8 | 260.1 | 285.9 | 514.8 | 731.3 | 684.1 | 363.7 | 387.4 | 524.9 | 417.5 | 352.7 | 481 | 246.8 | 502.5 | 239.6 | 282.4 | 276.5 | 261.1 | 235.2 | 260.3 | 258.4 | 229.6
944 | 723 | 457.9 | 183.16 | 214.1035 | 257.9 | 246.7 | 271.8 | 253.8 | 394.4 | 49 | 19.9 | 87.3 | 4.3 | 162.6 | 2.1 | 146.4 | 160.4 | 526.6 | 724.8 | 260.4 | 286.3 | 512.7 | 731.2 | 684.2 | 364 | 389.6 | 537.5 | 418 | 354.6 | 483.9 | 247 | 502.9 | 239.9 | 282.5 | 276.5 | 261.3 | 235.4 | 260.4 | 258.2 | 229.7
945 | 724 | 458.2 | 183.28 | 214.2438 | 258.8 | 247.1 | 270.9 | 253.1 | 392.6 | 49.1 | 19.9 | 87.5 | 4.1 | 164.7 | 2 | 146.7 | 160.6 | 531.9 | 724.9 | 260.7 | 286.7 | 516.4 | 727.9 | 684.9 | 364.3 | 389.7 | 534.8 | 418.5 | 357.4 | 489.1 | 247.2 | 503.7 | 240.2 | 282.6 | 277 | 261.4 | 235.5 | 260.3 | 257.9 | 229.8
946 | 725 | 462 | 184.8 | 216.0206 | 259 | 247.7 | 270.3 | 251.8 | 390.2 | 49.1 | 19.9 | 87.6 | 3.7 | 171.2 | 2 | 147 | 160.9 | 522.6 | 716.9 | 260.8 | 287 | 513.3 | 717.3 | 683.7 | 364.6 | 388 | 522.5 | 419.1 | 356.8 | 484.3 | 247.4 | 503.4 | 240.5 | 283 | 277.2 | 261.5 | 235.7 | 260.1 | 257.8 | 229.8
947 | 726 | 463.3 | 185.32 | 216.6284 | 258.9 | 248.1 | 270.1 | 252 | 387 | 49.2 | 19.9 | 87.6 | 3.9 | 184.2 | 2 | 147.3 | 161.1 | 511.3 | 709.1 | 260.9 | 287.4 | 506 | 694.1 | 681.2 | 364.9 | 386 | 510 | 419.7 | 355.7 | 477.7 | 247.7 | 502.2 | 240.8 | 283.1 | 276.9 | 261.5 | 235.8 | 260.3 | 257.6 | 229.9
948 | 727 | 463.3 | 185.32 | 216.6284 | 260.5 | 248.2 | 269.3 | 252.2 | 384.1 | 49.2 | 19.9 | 87.5 | 4 | 195.6 | 2.1 | 147.5 | 161.4 | 502.9 | 709.2 | 261.5 | 287.7 | 502.8 | 703.6 | 681.9 | 365.2 | 381.7 | 500.6 | 420.4 | 356.1 | 477.9 | 247.9 | 501.2 | 241 | 282.8 | 276.4 | 261.2 | 236 | 260.5 | 257.4 | 230.1
949 | 728 | 464.1 | 185.64 | 217.0025 | 261.3 | 247.7 | 268.4 | 252 | 381.6 | 49.3 | 19.9 | 87.6 | 4.5 | 201.8 | 1.9 | 147.8 | 161.7 | 496 | 707.9 | 262 | 288 | 507.5 | 715.1 | 681.7 | 365.5 | 378.3 | 492.4 | 421.1 | 357.4 | 477.5 | 248.2 | 500.7 | 241.2 | 282.6 | 276 | 261 | 236.3 | 260.9 | 257.5 | 230.2
950 | 729 | 467.7 | 187.08 | 218.6857 | 261.7 | 247.8 | 267 | 252.7 | 382 | 49.3 | 19.9 | 87.6 | 4.4 | 203.4 | 1.8 | 148.1 | 161.9 | 489.4 | 704 | 262.2 | 288.3 | 504.5 | 708.8 | 679 | 365.8 | 375.6 | 483.6 | 421.7 | 358.2 | 475.4 | 248.4 | 499.9 | 241.4 | 282.2 | 275.6 | 260.9 | 236.6 | 260.7 | 257.6 | 230.3
951 | 730 | 467.9 | 187.16 | 218.7793 | 264.3 | 247.1 | 265.9 | 252.8 | 381.8 | 49.3 | 19.9 | 87.6 | 4.5 | 203 | 1.8 | 148.4 | 162.2 | 488.6 | 706.7 | 262.4 | 288.7 | 505.7 | 709.7 | 678.6 | 366 | 374.1 | 486.2 | 422.3 | 356.7 | 474.9 | 248.6 | 499.3 | 241.5 | 281.8 | 275.2 | 261.1 | 236.7 | 260.5 | 257.8 | 230.3
952 | 731 | 468.4 | 187.36 | 219.013 | 265.6 | 246.4 | 264.9 | 253.1 | 382.7 | 49.4 | 19.9 | 87.7 | 3.9 | 203.1 | 1.8 | 148.6 | 162.4 | 505.8 | 718.2 | 262.6 | 289 | 510.8 | 732.2 | 681.3 | 366.3 | 373.6 | 497.9 | 423 | 357.3 | 480.5 | 248.9 | 499.6 | 241.7 | 281.6 | 274.9 | 261.2 | 236.8 | 260.6 | 257.9 | 230.4
953 | 732 | 469.6 | 187.84 | 219.5741 | 266.3 | 246.9 | 264.4 | 253 | 382.9 | 49.4 | 19.9 | 87.8 | 3.8 | 202.9 | 1.7 | 148.9 | 162.7 | 524.9 | 724.5 | 262.9 | 289.4 | 534.8 | 765.5 | 686 | 366.6 | 373.7 | 515 | 423.6 | 364.2 | 496.5 | 249.1 | 501.4 | 241.9 | 281.4 | 274.8 | 261.1 | 237 | 260.6 | 258.1 | 230.7
954 | 733 | 469.8 | 187.92 | 219.6677 | 267.3 | 246.3 | 265.2 | 252.7 | 383.1 | 49.4 | 19.9 | 87.9 | 3.6 | 203 | 1.5 | 149.2 | 163 | 543.6 | 724.6 | 263.1 | 289.7 | 559.3 | 766.2 | 688 | 366.9 | 375.8 | 527.6 | 424 | 369.8 | 511.3 | 249.4 | 503.5 | 242.2 | 281.3 | 274.8 | 261.1 | 237.3 | 260.8 | 258.2 | 230.8
955 | 734 | 470.6 | 188.24 | 220.0417 | 266.9 | 246.3 | 265 | 253.5 | 383.9 | 49.4 | 19.9 | 88 | 3.5 | 203.1 | 1.3 | 149.5 | 163.3 | 545 | 718.2 | 263.2 | 290.1 | 578.4 | 786.3 | 689 | 367.1 | 376.9 | 522.6 | 424.3 | 382.2 | 526.3 | 249.6 | 505.1 | 242.4 | 281.1 | 274.7 | 260.8 | 237.6 | 261.4 | 258.4 | 231
956 | 735 | 470.8 | 188.32 | 220.1352 | 265.9 | 246.4 | 264.2 | 255.5 | 392.4 | 49.4 | 19.9 | 88.1 | 3.4 | 204.7 | 1 | 149.8 | 163.5 | 539.3 | 708.3 | 263.4 | 290.4 | 587.4 | 800.5 | 690.1 | 367.4 | 378.5 | 506.3 | 424.8 | 393.5 | 526.1 | 249.9 | 505.1 | 242.6 | 280.9 | 274.4 | 260.6 | 238 | 262.1 | 258.9 | 231.2
957 | 736 | 471.2 | 188.48 | 220.3223 | 265.1 | 245.2 | 264 | 258.1 | 396.7 | 49.5 | 19.9 | 88.2 | 3.6 | 219.8 | 0.8 | 150 | 163.8 | 538.1 | 714 | 263.8 | 290.8 | 592.2 | 801.9 | 693 | 367.7 | 378.2 | 506.3 | 425.1 | 394.7 | 522.7 | 250.1 | 505.1 | 242.7 | 280.6 | 274 | 260.5 | 238.3 | 262.7 | 259.4 | 231.3
958 | 737 | 471.1 | 188.44 | 220.2755 | 264.1 | 244.5 | 263.9 | 260.4 | 393.6 | 49.6 | 19.9 | 88.3 | 3.7 | 241.9 | 1 | 150.3 | 164.1 | 544.6 | 723.4 | 264 | 291.2 | 585.3 | 799 | 695 | 368 | 378.2 | 519.8 | 425.5 | 392.2 | 523.5 | 250.3 | 505.6 | 242.9 | 280.3 | 273.9 | 260.7 | 238.5 | 262.7 | 259.8 | 231.4
959 | 738 | 471.3 | 188.52 | 220.369 | 264 | 243.7 | 263 | 261 | 394.5 | 49.8 | 19.9 | 88.4 | 3.7 | 254.8 | 1.5 | 150.6 | 164.3 | 541.6 | 734.1 | 264 | 291.5 | 571.9 | 803.2 | 697.3 | 368.3 | 380.5 | 531.4 | 426 | 388 | 519.7 | 250.6 | 506.3 | 243.1 | 280 | 273.9 | 261 | 238.7 | 262.8 | 260.1 | 231.5
960 | 739 | 470.7 | 188.28 | 220.0885 | 265 | 243.1 | 262.9 | 260.6 | 399 | 50 | 19.9 | 88.4 | 4.1 | 255 | 1.8 | 150.9 | 164.6 | 546 | 743.2 | 264.2 | 291.7 | 561.3 | 802.1 | 698.7 | 368.5 | 384.2 | 541.6 | 426.6 | 385.8 | 517 | 250.8 | 506.7 | 243.4 | 279.8 | 274 | 261.3 | 238.9 | 262.8 | 260.5 | 231.6
961 | 740 | 471.1 | 188.44 | 220.2755 | 266 | 242.2 | 263.3 | 259 | 406.9 | 50.2 | 19.9 | 88.5 | 4 | 246.7 | 1.9 | 151.1 | 164.9 | 549.6 | 742.1 | 264.5 | 292 | 552.1 | 781.5 | 698.2 | 368.8 | 389.9 | 565.2 | 427.1 | 385.8 | 522.9 | 251.1 | 508.8 | 243.7 | 279.9 | 274.3 | 261.7 | 239.1 | 262.6 | 260.9 | 231.6
962 | 741 | 470.9 | 188.36 | 220.182 | 266.2 | 242.4 | 264.4 | 257.7 | 420.9 | 50.4 | 19.8 | 88.5 | 4.2 | 234.9 | 2.1 | 151.4 | 165.1 | 554.1 | 747.3 | 264.9 | 292.3 | 547.1 | 774 | 699.6 | 369.2 | 395.2 | 584.1 | 427.8 | 386.3 | 528.7 | 251.3 | 509.5 | 244 | 280.2 | 274.7 | 262.1 | 239.2 | 262.4 | 261.1 | 231.7
963 | 742 | 471.2 | 188.48 | 220.3223 | 266 | 243.3 | 266 | 257.4 | 426 | 50.5 | 19.9 | 88.7 | 4.2 | 230.4 | 2.3 | 151.7 | 165.4 | 567 | 753.2 | 265.2 | 292.7 | 548 | 753.8 | 699.7 | 369.5 | 398.2 | 603.2 | 428.4 | 385.2 | 525.1 | 251.5 | 510.7 | 244.4 | 280.4 | 275.3 | 262.3 | 239.4 | 262.3 | 261.2 | 231.8
964 | 743 | 472.7 | 189.08 | 221.0236 | 266.5 | 244.2 | 268.1 | 257.4 | 436.4 | 50.5 | 19.8 | 88.8 | 4.4 | 236 | 2.3 | 152 | 165.7 | 574.8 | 754.9 | 265.7 | 293 | 550.9 | 722.5 | 697.8 | 369.8 | 401 | 611.9 | 429 | 384.3 | 524 | 251.8 | 512.2 | 244.9 | 280.8 | 276.1 | 262.8 | 239.5 | 262.2 | 261.5 | 231.9
965 | 744 | 471.2 | 188.48 | 220.3223 | 267.8 | 245.8 | 269.1 | 256.9 | 440.4 | 50.4 | 19.8 | 88.9 | 4.2 | 244 | 2.5 | 152.3 | 165.9 | 589.9 | 749.2 | 265.7 | 293.5 | 560 | 705.5 | 696.6 | 370.2 | 402.7 | 616.1 | 429.6 | 385.7 | 530.7 | 252 | 513.8 | 245.3 | 281.5 | 276.9 | 263.3 | 239.6 | 262.2 | 261.9 | 231.9
966 | 745 | 471.8 | 188.72 | 220.6028 | 267.5 | 246.9 | 270.2 | 256.6 | 438.8 | 50.3 | 19.8 | 88.8 | 4.2 | 254.9 | 3.6 | 152.5 | 166.2 | 589.1 | 742.8 | 265.8 | 293.7 | 554.1 | 707.3 | 695.7 | 370.6 | 402.1 | 605 | 430.2 | 385.8 | 528.7 | 252.3 | 514.3 | 245.7 | 282.3 | 277.4 | 263.2 | 239.8 | 262.4 | 262 | 232.1
967 | 746 | 471 | 188.4 | 220.2287 | 268.8 | 247.4 | 271.1 | 256.4 | 431.7 | 50.2 | 19.8 | 88.8 | 3.9 | 258.3 | 4.4 | 152.8 | 166.5 | 582.8 | 736.6 | 265.7 | 294 | 559.7 | 734 | 697.4 | 371 | 401 | 591.9 | 430.8 | 388.7 | 528.9 | 252.6 | 514.2 | 246.1 | 283 | 278 | 263 | 240.1 | 262.9 | 262 | 232.2
968 | 747 | 471.2 | 188.48 | 220.3223 | 268.2 | 247.5 | 271.2 | 256.5 | 425.5 | 50.1 | 19.8 | 88.8 | 3.6 | 267.7 | 4.7 | 153.1 | 166.7 | 579.9 | 734.7 | 266.1 | 294.3 | 564.3 | 746.2 | 698.4 | 371.4 | 399.3 | 591 | 431.4 | 389.4 | 529 | 252.8 | 514.7 | 246.4 | 283.4 | 278.2 | 263.1 | 240.4 | 263.3 | 262.2 | 232.4
969 | 748 | 471.3 | 188.52 | 220.369 | 266.4 | 247.9 | 271.5 | 257.2 | 419.3 | 50.1 | 19.8 | 88.7 | 3.6 | 276.1 | 4.6 | 153.4 | 167 | 576.3 | 728.6 | 266.7 | 294.7 | 570.2 | 758.5 | 697.7 | 371.8 | 396.4 | 578.1 | 432 | 389.7 | 528.2 | 253.1 | 515 | 246.7 | 283.6 | 278.4 | 263.2 | 240.6 | 264 | 262.3 | 232.5
970 | 749 | 471 | 188.4 | 220.2287 | 264.8 | 248.5 | 272.1 | 258 | 414.3 | 50.1 | 19.8 | 88.6 | 4.2 | 278.3 | 4.6 | 153.7 | 167.3 | 572.5 | 734.9 | 267.1 | 295.1 | 563.3 | 765.1 | 699.1 | 372.2 | 393.3 | 567.9 | 432.6 | 388.5 | 528.8 | 253.4 | 514.9 | 247 | 283.7 | 278.6 | 263.3 | 240.8 | 263.9 | 262.5 | 232.6
971 | 750 | 471.5 | 188.6 | 220.4625 | 267.1 | 248.8 | 272 | 258.4 | 411.2 | 50.2 | 19.8 | 88.4 | 4.1 | 279.4 | 4.8 | 153.9 | 167.5 | 569.8 | 740.4 | 268.1 | 295.5 | 560.3 | 777.5 | 699.9 | 372.7 | 392.7 | 566.3 | 433.1 | 386.4 | 529.2 | 253.6 | 515.3 | 247.3 | 283.7 | 278.9 | 263.4 | 240.9 | 263.8 | 262.4 | 232.7
972 | 751 | 471.8 | 188.72 | 220.6028 | 267.2 | 248.6 | 271.5 | 258.6 | 409.2 | 50.2 | 19.8 | 88.3 | 4.3 | 277.4 | 4.8 | 154.2 | 167.8 | 567.2 | 746.1 | 268.6 | 295.8 | 564 | 790 | 701.9 | 373.1 | 393 | 565.7 | 433.7 | 386.5 | 534.6 | 253.9 | 516.2 | 247.5 | 283.8 | 279 | 263.5 | 241.2 | 263.9 | 262.4 | 232.8
973 | 752 | 471.2 | 188.48 | 220.3223 | 268.5 | 247.3 | 270.8 | 258.2 | 407 | 50.3 | 19.8 | 88.3 | 4.3 | 268.9 | 4.7 | 154.5 | 168.1 | 571.4 | 751.4 | 268.2 | 296.2 | 572.7 | 795 | 703.9 | 373.6 | 393.6 | 563.5 | 434.3 | 388.8 | 534.5 | 254.1 | 516.7 | 247.8 | 283.7 | 278.9 | 263.3 | 241.3 | 263.9 | 262.3 | 232.9
974 | 753 | 472.3 | 188.92 | 220.8366 | 268.6 | 246.4 | 270.8 | 256.8 | 405.1 | 50.4 | 19.8 | 88.2 | 4.1 | 260.3 | 4.8 | 154.8 | 168.4 | 584.2 | 752 | 268.7 | 296.5 | 580.4 | 802.5 | 706.8 | 374.1 | 394.9 | 570.7 | 434.9 | 391.8 | 545.7 | 254.4 | 518.1 | 248.1 | 283.6 | 278.9 | 263.3 | 241.5 | 263.9 | 262.2 | 233.1
975 | 754 | 472.1 | 188.84 | 220.7431 | 267.7 | 244.9 | 270.6 | 256.9 | 407.5 | 50.4 | 19.8 | 88.2 | 4.1 | 262.2 | 4.7 | 155.1 | 168.6 | 588.9 | 756.4 | 268.7 | 296.9 | 581.3 | 807.7 | 708.2 | 374.5 | 396.5 | 590.4 | 435.5 | 393 | 545.6 | 254.6 | 519.2 | 248.3 | 283.7 | 279 | 263.4 | 241.7 | 264 | 262.2 | 233.2
976 | 755 | 472.4 | 188.96 | 220.8834 | 266.9 | 245.7 | 271.1 | 257.5 | 410.8 | 50.4 | 19.8 | 88.2 | 4.5 | 262.6 | 4.6 | 155.3 | 168.9 | 611.8 | 760.3 | 268.4 | 297.2 | 614.8 | 801.2 | 709.7 | 375 | 398.3 | 612.7 | 436 | 397 | 557.5 | 254.9 | 522.3 | 248.6 | 283.6 | 279.1 | 263.6 | 241.8 | 263.9 | 262.5 | 233.3
977 | 756 | 472.1 | 188.84 | 220.7431 | 266.5 | 245.6 | 271.2 | 257.7 | 412.2 | 50.4 | 19.8 | 88.2 | 3.7 | 261.9 | 4.4 | 155.6 | 169.2 | 628.7 | 762.5 | 268.3 | 297.5 | 621 | 801 | 712.1 | 375.5 | 398.9 | 627.7 | 436.6 | 398.7 | 560.1 | 255.2 | 524.3 | 248.9 | 283.5 | 279.1 | 263.7 | 242 | 264 | 262.7 | 233.4
978 | 757 | 471.9 | 188.76 | 220.6496 | 266.4 | 246.8 | 271 | 258.6 | 410.4 | 50.4 | 19.8 | 88.2 | 3.9 | 261.8 | 4.3 | 155.9 | 169.5 | 643.1 | 765 | 268.3 | 297.9 | 632.2 | 820.3 | 714.2 | 376 | 398.1 | 634.8 | 437.1 | 404.9 | 569.9 | 255.5 | 526.7 | 249.2 | 283.5 | 279.1 | 263.6 | 242.2 | 264.4 | 262.8 | 233.5
979 | 758 | 471.7 | 188.68 | 220.556 | 266.6 | 248 | 270.7 | 258.6 | 408.7 | 50.3 | 19.8 | 88.2 | 3.5 | 262.8 | 4.2 | 156.2 | 169.8 | 665.4 | 764.9 | 269.4 | 298.2 | 648.6 | 826.8 | 715.8 | 376.5 | 398.3 | 633.8 | 437.6 | 409.5 | 578.2 | 255.7 | 529.2 | 249.4 | 283.6 | 279.2 | 263.6 | 242.5 | 264.7 | 263 | 233.7
980 | 759 | 471.7 | 188.68 | 220.556 | 266.2 | 248.5 | 269.7 | 259.3 | 407.3 | 50.3 | 19.8 | 88.2 | 3.9 | 263.3 | 4.1 | 156.5 | 170.1 | 662.2 | 763.8 | 270.1 | 298.5 | 646.5 | 817.1 | 715.9 | 377 | 399.5 | 634.5 | 438.2 | 410 | 576 | 256 | 530.2 | 249.7 | 283.7 | 279.3 | 263.7 | 242.7 | 264.8 | 263.1 | 233.8
981 | 760 | 472 | 188.8 | 220.6963 | 265.3 | 248.8 | 268.2 | 260.4 | 404.7 | 50.2 | 19.8 | 88.3 | 4.4 | 263.7 | 3.9 | 156.8 | 170.4 | 653.2 | 761.2 | 269.8 | 298.9 | 637.7 | 804.4 | 716.5 | 377.6 | 401.6 | 631.8 | 438.8 | 409.9 | 576.9 | 256.3 | 531.9 | 249.9 | 283.7 | 279.1 | 263.8 | 242.9 | 265.1 | 263.1 | 233.9
982 | 761 | 471.2 | 188.48 | 220.3223 | 264.1 | 248.8 | 267.4 | 260.9 | 404.9 | 50.2 | 19.8 | 88.3 | 4.4 | 266.7 | 3.7 | 157.1 | 170.6 | 636.8 | 751.6 | 269.7 | 299.2 | 613.2 | 786.2 | 715 | 378.1 | 403.3 | 610.3 | 439.3 | 406.3 | 564.1 | 256.5 | 531.1 | 250.2 | 283.8 | 279 | 263.9 | 243.1 | 265.3 | 263.1 | 234.1
983 | 762 | 473.1 | 189.24 | 221.2107 | 265.7 | 248.3 | 267.1 | 261.5 | 402.4 | 50.1 | 19.8 | 88.5 | 4.2 | 268.5 | 3.6 | 157.3 | 170.9 | 623.8 | 751.4 | 269.7 | 299.5 | 598.5 | 784.8 | 715.2 | 378.7 | 401.4 | 596.7 | 439.9 | 402 | 554.6 | 256.8 | 529.7 | 250.4 | 283.9 | 278.9 | 263.8 | 243.4 | 265.4 | 263.2 | 234.3
984 | 763 | 472 | 188.8 | 220.6963 | 267.6 | 247.9 | 267.1 | 261.5 | 399.3 | 50.1 | 19.8 | 88.6 | 3.7 | 269 | 3.5 | 157.6 | 171.2 | 621.4 | 747.7 | 269.7 | 299.9 | 612.1 | 806.2 | 717 | 379.2 | 400 | 591.1 | 440.5 | 404.3 | 562.6 | 257 | 529.7 | 250.6 | 283.9 | 278.6 | 263.6 | 243.6 | 265.5 | 263.3 | 234.4
985 | 764 | 471.4 | 188.56 | 220.4158 | 270.3 | 248 | 266.8 | 260.8 | 399.2 | 50.1 | 19.8 | 88.6 | 3.6 | 267.2 | 3.3 | 157.9 | 171.5 | 626.6 | 741.2 | 269.7 | 300.2 | 640.6 | 820.9 | 718.5 | 379.8 | 402.5 | 584.7 | 441.1 | 411.9 | 572.4 | 257.3 | 530.7 | 250.8 | 283.9 | 278.6 | 263.5 | 243.8 | 265.8 | 263.5 | 234.6
986 | 765 | 470.6 | 188.24 | 220.0417 | 269.9 | 247.1 | 265.8 | 259.4 | 398.8 | 50.1 | 19.8 | 88.7 | 3.8 | 266.9 | 3.1 | 158.2 | 171.8 | 624.9 | 733.9 | 269.9 | 300.6 | 657.1 | 833 | 718.8 | 380.3 | 402 | 575.8 | 441.7 | 417.1 | 581.5 | 257.6 | 532.1 | 251 | 284.1 | 278.6 | 263.4 | 244.2 | 266.3 | 263.6 | 234.9
987 | 766 | 471.7 | 188.68 | 220.556 | 269.1 | 246.2 | 264.7 | 258 | 398.4 | 50.3 | 19.8 | 88.9 | 3.8 | 267 | 3 | 158.5 | 172.1 | 631.5 | 734 | 270 | 300.9 | 669.1 | 835.8 | 720.1 | 380.9 | 402.4 | 580.8 | 442.3 | 420.6 | 590 | 257.8 | 533.8 | 251.2 | 284.1 | 278.7 | 263.5 | 244.5 | 266.8 | 263.9 | 235.1
988 | 767 | 471.5 | 188.6 | 220.4625 | 268.5 | 245.3 | 263.9 | 257.9 | 396.3 | 50.4 | 19.8 | 89 | 3.8 | 269.3 | 2.9 | 158.8 | 172.4 | 624.3 | 726.9 | 270.2 | 301.3 | 667.8 | 820.6 | 718.1 | 381.4 | 402.4 | 570.4 | 442.8 | 420.9 | 591.3 | 258.1 | 534.2 | 251.4 | 283.9 | 278.4 | 263.7 | 244.9 | 267 | 264.1 | 235.2
989 | 768 | 471.7 | 188.68 | 220.556 | 266.8 | 244.7 | 262.8 | 257.6 | 393.5 | 50.5 | 19.8 | 89.1 | 4.2 | 271.6 | 2.9 | 159.1 | 172.7 | 606.9 | 720.5 | 270.2 | 301.6 | 655.9 | 806.9 | 716.8 | 382 | 402.9 | 560.6 | 443.4 | 419.7 | 587 | 258.4 | 533.5 | 251.6 | 283.6 | 278 | 263.6 | 245.2 | 267.1 | 264.2 | 235.4
990 | 769 | 470.8 | 188.32 | 220.1352 | 266.6 | 244.4 | 262.9 | 257.5 | 392.4 | 50.6 | 19.8 | 89.1 | 3.7 | 271.8 | 2.9 | 159.4 | 172.9 | 589.7 | 709.9 | 270.2 | 302 | 649.9 | 807.7 | 716.6 | 382.6 | 401.7 | 544.3 | 444 | 417.1 | 574.3 | 258.7 | 531.8 | 251.7 | 283.3 | 277.6 | 263.4 | 245.5 | 267.2 | 264.3 | 235.5
991 | 770 | 471.6 | 188.64 | 220.5093 | 265.8 | 244.4 | 262.3 | 259 | 390.2 | 50.6 | 19.8 | 89.1 | 4.2 | 269.8 | 2.7 | 159.7 | 173.2 | 585.7 | 709.2 | 270.5 | 302.3 | 642.4 | 827 | 718.8 | 383.3 | 399.4 | 533.9 | 444.5 | 421.5 | 571.7 | 258.9 | 531.1 | 251.8 | 283 | 277.2 | 263.2 | 245.7 | 267.4 | 264.5 | 235.6
992 | 771 | 471.7 | 188.68 | 220.556 | 265.7 | 244.4 | 261.6 | 260.6 | 390.1 | 50.5 | 19.8 | 89.1 | 4.4 | 269.6 | 2.8 | 160 | 173.5 | 606.1 | 707.7 | 270.9 | 302.7 | 653.4 | 837.7 | 721.2 | 383.9 | 397.9 | 531 | 445.2 | 428.9 | 572.2 | 259.2 | 532.3 | 251.9 | 282.6 | 276.8 | 263.1 | 246.1 | 268 | 264.8 | 235.7
993 | 772 | 472.3 | 188.92 | 220.8366 | 265.3 | 244 | 261.1 | 263.1 | 396.8 | 50.5 | 19.8 | 89.2 | 4.3 | 269.7 | 2.8 | 160.3 | 173.8 | 636.5 | 704.1 | 271.2 | 303 | 673.6 | 852.7 | 722.5 | 384.5 | 399.8 | 533.7 | 445.8 | 442.6 | 572.8 | 259.4 | 533.7 | 252 | 282.1 | 276.5 | 263.1 | 246.6 | 269 | 265.5 | 236
994 | 773 | 472.1 | 188.84 | 220.7431 | 264.8 | 244.3 | 261.6 | 266.1 | 405.3 | 50.5 | 19.8 | 89.3 | 4.1 | 270.4 | 2.7 | 160.6 | 174.2 | 654.9 | 696 | 271.2 | 303.4 | 694.9 | 842.6 | 720.5 | 385.1 | 400.5 | 523.5 | 446.5 | 457.7 | 577.1 | 259.7 | 534.6 | 252.1 | 281.7 | 276.2 | 263.1 | 247.4 | 270.3 | 266.7 | 236.3
995 | 774 | 470.4 | 188.16 | 219.9482 | 265 | 245.1 | 262.2 | 269.6 | 416.3 | 50.6 | 19.8 | 89.4 | 4.2 | 271 | 2.7 | 160.9 | 174.5 | 653.4 | 696.8 | 271.7 | 303.7 | 698.9 | 842.3 | 721.4 | 385.7 | 416.2 | 515.3 | 447.1 | 472.9 | 573.4 | 259.9 | 534.1 | 252.2 | 281.4 | 275.9 | 263.1 | 248 | 271.5 | 267.8 | 236.6
996 | 775 | 471.8 | 188.72 | 220.6028 | 265.2 | 246.5 | 262.7 | 272.8 | 421.2 | 50.5 | 19.8 | 89.4 | 4.3 | 271.3 | 2.7 | 161.2 | 174.8 | 650.9 | 703.1 | 272.5 | 304.1 | 704.8 | 847.9 | 723.2 | 386.2 | 419.9 | 518.7 | 447.6 | 477.4 | 580.3 | 260.2 | 534.7 | 252.4 | 281.3 | 275.7 | 263.1 | 248.4 | 272.2 | 268.5 | 236.8
997 | 776 | 471.2 | 188.48 | 220.3223 | 265.1 | 248.5 | 262.7 | 274.5 | 423.8 | 50.5 | 19.8 | 89.5 | 4 | 274.1 | 2.8 | 161.5 | 175.1 | 659.5 | 706.8 | 272.4 | 304.4 | 719.1 | 845.9 | 724.8 | 386.8 | 419.6 | 517.8 | 448.2 | 487.6 | 582.8 | 260.5 | 535 | 252.4 | 281.1 | 275.4 | 263.1 | 249 | 272.9 | 269.4 | 237.1
998 | 777 | 471.1 | 188.44 | 220.2755 | 264.2 | 249.7 | 263.3 | 275.6 | 430 | 50.5 | 19.8 | 89.6 | 3.9 | 277.3 | 2.9 | 161.8 | 175.4 | 655.5 | 706.4 | 272.4 | 304.8 | 715.1 | 823.5 | 722.8 | 387.3 | 423.5 | 509.7 | 448.8 | 488.4 | 580.5 | 260.7 | 534.6 | 252.6 | 281 | 275.2 | 263.1 | 249.5 | 273.7 | 270.2 | 237.4
999 | 778 | 472.8 | 189.12 | 221.0704 | 263.5 | 249.9 | 263.9 | 277 | 430.3 | 50.6 | 19.8 | 89.7 | 4.2 | 277.6 | 3 | 162.1 | 175.6 | 640.8 | 712.6 | 272.4 | 305.2 | 688.5 | 820.4 | 722.8 | 387.8 | 431.1 | 511.4 | 449.4 | 485.3 | 577.9 | 261 | 534.2 | 252.8 | 281 | 275.1 | 263.3 | 249.9 | 274.3 | 270.8 | 237.6
1000 | 779 | 471.7 | 188.68 | 220.556 | 264.1 | 251 | 264.3 | 277.5 | 431.6 | 50.6 | 19.8 | 89.7 | 4.2 | 276.3 | 3.3 | 162.4 | 175.9 | 639.8 | 721.7 | 272.4 | 305.6 | 670.8 | 815.2 | 722.8 | 388.3 | 455.2 | 521.9 | 449.9 | 479.6 | 577.7 | 261.2 | 534.4 | 253 | 281.1 | 275.4 | 263.8 | 250.2 | 274.5 | 271 | 237.8
1001 | 780 | 471.3 | 188.52 | 220.369 | 265.3 | 251.4 | 263.6 | 276.1 | 430 | 50.6 | 19.8 | 89.6 | 3.6 | 276.9 | 3.4 | 162.7 | 176.2 | 642.9 | 724.4 | 272.3 | 306 | 659.8 | 797.2 | 722.3 | 388.9 | 459.2 | 537.3 | 450.5 | 474.4 | 579.6 | 261.5 | 534.9 | 253.2 | 281.2 | 275.8 | 264.4 | 250.5 | 274.7 | 271.2 | 237.9
1002 | 781 | 470.9 | 188.36 | 220.182 | 266.1 | 251.2 | 263.6 | 273.1 | 429.2 | 50.7 | 19.8 | 89.6 | 3.8 | 283.7 | 3.4 | 163 | 176.5 | 633.3 | 727 | 272.3 | 306.4 | 640.2 | 784.6 | 720.4 | 389.4 | 469.1 | 546.1 | 451.1 | 468.2 | 575.6 | 261.7 | 535.1 | 253.4 | 281.5 | 276.5 | 265 | 250.8 | 274.6 | 271.2 | 238
1003 | 782 | 471.6 | 188.64 | 220.5093 | 267.6 | 250.6 | 264.8 | 270 | 427.9 | 50.8 | 19.8 | 89.7 | 4.1 | 286.6 | 3.2 | 163.3 | 176.8 | 624.9 | 726.2 | 272.3 | 306.8 | 632.1 | 798.8 | 721.5 | 389.9 | 464.1 | 554.3 | 451.7 | 463.1 | 572 | 262 | 535.6 | 253.7 | 282 | 276.9 | 265.1 | 251.1 | 274.5 | 271.1 | 238.2
1004 | 783 | 471.6 | 188.64 | 220.5093 | 267.7 | 250.1 | 265.7 | 268.2 | 425.3 | 50.8 | 19.8 | 89.9 | 4.5 | 285.8 | 3.2 | 163.6 | 177.1 | 609 | 714.5 | 272.4 | 307.2 | 633.5 | 778.3 | 720.5 | 390.5 | 462.4 | 539.2 | 452.4 | 463.9 | 565 | 262.2 | 535 | 253.9 | 282.4 | 277.1 | 264.7 | 251.3 | 274.7 | 271.1 | 238.3
1005 | 784 | 471.7 | 188.68 | 220.556 | 267.6 | 250.4 | 266.1 | 267.8 | 422.9 | 50.8 | 19.8 | 90 | 4.2 | 286.1 | 3.5 | 163.9 | 177.4 | 591.4 | 699.3 | 272.7 | 307.6 | 624.4 | 758.9 | 718.6 | 391 | 469.2 | 526 | 453 | 460.3 | 554.8 | 262.5 | 533.4 | 254.2 | 282.6 | 277.2 | 264.6 | 251.7 | 275.3 | 271.6 | 238.5
1006 | 785 | 472.6 | 189.04 | 220.9769 | 268.7 | 250.8 | 266 | 269.7 | 424.8 | 50.8 | 19.8 | 90.2 | 3.9 | 291 | 3.7 | 164.2 | 177.6 | 574 | 691.5 | 273.3 | 308.1 | 623.6 | 760.1 | 717.2 | 391.6 | 460.7 | 511.9 | 453.5 | 457.7 | 551.4 | 262.7 | 532.2 | 254.4 | 282.8 | 277.1 | 264.4 | 252.1 | 275.9 | 272.2 | 238.8
1007 | 786 | 471 | 188.4 | 220.2287 | 270.7 | 250 | 266.8 | 271.5 | 428.8 | 50.8 | 19.8 | 90.3 | 4.1 | 292.2 | 4 | 164.5 | 177.9 | 563.5 | 692.9 | 273.6 | 308.5 | 617.3 | 780.3 | 718.2 | 392.1 | 453.9 | 505.7 | 454.1 | 455.9 | 548.2 | 263 | 531.3 | 254.5 | 282.9 | 277 | 264.2 | 252.5 | 276.6 | 272.6 | 239
1008 | 787 | 472.7 | 189.08 | 221.0236 | 272.2 | 249.7 | 268 | 273.1 | 424.2 | 50.9 | 19.8 | 90.3 | 4.3 | 293 | 4 | 164.8 | 178.2 | 561.6 | 700.7 | 273.8 | 308.9 | 624.5 | 798.8 | 717.8 | 392.6 | 446.6 | 510.5 | 454.8 | 450.8 | 548 | 263.2 | 530.8 | 254.7 | 282.9 | 276.9 | 264.2 | 252.7 | 276.6 | 272.7 | 239.1
1009 | 788 | 473.4 | 189.36 | 221.3509 | 270.8 | 249.7 | 267.5 | 274 | 419.5 | 50.9 | 19.8 | 90.3 | 4.6 | 287.3 | 4 | 165.1 | 178.5 | 564.3 | 704.5 | 274.2 | 309.4 | 626.9 | 820.3 | 719.9 | 393.2 | 441.6 | 515 | 455.4 | 449.4 | 556.6 | 263.5 | 531.5 | 254.9 | 282.9 | 276.9 | 264.3 | 252.9 | 276.4 | 272.7 | 239.2
1010 | 789 | 471.1 | 188.44 | 220.2755 | 269.7 | 249.7 | 266.7 | 274.1 | 419.3 | 50.9 | 19.8 | 90.4 | 4.4 | 286.9 | 4.1 | 165.4 | 178.8 | 559.9 | 697.5 | 274.5 | 309.9 | 623.5 | 827.3 | 719 | 393.7 | 437.2 | 504.5 | 456 | 454.6 | 557.3 | 263.7 | 531.9 | 255 | 282.8 | 276.8 | 264.4 | 253.2 | 276.5 | 273 | 239.5
1011 | 790 | 471.4 | 188.56 | 220.4158 | 268.7 | 249.4 | 267 | 275.3 | 417.7 | 51 | 19.8 | 90.4 | 4.2 | 290.1 | 4.2 | 165.7 | 179.1 | 556.4 | 697.3 | 274.8 | 310.3 | 626.8 | 839 | 720.5 | 394.3 | 431.9 | 497.8 | 456.6 | 455.9 | 552.7 | 264 | 531.2 | 255.1 | 282.8 | 276.6 | 264.3 | 253.6 | 277.1 | 273.5 | 239.7
1012 | 791 | 472.1 | 188.84 | 220.7431 | 267.9 | 249.8 | 267.3 | 276.8 | 415.7 | 51 | 19.8 | 90.4 | 3.9 | 292.5 | 4.2 | 166 | 179.3 | 557.9 | 699.6 | 275.1 | 310.7 | 619.2 | 847 | 721.2 | 394.8 | 429 | 494.7 | 457.2 | 453.8 | 552.1 | 264.3 | 531 | 255.3 | 282.7 | 276.4 | 264.4 | 254 | 277.5 | 274 | 240
1013 | 792 | 473.4 | 189.36 | 221.3509 | 267.3 | 250.3 | 266.5 | 278.1 | 412.6 | 51.1 | 19.8 | 90.3 | 4 | 291 | 4.2 | 166.3 | 179.6 | 567.4 | 703.4 | 275.3 | 311.2 | 633 | 840 | 721.7 | 395.4 | 427.5 | 495.8 | 457.8 | 453.1 | 559.6 | 264.5 | 531.6 | 255.4 | 282.5 | 276.1 | 264.4 | 254.4 | 277.6 | 274.3 | 240.1
1014 | 793 | 473 | 189.2 | 221.1639 | 266.4 | 250.5 | 266.2 | 278.1 | 412.1 | 51.1 | 19.8 | 90.3 | 4.4 | 289.5 | 4.2 | 166.6 | 179.9 | 566.3 | 703 | 275.4 | 311.6 | 639.6 | 844.9 | 722.8 | 396 | 426.7 | 493.7 | 458.2 | 459.6 | 559.3 | 264.8 | 532.1 | 255.5 | 282.3 | 276.2 | 264.4 | 254.7 | 278 | 274.7 | 240.4
1015 | 794 | 472.8 | 189.12 | 221.0704 | 265.5 | 250.6 | 266.4 | 278.4 | 412.4 | 51.2 | 19.8 | 90.3 | 4.4 | 288.1 | 4 | 166.9 | 180.2 | 566.2 | 704.4 | 275.7 | 312.1 | 634 | 841.7 | 722.1 | 396.5 | 426.8 | 495.7 | 458.7 | 459.5 | 560.3 | 265 | 532.9 | 255.7 | 282.4 | 276.3 | 264.4 | 255 | 278.4 | 275.2 | 240.6
1016 | 795 | 473.9 | 189.56 | 221.5847 | 264.5 | 251.2 | 266.5 | 278.6 | 411 | 51.2 | 19.8 | 90.3 | 3.9 | 285.6 | 3.8 | 167.2 | 180.5 | 583.7 | 715.1 | 276 | 312.6 | 634.7 | 855.7 | 724.7 | 397.1 | 427.7 | 501.7 | 459.3 | 459.1 | 572.3 | 265.3 | 534.8 | 255.8 | 282.3 | 276.3 | 264.5 | 255.3 | 278.8 | 275.3 | 240.8
1017 | 796 | 471.6 | 188.64 | 220.5093 | 264.3 | 251.9 | 266.1 | 277.9 | 407.8 | 51.2 | 19.7 | 90.2 | 4 | 281.7 | 3.5 | 167.6 | 180.8 | 592.1 | 723.7 | 276.3 | 313.1 | 645.9 | 850.8 | 725.4 | 397.7 | 429.4 | 525 | 459.8 | 458.3 | 583.7 | 265.6 | 538.2 | 256 | 282.3 | 276.2 | 264.6 | 255.6 | 279 | 275.5 | 240.9
1018 | 797 | 470.9 | 188.36 | 220.182 | 264.4 | 252.3 | 265.9 | 277.1 | 406.9 | 51.3 | 19.8 | 90.2 | 3.7 | 281.5 | 3.3 | 167.9 | 181.1 | 601.4 | 730.2 | 276.8 | 313.5 | 636.6 | 833 | 724.6 | 398.3 | 432.4 | 550.1 | 460.4 | 454.9 | 588.5 | 265.8 | 539.8 | 256.2 | 282.3 | 276.4 | 264.9 | 255.7 | 278.8 | 275.6 | 241
1019 | 798 | 470.4 | 188.16 | 219.9482 | 263.8 | 252.6 | 266 | 275.9 | 410.8 | 51.3 | 19.8 | 90.2 | 3.9 | 281.6 | 3.2 | 168.2 | 181.3 | 599 | 735.4 | 276.9 | 314 | 625.9 | 828 | 725.6 | 398.8 | 435.5 | 567.9 | 460.8 | 453 | 585.4 | 266.1 | 541 | 256.4 | 282.4 | 276.7 | 265.2 | 255.9 | 278.5 | 275.4 | 241.2
1020 | 799 | 470.4 | 188.16 | 219.9482 | 263.5 | 251.6 | 266.7 | 274 | 414.8 | 51.3 | 19.7 | 90.2 | 4.1 | 281.6 | 3 | 168.5 | 181.6 | 596 | 731.2 | 277.1 | 314.5 | 616.7 | 823 | 724 | 399.4 | 437.1 | 561.9 | 461.3 | 449.2 | 578.3 | 266.3 | 541.3 | 256.6 | 282.5 | 276.8 | 265.4 | 256.1 | 278.1 | 275.3 | 241.2
1021 | 800 | 472.4 | 188.96 | 220.8834 | 263.7 | 250.7 | 266.8 | 273.3 | 413.7 | 51.3 | 19.7 | 90.3 | 4.3 | 281.6 | 2.8 | 168.8 | 181.9 | 594.8 | 732.2 | 277.5 | 315 | 604.6 | 803.9 | 722.7 | 400 | 444.5 | 566.8 | 461.8 | 448.4 | 578.7 | 266.6 | 542.1 | 256.8 | 282.6 | 277 | 265.5 | 256.2 | 277.8 | 275.2 | 241.3
1022 | 801 | 471.5 | 188.6 | 220.4625 | 264.4 | 250.9 | 267.1 | 273 | 417.4 | 51.5 | 19.7 | 90.2 | 4.2 | 280.8 | 2.7 | 169.1 | 182.1 | 594.4 | 735.2 | 277.9 | 315.4 | 589.3 | 788.6 | 722.9 | 400.7 | 447.5 | 568.9 | 462.3 | 443.6 | 572.4 | 266.9 | 543 | 257 | 282.7 | 277.3 | 265.6 | 256.2 | 277.5 | 275.1 | 241.4
1023 | 802 | 471.9 | 188.76 | 220.6496 | 266.4 | 251.6 | 268.6 | 272.4 | 420.6 | 51.6 | 19.7 | 90.3 | 3.8 | 280.7 | 2.6 | 169.4 | 182.4 | 580.8 | 720.4 | 278 | 315.9 | 573.1 | 754.1 | 719.9 | 401.3 | 446.9 | 557.4 | 462.7 | 438.6 | 561 | 267.1 | 543.3 | 257.2 | 282.9 | 277.8 | 265.9 | 256.3 | 277.1 | 274.9 | 241.5
1024 | 803 | 472.3 | 188.92 | 220.8366 | 269.1 | 252.2 | 269.7 | 271.2 | 426.5 | 51.7 | 19.7 | 90.4 | 3.9 | 281.3 | 2.5 | 169.8 | 182.7 | 570.9 | 705.2 | 278.3 | 316.4 | 553 | 722.7 | 717.8 | 402 | 448.1 | 542.3 | 463.2 | 435.3 | 550 | 267.4 | 542.5 | 257.4 | 283.4 | 278.4 | 266.2 | 256.4 | 276.7 | 274.7 | 241.6
1025 | 804 | 471.9 | 188.76 | 220.6496 | 271.7 | 253.1 | 270.6 | 269.6 | 426.4 | 51.7 | 19.7 | 90.5 | 4.1 | 280.9 | 2.4 | 170.1 | 182.9 | 566 | 693.1 | 278.5 | 316.9 | 536.8 | 700.3 | 715 | 402.6 | 443.9 | 533 | 463.6 | 432.6 | 539.9 | 267.7 | 542 | 257.6 | 283.9 | 279.1 | 266.6 | 256.5 | 276.5 | 274.6 | 241.7
1026 | 805 | 472.6 | 189.04 | 220.9769 | 275.3 | 253.3 | 271.2 | 269.4 | 426 | 51.7 | 19.7 | 90.5 | 4.2 | 279.9 | 2.3 | 170.4 | 183.2 | 549.7 | 686.2 | 278.9 | 317.3 | 522.8 | 677.2 | 711.7 | 403.3 | 439.7 | 524 | 464 | 431.3 | 526.4 | 267.9 | 539.8 | 257.8 | 284.4 | 280.1 | 266.9 | 256.6 | 276.2 | 274.6 | 241.7
1027 | 806 | 472.3 | 188.92 | 220.8366 | 279 | 254.5 | 272 | 269.9 | 426.1 | 51.6 | 19.7 | 90.5 | 4.3 | 280.1 | 2.3 | 170.7 | 183.5 | 547.7 | 682.9 | 279.2 | 317.8 | 518.9 | 668.4 | 708.8 | 404 | 436.6 | 516.1 | 464.4 | 428.5 | 519 | 268.2 | 538.3 | 258.1 | 285 | 280.9 | 267.4 | 256.7 | 275.8 | 274.4 | 241.8
1028 | 807 | 472.6 | 189.04 | 220.9769 | 283.6 | 255.7 | 273.5 | 270.2 | 427.9 | 51.6 | 19.7 | 90.5 | 4.2 | 280.1 | 2.3 | 171 | 183.8 | 540.7 | 685.8 | 279.3 | 318.3 | 522.5 | 680.1 | 707.1 | 404.7 | 431.1 | 505.4 | 464.7 | 425 | 515.6 | 268.5 | 536.8 | 258.3 | 285.6 | 281.4 | 267.5 | 256.8 | 275.9 | 274.1 | 241.9
1029 | 808 | 472.4 | 188.96 | 220.8834 | 284.7 | 256.6 | 274 | 268.4 | 423.6 | 51.5 | 19.7 | 90.5 | 4.4 | 280.2 | 2.4 | 171.3 | 184 | 529.5 | 682.6 | 279.5 | 318.9 | 523.5 | 682.6 | 706.5 | 405.4 | 426.5 | 499.2 | 465 | 420.9 | 508.2 | 268.7 | 535 | 258.5 | 285.9 | 281.8 | 267.5 | 256.9 | 275.9 | 273.9 | 242.1
1030 | 809 | 472.1 | 188.84 | 220.7431 | 284.2 | 257.3 | 275.4 | 267.6 | 424 | 51.5 | 19.7 | 90.5 | 4 | 280.1 | 2.3 | 171.6 | 184.3 | 522.9 | 675.4 | 279.7 | 319.3 | 521.8 | 687.5 | 704.2 | 406.1 | 424.7 | 490.5 | 465.3 | 417.5 | 499.4 | 269 | 533.5 | 258.7 | 286.1 | 282.5 | 267.6 | 257 | 276 | 273.7 | 242.2
1031 | 810 | 471.9 | 188.76 | 220.6496 | 284.4 | 257.4 | 276.4 | 268.2 | 426.1 | 51.5 | 19.7 | 90.6 | 3.6 | 280.1 | 2.3 | 171.9 | 184.5 | 516 | 680 | 280 | 319.9 | 525.6 | 700.5 | 703.3 | 406.8 | 422.5 | 486.1 | 465.6 | 415.1 | 499.7 | 269.3 | 532.3 | 258.9 | 286.4 | 283.1 | 268 | 257.1 | 276.1 | 273.8 | 242.3
1032 | 811 | 471.9 | 188.76 | 220.6496 | 285.6 | 257.3 | 275.9 | 269.5 | 427.3 | 51.6 | 19.7 | 90.7 | 3.8 | 280.1 | 2.3 | 172.3 | 184.8 | 510.6 | 687.4 | 280.1 | 320.3 | 524.4 | 711 | 701.7 | 407.6 | 420.3 | 490.4 | 465.8 | 412.1 | 497.6 | 269.5 | 531.2 | 259.2 | 286.7 | 283.5 | 268.3 | 257.2 | 276.1 | 273.8 | 242.4
1033 | 812 | 472.8 | 189.12 | 221.0704 | 285.8 | 256.9 | 276.6 | 269.9 | 427.4 | 51.6 | 19.7 | 90.8 | 3.5 | 280 | 2.3 | 172.6 | 185.1 | 506.7 | 691.8 | 280.2 | 320.9 | 528.9 | 715.6 | 701.5 | 408.3 | 418.1 | 487.2 | 466.1 | 410.2 | 499.6 | 269.8 | 530.1 | 259.4 | 287.1 | 283.7 | 268.2 | 257.3 | 276.4 | 273.9 | 242.6
1034 | 813 | 472.9 | 189.16 | 221.1171 | 286.1 | 256.7 | 277.8 | 270.5 | 427.8 | 51.6 | 19.7 | 90.8 | 3.7 | 280.1 | 2.3 | 172.9 | 185.4 | 501.3 | 692.6 | 280.4 | 321.4 | 550.4 | 722.2 | 703.1 | 409 | 416.5 | 484.1 | 466.4 | 410.2 | 501.3 | 270 | 529.5 | 259.6 | 287.6 | 284 | 268 | 257.4 | 276.7 | 274 | 242.7
1035 | 814 | 473.4 | 189.36 | 221.3509 | 287.5 | 256.4 | 278.3 | 269.7 | 429.8 | 51.6 | 19.7 | 91 | 4 | 280.1 | 2.2 | 173.2 | 185.6 | 495.9 | 690.1 | 280.8 | 321.9 | 554 | 717.8 | 700.5 | 409.7 | 414 | 477 | 466.7 | 413.2 | 501.2 | 270.3 | 528.4 | 259.7 | 287.7 | 284.1 | 267.8 | 257.7 | 277.3 | 274.2 | 243
1036 | 815 | 472.9 | 189.16 | 221.1171 | 288.8 | 255.3 | 278.2 | 268.2 | 429.3 | 51.6 | 19.7 | 91.1 | 3.9 | 279.9 | 2.1 | 173.5 | 185.9 | 489.8 | 692.8 | 281 | 322.5 | 550.2 | 733.6 | 699.2 | 410.4 | 409.9 | 473.9 | 467 | 413 | 498.8 | 270.5 | 527.3 | 259.9 | 287.7 | 283.9 | 267.7 | 258 | 277.8 | 274.5 | 243.2
1037 | 816 | 472.2 | 188.88 | 220.7898 | 288.3 | 255.3 | 277 | 269 | 422.5 | 51.6 | 19.7 | 91.1 | 3.3 | 279.6 | 2 | 173.8 | 186.2 | 492 | 695.1 | 281.5 | 323.1 | 546.5 | 747.5 | 699.1 | 411.2 | 407.5 | 470.8 | 467.4 | 414.9 | 501 | 270.8 | 526.9 | 260 | 287.5 | 283.6 | 267.5 | 258.2 | 278.2 | 274.8 | 243.3
1038 | 817 | 472.8 | 189.12 | 221.0704 | 287.4 | 256.4 | 275.2 | 270.8 | 418.7 | 51.7 | 19.7 | 91.2 | 3.6 | 279.5 | 1.9 | 174.1 | 186.5 | 487.9 | 696.2 | 281.7 | 323.8 | 545.5 | 728.2 | 695.5 | 411.9 | 404.9 | 467.3 | 467.7 | 414.9 | 504.3 | 271.1 | 526.3 | 260.1 | 287.3 | 283.3 | 267.4 | 258.5 | 278.8 | 275.1 | 243.5
1039 | 818 | 472.1 | 188.84 | 220.7431 | 285.3 | 257.3 | 273.5 | 272.4 | 418.2 | 51.7 | 19.7 | 91.4 | 3.8 | 279.5 | 1.9 | 174.4 | 186.7 | 492.7 | 700.5 | 282 | 324.4 | 548.2 | 736 | 694.6 | 412.6 | 404.2 | 466.4 | 468 | 413.2 | 502.4 | 271.3 | 525.2 | 260.2 | 287.3 | 283.2 | 267.3 | 258.8 | 279.7 | 275.4 | 243.6
1040 | 819 | 473.9 | 189.56 | 221.5847 | 284.3 | 258.3 | 272.2 | 273.3 | 414.6 | 51.7 | 19.7 | 91.4 | 3.6 | 279.4 | 1.8 | 174.8 | 187 | 488.5 | 698.2 | 282.4 | 325 | 558.9 | 754.1 | 695.1 | 413.4 | 403.1 | 464 | 468.3 | 411.4 | 501.6 | 271.6 | 524.6 | 260.3 | 287.4 | 282.9 | 267.3 | 259 | 279.9 | 275.6 | 243.8
1041 | 820 | 472.3 | 188.92 | 220.8366 | 283.4 | 258.6 | 271.4 | 273.5 | 411.5 | 51.8 | 19.7 | 91.6 | 3.7 | 279.6 | 1.9 | 175.1 | 187.3 | 484.9 | 699.2 | 283.4 | 325.4 | 557.5 | 756 | 694.3 | 414.1 | 403.2 | 461.4 | 468.6 | 410.5 | 499.7 | 271.8 | 523.7 | 260.4 | 287.3 | 282.5 | 267.3 | 259.2 | 279.8 | 275.7 | 243.8
1042 | 821 | 472.2 | 188.88 | 220.7898 | 284.9 | 258.8 | 270.8 | 272.7 | 413.4 | 51.8 | 19.7 | 91.7 | 3.9 | 280.3 | 1.9 | 175.4 | 187.6 | 482.5 | 701.8 | 283.1 | 325.8 | 569.5 | 756.6 | 694 | 414.8 | 405.1 | 464.7 | 469 | 411.3 | 503.5 | 272.1 | 523.5 | 260.5 | 287.1 | 282.2 | 267.3 | 259.4 | 279.8 | 275.7 | 244
1043 | 822 | 472.4 | 188.96 | 220.8834 | 286 | 258.1 | 270.3 | 272.2 | 418.3 | 51.9 | 19.7 | 91.8 | 3.8 | 280.4 | 1.9 | 175.7 | 187.8 | 482.5 | 713.5 | 283.2 | 326.4 | 567 | 758.7 | 696.1 | 415.6 | 411.6 | 481 | 469.4 | 414.2 | 507.1 | 272.3 | 523.6 | 260.6 | 286.9 | 282 | 267.5 | 259.7 | 280.1 | 275.7 | 244.2
1044 | 823 | 472.2 | 188.88 | 220.7898 | 285.7 | 257.3 | 270 | 272.9 | 427.4 | 51.9 | 19.7 | 92 | 3.6 | 279.8 | 1.9 | 176 | 188.1 | 496 | 723 | 283.5 | 327.1 | 561.4 | 747.9 | 697.8 | 416.3 | 425.7 | 504.4 | 469.7 | 412.7 | 510 | 272.6 | 524.6 | 260.8 | 286.6 | 282 | 267.8 | 259.8 | 279.9 | 275.8 | 244.2
1045 | 824 | 472.3 | 188.92 | 220.8366 | 284.6 | 257.3 | 269.1 | 272.8 | 436.9 | 52 | 19.7 | 92.1 | 4.4 | 278.5 | 1.9 | 176.3 | 188.4 | 515.6 | 732.8 | 283.7 | 327.7 | 563.5 | 761.7 | 699.9 | 417.1 | 434.4 | 529.1 | 470 | 414 | 516.7 | 272.8 | 526.1 | 261 | 286.5 | 282.1 | 268.1 | 260 | 280.2 | 275.9 | 244.3
1046 | 825 | 471.7 | 188.68 | 220.556 | 283.2 | 258 | 268.6 | 272.8 | 438.7 | 52 | 19.7 | 92.3 | 4.5 | 274 | 1.8 | 176.7 | 188.7 | 529.2 | 734.3 | 283.9 | 328.3 | 578.7 | 780.1 | 703.7 | 417.8 | 434 | 547 | 470.3 | 419.5 | 529.2 | 273.1 | 527.8 | 261.2 | 286.6 | 282.2 | 268.2 | 260.2 | 280.9 | 276.1 | 244.6
1047 | 826 | 472.5 | 189 | 220.9301 | 282.2 | 258.7 | 269.1 | 273.9 | 434.9 | 52.1 | 19.7 | 92.4 | 4 | 271.3 | 1.7 | 177 | 189 | 538.2 | 738.2 | 284.2 | 328.8 | 597.8 | 787.4 | 705.7 | 418.6 | 435.1 | 556.6 | 470.7 | 424.6 | 537.1 | 273.3 | 529.3 | 261.4 | 287 | 282.9 | 268.2 | 260.4 | 281.3 | 276.2 | 244.8
1048 | 827 | 471.8 | 188.72 | 220.6028 | 280.7 | 258.8 | 269.2 | 274.9 | 431.8 | 52.1 | 19.7 | 92.6 | 4 | 271.2 | 1.7 | 177.3 | 189.3 | 540.6 | 734.4 | 284.6 | 329.2 | 602 | 787.7 | 706.4 | 419.3 | 437.5 | 559.4 | 471.1 | 426.3 | 544.8 | 273.5 | 530.1 | 261.6 | 287.3 | 283.4 | 268.4 | 260.6 | 281.7 | 276.3 | 245
1049 | 828 | 470.3 | 188.12 | 219.9014 | 278.5 | 258.4 | 269.3 | 275.6 | 430 | 52.1 | 19.7 | 92.7 | 4.3 | 271.6 | 1.8 | 177.6 | 189.5 | 541.9 | 726.5 | 284.9 | 329.5 | 593.8 | 770.7 | 706.2 | 420.1 | 438.2 | 549.9 | 471.6 | 423.8 | 543 | 273.8 | 530.5 | 261.8 | 287.5 | 283.7 | 268.6 | 260.8 | 281.4 | 276.6 | 245
1050 | 829 | 471.7 | 188.68 | 220.556 | 277.2 | 257.8 | 270.2 | 274.7 | 425.9 | 52.2 | 19.7 | 92.8 | 4.3 | 272 | 1.8 | 177.9 | 189.8 | 536.3 | 718.6 | 285.1 | 329.1 | 595.1 | 769.1 | 706.8 | 420.9 | 434.6 | 544.9 | 472 | 420.3 | 536.5 | 274 | 530 | 262 | 287.5 | 283.7 | 268.7 | 260.9 | 280.9 | 276.5 | 245.1
1051 | 830 | 472.5 | 189 | 220.9301 | 276.1 | 256.7 | 270.4 | 272.9 | 419.8 | 52.3 | 19.7 | 92.9 | 3.9 | 273.7 | 1.9 | 178.2 | 190 | 527.7 | 712.4 | 285.5 | 329.3 | 599.1 | 773.4 | 706.1 | 421.6 | 430 | 532.6 | 472.5 | 419.8 | 532.3 | 274.2 | 529.6 | 262.2 | 287.6 | 283.7 | 268.6 | 261.1 | 280.6 | 276.5 | 245.2
1052 | 831 | 473.5 | 189.4 | 221.3977 | 276.2 | 255.2 | 270.3 | 272.2 | 415.3 | 52.4 | 19.7 | 92.8 | 3.7 | 275.1 | 1.8 | 178.6 | 190.3 | 524.7 | 709.4 | 285.8 | 329.8 | 594.7 | 764.7 | 706.2 | 422.4 | 426 | 527.9 | 473 | 418.2 | 529.4 | 274.4 | 529.2 | 262.3 | 287.5 | 283.7 | 268.5 | 261.3 | 280.4 | 276.4 | 245.4
1053 | 832 | 470.9 | 188.36 | 220.182 | 277.8 | 254.2 | 269.7 | 272 | 412.1 | 52.5 | 19.7 | 92.8 | 3.5 | 273 | 1.7 | 178.9 | 190.6 | 520.1 | 706.4 | 286 | 330.1 | 591.5 | 756.2 | 704.3 | 423.2 | 421 | 520.8 | 473.5 | 416.5 | 525.2 | 274.7 | 528.5 | 262.4 | 287.5 | 283.5 | 268.6 | 261.5 | 280.6 | 276.3 | 245.6
1054 | 833 | 471 | 188.4 | 220.2287 | 278 | 253.4 | 270.2 | 271.5 | 409.1 | 52.4 | 19.7 | 92.8 | 4.2 | 268.6 | 1.6 | 179.2 | 190.8 | 514.1 | 707.5 | 286.2 | 330.4 | 581.7 | 751.4 | 703.6 | 424 | 419.1 | 514.4 | 474 | 413 | 523.2 | 274.9 | 527.5 | 262.5 | 287.4 | 283.4 | 268.6 | 261.7 | 281 | 276.4 | 245.9
1055 | 834 | 471.5 | 188.6 | 220.4625 | 278.3 | 253 | 270.5 | 271.2 | 405.7 | 52.5 | 19.7 | 92.8 | 4.5 | 263.4 | 1.6 | 179.5 | 191.1 | 509 | 705.2 | 286.5 | 331 | 573.3 | 743.6 | 701.5 | 424.8 | 415.3 | 515 | 474.5 | 410.4 | 517.6 | 275.1 | 526.8 | 262.6 | 287.4 | 283.2 | 268.5 | 261.9 | 280.8 | 276.4 | 246
1056 | 835 | 471.7 | 188.68 | 220.556 | 279.1 | 252.8 | 270.5 | 270.7 | 404.6 | 52.5 | 19.6 | 92.8 | 4.3 | 262.2 | 1.5 | 179.8 | 191.3 | 504.2 | 696.6 | 286.8 | 331.4 | 571.8 | 728.7 | 700.4 | 425.6 | 412.8 | 506.8 | 475.1 | 409.2 | 515.6 | 275.3 | 525.9 | 262.8 | 287.3 | 283 | 268.4 | 262 | 280.7 | 276.4 | 246.1
1057 | 836 | 471.4 | 188.56 | 220.4158 | 282.9 | 251.3 | 270.7 | 269.5 | 406.5 | 52.5 | 19.6 | 92.7 | 4.2 | 262.2 | 1.5 | 180.1 | 191.6 | 499.5 | 694.1 | 287.1 | 331.9 | 570 | 723.2 | 699.4 | 426.4 | 411.6 | 496.3 | 475.5 | 408 | 512.1 | 275.5 | 525 | 262.8 | 287.3 | 282.8 | 268.4 | 262.3 | 280.9 | 276.4 | 246.4
1058 | 837 | 471.4 | 188.56 | 220.4158 | 284.5 | 250.9 | 270.2 | 270.4 | 410.6 | 52.5 | 19.7 | 92.6 | 4.1 | 262.1 | 1.4 | 180.4 | 191.8 | 501.7 | 698.6 | 287.2 | 332.4 | 558.8 | 727.2 | 698.9 | 427.2 | 411.5 | 495 | 476.1 | 406 | 514.9 | 275.7 | 524.6 | 262.9 | 287.2 | 282.7 | 268.4 | 262.5 | 281.2 | 276.6 | 246.5
1059 | 838 | 471 | 188.4 | 220.2287 | 284.5 | 250.6 | 270.6 | 271.5 | 413 | 52.5 | 19.6 | 92.7 | 4.1 | 256.8 | 1.5 | 180.7 | 192.1 | 502.7 | 703.6 | 287.8 | 332.6 | 553.4 | 725.1 | 698.1 | 427.9 | 412.3 | 495.7 | 476.7 | 402.5 | 508.9 | 275.9 | 524.1 | 263.1 | 287.2 | 282.9 | 268.8 | 262.6 | 281.4 | 276.9 | 246.6
1060 | 839 | 472.2 | 188.88 | 220.7898 | 283.1 | 251.8 | 271.7 | 272.4 | 416.4 | 52.6 | 19.6 | 92.8 | 4.2 | 246.4 | 1.6 | 181.1 | 192.3 | 495.8 | 697.7 | 288.3 | 333 | 545.9 | 711.4 | 695.4 | 428.7 | 414.1 | 486.5 | 477.2 | 400.9 | 500.1 | 276.1 | 522.7 | 263.3 | 287.4 | 283.3 | 269.2 | 262.7 | 281.4 | 277.2 | 246.7
1061 | 840 | 471.3 | 188.52 | 220.369 | 281.9 | 252.5 | 273.7 | 272 | 420.2 | 52.7 | 19.6 | 92.8 | 4.4 | 238.4 | 1.7 | 181.4 | 192.6 | 486.5 | 683.4 | 288.4 | 333.5 | 528.8 | 674.7 | 691.4 | 429.5 | 413.6 | 479.8 | 477.7 | 399.4 | 492.5 | 276.3 | 521.5 | 263.5 | 287.8 | 284 | 269.5 | 262.8 | 281.3 | 277.4 | 246.8
1062 | 841 | 469.5 | 187.8 | 219.5274 | 281.2 | 252.3 | 275.3 | 270.9 | 421.2 | 52.7 | 19.6 | 92.8 | 4.1 | 236.8 | 1.8 | 181.7 | 192.9 | 477.8 | 673 | 288.6 | 334 | 514.7 | 651.9 | 688.7 | 430.3 | 415.2 | 473.5 | 478.3 | 396.1 | 486 | 276.5 | 520.3 | 263.7 | 288.5 | 284.8 | 269.9 | 262.9 | 281.2 | 277.7 | 246.8
1063 | 842 | 470.7 | 188.28 | 220.0885 | 281 | 253 | 277.1 | 271.2 | 421.7 | 52.8 | 19.6 | 92.7 | 4.2 | 239.2 | 1.8 | 182 | 193.1 | 473.5 | 672.7 | 288.9 | 334.4 | 509.9 | 652 | 687.8 | 431.1 | 417 | 469.1 | 478.9 | 399.1 | 478.7 | 276.7 | 519 | 263.9 | 289.2 | 285.3 | 270.2 | 263 | 281 | 277.9 | 246.9
1064 | 843 | 469.3 | 187.72 | 219.4339 | 280.8 | 254.3 | 278 | 271.5 | 426.6 | 52.9 | 19.6 | 92.7 | 5.1 | 243.3 | 1.9 | 182.3 | 193.4 | 471.2 | 682.9 | 288.9 | 335 | 500.5 | 654.3 | 685.8 | 431.9 | 424.4 | 473 | 479.5 | 399.7 | 474.3 | 276.9 | 518.1 | 264.2 | 290.1 | 285.9 | 270.6 | 263.1 | 280.8 | 278 | 246.9
1065 | 844 | 469.6 | 187.84 | 219.5741 | 280.5 | 254.9 | 279.2 | 271.7 | 433.8 | 52.9 | 19.6 | 92.7 | 4.7 | 246 | 1.9 | 182.6 | 193.6 | 477 | 695.9 | 289.3 | 335.4 | 492.5 | 644.5 | 684.7 | 432.7 | 435.5 | 489.7 | 480.2 | 401.7 | 479.3 | 277.1 | 518.3 | 264.6 | 290.9 | 287 | 271 | 263.2 | 281 | 278.2 | 247
1066 | 845 | 470 | 188 | 219.7612 | 280.8 | 255.7 | 280.2 | 272.5 | 445.1 | 52.9 | 19.6 | 92.6 | 4.7 | 246.4 | 2 | 182.9 | 193.9 | 479.3 | 704.3 | 289.7 | 335.6 | 490.8 | 662.8 | 685.8 | 433.4 | 438.4 | 507.1 | 480.7 | 402.5 | 483.5 | 277.3 | 519.3 | 265 | 291.3 | 287.7 | 271.3 | 263.3 | 281 | 278.3 | 247.1
1067 | 846 | 471.3 | 188.52 | 220.369 | 281 | 256.5 | 280.8 | 273.8 | 452.2 | 52.9 | 19.6 | 92.7 | 4.5 | 246.5 | 2.2 | 183.2 | 194.2 | 484.7 | 708 | 290.1 | 336 | 503.5 | 686.7 | 688.2 | 434.2 | 438 | 506.9 | 481.1 | 408.8 | 494.1 | 277.4 | 519.7 | 265.3 | 292.1 | 288.6 | 271.4 | 263.4 | 281.5 | 278.5 | 247.3
1068 | 847 | 471.4 | 188.56 | 220.4158 | 281.3 | 256.8 | 281.2 | 273.8 | 452.4 | 52.9 | 19.6 | 92.8 | 4.5 | 247 | 2.3 | 183.5 | 194.4 | 485.9 | 703 | 290.6 | 336.5 | 509.8 | 684.9 | 685.9 | 435 | 454 | 499.8 | 481.5 | 414.5 | 492.2 | 277.6 | 519 | 265.6 | 292.8 | 289.7 | 271.5 | 263.6 | 282.3 | 278.9 | 247.5
1069 | 848 | 470.6 | 188.24 | 220.0417 | 281.1 | 256.7 | 280.8 | 274.2 | 453.6 | 53 | 19.6 | 92.9 | 4.8 | 248.2 | 2.4 | 183.9 | 194.7 | 481.8 | 700.6 | 291 | 336.9 | 521.5 | 705.5 | 685.9 | 435.7 | 467.6 | 490.3 | 482 | 420.7 | 492.1 | 277.8 | 518.2 | 265.9 | 293.4 | 290.2 | 271.6 | 263.9 | 283.3 | 279.3 | 247.8
1070 | 849 | 470.9 | 188.36 | 220.182 | 280.5 | 256.8 | 281.3 | 275.4 | 455 | 53.1 | 19.6 | 92.9 | 4.7 | 253.7 | 2.5 | 184.2 | 195 | 479.9 | 696 | 291.4 | 337.4 | 529.3 | 721.6 | 686.9 | 436.5 | 478.5 | 484.3 | 482.4 | 422 | 498.8 | 278 | 518.4 | 266.2 | 293.7 | 290.4 | 271.6 | 264.1 | 283.9 | 279.8 | 248
1071 | 850 | 471.5 | 188.6 | 220.4625 | 281.1 | 257.3 | 281.1 | 276.6 | 453.4 | 53.1 | 19.6 | 92.9 | 5 | 255.6 | 2.5 | 184.5 | 195.2 | 479.3 | 692.3 | 291.4 | 337.8 | 531.7 | 728.4 | 688.4 | 437.3 | 481.5 | 480.5 | 482.9 | 424.1 | 501.4 | 278.1 | 518.6 | 266.5 | 293.9 | 290.5 | 271.4 | 264.4 | 284.7 | 280.4 | 248.2
1072 | 851 | 471.4 | 188.56 | 220.4158 | 280.1 | 257.5 | 280.6 | 278.4 | 451.1 | 53.1 | 19.6 | 93 | 4.6 | 256.2 | 2.6 | 184.8 | 195.5 | 481.5 | 691.6 | 291.6 | 338.2 | 541.1 | 729.2 | 688.7 | 438 | 474.7 | 477.9 | 483.5 | 421.5 | 500.6 | 278.3 | 518.4 | 266.8 | 294.2 | 290.5 | 271.4 | 264.8 | 285.6 | 281.2 | 248.7
1073 | 852 | 471.2 | 188.48 | 220.3223 | 280 | 257.9 | 279.7 | 278.6 | 448.5 | 53.1 | 19.6 | 93.2 | 4.8 | 257.9 | 2.6 | 185.1 | 195.8 | 488.9 | 688.1 | 291.9 | 338.7 | 546.5 | 724.3 | 687.3 | 438.8 | 468.5 | 476 | 484 | 418.6 | 499 | 278.5 | 517.9 | 267 | 294.4 | 290.5 | 271.6 | 265.1 | 286.1 | 281.8 | 249
1074 | 853 | 471.9 | 188.76 | 220.6496 | 280.7 | 258.8 | 279.1 | 278.2 | 444.4 | 53.1 | 19.6 | 93.4 | 4.6 | 260.6 | 2.6 | 185.4 | 196 | 491.3 | 689.4 | 292 | 339 | 551.8 | 737.2 | 688.2 | 439.6 | 460.9 | 471.5 | 484.4 | 416.7 | 497.3 | 278.7 | 517.2 | 267.2 | 294.4 | 290.4 | 271.6 | 265.5 | 286.6 | 282.4 | 249.2
1075 | 854 | 471.9 | 188.76 | 220.6496 | 282.5 | 259.2 | 278.9 | 278 | 440.7 | 53.1 | 19.6 | 93.5 | 4.7 | 260.5 | 2.6 | 185.7 | 196.3 | 495.8 | 691.7 | 292.2 | 339.3 | 560.7 | 756.7 | 689 | 440.3 | 456.4 | 470.5 | 484.9 | 419.9 | 506.3 | 278.8 | 517.5 | 267.5 | 294.4 | 290.2 | 271.5 | 265.8 | 287.1 | 282.8 | 249.4
1076 | 855 | 471.9 | 188.76 | 220.6496 | 283.7 | 258.4 | 278.3 | 277.3 | 441.6 | 53.1 | 19.6 | 93.5 | 4.7 | 254.8 | 2.5 | 186 | 196.6 | 497.6 | 690.7 | 292.8 | 339.7 | 568.8 | 750.5 | 688.4 | 441.1 | 452.1 | 464.8 | 485.4 | 418.9 | 502.2 | 279 | 517.3 | 267.7 | 294.5 | 290.5 | 271.6 | 266.1 | 287.4 | 283.2 | 249.7
1077 | 856 | 472.1 | 188.84 | 220.7431 | 283.6 | 258.1 | 277.1 | 276.8 | 439.1 | 53.1 | 19.6 | 93.5 | 4.2 | 250.6 | 2.3 | 186.3 | 196.8 | 504.9 | 694.1 | 293 | 339.9 | 571.9 | 764.2 | 687.7 | 441.9 | 446.8 | 462.6 | 485.9 | 417.8 | 505.4 | 279.2 | 517.1 | 267.9 | 294.6 | 290.6 | 271.9 | 266.5 | 287.8 | 283.5 | 250.1
1078 | 857 | 473.1 | 189.24 | 221.2107 | 283.7 | 258.1 | 276.4 | 276.6 | 434.2 | 53.2 | 19.6 | 93.5 | 4.5 | 253.2 | 2.2 | 186.7 | 197.1 | 509 | 698.8 | 293.4 | 340.3 | 576.2 | 772.5 | 688.9 | 442.7 | 444.8 | 466.5 | 486.4 | 416.9 | 507.9 | 279.4 | 517.1 | 268.1 | 294.6 | 290.5 | 272 | 266.7 | 287.8 | 283.8 | 250.2
1079 | 858 | 472.6 | 189.04 | 220.9769 | 285.1 | 257.6 | 277 | 276.9 | 433.4 | 53.1 | 19.6 | 93.6 | 4.8 | 259.8 | 2.2 | 187 | 197.3 | 503.2 | 696.4 | 293.8 | 340.4 | 569.7 | 754.4 | 686.7 | 443.5 | 442.9 | 464.3 | 486.9 | 416.1 | 506.9 | 279.6 | 516.9 | 268.3 | 294.5 | 290.4 | 272.1 | 266.9 | 287.9 | 284.3 | 250.2
1080 | 859 | 472.8 | 189.12 | 221.0704 | 286.6 | 256.9 | 277.7 | 276.9 | 433.3 | 53.1 | 19.6 | 93.6 | 4.7 | 263.6 | 2.2 | 187.3 | 197.6 | 496.2 | 701.9 | 294.3 | 340.6 | 561.7 | 744.3 | 686.6 | 444.3 | 438.4 | 459.6 | 487.4 | 412.4 | 500.1 | 279.7 | 516.2 | 268.5 | 294.4 | 290.3 | 272.2 | 267.1 | 287.5 | 284.7 | 250.3
1081 | 860 | 473 | 189.2 | 221.1639 | 288.2 | 257.2 | 278.1 | 276.4 | 429.5 | 53 | 19.6 | 93.6 | 4.7 | 263.6 | 2.1 | 187.6 | 197.9 | 489 | 701.3 | 294.5 | 341 | 557.9 | 743.7 | 687.3 | 445.2 | 434.9 | 466.3 | 487.8 | 409 | 496.1 | 279.9 | 515.2 | 268.6 | 294.5 | 290.4 | 272.3 | 267.3 | 287.2 | 285 | 250.4
1082 | 861 | 472 | 188.8 | 220.6963 | 290.4 | 257.5 | 278.5 | 275.9 | 431.3 | 53 | 19.6 | 93.7 | 4.6 | 263.3 | 2.1 | 187.9 | 198.1 | 482.6 | 701.4 | 294.8 | 341.4 | 551.5 | 742.7 | 684.1 | 446 | 433.4 | 466.2 | 488.2 | 406.1 | 490.6 | 280.1 | 514.7 | 268.8 | 294.7 | 290.7 | 272.7 | 267.4 | 286.9 | 285 | 250.5
1083 | 862 | 471.5 | 188.6 | 220.4625 | 292.7 | 257.4 | 279 | 275.7 | 434.1 | 52.9 | 19.6 | 93.8 | 4.8 | 263.3 | 2 | 188.2 | 198.4 | 481.3 | 705.2 | 295.1 | 341.8 | 543.8 | 736.4 | 683.2 | 446.9 | 430.3 | 471.2 | 488.7 | 405.7 | 495.7 | 280.3 | 514.4 | 269 | 295 | 290.9 | 273 | 267.6 | 286.6 | 285.2 | 250.5
1084 | 863 | 471.5 | 188.6 | 220.4625 | 295.3 | 257.6 | 279.7 | 275 | 438.6 | 53 | 19.6 | 93.8 | 4.9 | 263.1 | 2.2 | 188.5 | 198.6 | 489.4 | 712.9 | 295.2 | 342 | 537.6 | 746.2 | 684.1 | 447.8 | 427.4 | 476.1 | 489.1 | 405.7 | 500.1 | 280.5 | 514.7 | 269.2 | 295.5 | 291.3 | 273.2 | 267.7 | 286.6 | 285.4 | 250.7
1085 | 864 | 473.1 | 189.24 | 221.2107 | 297 | 257.6 | 281.3 | 275.6 | 438.2 | 53 | 19.6 | 93.8 | 5.4 | 262.6 | 2.3 | 188.8 | 198.9 | 502.1 | 713.3 | 295.5 | 342.3 | 538.4 | 754.6 | 684.6 | 448.7 | 425.5 | 477 | 489.6 | 405 | 504.2 | 280.7 | 515.4 | 269.5 | 296.2 | 291.6 | 273.2 | 268 | 287 | 285.5 | 250.9
1086 | 865 | 473.4 | 189.36 | 221.3509 | 296.7 | 258.4 | 282.7 | 276.6 | 434.5 | 53.1 | 19.6 | 94 | 5.7 | 261.2 | 2.4 | 189.1 | 199.2 | 505.9 | 716.9 | 295.9 | 342.6 | 530.3 | 751.1 | 683 | 449.7 | 423.3 | 481.3 | 490.1 | 402.7 | 503.3 | 280.9 | 515.6 | 269.7 | 296.5 | 291.6 | 273.2 | 268.2 | 287.1 | 285.5 | 251.1
1087 | 866 | 471.9 | 188.76 | 220.6496 | 295.5 | 260.3 | 282.7 | 277.1 | 433.5 | 53.1 | 19.6 | 94.2 | 5.2 | 260.9 | 2.5 | 189.4 | 199.4 | 502 | 713.5 | 296.2 | 343.2 | 525.1 | 739.1 | 681.8 | 450.8 | 422.7 | 483.2 | 490.6 | 399.9 | 501.6 | 281.1 | 515.6 | 269.9 | 296.6 | 291.7 | 273.3 | 268.3 | 287 | 285.6 | 251.2
1088 | 867 | 471.3 | 188.52 | 220.369 | 294.9 | 260.4 | 282.6 | 277.2 | 432.4 | 53.1 | 19.6 | 94.4 | 5 | 259.9 | 2.5 | 189.7 | 199.7 | 497.4 | 712.8 | 296.3 | 343.7 | 521 | 728.3 | 680.1 | 451.9 | 420.9 | 480.6 | 491.1 | 396.2 | 500.6 | 281.3 | 516.2 | 270.2 | 297.4 | 292.1 | 273.5 | 268.5 | 287.2 | 285.7 | 251.3
1089 | 868 | 471.1 | 188.44 | 220.2755 | 293.9 | 260.6 | 282.5 | 276.5 | 428.3 | 53 | 19.6 | 94.5 | 5.5 | 256.7 | 2.7 | 190 | 199.9 | 498.6 | 713.7 | 296.7 | 344.1 | 519.5 | 717.7 | 679.5 | 453.2 | 419.6 | 483.3 | 491.6 | 395.6 | 502.4 | 281.5 | 516.3 | 270.4 | 297.9 | 292.3 | 273.6 | 268.7 | 287.5 | 285.9 | 251.5
1090 | 869 | 471.8 | 188.72 | 220.6028 | 293.5 | 261.7 | 283.2 | 275.6 | 430.3 | 53 | 19.6 | 94.7 | 4.9 | 255.2 | 3.1 | 190.3 | 200.2 | 493.5 | 705.3 | 297.1 | 344.5 | 518 | 700.3 | 676.6 | 454.8 | 417.6 | 484.8 | 492.1 | 394.8 | 500.4 | 281.7 | 516 | 270.8 | 298.4 | 292.7 | 274 | 268.9 | 287.3 | 286 | 251.6
1091 | 870 | 472.1 | 188.84 | 220.7431 | 293.9 | 262.1 | 283.6 | 275.7 | 430.5 | 53 | 19.6 | 94.7 | 4.5 | 255.6 | 3.5 | 190.6 | 200.5 | 484.3 | 702.4 | 297.3 | 345 | 511.7 | 705.8 | 675.4 | 456.4 | 413.9 | 479.1 | 492.5 | 392.1 | 496.9 | 281.9 | 515.1 | 271 | 298.9 | 293.1 | 274.3 | 268.9 | 286.9 | 285.9 | 251.6
1092 | 871 | 472 | 188.8 | 220.6963 | 294.7 | 262.6 | 284.3 | 276.3 | 431.9 | 53.1 | 19.6 | 94.7 | 4.8 | 253.9 | 3.9 | 190.9 | 200.7 | 480.7 | 700.5 | 297.7 | 345.4 | 505.1 | 694.5 | 673.7 | 458.4 | 411.5 | 479.2 | 492.8 | 388.9 | 493.5 | 282.1 | 514.2 | 271.3 | 299.3 | 293.8 | 274.7 | 269 | 286.6 | 286 | 251.6
1093 | 872 | 472.4 | 188.96 | 220.8834 | 293.7 | 262.1 | 285.4 | 275.9 | 432.2 | 53.1 | 19.6 | 94.7 | 4.9 | 255.1 | 3.9 | 191.3 | 201 | 475.4 | 699.5 | 297.9 | 345.7 | 505.9 | 693.6 | 673.1 | 460.7 | 411.5 | 478.3 | 493.2 | 386.3 | 487.6 | 282.3 | 513.5 | 271.6 | 299.7 | 294.5 | 275.1 | 269.2 | 286.4 | 286.3 | 251.7
1094 | 873 | 471.3 | 188.52 | 220.369 | 293.5 | 262.1 | 286.7 | 276 | 435 | 53.1 | 19.6 | 94.7 | 4.7 | 251.9 | 3.9 | 191.5 | 201.2 | 475.5 | 699.7 | 298.4 | 346.1 | 512.3 | 690.4 | 672.1 | 462.9 | 412 | 475.5 | 493.6 | 387 | 483.8 | 282.5 | 512.8 | 271.9 | 300.3 | 295.1 | 275.4 | 269.3 | 286.3 | 286.5 | 251.9
1095 | 874 | 472.3 | 188.92 | 220.8366 | 292.5 | 263.2 | 288.1 | 276.9 | 436.9 | 53.2 | 19.6 | 94.7 | 4.5 | 248.9 | 3.8 | 191.9 | 201.5 | 475 | 703.6 | 298.6 | 346.5 | 517.8 | 691.9 | 672.6 | 465 | 410.8 | 474.7 | 494.1 | 387.9 | 483.8 | 282.7 | 512.1 | 272.2 | 300.5 | 295.4 | 275.5 | 269.4 | 286.3 | 286.5 | 252
1096 | 875 | 472.4 | 188.96 | 220.8834 | 290.3 | 263.9 | 288.9 | 277.3 | 438.4 | 53.1 | 19.6 | 94.7 | 4.8 | 248.7 | 3.6 | 192.2 | 201.7 | 477.9 | 706.1 | 298.6 | 347 | 525.2 | 707.8 | 673.7 | 467 | 409.2 | 472.1 | 494.4 | 388.6 | 482.4 | 282.9 | 511.3 | 272.4 | 300.6 | 295.5 | 275.7 | 269.6 | 286.8 | 286.4 | 252.2
1097 | 876 | 472.1 | 188.84 | 220.7431 | 290.3 | 263.8 | 289.1 | 278.1 | 438.5 | 53 | 19.6 | 94.8 | 4.2 | 250.5 | 3.4 | 192.5 | 202 | 483 | 711 | 298.8 | 347.4 | 534.1 | 716.9 | 673.8 | 468.8 | 409.9 | 483.4 | 494.7 | 390.4 | 483.6 | 283.1 | 511.1 | 272.7 | 300.6 | 295.8 | 275.8 | 269.8 | 287 | 286.5 | 252.3
1098 | 877 | 471.7 | 188.68 | 220.556 | 292.8 | 263.6 | 289.3 | 277.8 | 447.5 | 53 | 19.6 | 94.8 | 4.5 | 247.2 | 3.7 | 192.8 | 202.3 | 499.4 | 718.9 | 299.1 | 347.7 | 534 | 703.5 | 673.6 | 470.6 | 413.8 | 507 | 495 | 392.3 | 489.6 | 283.3 | 512.8 | 272.9 | 300.7 | 296.2 | 276.2 | 269.9 | 287 | 286.7 | 252.4
1099 | 878 | 472.6 | 189.04 | 220.9769 | 293.8 | 263.4 | 288.9 | 277.7 | 449.7 | 53.1 | 19.6 | 94.9 | 4.7 | 234.8 | 4.3 | 193 | 202.5 | 498.9 | 729.8 | 299.4 | 347.9 | 536.4 | 706.9 | 673.5 | 472.3 | 415.9 | 522.1 | 495.2 | 392.5 | 490.7 | 283.5 | 513.8 | 273.2 | 300.7 | 296.3 | 276.6 | 270 | 286.7 | 287 | 252.5
1100 | 879 | 473 | 189.2 | 221.1639 | 294.8 | 264 | 288.7 | 278.4 | 453.5 | 53.2 | 19.6 | 94.9 | 4.5 | 231.9 | 4.6 | 193.4 | 202.8 | 502.1 | 732.1 | 299.8 | 348.4 | 532.1 | 701 | 673.3 | 474 | 422.7 | 537 | 495.4 | 394.5 | 493.7 | 283.7 | 514.6 | 273.6 | 300.9 | 296.8 | 276.9 | 270.1 | 287.2 | 287.3 | 252.6
1101 | 880 | 472.7 | 189.08 | 221.0236 | 294.8 | 265.2 | 290.4 | 280.1 | 461.3 | 53.3 | 19.6 | 95 | 4.7 | 254.6 | 4.8 | 193.7 | 203 | 509.9 | 724.9 | 300 | 348.9 | 530.5 | 695.7 | 671.2 | 475.8 | 424.6 | 544.7 | 495.6 | 394.7 | 492.5 | 283.9 | 514.9 | 273.8 | 301.5 | 296.9 | 277.1 | 270.2 | 287.1 | 287.5 | 252.7
1102 | 881 | 472.5 | 189 | 220.9301 | 294.5 | 266.1 | 291.6 | 281.5 | 466.6 | 53.4 | 19.6 | 95.1 | 4.1 | 257.3 | 4.9 | 193.9 | 203.3 | 509.7 | 717.1 | 300.2 | 349.4 | 538.1 | 704.9 | 671.4 | 477.3 | 423.7 | 534.8 | 495.9 | 397.1 | 493.1 | 284.1 | 515 | 274.2 | 301.9 | 297.3 | 277.1 | 270.3 | 287.2 | 287.8 | 252.9
1103 | 882 | 472.7 | 189.08 | 221.0236 | 294 | 266.2 | 292 | 281.4 | 463.5 | 53.4 | 19.6 | 95.1 | 3.9 | 241.4 | 5.4 | 194.2 | 203.6 | 510.8 | 716.9 | 300.4 | 349.8 | 543.9 | 727.1 | 673.1 | 478.8 | 420.9 | 530.8 | 496.1 | 397.6 | 493.6 | 284.3 | 514.6 | 274.5 | 302.3 | 297.6 | 277 | 270.5 | 287.8 | 288 | 253.1
1104 | 883 | 472.5 | 189 | 220.9301 | 293.5 | 266 | 292 | 280.9 | 457.5 | 53.5 | 19.6 | 95.1 | 4.6 | 237.3 | 5.5 | 194.5 | 203.8 | 528.1 | 721 | 300.9 | 350.3 | 550.3 | 758.1 | 674.9 | 480.3 | 421.7 | 544.6 | 496.2 | 401.3 | 509.2 | 284.5 | 516.7 | 274.7 | 302.8 | 298.1 | 277 | 270.7 | 288.5 | 288.3 | 253.4
1105 | 884 | 472.2 | 188.88 | 220.7898 | 292.4 | 266.4 | 291.5 | 280.3 | 454.6 | 53.6 | 19.6 | 95.2 | 4.8 | 236.2 | 5.6 | 194.8 | 204.1 | 527.7 | 715.1 | 301.1 | 350.7 | 567.2 | 776.8 | 677 | 481.7 | 423.3 | 535.8 | 496.3 | 411.8 | 516.6 | 284.7 | 518.2 | 275 | 303.1 | 298.4 | 277.1 | 271 | 289.4 | 288.6 | 253.7
1106 | 885 | 473 | 189.2 | 221.1639 | 291.5 | 266.7 | 291 | 281.1 | 455.5 | 53.7 | 19.6 | 95.2 | 4.1 | 234.8 | 5.4 | 195.1 | 204.4 | 517.5 | 702.2 | 301.3 | 351.1 | 563.8 | 772.7 | 677.7 | 482.8 | 423.3 | 520.4 | 496.6 | 418.1 | 517.6 | 285 | 517.6 | 275.3 | 303.2 | 298.3 | 276.9 | 271.4 | 290.4 | 289 | 253.9
1107 | 886 | 472.5 | 189 | 220.9301 | 292 | 266.7 | 290.3 | 283.6 | 457.6 | 53.7 | 19.5 | 95.3 | 4.2 | 249.8 | 5.4 | 195.4 | 204.6 | 508.9 | 691.7 | 301.4 | 351.6 | 559.5 | 768.8 | 677.2 | 483.8 | 422.1 | 506.5 | 497.2 | 423.3 | 510.3 | 285.2 | 516.5 | 275.5 | 303.5 | 298.2 | 276.7 | 271.7 | 291.1 | 289.5 | 254.1
1108 | 887 | 473 | 189.2 | 221.1639 | 292 | 266.6 | 290.1 | 285.2 | 456.2 | 53.7 | 19.5 | 95.3 | 4 | 258.4 | 5.1 | 195.7 | 204.9 | 504.7 | 688.4 | 301.8 | 352.1 | 556.5 | 767.6 | 678.1 | 484.6 | 420 | 495.9 | 497.7 | 422.6 | 508.1 | 285.4 | 515.2 | 275.8 | 303.9 | 298.3 | 276.7 | 272.1 | 291.8 | 290.4 | 254.4
1109 | 888 | 472.8 | 189.12 | 221.0704 | 292.2 | 267 | 289.6 | 286.7 | 452.4 | 53.7 | 19.5 | 95.3 | 4.1 | 260.3 | 4.7 | 196 | 205.2 | 506.9 | 686.2 | 302.3 | 352.5 | 567.1 | 765.7 | 678 | 485.3 | 419.7 | 489.6 | 498.1 | 421.6 | 508.7 | 285.6 | 514.8 | 276 | 304 | 298.2 | 276.8 | 272.5 | 292.3 | 290.9 | 254.6
1110 | 889 | 472.9 | 189.16 | 221.1171 | 293.7 | 266.7 | 289.6 | 286.8 | 449.8 | 53.8 | 19.5 | 95.3 | 4.3 | 258 | 4.3 | 196.3 | 205.4 | 508 | 688.3 | 302.8 | 352.9 | 577.2 | 787.5 | 679.9 | 486 | 417.9 | 481.9 | 498.6 | 423.5 | 508.8 | 285.8 | 514.6 | 276.2 | 303.9 | 298 | 276.9 | 272.8 | 292.6 | 291.2 | 254.8
1111 | 890 | 472.8 | 189.12 | 221.0704 | 294.6 | 267 | 289.8 | 286.1 | 453.8 | 53.9 | 19.5 | 95.3 | 4.3 | 258 | 4.1 | 196.6 | 205.7 | 506.6 | 691.7 | 303.1 | 353.3 | 582.2 | 790.5 | 682 | 486.8 | 417.1 | 482.4 | 499.2 | 426 | 512 | 286 | 514.7 | 276.4 | 303.8 | 297.9 | 277 | 273.2 | 293.2 | 291.7 | 255.1
1112 | 891 | 472.4 | 188.96 | 220.8834 | 293.8 | 266.4 | 289.3 | 285.5 | 451.4 | 53.9 | 19.5 | 95.2 | 4 | 255.8 | 3.7 | 196.9 | 205.9 | 509.2 | 704.2 | 303.4 | 353.7 | 577.6 | 788.2 | 684.8 | 487.7 | 417.3 | 488.9 | 499.7 | 426.2 | 517.5 | 286.2 | 515.4 | 276.6 | 303.7 | 298 | 277.2 | 273.5 | 293.4 | 291.8 | 255.3
1113 | 892 | 472.9 | 189.16 | 221.1171 | 292.6 | 266.1 | 289.4 | 285.4 | 448.5 | 54 | 19.5 | 95.1 | 4.1 | 257.1 | 3.6 | 197.2 | 206.2 | 508.2 | 713.2 | 303.7 | 354.1 | 572.6 | 777.1 | 684.1 | 488.7 | 416.2 | 498.6 | 500.1 | 424.1 | 522.6 | 286.4 | 516.3 | 276.8 | 303.7 | 298.1 | 277.5 | 273.8 | 293.4 | 292 | 255.4
1114 | 893 | 470.1 | 188.04 | 219.8079 | 293 | 265.9 | 288.8 | 285.1 | 448.7 | 54.1 | 19.5 | 95.1 | 4.5 | 253 | 4 | 197.5 | 206.5 | 507.1 | 720.7 | 304 | 354.5 | 561.7 | 773.3 | 684.4 | 489.5 | 418.1 | 508.3 | 500.7 | 422.2 | 519.4 | 286.7 | 516.8 | 277 | 303.9 | 298.5 | 278 | 273.9 | 293.3 | 292.2 | 255.4
1115 | 894 | 469.8 | 187.92 | 219.6677 | 295.4 | 266.1 | 289.3 | 284.3 | 451.3 | 54.2 | 19.5 | 95.1 | 4.4 | 251.7 | 4.6 | 197.8 | 206.7 | 508 | 723.8 | 304.4 | 355 | 560.6 | 782 | 685.8 | 490.6 | 418.4 | 524 | 501.2 | 420.6 | 517.2 | 286.9 | 518 | 277.3 | 304.6 | 299.1 | 278.4 | 274.1 | 293.1 | 292.5 | 255.5
1116 | 895 | 471.2 | 188.48 | 220.3223 | 297.8 | 265.6 | 291.2 | 284.6 | 448.8 | 54.2 | 19.5 | 95 | 4.4 | 251.6 | 4.8 | 198.1 | 207 | 504.8 | 723 | 304.6 | 355.4 | 557.4 | 785.8 | 686.7 | 491.8 | 417 | 522.3 | 501.5 | 419.4 | 515.2 | 287.1 | 518.1 | 277.5 | 305.1 | 299.5 | 278.6 | 274.3 | 293 | 292.8 | 255.7
1117 | 896 | 472.7 | 189.08 | 221.0236 | 299.3 | 265.3 | 291.6 | 285.4 | 446.8 | 54.2 | 19.5 | 95 | 4.4 | 252.3 | 4.7 | 198.4 | 207.2 | 504.6 | 721.1 | 304.8 | 355.8 | 552.2 | 780.5 | 685.3 | 492.9 | 415.6 | 515.9 | 501.9 | 416.9 | 510.2 | 287.3 | 517.5 | 277.7 | 305.2 | 299.7 | 278.7 | 274.5 | 293 | 292.9 | 255.9
1118 | 897 | 471.2 | 188.48 | 220.3223 | 299.8 | 265.5 | 291.5 | 284.9 | 449.6 | 54.2 | 19.5 | 95 | 4.3 | 255.1 | 4.6 | 198.7 | 207.5 | 509.3 | 722.4 | 304.9 | 356.2 | 544.4 | 776.8 | 684 | 494 | 413.7 | 511.4 | 502.2 | 413.3 | 505.4 | 287.6 | 516.8 | 277.9 | 305.1 | 299.9 | 279 | 274.7 | 293.3 | 292.9 | 256
1119 | 898 | 471.8 | 188.72 | 220.6028 | 299.9 | 265.8 | 290.3 | 284.7 | 450.7 | 54.2 | 19.5 | 95.1 | 4.5 | 262.2 | 4.7 | 199 | 207.8 | 504.7 | 721.6 | 305.3 | 356.7 | 549.7 | 772.6 | 683.1 | 494.8 | 413.1 | 510.3 | 502.5 | 412.3 | 505.2 | 287.8 | 516.3 | 278.1 | 305.1 | 300 | 279.1 | 274.9 | 293.3 | 293.2 | 256.1
1120 | 899 | 471.7 | 188.68 | 220.556 | 301.6 | 265.6 | 289.7 | 284.2 | 449.5 | 54.2 | 19.5 | 95.3 | 4.7 | 272.9 | 4.7 | 199.3 | 208 | 503.8 | 719 | 305.6 | 357.1 | 549.2 | 774.4 | 686.1 | 495.9 | 412.4 | 512 | 502.8 | 413.8 | 509.7 | 288 | 516 | 278.3 | 305.3 | 299.9 | 279 | 275.1 | 293.4 | 293.5 | 256.3
1121 | 900 | 472 | 188.8 | 220.6963 | 302.7 | 265.7 | 289.2 | 284.4 | 451.2 | 54.1 | 19.5 | 95.4 | 4.7 | 272.6 | 4.8 | 199.6 | 208.3 | 504.1 | 709.9 | 305.8 | 357.6 | 559.3 | 791.1 | 686.4 | 496.9 | 411.5 | 503.6 | 503.2 | 420.5 | 514.6 | 288.2 | 516.5 | 278.5 | 305.1 | 299.7 | 278.9 | 275.4 | 294 | 294 | 256.6
1122 | 901 | 471.9 | 188.76 | 220.6496 | 301.9 | 266.4 | 288.6 | 284.7 | 449.8 | 54.2 | 19.5 | 95.6 | 4.6 | 262.8 | 5.4 | 199.8 | 208.6 | 505.7 | 715.2 | 306.2 | 358 | 559.7 | 803.7 | 689.7 | 498 | 411.6 | 506.8 | 503.6 | 419 | 512.9 | 288.5 | 516.2 | 278.6 | 304.7 | 299.2 | 278.9 | 275.7 | 294.3 | 294.6 | 256.8
1123 | 902 | 471.5 | 188.6 | 220.4625 | 299.8 | 267.4 | 288 | 285.5 | 449.7 | 54.3 | 19.5 | 95.7 | 4.7 | 283.5 | 5.3 | 200.1 | 208.8 | 502.4 | 717.5 | 306.5 | 358.4 | 556.8 | 781.4 | 687.9 | 499.3 | 413.9 | 512.9 | 504 | 418.5 | 515.3 | 288.7 | 516.2 | 278.7 | 304.6 | 299.1 | 279.1 | 275.9 | 294.9 | 295 | 257
1124 | 903 | 471.3 | 188.52 | 220.369 | 298.6 | 267.5 | 287.7 | 286.1 | 449.7 | 54.3 | 19.5 | 95.8 | 4.9 | 285.4 | 4.8 | 200.4 | 209.1 | 501.2 | 713.9 | 306.8 | 358.9 | 561.6 | 783.6 | 688.6 | 500.5 | 413.7 | 511.6 | 504.3 | 418.3 | 512.8 | 288.9 | 516.1 | 278.9 | 304.4 | 299 | 279.1 | 276.1 | 295.5 | 295.1 | 257.3
1125 | 904 | 471.6 | 188.64 | 220.5093 | 297.2 | 267.3 | 287.8 | 285.8 | 451.4 | 54.3 | 19.5 | 96 | 4.8 | 270 | 4.9 | 200.7 | 209.3 | 507 | 709 | 307 | 359.3 | 577.7 | 795.8 | 690.4 | 501.6 | 414.3 | 503.1 | 504.4 | 420.7 | 518.6 | 289.2 | 516.1 | 279 | 304.4 | 299.1 | 279 | 276.5 | 296.1 | 295.3 | 257.5
1126 | 905 | 472.4 | 188.96 | 220.8834 | 295.1 | 266.9 | 287.8 | 285.6 | 455.5 | 54.3 | 19.5 | 96.2 | 4.5 | 268.4 | 5.1 | 201 | 209.6 | 512.6 | 709.7 | 307.3 | 359.7 | 586.3 | 809.4 | 690.9 | 502.2 | 414.1 | 501.4 | 504.6 | 426.2 | 520 | 289.4 | 516.4 | 279.1 | 304.7 | 299.4 | 279.1 | 276.8 | 296.6 | 295.7 | 257.7
1127 | 906 | 473.3 | 189.32 | 221.3042 | 293.7 | 267 | 286.8 | 286.6 | 459.7 | 54.3 | 19.5 | 96.4 | 4.5 | 264.1 | 5.3 | 201.3 | 209.8 | 519.2 | 715.2 | 307.7 | 360.1 | 597.6 | 825.8 | 692 | 502.9 | 414.3 | 504.7 | 505 | 429.3 | 526.9 | 289.6 | 517.4 | 279.3 | 304.9 | 299.6 | 279.4 | 277.1 | 296.8 | 296.3 | 257.9
1128 | 907 | 473.4 | 189.36 | 221.3509 | 292.6 | 267 | 286.5 | 287.1 | 460.5 | 54.3 | 19.5 | 96.5 | 4.5 | 251.1 | 5.9 | 201.6 | 210.1 | 520.3 | 725 | 308 | 360.5 | 589.2 | 825.2 | 692.8 | 503.8 | 416.9 | 519 | 505.3 | 428.8 | 530.6 | 289.9 | 518.6 | 279.4 | 305 | 299.5 | 279.8 | 277.3 | 296.7 | 296.6 | 258
1129 | 908 | 472.4 | 188.96 | 220.8834 | 292 | 267.3 | 286.3 | 286.7 | 458 | 54.4 | 19.5 | 96.6 | 4.8 | 250.5 | 6.3 | 201.9 | 210.4 | 521.6 | 727.8 | 308.3 | 360.9 | 582.7 | 809.6 | 692.9 | 505 | 419.2 | 523.1 | 505.6 | 425.8 | 527.5 | 290.1 | 519 | 279.6 | 305.1 | 299.7 | 280 | 277.4 | 296.8 | 296.5 | 258.2
1130 | 909 | 471.7 | 188.68 | 220.556 | 291.3 | 267.8 | 287.3 | 285.4 | 468.2 | 54.5 | 19.5 | 96.7 | 4.8 | 248.6 | 6.2 | 202.2 | 210.6 | 520.3 | 730.4 | 308.6 | 361.3 | 568.9 | 777.2 | 690.2 | 506.1 | 422.1 | 530.7 | 505.8 | 421.8 | 520.3 | 290.4 | 518.6 | 279.8 | 305.2 | 300.4 | 280.6 | 277.6 | 296.6 | 296.3 | 258.2
1131 | 910 | 472.8 | 189.12 | 221.0704 | 290.8 | 268.6 | 288.8 | 285 | 480.8 | 54.5 | 19.5 | 96.8 | 4.8 | 244.4 | 6.3 | 202.5 | 210.9 | 523 | 725 | 309.2 | 361.7 | 566.5 | 748.7 | 686.4 | 507.1 | 426.2 | 537.6 | 505.8 | 420.5 | 519.8 | 290.6 | 518.8 | 280.2 | 305.6 | 301.2 | 281.3 | 277.8 | 296.2 | 296.3 | 258.3
1132 | 911 | 473.3 | 189.32 | 221.3042 | 291 | 269.1 | 291.3 | 284.7 | 488.9 | 54.6 | 19.5 | 96.8 | 4.9 | 247.3 | 6.4 | 202.7 | 211.1 | 518.5 | 720.4 | 309.4 | 362.2 | 564.5 | 719.9 | 683.8 | 508.1 | 430.2 | 541.9 | 506.2 | 419.6 | 519.5 | 290.8 | 519.1 | 280.6 | 306.4 | 302.2 | 281.8 | 277.9 | 296 | 296.5 | 258.4
1133 | 912 | 472.7 | 189.08 | 221.0236 | 291.8 | 269.5 | 294.4 | 286.1 | 494.2 | 54.6 | 19.5 | 96.7 | 4.3 | 246.5 | 6.4 | 203 | 211.4 | 514.3 | 720 | 309.8 | 362.6 | 556.1 | 695.3 | 680.5 | 509.4 | 430.8 | 543 | 506.7 | 417.3 | 512.3 | 291.1 | 518.8 | 281 | 307.6 | 303.2 | 282.3 | 278 | 295.8 | 296.9 | 258.5
1134 | 913 | 473.2 | 189.28 | 221.2574 | 292.3 | 270 | 296.8 | 287.3 | 496.8 | 54.6 | 19.5 | 96.7 | 4.3 | 238.9 | 6.2 | 203.3 | 211.7 | 516.2 | 720.5 | 310.2 | 363.1 | 554.6 | 693 | 679.7 | 510.7 | 429.9 | 546 | 507.1 | 415 | 506.4 | 291.3 | 519 | 281.4 | 308.3 | 303.8 | 282.7 | 278.1 | 295.7 | 297.1 | 258.6
1135 | 914 | 472.9 | 189.16 | 221.1171 | 294.2 | 270.6 | 298.3 | 287.4 | 496.9 | 54.6 | 19.5 | 96.6 | 4.7 | 234.2 | 5.8 | 203.6 | 211.9 | 524.6 | 716 | 310.4 | 363.5 | 553 | 690.4 | 678.5 | 511.7 | 430.1 | 544.3 | 507.5 | 415 | 504.6 | 291.6 | 518.4 | 281.7 | 308.8 | 304.3 | 282.8 | 278.3 | 296 | 297.1 | 258.9
1136 | 915 | 472.4 | 188.96 | 220.8834 | 295.2 | 270.9 | 298.8 | 286.2 | 502.3 | 54.6 | 19.5 | 96.7 | 4.4 | 238.6 | 5.1 | 203.9 | 212.2 | 521.1 | 715.1 | 310.7 | 363.8 | 545.4 | 687.5 | 677.5 | 512.7 | 430.8 | 543.1 | 507.7 | 414.9 | 506.6 | 291.8 | 518.5 | 282.1 | 309.2 | 304.7 | 283.1 | 278.4 | 296.1 | 297 | 259
1137 | 916 | 472.8 | 189.12 | 221.0704 | 296.6 | 271.5 | 298.8 | 286.2 | 502.2 | 54.6 | 19.5 | 96.7 | 5.3 | 246.8 | 4.4 | 204.2 | 212.4 | 521.6 | 716.7 | 311.1 | 364.3 | 542.7 | 689.3 | 676.7 | 513.7 | 430.5 | 540.6 | 507.7 | 415.3 | 506.8 | 292 | 518.8 | 282.5 | 309.6 | 305.2 | 283.5 | 278.5 | 296.1 | 297.1 | 259.1
1138 | 917 | 472.7 | 189.08 | 221.0236 | 298.2 | 271.9 | 299.8 | 286.6 | 505 | 54.6 | 19.5 | 96.7 | 4.8 | 249.3 | 3.8 | 204.5 | 212.7 | 514.2 | 710.7 | 311.6 | 364.8 | 530.5 | 673.9 | 674.5 | 514.4 | 427.4 | 530 | 508.1 | 411.5 | 502 | 292.3 | 518.1 | 282.8 | 309.9 | 305.4 | 283.8 | 278.5 | 295.9 | 297.2 | 259.3
1139 | 918 | 472.5 | 189 | 220.9301 | 300.3 | 273 | 300 | 287.8 | 503.5 | 54.7 | 19.5 | 96.7 | 4.9 | 242.7 | 3.2 | 204.7 | 212.9 | 508 | 697.2 | 312.1 | 365.3 | 518.3 | 642.7 | 670.9 | 515 | 425.5 | 527 | 508.4 | 407.3 | 494.9 | 292.5 | 517.5 | 283.1 | 310.7 | 306 | 284.1 | 278.6 | 295.5 | 297.3 | 259.3
1140 | 919 | 471.7 | 188.68 | 220.556 | 301.2 | 272.9 | 300.4 | 288.1 | 497.9 | 54.7 | 19.4 | 96.8 | 4.7 | 251.4 | 3.8 | 205 | 213.2 | 506.5 | 689.5 | 312.3 | 365.8 | 512.6 | 624.4 | 668.3 | 515.7 | 424.6 | 534.7 | 508.6 | 404.5 | 492.8 | 292.8 | 517.5 | 283.4 | 311.6 | 306.8 | 284.5 | 278.6 | 295.1 | 297.5 | 259.4
1141 | 920 | 473.2 | 189.28 | 221.2574 | 302 | 272.9 | 302.2 | 288.5 | 493.2 | 54.7 | 19.4 | 96.9 | 4.5 | 260.7 | 4.7 | 205.3 | 213.4 | 506.2 | 684.1 | 312.7 | 366.3 | 504.1 | 601 | 665.4 | 516.4 | 423.7 | 533 | 508.8 | 403.4 | 494.6 | 293 | 517.8 | 283.8 | 312.9 | 307.6 | 284.9 | 278.7 | 294.8 | 297.7 | 259.6
1142 | 921 | 471.6 | 188.64 | 220.5093 | 302.1 | 272.5 | 304.4 | 290.9 | 490.5 | 54.7 | 19.4 | 96.9 | 4.5 | 261.5 | 5.2 | 205.6 | 213.7 | 506.6 | 676.2 | 313.1 | 366.9 | 498.4 | 582.1 | 662 | 517.1 | 422.4 | 531.8 | 509.1 | 401.9 | 490.8 | 293.3 | 517.8 | 284.3 | 313.9 | 308.4 | 285.5 | 278.8 | 294.3 | 298 | 259.7
1143 | 922 | 472.3 | 188.92 | 220.8366 | 302.8 | 273.2 | 305.5 | 292.1 | 487.7 | 54.7 | 19.4 | 96.9 | 4.9 | 262.8 | 5.5 | 205.9 | 213.9 | 504.6 | 669.5 | 313.3 | 367.3 | 503.8 | 566.9 | 659.4 | 517.7 | 422.7 | 528.8 | 509.4 | 399.6 | 489.2 | 293.5 | 517.5 | 284.7 | 314.3 | 309.1 | 285.9 | 278.8 | 293.9 | 298.2 | 259.8
1144 | 923 | 471.9 | 188.76 | 220.6496 | 302.1 | 273.8 | 306.8 | 293.5 | 492.6 | 54.8 | 19.4 | 96.9 | 4 | 266.3 | 5 | 206.2 | 214.2 | 504.4 | 673.2 | 313.5 | 367.9 | 501.6 | 570.9 | 657.6 | 518.5 | 423.5 | 528.7 | 509.5 | 398.4 | 490.4 | 293.8 | 517.3 | 284.9 | 314.4 | 309.5 | 286 | 278.8 | 293.6 | 298.6 | 260
1145 | 924 | 472.3 | 188.92 | 220.8366 | 301.5 | 273.7 | 307.1 | 294.6 | 501.8 | 54.9 | 19.5 | 96.8 | 4.8 | 271.7 | 4.4 | 206.4 | 214.4 | 505.6 | 679.5 | 313.9 | 368.3 | 504.4 | 573.2 | 657.1 | 519.3 | 426.8 | 537.9 | 509.5 | 397.7 | 488.6 | 294.1 | 517.4 | 285.2 | 314.3 | 309.9 | 286.2 | 278.9 | 293.5 | 298.7 | 260.1
1146 | 925 | 473.8 | 189.52 | 221.538 | 301.6 | 273.9 | 307 | 294.7 | 507.5 | 54.9 | 19.5 | 96.8 | 4.5 | 271.1 | 4.4 | 206.7 | 214.7 | 509.9 | 688.6 | 314.1 | 368.7 | 510.8 | 581.2 | 656 | 519.9 | 425.3 | 542.4 | 509.6 | 396.9 | 488.7 | 294.3 | 517.3 | 285.5 | 314.4 | 310.1 | 286.4 | 278.9 | 293.4 | 298.7 | 260.2
1147 | 926 | 473.6 | 189.44 | 221.4444 | 301.9 | 274 | 306.2 | 294.1 | 505.8 | 55 | 19.4 | 96.8 | 5.5 | 262.8 | 4.9 | 207 | 215 | 526.3 | 694.1 | 314.5 | 369.2 | 524.5 | 611.6 | 656.9 | 520.4 | 426.7 | 549.7 | 509.7 | 399.5 | 495 | 294.6 | 517.7 | 285.8 | 314.7 | 310.3 | 286.6 | 279 | 293.2 | 298.9 | 260.3
1148 | 927 | 473.2 | 189.28 | 221.2574 | 303 | 274 | 305.1 | 293.6 | 504.2 | 55 | 19.4 | 96.9 | 5.1 | 259.7 | 5.1 | 207.3 | 215.2 | 523.3 | 693 | 315 | 369.7 | 523.4 | 604.1 | 655.3 | 521 | 428.5 | 548.3 | 510 | 400.4 | 493.8 | 294.8 | 517.5 | 286 | 315.1 | 310.5 | 286.8 | 279 | 292.9 | 298.8 | 260.4
1149 | 928 | 473.6 | 189.44 | 221.4444 | 302.9 | 273.8 | 305.3 | 292.5 | 506.8 | 55.1 | 19.4 | 96.9 | 3.6 | 259.7 | 4.7 | 207.6 | 215.5 | 514.9 | 690.4 | 315.2 | 370.3 | 516.6 | 587.6 | 652.4 | 521.6 | 430 | 543.2 | 510.2 | 400 | 488.6 | 295.1 | 516.9 | 286.3 | 315.3 | 310.7 | 287.2 | 279.1 | 292.7 | 298.6 | 260.5
1150 | 929 | 473.2 | 189.28 | 221.2574 | 302.9 | 273.9 | 306.6 | 292 | 511.9 | 55 | 19.4 | 96.8 | 3.9 | 281.5 | 4.1 | 207.8 | 215.7 | 511.9 | 689.6 | 315.7 | 370.9 | 515.4 | 573.8 | 649.6 | 522.2 | 430.3 | 541.2 | 510.4 | 398.7 | 483.2 | 295.4 | 516.4 | 286.7 | 315.8 | 310.7 | 287.5 | 279.1 | 292.5 | 298.5 | 260.6
1151 | 930 | 473.6 | 189.44 | 221.4444 | 303.6 | 273.7 | 308.2 | 291.7 | 515.3 | 55 | 19.4 | 96.9 | 4 | 265 | 4.1 | 208.1 | 216 | 509.8 | 681.8 | 316.2 | 371.5 | 512.6 | 553.9 | 646.8 | 522.6 | 431.3 | 537.4 | 510.5 | 397.9 | 485.1 | 295.6 | 516.5 | 287 | 316.2 | 310.9 | 287.7 | 279.1 | 292.7 | 298.9 | 260.7
1152 | 931 | 473.3 | 189.32 | 221.3042 | 305.2 | 273.5 | 309.6 | 291.8 | 512.3 | 55 | 19.4 | 97 | 3.6 | 244.5 | 4.4 | 208.4 | 216.3 | 503.4 | 673.7 | 316.6 | 372 | 505.2 | 543.8 | 643.7 | 522.8 | 430.2 | 526.2 | 510.6 | 397.7 | 480.3 | 295.9 | 515.5 | 287.3 | 316.6 | 311.2 | 288 | 279.1 | 293.5 | 299 | 260.9
1153 | 932 | 473.5 | 189.4 | 221.3977 | 305.3 | 273.7 | 311 | 292.2 | 510.9 | 55 | 19.4 | 97 | 4.2 | 260.4 | 4.8 | 208.7 | 216.5 | 496.7 | 666.5 | 317 | 372.6 | 502.2 | 528.5 | 641 | 523.1 | 428.8 | 520.7 | 510.7 | 396.6 | 476.3 | 296.2 | 514.4 | 287.6 | 317.3 | 311.7 | 288.4 | 279.2 | 294.2 | 299 | 261.2
1154 | 933 | 473.4 | 189.36 | 221.3509 | 305.9 | 273.8 | 313.5 | 292.3 | 508 | 54.9 | 19.4 | 97.1 | 4.8 | 263.1 | 5.6 | 209 | 216.8 | 492 | 670.7 | 317.3 | 373.2 | 500 | 547.2 | 641 | 523.4 | 427.5 | 519.1 | 510.7 | 396.1 | 475.5 | 296.4 | 513.6 | 287.9 | 318 | 312.3 | 288.8 | 279.2 | 294.7 | 298.9 | 261.4
1155 | 934 | 473.1 | 189.24 | 221.2107 | 305 | 274.3 | 315.4 | 293 | 509 | 54.9 | 19.4 | 97.1 | 4.9 | 258.5 | 5.4 | 209.2 | 217 | 491.3 | 680.1 | 317.6 | 373.7 | 493.8 | 553.1 | 641.2 | 523.8 | 427.7 | 526.5 | 510.8 | 395.2 | 471.9 | 296.7 | 513.3 | 288.2 | 318.4 | 313.1 | 289.3 | 279.3 | 295.3 | 298.9 | 261.5
1156 | 935 | 472.9 | 189.16 | 221.1171 | 305.5 | 274.5 | 316 | 293.8 | 508.1 | 54.8 | 19.4 | 97.1 | 5.1 | 263.9 | 5.5 | 209.5 | 217.3 | 492.1 | 682.8 | 318.1 | 374.2 | 495.3 | 581.1 | 640.8 | 524.3 | 426.7 | 524.3 | 510.7 | 394.1 | 467.7 | 297 | 513 | 288.5 | 319 | 313.8 | 289.9 | 279.4 | 295.9 | 299.1 | 261.7
1157 | 936 | 473.4 | 189.36 | 221.3509 | 306.2 | 274.4 | 314.7 | 294.1 | 499 | 54.8 | 19.4 | 97.1 | 5.2 | 266.1 | 5.8 | 209.8 | 217.5 | 491.5 | 679.7 | 318.5 | 374.8 | 502.5 | 610 | 641 | 524.8 | 423.8 | 513.9 | 510.2 | 395.3 | 468.9 | 297.2 | 512.2 | 288.7 | 319.1 | 313.7 | 289.7 | 279.5 | 296.9 | 299.5 | 261.9
1158 | 937 | 472.9 | 189.16 | 221.1171 | 307.4 | 275 | 313.1 | 293.9 | 493.2 | 54.8 | 19.4 | 97.1 | 5.3 | 269.6 | 5.7 | 210.1 | 217.8 | 490.5 | 689.3 | 319 | 375.4 | 500.4 | 644 | 643.1 | 525.5 | 422.3 | 517.3 | 509.9 | 395.3 | 469.3 | 297.5 | 511.6 | 288.8 | 319.1 | 313.8 | 289.4 | 279.6 | 297.7 | 300 | 262.1
1159 | 938 | 473.4 | 189.36 | 221.3509 | 308.1 | 275.4 | 310.4 | 292.8 | 488.6 | 54.8 | 19.4 | 97.2 | 5.1 | 265.8 | 5.7 | 210.3 | 218.1 | 492.3 | 691.3 | 319.5 | 376 | 504.3 | 674.9 | 645.5 | 526.1 | 421.1 | 513.9 | 509.9 | 396.6 | 474.2 | 297.8 | 511.8 | 288.9 | 319.2 | 313.9 | 289.4 | 279.8 | 297.7 | 300.3 | 262.2
1160 | 939 | 472.5 | 189 | 220.9301 | 310.3 | 275.7 | 309 | 292.7 | 485 | 54.9 | 19.4 | 97.3 | 4.8 | 259 | 5.5 | 210.6 | 218.3 | 487.6 | 696.7 | 319.9 | 376.6 | 511.1 | 690.3 | 646.3 | 526.6 | 419.6 | 511.2 | 509.9 | 396.7 | 474.6 | 298.1 | 511.3 | 289 | 319.4 | 313.9 | 289.5 | 279.9 | 298 | 300.4 | 262.4
1161 | 940 | 472.9 | 189.16 | 221.1171 | 309.7 | 276 | 307.4 | 291.5 | 482.9 | 54.9 | 19.4 | 97.3 | 4.8 | 249.1 | 5.5 | 210.9 | 218.6 | 488.5 | 705.1 | 320.2 | 377.2 | 505.6 | 691.8 | 645.9 | 527.2 | 419.1 | 513.8 | 509.7 | 396.9 | 476.3 | 298.3 | 510.5 | 289.1 | 319.2 | 313.9 | 289.7 | 280 | 298.5 | 300.3 | 262.6
1162 | 941 | 472.8 | 189.12 | 221.0704 | 309 | 275.5 | 306.2 | 290.2 | 480.4 | 54.9 | 19.4 | 97.4 | 4.4 | 235.4 | 5.9 | 211.2 | 218.9 | 494.2 | 711.8 | 320.6 | 377.9 | 512 | 702.2 | 647.4 | 527.7 | 418.1 | 513 | 509.8 | 397 | 481 | 298.6 | 510.3 | 289.2 | 318.8 | 313.5 | 289.6 | 280.1 | 298.9 | 300.1 | 262.7
1163 | 942 | 473.6 | 189.44 | 221.4444 | 308.4 | 275.7 | 305.1 | 290 | 478 | 54.9 | 19.4 | 97.5 | 5.1 | 235.2 | 6.5 | 211.5 | 219.1 | 492 | 718 | 320.9 | 378.5 | 510.3 | 719.8 | 648.7 | 528.2 | 418.3 | 516.3 | 509.2 | 396.9 | 479.6 | 298.9 | 509.9 | 289.3 | 318.4 | 313.1 | 289.6 | 280.2 | 298.9 | 300.1 | 262.8
1164 | 943 | 472.7 | 189.08 | 221.0236 | 307.3 | 276.1 | 304.7 | 290.3 | 478.1 | 55 | 19.4 | 97.5 | 4.9 | 251.2 | 6.8 | 211.8 | 219.4 | 490.3 | 721 | 321.3 | 379.1 | 508.6 | 729.2 | 651 | 528.6 | 418.1 | 521.4 | 508 | 397.5 | 480.1 | 299.2 | 509.5 | 289.4 | 317.9 | 312.7 | 289.7 | 280.3 | 298.5 | 300.1 | 262.9
1165 | 944 | 472.7 | 189.08 | 221.0236 | 306.8 | 276.2 | 303.9 | 289.8 | 477.7 | 55 | 19.4 | 97.7 | 4.9 | 241.4 | 6.7 | 212 | 219.7 | 494.1 | 725.1 | 321.5 | 379.7 | 525.2 | 747.4 | 652.8 | 528.9 | 417.9 | 529.8 | 507.9 | 398.9 | 481.1 | 299.4 | 509.1 | 289.4 | 317.6 | 312.4 | 289.7 | 280.4 | 298.4 | 300.3 | 263.1
1166 | 945 | 473.2 | 189.28 | 221.2574 | 306.9 | 276 | 303.2 | 290.1 | 476.8 | 55.1 | 19.4 | 97.8 | 5.2 | 254.5 | 6.5 | 212.3 | 219.9 | 493.8 | 716.3 | 321.9 | 380.2 | 532.9 | 742.8 | 653.4 | 529.1 | 416.7 | 521.7 | 507.4 | 400.4 | 483.4 | 299.7 | 508.6 | 289.5 | 317.4 | 311.9 | 289.5 | 280.6 | 299.2 | 300.5 | 263.4
1167 | 946 | 471.9 | 188.76 | 220.6496 | 306.8 | 275.8 | 303.6 | 290.1 | 473.8 | 55.1 | 19.4 | 97.9 | 4.9 | 273.1 | 5.8 | 212.6 | 220.2 | 491.3 | 712.9 | 322.4 | 380.8 | 543.5 | 745.4 | 654.6 | 529.3 | 415.5 | 513.9 | 507.1 | 402.4 | 487.2 | 300 | 508.5 | 289.5 | 316.9 | 311.5 | 289.2 | 280.8 | 299.9 | 300.5 | 263.6
1168 | 947 | 472 | 188.8 | 220.6963 | 306.7 | 275.3 | 302.7 | 290.4 | 469.5 | 55 | 19.4 | 98 | 4.6 | 253.9 | 6 | 212.9 | 220.5 | 495.1 | 705.7 | 322.7 | 381.3 | 543.2 | 726.3 | 653.1 | 529.6 | 414.9 | 508.5 | 506.7 | 403.9 | 485.8 | 300.3 | 508 | 289.5 | 316.5 | 311 | 289.1 | 281.1 | 300.1 | 300.5 | 263.8
1169 | 948 | 472.2 | 188.88 | 220.7898 | 307.1 | 274.2 | 301.2 | 291.4 | 467.4 | 55.1 | 19.4 | 98.1 | 5 | 248.1 | 6.6 | 213.1 | 220.7 | 491.5 | 707.6 | 323 | 381.8 | 537.8 | 714.9 | 651 | 529.9 | 414.6 | 506.4 | 506.8 | 403.2 | 484 | 300.6 | 507.3 | 289.5 | 316.3 | 310.7 | 289.2 | 281.2 | 300 | 300.3 | 263.9
1170 | 949 | 472.1 | 188.84 | 220.7431 | 307.4 | 273.3 | 299.8 | 291.7 | 467.9 | 55.1 | 19.4 | 98.1 | 4.8 | 256.3 | 7 | 213.4 | 221 | 497.2 | 708.5 | 323.5 | 382.3 | 549.5 | 722 | 650.7 | 530.2 | 414.1 | 503.3 | 507.2 | 404.5 | 484.7 | 300.9 | 507.2 | 289.5 | 316.1 | 310.3 | 289.1 | 281.4 | 300.4 | 300.1 | 264.1
1171 | 950 | 472.5 | 189 | 220.9301 | 307.3 | 273.2 | 298.8 | 291.1 | 469.2 | 55.1 | 19.4 | 98.2 | 4.7 | 249.3 | 7 | 213.7 | 221.3 | 493.7 | 709.6 | 323.9 | 382.7 | 549.2 | 738.2 | 651.7 | 530.6 | 412.5 | 501.2 | 507.6 | 406.5 | 489.6 | 301.2 | 507.3 | 289.5 | 316 | 310.1 | 289.2 | 281.6 | 301.2 | 300 | 264.4
1172 | 951 | 472.5 | 189 | 220.9301 | 307.3 | 272.6 | 298.3 | 290.8 | 466.8 | 55.2 | 19.4 | 98.2 | 4.6 | 253.7 | 7.4 | 213.9 | 221.5 | 492.1 | 704.7 | 324.3 | 383.2 | 549.4 | 735.9 | 654 | 530.9 | 409.5 | 496.3 | 507.7 | 409.4 | 491.4 | 301.5 | 507.3 | 289.5 | 315.9 | 309.8 | 289.2 | 281.9 | 301.6 | 300 | 264.5
1173 | 952 | 472.1 | 188.84 | 220.7431 | 307.5 | 273.1 | 297.4 | 291.6 | 464.3 | 55.2 | 19.4 | 98.3 | 5 | 247 | 7.4 | 214.2 | 221.8 | 486.7 | 697.8 | 324.9 | 383.6 | 542.2 | 720.3 | 650.3 | 531.1 | 406.9 | 486.3 | 507.4 | 410 | 491.1 | 301.7 | 506.7 | 289.5 | 316 | 309.6 | 289.3 | 282.1 | 301.8 | 300.1 | 264.6
1174 | 953 | 472.4 | 188.96 | 220.8834 | 307.5 | 273.5 | 297.1 | 292.1 | 461.2 | 55.3 | 19.4 | 98.4 | 4.1 | 237.8 | 7.4 | 214.5 | 222.1 | 480.5 | 698 | 325.3 | 384.1 | 543 | 720.4 | 650.7 | 531.6 | 404.2 | 485.8 | 507.1 | 408.4 | 489 | 302 | 506.1 | 289.5 | 315.8 | 309.3 | 289.6 | 282.3 | 301.6 | 300.4 | 264.7
1175 | 954 | 472.3 | 188.92 | 220.8366 | 306.3 | 273.2 | 297.1 | 292.2 | 453.8 | 55.3 | 19.4 | 98.4 | 4.3 | 238.2 | 7.5 | 214.8 | 222.3 | 478.7 | 706 | 325.4 | 384.5 | 538.7 | 720.2 | 651.4 | 532 | 403.5 | 492.4 | 507.3 | 407.2 | 489.1 | 302.3 | 505.5 | 289.5 | 315.4 | 309 | 289.8 | 282.4 | 302 | 300.5 | 265
1176 | 955 | 472.8 | 189.12 | 221.0704 | 306.4 | 272.9 | 296.7 | 290.9 | 449.5 | 55.3 | 19.4 | 98.5 | 4.7 | 248.3 | 7.8 | 215 | 222.6 | 481.7 | 712.6 | 325.8 | 384.9 | 536 | 717.8 | 652.1 | 532.6 | 403.6 | 497.8 | 507.5 | 407.2 | 493.5 | 302.6 | 505.8 | 289.5 | 314.8 | 308.5 | 289.9 | 282.6 | 302.5 | 300.5 | 265.2
1177 | 956 | 471.7 | 188.68 | 220.556 | 307.6 | 272.9 | 296.2 | 289.5 | 449.2 | 55.4 | 19.4 | 98.6 | 4.9 | 248.8 | 8.1 | 215.3 | 222.8 | 495.1 | 722.4 | 326.2 | 385.3 | 552.4 | 737.7 | 656.1 | 533.2 | 405.3 | 505 | 507.6 | 411.3 | 502 | 302.9 | 506.7 | 289.5 | 314.3 | 307.9 | 289.9 | 282.8 | 302.5 | 300.6 | 265.3
1178 | 957 | 472.8 | 189.12 | 221.0704 | 307.4 | 273.4 | 294.9 | 289.8 | 452.6 | 55.5 | 19.4 | 98.6 | 4.7 | 238.9 | 7.8 | 215.6 | 223.1 | 503.3 | 727.7 | 326.3 | 385.7 | 571.9 | 779.9 | 660.6 | 533.8 | 407.7 | 514.1 | 507.2 | 420 | 514.4 | 303.2 | 508.7 | 289.5 | 313.8 | 307.3 | 289.7 | 283.1 | 302.6 | 300.9 | 265.4
1179 | 958 | 473.7 | 189.48 | 221.4912 | 306.9 | 273 | 293.5 | 290.6 | 456.4 | 55.6 | 19.4 | 98.7 | 5.1 | 237.3 | 7.7 | 215.8 | 223.4 | 515.7 | 729.3 | 326.8 | 386.1 | 579.8 | 801.1 | 664.8 | 534.5 | 410.5 | 518.2 | 506.8 | 427.7 | 525.7 | 303.5 | 509.8 | 289.4 | 313.5 | 307.2 | 289.5 | 283.3 | 302.6 | 301.3 | 265.7
1180 | 959 | 472.1 | 188.84 | 220.7431 | 304.5 | 272.8 | 292 | 291.8 | 457.3 | 55.6 | 19.4 | 98.8 | 4.8 | 243 | 7.4 | 216.1 | 223.7 | 527.8 | 727.8 | 327.2 | 386.5 | 583.1 | 803.2 | 668.3 | 535 | 412.2 | 523.5 | 507.2 | 431.7 | 537.3 | 303.8 | 511 | 289.5 | 313.3 | 306.9 | 289.4 | 283.6 | 302.7 | 301.8 | 265.9
1181 | 960 | 472.7 | 189.08 | 221.0236 | 302.5 | 272.9 | 291 | 292.8 | 457.2 | 55.6 | 19.4 | 98.8 | 5.4 | 249.2 | 7.2 | 216.4 | 224 | 538.7 | 725.2 | 327.5 | 386.9 | 591.4 | 791.4 | 668.2 | 535.6 | 413.3 | 519.7 | 507.4 | 433.6 | 540.2 | 304.1 | 512.1 | 289.5 | 313 | 306.6 | 289.4 | 283.8 | 303 | 302.2 | 266.1
1182 | 961 | 473.8 | 189.52 | 221.538 | 301.3 | 273.2 | 290.2 | 293 | 452.5 | 55.7 | 19.4 | 98.8 | 5.2 | 255.5 | 6.8 | 216.6 | 224.2 | 536 | 719.1 | 328.1 | 387.3 | 583.4 | 780.7 | 667.6 | 536.2 | 412.5 | 516.6 | 507.5 | 430 | 537.7 | 304.4 | 512.8 | 289.5 | 312.7 | 306.3 | 289.4 | 284 | 302.7 | 302.2 | 266.2
1183 | 962 | 473.3 | 189.32 | 221.3042 | 300.3 | 272.4 | 289.5 | 292.2 | 447.3 | 55.7 | 19.4 | 98.9 | 5.6 | 239.7 | 6.2 | 216.9 | 224.5 | 524 | 706 | 328.3 | 387.8 | 578.7 | 766.5 | 664.9 | 536.7 | 411.1 | 504.2 | 507.7 | 426.7 | 530.8 | 304.7 | 511.6 | 289.5 | 312.3 | 306 | 289.4 | 284.1 | 302.3 | 302.1 | 266.2
1184 | 963 | 473.6 | 189.44 | 221.4444 | 302.1 | 272 | 290.1 | 291.1 | 445.3 | 55.7 | 19.4 | 98.9 | 5 | 250.5 | 5.7 | 217.2 | 224.7 | 512.1 | 699.7 | 328.4 | 388.2 | 574.6 | 767.6 | 665.3 | 535.7 | 409.2 | 492.7 | 507.3 | 425.8 | 525 | 305.1 | 510.8 | 289.5 | 312 | 305.5 | 289.4 | 284.2 | 301.8 | 301.8 | 266.3
1185 | 964 | 473.3 | 189.32 | 221.3042 | 303.8 | 271.7 | 289.8 | 289.8 | 440.7 | 55.7 | 19.4 | 98.9 | 5.3 | 259.2 | 5.7 | 217.5 | 225 | 506.3 | 707 | 328.9 | 388.6 | 567.1 | 766.4 | 667.6 | 534.8 | 409.3 | 494.8 | 507.3 | 421.8 | 520.7 | 305.4 | 510 | 289.5 | 311.7 | 305.3 | 289.7 | 284.3 | 301.4 | 301.3 | 266.4
1186 | 965 | 472.4 | 188.96 | 220.8834 | 305.5 | 271.8 | 289.3 | 289.2 | 439.6 | 55.8 | 19.4 | 98.8 | 5.2 | 264.9 | 6.1 | 217.7 | 225.3 | 503.1 | 711 | 329.1 | 389 | 564.9 | 734.2 | 665.8 | 534.7 | 410.3 | 503.1 | 507.6 | 417.8 | 517.3 | 305.7 | 510 | 289.5 | 312 | 305.5 | 290.2 | 284.4 | 300.7 | 300.9 | 266.4
1187 | 966 | 473 | 189.2 | 221.1639 | 307.3 | 272.4 | 290.3 | 288 | 444.3 | 55.8 | 19.4 | 98.8 | 4.6 | 262.8 | 6.4 | 218 | 225.5 | 510.2 | 710.8 | 329.4 | 389.4 | 573.8 | 732.4 | 664.8 | 534.7 | 412 | 514.6 | 508 | 415.2 | 514.3 | 306 | 509.5 | 289.7 | 312.6 | 306 | 290.9 | 284.4 | 300.4 | 300.6 | 266.5
1188 | 967 | 473.1 | 189.24 | 221.2107 | 307.7 | 273.6 | 290.6 | 287.3 | 452.2 | 55.9 | 19.3 | 98.9 | 4.5 | 267.7 | 6.9 | 218.3 | 225.8 | 516.4 | 712.7 | 329.8 | 389.8 | 566.9 | 726.2 | 665.1 | 534.9 | 412.5 | 519.9 | 508 | 411.9 | 514.3 | 306.3 | 509.4 | 290 | 312.8 | 306.1 | 291.1 | 284.4 | 299.9 | 300.5 | 266.5
1189 | 968 | 472.8 | 189.12 | 221.0704 | 307.3 | 274.6 | 290.4 | 286.8 | 456.5 | 55.9 | 19.3 | 99.1 | 5.2 | 262.3 | 7.5 | 218.5 | 226.1 | 524.3 | 719.9 | 330.3 | 390.2 | 577.1 | 728.3 | 667.5 | 535.3 | 414 | 539.4 | 507.2 | 413.3 | 523.7 | 306.6 | 510.8 | 290.2 | 312.7 | 306 | 290.9 | 284.5 | 299.6 | 300.4 | 266.6
1190 | 969 | 473 | 189.2 | 221.1639 | 305.7 | 274.7 | 290.2 | 285.7 | 455.1 | 55.8 | 19.3 | 99.3 | 4.9 | 256.1 | 8.1 | 218.8 | 226.4 | 529.2 | 724.4 | 330.9 | 390.7 | 578.4 | 731.2 | 668.3 | 535.8 | 415.3 | 549.3 | 507.7 | 414.6 | 531.4 | 306.9 | 512.5 | 290.3 | 312.7 | 305.8 | 290.7 | 284.6 | 299.3 | 301.4 | 266.8
1191 | 970 | 472.8 | 189.12 | 221.0704 | 303.2 | 274 | 288.9 | 285.8 | 451.2 | 55.8 | 19.3 | 99.4 | 4.8 | 252.9 | 8.3 | 219.1 | 226.6 | 531.3 | 730.9 | 331.3 | 391.1 | 571.2 | 727.3 | 668 | 536.4 | 417.4 | 553.2 | 508.4 | 414.6 | 535.7 | 307.2 | 513.9 | 290.4 | 312.7 | 305.7 | 290.7 | 284.6 | 298.9 | 301.4 | 266.8
1192 | 971 | 472.4 | 188.96 | 220.8834 | 302.8 | 273.6 | 288.8 | 286.7 | 449.5 | 55.8 | 19.3 | 99.4 | 4.8 | 252.7 | 7.7 | 219.3 | 226.9 | 540.9 | 732.9 | 331.7 | 391.4 | 564.5 | 717.9 | 668.1 | 537.1 | 419.6 | 559.6 | 508.8 | 413.2 | 542.6 | 307.5 | 515.8 | 290.5 | 312.6 | 305.3 | 290.7 | 284.6 | 298.5 | 301.2 | 266.9
1193 | 972 | 472.8 | 189.12 | 221.0704 | 303.6 | 273.1 | 290.2 | 286.5 | 450.5 | 55.9 | 19.3 | 99.5 | 5.1 | 240.9 | 7.2 | 219.6 | 227.2 | 552.8 | 742.7 | 332.1 | 391.8 | 560.2 | 723.1 | 670.1 | 537.8 | 426.1 | 572.7 | 508.4 | 414 | 548.9 | 307.8 | 517.9 | 290.6 | 312.4 | 305.2 | 290.9 | 284.7 | 298.1 | 300.9 | 267
1194 | 973 | 472.2 | 188.88 | 220.7898 | 303.8 | 273.2 | 291.3 | 286 | 455 | 55.9 | 19.3 | 99.5 | 4.6 | 230.7 | 6.7 | 219.9 | 227.4 | 552.1 | 743.8 | 332.4 | 392.2 | 552.3 | 699.7 | 669 | 538.8 | 428.5 | 574 | 507.6 | 415.1 | 549.8 | 308.2 | 518.9 | 290.8 | 312.5 | 305.3 | 291.2 | 284.7 | 297.8 | 300.7 | 267
1195 | 974 | 472.3 | 188.92 | 220.8366 | 304.9 | 273.6 | 292.7 | 285.1 | 463.7 | 56 | 19.3 | 99.5 | 4.8 | 246.5 | 5.8 | 220.2 | 227.7 | 541.7 | 740.6 | 332.8 | 392.6 | 545.9 | 667.5 | 664 | 539.8 | 431 | 574.3 | 508.1 | 414.1 | 544.4 | 308.5 | 519.2 | 291.1 | 313.1 | 306 | 291.7 | 284.7 | 297.5 | 300.5 | 267
1196 | 975 | 472.4 | 188.96 | 220.8834 | 305.8 | 274.2 | 294.7 | 283.2 | 479.3 | 56 | 19.3 | 99.3 | 4.6 | 238 | 5.6 | 220.4 | 228 | 542.6 | 741.9 | 333.3 | 393 | 530.8 | 649.3 | 663.4 | 540.7 | 433.8 | 581.1 | 508.1 | 412.3 | 536.3 | 308.8 | 519.3 | 291.5 | 314.2 | 307.1 | 292.5 | 284.7 | 297.4 | 300.6 | 267.1
1197 | 976 | 472.8 | 189.12 | 221.0704 | 306.8 | 275.6 | 298.3 | 283.3 | 490.1 | 56.1 | 19.3 | 99.2 | 4.4 | 248.5 | 6 | 220.7 | 228.2 | 540 | 743.1 | 333.7 | 393.3 | 520.3 | 641.6 | 663.5 | 541.7 | 439.4 | 588.3 | 508.7 | 410.1 | 531.5 | 309.1 | 519.4 | 291.9 | 315.2 | 308.3 | 292.8 | 284.7 | 297.4 | 300.8 | 267.2
1198 | 977 | 472.6 | 189.04 | 220.9769 | 307.8 | 277 | 300.8 | 284.9 | 498.8 | 56.1 | 19.3 | 99.1 | 4.7 | 240 | 6.7 | 221 | 228.5 | 545.7 | 745.3 | 334.2 | 393.7 | 520.6 | 660.8 | 664.2 | 542.7 | 442.8 | 597.3 | 509.5 | 410.5 | 532.2 | 309.4 | 519.8 | 292.3 | 316.3 | 309.1 | 293.2 | 284.7 | 297.5 | 301.4 | 267.3
1199 | 978 | 472.4 | 188.96 | 220.8834 | 306.7 | 277.9 | 302.5 | 285.3 | 496.8 | 56.1 | 19.3 | 99 | 4.8 | 236.3 | 7.6 | 221.3 | 228.8 | 555.4 | 750.2 | 334.7 | 394 | 526.8 | 688 | 667.9 | 543.6 | 446.5 | 612.8 | 509.6 | 411.5 | 536.3 | 309.8 | 521.7 | 292.7 | 316.8 | 309.8 | 293.2 | 284.8 | 297.4 | 301.5 | 267.4
1200 | 979 | 472.6 | 189.04 | 220.9769 | 305.4 | 278.7 | 303.5 | 286.9 | 497.5 | 56.1 | 19.3 | 98.7 | 5.8 | 233.5 | 7.9 | 221.5 | 229.1 | 565.2 | 754.4 | 335.1 | 394.4 | 526.9 | 705.7 | 671.3 | 544.6 | 451.6 | 625.7 | 508.6 | 414.8 | 543.6 | 310.1 | 524.1 | 292.9 | 317.5 | 310.5 | 293.4 | 284.8 | 297.8 | 301.6 | 267.6
1201 | 980 | 472.6 | 189.04 | 220.9769 | 304.4 | 279.4 | 303.5 | 287.4 | 501.7 | 56.1 | 19.3 | 98.5 | 4.6 | 242.9 | 7 | 221.8 | 229.3 | 567.9 | 756.4 | 335.6 | 394.7 | 535.7 | 687 | 672 | 545.6 | 464.2 | 647.4 | 508.9 | 418.9 | 550.2 | 310.4 | 526.8 | 293.2 | 318.1 | 311.2 | 293.8 | 284.9 | 298.1 | 301.5 | 267.7
1202 | 981 | 472.7 | 189.08 | 221.0236 | 304.4 | 281.2 | 303.4 | 286.7 | 513.4 | 56.1 | 19.3 | 98.3 | 5 | 238.2 | 5.9 | 222.1 | 229.6 | 567.4 | 752.1 | 336 | 395.1 | 536.5 | 664.4 | 669.7 | 546.6 | 475.1 | 656.8 | 508.8 | 421.7 | 552.3 | 310.7 | 528.6 | 293.5 | 318.5 | 311.9 | 294.3 | 284.9 | 298.5 | 301.6 | 267.8
1203 | 982 | 472.9 | 189.16 | 221.1171 | 304.4 | 282.2 | 304.6 | 286.7 | 518.5 | 56.1 | 19.3 | 98.2 | 5 | 246.2 | 5.9 | 222.4 | 229.9 | 567.8 | 748.9 | 336.5 | 395.5 | 535.6 | 650 | 668.2 | 547.5 | 476 | 656 | 508.8 | 421.5 | 549.2 | 311.1 | 529.2 | 293.9 | 319.4 | 312.7 | 294.7 | 284.9 | 298.5 | 301.9 | 267.9
1204 | 983 | 471.8 | 188.72 | 220.6028 | 304.8 | 283.6 | 305.7 | 286.9 | 516.7 | 56.1 | 19.3 | 98 | 5 | 234.8 | 6 | 222.6 | 230.1 | 562 | 744.2 | 336.8 | 395.8 | 534.7 | 651.9 | 668.1 | 548.3 | 476 | 639.7 | 509 | 420.6 | 542.9 | 311.4 | 529.4 | 294.2 | 320.3 | 313.3 | 295 | 284.9 | 298.4 | 302.1 | 267.9
1205 | 984 | 471.7 | 188.68 | 220.556 | 305.4 | 284.4 | 307.1 | 287.6 | 517 | 56.1 | 19.3 | 97.9 | 4.9 | 239.6 | 6.1 | 222.9 | 230.4 | 557.7 | 740.7 | 337.3 | 396.2 | 529.1 | 666.4 | 668 | 549 | 478.7 | 620.7 | 509.7 | 420.1 | 534.4 | 311.7 | 528.6 | 294.6 | 320.9 | 313.7 | 295.2 | 285 | 298.7 | 302.2 | 268.1
1206 | 985 | 471.6 | 188.64 | 220.5093 | 306.5 | 283.9 | 308.6 | 287.8 | 517.9 | 56.1 | 19.3 | 97.9 | 4.6 | 242.7 | 5.9 | 223.2 | 230.7 | 553.1 | 734 | 337.6 | 396.5 | 522.9 | 675.1 | 667.1 | 549.7 | 477.3 | 602.9 | 510.2 | 419.9 | 525.4 | 312 | 527.3 | 294.9 | 321.7 | 314.4 | 295.3 | 285 | 299.1 | 302.3 | 268.3
1207 | 986 | 472.4 | 188.96 | 220.8834 | 306.4 | 283.6 | 309.4 | 287.7 | 517.2 | 56.2 | 19.3 | 97.8 | 4.6 | 242.8 | 5.3 | 223.4 | 231 | 550.1 | 725.9 | 338 | 396.9 | 514.6 | 667.2 | 665.1 | 550.3 | 474.3 | 589.7 | 510.4 | 418.3 | 518 | 312.4 | 526.2 | 295.1 | 322.5 | 314.9 | 295.5 | 285.1 | 299.2 | 302.4 | 268.4
1208 | 987 | 473.8 | 189.52 | 221.538 | 303.9 | 283.6 | 309.6 | 287.7 | 516.2 | 56.2 | 19.3 | 97.8 | 4.7 | 243.4 | 5 | 223.7 | 231.2 | 539.5 | 720.5 | 338.3 | 397.2 | 513.6 | 671.5 | 665.4 | 550.8 | 470.3 | 572 | 510.1 | 416.6 | 511.8 | 312.7 | 525.2 | 295.4 | 322.7 | 315.1 | 295.4 | 285.2 | 299.5 | 302.6 | 268.6
1209 | 988 | 473.3 | 189.32 | 221.3042 | 302.1 | 283.4 | 309.6 | 288.2 | 509 | 56.2 | 19.3 | 97.8 | 4.9 | 243.7 | 5.3 | 224 | 231.5 | 529.1 | 720.3 | 338.7 | 397.5 | 508.6 | 674.6 | 664.7 | 551.3 | 468.9 | 558.4 | 510.1 | 415.8 | 509.7 | 313.1 | 524.5 | 295.6 | 323.1 | 315.3 | 295.4 | 285.3 | 299.7 | 302.8 | 268.7
1210 | 989 | 473.3 | 189.32 | 221.3042 | 301.7 | 284 | 308.4 | 289 | 500.8 | 56.2 | 19.3 | 98 | 5 | 243.5 | 5.5 | 224.3 | 231.8 | 519.3 | 712.9 | 339.1 | 397.8 | 509.4 | 686.8 | 664.9 | 551.6 | 463.4 | 545.9 | 510.4 | 414.2 | 507.4 | 313.4 | 523.4 | 295.7 | 323.4 | 315.2 | 295.5 | 285.4 | 299.8 | 302.9 | 268.8
1211 | 990 | 472.7 | 189.08 | 221.0236 | 301.9 | 283.8 | 307.3 | 289.8 | 490 | 56.2 | 19.3 | 98 | 4.9 | 244.4 | 5.7 | 224.5 | 232.1 | 514.9 | 709.4 | 339.4 | 398.1 | 524.3 | 712.7 | 667.3 | 551.9 | 458 | 541.5 | 509.9 | 415.2 | 511.9 | 313.8 | 523.4 | 295.7 | 323.3 | 314.8 | 295.3 | 285.5 | 300.4 | 303.2 | 269
1212 | 991 | 473.4 | 189.36 | 221.3509 | 302.4 | 283.1 | 305.5 | 289.8 | 483 | 56.3 | 19.3 | 98 | 4.8 | 245 | 5.6 | 224.8 | 232.3 | 512.5 | 702 | 339.8 | 398.4 | 529.1 | 737.8 | 668.7 | 552.1 | 451.9 | 530.9 | 510.5 | 418.5 | 509.8 | 314.1 | 522.8 | 295.7 | 323.2 | 314.4 | 295 | 285.7 | 300.9 | 303.4 | 269.3
1213 | 992 | 473.1 | 189.24 | 221.2107 | 302.8 | 282.8 | 303 | 290.4 | 473.3 | 56.3 | 19.3 | 98.1 | 5.1 | 246.2 | 5.6 | 225.1 | 232.6 | 513.8 | 704.6 | 340.1 | 398.7 | 538.3 | 746 | 669.1 | 552.4 | 449.1 | 528.3 | 510.9 | 418.7 | 510.4 | 314.5 | 522.3 | 295.7 | 323.1 | 314.2 | 295 | 285.9 | 301 | 303.7 | 269.4
1214 | 993 | 472.5 | 189 | 220.9301 | 302.1 | 282.3 | 301 | 290.5 | 464.9 | 56.4 | 19.3 | 98.2 | 4.4 | 243.3 | 5.4 | 225.4 | 232.9 | 513 | 706.5 | 340.5 | 398.9 | 538.5 | 744 | 669.1 | 552.7 | 446.1 | 521.5 | 510.3 | 418.5 | 511.4 | 314.8 | 522.4 | 295.8 | 322.9 | 314 | 295.1 | 286 | 301.1 | 303.8 | 269.6
1215 | 994 | 473.5 | 189.4 | 221.3977 | 302.6 | 281.3 | 299.9 | 290.2 | 459.7 | 56.4 | 19.3 | 98.2 | 4.2 | 253 | 5.2 | 225.6 | 233.1 | 502.5 | 711.5 | 340.8 | 399.2 | 540.5 | 754.6 | 668.5 | 552.9 | 442.3 | 510.9 | 510.7 | 425.5 | 510.5 | 315.2 | 521.5 | 295.7 | 322.5 | 313.4 | 295 | 286.2 | 301.4 | 304.1 | 269.9
1216 | 995 | 473.1 | 189.24 | 221.2107 | 304.8 | 280.2 | 299.3 | 289 | 458.5 | 56.4 | 19.3 | 98.2 | 3.7 | 261 | 4.9 | 225.9 | 233.4 | 497.8 | 709.6 | 341.1 | 399.4 | 548.2 | 756.8 | 668.7 | 553.2 | 440.9 | 504.5 | 510.8 | 427.4 | 513.3 | 315.5 | 521.1 | 295.6 | 322.2 | 312.9 | 294.9 | 286.3 | 301.6 | 304.1 | 270.1
1217 | 996 | 473 | 189.2 | 221.1639 | 307.3 | 279.6 | 298.6 | 288 | 457.9 | 56.5 | 19.3 | 98.2 | 4.3 | 251.9 | 4.5 | 226.2 | 233.7 | 491.4 | 708.5 | 341.5 | 399.6 | 547.9 | 750.8 | 668.7 | 553.4 | 438.7 | 495 | 511.2 | 425.8 | 510.4 | 315.9 | 520 | 295.6 | 321.8 | 312.5 | 295 | 286.5 | 301.5 | 304.1 | 270.1
1218 | 997 | 473.7 | 189.48 | 221.4912 | 308.6 | 278.7 | 298.1 | 288.5 | 458 | 56.6 | 19.3 | 98.2 | 4.3 | 245.6 | 4.7 | 226.4 | 233.9 | 487.3 | 712.3 | 341.8 | 399.8 | 554.5 | 753.1 | 667.7 | 553.8 | 435.2 | 488.8 | 511.4 | 426.1 | 509.3 | 316.3 | 519 | 295.5 | 321.4 | 312.2 | 294.9 | 286.6 | 301.4 | 303.9 | 270.2
1219 | 998 | 473.3 | 189.32 | 221.3042 | 308.7 | 278.1 | 297.2 | 288.8 | 455.4 | 56.7 | 19.3 | 98.2 | 4.3 | 237.8 | 5 | 226.7 | 234.2 | 483.2 | 708 | 342.2 | 400 | 547.8 | 734.4 | 667.9 | 554 | 431.2 | 485.7 | 511.4 | 423.7 | 503.4 | 316.6 | 518.5 | 295.4 | 321 | 312 | 294.9 | 286.7 | 301.2 | 303.9 | 270.3
1220 | 999 | 472.7 | 189.08 | 221.0236 | 308.6 | 278.2 | 295.9 | 289.4 | 449.4 | 56.8 | 19.3 | 98.2 | 4.5 | 231.4 | 5.3 | 227 | 234.4 | 477.9 | 699.6 | 342.6 | 400.2 | 538.8 | 717.3 | 667 | 554.3 | 427.2 | 479.7 | 511.4 | 418.8 | 498.7 | 317 | 517.7 | 295.4 | 320.7 | 311.8 | 295 | 286.9 | 301.1 | 303.9 | 270.4
1221 | 1000 | 472.8 | 189.12 | 221.0704 | 310 | 279 | 295.1 | 289.2 | 446.6 | 56.8 | 19.3 | 98.2 | 4.5 | 232.1 | 5.3 | 227.3 | 234.7 | 469.3 | 688.3 | 342.9 | 400.4 | 534 | 697.5 | 665.3 | 554.5 | 424 | 472.5 | 511 | 414.2 | 495.1 | 317.4 | 516.6 | 295.3 | 320.4 | 311.4 | 295 | 287 | 301.2 | 303.8 | 270.6
1222 | 1001 | 473.3 | 189.32 | 221.3042 | 311.9 | 278.6 | 293.6 | 288.9 | 441.5 | 56.8 | 19.3 | 98.2 | 4.7 | 233.3 | 5 | 227.5 | 234.9 | 459.6 | 677.2 | 343.3 | 400.6 | 523 | 684.1 | 661.9 | 554.6 | 421.7 | 463.4 | 511.2 | 412.2 | 489.4 | 317.7 | 515.2 | 295.3 | 320.1 | 310.9 | 294.9 | 287.2 | 301.3 | 303.9 | 270.7
1223 | 1002 | 473 | 189.2 | 221.1639 | 314.7 | 278.5 | 292.1 | 290 | 437.8 | 56.8 | 19.3 | 98.2 | 4.4 | 232.2 | 4.8 | 227.8 | 235.2 | 452 | 671.8 | 343.6 | 400.7 | 519.8 | 686.4 | 660.6 | 554.7 | 417.7 | 454.2 | 511.5 | 409.7 | 485.2 | 318.1 | 513.5 | 295.2 | 319.7 | 310.5 | 294.8 | 287.3 | 301.2 | 304 | 270.9
1224 | 1003 | 473.1 | 189.24 | 221.2107 | 315.1 | 280.9 | 291 | 290.6 | 435.7 | 56.8 | 19.3 | 98.2 | 4.3 | 236.7 | 4.8 | 228.1 | 235.5 | 445.7 | 674.1 | 344 | 400.9 | 509 | 671.7 | 659.3 | 554.9 | 414.6 | 449.7 | 511.7 | 406.4 | 482.5 | 318.5 | 512.4 | 295.1 | 319.3 | 310.1 | 294.8 | 287.5 | 301.1 | 304 | 271
1225 | 1004 | 473.2 | 189.28 | 221.2574 | 315.4 | 280.5 | 290 | 290.9 | 431.6 | 56.8 | 19.3 | 98.2 | 4.5 | 239.3 | 4.8 | 228.4 | 235.7 | 441.4 | 667.2 | 344.4 | 401 | 507.6 | 661.1 | 657.1 | 555 | 411.8 | 443 | 512 | 402.7 | 476.6 | 318.9 | 511 | 295.1 | 318.9 | 309.6 | 294.8 | 287.6 | 300.9 | 304.3 | 271.2
1226 | 1005 | 472.3 | 188.92 | 220.8366 | 315 | 279.7 | 289.2 | 291.4 | 427.7 | 56.8 | 19.3 | 98.2 | 4.7 | 240.3 | 5 | 228.6 | 236 | 443.1 | 669.4 | 344.8 | 401.1 | 504.2 | 660.7 | 655.4 | 555.4 | 411 | 448.3 | 512.5 | 401 | 478 | 319.2 | 510.3 | 295 | 318.3 | 309.2 | 294.8 | 287.7 | 300.8 | 304.4 | 271.3
1227 | 1006 | 472.9 | 189.16 | 221.1171 | 315.5 | 279 | 288.8 | 292.7 | 426.6 | 56.8 | 19.3 | 98.2 | 4.8 | 247.9 | 4.9 | 228.9 | 236.2 | 449.7 | 683.9 | 345.2 | 401.3 | 510 | 664.1 | 657.5 | 555.9 | 415.4 | 466.7 | 512.8 | 400.4 | 484.8 | 319.6 | 510.8 | 295 | 317.9 | 309.1 | 295.2 | 287.7 | 300.4 | 304.1 | 271.3
1228 | 1007 | 474.2 | 189.68 | 221.725 | 318.1 | 278.3 | 289.1 | 292.7 | 438.6 | 56.8 | 19.3 | 98.3 | 4.9 | 250.1 | 4.8 | 229.2 | 236.5 | 459 | 700.2 | 345.5 | 401.4 | 519.7 | 664.4 | 657.1 | 556.5 | 423.5 | 496.9 | 513 | 401.4 | 495.6 | 320 | 512.6 | 295.1 | 317.8 | 309.2 | 295.8 | 287.7 | 300 | 303.9 | 271.3
1229 | 1008 | 472.9 | 189.16 | 221.1171 | 318.7 | 276.9 | 290.3 | 291.5 | 455.2 | 56.7 | 19.3 | 98.5 | 4.7 | 249.4 | 4.7 | 229.4 | 236.8 | 483.1 | 720.4 | 345.9 | 401.5 | 535.4 | 686.6 | 659.3 | 557.2 | 437.1 | 538.6 | 512.8 | 405.6 | 502.3 | 320.4 | 515 | 295.3 | 318 | 309.8 | 296.1 | 287.7 | 299.6 | 303.8 | 271.4
1230 | 1009 | 473.2 | 189.28 | 221.2574 | 317.7 | 277.1 | 292 | 291.1 | 464.6 | 56.7 | 19.3 | 98.7 | 4.4 | 248.3 | 4.5 | 229.7 | 237.1 | 502.8 | 732 | 346.2 | 401.6 | 547 | 709.8 | 664.2 | 558 | 448.8 | 570.4 | 512.7 | 413 | 519.5 | 320.7 | 518.5 | 295.5 | 318.4 | 310.3 | 296.4 | 287.7 | 299.3 | 303.8 | 271.4
1231 | 1010 | 472.4 | 188.96 | 220.8834 | 315.6 | 277.2 | 293.9 | 291.7 | 468 | 56.7 | 19.3 | 98.8 | 3.8 | 242.8 | 4.5 | 230 | 237.3 | 538.8 | 740.8 | 346.6 | 401.7 | 576.8 | 708.1 | 667.3 | 558.8 | 459.7 | 599.3 | 512.7 | 420 | 541 | 321.1 | 522.4 | 295.7 | 318.7 | 311 | 296.7 | 287.7 | 299.3 | 303.6 | 271.5
1232 | 1011 | 472.5 | 189 | 220.9301 | 314.4 | 276.9 | 294.2 | 292.6 | 471.7 | 56.7 | 19.3 | 98.9 | 4.4 | 247.1 | 4.4 | 230.2 | 237.6 | 546.5 | 746.6 | 346.9 | 401.9 | 593.8 | 716.2 | 668.7 | 559.5 | 472.3 | 605.6 | 512.8 | 426.6 | 551.1 | 321.5 | 525 | 296 | 318.9 | 311.3 | 296.9 | 287.7 | 299 | 303.5 | 271.6
1233 | 1012 | 472.1 | 188.84 | 220.7431 | 312.2 | 276.8 | 294.9 | 292.9 | 467.8 | 56.8 | 19.3 | 98.9 | 4.8 | 245.9 | 4.3 | 230.5 | 237.9 | 543.7 | 744.6 | 347.2 | 402.1 | 583.4 | 729.3 | 669.3 | 560.2 | 469.3 | 610.5 | 512.9 | 425.9 | 552.9 | 321.9 | 526.2 | 296.1 | 319.1 | 311.3 | 296.9 | 287.7 | 299.3 | 303.5 | 271.8
1234 | 1013 | 471.8 | 188.72 | 220.6028 | 310.1 | 277.2 | 295 | 292 | 458.8 | 56.8 | 19.3 | 98.9 | 4.5 | 246.6 | 4.2 | 230.7 | 238.1 | 538 | 738.3 | 347.5 | 402.3 | 580.1 | 740.5 | 671.8 | 560.9 | 465.7 | 593.4 | 512.9 | 423.9 | 549.4 | 322.3 | 526.5 | 296.3 | 319.4 | 311.3 | 296.7 | 287.8 | 299.9 | 303.4 | 271.9
1235 | 1014 | 471.2 | 188.48 | 220.3223 | 309 | 277.4 | 294.8 | 291.3 | 451.9 | 56.9 | 19.3 | 98.8 | 4.7 | 250.6 | 4.3 | 231 | 238.4 | 532.4 | 736.2 | 347.9 | 402.5 | 570.9 | 732.9 | 671.7 | 561.7 | 462.2 | 587 | 513 | 420.6 | 536.1 | 322.7 | 525.5 | 296.3 | 319.5 | 311.1 | 296.8 | 287.8 | 299.9 | 303.1 | 272
1236 | 1015 | 471.9 | 188.76 | 220.6496 | 308 | 278.5 | 294.3 | 290.5 | 454.3 | 56.9 | 19.3 | 98.7 | 5.2 | 244.7 | 4.5 | 231.3 | 238.7 | 526.9 | 737.5 | 348.2 | 402.7 | 566.3 | 742.9 | 672.4 | 562.3 | 459.4 | 581.2 | 512.7 | 419 | 530.6 | 323.1 | 524.9 | 296.5 | 319.5 | 311 | 297 | 287.8 | 299.7 | 302.7 | 272
1237 | 1016 | 472.4 | 188.96 | 220.8834 | 307.1 | 278.3 | 294.2 | 288.9 | 453 | 56.9 | 19.3 | 98.6 | 4.7 | 242.4 | 4.4 | 231.5 | 238.9 | 524.4 | 742.2 | 348.5 | 402.9 | 559.9 | 745.4 | 672.6 | 563.1 | 454.7 | 576.8 | 512.8 | 418 | 528.3 | 323.5 | 525 | 296.7 | 319.5 | 311.1 | 297.2 | 287.8 | 299.3 | 302.3 | 272
1238 | 1017 | 472 | 188.8 | 220.6963 | 306.3 | 277.3 | 294.2 | 287.4 | 454.6 | 56.9 | 19.3 | 98.5 | 4.8 | 248.7 | 4.5 | 231.8 | 239.2 | 519.6 | 742.5 | 348.8 | 403.1 | 561.4 | 745.6 | 673.6 | 563.8 | 451.4 | 564.6 | 513.1 | 417.1 | 526.3 | 323.9 | 524.3 | 296.8 | 319.7 | 311.3 | 297.4 | 287.8 | 298.8 | 301.7 | 272.1
1239 | 1018 | 473.2 | 189.28 | 221.2574 | 305.4 | 276.9 | 293.6 | 286.7 | 451.4 | 56.9 | 19.3 | 98.5 | 4.6 | 247.5 | 4.7 | 232 | 239.5 | 513.8 | 740.5 | 349.1 | 403.4 | 551.8 | 756.9 | 674.8 | 564.4 | 446.6 | 555.6 | 512.9 | 417.1 | 526.7 | 324.3 | 523.8 | 296.8 | 319.9 | 310.9 | 297.2 | 287.8 | 298.3 | 301.3 | 272.2
1240 | 1019 | 473.4 | 189.36 | 221.3509 | 304.1 | 276.7 | 293 | 286.1 | 447 | 56.9 | 19.2 | 98.5 | 4.6 | 235.8 | 5.1 | 232.3 | 239.7 | 509.6 | 736.8 | 349.5 | 403.6 | 552.7 | 758 | 675.6 | 565.1 | 447 | 545.4 | 512.9 | 419.2 | 531.6 | 324.7 | 524 | 296.9 | 319.6 | 310.3 | 296.8 | 287.9 | 298.1 | 301 | 272.3
1241 | 1020 | 473.1 | 189.24 | 221.2107 | 304 | 276.2 | 293.1 | 285.7 | 443.1 | 56.9 | 19.2 | 98.5 | 4.9 | 234.4 | 5 | 232.5 | 240 | 505.1 | 735.3 | 349.7 | 403.8 | 546.1 | 753.8 | 673.5 | 565.6 | 447.9 | 541.1 | 512.5 | 419.5 | 533.6 | 325.1 | 523.8 | 296.9 | 319.2 | 310.2 | 296.7 | 287.9 | 297.8 | 300.8 | 272.3
1242 | 1021 | 473.1 | 189.24 | 221.2107 | 305.9 | 275.3 | 292 | 285.8 | 443.8 | 56.9 | 19.2 | 98.6 | 5 | 217.5 | 4.9 | 232.8 | 240.3 | 500.9 | 733.1 | 350 | 404 | 534.8 | 740.1 | 673.1 | 566 | 445.6 | 534 | 512.2 | 417.8 | 535.7 | 325.5 | 524.1 | 297 | 319 | 310 | 296.9 | 288 | 297.5 | 300.6 | 272.4
1243 | 1022 | 472.6 | 189.04 | 220.9769 | 307 | 274.3 | 291.6 | 285.7 | 439.5 | 56.9 | 19.2 | 98.6 | 4.4 | 211.4 | 5 | 233 | 240.6 | 501.4 | 736.1 | 350.2 | 404.2 | 538.6 | 751.5 | 674.1 | 566.5 | 441.3 | 526.4 | 512.3 | 416.2 | 531.1 | 325.9 | 523.6 | 297 | 319 | 309.8 | 296.9 | 288 | 297.3 | 300.3 | 272.5
1244 | 1023 | 473.9 | 189.56 | 221.5847 | 306.6 | 274.7 | 291.5 | 285.4 | 436 | 56.8 | 19.2 | 98.6 | 4.8 | 214 | 4.8 | 233.3 | 240.8 | 498.2 | 726.6 | 350.3 | 404.4 | 537.2 | 749.4 | 672.4 | 566.9 | 438.7 | 515.6 | 512.4 | 416.4 | 528.7 | 326.4 | 522.8 | 297 | 318.9 | 309.9 | 296.8 | 288 | 297.2 | 300 | 272.5
1245 | 1024 | 474.2 | 189.68 | 221.725 | 308 | 274.9 | 290.8 | 285.2 | 436 | 56.8 | 19.2 | 98.5 | 5.1 | 204.7 | 4.4 | 233.5 | 241.1 | 492.9 | 713.4 | 350.5 | 404.6 | 542.2 | 739 | 671.6 | 567.2 | 436.1 | 504 | 512.8 | 417.6 | 522.1 | 326.8 | 521.8 | 297 | 318.6 | 309.4 | 296.8 | 288.1 | 297.3 | 300.1 | 272.7
1246 | 1025 | 474.4 | 189.76 | 221.8185 | 309.6 | 275.9 | 290.5 | 285.4 | 435.6 | 56.8 | 19.2 | 98.4 | 5 | 196.8 | 4 | 233.8 | 241.4 | 484.7 | 703.3 | 350.8 | 404.8 | 540.5 | 724.9 | 670 | 567.4 | 431.3 | 490.4 | 512.8 | 415.8 | 519.2 | 327.2 | 520.6 | 297 | 318 | 308.7 | 296.5 | 288.3 | 297.2 | 300.3 | 272.7
1247 | 1026 | 474.4 | 189.76 | 221.8185 | 310.5 | 276.5 | 290.1 | 286 | 434 | 56.7 | 19.2 | 98.4 | 5.2 | 202.3 | 3.8 | 234.1 | 241.7 | 478.3 | 697.3 | 351 | 404.9 | 538.6 | 737 | 669.2 | 567.5 | 429.3 | 481 | 513.3 | 417.4 | 517.1 | 327.7 | 519.6 | 296.9 | 317.6 | 308.4 | 296.3 | 288.4 | 297.5 | 300.8 | 272.9
1248 | 1027 | 472.2 | 188.88 | 220.7898 | 310.7 | 276.8 | 289.2 | 286.3 | 436.9 | 56.8 | 19.2 | 98.3 | 5.2 | 221.1 | 3.5 | 234.3 | 241.9 | 471.4 | 691.4 | 351.2 | 405.1 | 526.4 | 717.6 | 667.3 | 567.6 | 428 | 473.5 | 513.7 | 417 | 514 | 328.1 | 518.9 | 296.8 | 317.3 | 308.1 | 296.3 | 288.7 | 297.9 | 301.3 | 273.1
1249 | 1028 | 472 | 188.8 | 220.6963 | 311.2 | 275.5 | 289 | 286.3 | 443.2 | 56.8 | 19.2 | 98.4 | 5 | 226.9 | 3.2 | 234.6 | 242.2 | 462.5 | 679.7 | 351.3 | 405.2 | 516.7 | 700.5 | 665.4 | 567.6 | 424.7 | 464.9 | 514.1 | 415.6 | 508.2 | 328.5 | 517.5 | 296.7 | 317 | 307.7 | 296.2 | 288.9 | 298.4 | 301.9 | 273.3
1250 | 1029 | 472.2 | 188.88 | 220.7898 | 311.8 | 274.9 | 288.7 | 287.1 | 448.4 | 56.8 | 19.2 | 98.4 | 4.7 | 208.3 | 2.9 | 234.8 | 242.5 | 460.5 | 676.2 | 351.6 | 405.4 | 507.9 | 687.4 | 662.9 | 567.7 | 422.5 | 457.9 | 513.8 | 413.7 | 504.9 | 329 | 516.3 | 296.7 | 316.8 | 307.3 | 296.2 | 289.1 | 299.1 | 302.4 | 273.4
1251 | 1030 | 472 | 188.8 | 220.6963 | 312.7 | 276.4 | 288.6 | 288.6 | 448.6 | 56.7 | 19.2 | 98.6 | 5.3 | 194.3 | 2.7 | 235.1 | 242.7 | 456 | 679.3 | 351.8 | 405.5 | 507.3 | 682.6 | 661.2 | 567.7 | 421.4 | 452.5 | 513.6 | 412.2 | 503.9 | 329.4 | 515.3 | 296.6 | 316.5 | 307.2 | 296.1 | 289.3 | 299.7 | 303.1 | 273.7
1252 | 1031 | 471.4 | 188.56 | 220.4158 | 312.9 | 277 | 288.6 | 290.4 | 444.9 | 56.7 | 19.2 | 98.7 | 5.2 | 214.9 | 2.5 | 235.3 | 243 | 457.2 | 670.4 | 352 | 405.7 | 511.2 | 684.3 | 661.3 | 567.6 | 418.9 | 445.2 | 514 | 413 | 500.1 | 329.9 | 514.1 | 296.5 | 316.3 | 306.9 | 296.1 | 289.7 | 300.5 | 304 | 273.9
1253 | 1032 | 471.9 | 188.76 | 220.6496 | 313.2 | 276.9 | 288.4 | 292.4 | 444.9 | 56.7 | 19.2 | 98.9 | 4.5 | 247.1 | 2.9 | 235.6 | 243.3 | 452.8 | 653.9 | 352.2 | 405.8 | 515.3 | 675.6 | 657.9 | 567.5 | 417.2 | 440.4 | 514.4 | 413.4 | 496.9 | 330.3 | 512.7 | 296.5 | 316.1 | 306.7 | 296 | 290.1 | 301.7 | 305.4 | 274.2
1254 | 1033 | 472.6 | 189.04 | 220.9769 | 314.4 | 277 | 288.2 | 295.2 | 444.6 | 56.8 | 19.2 | 99.1 | 5.3 | 259.4 | 3.3 | 235.9 | 243.5 | 445.1 | 635.7 | 352.5 | 405.9 | 508.8 | 655.6 | 654.1 | 567.3 | 415.1 | 433.5 | 514.8 | 412.4 | 491 | 330.8 | 511.3 | 296.5 | 316.2 | 306.7 | 296 | 290.5 | 302.9 | 306.6 | 274.5
1255 | 1034 | 473.3 | 189.32 | 221.3042 | 316.4 | 276.8 | 287.9 | 297.9 | 446.7 | 56.8 | 19.2 | 99.3 | 5.5 | 251.2 | 3.8 | 236.1 | 243.8 | 444.4 | 627.1 | 352.8 | 406 | 509.5 | 650.9 | 651.6 | 567 | 413 | 429.1 | 514.7 | 417.4 | 487.3 | 331.2 | 509.9 | 296.5 | 316.1 | 306.5 | 296.1 | 290.9 | 304 | 307.6 | 274.8
1256 | 1035 | 472.8 | 189.12 | 221.0704 | 315.1 | 277.2 | 288.5 | 300.8 | 447.7 | 56.8 | 19.2 | 99.4 | 4.8 | 247.4 | 4.2 | 236.4 | 244 | 449.7 | 620.4 | 353 | 406.1 | 511.2 | 650.8 | 650.3 | 566.7 | 413 | 423.4 | 515 | 432.6 | 481 | 331.7 | 508.7 | 296.5 | 316.1 | 306.5 | 296.1 | 291.3 | 304.9 | 308.9 | 275
1257 | 1036 | 471.4 | 188.56 | 220.4158 | 313.3 | 277.6 | 290.8 | 302.9 | 451.7 | 56.8 | 19.2 | 99.5 | 5.3 | 248.3 | 4.4 | 236.6 | 244.3 | 452.2 | 629.2 | 353.2 | 406.2 | 529.3 | 671 | 651.2 | 566.2 | 414.2 | 419.2 | 515.2 | 441 | 482.2 | 332.2 | 507.9 | 296.5 | 316.1 | 306.4 | 296 | 291.6 | 305.4 | 309.6 | 275.2
1258 | 1037 | 472.2 | 188.88 | 220.7898 | 312.1 | 278.5 | 291.8 | 303.6 | 454.1 | 56.8 | 19.2 | 99.6 | 5.4 | 244.8 | 4.5 | 236.9 | 244.5 | 462.7 | 648.4 | 353.5 | 406.3 | 542.4 | 690.4 | 654.4 | 565.8 | 416.1 | 428.8 | 514.9 | 447.3 | 490.4 | 332.7 | 508.1 | 296.5 | 316.1 | 306.5 | 296.1 | 291.9 | 306.2 | 310.4 | 275.4
1259 | 1038 | 473.8 | 189.52 | 221.538 | 312 | 278 | 292.2 | 304.6 | 460.4 | 56.7 | 19.2 | 99.6 | 4.7 | 245.8 | 4.7 | 237.1 | 244.8 | 468.2 | 663.5 | 353.7 | 406.4 | 543.5 | 702.5 | 654.3 | 565.6 | 416.7 | 440.6 | 514.5 | 448 | 497.1 | 333.1 | 508.4 | 296.6 | 316.2 | 306.8 | 296.2 | 292.2 | 306.8 | 310.7 | 275.6
1260 | 1039 | 473.3 | 189.32 | 221.3042 | 311.1 | 277.5 | 291.5 | 305.1 | 460 | 56.7 | 19.2 | 99.6 | 4.8 | 245.5 | 4.9 | 237.4 | 245 | 468.7 | 662.8 | 354 | 406.5 | 542 | 714.1 | 654.8 | 565.5 | 417 | 436.8 | 515.1 | 447.4 | 499.9 | 333.6 | 508.2 | 296.7 | 316.3 | 307 | 296.4 | 292.5 | 307.8 | 310.7 | 275.9
1261 | 1040 | 472.9 | 189.16 | 221.1171 | 310.4 | 277.6 | 291.6 | 304.5 | 462.1 | 56.7 | 19.2 | 99.6 | 4.9 | 245.6 | 4.9 | 237.6 | 245.2 | 464.4 | 654.8 | 354.3 | 406.7 | 539.6 | 702.3 | 653.5 | 565.2 | 417.8 | 430.3 | 515.5 | 447.4 | 500 | 334.1 | 507.5 | 296.7 | 316.2 | 307 | 296.4 | 292.9 | 308.4 | 310.8 | 276
1262 | 1041 | 473.2 | 189.28 | 221.2574 | 309 | 277.1 | 292.1 | 303.9 | 463.9 | 56.7 | 19.2 | 99.6 | 4.9 | 243.5 | 4.8 | 237.9 | 245.5 | 461.3 | 659 | 354.5 | 406.8 | 534.7 | 715.8 | 654.5 | 565 | 417.4 | 427.7 | 515.7 | 444.4 | 496.2 | 334.6 | 506.8 | 296.8 | 316.3 | 307 | 296.4 | 293.2 | 308.8 | 311.1 | 276.3
1263 | 1042 | 473.6 | 189.44 | 221.4444 | 308.4 | 277.4 | 292.4 | 302.9 | 459 | 56.7 | 19.2 | 99.7 | 5.1 | 239.8 | 4.9 | 238.2 | 245.7 | 481.5 | 681.3 | 354.8 | 407 | 549.3 | 750.5 | 658.5 | 564.9 | 424.7 | 438 | 516.1 | 446.2 | 509.8 | 335.1 | 508 | 296.8 | 316.3 | 307.1 | 296.5 | 293.5 | 309.2 | 311.2 | 276.5
1264 | 1043 | 471 | 188.4 | 220.2287 | 308.5 | 278.3 | 292.4 | 301.5 | 458 | 56.8 | 19.2 | 99.8 | 4.6 | 236.9 | 5.2 | 238.4 | 245.9 | 513.7 | 682.8 | 355 | 407.1 | 575 | 763 | 659.1 | 564.9 | 432.3 | 438.9 | 516.6 | 453.4 | 518.3 | 335.5 | 509 | 296.8 | 316.2 | 307.1 | 296.6 | 293.8 | 309.6 | 311.3 | 276.7
1265 | 1044 | 471.5 | 188.6 | 220.4625 | 308.3 | 278.5 | 292 | 302.7 | 465.8 | 56.9 | 19.2 | 99.8 | 4.7 | 231.1 | 4.9 | 238.7 | 246.2 | 509.3 | 674.7 | 355.3 | 407.3 | 580.5 | 773.2 | 660.3 | 564.8 | 433.2 | 438.6 | 517 | 467.6 | 528.5 | 336 | 509.7 | 296.8 | 316.1 | 307 | 296.6 | 294.1 | 309.8 | 311.4 | 276.9
1266 | 1045 | 473 | 189.2 | 221.1639 | 309 | 278.9 | 292 | 302.9 | 472.4 | 56.9 | 19.2 | 99.9 | 5.2 | 226.5 | 4.5 | 238.9 | 246.4 | 504.3 | 674.9 | 355.6 | 407.5 | 576.9 | 770.6 | 660.8 | 564.7 | 433.3 | 436.9 | 517.2 | 469.9 | 529.7 | 336.5 | 510.3 | 296.8 | 315.9 | 306.9 | 296.6 | 294.3 | 309.9 | 311.7 | 277
1267 | 1046 | 472.8 | 189.12 | 221.0704 | 308 | 279.4 | 291.1 | 303.1 | 469.7 | 56.8 | 19.2 | 100 | 5.1 | 253.5 | 4.1 | 239.2 | 246.6 | 499.2 | 677.1 | 355.9 | 407.7 | 576.6 | 781.2 | 662.2 | 564.6 | 430.9 | 437.6 | 517.3 | 469.7 | 527.7 | 337 | 510 | 296.8 | 315.6 | 306.6 | 296.6 | 294.6 | 310.1 | 312.2 | 277.2
1268 | 1047 | 473.3 | 189.32 | 221.3042 | 307.3 | 280 | 290.4 | 302.6 | 468.2 | 56.7 | 19.2 | 100.1 | 4.9 | 260.5 | 3.8 | 239.4 | 246.8 | 502.7 | 691.2 | 356.2 | 407.9 | 589 | 796.6 | 663.8 | 564.6 | 430.4 | 451.7 | 517.3 | 468.7 | 530.6 | 337.5 | 510.3 | 296.9 | 315.7 | 306.5 | 296.8 | 294.8 | 310.5 | 312.5 | 277.3
1269 | 1048 | 472 | 188.8 | 220.6963 | 307.9 | 281.9 | 290.2 | 302.3 | 469.6 | 56.7 | 19.2 | 100.2 | 5 | 221.6 | 4.5 | 239.7 | 247 | 499 | 688.7 | 356.5 | 408 | 589.3 | 800.1 | 663.6 | 564.6 | 431.6 | 449.4 | 517.4 | 469.2 | 531.3 | 338 | 510.5 | 296.9 | 315.7 | 306.6 | 297 | 295.1 | 310.6 | 312.9 | 277.5
1270 | 1049 | 472.1 | 188.84 | 220.7431 | 307.2 | 282.4 | 291.1 | 302.2 | 470.3 | 56.6 | 19.2 | 100.2 | 4.9 | 228.4 | 5.5 | 239.9 | 247.3 | 494.3 | 683.6 | 356.8 | 408.2 | 590.9 | 787.1 | 662.3 | 564.6 | 433 | 445.4 | 517.7 | 473.4 | 528.9 | 338.5 | 510.5 | 296.9 | 315.8 | 306.7 | 296.9 | 295.3 | 310.8 | 312.8 | 277.6
1271 | 1050 | 471.6 | 188.64 | 220.5093 | 307.1 | 281.8 | 291.2 | 302 | 471.6 | 56.7 | 19.2 | 100.2 | 5.2 | 200.6 | 5.2 | 240.2 | 247.5 | 486 | 685.2 | 356.9 | 408.4 | 584.7 | 770.7 | 661.4 | 564.6 | 432.3 | 440 | 518 | 473.4 | 527.5 | 339.1 | 510.2 | 297 | 315.9 | 306.7 | 296.9 | 295.6 | 311.2 | 312.7 | 277.9
1272 | 1051 | 471.2 | 188.48 | 220.3223 | 307.1 | 281.7 | 291.4 | 301.8 | 472.9 | 56.8 | 19.2 | 100.2 | 4.5 | 208.6 | 4.9 | 240.4 | 247.7 | 482.7 | 669.5 | 357.2 | 408.6 | 589.8 | 774.6 | 661.5 | 564.6 | 431.6 | 435.1 | 518.1 | 473.1 | 527.2 | 339.6 | 509.7 | 297 | 315.9 | 306.8 | 296.7 | 296 | 312.1 | 313 | 278.1
1273 | 1052 | 472.3 | 188.92 | 220.8366 | 308.2 | 281.3 | 290.4 | 302.7 | 476.4 | 56.7 | 19.2 | 100.2 | 4.3 | 259.9 | 4.6 | 240.7 | 247.9 | 479.1 | 657.2 | 357.5 | 408.8 | 590.7 | 759.9 | 660.8 | 564.5 | 447.4 | 429.8 | 518.3 | 472.1 | 521.8 | 340.1 | 509.1 | 297.1 | 315.9 | 306.6 | 296.6 | 296.5 | 312.9 | 313.8 | 278.4
1274 | 1053 | 473.5 | 189.4 | 221.3977 | 309.1 | 280.8 | 289.7 | 304.4 | 481.4 | 56.8 | 19.2 | 100.1 | 4.8 | 250.5 | 5.6 | 240.9 | 248.2 | 470 | 642.8 | 357.8 | 408.9 | 575.5 | 738.3 | 658.1 | 564.3 | 464.9 | 423.1 | 518.4 | 468.8 | 515.5 | 340.7 | 508 | 297.1 | 315.9 | 306.5 | 296.5 | 296.8 | 313.5 | 314.6 | 278.6
1275 | 1054 | 474.9 | 189.96 | 222.0523 | 308.9 | 280.4 | 289.9 | 305.7 | 482.9 | 56.9 | 19.2 | 100.1 | 5 | 243.9 | 7.2 | 241.1 | 248.4 | 460.3 | 633.9 | 358.1 | 409.1 | 565.3 | 724 | 655.8 | 564.1 | 466.3 | 418.3 | 518.6 | 465.7 | 509.1 | 341.2 | 507 | 297.1 | 316 | 306.4 | 296.5 | 297.2 | 314.1 | 315.3 | 278.9
1276 | 1055 | 472.4 | 188.96 | 220.8834 | 309 | 280.1 | 291.5 | 306 | 486.7 | 57 | 19.2 | 100.2 | 4.7 | 240.4 | 7.7 | 241.4 | 248.6 | 452.6 | 624.3 | 358.4 | 409.3 | 568.5 | 726.6 | 653.6 | 563.9 | 470.8 | 414.5 | 518.8 | 475.5 | 507.2 | 341.8 | 506.2 | 297.2 | 315.9 | 306.4 | 296.6 | 297.5 | 315 | 316.1 | 279.1
1277 | 1056 | 472.2 | 188.88 | 220.7898 | 310 | 279.9 | 292.3 | 307.1 | 491.1 | 57 | 19.2 | 100.2 | 4.9 | 247.6 | 7.7 | 241.6 | 248.9 | 449.9 | 630.2 | 358.7 | 409.4 | 559.3 | 732.6 | 653.3 | 563.6 | 473.4 | 413.4 | 519 | 482.4 | 505.2 | 342.3 | 505.3 | 297.3 | 315.8 | 306.4 | 296.7 | 298 | 315.9 | 317 | 279.4
1278 | 1057 | 473.2 | 189.28 | 221.2574 | 309.6 | 281.4 | 292.2 | 308.8 | 491.5 | 57.1 | 19.2 | 100.2 | 4.8 | 242.7 | 8.1 | 241.9 | 249.1 | 455.1 | 649.3 | 358.9 | 409.6 | 558.8 | 747.5 | 654.5 | 563.5 | 468.5 | 424.3 | 519.2 | 480.2 | 510 | 342.9 | 505.7 | 297.3 | 315.7 | 306.5 | 296.9 | 298.4 | 316.2 | 317.9 | 279.6
1279 | 1058 | 473.4 | 189.36 | 221.3509 | 308 | 282.1 | 292.2 | 309.1 | 486.8 | 57.1 | 19.2 | 100.2 | 5.3 | 243.9 | 8.1 | 242.1 | 249.3 | 458.4 | 659.6 | 359.2 | 409.7 | 560.7 | 751.6 | 655.4 | 563.5 | 465.5 | 439.1 | 519.4 | 476 | 507.9 | 343.5 | 506.1 | 297.4 | 315.5 | 306.6 | 297.1 | 298.5 | 316.2 | 318.4 | 279.8
1280 | 1059 | 472.9 | 189.16 | 221.1171 | 308.4 | 282.1 | 293 | 307.1 | 485.1 | 57 | 19.2 | 100.2 | 5.2 | 248.5 | 8 | 242.4 | 249.5 | 452.3 | 657.9 | 359.5 | 409.9 | 551 | 733 | 653.8 | 563.5 | 461.9 | 436.3 | 519.8 | 470.6 | 505 | 344 | 505.4 | 297.4 | 315.4 | 306.7 | 297.2 | 298.6 | 316.1 | 318.7 | 279.9
1281 | 1060 | 473.3 | 189.32 | 221.3042 | 308.5 | 282.4 | 293.1 | 306.6 | 475.7 | 57.1 | 19.1 | 100.2 | 4.7 | 248.6 | 7.8 | 242.6 | 249.7 | 445.7 | 663.9 | 359.7 | 410 | 540.4 | 724.5 | 651.9 | 563.5 | 455.5 | 432.2 | 519.8 | 464.3 | 500.3 | 344.6 | 504.4 | 297.5 | 315.3 | 306.8 | 297.1 | 298.8 | 315.9 | 318.7 | 280.1
1282 | 1061 | 472.4 | 188.96 | 220.8834 | 310.1 | 281.6 | 292.8 | 306.3 | 467.6 | 57 | 19.1 | 100.3 | 4.1 | 242.7 | 7.9 | 242.8 | 250 | 446.6 | 684.6 | 360 | 410.2 | 534.3 | 744.1 | 654.3 | 563.5 | 450.9 | 440.5 | 519.9 | 461.8 | 498.9 | 345.2 | 503.9 | 297.5 | 315.2 | 306.9 | 297.1 | 298.9 | 315.8 | 318.7 | 280.3
1283 | 1062 | 472.6 | 189.04 | 220.9769 | 311.4 | 280.9 | 291.4 | 305.1 | 463.9 | 57 | 19.2 | 100.4 | 4 | 247.8 | 7.9 | 243.1 | 250.2 | 464.6 | 683.5 | 360.3 | 410.3 | 549.6 | 776.3 | 659.4 | 563.6 | 449.2 | 447.2 | 520.1 | 461.9 | 508.1 | 345.7 | 505.1 | 297.5 | 315.1 | 307 | 297.2 | 299 | 315.7 | 318.7 | 280.4
1284 | 1063 | 472.7 | 189.08 | 221.0236 | 312.6 | 280.6 | 289.8 | 304.5 | 461.6 | 57 | 19.2 | 100.4 | 4.4 | 240.4 | 8.2 | 243.3 | 250.4 | 480.3 | 682.8 | 360.5 | 410.5 | 570.8 | 799.5 | 662.9 | 563.7 | 447.3 | 447.8 | 520.2 | 465.3 | 514.4 | 346.3 | 506.4 | 297.5 | 315 | 307 | 297.2 | 299.1 | 315.5 | 318.7 | 280.6
1285 | 1064 | 472.7 | 189.08 | 221.0236 | 312.5 | 281.3 | 289 | 303.5 | 463.3 | 57.1 | 19.2 | 100.5 | 5 | 247 | 8.2 | 243.5 | 250.6 | 490.6 | 682.4 | 360.8 | 410.6 | 586.3 | 809.9 | 666.4 | 563.8 | 456.8 | 453.8 | 520.5 | 468.6 | 520.7 | 346.9 | 507.6 | 297.5 | 315 | 306.8 | 297.2 | 299.3 | 315.3 | 318.7 | 280.7
1286 | 1065 | 473.1 | 189.24 | 221.2107 | 312.9 | 280.8 | 288.5 | 302.5 | 465.2 | 57 | 19.2 | 100.4 | 4.9 | 258.8 | 8.2 | 243.8 | 250.8 | 499.7 | 694.2 | 361 | 410.7 | 589.4 | 824.8 | 670.3 | 564.1 | 479.5 | 459.7 | 520.8 | 472.4 | 523.3 | 347.5 | 508.1 | 297.5 | 315 | 306.6 | 297.1 | 299.3 | 315.1 | 318.5 | 280.9
1287 | 1066 | 472.3 | 188.92 | 220.8366 | 311.6 | 280.5 | 288.4 | 302.4 | 467.4 | 57 | 19.1 | 100.4 | 5 | 248.7 | 7.9 | 244 | 251 | 514.4 | 703.7 | 361.2 | 410.9 | 607.5 | 829.9 | 673.9 | 564.3 | 490.8 | 468.9 | 520.8 | 478.4 | 540.6 | 348.1 | 510.1 | 297.6 | 315 | 306.4 | 297.1 | 299.4 | 314.8 | 318.5 | 281
1288 | 1067 | 472.4 | 188.96 | 220.8834 | 311.4 | 281 | 288.9 | 302 | 464.8 | 57 | 19.1 | 100.5 | 5.3 | 256 | 7.8 | 244.3 | 251.3 | 545 | 714.2 | 361.5 | 411 | 640.8 | 831.9 | 676.4 | 564.6 | 502.4 | 477.9 | 521 | 488.6 | 551.6 | 348.7 | 512.2 | 297.6 | 314.7 | 306.3 | 297.2 | 299.5 | 314.7 | 318.4 | 281.2
1289 | 1068 | 472.8 | 189.12 | 221.0704 | 311.5 | 280.9 | 289.2 | 302.1 | 467.8 | 57 | 19.1 | 100.6 | 5 | 258.9 | 7.9 | 244.5 | 251.5 | 555 | 725.9 | 361.8 | 411.2 | 642.5 | 838.5 | 679.7 | 565 | 500.5 | 490.7 | 521.3 | 491.9 | 557.6 | 349.3 | 514.3 | 297.6 | 314.4 | 306.3 | 297.3 | 299.6 | 314.2 | 318.1 | 281.3
1290 | 1069 | 472.9 | 189.16 | 221.1171 | 310.1 | 280.7 | 289.6 | 301.4 | 468.5 | 57.1 | 19.1 | 100.6 | 5.1 | 256.5 | 7.9 | 244.7 | 251.7 | 567.3 | 734.4 | 362.1 | 411.4 | 639 | 829.8 | 681.2 | 565.4 | 498.2 | 509.9 | 521.5 | 490.1 | 563.8 | 350 | 516.8 | 297.7 | 314.3 | 306.3 | 297.4 | 299.6 | 313.7 | 317.6 | 281.4
1291 | 1070 | 472 | 188.8 | 220.6963 | 308.4 | 282.3 | 290 | 300 | 464.5 | 57.3 | 19.1 | 100.7 | 4.9 | 254.3 | 8.1 | 244.9 | 251.8 | 568.6 | 732.4 | 362.3 | 411.6 | 623.5 | 823.2 | 682.3 | 566 | 495.3 | 518.7 | 522 | 486 | 562.6 | 350.6 | 517.7 | 297.8 | 314.3 | 306.5 | 297.7 | 299.6 | 313.3 | 317 | 281.6
1292 | 1071 | 473.5 | 189.4 | 221.3977 | 309.2 | 282.4 | 289.6 | 298.9 | 460.2 | 57.4 | 19.1 | 100.7 | 4.4 | 254.6 | 8.6 | 245.2 | 252 | 559.6 | 731.1 | 362.5 | 411.7 | 613.6 | 804.9 | 681.8 | 566.5 | 492.3 | 526.6 | 522.5 | 482.5 | 565.8 | 351.2 | 518.8 | 297.8 | 314.4 | 306.8 | 298.1 | 299.5 | 312.8 | 316.5 | 281.7
1293 | 1072 | 474.1 | 189.64 | 221.6782 | 308.9 | 282.5 | 289.9 | 298.1 | 460.8 | 57.5 | 19.1 | 100.7 | 4.5 | 247.4 | 9 | 245.4 | 252.2 | 554.5 | 725.7 | 362.8 | 411.9 | 593.4 | 783.7 | 679.5 | 567.2 | 490.6 | 522.3 | 523.1 | 477.2 | 563.1 | 351.8 | 518.9 | 298 | 314.4 | 307 | 298.2 | 299.5 | 312.3 | 315.9 | 281.7
1294 | 1073 | 473.3 | 189.32 | 221.3042 | 309.2 | 282.3 | 291.2 | 296.3 | 457.9 | 57.6 | 19.1 | 100.6 | 5 | 249.4 | 8.8 | 245.6 | 252.4 | 547.8 | 723 | 363.1 | 412.1 | 575.7 | 762.9 | 678.1 | 567.8 | 496.3 | 518.5 | 523.7 | 470.5 | 560.1 | 352.5 | 519.3 | 298.1 | 314.4 | 307.1 | 298.2 | 299.4 | 311.6 | 315.1 | 281.7
1295 | 1074 | 473.5 | 189.4 | 221.3977 | 310.2 | 282 | 291.8 | 294.6 | 453.3 | 57.7 | 19.1 | 100.6 | 5.4 | 236.6 | 8.1 | 245.9 | 252.6 | 539.6 | 716.1 | 363.4 | 412.3 | 584.1 | 764 | 679 | 568.4 | 491.8 | 514.4 | 524.2 | 465.1 | 557.3 | 353.1 | 519.6 | 298.1 | 314.4 | 307.2 | 298.2 | 299.4 | 310.9 | 314.5 | 281.7
1296 | 1075 | 473.1 | 189.24 | 221.2107 | 310.8 | 280.8 | 292 | 293.7 | 445.4 | 57.7 | 19.1 | 100.7 | 4.8 | 238.6 | 7.7 | 246.1 | 252.8 | 526.9 | 698.1 | 363.7 | 412.5 | 583.1 | 749.3 | 676.9 | 568.7 | 484.9 | 502.5 | 524.7 | 459.9 | 545.4 | 353.8 | 518.8 | 298.2 | 314.4 | 307.1 | 298 | 299.3 | 310.3 | 313.9 | 281.8
1297 | 1076 | 473.2 | 189.28 | 221.2574 | 311.4 | 279.8 | 291.3 | 292.1 | 439.8 | 57.6 | 19.1 | 100.6 | 5 | 246.8 | 7.6 | 246.3 | 253 | 519.6 | 687.4 | 364 | 412.7 | 580.2 | 725.6 | 673.3 | 568.9 | 476.4 | 490.6 | 525.3 | 454.9 | 537.6 | 354.4 | 517.6 | 298.1 | 314.2 | 306.9 | 297.8 | 299.3 | 310 | 313.6 | 281.9
1298 | 1077 | 473.6 | 189.44 | 221.4444 | 311.5 | 279.1 | 290.1 | 291.6 | 439.9 | 57.6 | 19.1 | 100.6 | 4.7 | 245.3 | 7.4 | 246.6 | 253.2 | 514.6 | 676.9 | 364.2 | 412.9 | 574.4 | 711.6 | 671 | 569.1 | 469.2 | 480.1 | 525.9 | 451.1 | 530.6 | 355.1 | 516.3 | 298.1 | 313.9 | 306.6 | 297.5 | 299.5 | 310.1 | 313.4 | 282
1299 | 1078 | 473.4 | 189.36 | 221.3509 | 312.7 | 279.3 | 289.3 | 292.2 | 442.1 | 57.6 | 19.1 | 100.6 | 4.5 | 249.6 | 7.2 | 246.8 | 253.4 | 507 | 674.3 | 364.5 | 413.2 | 568.2 | 696.5 | 670 | 569.2 | 463.1 | 474.3 | 526.5 | 446.8 | 524.3 | 355.7 | 515.4 | 298.1 | 313.6 | 306.3 | 297.4 | 299.6 | 310.1 | 313.2 | 282.1
1300 | 1079 | 473.1 | 189.24 | 221.2107 | 313.4 | 279.2 | 288 | 292.5 | 441.7 | 57.6 | 19.1 | 100.7 | 4.3 | 247 | 7.2 | 247 | 253.6 | 502.8 | 665.1 | 364.8 | 413.4 | 567.5 | 674.6 | 667.8 | 569.2 | 457.7 | 467.2 | 527.2 | 442.7 | 519.5 | 356.4 | 514.5 | 298 | 313.4 | 305.7 | 297.4 | 299.6 | 310 | 313 | 282.2
1301 | 1080 | 472.9 | 189.16 | 221.1171 | 313.8 | 278.3 | 287.9 | 292.6 | 437.4 | 57.6 | 19.1 | 100.7 | 4.4 | 240.2 | 6.9 | 247.2 | 253.8 | 502.8 | 671.7 | 365.1 | 413.7 | 576.4 | 669.9 | 667.7 | 569.2 | 451.7 | 464.3 | 527.9 | 438.6 | 515.3 | 357 | 513.7 | 298 | 313.1 | 305.3 | 297.3 | 299.7 | 309.7 | 312.9 | 282.3
1302 | 1081 | 472.8 | 189.12 | 221.0704 | 315.2 | 277.5 | 287.3 | 292.7 | 433.2 | 57.4 | 19.1 | 100.6 | 4.7 | 246.3 | 6.2 | 247.5 | 254 | 496.9 | 683.7 | 365.4 | 414 | 571.6 | 696.6 | 669.4 | 569.2 | 446.8 | 461.6 | 528.3 | 436.7 | 517.1 | 357.7 | 513.4 | 298 | 312.9 | 304.9 | 297.2 | 299.8 | 309.9 | 313 | 282.5
1303 | 1082 | 473.5 | 189.4 | 221.3977 | 316.1 | 277.1 | 286.9 | 291.6 | 432.8 | 57.4 | 19.1 | 100.6 | 5.5 | 243.1 | 5.6 | 247.7 | 254.2 | 487.5 | 683.7 | 365.7 | 414.3 | 573.3 | 715.7 | 668.6 | 569.2 | 442.6 | 456.6 | 528.8 | 435.2 | 513 | 358.4 | 512.8 | 297.9 | 312.8 | 304.7 | 297.1 | 299.9 | 310.1 | 313.1 | 282.6
1304 | 1083 | 471.9 | 188.76 | 220.6496 | 316.7 | 276.8 | 286.2 | 292.7 | 435.4 | 57.4 | 19.1 | 100.5 | 5 | 245.9 | 5.6 | 247.9 | 254.4 | 480.5 | 689.2 | 366 | 414.6 | 564.1 | 725.6 | 669.2 | 569.3 | 440.6 | 454.7 | 529.3 | 432.2 | 507.9 | 359 | 511.7 | 297.9 | 312.7 | 304.8 | 297.1 | 300 | 310 | 313.3 | 282.7
1305 | 1084 | 470.6 | 188.24 | 220.0417 | 317.2 | 276.2 | 285.4 | 293.8 | 439.2 | 57.4 | 19.1 | 100.4 | 4.9 | 251.2 | 5.6 | 248.1 | 254.6 | 494.3 | 702.9 | 366.3 | 414.9 | 561.4 | 742.3 | 672 | 569.4 | 438.8 | 461.8 | 529.6 | 432.9 | 515.1 | 359.7 | 511.9 | 298 | 312.8 | 304.9 | 297.3 | 300 | 309.9 | 313.1 | 282.8
1306 | 1085 | 471.8 | 188.72 | 220.6028 | 317.4 | 276 | 286.5 | 293.9 | 438.8 | 57.3 | 19.1 | 100.3 | 4.4 | 250.5 | 5.5 | 248.4 | 254.8 | 495.5 | 705.9 | 366.5 | 415.2 | 574.7 | 759.6 | 673.6 | 569.5 | 440.6 | 465.8 | 529.9 | 438.7 | 526 | 360.4 | 513.2 | 298 | 312.7 | 304.7 | 297.3 | 300 | 309.8 | 313.1 | 282.9
1307 | 1086 | 471.7 | 188.68 | 220.556 | 317.5 | 276.3 | 287.1 | 294 | 443 | 57.3 | 19.1 | 100.3 | 4.9 | 235.1 | 5.2 | 248.6 | 254.9 | 501 | 723 | 366.7 | 415.4 | 571.8 | 773.6 | 675.6 | 569.6 | 442.7 | 475.5 | 530.2 | 441.6 | 526.1 | 361.1 | 513.6 | 298 | 312.5 | 304.9 | 297.5 | 300.1 | 309.7 | 313.3 | 282.9
1308 | 1087 | 471.5 | 188.6 | 220.4625 | 316.5 | 276.9 | 287.2 | 294.3 | 449.9 | 57.3 | 19.1 | 100.3 | 5.1 | 250.1 | 5 | 248.8 | 255.1 | 509.4 | 716.8 | 367 | 415.7 | 588.5 | 785.9 | 677.7 | 569.8 | 462.6 | 477.8 | 530.5 | 449.1 | 530.3 | 361.8 | 514.2 | 298.1 | 312.7 | 305.3 | 297.7 | 300.1 | 309.9 | 313.2 | 283.1
1309 | 1088 | 472.5 | 189 | 220.9301 | 315.1 | 277.1 | 287.7 | 294.2 | 456 | 57.3 | 19.1 | 100.3 | 5 | 252.3 | 4.9 | 249 | 255.3 | 502 | 713.3 | 367.3 | 415.9 | 604.6 | 778.3 | 675.4 | 570 | 477.1 | 471 | 530.9 | 458.4 | 528.7 | 362.5 | 514 | 298.2 | 312.8 | 305.6 | 297.7 | 300.4 | 310.6 | 313.6 | 283.3
1310 | 1089 | 473.2 | 189.28 | 221.2574 | 313.6 | 277.6 | 288.7 | 295.3 | 460.8 | 57.3 | 19.1 | 100.3 | 4.8 | 217.6 | 4.7 | 249.3 | 255.5 | 494.7 | 705.7 | 367.5 | 416.2 | 593.9 | 764.1 | 674.4 | 570.1 | 470.5 | 466.2 | 531.4 | 452.9 | 520.8 | 363.2 | 513.1 | 298.3 | 312.9 | 305.6 | 297.7 | 300.5 | 310.9 | 314 | 283.5
1311 | 1090 | 471.4 | 188.56 | 220.4158 | 311.4 | 277.6 | 288.9 | 296.4 | 460.7 | 57.3 | 19.1 | 100.4 | 4.7 | 228.5 | 4.3 | 249.5 | 255.6 | 488.7 | 693.3 | 367.8 | 416.4 | 586.3 | 750.2 | 672.9 | 570.1 | 466 | 461.2 | 531.9 | 448.5 | 513.1 | 363.9 | 512.4 | 298.3 | 313.1 | 305.9 | 297.8 | 300.6 | 310.9 | 314.2 | 283.5
1312 | 1091 | 472.2 | 188.88 | 220.7898 | 312.1 | 277.7 | 288.5 | 296 | 460.2 | 57.3 | 19.1 | 100.4 | 5.2 | 250.1 | 4.4 | 249.7 | 255.8 | 486.1 | 688.5 | 368 | 416.7 | 589.3 | 745.5 | 672.9 | 570.2 | 460.5 | 462.4 | 532.3 | 446.5 | 515 | 364.6 | 512.1 | 298.4 | 313.3 | 306.2 | 297.8 | 300.7 | 310.9 | 314.4 | 283.7
1313 | 1092 | 471.9 | 188.76 | 220.6496 | 313.6 | 277.7 | 288.7 | 296.4 | 459.7 | 57.3 | 19.1 | 100.4 | 5.1 | 248.8 | 5.5 | 249.9 | 256 | 483.3 | 699.3 | 368.3 | 416.9 | 586.2 | 752.9 | 673.9 | 570.3 | 456 | 461.1 | 532.6 | 446.4 | 517.7 | 365.3 | 511.9 | 298.5 | 313.6 | 306.4 | 297.9 | 300.8 | 311 | 314.3 | 283.8
1314 | 1093 | 472.3 | 188.92 | 220.8366 | 313.8 | 277.7 | 288.8 | 296.4 | 461.3 | 57.3 | 19.1 | 100.4 | 5 | 245.5 | 6.5 | 250.2 | 256.2 | 489.1 | 709.9 | 368.6 | 417.1 | 590.1 | 770.5 | 676.2 | 570.5 | 452.2 | 468.8 | 532.9 | 449 | 525.6 | 366 | 512.6 | 298.6 | 313.8 | 306.5 | 297.9 | 300.9 | 311 | 314.2 | 283.9
1315 | 1094 | 471.9 | 188.76 | 220.6496 | 314.3 | 277.8 | 288.8 | 296.2 | 465.9 | 57.4 | 19.1 | 100.4 | 4.9 | 247.2 | 6.9 | 250.4 | 256.4 | 503 | 717.1 | 368.8 | 417.3 | 603.5 | 793.4 | 679.7 | 570.8 | 449.4 | 475.8 | 533.2 | 450 | 530.7 | 366.8 | 513.5 | 298.6 | 313.9 | 306.6 | 297.9 | 301 | 311.1 | 314.2 | 284
1316 | 1095 | 472.5 | 189 | 220.9301 | 313.8 | 277.6 | 288.6 | 296.3 | 464.4 | 57.5 | 19.1 | 100.5 | 5.2 | 244.3 | 6.9 | 250.6 | 256.6 | 518.4 | 726.5 | 369.1 | 417.6 | 612.2 | 810 | 682.6 | 571 | 448.8 | 486.2 | 533.5 | 453.4 | 541.2 | 367.5 | 515 | 298.7 | 314.1 | 306.6 | 297.9 | 301.2 | 311.6 | 314.7 | 284.2
1317 | 1096 | 472.5 | 189 | 220.9301 | 313.2 | 278.1 | 288.3 | 296.4 | 460.1 | 57.5 | 19.1 | 100.5 | 5.2 | 246.4 | 6.9 | 250.8 | 256.8 | 533.1 | 735.2 | 369.3 | 417.8 | 612.8 | 817.4 | 686.2 | 571.4 | 447.6 | 503 | 533.7 | 456.9 | 552.1 | 368.2 | 517.1 | 298.8 | 314.4 | 306.9 | 298 | 301.4 | 312.1 | 315 | 284.4
1318 | 1097 | 472.5 | 189 | 220.9301 | 312.3 | 278.9 | 288.7 | 295.8 | 457.9 | 57.5 | 19.1 | 100.6 | 5.1 | 249.9 | 6.9 | 251.1 | 257 | 537.1 | 733.6 | 369.5 | 418 | 641.8 | 822.8 | 687.7 | 571.6 | 448 | 501.2 | 534 | 460.7 | 559.7 | 369 | 519 | 299 | 314.5 | 306.9 | 297.9 | 301.5 | 312.5 | 315.2 | 284.6
1319 | 1098 | 472.4 | 188.96 | 220.8834 | 310.1 | 278.5 | 288.9 | 296 | 462.6 | 57.6 | 19.1 | 100.5 | 5.4 | 256.4 | 6.6 | 251.3 | 257.2 | 531.9 | 718 | 369.7 | 418.2 | 640.5 | 808 | 686.5 | 571.8 | 450.1 | 492.4 | 534.3 | 467.2 | 555.5 | 369.7 | 519 | 299 | 314.5 | 306.7 | 297.8 | 301.8 | 313.3 | 315.7 | 284.8
1320 | 1099 | 473 | 189.2 | 221.1639 | 308.8 | 278.2 | 288.3 | 297.8 | 469.5 | 57.6 | 19.1 | 100.5 | 5.8 | 244 | 6.4 | 251.5 | 257.4 | 524.1 | 708 | 370 | 418.4 | 631.2 | 812.2 | 687 | 571.9 | 465.1 | 484.7 | 534.6 | 472.4 | 553.1 | 370.5 | 518.6 | 299.1 | 314.3 | 306.4 | 297.6 | 302.1 | 314 | 316.2 | 284.9
1321 | 1100 | 473 | 189.2 | 221.1639 | 307.6 | 278.1 | 288.5 | 298.2 | 478.2 | 57.6 | 19.1 | 100.5 | 4.8 | 254.1 | 6.4 | 251.7 | 257.6 | 523.9 | 701.7 | 370.3 | 418.6 | 646.8 | 817.9 | 689.6 | 572 | 484.9 | 483 | 534.9 | 483.4 | 561.1 | 371.2 | 519.3 | 299.2 | 314.2 | 306.2 | 297.6 | 302.5 | 314.8 | 316.5 | 285.1
1322 | 1101 | 473 | 189.2 | 221.1639 | 307.3 | 279 | 288.3 | 298.2 | 482.9 | 57.7 | 19.1 | 100.5 | 4.7 | 253.2 | 6.5 | 252 | 257.8 | 521.6 | 702.8 | 370.6 | 418.9 | 651.1 | 816.9 | 689.9 | 572.2 | 495.8 | 483.1 | 535.4 | 489.1 | 559 | 371.9 | 519.5 | 299.2 | 314.1 | 306.2 | 297.6 | 302.7 | 315.5 | 316.9 | 285.4
1323 | 1102 | 472.9 | 189.16 | 221.1171 | 306.3 | 279.4 | 288.4 | 298.9 | 481.4 | 57.8 | 19.1 | 100.5 | 4.3 | 248.2 | 6.5 | 252.2 | 257.9 | 523.3 | 707.8 | 370.9 | 419.1 | 646.2 | 813.6 | 689.7 | 572.3 | 508.8 | 482.6 | 536 | 498.6 | 554.5 | 372.7 | 519.4 | 299.3 | 314.1 | 306.4 | 297.7 | 302.9 | 315.7 | 317.2 | 285.5
1324 | 1103 | 472.8 | 189.12 | 221.0704 | 305.6 | 279.9 | 289 | 299.8 | 479.9 | 57.9 | 19.1 | 100.6 | 3.9 | 249.1 | 6.4 | 252.4 | 258.1 | 517.5 | 714.3 | 371.1 | 419.4 | 631.4 | 816.5 | 689.2 | 572.5 | 535 | 478.6 | 536.5 | 510.9 | 549.9 | 373.4 | 518.4 | 299.3 | 313.8 | 306.5 | 297.8 | 303 | 315.5 | 317.2 | 285.5
1325 | 1104 | 472.1 | 188.84 | 220.7431 | 304.4 | 279.8 | 289.5 | 299.3 | 476 | 57.9 | 19.1 | 100.6 | 4.2 | 248.6 | 6.3 | 252.7 | 258.3 | 516 | 719 | 371.4 | 419.6 | 624.4 | 807.9 | 690.2 | 572.8 | 544.5 | 481.5 | 536.9 | 524.3 | 550.9 | 374.3 | 518.5 | 299.4 | 313.6 | 306.5 | 298 | 303.1 | 315.1 | 317 | 285.6
1326 | 1105 | 472.6 | 189.04 | 220.9769 | 305.4 | 280.1 | 290.1 | 298.7 | 474.4 | 58 | 19.1 | 100.7 | 4.3 | 252.8 | 6.4 | 252.9 | 258.4 | 510.1 | 713.3 | 371.7 | 419.9 | 609 | 783.8 | 686.6 | 573.1 | 542 | 480.9 | 537.3 | 523.2 | 547.7 | 375 | 518.9 | 299.4 | 313.5 | 306.8 | 298.5 | 303.2 | 314.6 | 316.7 | 285.6
1327 | 1106 | 472 | 188.8 | 220.6963 | 309.1 | 281.7 | 291 | 298.6 | 477 | 58 | 19.1 | 100.9 | 4.6 | 241.1 | 6 | 253.1 | 258.6 | 507.7 | 710.8 | 372 | 420.1 | 620.9 | 793.3 | 688 | 573.4 | 546.1 | 474.8 | 537.6 | 530 | 542.2 | 375.7 | 518.5 | 299.5 | 313.5 | 306.9 | 298.6 | 303.3 | 314.7 | 316.6 | 285.8
1328 | 1107 | 473 | 189.2 | 221.1639 | 311.3 | 282.1 | 291.5 | 298.3 | 474.5 | 58.1 | 19.1 | 101 | 4.4 | 247.9 | 5.4 | 253.3 | 258.8 | 516.1 | 697.1 | 372.2 | 420.4 | 617.7 | 785.7 | 687.4 | 573.6 | 542.7 | 466.5 | 538.1 | 542.8 | 534 | 376.5 | 517.8 | 299.6 | 313.6 | 307.5 | 298.8 | 303.6 | 315.5 | 316.8 | 286.1
1329 | 1108 | 472.9 | 189.16 | 221.1171 | 312.3 | 282.4 | 291 | 299.4 | 477.5 | 58.1 | 19.1 | 101.2 | 5.1 | 262.2 | 4.9 | 253.5 | 258.9 | 508.2 | 674.8 | 372.5 | 420.6 | 612 | 756.6 | 682.9 | 573.6 | 538.8 | 459.3 | 538.4 | 558.5 | 526.7 | 377.3 | 516.5 | 299.7 | 313.7 | 307.8 | 298.8 | 303.9 | 316.5 | 317.6 | 286.3
1330 | 1109 | 472.7 | 189.08 | 221.0236 | 313.1 | 282.5 | 290.6 | 302 | 480 | 58.1 | 19.1 | 101.3 | 5.2 | 255.7 | 4.5 | 253.8 | 259.1 | 500 | 653.6 | 372.8 | 420.8 | 602.2 | 736.1 | 679.3 | 573.4 | 530.9 | 450.1 | 538.7 | 571.2 | 521.2 | 378.1 | 515.5 | 299.8 | 313.8 | 307.7 | 298.7 | 304.3 | 317.6 | 319 | 286.7
1331 | 1110 | 472.6 | 189.04 | 220.9769 | 312.8 | 283.1 | 291.4 | 304.5 | 480 | 58.1 | 19.1 | 101.5 | 4.6 | 252.6 | 4.5 | 254 | 259.2 | 491.4 | 649.4 | 373.2 | 421 | 592.1 | 730.4 | 677.8 | 573.1 | 524.9 | 443 | 539.2 | 587.5 | 514.4 | 378.8 | 514.3 | 299.9 | 313.9 | 307.7 | 298.6 | 304.6 | 318.5 | 320.1 | 286.9
1332 | 1111 | 471.5 | 188.6 | 220.4625 | 312 | 284.1 | 292.8 | 307.9 | 483.6 | 58.1 | 19.1 | 101.6 | 4.9 | 254.4 | 4.6 | 254.2 | 259.4 | 491 | 652.6 | 373.5 | 421.2 | 598.5 | 743.1 | 678 | 572.7 | 538.2 | 437.7 | 540.1 | 602.7 | 511.7 | 379.6 | 513.5 | 300 | 314.2 | 307.7 | 298.5 | 305 | 319.1 | 320.9 | 287.1
1333 | 1112 | 472 | 188.8 | 220.6963 | 311.4 | 284.4 | 293.4 | 309.9 | 488.6 | 58.1 | 19.1 | 101.6 | 4.9 | 260.7 | 5.3 | 254.4 | 259.5 | 493.6 | 662.6 | 373.9 | 421.4 | 600.2 | 751.8 | 679.1 | 572.4 | 554 | 434.3 | 541 | 612.5 | 511.8 | 380.3 | 513.4 | 300.2 | 314.4 | 308.1 | 298.5 | 305.2 | 319.4 | 321.3 | 287.2
1334 | 1113 | 471.6 | 188.64 | 220.5093 | 312.3 | 284.9 | 293.7 | 310.9 | 493 | 58.1 | 19 | 101.6 | 4.8 | 273.5 | 6.2 | 254.6 | 259.7 | 491.1 | 669.9 | 374.3 | 421.6 | 609.5 | 760.9 | 680.5 | 572.1 | 572.4 | 433 | 541.9 | 621.9 | 511.5 | 381.1 | 512.9 | 300.3 | 314.4 | 308.3 | 298.6 | 305.5 | 319.7 | 321.9 | 287.4
1335 | 1114 | 472 | 188.8 | 220.6963 | 313.1 | 285.8 | 293.9 | 310.9 | 494.8 | 58.2 | 19 | 101.7 | 5.2 | 269.4 | 6.6 | 254.8 | 259.9 | 494.1 | 690 | 374.7 | 421.8 | 620.4 | 760.3 | 680.6 | 572.1 | 600.3 | 446.3 | 542.6 | 618.7 | 524.2 | 381.8 | 513.4 | 300.4 | 314.6 | 308.7 | 298.9 | 305.7 | 320 | 322.4 | 287.6
1336 | 1115 | 472.3 | 188.92 | 220.8366 | 312.4 | 286.9 | 294.1 | 310.2 | 496.7 | 58.3 | 19 | 101.7 | 5.1 | 269.3 | 6.4 | 255 | 260 | 494.5 | 696.5 | 375 | 422 | 614.4 | 759.8 | 681.6 | 572.2 | 617.8 | 451.5 | 543.1 | 618.2 | 524.3 | 382.6 | 513.6 | 300.5 | 314.7 | 309.2 | 299.1 | 305.9 | 320 | 322.4 | 287.8
1337 | 1116 | 471.5 | 188.6 | 220.4625 | 311.2 | 286.6 | 295.1 | 310 | 493.4 | 58.4 | 19.1 | 101.7 | 4.8 | 275.1 | 6.6 | 255.3 | 260.1 | 496.3 | 711.5 | 375.3 | 422.2 | 607.5 | 768.2 | 684.3 | 572.3 | 623.1 | 460.7 | 543.5 | 616.9 | 527.6 | 383.4 | 513.5 | 300.6 | 314.9 | 309.5 | 299.3 | 306 | 319.6 | 322.1 | 287.8
1338 | 1117 | 471.8 | 188.72 | 220.6028 | 312.3 | 286.3 | 295.8 | 309.4 | 487.7 | 58.4 | 19.1 | 101.7 | 4.4 | 270.6 | 7.3 | 255.5 | 260.3 | 498.6 | 722.2 | 375.7 | 422.5 | 604.1 | 763.3 | 683.9 | 572.6 | 631.1 | 474.1 | 543.8 | 608.6 | 537.9 | 384.2 | 514.9 | 300.8 | 315.3 | 310.1 | 299.5 | 306 | 319.3 | 322.1 | 287.9
1339 | 1118 | 471.7 | 188.68 | 220.556 | 313.1 | 285.9 | 296.3 | 308.4 | 487.2 | 58.3 | 19 | 101.7 | 4.6 | 270.2 | 7.7 | 255.7 | 260.4 | 506.7 | 724.8 | 376 | 422.7 | 596 | 764.9 | 683.8 | 572.9 | 632.3 | 482.3 | 544.1 | 594.4 | 545.5 | 385 | 515.8 | 301 | 315.7 | 310.6 | 299.8 | 306.1 | 319.3 | 322 | 288
1340 | 1119 | 472.1 | 188.84 | 220.7431 | 314.5 | 285.3 | 296.5 | 307.7 | 487.9 | 58.4 | 19 | 101.8 | 4.6 | 277.9 | 7.3 | 255.9 | 260.5 | 509.9 | 728.2 | 376.3 | 423 | 603 | 769.4 | 685 | 573.3 | 638.6 | 495.1 | 544.5 | 592.7 | 547.3 | 385.8 | 516.7 | 301.2 | 316.1 | 311.1 | 300.1 | 306.2 | 319.3 | 322 | 288.2
1341 | 1120 | 472.5 | 189 | 220.9301 | 314.9 | 284.4 | 296.1 | 306.4 | 487.6 | 58.3 | 19 | 101.9 | 4.2 | 259.3 | 6.9 | 256.1 | 260.7 | 505.4 | 716.6 | 376.6 | 423.2 | 604.8 | 777.7 | 687.1 | 573.6 | 655.3 | 491.2 | 545 | 594.8 | 553.8 | 386.7 | 517.3 | 301.4 | 316.5 | 311.5 | 300.2 | 306.3 | 319.6 | 322.1 | 288.4
1342 | 1121 | 471.7 | 188.68 | 220.556 | 314.9 | 283.7 | 295.8 | 304.5 | 490.8 | 58.3 | 19 | 101.8 | 4.7 | 275.3 | 6.7 | 256.4 | 260.8 | 505.6 | 699.8 | 376.9 | 423.5 | 612.4 | 786.6 | 687.8 | 573.9 | 663.1 | 484 | 545.5 | 602.3 | 549.8 | 387.6 | 517.4 | 301.6 | 316.8 | 311.5 | 300 | 306.5 | 319.9 | 322.4 | 288.6
1343 | 1122 | 472.1 | 188.84 | 220.7431 | 314.4 | 283.9 | 295.5 | 305 | 496 | 58.3 | 19 | 101.7 | 4.7 | 261.6 | 6.5 | 256.6 | 261 | 503.2 | 686.8 | 377.2 | 423.7 | 615.7 | 794 | 688.4 | 574 | 660 | 479 | 546.2 | 612.7 | 551 | 388.5 | 517.7 | 301.7 | 316.9 | 311.7 | 300 | 306.7 | 320.5 | 322.8 | 288.8
1344 | 1123 | 471.8 | 188.72 | 220.6028 | 313.1 | 284.7 | 295.1 | 305.4 | 499.4 | 58.3 | 19 | 101.6 | 4.5 | 260.5 | 6.7 | 256.8 | 261.2 | 507.8 | 679.8 | 377.5 | 424 | 623.1 | 808.8 | 689.4 | 574 | 657.1 | 474 | 546.9 | 620.2 | 554.3 | 389.4 | 519 | 301.8 | 316.9 | 311.7 | 300 | 307 | 321.1 | 323.3 | 289
1345 | 1124 | 473.6 | 189.44 | 221.4444 | 312 | 285.4 | 295.4 | 306.4 | 508.6 | 58.3 | 19 | 101.7 | 4.9 | 265.4 | 6.9 | 257 | 261.3 | 516.3 | 688.5 | 377.8 | 424.2 | 619.1 | 821.5 | 690.5 | 574 | 664.7 | 472.8 | 547.4 | 632.1 | 551.8 | 390.4 | 518.9 | 301.9 | 316.9 | 311.5 | 300 | 307.2 | 321.5 | 323.7 | 289.1
1346 | 1125 | 473.4 | 189.36 | 221.3509 | 311 | 285.3 | 296.2 | 306.6 | 516.9 | 58.3 | 19 | 101.8 | 4.6 | 262.2 | 6.7 | 257.2 | 261.4 | 522.4 | 704.1 | 378.1 | 424.5 | 626.6 | 830.6 | 691.6 | 574.1 | 658.8 | 484.9 | 547.9 | 633.5 | 554.9 | 391.2 | 519.6 | 302 | 316.9 | 311.5 | 300 | 307.4 | 321.5 | 324 | 289.3
1347 | 1126 | 472 | 188.8 | 220.6963 | 309.9 | 285.4 | 296.3 | 305.1 | 512.9 | 58.3 | 19 | 101.9 | 4.4 | 263.1 | 6.5 | 257.4 | 261.6 | 533 | 710.4 | 378.4 | 424.7 | 620.8 | 806.8 | 690.6 | 574.3 | 652.9 | 493.8 | 548.3 | 629.1 | 553.9 | 392.1 | 520.4 | 302.2 | 316.9 | 311.8 | 300.2 | 307.5 | 321.3 | 323.9 | 289.3
1348 | 1127 | 471.8 | 188.72 | 220.6028 | 309.4 | 286.9 | 296.5 | 303.5 | 512 | 58.4 | 19 | 101.9 | 4.7 | 264.4 | 6.4 | 257.6 | 261.7 | 526.7 | 711 | 378.6 | 425 | 610.5 | 789.2 | 689.9 | 574.6 | 648.9 | 491 | 548.9 | 622.4 | 550.6 | 393.2 | 521 | 302.3 | 317 | 312 | 300.4 | 307.6 | 321.1 | 323.8 | 289.4
1349 | 1128 | 473 | 189.2 | 221.1639 | 310.2 | 287.8 | 297.1 | 302.8 | 506.7 | 58.4 | 19 | 101.9 | 4.9 | 262.8 | 6.1 | 257.9 | 261.8 | 517.9 | 702 | 378.9 | 425.2 | 601.8 | 763.1 | 687.2 | 574.8 | 647 | 486.5 | 549.6 | 617.2 | 547 | 394.1 | 521 | 302.5 | 317.1 | 312.3 | 300.6 | 307.6 | 321.1 | 323.7 | 289.6
1350 | 1129 | 473.3 | 189.32 | 221.3042 | 311.4 | 288.3 | 297.6 | 302.8 | 504.1 | 58.4 | 19 | 101.9 | 5.1 | 262.2 | 6.2 | 258.1 | 262 | 509.3 | 708.3 | 379.2 | 425.5 | 600.7 | 778.3 | 688.8 | 575.1 | 658.9 | 484.2 | 550 | 616.9 | 547.9 | 395.1 | 521 | 302.6 | 317.4 | 312.6 | 300.7 | 307.8 | 321.2 | 323.6 | 289.7
1351 | 1130 | 473.7 | 189.48 | 221.4912 | 313.2 | 288.6 | 298.4 | 301.7 | 501.8 | 58.5 | 19 | 102 | 4.8 | 279.6 | 6.3 | 258.3 | 262.1 | 511.7 | 716.4 | 379.4 | 425.7 | 599.3 | 796.4 | 689.4 | 575.4 | 673.7 | 483.5 | 550.3 | 621 | 544 | 396 | 520.8 | 302.8 | 317.8 | 313 | 300.8 | 307.9 | 321.1 | 323.5 | 289.9
1352 | 1131 | 473.2 | 189.28 | 221.2574 | 313.1 | 288.7 | 298.4 | 301 | 499.5 | 58.4 | 19 | 102.1 | 4.7 | 286.6 | 6.3 | 258.5 | 262.3 | 518.2 | 724.6 | 379.6 | 425.9 | 605.5 | 800.6 | 690.1 | 575.7 | 682.8 | 488 | 550.9 | 621.9 | 542 | 396.9 | 520.9 | 302.9 | 318.2 | 313.6 | 301 | 307.9 | 321.1 | 323.6 | 290
1353 | 1132 | 474 | 189.6 | 221.6315 | 313.8 | 288.7 | 297.8 | 301.5 | 499.3 | 58.3 | 19 | 102.2 | 4.7 | 273.6 | 6.3 | 258.7 | 262.5 | 524.3 | 721.9 | 379.8 | 426.1 | 624.5 | 806 | 691.7 | 576.1 | 692 | 483.9 | 551.6 | 630.3 | 540.1 | 397.8 | 521.3 | 303.1 | 318.5 | 313.6 | 301 | 308 | 321.6 | 323.7 | 290.3
1354 | 1133 | 471.2 | 188.48 | 220.3223 | 314.3 | 288.8 | 297 | 302.2 | 510.5 | 58.3 | 19 | 102.2 | 4.2 | 257.2 | 5.9 | 258.9 | 262.7 | 520.4 | 709 | 380.1 | 426.4 | 614.1 | 793.2 | 690 | 576.3 | 701.9 | 476.4 | 552.2 | 640.7 | 534.9 | 398.8 | 520.4 | 303.2 | 318.6 | 313.6 | 300.8 | 308.3 | 322.6 | 324.3 | 290.7
1355 | 1134 | 471.5 | 188.6 | 220.4625 | 314.9 | 288.5 | 296.7 | 302.6 | 515 | 58.4 | 19 | 102.2 | 4 | 274.6 | 6.3 | 259.1 | 262.8 | 509.8 | 704.6 | 380.3 | 426.6 | 606.4 | 787.5 | 688.6 | 576.6 | 704.6 | 470.1 | 552.5 | 646.6 | 528.7 | 399.7 | 519.2 | 303.3 | 318.9 | 313.7 | 300.8 | 308.7 | 323.3 | 325.1 | 290.9
1356 | 1135 | 471.3 | 188.52 | 220.369 | 314.1 | 288.9 | 297.4 | 303.8 | 513.7 | 58.4 | 19 | 102.2 | 4.1 | 287.2 | 6.9 | 259.3 | 263 | 506.3 | 699.2 | 380.5 | 426.8 | 609.3 | 785 | 689.1 | 576.7 | 702.2 | 466 | 553.1 | 638.7 | 525.8 | 400.7 | 518.8 | 303.5 | 319.2 | 314 | 300.9 | 308.9 | 323.6 | 325.6 | 291.1
1357 | 1136 | 471.6 | 188.64 | 220.5093 | 313.5 | 289.1 | 298 | 303.7 | 510.7 | 58.4 | 19 | 102.1 | 3.7 | 279.2 | 7 | 259.5 | 263.1 | 504.1 | 704.2 | 380.7 | 427 | 607.4 | 769.6 | 689.4 | 576.8 | 696.8 | 466.4 | 553.8 | 637.4 | 522.6 | 401.6 | 518.1 | 303.6 | 319.6 | 314.1 | 301 | 309.2 | 323.8 | 325.9 | 291.2
1358 | 1137 | 471.9 | 188.76 | 220.6496 | 312.4 | 289.3 | 298.7 | 302.9 | 509.4 | 58.4 | 19 | 102.2 | 4.2 | 286.4 | 7.1 | 259.7 | 263.3 | 504.3 | 698.9 | 380.9 | 427.3 | 602.4 | 770.3 | 689.3 | 576.9 | 687.1 | 464.2 | 554.4 | 643.7 | 521.9 | 402.5 | 517.8 | 303.7 | 319.9 | 314.3 | 301.1 | 309.3 | 323.9 | 326.1 | 291.4
1359 | 1138 | 471.9 | 188.76 | 220.6496 | 312.7 | 289.8 | 298.9 | 302.4 | 509.1 | 58.3 | 19 | 102.2 | 4.7 | 289.7 | 6.9 | 259.9 | 263.5 | 497.7 | 696.7 | 381.2 | 427.5 | 596.5 | 753.3 | 687 | 577 | 684.5 | 462.9 | 554.8 | 649 | 521.9 | 403.4 | 517.8 | 303.8 | 320.3 | 314.6 | 301.3 | 309.5 | 323.8 | 326.1 | 291.5
1360 | 1139 | 472 | 188.8 | 220.6963 | 312.3 | 290.5 | 299.5 | 302.1 | 506.3 | 58.2 | 19 | 102.2 | 4.9 | 286.3 | 6.7 | 260.1 | 263.6 | 493.4 | 706.9 | 381.4 | 427.7 | 586.1 | 757.2 | 687.6 | 577 | 688.5 | 461.9 | 555.2 | 652.4 | 519.3 | 404.4 | 517.3 | 303.9 | 320.5 | 314.9 | 301.5 | 309.6 | 323.7 | 326.1 | 291.6
1361 | 1140 | 472.3 | 188.92 | 220.8366 | 314.5 | 291.2 | 300.1 | 301.4 | 504.3 | 58.1 | 19 | 102.3 | 5.7 | 284.5 | 6.6 | 260.3 | 263.8 | 495.6 | 707.9 | 381.6 | 427.9 | 590.3 | 775.5 | 689.7 | 577.1 | 688.7 | 465.6 | 555.7 | 646.7 | 523.5 | 405.3 | 517.3 | 304.1 | 320.9 | 315.2 | 301.7 | 309.6 | 323.8 | 326.1 | 291.8
1362 | 1141 | 472.1 | 188.84 | 220.7431 | 316.8 | 291.8 | 300.2 | 301.7 | 506.6 | 58.1 | 19 | 102.2 | 5 | 290.3 | 6.5 | 260.5 | 264 | 520 | 710.4 | 381.9 | 428.1 | 620.1 | 795 | 693.9 | 577.2 | 679.1 | 475.6 | 556.1 | 650.7 | 537.5 | 406.2 | 518.9 | 304.2 | 321.1 | 315.4 | 301.8 | 309.8 | 324.2 | 326.4 | 292
1363 | 1142 | 471.7 | 188.68 | 220.556 | 317.1 | 291.6 | 299.9 | 302.1 | 511.3 | 58.3 | 19 | 102.2 | 4.9 | 290.3 | 6.4 | 260.7 | 264.3 | 535.5 | 730.1 | 382.1 | 428.3 | 637.6 | 814.2 | 696.8 | 577.4 | 665.9 | 491.1 | 556.5 | 646.2 | 544 | 407.1 | 520.1 | 304.3 | 321.2 | 315.7 | 301.9 | 310 | 324.3 | 326.5 | 292.1
1364 | 1143 | 471.3 | 188.52 | 220.369 | 317 | 291.4 | 299.7 | 302.2 | 508.7 | 58.4 | 19 | 102.3 | 5.4 | 290.6 | 6.3 | 260.8 | 264.5 | 553.8 | 739.8 | 382.3 | 428.5 | 631.2 | 816.6 | 696.1 | 577.8 | 659.4 | 506.1 | 557 | 644.5 | 552.1 | 407.9 | 521.9 | 304.5 | 321.6 | 316.2 | 302.2 | 310.1 | 324.7 | 326.7 | 292.4
1365 | 1144 | 472.2 | 188.88 | 220.7898 | 316.8 | 292.2 | 300.1 | 302.9 | 506.2 | 58.5 | 19 | 102.4 | 5.6 | 287.2 | 6.1 | 261 | 264.8 | 565.7 | 749.8 | 382.6 | 428.8 | 638.2 | 821.7 | 697.7 | 578.2 | 651.4 | 526 | 557.7 | 642 | 561.3 | 408.8 | 523.7 | 304.7 | 322 | 316.8 | 302.5 | 310.2 | 325 | 326.8 | 292.6
1366 | 1145 | 471.8 | 188.72 | 220.6028 | 316.6 | 292.8 | 300.5 | 303.6 | 505.6 | 58.7 | 19 | 102.4 | 5.1 | 287.6 | 5.9 | 261.2 | 265.2 | 570.3 | 744.4 | 382.8 | 429.1 | 644.3 | 819.8 | 698.8 | 578.8 | 649.2 | 530.4 | 558.3 | 639 | 569.2 | 409.7 | 525.2 | 304.9 | 322.3 | 317.2 | 302.8 | 310.3 | 324.9 | 326.7 | 292.7
1367 | 1146 | 473 | 189.2 | 221.1639 | 316.4 | 293.1 | 301.1 | 304.1 | 503.4 | 58.9 | 19 | 102.6 | 4.7 | 287.6 | 5.8 | 261.3 | 265.5 | 560.1 | 733.8 | 383 | 429.4 | 628.4 | 807.5 | 697 | 579.2 | 646.4 | 526.1 | 558.8 | 633.8 | 562.2 | 410.8 | 525.1 | 305.1 | 322.7 | 317.5 | 302.9 | 310.4 | 324.8 | 326.6 | 292.8
1368 | 1147 | 473.3 | 189.32 | 221.3042 | 316.2 | 292.9 | 301.2 | 304.5 | 502.8 | 59.2 | 19 | 102.6 | 4.8 | 288.3 | 5.8 | 261.5 | 265.8 | 549 | 735.3 | 383.3 | 429.6 | 623.9 | 791.3 | 695.8 | 579.7 | 662.2 | 521.5 | 559.4 | 633.5 | 558.8 | 411.9 | 525 | 305.3 | 323 | 317.9 | 303.2 | 310.6 | 324.8 | 326.6 | 292.9
1369 | 1148 | 473.5 | 189.4 | 221.3977 | 316.3 | 292.9 | 302.1 | 304.2 | 502.4 | 59.3 | 19 | 102.7 | 5.2 | 280.8 | 5.8 | 261.7 | 266 | 546.1 | 731.7 | 383.5 | 429.9 | 619.8 | 783.5 | 694.3 | 580.2 | 669.1 | 520 | 559.8 | 648.1 | 558.8 | 413 | 525 | 305.5 | 323.1 | 318.2 | 303.6 | 310.7 | 324.9 | 326.6 | 293.1
1370 | 1149 | 473.1 | 189.24 | 221.2107 | 317.6 | 293.2 | 302.6 | 302.6 | 501.6 | 59.5 | 19 | 102.9 | 4.8 | 273.8 | 5.7 | 261.9 | 266.3 | 544.9 | 723.2 | 383.8 | 430.1 | 620.8 | 774.5 | 693.6 | 580.5 | 663.8 | 511.5 | 560.2 | 652.7 | 554.9 | 413.7 | 524.6 | 305.7 | 323.3 | 318.2 | 303.6 | 310.7 | 324.9 | 326.6 | 293.3
1371 | 1150 | 473.3 | 189.32 | 221.3042 | 318.1 | 293.4 | 302.7 | 301.7 | 502.5 | 59.5 | 19 | 103 | 4.8 | 281.7 | 5.5 | 262.1 | 266.5 | 542.7 | 709.8 | 384 | 430.4 | 608.3 | 779.7 | 693.9 | 580.9 | 662.4 | 502.4 | 560.6 | 653 | 549.1 | 414.9 | 524.2 | 305.8 | 323.6 | 318.4 | 303.5 | 310.8 | 325.1 | 326.5 | 293.4
1372 | 1151 | 474.9 | 189.96 | 222.0523 | 319.3 | 293 | 302.3 | 302.4 | 502.3 | 59.6 | 19 | 103.2 | 5.1 | 278.6 | 5.4 | 262.3 | 266.7 | 555.4 | 715.4 | 384.3 | 430.7 | 616.1 | 792.1 | 697.4 | 581.2 | 681 | 513 | 561 | 648.2 | 554.1 | 415.3 | 525.2 | 306 | 323.8 | 318.7 | 303.6 | 310.9 | 325 | 326.7 | 293.5
1373 | 1152 | 474.5 | 189.8 | 221.8653 | 319.2 | 293.5 | 301.5 | 302.5 | 499.6 | 59.6 | 19 | 103.4 | 5 | 275 | 5.7 | 262.5 | 266.9 | 547.7 | 712 | 384.5 | 431 | 618.2 | 790.2 | 697.3 | 581.5 | 683.5 | 507.3 | 561.5 | 640.6 | 553.6 | 416.4 | 525.2 | 306.1 | 324 | 318.9 | 303.7 | 311 | 324.9 | 326.7 | 293.6
1374 | 1153 | 473 | 189.2 | 221.1639 | 320.1 | 292.8 | 300.3 | 301.9 | 501.4 | 59.7 | 19 | 103.5 | 5.4 | 275.3 | 6 | 262.7 | 267.1 | 533.4 | 704.8 | 384.8 | 431.2 | 611.5 | 778 | 694.4 | 581.7 | 691 | 498.7 | 562.1 | 640.5 | 545.9 | 417.4 | 524.3 | 306.3 | 324.1 | 319.1 | 303.9 | 311.1 | 325.1 | 326.8 | 293.7
1375 | 1154 | 472.2 | 188.88 | 220.7898 | 320.9 | 292.9 | 299.7 | 302 | 499.8 | 59.7 | 18.9 | 103.6 | 5.7 | 261.5 | 6.5 | 262.9 | 267.3 | 520.8 | 690.4 | 385 | 431.4 | 599.6 | 769 | 692.7 | 581.8 | 689.5 | 491.8 | 562.6 | 648 | 538.5 | 418.3 | 523.2 | 306.4 | 324.1 | 319 | 303.9 | 311.3 | 325.4 | 327.2 | 294.1
1376 | 1155 | 472.5 | 189 | 220.9301 | 322 | 292.9 | 299.5 | 302.5 | 499.2 | 59.6 | 18.9 | 103.6 | 4.9 | 257.8 | 6.4 | 263 | 267.5 | 518.6 | 684 | 385.3 | 431.6 | 593.1 | 758 | 691.3 | 581.8 | 684.7 | 487 | 563.3 | 644.6 | 534.2 | 419.5 | 522.3 | 306.5 | 323.9 | 318.7 | 303.8 | 311.4 | 325.7 | 327.4 | 294.1
1377 | 1156 | 471.3 | 188.52 | 220.369 | 323.6 | 293.1 | 298.9 | 302.9 | 499.4 | 59.6 | 18.9 | 103.6 | 5.2 | 264.7 | 5.7 | 263.2 | 267.7 | 525.2 | 669.6 | 385.5 | 431.8 | 607 | 758.8 | 691.9 | 581.7 | 683.9 | 479.1 | 563.9 | 654.7 | 534 | 420.4 | 521.9 | 306.5 | 323.6 | 318.4 | 303.6 | 311.6 | 326.3 | 327.9 | 294.3
1378 | 1157 | 472 | 188.8 | 220.6963 | 324.1 | 293.5 | 298.1 | 303 | 510.4 | 59.7 | 18.9 | 103.7 | 5.5 | 254.3 | 5.3 | 263.4 | 268 | 534.4 | 655.1 | 385.8 | 431.9 | 609.7 | 751.1 | 690.5 | 581.5 | 684.1 | 471.8 | 564.6 | 662.4 | 531.6 | 421.8 | 521.4 | 306.6 | 323.6 | 318.3 | 303.5 | 311.8 | 327.1 | 328.6 | 294.6
1379 | 1158 | 472 | 188.8 | 220.6963 | 322.7 | 293.5 | 298 | 304.8 | 519.4 | 59.7 | 18.9 | 103.7 | 5 | 249.3 | 4.9 | 263.6 | 268.2 | 538.2 | 641.7 | 386 | 432.1 | 608 | 747.9 | 689.4 | 581.2 | 682.5 | 469.2 | 565.2 | 666.7 | 526.2 | 422.7 | 520.7 | 306.7 | 323.9 | 318.4 | 303.6 | 312.1 | 327.5 | 329.3 | 294.7
1380 | 1159 | 471.8 | 188.72 | 220.6028 | 320.9 | 293.8 | 298.5 | 307.1 | 520.6 | 59.7 | 18.9 | 103.7 | 4.8 | 258.3 | 5.1 | 263.9 | 268.4 | 534 | 622.7 | 386.3 | 432.2 | 611.2 | 725.7 | 686.7 | 580.8 | 684.4 | 464.5 | 565.4 | 668.7 | 518.5 | 423.7 | 519.6 | 306.9 | 324.2 | 318.7 | 303.7 | 312.3 | 328.1 | 330.2 | 295
1381 | 1160 | 472.1 | 188.84 | 220.7431 | 319.9 | 294 | 299.7 | 308.1 | 520.6 | 59.7 | 18.9 | 103.8 | 5 | 253.1 | 5.5 | 264.1 | 268.7 | 526.2 | 611.5 | 386.5 | 432.4 | 606 | 703 | 683.8 | 580.4 | 684.7 | 457.5 | 565.9 | 665.4 | 509.3 | 425 | 518.5 | 307.1 | 324.4 | 318.9 | 303.9 | 312.6 | 328.8 | 330.9 | 295.3
1382 | 1161 | 471.2 | 188.48 | 220.3223 | 320.8 | 294.4 | 300.9 | 308.2 | 520.5 | 59.7 | 18.9 | 103.8 | 4.9 | 267.6 | 5.4 | 264.3 | 268.9 | 512.8 | 597.5 | 386.7 | 432.5 | 587 | 675.8 | 681 | 579.8 | 683.4 | 451.8 | 566.3 | 663.6 | 500.7 | 426.4 | 516.8 | 307.3 | 324.8 | 319.1 | 304.1 | 312.8 | 328.9 | 331.1 | 295.5
1383 | 1162 | 471.5 | 188.6 | 220.4625 | 323.5 | 294.9 | 301.7 | 308.4 | 512.2 | 59.8 | 18.9 | 103.6 | 4.8 | 245.2 | 5.9 | 264.5 | 269.1 | 498.9 | 583.8 | 387 | 432.6 | 569.5 | 655.6 | 677.9 | 579.1 | 682.8 | 447.1 | 566.5 | 651.4 | 493.8 | 427.7 | 515.2 | 307.5 | 325.3 | 319.2 | 304.1 | 313 | 328.8 | 331 | 295.7
1384 | 1163 | 472.6 | 189.04 | 220.9769 | 325.6 | 295.3 | 304 | 309.2 | 505.5 | 59.7 | 18.9 | 103.6 | 5.3 | 247.8 | 6.9 | 264.7 | 269.2 | 490.5 | 588.4 | 387.2 | 432.8 | 569.4 | 657.9 | 676.9 | 578.3 | 680.5 | 441.6 | 566.7 | 647.9 | 490.1 | 428.8 | 514 | 307.7 | 325.4 | 319.2 | 303.9 | 313.3 | 329.3 | 331 | 296
1385 | 1164 | 471.9 | 188.76 | 220.6496 | 325.5 | 294.8 | 306 | 310.3 | 507.6 | 59.8 | 18.9 | 103.6 | 5.1 | 247.3 | 6.8 | 264.8 | 269.5 | 491.6 | 581.7 | 387.4 | 433.1 | 575.3 | 682.7 | 676.2 | 577.5 | 681 | 437.4 | 567.1 | 653.3 | 490.5 | 429.9 | 513.2 | 307.8 | 325.3 | 319 | 303.9 | 313.5 | 329.4 | 331.2 | 296.1
1386 | 1165 | 473.1 | 189.24 | 221.2107 | 324.7 | 295.3 | 306.8 | 311.4 | 510.3 | 59.8 | 18.9 | 103.5 | 4.8 | 245.1 | 6.6 | 265 | 269.7 | 497.3 | 597 | 387.5 | 433.4 | 583.2 | 715.8 | 679.3 | 576.8 | 685.8 | 436.1 | 567.5 | 658.2 | 494.8 | 430.3 | 512.8 | 308 | 325.3 | 319 | 303.9 | 313.7 | 329.3 | 331.1 | 296.2
1387 | 1166 | 473.1 | 189.24 | 221.2107 | 323.8 | 295.7 | 306.5 | 312.3 | 512 | 59.8 | 18.9 | 103.5 | 5.1 | 241.3 | 6.4 | 265.2 | 270 | 506.9 | 617.4 | 387.7 | 433.7 | 600.6 | 738.7 | 680.4 | 576.2 | 692.5 | 438.8 | 568.2 | 661.4 | 502.7 | 431.5 | 513.2 | 308.2 | 325.3 | 318.9 | 304.1 | 313.8 | 329 | 330.9 | 296.3
1388 | 1167 | 473.3 | 189.32 | 221.3042 | 322.3 | 295.5 | 306.7 | 311.1 | 515 | 59.7 | 18.9 | 103.6 | 5 | 250.6 | 6.2 | 265.4 | 270.2 | 521.2 | 640.7 | 387.9 | 434 | 617.3 | 749.7 | 682.1 | 575.9 | 687.9 | 448.9 | 568.6 | 655.9 | 515.3 | 432.4 | 514.7 | 308.3 | 325.3 | 318.9 | 304.4 | 314 | 328.6 | 330.5 | 296.4
1389 | 1168 | 473 | 189.2 | 221.1639 | 320.3 | 295.6 | 307 | 309.3 | 513.6 | 59.7 | 18.9 | 103.7 | 4.5 | 247.5 | 6 | 265.6 | 270.3 | 522.3 | 647.2 | 388.1 | 434.3 | 621.9 | 749.6 | 681.4 | 575.7 | 681.9 | 450.9 | 568.8 | 658.9 | 518.4 | 432.6 | 515 | 308.5 | 325.4 | 319 | 304.6 | 314.1 | 328.6 | 330.3 | 296.5
1390 | 1169 | 472.6 | 189.04 | 220.9769 | 319.2 | 295.5 | 307.1 | 309.2 | 512.9 | 59.6 | 18.9 | 103.6 | 4.1 | 245.6 | 5.9 | 265.8 | 270.5 | 524.1 | 641.8 | 388.3 | 434.5 | 611.6 | 732.5 | 680.6 | 575.4 | 680.2 | 449.1 | 569.3 | 661.2 | 514 | 433.4 | 514.9 | 308.6 | 325.9 | 319.2 | 304.7 | 314.2 | 328.6 | 330.4 | 296.6
1391 | 1170 | 472.8 | 189.12 | 221.0704 | 319.1 | 295.8 | 307.4 | 309.6 | 511.7 | 59.6 | 18.9 | 103.5 | 4.5 | 248.8 | 5.5 | 265.9 | 270.7 | 525.8 | 639.7 | 388.5 | 434.8 | 632.3 | 756.9 | 681.7 | 575.2 | 681.6 | 448.7 | 569.7 | 656.8 | 512.8 | 435 | 514.6 | 308.8 | 326.1 | 319.5 | 304.9 | 314.4 | 328.9 | 330.5 | 296.8
1392 | 1171 | 472.5 | 189 | 220.9301 | 319.7 | 295.8 | 307 | 309.2 | 510.9 | 59.5 | 18.9 | 103.5 | 5 | 248.1 | 5.1 | 266.1 | 271 | 520.8 | 624.5 | 388.7 | 435.1 | 635.8 | 752.7 | 681.1 | 574.8 | 678.9 | 443.5 | 570.2 | 660 | 515.4 | 435.6 | 514.9 | 308.9 | 326.1 | 319.7 | 304.9 | 314.6 | 329.7 | 330.9 | 297.1
1393 | 1172 | 472.5 | 189 | 220.9301 | 319.3 | 295.7 | 306.1 | 310.4 | 516.5 | 59.4 | 18.9 | 103.6 | 5.7 | 248.9 | 4.9 | 266.3 | 271.2 | 521.3 | 620.4 | 388.8 | 435.4 | 623.5 | 742.7 | 679.7 | 574.5 | 678.8 | 438.5 | 570.6 | 665.3 | 508.7 | 436.9 | 514.3 | 309.1 | 326.3 | 319.9 | 305 | 314.9 | 330.8 | 331.9 | 297.5
1394 | 1173 | 472.2 | 188.88 | 220.7898 | 318.5 | 295.5 | 306 | 313.4 | 514.9 | 59.4 | 18.9 | 103.6 | 4.9 | 243.7 | 4.7 | 266.5 | 271.4 | 536.2 | 636.9 | 389 | 435.7 | 616.4 | 751.1 | 680.2 | 574.4 | 673 | 443.6 | 571.1 | 661.1 | 513.2 | 438.2 | 514.3 | 309.2 | 326.3 | 320 | 305.2 | 315.1 | 331.1 | 332.5 | 297.6
1395 | 1174 | 472.6 | 189.04 | 220.9769 | 317.3 | 295.7 | 306.6 | 314.9 | 513 | 59.4 | 18.9 | 103.6 | 5.3 | 245.8 | 4.8 | 266.7 | 271.6 | 536.8 | 641.2 | 389.2 | 436 | 618.5 | 757 | 681.7 | 574.2 | 673 | 442.4 | 571.4 | 665.4 | 514.5 | 439.2 | 514.5 | 309.4 | 326.3 | 320.2 | 305.5 | 315.3 | 331.2 | 332.9 | 297.8
1396 | 1175 | 472.5 | 189 | 220.9301 | 316.9 | 295.8 | 307.5 | 315.5 | 510.9 | 59.3 | 18.9 | 103.7 | 5.6 | 259.2 | 5.3 | 266.9 | 271.7 | 531.8 | 654.2 | 389.5 | 436.3 | 599.5 | 745.1 | 680.3 | 574.1 | 677.4 | 442.8 | 571.8 | 669.4 | 514 | 440.5 | 514.1 | 309.5 | 326.3 | 320.4 | 305.7 | 315.4 | 331.2 | 333 | 297.9
1397 | 1176 | 472.5 | 189 | 220.9301 | 319.4 | 296.4 | 306.6 | 315.2 | 511.1 | 59.3 | 18.9 | 103.7 | 5.4 | 251.2 | 5.7 | 267.1 | 272 | 526.4 | 656.2 | 389.7 | 436.7 | 588.7 | 721.8 | 678.4 | 574.1 | 675.4 | 446 | 572.3 | 671.8 | 517.3 | 441.7 | 514.3 | 309.7 | 326.5 | 320.8 | 306 | 315.5 | 331 | 332.8 | 298.1
1398 | 1177 | 472.5 | 189 | 220.9301 | 321.5 | 296.2 | 306.7 | 313.9 | 508 | 59.3 | 18.9 | 103.7 | 5.6 | 250.4 | 6 | 267.2 | 272.1 | 516.1 | 659.7 | 389.9 | 437 | 587.5 | 719.1 | 679.3 | 574.2 | 668.8 | 447.4 | 572.8 | 661.2 | 514.9 | 443 | 514.5 | 309.9 | 327 | 321.1 | 306.2 | 315.6 | 330.8 | 332.7 | 298.2
1399 | 1178 | 472.5 | 189 | 220.9301 | 322.7 | 295.9 | 306.9 | 312.3 | 504.3 | 59.3 | 18.9 | 103.8 | 5.3 | 257.9 | 6.1 | 267.4 | 272.3 | 512.2 | 648.2 | 390.2 | 437.4 | 577.2 | 707.7 | 677.5 | 574.3 | 666.6 | 447 | 573.1 | 654 | 514.1 | 443.9 | 514.4 | 310.1 | 327.5 | 321.6 | 306.2 | 315.7 | 330.8 | 332.8 | 298.4
1400 | 1179 | 472.2 | 188.88 | 220.7898 | 323.4 | 295.4 | 306.5 | 312.3 | 507.5 | 59.3 | 18.9 | 103.8 | 5 | 258.5 | 6.4 | 267.6 | 272.4 | 502.8 | 628.5 | 390.4 | 437.7 | 571.6 | 701.7 | 676 | 574.4 | 666.5 | 444.2 | 573.4 | 648.9 | 508.7 | 445.1 | 513.5 | 310.3 | 328 | 322.3 | 306.3 | 315.9 | 330.9 | 333.1 | 298.5
1401 | 1180 | 472.8 | 189.12 | 221.0704 | 323.6 | 295 | 306 | 312.2 | 508.2 | 59.3 | 18.9 | 103.9 | 5 | 255.8 | 6.5 | 267.8 | 272.7 | 491 | 610.3 | 390.6 | 438 | 566.4 | 681.3 | 673.1 | 574.4 | 665.6 | 441.5 | 573.6 | 639 | 503.7 | 446 | 512.7 | 310.5 | 328.5 | 322.7 | 306.6 | 316 | 331 | 333.6 | 298.7
1402 | 1181 | 473.3 | 189.32 | 221.3042 | 325.4 | 294.5 | 305.6 | 312.2 | 506.5 | 59.3 | 18.9 | 104.1 | 5.4 | 254.4 | 5.8 | 268 | 272.9 | 482.7 | 599.8 | 390.8 | 438.3 | 568.7 | 671.5 | 672.3 | 574.2 | 660.8 | 438.7 | 573.7 | 631.5 | 498.8 | 447 | 511.8 | 310.6 | 328.6 | 322.7 | 306.6 | 316.2 | 331.1 | 334 | 298.9
1403 | 1182 | 472.7 | 189.08 | 221.0236 | 326.7 | 293.3 | 305.8 | 311.4 | 503.8 | 59.4 | 18.9 | 104.3 | 5.4 | 243.7 | 5.6 | 268.2 | 273 | 478 | 603.8 | 391.1 | 438.6 | 562.2 | 670.2 | 669.8 | 573.9 | 649.6 | 435.1 | 573.8 | 631.5 | 490.9 | 448 | 510.7 | 310.8 | 328.7 | 322.8 | 306.7 | 316.3 | 331 | 334 | 298.9
1404 | 1183 | 473.1 | 189.24 | 221.2107 | 327.6 | 292.9 | 306.2 | 309.4 | 499.4 | 59.4 | 18.9 | 104.4 | 6.3 | 235 | 6 | 268.4 | 273.2 | 468.9 | 598.3 | 391.3 | 438.9 | 574.8 | 663.4 | 667.6 | 573.5 | 635.6 | 431.9 | 574 | 633.4 | 488.3 | 448.5 | 509.7 | 311 | 328.8 | 322.9 | 306.7 | 316.5 | 330.9 | 334.2 | 299
1405 | 1184 | 473.1 | 189.24 | 221.2107 | 329.2 | 293 | 306.9 | 307.9 | 495 | 59.4 | 18.9 | 104.5 | 5.9 | 241.7 | 6.4 | 268.5 | 273.4 | 461.3 | 587.1 | 391.5 | 439.1 | 573.9 | 646.5 | 665.2 | 573 | 634.9 | 428.3 | 574.3 | 633.3 | 487.2 | 449.2 | 508.9 | 311.1 | 329 | 322.9 | 306.8 | 316.6 | 331.1 | 334.4 | 299.2
1406 | 1185 | 473 | 189.2 | 221.1639 | 331.3 | 293 | 307.7 | 310.5 | 496.2 | 59.4 | 18.9 | 104.6 | 5.7 | 247.5 | 6.7 | 268.7 | 273.6 | 459.4 | 590.7 | 391.7 | 439.3 | 575.5 | 652.4 | 663.7 | 572.5 | 630.8 | 423.6 | 574.5 | 627.3 | 482.9 | 449.6 | 508 | 311.3 | 329.3 | 323.2 | 306.9 | 316.8 | 331.3 | 334.5 | 299.3
1407 | 1186 | 473 | 189.2 | 221.1639 | 332.3 | 293.3 | 308.9 | 312.5 | 498.2 | 59.4 | 18.9 | 104.6 | 5.8 | 271.9 | 6.5 | 268.9 | 273.7 | 455.6 | 584.1 | 391.9 | 439.5 | 576.7 | 656.4 | 661.4 | 571.9 | 619.3 | 418 | 574.6 | 635 | 479.8 | 449.9 | 507.2 | 311.4 | 329.5 | 323.5 | 306.9 | 317.1 | 332 | 334.9 | 299.6
1408 | 1187 | 473 | 189.2 | 221.1639 | 332.7 | 294.1 | 310 | 314 | 498.9 | 59.4 | 18.9 | 104.7 | 6.2 | 269.6 | 5.8 | 269.1 | 274 | 449.8 | 573.1 | 392.1 | 439.8 | 572.6 | 640.6 | 659 | 571.4 | 605.2 | 415.4 | 574.6 | 639.2 | 475.3 | 450.6 | 506.2 | 311.7 | 329.8 | 323.8 | 307.1 | 317.5 | 332.7 | 335.6 | 299.9
1409 | 1188 | 472.7 | 189.08 | 221.0236 | 332.6 | 294.5 | 310 | 315.6 | 498.7 | 59.3 | 18.9 | 104.6 | 6.4 | 226 | 5.3 | 269.3 | 274.2 | 442.3 | 573.4 | 392.3 | 440.1 | 572 | 629.5 | 657.1 | 570.7 | 531.2 | 412.7 | 574.8 | 631.3 | 469.9 | 450.8 | 505.3 | 311.9 | 330 | 323.8 | 307.2 | 317.9 | 333.8 | 336.9 | 300.4
1410 | 1189 | 471.1 | 188.44 | 220.2755 | 332 | 294.5 | 310.8 | 318.5 | 498.9 | 59.3 | 18.9 | 104.6 | 6.1 | 240.3 | 5.3 | 269.5 | 274.5 | 435.6 | 573.1 | 392.5 | 440.3 | 576.2 | 637.8 | 655.1 | 569.9 | 436 | 409.8 | 574.5 | 628.1 | 469.1 | 451.7 | 504.4 | 312 | 330.2 | 323.8 | 307.2 | 318.2 | 334.7 | 337.8 | 300.8
1411 | 1190 | 471.7 | 188.68 | 220.556 | 331 | 295 | 312.6 | 321.3 | 500.6 | 59.2 | 18.9 | 104.5 | 5.6 | 240.7 | 5.7 | 269.6 | 274.8 | 439.2 | 574.4 | 392.7 | 440.5 | 571.2 | 660.3 | 654.3 | 569.1 | 589.7 | 405.8 | 574.2 | 639.8 | 465.9 | 451.2 | 503.4 | 312.3 | 330.5 | 324 | 307.3 | 318.6 | 335.3 | 338.7 | 300.9
1412 | 1191 | 471.8 | 188.72 | 220.6028 | 331 | 295.4 | 314 | 323.7 | 503.3 | 59.3 | 18.9 | 104.5 | 5.1 | 237 | 7.8 | 269.8 | 275 | 438.8 | 576.8 | 392.9 | 440.7 | 573.1 | 671.5 | 653.7 | 568.5 | 462.2 | 404.1 | 574.6 | 651 | 475.1 | 451.2 | 502.7 | 312.5 | 330.7 | 324.1 | 307.4 | 319 | 336.2 | 340 | 301.1
1413 | 1192 | 472.3 | 188.92 | 220.8366 | 330.8 | 296.4 | 315 | 325.5 | 507.9 | 59.3 | 18.9 | 104.5 | 4.8 | 251 | 9.3 | 270 | 275.2 | 443.1 | 573.5 | 393.1 | 440.9 | 572.5 | 665 | 652.3 | 567.8 | 478.9 | 399.9 | 574.6 | 661.6 | 475.3 | 450.7 | 502.3 | 312.7 | 331 | 324.3 | 307.6 | 319.5 | 337.1 | 340.7 | 301.4
1414 | 1193 | 472.5 | 189 | 220.9301 | 330.8 | 297.7 | 314.7 | 326.8 | 509.4 | 59.5 | 18.9 | 104.5 | 5.2 | 252.9 | 9.1 | 270.2 | 275.5 | 442.1 | 579.3 | 393.3 | 441.1 | 574.6 | 655.1 | 650.2 | 567.2 | 602 | 399.2 | 575 | 662.3 | 476.7 | 451.1 | 501.8 | 312.9 | 331.2 | 324.7 | 307.8 | 319.8 | 337.4 | 341.4 | 301.6
1415 | 1194 | 471.6 | 188.64 | 220.5093 | 332.2 | 298.6 | 315.4 | 325.3 | 510 | 59.6 | 18.9 | 104.5 | 5.2 | 256.8 | 7.8 | 270.4 | 275.7 | 445.4 | 605.5 | 393.5 | 441.3 | 583.5 | 671.6 | 651 | 566.9 | 429.4 | 407.6 | 575.3 | 660.4 | 486.5 | 452 | 502.1 | 313.2 | 331.5 | 325.3 | 308.3 | 320.1 | 337.5 | 341.8 | 301.7
1416 | 1195 | 471.9 | 188.76 | 220.6496 | 335.7 | 299.2 | 316.2 | 323.4 | 510.2 | 59.6 | 18.9 | 104.6 | 5.3 | 260.3 | 6.9 | 270.6 | 275.9 | 459.2 | 645.2 | 393.7 | 441.6 | 595.2 | 685.3 | 653 | 566.8 | 562.9 | 423.5 | 575.7 | 646.2 | 491.3 | 450.8 | 503.3 | 313.4 | 331.8 | 325.8 | 309 | 320.3 | 337.3 | 341.9 | 301.8
1417 | 1196 | 472.5 | 189 | 220.9301 | 338.5 | 299.3 | 316.9 | 321.2 | 511.2 | 59.6 | 18.9 | 104.7 | 5.6 | 251 | 5.9 | 270.8 | 276.1 | 462.4 | 665.6 | 393.9 | 441.8 | 603.9 | 693 | 653 | 566.9 | 633.2 | 434.7 | 576.3 | 642.9 | 495.2 | 450.2 | 503.1 | 313.7 | 332 | 326.1 | 309.2 | 320.5 | 337.3 | 342 | 302
1418 | 1197 | 472 | 188.8 | 220.6963 | 339.9 | 298.8 | 317.3 | 318.8 | 513.7 | 59.6 | 18.9 | 104.9 | 5.7 | 257.5 | 5.3 | 271 | 276.3 | 469.6 | 685.9 | 394.1 | 442.1 | 590.1 | 696.5 | 653.6 | 567.2 | 376.6 | 455.5 | 576.4 | 644.5 | 505.1 | 450.3 | 503.7 | 314 | 332.6 | 326.7 | 309.5 | 320.7 | 337.2 | 342.1 | 302.2
1419 | 1198 | 471.9 | 188.76 | 220.6496 | 340.6 | 298.5 | 316.9 | 317.2 | 518.9 | 59.6 | 18.8 | 105 | 5.8 | 243 | 5.1 | 271.1 | 276.5 | 484.1 | 714.8 | 394.3 | 442.4 | 592.3 | 698.2 | 655.6 | 567.6 | 632.6 | 492.6 | 576.8 | 646.4 | 515.4 | 449.3 | 505.8 | 314.3 | 333.3 | 327.5 | 309.9 | 320.8 | 337 | 342.2 | 302.4
1420 | 1199 | 472.6 | 189.04 | 220.9769 | 341 | 298.7 | 316.5 | 317.3 | 522.4 | 59.5 | 18.8 | 105.1 | 5.7 | 266.9 | 4.7 | 271.3 | 276.7 | 490 | 726.5 | 394.4 | 442.8 | 580 | 713.9 | 656.8 | 568.1 | 631.9 | 502.9 | 577.1 | 644.4 | 521.9 | 448 | 507.8 | 314.7 | 334.4 | 328.5 | 310.5 | 321 | 337.1 | 342.3 | 302.5
1421 | 1200 | 472.8 | 189.12 | 221.0704 | 341.4 | 299.2 | 316.6 | 317.6 | 522.6 | 59.5 | 18.8 | 105.2 | 5.2 | 274.2 | 4.7 | 271.5 | 276.9 | 495.3 | 731.8 | 394.6 | 443.1 | 587.4 | 736.6 | 659.3 | 568.6 | 453.3 | 506.8 | 577.6 | 642.8 | 522.2 | 448 | 508.2 | 315.1 | 335.1 | 328.9 | 310.7 | 321.1 | 337.2 | 342.3 | 302.7
1422 | 1201 | 473.2 | 189.28 | 221.2574 | 341 | 299.8 | 316.1 | 317.6 | 521.7 | 59.6 | 18.8 | 105.2 | 5.2 | 256.1 | 4.9 | 271.7 | 277.1 | 496.8 | 717.6 | 394.8 | 443.4 | 599.2 | 750.4 | 661.3 | 569.1 | 654.7 | 503.5 | 578.2 | 649.9 | 527.8 | 448.1 | 509.1 | 315.4 | 335.6 | 329.2 | 310.6 | 321.3 | 337.4 | 342.2 | 302.9
1423 | 1202 | 473.2 | 189.28 | 221.2574 | 340 | 299.6 | 315.8 | 317.8 | 520.8 | 59.6 | 18.8 | 105.3 | 6.3 | 257 | 5.2 | 271.9 | 277.3 | 496.5 | 716 | 395 | 443.7 | 607.5 | 763.7 | 662.7 | 569.4 | 580.2 | 500.8 | 578.7 | 663.4 | 534.2 | 448.1 | 510 | 315.7 | 335.9 | 329.6 | 310.6 | 321.5 | 337.5 | 342.3 | 303.1
1424 | 1203 | 473.2 | 189.28 | 221.2574 | 339.1 | 299.7 | 314.5 | 318.4 | 522.9 | 59.6 | 18.8 | 105.4 | 5.9 | 251.9 | 5.1 | 272.1 | 277.5 | 497.4 | 725.6 | 395.2 | 443.9 | 615.7 | 790.3 | 666.7 | 569.7 | 479.8 | 497.1 | 579.3 | 671.4 | 534 | 447.6 | 510.3 | 316 | 336.3 | 329.8 | 310.7 | 321.8 | 338.2 | 342.7 | 303.5
1425 | 1204 | 473 | 189.2 | 221.1639 | 338.7 | 299.9 | 314.1 | 319.1 | 524.6 | 59.7 | 18.8 | 105.4 | 5 | 246.6 | 5.5 | 272.2 | 277.7 | 501.4 | 726.1 | 395.3 | 444.2 | 624.1 | 795.8 | 669.9 | 570.1 | 664.9 | 495.7 | 579.8 | 678.3 | 534.8 | 447 | 510.6 | 316.3 | 336.3 | 329.8 | 310.7 | 322.1 | 339 | 343.4 | 303.8
1426 | 1205 | 472.5 | 189 | 220.9301 | 338.6 | 300.2 | 313.5 | 319.1 | 528.6 | 59.7 | 18.8 | 105.4 | 4.4 | 252.8 | 5.2 | 272.4 | 277.9 | 500 | 719.4 | 395.5 | 444.4 | 625.3 | 783.3 | 669.1 | 570.6 | 529.3 | 492 | 580.4 | 679.4 | 534.2 | 446.7 | 510.5 | 316.5 | 336.5 | 330 | 310.7 | 322.4 | 339.6 | 343.9 | 304.1
1427 | 1206 | 473.1 | 189.24 | 221.2107 | 337.7 | 300.1 | 312.3 | 319.6 | 530.7 | 59.8 | 18.8 | 105.3 | 4.9 | 260.9 | 5.1 | 272.6 | 278.1 | 507.1 | 738.8 | 395.7 | 444.6 | 626.6 | 793.7 | 673.4 | 571.2 | 542.3 | 509.5 | 580.7 | 673.2 | 542.4 | 446.7 | 512.1 | 316.7 | 336.6 | 330.5 | 311.1 | 322.7 | 339.8 | 344.3 | 304.3
1428 | 1207 | 472.4 | 188.96 | 220.8834 | 336.9 | 300.4 | 312 | 320.3 | 528.6 | 59.8 | 18.8 | 105.3 | 5.5 | 256.5 | 5.2 | 272.7 | 278.3 | 517 | 741.6 | 395.8 | 444.8 | 629.7 | 813.1 | 677 | 571.8 | 680.9 | 514 | 580.8 | 664.4 | 555.3 | 446.7 | 514.9 | 316.9 | 337 | 331 | 311.5 | 323 | 340.3 | 344.5 | 304.6
1429 | 1208 | 472.6 | 189.04 | 220.9769 | 336.7 | 301.1 | 312.3 | 320.6 | 533.7 | 59.8 | 18.8 | 105.2 | 5.2 | 265.2 | 5.2 | 272.9 | 278.5 | 521.1 | 742.2 | 396 | 445.1 | 639.1 | 812.9 | 678.1 | 572.5 | 462.6 | 509 | 581.2 | 653.8 | 555.6 | 447.1 | 515.5 | 317 | 337.4 | 331.5 | 312 | 323.3 | 340.8 | 344.9 | 304.8
1430 | 1209 | 472.4 | 188.96 | 220.8834 | 336.8 | 302.7 | 311.9 | 320.8 | 535.6 | 59.9 | 18.8 | 105.1 | 5.1 | 265.2 | 5 | 273.1 | 278.7 | 525.3 | 741.2 | 396.1 | 445.4 | 628.7 | 804.2 | 679.2 | 573.1 | 608 | 510.7 | 581.7 | 649.8 | 554.4 | 447.6 | 515.8 | 317.2 | 337.8 | 331.9 | 312.3 | 323.6 | 341.3 | 345.1 | 305
1431 | 1210 | 472.5 | 189 | 220.9301 | 336.3 | 303.7 | 312.2 | 321 | 535.9 | 59.9 | 18.8 | 105.1 | 5.1 | 241.9 | 4.4 | 273.3 | 278.9 | 515.4 | 728.4 | 396.3 | 445.6 | 613.5 | 802 | 678.3 | 573.7 | 692.5 | 501 | 581.8 | 658.8 | 550.7 | 448 | 515.9 | 317.4 | 338.1 | 332.1 | 312.3 | 323.8 | 341.8 | 345.4 | 305.3
1432 | 1211 | 472.3 | 188.92 | 220.8366 | 336.7 | 303.6 | 312.3 | 321 | 540.1 | 59.9 | 18.8 | 105.3 | 5 | 244.1 | 4.3 | 273.4 | 279.1 | 504.6 | 714.7 | 396.5 | 445.7 | 606 | 782.4 | 676.1 | 574 | 427.1 | 490 | 582.4 | 674.7 | 543 | 448.4 | 515.3 | 317.6 | 338.3 | 332.1 | 312.3 | 324.1 | 342.6 | 345.8 | 305.5
1433 | 1212 | 472.1 | 188.84 | 220.7431 | 337.8 | 304.2 | 312.9 | 322 | 539.2 | 59.9 | 18.8 | 105.4 | 4.9 | 261.6 | 4.6 | 273.6 | 279.3 | 497 | 720.2 | 396.6 | 445.9 | 601.6 | 779.7 | 676.1 | 574.2 | 672.5 | 486 | 582.8 | 681.8 | 541.2 | 448.8 | 515 | 317.8 | 338.4 | 332.2 | 312.4 | 324.4 | 343.3 | 346.3 | 305.9
1434 | 1213 | 472.1 | 188.84 | 220.7431 | 338.2 | 304.9 | 313.3 | 323.2 | 537.3 | 60 | 18.8 | 105.6 | 5.4 | 265.6 | 5.6 | 273.8 | 279.5 | 500 | 728.9 | 396.8 | 446.1 | 619.8 | 800.5 | 679.4 | 574.4 | 659.1 | 482.7 | 583.3 | 695.9 | 544.6 | 449.3 | 515.3 | 317.9 | 338.3 | 332.2 | 312.5 | 324.8 | 344.3 | 346.9 | 306.3
1435 | 1214 | 472.1 | 188.84 | 220.7431 | 337.8 | 305 | 312.3 | 323.2 | 544 | 60 | 18.8 | 105.8 | 5.7 | 256.5 | 5.9 | 273.9 | 279.7 | 504.8 | 722 | 396.9 | 446.3 | 640.9 | 813.8 | 681.1 | 574.4 | 443.4 | 479.8 | 583.5 | 691.5 | 554.8 | 449.7 | 516.6 | 318 | 338.1 | 332.1 | 312.5 | 325.2 | 345.6 | 348 | 306.7
1436 | 1215 | 472.3 | 188.92 | 220.8366 | 338.3 | 305.3 | 312.1 | 324.6 | 549.7 | 60 | 18.8 | 105.8 | 5.9 | 269.3 | 6.3 | 274.1 | 280 | 513 | 730.2 | 397.1 | 446.4 | 664.5 | 817.2 | 683.9 | 574.5 | 691.2 | 486.3 | 583.6 | 684.4 | 565.4 | 450.2 | 517.6 | 318.1 | 338 | 332.4 | 312.7 | 325.6 | 346.1 | 348.7 | 307
1437 | 1216 | 472.7 | 189.08 | 221.0236 | 338.3 | 306.5 | 312 | 325.1 | 553 | 60.1 | 18.8 | 105.9 | 5.1 | 282.3 | 6 | 274.3 | 280.2 | 521.8 | 727.7 | 397.2 | 446.6 | 666.4 | 814.8 | 685.9 | 574.7 | 602.9 | 489.7 | 583.8 | 674.9 | 569.3 | 450.5 | 518.3 | 318.2 | 338.2 | 332.6 | 313.1 | 326.1 | 346.8 | 349.4 | 307.2
1438 | 1217 | 472.6 | 189.04 | 220.9769 | 336.8 | 307.8 | 312.9 | 324 | 550.9 | 60.2 | 18.8 | 105.9 | 5.4 | 261.6 | 5.7 | 274.5 | 280.4 | 530.3 | 743.9 | 397.4 | 446.9 | 653.9 | 818.5 | 689.6 | 574.9 | 493.6 | 509.7 | 584.1 | 667.8 | 572.7 | 450.9 | 519.4 | 318.4 | 338.5 | 333.1 | 313.5 | 326.3 | 347 | 349.6 | 307.4
1439 | 1218 | 472.2 | 188.88 | 220.7898 | 335.3 | 308.6 | 314.9 | 323.7 | 551.3 | 60.3 | 18.8 | 106 | 5.2 | 250.3 | 5.5 | 274.7 | 280.6 | 542.2 | 750.3 | 397.5 | 447 | 641.7 | 798.7 | 688.5 | 575.3 | 705.3 | 529.6 | 584.6 | 666.2 | 575.8 | 451.4 | 521.7 | 318.6 | 339.2 | 334 | 314.1 | 326.5 | 346.5 | 349.3 | 307.5
1440 | 1219 | 471.9 | 188.76 | 220.6496 | 334 | 307.9 | 316.5 | 323.3 | 563.5 | 60.4 | 18.8 | 106.1 | 5.5 | 266 | 5.6 | 274.8 | 280.8 | 548 | 754.5 | 397.7 | 447.2 | 630 | 797.5 | 689.9 | 575.8 | 554.5 | 541 | 585.1 | 673.9 | 577.6 | 451.8 | 523 | 318.9 | 339.5 | 334.4 | 314.5 | 326.5 | 345.9 | 348.9 | 307.5
1441 | 1220 | 472.9 | 189.16 | 221.1171 | 334.9 | 307.8 | 317.5 | 323.3 | 564.8 | 60.5 | 18.8 | 106.2 | 5 | 268.4 | 5.9 | 275 | 281 | 555.1 | 768.1 | 397.9 | 447.5 | 637.9 | 813.6 | 693.3 | 576.4 | 570.3 | 552.3 | 585.7 | 672.7 | 582.2 | 452.2 | 524.7 | 319.2 | 340 | 335.1 | 314.7 | 326.6 | 345.2 | 348.3 | 307.7
1442 | 1221 | 472.2 | 188.88 | 220.7898 | 335.5 | 308.6 | 317.4 | 323.2 | 561 | 60.7 | 18.8 | 106.2 | 4.8 | 261.4 | 5.9 | 275.2 | 281.3 | 564.3 | 768.3 | 398 | 447.7 | 638.6 | 799.8 | 694.7 | 577 | 701.9 | 570 | 586.1 | 659.1 | 591.3 | 452.7 | 527.3 | 319.6 | 340.3 | 335.6 | 315 | 326.7 | 344.7 | 347.9 | 307.8
1443 | 1222 | 472.6 | 189.04 | 220.9769 | 337.4 | 308.4 | 317.4 | 322.9 | 563.4 | 60.8 | 18.8 | 106.3 | 4.8 | 264.7 | 5.6 | 275.3 | 281.5 | 576.7 | 773.7 | 398.2 | 448 | 634.2 | 775.9 | 693.9 | 577.7 | 498.6 | 592 | 586.6 | 642.8 | 596.8 | 453.1 | 529.8 | 320 | 340.9 | 336.2 | 315.5 | 326.7 | 344.2 | 347.5 | 307.9
1444 | 1223 | 472.4 | 188.96 | 220.8834 | 337.9 | 308.6 | 318.2 | 322.6 | 571.9 | 60.9 | 18.8 | 106.4 | 5.2 | 272.8 | 5.5 | 275.5 | 281.7 | 597.4 | 781.6 | 398.4 | 448.3 | 632.5 | 744.2 | 693.1 | 578.5 | 631.9 | 613.8 | 586.9 | 633.8 | 605.2 | 453.5 | 533 | 320.4 | 341.3 | 336.7 | 316 | 326.7 | 343.9 | 347.1 | 308
1445 | 1224 | 472.6 | 189.04 | 220.9769 | 338.1 | 308.9 | 319.5 | 322.7 | 585.3 | 60.9 | 18.8 | 106.5 | 5.7 | 270.4 | 5.7 | 275.7 | 281.9 | 597.9 | 789.4 | 398.5 | 448.5 | 630.3 | 761.7 | 695 | 579.3 | 696.2 | 623.6 | 587.1 | 630.2 | 608.5 | 454 | 535.3 | 320.9 | 341.7 | 337.3 | 316.2 | 326.7 | 343.4 | 346.8 | 308.1
1446 | 1225 | 473.1 | 189.24 | 221.2107 | 338.9 | 309.2 | 320.5 | 322.9 | 580.1 | 60.9 | 18.8 | 106.6 | 5.1 | 257.8 | 5.5 | 275.9 | 282.2 | 608 | 792.8 | 398.7 | 448.9 | 637.8 | 791.8 | 699 | 580.1 | 438.2 | 630.5 | 587.6 | 638.1 | 609.8 | 454.4 | 536.6 | 321.3 | 342 | 337.5 | 316.2 | 326.8 | 343.3 | 346.5 | 308.3
1447 | 1226 | 472.4 | 188.96 | 220.8834 | 338.8 | 309.5 | 321.3 | 322.5 | 571.1 | 60.9 | 18.8 | 106.6 | 4.8 | 251.2 | 6 | 276.1 | 282.4 | 606.6 | 782.9 | 398.8 | 449.2 | 640.6 | 797.6 | 701.2 | 580.9 | 682 | 624.2 | 587.9 | 629.7 | 607.1 | 454.9 | 537.8 | 321.7 | 342.4 | 338 | 316.3 | 326.8 | 343 | 346.3 | 308.5
1448 | 1227 | 472.9 | 189.16 | 221.1171 | 337.4 | 309.8 | 321.6 | 323 | 563.8 | 60.9 | 18.8 | 106.5 | 5.4 | 245.2 | 6.6 | 276.2 | 282.6 | 604.7 | 770.5 | 399 | 449.5 | 634.1 | 784 | 699.2 | 581.8 | 672.4 | 617.6 | 588.4 | 634.8 | 609.4 | 455.3 | 539.9 | 322 | 342.9 | 338.6 | 316.5 | 326.9 | 342.9 | 346.3 | 308.6
1449 | 1228 | 473.4 | 189.36 | 221.3509 | 335.8 | 312.2 | 321.6 | 323.7 | 563 | 61 | 18.8 | 106.4 | 5.6 | 251.9 | 6.8 | 276.4 | 282.9 | 598.5 | 771.8 | 399.1 | 449.8 | 632 | 779.9 | 699.8 | 582.5 | 447.8 | 601.6 | 588.8 | 629.8 | 604.2 | 455.7 | 539.4 | 322.3 | 343.2 | 338.8 | 316.8 | 326.9 | 342.6 | 346.1 | 308.7
1450 | 1229 | 470.9 | 188.36 | 220.182 | 334 | 313.1 | 321.6 | 323.8 | 559.7 | 61 | 18.8 | 106.4 | 5 | 274.7 | 6.6 | 276.5 | 283.1 | 592.1 | 772.2 | 399.3 | 450 | 628.5 | 781.7 | 699.7 | 583.3 | 708 | 597.5 | 589.3 | 639.2 | 604 | 456.2 | 539.6 | 322.6 | 343.2 | 338.8 | 316.9 | 326.9 | 342.8 | 345.8 | 308.9
1451 | 1230 | 468.1 | 187.24 | 218.8728 | 334.3 | 312.4 | 321.5 | 323 | 558.6 | 61.1 | 18.8 | 106.4 | 5.7 | 250.3 | 7 | 276.7 | 283.3 | 582.5 | 771.9 | 399.4 | 450.3 | 621.1 | 790.5 | 700.1 | 583.9 | 619.3 | 591.6 | 589.7 | 640.3 | 607.8 | 456.6 | 540.7 | 322.8 | 343 | 338.6 | 317 | 327 | 343 | 345.5 | 309
1452 | 1231 | 470 | 188 | 219.7612 | 334.6 | 313.4 | 321.7 | 321.5 | 554.4 | 61.1 | 18.8 | 106.6 | 5.7 | 252.8 | 8.1 | 276.9 | 283.6 | 581 | 771.4 | 399.6 | 450.5 | 620.1 | 793.5 | 700.8 | 584.5 | 509.2 | 581.5 | 590.1 | 649.5 | 608.4 | 457.1 | 541.6 | 323 | 343 | 338.4 | 317 | 327.1 | 342.9 | 345.6 | 309.2
1453 | 1232 | 471.7 | 188.68 | 220.556 | 335.3 | 313.8 | 321.2 | 320.2 | 554 | 61.1 | 18.8 | 106.7 | 6.1 | 255.8 | 8.4 | 277 | 283.8 | 581.4 | 773.2 | 399.7 | 450.7 | 616.1 | 784.1 | 701 | 584.9 | 719.2 | 572.9 | 590.7 | 656.3 | 602.3 | 457.5 | 541.3 | 323.1 | 343 | 338.2 | 317.2 | 327.2 | 342.8 | 345.8 | 309.3
1454 | 1233 | 472.6 | 189.04 | 220.9769 | 335.9 | 313.8 | 321.2 | 320.2 | 551.4 | 61.1 | 18.8 | 106.9 | 5.9 | 259 | 8.4 | 277.2 | 284.1 | 574.5 | 752.1 | 399.9 | 450.9 | 603.8 | 770.1 | 698.1 | 585.5 | 722.9 | 563.9 | 591.4 | 653.5 | 593.6 | 457.9 | 541 | 323.2 | 343.1 | 337.9 | 317.3 | 327.2 | 342.9 | 346 | 309.5
1455 | 1234 | 472.5 | 189 | 220.9301 | 335.4 | 313 | 321 | 320.2 | 547.7 | 61 | 18.8 | 107 | 6.6 | 258.7 | 8 | 277.4 | 284.3 | 573.7 | 741.8 | 400 | 451.1 | 592.5 | 770.1 | 698.4 | 585.9 | 724.5 | 564.2 | 592 | 660.8 | 591.4 | 458.4 | 542.2 | 323.4 | 343 | 337.8 | 317.3 | 327.4 | 343.6 | 346.2 | 309.8
1456 | 1235 | 471.6 | 188.64 | 220.5093 | 334.5 | 313.4 | 320.7 | 320.7 | 541.2 | 61 | 18.8 | 107.1 | 6.2 | 269.5 | 7.9 | 277.6 | 284.6 | 584.4 | 741.1 | 400.2 | 451.2 | 596.7 | 765.8 | 698.2 | 586.3 | 712.7 | 561.8 | 592.6 | 657.5 | 592.8 | 458.8 | 543.9 | 323.5 | 343 | 337.4 | 317.5 | 327.5 | 343.6 | 346.3 | 309.9
1457 | 1236 | 471.6 | 188.64 | 220.5093 | 334 | 313 | 319.2 | 321.6 | 533 | 61.1 | 18.8 | 107.2 | 6 | 286.4 | 7.9 | 277.7 | 284.9 | 577.9 | 731.3 | 400.3 | 451.4 | 622.4 | 769.5 | 698.3 | 586.5 | 708.3 | 551.4 | 593.2 | 654.2 | 589.6 | 459.3 | 543.8 | 323.6 | 342.6 | 337 | 317.3 | 327.6 | 343.6 | 346.2 | 310.1
1458 | 1237 | 471.7 | 188.68 | 220.556 | 334.5 | 312.2 | 319.1 | 322.1 | 540.3 | 61 | 18.8 | 107.3 | 6.1 | 285.1 | 7 | 277.9 | 285.1 | 573.5 | 738.1 | 400.5 | 451.6 | 629 | 777.7 | 697.6 | 586.7 | 716.4 | 545.2 | 593.9 | 656.9 | 587 | 459.7 | 544.1 | 323.7 | 342.7 | 337 | 317.3 | 327.8 | 343.9 | 346.2 | 310.3
1459 | 1238 | 471.7 | 188.68 | 220.556 | 334.6 | 312.4 | 318.3 | 321.8 | 543.4 | 61 | 18.8 | 107.5 | 5.8 | 268.4 | 6.3 | 278.1 | 285.4 | 570.8 | 747.2 | 400.6 | 451.7 | 626.8 | 787.8 | 699.3 | 586.9 | 720.7 | 535.2 | 594.3 | 664.6 | 586.7 | 460.2 | 543.9 | 323.8 | 342.8 | 337.1 | 317.5 | 327.9 | 344.2 | 346.3 | 310.5
1460 | 1239 | 471.8 | 188.72 | 220.6028 | 335.3 | 313.2 | 317.7 | 321.7 | 542.6 | 61.1 | 18.8 | 107.6 | 5.7 | 269.8 | 5.9 | 278.2 | 285.7 | 568.2 | 749.9 | 400.8 | 451.9 | 625.2 | 787.1 | 701.3 | 587.2 | 725 | 534.2 | 595 | 674.1 | 585.2 | 460.6 | 543.9 | 323.9 | 342.9 | 337.1 | 317.6 | 328.1 | 344.5 | 346.5 | 310.7
1461 | 1240 | 470.6 | 188.24 | 220.0417 | 335.2 | 313.2 | 317.4 | 322.1 | 543.3 | 61.1 | 18.7 | 107.8 | 5.3 | 269.1 | 5.8 | 278.4 | 285.9 | 562 | 747.9 | 400.9 | 452.1 | 621.5 | 797.6 | 701.1 | 587.4 | 719.7 | 530.3 | 595.5 | 669.7 | 581.1 | 461.1 | 543.8 | 324.1 | 343 | 337.1 | 317.8 | 328.2 | 344.7 | 346.7 | 310.9
1462 | 1241 | 471.2 | 188.48 | 220.3223 | 335.7 | 313.3 | 317.4 | 321.8 | 546.2 | 61.1 | 18.8 | 107.9 | 5.8 | 256.9 | 5.7 | 278.6 | 286.2 | 556.7 | 739.2 | 401.1 | 452.2 | 622.7 | 788.2 | 699.3 | 587.7 | 717.6 | 525.1 | 596.2 | 672.5 | 574.9 | 461.5 | 543 | 324.2 | 343.2 | 337.2 | 318.1 | 328.4 | 344.7 | 346.8 | 311.1
1463 | 1242 | 471.8 | 188.72 | 220.6028 | 337.5 | 313.3 | 317.3 | 322.1 | 546.1 | 61.1 | 18.7 | 107.9 | 5.1 | 236.5 | 5.6 | 278.8 | 286.5 | 572.9 | 753.1 | 401.3 | 452.4 | 626.1 | 781.7 | 701 | 588 | 723.8 | 537 | 596.7 | 664.9 | 584.4 | 461.9 | 543.7 | 324.4 | 343.3 | 337.4 | 318.5 | 328.5 | 344.7 | 346.9 | 311.2
1464 | 1243 | 471.6 | 188.64 | 220.5093 | 340.3 | 313.9 | 317.3 | 322 | 544.9 | 61.1 | 18.7 | 107.7 | 5.3 | 246.8 | 5.4 | 278.9 | 286.7 | 580.6 | 761.5 | 401.4 | 452.5 | 620.4 | 797.4 | 701.4 | 588.3 | 731.4 | 543.3 | 597.1 | 659.4 | 590.3 | 462.3 | 545.1 | 324.5 | 343.5 | 337.7 | 319 | 328.7 | 344.6 | 346.9 | 311.3
1465 | 1244 | 473.3 | 189.32 | 221.3042 | 341.9 | 313.9 | 317.8 | 322.2 | 545.9 | 61.1 | 18.7 | 107.7 | 5.5 | 250.4 | 5.9 | 279.1 | 287 | 570.6 | 748 | 401.6 | 452.7 | 609.4 | 782.1 | 700.2 | 588.7 | 736.1 | 535.5 | 597.8 | 667.6 | 581.8 | 462.7 | 544.3 | 324.8 | 343.8 | 337.9 | 319 | 328.8 | 344.6 | 346.9 | 311.5
1466 | 1245 | 473.2 | 189.28 | 221.2574 | 342.4 | 313.1 | 318.3 | 323.4 | 547 | 61.3 | 18.7 | 107.7 | 4.6 | 247.7 | 6.5 | 279.3 | 287.3 | 564.5 | 741.1 | 401.8 | 452.9 | 612.5 | 777.7 | 699.2 | 588.9 | 737.7 | 525.4 | 598.4 | 672 | 576.8 | 463.1 | 543.6 | 325 | 344.2 | 338.4 | 319.2 | 329 | 345.1 | 347.1 | 311.8
1467 | 1246 | 473.3 | 189.32 | 221.3042 | 341.2 | 312.9 | 317.9 | 324.3 | 546.5 | 61.4 | 18.7 | 107.7 | 5.4 | 253.7 | 7 | 279.5 | 287.5 | 551.4 | 719.2 | 402 | 453.1 | 617.2 | 772.4 | 697.9 | 588.9 | 736.6 | 514.4 | 599 | 682.6 | 571.7 | 463.4 | 542.8 | 325.2 | 344.4 | 338.4 | 319.4 | 329.2 | 345.6 | 347.4 | 312
1468 | 1247 | 472.4 | 188.96 | 220.8834 | 340.6 | 312.5 | 317.7 | 325.3 | 548.8 | 61.6 | 18.7 | 107.8 | 5.7 | 256.1 | 6.7 | 279.6 | 287.8 | 543.8 | 722.9 | 402.2 | 453.2 | 633.1 | 775.6 | 697.6 | 588.8 | 733.6 | 508.7 | 599.4 | 683.7 | 577.5 | 463.8 | 543.5 | 325.4 | 344.5 | 338.3 | 319.5 | 329.5 | 346 | 348 | 312.1
1469 | 1248 | 474 | 189.6 | 221.6315 | 343.4 | 311.8 | 317 | 325.6 | 550.4 | 61.8 | 18.7 | 107.8 | 5.3 | 258.9 | 6.7 | 279.8 | 288.1 | 542.8 | 731.6 | 402.4 | 453.4 | 640.2 | 784.5 | 699.5 | 588.6 | 736.8 | 507.4 | 599.7 | 673.5 | 583.5 | 464.1 | 544.6 | 325.5 | 344.4 | 338 | 319.4 | 329.7 | 346.6 | 348.7 | 312.4
1470 | 1249 | 472.5 | 189 | 220.9301 | 344.7 | 311.6 | 316 | 326 | 553.8 | 61.9 | 18.7 | 107.7 | 5.4 | 246.9 | 6.6 | 280 | 288.3 | 543.9 | 746 | 402.6 | 453.6 | 634.3 | 790 | 700.1 | 588.4 | 733.9 | 509.7 | 600.3 | 661 | 588.7 | 464.5 | 545.7 | 325.6 | 344.4 | 338 | 319.5 | 330 | 347 | 349.2 | 312.6
1471 | 1250 | 471.8 | 188.72 | 220.6028 | 344.2 | 311.4 | 315.7 | 326 | 549 | 61.9 | 18.7 | 107.8 | 5.5 | 245.8 | 6.6 | 280.1 | 288.5 | 544.7 | 753.4 | 402.8 | 453.8 | 639.3 | 794.9 | 701.1 | 588.4 | 726.3 | 515.8 | 600.9 | 659.7 | 590 | 464.9 | 545.9 | 325.8 | 344.4 | 338 | 319.7 | 330.2 | 347.2 | 349.5 | 312.8
1472 | 1251 | 471.5 | 188.6 | 220.4625 | 344.8 | 311.5 | 315.9 | 325.9 | 548.8 | 61.8 | 18.7 | 107.9 | 5.7 | 243.2 | 6.5 | 280.3 | 288.8 | 551.5 | 758.3 | 403 | 454.1 | 631.3 | 792.7 | 700.6 | 588.5 | 724.6 | 530.8 | 601.4 | 647.8 | 599.1 | 465.3 | 547.5 | 326 | 344.6 | 338.3 | 320 | 330.5 | 347.3 | 349.7 | 313
1473 | 1252 | 469.7 | 187.88 | 219.6209 | 346.2 | 311.1 | 317.2 | 325.8 | 547 | 61.7 | 18.7 | 108 | 5.8 | 260.6 | 6.3 | 280.5 | 289 | 557 | 752.8 | 403.2 | 454.3 | 635.5 | 803.6 | 703.7 | 588.7 | 702.4 | 537.1 | 601.8 | 636.9 | 596.6 | 465.7 | 548.2 | 326.2 | 344.9 | 338.5 | 320.3 | 330.7 | 347.5 | 349.8 | 313.2
1474 | 1253 | 469.4 | 187.76 | 219.4806 | 345 | 311.3 | 319.3 | 325.9 | 543.6 | 61.6 | 18.7 | 108.1 | 5.2 | 250 | 6.5 | 280.7 | 289.2 | 562.4 | 755.6 | 403.4 | 454.5 | 643 | 814.9 | 708.1 | 588.7 | 690.4 | 542.4 | 602.3 | 631.7 | 599.1 | 466.1 | 549 | 326.5 | 345.1 | 338.8 | 320.4 | 330.9 | 347.9 | 350 | 313.5
1475 | 1254 | 472.6 | 189.04 | 220.9769 | 343.9 | 311.6 | 319 | 325.5 | 544 | 61.6 | 18.7 | 108.1 | 5.5 | 246.4 | 6.6 | 280.9 | 289.4 | 586.2 | 770 | 403.6 | 454.8 | 653.1 | 827.4 | 711 | 588.8 | 688.9 | 553.1 | 602.9 | 633 | 604.6 | 466.5 | 550.7 | 326.7 | 345.3 | 339.2 | 320.7 | 331.2 | 348.2 | 350.4 | 313.6
1476 | 1255 | 473.7 | 189.48 | 221.4912 | 342 | 311.5 | 319.1 | 326.1 | 540.7 | 61.5 | 18.7 | 108.2 | 5.8 | 253.4 | 6.8 | 281 | 289.6 | 593.5 | 765 | 403.9 | 455 | 664.3 | 823.5 | 712.3 | 588.9 | 688.1 | 561.4 | 603.4 | 627.5 | 605.2 | 466.9 | 551.7 | 326.9 | 345.4 | 339.1 | 320.7 | 331.4 | 348.2 | 351 | 313.8
1477 | 1256 | 470.7 | 188.28 | 220.0885 | 339.7 | 311.4 | 319.2 | 326 | 538 | 61.5 | 18.7 | 108.3 | 5.6 | 255.9 | 6.6 | 281.2 | 289.8 | 593.6 | 760.8 | 404.1 | 455.2 | 674.7 | 813.1 | 712.5 | 589.2 | 685.5 | 571.1 | 604.3 | 624.5 | 607.7 | 467.3 | 552.5 | 327.1 | 345.3 | 338.8 | 320.7 | 331.6 | 348 | 351.3 | 313.9
1478 | 1257 | 470.8 | 188.32 | 220.1352 | 337.9 | 311.2 | 319.3 | 325.8 | 538.7 | 61.4 | 18.7 | 108.3 | 6.2 | 261.7 | 7 | 281.4 | 290.1 | 595.5 | 772 | 404.3 | 455.4 | 673.7 | 803.8 | 714.4 | 589.4 | 683.6 | 576.3 | 604.9 | 627.1 | 615.6 | 467.6 | 555.1 | 327.3 | 345.1 | 338.6 | 320.7 | 331.8 | 348 | 351.3 | 314.1
1479 | 1258 | 471.7 | 188.68 | 220.556 | 336.4 | 310.9 | 319 | 325.6 | 539.2 | 61.5 | 18.7 | 108.2 | 5.6 | 247.1 | 7.4 | 281.6 | 290.3 | 596.7 | 768.2 | 404.5 | 455.6 | 669.1 | 797.6 | 714.2 | 589.7 | 685 | 573.1 | 605.6 | 621.7 | 616.2 | 468 | 555.9 | 327.4 | 345.1 | 338.5 | 320.8 | 332 | 347.7 | 351.4 | 314.2
1480 | 1259 | 471.5 | 188.6 | 220.4625 | 334.9 | 310.7 | 318.5 | 324.3 | 537.9 | 61.5 | 18.7 | 108.2 | 5.2 | 265.5 | 7.5 | 281.8 | 290.5 | 595 | 766 | 404.8 | 455.8 | 676.8 | 813.7 | 715.6 | 590 | 689 | 565.6 | 606.4 | 635.2 | 615.9 | 468.3 | 556 | 327.5 | 345 | 338.3 | 320.6 | 332.2 | 347.9 | 351.3 | 314.4
1481 | 1260 | 471.6 | 188.64 | 220.5093 | 334.3 | 310.4 | 317.5 | 323.2 | 553.9 | 61.5 | 18.7 | 108.2 | 5.6 | 254.3 | 8 | 281.9 | 290.7 | 593.2 | 756.6 | 405 | 455.9 | 680.4 | 824 | 717.7 | 590.2 | 696.3 | 559.8 | 607 | 648.9 | 624 | 468.7 | 557.7 | 327.7 | 344.9 | 338.2 | 320.6 | 332.4 | 348.5 | 351.8 | 314.7
1482 | 1261 | 471.6 | 188.64 | 220.5093 | 334 | 310.2 | 316.6 | 324.1 | 573.2 | 61.5 | 18.7 | 108.1 | 5.8 | 235.6 | 8.1 | 282.1 | 290.9 | 589.3 | 734 | 405.2 | 456 | 683 | 826.7 | 718 | 590.3 | 702.1 | 545.5 | 607.7 | 655.2 | 620.4 | 469.1 | 558.4 | 327.8 | 345 | 338.1 | 320.6 | 332.8 | 349.5 | 352.5 | 315
1483 | 1262 | 471.8 | 188.72 | 220.6028 | 334.3 | 310.5 | 317.2 | 325.3 | 576.2 | 61.5 | 18.7 | 108 | 5.9 | 245.2 | 8.6 | 282.2 | 291.2 | 590 | 718.1 | 405.4 | 456.1 | 691.3 | 824.6 | 718.2 | 590.3 | 704.1 | 533.9 | 608.9 | 664.3 | 615.1 | 469.5 | 558.5 | 328 | 345.3 | 338.1 | 320.7 | 333.2 | 350.6 | 353.4 | 315.2
1484 | 1263 | 472 | 188.8 | 220.6963 | 333.7 | 311.4 | 318.3 | 327.8 | 580.7 | 61.5 | 18.7 | 108 | 5.9 | 243.8 | 8.7 | 282.4 | 291.4 | 602.2 | 734.5 | 405.6 | 456.3 | 699.3 | 832.1 | 720.4 | 590.1 | 707.5 | 539 | 609.9 | 677.7 | 615.9 | 469.9 | 559.1 | 328.2 | 345.7 | 338.4 | 321 | 333.5 | 351.1 | 354.3 | 315.4
1485 | 1264 | 471.7 | 188.68 | 220.556 | 333.4 | 312.4 | 319.4 | 328.5 | 575.1 | 61.5 | 18.7 | 108.1 | 5.5 | 247.5 | 8.8 | 282.5 | 291.6 | 618.9 | 745.2 | 405.8 | 456.4 | 698.4 | 831 | 721.5 | 590 | 700.3 | 545.8 | 610.8 | 666 | 617.8 | 470.3 | 560.1 | 328.5 | 346.1 | 338.9 | 321.5 | 333.8 | 351.3 | 354.7 | 315.6
1486 | 1265 | 471.7 | 188.68 | 220.556 | 333.5 | 312.5 | 320.1 | 329.5 | 566.8 | 61.5 | 18.6 | 108.1 | 5.3 | 244.3 | 8.9 | 282.7 | 291.9 | 618.2 | 740.2 | 406.1 | 456.5 | 700.7 | 819.2 | 722.3 | 590 | 697.4 | 540.2 | 611.8 | 671.6 | 618.8 | 470.6 | 560.7 | 328.7 | 346.4 | 339.1 | 321.8 | 334.3 | 352.2 | 355 | 315.9
1487 | 1266 | 470.9 | 188.36 | 220.182 | 333.7 | 312.4 | 320.8 | 329.8 | 567.3 | 61.6 | 18.6 | 108.2 | 4.6 | 246.6 | 8.9 | 282.8 | 292.1 | 605.8 | 714.7 | 406.3 | 456.6 | 693.8 | 816.3 | 722.1 | 589.8 | 693 | 531.4 | 612.8 | 677.3 | 615.1 | 471 | 561.3 | 329 | 346.6 | 339.2 | 321.9 | 334.7 | 352.5 | 355.4 | 316.1
1488 | 1267 | 471.3 | 188.52 | 220.369 | 333.6 | 313.5 | 319.4 | 330.6 | 567.3 | 61.7 | 18.6 | 108.2 | 5 | 244.3 | 8.6 | 282.9 | 292.3 | 605.7 | 695.3 | 406.5 | 456.7 | 685.8 | 805.6 | 721.3 | 589.7 | 695.2 | 520.3 | 613.8 | 681.1 | 616.9 | 471.4 | 562.4 | 329.3 | 347.1 | 339.4 | 321.8 | 335 | 352.9 | 355.7 | 316.4
1489 | 1268 | 471.7 | 188.68 | 220.556 | 334.4 | 314 | 319 | 332.2 | 568.7 | 61.8 | 18.6 | 108.3 | 5.4 | 239.4 | 8 | 283 | 292.5 | 588.7 | 670.6 | 406.8 | 456.8 | 677.5 | 795.2 | 717.5 | 589.4 | 692.3 | 513.8 | 614.8 | 686.1 | 612 | 471.8 | 562.7 | 329.6 | 347.7 | 339.6 | 321.9 | 335.5 | 353.9 | 356.4 | 316.7
1490 | 1269 | 472.1 | 188.84 | 220.7431 | 334.8 | 314.4 | 319.4 | 335.7 | 580.6 | 61.9 | 18.6 | 108.3 | 5.9 | 239.4 | 7.5 | 283.2 | 292.8 | 586 | 661.9 | 407 | 456.8 | 682.4 | 797.6 | 717.3 | 589 | 687.4 | 507.7 | 615.8 | 704.2 | 606.9 | 472.2 | 563.4 | 329.9 | 348 | 339.9 | 322 | 336 | 354.8 | 357.6 | 316.9
1491 | 1270 | 472.2 | 188.88 | 220.7898 | 334.9 | 315.1 | 319.1 | 338.3 | 584.3 | 62 | 18.6 | 108.3 | 6 | 248.7 | 7.7 | 283.3 | 293 | 597.3 | 662 | 407.3 | 456.9 | 685.6 | 818.7 | 719.7 | 588.4 | 687.5 | 504 | 617 | 713.7 | 604 | 472.7 | 564.8 | 330.2 | 348.2 | 340 | 322.3 | 336.4 | 355.6 | 358.6 | 317.2
1492 | 1271 | 472.5 | 189 | 220.9301 | 336.4 | 316.2 | 319.9 | 339.3 | 581.7 | 62.1 | 18.6 | 108.5 | 5.4 | 248.4 | 7.6 | 283.5 | 293.2 | 603 | 654.6 | 407.5 | 457 | 685.8 | 819.9 | 720.3 | 587.9 | 687.7 | 494.5 | 617.8 | 708 | 596.1 | 473.1 | 564.3 | 330.6 | 348.5 | 340.3 | 322.5 | 336.9 | 356.4 | 359.1 | 317.5
1493 | 1272 | 472.4 | 188.96 | 220.8834 | 336.4 | 317.1 | 321 | 338.9 | 578.3 | 62.1 | 18.6 | 108.6 | 4.8 | 253.2 | 7.5 | 283.6 | 293.5 | 594.9 | 645.3 | 407.8 | 457.1 | 676.4 | 809 | 718.6 | 587.4 | 689.8 | 485.6 | 618.9 | 707.8 | 589.8 | 473.5 | 563.6 | 330.9 | 348.9 | 340.6 | 322.7 | 337.3 | 357 | 359.6 | 317.9
1494 | 1273 | 472.3 | 188.92 | 220.8366 | 336.9 | 317.8 | 321.5 | 339.6 | 573.9 | 62.1 | 18.6 | 108.7 | 4.7 | 242.2 | 7.2 | 283.8 | 293.8 | 581.9 | 642.2 | 408 | 457.2 | 663.3 | 804.4 | 716.2 | 586.8 | 687 | 485.9 | 619.9 | 707.7 | 585.3 | 474 | 563.9 | 331.2 | 349.2 | 341 | 322.9 | 337.8 | 357.4 | 359.8 | 318.1
1495 | 1274 | 472.5 | 189 | 220.9301 | 337.8 | 318.2 | 322.4 | 340.7 | 570.4 | 62 | 18.6 | 108.8 | 5.5 | 253 | 6.8 | 283.9 | 294.1 | 577.5 | 646.1 | 408.3 | 457.2 | 673.5 | 819.3 | 718.3 | 586.1 | 680.4 | 483 | 620.8 | 712.9 | 581.4 | 474.5 | 565.4 | 331.4 | 349.6 | 341.2 | 323 | 338.2 | 358.1 | 360.4 | 318.5
1496 | 1275 | 471.4 | 188.56 | 220.4158 | 338.1 | 318.1 | 321.9 | 340.4 | 571.3 | 62.1 | 18.6 | 108.8 | 4.9 | 274.6 | 6.5 | 284.1 | 294.3 | 582.8 | 647.8 | 408.5 | 457.2 | 679.2 | 826.5 | 719.4 | 585.6 | 679.9 | 481.8 | 621.8 | 715.2 | 587.7 | 475 | 565.4 | 331.7 | 350 | 341.3 | 323.1 | 338.6 | 358.6 | 360.9 | 318.9
1497 | 1276 | 471.2 | 188.48 | 220.3223 | 338.1 | 318.1 | 321.2 | 339.9 | 564.9 | 62.1 | 18.6 | 108.8 | 5.6 | 275.7 | 6.9 | 284.4 | 294.5 | 587.2 | 655.3 | 408.8 | 457.2 | 674.6 | 813.5 | 719.1 | 585.1 | 680.2 | 483.5 | 622.6 | 709.9 | 589 | 475.5 | 565.3 | 332 | 350.2 | 341.3 | 323.4 | 339 | 358.9 | 360.9 | 319
1498 | 1277 | 471.6 | 188.64 | 220.5093 | 338.1 | 318 | 321.8 | 339.1 | 558.5 | 62.3 | 18.6 | 108.9 | 5.3 | 266 | 7.2 | 284.6 | 294.8 | 578.2 | 649.9 | 409 | 457.3 | 666.4 | 788 | 715.7 | 584.7 | 676.4 | 479.5 | 623.2 | 693.7 | 581.8 | 475.9 | 564.4 | 332.2 | 350.3 | 341.2 | 323.7 | 339.3 | 358.5 | 360.6 | 319.2
1499 | 1278 | 472.3 | 188.92 | 220.8366 | 338.2 | 317.8 | 322.9 | 338.1 | 549.8 | 62.5 | 18.6 | 109 | 5.4 | 247.6 | 6.8 | 284.8 | 294.9 | 568.9 | 640.3 | 409.3 | 457.3 | 668.1 | 762.2 | 714.8 | 584.2 | 682.3 | 477.2 | 624 | 687.4 | 572.7 | 476.2 | 563.6 | 332.4 | 350.3 | 341.2 | 323.8 | 339.6 | 357.9 | 360.2 | 319.3
1500 | 1279 | 473.6 | 189.44 | 221.4444 | 338.8 | 318.7 | 324.2 | 337.8 | 542.7 | 62.7 | 18.6 | 109.1 | 5.5 | 242.8 | 6.5 | 284.9 | 295.1 | 564.2 | 632.2 | 409.6 | 457.4 | 670.6 | 733.9 | 712.1 | 583.7 | 682.2 | 476.2 | 624.8 | 679.6 | 568.3 | 476.7 | 563.3 | 332.6 | 350.2 | 341.3 | 324 | 339.8 | 357.2 | 359.8 | 319.4
1501 | 1280 | 473.3 | 189.32 | 221.3042 | 341.8 | 318.2 | 324.5 | 336.6 | 541.8 | 62.7 | 18.6 | 109.2 | 5.2 | 252.6 | 6.6 | 285 | 295.2 | 552.4 | 626.1 | 409.9 | 457.4 | 657.8 | 708.8 | 707.7 | 583.3 | 684.3 | 472.4 | 625.7 | 674.9 | 562.2 | 477.1 | 562.8 | 332.8 | 350.1 | 341.5 | 324.3 | 339.9 | 356.7 | 359.5 | 319.5
1502 | 1281 | 473.3 | 189.32 | 221.3042 | 345.1 | 317.7 | 323.8 | 334.9 | 542.9 | 62.9 | 18.6 | 109.3 | 5.6 | 252.5 | 6.7 | 285.1 | 295.4 | 547.9 | 651 | 410.2 | 457.5 | 650.8 | 717.6 | 707 | 583 | 690.1 | 483.2 | 626.4 | 673.5 | 564.1 | 477.6 | 563.4 | 333 | 350.2 | 342 | 324.8 | 340 | 356.1 | 359.4 | 319.5
1503 | 1282 | 473.1 | 189.24 | 221.2107 | 347.7 | 317.3 | 324 | 333 | 547.3 | 63.2 | 18.6 | 109.4 | 5.5 | 246.4 | 6.9 | 285.3 | 295.6 | 554.3 | 666.8 | 410.4 | 457.5 | 640.4 | 715.5 | 705.5 | 583 | 699 | 496 | 626.8 | 671.9 | 570.6 | 478 | 564.2 | 333.3 | 350.6 | 342.5 | 325.2 | 340.1 | 355.8 | 359.1 | 319.7
1504 | 1283 | 473.1 | 189.24 | 221.2107 | 349.5 | 316.6 | 324.9 | 330.8 | 550.6 | 63.4 | 18.6 | 109.5 | 5.3 | 252.3 | 6.6 | 285.4 | 295.8 | 554.2 | 659.7 | 410.7 | 457.6 | 634.5 | 693.2 | 702.2 | 583.3 | 709.1 | 492 | 627.1 | 665.3 | 570.9 | 478.3 | 563.6 | 333.6 | 351.3 | 343.2 | 325.4 | 340.1 | 355.5 | 359.1 | 319.8
1505 | 1284 | 473 | 189.2 | 221.1639 | 350 | 316.5 | 325.4 | 329.5 | 554.3 | 63.3 | 18.6 | 109.7 | 5.3 | 276.4 | 6 | 285.5 | 296 | 569.5 | 660 | 410.9 | 457.7 | 620.3 | 677.9 | 699.7 | 583.5 | 704.7 | 493.6 | 627.5 | 664.3 | 569.8 | 478.8 | 564 | 334 | 352 | 344.1 | 325.9 | 340.2 | 355.2 | 359.1 | 319.9
1506 | 1285 | 473.3 | 189.32 | 221.3042 | 353.1 | 316.6 | 325.6 | 329.3 | 548.4 | 63.3 | 18.6 | 109.9 | 4.9 | 274.5 | 5.9 | 285.7 | 296.2 | 574.6 | 680.7 | 411.2 | 457.8 | 628.5 | 702.7 | 701 | 583.7 | 697.5 | 511.4 | 627.8 | 669.4 | 577.8 | 479.2 | 564.7 | 334.4 | 352.7 | 344.8 | 326.3 | 340.2 | 355 | 358.9 | 320.1
1507 | 1286 | 473.5 | 189.4 | 221.3977 | 357.2 | 316.9 | 326.5 | 329.7 | 542.7 | 63.2 | 18.6 | 110 | 5 | 259 | 5.5 | 285.8 | 296.4 | 577.1 | 697.8 | 411.5 | 457.9 | 630.1 | 725.4 | 700.3 | 584 | 690.6 | 512 | 628.1 | 665.2 | 579.6 | 479.5 | 565 | 334.7 | 353.4 | 345.5 | 326.6 | 340.3 | 355.1 | 358.9 | 320.3
1508 | 1287 | 472.5 | 189 | 220.9301 | 356.9 | 316.4 | 327.1 | 330.3 | 543.3 | 63.1 | 18.6 | 110.1 | 5.6 | 246.1 | 6.8 | 285.9 | 296.6 | 579.8 | 712.3 | 411.8 | 458 | 632.3 | 753.3 | 700.9 | 584.4 | 696.6 | 512.7 | 628.6 | 673.1 | 579.4 | 479.7 | 564.7 | 335.1 | 354.1 | 346.2 | 326.6 | 340.4 | 355.5 | 359.1 | 320.5
1509 | 1288 | 472.9 | 189.16 | 221.1171 | 355.4 | 315.9 | 327.3 | 331.1 | 543.7 | 63 | 18.6 | 110.2 | 5.6 | 258.8 | 8.7 | 286.1 | 296.8 | 585.9 | 733 | 412.1 | 458.1 | 628.7 | 773.1 | 703.2 | 584.8 | 700.7 | 520.2 | 629.1 | 676.9 | 579.7 | 479.9 | 565.4 | 335.5 | 354.4 | 346.1 | 326.8 | 340.6 | 355.9 | 359.3 | 320.8
1510 | 1289 | 472.1 | 188.84 | 220.7431 | 354.1 | 316.8 | 328 | 332.4 | 541.2 | 62.9 | 18.6 | 110.3 | 5.9 | 258 | 9.6 | 286.2 | 297.1 | 592.2 | 734.5 | 412.4 | 458.2 | 631.1 | 785.4 | 704.1 | 585.1 | 705.7 | 517.8 | 629.8 | 682.3 | 577.4 | 479.8 | 565.2 | 335.7 | 354.4 | 346 | 326.8 | 340.8 | 356.1 | 359.6 | 321
1511 | 1290 | 474.1 | 189.64 | 221.6782 | 353.5 | 316.8 | 328.2 | 333.8 | 542.3 | 62.8 | 18.6 | 110.5 | 6.1 | 261.1 | 9.9 | 286.3 | 297.4 | 595.6 | 730.5 | 412.6 | 458.3 | 639.5 | 785.7 | 704.7 | 585.4 | 706.8 | 516.9 | 630.5 | 682.7 | 582.2 | 479.7 | 565.5 | 336 | 354.5 | 345.9 | 326.8 | 341 | 357.1 | 360.1 | 321.4
1512 | 1291 | 472.9 | 189.16 | 221.1171 | 353.9 | 316.8 | 327.3 | 334.3 | 546.2 | 62.8 | 18.6 | 110.5 | 6 | 263.5 | 9.5 | 286.5 | 297.7 | 596.4 | 714.9 | 412.9 | 458.4 | 649 | 787.1 | 702.7 | 585.6 | 707.2 | 510.2 | 631.2 | 686.5 | 579.2 | 479.6 | 565.5 | 336.2 | 354.6 | 345.3 | 326.6 | 341.4 | 358 | 361 | 321.7
1513 | 1292 | 473.8 | 189.52 | 221.538 | 353.4 | 317.1 | 327 | 334.2 | 548.8 | 62.6 | 18.6 | 110.5 | 5.6 | 261.8 | 9.3 | 286.6 | 297.9 | 598.4 | 700.1 | 413.2 | 458.5 | 654.7 | 786.9 | 703.5 | 585.5 | 700.9 | 500.4 | 632.1 | 689.1 | 572.7 | 479.6 | 564.9 | 336.4 | 354.8 | 345 | 326.5 | 341.8 | 358.8 | 361.8 | 322
1514 | 1293 | 472.6 | 189.04 | 220.9769 | 351.9 | 317.8 | 327 | 335 | 552.9 | 62.6 | 18.6 | 110.5 | 6.4 | 266.4 | 8.8 | 286.7 | 298.2 | 600 | 687.3 | 413.6 | 458.6 | 654.4 | 786.6 | 703.6 | 585.3 | 701.4 | 490.6 | 632.8 | 698.7 | 568.6 | 479.7 | 564.3 | 336.6 | 355.2 | 345.1 | 326.5 | 342.1 | 359.8 | 362.6 | 322.3
1515 | 1294 | 470.7 | 188.28 | 220.0885 | 350.9 | 318.6 | 327.7 | 336.8 | 560.7 | 62.6 | 18.6 | 110.5 | 5.7 | 263.1 | 8.5 | 286.9 | 298.4 | 606.5 | 675 | 413.9 | 458.8 | 664 | 798.9 | 706 | 585.1 | 702.3 | 486.6 | 633.5 | 713 | 572 | 479.8 | 563.9 | 336.9 | 355.7 | 345.3 | 326.8 | 342.6 | 360.5 | 363.4 | 322.5
1516 | 1295 | 471.8 | 188.72 | 220.6028 | 349.5 | 319.8 | 328.6 | 337.9 | 567.2 | 62.5 | 18.6 | 110.5 | 6 | 256.8 | 8.8 | 287 | 298.7 | 605.8 | 667.8 | 414.2 | 459 | 668 | 810.9 | 707.1 | 584.9 | 705.8 | 481.1 | 634.1 | 719.2 | 577.2 | 479.9 | 564.3 | 337.2 | 356 | 345.5 | 326.9 | 343.2 | 361.7 | 364.5 | 322.9
1517 | 1296 | 471.8 | 188.72 | 220.6028 | 348.5 | 320.9 | 328.9 | 339.3 | 567.9 | 62.5 | 18.6 | 110.4 | 6 | 247.2 | 8.9 | 287.1 | 299 | 609.9 | 674.6 | 414.4 | 459.1 | 665.5 | 826 | 710 | 584.5 | 702.6 | 479.7 | 634.7 | 721.3 | 576.5 | 480.1 | 564.5 | 337.5 | 356.3 | 345.7 | 327.1 | 343.8 | 362.7 | 365.6 | 323.2
1518 | 1297 | 471.1 | 188.44 | 220.2755 | 347.9 | 321.4 | 328.6 | 341.8 | 578.1 | 62.4 | 18.6 | 110.3 | 5.1 | 253.8 | 8.9 | 287.3 | 299.3 | 628 | 685.8 | 414.7 | 459.4 | 682.2 | 832.7 | 710.7 | 584.2 | 698.8 | 490.2 | 635.4 | 722.6 | 582.4 | 480.3 | 564.9 | 337.8 | 356.5 | 346 | 327.4 | 344.3 | 363.8 | 367.1 | 323.5
1519 | 1298 | 471.3 | 188.52 | 220.369 | 348.4 | 322.1 | 327.8 | 342.8 | 581.2 | 62.4 | 18.6 | 110.2 | 4.7 | 238.7 | 8.8 | 287.4 | 299.5 | 639.7 | 697.8 | 415 | 459.6 | 691.9 | 842 | 713.6 | 584.1 | 688.1 | 494.4 | 636.1 | 710.4 | 583.8 | 480.5 | 565.6 | 338.1 | 356.7 | 346.3 | 327.7 | 344.8 | 364.2 | 367.9 | 323.7
1520 | 1299 | 471.7 | 188.68 | 220.556 | 349.7 | 323.1 | 328.2 | 343.2 | 577.1 | 62.4 | 18.6 | 110.2 | 5.1 | 249.2 | 9.2 | 287.6 | 299.8 | 634.3 | 727.6 | 415.4 | 459.7 | 682.3 | 839.5 | 715.2 | 584 | 689.5 | 502 | 636.8 | 699.8 | 586.5 | 480.7 | 566 | 338.4 | 356.9 | 346.8 | 328.2 | 345.3 | 363.9 | 368.5 | 323.8
1521 | 1300 | 471.5 | 188.6 | 220.4625 | 350.3 | 323.7 | 328.8 | 343.9 | 573.1 | 62.4 | 18.6 | 110.2 | 5.4 | 252.9 | 8.8 | 287.7 | 300 | 636.4 | 735.7 | 415.7 | 459.8 | 665.1 | 826.3 | 714.8 | 584.2 | 688.7 | 516.8 | 637.2 | 687.4 | 593.6 | 481 | 567.2 | 338.8 | 357.2 | 347.4 | 328.8 | 345.6 | 363.6 | 368.6 | 324
1522 | 1301 | 472.2 | 188.88 | 220.7898 | 350.6 | 324.4 | 330.9 | 343.1 | 566.5 | 62.5 | 18.6 | 110.2 | 5 | 249.4 | 8.2 | 287.9 | 300.2 | 627.5 | 741.6 | 416 | 460 | 660.5 | 825.8 | 713.2 | 584.6 | 692.5 | 517.5 | 637.8 | 685.4 | 590.9 | 481.2 | 567.4 | 339.1 | 357.6 | 347.9 | 329.2 | 345.8 | 363.4 | 368.4 | 324.2
1523 | 1302 | 472.7 | 189.08 | 221.0236 | 350.4 | 324.2 | 331.7 | 342.2 | 559.2 | 62.5 | 18.5 | 110.1 | 5 | 261.1 | 7.5 | 288.1 | 300.5 | 626.1 | 740.3 | 416.2 | 460.2 | 659.1 | 822.1 | 712.9 | 584.9 | 696.6 | 516.9 | 638.3 | 689.1 | 591 | 481.5 | 568 | 339.5 | 357.9 | 348.2 | 329.4 | 346.1 | 363.3 | 368.1 | 324.5
1524 | 1303 | 472.9 | 189.16 | 221.1171 | 351.8 | 323.6 | 332.5 | 340.5 | 558.1 | 62.5 | 18.5 | 110.1 | 5.6 | 264.1 | 7.9 | 288.2 | 300.7 | 622.9 | 749.6 | 416.5 | 460.3 | 659.8 | 821.4 | 713.4 | 585.1 | 697.8 | 526.8 | 638.8 | 691 | 596.8 | 481.9 | 569.1 | 339.8 | 358.1 | 348.6 | 329.5 | 346.2 | 363.1 | 367.7 | 324.6
1525 | 1304 | 472.4 | 188.96 | 220.8834 | 354.3 | 323.3 | 332.4 | 339.5 | 553.2 | 62.5 | 18.5 | 110.2 | 5.7 | 284.1 | 7.7 | 288.3 | 300.9 | 618.9 | 751.7 | 416.8 | 460.5 | 659.9 | 820.1 | 715.2 | 585.5 | 700.1 | 533.3 | 639.3 | 685.2 | 596.6 | 482.3 | 569.6 | 340.1 | 358.2 | 348.8 | 329.7 | 346.4 | 362.7 | 367.3 | 324.8
1526 | 1305 | 472.3 | 188.92 | 220.8366 | 354.8 | 323 | 331.2 | 338.6 | 554.2 | 62.4 | 18.5 | 110.4 | 6.2 | 270.6 | 7.3 | 288.5 | 301.1 | 619.3 | 767.1 | 417.1 | 460.6 | 664.6 | 824.5 | 716.3 | 585.8 | 704.3 | 552.1 | 639.9 | 687.5 | 605.2 | 482.7 | 571.4 | 340.4 | 358.2 | 349 | 330 | 346.5 | 362.6 | 367 | 325
1527 | 1306 | 472.4 | 188.96 | 220.8834 | 355.7 | 323.1 | 330.8 | 336.7 | 555.5 | 62.4 | 18.5 | 110.6 | 5.1 | 273.4 | 6.8 | 288.6 | 301.3 | 630.4 | 777.2 | 417.4 | 460.8 | 680.4 | 824.4 | 717.3 | 586.3 | 706.1 | 573.1 | 640.7 | 681.6 | 613.1 | 483.1 | 573.4 | 340.6 | 358.2 | 349.3 | 330.3 | 346.6 | 362.1 | 366.9 | 325.1
1528 | 1307 | 472.7 | 189.08 | 221.0236 | 356.6 | 323.6 | 331.2 | 335.6 | 555 | 62.3 | 18.5 | 110.8 | 5.6 | 265.2 | 6 | 288.8 | 301.6 | 628.9 | 767.3 | 417.7 | 460.9 | 684.1 | 798.2 | 714.5 | 586.8 | 707.3 | 570 | 641.8 | 667.9 | 613.5 | 483.3 | 574 | 340.9 | 358.4 | 349.8 | 330.6 | 346.7 | 361.4 | 366.7 | 325.2
1529 | 1308 | 471.2 | 188.48 | 220.3223 | 356.5 | 323.6 | 331.1 | 335.5 | 551.7 | 62.3 | 18.5 | 110.9 | 5.6 | 257.6 | 5.3 | 289 | 301.9 | 626.5 | 759.3 | 418 | 460.9 | 675.3 | 790.6 | 713.6 | 587.2 | 711.1 | 557.7 | 642.8 | 669.2 | 603.6 | 483.6 | 573.3 | 341.3 | 358.7 | 350.2 | 330.9 | 346.8 | 360.9 | 366.7 | 325.4
1530 | 1309 | 472.2 | 188.88 | 220.7898 | 355.4 | 323.9 | 331.9 | 336 | 547.7 | 62.3 | 18.5 | 111 | 6.1 | 262.9 | 4.9 | 289.1 | 302.1 | 626.8 | 767.4 | 418.3 | 461 | 681.3 | 801.8 | 715.4 | 587.7 | 708.6 | 563 | 643.5 | 678 | 600.7 | 484 | 573.3 | 341.6 | 358.9 | 350.3 | 330.9 | 346.8 | 360.4 | 366.4 | 325.5
1531 | 1310 | 471.9 | 188.76 | 220.6496 | 354.4 | 323.7 | 332 | 336.2 | 544.6 | 62.3 | 18.5 | 110.9 | 5.9 | 270 | 5.3 | 289.3 | 302.4 | 625.3 | 752.3 | 418.6 | 461.2 | 686.3 | 823.2 | 717.9 | 588.1 | 702 | 561.9 | 644 | 674.4 | 601.9 | 484.3 | 574.2 | 341.8 | 358.8 | 350.1 | 330.9 | 346.9 | 360.1 | 366 | 325.7
1532 | 1311 | 471.8 | 188.72 | 220.6028 | 353.1 | 323 | 331.7 | 335.4 | 562.1 | 62.3 | 18.5 | 110.8 | 5.6 | 248.6 | 6 | 289.4 | 302.7 | 621.9 | 733.5 | 418.9 | 461.4 | 699.4 | 842.5 | 720.3 | 588.4 | 702.4 | 549.8 | 644.9 | 693.6 | 603.6 | 484.7 | 574.9 | 342 | 358.8 | 349.9 | 330.7 | 347.1 | 360.5 | 365.9 | 326
1533 | 1312 | 472.3 | 188.92 | 220.8366 | 352.9 | 322.5 | 330.3 | 337.1 | 575.8 | 62.4 | 18.5 | 110.7 | 5.7 | 256.1 | 6.4 | 289.6 | 302.9 | 631.3 | 710.5 | 419.2 | 461.5 | 699.1 | 851.7 | 721.8 | 588.6 | 697.1 | 544.2 | 645.9 | 700.6 | 599.2 | 485.2 | 575.4 | 342.2 | 358.8 | 349.7 | 330.7 | 347.4 | 361.7 | 366.3 | 326.3
1534 | 1313 | 472 | 188.8 | 220.6963 | 353.4 | 323.2 | 329.5 | 338.6 | 582.5 | 62.4 | 18.5 | 110.6 | 5.4 | 267.3 | 6.7 | 289.8 | 303.1 | 653 | 692.1 | 419.5 | 461.5 | 701.3 | 842.3 | 719.6 | 588.8 | 691.5 | 536.4 | 646.7 | 708 | 597.8 | 485.6 | 575.7 | 342.5 | 359 | 349.3 | 330.7 | 347.8 | 363.5 | 368.1 | 326.6
1535 | 1314 | 472.6 | 189.04 | 220.9769 | 355.1 | 324 | 330 | 340.7 | 584.9 | 62.4 | 18.5 | 110.7 | 5.7 | 275.4 | 7.5 | 289.9 | 303.4 | 664.2 | 675.3 | 419.8 | 461.6 | 698.3 | 839.8 | 718 | 589.1 | 686.1 | 527.1 | 647.4 | 717.9 | 595.5 | 486 | 575.3 | 342.7 | 359.4 | 349.3 | 330.7 | 348.3 | 364.7 | 369.3 | 326.9
1536 | 1315 | 471.7 | 188.68 | 220.556 | 355.7 | 324.6 | 330.5 | 343.3 | 588.4 | 62.5 | 18.5 | 110.7 | 6 | 275.3 | 7.6 | 290.1 | 303.6 | 679.6 | 666 | 420.1 | 461.7 | 699.6 | 847.7 | 720.5 | 589.1 | 686.7 | 520.9 | 648.3 | 722.3 | 592.8 | 486.4 | 575.8 | 343.1 | 359.8 | 349.8 | 330.8 | 348.8 | 365.8 | 370.6 | 327.2
1537 | 1316 | 470.6 | 188.24 | 220.0417 | 355.9 | 325.4 | 330.9 | 345.7 | 593.8 | 62.5 | 18.5 | 110.6 | 6.5 | 265.1 | 8.1 | 290.2 | 303.9 | 694.6 | 664 | 420.4 | 461.9 | 705.7 | 857.8 | 723.1 | 589.2 | 478.9 | 518.6 | 648.9 | 722.2 | 593.9 | 487 | 576.4 | 343.4 | 360.2 | 350.2 | 331.3 | 349.3 | 367.2 | 372 | 327.5
1538 | 1317 | 472.2 | 188.88 | 220.7898 | 356.9 | 326.4 | 332.8 | 347.6 | 590.8 | 62.6 | 18.5 | 110.6 | 6.5 | 275.5 | 9.5 | 290.4 | 304.2 | 704.3 | 664.6 | 420.8 | 462.1 | 712.8 | 863.5 | 725.1 | 589.2 | 674.4 | 518 | 649.6 | 717.8 | 593.5 | 487.5 | 576 | 343.8 | 360.5 | 350.6 | 331.8 | 349.8 | 367.9 | 372.9 | 327.8
1539 | 1318 | 473.1 | 189.24 | 221.2107 | 357.5 | 327 | 334.1 | 348.3 | 588.2 | 62.7 | 18.5 | 110.7 | 6.4 | 263.3 | 10.1 | 290.5 | 304.5 | 712.5 | 667.2 | 421.1 | 462.3 | 729.2 | 857.3 | 724.7 | 589.3 | 652.8 | 518.2 | 650.1 | 719.7 | 591.6 | 487.9 | 575.7 | 344.1 | 360.7 | 350.8 | 332 | 350.3 | 368.9 | 373.7 | 328.2
1540 | 1319 | 473 | 189.2 | 221.1639 | 357.8 | 327.5 | 334.7 | 349.8 | 591.9 | 62.6 | 18.5 | 110.7 | 6.6 | 269.8 | 9.7 | 290.7 | 304.8 | 717.3 | 662.2 | 421.4 | 462.5 | 756.8 | 861.2 | 724.5 | 589.4 | 478.6 | 514.1 | 650.7 | 719 | 593.8 | 488.4 | 576.1 | 344.5 | 361 | 351.2 | 332.1 | 350.9 | 370.5 | 374.8 | 328.6
1541 | 1320 | 473.2 | 189.28 | 221.2574 | 357.8 | 328.1 | 335.3 | 351.5 | 594.7 | 62.6 | 18.5 | 110.7 | 5.9 | 268.5 | 10.5 | 290.9 | 305 | 712.3 | 652.4 | 421.6 | 462.7 | 754.3 | 858 | 725 | 589.5 | 676.7 | 509.9 | 651.4 | 712.2 | 592.4 | 489 | 575.7 | 344.8 | 361.4 | 351.5 | 332.2 | 351.6 | 371.8 | 375.9 | 328.9
1542 | 1321 | 472.7 | 189.08 | 221.0236 | 358.3 | 328.8 | 335.8 | 353.5 | 589 | 62.5 | 18.5 | 110.7 | 5.5 | 256.1 | 9.4 | 291 | 305.3 | 695.4 | 644.4 | 421.8 | 462.9 | 753 | 855.5 | 723.7 | 589.6 | 673.6 | 503 | 652.1 | 713.3 | 591.6 | 489.5 | 575.8 | 345.2 | 361.7 | 351.8 | 332.4 | 352.2 | 372.6 | 376.6 | 329.2
1543 | 1322 | 472.7 | 189.08 | 221.0236 | 358.3 | 329.6 | 336.3 | 354.4 | 587.5 | 62.4 | 18.5 | 110.8 | 6 | 269.6 | 8.3 | 291.2 | 305.6 | 686.8 | 653 | 422 | 463.1 | 736.7 | 863.8 | 725.7 | 589.6 | 669.5 | 507.3 | 652.9 | 712.7 | 593.7 | 490 | 576.3 | 345.5 | 362.2 | 352.1 | 332.7 | 352.9 | 373.2 | 377.2 | 329.5
1544 | 1323 | 472.8 | 189.12 | 221.0704 | 359.2 | 329.4 | 337.2 | 354.9 | 582.8 | 62.4 | 18.5 | 110.9 | 6.6 | 269.8 | 9.6 | 291.4 | 305.8 | 698.7 | 673.3 | 422.1 | 463.3 | 725.9 | 859.3 | 726.7 | 589.8 | 666.8 | 515.1 | 653.1 | 710.5 | 605.8 | 490.5 | 577.5 | 345.9 | 362.7 | 352.5 | 332.9 | 353.5 | 373.6 | 377.7 | 329.8
1545 | 1324 | 472.9 | 189.16 | 221.1171 | 359.4 | 329.6 | 337.8 | 355 | 582 | 62.4 | 18.5 | 111 | 5.9 | 266.8 | 10.6 | 291.5 | 306.1 | 708.9 | 678.3 | 422.3 | 463.5 | 720.7 | 860.7 | 727.3 | 590 | 661.1 | 510.3 | 653.8 | 706.9 | 599.7 | 490.9 | 577.6 | 346.2 | 362.9 | 352.8 | 333.1 | 354.1 | 374.5 | 378.3 | 330.3
1546 | 1325 | 472.5 | 189 | 220.9301 | 359.6 | 330.2 | 338.1 | 355.7 | 581.8 | 62.5 | 18.5 | 111.3 | 7.5 | 271 | 11.1 | 291.7 | 306.4 | 708.6 | 670.3 | 422.5 | 463.7 | 720.3 | 849.2 | 726.5 | 590.1 | 658 | 501.8 | 654.7 | 702.7 | 591.5 | 491.3 | 576 | 346.5 | 363 | 352.6 | 333.2 | 354.8 | 376.7 | 379.1 | 330.8
1547 | 1326 | 472.3 | 188.92 | 220.8366 | 360.1 | 330.9 | 338.3 | 357 | 582.6 | 62.6 | 18.5 | 111.5 | 7.2 | 276.4 | 10.2 | 291.8 | 306.7 | 705.7 | 659.7 | 422.6 | 463.9 | 724.2 | 852.4 | 727.1 | 590.2 | 662.2 | 497.3 | 655.6 | 702.4 | 590.2 | 491.9 | 575.4 | 346.8 | 363.2 | 352.9 | 333.8 | 355.6 | 378.1 | 380.2 | 331.2
1548 | 1327 | 472.9 | 189.16 | 221.1171 | 360.2 | 331.3 | 338 | 357.5 | 585 | 62.6 | 18.5 | 111.6 | 5.5 | 265.8 | 9.3 | 292 | 306.9 | 703.1 | 662.7 | 422.8 | 464.1 | 728.4 | 853.5 | 727.2 | 590 | 660.1 | 498.7 | 656.2 | 702 | 591.9 | 492.5 | 575.2 | 347.1 | 363.3 | 353.1 | 334.1 | 356.2 | 378.6 | 381 | 331.5
1549 | 1328 | 472.9 | 189.16 | 221.1171 | 360.5 | 331.3 | 338.2 | 358.5 | 586.6 | 62.7 | 18.5 | 111.8 | 5.3 | 280 | 9.2 | 292.2 | 307.3 | 704.1 | 657.8 | 423 | 464.3 | 734.1 | 851.4 | 727.4 | 590 | 664.1 | 497 | 657.2 | 703.8 | 591.6 | 493.1 | 575 | 347.4 | 363.5 | 353.3 | 334.2 | 357 | 379 | 381.8 | 331.8
1550 | 1329 | 472.9 | 189.16 | 221.1171 | 360.9 | 330.2 | 338 | 359.5 | 590.4 | 62.8 | 18.5 | 111.9 | 6.1 | 268.2 | 9 | 292.4 | 307.6 | 693.2 | 637.4 | 423 | 464.6 | 725.7 | 843 | 726.4 | 589.8 | 659.4 | 488.9 | 657.8 | 710.2 | 588.9 | 493.9 | 575.2 | 347.7 | 363.8 | 353.4 | 334.2 | 357.7 | 379.4 | 382.8 | 332.1
1551 | 1330 | 472.6 | 189.04 | 220.9769 | 361.3 | 330.4 | 338 | 360.9 | 590.1 | 62.8 | 18.5 | 112.2 | 5.7 | 283.9 | 9.1 | 292.5 | 307.9 | 685.7 | 623 | 423.2 | 464.8 | 718.7 | 825.2 | 724 | 589.5 | 649.4 | 482.5 | 658.3 | 724.9 | 579.1 | 494.4 | 575.4 | 348 | 364.2 | 353.7 | 334.2 | 358.4 | 380.1 | 383.7 | 332.4
1552 | 1331 | 472.6 | 189.04 | 220.9769 | 362.4 | 332.1 | 338.2 | 362.5 | 595.5 | 62.8 | 18.5 | 112.3 | 5.1 | 278.1 | 9.9 | 292.7 | 308.2 | 679.7 | 602.4 | 423.3 | 465 | 712.5 | 801.8 | 720.5 | 589.1 | 643.1 | 474.5 | 658.3 | 728.9 | 571.5 | 495 | 575.5 | 348.4 | 364.8 | 354 | 334.2 | 359.3 | 381.3 | 385.1 | 332.8
1553 | 1332 | 473 | 189.2 | 221.1639 | 363.9 | 333.6 | 339.4 | 364.2 | 600.2 | 62.7 | 18.5 | 112.2 | 5.7 | 272.1 | 10.6 | 292.9 | 308.5 | 677.2 | 599 | 423.5 | 465.2 | 719.2 | 792.6 | 719.1 | 588.5 | 637.8 | 466.4 | 659.1 | 732 | 565.4 | 495.7 | 575.6 | 348.7 | 365.1 | 354.5 | 334.3 | 360.2 | 382.3 | 386.6 | 333.3
1554 | 1333 | 472.6 | 189.04 | 220.9769 | 364.6 | 334.7 | 341 | 365.5 | 592 | 62.6 | 18.5 | 112.3 | 5.9 | 273.1 | 10.5 | 293 | 308.8 | 669.1 | 597 | 423.8 | 465.3 | 711.8 | 783.8 | 717.8 | 588 | 641.9 | 461.3 | 659.8 | 731.6 | 561.9 | 496.3 | 575.9 | 349.1 | 365.5 | 354.9 | 334.5 | 360.8 | 382.9 | 387.7 | 333.7
1555 | 1334 | 472.7 | 189.08 | 221.0236 | 365.2 | 335.3 | 342.2 | 365.8 | 586 | 62.6 | 18.5 | 112.3 | 5.2 | 264.1 | 10.3 | 293.2 | 309.1 | 667.2 | 583.9 | 423.9 | 465.4 | 713.5 | 765.9 | 715.6 | 587.4 | 646.6 | 458.3 | 660.8 | 729 | 560.5 | 496.9 | 575.8 | 349.5 | 366.1 | 355.3 | 334.8 | 361.6 | 383.9 | 388.7 | 334
1556 | 1335 | 472.7 | 189.08 | 221.0236 | 366.1 | 336.5 | 343.2 | 366.5 | 585.5 | 62.6 | 18.5 | 112.4 | 5.9 | 262.6 | 9.8 | 293.4 | 309.4 | 670.4 | 584.3 | 424.1 | 465.6 | 717.7 | 771.1 | 717 | 586.9 | 652.8 | 459.5 | 661.9 | 728.6 | 562.8 | 497.6 | 576.3 | 349.9 | 366.6 | 355.6 | 335.2 | 362.3 | 384.8 | 389.9 | 334.4
1557 | 1336 | 472.3 | 188.92 | 220.8366 | 366.4 | 337 | 343.5 | 366.8 | 583.7 | 62.7 | 18.4 | 112.5 | 6.1 | 261.2 | 8.9 | 293.6 | 309.7 | 665.6 | 595.7 | 424.2 | 465.8 | 733.3 | 797.4 | 719 | 586.5 | 657.7 | 466.7 | 662.4 | 726.2 | 579.4 | 498 | 578.3 | 350.3 | 367.1 | 355.9 | 335.5 | 363 | 385.2 | 390.5 | 334.8
1558 | 1337 | 472.4 | 188.96 | 220.8834 | 366.9 | 337.5 | 344.4 | 366.9 | 583.8 | 62.8 | 18.4 | 112.5 | 6.2 | 271.8 | 8.7 | 293.7 | 309.9 | 673.6 | 620.3 | 424.5 | 466 | 750.1 | 818.5 | 721.3 | 586.4 | 661.7 | 478.3 | 662.3 | 719.6 | 587 | 498.6 | 579.5 | 350.8 | 367.3 | 356.1 | 335.8 | 363.5 | 385.1 | 390.6 | 335.1
1559 | 1338 | 472.5 | 189 | 220.9301 | 371.9 | 338.1 | 345.4 | 365.8 | 582.8 | 62.9 | 18.4 | 112.6 | 5.7 | 272.3 | 9.1 | 293.9 | 310.2 | 686.6 | 636.4 | 424.7 | 466.2 | 752.8 | 836.1 | 723.2 | 586.4 | 655.9 | 486.3 | 662.4 | 715.6 | 597.7 | 499.1 | 580.5 | 351.1 | 367.4 | 356.6 | 336 | 364 | 385 | 390.6 | 335.4
1560 | 1339 | 473 | 189.2 | 221.1639 | 380.5 | 338.2 | 345.1 | 365.2 | 588.2 | 63.1 | 18.4 | 112.7 | 6.3 | 277.6 | 9.5 | 294.1 | 310.5 | 696.7 | 641.9 | 424.9 | 466.5 | 756.7 | 855.9 | 726.3 | 586.4 | 650 | 485.7 | 662.8 | 715.6 | 593.1 | 499.6 | 581.1 | 351.5 | 367.6 | 357.3 | 336.2 | 364.6 | 385.5 | 390.9 | 335.8
1561 | 1340 | 473 | 189.2 | 221.1639 | 388.4 | 339.1 | 344.9 | 365 | 587.2 | 63.2 | 18.4 | 112.7 | 5.3 | 273.2 | 9.5 | 294.2 | 310.7 | 717.2 | 662.6 | 425 | 466.8 | 765.7 | 869.7 | 729.3 | 586.6 | 652.3 | 500 | 663.3 | 712.3 | 603 | 500.3 | 583 | 351.8 | 367.8 | 358 | 336.6 | 365.2 | 385.8 | 391.3 | 336.2
1562 | 1341 | 473.4 | 189.36 | 221.3509 | 394.8 | 339.3 | 345.3 | 365.9 | 577.3 | 63.3 | 18.4 | 112.6 | 5.2 | 274.5 | 9.4 | 294.4 | 311 | 720.6 | 685 | 425.2 | 467 | 768.2 | 872.7 | 731.1 | 586.7 | 646.1 | 515 | 663.6 | 701.7 | 613.1 | 500.5 | 584.9 | 352.1 | 368.1 | 358.5 | 337 | 365.7 | 385.6 | 391.5 | 336.5
1563 | 1342 | 471.4 | 188.56 | 220.4158 | 405 | 338.9 | 346.3 | 365.7 | 570 | 63.5 | 18.4 | 112.4 | 6.3 | 272.4 | 9.2 | 294.6 | 311.3 | 720.6 | 693.2 | 425.5 | 467.2 | 757 | 864 | 731.5 | 587.1 | 638.1 | 518.7 | 664 | 693.7 | 616.4 | 501.2 | 585.7 | 352.5 | 368.5 | 358.8 | 337.3 | 366.1 | 385.7 | 392 | 336.8
1564 | 1343 | 471.3 | 188.52 | 220.369 | 421.7 | 338.8 | 347.1 | 366.5 | 562.5 | 63.7 | 18.4 | 112.3 | 6 | 275 | 8.9 | 294.8 | 311.6 | 711.2 | 695.8 | 425.7 | 467.5 | 746.8 | 856 | 731.9 | 587.5 | 636.5 | 521.2 | 664.6 | 692.9 | 617.1 | 501.7 | 585.4 | 352.8 | 368.8 | 359.3 | 337.6 | 366.5 | 385.5 | 392.2 | 337.2
1565 | 1344 | 471.6 | 188.64 | 220.5093 | 433.1 | 338.8 | 347.1 | 366.2 | 554.4 | 63.9 | 18.4 | 112.1 | 5.8 | 269.3 | 8.5 | 295 | 312 | 707.9 | 710.9 | 425.9 | 467.7 | 751.8 | 853 | 732.5 | 588.1 | 546.5 | 530.1 | 665.3 | 683.4 | 621.7 | 502 | 586.5 | 353.2 | 369.3 | 359.6 | 337.9 | 366.9 | 385.3 | 392 | 337.5
1566 | 1345 | 471.8 | 188.72 | 220.6028 | 442.8 | 339 | 346.4 | 364.9 | 549.6 | 63.8 | 18.4 | 112 | 5.7 | 275.7 | 8.3 | 295.2 | 312.2 | 698 | 709 | 426.2 | 468 | 745.5 | 846.5 | 732.3 | 588.6 | 637 | 527.6 | 666 | 675.7 | 617.5 | 502.6 | 587.1 | 353.5 | 369.6 | 359.8 | 338.1 | 367.3 | 385.1 | 392 | 337.8
1567 | 1346 | 471.1 | 188.44 | 220.2755 | 452.1 | 339.8 | 346 | 362.7 | 546.3 | 63.7 | 18.4 | 112.1 | 6 | 275.9 | 8.1 | 295.4 | 312.5 | 690.9 | 706 | 426.5 | 468.3 | 741.7 | 846.5 | 732.7 | 589.3 | 638.8 | 521.9 | 666.7 | 672 | 617.7 | 503.3 | 587.4 | 353.8 | 369.7 | 359.6 | 338.2 | 367.6 | 385.1 | 392.1 | 338.1
1568 | 1347 | 471.1 | 188.44 | 220.2755 | 461.2 | 339.9 | 345.5 | 361.5 | 545 | 63.7 | 18.4 | 112 | 6.3 | 276.4 | 7.7 | 295.6 | 312.7 | 692.8 | 703.9 | 426.8 | 468.5 | 735 | 843 | 733 | 590 | 638.9 | 521.2 | 667.4 | 666.8 | 613.6 | 504 | 587.5 | 354.1 | 369.9 | 359.9 | 338.3 | 368 | 385.1 | 392.1 | 338.4
1569 | 1348 | 471.9 | 188.76 | 220.6496 | 467 | 339.5 | 345.9 | 361.6 | 542.1 | 63.7 | 18.4 | 111.9 | 6.3 | 279.1 | 8.5 | 295.7 | 313 | 690.1 | 715.6 | 427 | 468.7 | 731.4 | 830.8 | 732.6 | 590.8 | 642.3 | 528.6 | 668.1 | 659 | 615.7 | 504.7 | 587.7 | 354.4 | 370.1 | 360.3 | 338.7 | 368.3 | 384.9 | 392.3 | 338.6
1570 | 1349 | 472.7 | 189.08 | 221.0236 | 476 | 339.5 | 345.9 | 360.7 | 539.5 | 63.6 | 18.4 | 111.9 | 6 | 277.3 | 9.8 | 295.9 | 313.3 | 686.1 | 721.8 | 427.4 | 468.9 | 728.9 | 825.7 | 732.5 | 591.6 | 646.8 | 541.6 | 668.4 | 652.4 | 617.4 | 505.3 | 588.7 | 354.7 | 370.4 | 361 | 339.2 | 368.5 | 384.4 | 391.8 | 338.8
1571 | 1350 | 472.8 | 189.12 | 221.0704 | 480.8 | 339.3 | 347.1 | 357.7 | 534.6 | 63.5 | 18.4 | 112 | 6 | 273 | 9.8 | 296.1 | 313.6 | 685.3 | 723.4 | 427.7 | 469.2 | 730.6 | 829 | 733.5 | 592.4 | 647.7 | 537.9 | 669.2 | 655.4 | 620.4 | 505.7 | 588.1 | 355.1 | 370.8 | 361.5 | 339.6 | 368.7 | 384 | 391.6 | 339.1
1572 | 1351 | 472 | 188.8 | 220.6963 | 484.5 | 338.8 | 347.8 | 357.1 | 535.1 | 63.4 | 18.4 | 112.2 | 6 | 258.1 | 8.9 | 296.3 | 313.8 | 681.9 | 714.4 | 428 | 469.4 | 725.1 | 825.8 | 732.4 | 593.1 | 651.5 | 533.3 | 670.2 | 656.6 | 614.1 | 506.3 | 586.9 | 355.5 | 371.1 | 361.8 | 339.9 | 369 | 383.6 | 391.3 | 339.4
1573 | 1352 | 473 | 189.2 | 221.1639 | 488.3 | 338.1 | 347.6 | 356.5 | 533.8 | 63.4 | 18.4 | 112.2 | 5.9 | 282.6 | 8.7 | 296.5 | 314.1 | 682.4 | 717.7 | 428.4 | 469.6 | 712.6 | 830.8 | 733.5 | 593.7 | 660.7 | 534.6 | 671.2 | 658.9 | 609.7 | 506.7 | 585.7 | 355.8 | 371.6 | 362.3 | 340.1 | 369.2 | 383.1 | 391.2 | 339.6
1574 | 1353 | 473.7 | 189.48 | 221.4912 | 493.7 | 337.7 | 347 | 356 | 531.5 | 63.5 | 18.4 | 112.3 | 5.3 | 274 | 8.8 | 296.7 | 314.4 | 684.4 | 730.4 | 428.8 | 469.8 | 708.7 | 832.8 | 736 | 594.4 | 661.1 | 545.2 | 671.8 | 659.3 | 610 | 507.4 | 585.7 | 356.2 | 372.2 | 362.9 | 340.3 | 369.4 | 382.6 | 390.9 | 339.8
1575 | 1354 | 473.6 | 189.44 | 221.4444 | 500.3 | 337.4 | 348.5 | 355.9 | 533.9 | 63.7 | 18.4 | 112.4 | 5.9 | 272.1 | 8.7 | 296.9 | 314.6 | 685.5 | 721.9 | 429.1 | 470 | 710.8 | 850.2 | 737.9 | 595.1 | 655.3 | 542.9 | 672.2 | 659.4 | 610.4 | 508.3 | 586.2 | 356.6 | 372.6 | 363.4 | 340.6 | 369.7 | 383 | 391 | 340.1
1576 | 1355 | 473.3 | 189.32 | 221.3042 | 499.4 | 337.4 | 349.8 | 355.6 | 545.2 | 63.8 | 18.4 | 112.3 | 6.3 | 281.6 | 8.6 | 297.1 | 314.8 | 692.5 | 727.1 | 429.5 | 470.3 | 703 | 854.7 | 739.1 | 595.7 | 655 | 542.1 | 672.9 | 664.1 | 608.2 | 509.3 | 586.6 | 356.9 | 372.9 | 363.6 | 340.8 | 370.1 | 383.7 | 391.7 | 340.5
1577 | 1356 | 473.2 | 189.28 | 221.2574 | 501.5 | 337 | 350.8 | 355.5 | 545.5 | 64 | 18.4 | 112.3 | 5.6 | 264.9 | 8.6 | 297.3 | 315 | 694.2 | 724.2 | 429.9 | 470.6 | 701.6 | 844.3 | 738.6 | 596.4 | 649.7 | 549 | 673.3 | 660.5 | 608.6 | 510.1 | 587.9 | 357.3 | 373.5 | 364.1 | 341.1 | 370.4 | 383.6 | 391.9 | 340.8
1578 | 1357 | 473.3 | 189.32 | 221.3042 | 500.6 | 337.4 | 352.5 | 355.7 | 542.3 | 64 | 18.4 | 112.3 | 5.6 | 268 | 8.5 | 297.5 | 315.4 | 681.5 | 713.8 | 430.2 | 470.7 | 700.8 | 813.5 | 734.2 | 597 | 642.5 | 540.5 | 673.8 | 652 | 599.4 | 510.8 | 587.9 | 357.7 | 374.2 | 364.6 | 341.5 | 370.7 | 383.3 | 391.8 | 341
1579 | 1358 | 473 | 189.2 | 221.1639 | 506.8 | 337.4 | 352.5 | 354.9 | 537.2 | 64.1 | 18.4 | 112.2 | 5.7 | 268.8 | 8.3 | 297.7 | 315.8 | 680.1 | 704 | 430.5 | 470.9 | 693.8 | 804.6 | 733.3 | 597.8 | 646.6 | 531.5 | 674.2 | 649.8 | 591.4 | 511.6 | 587.8 | 358 | 374.6 | 364.8 | 341.9 | 371.1 | 383.6 | 392.3 | 341.3
1580 | 1359 | 473.1 | 189.24 | 221.2107 | 517.3 | 337.9 | 352.6 | 355.5 | 536.1 | 64.2 | 18.4 | 112.3 | 5.5 | 270.3 | 7.7 | 297.9 | 316.2 | 680 | 702.4 | 430.9 | 471.1 | 697.6 | 799.9 | 732.8 | 598.4 | 645.6 | 527.4 | 674.8 | 648.7 | 592.5 | 512.3 | 588.4 | 358.4 | 374.8 | 364.9 | 342.2 | 371.5 | 384.1 | 392.6 | 341.6
1581 | 1360 | 473.2 | 189.28 | 221.2574 | 520.6 | 338 | 352.2 | 357.3 | 536.3 | 64.2 | 18.4 | 112.4 | 5 | 275.8 | 7.6 | 298.1 | 316.4 | 673.9 | 713.7 | 431.2 | 471.2 | 703.2 | 810 | 732.2 | 599.1 | 650.1 | 527.8 | 675.5 | 650.9 | 593.9 | 513 | 588.9 | 358.6 | 375.1 | 365.1 | 342.4 | 371.8 | 384.7 | 393.2 | 342
1582 | 1361 | 472.3 | 188.92 | 220.8366 | 518.9 | 338 | 352.3 | 358.4 | 539.3 | 64.3 | 18.4 | 112.5 | 4.4 | 273.4 | 7.9 | 298.3 | 316.8 | 673.7 | 733.5 | 431.5 | 471.4 | 710.3 | 828.9 | 734.7 | 599.7 | 657.4 | 539.2 | 675.9 | 656 | 603.8 | 513.7 | 590.4 | 359 | 375.7 | 365.6 | 342.6 | 372.3 | 385.7 | 394.1 | 342.3
1583 | 1362 | 473.8 | 189.52 | 221.538 | 516.7 | 338.1 | 352.2 | 359.3 | 543.4 | 64.2 | 18.4 | 112.6 | 4.8 | 276.6 | 7.6 | 298.4 | 317.2 | 672.9 | 738.2 | 431.8 | 471.7 | 706.9 | 840.3 | 733.9 | 600.3 | 653.4 | 547 | 676.1 | 659.4 | 606 | 514.8 | 591.5 | 359.4 | 375.9 | 366.2 | 343 | 372.7 | 385.9 | 395 | 342.6
1584 | 1363 | 473.1 | 189.24 | 221.2107 | 513.6 | 338.5 | 352.7 | 360.1 | 546.1 | 64.2 | 18.3 | 112.8 | 5.6 | 272.4 | 7.7 | 298.7 | 317.6 | 671 | 737 | 432.1 | 471.8 | 713 | 840.2 | 734.2 | 600.9 | 648.4 | 547.1 | 676.4 | 659.6 | 606.2 | 515.6 | 591.7 | 359.7 | 376.3 | 366.7 | 343.3 | 373.1 | 385.7 | 395.4 | 342.8
1585 | 1364 | 472.8 | 189.12 | 221.0704 | 513.8 | 339.1 | 353.6 | 360.3 | 546.7 | 64.1 | 18.3 | 112.9 | 5.6 | 267.1 | 7.3 | 298.8 | 318.1 | 673.5 | 732.9 | 432.3 | 472 | 724.1 | 843.4 | 735.7 | 601.6 | 645.4 | 547.8 | 676.8 | 667.4 | 612.7 | 516.5 | 592.9 | 360.1 | 376.9 | 367.1 | 343.6 | 373.6 | 386.2 | 395.7 | 343.2
1586 | 1365 | 471.6 | 188.64 | 220.5093 | 510 | 339.6 | 354.1 | 360.7 | 552 | 64.1 | 18.3 | 113.1 | 6 | 275.9 | 7.4 | 299.1 | 318.6 | 683.4 | 716.1 | 432.7 | 472.2 | 730.3 | 840.1 | 734.9 | 602 | 640.8 | 543 | 677.1 | 665.9 | 615.3 | 517.4 | 593.9 | 360.5 | 377.5 | 367.3 | 343.8 | 374 | 386.7 | 396.4 | 343.5
1587 | 1366 | 471.6 | 188.64 | 220.5093 | 511.9 | 340.7 | 354.7 | 360.5 | 553.5 | 64.1 | 18.3 | 113.2 | 6.1 | 273.9 | 7.5 | 299.3 | 319 | 692.4 | 705.6 | 432.9 | 472.4 | 728.4 | 847.6 | 734.6 | 602.3 | 640 | 539.7 | 677.3 | 663 | 616.4 | 518.4 | 594.5 | 360.9 | 377.9 | 367.6 | 344 | 374.5 | 387.3 | 397.2 | 343.9
1588 | 1367 | 472 | 188.8 | 220.6963 | 512.5 | 341.3 | 355 | 361.3 | 556.6 | 64.1 | 18.3 | 113.4 | 5.8 | 281.8 | 7.2 | 299.5 | 319.5 | 693.3 | 679.3 | 433.2 | 472.6 | 737.2 | 825.5 | 730.7 | 602.4 | 640 | 529.8 | 677.8 | 658.8 | 615.3 | 519.4 | 594.5 | 361.3 | 378.2 | 367.7 | 344.2 | 375.1 | 388.6 | 398.5 | 344.4
1589 | 1368 | 472 | 188.8 | 220.6963 | 512.4 | 342 | 356.6 | 363.2 | 560.1 | 64.2 | 18.3 | 113.5 | 5.9 | 268.6 | 6.7 | 299.7 | 320 | 691.6 | 669.1 | 433.6 | 472.9 | 722.3 | 810.3 | 730.4 | 602.4 | 643.2 | 520.9 | 678.5 | 661 | 603 | 520.6 | 593.1 | 361.7 | 378.7 | 367.9 | 344.4 | 375.7 | 389.1 | 399.3 | 344.8
1590 | 1369 | 471.7 | 188.68 | 220.556 | 511.6 | 342.4 | 357.7 | 364.9 | 559 | 64.2 | 18.3 | 113.5 | 4.7 | 265.8 | 6.6 | 299.9 | 320.6 | 686.9 | 651.2 | 433.9 | 473.1 | 718.3 | 806.2 | 729.7 | 602.4 | 651.6 | 512.8 | 679 | 667.6 | 595.9 | 521.4 | 592.6 | 362.2 | 379.4 | 368.4 | 344.6 | 376.2 | 389.6 | 399.9 | 345.1
1591 | 1370 | 472.5 | 189 | 220.9301 | 511.1 | 343.1 | 359.7 | 365.5 | 561.3 | 64.3 | 18.3 | 113.6 | 4.6 | 270.3 | 6.5 | 300.1 | 321.1 | 681.7 | 650.5 | 434.1 | 473.3 | 723.1 | 801.5 | 728.5 | 602.3 | 658.6 | 508.1 | 679.7 | 670.8 | 590.4 | 522.4 | 592.1 | 362.7 | 380.2 | 369 | 344.9 | 376.8 | 390.4 | 400.5 | 345.5
1592 | 1371 | 472.3 | 188.92 | 220.8366 | 511.3 | 345.1 | 361.2 | 365.7 | 564.1 | 64.3 | 18.3 | 113.8 | 5.4 | 281.4 | 6.8 | 300.3 | 321.6 | 675.1 | 656.9 | 434.4 | 473.4 | 724.7 | 800.1 | 728.4 | 602.1 | 659.3 | 509.1 | 680.1 | 676.6 | 590.6 | 523.5 | 592.3 | 363.3 | 380.7 | 369.6 | 345.4 | 377.3 | 390.8 | 400.9 | 346
1593 | 1372 | 472.3 | 188.92 | 220.8366 | 510.8 | 345.3 | 360.5 | 365.9 | 567.8 | 64.4 | 18.3 | 113.8 | 5.6 | 281.6 | 6.5 | 300.4 | 322 | 672 | 649.5 | 434.7 | 473.7 | 723.5 | 795.8 | 727.4 | 602 | 658.7 | 503.4 | 680.5 | 678.2 | 591.3 | 524.2 | 592.4 | 363.8 | 381.1 | 370 | 345.6 | 377.8 | 391.4 | 401.2 | 346.3
1594 | 1373 | 471.5 | 188.6 | 220.4625 | 509.7 | 345.4 | 360.2 | 366.4 | 573.4 | 64.4 | 18.3 | 113.9 | 5.7 | 284.4 | 6.1 | 300.7 | 322.5 | 668.9 | 641.6 | 435 | 473.9 | 724.4 | 790.5 | 725.2 | 601.8 | 652 | 499.5 | 680.6 | 681.2 | 596 | 524.9 | 592.3 | 364.3 | 381.5 | 370.6 | 345.9 | 378.4 | 392.1 | 401.9 | 346.7
1595 | 1374 | 472.6 | 189.04 | 220.9769 | 512.4 | 346.2 | 361.2 | 367.7 | 572 | 64.5 | 18.3 | 114 | 5.7 | 280.9 | 5.8 | 300.9 | 323.4 | 665.9 | 673.2 | 435.2 | 474.1 | 732 | 811.9 | 729.6 | 601.9 | 651.7 | 509 | 681.1 | 677.3 | 598.8 | 525.7 | 592.7 | 364.8 | 381.9 | 371.1 | 346.3 | 378.8 | 392.2 | 402.4 | 347
1596 | 1375 | 472.2 | 188.88 | 220.7898 | 508.3 | 346.9 | 361.8 | 367.2 | 568.3 | 64.5 | 18.3 | 114.1 | 5.6 | 280.3 | 5.6 | 301.1 | 324 | 677.5 | 705.5 | 435.4 | 474.4 | 749.4 | 817.4 | 730.1 | 602.1 | 650 | 528.3 | 681.3 | 671.2 | 601.4 | 526.3 | 593.4 | 365.2 | 382.1 | 371.8 | 346.8 | 379.2 | 392.2 | 402.8 | 347.2
1597 | 1376 | 470.2 | 188.08 | 219.8547 | 504.6 | 346.8 | 361.7 | 366.8 | 566.1 | 64.6 | 18.3 | 114.3 | 6.3 | 277.8 | 5 | 301.3 | 324.4 | 683.5 | 722.4 | 435.6 | 474.6 | 755.7 | 798.7 | 729.4 | 602.3 | 651 | 551.5 | 681.3 | 663.6 | 612.3 | 527.2 | 594.5 | 365.6 | 382.2 | 372.4 | 347.4 | 379.5 | 392 | 403.2 | 347.4
1598 | 1377 | 470.3 | 188.12 | 219.9014 | 503.5 | 347.4 | 362.3 | 367.4 | 573.6 | 64.6 | 18.3 | 114.4 | 6.1 | 281.1 | 5 | 301.5 | 324.2 | 680.8 | 732.8 | 435.9 | 474.8 | 762.7 | 808.8 | 729.8 | 602.6 | 656.1 | 570.4 | 681 | 658.6 | 625.5 | 528.1 | 596.8 | 366.1 | 382.6 | 373.1 | 348.3 | 379.8 | 391.9 | 403.1 | 347.7
1599 | 1378 | 470.4 | 188.16 | 219.9482 | 498.2 | 347.8 | 362.8 | 367.1 | 574.9 | 64.7 | 18.3 | 114.5 | 5.4 | 285.2 | 4.9 | 301.8 | 324.5 | 686.9 | 741.1 | 436.2 | 474.9 | 765.2 | 822.3 | 733 | 602.8 | 655.8 | 584.3 | 681 | 654.1 | 627.3 | 528.8 | 597.4 | 366.6 | 383 | 373.3 | 348.6 | 380.1 | 391.6 | 403 | 347.9
1600 | 1379 | 472.6 | 189.04 | 220.9769 | 489.5 | 347.8 | 363.8 | 365.7 | 568.9 | 64.6 | 18.3 | 114.6 | 6 | 257.9 | 5 | 302 | 324.8 | 694.6 | 748.9 | 436.4 | 475.1 | 768.6 | 828.3 | 734.7 | 602.9 | 654.1 | 605 | 681.3 | 651.2 | 630.2 | 529.6 | 598.7 | 367.1 | 383.5 | 373.7 | 348.7 | 380.3 | 391.3 | 402.6 | 348.2
1601 | 1380 | 472.6 | 189.04 | 220.9769 | 483.5 | 348.2 | 363.8 | 364.1 | 570.1 | 64.7 | 18.3 | 114.7 | 6.1 | 255.7 | 5.6 | 302.3 | 324.8 | 705.2 | 755.1 | 436.7 | 475.2 | 779 | 827.2 | 737.2 | 603.4 | 660 | 636.8 | 681.3 | 647 | 638.8 | 530.4 | 600.8 | 367.6 | 384.3 | 374.6 | 349.1 | 380.4 | 391.1 | 402.4 | 348.4
1602 | 1381 | 471.6 | 188.64 | 220.5093 | 492 | 349.2 | 363.3 | 363.5 | 574 | 64.6 | 18.3 | 114.9 | 6.9 | 260.1 | 5.9 | 302.5 | 324.7 | 716.2 | 762.6 | 436.9 | 475.4 | 785.8 | 827.6 | 738.8 | 604.2 | 663.9 | 655.9 | 681.5 | 642.5 | 638.3 | 531.3 | 601.8 | 368.2 | 385.1 | 375.5 | 349.7 | 380.5 | 390.5 | 402.2 | 348.7
1603 | 1382 | 471.2 | 188.48 | 220.3223 | 488.3 | 350 | 363 | 363.5 | 576.3 | 64.7 | 18.3 | 115.1 | 6.8 | 244.6 | 6.2 | 302.7 | 324.9 | 711.8 | 770.8 | 437.1 | 475.6 | 781.3 | 808 | 736.1 | 605.1 | 666.9 | 660.1 | 682 | 638.7 | 636.6 | 532.4 | 601.8 | 368.7 | 385.6 | 375.9 | 350.3 | 380.7 | 390.2 | 402 | 349
1604 | 1383 | 471.1 | 188.44 | 220.2755 | 488.1 | 350 | 362.8 | 362.9 | 581.2 | 64.7 | 18.3 | 115.2 | 6.3 | 250.6 | 6.3 | 303 | 324.9 | 689.3 | 766.6 | 437.3 | 475.7 | 765.3 | 787.6 | 732.9 | 605.9 | 670.9 | 649 | 682.2 | 637.2 | 634.9 | 533.3 | 601.4 | 369.3 | 386.3 | 376.5 | 350.8 | 380.8 | 389.7 | 402 | 349.2
1605 | 1384 | 471.5 | 188.6 | 220.4625 | 496.2 | 349.7 | 363.7 | 362.2 | 576.5 | 64.7 | 18.3 | 115.3 | 5.8 | 251.9 | 6 | 303.2 | 324.8 | 677.1 | 761 | 437.6 | 475.9 | 757.8 | 772.8 | 730.9 | 606.6 | 671.3 | 639.3 | 683 | 643.1 | 631 | 534.1 | 601.1 | 369.9 | 387 | 377.4 | 351.2 | 380.8 | 389.2 | 401.4 | 349.4
1606 | 1385 | 470.9 | 188.36 | 220.182 | 496.5 | 349.9 | 364.2 | 361.8 | 572.9 | 64.6 | 18.3 | 115.3 | 5.5 | 247.2 | 5.9 | 303.4 | 324.7 | 665.9 | 732.2 | 437.8 | 476.1 | 733.9 | 744.4 | 726.9 | 607.4 | 674 | 624.1 | 683.5 | 639.4 | 624.8 | 535 | 600.3 | 370.4 | 387.6 | 378.1 | 351.6 | 380.8 | 388.8 | 400.8 | 349.7
1607 | 1386 | 471.2 | 188.48 | 220.3223 | 497.1 | 350 | 365.5 | 360.9 | 570.4 | 64.6 | 18.3 | 115.3 | 5.7 | 248.7 | 5.3 | 303.6 | 324.9 | 663.9 | 716.6 | 438.1 | 476.4 | 721.2 | 731.3 | 724.2 | 608 | 676.4 | 609.6 | 684 | 631.2 | 613.6 | 535.9 | 599.2 | 371.1 | 388.5 | 379.1 | 352.1 | 380.9 | 388.8 | 400.7 | 349.9
1608 | 1387 | 471.6 | 188.64 | 220.5093 | 497.7 | 349.9 | 367.1 | 361.4 | 562.5 | 64.7 | 18.3 | 115.3 | 5.5 | 255.6 | 4.5 | 303.9 | 325 | 648.7 | 693.5 | 438.3 | 476.6 | 720.2 | 730 | 722 | 608.4 | 674.8 | 590.4 | 685.1 | 628.9 | 601.3 | 536.8 | 598.2 | 371.6 | 388.7 | 379.6 | 352.3 | 381.2 | 389.2 | 401.1 | 350.3
1609 | 1388 | 472 | 188.8 | 220.6963 | 499.5 | 349.5 | 368.3 | 362.7 | 557.5 | 64.8 | 18.3 | 115.3 | 5.4 | 255.8 | 4.3 | 304.1 | 324.9 | 631.2 | 680 | 438.5 | 476.7 | 699.1 | 716.4 | 719.1 | 608.7 | 676.9 | 574.5 | 685.8 | 636.5 | 589.6 | 537.7 | 596.9 | 372 | 389 | 379.9 | 352.4 | 381.5 | 389.9 | 401.6 | 350.7
1610 | 1389 | 471.8 | 188.72 | 220.6028 | 501.3 | 349.5 | 367.6 | 364.6 | 555.3 | 64.9 | 18.3 | 115.5 | 5.8 | 264.5 | 4.3 | 304.4 | 325 | 616.6 | 670 | 438.7 | 476.8 | 682.8 | 707.7 | 715.8 | 608.8 | 683.7 | 559.5 | 686.2 | 640.3 | 580.5 | 538.5 | 595.8 | 372.4 | 389.3 | 380 | 352.5 | 381.9 | 390.7 | 402.2 | 351
1611 | 1390 | 472.3 | 188.92 | 220.8366 | 503.7 | 349.5 | 367.4 | 366.3 | 553.8 | 65 | 18.3 | 115.6 | 5.8 | 260.4 | 4.1 | 304.7 | 325.3 | 616.3 | 663.6 | 438.9 | 476.9 | 673.4 | 704.5 | 713.1 | 608.9 | 682.2 | 547.2 | 686.7 | 641.6 | 572.8 | 539.5 | 594.8 | 372.8 | 389.6 | 380.1 | 352.7 | 382.2 | 390.9 | 402.8 | 351.3
1612 | 1391 | 472 | 188.8 | 220.6963 | 505.7 | 349.8 | 366.4 | 367.8 | 549 | 65 | 18.3 | 115.8 | 5.2 | 249.5 | 3.9 | 304.9 | 325.5 | 616.6 | 667.4 | 439.1 | 477.1 | 668.3 | 706 | 711 | 609.1 | 683.1 | 541.9 | 687.1 | 639.5 | 571.5 | 540.4 | 594.4 | 373.1 | 389.8 | 380.4 | 352.9 | 382.5 | 391.2 | 403.6 | 351.6
1613 | 1392 | 472.8 | 189.12 | 221.0704 | 509 | 349.9 | 365.8 | 368.6 | 549.1 | 65.1 | 18.3 | 116.1 | 5.8 | 248.5 | 4.2 | 305.2 | 325.8 | 616.9 | 667.5 | 439.3 | 477.4 | 674 | 723.3 | 710.7 | 609.4 | 686.1 | 534.4 | 687.5 | 641.5 | 570.3 | 541.2 | 593.7 | 373.4 | 390.3 | 380.6 | 353 | 382.9 | 392.1 | 404.8 | 352
1614 | 1393 | 472 | 188.8 | 220.6963 | 510 | 349.2 | 365.3 | 368.8 | 551.5 | 65.1 | 18.2 | 116.4 | 6.2 | 238.9 | 4.7 | 305.4 | 325.9 | 608.6 | 666.4 | 439.5 | 477.5 | 667.8 | 736.9 | 710.1 | 609.8 | 685.3 | 531 | 687.9 | 641.7 | 568.5 | 542 | 592.9 | 373.7 | 391 | 380.7 | 353.2 | 383.4 | 392.8 | 405.9 | 352.4
1615 | 1394 | 472.7 | 189.08 | 221.0236 | 511.2 | 348.9 | 364.1 | 369.8 | 551.8 | 65.1 | 18.2 | 116.6 | 5.9 | 234.6 | 5.2 | 305.7 | 326.2 | 608.6 | 681.1 | 439.7 | 477.6 | 656.4 | 742.5 | 709.6 | 610.2 | 683.5 | 531.8 | 688 | 637.1 | 569.4 | 543.1 | 592.6 | 374.1 | 391.1 | 381.1 | 353.6 | 383.8 | 393.4 | 406.3 | 352.8
1616 | 1395 | 472.6 | 189.04 | 220.9769 | 509.1 | 348.6 | 364 | 371.1 | 550.7 | 65 | 18.2 | 116.7 | 5.6 | 234.6 | 5.4 | 305.9 | 326.4 | 600.9 | 685.6 | 439.9 | 477.8 | 659.8 | 744.9 | 708.2 | 610.6 | 682.1 | 524.5 | 688.2 | 637.2 | 568.5 | 544.1 | 591.7 | 374.5 | 391.5 | 381.4 | 354 | 384.2 | 394.1 | 406.7 | 353.1
1617 | 1396 | 472.6 | 189.04 | 220.9769 | 502.9 | 348.3 | 363.8 | 371.3 | 548.9 | 64.9 | 18.2 | 116.7 | 5.5 | 235.1 | 5.6 | 306.2 | 326.6 | 599.5 | 689 | 440.1 | 478 | 660.1 | 764.2 | 709.6 | 611.1 | 686.2 | 532.3 | 688.3 | 634.1 | 580.6 | 544.6 | 592.2 | 374.9 | 391.7 | 381.8 | 354.4 | 384.5 | 394.4 | 406.9 | 353.4
1618 | 1397 | 472.8 | 189.12 | 221.0704 | 501.8 | 349 | 364.3 | 371.4 | 545 | 64.8 | 18.2 | 116.9 | 5.9 | 234.2 | 5.7 | 306.3 | 326.8 | 613.8 | 716 | 440.3 | 478.2 | 684.7 | 782.5 | 713.7 | 611.6 | 683.5 | 545.2 | 688.3 | 638.5 | 590.1 | 545.6 | 593.1 | 375.3 | 392 | 381.9 | 354.8 | 384.7 | 394.1 | 406.5 | 353.6
1619 | 1398 | 472.7 | 189.08 | 221.0236 | 502.9 | 348.6 | 364.6 | 370.1 | 547.5 | 64.8 | 18.2 | 117 | 5.7 | 242 | 5.8 | 306.6 | 327 | 649.6 | 738.9 | 440.4 | 478.4 | 711.5 | 783.2 | 716.4 | 612.2 | 677.2 | 585.1 | 687.7 | 638 | 610.2 | 546.6 | 596.4 | 375.6 | 392.1 | 381.9 | 355.1 | 384.9 | 393.5 | 406 | 353.7
1620 | 1399 | 472.8 | 189.12 | 221.0704 | 503.6 | 349.7 | 364.6 | 368.5 | 557.9 | 64.9 | 18.2 | 117.1 | 5.6 | 250.6 | 5.8 | 306.8 | 327.3 | 661 | 755.9 | 440.6 | 478.7 | 710.4 | 768.1 | 716.4 | 613.1 | 675.4 | 607.1 | 687.2 | 632.9 | 615.2 | 547.5 | 597.6 | 376 | 392.3 | 382.5 | 355.6 | 385 | 392.8 | 405.6 | 353.8
1621 | 1400 | 472.3 | 188.92 | 220.8366 | 503.3 | 350.7 | 366.2 | 368.1 | 572.5 | 64.9 | 18.2 | 117.2 | 5.7 | 246.8 | 5.5 | 307.1 | 327.5 | 655.9 | 766.8 | 440.7 | 479 | 703.4 | 742.2 | 715 | 614 | 675.9 | 626 | 687.3 | 632.6 | 619.1 | 548.4 | 598.4 | 376.6 | 392.8 | 383.1 | 356.4 | 385 | 392.1 | 405.2 | 354
1622 | 1401 | 472 | 188.8 | 220.6963 | 502.8 | 351.1 | 368.7 | 368.8 | 582.1 | 65 | 18.2 | 117.3 | 5.8 | 257.6 | 5.4 | 307.3 | 327.5 | 648.5 | 762.1 | 440.9 | 479.2 | 694.4 | 731.2 | 712.9 | 614.9 | 676.2 | 625.4 | 687.8 | 633.6 | 612.4 | 549 | 597.8 | 377.3 | 393.3 | 383.5 | 357.1 | 385.1 | 391.6 | 405.3 | 354.2
1623 | 1402 | 471.6 | 188.64 | 220.5093 | 496.6 | 351.6 | 369.8 | 369.2 | 580.9 | 65 | 18.2 | 117.5 | 5.9 | 264.4 | 5.4 | 307.6 | 327.6 | 638.3 | 773.7 | 441 | 479.5 | 692.9 | 750.8 | 714.6 | 616 | 680.8 | 621.1 | 688.2 | 639.6 | 611.9 | 549.9 | 598 | 378 | 393.6 | 383.7 | 357.3 | 385.3 | 391.4 | 405.4 | 354.6
1624 | 1403 | 471.8 | 188.72 | 220.6028 | 494.2 | 352.2 | 369.1 | 368.9 | 572.5 | 65.2 | 18.2 | 117.5 | 6.1 | 258.7 | 5.1 | 307.9 | 328 | 641 | 769.7 | 441.2 | 479.8 | 706 | 783.7 | 719.4 | 617.1 | 681.4 | 619.2 | 688.4 | 642 | 622.4 | 550.8 | 600.2 | 378.4 | 393.8 | 383.8 | 357.3 | 385.5 | 391.6 | 405.3 | 354.9
1625 | 1404 | 472.1 | 188.84 | 220.7431 | 494 | 353.4 | 368.4 | 369.9 | 573 | 65.5 | 18.2 | 117.5 | 5.8 | 247.1 | 4.8 | 308.1 | 328.2 | 647.1 | 731.6 | 441.3 | 480 | 724.4 | 801 | 721.7 | 618.1 | 677.4 | 604.6 | 688.7 | 650.2 | 626.6 | 551.6 | 600.8 | 378.9 | 394.2 | 384.1 | 357.3 | 385.8 | 392.5 | 405.6 | 355.2
1626 | 1405 | 472.1 | 188.84 | 220.7431 | 493.9 | 353.4 | 367.3 | 370.6 | 589.9 | 65.8 | 18.2 | 117.4 | 5.9 | 242.7 | 4.8 | 308.4 | 328.5 | 661.2 | 701.5 | 441.4 | 480.3 | 736.8 | 808.7 | 722.8 | 618.9 | 675.8 | 594.1 | 689.1 | 659.9 | 630.3 | 552.5 | 602.4 | 379.3 | 394.8 | 384.3 | 357.4 | 386.2 | 393.8 | 406.8 | 355.6
1627 | 1406 | 472.1 | 188.84 | 220.7431 | 494.7 | 353.9 | 367.7 | 373.3 | 600.2 | 66.1 | 18.2 | 117.3 | 6.3 | 242.9 | 4.9 | 308.6 | 328.8 | 680.1 | 699.4 | 441.5 | 480.6 | 753.8 | 816.5 | 723.8 | 619.6 | 672.5 | 592.9 | 689.5 | 663.9 | 636.3 | 553.2 | 603.3 | 379.8 | 395.4 | 384.5 | 357.5 | 386.6 | 395.1 | 407.4 | 356
1628 | 1407 | 471.8 | 188.72 | 220.6028 | 493.4 | 354.5 | 369.9 | 374.9 | 598.2 | 66.4 | 18.2 | 117.2 | 6 | 250.1 | 4.6 | 308.9 | 329 | 694.2 | 720.3 | 441.6 | 481 | 760 | 806.1 | 726.5 | 620.6 | 672.2 | 612.6 | 689.9 | 658.9 | 644.9 | 554 | 605.8 | 380.2 | 395.7 | 384.7 | 357.9 | 386.8 | 395.1 | 407.6 | 356.3
1629 | 1408 | 472.3 | 188.92 | 220.8366 | 490.4 | 355.6 | 370.8 | 375.2 | 593.9 | 66.6 | 18.2 | 117.2 | 6 | 250.8 | 4.5 | 309.2 | 329.3 | 701.5 | 741.5 | 441.7 | 481.3 | 753.2 | 794.3 | 726.2 | 621.5 | 673.4 | 629.4 | 689.8 | 650.1 | 647.3 | 554.5 | 607.1 | 380.6 | 396 | 385.4 | 358.5 | 387.1 | 394.8 | 407.6 | 356.5
1630 | 1409 | 471.7 | 188.68 | 220.556 | 489.3 | 356.8 | 371.4 | 374.8 | 593.7 | 66.6 | 18.2 | 117.2 | 5.3 | 235.7 | 4.7 | 309.4 | 329.6 | 717.3 | 754.3 | 441.8 | 481.6 | 760.1 | 801.7 | 729.7 | 622.3 | 675 | 649.9 | 689.6 | 644.6 | 652.9 | 555.3 | 608.9 | 381.1 | 396.3 | 385.9 | 359.3 | 387.4 | 394.8 | 407.5 | 356.8
1631 | 1410 | 471.5 | 188.6 | 220.4625 | 487.8 | 357.1 | 371.7 | 374.6 | 588.4 | 66.7 | 18.2 | 117.3 | 5.8 | 233.5 | 4.7 | 309.7 | 329.9 | 720.6 | 759.7 | 441.9 | 482 | 761.6 | 798.3 | 730.3 | 623.2 | 677.6 | 654.6 | 689.7 | 638.6 | 654.3 | 555.9 | 609.4 | 381.6 | 396.4 | 386.3 | 359.8 | 387.6 | 394.7 | 407.6 | 357.1
1632 | 1411 | 471.8 | 188.72 | 220.6028 | 488.1 | 357.8 | 370.9 | 374.8 | 589.4 | 66.7 | 18.2 | 117.4 | 5.9 | 240 | 4.6 | 310 | 330.3 | 706.1 | 758.7 | 442 | 482.3 | 760.8 | 797 | 730.4 | 624.1 | 676.3 | 653.8 | 690 | 635.4 | 653.7 | 556.5 | 609.6 | 382 | 396.5 | 386.7 | 360.1 | 387.8 | 394.7 | 407.6 | 357.4
1633 | 1412 | 471.6 | 188.64 | 220.5093 | 491.1 | 358.5 | 370.2 | 375 | 580.9 | 66.7 | 18.2 | 117.4 | 5.9 | 245.4 | 5.3 | 310.3 | 330.5 | 704 | 750 | 442.1 | 482.5 | 756.3 | 800.5 | 730.5 | 625 | 674.4 | 642.4 | 690.6 | 637.2 | 647.6 | 557.2 | 609.3 | 382.4 | 396.6 | 386.6 | 360.4 | 388.1 | 394.7 | 407.7 | 357.6
1634 | 1413 | 472 | 188.8 | 220.6963 | 492.2 | 358.5 | 369.6 | 375.4 | 573.9 | 66.8 | 18.2 | 117.4 | 5.7 | 242.8 | 5.7 | 310.6 | 330.8 | 692.6 | 728.2 | 442.2 | 482.8 | 741 | 771.7 | 727.5 | 625.7 | 668.2 | 625.1 | 691.4 | 643 | 641.7 | 558.1 | 607.8 | 382.7 | 396.3 | 386 | 360.4 | 388.3 | 394.7 | 407.8 | 357.9
1635 | 1414 | 472.2 | 188.88 | 220.7898 | 495.7 | 358.6 | 369.4 | 376.1 | 566.1 | 66.8 | 18.2 | 117.5 | 5.8 | 241 | 6.1 | 310.9 | 331 | 679.6 | 708.7 | 442.3 | 483.1 | 721.7 | 730 | 722.8 | 626.6 | 668.7 | 611 | 691.9 | 636.6 | 638.3 | 558.9 | 607 | 382.9 | 395.9 | 385.4 | 360.4 | 388.6 | 394.8 | 407.7 | 358.2
1636 | 1415 | 472.3 | 188.92 | 220.8366 | 497.6 | 359.4 | 368.2 | 375.5 | 559.2 | 66.8 | 18.2 | 117.6 | 5.6 | 246.4 | 6.6 | 311.1 | 331.3 | 668.4 | 691.3 | 442.4 | 483.4 | 714.6 | 717.5 | 721.4 | 627.1 | 670.8 | 595.6 | 692.7 | 631.8 | 626.7 | 559.5 | 605.9 | 383 | 395.7 | 385.4 | 360.4 | 388.9 | 394.8 | 407.5 | 358.4
1637 | 1416 | 472.2 | 188.88 | 220.7898 | 501.1 | 359.5 | 367.4 | 375.1 | 552.6 | 66.9 | 18.2 | 117.7 | 5.7 | 243.8 | 7.3 | 311.4 | 331.5 | 669.3 | 667.9 | 442.5 | 483.7 | 709.2 | 707.3 | 720.1 | 627.4 | 662.1 | 581.9 | 693.6 | 629.3 | 615.6 | 560.2 | 605 | 383.3 | 396.1 | 385.4 | 360.4 | 389.1 | 394.8 | 407.3 | 358.7
1638 | 1417 | 472.8 | 189.12 | 221.0704 | 507.5 | 358.6 | 366.1 | 374.9 | 552 | 66.9 | 18.2 | 118 | 6.3 | 238.6 | 7.5 | 311.7 | 331.8 | 651.4 | 647.5 | 442.5 | 483.9 | 703 | 696.3 | 717.5 | 627.5 | 653.2 | 569.4 | 694.2 | 628.7 | 608.6 | 560.9 | 604.1 | 383.6 | 396.4 | 385.8 | 360.6 | 389.4 | 394.8 | 406.9 | 359
1639 | 1418 | 472.3 | 188.92 | 220.8366 | 508.5 | 357.3 | 365.4 | 373.6 | 552.4 | 66.9 | 18.2 | 118.3 | 6.1 | 252.3 | 7.3 | 312 | 332 | 645.3 | 628.2 | 442.6 | 484 | 708 | 683 | 715.8 | 627.4 | 644.2 | 556.5 | 694.8 | 637.6 | 600 | 561.6 | 603 | 384 | 396.7 | 386.2 | 360.9 | 389.7 | 395 | 406.8 | 359.2
1640 | 1419 | 472.6 | 189.04 | 220.9769 | 513 | 356.8 | 366.7 | 373.2 | 552.6 | 67 | 18.1 | 118.4 | 5.4 | 231.6 | 7 | 312.3 | 332.3 | 644.2 | 613.3 | 442.7 | 484.3 | 708 | 685.8 | 713.5 | 627.2 | 636 | 550.1 | 695.3 | 645.4 | 596.4 | 562.4 | 602.3 | 384.5 | 397.5 | 386.6 | 361.1 | 390 | 395.7 | 407.3 | 359.5
1641 | 1420 | 472.7 | 189.08 | 221.0236 | 514.9 | 356.5 | 369.1 | 374 | 553.8 | 67 | 18.1 | 118.5 | 5.6 | 240.8 | 7.1 | 312.5 | 332.7 | 643.8 | 626.8 | 442.8 | 484.6 | 710.9 | 731.3 | 714.8 | 627.1 | 634 | 546.2 | 695.9 | 649.2 | 593.6 | 563.2 | 601.6 | 385 | 398.5 | 387.1 | 361.4 | 390.3 | 396.2 | 407.6 | 359.8
1642 | 1421 | 472.5 | 189 | 220.9301 | 511.3 | 356.2 | 371.5 | 374.4 | 552.6 | 66.9 | 18.1 | 118.7 | 5.7 | 246 | 7.2 | 312.8 | 332.9 | 661.1 | 640.3 | 442.9 | 484.8 | 731.9 | 771.3 | 717.3 | 627.3 | 634.6 | 551.3 | 695.8 | 647.5 | 602.9 | 563.9 | 603.3 | 385.6 | 399.1 | 387.4 | 361.8 | 390.6 | 396.5 | 407.5 | 360
1643 | 1422 | 472.7 | 189.08 | 221.0236 | 507.9 | 355.9 | 372.4 | 373.5 | 547.8 | 66.7 | 18.1 | 118.7 | 5.9 | 235.8 | 7.3 | 313.1 | 333.2 | 672.6 | 661.1 | 442.9 | 485.1 | 744.8 | 790 | 720.6 | 627.5 | 632.8 | 562.2 | 695.6 | 646.1 | 611.8 | 564.3 | 604.8 | 386 | 399.2 | 387.4 | 362.2 | 390.8 | 396.4 | 406.9 | 360.3
1644 | 1423 | 472 | 188.8 | 220.6963 | 507.3 | 355.5 | 372.3 | 372.7 | 544.4 | 66.6 | 18.1 | 118.8 | 6.2 | 235 | 6.9 | 313.4 | 333.5 | 683.3 | 692.3 | 443 | 485.4 | 759.4 | 811.7 | 722.7 | 627.9 | 633.1 | 581.6 | 695.4 | 643.7 | 624.6 | 564.7 | 606.6 | 386.3 | 399 | 387.1 | 362.4 | 391 | 396.2 | 406.6 | 360.5
1645 | 1424 | 472.7 | 189.08 | 221.0236 | 502 | 355.3 | 371.6 | 372.5 | 542.1 | 66.6 | 18.1 | 118.8 | 5.8 | 229.5 | 6.4 | 313.7 | 333.8 | 693 | 711.5 | 443.1 | 485.7 | 766 | 822.7 | 726.1 | 628.5 | 634.1 | 602.7 | 695.2 | 642.9 | 639.3 | 565.3 | 608.5 | 386.6 | 398.8 | 386.7 | 362.5 | 391.2 | 395.9 | 406.3 | 360.6
1646 | 1425 | 472.1 | 188.84 | 220.7431 | 500.4 | 355.5 | 371.2 | 371.7 | 544.3 | 66.6 | 18.1 | 118.9 | 6.1 | 256.6 | 5.7 | 314 | 333.9 | 706.2 | 735.7 | 443.1 | 486.1 | 775.3 | 826.2 | 727.6 | 629.3 | 639.3 | 630.5 | 695 | 641.4 | 651 | 565.9 | 611.6 | 386.8 | 398.6 | 386.7 | 362.9 | 391.5 | 395.8 | 406.3 | 360.8
1647 | 1426 | 472.2 | 188.88 | 220.7898 | 502.5 | 355.8 | 370.8 | 371.1 | 546.8 | 66.7 | 18.1 | 118.9 | 5.7 | 240.5 | 5.7 | 314.3 | 334.1 | 715.6 | 750.4 | 443.2 | 486.4 | 780.9 | 820.8 | 729.4 | 630.3 | 642.1 | 643.4 | 695.2 | 638.9 | 650.7 | 566.6 | 612.4 | 387.1 | 398.4 | 386.6 | 363.3 | 391.7 | 395.8 | 406.5 | 361
1648 | 1427 | 472.1 | 188.84 | 220.7431 | 500.6 | 356 | 370.9 | 371 | 547.3 | 66.7 | 18.1 | 118.8 | 5.9 | 243.1 | 5.7 | 314.6 | 334.4 | 717.4 | 738.4 | 443.3 | 486.8 | 769.7 | 789.1 | 727.2 | 631.3 | 642.9 | 645.4 | 695.6 | 633.1 | 649.4 | 567.1 | 612.9 | 387.3 | 398.2 | 386.5 | 363.6 | 391.9 | 395.8 | 406.6 | 361.1
1649 | 1428 | 471.8 | 188.72 | 220.6028 | 504.4 | 356.3 | 370.2 | 371.3 | 547.4 | 66.7 | 18.1 | 118.8 | 5.6 | 249.2 | 6.4 | 314.8 | 334.6 | 701.6 | 733.3 | 443.3 | 487.2 | 751.7 | 770.3 | 722.7 | 632.5 | 648 | 639.8 | 696.4 | 637.6 | 638.7 | 567.7 | 612 | 387.6 | 398.1 | 386.9 | 364 | 392.2 | 395.6 | 406.7 | 361.3
1650 | 1429 | 472.5 | 189 | 220.9301 | 509.4 | 357 | 370 | 371.3 | 550.6 | 66.8 | 18.1 | 118.7 | 5.8 | 234.8 | 6.4 | 315.1 | 334.9 | 688.7 | 736 | 443.3 | 487.5 | 744.1 | 778.1 | 722.2 | 633.8 | 654.3 | 632 | 696.9 | 634.5 | 637.1 | 568.5 | 612.2 | 388 | 398.5 | 387.5 | 364.5 | 392.4 | 395.6 | 406.7 | 361.6
1651 | 1430 | 472.1 | 188.84 | 220.7431 | 507.9 | 356.7 | 370.1 | 370.7 | 548.7 | 66.9 | 18.1 | 118.8 | 5.1 | 238.1 | 6 | 315.4 | 335.2 | 692.3 | 730.2 | 443.4 | 487.7 | 753.1 | 796.5 | 724.6 | 634.9 | 652.4 | 629.2 | 697.4 | 637.8 | 639.1 | 569.5 | 613 | 388.4 | 399 | 388 | 364.7 | 392.7 | 395.9 | 406.7 | 361.9
1652 | 1431 | 471.7 | 188.68 | 220.556 | 505.8 | 357.5 | 370 | 370.5 | 547.1 | 67 | 18.1 | 118.7 | 5.9 | 242.1 | 5.2 | 315.7 | 335.5 | 691.6 | 737.1 | 443.5 | 488 | 750.2 | 793.2 | 724.2 | 636 | 653.1 | 634.4 | 697.8 | 635 | 638.6 | 570.1 | 614 | 388.8 | 399.5 | 388.4 | 365 | 392.9 | 396 | 406.8 | 362.2
1653 | 1432 | 472.9 | 189.16 | 221.1171 | 501.4 | 358.1 | 370.3 | 371.1 | 544.1 | 67 | 18.1 | 118.9 | 5.8 | 245.9 | 4.7 | 316 | 335.7 | 689.5 | 732.9 | 443.6 | 488.3 | 761.8 | 779.1 | 721.3 | 637.2 | 652.6 | 639.3 | 697.9 | 632 | 640.5 | 570.9 | 614.8 | 389.2 | 399.9 | 388.8 | 365.5 | 393.1 | 396 | 407.1 | 362.3
1654 | 1433 | 472.9 | 189.16 | 221.1171 | 497.2 | 358.7 | 370.4 | 371 | 543.3 | 67 | 18.1 | 119.1 | 5.9 | 258.9 | 4.3 | 316.3 | 336 | 686.2 | 724.8 | 443.6 | 488.6 | 752.5 | 773.6 | 720 | 638.3 | 652.7 | 619.3 | 698.7 | 629.7 | 628.5 | 571.5 | 613.6 | 389.6 | 400.1 | 389 | 365.7 | 393.3 | 395.8 | 406.9 | 362.5
1655 | 1434 | 472.5 | 189 | 220.9301 | 497.1 | 358.5 | 370.5 | 370.9 | 540.5 | 67.2 | 18.1 | 119.2 | 6 | 253.2 | 5.3 | 316.6 | 336.2 | 682.8 | 720.4 | 443.7 | 488.8 | 738.3 | 773.2 | 719.8 | 639.4 | 654.8 | 614.1 | 699.5 | 630.8 | 623.7 | 572.1 | 612.9 | 389.9 | 400.1 | 388.9 | 365.9 | 393.4 | 395.6 | 406.6 | 362.7
1656 | 1435 | 472.6 | 189.04 | 220.9769 | 496.7 | 358.7 | 370.4 | 370.4 | 539.9 | 67.2 | 18.1 | 119.3 | 6 | 253 | 6.1 | 316.9 | 336.5 | 688 | 726.3 | 443.7 | 489.1 | 731.6 | 783.9 | 720.3 | 640.6 | 659.6 | 605.4 | 700.2 | 630.1 | 621.5 | 572.7 | 612.8 | 390.1 | 400.2 | 388.8 | 365.9 | 393.6 | 395.4 | 406.6 | 363
1657 | 1436 | 472.7 | 189.08 | 221.0236 | 501.2 | 358.9 | 369 | 370.4 | 536.2 | 67.2 | 18.1 | 119.4 | 5.7 | 246.4 | 6.9 | 317.2 | 336.7 | 693.1 | 731.4 | 443.8 | 489.3 | 726.1 | 783.7 | 720.7 | 641.6 | 659 | 608.1 | 700.7 | 626.5 | 620.1 | 573.3 | 613.2 | 390.4 | 400.3 | 389.1 | 366.1 | 393.9 | 395.4 | 407 | 363.2
1658 | 1437 | 472.6 | 189.04 | 220.9769 | 503 | 359.5 | 367.9 | 371 | 535 | 67.1 | 18.1 | 119.5 | 5.4 | 252.3 | 6.9 | 317.4 | 336.9 | 685.5 | 725.1 | 443.9 | 489.6 | 744 | 783.5 | 721 | 642.6 | 661.6 | 604.4 | 701.1 | 627.9 | 623 | 574 | 613.1 | 390.6 | 400.5 | 389.3 | 366.3 | 394.1 | 395.6 | 407.3 | 363.4
1659 | 1438 | 472.8 | 189.12 | 221.0704 | 501.4 | 359.6 | 367.5 | 371.7 | 536.7 | 67.1 | 18.1 | 119.6 | 6.1 | 254.3 | 6.6 | 317.8 | 337.2 | 674.5 | 720.3 | 443.9 | 489.9 | 744.7 | 782.2 | 719.2 | 643.6 | 664.7 | 601.5 | 701.7 | 625.1 | 623.8 | 574.7 | 613.3 | 391 | 400.7 | 389.6 | 366.4 | 394.3 | 395.6 | 407.5 | 363.6
1660 | 1439 | 472.4 | 188.96 | 220.8834 | 499.5 | 358.6 | 367.3 | 372.1 | 534.6 | 67.2 | 18.1 | 119.7 | 6.1 | 244.3 | 6.7 | 318 | 337.4 | 669.8 | 724.3 | 444.1 | 490.2 | 752 | 783.1 | 718.4 | 644.4 | 663.8 | 594.8 | 702.5 | 621.7 | 624.4 | 575.3 | 613.2 | 391.3 | 400.7 | 389.6 | 366.6 | 394.6 | 395.4 | 407.9 | 363.8
1661 | 1440 | 472.7 | 189.08 | 221.0236 | 504.3 | 358.2 | 366 | 372.8 | 531.2 | 67.2 | 18.1 | 119.8 | 6.2 | 252.2 | 6.9 | 318.3 | 337.6 | 669.8 | 736.4 | 444.2 | 490.5 | 754.8 | 800.4 | 721 | 645.3 | 662.6 | 591 | 702.8 | 622.1 | 628.9 | 575.9 | 614.1 | 391.5 | 400.7 | 389.5 | 366.8 | 394.9 | 395.4 | 408.5 | 364.1
1662 | 1441 | 472.4 | 188.96 | 220.8834 | 503.1 | 358.2 | 364.3 | 373.1 | 530.6 | 67.2 | 18.1 | 119.9 | 6.2 | 238.9 | 7 | 318.6 | 337.9 | 669.3 | 741.1 | 444.3 | 490.7 | 757.9 | 812.5 | 722.8 | 646.1 | 665 | 598.1 | 703 | 622.2 | 634.2 | 576.5 | 614.9 | 391.7 | 400.6 | 389.7 | 367.2 | 395.1 | 395.5 | 408.8 | 364.2
1663 | 1442 | 472.6 | 189.04 | 220.9769 | 502 | 358.3 | 363.3 | 373.6 | 531.3 | 67.3 | 18.1 | 119.9 | 6.3 | 238 | 7.3 | 318.9 | 338.1 | 666 | 752.2 | 444.4 | 491 | 756.9 | 830.3 | 726 | 647 | 670.5 | 614.5 | 703.3 | 623.7 | 634.7 | 576.9 | 615.5 | 392 | 400.7 | 389.9 | 367.7 | 395.3 | 395.6 | 409 | 364.4
1664 | 1443 | 472.6 | 189.04 | 220.9769 | 499.4 | 358.5 | 364.1 | 374.4 | 533.3 | 67.3 | 18.1 | 119.8 | 7.2 | 243.2 | 8.4 | 319.2 | 338.4 | 674.2 | 763.8 | 444.5 | 491.2 | 760.2 | 829.2 | 726.9 | 647.9 | 669.5 | 622 | 703.4 | 627.2 | 639.2 | 577.4 | 616.5 | 392.3 | 401 | 390.4 | 368.2 | 395.5 | 395.4 | 408.6 | 364.6
1665 | 1444 | 472.5 | 189 | 220.9301 | 497.9 | 359.3 | 365.6 | 374 | 534.8 | 67.3 | 18 | 119.6 | 6.9 | 245.4 | 9 | 319.5 | 338.7 | 671.6 | 753.8 | 444.7 | 491.4 | 741 | 810.9 | 724.6 | 648.7 | 668.1 | 611.2 | 703.9 | 628.8 | 635.6 | 577.9 | 616.3 | 392.7 | 401.4 | 391 | 368.6 | 395.7 | 395.3 | 408.3 | 364.8
1666 | 1445 | 472.8 | 189.12 | 221.0704 | 498.2 | 359.7 | 365.9 | 373 | 535.9 | 67.4 | 18 | 119.4 | 6.8 | 242.9 | 8.8 | 319.8 | 338.9 | 668 | 760.2 | 444.8 | 491.6 | 740.4 | 809.9 | 724.2 | 649.8 | 667.3 | 602 | 704.3 | 627.1 | 630.6 | 578.8 | 615.3 | 393.1 | 401.8 | 391.2 | 368.9 | 396 | 395.3 | 408.7 | 365
1667 | 1446 | 472.8 | 189.12 | 221.0704 | 500.5 | 360.2 | 366.2 | 373.5 | 534.4 | 67.4 | 18 | 119.3 | 6.2 | 249.6 | 8.1 | 320.1 | 339.1 | 672 | 764.6 | 444.9 | 491.9 | 747.4 | 831.9 | 728.1 | 650.9 | 673.6 | 605.3 | 705 | 626 | 633.3 | 579.5 | 616 | 393.4 | 402 | 391.2 | 369.2 | 396.2 | 395.3 | 409.2 | 365.2
1668 | 1447 | 471.8 | 188.72 | 220.6028 | 500.5 | 360.5 | 365.5 | 374.2 | 534.8 | 67.4 | 18 | 119.3 | 5.8 | 251.7 | 8.4 | 320.4 | 339.4 | 683.3 | 770.7 | 445 | 492.1 | 752.2 | 835.3 | 729.2 | 652 | 675.9 | 627.9 | 704.8 | 626.1 | 648.4 | 580.2 | 619 | 393.8 | 402.1 | 391.2 | 369.4 | 396.4 | 395.2 | 409.1 | 365.4
1669 | 1448 | 471.2 | 188.48 | 220.3223 | 498.5 | 360.6 | 365.2 | 374.4 | 538.5 | 67.4 | 18 | 119.3 | 5 | 257.7 | 8.1 | 320.7 | 339.7 | 682.1 | 762.1 | 445.1 | 492.4 | 749 | 812.3 | 728.6 | 653 | 670.1 | 631 | 704.5 | 623.7 | 649.3 | 580.8 | 620.1 | 394.1 | 402.5 | 391.5 | 369.7 | 396.5 | 395.1 | 409.1 | 365.6
1670 | 1449 | 473.3 | 189.32 | 221.3042 | 494.6 | 360.9 | 366.6 | 374 | 539.6 | 67.5 | 18 | 119.2 | 4.7 | 250.4 | 7.6 | 321 | 340 | 675.1 | 759.4 | 445.3 | 492.7 | 741.8 | 793.2 | 727.7 | 654 | 669.8 | 629.6 | 704.5 | 622.3 | 646.4 | 581.5 | 620.2 | 394.6 | 403.3 | 392.2 | 370.1 | 396.6 | 395.1 | 408.9 | 365.9
1671 | 1450 | 473.3 | 189.32 | 221.3042 | 491.6 | 361.2 | 368.1 | 373.6 | 537.4 | 67.5 | 18 | 119.2 | 5.1 | 263.9 | 6.9 | 321.3 | 340.2 | 684.3 | 763.5 | 445.4 | 493 | 749.2 | 786.4 | 729.1 | 655 | 676.3 | 637.8 | 704.8 | 624.2 | 652.1 | 582 | 621.5 | 395.1 | 403.7 | 392.9 | 370.5 | 396.8 | 395.1 | 409 | 366.1
1672 | 1451 | 473.3 | 189.32 | 221.3042 | 494 | 361.4 | 369 | 373 | 539.9 | 67.4 | 18 | 119.3 | 5.5 | 216.9 | 7.2 | 321.6 | 340.5 | 677.9 | 747.2 | 445.5 | 493.4 | 743.1 | 770.4 | 726.5 | 655.9 | 674.3 | 620.9 | 705.3 | 621.8 | 645 | 582.6 | 621.1 | 395.6 | 404.1 | 393.3 | 370.7 | 396.9 | 395.2 | 409.1 | 366.3
1673 | 1452 | 473.5 | 189.4 | 221.3977 | 497.9 | 361.3 | 368.9 | 372.7 | 543.2 | 67.4 | 18 | 119.3 | 5.9 | 222.5 | 7.3 | 321.9 | 340.8 | 666.8 | 727.8 | 445.7 | 493.6 | 741.2 | 764.2 | 724.7 | 656.6 | 678.9 | 607.6 | 706.4 | 621.8 | 635.8 | 583.1 | 620 | 396 | 404.3 | 393.5 | 370.8 | 397 | 395.2 | 409 | 366.5
1674 | 1453 | 473.9 | 189.56 | 221.5847 | 504.6 | 361.4 | 368.8 | 373 | 541.2 | 67.5 | 18 | 119.2 | 7 | 252.9 | 8.5 | 322.2 | 341.1 | 658.4 | 723.4 | 445.9 | 493.8 | 744.2 | 762.1 | 725.1 | 657.4 | 683.9 | 601.5 | 707.2 | 618.3 | 635.1 | 583.5 | 620.2 | 396.3 | 404.4 | 393.9 | 371.1 | 397.1 | 395.2 | 408.7 | 366.7
1675 | 1454 | 470.4 | 188.16 | 219.9482 | 504.9 | 361 | 369.5 | 372.9 | 539.8 | 67.5 | 18 | 119.2 | 6.9 | 238.8 | 8.7 | 322.5 | 341.3 | 657.8 | 725.4 | 446 | 494 | 750.1 | 763.6 | 723.7 | 658.1 | 683.2 | 598.5 | 707.8 | 623.3 | 631 | 584.3 | 620.4 | 396.7 | 404.8 | 394.1 | 371.4 | 397.3 | 395.5 | 408.9 | 366.9
1676 | 1455 | 470.2 | 188.08 | 219.8547 | 505.8 | 360.7 | 369.6 | 372.8 | 537.5 | 67.5 | 18 | 119.1 | 7.7 | 234 | 8.6 | 322.9 | 341.5 | 649.1 | 715 | 446.1 | 494.2 | 748.9 | 759.1 | 722.4 | 658.6 | 673.7 | 586.5 | 708.8 | 619.5 | 623.9 | 584.9 | 619 | 397 | 404.9 | 394.2 | 371.6 | 397.5 | 396.1 | 409.1 | 367.2
1677 | 1456 | 470.6 | 188.24 | 220.0417 | 503.8 | 360.2 | 369.4 | 373.2 | 535.3 | 67.5 | 18 | 119.1 | 7.3 | 245.6 | 8.9 | 323.2 | 341.8 | 650 | 697.8 | 446.3 | 494.3 | 748.2 | 753.7 | 721.3 | 658.9 | 668.1 | 573.1 | 709.7 | 621.3 | 614 | 585.5 | 618.3 | 397.3 | 405 | 394.1 | 371.7 | 397.9 | 397.2 | 409.6 | 367.5
1678 | 1457 | 471.2 | 188.48 | 220.3223 | 503.8 | 359.7 | 368.5 | 373.3 | 537.7 | 67.6 | 18 | 119.1 | 6.8 | 242.3 | 9 | 323.5 | 342 | 654 | 676.1 | 446.4 | 494.4 | 732.6 | 747.7 | 719 | 658.9 | 664.6 | 559.3 | 710.4 | 627 | 603.9 | 586.3 | 617.2 | 397.6 | 405.2 | 393.9 | 371.7 | 398.4 | 398.3 | 410.2 | 367.8
1679 | 1458 | 472 | 188.8 | 220.6963 | 503.3 | 359.2 | 368.2 | 374.5 | 542.2 | 67.6 | 18 | 119.1 | 6.9 | 244.2 | 9.1 | 323.8 | 342.3 | 634.8 | 671.2 | 446.6 | 494.5 | 727.8 | 739.3 | 716.5 | 658.9 | 662.2 | 549.3 | 711.1 | 636 | 597.4 | 587.1 | 615.5 | 397.9 | 405.5 | 394 | 371.7 | 398.7 | 398.6 | 411.1 | 368
1680 | 1459 | 473 | 189.2 | 221.1639 | 502.7 | 358.4 | 370.1 | 375.9 | 543.5 | 67.7 | 18 | 119.1 | 7.1 | 238.1 | 10 | 324.2 | 342.5 | 627.6 | 658.8 | 446.8 | 494.6 | 728.9 | 726.7 | 713.9 | 658.8 | 662.8 | 540.7 | 711.6 | 628.5 | 591.7 | 587.9 | 614.3 | 398.3 | 405.6 | 394 | 371.9 | 399 | 398.4 | 411.5 | 368.2
1681 | 1460 | 473 | 189.2 | 221.1639 | 502.4 | 358 | 371.6 | 376.9 | 545.6 | 67.7 | 18 | 119.1 | 7.7 | 252.4 | 10.6 | 324.5 | 342.7 | 632.8 | 642.3 | 447 | 494.8 | 722.8 | 715.6 | 711.5 | 658.6 | 664.2 | 530.7 | 712.3 | 627.9 | 584.5 | 588.4 | 613 | 398.5 | 405.6 | 394 | 372.1 | 399.3 | 398.2 | 411.9 | 368.4
1682 | 1461 | 471.8 | 188.72 | 220.6028 | 502.2 | 358.1 | 372.4 | 377.6 | 543.3 | 67.8 | 18 | 119.1 | 7 | 242.6 | 11.9 | 324.8 | 343 | 629.7 | 623.1 | 447.1 | 495 | 715.1 | 689.6 | 707.2 | 658.3 | 656.3 | 522.2 | 712.6 | 624.6 | 577.4 | 588.9 | 611.4 | 398.7 | 405.6 | 394 | 372.3 | 399.7 | 398.9 | 412.5 | 368.7
1683 | 1462 | 472 | 188.8 | 220.6963 | 502.8 | 358.3 | 372.1 | 378.2 | 545.2 | 67.9 | 18 | 119 | 7.1 | 242.4 | 12.5 | 325.2 | 343.1 | 622.3 | 604.6 | 447.3 | 495.1 | 712 | 668 | 704.6 | 657.7 | 643.1 | 514.8 | 712.8 | 619.4 | 569 | 589.7 | 609.9 | 399 | 405.6 | 393.7 | 372.4 | 400.2 | 400.2 | 412.9 | 369.2
1684 | 1463 | 471.7 | 188.68 | 220.556 | 502.9 | 358.1 | 372 | 379.4 | 549 | 67.9 | 18 | 119.1 | 8.6 | 248.4 | 12 | 325.5 | 343.3 | 623 | 595.2 | 447.5 | 495.3 | 723.2 | 661.6 | 701.2 | 657 | 633.2 | 506.8 | 712.8 | 628.3 | 561.2 | 590.6 | 608.6 | 399.3 | 406 | 393.7 | 372.6 | 400.7 | 401.2 | 413.2 | 369.5
1685 | 1464 | 472.2 | 188.88 | 220.7898 | 500.5 | 358.1 | 373.6 | 380.3 | 548.9 | 67.9 | 18 | 119.2 | 9.1 | 240.4 | 11.9 | 325.8 | 343.5 | 618.7 | 586.4 | 447.6 | 495.4 | 719.5 | 659.7 | 699.6 | 656.5 | 633 | 496.8 | 712.8 | 634.4 | 558 | 591.4 | 607.3 | 399.7 | 406.7 | 394 | 372.8 | 401.1 | 401.8 | 413.3 | 369.7
1686 | 1465 | 472 | 188.8 | 220.6963 | 499.2 | 358.4 | 376.8 | 380.5 | 543.6 | 67.9 | 18 | 119.3 | 8 | 251.7 | 11.9 | 326.1 | 343.8 | 624.7 | 580.5 | 447.8 | 495.6 | 719.5 | 679.2 | 699.7 | 655.9 | 626.9 | 491.1 | 712.7 | 639.9 | 559.4 | 591.9 | 606.6 | 400.1 | 407 | 394.1 | 372.9 | 401.4 | 401.8 | 412.7 | 369.9
1687 | 1466 | 471.4 | 188.56 | 220.4158 | 496.4 | 358.7 | 377.2 | 379.5 | 541.6 | 67.9 | 18 | 119.4 | 8.3 | 247.8 | 12.6 | 326.4 | 344 | 627.4 | 571.4 | 448 | 495.8 | 726 | 686.2 | 697.2 | 655.2 | 631 | 484.8 | 712.6 | 647.8 | 563 | 592.6 | 605.5 | 400.5 | 407.2 | 394.1 | 373 | 401.8 | 402.4 | 412.4 | 370.2
1688 | 1467 | 470.6 | 188.24 | 220.0417 | 496.8 | 358.6 | 376.4 | 378.9 | 550.5 | 68 | 17.9 | 119.5 | 7.4 | 241.8 | 11.8 | 326.7 | 344.3 | 638.6 | 567.2 | 448.1 | 495.9 | 723.3 | 707.6 | 698 | 654.5 | 625 | 483.4 | 712.5 | 649.7 | 565 | 593.3 | 605.3 | 400.8 | 407.5 | 394 | 373.2 | 402.2 | 402.4 | 412.3 | 370.3
1689 | 1468 | 471.2 | 188.48 | 220.3223 | 497 | 358.4 | 377.5 | 378.5 | 552.6 | 68 | 17.9 | 119.4 | 6.2 | 252 | 11.6 | 327.1 | 344.5 | 639.1 | 576.8 | 448.2 | 496 | 729.3 | 737.7 | 699.4 | 654.1 | 626.6 | 487.1 | 712.1 | 652.6 | 573.6 | 594.2 | 605.7 | 401.2 | 407.5 | 393.6 | 373.3 | 402.6 | 402.1 | 411.8 | 370.4
1690 | 1469 | 472 | 188.8 | 220.6963 | 497 | 359.6 | 377.7 | 378.8 | 549.1 | 68 | 17.9 | 119.3 | 6.2 | 238.5 | 13.7 | 327.4 | 344.8 | 648.3 | 607.7 | 448.4 | 496 | 751 | 771 | 703.4 | 653.9 | 629.7 | 497.2 | 711.9 | 649.2 | 586.1 | 594.9 | 606.3 | 401.6 | 407.3 | 393.3 | 373.4 | 403 | 401.8 | 411.6 | 370.5
1691 | 1470 | 472.6 | 189.04 | 220.9769 | 494.1 | 360.1 | 378.2 | 378.8 | 547.2 | 68.1 | 17.9 | 119.3 | 6.5 | 234 | 13.2 | 327.7 | 345.1 | 669.7 | 643 | 448.6 | 496.2 | 761.1 | 782.7 | 707.6 | 653.9 | 632.9 | 522.8 | 711.8 | 648.9 | 603 | 595.6 | 608.3 | 401.8 | 406.9 | 393.1 | 373.7 | 403.2 | 401.2 | 411.2 | 370.7
1692 | 1471 | 471.5 | 188.6 | 220.4625 | 492 | 359.4 | 378.3 | 377.6 | 546.3 | 68 | 17.9 | 119.5 | 6.5 | 244.9 | 13.3 | 328 | 345.3 | 685.1 | 668.8 | 448.8 | 496.5 | 755.9 | 791.6 | 711.3 | 654.1 | 636.1 | 556.8 | 711.3 | 642.9 | 618 | 596 | 611.6 | 402 | 406.5 | 392.8 | 374 | 403.5 | 400.5 | 410.7 | 370.8
1693 | 1472 | 473.5 | 189.4 | 221.3977 | 489.8 | 359.3 | 377.8 | 376.8 | 542.9 | 68 | 17.9 | 119.8 | 6.4 | 245.4 | 12.8 | 328.4 | 345.4 | 700.3 | 687.6 | 449 | 496.7 | 756.6 | 801.8 | 714.5 | 654.6 | 636.8 | 582.8 | 710.8 | 638.3 | 629.8 | 596.6 | 614.2 | 402.2 | 406.2 | 392.6 | 374.4 | 403.7 | 400.2 | 410.5 | 371
1694 | 1473 | 473 | 189.2 | 221.1639 | 489.4 | 359 | 376.6 | 377.1 | 538.4 | 68 | 17.9 | 120 | 6.1 | 252.3 | 12 | 328.7 | 345.6 | 714.4 | 715.3 | 449.1 | 497 | 763.3 | 805.8 | 718 | 655.3 | 637.6 | 614.1 | 710.1 | 633.5 | 644.1 | 597.1 | 617.2 | 402.4 | 405.8 | 392.3 | 374.6 | 403.8 | 399.8 | 410.4 | 371.2
1695 | 1474 | 473.9 | 189.56 | 221.5847 | 491 | 359.1 | 376 | 377 | 538.1 | 67.9 | 17.9 | 120 | 6.7 | 245.4 | 11.4 | 329.1 | 345.7 | 728.2 | 730.2 | 449.3 | 497.3 | 769.9 | 795.4 | 718.4 | 656.1 | 637.4 | 639.4 | 709.7 | 630.1 | 656.3 | 597.6 | 620.2 | 402.5 | 405.4 | 392.2 | 374.8 | 404 | 399.1 | 409.7 | 371.3
1696 | 1475 | 473.4 | 189.36 | 221.3509 | 492.8 | 357.9 | 375 | 376.2 | 535.6 | 67.9 | 17.9 | 120 | 6.9 | 250.6 | 11.1 | 329.4 | 345.9 | 733.3 | 741.5 | 449.4 | 497.5 | 770.7 | 809.4 | 720.2 | 656.7 | 635.8 | 640.7 | 709.7 | 627.5 | 656.7 | 598.2 | 621.2 | 402.6 | 404.8 | 391.8 | 375 | 404 | 398.4 | 409.1 | 371.5
1697 | 1476 | 473 | 189.2 | 221.1639 | 490.2 | 357.3 | 374.4 | 375.3 | 532.1 | 67.9 | 17.9 | 120.1 | 6.8 | 254.7 | 11.3 | 329.7 | 346 | 728.6 | 733 | 449.6 | 497.7 | 780.8 | 820.4 | 721.5 | 657.3 | 631.6 | 631.6 | 710 | 627.5 | 659 | 598.9 | 621.7 | 402.7 | 404.2 | 391.2 | 374.9 | 404 | 397.9 | 408.5 | 371.6
1698 | 1477 | 473.8 | 189.52 | 221.538 | 490.1 | 356.6 | 373.6 | 374.5 | 535.5 | 67.9 | 17.9 | 120 | 7.2 | 256 | 11 | 330.1 | 346.2 | 714.9 | 736.6 | 449.8 | 497.9 | 775.6 | 828.7 | 720.9 | 658.1 | 629.1 | 620.8 | 710.6 | 629.2 | 655.1 | 599.6 | 621.4 | 402.7 | 403.7 | 390.5 | 374.9 | 404.2 | 397.8 | 408.2 | 371.8
1699 | 1478 | 473.7 | 189.48 | 221.4912 | 494.7 | 356.1 | 372.7 | 374.6 | 538.8 | 67.9 | 17.9 | 119.9 | 7.3 | 243.2 | 10.6 | 330.4 | 346.3 | 704.1 | 731.9 | 449.9 | 498.1 | 768.4 | 822.7 | 721 | 658.9 | 628.9 | 610.8 | 711.5 | 629.2 | 650 | 600.3 | 620.6 | 402.7 | 403.4 | 390 | 374.8 | 404.4 | 397.7 | 408.2 | 372
1700 | 1479 | 473 | 189.2 | 221.1639 | 497.8 | 356.5 | 372 | 375.5 | 540.4 | 67.9 | 17.9 | 119.9 | 7.1 | 243.4 | 9.8 | 330.8 | 346.4 | 692.5 | 717.4 | 450.1 | 498.2 | 761.9 | 806.6 | 719.7 | 659.6 | 631.9 | 597.2 | 712.2 | 631.4 | 644.7 | 601 | 620.1 | 402.8 | 403.2 | 389.8 | 374.8 | 404.7 | 398 | 408.4 | 372.2
1701 | 1480 | 473.2 | 189.28 | 221.2574 | 496.9 | 357 | 372.1 | 375.3 | 545.8 | 68 | 17.9 | 119.7 | 7.3 | 246 | 9.3 | 331 | 346.6 | 688.1 | 708.2 | 450.3 | 498.3 | 757.3 | 816.4 | 721.3 | 660.1 | 638.1 | 591.2 | 713.1 | 636.2 | 641.3 | 601.7 | 619.5 | 402.9 | 402.9 | 389.7 | 374.9 | 405 | 398.3 | 408.9 | 372.4
1702 | 1481 | 473.7 | 189.48 | 221.4912 | 497.1 | 357.2 | 372 | 375.4 | 546.8 | 68.1 | 17.9 | 119.6 | 7.4 | 247.2 | 9 | 331.3 | 346.8 | 691.6 | 705.1 | 450.5 | 498.4 | 760.8 | 828.4 | 723.9 | 660.7 | 640.4 | 590.2 | 713.5 | 636.5 | 637.7 | 602.5 | 620.1 | 403.1 | 402.8 | 389.8 | 375.1 | 405.3 | 398.7 | 409.7 | 372.6
1703 | 1482 | 473.1 | 189.24 | 221.2107 | 498.5 | 357.2 | 370.8 | 376.5 | 544.8 | 68.2 | 17.9 | 119.6 | 7.6 | 236.6 | 9.7 | 331.7 | 346.9 | 688.4 | 698 | 450.7 | 498.5 | 768.7 | 823.6 | 725.5 | 661.2 | 638.2 | 582.5 | 714.2 | 638.1 | 631.8 | 603.1 | 619.6 | 403.3 | 402.7 | 389.9 | 375.3 | 405.7 | 399.2 | 410.2 | 372.9
1704 | 1483 | 473 | 189.2 | 221.1639 | 501.1 | 357.2 | 369.8 | 377.7 | 545.7 | 68.4 | 17.9 | 119.6 | 7.9 | 241.9 | 10.8 | 332 | 347.1 | 686.3 | 688.2 | 450.9 | 498.6 | 753.6 | 819.2 | 724.8 | 661.5 | 630.2 | 572 | 715.1 | 639.3 | 627.7 | 603.8 | 618.8 | 403.4 | 402.8 | 389.9 | 375.5 | 406 | 399.7 | 410.8 | 373.2
1705 | 1484 | 473.3 | 189.32 | 221.3042 | 500.3 | 357.2 | 370 | 377.9 | 543.2 | 68.5 | 17.9 | 119.6 | 6.3 | 229.4 | 10.6 | 332.3 | 347.3 | 679.8 | 675.6 | 451 | 498.6 | 752.8 | 804.8 | 723.7 | 661.7 | 627.1 | 562.5 | 715.4 | 637.3 | 626.5 | 604.4 | 618.4 | 403.5 | 403 | 390 | 375.6 | 406.4 | 400.1 | 411 | 373.3
1706 | 1485 | 474 | 189.6 | 221.6315 | 498.8 | 356 | 370.4 | 377.5 | 540.9 | 68.6 | 17.9 | 119.7 | 6.5 | 241.9 | 8.7 | 332.7 | 347.5 | 672 | 671.5 | 451.2 | 498.7 | 755.8 | 795.4 | 723.1 | 661.8 | 632.4 | 551.9 | 715.6 | 633.3 | 622.4 | 605.1 | 617.7 | 403.8 | 403.3 | 390.1 | 375.7 | 406.6 | 400.1 | 411 | 373.5
1707 | 1486 | 472.5 | 189 | 220.9301 | 498.3 | 355.7 | 371.1 | 376.4 | 537 | 68.6 | 17.9 | 119.7 | 6.4 | 252.1 | 8.5 | 333 | 347.7 | 670.9 | 664.5 | 451.4 | 498.7 | 757.4 | 799 | 723.3 | 661.8 | 636.2 | 546.4 | 716.5 | 633.4 | 617.2 | 605.6 | 617 | 404.1 | 403.6 | 390.2 | 375.8 | 406.9 | 399.9 | 410.8 | 373.6
1708 | 1487 | 471.9 | 188.76 | 220.6496 | 498.7 | 357 | 371.3 | 376.4 | 537.5 | 68.7 | 17.9 | 119.5 | 6.3 | 246.9 | 10.4 | 333.3 | 347.9 | 673.9 | 652.8 | 451.6 | 498.7 | 753.3 | 786 | 723.2 | 661.7 | 632.1 | 534.6 | 717.1 | 637.3 | 609.7 | 606.4 | 616.1 | 404.4 | 403.7 | 390.2 | 375.9 | 407.2 | 400 | 410.6 | 373.9
1709 | 1488 | 472.2 | 188.88 | 220.7898 | 499.2 | 358.3 | 371.5 | 377 | 542.5 | 68.7 | 17.9 | 119.4 | 6.3 | 248 | 11.9 | 333.6 | 348.1 | 677.5 | 641.1 | 451.8 | 498.9 | 740.9 | 764.5 | 720.3 | 661.4 | 625.5 | 527 | 717.4 | 639.5 | 602 | 607 | 614.6 | 404.7 | 403.7 | 390 | 375.9 | 407.6 | 400.3 | 410.9 | 374.1
1710 | 1489 | 472.6 | 189.04 | 220.9769 | 503.3 | 358.8 | 371.8 | 378.7 | 544.7 | 68.6 | 17.9 | 119.3 | 7.3 | 246.3 | 11.2 | 334 | 348.3 | 685.9 | 630.6 | 452 | 499 | 724.9 | 769.6 | 719.1 | 660.9 | 621.1 | 521 | 717.6 | 634.6 | 595.7 | 607.6 | 613.5 | 405 | 403.9 | 390 | 376 | 407.9 | 400.4 | 410.9 | 374.2
1711 | 1490 | 471.5 | 188.6 | 220.4625 | 505.6 | 358 | 372.3 | 379.8 | 544.2 | 68.4 | 17.9 | 119.1 | 6.5 | 245.1 | 10.3 | 334.3 | 348.5 | 702.1 | 625.6 | 452.3 | 499.1 | 725.5 | 778.5 | 718 | 660.4 | 618.5 | 516 | 717.3 | 635.2 | 613.1 | 608.2 | 614.1 | 405.4 | 404 | 389.8 | 376.1 | 408.4 | 401.7 | 411.5 | 374.5
1712 | 1491 | 472 | 188.8 | 220.6963 | 506.3 | 357.5 | 373.6 | 380.6 | 547 | 68.4 | 17.9 | 119.1 | 5.9 | 241.9 | 10.6 | 334.6 | 348.7 | 718.8 | 617.3 | 452.5 | 499.4 | 728.8 | 789.8 | 716.9 | 659.8 | 615.9 | 512.5 | 716.7 | 637.2 | 614.5 | 608.8 | 615.4 | 405.7 | 404.1 | 389.9 | 376.2 | 409 | 403 | 412.4 | 374.8
1713 | 1492 | 472.1 | 188.84 | 220.7431 | 501.9 | 357.2 | 374.5 | 381.5 | 549.1 | 68.3 | 17.9 | 119.1 | 5.2 | 241.6 | 11.1 | 334.9 | 349 | 727.8 | 623.8 | 452.7 | 499.5 | 745.9 | 789.3 | 717.4 | 659.6 | 616.5 | 519.3 | 716.9 | 634.2 | 612.1 | 609.5 | 615.1 | 406 | 404.1 | 389.6 | 376.3 | 409.3 | 403.4 | 412.9 | 375
1714 | 1493 | 471.9 | 188.76 | 220.6496 | 497.6 | 357.4 | 375 | 382.4 | 545.6 | 68.3 | 17.9 | 119.1 | 5.3 | 242.8 | 11 | 335.3 | 349.2 | 722.1 | 630.3 | 452.9 | 499.7 | 746.7 | 782.4 | 717.9 | 659.4 | 620.2 | 515.6 | 717.6 | 629.1 | 608.4 | 610 | 613.9 | 406.3 | 403.9 | 389.4 | 376.4 | 409.5 | 402.9 | 412.5 | 375.1
1715 | 1494 | 471.9 | 188.76 | 220.6496 | 494.6 | 358.3 | 374.7 | 381.9 | 541.7 | 68.2 | 17.9 | 119.1 | 5.6 | 245.1 | 10.4 | 335.6 | 349.4 | 715.8 | 641.9 | 453.4 | 499.8 | 754.7 | 773.9 | 717.7 | 659.4 | 624.7 | 526.4 | 718.3 | 623.6 | 613.2 | 610.7 | 614.3 | 406.5 | 403.7 | 389.4 | 376.6 | 409.7 | 402.5 | 412 | 375.2
1716 | 1495 | 472.1 | 188.84 | 220.7431 | 493.5 | 358.1 | 374.3 | 381.6 | 538.9 | 68.2 | 17.9 | 119.2 | 6 | 244.6 | 10.1 | 335.9 | 349.6 | 703.7 | 655.9 | 453.8 | 500 | 762.2 | 785.9 | 718.4 | 659.7 | 623.1 | 531.1 | 718.1 | 622.2 | 613 | 611.2 | 614 | 406.7 | 403.4 | 389.1 | 376.7 | 409.9 | 402.1 | 412 | 375.3
1717 | 1496 | 472.2 | 188.88 | 220.7898 | 493.7 | 357.8 | 373.7 | 380.2 | 536 | 68.2 | 17.9 | 119.5 | 7.3 | 242.5 | 10.3 | 336.3 | 349.8 | 693 | 648.3 | 454 | 500 | 765.2 | 804.4 | 719.7 | 659.9 | 626 | 533.3 | 718.1 | 625.7 | 621.7 | 611.9 | 614.4 | 406.8 | 403.1 | 388.8 | 376.7 | 410.2 | 402.3 | 412.4 | 375.6
1718 | 1497 | 472.3 | 188.92 | 220.8366 | 493.4 | 358.2 | 373.3 | 379.5 | 538.3 | 68.3 | 17.9 | 119.6 | 7.2 | 244.1 | 10.4 | 336.6 | 350 | 694.4 | 653.7 | 454.5 | 500.2 | 763 | 788.7 | 717.5 | 660.2 | 625.6 | 539.9 | 718.1 | 627.5 | 624.5 | 612.6 | 615.1 | 406.9 | 403.1 | 388.6 | 376.9 | 410.6 | 402.5 | 412.2 | 375.8
1719 | 1498 | 472.1 | 188.84 | 220.7431 | 493.8 | 358.3 | 373.2 | 379.1 | 540 | 68.3 | 17.9 | 119.7 | 7.3 | 251.5 | 10.1 | 336.9 | 350.2 | 694.6 | 668.2 | 454.8 | 500.4 | 761 | 786.2 | 715.4 | 660.6 | 627.6 | 542.5 | 718.4 | 627.2 | 627.2 | 613.4 | 615.2 | 407 | 403.1 | 388.6 | 377 | 410.8 | 402.2 | 412.2 | 375.9
1720 | 1499 | 471.6 | 188.64 | 220.5093 | 492.9 | 358.1 | 372.8 | 378.9 | 538.6 | 68.3 | 17.9 | 119.7 | 6.8 | 248.8 | 9.9 | 337.3 | 350.4 | 688.1 | 678.8 | 455.1 | 500.6 | 763 | 784.7 | 714.8 | 661.2 | 630.5 | 547.2 | 718.6 | 626.4 | 626.2 | 614 | 615.3 | 407.2 | 403 | 388.8 | 377.1 | 410.9 | 401.7 | 411.9 | 376
1721 | 1500 | 471.9 | 188.76 | 220.6496 | 493.9 | 358 | 371.8 | 378.2 | 536.6 | 68.2 | 17.9 | 119.9 | 6.5 | 237.7 | 9.5 | 337.6 | 350.6 | 681 | 692.3 | 455.3 | 500.9 | 746.1 | 784.7 | 714.3 | 661.5 | 627.3 | 541.5 | 719.4 | 621 | 614.7 | 614.5 | 613.7 | 407.3 | 402.9 | 388.9 | 377.4 | 411 | 401.1 | 411.6 | 376.2
1722 | 1501 | 472.2 | 188.88 | 220.7898 | 492.7 | 357.9 | 371.2 | 377.9 | 532.5 | 68.1 | 17.8 | 119.9 | 6.5 | 246.7 | 8.9 | 337.9 | 350.8 | 672.2 | 698.7 | 455.6 | 501 | 735.1 | 786.1 | 714 | 661.9 | 625.5 | 542.6 | 720.1 | 620.6 | 610.1 | 615.1 | 613.3 | 407.5 | 402.7 | 388.9 | 377.5 | 411.2 | 400.9 | 411.6 | 376.3
1723 | 1502 | 472.1 | 188.84 | 220.7431 | 491.7 | 357.7 | 370.3 | 377.7 | 531.4 | 68.2 | 17.8 | 119.8 | 6.6 | 246.5 | 9.5 | 338.2 | 351 | 663 | 705.1 | 456.1 | 501.2 | 731.6 | 792.9 | 713.6 | 662.4 | 632.5 | 543.5 | 720.2 | 623.8 | 612.7 | 615.6 | 613.1 | 407.6 | 402.3 | 388.8 | 377.5 | 411.4 | 401.1 | 411.8 | 376.5
1724 | 1503 | 472.4 | 188.96 | 220.8834 | 491.7 | 357.4 | 368.9 | 377.7 | 533.1 | 68.4 | 17.8 | 119.8 | 6.1 | 247.5 | 10.5 | 338.6 | 351.3 | 659.6 | 706.6 | 456.4 | 501.5 | 726.9 | 778.1 | 712.5 | 663.1 | 639.1 | 547.5 | 719.7 | 621.6 | 611.8 | 616.3 | 613.6 | 407.6 | 402 | 388.8 | 377.6 | 411.6 | 400.9 | 411.8 | 376.6
1725 | 1504 | 472.3 | 188.92 | 220.8366 | 492.6 | 357 | 368.6 | 377.3 | 528 | 68.4 | 17.8 | 119.7 | 6.3 | 248.3 | 10.8 | 339 | 351.7 | 652.9 | 695.3 | 456.7 | 501.7 | 740.4 | 783.1 | 713.9 | 663.5 | 630.7 | 539.4 | 720 | 617.4 | 608.4 | 616.8 | 613.1 | 407.7 | 401.7 | 388.9 | 377.7 | 411.7 | 400.4 | 411.5 | 376.8
1726 | 1505 | 471.9 | 188.76 | 220.6496 | 492.5 | 356.7 | 368.5 | 377 | 529.6 | 68.4 | 17.8 | 119.8 | 6.3 | 228.2 | 10.7 | 339.4 | 352 | 644.8 | 684.8 | 457.1 | 501.8 | 742 | 800.9 | 715.1 | 663.7 | 629.9 | 533.6 | 720.5 | 621.7 | 607.8 | 617.3 | 613 | 407.8 | 401.8 | 389 | 377.8 | 411.9 | 400.8 | 411.4 | 377
1727 | 1506 | 470.6 | 188.24 | 220.0417 | 493.8 | 356.7 | 367.6 | 376.9 | 532.3 | 68.3 | 17.8 | 119.9 | 5.9 | 243.6 | 10.2 | 339.8 | 352.4 | 652.4 | 686.5 | 457.3 | 502 | 743.2 | 818.2 | 717.4 | 664.2 | 630.1 | 546 | 720.5 | 624.8 | 618.4 | 617.9 | 614.2 | 407.9 | 401.9 | 389.1 | 378 | 412.1 | 401.2 | 411.4 | 377.1
1728 | 1507 | 471 | 188.4 | 220.2287 | 495.1 | 356.9 | 368.6 | 377.6 | 531.8 | 68.2 | 17.8 | 120.2 | 6.7 | 244 | 10.9 | 340.2 | 352.8 | 653.8 | 691.6 | 457.6 | 502.3 | 745.8 | 811.1 | 716.6 | 664.8 | 633.4 | 555.6 | 720.3 | 624.5 | 628.3 | 618.6 | 615.1 | 408.2 | 402 | 389 | 378 | 412.4 | 401.1 | 411.2 | 377.2
1729 | 1508 | 472.7 | 189.08 | 221.0236 | 497.1 | 356.9 | 369.2 | 378.5 | 531 | 68.2 | 17.8 | 120.5 | 7.2 | 246.3 | 10.5 | 340.5 | 353.1 | 651.5 | 706 | 457.9 | 502.5 | 736.4 | 804.8 | 717.5 | 665.2 | 638.1 | 552.4 | 720.3 | 621.9 | 628.1 | 619.2 | 614.7 | 408.3 | 401.8 | 388.7 | 378.1 | 412.5 | 400.7 | 411.3 | 377.3
1730 | 1509 | 473.3 | 189.32 | 221.3042 | 496.5 | 356.9 | 368.7 | 378.5 | 529.6 | 68.2 | 17.8 | 120.6 | 6.5 | 248 | 10.1 | 340.9 | 353.5 | 657.2 | 692.3 | 458.1 | 502.7 | 739.9 | 806.9 | 718 | 665.8 | 637.5 | 548.9 | 720.7 | 623.3 | 628.2 | 619.8 | 615.1 | 408.4 | 401.6 | 388.6 | 378 | 412.8 | 400.9 | 411.3 | 377.5
1731 | 1510 | 473.3 | 189.32 | 221.3042 | 496.9 | 356.6 | 367.9 | 378.5 | 533.9 | 68.3 | 17.8 | 120.7 | 5.9 | 243.7 | 11 | 341.3 | 353.8 | 663.8 | 665.1 | 458.4 | 503 | 728.2 | 786.6 | 713.8 | 665.8 | 630.7 | 538.5 | 721.1 | 623.7 | 621.7 | 620.4 | 614.3 | 408.5 | 401.3 | 388.5 | 377.9 | 413.3 | 401.8 | 412 | 377.8
1732 | 1511 | 473 | 189.2 | 221.1639 | 498.7 | 356.5 | 367.3 | 379.4 | 545.9 | 68.4 | 17.8 | 120.6 | 5.3 | 250.1 | 11.1 | 341.6 | 354.2 | 663.2 | 647.7 | 458.7 | 503.2 | 718 | 770.1 | 711.6 | 665.7 | 635 | 532.8 | 721.3 | 625.3 | 618.4 | 621.1 | 613.7 | 408.6 | 401.3 | 388.4 | 377.9 | 413.8 | 402.7 | 413 | 378
1733 | 1512 | 473.5 | 189.4 | 221.3977 | 501.1 | 356.6 | 368.5 | 380.7 | 549.6 | 68.6 | 17.8 | 120.5 | 5.7 | 250 | 11.2 | 342 | 354.4 | 657.1 | 639.9 | 459 | 503.4 | 718.8 | 781.9 | 712 | 665.8 | 638.3 | 531.5 | 721.7 | 634.9 | 613 | 621.7 | 613.2 | 408.9 | 401.7 | 388.6 | 378.1 | 414.2 | 403.7 | 413.6 | 378.3
1734 | 1513 | 473.4 | 189.36 | 221.3509 | 500.1 | 357.4 | 370 | 381.6 | 556.4 | 68.7 | 17.8 | 120.3 | 5.6 | 254.2 | 10.7 | 342.3 | 354.8 | 672.3 | 619.3 | 459.4 | 503.6 | 742.3 | 777.2 | 709.5 | 665.6 | 634.3 | 525 | 722.2 | 644.7 | 617.4 | 622.4 | 613.3 | 409.2 | 401.9 | 389.1 | 378.3 | 414.7 | 405 | 414.9 | 378.6
1735 | 1514 | 473.3 | 189.32 | 221.3042 | 496.5 | 358.1 | 370.4 | 384.8 | 558.4 | 68.6 | 17.8 | 120.1 | 5.9 | 262.7 | 9.5 | 342.6 | 355.2 | 681.8 | 608.8 | 459.6 | 503.9 | 750.5 | 787.2 | 709.7 | 665.8 | 632.6 | 522 | 722.3 | 648.1 | 617.3 | 623 | 613 | 409.5 | 402.2 | 389.5 | 378.5 | 415.2 | 405.3 | 415.2 | 378.8
1736 | 1515 | 473.5 | 189.4 | 221.3977 | 492.7 | 358.5 | 371.3 | 387.2 | 561.8 | 68.6 | 17.8 | 119.9 | 6.1 | 262.6 | 8 | 342.9 | 355.6 | 673.5 | 601.8 | 459.9 | 504.1 | 746.9 | 790.8 | 709 | 666 | 634.5 | 526.2 | 722.1 | 654.6 | 625.5 | 623.6 | 613.2 | 409.8 | 402.1 | 389.6 | 378.7 | 415.7 | 405.8 | 415.7 | 379
1737 | 1516 | 473 | 189.2 | 221.1639 | 490.1 | 357.8 | 372.3 | 388.6 | 565.1 | 68.6 | 17.8 | 119.7 | 5.8 | 251.5 | 7.7 | 343.3 | 355.9 | 664.5 | 591.1 | 460.2 | 504.3 | 729.5 | 785.6 | 707.5 | 666.1 | 637.7 | 520.2 | 721.7 | 656.8 | 630.5 | 624.2 | 613.2 | 410.1 | 402 | 389.5 | 379 | 416.2 | 406.3 | 416.5 | 379.2
1738 | 1517 | 472.8 | 189.12 | 221.0704 | 489.7 | 357.8 | 372.9 | 389.8 | 569.4 | 68.6 | 17.8 | 119.6 | 5.7 | 258.9 | 7.8 | 343.7 | 356.3 | 675.6 | 581.6 | 460.5 | 504.6 | 728.5 | 797.5 | 708.7 | 666.1 | 639.4 | 516.2 | 721.7 | 654.6 | 628.6 | 624.8 | 613.5 | 410.3 | 401.9 | 389.4 | 379.1 | 416.6 | 406.6 | 417.1 | 379.5
1739 | 1518 | 472.6 | 189.04 | 220.9769 | 490.2 | 358.7 | 372.9 | 389.5 | 563 | 68.7 | 17.8 | 119.6 | 5.3 | 249.1 | 7.8 | 344 | 356.7 | 690.1 | 584.5 | 460.8 | 505 | 728.6 | 810 | 708.9 | 665.8 | 639.1 | 512.9 | 721.5 | 658.2 | 630.4 | 625.5 | 613.9 | 410.4 | 401.6 | 389.1 | 379 | 417.1 | 407 | 417.3 | 379.7
1740 | 1519 | 473 | 189.2 | 221.1639 | 489.6 | 359.9 | 372.7 | 389 | 563.1 | 68.7 | 17.8 | 119.5 | 5.2 | 259 | 7.6 | 344.3 | 357 | 703.2 | 604.4 | 461.1 | 505.3 | 723.7 | 825.8 | 711.1 | 665.8 | 642.9 | 523.4 | 721.8 | 659.6 | 636.7 | 626.2 | 614.6 | 410.6 | 401.5 | 389.1 | 379 | 417.5 | 407.3 | 417.7 | 380
1741 | 1520 | 473 | 189.2 | 221.1639 | 486.7 | 360.4 | 373.8 | 388.8 | 561.2 | 68.7 | 17.8 | 119.5 | 5.5 | 262.4 | 7.6 | 344.6 | 357.4 | 713.2 | 635 | 461.4 | 505.6 | 732.3 | 839 | 714.5 | 665.8 | 645.7 | 539.2 | 722 | 658.7 | 638.8 | 626.8 | 615.7 | 410.7 | 401.3 | 388.9 | 379.1 | 417.8 | 407.2 | 418 | 380.1
1742 | 1521 | 472.9 | 189.16 | 221.1171 | 488.2 | 360.5 | 373.9 | 388.6 | 562 | 68.7 | 17.8 | 119.4 | 5.7 | 249.5 | 7.3 | 344.9 | 357.7 | 709.8 | 653.5 | 461.7 | 505.8 | 744.1 | 840.6 | 716.2 | 666.1 | 648.3 | 547.6 | 722.5 | 661.7 | 643.9 | 627.4 | 616.4 | 410.9 | 401.3 | 389 | 379.2 | 418.1 | 407 | 417.7 | 380.3
1743 | 1522 | 473.1 | 189.24 | 221.2107 | 490.1 | 361.5 | 373.6 | 387.6 | 565 | 68.6 | 17.8 | 119.3 | 6.1 | 254.9 | 7.1 | 345.1 | 357.9 | 706.4 | 651 | 461.9 | 506.1 | 747.7 | 837.5 | 717.1 | 666.4 | 649.4 | 542.5 | 723.1 | 660.9 | 643.5 | 628 | 616.8 | 411 | 401.4 | 388.9 | 379.3 | 418.4 | 407.1 | 417.5 | 380.5
1744 | 1523 | 472.6 | 189.04 | 220.9769 | 488.1 | 362.5 | 373.2 | 387 | 563.3 | 68.5 | 17.8 | 119.3 | 5.4 | 257 | 7.1 | 345.4 | 358.2 | 710.6 | 652.7 | 462.2 | 506.4 | 746.1 | 838.3 | 717 | 666.8 | 646.8 | 539.5 | 724.1 | 667.2 | 637.4 | 628.7 | 616.2 | 411.2 | 401.3 | 388.7 | 379.4 | 418.7 | 407.1 | 417.3 | 380.7
1745 | 1524 | 473.4 | 189.36 | 221.3509 | 486.9 | 362.8 | 373.1 | 386.6 | 562.4 | 68.4 | 17.8 | 119.2 | 5.3 | 253.9 | 6.5 | 345.7 | 358.5 | 713.2 | 649.1 | 462.5 | 506.7 | 752.8 | 842.1 | 717.6 | 667.3 | 643.4 | 541 | 724.8 | 669 | 635.3 | 629.5 | 616.3 | 411.4 | 401.3 | 388.4 | 379.5 | 418.9 | 407 | 417.1 | 380.8
1746 | 1525 | 473 | 189.2 | 221.1639 | 486.4 | 363.6 | 372.8 | 385.8 | 565 | 68.4 | 17.8 | 119.2 | 5.4 | 259.6 | 6.2 | 346 | 358.7 | 709 | 633.5 | 462.8 | 507 | 749.5 | 831.1 | 714.7 | 667.4 | 637.2 | 535.5 | 725.2 | 666.2 | 627.4 | 630.2 | 615.5 | 411.6 | 401.2 | 388.2 | 379.4 | 419.4 | 407.7 | 417.5 | 381.1
1747 | 1526 | 473 | 189.2 | 221.1639 | 485.7 | 363.7 | 372.5 | 386.6 | 574.1 | 68.4 | 17.8 | 119.2 | 5.5 | 277.8 | 6.6 | 346.3 | 359 | 714.6 | 624.4 | 463 | 507.3 | 751.6 | 827.4 | 714.3 | 667.1 | 634.8 | 526.2 | 725.8 | 664.9 | 617.9 | 630.9 | 614.7 | 411.8 | 401.2 | 388.2 | 379.3 | 419.8 | 408.8 | 418.2 | 381.4
1748 | 1527 | 473 | 189.2 | 221.1639 | 485.5 | 363.3 | 373.5 | 388.2 | 576.1 | 68.4 | 17.8 | 119.4 | 6.6 | 282.7 | 6.8 | 346.6 | 359.3 | 721.8 | 609.3 | 463.3 | 507.5 | 751.2 | 817.8 | 712.5 | 666.9 | 628.3 | 516.1 | 726 | 666.3 | 614.6 | 631.6 | 614.1 | 412.1 | 401.5 | 388.3 | 379.3 | 420.3 | 409.5 | 419.1 | 381.6
1749 | 1528 | 473.4 | 189.36 | 221.3509 | 487.4 | 362.8 | 375.2 | 389 | 579.8 | 68.5 | 17.8 | 119.5 | 7 | 267.2 | 6.7 | 346.9 | 359.5 | 720.7 | 601.2 | 463.7 | 507.8 | 760 | 791.7 | 709.7 | 666.5 | 619.3 | 510.3 | 726.1 | 669.8 | 612.8 | 632.4 | 613.6 | 412.5 | 401.7 | 388.3 | 379.4 | 420.8 | 409.9 | 419.9 | 381.8
1750 | 1529 | 473.4 | 189.36 | 221.3509 | 490.4 | 363.5 | 377 | 390.1 | 576.7 | 68.5 | 17.8 | 119.5 | 6 | 260.7 | 6.7 | 347.2 | 359.8 | 719.8 | 586.7 | 464 | 508.1 | 754.8 | 756.2 | 706.1 | 666.1 | 615.2 | 506.4 | 726.4 | 670.2 | 606.4 | 633.1 | 612 | 412.8 | 401.8 | 388 | 379.6 | 421.3 | 410.3 | 420.6 | 382.1
1751 | 1530 | 473.2 | 189.28 | 221.2574 | 494.5 | 364.7 | 378.1 | 390.7 | 572.3 | 68.6 | 17.8 | 119.5 | 5.9 | 260.9 | 6.4 | 347.5 | 360.2 | 718.7 | 571.5 | 464.3 | 508.5 | 742.4 | 728 | 702 | 665.5 | 608.7 | 502.8 | 727 | 676.9 | 596.6 | 633.9 | 610.5 | 413 | 401.8 | 387.8 | 379.6 | 421.9 | 410.9 | 421.2 | 382.3
1752 | 1531 | 473 | 189.2 | 221.1639 | 495 | 365.1 | 378.6 | 390.5 | 565.7 | 68.6 | 17.8 | 119.5 | 6.2 | 257.2 | 6.6 | 347.8 | 360.4 | 713.6 | 568.3 | 464.6 | 508.7 | 736 | 727.3 | 700.4 | 664.8 | 606.8 | 499.4 | 727.4 | 675.5 | 590.5 | 634.6 | 609.2 | 413.3 | 402 | 387.8 | 379.7 | 422.3 | 411.1 | 421.9 | 382.6
1753 | 1532 | 473 | 189.2 | 221.1639 | 493.3 | 365.1 | 379.6 | 390.7 | 557.5 | 68.6 | 17.8 | 119.5 | 6.4 | 254.5 | 7 | 348.1 | 360.6 | 717 | 568.2 | 464.9 | 509 | 734 | 729.6 | 699.8 | 664.5 | 606.2 | 493.3 | 727.1 | 665.9 | 586.3 | 635.3 | 608.1 | 413.6 | 402.2 | 388 | 379.8 | 422.5 | 411 | 422.1 | 382.8
1754 | 1533 | 473.1 | 189.24 | 221.2107 | 492.5 | 365.3 | 379.9 | 390.5 | 549.6 | 68.6 | 17.8 | 119.6 | 6.1 | 252.6 | 7 | 348.4 | 360.9 | 714.7 | 567 | 465.1 | 509.3 | 728.8 | 731.4 | 699.6 | 664 | 609.4 | 487.4 | 727.5 | 661.2 | 585 | 635.9 | 607.2 | 413.8 | 402.3 | 388.1 | 379.9 | 422.7 | 410.6 | 421.5 | 383
1755 | 1534 | 473.4 | 189.36 | 221.3509 | 492.2 | 366 | 379.9 | 389.8 | 546.2 | 68.8 | 17.7 | 119.7 | 5.7 | 253.8 | 7 | 348.7 | 361.2 | 708.2 | 577.6 | 465.4 | 509.5 | 733.3 | 739.2 | 699.4 | 663.6 | 612.7 | 484.1 | 727.7 | 657.3 | 580.3 | 636.6 | 606.3 | 414.1 | 402.4 | 388.2 | 380 | 423 | 410.6 | 421 | 383.1
1756 | 1535 | 472.5 | 189 | 220.9301 | 493.4 | 365.9 | 380.1 | 390.1 | 542.2 | 68.9 | 17.8 | 119.8 | 6.7 | 252.8 | 6.6 | 349 | 361.5 | 708.2 | 597.6 | 465.7 | 509.8 | 728 | 746.4 | 699.5 | 663.3 | 608.4 | 485.3 | 727.7 | 653.7 | 585.5 | 637.1 | 606 | 414.2 | 402.5 | 388.2 | 380.1 | 423.3 | 410.6 | 421.4 | 383.3
1757 | 1536 | 471.5 | 188.6 | 220.4625 | 495.5 | 365.6 | 380.4 | 390.8 | 537.6 | 69 | 17.7 | 119.8 | 6.4 | 257.5 | 6.2 | 349.3 | 361.7 | 706.5 | 621.5 | 465.9 | 510.1 | 721.8 | 775.1 | 702.8 | 663.1 | 615.4 | 488.8 | 727.8 | 650.4 | 594 | 637.7 | 606 | 414.4 | 402.6 | 388.1 | 380.2 | 423.4 | 410 | 420.7 | 383.4
1758 | 1537 | 471.2 | 188.48 | 220.3223 | 494.6 | 365.2 | 380.7 | 390 | 536.8 | 69.1 | 17.7 | 119.7 | 5.8 | 270.4 | 6.9 | 349.6 | 362.1 | 721.8 | 637.3 | 466.2 | 510.4 | 731.8 | 781.6 | 705.9 | 663.2 | 621 | 505.4 | 727.4 | 648.5 | 603.2 | 638.3 | 607.2 | 414.6 | 402.6 | 388 | 380.2 | 423.5 | 409.2 | 420.3 | 383.5
1759 | 1538 | 472.6 | 189.04 | 220.9769 | 492.1 | 364.8 | 381.1 | 389 | 538.9 | 69.1 | 17.7 | 119.9 | 5.6 | 261.6 | 9.6 | 349.8 | 362.4 | 734.1 | 641.4 | 466.5 | 510.7 | 745.1 | 792.2 | 707.8 | 663.3 | 620.1 | 515.8 | 726.8 | 647.7 | 616.7 | 638.9 | 609.2 | 414.7 | 402.3 | 388 | 380.2 | 423.6 | 408.2 | 419.7 | 383.6
1760 | 1539 | 473.5 | 189.4 | 221.3977 | 493.8 | 364.4 | 381 | 388.2 | 539.1 | 69.2 | 17.7 | 120.1 | 5.9 | 256 | 11.6 | 350.1 | 362.7 | 742.9 | 665.3 | 466.7 | 511 | 759.5 | 816.5 | 711.5 | 663.6 | 619.5 | 543.6 | 726.4 | 648.1 | 626.5 | 639.4 | 611.2 | 414.8 | 402.2 | 387.9 | 380.2 | 423.6 | 407.6 | 419 | 383.7
1761 | 1540 | 471.8 | 188.72 | 220.6028 | 496.9 | 364 | 379.5 | 386.9 | 542.9 | 69.3 | 17.7 | 120.3 | 5.3 | 256.5 | 11.3 | 350.5 | 363 | 737.6 | 676.4 | 467 | 511.3 | 768.5 | 831.5 | 715.1 | 664 | 624.9 | 565.6 | 725.7 | 649.3 | 638.8 | 640 | 613.4 | 414.9 | 402 | 387.9 | 380.4 | 423.6 | 407.1 | 418.4 | 383.8
1762 | 1541 | 471.9 | 188.76 | 220.6496 | 499.6 | 364.4 | 378.7 | 385.9 | 552.1 | 69.4 | 17.7 | 120.2 | 5.6 | 254.5 | 10.5 | 350.7 | 363.3 | 735.9 | 687.6 | 467.2 | 511.7 | 781 | 843.4 | 716.8 | 664.3 | 637.2 | 572.1 | 725.3 | 659.3 | 644.5 | 640.6 | 614.2 | 415.1 | 402.1 | 387.9 | 380.7 | 423.6 | 406.9 | 418.1 | 383.9
1763 | 1542 | 471.7 | 188.68 | 220.556 | 500.3 | 364.5 | 378.6 | 386 | 559.4 | 69.5 | 17.7 | 120.1 | 5.4 | 258.3 | 10.4 | 351 | 363.6 | 733.8 | 688.9 | 467.5 | 512 | 784.9 | 851.1 | 718.8 | 665 | 643.9 | 577.8 | 725.6 | 669.2 | 644.4 | 641.2 | 614.7 | 415.2 | 402.2 | 387.9 | 380.7 | 423.7 | 406.9 | 418.2 | 384
1764 | 1543 | 471.1 | 188.44 | 220.2755 | 498.7 | 363.5 | 377.7 | 386.5 | 564.9 | 69.6 | 17.7 | 120 | 5.2 | 265.1 | 10 | 351.3 | 364 | 733.4 | 699.3 | 467.8 | 512.4 | 796.1 | 855.9 | 721.8 | 665.7 | 644.9 | 583 | 725.7 | 670.5 | 650.8 | 641.8 | 616.4 | 415.4 | 402.1 | 388 | 380.7 | 423.8 | 406.6 | 418.1 | 384.2
1765 | 1544 | 474 | 189.6 | 221.6315 | 498.2 | 362.7 | 376.3 | 386.3 | 566.8 | 69.7 | 17.7 | 119.8 | 6.1 | 251 | 9.8 | 351.6 | 364.2 | 729.5 | 693 | 468 | 512.7 | 797.8 | 861.4 | 723.2 | 666.2 | 652.5 | 582.8 | 725.8 | 672.8 | 653.3 | 642.4 | 617.2 | 415.5 | 401.9 | 388.2 | 380.8 | 423.8 | 406.5 | 417.7 | 384.3
1766 | 1545 | 475.4 | 190.16 | 222.2861 | 497.7 | 362.1 | 375.7 | 386.3 | 567.2 | 69.8 | 17.7 | 119.7 | 5.6 | 254.7 | 8.4 | 351.9 | 364.5 | 729 | 677.2 | 468.3 | 513.1 | 784.3 | 856.9 | 723 | 666.7 | 654.7 | 572.9 | 726.5 | 674.2 | 644.3 | 643.1 | 616.6 | 415.7 | 401.8 | 388.2 | 380.8 | 423.9 | 407 | 417.7 | 384.5
1767 | 1546 | 474.5 | 189.8 | 221.8653 | 496.2 | 362 | 375.2 | 386.7 | 563.8 | 69.9 | 17.7 | 119.6 | 6.2 | 267.9 | 7.8 | 352.2 | 364.8 | 738.3 | 658.4 | 468.5 | 513.4 | 776.3 | 840.3 | 722.5 | 667 | 651.2 | 565.8 | 727.1 | 670.2 | 640 | 643.7 | 616.2 | 415.8 | 401.5 | 388 | 380.8 | 424.1 | 407.4 | 417.9 | 384.7
1768 | 1547 | 472.7 | 189.08 | 221.0236 | 497.7 | 361.9 | 374.8 | 386.9 | 562 | 70 | 17.7 | 119.5 | 6 | 273.4 | 8.2 | 352.5 | 365.1 | 722.2 | 647 | 468.8 | 513.8 | 754.2 | 795.1 | 717.4 | 667.2 | 643.7 | 553.7 | 727.6 | 660.2 | 628.1 | 644.3 | 615.1 | 416 | 401.5 | 387.9 | 380.8 | 424.3 | 407.7 | 418.1 | 384.8
1769 | 1548 | 472.8 | 189.12 | 221.0704 | 501.6 | 361.4 | 373.8 | 387.6 | 558.6 | 70 | 17.7 | 119.5 | 5.5 | 241.5 | 7.7 | 352.8 | 365.4 | 716.2 | 632 | 469.1 | 514.2 | 752.1 | 793.5 | 716.8 | 667.1 | 635 | 545.1 | 728.2 | 659.6 | 618.3 | 644.9 | 614.1 | 416.1 | 401.4 | 387.8 | 380.8 | 424.7 | 408.3 | 418.5 | 385.1
1770 | 1549 | 472.6 | 189.04 | 220.9769 | 505.4 | 361.6 | 373.2 | 388.1 | 557.3 | 70 | 17.7 | 119.4 | 5.6 | 261.4 | 6.6 | 353 | 365.7 | 712.7 | 612.1 | 469.3 | 514.5 | 758.3 | 780.7 | 715.7 | 667 | 627.8 | 535.4 | 728.6 | 659.7 | 613.2 | 645.4 | 613.6 | 416.2 | 401.4 | 387.7 | 380.8 | 425.1 | 409 | 419.5 | 385.4
1771 | 1550 | 472.3 | 188.92 | 220.8366 | 510.6 | 361.9 | 373.1 | 388.6 | 554.8 | 70 | 17.7 | 119.4 | 5.8 | 278.9 | 6.1 | 353.3 | 366 | 714.2 | 598.5 | 469.6 | 514.9 | 751.2 | 762.1 | 711.8 | 666.7 | 628.7 | 529.3 | 729.1 | 652.6 | 603.2 | 646 | 612.1 | 416.4 | 401.6 | 387.7 | 380.9 | 425.4 | 409.4 | 420.2 | 385.6
1772 | 1551 | 473.6 | 189.44 | 221.4444 | 519.7 | 362.6 | 373.7 | 388.7 | 550.3 | 70 | 17.7 | 119.4 | 5.9 | 268.8 | 6.2 | 353.6 | 366.3 | 708.7 | 584.3 | 469.9 | 515.2 | 746.9 | 743.8 | 708.8 | 666.3 | 626.4 | 522.5 | 729.4 | 654.6 | 595.3 | 646.6 | 610.3 | 416.7 | 402 | 388 | 380.9 | 425.9 | 410 | 420.7 | 385.8
1773 | 1552 | 473.9 | 189.56 | 221.5847 | 520.2 | 362.4 | 374.3 | 389.2 | 549.1 | 70 | 17.7 | 119.6 | 5.9 | 268.6 | 6.5 | 353.9 | 366.6 | 701.8 | 566.8 | 470.3 | 515.5 | 747.8 | 720.3 | 704.9 | 665.8 | 619.1 | 518.8 | 729.9 | 653.5 | 590 | 647.1 | 609.4 | 416.9 | 402.3 | 388.1 | 380.8 | 426.3 | 410.7 | 421.4 | 386.1
1774 | 1553 | 473.3 | 189.32 | 221.3042 | 520.5 | 362.4 | 375.2 | 390 | 548.9 | 70 | 17.7 | 119.8 | 5.9 | 268 | 8 | 354.2 | 366.9 | 695.2 | 548.2 | 470.6 | 515.8 | 747 | 690.8 | 700.4 | 665.2 | 612.8 | 511.1 | 730.1 | 655.1 | 580.6 | 647.5 | 607.6 | 417.2 | 402.8 | 388.3 | 380.9 | 427 | 412 | 422.7 | 386.4
1775 | 1554 | 473.2 | 189.28 | 221.2574 | 524.5 | 362.6 | 377.5 | 392 | 553.1 | 70 | 17.7 | 119.9 | 5.9 | 258.2 | 8.8 | 354.5 | 367.2 | 687.9 | 532 | 470.9 | 516 | 739.7 | 660.9 | 697.5 | 664.5 | 612.8 | 504.7 | 730.3 | 652.4 | 571.3 | 648.2 | 606 | 417.7 | 403.7 | 388.8 | 381.1 | 427.6 | 412.7 | 423.9 | 386.6
1776 | 1555 | 473.5 | 189.4 | 221.3977 | 528.5 | 363 | 379.7 | 394.3 | 554.8 | 70 | 17.7 | 120.1 | 6.1 | 259.4 | 9 | 354.8 | 367.5 | 675.9 | 521.5 | 471.1 | 516.3 | 735.5 | 646.3 | 693.9 | 663.6 | 610.5 | 499.7 | 730.3 | 650.6 | 566.2 | 648.8 | 604.5 | 418.1 | 404.4 | 389.3 | 381.1 | 428.1 | 413.1 | 425 | 386.8
1777 | 1556 | 473.6 | 189.44 | 221.4444 | 535.4 | 364.2 | 381.4 | 395.8 | 551.6 | 70 | 17.7 | 120.4 | 5.5 | 264.9 | 9.4 | 355.1 | 367.8 | 669.7 | 513.2 | 471.4 | 516.5 | 740.9 | 638.8 | 690.6 | 662.9 | 603.7 | 494.2 | 730.2 | 655.3 | 564.1 | 649.4 | 603.2 | 418.6 | 405 | 389.7 | 381.2 | 428.6 | 413.5 | 425.6 | 387.1
1778 | 1557 | 473 | 189.2 | 221.1639 | 538.7 | 365.8 | 383.2 | 397 | 552.9 | 70 | 17.7 | 120.7 | 5.8 | 261 | 9.8 | 355.4 | 368.1 | 666.6 | 507 | 471.7 | 516.7 | 751.1 | 639.1 | 688.2 | 662.1 | 598.4 | 491.4 | 729.8 | 653 | 568 | 649.9 | 602.5 | 419.1 | 405.6 | 390 | 381.5 | 429.1 | 414.2 | 426.1 | 387.4
1779 | 1558 | 472.7 | 189.08 | 221.0236 | 537.4 | 366.7 | 385.2 | 397.6 | 553.8 | 70 | 17.7 | 120.8 | 5.5 | 263.1 | 9.7 | 355.7 | 368.4 | 660.1 | 503.4 | 472 | 517 | 752.3 | 652.6 | 687.4 | 661.3 | 592.8 | 489.8 | 729.2 | 648.2 | 566.3 | 650.4 | 601.6 | 419.6 | 405.9 | 390.6 | 381.6 | 429.4 | 414.3 | 426.7 | 387.6
1780 | 1559 | 473.6 | 189.44 | 221.4444 | 535.2 | 368.1 | 387 | 398.5 | 550.6 | 69.9 | 17.7 | 120.9 | 5.2 | 262.8 | 9.8 | 356 | 368.7 | 662 | 500.7 | 472.2 | 517.3 | 751.4 | 660.4 | 686.8 | 660.5 | 594.1 | 488.5 | 729.1 | 656.8 | 568.7 | 650.8 | 601.1 | 420 | 406.1 | 390.9 | 381.9 | 429.6 | 414 | 426.4 | 387.7
1781 | 1560 | 473 | 189.2 | 221.1639 | 540.6 | 368.9 | 386.9 | 398.7 | 551.6 | 69.9 | 17.7 | 120.9 | 5.9 | 263.2 | 9.6 | 356.3 | 369.1 | 663.8 | 507.4 | 472.5 | 517.6 | 746 | 666 | 684.7 | 659.8 | 593.1 | 485.7 | 728.6 | 658.8 | 577.1 | 651.3 | 601.4 | 420.3 | 406.1 | 391.3 | 382 | 430 | 414.3 | 426.3 | 388
1782 | 1561 | 473.9 | 189.56 | 221.5847 | 539.7 | 369 | 386.4 | 398.9 | 551 | 69.8 | 17.7 | 120.9 | 6.6 | 266.1 | 9.6 | 356.6 | 369.4 | 680.5 | 515.6 | 472.8 | 517.8 | 729.3 | 716.3 | 687 | 659.4 | 594.7 | 489.9 | 727.8 | 657 | 591.5 | 651.8 | 602.4 | 420.5 | 406.2 | 391.6 | 382.2 | 430.3 | 414.7 | 426.6 | 388.3
1783 | 1562 | 473.7 | 189.48 | 221.4912 | 533.4 | 369.2 | 386.3 | 399.9 | 552.7 | 69.8 | 17.7 | 120.9 | 6.1 | 265.9 | 9.2 | 356.9 | 369.7 | 691.4 | 524.9 | 473 | 518.1 | 738 | 748.1 | 689 | 659.1 | 597.3 | 494.3 | 726.8 | 658.1 | 595.9 | 652.2 | 603.2 | 420.8 | 406.4 | 392 | 382.3 | 430.5 | 415.1 | 426.9 | 388.6
1784 | 1563 | 473.3 | 189.32 | 221.3042 | 526.4 | 369.1 | 386 | 400.4 | 550.8 | 69.8 | 17.7 | 121 | 6.1 | 270.5 | 8.9 | 357.2 | 370.2 | 706.2 | 553.1 | 473.3 | 518.5 | 747.7 | 781.5 | 693.3 | 658.8 | 599.5 | 511.4 | 726.1 | 654.3 | 603.4 | 652.6 | 604.6 | 421 | 406.4 | 392.2 | 382.5 | 430.7 | 414.7 | 426.3 | 388.7
1785 | 1564 | 472.5 | 189 | 220.9301 | 518.2 | 369.2 | 385.9 | 399.7 | 547.3 | 69.8 | 17.7 | 121.1 | 6.5 | 273.2 | 8.7 | 357.6 | 370.5 | 713.8 | 588.4 | 473.6 | 518.8 | 748.6 | 795 | 698.1 | 658.7 | 596.8 | 535.8 | 725.7 | 648.3 | 611.8 | 652.9 | 606.1 | 421.2 | 406.1 | 392.3 | 382.6 | 430.8 | 414 | 425.6 | 388.8
1786 | 1565 | 473.1 | 189.24 | 221.2107 | 514.5 | 367.8 | 385.5 | 398.2 | 542.5 | 69.9 | 17.7 | 121.3 | 6.5 | 275 | 8.5 | 357.9 | 370.8 | 716.6 | 604.3 | 473.8 | 519.2 | 764.9 | 795.5 | 699.3 | 659 | 598.6 | 541.8 | 725.8 | 641.2 | 615.9 | 653.2 | 607.2 | 421.3 | 405.8 | 392 | 382.7 | 430.8 | 413.2 | 424.9 | 388.8
1787 | 1566 | 473.8 | 189.52 | 221.538 | 515.3 | 366.7 | 384.3 | 396.1 | 538.9 | 70 | 17.7 | 121.2 | 6.3 | 281 | 8.2 | 358.2 | 371.2 | 713.5 | 638.8 | 474 | 519.6 | 775.9 | 796 | 700.4 | 659.4 | 619.7 | 547.6 | 726.7 | 638.9 | 619.3 | 653.5 | 607.7 | 421.3 | 405.5 | 391.6 | 382.8 | 430.7 | 412.2 | 424.1 | 388.9
1788 | 1567 | 474.2 | 189.68 | 221.725 | 519.9 | 366.8 | 383.2 | 393.6 | 535.1 | 70 | 17.7 | 121.2 | 6.3 | 278.6 | 8.3 | 358.6 | 371.5 | 713.9 | 667.6 | 474.3 | 519.9 | 770.6 | 815.5 | 703.7 | 660.3 | 633 | 555.9 | 727.3 | 638.3 | 628.4 | 653.8 | 608.8 | 421.3 | 405.3 | 391.3 | 382.7 | 430.6 | 411.2 | 423.5 | 389
1789 | 1568 | 474.8 | 189.92 | 222.0055 | 521 | 366.9 | 382.1 | 392 | 534.8 | 69.9 | 17.7 | 121.2 | 5.7 | 278.4 | 8.2 | 358.9 | 371.8 | 720 | 700 | 474.6 | 520.3 | 774.1 | 823.2 | 706.8 | 661.3 | 638 | 579.7 | 727.4 | 641.5 | 646.6 | 654.2 | 612.3 | 421.3 | 405.6 | 391.4 | 382.8 | 430.6 | 410.4 | 423.2 | 389.1
1790 | 1569 | 471.8 | 188.72 | 220.6028 | 528 | 366.4 | 381.3 | 390.6 | 538.7 | 69.7 | 17.7 | 121.2 | 6.2 | 281.4 | 8.2 | 359.2 | 372.2 | 721.3 | 720.7 | 474.9 | 520.7 | 775.9 | 818 | 707.7 | 662.5 | 644.5 | 597.6 | 726.8 | 641.6 | 660.5 | 654.6 | 615.4 | 421.4 | 405.6 | 391.6 | 383 | 430.6 | 409.8 | 423.1 | 389.2
1791 | 1570 | 471.9 | 188.76 | 220.6496 | 528.3 | 365.2 | 381.3 | 390.7 | 539.1 | 69.7 | 17.7 | 121.3 | 6.8 | 281.7 | 8.5 | 359.5 | 372.5 | 718.2 | 733.1 | 475.1 | 521.2 | 770 | 817.4 | 708.3 | 663.5 | 655.8 | 603.9 | 726.6 | 639.4 | 659.7 | 655 | 616 | 421.6 | 405.6 | 391.8 | 383.2 | 430.4 | 408.9 | 422.8 | 389.2
1792 | 1571 | 472.9 | 189.16 | 221.1171 | 527.9 | 364.6 | 380.5 | 390.2 | 537.5 | 69.6 | 17.7 | 121.3 | 6.3 | 281.7 | 8.5 | 359.9 | 372.9 | 730.2 | 742 | 475.4 | 521.6 | 775.4 | 825.4 | 710.3 | 664.7 | 657.2 | 615.7 | 727.1 | 638.9 | 664.4 | 655.4 | 617.7 | 421.8 | 405.7 | 391.9 | 383.2 | 430.3 | 408.1 | 422.1 | 389.3
1793 | 1572 | 472.4 | 188.96 | 220.8834 | 526.7 | 363.8 | 380.1 | 389.2 | 536.2 | 69.6 | 17.7 | 121.3 | 5.7 | 282.2 | 8.6 | 360.2 | 373.2 | 740.8 | 745.9 | 475.7 | 522.1 | 774.9 | 823.2 | 712.4 | 666 | 650.7 | 623.7 | 727.1 | 635.6 | 670.2 | 655.8 | 620.2 | 421.9 | 405.6 | 392 | 383.3 | 430.1 | 407.4 | 421.4 | 389.4
1794 | 1573 | 471.7 | 188.68 | 220.556 | 526.8 | 362.9 | 379.5 | 387.3 | 534.1 | 69.6 | 17.6 | 121.4 | 5.5 | 283.1 | 8.7 | 360.5 | 373.6 | 734.6 | 750.8 | 475.9 | 522.6 | 762.6 | 828.6 | 714.7 | 667.8 | 653.2 | 634.7 | 727.8 | 633 | 673 | 656.1 | 621.4 | 422 | 405.5 | 392.4 | 383.4 | 430 | 407 | 421.1 | 389.5
1795 | 1574 | 472.4 | 188.96 | 220.8834 | 528.6 | 361.5 | 378.6 | 385.7 | 535.2 | 69.6 | 17.6 | 121.4 | 5.2 | 276.1 | 8.6 | 360.8 | 373.9 | 740.6 | 742.3 | 476.2 | 523.1 | 765.1 | 839.9 | 717.5 | 669.2 | 651.9 | 651.3 | 728 | 638.9 | 685.6 | 656.4 | 625.2 | 422.2 | 405.4 | 392.5 | 383.6 | 430 | 406.7 | 420.8 | 389.6
1796 | 1575 | 473.3 | 189.32 | 221.3042 | 525.2 | 360.6 | 378.7 | 385.1 | 540.7 | 69.6 | 17.6 | 121.3 | 5.3 | 278.3 | 7.9 | 361.2 | 374.3 | 750.5 | 743.8 | 476.4 | 523.6 | 775.2 | 847.3 | 720 | 670.6 | 649.7 | 661.7 | 727.9 | 642.2 | 686.4 | 656.8 | 627 | 422.3 | 405.2 | 392.3 | 383.6 | 429.9 | 406.7 | 420.6 | 389.7
1797 | 1576 | 472 | 188.8 | 220.6963 | 525 | 360 | 377.8 | 385.3 | 540.2 | 69.5 | 17.6 | 121.2 | 5.3 | 271.4 | 7.8 | 361.5 | 374.7 | 747.5 | 761 | 476.7 | 524.2 | 773.4 | 845.7 | 722.6 | 671.8 | 648.4 | 676.7 | 727.7 | 638.7 | 686 | 657.1 | 628.6 | 422.3 | 405.1 | 392.2 | 383.6 | 429.7 | 405.9 | 420.2 | 389.7
1798 | 1577 | 471.7 | 188.68 | 220.556 | 524.5 | 359.2 | 378.2 | 385.9 | 538.2 | 69.5 | 17.6 | 121.2 | 5.8 | 252.1 | 7.6 | 361.8 | 375 | 749.6 | 766.5 | 476.9 | 524.7 | 783.3 | 850.4 | 725.7 | 672.9 | 655.9 | 685.5 | 728 | 639.6 | 685.3 | 657.4 | 630.1 | 422.4 | 405.2 | 392.4 | 383.8 | 429.6 | 405.6 | 420 | 389.7
1799 | 1578 | 472.4 | 188.96 | 220.8834 | 520.3 | 358.7 | 377.6 | 385.6 | 540.6 | 69.5 | 17.6 | 121.3 | 5 | 250.5 | 7.3 | 362.1 | 375.4 | 751.6 | 770.7 | 477.2 | 525.2 | 785.8 | 847.7 | 728 | 674 | 661.4 | 684.3 | 728.5 | 643.2 | 686.6 | 657.8 | 631.5 | 422.5 | 404.9 | 392.4 | 383.9 | 429.6 | 405.5 | 420 | 389.8
1800 | 1579 | 472.3 | 188.92 | 220.8366 | 521.9 | 358.4 | 376.8 | 385.3 | 543.3 | 69.4 | 17.6 | 121.2 | 4.5 | 244.9 | 7 | 362.4 | 375.8 | 760.3 | 784.5 | 477.4 | 525.8 | 792 | 840.7 | 730.2 | 675 | 661 | 704.4 | 728.5 | 641.4 | 696.2 | 658.1 | 635.3 | 422.6 | 404.8 | 392.6 | 384.1 | 429.5 | 405.2 | 419.9 | 389.9
1801 | 1580 | 472 | 188.8 | 220.6963 | 523.1 | 358 | 376.4 | 384.9 | 543.4 | 69.4 | 17.6 | 121.2 | 5.3 | 268.1 | 6.7 | 362.8 | 376.1 | 755 | 791.1 | 477.7 | 526.3 | 804.8 | 835.3 | 731.8 | 676.4 | 659.1 | 724.1 | 728.3 | 639 | 699.2 | 658.4 | 637.6 | 422.7 | 404.8 | 392.7 | 384.3 | 429.4 | 404.6 | 419.6 | 389.9
1802 | 1581 | 472.1 | 188.84 | 220.7431 | 523.1 | 357.8 | 376.3 | 384.5 | 541.9 | 69.4 | 17.6 | 121.2 | 5.8 | 256.4 | 6.3 | 363.1 | 376.4 | 754.6 | 792.8 | 477.9 | 526.8 | 805.7 | 835.5 | 733.6 | 678 | 655.9 | 726.9 | 728.6 | 643.6 | 701.8 | 658.7 | 639.3 | 422.9 | 404.5 | 392.6 | 384.4 | 429.4 | 404.3 | 419.3 | 390
1803 | 1582 | 472.4 | 188.96 | 220.8834 | 521.8 | 357.3 | 375.8 | 384.3 | 539 | 69.5 | 17.6 | 121.1 | 6.2 | 247.7 | 6.9 | 363.4 | 376.8 | 754.7 | 792.7 | 478.2 | 527.4 | 800.6 | 842.4 | 734.7 | 679.5 | 657.5 | 720.6 | 729.4 | 643 | 701.2 | 659 | 640 | 423.1 | 404.4 | 392.6 | 384.4 | 429.3 | 403.7 | 418.8 | 390
1804 | 1583 | 473 | 189.2 | 221.1639 | 527.6 | 357.3 | 375.6 | 384.1 | 538.6 | 69.6 | 17.6 | 121.1 | 6.1 | 247.4 | 6.8 | 363.8 | 377.2 | 762.8 | 792 | 478.4 | 527.9 | 805.8 | 846.1 | 736.3 | 680.9 | 666.1 | 726.6 | 730.2 | 644.9 | 708.4 | 659.3 | 643.5 | 423.2 | 404.2 | 392.7 | 384.4 | 429.1 | 403.3 | 418.3 | 390.1
1805 | 1584 | 472.6 | 189.04 | 220.9769 | 526.9 | 356.8 | 376 | 383.7 | 535.6 | 69.7 | 17.6 | 121 | 5.6 | 246.5 | 6.5 | 364.1 | 377.5 | 760 | 787.1 | 478.7 | 528.4 | 808 | 842.7 | 734.7 | 681.9 | 668.3 | 726.8 | 730.4 | 643.8 | 703.2 | 659.6 | 643.7 | 423.3 | 404 | 392.8 | 384.6 | 428.9 | 402.9 | 417.7 | 390.1
1806 | 1585 | 472.7 | 189.08 | 221.0236 | 526.9 | 356.4 | 376.6 | 382.7 | 535.5 | 69.7 | 17.6 | 120.9 | 5.5 | 255.9 | 6.3 | 364.4 | 377.8 | 751.7 | 766.6 | 479 | 528.9 | 803.5 | 832 | 734.5 | 682.8 | 669.8 | 710.6 | 730.9 | 639.9 | 689.6 | 659.9 | 642.4 | 423.4 | 404 | 393.1 | 385 | 428.8 | 402.1 | 417 | 390
1807 | 1586 | 472.5 | 189 | 220.9301 | 527.7 | 357.1 | 377.2 | 382 | 534.8 | 69.8 | 17.6 | 120.9 | 5.9 | 243.4 | 5.9 | 364.8 | 378.2 | 735.1 | 757.6 | 479.2 | 529.3 | 792.2 | 806.9 | 732.5 | 683.4 | 674.3 | 688.5 | 732 | 642 | 675.8 | 660.2 | 640.6 | 423.6 | 403.9 | 393.5 | 385.3 | 428.6 | 401.5 | 416.6 | 390
1808 | 1587 | 472.8 | 189.12 | 221.0704 | 526.3 | 357.3 | 378 | 381.4 | 531.8 | 69.8 | 17.6 | 121 | 5.7 | 253.7 | 5.6 | 365.1 | 378.5 | 720.6 | 758.6 | 479.5 | 529.7 | 797.4 | 798.5 | 732.6 | 684.3 | 678.2 | 673.8 | 732.9 | 641.6 | 666.2 | 660.5 | 639.1 | 423.7 | 403.6 | 393.4 | 385.3 | 428.4 | 401.1 | 416.3 | 390
1809 | 1588 | 472.9 | 189.16 | 221.1171 | 523.3 | 357.7 | 377.5 | 381.2 | 528.5 | 69.9 | 17.6 | 121.2 | 5.5 | 268.9 | 5.1 | 365.4 | 378.8 | 715.6 | 757.8 | 479.8 | 530.1 | 800.7 | 794.5 | 732.3 | 685.3 | 674.3 | 662.1 | 733.8 | 639 | 657.9 | 660.9 | 638.1 | 423.7 | 403.1 | 393 | 385.1 | 428.4 | 401.2 | 416.3 | 390.1
1810 | 1589 | 472.4 | 188.96 | 220.8834 | 516.9 | 357.8 | 376.8 | 381.4 | 527.2 | 69.9 | 17.6 | 121.2 | 5.3 | 268.9 | 4.8 | 365.7 | 379.1 | 710.7 | 745.2 | 480 | 530.5 | 808.7 | 792.6 | 732.9 | 686.4 | 670.6 | 653 | 734.4 | 637 | 654.8 | 661.3 | 637.6 | 423.6 | 402.6 | 392.3 | 384.9 | 428.3 | 401.4 | 416.4 | 390.1
1811 | 1590 | 473 | 189.2 | 221.1639 | 513.6 | 357.3 | 375.4 | 381.9 | 527.1 | 70 | 17.6 | 121.3 | 6 | 261.3 | 4.7 | 366 | 379.5 | 708.5 | 743.1 | 480.3 | 530.9 | 808.7 | 805.8 | 733.8 | 687.4 | 671.2 | 646.3 | 735 | 644.6 | 654.9 | 661.7 | 637.4 | 423.5 | 402.3 | 391.8 | 384.7 | 428.3 | 401.5 | 416.4 | 390.2
1812 | 1591 | 471.9 | 188.76 | 220.6496 | 516 | 356.8 | 373.8 | 381.7 | 532.9 | 70 | 17.6 | 121.3 | 6.2 | 259.4 | 4.6 | 366.3 | 379.8 | 714.8 | 737.1 | 480.6 | 531.3 | 812.2 | 821.5 | 734.4 | 688 | 678.4 | 647.4 | 735 | 656.9 | 664 | 662 | 639.1 | 423.6 | 402.4 | 391.6 | 384.7 | 428.3 | 401.8 | 416.3 | 390.3
1813 | 1592 | 471.7 | 188.68 | 220.556 | 517.4 | 356.9 | 373.9 | 381.7 | 537.8 | 70.1 | 17.6 | 121.5 | 6.4 | 261.3 | 4.9 | 366.7 | 380.1 | 723 | 744.4 | 480.8 | 531.8 | 823.7 | 834.8 | 735.4 | 688.9 | 677.5 | 651.5 | 734.7 | 656.8 | 673.8 | 662.4 | 640.8 | 423.7 | 402.5 | 391.6 | 384.8 | 428.4 | 402.1 | 416.5 | 390.4
1814 | 1593 | 473.1 | 189.24 | 221.2107 | 517.9 | 357.2 | 374.3 | 382.2 | 538.7 | 70.2 | 17.6 | 121.8 | 6.1 | 254.7 | 5.5 | 367 | 380.5 | 733.1 | 747.1 | 481.1 | 532.3 | 826.2 | 837.2 | 737.5 | 690.2 | 675.2 | 668.1 | 734.6 | 656 | 685.5 | 662.8 | 643.3 | 423.9 | 402.7 | 391.7 | 384.9 | 428.4 | 402 | 416.6 | 390.4
1815 | 1594 | 471.3 | 188.52 | 220.369 | 518.3 | 357.6 | 375.3 | 382.6 | 537.9 | 70.3 | 17.6 | 121.9 | 6.1 | 257.3 | 5.8 | 367.3 | 380.8 | 744.4 | 739.4 | 481.3 | 532.9 | 820.3 | 838.4 | 740.5 | 691.2 | 668.5 | 680.5 | 734.1 | 654.2 | 692.8 | 663.2 | 646.6 | 424.1 | 402.9 | 391.8 | 385 | 428.4 | 401.8 | 416.5 | 390.4
1816 | 1595 | 470.6 | 188.24 | 220.0417 | 524.4 | 357.4 | 375.4 | 382.8 | 538.3 | 70.3 | 17.6 | 121.9 | 6 | 265 | 5.6 | 367.7 | 381.1 | 749.7 | 725 | 481.6 | 533.4 | 821.9 | 837.2 | 742.8 | 692.1 | 663.8 | 682.5 | 734.1 | 652.8 | 692.1 | 663.6 | 647.8 | 424.3 | 403 | 391.6 | 385 | 428.5 | 401.9 | 416.7 | 390.5
1817 | 1596 | 471.8 | 188.72 | 220.6028 | 520.4 | 357.2 | 375.5 | 383.3 | 539.7 | 70.4 | 17.6 | 121.9 | 5.6 | 263.8 | 6.6 | 368 | 381.5 | 750.3 | 732.4 | 481.8 | 533.9 | 815 | 827.8 | 744.3 | 693.1 | 658.1 | 693 | 734.6 | 644.1 | 683.7 | 663.9 | 648.7 | 424.4 | 402.9 | 391.7 | 385.1 | 428.4 | 401.7 | 416.8 | 390.5
1818 | 1597 | 471.8 | 188.72 | 220.6028 | 521 | 357.4 | 375.4 | 383.2 | 543 | 70.4 | 17.6 | 121.9 | 5.3 | 269.2 | 7.5 | 368.3 | 381.8 | 757.7 | 739.6 | 482.1 | 534.4 | 806.7 | 803.2 | 742.5 | 693.7 | 651.8 | 704.3 | 735 | 636.6 | 680.9 | 664.1 | 649.6 | 424.7 | 403.1 | 392.2 | 385.7 | 428.3 | 401.1 | 416.7 | 390.5
1819 | 1598 | 472.2 | 188.88 | 220.7898 | 521 | 357.9 | 375.8 | 382 | 545.6 | 70.6 | 17.6 | 121.8 | 5.4 | 262.7 | 7.9 | 368.7 | 382.1 | 755.1 | 743.8 | 482.4 | 534.9 | 803.1 | 794.9 | 740.7 | 694.9 | 652.1 | 699 | 735.4 | 629.4 | 674 | 664.3 | 649.1 | 425.1 | 403.3 | 392.6 | 386.1 | 428.1 | 400.5 | 416.2 | 390.5
1820 | 1599 | 472.3 | 188.92 | 220.8366 | 523 | 358.8 | 376.5 | 380.5 | 549.3 | 70.7 | 17.6 | 121.7 | 5.7 | 268 | 8.2 | 369 | 382.4 | 752.6 | 755.5 | 482.7 | 535.3 | 800.2 | 786.3 | 739.6 | 695.7 | 663.4 | 691.5 | 735.8 | 624.9 | 671.8 | 664.4 | 649.1 | 425.5 | 403.5 | 392.8 | 386.2 | 427.9 | 399.9 | 415.6 | 390.5
1821 | 1600 | 472.5 | 189 | 220.9301 | 522.3 | 358.9 | 376.4 | 379.5 | 550.8 | 70.8 | 17.6 | 121.7 | 5.8 | 268.2 | 7.7 | 369.3 | 382.7 | 745.5 | 763.4 | 482.9 | 535.7 | 795.3 | 780.8 | 738.9 | 696.2 | 677.5 | 693.4 | 736.1 | 622.8 | 671.6 | 664.6 | 649.1 | 425.8 | 403.6 | 393.3 | 386.5 | 427.6 | 399.3 | 414.8 | 390.4
1822 | 1601 | 471.9 | 188.76 | 220.6496 | 524.3 | 359.3 | 376.6 | 379.1 | 552.3 | 70.8 | 17.6 | 121.7 | 5.8 | 269.7 | 7.2 | 369.7 | 383 | 740.2 | 770.8 | 483.2 | 536 | 786.5 | 789.6 | 740.9 | 696.9 | 680.8 | 699.5 | 736 | 623.2 | 675.8 | 664.9 | 649.8 | 426.1 | 403.9 | 394 | 386.6 | 427.3 | 398.6 | 413.8 | 390.4
1823 | 1602 | 472.2 | 188.88 | 220.7898 | 521.3 | 360.3 | 376.8 | 378.9 | 549.7 | 70.9 | 17.6 | 121.6 | 5.8 | 265.8 | 7.5 | 370 | 383.3 | 751 | 779 | 483.5 | 536.5 | 795.9 | 803.4 | 743.1 | 697.7 | 674 | 708.4 | 735.8 | 627.8 | 684.9 | 665.1 | 652.1 | 426.4 | 404.5 | 394.5 | 386.6 | 427.2 | 398.4 | 413.1 | 390.4
1824 | 1603 | 472.1 | 188.84 | 220.7431 | 523.1 | 361.1 | 375.9 | 379.3 | 552.3 | 71 | 17.6 | 121.6 | 6.1 | 265.5 | 8.1 | 370.4 | 383.6 | 748.7 | 772.8 | 483.8 | 537 | 802.2 | 781.3 | 739.7 | 698.5 | 670.8 | 703.7 | 735.6 | 622.9 | 676.6 | 665.4 | 652.1 | 426.8 | 405.1 | 395.1 | 386.9 | 427 | 398.1 | 412.6 | 390.4
1825 | 1604 | 472.8 | 189.12 | 221.0704 | 529.2 | 361.6 | 375.5 | 379.2 | 549.5 | 71.1 | 17.6 | 121.6 | 6.3 | 270.2 | 7.9 | 370.7 | 383.9 | 737.2 | 749.6 | 484 | 537.5 | 800.3 | 766.4 | 736 | 699.9 | 663 | 686.5 | 736.2 | 619.2 | 665.9 | 665.6 | 650.1 | 427.2 | 405.6 | 395.4 | 386.9 | 426.7 | 397.7 | 412.1 | 390.4
1826 | 1605 | 472.8 | 189.12 | 221.0704 | 533.7 | 362.1 | 376.9 | 379 | 545.5 | 71.1 | 17.5 | 121.6 | 6.3 | 268 | 7.4 | 371.1 | 384.2 | 723.7 | 734.9 | 484.3 | 538 | 786.3 | 756.3 | 734.2 | 700.6 | 675.4 | 669.4 | 737 | 622.9 | 652 | 665.8 | 648.5 | 427.5 | 405.8 | 395.5 | 386.9 | 426.5 | 397.6 | 411.9 | 390.4
1827 | 1606 | 473 | 189.2 | 221.1639 | 535.3 | 362 | 377.8 | 378.2 | 539 | 71.1 | 17.5 | 121.7 | 5.9 | 268.3 | 6.5 | 371.4 | 384.6 | 711.2 | 717.2 | 484.5 | 538.4 | 777.1 | 742 | 731.3 | 701.5 | 671.7 | 652.9 | 737.8 | 619.7 | 640.9 | 666.1 | 646.8 | 427.6 | 405.7 | 395.6 | 386.8 | 426.4 | 397.4 | 411.7 | 390.4
1828 | 1607 | 473 | 189.2 | 221.1639 | 540.1 | 362.1 | 377.5 | 378.2 | 531.5 | 71.1 | 17.5 | 122 | 5.5 | 265.3 | 6 | 371.7 | 385 | 712.6 | 699.2 | 484.8 | 538.9 | 769 | 732.4 | 729 | 701.6 | 664.7 | 636 | 738.3 | 614.1 | 632.9 | 666.3 | 644.8 | 427.7 | 405.5 | 395.4 | 386.7 | 426.2 | 397 | 411.6 | 390.4
1829 | 1608 | 471.7 | 188.68 | 220.556 | 541.1 | 361.9 | 376.4 | 377.1 | 524.5 | 71 | 17.5 | 122.1 | 5.7 | 271.4 | 5.8 | 372.1 | 385.4 | 705.3 | 680.2 | 485.1 | 539.4 | 764 | 722.3 | 726.9 | 701.7 | 655.3 | 619.2 | 738.5 | 610.5 | 629.6 | 666.7 | 643.7 | 427.7 | 405.3 | 395 | 386.5 | 426 | 397 | 411.3 | 390.5
1830 | 1609 | 470.6 | 188.24 | 220.0417 | 537.7 | 361.6 | 375.4 | 377 | 520.7 | 71.2 | 17.5 | 122.3 | 5.8 | 270.3 | 6 | 372.5 | 385.8 | 692.9 | 686.1 | 485.3 | 539.8 | 753.6 | 713.4 | 724.3 | 702.1 | 648.4 | 606.6 | 738.8 | 608.4 | 619.5 | 666.9 | 641.7 | 427.6 | 404.9 | 394.5 | 386.4 | 425.9 | 397.3 | 411.4 | 390.5
1831 | 1610 | 469.8 | 187.92 | 219.6677 | 534.1 | 361.6 | 374.5 | 378 | 517.1 | 71.2 | 17.5 | 122.5 | 5.6 | 266.7 | 6.3 | 372.8 | 386.1 | 691.7 | 678 | 485.6 | 540.2 | 751.1 | 708.2 | 722.1 | 702.8 | 646.7 | 600.3 | 738.9 | 609.9 | 617 | 667.1 | 640.5 | 427.5 | 404.3 | 394 | 386.5 | 425.9 | 397.5 | 411.8 | 390.6
1832 | 1611 | 472.3 | 188.92 | 220.8366 | 530.4 | 362.7 | 373.3 | 378.9 | 515.5 | 71.3 | 17.5 | 122.6 | 6.2 | 273 | 6.4 | 373.1 | 386.5 | 690.1 | 684.3 | 485.8 | 540.7 | 745 | 702.3 | 720.8 | 703.5 | 652.6 | 593.2 | 738.8 | 611.8 | 615.3 | 667.4 | 639.8 | 427.4 | 403.8 | 393.6 | 386.3 | 426 | 397.9 | 412.1 | 390.7
1833 | 1612 | 471.3 | 188.52 | 220.369 | 535.4 | 364.3 | 372.9 | 379.5 | 515.4 | 71.3 | 17.5 | 122.7 | 6.2 | 280.5 | 6.1 | 373.5 | 386.9 | 686.9 | 697.8 | 486.1 | 541.2 | 746.8 | 715.3 | 721.7 | 703.6 | 651.7 | 594.9 | 738.6 | 612.2 | 617.7 | 667.6 | 639.2 | 427.3 | 403.4 | 393.2 | 386.2 | 426 | 398.3 | 412.4 | 390.8
1834 | 1613 | 471.2 | 188.48 | 220.3223 | 536.1 | 364.5 | 372.3 | 380.4 | 515.7 | 71.3 | 17.5 | 122.9 | 6.1 | 259.4 | 5.9 | 373.8 | 387.2 | 682.3 | 696.5 | 486.3 | 541.6 | 740.3 | 720 | 720.6 | 704 | 658.8 | 594.2 | 738.6 | 615.2 | 616.9 | 667.8 | 638.5 | 427.3 | 403.7 | 393.3 | 386.2 | 426 | 398.8 | 412.6 | 390.8
1835 | 1614 | 472.2 | 188.88 | 220.7898 | 537.2 | 364.3 | 372.5 | 380.2 | 514.9 | 71.4 | 17.5 | 123.1 | 6.1 | 261 | 5.7 | 374.1 | 387.6 | 677.5 | 690.3 | 486.6 | 542 | 749.3 | 715.2 | 719.5 | 704 | 650.2 | 585.5 | 738.4 | 611.1 | 611.9 | 668 | 637.5 | 427.4 | 404.2 | 393.8 | 386.5 | 426 | 398.8 | 413.2 | 390.8
1836 | 1615 | 471.5 | 188.6 | 220.4625 | 538.5 | 363.5 | 373.5 | 380.4 | 511.9 | 71.5 | 17.5 | 123.3 | 5.9 | 267.9 | 5.6 | 374.5 | 387.9 | 669.7 | 680.4 | 486.8 | 542.4 | 757 | 712 | 717.9 | 704.1 | 647.9 | 573.7 | 738.3 | 606.7 | 606.4 | 668.3 | 636.2 | 427.7 | 404.7 | 394 | 386.9 | 426 | 398.9 | 413.1 | 390.8
1837 | 1616 | 471.3 | 188.52 | 220.369 | 540.5 | 363.2 | 374.3 | 379.9 | 511 | 71.5 | 17.5 | 123.4 | 6.3 | 267.7 | 5.5 | 374.8 | 388.3 | 670.5 | 679 | 487.1 | 542.8 | 741.6 | 715.5 | 716.2 | 704.1 | 642.8 | 563.7 | 738.6 | 606.9 | 600.6 | 668.6 | 634.3 | 427.9 | 404.7 | 393.7 | 386.7 | 426.1 | 398.9 | 413 | 390.9
1838 | 1617 | 471.6 | 188.64 | 220.5093 | 537.7 | 363.2 | 374.3 | 380.1 | 508 | 71.6 | 17.5 | 123.6 | 6.2 | 286.8 | 5.4 | 375.1 | 388.7 | 662.1 | 688.3 | 487.3 | 543.2 | 732 | 729.3 | 716.4 | 704.4 | 642.3 | 558.5 | 738.7 | 607.8 | 598.7 | 668.8 | 633.3 | 428.1 | 404.6 | 393.7 | 386.5 | 426.2 | 399.2 | 413 | 390.9
1839 | 1618 | 471.6 | 188.64 | 220.5093 | 543.1 | 363.3 | 374.8 | 381 | 507.3 | 71.7 | 17.5 | 123.7 | 6.3 | 276.5 | 5 | 375.5 | 389 | 663.1 | 700.3 | 487.6 | 543.6 | 731.6 | 750 | 717 | 704.6 | 644.2 | 560 | 738.7 | 610 | 599.5 | 668.8 | 632.9 | 428.2 | 404.3 | 393.9 | 386.6 | 426.2 | 399.3 | 413 | 390.9
1840 | 1619 | 472.3 | 188.92 | 220.8366 | 546.6 | 362.9 | 375.5 | 381 | 506.7 | 71.8 | 17.5 | 123.8 | 6.5 | 260.6 | 4.7 | 375.8 | 389.4 | 657.5 | 707 | 487.8 | 544 | 749.5 | 767.1 | 717.7 | 705.3 | 646.3 | 572.7 | 738.2 | 611.7 | 609.2 | 669 | 633 | 428.3 | 404.3 | 393.9 | 386.8 | 426.3 | 399.5 | 412.9 | 390.9
1841 | 1620 | 472.2 | 188.88 | 220.7898 | 544 | 362.7 | 375.4 | 381.2 | 508.3 | 71.8 | 17.5 | 123.8 | 6.5 | 260.1 | 4.6 | 376.1 | 389.7 | 660 | 686.7 | 488.1 | 544.5 | 757 | 769.7 | 716.3 | 705.5 | 642.3 | 568.1 | 737.9 | 613.4 | 608.6 | 669.2 | 632.7 | 428.3 | 404.1 | 393.7 | 386.9 | 426.4 | 400 | 413.4 | 391
1842 | 1621 | 472.2 | 188.88 | 220.7898 | 544.2 | 362.9 | 375.3 | 382 | 510.4 | 71.8 | 17.5 | 123.7 | 5.7 | 263.1 | 4.5 | 376.4 | 390 | 658.2 | 665.4 | 488.4 | 544.9 | 750.8 | 758.1 | 713.6 | 705.3 | 631.9 | 554.8 | 738 | 611.4 | 600 | 669.4 | 630.8 | 428.3 | 404.1 | 393.6 | 386.7 | 426.7 | 400.7 | 414.3 | 391.1
1843 | 1622 | 472.4 | 188.96 | 220.8834 | 541.5 | 362.8 | 374.6 | 383.6 | 512 | 71.8 | 17.5 | 123.7 | 5.6 | 271.8 | 4.3 | 376.7 | 390.4 | 655 | 653 | 488.6 | 545.4 | 737.8 | 736.8 | 709.9 | 705.4 | 627.9 | 545.3 | 738.2 | 612.2 | 594.8 | 669.6 | 629.3 | 428.4 | 404.7 | 393.9 | 386.6 | 426.9 | 401.5 | 415 | 391.2
1844 | 1623 | 472.6 | 189.04 | 220.9769 | 540.6 | 362 | 374.5 | 384.8 | 510.3 | 71.8 | 17.5 | 123.9 | 6.1 | 280 | 4.3 | 377 | 390.7 | 655 | 663.3 | 488.9 | 545.8 | 736.4 | 737.7 | 710 | 705.6 | 628.1 | 543.9 | 738.2 | 605.8 | 595.3 | 669.7 | 628.5 | 428.6 | 404.9 | 394.1 | 386.7 | 426.9 | 401.5 | 415.1 | 391.2
1845 | 1624 | 472.5 | 189 | 220.9301 | 551.9 | 361 | 374.8 | 384.5 | 509.3 | 71.8 | 17.5 | 124.1 | 6.2 | 274.1 | 4.6 | 377.3 | 391.1 | 654.6 | 670.7 | 489.1 | 546.4 | 736 | 747.5 | 708.6 | 705.9 | 627.7 | 543.6 | 738.1 | 606 | 600.7 | 669.9 | 628.4 | 428.8 | 404.9 | 394.1 | 386.7 | 426.9 | 401.4 | 414.7 | 391.2
1846 | 1625 | 472.3 | 188.92 | 220.8366 | 553.3 | 360.1 | 375.1 | 383.9 | 510.4 | 71.7 | 17.5 | 124.3 | 6 | 253.3 | 5 | 377.7 | 391.4 | 655.5 | 675.3 | 489.4 | 546.9 | 739 | 740.4 | 708.4 | 706.5 | 631.6 | 547.7 | 737.7 | 606.7 | 602.5 | 670 | 627.6 | 428.8 | 404.7 | 394 | 386.8 | 426.9 | 400.9 | 414.1 | 391.1
1847 | 1626 | 472.3 | 188.92 | 220.8366 | 551.7 | 359.9 | 375 | 383 | 513.1 | 71.7 | 17.5 | 124.6 | 5.5 | 254.5 | 4.9 | 378 | 391.7 | 658.8 | 679.7 | 489.7 | 547.4 | 741 | 730.8 | 705.9 | 706.8 | 637.5 | 558.9 | 737.3 | 602.7 | 605.1 | 670.2 | 627.5 | 429 | 404.8 | 394.2 | 387.2 | 426.9 | 400.5 | 413.8 | 391.1
1848 | 1627 | 472.4 | 188.96 | 220.8834 | 546.7 | 360.1 | 375.8 | 381.9 | 524 | 71.6 | 17.5 | 124.8 | 6.1 | 291 | 5.1 | 378.3 | 392.1 | 665.1 | 704.2 | 490 | 547.9 | 735.8 | 733.5 | 704.5 | 706.9 | 646.6 | 576.3 | 737 | 601.6 | 611.5 | 670.4 | 627.9 | 429.3 | 405.1 | 394.6 | 387.5 | 426.9 | 400.5 | 414 | 391.1
1849 | 1628 | 472.7 | 189.08 | 221.0236 | 545.4 | 360.4 | 377.6 | 381.7 | 532.3 | 71.6 | 17.5 | 124.9 | 5.8 | 267.4 | 5.4 | 378.6 | 392.4 | 664.5 | 720.2 | 490.2 | 548.4 | 724.2 | 744.6 | 705.4 | 707.3 | 652.3 | 583.7 | 736.3 | 600.7 | 617.7 | 670.6 | 628.1 | 429.6 | 405.5 | 395.1 | 387.8 | 426.8 | 400.2 | 414 | 391.1
1850 | 1629 | 472.8 | 189.12 | 221.0704 | 543.7 | 360.6 | 378.1 | 381.2 | 530.5 | 71.7 | 17.5 | 125.1 | 5.8 | 263.2 | 5.5 | 378.9 | 392.8 | 670.5 | 736 | 490.5 | 548.9 | 724.6 | 758.1 | 707.4 | 707.6 | 653.8 | 603 | 735.2 | 601.3 | 629.6 | 670.7 | 630.4 | 430 | 405.8 | 395.4 | 387.7 | 426.7 | 399.7 | 413.6 | 391.1
1851 | 1630 | 472.5 | 189 | 220.9301 | 540.5 | 360.7 | 378.2 | 380.7 | 527.4 | 71.7 | 17.5 | 125.1 | 6 | 262.4 | 6.4 | 379.2 | 393.2 | 679.8 | 738.3 | 490.8 | 549.5 | 726.9 | 779 | 710.4 | 707.9 | 655.6 | 613.3 | 734.7 | 606.8 | 639.3 | 670.8 | 632.3 | 430.3 | 406.4 | 395.7 | 387.7 | 426.6 | 399.7 | 413 | 391.1
1852 | 1631 | 472.6 | 189.04 | 220.9769 | 541.7 | 360.8 | 377.9 | 380.9 | 529.3 | 71.5 | 17.5 | 125.2 | 6.7 | 264 | 7.9 | 379.5 | 393.5 | 679.9 | 727.1 | 491.2 | 550.1 | 735.8 | 781.6 | 710.9 | 708.1 | 650 | 610 | 734.4 | 608.9 | 642.4 | 671 | 632.7 | 430.5 | 406.7 | 396 | 387.7 | 426.5 | 399.6 | 412.7 | 391.2
1853 | 1632 | 469.6 | 187.84 | 219.5741 | 548.3 | 360.6 | 378.1 | 381.5 | 527.6 | 71.5 | 17.4 | 125.2 | 6.2 | 274.3 | 8.5 | 379.8 | 393.9 | 677.1 | 730.5 | 491.5 | 550.6 | 737.7 | 777.6 | 710.8 | 708.4 | 647.6 | 607 | 734.3 | 608.9 | 639.2 | 671.2 | 632.7 | 430.7 | 406.7 | 395.8 | 387.7 | 426.5 | 399.2 | 412.3 | 391.1
1854 | 1633 | 471.2 | 188.48 | 220.3223 | 546.4 | 360.6 | 378.7 | 380.9 | 525.2 | 71.5 | 17.4 | 125.2 | 5.8 | 270.4 | 8.1 | 380.1 | 394.2 | 672.9 | 721.3 | 491.8 | 551.2 | 744.7 | 760.9 | 707.7 | 709 | 646.7 | 601 | 734.7 | 606.2 | 635.1 | 671.3 | 632 | 430.8 | 406.7 | 395.6 | 387.6 | 426.5 | 398.9 | 411.8 | 391.1
1855 | 1634 | 471.3 | 188.52 | 220.369 | 548.8 | 360.9 | 379.2 | 379.9 | 521.4 | 71.5 | 17.4 | 125.2 | 6.2 | 269.9 | 7.9 | 380.4 | 394.5 | 677.6 | 703.9 | 492.1 | 551.7 | 750.8 | 751.2 | 706.9 | 709 | 644.4 | 598 | 735.3 | 604.1 | 628.3 | 671.6 | 630.9 | 430.9 | 406.4 | 395.1 | 387.5 | 426.5 | 398.6 | 411.6 | 391.1
1856 | 1635 | 471.6 | 188.64 | 220.5093 | 553.9 | 361 | 379.1 | 379.2 | 518.2 | 71.6 | 17.4 | 125.1 | 5.7 | 260.8 | 7.6 | 380.7 | 394.8 | 674.2 | 708.3 | 492.3 | 552.2 | 758.3 | 745.5 | 706 | 709.2 | 647.6 | 600 | 736.1 | 601.2 | 625.1 | 671.7 | 630.4 | 431 | 406.1 | 394.9 | 387.6 | 426.4 | 398.8 | 411.5 | 391
1857 | 1636 | 472.8 | 189.12 | 221.0704 | 548 | 361.3 | 378.7 | 378.6 | 520.4 | 71.7 | 17.4 | 125 | 6.3 | 262.7 | 7.6 | 381 | 395.1 | 668.6 | 690.3 | 492.6 | 552.8 | 742.2 | 717.5 | 702.7 | 709.3 | 648.7 | 600.6 | 736.5 | 597.5 | 620.5 | 671.9 | 630.1 | 431.1 | 406.3 | 395.4 | 388 | 426.4 | 399 | 411.6 | 391
1858 | 1637 | 472.9 | 189.16 | 221.1171 | 545.7 | 361 | 379 | 378 | 519.4 | 71.8 | 17.4 | 125 | 5.9 | 258.2 | 8.1 | 381.3 | 395.5 | 669.6 | 683.9 | 492.9 | 553.4 | 744.8 | 719.5 | 703.5 | 709.3 | 649.5 | 594.3 | 736.6 | 590.7 | 611.8 | 672 | 629 | 431.3 | 406.5 | 395.6 | 388.3 | 426.4 | 399.3 | 411.6 | 391
1859 | 1638 | 471.4 | 188.56 | 220.4158 | 547.2 | 360.4 | 379.7 | 377.6 | 515.7 | 71.9 | 17.4 | 125 | 6.3 | 249.1 | 8.8 | 381.5 | 395.8 | 671.5 | 695.4 | 493.2 | 554 | 751.4 | 733.7 | 704.7 | 709.7 | 648.9 | 592.8 | 736.8 | 590.1 | 616.4 | 672.2 | 628.9 | 431.4 | 406.5 | 395.7 | 388.2 | 426.4 | 399.5 | 411.9 | 391.1
1860 | 1639 | 471.9 | 188.76 | 220.6496 | 547 | 360.1 | 380 | 376.9 | 515.5 | 71.9 | 17.4 | 124.9 | 5.4 | 251.5 | 8.9 | 381.8 | 396.1 | 677 | 707.1 | 493.5 | 554.6 | 743.4 | 734.2 | 705.1 | 710 | 651.2 | 598.8 | 736.7 | 591.6 | 614.1 | 672.4 | 628.7 | 431.5 | 406.6 | 396.1 | 388.4 | 426.3 | 399.6 | 411.9 | 391.1
1861 | 1640 | 472.1 | 188.84 | 220.7431 | 545.5 | 360 | 379.5 | 376.7 | 515.1 | 72 | 17.4 | 124.9 | 5.8 | 250.1 | 9 | 382.2 | 396.4 | 680 | 710.5 | 493.8 | 555.1 | 738.8 | 747.4 | 705.1 | 710.5 | 646.6 | 593.9 | 736.9 | 590.4 | 611.5 | 672.4 | 628.3 | 431.6 | 406.7 | 396.3 | 388.5 | 426.2 | 399.4 | 411.7 | 391
1862 | 1641 | 472.1 | 188.84 | 220.7431 | 548 | 360.8 | 379.2 | 377.1 | 514 | 72.2 | 17.4 | 124.9 | 5.4 | 249.3 | 9.5 | 382.4 | 396.7 | 679.9 | 713.5 | 494.1 | 555.6 | 747 | 771.4 | 706.4 | 711.1 | 649.6 | 588 | 737.2 | 598.8 | 611.7 | 672.6 | 628 | 431.7 | 406.8 | 396.3 | 388.4 | 426.3 | 399.5 | 411.8 | 391.1
1863 | 1642 | 471.2 | 188.48 | 220.3223 | 545.9 | 360.9 | 378.9 | 377.3 | 515.4 | 72.4 | 17.4 | 124.9 | 6 | 251.1 | 9.6 | 382.7 | 397 | 679.3 | 719.3 | 494.4 | 556.1 | 752.5 | 792.4 | 710.2 | 711.6 | 652.9 | 592.1 | 737.3 | 605 | 618.3 | 672.7 | 628.4 | 431.8 | 406.9 | 396.5 | 388.3 | 426.4 | 399.8 | 412 | 391.2
1864 | 1643 | 471.7 | 188.68 | 220.556 | 548.6 | 360.9 | 378.4 | 378.5 | 518 | 72.5 | 17.4 | 125 | 5.9 | 249.5 | 9.4 | 383 | 397.3 | 685.5 | 722.5 | 494.7 | 556.7 | 760.1 | 802.3 | 711.2 | 711.7 | 652.2 | 601.4 | 737 | 610.3 | 626.4 | 673 | 629.5 | 432 | 407.3 | 397.1 | 388.5 | 426.5 | 400 | 412.3 | 391.2
1865 | 1644 | 471.8 | 188.72 | 220.6028 | 550.7 | 361.5 | 378.9 | 379 | 521.2 | 72.6 | 17.4 | 125.1 | 6.7 | 242.9 | 9 | 383.3 | 397.6 | 695.5 | 722 | 495 | 557.3 | 764.6 | 807.5 | 713.2 | 712 | 648.3 | 604.9 | 736.7 | 618.6 | 629.9 | 673.2 | 629.7 | 432.2 | 407.8 | 397.4 | 388.5 | 426.7 | 400.4 | 412.4 | 391.3
1866 | 1645 | 472.5 | 189 | 220.9301 | 551 | 362.1 | 379.4 | 379.5 | 524.3 | 72.6 | 17.4 | 125.1 | 6.5 | 254.4 | 8.8 | 383.6 | 397.9 | 705 | 718.1 | 495.3 | 557.8 | 766.3 | 818.5 | 715.4 | 712.2 | 644.1 | 607.2 | 736.3 | 617.6 | 637.6 | 673.3 | 630.7 | 432.4 | 408.2 | 397.3 | 388.5 | 426.8 | 400.8 | 412.9 | 391.4
1867 | 1646 | 473.2 | 189.28 | 221.2574 | 550 | 362.5 | 379.6 | 380.9 | 526.7 | 72.7 | 17.4 | 125.2 | 5.9 | 253 | 8.9 | 383.9 | 398.1 | 704.5 | 697.2 | 495.7 | 558.3 | 775.4 | 825.8 | 717 | 712.2 | 639.5 | 599.2 | 736 | 622.1 | 639.2 | 673.7 | 630.2 | 432.6 | 408.3 | 397.1 | 388.3 | 427 | 401.4 | 413.2 | 391.4
1868 | 1647 | 472.7 | 189.08 | 221.0236 | 554.6 | 363.1 | 380.1 | 381.7 | 534.7 | 72.7 | 17.4 | 125.3 | 5.5 | 252.2 | 8.4 | 384.2 | 398.4 | 705 | 711.4 | 496 | 558.8 | 787.8 | 839.1 | 719.9 | 712.9 | 639.2 | 608.6 | 736 | 627.2 | 644.8 | 673.8 | 631.7 | 432.7 | 408.2 | 397 | 388.3 | 427.2 | 402.1 | 413.6 | 391.5
1869 | 1648 | 473 | 189.2 | 221.1639 | 549.1 | 363.8 | 379.9 | 382.1 | 534.6 | 72.8 | 17.4 | 125.3 | 5.1 | 246.5 | 8.7 | 384.5 | 398.7 | 704.4 | 723 | 496.3 | 559.4 | 796 | 837.2 | 721.4 | 712.8 | 646.3 | 613.7 | 735.7 | 625.2 | 645.1 | 674 | 632.1 | 432.9 | 407.9 | 396.9 | 388.4 | 427.2 | 401.8 | 413.4 | 391.5
1870 | 1649 | 473 | 189.2 | 221.1639 | 546 | 364.5 | 380.9 | 381.9 | 535 | 72.9 | 17.4 | 125.2 | 5.8 | 241.7 | 9.1 | 384.8 | 399 | 698 | 726.2 | 496.6 | 559.9 | 786.4 | 834.7 | 720.6 | 713.1 | 657.2 | 609.3 | 735.9 | 626.7 | 640.3 | 674.1 | 631.5 | 433 | 407.7 | 396.6 | 388.6 | 427.4 | 401.6 | 413.1 | 391.4
1871 | 1650 | 473 | 189.2 | 221.1639 | 544.8 | 364.4 | 381.4 | 381.1 | 534.3 | 73 | 17.4 | 125.2 | 6.2 | 252.1 | 8.8 | 385 | 399.2 | 699.7 | 730.4 | 496.9 | 560.5 | 773.3 | 837.2 | 721.6 | 714.1 | 656 | 613.2 | 736.4 | 628.9 | 637.6 | 674.4 | 631.3 | 433.1 | 407.2 | 396.6 | 388.6 | 427.6 | 401.9 | 413.5 | 391.5
1872 | 1651 | 473 | 189.2 | 221.1639 | 543.6 | 364.5 | 381.1 | 381.4 | 536.7 | 73.2 | 17.4 | 125.2 | 5.8 | 256.1 | 8.8 | 385.3 | 399.5 | 700.2 | 720.3 | 497.3 | 561.1 | 763.5 | 831.4 | 721.2 | 714.5 | 658.4 | 607 | 736.8 | 630 | 642.2 | 674.7 | 631.4 | 433.1 | 406.8 | 396.3 | 388.6 | 427.7 | 402.1 | 413.6 | 391.6
1873 | 1652 | 472.8 | 189.12 | 221.0704 | 546.5 | 365 | 380.9 | 381.7 | 538.5 | 73.4 | 17.4 | 125.2 | 6 | 248.7 | 8.7 | 385.6 | 399.7 | 704.2 | 715 | 497.6 | 561.6 | 748.9 | 801.6 | 719.2 | 714.7 | 658.8 | 602.1 | 736.8 | 626.9 | 636.5 | 674.8 | 630.7 | 433 | 406.7 | 395.8 | 388.6 | 427.8 | 401.8 | 413.6 | 391.5
1874 | 1653 | 473.1 | 189.24 | 221.2107 | 546 | 364.9 | 381 | 381.6 | 533.4 | 73.4 | 17.4 | 125.3 | 5.2 | 250.4 | 7.9 | 385.9 | 400 | 704.9 | 724.4 | 497.9 | 562.2 | 738.5 | 794.9 | 719.4 | 714.7 | 656.9 | 602 | 737.2 | 620.7 | 641.2 | 674.9 | 631.8 | 433.1 | 406.8 | 395.6 | 388.6 | 427.8 | 401.4 | 413.2 | 391.5
1875 | 1654 | 472.6 | 189.04 | 220.9769 | 547.8 | 364.8 | 380.6 | 381.5 | 529.8 | 73.3 | 17.4 | 125.4 | 5.5 | 247.9 | 8 | 386.2 | 400.2 | 702.3 | 706.6 | 498.3 | 562.8 | 741.8 | 791.1 | 719.6 | 714.6 | 648.7 | 592.3 | 737.3 | 619.7 | 638.9 | 675.4 | 631.9 | 433.2 | 407.1 | 395.8 | 388.6 | 428 | 401.8 | 413.1 | 391.7
1876 | 1655 | 472.4 | 188.96 | 220.8834 | 546.6 | 364.7 | 380.9 | 381.9 | 531.6 | 73.1 | 17.4 | 125.5 | 6.2 | 242.9 | 8.4 | 386.5 | 400.5 | 697.2 | 688.1 | 498.6 | 563.3 | 739.2 | 778.1 | 717.3 | 714.4 | 642.8 | 579.5 | 737.9 | 616.4 | 627 | 675.4 | 630.1 | 433.3 | 407.4 | 396.2 | 388.6 | 428.2 | 402.3 | 413.7 | 391.8
1877 | 1656 | 472 | 188.8 | 220.6963 | 545.7 | 364.1 | 380.7 | 383.6 | 533.6 | 73.2 | 17.4 | 125.7 | 6.7 | 244 | 8.2 | 386.8 | 400.7 | 687.4 | 666.8 | 498.9 | 563.8 | 736.2 | 753.8 | 714.2 | 714.2 | 634.7 | 569.9 | 738.2 | 610.3 | 614.5 | 675.7 | 628.5 | 433.4 | 407.5 | 396.1 | 388.5 | 428.5 | 402.8 | 414.3 | 391.9
1878 | 1657 | 472.4 | 188.96 | 220.8834 | 545.9 | 364.1 | 381.1 | 384.7 | 534.8 | 73.3 | 17.4 | 125.9 | 7.3 | 247.2 | 7.6 | 387.1 | 401 | 678.2 | 646.3 | 499.3 | 564.2 | 721.1 | 725.5 | 710.8 | 713.4 | 629.3 | 562.7 | 738.4 | 604.7 | 603.5 | 675.8 | 626.6 | 433.6 | 407.7 | 396.3 | 388.5 | 428.8 | 403.1 | 414.8 | 392
1879 | 1658 | 471.7 | 188.68 | 220.556 | 547.6 | 363.9 | 381.7 | 385.6 | 530.8 | 73.3 | 17.4 | 125.9 | 7.1 | 249.9 | 7.5 | 387.4 | 401.3 | 680.1 | 624.6 | 499.6 | 564.7 | 709 | 709.5 | 707.7 | 712.6 | 620.1 | 553 | 738.7 | 595.5 | 591.7 | 675.9 | 624.2 | 433.7 | 407.8 | 396.3 | 388.4 | 429 | 403.5 | 415.3 | 392
1880 | 1659 | 472.2 | 188.88 | 220.7898 | 550.1 | 363.6 | 381.7 | 387 | 526.2 | 73.2 | 17.4 | 125.9 | 7.1 | 247 | 7.6 | 387.6 | 401.5 | 670.7 | 610.4 | 499.9 | 565.2 | 699.3 | 707.2 | 705.3 | 711.7 | 610.6 | 543.6 | 738.7 | 591.3 | 581.1 | 676.2 | 622 | 433.7 | 407.7 | 396.1 | 388.4 | 429.4 | 404.3 | 416.1 | 392.2
1881 | 1660 | 472.4 | 188.96 | 220.8834 | 549.3 | 363.2 | 381.1 | 388.5 | 522.6 | 73 | 17.4 | 125.9 | 6 | 246.6 | 7.2 | 387.9 | 401.8 | 666.3 | 592.8 | 500 | 565.7 | 692.3 | 686.1 | 702.2 | 710.6 | 602.8 | 538.3 | 738.5 | 593.2 | 574.5 | 676.2 | 620.3 | 433.8 | 407.9 | 396.1 | 388.3 | 429.7 | 405 | 416.8 | 392.3
1882 | 1661 | 472.4 | 188.96 | 220.8834 | 548.8 | 363.8 | 381.7 | 389.9 | 521.9 | 73 | 17.4 | 125.9 | 6.1 | 236.3 | 6.8 | 388.2 | 402 | 670.8 | 576.9 | 500.3 | 566.1 | 696.1 | 666.6 | 698.2 | 709.5 | 597 | 529.4 | 738.3 | 593 | 565.9 | 676.2 | 618.4 | 433.8 | 408 | 396.1 | 388.3 | 429.9 | 405.7 | 417.2 | 392.4
1883 | 1662 | 472.4 | 188.96 | 220.8834 | 557.3 | 363.7 | 383.5 | 392.3 | 522.4 | 72.9 | 17.4 | 125.9 | 6.1 | 271.7 | 5.9 | 388.5 | 402.3 | 665.7 | 560.3 | 500.6 | 566.4 | 702.5 | 673.1 | 694.7 | 708.4 | 589.3 | 524.1 | 738.3 | 602.4 | 565.5 | 676.7 | 617.3 | 434 | 408.2 | 396.1 | 388.3 | 430.4 | 406.7 | 417.6 | 392.6
1884 | 1663 | 472.4 | 188.96 | 220.8834 | 562.2 | 363.5 | 385 | 394.2 | 529.7 | 72.9 | 17.4 | 125.9 | 6.9 | 256.1 | 6.4 | 388.8 | 402.6 | 665 | 559.5 | 500.8 | 566.8 | 707.5 | 684 | 693.5 | 707.3 | 584.9 | 522.4 | 737.8 | 607.9 | 571.5 | 677 | 617.1 | 434.1 | 408.4 | 396.1 | 388.4 | 431.1 | 409 | 418.7 | 392.9
1885 | 1664 | 472.6 | 189.04 | 220.9769 | 565.9 | 363.9 | 386.9 | 395 | 534.9 | 72.8 | 17.4 | 126.1 | 6.3 | 250.2 | 7.2 | 389.1 | 402.8 | 672.6 | 574.1 | 501.1 | 567.2 | 713.9 | 711.9 | 695.2 | 706.5 | 592.5 | 525.6 | 737 | 611.4 | 581.9 | 677.1 | 617.4 | 434.3 | 408.8 | 396.1 | 388.5 | 431.5 | 409.8 | 419.2 | 393
1886 | 1665 | 472.6 | 189.04 | 220.9769 | 565.2 | 364.6 | 388.4 | 394.8 | 536.2 | 72.8 | 17.4 | 126.2 | 6.2 | 239.7 | 7.7 | 389.4 | 403.1 | 680.8 | 600.6 | 501.4 | 567.7 | 726 | 731 | 695.8 | 706.4 | 598 | 534.9 | 736.5 | 617.5 | 591.3 | 677.1 | 617.7 | 434.5 | 409 | 396.1 | 388.6 | 432.3 | 412 | 419.9 | 393.3
1887 | 1666 | 472.2 | 188.88 | 220.7898 | 560.3 | 365.3 | 389.7 | 395.2 | 540.1 | 72.7 | 17.3 | 126.2 | 5.9 | 248.8 | 7.4 | 389.7 | 403.3 | 686.7 | 612.2 | 501.7 | 568.2 | 727.3 | 752.2 | 696.9 | 706.1 | 603.3 | 540.3 | 736.2 | 620.6 | 597.4 | 677.3 | 617.8 | 434.6 | 409.1 | 396.1 | 388.8 | 432.9 | 413 | 421.1 | 393.5
1888 | 1667 | 472.5 | 189 | 220.9301 | 558.1 | 365.9 | 389.6 | 396.1 | 545.4 | 72.6 | 17.3 | 126.2 | 6.3 | 246.3 | 7.6 | 390 | 403.6 | 685.5 | 615.1 | 502 | 568.7 | 722.3 | 763.7 | 696.6 | 705.7 | 607.1 | 538.3 | 735.7 | 623.3 | 596.8 | 677.1 | 617.2 | 434.7 | 409 | 396 | 388.9 | 433.4 | 413.9 | 422.1 | 393.6
1889 | 1668 | 472.4 | 188.96 | 220.8834 | 555.7 | 367 | 389 | 396.5 | 546.6 | 72.7 | 17.3 | 126.2 | 5.6 | 250 | 6.5 | 390.2 | 403.8 | 690.8 | 626.5 | 502.3 | 569.2 | 721.7 | 775 | 697.4 | 705.7 | 607.3 | 535.8 | 735.5 | 624.4 | 598.8 | 677.3 | 616.8 | 434.8 | 408.9 | 395.9 | 388.8 | 433.9 | 414.6 | 423 | 393.7
1890 | 1669 | 472.2 | 188.88 | 220.7898 | 555.9 | 368 | 388.6 | 396.7 | 542.8 | 72.7 | 17.3 | 126.3 | 5.5 | 255.6 | 5.8 | 390.5 | 404.1 | 689.1 | 634.1 | 502.6 | 569.8 | 719.3 | 781.5 | 697.7 | 706 | 609.8 | 541.4 | 735.6 | 620.2 | 601.9 | 677.7 | 617 | 434.8 | 408.7 | 395.9 | 388.9 | 434.3 | 414.5 | 423.3 | 393.9
1891 | 1670 | 472.3 | 188.92 | 220.8366 | 555.1 | 368.2 | 388.3 | 397.7 | 537.9 | 72.7 | 17.3 | 126.2 | 5.8 | 245.8 | 5.9 | 390.8 | 404.3 | 684.1 | 628.2 | 502.9 | 570.3 | 720.7 | 759 | 695.3 | 705.8 | 606.8 | 542.8 | 735.6 | 613.1 | 600.4 | 677.6 | 616.5 | 434.8 | 408.7 | 396.2 | 389 | 434.5 | 414.1 | 423.4 | 394
1892 | 1671 | 472.7 | 189.08 | 221.0236 | 554.6 | 368.2 | 388 | 397.8 | 533.1 | 72.7 | 17.3 | 126.1 | 5.7 | 243.6 | 6.2 | 391.1 | 404.6 | 678.2 | 633.5 | 503.2 | 570.9 | 728.1 | 737.4 | 695 | 705.5 | 605.7 | 544.4 | 735.6 | 603 | 599.7 | 677.5 | 616.1 | 434.9 | 408.7 | 396.4 | 389.2 | 434.7 | 413.3 | 423.1 | 394
1893 | 1672 | 473 | 189.2 | 221.1639 | 555.7 | 368.5 | 387.8 | 397.1 | 529.9 | 72.9 | 17.3 | 126.2 | 6.4 | 251.9 | 6.5 | 391.4 | 404.8 | 671.6 | 625.3 | 503.5 | 571.4 | 724.4 | 714.5 | 693.3 | 705.3 | 612.3 | 541.6 | 735.7 | 598.1 | 595.1 | 677.3 | 615.2 | 434.8 | 408.5 | 396.6 | 389.3 | 435 | 413.1 | 423 | 394.1
1894 | 1673 | 472.9 | 189.16 | 221.1171 | 561.5 | 368.3 | 386.6 | 396.3 | 526.7 | 73 | 17.3 | 126.4 | 6 | 266.2 | 7 | 391.7 | 405.1 | 665.8 | 631.9 | 503.8 | 571.9 | 719.1 | 714.2 | 692 | 705.1 | 609.9 | 540.3 | 735.8 | 590.8 | 589.9 | 676.9 | 614.3 | 434.9 | 408.3 | 396.5 | 389.3 | 435.1 | 413 | 423.2 | 394.2
1895 | 1674 | 472.8 | 189.12 | 221.0704 | 561.6 | 368.9 | 385.6 | 395.6 | 523.6 | 73.1 | 17.3 | 126.5 | 5.7 | 265.4 | 7.4 | 392 | 405.3 | 667.7 | 628.3 | 504.1 | 572.4 | 727.3 | 728.5 | 693.9 | 704.9 | 605.7 | 536.7 | 736 | 592.6 | 593 | 677.6 | 614.4 | 434.8 | 408.1 | 396.2 | 389.2 | 435.3 | 413.4 | 423.4 | 394.4
1896 | 1675 | 472.9 | 189.16 | 221.1171 | 560.3 | 368.6 | 385 | 395.5 | 526.3 | 73.3 | 17.3 | 126.6 | 5.6 | 263.3 | 7.5 | 392.3 | 405.5 | 680.1 | 622.5 | 504.4 | 572.8 | 733.4 | 732.4 | 692.9 | 704.5 | 608.3 | 536.2 | 735.7 | 598.3 | 598 | 677.6 | 614.7 | 434.8 | 408.4 | 396.3 | 389.1 | 435.6 | 413.9 | 423.9 | 394.6
1897 | 1676 | 473 | 189.2 | 221.1639 | 561.9 | 368.2 | 385.5 | 396.6 | 529.6 | 73.4 | 17.3 | 126.7 | 6 | 256.7 | 7.4 | 392.6 | 405.8 | 678.7 | 605.2 | 504.7 | 573.3 | 728.2 | 700.4 | 688.5 | 704.1 | 603.8 | 533.5 | 735.4 | 595.6 | 596.1 | 677.4 | 614 | 435 | 408.8 | 396.6 | 389.2 | 436 | 414.2 | 424.3 | 394.8
1898 | 1677 | 472.8 | 189.12 | 221.0704 | 565.4 | 368.8 | 387.1 | 397.7 | 531.5 | 73.5 | 17.3 | 126.6 | 5.8 | 257.3 | 7.4 | 392.9 | 406 | 668.4 | 590.1 | 505 | 573.8 | 717.8 | 689.4 | 685.6 | 703.2 | 599.1 | 529 | 735.2 | 589.8 | 588 | 677 | 612.5 | 435.2 | 409.6 | 397 | 389.2 | 436.4 | 414.3 | 424.6 | 394.9
1899 | 1678 | 472.4 | 188.96 | 220.8834 | 565.4 | 369 | 388.2 | 398.7 | 528.9 | 73.5 | 17.3 | 126.5 | 6.5 | 253.3 | 7.1 | 393.2 | 406.2 | 664.8 | 587 | 505.3 | 574.3 | 713.4 | 686.6 | 684.1 | 702.6 | 599.6 | 521.7 | 735.1 | 583.7 | 581.8 | 676.9 | 611 | 435.5 | 410.1 | 397.5 | 389.3 | 436.6 | 414.2 | 424.8 | 395
1900 | 1679 | 472.4 | 188.96 | 220.8834 | 565.4 | 369.8 | 389.6 | 399.5 | 529.5 | 73.5 | 17.3 | 126.5 | 6 | 239.6 | 6.9 | 393.5 | 406.5 | 657.9 | 578 | 505.6 | 574.7 | 720.5 | 684 | 682.3 | 702 | 597.4 | 518.6 | 735.1 | 579.1 | 584 | 676.9 | 610.2 | 435.7 | 410.6 | 397.7 | 389.4 | 436.8 | 414.2 | 424.9 | 395.1
1901 | 1680 | 470.8 | 188.32 | 220.1352 | 569.1 | 370.3 | 389.9 | 399.6 | 535.8 | 73.4 | 17.3 | 126.5 | 5.7 | 248.4 | 6.9 | 393.8 | 406.7 | 659.1 | 570.6 | 505.9 | 575.2 | 718.4 | 680.2 | 679.5 | 701.4 | 590.6 | 512.3 | 734.9 | 576.6 | 576.6 | 677.1 | 609.1 | 436 | 411 | 398 | 389.5 | 437.2 | 414.8 | 425.1 | 395.3
1902 | 1681 | 472.5 | 189 | 220.9301 | 576.3 | 370.2 | 389.1 | 400.4 | 534.9 | 73.3 | 17.3 | 126.6 | 5.6 | 244 | 6.9 | 394.1 | 406.9 | 660.6 | 569.2 | 506.2 | 575.6 | 726.9 | 697.5 | 679.4 | 700.9 | 584.2 | 509.1 | 734.7 | 575.7 | 575.5 | 676.9 | 608.2 | 436.2 | 411.6 | 398.4 | 389.6 | 437.5 | 415.2 | 425.2 | 395.4
1903 | 1682 | 472.5 | 189 | 220.9301 | 578.4 | 370.9 | 389.2 | 401.3 | 533.1 | 73.2 | 17.3 | 126.6 | 6 | 244.6 | 6.9 | 394.3 | 407.1 | 668.8 | 600.7 | 506.5 | 576.1 | 724.7 | 733.7 | 683.2 | 700.6 | 589.2 | 520.7 | 734.4 | 582.2 | 583.2 | 676.9 | 608.8 | 436.6 | 411.9 | 399.1 | 389.9 | 437.6 | 415.6 | 425.6 | 395.5
1904 | 1683 | 472.5 | 189 | 220.9301 | 583.2 | 371 | 390.5 | 402.1 | 532.4 | 73.2 | 17.3 | 126.6 | 6.5 | 242.2 | 7.2 | 394.6 | 407.3 | 678.5 | 641.5 | 506.8 | 576.5 | 729.2 | 754 | 686.7 | 700.9 | 597.5 | 539.3 | 733.9 | 587.5 | 596.8 | 677.1 | 610.6 | 436.9 | 411.9 | 399.4 | 390.2 | 437.7 | 415.3 | 425.5 | 395.5
1905 | 1684 | 471.7 | 188.68 | 220.556 | 587.7 | 371.4 | 390.9 | 401.3 | 531.6 | 73.2 | 17.3 | 126.6 | 7.4 | 241 | 7.2 | 394.9 | 407.5 | 670.3 | 660.7 | 507.2 | 577 | 729.8 | 741.4 | 685.7 | 701.2 | 601.2 | 546.1 | 733.3 | 587.3 | 597.6 | 677.1 | 611.1 | 437.1 | 411.8 | 399.4 | 390.5 | 437.7 | 414.9 | 425.3 | 395.6
1906 | 1685 | 472.7 | 189.08 | 221.0236 | 584.6 | 371.6 | 391.2 | 399.9 | 532.9 | 73.1 | 17.3 | 126.7 | 7 | 253.7 | 7.3 | 395.2 | 407.8 | 666.4 | 670 | 507.5 | 577.5 | 729.3 | 749.2 | 686.5 | 701.9 | 605.4 | 543.5 | 733.2 | 584.3 | 595.7 | 676.7 | 610.6 | 437.3 | 411.8 | 399.3 | 390.7 | 437.9 | 414.7 | 425.5 | 395.7
1907 | 1686 | 472.3 | 188.92 | 220.8366 | 581.3 | 372.3 | 392 | 399.5 | 532.4 | 73.1 | 17.3 | 126.6 | 6.4 | 270.3 | 7.4 | 395.5 | 408 | 671.2 | 666.3 | 507.8 | 578.1 | 728.5 | 763.2 | 686.9 | 702.4 | 606.2 | 543.5 | 733.3 | 586.5 | 598.6 | 677.1 | 610.6 | 437.4 | 412 | 399.3 | 390.6 | 438.2 | 415 | 425.9 | 396
1908 | 1687 | 472.6 | 189.04 | 220.9769 | 574.5 | 372 | 391.9 | 399.4 | 533.7 | 73 | 17.3 | 126.6 | 6 | 268.6 | 7.5 | 395.8 | 408.2 | 675.8 | 648.2 | 508.1 | 578.6 | 735.8 | 764.2 | 685.5 | 702.4 | 607.1 | 539.6 | 733.4 | 593.9 | 596.5 | 677.2 | 610.4 | 437.6 | 412.1 | 399.4 | 390.4 | 438.5 | 415.5 | 426.4 | 396.2
1909 | 1688 | 471.8 | 188.72 | 220.6028 | 584.1 | 372.6 | 392.1 | 400.2 | 543.8 | 73 | 17.3 | 126.6 | 5.9 | 253.9 | 7.8 | 396.1 | 408.5 | 672 | 648.9 | 508.5 | 579.1 | 726.4 | 778.7 | 688 | 702.5 | 607.1 | 541 | 733.4 | 598.4 | 600.4 | 677.3 | 610.4 | 437.7 | 412.2 | 399.7 | 390.5 | 438.9 | 415.8 | 426.7 | 396.3
1910 | 1689 | 473.5 | 189.4 | 221.3977 | 591.1 | 373 | 393.5 | 400.6 | 545.5 | 73.2 | 17.3 | 126.7 | 5.9 | 255 | 8.3 | 396.4 | 408.8 | 684.4 | 647.7 | 508.8 | 579.6 | 725.3 | 780.5 | 689.6 | 702.8 | 607.9 | 542 | 733.3 | 606.5 | 606.5 | 677.4 | 611.3 | 438 | 412.5 | 400 | 390.5 | 439.2 | 416.1 | 427.1 | 396.4
1911 | 1690 | 470.7 | 188.28 | 220.0885 | 593.9 | 373.3 | 394.6 | 401.2 | 548.5 | 73.3 | 17.3 | 126.9 | 6.6 | 249.2 | 8.6 | 396.7 | 409 | 697.3 | 644.8 | 509.2 | 580.2 | 734.6 | 783.6 | 690.2 | 702.9 | 609.4 | 541.7 | 733.5 | 611.4 | 611 | 677.4 | 611.6 | 438.1 | 412.4 | 399.9 | 390.6 | 439.7 | 416.8 | 428.3 | 396.6
1912 | 1691 | 469.3 | 187.72 | 219.4339 | 592.6 | 373.1 | 394.5 | 403.5 | 548.8 | 73.4 | 17.3 | 127 | 6.2 | 242.6 | 8.8 | 397 | 409.2 | 703.3 | 632.5 | 509.6 | 580.8 | 744.7 | 792.3 | 689.6 | 703.1 | 606.9 | 537.5 | 733.7 | 612.7 | 616.3 | 677.6 | 611.7 | 438.3 | 412.5 | 400.1 | 390.6 | 440.1 | 417.2 | 429.6 | 396.8
1913 | 1692 | 469.6 | 187.84 | 219.5741 | 591.8 | 372.7 | 393.9 | 405.1 | 553.7 | 73.4 | 17.3 | 127 | 6.7 | 243.8 | 8.2 | 397.3 | 409.5 | 701.4 | 619.8 | 510 | 581.4 | 743.1 | 781.4 | 686.5 | 703.1 | 604.2 | 531.3 | 733.7 | 614.4 | 607.7 | 677.7 | 611.3 | 438.4 | 412.7 | 400.7 | 390.7 | 440.7 | 418.3 | 430.5 | 397.1
1914 | 1693 | 471.2 | 188.48 | 220.3223 | 591.5 | 372.3 | 393.5 | 406.9 | 554.3 | 73.1 | 17.3 | 126.9 | 6.4 | 264.7 | 7.4 | 397.6 | 409.7 | 693.2 | 624.5 | 510.4 | 581.9 | 728.9 | 775.7 | 684.8 | 703 | 600.2 | 531.5 | 733.7 | 609.3 | 605.5 | 677.6 | 610.1 | 438.7 | 413.1 | 401.2 | 390.9 | 441.1 | 418.6 | 431.4 | 397.3
1915 | 1694 | 473.1 | 189.24 | 221.2107 | 593.2 | 372.2 | 394.6 | 408.2 | 548.9 | 72.9 | 17.3 | 126.8 | 6.2 | 241.2 | 6.9 | 397.9 | 409.9 | 697.8 | 619 | 510.8 | 582.4 | 738.1 | 761.3 | 683.7 | 702.8 | 603 | 531 | 733.7 | 605.6 | 606.2 | 677.6 | 610.2 | 439 | 413.4 | 401.7 | 391.2 | 441.6 | 419.2 | 432.1 | 397.5
1916 | 1695 | 473.9 | 189.56 | 221.5847 | 589.5 | 372.5 | 395.2 | 408.3 | 547 | 72.8 | 17.3 | 126.7 | 6.2 | 236.2 | 6.5 | 398.2 | 410.1 | 691.1 | 595.9 | 511.2 | 582.9 | 737.6 | 734.1 | 680.1 | 702.4 | 600.2 | 525.6 | 733.7 | 604.2 | 598 | 677.6 | 608.7 | 439.1 | 413.8 | 401.9 | 391.2 | 442.1 | 420.1 | 433 | 397.8
1917 | 1696 | 471.1 | 188.44 | 220.2755 | 587.2 | 372.8 | 394.6 | 411 | 547.1 | 72.8 | 17.3 | 126.5 | 5.9 | 256.5 | 7.5 | 398.5 | 410.4 | 687 | 578.7 | 511.6 | 583.3 | 729.3 | 726.8 | 677.8 | 701.9 | 594.1 | 522.1 | 733.8 | 607.8 | 592.7 | 677.6 | 607.4 | 439.3 | 414.2 | 401.7 | 391.2 | 442.7 | 421.1 | 434.1 | 398.1
1918 | 1697 | 471.6 | 188.64 | 220.5093 | 586.6 | 373 | 395.6 | 413.5 | 546.2 | 72.9 | 17.3 | 126.5 | 5.4 | 264.1 | 7.9 | 398.8 | 410.6 | 683.5 | 564.6 | 512 | 583.9 | 735.3 | 737.5 | 677.4 | 701.2 | 588.6 | 523.4 | 733.8 | 608.3 | 598.1 | 677.6 | 607.9 | 439.5 | 414.2 | 401.5 | 391.2 | 443.1 | 421.9 | 435.1 | 398.3
1919 | 1698 | 471.1 | 188.44 | 220.2755 | 586.1 | 373 | 396.2 | 414.7 | 549.5 | 73 | 17.3 | 126.4 | 5.5 | 261.3 | 7.5 | 399.1 | 410.8 | 690.7 | 552.2 | 512.4 | 584.3 | 741.5 | 741.3 | 676.4 | 700.7 | 586.6 | 525.1 | 733.4 | 615.4 | 602.2 | 677.7 | 608.5 | 439.7 | 414.3 | 401.4 | 391.2 | 443.6 | 423.1 | 435.9 | 398.6
1920 | 1699 | 472 | 188.8 | 220.6963 | 589.5 | 373.8 | 397 | 415.4 | 557.3 | 73.1 | 17.3 | 126.4 | 6.3 | 247.9 | 7.6 | 399.4 | 411 | 694.6 | 553 | 512.8 | 584.9 | 743.4 | 762 | 679.4 | 700.2 | 596.7 | 533.1 | 733.6 | 628.2 | 608.8 | 678 | 609.1 | 439.9 | 414.5 | 401.5 | 391.4 | 444.1 | 424.2 | 436.5 | 398.8
1921 | 1700 | 470.8 | 188.32 | 220.1352 | 596.6 | 374.6 | 398.3 | 415.8 | 562.1 | 73.3 | 17.2 | 126.3 | 6.2 | 271.1 | 7 | 399.6 | 411.2 | 704.1 | 572 | 513.3 | 585.5 | 751.6 | 780.4 | 681.6 | 699.8 | 602.5 | 542.6 | 733.4 | 630.7 | 614 | 678.2 | 610 | 440.1 | 414.8 | 401.7 | 391.6 | 444.5 | 424.8 | 437.2 | 399.1
1922 | 1701 | 471 | 188.4 | 220.2287 | 593.4 | 375.2 | 400.1 | 415.9 | 563.3 | 73.3 | 17.2 | 126.2 | 6.5 | 248.5 | 7.7 | 399.9 | 411.4 | 703.8 | 619.1 | 513.7 | 586 | 758.4 | 782.5 | 685 | 699.9 | 606.2 | 565.1 | 733.4 | 628 | 621.5 | 678.3 | 611.5 | 440.3 | 414.9 | 402 | 391.8 | 444.9 | 425.4 | 437.5 | 399.3
1923 | 1702 | 472 | 188.8 | 220.6963 | 600.4 | 375.5 | 400 | 414.9 | 558.7 | 73.4 | 17.2 | 126.4 | 6.8 | 254.6 | 8.7 | 400.2 | 411.6 | 704.1 | 637.9 | 514.1 | 586.6 | 761.3 | 801.5 | 687.8 | 700.4 | 610.6 | 577.4 | 733.1 | 625.7 | 634.8 | 678.4 | 614.3 | 440.4 | 415 | 402.3 | 392.2 | 445.1 | 425 | 437.6 | 399.5
1924 | 1703 | 472.2 | 188.88 | 220.7898 | 595.7 | 375.5 | 399.1 | 413.3 | 554.6 | 73.5 | 17.2 | 126.4 | 5.8 | 253.2 | 9.2 | 400.5 | 411.8 | 700.6 | 628.9 | 514.5 | 587.1 | 757.9 | 802.7 | 689 | 700.7 | 610 | 571 | 732.9 | 622.7 | 633.4 | 678.6 | 613.7 | 440.5 | 415 | 402.4 | 392.3 | 445.3 | 424.7 | 437.5 | 399.6
1925 | 1704 | 473 | 189.2 | 221.1639 | 591.8 | 374.9 | 398.2 | 412.8 | 550.6 | 73.4 | 17.2 | 126.4 | 5.3 | 256.5 | 9.4 | 400.8 | 412 | 710.6 | 631.8 | 514.9 | 587.8 | 763.6 | 812 | 690.7 | 700.7 | 609.8 | 571.2 | 733.3 | 623.8 | 643.5 | 678.8 | 615.4 | 440.6 | 415 | 402.4 | 392.4 | 445.7 | 425.1 | 437.4 | 399.8
1926 | 1705 | 472.5 | 189 | 220.9301 | 592.1 | 374.6 | 397.4 | 412.6 | 549.3 | 73.4 | 17.2 | 126.5 | 5.5 | 256.4 | 9.8 | 401 | 412.2 | 709.6 | 652.7 | 515.4 | 588.4 | 768.3 | 820.7 | 692.4 | 701 | 610.1 | 578.3 | 733.3 | 624.4 | 647.9 | 679 | 616.8 | 440.7 | 415.2 | 402.6 | 392.5 | 445.7 | 424.6 | 437.3 | 400
1927 | 1706 | 472.7 | 189.08 | 221.0236 | 590.8 | 375 | 398.7 | 412.5 | 547 | 73.4 | 17.2 | 126.5 | 6 | 260.6 | 9.6 | 401.3 | 412.4 | 700.6 | 658.1 | 515.8 | 589 | 774 | 820.6 | 695.1 | 702.1 | 612.4 | 580.1 | 733.3 | 624.5 | 645.6 | 679.1 | 617.1 | 440.8 | 415.4 | 402.9 | 392.8 | 445.9 | 423.8 | 436.6 | 400.1
1928 | 1707 | 473 | 189.2 | 221.1639 | 593 | 375.4 | 399.6 | 411.6 | 545.1 | 73.5 | 17.2 | 126.6 | 6.3 | 259.6 | 9.1 | 401.6 | 412.6 | 702.8 | 662.1 | 516.2 | 589.5 | 780.8 | 822.2 | 696 | 703 | 612.5 | 575.5 | 733.5 | 619.8 | 640.3 | 679.2 | 617.1 | 440.9 | 415.3 | 403 | 392.9 | 446.1 | 422.9 | 436.1 | 400.1
1929 | 1708 | 472.1 | 188.84 | 220.7431 | 592.6 | 375.9 | 399.1 | 410.5 | 541.8 | 73.5 | 17.2 | 126.6 | 6.3 | 260.4 | 8.8 | 401.9 | 412.8 | 706 | 648.1 | 516.6 | 590.2 | 783.9 | 819.4 | 696.8 | 703.4 | 606.2 | 566.7 | 733.9 | 619.3 | 640.4 | 679.3 | 616.6 | 441 | 415.1 | 402.8 | 392.8 | 446.4 | 422.8 | 436.1 | 400.3
1930 | 1709 | 472.7 | 189.08 | 221.0236 | 589.9 | 376.1 | 398.5 | 409.1 | 541.6 | 73.5 | 17.2 | 126.7 | 6.3 | 267.4 | 8.4 | 402.2 | 413 | 701.8 | 632.1 | 517 | 590.8 | 789.2 | 814 | 697.7 | 703.4 | 597.8 | 560.4 | 734.3 | 620.2 | 641.6 | 679.4 | 616.5 | 441 | 415.3 | 403 | 392.7 | 446.7 | 423.5 | 436.9 | 400.6
1931 | 1710 | 471.3 | 188.52 | 220.369 | 593.7 | 375.6 | 397.2 | 409.5 | 545 | 73.4 | 17.2 | 126.7 | 6.4 | 266.8 | 8.4 | 402.5 | 413.2 | 702.5 | 627.1 | 517.4 | 591.4 | 783.1 | 814.3 | 698 | 703.3 | 593.1 | 557.8 | 734.7 | 621.5 | 642.6 | 679.5 | 616.9 | 441.1 | 415.8 | 403.4 | 392.8 | 447.1 | 424.5 | 437.7 | 400.8
1932 | 1711 | 471.8 | 188.72 | 220.6028 | 604.2 | 375.4 | 398 | 410.5 | 548 | 73.5 | 17.2 | 126.8 | 7 | 275.3 | 8.2 | 402.7 | 413.4 | 699.4 | 616.2 | 517.8 | 591.9 | 779.5 | 823.3 | 697.7 | 703.4 | 589.9 | 551.4 | 735 | 622.7 | 638.7 | 679.6 | 616.3 | 441.4 | 416.3 | 403.7 | 393 | 447.4 | 425.1 | 438.2 | 401
1933 | 1712 | 472.9 | 189.16 | 221.1171 | 603.1 | 375.7 | 399.4 | 411.4 | 552.2 | 73.4 | 17.2 | 126.8 | 6.3 | 256.7 | 8 | 403 | 413.6 | 713.2 | 630.6 | 518.3 | 592.6 | 776.5 | 838.4 | 701.5 | 703.5 | 590.4 | 557.1 | 735.5 | 622.5 | 645.5 | 679.7 | 617.8 | 441.6 | 416.8 | 404.1 | 393 | 447.7 | 425.4 | 438.7 | 401.2
1934 | 1713 | 473.2 | 189.28 | 221.2574 | 596.2 | 376.3 | 400.9 | 411.6 | 548.4 | 73.3 | 17.2 | 126.8 | 6.3 | 262.4 | 8.2 | 403.3 | 413.7 | 725.2 | 677.9 | 518.7 | 593.3 | 781 | 847.9 | 703.8 | 703.8 | 598.8 | 585.5 | 735.8 | 622.5 | 660.3 | 679.9 | 621.5 | 441.7 | 416.7 | 404.3 | 393.2 | 447.8 | 425.2 | 439 | 401.4
1935 | 1714 | 472.8 | 189.12 | 221.0704 | 594.4 | 377.3 | 401.1 | 411.4 | 544.5 | 73.3 | 17.2 | 126.9 | 5.9 | 262.4 | 8.3 | 403.6 | 413.9 | 726.8 | 694.2 | 519.1 | 594.1 | 788.3 | 850 | 706.3 | 704.1 | 601.7 | 601.1 | 735.4 | 622.8 | 671 | 680 | 623.7 | 441.9 | 416.5 | 404.4 | 393.5 | 448 | 425.2 | 438.9 | 401.6
1936 | 1715 | 473 | 189.2 | 221.1639 | 593.2 | 376.8 | 400.1 | 410.9 | 542.4 | 73.3 | 17.2 | 127.1 | 5.9 | 258.6 | 8.4 | 403.8 | 414.1 | 717.7 | 693.6 | 519.5 | 594.6 | 790.3 | 841.5 | 708.2 | 704.5 | 600.6 | 594 | 735 | 618.5 | 661.5 | 680.2 | 623.2 | 441.9 | 416.1 | 404 | 393.6 | 448.1 | 424.9 | 438.7 | 401.7
1937 | 1716 | 472.2 | 188.88 | 220.7898 | 585.7 | 376.2 | 399.5 | 410.8 | 536.1 | 73.1 | 17.2 | 127.3 | 6.1 | 255.8 | 8.2 | 404.1 | 414.2 | 715.1 | 695.5 | 519.9 | 595.3 | 796.9 | 838.8 | 708.9 | 705.3 | 603.2 | 591.7 | 735.6 | 615.2 | 658.1 | 680.3 | 623.1 | 441.9 | 415.8 | 403.9 | 393.6 | 448.1 | 424.4 | 438.2 | 401.8
1938 | 1717 | 471.8 | 188.72 | 220.6028 | 580.7 | 375.9 | 399.5 | 410 | 537.3 | 73 | 17.2 | 127.5 | 6.7 | 259.4 | 8.4 | 404.4 | 414.4 | 718.7 | 693.6 | 520.3 | 595.9 | 795.8 | 844.5 | 712 | 706 | 607.4 | 590.2 | 736.2 | 620.2 | 658.3 | 680.4 | 623.8 | 441.9 | 415.7 | 404.1 | 393.7 | 448.1 | 424.1 | 437.5 | 401.9
1939 | 1718 | 471.4 | 188.56 | 220.4158 | 581.9 | 375.8 | 399.2 | 409.6 | 541.3 | 72.9 | 17.2 | 127.6 | 6.4 | 257.3 | 8.3 | 404.6 | 414.6 | 720 | 695.2 | 520.8 | 596.4 | 794.9 | 838.5 | 711.5 | 706.5 | 607.6 | 595.4 | 736.6 | 622.2 | 659.6 | 680.5 | 624.7 | 441.8 | 415.5 | 404.1 | 393.9 | 448.2 | 423.8 | 437 | 402
1940 | 1719 | 472.1 | 188.84 | 220.7431 | 586 | 375.6 | 399.1 | 410 | 539.8 | 73.1 | 17.2 | 127.6 | 6.1 | 257.7 | 8 | 404.9 | 414.8 | 717.3 | 700.8 | 521.2 | 597 | 800.5 | 844.1 | 711.9 | 707.3 | 607.8 | 599.2 | 736.9 | 621.7 | 664.9 | 680.7 | 625.8 | 441.8 | 415.5 | 404.2 | 394 | 448.2 | 423.2 | 436.4 | 402.1
1941 | 1720 | 472 | 188.8 | 220.6963 | 589.3 | 376.1 | 398.4 | 409.2 | 537.5 | 73.4 | 17.2 | 127.6 | 6.2 | 256.7 | 7.9 | 405.1 | 414.9 | 714.7 | 709.5 | 521.6 | 597.5 | 793.9 | 840.6 | 713.8 | 708.1 | 609.8 | 597.5 | 737.3 | 620.1 | 659.5 | 680.9 | 625.5 | 441.9 | 415.4 | 404.2 | 394.1 | 448.3 | 422.7 | 436.2 | 402.2
1942 | 1721 | 472.2 | 188.88 | 220.7898 | 585.7 | 375.9 | 398 | 409 | 535 | 73.7 | 17.2 | 127.7 | 6.2 | 257.2 | 7.7 | 405.4 | 415 | 710.4 | 709.9 | 522.1 | 598 | 797 | 832.1 | 715.4 | 709 | 610.7 | 602.3 | 737.7 | 616.2 | 658.8 | 681 | 625.4 | 441.9 | 415.4 | 404.3 | 394.2 | 448.2 | 422.3 | 436.2 | 402.2
1943 | 1722 | 475.1 | 190.04 | 222.1458 | 585.5 | 375.2 | 397.2 | 408.5 | 531.3 | 73.9 | 17.2 | 127.8 | 6.5 | 258.4 | 7.4 | 405.7 | 415.2 | 702.7 | 713.2 | 522.5 | 598.6 | 802.1 | 807.5 | 713.9 | 709.7 | 614.2 | 604.6 | 738.1 | 611 | 659.7 | 681 | 626.5 | 441.9 | 415.4 | 404.4 | 394.4 | 448.2 | 422 | 435.9 | 402.4
1944 | 1723 | 474.3 | 189.72 | 221.7717 | 585.5 | 374.7 | 397.5 | 408.2 | 528.7 | 74.1 | 17.2 | 127.8 | 6.6 | 258.5 | 7.1 | 405.9 | 415.4 | 697 | 725.3 | 522.9 | 599.1 | 790.4 | 783.3 | 712.5 | 710.6 | 618.9 | 606.7 | 738.4 | 605.7 | 658.6 | 681.1 | 626.5 | 442 | 415.4 | 404.6 | 394.6 | 448.1 | 421.2 | 435.4 | 402.4
1945 | 1724 | 471.6 | 188.64 | 220.5093 | 584.9 | 374.9 | 397.8 | 407.5 | 526.5 | 74.2 | 17.2 | 127.9 | 6.5 | 259.4 | 7.1 | 406.2 | 415.5 | 702.2 | 725.6 | 523.3 | 599.6 | 779.9 | 787.2 | 713.3 | 711.2 | 621.8 | 608.4 | 738.4 | 603.2 | 655.4 | 681.1 | 626.7 | 442 | 415.5 | 404.8 | 394.8 | 447.9 | 420.3 | 434.7 | 402.4
1946 | 1725 | 472.5 | 189 | 220.9301 | 585.3 | 374.8 | 397.6 | 406.4 | 526.2 | 74.2 | 17.2 | 128 | 6 | 261.1 | 7 | 406.5 | 415.7 | 705.6 | 726.9 | 523.7 | 600.2 | 779 | 800.8 | 713 | 711.6 | 626 | 605.1 | 738.6 | 606.5 | 655.8 | 681.2 | 626.8 | 442.2 | 415.9 | 405.3 | 394.9 | 447.8 | 419.8 | 434 | 402.5
1947 | 1726 | 472.4 | 188.96 | 220.8834 | 586.7 | 374.8 | 397.2 | 405.9 | 527.1 | 74.2 | 17.2 | 128.1 | 5.6 | 261.2 | 6.7 | 406.7 | 415.9 | 703.3 | 730.1 | 524.1 | 600.8 | 779.1 | 806.5 | 714.4 | 712.4 | 625.4 | 608.3 | 738.9 | 603.8 | 658.7 | 681.4 | 627.4 | 442.3 | 416.2 | 406 | 395.1 | 447.6 | 419.4 | 433.6 | 402.6
1948 | 1727 | 473.3 | 189.32 | 221.3042 | 588 | 375 | 397.3 | 405.4 | 524.7 | 74.2 | 17.2 | 128.3 | 5.3 | 261.4 | 6.5 | 407 | 416 | 696 | 734.4 | 524.5 | 601.3 | 771.5 | 803.1 | 713.6 | 713.3 | 626 | 608.8 | 739 | 602.1 | 661 | 681.4 | 628.5 | 442.5 | 416.5 | 406.5 | 395.4 | 447.5 | 419 | 433.2 | 402.6
1949 | 1728 | 473.7 | 189.48 | 221.4912 | 586.4 | 375.2 | 397.2 | 404.5 | 527.4 | 74.3 | 17.2 | 128.4 | 6.1 | 254.3 | 6.3 | 407.3 | 416.1 | 696.4 | 717 | 524.9 | 601.9 | 751.4 | 774.9 | 709.9 | 714.3 | 627.8 | 601.5 | 739.2 | 596.8 | 653.2 | 681.4 | 627.1 | 442.7 | 416.5 | 406.7 | 395.7 | 447.5 | 418.8 | 433.2 | 402.7
1950 | 1729 | 473.9 | 189.56 | 221.5847 | 590.7 | 374.8 | 397.3 | 403.9 | 526.2 | 74.2 | 17.2 | 128.4 | 5.7 | 258.9 | 6.4 | 407.5 | 416.3 | 698.1 | 709.6 | 525.3 | 602.3 | 743.8 | 760.2 | 707.7 | 715.4 | 621.2 | 595.2 | 739.3 | 590.3 | 642.6 | 681.5 | 625.7 | 442.8 | 416.3 | 406.6 | 395.8 | 447.4 | 418.7 | 433 | 402.8
1951 | 1730 | 473.7 | 189.48 | 221.4912 | 589.8 | 374.2 | 397.5 | 403.8 | 524.2 | 74.2 | 17.1 | 128.4 | 5.3 | 259 | 6.8 | 407.8 | 416.4 | 688.5 | 705.3 | 525.7 | 602.8 | 748.6 | 741.7 | 706.4 | 716.1 | 619.3 | 591.1 | 739.6 | 586.8 | 636.6 | 681.5 | 624.7 | 442.8 | 416.1 | 406.6 | 395.8 | 447.2 | 418.4 | 432.8 | 402.8
1952 | 1731 | 473.5 | 189.4 | 221.3977 | 591.4 | 374.2 | 397.4 | 403.3 | 524.8 | 74.2 | 17.1 | 128.5 | 5.8 | 261.5 | 7.3 | 408 | 416.6 | 694 | 707.5 | 526.2 | 603.3 | 747.4 | 748.4 | 708.3 | 716.8 | 624 | 599.1 | 739.9 | 584 | 635.3 | 681.8 | 625.1 | 442.9 | 416 | 406.9 | 396.1 | 447 | 417.9 | 432.4 | 402.8
1953 | 1732 | 473.5 | 189.4 | 221.3977 | 588.6 | 373.6 | 397.4 | 402.9 | 525.2 | 74.3 | 17.1 | 128.6 | 6.5 | 266.1 | 7.6 | 408.2 | 416.7 | 694.4 | 722.8 | 526.6 | 603.7 | 747.9 | 762.6 | 711.3 | 717.6 | 627.8 | 618.8 | 739.9 | 582.8 | 638.9 | 681.7 | 626.1 | 443.1 | 416.1 | 407.4 | 396.5 | 446.8 | 417.6 | 431.9 | 402.8
1954 | 1733 | 473.4 | 189.36 | 221.3509 | 587.6 | 373.4 | 398 | 401.8 | 530.5 | 74.2 | 17.1 | 128.8 | 6.3 | 263.4 | 7.6 | 408.5 | 416.8 | 691.3 | 739.7 | 527.1 | 604.3 | 739.8 | 756.8 | 710 | 718.6 | 632.2 | 630.6 | 739.6 | 581.7 | 640 | 681.5 | 627.2 | 443.4 | 416.3 | 408.1 | 396.7 | 446.6 | 417.2 | 431.5 | 402.8
1955 | 1734 | 474.5 | 189.8 | 221.8653 | 588.3 | 373.2 | 398.9 | 400.9 | 534.7 | 74.3 | 17.1 | 128.9 | 6.5 | 262.4 | 7.7 | 408.7 | 416.9 | 687.9 | 742 | 527.6 | 604.7 | 729.4 | 756.5 | 709.5 | 719.4 | 637.5 | 628.8 | 739.3 | 580.6 | 635.4 | 681.5 | 626.3 | 443.7 | 417 | 408.6 | 397 | 446.4 | 416.8 | 431.1 | 402.9
1956 | 1735 | 472.8 | 189.12 | 221.0704 | 581.4 | 372.7 | 399 | 400.9 | 536.5 | 74.2 | 17.1 | 129 | 6.2 | 264.1 | 7.9 | 408.9 | 417.1 | 684.7 | 746.3 | 528.1 | 605.2 | 724.8 | 747.8 | 708.1 | 720.3 | 643.6 | 634 | 739.6 | 581.1 | 634.4 | 681.6 | 626.6 | 444 | 417.4 | 409.1 | 397 | 446.2 | 416.7 | 431.1 | 402.9
1957 | 1736 | 473.6 | 189.44 | 221.4444 | 583.4 | 372.1 | 398.8 | 401.1 | 534.4 | 74.2 | 17.1 | 129.2 | 6 | 261.7 | 7.6 | 409.2 | 417.2 | 688.7 | 749.8 | 528.6 | 605.8 | 729.1 | 756.4 | 709.3 | 720.8 | 645.1 | 643.5 | 739.7 | 584.1 | 644.2 | 681.8 | 628.7 | 444.4 | 417.7 | 409.3 | 397.1 | 446 | 416.5 | 431 | 402.9
1958 | 1737 | 473.2 | 189.28 | 221.2574 | 583.9 | 371.8 | 399.1 | 401.2 | 529.6 | 74.3 | 17.1 | 129.2 | 6 | 261.2 | 7.5 | 409.4 | 417.4 | 698.5 | 748.1 | 529.1 | 606.4 | 735.5 | 771.6 | 711.9 | 721.5 | 643.2 | 648.9 | 739.1 | 589.4 | 654.6 | 681.7 | 630.8 | 444.6 | 418.3 | 409.5 | 397.1 | 445.8 | 416.3 | 430.8 | 403
1959 | 1738 | 474.6 | 189.84 | 221.912 | 587.2 | 371.7 | 398.8 | 400.8 | 528.4 | 74.3 | 17.1 | 129.3 | 5.8 | 269.7 | 7.3 | 409.6 | 417.5 | 716.1 | 743.7 | 529.7 | 607.1 | 749.4 | 793.5 | 714.6 | 722.3 | 639.8 | 654.4 | 738.8 | 596.8 | 664.1 | 681.7 | 632.9 | 444.9 | 418.7 | 409.7 | 397.1 | 445.6 | 416.2 | 430.3 | 403.1
1960 | 1739 | 473.1 | 189.24 | 221.2107 | 594.6 | 371.9 | 398.2 | 400.9 | 533.7 | 74.3 | 17.1 | 129.4 | 6 | 259.6 | 6.9 | 409.8 | 417.6 | 717.5 | 734.9 | 530.3 | 607.7 | 759.8 | 808.9 | 715.8 | 722.9 | 636.6 | 654.5 | 738.9 | 606.2 | 669.1 | 681.7 | 634.4 | 445.2 | 419.1 | 410.2 | 397.1 | 445.7 | 416.4 | 430.1 | 403.1
1961 | 1740 | 472 | 188.8 | 220.6963 | 589.8 | 371.9 | 398.4 | 401.2 | 536.4 | 74.4 | 17.1 | 129.4 | 6.6 | 259.1 | 6.4 | 410.1 | 417.7 | 715.5 | 738 | 530.8 | 608.3 | 760.3 | 822.9 | 718.6 | 723.6 | 632.3 | 653 | 739 | 606.9 | 672.1 | 682 | 634.4 | 445.4 | 419.2 | 410.2 | 397.2 | 445.7 | 416.3 | 430.5 | 403.2
1962 | 1741 | 472.4 | 188.96 | 220.8834 | 588.8 | 372.1 | 399.1 | 401.7 | 535.6 | 74.6 | 17.1 | 129.4 | 6.2 | 261.9 | 6.6 | 410.3 | 417.9 | 721.8 | 744.2 | 531.4 | 609 | 769.6 | 831 | 721.8 | 724.2 | 629.9 | 660.2 | 739.2 | 611.1 | 679.5 | 682.1 | 637 | 445.6 | 419.1 | 410.1 | 397.2 | 445.8 | 416.4 | 431 | 403.3
1963 | 1742 | 471.5 | 188.6 | 220.4625 | 586.2 | 372.3 | 399.3 | 402.2 | 535.3 | 74.8 | 17.1 | 129.4 | 5.7 | 255.4 | 6.8 | 410.5 | 418 | 725.8 | 748.3 | 531.9 | 609.6 | 775.2 | 840.9 | 723.7 | 725 | 627.3 | 662.9 | 739.4 | 614.3 | 689.3 | 682.3 | 639.1 | 445.7 | 419 | 410 | 397.2 | 445.9 | 416.6 | 431.4 | 403.4
1964 | 1743 | 473.2 | 189.28 | 221.2574 | 582.6 | 372.3 | 399.3 | 402.5 | 537.7 | 75 | 17.1 | 129.4 | 5.8 | 247.9 | 6.4 | 410.7 | 418.2 | 732.3 | 752.3 | 532.5 | 610.3 | 779.3 | 837.5 | 725.2 | 726.1 | 624.3 | 670.7 | 739.6 | 618.1 | 700.6 | 682.4 | 642.6 | 445.8 | 418.8 | 409.6 | 397.3 | 446 | 416.9 | 431.5 | 403.5
1965 | 1744 | 473.9 | 189.56 | 221.5847 | 584.1 | 372.2 | 399.5 | 402.5 | 536.1 | 75 | 17.1 | 129.3 | 5.5 | 255.8 | 6.4 | 410.9 | 418.3 | 731.4 | 758.3 | 533.1 | 610.9 | 780.2 | 826.5 | 725.5 | 727 | 622.6 | 671.2 | 739.6 | 616.1 | 703.5 | 682.5 | 644 | 445.8 | 418.7 | 409.4 | 397.4 | 446.1 | 416.8 | 431.6 | 403.5
1966 | 1745 | 475 | 190 | 222.0991 | 586.6 | 372.5 | 399.5 | 402.6 | 532.8 | 75 | 17.1 | 129.4 | 5.8 | 256.3 | 6 | 411.1 | 418.4 | 726.8 | 758.6 | 533.6 | 611.5 | 789 | 821 | 726.3 | 727.7 | 622.8 | 669.9 | 740 | 612.5 | 698.1 | 682.6 | 644.1 | 445.9 | 418.6 | 409.2 | 397.4 | 446 | 416.8 | 431.8 | 403.6
1967 | 1746 | 472.8 | 189.12 | 221.0704 | 588.5 | 372.3 | 399.1 | 402.7 | 531.6 | 75 | 17.1 | 129.5 | 5.7 | 250 | 5.6 | 411.3 | 418.5 | 725.8 | 750.7 | 534.1 | 612 | 789.3 | 811.9 | 725.6 | 728.4 | 622.8 | 674.2 | 740.9 | 612.3 | 704.4 | 682.8 | 646.2 | 445.9 | 418.3 | 409 | 397.4 | 446.1 | 417.1 | 432 | 403.7
1968 | 1747 | 472.6 | 189.04 | 220.9769 | 582 | 372.7 | 399 | 402.1 | 531.7 | 75 | 17.1 | 129.7 | 6 | 238.7 | 5.4 | 411.6 | 418.6 | 725.1 | 739 | 534.6 | 612.5 | 786.2 | 804.5 | 724 | 729 | 621.9 | 669.9 | 741.5 | 609.3 | 695.4 | 683 | 646.1 | 446 | 418.3 | 409.1 | 397.6 | 446.2 | 417.4 | 432.3 | 403.7
1969 | 1748 | 473.4 | 189.36 | 221.3509 | 582.4 | 373.2 | 398.7 | 401.6 | 530.6 | 75 | 17.1 | 129.7 | 5.7 | 244.4 | 4.8 | 411.8 | 418.8 | 719.5 | 726.4 | 535.1 | 613 | 780.5 | 786.6 | 721.5 | 729.6 | 619.5 | 658.7 | 742.1 | 602.2 | 681.5 | 683.1 | 645.1 | 446 | 418.3 | 409.2 | 397.7 | 446.3 | 417.7 | 432.8 | 403.8
1970 | 1749 | 473.1 | 189.24 | 221.2107 | 591.9 | 373.3 | 399.1 | 402.3 | 527.1 | 75 | 17.1 | 129.8 | 6.3 | 249.1 | 4.3 | 412 | 418.9 | 711.6 | 708.4 | 535.6 | 613.5 | 782.4 | 769.5 | 720.6 | 730.4 | 617.3 | 642.8 | 742.9 | 597.2 | 675.3 | 683.2 | 644.2 | 446.1 | 418.3 | 409.3 | 397.8 | 446.3 | 417.9 | 433 | 403.9
1971 | 1750 | 473.4 | 189.36 | 221.3509 | 590.5 | 373.5 | 399.7 | 402 | 523.7 | 75.1 | 17.1 | 129.7 | 6.4 | 258 | 4.8 | 412.2 | 419 | 705.1 | 701.3 | 536.2 | 614 | 769.2 | 751.1 | 719.3 | 730.8 | 617.3 | 630.9 | 743.3 | 592.9 | 661.1 | 683.4 | 642.4 | 446.1 | 418.2 | 409.4 | 398 | 446.3 | 417.6 | 432.9 | 403.9
1972 | 1751 | 472.7 | 189.08 | 221.0236 | 589.1 | 373.5 | 400.2 | 401.1 | 521 | 75.1 | 17.1 | 129.7 | 6.8 | 260.4 | 6 | 412.4 | 419.2 | 701.8 | 699.2 | 536.7 | 614.5 | 764.9 | 756.6 | 718.6 | 731.3 | 619 | 627.1 | 743.7 | 590.8 | 652.1 | 683.4 | 641.8 | 446.2 | 418.1 | 409.5 | 398.2 | 446.3 | 417.4 | 432.9 | 404
1973 | 1752 | 473.2 | 189.28 | 221.2574 | 584.5 | 373.1 | 400 | 400.5 | 520.6 | 75.3 | 17.1 | 129.7 | 6.9 | 253.4 | 7 | 412.6 | 419.3 | 697.8 | 717.6 | 537.3 | 614.9 | 765.9 | 771 | 717.6 | 732 | 624.3 | 626.2 | 744 | 591.1 | 651.4 | 683.6 | 641.7 | 446.2 | 417.9 | 409.5 | 398.4 | 446.3 | 417.5 | 433.1 | 404.1
1974 | 1753 | 473.1 | 189.24 | 221.2107 | 586.2 | 373 | 399.4 | 400 | 520.9 | 75.5 | 17.1 | 129.8 | 6.5 | 257.3 | 8 | 412.8 | 419.4 | 694.2 | 738.4 | 537.9 | 615.4 | 756 | 778.9 | 717.8 | 732.8 | 626 | 637.3 | 743.8 | 589.7 | 646.5 | 683.6 | 640.9 | 446.2 | 417.9 | 409.5 | 398.5 | 446.2 | 417.4 | 433.1 | 404.2
1975 | 1754 | 472.7 | 189.08 | 221.0236 | 588.5 | 373.5 | 398.5 | 399.5 | 523.5 | 75.7 | 17.1 | 129.9 | 6.2 | 250.6 | 8.3 | 413 | 419.6 | 701.1 | 751 | 538.5 | 615.9 | 764.2 | 797.1 | 720.4 | 733.4 | 630.9 | 658.1 | 744 | 589.5 | 655.2 | 683.7 | 642.7 | 446.4 | 418.4 | 410 | 398.7 | 446 | 417 | 432.6 | 404.2
1976 | 1755 | 472.2 | 188.88 | 220.7898 | 599.8 | 373.2 | 397.8 | 398.9 | 524.8 | 75.8 | 17.1 | 130 | 6.9 | 243.7 | 7.6 | 413.2 | 419.7 | 716 | 756.4 | 539.2 | 616.6 | 767.6 | 806.6 | 723.3 | 733.8 | 635.2 | 680.8 | 743.8 | 594.6 | 672 | 683.7 | 646.8 | 446.7 | 419.2 | 410.7 | 399.1 | 445.9 | 416.6 | 432 | 404.2
1977 | 1756 | 472.9 | 189.16 | 221.1171 | 599.5 | 373.9 | 397.9 | 397.8 | 528.8 | 75.9 | 17.1 | 130 | 6.8 | 245 | 7.4 | 413.3 | 419.8 | 715.6 | 760.7 | 539.8 | 617.2 | 765.6 | 788.8 | 721.9 | 734.3 | 636.3 | 690.6 | 743.1 | 595.1 | 669.3 | 683.7 | 647.5 | 447.1 | 419.8 | 411.4 | 399.6 | 445.7 | 416.1 | 431.6 | 404.2
1978 | 1757 | 472 | 188.8 | 220.6963 | 594.6 | 375.1 | 398.6 | 397.3 | 535.3 | 75.9 | 17.1 | 130.1 | 6.1 | 248.6 | 7.7 | 413.6 | 419.9 | 712 | 753.4 | 540.4 | 617.9 | 762.7 | 775.6 | 720.1 | 734.9 | 636.6 | 689 | 742.7 | 593.3 | 663.4 | 683.8 | 647.5 | 447.6 | 420.2 | 411.6 | 399.9 | 445.6 | 415.5 | 431.4 | 404.2
1979 | 1758 | 472.4 | 188.96 | 220.8834 | 591.1 | 375.8 | 400.3 | 397.1 | 546.6 | 75.9 | 17.1 | 130.2 | 6.1 | 251.5 | 6.9 | 413.7 | 420.1 | 709.4 | 745.5 | 541.1 | 618.7 | 754.6 | 769 | 719.3 | 735.3 | 636.5 | 686.8 | 742.8 | 592.2 | 658.3 | 683.9 | 647.3 | 448.1 | 420.4 | 412 | 400 | 445.4 | 415 | 431.3 | 404.2
1980 | 1759 | 472.3 | 188.92 | 220.8366 | 590 | 376 | 402 | 396.9 | 545.8 | 75.9 | 17.1 | 130.2 | 6.6 | 232.8 | 6 | 413.9 | 420.2 | 705.6 | 752.9 | 541.7 | 619.1 | 756.1 | 776.6 | 720.1 | 735.6 | 634.8 | 685.8 | 742.9 | 590.2 | 650.9 | 683.9 | 646.4 | 448.5 | 420.4 | 412.2 | 400.1 | 445.1 | 414.5 | 431.2 | 404.3
1981 | 1760 | 472.3 | 188.92 | 220.8366 | 580.5 | 376.1 | 402.7 | 397.6 | 543.5 | 75.9 | 17.1 | 130.3 | 7.7 | 237.5 | 5.8 | 414.1 | 420.3 | 713.2 | 754.9 | 542.4 | 619.6 | 763.2 | 779.4 | 720.9 | 735.8 | 636.3 | 691.1 | 743 | 590 | 654.8 | 684 | 648 | 448.9 | 420.7 | 412.7 | 400.4 | 444.8 | 414 | 430.7 | 404.3
1982 | 1761 | 472.1 | 188.84 | 220.7431 | 574.7 | 376.2 | 403 | 398.3 | 544.1 | 75.8 | 17 | 130.4 | 7 | 247.5 | 5.6 | 414.3 | 420.5 | 709 | 755.8 | 543.1 | 619.9 | 767.1 | 786.8 | 721.6 | 736.5 | 635.5 | 687.2 | 742.9 | 590.2 | 650.5 | 684 | 647.1 | 449.3 | 421.2 | 413 | 400.6 | 444.6 | 413.7 | 430.1 | 404.3
1983 | 1762 | 472.2 | 188.88 | 220.7898 | 578.7 | 376.6 | 402.8 | 397.5 | 541.3 | 75.8 | 17 | 130.4 | 7 | 242.5 | 5.6 | 414.5 | 420.6 | 709.1 | 752.2 | 543.7 | 620.2 | 759 | 789.4 | 720.6 | 737.1 | 635.9 | 682.5 | 742.8 | 591.3 | 649 | 684 | 646.5 | 449.6 | 421.4 | 413 | 400.6 | 444.5 | 413.6 | 429.6 | 404.3
1984 | 1763 | 472.2 | 188.88 | 220.7898 | 575.5 | 377.1 | 402.8 | 396.6 | 543.1 | 75.8 | 17 | 130.4 | 7.1 | 243 | 6 | 414.7 | 420.8 | 702.5 | 760.2 | 544.4 | 620.6 | 757.1 | 782.1 | 719.2 | 737.7 | 640.5 | 685.7 | 742.6 | 592 | 653 | 684.1 | 647 | 449.9 | 421.5 | 413.5 | 400.8 | 444.3 | 413.6 | 429.1 | 404.3
1985 | 1764 | 472 | 188.8 | 220.6963 | 575 | 377.6 | 403.4 | 396.5 | 548.4 | 75.7 | 17 | 130.6 | 6.6 | 267.4 | 7.1 | 414.9 | 420.9 | 698 | 754.5 | 545 | 621.1 | 758.3 | 760.2 | 716.3 | 738.2 | 644.3 | 682.6 | 742.5 | 591.4 | 648.7 | 684.2 | 646.7 | 450.3 | 422 | 414.1 | 401.1 | 444.1 | 413.5 | 428.5 | 404.3
1986 | 1765 | 471.9 | 188.76 | 220.6496 | 572.5 | 377.6 | 403.6 | 396.7 | 545.8 | 75.6 | 17 | 130.8 | 6.9 | 253.8 | 7.3 | 415.1 | 421 | 698.7 | 753.8 | 545.7 | 621.5 | 759.2 | 736.4 | 713.9 | 738.8 | 649.3 | 684.8 | 742.6 | 588.5 | 645.4 | 684.3 | 646.2 | 450.7 | 422.5 | 414.8 | 401.3 | 443.9 | 413.5 | 428.3 | 404.3
1987 | 1766 | 472.2 | 188.88 | 220.7898 | 574.4 | 377.2 | 403.2 | 396.9 | 542.8 | 75.6 | 17 | 131 | 6.7 | 249.4 | 7.9 | 415.3 | 421.2 | 691.6 | 738.9 | 546.3 | 621.9 | 752 | 719.5 | 712.4 | 739.2 | 646.6 | 675.2 | 742.5 | 588.8 | 641.6 | 684.3 | 645.4 | 451.1 | 423 | 414.9 | 401.4 | 443.5 | 413.5 | 428 | 404.3
1988 | 1767 | 472.1 | 188.84 | 220.7431 | 574.2 | 376.5 | 403.5 | 396.8 | 538.1 | 75.5 | 17 | 131.2 | 6.2 | 244.2 | 8.5 | 415.4 | 421.3 | 688 | 728.7 | 547 | 622.3 | 752.7 | 718.8 | 710.4 | 739.8 | 646.8 | 661.8 | 742.3 | 588.6 | 635.2 | 684.4 | 643.9 | 451.4 | 423.4 | 415.2 | 401.3 | 443.2 | 413.2 | 427.4 | 404.3
1989 | 1768 | 472.3 | 188.92 | 220.8366 | 581.7 | 375.9 | 403.8 | 396 | 536.8 | 75.5 | 17 | 131.5 | 7.1 | 244.8 | 9.7 | 415.6 | 421.4 | 692.6 | 721.4 | 547.6 | 622.7 | 743 | 734.8 | 709.1 | 740.1 | 647.8 | 659.8 | 742.4 | 588.8 | 630.6 | 684.4 | 642.9 | 451.7 | 423.3 | 415.1 | 401.4 | 443 | 412.9 | 426.9 | 404.3
1990 | 1769 | 472.3 | 188.92 | 220.8366 | 579.5 | 375.6 | 404 | 395.6 | 537.1 | 75.5 | 17 | 131.7 | 7.4 | 244.9 | 10.3 | 415.8 | 421.6 | 694.8 | 724.8 | 548.3 | 623.2 | 748.1 | 750 | 710.4 | 740.4 | 647 | 661.6 | 742.2 | 589.4 | 631 | 684.4 | 642.3 | 451.9 | 423.3 | 414.9 | 401.5 | 442.9 | 412.6 | 426.5 | 404.2
1991 | 1770 | 472.2 | 188.88 | 220.7898 | 591.3 | 375.8 | 404 | 395.2 | 534.2 | 75.6 | 17 | 131.9 | 6.8 | 245.2 | 9.7 | 416 | 421.7 | 696.1 | 731 | 549 | 623.6 | 746.7 | 747.8 | 710.6 | 740.8 | 648.9 | 662.6 | 742.2 | 589 | 635.8 | 684.5 | 642.8 | 452.1 | 423.4 | 414.8 | 401.5 | 442.7 | 412.4 | 426.4 | 404.2
1992 | 1771 | 472.3 | 188.92 | 220.8366 | 592.5 | 375.6 | 403.7 | 395.3 | 530.8 | 75.6 | 17 | 132.1 | 6.9 | 246.8 | 8 | 416.2 | 421.9 | 697.6 | 742.7 | 549.7 | 624.1 | 748.5 | 773.3 | 712.5 | 741.2 | 649.4 | 665.9 | 742.2 | 590.2 | 645.3 | 684.6 | 643.6 | 452.2 | 423.4 | 414.6 | 401.5 | 442.7 | 412.5 | 426.6 | 404.2
1993 | 1772 | 472 | 188.8 | 220.6963 | 591.9 | 375.6 | 403.3 | 395.3 | 529.2 | 75.7 | 17 | 132.1 | 6.8 | 248.9 | 7.6 | 416.4 | 422.1 | 705.7 | 745.3 | 550.4 | 624.8 | 754.2 | 799.8 | 715.4 | 741.9 | 644.7 | 668.2 | 742.1 | 596.6 | 654.7 | 684.7 | 645.2 | 452.4 | 423.7 | 414.6 | 401.4 | 442.8 | 412.9 | 426.8 | 404.3
1994 | 1773 | 441.8 | 176.72 | 206.5755 | 587.7 | 376.3 | 403 | 396 | 529.7 | 75.7 | 17 | 132.1 | 5.6 | 245.4 | 8.5 | 416.6 | 422.2 | 703.1 | 723.5 | 551.1 | 625.4 | 765.8 | 805.6 | 716.8 | 742.4 | 641.7 | 659 | 742 | 602.1 | 659.5 | 684.8 | 645.7 | 452.4 | 423.9 | 414.5 | 401.4 | 442.9 | 413.5 | 427.1 | 404.4
1995 | 1774 | 67 | 26.8 | 31.3277 | 587.8 | 376.7 | 402.8 | 396.6 | 532 | 75.8 | 17 | 132.1 | 5.8 | 245.3 | 8.8 | 416.8 | 422.4 | 717.5 | 705.4 | 551.7 | 625.9 | 773.2 | 804.6 | 715.7 | 742.6 | 635.1 | 647.2 | 741.9 | 604 | 658.8 | 684.8 | 645.4 | 452.5 | 424 | 414.3 | 401.4 | 443 | 413.8 | 427.7 | 404.5
1996 | 1775 | -6.8 | 0 | 0 | 589.8 | 376.5 | 402.7 | 397.2 | 529.8 | 75.9 | 17 | 132.1 | 5.8 | 232.8 | 7.3 | 417 | 422.5 | 723.5 | 690.3 | 552.3 | 626.5 | 761.1 | 786.1 | 714 | 742.9 | 629.8 | 639.2 | 742.1 | 599.1 | 648.9 | 685 | 644.1 | 452.6 | 423.9 | 413.9 | 401.2 | 443 | 413.3 | 427.6 | 404.4
1997 | 1776 | -6.8 | 0 | 0 | 588.4 | 376.1 | 402.2 | 397.9 | 519.6 | 75.9 | 17 | 132.2 | 5.8 | 234.9 | 6.5 | 417.2 | 422.7 | 720.9 | 648.8 | 553 | 627.1 | 743.2 | 728.1 | 706 | 742.7 | 619.2 | 622.3 | 742.2 | 592.4 | 629.4 | 685 | 641.1 | 452.6 | 423.5 | 413.2 | 400.8 | 442.8 | 412 | 426.9 | 404.1
1998 | 1777 | -6.8 | 0 | 0 | 581.7 | 375.6 | 400.8 | 396.7 | 509.1 | 75.8 | 17 | 132.1 | 5.5 | 227.2 | 6.4 | 417.4 | 422.9 | 715 | 613.6 | 553.7 | 627.4 | 714.9 | 681.7 | 699.8 | 742 | 610.4 | 609.1 | 742.1 | 582.7 | 611.7 | 684.8 | 638.5 | 452.4 | 422.7 | 411.9 | 400.2 | 442.5 | 410.5 | 425.8 | 403.9
1999 | 1778 | -6.8 | 0 | 0 | 579.1 | 374.6 | 399 | 394.4 | 500.1 | 75.8 | 17 | 132.1 | 5.5 | 218.8 | 6.2 | 417.6 | 423 | 702.8 | 582.3 | 554.3 | 627.7 | 691.5 | 641.6 | 694.1 | 740.9 | 600.5 | 595.7 | 741.8 | 572.3 | 595 | 684.8 | 635.3 | 452.1 | 421.7 | 410.4 | 399.6 | 442.1 | 409.1 | 424.7 | 403.7
2000 | 1779 | -6.8 | 0 | 0 | 582.7 | 373.4 | 396.6 | 391.7 | 493.1 | 75.9 | 17 | 131.9 | 5.8 | 237.8 | 7.3 | 417.8 | 423.1 | 701 | 559.7 | 554.9 | 628 | 676.4 | 608.5 | 688.6 | 739.8 | 590.4 | 584.4 | 741.3 | 563.8 | 581.4 | 684.3 | 632.3 | 451.8 | 420.7 | 408.7 | 399.1 | 441.6 | 407.6 | 423.7 | 403.5
2001 | 1780 | -6.8 | 0 | 0 | 580.9 | 372.1 | 394.2 | 389.7 | 486.4 | 76.1 | 17 | 131.7 | 6 | 252.7 | 8.1 | 418 | 423.2 | 690.5 | 541.1 | 555.5 | 628.3 | 654.4 | 581.9 | 684.1 | 738.5 | 580.6 | 575.9 | 740.8 | 557.1 | 568.5 | 684.1 | 629.9 | 451.4 | 419.7 | 406.8 | 398.5 | 441 | 405.7 | 423 | 403.1
2002 | 1781 | -6.8 | 0 | 0 | 571.7 | 370.6 | 392.2 | 387.7 | 480.2 | 76.3 | 17 | 131.3 | 6.4 | 240.3 | 8.5 | 418.2 | 423.4 | 686.4 | 525.7 | 556.1 | 628.4 | 630.5 | 556.9 | 679.6 | 737.1 | 572.5 | 567.1 | 740.3 | 550.8 | 558.9 | 683.9 | 627.4 | 450.9 | 418.5 | 404.8 | 397.8 | 440.3 | 403.6 | 421.5 | 402.8
2003 | 1782 | -6.8 | 0 | 0 | 567.1 | 369 | 389.7 | 385.5 | 476.4 | 76.2 | 17 | 130.8 | 6.2 | 247.1 | 9.6 | 418.4 | 423.5 | 677.5 | 509 | 556.7 | 628.5 | 614.5 | 535.7 | 675.3 | 735.9 | 565.3 | 561.3 | 739.8 | 546 | 560.8 | 683.7 | 625.3 | 450.3 | 417.3 | 402.8 | 397.2 | 439.5 | 401.4 | 419.7 | 402.5
2004 | 1783 | -6.8 | 0 | 0 | 573.8 | 367.3 | 387.2 | 383.9 | 479.1 | 76.1 | 17 | 130.2 | 6 | 246.1 | 9.9 | 418.6 | 423.7 | 679 | 490.8 | 557.3 | 628.7 | 595.7 | 515.6 | 671.6 | 734.5 | 560.9 | 555.8 | 738.9 | 543.5 | 561 | 683.5 | 623.9 | 449.9 | 415.9 | 401 | 396.8 | 438.8 | 399.5 | 418.2 | 402.1
2005 | 1784 | -6.8 | 0 | 0 | 578.7 | 365.7 | 384.6 | 382.3 | 478.9 | 76 | 17 | 129.6 | 6.2 | 242.4 | 9.6 | 418.7 | 423.9 | 681.1 | 474.2 | 557.8 | 628.9 | 577.4 | 498.4 | 666.5 | 733.1 | 557.5 | 550.9 | 737.9 | 539.1 | 558.1 | 683.4 | 622.3 | 449.3 | 414.7 | 399.1 | 396.4 | 438 | 397.4 | 416.7 | 401.8
2006 | 1785 | -6.8 | 0 | 0 | 570.7 | 364.2 | 382.4 | 380.3 | 476.1 | 75.9 | 17 | 128.9 | 6 | 237.4 | 10 | 418.9 | 424 | 681.3 | 458.5 | 558.4 | 629.1 | 562.7 | 482 | 661.8 | 731.9 | 552.9 | 548.4 | 736.8 | 534.5 | 559.2 | 683.1 | 621.7 | 448.9 | 414 | 397.3 | 396 | 437.1 | 395.6 | 415.3 | 401.5
2007 | 1786 | -6.8 | 0 | 0 | 563.7 | 362.7 | 381 | 379.2 | 471.9 | 75.7 | 17 | 128.3 | 5.8 | 247.1 | 11 | 419.1 | 424.1 | 686.5 | 444.5 | 558.9 | 629.3 | 553.9 | 468.1 | 657.5 | 730.8 | 549.8 | 548.3 | 735.7 | 531 | 561.8 | 682.7 | 620.7 | 448.4 | 412.9 | 395.5 | 395.6 | 436.3 | 394 | 414.5 | 401.2
2008 | 1787 | -6.8 | 0 | 0 | 566 | 361.2 | 379.2 | 378 | 468.3 | 75.6 | 17 | 127.7 | 5.2 | 242.3 | 10.3 | 419.3 | 424.3 | 686.1 | 434.4 | 559.5 | 629.6 | 547.3 | 455.9 | 653.5 | 729.7 | 546 | 542.5 | 734.8 | 527 | 549.3 | 682.3 | 618.6 | 447.8 | 411.7 | 393.8 | 395.2 | 435.5 | 392.5 | 413.5 | 400.9
2009 | 1788 | -6.8 | 0 | 0 | 564.3 | 360 | 377.9 | 376.7 | 466.4 | 75.5 | 17 | 127 | 5.7 | 243.1 | 10.6 | 419.5 | 424.4 | 690.5 | 425.7 | 560 | 629.6 | 533.8 | 446.3 | 650.1 | 728.4 | 540.2 | 538.9 | 734 | 523.5 | 542.8 | 682.1 | 616.8 | 447.3 | 410.7 | 392.2 | 394.9 | 434.6 | 390.9 | 412 | 400.5
2010 | 1789 | -6.8 | 0 | 0 | 565.3 | 358.9 | 376.4 | 375 | 463.4 | 75.4 | 17 | 126.4 | 5.3 | 232.2 | 10.1 | 419.7 | 424.5 | 693.1 | 415.9 | 560.5 | 629.7 | 522.5 | 437.6 | 647.1 | 727.2 | 537 | 537.6 | 733.3 | 520.1 | 542 | 681.8 | 615.2 | 446.8 | 409.7 | 390.7 | 394.5 | 433.8 | 389.4 | 411 | 400.1
2011 | 1790 | -6.8 | 0 | 0 | 561 | 357.8 | 375.7 | 373.3 | 460.6 | 75.3 | 17 | 125.7 | 5.4 | 242.7 | 9.5 | 419.9 | 424.7 | 694.8 | 408.1 | 561 | 629.9 | 513.3 | 428.3 | 644.2 | 726.1 | 535 | 538.5 | 732.6 | 517 | 538.6 | 681.7 | 614.3 | 446.3 | 408.4 | 389.2 | 394.2 | 432.9 | 387.9 | 409.9 | 399.8
2012 | 1791 | -6.8 | 0 | 0 | 550.3 | 356.7 | 374.7 | 372.8 | 457.5 | 75.1 | 17 | 125 | 5.7 | 240.8 | 9.4 | 420 | 424.8 | 694.6 | 401.5 | 561.5 | 630.1 | 502.8 | 419.1 | 640.9 | 725 | 532.1 | 535.1 | 731.9 | 513.3 | 532.2 | 681.3 | 612.6 | 445.9 | 407.3 | 387.8 | 393.8 | 432 | 386.4 | 408.7 | 399.5
2013 | 1792 | -6.8 | 0 | 0 | 549.9 | 355.8 | 373.6 | 371.5 | 455.3 | 75 | 17 | 124.4 | 5.7 | 235.5 | 9.2 | 420.2 | 425 | 700.7 | 394.7 | 561.9 | 630.3 | 493.8 | 411.2 | 637.9 | 724.1 | 528.7 | 537.7 | 731.1 | 511 | 532.5 | 681.1 | 612 | 445.3 | 406.2 | 386.3 | 393.4 | 431.2 | 384.9 | 407.7 | 399.2
2014 | 1793 | -6.8 | 0 | 0 | 548.9 | 355 | 372.4 | 370.4 | 452.5 | 74.9 | 17 | 123.7 | 5.4 | 247.8 | 8.5 | 420.4 | 425.1 | 697.7 | 388.2 | 562.4 | 630.4 | 484.9 | 402.7 | 635.2 | 723.2 | 528 | 540.1 | 730.2 | 509.5 | 531.3 | 680.8 | 611.1 | 444.9 | 405 | 385 | 393 | 430.4 | 383.5 | 406.5 | 398.8
2015 | 1794 | -6.8 | 0 | 0 | 544.2 | 354.1 | 371 | 368.7 | 450.6 | 74.8 | 16.9 | 123.1 | 4.7 | 246.5 | 8.9 | 420.6 | 425.2 | 700.8 | 382.3 | 562.9 | 630.6 | 476.3 | 396.5 | 632 | 722.4 | 526.8 | 541 | 729.4 | 506.4 | 530.9 | 680.4 | 609.4 | 444.4 | 404.1 | 384 | 392.7 | 429.6 | 382.3 | 405.5 | 398.5
2016 | 1795 | -6.8 | 0 | 0 | 540 | 353.2 | 369.6 | 367.1 | 448.1 | 74.7 | 17 | 122.6 | 4.9 | 250.8 | 9.9 | 420.7 | 425.3 | 705.8 | 375.3 | 563.3 | 630.8 | 469.2 | 388.9 | 629.7 | 721.6 | 524.8 | 544.6 | 728.8 | 504 | 537 | 680 | 610 | 443.9 | 403.1 | 383 | 392.3 | 428.8 | 381 | 404.4 | 398.1
2017 | 1796 | -6.8 | 0 | 0 | 536.6 | 352.4 | 368.6 | 365.7 | 445.7 | 74.6 | 17 | 122.1 | 5.6 | 229.6 | 10.1 | 420.9 | 425.5 | 708.8 | 367.9 | 563.8 | 630.8 | 463.7 | 379.8 | 626.1 | 720.8 | 522.1 | 544.5 | 728 | 501 | 533.5 | 679.6 | 608.4 | 443.5 | 402.3 | 382.1 | 392 | 427.9 | 379.9 | 403.5 | 397.8
2018 | 1797 | -6.8 | 0 | 0 | 533.8 | 351.5 | 367.7 | 364.5 | 443.4 | 74.5 | 17 | 121.6 | 5.8 | 231.9 | 9.4 | 421.1 | 425.6 | 700.9 | 360.8 | 564.2 | 630.9 | 458.4 | 371.6 | 622.7 | 719.9 | 519.6 | 539.6 | 727.3 | 499.2 | 527.7 | 679.2 | 606.7 | 443 | 401.6 | 381.2 | 391.6 | 427.2 | 378.8 | 402.7 | 397.5
2019 | 1798 | -6.8 | 0 | 0 | 534.2 | 350.7 | 366.6 | 363.8 | 442.6 | 74.4 | 17 | 121.2 | 5.8 | 232.4 | 8.6 | 421.3 | 425.8 | 702.1 | 355.5 | 564.7 | 631 | 455.6 | 363.6 | 618.3 | 718.9 | 515.4 | 536.6 | 726.6 | 497.2 | 524.1 | 678.9 | 605.5 | 442.6 | 400.8 | 380.3 | 391.3 | 426.4 | 377.8 | 402.1 | 397.2
2020 | 1799 | -6.7 | 0 | 0 | 539.1 | 349.8 | 365.7 | 363 | 441.5 | 74.3 | 17 | 120.8 | 5.5 | 244.8 | 8.1 | 421.4 | 425.9 | 702.2 | 350.5 | 565.1 | 631.1 | 461.5 | 356.5 | 614.6 | 718 | 513.4 | 533.4 | 725.9 | 495.7 | 524.4 | 678.6 | 604.4 | 442.2 | 399.8 | 379.2 | 390.9 | 425.6 | 376.8 | 401.4 | 396.8
2021 | 1800 | -6.8 | 0 | 0 | 533.1 | 349 | 364.9 | 362.1 | 441 | 74.2 | 16.9 | 120.3 | 5.9 | 256.5 | 7.7 | 421.6 | 426.1 | 704.5 | 345.7 | 565.5 | 631.2 | 461.4 | 351.2 | 611.5 | 717.1 | 513.8 | 534.6 | 725.4 | 494.3 | 528.2 | 678.3 | 604 | 441.8 | 398.8 | 378.2 | 390.4 | 424.8 | 375.8 | 400.9 | 396.5
2022 | 1801 | -6.7 | 0 | 0 | 524.2 | 348.3 | 363.9 | 361 | 440.7 | 74.2 | 16.9 | 119.8 | 5.8 | 255 | 7.5 | 421.8 | 426.3 | 706.3 | 340.2 | 566 | 631.4 | 463.2 | 345.4 | 607.5 | 716.3 | 513.6 | 536.6 | 724.7 | 492.4 | 526.3 | 678 | 603.4 | 441.4 | 397.9 | 377.1 | 390 | 424.1 | 374.7 | 400.2 | 396.2
2023 | 1802 | -6.7 | 0 | 0 | 518.6 | 347.6 | 363 | 360.4 | 439.6 | 74.3 | 16.9 | 119.4 | 5.7 | 251.7 | 6.9 | 421.9 | 426.5 | 706.1 | 335.1 | 566.4 | 631.7 | 462 | 338.9 | 604.2 | 715.5 | 512.1 | 534.6 | 723.9 | 490.2 | 522.1 | 677.6 | 602.1 | 441 | 396.9 | 376 | 389.6 | 423.4 | 373.7 | 399.5 | 395.8
2024 | 1803 | -6.7 | 0 | 0 | 516.1 | 346.8 | 362.4 | 360.5 | 439.1 | 74.3 | 16.9 | 119 | 5.6 | 240.9 | 6.3 | 422.1 | 426.6 | 707.5 | 331.1 | 566.8 | 631.9 | 458.7 | 333.8 | 601.2 | 714.8 | 509.9 | 535 | 723.2 | 487.1 | 515.8 | 677.2 | 601.9 | 440.6 | 395.9 | 375 | 389.2 | 422.6 | 372.7 | 398.6 | 395.4
2025 | 1804 | -6.7 | 0 | 0 | 518.8 | 346 | 361.6 | 360.5 | 437.7 | 74.3 | 16.9 | 118.6 | 6 | 260.4 | 6.3 | 422.2 | 426.7 | 702.2 | 325.6 | 567.1 | 632 | 455.2 | 329.9 | 597.8 | 714.1 | 507.9 | 529 | 722.4 | 484.6 | 509 | 676.7 | 599.6 | 440.2 | 394.9 | 374 | 388.8 | 421.8 | 371.9 | 397.8 | 395.1
2026 | 1805 | -6.7 | 0 | 0 | 517.4 | 345.4 | 360.9 | 359.6 | 436.2 | 74.2 | 16.9 | 118.2 | 5.9 | 258.5 | 6.6 | 422.4 | 427 | 696.2 | 322.6 | 567.5 | 632.1 | 450.9 | 326.4 | 595.6 | 713.4 | 505 | 526.3 | 721.7 | 481.5 | 506.5 | 676.2 | 597.4 | 439.8 | 394 | 373.1 | 388.4 | 421.1 | 371 | 397 | 394.8
2027 | 1806 | -6.7 | 0 | 0 | 515.8 | 344.8 | 360.1 | 358.4 | 435.3 | 74.1 | 16.9 | 117.8 | 6 | 263.6 | 6.2 | 422.6 | 427.2 | 690.5 | 319.7 | 567.9 | 632.2 | 446.5 | 322.6 | 593.5 | 712.7 | 502.1 | 526.1 | 721 | 479 | 509.8 | 675.7 | 596.7 | 439.4 | 393.1 | 372.2 | 388 | 420.5 | 370.3 | 396.3 | 394.5
2028 | 1807 | -6.7 | 0 | 0 | 519.2 | 344.2 | 359.2 | 357.2 | 434.8 | 74 | 16.9 | 117.4 | 5.8 | 268.8 | 5.9 | 422.7 | 427.4 | 688.9 | 316.6 | 568.2 | 632.5 | 444.4 | 318.9 | 591.3 | 712.1 | 500.7 | 524.9 | 720.4 | 479.8 | 510.5 | 675.4 | 595.8 | 439 | 392.5 | 371.4 | 387.7 | 419.7 | 369.6 | 395.6 | 394.2
2029 | 1808 | -6.7 | 0 | 0 | 517.6 | 343.3 | 358.4 | 356.5 | 434 | 73.9 | 16.9 | 117.1 | 5.7 | 247.3 | 6.2 | 422.9 | 427.6 | 682.5 | 313.1 | 568.6 | 632.8 | 447.5 | 314.8 | 589.8 | 711.3 | 502 | 525.1 | 719.9 | 478.3 | 509.8 | 675 | 594.6 | 438.6 | 391.7 | 370.5 | 387.3 | 419 | 368.7 | 394.9 | 393.8
2030 | 1809 | -6.7 | 0 | 0 | 515.3 | 342.6 | 357.8 | 356.4 | 433.4 | 73.8 | 16.9 | 116.8 | 5.4 | 238.1 | 6.6 | 423 | 427.7 | 678.1 | 309.9 | 568.9 | 633 | 465.2 | 309.1 | 588.5 | 710.4 | 502.2 | 530.7 | 719.4 | 477.2 | 513.8 | 674.7 | 594 | 438.3 | 390.8 | 369.8 | 386.9 | 418.4 | 367.9 | 394.1 | 393.4
2031 | 1810 | -6.7 | 0 | 0 | 511.4 | 342 | 357.2 | 355.7 | 432.7 | 73.7 | 16.9 | 116.4 | 4.9 | 240.1 | 7.4 | 423.2 | 428 | 678.8 | 306.5 | 569.2 | 633.1 | 465.3 | 303.6 | 587.1 | 709.6 | 504.9 | 527.9 | 719 | 476.6 | 509 | 674.3 | 593.4 | 437.9 | 390.2 | 369 | 386.5 | 417.7 | 367.2 | 393.6 | 393.1
2032 | 1811 | -6.7 | 0 | 0 | 507.3 | 341.5 | 356.7 | 354.7 | 433.8 | 73.6 | 16.9 | 116.1 | 4.6 | 249.6 | 7.8 | 423.3 | 428.2 | 680.1 | 302.5 | 569.5 | 633.3 | 462.7 | 299.1 | 584.9 | 708.9 | 505.5 | 525.7 | 718.5 | 476.8 | 509.2 | 674 | 592.4 | 437.5 | 389.5 | 368.2 | 386.1 | 417 | 366.4 | 393.4 | 392.7
2033 | 1812 | -6.7 | 0 | 0 | 504.9 | 341.2 | 356.2 | 354.5 | 433.4 | 73.5 | 16.9 | 115.8 | 5.1 | 242.7 | 9.1 | 423.5 | 428.4 | 678.6 | 299.5 | 569.9 | 633.4 | 460.3 | 295.5 | 582.9 | 708.3 | 504.2 | 522 | 717.9 | 476.2 | 506.6 | 673.6 | 590.5 | 437.2 | 388.6 | 367.4 | 385.6 | 416.3 | 365.9 | 392.7 | 392.4
2034 | 1813 | -6.7 | 0 | 0 | 509.3 | 340.8 | 356 | 353.5 | 433.2 | 73.4 | 16.9 | 115.6 | 5 | 251.6 | 9 | 423.6 | 428.6 | 674.9 | 296.9 | 570.2 | 633.5 | 454.8 | 292.1 | 581.2 | 708 | 501.3 | 522.3 | 717.3 | 475.3 | 501.8 | 673.3 | 589.2 | 436.8 | 387.7 | 366.5 | 385.2 | 415.6 | 365.2 | 392.6 | 392.1
2035 | 1814 | -6.7 | 0 | 0 | 513.7 | 340.3 | 355.5 | 352.3 | 432.6 | 73.4 | 16.9 | 115.3 | 5 | 247.8 | 8.6 | 423.8 | 428.8 | 672 | 294.4 | 570.5 | 633.5 | 449.6 | 289.7 | 579.1 | 707.4 | 501.2 | 518.3 | 716.6 | 473.6 | 500.4 | 673 | 587.9 | 436.4 | 386.8 | 365.6 | 384.8 | 415 | 364.4 | 391.9 | 391.7
2036 | 1815 | -6.7 | 0 | 0 | 515.3 | 339.9 | 354.6 | 352.1 | 431.5 | 73.4 | 16.9 | 115 | 5.4 | 247 | 7.9 | 423.9 | 429 | 664 | 292.1 | 570.8 | 633.5 | 444.6 | 288.2 | 577.1 | 706.6 | 498.7 | 515.1 | 715.8 | 473.1 | 495.2 | 672.6 | 586.3 | 436 | 386.3 | 365.1 | 384.5 | 414.3 | 363.6 | 391.3 | 391.3
2037 | 1816 | -6.7 | 0 | 0 | 511.9 | 339.8 | 353.5 | 351.7 | 431.3 | 73.3 | 16.9 | 114.7 | 5.7 | 258.2 | 7.7 | 424.1 | 429.2 | 663.8 | 289.4 | 571.1 | 633.5 | 442.6 | 285.9 | 575.2 | 705.9 | 496.1 | 513.7 | 715.2 | 472.3 | 494.1 | 672.3 | 585 | 435.6 | 385.5 | 364.6 | 384.1 | 413.7 | 362.9 | 390.9 | 390.9
2038 | 1817 | -6.7 | 0 | 0 | 506.1 | 339.9 | 353.1 | 350.9 | 430.2 | 73.3 | 16.9 | 114.4 | 5.3 | 240.6 | 7.4 | 424.2 | 429.3 | 667.7 | 286.7 | 571.5 | 633.4 | 443.1 | 282.6 | 573.3 | 705.4 | 495.6 | 513.5 | 714.6 | 469.9 | 490.1 | 671.9 | 583.7 | 435.2 | 384.9 | 363.9 | 383.7 | 413.1 | 362.2 | 390.4 | 390.6
2039 | 1818 | -6.7 | 0 | 0 | 499.4 | 339.7 | 352.9 | 350.8 | 428.8 | 73.2 | 16.9 | 114 | 5.5 | 249.4 | 7.4 | 424.4 | 429.5 | 661.8 | 284.4 | 571.7 | 633.5 | 440.1 | 279.8 | 571.6 | 704.8 | 495.7 | 511.9 | 714 | 468 | 487.3 | 671.4 | 582.6 | 434.8 | 384.2 | 363.4 | 383.3 | 412.4 | 361.6 | 389.7 | 390.3
2040 | 1819 | -6.7 | 0 | 0 | 492.9 | 339.6 | 352.3 | 350 | 427.9 | 73.1 | 16.9 | 113.7 | 5.3 | 249 | 7.6 | 424.5 | 429.7 | 654.8 | 282.2 | 572 | 633.5 | 437.1 | 277.2 | 570.2 | 704.2 | 494.9 | 511.6 | 713.1 | 466.6 | 490.6 | 671.1 | 582.1 | 434.4 | 383.5 | 362.8 | 382.9 | 411.9 | 361.1 | 389.3 | 389.9
2041 | 1820 | -6.7 | 0 | 0 | 488 | 339.7 | 351.6 | 349.1 | 427.6 | 72.8 | 16.9 | 113.3 | 5.3 | 245 | 8.1 | 424.7 | 429.9 | 647.1 | 280.5 | 572.3 | 633.4 | 433.4 | 275.2 | 569.8 | 703.6 | 493.9 | 511.2 | 712.5 | 466.4 | 496.8 | 670.6 | 581.4 | 434 | 382.9 | 362.1 | 382.5 | 411.3 | 360.6 | 388.7 | 389.6
2042 | 1821 | -6.7 | 0 | 0 | 489.1 | 339.2 | 351.1 | 348.6 | 427.4 | 72.6 | 16.9 | 113.1 | 5.3 | 267.2 | 8 | 424.9 | 430 | 635 | 279.1 | 572.6 | 633.5 | 432.1 | 273.9 | 568.3 | 702.9 | 491.6 | 513.7 | 711.9 | 466.2 | 499.2 | 670.3 | 581.7 | 433.6 | 382.4 | 361.6 | 382.1 | 410.7 | 360 | 388.2 | 389.2
2043 | 1822 | -6.7 | 0 | 0 | 494.2 | 338.7 | 350.4 | 347.8 | 425.9 | 72.4 | 16.9 | 112.8 | 4.7 | 278.1 | 7 | 425 | 430.2 | 633.2 | 277.4 | 572.9 | 633.5 | 429.8 | 272.4 | 567.3 | 702.1 | 488.7 | 512.6 | 711.3 | 465.5 | 495.4 | 669.8 | 580.5 | 433.3 | 381.8 | 361 | 381.7 | 410.1 | 359.4 | 387.7 | 388.9
2044 | 1823 | -6.7 | 0 | 0 | 498.8 | 338.2 | 349.7 | 347.3 | 424.4 | 72.3 | 16.9 | 112.5 | 5 | 245.9 | 7.2 | 425.2 | 430.3 | 639.6 | 275.8 | 573.2 | 633.5 | 428 | 270.9 | 565.1 | 701.3 | 486 | 512.9 | 710.5 | 464 | 491.3 | 669.3 | 578.9 | 432.9 | 381 | 360.3 | 381.3 | 409.6 | 358.8 | 386.7 | 388.5
2045 | 1824 | -6.7 | 0 | 0 | 503.5 | 337.7 | 349.1 | 346.9 | 423.1 | 72.1 | 16.9 | 112.2 | 5.2 | 238 | 8.4 | 425.3 | 430.5 | 649 | 274.2 | 573.4 | 633.7 | 429.1 | 269.1 | 562.8 | 700.7 | 486.6 | 512.7 | 709.9 | 463.5 | 491.5 | 669 | 578.2 | 432.5 | 380.3 | 359.6 | 380.8 | 409 | 358.2 | 385.9 | 388.2
2046 | 1825 | -6.7 | 0 | 0 | 504.6 | 337.3 | 348.7 | 346.7 | 423.2 | 71.9 | 16.9 | 111.8 | 5.8 | 234.4 | 8.7 | 425.5 | 430.6 | 649 | 273 | 573.6 | 633.7 | 427.1 | 266 | 560.6 | 700.1 | 487.2 | 511.1 | 709.4 | 461.6 | 486.2 | 668.6 | 576.9 | 432.2 | 379.9 | 359 | 380.5 | 408.4 | 358.3 | 385.6 | 387.8
2047 | 1826 | -6.7 | 0 | 0 | 500 | 336.9 | 348.2 | 346.5 | 423.3 | 71.6 | 16.9 | 111.5 | 5.7 | 244.4 | 9.1 | 425.6 | 430.8 | 642.4 | 271.8 | 573.9 | 633.7 | 427.5 | 263.4 | 559.6 | 699.7 | 485.9 | 510.5 | 708.7 | 460.1 | 482.8 | 668.1 | 575.9 | 431.7 | 379.2 | 358.3 | 380.1 | 407.9 | 358 | 385.4 | 387.5
2048 | 1827 | -6.7 | 0 | 0 | 496.3 | 336.6 | 347.8 | 346.8 | 423.3 | 71.5 | 16.9 | 111.2 | 5.8 | 243 | 8.6 | 425.8 | 431 | 646.1 | 270.6 | 574.1 | 633.7 | 426.9 | 261.8 | 557.9 | 699.3 | 484.8 | 509.8 | 708.1 | 458.7 | 485 | 667.7 | 574.7 | 431.4 | 378.4 | 357.6 | 379.7 | 407.2 | 357.5 | 385 | 387.1
2049 | 1828 | -6.7 | 0 | 0 | 495.7 | 336.4 | 347.5 | 346 | 423.5 | 71.4 | 16.9 | 111 | 5.3 | 245.3 | 8 | 425.9 | 431.2 | 655.8 | 268.8 | 574.3 | 633.7 | 426.4 | 260.5 | 555.9 | 699 | 484.3 | 511.8 | 707.4 | 457.4 | 481.9 | 667.3 | 573.9 | 431 | 377.6 | 357 | 379.3 | 406.6 | 356.8 | 383.9 | 386.7
2050 | 1829 | -6.7 | 0 | 0 | 491.7 | 336.2 | 347 | 345.1 | 424.4 | 71.4 | 16.9 | 110.7 | 5.4 | 248.2 | 6.9 | 426.1 | 431.3 | 658.6 | 267.5 | 574.5 | 633.7 | 424.8 | 258.8 | 554.2 | 698.7 | 483.2 | 511.7 | 706.7 | 456.1 | 479.2 | 666.9 | 573 | 430.6 | 377 | 356.3 | 378.9 | 406.1 | 356.1 | 383.3 | 386.4
2051 | 1830 | -6.7 | 0 | 0 | 490 | 336 | 346.5 | 344.9 | 424.4 | 71.1 | 16.9 | 110.5 | 5.3 | 262.8 | 6.2 | 426.3 | 431.5 | 652.9 | 265.5 | 574.7 | 634 | 424.2 | 256.9 | 552.4 | 698.2 | 482.4 | 510 | 705.9 | 454.7 | 476.6 | 666.4 | 572.7 | 430.2 | 376.4 | 355.7 | 378.5 | 405.6 | 355.6 | 382.6 | 386
2052 | 1831 | -6.7 | 0 | 0 | 490.9 | 335.8 | 346 | 344.5 | 423.8 | 70.8 | 16.9 | 110.2 | 5 | 252.6 | 6.5 | 426.4 | 431.7 | 652.3 | 263.7 | 574.9 | 634.1 | 422 | 254.9 | 551 | 697.7 | 481.1 | 510.4 | 705.2 | 454.7 | 476.4 | 666 | 571.9 | 429.8 | 375.9 | 355.3 | 378 | 405.1 | 355.1 | 382.1 | 385.6
2053 | 1832 | -6.7 | 0 | 0 | 502.4 | 335.5 | 345.4 | 344.1 | 422.7 | 70.6 | 17 | 110 | 4.9 | 239.4 | 8.3 | 426.6 | 431.8 | 661.3 | 261.1 | 575.1 | 634.1 | 419.8 | 252.6 | 549.3 | 697.3 | 481.5 | 514.7 | 704.7 | 453.4 | 476.7 | 665.5 | 571.2 | 429.4 | 375.6 | 355.2 | 377.6 | 404.5 | 354.8 | 381.7 | 385.3
2054 | 1833 | -6.7 | 0 | 0 | 502.7 | 335.1 | 344.8 | 343.2 | 421.3 | 70.5 | 17 | 109.7 | 5.3 | 238.6 | 9 | 426.7 | 432 | 666.3 | 259.2 | 575.2 | 634.2 | 419.1 | 250.3 | 547 | 697.1 | 482.6 | 518 | 704 | 452.6 | 477.3 | 665.1 | 570.8 | 429 | 375.2 | 355.2 | 377.3 | 404 | 354.4 | 381.1 | 385
2055 | 1834 | -6.7 | 0 | 0 | 502.2 | 334.7 | 344.4 | 342.6 | 420.5 | 70.3 | 17 | 109.5 | 5.5 | 240 | 9.4 | 426.9 | 432.1 | 668.6 | 258.4 | 575.4 | 634 | 418.3 | 248.6 | 545 | 696.8 | 481.4 | 516 | 703.2 | 452.4 | 484.2 | 664.6 | 569.9 | 428.7 | 374.5 | 354.7 | 376.9 | 403.4 | 353.9 | 380.7 | 384.6
2056 | 1835 | -6.7 | 0 | 0 | 507.2 | 334.4 | 344.2 | 341.9 | 418.6 | 70.1 | 16.9 | 109.4 | 5.6 | 244.6 | 9.1 | 427 | 432.3 | 666.8 | 256.4 | 575.6 | 634 | 415.8 | 246.5 | 543.7 | 696.6 | 481.1 | 514.8 | 702.4 | 452.9 | 484.1 | 664.2 | 569.3 | 428.3 | 373.8 | 354.1 | 376.5 | 402.9 | 353.3 | 380.2 | 384.3
2057 | 1836 | -6.7 | 0 | 0 | 505.6 | 334 | 344 | 341.4 | 420 | 69.9 | 16.9 | 109.2 | 5.7 | 235.7 | 8.8 | 427.2 | 432.5 | 663.3 | 254.8 | 575.9 | 633.9 | 413.1 | 244.8 | 542.3 | 696.6 | 480.6 | 514.2 | 701.8 | 453.3 | 480.7 | 663.8 | 569.1 | 427.9 | 373.2 | 353.6 | 376.2 | 402.4 | 353.4 | 380 | 384
2058 | 1837 | -6.7 | 0 | 0 | 503.5 | 333.4 | 343.9 | 341 | 419.4 | 69.8 | 16.9 | 109 | 5.6 | 247.6 | 8.2 | 427.3 | 432.6 | 665.5 | 252.7 | 576.1 | 633.8 | 410 | 244.2 | 539.9 | 696.3 | 478.9 | 515.1 | 701.2 | 453.2 | 479.7 | 663.5 | 568.8 | 427.6 | 372.6 | 353 | 375.8 | 401.9 | 352.9 | 379.6 | 383.6
2059 | 1838 | -6.7 | 0 | 0 | 504.4 | 332.8 | 343.3 | 340.8 | 417.8 | 69.6 | 16.9 | 108.7 | 5.7 | 258.7 | 7.4 | 427.5 | 432.7 | 670.8 | 250.4 | 576.3 | 633.7 | 410.9 | 243.7 | 537.6 | 696 | 476.6 | 512.8 | 700.6 | 453.4 | 479.8 | 663.1 | 567.9 | 427.2 | 372.1 | 352.3 | 375.4 | 401.4 | 352.3 | 379 | 383.3
2060 | 1839 | -6.7 | 0 | 0 | 510.4 | 332.4 | 342.8 | 340.2 | 415.4 | 69.3 | 17 | 108.4 | 5.8 | 274.7 | 6.7 | 427.6 | 432.8 | 676.7 | 248.9 | 576.5 | 633.7 | 412.4 | 242.1 | 535.7 | 695.7 | 473.5 | 510.6 | 700.1 | 452.9 | 482.8 | 662.7 | 566.7 | 426.9 | 371.7 | 352.1 | 375 | 400.9 | 351.6 | 378.2 | 382.9
2061 | 1840 | -6.7 | 0 | 0 | 507 | 332.2 | 342.3 | 339.9 | 413.7 | 68.9 | 16.9 | 108.2 | 6 | 236.5 | 7.4 | 427.7 | 432.9 | 682.3 | 248 | 576.6 | 633.6 | 411.9 | 241.4 | 533.4 | 695.3 | 471.8 | 508.8 | 699.6 | 452.8 | 482.9 | 662.3 | 566 | 426.6 | 371.4 | 351.9 | 374.7 | 400.3 | 351.1 | 378.3 | 382.6
2062 | 1841 | -6.7 | 0 | 0 | 502.9 | 332 | 342.2 | 339.7 | 412.5 | 68.6 | 16.9 | 107.9 | 6.2 | 255.8 | 6.8 | 427.9 | 433 | 677.6 | 246.9 | 576.9 | 633.5 | 412.3 | 241 | 531.3 | 694.9 | 469 | 507.7 | 699 | 452.8 | 485.8 | 661.8 | 565.4 | 426.2 | 371 | 351.6 | 374.3 | 399.9 | 350.6 | 378 | 382.2
2063 | 1842 | -6.7 | 0 | 0 | 498.7 | 331.8 | 342.5 | 339 | 412.7 | 68.3 | 16.9 | 107.8 | 5.8 | 255.4 | 6.8 | 428 | 433.1 | 681.6 | 245.5 | 577.1 | 633.4 | 410.6 | 239.7 | 529.6 | 694.5 | 468.4 | 509.1 | 698.5 | 453.6 | 496.4 | 661.4 | 565.7 | 425.9 | 370.4 | 351 | 373.9 | 399.4 | 350.1 | 377.6 | 381.9
2064 | 1843 | -6.7 | 0 | 0 | 495.4 | 331.6 | 342.3 | 338.6 | 412.6 | 68 | 16.9 | 107.6 | 5.9 | 259.5 | 6.9 | 428.2 | 433.2 | 674.2 | 244.2 | 577.3 | 633.4 | 411.9 | 237.7 | 528.5 | 694.2 | 469.1 | 512.8 | 697.9 | 453.9 | 496.7 | 661.1 | 565.8 | 425.6 | 369.7 | 350.5 | 373.5 | 398.9 | 349.6 | 377 | 381.6
2065 | 1844 | -6.7 | 0 | 0 | 494.1 | 331.4 | 341.8 | 338.5 | 412.4 | 67.8 | 16.9 | 107.4 | 6.6 | 266.6 | 7.4 | 428.3 | 433.2 | 665.2 | 242.8 | 577.4 | 633.3 | 412.9 | 236.2 | 526.9 | 693.8 | 470.4 | 514.2 | 697.4 | 453.1 | 498.2 | 660.6 | 565.6 | 425.2 | 369.1 | 350 | 373.2 | 398.4 | 348.9 | 376.3 | 381.2
2066 | 1845 | -6.7 | 0 | 0 | 489.5 | 331 | 341 | 338.5 | 411 | 67.5 | 16.9 | 107.2 | 6.2 | 264.4 | 8.5 | 428.5 | 433.3 | 662.5 | 241.1 | 577.6 | 633.2 | 413.4 | 234.6 | 525.4 | 693.5 | 472 | 515.3 | 696.8 | 452.5 | 492.8 | 660.2 | 565.3 | 424.8 | 368.8 | 349.5 | 372.8 | 398 | 348.4 | 375.5 | 380.8
2067 | 1846 | -6.7 | 0 | 0 | 482.1 | 330.7 | 340.4 | 337.9 | 410 | 67.3 | 16.9 | 107.1 | 5.1 | 273 | 8.9 | 428.6 | 433.5 | 651.6 | 239.6 | 577.8 | 633.2 | 415.2 | 233.3 | 524.1 | 693.1 | 471.5 | 515 | 696.3 | 451.2 | 492.5 | 659.7 | 563.9 | 424.4 | 368.2 | 349.3 | 372.4 | 397.5 | 348 | 375 | 380.5
2068 | 1847 | -6.7 | 0 | 0 | 478.3 | 330.5 | 339.9 | 337.3 | 409.4 | 67.2 | 16.9 | 106.9 | 4.8 | 271.6 | 8.1 | 428.7 | 433.6 | 644.6 | 238.6 | 578 | 633.3 | 417.4 | 232.4 | 522.9 | 692.5 | 469.3 | 514.1 | 695.9 | 449.9 | 492.4 | 659.4 | 563.4 | 424.1 | 367.6 | 348.7 | 372 | 397 | 347.5 | 374.9 | 380.1
2069 | 1848 | -6.7 | 0 | 0 | 477.4 | 330.2 | 339.6 | 337.4 | 408.2 | 67.1 | 16.9 | 106.8 | 4.8 | 273.2 | 7.5 | 428.9 | 433.7 | 642.4 | 237.4 | 578.1 | 633.5 | 418.4 | 231.7 | 521.5 | 692 | 468.1 | 514.1 | 695.6 | 449.3 | 492.1 | 659.1 | 563.1 | 423.7 | 366.9 | 347.9 | 371.5 | 396.5 | 347 | 374.2 | 379.7
2070 | 1849 | -6.7 | 0 | 0 | 479.5 | 329.7 | 339 | 337.1 | 406.6 | 67.1 | 16.9 | 106.6 | 5.1 | 265 | 7.6 | 429 | 433.8 | 635.1 | 236.1 | 578.3 | 633.5 | 417 | 230.9 | 520.2 | 691.4 | 467.6 | 515 | 695.2 | 448.4 | 497.8 | 658.7 | 563.8 | 423.3 | 366.7 | 347.5 | 371.1 | 396 | 346.5 | 373.4 | 379.4
2071 | 1850 | -6.7 | 0 | 0 | 477.3 | 329.3 | 338.5 | 336.4 | 405.1 | 67 | 16.9 | 106.4 | 4.9 | 238.1 | 6.8 | 429.2 | 433.9 | 640.6 | 234.6 | 578.4 | 633.6 | 416.5 | 229.2 | 518.4 | 691.1 | 467.3 | 515.4 | 694.9 | 447.7 | 494.1 | 658.4 | 563.8 | 422.9 | 366.4 | 347.1 | 370.8 | 395.6 | 346.1 | 372.7 | 379
2072 | 1851 | -6.7 | 0 | 0 | 472.2 | 328.9 | 338 | 336.2 | 404 | 66.8 | 16.9 | 106.1 | 4.9 | 259.8 | 6.2 | 429.3 | 434 | 644.6 | 233.5 | 578.6 | 633.4 | 413.5 | 227.9 | 516.5 | 690.6 | 467.9 | 515.9 | 694.5 | 446.8 | 492.6 | 658 | 563.2 | 422.5 | 366 | 346.3 | 370.3 | 395.1 | 345.6 | 372.2 | 378.6
2073 | 1852 | -6.7 | 0 | 0 | 467.5 | 328.4 | 337.4 | 335.8 | 403.1 | 66.7 | 16.9 | 105.9 | 5 | 259.7 | 6.1 | 429.4 | 434.1 | 645.9 | 231.8 | 578.7 | 633.2 | 411.9 | 227.1 | 515.1 | 690.1 | 465.3 | 512.7 | 694.1 | 446.5 | 490.8 | 657.5 | 562 | 422.2 | 365.4 | 345.8 | 369.9 | 394.6 | 345.1 | 371.7 | 378.3
2074 | 1853 | -6.7 | 0 | 0 | 463.8 | 327.9 | 337.3 | 335.5 | 403.3 | 66.6 | 16.9 | 105.7 | 5.2 | 249.9 | 6.8 | 429.6 | 434.1 | 644.9 | 230.7 | 578.9 | 633.1 | 410.1 | 226.5 | 513.6 | 689.7 | 463.2 | 511.3 | 693.7 | 446.7 | 489.2 | 657.2 | 561.1 | 421.8 | 364.8 | 345.2 | 369.5 | 394.2 | 344.6 | 371.5 | 378
2075 | 1854 | -6.7 | 0 | 0 | 461.4 | 327.7 | 337 | 334.6 | 402.9 | 66.5 | 16.9 | 105.5 | 5.3 | 256.4 | 6.8 | 429.7 | 434.2 | 643.3 | 229.3 | 579 | 633 | 409 | 225.7 | 512.3 | 689.2 | 461.5 | 510.8 | 693.4 | 445.7 | 487.4 | 656.8 | 560.4 | 421.4 | 364.1 | 344.6 | 369.1 | 393.7 | 344 | 370.7 | 377.6
2076 | 1855 | -6.7 | 0 | 0 | 459 | 327.7 | 336.4 | 333.9 | 402.1 | 66.4 | 16.9 | 105.4 | 5.2 | 268.3 | 6.5 | 429.8 | 434.4 | 643.7 | 227.7 | 579.1 | 632.9 | 406.4 | 224 | 510.9 | 688.8 | 460.4 | 510 | 693.1 | 444.5 | 483.5 | 656.5 | 559.3 | 421 | 363.7 | 344.4 | 368.6 | 393.2 | 343.4 | 370.2 | 377.2
2077 | 1856 | -6.7 | 0 | 0 | 457.4 | 327.6 | 335.8 | 333.4 | 401.4 | 66.4 | 16.9 | 105.2 | 5 | 260.9 | 6.3 | 430 | 434.5 | 646.1 | 226.4 | 579.3 | 632.7 | 406.3 | 222.3 | 509.7 | 688.6 | 459.2 | 508.5 | 692.7 | 445.3 | 481.4 | 656.1 | 558.4 | 420.6 | 363.3 | 344.1 | 368.3 | 392.7 | 342.8 | 369.2 | 376.9
2078 | 1857 | -6.7 | 0 | 0 | 454 | 327.4 | 335.4 | 333.3 | 400.3 | 66.3 | 16.9 | 105 | 5.8 | 247.6 | 5.5 | 430.1 | 434.6 | 645.5 | 225.4 | 579.4 | 632.6 | 406.5 | 221.1 | 508.5 | 688.4 | 458.2 | 507.1 | 692.3 | 443.2 | 479.6 | 655.7 | 557.5 | 420.2 | 362.8 | 343.4 | 367.8 | 392.3 | 342.4 | 368.3 | 376.5
2079 | 1858 | -6.7 | 0 | 0 | 452.2 | 327.1 | 335.2 | 332.8 | 399.4 | 66.2 | 16.9 | 104.9 | 6 | 276.3 | 5.4 | 430.2 | 434.7 | 654.9 | 224.3 | 579.5 | 632.4 | 406.1 | 219.8 | 507.3 | 688 | 459 | 507.1 | 691.8 | 441.5 | 484.6 | 655.4 | 556.9 | 419.8 | 362.3 | 342.9 | 367.4 | 391.8 | 342 | 367.7 | 376.2
2080 | 1859 | -6.7 | 0 | 0 | 451 | 326.8 | 334.7 | 332.1 | 399.1 | 66 | 16.9 | 104.7 | 5.7 | 273.4 | 5.9 | 430.4 | 434.8 | 661.1 | 223.2 | 579.7 | 632.4 | 406.3 | 218.3 | 506.3 | 687.6 | 459.9 | 509.7 | 691.4 | 441.7 | 483.4 | 655.1 | 556.6 | 419.5 | 361.8 | 342.6 | 367.1 | 391.3 | 341.9 | 367.3 | 375.8
2081 | 1860 | -6.7 | 0 | 0 | 448.7 | 326.3 | 334.1 | 331.7 | 398.3 | 65.9 | 17 | 104.5 | 5.2 | 274.4 | 6.4 | 430.5 | 434.9 | 662.9 | 222.2 | 579.8 | 632.3 | 403.8 | 218.1 | 505.3 | 687.3 | 462 | 516.4 | 690.9 | 441.5 | 485.9 | 654.6 | 556.7 | 419.1 | 361.2 | 342.2 | 366.7 | 390.9 | 341.5 | 366.9 | 375.5
2082 | 1861 | -6.7 | 0 | 0 | 448.4 | 325.8 | 333.6 | 330.8 | 398.2 | 65.9 | 17 | 104.2 | 5.4 | 279 | 6.5 | 430.6 | 434.9 | 664.8 | 220.8 | 579.9 | 632.2 | 403.1 | 217.8 | 504.3 | 687 | 464.6 | 519.7 | 690.5 | 442.7 | 485.1 | 654.2 | 556.6 | 418.7 | 360.8 | 341.8 | 366.4 | 390.4 | 341 | 366.4 | 375.1
2083 | 1862 | -6.7 | 0 | 0 | 447.1 | 325.5 | 333.2 | 330.1 | 398.6 | 65.8 | 16.9 | 104 | 5.3 | 270.9 | 6.3 | 430.7 | 435 | 662.2 | 219.5 | 580 | 632.1 | 403 | 217.4 | 503.2 | 686.6 | 466.6 | 518.7 | 690.1 | 443.3 | 481.6 | 653.9 | 555.9 | 418.4 | 360.6 | 341.5 | 366 | 389.9 | 340.5 | 366.3 | 374.8
2084 | 1863 | -6.7 | 0 | 0 | 447.1 | 325.4 | 332.9 | 329.8 | 398.4 | 65.8 | 17 | 103.7 | 5.3 | 265.4 | 6.6 | 430.9 | 435.1 | 664.1 | 218.4 | 580.1 | 632 | 400.9 | 217.3 | 502.2 | 686.1 | 465.8 | 518.5 | 689.7 | 444 | 481.1 | 653.6 | 556 | 418 | 360 | 341 | 365.5 | 389.5 | 340 | 365.9 | 374.4
2085 | 1864 | -6.7 | 0 | 0 | 446.5 | 325.2 | 332.7 | 329.7 | 397.8 | 65.7 | 17 | 103.5 | 5.1 | 269 | 6.9 | 431 | 435.2 | 668.7 | 217.4 | 580.2 | 631.9 | 399.4 | 216.8 | 500.9 | 685.7 | 465.4 | 520.1 | 689.2 | 444.1 | 482 | 653.2 | 555.8 | 417.6 | 359.6 | 340.5 | 365.1 | 389 | 339.6 | 365.6 | 374.1
2086 | 1865 | -6.7 | 0 | 0 | 447.1 | 324.9 | 332.7 | 329.5 | 397.4 | 65.7 | 17 | 103.3 | 4.9 | 264 | 7.1 | 431.1 | 435.2 | 668 | 216.3 | 580.3 | 631.7 | 397.5 | 215.7 | 499.7 | 685.4 | 465.9 | 520.3 | 688.7 | 443.7 | 481.4 | 652.8 | 555.6 | 417.3 | 359.2 | 340.2 | 364.8 | 388.6 | 339.2 | 365.5 | 373.7
2087 | 1866 | -6.7 | 0 | 0 | 446.8 | 324.6 | 332.5 | 329.3 | 397.1 | 65.6 | 17 | 103.2 | 5 | 258.4 | 7.3 | 431.2 | 435.3 | 672.7 | 215.3 | 580.4 | 631.5 | 395.9 | 214.4 | 498.1 | 685.3 | 464.1 | 518.9 | 688.2 | 443.8 | 485.2 | 652.4 | 555.1 | 416.9 | 358.9 | 339.7 | 364.5 | 388.2 | 338.8 | 365.3 | 373.4
2088 | 1867 | -6.7 | 0 | 0 | 444.6 | 324.4 | 332.2 | 329 | 396 | 65.5 | 17 | 103 | 4.5 | 268.4 | 6.7 | 431.3 | 435.4 | 666.5 | 214.6 | 580.5 | 631.5 | 395.9 | 214.2 | 496.4 | 685 | 462.2 | 516.3 | 687.6 | 443.8 | 482.3 | 652.1 | 553.9 | 416.5 | 358.3 | 339.3 | 364.1 | 387.7 | 338.3 | 364.8 | 373
2089 | 1868 | -6.7 | 0 | 0 | 445 | 324.1 | 331.8 | 328.7 | 394.9 | 65.3 | 17 | 102.8 | 4.3 | 250 | 6.2 | 431.4 | 435.5 | 664.9 | 213.8 | 580.6 | 631.5 | 396.1 | 212.1 | 494.8 | 684.5 | 460.3 | 513.4 | 687.3 | 442.1 | 476.1 | 651.8 | 552.8 | 416.1 | 357.8 | 339.1 | 363.7 | 387.3 | 337.9 | 364.3 | 372.7
2090 | 1869 | -6.7 | 0 | 0 | 443.9 | 323.7 | 331.6 | 328.2 | 393.4 | 65.1 | 17 | 102.7 | 4.8 | 248.1 | 6.5 | 431.6 | 435.6 | 667.4 | 212.4 | 580.7 | 631.4 | 398.1 | 210 | 492.9 | 684.1 | 459.8 | 511.7 | 687.1 | 439.7 | 474.3 | 651.4 | 552.1 | 415.8 | 357.4 | 338.7 | 363.3 | 386.8 | 337.4 | 364.2 | 372.3
2091 | 1870 | -6.7 | 0 | 0 | 442.1 | 323.4 | 331 | 328 | 392.3 | 64.8 | 17 | 102.5 | 4.3 | 247.5 | 7 | 431.7 | 435.6 | 664.3 | 211.4 | 580.8 | 631.3 | 398.3 | 208.3 | 491.2 | 683.8 | 459.2 | 511.5 | 686.9 | 438.1 | 471.5 | 651 | 551.5 | 415.4 | 356.9 | 338.2 | 362.9 | 386.3 | 337 | 363.6 | 372
2092 | 1871 | -6.7 | 0 | 0 | 442.4 | 323 | 330.5 | 327.4 | 392.1 | 64.6 | 17 | 102.4 | 4.9 | 239.1 | 6.7 | 431.8 | 435.7 | 666.8 | 210.4 | 581 | 631.4 | 398.2 | 207.4 | 489.3 | 683.5 | 458.4 | 511.3 | 686.5 | 437.1 | 472.9 | 650.7 | 551 | 415 | 356.4 | 338.1 | 362.6 | 385.9 | 336.7 | 363.3 | 371.6
2093 | 1872 | -6.7 | 0 | 0 | 442.1 | 322.6 | 330.1 | 326.4 | 392.1 | 64.5 | 17 | 102.3 | 5.1 | 235.1 | 6.2 | 431.9 | 435.7 | 670.6 | 209.1 | 581.1 | 631.2 | 397.4 | 206.3 | 487.6 | 683.4 | 457.8 | 512.6 | 686.2 | 436.1 | 478.7 | 650.4 | 550.6 | 414.7 | 356 | 337.7 | 362.2 | 385.4 | 336.3 | 362.8 | 371.3
2094 | 1873 | -6.7 | 0 | 0 | 440.2 | 322.1 | 329.7 | 326.3 | 392 | 64.4 | 17 | 102.1 | 4.8 | 237.6 | 6.5 | 432 | 435.8 | 673.9 | 207.5 | 581.2 | 631 | 395.1 | 204.4 | 486.5 | 683.1 | 457.2 | 512.8 | 685.8 | 436.1 | 483.5 | 650 | 550.8 | 414.3 | 355.6 | 337 | 361.8 | 385 | 336 | 362.2 | 370.9
2095 | 1874 | -6.7 | 0 | 0 | 438.5 | 321.8 | 329.2 | 325.8 | 391.5 | 64.3 | 17 | 102 | 4.7 | 230.8 | 6.9 | 432.1 | 435.8 | 673.6 | 206.4 | 581.3 | 630.8 | 393.8 | 203.2 | 485.2 | 682.7 | 456.6 | 512.2 | 685.2 | 435.2 | 481.7 | 649.6 | 550.4 | 413.9 | 355.3 | 336.7 | 361.4 | 384.5 | 335.6 | 361.6 | 370.5
2096 | 1875 | -6.7 | 0 | 0 | 437.6 | 321.5 | 328.9 | 325.4 | 391.7 | 64.2 | 17 | 101.8 | 5.1 | 238.6 | 7.3 | 432.2 | 435.9 | 669.8 | 205.6 | 581.4 | 630.5 | 391.2 | 202.1 | 484.2 | 682.5 | 456.8 | 511.1 | 684.6 | 435.5 | 482.4 | 649.2 | 549.4 | 413.5 | 355 | 336.5 | 361.1 | 384.1 | 335 | 360.9 | 370.2
2097 | 1876 | -6.7 | 0 | 0 | 436.5 | 321.2 | 328.5 | 325.3 | 392.6 | 64.1 | 17 | 101.7 | 5.1 | 227.5 | 7.6 | 432.3 | 435.9 | 657.8 | 205 | 581.6 | 630.2 | 388.5 | 201.2 | 483.1 | 682.2 | 455.7 | 509.8 | 684.1 | 436.2 | 478.7 | 648.7 | 548.7 | 413.1 | 354.6 | 336.3 | 360.8 | 383.7 | 334.5 | 360.3 | 369.8
2098 | 1877 | -6.7 | 0 | 0 | 433.2 | 320.9 | 328.1 | 325 | 393.6 | 64 | 17 | 101.6 | 5.3 | 243 | 7.5 | 432.4 | 436 | 652.6 | 204.1 | 581.7 | 630.1 | 389.1 | 200.4 | 482.6 | 682.1 | 456.2 | 509.7 | 683.6 | 436.1 | 477.8 | 648.4 | 548.1 | 412.8 | 354.1 | 336.1 | 360.4 | 383.3 | 333.9 | 359.9 | 369.4
2099 | 1878 | -6.7 | 0 | 0 | 430.7 | 320.7 | 327.9 | 324.7 | 393.2 | 63.9 | 17 | 101.5 | 4.8 | 251.4 | 6.8 | 432.5 | 436.1 | 654.7 | 202.7 | 581.8 | 630.1 | 388.3 | 199.5 | 481.7 | 681.9 | 454.6 | 509.8 | 683.1 | 436.1 | 477.2 | 648 | 548 | 412.5 | 353.6 | 335.7 | 360 | 382.8 | 333.5 | 359.4 | 369.1
2100 | 1879 | -6.7 | 0 | 0 | 429.1 | 320.4 | 327.8 | 324.7 | 392.3 | 63.9 | 17 | 101.3 | 4.5 | 254.5 | 5.7 | 432.6 | 436.2 | 654.3 | 201.8 | 581.8 | 630 | 387.9 | 197.8 | 480.7 | 681.7 | 454.1 | 510 | 682.7 | 435.8 | 480.4 | 647.8 | 547.9 | 412.1 | 353.2 | 335.2 | 359.7 | 382.4 | 333 | 358.7 | 368.7
2101 | 1880 | -6.7 | 0 | 0 | 428.3 | 320.1 | 327.5 | 324.8 | 391.5 | 63.8 | 17 | 101.1 | 4.6 | 262.2 | 5.5 | 432.7 | 436.2 | 642.5 | 200.7 | 581.9 | 629.9 | 389.3 | 196.9 | 479.7 | 681.3 | 453 | 507.4 | 682.4 | 436.3 | 478.3 | 647.5 | 547.2 | 411.7 | 352.7 | 334.8 | 359.4 | 382 | 332.6 | 358.1 | 368.3
2102 | 1881 | -6.7 | 0 | 0 | 428.9 | 319.8 | 327.1 | 324.3 | 391 | 63.7 | 17 | 100.9 | 5.1 | 267.3 | 5.6 | 432.8 | 436.3 | 637.6 | 200.3 | 582 | 629.5 | 386.7 | 195.9 | 478.7 | 680.9 | 450.8 | 505 | 682 | 435 | 477 | 647.2 | 546.2 | 411.4 | 352.4 | 334.4 | 359 | 381.6 | 332.1 | 357.7 | 368
2103 | 1882 | -6.7 | 0 | 0 | 432.3 | 319.7 | 326.6 | 323.7 | 390.4 | 63.6 | 17 | 100.8 | 4.8 | 268.6 | 5.3 | 432.9 | 436.4 | 627.6 | 199.5 | 582.1 | 629.3 | 384.7 | 195.6 | 477.6 | 680.5 | 450.9 | 504.7 | 681.5 | 434.6 | 476.6 | 647.1 | 546.3 | 411 | 351.9 | 333.9 | 358.6 | 381.1 | 331.8 | 357 | 367.6
2104 | 1883 | -6.7 | 0 | 0 | 439.5 | 319.5 | 326.8 | 323.6 | 389.6 | 63.5 | 17 | 100.7 | 4.8 | 239 | 5.7 | 433 | 436.5 | 623.4 | 198.6 | 582.1 | 629.1 | 383.1 | 195.1 | 476.6 | 680.2 | 450.1 | 504.2 | 680.9 | 434.7 | 477.2 | 646.7 | 546.1 | 410.7 | 351.7 | 333.5 | 358.1 | 380.8 | 331.5 | 356.6 | 367.3
2105 | 1884 | -6.7 | 0 | 0 | 443.8 | 319.4 | 326.9 | 323.7 | 389.5 | 63.5 | 17 | 100.6 | 4.8 | 243.5 | 5.8 | 433.1 | 436.6 | 625 | 198.3 | 582.2 | 628.8 | 383.1 | 194 | 475.5 | 679.7 | 450.6 | 502.7 | 680.4 | 434.3 | 472.6 | 646.3 | 545.1 | 410.3 | 351.4 | 333.9 | 357.8 | 380.4 | 331.2 | 356.2 | 367
2106 | 1885 | -6.7 | 0 | 0 | 444.2 | 319.4 | 326.8 | 323.6 | 389.4 | 63.5 | 17 | 100.5 | 4.8 | 254.5 | 5.3 | 433.1 | 436.7 | 619.7 | 198.2 | 582.3 | 628.6 | 384.4 | 192.4 | 473.8 | 679.2 | 449.4 | 501.1 | 680.1 | 434 | 468.4 | 645.9 | 544 | 410 | 351 | 334.2 | 357.5 | 380 | 330.8 | 355.7 | 366.6
2107 | 1886 | -6.7 | 0 | 0 | 442.6 | 319.1 | 326.7 | 323.8 | 388.6 | 63.5 | 17 | 100.3 | 4.9 | 256.3 | 5.1 | 433.2 | 436.8 | 613.8 | 198.2 | 582.4 | 628.4 | 384.9 | 191.4 | 472.7 | 678.8 | 450.2 | 501.3 | 679.8 | 433.2 | 463.8 | 645.6 | 543.9 | 409.7 | 350.5 | 334.2 | 357.1 | 379.5 | 330.4 | 355.5 | 366.2
2108 | 1887 | -6.7 | 0 | 0 | 442.7 | 318.7 | 326.5 | 324.1 | 388.1 | 63.5 | 17 | 100.2 | 4.6 | 262.9 | 4.9 | 433.3 | 436.9 | 601 | 197.2 | 582.5 | 627.8 | 381.4 | 190.2 | 471.1 | 678.7 | 449.7 | 500.6 | 679.3 | 433 | 460.5 | 645.2 | 544.4 | 409.3 | 350.1 | 334.1 | 356.8 | 379.1 | 330.1 | 354.9 | 365.9
2109 | 1888 | -6.7 | 0 | 0 | 440.2 | 318.4 | 326.2 | 323.9 | 387.6 | 63.5 | 17 | 100.1 | 4.8 | 262.1 | 4.8 | 433.4 | 436.9 | 604.9 | 195.5 | 582.5 | 627.5 | 378.2 | 188.7 | 469.7 | 678.6 | 448.2 | 500.2 | 678.5 | 432.9 | 458 | 644.7 | 544.4 | 408.9 | 349.7 | 334.1 | 356.5 | 378.8 | 329.8 | 354.7 | 365.5
2110 | 1889 | -6.7 | 0 | 0 | 435.4 | 318.1 | 325.8 | 323.6 | 386.8 | 63.5 | 17 | 100 | 4.6 | 252.3 | 5 | 433.4 | 437 | 604.2 | 194.2 | 582.6 | 627.3 | 376.7 | 187.4 | 468.2 | 678.6 | 446.7 | 499.9 | 677.7 | 431.7 | 455 | 644.3 | 543.4 | 408.6 | 349.3 | 334 | 356.2 | 378.3 | 329.5 | 354.4 | 365.2
2111 | 1890 | -6.7 | 0 | 0 | 431.5 | 317.8 | 325.2 | 323.2 | 386.3 | 63.4 | 17 | 99.8 | 4.5 | 273.1 | 5.5 | 433.5 | 437.1 | 599.1 | 193.1 | 582.7 | 626.8 | 373.9 | 186.4 | 466.8 | 678.6 | 445.6 | 497 | 677 | 431.3 | 458.5 | 643.9 | 543.8 | 408.2 | 349.1 | 333.6 | 355.9 | 377.9 | 329.2 | 354 | 364.9
2112 | 1891 | -6.7 | 0 | 0 | 427.6 | 317.5 | 324.7 | 323 | 385.6 | 63.3 | 17 | 99.6 | 4.6 | 248.7 | 6.4 | 433.5 | 437.1 | 590.6 | 192.1 | 582.7 | 626.3 | 372.4 | 185.5 | 465.7 | 678.1 | 444.1 | 495.5 | 676.4 | 431 | 453.8 | 643.4 | 543 | 407.8 | 349 | 333.2 | 355.6 | 377.5 | 329.1 | 353.9 | 364.6
2113 | 1892 | -6.7 | 0 | 0 | 426.1 | 317.3 | 324.7 | 322.3 | 385.4 | 63.3 | 17 | 99.5 | 4.8 | 251.8 | 6.7 | 433.5 | 437.2 | 581.4 | 192.1 | 582.7 | 625.7 | 370.9 | 184.3 | 464.3 | 677.6 | 442.2 | 492.6 | 675.8 | 430.7 | 450.5 | 643 | 542.1 | 407.4 | 348.6 | 332.8 | 355.2 | 377.1 | 328.8 | 353.6 | 364.3
2114 | 1893 | -6.7 | 0 | 0 | 423.9 | 317 | 324.8 | 322 | 384.8 | 63.2 | 17 | 99.3 | 4.1 | 261.6 | 7 | 433.5 | 437.3 | 574.1 | 191.2 | 582.8 | 625.3 | 370.5 | 183.1 | 463.3 | 677.2 | 439.3 | 491.4 | 675.4 | 431.3 | 451 | 642.7 | 541.7 | 407.1 | 348.2 | 332.4 | 354.9 | 376.8 | 328.7 | 353.2 | 364
2115 | 1894 | -6.7 | 0 | 0 | 421.4 | 316.7 | 324.2 | 322 | 384.9 | 63.2 | 17 | 99.2 | 4.2 | 263.8 | 6.7 | 433.6 | 437.4 | 579.3 | 190.3 | 582.8 | 624.9 | 369.1 | 182.4 | 461.8 | 676.7 | 437.7 | 490.4 | 675 | 431.8 | 450.3 | 642.3 | 541.7 | 406.7 | 347.8 | 331.8 | 354.5 | 376.4 | 328.4 | 352.8 | 363.6
2116 | 1895 | -6.7 | 0 | 0 | 420.1 | 316.4 | 323.8 | 321.9 | 384.5 | 63.1 | 17 | 99 | 4.1 | 264.7 | 6.2 | 433.6 | 437.5 | 577.8 | 189 | 582.8 | 624.6 | 366.3 | 181.3 | 460.7 | 676.2 | 437.3 | 489.9 | 674.6 | 432.7 | 449.2 | 641.9 | 541.5 | 406.3 | 347.4 | 331.3 | 354 | 376.1 | 328 | 352.2 | 363.2
2117 | 1896 | -6.7 | 0 | 0 | 419.7 | 316.1 | 323 | 321.5 | 383.9 | 63.1 | 17 | 98.9 | 4.4 | 266.4 | 6 | 433.7 | 437.6 | 577.6 | 187.8 | 582.9 | 624.4 | 363.9 | 180.2 | 459.6 | 675.9 | 436.3 | 489.7 | 674.3 | 432.9 | 449.6 | 641.6 | 541.4 | 406 | 347.1 | 330.7 | 353.6 | 375.7 | 327.6 | 351.6 | 362.9
2118 | 1897 | -6.7 | 0 | 0 | 422 | 315.7 | 322.6 | 321.1 | 383.8 | 63.1 | 17 | 98.7 | 4.2 | 269.8 | 5.5 | 433.7 | 437.7 | 577.6 | 187.2 | 582.9 | 624.1 | 361.5 | 179.6 | 458.8 | 675.6 | 435.6 | 489.2 | 673.9 | 432.7 | 454.7 | 641.4 | 540.8 | 405.6 | 346.6 | 330.1 | 353.2 | 375.4 | 327.4 | 351.2 | 362.6
2119 | 1898 | -6.7 | 0 | 0 | 424.2 | 315.2 | 322.7 | 321 | 383.8 | 63 | 17 | 98.5 | 4 | 270.3 | 4.8 | 433.7 | 437.8 | 581 | 187 | 582.9 | 624 | 359.8 | 179 | 458.4 | 675.3 | 434.8 | 488.6 | 673.5 | 433.5 | 455.6 | 641 | 540.4 | 405.3 | 346.4 | 329.8 | 352.9 | 375 | 327 | 350.9 | 362.2
2120 | 1899 | -6.7 | 0 | 0 | 426.6 | 314.7 | 322.7 | 321.1 | 383.3 | 62.9 | 17 | 98.4 | 4.1 | 269.9 | 5 | 433.8 | 437.8 | 584.1 | 186.6 | 582.9 | 623.9 | 360.1 | 178.8 | 457.9 | 675.1 | 435.5 | 487.1 | 673 | 432.9 | 452.6 | 640.6 | 539.4 | 404.9 | 346 | 329.4 | 352.6 | 374.6 | 326.5 | 350.3 | 361.8
2121 | 1900 | -6.7 | 0 | 0 | 435.7 | 314.2 | 322.4 | 320.9 | 383.1 | 62.8 | 17 | 98.2 | 4.6 | 277.7 | 5.3 | 433.8 | 437.9 | 581.3 | 186.2 | 583 | 624 | 362.6 | 178.4 | 457.5 | 674.6 | 435 | 488 | 672.6 | 432 | 451.2 | 640.3 | 539.4 | 404.5 | 345.5 | 328.7 | 352.2 | 374.3 | 326 | 350.1 | 361.5
2122 | 1901 | -6.7 | 0 | 0 | 441.1 | 313.8 | 322.5 | 321 | 382.9 | 62.7 | 17 | 98.1 | 4.7 | 266.2 | 5.4 | 433.8 | 438.1 | 579 | 184.9 | 583 | 623.9 | 361.6 | 177.4 | 457.1 | 674.2 | 434.1 | 488 | 672.1 | 431.9 | 451.2 | 639.9 | 539.4 | 404.1 | 345.1 | 328.2 | 351.8 | 373.9 | 325.7 | 349.6 | 361.2
2123 | 1902 | -6.7 | 0 | 0 | 444.2 | 313.5 | 322.3 | 320.5 | 383.2 | 62.5 | 17 | 97.9 | 4.4 | 248.1 | 5.7 | 433.8 | 438.2 | 582.2 | 183.7 | 582.9 | 623.7 | 361.6 | 176.7 | 456.5 | 673.8 | 432.7 | 487.8 | 671.6 | 433.1 | 452.7 | 639.6 | 539 | 403.8 | 344.7 | 327.8 | 351.4 | 373.5 | 325.3 | 349.2 | 360.8
2124 | 1903 | -6.7 | 0 | 0 | 449.1 | 313.2 | 322.1 | 320 | 383 | 62.5 | 17 | 97.8 | 4.4 | 251.3 | 5.4 | 433.9 | 438.3 | 589.5 | 183.1 | 582.9 | 623.5 | 359 | 176.1 | 455.9 | 673.4 | 431.7 | 490.7 | 671.1 | 433.5 | 455.5 | 639.3 | 538.6 | 403.4 | 344.6 | 327.5 | 351.1 | 373.1 | 325.1 | 348.7 | 360.5
2125 | 1904 | -6.7 | 0 | 0 | 453.3 | 313 | 322.2 | 319.6 | 382.3 | 62.4 | 17 | 97.7 | 4.9 | 260.4 | 5.1 | 433.9 | 438.4 | 582.8 | 182.6 | 583 | 623.2 | 357.2 | 175.1 | 455.2 | 673 | 431 | 490.3 | 670.6 | 433.8 | 455.3 | 639 | 538.9 | 403.1 | 344.2 | 327.1 | 350.9 | 372.7 | 324.9 | 348.2 | 360.2
2126 | 1905 | -6.7 | 0 | 0 | 453.6 | 312.9 | 322.1 | 319.8 | 381.8 | 62.3 | 17 | 97.6 | 4.3 | 271.3 | 4.8 | 433.9 | 438.5 | 582.1 | 182.3 | 583 | 622.8 | 354.1 | 173.8 | 454.4 | 672.8 | 430.4 | 490 | 670 | 433.9 | 452.8 | 638.7 | 537.7 | 402.7 | 343.7 | 326.6 | 350.5 | 372.4 | 324.9 | 347.9 | 359.8
2127 | 1906 | -6.7 | 0 | 0 | 451.8 | 312.7 | 322.2 | 319.9 | 381.2 | 62.3 | 17 | 97.5 | 5 | 276.4 | 5 | 433.9 | 438.6 | 585.3 | 181.3 | 583 | 622.4 | 352.9 | 172.9 | 453.5 | 672.7 | 428.9 | 489.4 | 669.4 | 433.4 | 456.1 | 638.3 | 537.8 | 402.4 | 343.3 | 326.4 | 350.2 | 372 | 324.7 | 347.7 | 359.5
2128 | 1907 | -6.7 | 0 | 0 | 447.6 | 312.5 | 322.1 | 319.9 | 380.6 | 62.2 | 17 | 97.3 | 4.8 | 273.5 | 4.9 | 433.9 | 438.7 | 584.1 | 179.9 | 583 | 622.2 | 350.9 | 172.1 | 452.5 | 672.3 | 426.9 | 492.2 | 668.9 | 432.8 | 460.6 | 637.9 | 538.9 | 402.1 | 343.1 | 326 | 349.8 | 371.6 | 324.4 | 347.3 | 359.1
2129 | 1908 | -6.7 | 0 | 0 | 445.5 | 312.1 | 321.8 | 319.9 | 380.2 | 62.2 | 17 | 97.1 | 4.9 | 273.2 | 5.1 | 433.9 | 438.9 | 584 | 179.3 | 583 | 621.9 | 349.3 | 171.5 | 451.2 | 671.9 | 427 | 491.4 | 668.3 | 431.3 | 457.1 | 637.5 | 538.6 | 401.7 | 342.8 | 325.7 | 349.4 | 371.2 | 324 | 346.7 | 358.8
2130 | 1909 | -6.7 | 0 | 0 | 442 | 311.5 | 321.3 | 319.6 | 379.9 | 62.1 | 17 | 97 | 4.9 | 270.8 | 5.4 | 433.9 | 439 | 579.2 | 178.3 | 583 | 621.7 | 348.9 | 171 | 450.4 | 671.5 | 427.4 | 490.2 | 667.8 | 428.9 | 455 | 637.1 | 537.9 | 401.3 | 342.5 | 325.5 | 349.1 | 370.8 | 323.5 | 346.3 | 358.4
2131 | 1910 | -6.7 | 0 | 0 | 437.3 | 310.9 | 320.3 | 318.8 | 379.2 | 62.1 | 17 | 96.9 | 4.5 | 267.6 | 5.5 | 434 | 439.1 | 570.7 | 177.9 | 583 | 621.4 | 347.6 | 170.8 | 449.3 | 671.1 | 429 | 488.7 | 667.2 | 426.5 | 455.8 | 636.6 | 537.1 | 401 | 342.1 | 325 | 348.6 | 370.4 | 323.2 | 345.9 | 358.1
2132 | 1911 | -6.7 | 0 | 0 | 433.8 | 310.4 | 319.9 | 317.9 | 378.2 | 62.1 | 17 | 96.7 | 4.2 | 270.4 | 5.8 | 434 | 439.2 | 567.3 | 177.5 | 583 | 621 | 345.8 | 170.9 | 448.5 | 670.6 | 429.6 | 488.5 | 666.8 | 424.2 | 462.4 | 636.2 | 537 | 400.6 | 341.5 | 324.6 | 348.2 | 370 | 323 | 345.4 | 357.8
2133 | 1912 | -6.7 | 0 | 0 | 429.9 | 310 | 319.8 | 317.2 | 377 | 62 | 17 | 96.6 | 4.1 | 271.1 | 5.7 | 434 | 439.3 | 567.6 | 176.9 | 582.9 | 620.6 | 343.9 | 170.8 | 447.7 | 670 | 429.1 | 488.1 | 666.4 | 421.7 | 459.6 | 635.8 | 536.5 | 400.2 | 341 | 324.2 | 347.9 | 369.6 | 322.6 | 344.8 | 357.5
2134 | 1913 | -6.7 | 0 | 0 | 426.2 | 309.7 | 319.5 | 316.4 | 376.1 | 62 | 17 | 96.5 | 4.6 | 263.4 | 5.9 | 434 | 439.4 | 563.4 | 176.3 | 582.9 | 620.3 | 342.9 | 170.8 | 446.7 | 669.4 | 428.5 | 486.3 | 666 | 418.4 | 452.2 | 635.4 | 535.5 | 399.8 | 340.7 | 323.8 | 347.6 | 369.2 | 322.2 | 344.3 | 357.1
2135 | 1914 | -6.7 | 0 | 0 | 423.2 | 309.5 | 318.8 | 315.9 | 374.9 | 61.9 | 17.1 | 96.4 | 4.4 | 254.5 | 6.1 | 434.1 | 439.5 | 563.2 | 175.4 | 582.9 | 619.8 | 342 | 170.7 | 445.7 | 668.8 | 428.1 | 484.2 | 665.5 | 415.9 | 449 | 635 | 535 | 399.4 | 340.2 | 323.4 | 347.2 | 368.7 | 321.9 | 343.7 | 356.7
2136 | 1915 | -6.7 | 0 | 0 | 421.6 | 309.2 | 318.1 | 315.5 | 373.9 | 61.9 | 17.1 | 96.2 | 4.8 | 256.8 | 6.6 | 434.1 | 439.6 | 566.6 | 174.5 | 582.9 | 619.5 | 340.1 | 170.4 | 444.9 | 668.1 | 427.2 | 483.1 | 665 | 414.6 | 447.8 | 634.5 | 534.2 | 399 | 339.5 | 323 | 346.7 | 368.3 | 321.4 | 343.1 | 356.4
2137 | 1916 | -6.7 | 0 | 0 | 424 | 308.9 | 317.2 | 314.9 | 373.2 | 61.8 | 17.1 | 96.1 | 4.7 | 271.3 | 7 | 434.2 | 439.7 | 566 | 172.8 | 582.9 | 619.3 | 339.7 | 170 | 444.1 | 667.5 | 426.3 | 481.6 | 664.6 | 414.3 | 451.1 | 634.2 | 534.4 | 398.7 | 339 | 322.7 | 346.4 | 367.9 | 321.1 | 342.7 | 356
2138 | 1917 | -6.7 | 0 | 0 | 432.3 | 308.6 | 316.5 | 314.3 | 373.1 | 61.7 | 17.1 | 96 | 4.4 | 253.9 | 7.2 | 434.2 | 439.8 | 570.5 | 172 | 582.9 | 619.2 | 340.7 | 169.2 | 443.1 | 667 | 425.1 | 480.7 | 664.1 | 413.3 | 454 | 633.8 | 533.6 | 398.2 | 338.3 | 322.1 | 346 | 367.5 | 320.6 | 342.3 | 355.7
2139 | 1918 | -6.7 | 0 | 0 | 433.5 | 308.1 | 316.2 | 313.9 | 372.7 | 61.7 | 17.1 | 95.9 | 4.5 | 249.7 | 7.1 | 434.2 | 439.9 | 572.6 | 171.2 | 582.9 | 619 | 340.5 | 168.3 | 442.2 | 666.4 | 424.6 | 480.6 | 663.8 | 411.4 | 455.7 | 633.5 | 533.1 | 397.8 | 337.7 | 321.8 | 345.6 | 367.1 | 320.1 | 341.7 | 355.3
2140 | 1919 | -6.7 | 0 | 0 | 436.3 | 307.7 | 315.8 | 313.3 | 371.5 | 61.6 | 17.1 | 95.8 | 4.3 | 256.1 | 6.8 | 434.3 | 440 | 569.9 | 170.2 | 582.8 | 618.8 | 340.1 | 167.4 | 441 | 665.9 | 423.4 | 481.7 | 663.5 | 409.4 | 453.8 | 633.2 | 532.6 | 397.3 | 337.2 | 321.4 | 345.2 | 366.7 | 319.7 | 341.2 | 354.9
2141 | 1920 | -6.7 | 0 | 0 | 435 | 307.3 | 315.5 | 313.1 | 370.4 | 61.6 | 17.1 | 95.7 | 4.7 | 247.6 | 6.2 | 434.4 | 440.1 | 562.7 | 169.6 | 582.8 | 618.6 | 338.9 | 166.2 | 440 | 665.7 | 421.3 | 481.9 | 663.2 | 408.7 | 451.8 | 632.9 | 531.9 | 396.9 | 336.7 | 320.9 | 344.8 | 366.3 | 319.1 | 340.6 | 354.6
2142 | 1921 | -6.7 | 0 | 0 | 430.8 | 307 | 315.1 | 312.8 | 369.3 | 61.5 | 17.1 | 95.5 | 5.3 | 220.5 | 5.5 | 434.4 | 440.2 | 557.4 | 168.5 | 582.8 | 618.2 | 336.5 | 165.1 | 438.9 | 665.7 | 420.8 | 481.7 | 662.8 | 406.8 | 447.8 | 632.5 | 532.2 | 396.5 | 336.2 | 320.4 | 344.4 | 365.9 | 318.6 | 340 | 354.2
2143 | 1922 | -6.7 | 0 | 0 | 428 | 306.6 | 314.5 | 312.3 | 368.3 | 61.4 | 17.1 | 95.4 | 5.5 | 241.2 | 4.7 | 434.5 | 440.3 | 554.3 | 167.2 | 582.8 | 617.9 | 334.5 | 164.7 | 437.8 | 665.5 | 421.5 | 479 | 662.1 | 405 | 446.7 | 632.2 | 531.5 | 396.1 | 335.9 | 319.9 | 344 | 365.5 | 318.2 | 339.5 | 353.8
2144 | 1923 | -6.7 | 0 | 0 | 425.6 | 306.2 | 313.9 | 311.6 | 368.1 | 61.3 | 17.1 | 95.3 | 5.8 | 276 | 5.5 | 434.5 | 440.4 | 551.7 | 166.6 | 582.7 | 617.4 | 331.6 | 163.8 | 436.8 | 665.1 | 420.9 | 477.6 | 661.6 | 403.6 | 444.7 | 631.8 | 530.2 | 395.7 | 335.5 | 319.6 | 343.6 | 365.1 | 317.7 | 339.2 | 353.5
2145 | 1924 | -6.7 | 0 | 0 | 423.6 | 306 | 313.3 | 311 | 368 | 61.2 | 17.1 | 95.2 | 6.2 | 263.8 | 6.6 | 434.6 | 440.5 | 547.9 | 166.2 | 582.7 | 617 | 329.3 | 162.7 | 435.8 | 664.6 | 419.7 | 475.6 | 661.1 | 403.4 | 438.7 | 631.5 | 529.6 | 395.3 | 335 | 319.2 | 343.3 | 364.6 | 317.4 | 338.8 | 353.2
2146 | 1925 | -6.7 | 0 | 0 | 421.7 | 305.8 | 312.8 | 310.6 | 368.3 | 61.1 | 17.1 | 95.1 | 6.4 | 283 | 6.2 | 434.7 | 440.6 | 543.3 | 165.6 | 582.6 | 616.7 | 327.9 | 162.3 | 435 | 664.2 | 418.2 | 473.8 | 660.5 | 403.1 | 436.3 | 631.2 | 529.1 | 394.9 | 334.5 | 318.7 | 342.9 | 364.3 | 317.1 | 338.5 | 352.8
2147 | 1926 | -6.7 | 0 | 0 | 419.2 | 305.5 | 312.8 | 310.5 | 368.6 | 61 | 17.1 | 95 | 5.7 | 263.2 | 5.2 | 434.8 | 440.6 | 543.2 | 165.1 | 582.6 | 616.3 | 325.4 | 161.8 | 434 | 663.8 | 417.4 | 472.1 | 660 | 402.7 | 432.3 | 630.8 | 527.9 | 394.5 | 334.1 | 318.2 | 342.6 | 363.9 | 316.7 | 338.3 | 352.4
2148 | 1927 | -6.7 | 0 | 0 | 419.3 | 305.1 | 312.6 | 310.2 | 367.7 | 60.9 | 17.1 | 94.8 | 5.2 | 233.5 | 4.8 | 434.8 | 440.7 | 547.8 | 165.1 | 582.5 | 616.1 | 323.7 | 161.7 | 433.1 | 663.4 | 415.4 | 470.8 | 659.6 | 401.2 | 438.7 | 630.4 | 527.8 | 394.2 | 333.9 | 317.9 | 342.3 | 363.5 | 316.5 | 338.2 | 352.1
2149 | 1928 | -6.7 | 0 | 0 | 418 | 304.9 | 312 | 310.1 | 367 | 60.8 | 17.1 | 94.7 | 4.8 | 262.1 | 5.3 | 434.9 | 440.8 | 540.1 | 164.7 | 582.5 | 615.7 | 320.4 | 161.2 | 432 | 663 | 415 | 470.3 | 659.2 | 401.1 | 438.2 | 630 | 528.3 | 393.8 | 333.5 | 317.7 | 341.9 | 363.1 | 316.3 | 337.8 | 351.8
2150 | 1929 | -6.7 | 0 | 0 | 415.2 | 304.7 | 311.7 | 309.7 | 366.3 | 60.7 | 17.1 | 94.6 | 4.8 | 258.7 | 5.9 | 435 | 440.9 | 543.6 | 164.1 | 582.5 | 615.5 | 316.2 | 160.5 | 431.1 | 662.7 | 414.5 | 468.2 | 658.7 | 399.7 | 436.9 | 629.6 | 527.6 | 393.4 | 333.1 | 317.4 | 341.6 | 362.7 | 315.9 | 337.5 | 351.4
2151 | 1930 | -6.6 | 0 | 0 | 413.2 | 304.4 | 311.3 | 309.2 | 365.8 | 60.7 | 17.1 | 94.5 | 5 | 245 | 6.1 | 435.1 | 441 | 543.5 | 163.4 | 582.4 | 615.4 | 312.5 | 160 | 430.2 | 662.4 | 413.7 | 468.5 | 658.1 | 397.7 | 436.9 | 629.2 | 527.7 | 393 | 332.8 | 317 | 341.3 | 362.4 | 315.5 | 337.5 | 351.1
2152 | 1931 | -6.7 | 0 | 0 | 411.4 | 304 | 311 | 308.8 | 365 | 60.6 | 17.1 | 94.4 | 4.5 | 231.2 | 7.1 | 435.2 | 441.1 | 537.8 | 162.9 | 582.4 | 615.2 | 307.4 | 159.4 | 429.2 | 662.2 | 413.1 | 469.2 | 657.5 | 397.2 | 432.8 | 628.8 | 527.1 | 392.6 | 332.3 | 316.5 | 340.9 | 362 | 315 | 336.9 | 350.7
2153 | 1932 | -6.7 | 0 | 0 | 409.8 | 303.7 | 310.4 | 308.4 | 364.5 | 60.5 | 17.1 | 94.3 | 4.5 | 226.8 | 6.9 | 435.3 | 441.2 | 534.7 | 162.5 | 582.3 | 615 | 303.3 | 158.7 | 428.3 | 662.1 | 411.7 | 469 | 656.9 | 397 | 431.2 | 628.4 | 526.7 | 392.2 | 331.8 | 315.9 | 340.5 | 361.6 | 314.5 | 336.3 | 350.4
2154 | 1933 | -6.7 | 0 | 0 | 407.3 | 303.4 | 310 | 308 | 363.8 | 60.3 | 17.1 | 94.1 | 4.3 | 222.3 | 6.4 | 435.3 | 441.2 | 531.6 | 161.5 | 582.2 | 614.7 | 302 | 157.9 | 427.5 | 661.7 | 410.9 | 468.1 | 656.3 | 396.5 | 429.2 | 628 | 526 | 391.8 | 331.4 | 315.4 | 340.1 | 361.2 | 314.1 | 335.8 | 350
2155 | 1934 | -6.7 | 0 | 0 | 404.3 | 303.2 | 309.7 | 307.6 | 362.9 | 60.2 | 17.1 | 94 | 5.1 | 229 | 6.7 | 435.4 | 441.3 | 529.8 | 160.9 | 582.2 | 614.5 | 301.1 | 157.4 | 426.5 | 661 | 409.3 | 467.7 | 655.7 | 396.2 | 428.7 | 627.5 | 525.7 | 391.4 | 331.1 | 315.1 | 339.7 | 360.8 | 313.8 | 335.4 | 349.7
2156 | 1935 | -6.7 | 0 | 0 | 403.7 | 302.9 | 309.5 | 307.1 | 361.9 | 60.2 | 17.1 | 93.9 | 5.4 | 230.8 | 7.4 | 435.5 | 441.4 | 533.8 | 160.3 | 582.1 | 614.4 | 300.3 | 156.7 | 425.2 | 660.4 | 408.5 | 466.6 | 655.3 | 396 | 430.6 | 627.2 | 525.6 | 391 | 330.7 | 314.8 | 339.5 | 360.4 | 313.4 | 335 | 349.3
2157 | 1936 | -6.7 | 0 | 0 | 402.2 | 302.5 | 309.3 | 306.7 | 361.4 | 60.1 | 17.1 | 93.8 | 5.4 | 225.9 | 7.3 | 435.6 | 441.5 | 533.6 | 160.2 | 582 | 614.1 | 298.2 | 155.6 | 424.5 | 660.1 | 407.9 | 466.6 | 654.7 | 396.2 | 431.4 | 626.8 | 525.1 | 390.6 | 330.2 | 314.6 | 339.2 | 360 | 313 | 334.4 | 348.9
2158 | 1937 | -6.7 | 0 | 0 | 400.9 | 302.2 | 308.9 | 306.3 | 361.4 | 60.1 | 17.1 | 93.6 | 4.8 | 241.5 | 6.7 | 435.7 | 441.6 | 528.7 | 160.2 | 582 | 613.8 | 295.5 | 154.9 | 423.8 | 659.7 | 408.1 | 464.6 | 654.2 | 395.9 | 427.9 | 626.4 | 524.4 | 390.2 | 329.7 | 314.2 | 338.8 | 359.7 | 312.6 | 333.8 | 348.6
2159 | 1938 | -6.7 | 0 | 0 | 399.9 | 301.9 | 308.3 | 305.9 | 361.8 | 60 | 17.1 | 93.5 | 4.9 | 249.7 | 7 | 435.7 | 441.7 | 525.3 | 159.6 | 581.9 | 613.5 | 293.4 | 154.1 | 423.1 | 659.1 | 406.8 | 463.3 | 653.6 | 395.8 | 426.1 | 626 | 523.9 | 389.7 | 329.3 | 313.8 | 338.4 | 359.3 | 312.1 | 333.5 | 348.2
2160 | 1939 | -6.7 | 0 | 0 | 401.6 | 301.6 | 308 | 305.5 | 362 | 59.9 | 17.1 | 93.4 | 5.8 | 270.2 | 6.5 | 435.8 | 441.8 | 521.2 | 159.5 | 581.8 | 613.4 | 291.6 | 153.7 | 422.3 | 658.5 | 407.1 | 462.7 | 653 | 395.5 | 423.3 | 625.6 | 523.3 | 389.3 | 328.9 | 313.2 | 338.1 | 358.9 | 311.7 | 332.9 | 347.8
2161 | 1940 | -6.7 | 0 | 0 | 401.9 | 301.2 | 308 | 305.1 | 361.8 | 59.8 | 17.1 | 93.3 | 5.4 | 243.8 | 6.5 | 435.8 | 441.9 | 518.9 | 159.2 | 581.7 | 613.1 | 289.5 | 153.6 | 421.5 | 657.9 | 407.2 | 463.8 | 652.4 | 394.5 | 425.1 | 625.2 | 523.1 | 388.9 | 328.6 | 312.9 | 337.6 | 358.5 | 311.2 | 332.4 | 347.4
2162 | 1941 | -6.7 | 0 | 0 | 400.3 | 300.6 | 307.8 | 304.6 | 361.1 | 59.8 | 17.1 | 93.1 | 5.1 | 245.7 | 7.5 | 435.9 | 441.9 | 516.2 | 159.5 | 581.6 | 612.8 | 288.8 | 153.6 | 420.9 | 657.6 | 406.4 | 465.7 | 651.9 | 393.5 | 425.3 | 624.8 | 523.4 | 388.4 | 328.3 | 312.6 | 337.3 | 358.1 | 310.7 | 332 | 347.1
2163 | 1942 | -6.7 | 0 | 0 | 400.3 | 300.1 | 307.4 | 304.2 | 360.4 | 59.7 | 17.1 | 93 | 5 | 237.3 | 8 | 436 | 442 | 516.6 | 159.7 | 581.5 | 612.8 | 288.1 | 153.6 | 420.2 | 657.3 | 405.6 | 465.4 | 651.4 | 392.3 | 422.5 | 624.4 | 522.7 | 388.1 | 328 | 312.3 | 337 | 357.7 | 310.3 | 331.5 | 346.7
2164 | 1943 | -6.7 | 0 | 0 | 398.2 | 299.7 | 307.1 | 304 | 359.8 | 59.6 | 17.1 | 92.9 | 4.9 | 244.1 | 8.7 | 436 | 442.1 | 518.9 | 159.1 | 581.5 | 612.9 | 288 | 153.9 | 419.6 | 656.6 | 406.3 | 464.6 | 651 | 391.7 | 421.9 | 624 | 522.1 | 387.7 | 327.6 | 312.1 | 336.6 | 357.3 | 309.8 | 330.9 | 346.3
2165 | 1944 | -6.7 | 0 | 0 | 395.6 | 299.5 | 306.9 | 303.8 | 359.1 | 59.5 | 17.1 | 92.9 | 5 | 245.4 | 9.1 | 436.1 | 442.1 | 517.7 | 158.7 | 581.4 | 612.9 | 289.3 | 154.4 | 418.8 | 655.9 | 405.2 | 463.7 | 650.6 | 391.4 | 420.2 | 623.7 | 521.7 | 387.3 | 327.3 | 311.8 | 336.3 | 356.9 | 309.3 | 330.4 | 346
2166 | 1945 | -6.7 | 0 | 0 | 394.8 | 299.2 | 306.6 | 303.4 | 358.8 | 59.5 | 17.1 | 92.8 | 5 | 238.9 | 8.5 | 436.2 | 442.1 | 517 | 158.3 | 581.3 | 612.8 | 291.2 | 154.8 | 418.1 | 655.3 | 404.2 | 463.4 | 650.2 | 390.5 | 420.8 | 623.4 | 521 | 386.9 | 326.7 | 311.4 | 335.9 | 356.6 | 308.9 | 330.2 | 345.6
2167 | 1946 | -6.7 | 0 | 0 | 395.9 | 299 | 306.3 | 303 | 358.8 | 59.4 | 17.1 | 92.7 | 5.3 | 238 | 8.6 | 436.2 | 442.3 | 517.5 | 157.9 | 581.2 | 612.9 | 290.5 | 155.2 | 417.3 | 654.7 | 403.6 | 464.3 | 649.8 | 390 | 422.1 | 623.1 | 520.6 | 386.5 | 326.2 | 311.1 | 335.5 | 356.1 | 308.6 | 329.9 | 345.3
2168 | 1947 | -6.7 | 0 | 0 | 396.9 | 298.7 | 305.9 | 302.7 | 358.8 | 59.3 | 17.1 | 92.6 | 5.6 | 250.8 | 7.5 | 436.3 | 442.3 | 520.6 | 157.8 | 581.1 | 613 | 290.7 | 155.1 | 416.6 | 654 | 404.8 | 466.5 | 649.5 | 390.3 | 424.4 | 622.8 | 520.8 | 386.1 | 325.9 | 310.8 | 335.2 | 355.7 | 308.2 | 329.4 | 344.9
2169 | 1948 | -6.7 | 0 | 0 | 397 | 298.4 | 305.7 | 302.7 | 358.8 | 59.2 | 17.1 | 92.5 | 5.5 | 241.6 | 6.3 | 436.3 | 442.4 | 530.4 | 158 | 581 | 612.7 | 290.7 | 155.3 | 415.7 | 653.4 | 406.4 | 466.9 | 649 | 390.4 | 428.2 | 622.6 | 520.4 | 385.7 | 325.5 | 310.5 | 334.9 | 355.3 | 307.8 | 328.9 | 344.6
2170 | 1949 | -6.7 | 0 | 0 | 396.8 | 298.1 | 305.6 | 302.6 | 357.9 | 59.2 | 17.1 | 92.4 | 5.3 | 232.7 | 6.1 | 436.4 | 442.4 | 530.4 | 158.1 | 580.8 | 612.6 | 290.9 | 155.6 | 415 | 652.8 | 406.2 | 468.1 | 648.6 | 389.3 | 432.1 | 622.4 | 520.3 | 385.2 | 325.1 | 310.1 | 334.6 | 354.9 | 307.4 | 328.3 | 344.2
2171 | 1950 | -6.7 | 0 | 0 | 396.4 | 297.8 | 305.4 | 302.4 | 356.6 | 59.1 | 17.1 | 92.3 | 4.9 | 226 | 6.3 | 436.4 | 442.4 | 530.4 | 158.2 | 580.7 | 612.6 | 291.8 | 156.1 | 414.1 | 652.3 | 407.2 | 469.2 | 648.3 | 387.9 | 434 | 622.2 | 520.1 | 384.8 | 324.8 | 309.8 | 334.2 | 354.5 | 307.1 | 327.8 | 343.9
2172 | 1951 | -6.7 | 0 | 0 | 395.2 | 297.6 | 304.9 | 302.4 | 355.9 | 59.1 | 17.1 | 92.2 | 4.6 | 230.5 | 6.1 | 436.5 | 442.4 | 541.9 | 157.8 | 580.7 | 612.4 | 292.7 | 156.4 | 413.2 | 651.8 | 408.8 | 470.4 | 647.9 | 387.3 | 438.4 | 622 | 519.8 | 384.4 | 324.4 | 309.5 | 333.8 | 354.2 | 306.8 | 327.4 | 343.5
2173 | 1952 | -6.7 | 0 | 0 | 394.5 | 297.4 | 304.1 | 302.1 | 356 | 59.1 | 17.2 | 92.1 | 4.6 | 225.4 | 5.7 | 436.5 | 442.4 | 540.4 | 157.9 | 580.6 | 612.2 | 293.4 | 156.3 | 412.3 | 651.3 | 408.3 | 470.8 | 647.7 | 386.6 | 440.1 | 621.8 | 519.6 | 384 | 323.9 | 309.1 | 333.5 | 353.9 | 306.6 | 327.2 | 343.2
2174 | 1953 | -6.7 | 0 | 0 | 395.3 | 297.2 | 303.7 | 301.6 | 355.2 | 59 | 17.2 | 92.1 | 4.9 | 244.2 | 4.9 | 436.6 | 442.5 | 540.3 | 157.5 | 580.5 | 612.1 | 294.2 | 156.3 | 411.5 | 650.8 | 408.5 | 471.5 | 647.5 | 386.4 | 442.3 | 621.6 | 519.3 | 383.6 | 323.6 | 308.7 | 333.2 | 353.5 | 306.2 | 326.8 | 342.8
2175 | 1954 | -6.7 | 0 | 0 | 395.9 | 296.9 | 303.3 | 301.1 | 354.5 | 58.9 | 17.2 | 92 | 5 | 240.1 | 5 | 436.6 | 442.6 | 536.8 | 157.6 | 580.4 | 611.8 | 294.3 | 156.6 | 410.6 | 650.6 | 408.4 | 471.6 | 647.2 | 385.1 | 442.6 | 621.4 | 518.9 | 383.2 | 323.1 | 308.3 | 332.9 | 353.1 | 305.8 | 326.3 | 342.4
2176 | 1955 | -6.7 | 0 | 0 | 396.4 | 296.7 | 303.1 | 300.9 | 354.1 | 58.8 | 17.2 | 91.9 | 5.1 | 230.6 | 6.6 | 436.7 | 442.8 | 536.4 | 157.7 | 580.3 | 611.6 | 295.7 | 156.6 | 409.8 | 650.2 | 407.5 | 471.6 | 646.9 | 384 | 440.8 | 621.2 | 518.4 | 382.8 | 322.7 | 307.9 | 332.6 | 352.8 | 305.5 | 325.9 | 342.1
2177 | 1956 | -6.7 | 0 | 0 | 397.4 | 296.4 | 302.7 | 300.6 | 354.2 | 58.7 | 17.2 | 91.8 | 5.5 | 232.5 | 8.1 | 436.7 | 442.8 | 531.2 | 157.4 | 580.2 | 611.4 | 297 | 156.2 | 408.9 | 649.8 | 407.6 | 471 | 646.6 | 383.4 | 438.6 | 621 | 517.4 | 382.3 | 322.3 | 307.7 | 332.2 | 352.4 | 305.1 | 325.4 | 341.7
2178 | 1957 | -6.7 | 0 | 0 | 397.3 | 296.2 | 302.3 | 300.4 | 354.3 | 58.5 | 17.2 | 91.7 | 5.7 | 239.1 | 8.3 | 436.8 | 442.9 | 527.9 | 156.8 | 580.1 | 611.5 | 296.6 | 155.9 | 408.1 | 649.4 | 407 | 471.3 | 646.4 | 382.5 | 437.7 | 620.8 | 517 | 382 | 322 | 307.3 | 331.8 | 352.1 | 304.9 | 325 | 341.4
2179 | 1958 | -6.7 | 0 | 0 | 399.2 | 296.1 | 301.9 | 300.2 | 354.1 | 58.3 | 17.2 | 91.7 | 5.7 | 241.6 | 8.5 | 436.9 | 443 | 529.4 | 156.9 | 580 | 611.5 | 296.2 | 155.6 | 407.4 | 649 | 406.8 | 470.9 | 646.1 | 381.6 | 436.1 | 620.6 | 517.3 | 381.6 | 321.6 | 307.1 | 331.5 | 351.7 | 304.7 | 324.7 | 341.1
2180 | 1959 | -6.7 | 0 | 0 | 400.8 | 295.8 | 301.6 | 300 | 353.1 | 58.1 | 17.2 | 91.6 | 4.7 | 247 | 7.7 | 436.9 | 443.1 | 529.8 | 156.7 | 579.9 | 611.7 | 296.5 | 155.1 | 406.6 | 648.5 | 407 | 470.5 | 645.8 | 381.3 | 438.2 | 620.4 | 516.7 | 381.2 | 321.2 | 306.7 | 331.2 | 351.4 | 304.4 | 324.4 | 340.8
2181 | 1960 | -6.7 | 0 | 0 | 400.1 | 295.6 | 301.3 | 300 | 352.4 | 58 | 17.2 | 91.5 | 5 | 245.6 | 7.2 | 437 | 443.1 | 529.7 | 156.6 | 579.9 | 611.9 | 297.1 | 154.7 | 405.8 | 647.9 | 406.1 | 471.5 | 645.4 | 381.3 | 441.3 | 620.2 | 516.6 | 380.8 | 320.9 | 306.4 | 330.8 | 351 | 304.2 | 324 | 340.4
2182 | 1961 | -6.7 | 0 | 0 | 399.1 | 295.5 | 301.1 | 299.8 | 352 | 57.9 | 17.2 | 91.5 | 5.3 | 246.8 | 7.5 | 437 | 443.1 | 530.5 | 156.6 | 579.8 | 612 | 297.8 | 154.7 | 405 | 647.5 | 407.7 | 471.4 | 645.1 | 380.3 | 441.4 | 620 | 516.3 | 380.4 | 320.6 | 306.2 | 330.5 | 350.7 | 303.9 | 323.6 | 340
2183 | 1962 | -6.7 | 0 | 0 | 397.4 | 295.4 | 301 | 299.6 | 351.7 | 57.8 | 17.2 | 91.4 | 5.1 | 241.9 | 7.9 | 437.1 | 443.2 | 533.5 | 156.3 | 579.7 | 611.9 | 298.7 | 154.8 | 404.3 | 647 | 408.7 | 471.4 | 644.7 | 379.2 | 441.2 | 619.8 | 515.9 | 379.9 | 320.3 | 305.9 | 330.2 | 350.3 | 303.6 | 323.2 | 339.7
2184 | 1963 | -6.7 | 0 | 0 | 396.6 | 295.2 | 300.9 | 299.4 | 351.2 | 57.6 | 17.2 | 91.3 | 4.9 | 253.1 | 8.4 | 437.1 | 443.2 | 536.3 | 155.5 | 579.6 | 611.9 | 299.2 | 154.5 | 403.5 | 646.5 | 409 | 471.1 | 644.3 | 378.4 | 436.1 | 619.6 | 514.9 | 379.5 | 320 | 305.7 | 329.8 | 350 | 303.3 | 322.9 | 339.3
2185 | 1964 | -6.7 | 0 | 0 | 394 | 295.1 | 301 | 299.4 | 350.6 | 57.6 | 17.2 | 91.3 | 4.3 | 244.9 | 8 | 437.2 | 443.3 | 544.2 | 154 | 579.5 | 611.7 | 298.7 | 153.5 | 402.9 | 646.1 | 408.9 | 470.4 | 644 | 377.5 | 431.5 | 619.4 | 514.3 | 379.2 | 319.7 | 305.5 | 329.5 | 349.7 | 303 | 322.6 | 339
2186 | 1965 | -6.7 | 0 | 0 | 393.6 | 294.9 | 300.9 | 299.4 | 350.6 | 57.5 | 17.2 | 91.2 | 4.2 | 242.5 | 8.1 | 437.3 | 443.4 | 541.2 | 153 | 579.4 | 611.5 | 297.6 | 152.4 | 402.2 | 645.8 | 409.2 | 469.9 | 643.8 | 377.2 | 429.3 | 619.1 | 514.2 | 378.8 | 319.5 | 305.5 | 329.2 | 349.4 | 302.8 | 322.3 | 338.7
2187 | 1966 | -6.7 | 0 | 0 | 395.6 | 294.8 | 300.7 | 299.1 | 350.3 | 57.4 | 17.2 | 91.1 | 5 | 234.6 | 7.3 | 437.3 | 443.5 | 537.7 | 152.7 | 579.3 | 611.1 | 295.8 | 151.9 | 401.4 | 645.4 | 409.7 | 467.8 | 643.6 | 376.1 | 425.6 | 618.8 | 513.4 | 378.4 | 319.3 | 305.6 | 328.9 | 349 | 302.4 | 322 | 338.4
2188 | 1967 | -6.7 | 0 | 0 | 396.3 | 294.5 | 300.4 | 298.5 | 350.2 | 57.3 | 17.2 | 91.1 | 4.3 | 239.8 | 6.7 | 437.4 | 443.5 | 540.1 | 152.4 | 579.2 | 610.8 | 293.4 | 151.2 | 400.7 | 645.1 | 407.4 | 466 | 643.1 | 375.2 | 422.3 | 618.5 | 512.5 | 378 | 318.9 | 305.4 | 328.6 | 348.7 | 302.1 | 321.8 | 338
2189 | 1968 | -6.7 | 0 | 0 | 397.1 | 294.3 | 300.2 | 298.1 | 349.6 | 57.3 | 17.2 | 91 | 4.2 | 239.3 | 6.8 | 437.5 | 443.6 | 538.9 | 152.1 | 579.2 | 610.4 | 291.3 | 150.3 | 400.1 | 644.8 | 405 | 464.2 | 642.7 | 374.7 | 420.4 | 618.1 | 511.7 | 377.6 | 318.6 | 305.2 | 328.3 | 348.3 | 301.8 | 321.6 | 337.7
2190 | 1969 | -6.7 | 0 | 0 | 395.9 | 294 | 299.9 | 298 | 349.3 | 57.2 | 17.2 | 90.9 | 4.2 | 263.5 | 5.9 | 437.6 | 443.6 | 533.7 | 152.1 | 579.1 | 610 | 288.6 | 149.5 | 399.4 | 644.8 | 403.2 | 462.3 | 642.2 | 373.8 | 418.5 | 617.8 | 511.2 | 377.2 | 318.2 | 304.8 | 328 | 348 | 301.5 | 321.6 | 337.3
2191 | 1970 | -6.7 | 0 | 0 | 393.6 | 293.8 | 299.6 | 297.9 | 348.9 | 57.2 | 17.2 | 90.8 | 4.8 | 243.6 | 5.9 | 437.6 | 443.7 | 527.9 | 151.6 | 579 | 609.6 | 286.6 | 149.5 | 398.6 | 644.7 | 402.4 | 459.8 | 641.7 | 373.5 | 416 | 617.4 | 510.3 | 376.8 | 318 | 304.6 | 327.7 | 347.6 | 301.2 | 321.2 | 337
2192 | 1971 | -6.7 | 0 | 0 | 392.6 | 293.6 | 299.2 | 297.6 | 348.8 | 57.1 | 17.2 | 90.7 | 4.3 | 267.5 | 6.3 | 437.7 | 443.7 | 526.7 | 151.3 | 578.9 | 609.3 | 285.6 | 149.7 | 397.8 | 644.6 | 400 | 459.2 | 641.2 | 373.4 | 418.1 | 617.1 | 510.1 | 376.5 | 317.7 | 304.4 | 327.4 | 347.2 | 300.8 | 320.9 | 336.6
2193 | 1972 | -6.7 | 0 | 0 | 395.7 | 293.3 | 298.9 | 297.4 | 348.1 | 57 | 17.2 | 90.6 | 4.7 | 239.1 | 6.6 | 437.8 | 443.7 | 525.1 | 151 | 578.8 | 608.9 | 283.9 | 149.8 | 397.1 | 644.6 | 398.8 | 458.5 | 640.8 | 374.3 | 422.8 | 616.8 | 510.6 | 376.1 | 317.6 | 304.1 | 327.2 | 346.8 | 300.5 | 320.5 | 336.3
2194 | 1973 | -6.7 | 0 | 0 | 399.1 | 293.1 | 298.7 | 297.4 | 348.2 | 56.9 | 17.2 | 90.5 | 4.6 | 238.9 | 7 | 437.8 | 443.8 | 530.6 | 151.1 | 578.7 | 608.3 | 282.1 | 149.9 | 396.3 | 644.6 | 398.2 | 457.9 | 640.2 | 375.1 | 423 | 616.4 | 510.4 | 375.6 | 317.4 | 303.8 | 326.8 | 346.5 | 300.2 | 320.2 | 335.9
2195 | 1974 | -6.7 | 0 | 0 | 397 | 292.9 | 298.4 | 296.9 | 348.1 | 56.8 | 17.2 | 90.4 | 4.8 | 255 | 7.6 | 437.9 | 443.8 | 533.7 | 151.1 | 578.7 | 607.9 | 280.8 | 149.8 | 395.5 | 644.4 | 398.9 | 457.1 | 639.7 | 374.8 | 429.1 | 616.1 | 510 | 375.3 | 317.1 | 303.5 | 326.5 | 346.2 | 299.9 | 319.9 | 335.6
2196 | 1975 | -6.7 | 0 | 0 | 394.8 | 292.7 | 298.2 | 296.3 | 347.6 | 56.7 | 17.2 | 90.4 | 4.6 | 236.8 | 7.8 | 437.9 | 443.8 | 528.7 | 150.8 | 578.6 | 607.6 | 280.2 | 149.7 | 394.8 | 644.2 | 398.3 | 456.9 | 639.2 | 374 | 428.9 | 615.9 | 509.4 | 374.9 | 316.8 | 303.3 | 326.3 | 345.8 | 299.7 | 319.7 | 335.3
2197 | 1976 | -6.7 | 0 | 0 | 391.2 | 292.5 | 298.1 | 295.9 | 346.8 | 56.6 | 17.2 | 90.3 | 4.6 | 249.9 | 7.6 | 438 | 443.9 | 528.5 | 150.8 | 578.5 | 607.2 | 279.4 | 149.5 | 393.9 | 643.8 | 398.5 | 456.6 | 638.9 | 372.9 | 426.9 | 615.6 | 508.8 | 374.5 | 316.5 | 303.1 | 325.9 | 345.5 | 299.4 | 319.4 | 335
2198 | 1977 | -6.7 | 0 | 0 | 388.9 | 292.4 | 297.9 | 295.6 | 346.1 | 56.5 | 17.2 | 90.3 | 5 | 246.6 | 7.3 | 438.1 | 444 | 531.8 | 150.7 | 578.5 | 606.9 | 279.2 | 148.9 | 393 | 643.5 | 398.3 | 456.4 | 638.6 | 373.1 | 435.5 | 615.4 | 510.1 | 374.1 | 316 | 302.7 | 325.6 | 345.1 | 299.2 | 319 | 334.6
2199 | 1978 | -6.7 | 0 | 0 | 387.7 | 292.3 | 297.9 | 295.2 | 346 | 56.4 | 17.2 | 90.2 | 5.1 | 266.5 | 6.5 | 438.2 | 444 | 533.9 | 150.4 | 578.4 | 606.8 | 279.3 | 148.4 | 392.1 | 643.1 | 398.7 | 457.2 | 638.2 | 373 | 435.7 | 615.2 | 510.1 | 373.7 | 315.6 | 302.5 | 325.2 | 344.8 | 298.9 | 318.6 | 334.3
2200 | 1979 | -6.7 | 0 | 0 | 384.1 | 292 | 297.3 | 294.6 | 346 | 56.4 | 17.2 | 90 | 5.2 | 246.3 | 6.3 | 438.2 | 444 | 535.5 | 150.1 | 578.3 | 606.5 | 278.2 | 147.9 | 391.3 | 642.8 | 397.6 | 457.2 | 637.9 | 372.3 | 433.7 | 615 | 509.4 | 373.3 | 315.4 | 302.2 | 324.9 | 344.5 | 298.6 | 318.2 | 334
2201 | 1980 | -6.7 | 0 | 0 | 382.4 | 291.7 | 296.7 | 294.4 | 345.7 | 56.3 | 17.2 | 89.9 | 4.7 | 245.7 | 6.7 | 438.3 | 444.1 | 530.8 | 149.6 | 578.2 | 606.2 | 278 | 147.8 | 390.5 | 642.5 | 397.3 | 455.7 | 637.6 | 372 | 433.3 | 614.7 | 509.5 | 372.9 | 315.2 | 301.9 | 324.6 | 344.1 | 298.4 | 317.8 | 333.7
2202 | 1981 | -6.7 | 0 | 0 | 381.8 | 291.4 | 296.3 | 294.1 | 344.7 | 56.2 | 17.2 | 89.8 | 4.8 | 242.7 | 7 | 438.3 | 444.2 | 527.7 | 149.2 | 578.1 | 605.8 | 278.2 | 147.9 | 389.7 | 642 | 396.3 | 454.2 | 637.3 | 371.7 | 429.5 | 614.5 | 509.3 | 372.5 | 314.9 | 301.8 | 324.3 | 343.7 | 298.1 | 317.3 | 333.4
2203 | 1982 | -6.7 | 0 | 0 | 380.6 | 291.2 | 295.8 | 293.6 | 344 | 56.2 | 17.3 | 89.7 | 4.6 | 244.1 | 7.4 | 438.4 | 444.2 | 531.5 | 148.7 | 578.1 | 605.3 | 277.7 | 148 | 388.9 | 641.5 | 394.5 | 453.2 | 637.1 | 370.9 | 425.3 | 614.2 | 508.6 | 372.1 | 314.7 | 301.5 | 324.1 | 343.4 | 297.9 | 317 | 333
2204 | 1983 | -6.7 | 0 | 0 | 380.1 | 290.9 | 295.4 | 293.1 | 343.3 | 56.2 | 17.3 | 89.6 | 4.6 | 242.4 | 8.3 | 438.5 | 444.2 | 532.1 | 148.5 | 578 | 604.9 | 277 | 147.7 | 388.1 | 640.9 | 393 | 453.1 | 636.8 | 369.7 | 423.8 | 613.9 | 508.2 | 371.7 | 314.4 | 301.2 | 323.7 | 343 | 297.7 | 316.6 | 332.7
2205 | 1984 | -6.7 | 0 | 0 | 379.3 | 290.6 | 294.9 | 293.1 | 342.9 | 56.1 | 17.3 | 89.5 | 4.5 | 247.9 | 9.9 | 438.6 | 444.3 | 533.1 | 148.4 | 577.9 | 604.6 | 275.9 | 147.5 | 387.3 | 640.5 | 392.6 | 453.1 | 636.4 | 367.9 | 422 | 613.6 | 508.2 | 371.3 | 314.1 | 300.8 | 323.4 | 342.7 | 297.3 | 316.2 | 332.3
2206 | 1985 | -6.7 | 0 | 0 | 382.1 | 290.4 | 294.4 | 292.8 | 343.2 | 56 | 17.3 | 89.4 | 4.7 | 240.7 | 10.2 | 438.6 | 444.3 | 533.4 | 148.2 | 577.8 | 604.2 | 275.7 | 147.5 | 386.5 | 640.1 | 393 | 453.7 | 636 | 366.7 | 424.6 | 613.3 | 507.9 | 370.9 | 313.8 | 300.4 | 323.1 | 342.3 | 296.9 | 315.9 | 332
2207 | 1986 | -6.7 | 0 | 0 | 382.3 | 290.1 | 293.7 | 292.6 | 342.5 | 55.9 | 17.3 | 89.3 | 4.9 | 243.5 | 9.5 | 438.7 | 444.3 | 535.2 | 147.9 | 577.7 | 603.8 | 275.1 | 147.6 | 385.8 | 639.7 | 393.3 | 454.1 | 635.7 | 367.2 | 428.5 | 613.1 | 508 | 370.4 | 313.6 | 300 | 322.8 | 342 | 296.6 | 315.6 | 331.7
2208 | 1987 | -6.7 | 0 | 0 | 381.8 | 289.9 | 293.6 | 292.6 | 342.1 | 55.9 | 17.3 | 89.2 | 5.2 | 242.7 | 8.8 | 438.8 | 444.3 | 534.2 | 147.8 | 577.6 | 603.5 | 275.2 | 147.4 | 385 | 639.2 | 393.1 | 453.9 | 635.4 | 367.5 | 426.9 | 612.9 | 508 | 370 | 313.3 | 299.5 | 322.4 | 341.7 | 296.2 | 315.4 | 331.4
2209 | 1988 | -6.7 | 0 | 0 | 381.7 | 289.6 | 293.6 | 292.7 | 341.5 | 55.9 | 17.3 | 89.1 | 4.7 | 244.3 | 8.9 | 438.9 | 444.4 | 528.9 | 147.6 | 577.5 | 603.3 | 274.6 | 147 | 384.2 | 638.8 | 393 | 453.5 | 635 | 367 | 429.3 | 612.7 | 507.8 | 369.6 | 312.9 | 299.1 | 322 | 341.4 | 296 | 315.2 | 331.1
2210 | 1989 | -6.7 | 0 | 0 | 379.9 | 289.2 | 293.5 | 292.4 | 340.9 | 55.8 | 17.3 | 89 | 5 | 246.3 | 9.6 | 438.9 | 444.4 | 524.6 | 147 | 577.4 | 603.1 | 273.9 | 146.4 | 383.4 | 638.3 | 392.7 | 452.9 | 634.7 | 365.5 | 426.7 | 612.5 | 507.4 | 369.2 | 312.4 | 298.7 | 321.7 | 341 | 295.7 | 314.9 | 330.7
2211 | 1990 | -6.7 | 0 | 0 | 378.3 | 288.9 | 293.3 | 292.1 | 340.5 | 55.7 | 17.3 | 88.9 | 5.3 | 248.1 | 9.6 | 439 | 444.4 | 527.1 | 146.6 | 577.2 | 603 | 272.9 | 145.6 | 382.5 | 637.8 | 391.3 | 452.2 | 634.3 | 364 | 423.5 | 612.3 | 507.2 | 368.8 | 312 | 298.4 | 321.3 | 340.6 | 295.5 | 314.6 | 330.4
2212 | 1991 | -6.7 | 0 | 0 | 378.9 | 288.6 | 293.1 | 291.7 | 339.5 | 55.6 | 17.3 | 88.8 | 5.8 | 241.4 | 9.4 | 439.1 | 444.3 | 526 | 146.3 | 577.1 | 602.6 | 272.3 | 144.8 | 381.6 | 637.3 | 391.1 | 451.9 | 634 | 363.5 | 419.8 | 612 | 506.9 | 368.3 | 311.6 | 298.2 | 321.1 | 340.3 | 295.2 | 314.3 | 330.1
2213 | 1992 | -6.7 | 0 | 0 | 379 | 288.3 | 292.6 | 291.2 | 338.6 | 55.5 | 17.3 | 88.7 | 5.3 | 244.7 | 8.1 | 439.2 | 444.4 | 523.4 | 145.9 | 577 | 602.2 | 271.6 | 144.7 | 380.9 | 636.9 | 391.3 | 451.4 | 633.6 | 362.3 | 414.9 | 611.7 | 506 | 368 | 311.3 | 297.8 | 320.8 | 339.9 | 294.9 | 314 | 329.8
2214 | 1993 | -6.7 | 0 | 0 | 377.9 | 288 | 292.5 | 291.2 | 338 | 55.3 | 17.3 | 88.6 | 5.2 | 253.7 | 6.6 | 439.3 | 444.5 | 522.4 | 145.7 | 576.9 | 602 | 271.3 | 144.7 | 380.1 | 636.5 | 391.8 | 450.5 | 633.2 | 361.8 | 411.5 | 611.4 | 505.4 | 367.6 | 310.9 | 297.5 | 320.4 | 339.5 | 294.6 | 313.6 | 329.5
2215 | 1994 | -6.7 | 0 | 0 | 377.1 | 287.8 | 292.5 | 291 | 337.8 | 55.2 | 17.3 | 88.5 | 4.5 | 226 | 5.4 | 439.4 | 444.4 | 521.1 | 145.4 | 576.8 | 601.8 | 270.5 | 144.9 | 379.4 | 636.1 | 391.1 | 451.2 | 632.7 | 362.1 | 409.7 | 611.1 | 504.7 | 367.2 | 310.5 | 297.1 | 320.1 | 339.1 | 294.3 | 313.3 | 329.2
2216 | 1995 | -6.7 | 0 | 0 | 376.7 | 287.7 | 292.2 | 290.8 | 338.6 | 55.1 | 17.3 | 88.4 | 4.5 | 239 | 6 | 439.4 | 444.4 | 522.1 | 145.3 | 576.6 | 601.6 | 268.6 | 145.2 | 378.8 | 635.6 | 390.7 | 451 | 632.4 | 362.6 | 405.7 | 610.9 | 504 | 366.8 | 310.1 | 296.8 | 319.8 | 338.8 | 294.1 | 312.9 | 328.8
2217 | 1996 | -6.7 | 0 | 0 | 374.9 | 287.5 | 292 | 290.6 | 338.5 | 55 | 17.3 | 88.3 | 4.3 | 245.1 | 7.6 | 439.5 | 444.4 | 523 | 145.1 | 576.5 | 601.2 | 268.4 | 145.5 | 378.1 | 635.2 | 390.2 | 450.9 | 632.1 | 362.3 | 404.2 | 610.6 | 503.5 | 366.4 | 309.7 | 296.6 | 319.5 | 338.5 | 293.8 | 312.5 | 328.5
2218 | 1997 | -6.7 | 0 | 0 | 374.7 | 287.3 | 291.7 | 290.2 | 338.2 | 54.9 | 17.3 | 88.2 | 5 | 246.1 | 8.8 | 439.6 | 444.5 | 518.7 | 144.9 | 576.4 | 600.8 | 268.3 | 145.8 | 377.4 | 634.7 | 388.9 | 449.9 | 631.7 | 362.2 | 400.8 | 610.4 | 502.6 | 366 | 309.4 | 296.4 | 319.3 | 338.1 | 293.6 | 312.5 | 328.2
2219 | 1998 | -6.5 | 0 | 0 | 377.2 | 287.1 | 291.5 | 289.8 | 338.6 | 54.8 | 17.3 | 88.1 | 5.1 | 231.7 | 8.3 | 439.7 | 444.7 | 511.4 | 144.7 | 576.2 | 600.5 | 268.5 | 145.9 | 376.7 | 634.3 | 388.3 | 449.5 | 631.3 | 362 | 397.1 | 610.2 | 501.9 | 365.7 | 309.2 | 296.2 | 319.1 | 337.7 | 293.4 | 312.2 | 327.9
2220 | 1999 | -6.6 | 0 | 0 | 376.7 | 287 | 291.3 | 289.4 | 338.5 | 54.8 | 17.3 | 88 | 4.5 | 222.5 | 8 | 439.8 | 444.8 | 507.2 | 144.6 | 576.1 | 600.3 | 267.5 | 146 | 376.1 | 633.9 | 387.6 | 450.1 | 630.9 | 362 | 397.5 | 610 | 501.4 | 365.3 | 309.2 | 296.2 | 318.8 | 337.4 | 293.2 | 312 | 327.6
2221 | 2000 | -6.7 | 0 | 0 | 375.2 | 286.8 | 291 | 288.9 | 338.8 | 54.7 | 17.3 | 87.9 | 4.6 | 226.8 | 7.2 | 439.9 | 444.9 | 510.3 | 144.3 | 576 | 600.2 | 266.3 | 146.2 | 375.4 | 633.4 | 386.8 | 450.3 | 630.5 | 362.4 | 397.2 | 609.7 | 500.9 | 364.9 | 309.1 | 296.1 | 318.6 | 337.1 | 292.9 | 311.7 | 327.3
2222 | 2001 | -6.7 | 0 | 0 | 373.7 | 286.6 | 290.9 | 288.7 | 338.5 | 54.7 | 17.3 | 87.8 | 4.9 | 235.5 | 6.6 | 440 | 444.9 | 515.2 | 144.2 | 575.8 | 599.9 | 264.9 | 146.6 | 374.7 | 633 | 386.6 | 450.7 | 630.1 | 362.7 | 402.6 | 609.4 | 500.5 | 364.6 | 308.8 | 295.8 | 318.3 | 336.7 | 292.7 | 311.9 | 327
2223 | 2002 | -6.7 | 0 | 0 | 373.9 | 286.5 | 290.9 | 288.5 | 338 | 54.6 | 17.3 | 87.7 | 4.6 | 235.2 | 7.2 | 440.1 | 445.1 | 515.8 | 143.8 | 575.7 | 599.8 | 264.1 | 146.9 | 374 | 632.8 | 387.1 | 450.9 | 629.8 | 362.7 | 402 | 609.2 | 500.1 | 364.2 | 308.5 | 295.6 | 318 | 336.4 | 292.4 | 311.9 | 326.7
2224 | 2003 | -6.7 | 0 | 0 | 376.1 | 286.2 | 290.8 | 288.3 | 337.7 | 54.6 | 17.3 | 87.6 | 4.5 | 231.7 | 7.5 | 440.1 | 445.1 | 515.7 | 142.9 | 575.6 | 599.6 | 262.8 | 146.9 | 373.3 | 632.6 | 387.6 | 450.5 | 629.4 | 362.6 | 401.1 | 609 | 499.8 | 363.9 | 308.1 | 295.3 | 317.6 | 336.1 | 292.2 | 311.4 | 326.4
2225 | 2004 | -6.7 | 0 | 0 | 377.3 | 285.9 | 290.4 | 288 | 337.5 | 54.5 | 17.3 | 87.5 | 4.5 | 223.3 | 7 | 440.2 | 445.2 | 510.2 | 142.1 | 575.5 | 599.2 | 262.8 | 146.4 | 372.6 | 632.5 | 388.4 | 450.6 | 629 | 362.9 | 399 | 608.7 | 499 | 363.5 | 307.8 | 295 | 317.3 | 335.8 | 291.9 | 311 | 326.1
2226 | 2005 | -6.7 | 0 | 0 | 377.1 | 285.7 | 290.2 | 287.7 | 337 | 54.5 | 17.3 | 87.4 | 4.1 | 239.3 | 7.3 | 440.3 | 445.5 | 513 | 141.6 | 575.4 | 598.9 | 262 | 146.1 | 371.9 | 632.2 | 388.3 | 452.5 | 628.6 | 362.4 | 402.2 | 608.5 | 499.2 | 363.1 | 307.6 | 294.7 | 317 | 335.5 | 291.7 | 310.7 | 325.8
2227 | 2006 | -6.7 | 0 | 0 | 380 | 285.6 | 290.1 | 287.6 | 336.5 | 54.6 | 17.3 | 87.3 | 4.4 | 250.8 | 7.6 | 440.4 | 445.6 | 509.7 | 141 | 575.2 | 598.6 | 262.2 | 145.9 | 371.3 | 632 | 387.8 | 452.4 | 628.2 | 363.2 | 403.1 | 608.3 | 499.5 | 362.7 | 307.3 | 294.4 | 316.7 | 335.1 | 291.5 | 310.4 | 325.5
2228 | 2007 | -6.7 | 0 | 0 | 383.7 | 285.4 | 290.1 | 287.6 | 336.6 | 54.6 | 17.3 | 87.2 | 4.4 | 251.8 | 7.5 | 440.4 | 445.8 | 510.1 | 140.7 | 575.1 | 598.4 | 260.7 | 145.8 | 370.7 | 631.8 | 388 | 451.7 | 627.8 | 363.1 | 403.8 | 608.1 | 499.9 | 362.3 | 307 | 294.1 | 316.3 | 334.8 | 291.2 | 310 | 325.2
2229 | 2008 | -6.7 | 0 | 0 | 385.6 | 285.1 | 289.8 | 287.6 | 335.8 | 54.6 | 17.4 | 87.1 | 4.3 | 255 | 7 | 440.5 | 445.9 | 509.9 | 140.2 | 575 | 598.1 | 259.4 | 145.7 | 370 | 631.7 | 387.7 | 451.4 | 627.3 | 363.2 | 404.1 | 607.9 | 500 | 362 | 306.7 | 293.7 | 316 | 334.6 | 291.1 | 309.8 | 324.9
2230 | 2009 | -6.7 | 0 | 0 | 386.6 | 284.8 | 289.6 | 287.5 | 334.9 | 54.5 | 17.3 | 87 | 4.3 | 230 | 7.1 | 440.6 | 446.1 | 510.1 | 139.6 | 574.9 | 597.8 | 258.6 | 145.3 | 369.2 | 631.6 | 387.6 | 450.4 | 626.8 | 362.5 | 402.3 | 607.7 | 499.8 | 361.6 | 306.4 | 293.4 | 315.7 | 334.3 | 291 | 309.5 | 324.6
2231 | 2010 | -6.7 | 0 | 0 | 384.6 | 284.5 | 289.4 | 287.4 | 334.4 | 54.4 | 17.4 | 86.9 | 4.2 | 243.2 | 7.6 | 440.7 | 446.2 | 508.8 | 139.3 | 574.8 | 597.4 | 257.3 | 145.1 | 368.6 | 631.4 | 386.7 | 449.9 | 626.4 | 361.6 | 401.5 | 607.4 | 499.4 | 361.2 | 306.2 | 293.2 | 315.4 | 334 | 290.7 | 309.3 | 324.3
2232 | 2011 | -6.7 | 0 | 0 | 382.8 | 284.3 | 289.3 | 287.3 | 334.1 | 54.3 | 17.4 | 86.8 | 4.5 | 239.6 | 8.3 | 440.8 | 446.3 | 511.7 | 139.1 | 574.7 | 597.2 | 256.6 | 144.9 | 367.9 | 631.3 | 386.7 | 450.1 | 625.9 | 360.9 | 411.4 | 607.2 | 499.3 | 360.8 | 305.9 | 293 | 315.2 | 333.7 | 290.5 | 309.1 | 324
2233 | 2012 | -6.7 | 0 | 0 | 380.5 | 284.1 | 289.2 | 287 | 333.8 | 54.3 | 17.4 | 86.8 | 4.6 | 248.3 | 8.3 | 440.8 | 446.4 | 507.7 | 138.9 | 574.6 | 596.9 | 255.1 | 144.9 | 367.2 | 631.1 | 386.9 | 451.6 | 625.5 | 360 | 412.1 | 607 | 499.1 | 360.4 | 305.7 | 292.9 | 314.9 | 333.4 | 290.2 | 309 | 323.7
2234 | 2013 | -6.7 | 0 | 0 | 378.7 | 283.8 | 288.9 | 286.7 | 333.5 | 54.2 | 17.4 | 86.7 | 4.7 | 240 | 8 | 440.9 | 446.5 | 505.3 | 138.9 | 574.4 | 596.6 | 254 | 144.7 | 366.5 | 631 | 386.1 | 450.9 | 625.2 | 358.8 | 414 | 606.7 | 499.5 | 360 | 305.4 | 292.7 | 314.7 | 333.1 | 290 | 308.9 | 323.4
2235 | 2014 | -6.7 | 0 | 0 | 377.9 | 283.5 | 288.6 | 286.2 | 333.4 | 54 | 17.4 | 86.7 | 4.5 | 244.3 | 7.6 | 441 | 446.5 | 503.3 | 138.8 | 574.3 | 596.3 | 252.9 | 145.1 | 365.9 | 630.8 | 385.7 | 449.9 | 624.8 | 358.1 | 413.9 | 606.5 | 499.4 | 359.7 | 305.1 | 292.5 | 314.4 | 332.8 | 289.8 | 308.8 | 323.1
2236 | 2015 | -6.7 | 0 | 0 | 381.3 | 283.4 | 288.2 | 286 | 332.9 | 53.9 | 17.4 | 86.7 | 4.2 | 241.7 | 7.3 | 441.1 | 446.6 | 504.8 | 138.4 | 574.2 | 596 | 252.4 | 145.1 | 365.3 | 630.6 | 385 | 449 | 624.4 | 356.3 | 413.9 | 606.3 | 499.6 | 359.3 | 304.8 | 292.4 | 314.1 | 332.4 | 289.6 | 308.3 | 322.8
2237 | 2016 | -6.7 | 0 | 0 | 381.1 | 283.3 | 288 | 285.6 | 332.5 | 53.8 | 17.4 | 86.6 | 4.4 | 241.8 | 6.9 | 441.2 | 446.7 | 502.8 | 137.8 | 574.1 | 595.7 | 251.5 | 144.8 | 364.7 | 630.5 | 384.5 | 448.2 | 624 | 355.5 | 411.9 | 606 | 499.2 | 358.9 | 304.6 | 292.2 | 313.8 | 332.2 | 289.4 | 307.9 | 322.5
2238 | 2017 | -6.7 | 0 | 0 | 378.9 | 283.2 | 287.6 | 285.4 | 332.1 | 53.6 | 17.4 | 86.6 | 4.6 | 241.9 | 7.1 | 441.2 | 447 | 500.1 | 137.4 | 574 | 595.4 | 251.4 | 144.8 | 364.1 | 630.3 | 383.7 | 448 | 623.6 | 355 | 411.3 | 605.7 | 499 | 358.5 | 304.3 | 292 | 313.5 | 331.8 | 289.1 | 307.7 | 322.3
2239 | 2018 | -6.7 | 0 | 0 | 376 | 283.1 | 287.2 | 285.1 | 331.9 | 53.6 | 17.4 | 86.6 | 4.7 | 247.7 | 7.6 | 441.3 | 447.1 | 500.5 | 137 | 573.9 | 595 | 250.2 | 145 | 363.5 | 630.2 | 383.8 | 447.2 | 623.2 | 355.1 | 413.5 | 605.5 | 498.9 | 358.2 | 304.1 | 291.6 | 313.2 | 331.5 | 288.9 | 307.3 | 321.9
2240 | 2019 | -6.7 | 0 | 0 | 373.9 | 282.8 | 287 | 284.9 | 332.1 | 53.5 | 17.4 | 86.6 | 4.4 | 242.9 | 7.4 | 441.4 | 447.3 | 503.3 | 136.4 | 573.8 | 594.8 | 249.7 | 145.1 | 362.9 | 630.3 | 384.7 | 446.6 | 622.9 | 354.5 | 413.9 | 605.2 | 499.1 | 357.8 | 303.6 | 291.3 | 312.9 | 331.2 | 288.7 | 307 | 321.6
2241 | 2020 | -6.7 | 0 | 0 | 374.6 | 282.6 | 286.6 | 284.6 | 332 | 53.4 | 17.4 | 86.5 | 4.2 | 247 | 7.2 | 441.5 | 447.5 | 502.1 | 135.9 | 573.6 | 594.4 | 249.5 | 145 | 362.2 | 630.3 | 384.7 | 447 | 622.6 | 352.4 | 412.3 | 605 | 498.5 | 357.4 | 303.3 | 290.9 | 312.6 | 330.9 | 288.5 | 306.7 | 321.3
2242 | 2021 | -6.7 | 0 | 0 | 375.7 | 282.4 | 286.2 | 284.1 | 331.6 | 53.3 | 17.4 | 86.5 | 4.3 | 244.1 | 6.8 | 441.6 | 447.7 | 503 | 135.5 | 573.5 | 594 | 248.8 | 145 | 361.6 | 630.4 | 383.9 | 447 | 622.2 | 350.6 | 408.7 | 604.7 | 497.8 | 357 | 303 | 290.7 | 312.3 | 330.6 | 288.3 | 306.6 | 321
2243 | 2022 | -6.6 | 0 | 0 | 375.8 | 282.2 | 286 | 283.9 | 330.8 | 53.3 | 17.4 | 86.4 | 4.4 | 252.1 | 6.2 | 441.6 | 447.8 | 501.7 | 135.2 | 573.4 | 593.7 | 246.7 | 144.7 | 361 | 630.5 | 383.1 | 447.3 | 621.9 | 348.9 | 409.8 | 604.5 | 498 | 356.6 | 302.7 | 290.4 | 312.1 | 330.3 | 288.1 | 306.3 | 320.7
2244 | 2023 | -6.3 | 0 | 0 | 375.9 | 282 | 286 | 283.6 | 330.1 | 53.2 | 17.4 | 86.4 | 4.1 | 246.7 | 6 | 441.7 | 447.9 | 498.2 | 135 | 573.3 | 593.3 | 245.1 | 143.5 | 360.4 | 630.5 | 382.5 | 446.2 | 621.6 | 347.2 | 413.4 | 604.2 | 498.8 | 356.2 | 302.5 | 290.1 | 311.8 | 329.9 | 287.9 | 305.9 | 320.4
2245 | 2024 | -6.7 | 0 | 0 | 374.8 | 281.9 | 285.7 | 283.2 | 329.9 | 53.1 | 17.4 | 86.3 | 4.2 | 259 | 5.8 | 441.8 | 448.1 | 495 | 134.9 | 573.1 | 593 | 243.7 | 142.4 | 359.9 | 630.5 | 382.4 | 444.9 | 621.2 | 346.1 | 412.2 | 603.9 | 498.5 | 355.8 | 302.2 | 289.9 | 311.5 | 329.7 | 287.5 | 305.6 | 320.1
2246 | 2025 | -6.7 | 0 | 0 | 371.5 | 281.7 | 285.5 | 282.9 | 329.3 | 53.1 | 17.4 | 86.2 | 4.1 | 255.9 | 5.7 | 441.8 | 448.3 | 494.4 | 134.2 | 573 | 592.7 | 242.1 | 141.1 | 359.3 | 630.5 | 381.5 | 445.6 | 620.8 | 344.7 | 412.5 | 603.7 | 498.3 | 355.4 | 301.9 | 289.8 | 311.3 | 329.4 | 287.1 | 305.4 | 319.8
2247 | 2026 | -6.7 | 0 | 0 | 369.4 | 281.5 | 285.4 | 282.1 | 328.7 | 53.1 | 17.4 | 86.1 | 3.8 | 244.3 | 5.7 | 441.9 | 448.4 | 492.5 | 133.4 | 572.9 | 592.4 | 240.8 | 139.9 | 358.7 | 630.3 | 381.4 | 444 | 620.4 | 343.6 | 408.8 | 603.4 | 497.8 | 355 | 301.5 | 289.7 | 311 | 329 | 286.8 | 305 | 319.5
2248 | 2027 | -6.7 | 0 | 0 | 366.6 | 281.2 | 284.8 | 281.5 | 328 | 53.1 | 17.4 | 86.1 | 4.1 | 251.5 | 5.5 | 442 | 448.6 | 496.5 | 132.9 | 572.8 | 592 | 239.3 | 139.6 | 358.2 | 630.1 | 379.8 | 441.8 | 620 | 342.8 | 404 | 603.1 | 496.6 | 354.6 | 301.1 | 289.3 | 310.6 | 328.7 | 286.5 | 304.6 | 319.2
2249 | 2028 | -6.7 | 0 | 0 | 364.2 | 280.9 | 284.2 | 281.3 | 327.7 | 53.1 | 17.4 | 86.1 | 4.1 | 237.8 | 5 | 442.1 | 448.7 | 494.4 | 132.5 | 572.6 | 591.7 | 238.4 | 139.9 | 357.8 | 629.9 | 378.4 | 440.4 | 619.7 | 342.1 | 400.8 | 602.8 | 495.6 | 354.2 | 300.9 | 288.9 | 310.3 | 328.3 | 286.1 | 304.2 | 318.9
2250 | 2029 | -6.7 | 0 | 0 | 362.2 | 280.6 | 283.9 | 281 | 327.4 | 53 | 17.4 | 86 | 4.2 | 237.8 | 4.6 | 442.1 | 448.9 | 495.6 | 132.1 | 572.5 | 591.4 | 238.1 | 139.9 | 357.2 | 629.5 | 377.4 | 438.4 | 619.3 | 342.3 | 396.8 | 602.5 | 494.7 | 353.7 | 300.5 | 288.6 | 310 | 328 | 285.8 | 303.8 | 318.6
2251 | 2030 | -6.7 | 0 | 0 | 360.3 | 280.5 | 283.7 | 280.4 | 327.6 | 53.1 | 17.4 | 86 | 3.7 | 241.3 | 4.7 | 442.2 | 449 | 496 | 131.6 | 572.4 | 591.1 | 236.7 | 139.1 | 356.6 | 629 | 375.5 | 436.9 | 618.9 | 342.3 | 393.4 | 602.2 | 493.6 | 353.3 | 300.2 | 288.3 | 309.7 | 327.7 | 285.5 | 303.4 | 318.3
2252 | 2031 | -6.7 | 0 | 0 | 358.8 | 280.2 | 283.3 | 279.8 | 327.3 | 53.2 | 17.4 | 85.9 | 3.9 | 255.5 | 4.6 | 442.3 | 449.2 | 490.8 | 131.2 | 572.2 | 590.8 | 236.5 | 138.5 | 356.1 | 628.4 | 373.5 | 435.2 | 618.5 | 342.4 | 389.7 | 601.9 | 492.6 | 352.9 | 299.8 | 288 | 309.4 | 327.3 | 285.2 | 303 | 318
2253 | 2032 | -6.7 | 0 | 0 | 359.9 | 279.9 | 283.1 | 279.6 | 327.5 | 53.2 | 17.4 | 85.9 | 3.7 | 251.8 | 4.6 | 442.4 | 449.4 | 487.7 | 130.7 | 572.1 | 590.5 | 235.6 | 138.2 | 355.6 | 627.8 | 373 | 434.2 | 618.1 | 342.8 | 386.4 | 601.6 | 491.7 | 352.5 | 299.4 | 287.6 | 309.1 | 327 | 284.9 | 302.7 | 317.7
2254 | 2033 | -6.7 | 0 | 0 | 359.3 | 279.7 | 282.9 | 279.5 | 328.1 | 53.2 | 17.4 | 85.8 | 3.7 | 235.3 | 4.3 | 442.5 | 449.5 | 486.8 | 130.2 | 571.9 | 590.2 | 235.6 | 138 | 355 | 627 | 373.1 | 433.5 | 617.6 | 342.9 | 385.7 | 601.4 | 490.8 | 352.1 | 299.1 | 287.5 | 308.8 | 326.7 | 284.5 | 302.4 | 317.4
2255 | 2034 | -6.7 | 0 | 0 | 357.5 | 279.4 | 282.8 | 279.4 | 327.7 | 53.2 | 17.4 | 85.7 | 4 | 246.2 | 4.5 | 442.5 | 449.7 | 485.4 | 129.8 | 571.8 | 590 | 237.1 | 137.5 | 354.4 | 626.3 | 372.2 | 433.1 | 617.1 | 342.5 | 383.6 | 601.1 | 490.1 | 351.8 | 298.8 | 287.3 | 308.6 | 326.4 | 284.2 | 302.1 | 317.1
2256 | 2035 | -6.7 | 0 | 0 | 356.6 | 279.2 | 282.7 | 279.3 | 326.8 | 53 | 17.4 | 85.6 | 4.4 | 250.9 | 5.2 | 442.6 | 449.9 | 485 | 129.7 | 571.6 | 589.9 | 237.7 | 136.9 | 353.7 | 625.6 | 371.6 | 433.7 | 616.7 | 342.5 | 382.4 | 600.9 | 489.9 | 351.4 | 298.7 | 287.1 | 308.4 | 326.1 | 283.9 | 302 | 316.8
2257 | 2036 | -6.7 | 0 | 0 | 357.3 | 279.1 | 282.3 | 279.2 | 326.6 | 52.8 | 17.4 | 85.5 | 4 | 246.9 | 5.4 | 442.7 | 450.1 | 490.8 | 129.9 | 571.4 | 589.9 | 237.8 | 136.2 | 353.1 | 625.2 | 371.8 | 434 | 616.2 | 343.1 | 381.3 | 600.7 | 489.3 | 351 | 298.4 | 287 | 308.1 | 325.8 | 283.6 | 302.1 | 316.5
2258 | 2037 | -6.7 | 0 | 0 | 361.5 | 278.8 | 281.9 | 278.7 | 326.4 | 52.7 | 17.5 | 85.4 | 4 | 247.4 | 5.1 | 442.7 | 450.2 | 490.5 | 129.7 | 571.3 | 589.8 | 237.9 | 135.8 | 352.4 | 624.8 | 371.7 | 433.6 | 615.8 | 343.9 | 380.6 | 600.6 | 488.8 | 350.7 | 298 | 286.9 | 307.9 | 325.4 | 283.3 | 301.7 | 316.2
2259 | 2038 | -6.7 | 0 | 0 | 368 | 278.6 | 281.3 | 278.5 | 326.6 | 52.6 | 17.5 | 85.4 | 3.9 | 245.5 | 5 | 442.8 | 450.3 | 490.5 | 129.6 | 571.1 | 589.6 | 239.1 | 135.4 | 351.8 | 624.5 | 372.2 | 433.2 | 615.5 | 344 | 379.3 | 600.4 | 488.3 | 350.3 | 297.8 | 286.6 | 307.5 | 325.1 | 283.1 | 301.3 | 315.9
2260 | 2039 | -6.7 | 0 | 0 | 370.9 | 278.4 | 280.9 | 278.4 | 326.7 | 52.5 | 17.5 | 85.3 | 4 | 244.7 | 4.7 | 442.9 | 450.5 | 499.9 | 129 | 571 | 589.5 | 240 | 134.5 | 351.1 | 624.1 | 371.4 | 432.8 | 615.1 | 343.9 | 379.5 | 600.3 | 487.6 | 349.9 | 297.6 | 286.3 | 307.2 | 324.8 | 282.9 | 300.9 | 315.6
2261 | 2040 | -6.6 | 0 | 0 | 375 | 278.2 | 280.9 | 278.3 | 326.2 | 52.5 | 17.5 | 85.3 | 4.2 | 245.1 | 4.8 | 442.9 | 450.6 | 506.2 | 127.7 | 570.8 | 589.3 | 239.8 | 133.4 | 350.5 | 623.7 | 371.8 | 433 | 614.7 | 343 | 379.4 | 600.2 | 487 | 349.6 | 297.4 | 285.9 | 306.9 | 324.4 | 282.6 | 300.7 | 315.3
2262 | 2041 | -6.7 | 0 | 0 | 382.7 | 278 | 280.9 | 278.3 | 325.7 | 52.5 | 17.5 | 85.2 | 4.1 | 246.8 | 5.1 | 443 | 450.7 | 511.5 | 126.8 | 570.6 | 589.1 | 240.5 | 132.3 | 349.9 | 623.3 | 372.2 | 433.1 | 614.3 | 343.6 | 379.9 | 600.1 | 486.6 | 349.2 | 297.2 | 285.5 | 306.6 | 324.1 | 282.4 | 300.5 | 315.1
2263 | 2042 | -6.7 | 0 | 0 | 382.6 | 277.8 | 281 | 278.3 | 325.4 | 52.4 | 17.5 | 85.2 | 4.3 | 249.6 | 5.3 | 443.1 | 450.8 | 512.5 | 126.3 | 570.5 | 588.9 | 240.2 | 131.7 | 349.3 | 623 | 372.6 | 431.9 | 613.9 | 343.8 | 378.1 | 599.9 | 485.9 | 348.8 | 296.9 | 285.1 | 306.4 | 323.8 | 282.2 | 300.2 | 314.8
2264 | 2043 | -6.7 | 0 | 0 | 380 | 277.5 | 281 | 278.4 | 325 | 52.3 | 17.5 | 85.2 | 4.2 | 249 | 5 | 443.1 | 450.9 | 513.3 | 126 | 570.3 | 588.8 | 239.3 | 130.8 | 348.6 | 622.7 | 372.6 | 431.3 | 613.5 | 343 | 375.4 | 599.7 | 485.3 | 348.5 | 296.7 | 284.8 | 306.1 | 323.5 | 282 | 299.9 | 314.5
2265 | 2044 | -6.7 | 0 | 0 | 376 | 277.4 | 280.8 | 278.3 | 324.6 | 52.2 | 17.5 | 85.1 | 3.9 | 251.6 | 4.9 | 443.2 | 450.9 | 515.4 | 125.8 | 570.1 | 588.5 | 238.5 | 130.1 | 347.9 | 622.5 | 372 | 430.8 | 613.1 | 343 | 373.3 | 599.5 | 484.8 | 348.1 | 296.4 | 284.7 | 306 | 323.3 | 281.8 | 299.7 | 314.2
2266 | 2045 | -6.7 | 0 | 0 | 376.1 | 277.3 | 280.6 | 278 | 324.4 | 52.2 | 17.5 | 85.1 | 4 | 252.2 | 5.1 | 443.3 | 451 | 510.5 | 125.3 | 570 | 588.2 | 238 | 129.5 | 347.4 | 622.2 | 370.8 | 429 | 612.6 | 343 | 372.3 | 599.3 | 484.4 | 347.8 | 296.1 | 284.6 | 305.7 | 323 | 281.7 | 300 | 313.9
2267 | 2046 | -6.7 | 0 | 0 | 381.5 | 277.3 | 280.3 | 277.7 | 324.3 | 52.2 | 17.5 | 85 | 3.4 | 249.8 | 5.3 | 443.4 | 451.2 | 512.8 | 124.6 | 569.8 | 588 | 237.3 | 128.6 | 346.8 | 621.9 | 370.2 | 428.9 | 612.1 | 342.6 | 371.3 | 599.1 | 484.2 | 347.4 | 295.8 | 284.3 | 305.3 | 322.7 | 281.4 | 299.6 | 313.5
2268 | 2047 | -6.7 | 0 | 0 | 386.2 | 277.2 | 279.8 | 277.6 | 323.9 | 52.3 | 17.5 | 85 | 3.6 | 245.9 | 5.2 | 443.4 | 451.3 | 515.9 | 123.8 | 569.6 | 587.9 | 237 | 127.6 | 346 | 621.6 | 370.7 | 429.8 | 611.7 | 342.8 | 372.7 | 599 | 483.8 | 347.1 | 295.5 | 284 | 305 | 322.4 | 281.1 | 299.4 | 313.3
2269 | 2048 | -6.7 | 0 | 0 | 390.9 | 276.9 | 279.5 | 277.6 | 323.2 | 52.3 | 17.5 | 84.9 | 3.6 | 230 | 5.2 | 443.5 | 451.3 | 515.7 | 123.5 | 569.5 | 587.8 | 236.8 | 127.3 | 345.4 | 621.5 | 371.3 | 430.7 | 611.2 | 343.1 | 373.2 | 598.9 | 483.6 | 346.7 | 295.3 | 283.6 | 304.7 | 322.1 | 280.9 | 299.4 | 313
2270 | 2049 | -6.7 | 0 | 0 | 389.3 | 276.8 | 279.3 | 277.5 | 322.7 | 52.2 | 17.5 | 84.8 | 3.8 | 218.1 | 4.8 | 443.6 | 451.4 | 520.7 | 123.2 | 569.3 | 587.7 | 233.9 | 126.8 | 344.8 | 621.3 | 371.5 | 430.7 | 610.9 | 342.3 | 372.8 | 598.8 | 483.2 | 346.3 | 295.1 | 283.3 | 304.4 | 321.7 | 280.7 | 299 | 312.8
2271 | 2050 | -6.7 | 0 | 0 | 388.3 | 276.7 | 279.1 | 277.4 | 322 | 52.2 | 17.5 | 84.8 | 3.9 | 245.2 | 5.1 | 443.6 | 451.4 | 521.7 | 122.5 | 569.2 | 587.6 | 231.6 | 126.1 | 344.2 | 621.4 | 372.4 | 432.2 | 610.5 | 342.2 | 375.3 | 598.7 | 483.1 | 346 | 294.8 | 283.1 | 304.2 | 321.5 | 280.5 | 298.7 | 312.5
2272 | 2051 | -6.7 | 0 | 0 | 386.4 | 276.5 | 278.8 | 277.3 | 321.5 | 52.2 | 17.5 | 84.7 | 4.1 | 243.4 | 5.6 | 443.7 | 451.5 | 517.3 | 121.6 | 569 | 587.4 | 230.7 | 125.2 | 343.6 | 621.4 | 373.1 | 431.4 | 610.1 | 341 | 376.6 | 598.5 | 482.6 | 345.6 | 294.4 | 282.9 | 303.9 | 321.2 | 280.3 | 298.3 | 312.2
2273 | 2052 | -6.7 | 0 | 0 | 383.6 | 276.4 | 278.6 | 277 | 321 | 52.1 | 17.5 | 84.6 | 4.2 | 233.9 | 5.5 | 443.8 | 451.5 | 516.7 | 120.7 | 568.9 | 587.2 | 229 | 124.2 | 343 | 621.2 | 373.1 | 430 | 609.8 | 340.1 | 376.4 | 598.3 | 481.9 | 345.3 | 294.1 | 282.6 | 303.6 | 320.9 | 280.1 | 297.9 | 311.9
2274 | 2053 | -6.7 | 0 | 0 | 380 | 276.3 | 278.4 | 276.9 | 320.9 | 52.1 | 17.5 | 84.6 | 4.3 | 235.3 | 5.4 | 443.8 | 451.4 | 514.4 | 120.1 | 568.7 | 586.9 | 228.9 | 123.7 | 342.3 | 621.1 | 370.8 | 428.3 | 609.3 | 339.3 | 374.8 | 598.1 | 481.3 | 344.9 | 293.9 | 282.2 | 303.3 | 320.5 | 279.9 | 297.6 | 311.7
2275 | 2054 | -6.6 | 0 | 0 | 375.5 | 276.2 | 278.4 | 276.5 | 320.1 | 52.1 | 17.5 | 84.5 | 4.2 | 239.8 | 5.4 | 443.9 | 451.5 | 511.2 | 120 | 568.6 | 586.7 | 228.5 | 123.7 | 341.8 | 620.9 | 367.9 | 426.3 | 608.9 | 339.1 | 373.6 | 597.8 | 481.1 | 344.5 | 293.7 | 281.9 | 303.1 | 320.2 | 279.7 | 297.3 | 311.4
2276 | 2055 | -5.8 | 0 | 0 | 371.6 | 276.1 | 278.2 | 275.9 | 319.8 | 52 | 17.5 | 84.5 | 4.2 | 242.8 | 5.9 | 444 | 451.6 | 506.7 | 119.9 | 568.4 | 586.5 | 228.1 | 123.7 | 341.3 | 620.6 | 366.2 | 426.4 | 608.3 | 339.1 | 372.3 | 597.6 | 480.8 | 344.2 | 293.6 | 281.5 | 302.8 | 320 | 279.5 | 296.9 | 311.1
2277 | 2056 | -4.7 | 0 | 0 | 367.9 | 275.9 | 277.6 | 275.6 | 319.9 | 52 | 17.5 | 84.4 | 4.2 | 249.6 | 6.8 | 444 | 451.7 | 504.9 | 119.5 | 568.3 | 586.3 | 227.8 | 123.7 | 340.8 | 620.1 | 364.4 | 425.8 | 607.8 | 339.2 | 371.8 | 597.3 | 480.3 | 343.8 | 293.5 | 281.2 | 302.6 | 319.7 | 279.3 | 296.6 | 310.9
2278 | 2057 | -4.1 | 0 | 0 | 364.5 | 275.8 | 277.3 | 275.3 | 319.5 | 52 | 17.6 | 84.3 | 4.1 | 250.7 | 7.3 | 444.1 | 451.8 | 503.9 | 119 | 568.1 | 586.2 | 227 | 123.7 | 340.3 | 619.6 | 362.9 | 425.1 | 607.3 | 339 | 370 | 597 | 479.7 | 343.5 | 293.2 | 280.9 | 302.3 | 319.4 | 279.1 | 296.4 | 310.6
2279 | 2058 | -3.9 | 0 | 0 | 362.5 | 275.7 | 277.1 | 274.8 | 319.3 | 51.9 | 17.6 | 84.3 | 4.5 | 253.6 | 7.5 | 444.2 | 451.7 | 500.6 | 118.6 | 568 | 586.1 | 226.3 | 123.9 | 339.9 | 619.1 | 362.5 | 424.4 | 606.8 | 339.6 | 370 | 596.8 | 479 | 343.1 | 292.9 | 280.6 | 302 | 319.1 | 278.9 | 296.2 | 310.3
2280 | 2059 | -5.3 | 0 | 0 | 360.8 | 275.6 | 276.9 | 274.5 | 319 | 51.9 | 17.6 | 84.2 | 4.5 | 247.8 | 7.3 | 444.2 | 451.8 | 498.1 | 118 | 567.9 | 585.9 | 224.4 | 123.8 | 339.4 | 618.9 | 360.7 | 424 | 606.4 | 339.8 | 371.4 | 596.6 | 478.7 | 342.8 | 292.5 | 280.4 | 301.7 | 318.8 | 279.1 | 296.2 | 310
2281 | 2060 | -5.5 | 0 | 0 | 359.2 | 275.5 | 276.6 | 274.4 | 318.7 | 51.9 | 17.6 | 84.2 | 4.4 | 247 | 6.9 | 444.3 | 451.8 | 493.9 | 117.7 | 567.7 | 585.7 | 223.4 | 123.5 | 339 | 618.9 | 360.2 | 423 | 606 | 340 | 371.6 | 596.4 | 478.1 | 342.4 | 292.2 | 280.1 | 301.5 | 318.5 | 279 | 295.9 | 309.7
2282 | 2061 | -6.4 | 0 | 0 | 358.1 | 275.2 | 276.1 | 274.1 | 319.4 | 51.8 | 17.6 | 84.1 | 4.4 | 249.1 | 6.6 | 444.4 | 451.9 | 492.5 | 117.6 | 567.6 | 585.5 | 222.5 | 123.5 | 338.5 | 618.8 | 360.3 | 422.1 | 605.6 | 341 | 370.7 | 596.2 | 477.8 | 342 | 291.9 | 279.8 | 301.2 | 318.2 | 278.7 | 295.7 | 309.4
2283 | 2062 | -6.7 | 0 | 0 | 358 | 274.9 | 275.8 | 273.7 | 320 | 51.8 | 17.6 | 84 | 4.1 | 254 | 6.4 | 444.4 | 452 | 490.3 | 117.4 | 567.5 | 585.2 | 221.4 | 123.6 | 338 | 618.5 | 359.3 | 420.4 | 605.2 | 341.4 | 369.1 | 595.9 | 477.4 | 341.6 | 291.6 | 279.5 | 300.9 | 317.9 | 278.4 | 295.4 | 309.1
2284 | 2063 | -6.7 | 0 | 0 | 357.2 | 274.7 | 275.5 | 273.2 | 319.9 | 51.9 | 17.6 | 83.9 | 4 | 246.1 | 6 | 444.5 | 452.1 | 487 | 117 | 567.4 | 585.1 | 221 | 123.1 | 337.6 | 618.1 | 359.3 | 419.2 | 604.7 | 341.2 | 368.3 | 595.7 | 477.5 | 341.2 | 291.3 | 279.2 | 300.6 | 317.6 | 278 | 295.1 | 308.9
2285 | 2064 | -6.7 | 0 | 0 | 358.7 | 274.5 | 275.3 | 272.8 | 319.5 | 51.9 | 17.6 | 83.9 | 3.9 | 242.9 | 5.6 | 444.5 | 452 | 490.2 | 116.5 | 567.2 | 584.9 | 220.1 | 122.8 | 337.2 | 617.9 | 358.8 | 418.7 | 604.3 | 341.5 | 369 | 595.4 | 477.1 | 340.8 | 291 | 278.9 | 300.3 | 317.3 | 277.6 | 294.8 | 308.6
2286 | 2065 | -6.7 | 0 | 0 | 359.6 | 274.2 | 275.1 | 272.7 | 319.2 | 51.9 | 17.6 | 83.8 | 4.1 | 254.9 | 5.1 | 444.6 | 451.9 | 494.2 | 116.5 | 567.1 | 584.7 | 219.2 | 123.3 | 336.8 | 617.6 | 359.2 | 417.8 | 603.8 | 341.1 | 367 | 595.2 | 476.4 | 340.5 | 290.7 | 278.6 | 300 | 317 | 277.3 | 294.4 | 308.3
2287 | 2066 | -6.7 | 0 | 0 | 359.2 | 274 | 274.9 | 272.5 | 319.1 | 51.9 | 17.6 | 83.8 | 4.2 | 237 | 4.8 | 444.7 | 451.9 | 495.4 | 116.5 | 567 | 584.6 | 218.6 | 123.6 | 336.3 | 617.3 | 358.4 | 416.9 | 603.4 | 340.3 | 364.7 | 595.1 | 475.8 | 340.1 | 290.5 | 278.6 | 299.7 | 316.7 | 276.9 | 294.1 | 308
2288 | 2067 | -6.7 | 0 | 0 | 357.2 | 273.8 | 274.8 | 272.2 | 319 | 51.8 | 17.6 | 83.7 | 3.7 | 243.7 | 4.7 | 444.7 | 452.1 | 495.5 | 116.4 | 566.9 | 584.6 | 218.9 | 123.7 | 335.8 | 617 | 358.2 | 416.2 | 602.9 | 339.2 | 364.4 | 594.9 | 475.4 | 339.8 | 290.2 | 278.3 | 299.5 | 316.4 | 276.7 | 293.9 | 307.8
2289 | 2068 | -6.6 | 0 | 0 | 355.2 | 273.6 | 274.6 | 272.1 | 318.9 | 51.8 | 17.6 | 83.6 | 3.8 | 242.4 | 5.2 | 444.8 | 452.1 | 500.5 | 115.9 | 566.7 | 584.5 | 218.6 | 123.1 | 335.2 | 616.6 | 357.7 | 415.5 | 602.5 | 339.1 | 363.3 | 594.8 | 475.2 | 339.4 | 289.9 | 278.1 | 299.3 | 316.1 | 276.4 | 293.6 | 307.5
2290 | 2069 | -6.7 | 0 | 0 | 356.6 | 273.3 | 274.7 | 272.1 | 319.2 | 51.7 | 17.6 | 83.6 | 3.6 | 244.3 | 5.8 | 444.8 | 452.1 | 504.2 | 115.6 | 566.6 | 584.4 | 218.1 | 123 | 334.5 | 616.1 | 357.3 | 415.5 | 602.1 | 339.3 | 362.2 | 594.7 | 474.8 | 339 | 289.7 | 278 | 299.1 | 315.8 | 276.2 | 293.3 | 307.2
2291 | 2070 | -6.7 | 0 | 0 | 362.5 | 273.1 | 274.4 | 272 | 319.2 | 51.6 | 17.6 | 83.6 | 3.5 | 254.3 | 6.2 | 444.9 | 452 | 501 | 115.3 | 566.5 | 584.3 | 218.4 | 122.4 | 334.1 | 615.7 | 357.7 | 414.8 | 601.7 | 339.9 | 361 | 594.5 | 474.5 | 338.7 | 289.5 | 277.9 | 298.8 | 315.5 | 276 | 293.2 | 307
2292 | 2071 | -6.7 | 0 | 0 | 361.7 | 272.9 | 274.4 | 272.1 | 319 | 51.6 | 17.6 | 83.5 | 3.9 | 248.9 | 6.4 | 444.9 | 452 | 498.6 | 114.7 | 566.4 | 584.2 | 218.9 | 121.9 | 333.4 | 615.3 | 356.2 | 413.7 | 601.2 | 340.7 | 361.5 | 594.4 | 473.9 | 338.3 | 289.4 | 277.8 | 298.5 | 315.2 | 275.8 | 293.1 | 306.7
2293 | 2072 | -6.7 | 0 | 0 | 359.9 | 272.7 | 274.2 | 272 | 318.5 | 51.5 | 17.6 | 83.4 | 4 | 244.3 | 6.3 | 445 | 452.2 | 498.1 | 114.4 | 566.2 | 584.1 | 218.2 | 121.6 | 332.9 | 614.8 | 355.6 | 414.3 | 600.7 | 341.5 | 360.9 | 594.2 | 473.6 | 338 | 289.2 | 277.5 | 298.2 | 314.9 | 275.5 | 293 | 306.4
2294 | 2073 | -6.7 | 0 | 0 | 359.4 | 272.5 | 274.1 | 271.7 | 318.4 | 51.3 | 17.6 | 83.3 | 4.1 | 246.1 | 6.3 | 445 | 452.2 | 495.7 | 114.1 | 566.1 | 584 | 216.9 | 121.2 | 332.3 | 614.4 | 356.3 | 414.9 | 600.3 | 342.2 | 360.8 | 594.1 | 473.3 | 337.7 | 288.9 | 277.2 | 298 | 314.6 | 275.4 | 292.9 | 306.2
2295 | 2074 | -6.6 | 0 | 0 | 360 | 272.4 | 273.8 | 271.4 | 318.7 | 51.2 | 17.6 | 83.2 | 4 | 246.6 | 6 | 445.1 | 452.2 | 492.4 | 114.1 | 566 | 583.9 | 216.5 | 120.8 | 331.8 | 614 | 356.1 | 415.1 | 599.9 | 342.3 | 359.5 | 594.1 | 473.2 | 337.4 | 288.8 | 277.2 | 297.7 | 314.3 | 275.4 | 292.6 | 306
2296 | 2075 | -6.7 | 0 | 0 | 362.4 | 272.3 | 273.6 | 271.2 | 317.9 | 51.2 | 17.6 | 83.2 | 3.9 | 270.5 | 5.3 | 445.1 | 452.1 | 488.6 | 114 | 565.9 | 583.7 | 214.7 | 120.5 | 331.3 | 613.7 | 356 | 415.3 | 599.4 | 342.5 | 359.4 | 593.9 | 472.8 | 337 | 288.6 | 277 | 297.5 | 314 | 275.3 | 292.4 | 305.7
2297 | 2076 | -6.7 | 0 | 0 | 361.3 | 272.3 | 273.2 | 270.9 | 317.7 | 51.1 | 17.6 | 83.1 | 3.8 | 276 | 5.4 | 445.2 | 452.1 | 488 | 113.6 | 565.8 | 583.5 | 213.9 | 119.8 | 330.8 | 613.2 | 356.1 | 414.5 | 599 | 343 | 359.2 | 593.8 | 472.3 | 336.6 | 288.4 | 276.8 | 297.3 | 313.8 | 275.1 | 292.4 | 305.4
2298 | 2077 | -6.7 | 0 | 0 | 361 | 272.3 | 273.1 | 270.7 | 317.4 | 51 | 17.6 | 83 | 3.9 | 273.6 | 5.7 | 445.2 | 452.2 | 489.1 | 113.5 | 565.6 | 583.4 | 213.6 | 119.5 | 330.3 | 612.8 | 354.8 | 412.8 | 598.5 | 343.4 | 358.8 | 593.6 | 472 | 336.3 | 288.1 | 276.5 | 297 | 313.5 | 275.1 | 292.5 | 305.2
2299 | 2078 | -6.7 | 0 | 0 | 361 | 272.2 | 273 | 270.6 | 317.1 | 51 | 17.6 | 82.9 | 3.7 | 268.8 | 5.6 | 445.3 | 452.1 | 495.7 | 113.5 | 565.5 | 583.2 | 212.7 | 120 | 329.7 | 612.3 | 353.3 | 412.8 | 598 | 343.2 | 357.7 | 593.4 | 471.5 | 336 | 287.9 | 276.3 | 296.7 | 313.2 | 275.2 | 292.5 | 304.9
2300 | 2079 | -6.7 | 0 | 0 | 360.9 | 272.1 | 272.7 | 270.3 | 316.9 | 51 | 17.6 | 82.9 | 3.9 | 265.1 | 5.2 | 445.3 | 452.2 | 497.1 | 113.3 | 565.4 | 583 | 213.7 | 120.7 | 329.3 | 611.9 | 352.5 | 411.7 | 597.5 | 342.6 | 357.5 | 593.2 | 471 | 335.7 | 287.6 | 276.1 | 296.5 | 312.9 | 275 | 292.5 | 304.6
2301 | 2080 | -6.7 | 0 | 0 | 360.1 | 271.8 | 272.6 | 270.3 | 316.5 | 51 | 17.6 | 82.8 | 3.8 | 256.5 | 4.8 | 445.4 | 452.1 | 495.9 | 113.4 | 565.3 | 582.8 | 212.8 | 121.1 | 328.9 | 611.7 | 352.2 | 410.9 | 597.1 | 343.2 | 357.6 | 593.1 | 470.5 | 335.3 | 287.3 | 275.9 | 296.3 | 312.6 | 274.8 | 292.2 | 304.4
2302 | 2081 | -6.7 | 0 | 0 | 364.3 | 271.5 | 272.5 | 270.4 | 316.2 | 50.9 | 17.7 | 82.8 | 3.7 | 260.9 | 4.7 | 445.4 | 452.2 | 493.5 | 113.4 | 565.2 | 582.7 | 210.7 | 121.3 | 328.5 | 611.6 | 351.3 | 411.4 | 596.7 | 343.6 | 362.2 | 593 | 470.7 | 335 | 287.1 | 275.8 | 296.1 | 312.4 | 274.6 | 292.2 | 304.1
2303 | 2082 | -6.7 | 0 | 0 | 369.2 | 271.4 | 272.4 | 270.5 | 316.2 | 50.9 | 17.7 | 82.7 | 4.1 | 262.7 | 5 | 445.5 | 452.2 | 490.6 | 113.2 | 565 | 582.6 | 210.6 | 121.5 | 328.1 | 611.6 | 351.8 | 413 | 596.3 | 345 | 364.2 | 592.9 | 471 | 334.6 | 287 | 275.9 | 295.9 | 312.1 | 274.4 | 292.3 | 303.9
2304 | 2083 | -6.7 | 0 | 0 | 368.6 | 271.3 | 272.5 | 270.5 | 316.7 | 50.9 | 17.7 | 82.7 | 3.8 | 265.6 | 5.5 | 445.5 | 452.2 | 489.4 | 112.9 | 564.9 | 582.4 | 210.8 | 121.2 | 327.8 | 611.6 | 352.4 | 412.9 | 596 | 345.8 | 364.4 | 592.8 | 470.3 | 334.3 | 286.7 | 276.3 | 295.7 | 311.9 | 274.3 | 292 | 303.6
2305 | 2084 | -6.7 | 0 | 0 | 365.4 | 271.2 | 272.3 | 270.4 | 317.4 | 50.9 | 17.7 | 82.6 | 3.4 | 266.5 | 5.6 | 445.5 | 452.1 | 487.2 | 112.5 | 564.8 | 582.1 | 209.9 | 120.9 | 327.5 | 611.6 | 351.9 | 412.1 | 595.6 | 347.1 | 361.9 | 592.6 | 469.6 | 334 | 286.5 | 276.3 | 295.5 | 311.6 | 274.1 | 291.8 | 303.4
2306 | 2085 | -6.7 | 0 | 0 | 366.2 | 271.2 | 272 | 270 | 317.7 | 50.8 | 17.7 | 82.6 | 3.4 | 263 | 5.5 | 445.6 | 452.1 | 486.8 | 112.2 | 564.7 | 581.8 | 208.9 | 120.4 | 327 | 611.4 | 352.2 | 411.7 | 595.2 | 347.8 | 361.7 | 592.4 | 469.2 | 333.7 | 286.2 | 276 | 295.2 | 311.3 | 273.9 | 291.5 | 303.2
2307 | 2086 | -6.7 | 0 | 0 | 368.3 | 271.2 | 272.1 | 270 | 318 | 50.8 | 17.7 | 82.5 | 3.5 | 260.3 | 5.4 | 445.6 | 452.2 | 482.8 | 111.9 | 564.5 | 581.6 | 207.9 | 119.9 | 326.7 | 611.1 | 352 | 410.7 | 594.8 | 347.6 | 360.9 | 592.3 | 468.5 | 333.4 | 285.9 | 275.7 | 294.9 | 311 | 273.7 | 291.1 | 302.9
2308 | 2087 | -6.7 | 0 | 0 | 372.1 | 271.1 | 272.2 | 269.9 | 317.5 | 50.7 | 17.7 | 82.4 | 3.8 | 257.2 | 5.3 | 445.7 | 452.3 | 478.1 | 111.6 | 564.4 | 581.3 | 207.1 | 119.6 | 326.5 | 610.8 | 351.2 | 410.1 | 594.4 | 347.4 | 359.4 | 592 | 467.9 | 333 | 285.8 | 275.4 | 294.7 | 310.8 | 273.5 | 290.7 | 302.6
2309 | 2088 | -6.7 | 0 | 0 | 376.4 | 271 | 272.3 | 269.6 | 317.3 | 50.7 | 17.7 | 82.4 | 3.7 | 257 | 5.2 | 445.7 | 452.2 | 475 | 111.7 | 564.3 | 581.1 | 206.3 | 119.5 | 325.8 | 610.5 | 351.5 | 408.4 | 594 | 347.7 | 357.9 | 591.8 | 467.4 | 332.7 | 285.6 | 275.3 | 294.5 | 310.5 | 273.3 | 290.4 | 302.4
2310 | 2089 | -6.7 | 0 | 0 | 377.3 | 271 | 272.4 | 269.6 | 317.7 | 50.6 | 17.7 | 82.4 | 3.5 | 254.6 | 4.9 | 445.8 | 452.2 | 473.3 | 111.7 | 564.2 | 580.8 | 205.5 | 119.2 | 325.5 | 610.3 | 351.1 | 407.3 | 593.7 | 347.7 | 356.7 | 591.6 | 467.2 | 332.4 | 285.4 | 275.1 | 294.3 | 310.3 | 273.2 | 290.2 | 302.2
2311 | 2090 | -6.7 | 0 | 0 | 375.2 | 270.8 | 272.4 | 269.9 | 318 | 50.6 | 17.7 | 82.3 | 3.6 | 251 | 4.6 | 445.8 | 452.3 | 473 | 111.7 | 564.1 | 580.5 | 204.7 | 119.3 | 325.2 | 610.1 | 350.3 | 405.8 | 593.3 | 347.6 | 355.5 | 591.3 | 467.3 | 332.1 | 285.2 | 275 | 294.1 | 310 | 273 | 290.2 | 301.9
2312 | 2091 | -6.7 | 0 | 0 | 372.1 | 270.7 | 272.4 | 269.7 | 318.3 | 50.6 | 17.7 | 82.2 | 3.6 | 248.1 | 4.1 | 445.8 | 452.4 | 470.7 | 111.8 | 563.9 | 580.3 | 204.5 | 119.5 | 324.9 | 609.7 | 350 | 405.1 | 592.9 | 348.1 | 355 | 591.1 | 467 | 331.7 | 285 | 274.7 | 293.8 | 309.7 | 272.8 | 289.9 | 301.7
2313 | 2092 | -6.7 | 0 | 0 | 370.1 | 270.6 | 272.2 | 269.6 | 318 | 50.7 | 17.7 | 82.2 | 3.6 | 250.8 | 3.6 | 445.9 | 452.5 | 473.1 | 111.8 | 563.8 | 580 | 204.4 | 119.9 | 324.5 | 609.2 | 349.5 | 405.1 | 592.4 | 347.8 | 353.3 | 591 | 466.4 | 331.4 | 284.7 | 274.5 | 293.6 | 309.5 | 272.6 | 289.5 | 301.4
2314 | 2093 | -6.7 | 0 | 0 | 368.9 | 270.6 | 272.1 | 269.9 | 317.3 | 50.7 | 17.7 | 82.1 | 3.5 | 261.4 | 3.5 | 445.9 | 452.5 | 470.8 | 111.8 | 563.7 | 579.8 | 204.6 | 120.2 | 324.2 | 608.7 | 348.7 | 404.6 | 591.9 | 346.5 | 352.2 | 590.8 | 466.1 | 331.1 | 284.5 | 274.4 | 293.4 | 309.2 | 272.5 | 289.4 | 301.2
2315 | 2094 | -6.7 | 0 | 0 | 370.4 | 270.5 | 272.1 | 269.9 | 316.6 | 50.7 | 17.7 | 82 | 3.5 | 262 | 3.5 | 445.9 | 452.4 | 467.8 | 111.7 | 563.5 | 579.6 | 203.9 | 120 | 323.8 | 608.3 | 346.9 | 403.7 | 591.5 | 346.7 | 351.8 | 590.6 | 465.9 | 330.8 | 284.3 | 274.1 | 293.1 | 309 | 272.4 | 289 | 301
2316 | 2095 | -6.7 | 0 | 0 | 371.2 | 270.4 | 271.8 | 269.6 | 316.8 | 50.7 | 17.7 | 82 | 4.1 | 251.9 | 3.9 | 446 | 452.5 | 468 | 111.6 | 563.4 | 579.4 | 203.3 | 119.9 | 323.4 | 608 | 345.7 | 403.3 | 591.1 | 346.8 | 352.7 | 590.4 | 465.9 | 330.5 | 284.2 | 273.9 | 292.9 | 308.7 | 272.5 | 288.8 | 300.7
2317 | 2096 | -6.7 | 0 | 0 | 368 | 270.3 | 271.6 | 268.9 | 316.6 | 50.7 | 17.7 | 81.9 | 3.9 | 242.8 | 4.3 | 446 | 452.5 | 464 | 111.6 | 563.3 | 579.2 | 203.2 | 119.6 | 323 | 607.7 | 345.2 | 402.8 | 590.7 | 347.3 | 351.5 | 590.3 | 465.6 | 330.2 | 284 | 273.8 | 292.7 | 308.5 | 272.5 | 288.6 | 300.5
2318 | 2097 | -6.7 | 0 | 0 | 364.2 | 270.1 | 271.4 | 268.7 | 316.7 | 50.7 | 17.7 | 81.9 | 3.9 | 228 | 5.3 | 446.1 | 452.5 | 462.5 | 111.3 | 563.2 | 579 | 203.4 | 119.1 | 322.7 | 607.4 | 344 | 402.9 | 590.2 | 346.8 | 351.5 | 590.1 | 465.2 | 329.9 | 283.8 | 273.7 | 292.5 | 308.2 | 272.5 | 288.2 | 300.2
2319 | 2098 | -6.7 | 0 | 0 | 361 | 269.9 | 271.4 | 268.6 | 316.6 | 50.7 | 17.7 | 81.8 | 4 | 221.7 | 5.6 | 446.1 | 452.5 | 459.9 | 111.1 | 563 | 578.8 | 203.2 | 118.7 | 322.4 | 607 | 344.4 | 402.8 | 589.8 | 347 | 350.9 | 589.9 | 464.8 | 329.5 | 283.7 | 273.4 | 292.2 | 308 | 272.3 | 287.9 | 300
2320 | 2099 | -6.7 | 0 | 0 | 357.8 | 269.8 | 271.4 | 268.5 | 316.3 | 50.6 | 17.7 | 81.8 | 3.9 | 219.4 | 5 | 446.2 | 452.5 | 458.3 | 110.8 | 562.9 | 578.6 | 202.2 | 118.5 | 322 | 606.5 | 345 | 402.6 | 589.3 | 347 | 350.6 | 589.8 | 464.3 | 329.2 | 283.4 | 273.2 | 292 | 307.7 | 272.1 | 287.7 | 299.8
2321 | 2100 | -6.6 | 0 | 0 | 354.9 | 269.7 | 271.1 | 268.5 | 315.7 | 50.6 | 17.7 | 81.8 | 3.9 | 235.8 | 4.9 | 446.2 | 452.6 | 456.1 | 110.6 | 562.8 | 578.5 | 202 | 118.3 | 321.6 | 605.9 | 345.8 | 402.6 | 588.9 | 346.6 | 349 | 589.6 | 464 | 328.9 | 283.2 | 273 | 291.7 | 307.5 | 271.8 | 287.5 | 299.5
2322 | 2101 | -6.1 | 0 | 0 | 355 | 269.5 | 270.9 | 268.4 | 315 | 50.5 | 17.7 | 81.7 | 4.1 | 252.8 | 4.7 | 446.2 | 452.6 | 461.2 | 110.5 | 562.6 | 578.4 | 202.2 | 117.9 | 321.2 | 605.4 | 345.5 | 401.8 | 588.5 | 346.5 | 346.9 | 589.5 | 463.2 | 328.6 | 283.1 | 272.9 | 291.5 | 307.3 | 271.6 | 287.4 | 299.3
2323 | 2102 | -5.4 | 0 | 0 | 354.4 | 269.3 | 270.7 | 268.2 | 314.1 | 50.4 | 17.7 | 81.6 | 3.8 | 255.9 | 4.3 | 446.3 | 452.6 | 462.3 | 110.6 | 562.5 | 578.3 | 202.2 | 117.8 | 320.7 | 605 | 345.7 | 401.4 | 588 | 346.4 | 344.6 | 589.3 | 462.8 | 328.3 | 282.9 | 272.5 | 291.3 | 307 | 271.4 | 287.3 | 299
2324 | 2103 | -4.2 | 0 | 0 | 357.3 | 269 | 270.5 | 267.6 | 313.8 | 50.3 | 17.7 | 81.6 | 4.1 | 233.5 | 4.2 | 446.3 | 452.6 | 468.5 | 110.5 | 562.4 | 578.5 | 202.5 | 117.6 | 320.3 | 604.6 | 344.6 | 401.6 | 587.5 | 345.8 | 344 | 589.2 | 462.4 | 327.9 | 282.7 | 272.2 | 291 | 306.7 | 271.2 | 287.2 | 298.8
2325 | 2104 | -5.6 | 0 | 0 | 359.6 | 268.7 | 270.4 | 267.3 | 313.2 | 50.2 | 17.7 | 81.5 | 4.1 | 236.3 | 4.3 | 446.4 | 452.6 | 470.7 | 110.5 | 562.3 | 578.6 | 202.2 | 117.3 | 319.8 | 604.2 | 344.3 | 402.1 | 587.1 | 345.7 | 343.4 | 589.1 | 461.9 | 327.6 | 282.6 | 272.1 | 290.8 | 306.4 | 271.1 | 287.2 | 298.5
2326 | 2105 | -6.6 | 0 | 0 | 361.8 | 268.5 | 270.1 | 267.3 | 312.5 | 50.2 | 17.7 | 81.4 | 3.6 | 252.6 | 4 | 446.4 | 452.6 | 473.8 | 110.5 | 562.1 | 578.6 | 203.1 | 117 | 319.4 | 603.9 | 344.2 | 402.5 | 586.6 | 346 | 344 | 589.1 | 461.6 | 327.3 | 282.4 | 272 | 290.6 | 306.1 | 271.4 | 286.9 | 298.3
2327 | 2106 | -6.7 | 0 | 0 | 363.2 | 268.4 | 270 | 266.9 | 312.4 | 50.1 | 17.7 | 81.3 | 3.5 | 256.7 | 4 | 446.4 | 452.7 | 474.4 | 110.3 | 562 | 578.6 | 202.8 | 116.5 | 319 | 603.5 | 343.8 | 402.4 | 586.3 | 346.7 | 343.9 | 589 | 461.3 | 327 | 282.2 | 271.8 | 290.4 | 305.9 | 271.5 | 286.6 | 298.1
2328 | 2107 | -6.6 | 0 | 0 | 365.5 | 268.4 | 269.5 | 266.7 | 312.4 | 50 | 17.8 | 81.3 | 3.9 | 251.1 | 3.9 | 446.4 | 452.6 | 472.6 | 110.1 | 561.9 | 578.6 | 201.7 | 116.2 | 318.5 | 603.3 | 343.9 | 402.1 | 585.8 | 346.3 | 344.2 | 588.9 | 460.8 | 326.7 | 281.9 | 271.6 | 290.1 | 305.6 | 271.4 | 286.3 | 297.8
2329 | 2108 | -6.7 | 0 | 0 | 368.4 | 268.2 | 268.9 | 266.6 | 312 | 49.9 | 17.8 | 81.2 | 3.6 | 248.8 | 3.9 | 446.5 | 452.6 | 475.1 | 109.9 | 561.7 | 578.5 | 200.2 | 115.9 | 318.1 | 602.9 | 344.4 | 401.8 | 585.4 | 345.7 | 342.9 | 588.9 | 460.3 | 326.4 | 281.8 | 271.4 | 289.9 | 305.3 | 271.2 | 286 | 297.6
2330 | 2109 | -6.7 | 0 | 0 | 371.5 | 268.2 | 268.3 | 266.7 | 311.2 | 49.8 | 17.8 | 81.1 | 3.6 | 252.4 | 4.1 | 446.5 | 452.7 | 477.9 | 109.8 | 561.6 | 578.4 | 200.7 | 115.6 | 317.7 | 602.5 | 344.2 | 402.1 | 585 | 345.2 | 342.5 | 588.9 | 459.6 | 326 | 281.6 | 271.3 | 289.6 | 305.1 | 270.9 | 285.7 | 297.4
2331 | 2110 | -6.7 | 0 | 0 | 374.3 | 268.2 | 268.1 | 266.6 | 310.7 | 49.7 | 17.8 | 81.1 | 3.6 | 232.8 | 3.7 | 446.6 | 452.8 | 478.1 | 109.6 | 561.4 | 578.3 | 201 | 115.6 | 317.3 | 602.2 | 344.9 | 401.9 | 584.6 | 345.4 | 342.2 | 588.8 | 459.1 | 325.7 | 281.3 | 271.5 | 289.5 | 304.9 | 270.7 | 285.5 | 297.1
2332 | 2111 | -6.7 | 0 | 0 | 376.8 | 268.1 | 268.2 | 266.5 | 310.5 | 49.7 | 17.8 | 81.1 | 3.3 | 195.6 | 3.3 | 446.6 | 452.8 | 474.4 | 109.5 | 561.3 | 578.2 | 201.5 | 115.7 | 316.8 | 601.9 | 345.7 | 401.8 | 584.2 | 344.8 | 340.9 | 588.6 | 458.5 | 325.4 | 281.1 | 271.5 | 289.3 | 304.6 | 270.9 | 285.3 | 296.9
2333 | 2112 | -6.6 | 0 | 0 | 378.4 | 268 | 268.1 | 266.4 | 310 | 49.6 | 17.8 | 81 | 3.6 | 212.4 | 2.9 | 446.7 | 452.7 | 473 | 109.6 | 561.1 | 578.1 | 201.8 | 115.6 | 316.4 | 601.7 | 346.5 | 401.8 | 583.8 | 344.4 | 339.1 | 588.5 | 458.1 | 325 | 280.9 | 271.4 | 289.1 | 304.4 | 271.3 | 285.1 | 296.6
2334 | 2113 | -6.5 | 0 | 0 | 375.3 | 267.9 | 268 | 265.9 | 309.8 | 49.6 | 17.8 | 81 | 3.7 | 258.5 | 2.9 | 446.7 | 452.8 | 474.8 | 109.3 | 561 | 578 | 201.7 | 115.5 | 316 | 601.5 | 346.4 | 402.3 | 583.3 | 344.1 | 339.3 | 588.4 | 457.8 | 324.7 | 280.6 | 271.3 | 288.9 | 304.1 | 271.2 | 284.9 | 296.4
2335 | 2114 | -6.7 | 0 | 0 | 372 | 267.7 | 268 | 265.7 | 309.5 | 49.6 | 17.8 | 81 | 3.6 | 270.9 | 2.7 | 446.7 | 452.9 | 477.4 | 108.8 | 560.8 | 577.9 | 201.3 | 115.1 | 315.6 | 601.4 | 346.6 | 401.9 | 582.9 | 344.8 | 340.2 | 588.5 | 457.4 | 324.4 | 280.4 | 271.1 | 288.7 | 303.9 | 271 | 284.5 | 296.2
2336 | 2115 | -6.7 | 0 | 0 | 370.3 | 267.6 | 267.8 | 265.3 | 309.8 | 49.5 | 17.8 | 81 | 3.6 | 255.4 | 2.6 | 446.8 | 453 | 477.9 | 108.4 | 560.7 | 577.8 | 201.4 | 114.6 | 315.2 | 601.3 | 346.6 | 401.4 | 582.5 | 345.5 | 339.8 | 588.5 | 456.8 | 324.1 | 280.3 | 270.8 | 288.4 | 303.6 | 270.8 | 284.3 | 295.9
2337 | 2116 | -6.7 | 0 | 0 | 368.9 | 267.4 | 267.5 | 265.3 | 310 | 49.5 | 17.8 | 80.9 | 3.8 | 236.5 | 2.6 | 446.8 | 453 | 473.9 | 108 | 560.6 | 577.6 | 201.2 | 114.2 | 314.8 | 601.2 | 347.9 | 401.5 | 582.2 | 345.9 | 339.9 | 588.4 | 456.4 | 323.8 | 280.1 | 270.6 | 288.2 | 303.4 | 270.6 | 284.1 | 295.7
2338 | 2117 | -6.7 | 0 | 0 | 367.6 | 267.2 | 267.5 | 265.2 | 309.6 | 49.5 | 17.8 | 80.8 | 3.9 | 220.5 | 2.8 | 446.8 | 453 | 475.5 | 107.4 | 560.4 | 577.4 | 199.5 | 113.9 | 314.4 | 601.1 | 347.7 | 400.7 | 581.9 | 346.2 | 340.6 | 588.3 | 456.4 | 323.5 | 279.7 | 270.3 | 288 | 303.2 | 270.4 | 283.9 | 295.4
2339 | 2118 | -6.7 | 0 | 0 | 365.8 | 267.1 | 267.3 | 265 | 308.9 | 49.5 | 17.8 | 80.8 | 4 | 216.1 | 3 | 446.9 | 453 | 475.9 | 107.1 | 560.3 | 577.1 | 198.5 | 113.4 | 314.1 | 600.9 | 346.4 | 400.5 | 581.6 | 346.7 | 340 | 588.2 | 455.6 | 323.1 | 279.5 | 270.1 | 287.8 | 303 | 270.2 | 283.6 | 295.2
2340 | 2119 | -6.7 | 0 | 0 | 366.2 | 267 | 267.1 | 264.5 | 308.7 | 49.5 | 17.8 | 80.8 | 3.9 | 216.7 | 3.2 | 446.9 | 453.1 | 473 | 107.1 | 560.1 | 576.9 | 198.1 | 113.1 | 313.8 | 600.7 | 346.1 | 399.6 | 581.2 | 346.1 | 338.4 | 588 | 455.1 | 322.9 | 279.4 | 270.1 | 287.6 | 302.7 | 270 | 283.5 | 294.9
2341 | 2120 | -6.6 | 0 | 0 | 369.5 | 266.9 | 266.8 | 264.1 | 308.4 | 49.4 | 17.8 | 80.7 | 3.8 | 216.3 | 3 | 446.9 | 453.1 | 470.2 | 106.8 | 560 | 576.7 | 197.4 | 113 | 313.3 | 600.4 | 345.9 | 399.6 | 580.7 | 345.6 | 340.4 | 587.8 | 454.9 | 322.6 | 279.3 | 270.3 | 287.4 | 302.5 | 269.7 | 283.5 | 294.7
2342 | 2121 | -6.7 | 0 | 0 | 369.3 | 266.8 | 266.6 | 264.1 | 308.3 | 49.3 | 17.8 | 80.7 | 4.1 | 211.2 | 2.9 | 447 | 453.1 | 472.1 | 106.8 | 559.9 | 576.4 | 197 | 113.2 | 312.7 | 600.1 | 346 | 400.2 | 580.3 | 345.5 | 341.8 | 587.6 | 454.5 | 322.3 | 279.1 | 270.3 | 287.2 | 302.2 | 269.5 | 283.2 | 294.5
2343 | 2122 | -6.7 | 0 | 0 | 368.4 | 266.5 | 266.2 | 264.1 | 308.2 | 49.3 | 17.8 | 80.6 | 4.3 | 215.4 | 2.8 | 447 | 453.2 | 471.9 | 106.9 | 559.7 | 576.1 | 198 | 113.7 | 312.4 | 599.7 | 345 | 400.6 | 579.8 | 345.4 | 341.8 | 587.5 | 454.2 | 322 | 278.9 | 270 | 286.9 | 302 | 269.5 | 283.1 | 294.3
2344 | 2123 | -6.4 | 0 | 0 | 364.5 | 266.3 | 265.9 | 264.2 | 307.8 | 49.3 | 17.8 | 80.5 | 4.1 | 227.3 | 2.9 | 447 | 453.2 | 470.1 | 106.7 | 559.6 | 575.9 | 198.6 | 114.1 | 312.1 | 599.3 | 344.2 | 400.4 | 579.4 | 344.9 | 340.2 | 587.4 | 453.6 | 321.7 | 278.7 | 269.7 | 286.7 | 301.8 | 269.4 | 283 | 294.1
2345 | 2124 | -6.2 | 0 | 0 | 362.7 | 266.2 | 265.9 | 264 | 307.4 | 49.3 | 17.8 | 80.5 | 4.1 | 229.7 | 2.9 | 447.1 | 453.3 | 469.5 | 106.5 | 559.5 | 575.7 | 198.1 | 114.5 | 311.7 | 599 | 343.5 | 400.2 | 579 | 343.5 | 339.5 | 587.4 | 453.4 | 321.4 | 278.7 | 269.5 | 286.5 | 301.6 | 269.3 | 282.8 | 293.8
2346 | 2125 | -5.5 | 0 | 0 | 359.2 | 266.2 | 265.6 | 263.6 | 306.9 | 49.2 | 17.8 | 80.4 | 3.7 | 230.6 | 3 | 447.1 | 453.2 | 468 | 106.2 | 559.4 | 575.5 | 197.2 | 114.7 | 311.4 | 598.6 | 343.9 | 399.5 | 578.5 | 342.4 | 337.6 | 587.3 | 452.7 | 321.1 | 278.5 | 269.6 | 286.3 | 301.4 | 269.1 | 282.6 | 293.6
2347 | 2126 | -5.6 | 0 | 0 | 356.1 | 266.2 | 265.6 | 263.2 | 306.8 | 49.2 | 17.8 | 80.3 | 3.8 | 239.2 | 2.7 | 447.1 | 453.3 | 467.6 | 105.9 | 559.2 | 575.3 | 196.6 | 114.4 | 311.1 | 598.2 | 344.3 | 399.2 | 578.1 | 341 | 337.7 | 587.2 | 452.3 | 320.8 | 278.4 | 269.5 | 286.2 | 301.1 | 268.8 | 282.5 | 293.4
2348 | 2127 | -6.2 | 0 | 0 | 353.2 | 266.1 | 265.8 | 263.3 | 306.3 | 49.2 | 17.8 | 80.3 | 3.6 | 251.8 | 2.5 | 447.1 | 453.4 | 464.9 | 105.8 | 559.1 | 575.1 | 196.3 | 114.6 | 310.7 | 597.9 | 344.2 | 398.7 | 577.7 | 341.3 | 336.9 | 587 | 452.3 | 320.5 | 278.3 | 269.1 | 285.9 | 300.8 | 268.5 | 282.1 | 293.1
2349 | 2128 | -6.6 | 0 | 0 | 351.5 | 266.1 | 265.8 | 263.3 | 306.4 | 49.2 | 17.8 | 80.3 | 3.9 | 255.7 | 2.6 | 447.2 | 453.5 | 463.4 | 105.6 | 559 | 574.9 | 196.1 | 115.1 | 310.4 | 597.7 | 342.9 | 398.3 | 577.4 | 341.9 | 336.5 | 586.8 | 452.3 | 320.3 | 278.2 | 268.9 | 285.7 | 300.6 | 268.2 | 282 | 292.9
2350 | 2129 | -6 | 0 | 0 | 351.3 | 266.1 | 265.6 | 263.3 | 306.2 | 49.2 | 17.8 | 80.3 | 3.7 | 259.8 | 2.7 | 447.2 | 453.7 | 461.4 | 105.4 | 558.9 | 574.7 | 195.8 | 115.5 | 310.1 | 597.4 | 342.6 | 398.1 | 577 | 342.5 | 337.7 | 586.7 | 452.3 | 320 | 278 | 268.8 | 285.5 | 300.4 | 268 | 281.9 | 292.7
2351 | 2130 | -6.2 | 0 | 0 | 349.4 | 266 | 265.5 | 262.8 | 306 | 49.2 | 17.8 | 80.2 | 3.6 | 261.8 | 3 | 447.2 | 453.7 | 460.5 | 104.9 | 558.8 | 574.5 | 195.2 | 115.6 | 309.8 | 597.1 | 342.8 | 397.8 | 576.6 | 343.2 | 338.8 | 586.6 | 452 | 319.7 | 278 | 268.7 | 285.3 | 300.2 | 267.7 | 281.7 | 292.5
2352 | 2131 | -5.4 | 0 | 0 | 349.8 | 265.8 | 265.4 | 262.6 | 306.1 | 49.1 | 17.8 | 80.1 | 3.9 | 251.1 | 3.1 | 447.3 | 453.8 | 463.5 | 104.4 | 558.7 | 574.3 | 195.4 | 115.6 | 309.5 | 596.9 | 342.5 | 397.3 | 576.2 | 343.2 | 339.1 | 586.6 | 451.9 | 319.4 | 277.8 | 268.4 | 285.1 | 300 | 267.4 | 281.5 | 292.2
2353 | 2132 | -5.8 | 0 | 0 | 350.6 | 265.6 | 265.3 | 262.8 | 305.9 | 49 | 17.9 | 80.1 | 3.9 | 244.3 | 3.1 | 447.3 | 453.7 | 463.1 | 104 | 558.6 | 574 | 195.1 | 115.2 | 309 | 596.7 | 342.3 | 397 | 575.8 | 344 | 340.3 | 586.4 | 451.6 | 319.1 | 277.5 | 268.2 | 284.8 | 299.8 | 267.2 | 281.4 | 292
2354 | 2133 | -6.6 | 0 | 0 | 349.7 | 265.3 | 265.2 | 262.8 | 305.8 | 49 | 17.9 | 80 | 3.8 | 252.5 | 3.3 | 447.3 | 453.7 | 459.3 | 103.7 | 558.5 | 573.8 | 194.3 | 114.5 | 308.8 | 596.6 | 343.3 | 396.5 | 575.5 | 344.9 | 341.8 | 586.2 | 451.6 | 318.9 | 277.3 | 268 | 284.6 | 299.5 | 267.2 | 281.2 | 291.8
2355 | 2134 | -6.7 | 0 | 0 | 348.9 | 265.2 | 264.6 | 262.6 | 306.3 | 49 | 17.9 | 80 | 3.7 | 258.4 | 3.9 | 447.4 | 453.7 | 455.4 | 103.3 | 558.4 | 573.5 | 194.3 | 113.9 | 308.1 | 596.4 | 343.3 | 396.7 | 575.1 | 345.9 | 343.2 | 586.1 | 451.6 | 318.6 | 277 | 267.8 | 284.4 | 299.3 | 267.1 | 281.2 | 291.6
2356 | 2135 | -6.7 | 0 | 0 | 349.1 | 265.1 | 264 | 262.7 | 306.4 | 49.1 | 17.9 | 79.9 | 3.6 | 255.5 | 4 | 447.4 | 453.8 | 454.1 | 103 | 558.3 | 573.3 | 193.5 | 113.5 | 307.5 | 596.1 | 343.7 | 396.9 | 574.8 | 346.3 | 343.8 | 586.1 | 451.4 | 318.3 | 276.8 | 267.6 | 284.2 | 299.1 | 266.9 | 281.1 | 291.4
2357 | 2136 | -6.7 | 0 | 0 | 351.9 | 265.1 | 263.8 | 262.9 | 306.6 | 49.1 | 17.9 | 79.9 | 3.4 | 256.9 | 3.9 | 447.4 | 453.7 | 458.4 | 102.8 | 558.3 | 573.1 | 192.3 | 113.2 | 307.2 | 595.9 | 342.2 | 397.1 | 574.3 | 346.2 | 342 | 586 | 451.2 | 318 | 276.7 | 267.3 | 284 | 298.9 | 266.7 | 280.9 | 291.1
2358 | 2137 | -6.7 | 0 | 0 | 353.8 | 265 | 263.9 | 262.6 | 306.7 | 49.1 | 17.9 | 79.9 | 3.5 | 243 | 4 | 447.4 | 453.8 | 461.9 | 102.9 | 558.2 | 572.9 | 191.3 | 113 | 306.6 | 595.7 | 341.6 | 396.3 | 573.9 | 345.5 | 340.7 | 586.2 | 451.2 | 317.7 | 276.5 | 267.3 | 283.8 | 298.7 | 266.5 | 280.9 | 290.9
2359 | 2138 | -6.7 | 0 | 0 | 353.5 | 265 | 264.1 | 262.5 | 306.7 | 49.1 | 17.9 | 79.8 | 3.9 | 233.4 | 4.1 | 447.5 | 453.9 | 464 | 102.7 | 558.1 | 572.6 | 190.4 | 112.6 | 306.2 | 595.6 | 340.4 | 396.9 | 573.6 | 346.1 | 341.4 | 586.2 | 451.2 | 317.4 | 276.4 | 267.1 | 283.6 | 298.5 | 266.3 | 280.9 | 290.7
2360 | 2139 | -6.7 | 0 | 0 | 352.1 | 264.8 | 263.9 | 262.6 | 306.6 | 49 | 17.9 | 79.7 | 3.7 | 234.6 | 4.2 | 447.5 | 453.8 | 459.4 | 102.2 | 558 | 572.4 | 190 | 111.9 | 305.8 | 595.5 | 340.5 | 397.2 | 573.2 | 345.9 | 341.4 | 586.2 | 450.6 | 317.1 | 276.3 | 267.1 | 283.4 | 298.3 | 266.2 | 280.8 | 290.5
2361 | 2140 | -6.7 | 0 | 0 | 348.6 | 264.7 | 264.1 | 262.2 | 307.1 | 48.9 | 17.9 | 79.6 | 3.4 | 236.4 | 4.6 | 447.5 | 453.8 | 458.7 | 102.2 | 557.9 | 572.1 | 190.6 | 111.5 | 305.5 | 595.3 | 341.2 | 396.7 | 572.9 | 345.9 | 341.3 | 586.3 | 450.2 | 316.8 | 276.1 | 267.2 | 283.2 | 298 | 266.1 | 280.9 | 290.3
2362 | 2141 | -6.6 | 0 | 0 | 346.6 | 264.6 | 264 | 261.9 | 306.9 | 48.8 | 17.9 | 79.6 | 3.5 | 230.1 | 5 | 447.5 | 453.7 | 454 | 102 | 557.8 | 571.9 | 190.5 | 111.5 | 305.2 | 595 | 340.6 | 395.9 | 572.5 | 345.3 | 340.1 | 586 | 449.8 | 316.5 | 275.9 | 267.1 | 283 | 297.8 | 266.1 | 280.7 | 290
2363 | 2142 | -6.2 | 0 | 0 | 345.8 | 264.4 | 264 | 261.5 | 306.6 | 48.7 | 17.9 | 79.5 | 3.7 | 229.5 | 5.1 | 447.6 | 453.8 | 453.5 | 101.7 | 557.7 | 571.7 | 189.7 | 111.3 | 305 | 594.8 | 340.4 | 396.1 | 572.2 | 344.7 | 340.2 | 585.9 | 449.6 | 316.2 | 275.7 | 266.8 | 282.8 | 297.5 | 265.8 | 280.4 | 289.8
2364 | 2143 | -6.4 | 0 | 0 | 344.9 | 264.1 | 263.8 | 261.2 | 306.1 | 48.7 | 17.9 | 79.4 | 3.8 | 244 | 4.8 | 447.6 | 453.7 | 454.9 | 101.8 | 557.6 | 571.5 | 188.4 | 111.3 | 304.7 | 594.4 | 340.9 | 396.4 | 571.7 | 344.2 | 340.5 | 585.8 | 449.3 | 315.9 | 275.5 | 266.7 | 282.6 | 297.3 | 265.5 | 280.2 | 289.6
2365 | 2144 | -6.6 | 0 | 0 | 345.5 | 263.9 | 263.4 | 261.3 | 305.2 | 48.7 | 17.9 | 79.4 | 4.1 | 250.7 | 4.6 | 447.6 | 453.7 | 453.2 | 101.6 | 557.5 | 571.2 | 187.5 | 111.3 | 304.4 | 594.1 | 341.2 | 397 | 571.3 | 343.2 | 339.7 | 585.6 | 448.9 | 315.7 | 275.3 | 266.5 | 282.4 | 297.1 | 265.3 | 280 | 289.3
2366 | 2145 | -6.7 | 0 | 0 | 344.2 | 263.9 | 263.5 | 260.8 | 304.7 | 48.7 | 17.9 | 79.4 | 4.1 | 246.1 | 4.5 | 447.6 | 453.7 | 452.8 | 101.3 | 557.4 | 571 | 187.9 | 111.1 | 304.2 | 593.8 | 339.9 | 397.2 | 571 | 342.8 | 339.9 | 585.5 | 448.7 | 315.4 | 275.2 | 266.3 | 282.2 | 296.9 | 265.1 | 280.1 | 289.1
2367 | 2146 | -6.7 | 0 | 0 | 342.5 | 263.8 | 263.3 | 260.6 | 304.3 | 48.7 | 17.9 | 79.3 | 3.8 | 249.7 | 4.3 | 447.6 | 453.6 | 452.3 | 101.2 | 557.3 | 570.8 | 188.1 | 110.8 | 303.9 | 593.6 | 338.9 | 396.7 | 570.6 | 342.2 | 340 | 585.4 | 448.2 | 315.1 | 274.9 | 266 | 282 | 296.6 | 264.9 | 280.2 | 288.9
2368 | 2147 | -6.7 | 0 | 0 | 342.5 | 263.7 | 263.3 | 260.2 | 304.4 | 48.7 | 17.9 | 79.3 | 3.8 | 254.2 | 4.1 | 447.7 | 453.5 | 453.5 | 101.2 | 557.2 | 570.6 | 188 | 110.7 | 303.8 | 593.5 | 339.3 | 396.5 | 570.3 | 341.6 | 337.9 | 585.3 | 447.8 | 314.9 | 274.8 | 265.8 | 281.8 | 296.4 | 264.8 | 280 | 288.7
2369 | 2148 | -6.7 | 0 | 0 | 341.1 | 263.6 | 263.2 | 260 | 304.1 | 48.7 | 17.9 | 79.2 | 3.5 | 255.4 | 4.3 | 447.7 | 453.5 | 454 | 101 | 557.1 | 570.3 | 187.5 | 111 | 303.4 | 593.5 | 340.3 | 395.9 | 569.9 | 340.5 | 337.7 | 585.2 | 447.4 | 314.6 | 274.6 | 265.6 | 281.6 | 296.2 | 264.6 | 280 | 288.5
2370 | 2149 | -6.6 | 0 | 0 | 340.9 | 263.5 | 262.9 | 259.9 | 303.4 | 48.8 | 17.9 | 79.2 | 3.7 | 255.2 | 4.4 | 447.7 | 453.5 | 451.3 | 100.8 | 557 | 570.2 | 187.3 | 111.1 | 303.1 | 593.3 | 340.8 | 395.6 | 569.5 | 340.4 | 337.8 | 585.1 | 446.8 | 314.3 | 274.4 | 265.4 | 281.3 | 295.9 | 264.4 | 279.7 | 288.3
2371 | 2150 | -6.5 | 0 | 0 | 341.5 | 263.4 | 262.7 | 260 | 303.3 | 48.8 | 17.9 | 79.2 | 3.4 | 257.6 | 4.5 | 447.7 | 453.6 | 450.6 | 100.9 | 556.8 | 570.1 | 187.3 | 111.6 | 302.8 | 593.1 | 340.5 | 395.9 | 569.1 | 340.6 | 339.3 | 585 | 446.8 | 314 | 274.2 | 265.2 | 281.1 | 295.7 | 264.2 | 279.6 | 288
2372 | 2151 | -6.6 | 0 | 0 | 340.6 | 263.3 | 262.6 | 259.9 | 303.4 | 48.8 | 17.9 | 79.2 | 3.6 | 254.7 | 4.4 | 447.8 | 453.7 | 454.9 | 101.1 | 556.7 | 570 | 186.9 | 112 | 302.5 | 592.9 | 341.7 | 397.1 | 568.7 | 340.2 | 338.5 | 584.9 | 446.5 | 313.7 | 274 | 265 | 280.9 | 295.5 | 264 | 279.4 | 287.8
2373 | 2152 | -6.7 | 0 | 0 | 339.7 | 263.2 | 262.5 | 259.8 | 303.3 | 48.7 | 17.9 | 79.1 | 3.7 | 248.3 | 4.1 | 447.8 | 454 | 456.3 | 101.4 | 556.6 | 569.9 | 187.1 | 112.2 | 302.2 | 592.6 | 341.6 | 397.1 | 568.3 | 339.7 | 337.8 | 584.8 | 446.1 | 313.5 | 273.7 | 264.9 | 280.8 | 295.3 | 263.8 | 279.3 | 287.6
2374 | 2153 | -6.6 | 0 | 0 | 338.6 | 263 | 262.6 | 259.4 | 302.8 | 48.7 | 17.9 | 79.1 | 3.6 | 246.8 | 3.8 | 447.8 | 453.8 | 452.8 | 101.5 | 556.5 | 569.8 | 187.3 | 112.4 | 301.9 | 592.5 | 341.2 | 396.5 | 567.9 | 339.6 | 336.8 | 584.7 | 445.8 | 313.2 | 273.5 | 264.7 | 280.6 | 295.1 | 263.6 | 279.4 | 287.4
2375 | 2154 | -6.6 | 0 | 0 | 338.3 | 262.8 | 262.6 | 259.8 | 302.6 | 48.7 | 17.9 | 79.1 | 3.7 | 248.3 | 3.5 | 447.8 | 453.7 | 450.5 | 101.7 | 556.3 | 569.6 | 187.5 | 112.6 | 301.6 | 592.5 | 342.4 | 395.7 | 567.5 | 339.8 | 335.9 | 584.7 | 445.4 | 312.9 | 273.4 | 264.6 | 280.4 | 294.9 | 263.6 | 279.4 | 287.2
2376 | 2155 | -6.7 | 0 | 0 | 336.8 | 262.7 | 262.5 | 259.7 | 302.5 | 48.6 | 17.9 | 79 | 4 | 251.2 | 3.3 | 447.8 | 454 | 454.3 | 101.9 | 556.2 | 569.5 | 186.9 | 112.7 | 301.3 | 592.3 | 342.8 | 396 | 567.2 | 340.7 | 336.6 | 584.5 | 445.4 | 312.6 | 273.2 | 264.3 | 280.2 | 294.6 | 263.5 | 279.1 | 287
2377 | 2156 | -6.7 | 0 | 0 | 338.3 | 262.6 | 262.5 | 259.5 | 302.8 | 48.6 | 17.9 | 79 | 4 | 254.8 | 3.1 | 447.8 | 453.9 | 453 | 101.9 | 556.1 | 569.4 | 186.6 | 113.1 | 300.9 | 592.1 | 342.7 | 396.2 | 566.8 | 341.1 | 336.3 | 584.6 | 445.4 | 312.4 | 273.1 | 264.1 | 280 | 294.4 | 263.5 | 278.9 | 286.8
2378 | 2157 | -6.7 | 0 | 0 | 340.6 | 262.5 | 262.3 | 259.2 | 302.7 | 48.6 | 17.9 | 79 | 3.9 | 255.9 | 2.9 | 447.9 | 453.8 | 452.3 | 102 | 556 | 569.2 | 186 | 113.2 | 300.6 | 591.8 | 341.6 | 395.8 | 566.5 | 342.4 | 336.9 | 584.5 | 445.5 | 312 | 272.9 | 263.9 | 279.8 | 294.2 | 263.5 | 278.6 | 286.6
2379 | 2158 | -6.5 | 0 | 0 | 344.7 | 262.2 | 262.1 | 259.1 | 302.3 | 48.6 | 17.9 | 78.9 | 3.9 | 255.8 | 2.7 | 447.9 | 453.7 | 453 | 101.9 | 555.9 | 569.1 | 185.3 | 113.5 | 300.3 | 591.6 | 341.8 | 395.4 | 566.1 | 343 | 335.7 | 584.4 | 445.2 | 311.8 | 272.9 | 263.6 | 279.6 | 293.9 | 263.3 | 278.3 | 286.4
2380 | 2159 | -5.8 | 0 | 0 | 344.6 | 262 | 262 | 259 | 302.4 | 48.6 | 18 | 78.9 | 3.9 | 255.7 | 2.5 | 447.9 | 453.6 | 450.2 | 101.7 | 555.7 | 568.9 | 185.7 | 113.4 | 299.9 | 591.5 | 341.2 | 395 | 565.7 | 343.2 | 334.8 | 584.4 | 445.3 | 311.5 | 272.6 | 263.4 | 279.3 | 293.7 | 263.1 | 278.1 | 286.2
2381 | 2160 | -6 | 0 | 0 | 343.7 | 261.9 | 261.8 | 258.6 | 302.4 | 48.5 | 18 | 78.8 | 3.9 | 255.7 | 2.3 | 447.9 | 453.5 | 447 | 101.5 | 555.6 | 568.7 | 184.2 | 112.9 | 299.3 | 591.4 | 340.9 | 394.2 | 565.4 | 343.2 | 333.5 | 584.2 | 444.9 | 311.2 | 272.3 | 263.2 | 279.1 | 293.5 | 262.9 | 277.8 | 286
2382 | 2161 | -6.3 | 0 | 0 | 342.5 | 261.9 | 261.4 | 258.5 | 302.7 | 48.5 | 18 | 78.8 | 3.7 | 255.7 | 2.2 | 447.9 | 453.5 | 444.7 | 101.5 | 555.5 | 568.5 | 183.9 | 113.1 | 299 | 591.2 | 341.4 | 394.2 | 565.1 | 342.9 | 334.7 | 584.2 | 444.9 | 310.9 | 272.1 | 262.9 | 278.9 | 293.3 | 262.6 | 277.6 | 285.8
2383 | 2162 | -5.9 | 0 | 0 | 341.8 | 261.8 | 261.1 | 258.4 | 302.5 | 48.5 | 18 | 78.7 | 3.7 | 255 | 2.1 | 447.9 | 453.4 | 443.3 | 101.7 | 555.4 | 568.4 | 183.2 | 113.3 | 298.7 | 591 | 342.1 | 394.4 | 564.7 | 343.1 | 335.7 | 584.2 | 444.6 | 310.6 | 271.9 | 262.8 | 278.7 | 293.1 | 262.4 | 277.4 | 285.6
2384 | 2163 | -6.5 | 0 | 0 | 340.3 | 261.7 | 260.9 | 258.3 | 302.3 | 48.5 | 18 | 78.7 | 4 | 253.2 | 2 | 447.9 | 453.4 | 443.9 | 101.7 | 555.3 | 568.2 | 182.5 | 113.6 | 298.5 | 590.7 | 343.2 | 394.6 | 564.4 | 342.9 | 336.2 | 584.1 | 444.3 | 310.4 | 271.8 | 262.7 | 278.6 | 292.9 | 262.2 | 277.5 | 285.4
2385 | 2164 | -6.7 | 0 | 0 | 339.1 | 261.6 | 260.8 | 258.3 | 302.2 | 48.5 | 18 | 78.7 | 4 | 250.6 | 2 | 448 | 453.4 | 442.4 | 101.6 | 555.2 | 568.2 | 182.2 | 113.7 | 298.2 | 590.5 | 342.8 | 394.4 | 564 | 343 | 336.5 | 583.9 | 444.1 | 310.1 | 271.6 | 262.5 | 278.4 | 292.7 | 262.1 | 277.7 | 285.2
2386 | 2165 | -6.7 | 0 | 0 | 336.3 | 261.4 | 260.8 | 258.3 | 302.3 | 48.5 | 18 | 78.6 | 3.8 | 244.5 | 2 | 448 | 453.2 | 439.3 | 101.6 | 555.1 | 568.1 | 182.3 | 113.5 | 298 | 590.3 | 341.2 | 393.5 | 563.7 | 343.2 | 335.7 | 583.8 | 444 | 309.8 | 271.5 | 262.4 | 278.2 | 292.5 | 262.1 | 277.7 | 285
2387 | 2166 | -6.5 | 0 | 0 | 334.5 | 261.2 | 260.7 | 258.1 | 302.7 | 48.5 | 18 | 78.6 | 3.6 | 240 | 2 | 448 | 453.2 | 438.4 | 101.6 | 555 | 568 | 181.9 | 113.3 | 297.8 | 590.1 | 339.5 | 392.7 | 563.4 | 343.2 | 335.9 | 583.8 | 443.6 | 309.6 | 271.4 | 262.2 | 278 | 292.2 | 262.1 | 277.5 | 284.8
2388 | 2167 | -6.2 | 0 | 0 | 333.8 | 261.1 | 260.2 | 257.6 | 302.6 | 48.5 | 18 | 78.6 | 3.9 | 238.2 | 1.9 | 448 | 453.2 | 436.8 | 101.5 | 554.9 | 567.9 | 181.8 | 113.3 | 297.5 | 589.9 | 338.4 | 391.5 | 563.1 | 343 | 335.2 | 583.7 | 443.2 | 309.3 | 271.2 | 262.1 | 277.8 | 292 | 261.9 | 277.3 | 284.6
2389 | 2168 | -6.4 | 0 | 0 | 336.4 | 260.9 | 260 | 257.1 | 302 | 48.5 | 18 | 78.6 | 3.7 | 237.6 | 1.9 | 448 | 453.2 | 437.2 | 101.3 | 554.8 | 567.8 | 181.7 | 113.4 | 297.3 | 589.8 | 338 | 391.6 | 562.8 | 342.8 | 334.7 | 583.7 | 443 | 309 | 270.9 | 261.9 | 277.6 | 291.8 | 261.8 | 277 | 284.4
2390 | 2169 | -6 | 0 | 0 | 336.6 | 260.8 | 259.8 | 256.9 | 301.3 | 48.4 | 18 | 78.6 | 3.2 | 237.8 | 2 | 448 | 453.1 | 438.6 | 101.1 | 554.7 | 567.7 | 181.5 | 112.9 | 297 | 589.7 | 336.3 | 390.8 | 562.4 | 342.7 | 333.9 | 583.7 | 442.6 | 308.8 | 270.8 | 261.8 | 277.4 | 291.7 | 261.5 | 276.7 | 284.2
2391 | 2170 | -5.4 | 0 | 0 | 334.5 | 260.7 | 259.4 | 256.8 | 301.5 | 48.3 | 18 | 78.5 | 3.4 | 241 | 2 | 448 | 453.1 | 442.5 | 100.9 | 554.6 | 567.6 | 182.1 | 112.9 | 296.9 | 589.8 | 336.8 | 389.7 | 562.2 | 342.8 | 332.3 | 583.6 | 442.2 | 308.5 | 270.7 | 261.6 | 277.2 | 291.5 | 261.4 | 276.7 | 284
2392 | 2171 | -5.5 | 0 | 0 | 332.2 | 260.6 | 259.3 | 256.6 | 301.5 | 48.3 | 18 | 78.5 | 3.5 | 242.3 | 1.9 | 448 | 453 | 443.9 | 100.7 | 554.5 | 567.5 | 182.9 | 113 | 296.5 | 589.9 | 335.5 | 389.1 | 561.8 | 341.9 | 330.9 | 583.6 | 441.7 | 308.3 | 270.5 | 261.5 | 277 | 291.3 | 261.2 | 276.5 | 283.9
2393 | 2172 | -6.3 | 0 | 0 | 330.1 | 260.5 | 259.3 | 256.1 | 300.8 | 48.2 | 18 | 78.5 | 3.6 | 242.2 | 1.8 | 448 | 453 | 452.1 | 100.4 | 554.4 | 567.5 | 182.3 | 112.5 | 296.3 | 589.9 | 335 | 389 | 561.4 | 341.4 | 330.7 | 583.7 | 441.4 | 308 | 270.3 | 261.3 | 276.8 | 291 | 261.1 | 276.2 | 283.7
2394 | 2173 | -6.3 | 0 | 0 | 329.1 | 260.3 | 259 | 255.8 | 300.6 | 48.1 | 18 | 78.5 | 3.3 | 242.4 | 1.9 | 448 | 453 | 452.4 | 99.9 | 554.3 | 567.5 | 182.9 | 111.9 | 296 | 589.9 | 337.9 | 389.6 | 560.9 | 342.1 | 333.4 | 583.7 | 441.4 | 307.8 | 270.1 | 261.4 | 276.6 | 290.8 | 260.9 | 275.9 | 283.4
2395 | 2174 | -6.6 | 0 | 0 | 328 | 260.2 | 258.7 | 255.6 | 300.5 | 48.1 | 18 | 78.4 | 3.7 | 244.1 | 1.9 | 448.1 | 453 | 448.4 | 99.5 | 554.2 | 567.5 | 182.9 | 111.6 | 295.7 | 589.9 | 338.1 | 389.7 | 560.6 | 343.7 | 333.7 | 583.8 | 441.3 | 307.5 | 270.1 | 261.2 | 276.4 | 290.6 | 260.8 | 275.8 | 283.2
2396 | 2175 | -6.7 | 0 | 0 | 328.1 | 260 | 258.5 | 255.5 | 301 | 48.1 | 18 | 78.4 | 3.8 | 243.4 | 1.9 | 448.1 | 453 | 446.5 | 99.2 | 554.1 | 567.4 | 182.1 | 111.2 | 295.3 | 590 | 338.8 | 390.1 | 560.2 | 343.5 | 334.3 | 583.9 | 441 | 307.3 | 269.9 | 261 | 276.2 | 290.3 | 260.6 | 275.5 | 283
2397 | 2176 | -6.6 | 0 | 0 | 327.3 | 259.8 | 258.4 | 255.4 | 300.9 | 48.1 | 18 | 78.3 | 3.8 | 243.9 | 2 | 448.1 | 452.9 | 442.8 | 99 | 554 | 567.4 | 181.6 | 111.1 | 294.9 | 590 | 338.8 | 390.5 | 559.9 | 343.9 | 333.9 | 583.7 | 441.1 | 307 | 269.7 | 260.8 | 276 | 290.1 | 260.4 | 275.5 | 282.9
2398 | 2177 | -6.6 | 0 | 0 | 326.7 | 259.6 | 258.3 | 255.3 | 300.8 | 48 | 18 | 78.3 | 3.4 | 245.3 | 2.1 | 448.1 | 452.9 | 445.2 | 98.7 | 553.9 | 567.3 | 182.2 | 110.8 | 294.6 | 590 | 338.9 | 390.2 | 559.7 | 344.4 | 333.5 | 583.5 | 441.1 | 306.7 | 269.5 | 260.6 | 275.8 | 289.9 | 260.2 | 275.2 | 282.7
2399 | 2178 | -6.3 | 0 | 0 | 326.3 | 259.5 | 258 | 255.3 | 301 | 48 | 18 | 78.2 | 3.4 | 243.8 | 2.5 | 448.1 | 453.1 | 446.1 | 98.4 | 553.8 | 567.3 | 182.5 | 110.7 | 294.3 | 590.1 | 339.2 | 389.7 | 559.4 | 345.1 | 334.2 | 583.4 | 441.2 | 306.5 | 269.3 | 260.5 | 275.6 | 289.7 | 259.9 | 274.8 | 282.5
2400 | 2179 | -6.3 | 0 | 0 | 325.6 | 259.4 | 257.7 | 255.3 | 301.1 | 47.9 | 18.1 | 78.2 | 3.6 | 244.1 | 2.8 | 448.1 | 453.1 | 447.2 | 98.1 | 553.7 | 567.2 | 182.5 | 110.3 | 293.9 | 590.1 | 339 | 389.6 | 559.1 | 345.4 | 333.8 | 583.5 | 441.2 | 306.2 | 269.1 | 260.3 | 275.5 | 289.5 | 259.7 | 274.5 | 282.3
2401 | 2180 | -6.5 | 0 | 0 | 324.6 | 259.2 | 257.5 | 255.2 | 300.8 | 47.9 | 18.1 | 78.2 | 3.6 | 252.5 | 3 | 448.1 | 453.1 | 443.4 | 97.8 | 553.6 | 567.1 | 182.7 | 110 | 293.6 | 589.9 | 338.9 | 389.8 | 558.8 | 345.8 | 333.3 | 583.4 | 440.8 | 305.9 | 268.9 | 260.1 | 275.3 | 289.3 | 259.4 | 274.3 | 282.1
2402 | 2181 | -6.6 | 0 | 0 | 323.4 | 259.1 | 257.2 | 255 | 300.6 | 47.9 | 18.1 | 78.2 | 3.6 | 253.4 | 3.2 | 448.1 | 453.1 | 440.2 | 97.6 | 553.5 | 566.9 | 181.9 | 110 | 293.3 | 589.8 | 339.1 | 389.2 | 558.5 | 345.9 | 332.5 | 583.3 | 440.8 | 305.6 | 268.8 | 259.9 | 275.1 | 289.1 | 259.2 | 274.1 | 281.9
2403 | 2182 | -6.6 | 0 | 0 | 322.7 | 259 | 257 | 255.2 | 300.2 | 47.9 | 18.1 | 78.1 | 3.9 | 243.3 | 3.2 | 448.1 | 453.1 | 436.3 | 97.7 | 553.4 | 566.8 | 181.3 | 110.1 | 293 | 589.7 | 339.6 | 389.8 | 558.3 | 346 | 333.7 | 583.2 | 440.8 | 305.3 | 268.7 | 259.8 | 274.9 | 288.9 | 259.1 | 274.3 | 281.7
2404 | 2183 | -6.7 | 0 | 0 | 321.5 | 258.9 | 256.8 | 254.9 | 299.7 | 47.8 | 18.1 | 78.1 | 3.7 | 227.4 | 3.1 | 448.1 | 453.1 | 433 | 97.6 | 553.3 | 566.6 | 180.6 | 110.4 | 292.8 | 589.7 | 339.8 | 390.6 | 558 | 346.7 | 334.3 | 583 | 440.8 | 305 | 268.4 | 259.6 | 274.7 | 288.6 | 258.9 | 274.2 | 281.4
2405 | 2184 | -6.7 | 0 | 0 | 320.7 | 258.8 | 256.5 | 254.6 | 299.3 | 47.7 | 18.1 | 78.1 | 3.8 | 230.4 | 2.8 | 448.1 | 453 | 431 | 97.7 | 553.3 | 566.4 | 180.3 | 110.7 | 292.5 | 589.5 | 340.1 | 391.1 | 557.8 | 347.1 | 334.4 | 582.8 | 440.4 | 304.7 | 268.3 | 259.4 | 274.5 | 288.5 | 258.7 | 273.9 | 281.2
2406 | 2185 | -6.7 | 0 | 0 | 320.2 | 258.5 | 256.4 | 254.2 | 299.3 | 47.6 | 18.1 | 78.1 | 3.9 | 238.6 | 2.6 | 448.1 | 453.1 | 428.7 | 97.8 | 553.2 | 566.3 | 180.2 | 111 | 292.2 | 589.4 | 340.5 | 391.5 | 557.4 | 346.9 | 332.5 | 582.7 | 440.1 | 304.4 | 268.3 | 259.2 | 274.3 | 288.2 | 258.5 | 273.6 | 281.1
2407 | 2186 | -6.7 | 0 | 0 | 319.9 | 258.3 | 256.2 | 253.8 | 299.3 | 47.6 | 18.1 | 78 | 3.8 | 241.9 | 2.4 | 448.1 | 453.1 | 427.4 | 98 | 553.1 | 566.1 | 180.8 | 111.2 | 292 | 589.1 | 340.6 | 391.7 | 557.1 | 346.5 | 331 | 582.8 | 440.2 | 304.2 | 268.1 | 258.9 | 274.1 | 288.1 | 258.3 | 273.4 | 280.9
2408 | 2187 | -6.7 | 0 | 0 | 319.5 | 258.2 | 255.8 | 253.8 | 298.9 | 47.5 | 18.1 | 77.9 | 3.8 | 245.4 | 2.3 | 448.1 | 453 | 428.2 | 98.3 | 553 | 565.8 | 180.9 | 111.4 | 291.7 | 588.9 | 339.8 | 391 | 556.8 | 346.4 | 330.7 | 582.7 | 440 | 303.9 | 268 | 258.7 | 273.9 | 287.9 | 258.2 | 273.2 | 280.7
2409 | 2188 | -6.7 | 0 | 0 | 318.7 | 258.2 | 255.6 | 253.7 | 298.9 | 47.5 | 18.1 | 77.9 | 4.1 | 247.5 | 2.3 | 448.1 | 452.9 | 428.2 | 98.5 | 552.9 | 565.7 | 182.1 | 111.6 | 291.5 | 588.6 | 339.5 | 391 | 556.5 | 345.6 | 330.9 | 582.8 | 439.6 | 303.6 | 267.8 | 258.5 | 273.7 | 287.7 | 258 | 273 | 280.5
2410 | 2189 | -6.7 | 0 | 0 | 318.1 | 258.1 | 255.6 | 253.6 | 298.5 | 47.5 | 18.1 | 77.9 | 4.2 | 235 | 2.2 | 448.2 | 452.8 | 426.6 | 98.8 | 552.8 | 565.5 | 182.4 | 111.5 | 291.3 | 588.3 | 340 | 390.5 | 556.2 | 345.2 | 330.9 | 582.7 | 439.4 | 303.4 | 267.7 | 258.3 | 273.5 | 287.5 | 257.9 | 272.9 | 280.3
2411 | 2190 | -6.7 | 0 | 0 | 317.5 | 258.1 | 255.6 | 253.3 | 298.3 | 47.5 | 18.1 | 77.9 | 4.1 | 212.9 | 2.2 | 448.2 | 452.8 | 424.7 | 99.1 | 552.7 | 565.4 | 181.8 | 111.8 | 291.1 | 588 | 339.8 | 391.4 | 555.9 | 344.5 | 330.9 | 582.7 | 439.1 | 303.1 | 267.4 | 258.1 | 273.3 | 287.3 | 257.7 | 273 | 280
2412 | 2191 | -6.7 | 0 | 0 | 318.6 | 258 | 255.5 | 252.7 | 297.8 | 47.4 | 18.1 | 77.8 | 4.1 | 200.7 | 2.1 | 448.2 | 452.8 | 426.5 | 99.2 | 552.6 | 565.4 | 181.3 | 112 | 290.9 | 587.8 | 340.8 | 392.6 | 555.5 | 343.5 | 331.3 | 582.7 | 438.7 | 302.9 | 267.3 | 257.9 | 273.1 | 287.1 | 257.6 | 272.8 | 279.9
2413 | 2192 | -6.7 | 0 | 0 | 321.5 | 257.9 | 255.2 | 252.7 | 297.6 | 47.4 | 18.1 | 77.8 | 4.2 | 202.8 | 2.2 | 448.2 | 452.9 | 427.5 | 99.3 | 552.5 | 565.4 | 181.2 | 112.4 | 290.6 | 587.6 | 340.9 | 392.1 | 555.2 | 342.7 | 330 | 582.8 | 438.3 | 302.6 | 267.1 | 257.9 | 272.9 | 286.9 | 257.4 | 272.5 | 279.7
2414 | 2193 | -6.4 | 0 | 0 | 320.8 | 257.8 | 255.1 | 252.7 | 297.4 | 47.4 | 18.1 | 77.7 | 3.6 | 204.9 | 2.2 | 448.2 | 452.8 | 427.6 | 99.3 | 552.4 | 565.3 | 181.9 | 112.5 | 290.3 | 587.4 | 340.1 | 391.4 | 554.9 | 342.5 | 328.8 | 582.6 | 437.8 | 302.4 | 267.1 | 257.9 | 272.8 | 286.7 | 257.3 | 272.2 | 279.5
2415 | 2194 | -6.4 | 0 | 0 | 319.6 | 257.6 | 255.1 | 252.9 | 297.1 | 47.3 | 18.1 | 77.6 | 4 | 204.8 | 2.3 | 448.2 | 453 | 425.3 | 99.4 | 552.2 | 565.3 | 181.2 | 112.6 | 290 | 587.2 | 338.1 | 390.2 | 554.6 | 342 | 327.3 | 582.5 | 437.3 | 302.2 | 266.8 | 257.8 | 272.6 | 286.4 | 257.1 | 272 | 279.3
2416 | 2195 | -6.3 | 0 | 0 | 317.8 | 257.3 | 255 | 252.8 | 296.9 | 47.3 | 18.1 | 77.6 | 4.2 | 203.7 | 2.6 | 448.2 | 453 | 422.8 | 99.4 | 552.1 | 565.2 | 180.8 | 112.8 | 289.8 | 586.9 | 338.2 | 390.6 | 554.2 | 341.7 | 327 | 582.6 | 437 | 302 | 266.6 | 257.7 | 272.4 | 286.3 | 257.2 | 271.9 | 279.1
2417 | 2196 | -6.2 | 0 | 0 | 315.7 | 257 | 254.7 | 252.6 | 296.5 | 47.3 | 18.1 | 77.5 | 3.7 | 203.1 | 2.8 | 448.2 | 452.9 | 422.2 | 99.1 | 552 | 565.2 | 180.2 | 112.6 | 289.6 | 586.6 | 338.9 | 390.1 | 553.9 | 341.8 | 327.1 | 582.6 | 437.1 | 301.7 | 266.4 | 257.5 | 272.2 | 286.1 | 257.2 | 271.9 | 278.9
2418 | 2197 | -6.4 | 0 | 0 | 314.7 | 256.9 | 254.5 | 252.6 | 296 | 47.2 | 18.1 | 77.5 | 3.9 | 204.9 | 2.8 | 448.2 | 452.9 | 423.8 | 98.7 | 551.9 | 565.2 | 180.4 | 112.2 | 289.4 | 586.2 | 338.9 | 389.7 | 553.5 | 341.9 | 327.5 | 582.7 | 437.1 | 301.4 | 266.2 | 257.3 | 272 | 285.9 | 257.1 | 271.7 | 278.7
2419 | 2198 | -6.7 | 0 | 0 | 314.4 | 256.9 | 254.1 | 252.7 | 295.3 | 47.2 | 18.1 | 77.4 | 3.6 | 206.3 | 2.7 | 448.2 | 453 | 428.3 | 98.2 | 551.8 | 565.2 | 180.2 | 111.9 | 289.1 | 585.8 | 339.1 | 390.5 | 553.1 | 341.8 | 329.1 | 582.9 | 436.8 | 301.1 | 266.1 | 257.1 | 271.9 | 285.7 | 257 | 271.5 | 278.5
2420 | 2199 | -6 | 0 | 0 | 314.5 | 256.7 | 253.8 | 252.6 | 295 | 47.1 | 18.1 | 77.3 | 3.6 | 206.5 | 2.5 | 448.2 | 453 | 429.3 | 97.9 | 551.6 | 565.2 | 180.5 | 111.6 | 288.8 | 585.6 | 341 | 391.1 | 552.7 | 341.3 | 328.6 | 582.9 | 436.9 | 300.9 | 266 | 257 | 271.7 | 285.5 | 256.8 | 271.6 | 278.3
2421 | 2200 | -6.2 | 0 | 0 | 315 | 256.6 | 253.9 | 252.3 | 295 | 47.1 | 18.1 | 77.3 | 3.6 | 207.4 | 2.5 | 448.2 | 453 | 432.2 | 97.7 | 551.5 | 565.1 | 180.6 | 111.4 | 288.5 | 585.4 | 340.9 | 390.8 | 552.4 | 340.3 | 327.7 | 582.6 | 436.8 | 300.6 | 265.9 | 256.8 | 271.5 | 285.3 | 256.7 | 271.7 | 278.1
2422 | 2201 | -6.6 | 0 | 0 | 314.5 | 256.5 | 254.1 | 252.2 | 295 | 47.1 | 18.1 | 77.2 | 4.1 | 207.3 | 2.3 | 448.2 | 452.8 | 432.2 | 97.6 | 551.4 | 565 | 179.8 | 111.2 | 288.3 | 585.2 | 341.9 | 391.1 | 552.1 | 339.9 | 327.7 | 582.2 | 436.3 | 300.4 | 265.7 | 256.6 | 271.3 | 285 | 256.7 | 271.5 | 277.9
2423 | 2202 | -6.7 | 0 | 0 | 314 | 256.2 | 254.2 | 251.6 | 294.9 | 47 | 18.1 | 77.2 | 4.7 | 209.3 | 2.2 | 448.2 | 452.8 | 429 | 97.2 | 551.3 | 565 | 179.6 | 111.1 | 288.1 | 585 | 341.6 | 391.1 | 551.8 | 339.5 | 328.4 | 582.1 | 436 | 300.1 | 265.5 | 256.4 | 271.1 | 284.8 | 256.7 | 271.2 | 277.8
2424 | 2203 | -6.7 | 0 | 0 | 313.3 | 256 | 253.9 | 251.3 | 294.4 | 47 | 18.1 | 77.2 | 4.3 | 215.8 | 2.4 | 448.2 | 452.8 | 427.8 | 97 | 551.2 | 564.8 | 179 | 111.1 | 287.8 | 584.8 | 341.5 | 390.5 | 551.5 | 340 | 327.6 | 582 | 435.7 | 299.9 | 265.3 | 256.3 | 271 | 284.6 | 256.7 | 270.9 | 277.6
2425 | 2204 | -6.7 | 0 | 0 | 313 | 256 | 253.6 | 251.2 | 294.1 | 47 | 18.1 | 77.1 | 4 | 216.6 | 3.6 | 448.2 | 452.9 | 426.6 | 96.8 | 551.1 | 564.7 | 179 | 111 | 287.5 | 584.7 | 341.8 | 389.6 | 551.2 | 340.3 | 326.9 | 582.2 | 435.4 | 299.6 | 265.1 | 256.1 | 270.8 | 284.4 | 256.5 | 270.7 | 277.4
2426 | 2205 | -6.7 | 0 | 0 | 312.1 | 255.9 | 253.3 | 251.3 | 294.2 | 47 | 18.1 | 77 | 4 | 206.6 | 4.6 | 448.2 | 452.7 | 424.3 | 96.7 | 551.1 | 564.6 | 178.8 | 111 | 287.2 | 584.6 | 342 | 390.3 | 550.9 | 341.2 | 326.9 | 582 | 435.4 | 299.4 | 264.8 | 256 | 270.6 | 284.3 | 256.2 | 270.4 | 277.2
2427 | 2206 | -6.7 | 0 | 0 | 312.8 | 255.8 | 253.2 | 251.5 | 294 | 47 | 18.1 | 77 | 4.4 | 208.4 | 5 | 448.2 | 452.8 | 423.4 | 96.6 | 551 | 564.4 | 177.9 | 110.9 | 287 | 584.4 | 340.9 | 390.6 | 550.6 | 341.3 | 326.5 | 581.8 | 435 | 299.2 | 264.6 | 255.7 | 270.4 | 284.1 | 255.9 | 270.1 | 277
2428 | 2207 | -6.7 | 0 | 0 | 313.1 | 255.7 | 253.2 | 251.7 | 293.6 | 47 | 18.1 | 76.9 | 4.1 | 216.9 | 4.8 | 448.2 | 452.7 | 418.7 | 96.4 | 550.9 | 564.3 | 177.8 | 110.8 | 286.8 | 584.3 | 342.2 | 390.5 | 550.3 | 341.9 | 326.6 | 581.6 | 435 | 298.9 | 264.4 | 255.5 | 270.2 | 283.9 | 255.7 | 269.9 | 276.8
2429 | 2208 | -6.7 | 0 | 0 | 311.5 | 255.6 | 252.8 | 251.6 | 293.4 | 47 | 18.2 | 76.8 | 4 | 204.5 | 3.9 | 448.2 | 452.6 | 419.6 | 96.4 | 550.8 | 564.1 | 177.2 | 110.6 | 286.6 | 584.2 | 343.5 | 390.9 | 550 | 342.2 | 325.6 | 581.2 | 434.8 | 298.7 | 264.3 | 255.3 | 270 | 283.8 | 255.6 | 269.7 | 276.6
2430 | 2209 | -6.5 | 0 | 0 | 311.3 | 255.5 | 252.2 | 251.3 | 293.5 | 47 | 18.2 | 76.7 | 3.9 | 203.3 | 3.5 | 448.2 | 452.6 | 420.7 | 96.4 | 550.7 | 563.9 | 178.1 | 110.7 | 286.4 | 584.1 | 344.9 | 390.4 | 549.7 | 341.8 | 324.6 | 581.3 | 434.4 | 298.5 | 264.1 | 255.2 | 269.8 | 283.6 | 255.4 | 269.5 | 276.4
2431 | 2210 | -6.4 | 0 | 0 | 312.2 | 255.2 | 252 | 251.3 | 293.5 | 47 | 18.2 | 76.6 | 3.8 | 208.8 | 3.4 | 448.2 | 452.6 | 423.6 | 96.4 | 550.7 | 563.8 | 177.5 | 110.8 | 286.1 | 584 | 345.9 | 389.4 | 549.4 | 342 | 323.2 | 581.3 | 434 | 298.2 | 264 | 255 | 269.7 | 283.4 | 255.2 | 269.4 | 276.2
2432 | 2211 | -6.6 | 0 | 0 | 312 | 255.1 | 251.9 | 250.9 | 294.1 | 47 | 18.2 | 76.5 | 3.9 | 221.8 | 3.3 | 448.2 | 452.5 | 424.3 | 96.4 | 550.6 | 563.6 | 177.1 | 110.8 | 285.9 | 583.9 | 345.1 | 389 | 549.1 | 342 | 321.7 | 581.4 | 433.8 | 298 | 263.8 | 254.8 | 269.5 | 283.2 | 255.1 | 269.2 | 276.1
2433 | 2212 | -6.7 | 0 | 0 | 311.7 | 255 | 251.8 | 251 | 294 | 47.1 | 18.2 | 76.5 | 3.9 | 247 | 4 | 448.2 | 452.5 | 427.8 | 96.4 | 550.5 | 563.4 | 176.5 | 111 | 285.6 | 583.8 | 344.5 | 389.1 | 548.8 | 341 | 322.1 | 581.5 | 433.6 | 297.8 | 263.6 | 254.6 | 269.3 | 283 | 255 | 269 | 275.9
2434 | 2213 | -6.7 | 0 | 0 | 311.8 | 254.9 | 251.4 | 250.8 | 293.3 | 47.2 | 18.2 | 76.4 | 3.9 | 242.7 | 4.4 | 448.2 | 452.3 | 428 | 96.4 | 550.4 | 563.2 | 176 | 111.1 | 285.4 | 583.7 | 345.3 | 389.1 | 548.5 | 340.3 | 320.6 | 581.4 | 433 | 297.6 | 263.4 | 254.4 | 269.1 | 282.8 | 254.9 | 269.1 | 275.7
2435 | 2214 | -6.7 | 0 | 0 | 311.3 | 254.8 | 251.4 | 250.4 | 292.5 | 47.2 | 18.2 | 76.3 | 3.9 | 228.5 | 4.9 | 448.2 | 452.4 | 424.5 | 96.3 | 550.3 | 563 | 175.1 | 111.1 | 285.2 | 583.7 | 344.8 | 389 | 548.2 | 339.4 | 318.7 | 581.4 | 432.5 | 297.3 | 263.2 | 254.3 | 269 | 282.6 | 254.8 | 269 | 275.5
2436 | 2215 | -6.7 | 0 | 0 | 311 | 254.8 | 250.9 | 250.3 | 292.1 | 47.1 | 18.2 | 76.3 | 4 | 234.8 | 5.2 | 448.2 | 452.5 | 423.9 | 96 | 550.3 | 562.8 | 174.1 | 111.3 | 285 | 583.6 | 344.7 | 388.4 | 547.8 | 338.5 | 316.7 | 581.4 | 432.4 | 297.1 | 263.1 | 254.1 | 268.8 | 282.4 | 254.6 | 269 | 275.3
2437 | 2216 | -6.7 | 0 | 0 | 310.4 | 254.7 | 250.7 | 250 | 292 | 47.1 | 18.2 | 76.2 | 3.7 | 235.2 | 5.2 | 448.2 | 452.5 | 425.5 | 95.9 | 550.2 | 562.6 | 173.3 | 111.1 | 284.8 | 583.5 | 344.1 | 387.8 | 547.5 | 337.7 | 315.6 | 581.3 | 432.1 | 296.9 | 263 | 254 | 268.6 | 282.1 | 254.4 | 269.2 | 275.1
2438 | 2217 | -6.7 | 0 | 0 | 310.4 | 254.7 | 250.5 | 249.5 | 291.9 | 47.1 | 18.2 | 76.2 | 4.1 | 225.5 | 4.9 | 448.3 | 452.5 | 424.1 | 95.7 | 550.1 | 562.5 | 173.3 | 110.6 | 284.7 | 583.4 | 344.3 | 387.4 | 547.2 | 336.7 | 315.9 | 581.2 | 431.6 | 296.6 | 262.8 | 254.1 | 268.4 | 281.9 | 254.3 | 269.3 | 274.9
2439 | 2218 | -6.7 | 0 | 0 | 309.9 | 254.7 | 250.2 | 249 | 291.3 | 47.1 | 18.2 | 76.1 | 3.9 | 229.6 | 4.4 | 448.2 | 452.5 | 426.3 | 95.4 | 550 | 562.4 | 172.5 | 110.3 | 284.4 | 583.2 | 344.5 | 387 | 546.8 | 335.2 | 315.8 | 581.2 | 431.1 | 296.4 | 262.6 | 253.9 | 268.3 | 281.7 | 254.2 | 269 | 274.8
2440 | 2219 | -6.7 | 0 | 0 | 308.9 | 254.7 | 250.1 | 248.5 | 290.5 | 47.1 | 18.2 | 76.1 | 3.9 | 254.8 | 4.1 | 448.3 | 452.6 | 424.5 | 95.2 | 549.9 | 562.3 | 172.7 | 109.7 | 284.3 | 583 | 343.9 | 386.7 | 546.4 | 333.4 | 316.3 | 581.1 | 430.8 | 296.2 | 262.5 | 253.7 | 268.1 | 281.5 | 254.5 | 268.7 | 274.6
2441 | 2220 | -6.7 | 0 | 0 | 307.9 | 254.6 | 249.9 | 248.2 | 290 | 47.1 | 18.2 | 76 | 3.5 | 265.9 | 3.8 | 448.3 | 452.6 | 420.6 | 95 | 549.9 | 562.2 | 172.8 | 109 | 284.2 | 582.8 | 343.3 | 386.1 | 546 | 332.5 | 317 | 580.9 | 430.6 | 296 | 262.4 | 253.5 | 267.9 | 281.3 | 254.6 | 268.4 | 274.4
2442 | 2221 | -6.7 | 0 | 0 | 307.4 | 254.5 | 249.6 | 248.1 | 289.8 | 47.1 | 18.2 | 76 | 3.5 | 246.1 | 3.6 | 448.3 | 452.6 | 421.9 | 94.9 | 549.8 | 562.1 | 173.1 | 108.8 | 284.1 | 582.4 | 342.5 | 385.5 | 545.6 | 332.2 | 318.1 | 580.9 | 430.6 | 295.7 | 262.4 | 253.5 | 267.8 | 281.1 | 254.8 | 268.3 | 274.2
2443 | 2222 | -6.7 | 0 | 0 | 306.7 | 254.3 | 249.4 | 247.9 | 289.2 | 47.1 | 18.2 | 76 | 3.7 | 220.2 | 3.9 | 448.3 | 452.7 | 419 | 94.6 | 549.7 | 562.1 | 172.9 | 108.5 | 283.9 | 582 | 342.1 | 385.5 | 545.3 | 331.8 | 318.2 | 580.9 | 430.3 | 295.5 | 262.3 | 253.4 | 267.6 | 280.9 | 254.7 | 268.2 | 274
2444 | 2223 | -6.7 | 0 | 0 | 307 | 254.2 | 249.1 | 247.7 | 289 | 47.1 | 18.2 | 76 | 3.9 | 241.8 | 4.2 | 448.3 | 452.6 | 417.8 | 94.3 | 549.6 | 562.1 | 173.5 | 108.5 | 283.7 | 581.5 | 340.4 | 385.6 | 544.9 | 331.2 | 318.9 | 580.7 | 430.3 | 295.3 | 262.2 | 253.2 | 267.4 | 280.7 | 254.9 | 268 | 273.8
2445 | 2224 | -6.7 | 0 | 0 | 307.8 | 254.1 | 248.7 | 247.5 | 289 | 47.1 | 18.2 | 75.9 | 3.6 | 247.7 | 4.5 | 448.3 | 452.6 | 417.8 | 94 | 549.5 | 562.1 | 172.6 | 108.4 | 283.4 | 581.2 | 339.5 | 385.8 | 544.5 | 330.4 | 318.1 | 580.2 | 430.2 | 295.1 | 262.2 | 253.1 | 267.2 | 280.5 | 255 | 267.8 | 273.6
2446 | 2225 | -6.7 | 0 | 0 | 309.2 | 254 | 248.3 | 247.2 | 289 | 47.1 | 18.2 | 75.9 | 3.4 | 240.3 | 4.6 | 448.3 | 452.5 | 418.2 | 93.8 | 549.3 | 562.1 | 172.2 | 108.1 | 283.2 | 580.9 | 340.7 | 385 | 544.1 | 328.8 | 318.4 | 580 | 429.7 | 294.8 | 262.1 | 253.2 | 267.1 | 280.3 | 255.2 | 267.7 | 273.4
2447 | 2226 | -6.7 | 0 | 0 | 310.6 | 253.9 | 247.8 | 247 | 288.7 | 47.1 | 18.2 | 75.9 | 3.6 | 239.2 | 4.6 | 448.3 | 452.4 | 427.9 | 93.7 | 549.3 | 562.1 | 171.5 | 107.8 | 283.1 | 580.6 | 338.9 | 383.8 | 543.7 | 327.6 | 317.3 | 579.8 | 429 | 294.6 | 261.9 | 253.2 | 266.9 | 280.1 | 255 | 268.1 | 273.2
2448 | 2227 | -6.7 | 0 | 0 | 309.8 | 253.8 | 247.6 | 246.8 | 288.4 | 47.1 | 18.2 | 75.8 | 3.7 | 240 | 4.6 | 448.2 | 452.7 | 430.4 | 93.7 | 549.2 | 562.1 | 171.1 | 107.6 | 282.9 | 580.4 | 337.8 | 382.3 | 543.4 | 327.2 | 316.9 | 579.9 | 428.6 | 294.4 | 261.7 | 253.1 | 266.7 | 279.9 | 254.9 | 267.9 | 273
2449 | 2228 | -6.7 | 0 | 0 | 309 | 253.7 | 247.8 | 246.7 | 288 | 47 | 18.2 | 75.7 | 3.4 | 242.4 | 4.6 | 448.2 | 452.8 | 427.5 | 93.7 | 549.1 | 562 | 170.3 | 107.9 | 282.7 | 580.4 | 337 | 381.5 | 543 | 327.2 | 316.7 | 580 | 428.2 | 294.2 | 261.5 | 252.9 | 266.6 | 279.7 | 254.9 | 267.6 | 272.9
2450.1 | 2229.1 | -6.6 | 0 | 0 | 308.1 | 253.6 | 247.9 | 246.7 | 287.8 | 47 | 18.2 | 75.7 | 3.5 | 242.4 | 4.6 | 448.2 | 452.9 | 430 | 93.5 | 549 | 562 | 169.8 | 108.1 | 282.5 | 580.4 | 337.8 | 381.3 | 542.6 | 327.2 | 316.4 | 580 | 427.9 | 293.9 | 261.3 | 252.8 | 266.4 | 279.6 | 255 | 267.4 | 272.7
2451.1 | 2230.1 | -6.5 | 0 | 0 | 306.1 | 253.6 | 247.8 | 246.7 | 287.7 | 47 | 18.2 | 75.7 | 3.2 | 242.4 | 4.6 | 448.2 | 452.9 | 428.1 | 93.2 | 549 | 561.9 | 169.2 | 108.1 | 282.3 | 580.5 | 337.8 | 379.7 | 542.2 | 326.8 | 316.1 | 580 | 427.4 | 293.7 | 261.1 | 252.6 | 266.2 | 279.4 | 254.8 | 267 | 272.5
2452.1 | 2231.1 | -6.7 | 0 | 0 | 304.7 | 253.5 | 247.6 | 246.7 | 287.6 | 47 | 18.2 | 75.7 | 3.6 | 242.8 | 4.6 | 448.2 | 452.9 | 425.7 | 93.1 | 548.9 | 561.7 | 169.4 | 108 | 282 | 580.5 | 336.2 | 379 | 541.8 | 326.3 | 315.3 | 580.1 | 427.2 | 293.5 | 260.9 | 252.5 | 266.1 | 279.2 | 254.6 | 266.6 | 272.3
2453.1 | 2232.1 | -6.7 | 0 | 0 | 303.3 | 253.4 | 247.4 | 247 | 287.7 | 47 | 18.2 | 75.7 | 3.7 | 243.1 | 4.5 | 448.2 | 452.9 | 424.7 | 92.8 | 548.8 | 561.6 | 168.8 | 107.7 | 281.8 | 580.4 | 334.5 | 377.6 | 541.5 | 326.3 | 314.3 | 580.2 | 426.9 | 293.2 | 260.6 | 252.2 | 265.9 | 279 | 254.2 | 266.5 | 272.1
2454.1 | 2233.1 | -6.7 | 0 | 0 | 301.8 | 253.4 | 247 | 247.1 | 287.8 | 47 | 18.2 | 75.7 | 3.5 | 243.7 | 4.4 | 448.2 | 452.9 | 422.2 | 92.4 | 548.8 | 561.4 | 168.7 | 107.6 | 281.5 | 580.2 | 332 | 376.7 | 541.1 | 326.8 | 313.9 | 580.3 | 426.6 | 293 | 260.4 | 252 | 265.7 | 278.7 | 253.9 | 266.4 | 271.9
2455.1 | 2234.1 | -6.7 | 0 | 0 | 301.5 | 253.3 | 246.6 | 247.5 | 287.9 | 47 | 18.2 | 75.6 | 3.4 | 244.9 | 4.4 | 448.2 | 452.9 | 420.2 | 92.1 | 548.7 | 561.2 | 168.4 | 107.4 | 281.2 | 579.9 | 331.1 | 376.7 | 540.8 | 326.6 | 313.4 | 580.1 | 426.4 | 292.8 | 260.2 | 251.8 | 265.5 | 278.6 | 253.6 | 266.5 | 271.8
2456.1 | 2235.1 | -6.7 | 0 | 0 | 301.2 | 253.1 | 246.4 | 247.3 | 287.4 | 46.9 | 18.3 | 75.6 | 3.7 | 245.9 | 4.3 | 448.2 | 453 | 417.7 | 91.9 | 548.7 | 561.1 | 168.5 | 107.1 | 281 | 579.6 | 331.5 | 376.1 | 540.4 | 325.9 | 312 | 579.8 | 426.2 | 292.5 | 260 | 251.6 | 265.3 | 278.4 | 253.4 | 266.7 | 271.6
2457.1 | 2236.1 | -6.7 | 0 | 0 | 301 | 252.8 | 246.5 | 247 | 286.9 | 46.9 | 18.3 | 75.6 | 3.3 | 247.4 | 4.1 | 448.2 | 453.1 | 416.3 | 91.9 | 548.6 | 560.9 | 168.4 | 107.2 | 280.7 | 579.3 | 331.2 | 375.9 | 540 | 326 | 312.3 | 579.6 | 425.9 | 292.3 | 259.8 | 251.4 | 265.1 | 278.2 | 253.2 | 266.4 | 271.4
2458.1 | 2237.1 | -6.7 | 0 | 0 | 300.6 | 252.5 | 246.6 | 246.4 | 286.4 | 46.9 | 18.3 | 75.6 | 3.3 | 250 | 3.9 | 448.2 | 453 | 415.4 | 92 | 548.5 | 560.8 | 168.6 | 107.3 | 280.5 | 579 | 330 | 375.9 | 539.7 | 326.2 | 311.2 | 579.6 | 425.4 | 292.1 | 259.6 | 251.3 | 265 | 278 | 252.8 | 266.2 | 271.2
2459.1 | 2238.1 | -6.7 | 0 | 0 | 300.4 | 252.3 | 246.2 | 245.9 | 286.3 | 46.8 | 18.3 | 75.5 | 3.3 | 252.5 | 3.7 | 448.2 | 453 | 414.4 | 92.2 | 548.5 | 560.7 | 169 | 107.6 | 280.3 | 578.7 | 330.3 | 375.3 | 539.3 | 325.7 | 309.2 | 579.5 | 425 | 291.8 | 259.5 | 251.2 | 264.8 | 277.8 | 252.4 | 266.3 | 271
2460.1 | 2239.1 | -6.7 | 0 | 0 | 300.3 | 252.2 | 246 | 245.7 | 285.9 | 46.8 | 18.3 | 75.5 | 3.4 | 253.7 | 3.6 | 448.2 | 453.1 | 415.1 | 92.3 | 548.4 | 560.5 | 168.4 | 107.9 | 280.1 | 578.5 | 330.8 | 374.7 | 539 | 325.6 | 307.6 | 579.4 | 424.8 | 291.6 | 259.3 | 251.1 | 264.6 | 277.6 | 252.1 | 266.5 | 270.9
2461.1 | 2240.1 | -6.6 | 0 | 0 | 300 | 252 | 246.1 | 245.5 | 285.9 | 46.8 | 18.3 | 75.4 | 3.7 | 254.7 | 3.5 | 448.2 | 453.1 | 414.2 | 92.2 | 548.3 | 560.4 | 168.1 | 107.9 | 279.9 | 578.4 | 332.1 | 375 | 538.5 | 324.7 | 308.3 | 579.1 | 424.4 | 291.4 | 259.1 | 250.8 | 264.4 | 277.4 | 252 | 266.1 | 270.7
2462.1 | 2241.1 | -6.3 | 0 | 0 | 299.6 | 251.8 | 245.9 | 245.1 | 285.9 | 46.7 | 18.3 | 75.4 | 3.6 | 257 | 3.3 | 448.2 | 453 | 413.6 | 92.3 | 548.2 | 560.2 | 167.9 | 107.7 | 279.6 | 578.1 | 332.6 | 374.9 | 538.1 | 324.3 | 307.2 | 579.2 | 424.2 | 291.1 | 258.9 | 250.6 | 264.2 | 277.2 | 251.8 | 265.8 | 270.5
2463.1 | 2242.1 | -6.3 | 0 | 0 | 298.7 | 251.6 | 245.9 | 244.7 | 285.7 | 46.7 | 18.3 | 75.4 | 3.7 | 257.1 | 3.2 | 448.2 | 453 | 410.5 | 92.2 | 548.2 | 560.1 | 168 | 107.2 | 279.5 | 577.9 | 333.2 | 375.5 | 537.7 | 323.3 | 307.2 | 579.3 | 423.9 | 290.9 | 258.6 | 250.3 | 264 | 277 | 251.8 | 265.7 | 270.3
2464.1 | 2243.1 | -6.2 | 0 | 0 | 298.2 | 251.3 | 245.9 | 244.4 | 285.5 | 46.7 | 18.3 | 75.3 | 3.4 | 256.2 | 3.1 | 448.2 | 453 | 412 | 92 | 548.1 | 560 | 168.5 | 106.9 | 279.4 | 577.6 | 334.3 | 375.3 | 537.4 | 323.8 | 307.9 | 579.2 | 423.9 | 290.6 | 258.4 | 250.1 | 263.8 | 276.8 | 252.2 | 265.7 | 270.1
2465.1 | 2244.1 | -6.4 | 0 | 0 | 297.7 | 251.1 | 245.6 | 244.2 | 285.3 | 46.6 | 18.3 | 75.3 | 3.5 | 256 | 3 | 448.2 | 453.2 | 412.9 | 91.7 | 548.1 | 559.8 | 168.2 | 106.9 | 279.1 | 577.5 | 333.4 | 375.3 | 537 | 323.9 | 307.3 | 578.9 | 423.6 | 290.4 | 258.2 | 249.9 | 263.7 | 276.6 | 252.2 | 265.4 | 270
2466.1 | 2245.1 | -6.7 | 0 | 0 | 297.7 | 250.8 | 245.3 | 243.9 | 285.1 | 46.7 | 18.3 | 75.3 | 3.4 | 253.8 | 3 | 448.2 | 453.1 | 408.8 | 91.3 | 548 | 559.7 | 167.7 | 106.9 | 278.8 | 577.4 | 333.8 | 375.2 | 536.6 | 323.9 | 306.7 | 578.6 | 423.3 | 290.2 | 258 | 249.9 | 263.5 | 276.5 | 251.9 | 265.1 | 269.8
2467.1 | 2246.1 | -6.7 | 0 | 0 | 297.8 | 250.6 | 245.1 | 243.6 | 285 | 46.7 | 18.3 | 75.3 | 3.7 | 251 | 3 | 448.2 | 453.1 | 406.4 | 91 | 547.9 | 559.5 | 167.9 | 106.6 | 278.6 | 577.3 | 333.5 | 375.2 | 536.2 | 324 | 308 | 578.2 | 423 | 289.9 | 257.7 | 249.8 | 263.4 | 276.2 | 251.6 | 264.7 | 269.6
2468.1 | 2247.1 | -6.7 | 0 | 0 | 297.6 | 250.5 | 245.1 | 243.4 | 285.1 | 46.7 | 18.3 | 75.3 | 4 | 249.9 | 2.9 | 448.2 | 453 | 405.1 | 91 | 547.9 | 559.3 | 167.9 | 106.5 | 278.3 | 577.2 | 332.2 | 375 | 535.9 | 324.5 | 306.7 | 577.9 | 422.6 | 289.7 | 257.5 | 249.6 | 263.2 | 276 | 251.2 | 264.4 | 269.4
2469.1 | 2248.1 | -6.1 | 0 | 0 | 297.1 | 250.4 | 244.8 | 243.2 | 285.2 | 46.7 | 18.3 | 75.3 | 3.9 | 249.1 | 2.9 | 448.2 | 453 | 403.3 | 90.7 | 547.8 | 559.2 | 167.4 | 106.4 | 278.1 | 577 | 332.1 | 375.1 | 535.5 | 325.1 | 306.6 | 578 | 422.5 | 289.5 | 257.3 | 249.4 | 263 | 275.8 | 251 | 264.4 | 269.2
2470.1 | 2249.1 | -5.1 | 0 | 0 | 297 | 250.3 | 244.7 | 243.4 | 285.3 | 46.7 | 18.3 | 75.2 | 3.9 | 249.1 | 2.8 | 448.2 | 453 | 401.2 | 90.5 | 547.8 | 559.1 | 167.3 | 106.2 | 277.8 | 576.8 | 332.9 | 374.9 | 535.2 | 325.5 | 305.7 | 578.2 | 422.1 | 289.3 | 257.2 | 249.2 | 262.8 | 275.6 | 250.7 | 264.2 | 269
2471.1 | 2250.1 | -5.7 | 0 | 0 | 296.4 | 250.2 | 244.4 | 243.4 | 285.2 | 46.7 | 18.3 | 75.1 | 3.8 | 249.1 | 2.7 | 448.2 | 453 | 399.6 | 90.4 | 547.7 | 559 | 167.7 | 106.2 | 277.6 | 576.7 | 332.3 | 374.4 | 534.8 | 326 | 304.8 | 578.1 | 422 | 289 | 257 | 249 | 262.6 | 275.5 | 250.4 | 263.9 | 268.8
2472.1 | 2251.1 | -6.2 | 0 | 0 | 295.6 | 250 | 244.1 | 243.5 | 284.6 | 46.6 | 18.3 | 75.1 | 3.8 | 249 | 2.6 | 448.2 | 453 | 397 | 90.5 | 547.7 | 558.9 | 167 | 106.3 | 277.4 | 576.5 | 332.6 | 373.7 | 534.5 | 326.7 | 304.5 | 577.8 | 421.6 | 288.8 | 256.8 | 248.8 | 262.4 | 275.2 | 250.2 | 263.7 | 268.6
2473.1 | 2252.1 | -6.4 | 0 | 0 | 294.8 | 249.8 | 243.9 | 243.6 | 284.1 | 46.6 | 18.3 | 75 | 4.3 | 248.6 | 2.5 | 448.2 | 453.1 | 395.5 | 90.6 | 547.6 | 558.7 | 166.6 | 106.5 | 277.1 | 576.4 | 332.8 | 373.1 | 534.1 | 327.1 | 305.2 | 578 | 421.3 | 288.6 | 256.6 | 248.6 | 262.2 | 275.1 | 249.9 | 263.5 | 268.5
2474.1 | 2253.1 | -6.5 | 0 | 0 | 293.9 | 249.7 | 244 | 243.6 | 284.1 | 46.5 | 18.3 | 75 | 4.2 | 248.5 | 2.4 | 448.2 | 453.1 | 391.7 | 90.6 | 547.6 | 558.6 | 166.3 | 106.5 | 276.9 | 576.2 | 332.3 | 372.9 | 533.8 | 326.9 | 305.1 | 578 | 421.2 | 288.4 | 256.4 | 248.4 | 262.1 | 274.9 | 249.6 | 263.3 | 268.3
2475.1 | 2254.1 | -6.7 | 0 | 0 | 293.6 | 249.7 | 244 | 243.3 | 283.8 | 46.5 | 18.3 | 75 | 4.3 | 248.2 | 2.4 | 448.2 | 453 | 390.8 | 90.4 | 547.5 | 558.5 | 165.6 | 106.4 | 276.7 | 575.9 | 332.1 | 373.3 | 533.4 | 326.8 | 303.6 | 578 | 421.1 | 288.2 | 256.3 | 248.2 | 261.9 | 274.7 | 249.3 | 263.2 | 268.1
2476.1 | 2255.1 | -6.5 | 0 | 0 | 293 | 249.5 | 243.8 | 243.5 | 283.4 | 46.4 | 18.3 | 74.9 | 4.2 | 248.6 | 2.4 | 448.2 | 453 | 389.5 | 90.1 | 547.5 | 558.4 | 165.4 | 106 | 276.6 | 575.6 | 331.5 | 374 | 533 | 327.1 | 303.4 | 577.8 | 420.7 | 287.9 | 256.2 | 248 | 261.7 | 274.4 | 249.1 | 263.1 | 267.9
2477.1 | 2256.1 | -6.2 | 0 | 0 | 292.1 | 249.4 | 243.5 | 243.5 | 283.1 | 46.4 | 18.3 | 74.9 | 4 | 248 | 2.4 | 448.2 | 453.1 | 388.9 | 89.9 | 547.4 | 558.2 | 165.1 | 105.8 | 276.5 | 575.3 | 333.2 | 373.6 | 532.7 | 326.8 | 303.4 | 577.8 | 420.5 | 287.7 | 255.9 | 247.8 | 261.5 | 274.2 | 249.1 | 263 | 267.8
2478.1 | 2257.1 | -6.5 | 0 | 0 | 291.5 | 249.2 | 243.4 | 243.1 | 282.7 | 46.4 | 18.3 | 74.8 | 3.8 | 248.6 | 2.4 | 448.2 | 453 | 389.7 | 89.8 | 547.3 | 558.1 | 164.7 | 105.7 | 276.2 | 575.1 | 332.1 | 373.8 | 532.3 | 326.9 | 303.4 | 577.7 | 420.3 | 287.5 | 255.6 | 247.6 | 261.4 | 274 | 248.9 | 262.9 | 267.6
2479.1 | 2258.1 | -6.5 | 0 | 0 | 291.5 | 249 | 243.4 | 242.7 | 282.3 | 46.3 | 18.3 | 74.8 | 3.9 | 248.9 | 2.4 | 448.2 | 452.9 | 386.3 | 89.8 | 547.3 | 557.9 | 164.3 | 105.7 | 276.1 | 574.9 | 331 | 373.2 | 532 | 326.6 | 303.8 | 577.5 | 420.1 | 287.2 | 255.5 | 247.4 | 261.2 | 273.7 | 248.7 | 262.6 | 267.4
2480.1 | 2259.1 | -6.6 | 0 | 0 | 291.5 | 248.8 | 243.2 | 242.2 | 282.1 | 46.3 | 18.3 | 74.8 | 4 | 249.2 | 2.3 | 448.2 | 452.9 | 385.7 | 89.8 | 547.2 | 557.8 | 163.8 | 105.6 | 275.9 | 574.7 | 330.2 | 372.9 | 531.6 | 326.5 | 304.7 | 577.4 | 419.9 | 287 | 255.3 | 247.4 | 261 | 273.6 | 249 | 262.6 | 267.2
2481.1 | 2260.1 | -6.7 | 0 | 0 | 291.9 | 248.6 | 242.9 | 241.9 | 281.9 | 46.3 | 18.3 | 74.8 | 3.9 | 249.8 | 2.3 | 448.2 | 452.8 | 384.6 | 89.6 | 547.1 | 557.7 | 163.3 | 105.5 | 275.7 | 574.5 | 330.1 | 372.9 | 531.3 | 326.4 | 305.9 | 577.4 | 419.5 | 286.8 | 255.2 | 247.3 | 260.9 | 273.4 | 249 | 262.5 | 267
2482.1 | 2261.1 | -6.7 | 0 | 0 | 291 | 248.5 | 242.5 | 241.9 | 281.6 | 46.3 | 18.4 | 74.7 | 4 | 254.6 | 2.3 | 448.2 | 452.7 | 381.6 | 89.5 | 547 | 557.7 | 163.6 | 105.1 | 275.6 | 574.2 | 328.8 | 373.3 | 530.9 | 325.9 | 306.2 | 577.2 | 419.4 | 286.6 | 255 | 247.1 | 260.7 | 273.2 | 248.9 | 262.1 | 266.8
2483.1 | 2262.1 | -6.6 | 0 | 0 | 290.1 | 248.5 | 242.1 | 242 | 281.2 | 46.2 | 18.4 | 74.7 | 3.8 | 261.7 | 2.4 | 448.2 | 452.7 | 381.6 | 89.5 | 546.9 | 557.6 | 163.5 | 105.1 | 275.4 | 573.9 | 328.7 | 373.4 | 530.6 | 325.8 | 306.3 | 577 | 418.9 | 286.4 | 254.8 | 246.9 | 260.5 | 273 | 248.8 | 261.9 | 266.7
2484.1 | 2263.1 | -6.5 | 0 | 0 | 289.5 | 248.5 | 241.9 | 241.9 | 281 | 46.2 | 18.4 | 74.7 | 3.5 | 261.4 | 2.6 | 448.2 | 452.7 | 383.3 | 89.6 | 546.9 | 557.6 | 163.6 | 105 | 275.2 | 573.7 | 330.2 | 373.5 | 530.2 | 325.3 | 306 | 576.9 | 418.7 | 286.2 | 254.5 | 246.8 | 260.3 | 272.8 | 248.6 | 261.6 | 266.5
2485.1 | 2264.1 | -6.7 | 0 | 0 | 288.9 | 248.4 | 241.9 | 241.7 | 280.8 | 46.1 | 18.4 | 74.7 | 3.6 | 259.2 | 2.8 | 448.2 | 452.5 | 380.8 | 89.7 | 546.8 | 557.5 | 163.1 | 104.9 | 275 | 573.4 | 330 | 373 | 529.9 | 325.3 | 305.9 | 577 | 418.3 | 285.9 | 254.3 | 246.6 | 260.1 | 272.6 | 248.3 | 261.5 | 266.3
2486.1 | 2265.1 | -6.2 | 0 | 0 | 288.5 | 248.2 | 241.9 | 241.5 | 280.6 | 46.1 | 18.4 | 74.7 | 3.7 | 258.9 | 2.9 | 448.2 | 452.5 | 380.9 | 89.9 | 546.7 | 557.4 | 163.4 | 105 | 274.8 | 573.1 | 328.3 | 372.4 | 529.5 | 325.7 | 306 | 576.9 | 418.4 | 285.7 | 254.1 | 246.4 | 260 | 272.4 | 248.1 | 261.5 | 266.2
2487.1 | 2266.1 | -6 | 0 | 0 | 288.2 | 248 | 241.7 | 241.6 | 280.5 | 46 | 18.4 | 74.7 | 3.7 | 259 | 3 | 448.2 | 452.5 | 379.2 | 90 | 546.6 | 557.3 | 163.9 | 105.3 | 274.8 | 572.8 | 326.3 | 371.9 | 529.2 | 325.7 | 304.3 | 576.8 | 418.3 | 285.4 | 253.9 | 246.2 | 259.8 | 272.3 | 248.1 | 261.2 | 266
2488.1 | 2267.1 | -6.5 | 0 | 0 | 288.5 | 247.8 | 241.2 | 241.6 | 280 | 45.8 | 18.4 | 74.7 | 3.6 | 259.3 | 3.1 | 448.2 | 452.6 | 381 | 90.1 | 546.5 | 557.2 | 163.3 | 105.1 | 274.6 | 572.5 | 325.4 | 371.4 | 528.8 | 325.7 | 304.9 | 576.8 | 417.9 | 285.2 | 253.7 | 246 | 259.6 | 272.1 | 247.9 | 261 | 265.8
2489.1 | 2268.1 | -6.7 | 0 | 0 | 288.9 | 247.7 | 240.9 | 241.4 | 279.8 | 45.8 | 18.4 | 74.6 | 3.6 | 253.8 | 3.3 | 448.2 | 452.8 | 381.8 | 90.1 | 546.4 | 557.1 | 163 | 104.8 | 274.4 | 572.3 | 326.4 | 370.8 | 528.5 | 325 | 303.2 | 576.4 | 417.7 | 285 | 253.6 | 245.8 | 259.4 | 271.9 | 247.7 | 260.8 | 265.6
2490.1 | 2269.1 | -6.7 | 0 | 0 | 288.7 | 247.5 | 241 | 241.5 | 279.4 | 45.8 | 18.4 | 74.6 | 3.4 | 246.6 | 3.6 | 448.1 | 452.8 | 384.8 | 90 | 546.3 | 557.1 | 162.9 | 104.6 | 274.3 | 572.2 | 326.7 | 369.6 | 528.2 | 324.4 | 301.9 | 576 | 417.1 | 284.8 | 253.4 | 245.6 | 259.2 | 271.7 | 247.4 | 261 | 265.5
2491.1 | 2270.1 | -6.7 | 0 | 0 | 288.2 | 247.5 | 241 | 241.6 | 279.2 | 45.7 | 18.4 | 74.6 | 3.4 | 245.6 | 3.8 | 448.1 | 452.9 | 384.2 | 89.9 | 546.2 | 557 | 162.5 | 104.5 | 274.2 | 572.1 | 325.4 | 368.9 | 527.8 | 323.5 | 302.5 | 575.8 | 416.6 | 284.5 | 253.3 | 245.5 | 259.1 | 271.5 | 247.2 | 261 | 265.3
2492.1 | 2271.1 | -6.7 | 0 | 0 | 288.1 | 247.4 | 241 | 241.3 | 279.1 | 45.7 | 18.4 | 74.5 | 3.4 | 244.6 | 4 | 448.1 | 452.9 | 382.4 | 89.7 | 546.1 | 556.8 | 162 | 104.4 | 274.1 | 572.2 | 323.5 | 368.3 | 527.5 | 323.5 | 303.8 | 575.4 | 416.5 | 284.3 | 253.1 | 245.4 | 258.9 | 271.3 | 247.1 | 260.7 | 265.1
2493.1 | 2272.1 | -6.7 | 0 | 0 | 287.8 | 247.4 | 240.7 | 241.3 | 279.1 | 45.6 | 18.4 | 74.5 | 3.5 | 240.7 | 4.1 | 448.1 | 453 | 384 | 89.5 | 546.1 | 556.7 | 162 | 104.3 | 274 | 572.2 | 321.6 | 368.5 | 527.2 | 323.4 | 304.1 | 575.5 | 416.5 | 284.1 | 253 | 245.3 | 258.8 | 271.1 | 246.8 | 260.3 | 264.9
2494.1 | 2273.1 | -6.4 | 0 | 0 | 287.4 | 247.4 | 240.6 | 241.2 | 279.1 | 45.6 | 18.4 | 74.4 | 3.7 | 238.3 | 4 | 448.1 | 452.9 | 385.1 | 89.5 | 546 | 556.7 | 161.3 | 104.5 | 273.8 | 572.1 | 321.1 | 368.6 | 526.8 | 322.7 | 304 | 575.5 | 416 | 283.9 | 252.8 | 245.1 | 258.6 | 270.9 | 246.6 | 260.1 | 264.8
2495.1 | 2274.1 | -6.3 | 0 | 0 | 287.1 | 247.3 | 240.5 | 241 | 279 | 45.5 | 18.4 | 74.3 | 3.9 | 238.4 | 3.7 | 448.1 | 452.9 | 384.2 | 89.4 | 545.9 | 556.7 | 161.3 | 104.6 | 273.6 | 571.9 | 322.3 | 369.2 | 526.5 | 321.7 | 304.7 | 575.5 | 415.7 | 283.7 | 252.6 | 244.9 | 258.4 | 270.7 | 246.4 | 260 | 264.6
2496.1 | 2275.1 | -6.6 | 0 | 0 | 287.1 | 247.3 | 240.2 | 240.5 | 279.3 | 45.5 | 18.4 | 74.2 | 3.6 | 238 | 3.3 | 448.1 | 452.8 | 382.8 | 89.2 | 545.9 | 556.7 | 161.7 | 104.5 | 273.4 | 571.7 | 322.8 | 369.2 | 526.2 | 321.3 | 304.5 | 575.5 | 415.4 | 283.4 | 252.4 | 244.7 | 258.2 | 270.5 | 246.6 | 259.9 | 264.4
2497.1 | 2276.1 | -6.5 | 0 | 0 | 286.6 | 247.2 | 240 | 240.3 | 279.2 | 45.5 | 18.4 | 74.2 | 3.6 | 238.1 | 3 | 448.1 | 452.9 | 385.3 | 89.1 | 545.8 | 556.6 | 161.9 | 104.4 | 273.2 | 571.5 | 323.1 | 369.2 | 525.8 | 321.8 | 304.1 | 575.7 | 414.9 | 283.2 | 252.2 | 244.5 | 258.1 | 270.4 | 246.5 | 259.7 | 264.2
2498.1 | 2277.1 | -6.2 | 0 | 0 | 286.4 | 246.9 | 239.8 | 240.2 | 279.1 | 45.4 | 18.4 | 74.2 | 3.9 | 232.2 | 2.7 | 448.1 | 453 | 382.9 | 89 | 545.7 | 556.6 | 162 | 104.2 | 273 | 571.1 | 321.8 | 369.3 | 525.5 | 321.3 | 304.7 | 575.8 | 414.7 | 283 | 252 | 244.4 | 257.9 | 270.2 | 246.4 | 259.7 | 264
2499.1 | 2278.1 | -6.6 | 0 | 0 | 286.1 | 246.7 | 239.7 | 240.1 | 278.9 | 45.4 | 18.4 | 74.1 | 3.7 | 220.3 | 2.6 | 448.1 | 453.1 | 382.1 | 88.8 | 545.6 | 556.5 | 161.8 | 104.5 | 272.7 | 570.8 | 320.6 | 369.5 | 525.1 | 321.5 | 304.5 | 575.6 | 414.5 | 282.8 | 251.9 | 244.1 | 257.7 | 270 | 246.5 | 260 | 263.8
2500.1 | 2279.1 | -6.7 | 0 | 0 | 286 | 246.4 | 239.6 | 240.2 | 278.8 | 45.4 | 18.4 | 74 | 4 | 210.2 | 2.5 | 448 | 453.1 | 386.4 | 88.8 | 545.6 | 556.5 | 161.9 | 104.6 | 272.5 | 570.5 | 321.1 | 369.1 | 524.8 | 322.3 | 303.7 | 575.5 | 414.1 | 282.6 | 251.7 | 244 | 257.6 | 269.8 | 246.6 | 259.9 | 263.7
2501.1 | 2280.1 | -6.7 | 0 | 0 | 285.9 | 246.3 | 239.6 | 240.1 | 278.4 | 45.4 | 18.4 | 74 | 3.6 | 208.2 | 2.3 | 448.1 | 453.1 | 387.1 | 88.6 | 545.5 | 556.4 | 161.3 | 104.6 | 272.2 | 570.2 | 321.1 | 368.2 | 524.5 | 322.3 | 302.9 | 575.3 | 413.8 | 282.3 | 251.5 | 243.8 | 257.4 | 269.6 | 246.4 | 259.6 | 263.5
2502.1 | 2281.1 | -6.7 | 0 | 0 | 285.7 | 246 | 239.5 | 239.8 | 278.4 | 45.4 | 18.4 | 73.9 | 3.3 | 207.7 | 2.1 | 448 | 453.2 | 386.6 | 88.4 | 545.5 | 556.3 | 161 | 104.7 | 272 | 570.1 | 319.8 | 366.8 | 524.2 | 322.7 | 302.9 | 575.3 | 413.7 | 282.1 | 251.2 | 243.6 | 257.2 | 269.5 | 246.3 | 259.4 | 263.3
2503.1 | 2282.1 | -6.7 | 0 | 0 | 285.1 | 245.8 | 239 | 239.7 | 278.1 | 45.4 | 18.5 | 73.8 | 3.8 | 208.5 | 2.5 | 448 | 453.2 | 385.3 | 88.1 | 545.4 | 556.2 | 160.6 | 104.6 | 271.8 | 570.1 | 319.5 | 365.8 | 523.9 | 323 | 302.7 | 575.2 | 413.5 | 281.9 | 251 | 243.5 | 257.1 | 269.3 | 246.3 | 259 | 263.1
2504.1 | 2283.1 | -6.7 | 0 | 0 | 284.7 | 245.6 | 238.7 | 239.5 | 277.9 | 45.3 | 18.5 | 73.8 | 3.8 | 211.8 | 3.3 | 448 | 453.2 | 383.7 | 88.1 | 545.4 | 556.1 | 160.7 | 104.7 | 271.6 | 570.2 | 319.3 | 365.7 | 523.6 | 323.4 | 303.3 | 575.1 | 413 | 281.7 | 250.9 | 243.3 | 256.9 | 269.1 | 246.3 | 258.7 | 263
2505.1 | 2284.1 | -6.7 | 0 | 0 | 284.5 | 245.4 | 238.5 | 239.2 | 278 | 45.3 | 18.5 | 73.8 | 4 | 216.3 | 3.7 | 448 | 453.1 | 382.3 | 88.1 | 545.3 | 556 | 160.5 | 104.8 | 271.4 | 570.2 | 319.9 | 364.8 | 523.3 | 323.7 | 302.6 | 575.1 | 412.8 | 281.5 | 250.7 | 243.1 | 256.7 | 269 | 246 | 258.4 | 262.8
2506.1 | 2285.1 | -6.7 | 0 | 0 | 284.1 | 245.3 | 238.3 | 239.1 | 277.7 | 45.3 | 18.5 | 73.7 | 3.8 | 219.2 | 4 | 448 | 453 | 382 | 88.2 | 545.3 | 555.9 | 159.8 | 104.9 | 271.2 | 570.3 | 320.6 | 364.4 | 523 | 323.7 | 301.4 | 574.8 | 412.5 | 281.3 | 250.6 | 242.9 | 256.5 | 268.8 | 245.9 | 258.5 | 262.6
2507.1 | 2286.1 | -6.6 | 0 | 0 | 283.6 | 245.1 | 238.1 | 239.1 | 278.2 | 45.3 | 18.5 | 73.7 | 3.8 | 212.5 | 4.1 | 448 | 453 | 380.5 | 88.2 | 545.3 | 555.7 | 159.7 | 104.9 | 271 | 570.3 | 321.3 | 364.9 | 522.7 | 323.7 | 301.7 | 574.3 | 412.3 | 281.1 | 250.4 | 242.7 | 256.3 | 268.6 | 245.5 | 258.5 | 262.5
2508.1 | 2287.1 | -6.7 | 0 | 0 | 283.3 | 245 | 238.1 | 239.1 | 278.1 | 45.3 | 18.5 | 73.6 | 3.4 | 217.4 | 4.3 | 448 | 453.2 | 382.6 | 88.1 | 545.2 | 555.6 | 160 | 104.9 | 270.8 | 570.2 | 322.1 | 364.7 | 522.4 | 323.5 | 301.6 | 574.1 | 411.9 | 280.8 | 250.3 | 242.6 | 256.2 | 268.4 | 245.2 | 258.3 | 262.3
2509.1 | 2288.1 | -6.7 | 0 | 0 | 283.1 | 244.9 | 237.9 | 239 | 277.8 | 45.2 | 18.5 | 73.6 | 3.6 | 229.7 | 4.3 | 448 | 453.1 | 382 | 88.1 | 545.1 | 555.5 | 159.6 | 104.8 | 270.7 | 570.1 | 322.4 | 364.3 | 522 | 323.4 | 301.3 | 574 | 411.4 | 280.7 | 250.2 | 242.6 | 256 | 268.2 | 245 | 258.1 | 262.1
2510.1 | 2289.1 | -6.2 | 0 | 0 | 282.8 | 244.8 | 237.9 | 239 | 277.6 | 45.2 | 18.5 | 73.5 | 3.9 | 226.1 | 4.5 | 448 | 453.2 | 382.8 | 88.2 | 545.1 | 555.4 | 158.7 | 104.6 | 270.5 | 570 | 322.3 | 364 | 521.7 | 323.8 | 301.7 | 573.9 | 410.8 | 280.5 | 250.1 | 242.5 | 255.9 | 268 | 244.7 | 258.3 | 262
2511.1 | 2290.1 | -6.5 | 0 | 0 | 282.4 | 244.5 | 237.9 | 239.1 | 277.4 | 45.2 | 18.5 | 73.5 | 4 | 214.3 | 4.9 | 448 | 453.3 | 383.7 | 88.1 | 545 | 555.3 | 158.6 | 104.5 | 270.3 | 570 | 321.4 | 362.9 | 521.3 | 323.9 | 301.5 | 573.8 | 410.5 | 280.2 | 249.9 | 242.3 | 255.7 | 267.8 | 244.5 | 258.2 | 261.8
2512.1 | 2291.1 | -6.7 | 0 | 0 | 282 | 244.2 | 238.1 | 238.8 | 277.1 | 45.2 | 18.5 | 73.5 | 4 | 209.3 | 5.3 | 448 | 453.3 | 385.6 | 87.9 | 545 | 555.2 | 158.4 | 104.5 | 270.1 | 570 | 320.9 | 362.1 | 521 | 324.6 | 301.4 | 574.1 | 410.2 | 280 | 249.7 | 242.1 | 255.5 | 267.6 | 244.5 | 258.1 | 261.6
2513.1 | 2292.1 | -6.7 | 0 | 0 | 281.5 | 244 | 238.1 | 238.4 | 277.1 | 45.1 | 18.5 | 73.4 | 3.7 | 213.7 | 5.6 | 447.9 | 453.3 | 384.9 | 87.7 | 544.9 | 555 | 158.3 | 104.3 | 270 | 570 | 321.1 | 361.8 | 520.7 | 325.2 | 300.7 | 573.9 | 410 | 279.9 | 249.6 | 242 | 255.3 | 267.4 | 244.5 | 257.8 | 261.5
2514.1 | 2293.1 | -6.5 | 0 | 0 | 281.5 | 243.9 | 238 | 238.3 | 276.8 | 45.1 | 18.5 | 73.4 | 3.4 | 230.6 | 5.1 | 447.9 | 453.3 | 385.8 | 87.5 | 544.9 | 554.9 | 158.4 | 104.6 | 269.8 | 570.1 | 320.4 | 361.3 | 520.3 | 325.1 | 299.2 | 573.7 | 409.7 | 279.6 | 249.4 | 241.8 | 255.2 | 267.2 | 244.6 | 257.4 | 261.3
2515.1 | 2294.1 | -6.7 | 0 | 0 | 281.5 | 243.9 | 237.7 | 238.1 | 276.6 | 45 | 18.5 | 73.4 | 3.6 | 246.7 | 4.5 | 447.9 | 453.2 | 385.3 | 87.3 | 544.8 | 554.7 | 158.1 | 104.6 | 269.6 | 570.1 | 319.2 | 361.2 | 520 | 325.4 | 298.3 | 573.8 | 409.2 | 279.4 | 249.2 | 241.7 | 255 | 267.1 | 244.4 | 257.3 | 261.1
2516.1 | 2295.1 | -6.7 | 0 | 0 | 281.3 | 244 | 237.2 | 238 | 276.6 | 45 | 18.5 | 73.3 | 3.8 | 245.3 | 4.2 | 447.9 | 453.1 | 389.6 | 87 | 544.8 | 554.6 | 157.9 | 104.2 | 269.4 | 569.9 | 318.8 | 360.9 | 519.7 | 325.3 | 297.9 | 573.7 | 408.9 | 279.2 | 249 | 241.6 | 254.9 | 266.9 | 244.3 | 257 | 260.9
2517.1 | 2296.1 | -6.6 | 0 | 0 | 281 | 244.1 | 237 | 237.8 | 276.7 | 44.9 | 18.5 | 73.3 | 3.8 | 244.3 | 4 | 447.9 | 453 | 387 | 86.5 | 544.7 | 554.4 | 158 | 103.8 | 269.2 | 569.8 | 318.9 | 360.3 | 519.4 | 325.6 | 297.2 | 573.4 | 409 | 279 | 248.8 | 241.4 | 254.7 | 266.7 | 244.4 | 256.9 | 260.7
2518.1 | 2297.1 | -6.6 | 0 | 0 | 280.5 | 244 | 236.9 | 237.6 | 276.7 | 44.9 | 18.5 | 73.3 | 3.7 | 244.5 | 3.8 | 447.9 | 453 | 387.3 | 86.3 | 544.7 | 554.2 | 158 | 103.5 | 269 | 569.6 | 319 | 359.9 | 519.1 | 326.1 | 296.2 | 573.4 | 408.8 | 278.8 | 248.6 | 241.2 | 254.5 | 266.5 | 244.3 | 257 | 260.6
2519.1 | 2298.1 | -6.4 | 0 | 0 | 280 | 243.7 | 236.9 | 237.5 | 276.5 | 44.9 | 18.5 | 73.2 | 3.9 | 246.1 | 3.5 | 447.9 | 452.9 | 390 | 86.1 | 544.6 | 554.1 | 158 | 103.1 | 268.7 | 569.4 | 319.3 | 359.5 | 518.8 | 325.9 | 295.8 | 573 | 408.4 | 278.6 | 248.4 | 241.1 | 254.4 | 266.4 | 244 | 256.9 | 260.4
2520.1 | 2299.1 | -6.5 | 0 | 0 | 279.9 | 243.5 | 236.8 | 237.3 | 276.3 | 44.9 | 18.5 | 73.2 | 3.8 | 247.6 | 3 | 447.9 | 453.1 | 392.6 | 85.9 | 544.6 | 554 | 158 | 102.7 | 268.5 | 569.2 | 320.5 | 359.5 | 518.5 | 325.4 | 295.9 | 572.7 | 408.2 | 278.4 | 248.2 | 240.9 | 254.2 | 266.2 | 243.8 | 256.6 | 260.3
2521.1 | 2300.1 | -6.4 | 0 | 0 | 280 | 243.2 | 236.5 | 237.1 | 275.9 | 44.9 | 18.5 | 73.1 | 3.9 | 239 | 2.6 | 447.9 | 453.2 | 391.8 | 85.7 | 544.5 | 553.8 | 157.7 | 102.3 | 268.2 | 569.1 | 321.8 | 359.5 | 518.1 | 325.3 | 295.5 | 572.3 | 407.9 | 278.2 | 248 | 240.8 | 254 | 266 | 244.1 | 256.5 | 260.1
2522.1 | 2301.1 | -5.7 | 0 | 0 | 280.3 | 243 | 236.3 | 237 | 275.7 | 44.8 | 18.5 | 73.1 | 4.1 | 225 | 2.4 | 447.8 | 453.4 | 392.1 | 85.4 | 544.5 | 553.7 | 157.1 | 102 | 267.9 | 568.9 | 322 | 359.6 | 517.8 | 325.8 | 295.6 | 572.1 | 407.6 | 278 | 247.8 | 240.5 | 253.9 | 265.9 | 244.2 | 256.2 | 259.9
2523.1 | 2302.1 | -5.8 | 0 | 0 | 280.2 | 242.7 | 236.1 | 237 | 275.3 | 44.8 | 18.5 | 73 | 3.8 | 222.7 | 2.3 | 447.8 | 453.4 | 393.2 | 85.2 | 544.4 | 553.6 | 156.8 | 101.7 | 267.7 | 568.6 | 321.7 | 360.4 | 517.5 | 326.4 | 295 | 571.9 | 407.5 | 277.8 | 247.6 | 240.4 | 253.7 | 265.7 | 244.3 | 256.1 | 259.8
2524.1 | 2303.1 | -6.7 | 0 | 0 | 279.9 | 242.5 | 235.7 | 237 | 275.7 | 44.8 | 18.5 | 73 | 3.8 | 222.2 | 2.2 | 447.8 | 453.5 | 392.7 | 85 | 544.4 | 553.4 | 156.8 | 101.6 | 267.4 | 568.4 | 321.8 | 359.4 | 517.2 | 327.1 | 294.3 | 571.8 | 407 | 277.6 | 247.5 | 240.3 | 253.5 | 265.5 | 244 | 256 | 259.6
2525.1 | 2304.1 | -6.4 | 0 | 0 | 279.6 | 242.3 | 235.4 | 236.8 | 276.2 | 44.8 | 18.5 | 73 | 3.3 | 221.8 | 2.2 | 447.8 | 453.5 | 395.1 | 84.8 | 544.3 | 553.3 | 156.5 | 101.6 | 267.1 | 568.3 | 321 | 358.5 | 516.8 | 327.2 | 293 | 571.6 | 406.8 | 277.4 | 247.4 | 240.2 | 253.4 | 265.3 | 243.6 | 255.7 | 259.4
2526.1 | 2305.1 | -6.2 | 0 | 0 | 279.7 | 242.2 | 235.2 | 236.9 | 275.6 | 44.8 | 18.5 | 72.9 | 3.6 | 221.2 | 2.5 | 447.8 | 453.4 | 393.1 | 84.6 | 544.3 | 553.2 | 155.8 | 101.4 | 266.9 | 568.1 | 320.5 | 358 | 516.5 | 327.4 | 293.1 | 571.3 | 406.3 | 277.2 | 247.3 | 240 | 253.2 | 265.2 | 243.3 | 255.4 | 259.3
2527.1 | 2306.1 | -6.4 | 0 | 0 | 280 | 242.1 | 235 | 236.9 | 275.3 | 44.8 | 18.5 | 72.9 | 3.6 | 227.3 | 3 | 447.8 | 453.4 | 392.5 | 84.4 | 544.2 | 553 | 155.3 | 101.2 | 266.7 | 568 | 319.9 | 357.5 | 516.2 | 326.4 | 292.4 | 571.1 | 405.8 | 277 | 247.2 | 239.8 | 253.1 | 265 | 242.9 | 255.4 | 259.1
2528.1 | 2307.1 | -6.7 | 0 | 0 | 280 | 241.9 | 235.2 | 236.5 | 274.6 | 44.7 | 18.5 | 72.8 | 3.7 | 251.7 | 3.4 | 447.8 | 453.3 | 392.2 | 84.2 | 544.2 | 552.8 | 155 | 101.2 | 266.4 | 567.9 | 320 | 357.5 | 515.9 | 325.6 | 291.9 | 571.2 | 405.5 | 276.9 | 247 | 239.7 | 252.9 | 264.8 | 242.6 | 255.3 | 258.9
2529.1 | 2308.1 | -6.5 | 0 | 0 | 279.8 | 241.7 | 235.3 | 236 | 274.2 | 44.7 | 18.5 | 72.8 | 3.7 | 262.1 | 3.4 | 447.8 | 453.2 | 393.3 | 84.1 | 544.1 | 552.7 | 154.6 | 101.4 | 266.3 | 567.7 | 320.3 | 357.1 | 515.6 | 325.4 | 291.2 | 571.3 | 405.4 | 276.6 | 246.9 | 239.5 | 252.7 | 264.7 | 242.2 | 255 | 258.7
2530.1 | 2309.1 | -5.3 | 0 | 0 | 279.8 | 241.5 | 235.2 | 235.6 | 273.8 | 44.6 | 18.5 | 72.8 | 3.5 | 245.5 | 3.3 | 447.7 | 453.3 | 396.6 | 84 | 544.1 | 552.5 | 154.5 | 101.5 | 266.3 | 567.6 | 319.6 | 357 | 515.3 | 325 | 291.4 | 571.2 | 405.2 | 276.4 | 246.8 | 239.4 | 252.6 | 264.5 | 241.9 | 254.8 | 258.6
2531.1 | 2310.1 | -5.9 | 0 | 0 | 279.4 | 241.3 | 235.1 | 235.5 | 273.4 | 44.6 | 18.5 | 72.8 | 3.8 | 234.9 | 3.1 | 447.7 | 453.3 | 394.6 | 84 | 544 | 552.3 | 154.6 | 101.6 | 266.1 | 567.4 | 318.7 | 356.1 | 514.9 | 325.4 | 291.3 | 571.3 | 405.2 | 276.3 | 246.6 | 239.2 | 252.4 | 264.3 | 241.6 | 255 | 258.4
2532.1 | 2311.1 | -6.2 | 0 | 0 | 279.6 | 241.1 | 235.1 | 235.5 | 273.1 | 44.6 | 18.5 | 72.7 | 4 | 234.1 | 2.8 | 447.7 | 453.2 | 392.1 | 83.9 | 544 | 552.2 | 154.5 | 101.4 | 266.1 | 567.3 | 318.3 | 355.5 | 514.6 | 325.7 | 290.5 | 571.3 | 404.8 | 276 | 246.5 | 239 | 252.3 | 264.1 | 241.5 | 255.1 | 258.2
2533.1 | 2312.1 | -6.5 | 0 | 0 | 279.2 | 240.9 | 235 | 235.1 | 273 | 44.6 | 18.6 | 72.7 | 3.7 | 236.7 | 2.8 | 447.7 | 453.1 | 389.4 | 84 | 543.9 | 552 | 153.8 | 101.3 | 266 | 567.2 | 317.3 | 355.2 | 514.3 | 325.5 | 289.1 | 571.3 | 404.6 | 275.8 | 246.4 | 238.8 | 252.1 | 264 | 241.7 | 255.1 | 258.1
2534.1 | 2313.1 | -6.6 | 0 | 0 | 278.7 | 240.8 | 235 | 234.5 | 273 | 44.6 | 18.6 | 72.6 | 3.6 | 238.7 | 3.1 | 447.7 | 453.2 | 388 | 84 | 543.8 | 551.9 | 153.6 | 101.2 | 265.8 | 566.9 | 316.2 | 355.5 | 514 | 325.5 | 289.8 | 571.2 | 404.5 | 275.6 | 246.2 | 238.8 | 252 | 263.8 | 241.8 | 255 | 257.9
2535.1 | 2314.1 | -6.7 | 0 | 0 | 278.2 | 240.7 | 234.7 | 234.2 | 273.2 | 44.5 | 18.6 | 72.6 | 3.4 | 226.3 | 3.1 | 447.7 | 453.1 | 385.9 | 83.9 | 543.8 | 551.8 | 153.4 | 101 | 265.7 | 566.7 | 315.3 | 355.9 | 513.6 | 325.9 | 291.4 | 571.2 | 404.5 | 275.4 | 246 | 238.7 | 251.8 | 263.7 | 241.8 | 254.6 | 257.7
2536.1 | 2315.1 | -6.7 | 0 | 0 | 277.7 | 240.5 | 234.4 | 234.1 | 272.8 | 44.5 | 18.6 | 72.5 | 3.9 | 189 | 3.5 | 447.7 | 453.1 | 384.7 | 83.6 | 543.7 | 551.6 | 153 | 101 | 265.5 | 566.5 | 314.9 | 355.8 | 513.3 | 325.9 | 291.1 | 571 | 404.3 | 275.2 | 245.8 | 238.5 | 251.6 | 263.5 | 241.5 | 254.3 | 257.5
2537.1 | 2316.1 | -6.7 | 0 | 0 | 277.4 | 240.5 | 234.1 | 234 | 272.8 | 44.5 | 18.6 | 72.5 | 3.7 | 181.7 | 3.7 | 447.7 | 453.4 | 382.3 | 83.5 | 543.7 | 551.5 | 152.4 | 100.8 | 265.4 | 566.2 | 315 | 355.7 | 513 | 325.4 | 291.1 | 570.9 | 404 | 275 | 245.6 | 238.3 | 251.5 | 263.3 | 241.3 | 254.2 | 257.3
2538.1 | 2317.1 | -6.7 | 0 | 0 | 276.9 | 240.6 | 233.9 | 233.7 | 272.6 | 44.5 | 18.6 | 72.4 | 3.6 | 193.8 | 3.4 | 447.7 | 453.4 | 378.4 | 83.3 | 543.6 | 551.4 | 151.8 | 100.6 | 265.2 | 566 | 314.5 | 355.1 | 512.6 | 325.1 | 290.9 | 570.6 | 403.8 | 274.8 | 245.4 | 238.1 | 251.3 | 263.2 | 240.9 | 254.1 | 257.2
2539.1 | 2318.1 | -6.6 | 0 | 0 | 277 | 240.6 | 233.8 | 233.5 | 272.6 | 44.5 | 18.6 | 72.4 | 3.5 | 217.3 | 3.1 | 447.6 | 453.5 | 377.5 | 83 | 543.6 | 551.3 | 151.8 | 100.1 | 264.9 | 565.7 | 313.2 | 355.2 | 512.2 | 324.7 | 291.1 | 570.5 | 403.6 | 274.6 | 245.4 | 238 | 251.2 | 263 | 240.6 | 254.3 | 257
2540.1 | 2319.1 | -6.5 | 0 | 0 | 276.9 | 240.5 | 233.8 | 233.5 | 272.3 | 44.5 | 18.6 | 72.3 | 3.6 | 228.5 | 3.3 | 447.6 | 453.7 | 377.7 | 82.6 | 543.5 | 551.2 | 151.4 | 99.5 | 264.7 | 565.4 | 312.9 | 354.8 | 511.9 | 324.7 | 289.2 | 570.6 | 403.3 | 274.5 | 245.3 | 237.9 | 251 | 262.8 | 240.6 | 254.3 | 256.9
2541.1 | 2320.1 | -6.5 | 0 | 0 | 276.4 | 240.4 | 233.8 | 233.1 | 271.9 | 44.4 | 18.6 | 72.3 | 3.6 | 225.1 | 3.5 | 447.6 | 453.8 | 377.6 | 82.3 | 543.4 | 551.1 | 150.8 | 99.1 | 264.4 | 565.2 | 312.1 | 354.2 | 511.6 | 324.3 | 287.7 | 570.3 | 402.9 | 274.3 | 245.2 | 237.7 | 250.9 | 262.6 | 240.8 | 254.2 | 256.7
2542.1 | 2321.1 | -6.5 | 0 | 0 | 275.7 | 240.3 | 233.6 | 232.7 | 272.3 | 44.4 | 18.6 | 72.3 | 3.6 | 223.9 | 3.4 | 447.6 | 453.9 | 377.9 | 82.2 | 543.4 | 551 | 150.6 | 98.8 | 264.1 | 565 | 311.3 | 353.2 | 511.3 | 323.7 | 286.8 | 570.3 | 402.6 | 274.1 | 245 | 237.5 | 250.7 | 262.5 | 240.6 | 254 | 256.5
2543.1 | 2322.1 | -5.4 | 0 | 0 | 275.8 | 240.2 | 233.5 | 232.4 | 272.4 | 44.4 | 18.6 | 72.2 | 4 | 223.9 | 3 | 447.6 | 454 | 378.7 | 82.1 | 543.3 | 550.9 | 149.9 | 98.4 | 263.8 | 564.9 | 310.1 | 352.7 | 510.9 | 323.8 | 286.1 | 570.1 | 402.5 | 273.9 | 244.9 | 237.4 | 250.5 | 262.3 | 240.2 | 253.7 | 256.4
2544.1 | 2323.1 | -4.7 | 0 | 0 | 275.7 | 240 | 233.4 | 232.4 | 272.4 | 44.4 | 18.6 | 72.2 | 3.5 | 224.7 | 2.8 | 447.6 | 453.9 | 375.8 | 82 | 543.2 | 550.8 | 149.7 | 98.2 | 263.5 | 564.7 | 309.1 | 351.7 | 510.6 | 323.6 | 285.4 | 570.2 | 402.2 | 273.7 | 244.7 | 237.2 | 250.4 | 262.1 | 240.1 | 253.8 | 256.2
2545.1 | 2324.1 | -5.7 | 0 | 0 | 275.4 | 239.9 | 233.2 | 232.6 | 272.8 | 44.3 | 18.6 | 72.2 | 3.5 | 232 | 2.8 | 447.6 | 453.9 | 377.5 | 82 | 543.1 | 550.6 | 149.2 | 97.9 | 263.2 | 564.6 | 308.1 | 351.4 | 510.2 | 323.2 | 286.6 | 569.8 | 401.9 | 273.5 | 244.6 | 237.1 | 250.2 | 261.9 | 240.1 | 253.9 | 256
2546.1 | 2325.1 | -6.6 | 0 | 0 | 275.3 | 239.8 | 233.1 | 232.5 | 272.4 | 44.3 | 18.6 | 72.1 | 3.5 | 247.3 | 3.2 | 447.6 | 453.9 | 377.6 | 81.9 | 543 | 550.5 | 149 | 97.7 | 263 | 564.4 | 306.7 | 351.3 | 509.9 | 323.2 | 286.7 | 569.7 | 401.8 | 273.3 | 244.5 | 237 | 250 | 261.8 | 240.3 | 253.7 | 255.9
2547.1 | 2326.1 | -6.7 | 0 | 0 | 275.1 | 239.7 | 232.9 | 232.6 | 271.8 | 44.3 | 18.6 | 72.1 | 3.4 | 242.1 | 3.2 | 447.5 | 453.9 | 374.7 | 81.8 | 543 | 550.4 | 148.8 | 97.4 | 262.8 | 564.2 | 306.5 | 351.1 | 509.5 | 323.1 | 287.7 | 569.8 | 401.7 | 273.1 | 244.3 | 236.8 | 249.9 | 261.6 | 240.6 | 253.3 | 255.7
2548.1 | 2327.1 | -6.6 | 0 | 0 | 274.8 | 239.7 | 232.9 | 232.6 | 271.6 | 44.3 | 18.6 | 72 | 3.1 | 224 | 3.1 | 447.5 | 453.9 | 372 | 81.7 | 542.9 | 550.3 | 148.9 | 97.3 | 262.6 | 564 | 307.1 | 351.2 | 509.2 | 323.6 | 288.7 | 570.1 | 401.6 | 272.9 | 244.2 | 236.7 | 249.8 | 261.5 | 240.8 | 253.3 | 255.6
2549.1 | 2328.1 | -6.5 | 0 | 0 | 274.2 | 239.5 | 232.8 | 232.6 | 272.2 | 44.3 | 18.6 | 72 | 3.5 | 208.2 | 2.9 | 447.5 | 453.9 | 371.6 | 81.6 | 542.8 | 550.1 | 149 | 97.2 | 262.4 | 563.7 | 306.4 | 351 | 508.9 | 323.5 | 288 | 570 | 401.4 | 272.7 | 244.1 | 236.6 | 249.6 | 261.3 | 240.9 | 253.3 | 255.4
2550.1 | 2329.1 | -6.6 | 0 | 0 | 274 | 239.4 | 232.7 | 232.8 | 272.3 | 44.3 | 18.6 | 71.9 | 3.3 | 202.8 | 2.7 | 447.5 | 454 | 369.7 | 81.6 | 542.8 | 550 | 148.7 | 97.1 | 262.2 | 563.4 | 306.1 | 350.7 | 508.6 | 322.9 | 288.5 | 569.7 | 400.8 | 272.5 | 244 | 236.4 | 249.5 | 261.2 | 240.9 | 253.3 | 255.3
2551.1 | 2330.1 | -6.6 | 0 | 0 | 273.7 | 239.2 | 232.8 | 232.7 | 272.1 | 44.2 | 18.6 | 71.9 | 3.4 | 204.4 | 2.6 | 447.5 | 453.9 | 367.4 | 81.6 | 542.7 | 549.9 | 148.3 | 97 | 262 | 563.2 | 305.8 | 350.6 | 508.3 | 322.2 | 288.9 | 569.7 | 400.5 | 272.3 | 243.8 | 236.3 | 249.3 | 261 | 240.6 | 253.3 | 255.1
2552.1 | 2331.1 | -6.6 | 0 | 0 | 273.3 | 239 | 232.8 | 232.5 | 272 | 44.2 | 18.6 | 71.8 | 3.6 | 209.6 | 2.5 | 447.5 | 453.7 | 363.3 | 81.7 | 542.6 | 549.7 | 148.1 | 97 | 261.9 | 562.9 | 305.3 | 350.4 | 507.9 | 322.6 | 289.6 | 569.8 | 400.2 | 272.2 | 243.8 | 236.2 | 249.1 | 260.8 | 240.3 | 253.2 | 254.9
2553.1 | 2332.1 | -6.7 | 0 | 0 | 273.2 | 238.9 | 232.6 | 232.2 | 271.6 | 44.3 | 18.6 | 71.8 | 3.5 | 213.4 | 3 | 447.5 | 453.6 | 361.9 | 81.7 | 542.6 | 549.5 | 148 | 97 | 261.7 | 562.6 | 304.2 | 350.1 | 507.6 | 323.4 | 289.2 | 569.8 | 400.1 | 272 | 243.7 | 236.1 | 249 | 260.7 | 239.9 | 253.3 | 254.8
2554.1 | 2333.1 | -6.7 | 0 | 0 | 273 | 238.7 | 232.4 | 232.1 | 271.3 | 44.3 | 18.6 | 71.7 | 3.5 | 215.3 | 3.5 | 447.5 | 453.7 | 361.1 | 81.8 | 542.5 | 549.4 | 147.9 | 97.1 | 261.6 | 562.3 | 303.6 | 350 | 507.2 | 324 | 290.6 | 569.9 | 399.7 | 271.8 | 243.6 | 235.9 | 248.9 | 260.5 | 239.6 | 253.3 | 254.6
2555.1 | 2334.1 | -6.7 | 0 | 0 | 272.6 | 238.6 | 232.3 | 232.1 | 271 | 44.3 | 18.6 | 71.7 | 3.5 | 222.8 | 3.8 | 447.4 | 453.6 | 359.8 | 81.9 | 542.4 | 549.2 | 147.5 | 97.2 | 261.4 | 562 | 304.6 | 350.1 | 506.9 | 324.2 | 290.9 | 570 | 399.5 | 271.6 | 243.4 | 235.7 | 248.7 | 260.3 | 239.4 | 253.1 | 254.4
2556.1 | 2335.1 | -6.7 | 0 | 0 | 272.4 | 238.4 | 232.2 | 232.1 | 270.8 | 44.3 | 18.6 | 71.6 | 3.4 | 232.4 | 4 | 447.4 | 453.6 | 357.4 | 82 | 542.4 | 549.1 | 146.9 | 97.3 | 261.4 | 561.8 | 305.5 | 349.9 | 506.6 | 323.6 | 291.4 | 569.9 | 399.5 | 271.4 | 243.3 | 235.6 | 248.5 | 260.2 | 239.1 | 253 | 254.3
2557.1 | 2336.1 | -6.7 | 0 | 0 | 272.2 | 238.2 | 231.9 | 232 | 270.7 | 44.3 | 18.6 | 71.6 | 3.7 | 244.4 | 3.8 | 447.4 | 453.7 | 356 | 82.1 | 542.3 | 548.9 | 146.8 | 97.4 | 261.3 | 561.5 | 304.9 | 349.7 | 506.2 | 323.7 | 291.8 | 569.4 | 399.3 | 271.3 | 243.2 | 235.4 | 248.4 | 260 | 238.8 | 252.8 | 254.1
2558.1 | 2337.1 | -6.7 | 0 | 0 | 272.3 | 238 | 231.8 | 231.9 | 270.6 | 44.3 | 18.6 | 71.6 | 3.5 | 247.5 | 3.5 | 447.4 | 453.7 | 353.4 | 82.3 | 542.3 | 548.8 | 146.8 | 97.4 | 261.2 | 561.2 | 304.5 | 349.9 | 506 | 323.8 | 291.8 | 568.9 | 399.1 | 271.1 | 243.2 | 235.3 | 248.2 | 259.8 | 238.6 | 252.8 | 254
2559.1 | 2338.1 | -6.7 | 0 | 0 | 272 | 237.7 | 231.8 | 232 | 270.7 | 44.2 | 18.6 | 71.6 | 3.9 | 233.6 | 3.3 | 447.4 | 453.6 | 352 | 82.6 | 542.2 | 548.7 | 146.4 | 97.6 | 261.2 | 560.9 | 304.6 | 350.9 | 505.6 | 323.8 | 293 | 568.9 | 399.1 | 270.9 | 243 | 235.1 | 248.1 | 259.6 | 238.5 | 252.5 | 253.8
2560.1 | 2339.1 | -6.7 | 0 | 0 | 272 | 237.5 | 231.7 | 231.9 | 270.5 | 44.2 | 18.6 | 71.5 | 3.9 | 215.1 | 3.3 | 447.4 | 453.5 | 351.7 | 83 | 542.1 | 548.6 | 146.8 | 97.8 | 261.1 | 560.6 | 305 | 350.8 | 505.3 | 323.9 | 292.1 | 568.6 | 399 | 270.7 | 242.8 | 235 | 247.9 | 259.5 | 238.2 | 252.2 | 253.6
2561.1 | 2340.1 | -6.7 | 0 | 0 | 272 | 237.4 | 231.6 | 231.7 | 270.5 | 44.1 | 18.6 | 71.5 | 3.8 | 208 | 3.2 | 447.4 | 453.5 | 350 | 83.2 | 542 | 548.6 | 147 | 98 | 261 | 560.4 | 305.2 | 350.6 | 505 | 324.3 | 292.6 | 568.6 | 399 | 270.5 | 242.7 | 234.9 | 247.7 | 259.3 | 237.9 | 252.3 | 253.5
2562.1 | 2341.1 | -6.4 | 0 | 0 | 271.7 | 237.3 | 231.3 | 231.6 | 270.4 | 44.1 | 18.6 | 71.5 | 3.5 | 222.1 | 3.1 | 447.4 | 453.6 | 350.5 | 82.9 | 541.9 | 548.7 | 147.5 | 97.9 | 260.9 | 560.2 | 305.4 | 350.9 | 504.7 | 324.7 | 292 | 568.3 | 398.7 | 270.3 | 242.6 | 235 | 247.6 | 259.1 | 237.7 | 252.2 | 253.3
2563.1 | 2342.1 | -6.2 | 0 | 0 | 271.6 | 237.1 | 231.1 | 231.5 | 270.3 | 44.1 | 18.6 | 71.5 | 3.6 | 227.1 | 3.2 | 447.3 | 453.5 | 351.1 | 82.8 | 541.9 | 548.7 | 147.5 | 97.5 | 260.9 | 560 | 306.6 | 350.7 | 504.4 | 325 | 292.1 | 568.2 | 398.7 | 270.1 | 242.3 | 234.9 | 247.4 | 259 | 237.6 | 252.1 | 253.1
2564.1 | 2343.1 | -6.7 | 0 | 0 | 271.5 | 236.9 | 230.8 | 231.4 | 270.4 | 44 | 18.6 | 71.5 | 3.6 | 223.6 | 3.3 | 447.3 | 453.5 | 350.7 | 82.7 | 541.8 | 548.7 | 147.5 | 97 | 260.8 | 559.8 | 306.7 | 350.5 | 504.1 | 325 | 290.8 | 568.1 | 398.5 | 269.9 | 242.1 | 234.7 | 247.3 | 258.8 | 237.4 | 252 | 253
2565.1 | 2344.1 | -6.7 | 0 | 0 | 271.6 | 236.8 | 230.7 | 231.6 | 270.2 | 44 | 18.7 | 71.5 | 3.2 | 222.5 | 3.4 | 447.3 | 453.4 | 348.5 | 82.6 | 541.7 | 548.8 | 147 | 96.6 | 260.7 | 559.6 | 306.7 | 349.9 | 503.8 | 325.1 | 290.3 | 567.9 | 398.3 | 269.8 | 242 | 234.6 | 247.1 | 258.6 | 237.4 | 251.7 | 252.8
2566.1 | 2345.1 | -6.7 | 0 | 0 | 271.8 | 237 | 230.7 | 231.8 | 269.9 | 44 | 18.7 | 71.5 | 3.2 | 228.5 | 3.3 | 447.3 | 453.6 | 347.7 | 82.5 | 541.6 | 548.8 | 146.4 | 96.4 | 260.5 | 559.4 | 307 | 350.4 | 503.5 | 324.6 | 289.9 | 567.4 | 397.9 | 269.6 | 241.8 | 234.5 | 247 | 258.4 | 237.3 | 251.2 | 252.7
2567.1 | 2346.1 | -6.7 | 0 | 0 | 271.8 | 236.9 | 230.5 | 231.7 | 269.1 | 44 | 18.7 | 71.4 | 2.9 | 239.6 | 3.1 | 447.3 | 453.6 | 344.3 | 82.5 | 541.5 | 548.8 | 145.9 | 96.1 | 260.3 | 559.2 | 307.2 | 351 | 503.2 | 324.7 | 289 | 567 | 397.6 | 269.4 | 241.7 | 234.4 | 246.9 | 258.2 | 236.9 | 250.9 | 252.5
2568.1 | 2347.1 | -6.7 | 0 | 0 | 271.9 | 236.7 | 230.5 | 231.5 | 268.5 | 43.9 | 18.7 | 71.3 | 3 | 246.5 | 3.1 | 447.3 | 453.6 | 343.6 | 82.3 | 541.5 | 548.7 | 145.5 | 95.8 | 260.1 | 559 | 308.1 | 350.5 | 502.9 | 324.6 | 288.5 | 566.6 | 397.2 | 269.2 | 241.5 | 234.3 | 246.7 | 258.1 | 236.6 | 250.5 | 252.4
2569.1 | 2348.1 | -6.7 | 0 | 0 | 272 | 236.6 | 230.4 | 231.3 | 268.4 | 43.9 | 18.7 | 71.3 | 3.5 | 242.7 | 3 | 447.3 | 453.8 | 343.3 | 82.3 | 541.4 | 548.7 | 145.3 | 95.6 | 259.9 | 558.9 | 307.8 | 350.5 | 502.6 | 325.5 | 287.7 | 566.7 | 397.1 | 269 | 241.4 | 234.2 | 246.6 | 257.9 | 236.4 | 250.5 | 252.2
2570.1 | 2349.1 | -6.7 | 0 | 0 | 273.1 | 236.5 | 230.2 | 231.2 | 268 | 43.9 | 18.7 | 71.3 | 3.4 | 241.3 | 3 | 447.2 | 453.7 | 342.9 | 82.2 | 541.4 | 548.7 | 145.2 | 95.4 | 259.8 | 558.8 | 308.9 | 349.5 | 502.3 | 326.2 | 287.2 | 566.7 | 397 | 268.8 | 241.2 | 234.1 | 246.4 | 257.7 | 236.2 | 250.7 | 252.1
2571.1 | 2350.1 | -6.7 | 0 | 0 | 273.6 | 236.3 | 229.9 | 231.1 | 267.9 | 43.9 | 18.7 | 71.3 | 3.5 | 242.5 | 3 | 447.2 | 453.6 | 342.8 | 81.9 | 541.3 | 548.6 | 145.2 | 95.2 | 259.6 | 558.7 | 309.3 | 349.1 | 502.1 | 326.7 | 287.5 | 566.6 | 396.8 | 268.6 | 241.1 | 234 | 246.3 | 257.6 | 236 | 250.6 | 251.9
2572.1 | 2351.1 | -6.6 | 0 | 0 | 273.6 | 236.1 | 229.9 | 231 | 268 | 43.9 | 18.7 | 71.3 | 3.4 | 244.9 | 3 | 447.2 | 453.9 | 344 | 81.8 | 541.3 | 548.6 | 145.4 | 95.1 | 259.4 | 558.5 | 310.6 | 349.3 | 501.8 | 326.8 | 287.4 | 566.6 | 396.9 | 268.5 | 241 | 233.9 | 246.1 | 257.4 | 235.8 | 250.2 | 251.8
2573.1 | 2352.1 | -5.5 | 0 | 0 | 273.5 | 235.9 | 230 | 230.7 | 267.8 | 43.8 | 18.7 | 71.3 | 3.2 | 242.1 | 3.1 | 447.2 | 453.8 | 342.3 | 81.6 | 541.3 | 548.5 | 145.9 | 95.1 | 259.2 | 558.4 | 310.6 | 348.7 | 501.5 | 327.3 | 287.1 | 566.6 | 397 | 268.3 | 240.9 | 233.7 | 246 | 257.2 | 235.6 | 249.7 | 251.6
2574.1 | 2353.1 | -5 | 0 | 0 | 273 | 235.7 | 229.9 | 230.3 | 268.2 | 43.8 | 18.7 | 71.3 | 3.5 | 236.3 | 3.1 | 447.2 | 453.8 | 341.7 | 81.3 | 541.2 | 548.4 | 145.8 | 94.9 | 259 | 558.2 | 310.6 | 348.7 | 501.2 | 327.4 | 287.6 | 566.7 | 396.8 | 268.1 | 240.7 | 233.5 | 245.8 | 257.1 | 235.3 | 249.5 | 251.5
2575.1 | 2354.1 | -5.9 | 0 | 0 | 272.7 | 235.7 | 229.9 | 230.2 | 267.9 | 43.8 | 18.7 | 71.3 | 3.2 | 245.2 | 3.2 | 447.2 | 453.9 | 341.6 | 81.1 | 541.2 | 548.3 | 145.5 | 94.7 | 258.8 | 558 | 311.5 | 348.1 | 500.9 | 326.9 | 286.6 | 566.7 | 396.7 | 267.9 | 240.5 | 233.4 | 245.7 | 256.9 | 235 | 249.6 | 251.3
2576.1 | 2355.1 | -6.2 | 0 | 0 | 272.7 | 235.8 | 229.7 | 229.9 | 267.5 | 43.8 | 18.7 | 71.2 | 3.4 | 246 | 3.4 | 447.2 | 453.8 | 340.3 | 80.9 | 541.1 | 548.1 | 145.1 | 94.6 | 258.6 | 557.8 | 312.8 | 347.6 | 500.6 | 326.2 | 286.6 | 566.5 | 396.4 | 267.7 | 240.4 | 233.2 | 245.5 | 256.7 | 234.8 | 249.4 | 251.2
2577.1 | 2356.1 | -6.7 | 0 | 0 | 272.8 | 235.7 | 229.3 | 229.5 | 267.3 | 43.8 | 18.7 | 71.1 | 3.6 | 241.5 | 3.7 | 447.2 | 453.8 | 341.1 | 80.8 | 541.1 | 548 | 144.7 | 94.5 | 258.5 | 557.6 | 312.2 | 346.1 | 500.3 | 325.5 | 286.5 | 566.6 | 396.3 | 267.5 | 240.3 | 233 | 245.4 | 256.5 | 234.7 | 249.2 | 251
2578.1 | 2357.1 | -6.7 | 0 | 0 | 272.2 | 235.6 | 228.9 | 229.2 | 267 | 43.8 | 18.7 | 71.1 | 3.5 | 242.9 | 3.8 | 447.2 | 453.9 | 341.3 | 80.7 | 541 | 547.9 | 144.6 | 94.3 | 258.4 | 557.4 | 311.4 | 345.9 | 500 | 324.4 | 286.6 | 566.4 | 396.1 | 267.4 | 240.2 | 232.9 | 245.2 | 256.4 | 234.5 | 249.1 | 250.9
2579.1 | 2358.1 | -6.7 | 0 | 0 | 271.8 | 235.4 | 228.7 | 229 | 266.6 | 43.7 | 18.7 | 71 | 3.4 | 244.9 | 3.7 | 447.1 | 453.9 | 343.7 | 80.6 | 541 | 547.8 | 144.2 | 94.3 | 258.3 | 557.1 | 310.3 | 345.2 | 499.8 | 324 | 286.3 | 566.3 | 395.8 | 267.2 | 240.1 | 232.8 | 245.1 | 256.2 | 234.2 | 249.1 | 250.7
2580.1 | 2359.1 | -6.7 | 0 | 0 | 271.3 | 235.2 | 228.6 | 228.7 | 266.4 | 43.7 | 18.7 | 71 | 3.4 | 243.3 | 3.7 | 447.1 | 453.9 | 341.5 | 80.6 | 540.9 | 547.6 | 143.8 | 94.2 | 258.1 | 556.9 | 310.1 | 344.8 | 499.5 | 322.9 | 285.2 | 565.8 | 395.3 | 267 | 239.9 | 232.7 | 244.9 | 256.1 | 233.9 | 249 | 250.5
2581.1 | 2360.1 | -6.3 | 0 | 0 | 270.9 | 235.2 | 228.5 | 228.7 | 266.3 | 43.6 | 18.7 | 71 | 3.4 | 230.8 | 3.5 | 447.1 | 453.9 | 339.6 | 80.5 | 540.9 | 547.5 | 143.6 | 94.2 | 258 | 556.7 | 309.5 | 344.5 | 499.2 | 321.2 | 285.2 | 565.5 | 394.7 | 266.8 | 239.6 | 232.5 | 244.8 | 255.9 | 233.9 | 248.7 | 250.4
2582.1 | 2361.1 | -5.9 | 0 | 0 | 270.1 | 235.1 | 228.5 | 228.6 | 266.6 | 43.6 | 18.7 | 71 | 3.2 | 216.1 | 3.4 | 447.1 | 454.1 | 337.4 | 80.4 | 540.8 | 547.4 | 143.6 | 94.1 | 257.9 | 556.5 | 308.2 | 343.9 | 498.8 | 319.6 | 285.5 | 565.7 | 394.5 | 266.6 | 239.5 | 232.4 | 244.6 | 255.7 | 234.2 | 248.6 | 250.2
2583.1 | 2362.1 | -6.3 | 0 | 0 | 269.3 | 235 | 228.4 | 228.5 | 266.4 | 43.6 | 18.7 | 70.9 | 3 | 211 | 3.2 | 447.1 | 454.1 | 341 | 80.4 | 540.8 | 547.4 | 143.8 | 94.2 | 257.8 | 556.3 | 307 | 344.1 | 498.4 | 318.2 | 285.5 | 565.8 | 394.3 | 266.5 | 239.4 | 232.2 | 244.5 | 255.5 | 234.1 | 248.3 | 250.1
2584.1 | 2363.1 | -6.3 | 0 | 0 | 268.8 | 234.8 | 228.1 | 228.2 | 266 | 43.5 | 18.7 | 70.9 | 3.2 | 216.3 | 3.1 | 447.1 | 454.1 | 341.2 | 80.4 | 540.7 | 547.3 | 143.6 | 94.3 | 257.7 | 556 | 307.6 | 343.8 | 498.1 | 317 | 285.4 | 565.7 | 393.8 | 266.3 | 239.2 | 232.1 | 244.4 | 255.4 | 234.2 | 248 | 249.9
2585.1 | 2364.1 | -6.5 | 0 | 0 | 268.2 | 234.6 | 227.9 | 228 | 266.2 | 43.5 | 18.7 | 70.8 | 3.2 | 228.5 | 3.1 | 447.1 | 454.3 | 339 | 80.3 | 540.7 | 547.3 | 143.3 | 94.4 | 257.6 | 555.8 | 307.5 | 343.5 | 497.7 | 316.4 | 285 | 565.9 | 393.4 | 266.1 | 239 | 232 | 244.2 | 255.2 | 234.1 | 248.1 | 249.8
2586.1 | 2365.1 | -6.5 | 0 | 0 | 267.6 | 234.4 | 227.7 | 227.7 | 266.2 | 43.4 | 18.7 | 70.8 | 3.5 | 236.9 | 3.2 | 447 | 454.2 | 335.3 | 80.3 | 540.7 | 547.2 | 143.2 | 94.6 | 257.5 | 555.6 | 306.5 | 343.1 | 497.5 | 316.7 | 285.2 | 566 | 393.1 | 265.9 | 238.9 | 231.8 | 244.1 | 255.1 | 234.1 | 248.2 | 249.6
2587.1 | 2366.1 | -6.6 | 0 | 0 | 267.2 | 234.2 | 227.4 | 227.8 | 266.8 | 43.4 | 18.7 | 70.8 | 3.3 | 239.7 | 3.2 | 447 | 454.3 | 334.4 | 80.4 | 540.6 | 547.1 | 142.9 | 94.7 | 257.5 | 555.3 | 305.8 | 343.1 | 497.2 | 317.2 | 285.6 | 565.8 | 393.2 | 265.8 | 238.8 | 231.7 | 243.9 | 255 | 234.6 | 247.9 | 249.5
2588.1 | 2367.1 | -6.7 | 0 | 0 | 266.9 | 234.1 | 227.2 | 227.8 | 267.3 | 43.3 | 18.7 | 70.7 | 3.2 | 241.9 | 3.2 | 447 | 454.2 | 333.3 | 80.5 | 540.6 | 547.1 | 142.6 | 94.9 | 257.4 | 555 | 305.5 | 343 | 496.9 | 317.6 | 286 | 565.8 | 393.2 | 265.6 | 238.6 | 231.6 | 243.8 | 254.8 | 234.7 | 248 | 249.3
2589.1 | 2368.1 | -6.7 | 0 | 0 | 266.6 | 234 | 227.3 | 227.7 | 267.7 | 43.3 | 18.8 | 70.7 | 3.2 | 243.5 | 3.1 | 447 | 454.2 | 334.1 | 80.6 | 540.5 | 547 | 142.9 | 94.9 | 257.3 | 554.7 | 305 | 342.9 | 496.6 | 317 | 286.4 | 565.7 | 393.3 | 265.4 | 238.5 | 231.5 | 243.6 | 254.7 | 234.8 | 247.7 | 249.1
2590.1 | 2369.1 | -6 | 0 | 0 | 266.7 | 234 | 227.3 | 227.6 | 267.6 | 43.3 | 18.8 | 70.7 | 3.2 | 242.8 | 2.9 | 447 | 454 | 332.4 | 80.7 | 540.5 | 547 | 143.5 | 95 | 257.2 | 554.5 | 304.5 | 343.1 | 496.2 | 317.1 | 286.9 | 565.5 | 393.4 | 265.2 | 238.3 | 231.4 | 243.5 | 254.5 | 234.8 | 247.5 | 249
2591.1 | 2370.1 | -6.5 | 0 | 0 | 267 | 233.9 | 227 | 227.5 | 267.3 | 43.3 | 18.8 | 70.6 | 3.4 | 242.1 | 2.8 | 447 | 453.8 | 332.2 | 80.8 | 540.4 | 547 | 143.5 | 95 | 257.2 | 554.3 | 303.5 | 343.6 | 495.9 | 316.2 | 286 | 565.2 | 393.4 | 265 | 238.2 | 231.3 | 243.4 | 254.4 | 235 | 247.3 | 248.8
2592.1 | 2371.1 | -6.7 | 0 | 0 | 266.7 | 233.9 | 227 | 227.4 | 266.5 | 43.3 | 18.8 | 70.6 | 3.7 | 241.9 | 2.9 | 447 | 454 | 333.1 | 80.8 | 540.3 | 547 | 143.1 | 94.9 | 257.2 | 554.1 | 302.7 | 342.3 | 495.6 | 315.6 | 285.3 | 565.1 | 393.2 | 264.9 | 238.1 | 231.2 | 243.3 | 254.3 | 234.7 | 247.1 | 248.7
2593.1 | 2372.1 | -6.7 | 0 | 0 | 266.3 | 233.9 | 227.1 | 227.3 | 266.2 | 43.2 | 18.8 | 70.5 | 3.3 | 240.6 | 3 | 447 | 454.3 | 330.9 | 80.6 | 540.3 | 547 | 143.9 | 94.7 | 257.1 | 554 | 302.8 | 341.7 | 495.3 | 314.9 | 285.4 | 564.9 | 392.9 | 264.7 | 237.9 | 231.1 | 243.1 | 254.1 | 234.6 | 246.9 | 248.6
2594.1 | 2373.1 | -6.7 | 0 | 0 | 266 | 234 | 227.2 | 227.4 | 266.1 | 43.2 | 18.8 | 70.5 | 3.2 | 239.5 | 3.1 | 447 | 454.1 | 329.5 | 80.5 | 540.2 | 547 | 144.2 | 94.6 | 256.9 | 553.9 | 303.2 | 342 | 495 | 313.4 | 286.9 | 564.8 | 392.9 | 264.5 | 237.8 | 230.9 | 242.9 | 254 | 235 | 247.1 | 248.4
2595.1 | 2374.1 | -6.7 | 0 | 0 | 266.2 | 234 | 227.1 | 227.4 | 265.4 | 43.2 | 18.8 | 70.5 | 3.7 | 240.3 | 3.1 | 446.9 | 454 | 328.4 | 80.4 | 540.1 | 547.1 | 145.9 | 94.2 | 256.6 | 553.7 | 303.1 | 342.4 | 494.6 | 313.4 | 287.9 | 564.6 | 392.7 | 264.4 | 237.7 | 230.8 | 242.8 | 253.9 | 235.3 | 247.1 | 248.3
2596.1 | 2375.1 | -6.7 | 0 | 0 | 266.6 | 234 | 226.9 | 227.1 | 265.2 | 43.2 | 18.8 | 70.5 | 3.5 | 237.7 | 3 | 446.9 | 453.8 | 327.1 | 80.4 | 540 | 547.2 | 147 | 94 | 256.6 | 553.6 | 303.4 | 342.9 | 494.3 | 313.1 | 288.9 | 564.7 | 392.4 | 264.1 | 237.6 | 230.7 | 242.6 | 253.8 | 235.3 | 247 | 248.1
2597.1 | 2376.1 | -6.7 | 0 | 0 | 266.4 | 234 | 226.7 | 227 | 264.8 | 43.2 | 18.8 | 70.5 | 3.1 | 234 | 3 | 446.9 | 453.8 | 333 | 80.3 | 539.9 | 547.4 | 147.4 | 94 | 256.5 | 553.5 | 304.4 | 342.9 | 494 | 313.3 | 287.7 | 564.5 | 392 | 264 | 237.5 | 230.7 | 242.5 | 253.6 | 235 | 247 | 248
2598.1 | 2377.1 | -6.7 | 0 | 0 | 266.2 | 233.9 | 226.6 | 226.9 | 264.3 | 43.2 | 18.8 | 70.5 | 3.4 | 227.4 | 3 | 446.9 | 453.9 | 335.3 | 80.2 | 539.8 | 547.6 | 147.3 | 93.8 | 256.4 | 553.4 | 304.7 | 342.7 | 493.7 | 313.4 | 288.1 | 564.6 | 391.6 | 263.8 | 237.3 | 230.6 | 242.4 | 253.5 | 234.7 | 246.8 | 247.9
2599.1 | 2378.1 | -6.7 | 0 | 0 | 265.9 | 233.8 | 226.7 | 226.8 | 264 | 43.2 | 18.8 | 70.4 | 3.6 | 222.7 | 2.8 | 446.9 | 454.1 | 341.5 | 80.2 | 539.7 | 547.8 | 147.1 | 93.8 | 256.4 | 553.3 | 304.6 | 342 | 493.4 | 313.7 | 286.8 | 564.6 | 391.2 | 263.7 | 237.2 | 230.4 | 242.3 | 253.3 | 234.5 | 246.8 | 247.7
2600.1 | 2379.1 | -6.7 | 0 | 0 | 265.8 | 233.6 | 226.8 | 226.5 | 263.5 | 43.1 | 18.8 | 70.4 | 3.4 | 219.7 | 2.8 | 446.9 | 454.2 | 344 | 80.2 | 539.6 | 547.9 | 146.3 | 93.8 | 256.4 | 553.2 | 304.2 | 341.9 | 493.1 | 314.6 | 286.5 | 564.9 | 391.1 | 263.5 | 237.1 | 230.2 | 242.1 | 253.2 | 234.4 | 246.8 | 247.6
2601.1 | 2380.1 | -6.7 | 0 | 0 | 265.6 | 233.6 | 226.8 | 226.3 | 263.6 | 43.1 | 18.8 | 70.3 | 3.3 | 219 | 2.7 | 446.8 | 454.2 | 347.7 | 80 | 539.5 | 548 | 146 | 93.8 | 256.3 | 553.1 | 304.8 | 341.1 | 492.9 | 314.1 | 285.9 | 564.9 | 390.8 | 263.3 | 237.1 | 230 | 241.9 | 253 | 234.3 | 246.6 | 247.4
2602.1 | 2381.1 | -6.7 | 0 | 0 | 265.4 | 233.6 | 226.5 | 226.4 | 263.9 | 43.1 | 18.8 | 70.3 | 3.4 | 218.1 | 2.6 | 446.8 | 454.4 | 350.3 | 80.1 | 539.4 | 548.1 | 145.6 | 93.8 | 256.2 | 553 | 304.3 | 341 | 492.6 | 313.9 | 286 | 564.9 | 390.3 | 263.1 | 237 | 229.9 | 241.8 | 252.9 | 234.5 | 246.4 | 247.3
2603.1 | 2382.1 | -6.7 | 0 | 0 | 265.3 | 233.5 | 226 | 226.5 | 264.2 | 43.1 | 18.8 | 70.3 | 3.6 | 217.6 | 2.4 | 446.8 | 454.3 | 349.5 | 80.3 | 539.3 | 548.2 | 145 | 93.9 | 256.1 | 552.8 | 304.1 | 340 | 492.3 | 313.3 | 286.3 | 564.7 | 389.9 | 262.9 | 236.9 | 229.8 | 241.6 | 252.8 | 235 | 246.4 | 247.1
2604.1 | 2383.1 | -6.7 | 0 | 0 | 264.9 | 233.4 | 225.6 | 226.6 | 263.9 | 43.1 | 18.8 | 70.3 | 3.3 | 217.2 | 2.2 | 446.8 | 454.4 | 351.5 | 80.5 | 539.3 | 548.3 | 144.8 | 94.1 | 256 | 552.7 | 303.3 | 339.5 | 491.9 | 312.2 | 285 | 564.6 | 389.8 | 262.8 | 236.7 | 229.7 | 241.5 | 252.7 | 235.2 | 246.4 | 247
2605.1 | 2384.1 | -6.7 | 0 | 0 | 264.4 | 233.4 | 225.7 | 226.4 | 263.7 | 43 | 18.8 | 70.2 | 3.6 | 215.4 | 2.2 | 446.8 | 454.4 | 349.3 | 80.7 | 539.2 | 548.3 | 144.3 | 94.2 | 255.9 | 552.7 | 303 | 338.8 | 491.7 | 312.1 | 283.6 | 564.8 | 389.6 | 262.6 | 236.5 | 229.6 | 241.4 | 252.5 | 234.8 | 246.2 | 246.8
2606.1 | 2385.1 | -6.7 | 0 | 0 | 264.8 | 233.2 | 225.7 | 226.5 | 263.3 | 43 | 18.8 | 70.2 | 3.4 | 206.1 | 2.2 | 446.8 | 454.3 | 345.4 | 80.8 | 539.2 | 548.3 | 144.3 | 94.4 | 255.9 | 552.7 | 302.6 | 336.9 | 491.4 | 312.2 | 283.5 | 564.7 | 389.1 | 262.4 | 236.4 | 229.4 | 241.3 | 252.4 | 234.6 | 245.8 | 246.7
2607.1 | 2386.1 | -6.5 | 0 | 0 | 264.6 | 233.1 | 225.6 | 226.5 | 263.3 | 43 | 18.8 | 70.2 | 3.7 | 196.6 | 2.1 | 446.8 | 454.3 | 344.2 | 80.9 | 539.2 | 548.3 | 143.9 | 94.7 | 255.8 | 552.7 | 301.6 | 336 | 491.1 | 312.8 | 283.6 | 564.6 | 388.6 | 262.3 | 236.3 | 229.3 | 241.1 | 252.2 | 234.6 | 245.8 | 246.5
2608.1 | 2387.1 | -6.4 | 0 | 0 | 264 | 233 | 225.5 | 226.4 | 263.6 | 43 | 18.8 | 70.1 | 3.9 | 194.9 | 2 | 446.7 | 454.2 | 342.8 | 80.9 | 539.2 | 548.2 | 143.5 | 94.9 | 255.6 | 552.7 | 300.6 | 335.2 | 490.8 | 313.9 | 282.7 | 564.6 | 388.2 | 262.1 | 236.1 | 229.2 | 241 | 252.1 | 234.7 | 245.7 | 246.4
2609.1 | 2388.1 | -5.9 | 0 | 0 | 263.7 | 232.8 | 225.3 | 226.3 | 263.9 | 43 | 18.8 | 70.1 | 3.6 | 197.3 | 2.1 | 446.7 | 454.2 | 340.8 | 81 | 539.1 | 548.1 | 143.4 | 95 | 255.6 | 552.6 | 299.9 | 335.3 | 490.6 | 313.8 | 283.5 | 564.4 | 388.2 | 262 | 236 | 229.1 | 240.8 | 252 | 234.8 | 245.7 | 246.2
2610.1 | 2389.1 | -6.3 | 0 | 0 | 263.6 | 232.8 | 225.2 | 226.1 | 264.1 | 43 | 18.8 | 70 | 3.3 | 202.8 | 2.5 | 446.7 | 454.3 | 340.3 | 81 | 539.1 | 548 | 143.3 | 95.2 | 255.5 | 552.5 | 301.4 | 335.5 | 490.3 | 314.1 | 284.5 | 564.3 | 388.4 | 261.8 | 235.8 | 229 | 240.7 | 251.9 | 234.6 | 245.7 | 246.1
2611.1 | 2390.1 | -6.5 | 0 | 0 | 263.2 | 232.7 | 225 | 225.9 | 263.7 | 43 | 18.8 | 70 | 3.1 | 218 | 2.6 | 446.7 | 454.3 | 338.5 | 81.1 | 539.1 | 547.9 | 143.2 | 95.3 | 255.4 | 552.3 | 302 | 336 | 490 | 314.1 | 285.3 | 564.2 | 388.3 | 261.7 | 235.7 | 228.8 | 240.5 | 251.8 | 234.5 | 245.5 | 246
2612.1 | 2391.1 | -6.5 | 0 | 0 | 263.3 | 232.6 | 224.7 | 225.7 | 263.3 | 43 | 18.8 | 70 | 3.3 | 233.6 | 3.1 | 446.7 | 454 | 335.9 | 81.1 | 539.1 | 547.8 | 143 | 95.4 | 255.3 | 552.2 | 301.9 | 336.1 | 489.7 | 314.9 | 285.7 | 564.3 | 388.1 | 261.5 | 235.7 | 228.8 | 240.4 | 251.6 | 234.2 | 245.4 | 245.8
2613.1 | 2392.1 | -6.7 | 0 | 0 | 263 | 232.5 | 224.5 | 225.5 | 263 | 43 | 18.8 | 70 | 3.6 | 232.1 | 3.3 | 446.7 | 453.9 | 333.7 | 81.2 | 539 | 547.6 | 143 | 95.4 | 255.2 | 552.1 | 301.1 | 336.7 | 489.4 | 315.2 | 286.4 | 564.4 | 388.2 | 261.3 | 235.5 | 228.6 | 240.3 | 251.5 | 233.9 | 245.2 | 245.7
2614.1 | 2393.1 | -6.7 | 0 | 0 | 262.6 | 232.3 | 224.5 | 225.3 | 263.1 | 42.9 | 18.8 | 70 | 3.4 | 221.3 | 3.3 | 446.7 | 454 | 337.6 | 81.2 | 539 | 547.5 | 143.5 | 95.5 | 255.1 | 552 | 300.3 | 336.7 | 489.1 | 315.2 | 285.9 | 564 | 388 | 261.2 | 235.3 | 228.5 | 240.1 | 251.3 | 233.6 | 244.9 | 245.6
2615.1 | 2394.1 | -6.7 | 0 | 0 | 262.4 | 232.2 | 224.4 | 225.2 | 263.1 | 42.9 | 18.8 | 69.9 | 3.2 | 210.2 | 2.9 | 446.6 | 453.9 | 348.5 | 81.2 | 539 | 547.4 | 143.8 | 95.6 | 255 | 551.9 | 299.6 | 335.8 | 488.8 | 314.9 | 284 | 563.8 | 387.7 | 261 | 235.3 | 228.4 | 240 | 251.1 | 233.2 | 244.7 | 245.4
2616.1 | 2395.1 | -6.7 | 0 | 0 | 262.2 | 232.1 | 224.2 | 225.1 | 262.9 | 42.9 | 18.8 | 69.9 | 3.6 | 198.6 | 2.6 | 446.6 | 454 | 352.5 | 81.3 | 538.9 | 547.3 | 143.3 | 95.8 | 254.9 | 551.7 | 299.2 | 336.2 | 488.6 | 314.1 | 283.1 | 563.6 | 387.2 | 260.8 | 235.2 | 228.2 | 239.9 | 251 | 233.3 | 244.7 | 245.3
2617.1 | 2396.1 | -6.7 | 0 | 0 | 262.1 | 232 | 224 | 225 | 262.4 | 42.9 | 18.8 | 69.9 | 3.6 | 198.9 | 2.3 | 446.6 | 454.2 | 360.6 | 81.6 | 538.9 | 547.3 | 143.1 | 95.9 | 254.7 | 551.6 | 300.3 | 335.7 | 488.3 | 312.8 | 282.7 | 563.2 | 387.2 | 260.7 | 235 | 228.1 | 239.7 | 250.9 | 233.4 | 244.7 | 245.1
2618.1 | 2397.1 | -6.7 | 0 | 0 | 262 | 231.8 | 223.8 | 224.8 | 261.8 | 42.9 | 18.8 | 69.9 | 3.3 | 210.8 | 2.5 | 446.6 | 454.1 | 367.7 | 81.8 | 538.8 | 547.3 | 142.6 | 96 | 254.6 | 551.5 | 300.8 | 334.8 | 488.1 | 312.4 | 282.4 | 563 | 386.8 | 260.5 | 234.8 | 228 | 239.6 | 250.8 | 233.6 | 244.7 | 245
2619.1 | 2398.1 | -6.7 | 0 | 0 | 261.8 | 231.7 | 223.5 | 224.7 | 261.3 | 42.8 | 18.8 | 69.9 | 3.4 | 215.2 | 3.4 | 446.6 | 454.2 | 368.7 | 81.9 | 538.8 | 547.2 | 142.5 | 96.2 | 254.5 | 551.4 | 300.2 | 334.1 | 487.8 | 312 | 281.4 | 563 | 386.4 | 260.3 | 234.7 | 227.9 | 239.4 | 250.7 | 233.8 | 244.7 | 244.9
2620.1 | 2399.1 | -6.7 | 0 | 0 | 261.8 | 231.6 | 223.3 | 224.7 | 261.1 | 42.8 | 18.8 | 69.8 | 3.3 | 214.6 | 3.8 | 446.6 | 454.3 | 367 | 82.1 | 538.8 | 547.2 | 142.5 | 96.3 | 254.4 | 551.2 | 298.7 | 333.4 | 487.6 | 312.2 | 281.4 | 562.8 | 386.2 | 260.1 | 234.6 | 227.8 | 239.3 | 250.5 | 233.7 | 244.6 | 244.7
2621.1 | 2400.1 | -6.7 | 0 | 0 | 261.7 | 231.5 | 223.3 | 224.6 | 261 | 42.8 | 18.9 | 69.8 | 3.5 | 213.8 | 3.9 | 446.5 | 454.2 | 365.8 | 82.4 | 538.7 | 547.2 | 142.6 | 96.6 | 254.3 | 551.1 | 297.6 | 332.8 | 487.3 | 312.8 | 282.1 | 562.9 | 386 | 260 | 234.5 | 227.8 | 239.2 | 250.4 | 233.3 | 244.4 | 244.6
2622.1 | 2401.1 | -6.7 | 0 | 0 | 261.5 | 231.5 | 223.3 | 224.5 | 260.9 | 42.8 | 18.9 | 69.8 | 3.3 | 209.6 | 3.6 | 446.5 | 454.2 | 368.2 | 82.5 | 538.7 | 547.1 | 142.6 | 96.9 | 254.2 | 550.9 | 296.9 | 331.7 | 487 | 313 | 281.5 | 562.8 | 385.8 | 259.8 | 234.3 | 227.7 | 239.1 | 250.2 | 233.4 | 244.4 | 244.4
2623.1 | 2402.1 | -6.7 | 0 | 0 | 261.4 | 231.4 | 223.2 | 224.3 | 260.7 | 42.8 | 18.9 | 69.8 | 3.2 | 211.1 | 3.5 | 446.5 | 454.3 | 370.5 | 82.4 | 538.6 | 547.2 | 142.3 | 97.2 | 254.1 | 550.7 | 295.5 | 331.1 | 486.8 | 313.4 | 280.5 | 562.6 | 385.5 | 259.6 | 234.2 | 227.5 | 238.9 | 250.1 | 233.5 | 244.1 | 244.3
2624.1 | 2403.1 | -6.6 | 0 | 0 | 261.4 | 231.3 | 223 | 224.3 | 261 | 42.8 | 18.9 | 69.7 | 3.7 | 211.9 | 3.2 | 446.5 | 454.1 | 368.4 | 82.3 | 538.6 | 547.1 | 141.9 | 97.3 | 253.9 | 550.6 | 294.7 | 330.5 | 486.5 | 313.8 | 279 | 562.8 | 385.2 | 259.4 | 234.1 | 227.3 | 238.8 | 250 | 233.5 | 243.8 | 244.2
2625.1 | 2404.1 | -6.4 | 0 | 0 | 261.4 | 231.2 | 223 | 224.2 | 261.3 | 42.8 | 18.9 | 69.7 | 3.6 | 210 | 3 | 446.5 | 454 | 364.1 | 82.2 | 538.6 | 547.1 | 141.7 | 97.3 | 253.8 | 550.5 | 294.3 | 330.1 | 486.2 | 313.3 | 279.3 | 562.8 | 385 | 259.3 | 233.9 | 227.1 | 238.6 | 249.8 | 233.4 | 243.6 | 244
2626.1 | 2405.1 | -6.5 | 0 | 0 | 261.4 | 231.1 | 223.1 | 224 | 261.3 | 42.8 | 18.9 | 69.7 | 3.3 | 211 | 3.2 | 446.5 | 453.9 | 362.8 | 82.2 | 538.5 | 547 | 141.7 | 97.3 | 253.7 | 550.3 | 293.2 | 329.3 | 485.9 | 313.3 | 278.6 | 562.7 | 384.8 | 259.2 | 233.7 | 227 | 238.5 | 249.7 | 233.4 | 243.5 | 243.9
2627.1 | 2406.1 | -6.7 | 0 | 0 | 261.3 | 231 | 223 | 223.7 | 261 | 42.8 | 18.9 | 69.7 | 3 | 214.8 | 3.8 | 446.5 | 453.7 | 360.2 | 82 | 538.5 | 546.8 | 141.9 | 97.2 | 253.6 | 550.2 | 291.9 | 329 | 485.6 | 312.8 | 277.5 | 562.3 | 384.6 | 259 | 233.6 | 226.9 | 238.3 | 249.6 | 233.1 | 243.5 | 243.7
2628.1 | 2407.1 | -6.6 | 0 | 0 | 261.4 | 230.9 | 222.8 | 223.6 | 260.6 | 42.8 | 18.9 | 69.7 | 3.1 | 215.9 | 4.2 | 446.4 | 453.6 | 357.3 | 81.8 | 538.5 | 546.6 | 141.6 | 97.1 | 253.5 | 550 | 291.4 | 328.7 | 485.4 | 312.3 | 277.6 | 562.3 | 384.3 | 258.8 | 233.5 | 226.9 | 238.2 | 249.4 | 232.7 | 243.4 | 243.6
2629.1 | 2408.1 | -6.6 | 0 | 0 | 260.8 | 230.7 | 222.8 | 223.7 | 260.5 | 42.8 | 18.9 | 69.7 | 3.1 | 213.2 | 4.5 | 446.4 | 453.7 | 355.3 | 81.8 | 538.5 | 546.5 | 141.5 | 97 | 253.3 | 549.9 | 290.7 | 328.5 | 485.1 | 312.4 | 277.8 | 562.6 | 384.3 | 258.6 | 233.4 | 226.8 | 238.1 | 249.2 | 232.4 | 243.3 | 243.4
2630.1 | 2409.1 | -6.7 | 0 | 0 | 260.4 | 230.5 | 222.7 | 223.8 | 260.7 | 42.8 | 18.9 | 69.7 | 3.3 | 208.3 | 4.6 | 446.4 | 453.9 | 353.6 | 82 | 538.4 | 546.4 | 141.2 | 97.1 | 253.1 | 549.7 | 290.9 | 327.8 | 484.9 | 312.1 | 277.6 | 562.6 | 384.1 | 258.5 | 233.3 | 226.7 | 238 | 249.1 | 231.9 | 243.2 | 243.3
2631.1 | 2410.1 | -6.7 | 0 | 0 | 260.6 | 230.5 | 222.6 | 223.6 | 260.7 | 42.8 | 18.9 | 69.7 | 3.4 | 207.9 | 4.3 | 446.4 | 454 | 349.1 | 82.1 | 538.4 | 546.3 | 140.7 | 97.1 | 253.1 | 549.5 | 290.9 | 327.5 | 484.6 | 311.8 | 277.9 | 562.6 | 383.9 | 258.3 | 233.2 | 226.6 | 237.8 | 248.9 | 231.5 | 243 | 243.1
2632.1 | 2411.1 | -6.7 | 0 | 0 | 260.4 | 230.4 | 222.6 | 223.5 | 260.5 | 42.7 | 18.9 | 69.6 | 3.3 | 205.5 | 4.2 | 446.4 | 453.8 | 347.2 | 82.1 | 538.3 | 546.2 | 140.6 | 97 | 253 | 549.3 | 291.3 | 327.2 | 484.3 | 311.6 | 278.1 | 562.6 | 383.7 | 258.2 | 233.1 | 226.5 | 237.7 | 248.7 | 231 | 242.8 | 243
2633.1 | 2412.1 | -6.3 | 0 | 0 | 259.9 | 230.2 | 222.5 | 223.4 | 260.1 | 42.7 | 18.9 | 69.6 | 3.1 | 198.4 | 4.3 | 446.3 | 453.9 | 350.2 | 81.9 | 538.3 | 546.1 | 140.7 | 96.9 | 252.9 | 549 | 290.6 | 327 | 484 | 311.6 | 277.7 | 562.7 | 383.4 | 258 | 232.9 | 226.4 | 237.6 | 248.5 | 230.7 | 242.7 | 242.8
2634.1 | 2413.1 | -5.9 | 0 | 0 | 259.8 | 230 | 222.3 | 223.1 | 259.9 | 42.7 | 18.9 | 69.5 | 3.3 | 199 | 4 | 446.3 | 454.2 | 350.7 | 81.7 | 538.2 | 546.1 | 140.4 | 96.8 | 252.8 | 548.7 | 290.5 | 326.3 | 483.8 | 311.8 | 276.6 | 562.6 | 383 | 257.8 | 232.7 | 226.2 | 237.4 | 248.3 | 230.3 | 242.5 | 242.7
2635.1 | 2414.1 | -6.3 | 0 | 0 | 259.9 | 229.8 | 222 | 222.8 | 259.5 | 42.7 | 18.9 | 69.5 | 3.4 | 206.3 | 3.8 | 446.3 | 454.1 | 347.1 | 81.6 | 538.2 | 546 | 140 | 96.8 | 252.7 | 548.5 | 289.9 | 325.7 | 483.5 | 311.5 | 275.6 | 562.6 | 382.7 | 257.7 | 232.6 | 226.1 | 237.3 | 248.2 | 230.2 | 242.4 | 242.5
2636.1 | 2415.1 | -6.6 | 0 | 0 | 260 | 229.6 | 221.8 | 222.7 | 259.4 | 42.7 | 18.9 | 69.5 | 3.5 | 209.4 | 3.6 | 446.3 | 453.9 | 344.2 | 81.5 | 538.2 | 545.9 | 140.1 | 96.8 | 252.6 | 548.4 | 289.4 | 325 | 483.2 | 310.9 | 275.5 | 562.3 | 382.3 | 257.5 | 232.5 | 226 | 237.1 | 248 | 229.8 | 242.4 | 242.4
2637.1 | 2416.1 | -6.7 | 0 | 0 | 259.8 | 229.5 | 221.5 | 222.6 | 259.2 | 42.7 | 18.9 | 69.4 | 3.5 | 223.5 | 3.3 | 446.3 | 453.8 | 342 | 81.3 | 538.1 | 545.7 | 140.1 | 96.5 | 252.5 | 548.2 | 288.4 | 325.1 | 482.9 | 310.4 | 274.3 | 562 | 382.2 | 257.3 | 232.4 | 225.9 | 237 | 247.8 | 229.5 | 242.3 | 242.2
2638.1 | 2417.1 | -6.7 | 0 | 0 | 259.6 | 229.5 | 221.6 | 222.4 | 259.1 | 42.7 | 18.9 | 69.4 | 3.6 | 235.1 | 3.1 | 446.3 | 453.8 | 339.1 | 81 | 538.1 | 545.6 | 139.8 | 96.1 | 252.3 | 548 | 288 | 324.5 | 482.7 | 310.1 | 274.3 | 562 | 382 | 257.1 | 232.3 | 225.8 | 236.9 | 247.7 | 229.7 | 242.3 | 242.1
2639.1 | 2418.1 | -6.7 | 0 | 0 | 259.5 | 229.3 | 221.4 | 222.2 | 258.7 | 42.7 | 18.9 | 69.4 | 3.5 | 235.1 | 2.9 | 446.3 | 453.9 | 335.8 | 80.9 | 538 | 545.4 | 139.9 | 96.2 | 252.1 | 547.9 | 288.6 | 323.5 | 482.4 | 309.6 | 273.8 | 561.5 | 381.8 | 257 | 232.2 | 225.8 | 236.8 | 247.6 | 229.9 | 241.9 | 241.9
2640.1 | 2419.1 | -6.7 | 0 | 0 | 259.6 | 229.1 | 221.2 | 222 | 258.4 | 42.6 | 18.9 | 69.3 | 3.5 | 225.9 | 2.7 | 446.2 | 454 | 334 | 80.9 | 538 | 545.3 | 140.1 | 96.1 | 251.9 | 547.7 | 289.2 | 323.1 | 482.1 | 309.3 | 273.7 | 561.1 | 381.5 | 256.9 | 232 | 225.6 | 236.6 | 247.5 | 230 | 241.8 | 241.8
2641.1 | 2420.1 | -6.7 | 0 | 0 | 259.4 | 229 | 221.1 | 221.7 | 258.2 | 42.6 | 18.9 | 69.3 | 3.8 | 211.6 | 2.7 | 446.2 | 454 | 334.5 | 80.8 | 537.9 | 545.1 | 140 | 96.2 | 251.7 | 547.5 | 289.3 | 322.7 | 481.9 | 309.5 | 273.2 | 561.2 | 381.4 | 256.7 | 231.9 | 225.4 | 236.5 | 247.3 | 230 | 241.8 | 241.6
2642.1 | 2421.1 | -6.7 | 0 | 0 | 259.3 | 229 | 221 | 221.5 | 258 | 42.6 | 18.9 | 69.3 | 3.6 | 197.6 | 2.9 | 446.2 | 454 | 336.2 | 80.8 | 537.9 | 544.9 | 139.8 | 96.1 | 251.6 | 547.2 | 288.7 | 322.4 | 481.6 | 310.2 | 272.4 | 561.3 | 381.2 | 256.5 | 231.7 | 225.2 | 236.3 | 247.2 | 229.8 | 241.9 | 241.5
2643.1 | 2422.1 | -6.7 | 0 | 0 | 259 | 228.8 | 220.9 | 221.6 | 257.7 | 42.6 | 18.9 | 69.3 | 3.2 | 201.6 | 3.4 | 446.2 | 454 | 333.8 | 80.6 | 537.9 | 544.7 | 139.6 | 96 | 251.4 | 547 | 288.2 | 322.7 | 481.3 | 309.9 | 272.6 | 561 | 381.1 | 256.4 | 231.6 | 225.1 | 236.1 | 247 | 229.8 | 241.7 | 241.4
2644.1 | 2423.1 | -6.7 | 0 | 0 | 258.7 | 228.6 | 220.8 | 221.6 | 257.5 | 42.6 | 18.9 | 69.2 | 3.2 | 211 | 4.1 | 446.2 | 454 | 332.1 | 80.4 | 537.8 | 544.5 | 139.6 | 95.9 | 251.3 | 546.9 | 287.6 | 322.1 | 481 | 310.1 | 272.6 | 560.5 | 381 | 256.2 | 231.4 | 224.9 | 236 | 246.9 | 229.6 | 241.5 | 241.2
2645.1 | 2424.1 | -6.7 | 0 | 0 | 258.3 | 228.4 | 220.6 | 221.5 | 257.1 | 42.6 | 18.9 | 69.2 | 3.3 | 207.9 | 4.7 | 446.2 | 453.9 | 331.6 | 80.3 | 537.8 | 544.3 | 139.8 | 95.8 | 251.2 | 546.7 | 286.9 | 321.9 | 480.7 | 310.1 | 272.3 | 560.3 | 381 | 256 | 231.3 | 224.7 | 235.9 | 246.7 | 229.4 | 241.3 | 241.1
2646.1 | 2425.1 | -6.7 | 0 | 0 | 257.9 | 228.2 | 220.5 | 221.2 | 257.3 | 42.5 | 18.9 | 69.1 | 3.4 | 206 | 4.9 | 446.1 | 453.9 | 330.5 | 80.1 | 537.7 | 544.2 | 139.5 | 95.7 | 251.1 | 546.7 | 286.6 | 321.5 | 480.4 | 310.6 | 272.4 | 560 | 380.9 | 255.9 | 231.1 | 224.6 | 235.8 | 246.6 | 229.6 | 241.1 | 240.9
2647.1 | 2426.1 | -6.7 | 0 | 0 | 257.5 | 228.1 | 220.4 | 221 | 257.1 | 42.5 | 18.9 | 69 | 3.5 | 211.4 | 4.6 | 446.1 | 453.9 | 333 | 80 | 537.7 | 544 | 139.3 | 95.7 | 251 | 546.6 | 288.6 | 322 | 480.2 | 310.7 | 272.3 | 559.9 | 380.7 | 255.7 | 231 | 224.5 | 235.6 | 246.5 | 229.6 | 240.9 | 240.8
2648.1 | 2427.1 | -6.7 | 0 | 0 | 257.1 | 228 | 220.4 | 220.9 | 256.7 | 42.5 | 18.9 | 69 | 3.5 | 213.8 | 4.4 | 446.1 | 453.8 | 327.9 | 79.9 | 537.6 | 543.9 | 139.1 | 95.7 | 250.8 | 546.5 | 289 | 321.7 | 479.9 | 310.9 | 271.6 | 559.8 | 380.7 | 255.6 | 230.9 | 224.4 | 235.5 | 246.3 | 229.7 | 240.7 | 240.7
2649.1 | 2428.1 | -6.1 | 0 | 0 | 256.7 | 227.9 | 220.2 | 220.6 | 256.5 | 42.4 | 18.9 | 68.9 | 3.5 | 213.4 | 4.1 | 446.1 | 453.6 | 325.8 | 79.9 | 537.6 | 543.8 | 139 | 95.8 | 250.7 | 546.5 | 288.6 | 321.4 | 479.6 | 310.8 | 270.1 | 559.3 | 380.4 | 255.4 | 230.9 | 224.2 | 235.4 | 246.2 | 229.7 | 240.4 | 240.5
2650.1 | 2429.1 | -6.3 | 0 | 0 | 256.5 | 227.7 | 220.1 | 220.4 | 256.5 | 42.4 | 18.9 | 68.9 | 3.4 | 212.6 | 4.1 | 446.1 | 453.5 | 323 | 79.9 | 537.5 | 543.7 | 139.3 | 95.8 | 250.6 | 546.4 | 288.4 | 320.4 | 479.4 | 310.6 | 269.3 | 559.2 | 380.2 | 255.3 | 230.8 | 224.2 | 235.3 | 246 | 229.4 | 240.2 | 240.4
2651.1 | 2430.1 | -6.6 | 0 | 0 | 256.3 | 227.6 | 220 | 220.3 | 256.6 | 42.4 | 18.9 | 68.9 | 3.2 | 209.5 | 3.9 | 446 | 453.7 | 321.3 | 80 | 537.5 | 543.6 | 138.7 | 95.6 | 250.5 | 546.2 | 287.3 | 320.4 | 479.2 | 310.6 | 268.9 | 558.7 | 379.9 | 255.1 | 230.6 | 224 | 235.2 | 245.9 | 229 | 239.9 | 240.2
2652.1 | 2431.1 | -6.7 | 0 | 0 | 256.1 | 227.5 | 219.9 | 220.4 | 256.8 | 42.3 | 18.9 | 68.8 | 3.3 | 203 | 3.6 | 446 | 453.6 | 319.1 | 79.9 | 537.4 | 543.5 | 138.6 | 95.3 | 250.3 | 546 | 286.9 | 320.4 | 478.9 | 311.6 | 269 | 558.8 | 379.7 | 254.9 | 230.5 | 223.9 | 235 | 245.7 | 228.5 | 239.7 | 240.1
2653.1 | 2432.1 | -6.6 | 0 | 0 | 256 | 227.4 | 220 | 220.4 | 256.8 | 42.3 | 18.9 | 68.8 | 3.4 | 201.1 | 3.5 | 446 | 453.6 | 316.5 | 79.5 | 537.4 | 543.4 | 138.4 | 94.8 | 250.1 | 545.8 | 287 | 321 | 478.7 | 311.6 | 268.9 | 558.7 | 379.6 | 254.8 | 230.3 | 223.8 | 234.9 | 245.6 | 228.1 | 239.6 | 239.9
2654.1 | 2433.1 | -6.5 | 0 | 0 | 256.5 | 227.2 | 220 | 220.4 | 257.1 | 42.3 | 18.9 | 68.7 | 3.3 | 201.5 | 3.4 | 446 | 453.5 | 315.9 | 79 | 537.3 | 543.3 | 138.1 | 94.5 | 249.9 | 545.6 | 287.2 | 321.1 | 478.4 | 312.4 | 268.5 | 558.7 | 379.5 | 254.6 | 230.2 | 223.7 | 234.7 | 245.4 | 227.7 | 239.4 | 239.8
2655.1 | 2434.1 | -6.7 | 0 | 0 | 257.4 | 227 | 219.8 | 220.1 | 257.3 | 42.2 | 18.9 | 68.7 | 3.3 | 201.9 | 3.5 | 446 | 453.4 | 317 | 78.7 | 537.3 | 543.3 | 138 | 94.2 | 249.7 | 545.4 | 286.9 | 320.9 | 478.2 | 312.3 | 267.2 | 558.9 | 379.2 | 254.5 | 230.1 | 223.6 | 234.6 | 245.2 | 227.3 | 239.2 | 239.7
2656.1 | 2435.1 | -6.7 | 0 | 0 | 258 | 226.8 | 219.8 | 219.9 | 257.1 | 42.2 | 19 | 68.7 | 3.2 | 202.1 | 3.4 | 446 | 453.4 | 316.3 | 78.4 | 537.2 | 543.2 | 137.9 | 94.2 | 249.5 | 545.3 | 287.5 | 320.5 | 477.9 | 312.1 | 266.3 | 558.8 | 379 | 254.3 | 230 | 223.5 | 234.5 | 245.1 | 226.9 | 238.8 | 239.5
2657.1 | 2436.1 | -6.7 | 0 | 0 | 258.3 | 226.7 | 219.9 | 219.7 | 256.9 | 42.2 | 19 | 68.6 | 3.2 | 209.6 | 3.2 | 445.9 | 453.5 | 314.1 | 78.2 | 537.2 | 543.1 | 137.5 | 94.1 | 249.3 | 545.1 | 287.4 | 319.1 | 477.7 | 311.9 | 265.7 | 558.7 | 378.8 | 254.1 | 229.9 | 223.4 | 234.3 | 244.9 | 226.6 | 238.5 | 239.4
2658.1 | 2437.1 | -6.6 | 0 | 0 | 258.6 | 226.6 | 219.9 | 219.4 | 256.6 | 42.2 | 19 | 68.6 | 3.3 | 219.7 | 3.1 | 445.9 | 453.7 | 312 | 78.1 | 537.1 | 543 | 137.4 | 94.1 | 249.1 | 544.9 | 289 | 317.5 | 477.4 | 312.1 | 264.6 | 558.7 | 378.6 | 253.9 | 229.7 | 223.2 | 234.2 | 244.8 | 226.2 | 238.1 | 239.2
2659.1 | 2438.1 | -6.6 | 0 | 0 | 258.7 | 226.5 | 219.7 | 219.1 | 256.6 | 42.2 | 19 | 68.6 | 3.6 | 230.3 | 3.2 | 445.9 | 453.8 | 310.9 | 78 | 537.1 | 542.9 | 137.1 | 93.8 | 249 | 544.7 | 289 | 316.4 | 477.2 | 311.5 | 263.6 | 558.5 | 378.4 | 253.8 | 229.6 | 223.1 | 234 | 244.6 | 225.9 | 237.9 | 239.1
2660.1 | 2439.1 | -6.5 | 0 | 0 | 258.9 | 226.3 | 219.6 | 218.8 | 256.6 | 42.2 | 19 | 68.6 | 3.5 | 227.5 | 3.3 | 445.9 | 453.9 | 308.4 | 77.8 | 537.1 | 542.8 | 136.6 | 93.6 | 248.8 | 544.5 | 288.9 | 315.4 | 477 | 311.4 | 263.5 | 558.5 | 378.2 | 253.7 | 229.6 | 223 | 233.9 | 244.4 | 225.6 | 237.5 | 239
2661.1 | 2440.1 | -6.1 | 0 | 0 | 258.8 | 226.2 | 219.5 | 218.6 | 256.6 | 42.2 | 19 | 68.5 | 3.4 | 223.8 | 3.2 | 445.9 | 453.9 | 304.6 | 77.7 | 537 | 542.7 | 136.2 | 93.4 | 248.7 | 544.3 | 287.8 | 315 | 476.7 | 311.2 | 263.4 | 558.7 | 377.8 | 253.5 | 229.5 | 222.9 | 233.8 | 244.2 | 225.3 | 237.4 | 238.9
2662.1 | 2441.1 | -6.5 | 0 | 0 | 258.8 | 226.1 | 219.4 | 218.6 | 256.1 | 42.1 | 19 | 68.5 | 3.3 | 224.1 | 3.1 | 445.9 | 453.8 | 301.8 | 77.5 | 537 | 542.5 | 135.7 | 93.2 | 248.5 | 544.1 | 285.6 | 314.2 | 476.5 | 310.9 | 262.6 | 558.6 | 377.3 | 253.4 | 229.4 | 222.8 | 233.7 | 244.1 | 225.1 | 237.2 | 238.7
2663.1 | 2442.1 | -6.7 | 0 | 0 | 258.1 | 226 | 219.4 | 218.6 | 255.8 | 42.1 | 19 | 68.4 | 3.4 | 224.6 | 3.1 | 445.9 | 453.6 | 299.2 | 77.4 | 537 | 542.3 | 135.1 | 93 | 248.4 | 543.9 | 285.5 | 314 | 476.3 | 310.6 | 263.8 | 558.3 | 377 | 253.2 | 229.3 | 222.7 | 233.6 | 243.9 | 224.9 | 237.1 | 238.6
2664.1 | 2443.1 | -6.6 | 0 | 0 | 257.4 | 225.9 | 219.3 | 218.5 | 255.4 | 42 | 19 | 68.4 | 3.8 | 223.9 | 3.1 | 445.8 | 453.7 | 296 | 77.4 | 537 | 542.1 | 134.1 | 92.8 | 248.3 | 543.8 | 286.1 | 314 | 475.9 | 310.6 | 265.2 | 558.2 | 377 | 253.1 | 229.2 | 222.5 | 233.4 | 243.7 | 224.6 | 237.1 | 238.4
2665.1 | 2444.1 | -6.6 | 0 | 0 | 256.8 | 225.8 | 219.1 | 218.4 | 255 | 42 | 19 | 68.4 | 3.6 | 205.5 | 3.2 | 445.8 | 453.7 | 293.9 | 77.5 | 537 | 541.9 | 133.5 | 92.4 | 248.3 | 543.5 | 285.9 | 314.3 | 475.6 | 309.9 | 266.4 | 558.2 | 376.9 | 252.9 | 229 | 222.3 | 233.3 | 243.6 | 224.3 | 236.9 | 238.3
2666.1 | 2445.1 | -6.4 | 0 | 0 | 256.2 | 225.7 | 218.9 | 218.2 | 254.9 | 42 | 19 | 68.4 | 3.4 | 186.8 | 3.5 | 445.8 | 453.7 | 291.2 | 77.6 | 536.9 | 541.7 | 132.7 | 92.3 | 248.2 | 543.2 | 285.8 | 315 | 475.3 | 309.8 | 267.5 | 558.2 | 376.6 | 252.8 | 228.9 | 222.2 | 233.1 | 243.4 | 224.1 | 236.7 | 238.1
2667.1 | 2446.1 | -6.2 | 0 | 0 | 255.7 | 225.5 | 218.8 | 218 | 254.9 | 42 | 19 | 68.3 | 3.6 | 182.6 | 3.8 | 445.8 | 453.7 | 288 | 77.7 | 536.9 | 541.6 | 132.5 | 92.1 | 248.3 | 543 | 286.2 | 316 | 475 | 309.2 | 268.4 | 558.5 | 376.5 | 252.6 | 228.8 | 222.1 | 233 | 243.3 | 224 | 236.6 | 238
2668.1 | 2447.1 | -6.6 | 0 | 0 | 255.1 | 225.4 | 218.7 | 217.7 | 255.2 | 42 | 19 | 68.3 | 3.2 | 193.1 | 4 | 445.8 | 453.6 | 283.8 | 77.6 | 536.9 | 541.4 | 132.3 | 91.8 | 248.3 | 542.9 | 287.3 | 316.8 | 474.7 | 308.4 | 269 | 558.5 | 376.5 | 252.5 | 228.7 | 222 | 232.9 | 243.1 | 223.8 | 236.4 | 237.8
2669.1 | 2448.1 | -6.7 | 0 | 0 | 254.7 | 225.3 | 218.7 | 217.7 | 255.5 | 41.9 | 19 | 68.3 | 3 | 221.5 | 4.5 | 445.8 | 453.6 | 281.9 | 77.7 | 536.9 | 541.3 | 132.7 | 91.7 | 248.2 | 542.7 | 288.9 | 317.8 | 474.4 | 307.6 | 269.6 | 558.3 | 376.5 | 252.3 | 228.5 | 221.9 | 232.8 | 242.9 | 223.5 | 236.2 | 237.7
2670.1 | 2449.1 | -6.6 | 0 | 0 | 254.2 | 225.1 | 218.7 | 217.9 | 255.2 | 42 | 19 | 68.2 | 3.1 | 217.1 | 4.7 | 445.8 | 453.7 | 282.7 | 77.8 | 536.8 | 541.2 | 133.6 | 91.6 | 248.2 | 542.5 | 289.9 | 318.7 | 474.1 | 306.8 | 270.9 | 558.3 | 376.3 | 252.2 | 228.4 | 221.7 | 232.6 | 242.7 | 223.3 | 235.9 | 237.5
2671.1 | 2450.1 | -6.4 | 0 | 0 | 254 | 224.9 | 218.6 | 217.8 | 254.7 | 42 | 19 | 68.2 | 3.3 | 219.4 | 4.8 | 445.7 | 453.9 | 280.6 | 77.9 | 536.8 | 541.2 | 133.2 | 91.9 | 248.2 | 542.4 | 290.7 | 319.1 | 473.7 | 305.9 | 271.1 | 558.2 | 376.1 | 252 | 228.2 | 221.6 | 232.5 | 242.6 | 223 | 235.8 | 237.4
2672.1 | 2451.1 | -6.5 | 0 | 0 | 253.6 | 224.8 | 218.4 | 217.8 | 254.7 | 42.1 | 19 | 68.1 | 3.5 | 237.5 | 4.7 | 445.7 | 453.9 | 280.5 | 77.9 | 536.7 | 541.3 | 133.1 | 92.1 | 248 | 542.3 | 290 | 319.6 | 473.5 | 305.6 | 269.9 | 558.1 | 375.7 | 251.8 | 228.1 | 221.5 | 232.4 | 242.4 | 222.9 | 235.9 | 237.2
2673.1 | 2452.1 | -6.7 | 0 | 0 | 253.3 | 224.6 | 218.1 | 217.7 | 255.2 | 42.1 | 19 | 68 | 3.3 | 238.8 | 4.4 | 445.7 | 453.7 | 280.7 | 77.9 | 536.7 | 541.6 | 133.6 | 92.2 | 248 | 542.1 | 289.7 | 319.6 | 473.2 | 306.1 | 270.1 | 558.1 | 375.3 | 251.7 | 228 | 221.4 | 232.2 | 242.2 | 222.9 | 236 | 237.1
2674.1 | 2453.1 | -6.7 | 0 | 0 | 253.1 | 224.5 | 217.7 | 217.5 | 255.4 | 42.1 | 19 | 68 | 3.3 | 235.1 | 4.3 | 445.7 | 453.7 | 282.8 | 78.1 | 536.6 | 541.8 | 134.4 | 92.1 | 248 | 542 | 288.7 | 319.6 | 472.8 | 305.6 | 269.6 | 558.1 | 375.2 | 251.5 | 227.9 | 221.3 | 232.1 | 242.1 | 222.9 | 235.9 | 237
2675.1 | 2454.1 | -6.3 | 0 | 0 | 252.8 | 224.4 | 217.4 | 217.3 | 255.5 | 42.1 | 19 | 68 | 3.4 | 247.6 | 4.2 | 445.7 | 453.8 | 284.5 | 78 | 536.5 | 542.1 | 134.6 | 91.9 | 248 | 541.9 | 289.3 | 320 | 472.5 | 305.6 | 270.1 | 558.2 | 375.1 | 251.4 | 227.8 | 221.3 | 232 | 241.9 | 222.9 | 235.8 | 236.8
2676.1 | 2455.1 | -6.1 | 0 | 0 | 252.5 | 224.3 | 217.3 | 217.1 | 255.2 | 42.1 | 19 | 68 | 3.8 | 255.6 | 4.2 | 445.6 | 453.9 | 285.7 | 77.9 | 536.4 | 542.2 | 135.2 | 92.2 | 247.9 | 541.7 | 288.2 | 319.9 | 472.2 | 305.9 | 270.6 | 558.3 | 375 | 251.2 | 227.7 | 221.1 | 231.8 | 241.7 | 222.7 | 235.5 | 236.7
2677.1 | 2456.1 | -6.7 | 0 | 0 | 252.4 | 224.3 | 217.1 | 217 | 255 | 42.1 | 19 | 68 | 3.7 | 238.1 | 4.2 | 445.6 | 454 | 287.5 | 77.9 | 536.4 | 542.4 | 135.6 | 92.2 | 247.8 | 541.6 | 288 | 319.4 | 471.8 | 305.3 | 269.4 | 558.5 | 374.6 | 251.1 | 227.5 | 221 | 231.7 | 241.6 | 222.5 | 235.3 | 236.5
2678.1 | 2457.1 | -6.7 | 0 | 0 | 252.2 | 224.3 | 216.7 | 216.8 | 255.1 | 42.1 | 19 | 68 | 3.6 | 249.3 | 4.2 | 445.6 | 454.1 | 288.2 | 78.1 | 536.3 | 542.5 | 135.2 | 92.4 | 247.8 | 541.4 | 287 | 319.1 | 471.5 | 305.7 | 267.9 | 558.5 | 374.2 | 250.9 | 227.4 | 220.9 | 231.6 | 241.4 | 222.2 | 235.2 | 236.4
2679.1 | 2458.1 | -6.7 | 0 | 0 | 252 | 224.3 | 216.5 | 216.6 | 255.6 | 42.1 | 19 | 67.9 | 3.8 | 247.3 | 4 | 445.6 | 454 | 286.7 | 78.4 | 536.2 | 542.6 | 135.2 | 92.6 | 247.8 | 541.3 | 286.5 | 318 | 471.2 | 305.1 | 267.4 | 558.4 | 373.9 | 250.8 | 227.3 | 220.8 | 231.5 | 241.3 | 222.3 | 235.2 | 236.3
2680.1 | 2459.1 | -6.7 | 0 | 0 | 251.8 | 224.3 | 216.5 | 216.7 | 255.8 | 42.1 | 19 | 67.9 | 3.3 | 231.8 | 4.2 | 445.6 | 453.8 | 286 | 78.6 | 536.2 | 542.7 | 135.1 | 92.5 | 247.8 | 541.2 | 286.6 | 317.4 | 471 | 304.3 | 266.3 | 558 | 373.8 | 250.6 | 227.1 | 220.6 | 231.3 | 241.1 | 222.2 | 234.9 | 236.1
2681.1 | 2460.1 | -6.7 | 0 | 0 | 251.5 | 224.2 | 216.5 | 216.7 | 255.9 | 42 | 19 | 67.9 | 3.4 | 228.7 | 4.6 | 445.6 | 453.8 | 284.8 | 78.9 | 536.1 | 542.7 | 135.1 | 92.6 | 247.7 | 541.1 | 285.7 | 317.3 | 470.8 | 304.5 | 266.8 | 557.6 | 373.7 | 250.5 | 227 | 220.4 | 231.2 | 241 | 222.2 | 234.5 | 236
2682.1 | 2461.1 | -6.4 | 0 | 0 | 251.2 | 224.1 | 216.4 | 216.6 | 255.6 | 42 | 19 | 67.8 | 3.2 | 237.8 | 4.9 | 445.5 | 453.9 | 283.5 | 79 | 536.1 | 542.7 | 136.1 | 92.9 | 247.6 | 540.9 | 284.8 | 316.9 | 470.6 | 304.5 | 267.2 | 557.4 | 373.6 | 250.3 | 226.9 | 220.3 | 231.1 | 240.8 | 222 | 234.1 | 235.8
2683.1 | 2462.1 | -6.3 | 0 | 0 | 251.3 | 223.9 | 216.4 | 216.3 | 255.1 | 42 | 19 | 67.8 | 3.2 | 239.8 | 5.1 | 445.5 | 454 | 284 | 79 | 536 | 542.8 | 137.8 | 93 | 247.6 | 540.7 | 285 | 316.5 | 470.3 | 304.3 | 267.6 | 557.4 | 373.4 | 250.1 | 226.8 | 220.2 | 230.9 | 240.7 | 222 | 234 | 235.7
2684.1 | 2463.1 | -6.7 | 0 | 0 | 251.1 | 223.9 | 216.4 | 216 | 254.7 | 42 | 19.1 | 67.8 | 3.5 | 246.8 | 5.5 | 445.5 | 453.9 | 283.2 | 79 | 535.9 | 542.8 | 137.8 | 93.2 | 247.6 | 540.5 | 285.6 | 316.3 | 470 | 304.7 | 267.8 | 557.3 | 373.3 | 250 | 226.7 | 220.1 | 230.8 | 240.6 | 222.3 | 234.1 | 235.6
2685.1 | 2464.1 | -6.7 | 0 | 0 | 250.7 | 223.8 | 216.4 | 215.8 | 254.5 | 41.9 | 19.1 | 67.7 | 3.4 | 237.4 | 5.2 | 445.5 | 453.7 | 282.1 | 79 | 535.9 | 542.8 | 138.6 | 93.3 | 247.5 | 540.2 | 284.8 | 316.3 | 469.8 | 304.3 | 266.9 | 557.2 | 373.3 | 249.8 | 226.6 | 220 | 230.7 | 240.4 | 222.5 | 234.1 | 235.4
2686.1 | 2465.1 | -6.3 | 0 | 0 | 250.3 | 223.7 | 216.3 | 215.9 | 254.2 | 41.8 | 19.1 | 67.7 | 3.6 | 235.3 | 5.1 | 445.4 | 453.6 | 279.5 | 78.9 | 535.8 | 542.8 | 139.8 | 93.4 | 247.4 | 540 | 284.2 | 316.7 | 469.5 | 303 | 268.2 | 557.1 | 373.4 | 249.7 | 226.4 | 219.8 | 230.5 | 240.3 | 222.6 | 234 | 235.3
2687.1 | 2466.1 | -6 | 0 | 0 | 250.1 | 223.5 | 216.4 | 216 | 254.1 | 41.8 | 19.1 | 67.6 | 3.7 | 241.2 | 5.4 | 445.4 | 453.5 | 279.6 | 78.9 | 535.7 | 542.8 | 139.4 | 93.6 | 247.3 | 539.8 | 285.2 | 317.1 | 469.2 | 302.5 | 270 | 556.8 | 373.2 | 249.5 | 226.2 | 219.7 | 230.4 | 240.2 | 222.6 | 233.9 | 235.2
2688.1 | 2467.1 | -6.4 | 0 | 0 | 250.2 | 223.3 | 216.2 | 215.9 | 253.8 | 41.7 | 19.1 | 67.6 | 3.8 | 252 | 5.6 | 445.4 | 453.6 | 281.6 | 78.9 | 535.6 | 542.7 | 139.2 | 93.6 | 247.2 | 539.6 | 286.2 | 316.5 | 469 | 302.3 | 270.1 | 557.1 | 373.1 | 249.4 | 226 | 219.6 | 230.3 | 240.1 | 222.8 | 233.5 | 235
2689.1 | 2468.1 | -6.4 | 0 | 0 | 250.2 | 223.2 | 216 | 215.7 | 253.4 | 41.7 | 19.1 | 67.6 | 3.3 | 245 | 5.5 | 445.4 | 453.5 | 284.2 | 78.8 | 535.6 | 542.6 | 138.8 | 93.6 | 247.1 | 539.5 | 284.9 | 316 | 468.7 | 302.2 | 269.5 | 557 | 372.7 | 249.2 | 225.9 | 219.5 | 230.2 | 240 | 222.9 | 233.2 | 234.9
2690.1 | 2469.1 | -6.2 | 0 | 0 | 250 | 223.1 | 215.8 | 215.5 | 253.1 | 41.6 | 19.1 | 67.5 | 3.2 | 234 | 5 | 445.4 | 453.3 | 280.4 | 78.6 | 535.5 | 542.5 | 138.2 | 93.5 | 247 | 539.4 | 284.6 | 315.1 | 468.5 | 302.7 | 268.3 | 557.2 | 372.5 | 249.1 | 225.8 | 219.4 | 230 | 239.9 | 222.7 | 233.1 | 234.7
2691.1 | 2470.1 | -6.3 | 0 | 0 | 249.9 | 223 | 215.6 | 215.6 | 252.4 | 41.6 | 19.1 | 67.5 | 3.3 | 239.9 | 4.5 | 445.4 | 453.3 | 277.9 | 78.5 | 535.5 | 542.4 | 137.5 | 93.4 | 246.9 | 539.3 | 284.7 | 314.2 | 468.3 | 303.1 | 268.6 | 557.1 | 372.5 | 248.9 | 225.7 | 219.3 | 229.9 | 239.8 | 222.5 | 233.1 | 234.6
2692.1 | 2471.1 | -6.4 | 0 | 0 | 249.6 | 222.9 | 215.4 | 215.7 | 252.1 | 41.6 | 19.1 | 67.4 | 3.1 | 237.9 | 4.5 | 445.3 | 453.4 | 277.5 | 78.1 | 535.5 | 542.3 | 137.3 | 93.2 | 246.8 | 539.2 | 285 | 313.8 | 468 | 302.4 | 268.8 | 556.6 | 372.3 | 248.8 | 225.6 | 219.2 | 229.8 | 239.7 | 222.5 | 232.8 | 234.5
2693.1 | 2472.1 | -6.7 | 0 | 0 | 249.3 | 222.8 | 215 | 215.6 | 251.9 | 41.6 | 19.1 | 67.4 | 3.3 | 232.1 | 4.2 | 445.3 | 453.5 | 276.6 | 77.9 | 535.5 | 542.2 | 137 | 93 | 246.7 | 539 | 284 | 313.7 | 467.8 | 302.5 | 268.1 | 556.2 | 372.2 | 248.6 | 225.5 | 219 | 229.7 | 239.6 | 222.7 | 232.8 | 234.3
2694.1 | 2473.1 | -6.3 | 0 | 0 | 249.5 | 222.6 | 214.8 | 215.6 | 252.1 | 41.6 | 19.1 | 67.4 | 3.2 | 241.6 | 4 | 445.3 | 453.6 | 274.7 | 77.9 | 535.4 | 542 | 136.3 | 92.9 | 246.6 | 538.7 | 283.7 | 313.8 | 467.6 | 302 | 267.6 | 556.1 | 372.1 | 248.5 | 225.3 | 218.9 | 229.5 | 239.4 | 222.9 | 232.9 | 234.2
2695.1 | 2474.1 | -5.3 | 0 | 0 | 249.4 | 222.4 | 214.7 | 215.5 | 252 | 41.6 | 19.1 | 67.4 | 3 | 247.9 | 4.1 | 445.3 | 453.7 | 274.1 | 77.9 | 535.4 | 541.9 | 135.9 | 92.9 | 246.5 | 538.5 | 283.2 | 313.8 | 467.3 | 301.7 | 268.1 | 556.1 | 371.9 | 248.4 | 225.3 | 219 | 229.4 | 239.3 | 223.1 | 232.7 | 234.1
2696.1 | 2475.1 | -5 | 0 | 0 | 249.1 | 222.3 | 214.7 | 215.4 | 251.4 | 41.5 | 19.1 | 67.4 | 3.1 | 218.7 | 3.7 | 445.3 | 453.6 | 272.7 | 77.9 | 535.4 | 541.7 | 135.5 | 93.1 | 246.4 | 538.3 | 282.3 | 313.6 | 467.1 | 301 | 268.3 | 555.9 | 371.8 | 248.2 | 225.1 | 218.8 | 229.3 | 239.3 | 223 | 232.9 | 234
2697.1 | 2476.1 | -4.5 | 0 | 0 | 248.9 | 222.3 | 214.7 | 215.2 | 251.4 | 41.5 | 19.1 | 67.4 | 3.2 | 202.2 | 3.5 | 445.3 | 453.7 | 271.3 | 77.9 | 535.4 | 541.5 | 135.1 | 93.1 | 246.3 | 538.2 | 282.7 | 312.2 | 466.8 | 301.1 | 268.4 | 555.8 | 371.2 | 248.1 | 224.9 | 218.6 | 229.2 | 239.2 | 223 | 232.9 | 233.9
2698.1 | 2477.1 | -5.8 | 0 | 0 | 248.6 | 222.1 | 214.5 | 214.9 | 251.3 | 41.6 | 19.1 | 67.4 | 3 | 222.5 | 3.2 | 445.2 | 453.6 | 270.7 | 77.8 | 535.4 | 541.3 | 134.7 | 93.1 | 246.2 | 538 | 283.3 | 311.6 | 466.6 | 300.4 | 267.8 | 555.7 | 370.8 | 247.9 | 224.8 | 218.5 | 229 | 239 | 223 | 233 | 233.7
2699.1 | 2478.1 | -5.5 | 0 | 0 | 248.7 | 221.9 | 214.2 | 214.6 | 251.1 | 41.6 | 19.1 | 67.4 | 3.4 | 240.3 | 3 | 445.2 | 453.5 | 269 | 77.7 | 535.4 | 541.1 | 134.2 | 93 | 246.1 | 537.8 | 282.1 | 310.7 | 466.4 | 298.8 | 265.2 | 555.4 | 370.5 | 247.8 | 224.6 | 218.4 | 228.9 | 238.9 | 222.7 | 232.9 | 233.6
2700.1 | 2479.1 | -5.4 | 0 | 0 | 248.6 | 221.7 | 214 | 214.5 | 251.3 | 41.5 | 19.1 | 67.4 | 3.5 | 229.5 | 3 | 445.2 | 453.6 | 266.7 | 77.6 | 535.4 | 540.9 | 133.6 | 92.8 | 246 | 537.7 | 281.5 | 309.9 | 466.1 | 298.3 | 265.1 | 555.3 | 370.1 | 247.6 | 224.5 | 218.2 | 228.8 | 238.7 | 222.5 | 232.7 | 233.4
2701.1 | 2480.1 | -6.1 | 0 | 0 | 248.7 | 221.6 | 213.8 | 214.6 | 251.3 | 41.5 | 19.1 | 67.4 | 3.5 | 207.3 | 3.1 | 445.2 | 453.6 | 264 | 77.5 | 535.4 | 540.8 | 132.8 | 92.6 | 245.8 | 537.5 | 280.1 | 309.7 | 465.8 | 298.1 | 265.2 | 555.3 | 370 | 247.5 | 224.3 | 218.1 | 228.6 | 238.6 | 222.3 | 232.5 | 233.3
2702.1 | 2481.1 | -6.2 | 0 | 0 | 248.4 | 221.4 | 213.5 | 214.6 | 251.3 | 41.5 | 19.1 | 67.4 | 3.4 | 193.9 | 3.5 | 445.2 | 453.5 | 262.4 | 77.3 | 535.4 | 540.6 | 132.3 | 92.4 | 245.7 | 537.2 | 278.1 | 308.2 | 465.6 | 297.9 | 264.5 | 555.2 | 369.8 | 247.3 | 224.2 | 217.9 | 228.5 | 238.4 | 221.8 | 232.3 | 233.2
2703.1 | 2482.1 | -5.9 | 0 | 0 | 248.4 | 221.2 | 213.3 | 214.4 | 251.4 | 41.5 | 19.1 | 67.4 | 3.2 | 196.4 | 3.5 | 445.1 | 453.4 | 261 | 77.2 | 535.4 | 540.6 | 132.5 | 91.8 | 245.5 | 536.9 | 278.2 | 307.6 | 465.3 | 297.5 | 264.7 | 555.2 | 369.5 | 247.2 | 224.2 | 217.8 | 228.4 | 238.3 | 221.4 | 232.3 | 233
2704.1 | 2483.1 | -6.3 | 0 | 0 | 248.4 | 221 | 213.3 | 214.1 | 251.2 | 41.4 | 19.1 | 67.3 | 3.2 | 219.5 | 3.3 | 445.1 | 453.4 | 259.9 | 77 | 535.3 | 540.6 | 133.7 | 91.6 | 245.3 | 536.7 | 278.5 | 307.8 | 465 | 297 | 265.2 | 554.7 | 369.3 | 247 | 224.1 | 217.6 | 228.3 | 238.1 | 220.9 | 232.3 | 232.9
2705.1 | 2484.1 | -5.9 | 0 | 0 | 248.2 | 220.9 | 213.2 | 213.7 | 251.2 | 41.4 | 19.1 | 67.2 | 3.3 | 248.5 | 3.2 | 445.1 | 453.1 | 256.4 | 76.7 | 535.3 | 540.7 | 134.8 | 91.4 | 245.2 | 536.5 | 280.1 | 307.7 | 464.8 | 295.7 | 265.7 | 554.5 | 368.8 | 246.9 | 224 | 217.5 | 228.1 | 238 | 220.5 | 232 | 232.8
2706.1 | 2485.1 | -6.5 | 0 | 0 | 248.2 | 220.8 | 213.1 | 213.6 | 250.5 | 41.5 | 19.1 | 67.2 | 3.5 | 249.8 | 2.9 | 445.1 | 453.1 | 253 | 76.4 | 535.2 | 540.9 | 136.6 | 90.9 | 244.9 | 536.4 | 280 | 308.2 | 464.5 | 295.4 | 266.8 | 554.3 | 368.8 | 246.8 | 224 | 217.4 | 228 | 237.8 | 220.2 | 232 | 232.6
2707.1 | 2486.1 | -6.6 | 0 | 0 | 248 | 220.6 | 212.9 | 213.5 | 249.9 | 41.5 | 19.1 | 67.1 | 3.2 | 229.6 | 2.8 | 445.1 | 453.1 | 251 | 76.4 | 535.2 | 541 | 138.2 | 90.6 | 244.8 | 536.2 | 279.7 | 308.3 | 464.3 | 295.7 | 267.9 | 554.4 | 368.6 | 246.6 | 223.8 | 217.2 | 227.9 | 237.7 | 219.8 | 231.7 | 232.5
2708.1 | 2487.1 | -5.8 | 0 | 0 | 248.2 | 220.5 | 212.9 | 213.2 | 249.2 | 41.5 | 19.1 | 67.1 | 3.2 | 218.6 | 3.3 | 445 | 453.1 | 249.4 | 76.4 | 535.1 | 541.1 | 139.1 | 90.6 | 244.7 | 536 | 280.7 | 308.6 | 464 | 295.6 | 268.1 | 554.4 | 368.3 | 246.5 | 223.7 | 217.1 | 227.7 | 237.5 | 219.5 | 231.4 | 232.3
2709.1 | 2488.1 | -4.2 | 0 | 0 | 248.2 | 220.5 | 212.8 | 213.1 | 249 | 41.5 | 19.1 | 67 | 3.1 | 232.3 | 3.5 | 445 | 453 | 247.4 | 76.6 | 535 | 541.4 | 139.9 | 90.8 | 244.7 | 535.8 | 282.3 | 308.6 | 463.7 | 294.7 | 268.1 | 554.2 | 368 | 246.3 | 223.5 | 217 | 227.6 | 237.3 | 219.1 | 231.2 | 232.2
2710.1 | 2489.1 | -3.2 | 0 | 0 | 248.4 | 220.4 | 212.6 | 213 | 248.9 | 41.5 | 19.1 | 67 | 3.1 | 240.9 | 3.3 | 445 | 453.1 | 246 | 76.6 | 534.9 | 541.6 | 140.4 | 90.8 | 244.6 | 535.7 | 281.4 | 308.8 | 463.4 | 294.6 | 268.3 | 553.9 | 367.8 | 246.2 | 223.3 | 216.9 | 227.5 | 237.1 | 218.9 | 230.9 | 232.1
2711.1 | 2490.1 | -3 | 0 | 0 | 248.1 | 220.3 | 212.4 | 212.8 | 248.8 | 41.5 | 19.1 | 67 | 3.2 | 229.3 | 3.2 | 445 | 453.1 | 244.8 | 76.6 | 534.8 | 541.8 | 139.6 | 90.8 | 244.5 | 535.6 | 280.8 | 309 | 463.1 | 294.5 | 269.1 | 553.7 | 367.8 | 246.1 | 223.2 | 216.9 | 227.3 | 237 | 219 | 230.6 | 231.9
2712.1 | 2491.1 | -4.8 | 0 | 0 | 247.2 | 220 | 212.2 | 212.6 | 248.9 | 41.5 | 19.1 | 66.9 | 3.2 | 213.1 | 3.1 | 445 | 453 | 243.8 | 76.7 | 534.7 | 541.9 | 138.8 | 90.9 | 244.5 | 535.4 | 279.1 | 309.2 | 462.9 | 294 | 269.7 | 553.5 | 367.6 | 245.9 | 223.1 | 216.8 | 227.2 | 236.9 | 219.3 | 230.4 | 231.8
2713.1 | 2492.1 | -6.1 | 0 | 0 | 246.7 | 219.8 | 212.1 | 212.3 | 248.6 | 41.5 | 19.1 | 67 | 3.1 | 217.3 | 2.9 | 444.9 | 452.9 | 241.6 | 76.6 | 534.6 | 542 | 138.6 | 91 | 244.5 | 535.2 | 278.3 | 308.7 | 462.7 | 294 | 269.6 | 553.5 | 367.4 | 245.7 | 223 | 216.6 | 227.1 | 236.7 | 219.1 | 230.1 | 231.6
2714.1 | 2493.1 | -6.6 | 0 | 0 | 246.2 | 219.7 | 212 | 212.1 | 248.6 | 41.5 | 19.1 | 67 | 3.3 | 214.1 | 2.8 | 444.9 | 452.9 | 240.7 | 76.5 | 534.5 | 542.1 | 137.7 | 91 | 244.4 | 534.9 | 277.9 | 308.3 | 462.4 | 293.8 | 269.8 | 553.5 | 367.4 | 245.6 | 222.8 | 216.5 | 226.9 | 236.5 | 218.8 | 230 | 231.5
2715.1 | 2494.1 | -6.7 | 0 | 0 | 245.9 | 219.5 | 211.7 | 211.9 | 248.3 | 41.5 | 19.1 | 67 | 3.3 | 201.1 | 3.1 | 444.9 | 453.1 | 240.5 | 76.3 | 534.5 | 542.2 | 137.1 | 91 | 244.3 | 534.7 | 277.5 | 308.5 | 462.2 | 293.4 | 270 | 553.5 | 367.3 | 245.4 | 222.7 | 216.5 | 226.8 | 236.4 | 218.5 | 229.7 | 231.4
2716.1 | 2495.1 | -6.7 | 0 | 0 | 245.9 | 219.5 | 211.7 | 212 | 248.1 | 41.5 | 19.1 | 67 | 3.2 | 196.9 | 3.4 | 444.9 | 453.2 | 239.9 | 76.1 | 534.5 | 542.1 | 136.5 | 90.9 | 244.2 | 534.4 | 277.4 | 307.9 | 461.9 | 293.5 | 269.3 | 553.3 | 367.3 | 245.3 | 222.6 | 216.4 | 226.7 | 236.2 | 218.1 | 229.5 | 231.2
2717.1 | 2496.1 | -6.7 | 0 | 0 | 245.8 | 219.4 | 211.7 | 211.9 | 248.2 | 41.4 | 19.1 | 67 | 3.2 | 219.8 | 3.7 | 444.9 | 453.4 | 237.2 | 75.9 | 534.4 | 542.1 | 136 | 90.9 | 244.1 | 534.1 | 279.2 | 307.2 | 461.7 | 294.4 | 268.2 | 553.4 | 367.2 | 245.1 | 222.4 | 216.3 | 226.6 | 236.1 | 217.8 | 229.3 | 231.1
2718.1 | 2497.1 | -6.7 | 0 | 0 | 245.5 | 219.3 | 211.7 | 211.8 | 248.3 | 41.4 | 19.1 | 67 | 3.2 | 233.4 | 3.9 | 444.8 | 453.2 | 236.3 | 75.9 | 534.4 | 542.1 | 135.7 | 90.9 | 244 | 533.8 | 278 | 306.1 | 461.5 | 295.3 | 268 | 553.5 | 366.6 | 245 | 222.3 | 216.2 | 226.4 | 235.9 | 217.6 | 229.2 | 231
2719.1 | 2498.1 | -6.2 | 0 | 0 | 245.1 | 219.2 | 211.6 | 211.8 | 248.1 | 41.4 | 19.1 | 66.9 | 3.3 | 231.6 | 3.7 | 444.8 | 452.9 | 236.7 | 76 | 534.3 | 542.2 | 135 | 90.9 | 244 | 533.6 | 277.4 | 305.5 | 461.3 | 293.9 | 267.7 | 553.5 | 366.4 | 244.8 | 222.2 | 216 | 226.3 | 235.8 | 217.5 | 229.1 | 230.8
2720.1 | 2499.1 | -5.9 | 0 | 0 | 244.9 | 219.1 | 211.4 | 211.6 | 247.7 | 41.3 | 19.1 | 66.9 | 3.2 | 222.2 | 3.8 | 444.8 | 452.9 | 235.3 | 75.9 | 534.3 | 542.2 | 134.4 | 90.8 | 243.8 | 533.3 | 275.4 | 304.7 | 461 | 293.6 | 267.1 | 553.2 | 366.3 | 244.7 | 222.1 | 215.8 | 226.2 | 235.6 | 217.4 | 228.9 | 230.7
2721.1 | 2500.1 | -6.1 | 0 | 0 | 244.8 | 219 | 211.1 | 211.4 | 247.6 | 41.3 | 19.2 | 66.9 | 3.1 | 213.9 | 4.1 | 444.8 | 452.9 | 234.5 | 75.9 | 534.3 | 542.2 | 134 | 90.7 | 243.7 | 533.1 | 274.7 | 304.2 | 460.8 | 292.9 | 266.8 | 553.2 | 366.2 | 244.6 | 222 | 215.7 | 226 | 235.5 | 217.2 | 228.9 | 230.6
2722.1 | 2501.1 | -6.5 | 0 | 0 | 244.8 | 218.9 | 210.8 | 211.1 | 247.7 | 41.3 | 19.2 | 66.9 | 3.5 | 207.8 | 4.2 | 444.8 | 452.9 | 233.7 | 75.7 | 534.3 | 542.3 | 133.4 | 90.4 | 243.7 | 532.8 | 274.5 | 304.1 | 460.6 | 292.6 | 267 | 553.1 | 365.9 | 244.4 | 221.9 | 215.6 | 225.9 | 235.3 | 217 | 228.6 | 230.4
2723.1 | 2502.1 | -6.7 | 0 | 0 | 244.6 | 218.8 | 210.6 | 210.9 | 247.9 | 41.3 | 19.2 | 66.8 | 3.3 | 206.1 | 4.3 | 444.7 | 452.9 | 234.1 | 75.5 | 534.2 | 542.3 | 132.6 | 90.2 | 243.5 | 532.6 | 273.9 | 303.9 | 460.3 | 292.9 | 266.5 | 553 | 365.8 | 244.3 | 221.7 | 215.5 | 225.8 | 235.2 | 216.8 | 228.5 | 230.3
2724.1 | 2503.1 | -6.7 | 0 | 0 | 244.5 | 218.7 | 210.5 | 210.7 | 247.8 | 41.4 | 19.2 | 66.8 | 3.4 | 201.7 | 4.3 | 444.7 | 452.8 | 233.5 | 75.2 | 534.2 | 542.2 | 132.1 | 90.1 | 243.3 | 532.3 | 273.8 | 303.9 | 460.1 | 292.4 | 265.4 | 552.8 | 365.8 | 244.1 | 221.6 | 215.3 | 225.6 | 235 | 216.6 | 228.3 | 230.2
2725.1 | 2504.1 | -6.6 | 0 | 0 | 244.5 | 218.5 | 210.6 | 210.6 | 247.3 | 41.3 | 19.2 | 66.8 | 3.1 | 190.1 | 4.3 | 444.7 | 452.9 | 233.1 | 75 | 534.2 | 542.2 | 131.4 | 90 | 243.2 | 532.1 | 272.8 | 303.7 | 459.9 | 292.4 | 265.4 | 552.6 | 365.4 | 244 | 221.5 | 215.2 | 225.5 | 234.9 | 216.7 | 228.1 | 230
2726.1 | 2505.1 | -6.7 | 0 | 0 | 244.1 | 218.3 | 210.5 | 210.6 | 246.8 | 41.3 | 19.2 | 66.8 | 3 | 183.9 | 4.4 | 444.7 | 452.9 | 232.9 | 74.9 | 534.3 | 542.2 | 131 | 90.1 | 243.1 | 531.8 | 272.2 | 303.2 | 459.6 | 292.4 | 265.7 | 552.6 | 365 | 243.8 | 221.4 | 215.1 | 225.4 | 234.7 | 216.6 | 227.9 | 229.9
2727.1 | 2506.1 | -6.7 | 0 | 0 | 243.6 | 218.2 | 210.4 | 210.6 | 246.4 | 41.4 | 19.2 | 66.8 | 3.4 | 192.2 | 4.4 | 444.7 | 453 | 232.4 | 74.9 | 534.3 | 542.1 | 130.4 | 90.2 | 243 | 531.6 | 273.3 | 303.4 | 459.4 | 292.1 | 265.5 | 552.7 | 364.9 | 243.6 | 221.3 | 214.9 | 225.2 | 234.6 | 216.4 | 227.6 | 229.8
2728.1 | 2507.1 | -6.7 | 0 | 0 | 243.3 | 218.1 | 210.2 | 210.6 | 245.9 | 41.4 | 19.2 | 66.8 | 3.6 | 195.1 | 4.4 | 444.7 | 453.1 | 232 | 74.8 | 534.3 | 542 | 129.8 | 90.3 | 242.9 | 531.4 | 274.6 | 302.6 | 459.1 | 292.2 | 265.6 | 552.9 | 364.5 | 243.5 | 221.1 | 214.9 | 225.1 | 234.5 | 216.1 | 227.4 | 229.6
2729.1 | 2508.1 | -6.7 | 0 | 0 | 243.1 | 218 | 210 | 210.4 | 245.9 | 41.4 | 19.2 | 66.7 | 3.4 | 194.6 | 4.7 | 444.6 | 453.1 | 230.6 | 74.7 | 534.3 | 541.8 | 129.3 | 90.3 | 242.8 | 531.1 | 273 | 301.8 | 458.9 | 291.8 | 265.3 | 552.8 | 364.3 | 243.4 | 220.9 | 214.7 | 225 | 234.3 | 215.8 | 227.3 | 229.5
2730.1 | 2509.1 | -6.7 | 0 | 0 | 243 | 218 | 209.6 | 210.4 | 245.9 | 41.4 | 19.2 | 66.7 | 3.6 | 196.9 | 5.1 | 444.6 | 453.1 | 230.3 | 74.7 | 534.4 | 541.6 | 128.8 | 90.2 | 242.8 | 530.8 | 272.1 | 301.3 | 458.6 | 292.1 | 264.7 | 552.8 | 364.3 | 243.2 | 220.7 | 214.6 | 224.9 | 234.2 | 215.5 | 227.4 | 229.4
2731.1 | 2510.1 | -6.7 | 0 | 0 | 242.7 | 218.1 | 209.4 | 210.3 | 246.1 | 41.4 | 19.2 | 66.7 | 3.4 | 205.7 | 5 | 444.6 | 453.1 | 229.3 | 74.7 | 534.4 | 541.5 | 128.5 | 90.1 | 242.8 | 530.6 | 270.6 | 301 | 458.4 | 293.4 | 264.5 | 552.9 | 364.1 | 243.1 | 220.6 | 214.5 | 224.7 | 234.1 | 215.5 | 227.4 | 229.3
2732.1 | 2511.1 | -6.7 | 0 | 0 | 242.4 | 218 | 209.4 | 210.2 | 246 | 41.3 | 19.2 | 66.6 | 3.6 | 210.8 | 4 | 444.6 | 453 | 229.7 | 74.5 | 534.4 | 541.3 | 128 | 90.2 | 242.7 | 530.4 | 270.5 | 300 | 458.1 | 294.2 | 264.5 | 552.9 | 364 | 242.9 | 220.5 | 214.3 | 224.6 | 233.9 | 215.3 | 227.3 | 229.1
2733.1 | 2512.1 | -6.4 | 0 | 0 | 242 | 217.9 | 209.4 | 210.3 | 246 | 41.3 | 19.2 | 66.6 | 3.5 | 220.8 | 3.4 | 444.6 | 453.1 | 229.8 | 74.4 | 534.5 | 541.1 | 128 | 90.1 | 242.6 | 530.2 | 270.3 | 299.4 | 457.9 | 294.4 | 264.4 | 552.9 | 364 | 242.8 | 220.4 | 214.2 | 224.5 | 233.8 | 215.4 | 227.2 | 229
2734.1 | 2513.1 | -6.5 | 0 | 0 | 242 | 217.8 | 209.3 | 210.2 | 245.6 | 41.3 | 19.2 | 66.5 | 3.4 | 220.5 | 2.9 | 444.5 | 453.1 | 227.7 | 74.3 | 534.5 | 540.9 | 128.2 | 89.9 | 242.5 | 529.9 | 270.4 | 298.9 | 457.7 | 293.3 | 264 | 552.9 | 363.7 | 242.6 | 220.2 | 214.1 | 224.4 | 233.6 | 215.7 | 227 | 228.9
2735.1 | 2514.1 | -6.6 | 0 | 0 | 241.9 | 217.7 | 209.4 | 210 | 245.3 | 41.3 | 19.2 | 66.4 | 3.5 | 197.5 | 2.9 | 444.5 | 453 | 225.9 | 74.2 | 534.4 | 540.8 | 128.2 | 89.7 | 242.4 | 529.6 | 268.9 | 298.9 | 457.5 | 291.4 | 264.3 | 552.5 | 363.6 | 242.5 | 220 | 214 | 224.2 | 233.5 | 215.7 | 226.8 | 228.7
2736.1 | 2515.1 | -6.7 | 0 | 0 | 241.8 | 217.6 | 209.5 | 210 | 245 | 41.3 | 19.2 | 66.3 | 3.4 | 177.8 | 2.7 | 444.5 | 452.8 | 224.7 | 74.1 | 534.4 | 540.7 | 127.9 | 89.5 | 242.3 | 529.2 | 268.8 | 298.8 | 457.2 | 291.1 | 265 | 551.9 | 363.6 | 242.4 | 219.9 | 213.9 | 224.1 | 233.3 | 215.4 | 226.6 | 228.6
2737.1 | 2516.1 | -6.2 | 0 | 0 | 241.7 | 217.5 | 209.4 | 209.9 | 244.6 | 41.3 | 19.2 | 66.3 | 3.1 | 183.9 | 2.1 | 444.5 | 453.1 | 223.3 | 74 | 534.4 | 540.5 | 128.2 | 89.5 | 242.2 | 528.9 | 268.9 | 298.7 | 457 | 289.9 | 264.5 | 551.5 | 363.6 | 242.2 | 219.7 | 213.7 | 224 | 233.2 | 215.3 | 226.5 | 228.5
2738.1 | 2517.1 | -6.5 | 0 | 0 | 241.5 | 217.5 | 209.2 | 209.9 | 244.2 | 41.3 | 19.2 | 66.2 | 3.2 | 206.1 | 1.5 | 444.5 | 453.2 | 222 | 74.1 | 534.3 | 540.4 | 128.3 | 89.5 | 242.1 | 528.6 | 270.4 | 299 | 456.8 | 289.3 | 264.4 | 551.2 | 363.4 | 242.1 | 219.6 | 213.6 | 223.9 | 233 | 215.6 | 226.4 | 228.4
2739.1 | 2518.1 | -6.5 | 0 | 0 | 241.4 | 217.5 | 209 | 209.8 | 243.7 | 41.2 | 19.2 | 66.2 | 3 | 241.2 | 1.5 | 444.5 | 453.1 | 221.7 | 74.1 | 534.3 | 540.2 | 128.2 | 89.5 | 242 | 528.2 | 271.2 | 299 | 456.5 | 288.3 | 263.5 | 551 | 363.3 | 241.9 | 219.5 | 213.5 | 223.8 | 232.9 | 215.5 | 226.1 | 228.2
2740.1 | 2519.1 | -6.6 | 0 | 0 | 241.8 | 217.5 | 209.1 | 209.6 | 243.3 | 41.2 | 19.2 | 66.2 | 3.1 | 271.2 | 1.6 | 444.4 | 453.3 | 221.4 | 74.1 | 534.2 | 540.1 | 128 | 89.5 | 242 | 527.9 | 270.6 | 298.7 | 456.3 | 287 | 262 | 550.6 | 363 | 241.8 | 219.3 | 213.5 | 223.6 | 232.8 | 215.2 | 225.9 | 228.1
2741.1 | 2520.1 | -6.7 | 0 | 0 | 241.8 | 217.4 | 209.1 | 209.3 | 243.1 | 41.1 | 19.2 | 66.2 | 3 | 277.9 | 1.8 | 444.4 | 453.3 | 220.1 | 74.1 | 534.2 | 539.9 | 127.8 | 89.4 | 242 | 527.5 | 270.4 | 298.4 | 456 | 286.2 | 261 | 550.3 | 362.9 | 241.7 | 219.1 | 213.4 | 223.5 | 232.6 | 214.9 | 225.8 | 227.9
2742.1 | 2521.1 | -6.6 | 0 | 0 | 241.5 | 217.3 | 209.1 | 209.3 | 243 | 41.1 | 19.2 | 66.1 | 3 | 262.7 | 2.3 | 444.4 | 453.1 | 218.2 | 74.1 | 534.1 | 539.9 | 127.9 | 89.4 | 242 | 527.1 | 270.5 | 298.3 | 455.8 | 285.7 | 260 | 550.2 | 362.8 | 241.5 | 219 | 213.3 | 223.4 | 232.4 | 214.9 | 225.5 | 227.8
2743.1 | 2522.1 | -6.2 | 0 | 0 | 241.3 | 217.2 | 208.9 | 209.2 | 242.7 | 41 | 19.2 | 66.1 | 3.1 | 249.8 | 3 | 444.4 | 453 | 217.4 | 74.1 | 534.1 | 539.9 | 128.1 | 89.3 | 242 | 526.8 | 270.9 | 298.3 | 455.5 | 284.7 | 259.5 | 550.2 | 362.5 | 241.4 | 218.9 | 213.2 | 223.3 | 232.3 | 214.9 | 225.3 | 227.7
2744.1 | 2523.1 | -5.1 | 0 | 0 | 241 | 217.2 | 208.5 | 209 | 242.7 | 41 | 19.2 | 66.1 | 3 | 249.2 | 3.4 | 444.3 | 452.9 | 217.6 | 74 | 534 | 539.9 | 127.7 | 89.3 | 241.9 | 526.5 | 271.2 | 298.5 | 455.2 | 283.9 | 259.3 | 550.3 | 362.3 | 241.2 | 218.8 | 213.1 | 223.2 | 232.2 | 214.6 | 225.1 | 227.5
2745.1 | 2524.1 | -4.6 | 0 | 0 | 240.6 | 217.1 | 208.3 | 208.8 | 242.8 | 41 | 19.2 | 66 | 3.1 | 251.1 | 3.5 | 444.3 | 452.7 | 218.1 | 74 | 534 | 539.9 | 127.2 | 89.3 | 241.9 | 526.1 | 271.1 | 298.4 | 454.9 | 283.5 | 258.9 | 550.4 | 362.3 | 241.1 | 218.8 | 212.9 | 223 | 232 | 214.4 | 224.9 | 227.4
2746.1 | 2525.1 | -3.8 | 0 | 0 | 240.8 | 217 | 208.1 | 208.7 | 242.6 | 41 | 19.2 | 66 | 3.3 | 256.6 | 3.3 | 444.3 | 452.7 | 217.6 | 74 | 534 | 539.9 | 126.8 | 89.2 | 241.8 | 525.8 | 271 | 297.9 | 454.6 | 284.1 | 258.4 | 550.6 | 362.1 | 241 | 218.6 | 212.8 | 222.9 | 231.9 | 214.1 | 224.7 | 227.3
2747.1 | 2526.1 | -3.6 | 0 | 0 | 240.9 | 216.9 | 208 | 208.5 | 242.6 | 41 | 19.2 | 66 | 3.3 | 258.3 | 3.2 | 444.3 | 452.5 | 216.8 | 73.8 | 534 | 539.8 | 126.5 | 88.9 | 241.8 | 525.6 | 271.4 | 297.8 | 454.4 | 284.6 | 258.4 | 550.8 | 361.9 | 240.8 | 218.5 | 212.7 | 222.8 | 231.7 | 213.8 | 224.6 | 227.1
2748.1 | 2527.1 | -3.1 | 0 | 0 | 240.4 | 216.8 | 207.7 | 208.5 | 242.3 | 41 | 19.2 | 66 | 3.4 | 256.8 | 3 | 444.3 | 452.3 | 217.3 | 73.8 | 533.9 | 539.7 | 126.3 | 88.8 | 241.7 | 525.4 | 270.1 | 297.9 | 454.1 | 284.8 | 258.2 | 551 | 361.7 | 240.7 | 218.4 | 212.6 | 222.6 | 231.6 | 213.6 | 224.5 | 227
2749.1 | 2528.1 | -4.4 | 0 | 0 | 240.2 | 216.7 | 207.6 | 208.4 | 242 | 41 | 19.2 | 65.9 | 3.1 | 263 | 2.9 | 444.3 | 452.2 | 217.2 | 73.7 | 533.9 | 539.6 | 125.9 | 88.5 | 241.5 | 525.2 | 270 | 297.9 | 453.8 | 285.9 | 258.7 | 551.2 | 361.6 | 240.5 | 218.3 | 212.5 | 222.5 | 231.4 | 213.5 | 224.3 | 226.9
2750.1 | 2529.1 | -5.3 | 0 | 0 | 240 | 216.6 | 207.5 | 208.2 | 242 | 41 | 19.2 | 65.9 | 2.8 | 280.2 | 3 | 444.2 | 452.5 | 217.5 | 73.5 | 533.9 | 539.6 | 125.7 | 88.3 | 241.4 | 524.9 | 270.5 | 297.1 | 453.5 | 285 | 259.1 | 551.2 | 361.4 | 240.4 | 218.3 | 212.5 | 222.4 | 231.3 | 213.3 | 224.1 | 226.7
2751.1 | 2530.1 | -6 | 0 | 0 | 240 | 216.5 | 207.2 | 208 | 242.2 | 41.1 | 19.2 | 65.8 | 2.9 | 288.5 | 3 | 444.2 | 452.3 | 218.6 | 73.4 | 533.9 | 539.6 | 125.6 | 88.2 | 241.2 | 524.7 | 269.4 | 297 | 453.2 | 285.4 | 258.8 | 551.1 | 361.3 | 240.3 | 218.2 | 212.4 | 222.3 | 231.2 | 213.1 | 224 | 226.6
2752.1 | 2531.1 | -6.5 | 0 | 0 | 239.9 | 216.4 | 207 | 207.9 | 242.3 | 41.1 | 19.2 | 65.8 | 3 | 282 | 2.8 | 444.2 | 452.2 | 218.4 | 73.3 | 533.9 | 539.7 | 126.1 | 88.3 | 241.1 | 524.5 | 269.5 | 296.9 | 453 | 285.7 | 259 | 551.1 | 361.2 | 240.1 | 218.2 | 212.3 | 222.2 | 231 | 212.9 | 223.9 | 226.5
2753.1 | 2532.1 | -6.7 | 0 | 0 | 239.7 | 216.3 | 206.9 | 207.8 | 242.4 | 41.1 | 19.3 | 65.7 | 3 | 269.9 | 2.7 | 444.2 | 452.2 | 216.6 | 73.3 | 533.8 | 539.9 | 126.6 | 88.5 | 240.9 | 524.2 | 269.5 | 296.9 | 452.7 | 285.5 | 258.5 | 551 | 361.1 | 240 | 218.1 | 212.2 | 222 | 230.9 | 212.7 | 224 | 226.4
2754.1 | 2533.1 | -6.3 | 0 | 0 | 239.7 | 216.2 | 206.6 | 207.8 | 242.3 | 41.1 | 19.3 | 65.6 | 3.4 | 261.9 | 2.9 | 444.2 | 452.3 | 215.7 | 73.5 | 533.8 | 540.1 | 126.7 | 88.7 | 240.9 | 524 | 270.6 | 297 | 452.4 | 285.3 | 259 | 551 | 361 | 239.9 | 217.9 | 212.1 | 221.9 | 230.8 | 212.5 | 224 | 226.2
2755.1 | 2534.1 | -6.1 | 0 | 0 | 239.8 | 216.1 | 206.3 | 207.7 | 241.9 | 41 | 19.3 | 65.6 | 3.3 | 264.4 | 2.9 | 444.2 | 452.4 | 214.8 | 73.5 | 533.7 | 540.3 | 127.3 | 88.7 | 240.8 | 523.8 | 270.7 | 297.5 | 452.2 | 284.9 | 259.4 | 550.8 | 360.7 | 239.7 | 217.8 | 212 | 221.8 | 230.6 | 212.4 | 223.8 | 226.1
2756.1 | 2535.1 | -6.4 | 0 | 0 | 239.9 | 216 | 206.1 | 207.5 | 241.6 | 40.9 | 19.3 | 65.6 | 3.3 | 265 | 3 | 444.1 | 452.4 | 213.9 | 73.4 | 533.6 | 540.5 | 128.6 | 88.6 | 240.9 | 523.5 | 272 | 297.5 | 451.9 | 284.7 | 259.4 | 550.5 | 360.6 | 239.6 | 217.6 | 211.8 | 221.6 | 230.5 | 212.2 | 223.5 | 226
2757.1 | 2536.1 | -6.7 | 0 | 0 | 239.5 | 216 | 206.1 | 207.4 | 241.5 | 40.9 | 19.3 | 65.6 | 3.1 | 259.7 | 2.9 | 444.1 | 452.4 | 212.7 | 73.4 | 533.5 | 540.7 | 129.5 | 88.6 | 240.9 | 523.2 | 273.2 | 297 | 451.7 | 285.5 | 258.7 | 550.5 | 360.4 | 239.5 | 217.5 | 211.7 | 221.5 | 230.3 | 212 | 223.3 | 225.8
2758.1 | 2537.1 | -6.7 | 0 | 0 | 239.3 | 215.9 | 206.2 | 207.3 | 241.4 | 40.9 | 19.3 | 65.6 | 3.1 | 238.4 | 2.7 | 444.1 | 452.3 | 211.1 | 73.5 | 533.4 | 540.8 | 129.3 | 88.5 | 240.8 | 523 | 274.1 | 297.2 | 451.4 | 285.6 | 259.2 | 550.3 | 360.2 | 239.3 | 217.4 | 211.5 | 221.4 | 230.2 | 211.8 | 223.1 | 225.7
2759.1 | 2538.1 | -6.7 | 0 | 0 | 239.2 | 215.9 | 206.1 | 207.2 | 240.9 | 40.9 | 19.3 | 65.6 | 3.5 | 237.8 | 2.7 | 444.1 | 452.3 | 210 | 73.7 | 533.3 | 540.9 | 130.5 | 88.5 | 240.7 | 522.8 | 274 | 297.4 | 451.1 | 285.3 | 259.4 | 550.4 | 360.1 | 239.2 | 217.2 | 211.4 | 221.3 | 230.1 | 211.6 | 222.8 | 225.6
2760.1 | 2539.1 | -6.6 | 0 | 0 | 239.3 | 215.8 | 205.9 | 207.1 | 240.6 | 40.9 | 19.3 | 65.6 | 3.6 | 263 | 3.7 | 444 | 452.4 | 208.6 | 73.7 | 533.2 | 541 | 131 | 88.8 | 240.7 | 522.6 | 273.9 | 297.7 | 450.8 | 285.9 | 258.8 | 550.5 | 359.8 | 239.1 | 217.1 | 211.2 | 221.1 | 229.9 | 211.4 | 222.5 | 225.4
2761.1 | 2540.1 | -6.6 | 0 | 0 | 238.9 | 215.7 | 205.8 | 206.9 | 240.5 | 41 | 19.3 | 65.6 | 3.7 | 254.4 | 4.3 | 444 | 452.5 | 209 | 73.7 | 533.1 | 541.1 | 130.5 | 88.9 | 240.6 | 522.4 | 272.9 | 297.8 | 450.5 | 285.6 | 258.7 | 550.6 | 359.5 | 238.9 | 217 | 211.1 | 221 | 229.8 | 211.2 | 222.3 | 225.3
2762.1 | 2541.1 | -6.7 | 0 | 0 | 238.4 | 215.6 | 205.5 | 206.8 | 240.5 | 41 | 19.3 | 65.6 | 3.5 | 236.6 | 4.6 | 444 | 452.4 | 211.4 | 73.6 | 533.1 | 541 | 130.1 | 88.8 | 240.4 | 522.3 | 271.9 | 297.1 | 450.3 | 285.8 | 257.5 | 550.8 | 359.1 | 238.8 | 216.9 | 211.1 | 220.9 | 229.7 | 211 | 222.1 | 225.2
2763.1 | 2542.1 | -6.7 | 0 | 0 | 238.2 | 215.5 | 205.4 | 206.7 | 240.8 | 41.1 | 19.3 | 65.6 | 3.2 | 242 | 4.8 | 444 | 452.2 | 211.4 | 73.4 | 533 | 541 | 129.8 | 88.8 | 240.3 | 522.1 | 271.9 | 295.5 | 450 | 285.8 | 256.9 | 550.7 | 358.4 | 238.7 | 216.9 | 211 | 220.8 | 229.5 | 210.8 | 222 | 225.1
2764.1 | 2543.1 | -6.7 | 0 | 0 | 238.1 | 215.3 | 205.2 | 206.6 | 240.9 | 41.2 | 19.3 | 65.5 | 3.4 | 241.1 | 4.9 | 444 | 452 | 212.4 | 73.4 | 533 | 540.9 | 129.7 | 88.7 | 240.3 | 522 | 271.3 | 294.5 | 449.7 | 285.3 | 257.1 | 550.7 | 358.1 | 238.5 | 216.8 | 210.8 | 220.7 | 229.4 | 210.7 | 222.1 | 224.9
2765.1 | 2544.1 | -6.7 | 0 | 0 | 237.8 | 215.2 | 205.1 | 206.5 | 240.8 | 41.2 | 19.3 | 65.5 | 3.7 | 241.7 | 4.9 | 443.9 | 452 | 212.2 | 73.4 | 533 | 540.9 | 129.6 | 88.7 | 240.1 | 521.8 | 270.1 | 293.8 | 449.5 | 285.4 | 256.5 | 550.5 | 357.9 | 238.4 | 216.7 | 210.7 | 220.5 | 229.2 | 210.5 | 222.1 | 224.8
2766.1 | 2545.1 | -6.7 | 0 | 0 | 237.5 | 215.1 | 204.9 | 206.6 | 240.5 | 41.2 | 19.3 | 65.5 | 3.6 | 243.2 | 4.7 | 443.9 | 451.9 | 212 | 73.5 | 533 | 540.9 | 129.5 | 88.7 | 240 | 521.7 | 270.3 | 292.7 | 449.3 | 284.8 | 256.2 | 550.5 | 357.7 | 238.2 | 216.6 | 210.6 | 220.4 | 229.1 | 210.4 | 222.1 | 224.7
2767.1 | 2546.1 | -6.7 | 0 | 0 | 237.4 | 215.1 | 204.6 | 206.6 | 240.3 | 41.2 | 19.3 | 65.5 | 3.6 | 252 | 3.9 | 443.9 | 452 | 212.8 | 73.5 | 533 | 540.9 | 129.2 | 88.8 | 239.9 | 521.5 | 270.2 | 292.7 | 449 | 284.6 | 256.8 | 550.5 | 357.5 | 238.1 | 216.5 | 210.4 | 220.3 | 228.9 | 210.4 | 222.1 | 224.6
2768.1 | 2547.1 | -6.7 | 0 | 0 | 237.2 | 215 | 204.5 | 206.4 | 240.2 | 41.1 | 19.3 | 65.5 | 3.4 | 267.9 | 3.7 | 443.9 | 452.1 | 212.4 | 73.5 | 533 | 540.9 | 129 | 88.9 | 239.8 | 521.3 | 270.7 | 292.4 | 448.8 | 284.6 | 257.3 | 550.5 | 357.3 | 238 | 216.4 | 210.3 | 220.1 | 228.8 | 210.2 | 222 | 224.4
2769.1 | 2548.1 | -6.6 | 0 | 0 | 236.9 | 215 | 204.3 | 206.3 | 240 | 41.1 | 19.3 | 65.5 | 3.2 | 261.4 | 3.7 | 443.9 | 452 | 212.6 | 73.5 | 533 | 540.8 | 128.7 | 88.9 | 239.8 | 521.1 | 270.3 | 292.2 | 448.5 | 284.6 | 257.7 | 550.6 | 357.1 | 237.8 | 216.3 | 210.2 | 220 | 228.6 | 210.2 | 221.8 | 224.3
2770.1 | 2549.1 | -6.6 | 0 | 0 | 236.8 | 215 | 204.2 | 206.3 | 240 | 41 | 19.3 | 65.4 | 3.2 | 231.9 | 3.5 | 443.9 | 451.9 | 213 | 73.5 | 533 | 540.7 | 128.2 | 88.9 | 239.7 | 520.8 | 269.6 | 292.4 | 448.3 | 285.4 | 258 | 550.7 | 356.9 | 237.7 | 216.1 | 210.1 | 219.9 | 228.5 | 210 | 221.7 | 224.2
2771.1 | 2550.1 | -6.6 | 0 | 0 | 236.5 | 215 | 204.3 | 206.3 | 239.9 | 41 | 19.3 | 65.4 | 3.4 | 232.8 | 3.2 | 443.8 | 451.8 | 212.8 | 73.4 | 533 | 540.6 | 127.6 | 88.8 | 239.6 | 520.6 | 268.7 | 292.3 | 448.1 | 284.2 | 257.1 | 550.6 | 356.6 | 237.6 | 216 | 209.9 | 219.8 | 228.4 | 209.9 | 221.5 | 224.1
2772.1 | 2551.1 | -6.6 | 0 | 0 | 236.3 | 214.9 | 204.4 | 206.3 | 239.4 | 41 | 19.3 | 65.4 | 3.3 | 246.4 | 3.2 | 443.8 | 451.8 | 213.1 | 73.3 | 533 | 540.4 | 126.9 | 88.7 | 239.6 | 520.4 | 268.8 | 291.9 | 447.9 | 283.1 | 257.2 | 550.3 | 356.5 | 237.4 | 215.9 | 209.9 | 219.7 | 228.3 | 209.7 | 221.2 | 224
2773.1 | 2552.1 | -6.6 | 0 | 0 | 236 | 214.8 | 204.3 | 206.1 | 239.2 | 41 | 19.3 | 65.4 | 3.1 | 245.6 | 3.3 | 443.8 | 451.8 | 213.8 | 73.3 | 533.1 | 540.2 | 126.4 | 88.8 | 239.5 | 520.1 | 268.1 | 291.2 | 447.7 | 282.7 | 256.1 | 550.3 | 356.4 | 237.3 | 215.9 | 209.8 | 219.6 | 228.2 | 209.8 | 221.1 | 223.8
2774.1 | 2553.1 | -6.7 | 0 | 0 | 235.7 | 214.7 | 204 | 205.9 | 239.3 | 40.9 | 19.3 | 65.3 | 2.8 | 240.7 | 3.3 | 443.8 | 451.8 | 213.1 | 73.2 | 533.1 | 540 | 126.1 | 88.6 | 239.4 | 519.9 | 268.3 | 290.8 | 447.4 | 282.1 | 256.3 | 550.2 | 356.4 | 237.2 | 215.8 | 209.7 | 219.5 | 228 | 209.8 | 221.1 | 223.7
2775.1 | 2554.1 | -6.7 | 0 | 0 | 235.4 | 214.6 | 203.7 | 205.8 | 239.3 | 40.9 | 19.3 | 65.3 | 3.1 | 252.1 | 3 | 443.8 | 451.9 | 213.3 | 73.1 | 533.1 | 539.9 | 125.6 | 88.4 | 239.4 | 519.7 | 268 | 290.4 | 447.2 | 283 | 256.3 | 550.3 | 356.3 | 237.1 | 215.7 | 209.6 | 219.3 | 227.9 | 209.6 | 221 | 223.6
2776.1 | 2555.1 | -6.7 | 0 | 0 | 235.1 | 214.6 | 203.7 | 205.7 | 239.6 | 40.8 | 19.3 | 65.2 | 3.2 | 269.7 | 2.9 | 443.7 | 452.1 | 214 | 73 | 533.1 | 539.8 | 125.2 | 88.3 | 239.1 | 519.5 | 267.4 | 290.5 | 447 | 282.1 | 256.9 | 550.2 | 356.3 | 236.9 | 215.6 | 209.5 | 219.2 | 227.8 | 209.5 | 220.8 | 223.4
2777.1 | 2556.1 | -6.6 | 0 | 0 | 235.2 | 214.5 | 203.5 | 205.6 | 239.8 | 40.8 | 19.3 | 65.2 | 3.9 | 276 | 3.4 | 443.7 | 452.1 | 213.7 | 72.8 | 533.2 | 539.6 | 124.8 | 88.2 | 239 | 519.2 | 266.4 | 290 | 446.7 | 282 | 257.4 | 550.1 | 356 | 236.8 | 215.5 | 209.4 | 219.1 | 227.7 | 209.4 | 220.8 | 223.3
2778.1 | 2557.1 | -6.6 | 0 | 0 | 235.2 | 214.4 | 203.4 | 205.5 | 240.1 | 40.8 | 19.3 | 65.2 | 3.9 | 259.9 | 4 | 443.7 | 452.2 | 214.5 | 72.7 | 533.2 | 539.4 | 124.2 | 87.9 | 238.8 | 519.1 | 266 | 289.1 | 446.5 | 282.3 | 257 | 550.1 | 355.5 | 236.6 | 215.4 | 209.3 | 219 | 227.5 | 209.2 | 220.8 | 223.2
2779.1 | 2558.1 | -6.6 | 0 | 0 | 235 | 214.4 | 203.2 | 205.5 | 240.1 | 40.8 | 19.3 | 65.2 | 3.6 | 245 | 4.4 | 443.7 | 452.3 | 214.5 | 72.6 | 533.2 | 539.2 | 123.7 | 87.6 | 238.7 | 519 | 266.5 | 287.8 | 446.3 | 282.3 | 256.4 | 550 | 355.3 | 236.5 | 215.3 | 209.2 | 218.8 | 227.4 | 209.1 | 220.7 | 223.1
2780.1 | 2559.1 | -6.4 | 0 | 0 | 234.5 | 214.3 | 203 | 205.5 | 239.5 | 40.8 | 19.3 | 65.1 | 3.6 | 239.9 | 4.7 | 443.7 | 452.4 | 215.6 | 72.4 | 533.2 | 539 | 123.3 | 87.4 | 238.6 | 518.8 | 265.8 | 287.2 | 446.1 | 282.2 | 254.7 | 549.9 | 355 | 236.4 | 215.3 | 209.1 | 218.7 | 227.3 | 208.9 | 220.8 | 222.9
2781.1 | 2560.1 | -6.4 | 0 | 0 | 234.2 | 214.2 | 202.9 | 205.4 | 238.9 | 40.8 | 19.3 | 65.1 | 3.3 | 242.4 | 4.9 | 443.7 | 452.4 | 216.6 | 72.2 | 533.2 | 538.8 | 123 | 87.2 | 238.4 | 518.5 | 265.6 | 287.6 | 445.9 | 281.8 | 253.6 | 549.7 | 354.6 | 236.2 | 215.2 | 209 | 218.6 | 227.2 | 208.7 | 220.8 | 222.8
2782.1 | 2561.1 | -6.5 | 0 | 0 | 233.9 | 214 | 202.8 | 205.4 | 238.7 | 40.8 | 19.3 | 65.1 | 3.2 | 241.1 | 4.9 | 443.6 | 452.3 | 217.6 | 72 | 533.3 | 538.5 | 122.8 | 87 | 238.3 | 518.3 | 266.6 | 287.2 | 445.7 | 282 | 252.6 | 549.5 | 354.3 | 236.1 | 215.1 | 208.8 | 218.4 | 227 | 208.6 | 220.5 | 222.7
2783.1 | 2562.1 | -6.6 | 0 | 0 | 234 | 213.9 | 202.7 | 205.3 | 238.6 | 40.8 | 19.3 | 65.1 | 3 | 236.2 | 4.6 | 443.6 | 452.2 | 217.6 | 71.8 | 533.3 | 538.3 | 122.7 | 86.8 | 238.1 | 518 | 267.3 | 286.2 | 445.5 | 283.1 | 251.8 | 549.6 | 354.2 | 236 | 214.9 | 208.7 | 218.3 | 226.9 | 208.5 | 220.4 | 222.6
2784.1 | 2563.1 | -6.6 | 0 | 0 | 233.7 | 213.8 | 202.8 | 205.2 | 238.3 | 40.8 | 19.3 | 65.1 | 2.8 | 242.7 | 4.4 | 443.6 | 452 | 217.4 | 71.7 | 533.3 | 538 | 122.6 | 86.4 | 238 | 517.6 | 266.8 | 286.3 | 445.2 | 283.1 | 252.3 | 549.8 | 354.1 | 235.9 | 214.8 | 208.6 | 218.2 | 226.7 | 208.3 | 220.1 | 222.4
2785.1 | 2564.1 | -6.7 | 0 | 0 | 233.6 | 213.7 | 202.7 | 204.9 | 237.9 | 40.7 | 19.3 | 65.1 | 2.7 | 263.9 | 4.3 | 443.6 | 451.9 | 217 | 71.5 | 533.3 | 537.8 | 122.3 | 86.3 | 238 | 517.4 | 268.5 | 286.8 | 445 | 282.1 | 252.9 | 549.5 | 354.1 | 235.7 | 214.6 | 208.4 | 218.1 | 226.6 | 208.2 | 219.8 | 222.3
2786.1 | 2565.1 | -6.7 | 0 | 0 | 233.5 | 213.7 | 202.6 | 204.6 | 237.5 | 40.6 | 19.3 | 65 | 2.8 | 235.6 | 3.8 | 443.6 | 451.9 | 216.8 | 71.4 | 533.3 | 537.9 | 122.2 | 86.3 | 238 | 517.1 | 269.2 | 287.2 | 444.8 | 281.3 | 253.6 | 549.2 | 353.9 | 235.6 | 214.5 | 208.3 | 217.9 | 226.5 | 208.1 | 219.6 | 222.2
2787.1 | 2566.1 | -6.7 | 0 | 0 | 233.2 | 213.6 | 202.4 | 204.4 | 237.2 | 40.5 | 19.3 | 64.9 | 2.8 | 211.4 | 3 | 443.6 | 451.8 | 216.3 | 71.2 | 533.2 | 537.9 | 122.2 | 86.1 | 238 | 516.8 | 269.6 | 287.5 | 444.5 | 281.3 | 254.1 | 549 | 353.8 | 235.5 | 214.3 | 208.2 | 217.8 | 226.4 | 208 | 219.4 | 222
2788.1 | 2567.1 | -6.7 | 0 | 0 | 233 | 213.5 | 202.3 | 204.3 | 236.8 | 40.4 | 19.3 | 64.8 | 2.8 | 221.8 | 2.4 | 443.5 | 451.8 | 214.2 | 71.1 | 533.2 | 538.1 | 123.8 | 86 | 237.9 | 516.6 | 270.2 | 287.6 | 444.3 | 281.4 | 254.6 | 548.9 | 353.7 | 235.3 | 214.2 | 208.2 | 217.7 | 226.2 | 208 | 219.3 | 221.9
2789.1 | 2568.1 | -6.7 | 0 | 0 | 232.9 | 213.4 | 202.3 | 204.1 | 236.5 | 40.4 | 19.3 | 64.8 | 3 | 244.7 | 2.4 | 443.5 | 451.8 | 212.1 | 71 | 533.2 | 538.2 | 124.2 | 86 | 237.8 | 516.4 | 271.4 | 287.7 | 444.1 | 281.4 | 254.6 | 548.8 | 353.6 | 235.2 | 214.1 | 208.1 | 217.6 | 226.1 | 208 | 219 | 221.8
2790.1 | 2569.1 | -6.7 | 0 | 0 | 232.5 | 213.3 | 202.1 | 203.9 | 236.2 | 40.4 | 19.3 | 64.7 | 3 | 255.8 | 2.5 | 443.5 | 451.8 | 211 | 71 | 533.1 | 538.4 | 124.1 | 86.1 | 237.8 | 516.2 | 271.6 | 287.1 | 443.9 | 280.8 | 253.9 | 548.8 | 353.6 | 235.1 | 214 | 208.1 | 217.5 | 226 | 208 | 218.8 | 221.7
2791.1 | 2570.1 | -6.4 | 0 | 0 | 232.2 | 213.1 | 201.9 | 203.7 | 235.9 | 40.3 | 19.3 | 64.7 | 3 | 252.8 | 2.4 | 443.5 | 451.7 | 210.2 | 71 | 533 | 538.6 | 124.2 | 86 | 237.7 | 516 | 272.2 | 287.3 | 443.6 | 279.2 | 253.9 | 548.6 | 353.4 | 234.9 | 213.9 | 207.9 | 217.4 | 225.8 | 207.8 | 218.6 | 221.5
2792.1 | 2571.1 | -6.7 | 0 | 0 | 232.1 | 213 | 201.9 | 203.5 | 235.9 | 40.3 | 19.3 | 64.7 | 2.9 | 248.5 | 2.6 | 443.5 | 451.6 | 210.1 | 70.9 | 533 | 538.8 | 124 | 86 | 237.6 | 515.9 | 273.1 | 287.1 | 443.4 | 278.9 | 253.8 | 548.6 | 353.1 | 234.8 | 213.7 | 207.8 | 217.2 | 225.7 | 207.6 | 218.4 | 221.4
2793.1 | 2572.1 | -6.7 | 0 | 0 | 232 | 212.9 | 201.9 | 203.3 | 235.5 | 40.2 | 19.3 | 64.7 | 2.9 | 242.9 | 2.7 | 443.5 | 451.6 | 210.3 | 70.8 | 532.9 | 538.8 | 123.5 | 85.9 | 237.5 | 515.8 | 272.8 | 287.4 | 443.1 | 278.4 | 253.7 | 548.6 | 352.8 | 234.7 | 213.5 | 207.7 | 217.1 | 225.6 | 207.5 | 218.2 | 221.3
2794.1 | 2573.1 | -6.7 | 0 | 0 | 231.8 | 212.8 | 201.9 | 203.1 | 235.4 | 40.2 | 19.3 | 64.7 | 2.8 | 239.9 | 2.7 | 443.4 | 451.7 | 210.4 | 70.7 | 532.9 | 538.8 | 122.9 | 85.9 | 237.4 | 515.7 | 271.6 | 287 | 442.9 | 278.3 | 253.1 | 548.8 | 352.4 | 234.5 | 213.4 | 207.5 | 217 | 225.4 | 207.5 | 218 | 221.2
2795.1 | 2574.1 | -6.7 | 0 | 0 | 231.5 | 212.6 | 201.7 | 202.9 | 235.5 | 40.1 | 19.4 | 64.7 | 2.9 | 240.8 | 2.7 | 443.4 | 451.9 | 210 | 70.7 | 532.9 | 538.8 | 122.5 | 85.8 | 237.3 | 515.6 | 270.5 | 286.2 | 442.6 | 278.2 | 252.1 | 548.9 | 352.1 | 234.4 | 213.3 | 207.5 | 216.9 | 225.3 | 207.4 | 218.1 | 221
2796.1 | 2575.1 | -6.7 | 0 | 0 | 231.1 | 212.5 | 201.5 | 202.8 | 235.7 | 40.1 | 19.4 | 64.7 | 2.7 | 246.9 | 2.5 | 443.4 | 452.1 | 209.8 | 70.6 | 532.8 | 538.7 | 122.2 | 85.6 | 237.2 | 515.5 | 269.8 | 285.4 | 442.4 | 278.1 | 252.2 | 548.7 | 351.9 | 234.2 | 213.2 | 207.4 | 216.8 | 225.1 | 207.3 | 217.9 | 220.9
2797.1 | 2576.1 | -6.7 | 0 | 0 | 230.8 | 212.4 | 201.3 | 202.7 | 235.5 | 40.1 | 19.4 | 64.6 | 2.5 | 259.3 | 2.4 | 443.4 | 452.2 | 210.3 | 70.5 | 532.8 | 538.6 | 121.7 | 85.6 | 237.1 | 515.2 | 269.2 | 284.6 | 442.2 | 277.8 | 252.2 | 548.4 | 351.8 | 234.1 | 213.1 | 207.3 | 216.6 | 225 | 207.2 | 217.7 | 220.8
2798.1 | 2577.1 | -6.7 | 0 | 0 | 230.6 | 212.3 | 201.1 | 202.5 | 235.5 | 40.1 | 19.4 | 64.6 | 2.6 | 268.4 | 2.5 | 443.4 | 452.1 | 211.2 | 70.6 | 532.9 | 538.4 | 121.2 | 85.7 | 237 | 514.9 | 268.5 | 283.3 | 441.9 | 277.6 | 251.4 | 548.2 | 351.6 | 234 | 212.9 | 207.1 | 216.5 | 224.9 | 207.2 | 217.6 | 220.6
2799.1 | 2578.1 | -6.7 | 0 | 0 | 230.5 | 212.1 | 200.9 | 202.3 | 235.4 | 40 | 19.4 | 64.6 | 3 | 272.7 | 2.6 | 443.3 | 451.9 | 209.9 | 70.7 | 532.9 | 538.2 | 120.9 | 85.8 | 236.9 | 514.8 | 268.3 | 282.6 | 441.7 | 278.1 | 251.1 | 548.2 | 351.4 | 233.9 | 212.9 | 207 | 216.4 | 224.8 | 207 | 217.5 | 220.5
2800.1 | 2579.1 | -6.7 | 0 | 0 | 230.2 | 211.9 | 200.8 | 202.2 | 235.4 | 40 | 19.4 | 64.6 | 3.4 | 273.7 | 2.7 | 443.3 | 451.8 | 209.4 | 70.9 | 532.9 | 537.9 | 120.7 | 85.8 | 236.9 | 514.6 | 267.2 | 282.8 | 441.4 | 277.7 | 251.2 | 548.3 | 351.2 | 233.7 | 212.8 | 206.9 | 216.3 | 224.6 | 206.9 | 217.5 | 220.4
2801.1 | 2580.1 | -6.7 | 0 | 0 | 229.8 | 211.8 | 200.7 | 202.3 | 235.4 | 39.9 | 19.4 | 64.6 | 3.3 | 274.6 | 2.7 | 443.3 | 451.6 | 209.3 | 71 | 532.9 | 537.8 | 120.4 | 85.6 | 236.8 | 514.5 | 266.5 | 282.3 | 441.2 | 277.6 | 251.2 | 548.4 | 350.9 | 233.6 | 212.7 | 206.8 | 216.1 | 224.5 | 206.7 | 217.4 | 220.3
2802.1 | 2581.1 | -6.7 | 0 | 0 | 229.6 | 211.7 | 200.7 | 202.2 | 235.2 | 39.9 | 19.4 | 64.5 | 3.2 | 274.4 | 2.9 | 443.3 | 451.5 | 209.9 | 70.9 | 532.9 | 537.5 | 120.2 | 85.6 | 236.7 | 514.4 | 265.8 | 282 | 440.9 | 277.7 | 251 | 548.4 | 350.7 | 233.4 | 212.6 | 206.6 | 216 | 224.4 | 206.6 | 217.4 | 220.1
2803.1 | 2582.1 | -6.5 | 0 | 0 | 229.5 | 211.6 | 200.5 | 202.3 | 235.1 | 39.9 | 19.4 | 64.5 | 3.3 | 274.1 | 3.1 | 443.3 | 451.5 | 210.4 | 70.7 | 532.9 | 537.3 | 119.7 | 85.5 | 236.6 | 514.2 | 264.9 | 281.7 | 440.7 | 277.4 | 251.2 | 548.5 | 350.7 | 233.3 | 212.5 | 206.5 | 215.9 | 224.2 | 206.4 | 217.3 | 220
2804.1 | 2583.1 | -6.4 | 0 | 0 | 229.3 | 211.5 | 200.5 | 202.4 | 235.1 | 39.9 | 19.4 | 64.4 | 3.3 | 272.9 | 3.2 | 443.2 | 451.6 | 208.9 | 70.6 | 533 | 537.1 | 119.2 | 85.4 | 236.5 | 514 | 263.5 | 280.9 | 440.5 | 276.9 | 251.4 | 548.5 | 350.6 | 233.2 | 212.4 | 206.4 | 215.8 | 224.1 | 206.2 | 217.2 | 219.9
2805.1 | 2584.1 | -6.7 | 0 | 0 | 229.3 | 211.4 | 200.4 | 202.3 | 235 | 39.8 | 19.4 | 64.3 | 3.2 | 272.7 | 3.4 | 443.2 | 451.6 | 208.3 | 70.5 | 533 | 537 | 119.1 | 85.3 | 236.4 | 513.8 | 262.9 | 280 | 440.3 | 275.8 | 251.6 | 548.4 | 350.5 | 233 | 212.3 | 206.3 | 215.7 | 224 | 206.1 | 217 | 219.8
2806.1 | 2585.1 | -6.7 | 0 | 0 | 229.2 | 211.2 | 200.3 | 202.1 | 234.8 | 39.8 | 19.4 | 64.3 | 3.2 | 270.7 | 3.6 | 443.2 | 451.6 | 209.2 | 70.4 | 532.9 | 537 | 118.7 | 85.1 | 236.2 | 513.6 | 261.8 | 279.2 | 440 | 276.1 | 251.3 | 548.3 | 350.4 | 232.9 | 212.2 | 206.1 | 215.5 | 223.9 | 205.9 | 216.9 | 219.6
2807.1 | 2586.1 | -6.7 | 0 | 0 | 229.1 | 211.1 | 200.2 | 202 | 234.6 | 39.8 | 19.4 | 64.2 | 3.3 | 265.7 | 3.8 | 443.2 | 451.5 | 207.4 | 70.4 | 532.9 | 536.9 | 118.4 | 84.9 | 236.1 | 513.4 | 261.6 | 278.8 | 439.8 | 275.4 | 251.1 | 548.3 | 350.2 | 232.8 | 212 | 206 | 215.4 | 223.7 | 205.7 | 216.6 | 219.5
2808.1 | 2587.1 | -6.7 | 0 | 0 | 228.9 | 211 | 200 | 201.9 | 234.5 | 39.8 | 19.4 | 64.2 | 3.5 | 262.3 | 3.9 | 443.2 | 451.6 | 207.8 | 70.2 | 532.9 | 536.8 | 118.3 | 84.8 | 236 | 513.1 | 260.9 | 278.9 | 439.5 | 275 | 251 | 548.4 | 350 | 232.6 | 211.9 | 205.9 | 215.3 | 223.6 | 205.6 | 216.3 | 219.4
2809.1 | 2588.1 | -6.7 | 0 | 0 | 228.7 | 210.8 | 200 | 201.8 | 234.2 | 39.7 | 19.4 | 64.2 | 3.6 | 256.6 | 3.9 | 443.2 | 451.6 | 209.2 | 70.1 | 532.9 | 536.8 | 117.9 | 84.7 | 235.9 | 512.8 | 260.4 | 278.8 | 439.3 | 273.9 | 250.2 | 548.4 | 349.7 | 232.5 | 211.8 | 205.7 | 215.2 | 223.5 | 205.5 | 216.1 | 219.3
2810.1 | 2589.1 | -6.7 | 0 | 0 | 228.5 | 210.8 | 200 | 201.7 | 234.2 | 39.7 | 19.4 | 64.2 | 3.5 | 254.5 | 3.7 | 443.1 | 451.6 | 209.2 | 70 | 532.9 | 536.7 | 117.6 | 84.6 | 235.7 | 512.6 | 260.3 | 278.6 | 439.1 | 273.6 | 249.1 | 548.1 | 349.4 | 232.4 | 211.7 | 205.6 | 215.1 | 223.3 | 205.3 | 215.9 | 219.1
2811.1 | 2590.1 | -6.7 | 0 | 0 | 228.4 | 210.7 | 199.9 | 201.6 | 233.9 | 39.7 | 19.4 | 64.2 | 3.7 | 254.2 | 3.4 | 443.1 | 451.6 | 209.6 | 69.8 | 532.9 | 536.6 | 117.2 | 84.5 | 235.6 | 512.3 | 259.8 | 278.1 | 438.8 | 272.9 | 248.9 | 547.9 | 349 | 232.3 | 211.6 | 205.5 | 215 | 223.2 | 205.2 | 215.8 | 219
2812.1 | 2591.1 | -6.7 | 0 | 0 | 228.3 | 210.5 | 199.7 | 201.5 | 233.5 | 39.7 | 19.4 | 64.1 | 3.4 | 254.5 | 3.4 | 443.1 | 451.6 | 209.5 | 69.7 | 532.9 | 536.4 | 116.8 | 84.5 | 235.5 | 512 | 259.9 | 277.2 | 438.6 | 272.5 | 248.7 | 547.8 | 348.8 | 232.1 | 211.5 | 205.4 | 214.8 | 223 | 205 | 215.6 | 218.9
2813.1 | 2592.1 | -6.7 | 0 | 0 | 228.2 | 210.4 | 199.5 | 201.3 | 233.3 | 39.6 | 19.4 | 64 | 3.6 | 254.3 | 3.3 | 443.1 | 451.6 | 209.9 | 69.7 | 532.9 | 536.3 | 116.2 | 84.5 | 235.4 | 511.7 | 260.1 | 277.3 | 438.3 | 272.3 | 248.6 | 547.8 | 348.5 | 232 | 211.3 | 205.3 | 214.7 | 222.9 | 204.9 | 215.4 | 218.8
2814.1 | 2593.1 | -6.7 | 0 | 0 | 228.1 | 210.3 | 199.3 | 201.3 | 233.2 | 39.6 | 19.4 | 64 | 3.4 | 250.6 | 3.2 | 443.1 | 451.6 | 209 | 69.7 | 532.9 | 536.1 | 115.7 | 84.4 | 235.3 | 511.5 | 260.1 | 277.7 | 438.1 | 272 | 247.7 | 547.6 | 348.3 | 231.9 | 211.2 | 205.1 | 214.6 | 222.8 | 204.7 | 215.2 | 218.6
2815.1 | 2594.1 | -6.7 | 0 | 0 | 228.1 | 210.2 | 199.2 | 201.1 | 233 | 39.6 | 19.4 | 63.9 | 3.1 | 241.9 | 3.2 | 443 | 451.6 | 209 | 69.6 | 532.9 | 536 | 115.2 | 84.2 | 235.2 | 511.3 | 260.5 | 278.3 | 437.8 | 272.1 | 247.5 | 547.4 | 348.3 | 231.8 | 211 | 205 | 214.5 | 222.6 | 204.6 | 215.1 | 218.5
2816.1 | 2595.1 | -6.7 | 0 | 0 | 227.8 | 210.1 | 199.1 | 201 | 233.1 | 39.6 | 19.4 | 63.8 | 3.3 | 238.8 | 3 | 443 | 451.5 | 208.2 | 69.4 | 532.9 | 535.9 | 114.9 | 84.1 | 235.1 | 511.1 | 259.6 | 278.5 | 437.6 | 271.4 | 246.3 | 547.4 | 348.1 | 231.6 | 210.9 | 204.9 | 214.4 | 222.5 | 204.5 | 215.1 | 218.4
2817.1 | 2596.1 | -6.7 | 0 | 0 | 227.6 | 209.9 | 199.2 | 200.9 | 233.3 | 39.5 | 19.4 | 63.8 | 2.9 | 246.5 | 2.9 | 443 | 451.6 | 209.4 | 69.3 | 532.8 | 535.7 | 114.7 | 84 | 235 | 510.8 | 258.9 | 278 | 437.4 | 271.9 | 245.1 | 547.2 | 347.9 | 231.5 | 210.7 | 204.8 | 214.2 | 222.4 | 204.3 | 214.9 | 218.3
2818.1 | 2597.1 | -6.7 | 0 | 0 | 227.4 | 209.7 | 199.1 | 200.9 | 233 | 39.5 | 19.4 | 63.8 | 3.1 | 253.5 | 2.9 | 443 | 451.6 | 208.8 | 69.3 | 532.8 | 535.6 | 114.5 | 83.9 | 234.9 | 510.5 | 257.7 | 277.5 | 437.2 | 271.4 | 244.6 | 547 | 347.9 | 231.4 | 210.6 | 204.7 | 214.1 | 222.2 | 204.2 | 214.7 | 218.2
2819.1 | 2598.1 | -6.7 | 0 | 0 | 227.1 | 209.6 | 199 | 200.7 | 232.9 | 39.5 | 19.4 | 63.7 | 3.2 | 252.6 | 3.5 | 443 | 451.5 | 208.9 | 69.3 | 532.8 | 535.4 | 114.5 | 83.8 | 234.8 | 510.3 | 257.5 | 277.7 | 436.9 | 270.3 | 244.5 | 546.9 | 347.7 | 231.3 | 210.5 | 204.6 | 214 | 222.1 | 204 | 214.5 | 218
2820.1 | 2599.1 | -6.7 | 0 | 0 | 227.1 | 209.6 | 198.8 | 200.7 | 232.7 | 39.4 | 19.4 | 63.7 | 2.9 | 249.6 | 4.6 | 443 | 451.4 | 207.9 | 69.2 | 532.7 | 535.3 | 114.1 | 83.5 | 234.6 | 510.1 | 257.1 | 277.6 | 436.7 | 269.7 | 244.4 | 546.7 | 347.5 | 231.1 | 210.4 | 204.5 | 213.9 | 221.9 | 203.9 | 214.4 | 217.9
2821.1 | 2600.1 | -6.7 | 0 | 0 | 226.8 | 209.6 | 198.7 | 200.8 | 232.2 | 39.4 | 19.4 | 63.7 | 2.9 | 244.3 | 5.1 | 442.9 | 451.4 | 207.1 | 69 | 532.7 | 535.2 | 113.7 | 83.2 | 234.5 | 509.9 | 257 | 277.2 | 436.5 | 268.8 | 243.8 | 546.4 | 347.3 | 231 | 210.4 | 204.4 | 213.8 | 221.8 | 203.8 | 214.2 | 217.8
2822.1 | 2601.1 | -6.6 | 0 | 0 | 226.6 | 209.6 | 198.4 | 200.8 | 231.7 | 39.4 | 19.4 | 63.6 | 3 | 256.5 | 5.1 | 442.9 | 451.3 | 206.2 | 68.8 | 532.6 | 535.1 | 113.4 | 82.9 | 234.3 | 509.6 | 257.4 | 276.8 | 436.3 | 268.7 | 243.4 | 546.2 | 347.2 | 230.8 | 210.2 | 204.2 | 213.6 | 221.7 | 203.6 | 214.1 | 217.7
2823.1 | 2602.1 | -6.7 | 0 | 0 | 226.4 | 209.6 | 198.3 | 200.7 | 231.8 | 39.4 | 19.4 | 63.6 | 2.9 | 262.7 | 4.9 | 442.9 | 451.2 | 205.2 | 68.7 | 532.6 | 534.9 | 113.1 | 82.7 | 234.2 | 509.3 | 257.1 | 276 | 436 | 268.8 | 243.4 | 546.1 | 347.1 | 230.7 | 210.1 | 204 | 213.5 | 221.5 | 203.5 | 213.9 | 217.5
2824.1 | 2603.1 | -6.7 | 0 | 0 | 226.1 | 209.5 | 198.3 | 200.6 | 231.9 | 39.3 | 19.4 | 63.6 | 2.8 | 246.4 | 4.4 | 442.9 | 451.1 | 202.5 | 68.7 | 532.5 | 534.8 | 112.9 | 82.5 | 234.1 | 509.1 | 256.3 | 275.5 | 435.8 | 268.8 | 243.2 | 546 | 346.9 | 230.6 | 209.9 | 203.9 | 213.4 | 221.4 | 203.3 | 213.8 | 217.4
2825.1 | 2604.1 | -6.6 | 0 | 0 | 225.9 | 209.4 | 198.3 | 200.5 | 232.1 | 39.3 | 19.4 | 63.5 | 2.8 | 228.5 | 4.3 | 442.9 | 451.1 | 202.2 | 68.7 | 532.5 | 534.6 | 112.7 | 82.4 | 234 | 508.8 | 255.3 | 275.3 | 435.5 | 269.2 | 243.1 | 546 | 346.7 | 230.4 | 209.8 | 203.7 | 213.3 | 221.3 | 203.2 | 213.8 | 217.3
2826.1 | 2605.1 | -6.6 | 0 | 0 | 225.8 | 209.3 | 198.1 | 200.5 | 232 | 39.3 | 19.4 | 63.5 | 2.9 | 241.5 | 4.5 | 442.8 | 451.2 | 202.5 | 68.7 | 532.4 | 534.4 | 112.5 | 82.3 | 233.9 | 508.6 | 254.4 | 274.9 | 435.3 | 270.2 | 242.8 | 546.1 | 346.5 | 230.3 | 209.7 | 203.6 | 213.1 | 221.2 | 203.1 | 213.7 | 217.2
2827.1 | 2606.1 | -6.6 | 0 | 0 | 225.8 | 209.2 | 197.9 | 200.4 | 231.7 | 39.2 | 19.4 | 63.5 | 2.8 | 247.7 | 4.6 | 442.8 | 451.2 | 203.6 | 68.6 | 532.4 | 534.2 | 112.3 | 82.1 | 233.8 | 508.4 | 254.3 | 273.2 | 435.1 | 269.6 | 242.1 | 546.1 | 346.3 | 230.2 | 209.6 | 203.5 | 213 | 221 | 203 | 213.5 | 217
2828.1 | 2607.1 | -6.7 | 0 | 0 | 225.8 | 209.2 | 197.7 | 200.2 | 231.4 | 39.2 | 19.4 | 63.5 | 2.9 | 247.1 | 4.7 | 442.8 | 451.2 | 203.1 | 68.5 | 532.4 | 534.1 | 111.8 | 82 | 233.7 | 508.1 | 254.9 | 271.8 | 434.9 | 268.7 | 242.3 | 546.1 | 346 | 230 | 209.4 | 203.4 | 212.9 | 220.9 | 202.9 | 213.7 | 216.9
2829.1 | 2608.1 | -6.7 | 0 | 0 | 225.6 | 209.1 | 197.4 | 199.8 | 231.2 | 39.3 | 19.4 | 63.4 | 3 | 245.7 | 4.5 | 442.8 | 451 | 202.7 | 68.4 | 532.4 | 534 | 111.4 | 81.8 | 233.6 | 507.8 | 255.1 | 271.2 | 434.6 | 267.9 | 242.1 | 546.1 | 345.8 | 229.9 | 209.3 | 203.2 | 212.8 | 220.7 | 203 | 213.8 | 216.8
2830.1 | 2609.1 | -6.4 | 0 | 0 | 225.5 | 209 | 197.3 | 199.5 | 231 | 39.3 | 19.4 | 63.4 | 3.1 | 244.3 | 4.2 | 442.8 | 450.9 | 201.7 | 68.3 | 532.3 | 533.9 | 111.1 | 81.5 | 233.6 | 507.5 | 255.3 | 271 | 434.4 | 267.8 | 241.8 | 546.2 | 345.6 | 229.8 | 209.1 | 203.1 | 212.7 | 220.6 | 203 | 213.8 | 216.7
2831.1 | 2610.1 | -5.7 | 0 | 0 | 225.4 | 208.8 | 197.3 | 199.3 | 231 | 39.3 | 19.4 | 63.4 | 3.4 | 244.5 | 3.9 | 442.8 | 450.7 | 200.4 | 68.1 | 532.3 | 534.2 | 110.7 | 81.4 | 233.5 | 507.3 | 255 | 271 | 434.2 | 267.3 | 241.2 | 546.1 | 345.5 | 229.7 | 209 | 202.9 | 212.5 | 220.5 | 203 | 213.7 | 216.5
2832.1 | 2611.1 | -5.5 | 0 | 0 | 225.3 | 208.8 | 197.3 | 199.2 | 230.7 | 39.3 | 19.4 | 63.4 | 3.1 | 246.2 | 3.7 | 442.7 | 450.7 | 200.5 | 68 | 532.3 | 534.3 | 110.2 | 81.4 | 233.5 | 507.1 | 255 | 271.1 | 433.9 | 267.2 | 240.7 | 546.1 | 345.3 | 229.5 | 208.8 | 202.8 | 212.4 | 220.4 | 202.8 | 213.5 | 216.4
2833.1 | 2612.1 | -5.6 | 0 | 0 | 225.3 | 208.7 | 197.1 | 199.1 | 230.7 | 39.3 | 19.4 | 63.3 | 3.1 | 245.1 | 3.6 | 442.7 | 450.6 | 200.1 | 68 | 532.3 | 534.5 | 111 | 81.4 | 233.6 | 506.8 | 255.9 | 271.5 | 433.7 | 266 | 240.7 | 546.1 | 345 | 229.4 | 208.7 | 202.6 | 212.3 | 220.2 | 202.7 | 213.3 | 216.3
2834.1 | 2613.1 | -6.1 | 0 | 0 | 225.3 | 208.5 | 197 | 198.9 | 230.6 | 39.3 | 19.4 | 63.3 | 3.2 | 244.7 | 3.5 | 442.7 | 450.8 | 201.5 | 68 | 532.2 | 534.5 | 110.8 | 81.5 | 233.6 | 506.6 | 255.7 | 271.7 | 433.4 | 264.2 | 240.5 | 546.1 | 344.8 | 229.2 | 208.6 | 202.5 | 212.2 | 220.1 | 202.5 | 213.2 | 216.2
2835.1 | 2614.1 | -6 | 0 | 0 | 225.2 | 208.4 | 196.9 | 198.8 | 230.6 | 39.2 | 19.4 | 63.3 | 3 | 241.5 | 3.4 | 442.7 | 450.8 | 202 | 68 | 532.2 | 534.6 | 110.7 | 81.7 | 233.6 | 506.4 | 255.9 | 271.9 | 433.2 | 264.3 | 240.5 | 546.2 | 344.6 | 229.1 | 208.5 | 202.4 | 212.1 | 220 | 202.3 | 213.1 | 216.1
2836.1 | 2615.1 | -5.1 | 0 | 0 | 225 | 208.3 | 196.8 | 198.5 | 230.9 | 39.1 | 19.5 | 63.3 | 3 | 240.9 | 3.4 | 442.6 | 450.9 | 200.7 | 68 | 532.2 | 534.6 | 110.8 | 81.5 | 233.6 | 506.1 | 255.8 | 272.1 | 432.9 | 263.4 | 239.9 | 546.3 | 344.4 | 229 | 208.4 | 202.3 | 212 | 219.8 | 202.1 | 212.8 | 215.9
2837.1 | 2616.1 | -5.4 | 0 | 0 | 225.1 | 208.2 | 196.7 | 198.1 | 231 | 39 | 19.5 | 63.3 | 3.1 | 240.1 | 3.5 | 442.6 | 451 | 200.6 | 67.9 | 532.1 | 534.6 | 110.4 | 81.5 | 233.5 | 505.9 | 257 | 272.5 | 432.7 | 261.7 | 239.7 | 546.4 | 344.3 | 228.9 | 208.3 | 202.2 | 211.9 | 219.7 | 201.9 | 212.7 | 215.8
2838.1 | 2617.1 | -5.8 | 0 | 0 | 225.1 | 208.2 | 196.6 | 197.9 | 230.5 | 38.9 | 19.5 | 63.3 | 3 | 238.4 | 3.5 | 442.6 | 451 | 200.7 | 67.8 | 532.1 | 534.6 | 110.2 | 81.5 | 233.4 | 505.7 | 257 | 272.3 | 432.5 | 260 | 239.6 | 546.5 | 344.2 | 228.7 | 208.2 | 202.1 | 211.7 | 219.6 | 201.7 | 212.5 | 215.7
2839.1 | 2618.1 | -6.1 | 0 | 0 | 224.8 | 208.1 | 196.5 | 197.8 | 229.9 | 38.9 | 19.5 | 63.3 | 2.9 | 237.4 | 3.3 | 442.6 | 450.9 | 200.7 | 67.8 | 532.1 | 534.6 | 109.9 | 81.5 | 233.4 | 505.4 | 257.2 | 271.3 | 432.2 | 258.7 | 238 | 546.4 | 344.1 | 228.6 | 208.1 | 202 | 211.6 | 219.5 | 201.6 | 212.3 | 215.6
2840.1 | 2619.1 | -6 | 0 | 0 | 224.6 | 208 | 196.3 | 197.7 | 229.5 | 38.9 | 19.5 | 63.3 | 3.1 | 240.7 | 3.3 | 442.6 | 450.7 | 200.3 | 67.8 | 532.1 | 534.5 | 109.7 | 81.4 | 233.5 | 505.2 | 256.8 | 271 | 432 | 257.9 | 237.8 | 546.2 | 344 | 228.5 | 208 | 201.9 | 211.5 | 219.4 | 201.5 | 212.3 | 215.4
2841.1 | 2620.1 | -6.2 | 0 | 0 | 224.5 | 207.9 | 196.1 | 197.5 | 229.3 | 38.9 | 19.5 | 63.2 | 3 | 248.4 | 3.2 | 442.5 | 450.6 | 199.1 | 67.9 | 532.1 | 534.4 | 109.4 | 81.3 | 233.5 | 504.9 | 256.1 | 271.1 | 431.7 | 257.8 | 238 | 546 | 343.8 | 228.4 | 207.9 | 201.8 | 211.4 | 219.3 | 201.5 | 212.1 | 215.3
2842.1 | 2621.1 | -6.5 | 0 | 0 | 224.5 | 207.7 | 196 | 197.4 | 229.6 | 38.9 | 19.5 | 63.2 | 3.2 | 246.7 | 3.2 | 442.5 | 450.7 | 198.3 | 67.8 | 532.1 | 534.3 | 109.4 | 81.4 | 233.5 | 504.7 | 255.3 | 271.1 | 431.5 | 258 | 238 | 546 | 343.6 | 228.2 | 207.7 | 201.7 | 211.3 | 219.1 | 201.4 | 212 | 215.2
2843.1 | 2622.1 | -6.4 | 0 | 0 | 224.6 | 207.6 | 195.9 | 197.3 | 229.5 | 38.9 | 19.5 | 63.1 | 3.2 | 246.6 | 3.2 | 442.5 | 450.8 | 198.3 | 67.7 | 532 | 534.3 | 109.2 | 81.3 | 233.5 | 504.5 | 255 | 270.7 | 431.2 | 258.3 | 237.8 | 546.1 | 343.4 | 228.1 | 207.6 | 201.6 | 211.2 | 219 | 201.2 | 211.9 | 215.1
2844.1 | 2623.1 | -6.4 | 0 | 0 | 224.6 | 207.4 | 195.8 | 197.1 | 229.3 | 38.9 | 19.5 | 63 | 3.1 | 247.1 | 3.2 | 442.5 | 450.7 | 197 | 67.6 | 532 | 534.3 | 108.9 | 81.1 | 233.4 | 504.2 | 254.3 | 270 | 431 | 257.7 | 237.8 | 546.1 | 343.2 | 227.9 | 207.5 | 201.5 | 211.1 | 218.9 | 201.1 | 211.6 | 214.9
2845.1 | 2624.1 | -6.7 | 0 | 0 | 224.6 | 207.3 | 195.7 | 196.9 | 229 | 38.8 | 19.5 | 63 | 3.2 | 248.4 | 3.2 | 442.5 | 450.7 | 196.1 | 67.5 | 531.9 | 534.3 | 108.7 | 80.8 | 233.4 | 503.9 | 253.5 | 269.4 | 430.8 | 256.3 | 237.6 | 545.9 | 342.9 | 227.8 | 207.4 | 201.4 | 210.9 | 218.7 | 201 | 211.4 | 214.8
2846.1 | 2625.1 | -6.7 | 0 | 0 | 224.4 | 207.3 | 195.5 | 196.8 | 228.8 | 38.8 | 19.5 | 63 | 3 | 250 | 3 | 442.4 | 450.7 | 195.2 | 67.5 | 531.9 | 534.4 | 108.6 | 80.5 | 233.4 | 503.6 | 252.8 | 269.4 | 430.5 | 255.9 | 236 | 545.9 | 342.7 | 227.7 | 207.3 | 201.3 | 210.8 | 218.6 | 200.8 | 211.2 | 214.7
2847.1 | 2626.1 | -6.7 | 0 | 0 | 224.3 | 207.2 | 195.4 | 196.7 | 229 | 38.8 | 19.5 | 63 | 3 | 250.3 | 2.8 | 442.4 | 450.6 | 196.6 | 67.6 | 531.9 | 534.4 | 109.3 | 80.3 | 233.3 | 503.4 | 254 | 269.2 | 430.3 | 256.5 | 235.1 | 545.8 | 342.6 | 227.6 | 207.2 | 201.2 | 210.7 | 218.5 | 200.7 | 211 | 214.6
2848.1 | 2627.1 | -6.7 | 0 | 0 | 224 | 207.1 | 195.2 | 196.6 | 228.9 | 38.7 | 19.5 | 63 | 3.1 | 251.6 | 2.7 | 442.4 | 450.6 | 197.7 | 67.6 | 531.8 | 534.5 | 109.9 | 80.3 | 233.3 | 503.1 | 253.9 | 269.2 | 430 | 257.7 | 235 | 545.8 | 342.4 | 227.4 | 207 | 201.1 | 210.6 | 218.4 | 200.5 | 211 | 214.5
2849.1 | 2628.1 | -6.7 | 0 | 0 | 223.9 | 206.9 | 195.1 | 196.5 | 228.9 | 38.7 | 19.5 | 62.9 | 3.3 | 255.6 | 2.7 | 442.4 | 450.7 | 196.2 | 67.6 | 531.8 | 534.5 | 109.8 | 80.3 | 233.4 | 502.9 | 254.9 | 268.9 | 429.8 | 258.3 | 235.3 | 545.9 | 342.2 | 227.3 | 206.9 | 201 | 210.5 | 218.3 | 200.5 | 210.9 | 214.3
2850.1 | 2629.1 | -6.6 | 0 | 0 | 223.8 | 206.7 | 195 | 196.3 | 228.7 | 38.7 | 19.5 | 62.8 | 3.1 | 263.6 | 2.6 | 442.4 | 450.7 | 194.1 | 67.6 | 531.8 | 534.5 | 110.2 | 80.2 | 233.5 | 502.6 | 254.5 | 268.7 | 429.5 | 257.6 | 235.4 | 545.8 | 342 | 227.2 | 206.8 | 200.9 | 210.4 | 218.2 | 200.6 | 210.8 | 214.2
2851.1 | 2630.1 | -6.7 | 0 | 0 | 223.7 | 206.6 | 194.9 | 196 | 228.2 | 38.6 | 19.5 | 62.7 | 3.2 | 273.9 | 2.6 | 442.3 | 450.5 | 192.5 | 67.6 | 531.7 | 534.6 | 110.2 | 80.2 | 233.5 | 502.4 | 255.1 | 268.6 | 429.3 | 257.5 | 235.5 | 545.8 | 341.8 | 227.1 | 206.7 | 200.7 | 210.3 | 218.1 | 200.5 | 210.7 | 214.1
2852.1 | 2631.1 | -6.6 | 0 | 0 | 223.6 | 206.5 | 194.8 | 195.8 | 228 | 38.6 | 19.5 | 62.7 | 3.2 | 274.3 | 2.5 | 442.3 | 450.5 | 191.7 | 67.7 | 531.7 | 534.7 | 110.3 | 80.3 | 233.6 | 502.1 | 254.5 | 268.3 | 429 | 257.1 | 235.6 | 545.7 | 341.5 | 226.9 | 206.6 | 200.6 | 210.1 | 218 | 200.4 | 210.5 | 214
2853.1 | 2632.1 | -6.4 | 0 | 0 | 223.5 | 206.5 | 194.7 | 195.7 | 227.9 | 38.6 | 19.5 | 62.6 | 3 | 262.9 | 2.5 | 442.3 | 450.6 | 190.2 | 67.9 | 531.6 | 534.7 | 110.4 | 80.3 | 233.6 | 501.9 | 254 | 267.8 | 428.8 | 257 | 235.2 | 545.7 | 341.3 | 226.8 | 206.5 | 200.5 | 210 | 217.8 | 200.3 | 210.4 | 213.8
2854.1 | 2633.1 | -6.7 | 0 | 0 | 223.4 | 206.4 | 194.5 | 195.5 | 227.7 | 38.6 | 19.5 | 62.5 | 3 | 251.1 | 2.4 | 442.3 | 450.7 | 189.8 | 67.9 | 531.6 | 534.7 | 110.7 | 80.4 | 233.6 | 501.6 | 254.4 | 267.3 | 428.6 | 256.6 | 235.2 | 545.7 | 341.1 | 226.7 | 206.4 | 200.5 | 209.9 | 217.7 | 200.2 | 210.3 | 213.7
2855.1 | 2634.1 | -6.7 | 0 | 0 | 223.3 | 206.3 | 194.3 | 195.4 | 227.4 | 38.6 | 19.5 | 62.4 | 3.1 | 251 | 2.3 | 442.2 | 450.6 | 189.2 | 67.8 | 531.5 | 534.7 | 110.8 | 80.3 | 233.6 | 501.3 | 254 | 267.1 | 428.3 | 256.2 | 234.8 | 545.7 | 340.9 | 226.5 | 206.4 | 200.4 | 209.8 | 217.6 | 200 | 210.3 | 213.6
2856.1 | 2635.1 | -6.3 | 0 | 0 | 223.3 | 206.3 | 194.3 | 195.2 | 227.4 | 38.6 | 19.5 | 62.4 | 3 | 250.9 | 2.3 | 442.2 | 450.4 | 189.8 | 67.7 | 531.5 | 534.6 | 111 | 80.2 | 233.6 | 501.1 | 253.5 | 266.8 | 428.1 | 256 | 235 | 545.6 | 340.6 | 226.4 | 206.3 | 200.3 | 209.7 | 217.5 | 199.9 | 210.3 | 213.5
2857.1 | 2636.1 | -6 | 0 | 0 | 223.1 | 206.1 | 194.2 | 195.2 | 227.1 | 38.5 | 19.5 | 62.3 | 3.3 | 249.5 | 2.3 | 442.2 | 450.3 | 188.9 | 67.7 | 531.4 | 534.5 | 112 | 80 | 233.4 | 500.8 | 253.5 | 266.5 | 427.9 | 256.4 | 235 | 545.5 | 340.5 | 226.3 | 206.2 | 200.2 | 209.5 | 217.4 | 199.8 | 210.2 | 213.3
2858.1 | 2637.1 | -6.1 | 0 | 0 | 223 | 206 | 193.9 | 195.1 | 226.8 | 38.5 | 19.5 | 62.3 | 3.1 | 249.4 | 2.3 | 442.2 | 450.3 | 187.6 | 67.6 | 531.4 | 534.4 | 113.6 | 80 | 233.5 | 500.6 | 253.9 | 266.1 | 427.6 | 257.4 | 234.4 | 545.5 | 340.2 | 226.2 | 206.1 | 200.1 | 209.4 | 217.2 | 199.7 | 210.1 | 213.2
2859.1 | 2638.1 | -6.5 | 0 | 0 | 222.9 | 206 | 193.6 | 194.9 | 226.7 | 38.5 | 19.5 | 62.2 | 2.9 | 249.6 | 2.5 | 442.2 | 450.3 | 187.2 | 67.6 | 531.3 | 534.4 | 114.8 | 80 | 233.5 | 500.3 | 253.6 | 266 | 427.4 | 258 | 233.5 | 545.7 | 340 | 226.1 | 205.9 | 200 | 209.3 | 217.1 | 199.6 | 209.9 | 213.1
2860.1 | 2639.1 | -6.7 | 0 | 0 | 222.6 | 205.9 | 193.6 | 194.8 | 226.7 | 38.5 | 19.5 | 62.2 | 3.3 | 255.1 | 2.7 | 442.1 | 450.5 | 186.2 | 67.8 | 531.2 | 534.4 | 115.8 | 79.9 | 233.5 | 500.1 | 253.1 | 265.8 | 427.2 | 258.2 | 232.7 | 545.7 | 339.7 | 225.9 | 205.8 | 199.9 | 209.2 | 217 | 199.5 | 209.8 | 213
2861.1 | 2640.1 | -6.7 | 0 | 0 | 222.3 | 205.8 | 193.5 | 194.6 | 226.4 | 38.5 | 19.5 | 62.2 | 3 | 261.8 | 3 | 442.1 | 450.4 | 185.7 | 67.8 | 531.1 | 534.4 | 117.4 | 80 | 233.4 | 500 | 253.6 | 265.5 | 426.9 | 257.1 | 232.5 | 545.7 | 339.5 | 225.8 | 205.7 | 199.8 | 209.1 | 216.9 | 199.4 | 209.6 | 212.9
2862.1 | 2641.1 | -6.7 | 0 | 0 | 221.9 | 205.7 | 193.4 | 194.5 | 226.2 | 38.5 | 19.5 | 62.2 | 3.2 | 255 | 3 | 442.1 | 450.2 | 187.2 | 67.8 | 531.1 | 534.5 | 117.6 | 79.8 | 233.4 | 499.8 | 253 | 265.4 | 426.7 | 255.7 | 232.5 | 545.7 | 339.4 | 225.7 | 205.5 | 199.7 | 209 | 216.8 | 199.2 | 209.4 | 212.7
2863.1 | 2642.1 | -6.7 | 0 | 0 | 221.6 | 205.6 | 193.4 | 194.4 | 225.7 | 38.4 | 19.5 | 62.2 | 3 | 244.2 | 3 | 442.1 | 450.1 | 188.9 | 68.1 | 531 | 534.5 | 118.2 | 79.8 | 233.4 | 499.7 | 252 | 265.5 | 426.5 | 256.4 | 232.4 | 545.5 | 339.2 | 225.6 | 205.4 | 199.5 | 208.9 | 216.7 | 199 | 209.2 | 212.6
2864.1 | 2643.1 | -6.7 | 0 | 0 | 221.5 | 205.5 | 193.4 | 194.3 | 225.8 | 38.4 | 19.5 | 62.2 | 3 | 243.6 | 3.1 | 442 | 450.2 | 190.4 | 68.3 | 531 | 534.5 | 118.7 | 80 | 233.4 | 499.5 | 251.6 | 265.1 | 426.2 | 255.9 | 231.9 | 545.4 | 338.9 | 225.5 | 205.3 | 199.4 | 208.8 | 216.5 | 198.9 | 209 | 212.5
2865.1 | 2644.1 | -6.7 | 0 | 0 | 221.4 | 205.4 | 193.3 | 194.4 | 226.2 | 38.4 | 19.5 | 62.2 | 3 | 246.5 | 3.4 | 442 | 450.2 | 190.7 | 68.5 | 530.9 | 534.4 | 118.8 | 80.1 | 233.4 | 499.3 | 251 | 264.7 | 426 | 255.1 | 231.8 | 545.4 | 338.7 | 225.3 | 205.2 | 199.4 | 208.7 | 216.4 | 198.7 | 208.9 | 212.4
2866.1 | 2645.1 | -6.7 | 0 | 0 | 221.1 | 205.3 | 193.2 | 194.3 | 225.8 | 38.5 | 19.5 | 62.2 | 3.3 | 259.4 | 3.7 | 442 | 450.2 | 191.1 | 68.5 | 530.9 | 534.6 | 119 | 80.1 | 233.4 | 499.2 | 251 | 264.8 | 425.8 | 254 | 232.1 | 545.4 | 338.6 | 225.2 | 205.1 | 199.3 | 208.6 | 216.3 | 198.6 | 208.9 | 212.3
2867.1 | 2646.1 | -6.7 | 0 | 0 | 220.8 | 205.2 | 193.1 | 194.3 | 225.4 | 38.5 | 19.5 | 62.1 | 3.3 | 272.6 | 3.8 | 442 | 450.1 | 190.6 | 68.5 | 530.9 | 534.8 | 119.8 | 80 | 233.3 | 499 | 250.2 | 264.5 | 425.6 | 252.4 | 232.2 | 545.3 | 338.5 | 225.1 | 205 | 199.2 | 208.5 | 216.2 | 198.5 | 208.8 | 212.1
2868.1 | 2647.1 | -6.7 | 0 | 0 | 220.6 | 205.1 | 192.9 | 194.3 | 225.3 | 38.6 | 19.5 | 62.1 | 3.2 | 271.8 | 3.9 | 441.9 | 450.1 | 191.1 | 68.5 | 530.9 | 534.9 | 120.5 | 79.9 | 233 | 498.8 | 250.1 | 264.6 | 425.4 | 252 | 232.6 | 545.2 | 338.5 | 225 | 204.9 | 199.1 | 208.4 | 216.1 | 198.4 | 208.7 | 212
2869.1 | 2648.1 | -6.7 | 0 | 0 | 220.4 | 205 | 192.7 | 194.2 | 225.2 | 38.6 | 19.5 | 62.1 | 3.2 | 270.3 | 3.8 | 441.9 | 450 | 190.9 | 68.4 | 530.8 | 535 | 121 | 79.6 | 232.7 | 498.6 | 249.7 | 264.6 | 425.2 | 251.9 | 232.9 | 545 | 338.3 | 224.8 | 204.7 | 198.9 | 208.2 | 216 | 198.3 | 208.5 | 211.9
2870.1 | 2649.1 | -6.7 | 0 | 0 | 220.3 | 205 | 192.6 | 194.1 | 225.3 | 38.6 | 19.5 | 62.1 | 3.5 | 270.1 | 3.7 | 441.9 | 449.9 | 190.1 | 68.4 | 530.8 | 535.1 | 122.4 | 79.5 | 232.8 | 498.4 | 249.8 | 264.7 | 425 | 252.1 | 232.6 | 544.8 | 338.2 | 224.7 | 204.6 | 198.8 | 208.1 | 215.9 | 198.2 | 208.4 | 211.8
2871.1 | 2650.1 | -6.7 | 0 | 0 | 220 | 204.9 | 192.5 | 193.9 | 225.4 | 38.5 | 19.5 | 62 | 3.8 | 269.5 | 3.8 | 441.9 | 449.8 | 189.4 | 68.3 | 530.8 | 535.2 | 123.7 | 79.3 | 232.6 | 498.2 | 250.1 | 264.8 | 424.8 | 252.3 | 232.6 | 544.7 | 338 | 224.6 | 204.5 | 198.7 | 208 | 215.8 | 198.1 | 208.4 | 211.7
2872.1 | 2651.1 | -6.7 | 0 | 0 | 219.9 | 204.9 | 192.3 | 193.7 | 225.1 | 38.5 | 19.6 | 62 | 3.7 | 269 | 3.5 | 441.8 | 449.6 | 188.5 | 68.1 | 530.8 | 535.4 | 125.1 | 79.1 | 232.5 | 498 | 251.1 | 264.6 | 424.6 | 252.4 | 232.1 | 544.6 | 338 | 224.5 | 204.4 | 198.6 | 207.9 | 215.7 | 198 | 208.2 | 211.5
2873.1 | 2652.1 | -6.7 | 0 | 0 | 219.8 | 204.9 | 192.1 | 193.6 | 224.9 | 38.5 | 19.6 | 62 | 3.6 | 262.7 | 3.1 | 441.8 | 449.6 | 187.4 | 68 | 530.8 | 535.4 | 124.7 | 79 | 232.2 | 497.8 | 250.4 | 264.5 | 424.4 | 252.4 | 231.8 | 544.6 | 337.7 | 224.4 | 204.3 | 198.5 | 207.8 | 215.6 | 197.9 | 208.1 | 211.4
2874.1 | 2653.1 | -6.7 | 0 | 0 | 219.6 | 204.8 | 191.9 | 193.4 | 224.6 | 38.5 | 19.6 | 62.1 | 3.5 | 256.6 | 3.1 | 441.8 | 449.7 | 187.1 | 67.9 | 530.8 | 535.5 | 126.7 | 79 | 232 | 497.6 | 249.8 | 264 | 424.2 | 253.4 | 231.5 | 544.5 | 337.6 | 224.2 | 204.2 | 198.4 | 207.7 | 215.5 | 197.7 | 207.9 | 211.3
2875.1 | 2654.1 | -6.7 | 0 | 0 | 219.2 | 204.8 | 191.9 | 193.4 | 224.8 | 38.4 | 19.6 | 62.1 | 3.8 | 259 | 3.3 | 441.8 | 449.8 | 186.9 | 67.9 | 530.8 | 535.7 | 127.3 | 79 | 231.9 | 497.4 | 249.4 | 263.5 | 424 | 253 | 230.3 | 544.4 | 337.4 | 224.1 | 204.1 | 198.2 | 207.6 | 215.4 | 197.6 | 207.8 | 211.2
2876.1 | 2655.1 | -6.7 | 0 | 0 | 219 | 204.8 | 191.8 | 193.4 | 225 | 38.4 | 19.6 | 62.1 | 3.8 | 256.5 | 3.4 | 441.7 | 449.8 | 186.4 | 67.9 | 530.8 | 535.8 | 127.7 | 79 | 231.6 | 497.2 | 249 | 262.9 | 423.8 | 252.7 | 230.3 | 544.3 | 337.3 | 224 | 204 | 198.1 | 207.4 | 215.2 | 197.5 | 207.6 | 211.1
2877.1 | 2656.1 | -6.7 | 0 | 0 | 219 | 204.7 | 191.8 | 193.2 | 224.8 | 38.4 | 19.6 | 62.1 | 3.4 | 250 | 3.7 | 441.7 | 449.6 | 185.4 | 67.9 | 530.8 | 535.8 | 128.4 | 79 | 231.7 | 496.9 | 248.8 | 263.1 | 423.6 | 253.6 | 230.7 | 544.2 | 337.2 | 223.9 | 203.9 | 198.2 | 207.4 | 215.1 | 197.4 | 207.6 | 211
2878.1 | 2657.1 | -6.7 | 0 | 0 | 218.8 | 204.6 | 191.7 | 193 | 224.6 | 38.4 | 19.6 | 62.1 | 2.9 | 258.6 | 4.1 | 441.7 | 449.6 | 185.2 | 67.8 | 530.8 | 535.9 | 128.1 | 79.2 | 231.6 | 496.7 | 248.8 | 262.6 | 423.3 | 253.4 | 230.7 | 544.1 | 336.9 | 223.7 | 203.8 | 198.1 | 207.2 | 215 | 197.3 | 207.6 | 210.8
2879.1 | 2658.1 | -6.1 | 0 | 0 | 218.6 | 204.4 | 191.6 | 192.8 | 224.3 | 38.3 | 19.6 | 62.1 | 3.3 | 267.4 | 4.1 | 441.7 | 449.5 | 185 | 67.9 | 530.9 | 535.9 | 127.9 | 79.4 | 231.5 | 496.5 | 248.7 | 261.3 | 423.1 | 253.5 | 230.9 | 544.2 | 336.8 | 223.6 | 203.6 | 198 | 207.1 | 214.9 | 197.2 | 207.4 | 210.7
2880.1 | 2659.1 | -5.4 | 0 | 0 | 218.5 | 204.3 | 191.5 | 192.6 | 223.9 | 38.3 | 19.6 | 62 | 3.4 | 265.8 | 4.3 | 441.6 | 449.4 | 185.3 | 68 | 530.9 | 535.8 | 127.9 | 79.7 | 231.7 | 496.3 | 248.2 | 261.1 | 422.9 | 254 | 231.3 | 544.2 | 336.6 | 223.5 | 203.4 | 197.9 | 207 | 214.8 | 197.1 | 207.3 | 210.6
2881.1 | 2660.1 | -4.8 | 0 | 0 | 218.1 | 204.2 | 191.5 | 192.6 | 223.5 | 38.3 | 19.6 | 62 | 3.1 | 256.4 | 4.4 | 441.6 | 449.5 | 184.3 | 68.1 | 530.9 | 535.6 | 128.6 | 79.8 | 231.7 | 496.1 | 247.9 | 260.9 | 422.7 | 252.9 | 230.4 | 544.2 | 336.3 | 223.4 | 203.3 | 197.8 | 206.9 | 214.7 | 196.9 | 207.1 | 210.5
2882.1 | 2661.1 | -4.7 | 0 | 0 | 217.8 | 204.2 | 191.3 | 192.5 | 223.5 | 38.2 | 19.6 | 62 | 3.4 | 255.2 | 4.7 | 441.6 | 449.5 | 183.6 | 68.1 | 530.9 | 535.5 | 128.9 | 80.1 | 231.7 | 495.9 | 248.3 | 260.8 | 422.5 | 252 | 229.1 | 544.2 | 336 | 223.3 | 203.1 | 197.7 | 206.8 | 214.6 | 196.8 | 206.9 | 210.4
2883.1 | 2662.1 | -6 | 0 | 0 | 217.8 | 204.2 | 191.1 | 192.4 | 223.6 | 38.2 | 19.6 | 62 | 3 | 257.3 | 4.5 | 441.6 | 449.7 | 185 | 68.1 | 530.9 | 535.3 | 129 | 80.2 | 231.9 | 495.7 | 248.9 | 261.2 | 422.2 | 250.8 | 227.5 | 544.3 | 335.8 | 223.1 | 203 | 197.5 | 206.7 | 214.5 | 196.8 | 206.8 | 210.2
2884.1 | 2663.1 | -6.5 | 0 | 0 | 217.7 | 204.2 | 191 | 192.3 | 223.7 | 38.2 | 19.6 | 62 | 2.8 | 256.7 | 4.5 | 441.5 | 449.6 | 184.7 | 67.9 | 530.9 | 535.2 | 129.3 | 80.1 | 231.8 | 495.5 | 249 | 261.4 | 422 | 249.6 | 226.5 | 544.3 | 335.6 | 223 | 202.9 | 197.4 | 206.6 | 214.4 | 197 | 206.7 | 210.1
2885.1 | 2664.1 | -6.5 | 0 | 0 | 217.6 | 204.1 | 190.9 | 192.2 | 223.7 | 38.2 | 19.6 | 62 | 3.3 | 258.2 | 4.2 | 441.5 | 449.5 | 183.6 | 67.8 | 530.9 | 535.1 | 129.4 | 80.1 | 231.7 | 495.4 | 249.9 | 261.4 | 421.8 | 248.8 | 225.9 | 544.3 | 335.4 | 222.9 | 202.8 | 197.3 | 206.5 | 214.3 | 196.9 | 206.6 | 210
2886.1 | 2665.1 | -6.6 | 0 | 0 | 217.5 | 203.9 | 190.7 | 192.1 | 223.6 | 38.1 | 19.6 | 62 | 3.2 | 258.5 | 4.1 | 441.5 | 449.2 | 182.1 | 67.6 | 530.9 | 535 | 128.8 | 80.1 | 231.7 | 495.2 | 250.8 | 261.6 | 421.6 | 248 | 225.2 | 544.3 | 335 | 222.8 | 202.7 | 197.1 | 206.3 | 214.2 | 196.7 | 206.7 | 209.9
2887.1 | 2666.1 | -6.5 | 0 | 0 | 217.4 | 203.9 | 190.5 | 192.1 | 223.2 | 38.1 | 19.6 | 62 | 3 | 253.2 | 4.1 | 441.5 | 449.1 | 182 | 67.4 | 530.8 | 535 | 128.5 | 80.3 | 231.6 | 495.1 | 250.4 | 261.5 | 421.4 | 246.7 | 225.3 | 544.2 | 334.8 | 222.7 | 202.6 | 197 | 206.2 | 214 | 196.7 | 206.6 | 209.8
2888.1 | 2667.1 | -6.4 | 0 | 0 | 217.2 | 203.8 | 190.4 | 192.1 | 222.6 | 38.1 | 19.6 | 62 | 3.5 | 236.2 | 3.9 | 441.4 | 449.1 | 181.3 | 67.4 | 530.9 | 534.9 | 129.1 | 80.4 | 231.5 | 494.9 | 250 | 261.4 | 421.2 | 245.6 | 225.1 | 544.1 | 334.7 | 222.6 | 202.5 | 196.9 | 206.1 | 213.9 | 196.5 | 206.5 | 209.7
2889.1 | 2668.1 | -6.6 | 0 | 0 | 217.2 | 203.7 | 190.3 | 192 | 222.4 | 38.1 | 19.6 | 62 | 3.4 | 242.8 | 3.8 | 441.4 | 449.1 | 181.6 | 67.4 | 530.8 | 534.8 | 129.3 | 80.5 | 231.5 | 494.7 | 249.1 | 260.8 | 421 | 245.3 | 224.5 | 543.9 | 334.5 | 222.4 | 202.3 | 196.8 | 206 | 213.8 | 196.4 | 206.3 | 209.6
2890.1 | 2669.1 | -6.7 | 0 | 0 | 217.2 | 203.6 | 190.2 | 191.7 | 222.1 | 38.1 | 19.6 | 62 | 3.2 | 255.3 | 4.7 | 441.4 | 449.2 | 180.1 | 67.3 | 530.8 | 534.7 | 129.1 | 80.7 | 231.5 | 494.5 | 248.3 | 260.6 | 420.8 | 245.4 | 224.3 | 543.7 | 334.3 | 222.3 | 202.2 | 196.7 | 205.9 | 213.7 | 196.3 | 206.2 | 209.4
2891.1 | 2670.1 | -6.5 | 0 | 0 | 217 | 203.5 | 190.1 | 191.5 | 221.7 | 38.1 | 19.6 | 62 | 3 | 247.8 | 5.1 | 441.4 | 449.3 | 180.5 | 67.3 | 530.8 | 534.7 | 128.9 | 80.7 | 231.4 | 494.3 | 247.7 | 260.3 | 420.6 | 245.1 | 223.3 | 543.6 | 334.1 | 222.1 | 202 | 196.5 | 205.8 | 213.6 | 196.2 | 206.1 | 209.3
2892.1 | 2671.1 | -5.8 | 0 | 0 | 217 | 203.4 | 190 | 191.4 | 221.6 | 38.1 | 19.6 | 62 | 2.9 | 248.4 | 5.3 | 441.3 | 449.3 | 180.9 | 67.3 | 530.8 | 534.6 | 128.3 | 80.8 | 231.4 | 494.1 | 247.9 | 260 | 420.4 | 245.2 | 223.5 | 543.5 | 334 | 222 | 201.9 | 196.3 | 205.6 | 213.5 | 196.1 | 206 | 209.2
2893.1 | 2672.1 | -5.6 | 0 | 0 | 216.9 | 203.3 | 189.9 | 191.2 | 221.5 | 38.1 | 19.6 | 62 | 3.4 | 256.1 | 5.7 | 441.3 | 449.3 | 180.7 | 67.2 | 530.8 | 534.5 | 127.5 | 81 | 231.3 | 493.9 | 247.3 | 259.7 | 420.1 | 245.4 | 224.2 | 543.5 | 333.8 | 221.9 | 201.7 | 196.2 | 205.5 | 213.4 | 196 | 205.9 | 209.1
2894.1 | 2673.1 | -5.4 | 0 | 0 | 216.8 | 203.2 | 189.7 | 191 | 221.5 | 38.1 | 19.6 | 62 | 3.3 | 258.9 | 5.3 | 441.3 | 449.4 | 180.5 | 67.2 | 530.8 | 534.4 | 127.2 | 80.9 | 231.3 | 493.6 | 247 | 259.8 | 419.9 | 245.5 | 224.6 | 543.4 | 333.6 | 221.8 | 201.6 | 196.1 | 205.4 | 213.3 | 195.9 | 205.7 | 209
2895.1 | 2674.1 | -6.1 | 0 | 0 | 216.5 | 203.1 | 189.6 | 190.8 | 221.3 | 38.1 | 19.6 | 62 | 3.5 | 247.9 | 5.3 | 441.3 | 449.2 | 180.6 | 67.1 | 530.8 | 534.2 | 126.3 | 80.8 | 231.2 | 493.4 | 247.2 | 259.8 | 419.7 | 245.5 | 224.8 | 543.3 | 333.5 | 221.7 | 201.5 | 196 | 205.3 | 213.2 | 195.8 | 205.6 | 208.8
2896.1 | 2675.1 | -6.7 | 0 | 0 | 216.2 | 202.9 | 189.6 | 190.7 | 221.2 | 38.1 | 19.6 | 62 | 3.2 | 241.1 | 5.5 | 441.2 | 449.1 | 181.7 | 67 | 530.8 | 534 | 125 | 80.8 | 231.1 | 493.3 | 247.1 | 258.7 | 419.5 | 245.2 | 225 | 543.1 | 333.3 | 221.5 | 201.3 | 195.9 | 205.2 | 213.1 | 195.6 | 205.4 | 208.7
2897.1 | 2676.1 | -6.7 | 0 | 0 | 216.1 | 202.8 | 189.6 | 190.7 | 221.2 | 38.1 | 19.6 | 62 | 3.2 | 246.8 | 5.3 | 441.2 | 449.1 | 181.2 | 66.8 | 530.9 | 533.9 | 124.4 | 80.7 | 231 | 493 | 247.6 | 258.5 | 419.3 | 245 | 225.3 | 542.8 | 333.1 | 221.4 | 201.2 | 195.8 | 205.1 | 213 | 195.5 | 205.3 | 208.6
2898.1 | 2677.1 | -6.7 | 0 | 0 | 215.9 | 202.7 | 189.5 | 190.6 | 221.4 | 38.1 | 19.6 | 62 | 3 | 250.2 | 5 | 441.2 | 449.1 | 180.7 | 66.8 | 530.9 | 533.7 | 123.8 | 80.8 | 230.8 | 492.8 | 246.8 | 258.1 | 419.1 | 244.9 | 225.9 | 542.6 | 333.1 | 221.3 | 201.1 | 195.7 | 205 | 212.9 | 195.4 | 205.2 | 208.5
2899.1 | 2678.1 | -6.4 | 0 | 0 | 215.7 | 202.7 | 189.5 | 190.5 | 221.2 | 38.1 | 19.6 | 62 | 3.4 | 251.1 | 4.7 | 441.2 | 449 | 180.5 | 66.8 | 531 | 533.7 | 122.8 | 80.9 | 230.8 | 492.6 | 246.5 | 257.9 | 418.9 | 244.9 | 226.2 | 542.5 | 332.9 | 221.2 | 201 | 195.6 | 204.9 | 212.8 | 195.3 | 205.2 | 208.4
2900.1 | 2679.1 | -6.5 | 0 | 0 | 215.7 | 202.7 | 189.4 | 190.5 | 221.2 | 38.1 | 19.6 | 62 | 3.5 | 252.8 | 4.5 | 441.2 | 448.9 | 180.6 | 66.7 | 531 | 533.6 | 122.1 | 80.9 | 230.6 | 492.5 | 245.9 | 257.8 | 418.6 | 245.3 | 226.7 | 542.5 | 332.7 | 221 | 200.9 | 195.5 | 204.8 | 212.6 | 195.2 | 205 | 208.3
2901.1 | 2680.1 | -6 | 0 | 0 | 215.7 | 202.6 | 189.5 | 190.5 | 221.3 | 38.1 | 19.6 | 61.9 | 3.1 | 254.9 | 4.5 | 441.1 | 448.9 | 179.8 | 66.6 | 531.1 | 533.5 | 121.3 | 80.8 | 230.5 | 492.3 | 246 | 257.7 | 418.4 | 245.9 | 226 | 542.5 | 332.7 | 220.9 | 200.8 | 195.4 | 204.7 | 212.5 | 195 | 204.9 | 208.1
2902.1 | 2681.1 | -4.8 | 0 | 0 | 215.6 | 202.5 | 189.4 | 190.5 | 221.1 | 38.1 | 19.6 | 61.9 | 3.2 | 255 | 4.4 | 441.1 | 448.7 | 181.9 | 66.6 | 531.1 | 533.4 | 120.3 | 80.6 | 230.4 | 492.1 | 246.4 | 257.6 | 418.2 | 245.6 | 225.5 | 542.3 | 332.5 | 220.8 | 200.7 | 195.3 | 204.6 | 212.4 | 194.9 | 204.8 | 208
2903.1 | 2682.1 | -3.9 | 0 | 0 | 215.5 | 202.3 | 189.2 | 190.4 | 221 | 38.1 | 19.6 | 61.8 | 3.1 | 253 | 4.3 | 441.1 | 448.6 | 182.9 | 66.5 | 531.2 | 533.4 | 119.8 | 80.3 | 230.2 | 491.9 | 245.9 | 256.6 | 418 | 245.2 | 225.6 | 542.2 | 332.3 | 220.6 | 200.6 | 195.2 | 204.4 | 212.3 | 194.7 | 204.6 | 207.9
2904.1 | 2683.1 | -4.4 | 0 | 0 | 215.2 | 202.2 | 188.9 | 190.2 | 220.8 | 38.2 | 19.6 | 61.8 | 3.1 | 256.3 | 4.1 | 441.1 | 448.4 | 183.4 | 66.4 | 531.2 | 533.3 | 119.3 | 80.1 | 230.1 | 491.7 | 245.5 | 256.1 | 417.8 | 244.9 | 225.6 | 542.1 | 332.1 | 220.5 | 200.5 | 195.1 | 204.3 | 212.2 | 194.6 | 204.6 | 207.8
2905.1 | 2684.1 | -4.4 | 0 | 0 | 215 | 202.1 | 188.7 | 190 | 220.4 | 38.2 | 19.6 | 61.7 | 3.1 | 254.9 | 4.1 | 441.1 | 448.1 | 183 | 66.4 | 531.2 | 533.2 | 118.8 | 80 | 229.9 | 491.5 | 245.7 | 255.9 | 417.5 | 244.7 | 224.2 | 542 | 332 | 220.4 | 200.5 | 195 | 204.2 | 212 | 194.5 | 204.5 | 207.7
2906.1 | 2685.1 | -5.2 | 0 | 0 | 214.9 | 202 | 188.6 | 189.9 | 220.2 | 38.2 | 19.6 | 61.7 | 2.9 | 254.5 | 4.1 | 441 | 448 | 182.8 | 66.4 | 531.2 | 533 | 118.1 | 80 | 229.8 | 491.2 | 245.3 | 254.9 | 417.3 | 244.8 | 222.3 | 542 | 331.9 | 220.3 | 200.4 | 194.9 | 204.1 | 211.9 | 194.4 | 204.4 | 207.5
2907.1 | 2686.1 | -5.8 | 0 | 0 | 214.9 | 202 | 188.5 | 189.8 | 220 | 38.2 | 19.6 | 61.7 | 3.1 | 255 | 3.9 | 441 | 447.9 | 183.5 | 66.4 | 531.3 | 532.9 | 117 | 80.1 | 229.7 | 491 | 244.7 | 254.3 | 417.1 | 244.8 | 221 | 541.9 | 331.6 | 220.1 | 200.2 | 194.8 | 204 | 211.8 | 194.2 | 204.2 | 207.4
2908.1 | 2687.1 | -5.8 | 0 | 0 | 214.9 | 202 | 188.3 | 189.8 | 219.9 | 38.2 | 19.6 | 61.7 | 3.1 | 255.8 | 4 | 441 | 447.8 | 183.7 | 66.5 | 531.3 | 532.7 | 116 | 80.2 | 229.7 | 490.9 | 245 | 253.7 | 416.9 | 245.2 | 220.2 | 541.9 | 331.1 | 220 | 200.1 | 194.7 | 203.9 | 211.7 | 194.1 | 204.1 | 207.3
2909.1 | 2688.1 | -5.6 | 0 | 0 | 214.7 | 201.9 | 188.3 | 189.6 | 219.6 | 38.1 | 19.6 | 61.7 | 3 | 254.2 | 4.3 | 441 | 447.7 | 183.6 | 66.5 | 531.3 | 532.6 | 115 | 80.1 | 229.6 | 490.7 | 245 | 253.8 | 416.7 | 245.1 | 220.5 | 541.7 | 330.7 | 219.9 | 200 | 194.6 | 203.7 | 211.6 | 194 | 204 | 207.2
2910.1 | 2689.1 | -6.2 | 0 | 0 | 214.5 | 201.9 | 188.3 | 189.4 | 219.3 | 38.1 | 19.6 | 61.6 | 2.7 | 253.1 | 4.7 | 440.9 | 447.7 | 183.2 | 66.5 | 531.4 | 532.4 | 114.3 | 80.1 | 229.6 | 490.5 | 245.4 | 253.7 | 416.5 | 244.3 | 220.9 | 541.8 | 330.6 | 219.8 | 200 | 194.5 | 203.6 | 211.5 | 193.9 | 204 | 207.1
2911.1 | 2690.1 | -6.7 | 0 | 0 | 214.3 | 201.8 | 188.2 | 189.3 | 219.1 | 38.1 | 19.6 | 61.6 | 3 | 251.3 | 4.9 | 440.9 | 447.7 | 184.1 | 66.6 | 531.4 | 532.3 | 113.3 | 80.1 | 229.5 | 490.3 | 245 | 253.5 | 416.3 | 244 | 221.1 | 541.9 | 330.4 | 219.7 | 199.9 | 194.4 | 203.5 | 211.4 | 193.8 | 203.9 | 207
2912.1 | 2691.1 | -6.7 | 0 | 0 | 214.2 | 201.7 | 188.2 | 189.3 | 219 | 38 | 19.6 | 61.6 | 3 | 249.5 | 4.9 | 440.9 | 447.7 | 184.2 | 66.7 | 531.4 | 532.2 | 112.2 | 80.2 | 229.5 | 490.1 | 244.9 | 253.8 | 416.1 | 243.2 | 221.2 | 541.8 | 330.4 | 219.6 | 199.8 | 194.3 | 203.4 | 211.3 | 193.7 | 203.7 | 206.8
2913.1 | 2692.1 | -6.7 | 0 | 0 | 214.3 | 201.6 | 188.1 | 189.3 | 219.1 | 38 | 19.6 | 61.5 | 2.7 | 240.6 | 4.9 | 440.9 | 447.7 | 183.5 | 66.8 | 531.4 | 532.1 | 110.8 | 80.2 | 229.5 | 490 | 244.8 | 253.5 | 415.8 | 242.7 | 220.9 | 541.7 | 330.2 | 219.5 | 199.7 | 194.2 | 203.3 | 211.2 | 193.6 | 203.6 | 206.7
2914.1 | 2693.1 | -6.5 | 0 | 0 | 214.3 | 201.4 | 188 | 189.3 | 219.3 | 38 | 19.6 | 61.5 | 2.8 | 236.3 | 4.9 | 440.9 | 447.6 | 183.4 | 66.7 | 531.4 | 531.9 | 110 | 80.2 | 229.6 | 489.8 | 244.9 | 253.2 | 415.6 | 242.2 | 221.3 | 541.6 | 330 | 219.4 | 199.6 | 194 | 203.2 | 211 | 193.5 | 203.5 | 206.6
2915.1 | 2694.1 | -6.6 | 0 | 0 | 214.2 | 201.2 | 187.9 | 189.2 | 219 | 38 | 19.6 | 61.4 | 3 | 237.5 | 4.8 | 440.8 | 447.6 | 183.3 | 66.7 | 531.4 | 531.8 | 109.5 | 80.3 | 229.5 | 489.6 | 244.9 | 252.8 | 415.4 | 241.5 | 221.3 | 541.5 | 329.9 | 219.3 | 199.5 | 194 | 203.1 | 210.9 | 193.4 | 203.4 | 206.5
2916.1 | 2695.1 | -6.4 | 0 | 0 | 213.9 | 201 | 187.9 | 189.1 | 218.6 | 38 | 19.6 | 61.4 | 2.8 | 239.7 | 4.6 | 440.8 | 447.5 | 183.5 | 66.5 | 531.4 | 531.8 | 109.1 | 80.1 | 229.4 | 489.5 | 244.5 | 252 | 415.2 | 240.9 | 220.1 | 541.4 | 329.7 | 219.1 | 199.4 | 193.8 | 203 | 210.8 | 193.3 | 203.2 | 206.4
2917.1 | 2696.1 | -6.2 | 0 | 0 | 213.7 | 200.9 | 187.8 | 189.1 | 218.5 | 37.9 | 19.6 | 61.4 | 2.9 | 241.4 | 4.6 | 440.8 | 447.5 | 182.7 | 66.3 | 531.4 | 531.9 | 108.9 | 80 | 229.4 | 489.2 | 243.9 | 250.7 | 415 | 240.1 | 219 | 541.2 | 329.5 | 219 | 199.2 | 193.7 | 202.8 | 210.6 | 193.2 | 203 | 206.3
2918.1 | 2697.1 | -6.5 | 0 | 0 | 213.5 | 200.9 | 187.7 | 188.9 | 218.7 | 37.9 | 19.6 | 61.4 | 3 | 240.3 | 4.5 | 440.8 | 447.3 | 183.6 | 66.3 | 531.4 | 532 | 108.8 | 79.8 | 229.3 | 489 | 243.6 | 249.3 | 414.8 | 240.3 | 218 | 541.2 | 329.3 | 218.9 | 199 | 193.5 | 202.7 | 210.5 | 193.1 | 202.9 | 206.1
2919.1 | 2698.1 | -6.5 | 0 | 0 | 213.4 | 200.8 | 187.4 | 188.9 | 218.8 | 37.8 | 19.6 | 61.4 | 3 | 238.9 | 4.3 | 440.8 | 447.3 | 182.7 | 66.2 | 531.4 | 532 | 108.8 | 79.7 | 229.2 | 488.8 | 243.1 | 248.9 | 414.6 | 239.9 | 217.9 | 541.2 | 328.9 | 218.8 | 198.9 | 193.4 | 202.6 | 210.4 | 193 | 202.7 | 206
2920.1 | 2699.1 | -6.6 | 0 | 0 | 213.4 | 200.7 | 187.4 | 188.7 | 218.7 | 37.8 | 19.6 | 61.3 | 3.1 | 243.4 | 4 | 440.7 | 447.2 | 183 | 66.2 | 531.3 | 532.1 | 108.5 | 79.5 | 229.1 | 488.6 | 243 | 248.4 | 414.3 | 239.2 | 218.4 | 541.1 | 328.7 | 218.7 | 198.8 | 193.3 | 202.5 | 210.3 | 192.9 | 202.6 | 205.9
2921.1 | 2700.1 | -6.7 | 0 | 0 | 213.4 | 200.5 | 187.3 | 188.6 | 218.5 | 37.8 | 19.7 | 61.2 | 2.8 | 245.3 | 3.7 | 440.7 | 447.2 | 183.1 | 66.1 | 531.3 | 532.1 | 108.4 | 79.3 | 228.9 | 488.5 | 242.6 | 248.2 | 414.1 | 238.9 | 217.8 | 540.9 | 328.6 | 218.6 | 198.7 | 193.2 | 202.4 | 210.2 | 192.8 | 202.5 | 205.8
2922.1 | 2701.1 | -6.7 | 0 | 0 | 213.3 | 200.4 | 187.2 | 188.5 | 218.2 | 37.7 | 19.7 | 61.2 | 2.8 | 245.6 | 3.5 | 440.7 | 447.3 | 183.6 | 66 | 531.3 | 532.1 | 108 | 79.1 | 228.7 | 488.3 | 242.4 | 248 | 413.9 | 238.9 | 217.2 | 540.9 | 328.4 | 218.5 | 198.6 | 193.2 | 202.3 | 210.1 | 192.8 | 202.5 | 205.7
2923.1 | 2702.1 | -6.7 | 0 | 0 | 213.3 | 200.3 | 187.2 | 188.5 | 217.9 | 37.6 | 19.7 | 61.1 | 2.8 | 246 | 3.6 | 440.7 | 447.1 | 183.2 | 65.9 | 531.2 | 532.1 | 107.6 | 79 | 228.6 | 488.1 | 243.1 | 248.1 | 413.7 | 238.5 | 216.9 | 541 | 328.2 | 218.4 | 198.5 | 193.1 | 202.2 | 210 | 192.7 | 202.4 | 205.6
2924.1 | 2703.1 | -6.7 | 0 | 0 | 213.2 | 200.2 | 187.2 | 188.3 | 217.6 | 37.5 | 19.7 | 61.1 | 2.8 | 247.6 | 3.6 | 440.7 | 447.1 | 183.9 | 65.8 | 531.1 | 532 | 107.2 | 78.9 | 228.6 | 487.9 | 243 | 248.3 | 413.4 | 237.9 | 217.1 | 540.8 | 328.1 | 218.2 | 198.4 | 193 | 202.1 | 209.9 | 192.6 | 202.3 | 205.5
2925.1 | 2704.1 | -6.7 | 0 | 0 | 213.2 | 200.1 | 187.2 | 188.1 | 217.7 | 37.4 | 19.7 | 61 | 2.9 | 258.2 | 3.4 | 440.6 | 446.8 | 184.7 | 65.8 | 531.1 | 531.9 | 106.2 | 79 | 228.5 | 487.9 | 243.5 | 248.5 | 413.2 | 236.8 | 216.8 | 540.7 | 327.7 | 218.1 | 198.2 | 192.9 | 202 | 209.7 | 192.5 | 202.2 | 205.4
2926.1 | 2705.1 | -6.7 | 0 | 0 | 213 | 200 | 187 | 188 | 217.8 | 37.4 | 19.7 | 61 | 2.8 | 267.5 | 3.1 | 440.6 | 446.7 | 184.4 | 65.8 | 531.1 | 531.8 | 105.1 | 79 | 228.4 | 487.8 | 243.1 | 248.5 | 413 | 235.6 | 217.2 | 540.6 | 327.6 | 218 | 198 | 192.7 | 201.9 | 209.6 | 192.3 | 202 | 205.2
2927.1 | 2706.1 | -6.7 | 0 | 0 | 212.9 | 199.8 | 186.7 | 187.9 | 218.1 | 37.3 | 19.7 | 61 | 2.6 | 259.8 | 2.9 | 440.6 | 446.9 | 183.9 | 65.8 | 531 | 531.8 | 104.6 | 78.9 | 228.2 | 487.7 | 243.9 | 248.8 | 412.8 | 235 | 217.3 | 540.5 | 327.4 | 217.9 | 197.9 | 192.6 | 201.8 | 209.5 | 192.2 | 201.9 | 205.1
2928.1 | 2707.1 | -6.7 | 0 | 0 | 212.8 | 199.7 | 186.5 | 187.8 | 218.4 | 37.3 | 19.7 | 61 | 2.9 | 252.4 | 2.9 | 440.6 | 446.9 | 183.9 | 65.7 | 531 | 531.7 | 104.5 | 78.9 | 228.1 | 487.5 | 244.1 | 248.8 | 412.6 | 234.9 | 217.2 | 540.5 | 327.3 | 217.7 | 197.8 | 192.5 | 201.6 | 209.4 | 192.1 | 201.8 | 205
2929.1 | 2708.1 | -6.7 | 0 | 0 | 212.6 | 199.5 | 186.3 | 187.7 | 218.2 | 37.4 | 19.7 | 60.9 | 2.9 | 245.2 | 3 | 440.6 | 446.8 | 182.6 | 65.5 | 531 | 531.7 | 104.4 | 78.8 | 228.1 | 487.4 | 243.3 | 248.6 | 412.3 | 234.5 | 217.7 | 540.4 | 327.1 | 217.6 | 197.7 | 192.4 | 201.5 | 209.3 | 191.9 | 201.7 | 204.9
2930.1 | 2709.1 | -6.7 | 0 | 0 | 212.5 | 199.4 | 186.2 | 187.5 | 218 | 37.4 | 19.7 | 60.9 | 3.2 | 236.1 | 2.9 | 440.5 | 446.7 | 182.5 | 65.4 | 531 | 531.6 | 104.6 | 78.8 | 228.1 | 487.2 | 243.4 | 247.9 | 412.1 | 234.7 | 218.2 | 540.4 | 326.9 | 217.5 | 197.6 | 192.3 | 201.4 | 209.1 | 191.8 | 201.6 | 204.8
2931.1 | 2710.1 | -6.7 | 0 | 0 | 212.2 | 199.3 | 186 | 187.3 | 217.8 | 37.4 | 19.7 | 60.9 | 3.1 | 236.4 | 2.9 | 440.5 | 446.6 | 182 | 65.4 | 531 | 531.6 | 104.9 | 78.9 | 228.1 | 487.1 | 242.4 | 248.5 | 411.9 | 234.8 | 218.4 | 540.2 | 326.8 | 217.4 | 197.5 | 192.3 | 201.3 | 209 | 191.6 | 201.5 | 204.7
2932.1 | 2711.1 | -6.6 | 0 | 0 | 211.7 | 199.2 | 185.8 | 187.1 | 217.5 | 37.3 | 19.7 | 60.9 | 3.4 | 244.7 | 3 | 440.5 | 446.5 | 181.5 | 65.4 | 531 | 531.5 | 104.9 | 79 | 228 | 487.1 | 241.7 | 248.7 | 411.7 | 234.5 | 219.1 | 540.1 | 326.6 | 217.2 | 197.5 | 192.2 | 201.2 | 208.9 | 191.5 | 201.4 | 204.6
2933.1 | 2712.1 | -6.5 | 0 | 0 | 211.4 | 199.1 | 185.7 | 187 | 217.3 | 37.3 | 19.7 | 60.8 | 3.1 | 243.9 | 3 | 440.5 | 446.4 | 181.3 | 65.6 | 531 | 531.4 | 104.9 | 79.5 | 228 | 487 | 241.4 | 248.3 | 411.5 | 234.3 | 219.1 | 540 | 326.1 | 217.1 | 197.4 | 192.1 | 201.1 | 208.8 | 191.4 | 201.3 | 204.4
2934.1 | 2713.1 | -6.5 | 0 | 0 | 211.1 | 199.1 | 185.6 | 186.9 | 217.1 | 37.3 | 19.7 | 60.8 | 3.1 | 242.5 | 3 | 440.5 | 446.7 | 181.2 | 65.7 | 531 | 531.3 | 104.6 | 80 | 228 | 486.9 | 241.3 | 248.2 | 411.3 | 234.4 | 219.4 | 539.8 | 326 | 217 | 197.3 | 192 | 201 | 208.7 | 191.3 | 201.2 | 204.3
2935.1 | 2714.1 | -5.8 | 0 | 0 | 211 | 199 | 185.7 | 186.7 | 217 | 37.3 | 19.7 | 60.8 | 3.2 | 245.9 | 3 | 440.4 | 446.5 | 181.5 | 65.8 | 531 | 531.2 | 104.2 | 80.2 | 227.9 | 486.8 | 241.5 | 248 | 411.1 | 234.4 | 219 | 539.7 | 325.9 | 216.9 | 197.1 | 191.9 | 200.9 | 208.6 | 191.2 | 201.1 | 204.2
2936.1 | 2715.1 | -6.4 | 0 | 0 | 211 | 198.8 | 185.8 | 186.6 | 216.8 | 37.4 | 19.7 | 60.8 | 3.1 | 247 | 3.2 | 440.4 | 446.5 | 181.7 | 65.8 | 531 | 531.3 | 103.5 | 80.3 | 227.9 | 486.6 | 241 | 248 | 410.9 | 234 | 218.8 | 539.8 | 325.8 | 216.8 | 197 | 191.8 | 200.8 | 208.4 | 191.1 | 200.9 | 204.1
2937.1 | 2716.1 | -6.7 | 0 | 0 | 211 | 198.8 | 185.9 | 186.4 | 216.5 | 37.4 | 19.7 | 60.8 | 3.3 | 255.6 | 3.3 | 440.4 | 446.6 | 182 | 65.9 | 531 | 531.4 | 103.3 | 80.2 | 227.9 | 486.5 | 240.7 | 247.8 | 410.6 | 233.6 | 218.4 | 540 | 325.7 | 216.6 | 196.9 | 191.8 | 200.7 | 208.3 | 191 | 200.8 | 204
2938.1 | 2717.1 | -6.3 | 0 | 0 | 211 | 198.6 | 185.8 | 186.2 | 216.3 | 37.4 | 19.7 | 60.8 | 3.2 | 267.9 | 3.2 | 440.4 | 446.6 | 181.8 | 66.1 | 531 | 531.5 | 103.5 | 80.4 | 227.8 | 486.3 | 240.7 | 247.7 | 410.4 | 233 | 217.9 | 540 | 325.6 | 216.5 | 196.9 | 191.7 | 200.6 | 208.2 | 190.9 | 200.7 | 203.9
2939.1 | 2718.1 | -6 | 0 | 0 | 211 | 198.5 | 185.7 | 186.2 | 216.3 | 37.4 | 19.7 | 60.8 | 3 | 262.7 | 3.1 | 440.4 | 446.5 | 182 | 66.4 | 531 | 531.6 | 104 | 80.4 | 227.8 | 486.1 | 240.6 | 247.4 | 410.2 | 232.4 | 218.1 | 540 | 325.3 | 216.4 | 196.8 | 191.6 | 200.5 | 208.1 | 190.8 | 200.6 | 203.8
2940.1 | 2719.1 | -3.6 | 0 | 0 | 210.9 | 198.4 | 185.7 | 186 | 215.9 | 37.4 | 19.7 | 60.7 | 2.7 | 238 | 3 | 440.3 | 446.4 | 181.8 | 66.6 | 531 | 531.6 | 104.6 | 80.4 | 227.8 | 485.9 | 239.7 | 247.1 | 409.9 | 231.9 | 217.1 | 540.2 | 325.1 | 216.3 | 196.7 | 191.5 | 200.4 | 208 | 190.7 | 200.5 | 203.7
2941.1 | 2720.1 | -1.9 | 0 | 0 | 210.9 | 198.3 | 185.6 | 185.9 | 216 | 37.4 | 19.7 | 60.7 | 2.9 | 220.6 | 2.9 | 440.3 | 446.4 | 182.6 | 66.6 | 530.9 | 531.7 | 105 | 80.4 | 227.7 | 485.8 | 238.6 | 246.8 | 409.7 | 232.2 | 217.2 | 540.3 | 325 | 216.2 | 196.6 | 191.5 | 200.3 | 207.9 | 190.6 | 200.4 | 203.6
2942.1 | 2721.1 | -3.9 | 0 | 0 | 210.9 | 198.2 | 185.4 | 185.8 | 216.1 | 37.5 | 19.7 | 60.6 | 2.8 | 219.7 | 2.7 | 440.3 | 446.4 | 182.7 | 66.4 | 530.9 | 531.9 | 106.6 | 80.5 | 227.7 | 485.6 | 238.3 | 246.9 | 409.5 | 232.1 | 218.1 | 540.5 | 324.9 | 216.1 | 196.5 | 191.4 | 200.2 | 207.7 | 190.5 | 200.3 | 203.4
2943.1 | 2722.1 | -4.7 | 0 | 0 | 210.7 | 198.1 | 185.4 | 185.9 | 216.1 | 37.5 | 19.7 | 60.6 | 3 | 232.6 | 2.4 | 440.3 | 446.5 | 182.7 | 66.3 | 530.9 | 532 | 107.4 | 80.7 | 227.7 | 485.5 | 238.2 | 247 | 409.3 | 232.2 | 218.6 | 540.5 | 324.6 | 215.9 | 196.4 | 191.3 | 200.1 | 207.6 | 190.4 | 200.2 | 203.3
2944.1 | 2723.1 | -4.4 | 0 | 0 | 210.4 | 198.1 | 185.3 | 185.9 | 215.9 | 37.5 | 19.7 | 60.5 | 3 | 258.8 | 2.6 | 440.2 | 446.5 | 183 | 66.3 | 530.8 | 532 | 107.8 | 80.9 | 227.7 | 485.3 | 238.1 | 247 | 409.1 | 232.2 | 218.5 | 540.5 | 324.1 | 215.8 | 196.4 | 191.2 | 199.9 | 207.5 | 190.3 | 200.1 | 203.2
2945.1 | 2724.1 | -5.6 | 0 | 0 | 210.2 | 198 | 185.1 | 185.8 | 216.1 | 37.4 | 19.7 | 60.5 | 3 | 266.9 | 3 | 440.2 | 446.4 | 181.9 | 66.3 | 530.8 | 532.2 | 107.6 | 80.9 | 227.6 | 485 | 238 | 247 | 408.9 | 232.8 | 218.4 | 540.6 | 323.5 | 215.7 | 196.3 | 191 | 199.8 | 207.4 | 190.2 | 200.1 | 203.1
2946.1 | 2725.1 | -6.6 | 0 | 0 | 210 | 197.9 | 185 | 185.8 | 216.4 | 37.3 | 19.7 | 60.4 | 2.9 | 244.9 | 3.6 | 440.2 | 446.3 | 181.6 | 66.2 | 530.7 | 532.3 | 107.4 | 80.8 | 227.5 | 484.8 | 237.4 | 246.6 | 408.7 | 232.7 | 217.4 | 540.7 | 323.5 | 215.6 | 196.2 | 190.9 | 199.7 | 207.3 | 190.1 | 200 | 203
2947.1 | 2726.1 | -6.7 | 0 | 0 | 209.8 | 197.8 | 184.8 | 185.8 | 216.3 | 37.3 | 19.7 | 60.3 | 3.1 | 243.9 | 4.2 | 440.2 | 446.1 | 180.2 | 66.2 | 530.7 | 532.6 | 107.3 | 80.7 | 227.4 | 484.6 | 237 | 246.1 | 408.5 | 232.5 | 215.9 | 540.7 | 323.4 | 215.5 | 196.2 | 190.8 | 199.6 | 207.2 | 190 | 200 | 202.9
2948.1 | 2727.1 | -6.7 | 0 | 0 | 209.6 | 197.8 | 184.7 | 185.7 | 216 | 37.3 | 19.7 | 60.3 | 3 | 259.4 | 4.7 | 440.2 | 446 | 178.8 | 66.1 | 530.6 | 532.9 | 107 | 80.7 | 227.4 | 484.5 | 237.1 | 246.1 | 408.3 | 232.4 | 215.9 | 540.5 | 323.1 | 215.4 | 196 | 190.8 | 199.5 | 207 | 189.9 | 199.8 | 202.8
2949.1 | 2728.1 | -6.7 | 0 | 0 | 209.3 | 197.7 | 184.6 | 185.5 | 215.6 | 37.2 | 19.7 | 60.2 | 3.2 | 253.8 | 4.9 | 440.1 | 446 | 178.1 | 66.1 | 530.6 | 533.3 | 106.7 | 80.6 | 227.4 | 484.3 | 237.3 | 246 | 408.1 | 232.5 | 216.6 | 540.3 | 322.9 | 215.3 | 195.9 | 190.7 | 199.4 | 206.9 | 189.8 | 199.7 | 202.7
2950.1 | 2729.1 | -6.7 | 0 | 0 | 209.1 | 197.6 | 184.5 | 185.5 | 215.4 | 37.2 | 19.7 | 60.2 | 3.1 | 242.2 | 5 | 440.1 | 446.1 | 178.2 | 66.1 | 530.6 | 533.6 | 106.5 | 80.6 | 227.4 | 484.1 | 237.5 | 246 | 407.9 | 232.6 | 216.5 | 540.3 | 322.8 | 215.1 | 195.7 | 190.6 | 199.3 | 206.8 | 189.7 | 199.6 | 202.6
2951.1 | 2730.1 | -6.7 | 0 | 0 | 209 | 197.5 | 184.6 | 185.5 | 215.2 | 37.1 | 19.7 | 60.2 | 3.2 | 243.8 | 4.9 | 440.1 | 446.2 | 178.1 | 66.3 | 530.5 | 533.8 | 105.9 | 80.6 | 227.4 | 483.9 | 236.9 | 245.8 | 407.7 | 233.1 | 215.8 | 540.2 | 322.6 | 215 | 195.7 | 190.5 | 199.2 | 206.7 | 189.6 | 199.4 | 202.5
2952.1 | 2731.1 | -6.7 | 0 | 0 | 208.8 | 197.4 | 184.7 | 185.5 | 215.1 | 37 | 19.7 | 60.2 | 3.2 | 260.6 | 4.9 | 440.1 | 446.2 | 178.1 | 66.4 | 530.5 | 534 | 105.6 | 80.4 | 227.4 | 483.7 | 237 | 245.6 | 407.5 | 232.9 | 214.9 | 540 | 322.5 | 214.9 | 195.5 | 190.4 | 199.1 | 206.5 | 189.5 | 199.2 | 202.3
2953.1 | 2732.1 | -6.7 | 0 | 0 | 208.6 | 197.3 | 184.7 | 185.4 | 214.9 | 37 | 19.7 | 60.1 | 2.9 | 257.3 | 5 | 440.1 | 446.2 | 177.7 | 66.5 | 530.5 | 534.1 | 105.5 | 80.3 | 227.5 | 483.5 | 238.2 | 245.5 | 407.2 | 232.6 | 214.1 | 539.8 | 322.5 | 214.8 | 195.4 | 190.3 | 199 | 206.4 | 189.3 | 199.1 | 202.2
2954.1 | 2733.1 | -6.7 | 0 | 0 | 208.4 | 197.2 | 184.6 | 185.3 | 214.7 | 36.9 | 19.7 | 60.1 | 3 | 243.7 | 5.2 | 440 | 446.2 | 176.6 | 66.5 | 530.5 | 534.1 | 105.5 | 80.1 | 227.6 | 483.3 | 237.8 | 245.3 | 407 | 232.7 | 214.3 | 539.7 | 322.4 | 214.7 | 195.3 | 190.2 | 198.9 | 206.3 | 189.2 | 199.1 | 202.1
2955.1 | 2734.1 | -6.7 | 0 | 0 | 208.1 | 197.1 | 184.4 | 185.2 | 214.6 | 36.9 | 19.7 | 60.1 | 3 | 240.4 | 5.6 | 440 | 446.2 | 175.9 | 66.4 | 530.5 | 534.1 | 106.6 | 80 | 227.6 | 483.1 | 237.7 | 244.9 | 406.8 | 232.3 | 213.6 | 539.8 | 322.2 | 214.6 | 195.2 | 190.1 | 198.8 | 206.2 | 189.1 | 199 | 202
2956.1 | 2735.1 | -6.7 | 0 | 0 | 208 | 197.1 | 184.3 | 185 | 214.6 | 36.9 | 19.7 | 60.1 | 2.9 | 242.7 | 5.5 | 440 | 446.5 | 176.1 | 66.4 | 530.5 | 534.1 | 107.5 | 80 | 227.6 | 482.9 | 238.1 | 244.8 | 406.6 | 231.5 | 212.4 | 539.8 | 321.8 | 214.5 | 195.1 | 190 | 198.7 | 206.1 | 189 | 198.8 | 201.9
2957.1 | 2736.1 | -6.7 | 0 | 0 | 207.7 | 197 | 184.2 | 184.8 | 214.4 | 36.9 | 19.7 | 60.1 | 3.1 | 241.5 | 5.1 | 440 | 446.7 | 177 | 66.4 | 530.4 | 533.9 | 107.7 | 80.2 | 227.6 | 482.7 | 239.4 | 244.6 | 406.4 | 230.4 | 211.8 | 539.7 | 321.6 | 214.3 | 195 | 189.9 | 198.6 | 206 | 188.9 | 198.7 | 201.8
2958.1 | 2737.1 | -6.7 | 0 | 0 | 207.5 | 196.9 | 184.2 | 184.7 | 214.2 | 36.9 | 19.7 | 60.1 | 3.2 | 245.9 | 4.6 | 439.9 | 446.7 | 176.1 | 66.3 | 530.4 | 533.8 | 108 | 80.3 | 227.5 | 482.4 | 240.1 | 243.4 | 406.2 | 229.9 | 210.4 | 539.7 | 321.2 | 214.2 | 194.9 | 189.8 | 198.4 | 205.9 | 188.8 | 198.6 | 201.7
2959.1 | 2738.1 | -6.7 | 0 | 0 | 207.4 | 196.8 | 184 | 184.5 | 213.8 | 36.9 | 19.8 | 60.1 | 3.2 | 245.9 | 4 | 439.9 | 446.7 | 175.5 | 66.4 | 530.4 | 533.8 | 108.1 | 80.2 | 227.5 | 482.2 | 239.7 | 243.1 | 406 | 229.7 | 210.6 | 539.9 | 321.1 | 214.1 | 194.8 | 189.8 | 198.3 | 205.7 | 188.7 | 198.5 | 201.6
2960.1 | 2739.1 | -6.3 | 0 | 0 | 207.4 | 196.7 | 183.8 | 184.4 | 213.5 | 37 | 19.8 | 60.1 | 3.2 | 241.8 | 3.8 | 439.9 | 446.3 | 175.5 | 66.3 | 530.3 | 533.7 | 108.3 | 80.3 | 227.4 | 482 | 240.1 | 243 | 405.8 | 229.4 | 211 | 539.9 | 320.9 | 214 | 194.7 | 189.7 | 198.2 | 205.6 | 188.6 | 198.3 | 201.5
2961.1 | 2740.1 | -6.1 | 0 | 0 | 207.3 | 196.5 | 183.8 | 184.3 | 213.2 | 37 | 19.8 | 60.1 | 3.2 | 239.2 | 3.5 | 439.9 | 446.1 | 174.5 | 66.2 | 530.3 | 533.5 | 108.1 | 80.5 | 227.4 | 481.9 | 240.5 | 243.2 | 405.6 | 229.4 | 211.3 | 539.8 | 320.7 | 213.9 | 194.7 | 189.6 | 198.1 | 205.5 | 188.5 | 198.2 | 201.3
2962.1 | 2741.1 | -6 | 0 | 0 | 207.3 | 196.4 | 183.6 | 184.3 | 213 | 37 | 19.8 | 60 | 3.1 | 237.6 | 3.1 | 439.9 | 446.2 | 175.2 | 66.2 | 530.2 | 533.4 | 108.1 | 80.6 | 227.4 | 481.7 | 239.6 | 243 | 405.4 | 229.3 | 211.4 | 539.8 | 320.6 | 213.8 | 194.5 | 189.5 | 198 | 205.4 | 188.4 | 198.1 | 201.2
2963.1 | 2742.1 | -5.6 | 0 | 0 | 207.2 | 196.3 | 183.5 | 184.2 | 213.1 | 36.9 | 19.8 | 60 | 3 | 244.9 | 3 | 439.9 | 446.1 | 176 | 66.2 | 530.2 | 533.3 | 107.8 | 80.5 | 227.4 | 481.5 | 239.2 | 242.2 | 405.2 | 228.3 | 211.5 | 539.8 | 320.5 | 213.7 | 194.4 | 189.4 | 197.9 | 205.3 | 188.3 | 197.9 | 201.1
2964.1 | 2743.1 | -5.9 | 0 | 0 | 207 | 196.1 | 183.4 | 184.1 | 212.8 | 36.9 | 19.8 | 60 | 3 | 249.9 | 3.1 | 439.8 | 445.9 | 174.5 | 66.2 | 530.2 | 533.2 | 107.7 | 80.6 | 227.4 | 481.2 | 238.4 | 242 | 405.1 | 228.2 | 212 | 539.8 | 320.4 | 213.6 | 194.2 | 189.3 | 197.8 | 205.2 | 188.2 | 197.8 | 201
2965.1 | 2744.1 | -6.4 | 0 | 0 | 206.9 | 195.9 | 183.4 | 183.9 | 212.6 | 36.9 | 19.8 | 59.9 | 3.2 | 241.2 | 3 | 439.8 | 445.9 | 173.8 | 66.3 | 530.1 | 533.2 | 107.9 | 80.6 | 227.4 | 481 | 238.4 | 241.7 | 404.9 | 228.5 | 212.3 | 539.8 | 320.3 | 213.4 | 194.1 | 189.1 | 197.7 | 205.1 | 188.1 | 197.7 | 200.9
2966.1 | 2745.1 | -6.7 | 0 | 0 | 206.8 | 195.8 | 183.2 | 183.7 | 212.6 | 36.9 | 19.8 | 59.9 | 3.2 | 225.7 | 3.3 | 439.8 | 446 | 173.1 | 66.3 | 530.1 | 533.3 | 108.7 | 80.6 | 227.5 | 480.8 | 239.2 | 241.5 | 404.7 | 228.5 | 212.6 | 539.8 | 320.1 | 213.3 | 194 | 189 | 197.6 | 205 | 187.9 | 197.5 | 200.8
2967.1 | 2746.1 | -6.7 | 0 | 0 | 206.6 | 195.7 | 183 | 183.6 | 212.5 | 36.9 | 19.8 | 59.9 | 3.1 | 230.3 | 3.3 | 439.8 | 445.9 | 173.1 | 66.2 | 530 | 533.4 | 109.5 | 80.6 | 227.5 | 480.6 | 238.3 | 241.6 | 404.5 | 227.8 | 212.9 | 539.8 | 320.1 | 213.1 | 193.9 | 188.9 | 197.5 | 204.9 | 187.8 | 197.4 | 200.7
2968.1 | 2747.1 | -6.5 | 0 | 0 | 206.4 | 195.5 | 182.8 | 183.5 | 212.5 | 36.9 | 19.8 | 59.8 | 3.1 | 245.4 | 3.2 | 439.7 | 445.7 | 172.7 | 66.2 | 530 | 533.5 | 109.7 | 80.6 | 227.4 | 480.4 | 237.6 | 241.8 | 404.3 | 227.8 | 212.8 | 539.7 | 320.1 | 213 | 193.8 | 188.8 | 197.4 | 204.8 | 187.7 | 197.3 | 200.6
2969.1 | 2748.1 | -6.6 | 0 | 0 | 206.2 | 195.4 | 182.7 | 183.4 | 212.6 | 36.9 | 19.8 | 59.8 | 3.2 | 257.1 | 3.2 | 439.7 | 445.8 | 172.3 | 66.1 | 529.9 | 533.5 | 110.1 | 80.5 | 227.4 | 480.2 | 237.7 | 242.3 | 404.1 | 227.6 | 212.8 | 539.5 | 319.8 | 212.9 | 193.7 | 188.7 | 197.3 | 204.7 | 187.6 | 197.1 | 200.5
2970.1 | 2749.1 | -6.6 | 0 | 0 | 206.1 | 195.3 | 182.5 | 183.2 | 212.6 | 36.9 | 19.8 | 59.8 | 3.2 | 256.4 | 3.3 | 439.7 | 445.9 | 171.2 | 66 | 529.9 | 533.5 | 110.4 | 80.4 | 227.4 | 480 | 238.2 | 242.4 | 403.9 | 227.2 | 213.1 | 539.4 | 319.7 | 212.8 | 193.5 | 188.6 | 197.2 | 204.6 | 187.6 | 197 | 200.3
2971.1 | 2750.1 | -6.3 | 0 | 0 | 206 | 195.3 | 182.3 | 183.1 | 212.4 | 36.8 | 19.8 | 59.8 | 3.1 | 240.8 | 3.4 | 439.7 | 446.2 | 171.6 | 65.9 | 529.9 | 533.4 | 110.3 | 80.3 | 227.4 | 479.7 | 238.2 | 242.3 | 403.7 | 227.2 | 213.4 | 539.5 | 319.6 | 212.7 | 193.4 | 188.4 | 197.1 | 204.5 | 187.5 | 196.9 | 200.2
2972.1 | 2751.1 | -6.6 | 0 | 0 | 205.8 | 195.2 | 182.1 | 183.1 | 212.1 | 36.8 | 19.8 | 59.7 | 3 | 228.7 | 3.6 | 439.7 | 446.1 | 172.6 | 65.7 | 529.9 | 533.4 | 110.4 | 80.1 | 227.3 | 479.5 | 238 | 242.1 | 403.4 | 227 | 212.7 | 539.7 | 319.5 | 212.6 | 193.3 | 188.3 | 197 | 204.4 | 187.3 | 196.8 | 200.1
2973.1 | 2752.1 | -6.5 | 0 | 0 | 205.6 | 195.2 | 181.9 | 183 | 211.7 | 36.8 | 19.8 | 59.7 | 2.8 | 238.6 | 3.5 | 439.7 | 446.1 | 172.7 | 65.5 | 529.9 | 533.3 | 110.1 | 79.9 | 227.3 | 479.3 | 238.1 | 242 | 403.3 | 227.2 | 212.9 | 539.6 | 319.3 | 212.5 | 193.2 | 188.2 | 196.9 | 204.3 | 187.2 | 196.7 | 200
2974.1 | 2753.1 | -5.4 | 0 | 0 | 205.4 | 195.1 | 181.8 | 183 | 211.5 | 36.8 | 19.8 | 59.6 | 2.6 | 248.9 | 3.8 | 439.6 | 446 | 173.5 | 65.3 | 529.9 | 533.2 | 109.7 | 80 | 227.2 | 479.1 | 238.2 | 241.6 | 403 | 226.6 | 213.4 | 539.5 | 319.1 | 212.3 | 193.1 | 188.1 | 196.8 | 204.2 | 187.1 | 196.6 | 199.9
2975.1 | 2754.1 | -4.2 | 0 | 0 | 205.2 | 195.1 | 181.6 | 182.8 | 211.3 | 36.8 | 19.8 | 59.6 | 2.8 | 249.3 | 4 | 439.6 | 445.8 | 172.9 | 65.4 | 530 | 533 | 109.6 | 80.1 | 227.1 | 478.9 | 238.8 | 241 | 402.8 | 225.7 | 213.5 | 539.6 | 318.8 | 212.2 | 193 | 188 | 196.7 | 204.1 | 187 | 196.4 | 199.8
2976.1 | 2755.1 | -2.1 | 0 | 0 | 205 | 195 | 181.4 | 182.6 | 211.1 | 36.8 | 19.8 | 59.6 | 3.1 | 242.2 | 4 | 439.6 | 445.7 | 171.6 | 65.4 | 530 | 532.9 | 110.3 | 80.2 | 227.2 | 478.7 | 238 | 240.5 | 402.6 | 225.1 | 213.3 | 539.7 | 318.6 | 212.1 | 192.9 | 187.9 | 196.5 | 204 | 186.9 | 196.2 | 199.7
2977.1 | 2756.1 | -3.6 | 0 | 0 | 204.8 | 194.9 | 181.4 | 182.5 | 210.8 | 36.8 | 19.8 | 59.6 | 3 | 244 | 4 | 439.6 | 445.8 | 170.2 | 65.3 | 530 | 532.9 | 111.9 | 79.9 | 227.2 | 478.4 | 238 | 240 | 402.4 | 224.9 | 213.1 | 539.8 | 318.4 | 212 | 192.8 | 187.8 | 196.4 | 203.9 | 186.8 | 196.1 | 199.6
2978.1 | 2757.1 | -4.9 | 0 | 0 | 204.6 | 194.8 | 181.3 | 182.3 | 210.6 | 36.8 | 19.8 | 59.6 | 3.2 | 239.4 | 4.2 | 439.6 | 445.7 | 170.9 | 65.1 | 529.9 | 533.2 | 111.9 | 79.6 | 227.2 | 478.2 | 237.5 | 239.7 | 402.2 | 225 | 212.7 | 539.8 | 318.2 | 211.9 | 192.6 | 187.7 | 196.3 | 203.8 | 186.6 | 195.9 | 199.4
2979.1 | 2758.1 | -5.6 | 0 | 0 | 204.4 | 194.7 | 181 | 182.2 | 210.3 | 36.8 | 19.8 | 59.6 | 3.3 | 218.5 | 4.2 | 439.5 | 445.5 | 169.7 | 65.1 | 529.9 | 533.5 | 111.3 | 79.3 | 227.3 | 478 | 237.7 | 239.7 | 402 | 224.7 | 212.8 | 539.8 | 318.1 | 211.8 | 192.5 | 187.6 | 196.2 | 203.6 | 186.5 | 195.8 | 199.3
2980.1 | 2759.1 | -5.6 | 0 | 0 | 204.1 | 194.6 | 180.8 | 182.1 | 210.2 | 36.8 | 19.8 | 59.5 | 3.1 | 218.5 | 4.3 | 439.5 | 445.9 | 169.8 | 65.1 | 529.9 | 533.6 | 110.8 | 79 | 227.4 | 477.7 | 238.4 | 239.7 | 401.8 | 224.3 | 212.4 | 539.7 | 318 | 211.7 | 192.4 | 187.5 | 196.1 | 203.5 | 186.4 | 195.6 | 199.2
2981.1 | 2760.1 | -6.4 | 0 | 0 | 203.8 | 194.5 | 180.7 | 182 | 210.2 | 36.8 | 19.8 | 59.5 | 3.3 | 224.7 | 4.3 | 439.5 | 445.9 | 171.2 | 65 | 529.9 | 533.7 | 110.5 | 79 | 227.3 | 477.5 | 238.7 | 239.7 | 401.6 | 224.3 | 211.7 | 539.7 | 317.9 | 211.6 | 192.3 | 187.4 | 196 | 203.4 | 186.3 | 195.5 | 199.1
2982.1 | 2761.1 | -6.7 | 0 | 0 | 203.7 | 194.3 | 180.5 | 181.9 | 210.1 | 36.8 | 19.8 | 59.5 | 3.1 | 225.2 | 4.4 | 439.5 | 445.7 | 172.2 | 64.9 | 529.8 | 533.8 | 110.6 | 79 | 227.4 | 477.3 | 237.9 | 239.6 | 401.4 | 224.1 | 211.4 | 539.6 | 317.8 | 211.5 | 192.2 | 187.3 | 195.9 | 203.3 | 186.1 | 195.4 | 199
2983.1 | 2762.1 | -6.7 | 0 | 0 | 203.6 | 194.2 | 180.4 | 181.8 | 209.9 | 36.8 | 19.8 | 59.5 | 3.3 | 232.6 | 4.3 | 439.5 | 445.5 | 172 | 64.8 | 529.8 | 533.9 | 110.9 | 78.8 | 227.4 | 477 | 237.1 | 239.4 | 401.2 | 223.6 | 210.9 | 539.3 | 317.8 | 211.3 | 192.1 | 187.1 | 195.8 | 203.2 | 186.1 | 195.3 | 198.9
2984.1 | 2763.1 | -6.7 | 0 | 0 | 203.6 | 194.1 | 180.3 | 181.8 | 209.5 | 36.8 | 19.8 | 59.5 | 3.1 | 239.1 | 3.9 | 439.5 | 445.3 | 171.5 | 64.7 | 529.8 | 534.1 | 110.8 | 78.7 | 227.4 | 476.8 | 236.6 | 239.4 | 401 | 223.3 | 209.1 | 539.2 | 317.6 | 211.2 | 192 | 187 | 195.7 | 203.1 | 186 | 195.2 | 198.8
2985.1 | 2764.1 | -6.7 | 0 | 0 | 203.6 | 194.1 | 180.2 | 181.7 | 209.3 | 36.8 | 19.8 | 59.4 | 3 | 240 | 3.4 | 439.4 | 445.2 | 171.9 | 64.4 | 529.8 | 534.3 | 110.4 | 78.7 | 227.5 | 476.6 | 235.7 | 239.2 | 400.8 | 223.3 | 208.2 | 538.9 | 317.6 | 211.1 | 192 | 186.9 | 195.6 | 203 | 185.8 | 195.1 | 198.7
2986.1 | 2765.1 | -6.7 | 0 | 0 | 203.4 | 194 | 180.1 | 181.6 | 209.1 | 36.8 | 19.8 | 59.4 | 2.9 | 241.1 | 3 | 439.4 | 445 | 172.8 | 64.2 | 529.7 | 534.4 | 110.1 | 78.7 | 227.5 | 476.4 | 235.6 | 238.8 | 400.6 | 223.6 | 208.3 | 538.6 | 317.4 | 211 | 191.9 | 186.8 | 195.5 | 202.9 | 185.7 | 195 | 198.6
2987.1 | 2766.1 | -6.4 | 0 | 0 | 203.2 | 194 | 180 | 181.5 | 208.8 | 36.8 | 19.8 | 59.4 | 3 | 241.2 | 2.7 | 439.4 | 444.9 | 173.1 | 64.1 | 529.7 | 534.5 | 109.5 | 78.5 | 227.5 | 476.1 | 235.2 | 238.7 | 400.4 | 222.9 | 207.3 | 538.6 | 317.2 | 210.9 | 191.8 | 186.7 | 195.4 | 202.8 | 185.6 | 194.9 | 198.4
2988.1 | 2767.1 | -6.3 | 0 | 0 | 203.1 | 193.9 | 179.9 | 181.4 | 208.5 | 36.9 | 19.8 | 59.4 | 3.2 | 241.5 | 2.7 | 439.4 | 444.9 | 173.2 | 64.1 | 529.7 | 534.5 | 109.2 | 78.4 | 227.5 | 475.9 | 234.2 | 238.1 | 400.1 | 222.7 | 206.7 | 538.6 | 317 | 210.7 | 191.7 | 186.6 | 195.2 | 202.7 | 185.5 | 194.8 | 198.3
2989.1 | 2768.1 | -6.7 | 0 | 0 | 203.1 | 193.7 | 179.9 | 181.3 | 208.2 | 36.9 | 19.8 | 59.4 | 3.4 | 241.3 | 2.8 | 439.4 | 445.1 | 173.2 | 64 | 529.7 | 534.5 | 109.6 | 78.3 | 227.5 | 475.7 | 233.3 | 237.9 | 399.9 | 223 | 206.3 | 538.7 | 316.8 | 210.7 | 191.7 | 186.6 | 195.1 | 202.6 | 185.4 | 194.7 | 198.2
2990.1 | 2769.1 | -6.7 | 0 | 0 | 203 | 193.5 | 179.8 | 181.1 | 208 | 37 | 19.8 | 59.4 | 3 | 241.3 | 2.9 | 439.3 | 445.1 | 172.5 | 63.9 | 529.7 | 534.5 | 110 | 78.2 | 227.5 | 475.5 | 232.4 | 237.7 | 399.7 | 222.7 | 205.7 | 538.7 | 316.6 | 210.5 | 191.6 | 186.5 | 195 | 202.5 | 185.3 | 194.6 | 198.1
2991.1 | 2770.1 | -6.7 | 0 | 0 | 203 | 193.3 | 179.8 | 181 | 207.8 | 37 | 19.8 | 59.4 | 3 | 243.2 | 3 | 439.3 | 445.1 | 172.2 | 63.8 | 529.7 | 534.4 | 109.3 | 78.2 | 227.5 | 475.3 | 231.5 | 237.1 | 399.5 | 222.2 | 204.7 | 538.8 | 316 | 210.5 | 191.4 | 186.4 | 194.9 | 202.4 | 185.1 | 194.5 | 198
2992.1 | 2771.1 | -6.7 | 0 | 0 | 202.9 | 193 | 179.7 | 180.8 | 207.5 | 36.9 | 19.8 | 59.4 | 3.3 | 245.6 | 3.3 | 439.3 | 445.1 | 172.2 | 63.6 | 529.7 | 534.4 | 108.6 | 78.2 | 227.6 | 475.1 | 230.7 | 236.8 | 399.2 | 222.1 | 205 | 539 | 315.9 | 210.3 | 191.3 | 186.3 | 194.8 | 202.2 | 185 | 194.3 | 197.9
2993.1 | 2772.1 | -6.7 | 0 | 0 | 202.7 | 192.9 | 179.6 | 180.8 | 207.3 | 36.9 | 19.8 | 59.4 | 3.3 | 249.6 | 3.6 | 439.3 | 445 | 172.3 | 63.5 | 529.7 | 534.4 | 107.7 | 78.1 | 227.5 | 474.9 | 230.8 | 236.1 | 399 | 222.2 | 204.7 | 539.1 | 315.6 | 210.2 | 191.1 | 186.2 | 194.7 | 202.1 | 184.9 | 194.2 | 197.8
2994.1 | 2773.1 | -6.7 | 0 | 0 | 202.3 | 192.7 | 179.5 | 180.7 | 207.1 | 36.9 | 19.8 | 59.4 | 3.3 | 242.5 | 3.8 | 439.3 | 444.9 | 172.9 | 63.7 | 529.7 | 534.4 | 107.5 | 78 | 227.5 | 474.7 | 230.2 | 235.7 | 398.8 | 222.2 | 204.2 | 539 | 315.2 | 210.1 | 191 | 186.1 | 194.6 | 202 | 184.8 | 194.1 | 197.7
2995.1 | 2774.1 | -6.7 | 0 | 0 | 202.1 | 192.6 | 179.4 | 180.7 | 206.9 | 36.9 | 19.8 | 59.3 | 3 | 237.6 | 3.9 | 439.3 | 444.8 | 173.4 | 63.6 | 529.7 | 534.3 | 107.2 | 78 | 227.4 | 474.5 | 230.2 | 235.4 | 398.6 | 221.6 | 204 | 538.8 | 315.2 | 210 | 190.9 | 186 | 194.5 | 201.9 | 184.7 | 194 | 197.6
2996.1 | 2775.1 | -6.6 | 0 | 0 | 202 | 192.5 | 179.2 | 180.6 | 206.8 | 36.8 | 19.8 | 59.3 | 3.1 | 238.9 | 3.9 | 439.2 | 444.8 | 172.5 | 63.6 | 529.7 | 534.2 | 106.7 | 78.1 | 227.3 | 474.4 | 229.7 | 235 | 398.4 | 220.7 | 203.9 | 538.6 | 315 | 209.9 | 190.8 | 185.9 | 194.4 | 201.7 | 184.6 | 193.9 | 197.5
2997.1 | 2776.1 | -6.3 | 0 | 0 | 202 | 192.5 | 179.1 | 180.6 | 206.6 | 36.8 | 19.8 | 59.3 | 3 | 233.4 | 4.2 | 439.2 | 445.1 | 172.1 | 63.5 | 529.7 | 534.2 | 106.4 | 78.2 | 227.2 | 474.2 | 229.3 | 233.9 | 398.2 | 220.2 | 202.8 | 538.6 | 314.8 | 209.8 | 190.7 | 185.8 | 194.3 | 201.6 | 184.5 | 193.8 | 197.4
2998.1 | 2777.1 | -6.5 | 0 | 0 | 201.9 | 192.4 | 178.9 | 180.5 | 206.4 | 36.8 | 19.8 | 59.3 | 3 | 240 | 4.4 | 439.2 | 445.2 | 171 | 63.3 | 529.8 | 534 | 105.9 | 78.2 | 227.1 | 474.1 | 230 | 233.3 | 398 | 220 | 202.3 | 538.6 | 314.6 | 209.6 | 190.6 | 185.7 | 194.2 | 201.5 | 184.4 | 193.7 | 197.3
2999.1 | 2778.1 | -6.7 | 0 | 0 | 201.7 | 192.3 | 178.8 | 180.2 | 206 | 36.8 | 19.8 | 59.3 | 3.2 | 241.7 | 4.6 | 439.2 | 445 | 170.1 | 63.3 | 529.8 | 533.8 | 105.4 | 78.2 | 227 | 473.9 | 229.7 | 232.3 | 397.7 | 220.3 | 201.7 | 538.6 | 314.5 | 209.5 | 190.5 | 185.5 | 194.1 | 201.4 | 184.3 | 193.6 | 197.1
3000.1 | 2779.1 | -6.7 | 0 | 0 | 201.6 | 192.2 | 178.8 | 180 | 205.8 | 36.7 | 19.8 | 59.2 | 3 | 238.3 | 4.7 | 439.2 | 444.9 | 169.2 | 63.3 | 529.8 | 533.7 | 104.8 | 78.2 | 226.9 | 473.7 | 229.2 | 231 | 397.5 | 220.5 | 201.6 | 538.4 | 314.4 | 209.4 | 190.4 | 185.4 | 193.9 | 201.3 | 184.1 | 193.5 | 197
3001.1 | 2780.1 | -6.7 | 0 | 0 | 201.6 | 192.1 | 178.7 | 179.8 | 206.1 | 36.7 | 19.8 | 59.2 | 3.2 | 236.5 | 4.8 | 439.2 | 444.8 | 168.5 | 63.3 | 529.9 | 533.5 | 104 | 78.3 | 226.8 | 473.6 | 228.6 | 229.9 | 397.3 | 220.6 | 200.8 | 538.4 | 314.2 | 209.3 | 190.3 | 185.3 | 193.9 | 201.2 | 184 | 193.3 | 196.9
3002.1 | 2781.1 | -6.7 | 0 | 0 | 201.6 | 191.9 | 178.5 | 179.7 | 206.2 | 36.6 | 19.8 | 59.2 | 3.2 | 229.4 | 4.8 | 439.1 | 444.8 | 169.1 | 63.2 | 529.9 | 533.4 | 103.2 | 78.4 | 226.7 | 473.4 | 227.9 | 228.4 | 397 | 221.4 | 200.4 | 538.5 | 313.9 | 209.2 | 190.2 | 185.1 | 193.8 | 201.1 | 183.9 | 193.2 | 196.8
3003.1 | 2782.1 | -6.7 | 0 | 0 | 201.6 | 191.8 | 178.4 | 179.6 | 206 | 36.6 | 19.8 | 59.2 | 3 | 229.4 | 4.6 | 439.1 | 444.7 | 169.4 | 63.2 | 530 | 533.4 | 102.8 | 78.5 | 226.6 | 473.2 | 228.3 | 227.4 | 396.8 | 221.7 | 200.5 | 538.4 | 313.7 | 209.1 | 190.1 | 185 | 193.7 | 201 | 183.7 | 193 | 196.7
3004.1 | 2783.1 | -6.6 | 0 | 0 | 201.5 | 191.7 | 178.4 | 179.5 | 206 | 36.6 | 19.8 | 59.2 | 2.9 | 232.2 | 4.6 | 439.1 | 444.6 | 169.2 | 63.1 | 530 | 533.2 | 102.4 | 78.5 | 226.5 | 473 | 228.5 | 226.9 | 396.6 | 222 | 199.6 | 538.4 | 313.6 | 209 | 190 | 184.9 | 193.6 | 200.9 | 183.6 | 192.9 | 196.6
3005.1 | 2784.1 | -6.6 | 0 | 0 | 201.5 | 191.6 | 178.2 | 179.3 | 205.9 | 36.6 | 19.8 | 59.2 | 3 | 238.1 | 4.5 | 439.1 | 444.4 | 169.1 | 62.9 | 530 | 533.1 | 102 | 78.5 | 226.4 | 472.9 | 227.6 | 226.6 | 396.4 | 221.5 | 199.1 | 538.3 | 313.4 | 208.8 | 189.9 | 184.8 | 193.4 | 200.8 | 183.5 | 192.8 | 196.5
3006.1 | 2785.1 | -6.3 | 0 | 0 | 201.3 | 191.6 | 178 | 179.2 | 205.8 | 36.6 | 19.8 | 59.2 | 3 | 246.8 | 4.5 | 439.1 | 444.7 | 169.7 | 62.8 | 530.1 | 533 | 101.6 | 78.6 | 226.2 | 472.7 | 227.1 | 226.3 | 396.2 | 221.1 | 199.6 | 538.1 | 313.2 | 208.7 | 189.8 | 184.8 | 193.3 | 200.7 | 183.4 | 192.6 | 196.4
3007.1 | 2786.1 | -5.8 | 0 | 0 | 201.1 | 191.5 | 177.8 | 179.1 | 205.5 | 36.6 | 19.8 | 59.2 | 2.8 | 248 | 4.6 | 439.1 | 444.6 | 168.3 | 62.7 | 530.2 | 532.9 | 101 | 78.6 | 226.1 | 472.5 | 226.3 | 226.2 | 396 | 221.4 | 199 | 538.1 | 313 | 208.6 | 189.7 | 184.7 | 193.2 | 200.5 | 183.3 | 192.5 | 196.2
3008.1 | 2787.1 | -3.5 | 0 | 0 | 200.8 | 191.4 | 177.6 | 179.2 | 205.5 | 36.5 | 19.8 | 59.2 | 2.9 | 247.6 | 4.8 | 439 | 444.7 | 168.7 | 62.7 | 530.2 | 532.8 | 100.6 | 78.4 | 226 | 472.4 | 225.6 | 225.6 | 395.8 | 221.3 | 198.6 | 538.1 | 312.8 | 208.5 | 189.6 | 184.5 | 193.1 | 200.4 | 183.2 | 192.4 | 196.1
3009.1 | 2788.1 | -3.9 | 0 | 0 | 200.6 | 191.3 | 177.5 | 179.1 | 205.3 | 36.5 | 19.8 | 59.1 | 3 | 242.3 | 5 | 439 | 444.5 | 168.4 | 62.7 | 530.3 | 532.7 | 100.1 | 78.2 | 225.8 | 472.2 | 225.2 | 225.3 | 395.5 | 221.6 | 198.5 | 537.9 | 312.6 | 208.4 | 189.5 | 184.4 | 193 | 200.3 | 183.1 | 192.4 | 196
3010.1 | 2789.1 | -5 | 0 | 0 | 200.4 | 191.1 | 177.5 | 178.9 | 205.1 | 36.6 | 19.8 | 59.1 | 3 | 242.4 | 5.2 | 439 | 444.5 | 168.3 | 62.6 | 530.3 | 532.6 | 99.9 | 78 | 225.7 | 472 | 224.7 | 224.6 | 395.3 | 221.6 | 197.4 | 537.9 | 312.2 | 208.3 | 189.4 | 184.2 | 192.9 | 200.2 | 183 | 192.3 | 195.9
3011.1 | 2790.1 | -5.3 | 0 | 0 | 200.3 | 191 | 177.3 | 178.7 | 204.9 | 36.5 | 19.8 | 59 | 3.1 | 244.6 | 5.2 | 439 | 444.6 | 168.4 | 62.5 | 530.4 | 532.4 | 99.7 | 77.8 | 225.6 | 471.9 | 224.4 | 223.9 | 395.1 | 221.2 | 197.2 | 537.7 | 312.1 | 208.2 | 189.3 | 184.1 | 192.8 | 200.1 | 182.9 | 192.2 | 195.8
3012.1 | 2791.1 | -5 | 0 | 0 | 200.2 | 191 | 177.2 | 178.6 | 204.7 | 36.5 | 19.8 | 59 | 3.3 | 245 | 4.8 | 439 | 444.6 | 167 | 62.3 | 530.4 | 532.2 | 99 | 77.8 | 225.5 | 471.7 | 224.1 | 222.9 | 394.9 | 221.3 | 197.2 | 537.7 | 311.8 | 208 | 189.3 | 184 | 192.7 | 200 | 182.8 | 192.1 | 195.7
3013.1 | 2792.1 | -5.6 | 0 | 0 | 200 | 190.9 | 177 | 178.5 | 204.4 | 36.5 | 19.9 | 59 | 3.6 | 242.5 | 4.6 | 439 | 444.6 | 166.4 | 62.4 | 530.5 | 532 | 98.4 | 77.8 | 225.4 | 471.5 | 223.7 | 222.2 | 394.7 | 221.5 | 197.1 | 537.8 | 311.6 | 207.9 | 189.2 | 184 | 192.6 | 199.9 | 182.7 | 192 | 195.6
3014.1 | 2793.1 | -6.3 | 0 | 0 | 199.8 | 190.8 | 176.8 | 178.4 | 204.2 | 36.5 | 19.9 | 59 | 3.4 | 254.6 | 4.8 | 438.9 | 444.5 | 164.3 | 62.5 | 530.5 | 531.8 | 98 | 77.6 | 225.2 | 471.3 | 223.3 | 221.6 | 394.4 | 221.2 | 196.9 | 537.8 | 311.4 | 207.8 | 189.1 | 183.9 | 192.5 | 199.8 | 182.6 | 191.9 | 195.5
3015.1 | 2794.1 | -6.4 | 0 | 0 | 199.6 | 190.6 | 176.7 | 178.2 | 204.1 | 36.5 | 19.9 | 58.9 | 3.2 | 251.5 | 4.7 | 438.9 | 444.5 | 164 | 62.4 | 530.5 | 531.6 | 97.7 | 77.3 | 225.1 | 471.1 | 223.1 | 221.3 | 394.2 | 221.3 | 196.1 | 537.6 | 311.2 | 207.7 | 189 | 183.8 | 192.4 | 199.7 | 182.4 | 191.9 | 195.4
3016.1 | 2795.1 | -6.4 | 0 | 0 | 199.6 | 190.5 | 176.7 | 178.1 | 204 | 36.5 | 19.9 | 58.9 | 3.2 | 243.7 | 4.5 | 438.9 | 444.4 | 163.9 | 62.3 | 530.5 | 531.5 | 97.7 | 77.1 | 224.9 | 470.9 | 223.4 | 221 | 394 | 220.9 | 195 | 537.4 | 311.1 | 207.6 | 188.9 | 183.7 | 192.3 | 199.5 | 182.3 | 191.8 | 195.2
3017.1 | 2796.1 | -5.6 | 0 | 0 | 199.6 | 190.4 | 176.6 | 178.1 | 204.4 | 36.4 | 19.9 | 58.9 | 3.2 | 238.3 | 4.4 | 438.9 | 444.3 | 164.8 | 62.2 | 530.4 | 531.4 | 97.5 | 76.9 | 224.8 | 470.8 | 223 | 221 | 393.8 | 221 | 195.3 | 537.1 | 311 | 207.5 | 188.8 | 183.6 | 192.2 | 199.4 | 182.2 | 191.7 | 195.1
3018.1 | 2797.1 | -4.8 | 0 | 0 | 199.5 | 190.3 | 176.5 | 178 | 204.5 | 36.4 | 19.9 | 58.9 | 3.3 | 237.5 | 4.6 | 438.9 | 444.2 | 166.2 | 62.2 | 530.4 | 531.3 | 97.2 | 77 | 224.7 | 470.6 | 223.2 | 220.8 | 393.6 | 220.8 | 195.5 | 537.1 | 310.8 | 207.4 | 188.7 | 183.5 | 192.1 | 199.3 | 182.1 | 191.6 | 195
3019.1 | 2798.1 | -5.1 | 0 | 0 | 199.5 | 190.1 | 176.4 | 177.8 | 204.6 | 36.4 | 19.9 | 58.8 | 3.6 | 240.2 | 4.9 | 438.8 | 444.2 | 165.9 | 62.2 | 530.4 | 531.4 | 96.8 | 77.5 | 224.6 | 470.4 | 223 | 219.8 | 393.4 | 220.9 | 194.6 | 537.2 | 310.5 | 207.3 | 188.6 | 183.4 | 192 | 199.2 | 181.9 | 191.5 | 194.9
3020.1 | 2799.1 | -6.3 | 0 | 0 | 199.4 | 190 | 176.3 | 177.8 | 204.4 | 36.3 | 19.9 | 58.8 | 3.4 | 243.4 | 5 | 438.8 | 444.2 | 166.6 | 62.3 | 530.4 | 531.5 | 96.6 | 77.9 | 224.5 | 470.2 | 222.8 | 219.8 | 393.2 | 221.1 | 194.4 | 537.1 | 310.3 | 207.2 | 188.5 | 183.3 | 191.9 | 199.1 | 181.9 | 191.4 | 194.8
3021.1 | 2800.1 | -6.3 | 0 | 0 | 199.2 | 190 | 176.3 | 177.8 | 204.3 | 36.3 | 19.9 | 58.8 | 3.7 | 243.2 | 4.9 | 438.8 | 444.2 | 167 | 62.4 | 530.4 | 531.6 | 96.5 | 78.3 | 224.5 | 470.1 | 222.2 | 220 | 393 | 220.8 | 195.2 | 537 | 310.2 | 207.1 | 188.3 | 183.2 | 191.8 | 199 | 181.8 | 191.4 | 194.7
3022.1 | 2801.1 | -6.6 | 0 | 0 | 198.9 | 189.9 | 176.2 | 177.7 | 204.3 | 36.2 | 19.9 | 58.8 | 3.9 | 245.6 | 5 | 438.8 | 444.1 | 167.7 | 62.6 | 530.4 | 531.7 | 97.2 | 78.6 | 224.5 | 469.9 | 222.3 | 220 | 392.8 | 220.9 | 194.8 | 536.9 | 310 | 207 | 188.2 | 183.1 | 191.7 | 198.9 | 181.7 | 191.3 | 194.6
3023.1 | 2802.1 | -6.7 | 0 | 0 | 198.7 | 189.8 | 176.2 | 177.7 | 204.1 | 36.2 | 19.9 | 58.7 | 3.7 | 249.9 | 5.3 | 438.8 | 443.9 | 166.1 | 62.7 | 530.4 | 531.9 | 98.2 | 78.8 | 224.5 | 469.7 | 222.7 | 220.2 | 392.6 | 220.5 | 195 | 536.7 | 309.8 | 206.9 | 188.1 | 183 | 191.6 | 198.7 | 181.5 | 191.1 | 194.5
3024.1 | 2803.1 | -6.7 | 0 | 0 | 198.6 | 189.7 | 176.2 | 177.6 | 204 | 36.2 | 19.9 | 58.7 | 3.6 | 247.4 | 5.4 | 438.7 | 444 | 165.3 | 62.8 | 530.4 | 532.3 | 99.4 | 78.8 | 224.6 | 469.6 | 223.7 | 220.6 | 392.4 | 220.5 | 195.2 | 536.5 | 309.7 | 206.7 | 188 | 183 | 191.5 | 198.6 | 181.4 | 191 | 194.4
3025.1 | 2804.1 | -6.7 | 0 | 0 | 198.4 | 189.6 | 176 | 177.4 | 203.8 | 36.1 | 19.9 | 58.7 | 3.4 | 241.2 | 5.3 | 438.7 | 444 | 164.6 | 63 | 530.3 | 532.6 | 101.5 | 78.9 | 224.6 | 469.4 | 224.7 | 220.6 | 392.2 | 220.6 | 195.2 | 536.4 | 309.6 | 206.6 | 187.9 | 182.8 | 191.4 | 198.5 | 181.3 | 190.9 | 194.3
3026.1 | 2805.1 | -6 | 0 | 0 | 198.3 | 189.4 | 176 | 177.2 | 203.7 | 36.1 | 19.9 | 58.7 | 3.1 | 235.9 | 5.5 | 438.7 | 444 | 164.5 | 63.2 | 530.2 | 533.1 | 102.6 | 79.1 | 224.7 | 469.2 | 225 | 220.8 | 391.9 | 220.3 | 195.9 | 536.3 | 309.3 | 206.5 | 187.8 | 182.7 | 191.3 | 198.4 | 181.2 | 190.8 | 194.2
3027.1 | 2806.1 | -4.9 | 0 | 0 | 198.2 | 189.3 | 176 | 177.1 | 203.5 | 36.1 | 19.9 | 58.7 | 3 | 239.5 | 5.8 | 438.7 | 444 | 165.4 | 63.3 | 530.1 | 533.6 | 102.3 | 79.3 | 224.7 | 469 | 225.3 | 220.5 | 391.7 | 220 | 195.6 | 536.4 | 309.2 | 206.4 | 187.7 | 182.6 | 191.2 | 198.3 | 181.1 | 190.7 | 194.1
3028.1 | 2807.1 | -5.8 | 0 | 0 | 198 | 189.2 | 176 | 177.1 | 203.4 | 36 | 19.9 | 58.7 | 3.1 | 241.4 | 5.7 | 438.7 | 444 | 165.1 | 63.3 | 530 | 533.9 | 102.5 | 79.1 | 224.7 | 468.8 | 226.4 | 219.7 | 391.5 | 220.2 | 194.7 | 536.5 | 309.1 | 206.3 | 187.6 | 182.5 | 191.1 | 198.2 | 181 | 190.6 | 194
3029.1 | 2808.1 | -6.3 | 0 | 0 | 197.8 | 189.2 | 176 | 176.9 | 203.1 | 36 | 19.9 | 58.7 | 3 | 240.9 | 5.5 | 438.7 | 444 | 165.3 | 63.3 | 530 | 534 | 102.3 | 79 | 224.6 | 468.6 | 227.1 | 219.8 | 391.3 | 219.1 | 193.7 | 536.3 | 309 | 206.2 | 187.5 | 182.4 | 190.9 | 198 | 180.9 | 190.5 | 193.8
3030.1 | 2809.1 | -6.7 | 0 | 0 | 197.8 | 189.1 | 175.9 | 176.8 | 202.9 | 36 | 19.9 | 58.7 | 3.3 | 242.5 | 5.2 | 438.6 | 444 | 166.6 | 63.4 | 529.9 | 534 | 103.2 | 78.8 | 224.4 | 468.5 | 227.5 | 219.5 | 391.1 | 218.6 | 192.9 | 536.2 | 308.7 | 206.1 | 187.3 | 182.3 | 190.8 | 197.9 | 180.8 | 190.3 | 193.7
3031.1 | 2810.1 | -6.6 | 0 | 0 | 197.8 | 188.9 | 175.7 | 176.8 | 202.8 | 36 | 19.9 | 58.6 | 3.3 | 242.1 | 5 | 438.6 | 443.9 | 168 | 63.3 | 529.9 | 534 | 103.3 | 78.4 | 224.4 | 468.3 | 227.8 | 219.5 | 390.9 | 218.3 | 192.3 | 536.1 | 308.5 | 206 | 187.2 | 182.2 | 190.7 | 197.8 | 180.7 | 190.2 | 193.6
3032.1 | 2811.1 | -6.3 | 0 | 0 | 197.8 | 188.7 | 175.4 | 176.7 | 202.9 | 36 | 19.9 | 58.6 | 3.3 | 231.8 | 5.3 | 438.6 | 444 | 168.2 | 63.4 | 529.8 | 533.9 | 103.7 | 78.2 | 224.3 | 468.1 | 226.9 | 219.6 | 390.7 | 217.7 | 192.4 | 536 | 308.5 | 205.9 | 187.1 | 182 | 190.6 | 197.7 | 180.6 | 190.1 | 193.5
3033.1 | 2812.1 | -6.1 | 0 | 0 | 197.8 | 188.6 | 175.2 | 176.7 | 203 | 36 | 19.9 | 58.6 | 2.8 | 233.9 | 5.4 | 438.6 | 443.9 | 168.7 | 63.5 | 529.8 | 533.7 | 103.8 | 78.4 | 224.2 | 467.9 | 226.5 | 219.2 | 390.5 | 217.8 | 192.1 | 536.1 | 308.2 | 205.8 | 187 | 181.9 | 190.5 | 197.6 | 180.4 | 190 | 193.4
3034.1 | 2813.1 | -5.1 | 0 | 0 | 197.6 | 188.5 | 175 | 176.5 | 203 | 36 | 19.9 | 58.5 | 2.5 | 238.9 | 5.5 | 438.5 | 444 | 170.3 | 63.7 | 529.8 | 533.5 | 103.4 | 78.4 | 224.3 | 467.7 | 226.3 | 218.6 | 390.3 | 217.8 | 192 | 536.1 | 307.6 | 205.6 | 186.9 | 181.8 | 190.4 | 197.5 | 180.3 | 189.9 | 193.3
3035.1 | 2814.1 | -4.7 | 0 | 0 | 197.4 | 188.4 | 174.8 | 176.3 | 202.9 | 35.9 | 19.9 | 58.5 | 2.7 | 236.8 | 5.5 | 438.5 | 443.9 | 169.9 | 63.8 | 529.8 | 533.3 | 103.5 | 78.5 | 224.3 | 467.5 | 225.7 | 218.7 | 390.1 | 217 | 191.8 | 536 | 307.6 | 205.5 | 186.8 | 181.7 | 190.3 | 197.3 | 180.2 | 189.7 | 193.2
3036.1 | 2815.1 | -4.2 | 0 | 0 | 197.2 | 188.3 | 174.4 | 176.3 | 202.6 | 35.9 | 19.9 | 58.5 | 2.8 | 236.7 | 5.5 | 438.5 | 443.9 | 170.5 | 63.8 | 529.8 | 533.2 | 103.7 | 78.7 | 224.3 | 467.3 | 225.2 | 218.8 | 389.9 | 217.1 | 192.2 | 535.9 | 307.5 | 205.4 | 186.7 | 181.6 | 190.2 | 197.2 | 180.1 | 189.6 | 193.1
3037.1 | 2816.1 | -4.7 | 0 | 0 | 197.1 | 188.1 | 174.1 | 176.2 | 202.1 | 35.9 | 19.9 | 58.4 | 2.9 | 236.8 | 5.4 | 438.5 | 443.9 | 170.7 | 63.8 | 529.8 | 533.1 | 103.2 | 78.8 | 224.2 | 467.1 | 225.2 | 218.5 | 389.7 | 217.1 | 191.8 | 535.9 | 307.2 | 205.3 | 186.6 | 181.4 | 190.1 | 197.1 | 179.9 | 189.5 | 193
3038.1 | 2817.1 | -6.3 | 0 | 0 | 197 | 187.9 | 174 | 176 | 201.9 | 35.9 | 19.9 | 58.4 | 2.9 | 236.8 | 5.3 | 438.5 | 443.7 | 170.3 | 63.7 | 529.8 | 533.3 | 102.9 | 78.9 | 224.2 | 467 | 225.2 | 218 | 389.5 | 216.9 | 192.1 | 535.7 | 306.9 | 205.1 | 186.5 | 181.3 | 190 | 197 | 179.8 | 189.4 | 192.9
3039.1 | 2818.1 | -6.6 | 0 | 0 | 196.8 | 187.7 | 173.9 | 176 | 201.8 | 35.9 | 19.9 | 58.3 | 2.7 | 238.7 | 5.2 | 438.4 | 443.8 | 171.3 | 63.6 | 529.8 | 533.4 | 102.4 | 78.9 | 224.1 | 466.8 | 224.8 | 217.8 | 389.2 | 216.7 | 192.3 | 535.6 | 306.6 | 205 | 186.4 | 181.2 | 189.9 | 196.9 | 179.7 | 189.3 | 192.8
3040.1 | 2819.1 | -6.5 | 0 | 0 | 196.7 | 187.7 | 173.9 | 175.9 | 201.8 | 35.9 | 19.9 | 58.3 | 2.8 | 241.8 | 5.1 | 438.4 | 443.6 | 171.6 | 63.5 | 529.9 | 533.4 | 102 | 78.7 | 224.1 | 466.6 | 224 | 217.5 | 389 | 216.7 | 192.5 | 535.6 | 306.1 | 204.9 | 186.2 | 181.1 | 189.8 | 196.8 | 179.6 | 189.2 | 192.7
3041.1 | 2820.1 | -6.6 | 0 | 0 | 196.6 | 187.6 | 173.9 | 175.8 | 201.7 | 35.9 | 19.9 | 58.3 | 2.6 | 243.8 | 4.9 | 438.4 | 443.5 | 171.5 | 63.3 | 529.9 | 533.2 | 101.7 | 78.6 | 224.1 | 466.4 | 224 | 218 | 388.9 | 217 | 193.5 | 535.7 | 306.2 | 204.8 | 186.2 | 180.9 | 189.7 | 196.6 | 179.5 | 189.1 | 192.6
3042.1 | 2821.1 | -6.7 | 0 | 0 | 196.4 | 187.4 | 173.9 | 175.7 | 201.5 | 35.9 | 19.9 | 58.2 | 2.5 | 240.5 | 4.8 | 438.4 | 443.5 | 170.1 | 63.2 | 529.9 | 533 | 101.8 | 78.4 | 224 | 466.2 | 224.7 | 218.4 | 388.6 | 216.9 | 193.7 | 535.6 | 306.1 | 204.7 | 186.1 | 180.8 | 189.6 | 196.5 | 179.4 | 188.9 | 192.5
3043.1 | 2822.1 | -6.7 | 0 | 0 | 196.2 | 187.3 | 173.7 | 175.6 | 201.1 | 35.9 | 19.9 | 58.2 | 2.7 | 238 | 4.6 | 438.3 | 443.6 | 169 | 63.1 | 529.9 | 533 | 102.3 | 78.3 | 224 | 466.1 | 224 | 218.4 | 388.4 | 216.7 | 193.6 | 535.7 | 305.9 | 204.6 | 186 | 180.7 | 189.5 | 196.4 | 179.3 | 188.8 | 192.3
3044.1 | 2823.1 | -6.7 | 0 | 0 | 196 | 187.2 | 173.5 | 175.5 | 200.9 | 35.9 | 19.9 | 58.2 | 2.7 | 236.7 | 4.5 | 438.3 | 443.5 | 168.2 | 63.1 | 529.9 | 533 | 102.1 | 78.2 | 223.9 | 465.9 | 223 | 218.4 | 388.2 | 216.3 | 193.1 | 535.8 | 305.8 | 204.5 | 185.9 | 180.6 | 189.4 | 196.3 | 179.2 | 188.7 | 192.2
3045.1 | 2824.1 | -6.4 | 0 | 0 | 195.9 | 187.1 | 173.4 | 175.2 | 200.8 | 35.9 | 19.9 | 58.2 | 3 | 232.9 | 4.3 | 438.3 | 443.4 | 168.2 | 63.2 | 529.9 | 532.9 | 101.8 | 78.1 | 223.8 | 465.7 | 222.4 | 218.2 | 388 | 216.2 | 193.2 | 535.9 | 305.6 | 204.4 | 185.8 | 180.5 | 189.3 | 196.2 | 179.1 | 188.6 | 192.1
3046.1 | 2825.1 | -6 | 0 | 0 | 195.8 | 187 | 173.5 | 175.2 | 200.8 | 35.9 | 19.9 | 58.2 | 2.8 | 230.6 | 4.2 | 438.3 | 443.4 | 168.3 | 63.2 | 529.8 | 533 | 101.3 | 77.9 | 223.8 | 465.5 | 222.3 | 217.7 | 387.8 | 216.5 | 192.1 | 535.9 | 305.3 | 204.3 | 185.6 | 180.4 | 189.2 | 196.1 | 179 | 188.5 | 192
3047.1 | 2826.1 | -5.9 | 0 | 0 | 195.8 | 186.9 | 173.5 | 175.2 | 200.9 | 35.9 | 19.9 | 58.2 | 3 | 230.2 | 4 | 438.3 | 443.4 | 167.6 | 63.1 | 529.8 | 533 | 100.8 | 77.7 | 223.8 | 465.2 | 221.8 | 217.1 | 387.6 | 216.8 | 190.7 | 536 | 305 | 204.1 | 185.5 | 180.3 | 189 | 195.9 | 178.9 | 188.4 | 191.9
3048.1 | 2827.1 | -6.1 | 0 | 0 | 195.7 | 186.7 | 173.4 | 175 | 200.8 | 35.9 | 19.9 | 58.1 | 2.8 | 230.1 | 3.9 | 438.2 | 443.5 | 167.5 | 63 | 529.8 | 533 | 100.4 | 77.5 | 223.9 | 465 | 221.4 | 216.4 | 387.4 | 216.5 | 190.5 | 535.9 | 304.6 | 204 | 185.4 | 180.2 | 188.9 | 195.8 | 178.7 | 188.3 | 191.8
3049.1 | 2828.1 | -6.1 | 0 | 0 | 195.5 | 186.5 | 173.2 | 174.9 | 200.6 | 35.9 | 19.9 | 58.1 | 2.8 | 229.5 | 3.6 | 438.2 | 443.4 | 167.3 | 62.9 | 529.8 | 533 | 99.9 | 77.2 | 224 | 464.8 | 221.7 | 216.2 | 387.1 | 217 | 190.3 | 535.9 | 304.5 | 203.9 | 185.3 | 180 | 188.9 | 195.7 | 178.6 | 188.2 | 191.7
3050.1 | 2829.1 | -6.4 | 0 | 0 | 195.4 | 186.4 | 173 | 174.8 | 200.6 | 35.9 | 19.9 | 58.1 | 2.7 | 228.8 | 3.6 | 438.2 | 443.2 | 166.7 | 62.8 | 529.8 | 532.9 | 99.5 | 77 | 223.9 | 464.6 | 221.4 | 215.3 | 386.9 | 216.9 | 190.2 | 536 | 304.4 | 203.8 | 185.2 | 179.9 | 188.8 | 195.6 | 178.6 | 188.1 | 191.6
3051.1 | 2830.1 | -6.6 | 0 | 0 | 195.3 | 186.4 | 172.9 | 174.6 | 200.9 | 35.9 | 19.9 | 58 | 2.8 | 225.2 | 3.5 | 438.2 | 443.2 | 166.6 | 62.9 | 529.9 | 532.8 | 99.1 | 77 | 223.9 | 464.4 | 221.1 | 214.8 | 386.7 | 216.5 | 190.3 | 535.9 | 304.2 | 203.7 | 185.1 | 179.8 | 188.7 | 195.5 | 178.5 | 188 | 191.5
3052.1 | 2831.1 | -6.7 | 0 | 0 | 195.2 | 186.4 | 172.7 | 174.4 | 201.4 | 35.9 | 19.9 | 58 | 2.9 | 224.7 | 3.2 | 438.2 | 443.1 | 166.1 | 62.9 | 529.9 | 532.7 | 98.6 | 76.9 | 224 | 464.2 | 221 | 214.5 | 386.5 | 216.7 | 190.1 | 535.9 | 304 | 203.6 | 185 | 179.7 | 188.5 | 195.4 | 178.4 | 187.9 | 191.4
3053.1 | 2832.1 | -6.7 | 0 | 0 | 195.1 | 186.4 | 172.6 | 174.2 | 201.7 | 35.8 | 19.9 | 57.9 | 2.7 | 226.7 | 2.9 | 438.1 | 443.2 | 166.3 | 62.8 | 529.9 | 532.6 | 98.2 | 76.9 | 224.2 | 464 | 220.9 | 214.2 | 386.3 | 216 | 189.8 | 535.7 | 304 | 203.5 | 184.8 | 179.6 | 188.4 | 195.3 | 178.3 | 187.8 | 191.3
3054.1 | 2833.1 | -6.7 | 0 | 0 | 195 | 186.3 | 172.5 | 174.1 | 201.6 | 35.8 | 19.9 | 57.9 | 2.7 | 235 | 2.7 | 438.1 | 443.1 | 166.1 | 62.8 | 529.9 | 532.5 | 97.9 | 77.1 | 224.1 | 463.8 | 221.1 | 213.5 | 386.1 | 215.9 | 189.4 | 535.8 | 303.8 | 203.4 | 184.8 | 179.5 | 188.3 | 195.1 | 178.2 | 187.7 | 191.2
3055.1 | 2834.1 | -6.7 | 0 | 0 | 194.8 | 186.3 | 172.3 | 174 | 201.3 | 35.8 | 19.9 | 57.9 | 2.7 | 249.7 | 2.8 | 438.1 | 442.9 | 166.3 | 62.8 | 529.9 | 532.4 | 98.2 | 77.2 | 224.1 | 463.6 | 220.5 | 213.8 | 385.8 | 216 | 189.4 | 535.9 | 303.5 | 203.3 | 184.7 | 179.4 | 188.2 | 195 | 178.1 | 187.6 | 191.1
3056.1 | 2835.1 | -6.7 | 0 | 0 | 194.7 | 186.3 | 172.1 | 173.9 | 201.2 | 35.8 | 19.9 | 57.8 | 3.1 | 256.1 | 2.9 | 438.1 | 443.2 | 165.8 | 62.8 | 529.9 | 532.3 | 98.3 | 77.5 | 224.1 | 463.4 | 220.3 | 213.8 | 385.6 | 215.8 | 189.7 | 535.8 | 303.3 | 203.1 | 184.5 | 179.3 | 188.1 | 194.9 | 178 | 187.5 | 191
3057.1 | 2836.1 | -6.7 | 0 | 0 | 194.7 | 186.1 | 172 | 173.8 | 200.8 | 35.8 | 19.9 | 57.8 | 2.8 | 252.4 | 3 | 438.1 | 443.1 | 165.9 | 62.9 | 529.9 | 532.4 | 98.5 | 77.7 | 224 | 463.2 | 220 | 213.6 | 385.4 | 215.3 | 190.1 | 535.8 | 303.1 | 203 | 184.4 | 179.1 | 188 | 194.8 | 177.9 | 187.4 | 190.8
3058.1 | 2837.1 | -6.7 | 0 | 0 | 194.6 | 185.8 | 171.8 | 173.7 | 200.8 | 35.8 | 19.9 | 57.7 | 3 | 249.2 | 3.1 | 438 | 443.1 | 166.2 | 63.1 | 529.8 | 532.5 | 99.2 | 77.8 | 224 | 463 | 219.6 | 213.5 | 385.2 | 215.5 | 190.3 | 535.8 | 303 | 203 | 184.3 | 179 | 187.9 | 194.7 | 177.8 | 187.4 | 190.7
3059.1 | 2838.1 | -6.6 | 0 | 0 | 194.4 | 185.6 | 171.8 | 173.7 | 200.9 | 35.7 | 19.9 | 57.7 | 2.9 | 249 | 3 | 438 | 443.1 | 165.7 | 63.3 | 529.8 | 532.5 | 99.4 | 77.9 | 224 | 462.8 | 219.3 | 213.2 | 384.9 | 214.8 | 190 | 535.9 | 302.9 | 202.8 | 184.2 | 178.9 | 187.8 | 194.6 | 177.7 | 187.3 | 190.6
3060.1 | 2839.1 | -6 | 0 | 0 | 194.3 | 185.4 | 171.7 | 173.7 | 200.6 | 35.7 | 20 | 57.7 | 2.9 | 249.1 | 3 | 438 | 443.2 | 165.7 | 63.4 | 529.7 | 532.5 | 100.2 | 78 | 223.9 | 462.6 | 219 | 213.1 | 384.7 | 214.2 | 188.9 | 535.9 | 302.7 | 202.7 | 184.1 | 178.8 | 187.7 | 194.5 | 177.6 | 187.2 | 190.5
3061.1 | 2840.1 | -4.6 | 0 | 0 | 194.1 | 185.4 | 171.6 | 173.6 | 200.2 | 35.6 | 20 | 57.6 | 2.7 | 248.9 | 3.3 | 438 | 443.2 | 166.6 | 63.5 | 529.6 | 532.5 | 101.6 | 78.2 | 223.9 | 462.4 | 218.9 | 212.6 | 384.5 | 214.2 | 187.9 | 535.8 | 302.1 | 202.6 | 184 | 178.6 | 187.6 | 194.3 | 177.4 | 187.1 | 190.4
3062.1 | 2841.1 | -4.1 | 0 | 0 | 193.8 | 185.3 | 171.5 | 173.5 | 199.9 | 35.5 | 20 | 57.6 | 2.6 | 251.1 | 3.6 | 438 | 443.1 | 165.3 | 63.3 | 529.6 | 532.5 | 101.5 | 78.2 | 223.8 | 462.2 | 219.3 | 212.1 | 384.2 | 213.7 | 188.2 | 535.6 | 301.7 | 202.5 | 183.9 | 178.5 | 187.5 | 194.2 | 177.3 | 186.9 | 190.3
3063.1 | 2842.1 | -4.8 | 0 | 0 | 193.4 | 185.2 | 171.4 | 173.4 | 199.8 | 35.5 | 20 | 57.6 | 2.8 | 249.5 | 3.5 | 437.9 | 443 | 165.8 | 63.2 | 529.5 | 532.5 | 101.5 | 78.3 | 223.8 | 462 | 220.3 | 212 | 384 | 213.4 | 187.7 | 535.5 | 301.6 | 202.4 | 183.8 | 178.4 | 187.4 | 194.1 | 177.2 | 186.8 | 190.2
3064.1 | 2843.1 | -4.6 | 0 | 0 | 193.4 | 185 | 171.3 | 173.4 | 199.5 | 35.5 | 20 | 57.5 | 3.1 | 249.6 | 3.5 | 437.9 | 442.9 | 166.2 | 63.1 | 529.4 | 532.5 | 101.2 | 78.4 | 223.7 | 461.8 | 220.5 | 211.8 | 383.7 | 213.8 | 187.3 | 535.5 | 301.5 | 202.3 | 183.7 | 178.3 | 187.3 | 194 | 177.1 | 186.7 | 190.1
3065.1 | 2844.1 | -4.9 | 0 | 0 | 193.4 | 184.8 | 171.2 | 173.3 | 199.6 | 35.5 | 20 | 57.5 | 3 | 250 | 3.4 | 437.9 | 443.1 | 165.9 | 63.1 | 529.4 | 532.4 | 100.8 | 78.4 | 223.7 | 461.6 | 220.4 | 211.1 | 383.5 | 213.3 | 187 | 535.4 | 301.3 | 202.2 | 183.6 | 178.2 | 187.2 | 193.9 | 177.1 | 186.6 | 190
3066.1 | 2845.1 | -5.7 | 0 | 0 | 193.3 | 184.7 | 171.2 | 173.2 | 199.8 | 35.6 | 20 | 57.5 | 2.9 | 257.6 | 3.6 | 437.9 | 442.9 | 166.5 | 63 | 529.4 | 532.4 | 100.4 | 78.4 | 223.8 | 461.4 | 220.1 | 211.5 | 383.2 | 212.9 | 187.3 | 535.4 | 301.2 | 202.1 | 183.5 | 178.1 | 187.1 | 193.9 | 177 | 186.5 | 189.9
3067.1 | 2846.1 | -5.9 | 0 | 0 | 193.1 | 184.6 | 171.2 | 173.1 | 199.8 | 35.6 | 20 | 57.5 | 2.6 | 259.2 | 3.6 | 437.9 | 443 | 167.1 | 63 | 529.4 | 532.3 | 100.1 | 78.4 | 223.8 | 461.3 | 220 | 211.2 | 383 | 212.7 | 187.5 | 535.4 | 300.9 | 201.9 | 183.5 | 178 | 187 | 193.7 | 176.9 | 186.4 | 189.8
3068.1 | 2847.1 | -5.7 | 0 | 0 | 193.2 | 184.5 | 171.1 | 173 | 199.5 | 35.6 | 20 | 57.5 | 2.6 | 257.3 | 3.6 | 437.8 | 442.9 | 167.2 | 63.1 | 529.4 | 532.2 | 99.9 | 78.4 | 223.7 | 461.1 | 220.9 | 211.3 | 382.8 | 212.9 | 187.7 | 535.3 | 300.8 | 201.8 | 183.4 | 177.9 | 186.9 | 193.6 | 176.8 | 186.3 | 189.7
3069.1 | 2848.1 | -3.6 | 0 | 0 | 193.1 | 184.5 | 171 | 172.9 | 199.4 | 35.6 | 20 | 57.5 | 2.6 | 263.9 | 3.9 | 437.8 | 442.8 | 166.8 | 63 | 529.4 | 532.2 | 99.4 | 78.4 | 223.7 | 461 | 220.7 | 211.6 | 382.6 | 212.2 | 187.7 | 535.3 | 300.7 | 201.7 | 183.3 | 177.8 | 186.8 | 193.5 | 176.7 | 186.1 | 189.6
3070.1 | 2849.1 | -3.5 | 0 | 0 | 192.9 | 184.5 | 170.9 | 172.9 | 199.4 | 35.5 | 20 | 57.5 | 2.6 | 266.4 | 4.1 | 437.8 | 442.8 | 166.1 | 62.9 | 529.4 | 532.2 | 99.4 | 78.4 | 223.6 | 460.8 | 220.2 | 211.6 | 382.4 | 212.1 | 187.6 | 535.3 | 300.6 | 201.6 | 183.1 | 177.8 | 186.7 | 193.4 | 176.6 | 186 | 189.5
3071.1 | 2850.1 | -5 | 0 | 0 | 192.8 | 184.5 | 170.8 | 172.8 | 199.2 | 35.6 | 20 | 57.5 | 2.7 | 260.3 | 4.1 | 437.8 | 442.6 | 164.9 | 62.9 | 529.3 | 532.6 | 99.1 | 78.4 | 223.5 | 460.7 | 219.7 | 211.4 | 382.1 | 212 | 187.4 | 535.4 | 300.4 | 201.5 | 183 | 177.7 | 186.6 | 193.3 | 176.5 | 185.9 | 189.4
3072.1 | 2851.1 | -4.9 | 0 | 0 | 192.7 | 184.4 | 170.7 | 172.6 | 198.9 | 35.5 | 20 | 57.5 | 2.9 | 255.1 | 4.3 | 437.8 | 442.6 | 163.6 | 62.8 | 529.3 | 532.8 | 98.8 | 78.4 | 223.5 | 460.5 | 219.1 | 211.3 | 381.9 | 211.5 | 186.8 | 535.3 | 300.1 | 201.4 | 182.8 | 177.7 | 186.5 | 193.2 | 176.4 | 185.8 | 189.3
3073.1 | 2852.1 | -5.2 | 0 | 0 | 192.5 | 184.3 | 170.7 | 172.5 | 198.5 | 35.5 | 20 | 57.5 | 3.1 | 258.1 | 4.3 | 437.7 | 442.9 | 163.8 | 62.8 | 529.2 | 532.9 | 98.4 | 78.3 | 223.6 | 460.4 | 218.6 | 211.1 | 381.7 | 211.6 | 186.6 | 535.3 | 299.9 | 201.3 | 182.8 | 177.6 | 186.4 | 193.1 | 176.3 | 185.7 | 189.1
3074.1 | 2853.1 | -6 | 0 | 0 | 192.3 | 184.2 | 170.7 | 172.4 | 198.2 | 35.5 | 20 | 57.5 | 3.1 | 253.4 | 4.4 | 437.7 | 442.9 | 163.7 | 62.8 | 529.2 | 532.8 | 98.1 | 78.3 | 223.6 | 460.2 | 218.3 | 211 | 381.5 | 211.8 | 185.6 | 535.2 | 299.6 | 201.2 | 182.6 | 177.6 | 186.3 | 193 | 176.2 | 185.6 | 189
3075.1 | 2854.1 | -6.4 | 0 | 0 | 192.2 | 184.1 | 170.5 | 172.3 | 198.1 | 35.5 | 20 | 57.5 | 2.9 | 252.3 | 4.4 | 437.7 | 442.7 | 163.3 | 62.7 | 529.2 | 532.6 | 97.9 | 78.5 | 223.6 | 460 | 218.1 | 210.6 | 381.3 | 211.7 | 185.5 | 535 | 299.6 | 201.1 | 182.5 | 177.5 | 186.2 | 192.9 | 176.1 | 185.5 | 188.9
3076.1 | 2855.1 | -6.7 | 0 | 0 | 192.1 | 183.9 | 170.4 | 172.1 | 198 | 35.5 | 20 | 57.5 | 2.8 | 256 | 4.4 | 437.7 | 442.7 | 163.2 | 62.9 | 529.2 | 532.5 | 97.7 | 78.5 | 223.6 | 459.9 | 217.5 | 210.3 | 381.1 | 211.5 | 185.4 | 534.9 | 299.4 | 201 | 182.4 | 177.4 | 186.1 | 192.8 | 176 | 185.4 | 188.8
3077.1 | 2856.1 | -6.7 | 0 | 0 | 191.9 | 183.7 | 170.4 | 172 | 197.9 | 35.5 | 20 | 57.5 | 2.9 | 258.6 | 4.5 | 437.7 | 442.6 | 162.8 | 63 | 529.2 | 532.3 | 97.7 | 78.6 | 223.5 | 459.7 | 217 | 210.1 | 380.9 | 211.6 | 184.7 | 534.7 | 299 | 200.9 | 182.2 | 177.3 | 186 | 192.7 | 175.9 | 185.3 | 188.7
3078.1 | 2857.1 | -6.7 | 0 | 0 | 191.9 | 183.5 | 170.4 | 172 | 197.5 | 35.5 | 20 | 57.5 | 3.1 | 260.9 | 4.8 | 437.7 | 442.7 | 162.9 | 63 | 529.2 | 532.1 | 97.7 | 78.7 | 223.4 | 459.5 | 217.6 | 209.5 | 380.7 | 211.1 | 184.8 | 534.5 | 298.9 | 200.8 | 182.1 | 177.2 | 185.9 | 192.5 | 175.8 | 185.1 | 188.6
3079.1 | 2858.1 | -6.7 | 0 | 0 | 191.8 | 183.5 | 170.3 | 171.9 | 197.2 | 35.5 | 20 | 57.5 | 3.2 | 261.1 | 5.1 | 437.6 | 442.7 | 162.3 | 62.9 | 529.2 | 531.9 | 97.8 | 78.5 | 223.1 | 459.4 | 217.2 | 208.7 | 380.5 | 210.7 | 185 | 534.3 | 298.7 | 200.7 | 182 | 177.2 | 185.8 | 192.4 | 175.7 | 185 | 188.5
3080.1 | 2859.1 | -6.7 | 0 | 0 | 191.8 | 183.3 | 170.2 | 171.7 | 197.1 | 35.5 | 20 | 57.4 | 3.1 | 257.6 | 5.4 | 437.6 | 442.5 | 161 | 62.8 | 529.2 | 531.7 | 97.6 | 78.4 | 222.8 | 459.2 | 216.6 | 208.1 | 380.3 | 210.9 | 185.5 | 534.2 | 298.6 | 200.6 | 182 | 177.1 | 185.7 | 192.3 | 175.5 | 184.9 | 188.4
3081.1 | 2860.1 | -6.7 | 0 | 0 | 191.7 | 183.3 | 170 | 171.6 | 197 | 35.5 | 20 | 57.4 | 3 | 256.5 | 5.4 | 437.6 | 442.5 | 161.6 | 63 | 529.2 | 531.5 | 97.3 | 78.3 | 222.8 | 459 | 216.3 | 208.1 | 380.1 | 211 | 185.2 | 534.2 | 298.5 | 200.5 | 181.9 | 177 | 185.6 | 192.2 | 175.4 | 184.8 | 188.3
3082.1 | 2861.1 | -6.7 | 0 | 0 | 191.5 | 183.3 | 169.9 | 171.5 | 196.9 | 35.5 | 20 | 57.4 | 3.1 | 258 | 5.5 | 437.6 | 442.4 | 162 | 63.1 | 529.1 | 531.5 | 97.5 | 78.2 | 222.8 | 458.8 | 216.3 | 208.1 | 379.9 | 210.7 | 185.1 | 534 | 298.4 | 200.4 | 181.8 | 176.8 | 185.5 | 192.1 | 175.3 | 184.7 | 188.2
3083.1 | 2862.1 | -6.7 | 0 | 0 | 191.2 | 183.2 | 169.8 | 171.3 | 196.9 | 35.5 | 20 | 57.3 | 3.1 | 258.7 | 5.5 | 437.5 | 442.3 | 161.1 | 63 | 529.1 | 531.4 | 98.3 | 78.2 | 222.7 | 458.6 | 216.8 | 207.8 | 379.7 | 210.3 | 185 | 533.8 | 298.1 | 200.3 | 181.8 | 176.7 | 185.4 | 192 | 175.3 | 184.5 | 188.1
3084.1 | 2863.1 | -6.3 | 0 | 0 | 191 | 183.1 | 169.7 | 171.1 | 196.6 | 35.4 | 20 | 57.3 | 3 | 260.3 | 5.4 | 437.5 | 442.3 | 159.9 | 62.9 | 529 | 531.4 | 99.9 | 78.4 | 222.6 | 458.5 | 216.8 | 207.9 | 379.5 | 209.8 | 184.6 | 533.8 | 297.6 | 200.2 | 181.7 | 176.6 | 185.3 | 191.9 | 175.2 | 184.4 | 188
3085.1 | 2864.1 | -6.7 | 0 | 0 | 190.8 | 183 | 169.6 | 170.8 | 196.2 | 35.4 | 20 | 57.3 | 3.1 | 258 | 5.4 | 437.5 | 442.3 | 158.9 | 62.9 | 528.9 | 531.6 | 101.4 | 78.4 | 222.5 | 458.3 | 216.4 | 207.7 | 379.2 | 209.5 | 185 | 533.8 | 297.5 | 200.1 | 181.6 | 176.5 | 185.2 | 191.8 | 175.1 | 184.3 | 187.9
3086.1 | 2865.1 | -6.7 | 0 | 0 | 190.6 | 182.8 | 169.7 | 170.5 | 195.9 | 35.4 | 20 | 57.3 | 3.1 | 259.5 | 5.5 | 437.5 | 442.3 | 158.1 | 62.8 | 528.8 | 531.7 | 102.3 | 78.2 | 222.6 | 458.1 | 216.3 | 207.9 | 379 | 208.9 | 185.1 | 533.7 | 297.4 | 200 | 181.5 | 176.4 | 185.1 | 191.7 | 175 | 184.2 | 187.8
3087.1 | 2866.1 | -6.7 | 0 | 0 | 190.4 | 182.7 | 169.7 | 170.3 | 195.5 | 35.3 | 20 | 57.2 | 3 | 261.5 | 5.4 | 437.5 | 442.2 | 157.5 | 62.7 | 528.7 | 531.7 | 102 | 78.1 | 222.6 | 457.9 | 217.2 | 208.1 | 378.8 | 208.3 | 184.6 | 533.6 | 297.4 | 199.9 | 181.4 | 176.3 | 185 | 191.6 | 174.9 | 184 | 187.7
3088.1 | 2867.1 | -6.7 | 0 | 0 | 190.3 | 182.6 | 169.6 | 170.2 | 195.5 | 35.3 | 20 | 57.2 | 3 | 261.8 | 5.3 | 437.5 | 442.2 | 156.5 | 62.5 | 528.6 | 531.8 | 101.5 | 77.8 | 222.5 | 457.8 | 217.1 | 207.9 | 378.6 | 208.5 | 184.7 | 533.5 | 296.9 | 199.8 | 181.3 | 176.2 | 184.9 | 191.5 | 174.8 | 183.9 | 187.6
3089.1 | 2868.1 | -6.7 | 0 | 0 | 190.2 | 182.4 | 169.5 | 170.2 | 195.5 | 35.3 | 20 | 57.2 | 3 | 261.5 | 5.3 | 437.4 | 442.1 | 156.3 | 62.3 | 528.6 | 531.8 | 100.9 | 77.5 | 222.5 | 457.6 | 216.6 | 207.8 | 378.3 | 208.5 | 185.2 | 533.6 | 296.8 | 199.6 | 181.2 | 176.2 | 184.8 | 191.4 | 174.6 | 183.8 | 187.5
3090.1 | 2869.1 | -6.7 | 0 | 0 | 190 | 182.2 | 169.4 | 170.1 | 195.3 | 35.2 | 20 | 57.2 | 3 | 262.2 | 5.2 | 437.4 | 442.1 | 156.8 | 62.1 | 528.5 | 531.8 | 100.3 | 77.3 | 222.4 | 457.4 | 216.1 | 207.3 | 378.1 | 208.8 | 185.2 | 533.7 | 296.7 | 199.5 | 181.1 | 176.1 | 184.7 | 191.3 | 174.6 | 183.7 | 187.4
3091.1 | 2870.1 | -6.7 | 0 | 0 | 189.8 | 182.1 | 169.4 | 170.1 | 195.2 | 35.2 | 20 | 57.1 | 3.3 | 266.5 | 4.9 | 437.4 | 442.1 | 156.2 | 62 | 528.5 | 531.7 | 99.6 | 77.2 | 222.3 | 457.2 | 215.6 | 206.1 | 377.9 | 208.6 | 185.1 | 534 | 296.4 | 199.4 | 181 | 175.9 | 184.6 | 191.1 | 174.5 | 183.6 | 187.3
3092.1 | 2871.1 | -6.7 | 0 | 0 | 189.5 | 182 | 169.3 | 170 | 195.3 | 35.2 | 20 | 57.1 | 3.3 | 269.6 | 4.9 | 437.4 | 442.2 | 155.9 | 61.9 | 528.5 | 531.5 | 98.9 | 77.1 | 222.3 | 457 | 215.4 | 205.2 | 377.7 | 208.8 | 184.4 | 534.3 | 296.2 | 199.3 | 180.9 | 175.8 | 184.5 | 191 | 174.4 | 183.5 | 187.2
3093.1 | 2872.1 | -6.5 | 0 | 0 | 189.2 | 182 | 169.1 | 169.8 | 195.6 | 35.2 | 20 | 57.1 | 3.1 | 266.9 | 4.9 | 437.4 | 442.2 | 155.7 | 61.9 | 528.6 | 531.2 | 98.3 | 77.1 | 222.3 | 456.9 | 215.5 | 204.3 | 377.5 | 208.4 | 184 | 534.4 | 295.9 | 199.2 | 180.8 | 175.7 | 184.4 | 190.9 | 174.3 | 183.4 | 187.1
3094.1 | 2873.1 | -6.6 | 0 | 0 | 189.2 | 182.1 | 168.9 | 169.7 | 195.7 | 35.2 | 20 | 57 | 3.1 | 258 | 4.9 | 437.3 | 442.2 | 156.2 | 61.9 | 528.6 | 530.9 | 97.7 | 77.1 | 222.2 | 456.7 | 214.7 | 203.4 | 377.3 | 207.8 | 183.5 | 534.3 | 295.7 | 199.1 | 180.7 | 175.5 | 184.3 | 190.8 | 174.2 | 183.3 | 186.9
3095.1 | 2874.1 | -6.4 | 0 | 0 | 189.1 | 182 | 168.8 | 169.5 | 195.4 | 35.2 | 20 | 57 | 3.2 | 255.7 | 4.9 | 437.3 | 442.3 | 156.2 | 61.8 | 528.6 | 530.6 | 97.7 | 77 | 222.2 | 456.5 | 214.4 | 203.1 | 377.1 | 207.4 | 182.9 | 534.3 | 295.6 | 199 | 180.6 | 175.4 | 184.2 | 190.7 | 174.1 | 183.2 | 186.8
3096.1 | 2875.1 | -6.4 | 0 | 0 | 189 | 181.9 | 168.8 | 169.4 | 195.5 | 35.2 | 20 | 57 | 3.3 | 268.9 | 4.9 | 437.3 | 442.1 | 155 | 61.8 | 528.6 | 530.4 | 98.5 | 76.8 | 222.2 | 456.3 | 214.5 | 202.9 | 376.9 | 207 | 182.5 | 534.3 | 295.5 | 198.9 | 180.5 | 175.3 | 184.1 | 190.6 | 174.1 | 183.1 | 186.7
3097.1 | 2876.1 | -6.4 | 0 | 0 | 189 | 181.8 | 168.7 | 169.4 | 195.3 | 35.2 | 20 | 56.9 | 2.9 | 267.6 | 4.6 | 437.3 | 442.2 | 153.8 | 61.8 | 528.6 | 530.5 | 99.5 | 76.7 | 222.2 | 456.1 | 214.7 | 202.6 | 376.7 | 207.4 | 182 | 534.2 | 295.4 | 198.7 | 180.3 | 175.2 | 184 | 190.5 | 173.9 | 183 | 186.6
3098.1 | 2877.1 | -6.5 | 0 | 0 | 188.9 | 181.6 | 168.6 | 169.4 | 194.9 | 35.2 | 20 | 56.9 | 2.9 | 263.9 | 4.2 | 437.3 | 442.1 | 153.3 | 61.8 | 528.5 | 530.6 | 100.8 | 76.8 | 222.2 | 456 | 214.4 | 202.7 | 376.5 | 207.1 | 182.2 | 534.1 | 295.3 | 198.7 | 180.2 | 175.1 | 183.9 | 190.4 | 173.8 | 182.9 | 186.5
3099.1 | 2878.1 | -6.2 | 0 | 0 | 188.8 | 181.4 | 168.4 | 169.4 | 194.7 | 35.2 | 20 | 56.8 | 2.9 | 253.9 | 3.9 | 437.2 | 442.1 | 153 | 61.8 | 528.4 | 530.8 | 101.7 | 76.8 | 222.2 | 455.8 | 215.1 | 202.7 | 376.3 | 206 | 182.2 | 534 | 295.2 | 198.6 | 180.1 | 175 | 183.8 | 190.3 | 173.7 | 182.8 | 186.4
3100.1 | 2879.1 | -4.4 | 0 | 0 | 188.6 | 181.1 | 168.2 | 169.3 | 194.5 | 35.2 | 20 | 56.8 | 2.9 | 253 | 4.2 | 437.2 | 442.1 | 153.2 | 61.8 | 528.4 | 531.1 | 102.1 | 76.9 | 222.2 | 455.6 | 215.4 | 203.1 | 376.2 | 206 | 182.2 | 533.7 | 295.1 | 198.4 | 180 | 174.9 | 183.7 | 190.2 | 173.6 | 182.7 | 186.3
3101.1 | 2880.1 | -3.8 | 0 | 0 | 188.3 | 180.9 | 168.1 | 169.2 | 194.5 | 35.2 | 20 | 56.8 | 2.8 | 252.6 | 4.5 | 437.2 | 442 | 152 | 61.7 | 528.3 | 531.3 | 102.7 | 77 | 222.2 | 455.5 | 215.9 | 203.2 | 376 | 206.6 | 182 | 533.4 | 295 | 198.3 | 179.9 | 174.8 | 183.6 | 190.1 | 173.4 | 182.6 | 186.2
3102.1 | 2881.1 | -3.3 | 0 | 0 | 188.1 | 180.7 | 168.1 | 169.1 | 194.3 | 35.2 | 20 | 56.8 | 2.9 | 245.8 | 4.4 | 437.2 | 442 | 151.6 | 61.6 | 528.2 | 531.5 | 103.6 | 76.9 | 222.3 | 455.3 | 215.5 | 203 | 375.8 | 206.1 | 180.9 | 533.2 | 294.8 | 198.2 | 179.8 | 174.7 | 183.5 | 190 | 173.2 | 182.5 | 186.1
3103.1 | 2882.1 | -3.2 | 0 | 0 | 187.9 | 180.4 | 167.9 | 168.9 | 194.1 | 35.1 | 20 | 56.7 | 3.2 | 237.3 | 4.5 | 437.2 | 441.9 | 150.9 | 61.5 | 528.1 | 532.1 | 104.4 | 76.8 | 222.3 | 455.1 | 215.6 | 202.5 | 375.5 | 206.7 | 179.9 | 533.2 | 294.7 | 198.1 | 179.7 | 174.6 | 183.4 | 189.8 | 173.1 | 182.4 | 186
3104.1 | 2883.1 | -3.2 | 0 | 0 | 187.8 | 180.2 | 167.8 | 168.7 | 194.2 | 35.2 | 20 | 56.7 | 3 | 244.2 | 4.5 | 437.1 | 441.9 | 151 | 61.4 | 528.1 | 532.5 | 104.4 | 76.5 | 222.2 | 454.9 | 216.4 | 201.9 | 375.3 | 206.8 | 179.4 | 533.1 | 294.6 | 198 | 179.6 | 174.5 | 183.3 | 189.7 | 173 | 182.2 | 185.9
3105.1 | 2884.1 | -2.9 | 0 | 0 | 187.8 | 180 | 167.6 | 168.7 | 194.2 | 35.1 | 20 | 56.6 | 3.1 | 255.1 | 4.9 | 437.1 | 442.2 | 152.9 | 61.3 | 528 | 532.7 | 104.3 | 76.3 | 222.1 | 454.7 | 216.5 | 201.8 | 375.1 | 206.4 | 178.6 | 533 | 294.4 | 197.9 | 179.4 | 174.5 | 183.2 | 189.6 | 172.9 | 182.1 | 185.8
3106.1 | 2885.1 | -3.6 | 0 | 0 | 187.7 | 179.8 | 167.5 | 168.6 | 194.2 | 35.2 | 20 | 56.5 | 3 | 250.4 | 4.9 | 437.1 | 441.9 | 153.2 | 61.1 | 527.9 | 532.9 | 104.4 | 76.2 | 222 | 454.5 | 217.5 | 201.3 | 374.8 | 205.7 | 177.9 | 532.8 | 293.6 | 197.8 | 179.3 | 174.4 | 183.1 | 189.5 | 172.8 | 181.9 | 185.7
3107.1 | 2886.1 | -2.3 | 0 | 0 | 187.5 | 179.7 | 167.3 | 168.5 | 194 | 35.2 | 20 | 56.5 | 2.7 | 237.7 | 5.3 | 437.1 | 441.7 | 153.5 | 61 | 527.9 | 533.2 | 104.5 | 76.1 | 221.9 | 454.3 | 218.1 | 201.3 | 374.6 | 205.1 | 178.1 | 532.6 | 293.2 | 197.7 | 179.1 | 174.3 | 183 | 189.4 | 172.7 | 181.8 | 185.6
3108.1 | 2887.1 | -1.8 | 0 | 0 | 187.5 | 179.6 | 167.2 | 168.3 | 193.8 | 35.1 | 20 | 56.5 | 3.1 | 245 | 5.6 | 437.1 | 441.9 | 154.1 | 61 | 527.8 | 533.2 | 104.1 | 76.1 | 221.9 | 454.1 | 218.1 | 201.2 | 374.4 | 204.4 | 178.3 | 532.5 | 293.3 | 197.6 | 179 | 174.2 | 182.9 | 189.3 | 172.6 | 181.7 | 185.5
3109.1 | 2888.1 | -3.1 | 0 | 0 | 187.5 | 179.6 | 167 | 168.2 | 193.8 | 35.1 | 20 | 56.5 | 3.1 | 257.6 | 5.9 | 437 | 441.9 | 153.4 | 60.9 | 527.8 | 533.2 | 103.8 | 76.1 | 221.7 | 453.9 | 217.8 | 200.5 | 374.2 | 203.9 | 178.4 | 532.4 | 293.2 | 197.5 | 179 | 174 | 182.8 | 189.2 | 172.5 | 181.7 | 185.4
3110.1 | 2889.1 | -4.2 | 0 | 0 | 187.4 | 179.5 | 166.7 | 168.1 | 193.7 | 35.1 | 20 | 56.4 | 2.8 | 245.6 | 6 | 437 | 442 | 154.5 | 60.9 | 527.7 | 533 | 103.2 | 76 | 221.6 | 453.7 | 217.1 | 200.3 | 374 | 204.3 | 178.3 | 532.3 | 293.1 | 197.3 | 178.8 | 173.9 | 182.7 | 189.1 | 172.4 | 181.5 | 185.3
3111.1 | 2890.1 | -5.4 | 0 | 0 | 187.4 | 179.6 | 166.6 | 168.1 | 193.4 | 35.1 | 20 | 56.4 | 3.2 | 250.7 | 6 | 437 | 441.7 | 155.6 | 61 | 527.7 | 532.8 | 102.6 | 75.9 | 221.5 | 453.5 | 216.4 | 200.1 | 373.8 | 204.6 | 176.9 | 532.3 | 292.8 | 197.3 | 178.8 | 173.8 | 182.6 | 188.9 | 172.4 | 181.4 | 185.2
3112.1 | 2891.1 | -6.1 | 0 | 0 | 187.3 | 179.6 | 166.5 | 167.9 | 193.1 | 35.1 | 20 | 56.4 | 3.1 | 266.6 | 5.9 | 437 | 441.7 | 155 | 61.1 | 527.7 | 532.7 | 102.3 | 75.8 | 221.5 | 453.3 | 216.4 | 200 | 373.5 | 204.4 | 176.2 | 532.2 | 292.3 | 197.2 | 178.7 | 173.7 | 182.5 | 188.8 | 172.3 | 181.3 | 185.1
3113.1 | 2892.1 | -6.4 | 0 | 0 | 187.1 | 179.5 | 166.5 | 167.8 | 192.9 | 35.1 | 20 | 56.4 | 3.3 | 248.5 | 5.2 | 437 | 441.7 | 154.2 | 61.1 | 527.7 | 532.6 | 102 | 75.7 | 221.4 | 453.1 | 216.1 | 199.9 | 373.3 | 204 | 176 | 532.2 | 292.2 | 197.1 | 178.6 | 173.5 | 182.4 | 188.7 | 172.1 | 181.2 | 185
3114.1 | 2893.1 | -6.7 | 0 | 0 | 186.9 | 179.4 | 166.4 | 167.7 | 192.9 | 35.1 | 20 | 56.4 | 3.3 | 253.1 | 4.5 | 437 | 441.7 | 153.2 | 61.1 | 527.6 | 532.5 | 102.3 | 75.7 | 221.4 | 452.9 | 215.5 | 199.6 | 373.1 | 203.8 | 175.6 | 532.2 | 292.1 | 196.9 | 178.5 | 173.5 | 182.3 | 188.6 | 172 | 181.1 | 184.9
3115.1 | 2894.1 | -6.7 | 0 | 0 | 186.7 | 179.4 | 166.3 | 167.6 | 192.8 | 35.1 | 20 | 56.3 | 3.7 | 274 | 5 | 436.9 | 441.6 | 152.3 | 61.1 | 527.6 | 532.6 | 102.4 | 75.6 | 221.4 | 452.7 | 215 | 199.3 | 372.8 | 204.4 | 175.4 | 532.2 | 291.9 | 196.8 | 178.4 | 173.4 | 182.2 | 188.5 | 171.9 | 180.9 | 184.8
3116.1 | 2895.1 | -6.6 | 0 | 0 | 186.5 | 179.4 | 166.3 | 167.5 | 192.6 | 35.1 | 20 | 56.3 | 3.1 | 260.3 | 5.7 | 436.9 | 441.5 | 151.5 | 61 | 527.5 | 532.7 | 101.9 | 75.4 | 221.4 | 452.5 | 214.5 | 199.1 | 372.6 | 204.7 | 174.8 | 532.5 | 291.7 | 196.7 | 178.2 | 173.2 | 182.1 | 188.3 | 171.7 | 180.8 | 184.7
3117.1 | 2896.1 | -5.9 | 0 | 0 | 186.4 | 179.4 | 166.2 | 167.3 | 192.9 | 35 | 20 | 56.3 | 2.9 | 260.8 | 6.8 | 436.9 | 441.5 | 150.8 | 61 | 527.5 | 532.7 | 102.2 | 75.2 | 221.4 | 452.4 | 214.7 | 198.6 | 372.4 | 203.8 | 174.6 | 532.5 | 291.3 | 196.6 | 178.1 | 173.2 | 182 | 188.2 | 171.6 | 180.7 | 184.5
3118.1 | 2897.1 | -6.4 | 0 | 0 | 186.4 | 179.3 | 166.1 | 167.2 | 193.3 | 35 | 20 | 56.3 | 3.1 | 258.6 | 7.4 | 436.9 | 441.6 | 150.3 | 60.9 | 527.5 | 532.7 | 102.4 | 75 | 221.5 | 452.2 | 214.5 | 198.4 | 372.1 | 203.6 | 174.9 | 532.6 | 290.8 | 196.5 | 178 | 173 | 181.9 | 188.1 | 171.5 | 180.6 | 184.4
3119.1 | 2898.1 | -6.5 | 0 | 0 | 186.3 | 179.1 | 165.9 | 167.1 | 193.4 | 35 | 20 | 56.3 | 2.9 | 243.5 | 7.3 | 436.9 | 441.8 | 150.9 | 61 | 527.5 | 532.6 | 101.7 | 75 | 221.4 | 452 | 213.9 | 198.3 | 371.9 | 203.5 | 175.7 | 532.7 | 290.7 | 196.4 | 178 | 172.9 | 181.8 | 188 | 171.4 | 180.4 | 184.3
3120.1 | 2899.1 | -6.6 | 0 | 0 | 186.2 | 178.8 | 165.8 | 166.9 | 193.6 | 35.1 | 20 | 56.3 | 2.8 | 243 | 7.1 | 436.8 | 441.6 | 150.1 | 61 | 527.5 | 532.5 | 102.5 | 75 | 221.5 | 451.8 | 213.5 | 198.2 | 371.6 | 203.3 | 175.8 | 533 | 290.6 | 196.3 | 177.9 | 172.8 | 181.7 | 187.9 | 171.3 | 180.3 | 184.2
3121.1 | 2900.1 | -6.6 | 0 | 0 | 186.2 | 178.7 | 165.7 | 166.7 | 193.8 | 35.1 | 20 | 56.2 | 2.8 | 246.3 | 6.8 | 436.8 | 441.6 | 149.2 | 60.9 | 527.5 | 532.4 | 102.2 | 75 | 221.4 | 451.6 | 212.6 | 197.9 | 371.4 | 203.4 | 176.2 | 533.2 | 290.3 | 196.2 | 177.7 | 172.7 | 181.6 | 187.8 | 171.3 | 180.2 | 184.1
3122.1 | 2901.1 | -6.7 | 0 | 0 | 186.1 | 178.7 | 165.5 | 166.6 | 193.5 | 35.1 | 20 | 56.2 | 2.9 | 248.7 | 6.6 | 436.8 | 441.5 | 148 | 60.9 | 527.5 | 532.4 | 102.1 | 75 | 221.5 | 451.4 | 211.7 | 197.7 | 371.2 | 203.5 | 176.2 | 533.4 | 290 | 196.1 | 177.6 | 172.6 | 181.5 | 187.7 | 171.2 | 180.2 | 184
3123.1 | 2902.1 | -5.9 | 0 | 0 | 186 | 178.7 | 165.4 | 166.6 | 193.3 | 35.1 | 20 | 56.2 | 2.6 | 251.7 | 6.8 | 436.8 | 441.6 | 146.9 | 60.9 | 527.5 | 532.6 | 101.8 | 75.1 | 221.5 | 451.2 | 211.3 | 197.4 | 370.9 | 203 | 175.9 | 533.6 | 289.9 | 196 | 177.5 | 172.5 | 181.4 | 187.6 | 171.1 | 180 | 183.9
3124.1 | 2903.1 | -5.1 | 0 | 0 | 185.9 | 178.6 | 165.3 | 166.6 | 193 | 35.1 | 20 | 56.2 | 2.7 | 253.2 | 6.6 | 436.8 | 441.6 | 146.1 | 61 | 527.4 | 532.8 | 101.6 | 75.1 | 221.5 | 451.1 | 211.1 | 196.9 | 370.7 | 202.8 | 175.7 | 533.6 | 289.7 | 195.9 | 177.4 | 172.4 | 181.3 | 187.5 | 171 | 179.9 | 183.8
3125.1 | 2904.1 | -6 | 0 | 0 | 185.8 | 178.5 | 165.2 | 166.5 | 192.8 | 35 | 20.1 | 56.2 | 3 | 249.2 | 6.6 | 436.8 | 441.4 | 146.3 | 61 | 527.4 | 533.1 | 101.2 | 74.9 | 221.5 | 450.9 | 211.2 | 196.8 | 370.5 | 202.3 | 175.7 | 533.5 | 289.6 | 195.8 | 177.3 | 172.3 | 181.2 | 187.4 | 170.8 | 179.8 | 183.7
3126.1 | 2905.1 | -6.7 | 0 | 0 | 185.6 | 178.3 | 165.1 | 166.5 | 192.5 | 35 | 20.1 | 56.2 | 3.1 | 245.2 | 6.7 | 436.7 | 441.4 | 146.4 | 60.9 | 527.5 | 533.2 | 100.5 | 74.8 | 221.5 | 450.7 | 211.5 | 196.9 | 370.3 | 201.9 | 175.8 | 533.4 | 289.6 | 195.7 | 177.3 | 172.2 | 181.1 | 187.3 | 170.8 | 179.6 | 183.6
3127.1 | 2906.1 | -6.7 | 0 | 0 | 185.4 | 178.3 | 165.1 | 166.5 | 192.5 | 35 | 20.1 | 56.2 | 3 | 244.3 | 6.4 | 436.7 | 441.4 | 146.7 | 60.7 | 527.5 | 533.2 | 99.9 | 74.6 | 221.5 | 450.5 | 212 | 197 | 370.1 | 201.4 | 176 | 533.3 | 289.5 | 195.6 | 177.2 | 172 | 181 | 187.2 | 170.7 | 179.5 | 183.5
3128.1 | 2907.1 | -6.7 | 0 | 0 | 185.3 | 178.3 | 165.1 | 166.3 | 192.7 | 35 | 20.1 | 56.1 | 3.1 | 256.8 | 6.2 | 436.7 | 441.3 | 147.8 | 60.6 | 527.6 | 533.3 | 99.5 | 74.5 | 221.4 | 450.3 | 212.8 | 197.3 | 369.8 | 201.2 | 176.5 | 533.3 | 289.4 | 195.4 | 177.1 | 171.9 | 180.9 | 187.1 | 170.6 | 179.4 | 183.4
3129.1 | 2908.1 | -6.6 | 0 | 0 | 185.2 | 178.3 | 165.1 | 166.2 | 193.1 | 35.1 | 20.1 | 56.1 | 2.9 | 239.8 | 5.9 | 436.7 | 441.3 | 148 | 60.5 | 527.6 | 533.3 | 99 | 74.5 | 221.4 | 450.1 | 213.9 | 197.4 | 369.6 | 200.6 | 176.4 | 533.4 | 289.3 | 195.3 | 177 | 171.8 | 180.8 | 187 | 170.4 | 179.4 | 183.3
3130.1 | 2909.1 | -5.9 | 0 | 0 | 185 | 178.2 | 165.1 | 166.2 | 193.3 | 35 | 20.1 | 56.1 | 2.9 | 239.5 | 5.8 | 436.7 | 441.2 | 149 | 60.5 | 527.7 | 533.3 | 99 | 74.8 | 221.3 | 450 | 213.4 | 197.3 | 369.4 | 200 | 176.2 | 533.4 | 289.1 | 195.2 | 176.9 | 171.7 | 180.7 | 186.9 | 170.3 | 179.2 | 183.2
3131.1 | 2910.1 | -5.2 | 0 | 0 | 184.7 | 178 | 165.1 | 166.1 | 193.2 | 35 | 20.1 | 56.1 | 2.7 | 245.7 | 5.7 | 436.7 | 441.2 | 150 | 60.5 | 527.8 | 533.5 | 98.5 | 74.7 | 221.2 | 449.8 | 213.8 | 197.2 | 369.2 | 199.5 | 176.1 | 533.1 | 289 | 195 | 176.8 | 171.6 | 180.6 | 186.8 | 170.2 | 179.1 | 183.1
3132.1 | 2911.1 | -5.2 | 0 | 0 | 184.3 | 177.9 | 165 | 165.9 | 193 | 35 | 20.1 | 56.1 | 2.8 | 245.7 | 5.5 | 436.6 | 441.1 | 151.5 | 60.4 | 527.8 | 533.5 | 98.7 | 74.6 | 221 | 449.6 | 213.8 | 197.3 | 369 | 199.6 | 175.7 | 532.8 | 288.9 | 195 | 176.6 | 171.5 | 180.5 | 186.7 | 170.1 | 179 | 183
3133.1 | 2912.1 | -5.5 | 0 | 0 | 184.1 | 177.9 | 164.8 | 165.7 | 192.6 | 35 | 20.1 | 56 | 2.6 | 246.5 | 5.3 | 436.6 | 441.1 | 152.1 | 60.4 | 527.9 | 533.6 | 98.6 | 74.2 | 220.8 | 449.4 | 213.2 | 197.6 | 368.8 | 199.5 | 174.7 | 532.6 | 288.7 | 194.9 | 176.5 | 171.4 | 180.4 | 186.6 | 170 | 178.9 | 182.9
3134.1 | 2913.1 | -6.3 | 0 | 0 | 184.3 | 177.8 | 164.7 | 165.7 | 192.2 | 35 | 20.1 | 56 | 2.9 | 248.2 | 5.2 | 436.6 | 441.1 | 153.2 | 60.3 | 527.9 | 533.8 | 99.4 | 73.8 | 220.4 | 449.2 | 214 | 197.4 | 368.6 | 199.1 | 174.4 | 532.4 | 288.7 | 194.8 | 176.5 | 171.2 | 180.3 | 186.4 | 169.9 | 178.9 | 182.8
3135.1 | 2914.1 | -6.3 | 0 | 0 | 184.3 | 177.7 | 164.6 | 165.5 | 191.9 | 35 | 20.1 | 56 | 2.8 | 247.5 | 5.2 | 436.6 | 441.1 | 153.9 | 60.3 | 528 | 533.9 | 99.7 | 73.5 | 220.3 | 449.1 | 214 | 197.1 | 368.4 | 198.5 | 174.1 | 532.3 | 288.6 | 194.6 | 176.4 | 171.1 | 180.2 | 186.3 | 169.8 | 178.8 | 182.7
3136.1 | 2915.1 | -6.6 | 0 | 0 | 183.9 | 177.5 | 164.6 | 165.2 | 191.5 | 35 | 20.1 | 56 | 2.7 | 245.1 | 5 | 436.6 | 441.1 | 153.7 | 60.4 | 528 | 533.8 | 100 | 73.3 | 220.1 | 448.9 | 214 | 196.8 | 368.2 | 198 | 173.9 | 532.2 | 288.6 | 194.6 | 176.3 | 171 | 180.1 | 186.2 | 169.6 | 178.7 | 182.6
3137.1 | 2916.1 | -6.7 | 0 | 0 | 183.5 | 177.5 | 164.6 | 164.9 | 191.1 | 35 | 20.1 | 56 | 2.8 | 245.2 | 4.9 | 436.6 | 440.8 | 153.4 | 60.3 | 528 | 533.6 | 101.8 | 73.1 | 219.9 | 448.7 | 213.4 | 196.5 | 368 | 197.1 | 173.7 | 532.1 | 288.5 | 194.4 | 176.2 | 170.9 | 180 | 186.1 | 169.5 | 178.6 | 182.5
3138.1 | 2917.1 | -6.7 | 0 | 0 | 183.2 | 177.5 | 164.5 | 164.8 | 190.6 | 35 | 20.1 | 55.9 | 2.9 | 245.3 | 4.9 | 436.5 | 440.8 | 153.1 | 60.4 | 528 | 533.5 | 102.7 | 72.8 | 219.9 | 448.5 | 213.5 | 196.1 | 367.7 | 196.9 | 173.2 | 532.1 | 288.4 | 194.3 | 176.1 | 170.8 | 179.9 | 186 | 169.5 | 178.5 | 182.4
3139.1 | 2918.1 | -6.7 | 0 | 0 | 183 | 177.4 | 164.3 | 164.8 | 190.6 | 34.9 | 20.1 | 55.9 | 3 | 242 | 5 | 436.5 | 440.8 | 152.4 | 60.4 | 528 | 533.8 | 104 | 72.5 | 219.9 | 448.4 | 213.6 | 195.3 | 367.5 | 196.4 | 172.8 | 532.3 | 288.2 | 194.2 | 176.1 | 170.7 | 179.8 | 185.9 | 169.4 | 178.4 | 182.3
3140.1 | 2919.1 | -6.7 | 0 | 0 | 183.2 | 177.4 | 164.2 | 164.7 | 190.7 | 34.9 | 20.1 | 55.8 | 2.8 | 236.1 | 5.1 | 436.5 | 440.8 | 154.1 | 60.5 | 528 | 533.9 | 104.8 | 72.4 | 219.9 | 448.2 | 214 | 194.3 | 367.3 | 195.9 | 172.1 | 532.2 | 287.9 | 194.1 | 176 | 170.6 | 179.7 | 185.8 | 169.3 | 178.3 | 182.2
3141.1 | 2920.1 | -6.7 | 0 | 0 | 183.4 | 177.2 | 164 | 164.7 | 190.6 | 34.9 | 20.1 | 55.8 | 2.9 | 237.6 | 5.3 | 436.5 | 440.9 | 155.5 | 60.6 | 528 | 533.9 | 104.6 | 72.4 | 219.8 | 448 | 213.9 | 193.3 | 367.1 | 195.2 | 170.9 | 532.1 | 287.5 | 194 | 175.9 | 170.5 | 179.7 | 185.7 | 169.2 | 178.2 | 182.1
3142.1 | 2921.1 | -6.7 | 0 | 0 | 183.5 | 177 | 163.9 | 164.7 | 190.4 | 34.9 | 20.1 | 55.8 | 2.7 | 238.1 | 5.2 | 436.5 | 440.7 | 155 | 60.5 | 528 | 534.2 | 104.9 | 72.4 | 219.7 | 447.9 | 214 | 193 | 366.9 | 193.9 | 170.5 | 532 | 287.1 | 193.9 | 175.8 | 170.4 | 179.6 | 185.6 | 169.1 | 178.2 | 182
3143.1 | 2922.1 | -6.7 | 0 | 0 | 183.6 | 176.8 | 163.8 | 164.6 | 190 | 34.9 | 20.1 | 55.8 | 2.8 | 237.2 | 4.8 | 436.5 | 440.7 | 155 | 60.6 | 528 | 534.7 | 106.7 | 72.4 | 219.8 | 447.7 | 214.7 | 192.1 | 366.6 | 193.4 | 169.2 | 531.9 | 286.9 | 193.8 | 175.7 | 170.4 | 179.5 | 185.5 | 169 | 178.1 | 181.9
3144.1 | 2923.1 | -6.7 | 0 | 0 | 183.6 | 176.3 | 163.6 | 164.6 | 190.1 | 34.9 | 20.1 | 55.8 | 3.1 | 229.2 | 4.7 | 436.4 | 440.6 | 156.3 | 60.8 | 528 | 534.9 | 106.8 | 72.6 | 219.9 | 447.5 | 214.4 | 191.8 | 366.4 | 193.2 | 168.9 | 532 | 286.6 | 193.7 | 175.7 | 170.3 | 179.4 | 185.4 | 168.9 | 178 | 181.8
3145.1 | 2924.1 | -6.2 | 0 | 0 | 183.7 | 176 | 163.5 | 164.5 | 190.2 | 34.8 | 20.1 | 55.8 | 3.6 | 237.8 | 4.5 | 436.4 | 440.7 | 156.7 | 60.9 | 528 | 534.9 | 106.3 | 72.7 | 220 | 447.3 | 214.6 | 191.9 | 366.2 | 193.4 | 168.2 | 532.1 | 286.4 | 193.6 | 175.6 | 170.2 | 179.3 | 185.3 | 168.8 | 177.9 | 181.7
3146.1 | 2925.1 | -3.8 | 0 | 0 | 183.6 | 175.9 | 163.4 | 164.4 | 190.1 | 34.8 | 20.1 | 55.8 | 3.8 | 254.7 | 4.3 | 436.4 | 440.5 | 155.7 | 60.9 | 528.1 | 534.8 | 106.7 | 72.8 | 220.1 | 447.2 | 213.5 | 192 | 365.9 | 193.5 | 167.9 | 532.1 | 286.3 | 193.5 | 175.5 | 170.1 | 179.1 | 185.2 | 168.7 | 177.8 | 181.6
3147.1 | 2926.1 | -3 | 0 | 0 | 183.5 | 175.9 | 163.3 | 164.2 | 190.3 | 34.8 | 20.1 | 55.7 | 3.3 | 254.7 | 3.9 | 436.4 | 440.8 | 156.4 | 60.9 | 528.1 | 534.8 | 107.7 | 72.8 | 220.1 | 447 | 212.1 | 192.1 | 365.7 | 193 | 167.8 | 532.1 | 286.2 | 193.4 | 175.4 | 170.1 | 179 | 185.1 | 168.6 | 177.8 | 181.5
3148.1 | 2927.1 | -2.4 | 0 | 0 | 183.5 | 175.9 | 163.1 | 164 | 190.6 | 34.7 | 20.1 | 55.7 | 3.5 | 248.5 | 3.6 | 436.4 | 440.6 | 156.3 | 61.1 | 528 | 534.7 | 107.6 | 73.1 | 220.1 | 446.9 | 211.6 | 192.3 | 365.4 | 193.5 | 167.5 | 532 | 285.9 | 193.3 | 175.2 | 170 | 178.9 | 185 | 168.5 | 177.7 | 181.4
3149.1 | 2928.1 | -3 | 0 | 0 | 183.5 | 175.8 | 163.2 | 163.8 | 190.3 | 34.7 | 20.1 | 55.7 | 3.5 | 237.5 | 3.9 | 436.4 | 440.5 | 156 | 61.2 | 528 | 534.6 | 106.9 | 73.5 | 220.1 | 446.7 | 211.1 | 192.6 | 365.2 | 194.1 | 167.6 | 531.9 | 285.7 | 193.2 | 175 | 169.9 | 178.8 | 184.9 | 168.4 | 177.6 | 181.3
3150.1 | 2929.1 | -5 | 0 | 0 | 183.1 | 175.7 | 163.2 | 163.7 | 189.8 | 34.7 | 20.1 | 55.7 | 3.5 | 237.4 | 4.4 | 436.3 | 440.5 | 155.8 | 61.3 | 528.1 | 534.3 | 106.4 | 73.7 | 220.1 | 446.6 | 211.6 | 192.6 | 365 | 194.2 | 167.8 | 531.8 | 285.4 | 193.1 | 174.9 | 169.8 | 178.7 | 184.8 | 168.3 | 177.5 | 181.2
3151.1 | 2930.1 | -6 | 0 | 0 | 182.8 | 175.7 | 163.2 | 163.7 | 189.5 | 34.7 | 20.1 | 55.7 | 3.2 | 245.8 | 4.6 | 436.3 | 440.5 | 154.4 | 61.4 | 528.1 | 534.1 | 106.4 | 74 | 220.1 | 446.4 | 211.3 | 192.5 | 364.8 | 194.5 | 167.5 | 531.7 | 284.9 | 193 | 174.8 | 169.7 | 178.7 | 184.7 | 168.2 | 177.4 | 181.1
3152.1 | 2931.1 | -5.6 | 0 | 0 | 182.5 | 175.6 | 163.1 | 163.6 | 189.1 | 34.6 | 20.1 | 55.7 | 3.3 | 248.9 | 4.4 | 436.3 | 440.4 | 153.7 | 61.4 | 528.1 | 533.9 | 106.2 | 74.2 | 220.1 | 446.3 | 210.5 | 192.6 | 364.6 | 194.7 | 168 | 531.7 | 284.7 | 192.9 | 174.7 | 169.6 | 178.6 | 184.6 | 168.1 | 177.3 | 181
3153.1 | 2932.1 | -5.3 | 0 | 0 | 182.3 | 175.6 | 163 | 163.5 | 188.8 | 34.6 | 20.1 | 55.7 | 3.6 | 253 | 4.2 | 436.3 | 440.5 | 153.3 | 61.5 | 528.1 | 533.9 | 107.1 | 74.5 | 220.1 | 446.1 | 209.7 | 192.3 | 364.3 | 194.3 | 168.1 | 531.7 | 284.7 | 192.8 | 174.7 | 169.5 | 178.5 | 184.5 | 168 | 177.2 | 180.9
3154.1 | 2933.1 | -4.6 | 0 | 0 | 182.2 | 175.6 | 162.9 | 163.4 | 188.5 | 34.6 | 20.1 | 55.7 | 3.2 | 254 | 4.1 | 436.3 | 440.3 | 152.7 | 61.6 | 528.1 | 533.8 | 106.9 | 74.5 | 220.1 | 445.9 | 209.5 | 192 | 364.1 | 193.9 | 167.4 | 531.7 | 284.4 | 192.7 | 174.5 | 169.4 | 178.4 | 184.4 | 167.9 | 177.1 | 180.8
3155.1 | 2934.1 | -4.9 | 0 | 0 | 182.1 | 175.2 | 162.8 | 163.2 | 188.3 | 34.6 | 20.1 | 55.6 | 3.4 | 255 | 3.9 | 436.2 | 440.5 | 151.9 | 61.7 | 528 | 533.8 | 106.9 | 74.6 | 220.1 | 445.8 | 210.5 | 191.7 | 363.9 | 193.7 | 166.9 | 531.6 | 284.1 | 192.6 | 174.4 | 169.3 | 178.3 | 184.3 | 167.8 | 177 | 180.7
3156.1 | 2935.1 | -5.4 | 0 | 0 | 182.1 | 174.9 | 162.6 | 163.2 | 188.2 | 34.5 | 20.1 | 55.6 | 3.7 | 254.6 | 3.9 | 436.2 | 440.3 | 151.6 | 61.8 | 528 | 533.7 | 105.9 | 74.8 | 220.1 | 445.7 | 210.4 | 191.5 | 363.7 | 193.2 | 166.6 | 531.5 | 283.8 | 192.5 | 174.3 | 169.2 | 178.2 | 184.2 | 167.7 | 176.9 | 180.5
3157.1 | 2936.1 | -6 | 0 | 0 | 182 | 174.7 | 162.3 | 163.1 | 188.5 | 34.5 | 20.1 | 55.5 | 3.5 | 261.9 | 3.7 | 436.2 | 440.4 | 152 | 61.8 | 528 | 533.5 | 105 | 74.9 | 220 | 445.5 | 209.6 | 191.2 | 363.5 | 192.5 | 166.4 | 531.4 | 283.9 | 192.4 | 174.1 | 169.1 | 178.1 | 184.1 | 167.6 | 176.8 | 180.4
3158.1 | 2937.1 | -6.3 | 0 | 0 | 181.8 | 174.5 | 162.3 | 163 | 188.7 | 34.5 | 20.1 | 55.4 | 3.6 | 259.9 | 3.7 | 436.2 | 440.3 | 152.9 | 61.9 | 528 | 533.2 | 104.3 | 75.1 | 220 | 445.4 | 209.4 | 190.8 | 363.2 | 192.6 | 165.8 | 531.3 | 283.7 | 192.3 | 174.1 | 168.9 | 178 | 184 | 167.5 | 176.6 | 180.4
3159.1 | 2938.1 | -6.2 | 0 | 0 | 181.6 | 174.3 | 162.1 | 162.8 | 188.5 | 34.5 | 20.1 | 55.4 | 3.8 | 237.1 | 3.8 | 436.2 | 440.3 | 152.7 | 61.9 | 528 | 532.9 | 103.6 | 75.3 | 220 | 445.2 | 208.9 | 191.2 | 363 | 192.7 | 166.2 | 531.3 | 283 | 192.2 | 174 | 168.8 | 177.9 | 183.9 | 167.4 | 176.5 | 180.3
3160.1 | 2939.1 | -6.4 | 0 | 0 | 181.5 | 174.2 | 161.9 | 162.8 | 188.1 | 34.5 | 20.1 | 55.4 | 3.5 | 228.5 | 3.9 | 436.1 | 440.1 | 152 | 62 | 528 | 532.7 | 102.8 | 75.4 | 220 | 445.1 | 208.4 | 191.4 | 362.8 | 192.9 | 166.5 | 531.2 | 282.9 | 192.1 | 173.9 | 168.7 | 177.8 | 183.8 | 167.3 | 176.4 | 180.1
3161.1 | 2940.1 | -6.6 | 0 | 0 | 181.3 | 174.2 | 161.8 | 162.8 | 187.7 | 34.5 | 20.1 | 55.4 | 3.3 | 228.8 | 4.5 | 436.1 | 440.3 | 152.3 | 62 | 528 | 532.4 | 101.9 | 75.4 | 220 | 444.9 | 207.6 | 190.9 | 362.6 | 192.6 | 166.9 | 531 | 283 | 192 | 173.8 | 168.6 | 177.7 | 183.7 | 167.2 | 176.3 | 180
3162.1 | 2941.1 | -6.5 | 0 | 0 | 181.2 | 174.3 | 161.7 | 162.8 | 187.8 | 34.5 | 20.1 | 55.4 | 3.4 | 228.5 | 5 | 436.1 | 440.1 | 152.5 | 61.8 | 528 | 532.1 | 101.4 | 75.3 | 220 | 444.8 | 206.8 | 190.4 | 362.4 | 193.2 | 166.4 | 530.8 | 282.8 | 191.9 | 173.7 | 168.5 | 177.6 | 183.6 | 167.1 | 176.2 | 179.9
3163.1 | 2942.1 | -6.4 | 0 | 0 | 181.2 | 174.4 | 161.6 | 162.7 | 187.9 | 34.4 | 20.1 | 55.3 | 3.7 | 225.2 | 5.3 | 436.1 | 440.1 | 151.7 | 61.6 | 528 | 532.1 | 101 | 75.4 | 219.9 | 444.6 | 206 | 190.2 | 362.2 | 193.6 | 166.2 | 530.7 | 282.2 | 191.8 | 173.6 | 168.4 | 177.5 | 183.5 | 167 | 176.1 | 179.8
3164.1 | 2943.1 | -6.6 | 0 | 0 | 181.1 | 174.3 | 161.4 | 162.6 | 187.5 | 34.3 | 20.1 | 55.3 | 3.6 | 216.6 | 5.2 | 436.1 | 440.1 | 151.2 | 61.5 | 528 | 532.4 | 100.7 | 75.5 | 219.8 | 444.4 | 205 | 189.9 | 362 | 193.8 | 166.1 | 530.6 | 282.1 | 191.7 | 173.4 | 168.3 | 177.4 | 183.4 | 166.9 | 176 | 179.7
3165.1 | 2944.1 | -6.5 | 0 | 0 | 181 | 174.3 | 161.2 | 162.5 | 187 | 34.3 | 20.1 | 55.3 | 3.4 | 226.2 | 4.9 | 436 | 440 | 149.7 | 61.5 | 528 | 532.6 | 100.3 | 75.6 | 219.7 | 444.3 | 204.6 | 189.7 | 361.7 | 193.4 | 166 | 530.4 | 282.1 | 191.6 | 173.3 | 168.2 | 177.3 | 183.3 | 166.8 | 175.9 | 179.6
3166.1 | 2945.1 | -6.5 | 0 | 0 | 180.9 | 174.1 | 161.2 | 162.5 | 186.7 | 34.3 | 20.1 | 55.2 | 3.5 | 229 | 4.5 | 436 | 440.1 | 148.5 | 61.4 | 527.9 | 532.7 | 101.3 | 75.9 | 219.7 | 444.1 | 204.2 | 189.5 | 361.5 | 193.1 | 166 | 530.4 | 281.9 | 191.5 | 173.1 | 168.1 | 177.2 | 183.2 | 166.6 | 175.8 | 179.5
3167.1 | 2946.1 | -6.7 | 0 | 0 | 180.7 | 174 | 161.1 | 162.3 | 186.6 | 34.3 | 20.1 | 55.2 | 3.7 | 221.8 | 4.4 | 436 | 440.1 | 148.1 | 61.4 | 527.8 | 533 | 102.9 | 76.1 | 219.7 | 444 | 204 | 189.5 | 361.2 | 193 | 165.9 | 530.3 | 281.6 | 191.3 | 173 | 167.9 | 177.1 | 183.1 | 166.4 | 175.7 | 179.4
3168.1 | 2947.1 | -6.7 | 0 | 0 | 180.6 | 173.8 | 161 | 162.1 | 186.4 | 34.3 | 20.1 | 55.2 | 3.4 | 222.3 | 4.3 | 436 | 439.9 | 147.2 | 61.5 | 527.7 | 533.2 | 103.6 | 76.2 | 219.7 | 443.9 | 204.7 | 189.3 | 361 | 192.5 | 165.6 | 530.3 | 281.5 | 191.3 | 172.9 | 167.9 | 177 | 183 | 166.3 | 175.6 | 179.3
3169.1 | 2948.1 | -6.6 | 0 | 0 | 180.4 | 173.6 | 160.9 | 162 | 186.1 | 34.3 | 20.1 | 55.1 | 3.5 | 230.7 | 3.9 | 436 | 439.9 | 145.9 | 61.4 | 527.6 | 533.4 | 104.2 | 76.4 | 219.7 | 443.7 | 205.5 | 189.1 | 360.8 | 192.3 | 165.6 | 530.2 | 281.4 | 191.2 | 172.8 | 167.8 | 176.9 | 182.9 | 166.2 | 175.5 | 179.2
3170.1 | 2949.1 | -6.5 | 0 | 0 | 180.3 | 173.5 | 160.9 | 162 | 186.2 | 34.3 | 20.1 | 55.1 | 3.6 | 235.2 | 4 | 435.9 | 439.9 | 145.7 | 61.3 | 527.5 | 533.5 | 104 | 76.3 | 219.7 | 443.5 | 206.8 | 188.7 | 360.6 | 191.9 | 165.3 | 530.2 | 281.2 | 191.1 | 172.8 | 167.7 | 176.8 | 182.8 | 166.1 | 175.4 | 179.1
3171.1 | 2950.1 | -6.3 | 0 | 0 | 180.3 | 173.4 | 160.8 | 162 | 186 | 34.3 | 20.2 | 55.1 | 3.5 | 229.4 | 4.2 | 435.9 | 440 | 146.7 | 61.2 | 527.4 | 533.7 | 103.6 | 76 | 219.7 | 443.4 | 207.6 | 188.4 | 360.4 | 191 | 165 | 530.2 | 281 | 191 | 172.7 | 167.6 | 176.7 | 182.6 | 166 | 175.2 | 179
3172.1 | 2951.1 | -6.3 | 0 | 0 | 180.3 | 173.3 | 160.8 | 161.9 | 186.1 | 34.3 | 20.1 | 55 | 3.4 | 227.8 | 4.2 | 435.9 | 439.9 | 146.5 | 60.9 | 527.3 | 534 | 103 | 75.6 | 219.6 | 443.2 | 208.1 | 188.4 | 360.2 | 190.7 | 165.4 | 530.3 | 280.9 | 190.9 | 172.6 | 167.5 | 176.6 | 182.5 | 165.8 | 175.1 | 178.9
3173.1 | 2952.1 | -6.5 | 0 | 0 | 180.3 | 173.1 | 160.7 | 161.7 | 186.5 | 34.3 | 20.2 | 55 | 3.5 | 231.9 | 4 | 435.9 | 439.8 | 146.5 | 60.7 | 527.2 | 534.6 | 102.9 | 75.3 | 219.6 | 443.1 | 208.4 | 188.2 | 359.9 | 190.4 | 165.3 | 530.4 | 280.8 | 190.7 | 172.5 | 167.4 | 176.5 | 182.4 | 165.7 | 175 | 178.8
3174.1 | 2953.1 | -6.7 | 0 | 0 | 180.3 | 173.1 | 160.5 | 161.6 | 186.4 | 34.3 | 20.2 | 54.9 | 3.7 | 238.6 | 3.9 | 435.9 | 439.7 | 146.4 | 60.5 | 527.1 | 534.8 | 102.8 | 75.3 | 219.4 | 442.9 | 209.4 | 187.9 | 359.7 | 189.9 | 165.3 | 530.4 | 280.6 | 190.7 | 172.4 | 167.3 | 176.4 | 182.3 | 165.6 | 174.9 | 178.7
3175.1 | 2954.1 | -6.7 | 0 | 0 | 180.1 | 172.9 | 160.4 | 161.6 | 186.1 | 34.2 | 20.2 | 54.9 | 3.5 | 239.2 | 3.8 | 435.8 | 439.8 | 147.4 | 60.6 | 527 | 534.7 | 102.9 | 75.4 | 219.3 | 442.8 | 210.5 | 187.6 | 359.4 | 189.8 | 164.6 | 530.5 | 280.3 | 190.5 | 172.3 | 167.2 | 176.3 | 182.2 | 165.5 | 174.8 | 178.6
3176.1 | 2955.1 | -6.7 | 0 | 0 | 180.1 | 172.7 | 160.2 | 161.5 | 186.3 | 34.2 | 20.2 | 54.8 | 3.4 | 237.2 | 3.8 | 435.8 | 439.6 | 146.8 | 60.7 | 526.9 | 534.6 | 103.2 | 75.3 | 219.3 | 442.6 | 210.8 | 187.5 | 359.2 | 189.9 | 164.9 | 530.6 | 279.8 | 190.4 | 172.1 | 167 | 176.2 | 182.1 | 165.4 | 174.7 | 178.5
3177.1 | 2956.1 | -6.7 | 0 | 0 | 180 | 172.6 | 160 | 161.4 | 186.7 | 34.2 | 20.2 | 54.7 | 3.9 | 236.2 | 3.6 | 435.8 | 439.6 | 145.8 | 60.6 | 526.8 | 534.4 | 103.8 | 75.3 | 219.3 | 442.4 | 211.3 | 187.1 | 359 | 189.5 | 165.3 | 530.7 | 279.8 | 190.3 | 172 | 166.9 | 176.1 | 182 | 165.3 | 174.6 | 178.4
3178.1 | 2957.1 | -6.7 | 0 | 0 | 179.9 | 172.6 | 159.9 | 161.3 | 186.6 | 34.2 | 20.2 | 54.7 | 3.8 | 234.3 | 3.5 | 435.8 | 439.7 | 144.7 | 60.4 | 526.8 | 534.2 | 104.2 | 74.9 | 219.4 | 442.3 | 211.6 | 186.7 | 358.8 | 189.4 | 165.6 | 530.9 | 279.7 | 190.2 | 171.9 | 166.9 | 176 | 181.9 | 165.3 | 174.5 | 178.3
3179.1 | 2958.1 | -6.7 | 0 | 0 | 179.9 | 172.6 | 159.8 | 161.1 | 186.2 | 34.1 | 20.2 | 54.6 | 3.8 | 233 | 3.4 | 435.8 | 439.7 | 144.9 | 60.2 | 526.7 | 534.1 | 103.2 | 74.5 | 219.4 | 442.1 | 211.8 | 186.3 | 358.6 | 188.8 | 165.3 | 530.9 | 279.5 | 190.1 | 171.8 | 166.8 | 175.9 | 181.8 | 165.2 | 174.4 | 178.2
3180.1 | 2959.1 | -6.6 | 0 | 0 | 179.8 | 172.5 | 159.8 | 161 | 185.8 | 34.1 | 20.2 | 54.6 | 3.8 | 235.4 | 3.1 | 435.8 | 439.7 | 145.1 | 59.9 | 526.7 | 533.9 | 102.4 | 74.3 | 219.3 | 441.9 | 211.8 | 186.1 | 358.4 | 188.5 | 165 | 530.9 | 279.4 | 190 | 171.7 | 166.7 | 175.8 | 181.7 | 165.1 | 174.3 | 178.1
3181.1 | 2960.1 | -6.6 | 0 | 0 | 179.7 | 172.4 | 159.8 | 161 | 185.9 | 34 | 20.2 | 54.5 | 3.7 | 244.2 | 2.7 | 435.7 | 439.7 | 144.4 | 59.8 | 526.7 | 533.7 | 102 | 73.9 | 219.3 | 441.8 | 212.7 | 185.9 | 358.2 | 188.4 | 165.3 | 530.8 | 279.1 | 189.9 | 171.6 | 166.6 | 175.7 | 181.6 | 164.9 | 174.2 | 178
3182.1 | 2961.1 | -6.7 | 0 | 0 | 179.6 | 172.3 | 159.6 | 161 | 186.3 | 34 | 20.2 | 54.5 | 3.4 | 255.2 | 2.5 | 435.7 | 439.5 | 143.6 | 59.5 | 526.7 | 533.7 | 102.3 | 73.7 | 219.2 | 441.6 | 212.8 | 185.8 | 358 | 188.5 | 164.9 | 530.7 | 278.9 | 189.8 | 171.6 | 166.5 | 175.6 | 181.5 | 164.8 | 174.1 | 177.9
3183.1 | 2962.1 | -6.6 | 0 | 0 | 179.5 | 172.1 | 159.4 | 160.9 | 186.2 | 34 | 20.2 | 54.5 | 3.5 | 260.2 | 2.5 | 435.7 | 439.5 | 142.5 | 59.4 | 526.7 | 533.4 | 102.7 | 73.6 | 219.1 | 441.4 | 213.1 | 185.7 | 357.8 | 188.2 | 164.5 | 530.6 | 278.7 | 189.7 | 171.5 | 166.4 | 175.5 | 181.4 | 164.7 | 174 | 177.8
3184.1 | 2963.1 | -6.6 | 0 | 0 | 179.5 | 171.9 | 159.3 | 160.7 | 185.9 | 34 | 20.2 | 54.4 | 3.7 | 260.4 | 2.7 | 435.7 | 439.6 | 142.3 | 59.4 | 526.6 | 533.1 | 103.4 | 73.5 | 219.1 | 441.2 | 213.3 | 185.8 | 357.5 | 187.9 | 164.6 | 530.5 | 278.6 | 189.6 | 171.3 | 166.3 | 175.4 | 181.3 | 164.5 | 173.9 | 177.7
3185.1 | 2964.1 | -6.5 | 0 | 0 | 179.5 | 171.9 | 159.3 | 160.4 | 185.5 | 33.9 | 20.2 | 54.4 | 3.4 | 261 | 3.1 | 435.7 | 439.4 | 142 | 59.4 | 526.6 | 532.9 | 103.6 | 73.4 | 219.2 | 441.1 | 214.1 | 185.7 | 357.3 | 187.8 | 164.2 | 530.4 | 278.6 | 189.5 | 171.2 | 166.2 | 175.3 | 181.2 | 164.5 | 173.7 | 177.6
3186.1 | 2965.1 | -6.4 | 0 | 0 | 179.5 | 171.8 | 159.1 | 160.2 | 185.2 | 33.9 | 20.2 | 54.4 | 3.9 | 259 | 3.5 | 435.6 | 439.4 | 141.5 | 59.4 | 526.6 | 532.8 | 103.9 | 73.3 | 219.2 | 440.9 | 213.9 | 185.4 | 357 | 187.7 | 164.1 | 530.3 | 278.5 | 189.3 | 171.1 | 166.1 | 175.3 | 181.1 | 164.4 | 173.6 | 177.5
3187.1 | 2966.1 | -6.3 | 0 | 0 | 179.5 | 171.7 | 159.1 | 160.1 | 185.1 | 33.9 | 20.2 | 54.3 | 3.6 | 256.5 | 3.9 | 435.6 | 439.3 | 140.7 | 59.3 | 526.5 | 532.9 | 104.2 | 73 | 219.3 | 440.7 | 213 | 185 | 356.8 | 187.5 | 163.5 | 530.2 | 278.3 | 189.3 | 171 | 165.9 | 175.2 | 181 | 164.3 | 173.4 | 177.4
3188.1 | 2967.1 | -6.2 | 0 | 0 | 179.3 | 171.6 | 159 | 160 | 185.1 | 33.9 | 20.2 | 54.3 | 3.4 | 264.1 | 4.1 | 435.6 | 439.2 | 139.6 | 59.2 | 526.5 | 532.9 | 105 | 72.8 | 219.3 | 440.5 | 212.7 | 184.5 | 356.5 | 187 | 162.7 | 530.1 | 278.2 | 189.1 | 170.9 | 165.9 | 175.1 | 180.8 | 164.2 | 173.3 | 177.3
3189.1 | 2968.1 | -6.2 | 0 | 0 | 178.9 | 171.6 | 158.9 | 159.8 | 185 | 33.9 | 20.2 | 54.3 | 3.5 | 266 | 4.3 | 435.6 | 439.3 | 138.5 | 59.2 | 526.5 | 532.8 | 105.8 | 72.7 | 219.4 | 440.3 | 213 | 183.9 | 356.3 | 186.1 | 162 | 530 | 277.8 | 189 | 170.9 | 165.8 | 175 | 180.7 | 164 | 173.1 | 177.2
3190.1 | 2969.1 | -6.4 | 0 | 0 | 178.6 | 171.4 | 158.9 | 159.7 | 184.6 | 33.8 | 20.2 | 54.3 | 3.6 | 265.3 | 4.4 | 435.6 | 439.3 | 137.7 | 59.1 | 526.4 | 532.7 | 106.2 | 72.8 | 219.3 | 440.2 | 212.7 | 183.4 | 356.1 | 185.9 | 161.5 | 529.9 | 277.5 | 189 | 170.8 | 165.6 | 174.9 | 180.6 | 163.9 | 173 | 177.1
3191.1 | 2970.1 | -6.5 | 0 | 0 | 178.5 | 171.2 | 158.8 | 159.6 | 184.4 | 33.8 | 20.2 | 54.3 | 3.6 | 275.4 | 4.2 | 435.6 | 439.2 | 136.6 | 59 | 526.4 | 532.7 | 106.2 | 72.8 | 219.3 | 440 | 212.3 | 183 | 355.9 | 185.2 | 161.7 | 529.9 | 277.5 | 188.9 | 170.7 | 165.5 | 174.8 | 180.5 | 163.7 | 172.9 | 177
3192.1 | 2971.1 | -6.5 | 0 | 0 | 178.3 | 171.1 | 158.7 | 159.4 | 184.3 | 33.8 | 20.2 | 54.3 | 3.8 | 285.1 | 4.1 | 435.5 | 439.2 | 135.5 | 59 | 526.4 | 532.6 | 105.6 | 72.8 | 219.4 | 439.8 | 211.4 | 182.7 | 355.7 | 185 | 160.8 | 530.2 | 277.2 | 188.7 | 170.5 | 165.5 | 174.7 | 180.4 | 163.6 | 172.8 | 176.9
3193.1 | 2972.1 | -6.5 | 0 | 0 | 178.2 | 171 | 158.6 | 159.4 | 184 | 33.7 | 20.2 | 54.2 | 3.7 | 273.6 | 3.9 | 435.5 | 439.2 | 135 | 59 | 526.4 | 532.4 | 105.1 | 72.8 | 219.3 | 439.6 | 211.2 | 182.2 | 355.4 | 184.2 | 160 | 530.1 | 276.8 | 188.6 | 170.4 | 165.3 | 174.6 | 180.3 | 163.5 | 172.7 | 176.8
3194.1 | 2973.1 | -6.4 | 0 | 0 | 178.2 | 170.9 | 158.5 | 159.3 | 183.8 | 33.7 | 20.2 | 54.2 | 3.1 | 253.2 | 3.8 | 435.5 | 439.3 | 136.3 | 58.9 | 526.3 | 532.3 | 104.5 | 72.8 | 219.2 | 439.4 | 211 | 182 | 355.2 | 184 | 159.7 | 530.1 | 276.4 | 188.5 | 170.3 | 165.2 | 174.5 | 180.2 | 163.4 | 172.6 | 176.7
3195.1 | 2974.1 | -6.3 | 0 | 0 | 178.2 | 170.8 | 158.4 | 159.2 | 183.7 | 33.7 | 20.2 | 54.2 | 3.1 | 251.1 | 3.8 | 435.5 | 439.2 | 138.2 | 58.8 | 526.4 | 532.2 | 103.6 | 72.7 | 219.1 | 439.3 | 211.1 | 181.8 | 355 | 184 | 159.3 | 530.2 | 276 | 188.4 | 170.1 | 165.1 | 174.3 | 180.1 | 163.4 | 172.5 | 176.6
3196.1 | 2975.1 | -6.3 | 0 | 0 | 178 | 170.7 | 158.3 | 159.2 | 183.7 | 33.7 | 20.2 | 54.1 | 3.5 | 256.3 | 3.6 | 435.5 | 439.1 | 138.9 | 58.9 | 526.4 | 532 | 103.5 | 72.8 | 219 | 439.1 | 211.1 | 181.5 | 354.8 | 184 | 158.7 | 530.2 | 275.8 | 188.3 | 170 | 165 | 174.3 | 180 | 163.2 | 172.4 | 176.5
3197.1 | 2976.1 | -5.9 | 0 | 0 | 177.5 | 170.6 | 158.1 | 159.1 | 183.5 | 33.7 | 20.2 | 54.1 | 3.7 | 250 | 3.5 | 435.4 | 438.9 | 138 | 59 | 526.4 | 531.9 | 104.6 | 72.7 | 219 | 438.9 | 210.8 | 181.3 | 354.5 | 183.9 | 158.5 | 530.4 | 275.6 | 188.2 | 169.9 | 164.9 | 174.1 | 179.9 | 163.1 | 172.3 | 176.4
3198.1 | 2977.1 | -5.9 | 0 | 0 | 177.3 | 170.5 | 158.1 | 159.1 | 183.3 | 33.7 | 20.2 | 54.1 | 3.6 | 247.9 | 3.5 | 435.4 | 439 | 137.9 | 58.9 | 526.4 | 531.7 | 105.2 | 72.4 | 219 | 438.7 | 209.8 | 181.1 | 354.2 | 184.2 | 158.7 | 530.5 | 275.5 | 188.1 | 169.8 | 164.8 | 174.1 | 179.8 | 163 | 172.2 | 176.3
3199.1 | 2978.1 | -6.1 | 0 | 0 | 177.2 | 170.4 | 157.9 | 159 | 183.3 | 33.7 | 20.2 | 54.1 | 3.4 | 240.9 | 3.4 | 435.4 | 439 | 138.3 | 58.9 | 526.4 | 531.6 | 106.4 | 72.3 | 218.8 | 438.5 | 208.9 | 180.7 | 353.9 | 184.5 | 157.5 | 530.7 | 275.3 | 188 | 169.6 | 164.7 | 174 | 179.6 | 162.9 | 172 | 176.2
3200.1 | 2979.1 | -6.2 | 0 | 0 | 177.1 | 170.3 | 157.8 | 158.9 | 183.3 | 33.7 | 20.2 | 54 | 3.5 | 240 | 3.1 | 435.4 | 439 | 139 | 58.9 | 526.4 | 531.7 | 105.3 | 72 | 218.7 | 438.3 | 208.1 | 180.2 | 353.6 | 184.8 | 156.5 | 530.8 | 274.9 | 187.9 | 169.4 | 164.5 | 173.9 | 179.5 | 162.8 | 171.9 | 176.1
3201.1 | 2980.1 | -6.4 | 0 | 0 | 177.1 | 170.1 | 157.7 | 158.7 | 183.2 | 33.7 | 20.2 | 54 | 4 | 247.6 | 3 | 435.4 | 439 | 139.3 | 58.9 | 526.4 | 532.1 | 106.3 | 71.9 | 218.6 | 438.1 | 207.7 | 180 | 353.4 | 184.2 | 156.2 | 530.8 | 274.8 | 187.8 | 169.3 | 164.4 | 173.8 | 179.4 | 162.6 | 171.8 | 176
3202.1 | 2981.1 | -6.5 | 0 | 0 | 177 | 170 | 157.6 | 158.5 | 183.3 | 33.7 | 20.2 | 53.9 | 3.6 | 252.2 | 3 | 435.4 | 438.9 | 140.3 | 58.9 | 526.4 | 532.3 | 105.7 | 71.7 | 218.6 | 437.9 | 208.2 | 179.5 | 353.1 | 183.9 | 155.7 | 530.8 | 274.7 | 187.7 | 169.2 | 164.3 | 173.7 | 179.3 | 162.5 | 171.7 | 175.9
3203.1 | 2982.1 | -6.7 | 0 | 0 | 176.9 | 169.8 | 157.6 | 158.4 | 183.4 | 33.7 | 20.2 | 53.9 | 3.5 | 244.8 | 2.8 | 435.3 | 438.8 | 140.4 | 58.8 | 526.5 | 532.2 | 105.3 | 71.6 | 218.5 | 437.7 | 209 | 179 | 352.9 | 183.8 | 154.9 | 530.8 | 274.5 | 187.6 | 169.1 | 164.2 | 173.6 | 179.2 | 162.3 | 171.6 | 175.8
3204.1 | 2983.1 | -6.7 | 0 | 0 | 176.8 | 169.7 | 157.4 | 158.2 | 183.5 | 33.7 | 20.2 | 53.9 | 3.5 | 235.5 | 2.6 | 435.3 | 438.7 | 140.1 | 58.7 | 526.5 | 532.1 | 105.4 | 71.4 | 218.3 | 437.5 | 208.3 | 178.6 | 352.6 | 184.3 | 154.2 | 531.1 | 274 | 187.5 | 169 | 164.1 | 173.5 | 179.1 | 162.2 | 171.5 | 175.7
3205.1 | 2984.1 | -6.5 | 0 | 0 | 176.6 | 169.6 | 157.3 | 158.1 | 183.5 | 33.7 | 20.2 | 53.9 | 3.4 | 231.1 | 2.5 | 435.3 | 438.7 | 138.9 | 58.7 | 526.5 | 532.1 | 104.9 | 71.2 | 218.3 | 437.4 | 207.8 | 178.1 | 352.4 | 184.7 | 154.1 | 531.3 | 273.7 | 187.4 | 168.9 | 163.9 | 173.4 | 179 | 162 | 171.4 | 175.6
3206.1 | 2985.1 | -6.4 | 0 | 0 | 176.3 | 169.6 | 157.2 | 158 | 183.6 | 33.7 | 20.2 | 53.8 | 3.5 | 231.1 | 2.4 | 435.3 | 438.8 | 139.3 | 58.6 | 526.6 | 532.1 | 104.5 | 71.1 | 218.2 | 437.2 | 208.6 | 177.7 | 352.1 | 184.3 | 153.4 | 531.2 | 273.5 | 187.3 | 168.8 | 163.8 | 173.3 | 178.9 | 161.9 | 171.3 | 175.5
3207.1 | 2986.1 | -6.7 | 0 | 0 | 175.9 | 169.6 | 157.2 | 158 | 183.5 | 33.7 | 20.2 | 53.8 | 3.6 | 230.5 | 2.4 | 435.3 | 438.7 | 139.6 | 58.5 | 526.6 | 531.9 | 104.7 | 71.2 | 218.1 | 437 | 208.5 | 177.3 | 351.8 | 183.7 | 153.2 | 531.1 | 273.2 | 187.1 | 168.7 | 163.7 | 173.2 | 178.8 | 161.8 | 171.2 | 175.4
3208.1 | 2987.1 | -6.7 | 0 | 0 | 175.7 | 169.5 | 157.1 | 158 | 183.1 | 33.7 | 20.2 | 53.8 | 3.8 | 228.8 | 2.6 | 435.2 | 438.7 | 141.1 | 58.6 | 526.7 | 531.9 | 104.6 | 71.3 | 218.2 | 436.8 | 208.7 | 176.9 | 351.6 | 183.3 | 152.7 | 531.1 | 272.8 | 187.1 | 168.6 | 163.5 | 173.1 | 178.7 | 161.7 | 171.1 | 175.3
3209.1 | 2988.1 | -6.8 | 0 | 0 | 175.4 | 169.4 | 156.9 | 157.9 | 182.6 | 33.7 | 20.2 | 53.8 | 4 | 230.7 | 2.8 | 435.2 | 438.7 | 141.8 | 58.9 | 526.8 | 532.5 | 103.3 | 71.3 | 218.2 | 436.6 | 209.3 | 176.5 | 351.4 | 182.6 | 152.4 | 530.9 | 272.7 | 187 | 168.5 | 163.4 | 173 | 178.5 | 161.6 | 171 | 175.2
3210.1 | 2989.1 | -6.7 | 0 | 0 | 175.4 | 169.2 | 156.7 | 157.8 | 182.4 | 33.7 | 20.2 | 53.8 | 3.8 | 230.1 | 2.8 | 435.2 | 438.7 | 143 | 59.1 | 526.9 | 532.8 | 102.6 | 71.5 | 218.2 | 436.5 | 209.6 | 176.3 | 351.1 | 182.3 | 152.4 | 530.7 | 272.2 | 186.9 | 168.3 | 163.3 | 172.9 | 178.4 | 161.5 | 170.9 | 175.1
3211.1 | 2990.1 | -6.7 | 0 | 0 | 175.5 | 169.1 | 156.7 | 157.7 | 182.5 | 33.7 | 20.2 | 53.7 | 3.9 | 228.6 | 2.9 | 435.2 | 438.5 | 142.3 | 59.2 | 527 | 532.8 | 102.3 | 71.5 | 218.3 | 436.3 | 209 | 175.6 | 350.9 | 182.2 | 152 | 530.7 | 271.9 | 186.8 | 168.2 | 163.2 | 172.8 | 178.3 | 161.4 | 170.8 | 175
3212.1 | 2991.1 | -6.7 | 0 | 0 | 175.5 | 169 | 156.4 | 157.6 | 182.6 | 33.7 | 20.2 | 53.7 | 3.5 | 215.6 | 3 | 435.2 | 438.5 | 141.9 | 59.1 | 527.1 | 532.9 | 102.3 | 71.5 | 218.2 | 436.1 | 207.7 | 174.8 | 350.7 | 181.3 | 151.5 | 530.5 | 271.4 | 186.6 | 168 | 163.1 | 172.7 | 178.2 | 161.2 | 170.7 | 174.9
3213.1 | 2992.1 | -6.7 | 0 | 0 | 175.4 | 168.8 | 156.2 | 157.5 | 182.4 | 33.8 | 20.2 | 53.7 | 3.7 | 203.8 | 3.2 | 435.1 | 438.5 | 142.7 | 59.2 | 527.1 | 532.9 | 102.1 | 71.3 | 218.1 | 435.9 | 207.9 | 174.4 | 350.4 | 180.9 | 151.4 | 530.3 | 271.2 | 186.6 | 167.9 | 162.9 | 172.6 | 178.1 | 161.1 | 170.5 | 174.8
3214.1 | 2993.1 | -6.7 | 0 | 0 | 175.1 | 168.6 | 156.2 | 157.3 | 182.4 | 33.7 | 20.2 | 53.7 | 4 | 202.8 | 3.5 | 435.1 | 438.6 | 142.3 | 59.2 | 527.2 | 532.9 | 101.8 | 71.2 | 217.9 | 435.7 | 207.6 | 173.9 | 350.1 | 180.4 | 151 | 530.3 | 270.8 | 186.5 | 167.8 | 162.9 | 172.5 | 178 | 161 | 170.4 | 174.7
3215.1 | 2994.1 | -6.7 | 0 | 0 | 174.7 | 168.3 | 156.1 | 157 | 182.3 | 33.7 | 20.2 | 53.7 | 3.6 | 204.7 | 4 | 435.1 | 438.4 | 143.7 | 59.2 | 527.3 | 533 | 102.2 | 71.2 | 217.7 | 435.6 | 207.9 | 173.5 | 349.8 | 179.8 | 151.2 | 530.2 | 270.5 | 186.3 | 167.7 | 162.7 | 172.4 | 177.9 | 160.9 | 170.3 | 174.6
3216.1 | 2995.1 | -6.7 | 0 | 0 | 174.6 | 168.2 | 155.9 | 156.8 | 182.2 | 33.7 | 20.2 | 53.6 | 3.9 | 204.7 | 4.2 | 435.1 | 438.4 | 146.1 | 59.2 | 527.5 | 532.9 | 101.5 | 71.3 | 217.6 | 435.4 | 208.2 | 173 | 349.6 | 179.7 | 150.9 | 530 | 270.2 | 186.2 | 167.6 | 162.6 | 172.3 | 177.8 | 160.9 | 170.2 | 174.5
3217.1 | 2996.1 | -6.7 | 0 | 0 | 174.6 | 168.2 | 155.7 | 156.8 | 181.9 | 33.7 | 20.2 | 53.6 | 3.9 | 203.8 | 4.1 | 435.1 | 438.4 | 147.4 | 59.2 | 527.6 | 532.7 | 101.1 | 71.3 | 217.6 | 435.2 | 208.2 | 172.5 | 349.4 | 179.6 | 151 | 529.9 | 269.7 | 186.1 | 167.5 | 162.5 | 172.2 | 177.7 | 160.8 | 170.1 | 174.4
3218.1 | 2997.1 | -6.6 | 0 | 0 | 174.7 | 168.2 | 155.5 | 156.7 | 181.4 | 33.7 | 20.2 | 53.6 | 3.7 | 202.6 | 4 | 435.1 | 438.3 | 148.5 | 59.2 | 527.8 | 532.6 | 100.9 | 71.6 | 217.5 | 435.1 | 208.7 | 172.2 | 349.2 | 179.7 | 150.8 | 529.8 | 269.4 | 186.1 | 167.4 | 162.4 | 172.1 | 177.6 | 160.7 | 170 | 174.3
3219.1 | 2998.1 | -6.7 | 0 | 0 | 174.7 | 168.2 | 155.4 | 156.5 | 181 | 33.6 | 20.2 | 53.6 | 3.5 | 202.7 | 3.8 | 435 | 438.3 | 148.5 | 59.4 | 527.8 | 532.4 | 100.6 | 71.7 | 217.4 | 434.9 | 209.1 | 172 | 348.9 | 179.8 | 150.6 | 529.7 | 269.1 | 185.9 | 167.3 | 162.3 | 172 | 177.5 | 160.5 | 169.9 | 174.2
3220.1 | 2999.1 | -6.7 | 0 | 0 | 174.7 | 168.2 | 155.3 | 156.4 | 181.3 | 33.6 | 20.2 | 53.6 | 3.8 | 203.1 | 3.5 | 435 | 438.3 | 147.3 | 59.7 | 527.9 | 532.3 | 100.3 | 72 | 217.5 | 434.7 | 209.9 | 171.8 | 348.6 | 179.5 | 150.9 | 529.7 | 268.8 | 185.9 | 167.2 | 162.3 | 171.9 | 177.4 | 160.5 | 169.8 | 174.1
3221.1 | 3000.1 | -6.7 | 0 | 0 | 174.5 | 168.1 | 155.1 | 156.2 | 181.6 | 33.6 | 20.2 | 53.6 | 3.4 | 202.9 | 3.6 | 435 | 438.2 | 145.3 | 59.9 | 527.9 | 532.1 | 100.5 | 72.4 | 217.5 | 434.5 | 210.4 | 171.5 | 348.3 | 179.6 | 151.1 | 529.6 | 268.8 | 185.7 | 167.1 | 162.2 | 171.8 | 177.3 | 160.4 | 169.7 | 174
3222.1 | 3001.1 | -6.7 | 0 | 0 | 174.4 | 167.9 | 155 | 156.1 | 181.5 | 33.5 | 20.2 | 53.5 | 3.6 | 199.2 | 4 | 435 | 438.3 | 143.7 | 59.9 | 527.9 | 531.8 | 100.1 | 72.5 | 217.4 | 434.4 | 210.8 | 171.6 | 348.1 | 179.3 | 151.4 | 529.6 | 268.8 | 185.6 | 167 | 162.1 | 171.7 | 177.1 | 160.3 | 169.6 | 173.9
3223.1 | 3002.1 | -6.7 | 0 | 0 | 173.9 | 167.8 | 154.9 | 156 | 181.3 | 33.5 | 20.2 | 53.5 | 3.5 | 197.4 | 4.5 | 434.9 | 438.2 | 143.5 | 59.8 | 527.8 | 531.7 | 99.9 | 72.4 | 217.4 | 434.2 | 210.8 | 171.8 | 347.8 | 179.6 | 151.6 | 529.4 | 268.8 | 185.5 | 166.8 | 162 | 171.6 | 177 | 160.1 | 169.5 | 173.8
3224.1 | 3003.1 | -6.7 | 0 | 0 | 173.6 | 167.6 | 154.9 | 156 | 181.1 | 33.5 | 20.2 | 53.5 | 3.7 | 205.1 | 4.7 | 434.9 | 438.2 | 144.7 | 59.7 | 527.8 | 531.8 | 99.4 | 72.4 | 217.4 | 434 | 210.9 | 172 | 347.6 | 180.7 | 150.8 | 529.2 | 268.6 | 185.4 | 166.7 | 161.9 | 171.5 | 176.9 | 159.9 | 169.4 | 173.7
3225.1 | 3004.1 | -6.7 | 0 | 0 | 173.7 | 167.5 | 154.7 | 155.8 | 180.9 | 33.5 | 20.2 | 53.5 | 3.3 | 217.5 | 4.4 | 434.9 | 438.1 | 144.3 | 59.6 | 527.8 | 531.8 | 98.8 | 72.4 | 217.3 | 433.9 | 210.2 | 172.2 | 347.3 | 181.3 | 150.3 | 528.9 | 268.3 | 185.3 | 166.5 | 161.8 | 171.4 | 176.8 | 159.8 | 169.3 | 173.6
3226.1 | 3005.1 | -6.5 | 0 | 0 | 173.8 | 167.4 | 154.6 | 155.6 | 180.6 | 33.5 | 20.2 | 53.4 | 3.6 | 231.2 | 3.9 | 434.9 | 438.1 | 143.3 | 59.5 | 527.8 | 531.8 | 98.2 | 72.3 | 217.3 | 433.7 | 209.4 | 172.5 | 347.1 | 181.1 | 150.9 | 528.7 | 268.3 | 185.2 | 166.4 | 161.7 | 171.3 | 176.7 | 159.6 | 169.2 | 173.5
3227.1 | 3006.1 | -6.1 | 0 | 0 | 173.8 | 167.1 | 154.5 | 155.5 | 180.1 | 33.5 | 20.2 | 53.4 | 3.4 | 224 | 3.9 | 434.9 | 438 | 142.3 | 59.4 | 527.8 | 531.8 | 98.7 | 72.3 | 217.3 | 433.6 | 208.7 | 172.7 | 346.9 | 180.8 | 151.7 | 528.6 | 268.3 | 185.1 | 166.3 | 161.6 | 171.2 | 176.6 | 159.4 | 169.1 | 173.4
3228.1 | 3007.1 | -6.4 | 0 | 0 | 173.8 | 166.8 | 154.3 | 155.3 | 179.9 | 33.5 | 20.2 | 53.3 | 3.8 | 218.4 | 3.8 | 434.8 | 438 | 140.9 | 59.4 | 527.7 | 531.8 | 99.5 | 72.2 | 217.2 | 433.4 | 207.4 | 173 | 346.6 | 180.5 | 151.8 | 528.5 | 268.2 | 185 | 166.2 | 161.5 | 171.1 | 176.5 | 159.3 | 169 | 173.3
3229.1 | 3008.1 | -6.3 | 0 | 0 | 173.8 | 166.5 | 154.3 | 155.1 | 179.8 | 33.5 | 20.2 | 53.3 | 3.6 | 239.2 | 3.6 | 434.8 | 438.1 | 140.2 | 59.4 | 527.7 | 531.6 | 99.2 | 72.2 | 217.2 | 433.3 | 206.4 | 173 | 346.4 | 180.1 | 152.3 | 528.4 | 268.2 | 184.9 | 166.1 | 161.4 | 171 | 176.4 | 159.2 | 168.9 | 173.2
3230.1 | 3009.1 | -5.9 | 0 | 0 | 173.6 | 166.3 | 154.2 | 155 | 179.6 | 33.5 | 20.2 | 53.3 | 3.7 | 233.2 | 3.4 | 434.8 | 438 | 139 | 59.3 | 527.7 | 531.5 | 98.4 | 72.2 | 217.2 | 433.1 | 206.3 | 173.3 | 346.2 | 180 | 152.7 | 528.2 | 268 | 184.8 | 165.9 | 161.3 | 170.9 | 176.3 | 159.1 | 168.8 | 173.1
3231.1 | 3010.1 | -5.8 | 0 | 0 | 173.4 | 166.2 | 154.1 | 155 | 179.5 | 33.4 | 20.2 | 53.2 | 3.7 | 213.1 | 3.2 | 434.8 | 438.1 | 138.5 | 59.5 | 527.7 | 531.6 | 98.1 | 72.1 | 217.2 | 432.9 | 206 | 173.4 | 345.9 | 179.8 | 152.3 | 528.1 | 267.9 | 184.7 | 165.7 | 161.2 | 170.8 | 176.2 | 159 | 168.7 | 173
3232.1 | 3011.1 | -5.7 | 0 | 0 | 173.3 | 166.1 | 153.9 | 154.9 | 179.1 | 33.4 | 20.2 | 53.2 | 3.6 | 206.1 | 3 | 434.8 | 438 | 138.2 | 59.5 | 527.6 | 531.6 | 98.4 | 72.1 | 217.3 | 432.8 | 205.8 | 173.1 | 345.7 | 180 | 152 | 527.9 | 267.8 | 184.6 | 165.6 | 161 | 170.7 | 176.1 | 158.9 | 168.5 | 172.9
3233.1 | 3012.1 | -5.5 | 0 | 0 | 173.2 | 166 | 153.8 | 154.9 | 178.9 | 33.4 | 20.2 | 53.1 | 3.7 | 221.5 | 3.1 | 434.7 | 437.9 | 138.5 | 59.4 | 527.5 | 531.6 | 99 | 72.2 | 217.3 | 432.6 | 205.4 | 173.1 | 345.5 | 180 | 151.8 | 527.8 | 267.8 | 184.4 | 165.5 | 160.9 | 170.6 | 176 | 158.8 | 168.4 | 172.8
3234.1 | 3013.1 | -5.4 | 0 | 0 | 173.1 | 166 | 153.6 | 154.5 | 178.9 | 33.4 | 20.2 | 53.1 | 3.6 | 242.8 | 3.2 | 434.7 | 437.8 | 137.6 | 59.3 | 527.4 | 531.7 | 100 | 72 | 217.3 | 432.5 | 206.4 | 173.2 | 345.2 | 179.8 | 152 | 527.6 | 267.7 | 184.4 | 165.4 | 160.8 | 170.5 | 175.8 | 158.7 | 168.3 | 172.7
3235.1 | 3014.1 | -5.3 | 0 | 0 | 173.1 | 165.9 | 153.5 | 154.3 | 178.8 | 33.4 | 20.2 | 53 | 3.8 | 240.1 | 3.3 | 434.7 | 438 | 137.7 | 59.2 | 527.4 | 531.7 | 100.3 | 71.9 | 217.3 | 432.3 | 207.2 | 173.3 | 345 | 179.8 | 152.2 | 527.3 | 267.7 | 184.3 | 165.3 | 160.7 | 170.4 | 175.7 | 158.6 | 168.2 | 172.6
3236.1 | 3015.1 | -5.7 | 0 | 0 | 173.2 | 165.8 | 153.5 | 154.2 | 178.5 | 33.4 | 20.2 | 53 | 3.5 | 233.4 | 3.3 | 434.7 | 437.9 | 138.1 | 59 | 527.3 | 531.7 | 99.9 | 71.7 | 217.3 | 432.2 | 207.1 | 173.4 | 344.8 | 179.6 | 152.4 | 527 | 267.5 | 184.1 | 165.2 | 160.6 | 170.3 | 175.6 | 158.5 | 168.1 | 172.5
3237.1 | 3016.1 | -5.7 | 0 | 0 | 173.2 | 165.8 | 153.4 | 154.1 | 178.2 | 33.4 | 20.2 | 52.9 | 3.1 | 243.3 | 3.3 | 434.7 | 437.8 | 139.3 | 59 | 527.2 | 531.7 | 99.8 | 71.5 | 217.4 | 432 | 206.8 | 173.3 | 344.6 | 178.9 | 151.9 | 526.8 | 267.5 | 184.1 | 165 | 160.4 | 170.2 | 175.5 | 158.4 | 168 | 172.4
3238.1 | 3017.1 | -6.3 | 0 | 0 | 173 | 165.7 | 153.4 | 154.1 | 177.9 | 33.4 | 20.2 | 52.9 | 3.5 | 240.4 | 3.2 | 434.6 | 437.8 | 138.5 | 58.9 | 527.2 | 531.8 | 99.7 | 71.3 | 217.5 | 431.9 | 206.5 | 173.1 | 344.4 | 178.5 | 151.7 | 526.5 | 267.3 | 184 | 165 | 160.3 | 170.1 | 175.4 | 158.3 | 167.9 | 172.3
3239.1 | 3018.1 | -6.7 | 0 | 0 | 172.8 | 165.7 | 153.3 | 154.1 | 177.8 | 33.4 | 20.3 | 52.9 | 3.4 | 222.2 | 3.1 | 434.6 | 437.8 | 137.3 | 58.8 | 527.1 | 531.9 | 99.7 | 71.3 | 217.5 | 431.7 | 207 | 173 | 344.2 | 177.8 | 151.9 | 526.3 | 267.1 | 183.9 | 164.9 | 160.2 | 170 | 175.3 | 158.2 | 167.8 | 172.2
3240.1 | 3019.1 | -6.7 | 0 | 0 | 172.8 | 165.5 | 153.2 | 154 | 177.7 | 33.4 | 20.3 | 52.9 | 3.5 | 206.1 | 3.2 | 434.6 | 437.7 | 136.3 | 58.7 | 527.1 | 531.9 | 100.4 | 71.3 | 217.7 | 431.5 | 206.3 | 172.9 | 344 | 177 | 152 | 526.1 | 267.1 | 183.7 | 164.8 | 160.1 | 169.9 | 175.2 | 158 | 167.7 | 172.1
3241.1 | 3020.1 | -6.6 | 0 | 0 | 172.7 | 165.2 | 153 | 153.9 | 177.7 | 33.3 | 20.3 | 52.8 | 3.7 | 216.3 | 3.1 | 434.6 | 437.6 | 136.3 | 58.6 | 527 | 531.9 | 99.9 | 71.1 | 217.8 | 431.4 | 205.8 | 172.7 | 343.8 | 176.6 | 152.2 | 525.9 | 267.1 | 183.6 | 164.6 | 160 | 169.8 | 175.1 | 157.8 | 167.6 | 172
3242.1 | 3021.1 | -6.1 | 0 | 0 | 172.5 | 164.9 | 152.9 | 153.8 | 177.7 | 33.3 | 20.3 | 52.8 | 3.2 | 229 | 3.1 | 434.6 | 437.6 | 137 | 58.5 | 527 | 531.6 | 99 | 70.9 | 217.8 | 431.2 | 206.2 | 172.7 | 343.6 | 176.1 | 152.6 | 525.7 | 266.9 | 183.5 | 164.5 | 159.8 | 169.7 | 174.9 | 157.7 | 167.4 | 171.9
3243.1 | 3022.1 | -5.9 | 0 | 0 | 172.2 | 164.8 | 152.8 | 153.7 | 177.5 | 33.3 | 20.3 | 52.8 | 3.5 | 233.5 | 2.9 | 434.5 | 437.6 | 136.5 | 58.3 | 526.9 | 531.6 | 99 | 70.8 | 217.7 | 431.1 | 206.9 | 173 | 343.3 | 176.1 | 153 | 525.6 | 266.5 | 183.4 | 164.4 | 159.7 | 169.6 | 174.8 | 157.6 | 167.3 | 171.8
3244.1 | 3023.1 | -6.2 | 0 | 0 | 172 | 164.7 | 152.6 | 153.5 | 177.7 | 33.3 | 20.3 | 52.8 | 3.4 | 235.6 | 2.8 | 434.5 | 437.5 | 135.4 | 58.2 | 526.9 | 531.7 | 98.8 | 70.6 | 217.8 | 430.9 | 207.5 | 173.2 | 343.1 | 176.1 | 152.7 | 525.5 | 266.3 | 183.3 | 164.3 | 159.6 | 169.5 | 174.7 | 157.5 | 167.2 | 171.7
3245.1 | 3024.1 | -6.3 | 0 | 0 | 172 | 164.6 | 152.3 | 153.4 | 177.9 | 33.2 | 20.3 | 52.7 | 3.3 | 236.7 | 2.4 | 434.5 | 437.6 | 134.8 | 58.1 | 526.8 | 531.6 | 99.1 | 70.6 | 217.9 | 430.8 | 207.5 | 173.4 | 342.9 | 175.4 | 152.3 | 525.4 | 266.1 | 183.2 | 164.2 | 159.5 | 169.4 | 174.6 | 157.3 | 167.1 | 171.6
3246.1 | 3025.1 | -6.1 | 0 | 0 | 171.8 | 164.5 | 152 | 153.2 | 177.6 | 33.2 | 20.3 | 52.7 | 3.3 | 236.4 | 2.2 | 434.5 | 437.5 | 134.2 | 58.1 | 526.8 | 531.4 | 99.1 | 70.8 | 217.7 | 430.6 | 207.8 | 173.8 | 342.7 | 174.9 | 152 | 525.4 | 265.8 | 183.1 | 164.1 | 159.3 | 169.3 | 174.5 | 157.1 | 167 | 171.5
3247.1 | 3026.1 | -5.8 | 0 | 0 | 171.6 | 164.5 | 151.8 | 152.9 | 177 | 33.2 | 20.3 | 52.7 | 3.4 | 236.4 | 2.2 | 434.5 | 437.4 | 134.6 | 58.1 | 526.7 | 531.4 | 99.9 | 71.1 | 217.7 | 430.4 | 208.1 | 173.6 | 342.4 | 174.4 | 151.2 | 525.4 | 265.6 | 183 | 164.1 | 159.2 | 169.3 | 174.4 | 157 | 166.9 | 171.4
3248.1 | 3027.1 | -6.1 | 0 | 0 | 171.3 | 164.4 | 151.7 | 152.8 | 176.5 | 33.2 | 20.3 | 52.7 | 3.8 | 235.7 | 2.2 | 434.4 | 437.5 | 135.1 | 58 | 526.7 | 531.4 | 99.7 | 71.3 | 217.8 | 430.2 | 207.4 | 173.6 | 342.2 | 174.1 | 150.5 | 525.3 | 265.6 | 182.9 | 164 | 159.1 | 169.2 | 174.3 | 156.8 | 166.7 | 171.3
3249.1 | 3028.1 | -6.6 | 0 | 0 | 171.1 | 164.3 | 151.6 | 152.8 | 176.2 | 33.2 | 20.3 | 52.6 | 3.7 | 232.7 | 2.3 | 434.4 | 437.5 | 135.8 | 58 | 526.7 | 531.3 | 99.7 | 71.4 | 217.8 | 430.1 | 207.3 | 173.3 | 342 | 173.9 | 149.7 | 525.3 | 265.1 | 182.8 | 164 | 159 | 169.1 | 174.2 | 156.6 | 166.6 | 171.2
3250.1 | 3029.1 | -6.7 | 0 | 0 | 171 | 164.3 | 151.6 | 152.6 | 176 | 33.2 | 20.3 | 52.6 | 3.6 | 236.1 | 2.3 | 434.4 | 437.6 | 136.1 | 57.9 | 526.7 | 531.2 | 99.7 | 71.3 | 217.7 | 429.9 | 207.2 | 172.7 | 341.7 | 173.5 | 148.9 | 525.4 | 264.4 | 182.7 | 163.8 | 158.9 | 169 | 174.1 | 156.5 | 166.5 | 171.1
3251.1 | 3030.1 | -6.7 | 0 | 0 | 170.9 | 164.3 | 151.5 | 152.5 | 176.1 | 33.2 | 20.3 | 52.6 | 3.9 | 239.4 | 2.4 | 434.4 | 437.4 | 136.5 | 57.9 | 526.7 | 531 | 99.3 | 71.2 | 217.6 | 429.7 | 207.5 | 172.4 | 341.5 | 173 | 148.5 | 525.4 | 263.8 | 182.6 | 163.7 | 158.8 | 168.9 | 173.9 | 156.3 | 166.4 | 171
3252.1 | 3031.1 | -6.7 | 0 | 0 | 170.6 | 164.3 | 151.3 | 152.5 | 176.1 | 33.1 | 20.3 | 52.5 | 3.6 | 238.1 | 2.5 | 434.4 | 437.4 | 136.4 | 58 | 526.6 | 530.8 | 98.7 | 71 | 217.7 | 429.5 | 206.9 | 172.6 | 341.2 | 172.9 | 147.9 | 525.3 | 263.7 | 182.5 | 163.6 | 158.7 | 168.7 | 173.8 | 156.2 | 166.2 | 170.9
3253.1 | 3032.1 | -6.7 | 0 | 0 | 170.4 | 164.3 | 151.2 | 152.4 | 176.2 | 32.9 | 20.3 | 52.5 | 3.5 | 238.3 | 2.5 | 434.4 | 437.4 | 137 | 58 | 526.7 | 530.6 | 98.3 | 70.9 | 217.6 | 429.3 | 206.3 | 172.3 | 341 | 172.6 | 147.4 | 525.1 | 263.6 | 182.4 | 163.4 | 158.5 | 168.7 | 173.7 | 156 | 166.1 | 170.8
3254.1 | 3033.1 | -6.7 | 0 | 0 | 170.3 | 164.3 | 151 | 152.3 | 176.3 | 32.8 | 20.3 | 52.5 | 3.7 | 237.7 | 2.4 | 434.3 | 437.3 | 136.2 | 57.9 | 526.7 | 530.5 | 99.3 | 71 | 217.6 | 429.2 | 207.1 | 171.9 | 340.8 | 172.2 | 147.5 | 524.9 | 263.6 | 182.3 | 163.3 | 158.4 | 168.6 | 173.6 | 155.9 | 166 | 170.7
3255.1 | 3034.1 | -6.7 | 0 | 0 | 170.3 | 164.2 | 150.9 | 152.2 | 176.4 | 32.7 | 20.3 | 52.5 | 3.7 | 237.8 | 2.3 | 434.3 | 437.2 | 136 | 57.7 | 526.7 | 530.4 | 100.4 | 71.2 | 217.6 | 429 | 207.3 | 171.9 | 340.6 | 171.8 | 147.5 | 524.7 | 263.6 | 182.2 | 163.2 | 158.2 | 168.4 | 173.5 | 155.8 | 165.9 | 170.6
3256.1 | 3035.1 | -6.7 | 0 | 0 | 170.2 | 164.1 | 150.8 | 152.1 | 176.3 | 32.6 | 20.3 | 52.4 | 3.4 | 237.5 | 2.3 | 434.3 | 437.2 | 134.5 | 57.7 | 526.7 | 530.4 | 101 | 71.3 | 217.5 | 428.8 | 206.7 | 171.7 | 340.3 | 171.4 | 147.3 | 524.6 | 263.4 | 182.1 | 163.2 | 158.2 | 168.3 | 173.4 | 155.7 | 165.8 | 170.5
3257.1 | 3036.1 | -6.6 | 0 | 0 | 170.1 | 163.9 | 150.6 | 152 | 176.3 | 32.6 | 20.3 | 52.4 | 3.7 | 237.1 | 2.5 | 434.3 | 437.1 | 134.2 | 57.6 | 526.7 | 530.3 | 100.6 | 71.3 | 217.5 | 428.6 | 206.1 | 171.5 | 340 | 171.2 | 147 | 524.6 | 263 | 182 | 163.1 | 158 | 168.2 | 173.2 | 155.5 | 165.7 | 170.4
3258.1 | 3037.1 | -6.3 | 0 | 0 | 170 | 163.8 | 150.6 | 151.8 | 176.1 | 32.6 | 20.3 | 52.4 | 3.6 | 236.2 | 2.7 | 434.3 | 437.2 | 135 | 57.5 | 526.7 | 530.1 | 100 | 71.3 | 217.4 | 428.5 | 206.3 | 171.1 | 339.8 | 170.8 | 146.5 | 524.6 | 262.7 | 181.9 | 162.9 | 157.9 | 168.1 | 173.1 | 155.4 | 165.5 | 170.3
3259.1 | 3038.1 | -6.5 | 0 | 0 | 170 | 163.7 | 150.5 | 151.6 | 175.8 | 32.6 | 20.3 | 52.4 | 3.6 | 233 | 2.9 | 434.2 | 437.1 | 134.4 | 57.4 | 526.7 | 529.9 | 99.2 | 71.3 | 217.4 | 428.3 | 206.5 | 171 | 339.6 | 170.9 | 146.8 | 524.5 | 262.4 | 181.8 | 162.8 | 157.8 | 168 | 173 | 155.3 | 165.4 | 170.2
3260.1 | 3039.1 | -6.7 | 0 | 0 | 170 | 163.6 | 150.4 | 151.6 | 175.5 | 32.6 | 20.3 | 52.4 | 3.3 | 225.3 | 3 | 434.2 | 437.1 | 134.3 | 57.4 | 526.6 | 529.7 | 98.7 | 71.2 | 217.3 | 428.1 | 206.9 | 170.7 | 339.3 | 170.8 | 146.7 | 524.3 | 262.3 | 181.6 | 162.7 | 157.7 | 168 | 172.9 | 155.2 | 165.3 | 170.1
3261.1 | 3040.1 | -6.6 | 0 | 0 | 169.9 | 163.6 | 150.3 | 151.5 | 175.3 | 32.6 | 20.3 | 52.3 | 3.4 | 220.8 | 2.8 | 434.2 | 437.1 | 133.5 | 57.3 | 526.6 | 529.5 | 97.9 | 71.2 | 217.2 | 428 | 206 | 170.4 | 339.1 | 170.6 | 146.9 | 524.2 | 262.3 | 181.6 | 162.5 | 157.6 | 167.9 | 172.8 | 155.2 | 165.1 | 170
3262.1 | 3041.1 | -6.5 | 0 | 0 | 169.9 | 163.5 | 150.3 | 151.4 | 175.2 | 32.5 | 20.3 | 52.3 | 3.3 | 229.5 | 2.6 | 434.2 | 437 | 132.9 | 57.2 | 526.6 | 529.4 | 97.3 | 71 | 217.1 | 427.8 | 205.4 | 170.5 | 338.9 | 170.5 | 147.6 | 523.9 | 262.2 | 181.5 | 162.4 | 157.5 | 167.8 | 172.7 | 155 | 165 | 169.9
3263.1 | 3042.1 | -6.6 | 0 | 0 | 169.7 | 163.4 | 150.2 | 151.3 | 175.3 | 32.5 | 20.3 | 52.3 | 3.3 | 241.8 | 2.5 | 434.2 | 436.9 | 132.2 | 57.2 | 526.6 | 529.2 | 96.6 | 71 | 217.1 | 427.6 | 205.1 | 170.3 | 338.7 | 169.8 | 147.8 | 523.7 | 262.1 | 181.3 | 162.2 | 157.3 | 167.6 | 172.5 | 154.9 | 164.9 | 169.8
3264.1 | 3043.1 | -6.6 | 0 | 0 | 169.6 | 163.2 | 150.1 | 151.2 | 175.7 | 32.4 | 20.3 | 52.3 | 4 | 244.7 | 2.4 | 434.1 | 437 | 132.5 | 57.1 | 526.6 | 528.9 | 96.2 | 71.1 | 217 | 427.4 | 203.9 | 169.6 | 338.5 | 169.5 | 147.8 | 523.5 | 261.7 | 181.3 | 162.1 | 157.2 | 167.6 | 172.4 | 154.8 | 164.8 | 169.7
3265.1 | 3044.1 | -6.6 | 0 | 0 | 169.5 | 162.9 | 149.9 | 151.1 | 175.4 | 32.4 | 20.3 | 52.2 | 3.9 | 248.1 | 2.6 | 434.1 | 437 | 132.6 | 57 | 526.6 | 528.6 | 95.7 | 71.2 | 216.9 | 427.3 | 203.3 | 169 | 338.3 | 168.8 | 147.5 | 523.2 | 261.4 | 181.1 | 162 | 157.1 | 167.5 | 172.3 | 154.7 | 164.7 | 169.6
3266.1 | 3045.1 | -6.6 | 0 | 0 | 169.4 | 162.7 | 149.8 | 151 | 175.1 | 32.3 | 20.3 | 52.2 | 3.5 | 250 | 3.3 | 434.1 | 436.9 | 131.9 | 57 | 526.5 | 528.5 | 95.3 | 71 | 216.8 | 427.1 | 202.7 | 168.5 | 338 | 168.5 | 147.8 | 522.9 | 260.8 | 181 | 161.9 | 157 | 167.4 | 172.2 | 154.6 | 164.5 | 169.5
3267.1 | 3046.1 | -6.7 | 0 | 0 | 169.3 | 162.5 | 149.7 | 151 | 175.2 | 32.3 | 20.3 | 52.2 | 3.4 | 247.6 | 3.7 | 434.1 | 436.9 | 131.4 | 56.9 | 526.5 | 528.5 | 94.7 | 70.9 | 216.8 | 426.9 | 202.2 | 168.6 | 337.9 | 168.4 | 147.7 | 522.7 | 260.9 | 180.9 | 161.8 | 156.9 | 167.3 | 172.1 | 154.5 | 164.4 | 169.4
3268.1 | 3047.1 | -6.7 | 0 | 0 | 169.2 | 162.3 | 149.6 | 150.8 | 175.2 | 32.2 | 20.3 | 52.1 | 3.7 | 239.1 | 3.7 | 434.1 | 436.8 | 131.2 | 56.7 | 526.5 | 528.4 | 94 | 70.8 | 216.7 | 426.7 | 202.1 | 168.3 | 337.6 | 168.4 | 147.4 | 522.4 | 260.7 | 180.8 | 161.6 | 156.8 | 167.2 | 172 | 154.4 | 164.2 | 169.3
3269.1 | 3048.1 | -6.6 | 0 | 0 | 169.1 | 162.2 | 149.4 | 150.6 | 175.4 | 32.3 | 20.3 | 52.1 | 3.5 | 242.4 | 3.9 | 434.1 | 436.8 | 131.7 | 56.6 | 526.5 | 528.2 | 93.2 | 70.7 | 216.6 | 426.6 | 202.1 | 167.8 | 337.4 | 168.7 | 147.4 | 522.2 | 260.3 | 180.7 | 161.4 | 156.7 | 167.1 | 171.9 | 154.3 | 164.1 | 169.2
3270.1 | 3049.1 | -6.7 | 0 | 0 | 169 | 162.3 | 149.3 | 150.4 | 175.2 | 32.2 | 20.3 | 52 | 3.3 | 242 | 4.5 | 434 | 436.8 | 133 | 56.5 | 526.5 | 528 | 92.4 | 70.5 | 216.6 | 426.4 | 201.8 | 167.4 | 337.2 | 169.4 | 146.8 | 522.1 | 260.1 | 180.6 | 161.3 | 156.6 | 167 | 171.8 | 154.2 | 163.9 | 169.1
3271.1 | 3050.1 | -6.7 | 0 | 0 | 168.7 | 162.3 | 149.2 | 150.3 | 175.1 | 32.2 | 20.3 | 52 | 3.5 | 246.2 | 5.5 | 434 | 436.9 | 133.4 | 56.4 | 526.5 | 527.8 | 91.8 | 70.2 | 216.5 | 426.2 | 201.3 | 166.9 | 336.9 | 170.2 | 146.8 | 521.9 | 259.8 | 180.5 | 161.2 | 156.5 | 166.9 | 171.7 | 154.1 | 163.8 | 169
3272.1 | 3051.1 | -6.7 | 0 | 0 | 168.4 | 162.3 | 149.1 | 150.3 | 175 | 32.2 | 20.3 | 51.9 | 3.6 | 252.9 | 6.6 | 434 | 436.7 | 135 | 56.4 | 526.6 | 527.7 | 91.2 | 69.9 | 216.3 | 426 | 200.9 | 166.5 | 336.8 | 170 | 146.4 | 521.6 | 259.6 | 180.4 | 161.1 | 156.4 | 166.8 | 171.6 | 154 | 163.7 | 168.9
3273.1 | 3052.1 | -6.6 | 0 | 0 | 168.4 | 162.3 | 149 | 150.1 | 174.5 | 32.2 | 20.3 | 51.9 | 3.4 | 250.3 | 7 | 434 | 436.8 | 135.7 | 56.4 | 526.7 | 527.4 | 90.6 | 69.8 | 216.5 | 425.8 | 201.3 | 166.4 | 336.5 | 169.8 | 146 | 521.4 | 259.1 | 180.3 | 161 | 156.3 | 166.7 | 171.5 | 154 | 163.6 | 168.8
3274.1 | 3053.1 | -6.7 | 0 | 0 | 168.3 | 162.3 | 148.9 | 149.9 | 174.3 | 32.2 | 20.3 | 51.9 | 3.8 | 247.7 | 6.7 | 434 | 436.7 | 136.3 | 56.2 | 526.8 | 527.1 | 89.9 | 69.5 | 216.5 | 425.6 | 202.4 | 166.3 | 336.3 | 169.5 | 145.9 | 521.1 | 259.1 | 180.2 | 160.9 | 156.2 | 166.6 | 171.4 | 153.8 | 163.6 | 168.7
3275.1 | 3054.1 | -6.7 | 0 | 0 | 168.2 | 162.2 | 148.8 | 149.9 | 174.1 | 32.2 | 20.3 | 51.9 | 3.6 | 242.3 | 6.2 | 433.9 | 436.7 | 137 | 56.2 | 526.8 | 526.8 | 90.7 | 69.1 | 216.3 | 425.4 | 202.8 | 166.6 | 336.1 | 169 | 145.6 | 520.9 | 259 | 180.1 | 160.8 | 156.1 | 166.5 | 171.2 | 153.7 | 163.5 | 168.6
3276.1 | 3055.1 | -6.7 | 0 | 0 | 168 | 162 | 148.7 | 149.8 | 173.9 | 32.2 | 20.3 | 51.8 | 3.5 | 247.7 | 5.6 | 433.9 | 436.7 | 136.6 | 56.1 | 526.8 | 526.6 | 91.8 | 68.7 | 216.3 | 425.2 | 202.2 | 166.7 | 335.9 | 168.6 | 145.2 | 520.7 | 258.6 | 179.9 | 160.7 | 156 | 166.4 | 171.1 | 153.6 | 163.3 | 168.5
3277.1 | 3056.1 | -6.7 | 0 | 0 | 167.8 | 161.7 | 148.6 | 149.7 | 174 | 32.2 | 20.3 | 51.8 | 3.2 | 253.4 | 5.3 | 433.9 | 436.7 | 137 | 56 | 526.7 | 526.6 | 92.1 | 68.3 | 216.2 | 425.1 | 201.6 | 167 | 335.7 | 168.5 | 145.4 | 520.4 | 258.5 | 179.9 | 160.6 | 155.9 | 166.3 | 171 | 153.5 | 163.2 | 168.4
3278.1 | 3057.1 | -6.7 | 0 | 0 | 167.6 | 161.5 | 148.5 | 149.7 | 174.2 | 32.2 | 20.3 | 51.8 | 3.5 | 253 | 5.1 | 433.9 | 436.6 | 138.1 | 56 | 526.6 | 526.5 | 92.1 | 68.1 | 216.1 | 424.9 | 202 | 167.3 | 335.5 | 168.3 | 144.9 | 520.2 | 258.4 | 179.8 | 160.4 | 155.8 | 166.2 | 170.9 | 153.4 | 163.1 | 168.3
3279.1 | 3058.1 | -6.7 | 0 | 0 | 167.5 | 161.4 | 148.4 | 149.6 | 174.2 | 32.2 | 20.3 | 51.8 | 3.9 | 253.3 | 5.9 | 433.9 | 436.5 | 138.4 | 55.9 | 526.5 | 526.5 | 92.1 | 67.8 | 215.9 | 424.7 | 202.4 | 167.4 | 335.3 | 168.2 | 144.8 | 519.9 | 258 | 179.7 | 160.3 | 155.7 | 166.1 | 170.8 | 153.3 | 163 | 168.2
3280.1 | 3059.1 | -6.6 | 0 | 0 | 167.3 | 161.2 | 148.4 | 149.4 | 173.9 | 32.3 | 20.3 | 51.8 | 4.1 | 256.3 | 6.8 | 433.8 | 436.4 | 138 | 55.9 | 526.3 | 526.5 | 92.3 | 67.7 | 215.8 | 424.6 | 202.2 | 167.3 | 335.1 | 167.8 | 145.3 | 519.6 | 257.9 | 179.6 | 160.2 | 155.6 | 166 | 170.7 | 153.2 | 162.9 | 168.1
3281.1 | 3060.1 | -6.7 | 0 | 0 | 166.9 | 160.9 | 148.3 | 149.1 | 173.4 | 32.3 | 20.3 | 51.8 | 4.2 | 263.4 | 7.5 | 433.8 | 436.3 | 137.7 | 55.8 | 526.2 | 526.6 | 93.4 | 67.5 | 215.7 | 424.4 | 201.1 | 167.5 | 334.8 | 168.1 | 144.7 | 519.4 | 258.1 | 179.5 | 160 | 155.5 | 165.9 | 170.6 | 153 | 162.8 | 168
3282.1 | 3061.1 | -6.7 | 0 | 0 | 166.7 | 160.6 | 148.2 | 148.9 | 173 | 32.3 | 20.3 | 51.8 | 4.1 | 259.9 | 8 | 433.8 | 436.3 | 137.8 | 55.8 | 526.1 | 526.7 | 93.2 | 67.5 | 215.8 | 424.3 | 200.5 | 167.2 | 334.6 | 167.6 | 144.3 | 519.2 | 258 | 179.4 | 159.9 | 155.3 | 165.8 | 170.5 | 152.9 | 162.7 | 167.9
3283.1 | 3062.1 | -6.7 | 0 | 0 | 166.4 | 160.4 | 148.2 | 148.9 | 172.4 | 32.3 | 20.3 | 51.8 | 4 | 251.7 | 8 | 433.8 | 436.3 | 137.7 | 55.7 | 526.1 | 526.8 | 93.8 | 67.6 | 215.8 | 424.1 | 200.8 | 167.2 | 334.4 | 167.8 | 143.8 | 518.9 | 258 | 179.2 | 159.8 | 155.2 | 165.7 | 170.4 | 152.8 | 162.6 | 167.8
3284.1 | 3063.1 | -6.7 | 0 | 0 | 166.1 | 160.3 | 148.2 | 148.9 | 172 | 32.2 | 20.3 | 51.8 | 3.4 | 248.4 | 7.8 | 433.7 | 436.4 | 138 | 55.8 | 526.1 | 526.9 | 94.1 | 67.7 | 215.7 | 423.9 | 200.5 | 166.8 | 334.1 | 167.7 | 143.4 | 518.8 | 257.8 | 179.1 | 159.7 | 155.1 | 165.6 | 170.3 | 152.7 | 162.5 | 167.7
3285.1 | 3064.1 | -6.7 | 0 | 0 | 166 | 160.2 | 148 | 148.8 | 171.6 | 32.1 | 20.3 | 51.7 | 3.4 | 245.4 | 7.2 | 433.7 | 436.2 | 137.3 | 56 | 526.1 | 526.8 | 93.3 | 67.8 | 215.7 | 423.7 | 200.8 | 166.2 | 333.9 | 167 | 143.2 | 518.6 | 257.4 | 179 | 159.6 | 154.9 | 165.5 | 170.1 | 152.5 | 162.4 | 167.6
3286.1 | 3065.1 | -6.6 | 0 | 0 | 165.8 | 160.1 | 147.8 | 148.8 | 171.1 | 32 | 20.3 | 51.7 | 3.9 | 250.1 | 6.5 | 433.7 | 436.2 | 137.5 | 56.1 | 526.1 | 526.8 | 92.8 | 68 | 215.7 | 423.6 | 200.5 | 165.8 | 333.7 | 167.3 | 143 | 518.4 | 257.2 | 178.9 | 159.5 | 154.8 | 165.4 | 170 | 152.4 | 162.3 | 167.5
3287.1 | 3066.1 | -6.6 | 0 | 0 | 165.7 | 159.9 | 147.7 | 148.7 | 170.7 | 32 | 20.3 | 51.7 | 3.7 | 259.3 | 6.2 | 433.7 | 436.2 | 137.6 | 56.3 | 526.1 | 526.8 | 92.5 | 68.2 | 215.6 | 423.4 | 201 | 165.4 | 333.5 | 167.1 | 142.5 | 518.2 | 256.8 | 178.8 | 159.4 | 154.6 | 165.3 | 169.9 | 152.3 | 162.3 | 167.4
3288.1 | 3067.1 | -6.7 | 0 | 0 | 165.7 | 159.9 | 147.5 | 148.6 | 170.5 | 31.9 | 20.3 | 51.7 | 3.2 | 244.5 | 6.2 | 433.6 | 436.1 | 137 | 56.4 | 526.1 | 526.6 | 93.6 | 68.4 | 215.6 | 423.2 | 201.7 | 164.9 | 333.3 | 167.1 | 142 | 517.9 | 256.2 | 178.7 | 159.3 | 154.5 | 165.2 | 169.8 | 152.2 | 162.1 | 167.3
3289.1 | 3068.1 | -6.6 | 0 | 0 | 165.6 | 159.8 | 147.2 | 148.6 | 170.4 | 31.9 | 20.3 | 51.7 | 3.1 | 252.8 | 6.7 | 433.6 | 436.1 | 137 | 56.4 | 526.1 | 526.5 | 93.7 | 68.8 | 215.6 | 423 | 202 | 164.6 | 333.1 | 166.6 | 142.2 | 517.8 | 256 | 178.6 | 159.2 | 154.4 | 165.1 | 169.6 | 152.1 | 162 | 167.2
3290.1 | 3069.1 | -6.7 | 0 | 0 | 165.5 | 159.8 | 147 | 148.3 | 170.5 | 31.8 | 20.3 | 51.7 | 3.4 | 236.9 | 7 | 433.6 | 436.1 | 136.8 | 56.4 | 526 | 526.4 | 94.3 | 68.9 | 215.5 | 422.9 | 202.1 | 164.8 | 332.8 | 166.2 | 142.3 | 517.7 | 256.1 | 178.5 | 159.1 | 154.2 | 165 | 169.5 | 152 | 161.9 | 167.1
3291.1 | 3070.1 | -6.7 | 0 | 0 | 165.3 | 159.7 | 146.8 | 148.2 | 170.6 | 31.8 | 20.3 | 51.7 | 3.8 | 239 | 6.4 | 433.6 | 436 | 136.3 | 56.3 | 526 | 526.4 | 94.7 | 68.9 | 215.5 | 422.7 | 202.3 | 165 | 332.6 | 165.7 | 142.4 | 517.6 | 256.2 | 178.4 | 159.1 | 154.1 | 164.9 | 169.4 | 151.9 | 161.8 | 167
3292.1 | 3071.1 | -6.7 | 0 | 0 | 165.2 | 159.5 | 146.7 | 148 | 170.5 | 31.8 | 20.3 | 51.7 | 3.5 | 252.4 | 5.4 | 433.5 | 435.9 | 136.7 | 56.1 | 525.9 | 526.5 | 94.3 | 68.9 | 215.5 | 422.5 | 201.9 | 165.1 | 332.3 | 165.5 | 141.6 | 517.4 | 256.2 | 178.3 | 159 | 153.9 | 164.8 | 169.3 | 151.8 | 161.7 | 166.9
3293.1 | 3072.1 | -6.7 | 0 | 0 | 165.1 | 159.4 | 146.6 | 147.9 | 170.2 | 31.7 | 20.3 | 51.6 | 3.3 | 264.9 | 5.5 | 433.5 | 436.1 | 137.6 | 56 | 525.9 | 526.7 | 93.7 | 68.9 | 215.4 | 422.3 | 201.1 | 165.1 | 332.1 | 165.5 | 141.3 | 517.2 | 256.1 | 178.2 | 158.9 | 153.7 | 164.7 | 169.2 | 151.6 | 161.6 | 166.8
3294.1 | 3073.1 | -6.7 | 0 | 0 | 164.8 | 159.4 | 146.6 | 147.7 | 170.1 | 31.6 | 20.3 | 51.6 | 3.3 | 255.8 | 5.8 | 433.5 | 435.9 | 137.6 | 55.9 | 526 | 526.7 | 93 | 69 | 215.4 | 422.2 | 200.3 | 165.1 | 331.9 | 166.2 | 141.1 | 517 | 256 | 178.1 | 158.8 | 153.5 | 164.6 | 169.1 | 151.5 | 161.4 | 166.7
3295.1 | 3074.1 | -6.7 | 0 | 0 | 164.6 | 159.3 | 146.4 | 147.7 | 170.1 | 31.6 | 20.3 | 51.6 | 3.3 | 231.4 | 5.9 | 433.5 | 435.9 | 136.7 | 55.9 | 526 | 527 | 92.5 | 69.1 | 215.4 | 422 | 198.9 | 164.5 | 331.7 | 166.7 | 140.8 | 516.8 | 255.6 | 178 | 158.7 | 153.4 | 164.5 | 168.9 | 151.3 | 161.3 | 166.6
3296.1 | 3075.1 | -6.7 | 0 | 0 | 164.6 | 159.2 | 146.4 | 147.5 | 169.9 | 31.6 | 20.3 | 51.6 | 3.4 | 229.9 | 6.2 | 433.5 | 435.9 | 136.2 | 55.9 | 526 | 527.3 | 92 | 69.1 | 215.3 | 421.8 | 197.8 | 164.4 | 331.5 | 166.6 | 141.1 | 516.5 | 255.3 | 177.9 | 158.6 | 153.2 | 164.4 | 168.8 | 151.2 | 161.2 | 166.5
3297.1 | 3076.1 | -6.7 | 0 | 0 | 164.6 | 159.1 | 146.3 | 147.5 | 169.7 | 31.6 | 20.3 | 51.5 | 3.6 | 241.6 | 7 | 433.4 | 435.9 | 135.9 | 55.9 | 526 | 527.3 | 91.7 | 69.4 | 215.2 | 421.7 | 197.4 | 164.3 | 331.3 | 166.7 | 140.7 | 516.3 | 255.2 | 177.7 | 158.6 | 153.1 | 164.3 | 168.7 | 151 | 161.1 | 166.4
3298.1 | 3077.1 | -6.7 | 0 | 0 | 164.6 | 158.9 | 146.3 | 147.4 | 169.6 | 31.7 | 20.3 | 51.5 | 3.5 | 243.9 | 7 | 433.4 | 435.8 | 135.3 | 55.9 | 525.9 | 527.6 | 92.3 | 69.5 | 215.2 | 421.5 | 197.7 | 163.8 | 331.1 | 166.3 | 140.7 | 516.1 | 254.9 | 177.6 | 158.5 | 153 | 164.2 | 168.6 | 150.9 | 161 | 166.3
3299.1 | 3078.1 | -6.7 | 0 | 0 | 164.5 | 158.7 | 146.2 | 147.3 | 169.6 | 31.7 | 20.3 | 51.4 | 3.4 | 250.4 | 6.6 | 433.4 | 435.7 | 135.3 | 55.9 | 525.9 | 527.7 | 92.2 | 69.6 | 215.1 | 421.3 | 198.3 | 163.5 | 330.9 | 165.9 | 141.2 | 515.9 | 254.8 | 177.5 | 158.4 | 152.9 | 164.2 | 168.5 | 150.7 | 160.9 | 166.2
3300.1 | 3079.1 | -6.7 | 0 | 0 | 164.2 | 158.5 | 146.1 | 147.1 | 169.4 | 31.8 | 20.4 | 51.4 | 3.8 | 252.1 | 6.2 | 433.4 | 435.8 | 135.9 | 55.8 | 525.9 | 527.6 | 92.5 | 69.7 | 215.1 | 421.1 | 198 | 163.5 | 330.6 | 165.5 | 141.2 | 515.6 | 254.7 | 177.4 | 158.3 | 152.8 | 164.1 | 168.3 | 150.6 | 160.7 | 166.1
3301.1 | 3080.1 | -6.5 | 0 | 0 | 163.8 | 158.4 | 145.9 | 147 | 168.8 | 31.8 | 20.3 | 51.4 | 3.6 | 244.6 | 6.6 | 433.3 | 435.8 | 136.8 | 55.7 | 525.9 | 527.5 | 92.5 | 69.8 | 215.1 | 421 | 197.8 | 163.6 | 330.4 | 165 | 141.5 | 515.3 | 254.7 | 177.3 | 158.2 | 152.7 | 164 | 168.2 | 150.4 | 160.6 | 166
3302.1 | 3081.1 | -6.5 | 0 | 0 | 163.6 | 158.2 | 145.7 | 147 | 168.5 | 31.8 | 20.4 | 51.3 | 3.5 | 242.2 | 7 | 433.3 | 435.7 | 136.6 | 55.8 | 525.8 | 527.5 | 92.7 | 69.9 | 215.1 | 420.8 | 197.8 | 163.7 | 330.2 | 164.7 | 141.2 | 515.2 | 254.4 | 177.2 | 158.1 | 152.6 | 163.9 | 168.1 | 150.2 | 160.4 | 165.8
3303.1 | 3082.1 | -6.4 | 0 | 0 | 163.5 | 158 | 145.6 | 146.8 | 168 | 31.8 | 20.3 | 51.3 | 3.5 | 245.7 | 7.4 | 433.3 | 435.7 | 136.1 | 55.7 | 525.8 | 527.5 | 92.3 | 70 | 215.1 | 420.6 | 197.9 | 163.7 | 329.9 | 164.6 | 140.8 | 515 | 253.9 | 177.1 | 157.9 | 152.4 | 163.7 | 168 | 150.1 | 160.2 | 165.7
3304.1 | 3083.1 | -6.2 | 0 | 0 | 163.5 | 157.8 | 145.3 | 146.5 | 167.8 | 31.8 | 20.3 | 51.3 | 3.3 | 242.7 | 7.2 | 433.3 | 435.6 | 136.3 | 55.7 | 525.7 | 527.6 | 92.2 | 69.7 | 215.1 | 420.4 | 197.7 | 163.5 | 329.7 | 164.2 | 141.1 | 514.8 | 253.9 | 177 | 157.7 | 152.3 | 163.6 | 167.9 | 149.9 | 160.1 | 165.6
3305.1 | 3084.1 | -6.5 | 0 | 0 | 163.4 | 157.6 | 145.2 | 146.3 | 167.7 | 31.8 | 20.3 | 51.3 | 3.4 | 241.9 | 6.8 | 433.2 | 435.6 | 135.1 | 55.7 | 525.8 | 527.6 | 91.7 | 69.6 | 215.1 | 420.2 | 197.9 | 163.3 | 329.4 | 163.8 | 140.7 | 514.7 | 253.8 | 176.9 | 157.5 | 152.1 | 163.5 | 167.8 | 149.8 | 159.9 | 165.5
3306.1 | 3085.1 | -6.7 | 0 | 0 | 163.3 | 157.6 | 145 | 146.1 | 167.6 | 31.8 | 20.3 | 51.2 | 3.6 | 244.3 | 7.1 | 433.2 | 435.5 | 135.3 | 55.7 | 525.8 | 527.6 | 91.6 | 69.7 | 215.2 | 420.1 | 198.1 | 163.3 | 329.2 | 163.6 | 141.3 | 514.5 | 253.6 | 176.8 | 157.4 | 151.9 | 163.4 | 167.7 | 149.7 | 159.8 | 165.4
3307.1 | 3086.1 | -6.6 | 0 | 0 | 163.2 | 157.5 | 144.8 | 146 | 167.4 | 31.9 | 20.3 | 51.2 | 3.2 | 256.9 | 6.8 | 433.2 | 435.6 | 135.6 | 55.7 | 525.8 | 527.7 | 92.4 | 69.7 | 215.3 | 419.9 | 197.5 | 162.8 | 329 | 163.4 | 141.1 | 514.2 | 253.5 | 176.7 | 157.3 | 151.8 | 163.3 | 167.6 | 149.6 | 159.7 | 165.3
3308.1 | 3087.1 | -6.7 | 0 | 0 | 163.1 | 157.3 | 144.8 | 145.9 | 167.5 | 31.8 | 20.4 | 51.2 | 3.1 | 252.4 | 6.3 | 433.2 | 435.4 | 134.3 | 55.7 | 525.8 | 527.9 | 92.8 | 70 | 215.3 | 419.7 | 196.9 | 162.7 | 328.8 | 162.9 | 141.1 | 514 | 253.6 | 176.6 | 157.3 | 151.7 | 163.2 | 167.4 | 149.5 | 159.6 | 165.2
3309.1 | 3088.1 | -6.7 | 0 | 0 | 163.1 | 157.2 | 144.7 | 145.8 | 167.9 | 31.8 | 20.4 | 51.2 | 3.5 | 247.9 | 6.4 | 433.1 | 435.4 | 133.3 | 55.7 | 525.8 | 528.2 | 93.9 | 70.1 | 215.2 | 419.5 | 197.1 | 162.4 | 328.5 | 162.8 | 141 | 513.8 | 253.5 | 176.5 | 157.2 | 151.6 | 163.2 | 167.3 | 149.3 | 159.5 | 165.2
3310.1 | 3089.1 | -6.7 | 0 | 0 | 163 | 157 | 144.5 | 145.8 | 168.1 | 31.8 | 20.4 | 51.1 | 3.7 | 251.8 | 6.6 | 433.1 | 435.3 | 132.3 | 55.6 | 525.7 | 528.4 | 94.6 | 70.1 | 215.2 | 419.3 | 196.9 | 162.2 | 328.3 | 162.2 | 140.7 | 513.5 | 253.4 | 176.4 | 157.2 | 151.5 | 163.1 | 167.2 | 149.2 | 159.3 | 165.1
3311.1 | 3090.1 | -6.7 | 0 | 0 | 162.9 | 156.9 | 144.4 | 145.8 | 167.8 | 31.8 | 20.4 | 51 | 4 | 245.8 | 6.5 | 433.1 | 435.4 | 132.7 | 55.6 | 525.7 | 528.4 | 94.9 | 70.1 | 215.2 | 419.2 | 196.8 | 162.2 | 328.1 | 161.7 | 140.3 | 513.3 | 253.2 | 176.2 | 157.1 | 151.3 | 162.9 | 167.1 | 149.1 | 159.2 | 165
3312.1 | 3091.1 | -6.7 | 0 | 0 | 162.8 | 156.8 | 144.4 | 145.7 | 167.4 | 31.8 | 20.4 | 51 | 3.9 | 250.6 | 6.2 | 433.1 | 435.4 | 133.4 | 55.5 | 525.7 | 528.3 | 94.2 | 70.2 | 215.1 | 419 | 197 | 162.3 | 327.9 | 161.2 | 140.3 | 513 | 253.2 | 176.2 | 157 | 151.2 | 162.8 | 167 | 149 | 159.1 | 164.9
3313.1 | 3092.1 | -6.7 | 0 | 0 | 162.7 | 156.8 | 144.3 | 145.4 | 167.2 | 31.8 | 20.4 | 50.9 | 4 | 281.2 | 5.7 | 433.1 | 435.4 | 133.8 | 55.5 | 525.8 | 528.5 | 93.8 | 70.1 | 215.1 | 418.8 | 196.8 | 162.4 | 327.6 | 161.1 | 140.4 | 512.8 | 253.2 | 176 | 156.8 | 151 | 162.7 | 166.8 | 148.9 | 159 | 164.8
3314.1 | 3093.1 | -6.7 | 0 | 0 | 162.6 | 156.6 | 144.2 | 145.1 | 167.4 | 31.8 | 20.4 | 50.8 | 3.8 | 266.3 | 5.2 | 433 | 435.3 | 135.1 | 55.4 | 525.8 | 529 | 93.2 | 70.1 | 215 | 418.6 | 196.5 | 162.4 | 327.4 | 161.4 | 140.4 | 512.5 | 253.1 | 175.9 | 156.7 | 151 | 162.7 | 166.7 | 148.8 | 158.8 | 164.7
3315.1 | 3094.1 | -6.5 | 0 | 0 | 162.6 | 156.5 | 144.1 | 144.9 | 167.5 | 31.7 | 20.4 | 50.8 | 4.4 | 243.5 | 5.7 | 433 | 435.3 | 135.5 | 55.4 | 525.8 | 529.3 | 92.5 | 70.3 | 215 | 418.4 | 196.3 | 162 | 327.1 | 160.9 | 139.9 | 512.4 | 253 | 175.8 | 156.6 | 150.9 | 162.6 | 166.6 | 148.7 | 158.7 | 164.6
3316.1 | 3095.1 | -6.5 | 0 | 0 | 162.4 | 156.5 | 144 | 144.6 | 167.6 | 31.6 | 20.4 | 50.7 | 4 | 261.4 | 6.7 | 433 | 435.3 | 135.4 | 55.5 | 525.9 | 529.3 | 92 | 70.1 | 215.1 | 418.3 | 195.9 | 161.6 | 326.8 | 160.7 | 139.2 | 512.2 | 252.6 | 175.7 | 156.5 | 150.8 | 162.5 | 166.5 | 148.7 | 158.6 | 164.5
3317.1 | 3096.1 | -6.7 | 0 | 0 | 162.2 | 156.5 | 144 | 144.5 | 167.4 | 31.6 | 20.4 | 50.7 | 4 | 261.3 | 7.6 | 433 | 435.1 | 135.7 | 55.6 | 526 | 529.3 | 91.4 | 70.1 | 215.2 | 418.1 | 195.3 | 161.2 | 326.6 | 160.5 | 138.6 | 512 | 252.3 | 175.6 | 156.4 | 150.7 | 162.4 | 166.4 | 148.6 | 158.5 | 164.4
3318.1 | 3097.1 | -6.7 | 0 | 0 | 161.8 | 156.4 | 143.9 | 144.3 | 167.2 | 31.6 | 20.4 | 50.6 | 4 | 260.5 | 7.9 | 432.9 | 435.1 | 135.1 | 55.6 | 526.1 | 529.4 | 91.7 | 70 | 215.1 | 417.9 | 194.9 | 160.8 | 326.3 | 160.4 | 138.2 | 511.8 | 252.1 | 175.5 | 156.2 | 150.6 | 162.3 | 166.3 | 148.6 | 158.4 | 164.3
3319.1 | 3098.1 | -6.7 | 0 | 0 | 161.6 | 156.2 | 143.9 | 144.2 | 167.1 | 31.6 | 20.4 | 50.6 | 3.7 | 257.5 | 7.9 | 432.9 | 435.1 | 134.1 | 55.7 | 526.1 | 529.5 | 91.3 | 70.1 | 215.1 | 417.7 | 194.5 | 160.6 | 326 | 160.1 | 137.9 | 511.6 | 251.7 | 175.4 | 156.1 | 150.5 | 162.2 | 166.1 | 148.4 | 158.3 | 164.2
3320.1 | 3099.1 | -6.7 | 0 | 0 | 161.4 | 156.1 | 143.8 | 144.2 | 167.1 | 31.5 | 20.4 | 50.6 | 3.6 | 256.5 | 7.8 | 432.9 | 435.1 | 133 | 55.8 | 526.1 | 529.6 | 91.2 | 70 | 215 | 417.5 | 194.4 | 160.3 | 325.8 | 159.8 | 137.6 | 511.4 | 251.3 | 175.3 | 155.9 | 150.4 | 162.1 | 166 | 148.3 | 158.2 | 164.1
3321.1 | 3100.1 | -6.7 | 0 | 0 | 161.3 | 156 | 143.6 | 144 | 167 | 31.4 | 20.4 | 50.5 | 3.6 | 255.8 | 8.2 | 432.9 | 435.1 | 132.2 | 55.9 | 526.1 | 529.6 | 91.1 | 70 | 215 | 417.3 | 194.8 | 160 | 325.5 | 159.8 | 137.5 | 511.2 | 251.1 | 175.2 | 155.7 | 150.3 | 162 | 165.9 | 148.2 | 158 | 164
3322.1 | 3101.1 | -6.7 | 0 | 0 | 161.3 | 156 | 143.5 | 143.8 | 166.8 | 31.4 | 20.4 | 50.5 | 3.6 | 249.1 | 8.1 | 432.8 | 435.1 | 131 | 55.8 | 526.1 | 529.5 | 91.4 | 70 | 215 | 417.2 | 195 | 159.5 | 325.2 | 159.4 | 137.5 | 511 | 251 | 175.1 | 155.7 | 150.1 | 161.9 | 165.7 | 148 | 157.9 | 163.9
3323.1 | 3102.1 | -6.7 | 0 | 0 | 161.2 | 156 | 143.4 | 143.7 | 166.4 | 31.4 | 20.4 | 50.4 | 3.2 | 244.2 | 7.8 | 432.8 | 435 | 130.6 | 55.7 | 526.1 | 529.4 | 92.2 | 69.9 | 215 | 417 | 195.5 | 159.4 | 325 | 158.8 | 137.5 | 510.7 | 250.6 | 175 | 155.6 | 150 | 161.8 | 165.6 | 147.9 | 157.8 | 163.8
3324.1 | 3103.1 | -6.7 | 0 | 0 | 161 | 155.9 | 143.2 | 143.5 | 166 | 31.4 | 20.4 | 50.4 | 3.2 | 244.5 | 7.3 | 432.8 | 435.1 | 130.9 | 55.6 | 526.1 | 529.7 | 91.6 | 69.8 | 214.9 | 416.8 | 196.2 | 159.6 | 324.7 | 158.6 | 137.1 | 510.4 | 250.4 | 174.9 | 155.5 | 149.9 | 161.7 | 165.5 | 147.8 | 157.6 | 163.7
3325.1 | 3104.1 | -6.7 | 0 | 0 | 160.8 | 155.8 | 143.1 | 143.5 | 166.1 | 31.4 | 20.4 | 50.4 | 3.3 | 244.1 | 7 | 432.8 | 434.9 | 130.7 | 55.5 | 526 | 530.1 | 91.4 | 69.7 | 214.9 | 416.6 | 196.5 | 159.8 | 324.5 | 158.3 | 136.8 | 510.2 | 250.2 | 174.8 | 155.4 | 149.7 | 161.6 | 165.4 | 147.7 | 157.5 | 163.6
3326.1 | 3105.1 | -6.7 | 0 | 0 | 160.7 | 155.8 | 142.9 | 143.4 | 165.8 | 31.3 | 20.4 | 50.3 | 3.6 | 242.9 | 7.1 | 432.7 | 434.9 | 131.5 | 55.4 | 526 | 530.6 | 91.9 | 69.5 | 214.8 | 416.4 | 197.2 | 159.7 | 324.2 | 158 | 136.8 | 509.9 | 250.2 | 174.7 | 155.3 | 149.4 | 161.5 | 165.3 | 147.6 | 157.4 | 163.5
3327.1 | 3106.1 | -6.7 | 0 | 0 | 160.6 | 155.8 | 142.7 | 143.3 | 165.4 | 31.4 | 20.4 | 50.3 | 3.1 | 243.2 | 7.3 | 432.7 | 434.8 | 132.5 | 55.2 | 525.9 | 530.6 | 91.5 | 69.4 | 214.8 | 416.2 | 197.5 | 159.7 | 324 | 158.2 | 137.1 | 509.6 | 250 | 174.6 | 155.2 | 149.2 | 161.4 | 165.1 | 147.5 | 157.3 | 163.4
3328.1 | 3107.1 | -6.7 | 0 | 0 | 160.4 | 155.6 | 142.6 | 143.3 | 165.2 | 31.4 | 20.4 | 50.3 | 3 | 244.1 | 7.3 | 432.7 | 434.8 | 132.9 | 55.1 | 526 | 530.4 | 90.8 | 69.3 | 214.7 | 416.1 | 198 | 159.9 | 323.8 | 158 | 136.7 | 509.4 | 249.9 | 174.5 | 155.1 | 149.1 | 161.3 | 165 | 147.4 | 157.1 | 163.3
3329.1 | 3108.1 | -6.7 | 0 | 0 | 160.3 | 155.4 | 142.4 | 143.2 | 165.3 | 31.4 | 20.4 | 50.3 | 3 | 242.7 | 7.1 | 432.7 | 434.7 | 132.2 | 54.9 | 526 | 530.3 | 91.1 | 69 | 214.7 | 415.9 | 197.9 | 159.9 | 323.5 | 158.3 | 136.3 | 509.1 | 249.5 | 174.4 | 155 | 148.9 | 161.2 | 164.9 | 147.3 | 157 | 163.2
3330.1 | 3109.1 | -6.7 | 0 | 0 | 160.3 | 155.2 | 142.3 | 143.2 | 165.4 | 31.4 | 20.4 | 50.3 | 3.1 | 242.1 | 6.9 | 432.7 | 434.7 | 131.2 | 54.7 | 525.9 | 530.1 | 92.6 | 68.7 | 214.6 | 415.7 | 197.8 | 160.1 | 323.3 | 158.9 | 136.2 | 508.8 | 249.4 | 174.2 | 154.9 | 148.8 | 161.1 | 164.8 | 147.2 | 156.9 | 163.1
3331.1 | 3110.1 | -6.6 | 0 | 0 | 160.2 | 155.1 | 142.2 | 143.1 | 165.5 | 31.4 | 20.4 | 50.2 | 3.9 | 239.6 | 6.7 | 432.6 | 434.6 | 131.1 | 54.5 | 525.9 | 530 | 92.8 | 68.5 | 214.5 | 415.5 | 197.9 | 160.1 | 323 | 158.8 | 135.7 | 508.6 | 249.3 | 174.1 | 154.8 | 148.7 | 161 | 164.6 | 147.1 | 156.8 | 163
3332.1 | 3111.1 | -6.5 | 0 | 0 | 160.1 | 154.9 | 142 | 143.1 | 165.7 | 31.3 | 20.4 | 50.2 | 3.7 | 242.4 | 6.4 | 432.6 | 434.7 | 132.3 | 54.5 | 526 | 529.8 | 92.2 | 68.3 | 214.3 | 415.3 | 197.3 | 160 | 322.8 | 158.6 | 135.1 | 508.2 | 249 | 174 | 154.6 | 148.6 | 160.9 | 164.5 | 147 | 156.6 | 162.9
3333.1 | 3112.1 | -6.2 | 0 | 0 | 160.1 | 154.7 | 141.8 | 143 | 165.8 | 31.3 | 20.4 | 50.2 | 3.8 | 242.3 | 6.4 | 432.6 | 434.6 | 132.4 | 54.5 | 526 | 529.6 | 92.1 | 68.1 | 214.1 | 415.1 | 196.3 | 159.7 | 322.5 | 158.4 | 134.6 | 507.9 | 248.6 | 173.9 | 154.5 | 148.4 | 160.9 | 164.3 | 146.9 | 156.5 | 162.8
3334.1 | 3113.1 | -6.4 | 0 | 0 | 159.9 | 154.5 | 141.6 | 142.8 | 165.8 | 31.3 | 20.4 | 50.1 | 3.7 | 243.5 | 6.4 | 432.6 | 434.5 | 132.6 | 54.5 | 526 | 529.4 | 92.3 | 67.9 | 214.2 | 415 | 196 | 159.5 | 322.3 | 157.8 | 134.7 | 507.6 | 248.2 | 173.8 | 154.3 | 148.3 | 160.8 | 164.2 | 146.8 | 156.4 | 162.7
3335.1 | 3114.1 | -6.7 | 0 | 0 | 159.8 | 154.4 | 141.5 | 142.7 | 165.6 | 31.2 | 20.4 | 50.1 | 3.8 | 242.3 | 6.3 | 432.5 | 434.5 | 133.9 | 54.6 | 526 | 529.2 | 91.8 | 67.8 | 214.2 | 414.8 | 196.1 | 159.7 | 322.1 | 157.3 | 134.6 | 507.4 | 247.9 | 173.7 | 154.2 | 148.1 | 160.7 | 164.1 | 146.7 | 156.2 | 162.6
3336.1 | 3115.1 | -6.7 | 0 | 0 | 159.6 | 154.4 | 141.4 | 142.6 | 165.3 | 31.1 | 20.4 | 50.1 | 4.2 | 250.1 | 6 | 432.5 | 434.5 | 133.3 | 54.7 | 526.1 | 529.3 | 91.4 | 67.8 | 214.3 | 414.6 | 195.4 | 159.5 | 321.8 | 157.2 | 134.1 | 507 | 247.8 | 173.5 | 154 | 148 | 160.6 | 163.9 | 146.6 | 156.1 | 162.5
3337.1 | 3116.1 | -6.7 | 0 | 0 | 159.5 | 154.3 | 141.4 | 142.5 | 164.9 | 31 | 20.4 | 50 | 3.8 | 257.8 | 5.8 | 432.5 | 434.5 | 133.4 | 54.7 | 526.1 | 529.3 | 91.1 | 67.8 | 214.4 | 414.4 | 195.5 | 159.6 | 321.6 | 157.2 | 133.8 | 506.8 | 247.5 | 173.4 | 153.9 | 147.8 | 160.5 | 163.8 | 146.5 | 156 | 162.4
3338.1 | 3117.1 | -6.7 | 0 | 0 | 159.5 | 154.1 | 141.3 | 142.4 | 164.5 | 31 | 20.4 | 50 | 3.7 | 246 | 5.5 | 432.5 | 434.5 | 133.2 | 54.8 | 526.1 | 529.1 | 90.5 | 67.5 | 214.4 | 414.2 | 195.4 | 159.3 | 321.3 | 157.2 | 133.5 | 506.5 | 247.3 | 173.3 | 153.8 | 147.7 | 160.4 | 163.7 | 146.4 | 155.8 | 162.3
3339.1 | 3118.1 | -6.7 | 0 | 0 | 159.4 | 153.9 | 141.2 | 142.3 | 164.1 | 30.9 | 20.4 | 50 | 3.6 | 244.2 | 5.5 | 432.4 | 434.4 | 133.8 | 54.7 | 526.1 | 529 | 90.2 | 67.5 | 214.5 | 414.1 | 195.7 | 159.3 | 321.1 | 157.3 | 133.9 | 506.1 | 247.3 | 173.2 | 153.7 | 147.6 | 160.3 | 163.6 | 146.3 | 155.7 | 162.2
3340.1 | 3119.1 | -6.7 | 0 | 0 | 159.3 | 153.9 | 141.1 | 142.2 | 163.8 | 30.8 | 20.4 | 50 | 3.1 | 249.7 | 5.8 | 432.4 | 434.4 | 132.4 | 54.7 | 526.2 | 529 | 90.5 | 67.7 | 214.4 | 413.9 | 195.8 | 159.2 | 320.9 | 156.9 | 134.3 | 505.8 | 247.2 | 173.1 | 153.5 | 147.5 | 160.2 | 163.5 | 146.2 | 155.6 | 162.1
3341.1 | 3120.1 | -6.7 | 0 | 0 | 159.3 | 153.8 | 141 | 142.1 | 164.1 | 30.8 | 20.4 | 50 | 3.2 | 257 | 6.2 | 432.4 | 434.3 | 131.8 | 54.5 | 526.2 | 528.9 | 90.4 | 67.9 | 214.4 | 413.7 | 196.1 | 158.7 | 320.6 | 156.6 | 134.2 | 505.4 | 247.1 | 173 | 153.3 | 147.4 | 160.1 | 163.3 | 146 | 155.5 | 162
3342.1 | 3121.1 | -6.7 | 0 | 0 | 159.2 | 153.6 | 140.8 | 142 | 164.5 | 30.9 | 20.4 | 50 | 3 | 249.3 | 6.4 | 432.4 | 434.3 | 131.5 | 54.3 | 526.2 | 528.8 | 90.6 | 67.8 | 214.4 | 413.5 | 195.5 | 158.4 | 320.4 | 156.3 | 134.3 | 505.1 | 246.9 | 172.9 | 153.2 | 147.2 | 160 | 163.2 | 146 | 155.4 | 161.9
3343.1 | 3122.1 | -6.7 | 0 | 0 | 159.2 | 153.3 | 140.8 | 141.9 | 164.4 | 30.9 | 20.4 | 50 | 3.1 | 252.6 | 6.7 | 432.4 | 434.2 | 130.7 | 54.2 | 526.2 | 528.6 | 90.4 | 67.7 | 214.3 | 413.3 | 195.2 | 158.5 | 320.2 | 156.1 | 134.4 | 504.8 | 246.7 | 172.8 | 153 | 147 | 159.8 | 163.1 | 145.9 | 155.3 | 161.8
3344.1 | 3123.1 | -6.6 | 0 | 0 | 159.1 | 153.2 | 140.7 | 141.8 | 164.2 | 30.9 | 20.4 | 50 | 3.1 | 253 | 6.7 | 432.3 | 434.2 | 131.2 | 54.2 | 526.2 | 528.6 | 89.7 | 67.6 | 214.3 | 413.2 | 194.7 | 158.5 | 319.9 | 155.8 | 133.8 | 504.5 | 246.4 | 172.7 | 152.9 | 146.9 | 159.7 | 162.9 | 145.8 | 155.2 | 161.7
3345.1 | 3124.1 | -6.6 | 0 | 0 | 159 | 153.1 | 140.6 | 141.7 | 164.2 | 30.9 | 20.4 | 50 | 3.1 | 257.1 | 6.8 | 432.3 | 434.2 | 132 | 54.3 | 526.2 | 528.6 | 89.2 | 67.5 | 214.3 | 413 | 194.3 | 158 | 319.7 | 155.7 | 133.6 | 504.2 | 246 | 172.6 | 152.7 | 146.8 | 159.6 | 162.8 | 145.7 | 155.1 | 161.6
3346.1 | 3125.1 | -6.7 | 0 | 0 | 158.9 | 153.1 | 140.5 | 141.7 | 164.1 | 30.9 | 20.4 | 50 | 3 | 258.9 | 6.6 | 432.3 | 434.2 | 131.8 | 54.3 | 526.3 | 528.6 | 88.7 | 67.4 | 214.3 | 412.9 | 193.8 | 157.9 | 319.4 | 155.5 | 133.4 | 504 | 245.7 | 172.4 | 152.6 | 146.7 | 159.6 | 162.6 | 145.7 | 155 | 161.5
3347.1 | 3126.1 | -6.7 | 0 | 0 | 158.8 | 153 | 140.3 | 141.6 | 163.9 | 30.9 | 20.4 | 50 | 3.2 | 251.1 | 6.5 | 432.3 | 434.1 | 131.9 | 54.4 | 526.3 | 528.5 | 87.9 | 67.4 | 214.4 | 412.7 | 192.4 | 157.8 | 319.1 | 155.4 | 132.9 | 503.7 | 245.4 | 172.3 | 152.6 | 146.6 | 159.5 | 162.5 | 145.6 | 154.8 | 161.4
3348.1 | 3127.1 | -6.7 | 0 | 0 | 158.7 | 153 | 140.2 | 141.5 | 163.7 | 30.8 | 20.4 | 50 | 3.4 | 253.3 | 6.4 | 432.2 | 434 | 133 | 54.3 | 526.4 | 528.3 | 87 | 67.3 | 214.6 | 412.5 | 192.1 | 157.7 | 318.9 | 155.3 | 132.7 | 503.3 | 245.2 | 172.2 | 152.6 | 146.5 | 159.4 | 162.4 | 145.5 | 154.7 | 161.3
3349.1 | 3128.1 | -6.7 | 0 | 0 | 158.5 | 152.9 | 140 | 141.3 | 163.6 | 30.8 | 20.4 | 49.9 | 3.2 | 250.5 | 6.2 | 432.2 | 434.1 | 133.1 | 54.3 | 526.5 | 528 | 87.2 | 67.2 | 214.5 | 412.4 | 192.4 | 157.2 | 318.6 | 155 | 132.4 | 502.9 | 245.1 | 172.1 | 152.5 | 146.4 | 159.3 | 162.3 | 145.4 | 154.5 | 161.2
3350.1 | 3129.1 | -6.7 | 0 | 0 | 158.3 | 152.9 | 139.8 | 141.2 | 163.4 | 30.8 | 20.4 | 49.8 | 3.3 | 248.1 | 6 | 432.2 | 434 | 132.4 | 54.3 | 526.5 | 527.8 | 88.5 | 67.2 | 214.4 | 412.2 | 193 | 156.8 | 318.3 | 154.8 | 132.5 | 502.6 | 244.7 | 172 | 152.5 | 146.3 | 159.2 | 162.1 | 145.3 | 154.4 | 161.1
3351.1 | 3130.1 | -6.7 | 0 | 0 | 158.2 | 152.8 | 139.7 | 141.1 | 163.2 | 30.8 | 20.4 | 49.8 | 3.3 | 249.7 | 5.9 | 432.2 | 433.9 | 131.2 | 54.3 | 526.5 | 528 | 89.7 | 67.2 | 214.2 | 412 | 193.3 | 156.8 | 318.1 | 154.6 | 133 | 502.2 | 244.6 | 171.8 | 152.4 | 146.2 | 159.1 | 162 | 145.2 | 154.3 | 161
3352.1 | 3131.1 | -6.7 | 0 | 0 | 158.1 | 152.7 | 139.7 | 141 | 163.4 | 30.8 | 20.4 | 49.8 | 3 | 247.2 | 5.7 | 432.1 | 433.9 | 129.9 | 54.3 | 526.5 | 528.2 | 90.2 | 67.3 | 214.2 | 411.8 | 192.6 | 156.6 | 317.8 | 154.2 | 132.7 | 501.9 | 244.5 | 171.7 | 152.3 | 146.1 | 159 | 161.9 | 145 | 154.2 | 160.9
3353.1 | 3132.1 | -6.7 | 0 | 0 | 158 | 152.7 | 139.7 | 140.9 | 163.4 | 30.8 | 20.4 | 49.7 | 3.2 | 250.9 | 5.6 | 432.1 | 433.8 | 129.2 | 54.4 | 526.4 | 528.2 | 91.6 | 67.3 | 214.2 | 411.6 | 192.3 | 156.3 | 317.6 | 154.5 | 132.3 | 501.5 | 244.2 | 171.6 | 152.3 | 146 | 158.9 | 161.8 | 145 | 154 | 160.8
3354.1 | 3133.1 | -6.7 | 0 | 0 | 157.8 | 152.6 | 139.6 | 140.7 | 163.4 | 30.8 | 20.4 | 49.7 | 3.2 | 255.7 | 5.3 | 432.1 | 433.9 | 128.2 | 54.3 | 526.3 | 528.3 | 91.9 | 67.4 | 214.2 | 411.5 | 192.2 | 156.3 | 317.4 | 154.5 | 132.2 | 501.2 | 244.1 | 171.5 | 152.1 | 145.9 | 158.8 | 161.7 | 144.8 | 153.9 | 160.7
3355.1 | 3134.1 | -6.6 | 0 | 0 | 157.7 | 152.5 | 139.4 | 140.6 | 163.6 | 30.8 | 20.4 | 49.6 | 3.1 | 253.8 | 5.2 | 432.1 | 433.9 | 128.2 | 54.2 | 526.2 | 528.5 | 91.5 | 67.3 | 214.2 | 411.3 | 191.7 | 156.2 | 317.1 | 154.8 | 132.5 | 500.8 | 244.2 | 171.4 | 152 | 145.8 | 158.7 | 161.6 | 144.8 | 153.8 | 160.6
3356.1 | 3135.1 | -6.6 | 0 | 0 | 157.5 | 152.4 | 139.2 | 140.5 | 163.7 | 30.8 | 20.4 | 49.6 | 3 | 252.5 | 4.9 | 432 | 433.8 | 128.3 | 54.1 | 526.2 | 528.6 | 91.3 | 67.3 | 214.2 | 411.1 | 192.6 | 156 | 316.9 | 155 | 132 | 500.4 | 244 | 171.3 | 151.9 | 145.7 | 158.6 | 161.5 | 144.6 | 153.7 | 160.5
3357.1 | 3136.1 | -6.7 | 0 | 0 | 157.1 | 152.3 | 139.1 | 140.4 | 163.4 | 30.9 | 20.4 | 49.6 | 2.9 | 254.8 | 4.5 | 432 | 433.8 | 127.4 | 54.1 | 526.1 | 529.4 | 92.1 | 67.1 | 214.2 | 410.9 | 193.2 | 155.9 | 316.6 | 155.1 | 131.5 | 500.1 | 243.7 | 171.1 | 151.9 | 145.6 | 158.4 | 161.4 | 144.5 | 153.6 | 160.4
3358.1 | 3137.1 | -6.2 | 0 | 0 | 157 | 152.2 | 139.1 | 140.3 | 162.9 | 30.9 | 20.4 | 49.5 | 3.2 | 261.5 | 4.4 | 432 | 433.7 | 126.2 | 54 | 526.1 | 529.9 | 92.7 | 67.1 | 214.3 | 410.7 | 193.6 | 155.8 | 316.3 | 155.1 | 131.1 | 499.6 | 243.3 | 171 | 151.8 | 145.6 | 158.4 | 161.3 | 144.5 | 153.5 | 160.3
3359.1 | 3138.1 | -5.6 | 0 | 0 | 157 | 152.1 | 139 | 140.3 | 162.6 | 30.9 | 20.4 | 49.5 | 3.1 | 253.8 | 4.6 | 432 | 433.6 | 125.3 | 53.9 | 526 | 530.5 | 93.1 | 67.3 | 214.1 | 410.5 | 193.3 | 155.8 | 316 | 155.6 | 130.8 | 499.2 | 243.1 | 170.9 | 151.8 | 145.4 | 158.3 | 161.2 | 144.3 | 153.4 | 160.2
3360.1 | 3139.1 | -5.9 | 0 | 0 | 157 | 152 | 138.9 | 140.2 | 162.6 | 30.9 | 20.4 | 49.4 | 3.4 | 253.2 | 4.9 | 431.9 | 433.7 | 125.9 | 53.9 | 525.9 | 530.7 | 93 | 67.3 | 214.1 | 410.3 | 192.6 | 155.6 | 315.7 | 155.7 | 130.7 | 498.8 | 242.9 | 170.8 | 151.6 | 145.3 | 158.2 | 161.1 | 144.2 | 153.2 | 160.1
3361.1 | 3140.1 | -5.9 | 0 | 0 | 156.9 | 152 | 138.8 | 140.1 | 162.7 | 30.9 | 20.4 | 49.4 | 3.5 | 257.9 | 5.1 | 431.9 | 433.6 | 125.4 | 53.8 | 525.9 | 530.9 | 92.8 | 67.1 | 214 | 410.2 | 192.1 | 155.5 | 315.4 | 155.2 | 130.9 | 498.4 | 242.9 | 170.8 | 151.5 | 145.2 | 158.1 | 161 | 144.1 | 153.1 | 160
3362.1 | 3141.1 | -5.5 | 0 | 0 | 156.8 | 151.9 | 138.7 | 140 | 162.7 | 30.8 | 20.4 | 49.3 | 3.5 | 258.6 | 5.2 | 431.9 | 433.6 | 124.7 | 53.8 | 525.8 | 531 | 92.4 | 67.1 | 213.9 | 410 | 192 | 155.3 | 315.2 | 154.6 | 130.6 | 498 | 242.5 | 170.7 | 151.3 | 145.1 | 158.1 | 160.9 | 143.9 | 153 | 159.9
3363.1 | 3142.1 | -6.1 | 0 | 0 | 156.7 | 151.8 | 138.6 | 139.9 | 162.8 | 30.8 | 20.4 | 49.3 | 3.5 | 258.5 | 5.2 | 431.9 | 433.6 | 125.5 | 53.7 | 525.8 | 531.1 | 92.6 | 67 | 213.8 | 409.8 | 192 | 155.1 | 314.9 | 154 | 130.4 | 497.7 | 241.9 | 170.6 | 151.3 | 145 | 158 | 160.8 | 143.8 | 152.9 | 159.8
3364.1 | 3143.1 | -6.6 | 0 | 0 | 156.6 | 151.7 | 138.5 | 139.9 | 162.9 | 30.8 | 20.4 | 49.3 | 3.4 | 258.6 | 5.1 | 431.8 | 433.4 | 124.9 | 53.8 | 525.7 | 531.1 | 93.3 | 67 | 213.8 | 409.6 | 191.6 | 154.8 | 314.7 | 153.8 | 130.3 | 497.3 | 241.7 | 170.4 | 151.2 | 144.9 | 157.9 | 160.7 | 143.7 | 152.8 | 159.7
3365.1 | 3144.1 | -6.7 | 0 | 0 | 156.5 | 151.6 | 138.5 | 139.8 | 162.9 | 30.8 | 20.4 | 49.3 | 3.6 | 258.9 | 5.1 | 431.8 | 433.5 | 124.9 | 53.8 | 525.6 | 531 | 93 | 66.9 | 213.8 | 409.5 | 191.4 | 154.6 | 314.4 | 153.7 | 130.2 | 497 | 241.5 | 170.4 | 151 | 144.8 | 157.8 | 160.5 | 143.6 | 152.7 | 159.6
3366.1 | 3145.1 | -6.7 | 0 | 0 | 156.4 | 151.5 | 138.4 | 139.7 | 163 | 30.8 | 20.4 | 49.3 | 3.6 | 259.7 | 5.1 | 431.8 | 433.5 | 125.3 | 53.7 | 525.6 | 530.8 | 92.3 | 66.6 | 213.8 | 409.3 | 192 | 154.4 | 314.2 | 153.7 | 130.4 | 496.5 | 241.4 | 170.3 | 150.9 | 144.7 | 157.7 | 160.4 | 143.4 | 152.6 | 159.5
3367.1 | 3146.1 | -6.7 | 0 | 0 | 156.2 | 151.4 | 138.3 | 139.5 | 163.1 | 30.8 | 20.4 | 49.2 | 3.4 | 263.6 | 5.1 | 431.8 | 433.4 | 124.9 | 53.5 | 525.6 | 531 | 91.5 | 66.5 | 213.8 | 409.1 | 192 | 154 | 313.9 | 153.5 | 130.9 | 496.1 | 241.3 | 170.2 | 150.7 | 144.6 | 157.6 | 160.3 | 143.3 | 152.5 | 159.5
3368.1 | 3147.1 | -6.7 | 0 | 0 | 156 | 151.2 | 138.2 | 139.5 | 163.1 | 30.7 | 20.4 | 49.2 | 3.4 | 265.9 | 5.3 | 431.8 | 433.4 | 125.4 | 53.6 | 525.6 | 531.4 | 90.8 | 66.5 | 213.8 | 409 | 191.5 | 154 | 313.7 | 152.6 | 130.7 | 495.7 | 241.2 | 170.1 | 150.5 | 144.5 | 157.5 | 160.3 | 143.2 | 152.4 | 159.4
3369.1 | 3148.1 | -6.7 | 0 | 0 | 156 | 150.9 | 138.1 | 139.4 | 163.1 | 30.7 | 20.4 | 49.2 | 3.4 | 269.3 | 5.4 | 431.8 | 433.4 | 125.2 | 53.7 | 525.7 | 531.4 | 90.8 | 66.5 | 213.8 | 408.8 | 191.9 | 153.6 | 313.4 | 151.7 | 130.5 | 495.2 | 241 | 170 | 150.4 | 144.3 | 157.4 | 160.2 | 143.1 | 152.3 | 159.3
3370.1 | 3149.1 | -6.7 | 0 | 0 | 155.9 | 150.7 | 138 | 139.3 | 163.1 | 30.6 | 20.4 | 49.2 | 3.4 | 268.8 | 5.5 | 431.7 | 433.3 | 125 | 53.8 | 525.7 | 531.3 | 91 | 66.5 | 213.8 | 408.6 | 191.8 | 153.4 | 313.1 | 151.3 | 130.8 | 494.8 | 240.7 | 169.9 | 150.3 | 144.2 | 157.3 | 160.1 | 143 | 152.2 | 159.2
3371.1 | 3150.1 | -6.6 | 0 | 0 | 155.8 | 150.5 | 137.9 | 139.2 | 162.8 | 30.6 | 20.4 | 49.2 | 3.4 | 272.7 | 5.7 | 431.7 | 433.2 | 124.8 | 53.8 | 525.7 | 531.1 | 90.7 | 66.5 | 213.7 | 408.4 | 192.1 | 153.3 | 312.8 | 150.9 | 130.8 | 494.4 | 240.7 | 169.7 | 150.3 | 144.1 | 157.2 | 160 | 142.9 | 152.1 | 159.1
3372.1 | 3151.1 | -6.3 | 0 | 0 | 155.7 | 150.4 | 137.8 | 139.1 | 162.3 | 30.6 | 20.5 | 49.2 | 3.3 | 277.2 | 5.7 | 431.7 | 433.2 | 123.5 | 53.8 | 525.7 | 531 | 90.8 | 66.6 | 213.8 | 408.3 | 191.9 | 153.1 | 312.6 | 150.5 | 130.6 | 494.1 | 240.2 | 169.6 | 150.1 | 144 | 157.1 | 159.9 | 142.8 | 152 | 159
3373.1 | 3152.1 | -6.1 | 0 | 0 | 155.6 | 150.3 | 137.7 | 139 | 162.4 | 30.5 | 20.5 | 49.2 | 3.3 | 280.5 | 5.4 | 431.7 | 433.1 | 122.7 | 53.8 | 525.7 | 530.8 | 91.1 | 66.6 | 213.8 | 408.1 | 191.6 | 152.9 | 312.3 | 150.1 | 130.7 | 493.9 | 239.9 | 169.5 | 149.9 | 143.9 | 157 | 159.8 | 142.7 | 151.9 | 158.9
3374.1 | 3153.1 | -6 | 0 | 0 | 155.5 | 150.1 | 137.5 | 139 | 162.7 | 30.4 | 20.5 | 49.1 | 3.4 | 275.6 | 5.1 | 431.7 | 433.1 | 123 | 53.9 | 525.8 | 530.5 | 90.6 | 66.6 | 213.7 | 407.9 | 191.3 | 152.6 | 312.1 | 149.6 | 130.2 | 493.5 | 239.9 | 169.4 | 149.8 | 143.8 | 157 | 159.7 | 142.6 | 151.8 | 158.8
3375.1 | 3154.1 | -6.3 | 0 | 0 | 155.3 | 150 | 137.4 | 138.8 | 163 | 30.4 | 20.5 | 49.1 | 3.2 | 269.6 | 5 | 431.6 | 433.2 | 124 | 53.9 | 525.8 | 530.2 | 89.9 | 66.4 | 213.9 | 407.7 | 191.1 | 152.2 | 311.8 | 149.8 | 129.8 | 493.1 | 239.7 | 169.3 | 149.7 | 143.7 | 156.9 | 159.6 | 142.5 | 151.6 | 158.7
3376.1 | 3155.1 | -6.3 | 0 | 0 | 154.9 | 149.9 | 137.3 | 138.7 | 163 | 30.4 | 20.5 | 49.1 | 3 | 268.7 | 5.1 | 431.6 | 433.1 | 124.7 | 53.8 | 525.9 | 529.7 | 89.2 | 66.4 | 213.8 | 407.5 | 190.5 | 151.8 | 311.5 | 149.8 | 129.4 | 492.8 | 239.5 | 169.2 | 149.6 | 143.6 | 156.8 | 159.4 | 142.4 | 151.5 | 158.6
3377.1 | 3156.1 | -6.3 | 0 | 0 | 154.7 | 149.8 | 137.2 | 138.6 | 162.9 | 30.4 | 20.5 | 49.1 | 3.2 | 274.2 | 5.1 | 431.6 | 433.1 | 125.3 | 53.7 | 525.9 | 529.2 | 88.7 | 66.2 | 213.8 | 407.3 | 190.2 | 151.3 | 311.2 | 149.8 | 129.1 | 492.5 | 239.1 | 169.1 | 149.5 | 143.5 | 156.7 | 159.3 | 142.3 | 151.4 | 158.5
3378.1 | 3157.1 | -6.7 | 0 | 0 | 154.6 | 149.8 | 137.2 | 138.5 | 162.8 | 30.4 | 20.5 | 49 | 2.9 | 275.8 | 5.1 | 431.6 | 433.1 | 126.5 | 53.6 | 526 | 528.6 | 88.4 | 66 | 213.7 | 407.1 | 190.6 | 150.6 | 310.9 | 149.4 | 129 | 492.2 | 238.6 | 169 | 149.5 | 143.4 | 156.6 | 159.1 | 142.2 | 151.2 | 158.4
3379.1 | 3158.1 | -6.7 | 0 | 0 | 154.5 | 149.7 | 137.2 | 138.4 | 162.6 | 30.5 | 20.5 | 49 | 2.9 | 265.9 | 4.9 | 431.6 | 433 | 128.5 | 53.6 | 526.1 | 528.1 | 88.1 | 65.8 | 213.7 | 407 | 190.9 | 150.6 | 310.7 | 149 | 128.8 | 491.9 | 238.3 | 168.9 | 149.4 | 143.3 | 156.5 | 159 | 142.1 | 151.1 | 158.3
3380.1 | 3159.1 | -6.6 | 0 | 0 | 154.4 | 149.6 | 137.1 | 138.3 | 162.6 | 30.5 | 20.5 | 49 | 2.9 | 264.9 | 4.9 | 431.6 | 433 | 129.6 | 53.5 | 526.2 | 527.7 | 87.5 | 65.6 | 213.8 | 406.7 | 190.6 | 150.2 | 310.4 | 148.9 | 128.8 | 491.5 | 238.3 | 168.8 | 149.3 | 143.2 | 156.4 | 158.8 | 142 | 150.9 | 158.2
3381.1 | 3160.1 | -6.5 | 0 | 0 | 154.2 | 149.5 | 137 | 138.2 | 162.6 | 30.5 | 20.5 | 48.9 | 3.1 | 271.4 | 4.7 | 431.5 | 432.9 | 131.3 | 53.4 | 526.3 | 527.3 | 87.2 | 65.5 | 213.8 | 406.6 | 190.8 | 149.9 | 310.1 | 148.9 | 128.4 | 491.2 | 238 | 168.7 | 149.1 | 143.1 | 156.3 | 158.7 | 141.9 | 150.8 | 158.1
3382.1 | 3161.1 | -6.7 | 0 | 0 | 154 | 149.3 | 136.7 | 138.1 | 162.5 | 30.6 | 20.5 | 48.9 | 3.1 | 268.4 | 4.3 | 431.5 | 432.9 | 132.4 | 53.4 | 526.4 | 526.9 | 86.7 | 65.3 | 213.8 | 406.3 | 190.7 | 149.6 | 309.9 | 148.8 | 128.1 | 490.8 | 237.7 | 168.6 | 149 | 143 | 156.2 | 158.5 | 141.8 | 150.8 | 158
3383.1 | 3162.1 | -6.8 | 0 | 0 | 153.9 | 149.3 | 136.7 | 138 | 162.6 | 30.5 | 20.5 | 48.9 | 2.8 | 265 | 4 | 431.5 | 432.9 | 133.7 | 53.5 | 526.5 | 526.6 | 86.3 | 65.1 | 213.8 | 406.2 | 190.9 | 149.6 | 309.7 | 148.5 | 127.7 | 490.4 | 237.5 | 168.5 | 148.9 | 142.9 | 156.1 | 158.4 | 141.7 | 150.7 | 157.9
3384.1 | 3163.1 | -6.7 | 0 | 0 | 153.8 | 149.1 | 136.6 | 137.9 | 162.5 | 30.4 | 20.5 | 48.8 | 3.2 | 270.4 | 3.8 | 431.5 | 432.8 | 133 | 53.8 | 526.5 | 526.6 | 86.9 | 65.1 | 213.7 | 406 | 191.5 | 149.4 | 309.4 | 148.3 | 127.5 | 489.9 | 237.4 | 168.4 | 148.8 | 142.8 | 156.1 | 158.3 | 141.6 | 150.6 | 157.8
3385.1 | 3164.1 | -6.7 | 0 | 0 | 153.7 | 148.9 | 136.6 | 137.8 | 162.3 | 30.5 | 20.5 | 48.8 | 3.4 | 272.9 | 3.9 | 431.5 | 432.8 | 132.6 | 53.9 | 526.5 | 526.5 | 87.3 | 65 | 213.8 | 405.8 | 192.3 | 149.3 | 309.1 | 147.9 | 127.6 | 489.4 | 237 | 168.3 | 148.6 | 142.7 | 156 | 158.2 | 141.6 | 150.5 | 157.7
3386.1 | 3165.1 | -6.7 | 0 | 0 | 153.5 | 148.7 | 136.5 | 137.7 | 162.2 | 30.5 | 20.5 | 48.8 | 3 | 269.9 | 4.2 | 431.5 | 432.7 | 132.5 | 53.8 | 526.5 | 526.3 | 88.2 | 65 | 213.7 | 405.7 | 192.5 | 149.3 | 308.9 | 147.6 | 127.5 | 489 | 236.7 | 168.2 | 148.5 | 142.7 | 155.9 | 158.1 | 141.5 | 150.3 | 157.6
3387.1 | 3166.1 | -6.7 | 0 | 0 | 153.4 | 148.5 | 136.3 | 137.5 | 162.1 | 30.5 | 20.5 | 48.7 | 3.1 | 261.7 | 4.4 | 431.4 | 432.7 | 131 | 53.6 | 526.5 | 526.5 | 88.2 | 65.2 | 213.5 | 405.5 | 193 | 149.2 | 308.6 | 147.3 | 127.5 | 488.5 | 236.6 | 168.1 | 148.5 | 142.6 | 155.8 | 158 | 141.4 | 150.3 | 157.5
3388.1 | 3167.1 | -6.7 | 0 | 0 | 153.5 | 148.4 | 136.2 | 137.4 | 162 | 30.5 | 20.5 | 48.8 | 3.3 | 254.6 | 4.3 | 431.4 | 432.6 | 130.2 | 53.4 | 526.5 | 526.9 | 88.5 | 65.2 | 213.3 | 405.3 | 192.3 | 149.4 | 308.4 | 147 | 127.8 | 488.1 | 236.6 | 168 | 148.4 | 142.5 | 155.7 | 157.9 | 141.3 | 150.2 | 157.4
3389.1 | 3168.1 | -6.7 | 0 | 0 | 153.4 | 148.2 | 136.2 | 137.3 | 162 | 30.6 | 20.5 | 48.7 | 3.3 | 252.9 | 4.3 | 431.4 | 432.6 | 130.3 | 53.3 | 526.4 | 527.5 | 88.8 | 65.3 | 213.2 | 405.2 | 191.8 | 149.4 | 308.1 | 146.9 | 128 | 487.6 | 236.5 | 168 | 148.2 | 142.4 | 155.6 | 157.9 | 141.2 | 150.1 | 157.4
3390.1 | 3169.1 | -6.7 | 0 | 0 | 153.4 | 148 | 136.1 | 137.1 | 161.8 | 30.6 | 20.5 | 48.7 | 3.4 | 253.4 | 4.2 | 431.4 | 432.5 | 128.8 | 53.3 | 526.4 | 528.1 | 89.7 | 65.1 | 213 | 405 | 191.8 | 149.5 | 307.9 | 146.9 | 127.8 | 487.1 | 236.2 | 167.9 | 148.1 | 142.3 | 155.5 | 157.8 | 141.1 | 149.9 | 157.3
3391.1 | 3170.1 | -6.7 | 0 | 0 | 153.1 | 148 | 136 | 137.1 | 161.5 | 30.6 | 20.5 | 48.7 | 3.1 | 253.2 | 4 | 431.3 | 432.5 | 127.6 | 53.2 | 526.4 | 528.4 | 90.6 | 65.1 | 212.9 | 404.8 | 191.1 | 149.4 | 307.7 | 146.7 | 128.2 | 486.7 | 235.9 | 167.8 | 148 | 142.2 | 155.4 | 157.7 | 141 | 149.8 | 157.2
3392.1 | 3171.1 | -6.7 | 0 | 0 | 152.8 | 147.9 | 135.8 | 137 | 161.2 | 30.6 | 20.5 | 48.8 | 2.8 | 253.4 | 3.9 | 431.3 | 432.5 | 126.8 | 53.3 | 526.3 | 529.1 | 91.2 | 65 | 213 | 404.7 | 190.4 | 149.5 | 307.4 | 146.5 | 128.1 | 486.2 | 235.9 | 167.7 | 147.9 | 142.1 | 155.3 | 157.6 | 140.9 | 149.7 | 157.1
3393.1 | 3172.1 | -6.7 | 0 | 0 | 152.7 | 147.9 | 135.6 | 136.8 | 161 | 30.5 | 20.5 | 48.7 | 3.3 | 253.2 | 3.9 | 431.3 | 432.4 | 126 | 53.4 | 526.3 | 529.5 | 90.8 | 65.1 | 212.9 | 404.5 | 189.5 | 149.4 | 307.2 | 146.6 | 128.1 | 485.7 | 236 | 167.6 | 147.9 | 142 | 155.2 | 157.5 | 140.8 | 149.6 | 157
3394.1 | 3173.1 | -6.7 | 0 | 0 | 152.7 | 147.8 | 135.5 | 136.6 | 160.9 | 30.4 | 20.5 | 48.7 | 3.6 | 251.3 | 3.8 | 431.3 | 432.3 | 126 | 53.6 | 526.2 | 529.8 | 90.3 | 65.2 | 212.9 | 404.3 | 188.4 | 149.3 | 306.9 | 147 | 128.2 | 485.2 | 236.1 | 167.5 | 147.8 | 142 | 155.1 | 157.4 | 140.7 | 149.5 | 156.9
3395.1 | 3174.1 | -6.7 | 0 | 0 | 152.7 | 147.6 | 135.4 | 136.5 | 160.6 | 30.4 | 20.5 | 48.7 | 3.1 | 250.2 | 3.6 | 431.3 | 432.3 | 125.9 | 53.6 | 526.2 | 529.8 | 89.9 | 65.3 | 212.9 | 404.2 | 187.3 | 149.3 | 306.6 | 147.2 | 128.1 | 484.7 | 236 | 167.4 | 147.8 | 141.9 | 155 | 157.2 | 140.6 | 149.4 | 156.8
3396.1 | 3175.1 | -6.7 | 0 | 0 | 152.6 | 147.6 | 135.3 | 136.5 | 160.5 | 30.4 | 20.5 | 48.6 | 3.3 | 252.1 | 3.2 | 431.2 | 432.4 | 126.5 | 53.6 | 526.2 | 529.6 | 89.4 | 65.2 | 212.9 | 404 | 187.1 | 149.4 | 306.4 | 147.3 | 127.9 | 484.1 | 235.6 | 167.2 | 147.7 | 141.8 | 154.9 | 157.1 | 140.6 | 149.3 | 156.7
3397.1 | 3176.1 | -6.7 | 0 | 0 | 152.6 | 147.5 | 135.3 | 136.4 | 160.4 | 30.4 | 20.5 | 48.6 | 3.2 | 262.2 | 3 | 431.2 | 432.3 | 127 | 53.7 | 526.1 | 529.5 | 89.2 | 65.1 | 213 | 403.8 | 186.6 | 149.3 | 306.1 | 148 | 127.8 | 483.6 | 235.1 | 167.1 | 147.7 | 141.7 | 154.8 | 157 | 140.5 | 149.2 | 156.6
3398.1 | 3177.1 | -6.7 | 0 | 0 | 152.6 | 147.3 | 135.2 | 136.4 | 160.4 | 30.4 | 20.5 | 48.6 | 3.2 | 266.4 | 3 | 431.2 | 432.3 | 127.6 | 53.8 | 526.1 | 529.4 | 89 | 65.2 | 212.9 | 403.6 | 187.3 | 149 | 305.9 | 148 | 127.4 | 483.1 | 235.1 | 167 | 147.6 | 141.6 | 154.7 | 156.9 | 140.4 | 149.1 | 156.5
3399.1 | 3178.1 | -6.7 | 0 | 0 | 152.5 | 147.2 | 135.2 | 136.3 | 160 | 30.4 | 20.5 | 48.5 | 3.1 | 265.4 | 3 | 431.1 | 432.2 | 128.1 | 53.8 | 526.1 | 529.1 | 90.4 | 65.3 | 212.9 | 403.5 | 187.8 | 148.9 | 305.6 | 148 | 127.4 | 482.5 | 234.8 | 166.9 | 147.6 | 141.5 | 154.6 | 156.8 | 140.3 | 149.1 | 156.4
3400.1 | 3179.1 | -6.7 | 0 | 0 | 152.5 | 147.2 | 135.1 | 136.2 | 159.7 | 30.5 | 20.5 | 48.5 | 3 | 263.4 | 2.9 | 431.1 | 432.1 | 128.8 | 53.9 | 526.1 | 528.9 | 90.6 | 65.6 | 212.9 | 403.3 | 186.9 | 148.7 | 305.3 | 147.9 | 127.5 | 482.1 | 234.4 | 166.8 | 147.5 | 141.4 | 154.5 | 156.7 | 140.2 | 149 | 156.3
3401.1 | 3180.1 | -6.8 | 0 | 0 | 152.3 | 147.2 | 135.1 | 136.1 | 159.2 | 30.5 | 20.5 | 48.5 | 3 | 253.7 | 2.9 | 431.1 | 432.1 | 128.8 | 53.9 | 526.1 | 528.8 | 90.7 | 65.9 | 212.8 | 403.1 | 186.7 | 148.5 | 305.1 | 147.9 | 127.2 | 481.6 | 234.1 | 166.7 | 147.3 | 141.3 | 154.4 | 156.6 | 140.1 | 148.9 | 156.2
3402.1 | 3181.1 | -6.8 | 0 | 0 | 152.2 | 147.2 | 135 | 136.1 | 159 | 30.5 | 20.5 | 48.5 | 3.1 | 252 | 2.8 | 431.1 | 432.1 | 129 | 53.9 | 526.1 | 528.5 | 91.1 | 66.2 | 212.8 | 403 | 187.3 | 148.4 | 304.8 | 147.6 | 127.1 | 481.1 | 234 | 166.6 | 147.2 | 141.2 | 154.3 | 156.4 | 139.9 | 148.8 | 156.1
3403.1 | 3182.1 | -6.8 | 0 | 0 | 152.1 | 147.1 | 135 | 136 | 158.8 | 30.5 | 20.5 | 48.5 | 3 | 253.7 | 2.9 | 431.1 | 432.1 | 129.3 | 54 | 526 | 528.2 | 91.4 | 66.4 | 212.7 | 402.8 | 186.9 | 148.4 | 304.5 | 147.5 | 126.8 | 480.6 | 233.6 | 166.5 | 147 | 141.1 | 154.3 | 156.3 | 139.8 | 148.7 | 156
3404.1 | 3183.1 | -6.7 | 0 | 0 | 152 | 146.9 | 134.9 | 135.9 | 158.7 | 30.5 | 20.5 | 48.4 | 2.9 | 258.2 | 3.1 | 431 | 432.1 | 130.1 | 54.1 | 526 | 527.9 | 91.2 | 66.4 | 212.8 | 402.6 | 187.1 | 148.2 | 304.2 | 147.4 | 126.6 | 480.2 | 233.2 | 166.4 | 146.9 | 141 | 154.2 | 156.2 | 139.7 | 148.6 | 156
3405.1 | 3184.1 | -6.7 | 0 | 0 | 152 | 146.7 | 134.9 | 135.8 | 158.6 | 30.4 | 20.5 | 48.4 | 3.1 | 268.6 | 3.5 | 431 | 432 | 130.4 | 54.3 | 526 | 527.4 | 91.4 | 66.5 | 212.8 | 402.4 | 186.6 | 147.9 | 304 | 147.2 | 126.2 | 479.7 | 233 | 166.3 | 146.8 | 140.9 | 154.1 | 156.2 | 139.6 | 148.5 | 155.9
3406.1 | 3185.1 | -6.7 | 0 | 0 | 152 | 146.5 | 134.8 | 135.7 | 158.6 | 30.4 | 20.5 | 48.4 | 3.4 | 268.4 | 3.7 | 431 | 431.9 | 130.8 | 54.4 | 526 | 527 | 92.1 | 66.7 | 212.7 | 402.2 | 186.3 | 147.8 | 303.7 | 147 | 126.2 | 479.3 | 232.9 | 166.2 | 146.8 | 140.7 | 154 | 156.1 | 139.6 | 148.4 | 155.8
3407.1 | 3186.1 | -6.7 | 0 | 0 | 152 | 146.4 | 134.8 | 135.6 | 158.8 | 30.4 | 20.5 | 48.4 | 3.1 | 265.8 | 3.8 | 431 | 431.9 | 129.4 | 54.4 | 526 | 527 | 92.2 | 66.7 | 212.7 | 402 | 186.5 | 147.5 | 303.4 | 146.9 | 126.1 | 478.8 | 232.7 | 166.1 | 146.6 | 140.6 | 153.9 | 156 | 139.5 | 148.3 | 155.7
3408.1 | 3187.1 | -6.7 | 0 | 0 | 151.9 | 146.3 | 134.7 | 135.5 | 158.9 | 30.4 | 20.5 | 48.3 | 3.2 | 263.2 | 3.9 | 430.9 | 431.9 | 129.1 | 54.4 | 526 | 527.1 | 92.3 | 66.8 | 212.8 | 401.9 | 186.2 | 147.3 | 303.2 | 146.7 | 126.3 | 478.4 | 232.6 | 166 | 146.5 | 140.6 | 153.8 | 155.9 | 139.4 | 148.2 | 155.6
3409.1 | 3188.1 | -6.7 | 0 | 0 | 151.8 | 146.2 | 134.6 | 135.4 | 158.7 | 30.4 | 20.5 | 48.3 | 3.4 | 262.3 | 3.9 | 430.9 | 431.8 | 128.2 | 54.3 | 526 | 527 | 92.2 | 66.8 | 212.7 | 401.7 | 186.5 | 147.2 | 302.9 | 146.6 | 126.3 | 478 | 232.4 | 165.9 | 146.5 | 140.4 | 153.7 | 155.8 | 139.3 | 148.1 | 155.5
3410.1 | 3189.1 | -6.7 | 0 | 0 | 151.6 | 146 | 134.5 | 135.3 | 158.4 | 30.4 | 20.5 | 48.3 | 3.4 | 260 | 3.8 | 430.9 | 431.8 | 127.1 | 54.2 | 525.9 | 527 | 92.5 | 66.9 | 212.8 | 401.5 | 186 | 147.3 | 302.7 | 146.4 | 126.3 | 477.5 | 232.4 | 165.8 | 146.4 | 140.4 | 153.6 | 155.7 | 139.1 | 148 | 155.4
3411.1 | 3190.1 | -6.7 | 0 | 0 | 151.1 | 145.7 | 134.3 | 135.3 | 158.1 | 30.4 | 20.5 | 48.3 | 3.4 | 262.3 | 3.7 | 430.9 | 431.8 | 125.9 | 54.2 | 525.8 | 527.1 | 92.4 | 66.9 | 212.7 | 401.3 | 185.4 | 147.4 | 302.4 | 146 | 126.1 | 477 | 232.3 | 165.7 | 146.3 | 140.2 | 153.5 | 155.7 | 139 | 147.9 | 155.3
3412.1 | 3191.1 | -6.7 | 0 | 0 | 150.9 | 145.5 | 134.2 | 135.2 | 158 | 30.4 | 20.5 | 48.2 | 3.5 | 263.9 | 3.5 | 430.8 | 431.8 | 125.4 | 54 | 525.8 | 527.2 | 92.2 | 66.8 | 212.6 | 401.1 | 185.3 | 147.4 | 302.2 | 145.7 | 125.8 | 476.5 | 232.1 | 165.6 | 146.2 | 140.1 | 153.4 | 155.6 | 138.9 | 147.8 | 155.2
3413.1 | 3192.1 | -6.7 | 0 | 0 | 150.8 | 145.4 | 134.1 | 135.2 | 158 | 30.4 | 20.5 | 48.2 | 3.6 | 275.1 | 3.2 | 430.8 | 431.7 | 125.1 | 53.8 | 525.7 | 527.2 | 92.2 | 66.7 | 212.5 | 401 | 185.3 | 147.3 | 302 | 145.4 | 125.8 | 476 | 231.8 | 165.5 | 146.2 | 140 | 153.3 | 155.5 | 138.8 | 147.7 | 155.1
3414.1 | 3193.1 | -6.7 | 0 | 0 | 150.6 | 145.3 | 134.1 | 135.2 | 158 | 30.4 | 20.5 | 48.2 | 3.3 | 288.2 | 3.1 | 430.8 | 431.7 | 124.8 | 53.7 | 525.6 | 527.3 | 91.6 | 66.7 | 212.4 | 400.8 | 184.9 | 147.4 | 301.7 | 145.3 | 125.5 | 475.5 | 231.6 | 165.4 | 146.1 | 140 | 153.2 | 155.4 | 138.7 | 147.6 | 155
3415.1 | 3194.1 | -6.4 | 0 | 0 | 150.5 | 145.1 | 134.1 | 135.1 | 157.7 | 30.4 | 20.5 | 48.2 | 3.2 | 286.7 | 3 | 430.8 | 431.7 | 124.4 | 53.6 | 525.6 | 527.4 | 91.2 | 66.5 | 212.3 | 400.6 | 184.7 | 147.4 | 301.5 | 145.3 | 125.3 | 474.9 | 231.2 | 165.3 | 146 | 139.9 | 153.1 | 155.3 | 138.6 | 147.5 | 154.9
3416.1 | 3195.1 | -6.1 | 0 | 0 | 150.3 | 145 | 134 | 134.9 | 157.6 | 30.3 | 20.5 | 48.3 | 3.3 | 283.2 | 2.9 | 430.8 | 431.6 | 124.4 | 53.4 | 525.6 | 527.3 | 90.4 | 66.3 | 212.2 | 400.5 | 185.1 | 147.6 | 301.3 | 145.1 | 125.1 | 474.4 | 230.8 | 165.1 | 145.8 | 139.8 | 153.1 | 155.2 | 138.4 | 147.4 | 154.8
3417.1 | 3196.1 | -6.3 | 0 | 0 | 150.1 | 144.9 | 133.9 | 134.7 | 157.7 | 30.3 | 20.5 | 48.3 | 3.5 | 283 | 3 | 430.7 | 431.6 | 124.4 | 53.3 | 525.6 | 527 | 89.8 | 66.2 | 212.1 | 400.3 | 185.6 | 147.6 | 301 | 145.1 | 124.9 | 473.9 | 230.5 | 165 | 145.7 | 139.7 | 153 | 155.1 | 138.3 | 147.3 | 154.7
3418.1 | 3197.1 | -6.6 | 0 | 0 | 150.1 | 144.8 | 133.8 | 134.5 | 157.8 | 30.3 | 20.5 | 48.3 | 3.5 | 282.1 | 3 | 430.7 | 431.5 | 124.1 | 53.2 | 525.5 | 526.9 | 89.1 | 66.1 | 212 | 400.1 | 185.7 | 147.5 | 300.8 | 144.9 | 124.7 | 473.4 | 230.3 | 164.9 | 145.6 | 139.6 | 152.9 | 155.1 | 138.2 | 147.2 | 154.6
3419.1 | 3198.1 | -6.6 | 0 | 0 | 150.1 | 144.9 | 133.7 | 134.4 | 157.8 | 30.3 | 20.5 | 48.3 | 3.3 | 278.6 | 2.9 | 430.7 | 431.5 | 123.6 | 53.1 | 525.5 | 526.8 | 88.5 | 65.9 | 211.8 | 399.9 | 185.4 | 147.4 | 300.5 | 144.9 | 124.3 | 472.9 | 230.2 | 164.8 | 145.5 | 139.5 | 152.8 | 155 | 138.1 | 147.1 | 154.5
3420.1 | 3199.1 | -6.4 | 0 | 0 | 150 | 144.9 | 133.6 | 134.3 | 157.8 | 30.3 | 20.5 | 48.3 | 3.4 | 267.2 | 3.2 | 430.7 | 431.5 | 123.7 | 53.1 | 525.4 | 526.8 | 87.9 | 65.8 | 211.7 | 399.7 | 185.2 | 147.4 | 300.3 | 145.6 | 124.5 | 472.4 | 230.1 | 164.7 | 145.4 | 139.3 | 152.7 | 154.9 | 138.1 | 147 | 154.4
3421.1 | 3200.1 | -6.4 | 0 | 0 | 150 | 144.8 | 133.6 | 134.2 | 157.6 | 30.2 | 20.5 | 48.3 | 3.5 | 262.3 | 3.4 | 430.6 | 431.4 | 122.6 | 52.9 | 525.3 | 526.9 | 88 | 65.8 | 211.7 | 399.5 | 185.8 | 147.4 | 300.1 | 145.5 | 125.2 | 471.9 | 229.8 | 164.6 | 145.3 | 139.3 | 152.7 | 154.7 | 138 | 146.9 | 154.4
3422.1 | 3201.1 | -6.6 | 0 | 0 | 150 | 144.8 | 133.4 | 134.1 | 157.6 | 30.2 | 20.5 | 48.2 | 3.7 | 262.4 | 3.6 | 430.6 | 431.4 | 122.4 | 52.7 | 525.3 | 527.1 | 88.2 | 65.7 | 211.6 | 399.4 | 185.9 | 147.4 | 299.9 | 145.4 | 125.5 | 471.3 | 230 | 164.6 | 145.2 | 139.2 | 152.5 | 154.6 | 137.9 | 146.8 | 154.3
3423.1 | 3202.1 | -6.4 | 0 | 0 | 149.9 | 144.8 | 133.2 | 134.1 | 157.4 | 30.2 | 20.5 | 48.1 | 3.2 | 262.4 | 3.5 | 430.6 | 431.3 | 121.5 | 52.6 | 525.2 | 527.1 | 88.4 | 65.7 | 211.6 | 399.2 | 186.2 | 147.2 | 299.7 | 145.3 | 125.4 | 470.8 | 230.1 | 164.5 | 145.1 | 139.1 | 152.4 | 154.5 | 137.8 | 146.7 | 154.2
3424.1 | 3203.1 | -5.8 | 0 | 0 | 149.7 | 144.8 | 133 | 134.1 | 157.6 | 30.2 | 20.5 | 48.1 | 3 | 262.1 | 3.5 | 430.6 | 431.4 | 120.9 | 52.5 | 525.2 | 527.2 | 89.2 | 65.7 | 211.7 | 399.1 | 186.8 | 147.1 | 299.5 | 145.1 | 125.6 | 470.2 | 230.1 | 164.4 | 145.1 | 139 | 152.3 | 154.4 | 137.7 | 146.6 | 154.1
3425.1 | 3204.1 | -5.3 | 0 | 0 | 149.6 | 144.8 | 132.9 | 134 | 157.7 | 30.2 | 20.5 | 48.1 | 3.2 | 264.9 | 3.5 | 430.5 | 431.4 | 120.9 | 52.4 | 525.1 | 527.1 | 89 | 65.6 | 211.7 | 398.9 | 187.3 | 146.9 | 299.3 | 144.6 | 125.7 | 469.7 | 230.1 | 164.3 | 145.1 | 138.9 | 152.2 | 154.3 | 137.7 | 146.5 | 154
3426.1 | 3205.1 | -5.7 | 0 | 0 | 149.6 | 144.7 | 132.8 | 133.9 | 157.7 | 30.1 | 20.5 | 48.1 | 3.1 | 264.9 | 3.5 | 430.5 | 431.3 | 122.1 | 52.3 | 525.1 | 527 | 89.7 | 65.5 | 211.8 | 398.8 | 186.7 | 146.6 | 299.1 | 144.1 | 125 | 469.1 | 230.1 | 164.2 | 145 | 138.7 | 152.2 | 154.2 | 137.6 | 146.4 | 153.9
3427.1 | 3206.1 | -6 | 0 | 0 | 149.6 | 144.7 | 132.7 | 133.8 | 157.3 | 30.1 | 20.5 | 48.1 | 3.1 | 262.9 | 3.5 | 430.5 | 431.3 | 121.6 | 52.2 | 525.1 | 527.1 | 90.1 | 65.3 | 211.6 | 398.6 | 186.3 | 146.5 | 298.9 | 144.3 | 125.2 | 468.5 | 230 | 164 | 145 | 138.6 | 152.1 | 154.1 | 137.5 | 146.3 | 153.8
3428.1 | 3207.1 | -6.3 | 0 | 0 | 149.5 | 144.6 | 132.6 | 133.7 | 156.8 | 30.1 | 20.5 | 48.1 | 3.3 | 261.1 | 3.3 | 430.5 | 431.2 | 120.9 | 52.2 | 525.1 | 527.5 | 90.5 | 65.1 | 211.2 | 398.4 | 185.9 | 146.4 | 298.7 | 144.2 | 125.6 | 468 | 229.8 | 163.9 | 144.8 | 138.5 | 152 | 154 | 137.4 | 146.2 | 153.7
3429.1 | 3208.1 | -6.6 | 0 | 0 | 149.4 | 144.5 | 132.5 | 133.6 | 156.5 | 30 | 20.5 | 48 | 3.5 | 256 | 3.3 | 430.4 | 431.1 | 121.3 | 52.1 | 525.2 | 527.7 | 90 | 64.8 | 210.9 | 398.2 | 185.8 | 146.5 | 298.5 | 144.1 | 125.7 | 467.4 | 229.9 | 163.8 | 144.7 | 138.4 | 151.9 | 153.9 | 137.3 | 146.1 | 153.6
3430.1 | 3209.1 | -6.7 | 0 | 0 | 149.4 | 144.4 | 132.5 | 133.5 | 156.2 | 30 | 20.6 | 48 | 3.6 | 255.6 | 3.5 | 430.4 | 431.2 | 122 | 52.1 | 525.3 | 527.7 | 89.3 | 64.7 | 210.7 | 398.1 | 185.7 | 146.4 | 298.2 | 144.1 | 125.2 | 466.9 | 230.1 | 163.7 | 144.6 | 138.4 | 151.8 | 153.8 | 137.2 | 146 | 153.5
3431.1 | 3210.1 | -6.7 | 0 | 0 | 149.3 | 144.3 | 132.5 | 133.5 | 156.2 | 30 | 20.5 | 48 | 3.1 | 255.8 | 3.5 | 430.4 | 431.1 | 122.5 | 52.2 | 525.4 | 527.7 | 89 | 64.6 | 210.7 | 397.9 | 185.3 | 146.4 | 298 | 143.9 | 124.6 | 466.3 | 229.8 | 163.7 | 144.5 | 138.3 | 151.8 | 153.7 | 137.2 | 145.9 | 153.4
3432.1 | 3211.1 | -6.7 | 0 | 0 | 149.3 | 144.2 | 132.4 | 133.4 | 156.2 | 30 | 20.5 | 48 | 3.4 | 254.9 | 3.3 | 430.4 | 431.1 | 122.1 | 52.1 | 525.5 | 527.6 | 88.8 | 64.7 | 210.8 | 397.7 | 185 | 145.9 | 297.7 | 143.8 | 124.1 | 465.8 | 229.7 | 163.6 | 144.3 | 138.2 | 151.7 | 153.6 | 137.1 | 145.8 | 153.3
3433.1 | 3212.1 | -6.1 | 0 | 0 | 148.8 | 144.1 | 132.3 | 133.3 | 156.2 | 30 | 20.5 | 48 | 3.6 | 254.5 | 3.1 | 430.3 | 431.1 | 122 | 52.1 | 525.7 | 527.3 | 88.4 | 64.6 | 210.8 | 397.5 | 185.5 | 145.4 | 297.5 | 143.5 | 123.6 | 465.2 | 229.4 | 163.5 | 144.3 | 138.1 | 151.6 | 153.5 | 137 | 145.7 | 153.2
3434.1 | 3213.1 | -5.6 | 0 | 0 | 148.3 | 143.9 | 132.2 | 133.2 | 156.2 | 30 | 20.5 | 48 | 3.5 | 260.2 | 3.1 | 430.3 | 431 | 123.7 | 52.2 | 525.8 | 527 | 87.6 | 64.7 | 210.9 | 397.4 | 185.3 | 145.1 | 297.2 | 143.2 | 123 | 464.7 | 229.1 | 163.4 | 144.2 | 138 | 151.5 | 153.3 | 136.9 | 145.6 | 153.1
3435.1 | 3214.1 | -5.7 | 0 | 0 | 148 | 143.7 | 132.2 | 133.1 | 156 | 30 | 20.6 | 48 | 3.5 | 278.3 | 3.2 | 430.3 | 431 | 125 | 52.2 | 525.9 | 526.9 | 87 | 64.7 | 210.8 | 397.2 | 185.6 | 144.6 | 297 | 143.1 | 122.7 | 464.2 | 228.8 | 163.3 | 144 | 137.9 | 151.4 | 153.2 | 136.8 | 145.5 | 153.1
3436.1 | 3215.1 | -5.9 | 0 | 0 | 147.9 | 143.5 | 132.1 | 133 | 155.8 | 30 | 20.6 | 48 | 3.8 | 278.7 | 3.4 | 430.3 | 431 | 124.9 | 52.2 | 526 | 526.7 | 86.5 | 64.8 | 210.7 | 397 | 185.6 | 144.3 | 296.7 | 143 | 122.8 | 463.6 | 228.5 | 163.2 | 143.9 | 137.7 | 151.3 | 153.1 | 136.7 | 145.5 | 153
3437.1 | 3216.1 | -6.1 | 0 | 0 | 147.8 | 143.3 | 131.9 | 132.9 | 155.7 | 30 | 20.6 | 48 | 3.6 | 278.1 | 3.4 | 430.2 | 430.9 | 125.8 | 52.2 | 526.1 | 526.6 | 86.6 | 64.9 | 210.8 | 396.8 | 186.1 | 143.9 | 296.4 | 142.8 | 122.4 | 463.1 | 228.4 | 163.1 | 143.8 | 137.6 | 151.2 | 153 | 136.6 | 145.4 | 152.9
3438.1 | 3217.1 | -6.3 | 0 | 0 | 147.8 | 143.2 | 131.6 | 132.8 | 155.6 | 30 | 20.6 | 48 | 3.3 | 278.1 | 3.4 | 430.2 | 430.9 | 125.6 | 52.3 | 526.2 | 526.3 | 85.9 | 64.8 | 210.6 | 396.7 | 186.3 | 143.2 | 296.2 | 142.7 | 121.9 | 462.6 | 228 | 163 | 143.6 | 137.6 | 151.1 | 152.9 | 136.5 | 145.3 | 152.8
3439.1 | 3218.1 | -6.6 | 0 | 0 | 147.8 | 143 | 131.4 | 132.6 | 155.6 | 29.9 | 20.6 | 47.9 | 3.4 | 278.5 | 3.4 | 430.2 | 430.9 | 126.1 | 52.3 | 526.2 | 526.1 | 85.8 | 65 | 210.4 | 396.5 | 186.1 | 142.8 | 296 | 142.5 | 121.6 | 462.1 | 227.6 | 163 | 143.5 | 137.5 | 151 | 152.8 | 136.4 | 145.2 | 152.7
3440.1 | 3219.1 | -6.7 | 0 | 0 | 147.9 | 142.9 | 131.1 | 132.2 | 155.4 | 29.9 | 20.6 | 47.9 | 3.2 | 278.9 | 3.4 | 430.2 | 430.9 | 125.5 | 52.2 | 526.3 | 526.3 | 86.5 | 65.3 | 210.3 | 396.3 | 186 | 142.7 | 295.7 | 142 | 121.4 | 461.6 | 227.5 | 162.9 | 143.4 | 137.4 | 150.9 | 152.7 | 136.3 | 145.1 | 152.6
3441.1 | 3220.1 | -6.8 | 0 | 0 | 147.8 | 142.7 | 130.9 | 132 | 155.3 | 29.9 | 20.6 | 47.9 | 3.2 | 276.3 | 3.4 | 430.1 | 430.7 | 125.2 | 52.3 | 526.2 | 526.5 | 86.9 | 65.2 | 210.4 | 396.1 | 185.9 | 142.8 | 295.5 | 141.6 | 121.2 | 461.2 | 227.5 | 162.8 | 143.3 | 137.4 | 150.8 | 152.6 | 136.2 | 145 | 152.5
3442.1 | 3221.1 | -6.7 | 0 | 0 | 147.7 | 142.6 | 130.7 | 132 | 155.2 | 29.9 | 20.6 | 47.8 | 3.1 | 265.7 | 3.3 | 430.1 | 430.7 | 124.3 | 52.3 | 526.2 | 526.4 | 87.4 | 65.2 | 210.3 | 395.9 | 185.1 | 142.8 | 295.2 | 141.4 | 121.1 | 460.7 | 227.5 | 162.7 | 143.2 | 137.3 | 150.7 | 152.4 | 136.1 | 144.9 | 152.4
3443.1 | 3222.1 | -6.6 | 0 | 0 | 147.8 | 142.4 | 130.5 | 132 | 155.2 | 29.9 | 20.6 | 47.8 | 3 | 259.7 | 3.2 | 430.1 | 430.7 | 123.5 | 52.2 | 526.1 | 526.2 | 87.8 | 65.2 | 210.3 | 395.7 | 184.6 | 142.7 | 295 | 141 | 121 | 460.2 | 227.4 | 162.6 | 143.1 | 137.2 | 150.6 | 152.3 | 136.1 | 144.8 | 152.3
3444.1 | 3223.1 | -6.6 | 0 | 0 | 147.8 | 142.3 | 130.4 | 131.9 | 155.2 | 29.9 | 20.6 | 47.8 | 2.7 | 252.6 | 3 | 430.1 | 430.6 | 124.1 | 52.2 | 526.1 | 525.9 | 87.4 | 65.3 | 210.3 | 395.5 | 183.8 | 142.6 | 294.7 | 140.8 | 120.8 | 459.6 | 227.2 | 162.5 | 143 | 137 | 150.5 | 152.2 | 136 | 144.8 | 152.2
3445.1 | 3224.1 | -6.7 | 0 | 0 | 147.7 | 142.2 | 130.4 | 131.9 | 155.2 | 29.8 | 20.6 | 47.8 | 2.7 | 251.9 | 2.8 | 430 | 430.6 | 125 | 52.2 | 526 | 525.7 | 86.8 | 65.3 | 210.3 | 395.3 | 183.4 | 142.8 | 294.4 | 141 | 120.7 | 459.1 | 226.9 | 162.4 | 143 | 136.9 | 150.4 | 152.1 | 135.9 | 144.7 | 152.1
3446.1 | 3225.1 | -6.5 | 0 | 0 | 147.6 | 142.2 | 130.4 | 131.8 | 155.1 | 29.8 | 20.6 | 47.8 | 2.8 | 251.9 | 2.7 | 430 | 430.6 | 125.2 | 52 | 526 | 525.4 | 86.4 | 65.3 | 210.4 | 395.2 | 183.3 | 142.9 | 294.2 | 141.2 | 120.2 | 458.5 | 226.8 | 162.3 | 142.9 | 136.8 | 150.3 | 152 | 135.8 | 144.6 | 152
3447.1 | 3226.1 | -6.2 | 0 | 0 | 147.6 | 142.1 | 130.2 | 131.8 | 154.9 | 29.8 | 20.6 | 47.8 | 2.8 | 251.9 | 2.7 | 430 | 430.5 | 125.6 | 51.8 | 526 | 525.1 | 85.8 | 65.2 | 210.5 | 395 | 183.6 | 142.9 | 293.9 | 141.3 | 120.4 | 458 | 226.6 | 162.2 | 142.8 | 136.7 | 150.2 | 151.9 | 135.7 | 144.5 | 151.9
3448.1 | 3227.1 | -6.4 | 0 | 0 | 147.4 | 142 | 130.2 | 131.6 | 154.9 | 29.8 | 20.6 | 47.8 | 3 | 252.1 | 3 | 429.9 | 430.5 | 125.3 | 51.7 | 526.1 | 524.9 | 86.5 | 65.1 | 210.4 | 394.8 | 183.6 | 142.8 | 293.7 | 141.2 | 120.2 | 457.4 | 226.2 | 162.1 | 142.7 | 136.6 | 150.1 | 151.8 | 135.6 | 144.4 | 151.9
3449.1 | 3228.1 | -6.5 | 0 | 0 | 147.3 | 141.9 | 130.2 | 131.4 | 154.9 | 29.8 | 20.6 | 47.8 | 3.1 | 248.4 | 3.2 | 429.9 | 430.4 | 124.4 | 51.8 | 526 | 524.7 | 87.6 | 65 | 210.4 | 394.6 | 183.9 | 142.9 | 293.4 | 141.2 | 120.5 | 456.8 | 226.1 | 162 | 142.6 | 136.5 | 150 | 151.7 | 135.5 | 144.3 | 151.8
3450.1 | 3229.1 | -6.7 | 0 | 0 | 147.3 | 141.9 | 130.2 | 131.3 | 154.9 | 29.8 | 20.6 | 47.7 | 3.1 | 246.4 | 3.1 | 429.9 | 430.4 | 123.9 | 51.7 | 526 | 524.6 | 87.1 | 65 | 210.3 | 394.4 | 183.8 | 143 | 293.2 | 140.7 | 120.4 | 456.2 | 226 | 161.9 | 142.5 | 136.5 | 149.9 | 151.5 | 135.5 | 144.2 | 151.7
3451.1 | 3230.1 | -6.7 | 0 | 0 | 147.2 | 141.9 | 130 | 131.2 | 154.8 | 29.7 | 20.6 | 47.7 | 2.8 | 242.1 | 3.3 | 429.9 | 430.3 | 124.4 | 51.7 | 525.9 | 524.6 | 86.5 | 65 | 210.3 | 394.3 | 183.2 | 142.9 | 292.9 | 140.5 | 120.1 | 455.6 | 225.7 | 161.8 | 142.3 | 136.3 | 149.8 | 151.4 | 135.3 | 144.1 | 151.6
3452.1 | 3231.1 | -6.7 | 0 | 0 | 147.1 | 141.9 | 129.9 | 131.1 | 154.5 | 29.7 | 20.6 | 47.7 | 3.2 | 239.3 | 3.4 | 429.8 | 430.3 | 123.5 | 51.5 | 525.9 | 524.7 | 85.9 | 64.9 | 210.3 | 394.1 | 183 | 142.8 | 292.6 | 140.4 | 120 | 455 | 225.4 | 161.6 | 142.2 | 136.2 | 149.7 | 151.4 | 135.2 | 144 | 151.5
3453.1 | 3232.1 | -6.7 | 0 | 0 | 147.1 | 141.8 | 129.8 | 131.1 | 154.4 | 29.6 | 20.6 | 47.7 | 3 | 239.3 | 3.5 | 429.8 | 430.3 | 123 | 51.5 | 525.8 | 524.6 | 85.7 | 64.9 | 210.2 | 393.9 | 183.2 | 142.8 | 292.4 | 140 | 120.2 | 454.4 | 225.4 | 161.5 | 142.1 | 136.1 | 149.7 | 151.3 | 135.1 | 143.9 | 151.4
3454.1 | 3233.1 | -6.7 | 0 | 0 | 147 | 141.8 | 129.7 | 131.1 | 154.3 | 29.6 | 20.6 | 47.7 | 2.9 | 242.4 | 3.7 | 429.8 | 430.3 | 122.7 | 51.3 | 525.7 | 524.6 | 86 | 65 | 210.1 | 393.7 | 183.2 | 143 | 292.1 | 139.8 | 120.3 | 453.8 | 225.4 | 161.4 | 142.1 | 136 | 149.6 | 151.2 | 135 | 143.7 | 151.3
3455.1 | 3234.1 | -6.7 | 0 | 0 | 146.7 | 141.7 | 129.7 | 131.1 | 154.2 | 29.6 | 20.6 | 47.6 | 2.8 | 256.9 | 3.7 | 429.7 | 430.2 | 123.2 | 51.3 | 525.6 | 524.8 | 85.4 | 65 | 210.1 | 393.6 | 183 | 143.1 | 291.8 | 139.4 | 120.2 | 453.2 | 225.3 | 161.3 | 142 | 135.9 | 149.5 | 151.1 | 134.8 | 143.6 | 151.2
3456.1 | 3235.1 | -6.7 | 0 | 0 | 146.5 | 141.5 | 129.7 | 131 | 153.9 | 29.5 | 20.6 | 47.6 | 3 | 266.4 | 3.6 | 429.7 | 430.1 | 122.9 | 51.2 | 525.6 | 525.2 | 85 | 65 | 210 | 393.4 | 182.4 | 143.1 | 291.5 | 139.8 | 119.9 | 452.6 | 225.2 | 161.2 | 142 | 135.8 | 149.4 | 151 | 134.7 | 143.6 | 151.1
3457.1 | 3236.1 | -6.8 | 0 | 0 | 146.4 | 141.4 | 129.5 | 130.9 | 153.3 | 29.5 | 20.6 | 47.6 | 3.1 | 262.5 | 3.6 | 429.7 | 430.1 | 123.7 | 51.1 | 525.5 | 525.4 | 85.3 | 64.9 | 210 | 393.2 | 181.8 | 143 | 291.2 | 139.5 | 119.5 | 452 | 225 | 161.1 | 141.9 | 135.7 | 149.3 | 150.9 | 134.6 | 143.5 | 151
3458.1 | 3237.1 | -6.8 | 0 | 0 | 146.2 | 141.2 | 129.5 | 130.7 | 153.2 | 29.5 | 20.6 | 47.6 | 3.2 | 253.6 | 3.7 | 429.7 | 430.1 | 124.9 | 51.1 | 525.5 | 525.7 | 85.3 | 64.9 | 209.9 | 393.1 | 181.7 | 142.9 | 291 | 138.8 | 119.2 | 451.3 | 224.5 | 161 | 141.8 | 135.6 | 149.2 | 150.8 | 134.5 | 143.4 | 150.9
3459.1 | 3238.1 | -6.8 | 0 | 0 | 145.9 | 141.1 | 129.5 | 130.5 | 153.4 | 29.5 | 20.6 | 47.6 | 3.5 | 254.7 | 3.8 | 429.6 | 430.1 | 123.8 | 51.1 | 525.4 | 526 | 85.5 | 65.1 | 209.8 | 392.9 | 182.2 | 142.9 | 290.7 | 138.1 | 119.2 | 450.7 | 224 | 160.9 | 141.7 | 135.5 | 149.1 | 150.7 | 134.4 | 143.3 | 150.8
3460.1 | 3239.1 | -6.8 | 0 | 0 | 145.7 | 141 | 129.3 | 130.4 | 153.5 | 29.4 | 20.6 | 47.7 | 3.3 | 256.8 | 3.8 | 429.6 | 430 | 122.7 | 51.2 | 525.3 | 526.6 | 86.4 | 65 | 209.9 | 392.7 | 182 | 142.8 | 290.5 | 137.7 | 119.4 | 450 | 223.9 | 160.8 | 141.6 | 135.3 | 149 | 150.6 | 134.3 | 143.2 | 150.7
3461.1 | 3240.1 | -6.8 | 0 | 0 | 145.6 | 140.9 | 129.1 | 130.2 | 153.5 | 29.4 | 20.6 | 47.6 | 3.1 | 256.8 | 3.8 | 429.6 | 429.9 | 122.6 | 51.1 | 525.2 | 527.5 | 86.4 | 65 | 209.8 | 392.6 | 182.3 | 142.8 | 290.2 | 137.5 | 119.5 | 449.4 | 224.1 | 160.6 | 141.6 | 135.2 | 148.9 | 150.4 | 134.2 | 143.1 | 150.6
3462.1 | 3241.1 | -6.8 | 0 | 0 | 145.5 | 140.7 | 129 | 130.1 | 153.5 | 29.4 | 20.6 | 47.6 | 2.9 | 260.8 | 3.5 | 429.6 | 430 | 123.4 | 51.1 | 525.1 | 527.7 | 86.3 | 64.9 | 209.9 | 392.4 | 182.5 | 142.8 | 289.9 | 137.1 | 119.1 | 448.7 | 224 | 160.5 | 141.6 | 135.1 | 148.8 | 150.3 | 134.1 | 143 | 150.5
3463.1 | 3242.1 | -6.8 | 0 | 0 | 145.4 | 140.6 | 128.7 | 130 | 153.4 | 29.5 | 20.6 | 47.6 | 2.9 | 268.9 | 3.4 | 429.5 | 430 | 124.7 | 51.1 | 525.1 | 527.7 | 85.9 | 64.8 | 209.8 | 392.3 | 182.4 | 142.7 | 289.7 | 136.9 | 119 | 448 | 223.6 | 160.4 | 141.5 | 135 | 148.7 | 150.2 | 134 | 142.9 | 150.4
3464.1 | 3243.1 | -6.8 | 0 | 0 | 145.2 | 140.4 | 128.5 | 129.9 | 153.4 | 29.4 | 20.6 | 47.6 | 3.2 | 267.7 | 3.5 | 429.5 | 429.9 | 126 | 51.1 | 525 | 527.7 | 85.6 | 64.9 | 209.8 | 392.1 | 182.1 | 142.7 | 289.5 | 136.7 | 119.1 | 447.3 | 223.2 | 160.3 | 141.4 | 134.9 | 148.6 | 150.1 | 133.9 | 142.8 | 150.4
3465.1 | 3244.1 | -6.8 | 0 | 0 | 145 | 140.2 | 128.3 | 129.8 | 153.3 | 29.4 | 20.6 | 47.5 | 3 | 259.2 | 3.7 | 429.5 | 429.8 | 126.8 | 51.1 | 525 | 527.7 | 85.3 | 64.9 | 209.8 | 391.9 | 181.3 | 142.7 | 289.3 | 136.5 | 119.3 | 446.6 | 223 | 160.2 | 141.3 | 134.8 | 148.6 | 149.9 | 133.8 | 142.7 | 150.3
3466.1 | 3245.1 | -6.7 | 0 | 0 | 144.9 | 140.1 | 128.2 | 129.7 | 153.2 | 29.4 | 20.6 | 47.5 | 3.2 | 256.7 | 3.8 | 429.5 | 429.8 | 126.6 | 51.1 | 525.1 | 527.5 | 85.9 | 64.9 | 210 | 391.7 | 181 | 142.8 | 289.1 | 136.3 | 119.3 | 445.9 | 223.2 | 160.2 | 141.2 | 134.7 | 148.5 | 149.8 | 133.8 | 142.6 | 150.2
3467.1 | 3246.1 | -6.6 | 0 | 0 | 144.8 | 140 | 128.2 | 129.6 | 153.2 | 29.4 | 20.6 | 47.4 | 3.7 | 256.6 | 3.8 | 429.4 | 429.7 | 125.9 | 51.3 | 525.1 | 527 | 85.8 | 65 | 209.9 | 391.6 | 181 | 142.7 | 288.8 | 136.3 | 118.9 | 445.2 | 223.1 | 160 | 141.1 | 134.6 | 148.4 | 149.7 | 133.7 | 142.5 | 150.1
3468.1 | 3247.1 | -6.6 | 0 | 0 | 144.7 | 139.9 | 128 | 129.6 | 153.2 | 29.4 | 20.6 | 47.4 | 3.6 | 256.7 | 3.8 | 429.4 | 429.7 | 125 | 51.3 | 525.1 | 526.8 | 86.1 | 65.2 | 210 | 391.4 | 181 | 142.5 | 288.6 | 136.3 | 118.9 | 444.5 | 222.8 | 159.9 | 140.9 | 134.4 | 148.3 | 149.5 | 133.6 | 142.4 | 150
3469.1 | 3248.1 | -6.7 | 0 | 0 | 144.6 | 139.9 | 127.8 | 129.4 | 153.2 | 29.4 | 20.6 | 47.3 | 3.4 | 256.3 | 3.9 | 429.4 | 429.6 | 125.1 | 51.4 | 525.2 | 526.8 | 85.6 | 65.3 | 210 | 391.3 | 181.2 | 142.3 | 288.3 | 136.6 | 118.9 | 443.8 | 222.5 | 159.8 | 140.8 | 134.3 | 148.3 | 149.4 | 133.5 | 142.3 | 149.9
3470.1 | 3249.1 | -6.5 | 0 | 0 | 144.6 | 139.8 | 127.6 | 129.4 | 153.1 | 29.4 | 20.6 | 47.3 | 3.5 | 255.9 | 4 | 429.3 | 429.7 | 126.2 | 51.4 | 525.2 | 526.7 | 85.2 | 65.2 | 210 | 391.1 | 181.4 | 141.9 | 288 | 136.6 | 118.8 | 443.1 | 222.5 | 159.6 | 140.7 | 134.2 | 148.1 | 149.2 | 133.4 | 142.2 | 149.8
3471.1 | 3250.1 | -6.3 | 0 | 0 | 144.5 | 139.6 | 127.5 | 129.3 | 152.9 | 29.4 | 20.6 | 47.3 | 3.5 | 257.9 | 4.1 | 429.3 | 429.7 | 126.4 | 51.4 | 525.3 | 526.6 | 84.6 | 65.1 | 209.9 | 390.9 | 180.3 | 141.6 | 287.7 | 136.4 | 118.5 | 442.3 | 222.4 | 159.6 | 140.7 | 134 | 148 | 149.1 | 133.3 | 142.1 | 149.7
3472.1 | 3251.1 | -6.2 | 0 | 0 | 144.4 | 139.5 | 127.4 | 129.2 | 152.8 | 29.4 | 20.6 | 47.3 | 3.5 | 263 | 4.1 | 429.3 | 429.6 | 126.8 | 51.6 | 525.4 | 526.5 | 84.1 | 65 | 209.9 | 390.8 | 180.3 | 141.5 | 287.4 | 136.4 | 118.8 | 441.6 | 222.3 | 159.5 | 140.6 | 133.9 | 148 | 149 | 133.2 | 142 | 149.6
3473.1 | 3252.1 | -6 | 0 | 0 | 144.3 | 139.3 | 127.4 | 129.1 | 152.5 | 29.4 | 20.6 | 47.2 | 3.5 | 255.6 | 3.9 | 429.3 | 429.6 | 127.3 | 51.7 | 525.5 | 526.2 | 84 | 64.7 | 210 | 390.6 | 179.8 | 141.2 | 287.2 | 136.3 | 118.5 | 440.8 | 222.1 | 159.4 | 140.5 | 133.8 | 147.9 | 148.9 | 133.1 | 141.9 | 149.5
3474.1 | 3253.1 | -6.2 | 0 | 0 | 144.3 | 139.1 | 127.3 | 129.1 | 152.1 | 29.4 | 20.6 | 47.2 | 3.5 | 237.5 | 3.5 | 429.3 | 429.5 | 127.6 | 51.7 | 525.5 | 525.8 | 84.2 | 64.8 | 210 | 390.4 | 179 | 141.1 | 286.9 | 136.4 | 118.3 | 440.1 | 221.7 | 159.3 | 140.4 | 133.7 | 147.8 | 148.7 | 133 | 141.7 | 149.4
3475.1 | 3254.1 | -6.3 | 0 | 0 | 144.3 | 139 | 127.3 | 129 | 151.9 | 29.4 | 20.6 | 47.2 | 3.2 | 236.6 | 3.4 | 429.2 | 429.4 | 127.8 | 51.8 | 525.6 | 525.5 | 84.9 | 64.7 | 210 | 390.2 | 178.2 | 140.9 | 286.6 | 136.7 | 118.3 | 439.3 | 221.3 | 159.2 | 140.2 | 133.6 | 147.7 | 148.6 | 132.9 | 141.7 | 149.3
3476.1 | 3255.1 | -6.1 | 0 | 0 | 144.1 | 138.9 | 127.1 | 128.8 | 151.8 | 29.4 | 20.6 | 47.1 | 3.2 | 250.8 | 3.7 | 429.2 | 429.4 | 128.1 | 51.9 | 525.6 | 525.2 | 84.5 | 64.7 | 209.9 | 390 | 177.2 | 140.7 | 286.4 | 136.9 | 118.2 | 438.5 | 221.2 | 159.1 | 140.2 | 133.5 | 147.6 | 148.5 | 132.8 | 141.6 | 149.2
3477.1 | 3256.1 | -6.1 | 0 | 0 | 143.9 | 138.8 | 127 | 128.7 | 151.7 | 29.4 | 20.6 | 47.1 | 3.1 | 251.8 | 3.9 | 429.2 | 429.4 | 127.2 | 52 | 525.7 | 525 | 84.1 | 64.6 | 209.9 | 389.9 | 177.2 | 140.6 | 286.1 | 136.9 | 118.3 | 437.7 | 221.1 | 159 | 140.1 | 133.5 | 147.6 | 148.4 | 132.7 | 141.6 | 149.1
3478.1 | 3257.1 | -6.4 | 0 | 0 | 143.7 | 138.7 | 126.9 | 128.5 | 151.6 | 29.5 | 20.6 | 47.1 | 3.2 | 237.6 | 3.8 | 429.2 | 429.3 | 126.4 | 52.1 | 525.7 | 524.8 | 83.8 | 64.5 | 209.9 | 389.6 | 176.4 | 140.5 | 285.8 | 137.2 | 118.3 | 436.9 | 220.9 | 158.9 | 140 | 133.4 | 147.5 | 148.3 | 132.6 | 141.5 | 149
3479.1 | 3258.1 | -6.7 | 0 | 0 | 143.7 | 138.6 | 126.9 | 128.4 | 151.5 | 29.5 | 20.6 | 47.1 | 3.1 | 232.2 | 3.5 | 429.1 | 429.3 | 125.3 | 52.1 | 525.7 | 524.7 | 83.6 | 64.3 | 209.9 | 389.5 | 175.5 | 140.4 | 285.5 | 137.2 | 117.9 | 436 | 220.9 | 158.8 | 139.8 | 133.3 | 147.4 | 148.2 | 132.5 | 141.5 | 148.9
3480.1 | 3259.1 | -6.7 | 0 | 0 | 143.7 | 138.5 | 126.8 | 128.4 | 151 | 29.6 | 20.6 | 47.1 | 3 | 234.7 | 3.2 | 429.1 | 429.3 | 125.3 | 52 | 525.8 | 524.6 | 83.6 | 64.2 | 209.7 | 389.2 | 175.6 | 140.2 | 285.3 | 137.1 | 117.6 | 435.2 | 220.8 | 158.8 | 139.8 | 133.2 | 147.3 | 148.1 | 132.3 | 141.4 | 148.9
3481.1 | 3260.1 | -6.8 | 0 | 0 | 143.6 | 138.3 | 126.6 | 128.3 | 150.6 | 29.6 | 20.6 | 47.1 | 2.9 | 240.5 | 3 | 429.1 | 429.3 | 125.9 | 52 | 525.9 | 524.4 | 84 | 64.3 | 209.7 | 389.1 | 176.4 | 139.8 | 285 | 136.9 | 117.3 | 434.3 | 220.5 | 158.6 | 139.6 | 133.1 | 147.3 | 148 | 132.2 | 141.3 | 148.8
3482.1 | 3261.1 | -6.7 | 0 | 0 | 143.4 | 138.2 | 126.5 | 128.2 | 150.5 | 29.6 | 20.6 | 47.1 | 3.1 | 242.9 | 3.1 | 429.1 | 429.3 | 126.1 | 52.1 | 526 | 524.2 | 83.9 | 64.3 | 209.7 | 388.9 | 176.6 | 139.3 | 284.8 | 136.8 | 117.1 | 433.5 | 220.2 | 158.6 | 139.5 | 133 | 147.2 | 147.9 | 132.1 | 141.2 | 148.7
3483.1 | 3262.1 | -6.8 | 0 | 0 | 143.2 | 138.1 | 126.5 | 128.1 | 150.3 | 29.6 | 20.6 | 47.1 | 2.8 | 247.6 | 3.1 | 429 | 429.3 | 126.5 | 52.1 | 526 | 524.2 | 83.7 | 64.2 | 209.6 | 388.7 | 176.3 | 139 | 284.5 | 137.2 | 116.7 | 432.6 | 219.9 | 158.5 | 139.4 | 133 | 147.1 | 147.8 | 131.9 | 141.1 | 148.6
3484.1 | 3263.1 | -6.8 | 0 | 0 | 143.1 | 138 | 126.5 | 128 | 150.2 | 29.5 | 20.6 | 47.1 | 3.2 | 252.6 | 3.1 | 429 | 429.3 | 127 | 52.1 | 526 | 524.2 | 83.5 | 64.1 | 209.5 | 388.5 | 175.6 | 138.5 | 284.3 | 137.4 | 116.5 | 431.7 | 219.7 | 158.4 | 139.3 | 132.9 | 147 | 147.7 | 131.8 | 141 | 148.5
3485.1 | 3264.1 | -6.8 | 0 | 0 | 143 | 137.9 | 126.5 | 127.9 | 150 | 29.5 | 20.6 | 47.1 | 3.1 | 252.7 | 3 | 429 | 429.2 | 127.6 | 52.2 | 526.1 | 524.1 | 84.1 | 64.2 | 209.5 | 388.3 | 174.5 | 138.5 | 284 | 137.7 | 116.4 | 430.8 | 219.6 | 158.3 | 139.2 | 132.8 | 146.9 | 147.6 | 131.8 | 140.9 | 148.4
3486.1 | 3265.1 | -6.8 | 0 | 0 | 142.9 | 137.8 | 126.5 | 127.8 | 149.8 | 29.5 | 20.6 | 47.1 | 3 | 247.2 | 2.8 | 429 | 429.1 | 128.5 | 52.3 | 526.1 | 524.1 | 83.9 | 64.3 | 209.6 | 388.1 | 173.6 | 138.8 | 283.8 | 138 | 116.4 | 429.8 | 219.3 | 158.2 | 139.2 | 132.7 | 146.8 | 147.6 | 131.7 | 140.8 | 148.3
3487.1 | 3266.1 | -6.7 | 0 | 0 | 142.7 | 137.8 | 126.4 | 127.7 | 149.6 | 29.5 | 20.6 | 47.1 | 2.8 | 247.3 | 2.8 | 428.9 | 429.1 | 127.1 | 52.3 | 526.1 | 524.3 | 83.7 | 64.4 | 209.6 | 387.9 | 173.4 | 139.2 | 283.5 | 137.8 | 116.5 | 428.8 | 219.3 | 158.1 | 139.2 | 132.6 | 146.7 | 147.5 | 131.6 | 140.7 | 148.2
3488.1 | 3267.1 | -6.4 | 0 | 0 | 142.5 | 137.8 | 126.2 | 127.6 | 149.5 | 29.5 | 20.6 | 47.1 | 3 | 249.2 | 2.9 | 428.9 | 429 | 126.6 | 52.5 | 526.1 | 524.7 | 83.8 | 64.6 | 209.6 | 387.7 | 173.9 | 139.2 | 283.2 | 137.7 | 116.7 | 427.7 | 219.5 | 158 | 139.1 | 132.6 | 146.6 | 147.4 | 131.5 | 140.5 | 148.2
3489.1 | 3268.1 | -6.2 | 0 | 0 | 142.3 | 137.7 | 126.2 | 127.6 | 149.6 | 29.5 | 20.6 | 47.1 | 3.2 | 252.6 | 3 | 428.9 | 429 | 126.3 | 52.6 | 526.1 | 524.9 | 85.5 | 64.9 | 209.6 | 387.5 | 173.7 | 139 | 283 | 137.3 | 116.5 | 426.7 | 219.3 | 157.9 | 139 | 132.5 | 146.5 | 147.3 | 131.4 | 140.4 | 148.1
3490.1 | 3269.1 | -6.2 | 0 | 0 | 142.2 | 137.5 | 126.2 | 127.5 | 149.5 | 29.5 | 20.6 | 47 | 2.9 | 247.2 | 2.9 | 428.9 | 428.9 | 124.7 | 52.7 | 526 | 525.2 | 86.4 | 65.2 | 209.6 | 387.3 | 173.1 | 139.1 | 282.7 | 137.2 | 116.5 | 425.6 | 219.2 | 157.8 | 138.9 | 132.4 | 146.4 | 147.3 | 131.4 | 140.3 | 148
3491.1 | 3270.1 | -6.5 | 0 | 0 | 142.1 | 137.4 | 126.2 | 127.5 | 149.2 | 29.5 | 20.6 | 47 | 3.1 | 228.3 | 2.7 | 428.9 | 428.9 | 124 | 52.7 | 526 | 525.3 | 86.6 | 65.2 | 209.6 | 387.1 | 173.3 | 139.2 | 282.5 | 136.9 | 116.5 | 424.5 | 219.2 | 157.7 | 138.8 | 132.3 | 146.2 | 147.2 | 131.3 | 140.2 | 147.9
3492.1 | 3271.1 | -6.7 | 0 | 0 | 141.9 | 137.4 | 126.2 | 127.5 | 149.2 | 29.5 | 20.6 | 47 | 3 | 226.7 | 2.7 | 428.8 | 428.9 | 123.9 | 52.8 | 525.9 | 525.3 | 86.1 | 65.3 | 209.5 | 387 | 173 | 139.2 | 282.2 | 136.6 | 116.6 | 423.5 | 219 | 157.7 | 138.8 | 132.2 | 146.2 | 147.1 | 131.2 | 140.2 | 147.8
3493.1 | 3272.1 | -6.7 | 0 | 0 | 141.9 | 137.3 | 126.1 | 127.4 | 149.3 | 29.5 | 20.6 | 47 | 3.5 | 239.3 | 2.5 | 428.8 | 428.8 | 123.5 | 52.9 | 525.9 | 525.2 | 86.9 | 65.5 | 209.5 | 386.8 | 173.1 | 139.1 | 281.9 | 136.1 | 116.6 | 422.5 | 218.7 | 157.6 | 138.7 | 132.2 | 146.1 | 147 | 131.1 | 140.1 | 147.7
3494.1 | 3273.1 | -6.5 | 0 | 0 | 141.9 | 137.3 | 126 | 127.3 | 149.4 | 29.5 | 20.6 | 47 | 3.3 | 245.5 | 2.3 | 428.8 | 428.8 | 123.2 | 52.9 | 525.8 | 525.3 | 87.3 | 65.8 | 209.5 | 386.6 | 172.9 | 139.1 | 281.6 | 135.7 | 116.4 | 421.4 | 218.4 | 157.5 | 138.6 | 132.2 | 146.1 | 146.9 | 131 | 140 | 147.6
3495.1 | 3274.1 | -6.6 | 0 | 0 | 142 | 137.2 | 125.9 | 127.2 | 149.3 | 29.5 | 20.6 | 46.9 | 3.6 | 249.2 | 2.1 | 428.8 | 428.8 | 122.4 | 52.9 | 525.7 | 525.1 | 87.8 | 66 | 209.5 | 386.4 | 173.1 | 139.1 | 281.4 | 135.3 | 116.5 | 420.4 | 218.4 | 157.4 | 138.5 | 132.1 | 146 | 146.9 | 130.9 | 139.9 | 147.6
3496.1 | 3275.1 | -6.7 | 0 | 0 | 141.9 | 137.1 | 125.8 | 127.2 | 149.3 | 29.5 | 20.6 | 46.8 | 3.8 | 249.7 | 2 | 428.7 | 428.7 | 122.1 | 52.8 | 525.7 | 524.9 | 88.4 | 66.1 | 209.6 | 386.3 | 173.5 | 138.9 | 281.1 | 134.9 | 116.4 | 419.5 | 218.1 | 157.3 | 138.4 | 132 | 145.9 | 146.7 | 130.8 | 139.8 | 147.5
3497.1 | 3276.1 | -6.6 | 0 | 0 | 141.8 | 137.1 | 125.7 | 127.1 | 149.2 | 29.5 | 20.6 | 46.7 | 4 | 247.6 | 1.8 | 428.7 | 428.7 | 123.1 | 52.8 | 525.6 | 524.6 | 88.7 | 66 | 209.6 | 386.1 | 174.1 | 138.9 | 280.9 | 134.5 | 116.5 | 418.6 | 217.9 | 157.2 | 138.3 | 131.9 | 145.8 | 146.6 | 130.7 | 139.8 | 147.4
3498.1 | 3277.1 | -6.6 | 0 | 0 | 141.6 | 137 | 125.4 | 127.1 | 148.9 | 29.5 | 20.7 | 46.7 | 3.5 | 246.6 | 1.8 | 428.7 | 428.7 | 123.8 | 52.7 | 525.6 | 524.4 | 88.1 | 66.1 | 209.5 | 385.9 | 174.8 | 138.8 | 280.6 | 134.3 | 116.3 | 417.7 | 217.8 | 157.1 | 138.3 | 131.8 | 145.7 | 146.5 | 130.6 | 139.7 | 147.3
3499.1 | 3278.1 | -6.6 | 0 | 0 | 141.4 | 136.9 | 125.3 | 127 | 148.6 | 29.5 | 20.7 | 46.7 | 3.2 | 245.8 | 1.7 | 428.7 | 428.6 | 124.4 | 52.7 | 525.6 | 524.4 | 87.5 | 66.4 | 209.5 | 385.8 | 173.8 | 138.5 | 280.4 | 134.2 | 116.1 | 416.9 | 217.8 | 157 | 138.3 | 131.7 | 145.6 | 146.4 | 130.5 | 139.6 | 147.2
3500.1 | 3279.1 | -6.7 | 0 | 0 | 141.4 | 136.7 | 125.2 | 126.9 | 148.5 | 29.5 | 20.7 | 46.6 | 3.2 | 245.1 | 1.7 | 428.6 | 428.6 | 124.6 | 52.8 | 525.7 | 524.3 | 86.7 | 66.5 | 209.5 | 385.6 | 173.7 | 138 | 280.1 | 134.3 | 116 | 416 | 217.5 | 156.9 | 138.1 | 131.6 | 145.6 | 146.3 | 130.4 | 139.5 | 147.1
3501.1 | 3280.1 | -6.7 | 0 | 0 | 141.4 | 136.5 | 125.2 | 126.8 | 148.4 | 29.5 | 20.7 | 46.6 | 3.3 | 233.2 | 1.5 | 428.6 | 428.6 | 125.3 | 52.6 | 525.7 | 524.4 | 86.2 | 66.5 | 209.7 | 385.5 | 174 | 137.8 | 279.8 | 134 | 115.7 | 415.3 | 217.4 | 156.8 | 137.9 | 131.5 | 145.5 | 146.2 | 130.4 | 139.4 | 147
3502.1 | 3281.1 | -6.5 | 0 | 0 | 141.3 | 136.4 | 125.1 | 126.6 | 148.5 | 29.5 | 20.7 | 46.5 | 3.1 | 214.2 | 1.5 | 428.6 | 428.6 | 125.7 | 52.5 | 525.7 | 524.8 | 85.7 | 66.4 | 209.8 | 385.3 | 174.3 | 137.6 | 279.6 | 133.8 | 115.5 | 414.5 | 217.1 | 156.7 | 137.8 | 131.4 | 145.4 | 146.1 | 130.3 | 139.3 | 146.9
3503.1 | 3282.1 | -6.7 | 0 | 0 | 141.3 | 136.4 | 125 | 126.5 | 148.5 | 29.5 | 20.7 | 46.5 | 3.4 | 201.4 | 1.6 | 428.6 | 428.5 | 124.9 | 52.5 | 525.7 | 525 | 86.3 | 66.4 | 209.7 | 385.1 | 174 | 137.4 | 279.3 | 133.7 | 115.6 | 413.8 | 216.9 | 156.7 | 137.7 | 131.3 | 145.3 | 146 | 130.3 | 139.2 | 146.8
3504.1 | 3283.1 | -6.7 | 0 | 0 | 141.1 | 136.4 | 124.8 | 126.3 | 148.5 | 29.5 | 20.7 | 46.4 | 3.3 | 198.6 | 1.2 | 428.5 | 428.5 | 124 | 52.5 | 525.6 | 525.3 | 87.4 | 66.3 | 209.7 | 385 | 174 | 137.5 | 279.1 | 133.3 | 115.7 | 413 | 216.9 | 156.5 | 137.6 | 131.2 | 145.2 | 145.9 | 130.2 | 139.1 | 146.7
3505.1 | 3284.1 | -6.8 | 0 | 0 | 141.1 | 136.4 | 124.6 | 126.3 | 148.5 | 29.4 | 20.7 | 46.4 | 3.2 | 212.9 | 1.1 | 428.5 | 428.4 | 123.5 | 52.4 | 525.5 | 525.8 | 87.4 | 66.4 | 209.8 | 384.8 | 174.5 | 137.5 | 278.8 | 133 | 116.1 | 412.3 | 217 | 156.4 | 137.5 | 131 | 145.1 | 145.8 | 130.1 | 139 | 146.6
3506.1 | 3285.1 | -6.8 | 0 | 0 | 141.1 | 136.3 | 124.6 | 126.3 | 148.4 | 29.4 | 20.7 | 46.4 | 3.1 | 231.6 | 2 | 428.5 | 428.4 | 124.7 | 52.4 | 525.5 | 526.1 | 86.9 | 66.4 | 209.8 | 384.6 | 174.1 | 137.4 | 278.6 | 132.9 | 116 | 411.6 | 216.9 | 156.3 | 137.4 | 130.9 | 145 | 145.7 | 130 | 138.9 | 146.5
3507.1 | 3286.1 | -6.8 | 0 | 0 | 141.1 | 136.2 | 124.5 | 126.3 | 148 | 29.5 | 20.7 | 46.4 | 3.2 | 253.7 | 3.4 | 428.5 | 428.4 | 125 | 52.4 | 525.5 | 526 | 86.2 | 66.3 | 209.7 | 384.5 | 173.8 | 137.5 | 278.3 | 132.9 | 115.5 | 411 | 216.8 | 156.2 | 137.3 | 130.8 | 144.8 | 145.6 | 129.9 | 138.8 | 146.4
3508.1 | 3287.1 | -6.7 | 0 | 0 | 141 | 135.8 | 124.5 | 126.2 | 147.8 | 29.5 | 20.7 | 46.3 | 3.3 | 264 | 4.4 | 428.4 | 428.3 | 125 | 52.4 | 525.5 | 525.8 | 85.5 | 66.3 | 209.7 | 384.3 | 174.4 | 137.5 | 278.1 | 133.1 | 115.4 | 410.3 | 216.4 | 156.1 | 137.1 | 130.7 | 144.7 | 145.5 | 129.8 | 138.7 | 146.3
3509.1 | 3288.1 | -6.6 | 0 | 0 | 140.9 | 135.6 | 124.4 | 126.1 | 147.6 | 29.4 | 20.7 | 46.3 | 3.6 | 249.7 | 4.9 | 428.4 | 428.3 | 125.4 | 52.4 | 525.5 | 525.5 | 85.1 | 66.4 | 209.6 | 384.2 | 174.4 | 137.4 | 277.8 | 133.3 | 115.6 | 409.6 | 216.3 | 156 | 137 | 130.6 | 144.6 | 145.4 | 129.7 | 138.6 | 146.3
3510.1 | 3289.1 | -6.6 | 0 | 0 | 140.8 | 135.5 | 124.3 | 126 | 147.4 | 29.4 | 20.7 | 46.3 | 3.7 | 236.6 | 5.2 | 428.4 | 428.3 | 124.3 | 52.4 | 525.5 | 525.5 | 84.7 | 66.4 | 209.5 | 384.1 | 174.7 | 137.5 | 277.5 | 133.3 | 115.6 | 409 | 216.1 | 155.9 | 136.9 | 130.5 | 144.5 | 145.2 | 129.6 | 138.5 | 146.2
3511.1 | 3290.1 | -6.5 | 0 | 0 | 140.7 | 135.5 | 124.1 | 125.9 | 147.5 | 29.4 | 20.7 | 46.3 | 3.5 | 235.7 | 5.2 | 428.4 | 428.1 | 123.8 | 52.3 | 525.4 | 526 | 84.6 | 66.2 | 209.3 | 383.9 | 174.6 | 137.6 | 277.2 | 133.3 | 115.7 | 408.3 | 216 | 155.8 | 136.8 | 130.5 | 144.4 | 145.1 | 129.5 | 138.4 | 146.1
3512.1 | 3291.1 | -6.3 | 0 | 0 | 140.6 | 135.4 | 124 | 125.8 | 147.6 | 29.4 | 20.7 | 46.2 | 3.6 | 237.9 | 5 | 428.3 | 428.2 | 122.7 | 52.3 | 525.4 | 526.1 | 84.9 | 66.3 | 209.3 | 383.7 | 174.8 | 137.8 | 277 | 133 | 115.6 | 407.7 | 215.8 | 155.7 | 136.8 | 130.4 | 144.4 | 145 | 129.4 | 138.4 | 146
3513.1 | 3292.1 | -6.3 | 0 | 0 | 140.4 | 135.4 | 123.9 | 125.7 | 147.6 | 29.4 | 20.7 | 46.2 | 3.2 | 243.1 | 5.5 | 428.3 | 428.1 | 122.2 | 52.4 | 525.3 | 526 | 84.9 | 66.8 | 209.2 | 383.6 | 174.4 | 137.9 | 276.7 | 133.2 | 115.5 | 407.1 | 215.5 | 155.7 | 136.7 | 130.3 | 144.3 | 144.9 | 129.3 | 138.3 | 145.9
3514.1 | 3293.1 | -6.6 | 0 | 0 | 140.3 | 135.3 | 123.8 | 125.7 | 147.4 | 29.4 | 20.7 | 46.2 | 3.2 | 243.2 | 5.2 | 428.3 | 428.1 | 121.4 | 52.3 | 525.3 | 525.7 | 84.9 | 67 | 209.1 | 383.5 | 173.8 | 137.8 | 276.5 | 133.1 | 115.4 | 406.5 | 215.3 | 155.6 | 136.7 | 130.2 | 144.2 | 144.8 | 129.2 | 138.2 | 145.8
3515.1 | 3294.1 | -6.5 | 0 | 0 | 140.2 | 135.2 | 123.7 | 125.6 | 147.2 | 29.4 | 20.7 | 46.2 | 3.4 | 242.7 | 4.8 | 428.3 | 428.1 | 120.7 | 52.2 | 525.2 | 525.6 | 85.4 | 66.9 | 209.1 | 383.3 | 173.3 | 137.6 | 276.2 | 133.1 | 115.2 | 405.9 | 215.3 | 155.5 | 136.5 | 130.1 | 144.1 | 144.7 | 129.2 | 138.1 | 145.7
3516.1 | 3295.1 | -6.3 | 0 | 0 | 140.2 | 135.1 | 123.7 | 125.5 | 147.2 | 29.4 | 20.7 | 46.2 | 3.4 | 235.3 | 4.5 | 428.2 | 428 | 120 | 52.1 | 525.1 | 525.6 | 85.2 | 66.8 | 209 | 383.1 | 173.8 | 137.8 | 276 | 132.8 | 115.1 | 405.3 | 215.1 | 155.4 | 136.4 | 130 | 144 | 144.6 | 129.1 | 138 | 145.6
3517.1 | 3296.1 | -6.2 | 0 | 0 | 140.1 | 135.1 | 123.6 | 125.3 | 147 | 29.4 | 20.7 | 46.2 | 3.3 | 234.6 | 4.1 | 428.2 | 428.1 | 119.4 | 52 | 525 | 525.7 | 85 | 66.7 | 208.9 | 383 | 173.6 | 138.1 | 275.8 | 132.6 | 115.2 | 404.7 | 215.1 | 155.3 | 136.3 | 129.9 | 143.9 | 144.4 | 129 | 137.9 | 145.5
3518.1 | 3297.1 | -6.5 | 0 | 0 | 140 | 135 | 123.5 | 125.3 | 146.9 | 29.3 | 20.7 | 46.1 | 3.5 | 247.4 | 4.3 | 428.2 | 428 | 118.7 | 51.8 | 524.9 | 525.6 | 84.8 | 66.4 | 208.8 | 382.9 | 173.3 | 138.1 | 275.5 | 132.7 | 115.1 | 404.1 | 215 | 155.2 | 136.3 | 129.8 | 143.9 | 144.3 | 128.9 | 137.8 | 145.4
3519.1 | 3298.1 | -6.7 | 0 | 0 | 139.9 | 135 | 123.5 | 125.2 | 146.8 | 29.3 | 20.7 | 46.1 | 3.2 | 253.2 | 4.6 | 428.2 | 428 | 117.5 | 51.5 | 524.9 | 525.5 | 84.6 | 66.3 | 208.7 | 382.7 | 173.2 | 138.1 | 275.3 | 132.4 | 115.1 | 403.5 | 214.9 | 155.2 | 136.2 | 129.7 | 143.8 | 144.2 | 128.8 | 137.7 | 145.4
3520.1 | 3299.1 | -6.7 | 0 | 0 | 139.8 | 134.9 | 123.5 | 125.1 | 146.8 | 29.3 | 20.7 | 46.1 | 3.1 | 243.8 | 4.8 | 428.1 | 427.9 | 116.8 | 51.4 | 524.9 | 525.2 | 84.4 | 66.3 | 208.6 | 382.5 | 172.9 | 137.9 | 275 | 132.1 | 115.1 | 403 | 214.9 | 155 | 136.1 | 129.6 | 143.7 | 144.1 | 128.8 | 137.6 | 145.3
3521.1 | 3300.1 | -5.5 | 0 | 0 | 139.6 | 134.8 | 123.6 | 125.1 | 146.9 | 29.2 | 20.7 | 46.1 | 3 | 243.4 | 5.1 | 428.1 | 427.8 | 116.8 | 51.1 | 524.8 | 525.1 | 85.3 | 66 | 208.5 | 382.4 | 172.4 | 137.7 | 274.7 | 131.8 | 115.2 | 402.4 | 214.7 | 154.9 | 136 | 129.5 | 143.7 | 144 | 128.6 | 137.5 | 145.2
3522.1 | 3301.1 | -5.1 | 0 | 0 | 139.4 | 134.6 | 123.5 | 125 | 146.9 | 29.2 | 20.7 | 46.1 | 3.3 | 245 | 5.2 | 428.1 | 427.8 | 116.2 | 51 | 524.8 | 525.5 | 85.6 | 66 | 208.4 | 382.2 | 172.5 | 137.7 | 274.5 | 131.7 | 115.3 | 401.9 | 214.8 | 154.8 | 135.9 | 129.4 | 143.6 | 143.9 | 128.5 | 137.4 | 145.1
3523.1 | 3302.1 | -5.7 | 0 | 0 | 139.3 | 134.3 | 123.4 | 124.9 | 146.8 | 29.2 | 20.7 | 46 | 3.4 | 245.9 | 5.2 | 428.1 | 427.8 | 115.9 | 50.9 | 524.7 | 525.4 | 86.5 | 66.2 | 208.3 | 382.1 | 172.4 | 137.7 | 274.2 | 131.5 | 115.4 | 401.3 | 214.6 | 154.7 | 135.9 | 129.3 | 143.5 | 143.7 | 128.4 | 137.3 | 145
3524.1 | 3303.1 | -6.2 | 0 | 0 | 139.2 | 134 | 123.3 | 124.8 | 146.6 | 29.2 | 20.7 | 46 | 3.6 | 250.3 | 5.5 | 428 | 427.7 | 116.9 | 50.9 | 524.7 | 525 | 87.1 | 66.2 | 208.2 | 381.9 | 172.7 | 137.9 | 274 | 131.2 | 115.2 | 400.8 | 214.3 | 154.6 | 135.8 | 129.2 | 143.4 | 143.6 | 128.3 | 137.2 | 144.9
3525.1 | 3304.1 | -6.3 | 0 | 0 | 139.1 | 133.8 | 123.3 | 124.6 | 146.6 | 29.2 | 20.7 | 46 | 3.5 | 244.2 | 5.9 | 428 | 427.8 | 118.3 | 51 | 524.6 | 524.8 | 86.6 | 66.3 | 208.1 | 381.8 | 172.9 | 137.8 | 273.7 | 131.1 | 115.1 | 400.2 | 214 | 154.5 | 135.7 | 129.1 | 143.3 | 143.5 | 128.2 | 137.1 | 144.8
3526.1 | 3305.1 | -6.3 | 0 | 0 | 139 | 133.7 | 123.3 | 124.5 | 146.5 | 29.2 | 20.7 | 46 | 3.7 | 232.3 | 6.2 | 428 | 427.7 | 118.1 | 51.2 | 524.6 | 524.8 | 86.1 | 66.2 | 208.1 | 381.6 | 173.2 | 137.8 | 273.5 | 130.8 | 115.2 | 399.7 | 213.8 | 154.4 | 135.6 | 129 | 143.1 | 143.4 | 128.1 | 137 | 144.8
3527.1 | 3306.1 | -6.3 | 0 | 0 | 138.9 | 133.7 | 123.2 | 124.2 | 146.2 | 29.2 | 20.7 | 45.9 | 3.6 | 243 | 5.9 | 427.9 | 427.6 | 118.2 | 51.4 | 524.6 | 524.8 | 86 | 66.2 | 208.1 | 381.4 | 173.5 | 137.8 | 273.3 | 130.6 | 115.2 | 399.1 | 213.7 | 154.3 | 135.5 | 128.9 | 143.1 | 143.3 | 128 | 136.9 | 144.7
3528.1 | 3307.1 | -6.2 | 0 | 0 | 138.8 | 133.7 | 123.1 | 123.9 | 145.7 | 29.2 | 20.7 | 45.9 | 3.3 | 243.6 | 5.5 | 427.9 | 427.7 | 118.3 | 51.6 | 524.5 | 524.7 | 86.3 | 66.1 | 208.1 | 381.3 | 173.7 | 137.6 | 273 | 130.4 | 115 | 398.6 | 213.4 | 154.2 | 135.5 | 128.8 | 143 | 143.3 | 127.8 | 136.8 | 144.6
3529.1 | 3308.1 | -6.4 | 0 | 0 | 138.7 | 133.6 | 123 | 123.7 | 145.6 | 29.2 | 20.7 | 45.9 | 3.2 | 243.1 | 5.2 | 427.9 | 427.6 | 117.5 | 51.7 | 524.5 | 524.6 | 86.4 | 66.1 | 208.1 | 381.1 | 173.6 | 137.6 | 272.8 | 130.3 | 115.1 | 398.1 | 213.3 | 154.1 | 135.4 | 128.7 | 142.9 | 143.2 | 127.8 | 136.7 | 144.5
3530.1 | 3309.1 | -6.6 | 0 | 0 | 138.4 | 133.6 | 122.9 | 123.7 | 145.6 | 29.1 | 20.7 | 45.9 | 3.6 | 236.9 | 5 | 427.9 | 427.6 | 116.6 | 51.9 | 524.4 | 524.7 | 87.6 | 66.3 | 208.1 | 380.9 | 173.9 | 137.7 | 272.5 | 130.2 | 115.1 | 397.6 | 213.1 | 154 | 135.4 | 128.6 | 142.9 | 143.1 | 127.7 | 136.6 | 144.4
3531.1 | 3310.1 | -6.7 | 0 | 0 | 138.2 | 133.6 | 122.8 | 123.6 | 145.7 | 29.1 | 20.7 | 45.8 | 3.9 | 237.1 | 5 | 427.8 | 427.5 | 115.5 | 51.9 | 524.3 | 524.7 | 87.2 | 66.5 | 208.2 | 380.8 | 173.4 | 137.6 | 272.3 | 130.4 | 115.3 | 397.1 | 213.2 | 153.9 | 135.4 | 128.5 | 142.8 | 143 | 127.5 | 136.5 | 144.3
3532.1 | 3311.1 | -6.8 | 0 | 0 | 138.1 | 133.6 | 122.6 | 123.6 | 145.5 | 29.1 | 20.7 | 45.8 | 3.5 | 237.1 | 5.5 | 427.8 | 427.5 | 115.4 | 51.9 | 524.2 | 524.9 | 86.3 | 66.5 | 208.1 | 380.6 | 173.6 | 137.5 | 272 | 130.7 | 115.2 | 396.6 | 213 | 153.8 | 135.4 | 128.3 | 142.7 | 142.9 | 127.4 | 136.5 | 144.2
3533.1 | 3312.1 | -6.8 | 0 | 0 | 137.9 | 133.4 | 122.3 | 123.6 | 145.1 | 29.1 | 20.7 | 45.7 | 3.5 | 240.3 | 5.8 | 427.8 | 427.5 | 116.2 | 51.7 | 524.2 | 524.9 | 85.3 | 66.3 | 208.2 | 380.4 | 173.7 | 137.3 | 271.8 | 130.6 | 115 | 396 | 212.9 | 153.7 | 135.3 | 128.3 | 142.6 | 142.8 | 127.3 | 136.4 | 144.1
3534.1 | 3313.1 | -6.8 | 0 | 0 | 137.7 | 133.3 | 122.1 | 123.5 | 144.7 | 29 | 20.7 | 45.7 | 3.7 | 243.5 | 6.2 | 427.8 | 427.4 | 115.6 | 51.6 | 524.2 | 525 | 84.6 | 66 | 208.2 | 380.3 | 173.4 | 137 | 271.6 | 130.3 | 114.9 | 395.5 | 212.8 | 153.6 | 135.2 | 128.2 | 142.5 | 142.7 | 127.3 | 136.3 | 144.1
3535.1 | 3314.1 | -6.8 | 0 | 0 | 137.5 | 133.3 | 121.9 | 123.4 | 144.6 | 29 | 20.7 | 45.7 | 3.5 | 239.9 | 6.4 | 427.7 | 427.4 | 115.6 | 51.4 | 524.2 | 525.1 | 84.4 | 65.7 | 208.1 | 380.1 | 172.8 | 136.8 | 271.3 | 130.2 | 114.8 | 395 | 212.7 | 153.5 | 135.1 | 128.1 | 142.5 | 142.6 | 127.3 | 136.1 | 144
3536.1 | 3315.1 | -6.7 | 0 | 0 | 137.4 | 133.2 | 121.7 | 123.3 | 144.6 | 29 | 20.7 | 45.7 | 3.4 | 240.6 | 6.4 | 427.7 | 427.3 | 115.6 | 51.3 | 524.2 | 524.8 | 84.8 | 65.5 | 208 | 379.9 | 173.1 | 136.7 | 271.1 | 129.9 | 114.3 | 394.5 | 212.5 | 153.4 | 135 | 128 | 142.3 | 142.6 | 127.3 | 136 | 143.9
3537.1 | 3316.1 | -6.7 | 0 | 0 | 137.3 | 133 | 121.6 | 123.2 | 144.3 | 29 | 20.7 | 45.7 | 3.5 | 240.8 | 6.6 | 427.7 | 427.3 | 117 | 51.1 | 524.2 | 524.6 | 85.3 | 65.4 | 208 | 379.8 | 172.9 | 136.3 | 270.9 | 129.8 | 113.8 | 394 | 212.3 | 153.3 | 134.9 | 127.9 | 142.2 | 142.5 | 127.2 | 135.9 | 143.8
3538.1 | 3317.1 | -6.5 | 0 | 0 | 137.2 | 132.8 | 121.5 | 123 | 144.1 | 29.1 | 20.7 | 45.7 | 3.6 | 227.9 | 6.4 | 427.7 | 427.3 | 118 | 50.9 | 524.3 | 524.3 | 85.1 | 65.1 | 207.9 | 379.6 | 172.9 | 136 | 270.6 | 129.6 | 113.7 | 393.5 | 212.3 | 153.2 | 134.8 | 127.9 | 142.1 | 142.4 | 127.2 | 135.8 | 143.7
3539.1 | 3318.1 | -6.6 | 0 | 0 | 137.1 | 132.8 | 121.5 | 122.9 | 144.3 | 29.1 | 20.7 | 45.7 | 3.6 | 254.9 | 5.3 | 427.6 | 427.3 | 118.6 | 50.8 | 524.3 | 524 | 85.1 | 64.9 | 207.9 | 379.4 | 172.9 | 135.9 | 270.3 | 129.5 | 113.7 | 393 | 211.9 | 153.1 | 134.8 | 127.8 | 142 | 142.3 | 127.1 | 135.7 | 143.6
3540.1 | 3319.1 | -6.5 | 0 | 0 | 136.9 | 132.7 | 121.4 | 122.7 | 144.6 | 29.1 | 20.7 | 45.7 | 2.9 | 268.7 | 4.5 | 427.6 | 427.2 | 118.3 | 50.7 | 524.3 | 524.1 | 85.4 | 64.7 | 207.9 | 379.2 | 172.8 | 135.8 | 270 | 129.4 | 113.5 | 392.5 | 211.7 | 153 | 134.6 | 127.7 | 141.9 | 142.2 | 127 | 135.6 | 143.5
3541.1 | 3320.1 | -6.2 | 0 | 0 | 136.8 | 132.6 | 121.2 | 122.6 | 144.6 | 29 | 20.7 | 45.7 | 3 | 231.3 | 4.3 | 427.6 | 427.2 | 118.3 | 50.6 | 524.3 | 524.3 | 85.7 | 64.3 | 207.9 | 379.1 | 172.8 | 135.7 | 269.8 | 129.3 | 113.4 | 392 | 211.7 | 152.9 | 134.6 | 127.6 | 141.8 | 142.1 | 126.9 | 135.5 | 143.4
3542.1 | 3321.1 | -5.8 | 0 | 0 | 136.8 | 132.5 | 121 | 122.5 | 144.4 | 29 | 20.7 | 45.6 | 3.1 | 202.1 | 4.1 | 427.6 | 427.1 | 118.2 | 50.5 | 524.2 | 524.2 | 85.3 | 64 | 207.8 | 378.9 | 173.2 | 135.5 | 269.6 | 129 | 113.6 | 391.5 | 211.7 | 152.8 | 134.5 | 127.6 | 141.7 | 142 | 126.8 | 135.4 | 143.4
3543.1 | 3322.1 | -6.4 | 0 | 0 | 136.8 | 132.4 | 121 | 122.4 | 144.4 | 28.9 | 20.7 | 45.6 | 3.1 | 209.2 | 3.7 | 427.5 | 427.1 | 118.9 | 50.5 | 524.2 | 524.2 | 85.2 | 63.7 | 207.7 | 378.7 | 173 | 135.4 | 269.4 | 128.8 | 113.4 | 391.1 | 211.8 | 152.8 | 134.5 | 127.5 | 141.6 | 141.9 | 126.7 | 135.3 | 143.3
3544.1 | 3323.1 | -6.6 | 0 | 0 | 136.8 | 132.3 | 120.9 | 122.4 | 144.5 | 28.9 | 20.7 | 45.6 | 3.2 | 220.4 | 3.1 | 427.5 | 427.1 | 118.4 | 50.5 | 524.2 | 524.2 | 85.2 | 63.5 | 207.4 | 378.5 | 172.6 | 135.2 | 269.1 | 128.6 | 113 | 390.5 | 211.5 | 152.7 | 134.4 | 127.4 | 141.5 | 141.7 | 126.6 | 135.2 | 143.2
3545.1 | 3324.1 | -6.5 | 0 | 0 | 136.7 | 132.2 | 120.8 | 122.4 | 144.5 | 28.9 | 20.7 | 45.6 | 3.9 | 236.5 | 2.7 | 427.5 | 427 | 118.1 | 50.5 | 524.3 | 524.1 | 84.7 | 63.4 | 207.4 | 378.3 | 172 | 135 | 268.9 | 128.4 | 112.8 | 390 | 211.2 | 152.6 | 134.3 | 127.3 | 141.5 | 141.6 | 126.5 | 135 | 143.1
3546.1 | 3325.1 | -6.3 | 0 | 0 | 136.6 | 132 | 120.7 | 122.3 | 144.5 | 28.9 | 20.7 | 45.6 | 3.9 | 245.6 | 3.4 | 427.4 | 427 | 119.1 | 50.5 | 524.4 | 524.1 | 84.1 | 63.2 | 207.4 | 378.2 | 172 | 134.9 | 268.7 | 128.2 | 112.5 | 389.6 | 211 | 152.5 | 134.3 | 127.2 | 141.4 | 141.5 | 126.4 | 134.9 | 143
3547.1 | 3326.1 | -5.8 | 0 | 0 | 136.5 | 131.8 | 120.6 | 122.2 | 144.5 | 28.9 | 20.7 | 45.5 | 3.8 | 232.3 | 4 | 427.4 | 426.9 | 119.9 | 50.5 | 524.5 | 524.2 | 83.5 | 63.3 | 207.3 | 378 | 171.8 | 134.4 | 268.4 | 128.3 | 112.2 | 389.1 | 210.8 | 152.4 | 134.2 | 127.1 | 141.3 | 141.4 | 126.4 | 134.7 | 142.9
3548.1 | 3327.1 | -5.7 | 0 | 0 | 136.4 | 131.6 | 120.5 | 122 | 144.4 | 28.9 | 20.7 | 45.5 | 3.2 | 248.2 | 3.9 | 427.4 | 426.9 | 120.1 | 50.6 | 524.5 | 524.2 | 83.2 | 63.3 | 207.3 | 377.8 | 171.9 | 134 | 268.2 | 128 | 111.7 | 388.6 | 210.6 | 152.3 | 134 | 127 | 141.3 | 141.3 | 126.3 | 134.7 | 142.8
3549.1 | 3328.1 | -6 | 0 | 0 | 136.2 | 131.5 | 120.3 | 121.8 | 144.3 | 28.9 | 20.7 | 45.5 | 3.3 | 240.3 | 4 | 427.4 | 426.9 | 120.6 | 50.6 | 524.7 | 524 | 82.6 | 63.1 | 207.4 | 377.6 | 172 | 133.8 | 267.9 | 127.8 | 111.5 | 388.1 | 210.3 | 152.2 | 133.8 | 126.9 | 141.2 | 141.2 | 126.2 | 134.6 | 142.7
3550.1 | 3329.1 | -6.5 | 0 | 0 | 136.2 | 131.4 | 120.2 | 121.8 | 144.3 | 28.8 | 20.7 | 45.6 | 3.2 | 232.8 | 4.2 | 427.3 | 426.9 | 121.3 | 50.5 | 524.8 | 523.8 | 82.2 | 62.9 | 207.4 | 377.5 | 171.9 | 133.7 | 267.7 | 127.9 | 111.3 | 387.7 | 210.1 | 152.2 | 133.7 | 126.7 | 141.1 | 141.2 | 126.1 | 134.6 | 142.6
3551.1 | 3330.1 | -6.7 | 0 | 0 | 136.1 | 131.3 | 120.2 | 121.7 | 144.3 | 28.8 | 20.7 | 45.6 | 3.4 | 240 | 4.2 | 427.3 | 426.8 | 121.5 | 50.3 | 524.8 | 523.8 | 82.2 | 62.8 | 207.2 | 377.3 | 171.8 | 133.5 | 267.4 | 127.9 | 111.2 | 387.2 | 209.9 | 152.1 | 133.6 | 126.6 | 141 | 141.1 | 126 | 134.5 | 142.5
3552.1 | 3331.1 | -6.8 | 0 | 0 | 136 | 131.2 | 120.1 | 121.7 | 144.2 | 28.9 | 20.7 | 45.6 | 3.7 | 248 | 4.5 | 427.3 | 426.8 | 122 | 50.3 | 524.9 | 523.8 | 81.9 | 62.8 | 207.2 | 377.1 | 172.5 | 133.4 | 267.1 | 127.9 | 111.2 | 386.7 | 209.8 | 151.9 | 133.4 | 126.5 | 141 | 141 | 125.9 | 134.5 | 142.5
3553.1 | 3332.1 | -6.8 | 0 | 0 | 136 | 131.2 | 120 | 121.6 | 144.2 | 28.8 | 20.7 | 45.6 | 3.3 | 229.2 | 5 | 427.2 | 426.7 | 122.5 | 50.3 | 524.9 | 523.7 | 82.5 | 62.8 | 207.3 | 376.9 | 172.7 | 132.9 | 266.8 | 127.6 | 111 | 386.2 | 209.8 | 151.9 | 133.3 | 126.4 | 140.9 | 140.9 | 125.8 | 134.4 | 142.4
3554.1 | 3333.1 | -6.8 | 0 | 0 | 135.7 | 131.1 | 119.9 | 121.5 | 143.9 | 28.8 | 20.7 | 45.5 | 3.4 | 227.9 | 5.4 | 427.2 | 426.7 | 121.6 | 50.3 | 524.9 | 523.6 | 82.7 | 62.8 | 207.3 | 376.7 | 172.8 | 132.7 | 266.6 | 127.5 | 111 | 385.8 | 209.4 | 151.8 | 133.1 | 126.4 | 140.8 | 140.8 | 125.8 | 134.4 | 142.3
3555.1 | 3334.1 | -6.8 | 0 | 0 | 135.5 | 131 | 119.8 | 121.5 | 143.5 | 28.8 | 20.7 | 45.5 | 3.2 | 223.7 | 5.4 | 427.2 | 426.6 | 121.5 | 50.3 | 524.9 | 523.5 | 82.4 | 63 | 207.4 | 376.5 | 171.9 | 132.7 | 266.3 | 127.4 | 110.8 | 385.3 | 209.4 | 151.7 | 133 | 126.3 | 140.7 | 140.7 | 125.6 | 134.3 | 142.2
3556.1 | 3335.1 | -6.7 | 0 | 0 | 135.4 | 131 | 119.7 | 121.5 | 143.3 | 28.8 | 20.7 | 45.5 | 3.3 | 232.9 | 4.9 | 427.2 | 426.7 | 122.8 | 50.3 | 524.9 | 523.4 | 82 | 63 | 207.3 | 376.3 | 171.8 | 132.6 | 266.1 | 127.5 | 110.7 | 384.8 | 209.4 | 151.7 | 132.9 | 126.2 | 140.6 | 140.6 | 125.5 | 134.2 | 142.1
3557.1 | 3336.1 | -6.7 | 0 | 0 | 135.3 | 130.9 | 119.7 | 121.5 | 143.1 | 28.7 | 20.7 | 45.4 | 3.2 | 246 | 4.6 | 427.1 | 426.6 | 123.9 | 50.3 | 524.9 | 523.2 | 81.9 | 63 | 207.4 | 376.1 | 171.8 | 132.3 | 265.8 | 127.4 | 110.7 | 384.4 | 209.1 | 151.6 | 132.8 | 126.1 | 140.5 | 140.6 | 125.4 | 134.1 | 142
3558.1 | 3337.1 | -6.7 | 0 | 0 | 135.3 | 130.7 | 119.7 | 121.4 | 143 | 28.7 | 20.7 | 45.4 | 3.5 | 241.9 | 4.4 | 427.1 | 426.5 | 124 | 50.3 | 524.9 | 523.2 | 82.5 | 63.1 | 207.3 | 376 | 171.4 | 132.1 | 265.6 | 127.3 | 111 | 383.9 | 208.9 | 151.5 | 132.7 | 126.1 | 140.5 | 140.5 | 125.3 | 134.1 | 142
3559.1 | 3338.1 | -6.8 | 0 | 0 | 135.3 | 130.3 | 119.7 | 121.4 | 143.1 | 28.7 | 20.7 | 45.4 | 3.1 | 228.8 | 4.3 | 427.1 | 426.5 | 123.4 | 50.4 | 524.8 | 523.9 | 83.3 | 63.1 | 207.3 | 375.8 | 170.9 | 132.2 | 265.3 | 127.2 | 111 | 383.5 | 208.9 | 151.4 | 132.6 | 126 | 140.4 | 140.4 | 125.2 | 134 | 141.9
3560.1 | 3339.1 | -6.8 | 0 | 0 | 135.4 | 130.1 | 119.7 | 121.2 | 143 | 28.6 | 20.7 | 45.4 | 3.2 | 223.3 | 4.5 | 427 | 426.5 | 122.5 | 50.5 | 524.7 | 525.2 | 83.8 | 63 | 207.2 | 375.6 | 170.6 | 132.2 | 265 | 127 | 110.9 | 383 | 208.8 | 151.3 | 132.6 | 125.9 | 140.3 | 140.3 | 125.1 | 133.9 | 141.8
3561.1 | 3340.1 | -6.8 | 0 | 0 | 135.3 | 130 | 119.6 | 121.1 | 142.9 | 28.6 | 20.7 | 45.4 | 3.4 | 220.1 | 5.2 | 427 | 426.4 | 121.4 | 50.6 | 524.6 | 525.6 | 84 | 63 | 207.1 | 375.4 | 170.4 | 132.2 | 264.8 | 126.9 | 110.9 | 382.6 | 208.9 | 151.2 | 132.5 | 125.8 | 140.2 | 140.2 | 125.1 | 133.8 | 141.7
3562.1 | 3341.1 | -6.7 | 0 | 0 | 135.1 | 129.9 | 119.5 | 120.9 | 143 | 28.6 | 20.7 | 45.3 | 3.4 | 229.2 | 5.5 | 427 | 426.4 | 121.5 | 50.7 | 524.5 | 525.7 | 83.7 | 63.2 | 207.1 | 375.2 | 170.2 | 132 | 264.6 | 126.7 | 110.7 | 382.1 | 208.8 | 151.1 | 132.4 | 125.7 | 140.1 | 140.2 | 125 | 133.7 | 141.6
3563.1 | 3342.1 | -6.8 | 0 | 0 | 135 | 129.8 | 119.4 | 120.7 | 143.1 | 28.6 | 20.7 | 45.3 | 3.2 | 251.8 | 5.7 | 426.9 | 426.4 | 121.9 | 50.8 | 524.4 | 525.8 | 82.9 | 63.3 | 207.1 | 375 | 169.9 | 131.9 | 264.3 | 126.6 | 110.8 | 381.7 | 208.7 | 151 | 132.4 | 125.6 | 140 | 140.1 | 124.9 | 133.6 | 141.5
3564.1 | 3343.1 | -6.8 | 0 | 0 | 134.9 | 129.6 | 119.3 | 120.6 | 143.1 | 28.6 | 20.7 | 45.3 | 3.2 | 237.4 | 6.5 | 426.9 | 426.4 | 122.3 | 51 | 524.3 | 525.9 | 82.1 | 63.3 | 207.2 | 374.8 | 169.3 | 131.6 | 264 | 126.5 | 110.9 | 381.2 | 208.5 | 151 | 132.3 | 125.5 | 140 | 140 | 124.8 | 133.5 | 141.4
3565.1 | 3344.1 | -6.8 | 0 | 0 | 134.8 | 129.5 | 119.2 | 120.5 | 142.9 | 28.7 | 20.7 | 45.3 | 3.3 | 236.4 | 6.9 | 426.9 | 426.3 | 121.7 | 51.1 | 524.3 | 525.9 | 82 | 63.3 | 207.1 | 374.7 | 168.6 | 131.4 | 263.7 | 126.4 | 110.6 | 380.8 | 208.3 | 150.9 | 132.3 | 125.4 | 139.9 | 139.9 | 124.7 | 133.4 | 141.4
3566.1 | 3345.1 | -6.7 | 0 | 0 | 134.7 | 129.5 | 119.1 | 120.5 | 142.4 | 28.7 | 20.7 | 45.3 | 3.2 | 246.7 | 6.2 | 426.9 | 426.2 | 122.3 | 51.2 | 524.3 | 525.6 | 82.3 | 63.3 | 207 | 374.5 | 168.5 | 131.1 | 263.5 | 126.2 | 110.8 | 380.3 | 208.1 | 150.8 | 132.2 | 125.3 | 139.8 | 139.8 | 124.6 | 133.4 | 141.3
3567.1 | 3346.1 | -6.8 | 0 | 0 | 134.7 | 129.5 | 118.9 | 120.5 | 142.2 | 28.7 | 20.7 | 45.2 | 3.1 | 237.2 | 6.2 | 426.8 | 426.2 | 123.3 | 51.4 | 524.3 | 525.2 | 81.8 | 63.1 | 206.9 | 374.3 | 168.3 | 130.9 | 263.2 | 126.4 | 110.7 | 379.9 | 207.9 | 150.6 | 132.1 | 125.2 | 139.7 | 139.7 | 124.5 | 133.3 | 141.2
3568.1 | 3347.1 | -6.8 | 0 | 0 | 134.6 | 129.5 | 118.8 | 120.4 | 142 | 28.7 | 20.7 | 45.2 | 3.1 | 238.8 | 6.4 | 426.8 | 426.3 | 124.2 | 51.5 | 524.2 | 524.8 | 82.3 | 63.1 | 206.9 | 374.1 | 167.9 | 130.6 | 263 | 126.4 | 110.7 | 379.4 | 207.6 | 150.6 | 132 | 125 | 139.6 | 139.5 | 124.4 | 133.2 | 141.1
3569.1 | 3348.1 | -6.8 | 0 | 0 | 134.4 | 129.5 | 118.7 | 120.4 | 142 | 28.7 | 20.7 | 45.2 | 3.1 | 248.2 | 6.5 | 426.8 | 426.2 | 123.2 | 51.5 | 524.2 | 524.8 | 82.9 | 63.2 | 206.9 | 373.9 | 167.6 | 130.5 | 262.7 | 126.3 | 110.5 | 379 | 207.6 | 150.5 | 131.9 | 124.9 | 139.4 | 139.5 | 124.4 | 133.2 | 141
3570.1 | 3349.1 | -6.8 | 0 | 0 | 134 | 129.4 | 118.5 | 120.3 | 142 | 28.7 | 20.7 | 45.2 | 3 | 241.8 | 6.3 | 426.7 | 426.1 | 121.7 | 51.4 | 524.1 | 524.8 | 83.6 | 63.2 | 206.9 | 373.7 | 167.7 | 130.3 | 262.5 | 126.1 | 110.4 | 378.5 | 207.6 | 150.4 | 131.8 | 124.9 | 139.3 | 139.4 | 124.3 | 133.1 | 140.9
3571.1 | 3350.1 | -6.8 | 0 | 0 | 133.9 | 129.3 | 118.4 | 120.3 | 141.9 | 28.7 | 20.7 | 45.2 | 3.1 | 242.2 | 6.3 | 426.7 | 426 | 122 | 51.4 | 524 | 524.8 | 83.6 | 63.1 | 206.9 | 373.5 | 167.7 | 130.2 | 262.2 | 125.8 | 110.2 | 378 | 207.5 | 150.4 | 131.7 | 124.8 | 139.3 | 139.3 | 124.3 | 133 | 140.9
3572.1 | 3351.1 | -6.7 | 0 | 0 | 133.8 | 129.3 | 118.3 | 120.2 | 141.7 | 28.7 | 20.7 | 45.2 | 3.1 | 243.8 | 6.4 | 426.7 | 426.1 | 122.4 | 51.4 | 524 | 524.6 | 83.7 | 63.1 | 206.7 | 373.3 | 167.4 | 129.7 | 261.9 | 125.6 | 110.1 | 377.6 | 207.3 | 150.2 | 131.6 | 124.8 | 139.2 | 139.2 | 124.2 | 132.9 | 140.8
3573.1 | 3352.1 | -6.5 | 0 | 0 | 133.9 | 129.2 | 118.2 | 120.1 | 141.5 | 28.7 | 20.7 | 45.2 | 3.2 | 241.1 | 6.3 | 426.7 | 426.1 | 123.3 | 51.4 | 524 | 524.2 | 84 | 63.1 | 206.7 | 373.1 | 166.6 | 129.1 | 261.7 | 125.5 | 110.1 | 377.1 | 207 | 150.2 | 131.6 | 124.7 | 139.2 | 139.1 | 124.2 | 132.8 | 140.7
3574.1 | 3353.1 | -6.4 | 0 | 0 | 133.9 | 129.2 | 118.1 | 120 | 141.5 | 28.7 | 20.7 | 45.2 | 3.5 | 240.4 | 5.9 | 426.6 | 426.1 | 124.1 | 51.3 | 524 | 523.9 | 83.7 | 63.2 | 206.8 | 373 | 166.3 | 128.8 | 261.5 | 125.4 | 110.1 | 376.7 | 206.7 | 150.1 | 131.6 | 124.7 | 139.1 | 139 | 124 | 132.7 | 140.6
3575.1 | 3354.1 | -6.4 | 0 | 0 | 133.7 | 129.2 | 118.1 | 119.9 | 141.7 | 28.7 | 20.7 | 45.2 | 3 | 247.1 | 5.6 | 426.6 | 426 | 123.7 | 51.3 | 524.1 | 523.8 | 83.7 | 63.2 | 206.6 | 372.8 | 165.9 | 128.9 | 261.3 | 125.3 | 110.4 | 376.2 | 206.5 | 150 | 131.5 | 124.7 | 139 | 138.9 | 123.9 | 132.6 | 140.5
3576.1 | 3355.1 | -6.3 | 0 | 0 | 133.4 | 129.2 | 118.1 | 119.7 | 141.7 | 28.7 | 20.7 | 45.2 | 2.9 | 253.1 | 5.3 | 426.6 | 425.9 | 123 | 51.2 | 524.1 | 523.5 | 83.5 | 63 | 206.5 | 372.6 | 166.4 | 129.1 | 261 | 125.2 | 110.9 | 375.8 | 206.4 | 149.9 | 131.5 | 124.6 | 138.9 | 138.9 | 123.8 | 132.5 | 140.4
3577.1 | 3356.1 | -5.7 | 0 | 0 | 133.3 | 129.1 | 118 | 119.6 | 141.6 | 28.7 | 20.7 | 45.2 | 3.2 | 255.7 | 5.2 | 426.5 | 425.9 | 122.7 | 51.1 | 524.1 | 523.3 | 83.5 | 62.7 | 206.3 | 372.3 | 167 | 129.3 | 260.8 | 125.1 | 110.7 | 375.3 | 206.5 | 149.8 | 131.5 | 124.5 | 138.8 | 138.8 | 123.7 | 132.4 | 140.4
3578.1 | 3357.1 | -5.5 | 0 | 0 | 133.2 | 129 | 118 | 119.4 | 141.7 | 28.7 | 20.7 | 45.2 | 3.5 | 260.3 | 5.1 | 426.5 | 425.8 | 123.1 | 51.1 | 524.1 | 523.1 | 83.5 | 62.5 | 206.2 | 372.2 | 167.4 | 129.1 | 260.5 | 125.2 | 110.4 | 374.9 | 206.3 | 149.7 | 131.4 | 124.4 | 138.8 | 138.7 | 123.6 | 132.3 | 140.3
3579.1 | 3358.1 | -5.8 | 0 | 0 | 133.3 | 129 | 117.9 | 119.3 | 141.6 | 28.6 | 20.7 | 45.2 | 3.1 | 249.3 | 4.9 | 426.5 | 425.8 | 123.2 | 51 | 524.1 | 522.9 | 83.3 | 62.4 | 206.1 | 372 | 167.2 | 129.1 | 260.2 | 125.2 | 110.4 | 374.5 | 206.1 | 149.6 | 131.4 | 124.3 | 138.7 | 138.7 | 123.6 | 132.2 | 140.2
3580.1 | 3359.1 | -5.1 | 0 | 0 | 133.2 | 128.9 | 117.9 | 119.2 | 141.1 | 28.6 | 20.7 | 45.2 | 3.3 | 245.5 | 4.9 | 426.5 | 425.8 | 121.6 | 50.9 | 524.1 | 522.7 | 84 | 62.2 | 206 | 371.8 | 166.6 | 129.2 | 260 | 125.2 | 110.2 | 374 | 205.7 | 149.5 | 131.3 | 124.2 | 138.6 | 138.6 | 123.6 | 132.1 | 140.1
3581.1 | 3360.1 | -5.3 | 0 | 0 | 132.9 | 128.9 | 117.9 | 119.2 | 140.7 | 28.6 | 20.7 | 45.3 | 3.1 | 235.2 | 4.7 | 426.4 | 425.7 | 120.8 | 50.9 | 524.1 | 522.7 | 84.6 | 62.2 | 206 | 371.6 | 166.6 | 129.2 | 259.8 | 125.1 | 110 | 373.6 | 205.5 | 149.4 | 131.3 | 124.2 | 138.5 | 138.6 | 123.5 | 132 | 140
3582.1 | 3361.1 | -5.9 | 0 | 0 | 132.8 | 128.9 | 117.9 | 119.2 | 140.4 | 28.6 | 20.7 | 45.3 | 3.4 | 232.2 | 4.3 | 426.4 | 425.8 | 121.3 | 51 | 524 | 522.5 | 84.7 | 62.4 | 205.9 | 371.4 | 166.5 | 128.9 | 259.5 | 125 | 109.8 | 373.1 | 205.3 | 149.3 | 131.2 | 124.1 | 138.5 | 138.5 | 123.4 | 131.9 | 139.9
3583.1 | 3362.1 | -5.8 | 0 | 0 | 132.7 | 128.8 | 117.9 | 119.2 | 140.4 | 28.6 | 20.8 | 45.3 | 3.1 | 250.7 | 3.9 | 426.4 | 425.7 | 120.9 | 51.2 | 523.9 | 522.3 | 84.6 | 62.8 | 205.9 | 371.3 | 167 | 128.9 | 259.3 | 125 | 109.7 | 372.7 | 205.3 | 149.2 | 131.1 | 124 | 138.4 | 138.4 | 123.2 | 131.9 | 139.8
3584.1 | 3363.1 | -5.5 | 0 | 0 | 132.6 | 128.8 | 117.9 | 119.1 | 140.3 | 28.6 | 20.7 | 45.3 | 3 | 270.8 | 3.7 | 426.3 | 425.6 | 121.4 | 51.2 | 523.9 | 522.2 | 84.6 | 63.1 | 205.9 | 371.1 | 167 | 128.8 | 259 | 125.1 | 109.7 | 372.2 | 205.2 | 149.1 | 131.1 | 123.9 | 138.3 | 138.3 | 123.1 | 131.7 | 139.7
3585.1 | 3364.1 | -5.8 | 0 | 0 | 132.5 | 128.7 | 117.7 | 119.1 | 139.9 | 28.6 | 20.8 | 45.3 | 3.3 | 265.5 | 3.3 | 426.3 | 425.6 | 120.9 | 51.3 | 523.8 | 522.1 | 85.1 | 63.4 | 205.9 | 370.9 | 167.2 | 128.8 | 258.8 | 125 | 109.7 | 371.8 | 205.1 | 149 | 131.1 | 123.8 | 138.2 | 138.2 | 123 | 131.7 | 139.7
3586.1 | 3365.1 | -6.2 | 0 | 0 | 132.4 | 128.7 | 117.6 | 119.1 | 139.6 | 28.6 | 20.8 | 45.3 | 3 | 239.3 | 3.2 | 426.3 | 425.6 | 120.6 | 51.4 | 523.8 | 521.9 | 85 | 63.7 | 205.9 | 370.7 | 167.2 | 128.9 | 258.5 | 124.8 | 109.6 | 371.3 | 204.9 | 148.9 | 131.1 | 123.7 | 138.1 | 138.1 | 122.9 | 131.6 | 139.6
3587.1 | 3366.1 | -5.9 | 0 | 0 | 132.4 | 128.5 | 117.5 | 119.1 | 139.7 | 28.6 | 20.8 | 45.3 | 3.3 | 216.9 | 3.5 | 426.3 | 425.5 | 121 | 51.5 | 523.7 | 521.7 | 85.9 | 63.9 | 205.9 | 370.5 | 167.5 | 129.1 | 258.2 | 124.9 | 109.8 | 370.9 | 204.6 | 148.8 | 131 | 123.6 | 138.1 | 138 | 122.8 | 131.6 | 139.5
3588.1 | 3367.1 | -5.4 | 0 | 0 | 132.4 | 128.3 | 117.4 | 119.1 | 139.9 | 28.6 | 20.7 | 45.3 | 3.2 | 225.6 | 3.9 | 426.2 | 425.5 | 120.4 | 51.5 | 523.6 | 521.5 | 85.7 | 64.2 | 205.9 | 370.4 | 167.8 | 129.2 | 257.9 | 124.8 | 109.7 | 370.4 | 204.4 | 148.7 | 131 | 123.5 | 138 | 137.9 | 122.7 | 131.5 | 139.4
3589.1 | 3368.1 | -5.3 | 0 | 0 | 132.4 | 128.2 | 117.3 | 119 | 140.1 | 28.7 | 20.8 | 45.3 | 3.1 | 222.3 | 4 | 426.2 | 425.5 | 119.3 | 51.5 | 523.6 | 521.3 | 86.2 | 64.4 | 205.8 | 370.2 | 168 | 129.3 | 257.7 | 124.5 | 110 | 370 | 204.4 | 148.6 | 130.9 | 123.5 | 137.9 | 137.8 | 122.6 | 131.4 | 139.3
3590.1 | 3369.1 | -5.5 | 0 | 0 | 132.3 | 128.1 | 117.2 | 118.8 | 140.1 | 28.7 | 20.8 | 45.3 | 3.3 | 217.2 | 4 | 426.2 | 425.4 | 118.7 | 51.5 | 523.5 | 521.3 | 85.9 | 64.6 | 205.8 | 370 | 168.1 | 129.5 | 257.4 | 124.3 | 110.1 | 369.6 | 204.3 | 148.5 | 130.8 | 123.4 | 137.8 | 137.7 | 122.6 | 131.3 | 139.2
3591.1 | 3370.1 | -6 | 0 | 0 | 132.3 | 128 | 117.2 | 118.5 | 140.1 | 28.7 | 20.8 | 45.3 | 2.9 | 230.3 | 4 | 426.1 | 425.4 | 118.9 | 51.6 | 523.5 | 521.3 | 85.6 | 64.7 | 205.8 | 369.9 | 167.7 | 129.4 | 257.2 | 124.2 | 109.8 | 369.2 | 204.1 | 148.4 | 130.7 | 123.3 | 137.8 | 137.6 | 122.5 | 131.2 | 139.2
3592.1 | 3371.1 | -6.1 | 0 | 0 | 132.3 | 127.8 | 117.1 | 118.4 | 140.2 | 28.7 | 20.8 | 45.3 | 3 | 237.3 | 3.9 | 426.1 | 425.4 | 119 | 51.6 | 523.4 | 521.1 | 85.2 | 64.6 | 205.9 | 369.7 | 167.4 | 129.5 | 256.9 | 124.1 | 109.8 | 368.7 | 203.9 | 148.3 | 130.6 | 123.2 | 137.7 | 137.5 | 122.4 | 131.2 | 139.1
3593.1 | 3372.1 | -6.5 | 0 | 0 | 132.3 | 127.6 | 117 | 118.4 | 140.2 | 28.7 | 20.8 | 45.2 | 3 | 226.3 | 3.7 | 426.1 | 425.3 | 118.7 | 51.6 | 523.5 | 521 | 84.8 | 64.6 | 205.8 | 369.5 | 166.9 | 129.5 | 256.7 | 123.8 | 109.8 | 368.3 | 203.6 | 148.2 | 130.5 | 123.1 | 137.6 | 137.3 | 122.3 | 131.1 | 139
3594.1 | 3373.1 | -6.7 | 0 | 0 | 132.2 | 127.6 | 117 | 118.3 | 140.1 | 28.7 | 20.8 | 45.2 | 3.2 | 218.9 | 3.7 | 426 | 425.3 | 118.5 | 51.6 | 523.5 | 521.2 | 84.7 | 64.8 | 205.9 | 369.3 | 165.9 | 129.4 | 256.5 | 123.9 | 109.9 | 367.9 | 203.5 | 148.2 | 130.5 | 123.1 | 137.6 | 137.2 | 122.2 | 130.9 | 138.9
3595.1 | 3374.1 | -6.7 | 0 | 0 | 132 | 127.7 | 116.9 | 118.1 | 140.1 | 28.7 | 20.8 | 45.1 | 3 | 218.8 | 3.6 | 426 | 425.3 | 119.4 | 51.6 | 523.5 | 521.6 | 84.5 | 64.7 | 205.8 | 369.1 | 165.9 | 129.5 | 256.2 | 124.4 | 109.7 | 367.5 | 203.5 | 148 | 130.4 | 123.1 | 137.5 | 137.1 | 122.2 | 130.8 | 138.8
3596.1 | 3375.1 | -6.7 | 0 | 0 | 131.8 | 127.7 | 116.8 | 118 | 140.1 | 28.8 | 20.8 | 45.1 | 3 | 219.9 | 3.3 | 426 | 425.3 | 120 | 51.6 | 523.6 | 521.8 | 83.8 | 64.8 | 205.8 | 369 | 166.2 | 129.3 | 256 | 124.3 | 109.7 | 367.1 | 203.5 | 148 | 130.3 | 123 | 137.3 | 137.1 | 122.1 | 130.7 | 138.7
3597.1 | 3376.1 | -6.7 | 0 | 0 | 131.8 | 127.7 | 116.7 | 117.9 | 139.8 | 28.8 | 20.8 | 45.1 | 3.2 | 221.1 | 3.4 | 426 | 425.2 | 119.3 | 51.6 | 523.7 | 521.8 | 83.3 | 64.8 | 205.8 | 368.8 | 165.9 | 129.1 | 255.7 | 124.2 | 109.5 | 366.7 | 203.1 | 147.9 | 130.2 | 122.9 | 137.2 | 137 | 122 | 130.7 | 138.7
3598.1 | 3377.1 | -6.7 | 0 | 0 | 131.7 | 127.5 | 116.6 | 117.9 | 139.6 | 28.8 | 20.8 | 45 | 3.4 | 224.6 | 3.4 | 425.9 | 425.2 | 119.4 | 51.6 | 523.7 | 521.9 | 83 | 64.7 | 205.8 | 368.6 | 165.9 | 129 | 255.5 | 124.4 | 109.5 | 366.2 | 203 | 147.8 | 130.1 | 122.8 | 137.1 | 136.9 | 121.9 | 130.6 | 138.6
3599.1 | 3378.1 | -6.7 | 0 | 0 | 131.6 | 127.4 | 116.6 | 117.9 | 139.5 | 28.8 | 20.8 | 45 | 3.5 | 231.4 | 3.3 | 425.9 | 425.1 | 119.5 | 51.6 | 523.8 | 521.9 | 82.9 | 64.6 | 205.8 | 368.5 | 166 | 128.8 | 255.3 | 124.4 | 109.5 | 365.8 | 202.8 | 147.7 | 130.1 | 122.7 | 137.1 | 136.8 | 121.8 | 130.5 | 138.5
3600.1 | 3379.1 | -6.7 | 0 | 0 | 131.6 | 127.4 | 116.4 | 117.9 | 139.4 | 28.8 | 20.8 | 45 | 3.1 | 236.8 | 3 | 425.9 | 425.1 | 119.6 | 51.7 | 523.8 | 521.8 | 83.1 | 64.6 | 205.7 | 368.3 | 166.1 | 128.8 | 255.1 | 124.4 | 109.4 | 365.4 | 202.9 | 147.6 | 130 | 122.6 | 137 | 136.7 | 121.7 | 130.5 | 138.4
3601.1 | 3380.1 | -6.6 | 0 | 0 | 131.4 | 127.4 | 116.2 | 117.9 | 139.1 | 28.7 | 20.8 | 44.9 | 3 | 237.5 | 3 | 425.8 | 425 | 119.9 | 51.7 | 523.8 | 521.8 | 82.8 | 64.8 | 205.6 | 368.1 | 165.9 | 128.6 | 254.8 | 124.3 | 109.5 | 365 | 203 | 147.5 | 129.9 | 122.5 | 136.9 | 136.6 | 121.6 | 130.4 | 138.3
3602.1 | 3381.1 | -6.6 | 0 | 0 | 131.3 | 127.4 | 116.1 | 117.8 | 139 | 28.7 | 20.8 | 44.9 | 3.2 | 236.2 | 2.9 | 425.8 | 425 | 119.6 | 51.6 | 523.9 | 521.9 | 82.6 | 65 | 205.7 | 367.9 | 165.4 | 128.8 | 254.6 | 124.5 | 109.5 | 364.6 | 202.9 | 147.4 | 129.8 | 122.4 | 136.8 | 136.5 | 121.6 | 130.3 | 138.2
3603.1 | 3382.1 | -6.7 | 0 | 0 | 131.3 | 127.3 | 116.1 | 117.7 | 139.1 | 28.7 | 20.8 | 44.9 | 3.1 | 235 | 2.7 | 425.8 | 425 | 119.6 | 51.5 | 523.9 | 522.1 | 82.2 | 65.1 | 205.6 | 367.8 | 164.5 | 128.7 | 254.4 | 124.5 | 109.6 | 364.2 | 202.7 | 147.3 | 129.7 | 122.4 | 136.8 | 136.5 | 121.5 | 130.2 | 138.1
3604.1 | 3383.1 | -6.8 | 0 | 0 | 131.3 | 127.2 | 116 | 117.6 | 139 | 28.8 | 20.8 | 44.8 | 3.1 | 229.3 | 2.5 | 425.8 | 424.9 | 120.6 | 51.5 | 523.9 | 522.2 | 81.7 | 65.1 | 205.5 | 367.6 | 163.7 | 128.7 | 254.2 | 124.4 | 109.6 | 363.8 | 202.4 | 147.3 | 129.5 | 122.3 | 136.6 | 136.4 | 121.5 | 130.1 | 138.1
3605.1 | 3384.1 | -6.8 | 0 | 0 | 131.3 | 127 | 116 | 117.5 | 138.9 | 28.7 | 20.8 | 44.8 | 2.9 | 223.9 | 2.6 | 425.7 | 424.9 | 120.5 | 51.7 | 524 | 522.2 | 81 | 65 | 205.6 | 367.4 | 163.9 | 128.5 | 254 | 124.4 | 109.4 | 363.4 | 202.5 | 147.2 | 129.4 | 122.2 | 136.6 | 136.3 | 121.4 | 130 | 138
3606.1 | 3385.1 | -6.8 | 0 | 0 | 131.2 | 126.9 | 115.9 | 117.4 | 138.8 | 28.7 | 20.8 | 44.8 | 3 | 232.8 | 2.8 | 425.7 | 424.8 | 119.5 | 52 | 524 | 522 | 80.4 | 65 | 205.6 | 367.3 | 164 | 128.4 | 253.7 | 124.3 | 109.6 | 363 | 202.4 | 147.1 | 129.3 | 122.1 | 136.5 | 136.2 | 121.3 | 129.9 | 137.9
3607.1 | 3386.1 | -6.8 | 0 | 0 | 131.2 | 126.8 | 115.8 | 117.3 | 138.4 | 28.7 | 20.8 | 44.8 | 3.2 | 242.8 | 3.1 | 425.7 | 424.9 | 118.5 | 52.2 | 524 | 522.6 | 80 | 65.2 | 205.5 | 367.1 | 163.5 | 128.6 | 253.5 | 124.3 | 109.9 | 362.5 | 202.4 | 147 | 129.2 | 122.1 | 136.4 | 136.1 | 121.2 | 129.9 | 137.8
3608.1 | 3387.1 | -6.8 | 0 | 0 | 131.2 | 126.7 | 115.8 | 117.1 | 138.2 | 28.7 | 20.8 | 44.8 | 3.1 | 245.1 | 3.5 | 425.6 | 424.8 | 117.5 | 52.3 | 523.9 | 523.5 | 79.9 | 65.4 | 205.5 | 366.9 | 162.6 | 128.8 | 253.3 | 124.7 | 110.4 | 362.1 | 202.4 | 147 | 129.1 | 122.1 | 136.4 | 136.1 | 121.1 | 129.8 | 137.7
3609.1 | 3388.1 | -6.8 | 0 | 0 | 131.1 | 126.6 | 115.7 | 117.1 | 138 | 28.6 | 20.8 | 44.7 | 2.7 | 244.2 | 3.7 | 425.6 | 424.7 | 116.6 | 52.5 | 523.8 | 524 | 80.3 | 65.7 | 205.5 | 366.7 | 162.2 | 128.8 | 253 | 124.6 | 110.4 | 361.7 | 202.2 | 146.9 | 129.1 | 121.9 | 136.3 | 136 | 121 | 129.7 | 137.6
3610.1 | 3389.1 | -6.7 | 0 | 0 | 131 | 126.4 | 115.7 | 117.1 | 137.6 | 28.6 | 20.8 | 44.7 | 2.8 | 245.3 | 3.4 | 425.6 | 424.7 | 116 | 52.5 | 523.7 | 524.6 | 80.8 | 66.1 | 205.4 | 366.5 | 162 | 128.7 | 252.8 | 124.6 | 110.4 | 361.2 | 202.1 | 146.8 | 129 | 121.8 | 136.2 | 135.9 | 121 | 129.7 | 137.6
3611.1 | 3390.1 | -6.7 | 0 | 0 | 130.9 | 126.3 | 115.6 | 117 | 137.3 | 28.6 | 20.8 | 44.6 | 3 | 251.8 | 3.1 | 425.6 | 424.7 | 116.5 | 52.6 | 523.6 | 525.1 | 81.4 | 66.4 | 205.4 | 366.3 | 162.3 | 128.9 | 252.5 | 124.5 | 110.3 | 360.8 | 202.1 | 146.7 | 128.9 | 121.7 | 136.2 | 135.8 | 120.9 | 129.6 | 137.5
3612.1 | 3391.1 | -6.8 | 0 | 0 | 130.7 | 126.3 | 115.6 | 116.9 | 137.2 | 28.5 | 20.8 | 44.6 | 2.8 | 263.3 | 3.1 | 425.6 | 424.6 | 115.5 | 52.6 | 523.6 | 525.3 | 81.3 | 66.4 | 205.4 | 366.2 | 162 | 128.8 | 252.3 | 124.4 | 110.5 | 360.4 | 201.9 | 146.6 | 128.8 | 121.6 | 136.1 | 135.7 | 120.8 | 129.6 | 137.4
3613.1 | 3392.1 | -6.8 | 0 | 0 | 130.6 | 126.2 | 115.5 | 116.8 | 137 | 28.5 | 20.8 | 44.6 | 2.7 | 260.6 | 3.1 | 425.5 | 424.6 | 115.3 | 52.6 | 523.5 | 525.8 | 81.3 | 66.3 | 205.3 | 366 | 161.7 | 128.8 | 252.1 | 124.3 | 110.6 | 360 | 201.7 | 146.5 | 128.8 | 121.6 | 136 | 135.6 | 120.7 | 129.5 | 137.3
3614.1 | 3393.1 | -6.7 | 0 | 0 | 130.5 | 126.1 | 115.4 | 116.8 | 136.6 | 28.4 | 20.8 | 44.6 | 3.1 | 228 | 3 | 425.5 | 424.6 | 114.3 | 52.4 | 523.3 | 526 | 81.6 | 66.3 | 205.3 | 365.8 | 161.6 | 128.9 | 251.8 | 124.2 | 110.8 | 359.5 | 201.5 | 146.5 | 128.6 | 121.5 | 136 | 135.5 | 120.5 | 129.4 | 137.3
3615.1 | 3394.1 | -6.8 | 0 | 0 | 130.3 | 126 | 115.4 | 116.7 | 136.5 | 28.4 | 20.8 | 44.5 | 2.9 | 211.7 | 3.2 | 425.5 | 424.5 | 113.2 | 52.1 | 523.2 | 526.2 | 82.6 | 66.2 | 205.2 | 365.6 | 161.4 | 129 | 251.6 | 124.1 | 110.9 | 359.1 | 201.6 | 146.3 | 128.5 | 121.4 | 135.9 | 135.4 | 120.4 | 129.3 | 137.2
3616.1 | 3395.1 | -6.8 | 0 | 0 | 130.2 | 125.9 | 115.4 | 116.7 | 136.4 | 28.4 | 20.8 | 44.5 | 3.1 | 236 | 3.4 | 425.4 | 424.5 | 112.6 | 52 | 523.1 | 526.8 | 82.8 | 66.1 | 205.1 | 365.4 | 161.7 | 129.2 | 251.4 | 124 | 110.9 | 358.7 | 201.6 | 146.2 | 128.3 | 121.4 | 135.8 | 135.3 | 120.3 | 129.2 | 137.1
3617.1 | 3396.1 | -6.7 | 0 | 0 | 130.1 | 125.8 | 115.4 | 116.6 | 136.5 | 28.3 | 20.8 | 44.5 | 3 | 256 | 3.6 | 425.4 | 424.4 | 112.9 | 51.8 | 522.9 | 527.1 | 83.7 | 66 | 205 | 365.3 | 161.7 | 129.3 | 251.1 | 123.9 | 111.3 | 358.3 | 201.7 | 146.2 | 128.3 | 121.3 | 135.7 | 135.2 | 120.3 | 129.1 | 137
3618.1 | 3397.1 | -6.6 | 0 | 0 | 130 | 125.8 | 115.3 | 116.6 | 136.5 | 28.3 | 20.8 | 44.4 | 3.2 | 238.5 | 4.1 | 425.4 | 424.4 | 113.3 | 51.6 | 522.8 | 527 | 84.3 | 66 | 204.9 | 365.1 | 161.6 | 129.3 | 250.9 | 123.8 | 111.3 | 357.8 | 201.6 | 146.1 | 128.2 | 121.2 | 135.7 | 135.1 | 120.3 | 129 | 136.9
3619.1 | 3398.1 | -6.5 | 0 | 0 | 129.9 | 125.7 | 115.3 | 116.5 | 136.7 | 28.3 | 20.8 | 44.4 | 3.3 | 235 | 4.3 | 425.4 | 424.4 | 113.6 | 51.4 | 522.7 | 526.9 | 84.7 | 66 | 204.9 | 364.9 | 161.6 | 129.3 | 250.7 | 123.7 | 111.4 | 357.4 | 201.4 | 146 | 128.1 | 121.1 | 135.6 | 135.1 | 120.2 | 128.9 | 136.8
3620.1 | 3399.1 | -6.6 | 0 | 0 | 129.9 | 125.6 | 115.2 | 116.5 | 136.9 | 28.3 | 20.8 | 44.4 | 3 | 259.4 | 3.9 | 425.4 | 424.4 | 114.1 | 51.4 | 522.6 | 526.9 | 85.2 | 66.1 | 204.8 | 364.7 | 162.3 | 129.3 | 250.4 | 123.6 | 111.4 | 357 | 201.1 | 145.9 | 128.1 | 121.1 | 135.5 | 135 | 120.1 | 128.8 | 136.8
3621.1 | 3400.1 | -6.6 | 0 | 0 | 130 | 125.6 | 115.2 | 116.4 | 137 | 28.3 | 20.8 | 44.4 | 2.9 | 272.5 | 3.4 | 425.4 | 424.4 | 114 | 51.4 | 522.5 | 527.1 | 85.2 | 66.2 | 204.7 | 364.6 | 162 | 129.2 | 250.2 | 123.5 | 111.2 | 356.6 | 200.9 | 145.8 | 128 | 120.9 | 135.4 | 134.8 | 120 | 128.8 | 136.7
3622.1 | 3401.1 | -6.6 | 0 | 0 | 129.8 | 125.5 | 115.2 | 116.4 | 137 | 28.2 | 20.8 | 44.4 | 3.2 | 259.5 | 3.1 | 425.3 | 424.3 | 113.3 | 51.5 | 522.4 | 527 | 85.5 | 66.3 | 204.7 | 364.4 | 161.7 | 129.2 | 250 | 123.2 | 111.2 | 356.1 | 200.8 | 145.7 | 127.9 | 120.9 | 135.2 | 134.7 | 119.9 | 128.7 | 136.6
3623.1 | 3402.1 | -6.6 | 0 | 0 | 129.7 | 125.3 | 115.1 | 116.3 | 137 | 28.2 | 20.8 | 44.4 | 3.1 | 236.3 | 3.3 | 425.3 | 424.3 | 112.2 | 51.6 | 522.3 | 527.1 | 85.6 | 66.5 | 204.7 | 364.2 | 161.6 | 129.6 | 249.8 | 122.9 | 111.8 | 355.7 | 200.9 | 145.7 | 127.9 | 120.9 | 135.2 | 134.7 | 119.9 | 128.6 | 136.5
3624.1 | 3403.1 | -6.7 | 0 | 0 | 129.6 | 125.2 | 115 | 116.3 | 137.1 | 28.3 | 20.8 | 44.4 | 3.1 | 226.4 | 3.5 | 425.3 | 424.3 | 111 | 51.7 | 522.2 | 527.4 | 85.7 | 66.6 | 204.7 | 364 | 161.5 | 129.8 | 249.6 | 122.6 | 111.7 | 355.3 | 201.1 | 145.5 | 127.8 | 120.8 | 135.1 | 134.6 | 119.8 | 128.5 | 136.4
3625.1 | 3404.1 | -6.8 | 0 | 0 | 129.6 | 125.1 | 114.9 | 116.2 | 137.2 | 28.3 | 20.8 | 44.4 | 3 | 233.6 | 3.5 | 425.3 | 424.2 | 110.4 | 51.6 | 522.2 | 527.4 | 85.2 | 66.6 | 204.7 | 363.8 | 161 | 129.6 | 249.4 | 122.7 | 111.7 | 354.9 | 201.1 | 145.5 | 127.7 | 120.8 | 135 | 134.5 | 119.8 | 128.5 | 136.4
3626.1 | 3405.1 | -6.7 | 0 | 0 | 129.5 | 125 | 114.7 | 116.2 | 137.2 | 28.2 | 20.8 | 44.4 | 2.9 | 239.2 | 3.6 | 425.3 | 424.2 | 110.3 | 51.5 | 522.1 | 527.3 | 84.9 | 66.6 | 204.7 | 363.7 | 161.1 | 129.6 | 249.1 | 122.6 | 111.4 | 354.4 | 200.7 | 145.4 | 127.6 | 120.7 | 134.9 | 134.4 | 119.7 | 128.5 | 136.3
3627.1 | 3406.1 | -6.8 | 0 | 0 | 129.4 | 125 | 114.6 | 116.1 | 136.9 | 28.2 | 20.8 | 44.4 | 3.1 | 238.1 | 3.5 | 425.2 | 424.2 | 110.9 | 51.4 | 522.1 | 528.1 | 84.7 | 66.7 | 204.7 | 363.5 | 161.2 | 129.6 | 248.9 | 122.4 | 111.1 | 354 | 200.5 | 145.4 | 127.5 | 120.6 | 134.9 | 134.3 | 119.6 | 128.5 | 136.2
3628.1 | 3407.1 | -6.8 | 0 | 0 | 129.3 | 124.9 | 114.4 | 116.1 | 136.6 | 28.2 | 20.8 | 44.4 | 2.9 | 231.7 | 3.3 | 425.2 | 424.2 | 110.5 | 51.4 | 522 | 528.8 | 84.9 | 66.8 | 204.6 | 363.3 | 160.9 | 129.8 | 248.7 | 122.3 | 111.1 | 353.6 | 200.4 | 145.3 | 127.5 | 120.5 | 134.8 | 134.2 | 119.5 | 128.4 | 136.1
3629.1 | 3408.1 | -6.8 | 0 | 0 | 129.1 | 124.8 | 114.4 | 116.1 | 136.4 | 28.2 | 20.8 | 44.4 | 2.9 | 230.3 | 3 | 425.2 | 424 | 109.8 | 51.4 | 521.9 | 529 | 85.2 | 66.9 | 204.6 | 363.1 | 161 | 129.9 | 248.5 | 122.1 | 111.6 | 353.2 | 200.3 | 145.2 | 127.4 | 120.4 | 134.7 | 134.2 | 119.5 | 128.4 | 136.1
3630.1 | 3409.1 | -6.8 | 0 | 0 | 129 | 124.7 | 114.3 | 116.1 | 136.2 | 28.2 | 20.8 | 44.3 | 3 | 232.7 | 2.8 | 425.2 | 424 | 110 | 51.4 | 521.9 | 528.9 | 85 | 66.8 | 204.6 | 362.9 | 160.8 | 130 | 248.3 | 121.7 | 112 | 352.7 | 200.2 | 145.1 | 127.3 | 120.4 | 134.6 | 134 | 119.4 | 128.3 | 136
3631.1 | 3410.1 | -6.8 | 0 | 0 | 129 | 124.7 | 114.1 | 116 | 136.1 | 28.2 | 20.8 | 44.3 | 2.9 | 234.3 | 2.8 | 425.2 | 424 | 109.5 | 51.5 | 521.9 | 528.8 | 84.3 | 66.7 | 204.5 | 362.8 | 161 | 129.9 | 248 | 121.4 | 112.1 | 352.3 | 200.2 | 145 | 127.2 | 120.3 | 134.5 | 134 | 119.3 | 128.2 | 135.9
3632.1 | 3411.1 | -6.8 | 0 | 0 | 128.9 | 124.7 | 114 | 115.8 | 136.3 | 28.2 | 20.8 | 44.3 | 2.9 | 242.3 | 3.1 | 425.1 | 424 | 110 | 51.5 | 522 | 528.4 | 84.3 | 66.5 | 204.5 | 362.6 | 161.2 | 129.6 | 247.8 | 121.4 | 112 | 351.9 | 200.2 | 145 | 127.1 | 120.2 | 134.4 | 133.8 | 119.3 | 128.2 | 135.8
3633.1 | 3412.1 | -6.7 | 0 | 0 | 128.8 | 124.7 | 114 | 115.7 | 136.4 | 28.2 | 20.8 | 44.3 | 3 | 262.3 | 3.4 | 425.1 | 424 | 111.3 | 51.4 | 522 | 527.8 | 84.6 | 66.4 | 204.5 | 362.4 | 161.4 | 129.2 | 247.6 | 121.7 | 112.1 | 351.4 | 200.1 | 144.9 | 127 | 120.1 | 134.4 | 133.7 | 119.2 | 128.1 | 135.7
3634.1 | 3413.1 | -6.8 | 0 | 0 | 128.8 | 124.6 | 114 | 115.5 | 136.2 | 28.2 | 20.8 | 44.3 | 3.1 | 259.7 | 3.5 | 425.1 | 424 | 111.9 | 51.3 | 522.1 | 527.2 | 84.5 | 66.3 | 204.4 | 362.2 | 161.9 | 128.8 | 247.3 | 121.6 | 111.9 | 351 | 199.9 | 144.8 | 127 | 120 | 134.3 | 133.6 | 119.1 | 128 | 135.7
3635.1 | 3414.1 | -6.7 | 0 | 0 | 128.8 | 124.6 | 113.9 | 115.4 | 135.9 | 28.2 | 20.8 | 44.3 | 3.1 | 247.7 | 3.4 | 425.1 | 423.9 | 112.3 | 51.3 | 522.1 | 526.7 | 84.4 | 66.4 | 204.4 | 362 | 161.4 | 128.5 | 247.1 | 121.6 | 111.6 | 350.6 | 199.6 | 144.7 | 126.9 | 120 | 134.2 | 133.5 | 119 | 127.9 | 135.6
3636.1 | 3415.1 | -6.7 | 0 | 0 | 128.8 | 124.5 | 113.9 | 115.3 | 135.6 | 28.2 | 20.8 | 44.3 | 2.9 | 241.9 | 3.3 | 425 | 423.8 | 111.6 | 51.2 | 522.1 | 526.3 | 85 | 66.6 | 204.3 | 361.8 | 161.1 | 128.2 | 246.9 | 121.5 | 111.3 | 350.1 | 199.3 | 144.6 | 126.8 | 119.9 | 134.1 | 133.5 | 118.9 | 127.8 | 135.5
3637.1 | 3416.1 | -6.7 | 0 | 0 | 128.7 | 124.4 | 113.8 | 115.3 | 135.3 | 28.2 | 20.8 | 44.3 | 3.1 | 234.9 | 2.9 | 425 | 423.9 | 111.5 | 51.3 | 522 | 525.9 | 85.5 | 66.9 | 204.2 | 361.6 | 161.1 | 127.9 | 246.7 | 121.3 | 111.2 | 349.7 | 199.1 | 144.5 | 126.7 | 119.8 | 134.1 | 133.4 | 118.9 | 127.7 | 135.4
3638.1 | 3417.1 | -6.1 | 0 | 0 | 128.6 | 124.3 | 113.8 | 115.2 | 135.2 | 28.2 | 20.8 | 44.2 | 3 | 226.3 | 2.8 | 425 | 423.9 | 111 | 51.3 | 522 | 525.7 | 84.9 | 66.9 | 204.2 | 361.4 | 161.1 | 127.6 | 246.5 | 121.2 | 111 | 349.3 | 198.9 | 144.5 | 126.5 | 119.7 | 134 | 133.3 | 118.8 | 127.6 | 135.4
3639.1 | 3418.1 | -6.1 | 0 | 0 | 128.7 | 124.2 | 113.7 | 115.2 | 135.2 | 28.3 | 20.8 | 44.2 | 2.9 | 216.3 | 2.9 | 425 | 423.8 | 111 | 51.4 | 521.9 | 525.7 | 85.1 | 66.9 | 204.2 | 361.2 | 161 | 127.7 | 246.3 | 121.1 | 110.9 | 348.8 | 198.8 | 144.4 | 126.4 | 119.7 | 133.9 | 133.2 | 118.7 | 127.6 | 135.3
3640.1 | 3419.1 | -5.8 | 0 | 0 | 128.6 | 124.1 | 113.6 | 115.1 | 135.3 | 28.3 | 20.8 | 44.2 | 3.2 | 208.9 | 3.1 | 424.9 | 423.8 | 111.2 | 51.4 | 522 | 525.8 | 84.7 | 66.8 | 204.2 | 361 | 160.4 | 127.6 | 246 | 120.9 | 110.7 | 348.4 | 198.7 | 144.3 | 126.2 | 119.5 | 133.8 | 133.1 | 118.6 | 127.5 | 135.2
3641.1 | 3420.1 | -6.3 | 0 | 0 | 128.6 | 124 | 113.5 | 115.1 | 135.2 | 28.3 | 20.8 | 44.2 | 3 | 215 | 3.1 | 424.9 | 423.7 | 112 | 51.3 | 522 | 525.6 | 84.1 | 66.6 | 204.3 | 360.8 | 159.9 | 127.2 | 245.8 | 120.8 | 110.6 | 348 | 198.7 | 144.2 | 126.1 | 119.4 | 133.7 | 133 | 118.5 | 127.4 | 135.1
3642.1 | 3421.1 | -6.6 | 0 | 0 | 128.6 | 123.8 | 113.4 | 115.1 | 134.9 | 28.3 | 20.8 | 44.2 | 3 | 231 | 3 | 424.9 | 423.7 | 113 | 51.2 | 522.1 | 525.1 | 83.6 | 66.3 | 204.3 | 360.6 | 159.8 | 126.8 | 245.5 | 120.6 | 110.4 | 347.5 | 198.5 | 144.1 | 126 | 119.4 | 133.7 | 132.9 | 118.5 | 127.3 | 135
3643.1 | 3422.1 | -6.7 | 0 | 0 | 128.5 | 123.7 | 113.4 | 115 | 134.8 | 28.3 | 20.8 | 44.2 | 3.1 | 226.2 | 3.1 | 424.8 | 423.7 | 112.9 | 51.2 | 522.2 | 524.7 | 83.5 | 66.1 | 204.3 | 360.4 | 159.4 | 126.6 | 245.3 | 120.3 | 110.1 | 347.1 | 198.3 | 144.1 | 126 | 119.3 | 133.6 | 132.8 | 118.4 | 127.2 | 135
3644.1 | 3423.1 | -6.8 | 0 | 0 | 128.5 | 123.6 | 113.4 | 114.9 | 134.7 | 28.3 | 20.8 | 44.2 | 3 | 213.4 | 3 | 424.8 | 423.6 | 113.5 | 51.3 | 522.3 | 524.5 | 82.7 | 66.1 | 204.2 | 360.2 | 159.4 | 126.3 | 245.1 | 120.3 | 110 | 346.7 | 198.1 | 144 | 125.9 | 119.2 | 133.5 | 132.8 | 118.3 | 127.1 | 134.9
3645.1 | 3424.1 | -6.8 | 0 | 0 | 128.3 | 123.5 | 113.4 | 114.8 | 134.6 | 28.3 | 20.8 | 44.2 | 3.1 | 215.1 | 2.9 | 424.8 | 423.7 | 113.2 | 51.4 | 522.4 | 524.4 | 83.4 | 66 | 204.2 | 360 | 159.2 | 126.2 | 244.8 | 120.2 | 109.7 | 346.2 | 198 | 143.9 | 125.9 | 119.1 | 133.5 | 132.7 | 118.2 | 127 | 134.8
3646.1 | 3425.1 | -6.8 | 0 | 0 | 128.1 | 123.4 | 113.3 | 114.7 | 134.3 | 28.3 | 20.8 | 44.2 | 2.9 | 214 | 2.6 | 424.8 | 423.6 | 112.2 | 51.4 | 522.3 | 524.2 | 83.5 | 66.2 | 204.2 | 359.8 | 159.2 | 126.2 | 244.6 | 120.3 | 109.5 | 345.8 | 197.8 | 143.8 | 125.8 | 119 | 133.4 | 132.6 | 118.1 | 127 | 134.7
3647.1 | 3426.1 | -6.8 | 0 | 0 | 127.9 | 123.2 | 113.2 | 114.6 | 133.9 | 28.3 | 20.8 | 44.2 | 2.9 | 221 | 2.2 | 424.7 | 423.6 | 112.3 | 51.4 | 522.2 | 523.9 | 83.4 | 66.2 | 204.2 | 359.6 | 159.1 | 126.2 | 244.4 | 120.4 | 109.1 | 345.4 | 197.7 | 143.7 | 125.8 | 119 | 133.3 | 132.5 | 118.1 | 126.9 | 134.7
3648.1 | 3427.1 | -6.8 | 0 | 0 | 127.9 | 123.1 | 113.2 | 114.5 | 133.5 | 28.3 | 20.8 | 44.2 | 2.9 | 242.6 | 2.1 | 424.7 | 423.5 | 112.2 | 51.2 | 522.2 | 524 | 83.5 | 66.1 | 204.2 | 359.4 | 159.3 | 126 | 244.1 | 120.3 | 108.7 | 345 | 197.6 | 143.6 | 125.8 | 118.9 | 133.2 | 132.4 | 118 | 126.9 | 134.6
3649.1 | 3428.1 | -6.8 | 0 | 0 | 127.9 | 123.1 | 113.2 | 114.5 | 133.6 | 28.3 | 20.8 | 44.2 | 2.8 | 269.5 | 2.8 | 424.7 | 423.5 | 113 | 51.2 | 522.1 | 524 | 83.4 | 66 | 204.3 | 359.2 | 158.9 | 125.7 | 243.9 | 120.1 | 108.6 | 344.5 | 197.5 | 143.5 | 125.7 | 118.8 | 133.1 | 132.4 | 117.9 | 126.8 | 134.5
3650.1 | 3429.1 | -6.8 | 0 | 0 | 127.9 | 123.1 | 113.1 | 114.5 | 133.7 | 28.3 | 20.8 | 44.2 | 2.8 | 261.6 | 3.4 | 424.6 | 423.5 | 112.8 | 50.9 | 522.1 | 524 | 83.6 | 66 | 204.3 | 359 | 158.1 | 125.6 | 243.6 | 119.9 | 108.5 | 344.1 | 197.3 | 143.4 | 125.6 | 118.8 | 133 | 132.3 | 117.9 | 126.7 | 134.4
3651.1 | 3430.1 | -6.8 | 0 | 0 | 127.7 | 123.1 | 113 | 114.5 | 133.8 | 28.3 | 20.8 | 44.2 | 2.9 | 261.1 | 3.9 | 424.6 | 423.4 | 111.9 | 50.8 | 522 | 524.2 | 83.2 | 65.9 | 204.2 | 358.8 | 157.4 | 125.8 | 243.4 | 120 | 108.7 | 343.7 | 197.2 | 143.3 | 125.6 | 118.7 | 132.9 | 132.2 | 117.7 | 126.6 | 134.3
3652.1 | 3431.1 | -6.7 | 0 | 0 | 127.6 | 123 | 112.9 | 114.4 | 133.7 | 28.3 | 20.8 | 44.2 | 3.1 | 278.1 | 4.3 | 424.6 | 423.4 | 111 | 50.6 | 521.9 | 524.2 | 83.2 | 66 | 204.2 | 358.6 | 157.6 | 125.8 | 243.1 | 120.2 | 108.4 | 343.2 | 197.1 | 143.2 | 125.6 | 118.6 | 132.8 | 132.1 | 117.6 | 126.5 | 134.2
3653.1 | 3432.1 | -6.6 | 0 | 0 | 127.5 | 123 | 112.8 | 114.2 | 133.6 | 28.4 | 20.8 | 44.2 | 3.3 | 262.9 | 4.7 | 424.6 | 423.4 | 110.3 | 50.5 | 521.9 | 524.2 | 83.9 | 65.9 | 204.2 | 358.4 | 157.7 | 125.8 | 242.9 | 120 | 108.1 | 342.8 | 196.8 | 143.2 | 125.6 | 118.5 | 132.8 | 132 | 117.5 | 126.4 | 134.2
3654.1 | 3433.1 | -6.7 | 0 | 0 | 127.4 | 122.9 | 112.7 | 114.1 | 133.5 | 28.4 | 20.8 | 44.1 | 2.9 | 244.7 | 4.9 | 424.5 | 423.4 | 109.3 | 50.5 | 521.8 | 524.4 | 84.5 | 65.9 | 204.1 | 358.2 | 157.8 | 125.6 | 242.7 | 120 | 108 | 342.4 | 196.8 | 143.1 | 125.5 | 118.4 | 132.7 | 131.8 | 117.4 | 126.3 | 134.1
3655.1 | 3434.1 | -6.8 | 0 | 0 | 127.3 | 122.9 | 112.6 | 113.9 | 133.4 | 28.4 | 20.8 | 44.1 | 3 | 252.3 | 4.5 | 424.5 | 423.3 | 110.2 | 50.2 | 521.6 | 524.6 | 84.5 | 65.9 | 204 | 358.1 | 157.5 | 125.5 | 242.5 | 119.7 | 107.6 | 342 | 196.8 | 143 | 125.4 | 118.3 | 132.6 | 131.8 | 117.4 | 126.2 | 134
3656.1 | 3435.1 | -6.8 | 0 | 0 | 127.2 | 122.8 | 112.5 | 113.8 | 133.2 | 28.3 | 20.8 | 44.1 | 3.2 | 260.4 | 4.4 | 424.5 | 423.4 | 111.2 | 50.1 | 521.5 | 524.8 | 84.7 | 66 | 203.9 | 357.9 | 157.4 | 125.3 | 242.3 | 119.3 | 107.2 | 341.5 | 196.6 | 142.9 | 125.4 | 118.3 | 132.5 | 131.7 | 117.2 | 126 | 133.9
3657.1 | 3436.1 | -6.8 | 0 | 0 | 127.2 | 122.8 | 112.4 | 113.7 | 133.2 | 28.3 | 20.8 | 44.1 | 3.4 | 263.5 | 4.3 | 424.4 | 423.3 | 111.3 | 50 | 521.4 | 524.8 | 85.7 | 66.1 | 203.9 | 357.7 | 156.9 | 125.3 | 242 | 118.9 | 106.9 | 341.1 | 196.5 | 142.8 | 125.3 | 118.2 | 132.5 | 131.6 | 117.1 | 125.9 | 133.9
3658.1 | 3437.1 | -6.8 | 0 | 0 | 127.1 | 122.7 | 112.4 | 113.6 | 133.4 | 28.3 | 20.8 | 44 | 3.5 | 261.3 | 4.3 | 424.4 | 423.3 | 112 | 50 | 521.4 | 524.6 | 85.9 | 66.2 | 203.9 | 357.5 | 156.6 | 125.1 | 241.8 | 118.7 | 106.5 | 340.7 | 196.3 | 142.7 | 125.3 | 118.1 | 132.4 | 131.5 | 117 | 125.8 | 133.8
3659.1 | 3438.1 | -6.8 | 0 | 0 | 126.9 | 122.6 | 112.3 | 113.5 | 133.1 | 28.3 | 20.8 | 44 | 3.4 | 261.7 | 4.3 | 424.4 | 423.2 | 111.9 | 49.9 | 521.3 | 524.3 | 85.6 | 66.4 | 203.8 | 357.3 | 156.2 | 125.1 | 241.6 | 118.5 | 106.4 | 340.3 | 196.1 | 142.7 | 125.2 | 118.1 | 132.3 | 131.4 | 116.9 | 125.8 | 133.7
3660.1 | 3439.1 | -6.8 | 0 | 0 | 126.9 | 122.6 | 112.3 | 113.5 | 132.9 | 28.3 | 20.8 | 44 | 3.2 | 262.7 | 4.3 | 424.4 | 423.2 | 110.7 | 49.9 | 521.3 | 524 | 85.8 | 66.3 | 203.8 | 357.2 | 156.3 | 124.9 | 241.4 | 118.4 | 106.7 | 339.8 | 195.8 | 142.6 | 125.2 | 118 | 132.2 | 131.3 | 116.9 | 125.7 | 133.6
3661.1 | 3440.1 | -6.8 | 0 | 0 | 126.9 | 122.6 | 112.3 | 113.4 | 132.7 | 28.3 | 20.8 | 44 | 3.1 | 261.2 | 4.1 | 424.3 | 423.2 | 109.9 | 49.9 | 521.2 | 523.8 | 86.5 | 66.4 | 203.7 | 357 | 157.1 | 124.9 | 241.1 | 118.3 | 107 | 339.4 | 195.8 | 142.5 | 125.2 | 117.9 | 132.2 | 131.2 | 116.8 | 125.6 | 133.5
3662.1 | 3441.1 | -6.8 | 0 | 0 | 126.9 | 122.5 | 112.2 | 113.2 | 132.5 | 28.3 | 20.8 | 44 | 3 | 255 | 4 | 424.3 | 423.1 | 109.5 | 50 | 521.1 | 523.5 | 86.2 | 66.8 | 203.6 | 356.8 | 157 | 124.8 | 240.9 | 118 | 106.7 | 339 | 195.7 | 142.3 | 125.1 | 117.8 | 132.1 | 131.1 | 116.7 | 125.5 | 133.4
3663.1 | 3442.1 | -6.8 | 0 | 0 | 126.8 | 122.3 | 112.1 | 113.1 | 132.4 | 28.3 | 20.8 | 43.9 | 2.9 | 252 | 3.9 | 424.3 | 423.1 | 109.1 | 50.1 | 521 | 523.1 | 86.5 | 66.8 | 203.6 | 356.7 | 156.7 | 124.8 | 240.6 | 117.9 | 106.3 | 338.5 | 195.5 | 142.3 | 125 | 117.7 | 132.1 | 131.1 | 116.8 | 125.4 | 133.3
3664.1 | 3443.1 | -6.8 | 0 | 0 | 126.7 | 122.1 | 112 | 113.1 | 132.1 | 28.2 | 20.9 | 43.9 | 2.8 | 252.1 | 4 | 424.2 | 423 | 108.1 | 50.2 | 520.9 | 522.8 | 87 | 66.6 | 203.6 | 356.5 | 156.9 | 124.6 | 240.4 | 117.5 | 106 | 338.1 | 195.4 | 142.1 | 124.9 | 117.6 | 132 | 131 | 116.6 | 125.4 | 133.3
3665.1 | 3444.1 | -6.8 | 0 | 0 | 126.5 | 121.8 | 111.8 | 113 | 132 | 28.2 | 20.9 | 43.9 | 2.8 | 256.3 | 4 | 424.2 | 423 | 107.4 | 50.4 | 520.9 | 522.9 | 87 | 66.3 | 203.6 | 356.3 | 157.2 | 124.6 | 240.2 | 117.3 | 105.8 | 337.6 | 195.5 | 142.1 | 124.7 | 117.5 | 131.9 | 130.9 | 116.5 | 125.3 | 133.2
3666.1 | 3445.1 | -6.8 | 0 | 0 | 126.3 | 121.7 | 111.7 | 113 | 132.3 | 28.2 | 20.8 | 43.9 | 2.9 | 259.6 | 3.6 | 424.2 | 423 | 107.5 | 50.4 | 520.8 | 523 | 86.6 | 66.2 | 203.5 | 356.2 | 157.3 | 124.4 | 239.9 | 117 | 105.6 | 337.2 | 195.5 | 142 | 124.6 | 117.4 | 131.7 | 130.8 | 116.5 | 125.3 | 133.1
3667.1 | 3446.1 | -6.8 | 0 | 0 | 126.2 | 121.7 | 111.6 | 112.9 | 132.5 | 28.2 | 20.8 | 43.9 | 3.1 | 263.9 | 3.4 | 424.2 | 423 | 107.5 | 50.3 | 520.8 | 522.7 | 86.5 | 66.3 | 203.6 | 356 | 157.1 | 124.3 | 239.7 | 116.8 | 105.3 | 336.8 | 195.3 | 141.8 | 124.5 | 117.3 | 131.7 | 130.7 | 116.4 | 125.2 | 133
3668.1 | 3447.1 | -6.7 | 0 | 0 | 126.2 | 121.7 | 111.5 | 112.8 | 132.7 | 28.1 | 20.8 | 43.9 | 3.2 | 263.7 | 3.4 | 424.1 | 423 | 107.8 | 50 | 520.8 | 522.4 | 86.8 | 66.1 | 203.6 | 355.8 | 157 | 124.1 | 239.4 | 116.7 | 105.2 | 336.3 | 195.1 | 141.8 | 124.4 | 117.1 | 131.6 | 130.6 | 116.3 | 125.1 | 133
3669.1 | 3448.1 | -6.8 | 0 | 0 | 126.2 | 121.7 | 111.3 | 112.7 | 133 | 28.1 | 20.8 | 43.9 | 3 | 262.7 | 3.5 | 424.1 | 422.9 | 107.1 | 49.8 | 520.8 | 522 | 86.2 | 65.7 | 203.6 | 355.7 | 157.4 | 124 | 239.2 | 116.6 | 105.2 | 335.9 | 194.9 | 141.7 | 124.3 | 117 | 131.5 | 130.5 | 116.2 | 125.1 | 132.9
3670.1 | 3449.1 | -6.8 | 0 | 0 | 126.1 | 121.7 | 111.2 | 112.7 | 133.1 | 28 | 20.8 | 43.9 | 3.3 | 262.6 | 3.5 | 424.1 | 422.9 | 107.5 | 49.7 | 520.8 | 521.5 | 85.2 | 65.4 | 203.6 | 355.5 | 157.6 | 123.8 | 238.9 | 116.6 | 104.8 | 335.4 | 194.7 | 141.6 | 124.2 | 117 | 131.5 | 130.4 | 116.1 | 125 | 132.8
3671.1 | 3450.1 | -6.8 | 0 | 0 | 126 | 121.7 | 111.1 | 112.6 | 133.2 | 28.1 | 20.8 | 43.9 | 2.9 | 263.5 | 3.4 | 424.1 | 422.9 | 108.9 | 49.8 | 520.9 | 521 | 84.2 | 65.2 | 203.5 | 355.3 | 157.6 | 123.5 | 238.6 | 116.3 | 104.6 | 335 | 194.6 | 141.5 | 124.1 | 116.9 | 131.4 | 130.3 | 116 | 124.9 | 132.7
3672.1 | 3451.1 | -6.8 | 0 | 0 | 125.8 | 121.7 | 111 | 112.5 | 133.2 | 28.1 | 20.9 | 43.9 | 3 | 269.1 | 3.3 | 424 | 422.9 | 110.2 | 49.8 | 521 | 520.6 | 84.3 | 64.8 | 203.5 | 355.1 | 157.6 | 123.1 | 238.4 | 116.2 | 104.6 | 334.5 | 194.5 | 141.4 | 124 | 116.8 | 131.3 | 130.2 | 116 | 124.8 | 132.6
3673.1 | 3452.1 | -6.8 | 0 | 0 | 125.7 | 121.7 | 110.9 | 112.3 | 133.2 | 28.1 | 20.9 | 43.9 | 3.1 | 268.4 | 3.1 | 424 | 422.9 | 111.1 | 49.8 | 521.2 | 520.3 | 83.5 | 64.5 | 203.6 | 355 | 157.3 | 122.7 | 238.2 | 116.3 | 104.6 | 334.1 | 194.3 | 141.3 | 124 | 116.7 | 131.3 | 130.2 | 115.9 | 124.7 | 132.5
3674.1 | 3453.1 | -6.8 | 0 | 0 | 125.6 | 121.7 | 110.9 | 112.2 | 133.2 | 28.1 | 20.9 | 43.9 | 3.2 | 268.4 | 2.9 | 424 | 422.8 | 111.4 | 49.8 | 521.3 | 520.1 | 82.8 | 64.3 | 203.6 | 354.8 | 157.3 | 122.4 | 238 | 116.7 | 104.2 | 333.6 | 194.2 | 141.2 | 123.8 | 116.6 | 131.2 | 130.1 | 115.9 | 124.6 | 132.5
3675.1 | 3454.1 | -6.8 | 0 | 0 | 125.5 | 121.7 | 110.8 | 112 | 133 | 28.1 | 20.8 | 43.9 | 3.3 | 268.3 | 2.9 | 424 | 422.8 | 110.6 | 49.8 | 521.4 | 520.2 | 82.1 | 64.2 | 203.7 | 354.6 | 157.9 | 122.2 | 237.7 | 116.7 | 104.1 | 333.2 | 194.1 | 141.1 | 123.7 | 116.6 | 131.1 | 129.9 | 115.8 | 124.5 | 132.4
3676.1 | 3455.1 | -6.8 | 0 | 0 | 125.4 | 121.7 | 110.6 | 111.9 | 132.5 | 28.1 | 20.8 | 43.8 | 3.3 | 260.6 | 2.9 | 423.9 | 422.7 | 110.5 | 50 | 521.4 | 520.3 | 81.4 | 64.1 | 203.7 | 354.4 | 158 | 121.9 | 237.5 | 116.4 | 104 | 332.7 | 194.1 | 141.1 | 123.6 | 116.5 | 131 | 129.9 | 115.8 | 124.4 | 132.3
3677.1 | 3456.1 | -6.8 | 0 | 0 | 125.3 | 121.6 | 110.5 | 111.8 | 132 | 28.1 | 20.8 | 43.8 | 3 | 236.4 | 2.8 | 423.9 | 422.7 | 109.9 | 50.1 | 521.5 | 520.7 | 80.7 | 64.2 | 203.7 | 354.2 | 157.9 | 121.7 | 237.3 | 116.3 | 103.8 | 332.3 | 194 | 141 | 123.6 | 116.4 | 130.9 | 129.8 | 115.7 | 124.4 | 132.2
3678.1 | 3457.1 | -6.8 | 0 | 0 | 125.2 | 121.4 | 110.4 | 111.8 | 131.6 | 28.1 | 20.8 | 43.8 | 2.8 | 223 | 2.8 | 423.9 | 422.7 | 109.9 | 50.1 | 521.5 | 520.7 | 80 | 64.2 | 203.7 | 353.9 | 158 | 121.6 | 237 | 116.1 | 103.7 | 331.9 | 194 | 140.9 | 123.5 | 116.3 | 130.9 | 129.7 | 115.6 | 124.3 | 132.2
3679.1 | 3458.1 | -6.8 | 0 | 0 | 125.1 | 121.2 | 110.4 | 111.8 | 131.6 | 28.2 | 20.8 | 43.8 | 3 | 224 | 2.8 | 423.9 | 422.7 | 109.6 | 50.2 | 521.6 | 520.5 | 79 | 64.2 | 203.7 | 353.7 | 158 | 121.4 | 236.8 | 115.9 | 103.9 | 331.4 | 193.9 | 140.8 | 123.4 | 116.3 | 130.8 | 129.6 | 115.5 | 124.3 | 132.1
3680.1 | 3459.1 | -6.8 | 0 | 0 | 125.1 | 121.1 | 110.3 | 111.7 | 131.4 | 28.2 | 20.9 | 43.8 | 2.9 | 224.5 | 2.8 | 423.9 | 422.6 | 108.8 | 50.2 | 521.6 | 520.4 | 78.6 | 64.3 | 203.7 | 353.5 | 157.8 | 121.3 | 236.5 | 115.7 | 103.9 | 331 | 193.8 | 140.8 | 123.2 | 116.2 | 130.7 | 129.5 | 115.4 | 124.2 | 132
3681.1 | 3460.1 | -6.8 | 0 | 0 | 125 | 121 | 110.3 | 111.6 | 131.1 | 28.2 | 20.8 | 43.8 | 3.2 | 226 | 2.8 | 423.8 | 422.6 | 108.5 | 50.1 | 521.6 | 520.2 | 78.8 | 64.3 | 203.7 | 353.3 | 157.4 | 121.3 | 236.3 | 115.5 | 103.9 | 330.5 | 193.6 | 140.7 | 123.1 | 116.2 | 130.7 | 129.4 | 115.3 | 124.1 | 131.9
3682.1 | 3461.1 | -6.8 | 0 | 0 | 124.9 | 120.9 | 110.3 | 111.5 | 130.9 | 28.2 | 20.8 | 43.8 | 3.2 | 231.6 | 2.6 | 423.8 | 422.5 | 107.2 | 50.1 | 521.6 | 520 | 78.6 | 64.2 | 203.7 | 353.1 | 156.6 | 121.4 | 236 | 115.6 | 104 | 330.1 | 193.3 | 140.6 | 123.1 | 116.1 | 130.6 | 129.3 | 115.2 | 124.1 | 131.8
3683.1 | 3462.1 | -6.8 | 0 | 0 | 124.9 | 120.9 | 110.3 | 111.4 | 130.8 | 28.2 | 20.9 | 43.8 | 3.1 | 232.3 | 2.5 | 423.8 | 422.5 | 106.2 | 50 | 521.5 | 519.9 | 78.6 | 64.3 | 203.7 | 352.9 | 156.7 | 121.1 | 235.8 | 115.5 | 103.9 | 329.6 | 193.2 | 140.5 | 123 | 116 | 130.5 | 129.2 | 115.1 | 124 | 131.8
3684.1 | 3463.1 | -6.8 | 0 | 0 | 124.9 | 120.8 | 110.2 | 111.2 | 130.6 | 28.2 | 20.8 | 43.8 | 3.1 | 228 | 2.3 | 423.7 | 422.5 | 105.8 | 50 | 521.5 | 520.3 | 79.1 | 64.4 | 203.6 | 352.7 | 156.8 | 121 | 235.5 | 115.3 | 103.9 | 329.2 | 193.1 | 140.4 | 122.9 | 115.9 | 130.5 | 129.1 | 115.1 | 123.9 | 131.7
3685.1 | 3464.1 | -6.8 | 0 | 0 | 124.9 | 120.8 | 110.1 | 111.1 | 130.5 | 28.1 | 20.9 | 43.8 | 3.4 | 223.5 | 2.2 | 423.7 | 422.5 | 106.3 | 49.8 | 521.4 | 520.7 | 79.3 | 64.4 | 203.7 | 352.5 | 156.5 | 120.9 | 235.3 | 115.1 | 103.7 | 328.7 | 192.9 | 140.3 | 122.9 | 115.9 | 130.4 | 129.1 | 115.1 | 123.8 | 131.6
3686.1 | 3465.1 | -6.8 | 0 | 0 | 124.8 | 120.7 | 110 | 110.9 | 130.4 | 28.1 | 20.9 | 43.8 | 3.2 | 229.8 | 2.1 | 423.7 | 422.4 | 106.8 | 49.8 | 521.3 | 520.9 | 79.6 | 64.3 | 203.6 | 352.3 | 156.3 | 120.8 | 235 | 115.1 | 103.6 | 328.3 | 192.8 | 140.2 | 122.9 | 115.8 | 130.3 | 129 | 115 | 123.7 | 131.5
3687.1 | 3466.1 | -6.8 | 0 | 0 | 124.8 | 120.7 | 109.9 | 110.8 | 130.4 | 28.1 | 20.9 | 43.8 | 3.3 | 246.9 | 2.3 | 423.7 | 422.3 | 106.6 | 49.7 | 521.3 | 520.9 | 79.3 | 64.1 | 203.6 | 352.1 | 156.5 | 120.7 | 234.8 | 115 | 103.8 | 327.8 | 192.8 | 140.1 | 122.8 | 115.8 | 130.3 | 128.9 | 114.9 | 123.7 | 131.5
3688.1 | 3467.1 | -6.7 | 0 | 0 | 124.7 | 120.7 | 109.8 | 110.7 | 130.1 | 28.1 | 20.8 | 43.8 | 3.1 | 245.2 | 2.5 | 423.6 | 422.3 | 106.1 | 49.6 | 521.3 | 520.7 | 78.8 | 63.9 | 203.6 | 351.9 | 156.2 | 120.6 | 234.6 | 114.9 | 103.7 | 327.4 | 192.8 | 140.1 | 122.8 | 115.7 | 130.2 | 128.9 | 114.8 | 123.6 | 131.4
3689.1 | 3468.1 | -6.6 | 0 | 0 | 124.4 | 120.7 | 109.7 | 110.6 | 129.8 | 28.1 | 20.8 | 43.8 | 2.8 | 236.8 | 2.7 | 423.6 | 422.3 | 106.6 | 49.5 | 521.4 | 520.4 | 78 | 63.8 | 203.6 | 351.7 | 156.7 | 120.5 | 234.3 | 114.9 | 103.6 | 326.9 | 192.8 | 140 | 122.7 | 115.6 | 130.1 | 128.8 | 114.8 | 123.5 | 131.3
3690.1 | 3469.1 | -6.6 | 0 | 0 | 124.2 | 120.6 | 109.6 | 110.6 | 129.5 | 28.1 | 20.9 | 43.7 | 2.8 | 234.1 | 2.6 | 423.6 | 422.3 | 107.2 | 49.4 | 521.4 | 520.3 | 77.5 | 63.4 | 203.6 | 351.5 | 156.8 | 120.6 | 234.1 | 115 | 103.4 | 326.5 | 192.5 | 139.9 | 122.6 | 115.6 | 130 | 128.7 | 114.7 | 123.4 | 131.2
3691.1 | 3470.1 | -6.7 | 0 | 0 | 124.1 | 120.6 | 109.6 | 110.5 | 129.5 | 28 | 20.9 | 43.7 | 2.8 | 234.7 | 2.6 | 423.5 | 422.3 | 108.7 | 49.3 | 521.4 | 520.3 | 77.2 | 63 | 203.7 | 351.3 | 156.8 | 120.4 | 233.9 | 115.2 | 103.2 | 326.1 | 192.4 | 139.8 | 122.5 | 115.5 | 130 | 128.6 | 114.6 | 123.3 | 131.1
3692.1 | 3471.1 | -6.7 | 0 | 0 | 124.1 | 120.6 | 109.5 | 110.4 | 129.6 | 28.1 | 20.9 | 43.7 | 2.7 | 246.2 | 2.5 | 423.5 | 422.3 | 109.7 | 49.4 | 521.5 | 520.5 | 77.4 | 62.9 | 203.6 | 351.1 | 156.7 | 120.2 | 233.7 | 115.3 | 103 | 325.6 | 192.1 | 139.7 | 122.4 | 115.4 | 129.9 | 128.5 | 114.5 | 123.2 | 131.1
3693.1 | 3472.1 | -6.8 | 0 | 0 | 124.1 | 120.6 | 109.5 | 110.3 | 129.8 | 28.1 | 20.9 | 43.7 | 2.8 | 247.6 | 2.7 | 423.5 | 422.2 | 109.3 | 49.4 | 521.5 | 520.9 | 77.8 | 63 | 203.6 | 350.9 | 156.4 | 120 | 233.4 | 115.3 | 103 | 325.2 | 192.1 | 139.7 | 122.3 | 115.3 | 129.8 | 128.4 | 114.4 | 123.2 | 131
3694.1 | 3473.1 | -6.8 | 0 | 0 | 124 | 120.5 | 109.5 | 110.2 | 129.8 | 28.1 | 20.9 | 43.7 | 3.2 | 234.7 | 2.9 | 423.5 | 422.1 | 108.9 | 49.4 | 521.6 | 521.3 | 78.1 | 63.1 | 203.7 | 350.7 | 156.2 | 119.9 | 233.2 | 115 | 102.8 | 324.7 | 192.1 | 139.6 | 122.4 | 115.3 | 129.8 | 128.3 | 114.3 | 123.1 | 130.9
3695.1 | 3474.1 | -6.8 | 0 | 0 | 123.9 | 120.5 | 109.4 | 110.2 | 129.8 | 28.1 | 20.9 | 43.7 | 3.1 | 226.6 | 2.7 | 423.4 | 422.1 | 109.5 | 49.3 | 521.6 | 521.5 | 77.7 | 63 | 203.6 | 350.5 | 156.1 | 119.8 | 233 | 115.2 | 102.8 | 324.3 | 191.9 | 139.5 | 122.3 | 115.2 | 129.8 | 128.2 | 114.3 | 123 | 130.8
3696.1 | 3475.1 | -6.7 | 0 | 0 | 123.8 | 120.4 | 109.3 | 110.2 | 129.7 | 28.1 | 20.9 | 43.7 | 2.9 | 229.9 | 2.9 | 423.4 | 422.1 | 110.3 | 49.3 | 521.7 | 521.5 | 77.5 | 63 | 203.6 | 350.3 | 155.8 | 119.8 | 232.7 | 115.5 | 102.5 | 323.8 | 191.7 | 139.4 | 122.3 | 115.1 | 129.7 | 128.1 | 114.2 | 122.9 | 130.8
3697.1 | 3476.1 | -6.8 | 0 | 0 | 123.8 | 120.1 | 109.2 | 110.2 | 129.7 | 28.1 | 20.9 | 43.7 | 2.8 | 236.5 | 3.1 | 423.4 | 422.1 | 109.5 | 49.2 | 521.8 | 521.4 | 78.1 | 62.8 | 203.6 | 350.1 | 155.3 | 119.6 | 232.5 | 115.3 | 102.6 | 323.4 | 191.4 | 139.3 | 122.2 | 115.1 | 129.6 | 128.1 | 114.1 | 122.9 | 130.7
3698.1 | 3477.1 | -6.8 | 0 | 0 | 123.8 | 119.8 | 109.1 | 110.2 | 129.8 | 28.1 | 20.9 | 43.7 | 2.9 | 244.1 | 3.3 | 423.4 | 422.1 | 109.2 | 49.2 | 521.9 | 521.4 | 79 | 62.6 | 203.3 | 349.9 | 154.9 | 119.3 | 232.3 | 115.2 | 102.4 | 322.9 | 191.2 | 139.2 | 122.2 | 115 | 129.5 | 128 | 114 | 122.8 | 130.6
3699.1 | 3478.1 | -6.8 | 0 | 0 | 123.7 | 119.5 | 109 | 110.1 | 129.5 | 28.1 | 20.9 | 43.7 | 3.1 | 239.5 | 3.4 | 423.3 | 422.1 | 110 | 49.4 | 521.9 | 521.5 | 78.3 | 62.5 | 203.3 | 349.7 | 155.2 | 118.9 | 232 | 115.3 | 102.4 | 322.5 | 191 | 139.2 | 122.1 | 115 | 129.4 | 128 | 113.9 | 122.8 | 130.6
3700.1 | 3479.1 | -6.8 | 0 | 0 | 123.7 | 119.5 | 109 | 110.1 | 129.4 | 28.1 | 20.9 | 43.7 | 3.1 | 222.4 | 3.1 | 423.3 | 422 | 109.9 | 49.3 | 522 | 521.8 | 78.2 | 62.4 | 203.2 | 349.5 | 155.3 | 119.1 | 231.8 | 116 | 102.2 | 322 | 190.9 | 139.1 | 122 | 114.9 | 129.4 | 127.9 | 113.8 | 122.7 | 130.5
3701.1 | 3480.1 | -6.8 | 0 | 0 | 123.5 | 119.4 | 109 | 110.1 | 129.5 | 28.1 | 20.9 | 43.7 | 3 | 199.4 | 2.9 | 423.3 | 422 | 110.3 | 49.2 | 522 | 522 | 78.8 | 62.4 | 203.1 | 349.3 | 155.9 | 119.1 | 231.5 | 115.9 | 102.1 | 321.6 | 191 | 139 | 121.9 | 114.8 | 129.2 | 127.8 | 113.7 | 122.6 | 130.4
3702.1 | 3481.1 | -6.7 | 0 | 0 | 123.3 | 119.4 | 109 | 110.1 | 129.7 | 28.1 | 20.9 | 43.7 | 2.8 | 194.4 | 2.7 | 423.2 | 422 | 111.3 | 49.2 | 522 | 521.9 | 78.2 | 62.2 | 203.1 | 349.1 | 156 | 118.6 | 231.3 | 115.7 | 101.7 | 321.1 | 190.8 | 138.9 | 121.8 | 114.7 | 129.1 | 127.8 | 113.7 | 122.6 | 130.3
3703.1 | 3482.1 | -6.5 | 0 | 0 | 123.1 | 119.3 | 109 | 110.1 | 129.9 | 28.1 | 20.9 | 43.7 | 2.8 | 221.6 | 2.4 | 423.2 | 421.9 | 111.8 | 49.2 | 522.1 | 521.8 | 78.2 | 61.9 | 203 | 348.9 | 155.9 | 118.1 | 231 | 115.6 | 101.6 | 320.6 | 190.5 | 138.9 | 121.7 | 114.6 | 129 | 127.7 | 113.7 | 122.6 | 130.3
3704.1 | 3483.1 | -6 | 0 | 0 | 123 | 119.3 | 108.9 | 110.1 | 130 | 28.1 | 20.9 | 43.6 | 2.9 | 246.5 | 2.2 | 423.2 | 421.9 | 112.2 | 49.2 | 522.2 | 521.9 | 78.7 | 61.7 | 202.9 | 348.8 | 155.3 | 117.8 | 230.8 | 115.4 | 101.3 | 320.2 | 190.3 | 138.8 | 121.6 | 114.5 | 129 | 127.6 | 113.6 | 122.5 | 130.2
3705.1 | 3484.1 | -5.8 | 0 | 0 | 123 | 119.4 | 108.7 | 110.1 | 130 | 28 | 20.9 | 43.6 | 3.1 | 258.2 | 2.3 | 423.1 | 421.8 | 110.9 | 49.1 | 522.2 | 521.8 | 79.5 | 61.5 | 202.9 | 348.6 | 154.7 | 117.5 | 230.6 | 115.1 | 101 | 319.7 | 190.3 | 138.7 | 121.5 | 114.4 | 128.9 | 127.5 | 113.5 | 122.4 | 130.1
3706.1 | 3485.1 | -5.9 | 0 | 0 | 122.8 | 119.3 | 108.6 | 110.1 | 130 | 28.1 | 20.9 | 43.6 | 3.4 | 255.2 | 2.3 | 423.1 | 421.8 | 109.6 | 49.1 | 522.2 | 521.6 | 80 | 61.3 | 202.9 | 348.4 | 154.1 | 117.4 | 230.4 | 114.9 | 100.6 | 319.3 | 190.2 | 138.6 | 121.4 | 114.4 | 128.9 | 127.5 | 113.5 | 122.3 | 130
3707.1 | 3486.1 | -6.2 | 0 | 0 | 122.6 | 119.3 | 108.6 | 109.9 | 129.8 | 28.1 | 20.9 | 43.6 | 2.9 | 240 | 2.4 | 423.1 | 421.8 | 109.4 | 49 | 522.3 | 521.3 | 80.1 | 61.3 | 202.6 | 348.2 | 154.5 | 117.2 | 230.2 | 114.6 | 100.5 | 318.8 | 190.2 | 138.5 | 121.2 | 114.3 | 128.8 | 127.4 | 113.4 | 122.3 | 130
3708.1 | 3487.1 | -6.3 | 0 | 0 | 122.4 | 119.3 | 108.5 | 109.8 | 130 | 28 | 20.9 | 43.6 | 3.3 | 215.9 | 2.6 | 423.1 | 421.7 | 109.9 | 48.9 | 522.4 | 520.9 | 80 | 61.2 | 202.6 | 348 | 154.1 | 117.1 | 229.9 | 114.2 | 100.3 | 318.4 | 189.8 | 138.4 | 121.1 | 114.3 | 128.7 | 127.3 | 113.3 | 122.2 | 129.9
3709.1 | 3488.1 | -6.2 | 0 | 0 | 122.4 | 119.2 | 108.5 | 109.6 | 130.2 | 28 | 20.9 | 43.6 | 3.4 | 208.3 | 3.1 | 423 | 421.7 | 110.5 | 48.8 | 522.5 | 520.9 | 79.5 | 61.2 | 202.7 | 347.8 | 154.2 | 116.9 | 229.7 | 114.1 | 100.1 | 317.9 | 189.8 | 138.4 | 121 | 114.2 | 128.6 | 127.2 | 113.2 | 122.1 | 129.8
3710.1 | 3489.1 | -6 | 0 | 0 | 122.4 | 119.2 | 108.5 | 109.5 | 130.3 | 27.9 | 20.9 | 43.6 | 3.5 | 212.2 | 3.2 | 423 | 421.6 | 111.2 | 48.8 | 522.7 | 520.9 | 79 | 61.3 | 202.5 | 347.7 | 153.9 | 116.6 | 229.5 | 113.9 | 100.1 | 317.4 | 189.8 | 138.3 | 120.9 | 114.1 | 128.5 | 127.1 | 113.2 | 122 | 129.7
3711.1 | 3490.1 | -5.5 | 0 | 0 | 122.5 | 119.2 | 108.4 | 109.4 | 130.3 | 27.9 | 20.9 | 43.6 | 3.3 | 232.4 | 3.1 | 423 | 421.6 | 111.4 | 48.8 | 522.8 | 520.8 | 79.1 | 61.4 | 202.4 | 347.5 | 153.2 | 116.5 | 229.2 | 113.9 | 100.2 | 317 | 189.5 | 138.2 | 120.8 | 114 | 128.5 | 127 | 113.1 | 121.9 | 129.7
3712.1 | 3491.1 | -6 | 0 | 0 | 122.4 | 119.1 | 108.4 | 109.3 | 130.1 | 27.8 | 20.9 | 43.6 | 3.3 | 244.8 | 3.1 | 422.9 | 421.6 | 111.2 | 48.8 | 522.7 | 520.8 | 80 | 61.5 | 202.5 | 347.3 | 152.3 | 116.6 | 229 | 113.8 | 100 | 316.5 | 189.4 | 138.1 | 120.8 | 114 | 128.4 | 127 | 113 | 121.9 | 129.6
3713.1 | 3492.1 | -6.6 | 0 | 0 | 122.2 | 119 | 108.3 | 109.2 | 129.8 | 27.8 | 20.9 | 43.5 | 3.2 | 214.6 | 3.4 | 422.9 | 421.5 | 111.5 | 48.9 | 522.7 | 521.1 | 79.7 | 61.5 | 202.5 | 347.1 | 152.1 | 116.5 | 228.7 | 113.6 | 100.1 | 316 | 189.3 | 138 | 120.7 | 113.9 | 128.4 | 126.9 | 113 | 121.9 | 129.5
3714.1 | 3493.1 | -6.8 | 0 | 0 | 122 | 118.9 | 108.3 | 109.1 | 129.4 | 27.7 | 20.9 | 43.5 | 3.2 | 206.7 | 4.3 | 422.9 | 421.5 | 111.1 | 48.9 | 522.7 | 521.5 | 79.5 | 61.5 | 202.5 | 346.9 | 152.4 | 116.4 | 228.5 | 113.8 | 100.2 | 315.6 | 189.2 | 138 | 120.7 | 113.8 | 128.3 | 126.8 | 112.9 | 121.8 | 129.4
3715.1 | 3494.1 | -6.7 | 0 | 0 | 121.7 | 118.8 | 108.2 | 108.9 | 129.1 | 27.7 | 20.9 | 43.5 | 2.9 | 210.3 | 5.1 | 422.8 | 421.5 | 112.1 | 48.8 | 522.7 | 521.7 | 79.5 | 61.2 | 202.6 | 346.8 | 152.3 | 116.4 | 228.2 | 114.3 | 100.1 | 315.1 | 188.9 | 137.9 | 120.6 | 113.7 | 128.2 | 126.7 | 112.8 | 121.8 | 129.4
3716.1 | 3495.1 | -6.2 | 0 | 0 | 121.4 | 118.8 | 108.2 | 108.8 | 129 | 27.6 | 20.9 | 43.4 | 2.8 | 209.3 | 5.3 | 422.8 | 421.5 | 113.5 | 48.8 | 522.7 | 521.6 | 78.8 | 61 | 202.5 | 346.6 | 152.2 | 116 | 228 | 114.2 | 100 | 314.6 | 188.7 | 137.8 | 120.5 | 113.6 | 128.1 | 126.7 | 112.8 | 121.7 | 129.3
3717.1 | 3496.1 | -6 | 0 | 0 | 121.4 | 118.9 | 108.1 | 108.7 | 129.2 | 27.6 | 20.9 | 43.4 | 2.9 | 218.3 | 4.7 | 422.8 | 421.4 | 114.4 | 48.9 | 522.8 | 521.2 | 79.7 | 61 | 202.6 | 346.4 | 152.3 | 115.9 | 227.8 | 114.2 | 100.1 | 314.1 | 188.5 | 137.7 | 120.5 | 113.5 | 128.1 | 126.6 | 112.7 | 121.6 | 129.2
3718.1 | 3497.1 | -6.2 | 0 | 0 | 121.3 | 118.9 | 108 | 108.7 | 129.4 | 27.6 | 20.9 | 43.4 | 3.1 | 235 | 4.2 | 422.7 | 421.4 | 115 | 48.9 | 522.8 | 520.9 | 80.5 | 61 | 202.6 | 346.2 | 152.8 | 115.8 | 227.5 | 114.1 | 100.3 | 313.6 | 188.3 | 137.6 | 120.4 | 113.4 | 128 | 126.5 | 112.6 | 121.6 | 129.1
3719.1 | 3498.1 | -6.5 | 0 | 0 | 121.2 | 118.7 | 107.8 | 108.6 | 129.3 | 27.6 | 20.9 | 43.3 | 3.3 | 247.3 | 3.7 | 422.7 | 421.3 | 115.4 | 49 | 522.8 | 520.8 | 80.9 | 61.1 | 202.7 | 346 | 152.9 | 115.7 | 227.3 | 114.1 | 100.2 | 313.1 | 188.1 | 137.6 | 120.4 | 113.4 | 128 | 126.4 | 112.6 | 121.5 | 129.1
3720.1 | 3499.1 | -6.7 | 0 | 0 | 121.1 | 118.5 | 107.7 | 108.6 | 129.2 | 27.6 | 20.9 | 43.3 | 3.2 | 231.3 | 3.5 | 422.7 | 421.3 | 114.8 | 49 | 522.7 | 520.8 | 81.4 | 61.3 | 202.7 | 345.8 | 153 | 115.8 | 227.1 | 113.8 | 100.4 | 312.6 | 188 | 137.4 | 120.3 | 113.3 | 127.9 | 126.3 | 112.5 | 121.3 | 129
3721.1 | 3500.1 | -6.8 | 0 | 0 | 121 | 118.4 | 107.6 | 108.6 | 129.1 | 27.6 | 20.9 | 43.3 | 3.3 | 212.8 | 3.6 | 422.6 | 421.2 | 113.9 | 48.9 | 522.7 | 520.9 | 81.6 | 61.5 | 202.7 | 345.6 | 153.5 | 116 | 226.8 | 113.4 | 100.7 | 312.1 | 188 | 137.4 | 120.1 | 113.2 | 127.8 | 126.2 | 112.4 | 121.2 | 128.9
3722.1 | 3501.1 | -6.8 | 0 | 0 | 121 | 118.4 | 107.5 | 108.5 | 129 | 27.6 | 20.9 | 43.2 | 3.4 | 218.7 | 3.6 | 422.6 | 421.2 | 114.2 | 49 | 522.6 | 521.1 | 81.1 | 61.6 | 202.8 | 345.4 | 153.4 | 116.1 | 226.6 | 113.1 | 100.4 | 311.6 | 187.9 | 137.2 | 120 | 113.1 | 127.7 | 126.1 | 112.3 | 121.1 | 128.8
3723.1 | 3502.1 | -6.8 | 0 | 0 | 121 | 118.3 | 107.4 | 108.5 | 129 | 27.6 | 20.9 | 43.2 | 3.6 | 233 | 3.9 | 422.6 | 421.2 | 115.1 | 48.9 | 522.6 | 521.1 | 80.5 | 61.9 | 202.7 | 345.2 | 153.7 | 115.9 | 226.4 | 113.3 | 100.4 | 311.2 | 187.6 | 137.2 | 119.9 | 113 | 127.6 | 126.1 | 112.3 | 121 | 128.8
3724.1 | 3503.1 | -6.8 | 0 | 0 | 120.9 | 118.3 | 107.4 | 108.4 | 129.1 | 27.6 | 20.9 | 43.2 | 3.7 | 212 | 4.6 | 422.5 | 421.2 | 114.6 | 48.8 | 522.6 | 520.9 | 80.4 | 62 | 202.6 | 345 | 153.6 | 115.8 | 226.1 | 113.2 | 100.6 | 310.7 | 187.6 | 137.1 | 119.7 | 113 | 127.6 | 126 | 112.2 | 120.9 | 128.7
3725.1 | 3504.1 | -6.7 | 0 | 0 | 120.8 | 118 | 107.3 | 108.4 | 129.2 | 27.6 | 20.9 | 43.1 | 3.5 | 212.6 | 5.6 | 422.5 | 421.1 | 114 | 48.8 | 522.6 | 520.6 | 81.3 | 62 | 202.5 | 344.8 | 153.5 | 115.8 | 225.9 | 113 | 100.6 | 310.2 | 187.6 | 137.1 | 119.5 | 112.9 | 127.5 | 125.9 | 112.1 | 120.9 | 128.6
3726.1 | 3505.1 | -6.8 | 0 | 0 | 120.7 | 117.9 | 107.2 | 108.3 | 129.4 | 27.6 | 20.9 | 43.1 | 3.6 | 206.3 | 5.8 | 422.5 | 421.1 | 114.9 | 48.8 | 522.6 | 520.4 | 80.9 | 61.9 | 202.5 | 344.6 | 153.6 | 115.7 | 225.6 | 113.1 | 100.6 | 309.6 | 187.3 | 137 | 119.4 | 112.8 | 127.4 | 125.8 | 112 | 120.8 | 128.5
3727.1 | 3506.1 | -6.8 | 0 | 0 | 120.7 | 117.9 | 107.1 | 108.3 | 129.5 | 27.6 | 20.9 | 43.1 | 3.3 | 200.2 | 5.2 | 422.4 | 421 | 115.6 | 48.8 | 522.6 | 520.6 | 80.2 | 61.8 | 202.5 | 344.4 | 154 | 115.9 | 225.4 | 113.1 | 100.6 | 309.1 | 187.3 | 136.9 | 119.4 | 112.7 | 127.3 | 125.7 | 111.9 | 120.7 | 128.4
3728.1 | 3507.1 | -6.8 | 0 | 0 | 120.6 | 117.8 | 107 | 108.2 | 129 | 27.6 | 20.9 | 43 | 3.2 | 231.5 | 4.3 | 422.4 | 421 | 114.5 | 48.9 | 522.6 | 520.8 | 79.7 | 61.7 | 202.4 | 344.2 | 153.6 | 115.9 | 225.2 | 113.3 | 100.5 | 308.6 | 187.3 | 136.8 | 119.4 | 112.7 | 127.3 | 125.6 | 111.8 | 120.6 | 128.4
3729.1 | 3508.1 | -6.8 | 0 | 0 | 120.4 | 117.7 | 106.9 | 108 | 128.4 | 27.5 | 20.9 | 43 | 3.1 | 243.8 | 4.4 | 422.3 | 420.9 | 113.4 | 48.9 | 522.6 | 521.6 | 79.8 | 61.7 | 202.3 | 344 | 153 | 115.8 | 225 | 113.3 | 100.5 | 308.1 | 187.3 | 136.7 | 119.3 | 112.6 | 127.2 | 125.5 | 111.7 | 120.5 | 128.3
3730.1 | 3509.1 | -6.6 | 0 | 0 | 120.3 | 117.6 | 106.8 | 107.9 | 128 | 27.5 | 20.9 | 43 | 3.1 | 231.2 | 4.8 | 422.3 | 420.9 | 112.5 | 48.9 | 522.5 | 522.2 | 79.8 | 61.6 | 202.3 | 343.8 | 152.1 | 116 | 224.8 | 113.2 | 100.5 | 307.6 | 187.3 | 136.7 | 119.2 | 112.6 | 127.1 | 125.4 | 111.7 | 120.4 | 128.2
3731.1 | 3510.1 | -6.7 | 0 | 0 | 120.2 | 117.5 | 106.8 | 107.8 | 127.6 | 27.6 | 20.9 | 42.9 | 3.7 | 261.6 | 4.6 | 422.3 | 420.9 | 111.4 | 48.9 | 522.4 | 522.4 | 80.4 | 61.5 | 202.3 | 343.6 | 151.9 | 116 | 224.5 | 113.1 | 100.3 | 307.1 | 187.2 | 136.6 | 119.1 | 112.5 | 127 | 125.3 | 111.6 | 120.4 | 128.1
3732.1 | 3511.1 | -6.7 | 0 | 0 | 120.2 | 117.5 | 106.8 | 107.7 | 127.5 | 27.6 | 20.9 | 42.9 | 3.3 | 268.9 | 4.3 | 422.2 | 420.9 | 110.6 | 48.9 | 522.2 | 522.5 | 81.8 | 61.6 | 202.3 | 343.4 | 151.9 | 116 | 224.3 | 112.9 | 100.3 | 306.6 | 187 | 136.5 | 119.1 | 112.4 | 127 | 125.2 | 111.5 | 120.3 | 128
3733.1 | 3512.1 | -6.6 | 0 | 0 | 120.2 | 117.4 | 106.8 | 107.6 | 127.3 | 27.6 | 20.9 | 42.9 | 3.3 | 230.8 | 4.5 | 422.2 | 420.9 | 109.3 | 48.9 | 522 | 522.5 | 82.2 | 61.9 | 202.2 | 343.2 | 151.5 | 116.1 | 224.1 | 112.6 | 100.3 | 306.1 | 186.9 | 136.4 | 118.9 | 112.4 | 126.9 | 125.2 | 111.4 | 120.1 | 128
3734.1 | 3513.1 | -6.6 | 0 | 0 | 120.1 | 117.3 | 106.7 | 107.5 | 127 | 27.6 | 20.9 | 42.9 | 3.2 | 236.9 | 5.2 | 422.2 | 420.8 | 109.3 | 48.9 | 521.9 | 522.5 | 83 | 62.1 | 202.1 | 343 | 151.2 | 116.2 | 223.9 | 112.2 | 100.2 | 305.5 | 186.7 | 136.4 | 118.9 | 112.3 | 126.8 | 125.1 | 111.3 | 120 | 127.9
3735.1 | 3514.1 | -6.3 | 0 | 0 | 120.1 | 117.2 | 106.6 | 107.5 | 126.9 | 27.6 | 20.9 | 42.9 | 3.2 | 258.7 | 5.3 | 422.1 | 420.8 | 109.4 | 48.9 | 521.8 | 522.5 | 82.9 | 62.4 | 202.1 | 342.9 | 150.8 | 116.2 | 223.7 | 112.2 | 100.1 | 305 | 186.8 | 136.3 | 118.8 | 112.3 | 126.8 | 125 | 111.2 | 119.9 | 127.8
3736.1 | 3515.1 | -6.2 | 0 | 0 | 120.1 | 117.1 | 106.6 | 107.5 | 127 | 27.6 | 20.9 | 42.9 | 3.2 | 238 | 5.5 | 422.1 | 420.7 | 108.4 | 49 | 521.7 | 522.5 | 83.8 | 62.6 | 202.1 | 342.7 | 150.7 | 116.2 | 223.4 | 112 | 100 | 304.5 | 186.8 | 136.2 | 118.7 | 112.2 | 126.7 | 124.9 | 111.1 | 119.8 | 127.8
3737.1 | 3516.1 | -6.2 | 0 | 0 | 120 | 117.1 | 106.5 | 107.4 | 127.1 | 27.6 | 20.9 | 42.9 | 2.9 | 233.7 | 6.7 | 422.1 | 420.6 | 107.7 | 49 | 521.6 | 522.4 | 83.5 | 62.8 | 202 | 342.5 | 150.8 | 116.3 | 223.2 | 111.8 | 99.9 | 303.9 | 186.8 | 136.2 | 118.6 | 112.1 | 126.6 | 124.9 | 111 | 119.7 | 127.7
3738.1 | 3517.1 | -6.4 | 0 | 0 | 119.9 | 117 | 106.4 | 107.4 | 127.1 | 27.6 | 20.9 | 42.8 | 3.4 | 230.5 | 7 | 422 | 420.6 | 107.6 | 49 | 521.5 | 522.3 | 82.7 | 62.9 | 202 | 342.3 | 150.4 | 116.1 | 223 | 111.8 | 99.8 | 303.4 | 186.6 | 136.1 | 118.5 | 112.1 | 126.5 | 124.8 | 111 | 119.7 | 127.6
3739.1 | 3518.1 | -6.5 | 0 | 0 | 119.8 | 116.9 | 106.3 | 107.3 | 127.3 | 27.7 | 20.9 | 42.8 | 3.4 | 241.6 | 7 | 422 | 420.6 | 108.2 | 49 | 521.4 | 522 | 81.5 | 62.9 | 201.9 | 342.2 | 150.2 | 116.1 | 222.8 | 111.6 | 99.9 | 302.8 | 186.6 | 136 | 118.3 | 112 | 126.5 | 124.7 | 110.8 | 119.7 | 127.5
3740.1 | 3519.1 | -6.3 | 0 | 0 | 119.8 | 116.8 | 106.2 | 107.2 | 127.4 | 27.7 | 20.9 | 42.7 | 3.2 | 231.3 | 7.1 | 422 | 420.6 | 108.7 | 48.9 | 521.4 | 521.7 | 80.5 | 62.8 | 201.9 | 342 | 149.7 | 116.1 | 222.6 | 111.3 | 99.6 | 302.3 | 186.4 | 136 | 118.3 | 111.9 | 126.4 | 124.6 | 110.7 | 119.6 | 127.5
3741.1 | 3520.1 | -6.3 | 0 | 0 | 119.7 | 116.5 | 106.2 | 107.2 | 127.4 | 27.7 | 20.9 | 42.6 | 3.2 | 237.8 | 7.1 | 421.9 | 420.5 | 109.2 | 48.8 | 521.4 | 521.5 | 79.6 | 62.8 | 201.9 | 341.8 | 149.4 | 116 | 222.4 | 111.1 | 99.5 | 301.8 | 186.2 | 135.9 | 118.2 | 111.9 | 126.4 | 124.5 | 110.7 | 119.4 | 127.4
3742.1 | 3521.1 | -6.4 | 0 | 0 | 119.6 | 116.3 | 106.2 | 107.3 | 126.9 | 27.7 | 20.9 | 42.6 | 3.6 | 236.3 | 6.8 | 421.9 | 420.5 | 108.7 | 48.8 | 521.4 | 521.3 | 79.3 | 62.9 | 201.9 | 341.6 | 149.1 | 116 | 222.1 | 110.9 | 99.4 | 301.2 | 186.2 | 135.9 | 118.1 | 111.8 | 126.3 | 124.4 | 110.6 | 119.4 | 127.3
3743.1 | 3522.1 | -6.6 | 0 | 0 | 119.5 | 116.3 | 106.1 | 107.3 | 126.7 | 27.7 | 20.9 | 42.5 | 3.4 | 224.4 | 6.5 | 421.9 | 420.5 | 108 | 48.8 | 521.3 | 521.2 | 80.2 | 63.1 | 201.8 | 341.5 | 148.4 | 116 | 221.9 | 110.7 | 99.1 | 300.6 | 186.1 | 135.7 | 118.2 | 111.8 | 126.2 | 124.3 | 110.5 | 119.3 | 127.2
3744.1 | 3523.1 | -6.7 | 0 | 0 | 119.4 | 116.4 | 106.1 | 107.3 | 126.6 | 27.7 | 20.9 | 42.5 | 3.4 | 215.2 | 5.8 | 421.8 | 420.4 | 107.2 | 48.7 | 521.3 | 521.5 | 80.5 | 63 | 201.7 | 341.3 | 148.1 | 116.1 | 221.7 | 110.4 | 99.2 | 300.1 | 186 | 135.7 | 118.2 | 111.7 | 126.1 | 124.3 | 110.5 | 119.2 | 127.2
3745.1 | 3524.1 | -6.8 | 0 | 0 | 119.2 | 116.4 | 106 | 107.2 | 126.6 | 27.7 | 20.9 | 42.4 | 3.3 | 237.5 | 5.2 | 421.8 | 420.3 | 108 | 48.5 | 521.2 | 521.6 | 80.1 | 62.9 | 201.6 | 341.1 | 147.8 | 116.2 | 221.5 | 110.3 | 99 | 299.5 | 186 | 135.6 | 118.1 | 111.7 | 126 | 124.2 | 110.4 | 119.2 | 127.1
3746.1 | 3525.1 | -6.8 | 0 | 0 | 119 | 116.4 | 105.9 | 107.2 | 126.4 | 27.7 | 20.9 | 42.4 | 3.4 | 249.5 | 4.9 | 421.8 | 420.3 | 108 | 48.4 | 521.1 | 521.5 | 80.2 | 62.9 | 201.6 | 341 | 147.8 | 116.2 | 221.3 | 110.4 | 98.9 | 298.9 | 185.8 | 135.5 | 118.1 | 111.6 | 125.9 | 124.1 | 110.3 | 119.1 | 127
3747.1 | 3526.1 | -6.8 | 0 | 0 | 119 | 116.3 | 105.8 | 107.1 | 126.2 | 27.8 | 20.9 | 42.4 | 3.2 | 238.9 | 5.1 | 421.8 | 420.4 | 108.2 | 48.3 | 521.1 | 521.3 | 79.9 | 62.7 | 201.5 | 340.8 | 147.9 | 116.1 | 221.1 | 110.6 | 99 | 298.3 | 185.6 | 135.5 | 118 | 111.5 | 125.8 | 124 | 110.2 | 119.1 | 127
3748.1 | 3527.1 | -6.8 | 0 | 0 | 119 | 116.2 | 105.8 | 107 | 126.2 | 27.7 | 20.9 | 42.4 | 3 | 240.7 | 5.5 | 421.7 | 420.3 | 108.5 | 48.2 | 521 | 521 | 79.1 | 62.8 | 201.4 | 340.6 | 147.9 | 116.1 | 220.9 | 110.5 | 99.1 | 297.8 | 185.4 | 135.3 | 117.9 | 111.4 | 125.7 | 123.9 | 110.1 | 119.1 | 126.9
3749.1 | 3528.1 | -6.8 | 0 | 0 | 119 | 116.1 | 105.7 | 106.9 | 126.4 | 27.7 | 20.9 | 42.4 | 3 | 248.9 | 5.3 | 421.7 | 420.2 | 107.8 | 48.1 | 520.9 | 521 | 78.6 | 62.7 | 201.3 | 340.5 | 148.2 | 116.3 | 220.7 | 110.1 | 99.2 | 297.2 | 185.4 | 135.3 | 117.9 | 111.3 | 125.6 | 123.9 | 110 | 119 | 126.8
3750.1 | 3529.1 | -6.8 | 0 | 0 | 118.9 | 116 | 105.7 | 106.9 | 126.4 | 27.7 | 20.9 | 42.4 | 2.9 | 258.4 | 5.1 | 421.7 | 420.1 | 107.8 | 48 | 520.9 | 521.1 | 78.2 | 62.5 | 201.2 | 340.3 | 147.8 | 116.3 | 220.5 | 109.8 | 99.2 | 296.6 | 185.4 | 135.2 | 117.8 | 111.2 | 125.6 | 123.8 | 110 | 119 | 126.7
3751.1 | 3530.1 | -6.8 | 0 | 0 | 118.9 | 115.8 | 105.6 | 106.9 | 126.3 | 27.7 | 20.9 | 42.4 | 3.1 | 252.3 | 5.2 | 421.6 | 420.2 | 107.6 | 47.8 | 520.9 | 521.2 | 77.9 | 62.3 | 201.1 | 340.1 | 147.6 | 116.2 | 220.3 | 109.6 | 99.2 | 296 | 185.3 | 135.1 | 117.8 | 111.1 | 125.5 | 123.8 | 110 | 118.9 | 126.7
3752.1 | 3531.1 | -6.8 | 0 | 0 | 118.7 | 115.7 | 105.6 | 106.8 | 126 | 27.7 | 20.9 | 42.3 | 2.8 | 254.8 | 5.7 | 421.6 | 420.1 | 107.4 | 47.7 | 520.9 | 521.4 | 78.4 | 62.2 | 201 | 340 | 147.1 | 116.4 | 220.1 | 109.5 | 99 | 295.4 | 185.3 | 135 | 117.7 | 111.1 | 125.5 | 123.7 | 109.9 | 118.9 | 126.6
3753.1 | 3532.1 | -6.8 | 0 | 0 | 118.5 | 115.6 | 105.5 | 106.7 | 125.7 | 27.7 | 20.9 | 42.3 | 2.7 | 261.7 | 5.5 | 421.6 | 420.1 | 106.6 | 47.6 | 520.9 | 521.7 | 78.4 | 62.1 | 200.9 | 339.8 | 146.7 | 116.4 | 219.9 | 109.6 | 98.9 | 294.8 | 185.3 | 134.9 | 117.7 | 111.1 | 125.4 | 123.6 | 109.9 | 118.9 | 126.6
3754.1 | 3533.1 | -6.7 | 0 | 0 | 118.3 | 115.4 | 105.4 | 106.7 | 125.6 | 27.6 | 20.9 | 42.3 | 2.7 | 252.3 | 6.3 | 421.6 | 420 | 105.5 | 47.5 | 520.8 | 522 | 78.1 | 61.9 | 200.8 | 339.6 | 146.1 | 116.6 | 219.7 | 109.7 | 99 | 294.2 | 185.1 | 134.9 | 117.6 | 111.1 | 125.4 | 123.5 | 109.8 | 118.8 | 126.5
3755.1 | 3534.1 | -6 | 0 | 0 | 118.3 | 115.3 | 105.3 | 106.6 | 125.7 | 27.6 | 20.9 | 42.3 | 2.4 | 254 | 7.4 | 421.5 | 420 | 105.3 | 47.4 | 520.7 | 522.2 | 77.8 | 61.8 | 200.8 | 339.5 | 145.9 | 116.7 | 219.5 | 109.9 | 98.9 | 293.7 | 185 | 134.8 | 117.7 | 111 | 125.3 | 123.4 | 109.8 | 118.7 | 126.4
3756.1 | 3535.1 | -5.8 | 0 | 0 | 118.3 | 115.2 | 105.2 | 106.6 | 125.7 | 27.6 | 20.9 | 42.3 | 2.5 | 252.5 | 8.1 | 421.5 | 420 | 106.1 | 47.4 | 520.7 | 522.3 | 77.3 | 61.8 | 200.8 | 339.3 | 145.3 | 116.6 | 219.3 | 110.1 | 98.7 | 293.1 | 184.9 | 134.7 | 117.6 | 110.9 | 125.2 | 123.3 | 109.8 | 118.6 | 126.3
3757.1 | 3536.1 | -5.9 | 0 | 0 | 118.3 | 115.2 | 105.2 | 106.5 | 125.3 | 27.6 | 20.9 | 42.3 | 2.7 | 250.5 | 8.3 | 421.5 | 420 | 106.6 | 47.4 | 520.7 | 522.3 | 76.8 | 61.8 | 200.8 | 339.1 | 144.9 | 116.5 | 219.1 | 110.1 | 98.5 | 292.5 | 185 | 134.6 | 117.5 | 110.8 | 125.1 | 123.3 | 109.7 | 118.5 | 126.3
3758.1 | 3537.1 | -5.9 | 0 | 0 | 118.2 | 115.1 | 105.2 | 106.4 | 125 | 27.6 | 20.9 | 42.3 | 2.7 | 248.7 | 8.2 | 421.5 | 419.9 | 106.2 | 47.3 | 520.7 | 522.4 | 76.4 | 61.9 | 200.7 | 338.9 | 145 | 116.2 | 218.9 | 110.2 | 98.6 | 291.9 | 184.9 | 134.6 | 117.5 | 110.8 | 125 | 123.2 | 109.6 | 118.4 | 126.2
3759.1 | 3538.1 | -5.9 | 0 | 0 | 118.1 | 115 | 105.1 | 106.4 | 124.8 | 27.5 | 20.9 | 42.3 | 2.6 | 245.8 | 8 | 421.4 | 419.9 | 106.7 | 47.2 | 520.7 | 522.3 | 75.9 | 61.9 | 200.7 | 338.8 | 145 | 116.2 | 218.7 | 110.2 | 98.6 | 291.3 | 184.8 | 134.5 | 117.4 | 110.7 | 124.9 | 123.1 | 109.6 | 118.3 | 126.1
3760.1 | 3539.1 | -6.1 | 0 | 0 | 118.1 | 115 | 105.1 | 106.3 | 124.8 | 27.5 | 20.9 | 42.3 | 2.6 | 250 | 7.7 | 421.4 | 419.9 | 107.5 | 47.2 | 520.6 | 522.4 | 75.5 | 61.9 | 200.6 | 338.6 | 144.8 | 116.1 | 218.5 | 109.9 | 98.7 | 290.7 | 184.6 | 134.4 | 117.3 | 110.7 | 124.8 | 123 | 109.5 | 118.3 | 126.1
3761.1 | 3540.1 | -6.5 | 0 | 0 | 118 | 114.9 | 105 | 106.2 | 125 | 27.5 | 20.9 | 42.3 | 2.6 | 250.6 | 7.7 | 421.4 | 419.8 | 107.1 | 47.2 | 520.5 | 522.6 | 75.9 | 61.9 | 200.6 | 338.4 | 144.9 | 115.8 | 218.3 | 109.9 | 98.7 | 290.1 | 184.4 | 134.4 | 117.3 | 110.6 | 124.8 | 123 | 109.5 | 118.3 | 126
3762.1 | 3541.1 | -6.7 | 0 | 0 | 118 | 114.9 | 105 | 106 | 125.2 | 27.5 | 20.9 | 42.3 | 2.7 | 253.2 | 7.7 | 421.3 | 419.7 | 106.6 | 47.2 | 520.5 | 522.8 | 75.4 | 61.9 | 200.6 | 338.3 | 145 | 115.7 | 218.1 | 110 | 98.7 | 289.6 | 184.3 | 134.3 | 117.2 | 110.5 | 124.7 | 122.9 | 109.5 | 118.2 | 125.9
3763.1 | 3542.1 | -6.8 | 0 | 0 | 118.1 | 114.9 | 104.9 | 105.8 | 125.3 | 27.5 | 20.9 | 42.3 | 3.2 | 249.9 | 7.6 | 421.3 | 419.7 | 106.2 | 47.2 | 520.4 | 523.1 | 75 | 61.9 | 200.6 | 338.1 | 145.7 | 115.7 | 217.9 | 109.7 | 98.5 | 289 | 184.3 | 134.2 | 117.1 | 110.4 | 124.7 | 122.8 | 109.4 | 118.2 | 125.8
3764.1 | 3543.1 | -6.8 | 0 | 0 | 118.1 | 114.8 | 104.8 | 105.8 | 125.2 | 27.5 | 20.9 | 42.3 | 3.6 | 239.9 | 7.6 | 421.3 | 419.7 | 105.2 | 47.1 | 520.3 | 523.2 | 74.7 | 62 | 200.6 | 337.9 | 146.1 | 115.8 | 217.7 | 109.5 | 98.6 | 288.4 | 184.2 | 134.1 | 117 | 110.4 | 124.6 | 122.7 | 109.3 | 118.1 | 125.8
3765.1 | 3544.1 | -6.7 | 0 | 0 | 118 | 114.7 | 104.8 | 105.8 | 125.1 | 27.5 | 20.9 | 42.3 | 3.5 | 238.9 | 7.5 | 421.3 | 419.6 | 104.4 | 47.1 | 520.3 | 523.3 | 75.4 | 62 | 200.5 | 337.7 | 146.3 | 115.9 | 217.5 | 109.4 | 98.5 | 287.8 | 184.1 | 134 | 117 | 110.3 | 124.6 | 122.6 | 109.2 | 118 | 125.7
3766.1 | 3545.1 | -6.7 | 0 | 0 | 117.9 | 114.7 | 104.7 | 105.8 | 125.3 | 27.5 | 20.9 | 42.3 | 3.7 | 242 | 7.4 | 421.2 | 419.6 | 104 | 47.1 | 520.2 | 523.3 | 75.2 | 62.1 | 200.5 | 337.5 | 146.6 | 115.9 | 217.3 | 109 | 98.5 | 287.3 | 184.1 | 134 | 116.9 | 110.2 | 124.5 | 122.6 | 109.1 | 118 | 125.6
3767.1 | 3546.1 | -6.7 | 0 | 0 | 117.8 | 114.7 | 104.7 | 105.7 | 125.3 | 27.5 | 20.9 | 42.3 | 3.4 | 242.9 | 7.3 | 421.2 | 419.6 | 104.8 | 47.1 | 520.2 | 523.3 | 74.9 | 62.1 | 200.5 | 337.3 | 146.9 | 115.8 | 217.1 | 108.8 | 98.2 | 286.7 | 183.9 | 133.9 | 116.9 | 110.1 | 124.4 | 122.5 | 109.1 | 117.9 | 125.6
3768.1 | 3547.1 | -6.8 | 0 | 0 | 117.6 | 114.7 | 104.6 | 105.8 | 125 | 27.5 | 20.9 | 42.2 | 3.2 | 256.2 | 6.8 | 421.2 | 419.5 | 106 | 47.2 | 520.2 | 523.3 | 74.8 | 62.1 | 200.5 | 337.1 | 146.8 | 115.7 | 216.9 | 108.6 | 98.1 | 286.2 | 183.6 | 133.8 | 116.8 | 110 | 124.3 | 122.4 | 109 | 117.9 | 125.5
3769.1 | 3548.1 | -6.8 | 0 | 0 | 117.5 | 114.6 | 104.5 | 105.8 | 124.6 | 27.4 | 20.9 | 42.2 | 3.2 | 250.1 | 6.3 | 421.1 | 419.5 | 105.9 | 47.2 | 520.2 | 523.2 | 74.7 | 61.9 | 200.4 | 336.9 | 146.5 | 115.5 | 216.7 | 108.4 | 98.1 | 285.6 | 183.5 | 133.7 | 116.8 | 110 | 124.2 | 122.4 | 108.9 | 117.8 | 125.4
3770.1 | 3549.1 | -6.7 | 0 | 0 | 117.4 | 114.5 | 104.4 | 105.8 | 124.5 | 27.4 | 20.9 | 42.2 | 3.5 | 238.9 | 6.2 | 421.1 | 419.5 | 105.1 | 47.2 | 520.2 | 523.2 | 74.3 | 62 | 200.4 | 336.8 | 145.9 | 115.3 | 216.5 | 108.1 | 98.1 | 285.1 | 183.3 | 133.6 | 116.8 | 109.9 | 124.1 | 122.3 | 108.9 | 117.7 | 125.3
3771.1 | 3550.1 | -6.7 | 0 | 0 | 117.3 | 114.5 | 104.4 | 105.8 | 124.3 | 27.3 | 20.9 | 42.2 | 3.7 | 250.8 | 6.5 | 421.1 | 419.4 | 105.3 | 47.3 | 520.2 | 523.2 | 73.9 | 62.1 | 200.4 | 336.6 | 145.8 | 115.1 | 216.3 | 108.1 | 98.1 | 284.5 | 183.3 | 133.6 | 116.7 | 109.8 | 124.1 | 122.2 | 108.9 | 117.7 | 125.3
3772.1 | 3551.1 | -6.7 | 0 | 0 | 117.3 | 114.5 | 104.3 | 105.6 | 124.3 | 27.3 | 20.9 | 42.2 | 3.5 | 237.7 | 6.7 | 421 | 419.4 | 105.8 | 47.4 | 520.2 | 523 | 73.5 | 62.1 | 200.3 | 336.4 | 146.3 | 114.9 | 216.1 | 108 | 98 | 284 | 183.2 | 133.5 | 116.6 | 109.8 | 124 | 122.1 | 108.8 | 117.6 | 125.2
3773.1 | 3552.1 | -6.7 | 0 | 0 | 117.2 | 114.5 | 104.2 | 105.4 | 124.3 | 27.3 | 20.9 | 42.1 | 3.7 | 242.5 | 6.4 | 421 | 419.4 | 105.6 | 47.5 | 520.3 | 522.7 | 73.1 | 62 | 200.3 | 336.2 | 146.7 | 114.9 | 215.9 | 108.1 | 98.3 | 283.4 | 183.1 | 133.4 | 116.5 | 109.8 | 123.9 | 122.1 | 108.8 | 117.6 | 125.1
3774.1 | 3553.1 | -6.8 | 0 | 0 | 117.1 | 114.5 | 104.1 | 105.2 | 124.5 | 27.2 | 20.9 | 42.1 | 3.5 | 234.5 | 6.2 | 421 | 419.3 | 104.6 | 47.7 | 520.3 | 522.3 | 73.4 | 61.8 | 200.4 | 336 | 146.7 | 115.1 | 215.7 | 108.1 | 98.4 | 282.9 | 182.9 | 133.3 | 116.5 | 109.7 | 123.9 | 122 | 108.7 | 117.5 | 125
3775.1 | 3554.1 | -6.8 | 0 | 0 | 117 | 114.4 | 104.1 | 105.1 | 124.6 | 27.2 | 20.9 | 42.1 | 3.3 | 231.4 | 5.9 | 421 | 419.3 | 104 | 47.7 | 520.3 | 522.2 | 74.2 | 61.6 | 200.4 | 335.8 | 146.7 | 115 | 215.5 | 108 | 98.2 | 282.3 | 182.9 | 133.3 | 116.5 | 109.6 | 123.8 | 121.9 | 108.7 | 117.4 | 125
3776.1 | 3555.1 | -6.8 | 0 | 0 | 116.9 | 114.4 | 104 | 105.2 | 124.5 | 27.2 | 20.9 | 42.1 | 3.4 | 243.4 | 5.8 | 420.9 | 419.2 | 104.4 | 47.8 | 520.3 | 521.9 | 74.8 | 61.7 | 200.3 | 335.6 | 146.4 | 114.9 | 215.2 | 108.5 | 98.1 | 281.8 | 182.8 | 133.2 | 116.4 | 109.5 | 123.7 | 121.8 | 108.6 | 117.3 | 124.9
3777.1 | 3556.1 | -6.8 | 0 | 0 | 116.7 | 114.3 | 103.9 | 105.1 | 124.5 | 27.2 | 20.9 | 42.1 | 3.2 | 238.3 | 5.9 | 420.9 | 419.2 | 105.6 | 47.9 | 520.3 | 521.5 | 74.7 | 61.7 | 200.3 | 335.4 | 146.2 | 114.7 | 215 | 108.9 | 98.1 | 281.3 | 182.6 | 133.1 | 116.3 | 109.4 | 123.7 | 121.8 | 108.6 | 117.2 | 124.8
3778.1 | 3557.1 | -6.8 | 0 | 0 | 116.6 | 114.3 | 103.8 | 105.1 | 124.4 | 27.2 | 20.9 | 42.1 | 3.3 | 251.6 | 5.8 | 420.9 | 419.2 | 105.3 | 48 | 520.3 | 521.2 | 74.9 | 61.6 | 200.4 | 335.2 | 146.4 | 114.7 | 214.8 | 108.8 | 98.2 | 280.8 | 182.4 | 133 | 116.1 | 109.3 | 123.6 | 121.7 | 108.6 | 117.1 | 124.7
3779.1 | 3558.1 | -6.8 | 0 | 0 | 116.6 | 114.3 | 103.7 | 105.1 | 124.3 | 27.2 | 20.9 | 42 | 3.2 | 248.4 | 5.8 | 420.9 | 419.2 | 105.8 | 48.1 | 520.3 | 520.8 | 75.2 | 61.7 | 200.2 | 335 | 146.7 | 114.4 | 214.6 | 108.8 | 98.3 | 280.3 | 182.4 | 132.9 | 116 | 109.2 | 123.6 | 121.6 | 108.5 | 117.1 | 124.7
3780.1 | 3559.1 | -6.8 | 0 | 0 | 116.6 | 114.2 | 103.7 | 105 | 124.4 | 27.2 | 20.9 | 42 | 3.2 | 251.1 | 5.7 | 420.8 | 419.2 | 105.3 | 48.2 | 520.3 | 520.3 | 75.6 | 61.7 | 200.2 | 334.8 | 146.4 | 114.4 | 214.4 | 108.9 | 98.2 | 279.8 | 182.3 | 132.8 | 115.9 | 109.2 | 123.5 | 121.6 | 108.5 | 117 | 124.6
3781.1 | 3560.1 | -6.8 | 0 | 0 | 116.7 | 114 | 103.6 | 104.8 | 124.5 | 27.2 | 20.9 | 42 | 3.5 | 251.3 | 5.4 | 420.8 | 419.1 | 104.4 | 48.2 | 520.3 | 520 | 76 | 61.7 | 200.2 | 334.6 | 145.9 | 114.3 | 214.3 | 108.9 | 98.2 | 279.3 | 182.1 | 132.8 | 115.8 | 109.1 | 123.5 | 121.6 | 108.5 | 117 | 124.5
3782.1 | 3561.1 | -6.8 | 0 | 0 | 116.7 | 113.9 | 103.6 | 104.7 | 124.6 | 27.2 | 20.9 | 41.9 | 3.3 | 243.4 | 5.1 | 420.8 | 419 | 103.7 | 48.1 | 520.2 | 520 | 75.7 | 61.3 | 200.3 | 334.4 | 145.8 | 114 | 214 | 108.9 | 98 | 278.8 | 182.2 | 132.7 | 115.7 | 109 | 123.3 | 121.5 | 108.4 | 116.9 | 124.4
3783.1 | 3562.1 | -6.8 | 0 | 0 | 116.6 | 113.9 | 103.5 | 104.6 | 124.7 | 27.3 | 20.9 | 41.9 | 3 | 248.8 | 4.7 | 420.7 | 419 | 103.5 | 48.1 | 520.2 | 520.2 | 76.2 | 61 | 200.1 | 334.1 | 145.8 | 113.8 | 213.8 | 108.8 | 97.8 | 278.3 | 182.1 | 132.7 | 115.6 | 108.9 | 123.3 | 121.4 | 108.3 | 116.8 | 124.4
3784.1 | 3563.1 | -6.8 | 0 | 0 | 116.6 | 113.8 | 103.5 | 104.5 | 124.4 | 27.3 | 20.9 | 41.9 | 3.3 | 241.6 | 4.6 | 420.7 | 419 | 104.7 | 48 | 520.2 | 520.1 | 76.3 | 60.8 | 200.1 | 333.9 | 145.7 | 113.4 | 213.6 | 108.7 | 97.7 | 277.8 | 181.8 | 132.6 | 115.5 | 108.9 | 123.2 | 121.4 | 108.2 | 116.7 | 124.3
3785.1 | 3564.1 | -6.8 | 0 | 0 | 116.4 | 113.7 | 103.4 | 104.5 | 124.3 | 27.3 | 20.9 | 41.9 | 3.4 | 245.7 | 4.6 | 420.7 | 419 | 105.9 | 48 | 520.3 | 519.8 | 76.5 | 60.7 | 200.1 | 333.7 | 146.4 | 113.2 | 213.4 | 108.6 | 97.7 | 277.3 | 181.5 | 132.5 | 115.5 | 108.9 | 123.2 | 121.3 | 108.1 | 116.6 | 124.2
3786.1 | 3565.1 | -6.8 | 0 | 0 | 116.3 | 113.5 | 103.4 | 104.5 | 124.2 | 27.3 | 21 | 41.9 | 3.4 | 248 | 4.6 | 420.7 | 418.9 | 106.4 | 48.1 | 520.3 | 519.4 | 77.1 | 60.6 | 200.1 | 333.5 | 146.8 | 113.1 | 213.2 | 108.4 | 97.8 | 276.8 | 181.3 | 132.5 | 115.5 | 108.9 | 123.2 | 121.2 | 108.1 | 116.6 | 124.1
3787.1 | 3566.1 | -6.6 | 0 | 0 | 116.2 | 113.4 | 103.4 | 104.6 | 124.2 | 27.3 | 21 | 41.9 | 3.4 | 236.6 | 4.7 | 420.6 | 418.9 | 107.6 | 48 | 520.4 | 519.1 | 77 | 60.5 | 200.1 | 333.3 | 147.1 | 112.9 | 213 | 108.2 | 97.5 | 276.4 | 181.1 | 132.4 | 115.5 | 108.8 | 123.1 | 121.1 | 108 | 116.6 | 124.1
3788.1 | 3567.1 | -6.7 | 0 | 0 | 115.9 | 113.3 | 103.3 | 104.5 | 124.3 | 27.4 | 20.9 | 41.9 | 3.2 | 248.8 | 4.6 | 420.6 | 418.8 | 107.7 | 48 | 520.3 | 518.8 | 76.4 | 60.2 | 200 | 333.1 | 146.9 | 112.8 | 212.8 | 108 | 97.3 | 275.9 | 180.8 | 132.3 | 115.3 | 108.8 | 123 | 121.1 | 108 | 116.5 | 124
3789.1 | 3568.1 | -6.7 | 0 | 0 | 115.6 | 113.3 | 103.3 | 104.4 | 124.4 | 27.3 | 20.9 | 41.9 | 3.3 | 248.4 | 4.7 | 420.6 | 418.8 | 107.5 | 48 | 520.3 | 518.7 | 76.7 | 60 | 199.8 | 332.8 | 146.9 | 112.6 | 212.6 | 108 | 97 | 275.4 | 180.8 | 132.2 | 115.2 | 108.7 | 122.9 | 121 | 107.9 | 116.5 | 123.9
3790.1 | 3569.1 | -6.5 | 0 | 0 | 115.3 | 113.4 | 103.2 | 104.3 | 124.6 | 27.4 | 20.9 | 41.9 | 3.1 | 227.2 | 4.8 | 420.6 | 418.8 | 106.3 | 47.9 | 520.2 | 518.8 | 77.8 | 60 | 199.7 | 332.6 | 147.1 | 112.3 | 212.4 | 107.7 | 96.9 | 275 | 180.6 | 132.2 | 115.2 | 108.6 | 122.9 | 120.9 | 107.8 | 116.4 | 123.9
3791.1 | 3570.1 | -6.7 | 0 | 0 | 115.3 | 113.4 | 103.2 | 104.3 | 124.7 | 27.4 | 21 | 41.9 | 3.4 | 214.2 | 4.6 | 420.5 | 418.7 | 106.3 | 48 | 520.1 | 518.9 | 78.5 | 59.8 | 199.5 | 332.4 | 147.2 | 112.1 | 212.2 | 107.5 | 96.8 | 274.5 | 180.6 | 132.1 | 115.1 | 108.6 | 122.8 | 120.8 | 107.7 | 116.2 | 123.8
3792.1 | 3571.1 | -6.8 | 0 | 0 | 115.2 | 113.4 | 103.1 | 104.2 | 124.6 | 27.4 | 21 | 41.9 | 2.9 | 234.7 | 4.7 | 420.5 | 418.7 | 106.7 | 47.8 | 520 | 518.8 | 79.7 | 59.8 | 199.3 | 332.2 | 147.8 | 111.9 | 212 | 107.3 | 96.9 | 274.1 | 180.4 | 132 | 115.1 | 108.5 | 122.8 | 120.8 | 107.6 | 116.1 | 123.7
3793.1 | 3572.1 | -6.8 | 0 | 0 | 115.3 | 113.4 | 103 | 104.1 | 124.5 | 27.4 | 21 | 41.9 | 3.2 | 237.9 | 4.7 | 420.5 | 418.7 | 107.3 | 47.6 | 519.9 | 518.9 | 79.7 | 59.9 | 199.1 | 331.9 | 147.6 | 111.6 | 211.8 | 107.1 | 96.7 | 273.7 | 180.3 | 132 | 115 | 108.4 | 122.7 | 120.7 | 107.6 | 116 | 123.6
3794.1 | 3573.1 | -6.8 | 0 | 0 | 115.3 | 113.2 | 103 | 104 | 124.4 | 27.3 | 20.9 | 41.9 | 2.9 | 226.1 | 4.9 | 420.5 | 418.6 | 106.9 | 47.5 | 519.8 | 519 | 79.5 | 59.6 | 199 | 331.7 | 146.9 | 111.5 | 211.6 | 107 | 96.7 | 273.2 | 180.3 | 131.9 | 114.9 | 108.3 | 122.6 | 120.6 | 107.6 | 116 | 123.6
3795.1 | 3574.1 | -6.8 | 0 | 0 | 115.3 | 113.1 | 102.9 | 103.9 | 124.4 | 27.3 | 21 | 41.9 | 3.1 | 235.8 | 5 | 420.4 | 418.6 | 106.3 | 47.4 | 519.8 | 519.1 | 79.7 | 59.4 | 199 | 331.5 | 146.6 | 111.3 | 211.4 | 106.8 | 96.5 | 272.8 | 180.2 | 131.7 | 114.7 | 108.3 | 122.6 | 120.6 | 107.5 | 115.9 | 123.5
3796.1 | 3575.1 | -6.7 | 0 | 0 | 115.3 | 113 | 102.8 | 103.8 | 124.5 | 27.3 | 21 | 41.9 | 3.2 | 241.2 | 5.1 | 420.4 | 418.5 | 105.6 | 47.3 | 519.7 | 519.6 | 80.3 | 59.5 | 198.9 | 331.2 | 146 | 111.1 | 211.2 | 106.8 | 95.9 | 272.4 | 179.9 | 131.7 | 114.6 | 108.2 | 122.5 | 120.5 | 107.4 | 115.9 | 123.4
3797.1 | 3576.1 | -6.7 | 0 | 0 | 115.3 | 112.7 | 102.7 | 103.8 | 124.6 | 27.3 | 20.9 | 41.9 | 3.2 | 240.8 | 5.3 | 420.4 | 418.5 | 104.8 | 47.3 | 519.7 | 520 | 80.5 | 59.8 | 198.8 | 331 | 146.2 | 111 | 211 | 106.9 | 95.6 | 272 | 179.8 | 131.6 | 114.6 | 108.2 | 122.4 | 120.4 | 107.3 | 115.9 | 123.4
3798.1 | 3577.1 | -6.8 | 0 | 0 | 115.4 | 112.6 | 102.7 | 103.8 | 124.5 | 27.3 | 20.9 | 41.9 | 3.3 | 240.9 | 5.3 | 420.3 | 418.4 | 103.9 | 47.4 | 519.7 | 520.2 | 81 | 60 | 198.7 | 330.8 | 145.9 | 110.8 | 210.8 | 106.6 | 95.7 | 271.5 | 179.7 | 131.5 | 114.5 | 108.1 | 122.3 | 120.3 | 107.2 | 115.9 | 123.3
3799.1 | 3578.1 | -6.8 | 0 | 0 | 115.3 | 112.5 | 102.6 | 103.7 | 124.5 | 27.3 | 21 | 41.9 | 3.3 | 240.9 | 5.1 | 420.3 | 418.4 | 103.3 | 47.5 | 519.7 | 520.4 | 80.5 | 60.1 | 198.7 | 330.6 | 145.8 | 110.6 | 210.6 | 106.6 | 95.6 | 271.1 | 179.5 | 131.4 | 114.5 | 108 | 122.2 | 120.3 | 107.2 | 115.9 | 123.2
3800.1 | 3579.1 | -6.8 | 0 | 0 | 115.3 | 112.5 | 102.6 | 103.7 | 124.6 | 27.3 | 21 | 41.9 | 3.5 | 240.1 | 5 | 420.3 | 418.4 | 103.8 | 47.5 | 519.7 | 520.4 | 80.2 | 60.3 | 198.6 | 330.3 | 145.3 | 110.6 | 210.4 | 106.7 | 95.4 | 270.7 | 179.4 | 131.4 | 114.4 | 107.9 | 122.1 | 120.2 | 107.1 | 115.8 | 123.2
3801.1 | 3580.1 | -6.7 | 0 | 0 | 115.2 | 112.4 | 102.5 | 103.6 | 124.6 | 27.3 | 21 | 41.9 | 3.7 | 243.3 | 5.1 | 420.2 | 418.3 | 104.1 | 47.5 | 519.6 | 520.5 | 79.9 | 60.4 | 198.6 | 330.1 | 145.3 | 110.5 | 210.2 | 106.6 | 95.3 | 270.3 | 179.2 | 131.3 | 114.4 | 107.8 | 122 | 120.1 | 107.1 | 115.7 | 123.1
3802.1 | 3581.1 | -6.6 | 0 | 0 | 115.1 | 112.4 | 102.5 | 103.5 | 124.2 | 27.3 | 21 | 41.9 | 3.7 | 252 | 5.1 | 420.2 | 418.3 | 104.2 | 47.4 | 519.6 | 520.6 | 79.4 | 60.4 | 198.5 | 329.9 | 144.8 | 110.3 | 210 | 106.5 | 95.4 | 269.9 | 179 | 131.2 | 114.4 | 107.8 | 121.9 | 120.1 | 107 | 115.6 | 123
3803.1 | 3582.1 | -6.6 | 0 | 0 | 115.1 | 112.3 | 102.4 | 103.4 | 123.7 | 27.3 | 21 | 41.9 | 3.4 | 258 | 5 | 420.2 | 418.3 | 104.2 | 47.4 | 519.5 | 520.7 | 78.7 | 60.5 | 198.4 | 329.7 | 144.3 | 110.3 | 209.8 | 106.2 | 95.5 | 269.5 | 179 | 131.1 | 114.3 | 107.7 | 121.9 | 120 | 106.9 | 115.6 | 123
3804.1 | 3583.1 | -6.1 | 0 | 0 | 115.1 | 112.2 | 102.4 | 103.2 | 123.5 | 27.3 | 21 | 41.9 | 3.2 | 264 | 4.9 | 420.1 | 418.2 | 103.9 | 47.3 | 519.5 | 521.1 | 78.2 | 60.8 | 198.4 | 329.5 | 144.1 | 110.3 | 209.6 | 106.3 | 95.6 | 269.1 | 178.9 | 131.1 | 114.3 | 107.6 | 121.8 | 119.9 | 106.9 | 115.5 | 122.9
3805.1 | 3584.1 | -6.2 | 0 | 0 | 115 | 112.1 | 102.4 | 103.1 | 123.6 | 27.3 | 21 | 41.9 | 3 | 269.3 | 5 | 420.1 | 418.2 | 104.6 | 47.4 | 519.5 | 521.5 | 77.8 | 60.9 | 198.4 | 329.3 | 143.6 | 110.1 | 209.4 | 106.8 | 95.5 | 268.7 | 178.6 | 131 | 114.2 | 107.7 | 121.8 | 119.8 | 106.8 | 115.5 | 122.8
3806.1 | 3585.1 | -6.4 | 0 | 0 | 115 | 112 | 102.3 | 103.2 | 123.8 | 27.3 | 21 | 41.9 | 2.8 | 268.6 | 5 | 420.1 | 418.2 | 105.2 | 47.4 | 519.5 | 521.6 | 77.3 | 60.9 | 198.4 | 329.1 | 143.6 | 110 | 209.2 | 106.9 | 95.7 | 268.4 | 178.4 | 130.9 | 114.2 | 107.7 | 121.7 | 119.8 | 106.7 | 115.5 | 122.8
3807.1 | 3586.1 | -6.7 | 0 | 0 | 114.8 | 111.9 | 102.3 | 103.3 | 123.8 | 27.3 | 21 | 41.9 | 2.5 | 270 | 5.1 | 420 | 418.1 | 105.4 | 47.3 | 519.5 | 521.5 | 76.7 | 60.7 | 198.4 | 328.8 | 143.7 | 110 | 209 | 106.9 | 95.8 | 268 | 178.4 | 130.8 | 114.1 | 107.6 | 121.7 | 119.7 | 106.6 | 115.4 | 122.7
3808.1 | 3587.1 | -6.7 | 0 | 0 | 114.7 | 111.9 | 102.3 | 103.3 | 123.8 | 27.3 | 21 | 41.9 | 3 | 267.5 | 4.9 | 420 | 418.1 | 105.2 | 47.2 | 519.5 | 521.4 | 75.9 | 60.5 | 198.4 | 328.6 | 143.6 | 109.8 | 208.8 | 106.6 | 95.7 | 267.6 | 178.4 | 130.8 | 114 | 107.6 | 121.6 | 119.6 | 106.6 | 115.4 | 122.6
3809.1 | 3588.1 | -6.8 | 0 | 0 | 114.7 | 112 | 102.2 | 103.1 | 123.5 | 27.3 | 21 | 41.8 | 3 | 246.6 | 4.6 | 420 | 418.1 | 105.4 | 47.1 | 519.5 | 521.1 | 75.4 | 60.6 | 198.4 | 328.4 | 143.3 | 109.7 | 208.7 | 106.4 | 95.6 | 267.2 | 178.2 | 130.7 | 113.9 | 107.6 | 121.5 | 119.6 | 106.5 | 115.3 | 122.6
3810.1 | 3589.1 | -6.7 | 0 | 0 | 114.6 | 111.9 | 102.2 | 103.1 | 123.3 | 27.3 | 21 | 41.8 | 3 | 241.7 | 4.6 | 420 | 418 | 105.9 | 47.1 | 519.5 | 520.8 | 74.9 | 60.6 | 198.4 | 328.2 | 143.2 | 109.4 | 208.5 | 106.4 | 95.5 | 266.8 | 178.1 | 130.7 | 113.9 | 107.5 | 121.5 | 119.5 | 106.4 | 115.2 | 122.5
3811.1 | 3590.1 | -6.5 | 0 | 0 | 114.7 | 111.9 | 102.1 | 103 | 123.2 | 27.3 | 21 | 41.8 | 3.1 | 245.6 | 4.9 | 419.9 | 418 | 106.6 | 47 | 519.5 | 520.5 | 74.4 | 60.4 | 198.4 | 328 | 143.1 | 109 | 208.3 | 106.4 | 95.4 | 266.5 | 178 | 130.6 | 113.9 | 107.5 | 121.4 | 119.5 | 106.4 | 115.2 | 122.4
3812.1 | 3591.1 | -6.4 | 0 | 0 | 114.7 | 111.8 | 102 | 102.9 | 123 | 27.3 | 21 | 41.8 | 3.2 | 255.1 | 5.6 | 419.9 | 418 | 106.8 | 47 | 519.6 | 520.1 | 73.6 | 60.4 | 198.3 | 327.8 | 143.2 | 108.7 | 208.1 | 106.4 | 95.2 | 266.1 | 178 | 130.5 | 113.8 | 107.3 | 121.3 | 119.4 | 106.4 | 115.1 | 122.3
3813.1 | 3592.1 | -6.3 | 0 | 0 | 114.7 | 111.8 | 102 | 102.9 | 123.2 | 27.3 | 21 | 41.7 | 3.5 | 258.7 | 6.5 | 419.9 | 417.9 | 106.4 | 46.9 | 519.6 | 519.7 | 72.7 | 60.4 | 198.2 | 327.6 | 143.6 | 108.7 | 207.9 | 106.3 | 95.4 | 265.7 | 178 | 130.4 | 113.8 | 107.2 | 121.2 | 119.4 | 106.3 | 115 | 122.3
3814.1 | 3593.1 | -6.6 | 0 | 0 | 114.7 | 111.7 | 101.9 | 102.9 | 123.2 | 27.3 | 21 | 41.7 | 3.4 | 258.7 | 7.5 | 419.8 | 417.9 | 106.7 | 46.9 | 519.7 | 519.2 | 72 | 60.4 | 198.3 | 327.4 | 143.7 | 108.5 | 207.7 | 106.3 | 95.6 | 265.4 | 178.1 | 130.4 | 113.6 | 107.1 | 121.1 | 119.3 | 106.2 | 115 | 122.2
3815.1 | 3594.1 | -6.7 | 0 | 0 | 114.7 | 111.6 | 101.9 | 102.8 | 122.8 | 27.3 | 21 | 41.7 | 3.3 | 272.9 | 7.8 | 419.8 | 417.9 | 106.1 | 46.9 | 519.7 | 518.8 | 71.4 | 60.6 | 198.3 | 327.2 | 143.5 | 108.4 | 207.5 | 106 | 95.5 | 265 | 178 | 130.3 | 113.5 | 107 | 121.1 | 119.2 | 106.2 | 114.9 | 122.1
3816.1 | 3595.1 | -6.8 | 0 | 0 | 114.7 | 111.5 | 101.7 | 102.7 | 122.3 | 27.2 | 21 | 41.6 | 3.5 | 282.1 | 7.6 | 419.8 | 417.9 | 105.2 | 46.9 | 519.8 | 518.4 | 70.9 | 60.7 | 198.2 | 327 | 143.5 | 108.5 | 207.3 | 105.9 | 95.5 | 264.6 | 177.8 | 130.2 | 113.4 | 107 | 121 | 119.1 | 106.1 | 114.8 | 122
3817.1 | 3596.1 | -6.7 | 0 | 0 | 114.5 | 111.4 | 101.5 | 102.6 | 122 | 27.2 | 21 | 41.6 | 3.6 | 267 | 7.1 | 419.7 | 417.8 | 104.1 | 47 | 519.8 | 518.3 | 70.7 | 60.7 | 198.3 | 326.8 | 143.1 | 108.5 | 207.1 | 105.9 | 95.4 | 264.3 | 177.7 | 130.1 | 113.3 | 107 | 121 | 119.1 | 106 | 114.8 | 122
3818.1 | 3597.1 | -6.6 | 0 | 0 | 114.4 | 111.4 | 101.4 | 102.6 | 121.6 | 27.2 | 21 | 41.6 | 3.5 | 267.1 | 7.6 | 419.7 | 417.7 | 103.4 | 47 | 519.7 | 518.6 | 70.3 | 60.7 | 198.4 | 326.6 | 143.5 | 108.5 | 207 | 105.9 | 95.2 | 263.9 | 177.8 | 130.1 | 113.3 | 106.9 | 121 | 119 | 105.9 | 114.7 | 121.9
3819.1 | 3598.1 | -6.6 | 0 | 0 | 114.3 | 111.4 | 101.4 | 102.6 | 121.3 | 27.1 | 21 | 41.6 | 3 | 264.7 | 7.9 | 419.7 | 417.7 | 103 | 47 | 519.7 | 518.8 | 69.7 | 60.7 | 198.3 | 326.4 | 143.7 | 108.7 | 206.8 | 105.8 | 95.2 | 263.6 | 177.8 | 130 | 113.3 | 106.9 | 120.9 | 119 | 105.8 | 114.6 | 121.8
3820.1 | 3599.1 | -6.6 | 0 | 0 | 114.3 | 111.3 | 101.4 | 102.5 | 121.2 | 27.1 | 21 | 41.5 | 3.4 | 256.6 | 8.1 | 419.6 | 417.7 | 102.3 | 47.1 | 519.7 | 518.9 | 69.5 | 60.6 | 198.2 | 326.2 | 143.2 | 108.7 | 206.6 | 105.7 | 95 | 263.2 | 177.8 | 129.9 | 113.3 | 106.9 | 120.9 | 118.9 | 105.8 | 114.5 | 121.8
3821.1 | 3600.1 | -6.7 | 0 | 0 | 114.3 | 111.3 | 101.4 | 102.4 | 121.5 | 27.1 | 21 | 41.5 | 3.3 | 264.2 | 7.9 | 419.6 | 417.7 | 102.3 | 47.1 | 519.7 | 519 | 69.3 | 60.4 | 198.2 | 326 | 143.1 | 108.8 | 206.4 | 105.5 | 94.8 | 262.9 | 177.6 | 129.8 | 113.2 | 106.8 | 120.8 | 118.8 | 105.8 | 114.5 | 121.7
3822.1 | 3601.1 | -6.7 | 0 | 0 | 114.4 | 111.2 | 101.4 | 102.3 | 121.8 | 27.1 | 21 | 41.5 | 3.6 | 265.3 | 7.9 | 419.6 | 417.6 | 102.9 | 47.1 | 519.8 | 519.2 | 69.4 | 60.3 | 198 | 325.7 | 142.8 | 108.7 | 206.2 | 105.5 | 95 | 262.5 | 177.5 | 129.8 | 113.2 | 106.8 | 120.8 | 118.8 | 105.7 | 114.4 | 121.6
3823.1 | 3602.1 | -6.7 | 0 | 0 | 114.3 | 111 | 101.4 | 102.4 | 121.8 | 27.1 | 21 | 41.5 | 3.3 | 269 | 8 | 419.5 | 417.6 | 103.6 | 47.1 | 519.9 | 519 | 70.6 | 60.5 | 198 | 325.5 | 142.7 | 108.6 | 206 | 105.4 | 94.8 | 262.2 | 177.4 | 129.7 | 113.1 | 106.8 | 120.7 | 118.7 | 105.6 | 114.3 | 121.5
3824.1 | 3603.1 | -6.7 | 0 | 0 | 114.1 | 110.9 | 101.4 | 102.4 | 121.8 | 27.1 | 21 | 41.4 | 3.2 | 267.4 | 7.5 | 419.5 | 417.6 | 104.4 | 47.1 | 520 | 518.6 | 71.3 | 60.5 | 198 | 325.3 | 142.1 | 108.5 | 205.8 | 105.3 | 94.6 | 261.9 | 177.1 | 129.6 | 113.1 | 106.7 | 120.6 | 118.6 | 105.6 | 114.2 | 121.5
3825.1 | 3604.1 | -6.7 | 0 | 0 | 113.9 | 110.8 | 101.3 | 102.4 | 121.9 | 27.1 | 21 | 41.4 | 2.7 | 265.8 | 6.9 | 419.5 | 417.5 | 104.7 | 47.1 | 520.1 | 518.2 | 71.2 | 60.4 | 197.8 | 325.1 | 142.5 | 108.5 | 205.7 | 105.2 | 94.5 | 261.5 | 176.9 | 129.5 | 113.1 | 106.7 | 120.5 | 118.6 | 105.5 | 114.1 | 121.4
3826.1 | 3605.1 | -6.7 | 0 | 0 | 113.7 | 110.7 | 101.2 | 102.5 | 122 | 27 | 21 | 41.4 | 2.8 | 257.7 | 6.4 | 419.5 | 417.5 | 104.5 | 47.1 | 520.1 | 517.7 | 71.5 | 60.3 | 197.7 | 324.9 | 142.8 | 108.2 | 205.5 | 105.1 | 94.4 | 261.2 | 176.8 | 129.5 | 113.1 | 106.6 | 120.4 | 118.5 | 105.4 | 114.1 | 121.4
3827.1 | 3606.1 | -6.1 | 0 | 0 | 113.5 | 110.7 | 101.1 | 102.5 | 121.8 | 27 | 21 | 41.4 | 2.6 | 264.4 | 6 | 419.5 | 417.5 | 104.6 | 47 | 520.2 | 517.3 | 72.2 | 60.3 | 197.6 | 324.7 | 142.6 | 107.9 | 205.4 | 104.9 | 94.4 | 260.9 | 176.9 | 129.4 | 113.1 | 106.6 | 120.3 | 118.5 | 105.4 | 114 | 121.3
3828.1 | 3607.1 | -5.8 | 0 | 0 | 113.5 | 110.6 | 100.9 | 102.4 | 121.4 | 26.9 | 21 | 41.4 | 2.8 | 278.3 | 6.2 | 419.4 | 417.5 | 104.5 | 46.9 | 520.2 | 516.9 | 71.7 | 60.4 | 197.5 | 324.5 | 142.2 | 107.8 | 205.2 | 105.2 | 94.4 | 260.6 | 176.7 | 129.3 | 113 | 106.4 | 120.3 | 118.4 | 105.4 | 114 | 121.2
3829.1 | 3608.1 | -6 | 0 | 0 | 113.5 | 110.6 | 100.8 | 102.3 | 121 | 27 | 21 | 41.3 | 3 | 280.3 | 6.6 | 419.4 | 417.4 | 104.7 | 47 | 520.3 | 516.5 | 71 | 60.6 | 197.5 | 324.3 | 142.1 | 107.6 | 205 | 105.8 | 94.3 | 260.2 | 176.6 | 129.2 | 113 | 106.4 | 120.2 | 118.4 | 105.3 | 114 | 121.2
3830.1 | 3609.1 | -6.4 | 0 | 0 | 113.5 | 110.5 | 100.8 | 102.1 | 120.7 | 27 | 21 | 41.3 | 3.2 | 279.2 | 7.2 | 419.4 | 417.3 | 104.7 | 47 | 520.2 | 516.2 | 70.3 | 60.4 | 197.5 | 324.1 | 142 | 107.4 | 204.9 | 106.2 | 94.3 | 259.9 | 176.6 | 129.2 | 113 | 106.3 | 120.2 | 118.3 | 105.2 | 113.9 | 121.1
3831.1 | 3610.1 | -6.7 | 0 | 0 | 113.5 | 110.4 | 100.7 | 101.9 | 120.5 | 26.9 | 21 | 41.3 | 2.9 | 272.9 | 7.4 | 419.4 | 417.3 | 104.8 | 46.9 | 520.2 | 515.9 | 69.6 | 60.1 | 197.4 | 323.8 | 142.2 | 107.1 | 204.7 | 106.5 | 94.2 | 259.6 | 176.6 | 129.1 | 113 | 106.2 | 120.1 | 118.2 | 105.2 | 113.9 | 121
3832.1 | 3611.1 | -6.8 | 0 | 0 | 113.4 | 110.3 | 100.7 | 101.8 | 120.3 | 27 | 21 | 41.2 | 3.1 | 279.2 | 6.7 | 419.3 | 417.3 | 105.1 | 46.8 | 520.2 | 515.8 | 69 | 60 | 197.1 | 323.6 | 142.7 | 106.8 | 204.5 | 106.4 | 94.3 | 259.3 | 176.6 | 129 | 113 | 106.2 | 120.1 | 118.2 | 105.2 | 113.8 | 121
3833.1 | 3612.1 | -6.8 | 0 | 0 | 113.4 | 110.3 | 100.7 | 101.7 | 120 | 27 | 21 | 41.2 | 3 | 277.5 | 6.5 | 419.3 | 417.2 | 105.7 | 46.7 | 520.1 | 515.6 | 68.4 | 59.9 | 197.2 | 323.4 | 142 | 106.5 | 204.4 | 106.3 | 94.2 | 259 | 176.5 | 128.9 | 113 | 106.2 | 120 | 118.1 | 105.1 | 113.7 | 120.9
3834.1 | 3613.1 | -6.8 | 0 | 0 | 113.4 | 110.2 | 100.6 | 101.7 | 119.8 | 27 | 21 | 41.2 | 3 | 282.4 | 6.7 | 419.3 | 417.2 | 105.9 | 46.6 | 520.1 | 515.5 | 68 | 60 | 197.2 | 323.2 | 141.3 | 106.3 | 204.2 | 106.3 | 94.1 | 258.7 | 176.4 | 128.9 | 113 | 106.1 | 120 | 118.1 | 105.1 | 113.6 | 120.8
3835.1 | 3614.1 | -6.8 | 0 | 0 | 113.4 | 110.1 | 100.6 | 101.6 | 120 | 27 | 21 | 41.1 | 3.5 | 282.3 | 7 | 419.2 | 417.2 | 106.8 | 46.6 | 520.1 | 515.4 | 67.6 | 60.2 | 197.1 | 323 | 141.4 | 106.1 | 204.1 | 106.4 | 93.9 | 258.4 | 176.2 | 128.8 | 113 | 106 | 119.9 | 118 | 105 | 113.5 | 120.7
3836.1 | 3615.1 | -6.7 | 0 | 0 | 113.3 | 110.1 | 100.5 | 101.5 | 120 | 27 | 21 | 41.1 | 3.4 | 271.2 | 7.3 | 419.2 | 417.1 | 107.8 | 46.7 | 520.1 | 515.2 | 67.2 | 60.2 | 197 | 322.7 | 141.3 | 106 | 203.9 | 106.5 | 93.6 | 258 | 176.2 | 128.7 | 112.9 | 106 | 119.8 | 117.9 | 105 | 113.5 | 120.7
3837.1 | 3616.1 | -6.7 | 0 | 0 | 113.2 | 110 | 100.5 | 101.4 | 119.9 | 27 | 21 | 41.1 | 3.1 | 273.1 | 7.8 | 419.2 | 417.2 | 108.9 | 46.7 | 520.1 | 515.2 | 66.9 | 60.2 | 197.1 | 322.5 | 141.1 | 105.9 | 203.8 | 106.7 | 93.4 | 257.7 | 176.2 | 128.7 | 112.8 | 105.9 | 119.7 | 117.9 | 104.9 | 113.4 | 120.6
3838.1 | 3617.1 | -6.7 | 0 | 0 | 113 | 110 | 100.4 | 101.4 | 119.8 | 27 | 21 | 41 | 3.2 | 275.4 | 7.3 | 419.2 | 417.1 | 109.4 | 46.7 | 520.1 | 515.3 | 66.7 | 60.3 | 197.1 | 322.3 | 140.4 | 105.8 | 203.6 | 106.9 | 93.4 | 257.4 | 175.9 | 128.7 | 112.8 | 105.9 | 119.7 | 117.8 | 104.8 | 113.4 | 120.6
3839.1 | 3618.1 | -6.7 | 0 | 0 | 112.9 | 109.9 | 100.4 | 101.4 | 119.7 | 27 | 21 | 41 | 3.2 | 274.9 | 6.8 | 419.1 | 417 | 109.5 | 46.9 | 520 | 515.4 | 66.7 | 60.4 | 197 | 322.1 | 139.5 | 105.8 | 203.4 | 106.9 | 93.3 | 257.1 | 175.8 | 128.6 | 112.7 | 105.8 | 119.6 | 117.8 | 104.8 | 113.3 | 120.5
3840.1 | 3619.1 | -6.7 | 0 | 0 | 112.8 | 109.8 | 100.3 | 101.5 | 119.5 | 27 | 21 | 40.9 | 3.4 | 257.8 | 6.2 | 419.1 | 417 | 109.1 | 47.1 | 520 | 515.4 | 66.5 | 60.7 | 197.1 | 321.8 | 138.9 | 105.6 | 203.3 | 106.9 | 93.4 | 256.8 | 175.9 | 128.5 | 112.7 | 105.7 | 119.5 | 117.8 | 104.7 | 113.3 | 120.4
3841.1 | 3620.1 | -6.7 | 0 | 0 | 112.8 | 109.7 | 100.3 | 101.6 | 119.2 | 27 | 21 | 40.9 | 2.7 | 253.3 | 5.4 | 419.1 | 417 | 109.3 | 47.2 | 519.9 | 515.4 | 66.5 | 61 | 197.1 | 321.6 | 138.6 | 105.6 | 203.1 | 106.9 | 93.5 | 256.5 | 175.8 | 128.5 | 112.5 | 105.7 | 119.5 | 117.7 | 104.7 | 113.2 | 120.4
3842.1 | 3621.1 | -6.7 | 0 | 0 | 112.9 | 109.6 | 100.3 | 101.5 | 119.1 | 27 | 21 | 40.8 | 2.8 | 262.7 | 5.1 | 419 | 416.9 | 109.1 | 47.3 | 519.8 | 515.4 | 66.9 | 61.1 | 197.1 | 321.4 | 137.9 | 105.6 | 202.9 | 107.4 | 93.7 | 256.2 | 175.8 | 128.4 | 112.5 | 105.7 | 119.4 | 117.6 | 104.6 | 113.1 | 120.3
3843.1 | 3622.1 | -6.7 | 0 | 0 | 112.9 | 109.5 | 100.3 | 101.4 | 119 | 27 | 21 | 40.8 | 3 | 255.9 | 5.4 | 419 | 416.9 | 108.6 | 47.4 | 519.7 | 515.6 | 67.9 | 61.2 | 197 | 321.1 | 137.2 | 105.5 | 202.7 | 107.4 | 93.9 | 255.9 | 175.6 | 128.3 | 112.4 | 105.6 | 119.4 | 117.5 | 104.6 | 113.1 | 120.2
3844.1 | 3623.1 | -6.8 | 0 | 0 | 112.8 | 109.3 | 100.2 | 101.2 | 119.2 | 27 | 21 | 40.8 | 3.2 | 248.8 | 5.6 | 419 | 416.8 | 108.4 | 47.5 | 519.6 | 516 | 69 | 61.4 | 197 | 320.9 | 136.8 | 105.6 | 202.5 | 107.5 | 94.1 | 255.6 | 175.5 | 128.3 | 112.3 | 105.5 | 119.3 | 117.5 | 104.5 | 113 | 120.2
3845.1 | 3624.1 | -6.7 | 0 | 0 | 112.7 | 109.2 | 100.2 | 101.1 | 119.3 | 26.9 | 21 | 40.7 | 3 | 259.1 | 5.7 | 418.9 | 416.8 | 107.6 | 47.6 | 519.4 | 516.4 | 70.3 | 61.7 | 197 | 320.7 | 135.9 | 105.8 | 202.3 | 107.6 | 94.2 | 255.3 | 175.4 | 128.2 | 112.3 | 105.4 | 119.2 | 117.4 | 104.5 | 113 | 120.1
3846.1 | 3625.1 | -6.7 | 0 | 0 | 112.6 | 109.1 | 100.1 | 101.1 | 119.5 | 26.9 | 21 | 40.7 | 3.2 | 228.6 | 6 | 418.9 | 416.8 | 107.7 | 47.6 | 519.3 | 517 | 70.4 | 61.8 | 197.1 | 320.5 | 135.1 | 105.8 | 202.1 | 107.6 | 94.4 | 255.1 | 175.3 | 128.1 | 112.2 | 105.3 | 119.1 | 117.3 | 104.4 | 112.9 | 120
3847.1 | 3626.1 | -6.7 | 0 | 0 | 112.6 | 109.1 | 100 | 101.2 | 119.7 | 26.9 | 21 | 40.7 | 3.8 | 250.8 | 6 | 418.9 | 416.7 | 108 | 47.8 | 519.1 | 517.7 | 70.8 | 61.8 | 197.1 | 320.2 | 134.6 | 105.9 | 201.9 | 107.7 | 94.8 | 254.8 | 175.3 | 128 | 112 | 105.2 | 119 | 117.3 | 104.3 | 112.9 | 120
3848.1 | 3627.1 | -6.7 | 0 | 0 | 112.5 | 109.1 | 99.9 | 101.2 | 119.7 | 26.9 | 21 | 40.7 | 3.5 | 248.3 | 6.2 | 418.9 | 416.7 | 108 | 47.9 | 519 | 518.2 | 71.4 | 61.9 | 197.1 | 320 | 135.1 | 105.9 | 201.7 | 107.4 | 95 | 254.5 | 175.3 | 128 | 111.9 | 105.1 | 118.9 | 117.2 | 104.3 | 112.8 | 119.9
3849.1 | 3628.1 | -6.7 | 0 | 0 | 112.5 | 109 | 99.8 | 101.2 | 119.8 | 26.9 | 21 | 40.7 | 3.6 | 238.1 | 6.5 | 418.8 | 416.7 | 107.2 | 48.1 | 518.9 | 518.4 | 71.9 | 62 | 197.1 | 319.8 | 135.2 | 105.9 | 201.5 | 107.1 | 94.9 | 254.2 | 175.2 | 127.9 | 111.9 | 105.1 | 118.9 | 117.2 | 104.3 | 112.8 | 119.9
3850.1 | 3629.1 | -6.7 | 0 | 0 | 112.4 | 109 | 99.8 | 101.2 | 119.7 | 26.9 | 21 | 40.6 | 3.9 | 218.7 | 6.6 | 418.8 | 416.7 | 106.9 | 48.2 | 518.8 | 518.5 | 71.7 | 62 | 197.1 | 319.6 | 135.4 | 106 | 201.3 | 106.9 | 95 | 253.9 | 175.1 | 127.8 | 111.9 | 105.1 | 118.8 | 117.1 | 104.2 | 112.8 | 119.8
3851.1 | 3630.1 | -6.6 | 0 | 0 | 112.3 | 108.9 | 99.7 | 101 | 119.6 | 26.9 | 21 | 40.6 | 3.6 | 221.2 | 6.8 | 418.8 | 416.6 | 106.5 | 48.2 | 518.7 | 518.2 | 72.3 | 62.2 | 197 | 319.4 | 135.2 | 106.1 | 201.1 | 106.9 | 95.4 | 253.6 | 175 | 127.7 | 111.8 | 105 | 118.8 | 117 | 104.1 | 112.7 | 119.7
3852.1 | 3631.1 | -6 | 0 | 0 | 112.1 | 108.8 | 99.7 | 100.8 | 119.4 | 26.9 | 21 | 40.7 | 3.5 | 219.8 | 6.1 | 418.7 | 416.6 | 105.8 | 48.1 | 518.6 | 518 | 73.3 | 62.5 | 197 | 319.2 | 134.9 | 106.1 | 200.9 | 106.9 | 95.4 | 253.3 | 174.8 | 127.7 | 111.8 | 105 | 118.7 | 117 | 104.1 | 112.7 | 119.7
3853.1 | 3632.1 | -5.9 | 0 | 0 | 112 | 108.7 | 99.7 | 100.8 | 119.1 | 26.9 | 21 | 40.6 | 3.7 | 220.7 | 5.4 | 418.7 | 416.5 | 105.5 | 48.1 | 518.5 | 517.9 | 73.7 | 62.7 | 197 | 318.9 | 134.4 | 106.1 | 200.8 | 106.8 | 95.3 | 253.1 | 174.8 | 127.6 | 111.9 | 105 | 118.7 | 116.9 | 104 | 112.6 | 119.6
3854.1 | 3633.1 | -6.3 | 0 | 0 | 112 | 108.5 | 99.6 | 100.7 | 119 | 26.9 | 21 | 40.6 | 3.2 | 245.3 | 4.8 | 418.7 | 416.6 | 104.2 | 48 | 518.4 | 517.6 | 75.2 | 62.8 | 197 | 318.7 | 134.1 | 106.1 | 200.6 | 107.1 | 95.3 | 252.8 | 174.8 | 127.5 | 111.8 | 104.9 | 118.6 | 116.8 | 104 | 112.6 | 119.5
3855.1 | 3634.1 | -6.7 | 0 | 0 | 111.9 | 108.5 | 99.6 | 100.6 | 119.2 | 26.9 | 21 | 40.6 | 3.3 | 272.3 | 4.7 | 418.6 | 416.5 | 103 | 48 | 518.3 | 517.4 | 75.2 | 63.1 | 197 | 318.5 | 134.1 | 106.1 | 200.4 | 107.3 | 95.1 | 252.5 | 174.7 | 127.5 | 111.8 | 104.9 | 118.5 | 116.8 | 103.9 | 112.5 | 119.5
3856.1 | 3635.1 | -6.8 | 0 | 0 | 111.9 | 108.4 | 99.5 | 100.4 | 119.2 | 27 | 21 | 40.6 | 3.4 | 240.6 | 4.7 | 418.6 | 416.5 | 101.7 | 48 | 518.2 | 517.4 | 75.3 | 63.3 | 196.9 | 318.3 | 134.2 | 106.1 | 200.2 | 107.5 | 95.1 | 252.2 | 174.7 | 127.4 | 111.8 | 104.8 | 118.5 | 116.8 | 103.9 | 112.4 | 119.4
3857.1 | 3636.1 | -6.8 | 0 | 0 | 111.8 | 108.3 | 99.5 | 100.4 | 119.2 | 26.9 | 21 | 40.6 | 3.2 | 244.1 | 4.5 | 418.6 | 416.4 | 101.1 | 47.8 | 518.1 | 517.6 | 75.8 | 63.3 | 196.9 | 318.1 | 134.4 | 106.1 | 200 | 107.3 | 95.1 | 252 | 174.5 | 127.3 | 111.8 | 104.7 | 118.4 | 116.7 | 103.8 | 112.3 | 119.3
3858.1 | 3637.1 | -6.8 | 0 | 0 | 111.8 | 108.3 | 99.4 | 100.4 | 118.9 | 26.9 | 21 | 40.6 | 3 | 250.9 | 4.3 | 418.6 | 416.4 | 100.2 | 47.8 | 518 | 518 | 76.2 | 63 | 196.8 | 317.9 | 134.3 | 106.1 | 199.8 | 107.1 | 95.1 | 251.7 | 174.6 | 127.2 | 111.8 | 104.7 | 118.3 | 116.7 | 103.7 | 112.2 | 119.3
3859.1 | 3638.1 | -6.8 | 0 | 0 | 111.7 | 108.1 | 99.4 | 100.3 | 118.5 | 26.8 | 21 | 40.6 | 3 | 244.3 | 5 | 418.5 | 416.4 | 99.4 | 47.7 | 517.9 | 518.2 | 76.9 | 62.8 | 196.7 | 317.7 | 134.3 | 105.9 | 199.6 | 106.8 | 94.9 | 251.4 | 174.5 | 127.2 | 111.8 | 104.6 | 118.3 | 116.6 | 103.6 | 112.2 | 119.2
3860.1 | 3639.1 | -6.7 | 0 | 0 | 111.7 | 107.9 | 99.4 | 100.2 | 118.3 | 26.8 | 21 | 40.6 | 3.1 | 239.1 | 5.8 | 418.5 | 416.3 | 100.4 | 47.7 | 517.8 | 518.7 | 76.7 | 62.5 | 196.6 | 317.5 | 134.4 | 105.7 | 199.4 | 106.6 | 94.6 | 251.2 | 174.5 | 127.1 | 111.7 | 104.6 | 118.2 | 116.5 | 103.6 | 112.1 | 119.2
3861.1 | 3640.1 | -6.5 | 0 | 0 | 111.7 | 107.8 | 99.3 | 100.1 | 118.1 | 26.8 | 21 | 40.5 | 3 | 249.5 | 6.5 | 418.5 | 416.3 | 101.7 | 47.7 | 517.9 | 518.9 | 75.9 | 62.5 | 196.5 | 317.3 | 134.4 | 105.5 | 199.3 | 106.5 | 94.5 | 250.9 | 174.5 | 127 | 111.6 | 104.5 | 118.1 | 116.5 | 103.6 | 112 | 119.1
3862.1 | 3641.1 | -6.5 | 0 | 0 | 111.6 | 107.8 | 99.3 | 100.1 | 118 | 26.8 | 21 | 40.5 | 2.7 | 243.6 | 6.8 | 418.5 | 416.2 | 101.9 | 47.8 | 518 | 518.9 | 75.1 | 62.5 | 196.4 | 317.1 | 134.1 | 105.4 | 199.1 | 106.6 | 94.4 | 250.6 | 174.4 | 127 | 111.4 | 104.4 | 118.1 | 116.5 | 103.5 | 111.8 | 119
3863.1 | 3642.1 | -6.7 | 0 | 0 | 111.6 | 107.8 | 99.2 | 100 | 117.7 | 26.8 | 21 | 40.5 | 3 | 244.4 | 6.9 | 418.4 | 416.2 | 102 | 47.8 | 518.1 | 518.8 | 74.8 | 62.5 | 196.5 | 316.9 | 134.1 | 105.3 | 198.9 | 106.9 | 94.6 | 250.4 | 174.3 | 126.9 | 111.3 | 104.4 | 118 | 116.4 | 103.5 | 111.8 | 118.9
3864.1 | 3643.1 | -6.8 | 0 | 0 | 111.5 | 107.8 | 99.1 | 100 | 117.3 | 26.8 | 21 | 40.5 | 3.2 | 240.5 | 6.8 | 418.4 | 416.2 | 102.5 | 47.7 | 518.2 | 518.6 | 74.4 | 62.5 | 196.5 | 316.7 | 134.5 | 105.3 | 198.7 | 106.9 | 94.6 | 250.1 | 174.3 | 126.8 | 111.2 | 104.3 | 118 | 116.4 | 103.5 | 111.7 | 118.9
3865.1 | 3644.1 | -6.7 | 0 | 0 | 111.5 | 107.8 | 99.1 | 100 | 117 | 26.9 | 21 | 40.5 | 3.4 | 243.6 | 6.9 | 418.4 | 416.1 | 101.8 | 47.7 | 518.3 | 518.3 | 74 | 62.6 | 196.5 | 316.5 | 134 | 105.2 | 198.5 | 106.8 | 94.6 | 249.8 | 174.1 | 126.8 | 111 | 104.3 | 117.9 | 116.4 | 103.5 | 111.7 | 118.8
3866.1 | 3645.1 | -6.8 | 0 | 0 | 111.5 | 107.8 | 99 | 100 | 116.8 | 26.9 | 21 | 40.5 | 3.1 | 245.8 | 7.1 | 418.3 | 416.1 | 101.2 | 47.8 | 518.2 | 518.2 | 73.9 | 62.7 | 196.5 | 316.3 | 133.9 | 105.1 | 198.4 | 106.7 | 94.4 | 249.6 | 174.1 | 126.8 | 110.9 | 104.2 | 117.8 | 116.4 | 103.4 | 111.7 | 118.7
3867.1 | 3646.1 | -6.6 | 0 | 0 | 111.5 | 107.7 | 99 | 100 | 116.7 | 26.9 | 21 | 40.5 | 3.2 | 247.8 | 7.1 | 418.3 | 416.1 | 100.2 | 48.1 | 518.2 | 518.3 | 74.5 | 62.8 | 196.5 | 316.1 | 133.8 | 105 | 198.2 | 106.6 | 94.4 | 249.3 | 174.1 | 126.7 | 110.8 | 104.1 | 117.7 | 116.3 | 103.4 | 111.6 | 118.7
3868.1 | 3647.1 | -6.5 | 0 | 0 | 111.4 | 107.6 | 99 | 100 | 116.5 | 27 | 21 | 40.5 | 3.5 | 252.2 | 6.9 | 418.3 | 416 | 99.9 | 48.1 | 518 | 519 | 74.6 | 62.7 | 196.6 | 315.9 | 133.4 | 104.9 | 198 | 106.6 | 94.3 | 249.1 | 173.9 | 126.6 | 110.8 | 104.1 | 117.7 | 116.3 | 103.3 | 111.5 | 118.6
3869.1 | 3648.1 | -6.5 | 0 | 0 | 111.3 | 107.6 | 98.9 | 99.9 | 116.4 | 27 | 21 | 40.5 | 3.3 | 259.3 | 6.7 | 418.2 | 416 | 99.9 | 48.1 | 517.9 | 519.2 | 74.5 | 62.7 | 196.6 | 315.7 | 132.7 | 104.6 | 197.8 | 106.6 | 94.1 | 248.8 | 173.8 | 126.6 | 110.7 | 104.1 | 117.6 | 116.2 | 103.2 | 111.5 | 118.5
3870.1 | 3649.1 | -6.7 | 0 | 0 | 111.2 | 107.6 | 98.8 | 99.9 | 116.2 | 27 | 21 | 40.4 | 3.2 | 251.3 | 7.1 | 418.2 | 416 | 99.8 | 48.1 | 517.8 | 519.2 | 73.9 | 62.8 | 196.6 | 315.5 | 132.4 | 104.5 | 197.7 | 106.6 | 93.9 | 248.5 | 173.7 | 126.5 | 110.6 | 104.1 | 117.6 | 116.1 | 103.1 | 111.4 | 118.5
3871.1 | 3650.1 | -6.7 | 0 | 0 | 111.1 | 107.5 | 98.7 | 99.8 | 116.1 | 27 | 21 | 40.4 | 3 | 252.4 | 7.2 | 418.2 | 416 | 100.4 | 47.9 | 517.7 | 519 | 73.2 | 62.8 | 196.6 | 315.3 | 131.8 | 104.5 | 197.5 | 106.8 | 93.8 | 248.3 | 173.5 | 126.5 | 110.6 | 104.1 | 117.5 | 116 | 103 | 111.4 | 118.4
3872.1 | 3651.1 | -6.3 | 0 | 0 | 111.1 | 107.5 | 98.7 | 99.8 | 116 | 27 | 21 | 40.4 | 3 | 258.9 | 7.1 | 418.2 | 416 | 100.4 | 47.8 | 517.6 | 518.6 | 72.6 | 62.7 | 196.6 | 315.1 | 131.9 | 104.3 | 197.3 | 106.9 | 93.8 | 248 | 173.3 | 126.4 | 110.5 | 104 | 117.5 | 116 | 102.9 | 111.3 | 118.4
3873.1 | 3652.1 | -6.8 | 0 | 0 | 111.1 | 107.4 | 98.6 | 99.7 | 116.1 | 27 | 21 | 40.4 | 2.7 | 266.6 | 6.9 | 418.1 | 415.9 | 99.7 | 47.7 | 517.6 | 518.3 | 72 | 62.7 | 196.6 | 314.9 | 131.8 | 104.2 | 197.1 | 106.9 | 93.6 | 247.7 | 173.2 | 126.4 | 110.5 | 103.9 | 117.4 | 115.9 | 102.8 | 111.3 | 118.3
3874.1 | 3653.1 | -6.8 | 0 | 0 | 111.1 | 107.2 | 98.6 | 99.7 | 116.3 | 27 | 21 | 40.4 | 2.6 | 255.5 | 6.6 | 418.1 | 415.9 | 99.7 | 47.6 | 517.5 | 517.9 | 71.5 | 62.6 | 196.6 | 314.7 | 131.6 | 104 | 197 | 106.8 | 93.6 | 247.5 | 173.1 | 126.3 | 110.5 | 103.9 | 117.4 | 115.8 | 102.7 | 111.2 | 118.2
3875.1 | 3654.1 | -6.8 | 0 | 0 | 111 | 107 | 98.5 | 99.5 | 116.3 | 27 | 21 | 40.4 | 3.2 | 260.8 | 6 | 418.1 | 415.8 | 99.4 | 47.5 | 517.5 | 517.6 | 71.2 | 62.4 | 196.6 | 314.5 | 131.2 | 103.8 | 196.8 | 106.5 | 93.5 | 247.2 | 172.9 | 126.2 | 110.4 | 103.8 | 117.3 | 115.7 | 102.6 | 111.2 | 118.2
3876.1 | 3655.1 | -6.7 | 0 | 0 | 111 | 106.9 | 98.5 | 99.4 | 116 | 27 | 21 | 40.4 | 3.2 | 258.5 | 5.7 | 418.1 | 415.8 | 99.3 | 47.4 | 517.4 | 517.4 | 70.6 | 62.4 | 196.6 | 314.3 | 131.4 | 103.5 | 196.6 | 106.2 | 93.4 | 247 | 173 | 126.2 | 110.3 | 103.8 | 117.2 | 115.6 | 102.6 | 111.1 | 118.1
3877.1 | 3656.1 | -6.7 | 0 | 0 | 110.9 | 106.8 | 98.5 | 99.4 | 115.8 | 27 | 21 | 40.3 | 3.1 | 255.7 | 5.9 | 418 | 415.8 | 99.6 | 47.3 | 517.4 | 517.3 | 70 | 62.2 | 196.6 | 314 | 131.6 | 103.2 | 196.5 | 106 | 93.4 | 246.7 | 172.9 | 126.1 | 110.2 | 103.7 | 117.1 | 115.6 | 102.5 | 111 | 118
3878.1 | 3657.1 | -6.7 | 0 | 0 | 110.8 | 106.7 | 98.5 | 99.2 | 115.7 | 27 | 21 | 40.3 | 3.3 | 260 | 6.6 | 418 | 415.8 | 99.1 | 47.2 | 517.4 | 517 | 69.5 | 61.9 | 196.5 | 313.8 | 131.6 | 103 | 196.3 | 105.8 | 93.2 | 246.5 | 172.8 | 126 | 110.1 | 103.7 | 117 | 115.5 | 102.5 | 111 | 118
3879.1 | 3658.1 | -6.7 | 0 | 0 | 110.8 | 106.5 | 98.4 | 99.2 | 115.8 | 27 | 21 | 40.2 | 3.7 | 254.5 | 6.1 | 418 | 415.7 | 98.8 | 47.1 | 517.4 | 516.8 | 68.8 | 61.7 | 196.5 | 313.6 | 131.9 | 102.7 | 196.1 | 105.7 | 93 | 246.2 | 172.7 | 125.9 | 110.1 | 103.6 | 117 | 115.4 | 102.5 | 110.9 | 117.9
3880.1 | 3659.1 | -6.7 | 0 | 0 | 110.7 | 106.4 | 98.4 | 99.2 | 115.6 | 27 | 21 | 40.2 | 3.4 | 250.6 | 5.1 | 418 | 415.7 | 99.3 | 46.9 | 517.3 | 516.5 | 68.3 | 61.5 | 196.4 | 313.4 | 132.6 | 102.6 | 196 | 105.7 | 92.9 | 246 | 172.5 | 125.9 | 110 | 103.5 | 117 | 115.3 | 102.5 | 110.9 | 117.9
3881.1 | 3660.1 | -6.7 | 0 | 0 | 110.7 | 106.3 | 98.3 | 99.1 | 115.5 | 27 | 21 | 40.2 | 3 | 248.7 | 5 | 417.9 | 415.7 | 99.7 | 46.8 | 517.3 | 516.3 | 67.8 | 61.2 | 196.3 | 313.2 | 132.7 | 102.5 | 195.8 | 105.8 | 92.8 | 245.7 | 172.2 | 125.8 | 109.9 | 103.5 | 116.9 | 115.3 | 102.4 | 110.9 | 117.8
3882.1 | 3661.1 | -6.7 | 0 | 0 | 110.7 | 106.3 | 98.3 | 99.2 | 115.3 | 27 | 21 | 40.2 | 2.7 | 258.7 | 5.4 | 417.9 | 415.7 | 99.9 | 46.7 | 517.3 | 516.2 | 67.2 | 60.9 | 196.3 | 312.9 | 132.7 | 102.5 | 195.7 | 105.6 | 92.6 | 245.5 | 172 | 125.8 | 109.8 | 103.5 | 116.9 | 115.2 | 102.4 | 110.8 | 117.7
3883.1 | 3662.1 | -6.8 | 0 | 0 | 110.6 | 106.2 | 98.3 | 99.2 | 115.4 | 27 | 21 | 40.2 | 2.9 | 256.2 | 6.4 | 417.9 | 415.6 | 100 | 46.5 | 517.3 | 516.2 | 66.5 | 60.7 | 196.2 | 312.7 | 132.3 | 102.5 | 195.5 | 105.7 | 92.4 | 245.2 | 172.1 | 125.7 | 109.7 | 103.5 | 116.9 | 115.1 | 102.3 | 110.8 | 117.7
3884.1 | 3663.1 | -6.8 | 0 | 0 | 110.6 | 106.1 | 98.3 | 99 | 115.9 | 27 | 21 | 40.2 | 2.9 | 253.9 | 6.8 | 417.8 | 415.6 | 99.4 | 46.5 | 517.3 | 516.4 | 66 | 60.7 | 196.1 | 312.5 | 132.4 | 102.3 | 195.4 | 105.5 | 92.3 | 245 | 172 | 125.6 | 109.7 | 103.4 | 116.8 | 115.1 | 102.2 | 110.7 | 117.6
3885.1 | 3664.1 | -6.8 | 0 | 0 | 110.4 | 106 | 98.2 | 98.9 | 116.3 | 27 | 21 | 40.2 | 3.1 | 264.3 | 6.5 | 417.8 | 415.5 | 99.5 | 46.5 | 517.3 | 516.7 | 65.4 | 60.8 | 196 | 312.3 | 132.7 | 102.2 | 195.2 | 105.3 | 92.1 | 244.7 | 172 | 125.5 | 109.6 | 103.4 | 116.7 | 115 | 102.2 | 110.7 | 117.5
3886.1 | 3665.1 | -6.8 | 0 | 0 | 110.3 | 105.9 | 98.1 | 98.9 | 116.6 | 27 | 21 | 40.2 | 3.4 | 237.9 | 6.3 | 417.8 | 415.5 | 99.2 | 46.5 | 517.3 | 516.9 | 64.9 | 60.7 | 196.1 | 312.1 | 132.8 | 101.9 | 195 | 105.2 | 91.8 | 244.5 | 171.8 | 125.5 | 109.5 | 103.3 | 116.6 | 114.9 | 102.2 | 110.7 | 117.5
3887.1 | 3666.1 | -6.8 | 0 | 0 | 110.2 | 105.8 | 98.1 | 98.9 | 116.7 | 26.9 | 21 | 40.2 | 3.1 | 237 | 6.2 | 417.8 | 415.4 | 99.2 | 46.6 | 517.2 | 517 | 64.9 | 60.6 | 195.8 | 311.9 | 133.5 | 101.9 | 194.8 | 105.1 | 91.8 | 244.3 | 171.9 | 125.4 | 109.5 | 103.2 | 116.6 | 114.8 | 102.1 | 110.7 | 117.4
3888.1 | 3667.1 | -6.6 | 0 | 0 | 110.2 | 105.8 | 98 | 98.8 | 116.5 | 26.9 | 21 | 40.2 | 3.3 | 248.7 | 6.3 | 417.7 | 415.4 | 98.7 | 46.5 | 517.2 | 517.2 | 64.5 | 60.4 | 195.9 | 311.6 | 133.5 | 101.8 | 194.7 | 104.9 | 91.9 | 244 | 171.8 | 125.3 | 109.5 | 103.2 | 116.5 | 114.8 | 102 | 110.6 | 117.3
3889.1 | 3668.1 | -6.5 | 0 | 0 | 110.1 | 105.7 | 97.9 | 98.7 | 116.3 | 26.9 | 21 | 40.2 | 3.3 | 246.2 | 6.4 | 417.7 | 415.4 | 98.9 | 46.3 | 517.1 | 517.1 | 64.1 | 60.1 | 196 | 311.4 | 133.2 | 101.8 | 194.5 | 104.7 | 91.7 | 243.8 | 171.8 | 125.3 | 109.5 | 103.2 | 116.5 | 114.7 | 102 | 110.6 | 117.3
3890.1 | 3669.1 | -6.7 | 0 | 0 | 110 | 105.6 | 97.9 | 98.7 | 116 | 26.9 | 21 | 40.1 | 2.9 | 248.5 | 6.3 | 417.7 | 415.3 | 98.9 | 46.3 | 517.1 | 517 | 64 | 59.7 | 195.9 | 311.2 | 133 | 101.8 | 194.3 | 104.5 | 91.7 | 243.5 | 171.5 | 125.2 | 109.5 | 103.2 | 116.4 | 114.6 | 101.9 | 110.6 | 117.2
3891.1 | 3670.1 | -6.2 | 0 | 0 | 110 | 105.5 | 97.8 | 98.7 | 116 | 26.9 | 21 | 40.1 | 3 | 245.1 | 5.9 | 417.6 | 415.3 | 99.1 | 46.2 | 517 | 517 | 64 | 59.4 | 195.7 | 311 | 132.9 | 101.8 | 194.2 | 104.4 | 91.8 | 243.3 | 171.6 | 125.1 | 109.5 | 103.1 | 116.3 | 114.6 | 101.8 | 110.5 | 117.2
3892.1 | 3671.1 | -6.1 | 0 | 0 | 109.9 | 105.4 | 97.8 | 98.6 | 116 | 26.9 | 21 | 40 | 2.8 | 249 | 5.7 | 417.6 | 415.3 | 98.9 | 46.2 | 517 | 517.1 | 64 | 59.2 | 195.7 | 310.8 | 132.6 | 101.7 | 194 | 104.2 | 91.7 | 243 | 171.4 | 125.1 | 109.4 | 103 | 116.3 | 114.5 | 101.8 | 110.5 | 117.1
3893.1 | 3672.1 | -5.9 | 0 | 0 | 109.9 | 105.3 | 97.7 | 98.5 | 115.9 | 27 | 21 | 40 | 3.1 | 256 | 5.6 | 417.6 | 415.2 | 98.4 | 46.3 | 517 | 517.4 | 65.7 | 59 | 195.7 | 310.6 | 133 | 101.8 | 193.8 | 104.1 | 91.7 | 242.8 | 171.2 | 125 | 109.3 | 102.9 | 116.3 | 114.4 | 101.7 | 110.4 | 117.1
3894.1 | 3673.1 | -5.8 | 0 | 0 | 109.9 | 105.2 | 97.7 | 98.4 | 115.7 | 26.9 | 21 | 40 | 2.9 | 264.7 | 5.5 | 417.5 | 415.2 | 98.8 | 46.3 | 517.1 | 517.5 | 65.5 | 58.8 | 195.8 | 310.4 | 133.2 | 101.7 | 193.7 | 103.7 | 91.6 | 242.5 | 171.2 | 124.9 | 109.3 | 102.9 | 116.2 | 114.3 | 101.7 | 110.4 | 117
3895.1 | 3674.1 | -5.8 | 0 | 0 | 109.8 | 105.1 | 97.6 | 98.3 | 115.4 | 26.9 | 21 | 40 | 3.1 | 255.6 | 5.4 | 417.5 | 415.2 | 99.5 | 46.4 | 517.2 | 517.4 | 65.3 | 58.6 | 195.8 | 310.2 | 133 | 101.5 | 193.5 | 103.8 | 91.8 | 242.3 | 171 | 124.8 | 109.1 | 102.8 | 116.1 | 114.3 | 101.6 | 110.3 | 116.9
3896.1 | 3675.1 | -5.9 | 0 | 0 | 109.7 | 105 | 97.5 | 98.3 | 115.2 | 26.9 | 21 | 40.1 | 2.9 | 241.8 | 5.4 | 417.5 | 415.1 | 99.9 | 46.5 | 517.3 | 517.5 | 66 | 58.5 | 195.7 | 310 | 133.1 | 101.4 | 193.4 | 103.7 | 91.8 | 242 | 170.9 | 124.8 | 109 | 102.8 | 116 | 114.2 | 101.6 | 110.3 | 116.9
3897.1 | 3676.1 | -6.4 | 0 | 0 | 109.5 | 105 | 97.4 | 98.3 | 115.2 | 26.9 | 21 | 40.1 | 2.7 | 243.3 | 6.1 | 417.5 | 415.1 | 99.4 | 46.5 | 517.4 | 517.2 | 66.1 | 58.2 | 195.5 | 309.9 | 132.7 | 101.4 | 193.2 | 103.6 | 91.6 | 241.8 | 170.7 | 124.7 | 108.9 | 102.7 | 116 | 114.1 | 101.5 | 110.2 | 116.8
3898.1 | 3677.1 | -6.6 | 0 | 0 | 109.4 | 105 | 97.3 | 98.3 | 115.4 | 26.9 | 21 | 40.1 | 2.8 | 244.2 | 6.5 | 417.4 | 415.1 | 99.2 | 46.5 | 517.4 | 516.9 | 67.3 | 58 | 195.5 | 309.7 | 132.9 | 101.3 | 193 | 103.5 | 91.5 | 241.6 | 170.6 | 124.6 | 108.8 | 102.7 | 116 | 114 | 101.4 | 110.1 | 116.7
3899.1 | 3678.1 | -6.7 | 0 | 0 | 109.2 | 105 | 97.2 | 98.3 | 115.8 | 26.9 | 21 | 40.1 | 2.8 | 237.7 | 6.6 | 417.4 | 415.1 | 100.1 | 46.5 | 517.5 | 516.6 | 68 | 58.1 | 195.4 | 309.4 | 133.1 | 101.1 | 192.9 | 103.3 | 91.6 | 241.3 | 170.7 | 124.6 | 108.7 | 102.6 | 115.9 | 113.9 | 101.4 | 110 | 116.7
3900.1 | 3679.1 | -6.6 | 0 | 0 | 109.1 | 104.9 | 97.1 | 98.2 | 116 | 26.9 | 21 | 40.2 | 2.7 | 239.6 | 6.4 | 417.4 | 415 | 100 | 46.5 | 517.5 | 516.3 | 68.6 | 58.1 | 195.2 | 309.2 | 133.3 | 100.8 | 192.7 | 103.1 | 91.8 | 241.1 | 170.5 | 124.5 | 108.7 | 102.6 | 115.9 | 113.9 | 101.3 | 109.9 | 116.6
3901.1 | 3680.1 | -6.7 | 0 | 0 | 109.1 | 104.8 | 97.1 | 98 | 116.1 | 26.9 | 21 | 40.2 | 2.8 | 239.7 | 5.9 | 417.3 | 415 | 98.9 | 46.5 | 517.4 | 516.4 | 69.4 | 58.2 | 195.1 | 309 | 133.1 | 100.6 | 192.5 | 103.1 | 91.6 | 240.9 | 170.3 | 124.5 | 108.5 | 102.6 | 115.8 | 113.8 | 101.2 | 109.8 | 116.5
3902.1 | 3681.1 | -6.7 | 0 | 0 | 109.1 | 104.7 | 97 | 98 | 116.2 | 26.9 | 21 | 40.2 | 2.8 | 240.8 | 5.7 | 417.3 | 414.9 | 98.7 | 46.5 | 517.3 | 516.9 | 69.6 | 58.4 | 195 | 308.8 | 133.6 | 100.4 | 192.4 | 102.8 | 91.6 | 240.6 | 170.2 | 124.4 | 108.5 | 102.5 | 115.7 | 113.7 | 101.1 | 109.8 | 116.5
3903.1 | 3682.1 | -6.7 | 0 | 0 | 109 | 104.7 | 97 | 97.9 | 116 | 26.9 | 21.1 | 40.2 | 3 | 249 | 5.5 | 417.3 | 414.9 | 98.8 | 46.6 | 517.3 | 517.5 | 70.4 | 58.5 | 194.9 | 308.6 | 134 | 100.2 | 192.2 | 102.6 | 91.4 | 240.4 | 170.2 | 124.3 | 108.4 | 102.4 | 115.7 | 113.7 | 101 | 109.7 | 116.4
3904.1 | 3683.1 | -6.7 | 0 | 0 | 108.8 | 104.6 | 96.9 | 97.9 | 115.9 | 26.8 | 21.1 | 40.2 | 3 | 251.7 | 5.5 | 417.2 | 414.8 | 97.7 | 46.7 | 517.2 | 518.1 | 71.3 | 58.6 | 194.9 | 308.4 | 134.1 | 100.2 | 192 | 102.3 | 91.4 | 240.1 | 170.2 | 124.2 | 108.3 | 102.4 | 115.6 | 113.6 | 101 | 109.6 | 116.3
3905.1 | 3684.1 | -6.8 | 0 | 0 | 108.7 | 104.6 | 96.8 | 97.9 | 115.9 | 26.8 | 21.1 | 40.2 | 3 | 244.9 | 5.7 | 417.2 | 414.8 | 96.9 | 46.7 | 517.1 | 518.7 | 71.3 | 58.7 | 194.8 | 308.2 | 133.9 | 100.2 | 191.8 | 102 | 91.2 | 239.9 | 170.1 | 124.2 | 108.2 | 102.3 | 115.6 | 113.6 | 101 | 109.6 | 116.3
3906.1 | 3685.1 | -6.8 | 0 | 0 | 108.7 | 104.6 | 96.7 | 97.9 | 115.9 | 26.8 | 21.1 | 40.2 | 3.1 | 254.8 | 5.5 | 417.2 | 414.8 | 97.5 | 46.7 | 517.1 | 519.3 | 71.7 | 58.7 | 194.8 | 308 | 133.6 | 100.1 | 191.6 | 101.8 | 90.9 | 239.7 | 170.1 | 124.1 | 108.1 | 102.3 | 115.5 | 113.5 | 101 | 109.5 | 116.2
3907.1 | 3686.1 | -6.8 | 0 | 0 | 108.6 | 104.6 | 96.8 | 97.8 | 115.9 | 26.9 | 21.1 | 40.2 | 3 | 257.9 | 5.3 | 417.1 | 414.8 | 97.1 | 46.8 | 517.1 | 519.7 | 71.8 | 58.7 | 194.8 | 307.8 | 133.5 | 100.1 | 191.5 | 102 | 90.7 | 239.5 | 170 | 124 | 108 | 102.2 | 115.4 | 113.4 | 101 | 109.5 | 116.2
3908.1 | 3687.1 | -6.8 | 0 | 0 | 108.6 | 104.4 | 96.8 | 97.8 | 115.9 | 26.9 | 21 | 40.2 | 3.1 | 256.9 | 5.1 | 417.1 | 414.7 | 96.3 | 46.9 | 517.1 | 519.8 | 72.7 | 58.7 | 194.7 | 307.6 | 133.7 | 100 | 191.3 | 102.1 | 90.6 | 239.2 | 169.9 | 123.9 | 108 | 102.1 | 115.4 | 113.4 | 101 | 109.5 | 116.1
3909.1 | 3688.1 | -6.8 | 0 | 0 | 108.6 | 104.2 | 96.7 | 97.8 | 116 | 26.9 | 21 | 40.1 | 3.2 | 270.4 | 5 | 417.1 | 414.7 | 97.4 | 47 | 517.2 | 519.7 | 73.1 | 58.8 | 194.7 | 307.4 | 133.9 | 100 | 191.2 | 101.9 | 90.6 | 239 | 169.6 | 123.8 | 107.8 | 102.1 | 115.3 | 113.3 | 100.9 | 109.4 | 116.1
3910.1 | 3689.1 | -6.8 | 0 | 0 | 108.5 | 104 | 96.7 | 97.8 | 115.9 | 26.9 | 21.1 | 40.1 | 3.3 | 272.3 | 4.7 | 417 | 414.7 | 97.8 | 47 | 517.2 | 519.9 | 74.3 | 58.7 | 194.7 | 307.2 | 134.4 | 100 | 191 | 101.6 | 90.6 | 238.8 | 169.4 | 123.7 | 107.7 | 102 | 115.3 | 113.2 | 100.8 | 109.3 | 116
3911.1 | 3690.1 | -6.8 | 0 | 0 | 108.4 | 103.9 | 96.6 | 97.7 | 116 | 26.8 | 21.1 | 40.1 | 3.2 | 267.4 | 4.5 | 417 | 414.7 | 97.9 | 47.1 | 517.2 | 520.2 | 74.7 | 58.7 | 194.8 | 307 | 134.6 | 99.7 | 190.8 | 101.4 | 90.5 | 238.5 | 169.4 | 123.7 | 107.6 | 102 | 115.2 | 113.1 | 100.7 | 109.2 | 115.9
3912.1 | 3691.1 | -6.8 | 0 | 0 | 108.3 | 103.8 | 96.5 | 97.6 | 116.1 | 26.8 | 21.1 | 40.1 | 3.3 | 260.4 | 4.5 | 417 | 414.6 | 98.2 | 46.9 | 517.2 | 520.2 | 74.8 | 58.7 | 194.7 | 306.8 | 134.7 | 99.5 | 190.7 | 101.5 | 90.4 | 238.3 | 169.1 | 123.6 | 107.6 | 101.9 | 115.1 | 113 | 100.6 | 109.1 | 115.8
3913.1 | 3692.1 | -6.8 | 0 | 0 | 108.2 | 103.7 | 96.4 | 97.5 | 116.2 | 26.8 | 21.1 | 40.1 | 3.4 | 255.2 | 4.5 | 416.9 | 414.6 | 99.2 | 46.9 | 517.3 | 520.2 | 74.3 | 58.7 | 194.7 | 306.5 | 134.5 | 99.3 | 190.5 | 101.5 | 90.3 | 238.1 | 169.1 | 123.6 | 107.6 | 101.8 | 115.1 | 113 | 100.6 | 109 | 115.8
3914.1 | 3693.1 | -6.8 | 0 | 0 | 108.1 | 103.5 | 96.3 | 97.4 | 116.2 | 26.8 | 21.1 | 40.1 | 3 | 261.1 | 3.9 | 416.9 | 414.5 | 100.8 | 46.8 | 517.4 | 519.9 | 74.1 | 58.7 | 194.6 | 306.3 | 134.6 | 99 | 190.3 | 101.5 | 90.3 | 237.8 | 169.1 | 123.5 | 107.6 | 101.8 | 115 | 112.9 | 100.6 | 108.9 | 115.7
3915.1 | 3694.1 | -6.7 | 0 | 0 | 108 | 103.4 | 96.2 | 97.3 | 116.2 | 26.8 | 21.1 | 40.1 | 3.1 | 282 | 3.8 | 416.9 | 414.5 | 102 | 46.8 | 517.4 | 519.7 | 73.9 | 58.7 | 194.6 | 306.1 | 134.7 | 98.6 | 190.2 | 101.2 | 90.4 | 237.6 | 168.9 | 123.4 | 107.5 | 101.7 | 115 | 112.9 | 100.6 | 108.9 | 115.7
3916.1 | 3695.1 | -6.1 | 0 | 0 | 108 | 103.3 | 96.1 | 97.2 | 116.3 | 26.8 | 21.1 | 40.1 | 3 | 281.3 | 4.2 | 416.8 | 414.5 | 103.5 | 46.9 | 517.4 | 519.6 | 73.8 | 58.8 | 194.6 | 305.9 | 134.5 | 98.3 | 190 | 100.8 | 90.6 | 237.4 | 168.8 | 123.4 | 107.4 | 101.7 | 114.9 | 112.9 | 100.5 | 108.8 | 115.6
3917.1 | 3696.1 | -6.2 | 0 | 0 | 108 | 103.3 | 96.1 | 97.1 | 116.3 | 26.8 | 21.1 | 40.1 | 3.1 | 258.7 | 5.1 | 416.8 | 414.5 | 104 | 47 | 517.4 | 519.5 | 73.8 | 58.8 | 194.6 | 305.6 | 134.5 | 98.2 | 189.8 | 100.7 | 90.8 | 237.2 | 168.6 | 123.3 | 107.4 | 101.5 | 114.8 | 112.8 | 100.5 | 108.7 | 115.5
3918.1 | 3697.1 | -6.2 | 0 | 0 | 108 | 103.3 | 96 | 97.1 | 116.4 | 26.8 | 21.1 | 40 | 3 | 246.8 | 6.2 | 416.8 | 414.4 | 103.5 | 47 | 517.3 | 519.6 | 74.4 | 58.9 | 194.7 | 305.4 | 134.5 | 98.2 | 189.6 | 100.8 | 90.7 | 236.9 | 168.6 | 123.3 | 107.2 | 101.4 | 114.8 | 112.8 | 100.4 | 108.6 | 115.5
3919.1 | 3698.1 | -6.3 | 0 | 0 | 108 | 103.3 | 95.9 | 97 | 116.3 | 26.8 | 21.1 | 40 | 3 | 254.5 | 6.8 | 416.7 | 414.4 | 103.2 | 46.9 | 517.2 | 519.7 | 75.2 | 58.9 | 194.6 | 305.2 | 134.1 | 97.9 | 189.4 | 100.8 | 90.6 | 236.7 | 168.5 | 123.2 | 107.1 | 101.4 | 114.7 | 112.7 | 100.2 | 108.6 | 115.4
3920.1 | 3699.1 | -6.3 | 0 | 0 | 107.9 | 103.3 | 95.9 | 97 | 116 | 26.8 | 21.1 | 40 | 3.4 | 245.7 | 7 | 416.7 | 414.3 | 101.8 | 46.8 | 517 | 519.4 | 75.3 | 58.9 | 194.6 | 304.9 | 133.5 | 97.7 | 189.3 | 101 | 90.4 | 236.5 | 168.3 | 123.1 | 107 | 101.3 | 114.7 | 112.7 | 100.2 | 108.6 | 115.4
3921.1 | 3700.1 | -6.5 | 0 | 0 | 107.8 | 103.3 | 95.9 | 96.9 | 115.9 | 26.7 | 21.1 | 40 | 3.1 | 263.6 | 6.9 | 416.7 | 414.3 | 101.7 | 46.7 | 516.9 | 519.1 | 74.9 | 58.5 | 194.7 | 304.7 | 132.8 | 97.7 | 189.1 | 101 | 90.2 | 236.2 | 168.3 | 123 | 107 | 101.2 | 114.6 | 112.6 | 100.2 | 108.5 | 115.3
3922.1 | 3701.1 | -6.6 | 0 | 0 | 107.7 | 103.2 | 95.9 | 96.8 | 115.5 | 26.7 | 21.1 | 40 | 3 | 261 | 6.9 | 416.7 | 414.3 | 101.9 | 46.6 | 516.9 | 518.8 | 75.5 | 58.3 | 194.6 | 304.5 | 132.2 | 97.2 | 189 | 100.6 | 90.1 | 236 | 168.2 | 123 | 107 | 101.2 | 114.5 | 112.6 | 100.1 | 108.5 | 115.2
3923.1 | 3702.1 | -6.6 | 0 | 0 | 107.6 | 103.1 | 95.8 | 96.9 | 115.1 | 26.7 | 21.1 | 40 | 2.9 | 266 | 6.9 | 416.6 | 414.3 | 101.8 | 46.6 | 516.9 | 518.4 | 75.2 | 58.1 | 194.6 | 304.2 | 131.8 | 96.9 | 188.8 | 100.6 | 90 | 235.8 | 168 | 122.9 | 107 | 101.1 | 114.5 | 112.5 | 100 | 108.4 | 115.2
3924.1 | 3703.1 | -6.7 | 0 | 0 | 107.4 | 103.1 | 95.7 | 96.8 | 114.9 | 26.7 | 21.1 | 39.9 | 2.9 | 264 | 7 | 416.6 | 414.2 | 101.4 | 46.6 | 517 | 518 | 74.3 | 58.1 | 194.6 | 304 | 131.1 | 96.6 | 188.7 | 100.6 | 90 | 235.6 | 167.8 | 122.8 | 106.9 | 101 | 114.4 | 112.4 | 100 | 108.4 | 115.1
3925.1 | 3704.1 | -6.7 | 0 | 0 | 107.3 | 103 | 95.7 | 96.8 | 114.7 | 26.7 | 21.1 | 39.9 | 2.9 | 262.4 | 6.9 | 416.5 | 414.2 | 101.7 | 46.5 | 517.1 | 517.6 | 74.4 | 58.1 | 194.6 | 303.8 | 131.2 | 96.4 | 188.5 | 100.5 | 89.9 | 235.3 | 167.7 | 122.7 | 106.9 | 101 | 114.3 | 112.3 | 99.9 | 108.3 | 115
3926.1 | 3705.1 | -6.6 | 0 | 0 | 107.3 | 103 | 95.7 | 96.7 | 114.7 | 26.7 | 21.1 | 39.9 | 3 | 261.9 | 6.7 | 416.5 | 414.1 | 101.5 | 46.5 | 517.1 | 517.4 | 75.3 | 58 | 194.6 | 303.6 | 131 | 96.2 | 188.3 | 100.5 | 89.6 | 235.1 | 167.7 | 122.7 | 106.9 | 101 | 114.2 | 112.3 | 99.8 | 108.3 | 115
3927.1 | 3706.1 | -6.7 | 0 | 0 | 107.3 | 103 | 95.6 | 96.6 | 114.7 | 26.6 | 21.1 | 39.9 | 3.2 | 263.4 | 6.3 | 416.5 | 414.1 | 101.3 | 46.6 | 517.2 | 517.3 | 75.1 | 58 | 194.6 | 303.3 | 130.9 | 96 | 188.2 | 100.4 | 89.3 | 234.9 | 167.7 | 122.6 | 106.9 | 100.9 | 114.2 | 112.2 | 99.8 | 108.2 | 114.9
3928.1 | 3707.1 | -6.8 | 0 | 0 | 107.3 | 102.9 | 95.5 | 96.5 | 114.5 | 26.6 | 21.1 | 39.9 | 3.9 | 268.7 | 6 | 416.4 | 414.1 | 101.7 | 46.6 | 517.3 | 517.1 | 74.4 | 58.2 | 194.7 | 303.1 | 130.7 | 95.8 | 188 | 100.4 | 89.2 | 234.7 | 167.6 | 122.6 | 106.8 | 100.9 | 114.2 | 112.2 | 99.7 | 108.2 | 114.9
3929.1 | 3708.1 | -6.8 | 0 | 0 | 107.2 | 102.9 | 95.4 | 96.4 | 114.3 | 26.6 | 21.1 | 39.9 | 3.7 | 268.7 | 6.2 | 416.4 | 414 | 102 | 46.7 | 517.4 | 516.9 | 74 | 58.2 | 194.7 | 302.9 | 130.2 | 95.9 | 187.8 | 100.6 | 89.3 | 234.4 | 167.3 | 122.5 | 106.7 | 100.9 | 114.2 | 112.1 | 99.6 | 108.2 | 114.8
3930.1 | 3709.1 | -6.8 | 0 | 0 | 107 | 103 | 95.2 | 96.3 | 114.5 | 26.7 | 21.1 | 39.9 | 3.9 | 266.2 | 6.7 | 416.4 | 414 | 102 | 46.6 | 517.3 | 516.9 | 73.3 | 57.9 | 194.7 | 302.7 | 129.7 | 95.8 | 187.6 | 100.5 | 89 | 234.2 | 167.2 | 122.4 | 106.6 | 100.8 | 114.1 | 112 | 99.5 | 108.1 | 114.7
3931.1 | 3710.1 | -6.7 | 0 | 0 | 106.9 | 103.2 | 95.1 | 96.3 | 114.6 | 26.7 | 21.1 | 39.9 | 3.7 | 265.2 | 7 | 416.3 | 413.9 | 102.9 | 46.4 | 517.3 | 516.8 | 72.8 | 57.5 | 194.8 | 302.5 | 129.7 | 95.6 | 187.5 | 100.2 | 88.9 | 234 | 167.1 | 122.4 | 106.5 | 100.8 | 114 | 112 | 99.4 | 108.1 | 114.7
3932.1 | 3711.1 | -6.6 | 0 | 0 | 106.7 | 103.2 | 95 | 96.3 | 114.7 | 26.7 | 21.1 | 39.9 | 3.5 | 258.4 | 7.2 | 416.3 | 413.9 | 103 | 46.3 | 517.3 | 516.9 | 71.6 | 57.3 | 194.8 | 302.2 | 129.7 | 95.4 | 187.3 | 100 | 88.7 | 233.8 | 166.9 | 122.3 | 106.4 | 100.7 | 114 | 112 | 99.4 | 108 | 114.6
3933.1 | 3712.1 | -6.5 | 0 | 0 | 106.5 | 103.1 | 95.2 | 96.3 | 114.8 | 26.7 | 21.1 | 39.9 | 3.7 | 250.9 | 6.7 | 416.3 | 413.8 | 102.9 | 46 | 517.4 | 517 | 70.7 | 57 | 194.8 | 302 | 129.6 | 95.3 | 187.1 | 99.6 | 88.4 | 233.6 | 166.9 | 122.2 | 106.3 | 100.6 | 113.9 | 111.9 | 99.3 | 107.9 | 114.5
3934.1 | 3713.1 | -6.4 | 0 | 0 | 106.5 | 102.8 | 95.2 | 96.1 | 114.9 | 26.7 | 21.1 | 39.8 | 3.4 | 256.3 | 6.3 | 416.2 | 413.8 | 103.2 | 46 | 517.5 | 517 | 71 | 57 | 194.6 | 301.8 | 129.4 | 95.1 | 187 | 99.4 | 88.2 | 233.3 | 166.7 | 122.2 | 106.2 | 100.5 | 113.8 | 111.9 | 99.3 | 107.9 | 114.5
3935.1 | 3714.1 | -6.5 | 0 | 0 | 106.6 | 102.5 | 95 | 96 | 114.7 | 26.7 | 21.1 | 39.8 | 2.7 | 244.7 | 6.3 | 416.2 | 413.8 | 103.2 | 45.9 | 517.6 | 516.8 | 71.3 | 57.1 | 194.7 | 301.6 | 129.3 | 94.8 | 186.8 | 99.3 | 87.9 | 233.1 | 166.5 | 122.1 | 106.2 | 100.5 | 113.8 | 111.8 | 99.2 | 107.8 | 114.4
3936.1 | 3715.1 | -6.4 | 0 | 0 | 106.6 | 102.4 | 94.9 | 96.1 | 115 | 26.7 | 21.1 | 39.8 | 3 | 273.2 | 5.6 | 416.2 | 413.7 | 103.9 | 45.8 | 517.6 | 516.7 | 70.8 | 57.4 | 194.8 | 301.3 | 128.9 | 94.6 | 186.6 | 99.3 | 87.8 | 232.9 | 166.4 | 122.1 | 106.2 | 100.5 | 113.8 | 111.8 | 99.2 | 107.8 | 114.4
3937.1 | 3716.1 | -6.5 | 0 | 0 | 106.6 | 102.4 | 95 | 96.1 | 115.2 | 26.6 | 21.1 | 39.7 | 3.1 | 272.5 | 5.7 | 416.1 | 413.7 | 103.9 | 45.8 | 517.7 | 516.5 | 70.1 | 57.7 | 194.8 | 301.1 | 128.4 | 94.3 | 186.4 | 99.4 | 87.6 | 232.7 | 166.2 | 122 | 106.2 | 100.5 | 113.7 | 111.8 | 99.2 | 107.7 | 114.3
3938.1 | 3717.1 | -6.5 | 0 | 0 | 106.5 | 102.4 | 95.1 | 96.1 | 115.2 | 26.7 | 21.1 | 39.7 | 3.8 | 253.3 | 6.6 | 416.1 | 413.7 | 103.7 | 45.7 | 517.7 | 516.3 | 69.8 | 57.6 | 194.8 | 300.9 | 128.1 | 94.1 | 186.3 | 99.3 | 87.5 | 232.5 | 166.2 | 121.9 | 106 | 100.4 | 113.6 | 111.8 | 99.2 | 107.6 | 114.2
3939.1 | 3718.1 | -6.5 | 0 | 0 | 106.3 | 102.4 | 94.9 | 96.1 | 115.2 | 26.6 | 21.1 | 39.6 | 3.7 | 234.5 | 7.6 | 416.1 | 413.6 | 103 | 45.6 | 517.7 | 516.4 | 69.9 | 57.6 | 194.8 | 300.6 | 128 | 94 | 186.1 | 99 | 87.3 | 232.3 | 166.1 | 121.9 | 105.8 | 100.3 | 113.5 | 111.7 | 99.2 | 107.5 | 114.2
3940.1 | 3719.1 | -6.6 | 0 | 0 | 105.9 | 102.2 | 94.6 | 96.1 | 115.3 | 26.6 | 21.1 | 39.6 | 4.3 | 237 | 7.7 | 416 | 413.6 | 102.4 | 45.3 | 517.6 | 516.9 | 70.4 | 57.4 | 194.8 | 300.4 | 127.7 | 94 | 185.9 | 98.8 | 87.2 | 232 | 166.1 | 121.8 | 105.6 | 100.2 | 113.4 | 111.7 | 99.1 | 107.5 | 114.1
3941.1 | 3720.1 | -6.7 | 0 | 0 | 105.6 | 102 | 94.5 | 96.2 | 115.3 | 26.6 | 21.1 | 39.5 | 4.3 | 236.4 | 7.2 | 416 | 413.6 | 102.1 | 45.1 | 517.5 | 517.3 | 70.4 | 57.3 | 194.7 | 300.2 | 127.4 | 93.8 | 185.7 | 98.7 | 87 | 231.8 | 166 | 121.7 | 105.6 | 100.2 | 113.3 | 111.7 | 99 | 107.4 | 114
3942.1 | 3721.1 | -6.7 | 0 | 0 | 105.5 | 101.8 | 94.6 | 96.2 | 115.2 | 26.6 | 21.1 | 39.5 | 4.1 | 237.1 | 6.9 | 416 | 413.5 | 101.2 | 44.9 | 517.4 | 517.4 | 70 | 57.1 | 194.6 | 299.9 | 127 | 93.8 | 185.5 | 98.8 | 87.2 | 231.6 | 165.8 | 121.6 | 105.5 | 100.3 | 113.3 | 111.6 | 99 | 107.4 | 114
3943.1 | 3722.1 | -6.7 | 0 | 0 | 105.2 | 101.8 | 94.6 | 96.2 | 115 | 26.6 | 21.1 | 39.4 | 3.5 | 239.7 | 6.8 | 415.9 | 413.5 | 101.6 | 44.8 | 517.3 | 517.5 | 69.8 | 57 | 194.6 | 299.7 | 126.2 | 93.7 | 185.3 | 99.3 | 87 | 231.3 | 165.6 | 121.6 | 105.5 | 100.3 | 113.3 | 111.6 | 98.9 | 107.4 | 113.9
3944.1 | 3723.1 | -6.7 | 0 | 0 | 105 | 102 | 94.6 | 96 | 114.8 | 26.5 | 21.1 | 39.4 | 3.4 | 234 | 6.3 | 415.9 | 413.4 | 102.1 | 44.7 | 517.3 | 517.7 | 69.2 | 56.9 | 194.5 | 299.5 | 125.9 | 93.6 | 185.2 | 99.6 | 86.8 | 231.1 | 165.5 | 121.5 | 105.5 | 100.2 | 113.3 | 111.6 | 98.9 | 107.3 | 113.9
3945.1 | 3724.1 | -6.7 | 0 | 0 | 105 | 102 | 94.6 | 96 | 114.7 | 26.5 | 21.1 | 39.3 | 3.3 | 240.9 | 5.7 | 415.9 | 413.4 | 101.3 | 44.5 | 517.2 | 517.6 | 69.3 | 56.9 | 194.4 | 299.2 | 125.1 | 93.5 | 185 | 99.3 | 86.7 | 230.9 | 165.5 | 121.5 | 105.4 | 100 | 113.2 | 111.5 | 98.8 | 107.2 | 113.8
3946.1 | 3725.1 | -6.8 | 0 | 0 | 104.9 | 102.2 | 94.6 | 96.1 | 114.5 | 26.5 | 21.1 | 39.3 | 3 | 236.1 | 5.1 | 415.8 | 413.4 | 100.8 | 44.3 | 517.1 | 517.3 | 68.9 | 56.8 | 194.3 | 299 | 124.7 | 93.2 | 184.8 | 99.2 | 86.5 | 230.7 | 165.2 | 121.4 | 105.3 | 99.9 | 113.1 | 111.5 | 98.8 | 107.1 | 113.7
3947.1 | 3726.1 | -6.7 | 0 | 0 | 104.9 | 102.2 | 94.6 | 96.2 | 114.5 | 26.5 | 21.1 | 39.2 | 2.7 | 249.3 | 5.6 | 415.8 | 413.3 | 100.9 | 44.2 | 517 | 517.1 | 68.6 | 56.7 | 194.2 | 298.7 | 124.6 | 93.1 | 184.7 | 99 | 86.5 | 230.5 | 165.2 | 121.3 | 105.2 | 99.8 | 113 | 111.5 | 98.7 | 107.1 | 113.7
3948.1 | 3727.1 | -6.7 | 0 | 0 | 104.9 | 101.9 | 94.4 | 96.2 | 114.6 | 26.5 | 21.1 | 39.2 | 2.8 | 241.8 | 5.4 | 415.7 | 413.3 | 100.3 | 44.1 | 516.9 | 517.2 | 68.2 | 56.6 | 194.1 | 298.5 | 124.7 | 93.1 | 184.5 | 98.6 | 86.6 | 230.3 | 165.1 | 121.3 | 105.2 | 99.8 | 113 | 111.4 | 98.6 | 107 | 113.6
3949.1 | 3728.1 | -6.7 | 0 | 0 | 104.8 | 101.5 | 94.2 | 96.1 | 114.7 | 26.5 | 21.1 | 39.1 | 2.8 | 283.4 | 5.2 | 415.7 | 413.3 | 99.8 | 44 | 516.8 | 517.8 | 68.2 | 56.6 | 194 | 298.3 | 124.4 | 93 | 184.3 | 98.3 | 86.6 | 230 | 165 | 121.2 | 105.1 | 99.8 | 112.9 | 111.3 | 98.4 | 106.9 | 113.5
3950.1 | 3729.1 | -6.7 | 0 | 0 | 104.8 | 101.3 | 94.1 | 95.9 | 114.8 | 26.5 | 21.1 | 39 | 2.7 | 281.2 | 4.9 | 415.7 | 413.2 | 99.2 | 43.9 | 516.7 | 518.4 | 68.3 | 56.4 | 194 | 298 | 124.5 | 93 | 184.2 | 98.1 | 86.5 | 229.8 | 165.1 | 121.2 | 105.1 | 99.8 | 112.9 | 111.2 | 98.3 | 106.8 | 113.5
3951.1 | 3730.1 | -6.7 | 0 | 0 | 104.7 | 101.2 | 94.1 | 95.5 | 114.8 | 26.5 | 21.1 | 38.9 | 2.6 | 233.9 | 4.7 | 415.6 | 413.2 | 98.2 | 43.8 | 516.5 | 518.8 | 68.5 | 56.1 | 193.7 | 297.8 | 124.5 | 92.8 | 184 | 97.9 | 86.4 | 229.6 | 164.8 | 121.2 | 105 | 99.7 | 112.8 | 111.2 | 98.2 | 106.8 | 113.4
3952.1 | 3731.1 | -6.7 | 0 | 0 | 104.8 | 101.2 | 94.1 | 95.3 | 114.9 | 26.5 | 21.1 | 38.8 | 2.6 | 245.5 | 4.8 | 415.6 | 413.2 | 98.3 | 43.6 | 516.3 | 519 | 68 | 55.8 | 193.5 | 297.6 | 124.6 | 92.8 | 183.9 | 97.8 | 86.3 | 229.4 | 164.8 | 121.1 | 104.9 | 99.6 | 112.7 | 111.1 | 98.2 | 106.7 | 113.3
3953.1 | 3732.1 | -6.7 | 0 | 0 | 104.9 | 101.2 | 94.1 | 95.3 | 114.7 | 26.5 | 21.1 | 38.8 | 2.6 | 251.3 | 4.8 | 415.6 | 413.1 | 98.3 | 43.3 | 516 | 519.2 | 67.5 | 55.5 | 193.6 | 297.4 | 124.8 | 92.8 | 183.7 | 97.8 | 86.2 | 229.2 | 164.6 | 121 | 104.9 | 99.5 | 112.7 | 111.1 | 98.2 | 106.7 | 113.3
3954.1 | 3733.1 | -6.7 | 0 | 0 | 104.9 | 101.2 | 93.7 | 95.4 | 114.6 | 26.4 | 21.1 | 38.7 | 2.7 | 263.3 | 4.4 | 415.5 | 413.1 | 97.9 | 43.1 | 515.9 | 519.1 | 67.2 | 55.3 | 193.5 | 297.2 | 124.8 | 92.5 | 183.6 | 97.6 | 86.2 | 229 | 164.4 | 121 | 104.8 | 99.5 | 112.6 | 111.1 | 98.3 | 106.6 | 113.2
3955.1 | 3734.1 | -6.7 | 0 | 0 | 104.9 | 101.3 | 93.3 | 95.4 | 114.6 | 26.3 | 21.1 | 38.7 | 2.5 | 274.4 | 5.1 | 415.5 | 413.1 | 98.2 | 43.1 | 515.8 | 518.8 | 66.7 | 55.4 | 193.5 | 296.9 | 124.6 | 92.3 | 183.4 | 97.3 | 86.2 | 228.7 | 164.4 | 121 | 104.8 | 99.4 | 112.5 | 111.1 | 98.2 | 106.5 | 113.2
3956.1 | 3735.1 | -6.7 | 0 | 0 | 104.9 | 101.2 | 93 | 95.3 | 114.6 | 26.3 | 21.1 | 38.6 | 2.8 | 256.6 | 5.6 | 415.5 | 413 | 98.3 | 43 | 515.7 | 518.7 | 66.4 | 55.4 | 193.4 | 296.7 | 124.9 | 92.3 | 183.3 | 97.2 | 86.3 | 228.5 | 164.3 | 120.9 | 104.7 | 99.3 | 112.4 | 111.1 | 98.2 | 106.5 | 113.1
3957.1 | 3736.1 | -6.7 | 0 | 0 | 104.8 | 101.2 | 93.1 | 95.2 | 114.5 | 26.2 | 21.1 | 38.5 | 3.2 | 258.7 | 5.8 | 415.4 | 413 | 97 | 43.1 | 515.7 | 518.9 | 65.7 | 55.5 | 193.3 | 296.5 | 125.2 | 92.2 | 183.2 | 97.1 | 86.3 | 228.3 | 164.3 | 120.9 | 104.6 | 99.3 | 112.3 | 111 | 98.2 | 106.4 | 113
3958.1 | 3737.1 | -6.7 | 0 | 0 | 104.6 | 101.2 | 93.2 | 95 | 114.4 | 26.2 | 21.1 | 38.5 | 3.6 | 262 | 5.5 | 415.4 | 413 | 96.2 | 43.1 | 515.6 | 519 | 65 | 55.7 | 193.3 | 296.2 | 125.3 | 92.1 | 183 | 97 | 86.4 | 228.1 | 164.3 | 120.9 | 104.5 | 99.2 | 112.3 | 111 | 98.2 | 106.4 | 113
3959.1 | 3738.1 | -6.6 | 0 | 0 | 104.4 | 101.2 | 93.1 | 95.1 | 114.4 | 26.2 | 21.1 | 38.4 | 3.9 | 267.9 | 4.8 | 415.4 | 412.9 | 96.6 | 43.3 | 515.6 | 518.8 | 64.6 | 55.8 | 193.2 | 296 | 125.5 | 91.7 | 182.9 | 97.1 | 86.6 | 227.9 | 164.3 | 120.8 | 104.5 | 99.2 | 112.2 | 110.9 | 98.1 | 106.3 | 112.9
3960.1 | 3739.1 | -6.6 | 0 | 0 | 104.3 | 101.1 | 92.8 | 95.2 | 114.4 | 26.2 | 21.1 | 38.4 | 3.8 | 264.6 | 4.9 | 415.3 | 412.9 | 96.6 | 43.3 | 515.6 | 518.6 | 64.1 | 55.7 | 193 | 295.7 | 124.7 | 91.5 | 182.8 | 97.4 | 86.6 | 227.7 | 164.4 | 120.7 | 104.4 | 99.1 | 112.2 | 110.8 | 98 | 106.3 | 112.9
3961.1 | 3740.1 | -6.6 | 0 | 0 | 104.3 | 100.9 | 92.6 | 95.2 | 114.3 | 26.1 | 21.1 | 38.4 | 3.6 | 268.6 | 5.5 | 415.3 | 412.8 | 96.7 | 43.2 | 515.5 | 518.3 | 63.6 | 55.7 | 193 | 295.5 | 123.9 | 91.3 | 182.7 | 97.3 | 86.5 | 227.5 | 164.4 | 120.6 | 104.3 | 99 | 112.1 | 110.8 | 97.9 | 106.2 | 112.8
3962.1 | 3741.1 | -6.5 | 0 | 0 | 104.2 | 100.7 | 92.5 | 95.1 | 114.1 | 26.1 | 21.1 | 38.4 | 3.7 | 275.3 | 5.7 | 415.3 | 412.8 | 96.9 | 43.2 | 515.4 | 518 | 63.1 | 55.6 | 193 | 295.2 | 123.4 | 91.2 | 182.7 | 97.2 | 86.2 | 227.3 | 164.3 | 120.6 | 104.3 | 99 | 112.1 | 110.7 | 97.8 | 106.2 | 112.7
3963.1 | 3742.1 | -6.6 | 0 | 0 | 104.1 | 100.6 | 92.7 | 95.1 | 114.1 | 26 | 21.1 | 38.4 | 3.2 | 255.4 | 6.7 | 415.2 | 412.8 | 97.3 | 43.1 | 515.3 | 517.8 | 62.6 | 55.6 | 193 | 295 | 122.6 | 91.2 | 182.6 | 97.5 | 86.2 | 227.1 | 164.3 | 120.5 | 104.3 | 99 | 112 | 110.7 | 97.7 | 106.1 | 112.7
3964.1 | 3743.1 | -6.7 | 0 | 0 | 103.9 | 100.6 | 92.8 | 94.9 | 114.2 | 25.9 | 21.1 | 38.3 | 3.4 | 256.6 | 7.1 | 415.2 | 412.7 | 97.7 | 43.1 | 515.3 | 517.5 | 62 | 55.5 | 192.9 | 294.8 | 122.3 | 91 | 182.6 | 98 | 86 | 226.9 | 164.3 | 120.4 | 104.3 | 98.9 | 112 | 110.6 | 97.6 | 106 | 112.6
3965.1 | 3744.1 | -6.7 | 0 | 0 | 103.8 | 100.5 | 92.9 | 94.7 | 114.2 | 26 | 21.1 | 38.3 | 3.3 | 258.7 | 7 | 415.2 | 412.7 | 97.7 | 43.1 | 515.2 | 517.2 | 61.6 | 55.5 | 192.8 | 294.5 | 121.7 | 91 | 182.5 | 98.2 | 86.1 | 226.7 | 164.2 | 120.4 | 104.3 | 98.8 | 111.9 | 110.6 | 97.5 | 105.9 | 112.6
3966.1 | 3745.1 | -6.7 | 0 | 0 | 103.7 | 100.3 | 92.8 | 94.6 | 114.2 | 25.9 | 21.1 | 38.3 | 3.6 | 263 | 6.6 | 415.1 | 412.7 | 97.7 | 43.1 | 515.3 | 516.9 | 61.2 | 55.5 | 192.8 | 294.3 | 120.9 | 90.9 | 182.4 | 98.1 | 86.1 | 226.4 | 164.1 | 120.3 | 104.2 | 98.7 | 111.8 | 110.6 | 97.5 | 105.9 | 112.5
3967.1 | 3746.1 | -6.7 | 0 | 0 | 103.6 | 100.3 | 92.6 | 94.5 | 114.2 | 25.9 | 21.1 | 38.2 | 3.5 | 261.5 | 5.7 | 415.1 | 412.6 | 98.6 | 43.1 | 515.3 | 516.6 | 60.9 | 55.6 | 192.8 | 294 | 120.1 | 91 | 182.3 | 98.5 | 86.1 | 226.2 | 163.9 | 120.2 | 104.2 | 98.6 | 111.8 | 110.6 | 97.5 | 105.8 | 112.4
3968.1 | 3747.1 | -6.7 | 0 | 0 | 103.6 | 100.3 | 92.5 | 94.4 | 114 | 25.9 | 21.1 | 38.2 | 3 | 240 | 5 | 415.1 | 412.6 | 98.8 | 43.1 | 515.3 | 516.6 | 60.5 | 55.7 | 192.8 | 293.7 | 119.3 | 90.9 | 182.2 | 98.8 | 86 | 226 | 163.9 | 120.1 | 104.1 | 98.6 | 111.7 | 110.5 | 97.4 | 105.8 | 112.4
3969.1 | 3748.1 | -6.7 | 0 | 0 | 103.6 | 100.3 | 92.6 | 94.2 | 113.6 | 25.9 | 21.1 | 38.2 | 3.1 | 221.6 | 4.7 | 415 | 412.5 | 98.5 | 43.2 | 515.3 | 516.5 | 60.2 | 55.6 | 192.7 | 293.5 | 118.7 | 91 | 182.1 | 98.9 | 85.9 | 225.8 | 163.9 | 120.1 | 104.1 | 98.6 | 111.7 | 110.4 | 97.3 | 105.7 | 112.3
3970.1 | 3749.1 | -6.6 | 0 | 0 | 103.7 | 100.2 | 92.6 | 94.2 | 113.1 | 25.9 | 21.1 | 38.1 | 3.2 | 235 | 4.9 | 415 | 412.5 | 98.4 | 43.2 | 515.2 | 516.3 | 60 | 55.5 | 192.6 | 293.2 | 118.2 | 91 | 182.1 | 99.2 | 85.8 | 225.6 | 164 | 120 | 104.1 | 98.6 | 111.6 | 110.4 | 97.2 | 105.6 | 112.3
3971.1 | 3750.1 | -6.6 | 0 | 0 | 103.6 | 100.1 | 92.7 | 94.2 | 113 | 26 | 21.1 | 38 | 2.7 | 252.7 | 5.1 | 415 | 412.4 | 99.3 | 43.1 | 515.3 | 516.2 | 60.1 | 55.6 | 192.5 | 292.9 | 118.3 | 90.7 | 181.9 | 99.4 | 85.8 | 225.4 | 164 | 120 | 104.1 | 98.5 | 111.6 | 110.3 | 97.1 | 105.6 | 112.2
3972.1 | 3751.1 | -6.6 | 0 | 0 | 103.5 | 100.1 | 92.7 | 94.2 | 113.2 | 26 | 21.1 | 37.9 | 2.8 | 238.2 | 4.9 | 414.9 | 412.4 | 99.3 | 43.2 | 515.3 | 516.3 | 60.3 | 55.6 | 192.5 | 292.7 | 118.2 | 90.6 | 181.8 | 99.2 | 85.8 | 225.2 | 163.8 | 119.9 | 104.1 | 98.4 | 111.5 | 110.2 | 97 | 105.5 | 112.1
3973.1 | 3752.1 | -6.7 | 0 | 0 | 103.3 | 100.3 | 92.6 | 94.1 | 113.4 | 26 | 21.1 | 37.8 | 3.1 | 234.5 | 4.7 | 414.9 | 412.4 | 98.8 | 43.2 | 515.2 | 516.8 | 60 | 55.5 | 192.4 | 292.4 | 117.8 | 90.5 | 181.7 | 99.1 | 85.8 | 225 | 163.8 | 119.9 | 104 | 98.4 | 111.5 | 110.2 | 96.9 | 105.4 | 112.1
3974.1 | 3753.1 | -6.7 | 0 | 0 | 103.2 | 100.4 | 92.6 | 94 | 113.2 | 26.1 | 21.1 | 37.8 | 3 | 245.1 | 4.5 | 414.9 | 412.3 | 98.3 | 43.1 | 515.1 | 517.3 | 59.7 | 55.5 | 192.4 | 292.1 | 117.7 | 90.4 | 181.6 | 99.1 | 85.8 | 224.8 | 163.7 | 119.8 | 103.9 | 98.4 | 111.4 | 110.1 | 96.8 | 105.4 | 112
3975.1 | 3754.1 | -6.7 | 0 | 0 | 103.1 | 100.4 | 92.5 | 93.9 | 112.7 | 26.2 | 21.1 | 37.7 | 3.2 | 250.1 | 5 | 414.9 | 412.2 | 98.2 | 43.2 | 515 | 517.6 | 59.3 | 55.7 | 192.4 | 291.8 | 117.2 | 90.4 | 181.5 | 99.2 | 85.9 | 224.6 | 163.7 | 119.8 | 103.7 | 98.3 | 111.4 | 110 | 96.8 | 105.3 | 112
3976.1 | 3755.1 | -6.8 | 0 | 0 | 103 | 100.3 | 92.5 | 93.9 | 112.2 | 26.1 | 21.1 | 37.6 | 3.3 | 254.2 | 6.1 | 414.8 | 412.2 | 98.5 | 43.3 | 515 | 517.8 | 59.1 | 55.8 | 192.3 | 291.6 | 116.6 | 90.1 | 181.4 | 99.1 | 85.9 | 224.4 | 163.8 | 119.7 | 103.6 | 98.2 | 111.3 | 110 | 96.8 | 105.2 | 111.9
3977.1 | 3756.1 | -6.7 | 0 | 0 | 102.8 | 100.3 | 92.6 | 93.9 | 112.1 | 26.1 | 21.1 | 37.5 | 3.2 | 249.8 | 5.9 | 414.8 | 412.2 | 98.7 | 43.4 | 514.9 | 517.8 | 58.8 | 55.8 | 192.3 | 291.3 | 116 | 89.8 | 181.3 | 99.2 | 85.9 | 224.2 | 163.7 | 119.6 | 103.6 | 98.2 | 111.2 | 110 | 96.8 | 105.2 | 111.8
3978.1 | 3757.1 | -6.7 | 0 | 0 | 102.6 | 100.3 | 92.6 | 93.9 | 112.1 | 26.1 | 21.1 | 37.4 | 3.5 | 253.8 | 5.8 | 414.8 | 412.1 | 99.1 | 43.5 | 514.9 | 517.6 | 58.4 | 55.8 | 192.3 | 291 | 116 | 89.8 | 181.1 | 99.4 | 85.8 | 224 | 163.6 | 119.6 | 103.5 | 98.2 | 111.2 | 109.9 | 96.8 | 105.1 | 111.8
3979.1 | 3758.1 | -6.6 | 0 | 0 | 102.5 | 100.2 | 92.7 | 93.9 | 112.3 | 26.2 | 21.1 | 37.3 | 3.2 | 275.1 | 6.1 | 414.7 | 412.1 | 99 | 43.4 | 514.9 | 517.2 | 58.2 | 55.9 | 192.3 | 290.8 | 115.9 | 89.8 | 180.9 | 99.4 | 86.1 | 223.8 | 163.5 | 119.5 | 103.5 | 98.2 | 111.1 | 109.8 | 96.7 | 105 | 111.7
3980.1 | 3759.1 | -6.6 | 0 | 0 | 102.4 | 100.1 | 92.6 | 93.8 | 112.4 | 26.2 | 21.1 | 37.1 | 3.5 | 260.4 | 6.4 | 414.7 | 412.1 | 99.7 | 43.4 | 514.9 | 516.7 | 58.1 | 56 | 192.3 | 290.5 | 115.5 | 89.9 | 180.8 | 99.7 | 86.3 | 223.6 | 163.3 | 119.5 | 103.5 | 98.1 | 111 | 109.7 | 96.6 | 104.9 | 111.6
3981.1 | 3760.1 | -6.6 | 0 | 0 | 102.5 | 99.9 | 92.6 | 93.8 | 112.4 | 26.3 | 21.1 | 37 | 3.4 | 247.2 | 6.1 | 414.7 | 412.1 | 100.2 | 43.4 | 514.9 | 516.3 | 57.9 | 56.2 | 192.2 | 290.2 | 115.1 | 89.9 | 180.7 | 99.7 | 86.2 | 223.4 | 163.3 | 119.3 | 103.4 | 98 | 110.9 | 109.7 | 96.5 | 104.8 | 111.6
3982.1 | 3761.1 | -6.6 | 0 | 0 | 102.6 | 99.8 | 92.6 | 93.7 | 112.4 | 26.3 | 21.1 | 37 | 3.5 | 260 | 5.6 | 414.7 | 412 | 100.5 | 43.4 | 514.9 | 516 | 57.7 | 56.4 | 192.2 | 290 | 114.8 | 89.9 | 180.6 | 99.6 | 86.1 | 223.1 | 163.2 | 119.3 | 103.4 | 98 | 110.9 | 109.6 | 96.5 | 104.8 | 111.5
3983.1 | 3762.1 | -6.3 | 0 | 0 | 102.6 | 99.8 | 92.5 | 93.6 | 112 | 26.4 | 21.1 | 36.8 | 3.1 | 265.3 | 5.2 | 414.6 | 412 | 100.2 | 43.5 | 514.9 | 515.8 | 57.5 | 56.7 | 192.2 | 289.7 | 114.7 | 89.8 | 180.4 | 99.8 | 86 | 222.9 | 163.2 | 119.3 | 103.3 | 98 | 110.9 | 109.6 | 96.5 | 104.8 | 111.5
3984.1 | 3763.1 | -6.6 | 0 | 0 | 102.6 | 99.9 | 92.4 | 93.5 | 111.6 | 26.5 | 21.1 | 36.8 | 3.5 | 258.7 | 4.8 | 414.6 | 412 | 99.8 | 43.6 | 514.9 | 516.1 | 57.2 | 56.7 | 192.3 | 289.4 | 114.6 | 89.6 | 180.3 | 99.9 | 86 | 222.7 | 163.1 | 119.2 | 103.3 | 98 | 110.8 | 109.5 | 96.4 | 104.7 | 111.4
3985.1 | 3764.1 | -6.6 | 0 | 0 | 102.4 | 99.9 | 92.4 | 93.4 | 111.3 | 26.6 | 21.1 | 36.7 | 3.2 | 261.4 | 4.2 | 414.6 | 411.9 | 100.3 | 43.6 | 514.9 | 516.3 | 56.9 | 56.5 | 192.2 | 289.2 | 114.4 | 89.6 | 180.2 | 100 | 86.2 | 222.5 | 163.1 | 119.1 | 103.2 | 97.9 | 110.7 | 109.4 | 96.4 | 104.7 | 111.4
3986.1 | 3765.1 | -6.7 | 0 | 0 | 102.1 | 99.8 | 92.4 | 93.3 | 111.1 | 26.6 | 21.1 | 36.7 | 3.2 | 264.1 | 3.5 | 414.5 | 411.9 | 99.2 | 43.6 | 514.9 | 516.3 | 56.7 | 56.5 | 192.2 | 288.9 | 114.2 | 89.5 | 180 | 99.9 | 86.1 | 222.4 | 163.1 | 119.1 | 103.1 | 97.9 | 110.7 | 109.4 | 96.3 | 104.7 | 111.3
3987.1 | 3766.1 | -6.7 | 0 | 0 | 101.9 | 99.7 | 92.5 | 93.4 | 111.3 | 26.6 | 21.1 | 36.7 | 3.5 | 265.4 | 3.7 | 414.5 | 411.8 | 99.3 | 43.5 | 514.9 | 516.4 | 56.7 | 56.6 | 192.2 | 288.7 | 114.1 | 89.5 | 179.9 | 99.8 | 86.1 | 222.2 | 163.1 | 119 | 103.1 | 97.9 | 110.6 | 109.4 | 96.4 | 104.7 | 111.2
3988.1 | 3767.1 | -6.8 | 0 | 0 | 101.8 | 99.6 | 92.5 | 93.5 | 111 | 26.6 | 21.1 | 36.6 | 3.4 | 272.9 | 4 | 414.5 | 411.8 | 99.1 | 43.5 | 515 | 517.3 | 56.6 | 56.8 | 192.2 | 288.4 | 113.5 | 89.7 | 179.7 | 100.1 | 86.2 | 222 | 163 | 119 | 103.1 | 97.9 | 110.5 | 109.3 | 96.4 | 104.6 | 111.2
3989.1 | 3768.1 | -6.8 | 0 | 0 | 101.7 | 99.5 | 92.4 | 93.5 | 110.6 | 26.6 | 21.1 | 36.6 | 3.3 | 275.4 | 4 | 414.4 | 411.7 | 99.3 | 43.5 | 515 | 519 | 56.5 | 57.1 | 192.1 | 288.1 | 113.2 | 89.4 | 179.6 | 100.1 | 86 | 221.8 | 163 | 118.9 | 103 | 97.8 | 110.5 | 109.3 | 96.3 | 104.6 | 111.1
3990.1 | 3769.1 | -6.8 | 0 | 0 | 101.6 | 99.4 | 92.1 | 93.4 | 110.4 | 26.6 | 21.1 | 36.5 | 3.8 | 273.7 | 3.9 | 414.4 | 411.7 | 99.4 | 43.5 | 514.9 | 520.8 | 56.6 | 57.3 | 192.1 | 287.8 | 112.7 | 89.3 | 179.5 | 100.3 | 85.8 | 221.6 | 162.9 | 118.8 | 103 | 97.8 | 110.5 | 109.2 | 96.2 | 104.5 | 111.1
3991.1 | 3770.1 | -6.8 | 0 | 0 | 101.6 | 99.4 | 92.2 | 93.3 | 110.7 | 26.7 | 21.1 | 36.5 | 3.5 | 271.8 | 4.2 | 414.4 | 411.7 | 99.5 | 43.6 | 514.9 | 521.6 | 56.9 | 57.4 | 192.1 | 287.6 | 112.5 | 89.1 | 179.3 | 100.6 | 85.8 | 221.4 | 162.8 | 118.7 | 102.9 | 97.7 | 110.5 | 109.1 | 96.1 | 104.5 | 111
3992.1 | 3771.1 | -6.8 | 0 | 0 | 101.6 | 99.3 | 92.3 | 93.3 | 111.1 | 26.7 | 21.1 | 36.4 | 3.6 | 261.6 | 4.3 | 414.3 | 411.6 | 98.7 | 43.7 | 514.9 | 521.6 | 56.9 | 57.5 | 192.1 | 287.3 | 112.8 | 89.1 | 179.2 | 100.6 | 85.7 | 221.2 | 162.7 | 118.7 | 102.9 | 97.7 | 110.4 | 109.1 | 96 | 104.4 | 111
3993.1 | 3772.1 | -6.8 | 0 | 0 | 101.6 | 99.2 | 92.3 | 93.2 | 111.2 | 26.8 | 21.1 | 36.3 | 3.3 | 271.5 | 4.4 | 414.3 | 411.6 | 98.4 | 43.7 | 514.8 | 521.7 | 57.8 | 57.5 | 192 | 287.1 | 112.7 | 89 | 179 | 100.5 | 85.9 | 220.9 | 162.5 | 118.6 | 102.8 | 97.6 | 110.3 | 109.1 | 96 | 104.3 | 110.9
3994.1 | 3773.1 | -6.8 | 0 | 0 | 101.7 | 99.3 | 92.2 | 93.2 | 111.1 | 26.9 | 21.1 | 36.3 | 3.4 | 262.2 | 4.6 | 414.3 | 411.6 | 98.8 | 43.8 | 514.7 | 521.8 | 59 | 57.6 | 191.8 | 286.8 | 112.4 | 89.1 | 178.9 | 100.2 | 85.9 | 220.8 | 162.4 | 118.5 | 102.8 | 97.5 | 110.2 | 109 | 96 | 104.2 | 110.8
3995.1 | 3774.1 | -6.8 | 0 | 0 | 101.8 | 99.3 | 92.2 | 93.1 | 110.9 | 27 | 21.1 | 36.2 | 3.1 | 259.1 | 5.1 | 414.2 | 411.5 | 99.2 | 43.8 | 514.6 | 521.6 | 60.1 | 57.8 | 191.7 | 286.6 | 112 | 89.2 | 178.7 | 100 | 85.9 | 220.5 | 162.4 | 118.5 | 102.8 | 97.5 | 110.1 | 109 | 96 | 104.2 | 110.8
3996.1 | 3775.1 | -6.8 | 0 | 0 | 101.8 | 99.4 | 92.2 | 93 | 111 | 27.1 | 21.1 | 36.2 | 2.6 | 265.1 | 5.6 | 414.2 | 411.5 | 98.1 | 43.9 | 514.6 | 521.5 | 60.4 | 58 | 191.7 | 286.4 | 112.7 | 89.1 | 178.6 | 99.9 | 85.8 | 220.4 | 162.3 | 118.5 | 102.7 | 97.4 | 110.1 | 108.9 | 95.9 | 104.1 | 110.7
3997.1 | 3776.1 | -6.8 | 0 | 0 | 101.6 | 99.5 | 92.1 | 93 | 111 | 27.1 | 21.1 | 36.2 | 2.8 | 234.3 | 5.5 | 414.2 | 411.4 | 98 | 43.8 | 514.5 | 522.5 | 60 | 58.1 | 191.7 | 286.1 | 112.6 | 89.1 | 178.4 | 99.8 | 85.7 | 220.2 | 162.2 | 118.4 | 102.7 | 97.4 | 110.1 | 108.8 | 95.7 | 104.1 | 110.7
3998.1 | 3777.1 | -6.8 | 0 | 0 | 101.2 | 99.5 | 92 | 93 | 110.9 | 27.1 | 21.1 | 36.2 | 3.4 | 219.5 | 4.9 | 414.1 | 411.4 | 97.5 | 43.8 | 514.4 | 523 | 59.9 | 58.1 | 191.6 | 285.9 | 112.9 | 89 | 178.3 | 99.7 | 85.8 | 220 | 162.2 | 118.4 | 102.7 | 97.4 | 110.1 | 108.7 | 95.6 | 104 | 110.6
3999.1 | 3778.1 | -6.7 | 0 | 0 | 100.7 | 99.3 | 91.9 | 93 | 110.7 | 27.2 | 21.1 | 36.2 | 3.5 | 257.4 | 5.1 | 414.1 | 411.4 | 97.7 | 43.7 | 514.4 | 523 | 59.8 | 58.2 | 191.5 | 285.7 | 114 | 88.7 | 178.2 | 99.4 | 85.6 | 219.8 | 162.1 | 118.3 | 102.6 | 97.4 | 110.1 | 108.7 | 95.5 | 103.9 | 110.6
4000.1 | 3779.1 | -6.8 | 0 | 0 | 100.4 | 99.3 | 92 | 93 | 110.7 | 27.2 | 21.1 | 36.1 | 3 | 220.6 | 6 | 414.1 | 411.4 | 98.6 | 43.6 | 514.4 | 522.6 | 59.7 | 58 | 191.4 | 285.4 | 114 | 88.5 | 178 | 99.3 | 85.4 | 219.6 | 161.9 | 118.2 | 102.6 | 97.4 | 110 | 108.6 | 95.5 | 103.9 | 110.5
4001.1 | 3780.1 | -6.8 | 0 | 0 | 100.5 | 99.2 | 92 | 92.9 | 110.7 | 27.2 | 21.1 | 36.1 | 3.1 | 234.5 | 6.1 | 414.1 | 411.3 | 99.1 | 43.6 | 514.3 | 522 | 59.5 | 58 | 191.4 | 285.2 | 114.1 | 88.5 | 177.9 | 99.1 | 85.2 | 219.4 | 161.9 | 118.2 | 102.6 | 97.4 | 109.9 | 108.6 | 95.6 | 103.8 | 110.4
4002.1 | 3781.1 | -6.8 | 0 | 0 | 100.6 | 99.1 | 92.1 | 92.7 | 110.5 | 27.3 | 21.1 | 36.1 | 3 | 236.9 | 5.8 | 414 | 411.3 | 99.8 | 43.5 | 514.3 | 521.5 | 59.7 | 57.8 | 191.4 | 285 | 114.1 | 88.5 | 177.7 | 98.9 | 85.1 | 219.2 | 161.9 | 118.1 | 102.6 | 97.3 | 109.9 | 108.5 | 95.5 | 103.8 | 110.4
4003.1 | 3782.1 | -6.8 | 0 | 0 | 100.7 | 99 | 92.1 | 92.6 | 110.3 | 27.4 | 21.1 | 36.1 | 2.9 | 230.6 | 5.9 | 414 | 411.3 | 100.4 | 43.4 | 514.3 | 520.8 | 60.2 | 57.8 | 191.4 | 284.8 | 114.5 | 88.6 | 177.6 | 98.8 | 85.2 | 219 | 161.8 | 118.1 | 102.6 | 97.2 | 109.8 | 108.4 | 95.5 | 103.8 | 110.3
4004.1 | 3783.1 | -6.7 | 0 | 0 | 100.8 | 98.9 | 92.1 | 92.5 | 110.1 | 27.4 | 21.1 | 36.1 | 2.8 | 244.2 | 6.4 | 414 | 411.2 | 100.6 | 43.5 | 514.2 | 520.2 | 60.2 | 58 | 191.4 | 284.5 | 114.7 | 88.6 | 177.4 | 98.7 | 85.3 | 218.8 | 161.7 | 118 | 102.5 | 97.1 | 109.8 | 108.4 | 95.5 | 103.7 | 110.3
4005.1 | 3784.1 | -6.7 | 0 | 0 | 100.9 | 98.9 | 92.1 | 92.6 | 110.2 | 27.4 | 21.1 | 36.1 | 3.3 | 241.9 | 6.9 | 413.9 | 411.2 | 101.1 | 43.6 | 514.2 | 519.6 | 60 | 58.1 | 191.3 | 284.3 | 114.8 | 88.6 | 177.3 | 98.4 | 85.4 | 218.6 | 161.7 | 117.9 | 102.4 | 97 | 109.7 | 108.4 | 95.5 | 103.6 | 110.2
4006.1 | 3785.1 | -6.7 | 0 | 0 | 101 | 98.8 | 91.9 | 92.5 | 110.1 | 27.4 | 21.1 | 36.1 | 3.8 | 236.7 | 7.2 | 413.9 | 411.1 | 101.2 | 43.6 | 514.2 | 518.9 | 60 | 58 | 191.2 | 284.1 | 114.5 | 88.7 | 177.2 | 98.3 | 85.5 | 218.4 | 161.7 | 117.8 | 102.3 | 96.9 | 109.7 | 108.4 | 95.5 | 103.6 | 110.2
4007.1 | 3786.1 | -6.6 | 0 | 0 | 101.1 | 98.7 | 91.7 | 92.4 | 109.9 | 27.4 | 21.1 | 36.1 | 4.5 | 239.8 | 7.2 | 413.9 | 411.1 | 100 | 43.6 | 514.1 | 518.4 | 60.7 | 57.9 | 191.2 | 283.9 | 114.9 | 88.8 | 177 | 98.2 | 85.4 | 218.2 | 161.4 | 117.7 | 102.2 | 96.9 | 109.6 | 108.4 | 95.4 | 103.5 | 110.1
4008.1 | 3787.1 | -6.5 | 0 | 0 | 101 | 98.3 | 91.7 | 92.4 | 109.6 | 27.5 | 21.1 | 36.1 | 4.3 | 241.3 | 7.2 | 413.8 | 411.1 | 99.1 | 43.7 | 514.1 | 518 | 61.1 | 58 | 191.2 | 283.7 | 116.1 | 88.9 | 176.9 | 98.1 | 85.6 | 218 | 161.4 | 117.6 | 102.1 | 96.9 | 109.5 | 108.4 | 95.4 | 103.4 | 110.1
4009.1 | 3788.1 | -6.3 | 0 | 0 | 100.7 | 98.2 | 91.7 | 92.5 | 109.5 | 27.4 | 21.1 | 36 | 4 | 238.9 | 7.6 | 413.8 | 411 | 98.5 | 43.9 | 513.9 | 517.8 | 61.1 | 58.1 | 191.3 | 283.5 | 116.8 | 88.5 | 176.7 | 97.9 | 85.8 | 217.8 | 161.2 | 117.6 | 102 | 96.9 | 109.5 | 108.4 | 95.4 | 103.3 | 110
4010.1 | 3789.1 | -6.2 | 0 | 0 | 100.6 | 98.2 | 91.8 | 92.6 | 109.6 | 27.4 | 21.1 | 35.9 | 4 | 238.7 | 7.8 | 413.8 | 411 | 98.7 | 44.2 | 513.8 | 517.8 | 61.2 | 58.2 | 191.3 | 283.3 | 117.1 | 88.3 | 176.6 | 98 | 85.8 | 217.6 | 161.2 | 117.6 | 102 | 96.9 | 109.4 | 108.3 | 95.3 | 103.2 | 109.9
4011.1 | 3790.1 | -6.2 | 0 | 0 | 100.6 | 98.3 | 91.7 | 92.5 | 109.6 | 27.4 | 21.1 | 35.9 | 4 | 246.6 | 8.2 | 413.7 | 411 | 99.2 | 44.5 | 513.7 | 517.9 | 61 | 58.5 | 191.3 | 283 | 117.4 | 88.1 | 176.5 | 97.7 | 85.9 | 217.4 | 161 | 117.5 | 101.9 | 96.9 | 109.4 | 108.3 | 95.3 | 103.2 | 109.9
4012.1 | 3791.1 | -6.5 | 0 | 0 | 100.7 | 98.3 | 91.7 | 92.5 | 109.4 | 27.5 | 21.1 | 35.8 | 3.6 | 248.5 | 8.8 | 413.7 | 410.9 | 99.8 | 44.8 | 513.7 | 517.9 | 60.8 | 58.7 | 191.3 | 282.8 | 116.9 | 87.9 | 176.3 | 97.5 | 85.9 | 217.2 | 161 | 117.4 | 101.9 | 96.9 | 109.3 | 108.2 | 95.2 | 103.2 | 109.9
4013.1 | 3792.1 | -6.6 | 0 | 0 | 100.8 | 98.3 | 91.7 | 92.4 | 109.1 | 27.5 | 21.1 | 35.8 | 3.4 | 246.4 | 9.2 | 413.7 | 410.9 | 99.8 | 45.1 | 513.6 | 517.7 | 60.8 | 58.9 | 191.3 | 282.6 | 116.3 | 87.8 | 176.2 | 97.6 | 86 | 217 | 161 | 117.4 | 101.9 | 96.8 | 109.3 | 108.2 | 95.2 | 103.2 | 109.8
4014.1 | 3793.1 | -6.7 | 0 | 0 | 100.8 | 98.2 | 91.7 | 92.4 | 109 | 27.4 | 21.1 | 35.8 | 3.5 | 241 | 9.5 | 413.7 | 410.9 | 99.2 | 45.1 | 513.6 | 517.5 | 60.9 | 59.2 | 191.4 | 282.3 | 115.6 | 87.7 | 176 | 97.6 | 86.1 | 216.8 | 160.9 | 117.3 | 101.9 | 96.7 | 109.2 | 108.2 | 95.2 | 103.1 | 109.7
4015.1 | 3794.1 | -6.7 | 0 | 0 | 100.8 | 98 | 91.6 | 92.3 | 109 | 27.4 | 21.1 | 35.8 | 3.6 | 240.5 | 9.2 | 413.6 | 410.8 | 98.3 | 45.3 | 513.4 | 517.4 | 61.1 | 59.5 | 191.4 | 282.1 | 115 | 87.7 | 175.9 | 97.6 | 86 | 216.6 | 160.8 | 117.3 | 101.8 | 96.6 | 109.1 | 108.1 | 95.1 | 103.1 | 109.6
4016.1 | 3795.1 | -6.8 | 0 | 0 | 100.8 | 98 | 91.5 | 92.3 | 108.9 | 27.4 | 21.1 | 35.8 | 3.5 | 239.4 | 8.9 | 413.6 | 410.8 | 97.8 | 45.4 | 513.3 | 517.6 | 61.5 | 59.6 | 191.4 | 281.9 | 115.3 | 87.5 | 175.7 | 97.4 | 86 | 216.4 | 160.7 | 117.2 | 101.8 | 96.5 | 109 | 108 | 95.1 | 103.1 | 109.6
4017.1 | 3796.1 | -6.8 | 0 | 0 | 100.8 | 98 | 91.4 | 92.2 | 108.5 | 27.4 | 21.1 | 35.7 | 3.5 | 243.1 | 8.7 | 413.6 | 410.8 | 97.1 | 45.4 | 513.2 | 517.6 | 61.6 | 59.7 | 191.4 | 281.6 | 116.3 | 87.4 | 175.6 | 97.2 | 86.1 | 216.2 | 160.7 | 117.2 | 101.7 | 96.5 | 109 | 108 | 95 | 103.1 | 109.5
4018.1 | 3797.1 | -6.8 | 0 | 0 | 100.8 | 98 | 91.3 | 92.2 | 108.2 | 27.4 | 21.1 | 35.7 | 3.4 | 244.7 | 8.4 | 413.5 | 410.7 | 96.5 | 45.4 | 513 | 517.4 | 61.6 | 59.8 | 191.4 | 281.4 | 116.9 | 87.2 | 175.5 | 96.9 | 86.1 | 216 | 160.6 | 117.1 | 101.7 | 96.4 | 108.9 | 107.9 | 95 | 103 | 109.5
4019.1 | 3798.1 | -6.8 | 0 | 0 | 100.7 | 97.8 | 91.3 | 92.3 | 107.9 | 27.3 | 21.2 | 35.7 | 3.5 | 234.8 | 8.4 | 413.5 | 410.7 | 96 | 45.4 | 512.9 | 517.6 | 61.6 | 59.7 | 191.4 | 281.2 | 117.5 | 86.9 | 175.3 | 96.5 | 86 | 215.8 | 160.5 | 117.1 | 101.7 | 96.4 | 108.9 | 107.9 | 95 | 102.9 | 109.4
4020.1 | 3799.1 | -6.7 | 0 | 0 | 100.7 | 97.6 | 91.3 | 92.3 | 107.6 | 27.3 | 21.2 | 35.7 | 3.2 | 255.4 | 8.1 | 413.5 | 410.7 | 95.7 | 45.2 | 512.8 | 518.3 | 61.4 | 59.3 | 191.3 | 280.9 | 117.7 | 86.8 | 175.2 | 96.2 | 85.9 | 215.6 | 160.4 | 117 | 101.7 | 96.4 | 108.8 | 107.8 | 95 | 102.9 | 109.4
4021.1 | 3800.1 | -6.8 | 0 | 0 | 100.6 | 97.6 | 91.3 | 92.3 | 107.5 | 27.4 | 21.2 | 35.7 | 3 | 253.2 | 8.1 | 413.4 | 410.6 | 95.6 | 44.9 | 512.6 | 518.7 | 61.2 | 59 | 191.2 | 280.7 | 117.8 | 86.4 | 175.1 | 96.2 | 85.7 | 215.5 | 160.4 | 116.9 | 101.5 | 96.3 | 108.8 | 107.7 | 95 | 102.8 | 109.3
4022.1 | 3801.1 | -6.8 | 0 | 0 | 100.5 | 97.7 | 91.3 | 92.3 | 107.3 | 27.4 | 21.2 | 35.6 | 2.8 | 253.1 | 7.6 | 413.4 | 410.6 | 95.5 | 44.8 | 512.6 | 519 | 61.1 | 58.7 | 191.2 | 280.5 | 117.6 | 86.3 | 175 | 96.2 | 85.7 | 215.3 | 160.2 | 116.8 | 101.3 | 96.3 | 108.8 | 107.7 | 94.9 | 102.8 | 109.2
4023.1 | 3802.1 | -6.8 | 0 | 0 | 100.6 | 97.8 | 91.2 | 92.3 | 107.2 | 27.4 | 21.2 | 35.6 | 2.7 | 245.6 | 7.2 | 413.4 | 410.6 | 96.9 | 44.5 | 512.5 | 519.1 | 61.2 | 58.3 | 191.1 | 280.2 | 117.2 | 86.4 | 174.9 | 96.3 | 85.7 | 215.1 | 160.2 | 116.8 | 101.2 | 96.2 | 108.7 | 107.6 | 94.8 | 102.7 | 109.2
4024.1 | 3803.1 | -6.8 | 0 | 0 | 100.7 | 97.8 | 91.1 | 92.3 | 107 | 27.4 | 21.2 | 35.6 | 2.9 | 251 | 7 | 413.3 | 410.5 | 97.3 | 44.2 | 512.5 | 519 | 62 | 57.9 | 190.9 | 280 | 116.5 | 86.3 | 174.7 | 96.2 | 85.8 | 214.9 | 160.3 | 116.7 | 101.1 | 96.3 | 108.7 | 107.6 | 94.8 | 102.7 | 109.1
4025.1 | 3804.1 | -6.8 | 0 | 0 | 100.8 | 97.6 | 91.1 | 92.1 | 106.9 | 27.4 | 21.2 | 35.7 | 3 | 259.5 | 6.1 | 413.3 | 410.5 | 96.2 | 44.1 | 512.4 | 518.8 | 62.8 | 57.7 | 190.7 | 279.7 | 115.7 | 86.4 | 174.6 | 96 | 86.2 | 214.7 | 160.3 | 116.7 | 101 | 96.3 | 108.7 | 107.5 | 94.9 | 102.6 | 109.1
4026.1 | 3805.1 | -6.8 | 0 | 0 | 100.6 | 97.3 | 91.2 | 92.1 | 106.8 | 27.4 | 21.2 | 35.6 | 2.4 | 250.3 | 6 | 413.3 | 410.5 | 95.7 | 44.2 | 512.3 | 518.4 | 63.4 | 57.7 | 190.7 | 279.5 | 115.6 | 86.6 | 174.4 | 95.9 | 86.3 | 214.5 | 160.3 | 116.6 | 101 | 96.3 | 108.6 | 107.5 | 94.8 | 102.6 | 109
4027.1 | 3806.1 | -6.8 | 0 | 0 | 100.4 | 97.2 | 91.2 | 92.1 | 106.7 | 27.3 | 21.2 | 35.6 | 2.9 | 250.4 | 6.8 | 413.3 | 410.4 | 96 | 44.2 | 512.2 | 518 | 63.5 | 57.6 | 190.5 | 279.2 | 116 | 86.9 | 174.3 | 96.1 | 86.5 | 214.3 | 160.2 | 116.5 | 101 | 96.3 | 108.6 | 107.4 | 94.8 | 102.6 | 109
4028.1 | 3807.1 | -6.8 | 0 | 0 | 100.1 | 97.2 | 91.2 | 92.2 | 106.7 | 27.4 | 21.2 | 35.5 | 2.9 | 257.2 | 7.4 | 413.2 | 410.4 | 95.5 | 44.1 | 512.1 | 517.9 | 63.2 | 57.7 | 190.4 | 279 | 116.1 | 87.2 | 174.1 | 96.2 | 86.8 | 214.1 | 160.2 | 116.5 | 101 | 96.2 | 108.5 | 107.3 | 94.8 | 102.5 | 108.9
4029.1 | 3808.1 | -6.8 | 0 | 0 | 100.3 | 97 | 91.1 | 92.3 | 107.2 | 27.4 | 21.2 | 35.5 | 2.6 | 261 | 7.5 | 413.2 | 410.3 | 95.8 | 44.1 | 512.1 | 517.7 | 63 | 57.8 | 190.3 | 278.8 | 115.9 | 87.5 | 174 | 96.3 | 86.5 | 213.9 | 160.1 | 116.5 | 100.9 | 96.1 | 108.5 | 107.3 | 94.8 | 102.5 | 108.9
4030.1 | 3809.1 | -6.8 | 0 | 0 | 100.4 | 96.8 | 90.8 | 92.4 | 107.6 | 27.4 | 21.2 | 35.5 | 2.4 | 252.4 | 8 | 413.2 | 410.3 | 95.7 | 44.1 | 512.1 | 517.3 | 63.4 | 57.8 | 190.2 | 278.5 | 115.6 | 87.6 | 173.9 | 96.2 | 86.2 | 213.7 | 160 | 116.4 | 100.9 | 96 | 108.4 | 107.2 | 94.8 | 102.4 | 108.8
4031.1 | 3810.1 | -6.8 | 0 | 0 | 100.5 | 96.7 | 90.6 | 92.3 | 107.9 | 27.4 | 21.2 | 35.5 | 2.7 | 256.5 | 8.4 | 413.1 | 410.3 | 94.9 | 44 | 512.2 | 517.1 | 63.3 | 57.8 | 190.2 | 278.3 | 115.1 | 87.7 | 173.7 | 96.1 | 86 | 213.5 | 159.9 | 116.4 | 100.9 | 96 | 108.3 | 107.1 | 94.8 | 102.4 | 108.7
4032.1 | 3811.1 | -6.8 | 0 | 0 | 100.3 | 96.8 | 90.5 | 92.2 | 108.1 | 27.3 | 21.2 | 35.5 | 2.7 | 258.6 | 8.3 | 413.1 | 410.2 | 94.1 | 44 | 512.1 | 517 | 63.5 | 57.8 | 190.1 | 278.1 | 114.9 | 87.8 | 173.6 | 96 | 86 | 213.3 | 159.9 | 116.3 | 100.8 | 96 | 108.3 | 107 | 94.7 | 102.3 | 108.7
4033.1 | 3812.1 | -6.8 | 0 | 0 | 99.9 | 96.9 | 90.6 | 92.3 | 108.1 | 27.3 | 21.2 | 35.5 | 2.7 | 258 | 8.4 | 413.1 | 410.2 | 93.6 | 43.8 | 512.1 | 517.2 | 63.8 | 57.5 | 190.1 | 277.9 | 115.5 | 87.8 | 173.4 | 95.8 | 86 | 213.1 | 159.9 | 116.2 | 100.8 | 95.9 | 108.2 | 107 | 94.5 | 102.2 | 108.6
4034.1 | 3813.1 | -6.8 | 0 | 0 | 99.9 | 97 | 90.6 | 92.3 | 108 | 27.4 | 21.2 | 35.4 | 3 | 259.1 | 8.5 | 413 | 410.1 | 93.1 | 43.8 | 512.1 | 517.2 | 63.8 | 57.5 | 190 | 277.7 | 116.5 | 87.7 | 173.3 | 95.7 | 86.1 | 212.9 | 159.8 | 116.2 | 100.7 | 95.9 | 108.1 | 107 | 94.5 | 102.1 | 108.6
4035.1 | 3814.1 | -6.7 | 0 | 0 | 100 | 96.8 | 90.5 | 92.1 | 107.9 | 27.5 | 21.2 | 35.4 | 3.3 | 259.7 | 8.1 | 413 | 410.1 | 93.3 | 43.8 | 512 | 517.1 | 63.5 | 57.8 | 190.1 | 277.5 | 116.9 | 87.6 | 173.1 | 95.3 | 86.1 | 212.7 | 159.6 | 116.1 | 100.7 | 95.8 | 108 | 106.9 | 94.5 | 102 | 108.5
4036.1 | 3815.1 | -6.7 | 0 | 0 | 100 | 96.4 | 90.4 | 92 | 107.7 | 27.5 | 21.2 | 35.4 | 3.6 | 261.9 | 7.9 | 413 | 410.1 | 93.2 | 43.9 | 511.9 | 516.9 | 63.2 | 57.9 | 190 | 277.3 | 117 | 87.5 | 173 | 95.1 | 86.2 | 212.5 | 159.7 | 116.1 | 100.7 | 95.8 | 108 | 106.8 | 94.5 | 102 | 108.5
4037.1 | 3816.1 | -6.7 | 0 | 0 | 100 | 96.1 | 90.4 | 92 | 107.7 | 27.4 | 21.2 | 35.3 | 3.9 | 262.6 | 7.5 | 412.9 | 410.1 | 92.9 | 43.9 | 511.8 | 516.8 | 62.8 | 57.9 | 189.9 | 277.1 | 117.1 | 87.2 | 172.8 | 94.9 | 86.3 | 212.3 | 159.6 | 116 | 100.7 | 95.8 | 108 | 106.7 | 94.4 | 102 | 108.4
4038.1 | 3817.1 | -6.7 | 0 | 0 | 100 | 96.1 | 90.5 | 92 | 107.6 | 27.4 | 21.2 | 35.3 | 3.7 | 264.3 | 7.5 | 412.9 | 410 | 92.6 | 44 | 511.8 | 516.6 | 63.2 | 58 | 189.9 | 276.8 | 116.6 | 87.2 | 172.7 | 94.8 | 86 | 212.1 | 159.5 | 116 | 100.6 | 95.7 | 108 | 106.7 | 94.3 | 101.9 | 108.4
4039.1 | 3818.1 | -6.8 | 0 | 0 | 99.9 | 96.1 | 90.6 | 92.1 | 107.4 | 27.4 | 21.2 | 35.2 | 3.4 | 270.6 | 8 | 412.9 | 410 | 93.2 | 44.3 | 511.8 | 516.2 | 64 | 58 | 189.9 | 276.6 | 116.5 | 87 | 172.6 | 94.7 | 86.2 | 212 | 159.4 | 116 | 100.6 | 95.6 | 107.9 | 106.6 | 94.3 | 101.9 | 108.3
4040.1 | 3819.1 | -6.8 | 0 | 0 | 99.7 | 96.1 | 90.5 | 92.1 | 107.2 | 27.5 | 21.2 | 35.2 | 3.4 | 259.9 | 9 | 412.8 | 410 | 93.2 | 44.5 | 511.7 | 515.9 | 64.2 | 58.1 | 190 | 276.4 | 116.3 | 87 | 172.5 | 94.7 | 86.4 | 211.8 | 159.3 | 115.9 | 100.6 | 95.7 | 107.8 | 106.6 | 94.3 | 101.8 | 108.3
4041.1 | 3820.1 | -6.8 | 0 | 0 | 99.6 | 96.2 | 90.4 | 92.1 | 107 | 27.6 | 21.2 | 35.1 | 3.6 | 263.1 | 8.6 | 412.8 | 409.9 | 92.6 | 44.6 | 511.6 | 515.5 | 65.4 | 58.2 | 190 | 276.2 | 116.2 | 87.2 | 172.3 | 94.6 | 86.4 | 211.6 | 159.3 | 115.9 | 100.6 | 95.6 | 107.8 | 106.5 | 94.2 | 101.8 | 108.2
4042.1 | 3821.1 | -6.8 | 0 | 0 | 99.6 | 96.2 | 90.3 | 92 | 106.9 | 27.5 | 21.2 | 35.1 | 3.4 | 254.7 | 7.9 | 412.8 | 409.9 | 92.3 | 44.5 | 511.5 | 515.2 | 66.6 | 58.1 | 189.9 | 276 | 116.8 | 87 | 172.2 | 94.3 | 86.2 | 211.4 | 159.2 | 115.8 | 100.6 | 95.5 | 107.7 | 106.5 | 94.2 | 101.8 | 108.1
4043.1 | 3822.1 | -6.7 | 0 | 0 | 99.6 | 96.2 | 90.2 | 91.9 | 107 | 27.5 | 21.2 | 35.1 | 3.1 | 254.9 | 7.4 | 412.7 | 409.9 | 93 | 44.4 | 511.4 | 514.7 | 67.2 | 57.8 | 189.7 | 275.8 | 117.3 | 86.8 | 172.1 | 94.2 | 86 | 211.2 | 159.1 | 115.7 | 100.5 | 95.4 | 107.6 | 106.4 | 94.1 | 101.7 | 108.1
4044.1 | 3823.1 | -6.7 | 0 | 0 | 99.4 | 96.2 | 90.2 | 91.9 | 107.3 | 27.5 | 21.2 | 35.1 | 3.4 | 252.9 | 7.4 | 412.7 | 409.8 | 93.7 | 44.3 | 511.3 | 514.5 | 67.7 | 57.9 | 189.7 | 275.6 | 117.8 | 86.6 | 171.9 | 94.2 | 85.8 | 211 | 159.1 | 115.7 | 100.5 | 95.3 | 107.6 | 106.3 | 94.1 | 101.7 | 108
4045.1 | 3824.1 | -6.7 | 0 | 0 | 99.2 | 96.3 | 90.2 | 91.9 | 107.5 | 27.5 | 21.2 | 35.1 | 3.5 | 248.6 | 7.6 | 412.6 | 409.8 | 93.6 | 44.2 | 511.3 | 514.3 | 67.9 | 58 | 189.6 | 275.4 | 118.3 | 86.6 | 171.8 | 94.2 | 86 | 210.8 | 159.1 | 115.6 | 100.5 | 95.3 | 107.5 | 106.2 | 94 | 101.6 | 108
4046.1 | 3825.1 | -6.8 | 0 | 0 | 99 | 96.3 | 90.3 | 91.9 | 107.5 | 27.5 | 21.2 | 35.1 | 3.7 | 262 | 8 | 412.6 | 409.8 | 93.4 | 44.1 | 511.3 | 514.1 | 68.5 | 57.9 | 189.5 | 275.2 | 118.6 | 86.7 | 171.7 | 94.2 | 86 | 210.6 | 159.1 | 115.5 | 100.5 | 95.3 | 107.5 | 106.1 | 93.9 | 101.6 | 107.9
4047.1 | 3826.1 | -6.7 | 0 | 0 | 99.1 | 96.2 | 90.3 | 91.9 | 107.5 | 27.4 | 21.2 | 35.1 | 3.3 | 249.2 | 8.6 | 412.6 | 409.7 | 94.3 | 44.1 | 511.3 | 513.9 | 68.1 | 58 | 189.4 | 275 | 118.6 | 86.8 | 171.5 | 94.2 | 86.1 | 210.4 | 159.2 | 115.4 | 100.5 | 95.3 | 107.5 | 106.1 | 93.8 | 101.6 | 107.9
4048.1 | 3827.1 | -6.7 | 0 | 0 | 99.1 | 96.1 | 90.3 | 91.8 | 107.3 | 27.4 | 21.2 | 35.1 | 3 | 250.8 | 8.2 | 412.6 | 409.7 | 95.3 | 44.1 | 511.2 | 513.8 | 67.7 | 58 | 189.3 | 274.8 | 118.8 | 86.8 | 171.4 | 94.2 | 86.1 | 210.2 | 159 | 115.4 | 100.5 | 95.2 | 107.4 | 106 | 93.7 | 101.6 | 107.8
4049.1 | 3828.1 | -6.8 | 0 | 0 | 99.1 | 96 | 90.3 | 91.6 | 107.1 | 27.3 | 21.2 | 35.1 | 3 | 249.7 | 8.1 | 412.5 | 409.7 | 95.8 | 44 | 511.2 | 513.5 | 67.2 | 58 | 189.3 | 274.6 | 119 | 86.7 | 171.3 | 94.1 | 85.9 | 210 | 158.8 | 115.4 | 100.5 | 95.2 | 107.3 | 105.9 | 93.7 | 101.5 | 107.8
4050.1 | 3829.1 | -6.8 | 0 | 0 | 99.1 | 96.1 | 90.2 | 91.5 | 107 | 27.4 | 21.2 | 35.1 | 2.9 | 241.6 | 8.4 | 412.5 | 409.6 | 95.6 | 44.1 | 511.2 | 513.2 | 66.6 | 58.1 | 189.3 | 274.4 | 119.4 | 86.5 | 171.1 | 94.2 | 86 | 209.8 | 158.8 | 115.3 | 100.4 | 95.1 | 107.3 | 105.9 | 93.8 | 101.5 | 107.7
4051.1 | 3830.1 | -6.8 | 0 | 0 | 99.1 | 96.1 | 90.2 | 91.3 | 107 | 27.5 | 21.2 | 35.2 | 2.9 | 240 | 7.4 | 412.4 | 409.6 | 95.6 | 44.1 | 511.2 | 513.1 | 66.4 | 58 | 189.3 | 274.2 | 120.1 | 86.4 | 171 | 94.4 | 86.1 | 209.6 | 158.7 | 115.2 | 100.4 | 95 | 107.2 | 105.8 | 93.8 | 101.5 | 107.7
4052.1 | 3831.1 | -6.8 | 0 | 0 | 99.2 | 96.2 | 90.1 | 91.2 | 106.8 | 27.5 | 21.2 | 35.2 | 2.9 | 251.1 | 6.2 | 412.4 | 409.5 | 96.4 | 43.9 | 511.2 | 513 | 66 | 57.8 | 189.2 | 274 | 120.6 | 86.3 | 170.9 | 94.2 | 86.2 | 209.5 | 158.6 | 115.1 | 100.4 | 95 | 107.1 | 105.8 | 93.8 | 101.4 | 107.6
4053.1 | 3832.1 | -6.8 | 0 | 0 | 99.2 | 96.3 | 90.1 | 91.4 | 106.6 | 27.5 | 21.2 | 35.1 | 3.1 | 264.4 | 6 | 412.4 | 409.5 | 97.2 | 43.7 | 511.3 | 513 | 65.8 | 57.8 | 189.2 | 273.8 | 121.1 | 86.1 | 170.8 | 94.1 | 86.2 | 209.3 | 158.5 | 115 | 100.4 | 95 | 107.1 | 105.8 | 93.9 | 101.4 | 107.6
4054.1 | 3833.1 | -6.8 | 0 | 0 | 99.3 | 96.3 | 90 | 91.5 | 106.4 | 27.5 | 21.2 | 35.1 | 3.2 | 249.5 | 7 | 412.3 | 409.4 | 97.7 | 43.6 | 511.3 | 513.2 | 65.4 | 57.9 | 189.2 | 273.6 | 121.2 | 86 | 170.6 | 93.9 | 86.3 | 209.1 | 158.4 | 115 | 100.4 | 95 | 107.1 | 105.8 | 93.9 | 101.4 | 107.5
4055.1 | 3834.1 | -6.8 | 0 | 0 | 99.2 | 96.3 | 89.9 | 91.5 | 106.5 | 27.5 | 21.2 | 35.1 | 3 | 265.9 | 6.9 | 412.3 | 409.4 | 98.3 | 43.5 | 511.3 | 513.5 | 65 | 58 | 189.2 | 273.4 | 121.3 | 85.8 | 170.5 | 93.9 | 86.3 | 208.9 | 158.3 | 114.9 | 100.3 | 95 | 107 | 105.7 | 93.9 | 101.4 | 107.4
4056.1 | 3835.1 | -6.8 | 0 | 0 | 99.1 | 96.2 | 89.9 | 91.5 | 106.6 | 27.4 | 21.2 | 35 | 3.4 | 243.3 | 5.6 | 412.3 | 409.4 | 97.9 | 43.5 | 511.3 | 513.6 | 64.8 | 57.8 | 189.1 | 273.2 | 120.8 | 85.7 | 170.4 | 93.9 | 86.2 | 208.7 | 158.4 | 114.9 | 100.2 | 95 | 107 | 105.7 | 93.9 | 101.4 | 107.4
4057.1 | 3836.1 | -6.8 | 0 | 0 | 98.9 | 96.1 | 89.9 | 91.5 | 106.5 | 27.3 | 21.2 | 35 | 3.4 | 244 | 5.1 | 412.2 | 409.3 | 97.5 | 43.3 | 511.3 | 513.9 | 64.5 | 57.8 | 189 | 272.9 | 120.6 | 85.4 | 170.3 | 93.9 | 86.3 | 208.5 | 158.4 | 114.8 | 100.1 | 95 | 107 | 105.6 | 93.8 | 101.3 | 107.3
4058.1 | 3837.1 | -6.7 | 0 | 0 | 98.8 | 96 | 89.9 | 91.6 | 106.8 | 27.3 | 21.2 | 35 | 3.1 | 246.3 | 5.8 | 412.2 | 409.3 | 97.5 | 43.3 | 511.3 | 514.8 | 64 | 57.7 | 188.9 | 272.7 | 120.4 | 85.4 | 170.1 | 93.9 | 86.5 | 208.3 | 158.2 | 114.8 | 100 | 94.9 | 106.9 | 105.5 | 93.8 | 101.3 | 107.3
4059.1 | 3838.1 | -6.7 | 0 | 0 | 98.8 | 96.1 | 89.9 | 91.6 | 106.9 | 27.4 | 21.2 | 35 | 3 | 259.7 | 6.3 | 412.1 | 409.2 | 96.7 | 43.3 | 511.3 | 515.5 | 63.7 | 57.8 | 188.9 | 272.5 | 119.8 | 85.4 | 170 | 93.9 | 86.7 | 208.1 | 158.1 | 114.7 | 100 | 94.9 | 106.9 | 105.5 | 93.7 | 101.3 | 107.2
4060.1 | 3839.1 | -6.7 | 0 | 0 | 98.9 | 96.3 | 89.8 | 91.6 | 106.8 | 27.4 | 21.2 | 35.1 | 2.8 | 250.4 | 7.1 | 412.1 | 409.2 | 96.3 | 43.2 | 511.3 | 515.9 | 63.5 | 57.9 | 188.8 | 272.3 | 119.5 | 85.5 | 169.9 | 94.1 | 86.7 | 207.9 | 158.2 | 114.7 | 99.9 | 94.9 | 106.8 | 105.5 | 93.7 | 101.3 | 107.2
4061.1 | 3840.1 | -6.7 | 0 | 0 | 99 | 96.5 | 89.8 | 91.6 | 107 | 27.5 | 21.2 | 35.1 | 3.1 | 248 | 7.5 | 412.1 | 409.2 | 96.2 | 43.2 | 511.2 | 516 | 63.4 | 58 | 188.8 | 272 | 119.5 | 85.4 | 169.8 | 94.2 | 86.7 | 207.7 | 158.3 | 114.6 | 99.8 | 94.8 | 106.8 | 105.4 | 93.6 | 101.3 | 107.1
4062.1 | 3841.1 | -6.8 | 0 | 0 | 99.1 | 96.6 | 89.9 | 91.4 | 107.2 | 27.5 | 21.2 | 35.1 | 2.6 | 256 | 7.6 | 412 | 409.1 | 95.8 | 43.3 | 511.2 | 515.9 | 63.8 | 58.2 | 188.7 | 271.8 | 119 | 85.4 | 169.6 | 94.2 | 86.6 | 207.5 | 158.3 | 114.5 | 99.7 | 94.8 | 106.7 | 105.3 | 93.5 | 101.2 | 107.1
4063.1 | 3842.1 | -6.8 | 0 | 0 | 99.2 | 96.6 | 89.8 | 91.2 | 107.1 | 27.6 | 21.2 | 35.2 | 2.7 | 249.8 | 7.5 | 412 | 409.1 | 95.5 | 43.3 | 511.1 | 515.9 | 64.1 | 58.4 | 188.7 | 271.6 | 118.2 | 85.4 | 169.5 | 94.3 | 86.6 | 207.4 | 158.1 | 114.5 | 99.6 | 94.8 | 106.7 | 105.2 | 93.5 | 101.2 | 107
4064.1 | 3843.1 | -6.8 | 0 | 0 | 99.2 | 96.3 | 89.7 | 91.1 | 106.9 | 27.6 | 21.2 | 35.1 | 3.1 | 240.8 | 7.4 | 411.9 | 409.1 | 94.5 | 43.3 | 511 | 516 | 64.1 | 58.2 | 188.5 | 271.4 | 117.5 | 85.2 | 169.4 | 94.3 | 86.7 | 207.2 | 157.8 | 114.4 | 99.6 | 94.8 | 106.6 | 105.2 | 93.5 | 101.1 | 107
4065.1 | 3844.1 | -6.8 | 0 | 0 | 99.2 | 96 | 89.7 | 91 | 106.7 | 27.6 | 21.2 | 35.1 | 3 | 254.5 | 7.1 | 411.9 | 409 | 94.4 | 43.4 | 510.9 | 516.1 | 64.3 | 58.3 | 188.5 | 271.1 | 116.7 | 85.2 | 169.3 | 94.4 | 86.5 | 207 | 157.8 | 114.4 | 99.6 | 94.8 | 106.5 | 105.2 | 93.5 | 101 | 106.9
4066.1 | 3845.1 | -6.8 | 0 | 0 | 99.2 | 95.9 | 89.7 | 90.9 | 106.7 | 27.6 | 21.2 | 35.1 | 3 | 246.1 | 7.1 | 411.9 | 409 | 95.3 | 43.3 | 510.8 | 516.4 | 64.3 | 58.3 | 188.4 | 270.9 | 116.2 | 85.1 | 169.1 | 94.6 | 86.4 | 206.8 | 157.7 | 114.3 | 99.6 | 94.8 | 106.5 | 105.2 | 93.5 | 101 | 106.8
4067.1 | 3846.1 | -6.8 | 0 | 0 | 99.1 | 96 | 89.8 | 90.9 | 106.7 | 27.7 | 21.2 | 35 | 2.9 | 249 | 6.7 | 411.8 | 409 | 95.5 | 43.2 | 510.7 | 516.5 | 64.1 | 58.3 | 188.2 | 270.7 | 116 | 85.1 | 169 | 94.5 | 86.3 | 206.6 | 157.7 | 114.3 | 99.5 | 94.7 | 106.4 | 105.1 | 93.5 | 100.9 | 106.8
4068.1 | 3847.1 | -6.8 | 0 | 0 | 99 | 95.9 | 89.7 | 90.8 | 106.9 | 27.7 | 21.2 | 35 | 2.9 | 257.6 | 6.5 | 411.8 | 408.9 | 95.4 | 43.3 | 510.8 | 516.5 | 63.7 | 58.1 | 188.2 | 270.5 | 116 | 85.1 | 168.9 | 94.4 | 86.4 | 206.4 | 157.6 | 114.2 | 99.5 | 94.7 | 106.4 | 105 | 93.4 | 100.9 | 106.7
4069.1 | 3848.1 | -6.8 | 0 | 0 | 99 | 95.7 | 89.6 | 90.7 | 106.9 | 27.8 | 21.2 | 35 | 3.5 | 254.1 | 6.9 | 411.8 | 408.9 | 94.9 | 43.2 | 510.9 | 516.6 | 63.6 | 57.8 | 188.1 | 270.3 | 116.3 | 84.9 | 168.8 | 94.6 | 86.1 | 206.2 | 157.4 | 114.2 | 99.5 | 94.7 | 106.4 | 105 | 93.4 | 100.8 | 106.7
4070.1 | 3849.1 | -6.8 | 0 | 0 | 99 | 95.4 | 89.6 | 90.7 | 106.7 | 27.8 | 21.2 | 35 | 3.2 | 256 | 7.4 | 411.7 | 408.8 | 95.3 | 43.2 | 511 | 516.5 | 63.8 | 57.7 | 188.1 | 270 | 116.1 | 84.7 | 168.7 | 94.6 | 86 | 206 | 157.5 | 114.2 | 99.5 | 94.7 | 106.3 | 105 | 93.3 | 100.8 | 106.6
4071.1 | 3850.1 | -6.8 | 0 | 0 | 99.1 | 95.1 | 89.6 | 90.7 | 106.6 | 27.8 | 21.2 | 35 | 3 | 248.6 | 7.4 | 411.7 | 408.8 | 96 | 43.1 | 511.2 | 516.2 | 63.8 | 57.4 | 188.1 | 269.8 | 115.8 | 84.6 | 168.6 | 94.6 | 85.8 | 205.9 | 157.5 | 114.1 | 99.4 | 94.6 | 106.2 | 104.9 | 93.2 | 100.7 | 106.6
4072.1 | 3851.1 | -6.7 | 0 | 0 | 99.1 | 95.1 | 89.6 | 90.8 | 106.6 | 27.8 | 21.2 | 35 | 3.4 | 249.2 | 7.2 | 411.6 | 408.8 | 96.1 | 43 | 511.3 | 515.7 | 64 | 57.1 | 188 | 269.6 | 115.8 | 84.6 | 168.5 | 94.8 | 86 | 205.7 | 157.4 | 114 | 99.3 | 94.6 | 106.2 | 104.8 | 93.1 | 100.7 | 106.5
4073.1 | 3852.1 | -6.8 | 0 | 0 | 99.1 | 95.2 | 89.6 | 90.8 | 106.5 | 27.9 | 21.2 | 35 | 4 | 250.7 | 7.1 | 411.6 | 408.7 | 97 | 42.9 | 511.5 | 515.2 | 63.8 | 56.9 | 187.9 | 269.3 | 115.1 | 84.8 | 168.4 | 95 | 86.3 | 205.5 | 157.4 | 114 | 99.3 | 94.6 | 106.2 | 104.8 | 93.1 | 100.6 | 106.5
4074.1 | 3853.1 | -6.8 | 0 | 0 | 99 | 95.2 | 89.6 | 90.8 | 106.2 | 27.9 | 21.2 | 35 | 4 | 248.7 | 6.9 | 411.6 | 408.7 | 97.2 | 42.8 | 511.6 | 514.9 | 63.3 | 56.8 | 187.9 | 269.1 | 114.3 | 84.8 | 168.3 | 95 | 86.4 | 205.3 | 157.2 | 113.9 | 99.2 | 94.6 | 106.1 | 104.8 | 93.1 | 100.6 | 106.4
4075.1 | 3854.1 | -6.8 | 0 | 0 | 99 | 95.2 | 89.5 | 90.8 | 106 | 27.9 | 21.2 | 35 | 3.8 | 249.1 | 6.5 | 411.5 | 408.6 | 96.7 | 42.7 | 511.7 | 514.6 | 62.8 | 56.4 | 187.8 | 268.9 | 113.7 | 84.7 | 168.2 | 95 | 86.4 | 205.1 | 157.2 | 113.9 | 99.1 | 94.6 | 106 | 104.7 | 93.2 | 100.5 | 106.4
4076.1 | 3855.1 | -6.8 | 0 | 0 | 99 | 95.3 | 89.3 | 90.8 | 105.8 | 27.9 | 21.2 | 34.9 | 3.9 | 252.1 | 6.1 | 411.5 | 408.6 | 97 | 42.5 | 511.9 | 514.3 | 62.6 | 56.3 | 187.8 | 268.6 | 113.2 | 84.6 | 168.1 | 95 | 86.3 | 204.9 | 157.2 | 113.8 | 99.1 | 94.5 | 106 | 104.7 | 93.1 | 100.5 | 106.3
4077.1 | 3856.1 | -6.8 | 0 | 0 | 99 | 95.5 | 89.4 | 90.9 | 105.9 | 27.8 | 21.2 | 34.8 | 3.6 | 250.1 | 6.3 | 411.5 | 408.5 | 97.5 | 42.4 | 512 | 513.9 | 62.4 | 56.3 | 187.8 | 268.4 | 112.9 | 84.6 | 168 | 95 | 86.2 | 204.7 | 157 | 113.8 | 99 | 94.5 | 105.9 | 104.6 | 93 | 100.4 | 106.3
4078.1 | 3857.1 | -6.8 | 0 | 0 | 98.9 | 95.5 | 89.4 | 91 | 106.2 | 27.8 | 21.2 | 34.8 | 3.6 | 240 | 6.6 | 411.4 | 408.5 | 97.2 | 42.3 | 512 | 513.7 | 62.1 | 56.5 | 187.8 | 268.2 | 112.4 | 84.6 | 167.8 | 95.1 | 86.2 | 204.5 | 156.9 | 113.7 | 98.9 | 94.4 | 105.8 | 104.5 | 93 | 100.4 | 106.2
4079.1 | 3858.1 | -6.8 | 0 | 0 | 98.8 | 95.5 | 89.4 | 91 | 106.2 | 27.9 | 21.2 | 34.7 | 3.3 | 243.9 | 7.4 | 411.4 | 408.5 | 97.7 | 42.3 | 511.9 | 513.5 | 61.8 | 56.5 | 187.7 | 267.9 | 112.9 | 84.5 | 167.7 | 95.1 | 86.1 | 204.3 | 156.8 | 113.6 | 98.8 | 94.3 | 105.8 | 104.5 | 93 | 100.4 | 106.2
4080.1 | 3859.1 | -6.7 | 0 | 0 | 98.9 | 95.5 | 89.3 | 91 | 106.1 | 28 | 21.2 | 34.7 | 2.8 | 247.1 | 7.7 | 411.4 | 408.4 | 98.2 | 42.3 | 511.9 | 513.3 | 61.5 | 56.6 | 187.8 | 267.7 | 112.7 | 84.3 | 167.6 | 95 | 86 | 204.1 | 156.7 | 113.6 | 98.7 | 94.2 | 105.8 | 104.5 | 93 | 100.3 | 106.1
4081.1 | 3860.1 | -6.7 | 0 | 0 | 99 | 95.4 | 89.3 | 90.9 | 106 | 28 | 21.2 | 34.7 | 2.4 | 245.8 | 7.9 | 411.3 | 408.4 | 98.8 | 42.3 | 511.9 | 513.3 | 61.2 | 56.5 | 187.7 | 267.4 | 112.4 | 84.2 | 167.5 | 94.8 | 85.8 | 203.9 | 156.8 | 113.5 | 98.7 | 94.2 | 105.8 | 104.4 | 92.9 | 100.2 | 106
4082.1 | 3861.1 | -6.7 | 0 | 0 | 99 | 95.3 | 89.3 | 90.8 | 106 | 27.9 | 21.2 | 34.7 | 2.3 | 246.3 | 8 | 411.3 | 408.3 | 99 | 42.4 | 511.8 | 513.3 | 61.2 | 56.5 | 187.8 | 267.2 | 112 | 84 | 167.4 | 95.1 | 85.7 | 203.8 | 156.6 | 113.4 | 98.7 | 94.2 | 105.7 | 104.4 | 92.9 | 100.2 | 106
4083.1 | 3862.1 | -6.7 | 0 | 0 | 98.7 | 95.2 | 89.3 | 90.8 | 105.6 | 27.9 | 21.2 | 34.7 | 2.6 | 240.5 | 8.1 | 411.3 | 408.3 | 99.2 | 42.5 | 511.8 | 513.2 | 61.1 | 56.5 | 187.6 | 266.9 | 112.3 | 83.8 | 167.3 | 95.3 | 85.5 | 203.6 | 156.5 | 113.3 | 98.7 | 94.3 | 105.7 | 104.3 | 92.8 | 100.1 | 105.9
4084.1 | 3863.1 | -6.7 | 0 | 0 | 98.3 | 95.2 | 89.2 | 90.8 | 105.3 | 28 | 21.2 | 34.7 | 2.7 | 246.6 | 7.9 | 411.2 | 408.2 | 99.4 | 42.5 | 511.8 | 513 | 60.8 | 56.4 | 187.6 | 266.7 | 112.1 | 83.6 | 167.1 | 95.4 | 85.4 | 203.4 | 156.5 | 113.3 | 98.7 | 94.3 | 105.7 | 104.3 | 92.8 | 100 | 105.9
4085.1 | 3864.1 | -6.8 | 0 | 0 | 98.3 | 95.1 | 89.1 | 90.7 | 105.2 | 28 | 21.2 | 34.7 | 2.7 | 253.5 | 7 | 411.2 | 408.2 | 99.7 | 42.4 | 511.7 | 512.8 | 60.5 | 56.2 | 187.7 | 266.4 | 111.8 | 83.5 | 167 | 95.4 | 85 | 203.2 | 156.5 | 113.2 | 98.7 | 94.3 | 105.6 | 104.2 | 92.7 | 100 | 105.8
4086.1 | 3865.1 | -6.8 | 0 | 0 | 98.3 | 95.1 | 89 | 90.6 | 105.2 | 28 | 21.2 | 34.7 | 2.8 | 248 | 6.1 | 411.1 | 408.2 | 99.8 | 42.3 | 511.6 | 512.8 | 60.3 | 56 | 187.7 | 266.2 | 112 | 83.4 | 166.9 | 95.4 | 84.7 | 203 | 156.2 | 113.2 | 98.7 | 94.2 | 105.6 | 104.1 | 92.7 | 99.9 | 105.8
4087.1 | 3866.1 | -6.8 | 0 | 0 | 98.4 | 95.1 | 88.9 | 90.5 | 105.1 | 28.1 | 21.2 | 34.6 | 2.9 | 247.1 | 5.8 | 411.1 | 408.2 | 99.5 | 42.3 | 511.6 | 512.7 | 60 | 55.9 | 187.6 | 265.9 | 112.4 | 83.3 | 166.8 | 95.5 | 84.4 | 202.8 | 156.1 | 113.2 | 98.7 | 94.2 | 105.5 | 104.1 | 92.6 | 99.8 | 105.7
4088.1 | 3867.1 | -6.8 | 0 | 0 | 98.4 | 95.1 | 88.9 | 90.4 | 105.1 | 28.1 | 21.2 | 34.6 | 2.7 | 255.1 | 5.7 | 411.1 | 408.1 | 99.5 | 42.1 | 511.5 | 512.7 | 59.9 | 55.6 | 187.6 | 265.7 | 112.3 | 83.1 | 166.7 | 95.4 | 84.1 | 202.7 | 156 | 113.1 | 98.6 | 94.1 | 105.5 | 104 | 92.5 | 99.7 | 105.7
4089.1 | 3868.1 | -6.8 | 0 | 0 | 98.4 | 95.1 | 88.9 | 90.4 | 105.1 | 28 | 21.2 | 34.5 | 2.6 | 259.7 | 5.9 | 411 | 408.1 | 99.9 | 42 | 511.3 | 512.8 | 59.7 | 55.2 | 187.5 | 265.5 | 112.6 | 83 | 166.6 | 95 | 84 | 202.5 | 155.9 | 113.1 | 98.6 | 94.1 | 105.4 | 104 | 92.5 | 99.7 | 105.6
4090.1 | 3869.1 | -6.8 | 0 | 0 | 98.5 | 95 | 89 | 90.3 | 105 | 27.9 | 21.2 | 34.5 | 2.7 | 257.4 | 6.1 | 411 | 408 | 99.6 | 41.9 | 511.3 | 513 | 59.7 | 55 | 187.4 | 265.3 | 113.3 | 83 | 166.5 | 94.6 | 84.2 | 202.3 | 155.8 | 113 | 98.5 | 94 | 105.3 | 104 | 92.4 | 99.6 | 105.6
4091.1 | 3870.1 | -6.8 | 0 | 0 | 98.5 | 95.1 | 88.9 | 90.1 | 105 | 28 | 21.2 | 34.5 | 2.4 | 255.2 | 6.1 | 411 | 408 | 99.5 | 42 | 511.2 | 513 | 59.7 | 54.9 | 187.3 | 265 | 113.7 | 82.8 | 166.4 | 94.6 | 84.2 | 202.1 | 155.7 | 113 | 98.5 | 94 | 105.3 | 104 | 92.4 | 99.5 | 105.5
4092.1 | 3871.1 | -6.8 | 0 | 0 | 98.4 | 95.1 | 88.7 | 90 | 105.2 | 28 | 21.2 | 34.4 | 2.9 | 254.1 | 6.5 | 410.9 | 408 | 99.4 | 42.1 | 511.2 | 513.1 | 60.3 | 55 | 187.4 | 264.8 | 113.9 | 82.7 | 166.2 | 94.8 | 84.3 | 201.9 | 155.6 | 112.9 | 98.5 | 93.9 | 105.3 | 103.9 | 92.3 | 99.5 | 105.5
4093.1 | 3872.1 | -6.8 | 0 | 0 | 98.3 | 95.1 | 88.6 | 90.1 | 105.4 | 28 | 21.2 | 34.4 | 2.8 | 255.4 | 6.7 | 410.9 | 407.9 | 98.3 | 42.2 | 511.1 | 513.1 | 61 | 55.1 | 187.3 | 264.6 | 114 | 82.8 | 166.1 | 94.7 | 84.4 | 201.7 | 155.6 | 112.9 | 98.5 | 93.9 | 105.2 | 103.8 | 92.2 | 99.4 | 105.4
4094.1 | 3873.1 | -6.8 | 0 | 0 | 98.2 | 95.1 | 88.6 | 90.2 | 105.6 | 28 | 21.2 | 34.5 | 3 | 251 | 6.6 | 410.8 | 407.9 | 97.5 | 42.1 | 511 | 513.1 | 61.7 | 55.2 | 187.2 | 264.4 | 114.4 | 83 | 166 | 94.6 | 84.4 | 201.6 | 155.7 | 112.9 | 98.5 | 93.8 | 105.1 | 103.8 | 92.2 | 99.4 | 105.4
4095.1 | 3874.1 | -6.8 | 0 | 0 | 98.1 | 95 | 88.7 | 90.2 | 105.6 | 28 | 21.2 | 34.5 | 3.2 | 256.3 | 6.7 | 410.8 | 407.8 | 96.5 | 42 | 510.8 | 513.1 | 62.7 | 55.4 | 187.1 | 264.2 | 114.4 | 83 | 165.9 | 94.3 | 84.4 | 201.4 | 155.7 | 112.8 | 98.5 | 93.8 | 105.1 | 103.8 | 92.3 | 99.3 | 105.3
4096.1 | 3875.1 | -6.8 | 0 | 0 | 97.9 | 94.8 | 88.6 | 90.3 | 105.6 | 28.1 | 21.2 | 34.5 | 2.9 | 255.6 | 6.7 | 410.8 | 407.8 | 96.2 | 42 | 510.7 | 513.2 | 63.1 | 55.5 | 187 | 263.9 | 114.6 | 82.8 | 165.8 | 94 | 84.4 | 201.2 | 155.6 | 112.8 | 98.5 | 93.7 | 105 | 103.8 | 92.3 | 99.3 | 105.2
4097.1 | 3876.1 | -6.8 | 0 | 0 | 97.9 | 94.7 | 88.5 | 90.2 | 105.6 | 28.1 | 21.2 | 34.6 | 2.7 | 255.6 | 6.3 | 410.7 | 407.8 | 95.7 | 42.1 | 510.6 | 513.1 | 63.7 | 55.5 | 186.9 | 263.7 | 114.7 | 82.9 | 165.6 | 93.9 | 84.2 | 201 | 155.6 | 112.7 | 98.5 | 93.6 | 104.9 | 103.8 | 92.2 | 99.2 | 105.2
4098.1 | 3877.1 | -6.8 | 0 | 0 | 97.9 | 94.6 | 88.4 | 89.9 | 105.6 | 28.1 | 21.2 | 34.6 | 2.7 | 258.2 | 5.5 | 410.7 | 407.8 | 95.7 | 42.1 | 510.5 | 513.1 | 64.3 | 55.4 | 186.9 | 263.5 | 114.5 | 82.9 | 165.5 | 93.8 | 84.2 | 200.8 | 155.7 | 112.7 | 98.4 | 93.6 | 104.8 | 103.7 | 92.2 | 99.2 | 105.1
4099.1 | 3878.1 | -6.8 | 0 | 0 | 97.7 | 94.5 | 88.4 | 89.8 | 105.4 | 28.2 | 21.2 | 34.6 | 3.1 | 251.6 | 4.8 | 410.7 | 407.7 | 95.5 | 42.1 | 510.5 | 513 | 64.6 | 55.2 | 186.9 | 263.3 | 114.5 | 82.9 | 165.3 | 93.7 | 84.1 | 200.7 | 155.6 | 112.6 | 98.4 | 93.5 | 104.8 | 103.7 | 92.1 | 99.2 | 105.1
4100.1 | 3879.1 | -6.8 | 0 | 0 | 97.4 | 94.4 | 88.4 | 89.6 | 105.2 | 28.1 | 21.2 | 34.7 | 3.3 | 251.3 | 4.3 | 410.6 | 407.7 | 94.8 | 42 | 510.4 | 512.9 | 64.4 | 55.1 | 186.7 | 263.1 | 114.4 | 82.7 | 165.2 | 93.5 | 84.2 | 200.5 | 155.6 | 112.6 | 98.4 | 93.5 | 104.7 | 103.6 | 92 | 99.2 | 105.1
4101.1 | 3880.1 | -6.8 | 0 | 0 | 97.5 | 94.4 | 88.4 | 89.5 | 105 | 28 | 21.2 | 34.6 | 2.8 | 254.6 | 4.3 | 410.6 | 407.6 | 94.5 | 42.1 | 510.3 | 513 | 65.7 | 55.3 | 186.7 | 262.9 | 114.4 | 82.4 | 165.1 | 93.2 | 84.3 | 200.3 | 155.5 | 112.5 | 98.3 | 93.4 | 104.7 | 103.5 | 92 | 99.1 | 105
4102.1 | 3881.1 | -6.8 | 0 | 0 | 97.6 | 94.3 | 88.4 | 89.4 | 104.9 | 27.9 | 21.2 | 34.6 | 2.5 | 260 | 4.4 | 410.5 | 407.6 | 93.7 | 42.1 | 510.2 | 513 | 66.5 | 55.3 | 186.6 | 262.7 | 114.9 | 82.2 | 165 | 93.2 | 84.4 | 200.1 | 155.4 | 112.5 | 98.3 | 93.3 | 104.7 | 103.4 | 91.9 | 99.1 | 104.9
4103.1 | 3882.1 | -6.8 | 0 | 0 | 97.8 | 94.2 | 88.2 | 89.2 | 104.8 | 28 | 21.2 | 34.7 | 3 | 257.2 | 4.6 | 410.5 | 407.6 | 93.8 | 42 | 510.1 | 513 | 66.6 | 55.2 | 186.6 | 262.6 | 114.9 | 82 | 164.8 | 93 | 84.6 | 199.9 | 155.2 | 112.5 | 98.3 | 93.3 | 104.7 | 103.4 | 91.8 | 99 | 104.9
4104.1 | 3883.1 | -6.8 | 0 | 0 | 97.8 | 94.1 | 88 | 89 | 104.5 | 28.1 | 21.2 | 34.7 | 3.3 | 253.6 | 4.6 | 410.5 | 407.5 | 93.8 | 41.9 | 510 | 513 | 66.4 | 55.2 | 186.5 | 262.3 | 114.9 | 81.8 | 164.7 | 92.9 | 84.6 | 199.7 | 155.1 | 112.4 | 98.3 | 93.2 | 104.6 | 103.4 | 91.8 | 98.9 | 104.8
4105.1 | 3884.1 | -6.8 | 0 | 0 | 97.7 | 94 | 87.9 | 88.8 | 104.3 | 28.1 | 21.2 | 34.6 | 2.5 | 265.1 | 4.8 | 410.4 | 407.4 | 93.5 | 41.8 | 509.9 | 512.9 | 65.9 | 55 | 186.4 | 262.1 | 115.1 | 81.6 | 164.6 | 92.8 | 84.5 | 199.5 | 155.1 | 112.3 | 98.2 | 93.2 | 104.6 | 103.3 | 91.7 | 98.9 | 104.8
4106.1 | 3885.1 | -6.8 | 0 | 0 | 97.6 | 93.7 | 87.9 | 88.7 | 104.3 | 28 | 21.2 | 34.6 | 2.4 | 264.3 | 5 | 410.4 | 407.4 | 93.5 | 41.8 | 509.9 | 512.7 | 65.4 | 54.9 | 186.3 | 262 | 115.2 | 81.3 | 164.5 | 92.8 | 84.5 | 199.4 | 155.1 | 112.3 | 98.2 | 93 | 104.5 | 103.3 | 91.8 | 98.9 | 104.8
4107.1 | 3886.1 | -6.8 | 0 | 0 | 97.5 | 93.7 | 87.9 | 88.7 | 104.3 | 28 | 21.2 | 34.6 | 2.7 | 260.8 | 5.1 | 410.3 | 407.4 | 93.4 | 41.7 | 509.8 | 512.7 | 65.5 | 54.8 | 186.3 | 261.7 | 114.8 | 81.1 | 164.4 | 93 | 84.5 | 199.2 | 155 | 112.2 | 98.1 | 92.9 | 104.5 | 103.2 | 91.8 | 98.9 | 104.7
4108.1 | 3887.1 | -6.8 | 0 | 0 | 97.4 | 93.8 | 87.9 | 88.8 | 104.3 | 27.9 | 21.2 | 34.6 | 2.4 | 262.6 | 5.3 | 410.3 | 407.3 | 94 | 41.7 | 509.8 | 512.7 | 65.5 | 54.9 | 186.1 | 261.6 | 114.3 | 81 | 164.2 | 93.1 | 84.5 | 199 | 155 | 112.1 | 97.9 | 92.9 | 104.4 | 103.2 | 91.7 | 98.9 | 104.7
4109.1 | 3888.1 | -6.8 | 0 | 0 | 97.4 | 93.9 | 87.7 | 89 | 104.1 | 27.8 | 21.2 | 34.6 | 2.5 | 263 | 5.3 | 410.3 | 407.3 | 94.6 | 41.6 | 509.8 | 512.8 | 65.7 | 54.9 | 186.1 | 261.4 | 113.5 | 81.2 | 164.1 | 93 | 84.5 | 198.8 | 155 | 112.1 | 97.8 | 92.8 | 104.4 | 103.1 | 91.7 | 98.8 | 104.6
4110.1 | 3889.1 | -6.8 | 0 | 0 | 97.4 | 94.1 | 87.7 | 89 | 103.9 | 27.9 | 21.2 | 34.6 | 2.6 | 264.5 | 5.3 | 410.2 | 407.3 | 94.7 | 41.5 | 509.8 | 512.6 | 65.4 | 54.8 | 186 | 261.2 | 113.1 | 81.3 | 163.9 | 92.8 | 84.5 | 198.6 | 154.9 | 112 | 97.7 | 92.8 | 104.4 | 103.1 | 91.6 | 98.8 | 104.6
4111.1 | 3890.1 | -6.8 | 0 | 0 | 97.3 | 94.1 | 87.7 | 89 | 103.9 | 27.9 | 21.2 | 34.6 | 3.1 | 263.6 | 5.1 | 410.2 | 407.2 | 95 | 41.5 | 509.8 | 512.4 | 65 | 54.9 | 185.8 | 261 | 113.1 | 81.3 | 163.8 | 92.6 | 84.7 | 198.5 | 154.8 | 112 | 97.6 | 92.7 | 104.3 | 103 | 91.6 | 98.8 | 104.5
4112.1 | 3891.1 | -6.8 | 0 | 0 | 97.1 | 94.1 | 87.6 | 88.9 | 103.7 | 27.8 | 21.2 | 34.6 | 2.9 | 263.8 | 4.7 | 410.1 | 407.2 | 95.8 | 41.5 | 509.8 | 512.2 | 64.6 | 55 | 185.7 | 260.8 | 112.6 | 81.3 | 163.7 | 92.6 | 84.6 | 198.3 | 154.7 | 112 | 97.6 | 92.7 | 104.3 | 103 | 91.5 | 98.8 | 104.5
4113.1 | 3892.1 | -6.8 | 0 | 0 | 96.9 | 94.1 | 87.6 | 88.8 | 103.5 | 27.8 | 21.2 | 34.6 | 3.3 | 266.6 | 4.6 | 410.1 | 407.1 | 96.4 | 41.6 | 509.8 | 511.9 | 64.1 | 55.3 | 185.7 | 260.6 | 112.2 | 81.1 | 163.6 | 92.6 | 84.6 | 198.1 | 154.5 | 111.9 | 97.6 | 92.8 | 104.2 | 103 | 91.5 | 98.8 | 104.4
4114.1 | 3893.1 | -6.8 | 0 | 0 | 97 | 94.1 | 87.6 | 88.8 | 103.3 | 27.7 | 21.2 | 34.6 | 3 | 269.1 | 4.8 | 410.1 | 407.1 | 95.6 | 41.7 | 509.8 | 511.6 | 63.7 | 55.3 | 185.8 | 260.4 | 111.4 | 81 | 163.5 | 92.7 | 84.5 | 197.9 | 154.5 | 111.9 | 97.5 | 92.7 | 104.2 | 102.9 | 91.4 | 98.7 | 104.4
4115.1 | 3894.1 | -6.8 | 0 | 0 | 97 | 94.1 | 87.5 | 88.7 | 103.1 | 27.6 | 21.2 | 34.6 | 2.9 | 270.2 | 5.7 | 410 | 407 | 95.4 | 41.8 | 509.7 | 511.4 | 63.3 | 55.1 | 185.7 | 260.2 | 110.9 | 80.8 | 163.4 | 93 | 84.4 | 197.7 | 154.5 | 111.8 | 97.4 | 92.7 | 104.1 | 102.8 | 91.4 | 98.7 | 104.3
4116.1 | 3895.1 | -6.8 | 0 | 0 | 97.1 | 94 | 87.4 | 88.9 | 103.2 | 27.6 | 21.2 | 34.5 | 2.7 | 265.1 | 7 | 410 | 407 | 95.2 | 41.8 | 509.6 | 511.1 | 62.9 | 55 | 185.8 | 259.9 | 110.1 | 80.6 | 163.3 | 93.1 | 84.3 | 197.5 | 154.5 | 111.8 | 97.4 | 92.7 | 104.1 | 102.8 | 91.4 | 98.7 | 104.3
4117.1 | 3896.1 | -6.7 | 0 | 0 | 97.1 | 93.9 | 87.3 | 89 | 103.5 | 27.6 | 21.2 | 34.5 | 2.9 | 261.7 | 7.2 | 409.9 | 407 | 95.1 | 41.8 | 509.6 | 511.1 | 62.5 | 55 | 185.8 | 259.7 | 109.6 | 80.3 | 163.2 | 93.3 | 84.1 | 197.4 | 154.3 | 111.7 | 97.4 | 92.7 | 104.1 | 102.7 | 91.3 | 98.6 | 104.2
4118.1 | 3897.1 | -6.7 | 0 | 0 | 97 | 93.8 | 87.3 | 89 | 103.6 | 27.7 | 21.2 | 34.5 | 3 | 257.5 | 6.9 | 409.9 | 406.9 | 95 | 42 | 509.5 | 511.1 | 62.7 | 54.9 | 185.9 | 259.5 | 109.2 | 79.9 | 163 | 93.8 | 84 | 197.2 | 154.2 | 111.7 | 97.4 | 92.6 | 104 | 102.7 | 91.3 | 98.6 | 104.2
4119.1 | 3898.1 | -6.8 | 0 | 0 | 96.8 | 93.7 | 87.3 | 88.9 | 103.5 | 27.7 | 21.2 | 34.5 | 3.1 | 252.5 | 6.9 | 409.9 | 406.9 | 94.3 | 42.1 | 509.5 | 510.8 | 63.2 | 54.7 | 185.8 | 259.3 | 109 | 79.7 | 162.9 | 93.8 | 83.9 | 197 | 154.1 | 111.6 | 97.4 | 92.5 | 103.9 | 102.6 | 91.2 | 98.6 | 104.1
4120.1 | 3899.1 | -6.8 | 0 | 0 | 96.7 | 93.7 | 87.3 | 88.9 | 103.2 | 27.6 | 21.2 | 34.5 | 3.3 | 255.3 | 7 | 409.8 | 406.9 | 94.2 | 42 | 509.5 | 510.6 | 64 | 54.8 | 185.7 | 259.1 | 109.3 | 79.5 | 162.8 | 93.9 | 84.1 | 196.8 | 154 | 111.6 | 97.4 | 92.4 | 103.8 | 102.6 | 91.2 | 98.6 | 104.1
4121.1 | 3900.1 | -6.8 | 0 | 0 | 96.6 | 93.8 | 87.2 | 88.8 | 103.2 | 27.5 | 21.2 | 34.5 | 3.5 | 251.2 | 6.9 | 409.8 | 406.8 | 94.1 | 42 | 509.6 | 510.4 | 64.2 | 55.2 | 185.6 | 258.9 | 109.7 | 79.3 | 162.6 | 94 | 84.1 | 196.7 | 153.9 | 111.5 | 97.3 | 92.3 | 103.8 | 102.5 | 91.1 | 98.5 | 104
4122.1 | 3901.1 | -6.8 | 0 | 0 | 96.6 | 93.9 | 87.2 | 88.9 | 103.3 | 27.4 | 21.2 | 34.5 | 3.2 | 251.7 | 6.8 | 409.7 | 406.8 | 93.5 | 42 | 509.6 | 510.2 | 64.6 | 55.6 | 185.8 | 258.6 | 109.2 | 79.2 | 162.5 | 94.3 | 84 | 196.5 | 153.8 | 111.4 | 97.3 | 92.2 | 103.7 | 102.4 | 91 | 98.5 | 104
4123.1 | 3902.1 | -6.8 | 0 | 0 | 96.7 | 94 | 87.2 | 88.9 | 103.4 | 27.4 | 21.2 | 34.5 | 3.4 | 251.1 | 6.9 | 409.7 | 406.7 | 93.6 | 42.1 | 509.5 | 510 | 65.6 | 55.8 | 185.8 | 258.4 | 108.7 | 79.2 | 162.3 | 94.4 | 83.7 | 196.3 | 153.6 | 111.4 | 97.2 | 92.2 | 103.7 | 102.3 | 90.9 | 98.4 | 103.9
4124.1 | 3903.1 | -6.8 | 0 | 0 | 96.7 | 94 | 87.3 | 88.9 | 103.3 | 27.4 | 21.2 | 34.5 | 3.6 | 248.7 | 6.9 | 409.7 | 406.7 | 93.9 | 42.2 | 509.5 | 509.9 | 66.8 | 55.8 | 185.8 | 258.2 | 108.3 | 79.1 | 162.2 | 94.5 | 83.7 | 196.1 | 153.5 | 111.3 | 97.2 | 92.2 | 103.7 | 102.3 | 90.8 | 98.3 | 103.9
4125.1 | 3904.1 | -6.8 | 0 | 0 | 96.5 | 93.7 | 87.3 | 88.8 | 103.1 | 27.4 | 21.2 | 34.5 | 3.2 | 248.8 | 6.6 | 409.6 | 406.6 | 93.7 | 42.3 | 509.4 | 509.8 | 67.4 | 55.9 | 185.7 | 258 | 107.9 | 79.3 | 162 | 94.6 | 83.6 | 195.9 | 153.5 | 111.3 | 97.1 | 92.1 | 103.6 | 102.2 | 90.8 | 98.2 | 103.8
4126.1 | 3905.1 | -6.8 | 0 | 0 | 96.2 | 93.4 | 87.3 | 88.6 | 103 | 27.4 | 21.2 | 34.4 | 3 | 251.9 | 6.4 | 409.6 | 406.6 | 93.3 | 42.6 | 509.3 | 509.8 | 67.2 | 56 | 185.7 | 257.8 | 108.4 | 79.3 | 161.9 | 94.6 | 83.6 | 195.7 | 153.4 | 111.2 | 97.1 | 92.1 | 103.6 | 102.2 | 90.8 | 98.2 | 103.8
4127.1 | 3906.1 | -6.8 | 0 | 0 | 96.1 | 93.2 | 87.3 | 88.4 | 103.1 | 27.5 | 21.2 | 34.4 | 2.5 | 249.8 | 6.1 | 409.6 | 406.6 | 92.8 | 42.8 | 509.3 | 509.8 | 66.8 | 56 | 185.8 | 257.6 | 109 | 79.4 | 161.7 | 94.3 | 83.8 | 195.5 | 153.5 | 111.2 | 97 | 92.1 | 103.6 | 102.2 | 90.8 | 98.1 | 103.7
4128.1 | 3907.1 | -6.8 | 0 | 0 | 96.1 | 93.2 | 87.3 | 88.3 | 103.2 | 27.5 | 21.2 | 34.4 | 2.4 | 249.8 | 6 | 409.5 | 406.5 | 92.2 | 43 | 509.2 | 509.9 | 66.4 | 56.1 | 185.8 | 257.4 | 109 | 79.4 | 161.6 | 94 | 83.8 | 195.4 | 153.3 | 111.1 | 97 | 92.1 | 103.5 | 102.1 | 90.7 | 98.1 | 103.7
4129.1 | 3908.1 | -6.8 | 0 | 0 | 96.2 | 93.2 | 87.2 | 88.2 | 103.2 | 27.6 | 21.2 | 34.3 | 2.8 | 250.4 | 6.3 | 409.5 | 406.5 | 92.4 | 43.1 | 509.1 | 509.9 | 66 | 56.4 | 185.9 | 257.2 | 109.1 | 79.3 | 161.5 | 93.9 | 83.8 | 195.2 | 153.1 | 111.1 | 97 | 92.1 | 103.5 | 102.1 | 90.6 | 98.1 | 103.6
4130.1 | 3909.1 | -6.8 | 0 | 0 | 96.2 | 93.2 | 87.2 | 88.2 | 103.3 | 27.6 | 21.2 | 34.3 | 2.9 | 248.1 | 6.4 | 409.4 | 406.4 | 92.3 | 43.1 | 509.1 | 510.1 | 65.8 | 56.6 | 185.9 | 257 | 108.7 | 79.4 | 161.3 | 93.7 | 83.9 | 195 | 152.9 | 111 | 96.9 | 92 | 103.4 | 102 | 90.4 | 98.1 | 103.6
4131.1 | 3910.1 | -6.8 | 0 | 0 | 96.3 | 93.1 | 87.2 | 88.1 | 103.3 | 27.6 | 21.2 | 34.3 | 2.9 | 247 | 6.3 | 409.4 | 406.4 | 92.5 | 43.1 | 509 | 510.2 | 65.6 | 56.7 | 185.9 | 256.8 | 108.2 | 79.3 | 161.2 | 93.3 | 83.9 | 194.8 | 153 | 111 | 97 | 92 | 103.3 | 102 | 90.4 | 98 | 103.5
4132.1 | 3911.1 | -6.8 | 0 | 0 | 96.3 | 92.9 | 87.3 | 88 | 103.2 | 27.5 | 21.2 | 34.3 | 2.6 | 250.4 | 5.9 | 409.4 | 406.4 | 93 | 43.1 | 508.9 | 510.2 | 65.4 | 56.5 | 185.9 | 256.5 | 107.8 | 79.1 | 161.1 | 93 | 83.8 | 194.6 | 153 | 110.9 | 97 | 91.9 | 103.3 | 102 | 90.4 | 98 | 103.5
4133.1 | 3912.1 | -6.8 | 0 | 0 | 96.1 | 92.7 | 87.2 | 88 | 103.1 | 27.5 | 21.2 | 34.2 | 2.9 | 251.5 | 5.7 | 409.3 | 406.3 | 92.5 | 43.3 | 508.8 | 510.1 | 65.2 | 56.5 | 186 | 256.3 | 107.7 | 79 | 161 | 92.9 | 83.8 | 194.5 | 152.9 | 110.9 | 97 | 91.9 | 103.3 | 101.9 | 90.4 | 97.9 | 103.4
4134.1 | 3913.1 | -6.8 | 0 | 0 | 95.7 | 92.8 | 87.1 | 88.1 | 103 | 27.5 | 21.2 | 34.2 | 3 | 251.1 | 5.8 | 409.3 | 406.3 | 92 | 43.6 | 508.6 | 510.1 | 65 | 56.4 | 186.1 | 256.1 | 107.6 | 78.9 | 160.8 | 92.8 | 84 | 194.3 | 153 | 110.9 | 96.9 | 91.8 | 103.2 | 101.9 | 90.4 | 97.8 | 103.4
4135.1 | 3914.1 | -6.8 | 0 | 0 | 95.5 | 93.1 | 87 | 88.2 | 103 | 27.6 | 21.2 | 34.2 | 2.8 | 250.2 | 6.1 | 409.2 | 406.2 | 91.8 | 43.5 | 508.5 | 510.2 | 64.8 | 56.4 | 186.2 | 255.9 | 108.1 | 78.9 | 160.7 | 92.6 | 83.9 | 194.1 | 152.9 | 110.8 | 96.9 | 91.8 | 103.2 | 101.9 | 90.4 | 97.8 | 103.4
4136.1 | 3915.1 | -6.8 | 0 | 0 | 95.5 | 93.2 | 87 | 88.2 | 103.1 | 27.7 | 21.2 | 34.2 | 2.6 | 256.4 | 5.9 | 409.2 | 406.2 | 92.2 | 43.5 | 508.3 | 510.5 | 65.5 | 56.3 | 186.2 | 255.7 | 108.3 | 78.8 | 160.6 | 92.3 | 83.8 | 193.9 | 152.8 | 110.7 | 96.8 | 91.7 | 103.1 | 101.8 | 90.4 | 97.8 | 103.3
4137.1 | 3916.1 | -6.7 | 0 | 0 | 95.5 | 93.1 | 86.9 | 88.1 | 103.3 | 27.7 | 21.2 | 34.1 | 2.9 | 259.6 | 5.9 | 409.2 | 406.2 | 92.3 | 43.3 | 508.2 | 511.2 | 65.7 | 56.2 | 186 | 255.5 | 107.9 | 78.8 | 160.5 | 92.2 | 83.8 | 193.8 | 152.7 | 110.7 | 96.8 | 91.6 | 103.1 | 101.8 | 90.4 | 97.8 | 103.3
4138.1 | 3917.1 | -6.5 | 0 | 0 | 95.5 | 93 | 86.8 | 88 | 103.3 | 27.7 | 21.2 | 34.1 | 2.9 | 258.5 | 6.1 | 409.1 | 406.1 | 91.8 | 43.2 | 508.1 | 511.4 | 66.3 | 56.1 | 185.9 | 255.3 | 107.8 | 78.9 | 160.3 | 91.8 | 83.8 | 193.6 | 152.6 | 110.7 | 96.8 | 91.7 | 103.1 | 101.7 | 90.3 | 97.7 | 103.2
4139.1 | 3918.1 | -6.6 | 0 | 0 | 95.4 | 93.1 | 86.8 | 88 | 103.1 | 27.7 | 21.2 | 34.1 | 3 | 244.2 | 6.3 | 409.1 | 406 | 91 | 43.1 | 508 | 511.5 | 66.8 | 56.1 | 185.9 | 255.1 | 107.8 | 79 | 160.2 | 91.7 | 83.5 | 193.4 | 152.7 | 110.6 | 96.8 | 91.7 | 103 | 101.7 | 90.3 | 97.7 | 103.2
4140.1 | 3919.1 | -6.7 | 0 | 0 | 95.1 | 93.1 | 86.8 | 88 | 103 | 27.6 | 21.2 | 34.1 | 3.1 | 253.4 | 6.2 | 409.1 | 406 | 90.8 | 43.1 | 508 | 511.5 | 67.6 | 56.1 | 185.8 | 254.9 | 107.9 | 78.8 | 160.1 | 91.8 | 83.4 | 193.2 | 152.5 | 110.5 | 96.7 | 91.7 | 102.9 | 101.6 | 90.2 | 97.7 | 103.1
4141.1 | 3920.1 | -6.7 | 0 | 0 | 94.8 | 93.1 | 86.7 | 87.9 | 102.8 | 27.6 | 21.2 | 34.1 | 3 | 270.2 | 5.6 | 409 | 405.9 | 90.9 | 43.1 | 507.9 | 511.6 | 69 | 56.3 | 185.7 | 254.7 | 108.2 | 78.8 | 159.9 | 91.8 | 83.4 | 193 | 152.5 | 110.5 | 96.6 | 91.6 | 102.9 | 101.6 | 90.2 | 97.7 | 103.1
4142.1 | 3921.1 | -6.7 | 0 | 0 | 94.7 | 93.1 | 86.7 | 87.9 | 102.7 | 27.6 | 21.2 | 34.1 | 2.8 | 268.9 | 5.1 | 409 | 405.9 | 90.6 | 43.2 | 507.8 | 511.9 | 70.3 | 56.5 | 185.7 | 254.5 | 108.5 | 78.7 | 159.8 | 91.8 | 83.4 | 192.9 | 152.5 | 110.4 | 96.6 | 91.6 | 102.8 | 101.5 | 90.2 | 97.6 | 103
4143.1 | 3922.1 | -6.8 | 0 | 0 | 94.8 | 93 | 86.7 | 87.8 | 102.8 | 27.6 | 21.2 | 34.1 | 3.1 | 264 | 4.7 | 408.9 | 405.9 | 90.4 | 43.6 | 507.7 | 512.1 | 70.7 | 56.7 | 185.6 | 254.3 | 108.8 | 78.6 | 159.7 | 91.7 | 83.4 | 192.7 | 152.4 | 110.3 | 96.6 | 91.6 | 102.8 | 101.4 | 90.1 | 97.6 | 103
4144.1 | 3923.1 | -6.8 | 0 | 0 | 95 | 93 | 86.6 | 87.7 | 103 | 27.5 | 21.2 | 34.1 | 3.3 | 263.4 | 4.4 | 408.9 | 405.8 | 90.1 | 43.8 | 507.6 | 512.1 | 71.4 | 56.7 | 185.6 | 254.1 | 109.7 | 78.4 | 159.5 | 91.7 | 83.2 | 192.5 | 152.2 | 110.3 | 96.6 | 91.6 | 102.8 | 101.3 | 90 | 97.5 | 102.9
4145.1 | 3924.1 | -6.8 | 0 | 0 | 95.1 | 92.9 | 86.7 | 87.8 | 103.1 | 27.6 | 21.2 | 34.1 | 3.4 | 269.9 | 4.4 | 408.9 | 405.8 | 90.5 | 43.8 | 507.5 | 512 | 70.9 | 56.8 | 185.6 | 253.9 | 110 | 78.2 | 159.4 | 91.8 | 83 | 192.3 | 152.2 | 110.3 | 96.5 | 91.5 | 102.7 | 101.3 | 90 | 97.4 | 102.9
4146.1 | 3925.1 | -6.8 | 0 | 0 | 95.1 | 92.9 | 86.7 | 87.7 | 102.9 | 27.6 | 21.2 | 34 | 3.2 | 278.9 | 4.9 | 408.8 | 405.7 | 90.8 | 43.8 | 507.5 | 511.8 | 70.4 | 57 | 185.6 | 253.7 | 109.8 | 78.1 | 159.3 | 91.8 | 82.8 | 192.2 | 152.3 | 110.2 | 96.5 | 91.4 | 102.6 | 101.2 | 90 | 97.4 | 102.8
4147.1 | 3926.1 | -6.8 | 0 | 0 | 95.1 | 92.8 | 86.7 | 87.6 | 102.6 | 27.5 | 21.2 | 34 | 3.3 | 263.5 | 5.3 | 408.8 | 405.7 | 90.7 | 43.9 | 507.4 | 511.6 | 70.6 | 57.3 | 185.6 | 253.5 | 109.4 | 78 | 159.2 | 91.7 | 82.8 | 192 | 152.3 | 110.1 | 96.4 | 91.4 | 102.6 | 101.2 | 90 | 97.3 | 102.8
4148.1 | 3927.1 | -6.8 | 0 | 0 | 95 | 92.6 | 86.6 | 87.4 | 102.2 | 27.5 | 21.2 | 34 | 3.2 | 258 | 5.2 | 408.8 | 405.6 | 90.6 | 43.9 | 507.3 | 511.5 | 71.1 | 57.2 | 185.5 | 253.3 | 109 | 77.8 | 159.1 | 91.8 | 82.6 | 191.8 | 152.2 | 110.1 | 96.4 | 91.3 | 102.5 | 101.2 | 90 | 97.3 | 102.7
4149.1 | 3928.1 | -6.8 | 0 | 0 | 94.7 | 92.4 | 86.6 | 87.3 | 102 | 27.5 | 21.2 | 33.9 | 2.9 | 255.3 | 5.1 | 408.7 | 405.6 | 90.6 | 43.9 | 507.2 | 511.3 | 71.3 | 57.2 | 185.5 | 253.1 | 108.5 | 77.7 | 158.9 | 91.9 | 82.3 | 191.6 | 152.3 | 110 | 96.4 | 91.3 | 102.5 | 101.2 | 90 | 97.3 | 102.7
4150.1 | 3929.1 | -6.8 | 0 | 0 | 94.5 | 92.5 | 86.6 | 87.2 | 101.9 | 27.6 | 21.2 | 33.8 | 3 | 264.2 | 4.7 | 408.7 | 405.6 | 91.1 | 43.8 | 507.1 | 511 | 71.3 | 57.2 | 185.5 | 252.9 | 107.9 | 77.7 | 158.8 | 91.9 | 82.3 | 191.5 | 152.2 | 110 | 96.4 | 91.3 | 102.5 | 101.1 | 90 | 97.3 | 102.6
4151.1 | 3930.1 | -6.8 | 0 | 0 | 94.4 | 92.6 | 86.6 | 87.4 | 101.9 | 27.6 | 21.2 | 33.8 | 3 | 271.3 | 4.6 | 408.7 | 405.5 | 90.8 | 43.8 | 507 | 510.8 | 71.4 | 57.2 | 185.3 | 252.7 | 107.4 | 77.8 | 158.7 | 91.9 | 82.3 | 191.3 | 152.1 | 109.9 | 96.3 | 91.3 | 102.4 | 101.1 | 89.9 | 97.2 | 102.6
4152.1 | 3931.1 | -6.8 | 0 | 0 | 94.3 | 92.7 | 86.5 | 87.5 | 102.1 | 27.6 | 21.2 | 33.8 | 2.8 | 280.4 | 4.4 | 408.6 | 405.5 | 90.4 | 43.7 | 506.9 | 510.6 | 71.7 | 57.1 | 185.2 | 252.5 | 106.8 | 77.9 | 158.5 | 91.8 | 82.4 | 191.1 | 152.1 | 109.9 | 96.2 | 91.2 | 102.4 | 101 | 89.9 | 97.2 | 102.5
4153.1 | 3932.1 | -6.8 | 0 | 0 | 94.3 | 92.7 | 86.4 | 87.6 | 102.3 | 27.6 | 21.2 | 33.8 | 3 | 275 | 4.5 | 408.6 | 405.4 | 90.4 | 43.8 | 506.7 | 510.8 | 72.3 | 57.2 | 185.3 | 252.3 | 106.4 | 78.2 | 158.4 | 91.9 | 82.3 | 190.9 | 152.1 | 109.8 | 96.1 | 91.2 | 102.3 | 101 | 89.8 | 97.1 | 102.5
4154.1 | 3933.1 | -6.8 | 0 | 0 | 94.3 | 92.7 | 86.3 | 87.6 | 102.5 | 27.6 | 21.2 | 33.8 | 3.5 | 270.5 | 4.6 | 408.5 | 405.4 | 89.6 | 43.9 | 506.6 | 510.9 | 72.7 | 57.3 | 185.2 | 252.1 | 106.1 | 78.3 | 158.3 | 91.9 | 82.4 | 190.7 | 152.3 | 109.7 | 96 | 91.1 | 102.3 | 100.9 | 89.8 | 97 | 102.4
4155.1 | 3934.1 | -6.8 | 0 | 0 | 94.2 | 92.7 | 86.2 | 87.7 | 102.5 | 27.7 | 21.2 | 33.8 | 3 | 267.1 | 4.8 | 408.5 | 405.4 | 89.4 | 43.9 | 506.4 | 511 | 72.8 | 57.5 | 185.2 | 252 | 106.2 | 78.2 | 158.2 | 91.7 | 82.2 | 190.6 | 152.3 | 109.7 | 95.9 | 91.1 | 102.3 | 100.9 | 89.7 | 97 | 102.4
4156.1 | 3935.1 | -6.8 | 0 | 0 | 94.1 | 92.7 | 86.1 | 87.7 | 102.6 | 27.8 | 21.2 | 33.8 | 2.6 | 261.7 | 4.7 | 408.5 | 405.3 | 89.6 | 44.1 | 506.2 | 510.9 | 73.4 | 57.7 | 185.2 | 251.8 | 106.4 | 78.2 | 158.1 | 91.3 | 82.1 | 190.4 | 152.2 | 109.6 | 95.8 | 91.1 | 102.2 | 100.9 | 89.7 | 97 | 102.3
4157.1 | 3936.1 | -6.7 | 0 | 0 | 94.1 | 92.7 | 86.1 | 87.6 | 102.7 | 27.8 | 21.2 | 33.8 | 2.5 | 267.8 | 4.6 | 408.4 | 405.2 | 89 | 44.3 | 506 | 510.7 | 73.6 | 57.6 | 185.2 | 251.6 | 106.8 | 78 | 158 | 90.9 | 82.1 | 190.2 | 152.1 | 109.6 | 95.8 | 91.1 | 102.1 | 100.8 | 89.6 | 97 | 102.3
4158.1 | 3937.1 | -6.7 | 0 | 0 | 94.1 | 92.7 | 86.1 | 87.5 | 102.7 | 27.7 | 21.2 | 33.9 | 3 | 269.4 | 4.6 | 408.4 | 405.2 | 89.1 | 44.3 | 505.9 | 510.6 | 73.5 | 57.6 | 185.2 | 251.4 | 106.7 | 77.8 | 157.9 | 90.6 | 82.2 | 190 | 152.2 | 109.6 | 95.8 | 91.1 | 102.1 | 100.7 | 89.5 | 96.9 | 102.2
4159.1 | 3938.1 | -6.7 | 0 | 0 | 94.2 | 92.7 | 86.1 | 87.3 | 102.7 | 27.6 | 21.2 | 33.9 | 2.5 | 260.6 | 4.5 | 408.4 | 405.2 | 89.4 | 44.3 | 505.8 | 510.5 | 72.8 | 57.6 | 185.2 | 251.2 | 106.7 | 77.6 | 157.8 | 90.8 | 82.2 | 189.9 | 152.1 | 109.5 | 95.7 | 91.1 | 102.1 | 100.7 | 89.4 | 96.9 | 102.2
4160.1 | 3939.1 | -6.7 | 0 | 0 | 94.3 | 92.6 | 86.1 | 87.2 | 102.7 | 27.5 | 21.2 | 33.9 | 2.6 | 261.5 | 4.4 | 408.3 | 405.1 | 88.9 | 44.4 | 505.6 | 510.6 | 72.1 | 57.6 | 185.1 | 251.1 | 107.1 | 77.3 | 157.6 | 90.8 | 81.9 | 189.7 | 152.1 | 109.5 | 95.7 | 91 | 102 | 100.6 | 89.4 | 96.8 | 102.1
4161.1 | 3940.1 | -6.7 | 0 | 0 | 94.4 | 92.4 | 86.1 | 87.1 | 102.7 | 27.5 | 21.2 | 33.9 | 2.9 | 272.6 | 4.7 | 408.3 | 405.1 | 89.2 | 44.3 | 505.5 | 510.8 | 71.2 | 57.5 | 185 | 250.9 | 106.9 | 76.9 | 157.5 | 90.6 | 81.5 | 189.5 | 151.9 | 109.4 | 95.6 | 90.9 | 101.9 | 100.6 | 89.4 | 96.7 | 102.1
4162.1 | 3941.1 | -6.7 | 0 | 0 | 94.4 | 92.1 | 86 | 87.1 | 102.5 | 27.5 | 21.3 | 34 | 2.7 | 271.3 | 5.2 | 408.3 | 405.1 | 88.8 | 44.3 | 505.4 | 510.8 | 70.4 | 57.2 | 185 | 250.7 | 106.8 | 76.5 | 157.4 | 90.5 | 81.2 | 189.3 | 151.7 | 109.3 | 95.5 | 90.8 | 101.8 | 100.6 | 89.4 | 96.6 | 102
4163.1 | 3942.1 | -6.7 | 0 | 0 | 94.5 | 92 | 85.9 | 87 | 102.4 | 27.6 | 21.2 | 34 | 3.4 | 267.3 | 5.4 | 408.2 | 405 | 88.9 | 44.1 | 505.4 | 510.7 | 69.7 | 56.7 | 185 | 250.5 | 107.1 | 76.2 | 157.3 | 90.4 | 80.8 | 189.2 | 151.7 | 109.3 | 95.4 | 90.7 | 101.8 | 100.6 | 89.5 | 96.5 | 101.9
4164.1 | 3943.1 | -6.7 | 0 | 0 | 94.4 | 92 | 85.8 | 87 | 102.4 | 27.6 | 21.2 | 34 | 3.6 | 265.9 | 5 | 408.2 | 405 | 88.7 | 43.7 | 505.3 | 510.7 | 68.9 | 56.2 | 184.9 | 250.4 | 107.1 | 76 | 157.2 | 90.2 | 80.8 | 189 | 151.8 | 109.2 | 95.3 | 90.7 | 101.8 | 100.5 | 89.4 | 96.5 | 101.9
4165.1 | 3944.1 | -6.8 | 0 | 0 | 94.4 | 92.1 | 85.6 | 87 | 102.5 | 27.7 | 21.2 | 34 | 3.6 | 263.8 | 4.6 | 408.2 | 404.9 | 88.4 | 43.5 | 505.3 | 510.8 | 68.6 | 55.9 | 184.7 | 250.2 | 107.4 | 75.9 | 157.1 | 90 | 80.7 | 188.8 | 151.7 | 109.1 | 95.2 | 90.7 | 101.8 | 100.5 | 89.4 | 96.4 | 101.9
4166.1 | 3945.1 | -6.8 | 0 | 0 | 94.5 | 92.1 | 85.5 | 87 | 102.7 | 27.7 | 21.3 | 34 | 3.3 | 268 | 4.7 | 408.1 | 404.9 | 88.2 | 43.4 | 505.2 | 510.7 | 69.2 | 55.7 | 184.6 | 250 | 107.6 | 75.8 | 157 | 89.8 | 80.6 | 188.6 | 151.7 | 109.1 | 95.2 | 90.7 | 101.7 | 100.5 | 89.4 | 96.4 | 101.8
4167.1 | 3946.1 | -6.8 | 0 | 0 | 94.6 | 92 | 85.5 | 87.1 | 102.7 | 27.8 | 21.2 | 34 | 3.1 | 266.6 | 5 | 408.1 | 404.8 | 88.3 | 43.2 | 505.2 | 510.6 | 69.1 | 55.7 | 184.6 | 249.8 | 107.5 | 75.9 | 156.9 | 89.6 | 80.7 | 188.5 | 151.8 | 109.1 | 95.3 | 90.6 | 101.6 | 100.4 | 89.4 | 96.4 | 101.8
4168.1 | 3947.1 | -6.8 | 0 | 0 | 94.6 | 91.7 | 85.5 | 87.1 | 102.6 | 27.9 | 21.2 | 34 | 3.4 | 258.8 | 5.4 | 408.1 | 404.8 | 88.1 | 43.2 | 505.1 | 510.8 | 69.2 | 55.8 | 184.5 | 249.6 | 107.5 | 76.1 | 156.8 | 89.6 | 80.7 | 188.3 | 151.6 | 109 | 95.2 | 90.5 | 101.5 | 100.4 | 89.4 | 96.4 | 101.7
4169.1 | 3948.1 | -6.8 | 0 | 0 | 94.6 | 91.4 | 85.5 | 87.1 | 102.6 | 27.8 | 21.3 | 34 | 3.6 | 258.6 | 5.7 | 408 | 404.7 | 87.8 | 43.1 | 505.1 | 510.7 | 69 | 55.8 | 184.5 | 249.4 | 107.6 | 76 | 156.7 | 89.5 | 80.7 | 188.1 | 151.6 | 109 | 95.2 | 90.4 | 101.5 | 100.4 | 89.4 | 96.4 | 101.7
4170.1 | 3949.1 | -6.8 | 0 | 0 | 94.5 | 91.2 | 85.5 | 87.1 | 102.6 | 27.8 | 21.2 | 34 | 3.3 | 261.6 | 5.7 | 408 | 404.7 | 87.9 | 43.1 | 505.2 | 510.5 | 68.9 | 55.9 | 184.3 | 249.3 | 107 | 75.8 | 156.6 | 89.6 | 80.5 | 187.9 | 151.5 | 108.9 | 95.1 | 90.3 | 101.5 | 100.4 | 89.4 | 96.4 | 101.6
4171.1 | 3950.1 | -6.8 | 0 | 0 | 94.3 | 91.1 | 85.5 | 87.1 | 102.4 | 27.8 | 21.2 | 34 | 2.9 | 261.7 | 5.4 | 408 | 404.6 | 87.4 | 43.2 | 505.2 | 510.5 | 69.2 | 56 | 184.2 | 249.1 | 106.4 | 75.8 | 156.5 | 89.9 | 80.5 | 187.8 | 151.4 | 108.8 | 95.1 | 90.3 | 101.4 | 100.3 | 89.3 | 96.3 | 101.6
4172.1 | 3951.1 | -6.8 | 0 | 0 | 94.2 | 91.2 | 85.5 | 87.2 | 102 | 27.7 | 21.3 | 33.9 | 3.2 | 266.7 | 5.3 | 407.9 | 404.6 | 86.9 | 43.1 | 505.1 | 510.6 | 69.7 | 56.1 | 184.2 | 248.9 | 105.8 | 75.7 | 156.4 | 90 | 80.8 | 187.6 | 151.4 | 108.8 | 95.1 | 90.3 | 101.4 | 100.2 | 89.2 | 96.3 | 101.5
4173.1 | 3952.1 | -6.8 | 0 | 0 | 94.3 | 91.2 | 85.4 | 87.3 | 101.9 | 27.7 | 21.3 | 33.9 | 3.4 | 264.5 | 5.1 | 407.9 | 404.5 | 86.5 | 43 | 505 | 510.8 | 70.2 | 56.1 | 184.3 | 248.7 | 105.3 | 75.8 | 156.3 | 90.1 | 80.8 | 187.4 | 151.4 | 108.7 | 95 | 90.2 | 101.3 | 100.2 | 89.1 | 96.3 | 101.5
4174.1 | 3953.1 | -6.8 | 0 | 0 | 94.3 | 91.2 | 85.3 | 87.3 | 101.9 | 27.6 | 21.3 | 33.9 | 3.3 | 260.6 | 4.9 | 407.9 | 404.5 | 87 | 42.9 | 505 | 510.8 | 71 | 56 | 184.2 | 248.5 | 104.9 | 75.7 | 156.2 | 89.9 | 80.9 | 187.2 | 151.5 | 108.7 | 94.9 | 90.2 | 101.3 | 100.2 | 89.1 | 96.2 | 101.5
4175.1 | 3954.1 | -6.8 | 0 | 0 | 94.3 | 91.1 | 85.2 | 87.2 | 101.9 | 27.5 | 21.3 | 33.9 | 3.1 | 266.3 | 4.8 | 407.8 | 404.5 | 87.5 | 43 | 505 | 510.7 | 70.8 | 56 | 184.1 | 248.4 | 104.8 | 75.8 | 156.1 | 89.7 | 80.7 | 187 | 151.5 | 108.7 | 94.9 | 90.2 | 101.3 | 100.2 | 89 | 96.2 | 101.4
4176.1 | 3955.1 | -6.8 | 0 | 0 | 94.3 | 91.2 | 85.2 | 87.2 | 102.1 | 27.4 | 21.3 | 33.9 | 2.9 | 274.4 | 4.5 | 407.8 | 404.4 | 87.4 | 42.9 | 504.9 | 510.5 | 70.2 | 56 | 184.1 | 248.2 | 104.6 | 76 | 156 | 89.8 | 80.6 | 186.9 | 151.5 | 108.6 | 94.9 | 90.2 | 101.2 | 100.1 | 88.9 | 96.2 | 101.4
4177.1 | 3956.1 | -6.8 | 0 | 0 | 94.4 | 91.3 | 85.2 | 87.2 | 102.3 | 27.5 | 21.3 | 34 | 3.2 | 262.8 | 4.4 | 407.8 | 404.4 | 87.6 | 42.8 | 504.9 | 510.3 | 69.4 | 55.9 | 184.1 | 248 | 104.3 | 75.9 | 155.8 | 89.8 | 80.7 | 186.7 | 151.5 | 108.6 | 94.9 | 90.1 | 101.2 | 100.1 | 88.8 | 96.2 | 101.3
4178.1 | 3957.1 | -6.8 | 0 | 0 | 94.3 | 91.3 | 85.2 | 87.1 | 102.5 | 27.6 | 21.3 | 34 | 3.3 | 259.8 | 4.1 | 407.7 | 404.4 | 88.3 | 42.7 | 505 | 510.1 | 69 | 56 | 183.9 | 247.9 | 103.9 | 75.7 | 155.7 | 89.7 | 80.6 | 186.5 | 151.3 | 108.5 | 94.9 | 90.1 | 101.1 | 100 | 88.7 | 96.1 | 101.3
4179.1 | 3958.1 | -6.8 | 0 | 0 | 94.2 | 91.3 | 85.1 | 87 | 102.6 | 27.7 | 21.3 | 34 | 3.4 | 260.6 | 3.7 | 407.7 | 404.3 | 89.2 | 42.8 | 505 | 509.9 | 69.6 | 56 | 184.1 | 247.7 | 103.6 | 75.5 | 155.6 | 89.6 | 80.5 | 186.3 | 151.2 | 108.5 | 94.9 | 90.1 | 101.1 | 100 | 88.7 | 96 | 101.2
4180.1 | 3959.1 | -6.8 | 0 | 0 | 94 | 91.2 | 85 | 86.9 | 102.6 | 27.7 | 21.3 | 34 | 3.3 | 260 | 3.5 | 407.7 | 404.3 | 89.5 | 42.8 | 505.1 | 509.8 | 70.2 | 56.1 | 184.1 | 247.5 | 103.4 | 75.7 | 155.5 | 89.6 | 80.4 | 186.2 | 151.1 | 108.4 | 94.8 | 90 | 101.1 | 100 | 88.6 | 95.9 | 101.2
4181.1 | 3960.1 | -6.8 | 0 | 0 | 93.8 | 91.1 | 84.9 | 86.8 | 102.3 | 27.7 | 21.3 | 34 | 3.3 | 259.7 | 3.3 | 407.6 | 404.2 | 88.9 | 42.8 | 505.1 | 509.6 | 70.1 | 56.2 | 184 | 247.3 | 103.2 | 75.9 | 155.4 | 89.5 | 80.5 | 186 | 151 | 108.4 | 94.8 | 89.9 | 101.1 | 99.9 | 88.6 | 95.9 | 101.1
4182.1 | 3961.1 | -6.8 | 0 | 0 | 93.6 | 90.9 | 84.9 | 86.7 | 101.9 | 27.8 | 21.3 | 34 | 3.2 | 258.6 | 3.1 | 407.6 | 404.1 | 88.2 | 42.8 | 505.1 | 509.5 | 70.5 | 56.2 | 184 | 247.1 | 103 | 76 | 155.2 | 89.3 | 80.4 | 185.8 | 150.7 | 108.3 | 94.8 | 89.8 | 101 | 99.9 | 88.6 | 95.9 | 101.1
4183.1 | 3962.1 | -6.8 | 0 | 0 | 93.6 | 90.6 | 84.8 | 86.6 | 101.5 | 27.8 | 21.3 | 34 | 3.2 | 257.7 | 3 | 407.6 | 404.1 | 87.7 | 42.9 | 505 | 509.6 | 71 | 56.5 | 183.9 | 246.9 | 102.8 | 76.1 | 155.1 | 89.3 | 80.3 | 185.7 | 150.6 | 108.2 | 94.8 | 89.8 | 101 | 99.9 | 88.6 | 95.8 | 101
4184.1 | 3963.1 | -6.8 | 0 | 0 | 93.5 | 90.6 | 84.8 | 86.6 | 101.2 | 27.8 | 21.3 | 34 | 3.1 | 246.8 | 3.4 | 407.5 | 404.1 | 87.2 | 42.9 | 504.9 | 509.7 | 71.3 | 56.6 | 183.9 | 246.8 | 103.1 | 76.2 | 155 | 89.2 | 80.4 | 185.5 | 150.6 | 108.1 | 94.8 | 89.7 | 100.9 | 99.9 | 88.5 | 95.8 | 101
4185.1 | 3964.1 | -6.8 | 0 | 0 | 93.6 | 90.6 | 84.9 | 86.6 | 101 | 27.8 | 21.3 | 34 | 3.3 | 227.6 | 3.9 | 407.5 | 404 | 86.5 | 42.9 | 504.8 | 509.8 | 71.6 | 56.4 | 183.7 | 246.6 | 103.7 | 76.2 | 154.9 | 88.9 | 80.3 | 185.3 | 150.6 | 108.1 | 94.8 | 89.7 | 100.8 | 99.8 | 88.4 | 95.8 | 100.9
4186.1 | 3965.1 | -6.8 | 0 | 0 | 93.5 | 90.6 | 84.9 | 86.5 | 101.2 | 27.7 | 21.3 | 34 | 3.4 | 232.1 | 3.7 | 407.5 | 404 | 86.5 | 42.7 | 504.7 | 509.9 | 71.5 | 56.2 | 183.6 | 246.4 | 104.1 | 76.2 | 154.7 | 88.6 | 80.3 | 185.1 | 150.4 | 108 | 94.8 | 89.6 | 100.8 | 99.8 | 88.3 | 95.7 | 100.9
4187.1 | 3966.1 | -6.8 | 0 | 0 | 93.4 | 90.6 | 84.8 | 86.4 | 101.3 | 27.8 | 21.3 | 33.9 | 3.6 | 244.1 | 4 | 407.4 | 403.9 | 86.2 | 42.6 | 504.6 | 509.9 | 70.9 | 56.1 | 183.5 | 246.2 | 104.5 | 76.1 | 154.6 | 88.6 | 80.2 | 185 | 150.2 | 108 | 94.8 | 89.6 | 100.7 | 99.7 | 88.2 | 95.7 | 100.8
4188.1 | 3967.1 | -6.8 | 0 | 0 | 93.4 | 90.6 | 84.8 | 86.2 | 101.3 | 27.8 | 21.3 | 33.9 | 3.1 | 242.1 | 4.4 | 407.4 | 403.9 | 85.9 | 42.5 | 504.6 | 509.8 | 70.6 | 55.9 | 183.5 | 246 | 104.8 | 75.9 | 154.5 | 88.8 | 80.2 | 184.8 | 150.2 | 107.9 | 94.7 | 89.5 | 100.7 | 99.7 | 88.2 | 95.7 | 100.8
4189.1 | 3968.1 | -6.8 | 0 | 0 | 93.4 | 90.4 | 84.9 | 86.2 | 101.2 | 27.7 | 21.3 | 33.9 | 2.7 | 241.4 | 4.7 | 407.4 | 403.9 | 86 | 42.4 | 504.5 | 509.7 | 71 | 56 | 183.4 | 245.8 | 104.8 | 75.6 | 154.4 | 89 | 79.9 | 184.6 | 150.1 | 107.9 | 94.6 | 89.5 | 100.6 | 99.7 | 88.2 | 95.6 | 100.7
4190.1 | 3969.1 | -6.8 | 0 | 0 | 93.4 | 90.4 | 84.9 | 86.2 | 101.2 | 27.7 | 21.3 | 33.9 | 2.6 | 241.9 | 4.7 | 407.4 | 403.8 | 85.8 | 42.3 | 504.5 | 509.6 | 71.2 | 55.9 | 183.3 | 245.7 | 104.9 | 75.5 | 154.3 | 89.2 | 79.7 | 184.5 | 149.8 | 107.8 | 94.5 | 89.4 | 100.6 | 99.7 | 88.1 | 95.6 | 100.7
4191.1 | 3970.1 | -6.7 | 0 | 0 | 93.4 | 90.4 | 84.8 | 86.3 | 101.1 | 27.6 | 21.3 | 33.9 | 2.3 | 241.4 | 4.8 | 407.3 | 403.8 | 85.2 | 42.1 | 504.6 | 509.3 | 71.9 | 55.8 | 183.2 | 245.5 | 105.4 | 75.2 | 154.2 | 89.1 | 79.6 | 184.3 | 149.7 | 107.7 | 94.4 | 89.4 | 100.5 | 99.6 | 88 | 95.5 | 100.6
4192.1 | 3971.1 | -6.7 | 0 | 0 | 93.5 | 90.5 | 84.6 | 86.4 | 100.9 | 27.5 | 21.3 | 33.9 | 2.3 | 239.1 | 4.7 | 407.3 | 403.7 | 84.9 | 42 | 504.7 | 509 | 72.1 | 55.7 | 183.2 | 245.3 | 106 | 75 | 154.1 | 88.9 | 79.2 | 184.1 | 149.7 | 107.7 | 94.4 | 89.3 | 100.5 | 99.6 | 88 | 95.5 | 100.6
4193.1 | 3972.1 | -6.7 | 0 | 0 | 93.5 | 90.5 | 84.3 | 86.3 | 100.7 | 27.4 | 21.3 | 33.9 | 2.1 | 239.3 | 4.6 | 407.3 | 403.7 | 84.8 | 41.9 | 504.9 | 508.7 | 72.3 | 55.5 | 183 | 245.1 | 106.5 | 74.9 | 154 | 88.9 | 79.1 | 184 | 149.7 | 107.6 | 94.3 | 89.2 | 100.4 | 99.6 | 87.9 | 95.4 | 100.5
4194.1 | 3973.1 | -6.8 | 0 | 0 | 93.6 | 90.6 | 84.2 | 86.2 | 100.5 | 27.4 | 21.3 | 34 | 2.3 | 242.7 | 4.3 | 407.2 | 403.6 | 84.8 | 41.8 | 505.1 | 508.3 | 71.7 | 55.4 | 183 | 244.9 | 106.6 | 75.1 | 153.9 | 88.7 | 78.8 | 183.8 | 149.6 | 107.5 | 94.2 | 89.2 | 100.4 | 99.6 | 87.8 | 95.4 | 100.5
4195.1 | 3974.1 | -6.7 | 0 | 0 | 93.7 | 90.6 | 84.3 | 86.1 | 100.4 | 27.6 | 21.3 | 34 | 2.4 | 249.7 | 4 | 407.2 | 403.6 | 85.6 | 41.7 | 505.3 | 508 | 70.8 | 55.3 | 182.9 | 244.7 | 107.1 | 75.2 | 153.8 | 88.6 | 78.5 | 183.6 | 149.6 | 107.5 | 94.2 | 89.1 | 100.3 | 99.5 | 87.9 | 95.4 | 100.4
4196.1 | 3975.1 | -6.8 | 0 | 0 | 93.8 | 90.6 | 84.3 | 86.1 | 100.6 | 27.6 | 21.3 | 34 | 2.1 | 247.4 | 4.1 | 407.2 | 403.6 | 85.9 | 41.5 | 505.5 | 507.6 | 70.1 | 55.4 | 182.7 | 244.5 | 107.5 | 75.1 | 153.7 | 88.5 | 78.3 | 183.5 | 149.6 | 107.4 | 94.1 | 89.1 | 100.3 | 99.5 | 87.8 | 95.4 | 100.4
4197.1 | 3976.1 | -6.8 | 0 | 0 | 93.8 | 90.5 | 84.2 | 86 | 100.8 | 27.5 | 21.3 | 34 | 2.1 | 247.1 | 4 | 407.2 | 403.5 | 86.6 | 41.4 | 505.6 | 507.2 | 69.3 | 55.4 | 182.6 | 244.3 | 107.7 | 75 | 153.6 | 88.4 | 78.3 | 183.3 | 149.4 | 107.4 | 94.1 | 89.2 | 100.3 | 99.4 | 87.8 | 95.4 | 100.3
4198.1 | 3977.1 | -6.7 | 0 | 0 | 93.8 | 90.2 | 84.2 | 85.9 | 100.8 | 27.5 | 21.3 | 34 | 2.1 | 247.8 | 3.9 | 407.1 | 403.4 | 86.8 | 41.5 | 505.6 | 506.9 | 68.5 | 55.3 | 182.6 | 244.1 | 107.7 | 74.9 | 153.5 | 88.4 | 78.4 | 183.1 | 149.3 | 107.3 | 94.1 | 89.1 | 100.2 | 99.3 | 87.7 | 95.3 | 100.3
4199.1 | 3978.1 | -6.8 | 0 | 0 | 93.8 | 89.9 | 84.2 | 86 | 100.8 | 27.5 | 21.3 | 34 | 2 | 250.2 | 3.8 | 407.1 | 403.4 | 87.2 | 41.4 | 505.7 | 506.7 | 67.9 | 55.1 | 182.4 | 243.9 | 108 | 74.9 | 153.4 | 88.3 | 78.6 | 183 | 149.3 | 107.3 | 94 | 89 | 100.2 | 99.3 | 87.7 | 95.3 | 100.3
4200.1 | 3979.1 | -6.8 | 0 | 0 | 93.8 | 89.7 | 84.3 | 85.9 | 100.9 | 27.5 | 21.3 | 33.9 | 2.1 | 249.5 | 4 | 407.1 | 403.3 | 87.3 | 41.4 | 505.8 | 506.6 | 67.2 | 55.2 | 182.4 | 243.7 | 107.4 | 75 | 153.3 | 88.3 | 78.6 | 182.8 | 149.2 | 107.2 | 94 | 89 | 100.1 | 99.2 | 87.6 | 95.2 | 100.2
4201.1 | 3980.1 | -6.7 | 0 | 0 | 93.9 | 89.6 | 84.2 | 85.9 | 100.9 | 27.6 | 21.3 | 33.9 | 2.1 | 238.8 | 4 | 407 | 403.3 | 86.4 | 41.4 | 505.8 | 506.4 | 66.6 | 55.1 | 182.4 | 243.5 | 107 | 74.9 | 153.2 | 88.3 | 78.7 | 182.6 | 149.1 | 107.2 | 94 | 88.9 | 100.1 | 99.2 | 87.6 | 95.2 | 100.2
4202.1 | 3981.1 | -6.7 | 0 | 0 | 93.9 | 89.6 | 84.1 | 85.9 | 100.9 | 27.5 | 21.3 | 33.9 | 2 | 241.2 | 3.7 | 407 | 403.3 | 87.1 | 41.3 | 505.8 | 506.2 | 66.2 | 55.2 | 182.4 | 243.3 | 106.9 | 74.7 | 153.1 | 88.3 | 78.6 | 182.5 | 149.1 | 107.1 | 93.9 | 88.8 | 100.1 | 99.2 | 87.6 | 95.1 | 100.1
4203.1 | 3982.1 | -6.7 | 0 | 0 | 93.9 | 89.5 | 84 | 85.9 | 100.9 | 27.4 | 21.3 | 33.9 | 2 | 249.5 | 3.5 | 406.9 | 403.2 | 88.2 | 41.4 | 505.8 | 506 | 65.6 | 55.2 | 182.5 | 243.1 | 106.2 | 74.9 | 153 | 88.5 | 78.7 | 182.3 | 149 | 107.1 | 93.9 | 88.8 | 100 | 99.1 | 87.6 | 95.1 | 100.1
4204.1 | 3983.1 | -6.7 | 0 | 0 | 93.8 | 89.4 | 83.9 | 85.9 | 101 | 27.4 | 21.3 | 34 | 2.2 | 239.9 | 3.3 | 406.9 | 403.2 | 87.7 | 41.5 | 505.8 | 505.9 | 65.3 | 55.4 | 182.5 | 242.9 | 105.5 | 75 | 152.9 | 88.8 | 78.8 | 182.1 | 148.9 | 107.1 | 93.9 | 88.8 | 99.9 | 99.1 | 87.6 | 95.1 | 100
4205.1 | 3984.1 | -6.7 | 0 | 0 | 93.7 | 89.4 | 83.9 | 85.9 | 101.1 | 27.3 | 21.3 | 34 | 2.3 | 236.6 | 3 | 406.9 | 403.1 | 87.1 | 41.4 | 505.7 | 505.8 | 65.2 | 55.3 | 182.4 | 242.7 | 105 | 75 | 152.8 | 89.2 | 78.8 | 182 | 148.8 | 107 | 93.8 | 88.8 | 99.9 | 99.1 | 87.6 | 95 | 100
4206.1 | 3985.1 | -6.7 | 0 | 0 | 93.5 | 89.5 | 83.8 | 85.9 | 101.2 | 27.3 | 21.3 | 34.1 | 2.4 | 236.7 | 2.8 | 406.8 | 403.1 | 87.1 | 41.4 | 505.7 | 505.7 | 65.2 | 55.1 | 182.4 | 242.5 | 104.6 | 75.1 | 152.7 | 89.6 | 78.9 | 181.8 | 148.7 | 107 | 93.8 | 88.7 | 99.8 | 99 | 87.5 | 94.9 | 99.9
4207.1 | 3986.1 | -6.7 | 0 | 0 | 93.3 | 89.5 | 83.8 | 86 | 101.3 | 27.3 | 21.3 | 34.1 | 2.2 | 236.5 | 2.6 | 406.8 | 403 | 87.2 | 41.4 | 505.7 | 505.6 | 65.3 | 55.2 | 182.3 | 242.3 | 104 | 75.1 | 152.6 | 89.6 | 79 | 181.6 | 148.8 | 106.9 | 93.8 | 88.7 | 99.8 | 99 | 87.5 | 94.9 | 99.9
4208.1 | 3987.1 | -6.7 | 0 | 0 | 93 | 89.6 | 83.8 | 85.9 | 101.3 | 27.3 | 21.3 | 34.1 | 2.2 | 241.3 | 2.4 | 406.8 | 403 | 87.1 | 41.3 | 505.7 | 505.7 | 65.6 | 55.4 | 182.2 | 242.1 | 103.5 | 75.2 | 152.5 | 89.8 | 78.8 | 181.5 | 148.8 | 106.8 | 93.7 | 88.6 | 99.7 | 98.9 | 87.5 | 94.8 | 99.8
4209.1 | 3988.1 | -6.7 | 0 | 0 | 92.6 | 89.7 | 83.8 | 85.8 | 101.3 | 27.3 | 21.3 | 34 | 2.1 | 246.3 | 2.6 | 406.7 | 403 | 86.5 | 41.4 | 505.7 | 506 | 66.8 | 55.3 | 182.2 | 241.9 | 102.7 | 75.3 | 152.4 | 89.9 | 78.6 | 181.3 | 148.7 | 106.8 | 93.6 | 88.6 | 99.7 | 98.8 | 87.5 | 94.7 | 99.8
4210.1 | 3989.1 | -6.8 | 0 | 0 | 92.4 | 89.7 | 83.7 | 85.7 | 101.1 | 27.3 | 21.3 | 34 | 2.8 | 246.6 | 3 | 406.7 | 402.9 | 86.1 | 41.5 | 505.7 | 506.5 | 67.3 | 55.3 | 182 | 241.7 | 102.4 | 75.4 | 152.3 | 89.6 | 78.5 | 181.1 | 148.5 | 106.7 | 93.6 | 88.6 | 99.7 | 98.8 | 87.4 | 94.7 | 99.7
4211.1 | 3990.1 | -6.7 | 0 | 0 | 92.3 | 89.8 | 83.6 | 85.6 | 100.7 | 27.3 | 21.3 | 34 | 2.3 | 244.3 | 3.2 | 406.7 | 402.9 | 86.1 | 41.4 | 505.7 | 507 | 67.1 | 55.4 | 182 | 241.5 | 102.3 | 75.5 | 152.2 | 89.6 | 78.6 | 181 | 148.3 | 106.7 | 93.5 | 88.6 | 99.7 | 98.7 | 87.3 | 94.6 | 99.7
4212.1 | 3991.1 | -6.7 | 0 | 0 | 92.3 | 89.8 | 83.6 | 85.4 | 100.4 | 27.2 | 21.3 | 34 | 2.5 | 227.4 | 3.1 | 406.6 | 402.8 | 86 | 41.3 | 505.7 | 507.4 | 67.2 | 55.6 | 182 | 241.2 | 102 | 75.5 | 152.1 | 89.4 | 78.6 | 180.8 | 148.2 | 106.6 | 93.5 | 88.6 | 99.7 | 98.6 | 87.2 | 94.6 | 99.6
4213.1 | 3992.1 | -6.7 | 0 | 0 | 92.3 | 89.8 | 83.7 | 85.3 | 100.1 | 27.2 | 21.3 | 34 | 2.6 | 195.8 | 3.5 | 406.6 | 402.8 | 86.1 | 41.3 | 505.6 | 507.6 | 66.9 | 55.6 | 181.9 | 241 | 102.2 | 75.4 | 151.9 | 89.2 | 78.5 | 180.7 | 148.2 | 106.6 | 93.4 | 88.6 | 99.6 | 98.5 | 87.1 | 94.5 | 99.6
4214.1 | 3993.1 | -6.7 | 0 | 0 | 92.4 | 89.8 | 83.8 | 85.2 | 100 | 27.2 | 21.3 | 34 | 2.5 | 203.6 | 3.7 | 406.6 | 402.8 | 86.9 | 41.3 | 505.6 | 507.5 | 66.4 | 55.5 | 181.9 | 240.8 | 102.2 | 75.3 | 151.8 | 89.1 | 78.7 | 180.5 | 148.2 | 106.6 | 93.4 | 88.6 | 99.5 | 98.5 | 87 | 94.5 | 99.6
4215.1 | 3994.1 | -6.8 | 0 | 0 | 92.5 | 89.7 | 83.9 | 85 | 100 | 27.3 | 21.3 | 34 | 2.9 | 226.3 | 3.7 | 406.5 | 402.7 | 87.9 | 41.3 | 505.6 | 507.4 | 66 | 55.4 | 181.8 | 240.6 | 101.7 | 75.3 | 151.7 | 89 | 79.2 | 180.3 | 147.9 | 106.5 | 93.3 | 88.6 | 99.5 | 98.4 | 86.9 | 94.4 | 99.5
4216.1 | 3995.1 | -6.8 | 0 | 0 | 92.5 | 89.6 | 84 | 84.9 | 99.8 | 27.3 | 21.3 | 34 | 2.5 | 227.7 | 3.5 | 406.5 | 402.7 | 88.2 | 41.4 | 505.6 | 507.5 | 65.6 | 55.4 | 181.8 | 240.4 | 101.1 | 75 | 151.6 | 89.2 | 79.1 | 180.2 | 147.8 | 106.5 | 93.3 | 88.5 | 99.5 | 98.4 | 86.9 | 94.4 | 99.5
4217.1 | 3996.1 | -6.8 | 0 | 0 | 92.4 | 89.5 | 83.9 | 84.8 | 99.6 | 27.3 | 21.3 | 34 | 2.8 | 226.3 | 3.3 | 406.5 | 402.6 | 88.2 | 41.4 | 505.5 | 507.6 | 65.5 | 55.5 | 181.8 | 240.2 | 100.7 | 74.7 | 151.5 | 89.3 | 79.4 | 180 | 147.7 | 106.5 | 93.3 | 88.5 | 99.4 | 98.4 | 86.9 | 94.3 | 99.4
4218.1 | 3997.1 | -6.8 | 0 | 0 | 92.2 | 89.2 | 83.9 | 84.7 | 99.4 | 27.2 | 21.3 | 33.9 | 2.7 | 225 | 3 | 406.4 | 402.6 | 87.4 | 41.5 | 505.4 | 508 | 66 | 55.4 | 181.7 | 240 | 100.4 | 75 | 151.4 | 89.7 | 79.6 | 179.9 | 147.6 | 106.4 | 93.3 | 88.4 | 99.3 | 98.3 | 86.9 | 94.3 | 99.4
4219.1 | 3998.1 | -6.7 | 0 | 0 | 92.1 | 89.1 | 83.8 | 84.7 | 99.3 | 27.2 | 21.3 | 34 | 3.1 | 221 | 2.8 | 406.4 | 402.6 | 86.7 | 41.5 | 505.3 | 508.3 | 66.8 | 55.5 | 181.6 | 239.8 | 100.3 | 75 | 151.3 | 89.8 | 79.9 | 179.7 | 147.6 | 106.3 | 93.2 | 88.3 | 99.3 | 98.3 | 86.9 | 94.3 | 99.3
4220.1 | 3999.1 | -6.6 | 0 | 0 | 92.1 | 88.9 | 83.7 | 84.7 | 99.3 | 27.2 | 21.3 | 33.9 | 3.2 | 224.5 | 3 | 406.3 | 402.5 | 86.5 | 41.7 | 505.1 | 508.5 | 67.5 | 55.7 | 181.6 | 239.6 | 100.6 | 75.1 | 151.2 | 89.5 | 80.1 | 179.5 | 147.7 | 106.2 | 93.2 | 88.3 | 99.2 | 98.2 | 86.8 | 94.3 | 99.3
4221.1 | 4000.1 | -6.6 | 0 | 0 | 92.1 | 88.7 | 83.7 | 84.8 | 99.3 | 27.2 | 21.3 | 33.9 | 3.3 | 229.3 | 3.3 | 406.3 | 402.5 | 86.3 | 41.7 | 505 | 508.6 | 67.9 | 55.8 | 181.7 | 239.4 | 101.5 | 75.4 | 151.1 | 89.2 | 80.1 | 179.4 | 147.6 | 106.2 | 93.2 | 88.2 | 99.2 | 98.2 | 86.7 | 94.2 | 99.2
4222.1 | 4001.1 | -6.7 | 0 | 0 | 92.1 | 88.6 | 83.7 | 84.8 | 99.2 | 27.2 | 21.3 | 33.9 | 3.1 | 224.1 | 3.2 | 406.3 | 402.4 | 85.9 | 41.7 | 504.8 | 508.5 | 68.4 | 55.9 | 181.7 | 239.2 | 101.9 | 75.6 | 151 | 88.8 | 80 | 179.2 | 147.5 | 106.1 | 93.2 | 88.1 | 99.1 | 98.1 | 86.6 | 94.2 | 99.2
4223.1 | 4002.1 | -6.7 | 0 | 0 | 92.1 | 88.6 | 83.7 | 84.6 | 99.1 | 27.1 | 21.3 | 33.9 | 2.8 | 229.6 | 3.3 | 406.2 | 402.4 | 85.4 | 41.6 | 504.7 | 508.5 | 68.4 | 55.6 | 181.7 | 239 | 102.3 | 75.6 | 150.9 | 88.7 | 79.7 | 179 | 147.4 | 106.1 | 93.1 | 88.1 | 99 | 98.1 | 86.6 | 94.2 | 99.2
4224.1 | 4003.1 | -6.7 | 0 | 0 | 92 | 88.6 | 83.6 | 84.3 | 99.1 | 27.1 | 21.3 | 33.8 | 2.6 | 236.2 | 3.4 | 406.2 | 402.3 | 85.1 | 41.5 | 504.6 | 508.7 | 68.6 | 55.5 | 181.7 | 238.8 | 102.5 | 75.8 | 150.7 | 88.5 | 79.4 | 178.9 | 147.5 | 106 | 93.1 | 88 | 99 | 98 | 86.5 | 94.2 | 99.1
4225.1 | 4004.1 | -6.7 | 0 | 0 | 92 | 88.8 | 83.6 | 84.1 | 99.1 | 27.2 | 21.3 | 33.8 | 2.5 | 237.1 | 3.4 | 406.2 | 402.3 | 85 | 41.4 | 504.4 | 509.2 | 68.1 | 55.3 | 181.6 | 238.6 | 102.2 | 75.8 | 150.6 | 88.2 | 79.5 | 178.7 | 147.4 | 105.9 | 93 | 87.9 | 98.9 | 98 | 86.5 | 94.1 | 99.1
4226.1 | 4005.1 | -6.7 | 0 | 0 | 92 | 88.9 | 83.7 | 84 | 98.9 | 27.3 | 21.3 | 33.8 | 2.5 | 232.6 | 3.1 | 406.1 | 402.2 | 85.7 | 41.4 | 504.3 | 509.7 | 67.4 | 55.2 | 181.5 | 238.4 | 101.9 | 75.6 | 150.5 | 87.9 | 79.3 | 178.6 | 147.4 | 105.9 | 93 | 87.9 | 98.9 | 97.9 | 86.4 | 94.1 | 99
4227.1 | 4006.1 | -6.8 | 0 | 0 | 92 | 89 | 83.7 | 84 | 98.7 | 27.3 | 21.3 | 33.8 | 3.1 | 236.8 | 2.7 | 406.1 | 402.2 | 86 | 41.3 | 504.2 | 510 | 66.5 | 54.9 | 181.5 | 238.2 | 101.9 | 75.7 | 150.4 | 87.8 | 79.2 | 178.4 | 147.1 | 105.9 | 93 | 87.9 | 98.9 | 97.9 | 86.3 | 94 | 99
4228.1 | 4007.1 | -6.8 | 0 | 0 | 92 | 88.8 | 83.6 | 84 | 98.5 | 27.3 | 21.3 | 33.8 | 2.8 | 240.2 | 2.3 | 406 | 402.1 | 85.7 | 41.3 | 504.2 | 510 | 65.9 | 54.9 | 181.5 | 238 | 102 | 75.7 | 150.3 | 87.9 | 79.1 | 178.3 | 147 | 105.8 | 92.9 | 87.9 | 98.9 | 97.8 | 86.3 | 94 | 99
4229.1 | 4008.1 | -6.8 | 0 | 0 | 92 | 88.6 | 83.5 | 84 | 98.7 | 27.3 | 21.3 | 33.7 | 2.7 | 238.1 | 2 | 406 | 402.1 | 85.7 | 41.3 | 504.1 | 509.9 | 65.2 | 55 | 181.3 | 237.8 | 102.5 | 75.6 | 150.2 | 87.7 | 79 | 178.1 | 146.9 | 105.8 | 92.8 | 87.9 | 98.9 | 97.8 | 86.3 | 93.9 | 98.9
4230.1 | 4009.1 | -6.8 | 0 | 0 | 92 | 88.4 | 83.3 | 83.9 | 98.7 | 27.2 | 21.3 | 33.7 | 2.5 | 236.3 | 1.9 | 406 | 402.1 | 85.6 | 41.4 | 504 | 509.8 | 64.6 | 55.2 | 181.3 | 237.7 | 102.6 | 75.4 | 150.1 | 87.6 | 79 | 177.9 | 146.8 | 105.7 | 92.8 | 88 | 98.8 | 97.7 | 86.3 | 93.9 | 98.9
4231.1 | 4010.1 | -6.8 | 0 | 0 | 92 | 88.4 | 83.1 | 84 | 98.7 | 27.1 | 21.3 | 33.7 | 2.8 | 236.8 | 2.1 | 405.9 | 402 | 85.8 | 41.5 | 504 | 509.7 | 64.3 | 55.4 | 181.4 | 237.5 | 102.4 | 75.3 | 150 | 87.6 | 78.9 | 177.8 | 146.8 | 105.6 | 92.7 | 87.9 | 98.8 | 97.7 | 86.3 | 93.9 | 98.8
4232.1 | 4011.1 | -6.8 | 0 | 0 | 91.9 | 88.4 | 83 | 84 | 98.7 | 27.1 | 21.3 | 33.6 | 2.8 | 233.9 | 2.1 | 405.9 | 402 | 86 | 41.6 | 503.9 | 509.6 | 63.9 | 55.4 | 181.4 | 237.3 | 102.2 | 75.3 | 149.9 | 87.8 | 78.8 | 177.6 | 146.8 | 105.6 | 92.7 | 87.9 | 98.7 | 97.6 | 86.3 | 93.9 | 98.8
4233.1 | 4012.1 | -6.8 | 0 | 0 | 91.8 | 88.5 | 82.9 | 84.2 | 98.7 | 27.1 | 21.3 | 33.5 | 2.8 | 227.1 | 2.2 | 405.8 | 401.9 | 86.3 | 41.6 | 503.9 | 509.4 | 63.9 | 55.4 | 181.3 | 237.1 | 101.7 | 75.2 | 149.8 | 88.1 | 78.6 | 177.5 | 146.8 | 105.6 | 92.5 | 87.7 | 98.6 | 97.5 | 86.3 | 93.8 | 98.7
4234.1 | 4013.1 | -6.7 | 0 | 0 | 91.7 | 88.5 | 82.9 | 84.3 | 98.8 | 27 | 21.3 | 33.4 | 3.1 | 228.8 | 2.4 | 405.8 | 401.9 | 86.9 | 41.5 | 503.8 | 509.1 | 63.9 | 55.5 | 181.1 | 236.9 | 101.5 | 75 | 149.7 | 88.5 | 78.5 | 177.3 | 146.6 | 105.5 | 92.3 | 87.6 | 98.5 | 97.5 | 86.3 | 93.7 | 98.7
4235.1 | 4014.1 | -6.8 | 0 | 0 | 91.7 | 88.5 | 82.8 | 84.2 | 98.8 | 27 | 21.3 | 33.3 | 3 | 226.9 | 2.3 | 405.8 | 401.8 | 86.9 | 41.5 | 503.7 | 508.8 | 64.4 | 55.5 | 181 | 236.7 | 101.5 | 74.9 | 149.5 | 88.4 | 78.4 | 177.2 | 146.6 | 105.4 | 92.2 | 87.5 | 98.5 | 97.4 | 86.2 | 93.7 | 98.6
4236.1 | 4015.1 | -6.8 | 0 | 0 | 91.8 | 88.5 | 82.8 | 84.1 | 98.9 | 27 | 21.3 | 33.2 | 3.7 | 223.1 | 2.1 | 405.7 | 401.8 | 87.6 | 41.5 | 503.6 | 508.5 | 64.7 | 55.5 | 181 | 236.5 | 101.3 | 74.8 | 149.4 | 88.4 | 78.2 | 177 | 146.6 | 105.4 | 92.1 | 87.4 | 98.5 | 97.4 | 86.2 | 93.6 | 98.6
4237.2 | 4016.2 | -6.8 | 0 | 0 | 91.8 | 88.4 | 82.7 | 84.1 | 99 | 27 | 21.3 | 33.2 | 3.3 | 224.2 | 2.1 | 405.7 | 401.8 | 88.1 | 41.4 | 503.4 | 508.2 | 65.4 | 55.4 | 181 | 236.4 | 101 | 74.8 | 149.3 | 88.5 | 78.2 | 176.9 | 146.4 | 105.3 | 92 | 87.4 | 98.5 | 97.3 | 86.1 | 93.6 | 98.5
4238.2 | 4017.2 | -6.8 | 0 | 0 | 91.8 | 88.5 | 82.7 | 84.1 | 98.9 | 27.1 | 21.3 | 33.3 | 2.8 | 220.2 | 2 | 405.6 | 401.7 | 88.6 | 41.4 | 503.3 | 507.9 | 65.9 | 55.4 | 181 | 236.2 | 100.5 | 74.7 | 149.2 | 88.5 | 78 | 176.7 | 146.3 | 105.3 | 91.9 | 87.4 | 98.4 | 97.3 | 86.1 | 93.5 | 98.5
4239.2 | 4018.2 | -6.8 | 0 | 0 | 91.8 | 88.6 | 82.7 | 84.1 | 98.7 | 27.1 | 21.3 | 33.3 | 3.3 | 218 | 2.4 | 405.6 | 401.7 | 88.4 | 41.3 | 503.2 | 507.6 | 65.8 | 55.3 | 180.9 | 236 | 100.3 | 74.8 | 149.1 | 88.6 | 78 | 176.5 | 146.2 | 105.2 | 91.8 | 87.3 | 98.3 | 97.3 | 86.1 | 93.5 | 98.5
4240.2 | 4019.2 | -6.8 | 0 | 0 | 91.7 | 88.7 | 82.7 | 84.1 | 98.6 | 27.2 | 21.3 | 33.3 | 3.6 | 217.6 | 2.8 | 405.6 | 401.6 | 87.6 | 41.3 | 503.1 | 507.4 | 65.5 | 55.5 | 180.8 | 235.8 | 100.5 | 74.7 | 149 | 88.7 | 78 | 176.4 | 146.2 | 105.2 | 91.7 | 87.3 | 98.2 | 97.2 | 86 | 93.5 | 98.4
4241.2 | 4020.2 | -6.7 | 0 | 0 | 91.3 | 88.7 | 82.7 | 83.9 | 98.8 | 27.2 | 21.3 | 33.4 | 3.6 | 219.2 | 2.6 | 405.5 | 401.6 | 87.5 | 41.3 | 502.9 | 507.3 | 65.3 | 55.4 | 180.8 | 235.7 | 100 | 74.7 | 148.9 | 88.5 | 77.9 | 176.2 | 146.2 | 105.2 | 91.7 | 87.3 | 98.2 | 97.1 | 86 | 93.5 | 98.4
4242.2 | 4021.2 | -6.7 | 0 | 0 | 90.8 | 88.7 | 82.7 | 83.8 | 99 | 27.3 | 21.3 | 33.3 | 3.1 | 229.2 | 2.6 | 405.5 | 401.5 | 87.3 | 41.2 | 502.8 | 507.4 | 64.7 | 55.2 | 180.7 | 235.5 | 99.7 | 74.6 | 148.8 | 88.5 | 77.6 | 176.1 | 145.9 | 105.1 | 91.6 | 87.3 | 98.2 | 97.1 | 85.9 | 93.5 | 98.3
4243.2 | 4022.2 | -6.6 | 0 | 0 | 90.7 | 88.7 | 82.7 | 83.7 | 99.1 | 27.2 | 21.3 | 33.3 | 2.6 | 252.1 | 3 | 405.5 | 401.5 | 87.4 | 41.1 | 502.7 | 507.4 | 65.3 | 55 | 180.8 | 235.3 | 100 | 74.4 | 148.7 | 88.5 | 77.4 | 175.9 | 145.7 | 105.1 | 91.5 | 87.3 | 98.2 | 97 | 85.9 | 93.4 | 98.3
4244.2 | 4023.2 | -6.6 | 0 | 0 | 90.8 | 88.6 | 82.7 | 83.8 | 99.2 | 27.2 | 21.3 | 33.3 | 2.6 | 255.7 | 3.4 | 405.4 | 401.4 | 87.3 | 41 | 502.7 | 507.2 | 66.9 | 54.7 | 180.7 | 235.1 | 100.5 | 74.1 | 148.6 | 88.4 | 77.1 | 175.8 | 145.6 | 105.1 | 91.5 | 87.3 | 98.1 | 96.9 | 85.9 | 93.3 | 98.2
4245.2 | 4024.2 | -6.7 | 0 | 0 | 90.9 | 88.5 | 82.6 | 83.7 | 99.2 | 27.2 | 21.3 | 33.3 | 2.8 | 246.1 | 3.6 | 405.4 | 401.4 | 86.8 | 40.9 | 502.7 | 506.9 | 67.6 | 54.4 | 180.7 | 235 | 100.8 | 74.1 | 148.5 | 88.2 | 77 | 175.6 | 145.7 | 105.1 | 91.5 | 87.3 | 98.1 | 96.9 | 85.8 | 93.3 | 98.2
4246.2 | 4025.2 | -6.7 | 0 | 0 | 90.8 | 88.4 | 82.5 | 83.7 | 99.2 | 27.1 | 21.3 | 33.3 | 2.9 | 245.3 | 3.7 | 405.4 | 401.4 | 86.6 | 40.8 | 502.7 | 506.9 | 67.2 | 54.1 | 180.6 | 234.8 | 100.9 | 74.3 | 148.3 | 88 | 77 | 175.5 | 145.7 | 105.1 | 91.5 | 87.2 | 98 | 96.8 | 85.7 | 93.2 | 98.1
4247.2 | 4026.2 | -6.7 | 0 | 0 | 90.9 | 88.3 | 82.5 | 83.6 | 98.9 | 27.1 | 21.3 | 33.3 | 2.6 | 244.2 | 3.9 | 405.3 | 401.3 | 86.1 | 40.6 | 502.7 | 507 | 67.4 | 53.8 | 180.6 | 234.6 | 100.6 | 74.1 | 148.2 | 87.7 | 76.9 | 175.3 | 145.7 | 105 | 91.5 | 87.2 | 98 | 96.8 | 85.7 | 93.1 | 98.1
4248.2 | 4027.2 | -6.7 | 0 | 0 | 90.9 | 88.3 | 82.6 | 83.6 | 98.9 | 27.1 | 21.3 | 33.4 | 2.2 | 242.7 | 4 | 405.3 | 401.3 | 86.2 | 40.6 | 502.9 | 507 | 66.8 | 53.8 | 180.5 | 234.5 | 100.3 | 73.8 | 148.1 | 87.6 | 76.5 | 175.1 | 145.6 | 105 | 91.6 | 87.1 | 97.9 | 96.8 | 85.7 | 93 | 98.1
4249.2 | 4028.2 | -6.8 | 0 | 0 | 90.9 | 88.2 | 82.6 | 83.7 | 99.1 | 27 | 21.3 | 33.4 | 2.3 | 247.4 | 4.3 | 405.3 | 401.2 | 86.6 | 40.6 | 502.9 | 506.9 | 66.1 | 53.8 | 180.4 | 234.3 | 100 | 73.6 | 148.1 | 87.5 | 76.2 | 175 | 145.4 | 104.9 | 91.5 | 87 | 97.8 | 96.8 | 85.6 | 93 | 98
4250.2 | 4029.2 | -6.7 | 0 | 0 | 91 | 88.2 | 82.6 | 83.6 | 99.2 | 27 | 21.3 | 33.5 | 2.8 | 249.5 | 4.5 | 405.2 | 401.2 | 86.6 | 40.5 | 502.9 | 506.9 | 65.6 | 53.6 | 180.4 | 234.1 | 100 | 73.4 | 148 | 87.5 | 75.8 | 174.9 | 145.2 | 104.9 | 91.4 | 86.9 | 97.8 | 96.7 | 85.5 | 92.9 | 98
4251.2 | 4030.2 | -6.7 | 0 | 0 | 91 | 88.1 | 82.5 | 83.5 | 99.3 | 26.9 | 21.3 | 33.5 | 2.6 | 252.6 | 5.3 | 405.2 | 401.1 | 85.6 | 40.3 | 503 | 506.7 | 65.2 | 53.4 | 180.3 | 233.9 | 99.4 | 73.1 | 147.9 | 87.4 | 75.8 | 174.7 | 145.1 | 104.8 | 91.3 | 86.9 | 97.8 | 96.6 | 85.5 | 92.9 | 97.9
4252.2 | 4031.2 | -6.7 | 0 | 0 | 91.1 | 88 | 82.5 | 83.4 | 99.3 | 26.9 | 21.3 | 33.6 | 2.5 | 243.7 | 6 | 405.2 | 401.1 | 85 | 40.2 | 503 | 506.6 | 65 | 53.2 | 180.3 | 233.8 | 98.8 | 73 | 147.8 | 87.3 | 75.6 | 174.6 | 145.1 | 104.8 | 91.2 | 86.9 | 97.7 | 96.5 | 85.4 | 92.9 | 97.9
4253.2 | 4032.2 | -6.7 | 0 | 0 | 91.1 | 87.9 | 82.4 | 83.3 | 99.2 | 26.9 | 21.3 | 33.5 | 3 | 231.8 | 6 | 405.1 | 401 | 84.4 | 40.2 | 503.1 | 506.5 | 64.7 | 53.1 | 180.3 | 233.6 | 99 | 72.9 | 147.7 | 87.3 | 75.6 | 174.4 | 145.1 | 104.7 | 91.2 | 86.9 | 97.7 | 96.5 | 85.4 | 92.8 | 97.9
4254.2 | 4033.2 | -6.7 | 0 | 0 | 91 | 87.9 | 82.3 | 83.3 | 99.1 | 26.9 | 21.3 | 33.5 | 3 | 236.7 | 5.7 | 405.1 | 401 | 84.3 | 40.2 | 503.2 | 506.5 | 64.5 | 53.1 | 180.1 | 233.4 | 98.7 | 72.8 | 147.6 | 87.1 | 75.8 | 174.3 | 145.1 | 104.7 | 91.1 | 86.8 | 97.7 | 96.5 | 85.3 | 92.7 | 97.8
4255.2 | 4034.2 | -6.7 | 0 | 0 | 91 | 87.8 | 82.1 | 83.3 | 98.8 | 26.9 | 21.3 | 33.5 | 3.1 | 237.6 | 5.7 | 405 | 400.9 | 84.6 | 40.2 | 503.1 | 506.7 | 64.3 | 53.1 | 180 | 233.2 | 98.6 | 73 | 147.5 | 87.1 | 75.9 | 174.1 | 145 | 104.6 | 91.1 | 86.8 | 97.6 | 96.4 | 85.3 | 92.7 | 97.8
4256.2 | 4035.2 | -6.7 | 0 | 0 | 90.9 | 87.5 | 82 | 83.3 | 98.5 | 26.8 | 21.3 | 33.4 | 3.1 | 232.6 | 5.5 | 405 | 400.9 | 85 | 40.2 | 503.1 | 507.1 | 64.2 | 53.2 | 180.1 | 233 | 98.3 | 73.1 | 147.4 | 87 | 76.2 | 173.9 | 144.9 | 104.6 | 91.1 | 86.7 | 97.6 | 96.4 | 85.4 | 92.6 | 97.7
4257.2 | 4036.2 | -6.6 | 0 | 0 | 90.9 | 87.2 | 82 | 83.3 | 98.1 | 26.9 | 21.3 | 33.4 | 2.9 | 208.6 | 5.1 | 405 | 400.9 | 85.5 | 40.2 | 503 | 507.5 | 64.9 | 53.3 | 180 | 232.9 | 97.9 | 72.8 | 147.3 | 87 | 76.2 | 173.8 | 145 | 104.5 | 91 | 86.6 | 97.5 | 96.4 | 85.3 | 92.6 | 97.7
4258.2 | 4037.2 | -6.6 | 0 | 0 | 90.9 | 87.1 | 82 | 83.3 | 97.8 | 26.9 | 21.3 | 33.4 | 2.6 | 205.9 | 4.8 | 405 | 400.8 | 84.9 | 40.3 | 502.9 | 507.7 | 65.7 | 53.4 | 180 | 232.7 | 97.3 | 72.7 | 147.3 | 87 | 76.3 | 173.7 | 144.9 | 104.5 | 91 | 86.6 | 97.5 | 96.3 | 85.3 | 92.6 | 97.6
4259.2 | 4038.2 | -6.7 | 0 | 0 | 90.8 | 87.3 | 82 | 83.4 | 97.6 | 27 | 21.3 | 33.4 | 2.8 | 214.6 | 4.4 | 404.9 | 400.8 | 84.9 | 40.2 | 502.9 | 507.8 | 66.6 | 53.1 | 179.8 | 232.5 | 97.3 | 72.7 | 147.2 | 87 | 76.3 | 173.5 | 144.7 | 104.4 | 91 | 86.6 | 97.5 | 96.3 | 85.2 | 92.5 | 97.6
4260.2 | 4039.2 | -6.7 | 0 | 0 | 90.7 | 87.5 | 82.1 | 83.4 | 97.8 | 27.1 | 21.3 | 33.4 | 2.5 | 228.1 | 4.2 | 404.9 | 400.7 | 84.3 | 40.1 | 502.9 | 507.6 | 68 | 53 | 179.7 | 232.3 | 97.3 | 72.7 | 147.1 | 87.1 | 76.4 | 173.4 | 144.7 | 104.4 | 91 | 86.6 | 97.4 | 96.2 | 85.2 | 92.4 | 97.5
4261.2 | 4040.2 | -6.7 | 0 | 0 | 90.5 | 87.6 | 82.1 | 83.4 | 97.9 | 27.1 | 21.3 | 33.4 | 2.2 | 235.3 | 4.3 | 404.9 | 400.7 | 84.1 | 40.1 | 503 | 507.4 | 69 | 53.2 | 179.7 | 232.1 | 96.7 | 72.8 | 147 | 87.2 | 76.3 | 173.2 | 144.7 | 104.3 | 90.9 | 86.6 | 97.4 | 96.2 | 85.2 | 92.4 | 97.5
4262.2 | 4041.2 | -6.8 | 0 | 0 | 90.2 | 87.6 | 82.1 | 83.2 | 97.9 | 27.2 | 21.3 | 33.4 | 2.5 | 245.5 | 4.5 | 404.8 | 400.7 | 83.8 | 40 | 503 | 507.2 | 69.7 | 53.3 | 179.6 | 231.9 | 96.3 | 72.8 | 146.9 | 87.4 | 76.5 | 173 | 144.6 | 104.2 | 90.8 | 86.5 | 97.3 | 96.1 | 85.1 | 92.3 | 97.4
4263.2 | 4042.2 | -6.8 | 0 | 0 | 90 | 87.5 | 82.1 | 83 | 97.9 | 27.2 | 21.3 | 33.4 | 2.8 | 249.8 | 4.7 | 404.8 | 400.6 | 84.2 | 40.1 | 503 | 507.1 | 70 | 53.2 | 179.5 | 231.7 | 96 | 72.9 | 146.7 | 87.4 | 76.6 | 172.9 | 144.7 | 104.2 | 90.8 | 86.5 | 97.3 | 96 | 85.1 | 92.2 | 97.4
4264.2 | 4043.2 | -6.8 | 0 | 0 | 90.1 | 87.5 | 82.1 | 83 | 97.9 | 27.2 | 21.3 | 33.5 | 2.8 | 234.1 | 4.6 | 404.8 | 400.6 | 84.9 | 40 | 503 | 507 | 70.2 | 53.1 | 179.3 | 231.5 | 95.8 | 73.1 | 146.6 | 87.4 | 76.6 | 172.7 | 144.6 | 104.2 | 90.9 | 86.5 | 97.3 | 95.9 | 84.9 | 92.1 | 97.3
4265.2 | 4044.2 | -6.8 | 0 | 0 | 90.1 | 87.5 | 82.2 | 82.9 | 98 | 27.1 | 21.3 | 33.5 | 2.5 | 222.6 | 4.5 | 404.7 | 400.5 | 85.4 | 40 | 502.9 | 507.1 | 70.2 | 53 | 179.4 | 231.4 | 96.3 | 73.1 | 146.5 | 87.4 | 76.8 | 172.6 | 144.4 | 104.2 | 90.9 | 86.5 | 97.2 | 95.9 | 84.9 | 92.1 | 97.3
4266.2 | 4045.2 | -6.7 | 0 | 0 | 90.1 | 87.4 | 82.2 | 82.9 | 98.1 | 27.1 | 21.3 | 33.5 | 2.4 | 234.8 | 4.4 | 404.7 | 400.5 | 85.4 | 40 | 502.9 | 507 | 71.1 | 53 | 179.4 | 231.2 | 96.1 | 73.1 | 146.4 | 87.2 | 76.9 | 172.5 | 144.4 | 104.1 | 90.9 | 86.5 | 97.2 | 95.8 | 84.8 | 92 | 97.3
4267.2 | 4046.2 | -6.8 | 0 | 0 | 90.1 | 87.2 | 82.3 | 82.8 | 98.1 | 27.2 | 21.3 | 33.5 | 2.9 | 249.2 | 4.5 | 404.7 | 400.4 | 85.2 | 40 | 502.9 | 506.9 | 71.1 | 52.9 | 179.4 | 231 | 96.4 | 73.4 | 146.2 | 87.1 | 76.9 | 172.3 | 144.4 | 104.1 | 90.8 | 86.4 | 97.1 | 95.8 | 84.7 | 92 | 97.2
4268.2 | 4047.2 | -6.8 | 0 | 0 | 90 | 87.1 | 82.2 | 82.8 | 97.9 | 27.2 | 21.3 | 33.5 | 2.6 | 247.5 | 4.8 | 404.7 | 400.4 | 85.1 | 40 | 502.9 | 506.8 | 70.8 | 52.8 | 179.3 | 230.8 | 96.8 | 73.5 | 146.1 | 86.8 | 76.8 | 172.1 | 144.3 | 104 | 90.8 | 86.4 | 97.1 | 95.7 | 84.6 | 91.9 | 97.2
4269.2 | 4048.2 | -6.7 | 0 | 0 | 89.8 | 87 | 82.2 | 82.7 | 97.7 | 27.3 | 21.3 | 33.5 | 2.1 | 243.1 | 5.1 | 404.6 | 400.3 | 85.5 | 40 | 502.7 | 506.6 | 70.1 | 52.7 | 179.3 | 230.6 | 97.3 | 73.5 | 146 | 86.6 | 76.7 | 172 | 144 | 104 | 90.8 | 86.4 | 97.1 | 95.6 | 84.6 | 91.8 | 97.1
4270.2 | 4049.2 | -6.7 | 0 | 0 | 89.6 | 86.9 | 82.2 | 82.7 | 97.6 | 27.3 | 21.3 | 33.5 | 2.4 | 238.9 | 5.1 | 404.6 | 400.3 | 85.2 | 40 | 502.6 | 506.6 | 69.4 | 52.6 | 179.2 | 230.4 | 97.7 | 73.3 | 145.9 | 86.3 | 76.4 | 171.8 | 143.8 | 103.9 | 90.9 | 86.4 | 97.1 | 95.6 | 84.5 | 91.8 | 97.1
4271.2 | 4050.2 | -6.7 | 0 | 0 | 89.5 | 86.8 | 82.2 | 82.6 | 97.6 | 27.3 | 21.3 | 33.5 | 2.3 | 244 | 4.7 | 404.6 | 400.2 | 85.3 | 40 | 502.5 | 506.9 | 68.4 | 52.5 | 179.3 | 230.2 | 97.8 | 72.8 | 145.8 | 86.1 | 76.3 | 171.7 | 143.8 | 103.9 | 90.8 | 86.4 | 97 | 95.6 | 84.5 | 91.8 | 97.1
4272.2 | 4051.2 | -6.8 | 0 | 0 | 89.4 | 86.6 | 82.2 | 82.5 | 97.9 | 27.4 | 21.3 | 33.5 | 2.1 | 258 | 4.4 | 404.5 | 400.2 | 84 | 39.9 | 502.4 | 507.3 | 67.4 | 52.3 | 179.2 | 230 | 97.7 | 72.6 | 145.7 | 85.8 | 76.3 | 171.5 | 143.8 | 103.9 | 90.8 | 86.3 | 96.8 | 95.6 | 84.5 | 91.7 | 97
4273.2 | 4052.2 | -6.7 | 0 | 0 | 89.3 | 86.5 | 82.1 | 82.5 | 98.2 | 27.4 | 21.3 | 33.5 | 2.1 | 253.1 | 4.1 | 404.5 | 400.1 | 83.1 | 39.9 | 502.4 | 507.4 | 66.3 | 52.1 | 179.2 | 229.8 | 97.8 | 72.4 | 145.6 | 85.8 | 76.3 | 171.4 | 143.8 | 103.8 | 90.6 | 86.2 | 96.7 | 95.5 | 84.5 | 91.7 | 97
4274.2 | 4053.2 | -6.7 | 0 | 0 | 89.3 | 86.6 | 82.1 | 82.6 | 98.3 | 27.3 | 21.3 | 33.5 | 2.4 | 250.6 | 4.2 | 404.4 | 400.1 | 82.4 | 39.8 | 502.4 | 507.5 | 65.3 | 52 | 179.2 | 229.6 | 97.2 | 72.1 | 145.5 | 85.7 | 76.3 | 171.3 | 143.9 | 103.7 | 90.6 | 86 | 96.7 | 95.4 | 84.5 | 91.7 | 96.9
4275.2 | 4054.2 | -6.7 | 0 | 0 | 89.3 | 86.8 | 82 | 82.6 | 98.3 | 27.4 | 21.3 | 33.5 | 2.3 | 272.3 | 4.5 | 404.4 | 400 | 82.3 | 39.8 | 502.3 | 507.5 | 64.6 | 52 | 179.2 | 229.4 | 96.9 | 71.8 | 145.4 | 85.7 | 76.3 | 171.1 | 143.9 | 103.6 | 90.4 | 86 | 96.7 | 95.4 | 84.5 | 91.7 | 96.9
4276.2 | 4055.2 | -6.7 | 0 | 0 | 89.2 | 86.9 | 81.7 | 82.6 | 98.3 | 27.4 | 21.3 | 33.5 | 2.4 | 274.1 | 5 | 404.4 | 400 | 81.9 | 39.8 | 502.2 | 507.6 | 64.3 | 51.9 | 179.1 | 229.2 | 96.7 | 71.9 | 145.3 | 85.6 | 76.2 | 171 | 143.9 | 103.6 | 90.3 | 85.9 | 96.7 | 95.3 | 84.5 | 91.6 | 96.8
4277.2 | 4056.2 | -6.7 | 0 | 0 | 89.2 | 87.1 | 81.5 | 82.7 | 98.2 | 27.3 | 21.3 | 33.5 | 2.8 | 256.5 | 5.3 | 404.3 | 400 | 81.6 | 39.8 | 502.1 | 507.8 | 63.7 | 51.8 | 179.1 | 229 | 96.8 | 71.9 | 145.2 | 85.5 | 76.3 | 170.8 | 143.9 | 103.5 | 90.2 | 85.8 | 96.6 | 95.3 | 84.4 | 91.6 | 96.8
4278.2 | 4057.2 | -6.7 | 0 | 0 | 89.2 | 87.2 | 81.3 | 82.8 | 98.1 | 27.2 | 21.3 | 33.5 | 2.9 | 246.5 | 5.1 | 404.3 | 399.9 | 80.9 | 39.8 | 502 | 507.7 | 63.2 | 51.6 | 179.1 | 228.8 | 97 | 71.9 | 145.1 | 85.4 | 76.3 | 170.7 | 143.9 | 103.5 | 90.2 | 85.8 | 96.6 | 95.2 | 84.3 | 91.6 | 96.7
4279.2 | 4058.2 | -6.7 | 0 | 0 | 89.1 | 87.2 | 81.2 | 82.8 | 97.9 | 27.3 | 21.3 | 33.5 | 3 | 261.3 | 4.9 | 404.3 | 399.9 | 80.6 | 39.7 | 501.9 | 507.6 | 63.7 | 51.4 | 179 | 228.6 | 97.1 | 71.9 | 145 | 85.2 | 76.4 | 170.5 | 143.9 | 103.4 | 90.1 | 85.7 | 96.5 | 95.2 | 84.2 | 91.6 | 96.7
4280.2 | 4059.2 | -6.7 | 0 | 0 | 88.9 | 87.2 | 81.2 | 82.8 | 97.8 | 27.3 | 21.3 | 33.6 | 2.7 | 259.9 | 4.2 | 404.2 | 399.8 | 80.8 | 39.8 | 501.9 | 507.6 | 64.6 | 51.3 | 179 | 228.4 | 96.5 | 71.8 | 144.9 | 85.1 | 76.4 | 170.4 | 143.8 | 103.4 | 90.1 | 85.7 | 96.5 | 95.1 | 84.2 | 91.5 | 96.7
4281.2 | 4060.2 | -6.7 | 0 | 0 | 88.6 | 87.1 | 81.1 | 82.8 | 97.7 | 27.4 | 21.3 | 33.6 | 2.8 | 250.4 | 3.7 | 404.2 | 399.8 | 81.1 | 39.8 | 502 | 507.7 | 65.1 | 51.5 | 179 | 228.2 | 96 | 71.8 | 144.8 | 85.1 | 76.3 | 170.3 | 143.8 | 103.3 | 90 | 85.7 | 96.5 | 95.1 | 84.2 | 91.5 | 96.6
4282.2 | 4061.2 | -6.7 | 0 | 0 | 88.3 | 87 | 81 | 82.8 | 97.5 | 27.5 | 21.3 | 33.6 | 2.8 | 253.6 | 3.6 | 404.2 | 399.8 | 80.7 | 39.9 | 502.1 | 507.6 | 65.1 | 51.8 | 178.9 | 228 | 95.8 | 71.9 | 144.8 | 85.3 | 76.1 | 170.1 | 143.8 | 103.3 | 90 | 85.8 | 96.5 | 95.1 | 84.2 | 91.5 | 96.6
4283.2 | 4062.2 | -6.7 | 0 | 0 | 87.9 | 86.8 | 80.9 | 82.8 | 97.3 | 27.5 | 21.3 | 33.6 | 2.9 | 267.2 | 3.4 | 404.2 | 399.7 | 80.7 | 39.9 | 502.1 | 507.5 | 64.4 | 51.8 | 178.9 | 227.8 | 95.5 | 71.7 | 144.7 | 85.5 | 76 | 170 | 143.8 | 103.3 | 90 | 85.7 | 96.4 | 95 | 84.2 | 91.4 | 96.5
4284.2 | 4063.2 | -6.7 | 0 | 0 | 88.1 | 86.6 | 80.9 | 82.8 | 97.3 | 27.5 | 21.3 | 33.6 | 2.7 | 266.1 | 3.4 | 404.1 | 399.7 | 80.4 | 39.8 | 502.2 | 507.6 | 63.8 | 51.8 | 178.8 | 227.6 | 95.1 | 71.4 | 144.6 | 85.9 | 76.1 | 169.9 | 143.8 | 103.2 | 89.9 | 85.7 | 96.3 | 95 | 84.2 | 91.4 | 96.5
4285.2 | 4064.2 | -6.7 | 0 | 0 | 88.2 | 86.3 | 80.9 | 82.7 | 97.5 | 27.4 | 21.3 | 33.6 | 3.3 | 259.5 | 4 | 404.1 | 399.6 | 80.8 | 39.7 | 502.2 | 507.8 | 63.5 | 51.7 | 178.9 | 227.4 | 95.1 | 71.4 | 144.5 | 85.9 | 76.2 | 169.7 | 143.6 | 103.2 | 89.9 | 85.6 | 96.3 | 95 | 84.2 | 91.4 | 96.4
4286.2 | 4065.2 | -6.7 | 0 | 0 | 88.3 | 86.2 | 80.9 | 82.6 | 97.4 | 27.4 | 21.3 | 33.6 | 2.9 | 246.9 | 4.6 | 404.1 | 399.6 | 80.8 | 39.7 | 502.2 | 507.7 | 62.9 | 51.7 | 178.9 | 227.2 | 94.8 | 71.5 | 144.4 | 85.9 | 76.1 | 169.6 | 143.5 | 103.1 | 89.9 | 85.6 | 96.3 | 94.9 | 84.2 | 91.4 | 96.4
4287.2 | 4066.2 | -6.7 | 0 | 0 | 88.3 | 86.2 | 80.9 | 82.4 | 97 | 27.4 | 21.3 | 33.6 | 3.2 | 238.5 | 4.9 | 404 | 399.5 | 80.3 | 39.7 | 502.2 | 507.4 | 62.3 | 51.7 | 178.9 | 226.9 | 94.6 | 71.4 | 144.4 | 86.1 | 76.1 | 169.4 | 143.4 | 103.1 | 89.9 | 85.6 | 96.2 | 94.9 | 84.1 | 91.3 | 96.4
4288.2 | 4067.2 | -6.8 | 0 | 0 | 88.2 | 86.2 | 80.9 | 82.3 | 96.7 | 27.5 | 21.3 | 33.6 | 3.1 | 250.2 | 5.5 | 404 | 399.5 | 80.6 | 39.8 | 502.2 | 507.5 | 61.9 | 51.7 | 178.9 | 226.7 | 94.4 | 71.3 | 144.3 | 86.3 | 75.9 | 169.3 | 143.2 | 103 | 89.9 | 85.5 | 96.2 | 94.9 | 84 | 91.3 | 96.3
4289.2 | 4068.2 | -6.7 | 0 | 0 | 88.2 | 86.2 | 80.9 | 82.2 | 96.7 | 27.5 | 21.3 | 33.6 | 3.2 | 251.1 | 5.9 | 404 | 399.5 | 81.4 | 39.9 | 502.2 | 507.4 | 61.4 | 51.6 | 178.9 | 226.5 | 94.1 | 71.1 | 144.2 | 86.2 | 75.8 | 169.1 | 143.1 | 103 | 89.9 | 85.5 | 96.2 | 94.8 | 83.9 | 91.2 | 96.3
4290.2 | 4069.2 | -6.8 | 0 | 0 | 88.2 | 86.1 | 81 | 82.1 | 96.9 | 27.4 | 21.3 | 33.6 | 3.2 | 234.2 | 6.5 | 403.9 | 399.4 | 81.6 | 39.8 | 502.1 | 507.2 | 60.9 | 51.5 | 178.8 | 226.3 | 94 | 71.2 | 144.1 | 86.1 | 76 | 169 | 143.1 | 102.9 | 89.9 | 85.5 | 96.1 | 94.7 | 83.8 | 91.2 | 96.2
4291.2 | 4070.2 | -6.8 | 0 | 0 | 88.2 | 85.9 | 80.9 | 82.1 | 97 | 27.3 | 21.3 | 33.6 | 2.9 | 245.3 | 6.5 | 403.9 | 399.4 | 82.5 | 39.8 | 502 | 506.9 | 60.5 | 51.5 | 178.7 | 226.1 | 94.1 | 71.3 | 144.1 | 86 | 76 | 168.8 | 143.2 | 102.9 | 89.9 | 85.5 | 96.1 | 94.6 | 83.7 | 91.1 | 96.2
4292.2 | 4071.2 | -6.7 | 0 | 0 | 88.3 | 85.6 | 80.8 | 82 | 97 | 27.3 | 21.3 | 33.6 | 2.9 | 250.3 | 6.2 | 403.9 | 399.3 | 83.1 | 39.7 | 501.9 | 506.7 | 60.7 | 51.3 | 178.5 | 225.9 | 93.9 | 71.3 | 144 | 86 | 75.9 | 168.7 | 143.3 | 102.9 | 89.8 | 85.5 | 96 | 94.6 | 83.7 | 91 | 96.1
4293.2 | 4072.2 | -6.8 | 0 | 0 | 88.3 | 85.6 | 80.7 | 81.8 | 96.9 | 27.2 | 21.3 | 33.5 | 2.8 | 255.2 | 6.1 | 403.8 | 399.3 | 83.1 | 39.7 | 501.8 | 506.5 | 60.7 | 51.1 | 178.6 | 225.7 | 93.7 | 71.3 | 143.9 | 85.9 | 75.7 | 168.6 | 143.2 | 102.8 | 89.7 | 85.5 | 96 | 94.5 | 83.7 | 91 | 96.1
4294.2 | 4073.2 | -6.7 | 0 | 0 | 88.3 | 85.7 | 80.7 | 81.6 | 96.7 | 27.1 | 21.3 | 33.5 | 2.8 | 246.7 | 6.3 | 403.8 | 399.3 | 82.8 | 39.8 | 501.7 | 506.3 | 60.9 | 51.2 | 178.4 | 225.5 | 93.5 | 71.5 | 143.8 | 85.7 | 75.6 | 168.4 | 143 | 102.8 | 89.7 | 85.5 | 96 | 94.5 | 83.6 | 90.9 | 96.1
4295.2 | 4074.2 | -6.7 | 0 | 0 | 88.2 | 85.8 | 80.7 | 81.4 | 96.6 | 27.1 | 21.3 | 33.5 | 2.6 | 240.4 | 6.5 | 403.8 | 399.2 | 83.2 | 39.9 | 501.5 | 506.1 | 61.5 | 51.3 | 178.4 | 225.3 | 93.4 | 71.5 | 143.7 | 85.7 | 75.6 | 168.3 | 142.8 | 102.8 | 89.7 | 85.5 | 96 | 94.5 | 83.6 | 90.9 | 96
4296.2 | 4075.2 | -6.7 | 0 | 0 | 87.9 | 85.8 | 80.8 | 81.2 | 96.6 | 27 | 21.3 | 33.5 | 2.9 | 245.2 | 6.6 | 403.8 | 399.2 | 84.2 | 40 | 501.4 | 505.9 | 61.3 | 51.4 | 178.3 | 225.1 | 93.4 | 71.6 | 143.6 | 85.7 | 76 | 168.1 | 142.6 | 102.7 | 89.7 | 85.6 | 95.9 | 94.4 | 83.5 | 90.8 | 96
4297.2 | 4076.2 | -6.7 | 0 | 0 | 87.8 | 85.8 | 80.8 | 81.1 | 96.7 | 27 | 21.3 | 33.5 | 2.6 | 241.4 | 6.4 | 403.7 | 399.1 | 85.3 | 40.1 | 501.3 | 505.8 | 61.3 | 51.3 | 178.3 | 224.9 | 93.3 | 71.6 | 143.5 | 85.8 | 75.9 | 168 | 142.5 | 102.7 | 89.7 | 85.5 | 95.9 | 94.4 | 83.4 | 90.8 | 95.9
4298.2 | 4077.2 | -6.7 | 0 | 0 | 87.8 | 85.8 | 80.9 | 81 | 96.7 | 27 | 21.3 | 33.5 | 2.8 | 240.8 | 6 | 403.7 | 399.1 | 85.3 | 40 | 501.2 | 505.7 | 61 | 51.2 | 178.3 | 224.7 | 93.1 | 71.5 | 143.4 | 85.9 | 76 | 167.8 | 142.5 | 102.7 | 89.7 | 85.4 | 95.8 | 94.3 | 83.3 | 90.8 | 95.9
4299.2 | 4078.2 | -6.8 | 0 | 0 | 87.9 | 85.6 | 80.9 | 81 | 96.6 | 27 | 21.3 | 33.5 | 3.1 | 235.8 | 5.9 | 403.7 | 399.1 | 85.9 | 40 | 501.2 | 505.5 | 60.4 | 51.2 | 178.3 | 224.5 | 92.9 | 71.5 | 143.3 | 85.9 | 76 | 167.7 | 142.4 | 102.6 | 89.6 | 85.3 | 95.7 | 94.3 | 83.3 | 90.8 | 95.9
4300.2 | 4079.2 | -6.7 | 0 | 0 | 88 | 85.4 | 80.8 | 81 | 96.4 | 27.1 | 21.3 | 33.5 | 3.5 | 239.4 | 5.7 | 403.6 | 399.1 | 86 | 40 | 501.1 | 505.3 | 60 | 51.2 | 178.3 | 224.3 | 92.8 | 71.5 | 143.3 | 85.9 | 75.9 | 167.6 | 142.3 | 102.6 | 89.5 | 85.3 | 95.7 | 94.2 | 83.3 | 90.8 | 95.8
4301.2 | 4080.2 | -6.7 | 0 | 0 | 88.1 | 85.2 | 80.6 | 81 | 96.4 | 27.1 | 21.3 | 33.5 | 2.9 | 240.1 | 5.5 | 403.6 | 399 | 86.2 | 39.9 | 501.1 | 505 | 59.8 | 51.2 | 178.2 | 224.1 | 92.7 | 71.6 | 143.2 | 85.8 | 75.7 | 167.4 | 142.1 | 102.5 | 89.5 | 85.2 | 95.6 | 94.2 | 83.3 | 90.7 | 95.8
4302.2 | 4081.2 | -6.8 | 0 | 0 | 88.2 | 85.1 | 80.5 | 81 | 96.5 | 27.1 | 21.3 | 33.5 | 3.1 | 243.3 | 5.4 | 403.5 | 399 | 86.9 | 39.8 | 501 | 504.6 | 59.6 | 51.3 | 178.3 | 223.8 | 92.5 | 71.7 | 143.1 | 85.9 | 75.6 | 167.3 | 141.9 | 102.4 | 89.4 | 85.2 | 95.6 | 94.1 | 83.2 | 90.7 | 95.7
4303.2 | 4082.2 | -6.8 | 0 | 0 | 88.1 | 85.2 | 80.5 | 81.1 | 96.6 | 27.1 | 21.3 | 33.5 | 2.7 | 244.7 | 4.9 | 403.5 | 398.9 | 87.3 | 39.9 | 500.9 | 504.4 | 59.7 | 51.6 | 178.3 | 223.6 | 92.3 | 71.8 | 143 | 85.8 | 75.7 | 167.2 | 141.8 | 102.4 | 89.4 | 85.2 | 95.6 | 94.1 | 83.2 | 90.6 | 95.7
4304.2 | 4083.2 | -6.7 | 0 | 0 | 87.9 | 85.2 | 80.5 | 81.3 | 96.6 | 27.1 | 21.3 | 33.5 | 2.6 | 249.8 | 4.5 | 403.4 | 398.9 | 87.7 | 40.1 | 500.8 | 504.5 | 59.7 | 51.8 | 178.3 | 223.4 | 92.3 | 71.9 | 142.9 | 85.7 | 75.6 | 167 | 141.8 | 102.3 | 89.3 | 85.2 | 95.6 | 94 | 83.1 | 90.5 | 95.6
4305.2 | 4084.2 | -6.7 | 0 | 0 | 87.8 | 85.2 | 80.5 | 81.4 | 96.6 | 27 | 21.3 | 33.5 | 2.9 | 246.2 | 4.3 | 403.4 | 398.8 | 88.3 | 40.3 | 500.7 | 504.6 | 59.4 | 52 | 178.3 | 223.2 | 92.3 | 72 | 142.8 | 85.5 | 75.7 | 166.9 | 141.9 | 102.3 | 89.4 | 85.2 | 95.5 | 94 | 83.1 | 90.5 | 95.6
4306.2 | 4085.2 | -6.7 | 0 | 0 | 87.8 | 85.2 | 80.4 | 81.4 | 96.7 | 27.1 | 21.3 | 33.5 | 2.3 | 243 | 4.5 | 403.4 | 398.8 | 88.9 | 40.4 | 500.6 | 505.1 | 59 | 51.9 | 178.3 | 223 | 92.8 | 71.8 | 142.7 | 85.3 | 75.7 | 166.7 | 141.7 | 102.3 | 89.3 | 85.2 | 95.4 | 93.9 | 83.1 | 90.5 | 95.6
4307.2 | 4086.2 | -6.7 | 0 | 0 | 87.7 | 85.1 | 80.4 | 81.4 | 96.9 | 27.1 | 21.3 | 33.5 | 1.9 | 242.7 | 4.9 | 403.3 | 398.8 | 89.3 | 40.4 | 500.5 | 505.4 | 58.5 | 51.8 | 178.3 | 222.8 | 92.5 | 71.7 | 142.6 | 85.2 | 75.7 | 166.6 | 141.6 | 102.2 | 89.3 | 85.1 | 95.4 | 93.9 | 83.1 | 90.4 | 95.5
4308.2 | 4087.2 | -6.7 | 0 | 0 | 87.6 | 85.2 | 80.4 | 81.3 | 97 | 27.1 | 21.3 | 33.5 | 2 | 243.5 | 4.8 | 403.3 | 398.7 | 89.1 | 40.3 | 500.4 | 505.5 | 58.9 | 51.7 | 178.4 | 222.5 | 92.3 | 71.3 | 142.5 | 85.4 | 75.7 | 166.5 | 141.5 | 102.2 | 89.3 | 85 | 95.3 | 93.9 | 83.1 | 90.4 | 95.4
4309.2 | 4088.2 | -6.7 | 0 | 0 | 87.6 | 85.2 | 80.5 | 81.3 | 97 | 27.1 | 21.3 | 33.5 | 1.8 | 249.2 | 4.5 | 403.3 | 398.7 | 88.5 | 40.3 | 500.2 | 505.7 | 60.2 | 51.7 | 178.5 | 222.3 | 92.3 | 71 | 142.4 | 85.5 | 75.6 | 166.3 | 141.4 | 102.1 | 89.3 | 84.9 | 95.3 | 93.9 | 83.1 | 90.3 | 95.4
4310.2 | 4089.2 | -6.7 | 0 | 0 | 87.6 | 85.3 | 80.5 | 81.3 | 97 | 27 | 21.3 | 33.5 | 1.9 | 253.3 | 4 | 403.2 | 398.7 | 87.9 | 40.3 | 500.1 | 506.2 | 61.2 | 52 | 178.4 | 222.1 | 92.2 | 70.7 | 142.3 | 85.8 | 75.3 | 166.2 | 141.3 | 102 | 89.3 | 84.8 | 95.2 | 93.8 | 83.1 | 90.3 | 95.4
4311.2 | 4090.2 | -6.7 | 0 | 0 | 87.5 | 85.3 | 80.5 | 81.2 | 97.1 | 27 | 21.3 | 33.5 | 2 | 237.5 | 3.5 | 403.2 | 398.6 | 87.7 | 40.3 | 499.9 | 506.5 | 62 | 52.3 | 178.4 | 221.9 | 92.1 | 70.4 | 142.2 | 85.9 | 75.1 | 166.1 | 141.3 | 102 | 89.3 | 84.8 | 95.2 | 93.7 | 83 | 90.2 | 95.3
4312.2 | 4091.2 | -6.7 | 0 | 0 | 87.4 | 85.3 | 80.3 | 81.1 | 97.1 | 26.9 | 21.3 | 33.5 | 2.2 | 204.6 | 3.3 | 403.1 | 398.6 | 87.9 | 40.4 | 499.9 | 506.4 | 62.2 | 52.4 | 178.5 | 221.7 | 92 | 70.2 | 142.1 | 85.8 | 75.1 | 165.9 | 141.1 | 101.9 | 89.3 | 84.8 | 95.1 | 93.7 | 82.9 | 90.1 | 95.3
4313.2 | 4092.2 | -6.8 | 0 | 0 | 87.4 | 85.2 | 80.1 | 81 | 97 | 26.9 | 21.4 | 33.5 | 2.5 | 206 | 3.2 | 403.1 | 398.5 | 88.1 | 40.4 | 499.8 | 506.2 | 62.9 | 52.3 | 178.5 | 221.5 | 91.8 | 70.2 | 141.9 | 85.6 | 75.1 | 165.8 | 141.1 | 101.9 | 89.2 | 84.7 | 95.1 | 93.7 | 82.8 | 90.1 | 95.2
4314.2 | 4093.2 | -6.8 | 0 | 0 | 87.5 | 85.2 | 80 | 80.9 | 97 | 26.9 | 21.3 | 33.6 | 2.9 | 236.7 | 3.1 | 403 | 398.5 | 87.2 | 40.3 | 499.6 | 506 | 62.7 | 52.2 | 178.4 | 221.3 | 91.6 | 70.3 | 141.8 | 85.5 | 75 | 165.6 | 141.1 | 101.8 | 89.2 | 84.7 | 95.1 | 93.6 | 82.8 | 90.1 | 95.2
4315.2 | 4094.2 | -6.8 | 0 | 0 | 87.6 | 85.3 | 80 | 80.9 | 96.9 | 26.9 | 21.3 | 33.6 | 3 | 260 | 3.2 | 403 | 398.5 | 86.8 | 40.3 | 499.5 | 505.9 | 62.2 | 52.1 | 178.4 | 221.1 | 91.5 | 70.3 | 141.7 | 85.3 | 75 | 165.5 | 140.9 | 101.8 | 89.2 | 84.7 | 95.1 | 93.6 | 82.7 | 90 | 95.2
4316.2 | 4095.2 | -6.8 | 0 | 0 | 87.6 | 85.2 | 80 | 81 | 96.8 | 26.9 | 21.3 | 33.6 | 2.6 | 240.9 | 3.6 | 403 | 398.4 | 86.7 | 40.2 | 499.5 | 505.7 | 62.3 | 52 | 178.3 | 220.9 | 91.3 | 70.2 | 141.6 | 85.2 | 74.9 | 165.4 | 140.8 | 101.7 | 89.2 | 84.7 | 95 | 93.6 | 82.7 | 89.9 | 95.1
4317.2 | 4096.2 | -6.8 | 0 | 0 | 87.5 | 85.1 | 80.1 | 81 | 96.7 | 26.9 | 21.3 | 33.5 | 2.4 | 219.4 | 3.9 | 402.9 | 398.4 | 87.4 | 40.2 | 499.5 | 505.5 | 62 | 52.1 | 178.3 | 220.7 | 90.9 | 70.2 | 141.5 | 85.3 | 74.9 | 165.2 | 140.7 | 101.7 | 89.1 | 84.7 | 95 | 93.5 | 82.8 | 89.9 | 95.1
4318.2 | 4097.2 | -6.8 | 0 | 0 | 87.4 | 84.9 | 80.1 | 81 | 96.5 | 26.8 | 21.3 | 33.5 | 2.6 | 234.6 | 4 | 402.9 | 398.3 | 87.4 | 40.3 | 499.4 | 505.1 | 61.6 | 52.2 | 178.3 | 220.5 | 90.6 | 70.3 | 141.4 | 85.3 | 74.9 | 165.1 | 140.6 | 101.6 | 89.1 | 84.6 | 95 | 93.5 | 82.8 | 89.8 | 95
4319.2 | 4098.2 | -6.8 | 0 | 0 | 87.4 | 84.8 | 80.2 | 80.9 | 96.2 | 26.7 | 21.3 | 33.5 | 2.4 | 249.3 | 4 | 402.8 | 398.3 | 87.9 | 40.4 | 499.3 | 504.7 | 61.4 | 52.3 | 178.2 | 220.3 | 90.8 | 70.2 | 141.3 | 85.1 | 74.9 | 165 | 140.7 | 101.6 | 89 | 84.5 | 94.9 | 93.5 | 82.9 | 89.8 | 95
4320.2 | 4099.2 | -6.7 | 0 | 0 | 87.4 | 84.7 | 80.1 | 80.9 | 96 | 26.6 | 21.3 | 33.5 | 2.4 | 264.8 | 3.8 | 402.8 | 398.2 | 88.3 | 40.6 | 499.2 | 504.4 | 61 | 52.6 | 178.2 | 220.1 | 90.9 | 70.3 | 141.2 | 84.9 | 74.9 | 164.8 | 140.6 | 101.5 | 88.9 | 84.4 | 94.9 | 93.4 | 82.9 | 89.8 | 95
4321.2 | 4100.2 | -6.7 | 0 | 0 | 87.3 | 84.6 | 80 | 80.9 | 96.1 | 26.6 | 21.3 | 33.5 | 2.7 | 273.5 | 3.9 | 402.7 | 398.2 | 88.5 | 40.9 | 499.1 | 504.3 | 60.8 | 52.7 | 178.2 | 219.9 | 91 | 70.2 | 141.1 | 84.6 | 74.9 | 164.7 | 140.4 | 101.5 | 88.8 | 84.3 | 94.8 | 93.4 | 82.8 | 89.8 | 94.9
4322.2 | 4101.2 | -6.7 | 0 | 0 | 87.2 | 84.5 | 79.9 | 80.8 | 96.2 | 26.5 | 21.3 | 33.5 | 2.7 | 265.3 | 4.6 | 402.7 | 398.1 | 88.9 | 41.1 | 499.1 | 504.3 | 60.4 | 52.8 | 178.2 | 219.7 | 91.4 | 70.2 | 141 | 84.2 | 75 | 164.6 | 140.3 | 101.4 | 88.7 | 84.3 | 94.8 | 93.4 | 82.7 | 89.8 | 94.9
4323.2 | 4102.2 | -6.7 | 0 | 0 | 87.2 | 84.5 | 79.7 | 80.7 | 96.2 | 26.5 | 21.3 | 33.4 | 2.7 | 265 | 4.8 | 402.6 | 398.1 | 89 | 41.2 | 499 | 504.4 | 60.3 | 53 | 178.1 | 219.5 | 91.6 | 70.1 | 140.9 | 84.1 | 75 | 164.4 | 140.2 | 101.4 | 88.6 | 84.3 | 94.7 | 93.4 | 82.8 | 89.7 | 94.9
4324.2 | 4103.2 | -6.7 | 0 | 0 | 87.2 | 84.6 | 79.7 | 80.6 | 96.2 | 26.6 | 21.3 | 33.4 | 2.8 | 257 | 5 | 402.6 | 398.1 | 88.6 | 41.3 | 498.9 | 504.6 | 60 | 53.3 | 178.2 | 219.2 | 91.4 | 70.2 | 140.8 | 84 | 74.9 | 164.3 | 140 | 101.3 | 88.5 | 84.2 | 94.7 | 93.3 | 82.8 | 89.7 | 94.8
4325.2 | 4104.2 | -6.7 | 0 | 0 | 87.2 | 84.6 | 79.7 | 80.5 | 96.2 | 26.7 | 21.3 | 33.4 | 2.9 | 260.6 | 5.5 | 402.6 | 398 | 88.1 | 41.3 | 498.7 | 504.7 | 59.8 | 53.5 | 178.2 | 219 | 91.3 | 70.2 | 140.7 | 84 | 74.6 | 164.2 | 139.8 | 101.3 | 88.5 | 84.3 | 94.7 | 93.3 | 82.8 | 89.7 | 94.8
4326.2 | 4105.2 | -6.7 | 0 | 0 | 87.2 | 84.7 | 79.7 | 80.5 | 96.2 | 26.8 | 21.3 | 33.4 | 2.6 | 258 | 5.6 | 402.5 | 398 | 87.4 | 41.2 | 498.6 | 504.8 | 59.2 | 53.5 | 178.1 | 218.8 | 91.2 | 70.2 | 140.6 | 84.2 | 74.6 | 164 | 139.7 | 101.2 | 88.5 | 84.3 | 94.7 | 93.2 | 82.7 | 89.7 | 94.7
4327.2 | 4106.2 | -6.8 | 0 | 0 | 87.1 | 84.7 | 79.8 | 80.4 | 96.2 | 26.8 | 21.3 | 33.3 | 2.3 | 245.3 | 5.8 | 402.5 | 397.9 | 87.3 | 41.1 | 498.5 | 504.9 | 58.8 | 53.3 | 178.1 | 218.6 | 91 | 70.3 | 140.5 | 84.3 | 74.6 | 163.9 | 139.7 | 101.2 | 88.5 | 84.3 | 94.6 | 93.2 | 82.6 | 89.6 | 94.7
4328.2 | 4107.2 | -6.7 | 0 | 0 | 87.1 | 84.6 | 79.8 | 80.4 | 96.2 | 26.8 | 21.3 | 33.3 | 2.7 | 252.3 | 5.9 | 402.4 | 397.9 | 86.5 | 41 | 498.4 | 504.8 | 58.3 | 53.1 | 178 | 218.4 | 90.5 | 70.5 | 140.4 | 84.3 | 74.4 | 163.7 | 139.7 | 101.2 | 88.4 | 84.3 | 94.6 | 93.2 | 82.5 | 89.6 | 94.6
4329.2 | 4108.2 | -6.7 | 0 | 0 | 87 | 84.4 | 79.6 | 80.4 | 96 | 26.8 | 21.3 | 33.3 | 2.8 | 258.2 | 5.8 | 402.4 | 397.8 | 85.8 | 40.9 | 498.4 | 504.5 | 57.9 | 53 | 178 | 218.1 | 90.2 | 70.4 | 140.3 | 84.4 | 74.4 | 163.6 | 139.7 | 101.1 | 88.4 | 84.2 | 94.5 | 93.1 | 82.5 | 89.5 | 94.6
4330.2 | 4109.2 | -6.7 | 0 | 0 | 86.9 | 84.2 | 79.3 | 80.3 | 95.8 | 26.8 | 21.3 | 33.3 | 2.7 | 258 | 5.9 | 402.4 | 397.8 | 85.8 | 40.9 | 498.3 | 504.2 | 57.9 | 52.8 | 177.9 | 217.9 | 90 | 70.2 | 140.2 | 84.5 | 74.3 | 163.5 | 139.6 | 101.1 | 88.4 | 84.2 | 94.5 | 93.1 | 82.4 | 89.4 | 94.5
4331.2 | 4110.2 | -6.7 | 0 | 0 | 86.9 | 84.2 | 79.1 | 80.3 | 95.7 | 26.8 | 21.3 | 33.3 | 2.5 | 257.9 | 5.9 | 402.3 | 397.7 | 86.4 | 40.8 | 498.2 | 504.1 | 58.1 | 52.6 | 177.7 | 217.7 | 89.8 | 70.1 | 140.1 | 84.4 | 74.4 | 163.3 | 139.4 | 101 | 88.4 | 84.2 | 94.4 | 93.1 | 82.3 | 89.4 | 94.5
4332.2 | 4111.2 | -6.7 | 0 | 0 | 86.9 | 84.2 | 79.1 | 80.2 | 95.6 | 26.9 | 21.3 | 33.3 | 2.4 | 259.4 | 6.1 | 402.3 | 397.7 | 86.6 | 40.7 | 498.1 | 504.1 | 59.2 | 52.9 | 177.7 | 217.5 | 89.8 | 70.4 | 140 | 84.4 | 74.4 | 163.2 | 139.3 | 101 | 88.3 | 84.1 | 94.4 | 93.1 | 82.3 | 89.4 | 94.5
4333.2 | 4112.2 | -6.7 | 0 | 0 | 87.1 | 84.3 | 79.2 | 80.2 | 95.5 | 27 | 21.3 | 33.3 | 2.5 | 248.6 | 6.4 | 402.2 | 397.7 | 86.6 | 40.9 | 498 | 504.2 | 59.8 | 53.1 | 177.9 | 217.3 | 89.7 | 70.5 | 139.9 | 84.2 | 74.4 | 163.1 | 139.2 | 100.9 | 88.3 | 84.1 | 94.4 | 93 | 82.2 | 89.3 | 94.4
4334.2 | 4113.2 | -6.8 | 0 | 0 | 87.2 | 84.4 | 79.2 | 80.1 | 95.6 | 27 | 21.3 | 33.3 | 2.2 | 246.6 | 6.8 | 402.2 | 397.6 | 87.5 | 41 | 497.9 | 504 | 60.2 | 53.2 | 177.9 | 217 | 90 | 70.5 | 139.8 | 84.1 | 74.5 | 163 | 139.2 | 100.8 | 88.3 | 84.1 | 94.3 | 93 | 82.1 | 89.3 | 94.4
4335.2 | 4114.2 | -6.8 | 0 | 0 | 87.2 | 84.4 | 79.3 | 80.1 | 95.8 | 27 | 21.3 | 33.4 | 2.4 | 253.5 | 6.6 | 402.2 | 397.6 | 88.1 | 41.1 | 497.8 | 503.8 | 60.3 | 53.2 | 178 | 216.8 | 90.4 | 70.3 | 139.7 | 83.6 | 74.6 | 162.8 | 139.1 | 100.8 | 88.2 | 84 | 94.2 | 92.9 | 82 | 89.2 | 94.3
4336.2 | 4115.2 | -6.8 | 0 | 0 | 87 | 84.4 | 79.3 | 80.1 | 95.8 | 27 | 21.3 | 33.3 | 2.5 | 266.5 | 6.5 | 402.2 | 397.6 | 88.5 | 41.1 | 497.7 | 503.6 | 59.9 | 53.3 | 177.8 | 216.6 | 90.5 | 70.2 | 139.6 | 83.4 | 74.4 | 162.7 | 139 | 100.7 | 88.2 | 83.9 | 94.2 | 92.9 | 82 | 89.2 | 94.3
4337.2 | 4116.2 | -6.8 | 0 | 0 | 86.7 | 84.3 | 79.4 | 80.1 | 95.8 | 27.1 | 21.3 | 33.3 | 2 | 259.7 | 6.4 | 402.1 | 397.5 | 88.8 | 41.1 | 497.6 | 503.4 | 59.6 | 53.6 | 177.7 | 216.4 | 90.5 | 70.2 | 139.5 | 83.4 | 74.5 | 162.6 | 138.9 | 100.7 | 88.2 | 83.8 | 94.1 | 92.9 | 82 | 89.2 | 94.3
4338.2 | 4117.2 | -6.7 | 0 | 0 | 86.6 | 84.3 | 79.4 | 80 | 95.7 | 27.1 | 21.3 | 33.3 | 2 | 250.2 | 5.6 | 402.1 | 397.5 | 88.3 | 41.1 | 497.5 | 503.2 | 59.3 | 53.5 | 177.5 | 216.2 | 90.3 | 70.3 | 139.3 | 83.4 | 74.6 | 162.4 | 138.7 | 100.6 | 88.2 | 83.7 | 94.1 | 92.8 | 82 | 89.2 | 94.2
4339.2 | 4118.2 | -6.7 | 0 | 0 | 86.6 | 84.2 | 79.4 | 79.9 | 95.5 | 27 | 21.3 | 33.3 | 2.1 | 249.5 | 4.7 | 402.1 | 397.4 | 87.6 | 41.1 | 497.4 | 503 | 59.3 | 53.5 | 177.3 | 216 | 90.1 | 70.4 | 139.2 | 83.4 | 74.5 | 162.3 | 138.7 | 100.6 | 88.2 | 83.7 | 94.1 | 92.8 | 81.9 | 89.2 | 94.2
4340.2 | 4119.2 | -6.7 | 0 | 0 | 86.5 | 84.1 | 79.3 | 79.9 | 95.4 | 27 | 21.3 | 33.3 | 2.3 | 248.1 | 4 | 402 | 397.4 | 86.6 | 41.2 | 497.3 | 503 | 59.8 | 53.4 | 177.4 | 215.8 | 89.8 | 70.5 | 139.1 | 83.4 | 74.7 | 162.1 | 138.6 | 100.5 | 88.1 | 83.7 | 94 | 92.7 | 81.9 | 89.2 | 94.1
4341.2 | 4120.2 | -6.8 | 0 | 0 | 86.4 | 84.1 | 79.3 | 79.8 | 95.2 | 27 | 21.3 | 33.3 | 2.5 | 246.5 | 3.9 | 402 | 397.3 | 85.5 | 41.2 | 497.2 | 503.1 | 60.9 | 53.5 | 177.3 | 215.6 | 89.6 | 70.5 | 139 | 83.3 | 74.6 | 162 | 138.5 | 100.5 | 88.1 | 83.7 | 94 | 92.7 | 81.8 | 89.2 | 94.1
4342.2 | 4121.2 | -6.8 | 0 | 0 | 86.3 | 84.2 | 79.3 | 79.7 | 95.1 | 26.9 | 21.3 | 33.3 | 2.4 | 243.2 | 4.1 | 402 | 397.3 | 85 | 41.2 | 497 | 503.3 | 61.2 | 53.6 | 177.3 | 215.4 | 89.4 | 70.4 | 138.9 | 83.2 | 74.7 | 161.9 | 138.4 | 100.4 | 88.1 | 83.6 | 93.9 | 92.6 | 81.8 | 89.2 | 94.1
4343.2 | 4122.2 | -6.7 | 0 | 0 | 86.2 | 84.3 | 79.3 | 79.6 | 95 | 26.8 | 21.3 | 33.3 | 2.1 | 237.9 | 4.4 | 401.9 | 397.2 | 84.8 | 41.2 | 496.8 | 503.3 | 61.3 | 53.6 | 177.2 | 215.2 | 89.5 | 70.5 | 138.8 | 83.1 | 74.8 | 161.7 | 138.3 | 100.4 | 88.1 | 83.5 | 93.9 | 92.6 | 81.7 | 89.1 | 94
4344.2 | 4123.2 | -6.8 | 0 | 0 | 86.2 | 84.3 | 79.3 | 79.5 | 94.9 | 26.9 | 21.3 | 33.3 | 1.9 | 236.6 | 4.6 | 401.9 | 397.2 | 84.9 | 41.2 | 496.6 | 503.2 | 61.5 | 53.8 | 177.3 | 215 | 89.6 | 70.5 | 138.7 | 83 | 74.7 | 161.6 | 138.2 | 100.4 | 88 | 83.5 | 93.9 | 92.5 | 81.7 | 89.1 | 94
4345.2 | 4124.2 | -6.7 | 0 | 0 | 86.2 | 84.3 | 79.3 | 79.4 | 94.9 | 26.9 | 21.3 | 33.3 | 1.9 | 244.4 | 4.9 | 401.9 | 397.1 | 85 | 41 | 496.5 | 503.1 | 61.8 | 53.7 | 177.3 | 214.8 | 89.6 | 70.4 | 138.5 | 83 | 74.5 | 161.5 | 138 | 100.4 | 88 | 83.6 | 93.9 | 92.5 | 81.6 | 89 | 93.9
4346.2 | 4125.2 | -6.8 | 0 | 0 | 86.2 | 84.3 | 79.3 | 79.4 | 95 | 27 | 21.3 | 33.3 | 2 | 262.3 | 5 | 401.8 | 397.1 | 85.2 | 40.9 | 496.3 | 502.8 | 61.4 | 53.8 | 177.3 | 214.6 | 90.3 | 70.3 | 138.4 | 82.9 | 74.3 | 161.3 | 138 | 100.3 | 88 | 83.5 | 93.8 | 92.4 | 81.6 | 88.9 | 93.9
4347.2 | 4126.2 | -6.7 | 0 | 0 | 86.3 | 84.2 | 79.3 | 79.4 | 95 | 27.1 | 21.3 | 33.3 | 2.2 | 245.1 | 4.7 | 401.8 | 397 | 84.7 | 40.8 | 496.2 | 502.6 | 61 | 53.7 | 177.3 | 214.4 | 90.7 | 70.4 | 138.3 | 83 | 74.4 | 161.2 | 138 | 100.3 | 88 | 83.4 | 93.8 | 92.4 | 81.6 | 88.9 | 93.9
4348.2 | 4127.2 | -6.6 | 0 | 0 | 86.4 | 84.1 | 79.3 | 79.3 | 95.1 | 27 | 21.3 | 33.3 | 2.4 | 242.1 | 5.1 | 401.8 | 397 | 84.4 | 40.6 | 496.1 | 502.5 | 60.7 | 53.5 | 177.4 | 214.2 | 90.8 | 70.4 | 138.2 | 82.9 | 74.4 | 161.1 | 138 | 100.3 | 87.9 | 83.4 | 93.7 | 92.4 | 81.6 | 88.8 | 93.8
4349.2 | 4128.2 | -6.6 | 0 | 0 | 86.4 | 84.1 | 79.2 | 79.3 | 95.1 | 27 | 21.3 | 33.3 | 2.4 | 253.8 | 5.1 | 401.7 | 396.9 | 84.5 | 40.6 | 496 | 502.4 | 60.4 | 53.5 | 177.3 | 214 | 90.6 | 70.3 | 138.1 | 82.9 | 74.3 | 161 | 137.9 | 100.2 | 87.7 | 83.3 | 93.7 | 92.3 | 81.6 | 88.7 | 93.8
4350.2 | 4129.2 | -6.5 | 0 | 0 | 86.4 | 84 | 79.2 | 79.2 | 95.1 | 26.9 | 21.3 | 33.3 | 2.1 | 250.3 | 5.1 | 401.7 | 396.9 | 84.3 | 40.5 | 496 | 502.2 | 60.7 | 53.4 | 177.3 | 213.8 | 90.6 | 70.2 | 138 | 82.7 | 74.1 | 160.8 | 137.7 | 100.2 | 87.6 | 83.2 | 93.7 | 92.3 | 81.6 | 88.7 | 93.7
4351.2 | 4130.2 | -6.6 | 0 | 0 | 86.3 | 84 | 79.2 | 79.2 | 95.2 | 26.9 | 21.3 | 33.3 | 2.3 | 264.7 | 5.9 | 401.7 | 396.9 | 84.2 | 40.4 | 496 | 502.1 | 60.1 | 53.2 | 177.2 | 213.6 | 90.7 | 69.9 | 138 | 82.9 | 73.6 | 160.7 | 137.5 | 100.1 | 87.5 | 83.2 | 93.6 | 92.3 | 81.5 | 88.6 | 93.7
4352.2 | 4131.2 | -6.7 | 0 | 0 | 86.2 | 83.9 | 79.1 | 79.1 | 95.1 | 26.9 | 21.3 | 33.3 | 2.3 | 269.2 | 6 | 401.6 | 396.8 | 83.7 | 40.3 | 496 | 502.1 | 60.2 | 53.1 | 177.1 | 213.5 | 91.2 | 69.8 | 137.9 | 82.7 | 73.5 | 160.6 | 137.4 | 100.1 | 87.5 | 83.1 | 93.6 | 92.2 | 81.5 | 88.5 | 93.7
4353.2 | 4132.2 | -6.7 | 0 | 0 | 86.1 | 83.7 | 78.9 | 79.1 | 95 | 26.9 | 21.3 | 33.3 | 2 | 266.8 | 6.1 | 401.6 | 396.7 | 83.1 | 40.2 | 496 | 502 | 61.4 | 53 | 177.1 | 213.3 | 92.1 | 69.8 | 137.8 | 82.6 | 73.3 | 160.4 | 137.2 | 100.1 | 87.5 | 83.1 | 93.6 | 92.2 | 81.6 | 88.5 | 93.6
4354.2 | 4133.2 | -6.8 | 0 | 0 | 86.2 | 83.5 | 78.8 | 79.1 | 94.9 | 27 | 21.3 | 33.3 | 2.1 | 262.9 | 6.4 | 401.6 | 396.7 | 82.7 | 40.1 | 496.1 | 501.9 | 61.6 | 52.9 | 177 | 213.1 | 92.7 | 69.8 | 137.7 | 82.6 | 73.3 | 160.3 | 137.2 | 100 | 87.4 | 83.1 | 93.5 | 92.2 | 81.6 | 88.5 | 93.6
4355.2 | 4134.2 | -6.7 | 0 | 0 | 86.2 | 83.3 | 78.8 | 79 | 94.7 | 27 | 21.3 | 33.3 | 1.9 | 256.2 | 6.2 | 401.5 | 396.6 | 82.7 | 39.9 | 496.1 | 501.8 | 61.7 | 52.8 | 177.1 | 212.9 | 93.3 | 69.9 | 137.6 | 82.5 | 73.3 | 160.2 | 137.1 | 100 | 87.4 | 83 | 93.5 | 92.2 | 81.6 | 88.5 | 93.5
4356.2 | 4135.2 | -6.7 | 0 | 0 | 86.3 | 83.3 | 78.8 | 79 | 94.4 | 27 | 21.3 | 33.3 | 2 | 256.2 | 5.5 | 401.5 | 396.6 | 83.3 | 39.8 | 496.1 | 501.6 | 61.9 | 52.6 | 177 | 212.7 | 93.2 | 69.7 | 137.4 | 82.6 | 73.3 | 160.1 | 137 | 99.9 | 87.3 | 83 | 93.5 | 92.1 | 81.5 | 88.5 | 93.5
4357.2 | 4136.2 | -6.8 | 0 | 0 | 86.3 | 83.3 | 78.8 | 79 | 94.2 | 27 | 21.3 | 33.3 | 2.1 | 275.5 | 5.4 | 401.5 | 396.6 | 83.2 | 39.7 | 496.1 | 501.3 | 61.5 | 52.5 | 177 | 212.5 | 93.1 | 69.5 | 137.3 | 82.8 | 73.4 | 159.9 | 137 | 99.9 | 87.2 | 83 | 93.4 | 92.1 | 81.5 | 88.4 | 93.5
4358.2 | 4137.2 | -6.8 | 0 | 0 | 86.4 | 83.3 | 78.7 | 79.2 | 94.3 | 27 | 21.4 | 33.3 | 2.4 | 268.3 | 5.3 | 401.4 | 396.5 | 83.3 | 39.7 | 496.1 | 501 | 61.1 | 52.4 | 176.9 | 212.3 | 92.8 | 69.3 | 137.2 | 82.9 | 73.5 | 159.8 | 136.9 | 99.8 | 87.1 | 82.9 | 93.4 | 92 | 81.4 | 88.4 | 93.4
4359.2 | 4138.2 | -6.8 | 0 | 0 | 86.4 | 83.3 | 78.6 | 79.3 | 94.5 | 27 | 21.4 | 33.3 | 2.6 | 257.7 | 5 | 401.4 | 396.5 | 83.8 | 39.6 | 496.2 | 500.7 | 61.5 | 52.2 | 176.8 | 212.1 | 92.5 | 69.2 | 137.1 | 83 | 73.8 | 159.6 | 136.8 | 99.8 | 87 | 82.9 | 93.3 | 91.9 | 81.4 | 88.4 | 93.4
4360.2 | 4139.2 | -6.8 | 0 | 0 | 86.3 | 83.2 | 78.5 | 79.4 | 94.5 | 26.9 | 21.4 | 33.3 | 2.5 | 260.1 | 4.9 | 401.4 | 396.5 | 83.7 | 39.5 | 496.2 | 500.5 | 62 | 52.2 | 176.8 | 211.9 | 92.3 | 69.1 | 137 | 83 | 74 | 159.5 | 136.7 | 99.8 | 86.9 | 82.8 | 93.3 | 91.9 | 81.4 | 88.4 | 93.4
4361.2 | 4140.2 | -6.8 | 0 | 0 | 86.2 | 83.1 | 78.5 | 79.4 | 94.3 | 26.8 | 21.4 | 33.3 | 2.4 | 266.9 | 4.9 | 401.3 | 396.4 | 83.8 | 39.4 | 496.2 | 500.3 | 62.7 | 52.1 | 176.8 | 211.7 | 92 | 69.1 | 136.9 | 82.8 | 74.1 | 159.4 | 136.6 | 99.7 | 86.8 | 82.8 | 93.3 | 91.8 | 81.3 | 88.3 | 93.3
4362.2 | 4141.2 | -6.8 | 0 | 0 | 86 | 83 | 78.5 | 79.4 | 93.9 | 26.9 | 21.3 | 33.2 | 2.3 | 267.9 | 5.1 | 401.3 | 396.4 | 84 | 39.4 | 496.2 | 500.3 | 63.2 | 52.2 | 176.6 | 211.5 | 91.9 | 69.3 | 136.8 | 82.5 | 74.2 | 159.2 | 136.6 | 99.7 | 86.8 | 82.8 | 93.2 | 91.8 | 81.3 | 88.3 | 93.3
4363.2 | 4142.2 | -6.8 | 0 | 0 | 85.8 | 83 | 78.5 | 79.4 | 93.6 | 26.9 | 21.3 | 33.2 | 2.2 | 269 | 5.2 | 401.3 | 396.3 | 84.4 | 39.5 | 496.1 | 500.3 | 63.8 | 52.4 | 176.8 | 211.3 | 92 | 69.3 | 136.7 | 82.5 | 74.2 | 159.1 | 136.5 | 99.6 | 86.8 | 82.9 | 93.2 | 91.7 | 81.2 | 88.3 | 93.2
4364.2 | 4143.2 | -6.8 | 0 | 0 | 85.8 | 83.1 | 78.5 | 79.4 | 93.6 | 26.8 | 21.4 | 33.2 | 2.1 | 266.9 | 5 | 401.2 | 396.2 | 84.3 | 39.6 | 496 | 500.2 | 63.9 | 52.2 | 176.8 | 211.1 | 92 | 69.3 | 136.6 | 82.5 | 74.2 | 159 | 136.3 | 99.6 | 86.8 | 82.9 | 93.2 | 91.6 | 81.1 | 88.2 | 93.2
4365.2 | 4144.2 | -6.5 | 0 | 0 | 85.7 | 83.1 | 78.5 | 79.4 | 93.7 | 26.8 | 21.4 | 33.2 | 1.9 | 260.9 | 5 | 401.2 | 396.2 | 84.7 | 39.6 | 495.9 | 500.2 | 63.7 | 52.2 | 176.7 | 211 | 92.2 | 69.5 | 136.4 | 82.4 | 74.4 | 158.9 | 136.2 | 99.5 | 86.8 | 82.9 | 93.1 | 91.6 | 81 | 88.2 | 93.2
4366.2 | 4145.2 | -6.6 | 0 | 0 | 85.6 | 83.2 | 78.5 | 79.3 | 93.8 | 26.8 | 21.4 | 33.1 | 1.7 | 263.6 | 5.5 | 401.1 | 396.1 | 84.7 | 39.8 | 495.8 | 500.1 | 63.8 | 52.4 | 176.8 | 210.8 | 92 | 69.6 | 136.3 | 82.5 | 74.4 | 158.7 | 136.1 | 99.5 | 86.8 | 82.8 | 93.1 | 91.5 | 81 | 88.2 | 93.1
4367.2 | 4146.2 | -6.6 | 0 | 0 | 85.7 | 83.2 | 78.4 | 79.1 | 93.9 | 26.8 | 21.4 | 33.1 | 1.9 | 257.5 | 5.6 | 401.1 | 396.1 | 84.5 | 39.9 | 495.7 | 500.3 | 63.5 | 52.4 | 176.8 | 210.6 | 91.9 | 69.5 | 136.2 | 82.6 | 74.4 | 158.6 | 136 | 99.5 | 86.8 | 82.8 | 93.1 | 91.4 | 80.9 | 88.1 | 93.1
4368.2 | 4147.2 | -6.7 | 0 | 0 | 85.8 | 83.1 | 78.4 | 79 | 93.9 | 26.9 | 21.4 | 33.1 | 1.9 | 256.1 | 5.3 | 401 | 396.1 | 84 | 39.8 | 495.6 | 500.5 | 63.1 | 52.5 | 176.8 | 210.4 | 92.2 | 69.5 | 136.1 | 82.4 | 74.2 | 158.5 | 135.9 | 99.5 | 86.8 | 82.8 | 93 | 91.4 | 80.9 | 88.1 | 93.1
4369.2 | 4148.2 | -6.6 | 0 | 0 | 85.9 | 82.9 | 78.3 | 78.9 | 93.9 | 26.8 | 21.4 | 33.1 | 1.8 | 225.4 | 5 | 401 | 396 | 83.8 | 39.8 | 495.5 | 500.5 | 62.6 | 52.6 | 176.8 | 210.2 | 92.5 | 69.3 | 136 | 82.2 | 74.1 | 158.3 | 135.9 | 99.4 | 86.7 | 82.8 | 93 | 91.3 | 80.9 | 88 | 93
4370.2 | 4149.2 | -6.6 | 0 | 0 | 85.9 | 82.8 | 78.4 | 78.9 | 93.7 | 26.7 | 21.4 | 33 | 2.1 | 230 | 4.8 | 400.9 | 396 | 83.9 | 40 | 495.3 | 500.5 | 62.2 | 52.6 | 176.8 | 210 | 92.4 | 69.1 | 135.9 | 82.2 | 74.1 | 158.2 | 135.9 | 99.3 | 86.7 | 82.7 | 93 | 91.3 | 80.8 | 87.9 | 93
4371.2 | 4150.2 | -6.6 | 0 | 0 | 85.9 | 82.8 | 78.4 | 78.9 | 93.4 | 26.6 | 21.4 | 33.1 | 2.2 | 238.3 | 5.1 | 400.9 | 395.9 | 84.5 | 40.1 | 495.2 | 500.4 | 61.7 | 52.4 | 176.7 | 209.8 | 92.5 | 68.9 | 135.8 | 82.1 | 73.9 | 158.1 | 135.9 | 99.3 | 86.6 | 82.6 | 92.9 | 91.2 | 80.8 | 87.8 | 92.9
4372.2 | 4151.2 | -6.7 | 0 | 0 | 85.6 | 83 | 78.4 | 78.9 | 93.3 | 26.6 | 21.4 | 33.1 | 2.7 | 241.4 | 5.2 | 400.9 | 395.9 | 84.6 | 40.1 | 495 | 500.2 | 61.7 | 52.5 | 176.7 | 209.6 | 92.2 | 68.9 | 135.8 | 82 | 73.8 | 158 | 135.9 | 99.3 | 86.6 | 82.6 | 92.9 | 91.2 | 80.8 | 87.7 | 92.9
4373.2 | 4152.2 | -6.7 | 0 | 0 | 85.2 | 83.2 | 78.4 | 79 | 93.2 | 26.5 | 21.4 | 33.1 | 2.5 | 235.2 | 5.1 | 400.8 | 395.8 | 84 | 40.1 | 494.9 | 500 | 61.4 | 52.6 | 176.7 | 209.4 | 91.9 | 68.6 | 135.7 | 81.8 | 73.5 | 157.8 | 135.8 | 99.2 | 86.6 | 82.6 | 92.9 | 91.2 | 80.8 | 87.7 | 92.9
4374.2 | 4153.2 | -6.7 | 0 | 0 | 85 | 83.3 | 78.4 | 79.1 | 93 | 26.5 | 21.4 | 33.1 | 2.4 | 231.3 | 5 | 400.8 | 395.8 | 84.2 | 40.2 | 494.8 | 500.1 | 61 | 52.8 | 176.7 | 209.2 | 92.1 | 68.6 | 135.6 | 81.5 | 73.5 | 157.7 | 135.8 | 99.2 | 86.5 | 82.6 | 92.9 | 91.2 | 80.9 | 87.6 | 92.8
4375.2 | 4154.2 | -6.7 | 0 | 0 | 85.1 | 83.3 | 78.3 | 79.1 | 92.9 | 26.4 | 21.4 | 33.1 | 2.9 | 232 | 4.9 | 400.7 | 395.7 | 84.2 | 40.5 | 494.7 | 500.5 | 60.7 | 52.9 | 176.7 | 209 | 92.1 | 68.7 | 135.5 | 81.4 | 73.6 | 157.6 | 135.7 | 99.1 | 86.5 | 82.6 | 92.8 | 91.2 | 80.9 | 87.6 | 92.8
4376.2 | 4155.2 | -6.7 | 0 | 0 | 85.1 | 83.2 | 78.2 | 79.1 | 92.6 | 26.3 | 21.3 | 33.1 | 2.7 | 234 | 4.7 | 400.7 | 395.7 | 84.1 | 40.6 | 494.6 | 501 | 60.4 | 52.9 | 176.7 | 208.8 | 92.2 | 68.7 | 135.4 | 81.4 | 73.6 | 157.5 | 135.6 | 99 | 86.3 | 82.5 | 92.7 | 91.2 | 80.8 | 87.6 | 92.7
4377.2 | 4156.2 | -6.8 | 0 | 0 | 85.1 | 83.1 | 78.2 | 78.8 | 92.2 | 26.3 | 21.4 | 33.1 | 2.4 | 245.3 | 4.2 | 400.6 | 395.6 | 84.3 | 40.6 | 494.6 | 501.6 | 60.1 | 52.9 | 176.7 | 208.6 | 92 | 68.7 | 135.3 | 81.4 | 73.5 | 157.3 | 135.5 | 99 | 86.2 | 82.4 | 92.7 | 91.2 | 80.7 | 87.5 | 92.7
4378.2 | 4157.2 | -6.8 | 0 | 0 | 85 | 83 | 78.2 | 78.6 | 92 | 26.3 | 21.4 | 33.1 | 2.4 | 260.1 | 3.6 | 400.6 | 395.6 | 84.1 | 40.5 | 494.5 | 501.9 | 59.8 | 52.9 | 176.7 | 208.4 | 91.7 | 68.7 | 135.3 | 81.4 | 73.3 | 157.2 | 135.4 | 98.9 | 86.2 | 82.4 | 92.6 | 91.2 | 80.7 | 87.5 | 92.7
4379.2 | 4158.2 | -6.8 | 0 | 0 | 85 | 83 | 78.3 | 78.6 | 91.8 | 26.3 | 21.4 | 33 | 2.5 | 269.5 | 3.2 | 400.5 | 395.5 | 83.9 | 40.3 | 494.5 | 501.9 | 59.7 | 52.9 | 176.7 | 208.2 | 91.2 | 68.7 | 135.2 | 81.5 | 73.2 | 157.1 | 135.3 | 98.9 | 86.1 | 82.4 | 92.6 | 91.2 | 80.8 | 87.5 | 92.6
4380.2 | 4159.2 | -6.8 | 0 | 0 | 85 | 82.9 | 78.3 | 78.7 | 91.8 | 26.4 | 21.4 | 32.9 | 2.4 | 270.4 | 3 | 400.5 | 395.5 | 83.6 | 40.3 | 494.4 | 501.8 | 59.4 | 52.8 | 176.7 | 208 | 90.9 | 68.7 | 135.1 | 81.7 | 73.1 | 156.9 | 135.2 | 98.8 | 86.1 | 82.3 | 92.5 | 91.1 | 80.8 | 87.5 | 92.6
4381.2 | 4160.2 | -6.8 | 0 | 0 | 85 | 82.8 | 78.3 | 78.8 | 91.9 | 26.4 | 21.4 | 32.9 | 2.5 | 266.5 | 3 | 400.4 | 395.4 | 83.9 | 40.1 | 494.3 | 501.7 | 59 | 52.6 | 176.7 | 207.8 | 90.5 | 68.7 | 135 | 82 | 73 | 156.8 | 135.1 | 98.8 | 86.1 | 82.2 | 92.5 | 91.1 | 80.9 | 87.5 | 92.6
4382.2 | 4161.2 | -6.8 | 0 | 0 | 85.1 | 82.7 | 78.3 | 78.9 | 92 | 26.4 | 21.4 | 32.9 | 3.3 | 257.5 | 3.3 | 400.4 | 395.4 | 84.3 | 39.9 | 494.2 | 501.6 | 58.6 | 52.3 | 176.6 | 207.6 | 90.4 | 68.7 | 134.9 | 82.1 | 73 | 156.7 | 134.9 | 98.7 | 86 | 82.1 | 92.4 | 91 | 80.8 | 87.4 | 92.5
4383.2 | 4162.2 | -6.8 | 0 | 0 | 85.2 | 82.7 | 78.3 | 79 | 92.2 | 26.3 | 21.4 | 32.9 | 3.6 | 260 | 3.4 | 400.3 | 395.3 | 84.4 | 39.8 | 494.2 | 501.3 | 58 | 52.1 | 176.6 | 207.3 | 90.5 | 68.8 | 134.9 | 82.3 | 73 | 156.6 | 134.8 | 98.7 | 85.9 | 82.1 | 92.4 | 91 | 80.8 | 87.4 | 92.5
4384.2 | 4163.2 | -6.8 | 0 | 0 | 85.2 | 82.7 | 78.2 | 79.1 | 92.3 | 26.3 | 21.4 | 32.8 | 3.7 | 259.2 | 3.2 | 400.3 | 395.3 | 83.8 | 39.7 | 494.2 | 501.2 | 57.5 | 52 | 176.6 | 207.1 | 90.4 | 68.9 | 134.8 | 82.6 | 73.2 | 156.4 | 134.8 | 98.7 | 85.9 | 82.1 | 92.3 | 91 | 80.7 | 87.3 | 92.5
4385.2 | 4164.2 | -6.8 | 0 | 0 | 85.3 | 82.6 | 78 | 79.1 | 92.1 | 26.3 | 21.4 | 32.8 | 3.4 | 246.9 | 2.8 | 400.3 | 395.2 | 84.1 | 39.7 | 494.2 | 501.4 | 57 | 52 | 176.7 | 206.9 | 90 | 69.1 | 134.7 | 82.5 | 73.2 | 156.3 | 134.8 | 98.6 | 85.9 | 82 | 92.3 | 90.9 | 80.7 | 87.2 | 92.4
4386.2 | 4165.2 | -6.8 | 0 | 0 | 85.3 | 82.6 | 77.9 | 79.1 | 92 | 26.4 | 21.4 | 32.8 | 3.2 | 233.2 | 2.6 | 400.2 | 395.2 | 83.5 | 39.9 | 494.1 | 502.3 | 56.6 | 52 | 176.8 | 206.7 | 89.6 | 69 | 134.6 | 82.4 | 73.1 | 156.2 | 134.7 | 98.6 | 85.9 | 82.1 | 92.3 | 90.9 | 80.7 | 87.2 | 92.4
4387.2 | 4166.2 | -6.8 | 0 | 0 | 85.2 | 82.5 | 77.9 | 79 | 91.9 | 26.4 | 21.4 | 32.8 | 2.8 | 232.9 | 2.5 | 400.2 | 395.2 | 83 | 39.8 | 494.1 | 502.9 | 56.1 | 51.9 | 176.9 | 206.5 | 89.3 | 68.8 | 134.5 | 82.4 | 73 | 156.1 | 134.6 | 98.5 | 85.9 | 82.1 | 92.3 | 90.9 | 80.7 | 87.1 | 92.4
4388.2 | 4167.2 | -6.7 | 0 | 0 | 85 | 82.5 | 77.9 | 79 | 91.7 | 26.4 | 21.4 | 32.8 | 2.5 | 237.6 | 2.4 | 400.1 | 395.1 | 83.3 | 39.7 | 494 | 503.3 | 55.8 | 51.7 | 176.8 | 206.3 | 89.2 | 68.6 | 134.5 | 82.3 | 73 | 155.9 | 134.5 | 98.5 | 85.9 | 82.1 | 92.3 | 90.9 | 80.7 | 87.1 | 92.3
4389.2 | 4168.2 | -6.7 | 0 | 0 | 84.7 | 82.6 | 77.9 | 79 | 91.7 | 26.6 | 21.4 | 32.7 | 2.5 | 240.4 | 2.6 | 400.1 | 395.1 | 82.7 | 39.6 | 494 | 503.5 | 55.3 | 51.8 | 176.8 | 206 | 88.9 | 68.5 | 134.4 | 82.5 | 72.9 | 155.8 | 134.5 | 98.5 | 85.9 | 82 | 92.2 | 90.9 | 80.7 | 87.1 | 92.3
4390.2 | 4169.2 | -6.8 | 0 | 0 | 84.4 | 82.8 | 77.8 | 79 | 91.7 | 26.6 | 21.4 | 32.7 | 2.8 | 242.3 | 2.7 | 400 | 395 | 82.8 | 39.6 | 494 | 503.4 | 55 | 51.8 | 176.8 | 205.8 | 88.8 | 68.7 | 134.3 | 82.6 | 73.1 | 155.7 | 134.5 | 98.4 | 85.9 | 81.9 | 92.1 | 90.8 | 80.7 | 87.1 | 92.2
4391.2 | 4170.2 | -6.8 | 0 | 0 | 84.3 | 82.9 | 77.7 | 78.9 | 91.8 | 26.6 | 21.4 | 32.7 | 2.5 | 247.1 | 2.9 | 400 | 395 | 83.3 | 39.6 | 494 | 503.2 | 54.8 | 51.8 | 176.8 | 205.6 | 88.5 | 68.7 | 134.2 | 82.4 | 73.1 | 155.6 | 134.4 | 98.3 | 85.9 | 81.9 | 92.1 | 90.8 | 80.6 | 87 | 92.2
4392.2 | 4171.2 | -6.7 | 0 | 0 | 84.3 | 82.9 | 77.6 | 78.8 | 91.9 | 26.5 | 21.4 | 32.7 | 3.2 | 253.3 | 3.5 | 399.9 | 394.9 | 82.8 | 39.6 | 493.9 | 502.9 | 54.6 | 51.9 | 176.8 | 205.4 | 88.1 | 68.5 | 134.1 | 82.4 | 73 | 155.4 | 134.2 | 98.3 | 85.9 | 81.8 | 92.1 | 90.8 | 80.6 | 87 | 92.2
4393.2 | 4172.2 | -6.8 | 0 | 0 | 84.2 | 82.8 | 77.6 | 78.7 | 91.9 | 26.5 | 21.4 | 32.8 | 3.3 | 251.3 | 3.8 | 399.9 | 394.9 | 82.5 | 39.6 | 493.9 | 502.6 | 54.3 | 51.6 | 176.7 | 205.1 | 87.7 | 68.3 | 134 | 82.2 | 72.8 | 155.3 | 134.2 | 98.3 | 85.9 | 81.8 | 92 | 90.7 | 80.6 | 87 | 92.1
4394.2 | 4173.2 | -6.8 | 0 | 0 | 84.3 | 82.7 | 77.6 | 78.6 | 91.9 | 26.5 | 21.4 | 32.7 | 3.6 | 226.8 | 3.9 | 399.8 | 394.8 | 82.4 | 39.5 | 493.8 | 502.7 | 54.6 | 51.4 | 176.6 | 204.9 | 87.6 | 68.1 | 134 | 82.1 | 72.7 | 155.2 | 134.2 | 98.2 | 85.9 | 81.8 | 92 | 90.7 | 80.5 | 87 | 92.1
4395.2 | 4174.2 | -6.7 | 0 | 0 | 84.2 | 82.6 | 77.7 | 78.5 | 92 | 26.6 | 21.4 | 32.7 | 3.2 | 211.3 | 4 | 399.8 | 394.8 | 82.3 | 39.4 | 493.8 | 502.5 | 54.9 | 51.2 | 176.5 | 204.7 | 87.7 | 68.1 | 133.9 | 82 | 72.6 | 155.1 | 134.2 | 98.1 | 85.8 | 81.8 | 91.9 | 90.6 | 80.5 | 87 | 92
4396.2 | 4175.2 | -6.8 | 0 | 0 | 83.9 | 82.5 | 77.7 | 78.4 | 92.1 | 26.6 | 21.4 | 32.6 | 3 | 231.4 | 4.1 | 399.8 | 394.7 | 82.2 | 39.4 | 493.8 | 502.2 | 55.6 | 51.1 | 176.2 | 204.5 | 87.7 | 67.9 | 133.8 | 81.9 | 72.5 | 154.9 | 134.2 | 98.1 | 85.8 | 81.7 | 91.9 | 90.6 | 80.4 | 86.9 | 92
4397.2 | 4176.2 | -6.8 | 0 | 0 | 83.9 | 82.5 | 77.7 | 78.3 | 92.1 | 26.6 | 21.4 | 32.6 | 2.9 | 217.9 | 3.8 | 399.7 | 394.7 | 82 | 39.4 | 493.8 | 501.8 | 56.1 | 51 | 176 | 204.3 | 87.5 | 67.6 | 133.7 | 81.8 | 72.2 | 154.8 | 134.1 | 98.1 | 85.7 | 81.7 | 91.9 | 90.5 | 80.3 | 86.9 | 91.9
4398.2 | 4177.2 | -6.8 | 0 | 0 | 84 | 82.5 | 77.7 | 78.1 | 92.1 | 26.5 | 21.4 | 32.6 | 2.9 | 188.3 | 3.7 | 399.7 | 394.7 | 82.4 | 39.3 | 493.7 | 501.4 | 56.3 | 51.1 | 176 | 204.1 | 87.3 | 67.5 | 133.6 | 81.6 | 72.2 | 154.7 | 134 | 98.1 | 85.7 | 81.7 | 91.9 | 90.5 | 80.2 | 86.8 | 91.9
4399.2 | 4178.2 | -6.8 | 0 | 0 | 84.1 | 82.5 | 77.6 | 78 | 92.2 | 26.4 | 21.4 | 32.6 | 3.1 | 191.4 | 3.4 | 399.6 | 394.6 | 82.8 | 39.4 | 493.7 | 501.1 | 57.4 | 51.1 | 175.9 | 203.9 | 87.4 | 67.3 | 133.5 | 81.5 | 71.9 | 154.6 | 133.9 | 98 | 85.7 | 81.7 | 91.9 | 90.4 | 80.1 | 86.7 | 91.9
4400.2 | 4179.2 | -6.8 | 0 | 0 | 84.2 | 82.5 | 77.6 | 77.9 | 92.1 | 26.5 | 21.4 | 32.6 | 3.3 | 208.6 | 3.3 | 399.6 | 394.6 | 82.4 | 39.5 | 493.7 | 500.8 | 58 | 51.3 | 175.9 | 203.7 | 87.1 | 67.1 | 133.4 | 81.3 | 71.9 | 154.4 | 133.8 | 98 | 85.7 | 81.7 | 91.8 | 90.4 | 80.1 | 86.7 | 91.8
4401.2 | 4180.2 | -6.8 | 0 | 0 | 84.2 | 82.5 | 77.6 | 77.9 | 92 | 26.4 | 21.4 | 32.5 | 3.4 | 216.2 | 2.9 | 399.6 | 394.5 | 81.9 | 39.6 | 493.6 | 500.5 | 58.8 | 51.5 | 175.9 | 203.5 | 87.2 | 67 | 133.3 | 81.2 | 71.8 | 154.3 | 133.6 | 97.9 | 85.7 | 81.7 | 91.8 | 90.3 | 80 | 86.6 | 91.8
4402.2 | 4181.2 | -6.8 | 0 | 0 | 83.8 | 82.4 | 77.7 | 78.1 | 91.8 | 26.4 | 21.4 | 32.5 | 3.5 | 230.3 | 2.5 | 399.5 | 394.5 | 81.7 | 39.8 | 493.5 | 500.2 | 59.5 | 51.8 | 175.9 | 203.2 | 87.1 | 66.8 | 133.2 | 81.2 | 71.6 | 154.2 | 133.5 | 97.9 | 85.7 | 81.6 | 91.8 | 90.3 | 80.1 | 86.6 | 91.8
4403.2 | 4182.2 | -6.8 | 0 | 0 | 83.4 | 82.3 | 77.7 | 78.2 | 91.8 | 26.4 | 21.4 | 32.5 | 3.6 | 238 | 2.4 | 399.5 | 394.5 | 81.2 | 39.9 | 493.4 | 500 | 59.9 | 51.9 | 175.9 | 203 | 87 | 66.7 | 133.1 | 81.1 | 71.6 | 154.1 | 133.4 | 97.8 | 85.7 | 81.6 | 91.7 | 90.2 | 80.1 | 86.5 | 91.7
4404.2 | 4183.2 | -6.8 | 0 | 0 | 83.4 | 82.3 | 77.7 | 78.2 | 91.8 | 26.3 | 21.4 | 32.4 | 3.5 | 242.3 | 2.4 | 399.5 | 394.4 | 80.8 | 39.9 | 493.3 | 499.6 | 60 | 51.9 | 175.8 | 202.8 | 87 | 66.7 | 133 | 81.1 | 71.5 | 154 | 133.2 | 97.8 | 85.7 | 81.5 | 91.7 | 90.2 | 80 | 86.5 | 91.7
4405.2 | 4184.2 | -6.8 | 0 | 0 | 83.4 | 82.3 | 77.7 | 78 | 91.9 | 26.3 | 21.4 | 32.4 | 2.9 | 245.9 | 2.8 | 399.4 | 394.4 | 80.5 | 39.7 | 493.3 | 499.3 | 59.6 | 51.6 | 175.8 | 202.6 | 86.9 | 66.6 | 132.9 | 81 | 71.4 | 153.8 | 133.2 | 97.7 | 85.6 | 81.4 | 91.6 | 90.2 | 80 | 86.5 | 91.6
4406.2 | 4185.2 | -6.8 | 0 | 0 | 83.5 | 82.4 | 77.7 | 77.9 | 91.8 | 26.4 | 21.4 | 32.4 | 2.7 | 229.5 | 3.5 | 399.4 | 394.3 | 80.4 | 39.7 | 493.2 | 499.1 | 59.2 | 51.6 | 175.6 | 202.4 | 87.3 | 66.7 | 132.8 | 80.8 | 71.5 | 153.7 | 133.2 | 97.7 | 85.6 | 81.4 | 91.6 | 90.1 | 79.9 | 86.5 | 91.6
4407.2 | 4186.2 | -6.8 | 0 | 0 | 83.5 | 82.4 | 77.6 | 77.7 | 91.7 | 26.4 | 21.4 | 32.4 | 2.5 | 211.7 | 3.5 | 399.4 | 394.3 | 80.7 | 39.6 | 493.2 | 498.9 | 58.7 | 51.5 | 175.6 | 202.3 | 87.3 | 66.7 | 132.7 | 80.6 | 71.4 | 153.6 | 133.2 | 97.7 | 85.5 | 81.4 | 91.6 | 90.1 | 79.9 | 86.4 | 91.6
4408.2 | 4187.2 | -6.8 | 0 | 0 | 83.6 | 82.3 | 77.5 | 77.6 | 91.4 | 26.4 | 21.4 | 32.4 | 2.8 | 209.6 | 3.2 | 399.3 | 394.2 | 81.6 | 39.5 | 493.2 | 498.6 | 58.2 | 51.4 | 175.6 | 202.1 | 87.2 | 66.7 | 132.6 | 80.7 | 71.5 | 153.5 | 133.2 | 97.6 | 85.5 | 81.4 | 91.5 | 90.1 | 79.8 | 86.4 | 91.5
4409.2 | 4188.2 | -6.8 | 0 | 0 | 83.6 | 82.2 | 77.5 | 77.6 | 91.2 | 26.4 | 21.4 | 32.4 | 3.2 | 212.3 | 3 | 399.3 | 394.2 | 82.2 | 39.5 | 493.2 | 498.3 | 57.6 | 51.3 | 175.6 | 201.9 | 87.4 | 66.6 | 132.5 | 80.6 | 71.8 | 153.4 | 133.2 | 97.6 | 85.5 | 81.3 | 91.4 | 90 | 79.8 | 86.3 | 91.5
4410.2 | 4189.2 | -6.7 | 0 | 0 | 83.6 | 81.9 | 77.5 | 77.8 | 91.1 | 26.4 | 21.4 | 32.3 | 2.7 | 220.8 | 2.7 | 399.3 | 394.1 | 82 | 39.4 | 493.2 | 498 | 57.3 | 51 | 175.5 | 201.7 | 87.2 | 66.7 | 132.4 | 80.6 | 72 | 153.2 | 133.2 | 97.5 | 85.4 | 81.3 | 91.4 | 90 | 79.8 | 86.3 | 91.5
4411.2 | 4190.2 | -6.6 | 0 | 0 | 83.6 | 81.7 | 77.4 | 77.8 | 91.1 | 26.3 | 21.4 | 32.3 | 2.4 | 237.5 | 2.7 | 399.2 | 394.1 | 82.5 | 39.3 | 493.2 | 497.7 | 56.7 | 50.8 | 175.5 | 201.5 | 87.1 | 66.7 | 132.3 | 80.7 | 72.2 | 153.1 | 133.2 | 97.5 | 85.3 | 81.2 | 91.4 | 90 | 79.7 | 86.2 | 91.4
4412.2 | 4191.2 | -6.3 | 0 | 0 | 83.6 | 81.8 | 77.3 | 77.8 | 91.1 | 26.3 | 21.4 | 32.3 | 2.4 | 248.8 | 2.9 | 399.2 | 394.1 | 82.6 | 39.2 | 493.2 | 497.4 | 56.3 | 50.9 | 175.5 | 201.3 | 87 | 66.7 | 132.2 | 80.7 | 72.4 | 153 | 133.2 | 97.5 | 85.3 | 81.2 | 91.3 | 90 | 79.7 | 86.2 | 91.4
4413.2 | 4192.2 | -6.5 | 0 | 0 | 83.6 | 81.9 | 77.3 | 77.8 | 91.1 | 26.2 | 21.4 | 32.3 | 2.6 | 253.7 | 3.2 | 399.2 | 394 | 81.7 | 39.1 | 493.1 | 497.2 | 55.8 | 50.8 | 175.4 | 201.1 | 87 | 66.7 | 132.2 | 80.7 | 72.6 | 152.9 | 133.2 | 97.4 | 85.3 | 81.1 | 91.2 | 89.9 | 79.6 | 86.2 | 91.4
4414.2 | 4193.2 | -6.6 | 0 | 0 | 83.4 | 81.9 | 77.3 | 77.9 | 91.1 | 26.2 | 21.4 | 32.3 | 2.7 | 252.8 | 3.2 | 399.1 | 394 | 81.6 | 39 | 493 | 497.2 | 55.4 | 50.6 | 175.4 | 200.9 | 86.9 | 66.7 | 132.1 | 80.6 | 72.6 | 152.7 | 133.1 | 97.4 | 85.3 | 81 | 91.2 | 89.9 | 79.6 | 86 | 91.3
4415.2 | 4194.2 | -6.7 | 0 | 0 | 83.3 | 81.8 | 77.2 | 77.9 | 91 | 26.2 | 21.4 | 32.3 | 2.9 | 247.4 | 3.2 | 399.1 | 393.9 | 82.1 | 38.8 | 492.9 | 497.2 | 55.2 | 50.5 | 175.4 | 200.7 | 86.5 | 66.8 | 132 | 80.6 | 72.7 | 152.6 | 133.2 | 97.3 | 85.3 | 80.9 | 91.2 | 89.9 | 79.6 | 86 | 91.3
4416.2 | 4195.2 | -6.7 | 0 | 0 | 83.2 | 81.7 | 77 | 77.9 | 91.1 | 26.2 | 21.4 | 32.2 | 3 | 243.5 | 3.2 | 399 | 393.9 | 81.9 | 38.7 | 492.8 | 497.3 | 54.7 | 50.3 | 175.3 | 200.5 | 86.1 | 66.6 | 131.9 | 80.5 | 72.7 | 152.5 | 133.2 | 97.2 | 85.2 | 80.9 | 91.2 | 89.9 | 79.6 | 85.9 | 91.2
4417.2 | 4196.2 | -6.7 | 0 | 0 | 83.2 | 81.7 | 76.9 | 77.9 | 91.3 | 26.2 | 21.4 | 32.2 | 3.2 | 239.5 | 2.9 | 399 | 393.8 | 81.6 | 38.6 | 492.8 | 497.5 | 54.8 | 50.2 | 175.3 | 200.3 | 85.9 | 66.5 | 131.8 | 80.6 | 72.4 | 152.4 | 133.2 | 97.2 | 85.2 | 80.8 | 91.2 | 89.9 | 79.6 | 85.9 | 91.2
4418.2 | 4197.2 | -6.7 | 0 | 0 | 83.3 | 81.8 | 76.8 | 77.8 | 91.5 | 26.1 | 21.4 | 32.2 | 2.6 | 227.6 | 2.8 | 399 | 393.8 | 81.8 | 38.5 | 492.8 | 497.5 | 55.3 | 49.9 | 175.2 | 200.1 | 85.7 | 66.5 | 131.7 | 80.5 | 71.8 | 152.3 | 133.1 | 97.2 | 85.2 | 80.8 | 91.1 | 89.9 | 79.6 | 85.9 | 91.2
4419.2 | 4198.2 | -6.8 | 0 | 0 | 83.3 | 81.8 | 76.8 | 77.7 | 91.5 | 26.1 | 21.4 | 32.2 | 2.4 | 220.2 | 2.9 | 398.9 | 393.7 | 81.7 | 38.4 | 492.8 | 497.4 | 56.2 | 49.8 | 175.1 | 199.9 | 85.3 | 66.5 | 131.6 | 80.6 | 71.6 | 152.1 | 132.9 | 97.1 | 85.1 | 80.8 | 91 | 89.8 | 79.6 | 85.9 | 91.1
4420.2 | 4199.2 | -6.8 | 0 | 0 | 83.2 | 81.7 | 76.9 | 77.6 | 91.6 | 26 | 21.4 | 32.2 | 2.2 | 221.3 | 3.1 | 398.9 | 393.7 | 80.7 | 38.3 | 492.9 | 497.1 | 56.7 | 49.7 | 175 | 199.7 | 85.1 | 66.6 | 131.5 | 80.6 | 71.2 | 152 | 132.9 | 97.1 | 85.1 | 80.7 | 91 | 89.8 | 79.6 | 85.9 | 91.1
4421.2 | 4200.2 | -6.8 | 0 | 0 | 83.2 | 81.6 | 76.9 | 77.6 | 91.6 | 26 | 21.4 | 32.2 | 2.2 | 221.5 | 3.2 | 398.8 | 393.6 | 80.8 | 38.4 | 493 | 497 | 57.5 | 49.7 | 174.9 | 199.5 | 85 | 66.4 | 131.4 | 80.6 | 71 | 151.9 | 132.7 | 97 | 85.1 | 80.6 | 90.9 | 89.7 | 79.5 | 85.8 | 91.1
4422.2 | 4201.2 | -6.8 | 0 | 0 | 83.2 | 81.5 | 76.9 | 77.5 | 91.7 | 26 | 21.4 | 32.2 | 2.2 | 224.3 | 3.2 | 398.8 | 393.6 | 80.7 | 38.4 | 493.1 | 496.9 | 57.8 | 49.7 | 174.8 | 199.3 | 84.9 | 66.2 | 131.3 | 80.8 | 70.6 | 151.8 | 132.7 | 97 | 85.1 | 80.6 | 90.9 | 89.6 | 79.4 | 85.7 | 91
4423.2 | 4202.2 | -6.8 | 0 | 0 | 83.3 | 81.5 | 76.9 | 77.4 | 91.7 | 26 | 21.4 | 32.2 | 2.2 | 233.2 | 2.9 | 398.8 | 393.6 | 80.7 | 38.4 | 493.1 | 496.8 | 57.8 | 49.7 | 174.8 | 199.1 | 84.7 | 66 | 131.3 | 80.9 | 70.5 | 151.7 | 132.7 | 96.9 | 85.1 | 80.6 | 90.9 | 89.6 | 79.3 | 85.7 | 91
4424.2 | 4203.2 | -6.8 | 0 | 0 | 83.3 | 81.6 | 76.8 | 77.3 | 91.8 | 26 | 21.4 | 32.2 | 2.4 | 233.8 | 2.7 | 398.7 | 393.5 | 80.5 | 38.3 | 493.1 | 496.6 | 58.3 | 49.6 | 174.8 | 199 | 84.5 | 65.7 | 131.2 | 81.1 | 70.6 | 151.5 | 132.7 | 96.9 | 85 | 80.6 | 90.8 | 89.5 | 79.2 | 85.6 | 90.9
4425.2 | 4204.2 | -6.8 | 0 | 0 | 83.4 | 81.6 | 76.8 | 77.3 | 91.7 | 26 | 21.4 | 32.2 | 2.3 | 234.3 | 2.6 | 398.7 | 393.5 | 80.3 | 38.4 | 493.1 | 496.7 | 58.7 | 49.6 | 174.8 | 198.8 | 84.3 | 65.7 | 131.1 | 81.2 | 70.5 | 151.4 | 132.6 | 96.8 | 85 | 80.6 | 90.8 | 89.4 | 79.2 | 85.6 | 90.9
4426.2 | 4205.2 | -6.8 | 0 | 0 | 83.4 | 81.5 | 76.8 | 77.2 | 91.5 | 26.1 | 21.4 | 32.2 | 2.5 | 233.5 | 2.7 | 398.7 | 393.4 | 80.8 | 38.5 | 493 | 496.7 | 58.3 | 49.8 | 174.7 | 198.6 | 84.1 | 65.5 | 131 | 81.2 | 70.5 | 151.3 | 132.6 | 96.8 | 85 | 80.6 | 90.7 | 89.3 | 79.1 | 85.5 | 90.9
4427.2 | 4206.2 | -6.8 | 0 | 0 | 83.3 | 81.4 | 76.8 | 77.1 | 91.4 | 26.1 | 21.4 | 32.2 | 1.9 | 232.4 | 2.9 | 398.6 | 393.4 | 81 | 38.5 | 493 | 496.6 | 58.1 | 50 | 174.7 | 198.4 | 84 | 65.6 | 130.9 | 81.2 | 70.6 | 151.2 | 132.6 | 96.8 | 85 | 80.6 | 90.7 | 89.3 | 79 | 85.5 | 90.8
4428.2 | 4207.2 | -6.8 | 0 | 0 | 83.3 | 81.2 | 76.9 | 77.1 | 91.3 | 26.1 | 21.4 | 32.2 | 1.5 | 228 | 3.1 | 398.6 | 393.3 | 81.2 | 38.7 | 493 | 496.6 | 58 | 50.1 | 174.7 | 198.2 | 83.8 | 65.6 | 130.8 | 81.2 | 70.5 | 151.1 | 132.5 | 96.7 | 85 | 80.5 | 90.6 | 89.2 | 79 | 85.4 | 90.8
4429.2 | 4208.2 | -6.8 | 0 | 0 | 83.3 | 81.1 | 76.8 | 77 | 91.3 | 26 | 21.4 | 32.2 | 1.4 | 219.5 | 3.1 | 398.5 | 393.3 | 82.3 | 38.7 | 492.9 | 496.5 | 57.8 | 50.3 | 174.7 | 198 | 83.4 | 65.7 | 130.8 | 81.1 | 70.5 | 151 | 132.4 | 96.7 | 85 | 80.6 | 90.6 | 89.1 | 78.9 | 85.4 | 90.7
4430.2 | 4209.2 | -6.8 | 0 | 0 | 83.4 | 80.9 | 76.8 | 77 | 91.3 | 26 | 21.4 | 32.2 | 1.5 | 227.5 | 3.2 | 398.5 | 393.3 | 82.9 | 38.9 | 492.9 | 496.3 | 57.8 | 50.5 | 174.6 | 197.8 | 83.1 | 65.7 | 130.7 | 81 | 70.6 | 150.8 | 132.3 | 96.7 | 84.9 | 80.5 | 90.5 | 89.1 | 78.8 | 85.4 | 90.7
4431.2 | 4210.2 | -6.8 | 0 | 0 | 83.5 | 80.8 | 76.9 | 76.9 | 91.2 | 26 | 21.4 | 32.2 | 1.4 | 219.3 | 3.5 | 398.5 | 393.2 | 82.8 | 39.1 | 492.9 | 496.2 | 58 | 50.7 | 174.7 | 197.7 | 83.1 | 65.7 | 130.6 | 80.9 | 70.6 | 150.7 | 132.1 | 96.7 | 84.8 | 80.4 | 90.5 | 89.1 | 78.8 | 85.3 | 90.7
4432.2 | 4211.2 | -6.8 | 0 | 0 | 83.5 | 80.7 | 76.9 | 76.9 | 91.2 | 25.9 | 21.4 | 32.1 | 1.4 | 200 | 3.9 | 398.4 | 393.2 | 83 | 39.2 | 492.8 | 496 | 58 | 50.8 | 174.8 | 197.5 | 82.9 | 65.6 | 130.5 | 80.8 | 70.9 | 150.6 | 132.1 | 96.6 | 84.6 | 80.4 | 90.5 | 89 | 78.7 | 85.3 | 90.6
4433.2 | 4212.2 | -6.8 | 0 | 0 | 83.4 | 80.5 | 76.9 | 76.8 | 91.2 | 26 | 21.4 | 32.1 | 1.3 | 216.5 | 4.9 | 398.4 | 393.1 | 82.7 | 39.2 | 492.7 | 496 | 57.7 | 50.8 | 174.7 | 197.3 | 82.7 | 65.6 | 130.3 | 80.8 | 70.9 | 150.5 | 132 | 96.6 | 84.5 | 80.3 | 90.4 | 89 | 78.6 | 85.3 | 90.6
4434.2 | 4213.2 | -6.8 | 0 | 0 | 83.2 | 80.5 | 76.9 | 76.8 | 91.3 | 26 | 21.4 | 32.1 | 1.2 | 216.7 | 5.6 | 398.4 | 393.1 | 82.8 | 39.2 | 492.6 | 496 | 57.8 | 50.6 | 174.7 | 197.1 | 82.6 | 65.7 | 130.2 | 80.9 | 70.9 | 150.4 | 131.8 | 96.5 | 84.5 | 80.2 | 90.4 | 88.9 | 78.6 | 85.3 | 90.6
4435.2 | 4214.2 | -6.8 | 0 | 0 | 83.1 | 80.4 | 76.8 | 76.7 | 91.4 | 26.1 | 21.4 | 32.1 | 1.4 | 214 | 5.8 | 398.3 | 393.1 | 82.8 | 39.2 | 492.5 | 496 | 59.1 | 50.6 | 174.6 | 196.9 | 82.5 | 65.6 | 130.1 | 80.9 | 71.1 | 150.2 | 131.6 | 96.5 | 84.5 | 80.2 | 90.3 | 88.9 | 78.6 | 85.3 | 90.5
4436.2 | 4215.2 | -6.8 | 0 | 0 | 83 | 80.3 | 76.7 | 76.6 | 91.5 | 26.2 | 21.4 | 32.2 | 1.3 | 214.1 | 5.6 | 398.3 | 393 | 82.4 | 39.2 | 492.4 | 495.9 | 60.5 | 50.7 | 174.6 | 196.7 | 82.2 | 65.6 | 130 | 80.7 | 71.3 | 150.1 | 131.6 | 96.4 | 84.4 | 80.1 | 90.3 | 88.9 | 78.5 | 85.3 | 90.5
4437.2 | 4216.2 | -6.8 | 0 | 0 | 83 | 80.3 | 76.6 | 76.4 | 91.4 | 26.2 | 21.4 | 32.3 | 1.1 | 214.7 | 5.3 | 398.2 | 392.9 | 81.8 | 39.3 | 492.3 | 495.8 | 61.6 | 50.6 | 174.6 | 196.5 | 81.9 | 65.2 | 129.9 | 80.5 | 71.1 | 150 | 131.6 | 96.4 | 84.5 | 80.1 | 90.3 | 88.8 | 78.5 | 85.2 | 90.4
4438.2 | 4217.2 | -6.8 | 0 | 0 | 83 | 80.3 | 76.6 | 76.3 | 91.2 | 26.2 | 21.4 | 32.3 | 1.3 | 215.3 | 5.4 | 398.2 | 392.9 | 81.9 | 39.3 | 492.3 | 495.7 | 62.1 | 50.5 | 174.5 | 196.3 | 81.8 | 65.1 | 129.8 | 80.4 | 71 | 149.9 | 131.5 | 96.4 | 84.4 | 80.1 | 90.3 | 88.8 | 78.5 | 85.1 | 90.4
4439.2 | 4218.2 | -6.8 | 0 | 0 | 83 | 80.5 | 76.6 | 76.3 | 90.9 | 26.2 | 21.4 | 32.3 | 1.2 | 219 | 5.3 | 398.2 | 392.9 | 81.8 | 39.4 | 492.1 | 495.7 | 62.4 | 50.3 | 174.5 | 196.1 | 82 | 65 | 129.7 | 80.2 | 70.8 | 149.7 | 131.4 | 96.4 | 84.4 | 80.2 | 90.3 | 88.7 | 78.4 | 85.1 | 90.4
4440.2 | 4219.2 | -6.8 | 0 | 0 | 83 | 80.8 | 76.5 | 76.3 | 90.5 | 26.2 | 21.4 | 32.3 | 1.2 | 223.2 | 5.1 | 398.1 | 392.8 | 81.7 | 39.4 | 492 | 495.5 | 62.4 | 50.3 | 174.4 | 195.9 | 82.5 | 64.9 | 129.6 | 80.1 | 70.7 | 149.6 | 131.3 | 96.3 | 84.4 | 80.1 | 90.2 | 88.7 | 78.4 | 85 | 90.3
4441.2 | 4220.2 | -6.8 | 0 | 0 | 83 | 81 | 76.5 | 76.3 | 90.4 | 26.3 | 21.4 | 32.3 | 1.2 | 211.2 | 5.2 | 398.1 | 392.8 | 81.7 | 39.4 | 491.9 | 495.4 | 62.6 | 50.4 | 174.2 | 195.7 | 82.8 | 64.8 | 129.6 | 80 | 70.4 | 149.5 | 131.2 | 96.3 | 84.4 | 80.1 | 90.2 | 88.6 | 78.3 | 84.9 | 90.3
4442.2 | 4221.2 | -6.8 | 0 | 0 | 83 | 81.2 | 76.5 | 76.3 | 90.5 | 26.3 | 21.4 | 32.3 | 1.3 | 225.4 | 4.9 | 398 | 392.8 | 81.2 | 39.3 | 491.9 | 495.3 | 63.1 | 50.7 | 174.2 | 195.5 | 83.1 | 64.6 | 129.5 | 79.6 | 70.2 | 149.4 | 131.1 | 96.2 | 84.4 | 80 | 90.2 | 88.6 | 78.3 | 84.9 | 90.3
4443.2 | 4222.2 | -6.8 | 0 | 0 | 83 | 81.2 | 76.6 | 76.2 | 90.4 | 26.3 | 21.4 | 32.3 | 1.2 | 228.8 | 4.5 | 398 | 392.7 | 80.9 | 39.3 | 491.8 | 495.2 | 63.2 | 50.9 | 174.2 | 195.3 | 83.7 | 64.5 | 129.4 | 79.3 | 70 | 149.3 | 131 | 96.2 | 84.4 | 80 | 90.1 | 88.6 | 78.3 | 84.9 | 90.2
4444.2 | 4223.2 | -6.7 | 0 | 0 | 83.1 | 81.1 | 76.5 | 76.1 | 90.4 | 26.4 | 21.4 | 32.4 | 0.9 | 216.6 | 4.6 | 398 | 392.7 | 80.1 | 39.3 | 491.7 | 495.1 | 63.6 | 51 | 174.2 | 195.1 | 83.9 | 64.5 | 129.3 | 79.1 | 69.6 | 149.2 | 131 | 96.1 | 84.3 | 79.9 | 90 | 88.6 | 78.3 | 84.8 | 90.2
4445.2 | 4224.2 | -6.7 | 0 | 0 | 83 | 80.8 | 76.4 | 76 | 90.5 | 26.5 | 21.4 | 32.4 | 0.9 | 219.2 | 4.5 | 397.9 | 392.6 | 79.4 | 39.2 | 491.6 | 495.1 | 63.6 | 50.8 | 174.1 | 195 | 84.1 | 64.5 | 129.2 | 79 | 69.4 | 149.1 | 130.8 | 96 | 84.3 | 79.8 | 90 | 88.5 | 78.3 | 84.8 | 90.1
4446.2 | 4225.2 | -6.7 | 0 | 0 | 82.8 | 80.7 | 76.4 | 76 | 90.5 | 26.5 | 21.4 | 32.5 | 0.9 | 224.1 | 4.1 | 397.9 | 392.6 | 79.8 | 39.2 | 491.6 | 495.1 | 63.3 | 50.6 | 174.1 | 194.8 | 84.4 | 64.6 | 129.1 | 79.1 | 69.3 | 149 | 130.7 | 96 | 84.3 | 79.7 | 89.9 | 88.5 | 78.3 | 84.8 | 90.1
4447.2 | 4226.2 | -6.7 | 0 | 0 | 82.6 | 80.7 | 76.3 | 76 | 90.5 | 26.6 | 21.4 | 32.5 | 0.8 | 224 | 3.6 | 397.8 | 392.5 | 79.6 | 39.1 | 491.5 | 495 | 62.7 | 50.5 | 174 | 194.6 | 84.8 | 64.7 | 129 | 79 | 69.2 | 148.9 | 130.6 | 95.9 | 84.2 | 79.7 | 89.9 | 88.5 | 78.2 | 84.8 | 90.1
4448.2 | 4227.2 | -6.8 | 0 | 0 | 82.6 | 80.6 | 76.3 | 75.9 | 90.5 | 26.7 | 21.4 | 32.5 | 0.8 | 225.1 | 3.3 | 397.8 | 392.5 | 79.2 | 39 | 491.5 | 495.1 | 62.1 | 50.4 | 173.9 | 194.4 | 84.7 | 64.7 | 128.9 | 78.9 | 69.4 | 148.7 | 130.6 | 95.9 | 84.2 | 79.6 | 89.9 | 88.4 | 78.2 | 84.8 | 90
4449.2 | 4228.2 | -6.8 | 0 | 0 | 82.7 | 80.4 | 76.2 | 75.8 | 90.5 | 26.7 | 21.4 | 32.5 | 0.7 | 230.7 | 3.1 | 397.8 | 392.4 | 78.7 | 39 | 491.4 | 495.1 | 61.6 | 50.5 | 173.9 | 194.2 | 84.7 | 64.7 | 128.8 | 78.8 | 69.5 | 148.6 | 130.5 | 95.9 | 84.2 | 79.6 | 89.8 | 88.4 | 78.1 | 84.8 | 90
4450.2 | 4229.2 | -6.8 | 0 | 0 | 82.9 | 80.2 | 76.1 | 75.8 | 90.5 | 26.7 | 21.4 | 32.5 | 0.7 | 224.5 | 3 | 397.7 | 392.4 | 78.5 | 38.9 | 491.3 | 495.2 | 60.9 | 50.5 | 173.8 | 194 | 85 | 64.7 | 128.7 | 78.6 | 69.6 | 148.5 | 130.4 | 95.8 | 84.2 | 79.5 | 89.7 | 88.3 | 78 | 84.8 | 90
4451.2 | 4230.2 | -6.8 | 0 | 0 | 82.9 | 80 | 75.9 | 75.8 | 90.5 | 26.6 | 21.4 | 32.6 | 0.7 | 222 | 2.9 | 397.7 | 392.4 | 78.6 | 38.8 | 491.2 | 495.2 | 60.5 | 50.3 | 173.7 | 193.8 | 84.7 | 64.7 | 128.6 | 78.2 | 69.9 | 148.4 | 130.3 | 95.7 | 84.1 | 79.4 | 89.7 | 88.3 | 78 | 84.8 | 89.9
4452.2 | 4231.2 | -6.8 | 0 | 0 | 83 | 79.9 | 75.7 | 75.8 | 90.5 | 26.5 | 21.4 | 32.6 | 0.9 | 230.9 | 2.6 | 397.7 | 392.3 | 78.9 | 38.7 | 491.2 | 495.1 | 60.3 | 50.3 | 173.7 | 193.6 | 84.3 | 64.5 | 128.5 | 78 | 70.1 | 148.3 | 130.4 | 95.7 | 84 | 79.4 | 89.7 | 88.2 | 78 | 84.8 | 89.9
4453.2 | 4232.2 | -6.8 | 0 | 0 | 83 | 80 | 75.5 | 75.9 | 90.5 | 26.5 | 21.4 | 32.7 | 1.1 | 242.5 | 2.4 | 397.6 | 392.2 | 79 | 38.7 | 491.2 | 495 | 60.1 | 50.2 | 173.6 | 193.4 | 84 | 64.5 | 128.4 | 77.7 | 70 | 148.2 | 130.2 | 95.7 | 84 | 79.4 | 89.7 | 88.2 | 78.1 | 84.7 | 89.9
4454.2 | 4233.2 | -6.8 | 0 | 0 | 82.8 | 80.1 | 75.5 | 76.1 | 90.4 | 26.4 | 21.4 | 32.7 | 1.1 | 250.5 | 2.2 | 397.6 | 392.2 | 79.1 | 38.7 | 491.2 | 494.9 | 60.8 | 50.2 | 173.5 | 193.2 | 84 | 64.4 | 128.4 | 77.7 | 69.9 | 148.1 | 130 | 95.6 | 84 | 79.4 | 89.7 | 88.2 | 78.1 | 84.7 | 89.8
4455.2 | 4234.2 | -6.8 | 0 | 0 | 82.5 | 80.1 | 75.4 | 76.3 | 90.3 | 26.5 | 21.4 | 32.7 | 1.2 | 247.3 | 2 | 397.5 | 392.2 | 79.1 | 38.6 | 491.2 | 494.7 | 60.4 | 50.1 | 173.5 | 193 | 84 | 64.4 | 128.3 | 77.8 | 70.1 | 147.9 | 130.1 | 95.6 | 83.9 | 79.4 | 89.7 | 88.1 | 78.1 | 84.7 | 89.8
4456.2 | 4235.2 | -6.8 | 0 | 0 | 82.4 | 80 | 75.4 | 76.4 | 90.4 | 26.5 | 21.4 | 32.8 | 1.1 | 242.2 | 2.3 | 397.5 | 392.1 | 79.3 | 38.6 | 491.3 | 494.5 | 60.6 | 50.2 | 173.5 | 192.8 | 84.2 | 64.4 | 128.2 | 77.9 | 70 | 147.8 | 130.2 | 95.6 | 83.9 | 79.3 | 89.6 | 88.1 | 78.1 | 84.7 | 89.7
4457.2 | 4236.2 | -6.8 | 0 | 0 | 82.4 | 79.9 | 75.4 | 76.5 | 90.6 | 26.5 | 21.4 | 32.8 | 1 | 236.3 | 2.8 | 397.5 | 392.1 | 79 | 38.5 | 491.2 | 494.3 | 60.3 | 50 | 173.4 | 192.6 | 84 | 64.5 | 128.2 | 77.9 | 69.9 | 147.7 | 130.2 | 95.5 | 83.7 | 79.2 | 89.5 | 88.1 | 78 | 84.6 | 89.7
4458.2 | 4237.2 | -6.8 | 0 | 0 | 82.5 | 79.9 | 75.1 | 76.3 | 90.6 | 26.5 | 21.4 | 32.8 | 1 | 239.7 | 3.1 | 397.4 | 392 | 78.5 | 38.1 | 491.3 | 494.2 | 59.8 | 49.4 | 173.2 | 192.4 | 84 | 64.4 | 128.1 | 77.6 | 69.4 | 147.6 | 130 | 95.4 | 83.6 | 79.2 | 89.5 | 88.1 | 78 | 84.6 | 89.7
4459.2 | 4238.2 | -6.8 | 0 | 0 | 82.5 | 80.1 | 74.8 | 75.8 | 90.4 | 26.4 | 21.4 | 32.7 | 1.1 | 241.2 | 3.2 | 397.4 | 392 | 78.3 | 37.8 | 491.3 | 494.1 | 59.4 | 48.8 | 173 | 192.2 | 84.3 | 64.1 | 128 | 77.1 | 68.7 | 147.5 | 129.8 | 95.4 | 83.5 | 79.2 | 89.5 | 88 | 77.9 | 84.6 | 89.6
4460.2 | 4239.2 | -6.8 | 0 | 0 | 80.6 | 80.2 | 74.8 | 75.5 | 90.2 | 26.3 | 21.4 | 32.8 | 1.1 | 241.2 | 3.2 | 397.4 | 391.9 | 77.6 | 37.6 | 491.3 | 493.9 | 59 | 48.3 | 173.1 | 192 | 84.8 | 64.2 | 128 | 77.2 | 68.7 | 147.4 | 129.8 | 95.3 | 83.4 | 79.2 | 89.5 | 88 | 77.9 | 84.5 | 89.6
4461.2 | 4240.2 | -6.8 | 0 | 0 | 77.1 | 80.3 | 75 | 75.5 | 90.2 | 26.3 | 21.4 | 32.8 | 1.1 | 243.5 | 3.3 | 397.3 | 391.9 | 77.2 | 37.7 | 491.3 | 493.9 | 58.6 | 48 | 173.2 | 191.9 | 84.9 | 64.3 | 127.9 | 77.4 | 68.9 | 147.3 | 129.8 | 95.2 | 83.4 | 79.1 | 89.4 | 88 | 77.9 | 84.5 | 89.6
4462.2 | 4241.2 | -6.8 | 0 | 0 | 76.2 | 80.3 | 75.1 | 75.5 | 90.3 | 26.4 | 21.4 | 32.8 | 1 | 241.3 | 3.3 | 397.3 | 391.8 | 76.7 | 37.4 | 491.3 | 494 | 58.2 | 47.6 | 173 | 191.7 | 85.1 | 64 | 127.8 | 77.8 | 68.4 | 147.1 | 129.7 | 95.2 | 83.3 | 79.1 | 89.4 | 87.9 | 77.7 | 84.5 | 89.5
4463.2 | 4242.2 | -6.8 | 0 | 0 | 76.5 | 80.3 | 75.1 | 74.9 | 90.3 | 26.5 | 21.4 | 32.7 | 1.1 | 238.5 | 3.2 | 397.3 | 391.8 | 76.7 | 37.1 | 491.3 | 493.9 | 57.7 | 46.9 | 172.8 | 191.5 | 85.3 | 63.8 | 127.8 | 77.1 | 67.9 | 147 | 129.7 | 95.2 | 83.3 | 79.1 | 89.3 | 87.9 | 77.5 | 84.3 | 89.5
4464.2 | 4243.2 | -6.8 | 0 | 0 | 76.8 | 80.2 | 75.1 | 73.5 | 90.3 | 26.5 | 21.4 | 32.7 | 1.2 | 236.4 | 3.2 | 397.2 | 391.7 | 76.2 | 36.9 | 491.3 | 493.9 | 57.1 | 46.9 | 172.7 | 191.3 | 85.2 | 63.4 | 127.7 | 76.5 | 67.7 | 146.9 | 129.5 | 95.2 | 83.2 | 79.1 | 89.2 | 87.9 | 77.4 | 84.3 | 89.4
4465.2 | 4244.2 | -6.8 | 0 | 0 | 76.6 | 79.9 | 75.1 | 72.9 | 90.2 | 26.4 | 21.4 | 32.7 | 1 | 240.9 | 3.2 | 397.2 | 391.7 | 76.1 | 36.9 | 491.1 | 494 | 57.3 | 47.1 | 172.5 | 191.1 | 84.7 | 63 | 127.6 | 76.3 | 67.9 | 146.8 | 129.4 | 95.1 | 83.1 | 79.1 | 89.2 | 87.9 | 77.4 | 84.2 | 89.4
4466.2 | 4245.2 | -6.8 | 0 | 0 | 75 | 79.3 | 75.2 | 73.3 | 90.3 | 26.3 | 21.4 | 32.6 | 1.2 | 247.6 | 3.3 | 397.2 | 391.6 | 76.3 | 36.9 | 490.9 | 493.9 | 57.8 | 47.3 | 172.5 | 190.9 | 84.3 | 62.8 | 127.6 | 76.5 | 68 | 146.7 | 129.3 | 95.1 | 83.1 | 79.1 | 89.2 | 87.8 | 77.5 | 84.1 | 89.4
4467.2 | 4246.2 | -6.8 | 0 | 0 | 73.6 | 78.6 | 75.3 | 73.7 | 90.5 | 26.2 | 21.4 | 32.4 | 1 | 235.3 | 3.1 | 397.1 | 391.6 | 77.1 | 37.2 | 490.8 | 493.9 | 57.6 | 47.5 | 172.5 | 190.7 | 84.1 | 62.9 | 127.5 | 76.5 | 68 | 146.6 | 129.3 | 95.1 | 83 | 79 | 89.2 | 87.8 | 77.5 | 84.1 | 89.3
4468.2 | 4247.2 | -6.8 | 0 | 0 | 74.1 | 78.2 | 75.2 | 74 | 90.5 | 26.2 | 21.4 | 32.3 | 1.1 | 216.9 | 2.8 | 397.1 | 391.5 | 77.4 | 37.4 | 490.7 | 493.8 | 57.3 | 47.7 | 172.4 | 190.5 | 83.9 | 62.9 | 127.4 | 76.2 | 68 | 146.4 | 129.2 | 95 | 82.9 | 78.8 | 89.1 | 87.7 | 77.4 | 84.1 | 89.3
4469.2 | 4248.2 | -6.8 | 0 | 0 | 74.5 | 78.3 | 75.2 | 73.9 | 90.5 | 26.2 | 21.4 | 32.2 | 1 | 210.3 | 2.7 | 397 | 391.5 | 76.8 | 37.3 | 490.6 | 493.8 | 56.6 | 47.6 | 172.3 | 190.4 | 84.4 | 62.7 | 127.4 | 75.6 | 67.7 | 146.3 | 129.2 | 95 | 82.7 | 78.5 | 88.9 | 87.7 | 77.3 | 84 | 89.2
4470.2 | 4249.2 | -6.8 | 0 | 0 | 75 | 78.3 | 75.1 | 73.3 | 90.4 | 26.1 | 21.4 | 32.1 | 1 | 211.8 | 2.5 | 397 | 391.4 | 75.9 | 37.1 | 490.5 | 493.9 | 55.9 | 47.9 | 172 | 190.2 | 84.2 | 62.6 | 127.3 | 75 | 67.6 | 146.2 | 129.1 | 94.9 | 82.6 | 78.2 | 88.8 | 87.7 | 77.3 | 83.9 | 89.2
4471.2 | 4250.2 | -6.8 | 0 | 0 | 75.3 | 78.1 | 74.8 | 73 | 90.4 | 26.1 | 21.4 | 31.9 | 1 | 225.9 | 2.4 | 396.9 | 391.4 | 75.5 | 37.2 | 490.3 | 494.2 | 55.5 | 47.2 | 171.8 | 190 | 84.1 | 62.5 | 127.3 | 75.3 | 68 | 146.1 | 129.1 | 94.8 | 82.3 | 78 | 88.7 | 87.7 | 77.4 | 83.9 | 89.2
4472.2 | 4251.2 | -6.8 | 0 | 0 | 75.1 | 77.9 | 74.2 | 72.5 | 90.4 | 26.2 | 21.4 | 31.8 | 0.8 | 247.3 | 2.7 | 396.9 | 391.4 | 75.4 | 36.9 | 490.2 | 494.4 | 55.4 | 46.5 | 171.5 | 189.8 | 84.4 | 62.1 | 127.2 | 75.5 | 67.8 | 146 | 129 | 94.7 | 82.2 | 77.9 | 88.7 | 87.6 | 77.4 | 83.8 | 89.1

## First Electrical Failures
First electrical failures observed for the two cables present extracted from the corresponding IRMS and SCDU data files
Location G: SCDU-3, single 7/C PVC/PVC |  |  | Location A: SCDU-1, 12-Cable all XLPE/CSPE Bundle, Inter-Cable |  |  | Location A: SCDU-2, Mixed 12-cable bundle, inter-cable configuration, Grounded |  |  |  | Location C: SCDU-4 Mixed 6-cable bundle, inter-cable configuration, XLPE and PE/PVC cables as source
Time (s) | Offset Time (s) | C3 V1 | Time (s) | Offset Time (s) | C1 V6 | Time (s) | Offset Time (s) | C1 V1 | C1 V6 | Time (s) | Offset Time (s) | C4 V1
0 | -221 | 130.5244 | 0 | -221 | 0.28424 | 0 | -221 | 132.5735 | 0.28848 | 0 | -221 | 127.0709
10 | -211 | 130.4284 | 10 | -211 | 0.28424 | 60 | -161 | 132.3787 | 0.19109 | 10 | -211 | 127.0709
20 | -201 | 130.4284 | 20 | -201 | 0.18829 | 120 | -101 | 132.7683 | 0.48328 | 20 | -201 | 126.9749
30 | -191 | 130.3325 | 30 | -191 | 0.28424 | 180 | -41 | 132.6709 | 0.38586 | 30 | -191 | 126.9749
40 | -181 | 130.2365 | 40 | -181 | 0.28424 | 240 | 19 | 132.4761 | 0.28848 | 40 | -181 | 126.879
50 | -171 | 130.1405 | 50 | -171 | 0.28424 | 300 | 79 | 132.3787 | 0.38586 | 50 | -171 | 126.687
60 | -161 | 130.1405 | 60 | -161 | 0.28424 | 330 | 109 | 132.6709 | 0.48328 | 60 | -161 | 126.687
70 | -151 | 129.7567 | 70 | -151 | 0.38019 | 350 | 129 | 132.0865 | 0.38586 | 70 | -151 | 126.3032
80 | -141 | 129.7567 | 80 | -141 | 0.38019 | 360 | 139 | 131.8917 | 0.28848 | 80 | -141 | 126.3991
90 | -131 | 129.6607 | 90 | -131 | 0.38019 | 360.2 | 139.2 | 132.0865 | 0.28848 | 90 | -131 | 126.2072
100 | -121 | 129.7567 | 100 | -121 | 0.47618 | 360.4 | 139.4 | 131.7944 | 0.38586 | 100 | -121 | 126.3032
110 | -111 | 129.8526 | 110 | -111 | 0.57213 | 360.6 | 139.6 | 131.7944 | 0.28848 | 110 | -111 | 126.3991
120 | -101 | 129.8526 | 120 | -101 | 0.47618 | 360.8 | 139.8 | 131.7944 | 0.38586 | 120 | -101 | 126.3032
130 | -91 | 130.0446 | 130 | -91 | 0.66813 | 361 | 140 | 131.8917 | 0.38586 | 130 | -91 | 126.4951
140 | -81 | 129.8526 | 140 | -81 | 0.57213 | 361.2 | 140.2 | 131.8917 | 0.77546 | 140 | -81 | 126.4951
150 | -71 | 129.6607 | 150 | -71 | 0.38019 | 361.4 | 140.4 | 131.6969 | 0.38586 | 150 | -71 | 126.3032
160 | -61 | 129.6607 | 160 | -61 | 0.38019 | 361.6 | 140.6 | 131.8917 | 0.38586 | 160 | -61 | 126.1112
170 | -51 | 129.9486 | 170 | -51 | 0.38019 | 361.8 | 140.8 | 131.9892 | 0.38586 | 170 | -51 | 126.4951
180 | -41 | 130.1405 | 180 | -41 | 0.28424 | 362 | 141 | 131.7944 | 0.48328 | 180 | -41 | 126.5911
190 | -31 | 130.1405 | 190 | -31 | 0.28424 | 362.2 | 141.2 | 131.8917 | 0.38586 | 190 | -31 | 126.687
200 | -21 | 129.9486 | 200 | -21 | 0.38019 | 362.4 | 141.4 | 131.8917 | 0.38586 | 200 | -21 | 126.5911
210 | -11 | 129.9486 | 210 | -11 | 0.28424 | 362.6 | 141.6 | 131.8917 | 0.38586 | 210 | -11 | 126.4951
220 | -1 | 129.8526 | 220 | -1 | 0.28424 | 362.8 | 141.8 | 131.6969 | 0.38586 | 220 | -1 | 126.3991
230 | 9 | 129.7567 | 230 | 9 | 0.28424 | 363 | 142 | 131.7944 | 0.28848 | 230 | 9 | 126.3032
240 | 19 | 129.5647 | 240 | 19 | 0.38019 | 363.2 | 142.2 | 131.9892 | 0.38586 | 240 | 19 | 126.0153
250 | 29 | 129.4687 | 250 | 29 | 0.47618 | 363.4 | 142.4 | 131.7944 | 0.38586 | 250 | 29 | 126.0153
260 | 39 | 129.7567 | 260 | 39 | 0.66813 | 363.6 | 142.6 | 131.8917 | 0.38586 | 260 | 39 | 126.3032
270 | 49 | 129.9486 | 270 | 49 | 0.66813 | 363.8 | 142.8 | 131.8917 | 0.67808 | 270 | 49 | 126.4951
270.2 | 49.2 | 129.9486 | 270.2 | 49.2 | 0.76408 | 364 | 143 | 131.6969 | 0.19109 | 270.2 | 49.2 | 126.4951
270.4 | 49.4 | 129.9486 | 270.4 | 49.4 | 0.66813 | 364.2 | 143.2 | 131.6969 | 0.38586 | 270.4 | 49.4 | 126.3991
270.6 | 49.6 | 129.9486 | 270.6 | 49.6 | 0.76408 | 364.4 | 143.4 | 131.6969 | 0.28848 | 270.6 | 49.6 | 126.3991
270.8 | 49.8 | 129.8526 | 270.8 | 49.8 | 0.76408 | 364.6 | 143.6 | 131.5996 | 0.19109 | 270.8 | 49.8 | 126.4951
271 | 50 | 129.9486 | 271 | 50 | 0.76408 | 364.8 | 143.8 | 131.0152 | 0.48328 | 271 | 50 | 126.4951
271.2 | 50.2 | 129.9486 | 271.2 | 50.2 | 0.76408 | 365 | 144 | 130.8204 | 0.58066 | 271.2 | 50.2 | 126.4951
271.4 | 50.4 | 129.9486 | 271.4 | 50.4 | 0.76408 | 365.2 | 144.2 | 131.5996 | 0.97026 | 271.4 | 50.4 | 126.4951
271.6 | 50.6 | 129.9486 | 271.6 | 50.6 | 0.76408 | 365.4 | 144.4 | 130.8204 | 1.2624 | 271.6 | 50.6 | 126.4951
271.8 | 50.8 | 129.9486 | 271.8 | 50.8 | 0.66813 | 365.6 | 144.6 | 130.6256 | 5.6453 | 271.8 | 50.8 | 126.4951
272 | 51 | 129.8526 | 272 | 51 | 0.66813 | 365.8 | 144.8 | 130.1386 | 7.5932 | 272 | 51 | 126.3991
272.2 | 51.2 | 129.9486 | 272.2 | 51.2 | 0.76408 | 366 | 145 | 129.1647 | 26.5855 | 272.2 | 51.2 | 126.4951
272.4 | 51.4 | 129.9486 | 272.4 | 51.4 | 0.76408 | 366.2 | 145.2 | 121.3729 | 13.924 | 272.4 | 51.4 | 126.3991
272.6 | 51.6 | 129.9486 | 272.6 | 51.6 | 0.57213 | 366.4 | 145.4 | 129.4568 | 31.358 | 272.6 | 51.6 | 126.4951
272.8 | 51.8 | 129.9486 | 272.8 | 51.8 | 0.66813 | 366.6 | 145.6 | 127.9959 | 52.493 | 272.8 | 51.8 | 126.4951
273 | 52 | 129.9486 | 273 | 52 | 0.66813 | 366.8 | 145.8 | 127.9959 | 64.5702 | 273 | 52 | 126.4951
273.2 | 52.2 | 129.9486 | 273.2 | 52.2 | 0.66813 | 367 | 146 | 128.5803 | 44.7987 | 273.2 | 52.2 | 126.4951
273.4 | 52.4 | 129.9486 | 273.4 | 52.4 | 0.76408 | 367.2 | 146.2 | 127.0219 | 48.1102 | 273.4 | 52.4 | 126.3991
273.6 | 52.6 | 129.9486 | 273.6 | 52.6 | 0.66813 | 367.4 | 146.4 | 126.3401 | 52.006 | 273.6 | 52.6 | 126.4951
273.8 | 52.8 | 129.8526 | 273.8 | 52.8 | 0.66813 | 367.6 | 146.6 | 127.4115 | 45.3831 | 273.8 | 52.8 | 126.4951
274 | 53 | 129.8526 | 274 | 53 | 0.66813 | 367.8 | 146.8 | 126.6323 | 50.6425 | 274 | 53 | 126.3991
274.2 | 53.2 | 129.9486 | 274.2 | 53.2 | 0.66813 | 368 | 147 | 125.9505 | 83.7573 | 274.2 | 53.2 | 126.4951
274.4 | 53.4 | 129.9486 | 274.4 | 53.4 | 0.66813 | 368.2 | 147.2 | 126.7297 | 81.712 | 274.4 | 53.4 | 126.4951
274.6 | 53.6 | 129.8526 | 274.6 | 53.6 | 0.76408 | 368.4 | 147.4 | 125.4636 | 80.251 | 274.6 | 53.6 | 126.4951
274.8 | 53.8 | 129.8526 | 274.8 | 53.8 | 0.66813 | 368.6 | 147.6 | 121.8599 | 96.3215 | 274.8 | 53.8 | 126.3991
275 | 54 | 129.8526 | 275 | 54 | 0.66813 | 368.8 | 147.8 | 121.5677 | 99.7303 | 275 | 54 | 126.3991
275.2 | 54.2 | 129.8526 | 275.2 | 54.2 | 0.66813 | 369 | 148 | 122.3469 | 107.9116 | 275.2 | 54.2 | 126.4951
275.4 | 54.4 | 129.8526 | 275.4 | 54.4 | 0.66813 | 369.2 | 148.2 | 122.5417 | 107.7168 | 275.4 | 54.4 | 126.3991
275.6 | 54.6 | 129.8526 | 275.6 | 54.6 | 0.66813 | 369.4 | 148.4 | 125.6584 | 114.9242 | 275.6 | 54.6 | 126.3991
275.8 | 54.8 | 129.7567 | 275.8 | 54.8 | 0.57213 | 369.6 | 148.6 | 125.3662 | 116.2877 | 275.8 | 54.8 | 126.3991
276 | 55 | 129.7567 | 276 | 55 | 0.66813 | 369.8 | 148.8 | 124.0026 | 116.2877 | 276 | 55 | 126.3032
276.2 | 55.2 | 129.7567 | 276.2 | 55.2 | 0.57213 | 370 | 149 | 125.6584 | 120.6706 | 276.2 | 55.2 | 126.3991
276.4 | 55.4 | 129.8526 | 276.4 | 55.4 | 0.66813 | 370.2 | 149.2 | 126.1453 | 121.5472 | 276.4 | 55.4 | 126.3991
276.6 | 55.6 | 129.8526 | 276.6 | 55.6 | 0.57213 | 370.4 | 149.4 | 125.3662 | 119.307 | 276.6 | 55.6 | 126.3991
276.8 | 55.8 | 129.8526 | 276.8 | 55.8 | 0.57213 | 370.6 | 149.6 | 124.6844 | 116.8721 | 276.8 | 55.8 | 126.3991
277 | 56 | 129.8526 | 277 | 56 | 0.57213 | 370.8 | 149.8 | 123.9052 | 116.0929 | 277 | 56 | 126.3991
277.2 | 56.2 | 129.7567 | 277.2 | 56.2 | 0.66813 | 371 | 150 | 123.7104 | 116.2877 | 277.2 | 56.2 | 126.3032
277.4 | 56.4 | 129.7567 | 277.4 | 56.4 | 0.66813 | 371.2 | 150.2 | 124.1974 | 116.5799 | 277.4 | 56.4 | 126.3032
277.6 | 56.6 | 129.7567 | 277.6 | 56.6 | 0.66813 | 371.4 | 150.4 | 118.451 | 116.6773 | 277.6 | 56.6 | 126.3032
277.8 | 56.8 | 129.7567 | 277.8 | 56.8 | 0.57213 | 371.6 | 150.6 | 122.5417 | 117.2617 | 277.8 | 56.8 | 126.3032
278 | 57 | 129.6607 | 278 | 57 | 0.57213 | 371.8 | 150.8 | 122.5417 | 116.3851 | 278 | 57 | 126.2072
278.2 | 57.2 | 129.7567 | 278.2 | 57.2 | 0.57213 | 372 | 151 | 119.2302 | 113.5606 | 278.2 | 57.2 | 126.3032
278.4 | 57.4 | 129.7567 | 278.4 | 57.4 | 0.57213 | 372.2 | 151.2 | 117.8667 | 108.8856 | 278.4 | 57.4 | 126.3032
278.6 | 57.6 | 129.7567 | 278.6 | 57.6 | 0.57213 | 372.4 | 151.4 | 116.6979 | 110.2492 | 278.6 | 57.6 | 126.3032
278.8 | 57.8 | 129.7567 | 278.8 | 57.8 | 0.66813 | 372.6 | 151.6 | 117.3797 | 111.0283 | 278.8 | 57.8 | 126.3032
279 | 58 | 129.7567 | 279 | 58 | 0.57213 | 372.8 | 151.8 | 119.912 | 114.4372 | 279 | 58 | 126.2072
279.2 | 58.2 | 129.6607 | 279.2 | 58.2 | 0.47618 | 373 | 152 | 123.7104 | 118.9175 | 279.2 | 58.2 | 126.2072
279.4 | 58.4 | 129.6607 | 279.4 | 58.4 | 0.57213 | 373.2 | 152.2 | 121.8599 | 116.8721 | 279.4 | 58.4 | 126.2072
279.6 | 58.6 | 129.6607 | 279.6 | 58.6 | 0.47618 | 373.4 | 152.4 | 123.9052 | 118.82 | 279.6 | 58.6 | 126.2072
279.8 | 58.8 | 129.6607 | 279.8 | 58.8 | 0.57213 | 373.6 | 152.6 | 124.0026 | 120.1836 | 279.8 | 58.8 | 126.2072
280 | 59 | 129.5647 | 280 | 59 | 0.47618 | 373.8 | 152.8 | 122.8339 | 119.2096 | 280 | 59 | 126.1112
280.2 | 59.2 | 129.5647 | 280.2 | 59.2 | 0.57213 | 374 | 153 | 121.9573 | 116.5799 | 280.2 | 59.2 | 126.1112
280.4 | 59.4 | 129.5647 | 280.4 | 59.4 | 0.47618 | 374.2 | 153.2 | 123.0287 | 119.794 | 280.4 | 59.4 | 126.1112
280.6 | 59.6 | 129.6607 | 280.6 | 59.6 | 0.47618 | 374.4 | 153.4 | 122.1521 | 118.9175 | 280.6 | 59.6 | 126.1112
280.8 | 59.8 | 129.6607 | 280.8 | 59.8 | 0.47618 | 374.6 | 153.6 | 118.0615 | 104.5028 | 280.8 | 59.8 | 126.1112
281 | 60 | 129.5647 | 281 | 60 | 0.47618 | 374.8 | 153.8 | 119.2302 | 72.3619 | 281 | 60 | 126.1112
281.2 | 60.2 | 129.6607 | 281.2 | 60.2 | 0.47618 | 375 | 154 | 121.8599 | 72.1671 | 281.2 | 60.2 | 126.2072
281.4 | 60.4 | 129.5647 | 281.4 | 60.4 | 0.47618 | 375.2 | 154.2 | 119.912 | 60.8691 | 281.4 | 60.4 | 126.1112
281.6 | 60.6 | 129.5647 | 281.6 | 60.6 | 0.38019 | 375.4 | 154.4 | 118.938 | 55.9993 | 281.6 | 60.6 | 126.1112
281.8 | 60.8 | 129.5647 | 281.8 | 60.8 | 0.38019 | 375.6 | 154.6 | 118.8406 | 45.0909 | 281.8 | 60.8 | 126.1112
282 | 61 | 129.4687 | 282 | 61 | 0.47618 | 375.8 | 154.8 | 119.425 | 45.4804 | 282 | 61 | 126.0153
282.2 | 61.2 | 129.5647 | 282.2 | 61.2 | 0.38019 | 376 | 155 | 121.6651 | 69.3426 | 282.2 | 61.2 | 126.1112
282.4 | 61.4 | 129.5647 | 282.4 | 61.4 | 0.38019 | 376.2 | 155.2 | 121.9573 | 67.2973 | 282.4 | 61.4 | 126.1112
282.6 | 61.6 | 129.5647 | 282.6 | 61.6 | 0.38019 | 376.4 | 155.4 | 118.1588 | 64.8624 | 282.6 | 61.6 | 126.1112
282.8 | 61.8 | 129.5647 | 282.8 | 61.8 | 0.47618 | 376.6 | 155.6 | 119.0354 | 58.142 | 282.8 | 61.8 | 126.1112
283 | 62 | 129.5647 | 283 | 62 | 0.38019 | 376.8 | 155.8 | 117.5745 | 66.9077 | 283 | 62 | 126.1112
283.2 | 62.2 | 129.5647 | 283.2 | 62.2 | 0.38019 | 377 | 156 | 117.8667 | 63.304 | 283.2 | 62.2 | 126.1112
283.4 | 62.4 | 129.5647 | 283.4 | 62.4 | 0.38019 | 377.2 | 156.2 | 115.7239 | 64.765 | 283.4 | 62.4 | 126.0153
283.6 | 62.6 | 129.5647 | 283.6 | 62.6 | 0.38019 | 377.4 | 156.4 | 123.7104 | 81.9067 | 283.6 | 62.6 | 126.0153
283.8 | 62.8 | 129.4687 | 283.8 | 62.8 | 0.38019 | 377.6 | 156.6 | 123.5156 | 87.0688 | 283.8 | 62.8 | 126.1112
284 | 63 | 129.5647 | 284 | 63 | 0.38019 | 377.8 | 156.8 | 125.2688 | 90.5751 | 284 | 63 | 126.0153
284.2 | 63.2 | 129.5647 | 284.2 | 63.2 | 0.38019 | 378 | 157 | 124.3922 | 89.3089 | 284.2 | 63.2 | 126.0153
284.4 | 63.4 | 129.5647 | 284.4 | 63.4 | 0.38019 | 378.2 | 157.2 | 123.6131 | 88.0427 | 284.4 | 63.4 | 126.1112
284.6 | 63.6 | 129.4687 | 284.6 | 63.6 | 0.38019 | 378.4 | 157.4 | 127.8011 | 103.9184 | 284.6 | 63.6 | 126.0153
284.8 | 63.8 | 129.4687 | 284.8 | 63.8 | 0.38019 | 378.6 | 157.6 | 126.6323 | 104.8923 | 284.8 | 63.8 | 126.1112
285 | 64 | 129.5647 | 285 | 64 | 0.38019 | 378.8 | 157.8 | 126.8271 | 118.4305 | 285 | 64 | 126.1112
285.2 | 64.2 | 129.5647 | 285.2 | 64.2 | 0.38019 | 379 | 158 | 127.8985 | 122.5211 | 285.2 | 64.2 | 126.0153
285.4 | 64.4 | 129.5647 | 285.4 | 64.4 | 0.38019 | 379.2 | 158.2 | 128.4829 | 123.5925 | 285.4 | 64.4 | 126.1112
285.6 | 64.6 | 129.5647 | 285.6 | 64.6 | 0.38019 | 379.4 | 158.4 | 128.6777 | 122.2289 | 285.6 | 64.6 | 126.1112
285.8 | 64.8 | 129.5647 | 285.8 | 64.8 | 0.38019 | 379.6 | 158.6 | 129.6516 | 122.3263 | 285.8 | 64.8 | 126.0153
286 | 65 | 129.5647 | 286 | 65 | 0.28424 | 379.8 | 158.8 | 127.7037 | 122.4237 | 286 | 65 | 126.0153
286.2 | 65.2 | 126.014 | 286.2 | 65.2 | 0.28424 | 380 | 159 | 123.3208 | 120.6706 | 286.2 | 65.2 | 122.6564
286.4 | 65.4 | 129.3728 | 286.4 | 65.4 | 0.38019 | 380.2 | 159.2 | 129.262 | 121.4497 | 286.4 | 65.4 | 125.9193
286.6 | 65.6 | 129.5647 | 286.6 | 65.6 | 0.38019 | 380.4 | 159.4 | 129.6516 | 118.4305 | 286.6 | 65.6 | 126.1112
286.8 | 65.8 | 129.6607 | 286.8 | 65.8 | 0.38019 | 380.6 | 159.6 | 128.8725 | 118.9175 | 286.8 | 65.8 | 126.1112
287 | 66 | 129.6607 | 287 | 66 | 0.38019 | 380.8 | 159.8 | 127.3141 | 113.8528 | 287 | 66 | 126.1112
287.2 | 66.2 | 129.5647 | 287.2 | 66.2 | 0.38019 | 381 | 160 | 126.6323 | 112.6841 | 287.2 | 66.2 | 126.1112
287.4 | 66.4 | 129.5647 | 287.4 | 66.4 | 0.38019 | 381.2 | 160.2 | 129.0672 | 121.255 | 287.4 | 66.4 | 126.2072
287.6 | 66.6 | 129.5647 | 287.6 | 66.6 | 0.38019 | 381.4 | 160.4 | 129.749 | 123.3003 | 287.6 | 66.6 | 126.1112
287.8 | 66.8 | 129.6607 | 287.8 | 66.8 | 0.38019 | 381.6 | 160.6 | 128.9699 | 118.5279 | 287.8 | 66.8 | 126.2072
288 | 67 | 129.6607 | 288 | 67 | 0.38019 | 381.8 | 160.8 | 129.0672 | 120.768 | 288 | 67 | 126.1112
288.2 | 67.2 | 129.6607 | 288.2 | 67.2 | 0.47618 | 382 | 161 | 128.7751 | 118.82 | 288.2 | 67.2 | 126.2072
288.4 | 67.4 | 129.6607 | 288.4 | 67.4 | 0.28424 | 382.2 | 161.2 | 128.7751 | 119.8914 | 288.4 | 67.4 | 126.2072
288.6 | 67.6 | 129.6607 | 288.6 | 67.6 | 0.38019 | 382.4 | 161.4 | 127.4115 | 97.5876 | 288.6 | 67.6 | 126.2072
288.8 | 67.8 | 129.6607 | 288.8 | 67.8 | 0.38019 | 382.6 | 161.6 | 127.9959 | 117.3591 | 288.8 | 67.8 | 126.2072
289 | 68 | 129.6607 | 289 | 68 | 0.38019 | 382.8 | 161.8 | 128.4829 | 120.3784 | 289 | 68 | 126.2072
289.2 | 68.2 | 129.7567 | 289.2 | 68.2 | 0.38019 | 383 | 162 | 127.8985 | 115.3138 | 289.2 | 68.2 | 126.2072
289.4 | 68.4 | 129.6607 | 289.4 | 68.4 | 0.38019 | 383.2 | 162.2 | 129.0672 | 108.7882 | 289.4 | 68.4 | 126.2072
289.6 | 68.6 | 129.6607 | 289.6 | 68.6 | 0.28424 | 383.4 | 162.4 | 129.1647 | 104.8923 | 289.6 | 68.6 | 126.2072
289.8 | 68.8 | 129.6607 | 289.8 | 68.8 | 0.38019 | 383.6 | 162.6 | 129.5542 | 102.2626 | 289.8 | 68.8 | 126.2072
290 | 69 | 129.6607 | 290 | 69 | 0.38019 | 383.8 | 162.8 | 129.6516 | 99.6329 | 290 | 69 | 126.2072
300 | 79 | 129.8526 | 300 | 79 | 0.38019 | 384 | 163 | 129.749 | 102.2626 | 300 | 79 | 126.3991
310 | 89 | 130.0446 | 310 | 89 | 0.47618 | 384.2 | 163.2 | 127.3141 | 116.9695 | 310 | 89 | 126.5911
320 | 99 | 129.9486 | 320 | 99 | 0.38019 | 384.4 | 163.4 | 111.7307 | 107.9116 | 320 | 99 | 126.4951
330 | 109 | 129.7567 | 330 | 109 | 0.38019 | 384.6 | 163.6 | 127.0219 | 105.9637 | 330 | 109 | 126.3032
340 | 119 | 129.7567 | 340 | 119 | 0.47618 | 384.8 | 163.8 | 130.236 | 107.522 | 340 | 119 | 126.3032
350 | 129 | 129.7567 | 350 | 129 | 0.47618 | 385 | 164 | 130.0412 | 103.9184 | 350 | 129 | 126.2072
360 | 139 | 129.8526 | 360 | 139 | 0.38019 | 385.2 | 164.2 | 127.8011 | 105.1846 | 360 | 139 | 126.3991
370 | 149 | 129.9486 | 370 | 149 | 0.28424 | 385.4 | 164.4 | 127.8985 | 86.6792 | 370 | 149 | 126.3991
380 | 159 | 129.8526 | 380 | 159 | 0.47618 | 385.6 | 164.6 | 125.1714 | 91.4516 | 380 | 159 | 126.3991
390 | 169 | 129.7567 | 390 | 169 | 0.38019 | 385.8 | 164.8 | 128.5803 | 92.1334 | 390 | 169 | 126.3032
400 | 179 | 129.8526 | 400 | 179 | 0.38019 | 386 | 165 | 129.0672 | 96.1267 | 400 | 179 | 126.3032
410 | 189 | 129.8526 | 410 | 189 | 0.38019 | 386.2 | 165.2 | 130.0412 | 106.7429 | 410 | 189 | 126.3991
420 | 199 | 129.7567 | 420 | 199 | 0.47618 | 386.4 | 165.4 | 130.723 | 102.0679 | 420 | 199 | 126.3991
430 | 209 | 129.8526 | 430 | 209 | 0.47618 | 386.6 | 165.6 | 129.1647 | 89.1141 | 430 | 209 | 126.3032
440 | 219 | 129.7567 | 440 | 219 | 0.47618 | 386.8 | 165.8 | 124.8792 | 61.6483 | 440 | 219 | 126.3032
450 | 229 | 129.7567 | 450 | 229 | 0.66813 | 387 | 166 | 126.6323 | 56.8759 | 450 | 229 | 126.2072
460 | 239 | 129.7567 | 460 | 239 | 0.86003 | 387.2 | 166.2 | 125.3662 | 55.9993 | 460 | 239 | 126.3032
470 | 249 | 129.8526 | 470 | 249 | 0.86003 | 387.4 | 166.4 | 125.8532 | 62.1353 | 470 | 249 | 126.3991
480 | 259 | 129.8526 | 480 | 259 | 1.052 | 387.6 | 166.6 | 127.1193 | 82.0042 | 480 | 259 | 126.3032
490 | 269 | 129.9486 | 490 | 269 | 0.95602 | 387.8 | 166.8 | 129.0672 | 97.5876 | 490 | 269 | 126.3991
500 | 279 | 129.9486 | 500 | 279 | 1.148 | 388 | 167 | 130.3334 | 109.7622 | 500 | 279 | 126.4951
510 | 289 | 130.2365 | 510 | 289 | 1.148 | 388.2 | 167.2 | 130.9178 | 114.632 | 510 | 289 | 126.879
520 | 299 | 130.0446 | 520 | 299 | 1.2439 | 388.4 | 167.4 | 130.9178 | 119.5018 | 520 | 299 | 126.5911
530 | 309 | 130.1405 | 530 | 309 | 1.148 | 388.6 | 167.6 | 124.4896 | 104.6975 | 530 | 309 | 126.687
540 | 319 | 129.9486 | 540 | 319 | 1.052 | 388.8 | 167.8 | 130.5282 | 112.4893 | 540 | 319 | 126.4951
550 | 329 | 129.8526 | 550 | 329 | 0.66813 | 389 | 168 | 131.1126 | 121.9367 | 550 | 329 | 126.3991
560 | 339 | 129.8526 | 560 | 339 | 0.38019 | 389.2 | 168.2 | 129.749 | 113.0736 | 560 | 339 | 126.3991
570 | 349 | 130.0446 | 570 | 349 | 1.148 | 389.4 | 168.4 | 131.1126 | 119.8914 | 570 | 349 | 126.4951
580 | 359 | 130.1405 | 580 | 359 | 1.4359 | 389.6 | 168.6 | 128.8725 | 102.1652 | 580 | 359 | 126.5911
590 | 369 | 130.2365 | 590 | 369 | 1.5318 | 389.8 | 168.8 | 128.2881 | 81.0302 | 590 | 369 | 126.783
600 | 379 | 130.2365 | 600 | 379 | 1.4359 | 390 | 169 | 126.048 | 82.5885 | 600 | 379 | 126.687
610 | 389 | 130.2365 | 610 | 389 | 1.6278 | 390.2 | 169.2 | 127.8011 | 88.9193 | 610 | 389 | 126.783
620 | 399 | 130.2365 | 620 | 399 | 1.3399 | 390.4 | 169.4 | 129.6516 | 107.522 | 620 | 399 | 126.687
630 | 409 | 130.1405 | 630 | 409 | 1.5318 | 390.6 | 169.6 | 130.5282 | 115.5086 | 630 | 409 | 126.5911
640 | 419 | 129.9486 | 640 | 419 | 1.4359 | 390.8 | 169.8 | 130.723 | 115.4112 | 640 | 419 | 126.3991
650 | 429 | 130.0446 | 650 | 429 | 1.5318 | 391 | 170 | 129.9438 | 94.2761 | 650 | 429 | 126.5911
660 | 439 | 130.0446 | 660 | 439 | 1.5318 | 391.2 | 170.2 | 130.1386 | 104.795 | 660 | 439 | 126.4951
670 | 449 | 130.0446 | 670 | 449 | 1.5318 | 391.4 | 170.4 | 130.3334 | 103.1392 | 670 | 449 | 126.5911
680 | 459 | 130.0446 | 680 | 459 | 1.5318 | 391.6 | 170.6 | 130.236 | 103.5288 | 680 | 459 | 126.4951
690 | 469 | 129.8526 | 690 | 469 | 1.2439 | 391.8 | 170.8 | 129.0672 | 100.9965 | 690 | 469 | 126.3032
700 | 479 | 129.8526 | 700 | 479 | 0.76408 | 392 | 171 | 130.236 | 113.3659 | 700 | 479 | 126.2072
710 | 489 | 129.9486 | 710 | 489 | 1.3399 | 392.2 | 171.2 | 129.1647 | 106.6455 | 710 | 489 | 126.3991
720 | 499 | 130.0446 | 720 | 499 | 1.4359 | 392.4 | 171.4 | 129.8464 | 115.5086 | 720 | 499 | 126.687
730 | 509 | 129.7567 | 730 | 509 | 0.47618 | 392.6 | 171.6 | 128.7751 | 112.5867 | 730 | 509 | 126.3032
740 | 519 | 129.9486 | 740 | 519 | 0.47618 | 392.8 | 171.8 | 130.0412 | 121.742 | 740 | 519 | 126.4951
750 | 529 | 130.2365 | 750 | 529 | 0.47618 | 393 | 172 | 128.8725 | 118.4305 | 750 | 529 | 126.3991
760 | 539 | 130.2365 | 760 | 539 | 0.47618 | 393.2 | 172.2 | 127.0219 | 112.3919 | 760 | 539 | 126.687
770 | 549 | 130.0446 | 770 | 549 | 0.47618 | 393.4 | 172.4 | 127.6063 | 117.7487 | 770 | 549 | 126.5911
780 | 559 | 130.1405 | 780 | 559 | 0.38019 | 393.6 | 172.6 | 127.6063 | 113.658 | 780 | 559 | 126.5911
790 | 569 | 130.1405 | 790 | 569 | 0.38019 | 393.8 | 172.8 | 128.0933 | 117.4565 | 790 | 569 | 126.687
790.2 | 569.2 | 130.2365 | 790.2 | 569.2 | 0.47618 | 394 | 173 | 126.5349 | 113.8528 | 790.2 | 569.2 | 126.687
790.4 | 569.4 | 130.1405 | 790.4 | 569.4 | 0.38019 | 394.2 | 173.2 | 127.4115 | 117.3591 | 790.4 | 569.4 | 126.687
790.6 | 569.6 | 130.1405 | 790.6 | 569.6 | 0.38019 | 394.4 | 173.4 | 129.3595 | 122.5211 | 790.6 | 569.6 | 126.687
790.8 | 569.8 | 130.1405 | 790.8 | 569.8 | 0.38019 | 394.6 | 173.6 | 129.0672 | 122.8133 | 790.8 | 569.8 | 126.687
791 | 570 | 130.1405 | 791 | 570 | 0.38019 | 394.8 | 173.8 | 127.9959 | 120.768 | 791 | 570 | 126.687
791.2 | 570.2 | 130.1405 | 791.2 | 570.2 | 0.38019 | 395 | 174 | 127.5089 | 122.0341 | 791.2 | 570.2 | 126.687
791.4 | 570.4 | 130.1405 | 791.4 | 570.4 | 0.38019 | 395.2 | 174.2 | 127.1193 | 121.742 | 791.4 | 570.4 | 126.687
791.6 | 570.6 | 130.2365 | 791.6 | 570.6 | 0.38019 | 395.4 | 174.4 | 127.8011 | 120.5732 | 791.6 | 570.6 | 126.687
791.8 | 570.8 | 130.2365 | 791.8 | 570.8 | 0.38019 | 395.6 | 174.6 | 127.6063 | 122.8133 | 791.8 | 570.8 | 126.687
792 | 571 | 130.1405 | 792 | 571 | 0.38019 | 395.8 | 174.8 | 128.9699 | 122.4237 | 792 | 571 | 126.687
792.2 | 571.2 | 130.1405 | 792.2 | 571.2 | 0.47618 | 396 | 175 | 128.1907 | 121.5472 | 792.2 | 571.2 | 126.687
792.4 | 571.4 | 130.1405 | 792.4 | 571.4 | 0.47618 | 396.2 | 175.2 | 130.0412 | 120.768 | 792.4 | 571.4 | 126.5911
792.6 | 571.6 | 130.1405 | 792.6 | 571.6 | 0.47618 | 396.4 | 175.4 | 131.0152 | 123.9821 | 792.6 | 571.6 | 126.783
792.8 | 571.8 | 130.1405 | 792.8 | 571.8 | 0.47618 | 396.6 | 175.6 | 131.0152 | 121.1576 | 792.8 | 571.8 | 126.687
793 | 572 | 130.1405 | 793 | 572 | 0.47618 | 396.8 | 175.8 | 130.4308 | 119.794 | 793 | 572 | 126.687
793.2 | 572.2 | 130.1405 | 793.2 | 572.2 | 0.38019 | 397 | 176 | 130.236 | 117.6513 | 793.2 | 572.2 | 126.687
793.4 | 572.4 | 130.1405 | 793.4 | 572.4 | 0.47618 | 397.2 | 176.2 | 129.8464 | 111.6127 | 793.4 | 572.4 | 126.687
793.6 | 572.6 | 130.1405 | 793.6 | 572.6 | 0.38019 | 397.4 | 176.4 | 129.3595 | 111.2231 | 793.6 | 572.6 | 126.687
793.8 | 572.8 | 130.2365 | 793.8 | 572.8 | 0.47618 | 397.6 | 176.6 | 130.4308 | 118.82 | 793.8 | 572.8 | 126.687
794 | 573 | 130.1405 | 794 | 573 | 0.38019 | 397.8 | 176.8 | 130.9178 | 121.5472 | 794 | 573 | 126.687
794.2 | 573.2 | 130.1405 | 794.2 | 573.2 | 0.38019 | 398 | 177 | 130.6256 | 119.1123 | 794.2 | 573.2 | 126.687
794.4 | 573.4 | 130.1405 | 794.4 | 573.4 | 0.38019 | 398.2 | 177.2 | 131.21 | 125.443 | 794.4 | 573.4 | 126.687
794.6 | 573.6 | 130.1405 | 794.6 | 573.6 | 0.47618 | 398.4 | 177.4 | 129.8464 | 119.5018 | 794.6 | 573.6 | 126.687
794.8 | 573.8 | 130.1405 | 794.8 | 573.8 | 0.47618 | 398.6 | 177.6 | 125.9505 | 107.6195 | 794.8 | 573.8 | 126.687
795 | 574 | 130.2365 | 795 | 574 | 0.47618 | 398.8 | 177.8 | 128.0933 | 117.6513 | 795 | 574 | 126.783
795.2 | 574.2 | 130.1405 | 795.2 | 574.2 | 0.38019 | 399 | 178 | 129.5542 | 116.0929 | 795.2 | 574.2 | 126.687
795.4 | 574.4 | 130.2365 | 795.4 | 574.4 | 0.38019 | 399.2 | 178.2 | 128.4829 | 115.8981 | 795.4 | 574.4 | 126.687
795.6 | 574.6 | 130.1405 | 795.6 | 574.6 | 0.38019 | 399.4 | 178.4 | 125.3662 | 114.4372 | 795.6 | 574.6 | 126.687
795.8 | 574.8 | 130.1405 | 795.8 | 574.8 | 0.47618 | 399.6 | 178.6 | 129.262 | 117.7487 | 795.8 | 574.8 | 126.687
796 | 575 | 130.1405 | 796 | 575 | 0.47618 | 399.8 | 178.8 | 128.9699 | 113.7554 | 796 | 575 | 126.5911
796.2 | 575.2 | 130.1405 | 796.2 | 575.2 | 0.47618 | 400 | 179 | 127.6063 | 103.1392 | 796.2 | 575.2 | 126.687
796.4 | 575.4 | 130.2365 | 796.4 | 575.4 | 0.47618 | 400.2 | 179.2 | 127.1193 | 92.036 | 796.4 | 575.4 | 126.687
796.6 | 575.6 | 130.1405 | 796.6 | 575.6 | 0.47618 | 400.4 | 179.4 | 125.3662 | 90.4777 | 796.6 | 575.6 | 126.687
796.8 | 575.8 | 130.1405 | 796.8 | 575.8 | 0.47618 | 400.6 | 179.6 | 122.6391 | 88.4323 | 796.8 | 575.8 | 126.687
797 | 576 | 130.1405 | 797 | 576 | 0.38019 | 400.8 | 179.8 | 19.1066 | 13.5344 | 797 | 576 | 126.687
797.2 | 576.2 | 130.1405 | 797.2 | 576.2 | 0.47618 | 401 | 180 | 3.3283 | 2.5286 | 797.2 | 576.2 | 126.687
797.4 | 576.4 | 130.1405 | 797.4 | 576.4 | 0.38019 | 401.2 | 180.2 | 1.283 | 1.1651 | 797.4 | 576.4 | 126.687
797.6 | 576.6 | 130.1405 | 797.6 | 576.6 | 0.38019 | 401.4 | 180.4 | 0.79601 | 0.77546 | 797.6 | 576.6 | 126.687
797.8 | 576.8 | 130.1405 | 797.8 | 576.8 | 0.47618 | 401.6 | 180.6 | 0.69863 | 0.67808 | 797.8 | 576.8 | 126.687
798 | 577 | 130.0446 | 798 | 577 | 0.47618 | 401.8 | 180.8 | 0.69863 | 0.67808 | 798 | 577 | 126.5911
798.2 | 577.2 | 130.1405 | 798.2 | 577.2 | 0.47618 | 402 | 181 | 0.40645 | 0.48328 | 798.2 | 577.2 | 126.687
798.4 | 577.4 | 130.1405 | 798.4 | 577.4 | 0.38019 | 405 | 184 | 0.40645 | 0.48328 | 798.4 | 577.4 | 126.687
798.6 | 577.6 | 130.1405 | 798.6 | 577.6 | 0.38019 | 410 | 189 | 0.21165 | 0.38586 | 798.6 | 577.6 | 126.687
798.8 | 577.8 | 130.1405 | 798.8 | 577.8 | 0.38019 | 413.4 | 192.4 | 0.21165 | 0.28848 | 798.8 | 577.8 | 126.687
799 | 578 | 130.1405 | 799 | 578 | 0.47618 |  |  |  |  | 799 | 578 | 126.687
799.2 | 578.2 | 130.1405 | 799.2 | 578.2 | 0.47618 |  |  |  |  | 799.2 | 578.2 | 126.687
799.4 | 578.4 | 130.2365 | 799.4 | 578.4 | 0.38019 |  |  |  |  | 799.4 | 578.4 | 126.687
799.6 | 578.6 | 130.1405 | 799.6 | 578.6 | 0.38019 |  |  |  |  | 799.6 | 578.6 | 126.687
799.8 | 578.8 | 130.1405 | 799.8 | 578.8 | 0.47618 |  |  |  |  | 799.8 | 578.8 | 126.687
800 | 579 | 130.0446 | 800 | 579 | 0.47618 |  |  |  |  | 800 | 579 | 126.5911
800.2 | 579.2 | 130.2365 | 800.2 | 579.2 | 0.38019 |  |  |  |  | 800.2 | 579.2 | 126.687
800.4 | 579.4 | 130.1405 | 800.4 | 579.4 | 0.47618 |  |  |  |  | 800.4 | 579.4 | 126.687
800.6 | 579.6 | 130.1405 | 800.6 | 579.6 | 0.47618 |  |  |  |  | 800.6 | 579.6 | 126.687
800.8 | 579.8 | 130.1405 | 800.8 | 579.8 | 0.38019 |  |  |  |  | 800.8 | 579.8 | 126.687
801 | 580 | 84.3641 | 801 | 580 | 0.38019 |  |  |  |  | 801 | 580 | 123.7121
801.2 | 580.2 | 9.6057 | 801.2 | 580.2 | 0.47618 |  |  |  |  | 801.2 | 580.2 | 126.5911
801.4 | 580.4 | 2.6001 | 801.4 | 580.4 | 0.38019 |  |  |  |  | 801.4 | 580.4 | 126.783
801.6 | 580.6 | 1.3525 | 801.6 | 580.6 | 0.38019 |  |  |  |  | 801.6 | 580.6 | 126.783
801.8 | 580.8 | 1.0646 | 801.8 | 580.8 | 0.47618 |  |  |  |  | 801.8 | 580.8 | 126.783
802 | 581 | 0.96863 | 802 | 581 | 0.47618 |  |  |  |  | 802 | 581 | 126.783
802.2 | 581.2 | 0.87268 | 802.2 | 581.2 | 0.38019 |  |  |  |  | 802.2 | 581.2 | 126.783
802.4 | 581.4 | 0.77673 | 802.4 | 581.4 | 0.47618 |  |  |  |  | 802.4 | 581.4 | 126.783
802.6 | 581.6 | 0.77673 | 802.6 | 581.6 | 0.38019 |  |  |  |  | 802.6 | 581.6 | 126.783
802.8 | 581.8 | 0.77673 | 802.8 | 581.8 | 0.47618 |  |  |  |  | 802.8 | 581.8 | 126.783
803 | 582 | 0.68074 | 803 | 582 | 0.47618 |  |  |  |  | 803 | 582 | 126.783
803.2 | 582.2 | 0.68074 | 803.2 | 582.2 | 0.38019 |  |  |  |  | 803.2 | 582.2 | 126.879
803.4 | 582.4 | 0.68074 | 803.4 | 582.4 | 0.47618 |  |  |  |  | 803.4 | 582.4 | 126.783
803.6 | 582.6 | 0.58479 | 803.6 | 582.6 | 0.38019 |  |  |  |  | 803.6 | 582.6 | 126.783
803.8 | 582.8 | 0.68074 | 803.8 | 582.8 | 0.47618 |  |  |  |  | 803.8 | 582.8 | 126.783
804 | 583 | 0.58479 | 804 | 583 | 0.47618 |  |  |  |  | 804 | 583 | 126.783
804.2 | 583.2 | 0.58479 | 804.2 | 583.2 | 0.47618 |  |  |  |  | 804.2 | 583.2 | 126.783
804.4 | 583.4 | 0.58479 | 804.4 | 583.4 | 0.38019 |  |  |  |  | 804.4 | 583.4 | 126.783
804.6 | 583.6 | 0.58479 | 804.6 | 583.6 | 0.38019 |  |  |  |  | 804.6 | 583.6 | 126.879
804.8 | 583.8 | 0.58479 | 804.8 | 583.8 | 0.38019 |  |  |  |  | 804.8 | 583.8 | 126.783
805 | 584 | 0.58479 | 805 | 584 | 0.38019 |  |  |  |  | 805 | 584 | 126.783
805.2 | 584.2 | 0.58479 | 805.2 | 584.2 | 0.47618 |  |  |  |  | 805.2 | 584.2 | 126.783
805.4 | 584.4 | 0.58479 | 805.4 | 584.4 | 0.38019 |  |  |  |  | 805.4 | 584.4 | 126.783
805.6 | 584.6 | 0.58479 | 805.6 | 584.6 | 0.47618 |  |  |  |  | 805.6 | 584.6 | 126.783
805.8 | 584.8 | 0.58479 | 805.8 | 584.8 | 0.47618 |  |  |  |  | 805.8 | 584.8 | 126.783
806 | 585 | 0.4888 | 806 | 585 | 0.47618 |  |  |  |  | 806 | 585 | 126.783
806.2 | 585.2 | 0.58479 | 806.2 | 585.2 | 0.38019 |  |  |  |  | 806.2 | 585.2 | 126.783
806.4 | 585.4 | 0.58479 | 806.4 | 585.4 | 0.47618 |  |  |  |  | 806.4 | 585.4 | 126.783
806.6 | 585.6 | 0.58479 | 806.6 | 585.6 | 0.38019 |  |  |  |  | 806.6 | 585.6 | 126.783
806.8 | 585.8 | 0.4888 | 806.8 | 585.8 | 0.38019 |  |  |  |  | 806.8 | 585.8 | 126.783
807 | 586 | 0.58479 | 807 | 586 | 0.47618 |  |  |  |  | 807 | 586 | 126.783
|  |  | 808 | 587 | 0.38019 |  |  |  |  | 808 | 587 | 126.687
|  |  | 810 | 589 | 0.47618 |  |  |  |  | 810 | 589 | 126.783
|  |  | 820 | 599 | 0.47618 |  |  |  |  | 820 | 599 | 126.687
|  |  | 830 | 609 | 0.47618 |  |  |  |  | 830 | 609 | 126.5911
|  |  | 840 | 619 | 0.86003 |  |  |  |  | 840 | 619 | 126.3032
|  |  | 850 | 629 | 0.95602 |  |  |  |  | 850 | 629 | 126.3032
|  |  | 860 | 639 | 1.2439 |  |  |  |  | 860 | 639 | 126.3032
|  |  | 870 | 649 | 1.052 |  |  |  |  | 870 | 649 | 126.3032
|  |  | 880 | 659 | 0.86003 |  |  |  |  | 880 | 659 | 126.3032
|  |  | 890 | 669 | 1.3399 |  |  |  |  | 890 | 669 | 126.4951
|  |  | 900 | 679 | 1.5318 |  |  |  |  | 900 | 679 | 126.5911
|  |  | 910 | 689 | 1.6278 |  |  |  |  | 910 | 689 | 126.687
|  |  | 920 | 699 | 1.052 |  |  |  |  | 920 | 699 | 126.4951
|  |  | 930 | 709 | 0.47618 |  |  |  |  | 930 | 709 | 126.3991
|  |  | 940 | 719 | 0.47618 |  |  |  |  | 940 | 719 | 126.3991
|  |  | 950 | 729 | 0.57213 |  |  |  |  | 950 | 729 | 126.3991
|  |  | 960 | 739 | 0.47618 |  |  |  |  | 960 | 739 | 126.3991
|  |  | 970 | 749 | 0.57213 |  |  |  |  | 970 | 749 | 126.4951
|  |  | 980 | 759 | 0.95602 |  |  |  |  | 980 | 759 | 126.4951
|  |  | 990 | 769 | 1.148 |  |  |  |  | 990 | 769 | 126.687
|  |  | 1000 | 779 | 1.2439 |  |  |  |  | 1000 | 779 | 126.687
|  |  | 1010 | 789 | 0.76408 |  |  |  |  | 1010 | 789 | 126.3991
|  |  | 1020 | 799 | 0.66813 |  |  |  |  | 1020 | 799 | 126.3991
|  |  | 1030 | 809 | 0.76408 |  |  |  |  | 1030 | 809 | 126.3991
|  |  | 1040 | 819 | 0.47618 |  |  |  |  | 1040 | 819 | 126.3991
|  |  | 1050 | 829 | 0.47618 |  |  |  |  | 1050 | 829 | 126.3032
|  |  | 1060 | 839 | 0.47618 |  |  |  |  | 1060 | 839 | 126.4951
|  |  | 1070 | 849 | 0.57213 |  |  |  |  | 1070 | 849 | 126.3032
|  |  | 1080 | 859 | 0.47618 |  |  |  |  | 1080 | 859 | 126.3991
|  |  | 1090 | 869 | 0.57213 |  |  |  |  | 1090 | 869 | 126.2072
|  |  | 1100 | 879 | 0.57213 |  |  |  |  | 1100 | 879 | 126.3032
|  |  | 1110 | 889 | 0.47618 |  |  |  |  | 1110 | 889 | 126.3032
|  |  | 1120 | 899 | 0.47618 |  |  |  |  | 1120 | 899 | 126.3032
|  |  | 1130 | 909 | 0.47618 |  |  |  |  | 1130 | 909 | 126.3991
|  |  | 1140 | 919 | 0.57213 |  |  |  |  | 1140 | 919 | 126.4951
|  |  | 1150 | 929 | 0.47618 |  |  |  |  | 1150 | 929 | 126.4951
|  |  | 1160 | 939 | 0.57213 |  |  |  |  | 1160 | 939 | 126.4951
|  |  | 1170 | 949 | 0.47618 |  |  |  |  | 1170 | 949 | 126.3991
|  |  | 1180 | 959 | 0.57213 |  |  |  |  | 1180 | 959 | 126.4951
|  |  | 1190 | 969 | 0.57213 |  |  |  |  | 1190 | 969 | 126.687
|  |  | 1200 | 979 | 0.57213 |  |  |  |  | 1200 | 979 | 126.687
|  |  | 1210 | 989 | 0.57213 |  |  |  |  | 1210 | 989 | 126.5911
|  |  | 1220 | 999 | 0.47618 |  |  |  |  | 1220 | 999 | 126.5911
|  |  | 1230 | 1009 | 0.47618 |  |  |  |  | 1230 | 1009 | 126.5911
|  |  | 1240 | 1019 | 0.47618 |  |  |  |  | 1240 | 1019 | 126.5911
|  |  | 1240.2 | 1019.2 | 0.47618 |  |  |  |  | 1240.2 | 1019.2 | 126.4951
|  |  | 1250 | 1029 | 0.47618 |  |  |  |  | 1250 | 1029 | 126.4951
|  |  | 1260 | 1039 | 0.66813 |  |  |  |  | 1260 | 1039 | 126.3991
|  |  | 1270 | 1049 | 1.2439 |  |  |  |  | 1270 | 1049 | 126.3032
|  |  | 1280 | 1059 | 1.7237 |  |  |  |  | 1280 | 1059 | 126.4951
|  |  | 1290 | 1069 | 2.0116 |  |  |  |  | 1290 | 1069 | 126.5911
|  |  | 1300 | 1079 | 1.5318 |  |  |  |  | 1300 | 1079 | 126.3991
|  |  | 1310 | 1089 | 0.86003 |  |  |  |  | 1310 | 1089 | 126.2072
|  |  | 1320 | 1099 | 0.95602 |  |  |  |  | 1320 | 1099 | 126.2072
|  |  | 1330 | 1109 | 1.4359 |  |  |  |  | 1330 | 1109 | 126.3991
|  |  | 1340 | 1119 | 1.6278 |  |  |  |  | 1340 | 1119 | 126.3991
|  |  | 1350 | 1129 | 1.3399 |  |  |  |  | 1350 | 1129 | 126.3032
|  |  | 1360 | 1139 | 0.86003 |  |  |  |  | 1360 | 1139 | 126.2072
|  |  | 1370 | 1149 | 0.47618 |  |  |  |  | 1370 | 1149 | 126.4951
|  |  | 1380 | 1159 | 0.38019 |  |  |  |  | 1380 | 1159 | 126.5911
|  |  | 1390 | 1169 | 0.47618 |  |  |  |  | 1390 | 1169 | 126.4951
|  |  | 1400 | 1179 | 0.76408 |  |  |  |  | 1400 | 1179 | 126.4951
|  |  | 1410 | 1189 | 1.052 |  |  |  |  | 1410 | 1189 | 126.4951
|  |  | 1420 | 1199 | 1.148 |  |  |  |  | 1420 | 1199 | 126.3032
|  |  | 1430 | 1209 | 1.2439 |  |  |  |  | 1430 | 1209 | 126.3991
|  |  | 1440 | 1219 | 1.4359 |  |  |  |  | 1440 | 1219 | 126.3991
|  |  | 1450 | 1229 | 1.6278 |  |  |  |  | 1450 | 1229 | 126.687
|  |  | 1450.2 | 1229.2 | 1.6278 |  |  |  |  | 1450.2 | 1229.2 | 126.687
|  |  | 1450.4 | 1229.4 | 1.6278 |  |  |  |  | 1450.4 | 1229.4 | 126.783
|  |  | 1450.6 | 1229.6 | 1.6278 |  |  |  |  | 1450.6 | 1229.6 | 126.783
|  |  | 1450.8 | 1229.8 | 1.6278 |  |  |  |  | 1450.8 | 1229.8 | 126.783
|  |  | 1451 | 1230 | 1.6278 |  |  |  |  | 1451 | 1230 | 126.9749
|  |  | 1451.2 | 1230.2 | 1.6278 |  |  |  |  | 1451.2 | 1230.2 | 127.2628
|  |  | 1451.4 | 1230.4 | 1.7237 |  |  |  |  | 1451.4 | 1230.4 | 127.2628
|  |  | 1451.6 | 1230.6 | 1.6278 |  |  |  |  | 1451.6 | 1230.6 | 126.879
|  |  | 1451.8 | 1230.8 | 1.6278 |  |  |  |  | 1451.8 | 1230.8 | 126.879
|  |  | 1452 | 1231 | 1.6278 |  |  |  |  | 1452 | 1231 | 126.879
|  |  | 1452.2 | 1231.2 | 1.7237 |  |  |  |  | 1452.2 | 1231.2 | 126.879
|  |  | 1452.4 | 1231.4 | 1.7237 |  |  |  |  | 1452.4 | 1231.4 | 126.879
|  |  | 1452.6 | 1231.6 | 1.7237 |  |  |  |  | 1452.6 | 1231.6 | 126.879
|  |  | 1452.8 | 1231.8 | 1.6278 |  |  |  |  | 1452.8 | 1231.8 | 126.783
|  |  | 1453 | 1232 | 1.7237 |  |  |  |  | 1453 | 1232 | 126.783
|  |  | 1453.2 | 1232.2 | 1.7237 |  |  |  |  | 1453.2 | 1232.2 | 126.783
|  |  | 1453.4 | 1232.4 | 1.7237 |  |  |  |  | 1453.4 | 1232.4 | 126.783
|  |  | 1453.6 | 1232.6 | 1.7237 |  |  |  |  | 1453.6 | 1232.6 | 126.783
|  |  | 1453.8 | 1232.8 | 1.7237 |  |  |  |  | 1453.8 | 1232.8 | 126.783
|  |  | 1454 | 1233 | 1.8197 |  |  |  |  | 1454 | 1233 | 126.783
|  |  | 1454.2 | 1233.2 | 1.6278 |  |  |  |  | 1454.2 | 1233.2 | 126.783
|  |  | 1454.4 | 1233.4 | 1.7237 |  |  |  |  | 1454.4 | 1233.4 | 126.783
|  |  | 1454.6 | 1233.6 | 1.7237 |  |  |  |  | 1454.6 | 1233.6 | 126.783
|  |  | 1454.8 | 1233.8 | 1.6278 |  |  |  |  | 1454.8 | 1233.8 | 126.783
|  |  | 1455 | 1234 | 1.6278 |  |  |  |  | 1455 | 1234 | 126.783
|  |  | 1455.2 | 1234.2 | 1.6278 |  |  |  |  | 1455.2 | 1234.2 | 126.783
|  |  | 1455.4 | 1234.4 | 1.6278 |  |  |  |  | 1455.4 | 1234.4 | 126.687
|  |  | 1455.6 | 1234.6 | 1.6278 |  |  |  |  | 1455.6 | 1234.6 | 126.783
|  |  | 1455.8 | 1234.8 | 1.6278 |  |  |  |  | 1455.8 | 1234.8 | 126.687
|  |  | 1456 | 1235 | 1.6278 |  |  |  |  | 1456 | 1235 | 126.783
|  |  | 1456.2 | 1235.2 | 1.5318 |  |  |  |  | 1456.2 | 1235.2 | 126.783
|  |  | 1456.4 | 1235.4 | 1.5318 |  |  |  |  | 1456.4 | 1235.4 | 126.783
|  |  | 1456.6 | 1235.6 | 1.5318 |  |  |  |  | 1456.6 | 1235.6 | 126.783
|  |  | 1456.8 | 1235.8 | 1.6278 |  |  |  |  | 1456.8 | 1235.8 | 126.783
|  |  | 1457 | 1236 | 1.5318 |  |  |  |  | 1457 | 1236 | 126.783
|  |  | 1457.2 | 1236.2 | 1.5318 |  |  |  |  | 1457.2 | 1236.2 | 126.783
|  |  | 1457.4 | 1236.4 | 1.5318 |  |  |  |  | 1457.4 | 1236.4 | 126.783
|  |  | 1457.6 | 1236.6 | 1.6278 |  |  |  |  | 1457.6 | 1236.6 | 126.879
|  |  | 1457.8 | 1236.8 | 1.5318 |  |  |  |  | 1457.8 | 1236.8 | 126.783
|  |  | 1458 | 1237 | 1.5318 |  |  |  |  | 1458 | 1237 | 126.687
|  |  | 1458.2 | 1237.2 | 1.6278 |  |  |  |  | 1458.2 | 1237.2 | 126.783
|  |  | 1458.4 | 1237.4 | 1.6278 |  |  |  |  | 1458.4 | 1237.4 | 126.687
|  |  | 1458.6 | 1237.6 | 1.5318 |  |  |  |  | 1458.6 | 1237.6 | 126.687
|  |  | 1458.8 | 1237.8 | 1.6278 |  |  |  |  | 1458.8 | 1237.8 | 126.687
|  |  | 1459 | 1238 | 1.5318 |  |  |  |  | 1459 | 1238 | 126.783
|  |  | 1459.2 | 1238.2 | 1.5318 |  |  |  |  | 1459.2 | 1238.2 | 126.687
|  |  | 1459.4 | 1238.4 | 1.5318 |  |  |  |  | 1459.4 | 1238.4 | 126.687
|  |  | 1459.6 | 1238.6 | 1.5318 |  |  |  |  | 1459.6 | 1238.6 | 126.687
|  |  | 1459.8 | 1238.8 | 1.5318 |  |  |  |  | 1459.8 | 1238.8 | 126.687
|  |  | 1460 | 1239 | 1.5318 |  |  |  |  | 1460 | 1239 | 126.687
|  |  | 1460.2 | 1239.2 | 1.5318 |  |  |  |  | 1460.2 | 1239.2 | 126.783
|  |  | 1460.4 | 1239.4 | 1.4359 |  |  |  |  | 1460.4 | 1239.4 | 126.783
|  |  | 1460.6 | 1239.6 | 1.4359 |  |  |  |  | 1460.6 | 1239.6 | 126.687
|  |  | 1460.8 | 1239.8 | 1.4359 |  |  |  |  | 1460.8 | 1239.8 | 126.687
|  |  | 1461 | 1240 | 1.5318 |  |  |  |  | 1461 | 1240 | 126.687
|  |  | 1461.2 | 1240.2 | 1.5318 |  |  |  |  | 1461.2 | 1240.2 | 126.783
|  |  | 1461.4 | 1240.4 | 1.4359 |  |  |  |  | 1461.4 | 1240.4 | 126.783
|  |  | 1461.6 | 1240.6 | 1.4359 |  |  |  |  | 1461.6 | 1240.6 | 126.783
|  |  | 1461.8 | 1240.8 | 1.4359 |  |  |  |  | 1461.8 | 1240.8 | 126.687
|  |  | 1462 | 1241 | 1.4359 |  |  |  |  | 1462 | 1241 | 126.5911
|  |  | 1462.2 | 1241.2 | 1.4359 |  |  |  |  | 1462.2 | 1241.2 | 126.5911
|  |  | 1462.4 | 1241.4 | 1.3399 |  |  |  |  | 1462.4 | 1241.4 | 126.687
|  |  | 1462.6 | 1241.6 | 1.4359 |  |  |  |  | 1462.6 | 1241.6 | 126.687
|  |  | 1462.8 | 1241.8 | 1.3399 |  |  |  |  | 1462.8 | 1241.8 | 126.783
|  |  | 1463 | 1242 | 1.3399 |  |  |  |  | 1463 | 1242 | 126.687
|  |  | 1463.2 | 1242.2 | 1.3399 |  |  |  |  | 1463.2 | 1242.2 | 126.687
|  |  | 1463.4 | 1242.4 | 1.3399 |  |  |  |  | 1463.4 | 1242.4 | 126.687
|  |  | 1463.6 | 1242.6 | 1.3399 |  |  |  |  | 1463.6 | 1242.6 | 126.687
|  |  | 1463.8 | 1242.8 | 1.4359 |  |  |  |  | 1463.8 | 1242.8 | 126.687
|  |  | 1464 | 1243 | 1.4359 |  |  |  |  | 1464 | 1243 | 126.5911
|  |  | 1464.2 | 1243.2 | 1.4359 |  |  |  |  | 1464.2 | 1243.2 | 126.5911
|  |  | 1464.4 | 1243.4 | 1.4359 |  |  |  |  | 1464.4 | 1243.4 | 126.5911
|  |  | 1464.6 | 1243.6 | 1.4359 |  |  |  |  | 1464.6 | 1243.6 | 126.687
|  |  | 1464.8 | 1243.8 | 1.5318 |  |  |  |  | 1464.8 | 1243.8 | 126.687
|  |  | 1465 | 1244 | 1.5318 |  |  |  |  | 1465 | 1244 | 126.5911
|  |  | 1465.2 | 1244.2 | 1.4359 |  |  |  |  | 1465.2 | 1244.2 | 126.687
|  |  | 1465.4 | 1244.4 | 1.4359 |  |  |  |  | 1465.4 | 1244.4 | 126.687
|  |  | 1465.6 | 1244.6 | 1.4359 |  |  |  |  | 1465.6 | 1244.6 | 126.687
|  |  | 1465.8 | 1244.8 | 1.4359 |  |  |  |  | 1465.8 | 1244.8 | 126.5911
|  |  | 1466 | 1245 | 1.4359 |  |  |  |  | 1466 | 1245 | 126.4951
|  |  | 1466.2 | 1245.2 | 1.4359 |  |  |  |  | 1466.2 | 1245.2 | 126.5911
|  |  | 1466.4 | 1245.4 | 1.4359 |  |  |  |  | 1466.4 | 1245.4 | 126.4951
|  |  | 1466.6 | 1245.6 | 1.4359 |  |  |  |  | 1466.6 | 1245.6 | 126.5911
|  |  | 1466.8 | 1245.8 | 1.3399 |  |  |  |  | 1466.8 | 1245.8 | 126.5911
|  |  | 1467 | 1246 | 1.3399 |  |  |  |  | 1467 | 1246 | 126.5911
|  |  | 1467.2 | 1246.2 | 1.3399 |  |  |  |  | 1467.2 | 1246.2 | 126.687
|  |  | 1467.4 | 1246.4 | 1.3399 |  |  |  |  | 1467.4 | 1246.4 | 126.5911
|  |  | 1467.6 | 1246.6 | 1.3399 |  |  |  |  | 1467.6 | 1246.6 | 126.5911
|  |  | 1467.8 | 1246.8 | 1.5318 |  |  |  |  | 1467.8 | 1246.8 | 126.5911
|  |  | 1468 | 1247 | 1.3399 |  |  |  |  | 1468 | 1247 | 126.4951
|  |  | 1468.2 | 1247.2 | 1.3399 |  |  |  |  | 1468.2 | 1247.2 | 126.5911
|  |  | 1468.4 | 1247.4 | 1.2439 |  |  |  |  | 1468.4 | 1247.4 | 126.4951
|  |  | 1468.6 | 1247.6 | 1.2439 |  |  |  |  | 1468.6 | 1247.6 | 126.5911
|  |  | 1468.8 | 1247.8 | 1.2439 |  |  |  |  | 1468.8 | 1247.8 | 126.5911
|  |  | 1469 | 1248 | 1.2439 |  |  |  |  | 1469 | 1248 | 126.5911
|  |  | 1469.2 | 1248.2 | 1.3399 |  |  |  |  | 1469.2 | 1248.2 | 126.4951
|  |  | 1469.4 | 1248.4 | 1.3399 |  |  |  |  | 1469.4 | 1248.4 | 126.5911
|  |  | 1469.6 | 1248.6 | 1.2439 |  |  |  |  | 1469.6 | 1248.6 | 126.5911
|  |  | 1469.8 | 1248.8 | 1.2439 |  |  |  |  | 1469.8 | 1248.8 | 126.4951
|  |  | 1470 | 1249 | 1.2439 |  |  |  |  | 1470 | 1249 | 126.4951
|  |  | 1470.2 | 1249.2 | 1.148 |  |  |  |  | 1470.2 | 1249.2 | 126.4951
|  |  | 1470.4 | 1249.4 | 1.148 |  |  |  |  | 1470.4 | 1249.4 | 126.3991
|  |  | 1470.6 | 1249.6 | 1.2439 |  |  |  |  | 1470.6 | 1249.6 | 126.3991
|  |  | 1470.8 | 1249.8 | 1.148 |  |  |  |  | 1470.8 | 1249.8 | 126.4951
|  |  | 1471 | 1250 | 1.148 |  |  |  |  | 1471 | 1250 | 126.4951
|  |  | 1471.2 | 1250.2 | 1.052 |  |  |  |  | 1471.2 | 1250.2 | 126.4951
|  |  | 1471.4 | 1250.4 | 1.148 |  |  |  |  | 1471.4 | 1250.4 | 126.4951
|  |  | 1471.6 | 1250.6 | 1.2439 |  |  |  |  | 1471.6 | 1250.6 | 126.4951
|  |  | 1471.8 | 1250.8 | 1.2439 |  |  |  |  | 1471.8 | 1250.8 | 126.4951
|  |  | 1472 | 1251 | 1.148 |  |  |  |  | 1472 | 1251 | 126.3991
|  |  | 1472.2 | 1251.2 | 1.052 |  |  |  |  | 1472.2 | 1251.2 | 126.4951
|  |  | 1472.4 | 1251.4 | 1.052 |  |  |  |  | 1472.4 | 1251.4 | 126.4951
|  |  | 1472.6 | 1251.6 | 1.052 |  |  |  |  | 1472.6 | 1251.6 | 126.3991
|  |  | 1472.8 | 1251.8 | 1.052 |  |  |  |  | 1472.8 | 1251.8 | 126.5911
|  |  | 1473 | 1252 | 1.052 |  |  |  |  | 1473 | 1252 | 126.4951
|  |  | 1473.2 | 1252.2 | 1.052 |  |  |  |  | 1473.2 | 1252.2 | 126.4951
|  |  | 1473.4 | 1252.4 | 1.052 |  |  |  |  | 1473.4 | 1252.4 | 126.3991
|  |  | 1473.6 | 1252.6 | 0.95602 |  |  |  |  | 1473.6 | 1252.6 | 126.3991
|  |  | 1473.8 | 1252.8 | 0.95602 |  |  |  |  | 1473.8 | 1252.8 | 28.1287
|  |  | 1474 | 1253 | 0.95602 |  |  |  |  | 1474 | 1253 | 4.3288
|  |  | 1474.2 | 1253.2 | 0.95602 |  |  |  |  | 1474.2 | 1253.2 | 1.7377
|  |  | 1474.4 | 1253.4 | 0.95602 |  |  |  |  | 1474.4 | 1253.4 | 1.0659
|  |  | 1474.6 | 1253.6 | 0.95602 |  |  |  |  | 1474.6 | 1253.6 | 0.874
|  |  | 1474.8 | 1253.8 | 0.76408 |  |  |  |  | 1474.8 | 1253.8 | 0.68206
|  |  | 1475 | 1254 | 0.76408 |  |  |  |  | 1475 | 1254 | 0.68206
|  |  | 1475.2 | 1254.2 | 0.76408 |  |  |  |  | 1475.2 | 1254.2 | 0.68206
|  |  | 1475.4 | 1254.4 | 0.76408 |  |  |  |  | 1475.4 | 1254.4 | 0.58611
|  |  | 1475.6 | 1254.6 | 0.76408 |  |  |  |  | 1475.6 | 1254.6 | 0.58611
|  |  | 1475.8 | 1254.8 | 0.76408 |  |  |  |  | 1475.8 | 1254.8 | 0.58611
|  |  | 1476 | 1255 | 0.66813 |  |  |  |  | 1476 | 1255 | 0.58611
|  |  | 1476.2 | 1255.2 | 0.66813 |  |  |  |  | 1476.2 | 1255.2 | 0.58611
|  |  | 1476.4 | 1255.4 | 0.76408 |  |  |  |  | 1476.4 | 1255.4 | 0.49012
|  |  | 1476.6 | 1255.6 | 0.76408 |  |  |  |  | 1476.6 | 1255.6 | 0.58611
|  |  | 1476.8 | 1255.8 | 0.66813 |  |  |  |  | 1476.8 | 1255.8 | 0.49012
|  |  | 1477 | 1256 | 0.66813 |  |  |  |  | 1477 | 1256 | 0.49012
|  |  | 1477.2 | 1256.2 | 0.66813 |  |  |  |  | 1477.2 | 1256.2 | 0.58611
|  |  | 1477.4 | 1256.4 | 0.66813 |  |  |  |  | 1477.4 | 1256.4 | 0.58611
|  |  | 1477.6 | 1256.6 | 0.66813 |  |  |  |  | 1477.6 | 1256.6 | 0.49012
|  |  | 1477.8 | 1256.8 | 0.57213 |  |  |  |  | 1477.8 | 1256.8 | 0.49012
|  |  | 1478 | 1257 | 0.66813 |  |  |  |  | 1478 | 1257 | 0.49012
|  |  | 1478.2 | 1257.2 | 0.66813 |  |  |  |  | 1478.2 | 1257.2 | 0.49012
|  |  | 1478.4 | 1257.4 | 0.57213 |  |  |  |  | 1478.4 | 1257.4 | 0.49012
|  |  | 1478.6 | 1257.6 | 0.66813 |  |  |  |  | 1478.6 | 1257.6 | 0.49012
|  |  | 1478.8 | 1257.8 | 0.57213 |  |  |  |  | 1478.8 | 1257.8 | 0.49012
|  |  | 1479 | 1258 | 0.57213 |  |  |  |  | 1479 | 1258 | 0.49012
|  |  | 1479.2 | 1258.2 | 0.66813 |  |  |  |  | 1479.2 | 1258.2 | 0.49012
|  |  | 1479.4 | 1258.4 | 0.57213 |  |  |  |  | 1479.4 | 1258.4 | 0.49012
|  |  | 1479.6 | 1258.6 | 0.57213 |  |  |  |  | 1479.6 | 1258.6 | 0.49012
|  |  | 1479.8 | 1258.8 | 0.57213 |  |  |  |  | 1479.8 | 1258.8 | 0.39416
|  |  | 1480 | 1259 | 0.57213 |  |  |  |  | 1480 | 1259 | 0.49012
|  |  | 1480.2 | 1259.2 | 0.57213
|  |  | 1480.4 | 1259.4 | 0.57213
|  |  | 1480.6 | 1259.6 | 0.57213
|  |  | 1480.8 | 1259.8 | 0.57213
|  |  | 1481 | 1260 | 0.57213
|  |  | 1481.2 | 1260.2 | 0.57213
|  |  | 1481.4 | 1260.4 | 0.57213
|  |  | 1481.6 | 1260.6 | 0.57213
|  |  | 1481.8 | 1260.8 | 0.57213
|  |  | 1482 | 1261 | 0.57213
|  |  | 1482.2 | 1261.2 | 0.57213
|  |  | 1482.4 | 1261.4 | 0.57213
|  |  | 1482.6 | 1261.6 | 0.47618
|  |  | 1482.8 | 1261.8 | 0.57213
|  |  | 1483 | 1262 | 0.57213
|  |  | 1483.2 | 1262.2 | 0.47618
|  |  | 1483.4 | 1262.4 | 0.57213
|  |  | 1483.6 | 1262.6 | 0.47618
|  |  | 1483.8 | 1262.8 | 0.57213
|  |  | 1484 | 1263 | 0.47618
|  |  | 1484.2 | 1263.2 | 0.57213
|  |  | 1484.4 | 1263.4 | 0.57213
|  |  | 1484.6 | 1263.6 | 0.57213
|  |  | 1484.8 | 1263.8 | 0.47618
|  |  | 1485 | 1264 | 0.47618
|  |  | 1485.2 | 1264.2 | 0.57213
|  |  | 1485.4 | 1264.4 | 0.47618
|  |  | 1485.6 | 1264.6 | 0.57213
|  |  | 1485.8 | 1264.8 | 0.47618
|  |  | 1486 | 1265 | 0.47618
|  |  | 1486.2 | 1265.2 | 0.47618
|  |  | 1486.4 | 1265.4 | 0.57213
|  |  | 1486.6 | 1265.6 | 0.47618
|  |  | 1486.8 | 1265.8 | 0.47618
|  |  | 1487 | 1266 | 0.57213
|  |  | 1487.2 | 1266.2 | 0.47618
|  |  | 1487.4 | 1266.4 | 0.57213
|  |  | 1487.6 | 1266.6 | 0.57213
|  |  | 1487.8 | 1266.8 | 0.57213
|  |  | 1488 | 1267 | 0.47618
|  |  | 1488.2 | 1267.2 | 0.57213
|  |  | 1488.4 | 1267.4 | 0.57213
|  |  | 1488.6 | 1267.6 | 0.57213
|  |  | 1488.8 | 1267.8 | 0.57213
|  |  | 1489 | 1268 | 0.47618
|  |  | 1489.2 | 1268.2 | 0.57213
|  |  | 1489.4 | 1268.4 | 0.47618
|  |  | 1489.6 | 1268.6 | 0.57213
|  |  | 1489.8 | 1268.8 | 0.57213
|  |  | 1490 | 1269 | 0.47618
|  |  | 1490.2 | 1269.2 | 0.47618
|  |  | 1490.4 | 1269.4 | 0.47618
|  |  | 1490.6 | 1269.6 | 0.57213
|  |  | 1490.8 | 1269.8 | 0.47618
|  |  | 1491 | 1270 | 0.47618
|  |  | 1491.2 | 1270.2 | 0.47618
|  |  | 1491.4 | 1270.4 | 0.57213
|  |  | 1491.6 | 1270.6 | 0.57213
|  |  | 1491.8 | 1270.8 | 0.47618
|  |  | 1492 | 1271 | 0.47618
|  |  | 1492.2 | 1271.2 | 0.57213
|  |  | 1492.4 | 1271.4 | 0.57213
|  |  | 1492.6 | 1271.6 | 0.57213
|  |  | 1492.8 | 1271.8 | 0.57213
|  |  | 1493 | 1272 | 0.47618
|  |  | 1493.2 | 1272.2 | 0.57213
|  |  | 1493.4 | 1272.4 | 0.57213
|  |  | 1493.6 | 1272.6 | 0.47618
|  |  | 1493.8 | 1272.8 | 0.47618
|  |  | 1494 | 1273 | 0.57213
|  |  | 1494.2 | 1273.2 | 0.57213
|  |  | 1494.4 | 1273.4 | 0.47618
|  |  | 1494.6 | 1273.6 | 0.57213
|  |  | 1494.8 | 1273.8 | 0.47618
|  |  | 1495 | 1274 | 0.57213
|  |  | 1495.2 | 1274.2 | 0.57213
|  |  | 1495.4 | 1274.4 | 0.47618
|  |  | 1495.6 | 1274.6 | 0.47618
|  |  | 1495.8 | 1274.8 | 0.47618
|  |  | 1496 | 1275 | 0.57213
|  |  | 1496.2 | 1275.2 | 0.57213
|  |  | 1496.4 | 1275.4 | 0.57213
|  |  | 1496.6 | 1275.6 | 0.57213
|  |  | 1496.8 | 1275.8 | 0.57213
|  |  | 1497 | 1276 | 0.47618
|  |  | 1497.2 | 1276.2 | 0.57213
|  |  | 1497.4 | 1276.4 | 0.57213
|  |  | 1497.6 | 1276.6 | 0.57213
|  |  | 1497.8 | 1276.8 | 0.57213
|  |  | 1498 | 1277 | 0.57213
|  |  | 1498.2 | 1277.2 | 0.57213
|  |  | 1498.4 | 1277.4 | 0.57213
|  |  | 1498.6 | 1277.6 | 0.57213
|  |  | 1498.8 | 1277.8 | 0.47618
|  |  | 1499 | 1278 | 0.57213
|  |  | 1499.2 | 1278.2 | 0.57213
|  |  | 1499.4 | 1278.4 | 0.57213
|  |  | 1499.6 | 1278.6 | 0.57213
|  |  | 1499.8 | 1278.8 | 0.47618
|  |  | 1500 | 1279 | 0.57213
|  |  | 1500.2 | 1279.2 | 0.57213
|  |  | 1500.4 | 1279.4 | 0.57213
|  |  | 1500.6 | 1279.6 | 0.57213
|  |  | 1500.8 | 1279.8 | 0.47618
|  |  | 1501 | 1280 | 0.57213
|  |  | 1501.2 | 1280.2 | 0.57213
|  |  | 1501.4 | 1280.4 | 0.57213
|  |  | 1501.6 | 1280.6 | 0.57213
|  |  | 1501.8 | 1280.8 | 0.57213
|  |  | 1502 | 1281 | 0.47618
|  |  | 1502.2 | 1281.2 | 0.57213
|  |  | 1502.4 | 1281.4 | 0.57213
|  |  | 1502.6 | 1281.6 | 0.47618
|  |  | 1502.8 | 1281.8 | 0.47618
|  |  | 1503 | 1282 | 0.57213
|  |  | 1503.2 | 1282.2 | 0.47618
|  |  | 1503.4 | 1282.4 | 0.57213
|  |  | 1503.6 | 1282.6 | 0.57213
|  |  | 1503.8 | 1282.8 | 0.47618
|  |  | 1504 | 1283 | 0.57213
|  |  | 1504.2 | 1283.2 | 0.57213
|  |  | 1504.4 | 1283.4 | 0.57213
|  |  | 1504.6 | 1283.6 | 0.57213
|  |  | 1504.8 | 1283.8 | 0.57213
|  |  | 1505 | 1284 | 0.57213
|  |  | 1505.2 | 1284.2 | 0.57213
|  |  | 1505.4 | 1284.4 | 0.57213
|  |  | 1505.6 | 1284.6 | 0.57213
|  |  | 1505.8 | 1284.8 | 0.57213
|  |  | 1506 | 1285 | 0.57213
|  |  | 1506.2 | 1285.2 | 0.57213
|  |  | 1506.4 | 1285.4 | 0.57213
|  |  | 1506.6 | 1285.6 | 0.57213
|  |  | 1506.8 | 1285.8 | 0.57213
|  |  | 1507 | 1286 | 0.47618
|  |  | 1507.2 | 1286.2 | 0.57213
|  |  | 1507.4 | 1286.4 | 0.57213
|  |  | 1507.6 | 1286.6 | 0.57213
|  |  | 1507.8 | 1286.8 | 0.47618
|  |  | 1508 | 1287 | 0.47618
|  |  | 1508.2 | 1287.2 | 0.47618
|  |  | 1508.4 | 1287.4 | 0.57213
|  |  | 1508.6 | 1287.6 | 0.57213
|  |  | 1508.8 | 1287.8 | 0.57213
|  |  | 1509 | 1288 | 0.57213
|  |  | 1509.2 | 1288.2 | 0.47618
|  |  | 1509.4 | 1288.4 | 0.57213
|  |  | 1509.6 | 1288.6 | 0.57213
|  |  | 1509.8 | 1288.8 | 0.57213
|  |  | 1510 | 1289 | 0.57213
|  |  | 1510.2 | 1289.2 | 0.57213
|  |  | 1510.4 | 1289.4 | 0.47618
|  |  | 1510.6 | 1289.6 | 0.57213
|  |  | 1510.8 | 1289.8 | 0.57213
|  |  | 1511 | 1290 | 0.47618
|  |  | 1511.2 | 1290.2 | 0.57213
|  |  | 1511.4 | 1290.4 | 0.57213
|  |  | 1511.6 | 1290.6 | 0.57213
|  |  | 1511.8 | 1290.8 | 0.57213
|  |  | 1512 | 1291 | 0.57213
|  |  | 1512.2 | 1291.2 | 0.57213
|  |  | 1512.4 | 1291.4 | 0.57213
|  |  | 1512.6 | 1291.6 | 0.47618
|  |  | 1512.8 | 1291.8 | 0.57213
|  |  | 1513 | 1292 | 0.47618
|  |  | 1513.2 | 1292.2 | 0.57213
|  |  | 1513.4 | 1292.4 | 0.47618
|  |  | 1513.6 | 1292.6 | 0.57213
|  |  | 1513.8 | 1292.8 | 0.57213
|  |  | 1514 | 1293 | 0.57213
|  |  | 1514.2 | 1293.2 | 0.57213
|  |  | 1514.4 | 1293.4 | 0.57213
|  |  | 1514.6 | 1293.6 | 0.57213
|  |  | 1514.8 | 1293.8 | 0.57213
|  |  | 1515 | 1294 | 0.57213
|  |  | 1515.2 | 1294.2 | 0.57213
|  |  | 1515.4 | 1294.4 | 0.57213
|  |  | 1515.6 | 1294.6 | 0.57213
|  |  | 1515.8 | 1294.8 | 0.57213
|  |  | 1516 | 1295 | 0.57213
|  |  | 1516.2 | 1295.2 | 0.47618
|  |  | 1516.4 | 1295.4 | 0.57213
|  |  | 1516.6 | 1295.6 | 0.57213
|  |  | 1516.8 | 1295.8 | 0.57213
|  |  | 1517 | 1296 | 0.47618
|  |  | 1517.2 | 1296.2 | 0.66813
|  |  | 1517.4 | 1296.4 | 0.57213
|  |  | 1517.6 | 1296.6 | 0.57213
|  |  | 1517.8 | 1296.8 | 0.47618
|  |  | 1518 | 1297 | 0.57213
|  |  | 1518.2 | 1297.2 | 0.57213
|  |  | 1518.4 | 1297.4 | 0.57213
|  |  | 1518.6 | 1297.6 | 0.57213
|  |  | 1518.8 | 1297.8 | 0.57213
|  |  | 1519 | 1298 | 0.57213
|  |  | 1519.2 | 1298.2 | 0.47618
|  |  | 1519.4 | 1298.4 | 0.57213
|  |  | 1519.6 | 1298.6 | 0.57213
|  |  | 1519.8 | 1298.8 | 0.57213
|  |  | 1520 | 1299 | 0.57213
|  |  | 1520.2 | 1299.2 | 0.57213
|  |  | 1520.4 | 1299.4 | 0.66813
|  |  | 1520.6 | 1299.6 | 0.66813
|  |  | 1520.8 | 1299.8 | 0.76408
|  |  | 1521 | 1300 | 0.47618
|  |  | 1521.2 | 1300.2 | 0.66813
|  |  | 1521.4 | 1300.4 | 0.57213
|  |  | 1521.6 | 1300.6 | 0.57213
|  |  | 1521.8 | 1300.8 | 0.57213
|  |  | 1522 | 1301 | 0.57213
|  |  | 1522.2 | 1301.2 | 0.57213
|  |  | 1522.4 | 1301.4 | 0.57213
|  |  | 1522.6 | 1301.6 | 0.57213
|  |  | 1522.8 | 1301.8 | 0.57213
|  |  | 1523 | 1302 | 0.57213
|  |  | 1523.2 | 1302.2 | 0.57213
|  |  | 1523.4 | 1302.4 | 0.47618
|  |  | 1523.6 | 1302.6 | 0.57213
|  |  | 1523.8 | 1302.8 | 0.57213
|  |  | 1524 | 1303 | 0.57213
|  |  | 1524.2 | 1303.2 | 0.57213
|  |  | 1524.4 | 1303.4 | 0.57213
|  |  | 1524.6 | 1303.6 | 0.57213
|  |  | 1524.8 | 1303.8 | 0.57213
|  |  | 1525 | 1304 | 0.57213
|  |  | 1525.2 | 1304.2 | 0.57213
|  |  | 1525.4 | 1304.4 | 0.57213
|  |  | 1525.6 | 1304.6 | 0.47618
|  |  | 1525.8 | 1304.8 | 0.57213
|  |  | 1526 | 1305 | 0.47618
|  |  | 1526.2 | 1305.2 | 0.47618
|  |  | 1526.4 | 1305.4 | 0.57213
|  |  | 1526.6 | 1305.6 | 0.47618
|  |  | 1526.8 | 1305.8 | 0.57213
|  |  | 1527 | 1306 | 0.47618
|  |  | 1527.2 | 1306.2 | 0.57213
|  |  | 1527.4 | 1306.4 | 0.47618
|  |  | 1527.6 | 1306.6 | 0.47618
|  |  | 1527.8 | 1306.8 | 0.47618
|  |  | 1528 | 1307 | 0.57213
|  |  | 1528.2 | 1307.2 | 0.57213
|  |  | 1528.4 | 1307.4 | 0.57213
|  |  | 1528.6 | 1307.6 | 0.47618
|  |  | 1528.8 | 1307.8 | 0.57213
|  |  | 1529 | 1308 | 0.47618
|  |  | 1529.2 | 1308.2 | 0.57213
|  |  | 1529.4 | 1308.4 | 0.57213
|  |  | 1529.6 | 1308.6 | 0.57213
|  |  | 1529.8 | 1308.8 | 0.57213
|  |  | 1530 | 1309 | 0.47618
|  |  | 1530.2 | 1309.2 | 0.47618
|  |  | 1530.4 | 1309.4 | 0.57213
|  |  | 1530.6 | 1309.6 | 0.47618
|  |  | 1530.8 | 1309.8 | 0.47618
|  |  | 1531 | 1310 | 0.57213
|  |  | 1531.2 | 1310.2 | 0.47618
|  |  | 1531.4 | 1310.4 | 0.47618
|  |  | 1531.6 | 1310.6 | 0.47618
|  |  | 1531.8 | 1310.8 | 0.47618
|  |  | 1532 | 1311 | 0.57213
|  |  | 1532.2 | 1311.2 | 0.47618
|  |  | 1532.4 | 1311.4 | 0.57213
|  |  | 1532.6 | 1311.6 | 0.57213
|  |  | 1532.8 | 1311.8 | 0.47618
|  |  | 1533 | 1312 | 0.57213
|  |  | 1533.2 | 1312.2 | 0.47618
|  |  | 1533.4 | 1312.4 | 0.57213
|  |  | 1533.6 | 1312.6 | 0.57213
|  |  | 1533.8 | 1312.8 | 0.57213
|  |  | 1534 | 1313 | 0.57213
|  |  | 1534.2 | 1313.2 | 0.57213
|  |  | 1534.4 | 1313.4 | 0.57213
|  |  | 1534.6 | 1313.6 | 0.66813
|  |  | 1534.8 | 1313.8 | 0.66813
|  |  | 1535 | 1314 | 0.66813
|  |  | 1535.2 | 1314.2 | 0.66813
|  |  | 1535.4 | 1314.4 | 0.66813
|  |  | 1535.6 | 1314.6 | 0.66813
|  |  | 1535.8 | 1314.8 | 0.76408
|  |  | 1536 | 1315 | 0.76408
|  |  | 1536.2 | 1315.2 | 0.76408
|  |  | 1536.4 | 1315.4 | 0.76408
|  |  | 1536.6 | 1315.6 | 0.76408
|  |  | 1536.8 | 1315.8 | 0.95602
|  |  | 1537 | 1316 | 0.86003
|  |  | 1537.2 | 1316.2 | 0.95602
|  |  | 1537.4 | 1316.4 | 0.95602
|  |  | 1537.6 | 1316.6 | 0.95602
|  |  | 1537.8 | 1316.8 | 1.052
|  |  | 1538 | 1317 | 1.052
|  |  | 1538.2 | 1317.2 | 1.052
|  |  | 1538.4 | 1317.4 | 1.052
|  |  | 1538.6 | 1317.6 | 1.2439
|  |  | 1538.8 | 1317.8 | 1.2439
|  |  | 1539 | 1318 | 1.2439
|  |  | 1539.2 | 1318.2 | 1.2439
|  |  | 1539.4 | 1318.4 | 1.3399
|  |  | 1539.6 | 1318.6 | 1.4359
|  |  | 1539.8 | 1318.8 | 1.4359
|  |  | 1540 | 1319 | 1.4359
|  |  | 1540.2 | 1319.2 | 1.6278
|  |  | 1540.4 | 1319.4 | 1.6278
|  |  | 1540.6 | 1319.6 | 1.6278
|  |  | 1540.8 | 1319.8 | 1.6278
|  |  | 1541 | 1320 | 1.7237
|  |  | 1541.2 | 1320.2 | 1.6278
|  |  | 1541.4 | 1320.4 | 2.0116
|  |  | 1541.6 | 1320.6 | 26.0035
|  |  | 1541.8 | 1320.8 | 34.1607
|  |  | 1542 | 1321 | 31.0897
|  |  | 1542.2 | 1321.2 | 52.9702
|  |  | 1542.4 | 1321.4 | 55.4654
|  |  | 1542.6 | 1321.6 | 64.3903
|  |  | 1542.8 | 1321.8 | 117.2683
|  |  | 1543 | 1322 | 122.2586
|  |  | 1543.2 | 1322.2 | 123.0263
|  |  | 1543.4 | 1322.4 | 123.2182
|  |  | 1543.6 | 1322.6 | 123.4102
|  |  | 1543.8 | 1322.8 | 123.6021
|  |  | 1544 | 1323 | 123.6021
|  |  | 1544.2 | 1323.2 | 123.6981
|  |  | 1544.4 | 1323.4 | 123.7941
|  |  | 1544.6 | 1323.6 | 123.89
|  |  | 1544.8 | 1323.8 | 123.89
|  |  | 1545 | 1324 | 123.89
|  |  | 1545.2 | 1324.2 | 123.7941
|  |  | 1545.4 | 1324.4 | 123.6981
|  |  | 1545.6 | 1324.6 | 123.7941
|  |  | 1545.8 | 1324.8 | 123.89
|  |  | 1546 | 1325 | 123.89
|  |  | 1546.2 | 1325.2 | 123.89
|  |  | 1546.4 | 1325.4 | 123.89
|  |  | 1546.6 | 1325.6 | 123.89
|  |  | 1546.8 | 1325.8 | 123.7941
|  |  | 1547 | 1326 | 123.6981
|  |  | 1547.2 | 1326.2 | 123.7941
|  |  | 1547.4 | 1326.4 | 123.6981
|  |  | 1547.6 | 1326.6 | 123.6981
|  |  | 1547.8 | 1326.8 | 123.6981
|  |  | 1548 | 1327 | 123.6981
|  |  | 1548.2 | 1327.2 | 123.7941
|  |  | 1548.4 | 1327.4 | 123.89
|  |  | 1548.6 | 1327.6 | 123.89
|  |  | 1548.8 | 1327.8 | 123.7941
|  |  | 1549 | 1328 | 123.7941
|  |  | 1549.2 | 1328.2 | 123.6981
|  |  | 1549.4 | 1328.4 | 123.7941
|  |  | 1549.6 | 1328.6 | 123.89
|  |  | 1549.8 | 1328.8 | 123.986
|  |  | 1550 | 1329 | 124.082
|  |  | 1550.2 | 1329.2 | 124.2739
|  |  | 1550.4 | 1329.4 | 124.4658
|  |  | 1550.6 | 1329.6 | 124.6577
|  |  | 1550.8 | 1329.8 | 124.5618
|  |  | 1551 | 1330 | 124.7537
|  |  | 1551.2 | 1330.2 | 124.6577
|  |  | 1551.4 | 1330.4 | 124.6577
|  |  | 1551.6 | 1330.6 | 124.6577
|  |  | 1551.8 | 1330.8 | 124.6577
|  |  | 1552 | 1331 | 124.7537
|  |  | 1552.2 | 1331.2 | 124.8497
|  |  | 1552.4 | 1331.4 | 124.8497
|  |  | 1552.6 | 1331.6 | 124.8497
|  |  | 1552.8 | 1331.8 | 124.8497
|  |  | 1553 | 1332 | 124.8497
|  |  | 1553.2 | 1332.2 | 124.7537
|  |  | 1553.4 | 1332.4 | 124.9457
|  |  | 1553.6 | 1332.6 | 124.8497
|  |  | 1553.8 | 1332.8 | 124.8497
|  |  | 1554 | 1333 | 124.7537
|  |  | 1554.2 | 1333.2 | 124.8497
|  |  | 1554.4 | 1333.4 | 124.8497
|  |  | 1554.6 | 1333.6 | 124.8497
|  |  | 1554.8 | 1333.8 | 124.8497
|  |  | 1555 | 1334 | 124.7537
|  |  | 1555.2 | 1334.2 | 124.8497
|  |  | 1555.4 | 1334.4 | 124.8497
|  |  | 1555.6 | 1334.6 | 124.8497
|  |  | 1555.8 | 1334.8 | 124.8497
|  |  | 1556 | 1335 | 124.7537
|  |  | 1556.2 | 1335.2 | 124.8497
|  |  | 1556.4 | 1335.4 | 124.8497
|  |  | 1556.6 | 1335.6 | 124.8497
|  |  | 1556.8 | 1335.8 | 124.9457
|  |  | 1557 | 1336 | 124.8497
|  |  | 1557.2 | 1336.2 | 124.9457
|  |  | 1557.4 | 1336.4 | 124.9457
|  |  | 1557.6 | 1336.6 | 124.9457
|  |  | 1557.8 | 1336.8 | 125.1376
|  |  | 1558 | 1337 | 125.0416
|  |  | 1558.2 | 1337.2 | 125.2336
|  |  | 1558.4 | 1337.4 | 125.1376
|  |  | 1558.6 | 1337.6 | 125.1376
|  |  | 1558.8 | 1337.8 | 125.1376
|  |  | 1559 | 1338 | 125.1376
|  |  | 1559.2 | 1338.2 | 125.2336
|  |  | 1559.4 | 1338.4 | 125.1376
|  |  | 1559.6 | 1338.6 | 125.1376
|  |  | 1559.8 | 1338.8 | 125.2336
|  |  | 1560 | 1339 | 125.1376
|  |  | 1560.2 | 1339.2 | 125.2336
|  |  | 1560.4 | 1339.4 | 125.2336
|  |  | 1560.6 | 1339.6 | 125.2336
|  |  | 1560.8 | 1339.8 | 125.2336
|  |  | 1561 | 1340 | 125.2336
|  |  | 1561.2 | 1340.2 | 125.2336
|  |  | 1561.4 | 1340.4 | 125.2336
|  |  | 1561.6 | 1340.6 | 125.3295
|  |  | 1561.8 | 1340.8 | 125.2336
|  |  | 1562 | 1341 | 125.2336
|  |  | 1562.2 | 1341.2 | 125.3295
|  |  | 1562.4 | 1341.4 | 125.2336
|  |  | 1562.6 | 1341.6 | 125.3295
|  |  | 1562.8 | 1341.8 | 125.3295
|  |  | 1563 | 1342 | 125.3295
|  |  | 1563.2 | 1342.2 | 125.3295
|  |  | 1563.4 | 1342.4 | 125.3295
|  |  | 1563.6 | 1342.6 | 125.3295
|  |  | 1563.8 | 1342.8 | 125.3295
|  |  | 1564 | 1343 | 125.3295
|  |  | 1564.2 | 1343.2 | 125.4255
|  |  | 1564.4 | 1343.4 | 125.4255
|  |  | 1564.6 | 1343.6 | 125.3295
|  |  | 1564.8 | 1343.8 | 125.4255
|  |  | 1565 | 1344 | 125.4255
|  |  | 1565.2 | 1344.2 | 125.4255
|  |  | 1565.4 | 1344.4 | 125.4255
|  |  | 1565.6 | 1344.6 | 125.3295
|  |  | 1565.8 | 1344.8 | 125.4255
|  |  | 1566 | 1345 | 125.4255
|  |  | 1566.2 | 1345.2 | 125.4255
|  |  | 1566.4 | 1345.4 | 125.4255
|  |  | 1566.6 | 1345.6 | 125.4255
|  |  | 1566.8 | 1345.8 | 125.4255
|  |  | 1567 | 1346 | 125.4255
|  |  | 1567.2 | 1346.2 | 125.4255
|  |  | 1567.4 | 1346.4 | 125.4255
|  |  | 1567.6 | 1346.6 | 125.4255
|  |  | 1567.8 | 1346.8 | 125.5215
|  |  | 1568 | 1347 | 125.4255
|  |  | 1568.2 | 1347.2 | 125.5215
|  |  | 1568.4 | 1347.4 | 125.5215
|  |  | 1568.6 | 1347.6 | 125.5215
|  |  | 1568.8 | 1347.8 | 125.5215
|  |  | 1569 | 1348 | 125.5215
|  |  | 1569.2 | 1348.2 | 125.5215
|  |  | 1569.4 | 1348.4 | 125.5215
|  |  | 1569.6 | 1348.6 | 125.5215
|  |  | 1569.8 | 1348.8 | 125.5215
|  |  | 1570 | 1349 | 125.5215
|  |  | 1570.2 | 1349.2 | 125.5215
|  |  | 1570.4 | 1349.4 | 125.5215
|  |  | 1570.6 | 1349.6 | 125.6175
|  |  | 1570.8 | 1349.8 | 125.6175
|  |  | 1571 | 1350 | 125.5215
|  |  | 1571.2 | 1350.2 | 125.6175
|  |  | 1571.4 | 1350.4 | 125.5215
|  |  | 1571.6 | 1350.6 | 125.5215
|  |  | 1571.8 | 1350.8 | 125.5215
|  |  | 1572 | 1351 | 125.5215
|  |  | 1572.2 | 1351.2 | 125.6175
|  |  | 1572.4 | 1351.4 | 125.5215
|  |  | 1572.6 | 1351.6 | 125.6175
|  |  | 1572.8 | 1351.8 | 125.6175
|  |  | 1573 | 1352 | 125.6175
|  |  | 1573.2 | 1352.2 | 125.5215
|  |  | 1573.4 | 1352.4 | 125.6175
|  |  | 1573.6 | 1352.6 | 125.6175
|  |  | 1573.8 | 1352.8 | 125.6175
|  |  | 1574 | 1353 | 125.6175
|  |  | 1574.2 | 1353.2 | 125.6175
|  |  | 1574.4 | 1353.4 | 125.5215
|  |  | 1574.6 | 1353.6 | 125.6175
|  |  | 1574.8 | 1353.8 | 125.6175
|  |  | 1575 | 1354 | 125.6175
|  |  | 1575.2 | 1354.2 | 125.6175
|  |  | 1575.4 | 1354.4 | 125.6175
|  |  | 1575.6 | 1354.6 | 125.6175
|  |  | 1575.8 | 1354.8 | 125.5215
|  |  | 1576 | 1355 | 125.6175
|  |  | 1576.2 | 1355.2 | 125.6175
|  |  | 1576.4 | 1355.4 | 125.5215
|  |  | 1576.6 | 1355.6 | 125.6175
|  |  | 1576.8 | 1355.8 | 125.5215
|  |  | 1577 | 1356 | 125.6175
|  |  | 1577.2 | 1356.2 | 125.6175
|  |  | 1577.4 | 1356.4 | 125.7134
|  |  | 1577.6 | 1356.6 | 125.6175
|  |  | 1577.8 | 1356.8 | 125.6175
|  |  | 1578 | 1357 | 125.6175
|  |  | 1578.2 | 1357.2 | 125.6175
|  |  | 1578.4 | 1357.4 | 125.6175
|  |  | 1578.6 | 1357.6 | 125.5215
|  |  | 1578.8 | 1357.8 | 125.6175
|  |  | 1579 | 1358 | 125.6175
|  |  | 1579.2 | 1358.2 | 125.6175
|  |  | 1579.4 | 1358.4 | 125.6175
|  |  | 1579.6 | 1358.6 | 125.6175
|  |  | 1579.8 | 1358.8 | 125.6175
|  |  | 1580 | 1359 | 125.6175
|  |  | 1580.2 | 1359.2 | 125.7134
|  |  | 1580.4 | 1359.4 | 125.7134
|  |  | 1580.6 | 1359.6 | 125.7134
|  |  | 1580.8 | 1359.8 | 125.6175
|  |  | 1581 | 1360 | 125.6175
|  |  | 1581.2 | 1360.2 | 125.7134
|  |  | 1581.4 | 1360.4 | 125.7134
|  |  | 1581.6 | 1360.6 | 125.6175
|  |  | 1581.8 | 1360.8 | 125.6175
|  |  | 1582 | 1361 | 125.6175
|  |  | 1582.2 | 1361.2 | 125.7134
|  |  | 1582.4 | 1361.4 | 125.6175
|  |  | 1582.6 | 1361.6 | 125.6175
|  |  | 1582.8 | 1361.8 | 125.6175
|  |  | 1583 | 1362 | 125.7134
|  |  | 1583.2 | 1362.2 | 125.7134
|  |  | 1583.4 | 1362.4 | 125.7134
|  |  | 1583.6 | 1362.6 | 125.7134
|  |  | 1583.8 | 1362.8 | 125.7134
|  |  | 1584 | 1363 | 125.7134
|  |  | 1584.2 | 1363.2 | 125.8094
|  |  | 1584.4 | 1363.4 | 125.7134
|  |  | 1584.6 | 1363.6 | 125.8094
|  |  | 1584.8 | 1363.8 | 125.8094
|  |  | 1585 | 1364 | 125.8094
|  |  | 1585.2 | 1364.2 | 125.8094
|  |  | 1585.4 | 1364.4 | 125.8094
|  |  | 1585.6 | 1364.6 | 125.8094
|  |  | 1585.8 | 1364.8 | 125.8094
|  |  | 1586 | 1365 | 125.7134
|  |  | 1586.2 | 1365.2 | 125.8094
|  |  | 1586.4 | 1365.4 | 125.7134
|  |  | 1586.6 | 1365.6 | 125.8094
|  |  | 1586.8 | 1365.8 | 125.8094
|  |  | 1587 | 1366 | 125.9054
|  |  | 1587.2 | 1366.2 | 125.8094
|  |  | 1587.4 | 1366.4 | 125.8094
|  |  | 1587.6 | 1366.6 | 125.9054
|  |  | 1587.8 | 1366.8 | 125.7134
|  |  | 1588 | 1367 | 125.7134
|  |  | 1588.2 | 1367.2 | 125.7134
|  |  | 1588.4 | 1367.4 | 125.7134
|  |  | 1588.6 | 1367.6 | 125.7134
|  |  | 1588.8 | 1367.8 | 125.8094
|  |  | 1589 | 1368 | 125.7134
|  |  | 1589.2 | 1368.2 | 125.7134
|  |  | 1589.4 | 1368.4 | 125.7134
|  |  | 1589.6 | 1368.6 | 125.7134
|  |  | 1589.8 | 1368.8 | 125.7134
|  |  | 1590 | 1369 | 125.7134
|  |  | 1590.2 | 1369.2 | 125.7134
|  |  | 1590.4 | 1369.4 | 125.7134
|  |  | 1590.6 | 1369.6 | 125.7134
|  |  | 1590.8 | 1369.8 | 125.8094
|  |  | 1591 | 1370 | 125.7134
|  |  | 1591.2 | 1370.2 | 125.8094
|  |  | 1591.4 | 1370.4 | 125.7134
|  |  | 1591.6 | 1370.6 | 125.7134
|  |  | 1591.8 | 1370.8 | 125.8094
|  |  | 1592 | 1371 | 125.7134
|  |  | 1592.2 | 1371.2 | 125.8094
|  |  | 1592.4 | 1371.4 | 125.8094
|  |  | 1592.6 | 1371.6 | 125.7134
|  |  | 1592.8 | 1371.8 | 125.8094
|  |  | 1593 | 1372 | 125.8094
|  |  | 1593.2 | 1372.2 | 125.8094
|  |  | 1593.4 | 1372.4 | 125.8094
|  |  | 1593.6 | 1372.6 | 125.8094
|  |  | 1593.8 | 1372.8 | 125.8094
|  |  | 1594 | 1373 | 125.7134
|  |  | 1594.2 | 1373.2 | 125.9054
|  |  | 1594.4 | 1373.4 | 125.8094
|  |  | 1594.6 | 1373.6 | 125.8094
|  |  | 1594.8 | 1373.8 | 125.9054
|  |  | 1595 | 1374 | 125.8094
|  |  | 1595.2 | 1374.2 | 125.8094
|  |  | 1595.4 | 1374.4 | 125.9054
|  |  | 1595.6 | 1374.6 | 125.8094
|  |  | 1595.8 | 1374.8 | 125.8094
|  |  | 1596 | 1375 | 125.6175
|  |  | 1596.2 | 1375.2 | 125.8094
|  |  | 1596.4 | 1375.4 | 125.7134
|  |  | 1596.6 | 1375.6 | 125.9054
|  |  | 1596.8 | 1375.8 | 125.9054
|  |  | 1597 | 1376 | 125.9054
|  |  | 1597.2 | 1376.2 | 125.9054
|  |  | 1597.4 | 1376.4 | 125.9054
|  |  | 1597.6 | 1376.6 | 125.9054
|  |  | 1597.8 | 1376.8 | 125.8094
|  |  | 1598 | 1377 | 125.8094
|  |  | 1598.2 | 1377.2 | 125.9054
|  |  | 1598.4 | 1377.4 | 125.9054
|  |  | 1598.6 | 1377.6 | 125.9054
|  |  | 1598.8 | 1377.8 | 125.9054
|  |  | 1599 | 1378 | 126.0013
|  |  | 1599.2 | 1378.2 | 125.9054
|  |  | 1599.4 | 1378.4 | 126.0013
|  |  | 1599.6 | 1378.6 | 125.9054
|  |  | 1599.8 | 1378.8 | 126.0013
|  |  | 1600 | 1379 | 125.9054
|  |  | 1600.2 | 1379.2 | 125.9054
|  |  | 1600.4 | 1379.4 | 126.0013
|  |  | 1600.6 | 1379.6 | 125.9054
|  |  | 1600.8 | 1379.8 | 125.9054
|  |  | 1601 | 1380 | 125.9054
|  |  | 1601.2 | 1380.2 | 125.9054
|  |  | 1601.4 | 1380.4 | 126.0013
|  |  | 1601.6 | 1380.6 | 125.9054
|  |  | 1601.8 | 1380.8 | 125.9054
|  |  | 1602 | 1381 | 126.0013
|  |  | 1602.2 | 1381.2 | 126.0013
|  |  | 1602.4 | 1381.4 | 126.0013
|  |  | 1602.6 | 1381.6 | 126.0013
|  |  | 1602.8 | 1381.8 | 126.0013
|  |  | 1603 | 1382 | 126.0013
|  |  | 1603.2 | 1382.2 | 126.0013
|  |  | 1603.4 | 1382.4 | 126.0013
|  |  | 1603.6 | 1382.6 | 125.9054
|  |  | 1603.8 | 1382.8 | 126.0013
|  |  | 1604 | 1383 | 125.9054
|  |  | 1604.2 | 1383.2 | 126.0013
|  |  | 1604.4 | 1383.4 | 125.9054
|  |  | 1604.6 | 1383.6 | 125.9054
|  |  | 1604.8 | 1383.8 | 126.0013
|  |  | 1605 | 1384 | 126.0013
|  |  | 1605.2 | 1384.2 | 126.0013
|  |  | 1605.4 | 1384.4 | 125.9054
|  |  | 1605.6 | 1384.6 | 126.0013
|  |  | 1605.8 | 1384.8 | 125.9054
|  |  | 1606 | 1385 | 126.0013
|  |  | 1606.2 | 1385.2 | 126.0013
|  |  | 1606.4 | 1385.4 | 125.9054
|  |  | 1606.6 | 1385.6 | 125.9054
|  |  | 1606.8 | 1385.8 | 126.0013
|  |  | 1607 | 1386 | 126.0013
|  |  | 1607.2 | 1386.2 | 126.0013
|  |  | 1607.4 | 1386.4 | 126.0013
|  |  | 1607.6 | 1386.6 | 126.0013
|  |  | 1607.8 | 1386.8 | 126.0013
|  |  | 1608 | 1387 | 126.0013
|  |  | 1608.2 | 1387.2 | 126.0973
|  |  | 1608.4 | 1387.4 | 126.0973
|  |  | 1608.6 | 1387.6 | 126.0973
|  |  | 1608.8 | 1387.8 | 126.0973
|  |  | 1609 | 1388 | 126.0973
|  |  | 1609.2 | 1388.2 | 126.0013
|  |  | 1609.4 | 1388.4 | 126.0013
|  |  | 1609.6 | 1388.6 | 126.0013
|  |  | 1609.8 | 1388.8 | 126.0013
|  |  | 1610 | 1389 | 126.0013
|  |  | 1610.2 | 1389.2 | 125.9054
|  |  | 1610.4 | 1389.4 | 125.9054
|  |  | 1610.6 | 1389.6 | 126.0013
|  |  | 1610.8 | 1389.8 | 125.9054
|  |  | 1611 | 1390 | 126.0013
|  |  | 1611.2 | 1390.2 | 126.0013
|  |  | 1611.4 | 1390.4 | 125.9054
|  |  | 1611.6 | 1390.6 | 126.0013
|  |  | 1611.8 | 1390.8 | 125.9054
|  |  | 1612 | 1391 | 125.9054
|  |  | 1612.2 | 1391.2 | 125.9054
|  |  | 1612.4 | 1391.4 | 125.9054
|  |  | 1612.6 | 1391.6 | 125.9054
|  |  | 1612.8 | 1391.8 | 125.9054
|  |  | 1613 | 1392 | 126.0013
|  |  | 1613.2 | 1392.2 | 125.9054
|  |  | 1613.4 | 1392.4 | 126.0013
|  |  | 1613.6 | 1392.6 | 126.0013
|  |  | 1613.8 | 1392.8 | 125.9054
|  |  | 1614 | 1393 | 126.0013
|  |  | 1614.2 | 1393.2 | 126.0013
|  |  | 1614.4 | 1393.4 | 126.0013
|  |  | 1614.6 | 1393.6 | 125.9054
|  |  | 1614.8 | 1393.8 | 125.9054
|  |  | 1615 | 1394 | 125.9054
|  |  | 1615.2 | 1394.2 | 125.9054
|  |  | 1615.4 | 1394.4 | 125.9054
|  |  | 1615.6 | 1394.6 | 126.0013
|  |  | 1615.8 | 1394.8 | 126.0013
|  |  | 1616 | 1395 | 125.9054
|  |  | 1616.2 | 1395.2 | 126.0013
|  |  | 1616.4 | 1395.4 | 126.0973
|  |  | 1616.6 | 1395.6 | 125.9054
|  |  | 1616.8 | 1395.8 | 126.0973
|  |  | 1617 | 1396 | 126.0013
|  |  | 1617.2 | 1396.2 | 126.0013
|  |  | 1617.4 | 1396.4 | 126.0013
|  |  | 1617.6 | 1396.6 | 126.0013
|  |  | 1617.8 | 1396.8 | 125.9054
|  |  | 1618 | 1397 | 125.9054
|  |  | 1618.2 | 1397.2 | 125.9054
|  |  | 1618.4 | 1397.4 | 125.9054
|  |  | 1618.6 | 1397.6 | 125.9054
|  |  | 1618.8 | 1397.8 | 126.0013
|  |  | 1619 | 1398 | 125.9054
|  |  | 1619.2 | 1398.2 | 126.0013
|  |  | 1619.4 | 1398.4 | 125.9054
|  |  | 1619.6 | 1398.6 | 125.9054
|  |  | 1619.8 | 1398.8 | 125.9054
|  |  | 1620 | 1399 | 125.9054
|  |  | 1620.2 | 1399.2 | 126.0013
|  |  | 1620.4 | 1399.4 | 126.0013
|  |  | 1620.6 | 1399.6 | 126.0013
|  |  | 1620.8 | 1399.8 | 126.0013
|  |  | 1621 | 1400 | 126.0013
|  |  | 1621.2 | 1400.2 | 126.0013
|  |  | 1621.4 | 1400.4 | 125.9054
|  |  | 1621.6 | 1400.6 | 126.0013
|  |  | 1621.8 | 1400.8 | 126.0013
|  |  | 1622 | 1401 | 125.9054
|  |  | 1622.2 | 1401.2 | 126.0013
|  |  | 1622.4 | 1401.4 | 125.9054
|  |  | 1622.6 | 1401.6 | 125.9054
|  |  | 1622.8 | 1401.8 | 126.0013
|  |  | 1623 | 1402 | 125.9054
|  |  | 1623.2 | 1402.2 | 126.0013
|  |  | 1623.4 | 1402.4 | 126.0973
|  |  | 1623.6 | 1402.6 | 126.0973
|  |  | 1623.8 | 1402.8 | 126.0973
|  |  | 1624 | 1403 | 126.0013
|  |  | 1624.2 | 1403.2 | 126.0973
|  |  | 1624.4 | 1403.4 | 126.0013
|  |  | 1624.6 | 1403.6 | 126.0973
|  |  | 1624.8 | 1403.8 | 126.0013
|  |  | 1625 | 1404 | 126.0973
|  |  | 1625.2 | 1404.2 | 126.0013
|  |  | 1625.4 | 1404.4 | 126.0013
|  |  | 1625.6 | 1404.6 | 126.0973
|  |  | 1625.8 | 1404.8 | 126.1932
|  |  | 1626 | 1405 | 126.0973
|  |  | 1626.2 | 1405.2 | 126.0973
|  |  | 1626.4 | 1405.4 | 126.1932
|  |  | 1626.6 | 1405.6 | 126.1932
|  |  | 1626.8 | 1405.8 | 126.1932
|  |  | 1627 | 1406 | 126.1932
|  |  | 1627.2 | 1406.2 | 126.1932
|  |  | 1627.4 | 1406.4 | 126.2892
|  |  | 1627.6 | 1406.6 | 126.1932
|  |  | 1627.8 | 1406.8 | 126.1932
|  |  | 1628 | 1407 | 126.0973
|  |  | 1628.2 | 1407.2 | 126.0973
|  |  | 1628.4 | 1407.4 | 126.1932
|  |  | 1628.6 | 1407.6 | 126.1932
|  |  | 1628.8 | 1407.8 | 126.1932
|  |  | 1629 | 1408 | 126.1932
|  |  | 1629.2 | 1408.2 | 126.0973
|  |  | 1629.4 | 1408.4 | 126.0973
|  |  | 1629.6 | 1408.6 | 126.0973
|  |  | 1629.8 | 1408.8 | 126.1932
|  |  | 1630 | 1409 | 126.0013
|  |  | 1630.2 | 1409.2 | 126.0973
|  |  | 1630.4 | 1409.4 | 126.1932
|  |  | 1630.6 | 1409.6 | 126.1932
|  |  | 1630.8 | 1409.8 | 126.2892
|  |  | 1631 | 1410 | 126.1932
|  |  | 1631.2 | 1410.2 | 126.1932
|  |  | 1631.4 | 1410.4 | 126.1932
|  |  | 1631.6 | 1410.6 | 126.1932
|  |  | 1631.8 | 1410.8 | 126.2892
|  |  | 1632 | 1411 | 126.0973
|  |  | 1632.2 | 1411.2 | 126.1932
|  |  | 1632.4 | 1411.4 | 126.0973
|  |  | 1632.6 | 1411.6 | 126.1932
|  |  | 1632.8 | 1411.8 | 126.0973
|  |  | 1633 | 1412 | 126.0013
|  |  | 1633.2 | 1412.2 | 126.1932
|  |  | 1633.4 | 1412.4 | 126.1932
|  |  | 1633.6 | 1412.6 | 126.1932
|  |  | 1633.8 | 1412.8 | 126.1932
|  |  | 1634 | 1413 | 126.0973
|  |  | 1634.2 | 1413.2 | 126.1932
|  |  | 1634.4 | 1413.4 | 126.0973
|  |  | 1634.6 | 1413.6 | 126.0973
|  |  | 1634.8 | 1413.8 | 126.1932
|  |  | 1635 | 1414 | 126.0973
|  |  | 1635.2 | 1414.2 | 126.0973
|  |  | 1635.4 | 1414.4 | 126.0973
|  |  | 1635.6 | 1414.6 | 126.0973
|  |  | 1635.8 | 1414.8 | 126.0973
|  |  | 1636 | 1415 | 126.0973
|  |  | 1636.2 | 1415.2 | 126.0973
|  |  | 1636.4 | 1415.4 | 126.0973
|  |  | 1636.6 | 1415.6 | 126.0973
|  |  | 1636.8 | 1415.8 | 126.0973
|  |  | 1637 | 1416 | 126.0013
|  |  | 1637.2 | 1416.2 | 126.0013
|  |  | 1637.4 | 1416.4 | 126.0013
|  |  | 1637.6 | 1416.6 | 126.0013
|  |  | 1637.8 | 1416.8 | 126.0013
|  |  | 1638 | 1417 | 126.0013
|  |  | 1638.2 | 1417.2 | 126.0013
|  |  | 1638.4 | 1417.4 | 126.0013
|  |  | 1638.6 | 1417.6 | 126.0973
|  |  | 1638.8 | 1417.8 | 126.0013
|  |  | 1639 | 1418 | 126.0013
|  |  | 1639.2 | 1418.2 | 126.0013
|  |  | 1639.4 | 1418.4 | 126.0013
|  |  | 1639.6 | 1418.6 | 126.0013
|  |  | 1639.8 | 1418.8 | 126.0013
|  |  | 1640 | 1419 | 126.0973
|  |  | 1640.2 | 1419.2 | 126.0973
|  |  | 1640.4 | 1419.4 | 126.1932
|  |  | 1640.6 | 1419.6 | 126.1932
|  |  | 1640.8 | 1419.8 | 126.0973
|  |  | 1641 | 1420 | 126.1932
|  |  | 1641.2 | 1420.2 | 126.0973
|  |  | 1641.4 | 1420.4 | 126.1932
|  |  | 1641.6 | 1420.6 | 126.1932
|  |  | 1641.8 | 1420.8 | 126.0013
|  |  | 1642 | 1421 | 126.1932
|  |  | 1642.2 | 1421.2 | 126.0973
|  |  | 1642.4 | 1421.4 | 126.0973
|  |  | 1642.6 | 1421.6 | 126.0973
|  |  | 1642.8 | 1421.8 | 126.0973
|  |  | 1643 | 1422 | 126.0973
|  |  | 1643.2 | 1422.2 | 126.0013
|  |  | 1643.4 | 1422.4 | 126.0973
|  |  | 1643.6 | 1422.6 | 126.0973
|  |  | 1643.8 | 1422.8 | 126.0973
|  |  | 1644 | 1423 | 126.0013
|  |  | 1644.2 | 1423.2 | 126.0973
|  |  | 1644.4 | 1423.4 | 126.0973
|  |  | 1644.6 | 1423.6 | 126.0973
|  |  | 1644.8 | 1423.8 | 126.0973
|  |  | 1645 | 1424 | 126.0973
|  |  | 1645.2 | 1424.2 | 126.0013
|  |  | 1645.4 | 1424.4 | 126.0973
|  |  | 1645.6 | 1424.6 | 126.0013
|  |  | 1645.8 | 1424.8 | 126.0973
|  |  | 1646 | 1425 | 126.0013
|  |  | 1646.2 | 1425.2 | 126.0973
|  |  | 1646.4 | 1425.4 | 126.0013
|  |  | 1646.6 | 1425.6 | 126.0973
|  |  | 1646.8 | 1425.8 | 126.0973
|  |  | 1647 | 1426 | 125.9054
|  |  | 1647.2 | 1426.2 | 126.0973
|  |  | 1647.4 | 1426.4 | 126.0973
|  |  | 1647.6 | 1426.6 | 126.0013
|  |  | 1647.8 | 1426.8 | 126.0973
|  |  | 1648 | 1427 | 125.9054
|  |  | 1648.2 | 1427.2 | 126.0013
|  |  | 1648.4 | 1427.4 | 126.0013
|  |  | 1648.6 | 1427.6 | 125.9054
|  |  | 1648.8 | 1427.8 | 126.0013
|  |  | 1649 | 1428 | 125.9054
|  |  | 1649.2 | 1428.2 | 126.0013
|  |  | 1649.4 | 1428.4 | 126.0013
|  |  | 1649.6 | 1428.6 | 126.0013
|  |  | 1649.8 | 1428.8 | 126.0013
|  |  | 1650 | 1429 | 125.8094
|  |  | 1650.2 | 1429.2 | 126.0013
|  |  | 1650.4 | 1429.4 | 126.0013
|  |  | 1650.6 | 1429.6 | 126.0973
|  |  | 1650.8 | 1429.8 | 126.0013
|  |  | 1651 | 1430 | 126.0973
|  |  | 1651.2 | 1430.2 | 126.1932
|  |  | 1651.4 | 1430.4 | 126.1932
|  |  | 1651.6 | 1430.6 | 126.2892
|  |  | 1651.8 | 1430.8 | 125.9054
|  |  | 1652 | 1431 | 125.5215
|  |  | 1652.2 | 1431.2 | 125.5215
|  |  | 1652.4 | 1431.4 | 125.5215
|  |  | 1652.6 | 1431.6 | 125.4255
|  |  | 1652.8 | 1431.8 | 125.8094
|  |  | 1653 | 1432 | 125.8094
|  |  | 1653.2 | 1432.2 | 125.1376
|  |  | 1653.4 | 1432.4 | 125.7134
|  |  | 1653.6 | 1432.6 | 126.0013
|  |  | 1653.8 | 1432.8 | 125.6175
|  |  | 1654 | 1433 | 125.7134
|  |  | 1654.2 | 1433.2 | 125.9054
|  |  | 1654.4 | 1433.4 | 125.9054
|  |  | 1654.6 | 1433.6 | 125.9054
|  |  | 1654.8 | 1433.8 | 125.8094
|  |  | 1655 | 1434 | 125.9054
|  |  | 1655.2 | 1434.2 | 125.9054
|  |  | 1655.4 | 1434.4 | 125.8094
|  |  | 1655.6 | 1434.6 | 125.9054
|  |  | 1655.8 | 1434.8 | 126.0013
|  |  | 1656 | 1435 | 126.0013
|  |  | 1656.2 | 1435.2 | 125.9054
|  |  | 1656.4 | 1435.4 | 126.0013
|  |  | 1656.6 | 1435.6 | 126.0013
|  |  | 1656.8 | 1435.8 | 126.0013
|  |  | 1657 | 1436 | 126.0973
|  |  | 1657.2 | 1436.2 | 126.0013
|  |  | 1657.4 | 1436.4 | 126.0013
|  |  | 1657.6 | 1436.6 | 126.0973
|  |  | 1657.8 | 1436.8 | 126.0973
|  |  | 1658 | 1437 | 126.0013
|  |  | 1658.2 | 1437.2 | 126.0013
|  |  | 1658.4 | 1437.4 | 126.0013
|  |  | 1658.6 | 1437.6 | 126.0013
|  |  | 1658.8 | 1437.8 | 126.0013
|  |  | 1659 | 1438 | 126.0013
|  |  | 1659.2 | 1438.2 | 126.0013
|  |  | 1659.4 | 1438.4 | 125.9054
|  |  | 1659.6 | 1438.6 | 125.9054
|  |  | 1659.8 | 1438.8 | 126.0013
|  |  | 1660 | 1439 | 125.9054
|  |  | 1660.2 | 1439.2 | 125.9054
|  |  | 1660.4 | 1439.4 | 126.0013
|  |  | 1660.6 | 1439.6 | 125.9054
|  |  | 1660.8 | 1439.8 | 126.0013
|  |  | 1661 | 1440 | 125.9054
|  |  | 1661.2 | 1440.2 | 126.0013
|  |  | 1661.4 | 1440.4 | 126.0973
|  |  | 1661.6 | 1440.6 | 126.1932
|  |  | 1661.8 | 1440.8 | 126.0973
|  |  | 1662 | 1441 | 126.0973
|  |  | 1662.2 | 1441.2 | 126.0013
|  |  | 1662.4 | 1441.4 | 126.0013
|  |  | 1662.6 | 1441.6 | 126.0013
|  |  | 1662.8 | 1441.8 | 126.0013
|  |  | 1663 | 1442 | 126.0013
|  |  | 1663.2 | 1442.2 | 126.0013
|  |  | 1663.4 | 1442.4 | 126.0013
|  |  | 1663.6 | 1442.6 | 126.0013
|  |  | 1663.8 | 1442.8 | 126.0013
|  |  | 1664 | 1443 | 125.9054
|  |  | 1664.2 | 1443.2 | 126.0013
|  |  | 1664.4 | 1443.4 | 126.0013
|  |  | 1664.6 | 1443.6 | 126.0013
|  |  | 1664.8 | 1443.8 | 125.9054
|  |  | 1665 | 1444 | 125.9054
|  |  | 1665.2 | 1444.2 | 126.0013
|  |  | 1665.4 | 1444.4 | 126.0973
|  |  | 1665.6 | 1444.6 | 126.0973
|  |  | 1665.8 | 1444.8 | 126.0013
|  |  | 1666 | 1445 | 125.9054
|  |  | 1666.2 | 1445.2 | 126.0013
|  |  | 1666.4 | 1445.4 | 126.0013
|  |  | 1666.6 | 1445.6 | 126.0013
|  |  | 1666.8 | 1445.8 | 125.9054
|  |  | 1667 | 1446 | 126.0013
|  |  | 1667.2 | 1446.2 | 126.0013
|  |  | 1667.4 | 1446.4 | 125.9054
|  |  | 1667.6 | 1446.6 | 126.0013
|  |  | 1667.8 | 1446.8 | 126.0013
|  |  | 1668 | 1447 | 125.9054
|  |  | 1668.2 | 1447.2 | 126.0013
|  |  | 1668.4 | 1447.4 | 125.9054
|  |  | 1668.6 | 1447.6 | 125.9054
|  |  | 1668.8 | 1447.8 | 125.9054
|  |  | 1669 | 1448 | 126.0013
|  |  | 1669.2 | 1448.2 | 125.9054
|  |  | 1669.4 | 1448.4 | 126.0013
|  |  | 1669.6 | 1448.6 | 126.0013
|  |  | 1669.8 | 1448.8 | 126.0973
|  |  | 1670 | 1449 | 125.9054
|  |  | 1670.2 | 1449.2 | 125.9054
|  |  | 1670.4 | 1449.4 | 126.0013
|  |  | 1670.6 | 1449.6 | 126.0013
|  |  | 1670.8 | 1449.8 | 125.9054
|  |  | 1671 | 1450 | 125.9054
|  |  | 1671.2 | 1450.2 | 125.9054
|  |  | 1671.4 | 1450.4 | 126.0013
|  |  | 1671.6 | 1450.6 | 125.9054
|  |  | 1671.8 | 1450.8 | 125.9054
|  |  | 1672 | 1451 | 125.9054
|  |  | 1672.2 | 1451.2 | 125.9054
|  |  | 1672.4 | 1451.4 | 126.0013
|  |  | 1672.6 | 1451.6 | 125.9054
|  |  | 1672.8 | 1451.8 | 125.8094
|  |  | 1673 | 1452 | 125.9054
|  |  | 1673.2 | 1452.2 | 126.0013
|  |  | 1673.4 | 1452.4 | 125.7134
|  |  | 1673.6 | 1452.6 | 125.1376
|  |  | 1673.8 | 1452.8 | 125.2336
|  |  | 1674 | 1453 | 125.3295
|  |  | 1674.2 | 1453.2 | 125.9054
|  |  | 1674.4 | 1453.4 | 125.8094
|  |  | 1674.6 | 1453.6 | 125.5215
|  |  | 1674.8 | 1453.8 | 125.5215
|  |  | 1675 | 1454 | 125.6175
|  |  | 1675.2 | 1454.2 | 125.6175
|  |  | 1675.4 | 1454.4 | 125.5215
|  |  | 1675.6 | 1454.6 | 125.7134
|  |  | 1675.8 | 1454.8 | 125.8094
|  |  | 1676 | 1455 | 126.0973
|  |  | 1676.2 | 1455.2 | 126.2892
|  |  | 1676.4 | 1455.4 | 126.2892
|  |  | 1676.6 | 1455.6 | 126.1932
|  |  | 1676.8 | 1455.8 | 126.1932
|  |  | 1677 | 1456 | 126.0973
|  |  | 1677.2 | 1456.2 | 126.0973
|  |  | 1677.4 | 1456.4 | 126.0973
|  |  | 1677.6 | 1456.6 | 126.0973
|  |  | 1677.8 | 1456.8 | 126.0013
|  |  | 1678 | 1457 | 125.9054
|  |  | 1678.2 | 1457.2 | 126.0013
|  |  | 1678.4 | 1457.4 | 126.0973
|  |  | 1678.6 | 1457.6 | 126.0013
|  |  | 1678.8 | 1457.8 | 126.0013
|  |  | 1679 | 1458 | 126.0013
|  |  | 1679.2 | 1458.2 | 125.9054
|  |  | 1679.4 | 1458.4 | 126.0013
|  |  | 1679.6 | 1458.6 | 126.0013
|  |  | 1679.8 | 1458.8 | 126.0013
|  |  | 1680 | 1459 | 125.9054
|  |  | 1680.2 | 1459.2 | 125.9054
|  |  | 1680.4 | 1459.4 | 125.9054
|  |  | 1680.6 | 1459.6 | 125.9054
|  |  | 1680.8 | 1459.8 | 125.9054
|  |  | 1681 | 1460 | 125.9054
|  |  | 1681.2 | 1460.2 | 125.9054
|  |  | 1681.4 | 1460.4 | 125.9054
|  |  | 1681.6 | 1460.6 | 125.9054
|  |  | 1681.8 | 1460.8 | 125.9054
|  |  | 1682 | 1461 | 125.9054
|  |  | 1682.2 | 1461.2 | 125.9054
|  |  | 1682.4 | 1461.4 | 126.0013
|  |  | 1682.6 | 1461.6 | 125.9054
|  |  | 1682.8 | 1461.8 | 126.0013
|  |  | 1683 | 1462 | 126.0013
|  |  | 1683.2 | 1462.2 | 126.0013
|  |  | 1683.4 | 1462.4 | 126.0973
|  |  | 1683.6 | 1462.6 | 126.0973
|  |  | 1683.8 | 1462.8 | 126.0973
|  |  | 1684 | 1463 | 126.0013
|  |  | 1684.2 | 1463.2 | 126.0973
|  |  | 1684.4 | 1463.4 | 126.0013
|  |  | 1684.6 | 1463.6 | 126.0013
|  |  | 1684.8 | 1463.8 | 126.0013
|  |  | 1685 | 1464 | 126.0013
|  |  | 1685.2 | 1464.2 | 126.0013
|  |  | 1685.4 | 1464.4 | 126.0013
|  |  | 1685.6 | 1464.6 | 126.0973
|  |  | 1685.8 | 1464.8 | 126.0973
|  |  | 1686 | 1465 | 126.0013
|  |  | 1686.2 | 1465.2 | 126.0973
|  |  | 1686.4 | 1465.4 | 126.0973
|  |  | 1686.6 | 1465.6 | 126.0973
|  |  | 1686.8 | 1465.8 | 126.1932
|  |  | 1687 | 1466 | 126.0973
|  |  | 1687.2 | 1466.2 | 126.1932
|  |  | 1687.4 | 1466.4 | 126.1932
|  |  | 1687.6 | 1466.6 | 126.0973
|  |  | 1687.8 | 1466.8 | 126.1932
|  |  | 1688 | 1467 | 126.0973
|  |  | 1688.2 | 1467.2 | 126.1932
|  |  | 1688.4 | 1467.4 | 126.1932
|  |  | 1688.6 | 1467.6 | 126.1932
|  |  | 1688.8 | 1467.8 | 126.0973
|  |  | 1689 | 1468 | 125.9054
|  |  | 1689.2 | 1468.2 | 126.0013
|  |  | 1689.4 | 1468.4 | 126.0013
|  |  | 1689.6 | 1468.6 | 126.0973
|  |  | 1689.8 | 1468.8 | 126.0973
|  |  | 1690 | 1469 | 126.0013
|  |  | 1690.2 | 1469.2 | 126.0973
|  |  | 1690.4 | 1469.4 | 126.0973
|  |  | 1690.6 | 1469.6 | 126.1932
|  |  | 1690.8 | 1469.8 | 126.0973
|  |  | 1691 | 1470 | 126.1932
|  |  | 1691.2 | 1470.2 | 126.1932
|  |  | 1691.4 | 1470.4 | 126.1932
|  |  | 1691.6 | 1470.6 | 126.0973
|  |  | 1691.8 | 1470.8 | 126.0973
|  |  | 1692 | 1471 | 126.1932
|  |  | 1692.2 | 1471.2 | 126.0973
|  |  | 1692.4 | 1471.4 | 126.1932
|  |  | 1692.6 | 1471.6 | 126.1932
|  |  | 1692.8 | 1471.8 | 126.0013
|  |  | 1693 | 1472 | 126.1932
|  |  | 1693.2 | 1472.2 | 126.1932
|  |  | 1693.4 | 1472.4 | 126.2892
|  |  | 1693.6 | 1472.6 | 126.1932
|  |  | 1693.8 | 1472.8 | 126.1932
|  |  | 1694 | 1473 | 126.0973
|  |  | 1694.2 | 1473.2 | 126.1932
|  |  | 1694.4 | 1473.4 | 126.1932
|  |  | 1694.6 | 1473.6 | 126.1932
|  |  | 1694.8 | 1473.8 | 126.2892
|  |  | 1695 | 1474 | 126.2892
|  |  | 1695.2 | 1474.2 | 126.2892
|  |  | 1695.4 | 1474.4 | 126.1932
|  |  | 1695.6 | 1474.6 | 126.2892
|  |  | 1695.8 | 1474.8 | 126.2892
|  |  | 1696 | 1475 | 126.1932
|  |  | 1696.2 | 1475.2 | 126.2892
|  |  | 1696.4 | 1475.4 | 126.1932
|  |  | 1696.6 | 1475.6 | 126.1932
|  |  | 1696.8 | 1475.8 | 126.1932
|  |  | 1697 | 1476 | 126.1932
|  |  | 1697.2 | 1476.2 | 126.1932
|  |  | 1697.4 | 1476.4 | 126.1932
|  |  | 1697.6 | 1476.6 | 126.1932
|  |  | 1697.8 | 1476.8 | 126.2892
|  |  | 1698 | 1477 | 126.1932
|  |  | 1698.2 | 1477.2 | 126.2892
|  |  | 1698.4 | 1477.4 | 126.2892
|  |  | 1698.6 | 1477.6 | 126.2892
|  |  | 1698.8 | 1477.8 | 126.2892
|  |  | 1699 | 1478 | 126.2892
|  |  | 1699.2 | 1478.2 | 126.2892
|  |  | 1699.4 | 1478.4 | 126.3852
|  |  | 1699.6 | 1478.6 | 126.2892
|  |  | 1699.8 | 1478.8 | 126.1932
|  |  | 1700 | 1479 | 126.1932
|  |  | 1720 | 1499 | 126.2892
|  |  | 1740 | 1519 | 126.865
|  |  | 1760 | 1539 | 127.9206
|  |  | 1780 | 1559 | 127.7287
|  |  | 1800 | 1579 | 127.4408
|  |  | 1850 | 1629 | 127.7287
|  |  | 1900 | 1679 | 126.3852
|  |  | 1950 | 1729 | 127.2489
|  |  | 2000 | 1779 | 126.4811
|  |  | 2050 | 1829 | 126.1932
|  |  | 2100 | 1879 | 128.0166
|  |  | 2150 | 1929 | 128.1126
|  |  | 2200 | 1979 | 128.0166
|  |  | 2250 | 2029 | 125.9054
|  |  | 2300 | 2079 | 125.9054
|  |  | 2350 | 2129 | 126.961
|  |  | 2400 | 2179 | 125.8094
|  |  | 2450 | 2229 | 128.0166
|  |  | 2500 | 2279 | 125.9054
|  |  | 2550 | 2329 | 127.8247
|  |  | 2600 | 2379 | 126.1932
|  |  | 2650 | 2429 | 125.9054
|  |  | 2700 | 2479 | 126.865
|  |  | 2750 | 2529 | 126.2892
|  |  | 2800 | 2579 | 125.9054
|  |  | 2850 | 2629 | 125.9054
|  |  | 2900 | 2679 | 125.7134
|  |  | 2950 | 2729 | 127.1529
|  |  | 3000 | 2779 | 127.8247
|  |  | 3050 | 2829 | 127.9206
|  |  | 3100 | 2879 | 127.6327
|  |  | 3150 | 2929 | 127.8247
|  |  | 3200 | 2979 | 126.0973
|  |  | 3250 | 3029 | 125.6175
|  |  | 3300 | 3079 | 127.6327
|  |  | 3350 | 3129 | 127.4408
|  |  | 3400 | 3179 | 126.769
|  |  | 3450 | 3229 | 126.0013
|  |  | 3500 | 3279 | 126.6731
|  |  | 3550 | 3329 | 126.0013
|  |  | 3577 | 3356 | 125.8094