## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-3
Test Date: | 2006-10-27
Ignition Time Relative to Thermal Data: | 145 | s
Ignition Time Relative to Electrical Data: | 145 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
3/C cable temperatures and IRMS data
3/C Cable at Location G

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable thermal bundle configuration 3-1 |  |  |  | Location A | Location C - 6-cable thermal Bundle configuration 3-2 |  |  |  | Location C | Location E - single 3/C PVC/PVC |  |  | Location E | Location G - single 3/C PVC/PVC |  |  | Location G
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | TC-1 Cable | TC-2 Above Cable | TC-3 Below Cable | Tray Rung | TC-1 Cable | TC-2 Above Cable | TC-3 Below Cable | Tray Rung
0 | -145 | -5 | 0 | 0 | 13.6 | 13.4 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 6.8 | 253.8 | 21.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13.1 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
1 | -144 | -5.5 | 0 | 0 | 13.5 | 13.4 | 13.4 | 13.5 | 14.4 | 11 | 21.9 | 11.9 | 6.6 | 260.2 | 26.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
2 | -143 | -5.3 | 0 | 0 | 13.6 | 13.4 | 13.4 | 13.5 | 14.4 | 11 | 21.9 | 11.9 | 6.9 | 260.2 | 24.1 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13.1 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
3 | -142 | -4.7 | 0 | 0 | 13.5 | 13.4 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 6.8 | 266.3 | 22.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
4 | -141 | -4.5 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.6 | 14.4 | 10.9 | 21.9 | 11.9 | 6.7 | 254.8 | 24.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
5 | -140 | -4.4 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.6 | 14.4 | 10.9 | 21.9 | 11.9 | 9.9 | 252.7 | 22.5 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
6 | -139 | -5.2 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 10.9 | 249.5 | 22.4 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
7 | -138 | -5.8 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 10.1 | 246.1 | 22.9 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
8 | -137 | -5.3 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 8.8 | 241.2 | 24 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
9 | -136 | -4.5 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 6.2 | 240.2 | 21.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.2 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
10 | -135 | -5 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 4.6 | 244.3 | 21.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
11 | -134 | -5.8 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 3.8 | 246.1 | 20.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
12 | -133 | -4.7 | 0 | 0 | 13.4 | 13.6 | 13.4 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 4.4 | 245.1 | 17.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 12 | 13.1 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
13 | -132 | -6 | 0 | 0 | 13.4 | 13.6 | 13.3 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 3.9 | 264.1 | 16 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
14 | -131 | -6.3 | 0 | 0 | 13.4 | 13.6 | 13.3 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 5.8 | 260.2 | 14.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
15 | -130 | -6.8 | 0 | 0 | 13.4 | 13.6 | 13.3 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 9.7 | 250.8 | 14.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 12 | 13.1 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
16 | -129 | -6.7 | 0 | 0 | 13.5 | 13.6 | 13.3 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 9.3 | 254.9 | 15.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
17 | -128 | -5.4 | 0 | 0 | 13.5 | 13.6 | 13.4 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 11.3 | 257.2 | 15.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
18 | -127 | -3.1 | 0 | 0 | 13.4 | 13.6 | 13.4 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 12.4 | 262.4 | 17.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
19 | -126 | -2.3 | 0 | 0 | 13.4 | 13.6 | 13.4 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 10.7 | 253.7 | 18.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
20 | -125 | -2.2 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 9.1 | 230.4 | 21 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.2 | 15
21 | -124 | -3.7 | 0 | 0 | 13.5 | 13.6 | 13.5 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 5.6 | 242.6 | 22.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.2 | 15
22 | -123 | -5 | 0 | 0 | 13.5 | 13.6 | 13.5 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 5.1 | 237.3 | 17.3 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
23 | -122 | -6.1 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 3.9 | 245 | 16.7 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
24 | -121 | -6.6 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 3.7 | 246.3 | 16.8 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
25 | -120 | -6.8 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 10.9 | 21.9 | 11.9 | 5.1 | 263.4 | 18.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
26 | -119 | -6.4 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 4.5 | 264.2 | 19.8 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.1 | 15
27 | -118 | -6.3 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 5.9 | 260.6 | 18.5 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
28 | -117 | -6.7 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.8 | 6.1 | 264.7 | 17.4 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
29 | -116 | -6.8 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11.1 | 21.9 | 11.8 | 5.8 | 262.5 | 18 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
30 | -115 | -6.1 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 11.1 | 21.9 | 11.8 | 5.2 | 260.6 | 19.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
31 | -114 | -4.1 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.4 | 14.4 | 11.1 | 21.9 | 11.8 | 5.6 | 263.5 | 18.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
32 | -113 | -2.6 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 11.8 | 5 | 276.9 | 17 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
33 | -112 | -3.2 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 11.8 | 5.3 | 265.6 | 13.2 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
34 | -111 | -3.1 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 11.8 | 4.7 | 271.9 | 12.3 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
35 | -110 | -2.7 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 11.8 | 4.2 | 267.2 | 15.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.2 | 15
36 | -109 | -3.3 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 11.8 | 3.5 | 267.2 | 15.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
37 | -108 | -4.5 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 3.8 | 265.1 | 14 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
38 | -107 | -5.6 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 4.6 | 256.5 | 12.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
39 | -106 | -6.1 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 5.1 | 246.3 | 11.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
40 | -105 | -6.3 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 5.4 | 238.3 | 10.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
41 | -104 | -6.4 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 4.2 | 236.6 | 11.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
42 | -103 | -6.8 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 3.5 | 266 | 9.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.9 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
43 | -102 | -6.8 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 3.2 | 255.2 | 10.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
44 | -101 | -6.6 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 2.9 | 254.6 | 14.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
45 | -100 | -6.6 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 3.2 | 260.3 | 15.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
46 | -99 | -6.2 | 0 | 0 | 13.4 | 13.5 | 13.6 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 4.2 | 259.4 | 14.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
47 | -98 | -5.6 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 6.3 | 256.6 | 12.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
48 | -97 | -4.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 6.7 | 264.2 | 10.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
49 | -96 | -3.8 | 0 | 0 | 13.4 | 13.4 | 13.6 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 6.7 | 252 | 11.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
50 | -95 | -3.3 | 0 | 0 | 13.4 | 13.4 | 13.6 | 13.5 | 14.4 | 11 | 21.9 | 11.8 | 8.4 | 275.6 | 9.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
51 | -94 | -2.9 | 0 | 0 | 13.5 | 13.4 | 13.6 | 13.5 | 14.4 | 11 | 21.9 | 11.9 | 7.7 | 243.3 | 11.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
52 | -93 | -2.3 | 0 | 0 | 13.5 | 13.3 | 13.6 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 6.2 | 233.2 | 14.1 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
53 | -92 | -3.5 | 0 | 0 | 13.4 | 13.3 | 13.6 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 4.8 | 245.8 | 10.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.5 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
54 | -91 | -5 | 0 | 0 | 13.4 | 13.3 | 13.6 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 4.5 | 247.8 | 9.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
55 | -90 | -5.9 | 0 | 0 | 13.5 | 13.3 | 13.6 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 2.5 | 240.8 | 14.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
56 | -89 | -5.8 | 0 | 0 | 13.5 | 13.3 | 13.6 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 2.4 | 236.2 | 16 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.2 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
57 | -88 | -5.7 | 0 | 0 | 13.4 | 13.3 | 13.6 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 2.5 | 231.5 | 15.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
58 | -87 | -5.9 | 0 | 0 | 13.5 | 13.3 | 13.5 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 2.7 | 235.3 | 15.5 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
59 | -86 | -5.9 | 0 | 0 | 13.5 | 13.3 | 13.5 | 13.5 | 14.4 | 10.9 | 21.9 | 11.9 | 4.1 | 261.2 | 14.5 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
60 | -85 | -6 | 0 | 0 | 13.5 | 13.3 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.9 | 5.9 | 263.8 | 13.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.4 | 15
61 | -84 | -4.9 | 0 | 0 | 13.5 | 13.3 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 4.4 | 266.8 | 14.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.6 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
62 | -83 | -5.6 | 0 | 0 | 13.5 | 13.3 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 3.1 | 275.1 | 15.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
63 | -82 | -6.3 | 0 | 0 | 13.5 | 13.3 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 4.3 | 263.4 | 13.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
64 | -81 | -5.9 | 0 | 0 | 13.4 | 13.3 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 5.4 | 240.5 | 10.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
65 | -80 | -5.7 | 0 | 0 | 13.5 | 13.3 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 5.7 | 258.2 | 8.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
66 | -79 | -6 | 0 | 0 | 13.5 | 13.4 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 5.9 | 264.8 | 9.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
67 | -78 | -5.9 | 0 | 0 | 13.5 | 13.4 | 13.4 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 6 | 241 | 10.2 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
68 | -77 | -6 | 0 | 0 | 13.5 | 13.4 | 13.4 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 6 | 272.5 | 9.2 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
69 | -76 | -6 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 4.6 | 245.5 | 12.5 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
70 | -75 | -6.4 | 0 | 0 | 13.5 | 13.5 | 13.4 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 5.9 | 246.6 | 16.8 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
71 | -74 | -6.5 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 5.6 | 250.2 | 16.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
72 | -73 | -6.2 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.3 | 14.3 | 10.9 | 21.9 | 11.9 | 5.8 | 240.9 | 16.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
73 | -72 | -6.7 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.2 | 14.3 | 10.9 | 21.9 | 11.9 | 5.3 | 228.2 | 16.2 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
74 | -71 | -6.5 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.2 | 14.3 | 10.9 | 21.9 | 11.9 | 3.9 | 244.2 | 14.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
75 | -70 | -5.9 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.2 | 14.3 | 11 | 21.9 | 11.9 | 6.1 | 240.2 | 15.3 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
76 | -69 | -6.4 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.2 | 14.3 | 11 | 21.9 | 11.9 | 6.3 | 241.5 | 14.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
77 | -68 | -3.4 | 0 | 0 | 13.5 | 13.5 | 13.6 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 7.7 | 243.9 | 15.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
78 | -67 | -6.9 | 0 | 0 | 13.5 | 13.5 | 13.6 | 13.3 | 14.4 | 11 | 21.9 | 11.9 | 8.8 | 257.2 | 14.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 12 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
79 | -66 | -6.9 | 0 | 0 | 13.5 | 13.5 | 13.5 | 13.3 | 14.4 | 10.9 | 21.9 | 11.9 | 5.9 | 266.6 | 12 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
80 | -65 | -4 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.3 | 14.4 | 11 | 21.9 | 11.9 | 6.6 | 226 | 16.8 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
81 | -64 | 2.3 | 0.92 | 1.0754 | 13.4 | 13.5 | 13.6 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 6.3 | 249.3 | 16 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
82 | -63 | 3.1 | 1.24 | 1.4495 | 13.4 | 13.5 | 13.6 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 5.9 | 265.1 | 14.1 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
83 | -62 | 2.2 | 0.88 | 1.0287 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 6 | 263.5 | 12.5 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
84 | -61 | -0.1 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 6 | 233.5 | 13.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
85 | -60 | -0.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 6.1 | 256.2 | 14.3 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
86 | -59 | -2.4 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 6.6 | 258.9 | 14.6 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
87 | -58 | -2 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 4.8 | 247.9 | 13 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
88 | -57 | -1 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.9 | 5.7 | 249.4 | 13.9 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
89 | -56 | -1.6 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 7.5 | 245.5 | 18.3 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
90 | -55 | -1.8 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 10.2 | 245.6 | 20 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
91 | -54 | -1.2 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 7.3 | 253.8 | 17.2 | 12.6 | 11.4 | 11.7 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.8 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
92 | -53 | -2.2 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 4.7 | 238.3 | 16.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
93 | -52 | -4.8 | 0 | 0 | 13.3 | 13.4 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 5.9 | 243.3 | 14.4 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
94 | -51 | -6.2 | 0 | 0 | 13.3 | 13.4 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 6.5 | 242.6 | 17.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
95 | -50 | -6.8 | 0 | 0 | 13.3 | 13.4 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 7 | 242.7 | 20.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
96 | -49 | -6.9 | 0 | 0 | 13.3 | 13.4 | 13.5 | 13.4 | 14.4 | 11 | 21.9 | 12 | 6.7 | 246.3 | 18.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
97 | -48 | -6.9 | 0 | 0 | 13.3 | 13.4 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 12 | 6.3 | 247.4 | 20.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
98 | -47 | -6.9 | 0 | 0 | 13.3 | 13.4 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 5.6 | 243 | 22.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
99 | -46 | -6.9 | 0 | 0 | 13.3 | 13.4 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 6.1 | 249.6 | 21.4 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
100 | -45 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 6.7 | 252.5 | 17.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
101 | -44 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.3 | 14.3 | 11 | 21.9 | 11.9 | 5.8 | 254.2 | 18.7 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
102 | -43 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 6.5 | 247.4 | 20.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.7 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
103 | -42 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 6.4 | 248.8 | 19 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
104 | -41 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 6.5 | 253.6 | 18 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.7 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
105 | -40 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 6.2 | 261.1 | 16 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
106 | -39 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 8.2 | 253.3 | 15.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
107 | -38 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 6.8 | 252.9 | 14.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
108 | -37 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 5.8 | 253.2 | 15.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
109 | -36 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 10.2 | 250.6 | 17.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 12.9 | 14.8 | 13.6 | 13.3 | 12.3 | 15
110 | -35 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 6.5 | 259.4 | 17.1 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
111 | -34 | -6.9 | 0 | 0 | 13.4 | 13.4 | 13.5 | 13.3 | 14.3 | 11.1 | 21.9 | 11.9 | 4.5 | 245.3 | 16.1 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
112 | -33 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.3 | 14.3 | 11.2 | 21.9 | 11.9 | 6.6 | 245.8 | 19.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
113 | -32 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 8.4 | 264.7 | 20.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
114 | -31 | -6.9 | 0 | 0 | 13.3 | 13.5 | 13.6 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 7.1 | 257 | 22.1 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
115 | -30 | -6.9 | 0 | 0 | 13.3 | 13.5 | 13.6 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 6.7 | 252.2 | 18.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
116 | -29 | -6.9 | 0 | 0 | 13.2 | 13.5 | 13.6 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 6.9 | 262.1 | 17 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
117 | -28 | -6.9 | 0 | 0 | 13.2 | 13.5 | 13.6 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 6.8 | 260.9 | 18.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
118 | -27 | -6.9 | 0 | 0 | 13.3 | 13.5 | 13.6 | 13.3 | 14.3 | 11.1 | 21.9 | 11.9 | 6.3 | 259.6 | 19.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
119 | -26 | -6.9 | 0 | 0 | 13.3 | 13.5 | 13.6 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 7.6 | 250.8 | 17 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
120 | -25 | -6.9 | 0 | 0 | 13.2 | 13.5 | 13.6 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 8.7 | 253.5 | 18.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
121 | -24 | -5.8 | 0 | 0 | 13.3 | 13.5 | 13.6 | 13.3 | 14.3 | 11.1 | 21.9 | 11.9 | 6.7 | 254.4 | 20.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
122 | -23 | -6.3 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.3 | 14.3 | 11.1 | 21.9 | 11.9 | 10.4 | 247.9 | 22.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
123 | -22 | -6.9 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 11.4 | 255.1 | 22.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
124 | -21 | -6.9 | 0 | 0 | 13.3 | 13.5 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 11.3 | 256.1 | 23.4 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
125 | -20 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 11.9 | 251.7 | 26.6 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
126 | -19 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.4 | 14.3 | 11.1 | 21.9 | 11.9 | 11.4 | 260.2 | 27.8 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
127 | -18 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 12.7 | 257.9 | 29.4 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
128 | -17 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.4 | 14.3 | 11 | 21.9 | 11.9 | 15.1 | 255.5 | 30.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
129 | -16 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.4 | 14.4 | 11 | 21.9 | 11.9 | 9.6 | 260 | 28.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
130 | -15 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.5 | 14.3 | 11 | 21.9 | 11.9 | 10.8 | 258.1 | 27.3 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
131 | -14 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.3 | 11 | 21.9 | 11.9 | 12.7 | 263.3 | 25.2 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
132 | -13 | -6.8 | 0 | 0 | 13.4 | 13.5 | 13.4 | 13.5 | 14.3 | 11 | 21.9 | 11.9 | 10.7 | 255.8 | 24.5 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
133 | -12 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.3 | 11 | 21.9 | 11.9 | 8.8 | 262.8 | 22.9 | 12.6 | 11.4 | 11.8 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
134 | -11 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 10 | 263 | 24.7 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
135 | -10 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 11.9 | 12.7 | 271.6 | 23 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.7 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
136 | -9 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 11.2 | 271.8 | 27.9 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
137 | -8 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 9.7 | 266.3 | 31.2 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
138 | -7 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 11.7 | 258.3 | 30.3 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
139 | -6 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 11.1 | 254.8 | 28.2 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.8 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
140 | -5 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 8.3 | 261.3 | 27.7 | 12.6 | 11.4 | 11.9 | 12.9 | 13.6 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
141 | -4 | -6.6 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11 | 21.9 | 12 | 7.6 | 265.5 | 29.3 | 12.6 | 11.4 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
142 | -3 | -6.5 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 12 | 8.8 | 259.8 | 25.3 | 12.6 | 11.4 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
143 | -2 | -6.8 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11.1 | 21.9 | 12 | 10.7 | 262.6 | 26 | 12.6 | 11.4 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
144 | -1 | -6.9 | 0 | 0 | 13.4 | 13.5 | 13.5 | 13.4 | 14.4 | 11.1 | 21.9 | 12 | 11.3 | 268.9 | 28.9 | 12.6 | 11.4 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 11.9 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
145 | 0 | 11.8 | 4.72 | 5.5174 | 13.4 | 13.5 | 13.5 | 13.4 | 14.3 | 11.1 | 21.9 | 12 | 12.8 | 263.6 | 26.9 | 12.6 | 11.4 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.3 | 15
146 | 1 | 276.7 | 110.68 | 129.3785 | 13.4 | 13.5 | 13.4 | 13.4 | 14.4 | 11.1 | 21.9 | 12 | 10.9 | 261.2 | 24.3 | 12.6 | 11.4 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
147 | 2 | 495.4 | 198.16 | 231.6376 | 13.4 | 13.5 | 13.4 | 13.4 | 14.4 | 11.1 | 21.9 | 12 | 10.6 | 264.4 | 26.1 | 12.6 | 11.5 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
148 | 3 | 539.6 | 215.84 | 252.3045 | 13.3 | 13.5 | 13.4 | 13.4 | 14.3 | 11.1 | 21.9 | 12 | 8.7 | 270.3 | 25.4 | 12.6 | 11.5 | 12 | 12.9 | 13.7 | 13.1 | 11.9 | 12 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.8 | 13.6 | 13.3 | 12.4 | 15
149 | 4 | 525 | 210 | 245.4779 | 13.4 | 13.5 | 13.5 | 13.5 | 14.4 | 11.1 | 21.9 | 11.9 | 7.6 | 264 | 24.6 | 12.6 | 12.6 | 17.9 | 12.9 | 14.2 | 13.1 | 11.9 | 12.2 | 13 | 13.8 | 13.4 | 12.8 | 13 | 14.9 | 13.6 | 13.4 | 12.4 | 15
150 | 5 | 500.6 | 200.24 | 234.069 | 13.4 | 13.6 | 13.6 | 13.6 | 14.4 | 11.1 | 21.9 | 11.9 | 8.3 | 259.9 | 25.5 | 12.6 | 25.3 | 51.6 | 12.9 | 17.7 | 13.1 | 14.4 | 23.1 | 13.1 | 14.6 | 13.4 | 12.9 | 13 | 15 | 13.6 | 13.4 | 12.4 | 15.1
151 | 6 | 479.1 | 191.64 | 224.0161 | 13.5 | 13.7 | 13.8 | 13.8 | 16.3 | 11.1 | 21.9 | 11.9 | 7.9 | 259.6 | 26.8 | 12.6 | 50.9 | 119.3 | 12.9 | 23 | 13.1 | 25.3 | 51.6 | 13.3 | 17.9 | 13.4 | 13 | 13.1 | 15.2 | 13.6 | 13.4 | 12.5 | 15.2
152 | 7 | 469.1 | 187.64 | 219.3403 | 13.6 | 13.8 | 14.1 | 14.1 | 25.9 | 11.1 | 21.9 | 11.9 | 8.1 | 261.5 | 27 | 12.7 | 85.2 | 192.6 | 13 | 31.6 | 13.1 | 41.2 | 89.4 | 13.7 | 22.2 | 13.4 | 13.2 | 13.2 | 15.6 | 13.6 | 13.4 | 12.6 | 15.3
153 | 8 | 464.5 | 185.8 | 217.1895 | 13.7 | 14.1 | 14.4 | 14.4 | 36.1 | 11.1 | 21.9 | 11.9 | 8.9 | 269.5 | 26.2 | 12.7 | 120.3 | 253.5 | 13.1 | 43 | 13.1 | 56 | 113.2 | 14 | 27.3 | 13.4 | 13.3 | 13.3 | 15.9 | 13.6 | 13.5 | 12.8 | 15.4
154 | 9 | 450.8 | 180.32 | 210.7837 | 14.2 | 14.6 | 14.9 | 15.2 | 47.1 | 11.1 | 21.9 | 11.9 | 6 | 273.3 | 23.6 | 12.7 | 175.5 | 320.1 | 13.4 | 54.4 | 13.1 | 82.4 | 164 | 14.6 | 35.3 | 13.4 | 13.6 | 13.9 | 16.3 | 13.6 | 13.6 | 13 | 15.6
155 | 10 | 442.4 | 176.96 | 206.856 | 14.9 | 15.1 | 16.3 | 16.9 | 68.8 | 11.2 | 21.9 | 11.9 | 7.5 | 274.4 | 21.4 | 12.7 | 223.2 | 375 | 13.6 | 61 | 13.1 | 108.3 | 210.2 | 15.4 | 44.5 | 13.4 | 14 | 14.4 | 16.8 | 13.6 | 13.9 | 13.3 | 15.8
156 | 11 | 437.2 | 174.88 | 204.4246 | 15.7 | 15.8 | 18.6 | 19.6 | 83.8 | 11.2 | 21.9 | 11.9 | 7.7 | 268.6 | 21 | 12.7 | 256.9 | 426.4 | 13.9 | 70 | 13.2 | 123 | 236.4 | 15.9 | 48.6 | 13.4 | 14.5 | 15.1 | 17.3 | 13.7 | 15.2 | 13.8 | 16
157 | 12 | 436 | 174.4 | 203.8636 | 16.5 | 16.7 | 20.8 | 22 | 93.9 | 11.2 | 21.9 | 11.9 | 7.5 | 264 | 21.3 | 12.8 | 294.3 | 473.1 | 14.2 | 84.2 | 13.2 | 143.2 | 268.8 | 16.3 | 55.1 | 13.4 | 15.5 | 16.5 | 17.9 | 13.7 | 18.6 | 14.8 | 16.3
158 | 13 | 436.3 | 174.52 | 204.0038 | 18.5 | 18.4 | 22.9 | 24.8 | 106 | 11.3 | 21.9 | 11.9 | 7.2 | 258.3 | 20.7 | 12.8 | 333.5 | 507 | 14.5 | 97.4 | 13.2 | 161 | 294.5 | 16.8 | 62.6 | 13.5 | 17.5 | 19.1 | 18.5 | 13.8 | 24.2 | 17.2 | 16.7
159 | 14 | 437.2 | 174.88 | 204.4246 | 20.6 | 20.8 | 25.3 | 28 | 122.8 | 11.3 | 21.9 | 11.9 | 6.9 | 254.2 | 21.5 | 12.8 | 383.3 | 537 | 15.1 | 110.4 | 13.3 | 188.7 | 330.3 | 17.2 | 74.2 | 13.5 | 19.5 | 20.7 | 19.1 | 13.9 | 27.2 | 19.6 | 17.1
160 | 15 | 439.1 | 175.64 | 205.313 | 22.4 | 23 | 28.5 | 31.7 | 140.2 | 11.3 | 21.9 | 11.9 | 7.3 | 260.9 | 22.1 | 12.8 | 440.1 | 557.5 | 16.4 | 121.6 | 13.3 | 218 | 379.5 | 17.8 | 85.4 | 13.6 | 21.2 | 22.8 | 19.5 | 14 | 30.8 | 21.3 | 17.5
161 | 16 | 438.7 | 175.48 | 205.126 | 24.3 | 25.5 | 32.3 | 35.6 | 159.6 | 11.3 | 21.9 | 12 | 6.5 | 264.8 | 20.7 | 12.8 | 500.4 | 573.2 | 18.3 | 130 | 13.4 | 259.4 | 431.9 | 18.7 | 99.5 | 13.6 | 22.9 | 25.3 | 20 | 14.1 | 35.5 | 23.7 | 18
162 | 17 | 438.1 | 175.24 | 204.8455 | 27.8 | 28.5 | 36.5 | 39.5 | 182.7 | 11.3 | 21.9 | 12.1 | 7.6 | 258.2 | 20.4 | 12.9 | 535.2 | 587.6 | 20.2 | 134.3 | 13.5 | 291.3 | 456.8 | 19.6 | 109.9 | 13.7 | 24.4 | 27.8 | 20.4 | 14.3 | 37.7 | 27.5 | 18.6
163 | 18 | 437.6 | 175.04 | 204.6117 | 31.9 | 31.8 | 40.5 | 43.2 | 193.8 | 11.4 | 21.9 | 12.2 | 7.5 | 262.3 | 20.7 | 12.9 | 561.1 | 608.6 | 22.4 | 144 | 13.6 | 304.3 | 467.2 | 20.1 | 114.3 | 13.8 | 26.7 | 30.6 | 20.7 | 14.4 | 39.9 | 30.8 | 19.1
164 | 19 | 438.6 | 175.44 | 205.0793 | 35.5 | 35 | 44.4 | 47 | 204.4 | 11.4 | 21.9 | 12.3 | 7.4 | 268.8 | 20.5 | 13.1 | 602.1 | 646.1 | 26 | 162.7 | 13.7 | 326.8 | 510.2 | 20.8 | 127.6 | 13.9 | 29.2 | 35 | 21.4 | 14.6 | 42.3 | 32.9 | 19.6
165 | 20 | 438.7 | 175.48 | 205.126 | 39.6 | 38.6 | 48.5 | 51.5 | 216.5 | 11.4 | 21.9 | 12.4 | 5.5 | 275.5 | 22.1 | 13.2 | 639.1 | 669.4 | 30.1 | 175.3 | 13.9 | 350.4 | 546.7 | 21.6 | 143.8 | 14 | 33 | 39.4 | 22.4 | 14.8 | 45.1 | 35 | 19.9
166 | 21 | 439.6 | 175.84 | 205.5468 | 43.5 | 43.2 | 52.7 | 56 | 229.7 | 11.4 | 21.9 | 12.5 | 4.3 | 276 | 22 | 13.4 | 672.8 | 679.6 | 33.9 | 182.9 | 14 | 374 | 564.8 | 22.4 | 155.6 | 14.2 | 35.8 | 42.8 | 23.2 | 15.1 | 48.1 | 37 | 20.2
167 | 22 | 439 | 175.6 | 205.2663 | 46.4 | 47.1 | 57.2 | 60.8 | 242.1 | 11.5 | 21.9 | 12.6 | 4 | 269.5 | 21.7 | 13.6 | 693 | 687.4 | 37.5 | 188.4 | 14.2 | 391.3 | 576.6 | 23.3 | 162.4 | 14.3 | 38.2 | 47.4 | 23.9 | 15.3 | 50.9 | 40.1 | 20.9
168 | 23 | 441.4 | 176.56 | 206.3885 | 51.6 | 51 | 61.9 | 66 | 246.7 | 11.5 | 21.9 | 12.7 | 3.9 | 274.9 | 21.1 | 13.9 | 718.8 | 688.5 | 41.8 | 197.5 | 14.5 | 400.6 | 585.1 | 24.2 | 167.1 | 14.4 | 41.8 | 52.1 | 24.6 | 15.5 | 54.2 | 43.9 | 21.4
169 | 24 | 441.1 | 176.44 | 206.2482 | 56.1 | 54.9 | 67.1 | 71.4 | 253 | 11.5 | 21.9 | 13 | 5.2 | 280.8 | 20.8 | 14.3 | 735.1 | 697.3 | 47.3 | 206.9 | 14.8 | 409.2 | 604.3 | 25.1 | 173 | 14.6 | 45.3 | 56.8 | 25.4 | 15.8 | 57.6 | 47.9 | 22
170 | 25 | 442.2 | 176.88 | 206.7625 | 60.3 | 58 | 71.5 | 76 | 259.2 | 11.6 | 21.9 | 13.4 | 5.8 | 284.1 | 21.9 | 14.7 | 739.7 | 709.9 | 51 | 212.6 | 15.1 | 413.5 | 607.2 | 27.3 | 177.4 | 14.8 | 48.2 | 61.2 | 27.1 | 16 | 61.9 | 50.9 | 22.5
171 | 26 | 443.9 | 177.56 | 207.5574 | 66 | 61.2 | 75.7 | 80.5 | 263.1 | 11.6 | 21.9 | 13.9 | 5.3 | 274.9 | 23.2 | 15.2 | 742.4 | 725.9 | 53.4 | 219.7 | 15.5 | 419 | 613.5 | 30.1 | 183.1 | 15 | 51.1 | 65 | 27.9 | 16.3 | 66.6 | 54.3 | 23
172 | 27 | 444.5 | 177.8 | 207.838 | 70.4 | 65.1 | 80.4 | 85.1 | 274.3 | 11.6 | 21.9 | 14.6 | 5.4 | 279.8 | 22.5 | 15.7 | 745.8 | 741.1 | 56.5 | 232.1 | 15.9 | 435.5 | 630.6 | 34 | 192.9 | 15.2 | 54.4 | 68.4 | 28.3 | 16.5 | 69.9 | 58.8 | 23.6
173 | 28 | 444.8 | 177.92 | 207.9782 | 73.7 | 69.3 | 85 | 90 | 281.2 | 11.6 | 21.9 | 15.2 | 4.7 | 283.9 | 21.9 | 16.3 | 746.4 | 750.3 | 57.6 | 239.8 | 16.4 | 443.6 | 643.2 | 36.8 | 199.9 | 15.4 | 58.6 | 72.3 | 29 | 16.8 | 73.5 | 62.7 | 24.4
174 | 29 | 447.1 | 178.84 | 209.0537 | 78.1 | 74.1 | 89 | 94.5 | 290.9 | 11.6 | 21.9 | 15.8 | 4.2 | 282.4 | 21.6 | 17 | 749.3 | 763.8 | 59.6 | 250.8 | 16.9 | 458.8 | 667.1 | 39.8 | 209.2 | 15.6 | 61.4 | 75.5 | 29.6 | 17.1 | 76.7 | 66.1 | 24.9
175 | 30 | 450 | 180 | 210.4096 | 83.6 | 78.4 | 92.4 | 98.5 | 304.5 | 11.6 | 21.9 | 16.4 | 4.7 | 282.5 | 21.9 | 17.7 | 753.9 | 767.8 | 63.3 | 259 | 17.5 | 461.8 | 672.9 | 41.6 | 217.9 | 15.8 | 64.7 | 78.6 | 30.2 | 17.3 | 80.3 | 69.5 | 25.6
176 | 31 | 452.2 | 180.88 | 211.4383 | 87.5 | 82.1 | 97 | 102.8 | 303.1 | 11.6 | 21.9 | 17 | 5.7 | 283.5 | 20.8 | 18.4 | 740.8 | 758.8 | 65.1 | 266.2 | 18.1 | 458.8 | 657.6 | 42.3 | 221.1 | 16.1 | 67.7 | 82.2 | 31.4 | 17.6 | 83.3 | 71.8 | 26.3
177 | 32 | 451.7 | 180.68 | 211.2045 | 90.1 | 85.8 | 101.5 | 107.2 | 303.7 | 11.6 | 21.9 | 17.7 | 6.5 | 281 | 19.5 | 19.1 | 727.1 | 747.1 | 67.1 | 271 | 18.8 | 452.1 | 645.3 | 42.9 | 224.6 | 16.3 | 70.5 | 86 | 31.7 | 17.9 | 87.7 | 74.3 | 26.8
178 | 33 | 451.8 | 180.72 | 211.2513 | 93.7 | 88.7 | 104.9 | 111.3 | 304.7 | 11.6 | 21.9 | 18.4 | 7.9 | 281.9 | 17.8 | 19.9 | 727.9 | 753.1 | 70.8 | 277.7 | 19.5 | 447.7 | 640 | 43.6 | 227.4 | 16.6 | 73.3 | 90.2 | 32.3 | 18.2 | 92.4 | 77.7 | 27.5
179 | 34 | 451.2 | 180.48 | 210.9707 | 98.3 | 91 | 108.2 | 115.2 | 306.2 | 11.7 | 21.9 | 19 | 6.4 | 282.4 | 16.7 | 20.7 | 733.6 | 760.2 | 74.4 | 284.4 | 20.2 | 449.9 | 659.2 | 45.7 | 233.2 | 16.9 | 76.5 | 93.7 | 32.6 | 18.5 | 96.6 | 81.2 | 28.2
180 | 35 | 452 | 180.8 | 211.3448 | 102.7 | 94.3 | 111.7 | 118.8 | 311.7 | 11.7 | 21.9 | 19.6 | 4.6 | 284.6 | 17 | 21.5 | 721.2 | 752.7 | 78.6 | 289.2 | 21 | 452.2 | 657.2 | 47.8 | 239.5 | 17.2 | 80.3 | 97.6 | 33.2 | 18.7 | 100.9 | 84.2 | 28.9
181 | 36 | 452.4 | 180.96 | 211.5318 | 106.2 | 98.6 | 115.6 | 122.1 | 311.9 | 11.7 | 21.9 | 20 | 3.6 | 280.8 | 16.8 | 22.3 | 719.9 | 748.5 | 82.8 | 294 | 21.7 | 450.1 | 644.8 | 48.3 | 241.6 | 17.5 | 83.7 | 100.9 | 33.9 | 19 | 104.3 | 87.3 | 29.6
182 | 37 | 452.6 | 181.04 | 211.6253 | 109.3 | 102.3 | 119.6 | 124.9 | 310 | 11.7 | 21.9 | 20.4 | 3.9 | 285.5 | 17.2 | 23.1 | 716.8 | 746.6 | 88.4 | 300.1 | 22.5 | 448.2 | 631.1 | 49.2 | 244 | 17.8 | 86.8 | 104.3 | 34.5 | 19.3 | 107.6 | 89.6 | 30
183 | 38 | 453.1 | 181.24 | 211.8591 | 112.1 | 105.9 | 123.4 | 127.8 | 307.8 | 11.7 | 21.9 | 20.8 | 4.6 | 286.8 | 18.4 | 24 | 726.2 | 747.5 | 95.6 | 305.2 | 23.2 | 444.4 | 627.3 | 50.4 | 247.6 | 18.1 | 89.5 | 107.2 | 35.5 | 19.6 | 110.6 | 92.3 | 30.5
184 | 39 | 452.1 | 180.84 | 211.3915 | 115.1 | 109.1 | 126.8 | 130.4 | 305.4 | 11.8 | 21.9 | 21.3 | 4.7 | 281.9 | 18.6 | 24.9 | 736.4 | 755.8 | 102.9 | 310.6 | 24 | 444.2 | 630.6 | 51.9 | 252.7 | 18.5 | 92.5 | 110.3 | 36.1 | 19.9 | 114.2 | 95 | 31.2
185 | 40 | 452.2 | 180.88 | 211.4383 | 118.5 | 111.3 | 130 | 133.4 | 305.9 | 11.8 | 21.9 | 21.7 | 3.9 | 275.5 | 18.8 | 25.8 | 740.4 | 771.2 | 110.1 | 315.4 | 24.8 | 443.7 | 634.8 | 53.1 | 256.6 | 18.8 | 95.9 | 114.6 | 37 | 20.2 | 117.4 | 98.6 | 31.8
186 | 41 | 452.2 | 180.88 | 211.4383 | 120.9 | 113.6 | 133 | 136.5 | 307.6 | 11.8 | 21.9 | 22.1 | 3.6 | 287 | 17.3 | 26.7 | 745.1 | 777.3 | 116.8 | 323.6 | 25.6 | 447.5 | 650.2 | 55.2 | 261.8 | 19.2 | 99.4 | 116.6 | 38.4 | 20.5 | 119.8 | 102.2 | 32.8
187 | 42 | 452.2 | 180.88 | 211.4383 | 122.3 | 117.2 | 135.6 | 139.6 | 317.8 | 11.9 | 21.9 | 22.6 | 4.7 | 280.9 | 17.1 | 27.7 | 761.3 | 782.6 | 125.7 | 325.3 | 26.4 | 454.7 | 670.5 | 57.2 | 266.6 | 19.6 | 101.8 | 118.6 | 39.1 | 20.8 | 121.8 | 104.2 | 33.5
188 | 43 | 454.1 | 181.64 | 212.3267 | 124.6 | 119.9 | 137.8 | 142.9 | 327.1 | 12 | 21.9 | 23.2 | 6.1 | 281.3 | 15.5 | 28.6 | 775.6 | 790.8 | 135.1 | 328.9 | 27.3 | 464.2 | 696.4 | 60 | 272.3 | 20 | 104.1 | 121.3 | 39.3 | 21.1 | 124.1 | 106.3 | 34.2
189 | 44 | 454.8 | 181.92 | 212.654 | 126.1 | 122.6 | 140.4 | 145.8 | 329.7 | 12.2 | 21.9 | 23.7 | 4.6 | 284 | 14 | 29.5 | 793.4 | 791.6 | 148.4 | 333.9 | 28.2 | 478.7 | 719.4 | 64.5 | 281.8 | 20.4 | 106.4 | 124.1 | 39.8 | 21.4 | 126.4 | 108.8 | 35.1
190 | 45 | 454.1 | 181.64 | 212.3267 | 128.3 | 125.8 | 142.8 | 147.9 | 334.8 | 12.4 | 21.9 | 24 | 3.9 | 285 | 14.1 | 30.4 | 808.9 | 806.7 | 162.6 | 340.9 | 29.1 | 492 | 736.4 | 69.5 | 292 | 20.8 | 109 | 126.6 | 40.6 | 21.7 | 128.9 | 110.6 | 36
191 | 46 | 453.7 | 181.48 | 212.1397 | 130.3 | 129 | 145 | 149.7 | 337.5 | 12.5 | 21.9 | 24.4 | 5 | 278.7 | 14.2 | 31.4 | 817.9 | 818.1 | 177.6 | 349.3 | 30.1 | 501.7 | 748.8 | 74.2 | 299 | 21.2 | 111.2 | 128.9 | 41.1 | 21.9 | 131.5 | 112.6 | 36.8
192 | 47 | 452.6 | 181.04 | 211.6253 | 131.6 | 131.4 | 147.1 | 151.5 | 338.2 | 12.4 | 21.9 | 24.6 | 5.1 | 292.1 | 14.1 | 32.4 | 817.7 | 820.8 | 187.3 | 356.5 | 31.1 | 509.1 | 754.1 | 79 | 307.8 | 21.6 | 113.8 | 131.4 | 41.8 | 22.2 | 134.2 | 114.8 | 37.5
193 | 48 | 453.8 | 181.52 | 212.1864 | 131.7 | 133.5 | 148.7 | 154 | 340.9 | 12.4 | 21.9 | 24.8 | 5.2 | 279.4 | 15 | 33.4 | 821.9 | 819.8 | 195.7 | 363.7 | 32.3 | 510.9 | 757.2 | 83.2 | 313.4 | 22 | 116.1 | 134.1 | 43 | 22.6 | 136.9 | 116.8 | 38.2
194 | 49 | 456 | 182.4 | 213.2151 | 131.8 | 135.2 | 150.6 | 156.2 | 346.5 | 12.3 | 21.9 | 25 | 6 | 270.1 | 14.2 | 34.5 | 822.7 | 821.7 | 204.5 | 371.7 | 33.5 | 513.9 | 758.5 | 87.1 | 321.1 | 22.5 | 118.3 | 136.4 | 43.7 | 22.9 | 139.5 | 118.8 | 38.9
195 | 50 | 455 | 182 | 212.7475 | 130.8 | 136.4 | 152.9 | 158.3 | 351.5 | 12.4 | 21.9 | 25.3 | 5.5 | 270.8 | 15.5 | 35.5 | 820.9 | 818.5 | 211.6 | 376.2 | 34.7 | 516.6 | 764.2 | 90.3 | 328 | 22.9 | 120.8 | 138.1 | 44.4 | 23.2 | 142.1 | 120.7 | 39.5
196 | 51 | 455.9 | 182.36 | 213.1683 | 131 | 138.4 | 155.1 | 160.1 | 354 | 12.5 | 21.9 | 25.5 | 5.1 | 267.3 | 16.1 | 36.5 | 823.6 | 820 | 221.2 | 381.7 | 35.9 | 517.2 | 767.9 | 92.9 | 335 | 23.3 | 123.2 | 140 | 45.4 | 23.5 | 144.6 | 123 | 40.2
197 | 52 | 455.7 | 182.28 | 213.0748 | 132.8 | 140.9 | 156.8 | 161.4 | 353.3 | 12.5 | 21.9 | 25.6 | 4.7 | 270.9 | 14.2 | 37.6 | 825.3 | 815.6 | 232.5 | 389.1 | 37.2 | 521.1 | 776.4 | 95.4 | 342.8 | 23.7 | 125 | 142.4 | 45.5 | 23.8 | 147.1 | 124.5 | 40.9
198 | 53 | 456 | 182.4 | 213.2151 | 134.4 | 143.4 | 158.4 | 162.7 | 354 | 12.5 | 21.9 | 25.8 | 4.5 | 267.9 | 16.6 | 38.7 | 836.7 | 819.5 | 246.9 | 394.4 | 38.5 | 526 | 778.2 | 98 | 350.9 | 24.2 | 127.1 | 144 | 46 | 24.1 | 149.4 | 126.1 | 41.6
199 | 54 | 456.8 | 182.72 | 213.5892 | 135.7 | 145.5 | 159.5 | 164.2 | 353.5 | 12.4 | 21.9 | 25.9 | 4.6 | 281 | 17.6 | 39.9 | 843.2 | 819.7 | 261.7 | 398.7 | 39.9 | 530.5 | 781 | 100.7 | 359.1 | 24.6 | 128.8 | 145.9 | 47 | 24.4 | 151.8 | 127.8 | 42.3
200 | 55 | 458.7 | 183.48 | 214.4775 | 137.3 | 147.2 | 161.2 | 165.9 | 350.6 | 12.4 | 21.9 | 26.1 | 5.2 | 288.3 | 16.5 | 41 | 845.1 | 810.7 | 269.6 | 402.9 | 41.2 | 531.1 | 777.7 | 102.3 | 366 | 25 | 131.2 | 148.3 | 47.5 | 24.8 | 154 | 129.5 | 42.9
201 | 56 | 458.5 | 183.4 | 214.384 | 138 | 149.1 | 162.8 | 166.8 | 353.3 | 12.4 | 21.9 | 26.3 | 5.1 | 289.4 | 16.5 | 42.2 | 843.6 | 813.3 | 275.5 | 408.9 | 42.7 | 531.1 | 778.5 | 103.7 | 372 | 25.5 | 133.2 | 149.5 | 48.6 | 25.1 | 155.8 | 131.1 | 43.7
202 | 57 | 456.7 | 182.68 | 213.5424 | 140.4 | 149.9 | 164.2 | 167.9 | 359 | 12.5 | 21.9 | 26.6 | 4.9 | 286.9 | 15.9 | 43.5 | 846.5 | 823 | 284 | 415.9 | 44.1 | 535.8 | 788.9 | 105 | 380.1 | 25.9 | 134.6 | 151.1 | 49 | 25.4 | 157.6 | 133 | 44.4
203 | 58 | 457.1 | 182.84 | 213.7294 | 141.8 | 152.5 | 165.6 | 169.2 | 361.6 | 12.5 | 21.9 | 26.8 | 3.9 | 303.1 | 14.3 | 44.7 | 852.9 | 832.5 | 294.4 | 424.7 | 45.5 | 542.8 | 796.2 | 105.7 | 390.3 | 26.4 | 136.2 | 153.4 | 49.8 | 25.7 | 159.2 | 134.2 | 45.1
204 | 59 | 459.4 | 183.76 | 214.8049 | 143.3 | 155.2 | 167.9 | 170.4 | 370 | 12.5 | 21.9 | 27.1 | 3.7 | 291.7 | 13.4 | 46.1 | 859.4 | 829 | 303.2 | 430.9 | 47 | 547.5 | 792.7 | 105.9 | 397.2 | 26.8 | 138 | 155.4 | 50.2 | 26 | 161 | 136.5 | 45.9
205 | 60 | 460.1 | 184.04 | 215.1322 | 144.4 | 156.5 | 170.1 | 171.7 | 374.2 | 12.5 | 21.8 | 27.3 | 3.4 | 284.6 | 14.1 | 47.6 | 866.3 | 834.1 | 314.9 | 438 | 48.4 | 547.9 | 792.6 | 105.9 | 402.7 | 27.3 | 139.7 | 157.2 | 50.7 | 26.3 | 162.7 | 138.2 | 46.7
206 | 61 | 459 | 183.6 | 214.6178 | 144.8 | 157.6 | 171.3 | 173.3 | 369.7 | 12.4 | 21.8 | 27.6 | 3.5 | 284.9 | 13.4 | 49 | 873.6 | 820.9 | 327.6 | 444.9 | 49.8 | 551.8 | 796.7 | 105.9 | 409.8 | 27.8 | 141.2 | 159.1 | 51.6 | 26.7 | 164 | 139.7 | 47.3
207 | 62 | 459.7 | 183.88 | 214.9451 | 144.3 | 159 | 172.4 | 174.9 | 365.8 | 12.5 | 21.8 | 27.9 | 4.7 | 294.4 | 12.8 | 50.3 | 876.5 | 803.9 | 331.9 | 447.5 | 51.3 | 550.5 | 784.6 | 106 | 413.6 | 28.2 | 142.7 | 161.1 | 52.4 | 27 | 166 | 141.4 | 48.1
208 | 63 | 462.3 | 184.92 | 216.1608 | 144.3 | 160 | 173.2 | 176.1 | 361.9 | 12.6 | 21.8 | 28.1 | 5.6 | 290.2 | 11.3 | 51.6 | 882.7 | 816.6 | 339 | 456.7 | 52.7 | 547.2 | 783.3 | 106 | 419 | 28.7 | 144.4 | 162.5 | 52.8 | 27.3 | 167.2 | 143 | 49
209 | 64 | 462.4 | 184.96 | 216.2076 | 144.2 | 160.2 | 174.2 | 177.4 | 359.3 | 12.7 | 21.8 | 28.4 | 5.8 | 302 | 9.1 | 53 | 889.5 | 826.2 | 347.4 | 466.2 | 54.1 | 546.1 | 786.1 | 106 | 424.5 | 29.2 | 146 | 163.9 | 53.2 | 27.6 | 168.3 | 144.5 | 49.7
210 | 65 | 461.7 | 184.68 | 215.8803 | 144.4 | 160.7 | 175 | 178.3 | 356.1 | 12.6 | 21.8 | 28.6 | 4.7 | 282.5 | 8.6 | 54.4 | 900.8 | 825.7 | 353.6 | 476.8 | 55.5 | 546 | 793.9 | 105.9 | 432.5 | 29.7 | 147.8 | 165.2 | 53.7 | 28 | 169.5 | 146.3 | 50.4
211 | 66 | 460.5 | 184.2 | 215.3192 | 145.4 | 161.5 | 176.2 | 178.9 | 354.3 | 12.7 | 21.8 | 28.9 | 5.9 | 284.4 | 8.1 | 55.8 | 907.5 | 833.4 | 358.3 | 486.3 | 56.8 | 551.5 | 804.2 | 105.9 | 444.1 | 30.2 | 149.1 | 166.8 | 54.8 | 28.3 | 170.4 | 148.2 | 51
212 | 67 | 461 | 184.4 | 215.553 | 146.6 | 161.7 | 177.4 | 179.5 | 365.1 | 12.7 | 21.8 | 29.2 | 6.8 | 281.2 | 9.3 | 57.3 | 907.6 | 820.2 | 358.4 | 491 | 58 | 562.7 | 812.3 | 105.7 | 455.8 | 30.7 | 150.7 | 169.5 | 55.7 | 28.6 | 171.4 | 149.5 | 51.7
213 | 68 | 460.4 | 184.16 | 215.2724 | 147.2 | 163.2 | 179 | 180.5 | 370.5 | 12.8 | 21.8 | 29.5 | 6.9 | 282.4 | 10.2 | 58.8 | 909.3 | 816.2 | 356.2 | 495.3 | 59.2 | 566.4 | 813.9 | 105.3 | 462.9 | 31.1 | 152.7 | 171.2 | 57.1 | 29 | 172.7 | 151 | 52.5
214 | 69 | 460.8 | 184.32 | 215.4595 | 148.7 | 164.6 | 180.9 | 181.4 | 363.9 | 13 | 21.8 | 29.9 | 7.3 | 300 | 10.2 | 60.4 | 910.4 | 810 | 356.9 | 504.3 | 60.4 | 564.9 | 811.3 | 104.8 | 470.7 | 31.7 | 154.3 | 172.2 | 58.2 | 29.3 | 173.8 | 152.3 | 53.3
215 | 70 | 460.5 | 184.2 | 215.3192 | 150.2 | 164.9 | 181.8 | 182.7 | 360.7 | 13.1 | 21.8 | 30.1 | 7 | 293.6 | 12.3 | 62 | 909.8 | 811.3 | 356.8 | 510.2 | 61.5 | 562.8 | 806.3 | 104.2 | 478.3 | 32.1 | 155.7 | 173.7 | 58.6 | 29.7 | 174.9 | 153.2 | 54
216 | 71 | 460.6 | 184.24 | 215.3659 | 150 | 165.6 | 182.9 | 184 | 356.1 | 13.2 | 21.8 | 30.3 | 6.9 | 295.6 | 13.9 | 63.6 | 903 | 824.6 | 359.6 | 519.4 | 62.5 | 560.1 | 803.9 | 103.6 | 485.3 | 32.7 | 157 | 175 | 59.5 | 30 | 176.3 | 154.2 | 54.6
217 | 72 | 463 | 185.2 | 216.4881 | 148.7 | 166 | 184.5 | 185 | 353.9 | 13.2 | 21.8 | 30.5 | 7.8 | 288.5 | 13.7 | 65.3 | 899.6 | 826.3 | 361.6 | 525.6 | 63.5 | 557.8 | 804.2 | 103 | 490.4 | 33.1 | 157.9 | 176 | 60.4 | 30.4 | 177.5 | 155.7 | 55.4
218 | 73 | 462.4 | 184.96 | 216.2076 | 149.5 | 166.7 | 185.4 | 185.6 | 352.8 | 13.3 | 21.8 | 30.7 | 7.4 | 291.3 | 13.8 | 67.1 | 901 | 830.7 | 360.4 | 529.4 | 64.4 | 559.2 | 812.8 | 102.5 | 497.2 | 33.6 | 159.1 | 177.3 | 61.4 | 30.8 | 178.5 | 157.2 | 56.2
219 | 74 | 463.3 | 185.32 | 216.6284 | 148.8 | 167.4 | 185.5 | 186.7 | 352.8 | 13.3 | 21.8 | 30.8 | 8.1 | 297.5 | 14.7 | 69.1 | 900.2 | 825.6 | 358.9 | 533.3 | 65.3 | 556.6 | 812.2 | 102.1 | 502.9 | 34.1 | 160.8 | 178.7 | 62.1 | 31.2 | 179.6 | 158.3 | 56.7
220 | 75 | 465.2 | 186.08 | 217.5168 | 148.4 | 169.3 | 185.3 | 187.5 | 353.9 | 13.3 | 21.8 | 30.9 | 8.6 | 298.1 | 14.8 | 70.9 | 892.5 | 826.7 | 358.8 | 538.7 | 66.3 | 558 | 816.4 | 101.8 | 511.2 | 34.6 | 162.4 | 179.8 | 62.2 | 31.5 | 180.5 | 159 | 57.5
221 | 76 | 465.4 | 186.16 | 217.6103 | 150.9 | 171.2 | 185.1 | 188.1 | 351.5 | 13.4 | 21.8 | 31 | 7 | 291.8 | 14.4 | 72.7 | 881.1 | 836.2 | 360.6 | 545.7 | 67.3 | 560.3 | 818.3 | 101.6 | 519.6 | 35.1 | 163.5 | 180.9 | 62.4 | 31.9 | 181.5 | 159.9 | 58.2
222 | 77 | 465.5 | 186.2 | 217.6571 | 152.1 | 172.5 | 185.3 | 188.7 | 351.5 | 13.5 | 21.8 | 31.1 | 5.5 | 277 | 13.5 | 74.6 | 883.7 | 840.8 | 358.5 | 551.6 | 68.2 | 559.9 | 819.2 | 101.4 | 526.3 | 35.6 | 164.6 | 182.2 | 62.7 | 32.3 | 182.6 | 160.8 | 59
223 | 78 | 468 | 187.2 | 218.826 | 152.2 | 173.5 | 186.3 | 189.6 | 349.7 | 13.5 | 21.8 | 31.2 | 5.7 | 278.7 | 13.3 | 76.4 | 893.8 | 844.6 | 355.2 | 554.3 | 69 | 555 | 815.4 | 101.3 | 529.9 | 36.1 | 165.8 | 182.7 | 63.6 | 32.6 | 183.3 | 162.3 | 59.9
224 | 79 | 465.8 | 186.32 | 217.7973 | 151.4 | 174.9 | 187.4 | 190.5 | 350.2 | 13.5 | 21.8 | 31.3 | 5.3 | 266.1 | 13.9 | 78.3 | 896.5 | 857 | 352 | 561 | 69.8 | 553.9 | 821 | 101.2 | 535.2 | 36.6 | 167.6 | 183.2 | 64.4 | 33 | 183.6 | 163.1 | 60.6
225 | 80 | 465.8 | 186.32 | 217.7973 | 150.9 | 175.9 | 188.7 | 190.8 | 360.5 | 13.5 | 21.8 | 31.5 | 4.7 | 257.3 | 14.8 | 80.2 | 889.1 | 862.9 | 348.5 | 565.2 | 70.6 | 555.8 | 820.5 | 101.1 | 541.5 | 37.1 | 168.8 | 183.9 | 64.9 | 33.4 | 184.4 | 163.8 | 61.2
226 | 81 | 468 | 187.2 | 218.826 | 149.7 | 176.9 | 189.2 | 191.1 | 366.4 | 13.4 | 21.8 | 31.6 | 4.4 | 266.9 | 16.2 | 82.1 | 886.2 | 864.8 | 345 | 571.6 | 71.3 | 560.6 | 830.6 | 101 | 550.1 | 37.6 | 169.9 | 184.8 | 65.6 | 33.7 | 185.5 | 164.8 | 61.8
227 | 82 | 466.9 | 186.76 | 218.3117 | 150.1 | 177 | 189.4 | 191.4 | 365.4 | 13.4 | 21.8 | 31.8 | 4.6 | 269.4 | 16.8 | 84.1 | 891.7 | 849.5 | 340 | 578.2 | 72.1 | 562.4 | 829.8 | 100.9 | 557.7 | 38.1 | 170.8 | 185.5 | 66.7 | 34.1 | 186.8 | 165.7 | 62.4
228 | 83 | 465.8 | 186.32 | 217.7973 | 149.9 | 177.8 | 190 | 192 | 359.4 | 13.4 | 21.8 | 32 | 4.4 | 278.3 | 15 | 86.2 | 896.9 | 846.6 | 333.5 | 584.4 | 72.9 | 554.6 | 816.1 | 100.7 | 561.7 | 38.6 | 172 | 186.8 | 67.9 | 34.5 | 187.9 | 166.6 | 63.1
229 | 84 | 467.4 | 186.96 | 218.5455 | 152.2 | 178.5 | 189.5 | 193.5 | 358.7 | 13.4 | 21.8 | 32.1 | 6.8 | 271.2 | 15.5 | 88.3 | 888.7 | 841.8 | 327.1 | 591.6 | 73.6 | 553.6 | 815.9 | 100.4 | 568 | 39.1 | 173 | 187.9 | 69 | 34.9 | 188.8 | 167.4 | 63.6
230 | 85 | 469.1 | 187.64 | 219.3403 | 154.1 | 179.3 | 189.7 | 194.6 | 359.8 | 13.4 | 21.8 | 32.4 | 7.9 | 271.4 | 17.8 | 90.4 | 890.2 | 836.4 | 321.7 | 595.8 | 74.4 | 549.5 | 807.8 | 99.9 | 572 | 39.6 | 174.2 | 189 | 69.5 | 35.2 | 189.9 | 168.2 | 64.4
231 | 86 | 469 | 187.6 | 219.2936 | 155.4 | 180.7 | 190.1 | 195.8 | 360 | 13.5 | 21.7 | 32.6 | 8.5 | 272.8 | 20.4 | 92.5 | 889.1 | 827.1 | 317 | 599.4 | 75.2 | 542.6 | 790.7 | 99.4 | 574 | 40.1 | 175.1 | 190.1 | 70.8 | 35.6 | 190.8 | 169 | 65.1
232 | 87 | 469.4 | 187.76 | 219.4806 | 158.4 | 182.3 | 191.2 | 197.1 | 356 | 13.5 | 21.7 | 32.7 | 7.8 | 273.7 | 21.9 | 94.7 | 889.8 | 824.6 | 312.4 | 604.8 | 76 | 537.4 | 784.1 | 99.2 | 577.2 | 40.6 | 176 | 191.3 | 72 | 36 | 191.7 | 169.9 | 65.7
233 | 88 | 469.5 | 187.8 | 219.5274 | 160.2 | 183.7 | 192.2 | 197.6 | 354.8 | 13.5 | 21.7 | 32.8 | 7.4 | 277.5 | 20.5 | 96.8 | 899.2 | 801.7 | 306.9 | 613.4 | 76.9 | 536.1 | 788.7 | 99 | 582.6 | 41.1 | 177.2 | 192.7 | 72.3 | 36.3 | 193 | 170.9 | 66.5
234 | 89 | 468.3 | 187.32 | 218.9663 | 161.4 | 184.1 | 194.7 | 197.9 | 353.6 | 13.5 | 21.7 | 33 | 8.1 | 286.7 | 15.4 | 98.9 | 902.6 | 793.6 | 303.9 | 619.8 | 77.8 | 533.7 | 789.2 | 99.1 | 587.1 | 41.5 | 178.1 | 193.7 | 72.2 | 36.7 | 194 | 171.9 | 67.4
235 | 90 | 468 | 187.2 | 218.826 | 162.7 | 184.2 | 195.9 | 198.2 | 353.4 | 13.5 | 21.7 | 33.2 | 9.6 | 288.4 | 13.4 | 101.1 | 892.3 | 802.3 | 303.4 | 624.5 | 78.7 | 532.1 | 786.7 | 99.2 | 589.8 | 42 | 178.8 | 194.2 | 72.4 | 37 | 195.2 | 172.5 | 67.9
236 | 91 | 468.1 | 187.24 | 218.8728 | 162.2 | 183.9 | 196.2 | 198.8 | 348.6 | 13.5 | 21.7 | 33.5 | 9.7 | 288.1 | 13.1 | 103.2 | 881.5 | 807.3 | 303.9 | 629 | 79.6 | 532.8 | 795.1 | 99.5 | 593.4 | 42.5 | 179.7 | 194.9 | 73 | 37.4 | 195.9 | 173.3 | 68.6
237 | 92 | 465.4 | 186.16 | 217.6103 | 161.8 | 182.8 | 196.3 | 199.6 | 347.1 | 13.5 | 21.7 | 33.9 | 8.3 | 260.5 | 15.4 | 105.5 | 878.8 | 810.3 | 305.5 | 632 | 80.6 | 533.6 | 794.7 | 100 | 596.4 | 43 | 180.6 | 195.7 | 74 | 37.8 | 196.6 | 174.2 | 69.4
238 | 93 | 466.9 | 186.76 | 218.3117 | 163.7 | 182.9 | 196.5 | 200.4 | 348.2 | 13.5 | 21.7 | 34.1 | 5.4 | 258.9 | 21.4 | 107.9 | 882.2 | 806.2 | 307.9 | 635.2 | 81.6 | 532.2 | 795.4 | 100.9 | 598.5 | 43.4 | 181.8 | 196.4 | 75.2 | 38.2 | 196.9 | 174.8 | 70
239 | 94 | 466.5 | 186.6 | 218.1246 | 166 | 184.4 | 197.2 | 201.5 | 355.3 | 13.5 | 21.7 | 34.3 | 4.3 | 255.6 | 20.4 | 110.2 | 875.9 | 812.6 | 310.3 | 636.9 | 82.7 | 531.6 | 792.2 | 101.9 | 600.1 | 43.9 | 182.9 | 196.8 | 75.9 | 38.6 | 197.3 | 175.8 | 70.7
240 | 95 | 467.6 | 187.04 | 218.639 | 166.5 | 186.1 | 198.3 | 202.1 | 358.5 | 13.6 | 21.7 | 34.5 | 5.8 | 262.7 | 18.3 | 112.6 | 871.4 | 795.1 | 312 | 637.6 | 83.7 | 531 | 784.9 | 102.9 | 602.5 | 44.4 | 183.9 | 196.9 | 76.9 | 38.9 | 198 | 176.6 | 71.4
241 | 96 | 467.4 | 186.96 | 218.5455 | 168 | 187.8 | 198 | 203.2 | 364.6 | 13.6 | 21.7 | 34.6 | 6.9 | 257.1 | 16.5 | 115 | 866.5 | 786.7 | 313 | 639.8 | 84.8 | 526.9 | 771.3 | 103.9 | 601.8 | 44.8 | 184.6 | 197.1 | 78 | 39.3 | 199.4 | 177.5 | 72.1
242 | 97 | 468.1 | 187.24 | 218.8728 | 169.4 | 188.5 | 197.6 | 204.8 | 363.5 | 13.7 | 21.7 | 34.9 | 6.7 | 270.3 | 16.5 | 117.3 | 865.3 | 796.2 | 314.2 | 643.4 | 85.8 | 525.1 | 772.4 | 105.2 | 603.8 | 45.3 | 185.2 | 197.5 | 79.2 | 39.7 | 200.1 | 178.5 | 72.9
243 | 98 | 468.4 | 187.36 | 219.013 | 169.9 | 189.3 | 197.8 | 205.9 | 362.2 | 13.7 | 21.7 | 35.3 | 5.2 | 274.8 | 17.3 | 119.6 | 859 | 781.6 | 316.4 | 643.8 | 86.8 | 523.6 | 767.8 | 106.9 | 605.2 | 45.8 | 185.9 | 198.3 | 79.8 | 40.1 | 200.9 | 179.8 | 73.8
244 | 99 | 468.1 | 187.24 | 218.8728 | 170.5 | 189.8 | 198.2 | 207.1 | 364.8 | 13.7 | 21.7 | 35.6 | 3.7 | 266.1 | 15.1 | 121.8 | 859.8 | 774 | 318.1 | 646.4 | 87.8 | 524.2 | 773.3 | 109.2 | 606.3 | 46.2 | 186.5 | 199 | 80.2 | 40.4 | 201.8 | 180.5 | 74.6
245 | 100 | 468.2 | 187.28 | 218.9195 | 170.9 | 189.6 | 198.9 | 208.3 | 363.6 | 13.7 | 21.7 | 35.8 | 4 | 280.3 | 12.6 | 124 | 862.2 | 771.3 | 320.2 | 648.4 | 88.8 | 524 | 773.8 | 112.5 | 608.1 | 46.7 | 187.1 | 199.5 | 80.8 | 40.8 | 202.5 | 181.5 | 75.4
246 | 101 | 468.1 | 187.24 | 218.8728 | 170.1 | 189.6 | 199.1 | 209 | 363 | 13.7 | 21.7 | 36 | 4.3 | 258.2 | 12.4 | 126.1 | 854.8 | 782.4 | 324.5 | 652.5 | 89.8 | 528.5 | 782 | 116.4 | 611.1 | 47.2 | 187.8 | 199.7 | 82.1 | 41.2 | 203 | 182.4 | 76.1
247 | 102 | 467.8 | 187.12 | 218.7325 | 169.3 | 190.4 | 199.4 | 210.1 | 364.2 | 13.8 | 21.7 | 36.2 | 4.3 | 256 | 13.7 | 128.2 | 855.6 | 782.2 | 327.5 | 654.9 | 90.8 | 530.4 | 787.9 | 120.2 | 614.5 | 47.6 | 188.6 | 200.3 | 82.6 | 41.6 | 203.6 | 183 | 76.8
248 | 103 | 468.1 | 187.24 | 218.8728 | 172.4 | 190.6 | 199.7 | 210.3 | 362.9 | 13.9 | 21.7 | 36.4 | 4.5 | 263.5 | 13.3 | 130.3 | 856.3 | 779.7 | 329.8 | 656.8 | 91.8 | 530.7 | 794.3 | 123.9 | 616.4 | 48.1 | 189.2 | 200.9 | 83.3 | 42 | 204.1 | 183.7 | 77.4
249 | 104 | 467.9 | 187.16 | 218.7793 | 173.6 | 190.7 | 200.1 | 210.4 | 367.2 | 13.9 | 21.7 | 36.6 | 4.7 | 264.7 | 13.4 | 132.3 | 861.5 | 768 | 330.6 | 657.4 | 92.8 | 529.7 | 789.5 | 127 | 616.6 | 48.6 | 189.9 | 201.2 | 83.6 | 42.3 | 204.5 | 184.3 | 78.1
250 | 105 | 468.5 | 187.4 | 219.0598 | 174 | 190.6 | 200.7 | 210.7 | 369.5 | 13.9 | 21.7 | 36.8 | 4.9 | 270.7 | 14.5 | 134.4 | 860.5 | 773.6 | 330.5 | 657.8 | 93.8 | 525.7 | 773.6 | 130.5 | 616.3 | 49.1 | 190.7 | 201.6 | 84.5 | 42.7 | 204.6 | 185 | 78.9
251 | 106 | 468.5 | 187.4 | 219.0598 | 174.8 | 189.5 | 202.1 | 211.4 | 371.1 | 14 | 21.7 | 36.9 | 4.6 | 270.6 | 15.2 | 136.5 | 856.9 | 769.9 | 331.1 | 660.5 | 94.8 | 518.8 | 756.6 | 133.9 | 615.6 | 49.5 | 191.7 | 201.9 | 84.8 | 43.1 | 204.8 | 185.9 | 79.7
252 | 107 | 468.7 | 187.48 | 219.1533 | 176.2 | 190.8 | 202.7 | 211.5 | 366.1 | 14 | 21.6 | 37 | 5.5 | 272.5 | 14.8 | 138.7 | 856.1 | 765.6 | 332.5 | 662.4 | 95.8 | 513.5 | 746 | 138.1 | 614.6 | 50 | 192 | 203 | 85.4 | 43.5 | 204.9 | 186.6 | 80.6
253 | 108 | 469.5 | 187.8 | 219.5274 | 177.1 | 191.3 | 203.5 | 211.9 | 362.3 | 14.1 | 21.6 | 37 | 5.2 | 271.2 | 13.3 | 140.9 | 853.6 | 767.5 | 334.4 | 665.4 | 96.8 | 512.4 | 747.4 | 145.8 | 616.3 | 50.5 | 192.3 | 203.4 | 86.8 | 43.9 | 205.2 | 187.5 | 81.2
254 | 109 | 469.1 | 187.64 | 219.3403 | 179.1 | 192.2 | 204.5 | 212.3 | 360.9 | 14.2 | 21.6 | 37.1 | 5.2 | 272.8 | 13.3 | 143.1 | 858.2 | 756.3 | 335.7 | 665.9 | 97.8 | 509.9 | 744.5 | 154.5 | 616.3 | 51 | 192.7 | 203.6 | 88 | 44.3 | 205.9 | 188.4 | 82
255 | 110 | 469.3 | 187.72 | 219.4339 | 180.7 | 192.9 | 205 | 212.1 | 359.3 | 14.2 | 21.6 | 37.2 | 5 | 263.6 | 15.4 | 145.4 | 859.2 | 758.6 | 336.9 | 668.9 | 98.8 | 506.5 | 737.7 | 163.8 | 616 | 51.5 | 193.2 | 203.9 | 88.9 | 44.7 | 206.7 | 189 | 82.6
256 | 111 | 469.6 | 187.84 | 219.5741 | 180.6 | 192.9 | 204.9 | 212.2 | 357.2 | 14.3 | 21.6 | 37.4 | 5.7 | 264.6 | 18.2 | 147.7 | 863 | 747.3 | 337.8 | 670.3 | 99.9 | 505.1 | 737.4 | 174.1 | 615.9 | 52 | 194.3 | 204.2 | 89 | 45.1 | 207.3 | 189.8 | 83.3
257 | 112 | 469 | 187.6 | 219.2936 | 181.8 | 193.2 | 204.3 | 212.2 | 359.3 | 14.3 | 21.6 | 37.5 | 4.5 | 261.7 | 17.6 | 150.1 | 864.9 | 740.7 | 338.3 | 670.1 | 100.9 | 502.9 | 740 | 182.4 | 616.1 | 52.5 | 195.3 | 204.5 | 89.2 | 45.5 | 208.3 | 190.6 | 83.9
258 | 113 | 469.9 | 187.96 | 219.7144 | 181.7 | 193.1 | 204.5 | 213 | 364.1 | 14.3 | 21.6 | 37.6 | 4.1 | 265.7 | 17.2 | 152.6 | 863.2 | 728.6 | 338 | 669.9 | 102 | 501.1 | 737.4 | 190.1 | 615.7 | 53 | 196.1 | 204.9 | 90.3 | 45.9 | 209.3 | 191.4 | 84.7
259 | 114 | 468.9 | 187.56 | 219.2468 | 181.7 | 193.1 | 205.4 | 213.7 | 365.3 | 14.4 | 21.6 | 37.6 | 4.6 | 269.8 | 16.7 | 155.2 | 859.4 | 730.2 | 337.5 | 670.8 | 103.1 | 498.2 | 738.1 | 197.3 | 615.2 | 53.4 | 196.7 | 205.6 | 91.7 | 46.3 | 210.2 | 191.9 | 85.5
260 | 115 | 467.7 | 187.08 | 218.6857 | 181.5 | 193.4 | 205.4 | 214.7 | 369.2 | 14.5 | 21.6 | 37.7 | 5 | 272.5 | 15.8 | 157.8 | 849.7 | 719.3 | 336.3 | 668.6 | 104.1 | 496.9 | 735.3 | 204 | 614.5 | 53.9 | 197.3 | 206.4 | 92.9 | 46.8 | 210.6 | 192.4 | 86.3
261 | 116 | 466 | 186.4 | 217.8909 | 182.6 | 193.4 | 205.6 | 215.8 | 374.7 | 14.5 | 21.6 | 37.7 | 5.3 | 268.2 | 13.3 | 160.3 | 843.2 | 723.3 | 335.1 | 668.8 | 105.2 | 495.5 | 735 | 211 | 614.1 | 54.4 | 198 | 207.4 | 93.4 | 47.2 | 210.8 | 192.9 | 87
262 | 117 | 466 | 186.4 | 217.8909 | 182.9 | 194.1 | 207.1 | 217 | 379 | 14.5 | 21.6 | 37.9 | 5.3 | 263.1 | 11.6 | 162.6 | 836.2 | 723.2 | 334.9 | 669.7 | 106.2 | 495.2 | 730.3 | 217.6 | 614.6 | 54.9 | 198.3 | 210.4 | 93.7 | 47.6 | 211.1 | 193.5 | 87.7
263 | 118 | 468.4 | 187.36 | 219.013 | 183.2 | 194.5 | 207.7 | 218.8 | 382.7 | 14.5 | 21.6 | 38 | 5.2 | 271 | 14.8 | 164.8 | 836.2 | 737.8 | 335.9 | 671.6 | 107.2 | 496.9 | 736.2 | 223.7 | 614.9 | 55.4 | 199 | 210.9 | 94.2 | 48 | 212.1 | 194.1 | 88.5
264 | 119 | 468.2 | 187.28 | 218.9195 | 183.2 | 194.8 | 208.7 | 220.2 | 384.5 | 14.5 | 21.6 | 38.2 | 5.4 | 254.9 | 15.2 | 166.9 | 840.8 | 753.2 | 337.7 | 673.5 | 108.2 | 501.2 | 749.6 | 230 | 617.7 | 55.9 | 199.5 | 211.5 | 94.6 | 48.4 | 213.2 | 194.4 | 89.1
265 | 120 | 468.1 | 187.24 | 218.8728 | 182.8 | 195.2 | 209.3 | 221 | 383.3 | 14.6 | 21.6 | 38.4 | 5 | 263.3 | 15.1 | 169 | 841 | 752.7 | 339.9 | 675 | 109.2 | 509.4 | 763 | 236.4 | 621.2 | 56.4 | 200.2 | 212 | 95.3 | 48.9 | 214 | 194.9 | 89.8
266 | 121 | 468.6 | 187.44 | 219.1066 | 183.6 | 195.8 | 209.8 | 221.4 | 382.8 | 14.6 | 21.6 | 38.6 | 4.8 | 265.3 | 15.2 | 170.9 | 846.5 | 775.3 | 342.2 | 678.5 | 110.1 | 512.8 | 765.4 | 241.8 | 623.3 | 56.9 | 200.8 | 212.8 | 96 | 49.3 | 214.9 | 195.3 | 90.6
267 | 122 | 469.6 | 187.84 | 219.5741 | 185.9 | 195.8 | 210.8 | 221.4 | 381.6 | 14.7 | 21.6 | 38.8 | 4 | 280.8 | 16.9 | 172.9 | 854.3 | 775.3 | 344.3 | 678.4 | 111 | 512.8 | 753.6 | 246 | 624.1 | 57.4 | 201.5 | 213.5 | 96.5 | 49.7 | 215.4 | 196.1 | 91.5
268 | 123 | 468.5 | 187.4 | 219.0598 | 186.8 | 196.4 | 211.8 | 221.5 | 377.3 | 14.7 | 21.6 | 38.8 | 3.6 | 270 | 16.2 | 174.8 | 857.1 | 772.9 | 346.5 | 679.4 | 111.9 | 511.4 | 748.5 | 250 | 623.9 | 57.9 | 202.8 | 214 | 96.9 | 50.2 | 215.9 | 196.3 | 92.2
269 | 124 | 469.3 | 187.72 | 219.4339 | 186.8 | 197.3 | 212.8 | 221.5 | 375.2 | 14.8 | 21.6 | 38.9 | 4.6 | 264.4 | 15.1 | 176.7 | 855.2 | 775.6 | 347.7 | 679.1 | 112.8 | 508.1 | 736.8 | 253.5 | 622.5 | 58.4 | 203.9 | 214.1 | 98.2 | 50.6 | 216.2 | 196.8 | 92.8
270 | 125 | 469 | 187.6 | 219.2936 | 186.3 | 197.9 | 213.3 | 221 | 376.9 | 14.8 | 21.6 | 39 | 5.7 | 280.8 | 14.4 | 178.6 | 853.7 | 779 | 349.1 | 678.7 | 113.7 | 508 | 743.6 | 257 | 622.3 | 58.9 | 204.3 | 214.4 | 99 | 51.1 | 216.6 | 197.6 | 93.6
271 | 126 | 468.7 | 187.48 | 219.1533 | 186.9 | 198.5 | 213.5 | 219.4 | 379.4 | 14.9 | 21.5 | 39.1 | 6.7 | 259.9 | 14.3 | 180.5 | 855.6 | 776.6 | 350.6 | 679.4 | 114.6 | 511.3 | 747.4 | 260.3 | 623.6 | 59.4 | 204.9 | 214.6 | 99.4 | 51.5 | 217.1 | 198.5 | 94.3
272 | 127 | 469.4 | 187.76 | 219.4806 | 186.5 | 198.9 | 213.4 | 218.9 | 387.3 | 14.9 | 21.6 | 39.1 | 6.3 | 254.9 | 13.4 | 182.5 | 856.2 | 777.9 | 351.6 | 680.8 | 115.5 | 516.2 | 751.7 | 263.8 | 625.1 | 59.9 | 205.7 | 214.7 | 99.9 | 52 | 217.8 | 199.1 | 95
273 | 128 | 467.1 | 186.84 | 218.4052 | 184.7 | 199 | 212.9 | 218.9 | 385.8 | 15 | 21.6 | 39.2 | 5.5 | 281.2 | 11.8 | 184.4 | 855.3 | 780 | 352.6 | 682.4 | 116.4 | 515.6 | 747.5 | 265.9 | 625 | 60.4 | 205.8 | 215.1 | 100.1 | 52.4 | 218.1 | 199.7 | 95.8
274 | 129 | 467.4 | 186.96 | 218.5455 | 182.9 | 198.6 | 211.6 | 219.1 | 383.2 | 15.1 | 21.6 | 39.4 | 5.1 | 285.1 | 14.2 | 186.4 | 854.2 | 787 | 354.1 | 684.8 | 117.3 | 520.6 | 758.7 | 268.6 | 626.9 | 60.9 | 206.1 | 215.7 | 100.8 | 52.9 | 218.4 | 199.8 | 96.4
275 | 130 | 467.5 | 187 | 218.5922 | 183.4 | 198.5 | 210.3 | 219.2 | 383.3 | 15.1 | 21.5 | 39.7 | 5.2 | 293.4 | 16.5 | 188.5 | 858.2 | 789.8 | 355.7 | 685.7 | 118.3 | 519 | 752.2 | 270.8 | 626.4 | 61.4 | 206.4 | 216.5 | 101.5 | 53.3 | 218.6 | 200 | 97.1
276 | 131 | 466.5 | 186.6 | 218.1246 | 184 | 198.2 | 209.8 | 219.4 | 378.7 | 15.2 | 21.5 | 40 | 4.5 | 270.3 | 15.7 | 190.6 | 860 | 781.5 | 356.9 | 684.5 | 119.3 | 515.4 | 744.9 | 272.6 | 624.8 | 61.9 | 207 | 216.9 | 102.3 | 53.8 | 218.8 | 200.2 | 97.6
277 | 132 | 467.1 | 186.84 | 218.4052 | 184.8 | 198.4 | 211 | 220.1 | 376.6 | 15.2 | 21.5 | 40.1 | 3.9 | 275.4 | 14.8 | 192.8 | 856 | 788.9 | 358.1 | 687.6 | 120.2 | 517.6 | 755.6 | 274.6 | 626.7 | 62.4 | 207.4 | 217 | 103 | 54.3 | 218.8 | 200.5 | 98.4
278 | 133 | 466.5 | 186.6 | 218.1246 | 185.4 | 198.7 | 211.8 | 220.5 | 376.7 | 15.2 | 21.5 | 40.2 | 4 | 258.9 | 14.4 | 194.9 | 849.6 | 773.5 | 359 | 687.2 | 121.2 | 518.4 | 757.2 | 276.1 | 626.2 | 62.9 | 207.7 | 217.3 | 104.2 | 54.7 | 218.9 | 201 | 99.1
279 | 134 | 467.9 | 187.16 | 218.7793 | 186.1 | 198.1 | 211.9 | 219.9 | 378.7 | 15.3 | 21.5 | 40.2 | 3.9 | 262.6 | 14.8 | 197 | 846 | 756.5 | 359.4 | 685.6 | 122.2 | 518.4 | 746.6 | 276.9 | 625.4 | 63.4 | 208.2 | 217.6 | 105.5 | 55.2 | 218.9 | 201.8 | 99.8
280 | 135 | 467.6 | 187.04 | 218.639 | 186.9 | 197.7 | 212.7 | 219.5 | 383.4 | 15.4 | 21.5 | 40.2 | 3.3 | 265.3 | 15.1 | 199.1 | 839.6 | 743.4 | 359.6 | 684.9 | 123.2 | 517.3 | 741.3 | 277.5 | 624.5 | 63.9 | 208.7 | 217.9 | 106.5 | 55.6 | 218.8 | 202.4 | 100.4
281 | 136 | 466 | 186.4 | 217.8909 | 187.8 | 198.2 | 213.9 | 219.9 | 386.8 | 15.6 | 21.5 | 40.3 | 3.5 | 262.4 | 15.4 | 201.2 | 833.2 | 728.8 | 359.2 | 682.5 | 124.2 | 514.5 | 728.7 | 277.8 | 622.3 | 64.4 | 209.3 | 218.5 | 107.1 | 56.1 | 218.9 | 203.1 | 101.2
282 | 137 | 467 | 186.8 | 218.3584 | 190.7 | 199 | 214.6 | 220.2 | 386.9 | 15.7 | 21.5 | 40.4 | 4.2 | 257.3 | 15.1 | 203.4 | 822.2 | 711.9 | 358.4 | 681.3 | 125.2 | 510.3 | 722.8 | 277.9 | 619.9 | 65 | 209.7 | 219.3 | 107.7 | 56.6 | 219.2 | 203.7 | 102.1
283 | 138 | 467.3 | 186.92 | 218.4987 | 191.5 | 200.2 | 215.5 | 220.4 | 391.7 | 15.8 | 21.5 | 40.6 | 3.9 | 263.5 | 13.9 | 205.7 | 805.3 | 694.5 | 357.5 | 679.6 | 126.2 | 508.3 | 719.4 | 278 | 617.9 | 65.5 | 210.2 | 220.2 | 108.3 | 57 | 220.3 | 203.9 | 102.7
284 | 139 | 469.1 | 187.64 | 219.3403 | 191.3 | 201.4 | 216.5 | 220.8 | 397.8 | 15.9 | 21.5 | 40.9 | 4.4 | 261.5 | 13.9 | 208.1 | 799.6 | 683.3 | 356.5 | 678.4 | 127.3 | 507.7 | 714.9 | 278.1 | 616.1 | 66 | 210.7 | 221 | 108.8 | 57.5 | 220.8 | 204.1 | 103.3
285 | 140 | 466.6 | 186.64 | 218.1714 | 190.4 | 202.2 | 217.4 | 221 | 408.8 | 16 | 21.5 | 41.1 | 4.2 | 254.5 | 13.8 | 210.4 | 796.1 | 668.3 | 355.3 | 677.1 | 128.3 | 506.2 | 704.3 | 278 | 613.6 | 66.5 | 211.2 | 221.9 | 109.3 | 57.9 | 221.8 | 204.5 | 103.9
286 | 141 | 466.2 | 186.48 | 217.9844 | 190.5 | 202.4 | 218.3 | 221 | 407.8 | 16 | 21.5 | 41.3 | 4.9 | 263.2 | 14.1 | 212.7 | 786.5 | 668.7 | 354 | 676.4 | 129.4 | 503.3 | 701.5 | 277.9 | 611.7 | 67 | 212.2 | 222.8 | 110 | 58.3 | 222.6 | 204.9 | 104.5
287 | 142 | 466.2 | 186.48 | 217.9844 | 189.9 | 202.3 | 218.5 | 221.3 | 405.6 | 16 | 21.5 | 41.5 | 4.8 | 265.1 | 14.3 | 214.9 | 781.3 | 652.9 | 353 | 675.3 | 130.4 | 500.4 | 696.6 | 278 | 610 | 67.5 | 213.3 | 223.2 | 110.9 | 58.8 | 223.5 | 205.2 | 105.2
288 | 143 | 466.2 | 186.48 | 217.9844 | 190.3 | 202.5 | 219.6 | 222 | 405.5 | 16.1 | 21.5 | 41.7 | 4.9 | 276.2 | 13.3 | 217.1 | 774.9 | 665.9 | 352 | 675.6 | 131.5 | 498.8 | 692.6 | 278 | 608.4 | 68 | 213.8 | 223.7 | 111.6 | 59.2 | 223.8 | 205.1 | 105.7
289 | 144 | 465.5 | 186.2 | 217.6571 | 190.3 | 202.6 | 220.1 | 222.9 | 407.4 | 16.1 | 21.5 | 41.8 | 4.9 | 263.7 | 12.3 | 219.2 | 786.5 | 688.7 | 351.2 | 677.3 | 132.6 | 500.5 | 701.7 | 278.8 | 609.2 | 68.5 | 214.4 | 224.3 | 112.1 | 59.7 | 224.1 | 205.2 | 106.4
290 | 145 | 465.1 | 186.04 | 217.47 | 190 | 202.4 | 220.4 | 223.4 | 407.7 | 16.1 | 21.5 | 41.9 | 4 | 254.7 | 12.3 | 221.4 | 798.1 | 726.6 | 350.9 | 682 | 133.7 | 506.8 | 724.2 | 280.4 | 613.2 | 69 | 215 | 224.8 | 112.8 | 60.1 | 224.2 | 205.5 | 107
291 | 146 | 466.1 | 186.44 | 217.9376 | 190.7 | 202.3 | 221 | 223.5 | 408.1 | 16.2 | 21.5 | 42.1 | 4.5 | 259.7 | 11.8 | 223.6 | 807.4 | 741.9 | 351 | 683.6 | 134.8 | 514 | 730.9 | 281.9 | 617 | 69.5 | 215.7 | 225.4 | 113.7 | 60.5 | 224.5 | 205.8 | 107.6
292 | 147 | 466.7 | 186.68 | 218.2182 | 189.6 | 202.5 | 221.4 | 223.7 | 410.9 | 16.2 | 21.5 | 42.4 | 5.3 | 255.6 | 14.2 | 225.9 | 815.4 | 749.1 | 351.3 | 685.4 | 135.9 | 515.4 | 727.6 | 282.8 | 618.1 | 70 | 216.1 | 226 | 114.6 | 61 | 225.3 | 206 | 108.3
293 | 148 | 465.7 | 186.28 | 217.7506 | 188.7 | 202.9 | 221.8 | 224.4 | 408.2 | 16.2 | 21.5 | 42.6 | 6 | 257.5 | 16.7 | 228.4 | 823.5 | 752.1 | 351.9 | 687.1 | 137 | 518.6 | 742.3 | 284.2 | 620.4 | 70.5 | 216.4 | 226.1 | 115.3 | 61.4 | 225.6 | 206.1 | 108.8
294 | 149 | 468.2 | 187.28 | 218.9195 | 187.5 | 203.1 | 222.4 | 224.8 | 401.7 | 16.3 | 21.5 | 42.8 | 5.9 | 251.2 | 17.8 | 231 | 831.5 | 759.7 | 352.8 | 687.6 | 138.1 | 522.5 | 752.4 | 285.7 | 622.4 | 71 | 216.5 | 226.6 | 116.2 | 61.8 | 225.7 | 206.7 | 109.4
295 | 150 | 468.5 | 187.4 | 219.0598 | 186.7 | 202.8 | 222.8 | 225.3 | 397.8 | 16.3 | 21.4 | 43 | 5.7 | 263.4 | 18.2 | 233.7 | 841.3 | 772.6 | 353.9 | 689.3 | 139.2 | 523.8 | 752.2 | 286.7 | 623.6 | 71.5 | 217.1 | 226.8 | 116.9 | 62.2 | 225.7 | 207.3 | 110
296 | 151 | 469.1 | 187.64 | 219.3403 | 186.5 | 202.6 | 222.8 | 225.3 | 402.5 | 16.4 | 21.4 | 43 | 4.6 | 255.8 | 21.2 | 236.3 | 841.3 | 772.5 | 354.9 | 689.4 | 140.3 | 526.9 | 753.8 | 287.6 | 625.2 | 72 | 217.5 | 227.3 | 117.5 | 62.7 | 225.8 | 207.4 | 110.7
297 | 152 | 469.6 | 187.84 | 219.5741 | 185.1 | 203.1 | 223 | 226.1 | 409.1 | 16.5 | 21.4 | 43.1 | 4.9 | 251.4 | 21.2 | 238.7 | 840.1 | 775.3 | 355.7 | 692.3 | 141.4 | 526.9 | 750.8 | 288 | 625 | 72.5 | 218 | 227.7 | 118.2 | 63.1 | 226 | 207.6 | 111.3
298 | 153 | 468.7 | 187.48 | 219.1533 | 185 | 204.3 | 223.3 | 226.9 | 407.6 | 16.7 | 21.4 | 43.2 | 5.3 | 246.6 | 19.8 | 241.1 | 845.6 | 758 | 356.2 | 692.4 | 142.5 | 526.8 | 749.7 | 288.7 | 625.1 | 73 | 218.5 | 227.8 | 118.6 | 63.5 | 226.3 | 207.9 | 111.9
299 | 154 | 468 | 187.2 | 218.826 | 185.5 | 205 | 223.8 | 226.9 | 404.1 | 16.7 | 21.4 | 43.3 | 5.7 | 241.8 | 17.2 | 243.4 | 841.1 | 738.7 | 356.6 | 691.4 | 143.6 | 525.1 | 746.6 | 289.1 | 624 | 73.5 | 218.5 | 227.9 | 119.5 | 63.9 | 226.4 | 208 | 112.5
300 | 155 | 466.3 | 186.52 | 218.0311 | 188.4 | 205.1 | 223.7 | 226.4 | 398.8 | 16.9 | 21.4 | 43.3 | 7.2 | 255.1 | 15 | 245.6 | 839.8 | 733.8 | 357 | 691.5 | 144.7 | 521.9 | 743 | 289.5 | 623.3 | 74 | 218.8 | 228.1 | 120.2 | 64.3 | 227.4 | 208.5 | 113.3
301 | 156 | 466.6 | 186.64 | 218.1714 | 190.7 | 205.2 | 223.3 | 226.2 | 394.4 | 17 | 21.4 | 43.4 | 7.4 | 266.3 | 19.5 | 247.7 | 843.8 | 730.2 | 357.2 | 691.7 | 145.8 | 518.3 | 731 | 290 | 622.7 | 74.5 | 219.2 | 228.4 | 121.1 | 64.8 | 227.8 | 209 | 114
302 | 157 | 467.1 | 186.84 | 218.4052 | 191.9 | 205.6 | 223.2 | 226.2 | 394.3 | 17.1 | 21.4 | 43.4 | 6.6 | 259 | 20.3 | 249.9 | 838.2 | 731.2 | 357.3 | 692.5 | 146.9 | 513.7 | 716.9 | 290.1 | 620.8 | 75 | 219.7 | 228.7 | 122.6 | 65.2 | 228.1 | 209.3 | 114.5
303 | 158 | 467.9 | 187.16 | 218.7793 | 191.8 | 205.8 | 223.7 | 226.5 | 390.8 | 17.2 | 21.4 | 43.4 | 6 | 265 | 17.6 | 252.1 | 839 | 727.5 | 357.2 | 692.7 | 148 | 511.7 | 721.3 | 290.4 | 620.4 | 75.4 | 220.1 | 229 | 123.2 | 65.6 | 228.3 | 209.4 | 115.2
304 | 159 | 467.9 | 187.16 | 218.7793 | 193.2 | 206 | 223.6 | 226.3 | 392.4 | 17.3 | 21.4 | 43.5 | 5.4 | 271.7 | 20.4 | 254.5 | 833 | 712 | 357.2 | 692.2 | 149.1 | 511.3 | 720.2 | 290.7 | 620.3 | 75.9 | 220.3 | 229.9 | 123.7 | 66 | 228.1 | 209.5 | 115.7
305 | 160 | 467.6 | 187.04 | 218.639 | 195.2 | 207 | 223.5 | 226.6 | 392.1 | 17.4 | 21.4 | 43.6 | 5.5 | 272.8 | 20.3 | 256.9 | 836.6 | 726.1 | 357.1 | 694.8 | 150.2 | 510.9 | 726.3 | 290.9 | 621 | 76.4 | 220.6 | 230.2 | 124 | 66.5 | 228 | 209.9 | 116.2
306 | 161 | 468.3 | 187.32 | 218.9663 | 196.2 | 206.6 | 223.4 | 226.8 | 392.3 | 17.5 | 21.4 | 43.7 | 4.5 | 269.1 | 18 | 259.1 | 840.3 | 732.4 | 357.1 | 696.7 | 151.3 | 511.6 | 728.5 | 291.2 | 621.8 | 76.9 | 220.7 | 230.4 | 124.4 | 66.9 | 228.1 | 210.3 | 116.7
307 | 162 | 467.8 | 187.12 | 218.7325 | 197.8 | 206.7 | 223.3 | 227.1 | 393.7 | 17.4 | 21.4 | 43.9 | 4.3 | 250.1 | 16.1 | 260.9 | 845.2 | 730.8 | 357.1 | 695.8 | 152.4 | 512.1 | 725.9 | 291.4 | 622 | 77.4 | 221.1 | 231.4 | 125.2 | 67.3 | 228.4 | 210.8 | 117.4
308 | 163 | 469.2 | 187.68 | 219.3871 | 198.7 | 206.5 | 223.8 | 227.5 | 398.1 | 17.4 | 21.4 | 44.2 | 4.2 | 247.4 | 15.5 | 262.6 | 845.4 | 735.7 | 357.1 | 695.8 | 153.5 | 511.7 | 724.4 | 291.3 | 621.8 | 77.9 | 221.9 | 231.9 | 126.2 | 67.8 | 228.8 | 211.2 | 117.9
309 | 164 | 470.1 | 188.04 | 219.8079 | 198.4 | 206.6 | 225.2 | 228.3 | 406.3 | 17.4 | 21.4 | 44.4 | 3.7 | 261.8 | 13.6 | 264 | 840.4 | 761 | 357.1 | 698.7 | 154.6 | 513 | 727.3 | 291.4 | 622.8 | 78.4 | 222.5 | 232.3 | 126.8 | 68.2 | 228.9 | 211.4 | 118.5
310 | 165 | 471 | 188.4 | 220.2287 | 197.7 | 206.9 | 225.6 | 229 | 409.5 | 17.4 | 21.4 | 44.5 | 3.9 | 243.1 | 11.3 | 265.1 | 846.6 | 767.2 | 357.1 | 701.6 | 155.8 | 513.9 | 734.7 | 291.9 | 624.8 | 78.9 | 223 | 232.7 | 127.6 | 68.6 | 229.3 | 211.7 | 119.2
311 | 166 | 472.1 | 188.84 | 220.7431 | 197.7 | 207.8 | 226.4 | 229 | 404.4 | 17.4 | 21.4 | 44.6 | 4.2 | 259.1 | 8.6 | 266.3 | 850.8 | 778 | 357.4 | 705.7 | 156.9 | 515.2 | 737.8 | 293 | 628.2 | 79.3 | 223.5 | 233.4 | 128.3 | 69 | 229.7 | 212 | 119.8
312 | 167 | 472.1 | 188.84 | 220.7431 | 197.6 | 208.5 | 227.3 | 228.7 | 397.5 | 17.5 | 21.4 | 44.7 | 4.9 | 257.1 | 7 | 267.4 | 849.4 | 794.3 | 357.7 | 707.7 | 158.1 | 519.6 | 752.8 | 294.2 | 633.2 | 79.8 | 223.7 | 234.1 | 128.5 | 69.4 | 230.3 | 212.4 | 120.5
313 | 168 | 471.3 | 188.52 | 220.369 | 197.5 | 208.9 | 228 | 228.4 | 399.1 | 17.7 | 21.4 | 44.8 | 5.5 | 263.3 | 6.7 | 268.4 | 861 | 791.9 | 358 | 708.2 | 159.3 | 525.2 | 753.1 | 295.1 | 635.7 | 80.3 | 224 | 234.6 | 128.8 | 69.9 | 230.6 | 212.9 | 121.3
314 | 169 | 469.2 | 187.68 | 219.3871 | 197.7 | 208.6 | 228.1 | 228.1 | 406.1 | 17.7 | 21.4 | 44.9 | 5.4 | 257.7 | 6.3 | 269.4 | 858.9 | 793.5 | 358.3 | 709.1 | 160.4 | 528.8 | 749.1 | 295.7 | 636.6 | 80.8 | 224.4 | 235.1 | 129.6 | 70.3 | 231 | 213.4 | 121.9
315 | 170 | 469.7 | 187.88 | 219.6209 | 197.3 | 208.8 | 229.2 | 228.6 | 411.9 | 17.7 | 21.4 | 45 | 4.4 | 229.8 | 5.7 | 270.5 | 857.9 | 800.8 | 358.4 | 710.8 | 161.6 | 534.7 | 760.2 | 296.7 | 640.3 | 81.3 | 224.7 | 235.3 | 130.2 | 70.7 | 231.4 | 213.6 | 122.6
316 | 171 | 471.4 | 188.56 | 220.4158 | 197.4 | 209.3 | 229.3 | 229.2 | 415.9 | 17.8 | 21.4 | 45 | 6.2 | 233.3 | 5.3 | 271.6 | 866.2 | 791 | 358.4 | 710.2 | 162.8 | 536.7 | 764 | 297.4 | 641.2 | 81.8 | 225.5 | 235.8 | 130.9 | 71.1 | 231.7 | 214.3 | 123.2
317 | 172 | 469.8 | 187.92 | 219.6677 | 198.2 | 210.3 | 229.3 | 229.5 | 413.4 | 17.8 | 21.4 | 45.1 | 7 | 260 | 6 | 272.7 | 864.3 | 792.5 | 358.3 | 710.1 | 164 | 537.3 | 763.1 | 297.6 | 641.3 | 82.2 | 226.4 | 236.3 | 131.5 | 71.6 | 232.2 | 214.6 | 123.8
318 | 173 | 469.4 | 187.76 | 219.4806 | 198.4 | 211.3 | 229.9 | 229.5 | 417 | 17.8 | 21.4 | 45.1 | 6.3 | 248.1 | 7.3 | 273.6 | 863.6 | 790.8 | 358.2 | 712.7 | 165.2 | 539.6 | 769 | 298.1 | 642.7 | 82.7 | 227.1 | 236.6 | 132.3 | 72 | 233 | 215.1 | 124.3
319 | 174 | 470.5 | 188.2 | 219.995 | 199 | 212.4 | 230.8 | 230.4 | 419.6 | 17.9 | 21.4 | 45.2 | 5.8 | 257.5 | 8.2 | 274.6 | 864.5 | 795.4 | 358.1 | 712.9 | 166.4 | 541.5 | 769.4 | 298.7 | 645.2 | 83.2 | 227.6 | 237.2 | 133.1 | 72.4 | 233.4 | 215.4 | 125
320 | 175 | 469.3 | 187.72 | 219.4339 | 200.3 | 213 | 231.6 | 230.4 | 419.6 | 17.9 | 21.4 | 45.2 | 5.6 | 253.2 | 7.9 | 275.9 | 863.3 | 802.5 | 358 | 715.4 | 167.6 | 545.8 | 786 | 299.7 | 648.7 | 83.7 | 228 | 237.5 | 133.7 | 72.9 | 233.7 | 215.5 | 125.6
321 | 176 | 470.1 | 188.04 | 219.8079 | 200.7 | 213.2 | 232.2 | 230.6 | 422.2 | 18 | 21.4 | 45.4 | 3.9 | 240.8 | 9.6 | 277 | 858.7 | 801.9 | 357.9 | 715.7 | 168.8 | 550.5 | 789.6 | 300.5 | 650.9 | 84.2 | 228.2 | 238.1 | 134.7 | 73.3 | 234.1 | 216.1 | 126.3
322 | 177 | 470.3 | 188.12 | 219.9014 | 200.3 | 213 | 232.7 | 231 | 420.6 | 18.1 | 21.4 | 45.4 | 7.2 | 231.9 | 14.6 | 278.5 | 874.4 | 782.5 | 357.9 | 714.6 | 170 | 550.4 | 779.9 | 301 | 651.4 | 84.7 | 228.7 | 238.4 | 135.2 | 73.7 | 234.9 | 216.9 | 126.8
323 | 178 | 468.6 | 187.44 | 219.1066 | 200.6 | 212.8 | 232.5 | 232.4 | 417.5 | 18.1 | 21.4 | 45.7 | 10.7 | 249.5 | 16.9 | 279.8 | 880.6 | 789.8 | 357.8 | 715.9 | 171.2 | 550.5 | 789 | 301.7 | 652.2 | 85.1 | 228.8 | 238.6 | 135.7 | 74.1 | 235.4 | 217.7 | 127.6
324 | 179 | 471.5 | 188.6 | 220.4625 | 201.1 | 213.5 | 232.4 | 233.4 | 417.1 | 18.2 | 21.4 | 45.9 | 8.8 | 250.3 | 20.4 | 280.9 | 884.2 | 794.7 | 357.7 | 717.3 | 172.5 | 554.7 | 793.9 | 302.5 | 655.1 | 85.6 | 229 | 238.7 | 136.2 | 74.6 | 235.4 | 218.1 | 128.3
325 | 180 | 470.3 | 188.12 | 219.9014 | 202 | 214.8 | 232.6 | 233.3 | 421.4 | 18.2 | 21.4 | 46 | 8.4 | 262.5 | 19.9 | 282.2 | 882.9 | 807 | 357.4 | 719.5 | 173.7 | 558.2 | 795.2 | 303.3 | 659 | 86.1 | 229.4 | 238.9 | 137.4 | 75 | 235.5 | 218.3 | 128.9
326 | 181 | 469.1 | 187.64 | 219.3403 | 202.8 | 215.5 | 232.2 | 233.1 | 427.7 | 18.2 | 21.4 | 46.1 | 7.1 | 247.1 | 17 | 284.3 | 877.8 | 806.4 | 357.1 | 720.1 | 175 | 562.3 | 798.9 | 304.2 | 662.4 | 86.6 | 229.8 | 239 | 138.8 | 75.4 | 235.5 | 218.5 | 129.4
327 | 182 | 470.9 | 188.36 | 220.182 | 203.6 | 215.5 | 232.7 | 233 | 427.7 | 18.2 | 21.4 | 46 | 5.8 | 236.4 | 15.8 | 286.3 | 877.1 | 785.4 | 356.8 | 719 | 176.2 | 562.6 | 799.8 | 304.7 | 663.1 | 87.1 | 229.9 | 239 | 139.5 | 75.9 | 235.6 | 218.5 | 129.9
328 | 183 | 471.2 | 188.48 | 220.3223 | 203.9 | 215.1 | 232.7 | 232.9 | 424.5 | 18.3 | 21.3 | 46 | 4.9 | 235.7 | 16 | 288 | 869.7 | 774.9 | 356.4 | 719 | 177.5 | 563.2 | 804.2 | 305.2 | 663.7 | 87.6 | 230.3 | 239.3 | 140.1 | 76.3 | 235.6 | 218.3 | 130.4
329 | 184 | 469.2 | 187.68 | 219.3871 | 204.3 | 215.4 | 233.6 | 232.9 | 423.8 | 18.3 | 21.3 | 45.9 | 5.1 | 257.1 | 14.4 | 289.5 | 871.8 | 770.9 | 356 | 719.4 | 178.7 | 565 | 804.5 | 305.8 | 664.7 | 88.1 | 230.7 | 239.2 | 140.7 | 76.7 | 235.9 | 218.3 | 131.1
330 | 185 | 467.9 | 187.16 | 218.7793 | 203.9 | 215.6 | 234.4 | 232.9 | 420.2 | 18.3 | 21.4 | 46 | 4.7 | 238.6 | 16 | 291.2 | 871.9 | 783.4 | 355.6 | 721 | 180 | 566.8 | 805.6 | 306.2 | 666.2 | 88.6 | 231.1 | 239.4 | 141 | 77.2 | 236.5 | 218.4 | 131.6
331 | 186 | 468.8 | 187.52 | 219.2001 | 204 | 216.2 | 233.9 | 233.5 | 417.8 | 18.4 | 21.4 | 46 | 5.7 | 236.4 | 15 | 293 | 871.6 | 774.8 | 355.3 | 720.7 | 181.3 | 565.8 | 803.6 | 306.6 | 666 | 89.1 | 231.2 | 239.4 | 141.5 | 77.6 | 236.6 | 218.7 | 132.2
332 | 187 | 469.2 | 187.68 | 219.3871 | 203.1 | 216.9 | 234 | 234.2 | 414.9 | 18.4 | 21.4 | 46 | 6.5 | 249.2 | 13.2 | 294.5 | 866.2 | 778.5 | 354.9 | 721.4 | 182.7 | 565 | 802.9 | 307.2 | 666.9 | 89.6 | 231.4 | 239.4 | 141.9 | 78 | 236.9 | 218.9 | 132.7
333 | 188 | 470.8 | 188.32 | 220.1352 | 202.4 | 218 | 233.9 | 234.3 | 413.7 | 18.5 | 21.3 | 46.1 | 7.8 | 238.6 | 11.8 | 295.7 | 867.4 | 785.1 | 354.7 | 722.2 | 184.2 | 564.4 | 804.7 | 307.8 | 667.9 | 90.1 | 231.4 | 239.6 | 142.5 | 78.5 | 237.2 | 219.1 | 133.2
334 | 189 | 470 | 188 | 219.7612 | 202.3 | 217.9 | 233.7 | 234.8 | 414.9 | 18.5 | 21.3 | 46.3 | 4.6 | 232.2 | 10 | 296.7 | 862.6 | 785.1 | 354.4 | 724.4 | 185.9 | 564.9 | 803.7 | 308.5 | 669.6 | 90.6 | 231.7 | 240 | 143.3 | 78.9 | 237.6 | 219.6 | 133.6
335 | 190 | 467.8 | 187.12 | 218.7325 | 203.2 | 217.6 | 233.6 | 235.1 | 418.8 | 18.6 | 21.3 | 46.5 | 4.5 | 222.7 | 7.3 | 298 | 861.4 | 792.7 | 354.3 | 724.6 | 187.6 | 568.7 | 811.3 | 309.5 | 672.6 | 91.1 | 231.9 | 240 | 143.9 | 79.3 | 237.7 | 219.9 | 134.2
336 | 191 | 466.9 | 186.76 | 218.3117 | 204.2 | 218.4 | 233.9 | 235.8 | 419 | 18.6 | 21.3 | 46.6 | 6 | 267.2 | 12.8 | 299.6 | 802.3 | 793.2 | 349.7 | 725.2 | 189.4 | 571.1 | 817.5 | 310.6 | 674.3 | 91.6 | 231.9 | 239.9 | 144.4 | 79.7 | 238.1 | 220.1 | 134.7
337 | 192 | 467.8 | 187.12 | 218.7325 | 204.6 | 219 | 233.9 | 236.2 | 414.2 | 18.6 | 21.3 | 46.8 | 5 | 259.2 | 15.4 | 301.1 | 801.6 | 807.9 | 353.2 | 728.8 | 191.5 | 571.9 | 821.1 | 311.7 | 677.3 | 92 | 231.8 | 240 | 144.5 | 80.1 | 238.6 | 220.7 | 135.2
338 | 193 | 468 | 187.2 | 218.826 | 205.6 | 219.3 | 233.4 | 236.5 | 408.5 | 18.7 | 21.3 | 47 | 3.8 | 266.4 | 14.3 | 302.5 | 854.1 | 806.7 | 354.5 | 728.9 | 194.6 | 570.6 | 817.6 | 312.8 | 679.2 | 92.5 | 232 | 240.1 | 145.1 | 80.6 | 238.8 | 220.9 | 135.9
339 | 194 | 467.9 | 187.16 | 218.7793 | 208.8 | 219 | 233.4 | 236.4 | 404.2 | 18.9 | 21.3 | 47.1 | 4 | 261.2 | 13.1 | 303.3 | 855.6 | 826.9 | 354.7 | 732.6 | 198.3 | 570.3 | 818.6 | 314 | 681.4 | 93 | 232.1 | 240.2 | 145.8 | 81 | 238.9 | 221.3 | 136.4
340 | 195 | 467.9 | 187.16 | 218.7793 | 208.7 | 219 | 233.2 | 236.3 | 401.2 | 19 | 21.3 | 47.2 | 5.1 | 250.8 | 15.4 | 304.5 | 862.8 | 817.1 | 355 | 733.3 | 202.3 | 570.9 | 822.7 | 315 | 684.2 | 93.5 | 232.2 | 240.4 | 146 | 81.4 | 238.8 | 221.6 | 137.1
341 | 196 | 469 | 187.6 | 219.2936 | 205.1 | 217.9 | 232.9 | 236.3 | 400.5 | 19.1 | 21.3 | 47.4 | 7.7 | 248.5 | 15.5 | 305.6 | 872.7 | 816.5 | 355.5 | 732.8 | 206.2 | 571.2 | 821.7 | 316.1 | 685.3 | 94 | 232.3 | 240.9 | 146.5 | 81.8 | 238.9 | 221.5 | 137.6
342 | 197 | 469.4 | 187.76 | 219.4806 | 203.5 | 217.9 | 233.4 | 235.7 | 401.5 | 19.2 | 21.3 | 47.5 | 7.5 | 255 | 13.6 | 307 | 878.1 | 817.5 | 355.9 | 737.2 | 210 | 571.5 | 825.5 | 317.3 | 688.2 | 94.5 | 232.5 | 240.7 | 147.1 | 82.2 | 239 | 221.9 | 138
343 | 198 | 470.4 | 188.16 | 219.9482 | 202.3 | 218 | 233.9 | 235.6 | 396.1 | 19.2 | 21.3 | 47.7 | 7.5 | 275.6 | 14.3 | 308.4 | 874.7 | 814.7 | 356.4 | 738.7 | 213.2 | 570.7 | 818.2 | 318.3 | 691.2 | 95 | 232.7 | 240.5 | 147.5 | 82.7 | 239.2 | 222.3 | 138.6
344 | 199 | 470 | 188 | 219.7612 | 200.6 | 219.8 | 233.9 | 235.6 | 388.1 | 19.2 | 21.3 | 47.8 | 7.4 | 264.8 | 11.9 | 309.7 | 871.3 | 810.3 | 356.9 | 737.8 | 216.1 | 568.4 | 816.1 | 319.2 | 692.3 | 95.5 | 232.8 | 240.6 | 148.3 | 83.1 | 239.4 | 222.7 | 139.2
345 | 200 | 469.4 | 187.76 | 219.4806 | 201.2 | 221.5 | 234.4 | 236.2 | 387.6 | 19.4 | 21.3 | 47.8 | 7.2 | 249.8 | 14 | 311.1 | 872.1 | 789 | 357.5 | 736.4 | 218.6 | 566.2 | 809.2 | 320 | 692 | 96 | 233.4 | 240.7 | 148.9 | 83.5 | 239.2 | 223 | 139.8
346 | 201 | 469.4 | 187.76 | 219.4806 | 204.2 | 221.9 | 233.3 | 235.7 | 391 | 19.5 | 21.3 | 47.9 | 6.1 | 246.6 | 15.1 | 312.6 | 869.7 | 794.9 | 358 | 739.5 | 220.8 | 564.8 | 811.1 | 320.6 | 692.7 | 96.5 | 234 | 240.8 | 149.6 | 83.9 | 239.3 | 223.4 | 140.4
347 | 202 | 470.6 | 188.24 | 220.0417 | 206 | 221.4 | 232.6 | 235.5 | 394.5 | 19.5 | 21.3 | 48 | 7 | 231.4 | 13.7 | 314.1 | 879.4 | 799.9 | 358.6 | 738.9 | 222.9 | 564.7 | 808.9 | 321.3 | 693.7 | 97 | 234.4 | 240.9 | 150.3 | 84.3 | 239.5 | 223.6 | 140.9
348 | 203 | 471.3 | 188.52 | 220.369 | 205.6 | 220.8 | 232.3 | 236.1 | 395.6 | 19.6 | 21.3 | 48.2 | 7.8 | 251.8 | 13.3 | 315.6 | 875.3 | 818.5 | 359.2 | 741.5 | 224.8 | 565.9 | 812.7 | 322.1 | 696 | 97.4 | 234.9 | 241 | 150.7 | 84.8 | 239.3 | 223.8 | 141.5
349 | 204 | 469.2 | 187.68 | 219.3871 | 202.9 | 219.7 | 232.9 | 236.4 | 398.2 | 19.7 | 21.3 | 48.3 | 7.3 | 232.4 | 13.9 | 317.3 | 878.7 | 810.4 | 359.6 | 741.8 | 226.6 | 567.9 | 815.9 | 323 | 698.6 | 97.9 | 235.9 | 241.5 | 151 | 85.2 | 239.6 | 223.9 | 142
350 | 205 | 469.8 | 187.92 | 219.6677 | 204.4 | 220 | 233 | 236.8 | 402.5 | 19.8 | 21.3 | 48.5 | 9 | 239.7 | 13.6 | 318.9 | 886.3 | 809 | 360.2 | 742.5 | 228.2 | 568.6 | 812.7 | 323.7 | 699.6 | 98.4 | 236.6 | 241.7 | 151.9 | 85.6 | 239.5 | 224.6 | 142.5
351 | 206 | 469.8 | 187.92 | 219.6677 | 204.5 | 219.5 | 234 | 237.6 | 402.2 | 19.9 | 21.3 | 48.7 | 7.8 | 233.6 | 11.6 | 320.5 | 884.6 | 801.6 | 360.8 | 741 | 229.8 | 569.5 | 813.4 | 324.3 | 701.4 | 98.9 | 237.4 | 242.4 | 153.4 | 86 | 239.9 | 225.1 | 143.1
352 | 207 | 470.8 | 188.32 | 220.1352 | 204.3 | 219.3 | 236 | 238.2 | 409.1 | 19.9 | 21.3 | 48.9 | 8.1 | 242 | 13.9 | 322 | 893.5 | 795.3 | 361.4 | 740.6 | 231.2 | 570.8 | 807.7 | 324.9 | 700.9 | 99.3 | 238.3 | 243 | 154.4 | 86.5 | 240.2 | 225 | 143.5
353 | 208 | 469.7 | 187.88 | 219.6209 | 205.4 | 219.7 | 237.8 | 238.6 | 418 | 20 | 21.3 | 49 | 5 | 207.8 | 15 | 323.4 | 896.3 | 797.1 | 362 | 740.3 | 232.6 | 571.6 | 806.4 | 325.4 | 702.5 | 99.8 | 238.9 | 244.3 | 155 | 86.9 | 241.1 | 225.2 | 143.8
354 | 209 | 469.5 | 187.8 | 219.5274 | 205.8 | 220.9 | 239 | 239.4 | 429.3 | 20.1 | 21.3 | 49.1 | 9.4 | 244.4 | 12.4 | 324.7 | 888.8 | 812.7 | 362.3 | 743 | 233.8 | 573.7 | 811.8 | 326.1 | 705 | 100.3 | 239.9 | 245.8 | 155.7 | 87.3 | 241.5 | 225.1 | 144.4
355 | 210 | 468.3 | 187.32 | 218.9663 | 205.5 | 222.1 | 240.8 | 240.6 | 432.2 | 20.2 | 21.3 | 49.3 | 10.5 | 207.3 | 11 | 326 | 878.6 | 823.4 | 362.6 | 745.9 | 235 | 574.7 | 816.4 | 326.9 | 707.3 | 100.8 | 240.5 | 246.9 | 156.2 | 87.7 | 241.9 | 225.5 | 144.9
356 | 211 | 467.5 | 187 | 218.5922 | 205.2 | 223.5 | 241.7 | 242.3 | 428.9 | 20.2 | 21.3 | 49.5 | 10.3 | 224.3 | 9.6 | 327.3 | 871.5 | 824.1 | 363.1 | 745.4 | 236.1 | 576 | 821 | 327.6 | 709.7 | 101.3 | 241.2 | 247.9 | 157.2 | 88.2 | 242.4 | 225.8 | 145.5
357 | 212 | 469.4 | 187.76 | 219.4806 | 205.7 | 224.4 | 242.6 | 243.4 | 430.4 | 20.3 | 21.3 | 49.6 | 7.4 | 231.5 | 8.6 | 328.7 | 868.8 | 821.4 | 363.5 | 745 | 237.2 | 576.2 | 817.8 | 328.3 | 709.6 | 101.7 | 241.9 | 248.8 | 157.8 | 88.6 | 242.9 | 226.2 | 146.1
358 | 213 | 469.7 | 187.88 | 219.6209 | 206.3 | 225 | 243.4 | 244.3 | 430.1 | 20.3 | 21.3 | 49.7 | 8.7 | 235.5 | 9.2 | 330 | 867.2 | 823 | 363.9 | 745.9 | 238.2 | 575.5 | 822.4 | 328.9 | 711.1 | 102.2 | 242.4 | 249.7 | 158.4 | 89 | 243.5 | 226.5 | 146.6
359 | 214 | 468.6 | 187.44 | 219.1066 | 205.8 | 225.5 | 243.7 | 245.1 | 428.5 | 20.3 | 21.3 | 49.7 | 8.5 | 238.2 | 13.7 | 331.3 | 859.6 | 823.1 | 364.4 | 746.1 | 239.3 | 577.8 | 825.9 | 329.7 | 713.4 | 102.7 | 242.8 | 250.6 | 159 | 89.4 | 243.7 | 226.7 | 147.3
360 | 215 | 468.9 | 187.56 | 219.2468 | 205.8 | 225.9 | 243.9 | 245.2 | 430.5 | 20.3 | 21.2 | 49.7 | 8.6 | 237 | 15.7 | 332.7 | 851.7 | 839 | 364.8 | 748.8 | 240.3 | 580.8 | 832.9 | 330.6 | 716.2 | 103.2 | 243.4 | 251.2 | 159.5 | 89.9 | 244.1 | 227.4 | 147.8
361 | 216 | 469.2 | 187.68 | 219.3871 | 204.8 | 225.9 | 244.1 | 245.9 | 430.2 | 20.4 | 21.2 | 49.7 | 7.8 | 230.6 | 15.2 | 334 | 848.5 | 834.3 | 365.2 | 749.7 | 241.4 | 582.6 | 830.2 | 331.4 | 719 | 103.6 | 244.1 | 251.1 | 160 | 90.3 | 244.4 | 228.2 | 148.3
362 | 217 | 467.4 | 186.96 | 218.5455 | 205.6 | 226.9 | 244.1 | 246.6 | 426.4 | 20.5 | 21.2 | 49.7 | 7.3 | 243.3 | 15.8 | 335.1 | 852.7 | 837.5 | 365.7 | 749.3 | 242.5 | 583 | 823.7 | 332.2 | 719.5 | 104.1 | 244.5 | 250.9 | 160.7 | 90.7 | 244.7 | 228.5 | 148.9
363 | 218 | 467.5 | 187 | 218.5922 | 206.8 | 227.7 | 244.4 | 246.7 | 429.6 | 20.5 | 21.2 | 49.7 | 7.2 | 237.6 | 18.8 | 336.4 | 864.1 | 824.2 | 366.2 | 747.7 | 243.6 | 585.4 | 825.8 | 333.1 | 719.6 | 104.6 | 244.9 | 250.9 | 161.5 | 91.1 | 245.1 | 228.9 | 149.5
364 | 219 | 468.7 | 187.48 | 219.1533 | 207.7 | 229.3 | 244.8 | 246.5 | 436.4 | 20.6 | 21.2 | 49.8 | 6.6 | 255.7 | 20.1 | 337.8 | 869.4 | 819.6 | 366.7 | 747.7 | 244.7 | 586.6 | 824.6 | 334 | 720.3 | 105.1 | 245.3 | 251.4 | 162.1 | 91.6 | 245.5 | 229.6 | 150.1
365 | 220 | 468.9 | 187.56 | 219.2468 | 208.8 | 230.5 | 245.8 | 247.2 | 437.8 | 20.7 | 21.2 | 49.8 | 5.9 | 248.2 | 16.4 | 339.2 | 862.3 | 819.2 | 367.2 | 749.3 | 245.9 | 585.8 | 825.1 | 334.9 | 721.1 | 105.6 | 246 | 251.6 | 162.4 | 92 | 245.8 | 230.3 | 150.7
366 | 221 | 468.2 | 187.28 | 218.9195 | 209.8 | 230.7 | 246.3 | 247.9 | 433 | 20.7 | 21.2 | 49.8 | 8.5 | 253.4 | 16.2 | 340.9 | 864.8 | 811.2 | 367.6 | 747.2 | 247.1 | 586.4 | 824.3 | 335.8 | 720.9 | 106.1 | 246.2 | 251.7 | 162.8 | 92.4 | 246.1 | 230.8 | 151.3
367 | 222 | 468.8 | 187.52 | 219.2001 | 209.5 | 231.5 | 246.1 | 248.8 | 434.3 | 20.9 | 21.2 | 50 | 8.8 | 249.5 | 16.2 | 342.3 | 861.7 | 797.7 | 368.2 | 748 | 248.4 | 585.9 | 816.2 | 336.5 | 720.1 | 106.6 | 246.5 | 251.8 | 163.4 | 92.9 | 246.2 | 231.4 | 151.8
368 | 223 | 468.9 | 187.56 | 219.2468 | 209.7 | 232.2 | 246.5 | 249.3 | 429.9 | 21.1 | 21.2 | 50.1 | 7.9 | 239.3 | 16.4 | 343.8 | 852.1 | 792.1 | 368.7 | 747.8 | 249.6 | 585.4 | 818.9 | 337.1 | 720.2 | 107.1 | 246.4 | 251.6 | 163.7 | 93.3 | 246.4 | 232.2 | 152.5
369 | 224 | 469.5 | 187.8 | 219.5274 | 211.3 | 231.7 | 246.4 | 249.4 | 423.5 | 21.1 | 21.2 | 50.1 | 5.6 | 257.3 | 13.9 | 345.2 | 846.2 | 802.9 | 369.2 | 748.7 | 250.9 | 585.4 | 820.7 | 337.9 | 721.4 | 107.6 | 246.3 | 252 | 164.2 | 93.7 | 246.6 | 232.9 | 152.9
370 | 225 | 469 | 187.6 | 219.2936 | 213.1 | 232.6 | 246.4 | 249.1 | 420.7 | 21.1 | 21.2 | 50.2 | 5.5 | 303.9 | 9.9 | 346.5 | 846.7 | 787.1 | 369.7 | 747 | 252.3 | 584.5 | 818.6 | 338.7 | 721.4 | 108.1 | 246.2 | 252.7 | 164.6 | 94.2 | 246.9 | 233.4 | 153.4
371 | 226 | 469.9 | 187.96 | 219.7144 | 217.5 | 232.3 | 246.8 | 248.5 | 413.8 | 21.2 | 21.2 | 50.3 | 4.1 | 270.9 | 6.6 | 347.8 | 857 | 775.5 | 370.4 | 745.8 | 253.7 | 581.6 | 807.2 | 339.4 | 719.3 | 108.6 | 246.2 | 253 | 165 | 94.6 | 246.9 | 233.5 | 154
372 | 227 | 470.4 | 188.16 | 219.9482 | 221 | 231.2 | 246.8 | 248.8 | 410.8 | 21.2 | 21.2 | 50.3 | 4.2 | 255.1 | 8.6 | 349.1 | 854.7 | 776.5 | 371 | 746 | 255 | 577.8 | 801.4 | 339.9 | 717.8 | 109.1 | 246.2 | 253.1 | 165.6 | 95.1 | 246.8 | 233.6 | 154.5
373 | 228 | 469.7 | 187.88 | 219.6209 | 222.4 | 230.9 | 247.4 | 248.9 | 407.4 | 21.2 | 21.2 | 50.3 | 5 | 245.7 | 10.2 | 350.3 | 855.6 | 780.4 | 371.6 | 745.9 | 256.4 | 574.8 | 799.5 | 340.5 | 717.3 | 109.5 | 246.6 | 253.2 | 166.1 | 95.6 | 246.8 | 233.7 | 155
374 | 229 | 469.4 | 187.76 | 219.4806 | 224.8 | 230.4 | 247 | 247.8 | 404.3 | 21.2 | 21.2 | 50.4 | 5.7 | 261.5 | 10.9 | 351.7 | 850.9 | 771.1 | 372.1 | 745 | 257.9 | 573.9 | 795.8 | 341.1 | 716.4 | 110 | 246.9 | 253.2 | 166.7 | 96.1 | 247.4 | 233.9 | 155.5
375 | 230 | 469.6 | 187.84 | 219.5741 | 225.2 | 230.4 | 246.4 | 246.8 | 403.3 | 21.2 | 21.2 | 50.6 | 5.2 | 267.4 | 10.5 | 353 | 849.7 | 786.9 | 372.5 | 747.4 | 259.3 | 573.1 | 802.8 | 341.8 | 717.6 | 110.5 | 247.4 | 253.9 | 167.8 | 96.6 | 247.5 | 234.1 | 156.1
376 | 231 | 469.6 | 187.84 | 219.5741 | 224.4 | 231.3 | 247.1 | 246.3 | 406.8 | 21.3 | 21.2 | 50.8 | 5 | 264.6 | 9.4 | 354.4 | 846.7 | 799 | 373 | 748.4 | 260.8 | 577.8 | 817.7 | 342.8 | 721.1 | 111 | 247.5 | 253.7 | 168.7 | 97 | 248 | 234.3 | 156.7
377 | 232 | 469.2 | 187.68 | 219.3871 | 222.5 | 231.9 | 246.1 | 244.9 | 410.3 | 21.5 | 21.2 | 50.8 | 4.4 | 286.3 | 12 | 355.8 | 843.5 | 799.8 | 373.5 | 747.9 | 262.4 | 581.2 | 827.7 | 343.9 | 723.1 | 111.5 | 247.6 | 253.7 | 169.2 | 97.5 | 248.4 | 234.4 | 157.2
378 | 233 | 469.1 | 187.64 | 219.3403 | 221.5 | 232.6 | 245.1 | 244.7 | 418 | 21.7 | 21.2 | 50.9 | 5.3 | 267.5 | 14.1 | 357.5 | 842.9 | 810.4 | 374 | 749.8 | 263.9 | 584.3 | 833.9 | 345 | 724.7 | 112 | 247.7 | 253.9 | 169.4 | 98 | 248.3 | 234.6 | 157.7
379 | 234 | 469.3 | 187.72 | 219.4339 | 222 | 232.8 | 246.2 | 245.4 | 419.4 | 21.8 | 21.2 | 51.1 | 4.9 | 265.2 | 14.6 | 359.3 | 837.8 | 825.2 | 374.5 | 751.5 | 265.5 | 589 | 842.1 | 346.2 | 727.4 | 112.5 | 248 | 254.5 | 169.9 | 98.5 | 248.3 | 234.5 | 158.2
380 | 235 | 469.4 | 187.76 | 219.4806 | 222.7 | 232.5 | 247.1 | 246.4 | 420.8 | 21.9 | 21.2 | 51.2 | 4.7 | 245.6 | 14 | 361.1 | 837.9 | 837.1 | 375 | 754.5 | 267 | 593.4 | 844.6 | 347.4 | 729.6 | 112.9 | 248.8 | 254.8 | 170.3 | 99 | 248.6 | 234.8 | 158.8
381 | 236 | 469.9 | 187.96 | 219.7144 | 223.2 | 231.8 | 247.9 | 246.5 | 419.5 | 22 | 21.2 | 51.4 | 5.6 | 262.6 | 14.4 | 362.8 | 836.7 | 837.3 | 375.5 | 755.5 | 268.6 | 595.2 | 845.7 | 348.4 | 730.8 | 113.4 | 249 | 255.4 | 171 | 99.4 | 248.8 | 235.4 | 159.3
382 | 237 | 469.5 | 187.8 | 219.5274 | 222.2 | 231.5 | 248 | 246.6 | 419.7 | 22.2 | 21.2 | 51.5 | 5.3 | 257.7 | 14.4 | 364.4 | 842.4 | 833.8 | 376.1 | 756.2 | 270.1 | 597 | 843.2 | 349.3 | 731.1 | 113.9 | 249.2 | 255.7 | 171.9 | 99.9 | 249.2 | 235.8 | 160
383 | 238 | 470 | 188 | 219.7612 | 221.7 | 232.2 | 248.1 | 247.3 | 424.3 | 22.4 | 21.2 | 51.6 | 4.8 | 269.5 | 12.6 | 365.7 | 845.5 | 839.6 | 376.8 | 757.2 | 271.7 | 599.7 | 847.6 | 350.4 | 733.4 | 114.4 | 249.4 | 256.2 | 172.5 | 100.4 | 249.5 | 236 | 160.5
384 | 239 | 469.7 | 187.88 | 219.6209 | 222 | 233 | 248 | 247.2 | 424.7 | 22.5 | 21.2 | 51.6 | 4.5 | 276.8 | 11.2 | 367.1 | 848.9 | 835.1 | 377.4 | 758.4 | 273.3 | 601.5 | 850 | 351.6 | 734.9 | 114.8 | 249.5 | 256.5 | 173.1 | 100.9 | 249.7 | 236.4 | 160.9
385 | 240 | 470.2 | 188.08 | 219.8547 | 220.6 | 233.3 | 248.1 | 247.5 | 429.9 | 22.6 | 21.2 | 51.6 | 3.9 | 287.2 | 10.3 | 368.5 | 847 | 828.7 | 378 | 758.9 | 274.9 | 600.8 | 846.5 | 352.8 | 735.6 | 115.3 | 249.6 | 257.1 | 173.7 | 101.3 | 250 | 236.6 | 161.3
386 | 241 | 470.8 | 188.32 | 220.1352 | 220.7 | 232.6 | 248 | 247.7 | 427.1 | 22.7 | 21.2 | 51.6 | 3.5 | 286.2 | 11.8 | 369.8 | 841.7 | 818.5 | 378.7 | 758.3 | 276.6 | 597.8 | 831.8 | 353.9 | 734.3 | 115.8 | 249.8 | 257.4 | 174.1 | 101.8 | 250.5 | 237 | 161.8
387 | 242 | 470.7 | 188.28 | 220.0885 | 221.2 | 232.9 | 248.3 | 248.5 | 422.2 | 22.8 | 21.2 | 51.6 | 3.4 | 287.5 | 11.5 | 370.9 | 839.6 | 785 | 379.7 | 755.2 | 278.1 | 593.6 | 812.6 | 354.6 | 731.9 | 116.2 | 249.9 | 257.6 | 174.3 | 102.3 | 251.1 | 237.1 | 162.4
388 | 243 | 470.1 | 188.04 | 219.8079 | 224.8 | 233 | 249 | 249.1 | 416 | 23 | 21.2 | 51.6 | 4.4 | 292.8 | 10.6 | 372.2 | 840.1 | 784 | 380.7 | 755.8 | 279.6 | 587.2 | 801.5 | 355.2 | 730.3 | 116.7 | 249.9 | 257.5 | 174.5 | 102.7 | 251.5 | 237.2 | 162.8
389 | 244 | 470.5 | 188.2 | 219.995 | 228.2 | 232.8 | 248.8 | 249.2 | 408.6 | 23.1 | 21.2 | 51.7 | 5.1 | 285.4 | 9 | 373.6 | 839.5 | 784.8 | 381.5 | 755.4 | 281.2 | 583.7 | 800.1 | 355.8 | 729.6 | 117.1 | 250.9 | 257.4 | 175.4 | 103.2 | 251.5 | 237.3 | 163.3
390 | 245 | 468.9 | 187.56 | 219.2468 | 229.2 | 233.2 | 247.9 | 249.3 | 410.5 | 23.3 | 21.2 | 52 | 4.6 | 278.6 | 8.9 | 375.1 | 846.7 | 769.9 | 382.4 | 753 | 282.8 | 581.4 | 795.2 | 356.5 | 728 | 117.6 | 251.6 | 257.5 | 176.5 | 103.7 | 251.9 | 237.2 | 163.7
391 | 246 | 468.1 | 187.24 | 218.8728 | 228.1 | 234.4 | 247.4 | 249.3 | 415.1 | 23.4 | 21.2 | 52.2 | 3.6 | 269.6 | 7.8 | 376.5 | 845.4 | 760.1 | 383.2 | 752.3 | 284.4 | 580.5 | 793 | 357.3 | 727.5 | 118.1 | 251.9 | 257.7 | 177.3 | 104.2 | 252.6 | 237.4 | 164.1
392 | 247 | 469.3 | 187.72 | 219.4339 | 225 | 234.4 | 248.3 | 250.1 | 412.9 | 23.4 | 21.1 | 52.4 | 5.5 | 254.5 | 7.3 | 378.3 | 837.3 | 755.6 | 384 | 750.8 | 285.9 | 576.6 | 778.8 | 357.9 | 726.2 | 118.5 | 252.2 | 257.7 | 177.6 | 104.6 | 252.9 | 237.5 | 164.6
393 | 248 | 471.4 | 188.56 | 220.4158 | 222.1 | 233.5 | 248.8 | 251.1 | 407 | 23.4 | 21.1 | 52.7 | 7.7 | 250.3 | 6.6 | 380.1 | 834.7 | 756.4 | 384.9 | 749.7 | 287.5 | 574.8 | 778.8 | 358.6 | 725.2 | 119 | 252.2 | 257.7 | 178.1 | 105.1 | 253.1 | 237.7 | 165
394 | 249 | 469.3 | 187.72 | 219.4339 | 220.7 | 233.6 | 247.7 | 251.3 | 405.6 | 23.6 | 21.1 | 53 | 6.8 | 292.3 | 6.4 | 381.7 | 838.8 | 735.9 | 386.2 | 748.4 | 288.9 | 570.9 | 770.5 | 359.1 | 723 | 119.4 | 252.5 | 258.1 | 179 | 105.6 | 252.8 | 238 | 165.6
395 | 250 | 469.3 | 187.72 | 219.4339 | 220 | 233.5 | 247.6 | 251.5 | 402.4 | 23.7 | 21.1 | 53.3 | 7.5 | 293.6 | 7.2 | 383.4 | 832.5 | 730.7 | 387.5 | 748.1 | 290.3 | 568.5 | 769.3 | 359.6 | 722.3 | 119.9 | 252.6 | 258.4 | 179.9 | 106.1 | 252.4 | 238.2 | 166.1
396 | 251 | 469.5 | 187.8 | 219.5274 | 219.2 | 233.9 | 248.1 | 250.5 | 399.5 | 23.9 | 21.1 | 53.5 | 7.2 | 293.4 | 10.4 | 385.2 | 829.7 | 741.2 | 388.8 | 748.6 | 291.7 | 566 | 767.1 | 360.1 | 720.9 | 120.3 | 252.6 | 258.6 | 180 | 106.6 | 252.1 | 238.8 | 166.6
397 | 252 | 470 | 188 | 219.7612 | 217.5 | 234.2 | 248.2 | 249.2 | 397.6 | 23.9 | 21.1 | 53.8 | 7.1 | 292.5 | 12.3 | 387.1 | 829.8 | 742.6 | 390.3 | 748.6 | 293.2 | 565.5 | 773 | 360.7 | 721 | 120.8 | 252.4 | 258.4 | 180.7 | 107.1 | 251.9 | 239.1 | 167.1
398 | 253 | 469.7 | 187.88 | 219.6209 | 216.9 | 233.8 | 247.7 | 247.9 | 397.5 | 23.9 | 21.1 | 54.2 | 5.3 | 289.6 | 11.9 | 389.1 | 828.5 | 728.5 | 391.8 | 746.6 | 294.7 | 566.3 | 781.9 | 361.5 | 720.6 | 121.2 | 252.8 | 258.4 | 181.2 | 107.5 | 251.7 | 239.1 | 167.6
399 | 254 | 469.2 | 187.68 | 219.3871 | 219.4 | 232.8 | 246.7 | 246.7 | 399.5 | 23.9 | 21.1 | 54.5 | 4.7 | 297.8 | 11 | 391.3 | 830.6 | 720.9 | 393.1 | 745.2 | 296.2 | 566 | 781.1 | 362.2 | 719.4 | 121.7 | 253.3 | 258.7 | 181.8 | 108 | 251.4 | 239 | 167.9
400 | 255 | 470.2 | 188.08 | 219.8547 | 220.5 | 232.3 | 246.3 | 245.1 | 398.8 | 23.9 | 21.1 | 54.7 | 5.4 | 291.5 | 11.1 | 393.2 | 834.1 | 713.1 | 394.4 | 743 | 297.7 | 565.6 | 780.3 | 363.1 | 719.4 | 122.2 | 253.8 | 258.7 | 182.2 | 108.5 | 251.4 | 238.7 | 168.3
401 | 256 | 470.5 | 188.2 | 219.995 | 220.1 | 232.1 | 245.7 | 244.2 | 395.7 | 24 | 21.1 | 54.9 | 5 | 276.9 | 9.8 | 395.3 | 830.6 | 699.6 | 395.7 | 741.2 | 299.2 | 564.4 | 774.4 | 363.8 | 717.4 | 122.6 | 254.2 | 258.7 | 183 | 109 | 251.3 | 238.6 | 168.8
402 | 257 | 470.7 | 188.28 | 220.0885 | 220.9 | 232 | 245.2 | 243.7 | 396.3 | 24.1 | 21.1 | 55.1 | 5.7 | 297.3 | 9.2 | 397.3 | 835.5 | 692.9 | 396.5 | 738.3 | 300.5 | 562.9 | 767.5 | 364.4 | 714.4 | 123 | 255.1 | 259.4 | 184.2 | 109.5 | 251.4 | 238.6 | 169.2
403 | 258 | 470.4 | 188.16 | 219.9482 | 220.2 | 232.8 | 245.4 | 244.1 | 400.1 | 24.2 | 21.1 | 55.3 | 5.5 | 298.1 | 11.1 | 399.5 | 835.5 | 717.1 | 397.2 | 738.1 | 301.7 | 564.5 | 779.7 | 365 | 714.8 | 123.5 | 255.6 | 259.4 | 184.9 | 110 | 251.6 | 238.7 | 169.6
404 | 259 | 470 | 188 | 219.7612 | 217.3 | 233.7 | 245.6 | 245 | 406.9 | 24.3 | 21.1 | 55.5 | 5.2 | 287.2 | 15.6 | 401.6 | 836.1 | 732.6 | 398.1 | 738.9 | 303 | 567.6 | 788.7 | 365.9 | 716.9 | 123.9 | 255.7 | 259.2 | 185.2 | 110.5 | 252.2 | 239.1 | 170.1
405 | 260 | 467.5 | 187 | 218.5922 | 214.3 | 234.2 | 246.1 | 245 | 411.5 | 24.3 | 21.1 | 55.6 | 4.5 | 297.7 | 18.8 | 403.9 | 836.7 | 734.8 | 399.2 | 737 | 304.2 | 567.5 | 789 | 367 | 716.1 | 124.4 | 255.9 | 259.6 | 185.7 | 111 | 252.7 | 239.6 | 170.5
406 | 261 | 466.9 | 186.76 | 218.3117 | 211.1 | 234.3 | 247.1 | 244.9 | 413.6 | 24.3 | 21.1 | 55.7 | 4.7 | 292.6 | 17.2 | 406.1 | 838 | 748 | 400.5 | 736.1 | 305.3 | 569.5 | 798.1 | 368 | 716 | 124.9 | 256.3 | 260 | 186.4 | 111.5 | 253.1 | 240 | 171.1
407 | 262 | 468.5 | 187.4 | 219.0598 | 209.1 | 234.6 | 247.9 | 245.4 | 421 | 24.3 | 21.1 | 55.8 | 3.4 | 289.5 | 13.2 | 408.4 | 836.1 | 750.2 | 402.4 | 735.1 | 306.3 | 571.3 | 800.1 | 369.3 | 717.9 | 125.3 | 256.7 | 260.3 | 186.9 | 112 | 254.2 | 240.3 | 171.6
408 | 263 | 469.1 | 187.64 | 219.3403 | 209.3 | 234.6 | 248.2 | 246.6 | 422.2 | 24.5 | 21.1 | 55.8 | 3.4 | 310 | 13 | 410.8 | 830.3 | 744.6 | 403.8 | 734.8 | 307.2 | 572.1 | 806 | 370.6 | 718.1 | 125.7 | 257.2 | 260.6 | 187.6 | 112.4 | 255.2 | 240.6 | 172
409 | 264 | 472.5 | 189 | 220.9301 | 209.5 | 234.8 | 247.2 | 247.5 | 421.4 | 24.6 | 21.1 | 55.9 | 3.4 | 286.7 | 12.4 | 413.5 | 823.4 | 734.7 | 405.4 | 733.6 | 308 | 570.8 | 797.3 | 371.7 | 716.2 | 126.2 | 257.7 | 260.9 | 188.4 | 112.9 | 255.7 | 240.7 | 172.6
410 | 265 | 472.3 | 188.92 | 220.8366 | 209.3 | 235.1 | 247.8 | 249.2 | 419.3 | 24.7 | 21.1 | 56 | 4 | 291.9 | 13.9 | 416.6 | 815.7 | 730.5 | 406.8 | 733.5 | 308.6 | 570.4 | 797.9 | 372.6 | 715.8 | 126.7 | 257.8 | 260.9 | 189.1 | 113.4 | 256.2 | 240.9 | 173
411 | 266 | 470.3 | 188.12 | 219.9014 | 209.9 | 235 | 248.3 | 250.2 | 415.8 | 24.8 | 21.1 | 56 | 4.1 | 286.6 | 14.9 | 419.1 | 815 | 739.9 | 408.3 | 734.6 | 309.3 | 570.2 | 792.5 | 373.6 | 715.7 | 127.1 | 257.5 | 260.6 | 189.2 | 113.9 | 256.5 | 241 | 173.5
412 | 267 | 468.6 | 187.44 | 219.1066 | 212.8 | 235.4 | 247.3 | 250.6 | 411.3 | 24.9 | 21.1 | 56.1 | 4.8 | 285.5 | 15.5 | 421.5 | 809.8 | 769.9 | 409.8 | 736.8 | 310 | 571.3 | 797.1 | 374.7 | 717.5 | 127.6 | 257.2 | 260.6 | 189.2 | 114.5 | 256.6 | 241.1 | 173.9
413 | 268 | 468.6 | 187.44 | 219.1066 | 213.2 | 235.7 | 247.1 | 250.5 | 413.2 | 24.9 | 21.1 | 56.2 | 5.5 | 279.6 | 16.1 | 423.7 | 811.3 | 774.1 | 411.3 | 737.5 | 310.7 | 573.3 | 808.3 | 376 | 720.2 | 128 | 257.2 | 260.5 | 189.6 | 115 | 256.8 | 241.3 | 174.4
414 | 269 | 470 | 188 | 219.7612 | 212.5 | 236 | 247.1 | 250.8 | 415.8 | 25 | 21.1 | 56.4 | 6 | 285.7 | 13.8 | 426.3 | 817.4 | 765.4 | 413.1 | 734.2 | 311.4 | 575.2 | 816.5 | 377.3 | 720.9 | 128.5 | 257.9 | 261 | 190.6 | 115.5 | 256.8 | 241.6 | 174.9
415 | 270 | 470.6 | 188.24 | 220.0417 | 213.3 | 235.8 | 247.7 | 251.5 | 416.2 | 25 | 21.1 | 56.5 | 5.5 | 261.8 | 11.3 | 428.7 | 815.1 | 781.4 | 415.3 | 734.8 | 312.1 | 575.7 | 818.4 | 378.4 | 720.6 | 128.9 | 258.6 | 261.4 | 191.9 | 116 | 257 | 241.9 | 175.4
416 | 271 | 470 | 188 | 219.7612 | 214.2 | 235.8 | 248.9 | 252.2 | 415 | 25.2 | 21.1 | 56.6 | 5.6 | 271.7 | 11 | 431.5 | 808.5 | 779.5 | 417.7 | 736.8 | 312.8 | 577.6 | 817.8 | 379.5 | 721.3 | 129.4 | 259.2 | 261.9 | 192.5 | 116.5 | 257.1 | 242.3 | 175.8
417 | 272 | 470.2 | 188.08 | 219.8547 | 215.7 | 236 | 249.7 | 252.7 | 410.5 | 25.4 | 21.1 | 56.7 | 6.5 | 256.4 | 10.6 | 434.2 | 801 | 774.7 | 420.3 | 735.9 | 313.6 | 576.8 | 813.7 | 380.5 | 720.9 | 129.9 | 260.2 | 262.3 | 193.3 | 117 | 257.1 | 242.6 | 176.4
418 | 273 | 470.7 | 188.28 | 220.0885 | 215.5 | 236.2 | 250.3 | 252.8 | 408.9 | 25.5 | 21.1 | 56.8 | 6.9 | 266.8 | 12.5 | 436.6 | 724.5 | 768.2 | 422.9 | 734.6 | 314.5 | 575.9 | 805.6 | 381 | 720.4 | 130.3 | 260.8 | 262.6 | 194 | 117.5 | 257.7 | 242.9 | 176.8
419 | 274 | 470.1 | 188.04 | 219.8079 | 216.5 | 236.5 | 251.4 | 252.9 | 411.2 | 25.6 | 21.1 | 56.9 | 5.7 | 278.1 | 13.3 | 439.4 | 559.8 | 761 | 425.3 | 734.3 | 315.3 | 573.9 | 790.5 | 381.1 | 718.4 | 130.8 | 261.7 | 263.1 | 194.5 | 118.1 | 258 | 242.9 | 177.2
420 | 275 | 470.2 | 188.08 | 219.8547 | 216.8 | 236.8 | 252.6 | 251.6 | 413.8 | 25.7 | 21.1 | 56.9 | 4.8 | 290.5 | 14.1 | 441.8 | 763.2 | 765.8 | 428 | 735.5 | 316.2 | 574.3 | 784.1 | 381.1 | 717.7 | 131.2 | 262.5 | 263.8 | 195 | 118.6 | 258 | 242.9 | 177.7
421 | 276 | 470.5 | 188.2 | 219.995 | 217.5 | 237.2 | 254 | 250.3 | 413.8 | 25.8 | 21 | 56.9 | 5.5 | 286.9 | 13.3 | 444.6 | 794.4 | 774.4 | 430.7 | 736 | 317.2 | 575.3 | 795.4 | 381.3 | 718.3 | 131.7 | 262.7 | 264.1 | 195.4 | 119.1 | 258.7 | 242.9 | 178.1
422 | 277 | 469.4 | 187.76 | 219.4806 | 218.3 | 238 | 254.4 | 249.9 | 413.4 | 25.8 | 21 | 57 | 4.6 | 281.3 | 12.3 | 447.1 | 789.7 | 780.1 | 433.4 | 738.7 | 318.3 | 579.6 | 804.8 | 381.7 | 719.5 | 132.2 | 262.9 | 264.5 | 195.9 | 119.6 | 259 | 243 | 178.5
423 | 278 | 468.9 | 187.56 | 219.2468 | 217.5 | 238.3 | 254.7 | 249.9 | 413.9 | 25.9 | 21 | 57 | 4.6 | 284.4 | 15.4 | 449.7 | 785.6 | 782.2 | 436.1 | 737.9 | 319.4 | 581.6 | 804.4 | 382.3 | 719.3 | 132.6 | 263 | 264.8 | 196.1 | 120.1 | 259.2 | 243 | 178.9
424 | 279 | 468.8 | 187.52 | 219.2001 | 215.8 | 238.4 | 254.7 | 250.8 | 417.3 | 26 | 21 | 57.1 | 5.1 | 270 | 15.2 | 452.1 | 788.9 | 781.7 | 438.8 | 738.8 | 320.6 | 582.2 | 794.2 | 382.7 | 719.5 | 133.1 | 263.2 | 265.2 | 196.5 | 120.6 | 259.3 | 243 | 179.3
425 | 280 | 469.7 | 187.88 | 219.6209 | 214.8 | 239.5 | 255.7 | 251.9 | 419.5 | 26.1 | 21 | 57.3 | 5.8 | 249.7 | 14.5 | 454.3 | 789.8 | 783.9 | 441.3 | 739.5 | 321.7 | 584.6 | 797 | 383.3 | 720.8 | 133.6 | 263.3 | 265.5 | 197.1 | 121.1 | 259.7 | 243.1 | 179.7
426 | 281 | 469 | 187.6 | 219.2936 | 215.1 | 240.4 | 257 | 252.8 | 423 | 26.2 | 21 | 57.5 | 5.7 | 273.5 | 15.6 | 456.2 | 785.7 | 771.7 | 443.9 | 737.9 | 322.9 | 585 | 800.2 | 383.7 | 721.9 | 134 | 263.4 | 265.9 | 197.7 | 121.6 | 260.3 | 243.3 | 180.1
427 | 282 | 469.6 | 187.84 | 219.5741 | 216.1 | 240.3 | 256.6 | 253.4 | 422.7 | 26.2 | 21 | 57.6 | 5.7 | 275.6 | 16.8 | 458.1 | 783.8 | 785.4 | 446.5 | 740 | 324.1 | 584.8 | 805.6 | 384 | 722.9 | 134.5 | 263.5 | 266.1 | 197.8 | 122.1 | 260.6 | 243.5 | 180.6
428 | 283 | 470 | 188 | 219.7612 | 216.1 | 240.3 | 256.2 | 254.2 | 420.1 | 26.2 | 21 | 57.7 | 6.1 | 270.4 | 14.5 | 459.9 | 783.2 | 789.6 | 449.3 | 740.4 | 325.3 | 585.7 | 815 | 384.3 | 723.3 | 135 | 264 | 266.7 | 198.1 | 122.7 | 261.3 | 244 | 181.1
429 | 284 | 469.9 | 187.96 | 219.7144 | 216.8 | 240.8 | 254.7 | 255 | 419 | 26.1 | 21 | 57.9 | 7 | 270.3 | 15 | 461.3 | 780.9 | 802.6 | 452.3 | 743.2 | 326.5 | 587.6 | 820.4 | 384.6 | 724.6 | 135.4 | 264.5 | 267.2 | 198.7 | 123.2 | 261.8 | 244.4 | 181.6
430 | 285 | 469.2 | 187.68 | 219.3871 | 217.5 | 241.1 | 254 | 256.1 | 421.5 | 26 | 21 | 58 | 8.1 | 241.9 | 14 | 462.6 | 778.4 | 806.2 | 455.2 | 743.3 | 327.7 | 590.6 | 827.2 | 385 | 727.1 | 135.9 | 265.2 | 267.4 | 199.3 | 123.7 | 261.8 | 244.8 | 182.1
431 | 286 | 468.6 | 187.44 | 219.1066 | 216.8 | 240.8 | 254.4 | 256.6 | 423.4 | 25.9 | 21 | 58.1 | 7.2 | 253.3 | 11.3 | 464 | 779.9 | 807.6 | 458.1 | 745.6 | 328.9 | 591.5 | 826.4 | 385.4 | 728.6 | 136.4 | 265.6 | 267.6 | 199.6 | 124.2 | 261.6 | 245 | 182.5
432 | 287 | 469.5 | 187.8 | 219.5274 | 216.9 | 240.9 | 255.7 | 257.1 | 422 | 25.8 | 21 | 58 | 6.8 | 246 | 10.4 | 465.5 | 780.9 | 809.4 | 461 | 746.8 | 330.2 | 590.2 | 823 | 385.9 | 728.5 | 136.8 | 265.9 | 268 | 200.2 | 124.8 | 261.4 | 245.3 | 183
433 | 288 | 470.9 | 188.36 | 220.182 | 220.4 | 241.4 | 256 | 256.6 | 420.3 | 25.8 | 21 | 58 | 7.3 | 258.7 | 10.4 | 467.1 | 781 | 810.9 | 463.6 | 746.9 | 331.4 | 591.1 | 826.1 | 386.3 | 729.7 | 137.3 | 265.9 | 268.1 | 200.8 | 125.3 | 261.4 | 245.6 | 183.4
434 | 289 | 471 | 188.4 | 220.2287 | 220.9 | 242.4 | 254.7 | 257.1 | 427.6 | 25.8 | 21 | 58.1 | 7.9 | 258.8 | 10.4 | 468.7 | 785.7 | 788.5 | 466.2 | 742.4 | 332.6 | 593.2 | 834.8 | 386.6 | 730.9 | 137.7 | 266.1 | 268.8 | 201.3 | 125.8 | 261.5 | 245.7 | 183.7
435 | 290 | 469.2 | 187.68 | 219.3871 | 220.9 | 243.9 | 255.1 | 257.6 | 433.7 | 25.7 | 21 | 58.2 | 10.6 | 269.5 | 10.9 | 470.5 | 784.8 | 779.8 | 468.8 | 741.5 | 333.9 | 594.5 | 836.9 | 387 | 731.8 | 138.2 | 266.9 | 269.5 | 202.1 | 126.4 | 262.1 | 245.8 | 184.1
436 | 291 | 470.3 | 188.12 | 219.9014 | 220.8 | 244.4 | 255.6 | 258 | 433.7 | 25.7 | 21 | 58.4 | 14.6 | 270.8 | 10.9 | 472.3 | 780.9 | 792.5 | 471.2 | 743.4 | 335.1 | 595.6 | 840.5 | 387.3 | 732.4 | 138.7 | 267.2 | 270.1 | 202.8 | 126.9 | 262.7 | 246.1 | 184.6
437 | 292 | 470.2 | 188.08 | 219.8547 | 224.4 | 244.2 | 255.5 | 258.3 | 431.7 | 25.7 | 21 | 58.5 | 14.1 | 266.4 | 10.2 | 474.4 | 777.4 | 795 | 473.6 | 745.2 | 336.3 | 596.5 | 842.6 | 387.2 | 733.3 | 139.2 | 267.7 | 270.4 | 203.2 | 127.5 | 263.2 | 246.3 | 185.1
438 | 293 | 469.9 | 187.96 | 219.7144 | 227.5 | 244.7 | 254.7 | 258.6 | 431.4 | 25.8 | 21 | 58.5 | 12.8 | 278 | 9.4 | 476.4 | 775.7 | 800.6 | 476 | 747.4 | 337.5 | 599.6 | 840.6 | 388.2 | 735.4 | 139.6 | 268 | 271.3 | 203.6 | 128 | 263.2 | 246.9 | 185.6
439 | 294 | 470.7 | 188.28 | 220.0885 | 228.3 | 244.5 | 254 | 258.8 | 427.4 | 26 | 21 | 58.6 | 12.2 | 302.9 | 9.5 | 478.3 | 773.2 | 811.3 | 478.2 | 750.2 | 338.7 | 603.2 | 843.4 | 391 | 736.9 | 140.1 | 268.3 | 271.9 | 204 | 128.6 | 263.2 | 247.8 | 186.1
440 | 295 | 470.6 | 188.24 | 220.0417 | 230 | 244.1 | 252.9 | 258.9 | 426.8 | 26.1 | 21 | 58.7 | 11.2 | 256.2 | 12.9 | 480.1 | 774.5 | 807.8 | 480.5 | 752.4 | 339.8 | 605.1 | 846.5 | 394.3 | 738.9 | 140.6 | 268.6 | 272.1 | 204.5 | 129.1 | 263.5 | 248.5 | 186.6
441 | 296 | 469.9 | 187.96 | 219.7144 | 232.5 | 243.9 | 252.6 | 258.9 | 424.8 | 26.1 | 21 | 58.8 | 8.9 | 251.7 | 13.3 | 482.1 | 776.4 | 813.8 | 483.4 | 752.3 | 341.1 | 605.1 | 852 | 397.7 | 739.3 | 141 | 268.9 | 272.5 | 205.1 | 129.7 | 263.6 | 249.1 | 187.2
442 | 297 | 470.7 | 188.28 | 220.0885 | 232.8 | 243.4 | 252.9 | 259.5 | 428.6 | 26.1 | 21 | 58.9 | 8.1 | 280.3 | 10.3 | 484.2 | 778.2 | 803.6 | 486.3 | 752.9 | 342.4 | 605.5 | 849.5 | 400.5 | 739.9 | 141.5 | 269.2 | 272.8 | 206 | 130.3 | 263.5 | 249.9 | 187.7
443 | 298 | 469.8 | 187.92 | 219.6677 | 232.5 | 242.7 | 254.3 | 259.7 | 429.6 | 26.2 | 21 | 58.9 | 6.7 | 278.8 | 10.8 | 486.6 | 776.7 | 796.2 | 488.3 | 751.3 | 343.8 | 607.8 | 847.3 | 403.1 | 738.8 | 142 | 269.4 | 272.9 | 206.2 | 130.8 | 263.3 | 250.2 | 188.2
444 | 299 | 470.1 | 188.04 | 219.8079 | 233.3 | 242.9 | 255.3 | 259 | 427.3 | 26.2 | 21 | 58.9 | 7.2 | 258.1 | 12.4 | 488.9 | 774.7 | 784.5 | 490.1 | 752.2 | 344.8 | 606.7 | 837 | 405.6 | 738.6 | 142.5 | 269.4 | 273.1 | 206.4 | 131.4 | 263.4 | 250.2 | 188.6
445 | 300 | 469.8 | 187.92 | 219.6677 | 233.4 | 242.6 | 255.4 | 257.6 | 424.4 | 26.2 | 21 | 58.9 | 4.7 | 246.9 | 12.8 | 491.4 | 773.5 | 774.4 | 491.7 | 751.9 | 345.8 | 607.1 | 823 | 407.6 | 738.1 | 143 | 269.3 | 273.2 | 206.6 | 132 | 263.4 | 250.6 | 189.1
446 | 301 | 469.8 | 187.92 | 219.6677 | 236.6 | 241.9 | 255.9 | 256.7 | 422 | 26.2 | 21 | 58.8 | 4.2 | 249.9 | 13.7 | 493.5 | 774.2 | 785.3 | 493.4 | 753.8 | 346.6 | 608.2 | 824.7 | 410.8 | 738.8 | 143.4 | 269.2 | 273.5 | 206.7 | 132.6 | 263.7 | 251 | 189.6
447 | 302 | 469.7 | 187.88 | 219.6209 | 235 | 241 | 256.9 | 255.7 | 421.9 | 26.2 | 21 | 58.7 | 4.4 | 251.3 | 15.1 | 495.3 | 777.9 | 790.6 | 495.5 | 758.4 | 347.4 | 609.8 | 819.2 | 414.2 | 740.8 | 143.9 | 269.2 | 273.8 | 207.3 | 133.2 | 264.3 | 251.7 | 190.1
448 | 303 | 469.9 | 187.96 | 219.7144 | 235.1 | 240.2 | 257 | 256.7 | 422.8 | 26.1 | 21 | 58.8 | 4.2 | 246.1 | 14.2 | 497 | 777 | 791.8 | 497.6 | 759.6 | 348 | 610.8 | 823.8 | 418.6 | 743.1 | 144.4 | 269.1 | 273.9 | 207.8 | 133.8 | 264.8 | 252.9 | 190.8
449 | 304 | 470 | 188 | 219.7612 | 235.4 | 240.2 | 256.5 | 257.2 | 422.7 | 26.2 | 21 | 58.9 | 3.8 | 243.3 | 13.2 | 498.8 | 784.8 | 792.5 | 500.2 | 761.2 | 348.5 | 611.5 | 825.1 | 423.5 | 743.6 | 144.8 | 269 | 274.2 | 208 | 134.4 | 265.8 | 253.8 | 191.2
450 | 305 | 469.6 | 187.84 | 219.5741 | 233.7 | 241.1 | 256.8 | 257.3 | 426.2 | 26.4 | 21 | 58.9 | 4.2 | 253.3 | 13.6 | 500.5 | 789.4 | 790.2 | 503.2 | 763.9 | 349 | 611.5 | 830 | 428.3 | 745.6 | 145.3 | 269 | 274.4 | 208.2 | 135.1 | 266.4 | 254.3 | 191.7
451 | 306 | 470.4 | 188.16 | 219.9482 | 231.8 | 240.5 | 257.3 | 257.8 | 429 | 26.6 | 21 | 58.9 | 3.9 | 250.4 | 13.2 | 502.1 | 792.6 | 784.4 | 506.3 | 765.7 | 349.4 | 611.5 | 821.3 | 432.6 | 745.8 | 145.8 | 269.2 | 274.5 | 208.4 | 135.7 | 266.8 | 255.2 | 192.3
452 | 307 | 469.9 | 187.96 | 219.7144 | 230.2 | 241.6 | 257.7 | 258.6 | 431.6 | 26.8 | 21 | 58.9 | 4.1 | 263 | 12.3 | 503.8 | 790.2 | 790.9 | 509.3 | 766.4 | 349.8 | 610.5 | 824.4 | 437.9 | 745.9 | 146.2 | 269.6 | 274.9 | 208.9 | 136.4 | 267.4 | 255.7 | 192.8
453 | 308 | 469.5 | 187.8 | 219.5274 | 229 | 242.5 | 258.8 | 259.5 | 429.3 | 26.9 | 21 | 58.9 | 4.2 | 266.8 | 11.7 | 505.9 | 791.1 | 796.9 | 512 | 765.6 | 350.3 | 607 | 824.4 | 444.3 | 746.8 | 146.6 | 269.9 | 275 | 209.8 | 137.1 | 267.8 | 256 | 193.3
454 | 309 | 469.6 | 187.84 | 219.5741 | 228.9 | 243.6 | 259.5 | 259.8 | 427.3 | 27 | 21 | 58.9 | 3.9 | 296.1 | 9.8 | 508.2 | 789 | 789.5 | 514.5 | 764 | 350.9 | 604.8 | 819.7 | 450.2 | 746.9 | 147.1 | 269.9 | 275.1 | 210.5 | 137.8 | 268.6 | 256.3 | 193.7
455 | 310 | 469.3 | 187.72 | 219.4339 | 228.2 | 243.9 | 259.9 | 260.2 | 426.2 | 27 | 21 | 58.8 | 3.8 | 289.7 | 7.6 | 510.8 | 782 | 785 | 516.6 | 764.9 | 351.7 | 600.8 | 808.8 | 454.3 | 745.8 | 147.5 | 269.6 | 275.1 | 210.8 | 138.4 | 268.8 | 256.8 | 194.2
456 | 311 | 469.2 | 187.68 | 219.3871 | 231.3 | 243.9 | 260.4 | 260.9 | 420.8 | 27 | 21 | 58.8 | 4.1 | 272.1 | 7.4 | 513.1 | 782.9 | 770.9 | 518.8 | 763.1 | 352.7 | 598.7 | 798.3 | 457.4 | 745.4 | 147.9 | 269.5 | 275.1 | 211 | 139.1 | 269.3 | 257 | 194.6
457 | 312 | 469.1 | 187.64 | 219.3403 | 234.4 | 244 | 260.3 | 260.8 | 417.4 | 27.1 | 21 | 59 | 4.1 | 286.3 | 9.6 | 515.6 | 784.3 | 762.8 | 521.1 | 761.8 | 354 | 595.7 | 791.5 | 459.5 | 744.1 | 148.4 | 269.9 | 275.1 | 211.4 | 139.8 | 269.6 | 257.4 | 195.1
458 | 313 | 469.5 | 187.8 | 219.5274 | 235.9 | 243.7 | 258.8 | 260.2 | 416.7 | 27.3 | 21 | 59.2 | 5.3 | 280.7 | 12.7 | 518.1 | 781.5 | 764.7 | 523.2 | 761.9 | 355.6 | 593.6 | 796.8 | 462.3 | 744.3 | 148.8 | 270.1 | 275.2 | 211.7 | 140.5 | 270.1 | 257.9 | 195.6
459 | 314 | 470.2 | 188.08 | 219.8547 | 236.9 | 243.3 | 257.8 | 260 | 420 | 27.5 | 21 | 59.4 | 4.5 | 267.5 | 15.7 | 520.7 | 779.6 | 757.5 | 525.2 | 760.5 | 357.6 | 590.9 | 797.4 | 463.9 | 744.4 | 149.2 | 270.6 | 275.5 | 212.1 | 141.2 | 270.8 | 258.5 | 196
460 | 315 | 470.2 | 188.08 | 219.8547 | 237.7 | 243.6 | 257.8 | 259.5 | 418 | 27.7 | 21 | 59.6 | 3.9 | 281.1 | 15.5 | 523.5 | 776.8 | 759.9 | 527.4 | 758.6 | 359.9 | 587.1 | 792.5 | 465.2 | 743.5 | 149.6 | 271 | 275.7 | 212.8 | 141.9 | 270.9 | 258.7 | 196.5
461 | 316 | 469.7 | 187.88 | 219.6209 | 237.5 | 244.5 | 257.2 | 259.5 | 418.7 | 27.8 | 20.9 | 59.8 | 5.2 | 281.8 | 17.3 | 526.1 | 773.8 | 761.6 | 529.3 | 758.3 | 362.5 | 584.1 | 803.8 | 465.7 | 744 | 150 | 271.5 | 276 | 213.6 | 142.6 | 270.7 | 259.1 | 197
462 | 317 | 470.5 | 188.2 | 219.995 | 237.3 | 246.1 | 258.1 | 259.1 | 422.9 | 28 | 20.9 | 60.2 | 9.1 | 275.6 | 19.5 | 528.8 | 775 | 749.4 | 530.9 | 754.8 | 365.2 | 581.6 | 794.2 | 464.8 | 742.7 | 150.3 | 272 | 276.4 | 214.4 | 143.3 | 270.7 | 259 | 197.4
463 | 318 | 470.2 | 188.08 | 219.8547 | 238.8 | 246.7 | 258.3 | 259.1 | 424.8 | 28 | 20.9 | 60.5 | 12.2 | 271.8 | 18.9 | 531.6 | 774.3 | 733.4 | 532.6 | 751.6 | 368.2 | 579.4 | 776.1 | 462.9 | 741.2 | 150.7 | 272.6 | 276.8 | 215.1 | 144 | 270.8 | 259 | 197.7
464 | 319 | 469.8 | 187.92 | 219.6677 | 240.4 | 247.3 | 257.1 | 259.8 | 423.2 | 28.2 | 20.9 | 60.8 | 10.6 | 268.6 | 19.7 | 534.4 | 772.1 | 736.7 | 534.3 | 749.8 | 371.2 | 578.5 | 782.7 | 461 | 740.8 | 151.1 | 273.1 | 277.7 | 215.7 | 144.7 | 270.8 | 259 | 198
465 | 320 | 469.1 | 187.64 | 219.3403 | 239.3 | 247.5 | 256.7 | 259.4 | 424.4 | 28.3 | 20.9 | 61.1 | 10.8 | 260.9 | 18.2 | 537.2 | 769.1 | 741.8 | 535.7 | 749.2 | 374.2 | 577.4 | 786 | 458.8 | 741.3 | 151.5 | 273.9 | 278.4 | 216.7 | 145.4 | 270.9 | 258.9 | 198.4
466 | 321 | 469 | 187.6 | 219.2936 | 238.9 | 248.1 | 256.6 | 259.3 | 421.9 | 28.3 | 20.9 | 61.4 | 11.7 | 266 | 16.5 | 540.2 | 764.4 | 731.7 | 537.1 | 748.7 | 377.1 | 575.2 | 778.5 | 456.5 | 739.4 | 151.8 | 274.4 | 278.6 | 217.3 | 146.1 | 271 | 259 | 198.9
467 | 322 | 468.8 | 187.52 | 219.2001 | 237.2 | 249.1 | 257.1 | 258.2 | 419.9 | 28.3 | 20.9 | 61.7 | 14 | 259.9 | 20.9 | 543 | 761.2 | 716.3 | 538.4 | 747.2 | 380.1 | 572.2 | 766.5 | 454.3 | 738 | 152.2 | 274.6 | 278.7 | 217.7 | 146.8 | 271 | 259.2 | 199.3
468 | 323 | 468.7 | 187.48 | 219.1533 | 236.9 | 249.4 | 257.4 | 257.6 | 416.6 | 28.2 | 20.9 | 62 | 16.2 | 269.7 | 23.6 | 545.8 | 757.8 | 707.4 | 539.3 | 745.2 | 383.3 | 569.6 | 766.1 | 452.4 | 736.5 | 152.6 | 274.8 | 278.8 | 218.2 | 147.5 | 271 | 259.3 | 199.7
469 | 324 | 469.3 | 187.72 | 219.4339 | 236.1 | 249.9 | 256.1 | 256.5 | 413.9 | 28.1 | 20.9 | 62.3 | 18 | 267.1 | 22.9 | 548.7 | 755.2 | 693.1 | 540.3 | 741.4 | 386.6 | 567.9 | 755.6 | 450.4 | 734.4 | 152.9 | 274.8 | 278.7 | 218.3 | 148.2 | 271 | 259.4 | 200.2
470 | 325 | 468.1 | 187.24 | 218.8728 | 235.4 | 249.3 | 255.7 | 255.5 | 410.3 | 28.2 | 20.9 | 62.6 | 15.7 | 255.6 | 27.2 | 551.7 | 755 | 685.9 | 542 | 739.6 | 390 | 565.4 | 749.8 | 448.2 | 732 | 153.3 | 274.5 | 278.6 | 218.4 | 148.9 | 270.9 | 259.6 | 200.6
471 | 326 | 468 | 187.2 | 218.826 | 233.5 | 248.1 | 255.4 | 256.1 | 408.5 | 28.4 | 20.9 | 62.9 | 9.9 | 262.3 | 24.4 | 554.7 | 756.2 | 687.6 | 543.6 | 738.6 | 393.1 | 564.7 | 752.5 | 446.3 | 731.7 | 153.6 | 274.2 | 278.2 | 218.7 | 149.5 | 271.7 | 259.8 | 201
472 | 327 | 468.1 | 187.24 | 218.8728 | 232.5 | 247.6 | 255.6 | 257.1 | 407.6 | 28.4 | 20.9 | 63 | 6.6 | 270.3 | 24.1 | 557.9 | 759.4 | 702.6 | 544.9 | 738.6 | 396.1 | 563.3 | 756.6 | 444.5 | 731.2 | 154 | 274.1 | 277.7 | 219.3 | 150.2 | 271.6 | 259.8 | 201.4
473 | 328 | 469.3 | 187.72 | 219.4339 | 235.1 | 247.5 | 255.6 | 257.8 | 406.2 | 28.4 | 20.9 | 63.1 | 4.6 | 272.7 | 21.8 | 561.3 | 761.6 | 707.5 | 546.1 | 736.5 | 399.1 | 562.1 | 764 | 443 | 731.3 | 154.4 | 274.3 | 277.5 | 219.9 | 150.9 | 271.9 | 259.9 | 201.8
474 | 329 | 469.6 | 187.84 | 219.5741 | 238.9 | 247.5 | 256.1 | 257.4 | 406.8 | 28.7 | 20.9 | 63.1 | 4.4 | 261.3 | 17.5 | 564.8 | 761.6 | 697 | 547.1 | 733.4 | 402.5 | 560.6 | 757.1 | 441.5 | 730 | 154.7 | 274.3 | 277.3 | 220.4 | 151.5 | 272.3 | 260 | 202.2
475 | 330 | 468.8 | 187.52 | 219.2001 | 241.2 | 248.3 | 256.5 | 256.9 | 409.2 | 28.7 | 20.9 | 63.2 | 5.1 | 259.7 | 14 | 568.4 | 762.1 | 688.9 | 548.2 | 731.2 | 406 | 560.1 | 760.7 | 439.9 | 729.7 | 155.1 | 275.3 | 277.4 | 221.1 | 152.2 | 272.4 | 260.3 | 202.8
476 | 331 | 468.5 | 187.4 | 219.0598 | 240.5 | 249.4 | 256.6 | 256.6 | 414 | 28.6 | 20.9 | 63.4 | 5.8 | 262.6 | 15.7 | 572.3 | 763.3 | 689.1 | 549.5 | 729.4 | 409.9 | 558.6 | 760.2 | 438.6 | 728.6 | 155.4 | 275.8 | 277.6 | 221.8 | 152.8 | 272 | 260.3 | 203.1
477 | 332 | 468.3 | 187.32 | 218.9663 | 238.6 | 249.9 | 256.1 | 256.3 | 413.9 | 28.6 | 20.9 | 63.6 | 6.2 | 280.8 | 15.3 | 575.7 | 765.7 | 686.1 | 550.8 | 727.8 | 414.2 | 558.4 | 758 | 437.5 | 727.2 | 155.8 | 276.1 | 277.7 | 222 | 153.5 | 271.9 | 260.3 | 203.5
478 | 333 | 468.3 | 187.32 | 218.9663 | 236.6 | 249.5 | 256.2 | 256.6 | 412.5 | 28.6 | 20.9 | 63.7 | 5.6 | 265.3 | 13.8 | 579 | 767.4 | 684.3 | 552.1 | 726.9 | 418.7 | 558.1 | 758.7 | 436.7 | 725.8 | 156.1 | 275.9 | 278.1 | 222.2 | 154.2 | 271.7 | 260.4 | 203.9
479 | 334 | 468.4 | 187.36 | 219.013 | 233.8 | 249 | 256.4 | 257.3 | 411.9 | 28.6 | 20.9 | 63.9 | 6.7 | 290 | 13.4 | 582.1 | 768.5 | 704.5 | 553.5 | 728.2 | 423.4 | 558.2 | 767.6 | 436.3 | 725.9 | 156.5 | 275.9 | 278.2 | 222.4 | 154.9 | 271.6 | 260.8 | 204.3
480 | 335 | 468.1 | 187.24 | 218.8728 | 232.5 | 248 | 258 | 257.1 | 414.1 | 28.7 | 20.9 | 64.1 | 5.9 | 296.7 | 13 | 585.4 | 765.2 | 721.7 | 554.8 | 731.2 | 428.1 | 558.9 | 767 | 436.2 | 725.6 | 156.8 | 276.1 | 278.3 | 222.7 | 155.7 | 271.4 | 261.4 | 204.8
481 | 336 | 468.4 | 187.36 | 219.013 | 230.8 | 247.8 | 258.3 | 255.6 | 413.1 | 28.8 | 20.9 | 64.2 | 6 | 299.6 | 10.4 | 588.5 | 765.1 | 728.9 | 556.4 | 731.8 | 433.9 | 559.9 | 766.1 | 436.2 | 725.7 | 157.2 | 276.2 | 278.4 | 222.8 | 156.4 | 271.2 | 261.5 | 205.4
482 | 337 | 469.4 | 187.76 | 219.4806 | 231.2 | 247.2 | 258.5 | 254.1 | 412.9 | 28.8 | 20.9 | 64.3 | 6.2 | 312.2 | 8.8 | 591.5 | 767.7 | 731.1 | 558.3 | 730.5 | 441.4 | 560.8 | 767.3 | 436.4 | 725.3 | 157.5 | 277.1 | 278.6 | 223.4 | 157.1 | 271.1 | 261.5 | 205.8
483 | 338 | 468.3 | 187.32 | 218.9663 | 231.8 | 246 | 258.8 | 253.6 | 413.7 | 28.8 | 20.9 | 64.5 | 6.5 | 293.1 | 7.6 | 594.3 | 774.8 | 719.8 | 560.9 | 728 | 445.4 | 559.5 | 757 | 436.5 | 723.3 | 157.8 | 277.7 | 279.2 | 224.1 | 157.8 | 270.9 | 261.5 | 206.2
484 | 339 | 468.2 | 187.28 | 218.9195 | 231.9 | 245.2 | 259.4 | 254.2 | 414.1 | 29 | 20.9 | 64.7 | 6.4 | 286.5 | 7.5 | 597 | 778.7 | 700.8 | 563.6 | 726.1 | 448.2 | 561.5 | 748.2 | 436.6 | 721.8 | 158.2 | 277.8 | 279.5 | 224.4 | 158.6 | 270.5 | 262 | 206.8
485 | 340 | 469.7 | 187.88 | 219.6209 | 232.4 | 244 | 259.3 | 254.6 | 415 | 29.2 | 20.9 | 64.8 | 5.8 | 265.4 | 7.8 | 599.5 | 781.5 | 671.4 | 566.4 | 723.3 | 451 | 564.7 | 737.2 | 436.6 | 720.1 | 158.5 | 277.7 | 279.8 | 224.6 | 159.3 | 270.6 | 262.6 | 207.4
486 | 341 | 469.1 | 187.64 | 219.3403 | 233 | 243.3 | 259.5 | 255.1 | 415.2 | 29.3 | 20.9 | 64.8 | 4.7 | 267 | 10.4 | 602.3 | 781.7 | 658.4 | 570 | 720.8 | 454.5 | 567.5 | 724.8 | 436.4 | 718.3 | 158.8 | 277.6 | 279.9 | 224.6 | 160.1 | 270.8 | 263.7 | 207.9
487 | 342 | 469.1 | 187.64 | 219.3403 | 237.2 | 243.1 | 260.8 | 255.4 | 412.9 | 29.4 | 20.9 | 64.8 | 5.6 | 263.2 | 12.9 | 605.7 | 780.6 | 643.3 | 573.5 | 718.2 | 458.7 | 568.1 | 721.6 | 435.8 | 716.7 | 159.1 | 277.3 | 280.6 | 224.7 | 160.9 | 271.1 | 264.1 | 208.4
488 | 343 | 469.8 | 187.92 | 219.6677 | 240.2 | 242.3 | 261.9 | 255.5 | 410.3 | 29.5 | 20.8 | 64.8 | 7.3 | 257.1 | 11.6 | 609 | 780.8 | 638 | 577 | 717.3 | 463.1 | 567.5 | 267 | 285.5 | 715.1 | 159.5 | 277.2 | 280.8 | 225 | 161.8 | 272.2 | 265.1 | 208.7
489 | 344 | 468.9 | 187.56 | 219.2468 | 240.7 | 241.3 | 262.7 | 255.2 | 410 | 29.7 | 20.8 | 64.8 | 8.1 | 267.8 | 11.5 | 612.1 | 782.5 | 653.4 | 580.6 | 717 | 467.5 | 566.5 | 627 | 397.5 | 713.9 | 159.8 | 277.1 | 280.9 | 225.6 | 162.6 | 273.5 | 265.8 | 209.2
490 | 345 | 470 | 188 | 219.7612 | 241.1 | 240.7 | 263.1 | 256.1 | 413.5 | 29.9 | 20.8 | 64.9 | 7.2 | 268.1 | 13.8 | 614.8 | 782.2 | 656.6 | 583.4 | 714.2 | 471.3 | 566 | 736.3 | 432.7 | 715 | 160.1 | 277.4 | 281.2 | 226.3 | 163.5 | 274.2 | 266.1 | 209.6
491 | 346 | 469.2 | 187.68 | 219.3871 | 243.8 | 240.9 | 262.9 | 255.9 | 417.7 | 30 | 20.8 | 64.9 | 6.1 | 264.3 | 15.9 | 617.5 | 783.3 | 655.4 | 586.3 | 711.3 | 474.7 | 564.3 | 202.6 | 294 | 714.3 | 160.4 | 278.3 | 281.6 | 227.1 | 164.4 | 274.9 | 266.1 | 209.9
492 | 347 | 469.3 | 187.72 | 219.4339 | 246.1 | 241.4 | 263.7 | 256.1 | 418.8 | 30.1 | 20.8 | 64.9 | 6.6 | 267.3 | 17.1 | 620.4 | 782.3 | 659.8 | 588.8 | 707.5 | 477.9 | 563.2 | 745.3 | 428.9 | 714.2 | 160.7 | 279 | 282.3 | 227.9 | 165.2 | 275.3 | 266.1 | 210.2
493 | 348 | 469.6 | 187.84 | 219.5741 | 245.1 | 243 | 264.8 | 257.4 | 423.6 | 30.2 | 20.8 | 65.1 | 8.3 | 271.6 | 15.9 | 624 | 784.5 | 658.6 | 592.3 | 704.8 | 480.8 | 562.2 | 762.4 | 430.5 | 714.2 | 161 | 279.7 | 282.9 | 228.6 | 166.2 | 276.8 | 266.1 | 210.5
494 | 349 | 466.4 | 186.56 | 218.0779 | 244.3 | 244.3 | 266.8 | 258.6 | 429.3 | 30.4 | 20.8 | 65.2 | 6.2 | 273.6 | 15.8 | 627.3 | 788 | 675.1 | 595.7 | 703.8 | 483.4 | 561.1 | 769.2 | 429.9 | 714.1 | 161.3 | 280.9 | 283.9 | 229.5 | 167.1 | 277.1 | 266.3 | 211
495 | 350 | 466 | 186.4 | 217.8909 | 244.9 | 245.8 | 268.8 | 260.7 | 434.1 | 30.7 | 20.8 | 65.3 | 5.3 | 268.9 | 15.5 | 630.6 | 790.7 | 689.3 | 599.6 | 703.8 | 486.1 | 560.6 | 779.3 | 429.3 | 714.3 | 161.6 | 281.6 | 284.8 | 230.2 | 167.9 | 278.2 | 267 | 211.5
496 | 351 | 464.3 | 185.72 | 217.096 | 246 | 246.7 | 269.3 | 262 | 438.4 | 30.9 | 20.8 | 65.5 | 6.1 | 273.4 | 16.6 | 634.7 | 792.6 | 693.9 | 605.2 | 702.4 | 488.7 | 559.8 | 556.1 | 417.3 | 715.4 | 161.9 | 282.4 | 285.5 | 230.7 | 168.8 | 278.6 | 267.6 | 212
497 | 352 | 465.2 | 186.08 | 217.5168 | 246 | 247.6 | 269.5 | 263.5 | 439 | 31 | 20.8 | 65.7 | 6.7 | 278.1 | 16.1 | 638.2 | 792.9 | 715.6 | 609.8 | 704.4 | 491.2 | 558.8 | 411.6 | 413.4 | 716.3 | 162.2 | 283.1 | 285.7 | 231.1 | 169.6 | 279.4 | 268 | 212.6
498 | 353 | 466.3 | 186.52 | 218.0311 | 244.3 | 249 | 269.7 | 264.9 | 436.1 | 31.2 | 20.8 | 65.8 | 7.3 | 278 | 15.5 | 640.9 | 794.1 | 722.9 | 613.7 | 702.6 | 493.6 | 558.6 | 794.8 | 427.8 | 716.1 | 162.5 | 282.7 | 285.6 | 231.7 | 170.4 | 280.2 | 268.7 | 213
499 | 354 | 467.8 | 187.12 | 218.7325 | 244.4 | 249.9 | 269 | 265.4 | 436.5 | 31.3 | 20.8 | 66 | 9.1 | 267 | 14.6 | 644.4 | 796.3 | 709.2 | 620.6 | 699.4 | 495.7 | 557.2 | 435.6 | 427.4 | 715.4 | 162.8 | 282.5 | 285.6 | 232.3 | 171.2 | 280.7 | 269.1 | 213.4
500 | 355 | 467.8 | 187.12 | 218.7325 | 245.5 | 250.8 | 268.3 | 266.2 | 437.6 | 31.4 | 20.8 | 66.3 | 7.7 | 271.3 | 14.1 | 648.3 | 799.2 | 685.6 | 626.7 | 695.4 | 497.7 | 556.6 | 539.9 | 427.1 | 713.6 | 163.1 | 282.7 | 286.1 | 232.8 | 172 | 280.6 | 269.5 | 213.9
501 | 356 | 468.4 | 187.36 | 219.013 | 248 | 251.1 | 269.6 | 267 | 441.8 | 31.5 | 20.8 | 66.5 | 6.9 | 282.8 | 13.5 | 651.3 | 799.8 | 673.8 | 630.5 | 692.5 | 499.8 | 557 | 761 | 427.2 | 712.2 | 163.5 | 283.3 | 287 | 233.4 | 172.8 | 280.6 | 269.7 | 214.3
502 | 357 | 467.4 | 186.96 | 218.5455 | 249.3 | 252.3 | 270.9 | 267.9 | 443.2 | 31.7 | 20.8 | 66.8 | 6.8 | 280.8 | 13.3 | 654.4 | 797.6 | 667.4 | 633.6 | 691.6 | 501.9 | 557.3 | 328.7 | 424.2 | 711.4 | 163.8 | 284.2 | 287.9 | 233.8 | 173.5 | 280.5 | 269.9 | 214.8
503 | 358 | 469.4 | 187.76 | 219.4806 | 249.7 | 252.8 | 271.7 | 267.6 | 439.1 | 31.6 | 20.8 | 67 | 7.7 | 270.9 | 12.6 | 657 | 794.8 | 673.3 | 635.3 | 692.6 | 504.2 | 558.2 | 657 | 426.3 | 711.7 | 164.1 | 284.9 | 288.5 | 234 | 174.3 | 281.4 | 270.1 | 215.1
504 | 359 | 470.4 | 188.16 | 219.9482 | 248.1 | 253 | 271.7 | 267.2 | 434.5 | 31.6 | 20.8 | 67.4 | 7.2 | 263.1 | 13.3 | 659.1 | 795.3 | 679.2 | 636.6 | 691 | 506.4 | 556.3 | 753.4 | 428.8 | 710.8 | 164.4 | 285.5 | 288.7 | 234.3 | 175 | 281.7 | 270.8 | 215.6
505 | 360 | 468.1 | 187.24 | 218.8728 | 248 | 252.4 | 272.6 | 267 | 431.5 | 31.6 | 20.8 | 67.5 | 7.8 | 261.7 | 12.7 | 661.7 | 793 | 697.9 | 638 | 692.2 | 508.7 | 557.6 | 272.3 | 429.6 | 710.4 | 164.8 | 285.7 | 288.8 | 234.5 | 175.8 | 281.8 | 271.5 | 216.2
506 | 361 | 466.8 | 186.72 | 218.2649 | 248 | 253 | 272.8 | 266.5 | 431.5 | 31.6 | 20.8 | 67.5 | 8.1 | 266.7 | 13.4 | 663.6 | 791.9 | 687.9 | 641.7 | 693.4 | 511.2 | 560.5 | 468.7 | 430.5 | 711.1 | 165.1 | 285.8 | 288.9 | 234.5 | 176.6 | 281.9 | 272.3 | 216.8
507 | 362 | 467.5 | 187 | 218.5922 | 252.4 | 252.8 | 271.5 | 266.8 | 431.6 | 31.7 | 20.8 | 67.4 | 6.9 | 308.4 | 11.4 | 665.5 | 792.6 | 676.8 | 647.1 | 692.6 | 513.8 | 564.1 | 571.3 | 431.5 | 711.2 | 165.4 | 285.9 | 289.1 | 234.8 | 177.5 | 281.9 | 272.6 | 217.2
508 | 363 | 467.6 | 187.04 | 218.639 | 255.5 | 251.4 | 270.9 | 266.1 | 431.1 | 32 | 20.8 | 67.3 | 7.2 | 276.5 | 9.9 | 667.9 | 791.5 | 681.5 | 652.9 | 694.2 | 516.7 | 565.7 | 711.3 | 432.5 | 709.3 | 165.8 | 285.4 | 289.3 | 234.9 | 178.3 | 282.1 | 272.8 | 217.5
509 | 364 | 467.9 | 187.16 | 218.7793 | 257.3 | 250.7 | 271.1 | 265.5 | 428.3 | 32.1 | 20.8 | 67.2 | 7.6 | 283.1 | 11.5 | 670.7 | 790.8 | 679.5 | 657.2 | 692.7 | 519.5 | 564.4 | 725.9 | 433.8 | 708.6 | 166.1 | 284.9 | 289.7 | 235 | 179.2 | 283.2 | 273.3 | 218
510 | 365 | 468.2 | 187.28 | 218.9195 | 258.2 | 249.7 | 271.1 | 266.2 | 423.8 | 31.9 | 20.8 | 67.1 | 8.1 | 288.1 | 11.5 | 673.7 | 791.9 | 685.3 | 661.9 | 692.5 | 522.1 | 565 | 725 | 435.2 | 709.2 | 166.4 | 284.3 | 289.8 | 235.1 | 180.1 | 284.4 | 273.9 | 218.4
511 | 366 | 468.3 | 187.32 | 218.9663 | 260.1 | 248.3 | 271.8 | 266.9 | 421.3 | 31.8 | 20.8 | 67 | 8.1 | 297 | 11.9 | 676.9 | 794.8 | 695.2 | 667.8 | 689.9 | 524.7 | 563.2 | 726 | 436.6 | 708 | 166.8 | 284 | 289.7 | 235.5 | 181 | 285.1 | 274.3 | 218.9
512 | 367 | 467.7 | 187.08 | 218.6857 | 261.9 | 246.9 | 272.2 | 266.7 | 418.6 | 31.9 | 20.8 | 66.9 | 8.5 | 292.2 | 12.1 | 680.4 | 796.5 | 700.4 | 673.1 | 690.3 | 527.1 | 561.6 | 731.8 | 438 | 706.9 | 167.1 | 283.9 | 289.6 | 236.1 | 181.8 | 285.5 | 274.5 | 219.2
513 | 368 | 468.4 | 187.36 | 219.013 | 262.2 | 246.1 | 272.1 | 267.4 | 417.8 | 31.9 | 20.8 | 66.9 | 7 | 300.1 | 11.5 | 683.5 | 796.8 | 705.1 | 676.6 | 689.5 | 529.3 | 560.2 | 734.1 | 439.4 | 706.1 | 167.4 | 283.9 | 289.3 | 236.7 | 182.7 | 285.7 | 274.5 | 219.6
514 | 369 | 468.8 | 187.52 | 219.2001 | 263.7 | 245.9 | 271.3 | 267.6 | 417.9 | 32 | 20.8 | 66.9 | 7.5 | 289.4 | 12.3 | 686.4 | 794.6 | 703.4 | 679.9 | 689.7 | 531 | 559 | 734.7 | 440.8 | 705.9 | 167.7 | 284.1 | 289.1 | 237.2 | 183.5 | 285.7 | 274.6 | 219.9
515 | 370 | 469.1 | 187.64 | 219.3403 | 262.6 | 246.3 | 270.2 | 267.7 | 421 | 32.1 | 20.8 | 67.1 | 7.7 | 291.8 | 13 | 689.6 | 797.4 | 701.3 | 683.8 | 687.5 | 532.7 | 558.4 | 744 | 442.3 | 705.7 | 168.1 | 284.2 | 289 | 237.8 | 184.3 | 285.5 | 274.6 | 220.2
516 | 371 | 469.1 | 187.64 | 219.3403 | 261.1 | 247.3 | 270 | 268.3 | 425.8 | 32.2 | 20.8 | 67.2 | 7.7 | 292.4 | 14.5 | 692.4 | 797.8 | 711 | 687.3 | 689.5 | 534.8 | 558.4 | 750.2 | 444 | 706 | 168.4 | 284.7 | 289 | 238.4 | 185.2 | 285.2 | 274.7 | 220.6
517 | 372 | 468.7 | 187.48 | 219.1533 | 259.7 | 249.2 | 270.2 | 268.7 | 428.8 | 32.4 | 20.8 | 67.3 | 6.8 | 292.9 | 14.6 | 695.5 | 795.5 | 712.9 | 692.3 | 688.8 | 536.9 | 557.9 | 749.1 | 445.9 | 705.5 | 168.7 | 285.7 | 289.4 | 238.9 | 186 | 284.7 | 274.8 | 221
518 | 373 | 468.6 | 187.44 | 219.1066 | 257.6 | 249.9 | 270 | 268.6 | 437.2 | 32.5 | 20.8 | 67.4 | 5.6 | 289.6 | 13.5 | 699.3 | 800.3 | 718.2 | 698.7 | 687.5 | 538.9 | 557.6 | 757.2 | 447.9 | 705.2 | 169.1 | 286.7 | 290 | 240.1 | 186.9 | 284.9 | 274.6 | 221.3
519 | 374 | 469.6 | 187.84 | 219.5741 | 255 | 250.4 | 270.2 | 269 | 442.9 | 32.7 | 20.8 | 67.6 | 6.1 | 287 | 14.2 | 703.9 | 801.3 | 711.6 | 706.7 | 686 | 540.9 | 558 | 767.3 | 450 | 705 | 169.4 | 287.2 | 290.6 | 241 | 187.7 | 284.9 | 274.6 | 221.7
520 | 375 | 469.2 | 187.68 | 219.3871 | 253.2 | 251.5 | 270.8 | 270.4 | 450.2 | 32.8 | 20.8 | 67.7 | 5.9 | 287.1 | 13 | 708.6 | 799.3 | 705.2 | 711.7 | 685.4 | 542.5 | 558.5 | 768.9 | 452.1 | 705.3 | 169.7 | 287.8 | 291.2 | 241.6 | 188.5 | 285 | 274.6 | 222.1
521 | 376 | 469.5 | 187.8 | 219.5274 | 250.9 | 252.6 | 271.9 | 270.6 | 451.5 | 32.9 | 20.8 | 67.8 | 5.5 | 269.2 | 11 | 712.8 | 800.9 | 704.6 | 714.9 | 684.3 | 544.2 | 558.3 | 775.3 | 454.2 | 705.5 | 170.1 | 288.5 | 292.2 | 242.4 | 189.2 | 285.8 | 274.6 | 222.5
522 | 377 | 469.8 | 187.92 | 219.6677 | 248.8 | 254 | 273.7 | 270.9 | 451.4 | 32.9 | 20.7 | 67.9 | 5.7 | 250.3 | 10.6 | 716.1 | 803 | 702 | 717.6 | 682 | 546.2 | 559.5 | 781.6 | 456.4 | 706 | 170.4 | 289.4 | 292.9 | 243.2 | 190 | 286.8 | 274.8 | 222.9
523 | 378 | 469.3 | 187.72 | 219.4339 | 248.4 | 255.2 | 275.2 | 271.9 | 450.9 | 33 | 20.7 | 67.9 | 5.3 | 250.6 | 9.9 | 719.3 | 807 | 685.2 | 719.5 | 679.3 | 548.5 | 559.1 | 776.7 | 458.1 | 705.5 | 170.8 | 290 | 293.5 | 243.5 | 190.7 | 287.1 | 275 | 223.3
524 | 379 | 469.5 | 187.8 | 219.5274 | 250.3 | 255.5 | 276 | 272.5 | 450.4 | 33 | 20.7 | 68 | 5.8 | 277 | 10.5 | 722.6 | 805.9 | 669.5 | 721.6 | 677.8 | 550.9 | 558.5 | 776.5 | 459.8 | 704.7 | 171.1 | 290.4 | 294.1 | 243.7 | 191.5 | 287.8 | 275 | 223.6
525 | 380 | 469.7 | 187.88 | 219.6209 | 252 | 255.9 | 275 | 272.3 | 446.3 | 33.1 | 20.7 | 68.1 | 5 | 274 | 10.8 | 727.3 | 803.3 | 660.4 | 725.8 | 675.4 | 553.3 | 558.8 | 760.7 | 461.1 | 702.4 | 171.5 | 290.8 | 294.5 | 243.8 | 192.2 | 288.3 | 275.3 | 224
526 | 381 | 469.7 | 187.88 | 219.6209 | 252.5 | 256.2 | 274.2 | 272.5 | 442 | 33.1 | 20.7 | 68.2 | 5.3 | 267.6 | 10 | 731.5 | 805.3 | 642.5 | 730 | 673.2 | 555.9 | 559 | 741.9 | 462.4 | 700.9 | 171.9 | 290.9 | 294.7 | 244.1 | 192.9 | 289 | 275.5 | 224.3
527 | 382 | 469.1 | 187.64 | 219.3403 | 251.8 | 256.1 | 273.7 | 272 | 438.4 | 33.2 | 20.7 | 68.3 | 5.4 | 263.8 | 10 | 735 | 807.8 | 624.2 | 734.2 | 669.3 | 558.3 | 559.3 | 726.2 | 463.5 | 698.5 | 172.2 | 290.7 | 294.8 | 244.2 | 193.6 | 289.4 | 275.7 | 224.8
528 | 383 | 470.7 | 188.28 | 220.0885 | 253.2 | 256.5 | 273.4 | 271.8 | 434.7 | 33.2 | 20.7 | 68.4 | 6.3 | 267.8 | 9.2 | 738.2 | 808.1 | 613.5 | 737.2 | 667.5 | 561 | 559.3 | 721.5 | 465 | 697.3 | 172.6 | 290.8 | 296 | 244.5 | 194.4 | 288.7 | 275.6 | 225.2
529 | 384 | 470.7 | 188.28 | 220.0885 | 253.6 | 257.4 | 272.1 | 271.6 | 432.7 | 33.2 | 20.7 | 68.8 | 6 | 263.6 | 9.8 | 741 | 811.7 | 612.6 | 740.7 | 664.8 | 563.7 | 559.8 | 719.6 | 466.5 | 696.6 | 173 | 291.2 | 296.5 | 245 | 195.1 | 288.1 | 275.8 | 225.5
530 | 385 | 468.7 | 187.48 | 219.1533 | 259.5 | 258.3 | 273.1 | 270.7 | 428.8 | 33.2 | 20.7 | 69.2 | 5.7 | 272.3 | 10.2 | 742.9 | 810.2 | 609.4 | 743.5 | 663.3 | 566.3 | 559.5 | 715.8 | 468.1 | 695.2 | 173.4 | 291.8 | 296.8 | 245.2 | 195.8 | 287.4 | 275.9 | 225.9
531 | 386 | 467 | 186.8 | 218.3584 | 263.5 | 257.4 | 273.9 | 269.9 | 424.7 | 33.3 | 20.7 | 69.4 | 5.7 | 269.5 | 11 | 745 | 807.7 | 617.7 | 746.1 | 662.5 | 568.4 | 561 | 715.9 | 470 | 694.8 | 173.8 | 291.5 | 296.9 | 245.4 | 196.5 | 286.5 | 275.5 | 226.1
532 | 387 | 467.8 | 187.12 | 218.7325 | 267.3 | 256.3 | 273.3 | 270.3 | 421.8 | 33.5 | 20.7 | 69.6 | 5.1 | 278.6 | 10.4 | 747 | 806.5 | 622.4 | 747.9 | 661 | 568.7 | 562.1 | 716.1 | 472 | 694 | 174.2 | 291.3 | 296.7 | 245.5 | 197.1 | 285.8 | 275.2 | 226.4
533 | 388 | 467.9 | 187.16 | 218.7793 | 271.5 | 255.8 | 272.1 | 269.4 | 417.9 | 33.6 | 20.7 | 69.7 | 5.8 | 270.9 | 9.3 | 750.4 | 807.2 | 630.8 | 750.9 | 659.7 | 568.2 | 562.1 | 713.8 | 474.2 | 692 | 174.6 | 291 | 296 | 245.8 | 197.8 | 285.5 | 275 | 226.7
534 | 389 | 468.7 | 187.48 | 219.1533 | 273.1 | 255.4 | 271.5 | 269.3 | 415.1 | 33.7 | 20.7 | 69.8 | 5.3 | 280.6 | 8.8 | 753.8 | 805.2 | 632.5 | 754 | 659.5 | 569 | 561.9 | 707.5 | 476 | 690.8 | 174.9 | 290.5 | 295.2 | 246.1 | 198.4 | 285.4 | 274.9 | 227
535 | 390 | 468.8 | 187.52 | 219.2001 | 275.1 | 254.3 | 270.9 | 269.7 | 413.1 | 33.8 | 20.7 | 69.8 | 5.3 | 270.1 | 8.9 | 754.7 | 805.3 | 644.8 | 755.7 | 659.6 | 570.3 | 561.8 | 696.5 | 478.3 | 690.4 | 175.3 | 290 | 294.5 | 246.2 | 199 | 286.4 | 274.9 | 227.3
536 | 391 | 468.7 | 187.48 | 219.1533 | 275.7 | 253.4 | 269.8 | 270.1 | 412.6 | 33.9 | 20.7 | 69.7 | 5.1 | 274.8 | 8.8 | 756.5 | 807.6 | 640.9 | 757.4 | 660.1 | 571.6 | 560.7 | 685 | 480.8 | 689.4 | 175.7 | 289.5 | 293.8 | 246.3 | 199.7 | 286.4 | 275.2 | 227.7
537 | 392 | 467.4 | 186.96 | 218.5455 | 276.8 | 252.7 | 269.1 | 270.8 | 414.2 | 33.9 | 20.7 | 69.6 | 5.2 | 261.3 | 9.4 | 758.6 | 806.2 | 656.3 | 759.5 | 660.8 | 573.1 | 559.9 | 705.4 | 483.1 | 688.9 | 176.1 | 289 | 293.4 | 246.5 | 200.4 | 286.4 | 275.1 | 228.1
538 | 393 | 467.9 | 187.16 | 218.7793 | 276.7 | 252.4 | 268.8 | 270.7 | 412.6 | 34 | 20.7 | 69.6 | 5.6 | 261.2 | 11.1 | 759.9 | 804 | 658.1 | 760.9 | 663 | 574.9 | 559.2 | 704.1 | 485.4 | 688.7 | 176.4 | 288.6 | 293 | 246.6 | 201.1 | 286.8 | 275.2 | 228.5
539 | 394 | 467.8 | 187.12 | 218.7325 | 277.3 | 252.3 | 268.5 | 269.5 | 409.8 | 34.1 | 20.7 | 69.5 | 5.6 | 257.5 | 11 | 760.9 | 805.6 | 656.1 | 761.7 | 663.1 | 576.6 | 559.3 | 710.7 | 487.9 | 689 | 176.8 | 288.3 | 292.6 | 246.7 | 201.8 | 286.9 | 275.5 | 228.8
540 | 395 | 467.7 | 187.08 | 218.6857 | 277.6 | 251.9 | 268.4 | 269.5 | 408.4 | 34.2 | 20.7 | 69.6 | 5.5 | 270.2 | 10.4 | 763.6 | 805.8 | 646.1 | 762.7 | 661.6 | 578.5 | 558.7 | 707 | 489.6 | 687.6 | 177.1 | 288.2 | 292.8 | 246.9 | 202.6 | 286.3 | 275.8 | 229.1
541 | 396 | 468.6 | 187.44 | 219.1066 | 278.9 | 251.1 | 267.7 | 269.4 | 406.4 | 34.3 | 20.7 | 69.7 | 5.5 | 275.5 | 10.1 | 766.6 | 807.6 | 647.8 | 764.8 | 661.7 | 580.7 | 557.9 | 703 | 491.4 | 686.6 | 177.5 | 288.4 | 292.8 | 247.2 | 203.4 | 287.1 | 275.8 | 229.4
542 | 397 | 468.4 | 187.36 | 219.013 | 280.2 | 250.4 | 267.6 | 268.6 | 409.9 | 34.4 | 20.7 | 69.8 | 5.4 | 267.1 | 9.3 | 769.4 | 808.2 | 636.5 | 767.8 | 660 | 582.7 | 559.3 | 710.3 | 493.5 | 686.7 | 177.8 | 288.8 | 292.9 | 247.9 | 204.2 | 287.9 | 276.1 | 229.7
543 | 398 | 467.8 | 187.12 | 218.7325 | 280.7 | 250.9 | 268.3 | 268.8 | 412.5 | 34.4 | 20.7 | 69.8 | 5.6 | 252.7 | 8 | 772.1 | 808.2 | 639.6 | 770.9 | 659.3 | 584.6 | 560.2 | 711.1 | 495.5 | 686.2 | 178.2 | 288.9 | 293.2 | 248.6 | 205 | 287.7 | 276.3 | 230.2
544 | 399 | 468.5 | 187.4 | 219.0598 | 279.7 | 251.3 | 270.4 | 268.7 | 412.9 | 34.5 | 20.7 | 69.9 | 6.6 | 249.4 | 7.8 | 773.4 | 806.7 | 637.1 | 773.4 | 658.9 | 586.5 | 561.7 | 715.3 | 497.5 | 686.1 | 178.5 | 288.9 | 293.2 | 249.1 | 205.8 | 287.3 | 276.3 | 230.3
545 | 400 | 469.1 | 187.64 | 219.3403 | 278.5 | 251.3 | 271.6 | 268.9 | 415.7 | 34.6 | 20.7 | 70.1 | 6.8 | 257.3 | 9.7 | 775.5 | 805.3 | 647.1 | 775.7 | 658.3 | 588.4 | 562.9 | 716 | 499.6 | 685.5 | 178.9 | 289 | 293.4 | 249.6 | 206.6 | 287 | 276.2 | 230.6
546 | 401 | 469.7 | 187.88 | 219.6209 | 278.8 | 251.9 | 271.7 | 268.5 | 421.3 | 34.8 | 20.7 | 70.2 | 6.9 | 244.4 | 10 | 776.2 | 805.8 | 669.3 | 776.2 | 659.4 | 590.3 | 564.7 | 733 | 502.4 | 685.7 | 179.2 | 289.6 | 293.8 | 250 | 207.3 | 286.5 | 276.4 | 231
547 | 402 | 468.6 | 187.44 | 219.1066 | 276.7 | 252.9 | 272.5 | 268.8 | 431.7 | 34.8 | 20.7 | 70.4 | 7.5 | 256.1 | 9.9 | 777.3 | 802.8 | 684.3 | 776.7 | 660.4 | 591.9 | 567.1 | 752.2 | 505.2 | 686.8 | 179.5 | 290.4 | 294.7 | 250.6 | 208 | 286.1 | 276.7 | 231.3
548 | 403 | 468.5 | 187.4 | 219.0598 | 276.7 | 253.7 | 273 | 270.1 | 436.8 | 34.8 | 20.7 | 70.6 | 6.6 | 217.8 | 8.9 | 779.5 | 800.1 | 704.6 | 778.4 | 661.3 | 593.4 | 567.3 | 760.8 | 507.3 | 687.4 | 179.9 | 291.1 | 295.5 | 251.1 | 208.7 | 285.9 | 277 | 231.6
549 | 404 | 468.7 | 187.48 | 219.1533 | 276.3 | 254.4 | 274.7 | 270.9 | 442.5 | 34.8 | 20.7 | 70.6 | 6.1 | 256 | 9 | 779.6 | 796.9 | 718 | 778 | 666.8 | 595.1 | 569.7 | 768.7 | 509.2 | 689.6 | 180.2 | 291.5 | 296.1 | 251.5 | 209.3 | 285.9 | 277.1 | 231.9
550 | 405 | 469.1 | 187.64 | 219.3403 | 278.1 | 255.4 | 276.5 | 271.9 | 446.4 | 34.7 | 20.7 | 70.7 | 6.2 | 245.7 | 9.6 | 780.5 | 798.9 | 714.1 | 777.7 | 667.7 | 596.9 | 570.4 | 773.9 | 510.7 | 690.9 | 180.5 | 291.9 | 296.7 | 251.7 | 209.9 | 286.2 | 277.4 | 232.2
551 | 406 | 470.3 | 188.12 | 219.9014 | 278.9 | 255.8 | 276.8 | 273.1 | 443.4 | 34.6 | 20.7 | 70.8 | 5.9 | 248.2 | 9.7 | 781.6 | 800.9 | 718.1 | 778 | 670.7 | 598.6 | 571.3 | 781.2 | 512.5 | 692.4 | 180.8 | 292.2 | 297.1 | 251.8 | 210.6 | 287 | 277.9 | 232.6
552 | 407 | 468.7 | 187.48 | 219.1533 | 278.8 | 255.8 | 276.5 | 273.7 | 438.7 | 34.6 | 20.7 | 70.9 | 6.6 | 253 | 11.1 | 783.3 | 803.6 | 719.8 | 778.4 | 672.1 | 600.2 | 570.3 | 777.3 | 513.8 | 691.8 | 181.2 | 292.3 | 297.2 | 252.2 | 211.4 | 287.5 | 278.4 | 233.1
553 | 408 | 469.9 | 187.96 | 219.7144 | 277.8 | 256.2 | 275.5 | 274.2 | 439.7 | 34.6 | 20.7 | 71 | 7.6 | 273.7 | 12.1 | 787.1 | 802.5 | 715.5 | 781 | 670.1 | 602 | 569.1 | 766.3 | 515.4 | 690.7 | 181.4 | 292.6 | 296.7 | 252.7 | 212.3 | 287.9 | 278.8 | 233.4
554 | 409 | 470.2 | 188.08 | 219.8547 | 276.4 | 256.3 | 275.3 | 275.2 | 444.8 | 34.5 | 20.7 | 71.1 | 7.3 | 256.6 | 15.4 | 790.5 | 796.9 | 700.1 | 784.1 | 667.9 | 603.9 | 568.5 | 748.7 | 516.2 | 689.1 | 181.7 | 292.8 | 296.6 | 253.3 | 213.1 | 288.3 | 279 | 233.8
555 | 410 | 469.4 | 187.76 | 219.4806 | 273.4 | 257 | 276.1 | 276.3 | 446.5 | 34.5 | 20.7 | 71.1 | 6.1 | 252.4 | 16.2 | 794.2 | 793.2 | 681 | 787.8 | 665 | 606.1 | 567.3 | 729.5 | 516.5 | 687.4 | 182 | 292.8 | 296.2 | 253.4 | 213.9 | 288.4 | 279.3 | 234.2
556 | 411 | 468.8 | 187.52 | 219.2001 | 271.9 | 257.8 | 276.3 | 276.6 | 445.2 | 34.6 | 20.7 | 71.2 | 5.7 | 249.3 | 16.3 | 795.9 | 791.3 | 659.6 | 790.5 | 662.5 | 608.4 | 568.1 | 721.1 | 516.5 | 686.6 | 182.3 | 292.4 | 295.9 | 253.2 | 214.7 | 288.4 | 279.5 | 234.6
557 | 412 | 470.8 | 188.32 | 220.1352 | 273.7 | 258.1 | 275.6 | 277 | 440 | 34.7 | 20.6 | 71.3 | 7.2 | 254.2 | 15.7 | 797.5 | 788.1 | 636.5 | 792.6 | 659.2 | 611 | 569.2 | 706.9 | 516.2 | 684.5 | 182.6 | 291.9 | 296.2 | 253.1 | 215.4 | 290.2 | 279.6 | 235
558 | 413 | 470.1 | 188.04 | 219.8079 | 275.7 | 257.9 | 274.8 | 276.8 | 438 | 34.8 | 20.6 | 71.5 | 7 | 262.7 | 14.2 | 799.7 | 786.1 | 623.2 | 795.2 | 656.7 | 613.8 | 571.3 | 694.3 | 516.4 | 682.3 | 182.9 | 291.5 | 297.1 | 253.1 | 216.3 | 290.6 | 280.2 | 235.4
559 | 414 | 470.4 | 188.16 | 219.9482 | 276.4 | 257.2 | 273.7 | 277.2 | 433 | 34.9 | 20.6 | 71.7 | 6.3 | 273.2 | 12.5 | 801.2 | 786.6 | 628.9 | 797.4 | 656.6 | 616.4 | 572 | 697.9 | 517.4 | 682.3 | 183.2 | 291.6 | 296.8 | 253.4 | 217.3 | 291 | 280.7 | 235.8
560 | 415 | 469.9 | 187.96 | 219.7144 | 275.1 | 256.1 | 273.3 | 278 | 434 | 35 | 20.6 | 71.7 | 5.6 | 263 | 12.2 | 801.3 | 785.3 | 633.8 | 799 | 656.6 | 618.1 | 573.8 | 709.9 | 519.7 | 682.7 | 183.5 | 291.9 | 296.6 | 254.1 | 218.3 | 292.9 | 280.8 | 236.1
561 | 416 | 470.1 | 188.04 | 219.8079 | 271.9 | 256.1 | 273.7 | 277.9 | 437 | 35 | 20.6 | 71.8 | 5.9 | 269.4 | 11.8 | 802.5 | 785 | 636.7 | 800.3 | 656.3 | 619.6 | 574.2 | 715.2 | 521.6 | 682.5 | 183.8 | 292.1 | 296.5 | 254.5 | 219.2 | 293.1 | 281.1 | 236.5
562 | 417 | 468.6 | 187.44 | 219.1066 | 270.9 | 256.3 | 273.6 | 277.1 | 437.5 | 35 | 20.6 | 72 | 5.6 | 273.1 | 11.4 | 804.7 | 786.3 | 640.3 | 802.5 | 654.7 | 621.2 | 574.7 | 710.7 | 522.7 | 681.7 | 184.1 | 291.9 | 296.1 | 254.9 | 220.1 | 293 | 281.2 | 236.9
563 | 418 | 469.2 | 187.68 | 219.3871 | 274 | 257 | 273.2 | 277.5 | 434.6 | 35.1 | 20.6 | 72.3 | 6.6 | 273.8 | 11.7 | 807 | 786.5 | 659 | 805.1 | 657.6 | 622.9 | 577.2 | 718.4 | 524.6 | 681.9 | 184.4 | 291.8 | 295.7 | 255 | 220.9 | 292.7 | 281.2 | 237.1
564 | 419 | 469.9 | 187.96 | 219.7144 | 274.8 | 257.5 | 272.9 | 277.4 | 438.3 | 35.1 | 20.6 | 72.5 | 7 | 280 | 12.5 | 808 | 787.2 | 697.2 | 806.5 | 662.3 | 624.5 | 578.1 | 735.7 | 527.4 | 682.8 | 184.7 | 291.4 | 295.7 | 255.4 | 221.7 | 292.3 | 281.3 | 237.4
565 | 420 | 468.7 | 187.48 | 219.1533 | 275.7 | 257.4 | 272.4 | 276.7 | 439.1 | 35 | 20.6 | 72.7 | 6.9 | 280.1 | 12.9 | 808.6 | 787.8 | 694.3 | 806.8 | 662.8 | 626.3 | 577.5 | 734.1 | 529.4 | 683.4 | 185 | 291 | 295.5 | 255.5 | 222.7 | 291.7 | 281.3 | 237.6
566 | 421 | 469.9 | 187.96 | 219.7144 | 278.5 | 257.8 | 273.1 | 275.8 | 434.3 | 35.1 | 20.6 | 72.8 | 8.2 | 270.8 | 13.2 | 810.7 | 785.3 | 673.2 | 807.5 | 660.7 | 628.4 | 577.3 | 719.7 | 530.2 | 681.8 | 185.3 | 290.6 | 295.3 | 255.4 | 223.6 | 291.4 | 281 | 237.8
567 | 422 | 470 | 188 | 219.7612 | 281.7 | 257.8 | 273.6 | 275 | 431.1 | 35.3 | 20.6 | 72.9 | 7.8 | 257.2 | 11.9 | 812.7 | 782.6 | 656.4 | 808.8 | 657.9 | 630.7 | 577.6 | 703.9 | 530.5 | 680.3 | 185.6 | 290.8 | 295.7 | 255.4 | 224.3 | 291.6 | 280.8 | 238.1
568 | 423 | 468.9 | 187.56 | 219.2468 | 283.2 | 257.4 | 273.6 | 273.9 | 429 | 35.4 | 20.6 | 72.9 | 6.6 | 244.1 | 11 | 815 | 782.9 | 661.1 | 810.5 | 657.8 | 632.7 | 578.4 | 697.2 | 531.3 | 679.2 | 185.8 | 290.8 | 295.5 | 255.7 | 225.1 | 292.2 | 280.7 | 238.3
569 | 424 | 469.8 | 187.92 | 219.6677 | 280.5 | 256.7 | 272.5 | 273.3 | 427.6 | 35.4 | 20.6 | 72.9 | 6.1 | 248.5 | 10.1 | 815.7 | 785.7 | 676.6 | 811.4 | 660.2 | 634.3 | 579 | 701.7 | 534.1 | 679.6 | 186.1 | 290.7 | 295.2 | 256 | 225.9 | 292.4 | 280.7 | 238.6
570 | 425 | 469.7 | 187.88 | 219.6209 | 279 | 256.1 | 271.6 | 273.9 | 425.6 | 35.4 | 20.6 | 72.9 | 8.7 | 246.3 | 11.7 | 816.5 | 786.6 | 692.7 | 812.1 | 661.3 | 635.2 | 581.2 | 707.8 | 537.1 | 680.2 | 186.4 | 290.5 | 295.1 | 256.4 | 226.8 | 292.3 | 280.8 | 238.9
571 | 426 | 469.8 | 187.92 | 219.6677 | 279.3 | 255.7 | 271.6 | 273.3 | 423.6 | 35.5 | 20.6 | 73.1 | 11 | 247.3 | 14.6 | 817.4 | 785.8 | 698.5 | 812.1 | 661.1 | 636.2 | 580.9 | 705.6 | 538.5 | 679.5 | 186.7 | 290.4 | 295.1 | 256.9 | 227.6 | 292.3 | 281.1 | 239.2
572 | 427 | 469.8 | 187.92 | 219.6677 | 281.2 | 256 | 272 | 273.6 | 419.9 | 35.5 | 20.6 | 73.2 | 8.7 | 251.7 | 14.1 | 820.1 | 785.1 | 691.4 | 812.9 | 659.6 | 636.9 | 579.5 | 700 | 539.8 | 678.6 | 187 | 290.3 | 294.9 | 257.1 | 228.5 | 292.3 | 281.3 | 239.5
573 | 428 | 470.3 | 188.12 | 219.9014 | 282 | 255.9 | 271.9 | 273.9 | 417.8 | 35.6 | 20.6 | 73.3 | 8.8 | 248.5 | 13.5 | 822 | 782.4 | 690.4 | 814.3 | 659.3 | 637.7 | 578 | 699.7 | 541.5 | 677.4 | 187.2 | 290.4 | 294.8 | 257.3 | 229.4 | 292 | 281.3 | 239.8
574 | 429 | 468.3 | 187.32 | 218.9663 | 280.9 | 255.7 | 272 | 273.3 | 415.5 | 35.8 | 20.6 | 73.3 | 9 | 255.7 | 12.4 | 822.6 | 778.9 | 675.4 | 815 | 656.9 | 638.2 | 576.5 | 697 | 542.9 | 676.6 | 187.4 | 290.3 | 294.6 | 257.6 | 230.2 | 291.7 | 281 | 240.1
575 | 430 | 469.1 | 187.64 | 219.3403 | 278 | 255.4 | 271.8 | 273.4 | 412 | 36 | 20.6 | 73.3 | 7.1 | 263.5 | 10.4 | 824.7 | 778 | 649.9 | 816.7 | 654.9 | 639.5 | 577.7 | 688.3 | 543 | 675.5 | 187.7 | 290.4 | 294.5 | 257.7 | 230.9 | 291 | 280.9 | 240.3
576 | 431 | 469.9 | 187.96 | 219.7144 | 277.8 | 254.8 | 271.6 | 273.5 | 410.6 | 36.2 | 20.6 | 73.3 | 8.7 | 259.1 | 9.5 | 826.3 | 774.8 | 633.5 | 818.4 | 652.7 | 640.7 | 578.8 | 680 | 543.5 | 674 | 188 | 290.9 | 294.4 | 257.9 | 231.9 | 290.4 | 280.9 | 240.5
577 | 432 | 468 | 187.2 | 218.826 | 277.1 | 254.3 | 271.6 | 273.3 | 408.6 | 36.4 | 20.6 | 73.4 | 11.9 | 244.1 | 13.1 | 827.9 | 770.1 | 621 | 820.2 | 649.9 | 642.1 | 578.4 | 667.1 | 543.8 | 672 | 188.3 | 291.1 | 294.4 | 258.4 | 232.8 | 289.9 | 280.9 | 240.8
578 | 433 | 468.9 | 187.56 | 219.2468 | 277.7 | 253.4 | 271.4 | 272.9 | 408.6 | 36.4 | 20.6 | 73.4 | 10.1 | 248.5 | 16.6 | 828.8 | 765.1 | 614.3 | 822.2 | 647.9 | 643.5 | 578.2 | 660.7 | 544.7 | 670.8 | 188.5 | 290.9 | 294.2 | 258.5 | 233.5 | 289.7 | 281.1 | 241.1
579 | 434 | 469.7 | 187.88 | 219.6209 | 279 | 252.5 | 271.8 | 271.9 | 407.6 | 36.4 | 20.6 | 73.5 | 8.9 | 252.7 | 18.2 | 829.2 | 762 | 602.4 | 824 | 645.7 | 645.3 | 580.5 | 650.4 | 545.1 | 669.5 | 188.8 | 290.7 | 294.1 | 258.5 | 234.4 | 289.3 | 281.5 | 241.4
580 | 435 | 468.5 | 187.4 | 219.0598 | 280.5 | 251.5 | 271.3 | 271.6 | 405.8 | 36.6 | 20.6 | 73.6 | 9.7 | 250.4 | 18.7 | 829.9 | 761.4 | 593.1 | 825.8 | 644.3 | 647.3 | 584.9 | 646.2 | 545.3 | 669 | 189.1 | 290.3 | 294 | 258.5 | 235.4 | 289.6 | 282 | 241.8
581 | 436 | 467.3 | 186.92 | 218.4987 | 279.6 | 249.9 | 270.8 | 271.9 | 407.1 | 36.6 | 20.6 | 73.7 | 7.8 | 252.7 | 19.1 | 830.8 | 764.6 | 604.1 | 828.2 | 645.9 | 648.6 | 588.4 | 648.6 | 546.4 | 669.3 | 189.3 | 289.9 | 294 | 258.5 | 236.3 | 289.9 | 282.3 | 242.1
582 | 437 | 467.8 | 187.12 | 218.7325 | 278.7 | 248.6 | 270.9 | 272.4 | 409.8 | 36.6 | 20.6 | 73.8 | 7.4 | 241.9 | 18.8 | 828.7 | 765.5 | 607.2 | 828.1 | 645.5 | 649.9 | 590 | 652.3 | 547.7 | 669.4 | 189.6 | 289.6 | 294 | 258.5 | 237.2 | 290.1 | 282.5 | 242.4
583 | 438 | 468.6 | 187.44 | 219.1066 | 280.4 | 247.5 | 270.7 | 272.3 | 409.6 | 36.6 | 20.6 | 73.9 | 8.8 | 247 | 18.1 | 829.2 | 764.5 | 603.8 | 828.1 | 644.6 | 651.1 | 591.1 | 650.4 | 549.5 | 668.5 | 189.8 | 289.5 | 293.8 | 258.6 | 238 | 290.8 | 282.6 | 242.6
584 | 439 | 468.9 | 187.56 | 219.2468 | 280.6 | 246.4 | 270.4 | 273.1 | 408.7 | 36.7 | 20.6 | 73.9 | 6.3 | 243.4 | 18.2 | 830.6 | 761.5 | 596.6 | 828.5 | 642.4 | 652.2 | 589.8 | 643.3 | 551.1 | 666.9 | 190.1 | 289.4 | 293.6 | 259.1 | 238.9 | 291.5 | 282.9 | 242.9
585 | 440 | 469 | 187.6 | 219.2936 | 280.5 | 245.7 | 270.3 | 272.8 | 407.1 | 36.8 | 20.6 | 73.9 | 6.9 | 245.3 | 17.1 | 833 | 759.5 | 596.3 | 830.6 | 641.2 | 653.3 | 589.8 | 638.6 | 551.5 | 665.1 | 190.4 | 289.2 | 293.4 | 259.3 | 239.8 | 291.9 | 283.1 | 243.1
586 | 441 | 468.9 | 187.56 | 219.2468 | 278.9 | 245.1 | 270.4 | 272.7 | 406.7 | 37 | 20.6 | 73.8 | 6.2 | 253.3 | 16 | 834.4 | 756.7 | 600 | 833.6 | 639.5 | 655 | 589.4 | 636.2 | 552.6 | 664.8 | 190.6 | 289 | 293.5 | 259.3 | 240.6 | 292.4 | 283.5 | 243.5
587 | 442 | 469.6 | 187.84 | 219.5741 | 279.2 | 244.9 | 270.6 | 273.4 | 405.3 | 37 | 20.6 | 73.8 | 6.9 | 251.9 | 16.1 | 835.5 | 755.1 | 589.5 | 836.5 | 637.8 | 656.5 | 589.5 | 635.9 | 554.7 | 664.4 | 190.9 | 289 | 293.3 | 259.5 | 241.6 | 293.6 | 284 | 244
588 | 443 | 468.5 | 187.4 | 219.0598 | 280.6 | 244.7 | 271.1 | 273.6 | 406.2 | 37 | 20.6 | 73.9 | 8 | 248.6 | 17.6 | 837.3 | 752.7 | 570.4 | 839.1 | 635.1 | 657.6 | 587.3 | 623.9 | 555.1 | 662.6 | 191.1 | 288.8 | 293.1 | 259.5 | 242.7 | 293.9 | 284.4 | 244.3
589 | 444 | 468.6 | 187.44 | 219.1066 | 282.1 | 245.4 | 271 | 274.1 | 405 | 36.9 | 20.6 | 74 | 7.8 | 253 | 18.6 | 837.5 | 752.2 | 566 | 841 | 633.7 | 658.4 | 585.4 | 615.6 | 555.7 | 660.7 | 191.4 | 288.7 | 293.3 | 259.6 | 243.6 | 294.2 | 284.8 | 244.7
590 | 445 | 468.8 | 187.52 | 219.2001 | 283.1 | 246.2 | 271.2 | 274.8 | 404.5 | 36.9 | 20.6 | 74.2 | 7.3 | 245 | 19.6 | 837 | 751 | 577.9 | 842.5 | 634 | 659.7 | 583.5 | 616.2 | 557 | 659.5 | 191.6 | 289 | 293.8 | 259.7 | 244.4 | 294.8 | 285.1 | 245
591 | 446 | 468.8 | 187.52 | 219.2001 | 283.7 | 247 | 271.5 | 276.1 | 405.6 | 37 | 20.6 | 74.3 | 7.7 | 250.9 | 18.8 | 836.6 | 748.3 | 566.4 | 843.8 | 631.7 | 660.7 | 592.3 | 622.5 | 559 | 658.9 | 191.8 | 289.3 | 294.1 | 260 | 245.2 | 295.2 | 285.5 | 245.5
592 | 447 | 468 | 187.2 | 218.826 | 283.8 | 247.9 | 272.3 | 276.6 | 410.5 | 37.2 | 20.6 | 74.4 | 6.8 | 248.2 | 19.4 | 834.1 | 749.1 | 574.4 | 843.9 | 632.5 | 662 | 594.7 | 629.6 | 560.5 | 658.6 | 192 | 289.2 | 294.4 | 260.2 | 246 | 295.7 | 286 | 245.9
593 | 448 | 469 | 187.6 | 219.2936 | 284.6 | 248.9 | 273.8 | 276.7 | 414.7 | 37.3 | 20.6 | 74.6 | 6.7 | 243.8 | 17.9 | 832 | 750.2 | 604 | 843.5 | 634.7 | 663.1 | 593.7 | 641.9 | 562.5 | 658.7 | 192.3 | 289.1 | 294.7 | 260.5 | 247.1 | 296.1 | 286.4 | 246.2
594 | 449 | 468.3 | 187.32 | 218.9663 | 282.1 | 250.1 | 274.8 | 277.8 | 418.3 | 37.5 | 20.6 | 74.8 | 5.7 | 248 | 17.1 | 830.7 | 751.8 | 624.6 | 842.3 | 637.8 | 664.5 | 592.8 | 644.1 | 564.1 | 658.8 | 192.5 | 289.3 | 295 | 260.8 | 248 | 296.6 | 286.9 | 246.6
595 | 450 | 468.9 | 187.56 | 219.2468 | 284.9 | 250.9 | 275.7 | 278.3 | 416.8 | 37.7 | 20.6 | 74.9 | 5.7 | 234.7 | 18.2 | 831.9 | 752 | 632.3 | 841.9 | 638.8 | 665.8 | 590.6 | 645.7 | 566 | 658.7 | 192.7 | 289.6 | 295.4 | 261.1 | 248.9 | 297.2 | 287.3 | 246.9
596 | 451 | 468.6 | 187.44 | 219.1066 | 285.3 | 251.2 | 276.2 | 278.7 | 415.6 | 37.9 | 20.6 | 75.1 | 6.3 | 243.5 | 16.3 | 833 | 751.8 | 631.1 | 842.3 | 637.4 | 666.7 | 588.7 | 642.7 | 567.3 | 658.3 | 193 | 289.8 | 296 | 261.3 | 249.9 | 298 | 287.7 | 247.3
597 | 452 | 469.5 | 187.8 | 219.5274 | 284.6 | 252.4 | 276.9 | 278.5 | 414.9 | 38 | 20.6 | 75.3 | 5.4 | 248.6 | 17.2 | 834.2 | 752.8 | 636.2 | 842.6 | 637.8 | 667.2 | 586.3 | 637.3 | 568.2 | 657.8 | 193.2 | 289.8 | 296.5 | 261.4 | 250.8 | 298.4 | 288.1 | 247.7
598 | 453 | 469.1 | 187.64 | 219.3403 | 283.8 | 253.7 | 276.7 | 278.3 | 412.4 | 38.2 | 20.6 | 75.3 | 5.3 | 253.8 | 17.3 | 836.1 | 751.5 | 622.6 | 843.6 | 636.5 | 667.9 | 583.2 | 630.4 | 569.1 | 657.5 | 193.5 | 289.6 | 296.7 | 261.5 | 251.8 | 298.1 | 288.6 | 248.1
599 | 454 | 470.1 | 188.04 | 219.8079 | 281.4 | 253.5 | 276.8 | 278.8 | 409.3 | 38.1 | 20.6 | 75.4 | 6.6 | 258.3 | 16.8 | 836.8 | 754.6 | 627.2 | 845.5 | 635.3 | 668.9 | 582.9 | 635.3 | 570.9 | 657.1 | 193.7 | 289.7 | 296.7 | 261.8 | 252.6 | 297.9 | 289 | 248.5
600 | 455 | 469.3 | 187.72 | 219.4339 | 281.2 | 253.3 | 276.9 | 278.8 | 408.3 | 38.2 | 20.5 | 75.4 | 7.5 | 261.2 | 15.5 | 837.4 | 758.4 | 639.8 | 846.4 | 636.5 | 669.6 | 583.9 | 641.3 | 572.1 | 657.4 | 193.9 | 289.7 | 296.7 | 262 | 253.4 | 297.7 | 289.4 | 248.8
601 | 456 | 469.9 | 187.96 | 219.7144 | 282.9 | 252.9 | 277.2 | 277.9 | 408 | 38.3 | 20.5 | 75.5 | 8.8 | 259.2 | 16.7 | 838.1 | 761.3 | 675.8 | 846.6 | 641.1 | 669.8 | 583.6 | 659.2 | 573.8 | 657.9 | 194.1 | 289.8 | 296.5 | 262.4 | 254.1 | 297.5 | 289.5 | 249.1
602 | 457 | 469.7 | 187.88 | 219.6209 | 281.5 | 252.1 | 277 | 277.4 | 408.7 | 38.4 | 20.6 | 75.6 | 9.2 | 267.7 | 18.2 | 840.1 | 763.3 | 670.4 | 846.5 | 641.4 | 669.7 | 582.6 | 668.8 | 575.6 | 658.9 | 194.3 | 290 | 296.2 | 262.9 | 254.8 | 297.4 | 289.7 | 249.2
603 | 458 | 469.7 | 187.88 | 219.6209 | 282.3 | 252.2 | 276.2 | 277.1 | 410.8 | 38.7 | 20.5 | 75.7 | 7.3 | 278.6 | 17.5 | 841.3 | 760.2 | 643.5 | 845.8 | 639 | 669.2 | 579.3 | 657.7 | 575.4 | 657 | 194.5 | 289.9 | 295.9 | 263.2 | 255.6 | 297.5 | 289.4 | 249.5
604 | 459 | 469.6 | 187.84 | 219.5741 | 282.8 | 252.2 | 275.4 | 278 | 408.8 | 38.9 | 20.5 | 75.6 | 5.3 | 273.2 | 15 | 841.8 | 756.7 | 617.3 | 845.1 | 635.9 | 669.3 | 575.6 | 647.1 | 573.7 | 655.6 | 194.7 | 289.6 | 295.5 | 263.1 | 256.3 | 297.4 | 289.5 | 249.8
605 | 460 | 469.2 | 187.68 | 219.3871 | 281.4 | 252.4 | 274.9 | 277.7 | 404.7 | 39 | 20.5 | 75.6 | 6.3 | 258.3 | 14.1 | 841.9 | 755.8 | 612.8 | 844.7 | 634.1 | 670.2 | 572 | 634.9 | 572.1 | 653.9 | 194.9 | 289 | 295.1 | 263 | 257 | 297 | 289.7 | 250.1
606 | 461 | 469.7 | 187.88 | 219.6209 | 280.3 | 252.6 | 274.3 | 278.3 | 402.4 | 39 | 20.5 | 75.6 | 5.5 | 253.6 | 15.6 | 842.7 | 753.3 | 613.5 | 845.5 | 633.8 | 671.5 | 569.5 | 633.6 | 572.5 | 653.5 | 195.1 | 288.6 | 295.5 | 262.9 | 257.8 | 296.4 | 289.9 | 250.5
607 | 462 | 469.6 | 187.84 | 219.5741 | 279.8 | 252.1 | 273.3 | 278.5 | 403.2 | 39.1 | 20.5 | 75.6 | 5.1 | 248.2 | 17.2 | 843 | 750.5 | 605.6 | 846.6 | 632.2 | 672.7 | 569.4 | 629.8 | 572.2 | 653 | 195.3 | 288.3 | 295.5 | 262.8 | 258.5 | 296.2 | 290.2 | 250.8
608 | 463 | 469.6 | 187.84 | 219.5741 | 279.8 | 251.6 | 272.8 | 278.6 | 404.1 | 39.3 | 20.5 | 75.7 | 4.5 | 242.3 | 16.9 | 842.8 | 750.6 | 597.8 | 847 | 631.4 | 673.7 | 568.1 | 627.7 | 572.5 | 652.1 | 195.5 | 288 | 295.5 | 263 | 259.2 | 295.5 | 290 | 251.1
609 | 464 | 469.2 | 187.68 | 219.3871 | 281.3 | 251.7 | 272.4 | 278 | 401.7 | 39.5 | 20.5 | 75.8 | 5.4 | 239.9 | 15.3 | 842.9 | 750.3 | 603.7 | 846.8 | 631 | 674.3 | 566.2 | 629.1 | 573.4 | 650.6 | 195.8 | 287.7 | 295.1 | 263.2 | 259.8 | 295 | 289.9 | 251.3
610 | 465 | 469.7 | 187.88 | 219.6209 | 283.4 | 251.4 | 272.1 | 276.8 | 399.9 | 39.6 | 20.5 | 76 | 6.5 | 238.9 | 14.1 | 843.1 | 751.4 | 627.5 | 846.3 | 632.5 | 674.9 | 565.5 | 631 | 573.8 | 650.8 | 196 | 287.6 | 294.8 | 263.4 | 260.2 | 294.5 | 289.7 | 251.4
611 | 466 | 468.8 | 187.52 | 219.2001 | 285.8 | 251 | 272.3 | 276.7 | 400.3 | 39.7 | 20.5 | 76.1 | 6.4 | 241.4 | 14.9 | 843 | 751.7 | 623.9 | 845.8 | 631.8 | 675.3 | 565.2 | 635 | 574.4 | 650.6 | 196.2 | 287.3 | 294.5 | 263.4 | 260.7 | 294.1 | 289.4 | 251.5
612 | 467 | 468.5 | 187.4 | 219.0598 | 287.1 | 250.8 | 272 | 275.3 | 398.5 | 39.7 | 20.5 | 76.2 | 7.5 | 251.3 | 15.5 | 842.6 | 756.2 | 636.9 | 845 | 632.9 | 675.3 | 566.7 | 652.1 | 575.7 | 651.2 | 196.3 | 287.5 | 294.3 | 263.6 | 261.1 | 293.8 | 289.2 | 251.7
613 | 468 | 465.3 | 186.12 | 217.5636 | 285.9 | 250.3 | 272 | 274.6 | 399.4 | 39.7 | 20.5 | 76.3 | 7 | 247.6 | 16.2 | 842.8 | 756.5 | 662.8 | 843.1 | 635.2 | 674.7 | 567.9 | 667.5 | 577.7 | 651.7 | 196.5 | 287.7 | 294.3 | 264.1 | 261.7 | 293.5 | 288.7 | 251.8
614 | 469 | 468.8 | 187.52 | 219.2001 | 282.5 | 250.1 | 272.3 | 274.4 | 400.8 | 39.7 | 20.5 | 76.4 | 6.5 | 246.8 | 16 | 843.5 | 754.8 | 675 | 841.8 | 638 | 674.2 | 568.5 | 670.9 | 578.9 | 651.8 | 196.7 | 288.3 | 294.5 | 264.5 | 262.1 | 293.4 | 288.4 | 251.9
615 | 470 | 468.6 | 187.44 | 219.1066 | 280.4 | 250.4 | 273.1 | 274.9 | 403.7 | 39.8 | 20.5 | 76.4 | 6 | 262.1 | 15.7 | 845 | 755.5 | 670.8 | 841.9 | 637.7 | 674.1 | 567.9 | 668.4 | 580 | 650.7 | 196.9 | 288.7 | 294.8 | 264.9 | 262.4 | 293.3 | 287.8 | 252
616 | 471 | 468.7 | 187.48 | 219.1533 | 280.7 | 250.4 | 272.9 | 275.2 | 405.1 | 39.8 | 20.5 | 76.4 | 6.3 | 264 | 14.3 | 846.2 | 753.9 | 651.5 | 842 | 635.9 | 674.5 | 566.8 | 659.5 | 579.1 | 650.2 | 197.1 | 288.8 | 295.2 | 265.1 | 262.8 | 293.2 | 287.5 | 252.1
617 | 472 | 468.6 | 187.44 | 219.1066 | 281 | 249.6 | 272.6 | 276.4 | 405.8 | 39.9 | 20.5 | 76.4 | 6.7 | 271 | 13.4 | 846.9 | 754.6 | 651 | 842.6 | 636.2 | 675.1 | 566.4 | 656.1 | 579.3 | 649.9 | 197.2 | 289 | 295.7 | 265.1 | 263.2 | 293.1 | 287.4 | 252.3
618 | 473 | 468.8 | 187.52 | 219.2001 | 278.4 | 249.2 | 273.1 | 277.4 | 404.4 | 39.8 | 20.5 | 76.4 | 8.8 | 270 | 13.4 | 848.2 | 752.5 | 638.7 | 842.8 | 634 | 675.4 | 565.5 | 649.8 | 579 | 649.1 | 197.4 | 289.1 | 296.1 | 265.1 | 263.7 | 292.9 | 287.2 | 252.5
619 | 474 | 469 | 187.6 | 219.2936 | 278 | 249.6 | 274.2 | 277.7 | 401.6 | 39.7 | 20.5 | 76.4 | 7.7 | 259.7 | 14.4 | 848.7 | 752.3 | 618.2 | 844.1 | 632.9 | 676.1 | 565 | 640.2 | 579 | 647.8 | 197.6 | 288.9 | 296.1 | 265.1 | 264.1 | 293.6 | 287.3 | 252.8
620 | 475 | 467.6 | 187.04 | 218.639 | 276.9 | 249.9 | 274.4 | 278 | 400.7 | 39.7 | 20.5 | 76.3 | 5.9 | 266.9 | 14.3 | 848.6 | 750.8 | 615.5 | 844.9 | 631.9 | 676.8 | 564.4 | 634.5 | 579.7 | 646.8 | 197.7 | 288.8 | 295.8 | 265.2 | 264.7 | 293.7 | 287.6 | 253.2
621 | 476 | 469.3 | 187.72 | 219.4339 | 275.3 | 249.7 | 274 | 278.7 | 399.5 | 39.7 | 20.5 | 76.3 | 6 | 272.5 | 15.7 | 848.4 | 753.3 | 631 | 845.2 | 632.9 | 677.7 | 564.1 | 638.9 | 580.2 | 646.5 | 197.9 | 288.6 | 295.6 | 265.3 | 265.2 | 293.5 | 287.7 | 253.4
622 | 477 | 469.2 | 187.68 | 219.3871 | 275.8 | 249.3 | 273.3 | 279 | 400.9 | 39.8 | 20.5 | 76.4 | 6.3 | 262.8 | 14.3 | 848 | 754.5 | 626 | 844.6 | 633.6 | 677.9 | 564.2 | 638.6 | 581.1 | 647 | 198.1 | 288.7 | 295.4 | 265.6 | 265.7 | 293.5 | 287.8 | 253.7
623 | 478 | 469.2 | 187.68 | 219.3871 | 277.2 | 248.7 | 273.5 | 278.8 | 403 | 39.9 | 20.5 | 76.6 | 5.8 | 257.5 | 14.7 | 847 | 755.5 | 639.6 | 845.7 | 637.1 | 678.6 | 566 | 637.9 | 582.3 | 646.4 | 198.3 | 288.7 | 295.5 | 265.7 | 266.2 | 293.9 | 288.1 | 253.9
624 | 479 | 469.1 | 187.64 | 219.3403 | 279.4 | 248.5 | 273.5 | 278.8 | 405.2 | 39.9 | 20.5 | 76.8 | 4.6 | 244.3 | 14.6 | 846.9 | 762.1 | 664.5 | 847.1 | 644.1 | 679.3 | 571.3 | 650.6 | 584.1 | 648.7 | 198.5 | 288.6 | 295.4 | 265.8 | 266.7 | 294.4 | 288.5 | 254.1
625 | 480 | 469.6 | 187.84 | 219.5741 | 280.3 | 249.3 | 274 | 279.1 | 409.8 | 40 | 20.5 | 77.1 | 4.8 | 242.7 | 14.9 | 847.5 | 766.9 | 679 | 846.9 | 646.1 | 679.7 | 572.9 | 667.3 | 586.8 | 649.9 | 198.7 | 288.6 | 295.2 | 266 | 267.2 | 294.6 | 288.5 | 254.3
626 | 481 | 469.7 | 187.88 | 219.6209 | 281.4 | 250 | 274.7 | 278.6 | 409.9 | 39.9 | 20.5 | 77.3 | 5.9 | 250.9 | 14.5 | 848.4 | 767.2 | 681.8 | 847.1 | 646.2 | 680.4 | 574.3 | 667.4 | 589 | 650 | 198.9 | 288.4 | 295.4 | 266.1 | 267.6 | 294.5 | 288.4 | 254.4
627 | 482 | 469.3 | 187.72 | 219.4339 | 281.8 | 250.9 | 275.1 | 277.9 | 409.5 | 40 | 20.5 | 77.4 | 6.8 | 267.7 | 14 | 848.4 | 768.2 | 698.2 | 847.4 | 649.4 | 681.5 | 578 | 675.1 | 590.9 | 650.7 | 199.1 | 288.4 | 295.7 | 266.3 | 268 | 294.6 | 288.4 | 254.6
628 | 483 | 468.7 | 187.48 | 219.1533 | 279.9 | 250.6 | 275.3 | 278 | 410.7 | 40 | 20.5 | 77.4 | 7.1 | 268.2 | 16.4 | 848.7 | 767.4 | 697.9 | 847 | 648.6 | 682 | 579.1 | 678.7 | 592.5 | 650.8 | 199.3 | 288.6 | 295.8 | 266.5 | 268.3 | 295 | 288.4 | 254.9
629 | 484 | 469.2 | 187.68 | 219.3871 | 277.8 | 250.1 | 276.1 | 278.4 | 411.5 | 40 | 20.5 | 77.4 | 7.1 | 261.7 | 17.5 | 849 | 769.4 | 702.1 | 847.9 | 650.6 | 682.4 | 580.3 | 682 | 594 | 651 | 199.5 | 288.8 | 295.8 | 266.7 | 268.8 | 295.9 | 288.7 | 255.2
630 | 485 | 469.4 | 187.76 | 219.4806 | 276.9 | 250.4 | 276.3 | 279.4 | 411.3 | 40.1 | 20.5 | 77.3 | 8.1 | 249.4 | 17.8 | 848.4 | 773.6 | 723.3 | 848.1 | 656.1 | 683 | 583.2 | 686 | 595.5 | 653.4 | 199.7 | 288.9 | 295.7 | 266.9 | 269.3 | 296.3 | 289 | 255.5
631 | 486 | 469.4 | 187.76 | 219.4806 | 279.4 | 250.5 | 275.8 | 280.2 | 412.2 | 40.1 | 20.5 | 77.2 | 10.1 | 250.3 | 16.4 | 848.7 | 773.1 | 722.1 | 847.5 | 656.6 | 683.3 | 585.4 | 698.2 | 597.3 | 655.5 | 200 | 289.1 | 295.7 | 267.3 | 269.7 | 296.5 | 289 | 255.8
632 | 487 | 469.3 | 187.72 | 219.4339 | 281.9 | 250.7 | 275 | 280.5 | 414.2 | 40.3 | 20.5 | 77.2 | 10.7 | 272.2 | 14.1 | 850 | 771.1 | 718.7 | 847.1 | 656.3 | 683.6 | 583.8 | 692.1 | 598.6 | 653.9 | 200.2 | 289.6 | 295.9 | 267.7 | 270 | 296.6 | 288.9 | 255.9
633 | 488 | 468.1 | 187.24 | 218.8728 | 284.6 | 251.4 | 275.6 | 280.7 | 412.5 | 40.4 | 20.5 | 77.2 | 10.5 | 257.4 | 14.1 | 851.5 | 768.2 | 709.6 | 847.5 | 655.6 | 684.6 | 580.3 | 685.6 | 598.9 | 653.2 | 200.4 | 290 | 296.1 | 268 | 270.3 | 296.9 | 288.9 | 256
634 | 489 | 466 | 186.4 | 217.8909 | 284.5 | 252.3 | 276.4 | 280.6 | 410.7 | 40.5 | 20.5 | 77.1 | 8.2 | 240.6 | 17.2 | 852.8 | 768.2 | 685.7 | 848 | 654 | 685.3 | 578.2 | 674.7 | 598.7 | 652.8 | 200.6 | 290.2 | 296.4 | 268 | 270.5 | 296.8 | 288.9 | 256.3
635 | 490 | 469.2 | 187.68 | 219.3871 | 280.8 | 253.4 | 276.4 | 281.2 | 408.3 | 40.6 | 20.5 | 77.1 | 8.5 | 248.7 | 19.3 | 853.6 | 764.4 | 668.3 | 848 | 651.9 | 686.1 | 575.7 | 666.7 | 598 | 651.5 | 200.8 | 290.5 | 296.6 | 268.1 | 270.9 | 297.1 | 289 | 256.5
636 | 491 | 470.3 | 188.12 | 219.9014 | 277.7 | 253.6 | 276.2 | 281.3 | 405 | 40.6 | 20.5 | 77.1 | 8.5 | 256.7 | 20 | 854.3 | 759.9 | 658.6 | 848.5 | 649.5 | 686.9 | 572.7 | 656.3 | 597.1 | 649.9 | 201 | 290.7 | 296.6 | 268.4 | 271.3 | 296.6 | 289 | 256.7
637 | 492 | 468.6 | 187.44 | 219.1066 | 276.7 | 253.5 | 276.1 | 280.9 | 404 | 40.5 | 20.5 | 77 | 7.3 | 257.1 | 18.8 | 854.4 | 758.4 | 642.5 | 849.2 | 648.6 | 687.9 | 571.3 | 648 | 596.2 | 648.8 | 201.2 | 290.4 | 296.1 | 268.6 | 271.5 | 296.3 | 289 | 256.9
638 | 493 | 468.8 | 187.52 | 219.2001 | 278.5 | 253.8 | 275 | 280.2 | 403.3 | 40.4 | 20.5 | 77 | 6.8 | 257.5 | 15.8 | 853.8 | 755.3 | 625.9 | 849.3 | 645.2 | 689.8 | 572.2 | 636.1 | 595.3 | 647.5 | 201.4 | 289.5 | 295.5 | 268.5 | 271.8 | 296 | 289 | 257.1
639 | 494 | 470.2 | 188.08 | 219.8547 | 280.3 | 254.6 | 273.4 | 279.3 | 401.7 | 40.3 | 20.5 | 77 | 7.4 | 269.5 | 17.1 | 853.2 | 754.8 | 627.6 | 849.1 | 644.9 | 691 | 573.9 | 631.6 | 594.7 | 646.7 | 201.6 | 289 | 294.5 | 268.5 | 272 | 295.9 | 288.8 | 257.3
640 | 495 | 469 | 187.6 | 219.2936 | 281 | 254.4 | 272.2 | 278.5 | 402 | 40.2 | 20.5 | 77.2 | 8.1 | 267.3 | 18.6 | 852.8 | 755.7 | 636.9 | 849 | 645.1 | 692 | 571.9 | 626.1 | 595.3 | 646.3 | 201.8 | 288.5 | 293.9 | 268.4 | 272.2 | 296.3 | 289 | 257.5
641 | 496 | 468 | 187.2 | 218.826 | 281.6 | 253.5 | 271.5 | 277.9 | 404 | 40.4 | 20.4 | 77.4 | 10 | 259.7 | 20.8 | 851.7 | 756.7 | 639.1 | 849.3 | 646.3 | 692.5 | 571.1 | 622.3 | 596.5 | 646.6 | 202 | 288.1 | 293.6 | 268.2 | 272.4 | 296.7 | 289.3 | 257.7
642 | 497 | 469.4 | 187.76 | 219.4806 | 280.8 | 252.9 | 270.8 | 277.9 | 409.7 | 40.5 | 20.4 | 77.8 | 12.3 | 266 | 19.6 | 850.8 | 757.9 | 649.2 | 849.3 | 648.3 | 693.3 | 575.1 | 626.9 | 597.8 | 647.1 | 202.2 | 288.2 | 293.7 | 268.2 | 272.7 | 297.4 | 289.6 | 258
643 | 498 | 470.1 | 188.04 | 219.8079 | 282 | 253.5 | 271.6 | 279.1 | 422.7 | 40.4 | 20.4 | 78.1 | 11.3 | 263.3 | 19.1 | 850.6 | 757.1 | 639.2 | 848.4 | 648.5 | 693.6 | 575.8 | 624.6 | 598.5 | 646.7 | 202.4 | 288.1 | 294.2 | 268.4 | 273 | 298.3 | 290 | 258.3
644 | 499 | 466.7 | 186.68 | 218.2182 | 281.8 | 254 | 273.2 | 279.7 | 423.3 | 40.3 | 20.4 | 78.2 | 9.4 | 266 | 18 | 849.8 | 752.7 | 624.9 | 847.4 | 646.1 | 694.6 | 574.8 | 614.2 | 597.8 | 645 | 202.6 | 288.2 | 294.6 | 268.6 | 273.2 | 298.9 | 290.1 | 258.6
645 | 500 | 467.4 | 186.96 | 218.5455 | 282.4 | 255.2 | 275.3 | 280.9 | 423.2 | 40.4 | 20.4 | 78.1 | 7.8 | 255.6 | 15.4 | 849.6 | 748.8 | 608.2 | 846.9 | 643.9 | 695.7 | 583.5 | 610.8 | 597.4 | 643.5 | 202.8 | 288.3 | 295.3 | 268.7 | 273.6 | 300.1 | 290.5 | 258.9
646 | 501 | 468.1 | 187.24 | 218.8728 | 281 | 256 | 276.3 | 281 | 419.7 | 40.6 | 20.4 | 78.1 | 7.4 | 255.6 | 16.1 | 849.4 | 747.5 | 601.6 | 846.4 | 642.2 | 696.2 | 579.9 | 607.8 | 596.8 | 642 | 203 | 288.5 | 295.9 | 268.9 | 274.2 | 300.8 | 291.3 | 259.3
647 | 502 | 467.8 | 187.12 | 218.7325 | 280.1 | 256.8 | 276.6 | 281.3 | 416.6 | 40.8 | 20.4 | 78 | 6.1 | 244.8 | 16.1 | 850.6 | 750.7 | 626.3 | 846.9 | 644.2 | 696.2 | 577.6 | 616.5 | 597.6 | 642.4 | 203.2 | 288.8 | 296.6 | 269.2 | 274.5 | 300.7 | 291.5 | 259.5
648 | 503 | 467.6 | 187.04 | 218.639 | 282.9 | 256.5 | 276.9 | 280.2 | 416.9 | 40.9 | 20.4 | 78 | 6.1 | 257 | 15.5 | 852.2 | 757.5 | 656.5 | 847.5 | 649.2 | 695.7 | 578.7 | 641.4 | 599.7 | 645.1 | 203.4 | 289.3 | 297.1 | 269.6 | 274.6 | 300.2 | 291.6 | 259.7
649 | 504 | 469.2 | 187.68 | 219.3871 | 282.4 | 256.4 | 277.8 | 279.5 | 417.6 | 40.9 | 20.4 | 78.1 | 7 | 268 | 15.5 | 851.6 | 754 | 635 | 846.2 | 646.4 | 695.6 | 577.2 | 638.2 | 600.5 | 643.7 | 203.7 | 289.6 | 297.2 | 269.9 | 274.7 | 299.7 | 291.7 | 259.9
650 | 505 | 469.9 | 187.96 | 219.7144 | 280.9 | 256.7 | 277.6 | 278.1 | 417.8 | 41 | 20.4 | 78.3 | 7 | 268.5 | 12.8 | 850.2 | 750.2 | 626.4 | 846 | 644.2 | 696 | 579 | 624.2 | 599.4 | 641.6 | 203.9 | 289.6 | 297.2 | 270 | 274.7 | 299.5 | 291.5 | 260.1
651 | 506 | 469.6 | 187.84 | 219.5741 | 280.3 | 256.8 | 276.8 | 278.2 | 418.5 | 40.9 | 20.4 | 78.3 | 8 | 272.4 | 11.9 | 849.7 | 749.5 | 622.4 | 846.3 | 643.6 | 696.4 | 579.3 | 621.7 | 599.1 | 641.1 | 204.1 | 289.5 | 297 | 270 | 274.8 | 299.2 | 291.5 | 260.2
652 | 507 | 468.6 | 187.44 | 219.1066 | 282.2 | 255.9 | 276 | 278.7 | 416.3 | 40.8 | 20.4 | 78.4 | 8.2 | 266.6 | 12.2 | 848.5 | 746.5 | 601.1 | 846.3 | 640.3 | 696.7 | 579.1 | 609.8 | 598.7 | 639.4 | 204.4 | 289.3 | 296.7 | 270 | 274.9 | 299 | 291.4 | 260.3
653 | 508 | 469.1 | 187.64 | 219.3403 | 282.8 | 255.4 | 274.6 | 278.8 | 413.7 | 40.8 | 20.4 | 78.5 | 9.3 | 259.1 | 11.4 | 847.7 | 743.6 | 586.3 | 846.2 | 638.1 | 697.7 | 576.3 | 604.9 | 598.6 | 638.2 | 204.6 | 289.1 | 296.2 | 269.9 | 275.2 | 300.1 | 291.4 | 260.6
654 | 509 | 469.2 | 187.68 | 219.3871 | 282.8 | 254.6 | 273.3 | 278.3 | 412.5 | 40.8 | 20.4 | 78.6 | 10.3 | 278.6 | 12.9 | 846.6 | 739.8 | 569.2 | 846.2 | 635.7 | 698.8 | 576.2 | 596.7 | 597.9 | 636.8 | 204.8 | 288.7 | 295.6 | 270 | 275.5 | 300.2 | 291.5 | 260.9
655 | 510 | 469.3 | 187.72 | 219.4339 | 282.6 | 254.3 | 273 | 279.1 | 412 | 40.7 | 20.4 | 78.7 | 12.3 | 246 | 13.1 | 846 | 736.8 | 568.2 | 846.1 | 634.8 | 699.5 | 573.4 | 592.2 | 598.1 | 635.3 | 205.1 | 288.4 | 295.3 | 270.1 | 275.6 | 300.5 | 291.5 | 261
656 | 511 | 469.1 | 187.64 | 219.3403 | 281.9 | 253.7 | 272.3 | 279.7 | 411.7 | 40.9 | 20.4 | 78.9 | 10.6 | 249.1 | 12.6 | 846.1 | 737.7 | 576.5 | 846.3 | 633.3 | 699.5 | 571.8 | 600.5 | 598.7 | 634.9 | 205.5 | 288.3 | 295.2 | 270.4 | 275.6 | 300.1 | 291.7 | 261.2
657 | 512 | 470.5 | 188.2 | 219.995 | 280.5 | 252.8 | 272.7 | 279.2 | 417.3 | 41.1 | 20.4 | 79.1 | 10.6 | 251.4 | 13.8 | 845.2 | 732.7 | 575.4 | 845 | 630.8 | 698.7 | 570.3 | 605.4 | 599.8 | 634.3 | 206 | 288.7 | 295.2 | 271.1 | 275.6 | 299.9 | 291.6 | 261.3
658 | 513 | 470.9 | 188.36 | 220.182 | 279.6 | 253 | 274 | 278.5 | 424.2 | 41.2 | 20.4 | 79.3 | 7.1 | 249.3 | 13.2 | 844.5 | 729.9 | 576.3 | 844.2 | 629.1 | 698.1 | 579.8 | 603.5 | 599.8 | 633.1 | 206.5 | 289.5 | 295.7 | 271.7 | 275.7 | 299.5 | 291.4 | 261.4
659 | 514 | 470.3 | 188.12 | 219.9014 | 279.1 | 254.4 | 275.9 | 277.9 | 448.4 | 41.4 | 20.4 | 79.4 | 6.3 | 242.4 | 16.4 | 843.7 | 728.2 | 562.4 | 843 | 626.2 | 697.6 | 577.3 | 599.3 | 599.9 | 632 | 207 | 290.9 | 296.6 | 272 | 275.7 | 299.3 | 291.1 | 261.5
660 | 515 | 468.6 | 187.44 | 219.1066 | 278.7 | 255.1 | 277.4 | 278.3 | 454.6 | 41.5 | 20.4 | 79.5 | 7.3 | 247.5 | 17.2 | 842.6 | 727.9 | 550.3 | 841.6 | 624.2 | 697.6 | 572.6 | 592.5 | 599.8 | 630.1 | 207.4 | 291.6 | 297.5 | 272.3 | 275.7 | 299 | 290.6 | 261.6
661 | 516 | 468.4 | 187.36 | 219.013 | 277.5 | 255.9 | 278.4 | 279.5 | 451.1 | 41.4 | 20.4 | 79.7 | 7.7 | 241.8 | 16.4 | 841.2 | 727.2 | 546.2 | 840.5 | 621.4 | 697.3 | 569.5 | 593.4 | 599.7 | 628.6 | 207.8 | 292 | 298.1 | 272.7 | 275.8 | 299.3 | 290.4 | 261.7
662 | 517 | 469.2 | 187.68 | 219.3871 | 276.4 | 256.4 | 279.3 | 280.3 | 448.7 | 41.2 | 20.4 | 79.9 | 6.9 | 253.8 | 14.8 | 839.8 | 725.6 | 536.9 | 839.9 | 619 | 696.7 | 573.4 | 586.1 | 599.3 | 627.1 | 208.2 | 292.8 | 298.9 | 272.9 | 275.9 | 299.6 | 290.4 | 261.9
663 | 518 | 469.4 | 187.76 | 219.4806 | 274.9 | 256.7 | 279.9 | 281.4 | 447.2 | 41.3 | 20.4 | 80 | 7.1 | 254.1 | 13.7 | 838.7 | 725.6 | 529.1 | 839.9 | 617.2 | 697 | 576.7 | 579.2 | 599.1 | 626.3 | 208.5 | 293.3 | 299.6 | 273.1 | 276 | 299.4 | 290.8 | 262.2
664 | 519 | 469.4 | 187.76 | 219.4806 | 275.4 | 256.8 | 279.8 | 281.5 | 443.5 | 41.4 | 20.4 | 80.2 | 7.8 | 263.2 | 15.2 | 837.5 | 724.6 | 521.5 | 839.5 | 615.7 | 697.7 | 576.2 | 571 | 598.9 | 625 | 208.9 | 293.8 | 300.2 | 273 | 276.1 | 299.2 | 290.7 | 262.4
665 | 520 | 468.2 | 187.28 | 218.9195 | 277.5 | 257.2 | 280.4 | 280.2 | 439.2 | 41.3 | 20.4 | 80.2 | 8.6 | 256.5 | 15 | 837.4 | 727.4 | 525.1 | 839 | 615 | 698 | 592.6 | 576 | 599 | 623.8 | 209.3 | 293.9 | 300.3 | 273.3 | 276.1 | 299.1 | 290.5 | 262.5
666 | 521 | 469.8 | 187.92 | 219.6677 | 277 | 257.6 | 281.4 | 279.9 | 444.3 | 41.4 | 20.4 | 80.2 | 8.4 | 250.9 | 13.1 | 837.3 | 727.5 | 526.1 | 838.4 | 613.6 | 697.7 | 588 | 581 | 599.6 | 623.1 | 209.7 | 294.2 | 300.3 | 273.5 | 276.2 | 298.8 | 290.5 | 262.7
667 | 522 | 468.6 | 187.44 | 219.1066 | 277.2 | 258.2 | 281.5 | 280.7 | 446.1 | 41.5 | 20.4 | 80.2 | 9.4 | 233.5 | 13.4 | 836.7 | 728.3 | 531.3 | 837.9 | 612.5 | 697.5 | 587.5 | 589.5 | 600.6 | 622.6 | 210 | 294.5 | 300.4 | 273.8 | 276.2 | 298.5 | 290.3 | 262.8
668 | 523 | 469.3 | 187.72 | 219.4339 | 278.1 | 258.9 | 280.7 | 281.6 | 443.8 | 41.6 | 20.4 | 80.1 | 9.5 | 247.4 | 12.8 | 836.2 | 729 | 547.7 | 836.1 | 611.9 | 697.6 | 585.6 | 587.3 | 601.9 | 621.9 | 210.2 | 294.4 | 300.3 | 273.9 | 276.2 | 298.2 | 290.4 | 262.9
669 | 524 | 468.9 | 187.56 | 219.2468 | 277.1 | 259.4 | 280.2 | 282.2 | 439.9 | 41.6 | 20.4 | 80.1 | 6.5 | 235.3 | 14.1 | 836.3 | 730.7 | 555.3 | 834.6 | 612.1 | 698 | 582.4 | 590.6 | 603.8 | 621.5 | 210.4 | 294.3 | 300.3 | 273.8 | 276.3 | 298 | 290.4 | 263.2
670 | 525 | 469.9 | 187.96 | 219.7144 | 276.5 | 260.3 | 280.5 | 283.1 | 436.9 | 41.6 | 20.4 | 80 | 6.2 | 253.7 | 12.9 | 836.2 | 730.7 | 556 | 833.2 | 611.7 | 698.1 | 579.3 | 587.5 | 605.1 | 621.2 | 210.6 | 294.4 | 300.4 | 274 | 276.3 | 298.2 | 290.2 | 263.3
671 | 526 | 469.3 | 187.72 | 219.4339 | 277.1 | 260.1 | 280.3 | 282.8 | 434.8 | 41.6 | 20.4 | 80 | 8.6 | 259.3 | 11.3 | 836 | 729.8 | 559.4 | 832.2 | 612.2 | 698.5 | 574 | 582.4 | 605.1 | 620.1 | 210.8 | 294.1 | 300.3 | 273.9 | 276.4 | 298.2 | 290.1 | 263.4
672 | 527 | 468.9 | 187.56 | 219.2468 | 280.6 | 260.6 | 279.1 | 282.8 | 432.5 | 41.5 | 20.4 | 80 | 8.5 | 251.5 | 14.8 | 836.2 | 732.3 | 550.5 | 831.8 | 612.2 | 698.6 | 579.9 | 586.6 | 605.6 | 619.9 | 210.9 | 293.7 | 299.9 | 273.9 | 276.5 | 297.8 | 290.4 | 263.6
673 | 528 | 468.6 | 187.44 | 219.1066 | 283 | 261 | 277.6 | 283.1 | 431.9 | 41.4 | 20.4 | 79.9 | 9.2 | 242.7 | 14.9 | 835.8 | 733.6 | 549.2 | 831 | 611.7 | 698.7 | 578 | 588.7 | 606 | 619.5 | 211.1 | 293.5 | 299.9 | 273.9 | 276.6 | 297.5 | 290.5 | 263.8
674 | 529 | 469.8 | 187.92 | 219.6677 | 282.7 | 260.3 | 277.4 | 282.7 | 427.1 | 41.6 | 20.4 | 79.9 | 10.4 | 244.9 | 15.2 | 834.4 | 729.8 | 547.2 | 829.8 | 609.7 | 698.9 | 573.7 | 584.8 | 606.7 | 617.9 | 211.3 | 294.1 | 299.9 | 274 | 276.6 | 298.5 | 290.5 | 264
675 | 530 | 468.9 | 187.56 | 219.2468 | 281.2 | 259.9 | 277.6 | 283.5 | 421.9 | 41.7 | 20.4 | 80 | 13.1 | 245.3 | 13.1 | 834 | 728 | 543.7 | 828.9 | 609.4 | 699 | 568.3 | 583.6 | 607.7 | 616.3 | 211.5 | 294.1 | 299.7 | 274.3 | 276.8 | 299 | 290.4 | 264.1
676 | 531 | 469.8 | 187.92 | 219.6677 | 279.8 | 258.9 | 278 | 283.9 | 418.3 | 41.7 | 20.4 | 80.2 | 11.7 | 235.6 | 12.5 | 832.7 | 721.8 | 528.5 | 826.6 | 606.7 | 698.8 | 567.6 | 570.9 | 607.7 | 615.2 | 211.7 | 294 | 299.8 | 274.4 | 276.8 | 299.5 | 290.3 | 264.2
677 | 532 | 469.2 | 187.68 | 219.3871 | 276.7 | 257.5 | 278.1 | 283.5 | 424 | 41.7 | 20.4 | 80.4 | 9.8 | 254.4 | 13.6 | 831.9 | 721.6 | 524.8 | 824.9 | 605.6 | 698.7 | 586.7 | 567.8 | 607.3 | 614.1 | 211.9 | 294 | 300 | 274.6 | 276.9 | 299.5 | 290.4 | 264.4
678 | 533 | 469.7 | 187.88 | 219.6209 | 275.6 | 257.2 | 278.2 | 282.8 | 423.8 | 41.7 | 20.4 | 80.6 | 9.1 | 254.5 | 14.5 | 831.3 | 719.9 | 534.6 | 823.6 | 604.3 | 698.3 | 580.6 | 565.1 | 607.7 | 613.2 | 212 | 294 | 300.4 | 274.7 | 277.1 | 299 | 290.4 | 264.6
679 | 534 | 469.3 | 187.72 | 219.4339 | 274.8 | 257.8 | 277.5 | 281.7 | 425 | 41.9 | 20.4 | 80.7 | 8.7 | 255.6 | 11.9 | 831.6 | 722.1 | 549.2 | 823.4 | 605.2 | 698 | 575.6 | 569.4 | 608.4 | 612.9 | 212.2 | 294.2 | 300.8 | 274.7 | 277.1 | 299 | 290.3 | 264.7
680 | 535 | 467.9 | 187.16 | 218.7793 | 274.5 | 257.8 | 277.3 | 281.7 | 423.8 | 42 | 20.4 | 80.9 | 10.2 | 251 | 11.3 | 830.7 | 722.3 | 564.2 | 823.3 | 604.8 | 697.6 | 571.8 | 571.7 | 609.1 | 612.4 | 212.4 | 294 | 300.8 | 274.7 | 277.1 | 298.4 | 290.1 | 264.8
681 | 536 | 467.6 | 187.04 | 218.639 | 276 | 257.8 | 277.9 | 281.1 | 419.9 | 42 | 20.4 | 81 | 9.3 | 263.8 | 16.8 | 830.9 | 726.5 | 575 | 825 | 606.6 | 697.1 | 569.4 | 577.2 | 610.1 | 612.6 | 212.5 | 293.8 | 300.6 | 274.6 | 277 | 297.6 | 290 | 264.9
682 | 537 | 466.8 | 186.72 | 218.2649 | 280.1 | 257.8 | 277.2 | 281.3 | 416.8 | 42.1 | 20.4 | 81.1 | 8.6 | 257.8 | 18.3 | 831.4 | 729.3 | 600.3 | 826 | 608.6 | 696.6 | 565.9 | 584 | 611.7 | 612.8 | 212.7 | 293.6 | 300.2 | 274.6 | 277 | 297 | 289.7 | 265
683 | 538 | 468.9 | 187.56 | 219.2468 | 281.3 | 257.7 | 276 | 281.4 | 414.9 | 42.2 | 20.4 | 81.1 | 7.1 | 248.6 | 20 | 832.9 | 730.9 | 624.3 | 826.1 | 610.5 | 696.4 | 563.5 | 589.4 | 613.4 | 613.3 | 212.9 | 293.4 | 300 | 274.8 | 277 | 296.4 | 289.3 | 265
684 | 539 | 467.2 | 186.88 | 218.452 | 278.6 | 257.3 | 275.7 | 281.1 | 413.8 | 42.2 | 20.4 | 81 | 5 | 252 | 19.7 | 833.1 | 734.1 | 631.2 | 826.5 | 612.1 | 696.2 | 561 | 597.8 | 614.8 | 613.9 | 213 | 293.6 | 299.9 | 274.9 | 276.9 | 296 | 288.9 | 265.1
685 | 540 | 468.6 | 187.44 | 219.1066 | 278.3 | 257.4 | 275.8 | 280.7 | 412.4 | 42.1 | 20.4 | 81 | 6.7 | 262.5 | 18.9 | 833.7 | 735.7 | 641.9 | 826.1 | 613.3 | 695.9 | 559 | 603.7 | 616.6 | 613.8 | 213.3 | 294.8 | 300.2 | 275.3 | 277 | 295.7 | 288.7 | 265.2
686 | 541 | 469.1 | 187.64 | 219.3403 | 278.7 | 258 | 275.8 | 280.4 | 414 | 42 | 20.4 | 81.1 | 8.4 | 274.4 | 17.3 | 834.2 | 733.5 | 631.1 | 825 | 612.3 | 695.7 | 556 | 597.2 | 617.6 | 612.5 | 213.5 | 294.8 | 300.3 | 275.6 | 277 | 295.5 | 288.4 | 265.2
687 | 542 | 468.6 | 187.44 | 219.1066 | 279.5 | 258.2 | 276.5 | 279.8 | 418.5 | 42 | 20.4 | 81.2 | 9.9 | 272.6 | 14.5 | 834.4 | 733.6 | 615 | 823.9 | 611.7 | 695.8 | 555 | 597.5 | 618.6 | 611.9 | 213.6 | 295.1 | 300.4 | 275.7 | 277 | 295.3 | 288.1 | 265.2
688 | 543 | 469 | 187.6 | 219.2936 | 281.4 | 258.5 | 277.3 | 280 | 422 | 42 | 20.4 | 81.4 | 10 | 262.7 | 13.8 | 834.4 | 735.5 | 619.1 | 823.7 | 612.3 | 696 | 555.7 | 597.7 | 619.8 | 611.5 | 213.8 | 295 | 300.3 | 275.8 | 277 | 295.2 | 287.9 | 265.3
689 | 544 | 469.5 | 187.8 | 219.5274 | 284.9 | 258.6 | 277.1 | 280.4 | 420.5 | 42 | 20.4 | 81.4 | 8.4 | 256.9 | 14.1 | 836.8 | 743.7 | 636.6 | 825.1 | 615.1 | 695.6 | 556.5 | 612.1 | 621.5 | 612.8 | 213.9 | 295 | 300.2 | 275.8 | 277 | 295.1 | 287.7 | 265.4
690 | 545 | 468.8 | 187.52 | 219.2001 | 286.6 | 258.3 | 277.1 | 281.1 | 421.2 | 42 | 20.4 | 81.3 | 9 | 254.1 | 14.2 | 838.5 | 748.8 | 659.3 | 824.9 | 618.7 | 694.9 | 557.1 | 618.9 | 623.5 | 613.9 | 214 | 295.2 | 300.4 | 275.9 | 277.1 | 294.9 | 287.4 | 265.4
691 | 546 | 468.9 | 187.56 | 219.2468 | 287.7 | 258.2 | 277.9 | 281.7 | 422.4 | 42.1 | 20.4 | 81.4 | 8.4 | 259.2 | 16.2 | 839.1 | 745.8 | 652.2 | 823.9 | 618.5 | 694.9 | 556.4 | 616.7 | 625.4 | 614 | 214.2 | 295.6 | 300.7 | 276.2 | 277.2 | 294.8 | 287.4 | 265.5
692 | 547 | 469.4 | 187.76 | 219.4806 | 288.8 | 258 | 278.3 | 281.8 | 421.1 | 42.2 | 20.4 | 81.3 | 7.9 | 260.1 | 16.6 | 837.9 | 740.2 | 641.7 | 821.9 | 617.7 | 695.2 | 552.6 | 603.3 | 626.6 | 612.3 | 214.3 | 295.6 | 301.1 | 276.4 | 277.2 | 295.2 | 287.2 | 265.7
693 | 548 | 468 | 187.2 | 218.826 | 287.9 | 257.8 | 279.2 | 281.3 | 415.8 | 42.3 | 20.4 | 81.2 | 7.9 | 248.5 | 16.2 | 837.8 | 740.7 | 642.2 | 821.5 | 619 | 696 | 549.7 | 604.5 | 627.5 | 612.1 | 214.4 | 295.7 | 302.1 | 276.6 | 277.2 | 295.7 | 287.3 | 265.8
694 | 549 | 465.8 | 186.32 | 217.7973 | 288.4 | 257.6 | 279.8 | 281 | 417 | 42.5 | 20.4 | 81.2 | 10.5 | 226.3 | 18 | 838.8 | 746.8 | 636.9 | 822.6 | 620.8 | 696.2 | 550.9 | 610.9 | 629.3 | 612.9 | 214.5 | 295.7 | 302.5 | 276.8 | 277.3 | 295.9 | 287.5 | 266
695 | 550 | 466 | 186.4 | 217.8909 | 289.4 | 257.1 | 279.7 | 281.5 | 417 | 42.6 | 20.4 | 81.2 | 9.7 | 244.7 | 15.4 | 838.1 | 748.3 | 634.2 | 822.6 | 620.9 | 696.3 | 551.5 | 607.6 | 630.2 | 613.1 | 214.6 | 295.6 | 302.4 | 276.9 | 277.2 | 296.4 | 287.8 | 266.2
696 | 551 | 466.9 | 186.76 | 218.3117 | 291.5 | 256.7 | 279.3 | 282.2 | 413.6 | 42.7 | 20.4 | 81.2 | 9.7 | 234.2 | 15.9 | 837.7 | 745.9 | 653.3 | 822.3 | 622.1 | 697.3 | 550.5 | 612.3 | 632.7 | 613.2 | 214.6 | 295.6 | 302.3 | 277 | 277.3 | 296.6 | 287.9 | 266.3
697 | 552 | 466.9 | 186.76 | 218.3117 | 290.9 | 257 | 278.6 | 283.1 | 411.1 | 42.6 | 20.4 | 81.2 | 9.4 | 240.4 | 16.4 | 838.3 | 745.5 | 650.2 | 822.4 | 622 | 698.4 | 553.5 | 616.5 | 634.6 | 613 | 214.7 | 295.5 | 302.4 | 277.2 | 277.3 | 296.6 | 288 | 266.4
698 | 553 | 467.7 | 187.08 | 218.6857 | 290.3 | 256.8 | 278.4 | 282.8 | 412.3 | 42.6 | 20.4 | 81.1 | 8.3 | 242.6 | 18.4 | 839.4 | 748.6 | 656.8 | 823 | 622.3 | 699.4 | 555.7 | 625.4 | 636.3 | 613.3 | 214.8 | 295.6 | 302.7 | 277.4 | 277.3 | 297 | 288.1 | 266.4
699 | 554 | 467.6 | 187.04 | 218.639 | 289.9 | 257.8 | 278.6 | 282 | 414.8 | 42.6 | 20.4 | 81 | 8.6 | 258 | 16.2 | 838.3 | 745.6 | 654 | 822 | 620.9 | 700.3 | 556.2 | 634.7 | 637.6 | 613.3 | 214.8 | 296.3 | 302.9 | 277.9 | 277.4 | 297.4 | 288.2 | 266.6
700 | 555 | 469 | 187.6 | 219.2936 | 289.9 | 258.5 | 279.4 | 282.2 | 424.6 | 42.7 | 20.4 | 81 | 7.2 | 244.7 | 15.1 | 838 | 740.8 | 656.8 | 821.3 | 620.5 | 701.4 | 562 | 634.3 | 638.7 | 613 | 214.9 | 297.3 | 303.6 | 278.5 | 277.5 | 297.3 | 288.4 | 266.7
701 | 556 | 467 | 186.8 | 218.3584 | 290.5 | 259.8 | 280.8 | 281.6 | 439.9 | 42.8 | 20.3 | 80.8 | 7.3 | 253.8 | 15.1 | 837.4 | 735.2 | 638 | 819.9 | 618.8 | 702.8 | 569.7 | 624.5 | 639.8 | 611.8 | 215 | 298.1 | 304.4 | 278.9 | 277.5 | 297.6 | 288.5 | 266.7
702 | 557 | 468 | 187.2 | 218.826 | 290.6 | 261 | 283.2 | 282.7 | 457.3 | 42.9 | 20.3 | 80.8 | 7.6 | 266 | 16.2 | 836.9 | 731.1 | 622.9 | 819.4 | 616.3 | 704.4 | 576.1 | 614.8 | 640.8 | 610.5 | 215.1 | 298.8 | 305.3 | 279.1 | 277.6 | 298.2 | 288.8 | 266.9
703 | 558 | 466.6 | 186.64 | 218.1714 | 292.3 | 262.4 | 285 | 284.5 | 475.4 | 43 | 20.3 | 80.8 | 7.5 | 262.6 | 18.2 | 836.6 | 727.7 | 624.1 | 819.3 | 615 | 706 | 586.9 | 609.8 | 641.7 | 609.7 | 215.2 | 299.8 | 308.1 | 279.6 | 277.8 | 299.4 | 289.2 | 267.1
704 | 559 | 467.4 | 186.96 | 218.5455 | 293.6 | 263.7 | 287 | 286.1 | 482.1 | 43 | 20.3 | 80.8 | 6.1 | 267.9 | 17.8 | 836.7 | 724.6 | 632.5 | 818.9 | 614.5 | 707.4 | 585.4 | 615.8 | 643 | 609.4 | 215.3 | 301.7 | 309.7 | 280.1 | 277.9 | 300.8 | 289.7 | 267.4
705 | 560 | 466.5 | 186.6 | 218.1246 | 294.5 | 264.7 | 289.6 | 288.2 | 498.1 | 43.1 | 20.3 | 80.8 | 7.6 | 257.7 | 16.8 | 835.7 | 718.8 | 627.6 | 817.8 | 612.8 | 708.7 | 585.7 | 608.9 | 643.7 | 608.1 | 215.4 | 302.9 | 311.5 | 280.6 | 278 | 302.4 | 290.3 | 267.6
706 | 561 | 467.9 | 187.16 | 218.7793 | 295.9 | 266.3 | 290.8 | 289.7 | 511 | 43.1 | 20.3 | 80.9 | 9.4 | 267.2 | 15.6 | 833.7 | 713 | 616.2 | 816.9 | 610.7 | 710.3 | 613.3 | 598 | 644.1 | 606.5 | 215.5 | 304.1 | 313.4 | 281.1 | 278.2 | 304.3 | 291 | 267.9
707 | 562 | 467.9 | 187.16 | 218.7793 | 298.2 | 267.2 | 293 | 291.1 | 518.1 | 43.2 | 20.3 | 81.2 | 8.9 | 259.5 | 17.3 | 832.1 | 709.6 | 608.2 | 816.4 | 608.9 | 712 | 632 | 587.6 | 644.5 | 605.4 | 215.6 | 305.2 | 314.7 | 281.4 | 278.4 | 306.2 | 291.8 | 268.2
708 | 563 | 468.3 | 187.32 | 218.9663 | 299.2 | 267.8 | 295.2 | 293.9 | 524 | 43.2 | 20.3 | 81.4 | 8.7 | 257.7 | 18.7 | 831.9 | 709.8 | 602.3 | 816.3 | 608.7 | 713.6 | 646.6 | 582.4 | 644.4 | 604.4 | 215.8 | 306.1 | 316.3 | 281.7 | 278.6 | 308.1 | 292.8 | 268.6
709 | 564 | 468.4 | 187.36 | 219.013 | 298.1 | 269.5 | 296.3 | 296 | 520.2 | 43 | 20.3 | 81.5 | 8.9 | 263.2 | 18.9 | 833 | 715.7 | 609.5 | 817 | 609.3 | 714.8 | 646.9 | 591.1 | 646.1 | 605.2 | 215.9 | 306.9 | 317.6 | 282.1 | 278.8 | 309.8 | 294.3 | 268.9
710 | 565 | 470 | 188 | 219.7612 | 295.8 | 270.7 | 296.7 | 298 | 518.2 | 43 | 20.3 | 81.5 | 9.5 | 255.1 | 20.7 | 833.3 | 715.9 | 599.8 | 816.7 | 608.7 | 715.6 | 641.9 | 584.7 | 647.2 | 604.5 | 216.1 | 307.4 | 318.2 | 282.1 | 279.1 | 311.4 | 295.5 | 269.3
711 | 566 | 469.4 | 187.76 | 219.4806 | 297.5 | 272.1 | 297.9 | 299.3 | 515.8 | 43 | 20.3 | 81.6 | 9.3 | 251.6 | 20.6 | 833 | 716.7 | 602.5 | 816.4 | 608.1 | 716.6 | 641 | 581.2 | 648.4 | 603.8 | 216.2 | 307.8 | 318.7 | 281.9 | 279.4 | 312.3 | 296.7 | 269.7
712 | 567 | 468.2 | 187.28 | 218.9195 | 297.4 | 273.5 | 297.9 | 300.4 | 517.2 | 43.1 | 20.3 | 81.5 | 8.4 | 249 | 21 | 833.2 | 717.2 | 628.2 | 815.8 | 610.5 | 717.8 | 648.6 | 582.5 | 649.2 | 603.5 | 216.3 | 308.1 | 318.8 | 282.1 | 279.6 | 313.2 | 297.7 | 270.1
713 | 568 | 468.5 | 187.4 | 219.0598 | 300.3 | 274.4 | 297.5 | 300.8 | 513.6 | 43.2 | 20.3 | 81.5 | 8 | 243.7 | 19.4 | 833.8 | 719.5 | 634.2 | 816.2 | 612.3 | 719.1 | 644.2 | 588.3 | 651.4 | 603.2 | 216.5 | 308.3 | 318.7 | 282.4 | 279.8 | 313.8 | 298.9 | 270.4
714 | 569 | 469.5 | 187.8 | 219.5274 | 300.4 | 274.9 | 297.2 | 300.5 | 514.8 | 43.3 | 20.3 | 81.4 | 7.7 | 250.6 | 17.9 | 836.3 | 727.4 | 654.8 | 818.4 | 615.5 | 720.3 | 636.8 | 612.7 | 653.8 | 604.6 | 216.6 | 308.6 | 318.8 | 282.5 | 280.1 | 315 | 300.1 | 270.7
715 | 570 | 470.1 | 188.04 | 219.8079 | 301.4 | 274 | 297.7 | 299.6 | 519.4 | 43.3 | 20.3 | 81.5 | 7.4 | 262.4 | 17.4 | 838.5 | 735.5 | 672.1 | 817.7 | 618.7 | 721 | 632.8 | 627.4 | 656.7 | 606.3 | 216.8 | 309.3 | 319.2 | 282.6 | 280.3 | 315.5 | 301.1 | 271.1
716 | 571 | 469.6 | 187.84 | 219.5741 | 302.3 | 273.4 | 298.3 | 298.4 | 512.2 | 43.4 | 20.3 | 81.6 | 7.3 | 254.9 | 18.4 | 840.5 | 742.7 | 708.2 | 816.2 | 626 | 721.6 | 628.5 | 639.6 | 660.1 | 608.8 | 216.9 | 309.5 | 319.5 | 282.7 | 280.5 | 315.7 | 302.3 | 271.4
717 | 572 | 469.7 | 187.88 | 219.6209 | 303.2 | 272.8 | 298.1 | 296.9 | 503.5 | 43.5 | 20.3 | 81.7 | 8.2 | 250.6 | 18.2 | 841.4 | 743.1 | 711.3 | 813.5 | 628.3 | 721.9 | 620.5 | 651.8 | 661.7 | 610.3 | 217.1 | 309.7 | 319.8 | 282.9 | 280.7 | 315.8 | 302.9 | 271.6
718 | 573 | 469.2 | 187.68 | 219.3871 | 303.8 | 272.4 | 297.5 | 295.9 | 494.1 | 43.5 | 20.3 | 81.8 | 8.2 | 252.8 | 19.6 | 839.5 | 735.7 | 690.6 | 809.1 | 627 | 722.5 | 619 | 633.5 | 662.4 | 608.2 | 217.2 | 309.6 | 319.5 | 282.9 | 280.9 | 315.8 | 303.6 | 271.9
719 | 574 | 469.1 | 187.64 | 219.3403 | 303.7 | 272.5 | 297.6 | 295.1 | 493.2 | 43.6 | 20.3 | 81.7 | 8.5 | 259 | 20.7 | 838.1 | 733.4 | 670.1 | 806.7 | 626.1 | 723.5 | 615 | 626.4 | 662.4 | 607.7 | 217.3 | 309.4 | 319.5 | 282.9 | 281.1 | 316.2 | 304.1 | 272.1
720 | 575 | 469 | 187.6 | 219.2936 | 302.9 | 272 | 297.9 | 294.4 | 493.4 | 43.6 | 20.3 | 81.6 | 9.2 | 259.3 | 20.4 | 838 | 732 | 658.4 | 804.8 | 625.3 | 724.7 | 610.1 | 618.9 | 663.3 | 607.2 | 217.5 | 309.3 | 319.7 | 283 | 281.4 | 316.4 | 304.3 | 272.4
721 | 576 | 470 | 188 | 219.7612 | 304.1 | 271.5 | 298.6 | 295.1 | 486.5 | 43.7 | 20.3 | 81.6 | 9.3 | 255.3 | 18.4 | 837.1 | 729.5 | 652.7 | 801.9 | 623.4 | 725.9 | 606.1 | 611.4 | 664.1 | 606.3 | 217.6 | 309.2 | 319.4 | 283.2 | 281.7 | 316.2 | 304.3 | 272.6
722 | 577 | 469.8 | 187.92 | 219.6677 | 304.6 | 271.1 | 298.1 | 294.9 | 490.5 | 43.7 | 20.3 | 81.5 | 8.5 | 260 | 18.7 | 836.7 | 726.7 | 651.8 | 799.8 | 622 | 727.1 | 605.3 | 610.2 | 665.1 | 605.9 | 217.7 | 309 | 318.9 | 283.3 | 281.9 | 316.5 | 304.3 | 272.8
723 | 578 | 469.9 | 187.96 | 219.7144 | 304.4 | 270.5 | 296.9 | 293.8 | 486.8 | 43.8 | 20.3 | 81.5 | 9 | 265.6 | 19.4 | 836.3 | 721.5 | 643.6 | 797.3 | 620.5 | 727.8 | 600.6 | 604.1 | 664.8 | 604.8 | 217.9 | 308.7 | 318.5 | 283.5 | 282.1 | 316.3 | 304.5 | 273.1
724 | 579 | 469.5 | 187.8 | 219.5274 | 301.5 | 269.5 | 295.5 | 293.6 | 490.2 | 43.7 | 20.3 | 81.6 | 8.9 | 263.3 | 19.8 | 835.2 | 715.2 | 630.4 | 794.6 | 618.5 | 728.5 | 605.9 | 593.3 | 664.8 | 603.4 | 218 | 308.6 | 318.2 | 283.7 | 282.3 | 316.8 | 304.6 | 273.2
725 | 580 | 469.4 | 187.76 | 219.4806 | 300 | 269.1 | 294.6 | 295.3 | 491.6 | 43.7 | 20.3 | 81.7 | 8.2 | 254.4 | 18.7 | 835.1 | 712.4 | 618.9 | 793.4 | 616.9 | 729.4 | 612 | 591.7 | 665.4 | 602.8 | 218.2 | 308.5 | 317.6 | 283.9 | 282.6 | 316.8 | 304.7 | 273.4
726 | 581 | 470.3 | 188.12 | 219.9014 | 299.2 | 270.6 | 293.8 | 297 | 492.5 | 43.6 | 20.3 | 81.8 | 6.7 | 267 | 18.8 | 834.2 | 708 | 615.2 | 791.4 | 615.5 | 730.3 | 611.9 | 587.9 | 665.8 | 601.8 | 218.3 | 308.2 | 316.9 | 283.9 | 282.8 | 316.8 | 304.8 | 273.7
727 | 582 | 469.6 | 187.84 | 219.5741 | 298.2 | 272.1 | 293.2 | 297.7 | 491.8 | 43.6 | 20.3 | 82 | 7 | 260.2 | 16.7 | 833.3 | 712.8 | 630.1 | 790.9 | 615 | 731.3 | 613.6 | 587.1 | 666.8 | 601.7 | 218.4 | 307.7 | 316 | 283.9 | 282.9 | 316.7 | 304.9 | 273.8
728 | 583 | 470.1 | 188.04 | 219.8079 | 297.3 | 272.8 | 291.5 | 297.4 | 494.4 | 43.6 | 20.3 | 82.3 | 7.7 | 257 | 15.4 | 833.1 | 711 | 622.4 | 790.3 | 614.4 | 732 | 609.7 | 587.8 | 668 | 601.2 | 218.5 | 307.3 | 315.5 | 283.8 | 283 | 316.4 | 305.1 | 274
729 | 584 | 469.7 | 187.88 | 219.6209 | 294.7 | 272.1 | 289.4 | 297 | 495.9 | 43.4 | 20.3 | 82.6 | 8.7 | 260.5 | 14.6 | 833.7 | 714.3 | 616.8 | 790.6 | 615.2 | 732.8 | 611.6 | 586.7 | 669.4 | 600.5 | 218.7 | 306.9 | 314.6 | 283.8 | 283.1 | 316.2 | 305.2 | 274.2
730 | 585 | 470.6 | 188.24 | 220.0417 | 292.5 | 271.5 | 288.4 | 296.3 | 498.6 | 43.4 | 20.3 | 82.8 | 9.2 | 252.8 | 11.8 | 834.6 | 720.4 | 610.6 | 791.2 | 615.9 | 733.5 | 608.7 | 589.1 | 670.9 | 601 | 218.8 | 306.5 | 314.3 | 283.9 | 283.3 | 316.5 | 305.3 | 274.4
731 | 586 | 471.1 | 188.44 | 220.2755 | 292.7 | 271.3 | 286.9 | 296 | 497.6 | 43.3 | 20.3 | 83 | 9.9 | 260.3 | 11.6 | 834.4 | 719.1 | 598.8 | 790.6 | 614.7 | 733.9 | 605.7 | 586.8 | 671.3 | 600 | 219 | 306.1 | 313.9 | 284 | 283.4 | 316.2 | 305.1 | 274.5
732 | 587 | 467.6 | 187.04 | 218.639 | 292.1 | 271.2 | 286.8 | 296 | 498.1 | 43.3 | 20.3 | 83.2 | 9.9 | 250.5 | 16.7 | 833.2 | 717.8 | 589.3 | 789.5 | 614.3 | 734.4 | 604.2 | 586.6 | 671.7 | 599.9 | 219.2 | 305.8 | 314 | 284.1 | 283.6 | 316.7 | 305 | 274.7
733 | 588 | 468.6 | 187.44 | 219.1066 | 293.1 | 271.5 | 286.1 | 295.9 | 496.7 | 43.2 | 20.3 | 83.4 | 8.2 | 255.4 | 16.7 | 831.9 | 711.9 | 574.5 | 787.5 | 611.9 | 734.8 | 607.6 | 581.3 | 671.6 | 598.7 | 219.3 | 305.7 | 313.8 | 284.3 | 283.7 | 317.2 | 304.8 | 274.8
734 | 589 | 469.1 | 187.64 | 219.3403 | 291.9 | 271.4 | 287 | 296.1 | 497.4 | 43.2 | 20.2 | 83.7 | 7.3 | 251 | 15.3 | 830.9 | 707.9 | 570.8 | 785.4 | 610 | 735.3 | 617.1 | 575.7 | 671.8 | 597.6 | 219.5 | 305.7 | 313.9 | 284.7 | 283.9 | 317 | 304.7 | 274.9
735 | 590 | 469.6 | 187.84 | 219.5741 | 291.2 | 271.6 | 287.8 | 296.8 | 499.2 | 43.3 | 20.3 | 83.9 | 6.4 | 262.3 | 15 | 829.1 | 701.5 | 562.6 | 782.4 | 607.9 | 736 | 622.1 | 569.3 | 671.6 | 596.5 | 219.7 | 305.7 | 313.8 | 284.9 | 284.1 | 317.1 | 304.5 | 275.1
736 | 591 | 469.9 | 187.96 | 219.7144 | 289.8 | 273 | 288.9 | 297 | 494.5 | 43.4 | 20.2 | 84.1 | 6.7 | 253.6 | 14.3 | 827.1 | 695.6 | 556.6 | 780.3 | 605.7 | 737.7 | 626.2 | 564 | 672.1 | 595.5 | 219.9 | 305.9 | 314.3 | 285.2 | 284.2 | 317.6 | 304.5 | 275.2
737 | 592 | 471 | 188.4 | 220.2287 | 288.1 | 273.5 | 289.7 | 297.3 | 490.4 | 43.5 | 20.3 | 84.3 | 7.6 | 257 | 12.7 | 825.5 | 688.8 | 550.3 | 778.6 | 603.7 | 740.1 | 632.1 | 556.3 | 672.2 | 594.6 | 220.1 | 306 | 314.8 | 285.4 | 284.3 | 319.7 | 304.8 | 275.4
738 | 593 | 467.6 | 187.04 | 218.639 | 288.8 | 273.3 | 289.1 | 298.2 | 486.9 | 43.7 | 20.2 | 84.4 | 7 | 256.3 | 14.3 | 823.6 | 684.8 | 548.6 | 776.8 | 602.3 | 741.2 | 643.7 | 551.6 | 672.8 | 593.9 | 220.3 | 306.3 | 315.8 | 285.4 | 284.4 | 320 | 305.1 | 275.6
739 | 594 | 467.7 | 187.08 | 218.6857 | 290.6 | 272.4 | 289 | 299.1 | 482.5 | 43.9 | 20.2 | 84.6 | 7.1 | 262.5 | 19.4 | 822.6 | 684.3 | 553.3 | 775.7 | 602 | 742.2 | 646.8 | 550.6 | 674.1 | 593 | 220.5 | 306.7 | 317.1 | 285.6 | 284.5 | 319.4 | 305.4 | 275.8
740 | 595 | 467.9 | 187.16 | 218.7793 | 292.5 | 272.2 | 288.8 | 298.8 | 481 | 44 | 20.2 | 84.7 | 5.6 | 263.6 | 19.9 | 821.7 | 681.7 | 551.9 | 775.2 | 600.2 | 742.7 | 650.6 | 548.3 | 675.9 | 592.5 | 220.7 | 307.2 | 317.1 | 285.7 | 284.5 | 319.1 | 305.8 | 276
741 | 596 | 467.9 | 187.16 | 218.7793 | 292.8 | 272.2 | 288.7 | 297.8 | 480.7 | 44.1 | 20.2 | 84.8 | 7.5 | 269.7 | 18.4 | 821 | 678.7 | 558 | 774.1 | 599.6 | 742.9 | 653.1 | 543 | 676.6 | 591.9 | 220.9 | 307.9 | 317 | 285.7 | 284.7 | 319.1 | 306 | 276.2
742 | 597 | 468.5 | 187.4 | 219.0598 | 293.1 | 273 | 289.1 | 297.4 | 481.7 | 44.1 | 20.2 | 84.9 | 8.8 | 278.4 | 16.4 | 820.7 | 679.1 | 551.8 | 773.5 | 597.8 | 743 | 654.9 | 542.5 | 677.7 | 592.1 | 221.1 | 308.1 | 317.2 | 285.8 | 284.8 | 320.9 | 306.5 | 276.3
743 | 598 | 468.2 | 187.28 | 218.9195 | 293.7 | 273.6 | 290.1 | 298.8 | 478.2 | 44.1 | 20.2 | 84.9 | 7.8 | 276.2 | 15.7 | 820.3 | 682.6 | 542.8 | 773.4 | 597.4 | 742.9 | 654 | 541 | 678.6 | 591.8 | 221.3 | 308.3 | 317.5 | 286.1 | 285 | 322.5 | 307 | 276.6
744 | 599 | 469.8 | 187.92 | 219.6677 | 295.4 | 272.8 | 291 | 299.5 | 477.3 | 44.2 | 20.2 | 84.8 | 6.8 | 277.1 | 19 | 820.3 | 687.3 | 550.6 | 773.6 | 597.4 | 743 | 651.8 | 545.5 | 679.9 | 591.7 | 221.6 | 308.3 | 317.4 | 286.2 | 285.2 | 322.7 | 307.3 | 276.8
745 | 600 | 470.2 | 188.08 | 219.8547 | 295.9 | 272.4 | 291.2 | 300 | 490.4 | 44.2 | 20.2 | 84.8 | 7.2 | 273.8 | 19 | 819.7 | 690.6 | 546.2 | 773.8 | 596.7 | 743.1 | 646.2 | 548.1 | 680.9 | 591.3 | 221.8 | 308.2 | 317.3 | 286.2 | 285.4 | 322.7 | 307.5 | 277.1
746 | 601 | 468.3 | 187.32 | 218.9663 | 296.8 | 272.3 | 291.5 | 299.3 | 509.2 | 44.2 | 20.2 | 84.9 | 7.6 | 275.6 | 18.9 | 820.7 | 702.1 | 578.9 | 776.8 | 600.4 | 742.9 | 644.4 | 563.2 | 682.9 | 592.5 | 222 | 308.1 | 317.3 | 286.3 | 285.5 | 325.4 | 308 | 277.3
747 | 602 | 469.1 | 187.64 | 219.3403 | 299.6 | 273.2 | 291.3 | 299.6 | 509 | 44.2 | 20.2 | 84.9 | 7.2 | 274.7 | 17.9 | 822.2 | 710.7 | 588.1 | 779.7 | 602 | 742.5 | 637.6 | 579 | 685.3 | 594.1 | 222.2 | 308.1 | 317.3 | 286.4 | 285.8 | 325.3 | 308.3 | 277.6
748 | 603 | 468.8 | 187.52 | 219.2001 | 301 | 273.8 | 291.6 | 300.1 | 501.2 | 44.2 | 20.2 | 84.9 | 6.4 | 273.4 | 17.6 | 821.2 | 709.3 | 588 | 778.9 | 600.9 | 742.4 | 628.7 | 577.8 | 686.5 | 593.3 | 222.5 | 308.5 | 317.2 | 286.5 | 285.9 | 324.7 | 308.4 | 277.8
749 | 604 | 470.4 | 188.16 | 219.9482 | 300.4 | 273.6 | 291.8 | 299.2 | 503.1 | 44.1 | 20.2 | 85 | 6.3 | 271.1 | 16.2 | 819.9 | 703 | 578.3 | 778.2 | 599.7 | 742.4 | 621.5 | 571.8 | 686.5 | 592.5 | 222.7 | 308.8 | 317.5 | 286.7 | 286 | 324 | 308.4 | 277.9
750 | 605 | 470.4 | 188.16 | 219.9482 | 300.5 | 273 | 292.6 | 298.9 | 508.2 | 44 | 20.2 | 85.1 | 7.2 | 269.6 | 15 | 818.9 | 704.1 | 571.2 | 778.8 | 598.9 | 742.5 | 620.2 | 567.2 | 686.5 | 592.5 | 222.9 | 309 | 318.6 | 287 | 286.2 | 324.6 | 308.7 | 278
751 | 606 | 470.1 | 188.04 | 219.8079 | 303.4 | 274 | 292.8 | 298.9 | 508.5 | 44 | 20.2 | 85.3 | 8.1 | 285.8 | 14.4 | 818.2 | 698.3 | 562.4 | 778.4 | 598.2 | 742.8 | 627.5 | 562.5 | 687.5 | 591.5 | 223.2 | 309.1 | 318.8 | 287.2 | 286.3 | 325.8 | 308.9 | 278.3
752 | 607 | 469.5 | 187.8 | 219.5274 | 306 | 274.4 | 291.9 | 299.6 | 506.7 | 44.2 | 20.2 | 85.4 | 8.2 | 281.6 | 13.7 | 819.2 | 700 | 568.7 | 778.6 | 598.8 | 742.9 | 628.2 | 570.2 | 689.7 | 591.6 | 223.4 | 309.1 | 319.4 | 287.4 | 286.4 | 327.8 | 309 | 278.4
753 | 608 | 470.5 | 188.2 | 219.995 | 305.9 | 273.9 | 291.6 | 299.8 | 502.5 | 44.4 | 20.2 | 85.7 | 7.8 | 278.2 | 12.2 | 819.3 | 700.6 | 556.6 | 777.8 | 598.9 | 743 | 627.3 | 568.1 | 691 | 590.9 | 223.7 | 309.2 | 319.4 | 287.6 | 286.6 | 328.5 | 309.3 | 278.7
754 | 609 | 470.8 | 188.32 | 220.1352 | 303.8 | 274.4 | 292.7 | 299.5 | 504.6 | 44.5 | 20.2 | 85.9 | 6.6 | 272.7 | 13.4 | 817.2 | 691.7 | 555.7 | 775.7 | 597.2 | 743.4 | 631.4 | 563.7 | 691.2 | 590.3 | 223.9 | 309.2 | 319.9 | 287.6 | 286.8 | 328.7 | 310 | 278.9
755 | 610 | 470.2 | 188.08 | 219.8547 | 303 | 274.7 | 293.9 | 300 | 507.6 | 44.7 | 20.2 | 86.2 | 7.1 | 281.1 | 16.6 | 814.4 | 683.8 | 552.9 | 774 | 595.5 | 743.6 | 633.3 | 559 | 691.7 | 589.4 | 224.1 | 309.2 | 320.4 | 287.6 | 287 | 330.4 | 311 | 279.3
756 | 611 | 470.2 | 188.08 | 219.8547 | 303.1 | 273.7 | 295.1 | 300 | 514.2 | 44.7 | 20.2 | 86.5 | 8.9 | 262.4 | 17.6 | 811.4 | 676.8 | 541.4 | 772.4 | 593.4 | 743.9 | 634.8 | 553 | 692.5 | 588.4 | 224.3 | 309.5 | 320.7 | 287.7 | 287.4 | 331.7 | 311.9 | 279.8
757 | 612 | 470.3 | 188.12 | 219.9014 | 304.1 | 273.9 | 296.5 | 301.6 | 512.2 | 44.8 | 20.2 | 86.6 | 7.4 | 258.2 | 18.5 | 809.5 | 675.6 | 533.7 | 771.6 | 592.8 | 744 | 647.2 | 548.8 | 692.7 | 587.5 | 224.5 | 309.7 | 320.8 | 287.7 | 287.7 | 331.7 | 312.8 | 280.1
758 | 613 | 469.9 | 187.96 | 219.7144 | 306.6 | 273.8 | 296.3 | 303.1 | 509.5 | 44.8 | 20.2 | 86.7 | 8 | 261.5 | 21.1 | 808 | 673.1 | 530.8 | 770.5 | 591.7 | 744.1 | 648.6 | 545.2 | 693.4 | 586.7 | 224.8 | 309.9 | 321.4 | 288 | 288 | 331.8 | 313.5 | 280.4
759 | 614 | 469.6 | 187.84 | 219.5741 | 306.3 | 273.9 | 298 | 303.6 | 506.3 | 44.9 | 20.2 | 86.8 | 8.9 | 263.9 | 21.6 | 807.2 | 668.8 | 519.3 | 769.2 | 590.4 | 744.3 | 652.8 | 539.5 | 693.6 | 585.7 | 225 | 310.1 | 322.5 | 288.3 | 288.2 | 332.4 | 313.9 | 280.7
760 | 615 | 469.4 | 187.76 | 219.4806 | 303.4 | 273.4 | 299.1 | 304.8 | 505.6 | 45 | 20.2 | 86.8 | 8.3 | 263.7 | 19.8 | 805.3 | 665.5 | 516.8 | 766.8 | 588.7 | 744.6 | 657.6 | 536.2 | 693.8 | 584.7 | 225.2 | 310.8 | 324.7 | 288.6 | 288.3 | 332.7 | 314.4 | 280.9
761 | 616 | 470 | 188 | 219.7612 | 304.4 | 272.7 | 298.6 | 306.5 | 502.7 | 45 | 20.2 | 86.7 | 9 | 278.3 | 19.7 | 803.9 | 666.4 | 534.4 | 765.9 | 588.4 | 744.9 | 658 | 539.4 | 694.8 | 584.2 | 225.4 | 311.6 | 325.4 | 289.2 | 288.4 | 332.8 | 314.8 | 281.2
762 | 617 | 470.3 | 188.12 | 219.9014 | 304.5 | 272.8 | 298.5 | 308 | 507.9 | 45.1 | 20.2 | 86.6 | 7.6 | 282.5 | 19.3 | 805.2 | 672 | 547.3 | 767.2 | 588.6 | 745 | 654.9 | 550.2 | 696.6 | 584 | 225.6 | 312.2 | 325.8 | 289.7 | 288.5 | 332.7 | 315 | 281.3
763 | 618 | 469.4 | 187.76 | 219.4806 | 305.2 | 272.6 | 299.4 | 308.4 | 518.1 | 45.1 | 20.2 | 86.7 | 7.3 | 277.5 | 19.1 | 806.2 | 678 | 541.9 | 767.5 | 588.4 | 744.8 | 650.3 | 554.8 | 698.4 | 583.7 | 225.8 | 312.5 | 325.8 | 289.9 | 288.7 | 332.5 | 315.3 | 281.6
764 | 619 | 469.6 | 187.84 | 219.5741 | 304 | 273.9 | 299.5 | 309 | 522.3 | 45.1 | 20.2 | 86.7 | 6.3 | 285.9 | 17 | 805.4 | 674.5 | 535.4 | 765.8 | 587.3 | 744.8 | 659.2 | 549.1 | 699.2 | 582.9 | 226 | 312.9 | 325.5 | 289.9 | 288.9 | 332.4 | 315.5 | 281.7
765 | 620 | 470.2 | 188.08 | 219.8547 | 303.4 | 275.5 | 298.8 | 309.2 | 527.8 | 45.1 | 20.2 | 86.7 | 6.1 | 278.4 | 14.7 | 804 | 676.3 | 536.9 | 764.9 | 586.4 | 745 | 661.2 | 546.4 | 699.8 | 582.4 | 226.3 | 312.8 | 325.1 | 290.1 | 289 | 332.4 | 315.6 | 281.9
766 | 621 | 469.8 | 187.92 | 219.6677 | 305.3 | 277 | 298.6 | 310.2 | 532.8 | 45.1 | 20.2 | 86.7 | 4.9 | 274.2 | 10.9 | 804.4 | 678.3 | 546.8 | 765.3 | 586.5 | 745.2 | 660 | 551.2 | 701.3 | 582.4 | 226.5 | 311.9 | 323.8 | 290.1 | 289.1 | 332.5 | 316 | 282.1
767 | 622 | 469.2 | 187.68 | 219.3871 | 307.1 | 278.3 | 298 | 310.6 | 539.4 | 44.9 | 20.2 | 86.7 | 5.4 | 256.6 | 9.5 | 805.7 | 682.8 | 559.6 | 766.2 | 588 | 745.4 | 657.7 | 563.5 | 703 | 583 | 226.7 | 311.8 | 323 | 290.2 | 289.2 | 332.8 | 316.1 | 282.3
768 | 623 | 468.7 | 187.48 | 219.1533 | 309.3 | 280 | 296.4 | 310.5 | 544.8 | 44.8 | 20.2 | 86.8 | 6.6 | 270.7 | 8.5 | 806 | 685.3 | 564.6 | 766.4 | 588.9 | 745.3 | 651.4 | 575.3 | 706.2 | 583.6 | 226.9 | 311.7 | 322.7 | 290.5 | 289.4 | 333 | 316 | 282.5
769 | 624 | 470.1 | 188.04 | 219.8079 | 308.8 | 281.1 | 295.9 | 310 | 557.4 | 44.8 | 20.2 | 86.9 | 7.4 | 274.4 | 8.4 | 805.5 | 680.7 | 557.4 | 765.3 | 588 | 745.4 | 647.9 | 573.5 | 707.8 | 582.8 | 227.1 | 312.1 | 323.3 | 290.8 | 289.7 | 333.5 | 316.5 | 282.8
770 | 625 | 470 | 188 | 219.7612 | 305.9 | 282 | 296.6 | 309.7 | 556.2 | 44.9 | 20.2 | 87.1 | 6.9 | 273.4 | 8.4 | 804.1 | 674.1 | 545.4 | 764 | 586.8 | 745.6 | 653.2 | 564.6 | 708.1 | 581.9 | 227.3 | 312.6 | 324.1 | 290.9 | 290.1 | 334.3 | 317.3 | 283.1
771 | 626 | 468.8 | 187.52 | 219.2001 | 305.4 | 282.9 | 297.2 | 311.7 | 559.3 | 44.9 | 20.2 | 87.2 | 6.3 | 267.1 | 8.7 | 802.9 | 671.9 | 538.4 | 763.2 | 585.8 | 746 | 657.5 | 563.1 | 707.4 | 581.3 | 227.6 | 313.2 | 324.5 | 291.2 | 290.3 | 335.1 | 318.2 | 283.5
772 | 627 | 469.4 | 187.76 | 219.4806 | 305.1 | 283.1 | 297.3 | 313.7 | 558.6 | 44.9 | 20.2 | 87.3 | 5.9 | 273.2 | 8.2 | 801.6 | 669.4 | 529 | 762.2 | 584.5 | 746.3 | 653.1 | 560.4 | 706.5 | 580.6 | 227.8 | 313.7 | 325 | 291.5 | 290.5 | 335.2 | 318.5 | 283.8
773 | 628 | 469 | 187.6 | 219.2936 | 304.1 | 282.9 | 296.6 | 314.4 | 554.2 | 44.9 | 20.2 | 87.4 | 5.7 | 297.1 | 6.5 | 799.9 | 666.3 | 519.3 | 760.7 | 582.7 | 746.4 | 654.2 | 553.8 | 706.3 | 579.4 | 228 | 314.3 | 325.4 | 291.8 | 290.7 | 335.3 | 318.9 | 284.1
774 | 629 | 468.7 | 187.48 | 219.1533 | 305.3 | 282.6 | 295.9 | 314.3 | 554.1 | 45 | 20.2 | 87.5 | 6 | 278.1 | 5.3 | 799.1 | 665.8 | 511.9 | 759.5 | 582 | 746.6 | 658.8 | 551.3 | 706.5 | 578.4 | 228.2 | 314.5 | 325.1 | 292.2 | 291 | 335.9 | 319.6 | 284.4
775 | 630 | 468.4 | 187.36 | 219.013 | 306.3 | 282.4 | 295.3 | 314.7 | 549.9 | 45.2 | 20.2 | 87.7 | 5.8 | 278.9 | 4.6 | 796.9 | 661 | 506.7 | 757.9 | 580.4 | 747 | 662.3 | 549.3 | 707.2 | 577.8 | 228.5 | 314.6 | 324.7 | 292.2 | 291.2 | 337.6 | 320.4 | 284.7
776 | 631 | 469.6 | 187.84 | 219.5741 | 307.2 | 282.5 | 295.4 | 316.4 | 541.3 | 45.3 | 20.2 | 87.8 | 5.6 | 278.7 | 4.2 | 794.1 | 656.9 | 508 | 756 | 579.2 | 747.4 | 672.2 | 547.7 | 708 | 577.1 | 228.7 | 314.9 | 325 | 292.1 | 291.5 | 338.2 | 321.3 | 285.2
777 | 632 | 469.1 | 187.64 | 219.3403 | 306.9 | 282 | 296.7 | 317.2 | 535.7 | 45.5 | 20.2 | 87.8 | 5.4 | 263.1 | 4.5 | 793.5 | 663.7 | 520.1 | 756.3 | 579.8 | 747.8 | 673.7 | 555.8 | 709.9 | 577 | 228.9 | 315.4 | 325.6 | 292.1 | 291.6 | 338.1 | 321.9 | 285.5
778 | 633 | 469 | 187.6 | 219.2936 | 307.9 | 281.9 | 297.8 | 317.5 | 537 | 45.5 | 20.2 | 87.8 | 5.6 | 241.6 | 5.1 | 792.8 | 670.8 | 534.6 | 756.5 | 580.4 | 748.1 | 670.2 | 557.7 | 711.6 | 577.3 | 229.1 | 315.7 | 326.3 | 292.4 | 291.8 | 338.6 | 322.2 | 285.8
779 | 634 | 468 | 187.2 | 218.826 | 307.6 | 282.1 | 298.8 | 317.4 | 535.4 | 45.6 | 20.2 | 87.8 | 5.1 | 236.4 | 5.5 | 793.3 | 670.6 | 536.2 | 756.1 | 580.2 | 748.3 | 662.6 | 556.5 | 712.5 | 576.8 | 229.4 | 316.3 | 326.5 | 292.6 | 292 | 339.6 | 322.5 | 286
780 | 635 | 469.6 | 187.84 | 219.5741 | 308.4 | 282.6 | 299.6 | 317.4 | 538.1 | 45.7 | 20.2 | 87.9 | 5.2 | 275 | 5 | 792.7 | 666.1 | 525.4 | 754.8 | 579.2 | 748.5 | 661.6 | 553.2 | 712.7 | 575.8 | 229.6 | 316 | 326.7 | 292.9 | 292.2 | 340.3 | 322.7 | 286.3
781 | 636 | 469.1 | 187.64 | 219.3403 | 308.7 | 283.6 | 300.6 | 317.7 | 540.7 | 45.8 | 20.1 | 88.1 | 4.5 | 239.9 | 6.5 | 792.1 | 667 | 526.8 | 754 | 579.6 | 748.7 | 663.5 | 553.3 | 713.4 | 575.2 | 229.9 | 316.2 | 327 | 293 | 292.4 | 341.1 | 323.3 | 286.6
782 | 637 | 469.2 | 187.68 | 219.3871 | 307.6 | 284.6 | 300.9 | 317.9 | 542.6 | 46 | 20.1 | 88.2 | 4.8 | 259 | 7.3 | 793.1 | 673.2 | 538 | 754.8 | 581 | 749 | 662.7 | 560.4 | 714.3 | 575.3 | 230.1 | 316.5 | 327 | 293.3 | 292.7 | 341.4 | 323.5 | 286.9
783 | 638 | 468.4 | 187.36 | 219.013 | 307.8 | 285.3 | 300.8 | 318.6 | 549.6 | 46.1 | 20.1 | 88.5 | 5.7 | 276.3 | 7.2 | 794.2 | 678.6 | 548.2 | 755 | 581.8 | 749 | 656.1 | 568.6 | 715.1 | 575.9 | 230.4 | 316.9 | 327.1 | 293.7 | 293 | 341.3 | 323.7 | 287.3
784 | 639 | 469.5 | 187.8 | 219.5274 | 307.5 | 286.2 | 300.2 | 317.9 | 569.9 | 46.1 | 20.1 | 88.7 | 6.8 | 273.4 | 7.9 | 793.6 | 673.1 | 543.7 | 753.9 | 580.5 | 749 | 653.1 | 569.3 | 715.2 | 575.9 | 230.6 | 317.2 | 327.4 | 294.2 | 293.2 | 341.4 | 324.1 | 287.6
785 | 640 | 468.8 | 187.52 | 219.2001 | 307.4 | 287.6 | 300.5 | 317.3 | 577.5 | 46.1 | 20.1 | 88.8 | 6.6 | 272.9 | 7.6 | 791.5 | 670.1 | 543.6 | 752.2 | 579.9 | 749 | 656.3 | 565.1 | 715.1 | 575.1 | 230.9 | 317.5 | 327.5 | 294.4 | 293.5 | 341.5 | 324.7 | 288
786 | 641 | 469.1 | 187.64 | 219.3403 | 307.7 | 288.9 | 300.9 | 318.6 | 566.8 | 46.2 | 20.1 | 88.9 | 5.9 | 279.9 | 7.4 | 791.1 | 673.6 | 558.3 | 751.9 | 580.4 | 749 | 660.7 | 568 | 716.5 | 574.9 | 231.2 | 318 | 327.6 | 294.6 | 293.7 | 341.5 | 325.2 | 288.2
787 | 642 | 470.2 | 188.08 | 219.8547 | 308.8 | 289 | 300.1 | 320.1 | 562.6 | 46.2 | 20.1 | 89.1 | 6 | 264.2 | 7.8 | 792.1 | 672.9 | 574.4 | 752.3 | 582.4 | 749.1 | 658.5 | 572.2 | 718 | 574.9 | 231.4 | 318.1 | 327.9 | 294.9 | 293.8 | 341.7 | 325.7 | 288.5
788 | 643 | 469.6 | 187.84 | 219.5741 | 309.9 | 289 | 300.2 | 320.2 | 563.9 | 46.1 | 20.1 | 89.4 | 5.8 | 268.8 | 8.1 | 790.6 | 674.3 | 575.4 | 751.5 | 582.8 | 749.1 | 652.1 | 573.9 | 718.7 | 574.3 | 231.7 | 318.1 | 328.2 | 294.9 | 294.1 | 342.5 | 326.1 | 288.8
789 | 644 | 469.3 | 187.72 | 219.4339 | 311.1 | 288.9 | 301.3 | 319.5 | 567.3 | 46 | 20.1 | 89.6 | 5.2 | 289.1 | 7.6 | 790.7 | 681.2 | 592.7 | 752.2 | 585.5 | 749.1 | 652.9 | 576.1 | 720.2 | 573.9 | 231.9 | 318.9 | 329.2 | 295.1 | 294.5 | 342.8 | 326.6 | 289.2
790 | 645 | 469.6 | 187.84 | 219.5741 | 312.6 | 288.5 | 302.5 | 319.4 | 559.6 | 46 | 20.1 | 89.8 | 5.3 | 269.9 | 9.8 | 792.5 | 692.8 | 612.3 | 755.1 | 589.5 | 749.2 | 646.7 | 585.7 | 721.6 | 576 | 232.2 | 320.1 | 330.4 | 295.4 | 294.8 | 343.2 | 326.9 | 289.4
791 | 646 | 470 | 188 | 219.7612 | 312.5 | 288.2 | 304 | 319.8 | 545.9 | 46.1 | 20.1 | 89.9 | 4.8 | 277.4 | 9.2 | 793 | 687 | 618.9 | 754.9 | 589.7 | 749 | 635.6 | 589 | 722.6 | 575.4 | 232.5 | 321 | 331 | 295.6 | 295 | 343.1 | 326.8 | 289.6
792 | 647 | 470.6 | 188.24 | 220.0417 | 312.2 | 287.9 | 304.6 | 320.2 | 540.2 | 46.2 | 20.1 | 90 | 4.9 | 252.9 | 7.6 | 795.6 | 697 | 628.5 | 757.4 | 593.1 | 748.9 | 629.5 | 598.6 | 723.8 | 576.5 | 232.7 | 322.1 | 331.4 | 296 | 295.2 | 343.3 | 326.8 | 289.8
793 | 648 | 469.8 | 187.92 | 219.6677 | 312.1 | 288.3 | 304.6 | 320.2 | 540.5 | 46.3 | 20.1 | 90.1 | 4.8 | 263.1 | 7.8 | 798 | 708.1 | 643.5 | 759.7 | 597.2 | 748.9 | 622.9 | 606.1 | 725 | 577 | 233 | 323 | 331.9 | 296.5 | 295.4 | 343.7 | 327.2 | 290.1
794 | 649 | 468.8 | 187.52 | 219.2001 | 312.7 | 288.9 | 305.3 | 319.7 | 544.1 | 46.4 | 20.1 | 90.1 | 5.4 | 274.7 | 7.4 | 802 | 723 | 659.4 | 764 | 601.7 | 749 | 619.4 | 624.1 | 726.5 | 579.2 | 233.3 | 323.1 | 332.1 | 296.9 | 295.7 | 343.8 | 327.3 | 290.4
795 | 650 | 470.5 | 188.2 | 219.995 | 314.2 | 289.4 | 306.4 | 318.6 | 529.4 | 46.3 | 20.1 | 90.2 | 5.4 | 259.8 | 6.4 | 804.9 | 725 | 679.9 | 765.6 | 605.4 | 748.8 | 613.5 | 628.6 | 727.6 | 580.5 | 233.5 | 323.4 | 332.4 | 297 | 296 | 343.3 | 327.2 | 290.7
796 | 651 | 470 | 188 | 219.7612 | 316 | 290.1 | 307.2 | 318.3 | 518.9 | 46.2 | 20.1 | 90.2 | 5.7 | 288.1 | 6 | 806.1 | 724.3 | 699 | 765.8 | 609.2 | 748.7 | 609.4 | 632.6 | 728.6 | 581 | 233.7 | 324.3 | 333.7 | 297.2 | 296.2 | 343.2 | 327.3 | 291
797 | 652 | 470.4 | 188.16 | 219.9482 | 316.9 | 289.8 | 308.7 | 318.2 | 514.8 | 46.2 | 20.1 | 90.3 | 6.5 | 274 | 6.5 | 804.4 | 717.6 | 691.5 | 764.4 | 608.8 | 748.9 | 603.7 | 629.2 | 728.9 | 580.6 | 234 | 325 | 334.3 | 297.5 | 296.4 | 343.3 | 327.3 | 291.2
798 | 653 | 470.3 | 188.12 | 219.9014 | 317.8 | 289.4 | 309.3 | 318.6 | 511.8 | 46.2 | 20.1 | 90.5 | 7.4 | 279.7 | 6.8 | 804.5 | 717.2 | 682.8 | 765.4 | 609.7 | 749.2 | 599.1 | 632.1 | 729.5 | 581.7 | 234.2 | 326.2 | 335.2 | 297.8 | 296.7 | 343.7 | 327.4 | 291.5
799 | 654 | 470 | 188 | 219.7612 | 314.7 | 288.7 | 309.5 | 318.6 | 511.7 | 46.3 | 20.1 | 90.7 | 7.8 | 305.8 | 7.7 | 804 | 719.7 | 679.6 | 765.9 | 611.5 | 749.5 | 596.7 | 627.9 | 729.8 | 581.6 | 234.5 | 326.9 | 335.7 | 298.2 | 296.9 | 344.1 | 327.6 | 291.7
800 | 655 | 469.7 | 187.88 | 219.6209 | 313.1 | 288.1 | 309.8 | 318.4 | 507.1 | 46.5 | 20.1 | 90.9 | 8 | 303 | 7.9 | 803 | 718.8 | 674.6 | 766.1 | 611.8 | 749.7 | 595.2 | 625.2 | 730.3 | 581.8 | 234.7 | 327.2 | 336 | 298.5 | 297.3 | 345 | 328 | 292.1
801 | 656 | 469.2 | 187.68 | 219.3871 | 313.4 | 288.1 | 309.7 | 317.6 | 513.3 | 46.7 | 20.1 | 91 | 8.6 | 321.4 | 7.1 | 802.1 | 709.3 | 666 | 765.5 | 611.7 | 750 | 592.7 | 622.2 | 731.1 | 581.7 | 235 | 327.3 | 336 | 298.8 | 297.8 | 345.1 | 328.4 | 292.5
802 | 657 | 468.3 | 187.32 | 218.9663 | 314.4 | 288.4 | 309 | 316.7 | 510.3 | 46.8 | 20.1 | 91.1 | 8.3 | 329 | 7.2 | 800.2 | 707.8 | 660.3 | 764.8 | 613.2 | 750.5 | 600.2 | 614.9 | 731.4 | 581.3 | 235.2 | 327.9 | 335.9 | 299.1 | 298 | 345.3 | 328.6 | 292.7
803 | 658 | 469 | 187.6 | 219.2936 | 316.6 | 288.8 | 308.9 | 315.2 | 508.5 | 46.8 | 20.1 | 91.2 | 8 | 326.8 | 8.3 | 800.8 | 713.8 | 658.8 | 766.1 | 613.6 | 751.1 | 597.8 | 617.3 | 732.7 | 581.4 | 235.4 | 328.2 | 336.5 | 299.4 | 298 | 345.6 | 328.5 | 292.9
804 | 659 | 469.3 | 187.72 | 219.4339 | 318.1 | 287.5 | 309.6 | 314.8 | 503.8 | 46.7 | 20.1 | 91.3 | 7.9 | 277 | 7.6 | 799 | 706.3 | 644.1 | 765.3 | 611.8 | 751.8 | 592.8 | 615.1 | 733.9 | 581 | 235.7 | 328.5 | 336.5 | 299.5 | 298.2 | 345.5 | 328.8 | 293.1
805 | 660 | 469.7 | 187.88 | 219.6209 | 318.7 | 286.7 | 309.4 | 315 | 508.1 | 46.6 | 20.1 | 91.4 | 7.5 | 245.4 | 7.1 | 796.4 | 696.8 | 621.3 | 763.4 | 609.4 | 752.3 | 591.7 | 604.7 | 733.8 | 579.8 | 235.9 | 329.3 | 336.3 | 299.5 | 298.4 | 345.4 | 329.1 | 293.4
806 | 661 | 469 | 187.6 | 219.2936 | 317.8 | 286.3 | 308.5 | 315.8 | 518.4 | 46.8 | 20.1 | 91.3 | 6.4 | 300.1 | 6.4 | 794.2 | 685.5 | 617.5 | 761.5 | 608.1 | 752.8 | 607.8 | 596.2 | 733.8 | 578.2 | 236.2 | 329.5 | 336.4 | 299.5 | 298.5 | 345.7 | 329.5 | 293.6
807 | 662 | 468.1 | 187.24 | 218.8728 | 316.9 | 285.8 | 308.6 | 316.4 | 522 | 47 | 20.1 | 91.1 | 5.9 | 290.5 | 7.8 | 791.7 | 677.5 | 599.3 | 759.7 | 605.9 | 753.4 | 611.3 | 591.8 | 734.1 | 577.5 | 236.4 | 329.9 | 336.2 | 299.5 | 298.7 | 346.1 | 330.2 | 293.8
808 | 663 | 468.3 | 187.32 | 218.9663 | 317.6 | 286 | 308.2 | 318 | 522.7 | 47.2 | 20.1 | 90.9 | 5.8 | 288.5 | 8.6 | 790.2 | 675.4 | 596.3 | 758.9 | 605.5 | 753.9 | 613 | 590.5 | 734.5 | 577.1 | 236.7 | 330 | 336.2 | 299.8 | 298.9 | 346.1 | 330.3 | 294.1
809 | 664 | 468.7 | 187.48 | 219.1533 | 317.1 | 285.5 | 308.7 | 318.3 | 525.6 | 47.3 | 20.1 | 90.7 | 5.6 | 284.5 | 9.1 | 788.8 | 673.5 | 592.2 | 758 | 603.9 | 754.5 | 618.4 | 589.8 | 735.3 | 576.6 | 236.9 | 329.6 | 336.4 | 300 | 299.1 | 346.7 | 330.5 | 294.4
810 | 665 | 468.9 | 187.56 | 219.2468 | 316.8 | 285.3 | 308.6 | 318.1 | 525.5 | 47.5 | 20.1 | 90.7 | 7 | 290.8 | 11.4 | 788.1 | 677.1 | 599 | 758.1 | 603.7 | 755 | 624.1 | 591.6 | 736 | 576.6 | 237.1 | 329.7 | 336.5 | 300 | 299.2 | 346.6 | 330.9 | 294.7
811 | 666 | 469.1 | 187.64 | 219.3403 | 317.6 | 285.7 | 309.5 | 318 | 522.1 | 47.6 | 20.1 | 90.7 | 7.3 | 286 | 12.6 | 787.3 | 676.2 | 603.1 | 757.3 | 602.9 | 755.4 | 626.5 | 589.9 | 736.5 | 576 | 237.4 | 329.6 | 336.7 | 300 | 299.3 | 346.3 | 331 | 295
812 | 667 | 468.9 | 187.56 | 219.2468 | 318.3 | 285.5 | 310.5 | 318 | 513.5 | 47.7 | 20.1 | 90.7 | 8.2 | 294.2 | 14 | 787.2 | 681.5 | 605.6 | 757.8 | 605.1 | 755.6 | 625.6 | 588.9 | 737.4 | 575.6 | 237.6 | 329.4 | 336.8 | 300.1 | 299.5 | 346.1 | 331.1 | 295.2
813 | 668 | 468.7 | 187.48 | 219.1533 | 319.9 | 286.2 | 310.8 | 317.8 | 511.1 | 47.6 | 20 | 90.8 | 8.8 | 291.5 | 14.8 | 788.9 | 683.1 | 608 | 758.9 | 605 | 755.8 | 623.1 | 592.2 | 738.1 | 575.7 | 237.9 | 330 | 337.3 | 300.5 | 299.6 | 346 | 331.4 | 295.4
814 | 669 | 467.4 | 186.96 | 218.5455 | 322.7 | 287.2 | 311.6 | 317.5 | 512.6 | 47.5 | 20 | 90.9 | 7.4 | 284.7 | 12.5 | 790.5 | 691.1 | 626.7 | 761 | 606.6 | 756 | 620.3 | 603.4 | 739.1 | 576.5 | 238.2 | 330.3 | 337.8 | 301.1 | 299.8 | 345.7 | 331.2 | 295.7
815 | 670 | 469.3 | 187.72 | 219.4339 | 325 | 287.9 | 311.9 | 317.7 | 507.3 | 47.4 | 20 | 91 | 5.8 | 273.1 | 12.1 | 792.9 | 696.1 | 626 | 761.8 | 606 | 756 | 614.6 | 609.5 | 740.1 | 576.8 | 238.4 | 330.6 | 338 | 301.7 | 299.9 | 346 | 331.2 | 295.8
816 | 671 | 469.7 | 187.88 | 219.6209 | 325.9 | 288.1 | 312.3 | 316.7 | 502.8 | 47.3 | 20 | 91.1 | 5.6 | 275.4 | 12.5 | 793 | 697.4 | 624 | 761.8 | 605.8 | 755.7 | 615.7 | 603.1 | 739.8 | 576.2 | 238.7 | 330.5 | 337.8 | 302 | 300.1 | 346.7 | 331.4 | 295.9
817 | 672 | 469.9 | 187.96 | 219.7144 | 325.1 | 287.7 | 311.8 | 316.2 | 500.7 | 47.3 | 20 | 91.2 | 6 | 269.5 | 11.9 | 794.9 | 699.8 | 611.2 | 762.4 | 605.6 | 755.5 | 615.7 | 602.7 | 739.6 | 576.3 | 238.9 | 330.5 | 337.5 | 302.2 | 300.4 | 346.7 | 332.1 | 296.1
818 | 673 | 470.2 | 188.08 | 219.8547 | 324.4 | 287.7 | 310.7 | 317.4 | 497.9 | 47.4 | 20 | 91.3 | 6.6 | 264.4 | 10.4 | 795.7 | 699.4 | 602.9 | 762.4 | 605 | 755.5 | 611.7 | 600.7 | 739.3 | 576 | 239.2 | 330.6 | 337.3 | 302.3 | 300.7 | 346.9 | 332.4 | 296.4
819 | 674 | 469.1 | 187.64 | 219.3403 | 323.1 | 287.9 | 309.6 | 318.4 | 493.6 | 47.5 | 20 | 91.4 | 7.4 | 269.7 | 9.3 | 795.1 | 694.3 | 600.1 | 760.9 | 604.3 | 755.3 | 607.4 | 600.5 | 738.6 | 575.4 | 239.4 | 330.5 | 336.9 | 302.7 | 300.9 | 346.3 | 332.2 | 296.6
820 | 675 | 470.3 | 188.12 | 219.9014 | 323.1 | 288.9 | 309.5 | 319 | 494.5 | 47.5 | 20 | 91.4 | 7.2 | 264.6 | 11 | 796.1 | 700.9 | 611.6 | 761.2 | 606.4 | 755 | 602.7 | 613.4 | 738.8 | 576 | 239.6 | 330.2 | 336.8 | 302.9 | 300.9 | 345.6 | 332 | 296.6
821 | 676 | 469.5 | 187.8 | 219.5274 | 323.4 | 289.5 | 309.5 | 318.9 | 493.7 | 47.6 | 20 | 91.3 | 7.3 | 255.1 | 10.5 | 797.6 | 699.6 | 625.6 | 760.8 | 607.9 | 754.7 | 598.1 | 618 | 739.1 | 576.7 | 239.9 | 329.8 | 336.4 | 302.9 | 301 | 344.9 | 331.6 | 296.8
822 | 677 | 468.9 | 187.56 | 219.2468 | 321.5 | 289.5 | 309.4 | 318.4 | 491.5 | 47.8 | 20 | 91.4 | 6.2 | 258.8 | 11.2 | 798.5 | 702 | 624.7 | 760.7 | 608.7 | 754.4 | 596.8 | 617 | 739.7 | 576.2 | 240.1 | 329.3 | 336.4 | 302.9 | 301.2 | 344.6 | 331.3 | 297
823 | 678 | 471.1 | 188.44 | 220.2755 | 318.8 | 289.8 | 308.5 | 318.2 | 489.2 | 47.9 | 20 | 91.6 | 6.5 | 259.5 | 12.5 | 798.1 | 704.8 | 625.3 | 760.2 | 609.4 | 754.2 | 600.7 | 612.7 | 740 | 576.1 | 240.3 | 329.2 | 336.1 | 303 | 301.2 | 344.5 | 332.1 | 297.1
824 | 679 | 472.4 | 188.96 | 220.8834 | 317.3 | 289.1 | 307.3 | 317.6 | 490.4 | 48 | 20 | 91.6 | 7.1 | 263.4 | 12 | 797.6 | 700.8 | 618.4 | 759 | 609 | 754 | 599.9 | 607.9 | 739.9 | 575.6 | 240.6 | 329.6 | 336.3 | 303.3 | 301.3 | 344 | 332.2 | 297.3
825 | 680 | 472.7 | 189.08 | 221.0236 | 315.8 | 288.2 | 307 | 316.6 | 486.1 | 48.1 | 20 | 91.7 | 6.5 | 254.5 | 11.2 | 794.9 | 685.4 | 595.8 | 756.1 | 606.3 | 753.9 | 599 | 597.2 | 739.4 | 574.5 | 240.9 | 329.4 | 336.1 | 303.4 | 301.4 | 343.4 | 331.8 | 297.5
826 | 681 | 471.2 | 188.48 | 220.3223 | 319.6 | 287.9 | 306.8 | 315.7 | 486.9 | 48 | 20 | 91.8 | 5 | 258.5 | 11.3 | 790.7 | 675.3 | 580.5 | 753.5 | 604.4 | 754 | 610.3 | 589.8 | 739.2 | 573.1 | 241.1 | 328.7 | 335 | 303.3 | 301.5 | 343 | 331.7 | 297.7
827 | 682 | 470.5 | 188.2 | 219.995 | 322 | 287.6 | 305.9 | 316.4 | 483.9 | 47.8 | 20 | 91.8 | 4.5 | 233.4 | 13.2 | 788.8 | 681.6 | 578.7 | 753.5 | 605 | 754.4 | 607.9 | 591.2 | 739.4 | 573.1 | 241.4 | 328 | 334.2 | 303.2 | 301.7 | 342.9 | 331.7 | 297.9
828 | 683 | 470.1 | 188.04 | 219.8079 | 320.8 | 287.1 | 305.4 | 317.3 | 477.3 | 47.7 | 20 | 91.9 | 5.9 | 232.1 | 13 | 790 | 692 | 580.7 | 755.7 | 605.6 | 755 | 605.1 | 603.2 | 740.3 | 574.6 | 241.6 | 327.5 | 333.4 | 303.2 | 301.8 | 343.1 | 331.6 | 298
829 | 684 | 470 | 188 | 219.7612 | 319.9 | 285.8 | 305.1 | 317.1 | 473.7 | 47.8 | 20 | 92 | 6.3 | 240.4 | 12.8 | 789.9 | 690 | 577.8 | 755.7 | 604 | 755.2 | 604.3 | 601.7 | 740.8 | 574.6 | 241.9 | 326.9 | 332.9 | 303.1 | 301.9 | 343.2 | 331.6 | 298.2
830 | 685 | 469.4 | 187.76 | 219.4806 | 320.5 | 284.8 | 304.7 | 315.7 | 471.2 | 47.9 | 20 | 92 | 6.6 | 253.7 | 11.6 | 787.5 | 674.9 | 563 | 753.3 | 602 | 755.3 | 607.3 | 594.8 | 741.2 | 573.5 | 242.1 | 326.4 | 332.6 | 303.1 | 302.1 | 343.5 | 331.7 | 298.4
831 | 686 | 470 | 188 | 219.7612 | 319.1 | 284 | 305.3 | 315.8 | 468.4 | 48 | 20 | 92 | 7.4 | 261.1 | 12.8 | 786.2 | 672.2 | 567.9 | 751.5 | 601.7 | 755.2 | 611.2 | 588.5 | 741 | 572.2 | 242.4 | 326.1 | 332.4 | 303.2 | 302.2 | 343 | 331.7 | 298.6
832 | 687 | 470 | 188 | 219.7612 | 318.5 | 284 | 305.7 | 316.2 | 469.9 | 48.1 | 20 | 92 | 6.2 | 257.2 | 12.9 | 783 | 662.8 | 563.6 | 749 | 599.8 | 755.1 | 610 | 582.3 | 740.6 | 571.4 | 242.6 | 326.3 | 333.7 | 303.3 | 302.4 | 342.7 | 332 | 298.8
833 | 688 | 470.6 | 188.24 | 220.0417 | 319.7 | 283.6 | 306 | 315.2 | 472.2 | 48.1 | 20 | 91.9 | 5.4 | 259.7 | 11.5 | 779.5 | 650.4 | 548.6 | 746.6 | 597.3 | 755.1 | 621.3 | 574.4 | 739.9 | 570.1 | 242.9 | 326.7 | 335.3 | 303.7 | 302.7 | 342.4 | 332.3 | 299.1
834 | 689 | 471 | 188.4 | 220.2287 | 320.9 | 283.8 | 307.1 | 314 | 475.5 | 48 | 20 | 91.8 | 5.3 | 259.8 | 10.7 | 776.6 | 641.3 | 542.2 | 744.3 | 595.3 | 755 | 633.9 | 567.3 | 739.5 | 568.9 | 243.1 | 326.7 | 336.3 | 303.8 | 302.9 | 342.4 | 332.6 | 299.4
835 | 690 | 469.6 | 187.84 | 219.5741 | 322.9 | 284.9 | 307.5 | 313.5 | 477.4 | 48.1 | 20 | 91.7 | 4.9 | 259.1 | 10.7 | 775.8 | 643.6 | 563.1 | 743.4 | 596.4 | 754.8 | 637.4 | 566.8 | 739.3 | 568 | 243.3 | 326.9 | 336.9 | 304 | 303 | 342.4 | 332.9 | 299.6
836 | 691 | 469.4 | 187.76 | 219.4806 | 323.6 | 285.8 | 308.6 | 314.8 | 480.2 | 48.2 | 20 | 91.7 | 4.4 | 269.9 | 12.1 | 776.4 | 651 | 564.6 | 744.1 | 595.7 | 754.8 | 631.4 | 573.3 | 739.7 | 567.8 | 243.5 | 327.5 | 337 | 304.4 | 303.3 | 342.6 | 333.3 | 299.7
837 | 692 | 470.6 | 188.24 | 220.0417 | 322.7 | 286.2 | 309.6 | 315.6 | 478.6 | 48.3 | 20 | 91.7 | 4.6 | 268.8 | 13.3 | 777 | 657.9 | 579.4 | 744.8 | 596.9 | 754.7 | 623 | 579 | 740.4 | 567.8 | 243.7 | 327.6 | 336.9 | 304.8 | 303.6 | 342.5 | 333.4 | 299.9
838 | 693 | 469.9 | 187.96 | 219.7144 | 323.3 | 287 | 309.5 | 315.4 | 474.1 | 48.4 | 20 | 91.7 | 5.1 | 261 | 12.7 | 775.5 | 655.3 | 574.5 | 743.7 | 594.8 | 754.3 | 617.6 | 577 | 740.3 | 567.3 | 244 | 327.7 | 336.6 | 304.9 | 303.7 | 342.3 | 333.4 | 300
839 | 694 | 469.8 | 187.92 | 219.6677 | 323.1 | 287.3 | 308.8 | 315.2 | 470 | 48.4 | 20 | 91.7 | 4.9 | 266.5 | 10.8 | 775.3 | 658.7 | 586.4 | 743 | 596.2 | 753.9 | 610.7 | 578.2 | 740.5 | 566.6 | 244.2 | 327.8 | 336.3 | 304.9 | 303.8 | 342.2 | 333.3 | 300.2
840 | 695 | 469.5 | 187.8 | 219.5274 | 322 | 287.3 | 308.1 | 315.6 | 462.9 | 48.5 | 20 | 91.8 | 5.3 | 285.1 | 9.9 | 775.1 | 666.9 | 580.3 | 743.2 | 596.1 | 753.7 | 604.9 | 582.3 | 740.8 | 567 | 244.4 | 327.9 | 336.2 | 305 | 303.8 | 341.9 | 333.2 | 300.3
841 | 696 | 470.1 | 188.04 | 219.8079 | 321.2 | 286.7 | 307 | 314.7 | 459.7 | 48.5 | 20 | 91.9 | 5.9 | 269.5 | 9.8 | 775 | 663.3 | 567.9 | 743 | 595 | 753.4 | 602.3 | 578.3 | 740.4 | 566.4 | 244.6 | 327.9 | 336.2 | 305.2 | 303.8 | 341.7 | 333.5 | 300.5
842 | 697 | 469.8 | 187.92 | 219.6677 | 320.6 | 285.8 | 306.5 | 313.7 | 461.6 | 48.5 | 20 | 92 | 6 | 282.6 | 9.3 | 773 | 655.7 | 561.5 | 741.6 | 593.3 | 752.9 | 607.6 | 571.6 | 740.1 | 565.6 | 244.9 | 327.8 | 336 | 305.2 | 303.9 | 341.3 | 333.4 | 300.7
843 | 698 | 469.2 | 187.68 | 219.3871 | 321.3 | 285.8 | 305.7 | 313.4 | 466.3 | 48.6 | 20 | 92.2 | 5.7 | 276.3 | 8.6 | 773.6 | 657.5 | 573.8 | 741.9 | 594.6 | 752.7 | 611.4 | 573.1 | 740.6 | 565.2 | 245.1 | 327.9 | 335.8 | 305.2 | 304 | 341.3 | 333.2 | 300.8
844 | 699 | 471.4 | 188.56 | 220.4158 | 322.1 | 286 | 305.7 | 312.9 | 467.8 | 48.6 | 20 | 92.4 | 5.4 | 278.1 | 8.4 | 773.9 | 659.8 | 569.9 | 742 | 593.2 | 752.5 | 614.2 | 570.8 | 740.6 | 564.8 | 245.4 | 327.7 | 335.5 | 305.3 | 304.1 | 341.3 | 332.9 | 300.9
845 | 700 | 470.1 | 188.04 | 219.8079 | 324.8 | 285.4 | 305.9 | 311.5 | 465.8 | 48.6 | 20 | 92.4 | 5.6 | 263.6 | 8.4 | 773.9 | 659.8 | 562.6 | 741.9 | 592.9 | 752.2 | 611.9 | 569.5 | 741.1 | 564.4 | 245.6 | 328 | 335.3 | 305.3 | 304.3 | 341.2 | 332.7 | 301
846 | 701 | 468.9 | 187.56 | 219.2468 | 324.5 | 285.6 | 306.1 | 311.1 | 467.1 | 48.5 | 20 | 92.5 | 5.8 | 222.3 | 7.2 | 773.1 | 650.1 | 549.1 | 740.5 | 590.5 | 751.9 | 619 | 564.9 | 740.5 | 563.3 | 245.9 | 328.3 | 335.2 | 305.7 | 304.6 | 341 | 332.5 | 301.2
847 | 702 | 469.9 | 187.96 | 219.7144 | 324.1 | 285.5 | 307.2 | 310.5 | 474.1 | 48.5 | 20 | 92.6 | 5.5 | 256.2 | 7.7 | 771 | 636.6 | 534.3 | 738.1 | 588.4 | 751.6 | 633.3 | 558.7 | 740.3 | 562.3 | 246.1 | 328.7 | 335.5 | 306.3 | 304.7 | 340.9 | 332.2 | 301.2
848 | 703 | 470 | 188 | 219.7612 | 324.4 | 285.1 | 309 | 310.9 | 475.4 | 48.6 | 20 | 92.6 | 5.5 | 264.3 | 8.7 | 768.6 | 629.6 | 537 | 736 | 586.6 | 751.3 | 648.4 | 556.4 | 740 | 561.3 | 246.4 | 329.2 | 336 | 307 | 304.8 | 340.8 | 331.9 | 301.3
849 | 704 | 469.6 | 187.84 | 219.5741 | 325.9 | 285.6 | 310 | 310.9 | 476.1 | 48.6 | 20 | 92.6 | 5.5 | 267.7 | 8.6 | 769.9 | 643.2 | 557 | 736.8 | 587.3 | 751.3 | 644 | 564.9 | 739.9 | 561.5 | 246.6 | 329.7 | 336.4 | 307.2 | 304.9 | 340.6 | 331.4 | 301.4
850 | 705 | 469.7 | 187.88 | 219.6209 | 326.8 | 286.7 | 310.3 | 310.1 | 474.8 | 48.6 | 20 | 92.7 | 5.8 | 289.9 | 7.6 | 772.3 | 650.1 | 577.5 | 737.8 | 588.4 | 751.2 | 638.9 | 578.6 | 740.5 | 562.1 | 246.9 | 330 | 336.3 | 307.5 | 304.9 | 340.4 | 330.9 | 301.4
851 | 706 | 470.3 | 188.12 | 219.9014 | 327.3 | 287.7 | 310 | 310.8 | 483.2 | 48.6 | 20 | 92.9 | 6 | 283.2 | 7.1 | 775.6 | 657.1 | 589.3 | 738.5 | 587.9 | 751 | 635.8 | 584 | 740.8 | 562.1 | 247.2 | 329.8 | 336.2 | 307.8 | 305.1 | 340.4 | 330.7 | 301.6
852 | 707 | 470.6 | 188.24 | 220.0417 | 326.7 | 288.8 | 309.9 | 312 | 480.4 | 48.7 | 20 | 93 | 5.8 | 271.1 | 7.6 | 777.5 | 660.4 | 604.2 | 739.1 | 588.6 | 750.7 | 627.9 | 587.4 | 740.9 | 561.9 | 247.4 | 330.1 | 335.9 | 307.9 | 305.2 | 340.4 | 330.4 | 301.7
853 | 708 | 469.9 | 187.96 | 219.7144 | 326.1 | 290.7 | 309.8 | 313.7 | 478.6 | 48.8 | 20 | 93.1 | 5.3 | 260.5 | 8.7 | 777.2 | 659.8 | 592.8 | 738.9 | 588 | 750.4 | 621.9 | 582.6 | 740.9 | 561.3 | 247.7 | 330.4 | 336 | 308.2 | 305.4 | 341 | 330.1 | 301.8
854 | 709 | 469.5 | 187.8 | 219.5274 | 325.1 | 292.1 | 310.3 | 315.3 | 477 | 48.8 | 20 | 93.2 | 4.9 | 257.7 | 9.5 | 776.5 | 654.5 | 575.8 | 738.1 | 586.5 | 750 | 616.8 | 579 | 740.6 | 560.8 | 247.9 | 330.3 | 336 | 308.3 | 305.5 | 342.8 | 329.9 | 301.9
855 | 710 | 470.5 | 188.2 | 219.995 | 323.7 | 292.6 | 310.8 | 316.5 | 474.2 | 48.8 | 20 | 93.2 | 5.3 | 232.4 | 8.6 | 776.6 | 660.5 | 582.8 | 738.5 | 586.6 | 749.7 | 618.8 | 584 | 740.9 | 560.8 | 248.2 | 330.1 | 335.8 | 308.4 | 305.7 | 344 | 330 | 302.1
856 | 711 | 469.5 | 187.8 | 219.5274 | 320.3 | 292.4 | 311.1 | 316.9 | 474.6 | 48.7 | 20 | 93.2 | 5.3 | 227.5 | 6.5 | 777 | 665.3 | 583.1 | 739.2 | 586.5 | 749.4 | 613.7 | 588.9 | 741.4 | 561.4 | 248.5 | 329.7 | 335.4 | 308.6 | 305.9 | 344.6 | 330.1 | 302.3
857 | 712 | 470.3 | 188.12 | 219.9014 | 319 | 291.8 | 311 | 316.9 | 479.2 | 48.7 | 19.9 | 93.1 | 5.2 | 253.7 | 6 | 778.3 | 666.4 | 598.2 | 739.3 | 587.1 | 749.1 | 612.5 | 593.3 | 742.1 | 561.4 | 248.7 | 330.4 | 335.6 | 309 | 306.1 | 344.5 | 330.2 | 302.5
858 | 713 | 469.1 | 187.64 | 219.3403 | 319.8 | 292.4 | 309.8 | 317.1 | 484.5 | 48.7 | 19.9 | 93 | 4.9 | 244.2 | 6 | 781.1 | 682.8 | 617.8 | 741.3 | 590.9 | 748.8 | 610.5 | 598.2 | 743.2 | 562.4 | 248.9 | 330.5 | 335.8 | 309.3 | 306.2 | 344.4 | 330.2 | 302.7
859 | 714 | 469.7 | 187.88 | 219.6209 | 320.2 | 293.5 | 308.6 | 317.6 | 483.3 | 48.8 | 19.9 | 93 | 4.8 | 264.8 | 6 | 783 | 684.7 | 630.8 | 741.5 | 591.9 | 748.5 | 604.9 | 601.9 | 743.8 | 562.6 | 249.1 | 330.6 | 335.9 | 309.4 | 306.3 | 344.4 | 329.9 | 302.8
860 | 715 | 469.6 | 187.84 | 219.5741 | 321 | 293.1 | 309.5 | 316.8 | 483.2 | 48.9 | 19.9 | 92.9 | 5.1 | 261.6 | 5.6 | 783.9 | 687.1 | 637.5 | 741.4 | 593 | 748.1 | 599.4 | 599.8 | 743.5 | 562.5 | 249.4 | 331.3 | 336.6 | 309.8 | 306.4 | 344.3 | 329.7 | 302.9
861 | 716 | 469 | 187.6 | 219.2936 | 322.2 | 293.3 | 311.4 | 316.1 | 486.5 | 49 | 19.9 | 92.8 | 5 | 235.7 | 5 | 783.3 | 682.7 | 644.5 | 739.8 | 593.4 | 747.8 | 594.2 | 599 | 743.9 | 561.8 | 249.6 | 331.5 | 337.6 | 310 | 306.5 | 344.1 | 329.4 | 302.9
862 | 717 | 470.1 | 188.04 | 219.8079 | 322.6 | 293.2 | 312.3 | 317 | 488.3 | 49.1 | 19.9 | 92.7 | 5.5 | 277.2 | 4.3 | 783.3 | 683.7 | 637.9 | 739.9 | 593 | 747.5 | 594.7 | 603.2 | 744.2 | 562.3 | 249.9 | 331.5 | 338.2 | 310 | 306.5 | 343.9 | 329.3 | 303.1
863 | 718 | 471.2 | 188.48 | 220.3223 | 322.6 | 293 | 312.5 | 317.8 | 486.3 | 49.1 | 19.9 | 92.7 | 5.6 | 268 | 5.2 | 784.6 | 692.7 | 635.7 | 741.7 | 593.4 | 747.4 | 593.7 | 605.7 | 744.5 | 562.7 | 250.2 | 332 | 338.8 | 310.3 | 306.5 | 343.8 | 329.5 | 303.2
864 | 719 | 470 | 188 | 219.7612 | 323.3 | 293 | 312.6 | 318 | 483.7 | 49.2 | 19.9 | 92.6 | 5.6 | 264.6 | 8.1 | 784.9 | 696.2 | 630 | 742 | 593.8 | 747.3 | 594.8 | 608.2 | 744.3 | 563.1 | 250.4 | 332.3 | 338.9 | 310.4 | 306.7 | 343.4 | 329.7 | 303.4
865 | 720 | 469.1 | 187.64 | 219.3403 | 322.1 | 292.2 | 313.1 | 317.6 | 480.2 | 49.3 | 19.9 | 92.5 | 5.3 | 261.1 | 9.5 | 782.9 | 696.9 | 629.4 | 741.2 | 593.9 | 747.3 | 595.7 | 603.7 | 744.5 | 562.9 | 250.7 | 332.4 | 338.9 | 310.5 | 306.9 | 343.4 | 329.9 | 303.6
866 | 721 | 469.2 | 187.68 | 219.3871 | 319.5 | 291 | 312.3 | 317 | 475.4 | 49.3 | 19.9 | 92.3 | 5.5 | 254.4 | 10 | 779.8 | 690.8 | 623.2 | 739.8 | 593.5 | 747.1 | 593.2 | 597.7 | 744.8 | 562.6 | 251 | 331.9 | 338.7 | 310.4 | 307.1 | 343.5 | 330 | 303.7
867 | 722 | 470.1 | 188.04 | 219.8079 | 318 | 290.1 | 310.8 | 317.3 | 470.3 | 49.3 | 19.9 | 92.2 | 6.6 | 274.3 | 9.8 | 779 | 701.3 | 634.3 | 741.1 | 594.7 | 747.2 | 594.8 | 598.9 | 745.4 | 562.9 | 251.3 | 331.8 | 338.6 | 310.2 | 307.3 | 343.4 | 330.1 | 303.9
868 | 723 | 469.7 | 187.88 | 219.6209 | 316.8 | 289.8 | 309.8 | 316.6 | 468.6 | 49.3 | 19.9 | 92.2 | 7 | 275 | 10.5 | 778.1 | 693.9 | 620.6 | 740.4 | 593.2 | 747.2 | 592 | 595.5 | 745.6 | 562.6 | 251.6 | 331.1 | 337.9 | 310.2 | 307.5 | 343.3 | 330.1 | 304
869 | 724 | 470.7 | 188.28 | 220.0885 | 314.2 | 289.1 | 309.4 | 314.9 | 467.3 | 49.3 | 19.9 | 92.3 | 7.4 | 272.3 | 11.4 | 776.6 | 676 | 603.8 | 738.7 | 591.7 | 746.9 | 591 | 591.3 | 744.9 | 561.9 | 251.9 | 330.4 | 337.1 | 310.2 | 307.6 | 342.9 | 329.8 | 304.1
870 | 725 | 469.6 | 187.84 | 219.5741 | 314.1 | 288.3 | 308 | 313.5 | 465.5 | 49.4 | 19.9 | 92.3 | 7.4 | 270.3 | 11.8 | 775.2 | 664.9 | 592.6 | 737 | 590.7 | 746.5 | 604 | 585.2 | 744.1 | 560.9 | 252.2 | 330 | 336.3 | 310.2 | 307.7 | 342.5 | 329.5 | 304.1
871 | 726 | 470.4 | 188.16 | 219.9482 | 315.2 | 288 | 306.9 | 312.8 | 463.2 | 49.4 | 19.9 | 92.3 | 6.8 | 261.3 | 12.7 | 774.1 | 659.8 | 591.8 | 736 | 590.2 | 746.4 | 605.1 | 588 | 743.4 | 560.5 | 252.4 | 329.4 | 335.6 | 310.3 | 307.7 | 342.1 | 329 | 304.2
872 | 727 | 470.1 | 188.04 | 219.8079 | 316.7 | 288.2 | 305.7 | 311.8 | 464 | 49.4 | 19.9 | 92.3 | 6.1 | 258.8 | 14 | 776.3 | 676.1 | 604.5 | 737.5 | 591.5 | 746.4 | 604.9 | 598.3 | 743.6 | 561.1 | 252.6 | 328.2 | 334.8 | 310.4 | 307.7 | 341.4 | 328.5 | 304.2
873 | 728 | 469.7 | 187.88 | 219.6209 | 317.5 | 288.5 | 304.4 | 311 | 466.8 | 49.4 | 19.9 | 92.4 | 6.1 | 262.6 | 13.7 | 777.8 | 675.3 | 593.8 | 737.7 | 590.8 | 746.3 | 606.4 | 600.6 | 743.8 | 561.3 | 252.9 | 327.5 | 333.8 | 310.4 | 307.8 | 341.2 | 328.1 | 304.3
874 | 729 | 468.2 | 187.28 | 218.9195 | 317.1 | 288.7 | 303.4 | 310.4 | 465.6 | 49.5 | 19.9 | 92.5 | 5.5 | 266.9 | 13.5 | 775.3 | 663.8 | 583.8 | 735.6 | 588.9 | 745.8 | 611.4 | 592.7 | 743.3 | 559.8 | 253.2 | 326.6 | 332.9 | 310.2 | 307.8 | 340.2 | 327.7 | 304.3
875 | 730 | 468.4 | 187.36 | 219.013 | 317.5 | 288.9 | 301.9 | 310.1 | 464.5 | 49.6 | 19.9 | 92.6 | 5.3 | 269 | 12 | 773.9 | 665.4 | 571.8 | 734.3 | 588.1 | 745.5 | 613.1 | 591.2 | 743.6 | 559.1 | 253.5 | 325.7 | 332.2 | 310.1 | 307.9 | 339.8 | 327.3 | 304.3
876 | 731 | 469.3 | 187.72 | 219.4339 | 316.4 | 288.7 | 300.1 | 309.4 | 464.3 | 49.6 | 19.9 | 92.7 | 5 | 280.7 | 12 | 773.1 | 668.5 | 564.7 | 734.2 | 587.5 | 745.3 | 609.6 | 592.1 | 744 | 558.8 | 253.9 | 325.2 | 331.9 | 310.1 | 307.9 | 339.2 | 326.8 | 304.4
877 | 732 | 468.9 | 187.56 | 219.2468 | 315.2 | 288.3 | 299.6 | 309.4 | 462.5 | 49.7 | 19.9 | 92.8 | 5.7 | 282.9 | 13.9 | 772.6 | 667.2 | 564.5 | 733.6 | 587.3 | 745.2 | 606.7 | 592.1 | 744.2 | 558.6 | 254.2 | 324.4 | 331.2 | 310 | 308 | 338.7 | 326.3 | 304.4
878 | 733 | 469.2 | 187.68 | 219.3871 | 314.8 | 288.1 | 298.9 | 310.5 | 458.5 | 49.8 | 19.9 | 92.9 | 5.6 | 287.5 | 14.1 | 769.7 | 653.1 | 555.5 | 730.9 | 585.2 | 744.6 | 603.3 | 586 | 744.3 | 557.4 | 254.5 | 323.7 | 330.3 | 309.8 | 308.1 | 338.2 | 325.8 | 304.5
879 | 734 | 468 | 187.2 | 218.826 | 316.9 | 287.7 | 297.3 | 310.6 | 457.3 | 49.8 | 19.9 | 93 | 6.1 | 276 | 14.5 | 765.3 | 636.4 | 545.5 | 727 | 582.7 | 744.5 | 613.9 | 579.1 | 744.2 | 556.3 | 254.8 | 323 | 329.6 | 309.6 | 308.1 | 338.1 | 325.8 | 304.6
880 | 735 | 468.6 | 187.44 | 219.1066 | 318.1 | 287.4 | 296.5 | 310.6 | 456.9 | 49.8 | 19.9 | 93.1 | 6.6 | 251.9 | 12.3 | 760.1 | 623.5 | 538.4 | 724.4 | 580.2 | 744.2 | 636.6 | 573.9 | 743.6 | 555.4 | 255 | 321.7 | 328.7 | 309.5 | 308.2 | 338.1 | 325.7 | 304.6
881 | 736 | 467.7 | 187.08 | 218.6857 | 318.5 | 286.8 | 295.8 | 311 | 456.7 | 49.7 | 19.9 | 93.2 | 6.8 | 260.4 | 11.2 | 756.9 | 618.3 | 531.5 | 722.6 | 578.6 | 743.6 | 647.9 | 571.4 | 743.5 | 554.4 | 255.3 | 320.9 | 328.1 | 309.5 | 308.2 | 338 | 325.4 | 304.7
882 | 737 | 468 | 187.2 | 218.826 | 318.5 | 286.4 | 295.8 | 311.2 | 456.9 | 49.7 | 19.9 | 93.3 | 6.3 | 237.9 | 14.8 | 755.9 | 614.1 | 533.8 | 721 | 577.6 | 742.8 | 661.8 | 568.7 | 743.2 | 553.4 | 255.5 | 320.4 | 327.6 | 309.6 | 308.2 | 337.4 | 324.9 | 304.7
883 | 738 | 469 | 187.6 | 219.2936 | 316.4 | 286.1 | 295.8 | 311.4 | 456.8 | 49.8 | 19.9 | 93.5 | 6.8 | 244.9 | 14.6 | 756.1 | 618.6 | 542.6 | 719.8 | 577.1 | 742.5 | 659.7 | 570 | 743.1 | 553.1 | 255.8 | 320.2 | 327 | 309.8 | 308.2 | 337.9 | 324.7 | 304.8
884 | 739 | 469.2 | 187.68 | 219.3871 | 315.7 | 286.3 | 295.2 | 311.4 | 460.1 | 49.7 | 19.9 | 93.7 | 7.3 | 247.2 | 14.2 | 756.2 | 619.3 | 538.4 | 719.3 | 576.2 | 742.3 | 660.6 | 568.3 | 742.8 | 552.9 | 256.1 | 319.6 | 326.3 | 309.9 | 308.2 | 337.6 | 324.6 | 304.9
885 | 740 | 469 | 187.6 | 219.2936 | 317.1 | 286.3 | 294.7 | 311.2 | 462.1 | 49.7 | 19.9 | 93.9 | 7.4 | 262.4 | 16.6 | 755.7 | 618.6 | 531.8 | 718.8 | 575.4 | 741.9 | 656.8 | 566.9 | 742.2 | 552.4 | 256.3 | 318.7 | 325.5 | 309.9 | 308.1 | 337 | 324.3 | 304.9
886 | 741 | 469 | 187.6 | 219.2936 | 315.5 | 287.1 | 293.7 | 310.2 | 465.4 | 49.7 | 19.9 | 94.1 | 6.6 | 257.3 | 14.2 | 754.3 | 617.7 | 528.1 | 717.5 | 574.8 | 741.3 | 661.9 | 565.1 | 742.1 | 551.3 | 256.6 | 317.8 | 324.6 | 309.7 | 308.1 | 336.3 | 324.3 | 304.9
887 | 742 | 468.9 | 187.56 | 219.2468 | 314.9 | 287.4 | 292.6 | 309.1 | 460.9 | 49.8 | 19.9 | 94.2 | 6.9 | 251.6 | 12.3 | 752.2 | 614.4 | 520.7 | 716.3 | 572.9 | 740.8 | 660.1 | 563.4 | 742.5 | 550.7 | 256.9 | 316 | 323.3 | 309.4 | 308.2 | 337.2 | 324.4 | 304.9
888 | 743 | 468.9 | 187.56 | 219.2468 | 314.6 | 287.3 | 291.7 | 308.5 | 453.8 | 50 | 19.9 | 94.4 | 6.6 | 272.8 | 11.9 | 750.5 | 609.7 | 526.2 | 715 | 571.9 | 740.4 | 655.5 | 561.4 | 742.5 | 549.8 | 257.1 | 315.4 | 323.5 | 309.3 | 308.4 | 337.5 | 324.3 | 305
889 | 744 | 469.1 | 187.64 | 219.3403 | 315 | 286.9 | 291.5 | 308.2 | 448.5 | 49.9 | 19.9 | 94.6 | 7.4 | 283.4 | 12.8 | 751.5 | 611.4 | 520.7 | 715.2 | 571.7 | 740.4 | 650.7 | 564.7 | 741.9 | 550 | 257.4 | 315.2 | 323.3 | 309.5 | 308.5 | 337.1 | 324.2 | 305.1
890 | 745 | 469.8 | 187.92 | 219.6677 | 314.9 | 286.3 | 291.8 | 307.4 | 447.8 | 49.7 | 19.9 | 94.7 | 7.9 | 283.4 | 16.4 | 749.9 | 607.6 | 521.4 | 714 | 570.1 | 739.5 | 651.4 | 561.3 | 741.3 | 549 | 257.6 | 315.4 | 323.3 | 309.9 | 308.5 | 336.8 | 323.8 | 305.1
891 | 746 | 469.1 | 187.64 | 219.3403 | 314.6 | 286 | 292.2 | 306.7 | 448.3 | 49.8 | 19.8 | 94.9 | 8.3 | 281.7 | 16.1 | 749.4 | 605.7 | 527.6 | 713.4 | 569.3 | 739 | 650 | 562.2 | 740.8 | 548.5 | 257.9 | 314.7 | 323.1 | 310.2 | 308.4 | 336.1 | 323.1 | 305
892 | 747 | 469.8 | 187.92 | 219.6677 | 314.4 | 287 | 292.4 | 306.8 | 457.6 | 49.9 | 19.9 | 95.1 | 8.6 | 278.3 | 15 | 750.2 | 606.7 | 520.1 | 713.4 | 569.3 | 738.3 | 644.3 | 561.7 | 740.5 | 547.9 | 258.1 | 314.1 | 322.3 | 310.2 | 308.3 | 335.5 | 322.7 | 305
893 | 748 | 470.1 | 188.04 | 219.8079 | 314 | 288 | 291.8 | 306.5 | 459.6 | 50 | 19.9 | 95.3 | 9.4 | 277.5 | 16.7 | 749.6 | 612.6 | 524.9 | 713.4 | 568.5 | 737.6 | 640.2 | 563.4 | 740.5 | 547.5 | 258.4 | 313.7 | 321.8 | 310.1 | 308.3 | 335.2 | 322.6 | 305
894 | 749 | 470.9 | 188.36 | 220.182 | 313.7 | 287.7 | 291 | 306.8 | 456.9 | 50.1 | 19.9 | 95.4 | 9.3 | 270.5 | 18.2 | 750.3 | 625.3 | 532.6 | 714.6 | 568.9 | 737.3 | 635.2 | 569.1 | 740.8 | 547.6 | 258.6 | 313.6 | 321.5 | 310 | 308.4 | 335.6 | 322.9 | 305.1
895 | 750 | 469.8 | 187.92 | 219.6677 | 314.2 | 287.8 | 290.6 | 306.8 | 453.7 | 50.2 | 19.8 | 95.4 | 7.4 | 258.6 | 16.5 | 749 | 623.8 | 538.3 | 714.1 | 568.2 | 736.8 | 632.8 | 569.7 | 741.1 | 547.4 | 258.8 | 314.1 | 322.2 | 310.2 | 308.5 | 335.5 | 322.7 | 305.2
896 | 751 | 470.2 | 188.08 | 219.8547 | 314.3 | 287.7 | 290.8 | 306.5 | 453.4 | 50.2 | 19.8 | 95.5 | 6.9 | 257.6 | 12.7 | 749.7 | 638.5 | 548.4 | 714.8 | 569.4 | 736.7 | 634.3 | 573.7 | 741.9 | 547.5 | 259.1 | 314.3 | 322.3 | 310.3 | 308.5 | 335.9 | 322.7 | 305.3
897 | 752 | 470.2 | 188.08 | 219.8547 | 314 | 287.4 | 291.6 | 306.2 | 458.2 | 50.2 | 19.8 | 95.6 | 7.9 | 259.9 | 12.4 | 751.8 | 647.9 | 559.5 | 715.8 | 570.7 | 736.5 | 633.1 | 577.1 | 742.3 | 547.4 | 259.3 | 314.6 | 322.4 | 310.3 | 308.7 | 336.3 | 323 | 305.3
898 | 753 | 469.8 | 187.92 | 219.6677 | 314.8 | 287.2 | 292.1 | 307.1 | 459.4 | 50 | 19.8 | 95.7 | 8.6 | 266.8 | 11.9 | 751.7 | 650.4 | 556.7 | 716 | 570.4 | 735.9 | 635.3 | 577.9 | 742.3 | 547.3 | 259.5 | 314.7 | 322.3 | 310.1 | 308.9 | 336.4 | 323.3 | 305.4
899 | 754 | 470.9 | 188.36 | 220.182 | 316.1 | 287 | 292.2 | 307.6 | 457.5 | 49.9 | 19.8 | 95.8 | 8.5 | 252.2 | 11.4 | 752.5 | 660.8 | 568.4 | 717.7 | 571.3 | 736 | 637.3 | 587.4 | 743.3 | 548.1 | 259.8 | 314.8 | 322.4 | 310.1 | 309 | 336.9 | 323.6 | 305.5
900 | 755 | 469.4 | 187.76 | 219.4806 | 316.9 | 286.8 | 292.5 | 307.4 | 461 | 50 | 19.8 | 95.7 | 7.5 | 249.5 | 14.7 | 754.7 | 685.6 | 593.9 | 721.5 | 574.6 | 736.8 | 634.7 | 603.3 | 744.6 | 551 | 260 | 315.2 | 322.6 | 310.1 | 309.1 | 337.6 | 324 | 305.7
901 | 756 | 469.9 | 187.96 | 219.7144 | 316.4 | 286.1 | 292.7 | 308.1 | 463.8 | 50 | 19.8 | 95.7 | 8 | 254.3 | 15.5 | 762.3 | 720.3 | 631.6 | 728 | 581.4 | 737 | 628.1 | 623.6 | 745.6 | 554.8 | 260.2 | 315.7 | 323.3 | 310.3 | 309.2 | 337.6 | 324.3 | 305.8
902 | 757 | 470.5 | 188.2 | 219.995 | 314.2 | 285.7 | 293 | 309 | 460 | 50.1 | 19.8 | 95.5 | 6.4 | 250.1 | 13.9 | 766.2 | 726.6 | 645.9 | 730.8 | 584.7 | 736.2 | 619.8 | 634.5 | 746.6 | 557.5 | 260.4 | 316.1 | 323.9 | 310.4 | 309.3 | 338.5 | 324.4 | 305.9
903 | 758 | 469.5 | 187.8 | 219.5274 | 312.9 | 285.6 | 293.9 | 309.4 | 455.1 | 50.1 | 19.8 | 95.3 | 5.3 | 248.3 | 17.2 | 768.1 | 732.7 | 674.3 | 732.7 | 590.3 | 735.6 | 612.3 | 640.1 | 747.3 | 558.3 | 260.6 | 316.4 | 324.5 | 310.5 | 309.5 | 339.3 | 324.4 | 306.1
904 | 759 | 469.8 | 187.92 | 219.6677 | 311.1 | 285.8 | 295.2 | 309.2 | 452.2 | 50.1 | 19.8 | 95.1 | 5.1 | 251.7 | 16.3 | 771.7 | 738.9 | 682 | 735.8 | 594.4 | 735.6 | 607 | 655.1 | 747.8 | 561.2 | 260.9 | 316.9 | 324.9 | 310.8 | 309.7 | 338.9 | 324.3 | 306.2
905 | 760 | 470 | 188 | 219.7612 | 310.3 | 285.5 | 296.1 | 308.4 | 451.7 | 50.2 | 19.8 | 94.9 | 5.7 | 263.2 | 17.3 | 773.6 | 737.1 | 677.4 | 737.3 | 594.7 | 735.1 | 599.2 | 655.1 | 747.8 | 561.1 | 261.1 | 317.1 | 325.1 | 310.8 | 309.8 | 338.5 | 324.1 | 306.2
906 | 761 | 470.1 | 188.04 | 219.8079 | 309.2 | 285 | 296.3 | 307.9 | 450.3 | 50.4 | 19.8 | 94.7 | 7.2 | 269.7 | 17.7 | 775.2 | 730.8 | 675.4 | 737.3 | 595 | 735 | 593.8 | 655 | 747.8 | 561.8 | 261.3 | 317.2 | 325.2 | 310.8 | 310 | 338.4 | 324.1 | 306.2
907 | 762 | 469.3 | 187.72 | 219.4339 | 310.6 | 284.5 | 296.8 | 307.6 | 448.6 | 50.6 | 19.8 | 94.6 | 7.6 | 266.9 | 19 | 776.7 | 746.4 | 690.3 | 739.6 | 598.3 | 735 | 589.8 | 660.9 | 748.2 | 563.7 | 261.5 | 317.8 | 325.4 | 310.8 | 310.1 | 338.3 | 324.5 | 306.3
908 | 763 | 469.8 | 187.92 | 219.6677 | 310 | 284.7 | 296.9 | 307.5 | 453.7 | 50.8 | 19.8 | 94.5 | 8 | 267.2 | 17.9 | 779.8 | 749.3 | 714.2 | 741.1 | 601.2 | 735.1 | 589.4 | 666.1 | 749 | 565.4 | 261.7 | 318.1 | 325.5 | 310.9 | 310.2 | 338.3 | 324.5 | 306.3
909 | 764 | 469.7 | 187.88 | 219.6209 | 308.8 | 284.8 | 297.1 | 307.9 | 457.5 | 51 | 19.8 | 94.4 | 8.5 | 258 | 15.5 | 784.3 | 751.4 | 731.7 | 743.1 | 605.5 | 735.2 | 586.7 | 668.1 | 749.6 | 566.4 | 261.9 | 318.3 | 325.8 | 311 | 310.2 | 337.6 | 323.8 | 306.3
910 | 765 | 469 | 187.6 | 219.2936 | 310 | 285.2 | 297.7 | 307.7 | 452.2 | 51.2 | 19.8 | 94.2 | 9.1 | 275 | 14.8 | 785.6 | 739.2 | 719.9 | 741.7 | 606.6 | 734.7 | 581.6 | 660.5 | 750.5 | 566.4 | 262.2 | 318.2 | 326 | 311 | 310.3 | 337.1 | 323.3 | 306.3
911 | 766 | 468.7 | 187.48 | 219.1533 | 311.1 | 285.4 | 297.7 | 307 | 447.1 | 51.3 | 19.8 | 94 | 8.4 | 251.4 | 17 | 784.4 | 724.9 | 697 | 739.2 | 604.8 | 734.5 | 577 | 656.2 | 750.4 | 566.5 | 262.4 | 318 | 325.8 | 311.1 | 310.4 | 336.4 | 322.9 | 306.3
912 | 767 | 469.4 | 187.76 | 219.4806 | 310.8 | 285.2 | 297.8 | 306.1 | 453.7 | 51.3 | 19.8 | 93.9 | 7.2 | 253.2 | 16 | 781.1 | 706.8 | 694.9 | 735.5 | 604.1 | 734.3 | 576.4 | 650 | 750.1 | 565.9 | 262.6 | 318.3 | 325.5 | 311.6 | 310.4 | 335.9 | 322.6 | 306.3
913 | 768 | 469.5 | 187.8 | 219.5274 | 307.9 | 285.4 | 298.4 | 305.7 | 467.5 | 51.3 | 19.8 | 93.8 | 7.1 | 253.7 | 15.9 | 779.2 | 692.3 | 692.1 | 732.7 | 604.2 | 734.5 | 583.5 | 644.1 | 750.1 | 565.6 | 262.8 | 319.2 | 326.2 | 312.1 | 310.4 | 335.7 | 322.4 | 306.3
914 | 769 | 469.1 | 187.64 | 219.3403 | 307 | 285.8 | 299.7 | 305.9 | 480 | 51.3 | 19.8 | 93.7 | 9.1 | 251.8 | 15.1 | 777.7 | 683.2 | 693.6 | 730 | 603.5 | 734.7 | 586.7 | 645.5 | 750.8 | 565.1 | 263 | 319.5 | 326.6 | 312.4 | 310.5 | 335.5 | 322.3 | 306.3
915 | 770 | 469 | 187.6 | 219.2936 | 308.8 | 287.4 | 300.4 | 307.2 | 481.3 | 51.3 | 19.8 | 93.7 | 8.4 | 251.8 | 13.7 | 775.9 | 680 | 680.1 | 727.6 | 602.2 | 734.7 | 586.1 | 640.2 | 750.8 | 564.9 | 263.2 | 322.2 | 327.3 | 313 | 310.5 | 336.4 | 322.3 | 306.3
916 | 771 | 469.6 | 187.84 | 219.5741 | 310.7 | 288.8 | 301.2 | 308.6 | 479.6 | 51.2 | 19.8 | 93.7 | 10.3 | 263.7 | 14.2 | 776.2 | 686 | 678 | 727.2 | 601.9 | 734.8 | 590.4 | 641.9 | 750.9 | 565 | 263.4 | 322.6 | 327.7 | 313.4 | 310.6 | 337.7 | 322.4 | 306.4
917 | 772 | 469.9 | 187.96 | 219.7144 | 312.5 | 289.4 | 301.3 | 310 | 483.4 | 51.2 | 19.8 | 93.8 | 11.9 | 258.1 | 17.9 | 774.9 | 678.2 | 675 | 725.6 | 601 | 734.7 | 585.4 | 636 | 750.6 | 564.2 | 263.6 | 323.9 | 328.7 | 313.8 | 310.8 | 339.8 | 322.5 | 306.5
918 | 773 | 470.1 | 188.04 | 219.8079 | 314.5 | 289.3 | 301.5 | 311.6 | 485.6 | 51.3 | 19.8 | 94 | 12.1 | 249.3 | 18.6 | 774.8 | 681.3 | 659.7 | 726.5 | 602.4 | 735.1 | 587.8 | 636.2 | 750.8 | 564.1 | 263.8 | 323.6 | 329 | 313.4 | 311.1 | 340.1 | 323.1 | 306.7
919 | 774 | 469.5 | 187.8 | 219.5274 | 315.4 | 289.4 | 301.3 | 312.6 | 483.4 | 51.4 | 19.8 | 94.2 | 12.3 | 242.1 | 17.7 | 772.6 | 670.8 | 636.3 | 725.1 | 600 | 735 | 597 | 628.5 | 750.9 | 563.5 | 264 | 323.7 | 329 | 313.1 | 311.3 | 341.8 | 323.7 | 306.9
920 | 775 | 470 | 188 | 219.7612 | 315 | 289.6 | 301.5 | 313.4 | 481.4 | 51.5 | 19.8 | 94.3 | 8.6 | 245.9 | 15 | 770 | 663.2 | 623.5 | 723.1 | 597.9 | 734.6 | 611.6 | 623.7 | 750.9 | 562.4 | 264.2 | 323.6 | 329.3 | 313.2 | 311.5 | 342 | 323.9 | 307.1
921 | 776 | 470.1 | 188.04 | 219.8079 | 313.9 | 290.4 | 302.3 | 314.1 | 481 | 51.6 | 19.8 | 94.3 | 9.9 | 251.5 | 14.4 | 769.1 | 663.4 | 617.2 | 722.1 | 595.9 | 734.7 | 609.1 | 623.7 | 750.6 | 561.9 | 264.4 | 323.6 | 329.5 | 313.3 | 311.6 | 341.6 | 323.9 | 307.2
922 | 777 | 469.7 | 187.88 | 219.6209 | 312.7 | 290.9 | 302.7 | 313.7 | 479 | 51.5 | 19.8 | 94.5 | 12.5 | 242 | 14.9 | 767.2 | 658 | 615.1 | 720.7 | 594.5 | 734.6 | 610.2 | 622.1 | 750.8 | 561 | 264.6 | 323.8 | 329.7 | 313.3 | 311.7 | 341.2 | 323.8 | 307.2
923 | 778 | 470.8 | 188.32 | 220.1352 | 311.4 | 290.8 | 302.7 | 312.9 | 474.6 | 51.5 | 19.8 | 94.7 | 11.6 | 252.9 | 15.3 | 767.9 | 672.8 | 622.4 | 722.3 | 596.1 | 735.1 | 610.8 | 630.3 | 751.5 | 562.3 | 264.8 | 323.9 | 329.9 | 313.3 | 311.8 | 340.9 | 323.9 | 307.3
924 | 779 | 470.4 | 188.16 | 219.9482 | 310.3 | 290.9 | 302.6 | 311.8 | 472.8 | 51.5 | 19.8 | 94.8 | 12.3 | 251.5 | 15.9 | 766.9 | 677.1 | 627.4 | 722.6 | 596.6 | 735.4 | 605.6 | 630.2 | 751.9 | 561.9 | 265 | 323.7 | 330.4 | 313.1 | 311.9 | 340.2 | 324.1 | 307.4
925 | 780 | 470.1 | 188.04 | 219.8079 | 309.8 | 290.6 | 302.5 | 311 | 470.9 | 51.6 | 19.8 | 94.8 | 11.1 | 257.8 | 16.4 | 766.8 | 689.2 | 616.6 | 723.6 | 596.6 | 735.7 | 610.3 | 631.9 | 752.5 | 562.2 | 265.2 | 323.4 | 330.2 | 313 | 312 | 340.6 | 324 | 307.5
926 | 781 | 470.9 | 188.36 | 220.182 | 309.8 | 290.9 | 301.6 | 310.4 | 471.1 | 51.7 | 19.8 | 94.8 | 8.8 | 259.5 | 14.6 | 766.6 | 687.4 | 596.8 | 723.3 | 595.9 | 735.9 | 607.6 | 631.3 | 752.4 | 562 | 265.4 | 323.5 | 330 | 312.9 | 312.1 | 340.2 | 323.9 | 307.6
927 | 782 | 469.8 | 187.92 | 219.6677 | 311.3 | 291.1 | 301.4 | 309.4 | 465.8 | 51.7 | 19.8 | 94.6 | 8 | 264.3 | 13.1 | 764.4 | 663.7 | 574.8 | 720.4 | 593 | 735.3 | 603.1 | 622.2 | 752.4 | 560.6 | 265.6 | 323 | 329.8 | 312.9 | 312.1 | 339.7 | 324 | 307.6
928 | 783 | 471.2 | 188.48 | 220.3223 | 311.8 | 291 | 301.5 | 309.3 | 460.3 | 51.5 | 19.8 | 94.4 | 6.6 | 242.9 | 12.6 | 762.8 | 660 | 563.8 | 719.2 | 591.7 | 735 | 616.7 | 619.7 | 752.7 | 559.7 | 265.8 | 322.3 | 329 | 312.9 | 312.3 | 340 | 324.2 | 307.7
929 | 784 | 469.6 | 187.84 | 219.5741 | 312.1 | 290.9 | 301.1 | 310.1 | 462.2 | 51.3 | 19.8 | 94.2 | 5.7 | 269.8 | 12.5 | 761.3 | 646.6 | 550.1 | 716.9 | 589.2 | 734.7 | 618.1 | 615.2 | 752.5 | 558.7 | 266 | 321.4 | 328.4 | 312.8 | 312.5 | 340.3 | 324.5 | 307.8
930 | 785 | 469.6 | 187.84 | 219.5741 | 310.7 | 290.7 | 299.8 | 311.2 | 465 | 51.3 | 19.8 | 94.1 | 7.5 | 254.8 | 15.5 | 759.7 | 629.7 | 535.9 | 714 | 586.6 | 734.2 | 633.1 | 609.5 | 752.3 | 557.5 | 266.2 | 320.5 | 327.8 | 312.6 | 312.7 | 340.3 | 324.6 | 307.9
931 | 786 | 469.6 | 187.84 | 219.5741 | 308.3 | 290.7 | 298.8 | 311.7 | 464 | 51.4 | 19.8 | 94.2 | 8.5 | 239.9 | 15.2 | 756.4 | 617.8 | 522.5 | 711.3 | 583.9 | 734.1 | 641.6 | 603.3 | 752 | 556.2 | 266.4 | 319.6 | 327.1 | 312.5 | 312.8 | 339.8 | 324.5 | 307.9
932 | 787 | 471.3 | 188.52 | 220.369 | 307.6 | 290.7 | 298.2 | 311.6 | 462.3 | 51.4 | 19.8 | 94.2 | 7.7 | 252.1 | 12.7 | 752 | 607.7 | 512.6 | 708.3 | 582.2 | 733.8 | 650.6 | 598 | 751.3 | 555 | 266.6 | 319.1 | 326.7 | 312.4 | 312.8 | 341.4 | 324.2 | 307.9
933 | 788 | 470.4 | 188.16 | 219.9482 | 307.9 | 290.6 | 298 | 310.9 | 459.4 | 51.4 | 19.8 | 94.2 | 7.7 | 268.9 | 15.1 | 748.8 | 600.3 | 503 | 705.8 | 579.9 | 733.6 | 657.4 | 595.1 | 751 | 553.9 | 266.8 | 318.7 | 326.3 | 312.3 | 312.9 | 340.5 | 323.9 | 308
934 | 789 | 471.5 | 188.6 | 220.4625 | 308.2 | 289.9 | 298.4 | 309.6 | 456.7 | 51.4 | 19.8 | 94.2 | 7 | 263.3 | 15.2 | 746.3 | 590.7 | 495.1 | 703.4 | 577.7 | 733.4 | 661.8 | 591.4 | 751 | 552.6 | 267 | 318.1 | 325.7 | 312.3 | 312.9 | 339.7 | 323.4 | 307.9
935 | 790 | 470.8 | 188.32 | 220.1352 | 308.6 | 288.7 | 298.3 | 308.2 | 453.3 | 51.5 | 19.8 | 94.2 | 7.9 | 270 | 18.8 | 744.9 | 592.5 | 494.4 | 702.3 | 577.2 | 733.3 | 659.9 | 592.7 | 752 | 552.2 | 267.2 | 317.5 | 325.1 | 312.1 | 312.9 | 338.7 | 323 | 307.9
936 | 791 | 469.5 | 187.8 | 219.5274 | 309.8 | 288.5 | 297.6 | 307 | 450.3 | 51.5 | 19.8 | 94.2 | 8 | 269.2 | 22.1 | 742.8 | 593 | 488.5 | 701.1 | 576.2 | 733.4 | 657.8 | 593.3 | 752.9 | 551.4 | 267.4 | 317 | 324.7 | 312 | 312.9 | 337.8 | 322.6 | 307.8
937 | 792 | 470.2 | 188.08 | 219.8547 | 308.9 | 288.4 | 296.5 | 306.8 | 447.1 | 51.5 | 19.8 | 94.3 | 8.6 | 254.2 | 17.9 | 742.5 | 600.7 | 490 | 701.3 | 575.1 | 734.2 | 650.7 | 595.6 | 752.9 | 551.3 | 267.6 | 316.6 | 324.4 | 311.9 | 312.9 | 336.9 | 322.5 | 307.8
938 | 793 | 470.2 | 188.08 | 219.8547 | 308.1 | 288.6 | 295.5 | 306.9 | 446 | 51.5 | 19.8 | 94.3 | 9.5 | 237.2 | 14.7 | 740.2 | 593.5 | 486.4 | 699.4 | 573.1 | 733.7 | 645.9 | 591.9 | 752.8 | 550 | 267.8 | 316.3 | 324.3 | 312.1 | 312.9 | 336.2 | 322.2 | 307.8
939 | 794 | 470.1 | 188.04 | 219.8079 | 308.2 | 288.7 | 295.3 | 306.9 | 447.1 | 51.6 | 19.8 | 94.3 | 8.6 | 237.8 | 13.4 | 737.5 | 586.7 | 488 | 696.8 | 572.1 | 733.3 | 645.6 | 589.1 | 752.8 | 549 | 268 | 316.3 | 324.3 | 312.3 | 312.9 | 336.1 | 321.9 | 307.8
940 | 795 | 469.1 | 187.64 | 219.3403 | 308.6 | 288.9 | 295.1 | 306.4 | 447.9 | 51.6 | 19.8 | 94.2 | 8.8 | 240.7 | 11.6 | 736.2 | 587.7 | 500.1 | 695.7 | 571.3 | 733.1 | 647 | 589.6 | 753.1 | 548.2 | 268.1 | 316.1 | 324.4 | 312.3 | 312.9 | 336.6 | 321.6 | 307.7
941 | 796 | 469.2 | 187.68 | 219.3871 | 308.7 | 288.1 | 296.2 | 306.2 | 448.2 | 51.6 | 19.8 | 94.1 | 9.3 | 254.5 | 11.2 | 737.4 | 602.6 | 525.1 | 696.8 | 572.1 | 733.4 | 644.3 | 593.8 | 753.6 | 548.5 | 268.3 | 316.5 | 324.5 | 312.7 | 312.8 | 336.2 | 321.2 | 307.7
942 | 797 | 470.1 | 188.04 | 219.8079 | 308.9 | 287.5 | 297.5 | 306.9 | 454.8 | 51.7 | 19.7 | 94.1 | 9.8 | 248.1 | 14.8 | 734.9 | 592.9 | 520.2 | 695.1 | 569.9 | 733.4 | 646.7 | 593.4 | 753.9 | 547.6 | 268.5 | 317.2 | 325.2 | 313.3 | 312.8 | 336 | 321.1 | 307.7
943 | 798 | 467.4 | 186.96 | 218.5455 | 310.1 | 287.7 | 299.1 | 307.6 | 459.2 | 51.8 | 19.7 | 94.2 | 8.9 | 241.7 | 16.3 | 730.7 | 582.4 | 506.3 | 693.1 | 567.3 | 733.2 | 643.7 | 590.8 | 753.8 | 546.6 | 268.7 | 318 | 326.1 | 313.7 | 313 | 336 | 321.1 | 307.8
944 | 799 | 468 | 187.2 | 218.826 | 314.6 | 288.2 | 300.8 | 308.2 | 460.9 | 51.8 | 19.8 | 94.3 | 10 | 241.1 | 16 | 727.7 | 574.1 | 492.6 | 691 | 565.4 | 732.5 | 642.2 | 588 | 753.4 | 545.4 | 268.9 | 319 | 327.1 | 314 | 313.1 | 337 | 321.2 | 307.9
945 | 800 | 469.2 | 187.68 | 219.3871 | 316.2 | 289 | 302.1 | 309.5 | 463.8 | 51.8 | 19.8 | 94.3 | 14.1 | 233.8 | 15.5 | 724.5 | 564.7 | 483 | 688.9 | 563 | 731.9 | 646.3 | 584.9 | 752.7 | 544.3 | 269.1 | 320.2 | 328.5 | 314.4 | 313.2 | 339.1 | 321.8 | 308
946 | 801 | 469.4 | 187.76 | 219.4806 | 315.9 | 289.8 | 304.1 | 312 | 464.7 | 51.9 | 19.7 | 94.5 | 16.4 | 244.4 | 14.4 | 722.5 | 559.6 | 478.8 | 687 | 561.1 | 731.5 | 647.7 | 585 | 752.5 | 543.4 | 269.3 | 321.3 | 330 | 314.5 | 313.5 | 339.8 | 322 | 308.2
947 | 802 | 468.3 | 187.32 | 218.9663 | 316.1 | 290.6 | 306.3 | 313.9 | 463 | 51.9 | 19.7 | 94.8 | 16.1 | 266.6 | 13.6 | 720.8 | 550 | 466.5 | 685.6 | 558.7 | 731.1 | 653 | 582.9 | 751.8 | 542.7 | 269.5 | 322 | 330.9 | 314.7 | 313.7 | 340.2 | 322.3 | 308.4
948 | 803 | 469 | 187.6 | 219.2936 | 318 | 291 | 307.4 | 314.7 | 462.1 | 51.9 | 19.7 | 94.9 | 13.7 | 237.9 | 22.2 | 719.3 | 538.8 | 456.5 | 683.9 | 557.1 | 730.1 | 653 | 579.3 | 751.8 | 541.9 | 269.7 | 322.8 | 331.4 | 314.6 | 313.8 | 340.3 | 322.6 | 308.5
949 | 804 | 469.1 | 187.64 | 219.3403 | 320.1 | 291.4 | 308 | 315.2 | 458.9 | 51.9 | 19.7 | 95.1 | 13.9 | 247.4 | 26.2 | 717.4 | 533.2 | 450.7 | 682.2 | 555.3 | 729.2 | 654.9 | 577.5 | 751.5 | 541 | 269.9 | 323.2 | 331.6 | 314.6 | 313.9 | 341.2 | 322.9 | 308.6
950 | 805 | 469 | 187.6 | 219.2936 | 320.6 | 292.1 | 308.5 | 315.6 | 457.4 | 51.9 | 19.7 | 95.3 | 12 | 246.4 | 23.7 | 715.4 | 529.4 | 443.9 | 680.6 | 553.6 | 728.5 | 662 | 577.1 | 750.4 | 540.1 | 270 | 323.5 | 331.7 | 314.8 | 314.1 | 341.2 | 322.9 | 308.7
951 | 806 | 467.7 | 187.08 | 218.6857 | 322.1 | 292.3 | 308.9 | 315 | 456.4 | 51.9 | 19.7 | 95.4 | 11 | 247.6 | 19 | 713.6 | 522.6 | 438.6 | 678.9 | 551.9 | 727.8 | 664.6 | 574.2 | 749.7 | 539.2 | 270.2 | 323.9 | 331.9 | 315 | 314.2 | 341.6 | 323 | 308.8
952 | 807 | 469.2 | 187.68 | 219.3871 | 319.1 | 292.8 | 309.5 | 313.9 | 457.5 | 51.9 | 19.7 | 95.6 | 12.7 | 264.2 | 15.6 | 711.2 | 518.8 | 440.2 | 677.2 | 550.6 | 727 | 670.1 | 572.9 | 748.6 | 538.1 | 270.4 | 324 | 332.7 | 314.8 | 314.3 | 341.9 | 323.1 | 308.9
953 | 808 | 467.3 | 186.92 | 218.4987 | 319.5 | 293.2 | 310.3 | 313.2 | 457.9 | 51.9 | 19.7 | 95.8 | 13.5 | 256.7 | 20.2 | 710.8 | 525.2 | 456.4 | 676.5 | 550.9 | 727.1 | 669.1 | 577.3 | 748 | 537.8 | 270.6 | 324.1 | 332.8 | 314.8 | 314.3 | 342.5 | 323 | 309
954 | 809 | 468.4 | 187.36 | 219.013 | 318.6 | 293 | 310.2 | 313.5 | 457.5 | 51.9 | 19.7 | 96 | 11.4 | 263.1 | 18.5 | 711.9 | 538.8 | 480.6 | 676.3 | 552.6 | 727.1 | 659.4 | 580.9 | 748.2 | 537.6 | 270.8 | 323.9 | 332.5 | 314.7 | 314.3 | 341.5 | 322.4 | 309
955 | 810 | 466.3 | 186.52 | 218.0311 | 317.8 | 292.6 | 309.4 | 313.6 | 454.1 | 51.9 | 19.7 | 96.1 | 10.6 | 265.5 | 15.6 | 713.2 | 551.1 | 492.1 | 676.8 | 552.4 | 726.9 | 655 | 582.2 | 748.4 | 537.4 | 270.9 | 323.9 | 332.1 | 314.7 | 314.2 | 340.3 | 321.9 | 308.9
956 | 811 | 465.6 | 186.24 | 217.7038 | 318.1 | 292.3 | 308.5 | 312.6 | 455.7 | 51.8 | 19.7 | 96.2 | 9.8 | 244.5 | 16.2 | 715.7 | 568.5 | 504.1 | 679 | 553.1 | 726.8 | 649.5 | 584.6 | 748 | 537.5 | 271.1 | 323.9 | 331.8 | 314.8 | 314.2 | 339.3 | 321.5 | 308.9
957 | 812 | 466.7 | 186.68 | 218.2182 | 318.5 | 292.2 | 308.3 | 312.4 | 458 | 51.7 | 19.7 | 96.1 | 8.7 | 225.7 | 15.9 | 714.7 | 563.4 | 501.1 | 678.2 | 551.3 | 726.5 | 635.5 | 585.3 | 747.8 | 537.2 | 271.3 | 323.8 | 331.5 | 314.9 | 314.2 | 338.5 | 321.1 | 308.9
958 | 813 | 466.4 | 186.56 | 218.0779 | 319.5 | 291.9 | 308.2 | 313 | 459.2 | 51.5 | 19.7 | 96 | 7.7 | 201.7 | 13.6 | 712 | 560.6 | 510.1 | 676.6 | 550.4 | 725.9 | 634.3 | 584.4 | 747.6 | 536.8 | 271.5 | 323.9 | 331.4 | 315.2 | 314.2 | 337.8 | 320.8 | 308.8
959 | 814 | 466.7 | 186.68 | 218.2182 | 321.7 | 291.9 | 309 | 313.4 | 461.6 | 51.4 | 19.7 | 95.7 | 8.4 | 254.5 | 13.1 | 711.9 | 566.2 | 519 | 676.9 | 550.5 | 725.2 | 630.3 | 588.8 | 747.3 | 537.2 | 271.7 | 324.6 | 331.9 | 315.5 | 314.2 | 338.2 | 320.6 | 308.8
960 | 815 | 466.8 | 186.72 | 218.2649 | 329.3 | 291.9 | 310 | 314.4 | 462.3 | 51.4 | 19.7 | 95.6 | 9.9 | 231 | 10.9 | 712.6 | 573.3 | 519 | 677.6 | 550.5 | 724.5 | 619.7 | 590.7 | 746.9 | 537 | 272 | 325.1 | 332.3 | 315.8 | 314.3 | 338.9 | 320.6 | 308.8
961 | 816 | 467.5 | 187 | 218.5922 | 334 | 291.9 | 310.5 | 315.6 | 465.2 | 51.3 | 19.7 | 95.6 | 11.7 | 244.3 | 10.7 | 714 | 593.5 | 540.5 | 679.5 | 551.8 | 724.1 | 609.6 | 597.8 | 746.3 | 537.3 | 272.2 | 325 | 332.1 | 315.9 | 314.4 | 339.4 | 320.7 | 308.9
962 | 817 | 468.8 | 187.52 | 219.2001 | 332.2 | 292 | 310.5 | 317 | 471.7 | 51.2 | 19.7 | 95.6 | 12.5 | 254 | 14.4 | 715.5 | 599.3 | 544 | 680 | 552.2 | 723.7 | 602.7 | 603 | 746 | 538.3 | 272.3 | 325.2 | 332.2 | 316.2 | 314.6 | 340 | 320.7 | 309
963 | 818 | 469.2 | 187.68 | 219.3871 | 331.1 | 292.2 | 310.4 | 318.3 | 473.9 | 51.2 | 19.7 | 95.5 | 10.8 | 282.6 | 15.1 | 713.3 | 592.2 | 530.2 | 678 | 550.9 | 723 | 594.3 | 601.3 | 745.9 | 537.2 | 272.5 | 325.6 | 332.7 | 316.5 | 314.7 | 340.2 | 320.9 | 309.1
964 | 819 | 469.9 | 187.96 | 219.7144 | 332.3 | 292.5 | 311.6 | 320.3 | 474.4 | 51.2 | 19.7 | 95.4 | 12.3 | 242.9 | 12.8 | 712.1 | 589.1 | 547.5 | 676.7 | 551.7 | 722.3 | 597.9 | 605.4 | 745.6 | 537.1 | 272.7 | 326.5 | 333.6 | 316.8 | 314.8 | 340.4 | 321 | 309.2
965 | 820 | 468.6 | 187.44 | 219.1066 | 335.5 | 292.9 | 313 | 321.7 | 471.5 | 51.2 | 19.7 | 95.2 | 10.7 | 246.4 | 19.8 | 709.7 | 580.7 | 531.8 | 675.4 | 549.9 | 721.3 | 591.4 | 602.6 | 745 | 536.7 | 272.9 | 327.5 | 334.2 | 317.2 | 315 | 341.4 | 321.3 | 309.3
966 | 821 | 467.6 | 187.04 | 218.639 | 336.8 | 293.2 | 314.1 | 323.2 | 472 | 51.2 | 19.7 | 95.2 | 10.7 | 236.8 | 25.2 | 706.7 | 571.1 | 522.3 | 673.7 | 548.2 | 720.3 | 589.4 | 598.7 | 744.3 | 536 | 273.1 | 328.9 | 335.3 | 317.7 | 315.2 | 342.4 | 321.6 | 309.4
967 | 822 | 467.8 | 187.12 | 218.7325 | 336.1 | 293.6 | 315.3 | 324.6 | 476.2 | 51.3 | 19.7 | 95.2 | 12.6 | 245.2 | 22.4 | 707.7 | 580.3 | 530.5 | 674.9 | 548.2 | 719.6 | 594.9 | 600.8 | 743.8 | 535.9 | 273.3 | 329.8 | 336.4 | 318 | 315.6 | 343.8 | 322.1 | 309.6
968 | 823 | 468.4 | 187.36 | 219.013 | 334.5 | 294.7 | 316.3 | 325.9 | 480.4 | 51.5 | 19.7 | 95.3 | 11.9 | 249.1 | 23.2 | 708.3 | 586.1 | 532.6 | 675.2 | 547.7 | 719.2 | 592.6 | 604.8 | 743.7 | 536.3 | 273.4 | 330.2 | 337.4 | 318 | 315.9 | 344.7 | 322.8 | 309.8
969 | 824 | 467.6 | 187.04 | 218.639 | 333.8 | 295.5 | 317.2 | 326.9 | 480.7 | 51.5 | 19.7 | 95.2 | 10.7 | 260.6 | 20.8 | 707.4 | 577.2 | 528 | 673.6 | 545.9 | 718.4 | 584.5 | 600.6 | 743.5 | 535.8 | 273.6 | 330.7 | 338.1 | 318.2 | 316.2 | 346.3 | 323.3 | 310
970 | 825 | 468.4 | 187.36 | 219.013 | 334.7 | 296.4 | 317.9 | 328.5 | 480.6 | 51.3 | 19.7 | 95.2 | 12.6 | 259 | 23.7 | 706.8 | 574.5 | 535.9 | 673.1 | 544.8 | 717.4 | 579.9 | 600.6 | 743.9 | 535.4 | 273.8 | 331.3 | 338.9 | 318.5 | 316.5 | 347.9 | 324 | 310.1
971 | 826 | 469.1 | 187.64 | 219.3403 | 336.9 | 296.7 | 317.8 | 329.2 | 477.9 | 51.2 | 19.7 | 95.1 | 11.3 | 255.2 | 21 | 706.2 | 575.6 | 544.2 | 673.4 | 544.2 | 716.8 | 580.4 | 605 | 744.2 | 536.2 | 274 | 331.7 | 339.4 | 318.6 | 316.6 | 348.1 | 324.4 | 310.3
972 | 827 | 471.4 | 188.56 | 220.4158 | 337.2 | 297 | 317.9 | 329.4 | 474.2 | 51.2 | 19.7 | 95 | 9.6 | 256.8 | 21.2 | 708.1 | 584.3 | 555.7 | 674.8 | 545.6 | 716 | 572.3 | 607.8 | 744.9 | 536.1 | 274.2 | 331.9 | 339.8 | 318.6 | 316.9 | 347.9 | 324.7 | 310.5
973 | 828 | 472 | 188.8 | 220.6963 | 338.4 | 296.9 | 318.7 | 328.4 | 472.3 | 51.2 | 19.7 | 94.9 | 10.1 | 260.4 | 19.4 | 711.2 | 589.2 | 568 | 676 | 547.2 | 715.4 | 567.8 | 611.2 | 745.3 | 536.5 | 274.3 | 332.4 | 340.4 | 318.9 | 317.1 | 347.5 | 325 | 310.7
974 | 829 | 471.7 | 188.68 | 220.556 | 341.3 | 296.2 | 319.6 | 326.6 | 473.2 | 51.2 | 19.7 | 94.8 | 10.8 | 264.6 | 18.9 | 710.6 | 584 | 553.7 | 675.3 | 545.3 | 714.7 | 563.4 | 604.9 | 746.2 | 535.9 | 274.5 | 332.8 | 340.8 | 319.1 | 317.3 | 347.3 | 325.2 | 310.8
975 | 830 | 471.3 | 188.52 | 220.369 | 341.1 | 296.1 | 320 | 325.6 | 469.6 | 51.2 | 19.7 | 94.7 | 11.3 | 265 | 17 | 708.4 | 589.9 | 548.6 | 674.8 | 545.5 | 713.7 | 565.8 | 602.7 | 747.6 | 535.3 | 274.7 | 333 | 340.8 | 319 | 317.4 | 348.1 | 325.5 | 310.9
976 | 831 | 471.1 | 188.44 | 220.2755 | 340.5 | 296.3 | 319.9 | 326.5 | 472.3 | 51.1 | 19.7 | 94.6 | 13.3 | 270.4 | 15.5 | 705.6 | 584.3 | 535.2 | 673.5 | 543.7 | 713.2 | 571.1 | 600.8 | 748.4 | 535.2 | 274.9 | 333.6 | 341 | 319.4 | 317.5 | 348 | 325.5 | 311
977 | 832 | 471.7 | 188.68 | 220.556 | 339.8 | 296.4 | 320 | 327.2 | 476.7 | 51 | 19.7 | 94.6 | 11.3 | 278 | 15.1 | 701.2 | 574.1 | 524.4 | 671 | 541.7 | 712.5 | 571.6 | 595.5 | 749.2 | 534.1 | 275.1 | 334.5 | 341.7 | 319.9 | 317.7 | 347.8 | 325.4 | 311.1
978 | 833 | 471.3 | 188.52 | 220.369 | 343.4 | 297.4 | 321.1 | 327.3 | 477.7 | 51 | 19.7 | 94.6 | 10.3 | 281.7 | 16.3 | 697.1 | 567.3 | 522.9 | 668.5 | 540.6 | 712 | 575.4 | 594.7 | 749.1 | 533.6 | 275.3 | 334.9 | 342.2 | 320.3 | 317.9 | 347.8 | 325.5 | 311.2
979 | 834 | 469.1 | 187.64 | 219.3403 | 345 | 298.4 | 321.5 | 327.1 | 476.1 | 50.9 | 19.7 | 94.6 | 9.7 | 257.7 | 14.5 | 694.7 | 564.4 | 521.8 | 666.9 | 539.4 | 711.6 | 581.1 | 594.9 | 748.8 | 533.2 | 275.5 | 335.7 | 342.5 | 320.5 | 318.2 | 348.7 | 325.9 | 311.4
980 | 835 | 469.5 | 187.8 | 219.5274 | 345.3 | 298.2 | 322.1 | 328.6 | 479.2 | 50.7 | 19.7 | 94.6 | 12 | 256.6 | 14.4 | 696.8 | 577.8 | 538.7 | 668.6 | 540.2 | 711.5 | 586.3 | 600.5 | 748.5 | 533.6 | 275.7 | 336.5 | 343.1 | 320.7 | 318.4 | 349.8 | 326.2 | 311.6
981 | 836 | 470.5 | 188.2 | 219.995 | 342.4 | 298.3 | 323.1 | 329.7 | 476.6 | 50.6 | 19.7 | 94.5 | 9.3 | 264.7 | 15.1 | 702.6 | 591 | 566.2 | 671.5 | 543.1 | 711.5 | 585 | 610.9 | 748.4 | 534.8 | 275.8 | 336.8 | 343.8 | 320.8 | 318.6 | 349.6 | 326.2 | 311.7
982 | 837 | 470 | 188 | 219.7612 | 340.6 | 299.2 | 324.5 | 329.8 | 470.9 | 50.5 | 19.7 | 94.4 | 8.4 | 253.2 | 15.4 | 707.9 | 607.8 | 581.3 | 674.6 | 545.2 | 711.3 | 580.8 | 618.3 | 748.9 | 535.2 | 276 | 336.9 | 344.4 | 320.8 | 318.7 | 349.5 | 326.3 | 311.8
983 | 838 | 469.9 | 187.96 | 219.7144 | 340.5 | 298.9 | 324.5 | 329.5 | 467.3 | 50.5 | 19.7 | 94.6 | 9.5 | 261.9 | 16.7 | 709.7 | 621.1 | 585.4 | 675.9 | 545.7 | 711 | 576.5 | 623.3 | 749.2 | 536 | 276.2 | 336.9 | 344.2 | 320.9 | 319 | 349.3 | 326.3 | 311.9
984 | 839 | 468.4 | 187.36 | 219.013 | 339.3 | 298.7 | 324 | 329.3 | 466.8 | 50.5 | 19.7 | 94.7 | 11 | 254.9 | 17.3 | 707 | 610 | 571.6 | 674.4 | 543.6 | 710 | 571.4 | 615 | 749.4 | 535.3 | 276.4 | 337.2 | 343.9 | 321.1 | 319.2 | 349.6 | 326.6 | 312
985 | 840 | 471.4 | 188.56 | 220.4158 | 340.6 | 298.9 | 323.2 | 329.4 | 465.2 | 50.4 | 19.7 | 94.9 | 11.9 | 267.1 | 15.4 | 707.5 | 611.4 | 571.9 | 674.5 | 543.8 | 709.1 | 572.2 | 611.7 | 750.2 | 534.7 | 276.7 | 337 | 343.7 | 321.1 | 319.5 | 350 | 326.9 | 312.2
986 | 841 | 469.6 | 187.84 | 219.5741 | 343.7 | 298.6 | 322.7 | 329.6 | 464.7 | 50.4 | 19.7 | 94.9 | 13.1 | 269.5 | 16.8 | 705.3 | 604.1 | 558.6 | 673 | 541.8 | 708.8 | 576.3 | 611.5 | 750.5 | 534.6 | 276.8 | 337.2 | 343.6 | 321.3 | 319.7 | 349.7 | 327.1 | 312.3
987 | 842 | 469.8 | 187.92 | 219.6677 | 344.4 | 298.1 | 322.4 | 329.8 | 466.7 | 50.4 | 19.7 | 94.8 | 9.9 | 256 | 16.3 | 703.9 | 604.5 | 563.3 | 672 | 541.7 | 708.4 | 580.8 | 614.4 | 750 | 534.6 | 277 | 337.5 | 344 | 321.7 | 319.8 | 349.6 | 327 | 312.4
988 | 843 | 469.9 | 187.96 | 219.7144 | 348.2 | 297.8 | 322.7 | 330.1 | 471.4 | 50.4 | 19.7 | 94.7 | 10.4 | 249.4 | 14.2 | 704.1 | 608 | 568.2 | 672.6 | 543.2 | 708 | 587.7 | 619.8 | 750.1 | 535.3 | 277.2 | 338.2 | 344.7 | 322 | 319.9 | 349.2 | 326.9 | 312.4
989 | 844 | 467.8 | 187.12 | 218.7325 | 353.1 | 298.5 | 323.1 | 330.6 | 481.7 | 50.4 | 19.7 | 94.7 | 11.3 | 264.6 | 12.5 | 703.8 | 604.4 | 567.6 | 672.6 | 542.9 | 707.8 | 587.6 | 621.6 | 750.8 | 535.7 | 277.4 | 338.7 | 345.6 | 322.1 | 320 | 349.7 | 326.9 | 312.5
990 | 845 | 469.4 | 187.76 | 219.4806 | 354.8 | 299.2 | 324.4 | 331.1 | 480.7 | 50.5 | 19.7 | 94.8 | 9.7 | 244.2 | 10.4 | 707.3 | 616.4 | 576.9 | 674.6 | 545.3 | 707.5 | 583.5 | 625.8 | 750.8 | 536.5 | 277.6 | 338.5 | 346.3 | 322.1 | 320.1 | 350.3 | 327 | 312.5
991 | 846 | 469.1 | 187.64 | 219.3403 | 354.8 | 299.7 | 325.3 | 332 | 480.6 | 50.5 | 19.7 | 94.8 | 11.6 | 255.1 | 12.1 | 708 | 613 | 566.8 | 674.3 | 544.1 | 707.1 | 579.1 | 622.7 | 750.6 | 536.4 | 277.8 | 338.4 | 346.6 | 322.2 | 320.4 | 351.1 | 327.2 | 312.7
992 | 847 | 467.6 | 187.04 | 218.639 | 353.2 | 299.9 | 325.3 | 333.3 | 478.1 | 50.4 | 19.7 | 94.9 | 13.9 | 259.2 | 15 | 709.7 | 613.5 | 555.5 | 675.4 | 544.9 | 706.7 | 575.1 | 620 | 750.8 | 536.4 | 277.9 | 338.3 | 346.5 | 322.3 | 320.7 | 351.8 | 327.5 | 313
993 | 848 | 468 | 187.2 | 218.826 | 350.4 | 299.5 | 324.2 | 333.9 | 475.2 | 50.2 | 19.7 | 95 | 11.8 | 254.2 | 12.9 | 707.3 | 613.1 | 541.4 | 673.8 | 543.2 | 706.1 | 570 | 617.2 | 750.7 | 535.9 | 278.1 | 338.3 | 346.6 | 322.1 | 321.1 | 351.7 | 328 | 313.2
994 | 849 | 468.5 | 187.4 | 219.0598 | 347.4 | 299.4 | 323.4 | 333.6 | 468.5 | 50.1 | 19.6 | 94.9 | 11.4 | 252.1 | 11.8 | 705.9 | 605.9 | 531.4 | 672.9 | 543.2 | 705.4 | 566.2 | 614 | 751 | 535.5 | 278.3 | 338.3 | 346.5 | 322.1 | 321.4 | 351.6 | 328.4 | 313.4
995 | 850 | 467.7 | 187.08 | 218.6857 | 344.8 | 299.5 | 323.1 | 333.5 | 461.7 | 50.1 | 19.6 | 95 | 11.5 | 246.2 | 13.1 | 703.8 | 597.6 | 517.2 | 670.7 | 541.6 | 704.3 | 561.7 | 608.8 | 750.7 | 534.8 | 278.5 | 338.4 | 346.3 | 322.3 | 321.6 | 351.3 | 328.5 | 313.5
996 | 851 | 469.3 | 187.72 | 219.4339 | 342.8 | 299.1 | 322.1 | 332.5 | 453.4 | 50.2 | 19.6 | 94.9 | 10.6 | 295.5 | 11.6 | 702.3 | 593.1 | 507.8 | 669.6 | 540.8 | 703.7 | 559.4 | 606.3 | 750.5 | 534.5 | 278.6 | 339.4 | 346.1 | 322.8 | 321.8 | 351 | 328.6 | 313.6
997 | 852 | 467.7 | 187.08 | 218.6857 | 341.6 | 298.7 | 321.1 | 330.5 | 453.4 | 50.3 | 19.6 | 94.8 | 10.3 | 270.5 | 9.5 | 699.6 | 584.6 | 505.4 | 668 | 540.3 | 702.9 | 556.1 | 601.4 | 750.7 | 533.7 | 278.8 | 338.3 | 345.7 | 322.6 | 322 | 350 | 328.7 | 313.8
998 | 853 | 468.5 | 187.4 | 219.0598 | 342.3 | 298.2 | 320.2 | 328.4 | 450.2 | 50.4 | 19.6 | 94.8 | 9.4 | 253.7 | 10.7 | 698.8 | 589.8 | 511.8 | 667.4 | 540.1 | 702.3 | 553 | 596.7 | 750.8 | 533.2 | 278.9 | 337.1 | 344.8 | 322 | 322 | 348.9 | 328.5 | 313.8
999 | 854 | 469 | 187.6 | 219.2936 | 340.9 | 297.7 | 318.7 | 326.8 | 446.4 | 50.4 | 19.6 | 94.9 | 8.7 | 282.8 | 12.3 | 697.4 | 587.9 | 520.8 | 666 | 540.1 | 701.9 | 551.2 | 594.2 | 751 | 532.4 | 279.1 | 336 | 344.2 | 321.6 | 322.1 | 347.6 | 328.2 | 313.9
1000 | 855 | 468.8 | 187.52 | 219.2001 | 336.8 | 297.1 | 317.4 | 325.7 | 446 | 50.4 | 19.6 | 94.9 | 9.1 | 280.8 | 12.9 | 697 | 595.6 | 519.5 | 666.7 | 539.9 | 702.1 | 551 | 599.9 | 751 | 533.1 | 279.3 | 335.3 | 343.7 | 321.4 | 322.1 | 346.4 | 327.9 | 313.8
1001 | 856 | 469.2 | 187.68 | 219.3871 | 334.2 | 296.8 | 316.8 | 324.5 | 444.1 | 50.3 | 19.6 | 94.8 | 8.4 | 275.6 | 13.1 | 698.1 | 596 | 521.9 | 666.9 | 540.2 | 701.7 | 547.8 | 600.4 | 750.5 | 532.8 | 279.4 | 334.6 | 343 | 321.4 | 322.1 | 345.3 | 327.5 | 313.8
1002 | 857 | 468.6 | 187.44 | 219.1066 | 334.6 | 296.6 | 316.1 | 323.1 | 441.3 | 50.4 | 19.6 | 94.6 | 8.3 | 276.6 | 13.8 | 699.9 | 599.9 | 517.5 | 667.3 | 540.4 | 701.1 | 545 | 597.3 | 750.1 | 532.5 | 279.6 | 333.6 | 342 | 321.4 | 322 | 344.1 | 327 | 313.8
1003 | 858 | 468.8 | 187.52 | 219.2001 | 333 | 296 | 315.1 | 321.7 | 437.9 | 50.4 | 19.6 | 94.6 | 10 | 272.8 | 13.7 | 700 | 604 | 514.9 | 667.2 | 540.4 | 700.6 | 543.2 | 597.6 | 749.7 | 532.3 | 279.7 | 332.5 | 340.8 | 321.2 | 322 | 343.2 | 326.6 | 313.7
1004 | 859 | 469.4 | 187.76 | 219.4806 | 331 | 295.4 | 313.9 | 320.3 | 435.9 | 50.5 | 19.6 | 94.6 | 10.3 | 283.1 | 13.8 | 697.9 | 594.5 | 516.5 | 665.5 | 540.4 | 700 | 540.7 | 595.8 | 749.3 | 532.1 | 279.9 | 331.8 | 340.1 | 321.2 | 322 | 342.6 | 326.3 | 313.7
1005 | 860 | 469.6 | 187.84 | 219.5741 | 330.3 | 294.8 | 312.9 | 319.8 | 438.1 | 50.4 | 19.6 | 94.6 | 9 | 286.4 | 13.9 | 697 | 584.8 | 515.8 | 664.4 | 539 | 699.2 | 537.9 | 590.9 | 749.2 | 531.6 | 280 | 331.3 | 339.4 | 321.4 | 322 | 341.8 | 325.8 | 313.6
1006 | 861 | 468.5 | 187.4 | 219.0598 | 330.2 | 294.1 | 312.4 | 319.3 | 437.8 | 50.5 | 19.6 | 94.6 | 9.8 | 289.1 | 13 | 697.9 | 584 | 522.5 | 664.3 | 539.2 | 698.6 | 537.3 | 589.4 | 748.7 | 531.4 | 280.2 | 330.8 | 338.6 | 321.4 | 322 | 341 | 325.3 | 313.6
1007 | 862 | 469.2 | 187.68 | 219.3871 | 330.2 | 294.1 | 311.7 | 318.6 | 444.5 | 50.3 | 19.6 | 94.6 | 10.3 | 283.3 | 12.8 | 698.2 | 584.3 | 530.7 | 663.9 | 539.6 | 698.2 | 535.7 | 589.8 | 748.1 | 531.1 | 280.3 | 330.6 | 337.8 | 321.5 | 321.9 | 340.5 | 324.7 | 313.5
1008 | 863 | 469 | 187.6 | 219.2936 | 331.5 | 293.4 | 311.3 | 317.4 | 446.6 | 50.1 | 19.6 | 94.7 | 9.1 | 284.9 | 11.9 | 696.9 | 581.6 | 527.1 | 662.9 | 538.9 | 697.4 | 533.9 | 588.8 | 747.3 | 530.6 | 280.5 | 330.3 | 337.3 | 321.8 | 321.7 | 339.9 | 324.2 | 313.4
1009 | 864 | 469.4 | 187.76 | 219.4806 | 333.1 | 293.1 | 310.9 | 316.6 | 443 | 50.1 | 19.6 | 94.9 | 7.6 | 262.1 | 13.2 | 695.4 | 577.6 | 531.5 | 662.4 | 537.6 | 697.1 | 533.2 | 587 | 746.9 | 530.2 | 280.6 | 330.2 | 337 | 321.9 | 321.7 | 339.7 | 324.1 | 313.4
1010 | 865 | 469.6 | 187.84 | 219.5741 | 334.8 | 293.1 | 310.5 | 316.4 | 443.9 | 49.8 | 19.6 | 94.8 | 5.9 | 273.7 | 11.6 | 692.8 | 568.1 | 517.3 | 660.9 | 535.8 | 696.3 | 532.6 | 579.7 | 746.6 | 529.2 | 280.7 | 330.6 | 337.1 | 322.1 | 321.7 | 339.6 | 324 | 313.4
1011 | 866 | 468.1 | 187.24 | 218.8728 | 334.8 | 293.1 | 311.3 | 316.9 | 445.4 | 49.7 | 19.6 | 94.8 | 6 | 252.4 | 10.7 | 689.5 | 557.9 | 499.9 | 658.8 | 533.4 | 695.5 | 538.2 | 574.7 | 746.3 | 528.3 | 280.9 | 331.2 | 337.6 | 322.6 | 321.7 | 339.6 | 324.1 | 313.3
1012 | 867 | 468.1 | 187.24 | 218.8728 | 334.1 | 293.7 | 312.3 | 317.6 | 445.2 | 49.7 | 19.6 | 94.8 | 6.5 | 246.7 | 9.6 | 685.5 | 546.6 | 484.1 | 656.6 | 530.8 | 694.7 | 542 | 568.1 | 745.9 | 527.6 | 281 | 332.1 | 338.3 | 323.3 | 321.8 | 339.6 | 324.2 | 313.3
1013 | 868 | 469.2 | 187.68 | 219.3871 | 335.8 | 294.6 | 313.5 | 318.5 | 442.7 | 49.5 | 19.6 | 95 | 6.5 | 235.7 | 7.7 | 682.3 | 537.8 | 472.1 | 654.6 | 528.6 | 693.7 | 540.7 | 561.1 | 745.8 | 527 | 281.1 | 332.2 | 338.6 | 323.5 | 321.9 | 339.6 | 324.3 | 313.3
1014 | 869 | 469.2 | 187.68 | 219.3871 | 336.6 | 295 | 314.8 | 319.5 | 440.1 | 49.5 | 19.6 | 95.2 | 7.8 | 250.6 | 5.8 | 680 | 535.9 | 471.9 | 653.2 | 527.9 | 692.7 | 543.8 | 559.1 | 745.5 | 526.2 | 281.3 | 332.4 | 338.7 | 323.6 | 321.8 | 340.7 | 324.5 | 313.4
1015 | 870 | 469.8 | 187.92 | 219.6677 | 334.8 | 295.2 | 315.2 | 320.4 | 440.6 | 49.5 | 19.6 | 95.3 | 7.4 | 252 | 7 | 679.3 | 545.3 | 488.6 | 652.5 | 528.6 | 692 | 547.9 | 561.9 | 744.8 | 526.4 | 281.4 | 332.4 | 338.9 | 323.5 | 321.9 | 341.4 | 324.7 | 313.5
1016 | 871 | 469.3 | 187.72 | 219.4339 | 334.6 | 295.4 | 315.1 | 320.9 | 441.8 | 49.6 | 19.6 | 95.4 | 7 | 247.5 | 9.1 | 679.8 | 557.9 | 513.5 | 653.1 | 530.8 | 691.8 | 550.5 | 570.9 | 743.8 | 526.9 | 281.6 | 332.3 | 338.9 | 323.3 | 321.9 | 341.4 | 324.9 | 313.6
1017 | 872 | 468.9 | 187.56 | 219.2468 | 336.6 | 294.9 | 315.2 | 320.9 | 442.9 | 49.7 | 19.6 | 95.4 | 6.3 | 255.7 | 9.1 | 681.8 | 570.1 | 513.2 | 655.5 | 530.4 | 692.2 | 549.5 | 581.9 | 744.3 | 528.1 | 281.7 | 332.5 | 339 | 323.2 | 321.9 | 340.9 | 324.8 | 313.7
1018 | 873 | 469.4 | 187.76 | 219.4806 | 337.4 | 294.6 | 315.2 | 320.2 | 441.4 | 49.7 | 19.6 | 95.4 | 6.2 | 291.1 | 8 | 682.7 | 568.9 | 503.5 | 655.9 | 530 | 691.9 | 546.1 | 575.1 | 744 | 527.1 | 281.8 | 332.4 | 338.9 | 323 | 321.9 | 341 | 325 | 313.7
1019 | 874 | 469.6 | 187.84 | 219.5741 | 338.4 | 294.5 | 315.1 | 319.4 | 438.3 | 49.6 | 19.6 | 95.3 | 5.5 | 274.1 | 8.1 | 681.7 | 555.1 | 493 | 654 | 528.7 | 690.9 | 541.9 | 566.2 | 743.3 | 526.2 | 281.9 | 332 | 338.9 | 322.8 | 322 | 340.6 | 325.1 | 313.8
1020 | 875 | 469.4 | 187.76 | 219.4806 | 336.8 | 294.3 | 315.2 | 318.7 | 435.1 | 49.6 | 19.6 | 95.2 | 5.2 | 254.7 | 10.2 | 680.1 | 549.4 | 488.5 | 652.1 | 528.2 | 689.7 | 536.7 | 560.3 | 742.8 | 525.4 | 282.1 | 331.7 | 338.8 | 322.6 | 322 | 340.2 | 325.2 | 313.9
1021 | 876 | 469.8 | 187.92 | 219.6677 | 335.3 | 293.7 | 314.9 | 318.7 | 432.4 | 49.6 | 19.6 | 95.2 | 6.1 | 273.9 | 10.6 | 678.9 | 550.5 | 487.1 | 651.1 | 528.2 | 688.9 | 535 | 557.9 | 741.9 | 524.7 | 282.2 | 331.3 | 338.3 | 322.4 | 322 | 340.1 | 325.2 | 313.9
1022 | 877 | 469 | 187.6 | 219.2936 | 334.1 | 293.5 | 314.2 | 317.9 | 430.4 | 49.7 | 19.6 | 95.1 | 7.3 | 278.3 | 11 | 679.3 | 548.9 | 478.9 | 650.5 | 527.3 | 688.2 | 532.1 | 554.3 | 741.1 | 524.1 | 282.3 | 330.7 | 337.7 | 322.4 | 322.1 | 339.8 | 325 | 314
1023 | 878 | 469.1 | 187.64 | 219.3403 | 332.6 | 293 | 313.2 | 316.7 | 425.9 | 49.6 | 19.6 | 95.2 | 7.8 | 280.1 | 12.4 | 679.7 | 548.6 | 475.2 | 649.5 | 526.8 | 687.9 | 529.9 | 555 | 740.7 | 523.6 | 282.4 | 330 | 337 | 322.4 | 322.1 | 339.4 | 324.6 | 313.9
1024 | 879 | 469.2 | 187.68 | 219.3871 | 332.2 | 292.6 | 311.7 | 316.1 | 424.9 | 49.6 | 19.6 | 95.3 | 6.8 | 280.6 | 13.1 | 679.2 | 552.7 | 473.9 | 649.2 | 526 | 687.7 | 527.9 | 555.5 | 740.3 | 523.6 | 282.6 | 329.3 | 336 | 322.4 | 322 | 338.8 | 324.3 | 313.9
1025 | 880 | 468.7 | 187.48 | 219.1533 | 332.1 | 292.5 | 310.1 | 315.3 | 425.7 | 49.7 | 19.6 | 95.3 | 6.7 | 282.9 | 13.6 | 677.4 | 547.1 | 463.8 | 648.7 | 524.4 | 687.3 | 525.2 | 552.5 | 740.1 | 523.4 | 282.7 | 328.2 | 334.8 | 322.4 | 322 | 338.1 | 323.8 | 313.8
1026 | 881 | 469.8 | 187.92 | 219.6677 | 332.4 | 292.5 | 308.8 | 314.5 | 428.2 | 49.7 | 19.6 | 95.4 | 6.9 | 285.4 | 14 | 677.9 | 549.7 | 468.7 | 648.9 | 524.6 | 686.9 | 522.2 | 554.3 | 740.2 | 523.1 | 282.8 | 327.4 | 334.1 | 322.4 | 321.9 | 337.4 | 323.3 | 313.8
1027 | 882 | 469.5 | 187.8 | 219.5274 | 332.5 | 292.8 | 307.8 | 314.3 | 429.5 | 49.7 | 19.6 | 95.4 | 6.6 | 276.9 | 14.4 | 682.2 | 571 | 495.8 | 650.9 | 528.2 | 686.7 | 521.6 | 564.7 | 740.5 | 524.4 | 282.9 | 325.2 | 332.8 | 322.3 | 321.8 | 336.8 | 322.7 | 313.7
1028 | 883 | 469.9 | 187.96 | 219.7144 | 331.9 | 293.1 | 308 | 314.6 | 431.6 | 49.7 | 19.6 | 95.5 | 6.2 | 280.2 | 13.2 | 682.6 | 573.4 | 498.6 | 650.1 | 528.9 | 686.5 | 521.3 | 570.2 | 740.4 | 525.7 | 283 | 324.7 | 332.1 | 322.4 | 321.7 | 336.7 | 322.5 | 313.6
1029 | 884 | 471.7 | 188.68 | 220.556 | 332.4 | 293.4 | 308 | 314.6 | 437.2 | 49.7 | 19.6 | 95.6 | 6.6 | 290.2 | 15.7 | 685.9 | 593.5 | 526.9 | 653.1 | 532.1 | 686.4 | 521.8 | 585.4 | 740.6 | 526.6 | 283.2 | 325 | 331.8 | 322.6 | 321.6 | 336.8 | 322.2 | 313.6
1030 | 885 | 470.9 | 188.36 | 220.182 | 332.5 | 293.6 | 309.1 | 315.4 | 443.3 | 49.6 | 19.6 | 95.6 | 6.2 | 299.2 | 16 | 693.6 | 633.8 | 554.7 | 660.5 | 536.8 | 687.1 | 527.1 | 618.2 | 742.3 | 532.5 | 283.3 | 325.2 | 332 | 322.7 | 321.6 | 336.6 | 322 | 313.6
1031 | 886 | 471.2 | 188.48 | 220.3223 | 332.1 | 293.6 | 309.5 | 316.1 | 455.1 | 49.5 | 19.6 | 95.7 | 5.4 | 293.1 | 16.4 | 697.9 | 643.6 | 551.9 | 664.5 | 536.3 | 687.6 | 530.8 | 619.4 | 742.2 | 533 | 283.4 | 325.6 | 332.7 | 323 | 321.5 | 337 | 322 | 313.6
1032 | 887 | 471 | 188.4 | 220.2287 | 330.9 | 294 | 310.7 | 317.2 | 456.5 | 49.6 | 19.6 | 95.8 | 4.7 | 284.2 | 15.8 | 700.6 | 643.7 | 545.8 | 666.3 | 536 | 687.9 | 532 | 618.2 | 741.6 | 533.2 | 283.5 | 326.2 | 333.7 | 323 | 321.5 | 337.7 | 322 | 313.6
1033 | 888 | 470.6 | 188.24 | 220.0417 | 329.5 | 294 | 312.2 | 318.7 | 456.1 | 49.8 | 19.6 | 95.8 | 4.7 | 290.8 | 14.1 | 700.6 | 645.5 | 536 | 666.7 | 536.3 | 688 | 532.4 | 612.6 | 741.2 | 533.7 | 283.6 | 326.8 | 334.8 | 323.2 | 321.5 | 337.7 | 321.9 | 313.7
1034 | 889 | 469 | 187.6 | 219.2936 | 329.2 | 293.3 | 314.1 | 319.4 | 455.6 | 49.8 | 19.6 | 95.7 | 5.1 | 296.7 | 13.4 | 698.9 | 630.8 | 521.7 | 665.2 | 535 | 687.7 | 531 | 603.1 | 740 | 533.4 | 283.8 | 327.3 | 335.4 | 323.2 | 321.5 | 337.7 | 321.9 | 313.8
1035 | 890 | 470.3 | 188.12 | 219.9014 | 329.6 | 293.2 | 314.5 | 319.9 | 450.7 | 49.9 | 19.6 | 95.7 | 5.6 | 278.9 | 11.4 | 694.3 | 610.6 | 509.2 | 661.3 | 533.2 | 686.8 | 527.2 | 590.6 | 739.1 | 532.5 | 283.9 | 327.5 | 335.8 | 323.1 | 321.6 | 337.8 | 322.3 | 313.8
1036 | 891 | 470 | 188 | 219.7612 | 329.1 | 293.4 | 314.7 | 319.8 | 445.9 | 49.9 | 19.6 | 95.6 | 5 | 285.4 | 9.4 | 689 | 592 | 496.8 | 657.5 | 531.3 | 685.8 | 521.7 | 579.9 | 738.3 | 531.5 | 284 | 327.5 | 336.2 | 323 | 321.7 | 337.7 | 322.6 | 314
1037 | 892 | 470.1 | 188.04 | 219.8079 | 327.7 | 293.4 | 314.9 | 319.2 | 440.5 | 50 | 19.6 | 95.5 | 5.6 | 289.8 | 8.8 | 684.6 | 578.5 | 491.9 | 653.4 | 530 | 684.9 | 518 | 571.6 | 737.2 | 530.8 | 284.1 | 327.4 | 336.2 | 322.8 | 321.8 | 337.4 | 322.8 | 314.1
1038 | 893 | 470.6 | 188.24 | 220.0417 | 327.4 | 293.4 | 314.5 | 318.2 | 435.3 | 50.1 | 19.6 | 95.3 | 6.3 | 276.1 | 8.7 | 681.3 | 580.5 | 491.8 | 650.8 | 529.3 | 684.5 | 516.1 | 569 | 736.3 | 530.2 | 284.2 | 327.3 | 336.3 | 322.6 | 321.7 | 336.9 | 322.9 | 314.2
1039 | 894 | 471 | 188.4 | 220.2287 | 329 | 293.6 | 313.8 | 316.7 | 433.4 | 50.2 | 19.6 | 95.3 | 7.2 | 266.2 | 7.8 | 680.6 | 584.5 | 502 | 650.9 | 530.1 | 684.7 | 516.8 | 570 | 735.6 | 530.4 | 284.3 | 327.1 | 336.3 | 322.5 | 321.7 | 336.3 | 322.8 | 314.2
1040 | 895 | 470.4 | 188.16 | 219.9482 | 328.9 | 293.4 | 312.9 | 315.8 | 429.7 | 50.3 | 19.6 | 95.3 | 7.3 | 263.2 | 7.6 | 678.8 | 578.4 | 500.3 | 649.4 | 529.2 | 684.8 | 516 | 565.6 | 735.3 | 529.8 | 284.4 | 326.9 | 336 | 322.5 | 321.6 | 335.9 | 322.6 | 314.1
1041 | 896 | 470.5 | 188.2 | 219.995 | 328.8 | 293.2 | 312 | 315.1 | 427.9 | 50.3 | 19.6 | 95.4 | 7.1 | 270.3 | 7.7 | 676.2 | 568.2 | 496.5 | 647.1 | 527.5 | 684.4 | 513.7 | 562 | 734.8 | 529.3 | 284.5 | 326.9 | 335.5 | 322.6 | 321.5 | 335.7 | 322.2 | 314
1042 | 897 | 470.6 | 188.24 | 220.0417 | 329.9 | 292.5 | 310.9 | 313.6 | 428.6 | 50.3 | 19.5 | 95.4 | 6.7 | 286 | 9 | 675.9 | 566.9 | 495.5 | 646.2 | 526.3 | 684.1 | 512.4 | 557.9 | 734.7 | 528.8 | 284.6 | 326.7 | 335 | 322.7 | 321.5 | 335.5 | 321.9 | 314
1043 | 898 | 470 | 188 | 219.7612 | 330.6 | 292 | 309.9 | 312.8 | 425.8 | 50.3 | 19.5 | 95.4 | 5.5 | 282.3 | 10.2 | 675.2 | 563.1 | 492.2 | 644.8 | 525 | 683.8 | 512 | 557.8 | 734.8 | 528.3 | 284.7 | 326.6 | 334.5 | 322.9 | 321.5 | 335.8 | 321.8 | 314
1044 | 899 | 468 | 187.2 | 218.826 | 331.7 | 291.9 | 309 | 312.9 | 424.4 | 50.3 | 19.5 | 95.4 | 4.9 | 257.6 | 11 | 674.4 | 559 | 486.3 | 643.4 | 524.6 | 683.3 | 510.4 | 554.5 | 734.5 | 527.7 | 284.8 | 326.2 | 334.1 | 322.7 | 321.5 | 336.1 | 321.7 | 314
1045 | 900 | 467.7 | 187.08 | 218.6857 | 334.4 | 292 | 308.5 | 312.7 | 421.1 | 50.2 | 19.5 | 95.3 | 5.3 | 263.9 | 10.4 | 672.3 | 555.9 | 481.8 | 641.4 | 523.8 | 682.8 | 508.2 | 549.9 | 734 | 526.7 | 284.9 | 326 | 334.3 | 322.6 | 321.6 | 336.1 | 321.7 | 314
1046 | 901 | 469.7 | 187.88 | 219.6209 | 335.1 | 292.3 | 308.7 | 312.8 | 421.9 | 50 | 19.5 | 95.3 | 5.8 | 264 | 10.9 | 670.8 | 559.4 | 481.3 | 640.8 | 522.9 | 682.4 | 507 | 546.9 | 733.9 | 526.2 | 285.1 | 325.8 | 334.3 | 322.5 | 321.7 | 336 | 321.9 | 314.1
1047 | 902 | 469 | 187.6 | 219.2936 | 335.2 | 292.4 | 309.5 | 312.6 | 419.7 | 49.8 | 19.5 | 95.4 | 7.3 | 248.4 | 10.4 | 673.9 | 576.4 | 488 | 644.5 | 524.4 | 682.3 | 506.4 | 549.5 | 733.9 | 526.2 | 285.2 | 325.4 | 334 | 322.3 | 321.7 | 335.7 | 322 | 314.1
1048 | 903 | 469.2 | 187.68 | 219.3871 | 334.8 | 292 | 310 | 312.3 | 417.2 | 49.7 | 19.5 | 95.6 | 6.8 | 274 | 9.1 | 674.2 | 577.9 | 487.5 | 645.1 | 525 | 682.1 | 505.7 | 551.3 | 733.2 | 525.9 | 285.3 | 325.1 | 333.7 | 322.1 | 321.7 | 335.6 | 322.3 | 314.2
1049 | 904 | 469.5 | 187.8 | 219.5274 | 334.8 | 291.3 | 309.5 | 311.7 | 416.6 | 49.6 | 19.5 | 95.7 | 6.9 | 258 | 10 | 676.3 | 587.7 | 510.1 | 646.7 | 528.1 | 682.4 | 506.9 | 558.7 | 733.1 | 526.2 | 285.4 | 325.2 | 333.5 | 322.2 | 321.6 | 335.1 | 322.2 | 314.2
1050 | 905 | 469 | 187.6 | 219.2936 | 335.9 | 290.6 | 309.2 | 311.2 | 418.1 | 49.7 | 19.5 | 95.8 | 6.7 | 268.4 | 9.5 | 678 | 597.1 | 513.9 | 648 | 529.1 | 682.8 | 509.4 | 563.9 | 733.1 | 526.6 | 285.5 | 325.6 | 333.6 | 322.5 | 321.5 | 334.4 | 321.9 | 314.1
1051 | 906 | 468.4 | 187.36 | 219.013 | 337 | 290.5 | 309.9 | 310.3 | 421.4 | 49.7 | 19.5 | 95.7 | 6.1 | 258.9 | 7.9 | 677.1 | 594.6 | 512.5 | 647.1 | 528.3 | 682.6 | 509.2 | 558.2 | 732.7 | 525.9 | 285.5 | 326.2 | 333.9 | 322.7 | 321.4 | 334.4 | 321.8 | 314.1
1052 | 907 | 468.2 | 187.28 | 218.9195 | 337.8 | 290.5 | 310.8 | 309.4 | 421.6 | 49.7 | 19.5 | 95.6 | 6.6 | 283.4 | 8.5 | 677.7 | 595.6 | 517.8 | 647 | 528.5 | 682.3 | 508.5 | 559.3 | 732.5 | 525.9 | 285.6 | 326.5 | 334.2 | 322.9 | 321.4 | 335 | 322 | 314.1
1053 | 908 | 467.3 | 186.92 | 218.4987 | 337.2 | 291.3 | 311.7 | 309 | 422.2 | 49.7 | 19.5 | 95.5 | 5.3 | 281.7 | 9.6 | 679.1 | 600.2 | 534.5 | 647.4 | 529.8 | 681.9 | 507.7 | 559.9 | 732.1 | 525.6 | 285.7 | 326.8 | 334.7 | 323.1 | 321.4 | 335 | 321.8 | 314
1054 | 909 | 468.1 | 187.24 | 218.8728 | 337.6 | 291.6 | 312.7 | 309.3 | 423 | 49.8 | 19.5 | 95.4 | 5.7 | 282 | 9.9 | 685.3 | 629 | 554.5 | 653.4 | 532.6 | 682.2 | 511.3 | 581.5 | 732.9 | 528.4 | 285.8 | 327.1 | 335.2 | 323.3 | 321.4 | 334.9 | 321.6 | 314
1055 | 910 | 468 | 187.2 | 218.826 | 339.1 | 291.5 | 313.7 | 309.5 | 424.4 | 49.8 | 19.5 | 95.3 | 6.5 | 277.5 | 9.9 | 689.6 | 638.2 | 555 | 656.1 | 534.7 | 682.2 | 513 | 581.6 | 732.9 | 528.5 | 285.9 | 327.2 | 335.5 | 323.4 | 321.5 | 335 | 321.6 | 314
1056 | 911 | 469.1 | 187.64 | 219.3403 | 338.6 | 291.6 | 314.1 | 310.2 | 424.1 | 49.8 | 19.5 | 95.3 | 6.1 | 277.7 | 10.3 | 687.8 | 625.6 | 542.1 | 654.4 | 533.4 | 682 | 513.6 | 576.2 | 732.4 | 528.1 | 286 | 327 | 335.6 | 323.2 | 321.5 | 335.4 | 321.8 | 314
1057 | 912 | 468.8 | 187.52 | 219.2001 | 337.4 | 292 | 313.8 | 311.9 | 420.7 | 50 | 19.5 | 95.4 | 5 | 276.6 | 10.3 | 683.7 | 613.2 | 530.8 | 651.9 | 532.3 | 681.4 | 511.1 | 568.8 | 731.4 | 527 | 286.1 | 326.7 | 335.4 | 322.9 | 321.5 | 335.7 | 321.7 | 314
1058 | 913 | 469.3 | 187.72 | 219.4339 | 337.3 | 292.4 | 313.2 | 313 | 417 | 49.9 | 19.5 | 95.4 | 5.1 | 272.6 | 10.6 | 681.3 | 610.3 | 531.6 | 650 | 532.5 | 681.3 | 511 | 569.5 | 730.9 | 526.7 | 286.2 | 326.5 | 334.9 | 322.8 | 321.4 | 335.9 | 321.6 | 314.1
1059 | 914 | 471.2 | 188.48 | 220.3223 | 337.5 | 292.5 | 312 | 313.5 | 415.5 | 49.9 | 19.5 | 95.5 | 6.3 | 273.5 | 11 | 680.4 | 618.6 | 544.4 | 649.6 | 534.7 | 681.3 | 511.4 | 568.8 | 730.3 | 526.5 | 286.3 | 326.2 | 334.2 | 322.7 | 321.5 | 336 | 321.7 | 314.2
1060 | 915 | 471.2 | 188.48 | 220.3223 | 340.6 | 292.2 | 310.7 | 313.6 | 416.3 | 50 | 19.5 | 95.5 | 5.3 | 273.3 | 12 | 679.9 | 624.7 | 550.5 | 650.2 | 535.2 | 681.8 | 513.2 | 571.5 | 729.9 | 526.7 | 286.4 | 325.8 | 333.6 | 322.6 | 321.6 | 336.1 | 321.9 | 314.2
1061 | 916 | 470.6 | 188.24 | 220.0417 | 340 | 292 | 310.1 | 313.5 | 417.3 | 50 | 19.5 | 95.4 | 5.2 | 264.9 | 12.5 | 681.7 | 629.3 | 546.4 | 653.8 | 535.2 | 682.3 | 513.9 | 576.4 | 730 | 526.7 | 286.5 | 325.3 | 333.2 | 322.6 | 321.6 | 336.3 | 321.8 | 314.2
1062 | 917 | 469.6 | 187.84 | 219.5741 | 337.2 | 291.9 | 309.4 | 312.8 | 416.9 | 50 | 19.5 | 95.4 | 5.2 | 279.3 | 13.1 | 683.9 | 636.6 | 561.8 | 657.6 | 536.3 | 682.7 | 514.6 | 577.4 | 729.6 | 526.8 | 286.6 | 324.7 | 332.7 | 322.5 | 321.6 | 336.3 | 321.7 | 314.2
1063 | 918 | 470 | 188 | 219.7612 | 334.6 | 292 | 308.4 | 312 | 417.5 | 50.1 | 19.5 | 95.5 | 6.2 | 275.8 | 15 | 683.7 | 633.4 | 549.6 | 658.5 | 535.2 | 682.8 | 514.8 | 576.2 | 729.4 | 526.9 | 286.7 | 323.8 | 332 | 322.5 | 321.6 | 337.7 | 321.9 | 314.2
1064 | 919 | 470.2 | 188.08 | 219.8547 | 333.8 | 291.4 | 307.2 | 312.4 | 416.7 | 50.2 | 19.5 | 95.7 | 6.2 | 287.9 | 14.5 | 682.2 | 620.8 | 542.4 | 657.7 | 534.3 | 682.5 | 513.1 | 571.2 | 728.7 | 526.2 | 286.8 | 323.1 | 331.2 | 322.2 | 321.6 | 337.6 | 321.7 | 314.2
1065 | 920 | 470.4 | 188.16 | 219.9482 | 334.7 | 290.9 | 306.2 | 312.9 | 417.2 | 50.4 | 19.5 | 95.9 | 6.4 | 281.1 | 12.2 | 681.4 | 617.9 | 536 | 657.6 | 534.2 | 682 | 510.7 | 566.2 | 728.4 | 525.5 | 286.9 | 322.6 | 330.3 | 322.1 | 321.6 | 337 | 321.4 | 314.2
1066 | 921 | 469.9 | 187.96 | 219.7144 | 335 | 290.2 | 305.1 | 312.8 | 416.3 | 50.6 | 19.5 | 96.1 | 6.9 | 275.7 | 11.3 | 682.5 | 617.6 | 534.3 | 658.4 | 534.1 | 681.8 | 510.5 | 568.7 | 727.9 | 525.9 | 286.9 | 322 | 329.3 | 322 | 321.5 | 336.6 | 321.2 | 314.1
1067 | 922 | 469.9 | 187.96 | 219.7144 | 333.2 | 290 | 303.9 | 312.8 | 421 | 50.7 | 19.5 | 96.2 | 6.5 | 265.4 | 13.5 | 682.8 | 619.3 | 535 | 658.6 | 534.1 | 681.8 | 510.6 | 568.9 | 727.8 | 525.7 | 287 | 321.5 | 328.3 | 321.9 | 321.5 | 336.1 | 321 | 314.1
1068 | 923 | 470.4 | 188.16 | 219.9482 | 331.1 | 289.6 | 303.8 | 313.1 | 420.1 | 50.9 | 19.5 | 96.4 | 6.6 | 266.4 | 13.6 | 683.1 | 615.3 | 541.8 | 657.8 | 533.5 | 681.7 | 510.9 | 568.1 | 727.6 | 525.3 | 287.1 | 321.2 | 328 | 321.9 | 321.4 | 335.7 | 320.7 | 314
1069 | 924 | 469.9 | 187.96 | 219.7144 | 332.8 | 289.8 | 304 | 312.6 | 422 | 51 | 19.5 | 96.6 | 6.1 | 264.4 | 12.4 | 684.4 | 618.6 | 543.8 | 658 | 533.4 | 681.5 | 510.6 | 569.2 | 727.3 | 525.1 | 287.2 | 321.2 | 328.2 | 322 | 321.3 | 335.9 | 320.6 | 314
1070 | 925 | 469.7 | 187.88 | 219.6209 | 335.7 | 289.8 | 304.3 | 312.5 | 421.3 | 51.1 | 19.5 | 96.8 | 5.4 | 280.7 | 11.6 | 688.6 | 637.3 | 559 | 661.5 | 535.5 | 681.6 | 512 | 577.3 | 727.2 | 525.7 | 287.3 | 321.1 | 328.2 | 322 | 321.2 | 335.4 | 320.4 | 313.9
1071 | 926 | 469.6 | 187.84 | 219.5741 | 334.9 | 289.5 | 304.1 | 313.3 | 419.4 | 51.2 | 19.5 | 96.9 | 6.1 | 266.8 | 11.5 | 690.8 | 646.3 | 576.8 | 664.8 | 537.9 | 682.1 | 514.5 | 588.2 | 727.4 | 527 | 287.4 | 321 | 328.1 | 322.1 | 321.1 | 335 | 320.3 | 313.9
1072 | 927 | 440.1 | 176.04 | 205.7806 | 334.4 | 289.4 | 304 | 313.5 | 419.8 | 51.2 | 19.5 | 97 | 5.9 | 287 | 11 | 693.2 | 648.4 | 587.7 | 667 | 540.3 | 682.1 | 515.6 | 592.2 | 727.4 | 527.7 | 287.5 | 320.7 | 327.8 | 322.1 | 321.1 | 335.2 | 320.3 | 313.9
1073 | 928 | 71.3 | 28.52 | 33.3382 | 335.1 | 289 | 304.1 | 314.1 | 417.9 | 51.2 | 19.5 | 97.1 | 7.4 | 272.8 | 10.7 | 695.6 | 657.1 | 586.7 | 669.5 | 541.3 | 682.2 | 516.1 | 590.2 | 727.2 | 528 | 287.5 | 320.7 | 327.5 | 321.9 | 321.1 | 335.5 | 321 | 314
1074 | 929 | -6.9 | 0 | 0 | 335 | 289 | 304.2 | 314.5 | 414.1 | 51.2 | 19.5 | 97.2 | 6.7 | 294.1 | 9.1 | 692.2 | 636.5 | 559.9 | 666.3 | 538.3 | 682 | 514.2 | 580.2 | 726.6 | 526.7 | 287.6 | 321 | 327.5 | 321.8 | 321.1 | 335.4 | 320.8 | 314
1075 | 930 | -7 | 0 | 0 | 334.1 | 288.6 | 303.9 | 314.3 | 408.1 | 51.2 | 19.5 | 97.3 | 5.9 | 285.6 | 7.1 | 683.5 | 610.8 | 531.7 | 660.8 | 533.9 | 681.1 | 510 | 567.5 | 725.9 | 525 | 287.7 | 320.5 | 327.3 | 321.3 | 321.1 | 335.1 | 320.3 | 313.9
1076 | 931 | -7 | 0 | 0 | 332.7 | 288.2 | 303.8 | 313.3 | 400.8 | 51.3 | 19.5 | 97.3 | 5.5 | 279 | 6.5 | 675.8 | 587 | 506.8 | 655.8 | 529.8 | 680.4 | 504.4 | 553.3 | 724.4 | 523.3 | 287.8 | 319.8 | 326.8 | 320.7 | 321 | 334.8 | 319.6 | 313.7
1077 | 932 | -6.9 | 0 | 0 | 331 | 288 | 303 | 311.9 | 394.8 | 51.3 | 19.5 | 97.4 | 5.7 | 276.6 | 7.1 | 669.2 | 565.6 | 481.9 | 651.2 | 525.7 | 679.8 | 497 | 540.6 | 723.3 | 521.9 | 287.9 | 319 | 326.2 | 320.1 | 320.8 | 334 | 318.8 | 313.5
1078 | 933 | -6.9 | 0 | 0 | 329.1 | 287.4 | 301.7 | 310.2 | 390.2 | 51.3 | 19.5 | 97.3 | 5 | 281.9 | 9.4 | 663.8 | 543.5 | 458.8 | 647 | 521.8 | 679.1 | 491.2 | 528.6 | 721.5 | 520 | 288 | 318 | 326.5 | 319.6 | 320.6 | 333 | 317.9 | 313.2
1079 | 934 | -6.9 | 0 | 0 | 328.8 | 286.3 | 300.2 | 308.2 | 385.1 | 51.2 | 19.5 | 97.1 | 5.3 | 272.7 | 12.1 | 659.3 | 527.3 | 439.7 | 643 | 518.3 | 678.5 | 486.2 | 520 | 719.7 | 518.3 | 288 | 316.8 | 326.4 | 319 | 320.2 | 332.1 | 316.9 | 312.9
1080 | 935 | -6.9 | 0 | 0 | 330.7 | 284.4 | 298.9 | 305.7 | 381.1 | 51.1 | 19.5 | 96.8 | 5.5 | 283.9 | 12.6 | 655.2 | 513.5 | 423 | 639.2 | 514.9 | 677.6 | 481.4 | 511.7 | 718.2 | 516.8 | 288.1 | 315.1 | 325.3 | 318.4 | 319.8 | 331 | 315.6 | 312.6
1081 | 936 | -6.9 | 0 | 0 | 333.6 | 282.5 | 297.5 | 303.3 | 377.2 | 51.1 | 19.5 | 96.4 | 4.3 | 282.8 | 12.2 | 651.3 | 499.4 | 407.2 | 635.3 | 511.5 | 677 | 476.8 | 502.8 | 715.6 | 515.2 | 288.2 | 313.2 | 324.3 | 317.7 | 319.4 | 329.6 | 314 | 312.3
1082 | 937 | -6.9 | 0 | 0 | 333.6 | 281 | 296.3 | 301.2 | 372.8 | 51.2 | 19.5 | 96 | 5.2 | 282.9 | 11.9 | 647 | 488 | 392.7 | 631.9 | 508.4 | 676.3 | 472.9 | 494.7 | 713.5 | 513.5 | 288.3 | 311.6 | 323.1 | 317.2 | 318.9 | 328.4 | 312.4 | 311.9
1083 | 938 | -6.9 | 0 | 0 | 331.9 | 279.4 | 295.3 | 299.3 | 369.1 | 51.4 | 19.5 | 95.5 | 5.8 | 273.2 | 10.9 | 641.5 | 477.8 | 380 | 628.2 | 505.1 | 675.3 | 469 | 488.2 | 711.7 | 511.7 | 288.4 | 310.4 | 322.1 | 316.7 | 318.3 | 327.3 | 310.9 | 311.6
1084 | 939 | -6.9 | 0 | 0 | 331.4 | 278.3 | 294.5 | 297.4 | 365.2 | 51.4 | 19.5 | 95 | 5.4 | 266.6 | 9.8 | 636.4 | 464.9 | 368.6 | 625 | 502.1 | 674.6 | 466.4 | 481.6 | 710.1 | 510.5 | 288.4 | 309.1 | 321.1 | 316.3 | 317.6 | 325.9 | 309.5 | 311.2
1085 | 940 | -6.9 | 0 | 0 | 332.2 | 276.9 | 293.5 | 295.7 | 361.2 | 51.3 | 19.5 | 94.6 | 5.4 | 262.2 | 8.8 | 632 | 454.7 | 355.8 | 622.2 | 499 | 673.9 | 463.7 | 475.6 | 708.9 | 509.3 | 288.5 | 307.8 | 320.1 | 315.9 | 316.9 | 324.8 | 308.1 | 310.8
1086 | 941 | -6.9 | 0 | 0 | 330.4 | 275.6 | 292.5 | 294.1 | 357.7 | 51.2 | 19.5 | 94.1 | 5.3 | 268.6 | 9.4 | 627.6 | 446.5 | 344.4 | 619.1 | 496.3 | 673.3 | 460.3 | 470.6 | 707 | 507.9 | 288.5 | 306.6 | 319 | 315.6 | 316.3 | 324.2 | 306.6 | 310.5
1087 | 942 | -6.9 | 0 | 0 | 329.5 | 274.3 | 291.3 | 292.5 | 354.7 | 51.2 | 19.5 | 93.6 | 5.1 | 267.6 | 9.5 | 623.4 | 437.4 | 333.2 | 616.3 | 493.3 | 672.6 | 457.6 | 466 | 705.5 | 506.4 | 288.6 | 305.4 | 317.9 | 315.3 | 315.6 | 323 | 305.1 | 310.2
1088 | 943 | -6.9 | 0 | 0 | 328.9 | 273 | 289.8 | 290.7 | 351.8 | 51.1 | 19.5 | 93.1 | 4.7 | 269.6 | 9.9 | 619.7 | 429.1 | 323.2 | 613.8 | 490.2 | 672 | 455 | 461.9 | 704.1 | 504.9 | 288.7 | 304.1 | 316.9 | 314.9 | 314.8 | 321.7 | 303.3 | 309.7
1089 | 944 | -6.9 | 0 | 0 | 327.3 | 272.4 | 288 | 288.9 | 350 | 51.1 | 19.5 | 92.5 | 4.4 | 260.7 | 10.8 | 615.2 | 422.3 | 312.5 | 610.7 | 487 | 671.5 | 451.8 | 457 | 702.6 | 503.3 | 288.7 | 302.7 | 316 | 314.5 | 314.1 | 320.6 | 301.6 | 309.4
1090 | 945 | -6.9 | 0 | 0 | 325.6 | 271.6 | 286.4 | 287.3 | 347.3 | 51.1 | 19.5 | 92 | 4.1 | 256.1 | 11.6 | 609.9 | 416.2 | 302.9 | 606.9 | 483.7 | 670.8 | 449.1 | 452.5 | 701.3 | 501.6 | 288.8 | 301.4 | 315 | 314 | 313.3 | 319.6 | 300.1 | 309
1091 | 946 | -6.9 | 0 | 0 | 323.2 | 270.4 | 284.9 | 285.8 | 344.2 | 51.2 | 19.5 | 91.5 | 4.3 | 276.6 | 10.1 | 604.7 | 409.1 | 294.4 | 603.6 | 480.6 | 670.3 | 446.7 | 449.3 | 700.3 | 499.6 | 288.8 | 300 | 314 | 313.5 | 312.4 | 318.4 | 298.9 | 308.5
1092 | 947 | -6.9 | 0 | 0 | 321.9 | 269.2 | 283.7 | 284.3 | 341.1 | 51.3 | 19.5 | 91 | 5.1 | 263.3 | 10.8 | 600 | 404.3 | 287.4 | 601.5 | 478 | 669.7 | 443.9 | 445.6 | 699.1 | 498.3 | 288.8 | 298.6 | 313 | 313 | 311.5 | 317.1 | 297.6 | 308.2
1093 | 948 | -6.9 | 0 | 0 | 320.9 | 268 | 282.5 | 283 | 338.3 | 51.4 | 19.5 | 90.6 | 5.1 | 267 | 11.4 | 596.2 | 397.8 | 280.7 | 599.8 | 475.2 | 669.3 | 441 | 441.9 | 698.6 | 497 | 288.9 | 297.3 | 311.9 | 312.7 | 310.7 | 315.7 | 296.2 | 307.8
1094 | 949 | -6.9 | 0 | 0 | 320 | 266.7 | 281 | 281.4 | 335.5 | 51.4 | 19.5 | 90.2 | 5.1 | 264.7 | 10.7 | 592.5 | 392.9 | 274.8 | 597.8 | 472.5 | 668.8 | 438.2 | 438 | 698.2 | 495.8 | 288.9 | 295.9 | 310.9 | 312.3 | 309.8 | 314.5 | 294.8 | 307.4
1095 | 950 | -6.9 | 0 | 0 | 319.1 | 265.4 | 279.4 | 280.1 | 333.3 | 51.3 | 19.5 | 89.8 | 4.5 | 271.2 | 10.1 | 587.8 | 389.1 | 268.8 | 595.3 | 469.6 | 668.3 | 436.1 | 435.5 | 697.1 | 494.2 | 289 | 294.7 | 309.9 | 311.9 | 308.9 | 313.2 | 293.5 | 307.1
1096 | 951 | -6.9 | 0 | 0 | 318.6 | 264.1 | 278 | 278.5 | 330.9 | 51.3 | 19.5 | 89.5 | 4.7 | 266.5 | 10 | 583 | 384.2 | 261.8 | 591.5 | 466.4 | 667.6 | 434.5 | 433.3 | 696.4 | 492.3 | 289 | 293.5 | 309.1 | 311.3 | 308.1 | 312 | 292.3 | 306.7
1097 | 952 | -6.9 | 0 | 0 | 318.8 | 263 | 276.7 | 276.8 | 328.7 | 51.3 | 19.5 | 89.2 | 4.6 | 268.2 | 10.9 | 578.3 | 380.5 | 255.3 | 589.2 | 463.8 | 667 | 433.5 | 430.5 | 695.2 | 490.6 | 289 | 292.2 | 308.2 | 310.8 | 307.3 | 310.9 | 291.2 | 306.3
1098 | 953 | -6.9 | 0 | 0 | 318.7 | 261.9 | 275.7 | 275.7 | 326.6 | 51.3 | 19.5 | 88.9 | 4.7 | 266.8 | 11 | 574.5 | 375.3 | 250 | 587.2 | 461.4 | 666.4 | 432 | 427.3 | 694.9 | 489.4 | 289 | 291 | 307.3 | 310.4 | 306.4 | 309.8 | 290.5 | 305.9
1099 | 954 | -6.9 | 0 | 0 | 317.7 | 260.8 | 274.8 | 274.7 | 324.8 | 51.3 | 19.5 | 88.5 | 5.3 | 262.1 | 10.3 | 571.5 | 370.4 | 245.7 | 585.3 | 459.3 | 665.9 | 430.3 | 424.4 | 694.2 | 488.4 | 289 | 289.9 | 306.3 | 310 | 305.4 | 308.9 | 289.5 | 305.5
1100 | 955 | -6.9 | 0 | 0 | 317 | 259.7 | 273.8 | 273.6 | 323.4 | 51.3 | 19.5 | 88.2 | 6.3 | 262.5 | 9.3 | 569 | 365.7 | 241.1 | 583.5 | 457.4 | 665.6 | 428.2 | 421.3 | 693.4 | 487.2 | 289.1 | 289 | 305.4 | 309.6 | 304.5 | 308.1 | 288.5 | 305.2
1101 | 956 | -6.9 | 0 | 0 | 316 | 258.7 | 272.8 | 272.7 | 322.4 | 51.4 | 19.5 | 87.9 | 7.7 | 275.3 | 7.7 | 567 | 361.8 | 236.2 | 581.4 | 455.4 | 665.3 | 427.1 | 419.1 | 692.9 | 486.2 | 289.1 | 287.9 | 304.6 | 309.2 | 303.6 | 307.5 | 287.3 | 304.9
1102 | 957 | -6.9 | 0 | 0 | 315.9 | 257.8 | 271.8 | 272.1 | 321 | 51.4 | 19.5 | 87.7 | 7.9 | 273.8 | 6.6 | 565.1 | 358.5 | 231.9 | 579.6 | 453.7 | 665.1 | 424.6 | 417.7 | 691.4 | 485.1 | 289.1 | 286.9 | 303.8 | 308.9 | 302.7 | 306.7 | 286 | 304.5
1103 | 958 | -6.9 | 0 | 0 | 315.9 | 257 | 270.8 | 271.2 | 319.8 | 51.4 | 19.5 | 87.4 | 6.9 | 255.6 | 6.9 | 562.6 | 354.3 | 227.6 | 577.9 | 452 | 664.8 | 423 | 415.8 | 690 | 484.1 | 289.1 | 285.8 | 303 | 308.6 | 301.8 | 305.8 | 284.9 | 304.1
1104 | 959 | -6.9 | 0 | 0 | 315.1 | 256.4 | 269.6 | 270.5 | 319.3 | 51.2 | 19.5 | 87.2 | 5.9 | 268 | 7 | 559 | 351.3 | 223.3 | 575.9 | 449.7 | 664.6 | 422 | 413.4 | 688.3 | 482.7 | 289.1 | 284.6 | 302.2 | 308.1 | 301 | 304.8 | 284 | 303.7
1105 | 960 | -6.9 | 0 | 0 | 314.4 | 255.8 | 268.7 | 269.6 | 318.3 | 50.9 | 19.5 | 87 | 6.8 | 255.4 | 8.3 | 554.2 | 349.3 | 218.8 | 573.4 | 447.6 | 664.3 | 421.5 | 411.1 | 687.1 | 481.4 | 289.1 | 283.6 | 301.6 | 307.6 | 300.2 | 303.8 | 283.2 | 303.4
1106 | 961 | -6.9 | 0 | 0 | 314.2 | 255.4 | 267.9 | 268.8 | 317.2 | 50.9 | 19.5 | 86.7 | 6.7 | 255.3 | 7.7 | 549 | 347.4 | 214.4 | 570 | 444.9 | 663.9 | 420.6 | 409.4 | 686.2 | 480 | 289.1 | 282.7 | 301 | 307.2 | 299.3 | 302.8 | 282.5 | 303
1107 | 962 | -6.9 | 0 | 0 | 313.4 | 254.5 | 267.2 | 268.1 | 316 | 50.8 | 19.5 | 86.4 | 6.1 | 262.4 | 7 | 544.4 | 344.4 | 210.3 | 568.3 | 442.8 | 663.6 | 419.6 | 406.6 | 685.4 | 478.9 | 289 | 281.8 | 300.3 | 306.7 | 298.5 | 301.9 | 281.6 | 302.7
1108 | 963 | -6.9 | 0 | 0 | 313.2 | 253.7 | 266.9 | 267.4 | 315.3 | 50.6 | 19.5 | 86.1 | 5.9 | 257.9 | 7.8 | 540.4 | 342.6 | 207.2 | 566.9 | 440.5 | 663.5 | 418.7 | 404.5 | 684.1 | 478 | 289 | 281.1 | 299.5 | 306.3 | 297.7 | 301 | 280.6 | 302.3
1109 | 964 | -6.9 | 0 | 0 | 313 | 253.3 | 266.3 | 266.5 | 314.2 | 50.3 | 19.5 | 85.8 | 5.8 | 222.6 | 9.6 | 536.9 | 340.7 | 203.7 | 565.2 | 438.3 | 663.4 | 416.9 | 402.7 | 684.1 | 476.7 | 289 | 280.5 | 298.7 | 306 | 296.9 | 300 | 279.7 | 301.9
1110 | 965 | -6.9 | 0 | 0 | 312.4 | 252.9 | 265.5 | 265.5 | 313.1 | 50.2 | 19.5 | 85.5 | 7 | 249.9 | 9 | 533 | 337.4 | 200.5 | 563.7 | 436.3 | 663.2 | 415.5 | 401.3 | 682.7 | 475.5 | 289 | 279.9 | 298 | 305.8 | 296 | 299.2 | 278.8 | 301.5
1111 | 966 | -6.9 | 0 | 0 | 311.6 | 252.4 | 264.7 | 264.6 | 312.2 | 49.8 | 19.5 | 85.3 | 6.9 | 253.5 | 10.4 | 529.1 | 335.6 | 197.4 | 562 | 434.3 | 663 | 415 | 399.8 | 681.6 | 474.6 | 289 | 279.3 | 297.5 | 305.4 | 295.2 | 298.5 | 277.8 | 301.2
1112 | 967 | -6.9 | 0 | 0 | 311.4 | 251.8 | 263.5 | 264 | 311.7 | 49.5 | 19.5 | 85 | 7.3 | 260.7 | 13.6 | 525.8 | 332.3 | 194.5 | 560 | 432.4 | 662.7 | 414.4 | 398.2 | 681 | 473.6 | 289 | 278.6 | 296.9 | 305 | 294.4 | 297.8 | 276.9 | 300.8
1113 | 968 | -6.9 | 0 | 0 | 311.1 | 251.2 | 262.8 | 263.3 | 310.9 | 49.2 | 19.5 | 84.7 | 8.8 | 273.9 | 14.6 | 523 | 327.8 | 192 | 558.2 | 430.4 | 662.5 | 413.1 | 397.2 | 679.7 | 472.7 | 289 | 277.8 | 296.2 | 304.6 | 293.5 | 297 | 276.2 | 300.5
1114 | 969 | -6.9 | 0 | 0 | 310.9 | 250.7 | 262.2 | 262.5 | 310 | 48.8 | 19.5 | 84.3 | 8.7 | 268.3 | 15.6 | 520.7 | 325.3 | 189.5 | 556.5 | 428.5 | 662.4 | 413.6 | 395.5 | 678.7 | 471.6 | 288.9 | 277 | 295.5 | 304.1 | 292.8 | 296.3 | 275.5 | 300.2
1115 | 970 | -6.9 | 0 | 0 | 310.5 | 250.1 | 262 | 261.8 | 309.4 | 48.6 | 19.5 | 84 | 6.8 | 257 | 15.3 | 518.3 | 322.5 | 186.8 | 554.7 | 426.5 | 662.1 | 412.3 | 392.8 | 677.7 | 470.6 | 288.9 | 276.3 | 294.8 | 303.7 | 292 | 295.5 | 274.8 | 299.8
1116 | 971 | -6.9 | 0 | 0 | 311.2 | 249.5 | 261.6 | 261.3 | 308.8 | 48.2 | 19.5 | 83.6 | 5 | 252.3 | 17.2 | 516.2 | 318.9 | 184.7 | 553.2 | 424.8 | 661.8 | 412.5 | 391.7 | 676.2 | 469.7 | 288.9 | 275.5 | 294.3 | 303.3 | 291.1 | 294.7 | 274 | 299.4
1117 | 972 | -6.9 | 0 | 0 | 311.5 | 249 | 261.2 | 260.8 | 308.6 | 48 | 19.5 | 83.3 | 6.2 | 245.2 | 18 | 514.9 | 316.1 | 182.5 | 551.7 | 423.4 | 661.6 | 412.2 | 391.2 | 675.5 | 468.6 | 288.8 | 274.8 | 293.7 | 302.9 | 290.4 | 293.9 | 273.2 | 299.1
1118 | 973 | -6.9 | 0 | 0 | 311.7 | 248.5 | 260.9 | 260.3 | 308.8 | 47.7 | 19.5 | 83.1 | 9.3 | 256.4 | 16.4 | 513.8 | 313.9 | 180.8 | 550.2 | 422.1 | 661.5 | 411.4 | 389.7 | 673.7 | 467.5 | 288.8 | 274.2 | 293.1 | 302.4 | 289.7 | 293.2 | 272.5 | 298.7
1119 | 974 | -6.9 | 0 | 0 | 312.9 | 248 | 260.3 | 259.6 | 308.6 | 47.6 | 19.5 | 82.8 | 10.1 | 258.9 | 19.5 | 512.6 | 313.1 | 179.1 | 548.9 | 420.9 | 661.5 | 410.4 | 388.4 | 672.3 | 466.8 | 288.8 | 273.5 | 292.5 | 302 | 288.9 | 292.6 | 271.9 | 298.3
1120 | 975 | -6.9 | 0 | 0 | 312.8 | 247.4 | 259.8 | 259.3 | 308.3 | 47.6 | 19.5 | 82.5 | 8.4 | 253.9 | 20.2 | 511.3 | 310.9 | 177.2 | 547.2 | 419.6 | 661.5 | 410.5 | 387.1 | 671.5 | 465.8 | 288.8 | 272.7 | 292.2 | 301.6 | 288.2 | 292 | 271.1 | 298
1121 | 976 | -6.9 | 0 | 0 | 311.9 | 246.8 | 259.3 | 258.7 | 308.2 | 47.7 | 19.5 | 82.1 | 7.1 | 258 | 15.9 | 510.2 | 308.1 | 175.1 | 545.6 | 418.1 | 661.6 | 410.6 | 385.5 | 670.2 | 464.9 | 288.7 | 271.9 | 291.7 | 301.2 | 287.4 | 291.5 | 270.4 | 297.7
1122 | 977 | -6.9 | 0 | 0 | 311.8 | 246.3 | 258.9 | 258.3 | 308.1 | 47.7 | 19.5 | 81.8 | 7.5 | 244.8 | 18.7 | 509.2 | 304.6 | 173.1 | 543.8 | 416.7 | 661.6 | 409.4 | 384.1 | 668.4 | 463.9 | 288.7 | 271.1 | 291.2 | 300.8 | 286.7 | 290.8 | 269.8 | 297.4
1123 | 978 | -6.9 | 0 | 0 | 312.5 | 245.7 | 258.6 | 257.9 | 307.6 | 47.7 | 19.5 | 81.5 | 8.9 | 238.6 | 19.9 | 508.2 | 302.3 | 171.3 | 542 | 415.5 | 661.5 | 408.6 | 382.8 | 666.8 | 462.8 | 288.7 | 270.4 | 290.5 | 300.4 | 286 | 290.6 | 269.3 | 297
1124 | 979 | -6.9 | 0 | 0 | 313.7 | 245.2 | 257.3 | 257.6 | 307.2 | 47.8 | 19.5 | 81.1 | 8.5 | 243 | 19.8 | 506.8 | 300.6 | 169.9 | 540.3 | 414.2 | 661.4 | 408.1 | 381.6 | 665.4 | 461.8 | 288.6 | 269.8 | 290 | 300.1 | 285.3 | 290.3 | 268.7 | 296.7
1125 | 980 | -6.9 | 0 | 0 | 315.2 | 244.7 | 256.9 | 257.1 | 307 | 47.7 | 19.5 | 80.9 | 7.7 | 241.7 | 17.8 | 504.7 | 298.3 | 167.8 | 539 | 412.7 | 661.2 | 407.6 | 380.5 | 663.7 | 460.7 | 288.6 | 269.2 | 289.5 | 299.7 | 284.6 | 290 | 268.2 | 296.4
1126 | 981 | -6.9 | 0 | 0 | 316 | 244.2 | 256.7 | 256.6 | 307.1 | 47.5 | 19.5 | 80.6 | 7.9 | 250 | 14.8 | 502.8 | 296.9 | 165.7 | 537.4 | 411 | 660.9 | 407.5 | 379.8 | 662.4 | 459.8 | 288.5 | 268.4 | 289 | 299.3 | 283.9 | 289.6 | 267.4 | 296
1127 | 982 | -6.9 | 0 | 0 | 315.6 | 243.7 | 256.4 | 256.3 | 307 | 47.3 | 19.5 | 80.3 | 7.1 | 251.3 | 11.5 | 501.3 | 294.7 | 163.9 | 535.6 | 409.6 | 660.7 | 407.3 | 379.3 | 661.4 | 458.8 | 288.5 | 267.8 | 288.4 | 298.9 | 283.2 | 289 | 266.8 | 295.7
1128 | 983 | -6.9 | 0 | 0 | 314.9 | 243.2 | 256.1 | 255.7 | 307.1 | 47.3 | 19.5 | 80.1 | 7.3 | 262 | 11.6 | 500 | 293.5 | 162.4 | 533.7 | 408.2 | 660.5 | 406.5 | 379.5 | 659.7 | 457.9 | 288.5 | 267.4 | 287.9 | 298.6 | 282.5 | 288.5 | 266.2 | 295.3
1129 | 984 | -6.9 | 0 | 0 | 314.6 | 242.9 | 255.2 | 255 | 307 | 47.3 | 19.5 | 79.8 | 6.8 | 268.5 | 15.3 | 498.7 | 291.1 | 160.8 | 532.1 | 406.7 | 660.2 | 406 | 378.8 | 658.6 | 457.1 | 288.4 | 266.9 | 287.3 | 298.2 | 281.8 | 287.8 | 265.8 | 294.9
1130 | 985 | -6.9 | 0 | 0 | 314.6 | 242.6 | 254.5 | 254.6 | 306.8 | 47.3 | 19.5 | 79.5 | 5.9 | 256.9 | 14.3 | 496.9 | 288.8 | 159.3 | 530.6 | 405.3 | 660 | 405.3 | 377.2 | 657.5 | 456.3 | 288.4 | 266.3 | 286.8 | 297.8 | 281.2 | 287.5 | 265.3 | 294.6
1131 | 986 | -6.9 | 0 | 0 | 314.5 | 242.3 | 253.8 | 254.1 | 306.2 | 46.9 | 19.5 | 79.3 | 5.7 | 247.6 | 14.3 | 494.7 | 286.7 | 157.6 | 529.2 | 403.7 | 659.6 | 404.9 | 375.7 | 656 | 455.5 | 288.3 | 265.7 | 286.2 | 297.4 | 280.6 | 287.3 | 264.6 | 294.2
1132 | 987 | -6.9 | 0 | 0 | 313.9 | 241.9 | 252.7 | 253.8 | 305.5 | 46.7 | 19.5 | 79 | 6.8 | 244.9 | 16 | 492.6 | 285.2 | 156.1 | 527.6 | 402 | 659.2 | 404.2 | 373.9 | 654.8 | 454.7 | 288.3 | 265.1 | 285.6 | 297 | 279.9 | 286.8 | 264.1 | 293.9
1133 | 988 | -6.9 | 0 | 0 | 313 | 241.5 | 252.1 | 253.5 | 304.7 | 46.4 | 19.5 | 78.8 | 7.2 | 243.5 | 16.3 | 490.1 | 282.8 | 154.6 | 526.1 | 400.3 | 658.7 | 403.2 | 372.3 | 654.2 | 453.8 | 288.3 | 264.5 | 285.1 | 296.6 | 279.3 | 286.3 | 263.5 | 293.5
1134 | 989 | -6.9 | 0 | 0 | 312.2 | 241.2 | 251.9 | 253.1 | 303.9 | 46.2 | 19.5 | 78.6 | 5.9 | 242.6 | 16.5 | 487.7 | 281.1 | 152.9 | 524.4 | 398.6 | 658.2 | 402.7 | 370.9 | 652.7 | 452.9 | 288.2 | 263.9 | 284.6 | 296.2 | 278.6 | 285.8 | 263 | 293.2
1135 | 990 | -6.9 | 0 | 0 | 311.4 | 240.8 | 250.9 | 252.5 | 303.2 | 46.1 | 19.5 | 78.3 | 5.1 | 259.6 | 14.5 | 485.6 | 279.3 | 151.9 | 522.9 | 397 | 657.9 | 402.2 | 369.3 | 651.8 | 452 | 288.2 | 263.3 | 284.1 | 295.8 | 278 | 285.3 | 262.5 | 292.8
1136 | 991 | -6.9 | 0 | 0 | 310.6 | 240.5 | 250.2 | 251.8 | 303.1 | 46.1 | 19.5 | 78.1 | 5.1 | 255.1 | 14.1 | 484.2 | 277.4 | 150.9 | 521.4 | 395.8 | 657.5 | 402.1 | 368.1 | 651 | 450.9 | 288.1 | 262.7 | 283.6 | 295.4 | 277.4 | 285.1 | 262 | 292.5
1137 | 992 | -6.9 | 0 | 0 | 309.9 | 240.2 | 249.9 | 251.4 | 303 | 46.1 | 19.5 | 77.9 | 5.8 | 251.6 | 14.4 | 483 | 276.3 | 149.7 | 519.9 | 394.5 | 657.3 | 401.5 | 366.8 | 650.1 | 449.6 | 288.1 | 262.1 | 283.2 | 295 | 276.8 | 284.7 | 261.5 | 292.2
1138 | 993 | -6.9 | 0 | 0 | 308.8 | 240 | 249.3 | 250.9 | 302.5 | 46 | 19.5 | 77.7 | 5.3 | 267.5 | 15 | 481.9 | 273.8 | 148.3 | 518.3 | 393.6 | 657 | 401.4 | 365.9 | 648.7 | 448.9 | 288 | 261.6 | 283 | 294.6 | 276.2 | 284.2 | 261 | 291.8
1139 | 994 | -6.9 | 0 | 0 | 308.3 | 239.6 | 248.7 | 250.2 | 302.4 | 45.9 | 19.5 | 77.6 | 7.6 | 268.1 | 17.4 | 481 | 272 | 147 | 516.9 | 392.6 | 656.7 | 401 | 365.2 | 647.4 | 448.1 | 288 | 261 | 282.6 | 294.2 | 275.6 | 283.7 | 260.7 | 291.5
1140 | 995 | -6.9 | 0 | 0 | 308.8 | 239.3 | 248.6 | 249.7 | 302 | 45.9 | 19.5 | 77.4 | 8.2 | 262.3 | 20.8 | 480 | 269.4 | 145.5 | 515.4 | 391.6 | 656.4 | 400.4 | 364.3 | 646.8 | 447.2 | 287.9 | 260.6 | 282.1 | 293.8 | 275 | 283.3 | 260.4 | 291.2
1141 | 996 | -6.9 | 0 | 0 | 309.4 | 238.9 | 248.3 | 249.2 | 301.5 | 45.9 | 19.5 | 77.1 | 8.9 | 267.5 | 18.6 | 478.9 | 266.6 | 144.1 | 513.9 | 390.6 | 656.1 | 399.9 | 363.5 | 645.1 | 446.5 | 287.9 | 260 | 281.7 | 293.4 | 274.4 | 283.1 | 259.9 | 290.9
1142 | 997 | -6.9 | 0 | 0 | 309.3 | 238.7 | 247.6 | 248.9 | 301.6 | 45.9 | 19.5 | 76.9 | 10.5 | 259.6 | 18.4 | 477.9 | 264.7 | 142.7 | 512.5 | 389.4 | 656 | 399.7 | 362.8 | 643.9 | 445.6 | 287.8 | 259.5 | 281.5 | 293 | 273.8 | 282.7 | 259.5 | 290.6
1143 | 998 | -6.9 | 0 | 0 | 308.6 | 238.6 | 247.2 | 248.6 | 301.7 | 45.8 | 19.5 | 76.7 | 9.5 | 258 | 21.2 | 477 | 262.9 | 141.4 | 511.1 | 388.4 | 655.8 | 399.9 | 362.2 | 642.8 | 445 | 287.8 | 259 | 281 | 292.6 | 273.3 | 282.2 | 259 | 290.2
1144 | 999 | -6.9 | 0 | 0 | 308.1 | 238.4 | 247.2 | 248.6 | 301.3 | 45.7 | 19.5 | 76.5 | 9.1 | 253.4 | 20.2 | 476 | 261.9 | 140.1 | 509.6 | 387.2 | 655.7 | 399.2 | 362 | 642 | 444.5 | 287.7 | 258.5 | 280.5 | 292.2 | 272.7 | 281.8 | 258.4 | 289.9
1145 | 1000 | -6.9 | 0 | 0 | 308 | 238 | 247 | 248.4 | 301.1 | 45.5 | 19.5 | 76.3 | 7.5 | 246.5 | 19.3 | 474.9 | 258.7 | 138.8 | 508.1 | 386 | 655.4 | 398.6 | 361.5 | 640.7 | 443.7 | 287.7 | 258 | 280.1 | 291.8 | 272.1 | 281.4 | 257.9 | 289.6
1146 | 1001 | -6.9 | 0 | 0 | 307.9 | 237.8 | 246.7 | 248.1 | 300.5 | 45.4 | 19.5 | 76.1 | 7.3 | 243.9 | 17.4 | 473.7 | 257.6 | 137.5 | 506.6 | 385 | 655.2 | 398 | 360.4 | 639.5 | 443.1 | 287.6 | 257.5 | 279.6 | 291.4 | 271.6 | 281.2 | 257.4 | 289.2
1147 | 1002 | -6.9 | 0 | 0 | 307.6 | 237.6 | 246.1 | 247.7 | 299.8 | 45.3 | 19.5 | 75.9 | 6.8 | 261.1 | 16.3 | 472.3 | 256.7 | 136.4 | 505.3 | 383.9 | 654.8 | 397.5 | 359.6 | 638.1 | 442.4 | 287.6 | 257 | 279.1 | 291.1 | 271 | 280.8 | 256.9 | 288.9
1148 | 1003 | -6.9 | 0 | 0 | 307.3 | 237.6 | 245.4 | 247.5 | 299.5 | 45.3 | 19.5 | 75.6 | 6.4 | 255.6 | 17.4 | 471 | 255.9 | 135.5 | 504 | 382.7 | 654.2 | 396.5 | 358.5 | 637.2 | 441.6 | 287.5 | 256.5 | 278.7 | 290.7 | 270.5 | 280.5 | 256.5 | 288.6
1149 | 1004 | -6.9 | 0 | 0 | 306.7 | 237.6 | 244.8 | 247.4 | 298.6 | 45.2 | 19.5 | 75.3 | 6.2 | 251.9 | 16.6 | 469.7 | 254.4 | 134.4 | 502.6 | 381.7 | 653.7 | 396.1 | 357.3 | 636.1 | 441.1 | 287.4 | 256.2 | 278.3 | 290.3 | 270 | 280.2 | 256.1 | 288.3
1150 | 1005 | -6.9 | 0 | 0 | 306 | 237.2 | 244.5 | 247 | 297.9 | 45.2 | 19.5 | 75 | 6.1 | 263.9 | 14.2 | 468.4 | 252.7 | 133.3 | 501.1 | 380.5 | 653.4 | 395.5 | 357.1 | 635.3 | 440.4 | 287.4 | 255.9 | 277.9 | 289.9 | 269.4 | 279.7 | 255.7 | 287.9
1151 | 1006 | -6.9 | 0 | 0 | 305.8 | 236.9 | 244.3 | 246.6 | 297.6 | 45.1 | 19.5 | 74.7 | 7.3 | 265.7 | 14.5 | 467.1 | 251.4 | 132.3 | 499.7 | 379.4 | 653 | 394.3 | 356.1 | 634.6 | 439.5 | 287.3 | 255.6 | 277.5 | 289.5 | 268.9 | 279.2 | 255.2 | 287.5
1152 | 1007 | -6.9 | 0 | 0 | 305.6 | 236.6 | 244.2 | 246.2 | 297.2 | 45.1 | 19.5 | 74.4 | 6.7 | 270.3 | 14.2 | 465.8 | 249.2 | 131.4 | 497.9 | 378.3 | 652.6 | 393.2 | 355.1 | 633.2 | 438.7 | 287.3 | 255.1 | 277 | 289.1 | 268.3 | 278.9 | 254.8 | 287.2
1153 | 1008 | -6.9 | 0 | 0 | 305.4 | 236.2 | 244.3 | 245.9 | 296.7 | 44.9 | 19.5 | 74.2 | 5.9 | 268.2 | 15.4 | 464.5 | 247.3 | 130.5 | 496.8 | 377.2 | 652.2 | 393 | 354.4 | 632.6 | 437.9 | 287.2 | 254.6 | 276.5 | 288.8 | 267.8 | 278.4 | 254.3 | 286.9
1154 | 1009 | -6.9 | 0 | 0 | 305 | 235.9 | 243.9 | 245.4 | 296.4 | 44.8 | 19.5 | 73.9 | 4.8 | 254.2 | 14.7 | 463.2 | 246.5 | 129.4 | 495.4 | 376.1 | 651.7 | 392.6 | 353.6 | 631.7 | 437.3 | 287.2 | 254.2 | 276 | 288.4 | 267.3 | 277.9 | 253.8 | 286.5
1155 | 1010 | -6.8 | 0 | 0 | 304.8 | 235.7 | 243.8 | 244.8 | 295.9 | 44.6 | 19.5 | 73.7 | 5 | 242.4 | 13.5 | 461.8 | 246 | 128.5 | 494.2 | 375 | 651.1 | 391.4 | 352.4 | 630.5 | 436.4 | 287.1 | 253.7 | 275.6 | 288 | 266.8 | 277.4 | 253.4 | 286.1
1156 | 1011 | -6.8 | 0 | 0 | 304.4 | 235.7 | 243.1 | 244.4 | 295.2 | 44.5 | 19.5 | 73.5 | 5.2 | 278.8 | 11.2 | 460.4 | 244.8 | 127.7 | 492.9 | 373.9 | 650.4 | 390.3 | 351.9 | 630.3 | 435.5 | 287 | 253.3 | 275.1 | 287.7 | 266.2 | 276.9 | 252.9 | 285.8
1157 | 1012 | -6.8 | 0 | 0 | 304.2 | 235.5 | 242.7 | 244.1 | 294.4 | 44.3 | 19.5 | 73.3 | 4.7 | 251.8 | 10 | 459 | 244.2 | 126.6 | 491.7 | 372.8 | 649.9 | 389.6 | 351 | 629.8 | 434.7 | 287 | 252.8 | 274.7 | 287.3 | 265.8 | 276.7 | 252.3 | 285.4
1158 | 1013 | -6.7 | 0 | 0 | 304.2 | 235.3 | 242.5 | 243.7 | 294.1 | 44.1 | 19.5 | 73 | 4.7 | 279.8 | 8.7 | 457.7 | 242.3 | 125.5 | 490.4 | 371.6 | 649.4 | 388.9 | 350.7 | 629.3 | 434 | 286.9 | 252.3 | 274.3 | 286.9 | 265.2 | 276.4 | 251.8 | 285.1
1159 | 1014 | -6.9 | 0 | 0 | 303.9 | 234.9 | 242.1 | 243.2 | 293.4 | 43.9 | 19.5 | 72.8 | 4.3 | 256.9 | 8 | 456.3 | 241 | 124.6 | 488.5 | 370.4 | 649 | 387.6 | 349.8 | 628.7 | 433.3 | 286.9 | 251.8 | 273.9 | 286.5 | 264.7 | 276 | 251.4 | 284.8
1160 | 1015 | -6.9 | 0 | 0 | 303.2 | 234.6 | 241.8 | 242.7 | 292.9 | 43.7 | 19.5 | 72.7 | 3.8 | 262.7 | 8.3 | 454.9 | 239.7 | 123.7 | 487.2 | 369.2 | 648.4 | 387.1 | 348.5 | 628.1 | 432.4 | 286.8 | 251.3 | 273.5 | 286.1 | 264.2 | 275.5 | 251 | 284.4
1161 | 1016 | -6.9 | 0 | 0 | 303 | 234.2 | 240.9 | 242.3 | 292.3 | 43.5 | 19.5 | 72.5 | 4.4 | 265.4 | 9.7 | 453.5 | 239.6 | 122.9 | 486 | 368.1 | 647.9 | 386.4 | 347.2 | 627.2 | 431.6 | 286.7 | 250.9 | 273.2 | 285.8 | 263.8 | 274.9 | 250.7 | 284.1
1162 | 1017 | -6.9 | 0 | 0 | 303.5 | 234 | 240.5 | 242 | 291.5 | 43.5 | 19.5 | 72.4 | 4.2 | 275.9 | 10.7 | 452.1 | 239.1 | 122.2 | 484.9 | 367.1 | 647.5 | 386 | 346.5 | 626.7 | 430.7 | 286.7 | 250.6 | 272.7 | 285.4 | 263.3 | 274.4 | 250.3 | 283.8
1163 | 1018 | -6.9 | 0 | 0 | 303.4 | 233.7 | 240.5 | 241.3 | 290.7 | 43.4 | 19.5 | 72.3 | 4 | 260 | 11.9 | 450.7 | 237.4 | 121.4 | 483.6 | 366.1 | 647 | 385.8 | 345.3 | 626.1 | 429.6 | 286.6 | 250.2 | 272.3 | 285.1 | 262.8 | 274 | 249.9 | 283.5
1164 | 1019 | -6.9 | 0 | 0 | 303.3 | 233.3 | 240.2 | 241 | 290 | 43.4 | 19.5 | 72.2 | 4.3 | 267.9 | 11.1 | 449.4 | 236.7 | 120.4 | 482.4 | 364.9 | 646.4 | 384.7 | 344.2 | 625 | 428.8 | 286.5 | 249.8 | 272 | 284.7 | 262.4 | 273.6 | 249.5 | 283.2
1165 | 1020 | -6.9 | 0 | 0 | 302.9 | 233.2 | 239.9 | 240.8 | 289.5 | 43.3 | 19.5 | 72.1 | 4.2 | 282.9 | 9.3 | 448.1 | 236.1 | 119.4 | 481.2 | 363.8 | 646 | 384.4 | 343.2 | 624.1 | 427.9 | 286.5 | 249.4 | 271.6 | 284.3 | 261.9 | 273.2 | 249.1 | 282.9
1166 | 1021 | -6.9 | 0 | 0 | 302.7 | 232.9 | 239.7 | 240.5 | 289.2 | 43.3 | 19.5 | 72 | 4.4 | 267.3 | 8.3 | 446.9 | 234.3 | 118.4 | 480 | 362.7 | 645.4 | 383.7 | 342.6 | 623.7 | 427.2 | 286.4 | 248.9 | 271.2 | 283.9 | 261.5 | 272.7 | 248.8 | 282.5
1167 | 1022 | -6.9 | 0 | 0 | 302 | 232.7 | 239.6 | 240.2 | 289 | 43.1 | 19.5 | 71.9 | 5 | 288.9 | 8.5 | 445.7 | 233.3 | 117.4 | 478.7 | 361.6 | 644.9 | 383.1 | 342 | 623 | 426.5 | 286.3 | 248.5 | 270.6 | 283.6 | 261 | 272.2 | 248.4 | 282.2
1168 | 1023 | -6.9 | 0 | 0 | 301.4 | 232.6 | 239.3 | 239.8 | 288.6 | 42.9 | 19.5 | 71.7 | 5 | 272.9 | 9.4 | 444.5 | 232.5 | 116.3 | 477.3 | 360.5 | 644.4 | 382.3 | 341.6 | 622.4 | 425.7 | 286.3 | 248.1 | 270.2 | 283.3 | 260.5 | 271.6 | 248 | 281.9
1169 | 1024 | -6.9 | 0 | 0 | 300.8 | 232.5 | 238.8 | 239.2 | 288.7 | 42.8 | 19.5 | 71.6 | 4.9 | 272.2 | 10.1 | 443.1 | 231.9 | 115.3 | 475.9 | 359.4 | 643.9 | 382 | 340.8 | 621.4 | 425 | 286.2 | 247.7 | 269.7 | 282.9 | 260 | 271.1 | 247.6 | 281.6
1170 | 1025 | -6.9 | 0 | 0 | 300.9 | 232.3 | 238.6 | 238.7 | 288.7 | 42.8 | 19.5 | 71.4 | 4.9 | 269.3 | 9.9 | 441.8 | 232 | 114.4 | 474.5 | 358.4 | 643.4 | 381.1 | 339.9 | 620.1 | 424.1 | 286.1 | 247.4 | 269.3 | 282.6 | 259.5 | 270.7 | 247.2 | 281.2
1171 | 1026 | -6.9 | 0 | 0 | 300.7 | 232.1 | 238.3 | 238.5 | 288.1 | 42.7 | 19.5 | 71.2 | 4.8 | 253 | 9.9 | 440.4 | 231.1 | 113.6 | 473.2 | 357.3 | 642.8 | 380.7 | 338.9 | 619.2 | 423.2 | 286.1 | 247.1 | 268.9 | 282.2 | 259.1 | 270.4 | 246.8 | 281
1172 | 1027 | -6.9 | 0 | 0 | 300.4 | 231.9 | 237.9 | 238 | 287.8 | 42.6 | 19.5 | 71.1 | 5.3 | 256.9 | 10.1 | 439 | 230.2 | 112.9 | 472 | 356 | 642 | 380.3 | 338.3 | 618.6 | 422.5 | 286 | 246.7 | 268.6 | 281.9 | 258.6 | 270 | 246.4 | 280.6
1173 | 1028 | -6.9 | 0 | 0 | 301 | 231.7 | 237.3 | 237.4 | 287.5 | 42.4 | 19.5 | 70.9 | 5 | 249.4 | 10.6 | 437.6 | 229.6 | 112.2 | 470.7 | 354.7 | 641.3 | 378.9 | 337.6 | 618.2 | 421.6 | 285.9 | 246.3 | 268.2 | 281.5 | 258.2 | 269.6 | 246 | 280.3
1174 | 1029 | -6.8 | 0 | 0 | 301.1 | 231.5 | 236.9 | 236.9 | 286.9 | 42.4 | 19.5 | 70.8 | 4.3 | 246.8 | 11 | 436 | 228.5 | 111.6 | 469.6 | 353.8 | 640.7 | 378.2 | 337.1 | 617.6 | 420.7 | 285.9 | 245.9 | 267.8 | 281.1 | 257.7 | 269.2 | 245.6 | 280
1175 | 1030 | -6.9 | 0 | 0 | 300.5 | 231.2 | 236.4 | 236.8 | 286.7 | 42.4 | 19.5 | 70.7 | 5.4 | 262.3 | 11.5 | 434.6 | 227.7 | 110.9 | 468.4 | 352.7 | 640 | 378 | 335.9 | 616.4 | 420 | 285.8 | 245.5 | 267.4 | 280.8 | 257.3 | 268.9 | 245.1 | 279.7
1176 | 1031 | -6.9 | 0 | 0 | 300.4 | 230.9 | 236 | 236.7 | 286.2 | 42.2 | 19.5 | 70.5 | 5.2 | 246 | 10 | 433.3 | 226.3 | 110.1 | 466.6 | 351.6 | 639.3 | 377.8 | 335.2 | 615.5 | 419.1 | 285.7 | 245.1 | 267.1 | 280.5 | 256.9 | 268.5 | 244.8 | 279.4
1177 | 1032 | -6.8 | 0 | 0 | 300.6 | 230.7 | 235.5 | 236.4 | 285.9 | 42.2 | 19.5 | 70.4 | 4.8 | 237.1 | 8.8 | 432 | 224.6 | 109.2 | 465.2 | 350.5 | 638.7 | 377.4 | 334.6 | 614.4 | 418.3 | 285.6 | 244.8 | 266.6 | 280.1 | 256.4 | 268.1 | 244.5 | 279.1
1178 | 1033 | -6.8 | 0 | 0 | 300.1 | 230.5 | 234.8 | 236.2 | 285.4 | 42.2 | 19.5 | 70.3 | 4.6 | 240.3 | 10.2 | 430.7 | 223.8 | 108.3 | 463.9 | 349.5 | 638.1 | 377.3 | 333.9 | 613.9 | 417.5 | 285.6 | 244.5 | 266.2 | 279.7 | 256 | 267.8 | 244.2 | 278.8
1179 | 1034 | -6.8 | 0 | 0 | 299 | 230.3 | 233.8 | 236.1 | 285.1 | 42.2 | 19.6 | 70.2 | 4.9 | 249.9 | 12.2 | 429.5 | 222.9 | 107.7 | 462.9 | 348.4 | 637.4 | 377.8 | 333.1 | 613.3 | 416.7 | 285.5 | 244.1 | 265.8 | 279.4 | 255.6 | 267.5 | 243.8 | 278.4
1180 | 1035 | -6.8 | 0 | 0 | 298.4 | 230.2 | 233.4 | 235.9 | 284.9 | 42 | 19.6 | 70 | 6 | 244.3 | 12.1 | 428.2 | 221.5 | 107.1 | 461.7 | 347.4 | 636.7 | 377.6 | 331.9 | 613 | 416 | 285.4 | 243.7 | 265.4 | 279 | 255.2 | 267.2 | 243.6 | 278.1
1181 | 1036 | -6.8 | 0 | 0 | 298.5 | 230.1 | 233.1 | 235.7 | 284.4 | 41.7 | 19.6 | 69.9 | 7.2 | 255.1 | 10.6 | 426.8 | 220.7 | 106.6 | 460.4 | 346.3 | 636 | 377.3 | 330.5 | 612.6 | 415.1 | 285.3 | 243.3 | 265 | 278.7 | 254.7 | 266.8 | 243.3 | 277.8
1182 | 1037 | -6.8 | 0 | 0 | 298.3 | 229.9 | 232.3 | 235.5 | 283.6 | 41.6 | 19.5 | 69.8 | 6.2 | 261.7 | 9.3 | 425.4 | 220 | 106 | 459.1 | 345.2 | 635.4 | 376.5 | 329.9 | 612.4 | 414.2 | 285.3 | 242.9 | 264.6 | 278.3 | 254.3 | 266.4 | 242.9 | 277.5
1183 | 1038 | -6.9 | 0 | 0 | 297.7 | 229.7 | 232.1 | 235.2 | 283 | 41.5 | 19.5 | 69.7 | 7 | 276.2 | 8.3 | 424.1 | 219.1 | 105.5 | 456.5 | 344.2 | 634.6 | 375.5 | 329.5 | 611.9 | 413.5 | 285.2 | 242.4 | 264.2 | 277.9 | 253.9 | 266 | 242.7 | 277.2
1184 | 1039 | -6.8 | 0 | 0 | 297.1 | 229.4 | 232.2 | 234.9 | 282.8 | 41.4 | 19.6 | 69.6 | 5.8 | 280.7 | 7.9 | 422.8 | 218.2 | 104.8 | 456 | 343.2 | 633.7 | 374.4 | 329.2 | 611.6 | 412.7 | 285.1 | 242.1 | 263.8 | 277.6 | 253.5 | 265.7 | 242.4 | 276.9
1185 | 1040 | -6.8 | 0 | 0 | 297.1 | 229.1 | 232.1 | 234.7 | 282.3 | 41.2 | 19.6 | 69.4 | 5.6 | 262.8 | 8.7 | 421.5 | 218.1 | 104.2 | 455 | 342.1 | 633 | 374.4 | 327.8 | 611.3 | 412.1 | 285.1 | 241.8 | 263.4 | 277.3 | 253.1 | 265.3 | 242 | 276.5
1186 | 1041 | -6.8 | 0 | 0 | 297.2 | 228.9 | 232 | 234.6 | 281.6 | 41 | 19.6 | 69.3 | 5.6 | 262.9 | 9.7 | 420.2 | 217.6 | 103.6 | 453.9 | 341.1 | 632.1 | 372.9 | 327 | 610.7 | 411.1 | 285 | 241.4 | 263.1 | 277 | 252.6 | 265 | 241.6 | 276.1
1187 | 1042 | -6.8 | 0 | 0 | 297.2 | 228.8 | 232 | 234.3 | 281.5 | 40.9 | 19.6 | 69.1 | 5.1 | 270 | 9.2 | 418.9 | 216.6 | 103 | 452.8 | 340.2 | 631.4 | 372.3 | 326.4 | 610.4 | 410.2 | 284.9 | 241.2 | 262.8 | 276.7 | 252.2 | 264.6 | 241.2 | 275.8
1188 | 1043 | -6.9 | 0 | 0 | 296.7 | 228.6 | 231.7 | 234.2 | 280.9 | 40.8 | 19.6 | 69 | 4.2 | 273.7 | 8.7 | 417.5 | 216.3 | 102.5 | 451.8 | 339.2 | 630.7 | 371.7 | 325 | 609.5 | 409.2 | 284.8 | 240.8 | 262.5 | 276.3 | 251.7 | 264.2 | 240.8 | 275.4
1189 | 1044 | -6.8 | 0 | 0 | 296.1 | 228.3 | 231 | 234.1 | 280.4 | 40.6 | 19.6 | 68.9 | 4.9 | 261.5 | 8.2 | 416.2 | 215 | 102.1 | 450.7 | 338.2 | 630 | 371.7 | 323.6 | 609.2 | 408.3 | 284.7 | 240.5 | 262.2 | 276 | 251.3 | 263.9 | 240.5 | 275.1
1190 | 1045 | -6.8 | 0 | 0 | 295.7 | 228.1 | 230.6 | 233.9 | 280.3 | 40.5 | 19.5 | 68.8 | 6 | 258 | 8.3 | 414.9 | 214.1 | 101.4 | 449.4 | 337.2 | 629.4 | 371.7 | 322.6 | 608.6 | 407.6 | 284.7 | 240.2 | 261.9 | 275.7 | 250.9 | 263.6 | 240.1 | 274.9
1191 | 1046 | -6.8 | 0 | 0 | 295.2 | 227.9 | 230.6 | 233.5 | 279.9 | 40.4 | 19.5 | 68.6 | 6.6 | 266.8 | 8.9 | 413.7 | 213.2 | 100.8 | 448.2 | 336.2 | 628.8 | 371.6 | 321.7 | 608.1 | 406.8 | 284.6 | 239.9 | 261.6 | 275.4 | 250.5 | 263.3 | 239.7 | 274.5
1192 | 1047 | -6.8 | 0 | 0 | 295.4 | 227.8 | 230 | 233 | 279.6 | 40.4 | 19.6 | 68.5 | 7.8 | 288 | 6.8 | 412.5 | 211.8 | 100.2 | 446.8 | 335.1 | 628.2 | 371.5 | 321.2 | 607.4 | 406.2 | 284.5 | 239.6 | 261.2 | 275 | 250 | 262.9 | 239.3 | 274.2
1193 | 1048 | -6.8 | 0 | 0 | 295.8 | 227.9 | 229.6 | 232.5 | 279.3 | 40.4 | 19.6 | 68.4 | 6.3 | 270.8 | 4.9 | 411.3 | 210.6 | 99.7 | 445.7 | 334.2 | 627.5 | 370.7 | 320.3 | 607.1 | 405.4 | 284.4 | 239.2 | 260.9 | 274.7 | 249.6 | 262.6 | 238.9 | 273.9
1194 | 1049 | -6.8 | 0 | 0 | 295.3 | 227.9 | 228.8 | 232.1 | 278.9 | 40.4 | 19.6 | 68.2 | 6 | 234.8 | 6.6 | 410.2 | 209.7 | 99.2 | 444.6 | 333.2 | 627.1 | 370.4 | 319.4 | 606.5 | 404.6 | 284.4 | 238.9 | 260.6 | 274.3 | 249.2 | 262.3 | 238.6 | 273.6
1195 | 1050 | -6.8 | 0 | 0 | 295 | 227.7 | 228.3 | 231.9 | 278.3 | 40.3 | 19.6 | 68.1 | 6.9 | 245.2 | 8.7 | 409.1 | 209.4 | 98.3 | 443.5 | 332.3 | 626.7 | 370.5 | 318.3 | 606 | 403.8 | 284.3 | 238.5 | 260.2 | 274 | 248.9 | 261.9 | 238.2 | 273.3
1196 | 1051 | -6.8 | 0 | 0 | 295.1 | 227.4 | 228.4 | 231.6 | 278.8 | 40.3 | 19.6 | 67.9 | 6.8 | 243.3 | 9.1 | 408.1 | 209 | 97.5 | 442.4 | 331.3 | 626.2 | 370.2 | 317.8 | 605.2 | 402.8 | 284.2 | 238.2 | 259.9 | 273.7 | 248.5 | 261.6 | 237.9 | 273
1197 | 1052 | -6.8 | 0 | 0 | 295.1 | 227.1 | 228.5 | 231.5 | 279.4 | 40.4 | 19.6 | 67.8 | 6.5 | 247.1 | 8.1 | 407.1 | 207.5 | 96.8 | 441.2 | 330.3 | 625.8 | 370.1 | 316.6 | 604.4 | 402 | 284.1 | 237.9 | 259.5 | 273.4 | 248.1 | 261.3 | 237.5 | 272.7
1198 | 1053 | -6.9 | 0 | 0 | 295.4 | 226.8 | 228.4 | 231.2 | 278.9 | 40.4 | 19.6 | 67.7 | 6 | 264.4 | 6.5 | 406 | 206.3 | 96.3 | 440.1 | 329.4 | 625.3 | 369.5 | 315.5 | 604.1 | 401.3 | 284 | 237.6 | 259.2 | 273.1 | 247.7 | 260.9 | 237.2 | 272.4
1199 | 1054 | -6.9 | 0 | 0 | 296.1 | 226.5 | 228.1 | 230.9 | 278.3 | 40.3 | 19.6 | 67.5 | 5.7 | 241.2 | 7.6 | 404.9 | 205.7 | 96 | 439.1 | 328.6 | 624.8 | 369.1 | 314.5 | 603.3 | 400.5 | 284 | 237.2 | 258.8 | 272.7 | 247.3 | 260.5 | 237 | 272.2
1200 | 1055 | -6.8 | 0 | 0 | 295.5 | 226.3 | 227.8 | 230.8 | 278 | 40.2 | 19.6 | 67.4 | 7 | 246.6 | 14.6 | 403.8 | 204.6 | 95.7 | 438 | 327.6 | 624.3 | 368.7 | 313.4 | 602.8 | 399.7 | 283.9 | 236.8 | 258.4 | 272.4 | 247 | 260.1 | 236.7 | 271.8
1201 | 1056 | -6.8 | 0 | 0 | 294.6 | 226 | 227.6 | 230.7 | 277.6 | 40.1 | 19.6 | 67.3 | 7.5 | 242.7 | 13.4 | 402.5 | 203.3 | 95.3 | 436.9 | 326.8 | 623.9 | 368.9 | 312.7 | 602.5 | 399 | 283.8 | 236.5 | 258 | 272 | 246.6 | 259.7 | 236.4 | 271.5
1202 | 1057 | -6.9 | 0 | 0 | 294 | 225.9 | 227.6 | 230.3 | 277.1 | 40 | 19.6 | 67.1 | 8 | 239.7 | 12.5 | 401.2 | 201.9 | 95.1 | 436 | 326.1 | 623.6 | 367.8 | 311.9 | 602.1 | 398.1 | 283.7 | 236.2 | 257.7 | 271.7 | 246.3 | 259.4 | 236.2 | 271.2
1203 | 1058 | -6.8 | 0 | 0 | 293.9 | 225.6 | 227.5 | 229.9 | 276.5 | 39.9 | 19.6 | 67 | 10.6 | 236.6 | 11.8 | 400 | 200.6 | 94.9 | 434.9 | 325.2 | 623.2 | 367 | 310.6 | 601.7 | 397.3 | 283.6 | 235.9 | 257.4 | 271.3 | 245.9 | 259 | 235.9 | 270.9
1204 | 1059 | -6.9 | 0 | 0 | 294 | 225.5 | 226.9 | 229.6 | 276.3 | 39.8 | 19.6 | 66.8 | 10.9 | 244 | 10.8 | 398.8 | 199.9 | 94.7 | 433.8 | 324.4 | 622.8 | 366.4 | 309.4 | 601.4 | 396.6 | 283.6 | 235.6 | 257.1 | 271 | 245.5 | 258.7 | 235.5 | 270.6
1205 | 1060 | -6.9 | 0 | 0 | 293.4 | 225.5 | 226.6 | 229.3 | 276.2 | 39.7 | 19.6 | 66.7 | 12.9 | 239.6 | 10 | 397.6 | 199.2 | 94.3 | 432.6 | 323.4 | 622.5 | 366 | 308.7 | 601.1 | 396 | 283.5 | 235.3 | 256.8 | 270.7 | 245.1 | 258.3 | 235.1 | 270.2
1206 | 1061 | -6.9 | 0 | 0 | 292.8 | 225.2 | 226.2 | 229 | 275.9 | 39.7 | 19.6 | 66.6 | 11.7 | 232.9 | 14.7 | 396.4 | 198 | 93.9 | 431.4 | 322.6 | 622.1 | 365.6 | 308.2 | 600.6 | 395.4 | 283.4 | 235.2 | 256.5 | 270.4 | 244.7 | 258 | 234.8 | 270
1207 | 1062 | -6.9 | 0 | 0 | 292 | 225 | 226.1 | 228.7 | 275.3 | 39.6 | 19.6 | 66.4 | 10.2 | 247.4 | 23.8 | 395.2 | 197.6 | 93.6 | 430.4 | 321.7 | 621.7 | 365.1 | 307.1 | 599.8 | 394.7 | 283.3 | 234.8 | 256.2 | 270.1 | 244.3 | 257.7 | 234.5 | 269.6
1208 | 1063 | -6.9 | 0 | 0 | 291.4 | 224.8 | 226.3 | 228.3 | 274.8 | 39.6 | 19.6 | 66.2 | 9.4 | 247.1 | 25.4 | 394.1 | 197 | 93.3 | 429.3 | 320.8 | 621.4 | 365 | 306.3 | 599 | 393.8 | 283.2 | 234.5 | 255.9 | 269.8 | 244 | 257.3 | 234.3 | 269.3
1209 | 1064 | -6.9 | 0 | 0 | 290.8 | 224.6 | 226.5 | 227.7 | 274.3 | 39.4 | 19.6 | 66 | 9.1 | 244.4 | 28.3 | 393 | 196.6 | 92.9 | 428.3 | 320 | 621 | 364.3 | 305.5 | 598.7 | 392.9 | 283.1 | 234.3 | 255.6 | 269.5 | 243.6 | 257 | 233.9 | 269
1210 | 1065 | -6.8 | 0 | 0 | 290.2 | 224.4 | 226.1 | 227.3 | 273.3 | 39.3 | 19.6 | 65.8 | 10.7 | 247.8 | 27.8 | 391.9 | 196.1 | 92.5 | 427 | 319.1 | 620.5 | 364 | 304.4 | 598.4 | 392.1 | 283.1 | 234 | 255.3 | 269.2 | 243.2 | 256.7 | 233.6 | 268.7
1211 | 1066 | -6.8 | 0 | 0 | 289.1 | 224.2 | 226.1 | 227.1 | 272.5 | 39.1 | 19.6 | 65.6 | 11.8 | 248.7 | 27.1 | 390.9 | 195.4 | 92 | 426 | 318.1 | 620 | 363.5 | 303.3 | 598.1 | 391.1 | 283 | 233.8 | 255.1 | 268.9 | 242.9 | 256.3 | 233.3 | 268.4
1212 | 1067 | -6.8 | 0 | 0 | 288.4 | 224.2 | 225.7 | 226.8 | 272.1 | 39 | 19.6 | 65.3 | 9.5 | 251.9 | 26 | 389.8 | 194.9 | 91.6 | 425 | 317.1 | 619.5 | 362.9 | 302.1 | 597.8 | 390.6 | 282.9 | 233.5 | 254.8 | 268.5 | 242.5 | 256 | 233 | 268.1
1213 | 1068 | -6.8 | 0 | 0 | 288.2 | 223.9 | 225 | 226.5 | 271.9 | 38.9 | 19.6 | 65 | 6.8 | 246.9 | 23.9 | 388.8 | 194.3 | 91.3 | 424.1 | 316.2 | 619 | 361.9 | 301.1 | 597.1 | 389.8 | 282.8 | 233.3 | 254.5 | 268.2 | 242.1 | 255.7 | 232.7 | 267.8
1214 | 1069 | -6.9 | 0 | 0 | 288 | 223.7 | 224.8 | 226.2 | 271.7 | 38.8 | 19.6 | 64.8 | 3.8 | 247.4 | 21.7 | 387.9 | 193.3 | 90.9 | 423 | 315.1 | 618.5 | 361.3 | 300.8 | 597.6 | 388.9 | 282.7 | 233 | 254.1 | 267.9 | 241.8 | 255.4 | 232.4 | 267.5
1215 | 1070 | -6.8 | 0 | 0 | 287.5 | 223.5 | 224.6 | 225.7 | 271.6 | 38.7 | 19.6 | 64.7 | 3.3 | 244.4 | 20.5 | 387 | 192.5 | 90.4 | 421.6 | 314.1 | 617.9 | 360.1 | 300 | 597.7 | 388.4 | 282.6 | 232.6 | 253.8 | 267.6 | 241.4 | 255 | 232.1 | 267.2
1216 | 1071 | -6.8 | 0 | 0 | 287.2 | 223.3 | 224.3 | 225.4 | 271.3 | 38.5 | 19.6 | 64.6 | 5 | 262.3 | 19.1 | 386 | 192.2 | 89.9 | 420.1 | 313.1 | 617.3 | 358.7 | 299.2 | 597.8 | 387.7 | 282.5 | 232.3 | 253.4 | 267.2 | 241.1 | 254.7 | 231.8 | 266.9
1217 | 1072 | -6.8 | 0 | 0 | 287.2 | 223 | 223.9 | 225.2 | 270.7 | 38.4 | 19.6 | 64.4 | 6.3 | 273 | 19.4 | 385 | 191.5 | 89.3 | 419.1 | 312.2 | 616.5 | 357.5 | 297.8 | 598.2 | 386.9 | 282.4 | 231.9 | 253 | 266.9 | 240.8 | 254.3 | 231.5 | 266.6
1218 | 1073 | -6.8 | 0 | 0 | 286.8 | 222.7 | 223.2 | 224.8 | 270 | 38.5 | 19.6 | 64.2 | 7.3 | 276.2 | 18.4 | 383.9 | 191.5 | 88.7 | 418.3 | 311.4 | 615.8 | 355.9 | 297.2 | 598.3 | 386.3 | 282.4 | 231.6 | 252.6 | 266.5 | 240.4 | 254 | 231.2 | 266.3
1219 | 1074 | -6.6 | 0 | 0 | 286.4 | 222.5 | 222.9 | 224.4 | 269.3 | 38.5 | 19.6 | 64 | 6.3 | 278.6 | 17.1 | 382.8 | 190.6 | 88.4 | 417.4 | 310.6 | 615.2 | 354.4 | 296.4 | 597.4 | 385.7 | 282.3 | 231.3 | 252.3 | 266.2 | 240.1 | 253.6 | 230.9 | 266.1
1220 | 1075 | -6.7 | 0 | 0 | 285.9 | 222.3 | 222.6 | 224.2 | 268.5 | 38.4 | 19.6 | 63.8 | 6 | 286.2 | 15 | 381.8 | 190 | 88 | 416.3 | 309.8 | 614.5 | 353.6 | 295.4 | 597.7 | 385.1 | 282.2 | 231 | 251.9 | 265.9 | 239.7 | 253.3 | 230.7 | 265.8
1221 | 1076 | -6.8 | 0 | 0 | 285.8 | 222 | 222.2 | 223.8 | 268 | 38.4 | 19.6 | 63.6 | 5.5 | 293.6 | 16.6 | 380.7 | 189.4 | 87.7 | 415.2 | 309 | 613.9 | 352.5 | 294.8 | 597.6 | 384.6 | 282.1 | 230.7 | 251.6 | 265.6 | 239.4 | 253 | 230.4 | 265.5
1222 | 1077 | -6.7 | 0 | 0 | 285.2 | 221.9 | 222.1 | 223.4 | 267.6 | 38.4 | 19.6 | 63.5 | 5.1 | 289.5 | 18.4 | 379.7 | 188.5 | 87.4 | 413.8 | 307.9 | 613.4 | 351.5 | 293.4 | 597 | 384 | 282 | 230.4 | 251.2 | 265.3 | 239 | 252.7 | 230 | 265.1
1223 | 1078 | -6.7 | 0 | 0 | 284.5 | 221.7 | 222 | 223 | 267.1 | 38.3 | 19.6 | 63.4 | 4.2 | 289.2 | 14.8 | 378.8 | 187.3 | 87.1 | 412.7 | 307 | 612.8 | 350.3 | 292.4 | 596.6 | 383.4 | 281.9 | 230 | 250.9 | 265 | 238.7 | 252.3 | 229.8 | 264.9
1224 | 1079 | -6.8 | 0 | 0 | 284.2 | 221.4 | 221.9 | 222.7 | 266.7 | 38.3 | 19.6 | 63.2 | 3.7 | 290.5 | 10 | 378 | 186.5 | 86.7 | 411.8 | 306.1 | 612.2 | 348.7 | 291.2 | 596.4 | 382.6 | 281.8 | 229.7 | 250.6 | 264.6 | 238.3 | 252 | 229.5 | 264.6
1225 | 1080 | -6.5 | 0 | 0 | 283.8 | 221.1 | 221.8 | 222.3 | 266.2 | 38.3 | 19.6 | 63.1 | 4 | 301 | 7.8 | 377.1 | 185.3 | 86.3 | 410.6 | 305.2 | 611.5 | 347.1 | 290 | 595.9 | 381.9 | 281.7 | 229.3 | 250.3 | 264.3 | 238 | 251.6 | 229.2 | 264.3
1226 | 1081 | -6.1 | 0 | 0 | 283.5 | 220.9 | 221.8 | 222 | 265.8 | 38.3 | 19.6 | 63 | 4.1 | 242.7 | 8.7 | 376.2 | 184.4 | 86.1 | 409.5 | 304.2 | 610.8 | 346.1 | 289 | 595.3 | 381.2 | 281.6 | 229 | 249.9 | 263.9 | 237.7 | 251.3 | 229 | 264
1227 | 1082 | -5.7 | 0 | 0 | 282.9 | 220.7 | 221.6 | 221.8 | 266.1 | 38.3 | 19.6 | 62.9 | 3.3 | 256.6 | 9.3 | 375.1 | 184 | 85.9 | 408.4 | 303.3 | 610.3 | 345.2 | 288 | 595.4 | 380.6 | 281.5 | 228.7 | 249.5 | 263.6 | 237.3 | 251 | 228.7 | 263.7
1228 | 1083 | -6.5 | 0 | 0 | 282.1 | 220.4 | 221.4 | 221.3 | 265.9 | 38.3 | 19.6 | 62.9 | 3.7 | 272.9 | 12 | 374.1 | 182.8 | 85.5 | 407.2 | 302.6 | 609.7 | 344.2 | 287.1 | 594.8 | 379.7 | 281.4 | 228.4 | 249.2 | 263.3 | 237 | 250.6 | 228.4 | 263.4
1229 | 1084 | -6.6 | 0 | 0 | 281.1 | 220.2 | 221.3 | 220.7 | 265.5 | 38.2 | 19.6 | 62.8 | 5 | 277.7 | 14.7 | 373.1 | 181.8 | 85.2 | 406.3 | 301.8 | 609.1 | 342.9 | 287 | 594.5 | 379.1 | 281.4 | 228.1 | 248.9 | 263 | 236.6 | 250.3 | 228 | 263.1
1230 | 1085 | -6.6 | 0 | 0 | 280.5 | 220 | 221.3 | 220.2 | 265.4 | 38.1 | 19.6 | 62.7 | 5.8 | 270 | 14.9 | 372 | 181 | 84.9 | 405.1 | 300.9 | 608.5 | 342.3 | 286.9 | 593.7 | 378.3 | 281.3 | 227.8 | 248.6 | 262.7 | 236.2 | 249.9 | 227.6 | 262.7
1231 | 1086 | -6.3 | 0 | 0 | 280.1 | 219.8 | 221.3 | 219.7 | 265.2 | 38 | 19.6 | 62.7 | 5.3 | 288.1 | 14.5 | 371 | 180.5 | 84.5 | 404.1 | 300.2 | 607.7 | 340.9 | 286 | 593 | 377.5 | 281.2 | 227.7 | 248.4 | 262.4 | 235.9 | 249.6 | 227.3 | 262.5
1232 | 1087 | -6.4 | 0 | 0 | 279.7 | 219.7 | 221 | 219.4 | 265.6 | 37.9 | 19.6 | 62.6 | 5.1 | 285.5 | 13.9 | 370.3 | 180.3 | 84 | 403 | 299.4 | 607.2 | 339.3 | 285.3 | 592.8 | 376.9 | 281.1 | 227.5 | 248.1 | 262.1 | 235.6 | 249.3 | 226.9 | 262.2
1233 | 1088 | -6.5 | 0 | 0 | 278.8 | 219.6 | 220.4 | 219 | 265.3 | 37.7 | 19.6 | 62.6 | 5 | 276.6 | 14.8 | 369.5 | 180.3 | 83.7 | 402.2 | 298.7 | 606.6 | 337.8 | 284.3 | 592.2 | 376.3 | 281 | 227.3 | 247.8 | 261.8 | 235.3 | 249 | 226.6 | 261.9
1234 | 1089 | -6.7 | 0 | 0 | 278.4 | 219.4 | 220 | 218.5 | 264.8 | 37.6 | 19.6 | 62.5 | 5.2 | 261.7 | 14.5 | 368.7 | 179.4 | 83.4 | 401.2 | 297.9 | 606.1 | 336.5 | 283.2 | 591.4 | 375.8 | 280.9 | 227 | 247.6 | 261.5 | 234.9 | 248.7 | 226.3 | 261.6
1235 | 1090 | -6.8 | 0 | 0 | 278.5 | 219.3 | 219.6 | 218.3 | 264.4 | 37.4 | 19.6 | 62.5 | 5.9 | 261.2 | 14.2 | 367.9 | 178.4 | 83.1 | 400.3 | 297.3 | 605.6 | 335.4 | 282.2 | 590.7 | 375.2 | 280.8 | 226.8 | 247.3 | 261.2 | 234.6 | 248.3 | 226.1 | 261.3
1236 | 1091 | -6.8 | 0 | 0 | 278.3 | 219 | 219.1 | 218 | 263.9 | 37.3 | 19.6 | 62.4 | 6.3 | 266.5 | 12.5 | 367.1 | 177.4 | 82.6 | 399.5 | 296.6 | 605.1 | 334.9 | 281.5 | 590.1 | 374.6 | 280.7 | 226.4 | 247 | 260.9 | 234.2 | 248 | 225.7 | 261
1237 | 1092 | -6.8 | 0 | 0 | 278 | 218.8 | 218.4 | 217.6 | 263.3 | 37.2 | 19.6 | 62.3 | 5.6 | 260.7 | 12.3 | 366.4 | 176.4 | 82.2 | 398.7 | 295.9 | 604.7 | 333.8 | 280.9 | 589 | 374 | 280.6 | 226.1 | 246.7 | 260.6 | 233.9 | 247.7 | 225.4 | 260.7
1238 | 1093 | -6.8 | 0 | 0 | 277.6 | 218.7 | 217.7 | 217.4 | 263.2 | 37.3 | 19.6 | 62.3 | 5.4 | 265.9 | 12.3 | 365.6 | 176.1 | 81.7 | 397.8 | 294.9 | 604.2 | 332.6 | 279.9 | 587.7 | 373.3 | 280.5 | 225.9 | 246.4 | 260.3 | 233.6 | 247.4 | 225.1 | 260.4
1239 | 1094 | -6.7 | 0 | 0 | 276.7 | 218.6 | 217.6 | 217.2 | 262.8 | 37.3 | 19.6 | 62.2 | 5.4 | 267.4 | 12.7 | 364.7 | 176.1 | 81.5 | 396.7 | 294.1 | 603.8 | 332.1 | 278.8 | 586.8 | 372.7 | 280.4 | 225.6 | 246.2 | 260 | 233.2 | 247.2 | 224.7 | 260.1
1240 | 1095 | -6.3 | 0 | 0 | 276.2 | 218.5 | 217.3 | 216.9 | 262.5 | 37.3 | 19.6 | 62.1 | 5.7 | 265 | 12.3 | 363.8 | 175.8 | 81.3 | 395.4 | 293.4 | 603.5 | 331.4 | 278.3 | 586.6 | 371.5 | 280.3 | 225.3 | 246 | 259.7 | 232.9 | 246.9 | 224.4 | 259.8
1241 | 1096 | -6.4 | 0 | 0 | 276 | 218.3 | 217.1 | 216.7 | 262.1 | 37.4 | 19.6 | 62 | 6.1 | 249 | 13.7 | 362.9 | 175.3 | 81.2 | 394.1 | 292.5 | 602.9 | 330.7 | 277.5 | 586.2 | 370.6 | 280.2 | 225.1 | 245.7 | 259.4 | 232.6 | 246.6 | 224.1 | 259.5
1242 | 1097 | -6.7 | 0 | 0 | 276.1 | 218.2 | 216.9 | 216.5 | 262.5 | 37.4 | 19.6 | 61.9 | 6.9 | 248.8 | 15 | 362.1 | 174.6 | 81 | 392.8 | 291.6 | 602.3 | 329.4 | 276.9 | 586.1 | 370.1 | 280.1 | 224.8 | 245.4 | 259.1 | 232.3 | 246.4 | 223.9 | 259.3
1243 | 1098 | -6.6 | 0 | 0 | 275.8 | 217.9 | 216.7 | 216.3 | 263.7 | 37.3 | 19.6 | 61.9 | 7.1 | 244.8 | 15.7 | 361.3 | 173.8 | 80.6 | 391.2 | 290.8 | 601.8 | 328 | 275.9 | 585.3 | 369.3 | 280 | 224.5 | 245 | 258.8 | 231.9 | 246.1 | 223.6 | 259
1244 | 1099 | -6.7 | 0 | 0 | 275.1 | 217.7 | 216.2 | 216.1 | 265.6 | 37.2 | 19.6 | 61.8 | 8.8 | 254 | 16.1 | 360.5 | 173.2 | 80.3 | 389.8 | 289.9 | 601.2 | 326.7 | 274.9 | 584.6 | 368.5 | 279.9 | 224.2 | 244.7 | 258.5 | 231.6 | 245.8 | 223.3 | 258.7
1245 | 1100 | -6.8 | 0 | 0 | 275.1 | 217.6 | 216.2 | 215.8 | 265.8 | 37.2 | 19.6 | 61.7 | 7.5 | 258.8 | 14.6 | 359.8 | 171.9 | 80 | 389.1 | 289 | 600.5 | 326.1 | 274.1 | 584.7 | 367.7 | 279.8 | 224 | 244.4 | 258.1 | 231.3 | 245.5 | 223 | 258.5
1246 | 1101 | -6.8 | 0 | 0 | 275.3 | 217.3 | 216.1 | 215.6 | 264.7 | 37.1 | 19.6 | 61.6 | 7 | 257.6 | 14.3 | 358.9 | 171.4 | 79.6 | 388.2 | 288.2 | 599.8 | 325.3 | 273.5 | 583.9 | 367.3 | 279.7 | 223.7 | 244.1 | 257.9 | 230.9 | 245.2 | 222.9 | 258.1
1247 | 1102 | -6.8 | 0 | 0 | 275.8 | 217.3 | 215.9 | 215.3 | 263.7 | 37.1 | 19.6 | 61.5 | 6.8 | 258.1 | 13.8 | 358 | 171.5 | 79.2 | 387.2 | 287.4 | 599 | 324 | 272.7 | 584.3 | 366.8 | 279.6 | 223.4 | 243.8 | 257.6 | 230.6 | 244.9 | 222.5 | 257.8
1248 | 1103 | -6.8 | 0 | 0 | 276.2 | 217 | 215.5 | 215 | 263.2 | 37.1 | 19.6 | 61.3 | 5.8 | 261.4 | 13.4 | 357 | 171 | 78.9 | 386 | 286.5 | 598.4 | 323.5 | 271.5 | 583.8 | 365.9 | 279.5 | 223.2 | 243.5 | 257.3 | 230.3 | 244.6 | 222.3 | 257.6
1249 | 1104 | -6.6 | 0 | 0 | 275.9 | 216.8 | 215.1 | 214.8 | 263.1 | 37.1 | 19.6 | 61.2 | 6.5 | 266.5 | 13.4 | 356.1 | 170.8 | 78.6 | 384.9 | 285.7 | 597.7 | 322.7 | 270.9 | 583.8 | 365.3 | 279.4 | 222.8 | 243.1 | 257 | 230 | 244.3 | 222.2 | 257.3
1250 | 1105 | -6.6 | 0 | 0 | 275.9 | 216.5 | 214.5 | 214.8 | 262.4 | 37 | 19.6 | 61.1 | 6.4 | 255.2 | 14.3 | 355.1 | 169.6 | 78.3 | 384.1 | 285 | 596.9 | 322.1 | 270.1 | 582.9 | 364.6 | 279.3 | 222.6 | 242.8 | 256.7 | 229.7 | 244 | 222 | 257
1251 | 1106 | -6.6 | 0 | 0 | 275.7 | 216.3 | 214.1 | 214.8 | 261.4 | 36.8 | 19.7 | 61.1 | 6.6 | 255.3 | 17.3 | 354.2 | 169.1 | 78.2 | 383.1 | 284.2 | 596.2 | 321 | 269.6 | 581.9 | 364.2 | 279.2 | 222.4 | 242.5 | 256.4 | 229.4 | 243.8 | 221.8 | 256.8
1252 | 1107 | -6.6 | 0 | 0 | 275.4 | 216.1 | 214.2 | 214.8 | 260.8 | 36.6 | 19.6 | 61 | 8.2 | 257.2 | 18.2 | 353.3 | 168.8 | 77.9 | 382.1 | 283.3 | 595.4 | 320.5 | 269.1 | 581.1 | 363.4 | 279.1 | 222.2 | 242.3 | 256.2 | 229.1 | 243.5 | 221.6 | 256.5
1253 | 1108 | -6.7 | 0 | 0 | 275.3 | 215.9 | 214 | 214.6 | 261 | 36.5 | 19.6 | 60.9 | 7.9 | 261.8 | 16.2 | 352.4 | 168.4 | 77.5 | 381.1 | 282.5 | 594.6 | 319.3 | 268.4 | 580.8 | 363.1 | 279 | 221.9 | 242 | 255.9 | 228.8 | 243.3 | 221.4 | 256.2
1254 | 1109 | -6.8 | 0 | 0 | 274.8 | 215.9 | 213.8 | 214.4 | 261 | 36.4 | 19.7 | 60.8 | 6 | 260.3 | 14.7 | 351.8 | 168 | 77.2 | 380.3 | 282 | 593.9 | 318.3 | 267.5 | 580 | 362.7 | 278.9 | 221.7 | 241.8 | 255.6 | 228.5 | 243 | 221.1 | 256
1255 | 1110 | -6.8 | 0 | 0 | 274.7 | 215.8 | 213.4 | 214.3 | 261.5 | 36.2 | 19.7 | 60.7 | 3.4 | 239.6 | 13.4 | 351 | 167.6 | 77 | 379.2 | 281.3 | 593.2 | 317.4 | 266.5 | 578.6 | 362.3 | 278.8 | 221.5 | 241.5 | 255.3 | 228.3 | 242.8 | 221 | 255.7
1256 | 1111 | -6.8 | 0 | 0 | 274.6 | 215.6 | 212.8 | 214.1 | 261.1 | 36 | 19.7 | 60.7 | 2.6 | 234.2 | 13.5 | 350.1 | 167 | 76.8 | 378.1 | 280.6 | 592.5 | 317.1 | 265.4 | 578.3 | 361.9 | 278.7 | 221.3 | 241.2 | 255 | 228 | 242.5 | 220.8 | 255.5
1257 | 1112 | -6.8 | 0 | 0 | 274.3 | 215.5 | 212.3 | 214.1 | 260.4 | 36 | 19.7 | 60.6 | 4.7 | 223.3 | 15.1 | 349.2 | 167 | 76.5 | 377.1 | 280 | 591.8 | 316.2 | 264.1 | 577.4 | 361.4 | 278.6 | 221 | 240.9 | 254.8 | 227.7 | 242.3 | 220.5 | 255.2
1258 | 1113 | -6.8 | 0 | 0 | 275 | 215.4 | 211.8 | 214 | 260 | 36 | 19.7 | 60.5 | 5.5 | 230.2 | 17.9 | 348.5 | 166.6 | 76.2 | 376.2 | 279.4 | 591.1 | 315.5 | 263.1 | 576.8 | 360.9 | 278.5 | 220.7 | 240.6 | 254.5 | 227.4 | 242.1 | 220.3 | 255
1259 | 1114 | -6.8 | 0 | 0 | 275.4 | 215.2 | 211.6 | 214 | 259.4 | 35.9 | 19.7 | 60.5 | 3.6 | 228.3 | 17.5 | 347.9 | 164.5 | 76 | 374 | 278.8 | 590.5 | 314.5 | 262.3 | 575.4 | 360.2 | 278.4 | 220.5 | 240.3 | 254.2 | 227.1 | 241.9 | 220 | 254.7
1260 | 1115 | -6.8 | 0 | 0 | 275.5 | 215.2 | 211.5 | 214 | 259 | 35.8 | 19.7 | 60.4 | 3 | 227.2 | 14.5 | 347.3 | 164.6 | 75.7 | 373.2 | 278.2 | 590.1 | 313.3 | 261.6 | 574.6 | 359.6 | 278.2 | 220.2 | 240.1 | 253.9 | 226.8 | 241.7 | 219.8 | 254.4
1261 | 1116 | -6.8 | 0 | 0 | 276 | 215.2 | 211.5 | 213.6 | 258.6 | 35.7 | 19.7 | 60.3 | 2.1 | 228.5 | 13.5 | 346.6 | 165.1 | 75.4 | 372.9 | 277.7 | 589.7 | 312.9 | 260.8 | 574.1 | 358.9 | 278.2 | 220 | 239.8 | 253.6 | 226.5 | 241.4 | 219.6 | 254.2
1262 | 1117 | -6.8 | 0 | 0 | 276.1 | 215 | 211.2 | 213.3 | 258.3 | 35.6 | 19.7 | 60.3 | 2 | 225.8 | 14.8 | 345.7 | 165.2 | 75.1 | 372.2 | 277 | 589.1 | 312 | 259.8 | 573 | 358.4 | 278 | 219.8 | 239.5 | 253.3 | 226.3 | 241.2 | 219.4 | 253.9
1263 | 1118 | -6.7 | 0 | 0 | 276.1 | 214.8 | 211.2 | 213.2 | 258 | 35.5 | 19.7 | 60.2 | 3.6 | 251.8 | 16.2 | 344.9 | 165.1 | 75 | 371.4 | 276.4 | 588.5 | 311.1 | 258.6 | 572.4 | 357.9 | 277.9 | 219.6 | 239.3 | 253 | 226 | 241 | 219.3 | 253.6
1264 | 1119 | -6.6 | 0 | 0 | 276 | 214.7 | 211 | 213 | 257.4 | 35.4 | 19.7 | 60.1 | 4.9 | 265.5 | 14.4 | 344.1 | 164.5 | 74.8 | 370.7 | 275.8 | 588 | 309.8 | 257.6 | 571.3 | 357.5 | 277.8 | 219.4 | 239.1 | 252.7 | 225.7 | 240.7 | 218.9 | 253.3
1265 | 1120 | -6.7 | 0 | 0 | 275.8 | 214.5 | 210.8 | 213.1 | 256.8 | 35.5 | 19.7 | 60 | 5.7 | 272.4 | 13.1 | 343.4 | 164.2 | 74.6 | 370.1 | 275.2 | 587.6 | 309.6 | 256.6 | 570.6 | 357.1 | 277.7 | 219.2 | 238.8 | 252.4 | 225.4 | 240.5 | 218.7 | 253.1
1266 | 1121 | -6.6 | 0 | 0 | 275.6 | 214.3 | 210.6 | 213 | 256.4 | 35.5 | 19.7 | 59.9 | 4 | 267.7 | 12.7 | 342.6 | 164 | 74.4 | 369.3 | 274.7 | 587.1 | 308.6 | 255.6 | 570.3 | 356.5 | 277.6 | 219 | 238.6 | 252.2 | 225.2 | 240.2 | 218.4 | 252.8
1267 | 1122 | -6.5 | 0 | 0 | 275.6 | 214.2 | 210 | 213 | 256.1 | 35.5 | 19.7 | 59.8 | 2.9 | 264.5 | 13.7 | 341.9 | 163.4 | 74.2 | 368.6 | 274.1 | 586.7 | 307.8 | 254.7 | 569.7 | 356.1 | 277.5 | 218.8 | 238.3 | 251.9 | 224.9 | 240 | 218.2 | 252.5
1268 | 1123 | -6.7 | 0 | 0 | 275.3 | 214 | 209.6 | 212.6 | 255.8 | 35.5 | 19.7 | 59.8 | 3.7 | 249.2 | 12.4 | 341.1 | 162.7 | 73.8 | 367.9 | 273.4 | 586.2 | 307.4 | 253.6 | 569 | 355.5 | 277.4 | 218.6 | 238.1 | 251.7 | 224.7 | 239.8 | 217.9 | 252.3
1269 | 1124 | -6.7 | 0 | 0 | 275 | 213.9 | 209.7 | 212.2 | 255.8 | 35.5 | 19.7 | 59.7 | 4.6 | 277 | 10.5 | 340.4 | 161.9 | 73.5 | 367.1 | 272.7 | 585.7 | 306.8 | 252.5 | 568.6 | 355 | 277.3 | 218.4 | 237.8 | 251.3 | 224.4 | 239.6 | 217.7 | 252
1270 | 1125 | -6.8 | 0 | 0 | 275.1 | 213.8 | 209.7 | 212 | 255.5 | 35.5 | 19.7 | 59.7 | 7.1 | 266.2 | 12.7 | 339.7 | 161.3 | 73.3 | 366.2 | 272 | 585.2 | 306.1 | 251.7 | 567.7 | 354.5 | 277.2 | 218.1 | 237.6 | 251 | 224.2 | 239.4 | 217.5 | 251.7
1271 | 1126 | -6.8 | 0 | 0 | 274.5 | 213.7 | 209.5 | 211.9 | 255.2 | 35.5 | 19.7 | 59.5 | 6.7 | 274.6 | 13.3 | 339.1 | 160.6 | 72.9 | 365.4 | 271.4 | 584.6 | 305.7 | 250.9 | 567.3 | 354 | 277.1 | 217.9 | 237.3 | 250.8 | 224 | 239.2 | 217.3 | 251.5
1272 | 1127 | -6.8 | 0 | 0 | 273.6 | 213.5 | 209.4 | 211.7 | 254.9 | 35.3 | 19.7 | 59.5 | 5.7 | 286.9 | 14.5 | 338.3 | 159.8 | 72.7 | 364.4 | 270.7 | 584 | 305.1 | 249.9 | 566.4 | 353.3 | 277 | 217.7 | 237.1 | 250.6 | 223.7 | 239 | 217.2 | 251.2
1273 | 1128 | -6.8 | 0 | 0 | 273.1 | 213.4 | 209.2 | 211.5 | 254.7 | 35.2 | 19.7 | 59.4 | 4.6 | 291.7 | 17.4 | 337.6 | 158.8 | 72.4 | 363.4 | 270 | 583.5 | 304.3 | 248.9 | 565.6 | 352.6 | 276.9 | 217.5 | 237 | 250.3 | 223.4 | 238.8 | 216.9 | 251
1274 | 1129 | -6.8 | 0 | 0 | 273.2 | 213.2 | 208.9 | 211.3 | 254.5 | 35.1 | 19.7 | 59.4 | 4.4 | 287.5 | 18 | 336.9 | 157.7 | 72 | 362.5 | 269.3 | 583 | 303.5 | 248.1 | 565.7 | 352.1 | 276.8 | 217.4 | 236.7 | 250 | 223.2 | 238.6 | 216.8 | 250.7
1275 | 1130 | -6.8 | 0 | 0 | 273.1 | 213.1 | 208.9 | 211.3 | 253.9 | 35 | 19.7 | 59.3 | 6.4 | 281.8 | 19.6 | 336.2 | 157.3 | 71.7 | 361.8 | 268.7 | 582.5 | 302.7 | 247.6 | 563.5 | 351.7 | 276.6 | 217.2 | 236.4 | 249.8 | 222.9 | 238.4 | 216.7 | 250.4
1276 | 1131 | -6.8 | 0 | 0 | 273.3 | 212.9 | 208.6 | 211.3 | 253.5 | 35 | 19.7 | 59.2 | 5.6 | 285.2 | 20 | 335.6 | 156.8 | 71.4 | 361 | 268.1 | 582 | 301.8 | 246.5 | 563.5 | 351.3 | 276.5 | 217 | 236.2 | 249.4 | 222.6 | 238.2 | 216.5 | 250.2
1277 | 1132 | -6.9 | 0 | 0 | 273.1 | 212.8 | 208.2 | 211.3 | 253.2 | 35 | 19.7 | 59.2 | 5.4 | 280.3 | 19.2 | 335 | 156 | 71.1 | 360.1 | 267.4 | 581.5 | 301.2 | 245.5 | 563 | 350.5 | 276.4 | 216.7 | 236 | 249.2 | 222.4 | 238 | 216.4 | 249.9
1278 | 1133 | -6.9 | 0 | 0 | 272 | 212.6 | 208 | 211.1 | 252.9 | 34.9 | 19.7 | 59.1 | 5.6 | 282.9 | 19 | 334.4 | 156.7 | 70.8 | 359.2 | 266.8 | 581 | 300.8 | 244.3 | 563.5 | 350 | 276.3 | 216.5 | 235.8 | 248.9 | 222.1 | 237.8 | 216.2 | 249.7
1279 | 1134 | -5.9 | 0 | 0 | 271.1 | 212.5 | 208.1 | 211 | 252.7 | 34.9 | 19.7 | 59.1 | 5.8 | 289.8 | 18 | 333.7 | 156.7 | 70.6 | 358.4 | 266.2 | 580.4 | 300.1 | 243.2 | 563.9 | 349.8 | 276.2 | 216.3 | 235.6 | 248.7 | 221.9 | 237.6 | 216 | 249.4
1280 | 1135 | -5.5 | 0 | 0 | 270.1 | 212.3 | 207.8 | 210.6 | 252.5 | 34.8 | 19.7 | 59.1 | 7.9 | 292.2 | 18.1 | 333 | 155.7 | 70.3 | 357.5 | 265.5 | 579.9 | 298.9 | 241.9 | 563.6 | 349.3 | 276.1 | 216.1 | 235.4 | 248.4 | 221.7 | 237.5 | 215.8 | 249.2
1281 | 1136 | -6.3 | 0 | 0 | 269.8 | 212.3 | 207 | 210.3 | 252.5 | 34.7 | 19.7 | 59 | 9.9 | 292.5 | 17.1 | 332.3 | 155.1 | 70 | 356.6 | 264.9 | 579.3 | 298.4 | 240.8 | 562.2 | 348.7 | 276 | 215.9 | 235.2 | 248.1 | 221.5 | 237.3 | 215.6 | 248.9
1282 | 1137 | -6.6 | 0 | 0 | 270.1 | 212.2 | 206.8 | 210.2 | 252.5 | 34.6 | 19.7 | 59 | 9.6 | 283.5 | 15.2 | 331.5 | 155.4 | 69.8 | 355.2 | 264.2 | 578.9 | 297.3 | 239.8 | 562.3 | 348 | 275.8 | 215.7 | 235 | 247.8 | 221.2 | 237.1 | 215.3 | 248.7
1283 | 1138 | -6.7 | 0 | 0 | 270.1 | 212.1 | 206.7 | 210.2 | 252.5 | 34.5 | 19.7 | 58.9 | 7.6 | 279.5 | 17.5 | 330.8 | 155.4 | 69.7 | 353.9 | 263.6 | 578.3 | 296.3 | 238.8 | 562.3 | 347.4 | 275.7 | 215.4 | 234.8 | 247.6 | 220.9 | 236.9 | 215.1 | 248.4
1284 | 1139 | -6.4 | 0 | 0 | 270.2 | 211.9 | 206.5 | 209.8 | 253.2 | 34.5 | 19.7 | 58.8 | 6.1 | 282.1 | 16.9 | 330 | 155.4 | 69.5 | 352.9 | 262.9 | 577.6 | 295.6 | 237.9 | 562.2 | 346.8 | 275.6 | 215.2 | 234.6 | 247.3 | 220.7 | 236.7 | 214.9 | 248.2
1285 | 1140 | -6.3 | 0 | 0 | 270.4 | 211.8 | 206.5 | 209.5 | 253.4 | 34.4 | 19.7 | 58.7 | 3.9 | 271.1 | 15.7 | 329.2 | 155.1 | 69.4 | 351.7 | 262.3 | 577 | 295.3 | 236.9 | 562 | 346.1 | 275.5 | 215 | 234.4 | 247 | 220.4 | 236.5 | 214.7 | 247.9
1286 | 1141 | -6.2 | 0 | 0 | 270.4 | 211.6 | 206.2 | 209.5 | 252.9 | 34.3 | 19.7 | 58.6 | 3.2 | 236.8 | 16 | 328.5 | 153.9 | 69.4 | 351.1 | 261.6 | 576.3 | 294.9 | 235.8 | 560.3 | 345.7 | 275.4 | 214.8 | 234.2 | 246.8 | 220.2 | 236.3 | 214.5 | 247.7
1287 | 1142 | -6.1 | 0 | 0 | 270.1 | 211.4 | 205.7 | 209.4 | 253.3 | 34.2 | 19.7 | 58.6 | 3.3 | 226.5 | 15.3 | 327.8 | 152.9 | 69.3 | 350.4 | 261 | 575.5 | 294.4 | 235.1 | 561 | 345 | 275.3 | 214.7 | 233.9 | 246.6 | 220 | 236.1 | 214.3 | 247.4
1288 | 1143 | -6.1 | 0 | 0 | 270.2 | 211.2 | 205.2 | 209.2 | 253.1 | 34.1 | 19.7 | 58.5 | 5 | 220.6 | 16.4 | 327 | 152.1 | 69.2 | 349.4 | 260.2 | 574.6 | 293.6 | 234 | 560.7 | 344.3 | 275.2 | 214.5 | 233.7 | 246.4 | 219.7 | 235.9 | 214.1 | 247.2
1289 | 1144 | -6.4 | 0 | 0 | 269.5 | 211 | 204.7 | 209 | 252.9 | 34.1 | 19.7 | 58.6 | 7.1 | 249.2 | 15.5 | 326.3 | 152.5 | 69.2 | 348.5 | 259.5 | 573.6 | 293 | 233 | 560.3 | 343.8 | 275.1 | 214.3 | 233.6 | 246.1 | 219.4 | 235.7 | 213.8 | 246.9
1290 | 1145 | -6.6 | 0 | 0 | 269.1 | 210.9 | 204.2 | 208.8 | 253 | 34.1 | 19.7 | 58.5 | 7.7 | 262.6 | 12.8 | 325.4 | 152.5 | 69.3 | 347.6 | 259 | 572.6 | 291.7 | 231.6 | 558.8 | 343.3 | 274.9 | 214.1 | 233.4 | 245.8 | 219.2 | 235.5 | 213.5 | 246.7
1291 | 1146 | -6.6 | 0 | 0 | 268.5 | 210.7 | 204.1 | 208.4 | 252.8 | 34.1 | 19.7 | 58.4 | 7.4 | 281.5 | 10.9 | 324.5 | 152 | 69.3 | 347.2 | 258.5 | 571.7 | 290.7 | 230.6 | 559.1 | 342.6 | 274.8 | 213.9 | 233.2 | 245.6 | 219 | 235.3 | 213.3 | 246.5
1292 | 1147 | -6.7 | 0 | 0 | 268.8 | 210.6 | 204 | 207.7 | 252.7 | 34.2 | 19.8 | 58.4 | 7.9 | 259.8 | 10.7 | 323.4 | 151.6 | 69 | 347 | 257.8 | 570.7 | 289.6 | 229.5 | 558.3 | 342 | 274.7 | 213.7 | 233 | 245.3 | 218.7 | 235.1 | 213.1 | 246.2
1293 | 1148 | -6.8 | 0 | 0 | 268.9 | 210.4 | 203.9 | 207.3 | 252.2 | 34.2 | 19.8 | 58.3 | 8.6 | 255.7 | 11.5 | 322.2 | 150.2 | 68.9 | 346.5 | 257.2 | 569.5 | 289.2 | 228.1 | 558 | 341.5 | 274.6 | 213.5 | 232.7 | 245 | 218.5 | 234.9 | 212.9 | 246
1294 | 1149 | -6.8 | 0 | 0 | 268.6 | 210.3 | 204.2 | 206.9 | 251.7 | 34.2 | 19.8 | 58.3 | 6 | 257 | 12.9 | 321.1 | 149.3 | 68.8 | 346.2 | 256.6 | 568.3 | 288.6 | 226.6 | 557.2 | 340.8 | 274.5 | 213.3 | 232.5 | 244.8 | 218.2 | 234.6 | 212.7 | 245.7
1295 | 1150 | -6.8 | 0 | 0 | 268.2 | 210.2 | 204.5 | 206.6 | 251.8 | 34.2 | 19.8 | 58.2 | 4.8 | 244.8 | 13.6 | 320.1 | 148.9 | 68.6 | 346.1 | 255.9 | 567.2 | 288.2 | 224.9 | 556.3 | 339.9 | 274.4 | 213.1 | 232.3 | 244.6 | 218 | 234.4 | 212.4 | 245.4
1296 | 1151 | -6.8 | 0 | 0 | 268.1 | 210.1 | 204.8 | 206.1 | 251.2 | 34.2 | 19.8 | 58.2 | 3.9 | 231.4 | 13.6 | 319 | 148.2 | 68.3 | 346 | 255.3 | 566.1 | 287.8 | 223.5 | 555.5 | 339.3 | 274.3 | 212.9 | 232.1 | 244.4 | 217.7 | 234.1 | 212.2 | 245.2
1297 | 1152 | -6.7 | 0 | 0 | 267.9 | 210 | 205 | 205.5 | 250.5 | 34.2 | 19.8 | 58.1 | 3.2 | 245.4 | 13.2 | 317.7 | 147.3 | 68.4 | 345.7 | 254.7 | 565.2 | 286.7 | 222.3 | 555 | 339 | 274.1 | 212.8 | 231.9 | 244.1 | 217.4 | 233.8 | 211.9 | 244.9
1298 | 1153 | -6.6 | 0 | 0 | 267.9 | 209.7 | 204.6 | 205.5 | 250.1 | 34.2 | 19.8 | 58 | 3.3 | 249.3 | 16.1 | 316.6 | 147.4 | 68.4 | 345.3 | 253.9 | 564.3 | 285.7 | 221.3 | 555.5 | 338.3 | 274 | 212.6 | 231.7 | 243.9 | 217.2 | 233.5 | 211.7 | 244.7
1299 | 1154 | -5.8 | 0 | 0 | 267.7 | 209.5 | 204.7 | 205.4 | 249.9 | 34.1 | 19.8 | 58 | 4.2 | 256 | 15 | 315.5 | 146.7 | 68.4 | 344.8 | 253.4 | 563.4 | 285.5 | 219.9 | 555.3 | 338 | 273.9 | 212.4 | 231.4 | 243.6 | 217 | 233.3 | 211.5 | 244.5
1300 | 1155 | -6.2 | 0 | 0 | 266.9 | 209.2 | 204.6 | 205.2 | 250.1 | 34 | 19.8 | 57.9 | 4.9 | 275.4 | 11.9 | 314.6 | 145.3 | 68.5 | 344.3 | 253 | 562.6 | 285 | 218.7 | 555 | 337.9 | 273.8 | 212.2 | 231.2 | 243.3 | 216.7 | 233.1 | 211.4 | 244.2
1301 | 1156 | -6.6 | 0 | 0 | 266.8 | 209.1 | 204.1 | 204.9 | 250.2 | 34 | 19.8 | 57.9 | 5 | 261.1 | 12.2 | 314 | 144.6 | 68.5 | 343.5 | 252.3 | 561.9 | 284.6 | 217.7 | 554.9 | 337.6 | 273.7 | 211.9 | 230.9 | 243 | 216.5 | 232.8 | 211.2 | 244
1302 | 1157 | -6.8 | 0 | 0 | 266.2 | 209 | 203.3 | 204.7 | 249.6 | 34.1 | 19.8 | 57.8 | 6.5 | 257.1 | 14.1 | 313.7 | 144.5 | 68.5 | 342.6 | 251.7 | 561.3 | 284.5 | 217.4 | 554.7 | 337.4 | 273.6 | 211.7 | 230.7 | 242.8 | 216.3 | 232.7 | 211.1 | 243.7
1303 | 1158 | -6.6 | 0 | 0 | 265.7 | 208.8 | 202.9 | 204.6 | 249.5 | 34.1 | 19.8 | 57.7 | 9 | 264.1 | 16 | 313.2 | 145 | 68.4 | 341.9 | 251.1 | 560.6 | 284.6 | 216.1 | 554.7 | 337.2 | 273.4 | 211.5 | 230.4 | 242.5 | 216.1 | 232.5 | 210.8 | 243.5
1304 | 1159 | -6.5 | 0 | 0 | 265.9 | 208.7 | 203 | 204.3 | 249.9 | 34 | 19.8 | 57.6 | 12.8 | 260.5 | 16.3 | 312.7 | 143.8 | 68.2 | 341.3 | 250.6 | 560.1 | 284.8 | 214.8 | 554 | 336.8 | 273.3 | 211.2 | 230.2 | 242.2 | 215.8 | 232.2 | 210.6 | 243.2
1305 | 1160 | -6.7 | 0 | 0 | 265.6 | 208.5 | 202.8 | 204.1 | 251.2 | 34 | 19.8 | 57.4 | 15.1 | 260.8 | 18.9 | 312.2 | 143.2 | 67.9 | 340.6 | 250.1 | 559.5 | 284.2 | 213.6 | 553.7 | 336 | 273.2 | 210.9 | 230 | 242 | 215.6 | 232 | 210.4 | 243
1306 | 1161 | -6.5 | 0 | 0 | 265.2 | 208.3 | 202.4 | 204 | 251 | 33.9 | 19.8 | 57.2 | 10.2 | 255.5 | 22.9 | 311.4 | 142.2 | 67.6 | 340.2 | 249.4 | 558.9 | 284.3 | 212.1 | 553.4 | 335.5 | 273.1 | 210.7 | 229.8 | 241.7 | 215.3 | 231.8 | 210.2 | 242.8
1307 | 1162 | -6.4 | 0 | 0 | 265.7 | 208.2 | 202.1 | 203.9 | 250.1 | 33.8 | 19.8 | 57.1 | 7.4 | 247.5 | 24.3 | 310.5 | 141.6 | 67.2 | 339.8 | 248.7 | 558.1 | 283.8 | 210.7 | 553.1 | 335.2 | 273 | 210.4 | 229.5 | 241.5 | 215.1 | 231.5 | 209.9 | 242.5
1308 | 1163 | -6.3 | 0 | 0 | 265.6 | 208.1 | 202.1 | 203.7 | 249.6 | 33.8 | 19.8 | 56.9 | 8.2 | 239.1 | 18.1 | 309.8 | 141.7 | 66.8 | 339 | 248 | 557.1 | 283.6 | 209.5 | 552.7 | 334.6 | 272.9 | 210.3 | 229.4 | 241.2 | 214.9 | 231.3 | 209.6 | 242.2
1309 | 1164 | -6.6 | 0 | 0 | 265.6 | 207.9 | 202.1 | 203.4 | 248.8 | 33.7 | 19.8 | 56.8 | 14.6 | 193 | 12.2 | 309 | 141.4 | 66.5 | 338.2 | 247.2 | 556 | 283.2 | 208 | 553 | 333.9 | 272.7 | 210 | 229.2 | 240.9 | 214.6 | 231 | 209.4 | 242
1310 | 1165 | -6.3 | 0 | 0 | 265.5 | 207.7 | 201.9 | 202.9 | 247.8 | 33.7 | 19.8 | 56.6 | 11.4 | 246.4 | 9.6 | 308.2 | 140.4 | 66.2 | 337.5 | 246.5 | 555.1 | 282.4 | 206.5 | 552.3 | 333.4 | 272.6 | 209.8 | 229 | 240.6 | 214.4 | 230.8 | 209.1 | 241.8
1311 | 1166 | -6.3 | 0 | 0 | 265 | 207.4 | 201.3 | 202.5 | 248.3 | 33.7 | 19.8 | 56.4 | 9.3 | 225.7 | 14.9 | 307.3 | 139.6 | 65.9 | 336.8 | 245.8 | 554.2 | 281.3 | 205.4 | 551.3 | 333.1 | 272.5 | 209.6 | 228.8 | 240.4 | 214.1 | 230.6 | 208.8 | 241.5
1312 | 1167 | -6.3 | 0 | 0 | 264.6 | 207.1 | 201 | 202.1 | 248.9 | 33.7 | 19.8 | 56.3 | 7.6 | 217.9 | 18.6 | 306.2 | 139.6 | 66 | 336.2 | 245.1 | 553.3 | 279.9 | 204.5 | 551 | 332.4 | 272.4 | 209.4 | 228.6 | 240.2 | 213.9 | 230.3 | 208.4 | 241.3
1313 | 1168 | -6.5 | 0 | 0 | 264.4 | 207 | 200.6 | 201.6 | 248.1 | 33.7 | 19.8 | 56.1 | 8.4 | 216.6 | 23.8 | 305.2 | 139.9 | 66 | 335.7 | 244.5 | 552.2 | 278.6 | 203.3 | 550.2 | 331.4 | 272.3 | 209.3 | 228.4 | 240 | 213.6 | 230 | 208.2 | 241
1314 | 1169 | -6.8 | 0 | 0 | 263.9 | 206.8 | 200.5 | 201.1 | 248.2 | 33.6 | 19.8 | 56 | 9.8 | 212.5 | 23.1 | 304 | 139.6 | 65.8 | 335.2 | 244.1 | 551.3 | 277.4 | 202 | 549.7 | 330.7 | 272.1 | 209.2 | 228.1 | 239.8 | 213.3 | 229.7 | 208 | 240.8
1315 | 1170 | -6.8 | 0 | 0 | 263.7 | 206.6 | 200.7 | 200.5 | 247.6 | 33.5 | 19.8 | 55.8 | 9.5 | 237.3 | 17.4 | 303.4 | 140.2 | 65.7 | 334.5 | 243.6 | 550.4 | 276.6 | 200.7 | 548.7 | 330.2 | 272 | 209 | 227.9 | 239.6 | 213.1 | 229.5 | 207.7 | 240.5
1316 | 1171 | -6.8 | 0 | 0 | 263.5 | 206.4 | 200.8 | 199.8 | 246.7 | 33.4 | 19.8 | 55.7 | 10.5 | 222.2 | 12.8 | 302.9 | 139.9 | 65.6 | 333.7 | 243.1 | 549.6 | 276 | 199.7 | 548.5 | 329.3 | 271.9 | 208.7 | 227.7 | 239.3 | 212.8 | 229.2 | 207.5 | 240.3
1317 | 1172 | -6.8 | 0 | 0 | 263.2 | 206.4 | 200.5 | 199.6 | 245.8 | 33.3 | 19.8 | 55.6 | 13.8 | 221.4 | 19.4 | 302.4 | 139.8 | 65.6 | 332.9 | 242.7 | 548.7 | 275.7 | 198.6 | 547.9 | 328.7 | 271.8 | 208.5 | 227.4 | 239 | 212.5 | 229 | 207.3 | 240
1318 | 1173 | -6.9 | 0 | 0 | 262.8 | 206.2 | 200 | 199.4 | 246.1 | 33.1 | 19.8 | 55.4 | 13.6 | 230 | 19 | 301.9 | 140.7 | 65.6 | 332.3 | 242.3 | 548 | 275.3 | 197.4 | 547.5 | 328 | 271.6 | 208.2 | 227.2 | 238.8 | 212.3 | 228.7 | 207.1 | 239.8
1319 | 1174 | -6.9 | 0 | 0 | 262.9 | 206 | 199.6 | 199.2 | 246.8 | 32.9 | 19.8 | 55.2 | 7.3 | 238.1 | 20.4 | 301.5 | 140.2 | 65.7 | 331.6 | 241.9 | 547.5 | 274.6 | 196 | 546.8 | 327.7 | 271.5 | 208 | 226.9 | 238.5 | 212 | 228.4 | 206.9 | 239.5
1320 | 1175 | -6.9 | 0 | 0 | 263.2 | 205.5 | 199.1 | 199.2 | 247.5 | 32.8 | 19.8 | 55.1 | 8.3 | 230.9 | 26.2 | 301 | 138.9 | 65.7 | 330.6 | 241.2 | 546.8 | 274 | 194.7 | 546.1 | 327 | 271.4 | 207.8 | 226.6 | 238.3 | 211.8 | 228.1 | 206.7 | 239.3
1321 | 1176 | -6.9 | 0 | 0 | 263.1 | 205.3 | 198.6 | 199 | 247 | 32.8 | 19.8 | 54.9 | 9.8 | 240.6 | 20 | 300.6 | 137.7 | 65.7 | 329.8 | 240.7 | 546.1 | 274 | 193.9 | 545.9 | 326.2 | 271.3 | 207.6 | 226.5 | 238.1 | 211.5 | 227.8 | 206.4 | 239
1322 | 1177 | -6.9 | 0 | 0 | 262.9 | 205 | 198.3 | 198.9 | 246 | 32.7 | 19.8 | 54.8 | 11.1 | 241.6 | 20.8 | 300.2 | 138 | 65.6 | 329 | 240.3 | 545.6 | 274.1 | 192.9 | 545.7 | 325.7 | 271.2 | 207.4 | 226.3 | 237.8 | 211.2 | 227.5 | 206.2 | 238.8
1323 | 1178 | -6.9 | 0 | 0 | 262.6 | 204.6 | 198.2 | 198.6 | 246 | 32.7 | 19.8 | 54.5 | 10.7 | 245.6 | 23.8 | 299.9 | 138.6 | 65.4 | 328.2 | 239.8 | 545.1 | 273.5 | 191.7 | 545.3 | 325.6 | 271 | 207.1 | 226 | 237.5 | 211 | 227.3 | 206.1 | 238.6
1324 | 1179 | -6.9 | 0 | 0 | 262 | 204.3 | 197.7 | 198.2 | 245.9 | 32.6 | 19.8 | 54.4 | 12.5 | 253.6 | 23.2 | 299.6 | 138.9 | 65.3 | 327.4 | 239.3 | 544.5 | 273 | 190.8 | 544.5 | 325.1 | 270.9 | 206.9 | 225.8 | 237.3 | 210.8 | 227 | 205.9 | 238.4
1325 | 1180 | -6.8 | 0 | 0 | 261.3 | 204.1 | 197.9 | 198 | 245.2 | 32.6 | 19.8 | 54.2 | 10.8 | 256 | 23.7 | 299.2 | 139.4 | 65 | 326.6 | 238.9 | 544.1 | 272.5 | 189.9 | 543.7 | 324.4 | 270.8 | 206.7 | 225.5 | 237 | 210.5 | 226.8 | 205.6 | 238.1
1326 | 1181 | -6.8 | 0 | 0 | 260.6 | 203.9 | 198.1 | 197.6 | 244.2 | 32.6 | 19.8 | 54.2 | 10.6 | 250.6 | 24.6 | 298.8 | 139.7 | 64.6 | 325.6 | 238.4 | 543.6 | 271.8 | 188.9 | 543.1 | 323.7 | 270.6 | 206.5 | 225.3 | 236.8 | 210.2 | 226.5 | 205.3 | 237.8
1327 | 1182 | -6.8 | 0 | 0 | 260.1 | 203.7 | 198.3 | 197.2 | 243.3 | 32.6 | 19.8 | 54.1 | 11.3 | 256.9 | 23.2 | 298.5 | 139.3 | 64.4 | 324.5 | 237.9 | 543 | 270.6 | 187.9 | 542.5 | 323.4 | 270.5 | 206.2 | 225.1 | 236.6 | 210 | 226.3 | 205 | 237.6
1328 | 1183 | -6.6 | 0 | 0 | 259.6 | 203.5 | 198.3 | 197.1 | 242.3 | 32.5 | 19.8 | 53.9 | 13.9 | 253.7 | 23.7 | 298.3 | 138.4 | 64.2 | 323.4 | 237.4 | 542.5 | 269.5 | 187 | 542.1 | 322.8 | 270.4 | 206 | 224.9 | 236.4 | 209.7 | 226 | 204.7 | 237.3
1329 | 1184 | -6.3 | 0 | 0 | 258.8 | 203.2 | 197.9 | 196.8 | 241.5 | 32.5 | 19.8 | 53.7 | 13.9 | 263.9 | 21.7 | 298 | 138.4 | 63.9 | 322.4 | 236.8 | 542 | 268.6 | 186.1 | 541.6 | 322.2 | 270.3 | 205.9 | 224.7 | 236.1 | 209.5 | 225.7 | 204.5 | 237.1
1330 | 1185 | -6.4 | 0 | 0 | 258.4 | 203 | 197.6 | 196.5 | 240.8 | 32.6 | 19.8 | 53.6 | 11.3 | 257.1 | 24.8 | 297.6 | 137.8 | 63.6 | 321.4 | 236.3 | 541.6 | 267.9 | 185.5 | 541 | 321.7 | 270.1 | 205.7 | 224.6 | 235.9 | 209.2 | 225.5 | 204.1 | 236.9
1331 | 1186 | -6.5 | 0 | 0 | 258.3 | 202.9 | 197.1 | 196.2 | 240.3 | 32.6 | 19.8 | 53.5 | 12.2 | 252.8 | 27.1 | 297.1 | 137.5 | 63.5 | 320.4 | 235.8 | 541.2 | 267.2 | 184.8 | 540.7 | 320.9 | 270 | 205.5 | 224.3 | 235.6 | 209 | 225.3 | 203.9 | 236.6
1332 | 1187 | -6.4 | 0 | 0 | 258.3 | 202.7 | 196.7 | 196 | 239.6 | 32.7 | 19.8 | 53.3 | 11.3 | 261.8 | 26.8 | 296.6 | 137.9 | 63.3 | 319.4 | 235.2 | 540.7 | 265.8 | 183.7 | 540.5 | 320.3 | 269.9 | 205.3 | 224.1 | 235.4 | 208.8 | 225 | 203.7 | 236.4
1333 | 1188 | -6.3 | 0 | 0 | 258.3 | 202.5 | 196.2 | 196 | 239.6 | 32.7 | 19.8 | 53.2 | 11.6 | 266.6 | 26.5 | 296.2 | 137.3 | 63.1 | 318.4 | 234.7 | 540.2 | 265.2 | 182.8 | 540.2 | 319.8 | 269.7 | 205.1 | 223.9 | 235.1 | 208.5 | 224.8 | 203.5 | 236.1
1334 | 1189 | -5.8 | 0 | 0 | 258.5 | 202.3 | 195.9 | 196 | 240.3 | 32.8 | 19.8 | 53.1 | 11.7 | 272.2 | 23.5 | 295.9 | 136.2 | 62.8 | 317.4 | 234.2 | 539.8 | 265 | 182 | 539.8 | 319.4 | 269.6 | 204.9 | 223.6 | 234.8 | 208.3 | 224.6 | 203.3 | 235.9
1335 | 1190 | -5.6 | 0 | 0 | 259.1 | 202.1 | 195.9 | 196 | 240.3 | 32.9 | 19.8 | 53 | 13.7 | 282.4 | 21 | 295.5 | 136 | 62.6 | 316.3 | 233.5 | 539.2 | 264.7 | 180.7 | 539.5 | 318.8 | 269.5 | 204.6 | 223.4 | 234.5 | 208.1 | 224.3 | 203 | 235.6
1336 | 1191 | -5.6 | 0 | 0 | 259.4 | 201.9 | 195.9 | 195.9 | 239.8 | 32.9 | 19.8 | 52.9 | 14.5 | 273.7 | 22.5 | 295.1 | 135.8 | 62.4 | 315.3 | 233 | 538.5 | 264.5 | 179.4 | 539.1 | 318.3 | 269.4 | 204.3 | 223.2 | 234.2 | 207.8 | 224.1 | 202.8 | 235.4
1337 | 1192 | -5.7 | 0 | 0 | 259.4 | 201.6 | 195.4 | 195.7 | 239.2 | 32.8 | 19.8 | 52.7 | 12.3 | 257 | 25.3 | 294.7 | 135.3 | 62.2 | 313 | 232.3 | 537.7 | 264.4 | 178.2 | 539 | 317.8 | 269.2 | 204.1 | 223 | 234.1 | 207.6 | 223.8 | 202.7 | 235.2
1338 | 1193 | -5.8 | 0 | 0 | 259 | 201.5 | 194.9 | 195.5 | 239.4 | 32.6 | 19.8 | 52.5 | 9.3 | 260.5 | 26.4 | 294.3 | 135 | 61.9 | 312.7 | 231.8 | 537 | 263.7 | 177 | 538.8 | 317.5 | 269.1 | 203.8 | 222.8 | 233.9 | 207.4 | 223.6 | 202.5 | 235
1339 | 1194 | -5.9 | 0 | 0 | 259.3 | 201.2 | 195 | 195.2 | 240.4 | 32.4 | 19.8 | 52.3 | 8.2 | 257.3 | 26 | 293.9 | 134.7 | 61.8 | 312.1 | 231.2 | 536.3 | 263.5 | 175.9 | 538.6 | 316.9 | 269 | 203.6 | 222.6 | 233.6 | 207.1 | 223.4 | 202.3 | 234.7
1340 | 1195 | -6 | 0 | 0 | 259.3 | 201 | 195 | 195 | 241 | 32.3 | 19.9 | 52.1 | 7.6 | 264.5 | 22.6 | 293.4 | 134.3 | 61.6 | 311.2 | 230.6 | 535.6 | 262.7 | 175.1 | 538.5 | 316.3 | 268.8 | 203.4 | 222.4 | 233.4 | 206.9 | 223.1 | 202.1 | 234.5
1341 | 1196 | -6 | 0 | 0 | 259 | 200.8 | 195.1 | 194.5 | 241.5 | 32.3 | 19.9 | 52 | 7.8 | 254.8 | 20 | 293 | 134.1 | 61.4 | 310.4 | 230 | 534.9 | 262.1 | 174.1 | 538 | 315.9 | 268.7 | 203.3 | 222.2 | 233.2 | 206.6 | 222.9 | 201.8 | 234.3
1342 | 1197 | -6.4 | 0 | 0 | 258.2 | 200.5 | 194.8 | 194 | 241.4 | 32.2 | 19.9 | 51.9 | 7.2 | 259.4 | 22.5 | 292.6 | 133.8 | 61.3 | 309.6 | 229.4 | 534.2 | 261.8 | 172.9 | 537.4 | 315.3 | 268.6 | 203.1 | 222 | 232.9 | 206.4 | 222.6 | 201.6 | 234
1343 | 1198 | -6.5 | 0 | 0 | 257.5 | 200.2 | 194.3 | 193.6 | 241.5 | 32.1 | 19.9 | 51.7 | 9.8 | 260.7 | 24.9 | 292.2 | 133.1 | 61 | 308.8 | 228.8 | 533.5 | 260.9 | 171.7 | 537 | 314.8 | 268.4 | 202.9 | 221.8 | 232.6 | 206.1 | 222.3 | 201.4 | 233.8
1344 | 1199 | -6.4 | 0 | 0 | 256.9 | 200 | 193.9 | 193.4 | 241.9 | 32 | 19.9 | 51.6 | 11.8 | 265.6 | 27 | 291.9 | 132.6 | 60.8 | 308.2 | 228.2 | 532.6 | 260.2 | 170.9 | 536.7 | 314.3 | 268.3 | 202.6 | 221.6 | 232.4 | 205.9 | 222.1 | 201.2 | 233.5
1345 | 1200 | -6.5 | 0 | 0 | 256.2 | 199.8 | 193.6 | 193.3 | 241.3 | 31.9 | 19.9 | 51.5 | 8.9 | 253.6 | 29.1 | 291.5 | 132.2 | 60.7 | 307.1 | 227.6 | 531.8 | 258.9 | 169.7 | 535.8 | 313.8 | 268.2 | 202.4 | 221.4 | 232.2 | 205.6 | 221.8 | 200.9 | 233.3
1346 | 1201 | -6.4 | 0 | 0 | 255.8 | 199.6 | 193.4 | 193.1 | 240.2 | 31.8 | 19.9 | 51.4 | 10.3 | 252.8 | 23.9 | 291.1 | 131.8 | 60.6 | 305.3 | 227 | 531.1 | 258.3 | 168.9 | 536 | 313.5 | 268 | 202.3 | 221.1 | 232 | 205.4 | 221.6 | 200.7 | 233
1347 | 1202 | -6.4 | 0 | 0 | 255.5 | 199.5 | 192.9 | 193 | 239.3 | 31.7 | 19.9 | 51.2 | 9 | 250.7 | 21.2 | 290.6 | 132.3 | 60.5 | 304.9 | 226.6 | 530.3 | 257.8 | 168 | 535.8 | 312.8 | 267.9 | 202 | 220.9 | 231.8 | 205.2 | 221.4 | 200.5 | 232.8
1348 | 1203 | -6.5 | 0 | 0 | 255.4 | 199.4 | 192.6 | 192.5 | 239.9 | 31.7 | 19.9 | 51.1 | 9.3 | 270.9 | 17.6 | 290.1 | 132 | 60.4 | 304.2 | 226.1 | 529.6 | 257.2 | 167.2 | 534.9 | 312.2 | 267.8 | 201.8 | 220.7 | 231.5 | 205 | 221.1 | 200.3 | 232.6
1349 | 1204 | -6.4 | 0 | 0 | 255.1 | 199.2 | 192.2 | 192 | 241.2 | 31.7 | 19.9 | 51 | 11.6 | 263.8 | 18 | 289.6 | 131.6 | 60.2 | 303.5 | 225.6 | 528.9 | 256.4 | 166.7 | 534.6 | 311.4 | 267.6 | 201.6 | 220.5 | 231.2 | 204.7 | 220.9 | 200.1 | 232.4
1350 | 1205 | -6.3 | 0 | 0 | 254.9 | 199.2 | 191.7 | 191.8 | 241.2 | 31.8 | 19.9 | 50.9 | 9.5 | 268.7 | 18.6 | 289.1 | 131.2 | 59.9 | 302.8 | 225.1 | 528.2 | 255.7 | 165.8 | 534.3 | 310.8 | 267.5 | 201.4 | 220.3 | 231 | 204.5 | 220.6 | 200 | 232.1
1351 | 1206 | -6.4 | 0 | 0 | 255.1 | 199 | 191.4 | 191.8 | 241.3 | 31.8 | 19.9 | 50.8 | 7.6 | 261.8 | 19.8 | 288.6 | 130.8 | 59.7 | 302.1 | 224.6 | 527.5 | 255.2 | 164.7 | 534.3 | 310.5 | 267.4 | 201.3 | 220.1 | 230.8 | 204.3 | 220.4 | 199.8 | 231.9
1352 | 1207 | -6 | 0 | 0 | 255.1 | 198.7 | 191.1 | 191.8 | 241.4 | 31.7 | 19.9 | 50.8 | 8.1 | 255.6 | 19.9 | 288.2 | 130.3 | 59.6 | 300.7 | 224.1 | 526.8 | 254.8 | 163.7 | 534.3 | 310 | 267.2 | 201.1 | 219.9 | 230.6 | 204 | 220.1 | 199.6 | 231.7
1353 | 1208 | -5.6 | 0 | 0 | 255.4 | 198.4 | 190.7 | 191.6 | 240.2 | 31.5 | 19.9 | 50.8 | 8.6 | 246.4 | 21.1 | 287.8 | 129.9 | 59.4 | 300.3 | 223.6 | 526.1 | 254.2 | 162.8 | 533.9 | 309.4 | 267.1 | 200.9 | 219.6 | 230.4 | 203.8 | 219.9 | 199.4 | 231.5
1354 | 1209 | -5.7 | 0 | 0 | 255.2 | 198.2 | 190.4 | 191.3 | 239.7 | 31.4 | 19.9 | 50.7 | 9.6 | 260 | 18.2 | 287.3 | 129.5 | 59.2 | 299.7 | 223.2 | 525.4 | 253.9 | 162 | 533.3 | 308.8 | 267 | 200.7 | 219.4 | 230.1 | 203.6 | 219.7 | 199.2 | 231.2
1355 | 1210 | -5.9 | 0 | 0 | 254.7 | 198 | 190.2 | 191.1 | 239.6 | 31.2 | 19.9 | 50.6 | 9.5 | 258.1 | 20.5 | 286.7 | 129.3 | 59.1 | 299.2 | 222.8 | 524.8 | 253.4 | 161.3 | 532.6 | 308.4 | 266.8 | 200.5 | 219.2 | 229.8 | 203.3 | 219.5 | 199 | 231
1356 | 1211 | -6 | 0 | 0 | 254.5 | 197.8 | 190 | 190.9 | 238.5 | 31.2 | 19.9 | 50.5 | 10.3 | 264.7 | 20.7 | 286.2 | 129.2 | 58.9 | 298.5 | 222.4 | 524.2 | 253.4 | 160.6 | 531.5 | 307.7 | 266.7 | 200.3 | 218.9 | 229.5 | 203.1 | 219.3 | 198.8 | 230.8
1357 | 1212 | -6 | 0 | 0 | 254.3 | 197.5 | 189.6 | 190.8 | 237.4 | 31.1 | 19.9 | 50.3 | 12.1 | 266.6 | 25.1 | 285.6 | 128.9 | 58.7 | 297.8 | 222 | 523.5 | 253.5 | 159.9 | 531.8 | 307 | 266.6 | 200.1 | 218.6 | 229.3 | 202.9 | 219.1 | 198.6 | 230.6
1358 | 1213 | -6.2 | 0 | 0 | 254 | 197.3 | 189.3 | 190.7 | 236.4 | 30.9 | 19.9 | 50.2 | 11.8 | 264.8 | 25.4 | 285 | 128.3 | 58.6 | 297.6 | 221.7 | 522.9 | 253.1 | 159.1 | 531.9 | 306.7 | 266.4 | 200 | 218.4 | 229.1 | 202.7 | 218.9 | 198.4 | 230.3
1359 | 1214 | -6.2 | 0 | 0 | 253.8 | 197.1 | 189.5 | 190.7 | 235.5 | 30.9 | 19.9 | 50.1 | 13.1 | 269.4 | 24.4 | 284.5 | 127.5 | 58.6 | 297.2 | 221.3 | 522.3 | 251.9 | 158.4 | 531 | 306.4 | 266.3 | 199.9 | 218.2 | 228.9 | 202.4 | 218.7 | 198.1 | 230.1
1360 | 1215 | -6.1 | 0 | 0 | 254 | 196.8 | 189.7 | 190.7 | 235 | 30.8 | 19.9 | 50.1 | 13.3 | 269.5 | 21.4 | 283.9 | 127.2 | 58.6 | 296.6 | 220.8 | 521.8 | 251.7 | 157.6 | 529.5 | 305.9 | 266.1 | 199.7 | 218 | 228.7 | 202.2 | 218.5 | 197.9 | 229.9
1361 | 1216 | -6 | 0 | 0 | 254.2 | 196.7 | 189.9 | 190.5 | 234.7 | 30.7 | 19.9 | 50 | 9.9 | 269.4 | 22.9 | 283.3 | 127.1 | 58.6 | 296.2 | 220.3 | 521.3 | 251.1 | 156.7 | 529.1 | 305.3 | 266 | 199.5 | 217.8 | 228.5 | 202 | 218.2 | 197.7 | 229.7
1362 | 1217 | -5.9 | 0 | 0 | 253.7 | 196.5 | 190.2 | 190.1 | 234 | 30.6 | 19.9 | 49.9 | 8.5 | 268.2 | 23.5 | 282.8 | 127.1 | 58.7 | 295.5 | 220 | 520.7 | 250.1 | 155.8 | 530.5 | 305 | 265.9 | 199.3 | 217.6 | 228.3 | 201.7 | 218 | 197.6 | 229.5
1363 | 1218 | -5.8 | 0 | 0 | 253.8 | 196.3 | 189.7 | 189.6 | 233.4 | 30.5 | 19.9 | 49.9 | 8.3 | 268.8 | 22.8 | 282.2 | 127.5 | 58.8 | 295.1 | 219.5 | 520.1 | 250 | 154.8 | 531 | 304.5 | 265.7 | 199.1 | 217.4 | 228.1 | 201.5 | 217.8 | 197.4 | 229.2
1364 | 1219 | -5.7 | 0 | 0 | 253.8 | 196.1 | 189.1 | 189.3 | 233.9 | 30.3 | 19.9 | 49.9 | 8.4 | 266.5 | 22.4 | 281.7 | 127.5 | 58.9 | 293.8 | 219 | 519.5 | 249.8 | 154 | 531 | 304.3 | 265.6 | 198.8 | 217.2 | 227.9 | 201.3 | 217.6 | 197.1 | 229
1365 | 1220 | -5.6 | 0 | 0 | 253.4 | 196 | 188.6 | 189.1 | 234.1 | 30.2 | 19.9 | 49.8 | 6.9 | 266.3 | 20.8 | 281.2 | 126.7 | 58.9 | 293 | 218.5 | 518.8 | 249.2 | 153.1 | 530.8 | 304.1 | 265.5 | 198.6 | 217 | 227.6 | 201.1 | 217.4 | 196.9 | 228.8
1366 | 1221 | -5.6 | 0 | 0 | 252.8 | 195.8 | 188.2 | 189 | 233.7 | 30.2 | 19.9 | 49.8 | 6.5 | 270.5 | 19.5 | 280.7 | 126.1 | 58.8 | 291.4 | 218.1 | 517.9 | 248.6 | 152.4 | 530.3 | 303.4 | 265.3 | 198.3 | 216.8 | 227.4 | 200.8 | 217.1 | 196.7 | 228.6
1367 | 1222 | -5.6 | 0 | 0 | 252.7 | 195.6 | 187.8 | 188.9 | 233.5 | 30.2 | 19.9 | 49.8 | 7.5 | 272 | 16.4 | 280.2 | 125.8 | 58.7 | 291.1 | 217.6 | 517.1 | 248.4 | 151.8 | 529.6 | 303 | 265.2 | 198.2 | 216.6 | 227.1 | 200.6 | 216.9 | 196.6 | 228.4
1368 | 1223 | -5.7 | 0 | 0 | 252.4 | 195.4 | 187.5 | 188.7 | 233.5 | 30.1 | 19.9 | 49.7 | 8.4 | 262.2 | 14.8 | 279.7 | 125.4 | 58.6 | 290.3 | 217.2 | 516.3 | 248 | 151.1 | 529 | 302.6 | 265.1 | 198 | 216.3 | 226.9 | 200.4 | 216.7 | 196.4 | 228.1
1369 | 1224 | -5.8 | 0 | 0 | 251.6 | 195.3 | 187.2 | 188.6 | 234.8 | 30 | 19.9 | 49.5 | 7.8 | 256.9 | 16.5 | 279.3 | 124.6 | 58.4 | 289.8 | 216.7 | 515.7 | 248.2 | 150.4 | 528.2 | 302.1 | 264.9 | 197.7 | 216.1 | 226.7 | 200.2 | 216.5 | 196.2 | 227.9
1370 | 1225 | -5.7 | 0 | 0 | 250.7 | 195.2 | 186.9 | 188.4 | 235.4 | 29.9 | 19.9 | 49.4 | 7.8 | 247.9 | 16.5 | 278.9 | 124.3 | 58.1 | 288.8 | 216.2 | 514.9 | 247.9 | 150.2 | 526.7 | 301.8 | 264.8 | 197.5 | 215.8 | 226.5 | 200 | 216.3 | 196 | 227.7
1371 | 1226 | -6 | 0 | 0 | 249.8 | 195.1 | 186.6 | 188.3 | 234.9 | 29.8 | 19.9 | 49.2 | 7.6 | 250.2 | 15.1 | 278.4 | 124 | 57.8 | 288.1 | 215.6 | 514.2 | 247.2 | 149.6 | 524.6 | 301.2 | 264.7 | 197.3 | 215.6 | 226.3 | 199.7 | 216.2 | 195.8 | 227.5
1372 | 1227 | -6.3 | 0 | 0 | 249.3 | 194.9 | 186.3 | 188.3 | 233.9 | 29.7 | 19.9 | 49.1 | 10.5 | 249.9 | 15.1 | 277.9 | 124.2 | 57.5 | 287.3 | 215.2 | 513.6 | 247.4 | 149.2 | 526.1 | 300.3 | 264.5 | 197 | 215.3 | 226 | 199.5 | 216 | 195.6 | 227.2
1373 | 1228 | -6.2 | 0 | 0 | 249.1 | 194.7 | 185.9 | 188 | 234.2 | 29.6 | 19.9 | 49 | 12.7 | 264.1 | 14.4 | 277.4 | 123.9 | 57.3 | 286.5 | 214.7 | 513.1 | 247.4 | 148.4 | 525.1 | 299.9 | 264.4 | 196.8 | 215.1 | 225.7 | 199.3 | 215.7 | 195.3 | 227
1374 | 1229 | -6.1 | 0 | 0 | 248.9 | 194.5 | 185.5 | 187.8 | 234.9 | 29.6 | 19.9 | 48.9 | 7.6 | 258.7 | 12.9 | 277 | 123 | 57.2 | 285.5 | 214.3 | 512.4 | 246.8 | 148.1 | 523.6 | 299.5 | 264.2 | 196.6 | 214.9 | 225.5 | 199.1 | 215.5 | 195.2 | 226.8
1375 | 1230 | -6 | 0 | 0 | 248.4 | 194.3 | 185.1 | 187.5 | 235.6 | 29.6 | 19.9 | 48.9 | 7 | 245.3 | 12.8 | 276.4 | 122.6 | 57.1 | 285.1 | 213.8 | 511.7 | 246.3 | 147.5 | 522.5 | 299.1 | 264.1 | 196.4 | 214.7 | 225.3 | 198.8 | 215.2 | 195 | 226.6
1376 | 1231 | -6.1 | 0 | 0 | 248.6 | 194.2 | 184.8 | 187.2 | 235.8 | 29.4 | 19.9 | 48.8 | 15.1 | 234.6 | 10.4 | 275.9 | 122.2 | 57 | 284.8 | 213.4 | 511.1 | 245.6 | 146.6 | 520.8 | 298.8 | 264 | 196.1 | 214.4 | 225.1 | 198.6 | 215 | 194.7 | 226.4
1377 | 1232 | -6.4 | 0 | 0 | 248.4 | 193.9 | 184.6 | 187 | 235.1 | 29.3 | 19.9 | 48.7 | 8.9 | 228.5 | 8.9 | 275.3 | 121.8 | 57 | 284.1 | 213 | 510.4 | 244.6 | 145.9 | 521.7 | 298.3 | 263.8 | 195.9 | 214.2 | 224.9 | 198.4 | 214.7 | 194.5 | 226.1
1378 | 1233 | -6.4 | 0 | 0 | 248.4 | 193.7 | 184.4 | 186.8 | 234.5 | 29.3 | 19.9 | 48.6 | 5.6 | 249.5 | 9.9 | 274.7 | 121.4 | 57 | 283.6 | 212.6 | 509.5 | 243.9 | 145.7 | 521.7 | 297.6 | 263.7 | 195.7 | 214 | 224.7 | 198.2 | 214.5 | 194.2 | 225.9
1379 | 1234 | -6 | 0 | 0 | 248.1 | 193.5 | 184.1 | 186.8 | 234.8 | 29.3 | 20 | 48.7 | 11.1 | 246.4 | 16.9 | 274 | 120.6 | 57 | 283.1 | 212.1 | 508.6 | 242.9 | 145.2 | 520.8 | 297.3 | 263.6 | 195.5 | 213.8 | 224.5 | 197.9 | 214.3 | 193.9 | 225.7
1380 | 1235 | -6 | 0 | 0 | 247.5 | 193.3 | 183.8 | 186.7 | 235 | 29.2 | 20 | 48.7 | 19.5 | 236.2 | 22.8 | 273.1 | 120.4 | 56.9 | 283.1 | 211.7 | 507.7 | 242.6 | 144.6 | 521.2 | 296.5 | 263.4 | 195.4 | 213.6 | 224.2 | 197.7 | 214 | 193.7 | 225.5
1381 | 1236 | -6.3 | 0 | 0 | 247.5 | 193 | 183.6 | 186.5 | 234.7 | 29.2 | 19.9 | 48.7 | 14.7 | 246.9 | 23 | 272.4 | 120.3 | 57 | 283.1 | 211.3 | 506.7 | 241.9 | 144.2 | 521.5 | 296.1 | 263.3 | 195.2 | 213.4 | 224 | 197.5 | 213.8 | 193.4 | 225.2
1382 | 1237 | -6.5 | 0 | 0 | 247.4 | 192.8 | 183.2 | 186.1 | 234.6 | 29.1 | 19.9 | 48.7 | 8.5 | 254.4 | 23.5 | 271.8 | 119.8 | 56.9 | 282.9 | 210.9 | 505.8 | 241.5 | 144 | 521.5 | 295.8 | 263.1 | 194.9 | 213.2 | 223.9 | 197.2 | 213.5 | 193.1 | 225
1383 | 1238 | -6.6 | 0 | 0 | 247.2 | 192.7 | 182.9 | 185.9 | 234.9 | 29 | 20 | 48.8 | 10.1 | 255.7 | 25.3 | 271.1 | 119.4 | 56.7 | 282.8 | 210.4 | 504.9 | 241.5 | 143.7 | 521.6 | 294.8 | 263 | 194.6 | 213 | 223.6 | 197 | 213.3 | 192.9 | 224.8
1384 | 1239 | -6.4 | 0 | 0 | 246.9 | 192.6 | 182.6 | 185.7 | 234.8 | 28.9 | 20 | 48.7 | 16 | 247.1 | 22.8 | 270.2 | 119.2 | 56.6 | 282.6 | 210 | 504 | 241.5 | 143.3 | 521.6 | 294.2 | 262.8 | 194.3 | 212.7 | 223.3 | 196.8 | 213 | 192.7 | 224.6
1385 | 1240 | -6.5 | 0 | 0 | 246.5 | 192.3 | 182.5 | 185.2 | 234.1 | 28.9 | 20 | 48.5 | 23.7 | 248.9 | 22.6 | 269.4 | 118.9 | 56.3 | 282.4 | 209.6 | 503 | 241.2 | 142.8 | 521.3 | 293.8 | 262.7 | 194 | 212.5 | 223 | 196.6 | 212.8 | 192.5 | 224.4
1386 | 1241 | -6.6 | 0 | 0 | 246 | 192 | 182.1 | 184.9 | 234.2 | 28.9 | 20 | 48.3 | 20.5 | 245.2 | 22.5 | 268.4 | 118.5 | 56.2 | 282.2 | 209.2 | 502.2 | 240.7 | 142.6 | 520.5 | 293.6 | 262.6 | 193.6 | 212.2 | 222.8 | 196.4 | 212.6 | 192.3 | 224.2
1387 | 1242 | -6.4 | 0 | 0 | 246.3 | 191.8 | 181.7 | 184.6 | 234.1 | 28.9 | 20 | 48.1 | 18.5 | 246.6 | 24.2 | 267.6 | 118.6 | 56.1 | 281.8 | 208.7 | 501.5 | 240.3 | 142.3 | 520 | 293.1 | 262.4 | 193.3 | 212 | 222.6 | 196.1 | 212.3 | 192.1 | 223.9
1388 | 1243 | -6.3 | 0 | 0 | 246.2 | 191.7 | 181.5 | 184.7 | 233.7 | 28.9 | 20 | 47.8 | 16.6 | 246 | 25.5 | 267.2 | 117.8 | 56.1 | 281.4 | 208.1 | 500.9 | 239.7 | 141.8 | 519 | 292.7 | 262.3 | 193 | 211.7 | 222.3 | 195.9 | 212.1 | 192 | 223.7
1389 | 1244 | -6.2 | 0 | 0 | 246.1 | 191.5 | 181.7 | 184.5 | 232.6 | 28.9 | 20 | 47.6 | 17.1 | 232.2 | 32.4 | 267 | 117.6 | 56 | 280.8 | 207.6 | 500.4 | 239.8 | 141.8 | 519.3 | 292.2 | 262.1 | 192.7 | 211.5 | 222.1 | 195.7 | 211.9 | 191.8 | 223.5
1390 | 1245 | -6.1 | 0 | 0 | 246.3 | 191.3 | 181.7 | 184.2 | 231.9 | 28.8 | 20 | 47.5 | 16.6 | 236.5 | 25.7 | 266.7 | 117.2 | 55.9 | 280.3 | 207.2 | 499.9 | 239.9 | 141.5 | 518.3 | 292 | 262 | 192.4 | 211.3 | 222 | 195.5 | 211.7 | 191.5 | 223.3
1391 | 1246 | -6.2 | 0 | 0 | 246.1 | 191.2 | 181.6 | 183.8 | 232.1 | 28.7 | 20 | 47.3 | 18.5 | 240.9 | 30.4 | 266.4 | 117 | 55.8 | 279.4 | 206.7 | 499.4 | 240.2 | 141.1 | 516.2 | 291.6 | 261.8 | 192.1 | 211.1 | 221.7 | 195.3 | 211.4 | 191.1 | 223.1
1392 | 1247 | -5.3 | 0 | 0 | 245.6 | 191 | 181.3 | 183.4 | 232.3 | 28.6 | 20 | 47.1 | 13.4 | 237.6 | 34.7 | 266.3 | 116.3 | 55.4 | 278.8 | 206.3 | 498.8 | 240.4 | 140.9 | 514.7 | 290.7 | 261.7 | 191.8 | 210.9 | 221.5 | 195.1 | 211.2 | 190.7 | 222.8
1393 | 1248 | -5.1 | 0 | 0 | 245.3 | 190.8 | 180.8 | 183 | 231.7 | 28.4 | 20 | 47 | 13.2 | 230.4 | 30.2 | 266.2 | 116 | 55 | 278.2 | 205.8 | 498.3 | 240 | 140.4 | 514.8 | 290.4 | 261.6 | 191.6 | 210.7 | 221.2 | 194.8 | 211 | 190.5 | 222.6
1394 | 1249 | -5.6 | 0 | 0 | 244.8 | 190.6 | 180.6 | 182.6 | 230.4 | 28.3 | 20 | 47 | 13.7 | 234.6 | 23.7 | 266.1 | 116.2 | 54.6 | 277.7 | 205.3 | 497.9 | 238.7 | 140.1 | 514.3 | 289.9 | 261.4 | 191.1 | 210.5 | 221 | 194.6 | 210.8 | 190.2 | 222.4
1395 | 1250 | -6.2 | 0 | 0 | 244.2 | 190.4 | 180.3 | 182.3 | 229.9 | 28.2 | 20 | 46.9 | 12.8 | 240.4 | 23.9 | 266 | 116.3 | 54.3 | 276.9 | 204.7 | 497.5 | 237.6 | 140 | 514.3 | 289.5 | 261.3 | 190.8 | 210.2 | 220.8 | 194.4 | 210.5 | 189.8 | 222.2
1396 | 1251 | -6.8 | 0 | 0 | 243.4 | 190.1 | 180.1 | 182.2 | 230.2 | 28.1 | 20 | 46.8 | 12.8 | 240.5 | 27.7 | 265.8 | 116.8 | 53.9 | 276.2 | 204.3 | 497.1 | 237.5 | 140.1 | 513.3 | 289.1 | 261.1 | 190.6 | 210 | 220.6 | 194.1 | 210.3 | 189.4 | 222
1397 | 1252 | -6.9 | 0 | 0 | 242.3 | 190 | 179.9 | 181.8 | 229.4 | 28.1 | 20 | 46.7 | 13.7 | 248.9 | 29.8 | 265.5 | 116.1 | 53.7 | 275.4 | 203.8 | 496.6 | 236.7 | 139.9 | 512.2 | 289 | 261 | 190.2 | 209.7 | 220.4 | 193.9 | 210 | 189.1 | 221.7
1398 | 1253 | -6.9 | 0 | 0 | 241.9 | 189.9 | 179.8 | 181.2 | 228.3 | 28.1 | 20 | 46.5 | 12.4 | 234.2 | 27.3 | 265.1 | 115.9 | 53.5 | 274.9 | 203.3 | 496.1 | 236.5 | 139.6 | 511.3 | 288.6 | 260.8 | 190 | 209.5 | 220.1 | 193.7 | 209.7 | 188.9 | 221.5
1399 | 1254 | -6.7 | 0 | 0 | 241.5 | 189.7 | 179.4 | 180.9 | 228.1 | 28.1 | 20 | 46.4 | 14.2 | 234.6 | 28.5 | 264.8 | 116.1 | 53.2 | 274.2 | 202.7 | 495.6 | 236 | 139.4 | 512.3 | 288.2 | 260.7 | 189.6 | 209.3 | 219.9 | 193.4 | 209.5 | 188.6 | 221.3
1400 | 1255 | -6.3 | 0 | 0 | 241.6 | 189.5 | 179.1 | 180.5 | 228.4 | 28.2 | 20 | 46.3 | 11.6 | 241.8 | 33.2 | 264.4 | 115.5 | 53 | 273.7 | 202.2 | 495.1 | 234.9 | 139.2 | 512.1 | 288.1 | 260.6 | 189.3 | 209.1 | 219.7 | 193.2 | 209.2 | 188.3 | 221.1
1401 | 1256 | -6.2 | 0 | 0 | 241.2 | 189.2 | 179 | 180.1 | 228.7 | 28.2 | 20 | 46.2 | 17 | 242.2 | 32.4 | 264 | 115.1 | 52.8 | 273.3 | 201.5 | 494.4 | 234.1 | 138.6 | 511.8 | 287.4 | 260.4 | 189.1 | 208.8 | 219.4 | 193 | 209 | 188 | 220.9
1402 | 1257 | -6.2 | 0 | 0 | 240.5 | 188.7 | 178.9 | 180 | 229.2 | 28.2 | 20 | 46 | 14.8 | 247.7 | 31.3 | 263.6 | 114.7 | 52.7 | 273 | 200.9 | 493.6 | 233.5 | 137.9 | 511.5 | 287.1 | 260.3 | 188.9 | 208.6 | 219.2 | 192.8 | 208.8 | 187.6 | 220.6
1403 | 1258 | -6.3 | 0 | 0 | 240.2 | 188.2 | 178.5 | 180 | 229.6 | 28.1 | 20 | 45.8 | 18 | 249 | 26.8 | 263.2 | 114.1 | 52.5 | 272.6 | 200.4 | 492.9 | 233.1 | 137.4 | 511.4 | 286.9 | 260.1 | 188.7 | 208.5 | 218.9 | 192.5 | 208.5 | 187.3 | 220.4
1404 | 1259 | -6 | 0 | 0 | 239.7 | 187.8 | 178.1 | 179.8 | 229.6 | 28.1 | 20 | 45.7 | 17.5 | 245.2 | 27.7 | 262.8 | 113.3 | 52.4 | 271.9 | 200 | 492.2 | 232.9 | 137.1 | 511.1 | 286.7 | 260 | 188.4 | 208.2 | 218.7 | 192.3 | 208.3 | 187 | 220.2
1405 | 1260 | -6.2 | 0 | 0 | 238.9 | 187.8 | 177.8 | 179.4 | 229.6 | 28.1 | 20 | 45.5 | 17 | 245.3 | 23.5 | 262.3 | 113.3 | 52.3 | 271.3 | 199.5 | 491.5 | 232.2 | 136.9 | 510.8 | 286.1 | 259.8 | 188 | 208 | 218.5 | 192.1 | 208 | 186.7 | 220
1406 | 1261 | -6.4 | 0 | 0 | 238.3 | 187.7 | 177.5 | 179.3 | 229.8 | 28 | 20 | 45.4 | 15.5 | 245.4 | 24.8 | 261.7 | 113.2 | 52.1 | 270.5 | 198.9 | 490.8 | 231.7 | 136.8 | 510.3 | 285.9 | 259.7 | 187.8 | 207.7 | 218.3 | 191.8 | 207.8 | 186.4 | 219.8
1407 | 1262 | -6.3 | 0 | 0 | 237.8 | 187.6 | 177.3 | 179.2 | 229.8 | 28 | 20 | 45.3 | 14.9 | 240 | 29.2 | 261.1 | 113.1 | 52 | 269.9 | 198.3 | 490.1 | 231.4 | 136.2 | 509.5 | 285.6 | 259.5 | 187.4 | 207.3 | 218 | 191.6 | 207.6 | 186.1 | 219.5
1408 | 1263 | -6.4 | 0 | 0 | 237.6 | 187.5 | 177.1 | 179.2 | 229.5 | 27.9 | 20 | 45.2 | 15.3 | 241.5 | 30.1 | 260.6 | 112.8 | 51.9 | 269.3 | 197.9 | 489.5 | 231.3 | 135.9 | 508.9 | 285.2 | 259.4 | 187.1 | 207.1 | 217.8 | 191.3 | 207.3 | 185.8 | 219.3
1409 | 1264 | -6.4 | 0 | 0 | 237.8 | 187.4 | 176.7 | 178.8 | 229.1 | 27.9 | 20 | 45.1 | 12.6 | 239.5 | 30.9 | 260.1 | 112.8 | 51.8 | 268.7 | 197.5 | 488.9 | 231.1 | 136.4 | 508.6 | 284.8 | 259.2 | 186.8 | 206.8 | 217.6 | 191.1 | 207.1 | 185.5 | 219.1
1410 | 1265 | -6.4 | 0 | 0 | 237.9 | 187.2 | 176.5 | 178.6 | 228.9 | 27.9 | 20 | 45 | 16.5 | 239.2 | 28.8 | 259.6 | 112.3 | 51.8 | 268.2 | 197 | 488.4 | 230.7 | 136.4 | 507.6 | 284.4 | 259.1 | 186.5 | 206.5 | 217.4 | 190.9 | 206.9 | 185.3 | 218.9
1411 | 1266 | -6.5 | 0 | 0 | 238 | 187.1 | 176.4 | 178.5 | 228.4 | 28 | 20 | 44.7 | 14.8 | 251.7 | 26.5 | 259.2 | 111.6 | 51.6 | 267.6 | 196.6 | 487.9 | 230 | 136 | 506.6 | 283.7 | 258.9 | 186.1 | 206.3 | 217.1 | 190.7 | 206.7 | 184.9 | 218.7
1412 | 1267 | -6.4 | 0 | 0 | 237.5 | 187 | 176.3 | 178.1 | 227.3 | 28 | 20 | 44.5 | 11.9 | 258.6 | 29.9 | 258.9 | 110.1 | 51.5 | 267.2 | 196.2 | 487.5 | 229 | 135.5 | 505.7 | 283.3 | 258.8 | 185.8 | 206 | 216.9 | 190.4 | 206.5 | 184.6 | 218.4
1413 | 1268 | -6.1 | 0 | 0 | 236.8 | 186.7 | 175.8 | 177.9 | 226.9 | 27.9 | 20 | 44.2 | 16.4 | 258.8 | 36.6 | 258.5 | 110 | 51.4 | 266.4 | 195.7 | 487.1 | 229.4 | 135.1 | 504.8 | 282.8 | 258.6 | 185.5 | 205.7 | 216.7 | 190.2 | 206.3 | 184.4 | 218.2
1414 | 1269 | -6.3 | 0 | 0 | 236.5 | 186.4 | 175.4 | 177.9 | 226.7 | 27.7 | 20 | 43.9 | 16.1 | 254.8 | 38.2 | 258 | 109.6 | 51.3 | 265.9 | 195.2 | 486.6 | 229.2 | 134.5 | 504.5 | 282.6 | 258.5 | 185.1 | 205.4 | 216.4 | 190 | 206 | 184.2 | 218
1415 | 1270 | -5.6 | 0 | 0 | 236.3 | 186.1 | 175.1 | 177.5 | 226.6 | 27.5 | 20 | 43.8 | 12.3 | 258.7 | 35.4 | 257.4 | 109.7 | 51.3 | 265.5 | 194.6 | 486.1 | 229.1 | 134.5 | 505 | 281.9 | 258.3 | 184.9 | 205.2 | 216.2 | 189.8 | 205.8 | 184 | 217.8
1416 | 1271 | -5 | 0 | 0 | 236.2 | 185.8 | 174.9 | 177.1 | 226.4 | 27.5 | 20 | 43.6 | 18.6 | 267 | 35.5 | 257 | 109.6 | 51.2 | 265.4 | 194.1 | 485.4 | 228.6 | 134 | 504.8 | 281.4 | 258.2 | 184.6 | 204.9 | 216 | 189.5 | 205.6 | 183.8 | 217.6
1417 | 1272 | -5.4 | 0 | 0 | 235.9 | 185.5 | 174.7 | 176.9 | 226.4 | 27.6 | 20 | 43.4 | 21 | 272.5 | 33.9 | 256.6 | 109.4 | 51.2 | 264.9 | 193.8 | 484.7 | 227.9 | 133.8 | 504.9 | 281.2 | 258 | 184.4 | 204.5 | 215.8 | 189.3 | 205.4 | 183.6 | 217.4
1418 | 1273 | -5.6 | 0 | 0 | 235.3 | 185.2 | 174.4 | 176.6 | 226.3 | 27.6 | 20 | 43.3 | 21.1 | 266.1 | 32.5 | 256.1 | 109.5 | 51.1 | 264.4 | 193.3 | 484 | 227 | 133.1 | 504 | 280.9 | 257.9 | 184.1 | 204.2 | 215.6 | 189.1 | 205.2 | 183.3 | 217.2
1419 | 1274 | -5.8 | 0 | 0 | 234.7 | 184.9 | 174.1 | 176.3 | 226.3 | 27.6 | 20 | 43.1 | 19.6 | 269.7 | 30.4 | 255.3 | 109.8 | 51 | 264 | 192.8 | 483.3 | 226.6 | 132.5 | 503.5 | 280.3 | 257.7 | 183.8 | 203.9 | 215.4 | 188.8 | 205 | 183.1 | 217
1420 | 1275 | -5.8 | 0 | 0 | 234.2 | 184.7 | 173.8 | 176.1 | 226 | 27.6 | 20.1 | 43 | 17.6 | 266.3 | 27.3 | 254.5 | 109.8 | 51 | 263.7 | 192.5 | 482.6 | 226.6 | 131.9 | 502.8 | 279.8 | 257.6 | 183.6 | 203.7 | 215.2 | 188.6 | 204.7 | 182.8 | 216.7
1421 | 1276 | -5.7 | 0 | 0 | 233.6 | 184.6 | 173.5 | 175.8 | 225.5 | 27.5 | 20.1 | 43 | 18.8 | 265.6 | 25.3 | 253.9 | 109.6 | 51 | 263.4 | 192 | 481.8 | 226.1 | 131.6 | 502.2 | 279.4 | 257.4 | 183.4 | 203.4 | 215 | 188.3 | 204.5 | 182.5 | 216.5
1422 | 1277 | -5.6 | 0 | 0 | 232.9 | 184.5 | 173.5 | 175.6 | 225.2 | 27.5 | 20.1 | 42.9 | 18.4 | 262.9 | 24.2 | 253.5 | 109.7 | 50.9 | 262.9 | 191.6 | 481.1 | 225.5 | 131.7 | 501.5 | 278.6 | 257.3 | 183.3 | 203.2 | 214.8 | 188 | 204.1 | 182.2 | 216.3
1423 | 1278 | -5.7 | 0 | 0 | 232.7 | 184.2 | 173.8 | 175.4 | 225.2 | 27.5 | 20.1 | 42.8 | 14.4 | 245.4 | 26.2 | 253 | 109.5 | 50.8 | 262.3 | 191.2 | 480.2 | 224.6 | 131.4 | 500.9 | 278.2 | 257.1 | 183 | 203 | 214.6 | 187.8 | 203.8 | 182 | 216.1
1424 | 1279 | -5.5 | 0 | 0 | 232.5 | 183.9 | 173.8 | 175.3 | 225 | 27.4 | 20.1 | 42.9 | 7.7 | 242 | 24.3 | 252.6 | 109.5 | 50.7 | 261.9 | 190.8 | 479.5 | 223.8 | 131 | 500.4 | 278 | 257 | 182.8 | 202.8 | 214.4 | 187.6 | 203.5 | 181.7 | 215.9
1425 | 1280 | -5.4 | 0 | 0 | 232.4 | 183.8 | 173.5 | 175.2 | 224.7 | 27.3 | 20.1 | 42.9 | 4.7 | 241.7 | 23.9 | 252.2 | 109.3 | 50.6 | 261.5 | 190.5 | 478.7 | 223.6 | 130.7 | 500 | 277.6 | 256.8 | 182.6 | 202.5 | 214.1 | 187.3 | 203.2 | 181.4 | 215.6
1426 | 1281 | -5.5 | 0 | 0 | 231.6 | 183.6 | 173.1 | 175 | 224.6 | 27.2 | 20.1 | 42.9 | 5.5 | 249.8 | 22.8 | 251.8 | 108.8 | 50.5 | 260.8 | 190.2 | 478 | 223.1 | 130.4 | 500 | 277.2 | 256.7 | 182.3 | 202.3 | 213.9 | 187.1 | 203 | 181.1 | 215.4
1427 | 1282 | -5.5 | 0 | 0 | 230.8 | 183.2 | 172.9 | 174.7 | 224.5 | 27.2 | 20.1 | 42.9 | 10.7 | 221.4 | 23.2 | 251.4 | 108.3 | 50.5 | 260.5 | 189.9 | 477.2 | 222.3 | 130.1 | 499.6 | 276.7 | 256.5 | 182 | 202 | 213.6 | 186.9 | 202.7 | 180.9 | 215.2
1428 | 1283 | -5.5 | 0 | 0 | 230.3 | 182.8 | 172.9 | 174.3 | 224.4 | 27.3 | 20.1 | 43 | 12.4 | 241.9 | 20.7 | 251.1 | 108.1 | 50.4 | 259.6 | 189.5 | 476.6 | 221.7 | 129.9 | 499.1 | 276.4 | 256.4 | 181.7 | 201.7 | 213.4 | 186.6 | 202.5 | 180.6 | 215
1429 | 1284 | -5.7 | 0 | 0 | 229.9 | 182.7 | 172.9 | 173.9 | 224.4 | 27.3 | 20.1 | 43 | 10.4 | 211.6 | 17.1 | 250.7 | 108 | 50.2 | 259 | 189.1 | 475.9 | 221.7 | 129.5 | 498.4 | 275.9 | 256.2 | 181.4 | 201.5 | 213.2 | 186.4 | 202.3 | 180.3 | 214.7
1430 | 1285 | -6.1 | 0 | 0 | 229.3 | 182.7 | 172.8 | 173.5 | 224.1 | 27.2 | 20.1 | 43.1 | 10.3 | 244.4 | 18.3 | 250.3 | 107.8 | 50 | 258.7 | 188.7 | 475.2 | 221.8 | 128.9 | 498.1 | 275.5 | 256 | 181.1 | 201.1 | 213 | 186.1 | 202 | 180.1 | 214.5
1431 | 1286 | -6.3 | 0 | 0 | 228.4 | 182.5 | 172.4 | 173.2 | 223.8 | 27.1 | 20.1 | 43 | 11.3 | 235.2 | 24.4 | 250 | 107.7 | 49.8 | 257.9 | 188.2 | 474.4 | 221.4 | 128.7 | 497.3 | 275 | 255.9 | 180.8 | 200.9 | 212.7 | 185.9 | 201.7 | 179.8 | 214.3
1432 | 1287 | -6.3 | 0 | 0 | 227.8 | 182.2 | 172 | 173 | 223.7 | 27 | 20.1 | 43 | 8.1 | 237.8 | 21.7 | 249.7 | 107.2 | 49.5 | 257.4 | 187.7 | 473.7 | 220.7 | 128.5 | 496.8 | 274.7 | 255.7 | 180.5 | 200.6 | 212.5 | 185.6 | 201.5 | 179.5 | 214.1
1433 | 1288 | -5.6 | 0 | 0 | 227.4 | 181.9 | 171.7 | 172.8 | 223.6 | 26.8 | 20.1 | 43 | 10.1 | 244.2 | 25.2 | 249.5 | 106.8 | 49.3 | 256.9 | 187.2 | 472.9 | 220.1 | 127.8 | 496.1 | 274.3 | 255.6 | 180.3 | 200.4 | 212.3 | 185.4 | 201.2 | 179.2 | 213.9
1434 | 1289 | -5.6 | 0 | 0 | 227.2 | 181.7 | 171.5 | 172.8 | 223.4 | 26.7 | 20.1 | 43 | 11.4 | 243.4 | 26.4 | 249.2 | 106.4 | 49.2 | 256.4 | 186.6 | 472.2 | 219.4 | 127.4 | 495.6 | 274.1 | 255.4 | 180 | 200 | 212 | 185.1 | 201 | 178.9 | 213.6
1435 | 1290 | -5.7 | 0 | 0 | 226.9 | 181.4 | 171.3 | 172.7 | 223.2 | 26.6 | 20.1 | 43 | 13.8 | 252 | 22.1 | 248.8 | 105.7 | 49 | 255.8 | 186.2 | 471.4 | 218.9 | 126.8 | 494.9 | 273.8 | 255.3 | 179.8 | 199.7 | 211.8 | 184.9 | 200.7 | 178.6 | 213.4
1436 | 1291 | -5.4 | 0 | 0 | 226.3 | 181.2 | 170.8 | 172.5 | 223 | 26.6 | 20.1 | 42.9 | 14.5 | 263.9 | 16 | 248.3 | 105.2 | 48.9 | 255.2 | 185.8 | 470.4 | 218.5 | 126.5 | 493.8 | 273.3 | 255.1 | 179.6 | 199.4 | 211.6 | 184.7 | 200.5 | 178.4 | 213.2
1437 | 1292 | -5.6 | 0 | 0 | 225.9 | 181 | 170.5 | 172.2 | 222.8 | 26.5 | 20.1 | 42.8 | 16.7 | 231.6 | 17 | 248 | 105.2 | 48.8 | 254.6 | 185.3 | 469.5 | 217.9 | 126 | 493.1 | 273 | 254.9 | 179.3 | 199.2 | 211.4 | 184.4 | 200.2 | 178.1 | 213
1438 | 1293 | -6 | 0 | 0 | 225 | 180.7 | 170.2 | 172.1 | 222.6 | 26.4 | 20.1 | 42.7 | 17.3 | 239.3 | 17.7 | 247.7 | 105.1 | 48.6 | 254.2 | 184.8 | 468.7 | 217.5 | 125.6 | 492.4 | 272.5 | 254.8 | 179 | 198.9 | 211.3 | 184.2 | 200 | 177.9 | 212.8
1439 | 1294 | -6 | 0 | 0 | 224.3 | 180.3 | 169.6 | 171.8 | 222.4 | 26.3 | 20.1 | 42.7 | 18.5 | 250.9 | 25 | 247.2 | 104.4 | 48.6 | 254.1 | 184.4 | 467.8 | 217.3 | 124.9 | 491.7 | 272.3 | 254.6 | 178.8 | 198.6 | 211.1 | 183.9 | 199.8 | 177.6 | 212.6
1440 | 1295 | -5.8 | 0 | 0 | 223.8 | 180.1 | 169.2 | 171.5 | 222.2 | 26.2 | 20.1 | 42.7 | 14.5 | 239 | 31.1 | 246.8 | 104.1 | 48.5 | 254.1 | 184 | 467.1 | 217.1 | 124.8 | 491.4 | 271.9 | 254.5 | 178.6 | 198.4 | 210.9 | 183.7 | 199.5 | 177.3 | 212.4
1441 | 1296 | -5.8 | 0 | 0 | 223 | 179.9 | 168.8 | 171.2 | 222 | 26.2 | 20.1 | 42.7 | 9.8 | 237.2 | 29 | 246.3 | 104.2 | 48.5 | 254 | 183.6 | 466.4 | 217.1 | 125.4 | 490.6 | 271.5 | 254.3 | 178.4 | 198.1 | 210.7 | 183.5 | 199.2 | 177 | 212.1
1442 | 1297 | -5.9 | 0 | 0 | 222.3 | 179.6 | 168.4 | 171 | 221.7 | 26.2 | 20.1 | 42.6 | 11.6 | 233.7 | 28.6 | 245.9 | 104 | 48.4 | 253.7 | 183.2 | 465.7 | 217 | 125.4 | 490.1 | 271.1 | 254.2 | 178.2 | 197.8 | 210.4 | 183.2 | 198.9 | 176.8 | 211.9
1443 | 1298 | -6.4 | 0 | 0 | 221.9 | 179.5 | 168.1 | 170.6 | 221.5 | 26.2 | 20.1 | 42.5 | 9.7 | 242.8 | 27 | 245.5 | 104.2 | 48.4 | 253.5 | 182.7 | 465 | 216.4 | 124.9 | 489 | 270.8 | 254 | 177.9 | 197.4 | 210.2 | 183 | 198.6 | 176.5 | 211.7
1444 | 1299 | -6.6 | 0 | 0 | 221.4 | 179.4 | 168 | 170.2 | 221.7 | 26.1 | 20.1 | 42.5 | 7 | 234.2 | 23.2 | 245.1 | 103.9 | 48.4 | 253.1 | 182.3 | 464.4 | 215.7 | 124.5 | 487.5 | 270.4 | 253.8 | 177.7 | 197.2 | 209.9 | 182.7 | 198.3 | 176.3 | 211.5
1445 | 1300 | -6.5 | 0 | 0 | 220.8 | 179.2 | 167.7 | 169.9 | 221.5 | 26.2 | 20.1 | 42.6 | 5.9 | 241.7 | 23.4 | 244.7 | 104 | 48.3 | 252.8 | 182 | 463.7 | 215.1 | 124.3 | 486.9 | 269.8 | 253.7 | 177.5 | 196.9 | 209.7 | 182.4 | 198.1 | 176 | 211.2
1446 | 1301 | -6.6 | 0 | 0 | 219.8 | 178.9 | 167.3 | 169.6 | 221.1 | 26.2 | 20.1 | 42.6 | 12.6 | 261.4 | 19.3 | 244.3 | 103.4 | 48.2 | 252.2 | 181.5 | 463 | 215.3 | 124.1 | 486.6 | 269.3 | 253.5 | 177.2 | 196.6 | 209.4 | 182.2 | 197.8 | 175.7 | 211
1447 | 1302 | -6.5 | 0 | 0 | 219.4 | 178.7 | 167.1 | 169.4 | 220.7 | 26.1 | 20.1 | 42.6 | 14.2 | 268.4 | 14.6 | 243.9 | 103.2 | 48.1 | 251.5 | 181.2 | 462.3 | 215.1 | 123.7 | 486 | 269.2 | 253.4 | 177 | 196.4 | 209.2 | 182 | 197.5 | 175.5 | 210.8
1448 | 1303 | -6.3 | 0 | 0 | 218.8 | 178.5 | 166.9 | 169.3 | 220.3 | 26.1 | 20.1 | 42.6 | 11.7 | 264.9 | 16.2 | 243.5 | 103.5 | 47.9 | 250.9 | 181 | 461.7 | 214.5 | 123.2 | 485.2 | 268.8 | 253.2 | 176.8 | 196.1 | 209 | 181.8 | 197.3 | 175.4 | 210.6
1449 | 1304 | -6.3 | 0 | 0 | 218.2 | 178.3 | 167 | 169.1 | 219.9 | 26 | 20.1 | 42.5 | 12.3 | 266.1 | 17.5 | 243 | 103.6 | 47.9 | 250.3 | 180.7 | 461 | 214.1 | 123.2 | 484.3 | 268.2 | 253.1 | 176.5 | 195.9 | 208.8 | 181.5 | 197 | 175.1 | 210.4
1450 | 1305 | -6.5 | 0 | 0 | 217.6 | 178.1 | 166.9 | 168.8 | 219.5 | 25.9 | 20.2 | 42.5 | 6.8 | 261.4 | 15.8 | 242.5 | 103.9 | 47.8 | 250.1 | 180.3 | 460.3 | 214 | 122.7 | 483.5 | 267.9 | 252.9 | 176.3 | 195.6 | 208.6 | 181.3 | 196.8 | 174.9 | 210.2
1451 | 1306 | -6.5 | 0 | 0 | 217.4 | 177.9 | 166.8 | 168.7 | 219.1 | 25.8 | 20.2 | 42.5 | 7.6 | 251 | 16.8 | 241.9 | 103.8 | 47.7 | 249.8 | 179.9 | 459.7 | 213.5 | 122.1 | 482.8 | 267.4 | 252.7 | 176.2 | 195.4 | 208.5 | 181.1 | 196.5 | 174.8 | 210
1452 | 1307 | -6.4 | 0 | 0 | 217.1 | 177.5 | 166.9 | 168.7 | 218.8 | 25.7 | 20.2 | 42.4 | 8.9 | 263.4 | 16.9 | 241.3 | 104.1 | 47.6 | 249.5 | 179.4 | 459.1 | 213.1 | 121.5 | 482 | 267 | 252.6 | 176 | 195.1 | 208.3 | 180.9 | 196.3 | 174.6 | 209.8
1453 | 1308 | -5.9 | 0 | 0 | 216.8 | 177.2 | 166.4 | 168.8 | 218.4 | 25.6 | 20.2 | 42.3 | 10.5 | 270.6 | 19 | 240.6 | 104.3 | 47.4 | 249.1 | 178.9 | 458.6 | 212.4 | 120.8 | 481.3 | 266.7 | 252.4 | 175.7 | 194.9 | 208.1 | 180.6 | 196 | 174.4 | 209.6
1454 | 1309 | -5.6 | 0 | 0 | 216 | 177 | 165.9 | 168.8 | 218 | 25.6 | 20.2 | 42.2 | 10.9 | 256.1 | 19.3 | 240 | 104.3 | 47.4 | 248.6 | 178.7 | 458.1 | 212.3 | 120.7 | 480.8 | 266.3 | 252.3 | 175.5 | 194.6 | 207.9 | 180.4 | 195.7 | 174.2 | 209.4
1455 | 1310 | -5.8 | 0 | 0 | 215.3 | 176.8 | 165.5 | 168.7 | 217.5 | 25.6 | 20.2 | 42.3 | 11 | 259.3 | 24.2 | 239.3 | 104.2 | 47.4 | 248.2 | 178.5 | 457.5 | 211.9 | 120.3 | 480.2 | 265.7 | 252.1 | 175.3 | 194.3 | 207.7 | 180.2 | 195.4 | 174 | 209.1
1456 | 1311 | -5.7 | 0 | 0 | 215.3 | 176.6 | 165.3 | 168.5 | 217.1 | 25.5 | 20.2 | 42.2 | 11.8 | 253.1 | 21.3 | 238.6 | 103.8 | 47.4 | 247.5 | 178.3 | 457.1 | 211.9 | 119.9 | 479.9 | 265.2 | 251.9 | 175 | 194.1 | 207.4 | 180 | 195.2 | 173.7 | 208.9
1457 | 1312 | -5.7 | 0 | 0 | 215.1 | 176.4 | 165.2 | 168.1 | 216.8 | 25.5 | 20.2 | 42.3 | 16.2 | 253.3 | 19.6 | 238 | 103 | 47.3 | 247 | 177.9 | 456.6 | 211.5 | 120.1 | 479.2 | 265 | 251.8 | 174.7 | 193.8 | 207.2 | 179.7 | 194.9 | 173.5 | 208.7
1458 | 1313 | -5.9 | 0 | 0 | 214.5 | 176.2 | 164.8 | 167.9 | 216.5 | 25.4 | 20.2 | 42.2 | 16.9 | 257.7 | 20.3 | 237.1 | 102.8 | 47.1 | 246.4 | 177.4 | 456.1 | 211.3 | 119.8 | 478.9 | 264.8 | 251.6 | 174.5 | 193.5 | 207 | 179.5 | 194.6 | 173.3 | 208.5
1459 | 1314 | -6.1 | 0 | 0 | 213.7 | 176 | 164.4 | 167.9 | 216.3 | 25.3 | 20.2 | 42.1 | 10.6 | 266 | 20.8 | 236 | 102.7 | 46.9 | 245.6 | 176.8 | 455.6 | 210.7 | 119.2 | 478.4 | 264.2 | 251.4 | 174.3 | 193.2 | 206.8 | 179.3 | 194.4 | 173.1 | 208.3
1460 | 1315 | -6 | 0 | 0 | 213.3 | 175.8 | 164 | 167.7 | 216.3 | 25.3 | 20.2 | 42.1 | 11.9 | 263.4 | 17.7 | 235 | 102.4 | 46.6 | 245.4 | 176.4 | 455 | 210.7 | 118.9 | 477.8 | 263.7 | 251.3 | 174.1 | 192.9 | 206.6 | 179.1 | 194.1 | 172.8 | 208.1
1461 | 1316 | -6.1 | 0 | 0 | 213.3 | 175.7 | 163.8 | 167.5 | 216 | 25.2 | 20.2 | 42.1 | 12.7 | 234.4 | 20.1 | 234.2 | 101.5 | 46.5 | 245.2 | 175.9 | 454.4 | 210.8 | 118.7 | 477 | 263.3 | 251.1 | 173.9 | 192.6 | 206.4 | 178.8 | 193.9 | 172.5 | 207.9
1462 | 1317 | -5.9 | 0 | 0 | 212.8 | 175.4 | 163.7 | 167.2 | 215.8 | 25.2 | 20.2 | 42 | 12 | 224.5 | 16.8 | 233.7 | 100.7 | 46.3 | 245.2 | 175.5 | 453.7 | 210.6 | 118.5 | 476.2 | 263.3 | 250.9 | 173.7 | 192.3 | 206.2 | 178.6 | 193.6 | 172.2 | 207.7
1463 | 1318 | -5.4 | 0 | 0 | 212.4 | 175.1 | 163.6 | 166.8 | 215.4 | 25.2 | 20.2 | 42.1 | 7.4 | 254.7 | 12.7 | 233.3 | 100.4 | 46.2 | 244.9 | 175.2 | 453.1 | 210.1 | 118.4 | 475.6 | 262.8 | 250.8 | 173.5 | 192 | 206 | 178.4 | 193.3 | 172 | 207.4
1464 | 1319 | -4.4 | 0 | 0 | 211.8 | 174.8 | 163.3 | 166.7 | 214.9 | 25.1 | 20.2 | 42.1 | 8.4 | 243.6 | 18.1 | 232.9 | 99.8 | 46.1 | 244.6 | 174.8 | 452.5 | 209.6 | 118.3 | 474.8 | 262.6 | 250.6 | 173.3 | 191.7 | 205.8 | 178.1 | 193 | 171.8 | 207.3
1465 | 1320 | -4 | 0 | 0 | 211.6 | 174.7 | 163 | 166.4 | 214.6 | 25 | 20.2 | 42.2 | 9.7 | 252.4 | 21.1 | 232.3 | 99.3 | 46 | 244.2 | 174.5 | 451.8 | 209.3 | 118.1 | 473.7 | 261.8 | 250.5 | 173.1 | 191.5 | 205.6 | 177.9 | 192.7 | 171.5 | 207
1466 | 1321 | -4.6 | 0 | 0 | 211.2 | 174.5 | 162.9 | 166 | 214.2 | 24.9 | 20.2 | 42.1 | 10.8 | 256.2 | 23.9 | 231.4 | 99 | 46 | 244 | 174.2 | 451 | 208.7 | 118.1 | 472.5 | 261.2 | 250.3 | 172.8 | 191.1 | 205.3 | 177.7 | 192.4 | 171.2 | 206.8
1467 | 1322 | -5.7 | 0 | 0 | 210.4 | 174.3 | 162.8 | 165.7 | 213.9 | 24.9 | 20.2 | 42 | 10.8 | 253.2 | 20.7 | 230.7 | 98.9 | 46 | 244 | 173.9 | 450.2 | 208.4 | 117.8 | 471.3 | 260.9 | 250.1 | 172.5 | 190.8 | 205 | 177.4 | 192.1 | 171 | 206.5
1468 | 1323 | -6.1 | 0 | 0 | 209.7 | 174.1 | 162.5 | 165.5 | 213.7 | 24.9 | 20.2 | 42 | 12.3 | 242.1 | 20.4 | 230.1 | 98.5 | 45.9 | 244 | 173.7 | 449.4 | 207.9 | 117.6 | 470.8 | 260.4 | 250 | 172.3 | 190.5 | 204.8 | 177.2 | 191.8 | 170.8 | 206.3
1469 | 1324 | -6.4 | 0 | 0 | 208.9 | 173.9 | 162.2 | 165.1 | 213.7 | 24.9 | 20.2 | 42 | 12.8 | 255 | 18 | 229.6 | 98.4 | 45.7 | 243.9 | 173.3 | 448.6 | 207.5 | 117.3 | 470.1 | 260.3 | 249.8 | 172.1 | 190.2 | 204.6 | 177 | 191.5 | 170.6 | 206.1
1470 | 1325 | -6.3 | 0 | 0 | 208.3 | 173.7 | 161.8 | 164.7 | 213.4 | 24.9 | 20.2 | 42 | 10.8 | 253.8 | 16.8 | 228.6 | 98.2 | 45.6 | 243.8 | 173 | 448 | 207.3 | 117.1 | 469.5 | 259.9 | 249.6 | 171.8 | 190 | 204.4 | 176.7 | 191.2 | 170.4 | 205.9
1471 | 1326 | -6.2 | 0 | 0 | 207.9 | 173.4 | 161.4 | 164.4 | 213.1 | 24.9 | 20.2 | 41.9 | 11.7 | 246.9 | 15.4 | 227.9 | 97.9 | 45.6 | 243.6 | 172.6 | 447.3 | 207 | 116.8 | 469 | 259.5 | 249.5 | 171.6 | 189.8 | 204.1 | 176.5 | 190.8 | 170.1 | 205.6
1472 | 1327 | -6 | 0 | 0 | 207.4 | 173 | 161.2 | 164.1 | 212.6 | 24.9 | 20.2 | 41.7 | 15 | 240.4 | 18.8 | 227.7 | 98 | 45.6 | 243.2 | 172.3 | 446.6 | 206.5 | 116.7 | 468.3 | 258.9 | 249.3 | 171.4 | 189.5 | 203.9 | 176.3 | 190.5 | 170 | 205.5
1473 | 1328 | -5.1 | 0 | 0 | 207 | 172.7 | 161.2 | 164 | 212.2 | 24.9 | 20.2 | 41.6 | 17.4 | 256.1 | 20.2 | 227.5 | 97.6 | 45.5 | 242.9 | 172.1 | 445.9 | 205.8 | 116.8 | 467.7 | 258.3 | 249.1 | 171.2 | 189.3 | 203.6 | 176 | 190.2 | 169.8 | 205.3
1474 | 1329 | -5.4 | 0 | 0 | 206.6 | 172.5 | 161 | 163.9 | 211.9 | 24.9 | 20.2 | 41.4 | 12.6 | 254.2 | 21.7 | 227.1 | 97.9 | 45.5 | 242.4 | 171.9 | 445.3 | 205.5 | 116.7 | 467.2 | 257.8 | 248.9 | 171 | 189.1 | 203.4 | 175.8 | 190 | 169.6 | 205
1475 | 1330 | -6.1 | 0 | 0 | 206 | 172.3 | 160.6 | 163.7 | 211.6 | 24.9 | 20.2 | 41.3 | 8.8 | 243.3 | 23.3 | 226.5 | 97.7 | 45.4 | 241.8 | 171.8 | 444.6 | 205.2 | 116.5 | 466.6 | 257.4 | 248.8 | 170.8 | 188.8 | 203.2 | 175.6 | 189.7 | 169.3 | 204.8
1476 | 1331 | -6.1 | 0 | 0 | 205.4 | 172 | 160.2 | 163.3 | 211.2 | 24.9 | 20.2 | 41.3 | 9.2 | 247.2 | 26.4 | 226 | 97.2 | 45.4 | 241.6 | 171.5 | 444 | 205.2 | 116.3 | 465.7 | 256.8 | 248.6 | 170.6 | 188.5 | 202.9 | 175.3 | 189.4 | 169 | 204.6
1477 | 1332 | -5.2 | 0 | 0 | 204.8 | 171.7 | 159.8 | 163 | 210.8 | 25 | 20.2 | 41.2 | 10 | 258.8 | 26.7 | 225.7 | 97 | 45.5 | 241.3 | 171.2 | 443.5 | 204.7 | 116 | 465.5 | 256.3 | 248.4 | 170.4 | 188.2 | 202.7 | 175.1 | 189.2 | 168.9 | 204.3
1478 | 1333 | -5 | 0 | 0 | 204.3 | 171.4 | 159.9 | 162.9 | 210.2 | 25.1 | 20.2 | 41.3 | 11.4 | 247.9 | 27.7 | 225.6 | 97.1 | 45.6 | 241 | 170.8 | 442.8 | 204.2 | 115.9 | 465.4 | 255.9 | 248.3 | 170.2 | 187.9 | 202.5 | 174.9 | 188.9 | 168.7 | 204.1
1479 | 1334 | -5.8 | 0 | 0 | 203.8 | 171 | 160 | 162.8 | 209.4 | 25 | 20.2 | 41.3 | 11.7 | 257.4 | 24.4 | 225.4 | 96.6 | 45.7 | 240.7 | 170.4 | 442.2 | 204.2 | 115.9 | 465 | 255.5 | 248.1 | 170 | 187.8 | 202.3 | 174.7 | 188.7 | 168.5 | 203.9
1480 | 1335 | -5.8 | 0 | 0 | 203.5 | 170.6 | 159.9 | 162.6 | 209.1 | 25 | 20.2 | 41.3 | 9.2 | 250.7 | 28.1 | 225.2 | 96.1 | 45.7 | 240.4 | 170.1 | 441.6 | 204 | 116 | 464.6 | 255.2 | 247.9 | 169.8 | 187.6 | 202.1 | 174.4 | 188.5 | 168.3 | 203.7
1481 | 1336 | -5.1 | 0 | 0 | 203 | 170.4 | 159.6 | 162.5 | 208.7 | 25.1 | 20.2 | 41.3 | 10.5 | 257.3 | 26.8 | 225 | 96 | 45.8 | 240.3 | 169.9 | 441 | 203.6 | 116.1 | 464.3 | 254.7 | 247.7 | 169.6 | 187.4 | 201.9 | 174.2 | 188.3 | 168 | 203.5
1482 | 1337 | -5.6 | 0 | 0 | 202.4 | 170.2 | 159.3 | 162.3 | 208.4 | 25.1 | 20.2 | 41.2 | 11.9 | 258.2 | 23.9 | 224.9 | 95.9 | 45.8 | 240.1 | 169.6 | 440.4 | 203.4 | 115.4 | 463.8 | 254.7 | 247.6 | 169.4 | 187.2 | 201.7 | 174 | 188 | 167.8 | 203.3
1483 | 1338 | -6 | 0 | 0 | 202.2 | 169.9 | 158.9 | 162.1 | 208.1 | 25.1 | 20.2 | 41.2 | 11.4 | 252.3 | 23.4 | 224.6 | 95.8 | 45.7 | 239.6 | 169.3 | 439.8 | 203.1 | 115 | 463.2 | 254.1 | 247.4 | 169.2 | 187 | 201.4 | 173.8 | 187.8 | 167.5 | 203
1484 | 1339 | -6.2 | 0 | 0 | 202 | 169.8 | 158.7 | 161.8 | 207.8 | 25 | 20.3 | 41.1 | 12.2 | 246.3 | 25.3 | 224.2 | 95.9 | 45.7 | 239.3 | 169.1 | 439.2 | 203.2 | 115.1 | 462.7 | 253.6 | 247.2 | 169 | 186.8 | 201.2 | 173.5 | 187.5 | 167.3 | 202.8
1485 | 1340 | -6 | 0 | 0 | 201.8 | 169.7 | 158.4 | 161.7 | 207.4 | 25 | 20.3 | 41 | 14.1 | 240.1 | 23.9 | 223.6 | 96.2 | 45.6 | 239 | 168.9 | 438.6 | 202.8 | 115.2 | 462.3 | 253.4 | 247.1 | 168.8 | 186.5 | 201 | 173.3 | 187.3 | 167.2 | 202.6
1486 | 1341 | -6.1 | 0 | 0 | 201.8 | 169.6 | 158.2 | 161.5 | 206.9 | 25.1 | 20.3 | 41 | 24.7 | 249.5 | 18.9 | 223 | 95.8 | 45.5 | 238.7 | 168.7 | 437.9 | 202.3 | 115.3 | 461.8 | 252.9 | 246.9 | 168.5 | 186.3 | 200.8 | 173.1 | 187.1 | 166.9 | 202.4
1487 | 1342 | -6.1 | 0 | 0 | 201.1 | 169.4 | 158 | 161.4 | 206.3 | 25.2 | 20.3 | 41 | 19.8 | 250.4 | 14.4 | 222.5 | 95.2 | 45.5 | 238.6 | 168.5 | 437.3 | 201.8 | 115 | 461.3 | 252.5 | 246.7 | 168.3 | 186.1 | 200.6 | 172.8 | 186.9 | 166.7 | 202.2
1488 | 1343 | -6.1 | 0 | 0 | 200.6 | 169.1 | 158 | 161 | 206 | 25.1 | 20.3 | 40.9 | 10.3 | 242 | 24.4 | 222.1 | 95.2 | 45.5 | 238.3 | 168.3 | 436.7 | 201.6 | 114.9 | 460.8 | 252.1 | 246.6 | 168.2 | 185.8 | 200.4 | 172.6 | 186.6 | 166.5 | 202
1489 | 1344 | -6 | 0 | 0 | 200.2 | 168.9 | 157.8 | 160.8 | 205.9 | 25.1 | 20.3 | 41 | 13.7 | 242.9 | 29.9 | 221.8 | 95.2 | 45.6 | 238.1 | 168.1 | 436.1 | 201.3 | 114.4 | 459.6 | 251.8 | 246.4 | 168 | 185.6 | 200.2 | 172.4 | 186.4 | 166.3 | 201.8
1490 | 1345 | -6 | 0 | 0 | 199.5 | 168.8 | 157.6 | 160.6 | 205.7 | 25.1 | 20.3 | 40.9 | 14.2 | 244.9 | 27.3 | 221.7 | 94.8 | 45.5 | 237.7 | 167.7 | 435.5 | 201 | 113.8 | 458.3 | 251.2 | 246.2 | 167.8 | 185.2 | 200.1 | 172.2 | 186.2 | 166.1 | 201.6
1491 | 1346 | -6.2 | 0 | 0 | 198.9 | 168.5 | 157.6 | 160.4 | 205.4 | 24.9 | 20.3 | 40.9 | 10 | 246 | 28.2 | 221.6 | 94.8 | 45.4 | 237.3 | 167.3 | 435 | 200.5 | 113.3 | 458 | 250.7 | 246 | 167.7 | 185 | 199.9 | 172 | 186 | 165.8 | 201.4
1492 | 1347 | -6.1 | 0 | 0 | 198.6 | 168.2 | 157.3 | 160.3 | 205.1 | 24.8 | 20.3 | 40.9 | 12.6 | 240.5 | 29.3 | 221.5 | 94.7 | 45.3 | 236.9 | 166.9 | 434.4 | 200.1 | 113.1 | 457.7 | 250.4 | 245.9 | 167.5 | 184.8 | 199.7 | 171.7 | 185.7 | 165.5 | 201.1
1493 | 1348 | -6.3 | 0 | 0 | 198.4 | 167.9 | 157 | 160.1 | 204.9 | 24.7 | 20.3 | 40.9 | 12.8 | 241.2 | 28.6 | 221.5 | 94.5 | 45.2 | 236.3 | 166.5 | 433.8 | 199.5 | 112.8 | 457.6 | 250.1 | 245.7 | 167.2 | 184.6 | 199.5 | 171.5 | 185.5 | 165.3 | 200.9
1494 | 1349 | -6.3 | 0 | 0 | 197.7 | 167.9 | 156.6 | 159.7 | 204.4 | 24.6 | 20.3 | 40.9 | 9.4 | 237.8 | 22.1 | 221.4 | 94 | 45.2 | 235.9 | 166.2 | 433.1 | 199.1 | 112.8 | 457.6 | 249.7 | 245.5 | 167 | 184.4 | 199.2 | 171.3 | 185.2 | 165.2 | 200.7
1495 | 1350 | -6 | 0 | 0 | 197.2 | 167.7 | 156.6 | 159.4 | 204.1 | 24.6 | 20.3 | 40.9 | 8.5 | 238.3 | 23 | 221.2 | 94 | 45.2 | 235.7 | 166 | 432.2 | 198.3 | 112.6 | 457.6 | 249.6 | 245.4 | 166.7 | 184.2 | 199 | 171.1 | 185 | 165 | 200.5
1496 | 1351 | -5.6 | 0 | 0 | 196.9 | 167.5 | 156.6 | 159.3 | 203.9 | 24.5 | 20.3 | 40.9 | 11.5 | 238.1 | 21.8 | 220.9 | 93.5 | 45.1 | 235.5 | 165.7 | 431.4 | 197.7 | 112.9 | 457.3 | 248.9 | 245.2 | 166.4 | 184 | 198.7 | 170.8 | 184.7 | 164.9 | 200.3
1497 | 1352 | -5.8 | 0 | 0 | 196.8 | 167.4 | 156.2 | 159.3 | 203.6 | 24.4 | 20.3 | 41 | 11.6 | 246 | 20.2 | 220.5 | 93 | 45 | 235.4 | 165.4 | 430.7 | 197.3 | 112.7 | 456.8 | 248.6 | 245 | 166.2 | 183.8 | 198.5 | 170.6 | 184.5 | 164.7 | 200.1
1498 | 1353 | -5.9 | 0 | 0 | 196.6 | 167.4 | 156.2 | 159.1 | 203.3 | 24.4 | 20.3 | 41 | 8.9 | 242.9 | 20 | 220.1 | 92.8 | 44.9 | 235.1 | 165.2 | 430 | 197 | 112.5 | 456.4 | 248.2 | 244.8 | 166 | 183.6 | 198.3 | 170.4 | 184.3 | 164.6 | 199.9
1499 | 1354 | -5.8 | 0 | 0 | 196.2 | 167.3 | 156.1 | 158.8 | 203 | 24.3 | 20.3 | 41 | 7 | 256.6 | 19.3 | 219.8 | 93.4 | 44.8 | 234.8 | 165 | 429.3 | 197.1 | 112.3 | 456 | 248 | 244.7 | 165.8 | 183.4 | 198.1 | 170.2 | 184.1 | 164.4 | 199.7
1500 | 1355 | -5.8 | 0 | 0 | 195.7 | 167.2 | 155.8 | 158.5 | 202.7 | 24.3 | 20.3 | 40.9 | 7.5 | 253 | 20.1 | 219.4 | 93.2 | 44.6 | 234.7 | 164.8 | 428.7 | 197.1 | 111.9 | 454.9 | 247.7 | 244.5 | 165.6 | 183.1 | 197.9 | 170 | 183.9 | 164.2 | 199.5
1501 | 1356 | -6 | 0 | 0 | 195.3 | 167 | 155.6 | 158.2 | 202.4 | 24.3 | 20.3 | 40.7 | 9.8 | 260.8 | 18.7 | 218.6 | 93 | 44.6 | 234.6 | 164.5 | 428.2 | 196.3 | 111.9 | 454.4 | 247 | 244.3 | 165.4 | 183 | 197.7 | 169.7 | 183.7 | 163.9 | 199.2
1502 | 1357 | -6.4 | 0 | 0 | 195 | 166.7 | 155.6 | 157.9 | 202.2 | 24.3 | 20.3 | 40.6 | 10.7 | 264.4 | 20.1 | 218 | 92.9 | 44.5 | 234.3 | 164.3 | 427.5 | 195.7 | 111.7 | 453.6 | 246.7 | 244.1 | 165.2 | 182.8 | 197.5 | 169.5 | 183.5 | 163.6 | 199
1503 | 1358 | -6.4 | 0 | 0 | 194.4 | 166.3 | 155.5 | 157.8 | 201.9 | 24.2 | 20.3 | 40.6 | 8 | 245.2 | 19.4 | 217.9 | 93 | 44.3 | 233.7 | 164 | 427 | 195.2 | 111.5 | 452.8 | 246.4 | 244 | 165 | 182.6 | 197.4 | 169.3 | 183.3 | 163.2 | 198.8
1504 | 1359 | -6.2 | 0 | 0 | 193.8 | 166.1 | 155.5 | 157.6 | 201.6 | 24.2 | 20.3 | 40.7 | 10.4 | 246.3 | 24 | 217.8 | 92.8 | 44.1 | 233.1 | 163.6 | 426.4 | 194.7 | 111.5 | 452.3 | 245.8 | 243.8 | 164.8 | 182.3 | 197.1 | 169 | 183 | 163 | 198.6
1505 | 1360 | -6.2 | 0 | 0 | 193.2 | 165.9 | 155.2 | 157.5 | 201.2 | 24.3 | 20.3 | 40.6 | 16.2 | 249.4 | 26.6 | 217.8 | 92.5 | 43.9 | 232.5 | 163.2 | 426 | 194.2 | 111.5 | 451.6 | 245.4 | 243.6 | 164.6 | 182.1 | 196.9 | 168.9 | 182.8 | 163 | 198.4
1506 | 1361 | -6.2 | 0 | 0 | 193 | 165.8 | 154.8 | 157.3 | 200.6 | 24.3 | 20.3 | 40.5 | 15.7 | 251.3 | 25.7 | 217.7 | 92.3 | 43.7 | 231.8 | 162.9 | 425.6 | 193 | 111.3 | 451.4 | 244.9 | 243.5 | 164.4 | 181.9 | 196.6 | 168.7 | 182.6 | 162.8 | 198.3
1507 | 1362 | -6 | 0 | 0 | 192.8 | 165.6 | 154.5 | 157.1 | 200.6 | 24.3 | 20.3 | 40.5 | 13.7 | 247.6 | 27.5 | 217.5 | 92.2 | 43.6 | 231.2 | 162.6 | 425 | 192.7 | 111.1 | 450.8 | 244.4 | 243.3 | 164.2 | 181.6 | 196.4 | 168.5 | 182.4 | 162.6 | 198.1
1508 | 1363 | -6 | 0 | 0 | 192.6 | 165.5 | 154.2 | 157 | 200.3 | 24.3 | 20.3 | 40.4 | 11.2 | 246.8 | 25.7 | 217.5 | 92.2 | 43.6 | 230.6 | 162.2 | 424.4 | 192.7 | 111.3 | 450 | 244.2 | 243.1 | 164 | 181.4 | 196.2 | 168.2 | 182.2 | 162.5 | 197.8
1509 | 1364 | -6.1 | 0 | 0 | 192.3 | 165.4 | 153.9 | 156.8 | 199.4 | 24.3 | 20.3 | 40.3 | 8.9 | 245.7 | 25.4 | 217.2 | 92.2 | 43.5 | 230 | 161.9 | 423.8 | 192.7 | 111 | 449.1 | 244.1 | 242.9 | 163.8 | 181.3 | 196 | 168 | 182 | 162.3 | 197.7
1510 | 1365 | -6.3 | 0 | 0 | 192 | 165.2 | 153.6 | 156.6 | 198.5 | 24.3 | 20.3 | 40.2 | 11.7 | 232.8 | 24.6 | 216.8 | 92.3 | 43.4 | 229.5 | 161.7 | 423.1 | 192.5 | 110.8 | 448.6 | 243.5 | 242.8 | 163.6 | 181.1 | 195.8 | 167.8 | 181.8 | 162.2 | 197.5
1511 | 1366 | -6.2 | 0 | 0 | 191.7 | 164.8 | 153.4 | 156.5 | 198.4 | 24.2 | 20.3 | 40.1 | 12.1 | 236.1 | 21.1 | 216.6 | 92.2 | 43.4 | 228.9 | 161.4 | 422.5 | 192.2 | 110.6 | 447.9 | 243.1 | 242.6 | 163.5 | 180.9 | 195.5 | 167.6 | 181.6 | 162 | 197.3
1512 | 1367 | -6.2 | 0 | 0 | 191.5 | 164.5 | 153.5 | 156.5 | 198.4 | 24.2 | 20.3 | 40 | 13.2 | 219.8 | 21.3 | 216.3 | 91.9 | 43.3 | 228.7 | 161.2 | 421.9 | 192.1 | 110.2 | 447.8 | 242.7 | 242.4 | 163.3 | 180.7 | 195.3 | 167.4 | 181.4 | 161.8 | 197.1
1513 | 1368 | -6.1 | 0 | 0 | 191.5 | 164.3 | 153.2 | 156.2 | 198.5 | 24.2 | 20.3 | 40 | 8.9 | 238.1 | 21.2 | 216.1 | 91.7 | 43.3 | 228.4 | 160.9 | 421.2 | 191.7 | 110 | 447.3 | 242.3 | 242.2 | 163.1 | 180.5 | 195.2 | 167.2 | 181.2 | 161.5 | 196.9
1514 | 1369 | -6.3 | 0 | 0 | 191.5 | 164.1 | 152.9 | 156.1 | 198.4 | 24.2 | 20.3 | 40 | 16.4 | 243.3 | 28.5 | 215.7 | 91.8 | 43.2 | 228.2 | 160.5 | 420.3 | 191.3 | 109.6 | 446.7 | 242 | 242.1 | 162.9 | 180.3 | 195 | 167 | 181 | 161.3 | 196.7
1515 | 1370 | -6.4 | 0 | 0 | 191.5 | 163.8 | 152.6 | 156.1 | 198.3 | 24.1 | 20.3 | 40 | 19.7 | 243.6 | 31.5 | 215.3 | 91.9 | 43.2 | 228 | 160.3 | 419.4 | 190.9 | 109.2 | 446.1 | 241.7 | 241.9 | 162.7 | 180 | 194.8 | 166.8 | 180.8 | 161.1 | 196.5
1516 | 1371 | -6.4 | 0 | 0 | 191.1 | 163.5 | 152.3 | 155.9 | 198.2 | 24 | 20.3 | 39.9 | 20.5 | 240.4 | 32.2 | 214.9 | 92.2 | 43.2 | 227.2 | 160 | 418.6 | 190.3 | 109 | 445.3 | 241.1 | 241.7 | 162.5 | 179.8 | 194.6 | 166.6 | 180.6 | 161 | 196.3
1517 | 1372 | -6.3 | 0 | 0 | 190.6 | 163.3 | 152.1 | 155.7 | 198 | 24 | 20.3 | 39.9 | 23.2 | 216.2 | 28.2 | 214.6 | 91.9 | 43.3 | 227 | 159.7 | 417.7 | 189.9 | 108.9 | 444.6 | 240.6 | 241.5 | 162.3 | 179.6 | 194.4 | 166.4 | 180.4 | 160.8 | 196.1
1518 | 1373 | -6.4 | 0 | 0 | 190.1 | 163.3 | 151.9 | 155.5 | 197.8 | 23.9 | 20.3 | 39.7 | 22.3 | 240.6 | 26.7 | 214.3 | 91.8 | 43.3 | 226.8 | 159.4 | 416.9 | 189.7 | 108.7 | 444.4 | 240.1 | 241.4 | 162.1 | 179.4 | 194.2 | 166.2 | 180.2 | 160.6 | 195.9
1519 | 1374 | -6.6 | 0 | 0 | 189.7 | 163.3 | 151.6 | 155.4 | 197.6 | 23.9 | 20.3 | 39.6 | 14.6 | 238 | 31.6 | 214 | 92 | 43.3 | 226.6 | 159.2 | 416.1 | 189.4 | 108.5 | 444.2 | 239.9 | 241.2 | 161.9 | 179.2 | 193.9 | 166 | 180 | 160.4 | 195.7
1520 | 1375 | -6.9 | 0 | 0 | 189.5 | 163.1 | 151.3 | 155.3 | 197.4 | 23.9 | 20.3 | 39.6 | 14.3 | 213.5 | 23.4 | 213.8 | 91.5 | 43.2 | 226.2 | 158.9 | 415.3 | 188.8 | 108.1 | 443.7 | 239.8 | 241 | 161.7 | 179 | 193.8 | 165.8 | 179.8 | 160.2 | 195.5
1521 | 1376 | -6.9 | 0 | 0 | 189.5 | 162.7 | 151 | 155 | 197.2 | 24 | 20.3 | 39.5 | 13.4 | 244.8 | 27.1 | 213.5 | 91.6 | 43 | 225.6 | 158.6 | 414.6 | 188.4 | 107.8 | 443.4 | 239.3 | 240.8 | 161.5 | 178.9 | 193.5 | 165.6 | 179.6 | 160 | 195.3
1522 | 1377 | -6.8 | 0 | 0 | 189.2 | 162.6 | 150.8 | 155 | 197.2 | 24 | 20.4 | 39.4 | 13.1 | 248.7 | 32.6 | 213.3 | 91.3 | 42.7 | 225 | 158.4 | 413.9 | 188.5 | 107.8 | 442.9 | 238.7 | 240.7 | 161.3 | 178.7 | 193.3 | 165.3 | 179.3 | 159.8 | 195
1523 | 1378 | -6.8 | 0 | 0 | 188.7 | 162.5 | 150.7 | 154.8 | 197.1 | 24 | 20.4 | 39.3 | 18.2 | 256 | 31.5 | 213.2 | 90.8 | 42.5 | 224.6 | 158.1 | 413.2 | 188.7 | 107.6 | 442.9 | 238.4 | 240.5 | 161.2 | 178.5 | 193.1 | 165.1 | 179 | 159.6 | 194.8
1524 | 1379 | -6.7 | 0 | 0 | 188.3 | 162.4 | 150.5 | 154.7 | 197 | 23.9 | 20.4 | 39.2 | 13.5 | 249.2 | 30.8 | 213 | 90.5 | 42.4 | 224.1 | 157.7 | 412.5 | 188.1 | 107.8 | 442.7 | 238.2 | 240.3 | 161 | 178.3 | 192.9 | 165 | 178.8 | 159.4 | 194.6
1525 | 1380 | -6.6 | 0 | 0 | 188.1 | 162.2 | 150.2 | 154.5 | 196.8 | 23.8 | 20.4 | 39.2 | 11.5 | 259.5 | 35.1 | 212.1 | 90.4 | 42.3 | 223.8 | 157.4 | 411.6 | 187.9 | 107.9 | 441.9 | 237.6 | 240.1 | 160.8 | 178.1 | 192.7 | 164.8 | 178.6 | 159.2 | 194.4
1526 | 1381 | -6.4 | 0 | 0 | 187.9 | 162.1 | 150.1 | 154.3 | 196.6 | 23.9 | 20.4 | 39.2 | 12.8 | 258.7 | 35.7 | 211.3 | 90.3 | 42.2 | 223.6 | 157 | 410.7 | 187.3 | 107.1 | 441 | 237.1 | 240 | 160.6 | 177.9 | 192.5 | 164.6 | 178.4 | 159 | 194.2
1527 | 1382 | -6.1 | 0 | 0 | 187.7 | 162 | 150 | 154 | 196.4 | 23.9 | 20.4 | 39.1 | 15.3 | 261.1 | 31.9 | 210.6 | 89.8 | 42.1 | 223.3 | 156.7 | 409.8 | 187.1 | 106.8 | 440.1 | 237.1 | 239.8 | 160.4 | 177.7 | 192.2 | 164.4 | 178.2 | 158.8 | 194
1528 | 1383 | -6.1 | 0 | 0 | 187.5 | 161.7 | 149.7 | 153.9 | 196.2 | 23.9 | 20.4 | 38.9 | 14.5 | 264.6 | 32.7 | 210.1 | 89.5 | 42.2 | 223.2 | 156.4 | 409 | 186.6 | 106.5 | 439.9 | 236.5 | 239.6 | 160.2 | 177.5 | 192 | 164.2 | 178 | 158.6 | 193.8
1529 | 1384 | -5.8 | 0 | 0 | 187.1 | 161.4 | 149.6 | 153.7 | 196 | 24 | 20.4 | 38.8 | 13.8 | 260.5 | 31.1 | 209.6 | 89.4 | 42.2 | 223 | 156.1 | 408.2 | 186.3 | 106.3 | 439.5 | 236.4 | 239.4 | 160 | 177.4 | 191.9 | 164 | 177.8 | 158.4 | 193.6
1530 | 1385 | -5.5 | 0 | 0 | 186.9 | 161.2 | 149.5 | 153.4 | 195.7 | 23.9 | 20.4 | 38.8 | 14.3 | 261.4 | 30.7 | 209.3 | 89 | 42.3 | 222.7 | 155.9 | 407.6 | 186.3 | 106.1 | 438.9 | 236.1 | 239.3 | 159.8 | 177.3 | 191.7 | 163.7 | 177.6 | 158.2 | 193.4
1531 | 1386 | -5.5 | 0 | 0 | 186.8 | 161.2 | 149.3 | 153.1 | 195.7 | 23.9 | 20.4 | 38.7 | 12.8 | 260.7 | 28.5 | 209.1 | 88.8 | 42.3 | 222.4 | 155.7 | 407 | 185.8 | 105.9 | 438.3 | 235.6 | 239.1 | 159.6 | 177.1 | 191.5 | 163.6 | 177.4 | 158 | 193.2
1532 | 1387 | -5.7 | 0 | 0 | 186.4 | 161.1 | 149.1 | 153.1 | 195.6 | 23.9 | 20.4 | 38.8 | 9.6 | 259.8 | 25.7 | 208.8 | 88.5 | 42.3 | 221.8 | 155.4 | 406.3 | 185.5 | 105.6 | 437.6 | 235 | 238.9 | 159.4 | 176.9 | 191.3 | 163.4 | 177.2 | 157.8 | 193
1533 | 1388 | -5.6 | 0 | 0 | 186 | 160.9 | 148.7 | 153 | 195.3 | 24 | 20.4 | 38.8 | 9 | 260.8 | 25.7 | 208.6 | 88.5 | 42.2 | 221.4 | 155.1 | 405.6 | 185.5 | 105.4 | 437.1 | 234.7 | 238.7 | 159.2 | 176.7 | 191.1 | 163.1 | 176.9 | 157.6 | 192.8
1534 | 1389 | -5.8 | 0 | 0 | 185.7 | 160.6 | 148.4 | 152.9 | 195.1 | 24 | 20.4 | 38.8 | 9.2 | 250.3 | 24.9 | 208.4 | 88.2 | 42.2 | 221 | 155 | 404.9 | 185 | 105.3 | 436.6 | 234.4 | 238.6 | 159 | 176.5 | 190.8 | 162.9 | 176.7 | 157.5 | 192.6
1535 | 1390 | -6 | 0 | 0 | 185.5 | 160.3 | 148.2 | 152.8 | 194.9 | 24.1 | 20.4 | 38.8 | 9 | 257 | 22.6 | 208.2 | 87.7 | 42.1 | 220.6 | 154.7 | 404.2 | 184.5 | 105.1 | 436.4 | 234 | 238.4 | 158.8 | 176.3 | 190.6 | 162.8 | 176.5 | 157.4 | 192.4
1536 | 1391 | -6.2 | 0 | 0 | 185.4 | 160 | 148 | 152.7 | 194.7 | 24.2 | 20.4 | 38.9 | 8.7 | 262.9 | 20.5 | 207.9 | 87.2 | 42.1 | 220.4 | 154.4 | 403.5 | 184.3 | 104.9 | 436 | 233.4 | 238.2 | 158.5 | 176.1 | 190.4 | 162.6 | 176.3 | 157.2 | 192.2
1537 | 1392 | -6 | 0 | 0 | 185.5 | 159.7 | 147.9 | 152.6 | 194.4 | 24.2 | 20.4 | 38.8 | 9.6 | 269.5 | 18.5 | 207.7 | 87.1 | 42.1 | 220 | 154.2 | 402.7 | 184.1 | 104.9 | 435.3 | 233.1 | 238 | 158.2 | 175.8 | 190.2 | 162.4 | 176.1 | 157.1 | 192
1538 | 1393 | -5.3 | 0 | 0 | 185.2 | 159.6 | 147.7 | 152.4 | 193.9 | 24.2 | 20.4 | 38.7 | 9.6 | 268 | 18.1 | 207.4 | 87.3 | 42.1 | 219.4 | 153.9 | 401.9 | 183.8 | 104.9 | 434.9 | 232.7 | 237.9 | 158 | 175.6 | 190 | 162.2 | 175.9 | 156.9 | 191.8
1539 | 1394 | -4.9 | 0 | 0 | 184.8 | 159.3 | 147.4 | 152 | 193.6 | 24.1 | 20.4 | 38.6 | 11.1 | 267 | 18.5 | 207 | 87.1 | 42.2 | 219.3 | 153.6 | 401.1 | 183.3 | 104.7 | 434.3 | 232.3 | 237.7 | 157.8 | 175.4 | 189.8 | 162 | 175.8 | 156.7 | 191.6
1540 | 1395 | -5.3 | 0 | 0 | 184.3 | 159.1 | 147.2 | 151.6 | 193.3 | 24 | 20.4 | 38.5 | 10.9 | 261.3 | 19.2 | 206.6 | 86.7 | 42.1 | 219.2 | 153.4 | 400.4 | 182.9 | 104.3 | 433.5 | 232.1 | 237.5 | 157.7 | 175.2 | 189.7 | 161.8 | 175.6 | 156.3 | 191.4
1541 | 1396 | -5.5 | 0 | 0 | 183.8 | 158.9 | 147 | 151.4 | 193 | 23.8 | 20.4 | 38.5 | 8.1 | 265.7 | 15.8 | 206.2 | 86.3 | 42.1 | 219 | 153.2 | 399.6 | 182.8 | 103.9 | 433 | 231.8 | 237.3 | 157.6 | 175 | 189.5 | 161.6 | 175.4 | 156.1 | 191.2
1542 | 1397 | -5.4 | 0 | 0 | 183.7 | 158.7 | 146.8 | 151.2 | 192.8 | 23.7 | 20.4 | 38.4 | 9.3 | 246.6 | 16.2 | 205.8 | 86.1 | 42 | 218.9 | 152.9 | 398.8 | 182.4 | 103.7 | 432.5 | 231.3 | 237.1 | 157.4 | 174.8 | 189.2 | 161.4 | 175.2 | 155.9 | 191
1543 | 1398 | -5.5 | 0 | 0 | 183.6 | 158.4 | 147 | 151.1 | 192.6 | 23.6 | 20.4 | 38.3 | 9.3 | 242.7 | 17.6 | 205.4 | 85.7 | 42 | 218.8 | 152.7 | 398.1 | 182.3 | 103.3 | 432.1 | 231 | 237 | 157.3 | 174.7 | 189 | 161.2 | 175 | 155.6 | 190.8
1544 | 1399 | -5.8 | 0 | 0 | 183.5 | 158.3 | 147.3 | 151 | 192.3 | 23.5 | 20.4 | 38.2 | 7.7 | 255.5 | 17.7 | 205.1 | 85.6 | 42 | 218.5 | 152.4 | 397.4 | 181.9 | 103 | 431.7 | 230.6 | 236.8 | 157.1 | 174.4 | 188.8 | 161 | 174.8 | 155.4 | 190.6
1545 | 1400 | -5.9 | 0 | 0 | 183.3 | 158 | 147.3 | 150.9 | 192 | 23.4 | 20.4 | 38.1 | 6.9 | 257.3 | 17.4 | 204.8 | 85.4 | 42 | 218 | 152.2 | 396.7 | 181.5 | 103 | 431.3 | 230.3 | 236.6 | 157 | 174.2 | 188.7 | 160.8 | 174.7 | 155.1 | 190.4
1546 | 1401 | -6 | 0 | 0 | 182.6 | 157.7 | 147.1 | 150.8 | 191.8 | 23.3 | 20.4 | 38.1 | 9.1 | 254.7 | 15.7 | 204.6 | 85.5 | 42 | 217.6 | 151.9 | 395.9 | 181.2 | 103 | 431 | 229.9 | 236.4 | 156.8 | 174 | 188.5 | 160.6 | 174.5 | 155 | 190.2
1547 | 1402 | -5.9 | 0 | 0 | 182 | 157.6 | 146.7 | 150.6 | 191.7 | 23.2 | 20.4 | 38.1 | 11 | 248.9 | 13.1 | 204.2 | 85.3 | 42 | 217.3 | 151.6 | 395.2 | 181 | 103.1 | 430.9 | 229.6 | 236.3 | 156.6 | 173.8 | 188.3 | 160.4 | 174.3 | 154.8 | 190
1548 | 1403 | -5.9 | 0 | 0 | 181.5 | 157.6 | 146.5 | 150.5 | 191.6 | 23 | 20.4 | 38.1 | 9.3 | 248.8 | 15.2 | 204 | 84.9 | 41.9 | 217.2 | 151.3 | 394.5 | 181.2 | 103.1 | 430.7 | 229.2 | 236.1 | 156.4 | 173.6 | 188.1 | 160.3 | 174.2 | 154.7 | 189.7
1549 | 1404 | -6 | 0 | 0 | 181.2 | 157.4 | 146.3 | 150.3 | 191.4 | 23 | 20.4 | 38.1 | 7.7 | 248.6 | 19 | 203.8 | 84.5 | 41.9 | 217 | 151.1 | 393.7 | 181.2 | 103.4 | 430.4 | 228.8 | 235.9 | 156.2 | 173.4 | 187.9 | 160.1 | 174 | 154.6 | 189.6
1550 | 1405 | -5.9 | 0 | 0 | 180.8 | 157.2 | 146 | 149.9 | 191.2 | 23 | 20.4 | 38.1 | 7.2 | 239.3 | 24.2 | 203.5 | 84.3 | 42 | 216.9 | 150.8 | 393.1 | 180.9 | 103.3 | 430.1 | 228.4 | 235.7 | 156 | 173.2 | 187.7 | 159.9 | 173.7 | 154.5 | 189.4
1551 | 1406 | -5.9 | 0 | 0 | 180.5 | 157.1 | 145.8 | 149.6 | 190.9 | 23.1 | 20.4 | 38.1 | 12.4 | 245.2 | 20.5 | 203.3 | 84.1 | 42 | 216.5 | 150.4 | 392.5 | 180.8 | 102.8 | 429.7 | 228.1 | 235.5 | 155.8 | 173.1 | 187.5 | 159.7 | 173.6 | 154.4 | 189.2
1552 | 1407 | -5.9 | 0 | 0 | 180.1 | 156.9 | 145.5 | 149.3 | 190.7 | 23.1 | 20.4 | 38.1 | 10.9 | 235.9 | 18.1 | 203.1 | 84.4 | 41.9 | 215.9 | 150.1 | 391.9 | 181 | 102.1 | 429.2 | 227.8 | 235.4 | 155.6 | 172.9 | 187.3 | 159.5 | 173.4 | 154.3 | 189
1553 | 1408 | -6.1 | 0 | 0 | 179.8 | 156.7 | 145.3 | 149.1 | 190.5 | 23 | 20.4 | 38.1 | 10.7 | 229.9 | 22.4 | 202.8 | 84.1 | 41.8 | 215.3 | 149.8 | 391.4 | 181.1 | 101.8 | 428.7 | 227.6 | 235.2 | 155.4 | 172.8 | 187.1 | 159.3 | 173.2 | 154.1 | 188.8
1554 | 1409 | -6.1 | 0 | 0 | 179.3 | 156.4 | 145.2 | 149 | 190.3 | 23 | 20.4 | 38.1 | 11.2 | 244.2 | 18.4 | 202.5 | 84 | 41.8 | 214.9 | 149.5 | 390.9 | 181.1 | 101.6 | 428.2 | 227.3 | 235 | 155.3 | 172.7 | 187 | 159.1 | 173 | 153.8 | 188.6
1555 | 1410 | -6.2 | 0 | 0 | 179.4 | 156.3 | 145.1 | 148.6 | 190.1 | 23.1 | 20.4 | 38.1 | 13.3 | 233.7 | 20.1 | 202.2 | 83.9 | 41.7 | 214.5 | 149.3 | 390.3 | 181.1 | 101.3 | 428 | 227 | 234.8 | 155.1 | 172.5 | 186.8 | 158.9 | 172.8 | 153.6 | 188.4
1556 | 1411 | -6.3 | 0 | 0 | 179.3 | 156.1 | 145 | 148.3 | 189.8 | 23.1 | 20.4 | 38.1 | 12.1 | 243 | 17.5 | 201.7 | 83.6 | 41.6 | 214 | 149 | 389.7 | 181.1 | 101.2 | 427.3 | 226.7 | 234.6 | 155 | 172.3 | 186.5 | 158.7 | 172.7 | 153.4 | 188.2
1557 | 1412 | -6.4 | 0 | 0 | 179.1 | 155.9 | 144.7 | 148 | 189.4 | 23.2 | 20.4 | 38.1 | 10.6 | 242.8 | 24.3 | 201.3 | 83.3 | 41.4 | 213.8 | 148.7 | 389.1 | 180.9 | 101.1 | 426.8 | 226.3 | 234.5 | 154.8 | 172 | 186.3 | 158.5 | 172.5 | 153.1 | 188
1558 | 1413 | -6.2 | 0 | 0 | 178.7 | 155.7 | 144.5 | 147.6 | 189 | 23.2 | 20.4 | 38.1 | 9.8 | 242.2 | 24.8 | 200.9 | 83.7 | 41.3 | 213.6 | 148.3 | 388.3 | 180.2 | 100.9 | 426.4 | 226.1 | 234.3 | 154.5 | 171.8 | 186.1 | 158.3 | 172.3 | 152.9 | 187.8
1559 | 1414 | -5.6 | 0 | 0 | 178.4 | 155.6 | 144.4 | 147.5 | 188.9 | 23.2 | 20.4 | 38.2 | 8.8 | 240.2 | 25 | 200.6 | 83.6 | 41.3 | 213.6 | 148.1 | 387.6 | 180 | 100.7 | 426 | 225.6 | 234.1 | 154.4 | 171.6 | 186 | 158.1 | 172.1 | 152.6 | 187.6
1560 | 1415 | -5.7 | 0 | 0 | 178 | 155.4 | 144.2 | 147.5 | 188.7 | 23.2 | 20.4 | 38.3 | 7.5 | 238.3 | 25.5 | 200.3 | 83.4 | 41.2 | 213.4 | 147.9 | 387.1 | 179.6 | 100.1 | 425.3 | 225.5 | 233.9 | 154.3 | 171.5 | 185.8 | 157.9 | 172 | 152.4 | 187.5
1561 | 1416 | -6 | 0 | 0 | 177.4 | 155.2 | 143.9 | 147.3 | 188.3 | 23.1 | 20.5 | 38.4 | 6.9 | 244.4 | 23 | 199.9 | 83.3 | 41.2 | 213.2 | 147.7 | 386.5 | 179.7 | 100 | 424.9 | 225.4 | 233.7 | 154.1 | 171.3 | 185.6 | 157.8 | 171.8 | 152.2 | 187.3
1562 | 1417 | -5.9 | 0 | 0 | 177 | 155 | 143.7 | 147.3 | 188 | 23 | 20.5 | 38.5 | 8.2 | 238.2 | 23.1 | 199.2 | 83.5 | 41.1 | 213.1 | 147.4 | 385.9 | 179.1 | 99.5 | 424.2 | 224.9 | 233.6 | 153.9 | 171.2 | 185.4 | 157.6 | 171.6 | 152.1 | 187.1
1563 | 1418 | -5.6 | 0 | 0 | 177 | 154.8 | 143.6 | 147.3 | 187.7 | 22.8 | 20.5 | 38.5 | 12.7 | 237.9 | 20.5 | 198.7 | 83.3 | 41.1 | 212.9 | 147.3 | 385.4 | 178.7 | 99.3 | 423.3 | 224.4 | 233.4 | 153.7 | 171 | 185.2 | 157.4 | 171.4 | 152 | 186.9
1564 | 1419 | -5.7 | 0 | 0 | 176.7 | 154.7 | 143.4 | 147.2 | 187.5 | 22.8 | 20.5 | 38.4 | 15.2 | 236.2 | 17.7 | 198.1 | 83.3 | 41.1 | 212.8 | 147.1 | 384.8 | 178.6 | 99.3 | 422.7 | 224.2 | 233.2 | 153.6 | 170.8 | 185 | 157.2 | 171.2 | 151.8 | 186.7
1565 | 1420 | -5.7 | 0 | 0 | 176.5 | 154.5 | 143.1 | 147 | 187.3 | 22.7 | 20.5 | 38.3 | 11.3 | 249.3 | 17.1 | 197.6 | 82.8 | 41.1 | 212.6 | 146.9 | 384.1 | 178.3 | 99.1 | 422.2 | 224.1 | 233 | 153.4 | 170.7 | 184.8 | 157 | 171 | 151.6 | 186.5
1566 | 1421 | -5.7 | 0 | 0 | 176.3 | 154.3 | 142.9 | 146.8 | 187.2 | 22.7 | 20.5 | 38.3 | 12 | 244.3 | 16.3 | 197.1 | 82.4 | 41.1 | 212.5 | 146.8 | 383.6 | 178.4 | 99.2 | 421.6 | 223.8 | 232.8 | 153.2 | 170.5 | 184.7 | 156.9 | 170.8 | 151.5 | 186.3
1567 | 1422 | -5.6 | 0 | 0 | 176.2 | 154.1 | 142.8 | 146.6 | 187 | 22.8 | 20.5 | 38.3 | 11.7 | 243.6 | 24.4 | 196.6 | 82.7 | 41.1 | 212.2 | 146.5 | 383.1 | 178.7 | 98.9 | 421.5 | 223.3 | 232.7 | 153 | 170.3 | 184.5 | 156.7 | 170.6 | 151.3 | 186.1
1568 | 1423 | -5.9 | 0 | 0 | 176 | 154 | 142.6 | 146.4 | 186.9 | 22.8 | 20.5 | 38.2 | 13.1 | 246.3 | 25.7 | 196.3 | 82.7 | 41 | 211.9 | 146.2 | 382.6 | 178.6 | 98.9 | 421.1 | 223 | 232.5 | 152.8 | 170.1 | 184.3 | 156.5 | 170.5 | 151.2 | 185.9
1569 | 1424 | -6.1 | 0 | 0 | 176 | 154 | 142.4 | 146.3 | 186.8 | 22.9 | 20.5 | 38.2 | 11.7 | 241 | 23 | 196.1 | 82.6 | 40.9 | 211.4 | 146 | 382.1 | 178.2 | 98.7 | 420.2 | 222.8 | 232.3 | 152.7 | 170 | 184.1 | 156.3 | 170.2 | 151 | 185.7
1570 | 1425 | -6.5 | 0 | 0 | 176 | 154 | 142.1 | 146.2 | 186.6 | 22.9 | 20.5 | 38.1 | 13.2 | 237.7 | 22.6 | 196 | 82.1 | 40.8 | 211 | 145.8 | 381.5 | 177.6 | 98.6 | 419.7 | 222.6 | 232.1 | 152.5 | 169.8 | 183.9 | 156.1 | 170 | 150.9 | 185.5
1571 | 1426 | -6.5 | 0 | 0 | 175.7 | 153.9 | 141.8 | 146 | 186.4 | 22.9 | 20.5 | 38.2 | 12.5 | 245.3 | 25.6 | 195.9 | 81.6 | 40.7 | 210.2 | 145.6 | 380.9 | 177.2 | 98.7 | 419.2 | 222.1 | 231.9 | 152.4 | 169.7 | 183.7 | 155.9 | 169.8 | 150.7 | 185.3
1572 | 1427 | -6.4 | 0 | 0 | 175.3 | 153.8 | 141.6 | 145.7 | 186.2 | 23 | 20.5 | 38.2 | 11.5 | 225.9 | 22.2 | 195.8 | 81.6 | 40.7 | 209.7 | 145.4 | 380.2 | 177.1 | 98.6 | 418.6 | 221.8 | 231.8 | 152.2 | 169.5 | 183.5 | 155.8 | 169.7 | 150.6 | 185.2
1573 | 1428 | -6.7 | 0 | 0 | 174.9 | 153.7 | 141.5 | 145.5 | 186.1 | 23 | 20.5 | 38.2 | 13.5 | 226.1 | 15.9 | 195.6 | 81.8 | 40.7 | 209.6 | 145.2 | 379.6 | 177.3 | 98.3 | 418.2 | 221.5 | 231.6 | 152 | 169.3 | 183.3 | 155.6 | 169.6 | 150.4 | 185
1574 | 1429 | -6.7 | 0 | 0 | 174.8 | 153.5 | 141.3 | 145.3 | 186 | 23.1 | 20.5 | 38.1 | 15.6 | 220.3 | 19.3 | 195.3 | 82.1 | 40.8 | 209.2 | 145 | 379 | 176.7 | 98.2 | 417.9 | 221.1 | 231.4 | 151.8 | 169.2 | 183.2 | 155.4 | 169.5 | 150.2 | 184.7
1575 | 1430 | -6.6 | 0 | 0 | 174.6 | 153.1 | 141.1 | 145.1 | 185.7 | 23.1 | 20.5 | 38 | 13.1 | 236 | 21.9 | 195.1 | 82.3 | 40.8 | 209 | 144.8 | 378.4 | 176.6 | 98.1 | 417.8 | 220.6 | 231.2 | 151.6 | 169 | 183 | 155.2 | 169.3 | 150 | 184.6
1576 | 1431 | -6.5 | 0 | 0 | 174.4 | 152.8 | 141 | 145.1 | 185.3 | 23.1 | 20.5 | 37.9 | 11.8 | 236.5 | 23.8 | 195 | 82.3 | 40.8 | 208.5 | 144.5 | 377.6 | 176.5 | 98 | 417.7 | 220.2 | 231 | 151.4 | 168.8 | 182.8 | 155.1 | 169.1 | 149.6 | 184.4
1577 | 1432 | -6.5 | 0 | 0 | 174.1 | 152.6 | 140.8 | 144.9 | 184.9 | 23.1 | 20.5 | 37.9 | 11.4 | 239.8 | 28.7 | 194.9 | 82.1 | 40.8 | 208.2 | 144.3 | 376.9 | 176 | 98 | 417.3 | 219.9 | 230.9 | 151.3 | 168.6 | 182.6 | 154.9 | 169 | 149.3 | 184.2
1578 | 1433 | -6.4 | 0 | 0 | 174.1 | 152.5 | 140.6 | 144.7 | 184.6 | 23 | 20.5 | 37.9 | 10.6 | 243.7 | 28.9 | 194.7 | 81.6 | 40.8 | 207.8 | 144.1 | 376.1 | 175.5 | 97.7 | 416.7 | 219.6 | 230.7 | 151.2 | 168.4 | 182.4 | 154.7 | 168.7 | 149.2 | 184
1579 | 1434 | -6.2 | 0 | 0 | 174 | 152.2 | 140.4 | 144.7 | 184.4 | 22.9 | 20.5 | 37.8 | 12.6 | 247 | 30.7 | 194.4 | 81.1 | 40.9 | 207.6 | 143.9 | 375.2 | 174.6 | 97.4 | 416.1 | 219.4 | 230.5 | 151 | 168.3 | 182.1 | 154.5 | 168.5 | 149.1 | 183.9
1580 | 1435 | -6.3 | 0 | 0 | 174 | 152 | 140.3 | 144.5 | 184.4 | 22.9 | 20.5 | 37.7 | 13.7 | 243.4 | 32 | 194.1 | 80.6 | 40.8 | 207.4 | 143.7 | 374.3 | 173.9 | 97.1 | 415.8 | 219.1 | 230.3 | 150.8 | 168.1 | 182 | 154.3 | 168.3 | 149 | 183.6
1581 | 1436 | -6.3 | 0 | 0 | 173.9 | 151.8 | 140.2 | 144.3 | 184.3 | 22.8 | 20.5 | 37.7 | 13.5 | 243.7 | 25.4 | 193.9 | 80.6 | 40.8 | 207.1 | 143.5 | 373.6 | 173.4 | 96.7 | 415.1 | 218.8 | 230.1 | 150.6 | 167.9 | 181.8 | 154.2 | 168.2 | 148.9 | 183.5
1582 | 1437 | -6.3 | 0 | 0 | 173.5 | 151.7 | 140.1 | 144.1 | 184.1 | 22.8 | 20.5 | 37.7 | 13.2 | 244.8 | 24.6 | 193.7 | 80.6 | 40.7 | 206.7 | 143.3 | 372.8 | 173.5 | 96.6 | 414.7 | 218.6 | 229.9 | 150.4 | 167.8 | 181.6 | 154 | 168 | 148.6 | 183.3
1583 | 1438 | -6.3 | 0 | 0 | 173.1 | 151.6 | 139.9 | 144.1 | 183.9 | 22.7 | 20.5 | 37.7 | 12.8 | 242 | 24.6 | 193.5 | 80.2 | 40.7 | 206.5 | 143 | 372.1 | 173.9 | 96.6 | 414.6 | 218.2 | 229.8 | 150.2 | 167.6 | 181.5 | 153.8 | 167.9 | 148.3 | 183.1
1584 | 1439 | -5.6 | 0 | 0 | 172.8 | 151.6 | 139.6 | 143.9 | 183.6 | 22.8 | 20.5 | 37.6 | 11.8 | 234.8 | 23.7 | 193.2 | 79.6 | 40.7 | 206.2 | 142.8 | 371.3 | 174.2 | 96.4 | 414.5 | 217.8 | 229.6 | 150.1 | 167.4 | 181.3 | 153.6 | 167.7 | 148.3 | 182.9
1585 | 1440 | -5 | 0 | 0 | 172.5 | 151.4 | 139.4 | 143.5 | 183.3 | 22.8 | 20.5 | 37.5 | 10.1 | 238.5 | 21.5 | 192.9 | 79 | 40.7 | 205.9 | 142.5 | 370.5 | 174.2 | 96.2 | 414.2 | 217.5 | 229.4 | 149.9 | 167.3 | 181.1 | 153.4 | 167.5 | 148.2 | 182.7
1586 | 1441 | -5.8 | 0 | 0 | 172.1 | 151.3 | 139.2 | 143.2 | 183 | 22.9 | 20.5 | 37.5 | 8.9 | 241.3 | 21.8 | 192.5 | 78.9 | 40.7 | 205.7 | 142.3 | 369.7 | 173.8 | 96.1 | 413.4 | 217.1 | 229.2 | 149.6 | 167.1 | 181 | 153.3 | 167.4 | 148.1 | 182.6
1587 | 1442 | -6.2 | 0 | 0 | 172.3 | 151.1 | 139 | 143.2 | 182.7 | 22.9 | 20.5 | 37.5 | 9.2 | 242.7 | 21.6 | 191.9 | 79.1 | 40.6 | 205.5 | 142 | 368.9 | 173.6 | 95.8 | 412.9 | 216.7 | 229 | 149.5 | 166.9 | 180.8 | 153.1 | 167.2 | 147.8 | 182.4
1588 | 1443 | -6.2 | 0 | 0 | 172.2 | 150.9 | 138.9 | 143.2 | 182.5 | 22.9 | 20.5 | 37.5 | 10.7 | 249.9 | 20.8 | 191.3 | 79.2 | 40.5 | 205.3 | 141.7 | 368.2 | 173.7 | 95.7 | 412.4 | 216.4 | 228.9 | 149.4 | 166.8 | 180.6 | 152.9 | 167.1 | 147.6 | 182.2
1589 | 1444 | -6.2 | 0 | 0 | 171.9 | 150.7 | 138.7 | 143.2 | 182.3 | 22.9 | 20.5 | 37.6 | 11.1 | 261.8 | 18.9 | 191 | 79.1 | 40.4 | 204.9 | 141.5 | 367.5 | 173.5 | 95.5 | 412 | 216.1 | 228.7 | 149.3 | 166.7 | 180.4 | 152.7 | 167 | 147.3 | 182
1590 | 1445 | -6.2 | 0 | 0 | 171.5 | 150.5 | 138.7 | 143.2 | 182.1 | 22.9 | 20.5 | 37.5 | 11 | 246.1 | 23.2 | 190.8 | 79 | 40.4 | 204.6 | 141.3 | 366.8 | 173.1 | 95.3 | 411.7 | 216 | 228.5 | 149.1 | 166.5 | 180.2 | 152.6 | 166.8 | 147.2 | 181.8
1591 | 1446 | -6.2 | 0 | 0 | 171.2 | 150.3 | 138.5 | 142.9 | 181.9 | 22.9 | 20.5 | 37.5 | 11.4 | 237.5 | 25.4 | 190.7 | 79 | 40.4 | 204 | 141.1 | 366.1 | 172.9 | 95.1 | 411 | 215.7 | 228.3 | 148.8 | 166.4 | 180 | 152.4 | 166.6 | 147 | 181.7
1592 | 1447 | -6.1 | 0 | 0 | 171.1 | 150 | 138.4 | 142.5 | 181.7 | 22.9 | 20.5 | 37.4 | 11.9 | 248.9 | 21.2 | 190.5 | 78.8 | 40.3 | 203.9 | 140.9 | 365.5 | 172.5 | 94.9 | 410.3 | 215.4 | 228.1 | 148.6 | 166.3 | 179.9 | 152.2 | 166.5 | 146.7 | 181.5
1593 | 1448 | -6.2 | 0 | 0 | 170.8 | 149.8 | 138.1 | 142.2 | 181.6 | 22.9 | 20.6 | 37.2 | 13.8 | 245.4 | 24.9 | 190.3 | 79 | 40.1 | 203.6 | 140.7 | 365 | 172 | 94.7 | 409.6 | 215 | 228 | 148.6 | 166.1 | 179.8 | 152 | 166.3 | 146.5 | 181.3
1594 | 1449 | -6 | 0 | 0 | 170.4 | 149.7 | 138 | 142.1 | 181.4 | 22.8 | 20.5 | 37 | 14.9 | 248 | 23.2 | 190.2 | 78.8 | 39.8 | 203.1 | 140.4 | 364.4 | 171.9 | 94.7 | 409 | 214.6 | 227.8 | 148.5 | 165.9 | 179.6 | 151.9 | 166.1 | 146.1 | 181.1
1595 | 1450 | -5.4 | 0 | 0 | 169.8 | 149.5 | 138.1 | 141.8 | 181.2 | 22.7 | 20.6 | 36.9 | 12.2 | 247.2 | 22.3 | 190.2 | 78.8 | 39.5 | 202.7 | 140.3 | 363.6 | 171.8 | 94.6 | 408.6 | 214.2 | 227.6 | 148.5 | 165.8 | 179.4 | 151.7 | 165.9 | 145.9 | 180.9
1596 | 1451 | -5.1 | 0 | 0 | 169.2 | 149.5 | 138 | 141.4 | 181 | 22.6 | 20.6 | 36.8 | 8.7 | 251.3 | 19.4 | 190.3 | 79.3 | 39.2 | 202.4 | 140 | 363 | 171.3 | 94.5 | 408.2 | 213.9 | 227.4 | 148.3 | 165.6 | 179.2 | 151.5 | 165.7 | 145.8 | 180.8
1597 | 1452 | -5.5 | 0 | 0 | 168.7 | 149.3 | 137.8 | 141.2 | 180.7 | 22.5 | 20.6 | 36.8 | 11.3 | 256.6 | 16.4 | 190.3 | 79.6 | 39 | 202 | 139.8 | 362.1 | 170.7 | 94.5 | 408.1 | 213.7 | 227.2 | 148 | 165.4 | 179 | 151.3 | 165.6 | 145.7 | 180.6
1598 | 1453 | -5.9 | 0 | 0 | 168.5 | 149.1 | 137.8 | 140.8 | 180.4 | 22.4 | 20.6 | 36.7 | 11.7 | 242.5 | 18.3 | 190.4 | 79.5 | 38.7 | 201.6 | 139.6 | 361.3 | 170.5 | 94.5 | 407.9 | 213.1 | 227.1 | 147.8 | 165.2 | 178.8 | 151.1 | 165.4 | 145.7 | 180.4
1599 | 1454 | -6.4 | 0 | 0 | 168.3 | 148.9 | 137.6 | 140.4 | 179.5 | 22.4 | 20.6 | 36.7 | 11.1 | 251.6 | 25.1 | 190.4 | 79.4 | 38.5 | 201.3 | 139.3 | 360.7 | 170.3 | 94.2 | 407.8 | 212.7 | 226.9 | 147.7 | 165 | 178.6 | 151 | 165.3 | 145.6 | 180.3
1600 | 1455 | -6.2 | 0 | 0 | 168.2 | 148.7 | 137.3 | 140 | 179.4 | 22.3 | 20.6 | 36.8 | 12 | 248.3 | 24.4 | 190.3 | 79.1 | 38.3 | 200.8 | 139.1 | 360.1 | 171.4 | 94.1 | 407.4 | 212.4 | 226.7 | 147.5 | 164.8 | 178.4 | 150.8 | 165.1 | 145.3 | 180.1
1601 | 1456 | -5.8 | 0 | 0 | 168 | 148.5 | 137.1 | 139.6 | 179.3 | 22.2 | 20.6 | 36.8 | 15.4 | 250.5 | 25.5 | 190.2 | 78.7 | 38.2 | 200.3 | 138.9 | 359.5 | 172 | 94 | 407.2 | 212.2 | 226.5 | 147.4 | 164.7 | 178.2 | 150.6 | 164.9 | 145.1 | 179.9
1602 | 1457 | -5.6 | 0 | 0 | 168 | 148.3 | 136.9 | 139.1 | 179.1 | 22.2 | 20.6 | 36.8 | 17.1 | 241.2 | 24 | 189.9 | 78.7 | 38.2 | 199.9 | 138.7 | 358.8 | 172 | 93.8 | 406.6 | 211.7 | 226.3 | 147.1 | 164.5 | 178 | 150.5 | 164.7 | 145 | 179.7
1603 | 1458 | -5.5 | 0 | 0 | 167.9 | 148.1 | 136.7 | 139 | 179.1 | 22.1 | 20.6 | 36.7 | 15.1 | 248.9 | 23.4 | 189.7 | 78.4 | 38.1 | 199.7 | 138.4 | 358.2 | 171.4 | 93.5 | 406.4 | 211.5 | 226.2 | 146.8 | 164.3 | 177.9 | 150.3 | 164.6 | 145 | 179.5
1604 | 1459 | -5.6 | 0 | 0 | 168 | 148 | 136.6 | 138.9 | 178.8 | 22.2 | 20.6 | 36.7 | 13.5 | 236.7 | 19.9 | 189.4 | 78 | 38 | 199.5 | 138.2 | 357.7 | 171 | 93.2 | 406.2 | 211.3 | 226 | 146.6 | 164.2 | 177.7 | 150.1 | 164.4 | 144.8 | 179.4
1605 | 1460 | -5.4 | 0 | 0 | 168.1 | 147.8 | 136.4 | 138.8 | 178.6 | 22.2 | 20.6 | 36.6 | 9.3 | 251.5 | 22.9 | 189.2 | 78 | 37.8 | 199.2 | 137.9 | 357.1 | 170.8 | 93.1 | 406.1 | 211 | 225.8 | 146.5 | 164 | 177.5 | 150 | 164.2 | 144.6 | 179.2
1606 | 1461 | -5.5 | 0 | 0 | 168.6 | 147.5 | 136.2 | 138.8 | 178.5 | 22.2 | 20.6 | 36.5 | 5.7 | 246.3 | 23.1 | 189.1 | 77.9 | 37.7 | 198.5 | 137.7 | 356.4 | 171 | 93.1 | 406 | 210.8 | 225.6 | 146.3 | 163.9 | 177.4 | 149.8 | 164.1 | 144.4 | 179
1607 | 1462 | -5.9 | 0 | 0 | 168.5 | 147.2 | 136.1 | 138.9 | 178.4 | 22.3 | 20.6 | 36.5 | 6.4 | 249.9 | 29.8 | 188.9 | 77.7 | 37.6 | 198.3 | 137.4 | 355.8 | 170.9 | 93.1 | 405.6 | 210.5 | 225.4 | 146.2 | 163.7 | 177.2 | 149.6 | 163.9 | 144.4 | 178.9
1608 | 1463 | -6.3 | 0 | 0 | 168.3 | 146.9 | 136 | 138.8 | 178.3 | 22.4 | 20.6 | 36.4 | 10.1 | 256.6 | 25.4 | 188.7 | 77.7 | 37.3 | 198 | 137.2 | 355.2 | 170.6 | 92.8 | 405.2 | 210.1 | 225.3 | 146 | 163.5 | 177 | 149.5 | 163.8 | 144.4 | 178.7
1609 | 1464 | -6.6 | 0 | 0 | 168.2 | 146.6 | 135.8 | 138.6 | 178.3 | 22.4 | 20.6 | 36.4 | 12.1 | 251.7 | 22.1 | 188.5 | 77.8 | 37.1 | 197.8 | 137 | 354.6 | 169.8 | 92.7 | 404.9 | 210 | 225.1 | 145.8 | 163.3 | 176.8 | 149.3 | 163.5 | 144.2 | 178.5
1610 | 1465 | -6.7 | 0 | 0 | 168 | 146.4 | 135.6 | 138.5 | 178.2 | 22.3 | 20.6 | 36.5 | 10.9 | 251.4 | 22.2 | 188.2 | 77.7 | 37 | 197.6 | 136.8 | 354 | 169.4 | 92.7 | 404.6 | 209.6 | 224.9 | 145.7 | 163.1 | 176.6 | 149.1 | 163.4 | 143.9 | 178.4
1611 | 1466 | -6.5 | 0 | 0 | 167.7 | 146.4 | 135.4 | 138.3 | 178 | 22.3 | 20.6 | 36.5 | 14.3 | 249 | 20 | 188.1 | 77.3 | 36.9 | 197.4 | 136.6 | 353.3 | 168.7 | 92.6 | 404.4 | 209.3 | 224.7 | 145.7 | 162.9 | 176.4 | 149 | 163.2 | 143.6 | 178.2
1612 | 1467 | -6.4 | 0 | 0 | 167.4 | 146.4 | 135.2 | 138.2 | 177.8 | 22.2 | 20.6 | 36.4 | 15.2 | 245.8 | 21.8 | 187.9 | 77.4 | 36.8 | 197 | 136.4 | 352.7 | 168.4 | 92.5 | 403.7 | 209 | 224.5 | 145.5 | 162.8 | 176.2 | 148.8 | 163 | 143.5 | 178
1613 | 1468 | -6.3 | 0 | 0 | 167.3 | 146.3 | 135 | 138.2 | 177.7 | 22.2 | 20.6 | 36.3 | 14.5 | 244.8 | 30.2 | 187.7 | 77.5 | 36.7 | 196.7 | 136.1 | 352.1 | 168.3 | 92.2 | 403.1 | 208.7 | 224.3 | 145.3 | 162.6 | 176.1 | 148.6 | 162.8 | 143.4 | 177.8
1614 | 1469 | -6.1 | 0 | 0 | 167 | 146.3 | 134.9 | 137.9 | 177.6 | 22.1 | 20.6 | 36.2 | 13.7 | 239.7 | 32.3 | 187.4 | 77.7 | 36.7 | 196.4 | 135.9 | 351.4 | 167.7 | 92 | 402.5 | 208.4 | 224.2 | 145.2 | 162.4 | 175.9 | 148.5 | 162.6 | 143.4 | 177.7
1615 | 1470 | -6 | 0 | 0 | 166.6 | 146.4 | 134.9 | 137.7 | 177.7 | 22.1 | 20.6 | 36.1 | 14.5 | 252.1 | 31.5 | 187.2 | 78 | 36.7 | 196.1 | 135.7 | 350.8 | 167.2 | 91.8 | 402.2 | 208.1 | 224 | 145 | 162.3 | 175.8 | 148.3 | 162.5 | 143.1 | 177.5
1616 | 1471 | -6.4 | 0 | 0 | 166.2 | 146.3 | 134.8 | 137.8 | 177.6 | 22 | 20.6 | 36 | 18.4 | 245.5 | 27.8 | 186.9 | 78.1 | 36.6 | 195.4 | 135.5 | 350.1 | 166.6 | 91.7 | 401.5 | 207.9 | 223.8 | 144.8 | 162.1 | 175.6 | 148.1 | 162.3 | 142.7 | 177.3
1617 | 1472 | -6.7 | 0 | 0 | 166 | 146.2 | 134.6 | 137.8 | 177.3 | 22 | 20.6 | 36 | 15.7 | 247.3 | 27.2 | 186.4 | 77.9 | 36.5 | 195 | 135.4 | 349.4 | 166.2 | 91.7 | 400.7 | 207.3 | 223.6 | 144.5 | 161.9 | 175.4 | 147.9 | 162.2 | 142.5 | 177.1
1618 | 1473 | -6.8 | 0 | 0 | 165.8 | 146 | 134.4 | 137.6 | 177.1 | 22.1 | 20.6 | 35.9 | 9.7 | 230.4 | 31.6 | 185.8 | 77.8 | 36.4 | 195 | 135.3 | 348.7 | 166 | 91.7 | 400.3 | 207 | 223.5 | 144.4 | 161.8 | 175.3 | 147.8 | 162 | 142.3 | 176.9
1619 | 1474 | -6.8 | 0 | 0 | 165.4 | 145.8 | 134.2 | 137.4 | 176.9 | 22.1 | 20.6 | 35.9 | 13 | 238.4 | 28 | 185 | 77.7 | 36.2 | 195.1 | 135.1 | 348 | 165.7 | 91.5 | 399.4 | 206.8 | 223.3 | 144.2 | 161.7 | 175.1 | 147.6 | 161.8 | 142.2 | 176.8
1620 | 1475 | -6.7 | 0 | 0 | 165.3 | 145.5 | 134.1 | 137.4 | 176.7 | 22.1 | 20.6 | 35.8 | 16.6 | 242.4 | 24.2 | 184.2 | 77.9 | 36.2 | 195.1 | 134.8 | 347.4 | 165.5 | 91.1 | 398.8 | 206.4 | 223.1 | 144.1 | 161.5 | 174.9 | 147.5 | 161.7 | 142 | 176.6
1621 | 1476 | -6.6 | 0 | 0 | 165.3 | 145.2 | 134 | 137.4 | 176.5 | 22.1 | 20.6 | 35.7 | 9.6 | 245.3 | 23.8 | 183.5 | 77.7 | 36.1 | 194.3 | 134.5 | 346.8 | 165.3 | 90.8 | 398.6 | 206.1 | 222.9 | 143.9 | 161.3 | 174.7 | 147.3 | 161.6 | 141.7 | 176.4
1622 | 1477 | -6.2 | 0 | 0 | 165.2 | 145 | 133.8 | 137.2 | 176.4 | 22.1 | 20.6 | 35.8 | 6.6 | 242 | 21.9 | 183 | 77.3 | 36.1 | 193.8 | 134.4 | 346 | 165 | 90.9 | 398.6 | 205.8 | 222.7 | 143.7 | 161.2 | 174.5 | 147.2 | 161.4 | 141.4 | 176.2
1623 | 1478 | -6 | 0 | 0 | 165.1 | 145 | 133.9 | 136.9 | 176.3 | 22 | 20.6 | 35.8 | 8.3 | 241.9 | 24.4 | 182.5 | 77.1 | 36.1 | 193.9 | 134.2 | 345.3 | 164.9 | 91 | 398.5 | 205.5 | 222.6 | 143.5 | 161 | 174.4 | 147 | 161.3 | 141.3 | 176.1
1624 | 1479 | -6 | 0 | 0 | 165.2 | 144.9 | 133.6 | 136.8 | 176.1 | 22 | 20.6 | 35.8 | 9.6 | 244.4 | 22.8 | 182 | 76.7 | 36.1 | 193.9 | 133.9 | 344.5 | 164.9 | 91 | 398.4 | 205.2 | 222.4 | 143.4 | 160.8 | 174.2 | 146.9 | 161.2 | 141.2 | 175.9
1625 | 1480 | -6 | 0 | 0 | 164.9 | 144.7 | 133.3 | 136.7 | 175.9 | 22.1 | 20.6 | 35.8 | 8.7 | 241 | 22.6 | 181.3 | 76.4 | 36 | 193.8 | 133.7 | 343.7 | 164.5 | 91 | 398.5 | 204.8 | 222.2 | 143.3 | 160.7 | 174 | 146.7 | 161 | 141.1 | 175.7
1626 | 1481 | -6 | 0 | 0 | 164.7 | 144.4 | 133.2 | 136.5 | 175.8 | 22.1 | 20.6 | 35.8 | 7.7 | 241.4 | 20.9 | 180.7 | 76 | 36 | 193.7 | 133.4 | 343 | 164.1 | 90.7 | 398.1 | 204.7 | 222 | 143 | 160.6 | 173.8 | 146.5 | 160.9 | 141.1 | 175.6
1627 | 1482 | -6.3 | 0 | 0 | 164.3 | 144.3 | 133.2 | 136.4 | 175.6 | 22.1 | 20.6 | 35.9 | 9.2 | 237.1 | 23 | 180.3 | 76.1 | 36 | 193.5 | 133.2 | 342.2 | 164.2 | 90.6 | 397.7 | 204.4 | 221.8 | 142.8 | 160.4 | 173.6 | 146.4 | 160.7 | 141 | 175.4
1628 | 1483 | -6.3 | 0 | 0 | 163.8 | 144.1 | 133.1 | 136.3 | 175.3 | 22.1 | 20.6 | 35.8 | 15.9 | 249.2 | 21.1 | 180 | 76.6 | 36 | 193.4 | 133.1 | 341.5 | 163.6 | 90.3 | 397.3 | 204.1 | 221.7 | 142.6 | 160.3 | 173.5 | 146.2 | 160.6 | 140.9 | 175.2
1629 | 1484 | -6.2 | 0 | 0 | 163.4 | 144 | 132.8 | 136 | 175.1 | 22.1 | 20.6 | 35.7 | 17.4 | 271 | 18.7 | 179.5 | 76.5 | 35.9 | 193.2 | 132.8 | 340.6 | 163.3 | 90.3 | 396.7 | 203.8 | 221.5 | 142.4 | 160.1 | 173.3 | 146.1 | 160.4 | 140.7 | 175.1
1630 | 1485 | -6.3 | 0 | 0 | 163.3 | 143.9 | 132.7 | 135.7 | 174.9 | 22.1 | 20.6 | 35.7 | 14.2 | 247.9 | 19.6 | 178.8 | 76.4 | 35.9 | 193 | 132.7 | 339.9 | 163 | 89.9 | 396.4 | 203.5 | 221.3 | 142.1 | 160 | 173.2 | 145.9 | 160.2 | 140.5 | 174.9
1631 | 1486 | -6.4 | 0 | 0 | 163 | 143.8 | 132.5 | 135.6 | 174.6 | 22 | 20.6 | 35.6 | 11.1 | 253.7 | 18.8 | 178.7 | 76.1 | 35.8 | 192.6 | 132.4 | 339.3 | 163 | 89.6 | 395.8 | 203.1 | 221.1 | 142 | 159.8 | 173 | 145.8 | 160 | 140.3 | 174.7
1632 | 1487 | -6.4 | 0 | 0 | 162.7 | 143.7 | 132.4 | 135.4 | 174.4 | 22 | 20.6 | 35.6 | 11 | 242.4 | 23.4 | 178.6 | 75.5 | 35.8 | 192.1 | 132.2 | 338.7 | 162.7 | 89.5 | 395.3 | 202.9 | 221 | 141.8 | 159.7 | 172.9 | 145.6 | 159.8 | 140.1 | 174.5
1633 | 1488 | -6.3 | 0 | 0 | 162.1 | 143.7 | 132.3 | 135.1 | 174.2 | 22 | 20.6 | 35.6 | 10.1 | 246.1 | 18.3 | 178.6 | 75.3 | 35.8 | 191.9 | 132 | 338.1 | 162.4 | 89.2 | 394.5 | 202.7 | 220.8 | 141.5 | 159.5 | 172.8 | 145.4 | 159.6 | 139.9 | 174.4
1634 | 1489 | -6.3 | 0 | 0 | 162 | 143.5 | 132.2 | 134.8 | 174 | 22 | 20.6 | 35.5 | 14.2 | 241.9 | 18 | 178.4 | 75.1 | 35.8 | 191.7 | 131.7 | 337.5 | 162.1 | 89.3 | 394.4 | 202.3 | 220.6 | 141.3 | 159.3 | 172.5 | 145.3 | 159.4 | 139.7 | 174.2
1635 | 1490 | -6.2 | 0 | 0 | 161.9 | 143.1 | 132.1 | 134.6 | 173.7 | 22 | 20.6 | 35.5 | 13.8 | 241 | 24.1 | 178.3 | 75 | 35.8 | 191.3 | 131.5 | 337 | 161.6 | 89.2 | 393.9 | 202.2 | 220.4 | 141.2 | 159.1 | 172.4 | 145.1 | 159.2 | 139.5 | 174.1
1636 | 1491 | -6.4 | 0 | 0 | 161.7 | 142.9 | 132.2 | 134.7 | 173.4 | 21.9 | 20.6 | 35.5 | 13.5 | 243.9 | 26.7 | 178.3 | 74.7 | 35.7 | 190.6 | 131.2 | 336.5 | 161.7 | 89.2 | 393.6 | 201.9 | 220.2 | 141 | 158.9 | 172.1 | 145 | 159.1 | 139.2 | 173.9
1637 | 1492 | -6.6 | 0 | 0 | 161.6 | 142.8 | 132 | 134.8 | 173.2 | 21.9 | 20.6 | 35.5 | 12.6 | 239.8 | 26.1 | 178.2 | 74.8 | 35.6 | 190.4 | 131 | 335.9 | 161.5 | 89.1 | 393.6 | 201.6 | 220.1 | 140.8 | 158.8 | 172 | 144.8 | 158.9 | 139 | 173.7
1638 | 1493 | -6.3 | 0 | 0 | 161.8 | 142.5 | 131.6 | 134.5 | 173.3 | 21.9 | 20.6 | 35.5 | 12.4 | 246 | 27.2 | 178.1 | 74.8 | 35.5 | 190 | 130.8 | 335.3 | 161.1 | 89.2 | 393.5 | 201.3 | 219.9 | 140.6 | 158.6 | 171.8 | 144.7 | 158.7 | 138.9 | 173.6
1639 | 1494 | -6.1 | 0 | 0 | 161.9 | 142.2 | 131.3 | 134.4 | 173.2 | 21.9 | 20.6 | 35.5 | 12.4 | 240.7 | 27.5 | 178 | 74.6 | 35.3 | 189.8 | 130.5 | 334.5 | 160.5 | 89.3 | 393.2 | 201 | 219.7 | 140.4 | 158.4 | 171.7 | 144.5 | 158.6 | 139 | 173.4
1640 | 1495 | -6.4 | 0 | 0 | 161.7 | 141.9 | 131.1 | 134.5 | 173 | 21.8 | 20.6 | 35.5 | 6.9 | 244.9 | 25.9 | 178 | 74.5 | 35.2 | 189.7 | 130.2 | 333.8 | 160.1 | 89.4 | 393.1 | 200.7 | 219.5 | 140.3 | 158.3 | 171.5 | 144.4 | 158.4 | 138.8 | 173.2
1641 | 1496 | -6.5 | 0 | 0 | 161.7 | 141.7 | 131.1 | 134.6 | 172.9 | 21.8 | 20.6 | 35.6 | 6.9 | 243.2 | 30 | 178 | 74.4 | 35 | 189.5 | 130 | 333 | 160 | 89.8 | 393 | 200.6 | 219.3 | 140.1 | 158.2 | 171.4 | 144.2 | 158.2 | 138.6 | 173.1
1642 | 1497 | -6.4 | 0 | 0 | 161.4 | 141.6 | 131 | 134.5 | 172.7 | 21.8 | 20.7 | 35.6 | 11.4 | 246.4 | 27.8 | 178 | 74.3 | 34.9 | 189.2 | 129.7 | 332.4 | 160 | 89.7 | 392.7 | 200.4 | 219.2 | 139.9 | 158.1 | 171.2 | 144 | 158.1 | 138.3 | 172.9
1643 | 1498 | -6.5 | 0 | 0 | 161.2 | 141.6 | 130.9 | 134.3 | 172.5 | 21.8 | 20.6 | 35.6 | 12.5 | 246.6 | 23.7 | 178.1 | 74.6 | 34.7 | 189 | 129.5 | 331.7 | 160 | 89.3 | 392.3 | 199.9 | 219 | 139.7 | 157.9 | 171 | 143.9 | 157.9 | 138 | 172.8
1644 | 1499 | -6.4 | 0 | 0 | 161 | 141.6 | 130.8 | 134 | 172.3 | 21.9 | 20.6 | 35.5 | 13.3 | 253.9 | 24.3 | 178.1 | 74.5 | 34.6 | 188.6 | 129.3 | 331.1 | 159.8 | 89.2 | 392.3 | 199.6 | 218.8 | 139.5 | 157.8 | 170.8 | 143.7 | 157.7 | 137.8 | 172.6
1645 | 1500 | -6.2 | 0 | 0 | 160.8 | 141.5 | 130.7 | 133.7 | 172.1 | 21.9 | 20.7 | 35.5 | 11.1 | 244.4 | 22.4 | 178 | 74.3 | 34.5 | 188 | 129 | 330.6 | 160 | 89.1 | 392.2 | 199.3 | 218.6 | 139.3 | 157.6 | 170.7 | 143.5 | 157.6 | 137.7 | 172.4
1646 | 1501 | -6 | 0 | 0 | 160.4 | 141.4 | 130.5 | 133.4 | 171.9 | 21.9 | 20.7 | 35.4 | 10.4 | 243.1 | 18.7 | 177.9 | 74.5 | 34.3 | 187.5 | 128.8 | 330.1 | 159.6 | 88.8 | 391.9 | 198.9 | 218.4 | 139 | 157.4 | 170.5 | 143.3 | 157.4 | 137.6 | 172.3
1647 | 1502 | -5.2 | 0 | 0 | 160.1 | 141.2 | 130.4 | 133.1 | 171.7 | 21.9 | 20.7 | 35.5 | 9.4 | 244.3 | 19.2 | 177.7 | 74.1 | 34.3 | 187.1 | 128.5 | 329.5 | 159.5 | 88.5 | 391.6 | 198.8 | 218.3 | 138.8 | 157.2 | 170.3 | 143.2 | 157.2 | 137.3 | 172.1
1648 | 1503 | -5.3 | 0 | 0 | 159.9 | 141 | 130.3 | 132.9 | 171.5 | 21.9 | 20.7 | 35.4 | 9.3 | 247.1 | 18.5 | 177.7 | 73.7 | 34.2 | 186.7 | 128.3 | 329 | 159.4 | 88.2 | 391.2 | 198.6 | 218.1 | 138.6 | 157 | 170.2 | 143 | 157 | 137 | 171.9
1649 | 1504 | -5.8 | 0 | 0 | 159.7 | 140.7 | 130.1 | 132.9 | 171.3 | 21.9 | 20.7 | 35.4 | 7.1 | 242.4 | 13.9 | 177.8 | 73.2 | 34.1 | 186.3 | 128.1 | 328.4 | 159.5 | 88 | 390.8 | 198.2 | 217.9 | 138.4 | 156.9 | 169.9 | 142.8 | 156.9 | 136.8 | 171.7
1650 | 1505 | -6.1 | 0 | 0 | 159.5 | 140.4 | 130 | 132.9 | 171.1 | 21.9 | 20.7 | 35.4 | 5.8 | 239.5 | 14.3 | 177.6 | 73.4 | 34 | 185.9 | 127.8 | 327.9 | 159.4 | 87.6 | 390.2 | 197.7 | 217.7 | 138.3 | 156.8 | 169.8 | 142.7 | 156.7 | 136.8 | 171.6
1651 | 1506 | -6.3 | 0 | 0 | 159.1 | 140.3 | 129.9 | 132.9 | 170.9 | 21.8 | 20.7 | 35.3 | 7.5 | 248.4 | 14.6 | 177.3 | 73.2 | 33.9 | 185.6 | 127.6 | 327.4 | 159.1 | 87.4 | 389.4 | 197.5 | 217.5 | 138 | 156.6 | 169.6 | 142.5 | 156.6 | 136.8 | 171.4
1652 | 1507 | -5.9 | 0 | 0 | 158.6 | 140.2 | 129.8 | 133 | 170.6 | 21.7 | 20.7 | 35.3 | 9.9 | 246.5 | 16.8 | 177.1 | 73.5 | 33.8 | 185.2 | 127.2 | 326.8 | 158.8 | 87.2 | 388.8 | 197.4 | 217.4 | 137.8 | 156.4 | 169.4 | 142.4 | 156.4 | 136.7 | 171.3
1653 | 1508 | -6.1 | 0 | 0 | 158.3 | 140.1 | 129.6 | 133 | 170.3 | 21.6 | 20.7 | 35.3 | 9.1 | 236.9 | 18.8 | 176.8 | 73.6 | 33.8 | 185 | 126.9 | 326.3 | 158.6 | 87.1 | 388.2 | 197.2 | 217.2 | 137.6 | 156.2 | 169.2 | 142.2 | 156.3 | 136.5 | 171.1
1654 | 1509 | -6.4 | 0 | 0 | 158.3 | 140 | 129.5 | 133 | 170 | 21.5 | 20.7 | 35.2 | 6.2 | 235.2 | 17.3 | 176.6 | 73.6 | 33.8 | 184.7 | 126.6 | 325.7 | 158.5 | 87 | 387.7 | 197.1 | 217 | 137.4 | 156.1 | 169 | 142.1 | 156.1 | 136.2 | 170.9
1655 | 1510 | -6.3 | 0 | 0 | 158.4 | 139.9 | 129.4 | 132.7 | 169.8 | 21.5 | 20.7 | 35.1 | 4.6 | 268.7 | 12.6 | 176.5 | 73.6 | 33.8 | 184.4 | 126.3 | 325.1 | 158.6 | 86.8 | 387.7 | 196.8 | 216.8 | 137.2 | 155.9 | 168.8 | 141.9 | 155.9 | 136 | 170.8
1656 | 1511 | -6.2 | 0 | 0 | 158.4 | 139.9 | 129.2 | 132.2 | 169.7 | 21.6 | 20.7 | 35 | 8.4 | 260.6 | 12.1 | 176.3 | 73.9 | 33.8 | 183.9 | 125.9 | 324.6 | 158.9 | 86.6 | 387.1 | 196.5 | 216.7 | 137 | 155.8 | 168.7 | 141.7 | 155.8 | 135.8 | 170.6
1657 | 1512 | -6.2 | 0 | 0 | 158.3 | 139.9 | 129.1 | 131.7 | 169.5 | 21.6 | 20.7 | 34.9 | 11.6 | 258.8 | 12.9 | 176.1 | 74 | 33.7 | 183.5 | 125.6 | 324 | 158.6 | 86.3 | 386.6 | 196.3 | 216.5 | 136.7 | 155.6 | 168.5 | 141.6 | 155.6 | 135.6 | 170.4
1658 | 1513 | -6.3 | 0 | 0 | 158 | 139.7 | 129 | 131.3 | 169.4 | 21.6 | 20.7 | 34.9 | 8.5 | 253.1 | 11.6 | 175.9 | 74 | 33.7 | 183.1 | 125.2 | 323.5 | 158.4 | 86 | 386.2 | 196.1 | 216.3 | 136.5 | 155.5 | 168.4 | 141.5 | 155.5 | 135.5 | 170.3
1659 | 1514 | -6.4 | 0 | 0 | 157.7 | 139.5 | 128.9 | 131.2 | 169.2 | 21.5 | 20.7 | 34.9 | 7.8 | 248.8 | 13.1 | 175.6 | 74.3 | 33.7 | 182.7 | 124.9 | 322.9 | 158.3 | 85.9 | 385.8 | 196 | 216.1 | 136.3 | 155.4 | 168.2 | 141.3 | 155.3 | 135.4 | 170.2
1660 | 1515 | -6.3 | 0 | 0 | 157.3 | 139.3 | 128.9 | 130.9 | 169 | 21.6 | 20.7 | 35 | 10.2 | 238.7 | 16.6 | 175.4 | 74.2 | 33.7 | 182.4 | 124.6 | 322.2 | 158.1 | 85.6 | 385.5 | 195.6 | 215.9 | 136.1 | 155.3 | 168.1 | 141.2 | 155.2 | 135.2 | 170
1661 | 1516 | -6.1 | 0 | 0 | 157 | 139 | 128.8 | 130.6 | 168.8 | 21.6 | 20.7 | 35.1 | 10.5 | 239.6 | 20.6 | 175.1 | 74 | 33.6 | 182.2 | 124.3 | 321.7 | 158.1 | 85.1 | 385.3 | 195.6 | 215.8 | 135.9 | 155.2 | 167.9 | 141 | 155 | 134.9 | 169.8
1662 | 1517 | -6 | 0 | 0 | 156.7 | 138.8 | 128.7 | 130.3 | 168.5 | 21.6 | 20.7 | 35.2 | 10.5 | 252 | 25.5 | 174.7 | 73.8 | 33.6 | 182 | 124 | 321.1 | 158.3 | 84.9 | 385.3 | 195.5 | 215.6 | 135.7 | 155 | 167.8 | 140.8 | 154.9 | 134.6 | 169.7
1663 | 1518 | -6.1 | 0 | 0 | 156.8 | 138.6 | 128.6 | 130.3 | 168.3 | 21.6 | 20.7 | 35.2 | 12.2 | 245.2 | 28.7 | 174.4 | 73.7 | 33.5 | 181.8 | 123.7 | 320.6 | 158 | 84.8 | 385.3 | 195.5 | 215.4 | 135.6 | 154.9 | 167.6 | 140.7 | 154.7 | 134.4 | 169.5
1664 | 1519 | -5.7 | 0 | 0 | 156.7 | 138.4 | 128.5 | 130.3 | 168.1 | 21.6 | 20.7 | 35.2 | 9.6 | 256 | 29.5 | 174 | 73.6 | 33.4 | 181.6 | 123.6 | 319.9 | 157.4 | 85 | 385.1 | 195.3 | 215.2 | 135.5 | 154.8 | 167.5 | 140.5 | 154.6 | 134.3 | 169.4
1665 | 1520 | -4.9 | 0 | 0 | 156.5 | 138.2 | 128.4 | 130 | 168 | 21.6 | 20.7 | 35.2 | 8.6 | 255.8 | 28.1 | 173.6 | 73.2 | 33.3 | 181.4 | 123.4 | 319.4 | 157 | 84.9 | 384.9 | 195.2 | 215.1 | 135.3 | 154.6 | 167.3 | 140.3 | 154.4 | 134.1 | 169.2
1666 | 1521 | -5.4 | 0 | 0 | 156.1 | 138.1 | 128.3 | 129.7 | 167.8 | 21.6 | 20.7 | 35.3 | 7.8 | 253.4 | 27.2 | 173 | 73 | 33.3 | 181.4 | 123.3 | 318.7 | 156.9 | 84.4 | 384.4 | 195.1 | 214.9 | 135.1 | 154.4 | 167.1 | 140.2 | 154.3 | 134 | 169
1667 | 1522 | -5.6 | 0 | 0 | 155.8 | 138 | 128.2 | 129.7 | 167.6 | 21.6 | 20.7 | 35.3 | 7.3 | 254.5 | 24.4 | 172.5 | 72.6 | 33.3 | 181.2 | 123.1 | 318.1 | 156.8 | 84.3 | 383.6 | 194.9 | 214.7 | 135 | 154.2 | 167 | 140 | 154.2 | 133.9 | 168.9
1668 | 1523 | -5.6 | 0 | 0 | 155.6 | 137.7 | 128.1 | 129.7 | 167.4 | 21.7 | 20.7 | 35.4 | 5.8 | 258.5 | 22 | 172.1 | 72.1 | 33.3 | 181 | 122.8 | 317.6 | 156.8 | 84.2 | 383.1 | 194.8 | 214.5 | 134.8 | 154.1 | 166.8 | 139.9 | 154 | 133.7 | 168.7
1669 | 1524 | -6 | 0 | 0 | 155.3 | 137.4 | 127.9 | 129.5 | 167.3 | 21.7 | 20.7 | 35.4 | 7.8 | 267.4 | 25.2 | 171.7 | 71.8 | 33.4 | 181 | 122.6 | 317.2 | 156.5 | 84.1 | 382.3 | 194.7 | 214.4 | 134.6 | 153.9 | 166.6 | 139.7 | 153.9 | 133.6 | 168.6
1670 | 1525 | -6.2 | 0 | 0 | 155.1 | 137.3 | 127.8 | 129.3 | 167.2 | 21.6 | 20.7 | 35.4 | 10.1 | 263.1 | 24 | 171.1 | 72 | 33.4 | 180.8 | 122.5 | 316.8 | 156 | 83.9 | 381.6 | 194.4 | 214.2 | 134.4 | 153.8 | 166.4 | 139.6 | 153.7 | 133.4 | 168.4
1671 | 1526 | -6.3 | 0 | 0 | 155.3 | 137.3 | 127.7 | 129.2 | 167.1 | 21.5 | 20.7 | 35.5 | 9.2 | 274.5 | 22.1 | 170.7 | 71.8 | 33.4 | 180.6 | 122.2 | 316.3 | 155.5 | 83.8 | 381 | 193.9 | 214 | 134.3 | 153.6 | 166.2 | 139.4 | 153.6 | 133.3 | 168.3
1672 | 1527 | -6.1 | 0 | 0 | 155 | 137.3 | 127.6 | 129.3 | 166.9 | 21.4 | 20.7 | 35.5 | 7 | 266.8 | 25.6 | 170.4 | 71.7 | 33.4 | 180.3 | 122 | 315.8 | 155.3 | 83.6 | 380.4 | 193.7 | 213.8 | 134.2 | 153.5 | 166.1 | 139.2 | 153.4 | 133 | 168.1
1673 | 1528 | -6.1 | 0 | 0 | 154.6 | 137.2 | 127.5 | 129.2 | 166.8 | 21.4 | 20.7 | 35.6 | 6.6 | 262.3 | 24.7 | 170.2 | 71.6 | 33.4 | 179.8 | 121.8 | 315.4 | 155.1 | 83.5 | 379.5 | 193.5 | 213.7 | 134 | 153.4 | 165.9 | 139.1 | 153.3 | 132.7 | 167.9
1674 | 1529 | -6.1 | 0 | 0 | 154.3 | 137.1 | 127.3 | 129.2 | 166.7 | 21.4 | 20.7 | 35.6 | 6.8 | 252.8 | 21.7 | 170 | 71.2 | 33.4 | 178.6 | 121.6 | 314.8 | 154.9 | 83.3 | 378.9 | 193 | 213.5 | 133.8 | 153.3 | 165.8 | 138.9 | 153.2 | 132.6 | 167.8
1675 | 1530 | -6 | 0 | 0 | 154 | 137.1 | 127.1 | 129.2 | 166.5 | 21.3 | 20.7 | 35.7 | 7.2 | 246 | 18.1 | 169.8 | 71 | 33.3 | 178.1 | 121.4 | 314.3 | 154.5 | 83.3 | 378.3 | 192.6 | 213.3 | 133.6 | 153.1 | 165.6 | 138.8 | 153 | 132.5 | 167.6
1676 | 1531 | -6.1 | 0 | 0 | 153.9 | 137 | 126.9 | 129.1 | 166.3 | 21.2 | 20.7 | 35.7 | 7.5 | 243 | 17.4 | 169.6 | 71.1 | 33.3 | 178.1 | 121.2 | 313.8 | 154.3 | 83.5 | 378 | 192.5 | 213.1 | 133.4 | 152.9 | 165.3 | 138.6 | 152.9 | 132.4 | 167.4
1677 | 1532 | -6.1 | 0 | 0 | 153.8 | 136.8 | 126.8 | 129 | 166.1 | 21.1 | 20.7 | 35.7 | 6.4 | 248.6 | 15.9 | 169.4 | 71 | 33.3 | 177.9 | 121 | 313.4 | 154.3 | 83.4 | 377.7 | 192.2 | 212.9 | 133.2 | 152.8 | 165.2 | 138.5 | 152.8 | 132.3 | 167.3
1678 | 1533 | -6.1 | 0 | 0 | 153.7 | 136.5 | 126.7 | 129 | 166 | 21.1 | 20.7 | 35.7 | 6 | 240.6 | 14.9 | 169.2 | 71 | 33.3 | 177.6 | 120.8 | 313 | 154.4 | 83.1 | 377.4 | 192 | 212.8 | 133 | 152.6 | 165.1 | 138.3 | 152.7 | 132 | 167.1
1679 | 1534 | -6.1 | 0 | 0 | 153.4 | 136.3 | 126.6 | 129.1 | 165.9 | 21 | 20.7 | 35.7 | 6.7 | 262.6 | 13.7 | 168.9 | 70.5 | 33.3 | 177.3 | 120.6 | 312.6 | 154.4 | 82.9 | 377.3 | 191.6 | 212.6 | 133 | 152.5 | 164.9 | 138.1 | 152.5 | 131.9 | 167
1680 | 1535 | -6.1 | 0 | 0 | 153.4 | 136 | 126.4 | 129.2 | 165.8 | 21 | 20.7 | 35.8 | 8.9 | 263.1 | 13.2 | 168.7 | 70 | 33.3 | 177 | 120.4 | 312.2 | 154 | 82.6 | 377.1 | 191.4 | 212.4 | 132.9 | 152.4 | 164.8 | 138 | 152.4 | 131.9 | 166.8
1681 | 1536 | -5.9 | 0 | 0 | 153.4 | 135.8 | 126.2 | 129.3 | 165.7 | 21 | 20.7 | 35.7 | 10.1 | 263.1 | 15.9 | 168.4 | 70.2 | 33.3 | 176.8 | 120.3 | 311.9 | 153.5 | 82.3 | 376.8 | 191 | 212.2 | 132.6 | 152.2 | 164.6 | 137.8 | 152.2 | 131.7 | 166.6
1682 | 1537 | -6 | 0 | 0 | 153.5 | 135.7 | 126.1 | 129.1 | 165.5 | 21 | 20.7 | 35.6 | 8.3 | 259.5 | 15.8 | 168 | 70.3 | 33.3 | 176.6 | 120.1 | 311.5 | 153.4 | 82.3 | 376.4 | 190.8 | 212.1 | 132.5 | 152.1 | 164.5 | 137.7 | 151.9 | 131.5 | 166.5
1683 | 1538 | -6 | 0 | 0 | 153.5 | 135.6 | 125.9 | 128.7 | 165.4 | 21.2 | 20.7 | 35.6 | 4.5 | 246.2 | 15.1 | 167.4 | 70.2 | 33.3 | 176.6 | 119.9 | 311.1 | 153.2 | 82.2 | 375.7 | 190.5 | 211.9 | 132.3 | 151.9 | 164.3 | 137.6 | 151.8 | 131.2 | 166.4
1684 | 1539 | -6 | 0 | 0 | 153.1 | 135.7 | 125.8 | 128.3 | 165.3 | 21.2 | 20.7 | 35.7 | 3.3 | 227.3 | 15.1 | 166.9 | 69.9 | 33.2 | 176.6 | 119.7 | 310.6 | 153 | 82.2 | 375.1 | 190.5 | 211.7 | 132.1 | 151.7 | 164.2 | 137.4 | 151.6 | 131.1 | 166.2
1685 | 1540 | -6.1 | 0 | 0 | 152.7 | 135.8 | 125.7 | 128 | 165.2 | 21.3 | 20.7 | 35.7 | 3.9 | 239.4 | 14.7 | 166.4 | 69.7 | 33.3 | 176.5 | 119.5 | 310.1 | 153 | 82 | 374.7 | 190.1 | 211.5 | 132 | 151.6 | 164.1 | 137.2 | 151.4 | 130.9 | 166.1
1686 | 1541 | -6.1 | 0 | 0 | 152.5 | 135.7 | 125.6 | 127.7 | 165 | 21.3 | 20.7 | 35.7 | 4.1 | 236.6 | 17.1 | 165.9 | 69.7 | 33.2 | 176.6 | 119.4 | 309.7 | 153 | 81.8 | 374.4 | 189.7 | 211.4 | 131.8 | 151.5 | 163.9 | 137.1 | 151.3 | 130.9 | 165.9
1687 | 1542 | -6 | 0 | 0 | 152.4 | 135.4 | 125.5 | 127.3 | 164.8 | 21.4 | 20.7 | 35.7 | 5.6 | 260.7 | 12.9 | 165.3 | 69.3 | 33.3 | 176.4 | 119.2 | 309.3 | 152.8 | 81.7 | 374.1 | 189.2 | 211.2 | 131.6 | 151.3 | 163.8 | 137 | 151.1 | 130.8 | 165.8
1688 | 1543 | -6 | 0 | 0 | 152.3 | 135.1 | 125.4 | 127 | 164.6 | 21.4 | 20.7 | 35.7 | 6.2 | 249.4 | 8 | 164.7 | 69.2 | 33.3 | 176.4 | 119 | 308.9 | 152.6 | 81.7 | 373.4 | 189 | 211 | 131.6 | 151.1 | 163.6 | 136.8 | 151 | 130.5 | 165.5
1689 | 1544 | -6.1 | 0 | 0 | 152.1 | 135.1 | 125.3 | 126.8 | 164.5 | 21.4 | 20.8 | 35.7 | 8.3 | 242.3 | 6.3 | 164.3 | 69.2 | 33.3 | 176.3 | 118.9 | 308.5 | 152.3 | 81.6 | 372.8 | 188.9 | 210.8 | 131.6 | 151 | 163.5 | 136.6 | 150.9 | 130.2 | 165.4
1690 | 1545 | -5.5 | 0 | 0 | 151.8 | 135.2 | 125.2 | 126.5 | 164.3 | 21.4 | 20.8 | 35.7 | 8.2 | 276.9 | 9.6 | 164.1 | 69.4 | 33.3 | 175.9 | 118.8 | 308.1 | 152.1 | 81.5 | 372.7 | 188.6 | 210.7 | 131.5 | 150.9 | 163.3 | 136.4 | 150.7 | 129.9 | 165.2
1691 | 1546 | -5.4 | 0 | 0 | 152 | 135.1 | 125 | 126.2 | 164.1 | 21.5 | 20.8 | 35.7 | 7.5 | 262.9 | 13.5 | 163.8 | 69.4 | 33.3 | 175.8 | 118.6 | 307.7 | 152 | 81.4 | 372.2 | 188.4 | 210.5 | 131.5 | 150.8 | 163.2 | 136.3 | 150.5 | 129.9 | 165.1
1692 | 1547 | -5.7 | 0 | 0 | 152.1 | 134.8 | 124.8 | 125.9 | 164 | 21.5 | 20.8 | 35.7 | 6.8 | 253.7 | 18.8 | 163.5 | 69.3 | 33.4 | 175.7 | 118.5 | 307.3 | 151.9 | 81.2 | 372 | 188.1 | 210.3 | 131.3 | 150.7 | 163 | 136.2 | 150.3 | 129.9 | 165
1693 | 1548 | -4.7 | 0 | 0 | 151.8 | 134.6 | 124.5 | 125.8 | 163.9 | 21.5 | 20.8 | 35.7 | 9.1 | 250 | 21.4 | 163.2 | 69 | 33.4 | 175.5 | 118.3 | 307 | 151.6 | 81 | 371.7 | 187.9 | 210.1 | 131.2 | 150.6 | 162.9 | 136 | 150.1 | 129.9 | 164.8
1694 | 1549 | -3.3 | 0 | 0 | 151.5 | 134.5 | 124.4 | 125.7 | 163.7 | 21.6 | 20.8 | 35.7 | 8.9 | 262.3 | 18.5 | 163 | 68.7 | 33.5 | 175.3 | 118 | 306.6 | 151.2 | 80.8 | 371.3 | 187.6 | 210 | 131 | 150.4 | 162.7 | 135.9 | 150 | 129.9 | 164.7
1695 | 1550 | -3.5 | 0 | 0 | 151.2 | 134.4 | 124.1 | 125.8 | 163.5 | 21.7 | 20.8 | 35.7 | 6 | 258.8 | 15 | 162.8 | 68.5 | 33.5 | 175.2 | 117.9 | 306.3 | 151.1 | 80.7 | 370.7 | 187.5 | 209.8 | 130.8 | 150.3 | 162.6 | 135.8 | 149.9 | 129.7 | 164.5
1696 | 1551 | -3.5 | 0 | 0 | 150.9 | 134.4 | 123.9 | 125.8 | 163.3 | 21.8 | 20.8 | 35.7 | 4.1 | 260.7 | 12.4 | 162.5 | 68 | 33.4 | 175.1 | 117.7 | 306 | 151.1 | 80.6 | 370.2 | 187.3 | 209.6 | 130.6 | 150.2 | 162.3 | 135.6 | 149.7 | 129.4 | 164.3
1697 | 1552 | -4.3 | 0 | 0 | 150.9 | 134.2 | 123.8 | 125.5 | 163.1 | 21.8 | 20.8 | 35.7 | 4.6 | 248.6 | 17.4 | 162.2 | 67.7 | 33.4 | 174.8 | 117.6 | 305.6 | 151.4 | 80.5 | 370 | 187 | 209.4 | 130.5 | 150.1 | 162.2 | 135.4 | 149.6 | 129.3 | 164.2
1698 | 1553 | -4.6 | 0 | 0 | 150.8 | 134.2 | 123.7 | 125.1 | 162.9 | 21.9 | 20.8 | 35.7 | 6.4 | 264.1 | 18.6 | 162 | 67.7 | 33.3 | 174.6 | 117.4 | 305.3 | 151 | 80.4 | 369.8 | 186.7 | 209.3 | 130.3 | 149.9 | 162 | 135.3 | 149.4 | 129 | 164
1699 | 1554 | -5.1 | 0 | 0 | 150.5 | 134 | 123.6 | 124.8 | 162.6 | 21.8 | 20.8 | 35.7 | 7 | 261.1 | 15.8 | 161.6 | 67.7 | 33.3 | 174.6 | 117.3 | 305 | 150.6 | 80.3 | 369.3 | 186.3 | 209.1 | 130.1 | 149.8 | 161.9 | 135.2 | 149.2 | 128.7 | 163.8
1700 | 1555 | -5.4 | 0 | 0 | 150.2 | 133.7 | 123.5 | 124.5 | 162.5 | 21.8 | 20.8 | 35.7 | 4.8 | 258.6 | 14.3 | 161.1 | 67.3 | 33.2 | 174.5 | 117 | 304.7 | 150.7 | 80.3 | 368.9 | 186.1 | 208.9 | 129.9 | 149.6 | 161.7 | 135 | 149.1 | 128.6 | 163.7
1701 | 1556 | -6 | 0 | 0 | 150 | 133.4 | 123.3 | 124.3 | 162.4 | 21.7 | 20.8 | 35.7 | 7 | 248.3 | 13 | 160.9 | 67.4 | 33.2 | 174.2 | 116.9 | 304.3 | 150.5 | 80.2 | 368.5 | 185.8 | 208.7 | 129.9 | 149.5 | 161.5 | 134.8 | 149 | 128.4 | 163.6
1702 | 1557 | -6.2 | 0 | 0 | 150.1 | 133.1 | 123 | 124.1 | 162.4 | 21.8 | 20.8 | 35.6 | 9.7 | 260.3 | 12 | 160.7 | 67 | 33.2 | 173.5 | 116.7 | 303.8 | 150.3 | 80.3 | 368.3 | 185.6 | 208.6 | 129.8 | 149.4 | 161.3 | 134.7 | 148.8 | 128.3 | 163.4
1703 | 1558 | -6.2 | 0 | 0 | 150 | 132.9 | 122.8 | 124 | 162.2 | 21.8 | 20.8 | 35.6 | 10.3 | 272.3 | 13.1 | 160.3 | 66.8 | 33.2 | 173.5 | 116.6 | 303.4 | 150.1 | 80.1 | 368 | 185.3 | 208.4 | 129.5 | 149.2 | 161.2 | 134.5 | 148.7 | 128.2 | 163.3
1704 | 1559 | -6.2 | 0 | 0 | 149.7 | 132.7 | 122.7 | 124.1 | 162.1 | 21.8 | 20.8 | 35.6 | 10.1 | 251.8 | 10.2 | 159.9 | 66.7 | 33.2 | 173.5 | 116.4 | 302.9 | 150.1 | 80 | 367.6 | 185.1 | 208.2 | 129.3 | 149.1 | 161 | 134.4 | 148.4 | 128.2 | 163.1
1705 | 1560 | -6.2 | 0 | 0 | 149.2 | 132.5 | 122.6 | 124.3 | 161.9 | 21.8 | 20.8 | 35.5 | 8 | 264.5 | 11.3 | 159.8 | 66.3 | 33.2 | 173.3 | 116.3 | 302.5 | 149.8 | 79.8 | 367.5 | 185 | 208 | 129.1 | 148.9 | 160.9 | 134.2 | 148.3 | 128.2 | 162.9
1706 | 1561 | -6.1 | 0 | 0 | 148.9 | 132.5 | 122.6 | 124.3 | 161.7 | 21.8 | 20.8 | 35.5 | 7.7 | 248 | 11.2 | 159.8 | 66.2 | 33.2 | 173 | 116.1 | 302.2 | 149.5 | 79.8 | 367.4 | 184.6 | 207.9 | 128.9 | 148.7 | 160.8 | 134.1 | 148.2 | 128 | 162.7
1707 | 1562 | -5.8 | 0 | 0 | 148.7 | 132.5 | 122.4 | 124 | 161.6 | 21.8 | 20.8 | 35.4 | 8 | 243.3 | 12.2 | 159.7 | 66.2 | 33.2 | 172.6 | 116 | 301.8 | 149.4 | 79.6 | 366.7 | 184.3 | 207.7 | 128.9 | 148.7 | 160.7 | 133.9 | 148.1 | 127.7 | 162.6
1708 | 1563 | -5.7 | 0 | 0 | 148.6 | 132.4 | 122.1 | 123.7 | 161.4 | 21.8 | 20.8 | 35.4 | 12.4 | 235.5 | 13.8 | 159.6 | 66 | 33.1 | 172.3 | 115.8 | 301.4 | 149.2 | 79.4 | 366.3 | 184 | 207.5 | 128.7 | 148.6 | 160.5 | 133.8 | 147.9 | 127.6 | 162.4
1709 | 1564 | -5.4 | 0 | 0 | 148.2 | 132.1 | 122.1 | 123.4 | 161.2 | 21.8 | 20.8 | 35.5 | 13.3 | 226.7 | 17.7 | 159.6 | 65.7 | 33.1 | 172 | 115.6 | 300.9 | 148.8 | 79.4 | 366.1 | 184 | 207.3 | 128.6 | 148.4 | 160.4 | 133.6 | 147.8 | 127.5 | 162.3
1710 | 1565 | -5.6 | 0 | 0 | 148 | 131.8 | 122 | 123.1 | 161 | 21.7 | 20.8 | 35.4 | 13 | 242 | 16.2 | 159.5 | 65.7 | 32.9 | 171.7 | 115.4 | 300.5 | 148.4 | 79.2 | 365.9 | 183.7 | 207.2 | 128.4 | 148.2 | 160.2 | 133.5 | 147.6 | 127.3 | 162.1
1711 | 1566 | -5.7 | 0 | 0 | 148.1 | 131.6 | 121.9 | 122.8 | 160.9 | 21.7 | 20.8 | 35.4 | 7.2 | 239.4 | 23.3 | 159.4 | 65.7 | 32.9 | 171.1 | 115.3 | 300.2 | 148.1 | 79.2 | 365.5 | 183.4 | 207 | 128.2 | 148.1 | 160 | 133.3 | 147.5 | 127.3 | 162
1712 | 1567 | -5.4 | 0 | 0 | 148 | 131.4 | 121.8 | 122.6 | 160.8 | 21.7 | 20.8 | 35.4 | 5 | 239.9 | 24.3 | 159.4 | 65.7 | 33 | 170.6 | 115 | 299.7 | 148.1 | 79.4 | 365.1 | 183.3 | 206.8 | 128 | 147.9 | 159.8 | 133.2 | 147.3 | 127.1 | 161.9
1713 | 1568 | -5.7 | 0 | 0 | 148.1 | 131.2 | 121.7 | 122.5 | 160.7 | 21.6 | 20.8 | 35.5 | 9.9 | 252.2 | 23.1 | 159.3 | 65.5 | 33 | 170.4 | 114.8 | 299.3 | 148 | 79.5 | 364.7 | 183.1 | 206.6 | 127.8 | 147.7 | 159.6 | 133 | 147.1 | 126.9 | 161.7
1714 | 1569 | -6.2 | 0 | 0 | 148 | 131 | 121.5 | 122.4 | 160.5 | 21.6 | 20.8 | 35.6 | 13.4 | 267.5 | 21.8 | 159.3 | 65.5 | 33.1 | 170.3 | 114.7 | 298.9 | 147.9 | 79.3 | 364.5 | 182.9 | 206.5 | 127.7 | 147.6 | 159.4 | 132.8 | 147.1 | 126.6 | 161.5
1715 | 1570 | -5.1 | 0 | 0 | 147.8 | 130.8 | 121.4 | 122.4 | 160.4 | 21.6 | 20.8 | 35.5 | 18.6 | 270.7 | 20.7 | 159.1 | 65.5 | 33 | 170.2 | 114.5 | 298.5 | 147.5 | 79.1 | 364.3 | 182.7 | 206.3 | 127.7 | 147.5 | 159.2 | 132.7 | 146.9 | 126.5 | 161.4
1716 | 1571 | -4.4 | 0 | 0 | 147.4 | 130.6 | 121.3 | 122.3 | 160.2 | 21.5 | 20.8 | 35.5 | 13.1 | 263.5 | 21.3 | 159 | 65.4 | 33 | 169.9 | 114.4 | 298.2 | 147.1 | 79.1 | 364 | 182.2 | 206.1 | 127.5 | 147.4 | 159.1 | 132.5 | 146.7 | 126.5 | 161.2
1717 | 1572 | -5.6 | 0 | 0 | 147 | 130.5 | 121.1 | 122 | 160 | 21.5 | 20.8 | 35.6 | 12.6 | 258.4 | 23 | 158.9 | 65.3 | 33 | 169.7 | 114.2 | 297.9 | 146.7 | 78.6 | 363.8 | 182 | 206 | 127.4 | 147.3 | 159 | 132.4 | 146.5 | 126.4 | 161
1718 | 1573 | -6.1 | 0 | 0 | 146.8 | 130.6 | 121 | 121.8 | 159.8 | 21.5 | 20.8 | 35.6 | 9.6 | 237.7 | 25.4 | 158.8 | 65.1 | 33 | 169.5 | 114 | 297.5 | 146.6 | 78.5 | 363.6 | 181.7 | 205.8 | 127.2 | 147.1 | 158.8 | 132.2 | 146.3 | 126.1 | 160.9
1719 | 1574 | -6.1 | 0 | 0 | 146.5 | 130.5 | 120.9 | 121.5 | 159.5 | 21.4 | 20.8 | 35.6 | 12.1 | 224.8 | 24.8 | 158.6 | 64.9 | 33.1 | 169.3 | 113.8 | 297.3 | 146.6 | 78.3 | 363.4 | 181.5 | 205.6 | 127 | 146.9 | 158.7 | 132.1 | 146.2 | 126 | 160.7
1720 | 1575 | -5.9 | 0 | 0 | 146.2 | 130.3 | 120.8 | 121.4 | 159.4 | 21.4 | 20.8 | 35.5 | 12.4 | 246.5 | 21 | 158.5 | 64.9 | 33.1 | 169.3 | 113.5 | 297 | 146.6 | 77.9 | 363.1 | 181.3 | 205.4 | 126.9 | 146.8 | 158.6 | 131.9 | 146 | 125.9 | 160.6
1721 | 1576 | -5.7 | 0 | 0 | 146 | 130 | 120.7 | 121.2 | 159.2 | 21.4 | 20.8 | 35.5 | 14.2 | 241.9 | 21.4 | 158.3 | 64.7 | 33 | 169.2 | 113.5 | 296.7 | 146.2 | 77.7 | 362.2 | 181.2 | 205.3 | 126.7 | 146.7 | 158.5 | 131.8 | 145.9 | 125.8 | 160.4
1722 | 1577 | -6 | 0 | 0 | 145.7 | 129.8 | 120.5 | 121 | 159 | 21.4 | 20.8 | 35.5 | 9.3 | 240.5 | 24.6 | 158.1 | 64.8 | 33 | 169.1 | 113.3 | 296.4 | 145.8 | 77.6 | 361.8 | 180.9 | 205.1 | 126.5 | 146.5 | 158.3 | 131.6 | 145.8 | 125.6 | 160.3
1723 | 1578 | -6.1 | 0 | 0 | 145.4 | 129.5 | 120.3 | 120.8 | 158.8 | 21.3 | 20.8 | 35.4 | 4.3 | 233.8 | 28.3 | 157.9 | 65.1 | 32.9 | 169 | 113.2 | 296.1 | 145.5 | 77.4 | 361.1 | 180.5 | 204.9 | 126.3 | 146.3 | 158.2 | 131.5 | 145.7 | 125.4 | 160.1
1724 | 1579 | -6.4 | 0 | 0 | 145.3 | 129.4 | 120.2 | 120.6 | 158.6 | 21.2 | 20.8 | 35.5 | 5.3 | 249.3 | 28 | 157.5 | 65.1 | 32.8 | 168.9 | 113.1 | 295.8 | 145.4 | 77.6 | 360.7 | 180.3 | 204.7 | 126.3 | 146.2 | 158 | 131.3 | 145.6 | 125.1 | 159.9
1725 | 1580 | -6.7 | 0 | 0 | 145.4 | 129.3 | 120.1 | 120.4 | 158.5 | 21.2 | 20.8 | 35.4 | 8.5 | 247.4 | 22.4 | 157 | 64.8 | 32.8 | 168.9 | 112.9 | 295.5 | 145.2 | 77.5 | 360.2 | 180.1 | 204.6 | 126.3 | 146 | 157.7 | 131.2 | 145.4 | 125 | 159.8
1726 | 1581 | -6.6 | 0 | 0 | 145.5 | 129.1 | 120 | 120.2 | 158.3 | 21.1 | 20.8 | 35.3 | 10.4 | 260 | 22.2 | 156.4 | 64.9 | 32.8 | 168.9 | 112.8 | 295.2 | 144.8 | 77.4 | 359.6 | 179.7 | 204.4 | 126.3 | 145.9 | 157.6 | 131.1 | 145.2 | 124.9 | 159.7
1727 | 1582 | -6.7 | 0 | 0 | 145.2 | 129 | 120 | 120.1 | 158.2 | 21.1 | 20.8 | 35.2 | 9.3 | 258.1 | 21.1 | 155.9 | 64.8 | 32.8 | 168.3 | 112.7 | 294.8 | 144.2 | 77.2 | 359 | 179.5 | 204.2 | 126.1 | 145.8 | 157.5 | 130.9 | 145.1 | 124.7 | 159.5
1728 | 1583 | -6.8 | 0 | 0 | 145.2 | 129.2 | 119.9 | 119.9 | 158.1 | 21.1 | 20.8 | 35.2 | 13.3 | 247.8 | 17.2 | 155.3 | 64.7 | 32.8 | 168 | 112.5 | 294.4 | 143.8 | 77.2 | 358.6 | 179.4 | 204.1 | 125.9 | 145.7 | 157.4 | 130.8 | 145 | 124.6 | 159.3
1729 | 1584 | -6.6 | 0 | 0 | 145 | 129.2 | 119.8 | 119.7 | 158 | 21 | 20.8 | 35.2 | 10.7 | 247.2 | 14.8 | 154.7 | 64.5 | 32.7 | 167.7 | 112.3 | 294 | 143.6 | 77 | 358.1 | 179.1 | 203.9 | 125.8 | 145.6 | 157.3 | 130.6 | 144.9 | 124.6 | 159.1
1730 | 1585 | -6.2 | 0 | 0 | 144.8 | 129.1 | 119.7 | 119.5 | 157.8 | 20.9 | 20.8 | 35.1 | 9.3 | 255.9 | 22 | 154.4 | 64.4 | 32.7 | 166.9 | 112.2 | 293.6 | 143.7 | 76.7 | 357.8 | 178.7 | 203.7 | 125.6 | 145.4 | 157.1 | 130.5 | 144.7 | 124.4 | 159
1731 | 1586 | -6.4 | 0 | 0 | 144.6 | 129 | 119.6 | 119.3 | 157.6 | 20.8 | 20.8 | 35.1 | 7.6 | 259 | 28.3 | 154 | 64.2 | 32.6 | 167 | 112 | 293.1 | 143.2 | 76.6 | 357.4 | 178.5 | 203.5 | 125.4 | 145.3 | 157 | 130.3 | 144.5 | 124.2 | 158.8
1732 | 1587 | -6.4 | 0 | 0 | 144.3 | 128.8 | 119.5 | 119.2 | 157.4 | 20.8 | 20.8 | 35.1 | 8 | 255.6 | 23.5 | 153.6 | 64.2 | 32.6 | 167.1 | 111.8 | 292.6 | 142.8 | 76.6 | 356.9 | 178.3 | 203.4 | 125.2 | 145.2 | 156.9 | 130.2 | 144.4 | 124 | 158.7
1733 | 1588 | -6.5 | 0 | 0 | 144 | 128.5 | 119.3 | 119 | 157.3 | 20.7 | 20.8 | 35 | 13 | 254.2 | 19.3 | 153.2 | 63.8 | 32.5 | 167.1 | 111.7 | 292.1 | 142.5 | 76.5 | 356.4 | 177.9 | 203.2 | 125 | 145.1 | 156.8 | 130 | 144.3 | 124 | 158.5
1734 | 1589 | -6.7 | 0 | 0 | 144 | 128.3 | 119.2 | 118.9 | 157.1 | 20.7 | 20.8 | 34.9 | 11.8 | 246.9 | 14.7 | 152.7 | 63.7 | 32.5 | 167.2 | 111.5 | 291.7 | 142.3 | 76.3 | 356.1 | 177.5 | 203 | 124.8 | 144.9 | 156.6 | 129.9 | 144.1 | 123.9 | 158.4
1735 | 1590 | -6.8 | 0 | 0 | 143.8 | 128.1 | 119 | 118.8 | 157 | 20.8 | 20.9 | 34.7 | 13.3 | 238.3 | 13.4 | 152.2 | 63.8 | 32.5 | 167.1 | 111.4 | 291.3 | 142 | 76.4 | 355.8 | 177.4 | 202.8 | 124.6 | 144.8 | 156.4 | 129.7 | 144 | 123.9 | 158.2
1736 | 1591 | -6.9 | 0 | 0 | 143.6 | 127.9 | 118.9 | 118.6 | 157 | 20.7 | 20.9 | 34.6 | 13.9 | 255.6 | 13.7 | 151.8 | 63.7 | 32.4 | 167 | 111.2 | 290.8 | 141.9 | 76.5 | 355.5 | 177.1 | 202.7 | 124.4 | 144.6 | 156.1 | 129.6 | 143.9 | 123.8 | 158.1
1737 | 1592 | -6.7 | 0 | 0 | 143.2 | 127.8 | 118.7 | 118.4 | 156.9 | 20.7 | 20.9 | 34.5 | 16.7 | 249.6 | 21.9 | 151.6 | 63.7 | 32.4 | 166.8 | 111 | 290.3 | 142 | 76.1 | 355.2 | 176.7 | 202.5 | 124.3 | 144.4 | 155.9 | 129.4 | 143.9 | 123.6 | 158
1738 | 1593 | -6.6 | 0 | 0 | 143.1 | 127.7 | 118.6 | 118.3 | 156.8 | 20.7 | 20.9 | 34.4 | 17 | 241.5 | 28.9 | 151.4 | 63.3 | 32.4 | 166.7 | 110.9 | 290 | 142 | 76.2 | 354.8 | 176.5 | 202.3 | 124.1 | 144.3 | 155.8 | 129.3 | 143.7 | 123.4 | 157.9
1739 | 1594 | -6.7 | 0 | 0 | 142.8 | 127.6 | 118.5 | 118.2 | 156.7 | 20.7 | 20.9 | 34.3 | 20.1 | 239.7 | 28.7 | 151.1 | 63.2 | 32.3 | 166.3 | 110.7 | 289.6 | 141.9 | 76.3 | 354.7 | 176.4 | 202.2 | 123.9 | 144.1 | 155.7 | 129.2 | 143.6 | 123.3 | 157.7
1740 | 1595 | -6.5 | 0 | 0 | 142.9 | 127.6 | 118.4 | 118 | 156.5 | 20.8 | 20.9 | 34.3 | 15.6 | 244.7 | 30.9 | 150.9 | 63.2 | 32.3 | 165.9 | 110.6 | 289.2 | 141.7 | 76.3 | 354.4 | 176.3 | 202 | 123.8 | 144 | 155.5 | 129 | 143.4 | 123.2 | 157.6
1741 | 1596 | -6.3 | 0 | 0 | 142.9 | 127.4 | 118.3 | 117.9 | 156.4 | 20.8 | 20.9 | 34.3 | 14.8 | 241.3 | 30.5 | 150.7 | 63.3 | 32.2 | 164.7 | 110.3 | 288.8 | 141.6 | 76.1 | 353.9 | 176 | 201.8 | 123.6 | 143.9 | 155.4 | 128.9 | 143.3 | 123.1 | 157.4
1742 | 1597 | -6.1 | 0 | 0 | 143.1 | 127.2 | 118.2 | 117.8 | 156.2 | 20.8 | 20.9 | 34.2 | 11.8 | 244.8 | 28.8 | 150.4 | 63.1 | 32.1 | 164.5 | 110.2 | 288.4 | 141.6 | 76.1 | 353.7 | 175.8 | 201.6 | 123.5 | 143.7 | 155.2 | 128.7 | 143.1 | 122.9 | 157.2
1743 | 1598 | -6.4 | 0 | 0 | 143.1 | 127.2 | 118.1 | 117.6 | 156 | 20.8 | 20.9 | 34.1 | 10.4 | 242.6 | 29.5 | 150.4 | 63.1 | 32 | 164.2 | 110 | 288 | 141.3 | 76 | 353.3 | 175.5 | 201.5 | 123.4 | 143.6 | 155.1 | 128.6 | 143 | 122.7 | 157.1
1744 | 1599 | -6.5 | 0 | 0 | 142.9 | 127.2 | 118 | 117.4 | 155.8 | 20.8 | 20.9 | 34.1 | 13.1 | 248.7 | 26.2 | 150.6 | 62.9 | 31.9 | 164.2 | 109.8 | 287.7 | 141.2 | 75.7 | 353 | 175.1 | 201.3 | 123.2 | 143.5 | 154.9 | 128.4 | 142.8 | 122.5 | 156.9
1745 | 1600 | -6.5 | 0 | 0 | 142.7 | 127.1 | 117.9 | 117.1 | 155.6 | 20.8 | 20.9 | 34 | 12.7 | 273.4 | 19.1 | 150.7 | 62.7 | 31.8 | 164.1 | 109.8 | 287.3 | 140.9 | 75.4 | 352.2 | 174.9 | 201.1 | 123.1 | 143.4 | 154.8 | 128.3 | 142.7 | 122.4 | 156.8
1746 | 1601 | -6.5 | 0 | 0 | 142.4 | 126.9 | 117.7 | 117 | 155.5 | 20.8 | 20.9 | 34 | 11.3 | 247.7 | 18.2 | 150.8 | 63 | 31.8 | 163.9 | 109.5 | 286.8 | 141 | 75.2 | 351.4 | 174.6 | 201 | 123 | 143.3 | 154.6 | 128.2 | 142.6 | 122.3 | 156.7
1747 | 1602 | -6.4 | 0 | 0 | 142.1 | 126.8 | 117.6 | 116.9 | 155.4 | 20.7 | 20.9 | 33.9 | 9.9 | 246.3 | 20.2 | 150.9 | 63 | 31.7 | 163.3 | 109.2 | 286.4 | 140.4 | 75 | 351.1 | 174.4 | 200.8 | 122.9 | 143.1 | 154.5 | 128 | 142.4 | 122 | 156.6
1748 | 1603 | -6.4 | 0 | 0 | 141.9 | 126.7 | 117.5 | 116.9 | 155.3 | 20.7 | 20.9 | 33.9 | 7.7 | 243.8 | 22.9 | 151 | 63 | 31.7 | 163.1 | 109 | 285.9 | 139.8 | 74.8 | 350.5 | 174.1 | 200.6 | 122.7 | 143 | 154.3 | 127.9 | 142.2 | 121.8 | 156.4
1749 | 1604 | -6.4 | 0 | 0 | 141.9 | 126.6 | 117.3 | 116.7 | 155 | 20.8 | 20.9 | 33.9 | 10.3 | 242.9 | 30.2 | 151.1 | 63 | 31.6 | 162.8 | 108.8 | 285.5 | 139.3 | 74.8 | 350.4 | 173.9 | 200.5 | 122.5 | 142.8 | 154.2 | 127.7 | 142.1 | 121.7 | 156.3
1750 | 1605 | -6.3 | 0 | 0 | 141.6 | 126.6 | 117.1 | 116.5 | 154.2 | 20.9 | 20.9 | 33.9 | 11.1 | 234.8 | 25.1 | 151.1 | 63 | 31.5 | 162.3 | 108.6 | 285.2 | 139.3 | 74.8 | 350.1 | 173.5 | 200.3 | 122.3 | 142.7 | 154.1 | 127.6 | 141.9 | 121.5 | 156.1
1751 | 1606 | -6.3 | 0 | 0 | 141.2 | 126.3 | 116.9 | 116.5 | 153.6 | 21 | 20.9 | 33.8 | 10 | 246.5 | 22.1 | 151 | 63 | 31.4 | 161.8 | 108.3 | 284.8 | 139.3 | 74.3 | 349.3 | 173.2 | 200.1 | 122.2 | 142.5 | 154 | 127.5 | 141.8 | 121.5 | 156
1752 | 1607 | -6.7 | 0 | 0 | 140.8 | 126 | 116.8 | 116.6 | 153.6 | 21.1 | 20.9 | 33.7 | 11.1 | 249.3 | 19.6 | 150.9 | 62.9 | 31.3 | 161.3 | 108.2 | 284.4 | 139.1 | 74 | 348.6 | 173 | 200 | 122 | 142.4 | 153.9 | 127.3 | 141.7 | 121.5 | 155.9
1753 | 1608 | -6.7 | 0 | 0 | 140.4 | 125.8 | 116.7 | 116.6 | 153.6 | 21.2 | 20.9 | 33.7 | 10.1 | 246.1 | 20.4 | 150.9 | 62.8 | 31.3 | 161 | 107.9 | 284 | 138.7 | 73.8 | 348.2 | 172.7 | 199.8 | 121.9 | 142.2 | 153.8 | 127.2 | 141.5 | 121.5 | 155.7
1754 | 1609 | -6.7 | 0 | 0 | 140.1 | 125.7 | 116.6 | 116.5 | 153.6 | 21.2 | 20.9 | 33.6 | 10.4 | 235.6 | 20 | 150.9 | 62.8 | 31.2 | 160.7 | 107.8 | 283.6 | 138.4 | 73.5 | 347.9 | 172.6 | 199.6 | 121.7 | 142.1 | 153.6 | 127 | 141.3 | 121.2 | 155.5
1755 | 1610 | -4.9 | 0 | 0 | 139.7 | 125.7 | 116.5 | 116.4 | 153.5 | 21.2 | 20.9 | 33.6 | 12 | 227.6 | 22.2 | 150.8 | 63.1 | 31.2 | 160.3 | 107.5 | 283.2 | 138.1 | 73.2 | 347.7 | 172.4 | 199.5 | 121.5 | 142 | 153.5 | 126.9 | 141.2 | 121.1 | 155.4
1756 | 1611 | -4.1 | 0 | 0 | 139.4 | 125.6 | 116.4 | 116.2 | 153.1 | 21.3 | 20.9 | 33.6 | 10.9 | 234.6 | 21.4 | 150.7 | 63.1 | 31.1 | 159.9 | 107.3 | 282.9 | 137.8 | 73.1 | 347.1 | 172.1 | 199.3 | 121.3 | 141.9 | 153.4 | 126.7 | 141.1 | 120.8 | 155.2
1757 | 1612 | -4.8 | 0 | 0 | 139.4 | 125.3 | 116.4 | 116.1 | 152.7 | 21.3 | 20.9 | 33.5 | 8.6 | 246.4 | 15.4 | 150.5 | 63.1 | 31.1 | 159.4 | 107 | 282.5 | 137.9 | 73 | 346.8 | 172.1 | 199.1 | 121.2 | 141.7 | 153.2 | 126.6 | 140.9 | 120.7 | 155.1
1758 | 1613 | -5.2 | 0 | 0 | 139.2 | 125.2 | 116.3 | 115.9 | 152.5 | 21.3 | 20.9 | 33.5 | 7.8 | 243.6 | 20.9 | 150.5 | 63 | 31 | 159.2 | 106.7 | 282 | 137.9 | 73.1 | 346.8 | 171.9 | 198.9 | 121 | 141.6 | 153.2 | 126.4 | 140.7 | 120.5 | 154.9
1759 | 1614 | -5.3 | 0 | 0 | 139 | 125 | 116.1 | 115.7 | 152.5 | 21.3 | 20.9 | 33.5 | 9.1 | 242 | 27.1 | 150.4 | 63.1 | 30.9 | 159.1 | 106.5 | 281.5 | 137.9 | 73.3 | 346.7 | 171.8 | 198.8 | 120.9 | 141.4 | 153 | 126.3 | 140.6 | 120.5 | 154.8
1760 | 1615 | -5.2 | 0 | 0 | 138.9 | 124.7 | 116 | 115.5 | 152.5 | 21.2 | 20.9 | 33.5 | 8.8 | 250.3 | 26.1 | 150.2 | 63 | 30.9 | 158.8 | 106.3 | 281 | 137.6 | 73.2 | 346.4 | 171.7 | 198.6 | 120.7 | 141.3 | 152.9 | 126.2 | 140.5 | 120.2 | 154.6
1761 | 1616 | -6 | 0 | 0 | 138.8 | 124.4 | 115.8 | 115.3 | 152.3 | 21.1 | 20.9 | 33.4 | 8.2 | 250.6 | 28 | 150 | 62.7 | 31 | 158.6 | 106.1 | 280.6 | 137.5 | 73 | 346 | 171.5 | 198.4 | 120.5 | 141.2 | 152.7 | 126 | 140.4 | 120 | 154.5
1762 | 1617 | -6.6 | 0 | 0 | 138.9 | 124.1 | 115.7 | 115.1 | 152.2 | 21.1 | 20.9 | 33.4 | 5.4 | 267.5 | 25 | 149.9 | 62.4 | 31 | 158.4 | 106 | 280.3 | 137.2 | 72.8 | 345.4 | 171.2 | 198.3 | 120.4 | 141 | 152.5 | 125.9 | 140.3 | 119.7 | 154.3
1763 | 1618 | -6.7 | 0 | 0 | 138.7 | 124 | 115.7 | 115 | 152.1 | 21 | 20.9 | 33.5 | 6.1 | 243.1 | 22.7 | 149.7 | 62.4 | 30.9 | 158.1 | 105.8 | 279.9 | 137.2 | 72.5 | 345.1 | 171.1 | 198.1 | 120.2 | 140.9 | 152.4 | 125.7 | 140.1 | 119.7 | 154.2
1764 | 1619 | -6.7 | 0 | 0 | 138.4 | 123.8 | 115.6 | 115 | 152 | 21 | 20.9 | 33.5 | 7.1 | 242.1 | 19 | 149.5 | 62.4 | 30.8 | 157.7 | 105.6 | 279.5 | 137.2 | 72.3 | 345 | 170.9 | 197.9 | 120 | 140.8 | 152.2 | 125.6 | 140 | 119.5 | 154
1765 | 1620 | -6.7 | 0 | 0 | 138.1 | 123.6 | 115.5 | 114.8 | 151.9 | 20.9 | 20.9 | 33.5 | 7.4 | 243.1 | 18.9 | 149.2 | 62.3 | 30.8 | 157.5 | 105.4 | 279.3 | 136.9 | 72.1 | 344.8 | 170.8 | 197.8 | 119.9 | 140.6 | 152.1 | 125.5 | 139.9 | 119.4 | 153.9
1766 | 1621 | -6.5 | 0 | 0 | 138 | 123.4 | 115.3 | 114.8 | 151.8 | 20.8 | 20.9 | 33.5 | 6.1 | 257 | 18.6 | 148.8 | 62.2 | 30.8 | 157.4 | 105.3 | 279 | 136.6 | 72.1 | 344.5 | 170.5 | 197.6 | 119.7 | 140.5 | 151.9 | 125.3 | 139.8 | 119.4 | 153.8
1767 | 1622 | -6.4 | 0 | 0 | 137.9 | 123.3 | 115.1 | 114.7 | 151.7 | 20.8 | 20.9 | 33.6 | 7.1 | 265.2 | 18 | 148.4 | 62 | 30.8 | 157.3 | 105 | 278.8 | 136.4 | 71.9 | 344.4 | 170.1 | 197.4 | 119.6 | 140.4 | 151.8 | 125.2 | 139.6 | 119.3 | 153.6
1768 | 1623 | -5.5 | 0 | 0 | 137.8 | 123.3 | 114.9 | 114.6 | 151.6 | 20.7 | 20.9 | 33.6 | 8.1 | 251.6 | 20 | 147.9 | 61.9 | 30.8 | 157 | 104.8 | 278.5 | 136.2 | 71.9 | 344.2 | 170.1 | 197.2 | 119.5 | 140.3 | 151.6 | 125 | 139.5 | 119.1 | 153.5
1769 | 1624 | -5.5 | 0 | 0 | 137.3 | 123.4 | 114.7 | 114.4 | 151.4 | 20.7 | 20.9 | 33.6 | 9 | 248.9 | 18.5 | 147.3 | 62.1 | 30.8 | 156.6 | 104.5 | 278.3 | 136.4 | 71.7 | 343.9 | 169.8 | 197.1 | 119.3 | 140.1 | 151.4 | 124.9 | 139.4 | 118.9 | 153.3
1770 | 1625 | -5.9 | 0 | 0 | 137 | 123.3 | 114.6 | 114.2 | 151.4 | 20.7 | 20.9 | 33.6 | 9.1 | 248.2 | 19.7 | 147 | 62.6 | 30.8 | 156.1 | 104.4 | 278 | 136 | 71.8 | 343.1 | 169.6 | 196.9 | 119.2 | 139.9 | 151.3 | 124.7 | 139.3 | 118.8 | 153.2
1771 | 1626 | -5.9 | 0 | 0 | 137.1 | 123.2 | 114.6 | 114 | 151.3 | 20.8 | 20.9 | 33.5 | 11.8 | 255 | 20.7 | 146.7 | 62.9 | 30.8 | 155.7 | 104.2 | 277.7 | 135.8 | 71.8 | 342.4 | 169.3 | 196.7 | 119.1 | 139.8 | 151.1 | 124.6 | 139.1 | 118.7 | 153
1772 | 1627 | -6 | 0 | 0 | 137 | 122.8 | 114.5 | 113.8 | 151.2 | 20.8 | 20.9 | 33.5 | 14.8 | 250.9 | 23.3 | 146.5 | 62.7 | 30.8 | 155.2 | 103.9 | 277.2 | 135.6 | 71.5 | 342.2 | 169.1 | 196.6 | 119.1 | 139.6 | 151 | 124.5 | 139 | 118.5 | 152.9
1773 | 1628 | -5.8 | 0 | 0 | 137 | 122.6 | 114.4 | 113.6 | 151.1 | 20.9 | 20.9 | 33.5 | 18.1 | 251.7 | 26 | 146.1 | 62.9 | 30.8 | 155 | 103.8 | 276.9 | 135.3 | 71.4 | 341.7 | 168.8 | 196.4 | 119 | 139.5 | 150.9 | 124.3 | 138.9 | 118.2 | 152.7
1774 | 1629 | -6 | 0 | 0 | 136.8 | 122.5 | 114.3 | 113.4 | 150.9 | 20.9 | 20.9 | 33.5 | 13.3 | 240.9 | 20.5 | 145.6 | 62.8 | 30.8 | 155 | 103.6 | 276.5 | 135.2 | 71.2 | 341.3 | 168.6 | 196.2 | 118.9 | 139.3 | 150.8 | 124.1 | 138.7 | 118 | 152.6
1775 | 1630 | -6.3 | 0 | 0 | 136.8 | 122.5 | 114.1 | 113.3 | 150.8 | 20.9 | 20.9 | 33.4 | 7 | 237.4 | 19.4 | 145.2 | 63.1 | 30.7 | 155.1 | 103.4 | 276.1 | 134.9 | 71.1 | 340.8 | 168.4 | 196.1 | 118.8 | 139.2 | 150.7 | 124 | 138.5 | 117.8 | 152.4
1776 | 1631 | -6.4 | 0 | 0 | 136.7 | 122.3 | 113.9 | 113.2 | 150.6 | 20.8 | 20.9 | 33.4 | 6.3 | 248.2 | 24.5 | 144.7 | 62.9 | 30.6 | 155 | 103.3 | 275.6 | 134.7 | 71.1 | 340.5 | 168.3 | 195.9 | 118.6 | 139.1 | 150.6 | 123.9 | 138.4 | 117.7 | 152.3
1777 | 1632 | -6.4 | 0 | 0 | 136.4 | 122.1 | 113.8 | 113.1 | 150.5 | 20.8 | 20.9 | 33.3 | 10.8 | 266.8 | 22.9 | 144.3 | 63 | 30.6 | 154.4 | 103.1 | 275 | 134.3 | 71 | 340.3 | 168.2 | 195.7 | 118.5 | 139 | 150.4 | 123.8 | 138.3 | 117.5 | 152.2
1778 | 1633 | -6.5 | 0 | 0 | 136.3 | 122 | 113.6 | 112.9 | 150.3 | 20.8 | 20.9 | 33.2 | 9.6 | 269.3 | 23.7 | 143.8 | 63 | 30.5 | 154.8 | 103 | 274.5 | 134.2 | 71 | 340 | 168.2 | 195.6 | 118.3 | 138.8 | 150.2 | 123.6 | 138.2 | 117.4 | 152
1779 | 1634 | -6.6 | 0 | 0 | 136.3 | 121.9 | 113.6 | 112.7 | 150.2 | 20.9 | 20.9 | 33.2 | 9.5 | 258.2 | 24.3 | 143.6 | 62.8 | 30.4 | 154.8 | 102.9 | 274 | 134.1 | 70.9 | 339.5 | 168 | 195.4 | 118.2 | 138.7 | 150 | 123.5 | 138.1 | 117.3 | 151.9
1780 | 1635 | -6.4 | 0 | 0 | 136.2 | 121.9 | 113.5 | 112.5 | 150.1 | 20.8 | 20.9 | 33.2 | 9.4 | 254 | 20.9 | 143.5 | 62.6 | 30.4 | 154.7 | 102.7 | 273.5 | 134 | 70.8 | 339.3 | 167.9 | 195.2 | 118.1 | 138.6 | 149.8 | 123.4 | 138 | 117.1 | 151.7
1781 | 1636 | -5.8 | 0 | 0 | 136 | 121.8 | 113.5 | 112.3 | 149.9 | 20.7 | 20.9 | 33.2 | 11.5 | 254.5 | 19.5 | 143.5 | 62.6 | 30.3 | 154.6 | 102.6 | 273.1 | 134.1 | 70.7 | 338.8 | 167.5 | 195.1 | 117.9 | 138.4 | 149.7 | 123.2 | 137.9 | 116.9 | 151.6
1782 | 1637 | -6.1 | 0 | 0 | 135.6 | 121.8 | 113.4 | 112.2 | 149.8 | 20.6 | 20.9 | 33.3 | 9.9 | 255.3 | 18.7 | 143.6 | 62.1 | 30.2 | 154.4 | 102.4 | 272.7 | 134 | 70.7 | 338.5 | 167.2 | 194.9 | 117.7 | 138.3 | 149.5 | 123.1 | 137.8 | 116.8 | 151.5
1783 | 1638 | -6.2 | 0 | 0 | 135.3 | 121.9 | 113.2 | 112 | 149.6 | 20.6 | 20.9 | 33.3 | 7.7 | 246.8 | 16.1 | 143.6 | 61.8 | 30.1 | 154.2 | 102.4 | 272.4 | 134.1 | 70.7 | 338.1 | 166.9 | 194.7 | 117.5 | 138.1 | 149.3 | 122.9 | 137.7 | 116.6 | 151.3
1784 | 1639 | -6.2 | 0 | 0 | 135 | 121.7 | 113 | 111.9 | 149.4 | 20.7 | 20.9 | 33.4 | 6.4 | 268.8 | 23.4 | 143.5 | 61.6 | 30 | 153.6 | 102.3 | 272.1 | 133.7 | 70.5 | 337.6 | 166.5 | 194.6 | 117.4 | 138 | 149.2 | 122.8 | 137.6 | 116.5 | 151.2
1785 | 1640 | -6.2 | 0 | 0 | 134.9 | 121.4 | 112.9 | 111.8 | 149.3 | 20.7 | 20.9 | 33.4 | 5.8 | 249.4 | 25.2 | 143.4 | 61.6 | 30 | 153.5 | 102.1 | 271.8 | 133.3 | 70.4 | 337.3 | 166.3 | 194.4 | 117.3 | 137.8 | 149.1 | 122.7 | 137.4 | 116.3 | 151.1
1786 | 1641 | -6.2 | 0 | 0 | 134.7 | 121.3 | 112.8 | 111.7 | 149.1 | 20.8 | 20.9 | 33.4 | 5.6 | 254.1 | 24.1 | 143.2 | 61.6 | 29.9 | 153.3 | 102 | 271.5 | 133.1 | 70.4 | 337.1 | 166.1 | 194.2 | 117.2 | 137.7 | 149.1 | 122.5 | 137.3 | 116.1 | 150.9
1787 | 1642 | -6 | 0 | 0 | 134.6 | 121.2 | 112.7 | 111.5 | 149 | 20.8 | 20.9 | 33.5 | 9.9 | 240.6 | 21.4 | 142.8 | 61.3 | 29.9 | 153.3 | 102 | 271.2 | 133.1 | 70.5 | 337 | 165.8 | 194 | 117 | 137.5 | 148.9 | 122.4 | 137.2 | 116.1 | 150.8
1788 | 1643 | -6.3 | 0 | 0 | 134.8 | 121 | 112.6 | 111.4 | 148.9 | 20.8 | 20.9 | 33.5 | 15.9 | 235.5 | 16.8 | 142.3 | 60.9 | 29.9 | 153.2 | 101.9 | 270.9 | 133.3 | 70.5 | 336.9 | 165.6 | 193.9 | 116.9 | 137.4 | 148.7 | 122.2 | 137 | 116.1 | 150.7
1789 | 1644 | -6.1 | 0 | 0 | 135 | 120.8 | 112.4 | 111.3 | 148.7 | 20.9 | 20.9 | 33.5 | 12.1 | 246.2 | 12.3 | 141.9 | 60.5 | 29.9 | 153.1 | 101.7 | 270.6 | 133.3 | 70.6 | 336.9 | 165.3 | 193.7 | 116.7 | 137.2 | 148.6 | 122.1 | 136.9 | 116 | 150.5
1790 | 1645 | -5.8 | 0 | 0 | 135.3 | 120.6 | 112.3 | 111.1 | 148.5 | 20.9 | 20.9 | 33.5 | 10.8 | 253.1 | 11 | 141.5 | 60.1 | 29.9 | 153 | 101.6 | 270.3 | 133.1 | 70.6 | 336.8 | 165.2 | 193.5 | 116.5 | 137.1 | 148.4 | 122 | 136.8 | 116 | 150.4
1791 | 1646 | -5.9 | 0 | 0 | 135.1 | 120.4 | 112.2 | 111 | 148.4 | 21 | 20.9 | 33.5 | 7.7 | 253.7 | 13.6 | 141.1 | 59.7 | 29.9 | 152.8 | 101.4 | 270 | 132.7 | 70.5 | 336.6 | 164.9 | 193.4 | 116.4 | 136.9 | 148.3 | 121.9 | 136.7 | 116 | 150.2
1792 | 1647 | -6 | 0 | 0 | 135.3 | 120.2 | 112 | 110.9 | 148.3 | 21 | 20.9 | 33.5 | 8.5 | 248.7 | 13.6 | 140.9 | 59.6 | 29.9 | 152.6 | 101.1 | 269.7 | 132.7 | 70.3 | 336.4 | 164.7 | 193.2 | 116.3 | 136.8 | 148.2 | 121.7 | 136.6 | 115.8 | 150.1
1793 | 1648 | -6.1 | 0 | 0 | 134.9 | 120.1 | 111.9 | 110.8 | 148.2 | 21.1 | 20.9 | 33.4 | 12.6 | 245.5 | 21.5 | 140.7 | 59.5 | 29.9 | 152.5 | 101 | 269.3 | 133 | 70 | 336.3 | 164.4 | 193 | 116.2 | 136.7 | 148.1 | 121.6 | 136.3 | 115.6 | 149.9
1794 | 1649 | -6.1 | 0 | 0 | 134.5 | 120 | 111.7 | 110.7 | 148.1 | 21.1 | 20.9 | 33.4 | 9.8 | 245.4 | 21.6 | 140.5 | 59.7 | 29.9 | 152.4 | 100.9 | 269 | 133.3 | 69.9 | 336.3 | 164.4 | 192.9 | 116 | 136.6 | 148 | 121.4 | 136.1 | 115.6 | 149.8
1795 | 1650 | -5.7 | 0 | 0 | 134.2 | 119.9 | 111.6 | 110.6 | 148 | 21.1 | 20.9 | 33.4 | 8.6 | 245.4 | 20.5 | 140.4 | 59.6 | 29.9 | 152.1 | 100.7 | 268.7 | 133.4 | 70 | 336.1 | 164.2 | 192.7 | 115.9 | 136.5 | 148 | 121.3 | 135.9 | 115.5 | 149.7
1796 | 1651 | -5.8 | 0 | 0 | 134 | 119.7 | 111.4 | 110.5 | 148 | 21.1 | 20.9 | 33.4 | 10.4 | 237.5 | 21.1 | 140.3 | 59.3 | 29.8 | 152 | 100.5 | 268.3 | 133.4 | 70 | 335.7 | 164.1 | 192.5 | 115.8 | 136.3 | 147.8 | 121.2 | 135.8 | 115.3 | 149.5
1797 | 1652 | -6.2 | 0 | 0 | 133.8 | 119.7 | 111.2 | 110.4 | 147.9 | 21.1 | 20.9 | 33.3 | 10.9 | 243.4 | 19.7 | 140.3 | 59.4 | 29.9 | 151.8 | 100.3 | 268 | 133.4 | 70 | 335.4 | 163.9 | 192.4 | 115.7 | 136.1 | 147.6 | 121 | 135.7 | 115 | 149.4
1798 | 1653 | -6.5 | 0 | 0 | 133.7 | 119.8 | 111 | 110.4 | 147.7 | 21 | 20.9 | 33.2 | 11.4 | 245.7 | 21.3 | 140.1 | 59.6 | 30 | 151.5 | 100.2 | 267.8 | 133 | 70.1 | 335.1 | 163.7 | 192.2 | 115.7 | 136 | 147.4 | 120.9 | 135.6 | 114.8 | 149.2
1799 | 1654 | -6.6 | 0 | 0 | 133.5 | 119.8 | 110.9 | 110.3 | 147.5 | 21 | 20.9 | 33.1 | 12 | 264.9 | 22.2 | 139.8 | 59.6 | 30 | 151.2 | 100 | 267.5 | 133 | 70 | 334.7 | 163.4 | 192 | 115.6 | 135.8 | 147.2 | 120.8 | 135.5 | 114.6 | 149.1
1800 | 1655 | -6.6 | 0 | 0 | 133.1 | 119.6 | 110.8 | 110.2 | 147.4 | 21.1 | 20.9 | 33.1 | 11.2 | 243.8 | 21.2 | 139.6 | 59.5 | 30 | 151 | 99.9 | 267.2 | 133.3 | 69.9 | 334.3 | 163.1 | 191.9 | 115.5 | 135.7 | 147 | 120.6 | 135.4 | 114.6 | 148.9
1801 | 1656 | -6.7 | 0 | 0 | 132.8 | 119.5 | 110.7 | 110.1 | 147.3 | 21 | 20.9 | 33 | 8.8 | 235.8 | 19.6 | 139.3 | 59.5 | 30 | 150.9 | 99.8 | 266.9 | 133.3 | 69.8 | 334 | 162.9 | 191.7 | 115.4 | 135.5 | 146.8 | 120.5 | 135.3 | 114.6 | 148.8
1802 | 1657 | -6.7 | 0 | 0 | 132.4 | 119.4 | 110.5 | 109.8 | 147.1 | 21 | 20.9 | 32.9 | 9.4 | 245.1 | 24.9 | 138.8 | 59.3 | 30 | 150.8 | 99.7 | 266.6 | 132.9 | 69.7 | 333.9 | 162.7 | 191.5 | 115.2 | 135.3 | 146.7 | 120.4 | 135.2 | 114.4 | 148.7
1803 | 1658 | -6.8 | 0 | 0 | 132.3 | 119.3 | 110.4 | 109.8 | 146.6 | 21 | 20.9 | 32.9 | 11.6 | 239.4 | 28.9 | 138.3 | 59.2 | 29.9 | 150.9 | 99.6 | 266.3 | 132.6 | 69.6 | 333.6 | 162.6 | 191.4 | 115.1 | 135.1 | 146.5 | 120.3 | 135.1 | 114.2 | 148.5
1804 | 1659 | -6.8 | 0 | 0 | 132.4 | 119.2 | 110.3 | 109.9 | 146.2 | 21.1 | 20.9 | 32.8 | 12.5 | 239.8 | 26.1 | 137.7 | 59.2 | 29.9 | 150.8 | 99.6 | 266 | 132.1 | 69.6 | 333.3 | 162.3 | 191.2 | 115.1 | 134.9 | 146.4 | 120.1 | 135 | 114.1 | 148.4
1805 | 1660 | -6.6 | 0 | 0 | 132.8 | 119 | 110.2 | 109.8 | 146 | 21.1 | 20.9 | 32.8 | 11.5 | 225.6 | 25.4 | 137.1 | 59.1 | 29.8 | 150.8 | 99.4 | 265.7 | 132.1 | 69.5 | 332.6 | 162 | 191 | 115 | 134.8 | 146.2 | 120 | 134.8 | 113.8 | 148.3
1806 | 1661 | -6.5 | 0 | 0 | 132.8 | 118.9 | 110.1 | 109.7 | 145.9 | 21.1 | 20.9 | 32.8 | 15.4 | 242.3 | 25.1 | 136.6 | 58.9 | 29.8 | 150.7 | 99.3 | 265.3 | 131.9 | 69.3 | 332.1 | 161.7 | 190.9 | 114.9 | 134.7 | 146.1 | 119.8 | 134.6 | 113.7 | 148.1
1807 | 1662 | -6.5 | 0 | 0 | 132.3 | 118.8 | 110 | 109.5 | 145.8 | 21.2 | 20.9 | 32.8 | 12.1 | 247 | 27 | 136.2 | 58.9 | 29.8 | 150.6 | 99.2 | 264.8 | 131.8 | 69.4 | 331.8 | 161.4 | 190.7 | 114.7 | 134.6 | 145.9 | 119.7 | 134.5 | 113.6 | 148
1808 | 1663 | -6.4 | 0 | 0 | 132 | 118.7 | 109.9 | 109.3 | 145.7 | 21.2 | 20.9 | 32.9 | 6.7 | 237.7 | 30.4 | 135.8 | 58.9 | 29.8 | 150.5 | 99 | 264.5 | 131.5 | 69.4 | 331.7 | 161.2 | 190.5 | 114.6 | 134.4 | 145.8 | 119.6 | 134.4 | 113.5 | 147.8
1809 | 1664 | -6.4 | 0 | 0 | 131.8 | 118.5 | 109.8 | 109 | 145.6 | 21.2 | 21 | 32.9 | 11.7 | 256.9 | 30.2 | 135.6 | 58.9 | 29.8 | 150.4 | 98.8 | 264.2 | 131.3 | 69.4 | 331.6 | 161.2 | 190.4 | 114.4 | 134.3 | 145.7 | 119.5 | 134.2 | 113.5 | 147.7
1810 | 1665 | -6.4 | 0 | 0 | 131.9 | 118.3 | 109.7 | 108.9 | 145.4 | 21.2 | 21 | 32.9 | 18.3 | 259.6 | 25 | 135.5 | 58.5 | 29.8 | 150.3 | 98.6 | 263.8 | 131 | 69 | 331.5 | 161.1 | 190.2 | 114.3 | 134.2 | 145.6 | 119.3 | 134 | 113.4 | 147.6
1811 | 1666 | -6.4 | 0 | 0 | 132 | 118.1 | 109.6 | 108.8 | 145.3 | 21.1 | 20.9 | 32.9 | 13.8 | 252.4 | 25.1 | 135.4 | 58.7 | 29.8 | 150 | 98.4 | 263.5 | 131.1 | 68.9 | 331.3 | 161 | 190 | 114.1 | 134 | 145.4 | 119.2 | 133.9 | 113.3 | 147.4
1812 | 1667 | -6.7 | 0 | 0 | 131.6 | 118 | 109.5 | 108.7 | 145.2 | 20.9 | 21 | 32.8 | 10.7 | 241 | 26.5 | 135.3 | 58.4 | 29.8 | 149.8 | 98.2 | 263.2 | 131.1 | 68.9 | 331.1 | 160.7 | 189.9 | 114 | 133.8 | 145.3 | 119 | 133.7 | 113.1 | 147.3
1813 | 1668 | -6.8 | 0 | 0 | 131 | 118 | 109.4 | 108.6 | 145.1 | 20.8 | 21 | 32.7 | 15.6 | 239.4 | 21.5 | 135.4 | 58.6 | 29.9 | 149.5 | 98 | 262.9 | 131.1 | 68.8 | 330.9 | 160.5 | 189.7 | 113.8 | 133.7 | 145.2 | 118.9 | 133.6 | 113 | 147.2
1814 | 1669 | -6.5 | 0 | 0 | 130.5 | 118 | 109.3 | 108.5 | 145 | 20.6 | 21 | 32.6 | 15.2 | 233.5 | 22.7 | 135.4 | 58.6 | 29.8 | 149.3 | 97.9 | 262.6 | 130.8 | 68.6 | 330.7 | 160.5 | 189.5 | 113.7 | 133.5 | 145.1 | 118.8 | 133.5 | 112.8 | 147.1
1815 | 1670 | -6.2 | 0 | 0 | 130.4 | 118 | 109.3 | 108.5 | 144.9 | 20.5 | 21 | 32.5 | 13.6 | 244.1 | 30 | 135.2 | 58.4 | 29.8 | 149.1 | 97.7 | 262.3 | 130.6 | 68.3 | 330.1 | 160.5 | 189.4 | 113.6 | 133.3 | 145 | 118.7 | 133.4 | 112.7 | 146.9
1816 | 1671 | -6.2 | 0 | 0 | 130.6 | 117.8 | 109.2 | 108.4 | 144.8 | 20.4 | 21 | 32.5 | 9.8 | 256.1 | 30.1 | 135.1 | 58.4 | 29.8 | 149 | 97.4 | 261.9 | 130.5 | 68.1 | 329.7 | 160.1 | 189.2 | 113.4 | 133.2 | 144.8 | 118.6 | 133.3 | 112.6 | 146.9
1817 | 1672 | -6.2 | 0 | 0 | 130.6 | 117.6 | 109.1 | 108.1 | 144.7 | 20.3 | 21 | 32.5 | 7.9 | 265.2 | 25.2 | 135.1 | 58.5 | 29.8 | 148.8 | 97.2 | 261.6 | 130.4 | 67.7 | 329.8 | 160 | 189.1 | 113.3 | 133 | 144.6 | 118.4 | 133.2 | 112.4 | 146.7
1818 | 1673 | -6 | 0 | 0 | 130.6 | 117.6 | 108.8 | 107.7 | 144.6 | 20.3 | 21 | 32.5 | 9 | 256.4 | 21.5 | 135 | 58.7 | 29.7 | 148.7 | 97 | 261.3 | 130.6 | 67.5 | 329.9 | 160.1 | 188.9 | 113.1 | 132.9 | 144.4 | 118.3 | 133.1 | 112.2 | 146.6
1819 | 1674 | -6 | 0 | 0 | 130.2 | 117.6 | 108.7 | 107.5 | 144.4 | 20.3 | 21 | 32.4 | 17.4 | 247.7 | 19.1 | 134.9 | 58.1 | 29.7 | 148.5 | 96.8 | 261 | 130.7 | 67.3 | 329.9 | 160 | 188.7 | 113 | 132.8 | 144.3 | 118.2 | 132.9 | 112.2 | 146.5
1820 | 1675 | -6.3 | 0 | 0 | 129.9 | 117.5 | 108.7 | 107.5 | 144.2 | 20.2 | 21 | 32.3 | 11.8 | 252.4 | 19.2 | 134.7 | 58 | 29.6 | 148.3 | 96.6 | 260.6 | 130.7 | 67.2 | 329.6 | 159.9 | 188.6 | 112.9 | 132.7 | 144.1 | 118.1 | 132.8 | 112.1 | 146.3
1821 | 1676 | -6.3 | 0 | 0 | 130 | 117.4 | 108.6 | 107.5 | 144.1 | 20.2 | 21 | 32.3 | 5.2 | 238.4 | 22.8 | 134.7 | 58.2 | 29.5 | 148 | 96.4 | 260.2 | 130.5 | 67.2 | 329.4 | 159.7 | 188.4 | 112.7 | 132.5 | 144 | 117.9 | 132.6 | 111.8 | 146.2
1822 | 1677 | -6.4 | 0 | 0 | 130.3 | 117.2 | 108.4 | 107.5 | 144.1 | 20.2 | 21 | 32.3 | 4.9 | 243.5 | 27.3 | 134.6 | 58.5 | 29.5 | 147.8 | 96.5 | 259.9 | 130.5 | 67.1 | 329 | 159.5 | 188.2 | 112.6 | 132.4 | 143.9 | 117.7 | 132.5 | 111.7 | 146
1823 | 1678 | -6.3 | 0 | 0 | 130.1 | 117.2 | 108.3 | 107.4 | 143.9 | 20.1 | 21 | 32.3 | 5.6 | 249.7 | 26.3 | 134.6 | 58.7 | 29.4 | 147.4 | 96.3 | 259.5 | 130.2 | 67.1 | 328.6 | 159.4 | 188.1 | 112.5 | 132.3 | 143.8 | 117.6 | 132.4 | 111.5 | 145.9
1824 | 1679 | -6.3 | 0 | 0 | 129.7 | 117.1 | 108.3 | 107.3 | 143.7 | 20.1 | 21 | 32.3 | 7.3 | 248.1 | 25.2 | 134.6 | 58.7 | 29.4 | 147.2 | 96.2 | 259.2 | 129.8 | 67 | 328.2 | 159.1 | 187.9 | 112.4 | 132.2 | 143.8 | 117.5 | 132.3 | 111.5 | 145.8
1825 | 1680 | -6.8 | 0 | 0 | 129.3 | 116.9 | 108.2 | 107.2 | 143.6 | 20.1 | 21 | 32.3 | 10.2 | 257.7 | 27 | 134.4 | 58.7 | 29.4 | 147 | 96.1 | 258.9 | 129.7 | 67 | 327.9 | 158.9 | 187.7 | 112.3 | 132.1 | 143.6 | 117.4 | 132.2 | 111.6 | 145.7
1826 | 1681 | -6.9 | 0 | 0 | 129.1 | 116.6 | 108.1 | 107.1 | 143.5 | 20.1 | 21 | 32.4 | 12.3 | 248.2 | 27.1 | 134 | 58.5 | 29.2 | 146.8 | 96.1 | 258.6 | 129.3 | 66.9 | 327.4 | 158.5 | 187.6 | 112.2 | 131.9 | 143.5 | 117.3 | 132.1 | 111.4 | 145.5
1827 | 1682 | -6.9 | 0 | 0 | 129.1 | 116.4 | 108 | 107 | 143.4 | 20.2 | 21 | 32.3 | 18.6 | 245.8 | 20.2 | 133.8 | 58.8 | 29.1 | 146.8 | 96 | 258.3 | 129.1 | 66.8 | 327.1 | 158.3 | 187.4 | 112 | 131.7 | 143.5 | 117.1 | 132 | 111.2 | 145.4
1828 | 1683 | -6.8 | 0 | 0 | 129.1 | 116.4 | 107.9 | 106.9 | 143.3 | 20.3 | 21 | 32.3 | 18.5 | 200.5 | 16.4 | 133.7 | 58.8 | 29 | 146.6 | 96 | 258 | 128.7 | 66.8 | 326.9 | 158.1 | 187.3 | 111.9 | 131.6 | 143.4 | 117 | 131.9 | 111.1 | 145.2
1829 | 1684 | -6.7 | 0 | 0 | 129 | 116.5 | 107.8 | 106.7 | 143 | 20.4 | 21 | 32.3 | 10.4 | 241.2 | 14 | 133.7 | 58.7 | 28.9 | 145.9 | 95.8 | 257.6 | 128.3 | 66.7 | 326.5 | 157.9 | 187.1 | 111.9 | 131.5 | 143.2 | 116.9 | 131.8 | 110.9 | 145.1
1830 | 1685 | -6.6 | 0 | 0 | 128.8 | 116.5 | 107.7 | 106.7 | 142.7 | 20.4 | 21 | 32.3 | 13.6 | 244.7 | 19.2 | 133.7 | 58.5 | 28.9 | 145.8 | 95.8 | 257.2 | 128.3 | 66.5 | 326.2 | 157.7 | 186.9 | 111.8 | 131.4 | 143 | 116.8 | 131.7 | 110.8 | 145
1831 | 1686 | -6.6 | 0 | 0 | 128.5 | 116.4 | 107.6 | 106.6 | 142.8 | 20.5 | 21 | 32.2 | 17.9 | 240.7 | 27.8 | 133.6 | 58.5 | 28.8 | 145.8 | 95.6 | 256.9 | 128.1 | 66.3 | 325.8 | 157.4 | 186.8 | 111.6 | 131.3 | 142.9 | 116.6 | 131.6 | 110.9 | 144.8
1832 | 1687 | -6.8 | 0 | 0 | 128.5 | 116.1 | 107.6 | 106.5 | 142.8 | 20.4 | 21 | 32.2 | 16.6 | 235.8 | 29.9 | 133.3 | 58.2 | 28.7 | 145.8 | 95.5 | 256.5 | 127.8 | 66.4 | 325.4 | 157.2 | 186.6 | 111.5 | 131.1 | 142.8 | 116.6 | 131.5 | 110.9 | 144.7
1833 | 1688 | -6.9 | 0 | 0 | 128.5 | 115.9 | 107.5 | 106.4 | 142.7 | 20.4 | 21 | 32.2 | 14.6 | 241.7 | 33.8 | 133.1 | 57.9 | 28.7 | 145.2 | 95.4 | 256.1 | 127.4 | 66.4 | 325 | 156.9 | 186.4 | 111.3 | 131 | 142.7 | 116.5 | 131.3 | 110.7 | 144.6
1834 | 1689 | -6.9 | 0 | 0 | 128.7 | 115.7 | 107.4 | 106.3 | 142.6 | 20.3 | 21 | 32.1 | 23.3 | 247.3 | 34.8 | 132.8 | 57.7 | 28.6 | 144.9 | 95.3 | 255.8 | 127 | 66.3 | 324.6 | 156.6 | 186.3 | 111.2 | 130.9 | 142.5 | 116.3 | 131.3 | 110.5 | 144.5
1835 | 1690 | -6.7 | 0 | 0 | 128.7 | 115.5 | 107.2 | 106.2 | 142.5 | 20.2 | 21 | 32 | 23.9 | 245.1 | 30.3 | 132.3 | 57.7 | 28.7 | 144.8 | 95.1 | 255.3 | 126.6 | 66.6 | 324.5 | 156.5 | 186.1 | 111.1 | 130.8 | 142.2 | 116.2 | 131.1 | 110.2 | 144.4
1836 | 1691 | -6.8 | 0 | 0 | 128.6 | 115.5 | 107.1 | 106.1 | 142.4 | 20.1 | 21 | 32.1 | 18.1 | 239 | 36.5 | 131.8 | 57.7 | 28.6 | 144.5 | 95 | 254.9 | 126.3 | 66.7 | 324.2 | 156.4 | 186 | 110.9 | 130.7 | 142.1 | 116.1 | 131.1 | 110.1 | 144.2
1837 | 1692 | -6.8 | 0 | 0 | 128.4 | 115.4 | 107 | 106 | 142.3 | 20.1 | 21 | 32.1 | 14.3 | 243.8 | 31.7 | 131.5 | 57.4 | 28.7 | 144.5 | 94.8 | 254.4 | 126.2 | 66.6 | 324 | 156.2 | 185.8 | 110.8 | 130.6 | 142 | 115.9 | 131 | 110.1 | 144.1
1838 | 1693 | -6.6 | 0 | 0 | 128.5 | 115.2 | 106.9 | 105.8 | 142.2 | 20 | 21 | 32 | 17.8 | 233.5 | 30.7 | 131.2 | 57.3 | 28.7 | 144.5 | 94.7 | 254 | 126.2 | 66.4 | 323.6 | 156 | 185.6 | 110.6 | 130.4 | 142 | 115.8 | 130.9 | 110 | 144
1839 | 1694 | -6.5 | 0 | 0 | 128.3 | 115.1 | 106.8 | 105.7 | 142.1 | 19.9 | 21 | 31.8 | 18.4 | 253.8 | 27.3 | 131 | 57.3 | 28.6 | 144.2 | 94.5 | 253.7 | 126 | 66.3 | 323.1 | 155.9 | 185.5 | 110.4 | 130.3 | 141.9 | 115.7 | 130.8 | 109.8 | 143.9
1840 | 1695 | -6.6 | 0 | 0 | 127.9 | 114.9 | 106.7 | 105.5 | 141.9 | 19.9 | 21 | 31.7 | 17.2 | 240.8 | 22.8 | 130.7 | 57.3 | 28.6 | 143.6 | 94.4 | 253.2 | 125.8 | 66.3 | 322.9 | 155.5 | 185.3 | 110.4 | 130.2 | 141.8 | 115.6 | 130.7 | 109.6 | 143.8
1841 | 1696 | -6.7 | 0 | 0 | 127.7 | 114.8 | 106.6 | 105.5 | 141.8 | 19.9 | 21 | 31.7 | 8.5 | 233.4 | 31.6 | 130.4 | 56.8 | 28.5 | 143.7 | 94.1 | 252.9 | 125.9 | 66.3 | 322.7 | 155.4 | 185.2 | 110.3 | 130.1 | 141.7 | 115.4 | 130.5 | 109.4 | 143.6
1842 | 1697 | -6.9 | 0 | 0 | 127.7 | 114.8 | 106.5 | 105.5 | 141.7 | 20 | 21 | 31.7 | 12.8 | 234.4 | 24.4 | 130.2 | 56.7 | 28.5 | 143.9 | 93.9 | 252.5 | 126 | 66.2 | 322.4 | 155.4 | 185 | 110.2 | 130 | 141.5 | 115.3 | 130.4 | 109.4 | 143.5
1843 | 1698 | -6.8 | 0 | 0 | 127.7 | 114.6 | 106.4 | 105.4 | 141.6 | 20 | 21 | 31.6 | 14.9 | 247.6 | 23.2 | 129.8 | 56.4 | 28.5 | 144 | 93.9 | 252.2 | 125.9 | 66.2 | 322.1 | 155.1 | 184.8 | 110.1 | 129.9 | 141.3 | 115.2 | 130.3 | 109.5 | 143.4
1844 | 1699 | -6.9 | 0 | 0 | 127.6 | 114.3 | 106.3 | 105.3 | 141.4 | 20.1 | 21 | 31.6 | 13.9 | 243.4 | 29.7 | 129.5 | 56.2 | 28.5 | 143.8 | 93.7 | 251.8 | 125.8 | 66.1 | 321.2 | 154.8 | 184.7 | 110.1 | 129.8 | 141.2 | 115.1 | 130.2 | 109.3 | 143.3
1845 | 1700 | -6.7 | 0 | 0 | 127.3 | 114.1 | 106.2 | 105.1 | 141.3 | 20.2 | 21 | 31.5 | 13.3 | 235.6 | 32 | 129.2 | 56.1 | 28.5 | 143.5 | 93.6 | 251.4 | 125.4 | 66.1 | 320.4 | 154.5 | 184.5 | 109.9 | 129.7 | 141.1 | 115 | 130.1 | 109.1 | 143.1
1846 | 1701 | -6.1 | 0 | 0 | 127.2 | 114 | 106.2 | 105.1 | 141.2 | 20.3 | 21 | 31.4 | 14.2 | 246.8 | 23.5 | 128.8 | 56.1 | 28.5 | 143.3 | 93.5 | 251.1 | 125.2 | 66.1 | 320.3 | 154.2 | 184.3 | 109.8 | 129.5 | 140.9 | 114.8 | 130 | 109 | 143
1847 | 1702 | -5.7 | 0 | 0 | 127 | 114 | 106.1 | 105 | 141.1 | 20.3 | 21 | 31.3 | 19.1 | 245.2 | 22.4 | 128.4 | 55.9 | 28.4 | 143.4 | 93.4 | 250.8 | 124.8 | 66.1 | 319.9 | 154.2 | 184.2 | 109.8 | 129.4 | 140.8 | 114.7 | 129.9 | 108.8 | 142.9
1848 | 1703 | -6.2 | 0 | 0 | 126.8 | 114 | 106 | 104.9 | 141 | 20.3 | 21 | 31.2 | 18.1 | 246.5 | 31.7 | 128 | 55.8 | 28.4 | 143.7 | 93.3 | 250.5 | 124.4 | 66.1 | 319.7 | 154 | 184 | 109.8 | 129.2 | 140.6 | 114.6 | 129.7 | 108.7 | 142.7
1849 | 1704 | -6.4 | 0 | 0 | 126.5 | 113.9 | 105.9 | 104.8 | 140.9 | 20.4 | 21 | 31 | 28 | 242.6 | 32.4 | 127.7 | 55.7 | 28.4 | 143.5 | 93.2 | 250.2 | 124.1 | 66 | 319.6 | 153.7 | 183.9 | 109.7 | 129.2 | 140.5 | 114.5 | 129.6 | 108.8 | 142.6
1850 | 1705 | -6.2 | 0 | 0 | 126.4 | 113.8 | 105.7 | 104.7 | 140.8 | 20.4 | 21 | 30.9 | 18.8 | 241.2 | 34.6 | 127.7 | 55.6 | 28.4 | 143.1 | 93 | 249.9 | 124 | 66 | 319.4 | 153.5 | 183.7 | 109.6 | 129 | 140.4 | 114.4 | 129.4 | 108.9 | 142.5
1851 | 1706 | -6.2 | 0 | 0 | 126.3 | 113.7 | 105.5 | 104.6 | 140.6 | 20.5 | 21 | 30.8 | 16.8 | 239.3 | 38 | 127.7 | 55.5 | 28.4 | 142.8 | 92.9 | 249.5 | 123.7 | 65.9 | 319.1 | 153.3 | 183.6 | 109.4 | 128.9 | 140.2 | 114.3 | 129.3 | 108.8 | 142.4
1852 | 1707 | -6.1 | 0 | 0 | 126.2 | 113.5 | 105.5 | 104.5 | 140.5 | 20.5 | 21 | 30.7 | 15.3 | 242.1 | 35.6 | 127.6 | 55.6 | 28.3 | 142.9 | 92.8 | 249.1 | 123.4 | 65.7 | 318.9 | 153.1 | 183.4 | 109.3 | 128.8 | 140.1 | 114.2 | 129.2 | 108.6 | 142.2
1853 | 1708 | -6.2 | 0 | 0 | 126.2 | 113.4 | 105.4 | 104.4 | 140.4 | 20.4 | 21 | 30.6 | 13.7 | 240.9 | 33.4 | 127.7 | 55.4 | 28.4 | 142.6 | 92.6 | 248.7 | 123.4 | 65.7 | 318.7 | 152.9 | 183.2 | 109.3 | 128.7 | 140 | 114 | 129.1 | 108.4 | 142.1
1854 | 1709 | -6.5 | 0 | 0 | 126.1 | 113.3 | 105.3 | 104.4 | 140.4 | 20.3 | 21 | 30.6 | 10.2 | 246.9 | 34.7 | 127.7 | 55.3 | 28.4 | 142.5 | 92.4 | 248.3 | 123.4 | 65.5 | 318.3 | 152.8 | 183.1 | 109.1 | 128.6 | 139.9 | 113.9 | 129 | 108.3 | 142
1855 | 1710 | -6.6 | 0 | 0 | 126 | 113.2 | 105.2 | 104.3 | 140.3 | 20.2 | 21 | 30.6 | 13.2 | 247.1 | 31.3 | 127.8 | 55.3 | 28.3 | 142.5 | 92.2 | 247.9 | 123.5 | 65.4 | 317.6 | 152.4 | 182.9 | 109 | 128.6 | 139.7 | 113.8 | 128.9 | 108.3 | 141.8
1856 | 1711 | -6.2 | 0 | 0 | 125.7 | 113.1 | 105.1 | 104.2 | 140.3 | 20.1 | 21 | 30.5 | 14.7 | 248.5 | 28.1 | 127.8 | 55.3 | 28.3 | 142.3 | 92.1 | 247.4 | 123.4 | 65.2 | 317.4 | 152.2 | 182.8 | 108.9 | 128.4 | 139.6 | 113.7 | 128.8 | 108.4 | 141.8
1857 | 1712 | -6.3 | 0 | 0 | 125.8 | 112.9 | 105.1 | 104 | 140.1 | 20.1 | 21 | 30.4 | 16.1 | 245 | 27.5 | 127.5 | 55.5 | 28.3 | 142.1 | 92 | 247.1 | 123.2 | 65.1 | 317.3 | 151.9 | 182.6 | 108.7 | 128.3 | 139.5 | 113.6 | 128.7 | 108.3 | 141.6
1858 | 1713 | -6.7 | 0 | 0 | 125.7 | 112.9 | 105 | 103.9 | 140 | 20 | 21 | 30.4 | 15.3 | 246.3 | 29.2 | 127.3 | 55.5 | 28.2 | 142 | 91.8 | 246.8 | 123.1 | 65 | 317.2 | 151.9 | 182.4 | 108.6 | 128.1 | 139.3 | 113.5 | 128.6 | 108.2 | 141.5
1859 | 1714 | -5.9 | 0 | 0 | 125.7 | 112.9 | 104.8 | 103.9 | 139.8 | 19.9 | 21 | 30.4 | 14.5 | 245.7 | 27.8 | 127.1 | 55.4 | 28.2 | 141.7 | 91.8 | 246.4 | 122.9 | 65 | 317 | 151.6 | 182.3 | 108.5 | 128 | 139.2 | 113.3 | 128.5 | 108 | 141.4
1860 | 1715 | -6 | 0 | 0 | 125.3 | 112.9 | 104.5 | 103.8 | 139.7 | 19.8 | 21 | 30.5 | 14.5 | 240.8 | 26.9 | 126.8 | 55.5 | 28.3 | 141.5 | 91.6 | 246.1 | 122.9 | 64.9 | 316.7 | 151.5 | 182.1 | 108.4 | 127.9 | 139 | 113.2 | 128.4 | 107.8 | 141.3
1861 | 1716 | -6.7 | 0 | 0 | 125.3 | 112.9 | 104.4 | 103.7 | 139.6 | 19.8 | 21 | 30.4 | 11 | 236.2 | 32.1 | 126.5 | 55.7 | 28.2 | 141.2 | 91.5 | 245.7 | 122.9 | 64.6 | 316.5 | 151.1 | 182 | 108.2 | 127.8 | 138.9 | 113.1 | 128.3 | 107.8 | 141.2
1862 | 1717 | -6.1 | 0 | 0 | 125 | 112.9 | 104.3 | 103.6 | 139.5 | 19.8 | 21 | 30.5 | 11.4 | 246.4 | 26.1 | 126.2 | 55.6 | 28.2 | 140.9 | 91.4 | 245.3 | 122.7 | 64.5 | 316.1 | 150.9 | 181.8 | 108.1 | 127.7 | 138.8 | 113 | 128.1 | 107.7 | 141.1
1863 | 1718 | -5 | 0 | 0 | 125 | 112.8 | 104.3 | 103.3 | 139.3 | 20 | 21 | 30.5 | 17.3 | 239.9 | 25.1 | 125.8 | 55.4 | 28.2 | 140.9 | 91.3 | 245 | 122.6 | 64.4 | 315.8 | 150.7 | 181.7 | 108 | 127.6 | 138.8 | 112.9 | 128 | 107.6 | 140.9
1864 | 1719 | -4.8 | 0 | 0 | 125.1 | 112.7 | 104.2 | 103.1 | 139 | 20 | 21 | 30.4 | 13 | 240.7 | 21.8 | 125.5 | 55.3 | 28.1 | 140.8 | 91.1 | 244.6 | 122.6 | 64.2 | 315.3 | 150.5 | 181.5 | 107.8 | 127.5 | 138.7 | 112.8 | 127.9 | 107.3 | 140.8
1865 | 1720 | -5.6 | 0 | 0 | 125 | 112.5 | 104.2 | 103 | 138.6 | 20.1 | 21 | 30.4 | 8.5 | 240.2 | 20.8 | 125.2 | 55.2 | 28.1 | 140.7 | 90.9 | 244.1 | 122.3 | 64.4 | 314.9 | 150.3 | 181.4 | 107.7 | 127.4 | 138.5 | 112.7 | 127.8 | 107.1 | 140.7
1866 | 1721 | -6 | 0 | 0 | 124.8 | 112.3 | 104.1 | 103 | 138.5 | 20.1 | 21 | 30.3 | 10.6 | 232.8 | 17.8 | 125 | 55.3 | 28 | 140.4 | 90.8 | 243.7 | 122.2 | 64.7 | 314.7 | 150.1 | 181.2 | 107.7 | 127.3 | 138.4 | 112.6 | 127.6 | 106.9 | 140.5
1867 | 1722 | -6.1 | 0 | 0 | 124.9 | 112.1 | 104.1 | 103 | 138.4 | 20.2 | 21 | 30.2 | 12.1 | 222.2 | 16.7 | 124.7 | 55.1 | 28 | 139.4 | 90.7 | 243.2 | 121.8 | 64.8 | 314.5 | 149.9 | 181 | 107.6 | 127.3 | 138.4 | 112.5 | 127.5 | 106.8 | 140.4
1868 | 1723 | -6.2 | 0 | 0 | 124.7 | 111.9 | 104 | 102.9 | 138.4 | 20.2 | 21.1 | 30.2 | 12.8 | 246.4 | 15.6 | 124.4 | 55 | 28 | 139.5 | 90.6 | 242.9 | 121.3 | 64.5 | 314.3 | 149.9 | 180.9 | 107.5 | 127.2 | 138.3 | 112.4 | 127.3 | 106.7 | 140.3
1869 | 1724 | -6.2 | 0 | 0 | 124.6 | 111.7 | 103.9 | 102.7 | 138.4 | 20.1 | 21.1 | 30.2 | 9 | 253.3 | 13.9 | 124.2 | 55.1 | 28 | 139.6 | 90.5 | 242.5 | 120.9 | 64.5 | 314.2 | 149.8 | 180.7 | 107.4 | 127.1 | 138.1 | 112.3 | 127.2 | 106.7 | 140.2
1870 | 1725 | -6.1 | 0 | 0 | 124.4 | 111.6 | 103.9 | 102.6 | 138.3 | 20 | 21.1 | 30.2 | 8.2 | 228.4 | 16.5 | 124 | 55.1 | 27.9 | 139.6 | 90.3 | 242 | 120.8 | 64.4 | 314.1 | 149.6 | 180.6 | 107.3 | 127 | 138 | 112.1 | 127.1 | 106.6 | 140.1
1871 | 1726 | -6.5 | 0 | 0 | 124.1 | 111.4 | 103.7 | 102.5 | 138.2 | 19.9 | 21.1 | 30.2 | 9.4 | 204.2 | 16 | 123.9 | 54.9 | 27.8 | 139.6 | 90.2 | 241.5 | 120.8 | 64.2 | 313.7 | 149.5 | 180.4 | 107.2 | 126.9 | 137.9 | 112 | 127 | 106.5 | 139.9
1872 | 1727 | -6.8 | 0 | 0 | 124.1 | 111.3 | 103.6 | 102.5 | 138.1 | 19.8 | 21 | 30.2 | 8.6 | 221.5 | 14.8 | 123.6 | 54.9 | 27.6 | 139.3 | 90.1 | 241.2 | 120.7 | 64 | 313.5 | 149.3 | 180.3 | 107.1 | 126.8 | 137.8 | 111.9 | 126.9 | 106.4 | 139.8
1873 | 1728 | -6.9 | 0 | 0 | 124.2 | 111.4 | 103.5 | 102.4 | 138 | 19.8 | 21 | 30.1 | 7.7 | 241.5 | 15.2 | 123.3 | 54.8 | 27.5 | 139.5 | 89.9 | 240.8 | 120.6 | 63.8 | 313.3 | 149.1 | 180.1 | 106.9 | 126.6 | 137.6 | 111.8 | 126.7 | 106.3 | 139.7
1874 | 1729 | -6.8 | 0 | 0 | 124.4 | 111.5 | 103.3 | 102.3 | 137.9 | 19.8 | 21.1 | 30.2 | 8.7 | 231.5 | 15.1 | 123.2 | 54.7 | 27.4 | 139.4 | 89.7 | 240.3 | 120.3 | 64 | 313.2 | 148.9 | 180 | 106.8 | 126.5 | 137.4 | 111.7 | 126.5 | 106.2 | 139.6
1875 | 1730 | -6.1 | 0 | 0 | 124.4 | 111.4 | 103.2 | 102.1 | 137.8 | 19.9 | 21.1 | 30.2 | 9.9 | 227.8 | 15.5 | 123 | 54.7 | 27.4 | 139.1 | 89.5 | 239.9 | 120 | 64.1 | 313 | 148.9 | 179.8 | 106.6 | 126.4 | 137.2 | 111.6 | 126.4 | 106.1 | 139.4
1876 | 1731 | -5.3 | 0 | 0 | 124.3 | 111.2 | 103.1 | 102 | 137.7 | 19.9 | 21 | 30.2 | 10.1 | 243.5 | 19.8 | 122.9 | 54.7 | 27.4 | 138.8 | 89.4 | 239.5 | 119.7 | 63.8 | 312.7 | 148.8 | 179.6 | 106.5 | 126.3 | 137.2 | 111.5 | 126.3 | 106.1 | 139.3
1877 | 1732 | -5.9 | 0 | 0 | 124.2 | 111 | 103 | 102 | 137.7 | 20 | 21.1 | 30.2 | 7.5 | 234.7 | 23.2 | 122.7 | 54.7 | 27.3 | 138.7 | 89.3 | 239.2 | 119.5 | 63.5 | 312.3 | 148.5 | 179.5 | 106.4 | 126.2 | 137.2 | 111.4 | 126.3 | 105.9 | 139.2
1878 | 1733 | -6.3 | 0 | 0 | 124.3 | 110.9 | 103 | 102.1 | 137.6 | 20 | 21.1 | 30.2 | 8.3 | 231.2 | 22.2 | 122.4 | 54.3 | 27.2 | 138.7 | 89.2 | 238.9 | 119.7 | 63.4 | 311.7 | 148.2 | 179.3 | 106.3 | 126 | 137.1 | 111.3 | 126.2 | 105.8 | 139.1
1879 | 1734 | -6.8 | 0 | 0 | 124.2 | 110.9 | 102.9 | 102 | 137.5 | 20 | 21.1 | 30.2 | 8.5 | 243.1 | 23.5 | 121.8 | 54.4 | 27.2 | 138.8 | 89 | 238.6 | 119.8 | 63.2 | 311.5 | 147.9 | 179.2 | 106.1 | 125.9 | 136.9 | 111.2 | 126.1 | 105.7 | 139
1880 | 1735 | -6.8 | 0 | 0 | 124 | 110.8 | 102.9 | 101.7 | 137.4 | 20.1 | 21.1 | 30.3 | 9.5 | 247.9 | 24.6 | 121.5 | 54.1 | 27.1 | 138.8 | 88.9 | 238.3 | 120.1 | 63 | 311 | 147.9 | 179 | 106 | 125.8 | 136.7 | 111.1 | 126.1 | 105.6 | 138.9
1881 | 1736 | -6.8 | 0 | 0 | 123.7 | 110.5 | 102.8 | 101.6 | 137.3 | 20.1 | 21.1 | 30.3 | 12.5 | 243 | 21.5 | 121.3 | 53.9 | 27.1 | 138.7 | 88.8 | 238 | 120 | 62.9 | 310.5 | 147.8 | 178.9 | 105.8 | 125.7 | 136.5 | 111 | 125.9 | 105.4 | 138.7
1882 | 1737 | -6.6 | 0 | 0 | 123.7 | 110.3 | 102.5 | 101.5 | 137.2 | 20.1 | 21.1 | 30.3 | 10.9 | 243 | 19.5 | 121.1 | 53.6 | 27 | 138.7 | 88.7 | 237.7 | 119.8 | 63 | 310.4 | 147.6 | 178.7 | 105.7 | 125.5 | 136.4 | 110.9 | 125.8 | 105.2 | 138.6
1883 | 1738 | -6.4 | 0 | 0 | 123.7 | 110.3 | 102.3 | 101.4 | 137.1 | 20 | 21.1 | 30.2 | 8.7 | 240.9 | 22.5 | 120.8 | 53.3 | 27 | 138.3 | 88.6 | 237.5 | 119.5 | 62.8 | 310.1 | 147.5 | 178.6 | 105.6 | 125.4 | 136.3 | 110.7 | 125.7 | 105.1 | 138.5
1884 | 1739 | -6.5 | 0 | 0 | 123.6 | 110.3 | 102.2 | 101.4 | 136.9 | 19.9 | 21.1 | 30.2 | 6.7 | 247.8 | 25.2 | 120.3 | 53.4 | 26.9 | 138.4 | 88.5 | 237.1 | 119.7 | 62.8 | 309.8 | 147.5 | 178.4 | 105.5 | 125.3 | 136.1 | 110.6 | 125.6 | 105 | 138.3
1885 | 1740 | -6.5 | 0 | 0 | 123.5 | 110.3 | 102.1 | 101.3 | 136.9 | 19.8 | 21.1 | 30.2 | 6.9 | 237.6 | 23.9 | 120 | 53.4 | 26.9 | 138.3 | 88.4 | 236.8 | 119.7 | 62.8 | 309.3 | 147.3 | 178.3 | 105.4 | 125.3 | 136 | 110.5 | 125.4 | 105.1 | 138.2
1886 | 1741 | -5.4 | 0 | 0 | 123.2 | 110.1 | 102 | 101.2 | 136.8 | 19.7 | 21.1 | 30.2 | 6.8 | 244.9 | 21.8 | 119.8 | 53.4 | 26.9 | 138.2 | 88.3 | 236.5 | 119.6 | 62.9 | 308.6 | 147 | 178.1 | 105.3 | 125.2 | 136 | 110.5 | 125.3 | 105.1 | 138.1
1887 | 1742 | -6.2 | 0 | 0 | 122.9 | 109.9 | 102 | 101.1 | 136.7 | 19.6 | 21.1 | 30.3 | 9.6 | 244.3 | 21.5 | 119.6 | 53.3 | 26.8 | 138 | 88.1 | 236.3 | 119.2 | 62.8 | 308.1 | 146.8 | 177.9 | 105.2 | 125.1 | 135.9 | 110.4 | 125.3 | 105 | 138
1888 | 1743 | -5.1 | 0 | 0 | 122.7 | 109.7 | 101.9 | 101 | 136.6 | 19.6 | 21.1 | 30.3 | 10.1 | 249.6 | 21.2 | 119.3 | 53.2 | 26.8 | 137.9 | 88 | 235.9 | 118.7 | 62.7 | 308.1 | 146.7 | 177.8 | 105.1 | 125 | 135.8 | 110.2 | 125.2 | 104.8 | 137.8
1889 | 1744 | -5.5 | 0 | 0 | 122.7 | 109.5 | 101.8 | 100.8 | 136.4 | 19.5 | 21.1 | 30.3 | 10.2 | 264.1 | 18.6 | 119 | 52.9 | 26.8 | 137.9 | 87.8 | 235.6 | 118.4 | 62.8 | 307.9 | 146.4 | 177.6 | 105.1 | 124.9 | 135.6 | 110.1 | 125.1 | 104.7 | 137.7
1890 | 1745 | -6.6 | 0 | 0 | 122.5 | 109.4 | 101.7 | 100.7 | 136.2 | 19.4 | 21.1 | 30.4 | 8.6 | 235.1 | 16.6 | 118.7 | 52.7 | 26.8 | 137.6 | 87.7 | 235.3 | 118.4 | 62.8 | 307.5 | 146.2 | 177.5 | 105.1 | 124.8 | 135.5 | 110 | 125 | 104.4 | 137.6
1891 | 1746 | -6.9 | 0 | 0 | 122.4 | 109.2 | 101.6 | 100.7 | 136.1 | 19.4 | 21.1 | 30.5 | 8.5 | 250.3 | 16.2 | 118.7 | 52.8 | 26.7 | 137.4 | 87.6 | 234.9 | 118.3 | 62.7 | 307.2 | 146.1 | 177.3 | 105.1 | 124.7 | 135.4 | 109.9 | 124.9 | 104.3 | 137.5
1892 | 1747 | -6.5 | 0 | 0 | 122.1 | 109.1 | 101.5 | 100.6 | 136 | 19.4 | 21.1 | 30.5 | 12.1 | 252.1 | 17.3 | 118.7 | 52.8 | 26.7 | 137.1 | 87.4 | 234.5 | 118 | 62.5 | 306.4 | 146 | 177.2 | 105 | 124.6 | 135.3 | 109.8 | 124.8 | 104.2 | 137.4
1893 | 1748 | -5.7 | 0 | 0 | 122.2 | 109 | 101.5 | 100.4 | 135.9 | 19.5 | 21.1 | 30.5 | 13.4 | 259.8 | 20.7 | 118.4 | 52.9 | 26.6 | 137.2 | 87.3 | 234.2 | 117.8 | 62.4 | 305.8 | 145.8 | 177 | 104.9 | 124.4 | 135.2 | 109.7 | 124.7 | 104.1 | 137.2
1894 | 1749 | -6.1 | 0 | 0 | 122.3 | 108.8 | 101.4 | 100.3 | 135.7 | 19.5 | 21.1 | 30.4 | 14.1 | 253.4 | 19.6 | 118.2 | 52.7 | 26.6 | 137.1 | 87.2 | 233.8 | 117.7 | 62.5 | 305.3 | 145.6 | 176.9 | 104.8 | 124.3 | 135.1 | 109.5 | 124.6 | 104 | 137.1
1895 | 1750 | -5.6 | 0 | 0 | 122.2 | 108.6 | 101.4 | 100.2 | 135.6 | 19.6 | 21.1 | 30.4 | 13.5 | 249.2 | 21.6 | 118.2 | 52.8 | 26.6 | 137 | 87 | 233.5 | 117.4 | 62.4 | 304.9 | 145.3 | 176.7 | 104.7 | 124.1 | 135.1 | 109.4 | 124.5 | 103.8 | 137
1896 | 1751 | -5.3 | 0 | 0 | 122.2 | 108.4 | 101.3 | 100.1 | 135.5 | 19.6 | 21.1 | 30.4 | 11.5 | 235 | 26.1 | 118.4 | 52.7 | 26.5 | 136.9 | 86.9 | 233.2 | 117.6 | 62.4 | 304.7 | 145.2 | 176.6 | 104.7 | 124.1 | 135 | 109.3 | 124.4 | 103.7 | 136.9
1897 | 1752 | -5.3 | 0 | 0 | 122.3 | 108.2 | 101.2 | 100.1 | 135.4 | 19.6 | 21.1 | 30.5 | 13 | 246.5 | 21.7 | 118.6 | 52.8 | 26.5 | 136.7 | 86.7 | 232.9 | 117.8 | 62.4 | 304.4 | 144.9 | 176.4 | 104.6 | 124 | 134.8 | 109.2 | 124.3 | 103.6 | 136.8
1898 | 1753 | -5.7 | 0 | 0 | 122.3 | 108.1 | 101.1 | 100 | 135.3 | 19.6 | 21.1 | 30.5 | 10.3 | 240.3 | 18.8 | 118.8 | 52.7 | 26.5 | 136.5 | 86.5 | 232.7 | 117.7 | 62.1 | 304 | 144.7 | 176.3 | 104.4 | 123.8 | 134.6 | 109.1 | 124.3 | 103.4 | 136.7
1899 | 1754 | -5.9 | 0 | 0 | 122.1 | 108 | 100.9 | 99.9 | 135.2 | 19.6 | 21.1 | 30.6 | 9.2 | 241.4 | 20.9 | 119 | 52.5 | 26.5 | 136.3 | 86.4 | 232.4 | 117.6 | 61.9 | 303.5 | 144.5 | 176.1 | 104.3 | 123.7 | 134.5 | 109 | 124.2 | 103.3 | 136.5
1900 | 1755 | -6.3 | 0 | 0 | 121.8 | 107.8 | 100.8 | 99.9 | 135.1 | 19.7 | 21.1 | 30.6 | 9 | 239.1 | 22.9 | 118.9 | 52.6 | 26.5 | 136.2 | 86.4 | 232.2 | 117.7 | 61.9 | 302.4 | 144.4 | 176 | 104.3 | 123.6 | 134.5 | 108.9 | 124.1 | 103.1 | 136.4
1901 | 1756 | -6.3 | 0 | 0 | 121.6 | 107.8 | 100.7 | 99.8 | 134.9 | 19.8 | 21.1 | 30.7 | 7.9 | 246 | 25.5 | 118.6 | 52.7 | 26.5 | 136.1 | 86.3 | 231.9 | 117.7 | 61.7 | 302.1 | 144.2 | 175.8 | 104.2 | 123.6 | 134.3 | 108.7 | 124 | 102.9 | 136.3
1902 | 1757 | -6.3 | 0 | 0 | 121.4 | 107.8 | 100.7 | 99.7 | 134.8 | 19.8 | 21.1 | 30.7 | 6.8 | 242.2 | 24.7 | 118.3 | 52.6 | 26.5 | 136.1 | 86.2 | 231.5 | 117.6 | 61.7 | 301.3 | 144.1 | 175.7 | 104 | 123.5 | 134.1 | 108.6 | 123.9 | 102.9 | 136.2
1903 | 1758 | -6.4 | 0 | 0 | 121.4 | 107.7 | 100.6 | 99.6 | 134.7 | 19.9 | 21.1 | 30.8 | 6.2 | 242.7 | 21.3 | 118 | 52.4 | 26.5 | 136 | 86.1 | 231.2 | 117.4 | 61.5 | 300.6 | 143.7 | 175.5 | 103.9 | 123.3 | 134 | 108.5 | 123.8 | 103 | 136
1904 | 1759 | -6.3 | 0 | 0 | 121.3 | 107.5 | 100.5 | 99.4 | 134.6 | 20 | 21.1 | 30.8 | 6 | 241.8 | 18.8 | 117.9 | 52.4 | 26.5 | 135.8 | 85.9 | 230.8 | 117.1 | 61.2 | 300.5 | 143.5 | 175.4 | 103.9 | 123.2 | 133.8 | 108.5 | 123.7 | 102.9 | 135.9
1905 | 1760 | -6.3 | 0 | 0 | 121.1 | 107.4 | 100.3 | 99.4 | 134.6 | 20.1 | 21.1 | 30.9 | 8.9 | 241.7 | 20.9 | 117.8 | 52.2 | 26.6 | 135.4 | 85.9 | 230.5 | 116.7 | 61.1 | 300.2 | 143.4 | 175.2 | 103.8 | 123.1 | 133.7 | 108.4 | 123.6 | 102.8 | 135.8
1906 | 1761 | -6.1 | 0 | 0 | 121 | 107.3 | 100.1 | 99.3 | 134.5 | 20.1 | 21.1 | 30.9 | 8.6 | 262.2 | 20.3 | 117.8 | 52.2 | 26.7 | 135 | 85.6 | 230.3 | 116.6 | 61 | 299.9 | 143.2 | 175.1 | 103.7 | 122.9 | 133.6 | 108.2 | 123.5 | 102.7 | 135.7
1907 | 1762 | -6 | 0 | 0 | 120.6 | 107.3 | 100 | 99.2 | 134.4 | 20.2 | 21.1 | 30.9 | 8.3 | 263.2 | 16.7 | 117.7 | 52.3 | 26.8 | 134.6 | 85.5 | 230 | 116.7 | 60.9 | 299.8 | 143 | 174.9 | 103.7 | 122.8 | 133.5 | 108.1 | 123.4 | 102.5 | 135.6
1908 | 1763 | -6.2 | 0 | 0 | 120.4 | 107.2 | 100 | 99.1 | 134.3 | 20.2 | 21.1 | 30.9 | 8.8 | 273.4 | 13.9 | 117.6 | 52.5 | 26.9 | 134.2 | 85.4 | 229.7 | 116.8 | 60.8 | 299.6 | 142.8 | 174.8 | 103.6 | 122.7 | 133.4 | 108 | 123.3 | 102.4 | 135.5
1909 | 1764 | -6.2 | 0 | 0 | 120.6 | 107.1 | 99.9 | 99.1 | 134.1 | 20 | 21.1 | 30.9 | 6.9 | 258.1 | 15.1 | 117.5 | 52.3 | 26.9 | 133.9 | 85.3 | 229.4 | 117 | 60.8 | 299.4 | 142.8 | 174.6 | 103.5 | 122.6 | 133.3 | 107.9 | 123.2 | 102.4 | 135.4
1910 | 1765 | -6.1 | 0 | 0 | 120.9 | 107 | 99.9 | 98.9 | 134 | 19.9 | 21.1 | 30.9 | 5.9 | 270.2 | 15.2 | 117.4 | 52.1 | 26.9 | 133.7 | 85.1 | 229.2 | 116.9 | 60.8 | 299.2 | 142.7 | 174.5 | 103.4 | 122.6 | 133.2 | 107.8 | 123.1 | 102.4 | 135.3
1911 | 1766 | -5.9 | 0 | 0 | 120.7 | 107 | 99.8 | 98.8 | 133.9 | 19.8 | 21.1 | 30.9 | 4.6 | 241.3 | 15.8 | 117.4 | 51.9 | 26.9 | 133.5 | 85 | 228.9 | 116.8 | 60.5 | 298.8 | 142.4 | 174.3 | 103.3 | 122.5 | 133.1 | 107.7 | 123 | 102.2 | 135.1
1912 | 1767 | -5.3 | 0 | 0 | 120.5 | 106.9 | 99.8 | 98.7 | 133.7 | 19.7 | 21.1 | 30.9 | 5.9 | 232.5 | 17.9 | 117.4 | 51.9 | 26.9 | 133.4 | 84.9 | 228.6 | 116.7 | 60.4 | 298.6 | 142.1 | 174.2 | 103.2 | 122.4 | 132.9 | 107.6 | 122.9 | 102.1 | 135
1913 | 1768 | -5.2 | 0 | 0 | 120.4 | 106.9 | 99.8 | 98.6 | 133.6 | 19.6 | 21.1 | 30.9 | 7.4 | 236.4 | 14.7 | 117.4 | 51.9 | 26.9 | 133.2 | 84.8 | 228.4 | 116.7 | 60.3 | 298.2 | 142 | 174 | 103.1 | 122.3 | 132.8 | 107.5 | 122.8 | 101.9 | 134.9
1914 | 1769 | -5.6 | 0 | 0 | 120.3 | 106.9 | 99.7 | 98.5 | 133.5 | 19.6 | 21.1 | 31 | 6 | 249 | 14.7 | 117.3 | 51.9 | 26.9 | 133.1 | 84.7 | 228.1 | 116.8 | 60.2 | 297.8 | 141.7 | 173.9 | 103 | 122.3 | 132.6 | 107.4 | 122.7 | 101.8 | 134.8
1915 | 1770 | -5.8 | 0 | 0 | 120.2 | 106.9 | 99.5 | 98.4 | 133.4 | 19.6 | 21.1 | 31 | 4.5 | 267.3 | 15.1 | 117.3 | 51.7 | 26.9 | 132.9 | 84.6 | 227.8 | 116.5 | 60 | 297.5 | 141.6 | 173.7 | 102.9 | 122.2 | 132.5 | 107.3 | 122.6 | 101.8 | 134.7
1916 | 1771 | -6.2 | 0 | 0 | 120 | 106.8 | 99.3 | 98.3 | 133.3 | 19.7 | 21.1 | 31.1 | 4 | 265.6 | 16.7 | 117.1 | 51.6 | 27 | 132.7 | 84.5 | 227.6 | 116.1 | 59.8 | 297.3 | 141.4 | 173.6 | 102.8 | 122 | 132.4 | 107.2 | 122.6 | 101.7 | 134.5
1917 | 1772 | -5.9 | 0 | 0 | 119.7 | 106.8 | 99.1 | 98.2 | 133.2 | 19.7 | 21.1 | 31.2 | 5.9 | 255 | 18.5 | 117 | 51.7 | 27.1 | 132.5 | 84.4 | 227.3 | 115.8 | 59.8 | 296.9 | 141.1 | 173.4 | 102.7 | 121.9 | 132.3 | 107.1 | 122.5 | 101.6 | 134.5
1918 | 1773 | -5 | 0 | 0 | 119.3 | 106.6 | 99.1 | 97.9 | 133 | 19.7 | 21.1 | 31.2 | 7 | 261.7 | 18.2 | 116.9 | 51.9 | 27.1 | 132.4 | 84.3 | 227.1 | 115.8 | 59.8 | 296.3 | 140.9 | 173.3 | 102.6 | 121.7 | 132.1 | 107 | 122.4 | 101.5 | 134.4
1919 | 1774 | -5.4 | 0 | 0 | 119.2 | 106.5 | 99.1 | 97.8 | 132.9 | 19.8 | 21.1 | 31.3 | 6.5 | 243 | 18.8 | 116.9 | 51.9 | 27.1 | 132.3 | 84.2 | 226.8 | 115.8 | 59.7 | 295.7 | 140.9 | 173.1 | 102.5 | 121.6 | 132 | 106.8 | 122.3 | 101.3 | 134.2
1920 | 1775 | -5.8 | 0 | 0 | 119.1 | 106.5 | 99 | 97.8 | 132.8 | 19.8 | 21.1 | 31.2 | 6.3 | 257.4 | 20.5 | 116.8 | 51.9 | 27.1 | 132.1 | 84.1 | 226.5 | 115.9 | 59.7 | 295.6 | 140.8 | 173 | 102.5 | 121.5 | 132 | 106.7 | 122.1 | 101.2 | 134.1
1921 | 1776 | -6.1 | 0 | 0 | 119.2 | 106.4 | 98.8 | 97.7 | 132.7 | 19.9 | 21.1 | 31.2 | 6.8 | 257.3 | 22 | 116.7 | 51.9 | 27.1 | 131.9 | 83.9 | 226.2 | 115.8 | 59.5 | 295.3 | 140.7 | 172.8 | 102.4 | 121.4 | 131.9 | 106.6 | 122 | 101.2 | 134
1922 | 1777 | -6.1 | 0 | 0 | 119 | 106.4 | 98.7 | 97.6 | 132.7 | 20 | 21.1 | 31.2 | 4.9 | 249.1 | 20.2 | 116.6 | 51.7 | 27.1 | 131.8 | 83.7 | 226 | 115.7 | 59.3 | 295 | 140.4 | 172.7 | 102.3 | 121.3 | 131.8 | 106.6 | 121.9 | 101.1 | 133.9
1923 | 1778 | -6.2 | 0 | 0 | 118.7 | 106.4 | 98.7 | 97.5 | 132.5 | 20 | 21.1 | 31.1 | 4.6 | 255.4 | 18.9 | 116.5 | 51.7 | 27.2 | 131.6 | 83.6 | 225.7 | 115.3 | 59.2 | 294.9 | 140.2 | 172.5 | 102.2 | 121.2 | 131.7 | 106.5 | 121.8 | 101 | 133.8
1924 | 1779 | -6.4 | 0 | 0 | 118.5 | 106.3 | 98.6 | 97.4 | 132.3 | 20 | 21.1 | 31.1 | 8.1 | 241 | 14.9 | 116.5 | 51.5 | 27.2 | 131.4 | 83.5 | 225.4 | 115 | 59 | 294.7 | 140 | 172.4 | 102.1 | 121 | 131.6 | 106.4 | 121.7 | 100.9 | 133.7
1925 | 1780 | -6.4 | 0 | 0 | 118.3 | 106.1 | 98.6 | 97.4 | 132.2 | 20 | 21.1 | 31 | 10.3 | 244.8 | 13.4 | 116.3 | 51.3 | 27.1 | 131.2 | 83.4 | 225.1 | 115 | 58.9 | 294.5 | 139.8 | 172.2 | 102 | 120.9 | 131.5 | 106.2 | 121.6 | 100.7 | 133.6
1926 | 1781 | -6.3 | 0 | 0 | 118.2 | 105.9 | 98.6 | 97.3 | 132 | 20.1 | 21.1 | 31 | 9.5 | 253.2 | 12.8 | 116 | 51.4 | 27.1 | 131.2 | 83.2 | 224.8 | 114.9 | 58.8 | 294.1 | 139.8 | 172.1 | 101.9 | 120.8 | 131.4 | 106.1 | 121.5 | 100.6 | 133.4
1927 | 1782 | -6.1 | 0 | 0 | 118.1 | 105.6 | 98.5 | 97.2 | 131.9 | 20.1 | 21.1 | 31 | 7.9 | 266.6 | 15.2 | 115.7 | 51.2 | 27.1 | 131.2 | 83.1 | 224.5 | 115 | 58.7 | 293.7 | 139.9 | 171.9 | 101.7 | 120.8 | 131.4 | 106 | 121.4 | 100.5 | 133.3
1928 | 1783 | -5.9 | 0 | 0 | 118.1 | 105.4 | 98.4 | 97 | 131.8 | 20.1 | 21.1 | 31.1 | 3.8 | 248.7 | 19 | 115.4 | 51.1 | 27.1 | 131.2 | 83.1 | 224.2 | 114.8 | 58.8 | 293.4 | 139.8 | 171.8 | 101.6 | 120.7 | 131.2 | 106 | 121.3 | 100.5 | 133.2
1929 | 1784 | -5.9 | 0 | 0 | 118 | 105.3 | 98.3 | 96.8 | 131.8 | 20 | 21.1 | 31.1 | 3.5 | 237.2 | 20.4 | 115.2 | 50.9 | 27 | 131.1 | 83 | 223.9 | 114.4 | 59 | 293.1 | 139.6 | 171.7 | 101.6 | 120.6 | 131.2 | 105.9 | 121.2 | 100.3 | 133.1
1930 | 1785 | -6.2 | 0 | 0 | 117.8 | 105.1 | 98.3 | 96.8 | 131.7 | 19.9 | 21.1 | 31.2 | 4.2 | 245 | 17.3 | 115.2 | 50.9 | 27 | 131 | 82.9 | 223.7 | 114.1 | 59.1 | 292.7 | 139.3 | 171.5 | 101.4 | 120.5 | 131 | 105.8 | 121 | 100.2 | 133
1931 | 1786 | -6.4 | 0 | 0 | 117.5 | 105 | 98.2 | 96.7 | 131.5 | 19.8 | 21.1 | 31.3 | 4.7 | 246.6 | 14.5 | 115.2 | 50.8 | 27 | 130.2 | 82.8 | 223.4 | 114.1 | 59.1 | 292 | 139.1 | 171.3 | 101.4 | 120.4 | 130.8 | 105.6 | 120.9 | 100.1 | 132.9
1932 | 1787 | -6.5 | 0 | 0 | 117.5 | 105 | 98 | 96.7 | 131.4 | 19.8 | 21.1 | 31.3 | 5.7 | 248.2 | 13.4 | 115.3 | 50.8 | 26.9 | 129.7 | 82.7 | 223.1 | 114.2 | 59 | 291.5 | 138.9 | 171.2 | 101.2 | 120.3 | 130.7 | 105.5 | 120.8 | 100.1 | 132.8
1933 | 1788 | -6.5 | 0 | 0 | 117.5 | 104.9 | 97.9 | 96.7 | 131.3 | 19.8 | 21.1 | 31.4 | 5.3 | 245 | 14.9 | 115.3 | 50.8 | 27 | 129.8 | 82.6 | 222.8 | 114.2 | 59 | 291.2 | 138.8 | 171.1 | 101.1 | 120.1 | 130.5 | 105.4 | 120.7 | 100 | 132.6
1934 | 1789 | -6.5 | 0 | 0 | 117.3 | 104.9 | 97.9 | 96.6 | 131.3 | 19.8 | 21.1 | 31.4 | 6.6 | 242.8 | 17.2 | 115.3 | 50.4 | 26.9 | 129.8 | 82.6 | 222.5 | 114.2 | 59 | 290.8 | 138.6 | 170.9 | 101 | 120 | 130.4 | 105.4 | 120.6 | 100.1 | 132.5
1935 | 1790 | -6.4 | 0 | 0 | 117.2 | 104.8 | 97.9 | 96.4 | 131.2 | 19.8 | 21.1 | 31.3 | 7.6 | 247.9 | 20.1 | 115.3 | 50.4 | 26.9 | 129.8 | 82.5 | 222.3 | 114 | 59.1 | 290.5 | 138.4 | 170.8 | 100.8 | 119.9 | 130.3 | 105.3 | 120.5 | 100.1 | 132.4
1936 | 1791 | -6.7 | 0 | 0 | 117.2 | 104.7 | 97.8 | 96.3 | 131.1 | 19.9 | 21.1 | 31 | 9.6 | 239.1 | 18.9 | 115.1 | 50.5 | 26.9 | 129.7 | 82.4 | 222 | 113.8 | 59.3 | 290.3 | 138.2 | 170.6 | 100.7 | 119.7 | 130.2 | 105.2 | 120.4 | 99.9 | 132.3
1937 | 1792 | -6.8 | 0 | 0 | 117 | 104.7 | 97.7 | 96.3 | 130.9 | 20 | 21.1 | 30.8 | 12.3 | 247.4 | 16.2 | 114.8 | 50.6 | 26.9 | 129.7 | 82.3 | 221.7 | 113.7 | 59.5 | 290.1 | 138 | 170.5 | 100.6 | 119.6 | 130.1 | 105 | 120.3 | 99.7 | 132.2
1938 | 1793 | -6.6 | 0 | 0 | 116.8 | 104.7 | 97.6 | 96.2 | 130.8 | 20 | 21.1 | 30.7 | 14.8 | 240.1 | 19.7 | 114.6 | 50.8 | 26.9 | 129.7 | 82.2 | 221.4 | 113.8 | 59.2 | 289.9 | 137.9 | 170.3 | 100.6 | 119.5 | 130 | 104.9 | 120.2 | 99.6 | 132.1
1939 | 1794 | -6.4 | 0 | 0 | 116.6 | 104.6 | 97.5 | 96.2 | 130.8 | 20 | 21.1 | 30.7 | 14.3 | 240.2 | 23.2 | 114.5 | 50.8 | 26.9 | 129.5 | 82.1 | 221.2 | 113.8 | 58.9 | 289.4 | 137.8 | 170.2 | 100.4 | 119.4 | 129.8 | 104.8 | 120.1 | 99.6 | 132
1940 | 1795 | -6.2 | 0 | 0 | 116.5 | 104.5 | 97.4 | 96.1 | 130.8 | 20 | 21.1 | 30.8 | 13.1 | 245.2 | 25.1 | 114.5 | 50.6 | 26.9 | 129.5 | 81.9 | 220.9 | 113.8 | 58.7 | 288.9 | 137.6 | 170 | 100.3 | 119.2 | 129.7 | 104.8 | 119.9 | 99.6 | 131.9
1941 | 1796 | -6.3 | 0 | 0 | 116.5 | 104.4 | 97.4 | 96 | 130.7 | 19.8 | 21.1 | 30.9 | 9.6 | 239.7 | 29.6 | 114.4 | 50.9 | 27 | 129.4 | 81.8 | 220.7 | 113.6 | 58.5 | 288.6 | 137.5 | 169.9 | 100.2 | 119.1 | 129.6 | 104.7 | 119.8 | 99.5 | 131.8
1942 | 1797 | -6.3 | 0 | 0 | 116.5 | 104.3 | 97.3 | 95.9 | 130.6 | 19.7 | 21.1 | 31 | 6.9 | 237.4 | 22 | 114.3 | 50.6 | 27 | 129.4 | 81.7 | 220.4 | 113.1 | 58.2 | 288.2 | 137.4 | 169.8 | 100 | 119 | 129.4 | 104.6 | 119.8 | 99.4 | 131.7
1943 | 1798 | -6.3 | 0 | 0 | 116.5 | 104.2 | 97.1 | 95.8 | 130.4 | 19.6 | 21.1 | 31 | 7.2 | 214.4 | 14.6 | 114.3 | 50.2 | 27 | 129.4 | 81.6 | 220.1 | 113.2 | 58 | 288 | 137.5 | 169.6 | 99.9 | 118.8 | 129.2 | 104.5 | 119.7 | 99.2 | 131.5
1944 | 1799 | -6.3 | 0 | 0 | 116.4 | 104.1 | 96.9 | 95.8 | 130.3 | 19.6 | 21.1 | 31 | 9.6 | 237.7 | 17.5 | 114.2 | 49.9 | 27 | 129.2 | 81.5 | 219.8 | 113.1 | 57.9 | 287.7 | 137.4 | 169.5 | 99.9 | 118.6 | 129.1 | 104.4 | 119.6 | 99.1 | 131.4
1945 | 1800 | -6.7 | 0 | 0 | 116.6 | 104 | 96.8 | 95.7 | 130.2 | 19.5 | 21.1 | 31.1 | 12.6 | 242.6 | 20.3 | 114.1 | 49.6 | 27 | 129.1 | 81.3 | 219.5 | 113.2 | 58 | 287.6 | 137.4 | 169.3 | 99.9 | 118.6 | 129 | 104.3 | 119.5 | 98.9 | 131.3
1946 | 1801 | -6.9 | 0 | 0 | 116.5 | 103.9 | 96.8 | 95.7 | 130.2 | 19.6 | 21.1 | 31.3 | 10.5 | 241.1 | 20.1 | 114 | 49.7 | 27.1 | 128.9 | 81.1 | 219.2 | 113.4 | 57.8 | 287.4 | 137.3 | 169.2 | 99.8 | 118.5 | 128.9 | 104.2 | 119.4 | 98.9 | 131.2
1947 | 1802 | -6.8 | 0 | 0 | 116.4 | 103.8 | 96.7 | 95.5 | 130.1 | 19.6 | 21.1 | 31.4 | 6.8 | 243.3 | 21.2 | 114 | 49.8 | 27.1 | 128.8 | 80.9 | 218.9 | 113.3 | 57.7 | 287.1 | 137.1 | 169 | 99.7 | 118.4 | 128.9 | 104.1 | 119.3 | 98.7 | 131
1948 | 1803 | -6.8 | 0 | 0 | 116.3 | 103.7 | 96.7 | 95.4 | 130 | 19.5 | 21.1 | 31.4 | 7.4 | 240 | 22.7 | 113.7 | 49.7 | 27 | 128.7 | 80.8 | 218.6 | 113.1 | 57.8 | 286.8 | 136.8 | 168.9 | 99.5 | 118.3 | 128.7 | 104 | 119.1 | 98.5 | 131
1949 | 1804 | -6.7 | 0 | 0 | 116.4 | 103.7 | 96.6 | 95.2 | 129.9 | 19.6 | 21.1 | 31.4 | 6.2 | 258.6 | 20.5 | 113.5 | 49.7 | 27 | 128.6 | 80.6 | 218.4 | 112.8 | 57.7 | 286.5 | 136.6 | 168.7 | 99.5 | 118.2 | 128.6 | 103.9 | 119 | 98.4 | 130.8
1950 | 1805 | -6.6 | 0 | 0 | 116.5 | 103.5 | 96.5 | 95.1 | 129.7 | 19.6 | 21.1 | 31.4 | 8.5 | 241.3 | 16.8 | 113.3 | 49.4 | 27.1 | 128.6 | 80.5 | 218.1 | 112.6 | 57.6 | 286.3 | 136.5 | 168.6 | 99.3 | 118.1 | 128.5 | 103.7 | 118.9 | 98.3 | 130.7
1951 | 1806 | -6.1 | 0 | 0 | 116.2 | 103.3 | 96.5 | 95.1 | 129.5 | 19.7 | 21.1 | 31.3 | 7.1 | 245.3 | 12.7 | 113.1 | 49.2 | 27.1 | 128.5 | 80.3 | 217.8 | 112.8 | 57.4 | 286 | 136.5 | 168.5 | 99.2 | 118.1 | 128.5 | 103.6 | 118.8 | 98.2 | 130.6
1952 | 1807 | -6.3 | 0 | 0 | 116 | 103.2 | 96.4 | 95 | 129.4 | 19.7 | 21.1 | 31.2 | 5.8 | 248 | 11.9 | 113 | 49.3 | 27 | 128.2 | 80.2 | 217.5 | 112.9 | 57.3 | 285.7 | 136.4 | 168.3 | 99.1 | 118 | 128.5 | 103.5 | 118.7 | 98.1 | 130.5
1953 | 1808 | -6.5 | 0 | 0 | 116 | 103 | 96.4 | 94.9 | 129.3 | 19.7 | 21.1 | 31.2 | 8.6 | 248.8 | 15.9 | 112.9 | 49.3 | 27 | 127.8 | 80.1 | 217.2 | 112.9 | 57.1 | 285.3 | 136.3 | 168.2 | 99 | 117.8 | 128.4 | 103.4 | 118.6 | 98.1 | 130.4
1954 | 1809 | -6.6 | 0 | 0 | 116.2 | 102.8 | 96.2 | 94.8 | 129.2 | 19.6 | 21.1 | 31.2 | 9.8 | 259.2 | 19.3 | 112.7 | 49.3 | 27 | 127.4 | 80 | 217 | 112.8 | 57 | 284.9 | 136.1 | 168 | 98.9 | 117.7 | 128.3 | 103.4 | 118.5 | 98.1 | 130.2
1955 | 1810 | -6.5 | 0 | 0 | 116.4 | 102.6 | 96 | 94.6 | 129.1 | 19.5 | 21.1 | 31.2 | 11.7 | 229 | 22.6 | 112.5 | 49.4 | 26.9 | 127.2 | 79.9 | 216.7 | 112.5 | 56.9 | 284.4 | 135.9 | 167.9 | 98.8 | 117.6 | 128.1 | 103.3 | 118.4 | 98 | 130.2
1956 | 1811 | -6.4 | 0 | 0 | 116.2 | 102.5 | 95.9 | 94.5 | 128.9 | 19.4 | 21.1 | 31.1 | 11.5 | 236.3 | 19.5 | 112.2 | 49.6 | 26.9 | 127 | 79.8 | 216.4 | 112.1 | 56.8 | 284 | 135.7 | 167.7 | 98.7 | 117.6 | 128 | 103.2 | 118.3 | 98 | 130
1957 | 1812 | -6.4 | 0 | 0 | 115.9 | 102.6 | 95.8 | 94.4 | 128.9 | 19.3 | 21.1 | 31 | 7.6 | 237.5 | 20.1 | 112 | 49.6 | 26.8 | 126.8 | 79.7 | 216.2 | 112.2 | 56.7 | 283.6 | 135.6 | 167.6 | 98.6 | 117.5 | 127.9 | 103 | 118.2 | 97.8 | 129.9
1958 | 1813 | -6.4 | 0 | 0 | 115.7 | 102.7 | 95.8 | 94.3 | 128.8 | 19.2 | 21.1 | 31 | 6.5 | 243.5 | 16.7 | 111.7 | 49.7 | 26.8 | 126.6 | 79.5 | 215.9 | 112.3 | 56.6 | 283.2 | 135.4 | 167.4 | 98.5 | 117.3 | 127.7 | 102.9 | 118.1 | 97.6 | 129.8
1959 | 1814 | -6.4 | 0 | 0 | 115.5 | 102.7 | 95.8 | 94.3 | 128.7 | 19.2 | 21.1 | 31 | 5.3 | 241.4 | 16.6 | 111.5 | 49.9 | 26.7 | 126.3 | 79.4 | 215.6 | 112.2 | 56.6 | 282.7 | 135.3 | 167.3 | 98.3 | 117.2 | 127.6 | 102.8 | 118 | 97.7 | 129.7
1960 | 1815 | -6.4 | 0 | 0 | 115.5 | 102.6 | 95.7 | 94.3 | 128.7 | 19.2 | 21.1 | 31 | 7.5 | 258.5 | 15.5 | 111.3 | 50.1 | 26.7 | 126.1 | 79.3 | 215.3 | 112 | 56.6 | 282.2 | 135.1 | 167.2 | 98.3 | 117.1 | 127.5 | 102.8 | 117.9 | 97.6 | 129.6
1961 | 1816 | -6.3 | 0 | 0 | 115.4 | 102.5 | 95.6 | 94.2 | 128.6 | 19.2 | 21.1 | 31.1 | 8.5 | 234.1 | 13.8 | 111.1 | 50.3 | 26.7 | 125.9 | 79.1 | 215 | 111.8 | 56.5 | 281.7 | 134.9 | 167 | 98.2 | 117 | 127.4 | 102.7 | 117.9 | 97.5 | 129.5
1962 | 1817 | -6.2 | 0 | 0 | 115.2 | 102.3 | 95.4 | 94.2 | 128.5 | 19.2 | 21.1 | 31.1 | 7.3 | 241.9 | 13.6 | 110.9 | 50.3 | 26.7 | 125.8 | 79.1 | 214.6 | 111.7 | 56.4 | 281.1 | 134.8 | 166.9 | 98.2 | 117 | 127.3 | 102.6 | 117.8 | 97.4 | 129.4
1963 | 1818 | -6.3 | 0 | 0 | 115 | 102.1 | 95.2 | 94.2 | 128.4 | 19.3 | 21.2 | 31.2 | 9.1 | 254.2 | 13.7 | 110.5 | 50.2 | 26.7 | 125.7 | 79 | 214.3 | 111.4 | 56.5 | 280.7 | 134.5 | 166.7 | 98.2 | 116.9 | 127.2 | 102.5 | 117.8 | 97.3 | 129.3
1964 | 1819 | -5.9 | 0 | 0 | 114.7 | 102.1 | 95.2 | 94.1 | 128.3 | 19.4 | 21.2 | 31 | 8.4 | 251.4 | 17.1 | 110.3 | 49.7 | 26.7 | 125.7 | 78.9 | 213.9 | 111.3 | 56.6 | 280.3 | 134.3 | 166.6 | 98.1 | 116.8 | 127 | 102.3 | 117.7 | 97.1 | 129.2
1965 | 1820 | -6.1 | 0 | 0 | 114.4 | 102.1 | 95.1 | 94 | 128.2 | 19.4 | 21.2 | 30.9 | 8.6 | 255.9 | 16.6 | 110.2 | 49.5 | 26.7 | 125.5 | 78.8 | 213.5 | 111.1 | 56.6 | 279.8 | 134.1 | 166.5 | 98 | 116.7 | 126.9 | 102.2 | 117.6 | 97 | 129.1
1966 | 1821 | -6.6 | 0 | 0 | 114.2 | 102.1 | 95.1 | 94 | 128.1 | 19.4 | 21.1 | 30.9 | 6.8 | 240.4 | 15 | 109.9 | 49.4 | 26.7 | 125.5 | 78.8 | 213.2 | 110.6 | 56.6 | 279.5 | 133.8 | 166.3 | 98 | 116.5 | 126.8 | 102.2 | 117.5 | 97 | 129
1967 | 1822 | -6.3 | 0 | 0 | 114.1 | 102.1 | 95.1 | 93.8 | 128 | 19.4 | 21.2 | 30.9 | 7.8 | 240.3 | 17.8 | 109.7 | 49.4 | 26.6 | 125.5 | 78.7 | 212.8 | 110.3 | 56.9 | 279.2 | 133.6 | 166.2 | 97.9 | 116.4 | 126.7 | 102.1 | 117.4 | 96.9 | 128.9
1968 | 1823 | -6.4 | 0 | 0 | 114.1 | 102 | 95 | 93.7 | 127.9 | 19.4 | 21.2 | 30.9 | 8.4 | 253.1 | 18.1 | 109.4 | 49.4 | 26.6 | 125.3 | 78.5 | 212.4 | 110.3 | 56.8 | 279 | 133.5 | 166 | 97.8 | 116.3 | 126.6 | 102 | 117.3 | 96.8 | 128.8
1969 | 1824 | -6.6 | 0 | 0 | 114.2 | 101.9 | 95 | 93.7 | 127.8 | 19.3 | 21.2 | 30.9 | 6.9 | 244.9 | 18.6 | 109.2 | 49.4 | 26.5 | 125.2 | 78.4 | 212.1 | 110.2 | 56.7 | 278.6 | 133.5 | 165.9 | 97.7 | 116.2 | 126.5 | 101.9 | 117.3 | 96.7 | 128.7
1970 | 1825 | -6.7 | 0 | 0 | 114.1 | 101.7 | 94.9 | 93.7 | 127.7 | 19.2 | 21.2 | 30.8 | 6.7 | 250.7 | 17.8 | 109.1 | 49.5 | 26.5 | 125 | 78.3 | 211.7 | 110.1 | 56.6 | 278.5 | 133.4 | 165.7 | 97.6 | 116.2 | 126.4 | 101.8 | 117.2 | 96.6 | 128.6
1971 | 1826 | -6.6 | 0 | 0 | 113.9 | 101.6 | 94.8 | 93.7 | 127.6 | 19.2 | 21.2 | 30.9 | 7 | 240.9 | 13.7 | 108.9 | 49.5 | 26.4 | 124.9 | 78.2 | 211.4 | 109.9 | 56.6 | 278.1 | 133.1 | 165.6 | 97.6 | 116.1 | 126.3 | 101.6 | 117 | 96.5 | 128.5
1972 | 1827 | -6.6 | 0 | 0 | 113.6 | 101.4 | 94.8 | 93.6 | 127.6 | 19.1 | 21.2 | 30.9 | 7.7 | 256.2 | 12.7 | 108.6 | 49.4 | 26.4 | 124.7 | 78.1 | 211 | 109.6 | 56.5 | 277.9 | 132.9 | 165.5 | 97.5 | 116 | 126.2 | 101.6 | 116.9 | 96.5 | 128.4
1973 | 1828 | -6.6 | 0 | 0 | 113.5 | 101.1 | 94.7 | 93.5 | 127.5 | 19 | 21.2 | 30.9 | 7.2 | 240.4 | 12.4 | 108.3 | 49.1 | 26.3 | 124.6 | 78 | 210.6 | 109.3 | 56.3 | 277.6 | 132.8 | 165.3 | 97.4 | 115.9 | 126.1 | 101.5 | 116.8 | 96.3 | 128.2
1974 | 1829 | -6.3 | 0 | 0 | 113.5 | 101 | 94.6 | 93.3 | 127.4 | 19 | 21.2 | 30.9 | 5.4 | 245.9 | 14.1 | 107.9 | 48.8 | 26.2 | 124.5 | 77.9 | 210.2 | 109.1 | 56.2 | 277.2 | 132.6 | 165.2 | 97.4 | 115.8 | 126.1 | 101.4 | 116.7 | 96.3 | 128.2
1975 | 1830 | -5.2 | 0 | 0 | 113.4 | 101 | 94.4 | 93.1 | 127.3 | 18.9 | 21.2 | 30.9 | 5.5 | 245.6 | 16.8 | 107.4 | 48.7 | 26.2 | 124.4 | 77.8 | 209.9 | 109.1 | 56.2 | 277.2 | 132.5 | 165 | 97.4 | 115.7 | 126 | 101.3 | 116.6 | 96.2 | 128.1
1976 | 1831 | -4.9 | 0 | 0 | 113.3 | 101 | 94.3 | 93 | 127.2 | 18.9 | 21.2 | 30.8 | 4.4 | 252 | 18 | 107.2 | 48.7 | 26.3 | 124.1 | 77.7 | 209.5 | 109 | 56.3 | 277.1 | 132.6 | 164.9 | 97.3 | 115.6 | 125.8 | 101.2 | 116.5 | 96.1 | 128
1977 | 1832 | -5.4 | 0 | 0 | 113.1 | 101.1 | 94.1 | 93 | 127 | 18.9 | 21.2 | 30.8 | 3.7 | 264.4 | 15.7 | 107.1 | 48.6 | 26.3 | 123.9 | 77.6 | 209.2 | 108.9 | 56.5 | 276.8 | 132.6 | 164.7 | 97.2 | 115.5 | 125.7 | 101.1 | 116.5 | 96.1 | 127.9
1978 | 1833 | -5.8 | 0 | 0 | 112.9 | 101 | 94 | 93 | 127 | 19 | 21.2 | 30.7 | 5.7 | 258.8 | 11.1 | 107.1 | 48.5 | 26.3 | 123.7 | 77.5 | 208.8 | 108.8 | 56.8 | 276.5 | 132.6 | 164.6 | 97.2 | 115.3 | 125.6 | 101 | 116.4 | 96.1 | 127.7
1979 | 1834 | -5.2 | 0 | 0 | 113 | 100.8 | 93.9 | 93 | 126.9 | 19.1 | 21.2 | 30.7 | 7.2 | 263.5 | 9.7 | 107 | 48.6 | 26.3 | 123.6 | 77.4 | 208.5 | 108.4 | 57.1 | 276.2 | 132.5 | 164.5 | 97.1 | 115.2 | 125.5 | 101 | 116.4 | 96 | 127.6
1980 | 1835 | -4.6 | 0 | 0 | 112.9 | 100.7 | 93.8 | 93 | 126.8 | 19.1 | 21.2 | 30.7 | 8.1 | 262.4 | 11.6 | 106.9 | 48.6 | 26.3 | 123.3 | 77.3 | 208.2 | 108.2 | 57.3 | 276 | 132.5 | 164.3 | 97 | 115.1 | 125.4 | 100.8 | 116.3 | 95.9 | 127.5
1981 | 1836 | -4.8 | 0 | 0 | 112.8 | 100.8 | 93.7 | 92.9 | 126.7 | 19.1 | 21.2 | 30.7 | 6.7 | 267 | 14 | 107 | 48.7 | 26.2 | 123.2 | 77.2 | 207.9 | 108.1 | 57.3 | 275.7 | 132.4 | 164.2 | 97 | 115 | 125.4 | 100.8 | 116.2 | 95.7 | 127.4
1982 | 1837 | -5.5 | 0 | 0 | 112.7 | 100.8 | 93.6 | 92.8 | 126.6 | 19.1 | 21.2 | 30.7 | 8.1 | 269.2 | 15.6 | 107 | 48.8 | 26.3 | 122.9 | 77.1 | 207.6 | 108.2 | 57 | 275.4 | 132.3 | 164.1 | 97 | 114.9 | 125.3 | 100.7 | 116 | 95.7 | 127.3
1983 | 1838 | -5.6 | 0 | 0 | 112.5 | 100.8 | 93.4 | 92.7 | 126.5 | 19.1 | 21.2 | 30.7 | 9.2 | 271.8 | 13.9 | 106.8 | 48.9 | 26.3 | 122.7 | 77 | 207.3 | 108.2 | 57 | 275.1 | 132.2 | 163.9 | 96.9 | 114.9 | 125.2 | 100.6 | 116 | 95.6 | 127.2
1984 | 1839 | -4.9 | 0 | 0 | 112.6 | 100.8 | 93.3 | 92.7 | 126.4 | 19.2 | 21.2 | 30.6 | 9.2 | 264.4 | 13 | 106.7 | 49 | 26.2 | 122.5 | 76.9 | 207 | 108.1 | 56.8 | 274.8 | 131.9 | 163.8 | 96.8 | 114.7 | 125.1 | 100.5 | 115.9 | 95.5 | 127.1
1985 | 1840 | -4.5 | 0 | 0 | 112.7 | 100.9 | 93.2 | 92.6 | 126.4 | 19.1 | 21.2 | 30.5 | 10.3 | 261.4 | 15.4 | 106.6 | 48.8 | 26.2 | 122.4 | 76.8 | 206.8 | 108.1 | 56.4 | 274.5 | 131.7 | 163.7 | 96.7 | 114.5 | 125 | 100.4 | 115.8 | 95.4 | 127
1986 | 1841 | -3.4 | 0 | 0 | 112.7 | 100.9 | 93.2 | 92.5 | 126.4 | 19.1 | 21.2 | 30.5 | 9.7 | 265.8 | 16.1 | 106.6 | 48.7 | 26.2 | 122.3 | 76.7 | 206.5 | 107.9 | 56.2 | 274.3 | 131.6 | 163.5 | 96.7 | 114.5 | 124.9 | 100.3 | 115.7 | 95.2 | 126.9
1987 | 1842 | -3.7 | 0 | 0 | 112.6 | 100.9 | 93 | 92.5 | 126.2 | 19 | 21.2 | 30.5 | 9.7 | 274.9 | 12.4 | 106.5 | 48.5 | 26.1 | 122.1 | 76.5 | 206.3 | 108 | 56 | 274 | 131.4 | 163.4 | 96.8 | 114.4 | 124.8 | 100.2 | 115.6 | 95.1 | 126.8
1988 | 1843 | -4.8 | 0 | 0 | 112.5 | 100.9 | 92.9 | 92.4 | 126.2 | 19 | 21.2 | 30.5 | 7.7 | 248.5 | 11.5 | 106.3 | 48.4 | 26 | 122 | 76.5 | 206.1 | 108.1 | 55.9 | 273.5 | 131.4 | 163.2 | 96.7 | 114.4 | 124.7 | 100.1 | 115.5 | 94.9 | 126.6
1989 | 1844 | -4.6 | 0 | 0 | 112.4 | 100.7 | 92.9 | 92.3 | 126.1 | 18.9 | 21.2 | 30.5 | 8.7 | 259.1 | 12 | 106.2 | 48.3 | 26 | 122 | 76.5 | 205.8 | 108.2 | 56 | 273 | 131.2 | 163.1 | 96.6 | 114.3 | 124.7 | 100 | 115.4 | 94.9 | 126.5
1990 | 1845 | -3.8 | 0 | 0 | 112.1 | 100.6 | 92.9 | 92.3 | 126 | 18.9 | 21.2 | 30.5 | 7.3 | 263.2 | 11.9 | 106 | 48.3 | 25.9 | 121.8 | 76.4 | 205.5 | 108 | 56 | 272.6 | 130.9 | 163 | 96.6 | 114.3 | 124.5 | 100 | 115.3 | 94.9 | 126.4
1991 | 1846 | -4.8 | 0 | 0 | 112.2 | 100.4 | 92.9 | 92.2 | 125.9 | 18.8 | 21.2 | 30.5 | 6.8 | 256.1 | 10.6 | 106 | 48.2 | 25.8 | 121.7 | 76.3 | 205.2 | 107.8 | 55.9 | 272 | 130.7 | 162.8 | 96.6 | 114.3 | 124.4 | 99.9 | 115.2 | 94.8 | 126.3
1992 | 1847 | -4.4 | 0 | 0 | 112 | 100.3 | 92.8 | 92.1 | 125.8 | 18.8 | 21.2 | 30.6 | 8.7 | 254.1 | 10.2 | 106 | 48.2 | 25.8 | 121.6 | 76.3 | 204.9 | 107.7 | 55.8 | 271.6 | 130.6 | 162.7 | 96.4 | 114.2 | 124.2 | 99.8 | 115.1 | 94.6 | 126.2
1993 | 1848 | -4.7 | 0 | 0 | 111.9 | 100.1 | 92.8 | 92 | 125.6 | 18.7 | 21.2 | 30.7 | 9.1 | 241.8 | 11 | 105.9 | 48.2 | 25.7 | 121.5 | 76.2 | 204.6 | 107.4 | 55.8 | 271.4 | 130.3 | 162.6 | 96.3 | 114.2 | 124.1 | 99.7 | 115 | 94.5 | 126.1
1994 | 1849 | -5.4 | 0 | 0 | 112.1 | 100 | 92.7 | 92 | 125.4 | 18.7 | 21.2 | 30.8 | 9 | 264.8 | 9.7 | 105.9 | 47.9 | 25.7 | 121.2 | 76.1 | 204.3 | 107.2 | 55.8 | 271.2 | 130.1 | 162.4 | 96.3 | 114 | 124 | 99.6 | 114.9 | 94.4 | 126
1995 | 1850 | -4.9 | 0 | 0 | 112 | 99.9 | 92.6 | 91.9 | 125.3 | 18.7 | 21.2 | 30.8 | 7.6 | 252.4 | 13.4 | 105.9 | 47.9 | 25.7 | 121 | 76 | 204 | 107 | 55.6 | 271 | 130 | 162.3 | 96.1 | 113.9 | 123.8 | 99.5 | 114.8 | 94.3 | 125.9
1996 | 1851 | -5.2 | 0 | 0 | 111.7 | 99.8 | 92.6 | 91.8 | 125.2 | 18.6 | 21.2 | 30.7 | 7.6 | 254.6 | 14.3 | 105.9 | 47.8 | 25.8 | 120.8 | 75.9 | 203.7 | 106.8 | 55.5 | 270.8 | 129.8 | 162.2 | 95.9 | 113.8 | 123.6 | 99.4 | 114.8 | 94.3 | 125.8
1997 | 1852 | -6.1 | 0 | 0 | 111.6 | 99.7 | 92.5 | 91.8 | 125 | 18.6 | 21.2 | 30.7 | 7 | 247.3 | 10.7 | 105.9 | 47.7 | 25.7 | 120.7 | 75.8 | 203.4 | 106.6 | 55.4 | 270.7 | 129.6 | 162 | 95.8 | 113.6 | 123.5 | 99.3 | 114.7 | 94.3 | 125.7
1998 | 1853 | -6.3 | 0 | 0 | 111.4 | 99.7 | 92.5 | 91.7 | 125 | 18.6 | 21.2 | 30.7 | 6.9 | 235.9 | 15.7 | 105.6 | 47.7 | 25.6 | 120.6 | 75.7 | 203.1 | 106.4 | 55.2 | 270.4 | 129.5 | 161.9 | 95.7 | 113.5 | 123.4 | 99.2 | 114.7 | 94.3 | 125.7
1999 | 1854 | -6.2 | 0 | 0 | 111.2 | 99.6 | 92.5 | 91.6 | 124.9 | 18.5 | 21.2 | 30.7 | 7.1 | 241.5 | 19.1 | 105.4 | 47.6 | 25.6 | 120.6 | 75.7 | 202.7 | 106.2 | 55.2 | 270.2 | 129.3 | 161.8 | 95.6 | 113.4 | 123.3 | 99.2 | 114.6 | 94.3 | 125.6
2000 | 1855 | -6.1 | 0 | 0 | 111.2 | 99.5 | 92.4 | 91.5 | 124.8 | 18.5 | 21.2 | 30.7 | 8.8 | 250.8 | 19 | 105.2 | 47.5 | 25.5 | 120.5 | 75.6 | 202.4 | 106.2 | 55 | 270 | 129.2 | 161.6 | 95.5 | 113.3 | 123.2 | 99.1 | 114.5 | 94.2 | 125.5
2001 | 1856 | -4.9 | 0 | 0 | 111.2 | 99.4 | 92.4 | 91.4 | 124.7 | 18.5 | 21.2 | 30.7 | 9.1 | 258.5 | 17.5 | 105 | 47.4 | 25.5 | 120.4 | 75.4 | 202 | 106.4 | 54.7 | 269.9 | 129 | 161.5 | 95.4 | 113.1 | 123.1 | 99 | 114.5 | 94.1 | 125.4
2002 | 1857 | -4.4 | 0 | 0 | 111.1 | 99.3 | 92.3 | 91.4 | 124.6 | 18.4 | 21.2 | 30.6 | 11.1 | 256.1 | 14.5 | 104.9 | 47.3 | 25.5 | 120.2 | 75.4 | 201.7 | 106.8 | 54.5 | 269.7 | 128.9 | 161.4 | 95.3 | 113 | 123.1 | 98.9 | 114.4 | 94 | 125.3
2003 | 1858 | -5.3 | 0 | 0 | 111.1 | 99.2 | 92.2 | 91.3 | 124.5 | 18.4 | 21.2 | 30.5 | 11.8 | 263.9 | 11.7 | 104.8 | 46.7 | 25.5 | 120.2 | 75.3 | 201.4 | 106.9 | 54.4 | 269.5 | 128.9 | 161.2 | 95.3 | 113 | 123 | 98.8 | 114.3 | 93.9 | 125.2
2004 | 1859 | -5.7 | 0 | 0 | 111 | 99.2 | 92.2 | 91.2 | 124.4 | 18.5 | 21.2 | 30.4 | 10.6 | 269.6 | 11.5 | 104.5 | 46.8 | 25.5 | 120.2 | 75.2 | 201.1 | 106.8 | 54.3 | 269.2 | 128.8 | 161.1 | 95.2 | 112.9 | 122.9 | 98.7 | 114.2 | 93.8 | 125
2005 | 1860 | -4.8 | 0 | 0 | 110.9 | 99 | 92.1 | 91.2 | 124.3 | 18.4 | 21.2 | 30.4 | 9.7 | 257.7 | 10.8 | 104.2 | 46.9 | 25.5 | 120 | 75.1 | 200.8 | 106.5 | 54.2 | 268.9 | 128.8 | 161 | 95.1 | 112.9 | 122.9 | 98.6 | 114.1 | 93.8 | 125
2006 | 1861 | -5.6 | 0 | 0 | 110.8 | 99 | 92 | 91.1 | 124.1 | 18.5 | 21.2 | 30.4 | 8.4 | 248.6 | 11 | 104 | 46.9 | 25.4 | 119.9 | 75 | 200.5 | 106.3 | 54.1 | 268.6 | 128.6 | 160.8 | 95.1 | 112.8 | 122.8 | 98.5 | 113.9 | 93.7 | 124.8
2007 | 1862 | -6 | 0 | 0 | 110.6 | 98.9 | 91.8 | 91.1 | 124 | 18.4 | 21.2 | 30.4 | 8.3 | 242.3 | 15.6 | 103.6 | 46.8 | 25.4 | 119.8 | 75 | 200.2 | 106.1 | 54 | 268.3 | 128.4 | 160.7 | 95 | 112.8 | 122.8 | 98.5 | 113.8 | 93.7 | 124.7
2008 | 1863 | -5.4 | 0 | 0 | 110.3 | 98.9 | 91.6 | 91 | 124 | 18.4 | 21.2 | 30.4 | 5.8 | 246.8 | 19.2 | 103.2 | 46.9 | 25.3 | 119.7 | 74.9 | 199.9 | 106.2 | 53.9 | 267.8 | 128.1 | 160.6 | 94.9 | 112.7 | 122.7 | 98.4 | 113.8 | 93.6 | 124.6
2009 | 1864 | -4.6 | 0 | 0 | 110 | 98.8 | 91.6 | 91 | 123.9 | 18.4 | 21.2 | 30.3 | 7.3 | 231.7 | 20.2 | 102.8 | 46.9 | 25.3 | 119.7 | 74.8 | 199.6 | 106.1 | 53.8 | 267.2 | 127.9 | 160.4 | 94.8 | 112.6 | 122.6 | 98.3 | 113.7 | 93.4 | 124.5
2010 | 1865 | -4.4 | 0 | 0 | 110 | 98.8 | 91.4 | 90.9 | 123.8 | 18.5 | 21.2 | 30.3 | 6.5 | 248.2 | 21.1 | 102.5 | 46.8 | 25.3 | 119.6 | 74.6 | 199.2 | 106.1 | 53.8 | 267 | 127.9 | 160.3 | 94.7 | 112.5 | 122.5 | 98.2 | 113.5 | 93.2 | 124.4
2011 | 1866 | -4.7 | 0 | 0 | 110.1 | 98.7 | 91.3 | 90.8 | 123.6 | 18.6 | 21.2 | 30.2 | 7.2 | 235.7 | 18.2 | 102.5 | 46.6 | 25.3 | 119.3 | 74.5 | 198.9 | 105.8 | 53.8 | 266.7 | 127.8 | 160.1 | 94.7 | 112.3 | 122.4 | 98.1 | 113.4 | 93.1 | 124.3
2012 | 1867 | -5.4 | 0 | 0 | 109.8 | 98.4 | 91.4 | 90.5 | 123.5 | 18.7 | 21.2 | 30.1 | 9.2 | 241.4 | 16.2 | 102.5 | 46.6 | 25.3 | 118.9 | 74.4 | 198.6 | 105.7 | 53.6 | 266.4 | 127.7 | 160 | 94.7 | 112.2 | 122.1 | 98 | 113.2 | 93 | 124.2
2013 | 1868 | -5.9 | 0 | 0 | 109.7 | 98.1 | 91.7 | 90.2 | 123.3 | 18.8 | 21.2 | 29.9 | 7.2 | 253.9 | 15.5 | 102.4 | 46.7 | 25.3 | 118.6 | 74.3 | 198.3 | 105.7 | 53.3 | 266.3 | 127.6 | 159.9 | 94.8 | 112.2 | 122 | 97.9 | 113.1 | 92.8 | 124
2014 | 1869 | -6.2 | 0 | 0 | 109.9 | 97.8 | 91.6 | 89.9 | 123.2 | 18.9 | 21.2 | 29.7 | 5.9 | 244.4 | 15.6 | 102.3 | 46.5 | 25.4 | 118.2 | 74.2 | 198.1 | 105.6 | 53.2 | 266 | 127.3 | 159.7 | 94.7 | 112.1 | 121.9 | 97.8 | 112.9 | 92.6 | 123.9
2015 | 1870 | -6.2 | 0 | 0 | 110.3 | 97.5 | 91.1 | 89.9 | 123.2 | 19 | 21.2 | 29.6 | 5.2 | 241.1 | 19.1 | 102.2 | 46.4 | 25.4 | 117.8 | 74 | 197.8 | 105.5 | 53.1 | 265.5 | 126.9 | 159.6 | 94.5 | 112 | 121.8 | 97.7 | 112.7 | 92.5 | 123.9
2016 | 1871 | -6.2 | 0 | 0 | 110.5 | 97.3 | 90.6 | 89.9 | 123 | 19.1 | 21.2 | 29.5 | 5 | 243.1 | 18 | 102.1 | 46.3 | 25.4 | 117.6 | 73.9 | 197.5 | 105.1 | 52.8 | 265.2 | 126.9 | 159.5 | 94.3 | 111.8 | 121.8 | 97.6 | 112.6 | 92.6 | 123.7
2017 | 1872 | -6.2 | 0 | 0 | 110.5 | 97.4 | 90.4 | 89.9 | 122.8 | 19.2 | 21.2 | 29.5 | 3.4 | 245.9 | 15.9 | 102 | 46.4 | 25.5 | 117.3 | 73.8 | 197.2 | 104.8 | 52.5 | 264.8 | 126.7 | 159.3 | 94.2 | 111.6 | 121.7 | 97.6 | 112.5 | 92.7 | 123.6
2018 | 1873 | -6.1 | 0 | 0 | 110.1 | 97.5 | 90.4 | 89.8 | 122.7 | 19.2 | 21.2 | 29.6 | 2.4 | 262.4 | 14.2 | 101.9 | 46.3 | 25.5 | 116.9 | 73.7 | 196.8 | 104.5 | 52.1 | 264.6 | 126.5 | 159.2 | 94.1 | 111.4 | 121.6 | 97.5 | 112.4 | 92.7 | 123.6
2019 | 1874 | -6.2 | 0 | 0 | 109.6 | 97.5 | 90.4 | 89.8 | 122.6 | 19.3 | 21.2 | 29.8 | 2.5 | 286 | 10.7 | 101.8 | 46.2 | 25.5 | 116.8 | 73.5 | 196.5 | 104.3 | 51.8 | 264.5 | 126.4 | 159.1 | 94 | 111.3 | 121.4 | 97.4 | 112.4 | 92.6 | 123.5
2020 | 1875 | -6.1 | 0 | 0 | 109.3 | 97.5 | 90.4 | 89.7 | 122.6 | 19.4 | 21.2 | 29.8 | 6.9 | 262 | 10.4 | 101.7 | 46.4 | 25.5 | 116.6 | 73.4 | 196.1 | 103.9 | 51.7 | 264.1 | 126.4 | 159 | 93.9 | 111.2 | 121.3 | 97.3 | 112.3 | 92.4 | 123.4
2021 | 1876 | -6 | 0 | 0 | 109 | 97.5 | 90.4 | 89.5 | 122.5 | 19.4 | 21.2 | 29.8 | 7.2 | 257 | 10 | 101.6 | 46.6 | 25.6 | 116.4 | 73.3 | 195.8 | 103.5 | 51.6 | 263.9 | 126.2 | 158.8 | 93.7 | 111.1 | 121.2 | 97.2 | 112.2 | 92.4 | 123.4
2022 | 1877 | -6.2 | 0 | 0 | 108.8 | 97.4 | 90.4 | 89.3 | 122.4 | 19.5 | 21.2 | 29.6 | 6.2 | 262.6 | 11.4 | 101.5 | 46.5 | 25.5 | 116.2 | 73.1 | 195.5 | 103.3 | 51.3 | 263.8 | 126.1 | 158.7 | 93.7 | 111 | 121.1 | 97.2 | 112.1 | 92.4 | 123.3
2023 | 1878 | -6.2 | 0 | 0 | 109.1 | 97.2 | 90.2 | 89.3 | 122.4 | 19.5 | 21.2 | 29.5 | 5.2 | 251.1 | 14.1 | 101.4 | 46.6 | 25.5 | 116 | 72.9 | 195.3 | 103.3 | 51.1 | 263.8 | 126 | 158.5 | 93.8 | 111 | 121.1 | 97.1 | 112 | 92.3 | 123.2
2024 | 1879 | -6.3 | 0 | 0 | 108.9 | 97.1 | 90 | 89.5 | 122.3 | 19.5 | 21.2 | 29.5 | 5.2 | 244 | 19.1 | 101.3 | 46.7 | 25.5 | 115.8 | 72.8 | 195 | 103.3 | 51 | 263.6 | 125.9 | 158.4 | 93.8 | 110.9 | 121 | 97 | 112 | 92.3 | 123.1
2025 | 1880 | -6.3 | 0 | 0 | 109 | 97 | 89.9 | 89.5 | 122.1 | 19.6 | 21.2 | 29.4 | 5.8 | 241 | 20.6 | 101.3 | 46.5 | 25.5 | 115.6 | 72.7 | 194.7 | 103.2 | 51 | 263 | 125.8 | 158.3 | 93.6 | 110.8 | 120.9 | 96.9 | 111.9 | 92.1 | 123
2026 | 1881 | -6.3 | 0 | 0 | 109.2 | 96.8 | 89.8 | 89.3 | 122 | 19.6 | 21.2 | 29.4 | 6.1 | 259.5 | 18.8 | 101.2 | 46.6 | 25.5 | 115.5 | 72.5 | 194.4 | 103.1 | 51.1 | 262.5 | 125.7 | 158.2 | 93.4 | 110.7 | 120.8 | 96.8 | 111.7 | 92 | 122.9
2027 | 1882 | -6.1 | 0 | 0 | 109.1 | 96.6 | 89.7 | 89.2 | 121.9 | 19.5 | 21.2 | 29.3 | 4.5 | 253 | 19 | 101.2 | 46.7 | 25.5 | 115.1 | 72.4 | 194.1 | 103 | 51.1 | 262.3 | 125.6 | 158 | 93.4 | 110.6 | 120.8 | 96.8 | 111.6 | 91.9 | 122.8
2028 | 1883 | -6 | 0 | 0 | 108.9 | 96.4 | 89.6 | 89 | 121.8 | 19.5 | 21.2 | 29.2 | 2.4 | 253.4 | 20.7 | 101.1 | 46.7 | 25.4 | 115.1 | 72.3 | 193.8 | 102.8 | 51 | 262.4 | 125.4 | 157.9 | 93.3 | 110.5 | 120.7 | 96.7 | 111.4 | 91.9 | 122.7
2029 | 1884 | -6 | 0 | 0 | 108.7 | 96.3 | 89.5 | 88.9 | 121.7 | 19.4 | 21.2 | 29.3 | 3.1 | 264.3 | 18.5 | 101 | 46.4 | 25.4 | 115 | 72.1 | 193.5 | 102.5 | 50.7 | 262.2 | 125.2 | 157.8 | 93.2 | 110.3 | 120.6 | 96.6 | 111.4 | 91.8 | 122.7
2030 | 1885 | -5.9 | 0 | 0 | 108.4 | 96.3 | 89.6 | 88.8 | 121.7 | 19.4 | 21.2 | 29.4 | 3.8 | 254.3 | 15.6 | 101 | 46.3 | 25.4 | 115 | 72 | 193.2 | 102.3 | 50.8 | 262.1 | 125.2 | 157.6 | 93 | 110.2 | 120.5 | 96.5 | 111.3 | 91.6 | 122.6
2031 | 1886 | -5.9 | 0 | 0 | 108.5 | 96 | 89.7 | 88.8 | 121.6 | 19.4 | 21.2 | 29.4 | 4.7 | 258.4 | 14.9 | 100.9 | 45.9 | 25.3 | 115 | 71.9 | 192.8 | 102.2 | 50.8 | 261.9 | 125.2 | 157.5 | 92.9 | 110.1 | 120.4 | 96.4 | 111.2 | 91.5 | 122.5
2032 | 1887 | -6.1 | 0 | 0 | 108.6 | 95.7 | 89.5 | 88.7 | 121.5 | 19.5 | 21.2 | 29.4 | 4.9 | 255.6 | 14.2 | 100.8 | 45.4 | 25.3 | 115 | 71.8 | 192.6 | 102 | 50.9 | 261.6 | 125.2 | 157.4 | 92.9 | 110 | 120.3 | 96.4 | 111.1 | 91.4 | 122.4
2033 | 1888 | -6.1 | 0 | 0 | 108.6 | 95.6 | 89.3 | 88.7 | 121.4 | 19.6 | 21.2 | 29.4 | 6.5 | 261.6 | 14.9 | 100.8 | 44.7 | 25.3 | 114.7 | 71.6 | 192.3 | 101.6 | 51 | 261.3 | 125.2 | 157.3 | 92.7 | 110 | 120.2 | 96.3 | 111 | 91.3 | 122.2
2034 | 1889 | -6.2 | 0 | 0 | 108.5 | 95.7 | 89 | 88.5 | 121.3 | 19.8 | 21.2 | 29.3 | 6.8 | 258.2 | 16.9 | 100.9 | 44.1 | 25.2 | 114.4 | 71.5 | 192 | 101.3 | 51.1 | 261 | 125.2 | 157.1 | 92.6 | 109.9 | 120 | 96.2 | 110.9 | 91.1 | 122.1
2035 | 1890 | -6.2 | 0 | 0 | 108.3 | 95.7 | 89 | 88.4 | 121.1 | 20 | 21.2 | 29.2 | 7.8 | 257.3 | 17 | 101 | 44.1 | 25.2 | 114.1 | 71.4 | 191.7 | 101.1 | 51.3 | 260.9 | 125.1 | 157 | 92.5 | 109.9 | 119.9 | 96.1 | 110.9 | 91.1 | 122
2036 | 1891 | -6.2 | 0 | 0 | 108.1 | 95.7 | 89 | 88.4 | 121 | 19.9 | 21.2 | 29 | 8.3 | 268.8 | 15.1 | 101 | 44.2 | 25.2 | 113.9 | 71.3 | 191.5 | 101 | 51.3 | 260.5 | 125.1 | 156.9 | 92.5 | 109.8 | 119.8 | 96 | 110.8 | 91 | 121.9
2037 | 1892 | -6.1 | 0 | 0 | 108.3 | 95.8 | 88.9 | 88.3 | 120.9 | 19.9 | 21.3 | 28.8 | 8.6 | 272.5 | 14.6 | 101 | 44.4 | 25.2 | 113.8 | 71.2 | 191.2 | 100.9 | 51.1 | 260.2 | 125.1 | 156.7 | 92.4 | 109.8 | 119.7 | 96 | 110.7 | 90.9 | 121.8
2038 | 1893 | -6.2 | 0 | 0 | 108.7 | 95.7 | 88.7 | 88.3 | 120.8 | 19.8 | 21.2 | 28.6 | 8.9 | 272 | 14.8 | 101 | 44.8 | 25.2 | 113.7 | 71.1 | 191 | 100.9 | 51 | 259.9 | 125.1 | 156.6 | 92.3 | 109.7 | 119.6 | 95.9 | 110.6 | 90.9 | 121.7
2039 | 1894 | -6.2 | 0 | 0 | 108.8 | 95.7 | 88.6 | 88.3 | 120.7 | 19.8 | 21.2 | 28.4 | 7.5 | 261.1 | 14.1 | 101 | 45 | 25.3 | 113.6 | 71 | 190.7 | 100.7 | 51.1 | 259.5 | 124.9 | 156.5 | 92.1 | 109.6 | 119.4 | 95.8 | 110.5 | 90.9 | 121.6
2040 | 1895 | -6.3 | 0 | 0 | 108.5 | 95.7 | 88.5 | 88.2 | 120.7 | 19.8 | 21.2 | 28.4 | 4.7 | 245.3 | 13.4 | 101 | 44.8 | 25.3 | 113.4 | 70.9 | 190.4 | 100.3 | 51.2 | 259.3 | 124.7 | 156.3 | 92 | 109.4 | 119.3 | 95.7 | 110.4 | 90.7 | 121.5
2041 | 1896 | -6.3 | 0 | 0 | 108.2 | 95.8 | 88.5 | 88.2 | 120.6 | 19.8 | 21.3 | 28.4 | 2.5 | 253.4 | 12 | 100.9 | 44.8 | 25.3 | 113.1 | 70.8 | 190.2 | 100.1 | 51.2 | 259.1 | 124.5 | 156.2 | 91.9 | 109.2 | 119.2 | 95.6 | 110.3 | 90.6 | 121.4
2042 | 1897 | -6.3 | 0 | 0 | 108 | 95.8 | 88.4 | 88.1 | 120.6 | 19.8 | 21.3 | 28.4 | 2.5 | 235.2 | 16.1 | 100.8 | 45 | 25.3 | 113 | 70.7 | 189.9 | 100.1 | 51.2 | 258.9 | 124.4 | 156.1 | 91.8 | 109.1 | 119.2 | 95.6 | 110.3 | 90.6 | 121.3
2043 | 1898 | -6.2 | 0 | 0 | 108 | 95.8 | 88.3 | 88.1 | 120.5 | 19.7 | 21.3 | 28.5 | 3.6 | 241.1 | 15.1 | 100.7 | 45 | 25.3 | 112.8 | 70.6 | 189.7 | 100 | 51.1 | 258.7 | 124.3 | 156 | 91.8 | 109 | 119.1 | 95.5 | 110.2 | 90.5 | 121.2
2044 | 1899 | -6.1 | 0 | 0 | 107.9 | 95.8 | 88.4 | 88 | 120.3 | 19.6 | 21.3 | 28.5 | 5.8 | 237.2 | 12.2 | 100.6 | 45.2 | 25.3 | 112.6 | 70.6 | 189.4 | 99.9 | 50.9 | 258.6 | 124.1 | 155.8 | 91.7 | 109 | 119.1 | 95.4 | 110.1 | 90.5 | 121.1
2045 | 1900 | -6.1 | 0 | 0 | 107.8 | 95.6 | 88.4 | 88 | 120.2 | 19.7 | 21.3 | 28.5 | 5 | 253.1 | 12.5 | 100.6 | 45.2 | 25.3 | 112.4 | 70.4 | 189.2 | 99.8 | 50.8 | 258.3 | 123.9 | 155.7 | 91.6 | 109 | 118.9 | 95.3 | 110.1 | 90.3 | 121
2046 | 1901 | -6.2 | 0 | 0 | 107.9 | 95.4 | 88.5 | 87.9 | 120.1 | 19.7 | 21.3 | 28.4 | 3.5 | 253.9 | 12.8 | 100.4 | 45.3 | 25.3 | 112.1 | 70.4 | 189 | 99.7 | 50.7 | 257.8 | 123.7 | 155.6 | 91.5 | 108.9 | 118.7 | 95.2 | 110 | 90.2 | 120.9
2047 | 1902 | -6.2 | 0 | 0 | 108.2 | 95.3 | 88.5 | 87.9 | 120.1 | 19.7 | 21.3 | 28.4 | 2.8 | 246.7 | 13.3 | 100.3 | 45.5 | 25.3 | 111.9 | 70.3 | 188.7 | 99.6 | 50.5 | 257.6 | 123.6 | 155.5 | 91.4 | 108.9 | 118.6 | 95.2 | 109.9 | 90.1 | 120.8
2048 | 1903 | -6.2 | 0 | 0 | 108.5 | 95.2 | 88.2 | 87.8 | 120 | 19.7 | 21.3 | 28.4 | 3 | 256.2 | 13.9 | 100.3 | 45.4 | 25.3 | 111.7 | 70.2 | 188.5 | 99.6 | 50.5 | 257.6 | 123.5 | 155.3 | 91.3 | 108.8 | 118.5 | 95.1 | 109.8 | 90.1 | 120.7
2049 | 1904 | -6.3 | 0 | 0 | 108.4 | 95.2 | 87.9 | 87.8 | 119.9 | 19.7 | 21.3 | 28.4 | 3.2 | 255.6 | 15.2 | 100.2 | 45.3 | 25.3 | 111.6 | 70.1 | 188.3 | 99.8 | 50.6 | 257.5 | 123.2 | 155.2 | 91.2 | 108.7 | 118.4 | 95 | 109.7 | 90 | 120.6
2050 | 1905 | -6.4 | 0 | 0 | 108.2 | 95.2 | 87.8 | 87.7 | 119.9 | 19.8 | 21.3 | 28.4 | 3.2 | 253.7 | 15.8 | 100.1 | 45.4 | 25.3 | 111.6 | 70 | 188.1 | 99.7 | 50.6 | 257.5 | 123.2 | 155.1 | 91.1 | 108.7 | 118.4 | 94.9 | 109.6 | 89.9 | 120.5
2051 | 1906 | -6.5 | 0 | 0 | 107.9 | 95 | 87.8 | 87.6 | 119.8 | 19.8 | 21.3 | 28.4 | 2.9 | 256.1 | 16.3 | 100 | 45.3 | 25.3 | 111.5 | 69.9 | 187.8 | 99.6 | 50.6 | 257.4 | 123.1 | 154.9 | 90.9 | 108.6 | 118.4 | 94.8 | 109.5 | 89.7 | 120.4
2052 | 1907 | -6.4 | 0 | 0 | 107.6 | 94.8 | 87.8 | 87.5 | 119.7 | 19.8 | 21.3 | 28.4 | 2.6 | 262 | 14.7 | 99.9 | 45.2 | 25.2 | 111.2 | 69.8 | 187.6 | 99.3 | 50.8 | 257.1 | 123.1 | 154.8 | 90.8 | 108.5 | 118.3 | 94.8 | 109.4 | 89.7 | 120.4
2053 | 1908 | -6.4 | 0 | 0 | 107.7 | 94.8 | 87.6 | 87.4 | 119.6 | 19.8 | 21.3 | 28.4 | 4.1 | 260.6 | 12.3 | 99.8 | 45.4 | 25.2 | 111.1 | 69.7 | 187.4 | 99 | 50.8 | 256.9 | 123.1 | 154.7 | 90.7 | 108.4 | 118 | 94.7 | 109.4 | 89.7 | 120.3
2054 | 1909 | -6.4 | 0 | 0 | 107.6 | 94.9 | 87.4 | 87.4 | 119.4 | 19.7 | 21.3 | 28.4 | 5.5 | 259.3 | 12.6 | 99.7 | 45.5 | 25.3 | 111 | 69.6 | 187.2 | 98.9 | 50.9 | 256.8 | 123 | 154.6 | 90.5 | 108.3 | 117.9 | 94.6 | 109.3 | 89.6 | 120.2
2055 | 1910 | -6.4 | 0 | 0 | 107.1 | 95 | 87.4 | 87.3 | 119.3 | 19.7 | 21.3 | 28.4 | 5.1 | 278.8 | 11.4 | 99.7 | 45.1 | 25.3 | 111 | 69.5 | 187 | 98.5 | 51 | 256.6 | 123 | 154.4 | 90.4 | 108.2 | 117.7 | 94.5 | 109.2 | 89.4 | 120.1
2056 | 1911 | -6.4 | 0 | 0 | 106.8 | 94.9 | 87.4 | 87.2 | 119.2 | 19.6 | 21.3 | 28.5 | 7.3 | 270.1 | 11.8 | 99.6 | 44.9 | 25.3 | 111 | 69.4 | 186.8 | 98.4 | 50.9 | 256.4 | 122.9 | 154.3 | 90.3 | 108.1 | 117.7 | 94.4 | 109.1 | 89.4 | 120
2057 | 1912 | -6.4 | 0 | 0 | 106.7 | 94.7 | 87.1 | 87.2 | 119.1 | 19.6 | 21.3 | 28.4 | 11.8 | 251.9 | 11.1 | 99.6 | 44.9 | 25.2 | 110.7 | 69.4 | 186.6 | 98.6 | 51 | 256.1 | 122.9 | 154.2 | 90.2 | 108 | 117.6 | 94.4 | 109.1 | 89.3 | 119.9
2058 | 1913 | -6.4 | 0 | 0 | 106.8 | 94.6 | 86.8 | 87.1 | 119 | 19.6 | 21.3 | 28.4 | 7.2 | 234.6 | 11.8 | 99.6 | 45.3 | 25.2 | 110.6 | 69.3 | 186.3 | 98.7 | 51.1 | 255.9 | 122.8 | 154 | 90.1 | 108 | 117.5 | 94.3 | 109 | 89.4 | 119.8
2059 | 1914 | -6.4 | 0 | 0 | 106.5 | 94.4 | 86.6 | 87 | 118.8 | 19.6 | 21.3 | 28.4 | 5.2 | 234.9 | 11.2 | 99.6 | 45.5 | 25.2 | 110.7 | 69.1 | 186.1 | 98.8 | 51 | 255.6 | 122.7 | 153.9 | 90 | 107.9 | 117.5 | 94.2 | 109 | 89.3 | 119.7
2060 | 1915 | -6.4 | 0 | 0 | 106.4 | 94.3 | 86.7 | 87 | 118.7 | 19.7 | 21.3 | 28.4 | 6.8 | 249.1 | 12.2 | 99.5 | 45.4 | 25.2 | 110.6 | 69 | 185.9 | 98.7 | 50.9 | 255.2 | 122.5 | 153.8 | 89.8 | 107.8 | 117.4 | 94.1 | 108.9 | 89.1 | 119.6
2061 | 1916 | -6.4 | 0 | 0 | 106.2 | 94.3 | 86.7 | 86.9 | 118.5 | 19.6 | 21.3 | 28.4 | 10.1 | 245.1 | 13.7 | 99.4 | 45.3 | 25.2 | 110.4 | 68.9 | 185.8 | 98.9 | 50.8 | 255.1 | 122.3 | 153.7 | 89.8 | 107.7 | 117.3 | 94 | 108.8 | 89 | 119.5
2062 | 1917 | -6.4 | 0 | 0 | 105.8 | 94.3 | 86.8 | 86.8 | 118.4 | 19.6 | 21.3 | 28.3 | 10.6 | 263.9 | 20.5 | 99.3 | 45 | 25.2 | 110.4 | 68.9 | 185.6 | 99 | 50.7 | 254.9 | 122.2 | 153.5 | 89.8 | 107.6 | 117.1 | 93.9 | 108.7 | 88.9 | 119.4
2063 | 1918 | -6.4 | 0 | 0 | 105.6 | 94.2 | 86.8 | 86.7 | 118.3 | 19.6 | 21.3 | 28.2 | 9.2 | 269.7 | 22.9 | 99.3 | 45 | 25.2 | 110.1 | 68.8 | 185.4 | 99.3 | 50.5 | 254.5 | 122.1 | 153.4 | 89.7 | 107.5 | 117.1 | 93.9 | 108.6 | 88.8 | 119.4
2064 | 1919 | -6.5 | 0 | 0 | 105.6 | 94.2 | 86.8 | 86.6 | 118.2 | 19.6 | 21.3 | 28.1 | 8.1 | 244.9 | 22.3 | 99.3 | 44.9 | 25.1 | 110 | 68.7 | 185.2 | 99.4 | 50.4 | 254.3 | 121.9 | 153.3 | 89.6 | 107.4 | 117 | 93.8 | 108.4 | 88.8 | 119.3
2065 | 1920 | -6.5 | 0 | 0 | 105.9 | 94.1 | 86.8 | 86.5 | 118.1 | 19.7 | 21.3 | 28.1 | 8.1 | 241.7 | 17.4 | 99.2 | 44.8 | 25 | 109.8 | 68.7 | 185.1 | 99.7 | 50.2 | 254.1 | 121.6 | 153.1 | 89.5 | 107.4 | 116.9 | 93.7 | 108.3 | 88.8 | 119.1
2066 | 1921 | -6.4 | 0 | 0 | 105.9 | 94 | 86.8 | 86.5 | 118 | 19.7 | 21.3 | 28.1 | 8.9 | 249.1 | 17 | 99.2 | 44.9 | 25 | 109.7 | 68.6 | 184.9 | 99.6 | 50.2 | 253.8 | 121.6 | 153 | 89.4 | 107.3 | 116.7 | 93.6 | 108.3 | 88.7 | 119
2067 | 1922 | -6.4 | 0 | 0 | 105.8 | 94 | 86.7 | 86.5 | 117.8 | 19.6 | 21.3 | 28 | 8.8 | 247.3 | 20.3 | 99.2 | 45 | 25 | 109.7 | 68.5 | 184.8 | 99.4 | 50.2 | 253.5 | 121.5 | 152.9 | 89.3 | 107.2 | 116.6 | 93.6 | 108.2 | 88.5 | 118.9
2068 | 1923 | -6.4 | 0 | 0 | 105.6 | 94 | 86.6 | 86.5 | 117.7 | 19.7 | 21.3 | 27.9 | 8.7 | 251.6 | 18.9 | 99.2 | 45.3 | 24.9 | 109.5 | 68.5 | 184.6 | 99 | 50.1 | 253.1 | 121.3 | 152.8 | 89.3 | 107.2 | 116.5 | 93.5 | 108.1 | 88.3 | 118.8
2069 | 1924 | -6.5 | 0 | 0 | 105.2 | 93.9 | 86.5 | 86.4 | 117.6 | 19.7 | 21.3 | 27.8 | 11.2 | 241.9 | 17.2 | 99.2 | 45.4 | 24.9 | 109.4 | 68.4 | 184.4 | 98.9 | 50 | 252.6 | 121.1 | 152.6 | 89.3 | 107.1 | 116.5 | 93.4 | 108 | 88.3 | 118.8
2070 | 1925 | -6.5 | 0 | 0 | 104.9 | 93.9 | 86.6 | 86.2 | 117.6 | 19.7 | 21.3 | 27.7 | 12.3 | 239 | 17.9 | 99.1 | 45.5 | 24.9 | 109.3 | 68.3 | 184.2 | 99 | 49.9 | 252.2 | 121 | 152.5 | 89.4 | 107.1 | 116.4 | 93.3 | 107.9 | 88.3 | 118.7
2071 | 1926 | -6.5 | 0 | 0 | 104.6 | 94 | 86.6 | 86.1 | 117.6 | 19.7 | 21.3 | 27.6 | 9.2 | 240.2 | 16.7 | 99 | 45.3 | 24.9 | 109.3 | 68.2 | 184 | 98.8 | 49.8 | 251.9 | 120.9 | 152.4 | 89.3 | 106.9 | 116.3 | 93.3 | 107.9 | 88.3 | 118.6
2072 | 1927 | -6.5 | 0 | 0 | 104.3 | 94 | 86.5 | 86 | 117.6 | 19.8 | 21.3 | 27.5 | 10.1 | 256 | 14.9 | 98.9 | 45.3 | 24.9 | 109.1 | 68.1 | 183.8 | 98.7 | 49.8 | 251.5 | 120.6 | 152.3 | 89.2 | 106.8 | 116.2 | 93.2 | 107.8 | 88.2 | 118.5
2073 | 1928 | -6.4 | 0 | 0 | 104 | 94 | 86.5 | 86 | 117.4 | 19.8 | 21.3 | 27.6 | 11 | 268 | 13.3 | 98.8 | 45.3 | 24.8 | 108.8 | 68 | 183.6 | 98.6 | 49.7 | 251.4 | 120.4 | 152.1 | 89.1 | 106.6 | 116.1 | 93.1 | 107.7 | 88.1 | 118.4
2074 | 1929 | -6.4 | 0 | 0 | 104 | 94 | 86.4 | 86.1 | 117.3 | 19.8 | 21.3 | 27.5 | 14.5 | 237 | 15.5 | 98.7 | 45.1 | 24.8 | 108.6 | 67.9 | 183.4 | 98.4 | 49.7 | 251.2 | 120.3 | 152 | 89.1 | 106.5 | 116.1 | 93 | 107.6 | 88.1 | 118.3
2075 | 1930 | -6.5 | 0 | 0 | 103.9 | 93.9 | 86.3 | 86 | 117.1 | 19.8 | 21.3 | 27.5 | 15.5 | 239.9 | 17.9 | 98.6 | 45 | 24.7 | 108.4 | 67.8 | 183.2 | 98.2 | 49.8 | 250.9 | 120.1 | 151.9 | 89.2 | 106.5 | 116 | 92.9 | 107.4 | 88.1 | 118.1
2076 | 1931 | -6.4 | 0 | 0 | 103.9 | 93.7 | 86.3 | 85.9 | 117.1 | 19.8 | 21.3 | 27.3 | 12.2 | 244.4 | 15.2 | 98.4 | 45 | 24.7 | 108.1 | 67.7 | 183 | 98.2 | 49.8 | 250.6 | 119.9 | 151.7 | 89.1 | 106.5 | 115.9 | 92.9 | 107.3 | 88.1 | 118.1
2077 | 1932 | -6.4 | 0 | 0 | 104 | 93.4 | 86.4 | 85.9 | 117 | 19.9 | 21.3 | 27.2 | 12.5 | 247.4 | 16.7 | 98.2 | 45 | 24.7 | 107.9 | 67.7 | 182.8 | 98.1 | 49.8 | 250.5 | 119.7 | 151.6 | 89 | 106.4 | 115.8 | 92.8 | 107.2 | 88 | 118
2078 | 1933 | -6.4 | 0 | 0 | 104 | 93.3 | 86.4 | 85.8 | 116.9 | 20 | 21.3 | 27.1 | 8.8 | 242.8 | 24.9 | 98.1 | 44.7 | 24.7 | 107.7 | 67.5 | 182.6 | 97.8 | 49.8 | 250.4 | 119.5 | 151.5 | 88.9 | 106.3 | 115.6 | 92.7 | 107.1 | 87.9 | 117.9
2079 | 1934 | -6.4 | 0 | 0 | 103.9 | 93.2 | 86.3 | 85.8 | 116.8 | 20.1 | 21.3 | 27.2 | 8.3 | 244.3 | 27.5 | 97.9 | 44.6 | 24.7 | 107.5 | 67.5 | 182.4 | 97.6 | 50 | 250.1 | 119.3 | 151.4 | 88.8 | 106.1 | 115.5 | 92.7 | 107 | 87.9 | 117.8
2080 | 1935 | -6.4 | 0 | 0 | 103.9 | 93 | 86.3 | 85.7 | 116.7 | 20.1 | 21.3 | 27.2 | 6.5 | 259 | 27.1 | 97.9 | 44.5 | 24.7 | 107.3 | 67.4 | 182.1 | 97.4 | 50 | 249.8 | 119.3 | 151.2 | 88.7 | 106 | 115.4 | 92.6 | 106.9 | 87.8 | 117.7
2081 | 1936 | -6.3 | 0 | 0 | 104.1 | 92.8 | 86.2 | 85.6 | 116.7 | 20.1 | 21.3 | 27.2 | 6.5 | 264.6 | 26.8 | 97.8 | 44.5 | 24.7 | 107.2 | 67.3 | 181.9 | 97 | 49.9 | 249.5 | 119 | 151.1 | 88.7 | 106 | 115.3 | 92.5 | 106.9 | 87.7 | 117.7
2082 | 1937 | -6.3 | 0 | 0 | 103.9 | 92.8 | 86.1 | 85.4 | 116.6 | 20.2 | 21.3 | 27.2 | 8.4 | 257.1 | 31.3 | 97.7 | 44.7 | 24.7 | 107 | 67.2 | 181.6 | 96.9 | 49.9 | 249.2 | 118.8 | 151 | 88.7 | 105.9 | 115.2 | 92.4 | 106.8 | 87.6 | 117.6
2083 | 1938 | -6.3 | 0 | 0 | 103.9 | 92.9 | 86 | 85.3 | 116.4 | 20.2 | 21.3 | 27.2 | 10.7 | 288.9 | 28.6 | 97.6 | 44.9 | 24.7 | 106.9 | 67.1 | 181.4 | 96.7 | 49.9 | 248.7 | 118.5 | 150.9 | 88.6 | 105.9 | 115.2 | 92.3 | 106.8 | 87.5 | 117.5
2084 | 1939 | -6.4 | 0 | 0 | 103.9 | 93 | 86 | 85.2 | 116.2 | 20.3 | 21.3 | 27 | 7.6 | 281.6 | 26.6 | 97.5 | 44.9 | 24.7 | 106.8 | 67 | 181.1 | 96.7 | 49.8 | 248.1 | 118.3 | 150.7 | 88.5 | 105.8 | 115.2 | 92.2 | 106.6 | 87.6 | 117.4
2085 | 1940 | -6.4 | 0 | 0 | 103.9 | 92.8 | 86.1 | 85.1 | 116.1 | 20.3 | 21.3 | 26.9 | 7.3 | 249 | 25.2 | 97.3 | 44.9 | 24.7 | 106.6 | 66.9 | 180.8 | 96.5 | 49.8 | 247.8 | 118.2 | 150.6 | 88.5 | 105.8 | 115.1 | 92.2 | 106.5 | 87.5 | 117.3
2086 | 1941 | -6.4 | 0 | 0 | 103.8 | 92.6 | 86.1 | 85.1 | 115.9 | 20.4 | 21.3 | 26.8 | 10.2 | 255.7 | 21.6 | 97.1 | 44.9 | 24.7 | 106.4 | 66.8 | 180.5 | 96.1 | 49.9 | 247.6 | 118.1 | 150.5 | 88.5 | 105.8 | 115 | 92.1 | 106.4 | 87.5 | 117.2
2087 | 1942 | -6.4 | 0 | 0 | 103.8 | 92.4 | 85.8 | 85.1 | 115.7 | 20.4 | 21.3 | 26.7 | 13.6 | 259 | 18.3 | 96.9 | 44.8 | 24.7 | 106.2 | 66.7 | 180.2 | 95.9 | 50.2 | 247.4 | 118.1 | 150.4 | 88.4 | 105.7 | 114.9 | 92 | 106.4 | 87.4 | 117.1
2088 | 1943 | -6.5 | 0 | 0 | 103.6 | 92.3 | 85.5 | 85.2 | 115.7 | 20.5 | 21.3 | 26.8 | 15.1 | 256.7 | 19.6 | 96.7 | 44.7 | 24.7 | 105.9 | 66.6 | 179.9 | 96 | 50.2 | 247 | 118.1 | 150.2 | 88.3 | 105.7 | 114.8 | 92 | 106.3 | 87.5 | 117
2089 | 1944 | -6.6 | 0 | 0 | 103.3 | 92.4 | 85.4 | 85.3 | 115.7 | 20.5 | 21.3 | 26.8 | 14 | 257.2 | 25.3 | 96.6 | 44.5 | 24.7 | 105.8 | 66.5 | 179.6 | 96.1 | 50.1 | 246.7 | 118.1 | 150.1 | 88.2 | 105.5 | 114.6 | 91.9 | 106.2 | 87.4 | 116.9
2090 | 1945 | -6.4 | 0 | 0 | 103.1 | 92.5 | 85.4 | 85.3 | 115.5 | 20.6 | 21.3 | 26.8 | 13.5 | 254.6 | 24.8 | 96.5 | 44.4 | 24.7 | 105.8 | 66.4 | 179.3 | 95.9 | 49.9 | 246.4 | 118.1 | 150 | 88.1 | 105.2 | 114.5 | 91.8 | 106.2 | 87.3 | 116.8
2091 | 1946 | -6.3 | 0 | 0 | 102.8 | 92.5 | 85.3 | 85.2 | 115.4 | 20.7 | 21.3 | 26.7 | 11.4 | 252.5 | 22.4 | 96.5 | 44.4 | 24.7 | 105.7 | 66.3 | 179 | 95.4 | 49.8 | 246.1 | 118 | 149.9 | 88 | 105 | 114.5 | 91.8 | 106.1 | 87.3 | 116.7
2092 | 1947 | -6.3 | 0 | 0 | 102.5 | 92.4 | 85.2 | 85.1 | 115.2 | 20.6 | 21.3 | 26.7 | 11.5 | 261.4 | 22.3 | 96.4 | 44.3 | 24.8 | 105.5 | 66.2 | 178.7 | 95.3 | 49.9 | 245.7 | 117.9 | 149.7 | 88.1 | 104.9 | 114.5 | 91.7 | 106.1 | 87.3 | 116.7
2093 | 1948 | -6.4 | 0 | 0 | 102.4 | 92.1 | 85 | 85 | 115.2 | 20.6 | 21.3 | 26.7 | 10.9 | 253.7 | 21.6 | 96.3 | 44.4 | 24.8 | 105.4 | 66.2 | 178.5 | 95.1 | 49.8 | 245.5 | 117.8 | 149.6 | 88.2 | 104.8 | 114.4 | 91.7 | 106 | 87.2 | 116.6
2094 | 1949 | -6.4 | 0 | 0 | 102.4 | 91.9 | 84.9 | 85 | 115.1 | 20.6 | 21.3 | 26.7 | 8.1 | 252 | 20.9 | 96.2 | 44.1 | 24.8 | 105.3 | 66.1 | 178.2 | 95.2 | 49.7 | 245.1 | 117.7 | 149.5 | 88.1 | 104.7 | 114.2 | 91.6 | 106 | 87.1 | 116.5
2095 | 1950 | -6.3 | 0 | 0 | 102.5 | 91.8 | 84.9 | 85 | 115.1 | 20.6 | 21.3 | 26.8 | 6.4 | 265.3 | 20.4 | 96.1 | 43.7 | 24.8 | 105.3 | 65.9 | 178 | 95.6 | 49.6 | 244.6 | 117.6 | 149.4 | 88 | 104.7 | 114.2 | 91.5 | 106 | 86.9 | 116.4
2096 | 1951 | -6.3 | 0 | 0 | 102.5 | 91.8 | 85 | 85 | 115 | 20.6 | 21.3 | 26.8 | 8.1 | 268.3 | 22.3 | 96.1 | 43.8 | 24.8 | 105 | 65.8 | 177.8 | 95.8 | 49.3 | 244.3 | 117.4 | 149.3 | 88 | 104.7 | 114.1 | 91.4 | 105.9 | 86.9 | 116.3
2097 | 1952 | -6.3 | 0 | 0 | 102.3 | 91.7 | 84.9 | 84.9 | 114.9 | 20.5 | 21.3 | 26.7 | 8.5 | 270.2 | 20.6 | 96.1 | 43.8 | 24.8 | 105 | 65.7 | 177.5 | 95.9 | 49.2 | 243.8 | 117.2 | 149.1 | 88 | 104.6 | 114 | 91.3 | 105.8 | 86.8 | 116.2
2098 | 1953 | -6.4 | 0 | 0 | 102.1 | 91.6 | 84.9 | 84.8 | 114.9 | 20.4 | 21.3 | 26.6 | 7.4 | 270.6 | 19.5 | 96 | 43.8 | 24.9 | 104.8 | 65.7 | 177.3 | 95.7 | 49.2 | 243.4 | 116.9 | 149 | 87.9 | 104.5 | 114 | 91.3 | 105.8 | 86.7 | 116.1
2099 | 1954 | -6.2 | 0 | 0 | 102.4 | 91.3 | 84.7 | 84.7 | 114.8 | 20.4 | 21.3 | 26.6 | 6.7 | 267.8 | 16.7 | 95.9 | 43.9 | 24.9 | 104.6 | 65.6 | 177.1 | 95.4 | 49.1 | 242.9 | 116.8 | 148.9 | 87.8 | 104.5 | 113.9 | 91.2 | 105.7 | 86.5 | 116
2100 | 1955 | -6.3 | 0 | 0 | 102.3 | 91.3 | 84.5 | 84.5 | 114.8 | 20.4 | 21.3 | 26.6 | 4.6 | 264.3 | 14.6 | 95.7 | 43.9 | 24.9 | 104.4 | 65.6 | 176.8 | 95.4 | 49 | 242.4 | 116.7 | 148.8 | 87.7 | 104.4 | 113.8 | 91.1 | 105.6 | 86.3 | 115.9
2101 | 1956 | -6.2 | 0 | 0 | 102.4 | 91.4 | 84.5 | 84.4 | 114.8 | 20.4 | 21.3 | 26.6 | 4.2 | 263.3 | 14.5 | 95.6 | 44 | 24.8 | 104.2 | 65.5 | 176.6 | 95.4 | 48.7 | 242 | 116.6 | 148.6 | 87.6 | 104.4 | 113.8 | 91 | 105.5 | 86.2 | 115.8
2102 | 1957 | -6.2 | 0 | 0 | 102.5 | 91.6 | 84.5 | 84.4 | 114.7 | 20.4 | 21.3 | 26.6 | 5.1 | 264.2 | 15.7 | 95.5 | 44 | 24.8 | 104 | 65.4 | 176.4 | 95.5 | 48.5 | 241.8 | 116.5 | 148.5 | 87.5 | 104.3 | 113.7 | 91 | 105.3 | 86.2 | 115.7
2103 | 1958 | -6.2 | 0 | 0 | 102.2 | 91.6 | 84.5 | 84.3 | 114.6 | 20.5 | 21.3 | 26.8 | 7.6 | 260.4 | 15 | 95.4 | 43.9 | 24.8 | 103.8 | 65.4 | 176.2 | 95.6 | 48.4 | 241.5 | 116.4 | 148.4 | 87.4 | 104.2 | 113.5 | 90.9 | 105.2 | 86.2 | 115.6
2104 | 1959 | -6.3 | 0 | 0 | 102.1 | 91.6 | 84.4 | 84.1 | 114.5 | 20.6 | 21.3 | 26.8 | 8.5 | 265.2 | 14.3 | 95.3 | 43.9 | 24.8 | 103.6 | 65.3 | 176 | 95.5 | 48.4 | 241.1 | 116.3 | 148.3 | 87.3 | 104 | 113.4 | 90.8 | 105.2 | 86.1 | 115.6
2105 | 1960 | -6.4 | 0 | 0 | 102.3 | 91.5 | 84.3 | 84.1 | 114.4 | 20.6 | 21.3 | 26.8 | 7.1 | 259.5 | 14.2 | 95.1 | 43.9 | 24.8 | 103.3 | 65.1 | 175.8 | 95.6 | 48.6 | 241 | 116.1 | 148.2 | 87.3 | 103.9 | 113.4 | 90.7 | 105.1 | 86.1 | 115.5
2106 | 1961 | -6.4 | 0 | 0 | 102.5 | 91.4 | 84.2 | 84.3 | 114.3 | 20.5 | 21.3 | 26.8 | 7 | 254.9 | 16 | 95 | 44 | 24.9 | 103.3 | 65 | 175.5 | 95.4 | 48.7 | 240.8 | 115.9 | 148 | 87.2 | 103.9 | 113.3 | 90.7 | 105 | 86 | 115.4
2107 | 1962 | -6.6 | 0 | 0 | 102.2 | 91.2 | 84.2 | 84.5 | 114.2 | 20.6 | 21.3 | 26.8 | 8.1 | 253.8 | 15.2 | 94.9 | 44.2 | 24.9 | 103.2 | 65 | 175.4 | 95 | 48.9 | 240.4 | 115.7 | 147.9 | 87.1 | 103.8 | 113.2 | 90.6 | 104.9 | 85.8 | 115.3
2108 | 1963 | -6.6 | 0 | 0 | 101.9 | 90.8 | 84.2 | 84.3 | 114.2 | 20.5 | 21.3 | 26.9 | 8.4 | 250.4 | 14.1 | 94.7 | 44.2 | 24.9 | 102.9 | 64.9 | 175.1 | 94.8 | 49 | 240.1 | 115.6 | 147.8 | 87.1 | 103.8 | 113 | 90.5 | 104.8 | 85.7 | 115.1
2109 | 1964 | -6.5 | 0 | 0 | 101.7 | 90.6 | 84.3 | 84 | 114.1 | 20.4 | 21.3 | 26.9 | 9.7 | 250.8 | 17.4 | 94.5 | 43.8 | 24.9 | 102.6 | 64.8 | 174.9 | 94.7 | 48.8 | 239.7 | 115.4 | 147.7 | 87.1 | 103.7 | 112.9 | 90.4 | 104.7 | 85.6 | 115.1
2110 | 1965 | -6.5 | 0 | 0 | 101.7 | 90.5 | 84.3 | 83.7 | 113.9 | 20.4 | 21.3 | 26.8 | 9.2 | 244.3 | 23.1 | 94.4 | 43.9 | 24.9 | 102.2 | 64.7 | 174.6 | 94.8 | 48.8 | 239.4 | 115.3 | 147.6 | 86.9 | 103.6 | 112.8 | 90.3 | 104.6 | 85.4 | 115
2111 | 1966 | -6.5 | 0 | 0 | 101.6 | 90.6 | 84.3 | 83.5 | 113.9 | 20.4 | 21.3 | 26.8 | 8.6 | 246.4 | 21.4 | 94.3 | 43.9 | 24.8 | 101.9 | 64.6 | 174.4 | 94.8 | 48.9 | 239.1 | 115.2 | 147.4 | 86.8 | 103.5 | 112.8 | 90.3 | 104.4 | 85.4 | 114.9
2112 | 1967 | -6.5 | 0 | 0 | 101.5 | 90.6 | 84.3 | 83.4 | 113.8 | 20.4 | 21.3 | 26.8 | 7.9 | 238.1 | 22.5 | 94.2 | 43.8 | 24.8 | 101.7 | 64.5 | 174.1 | 94.9 | 48.7 | 238.7 | 115.2 | 147.3 | 86.8 | 103.5 | 112.8 | 90.2 | 104.3 | 85.5 | 114.9
2113 | 1968 | -6.4 | 0 | 0 | 101.3 | 90.2 | 84.2 | 83.5 | 113.6 | 20.5 | 21.3 | 26.8 | 8.6 | 243.9 | 22.6 | 94 | 43.9 | 24.8 | 101.5 | 64.5 | 173.9 | 95 | 48.6 | 238.5 | 114.9 | 147.2 | 86.8 | 103.4 | 112.7 | 90.2 | 104.2 | 85.5 | 114.8
2114 | 1969 | -6.4 | 0 | 0 | 101.4 | 90 | 84 | 83.5 | 113.6 | 20.6 | 21.3 | 26.7 | 7.8 | 247.6 | 21.1 | 94 | 44.2 | 24.7 | 101.2 | 64.4 | 173.6 | 95.1 | 48.5 | 238.2 | 115 | 147.1 | 86.7 | 103.3 | 112.5 | 90.1 | 104.1 | 85.5 | 114.7
2115 | 1970 | -6.4 | 0 | 0 | 101.3 | 90.1 | 83.8 | 83.6 | 113.5 | 20.8 | 21.3 | 26.7 | 5.8 | 239 | 20.6 | 93.9 | 44.2 | 24.6 | 100.9 | 64.3 | 173.4 | 95.1 | 48.6 | 237.9 | 114.9 | 147 | 86.6 | 103.2 | 112.4 | 90.1 | 104.1 | 85.5 | 114.6
2116 | 1971 | -6.4 | 0 | 0 | 101.1 | 90.3 | 83.8 | 83.5 | 113.4 | 20.8 | 21.3 | 26.7 | 8.3 | 236.9 | 24.7 | 93.9 | 44.3 | 24.5 | 100.8 | 64.2 | 173.2 | 95 | 48.7 | 237.7 | 114.8 | 146.9 | 86.5 | 103 | 112.3 | 90 | 104 | 85.5 | 114.5
2117 | 1972 | -6.5 | 0 | 0 | 100.8 | 90.3 | 83.7 | 83.4 | 113.3 | 20.8 | 21.3 | 26.7 | 11.7 | 247.5 | 26.3 | 93.8 | 44.1 | 24.5 | 100.8 | 64.2 | 173 | 94.9 | 48.7 | 237.4 | 114.6 | 146.7 | 86.5 | 102.9 | 112.2 | 89.9 | 103.9 | 85.4 | 114.4
2118 | 1973 | -6.4 | 0 | 0 | 100.9 | 90.1 | 83.8 | 83.4 | 113.3 | 20.7 | 21.3 | 26.6 | 11.7 | 259.7 | 20.3 | 93.7 | 44 | 24.4 | 100.6 | 64.1 | 172.8 | 95.1 | 48.7 | 236.9 | 114.4 | 146.6 | 86.4 | 102.7 | 112.1 | 89.8 | 103.8 | 85.2 | 114.3
2119 | 1974 | -6.4 | 0 | 0 | 100.9 | 90 | 83.7 | 83.3 | 113.2 | 20.6 | 21.3 | 26.5 | 15.9 | 245 | 15 | 93.6 | 44.4 | 24.3 | 100.6 | 64 | 172.6 | 95.3 | 48.8 | 236 | 114.3 | 146.5 | 86.4 | 102.6 | 112.1 | 89.7 | 103.8 | 85.1 | 114.2
2120 | 1975 | -6.4 | 0 | 0 | 101 | 90 | 83.5 | 83.2 | 113.2 | 20.6 | 21.3 | 26.4 | 16.7 | 241.2 | 15.9 | 93.6 | 44.8 | 24.4 | 100.6 | 63.9 | 172.4 | 95.6 | 48.7 | 235.6 | 114.1 | 146.4 | 86.4 | 102.5 | 112 | 89.7 | 103.7 | 85.1 | 114.1
2121 | 1976 | -6.4 | 0 | 0 | 101.1 | 90 | 83.4 | 83.1 | 113.1 | 20.5 | 21.3 | 26.4 | 17.3 | 253.6 | 19.8 | 93.4 | 44.9 | 24.4 | 100.5 | 63.9 | 172.2 | 95.6 | 48.6 | 235.1 | 113.9 | 146.3 | 86.4 | 102.5 | 112 | 89.6 | 103.7 | 85 | 114
2122 | 1977 | -6.4 | 0 | 0 | 100.9 | 89.9 | 83.4 | 83 | 113 | 20.5 | 21.3 | 26.4 | 13.8 | 241.2 | 20.6 | 93.1 | 44.9 | 24.5 | 100.5 | 63.8 | 171.9 | 95.7 | 48.4 | 234.7 | 113.7 | 146.2 | 86.3 | 102.5 | 111.9 | 89.5 | 103.7 | 84.9 | 113.9
2123 | 1978 | -6.5 | 0 | 0 | 100.5 | 89.7 | 83.4 | 83 | 112.9 | 20.4 | 21.3 | 26.4 | 10.1 | 242.6 | 27.5 | 92.9 | 44.9 | 24.5 | 100.4 | 63.8 | 171.7 | 95.4 | 48.6 | 234 | 113.4 | 146 | 86.3 | 102.4 | 111.9 | 89.4 | 103.6 | 84.8 | 113.8
2124 | 1979 | -6.5 | 0 | 0 | 100.3 | 89.5 | 83.3 | 83 | 112.8 | 20.4 | 21.3 | 26.4 | 9.5 | 243 | 28 | 92.9 | 45 | 24.5 | 100.3 | 63.7 | 171.4 | 95.1 | 48.6 | 233.4 | 113.3 | 145.9 | 86.2 | 102.3 | 111.8 | 89.4 | 103.4 | 84.6 | 113.7
2125 | 1980 | -6.8 | 0 | 0 | 100.2 | 89.5 | 83.3 | 82.9 | 112.7 | 20.5 | 21.3 | 26.5 | 7.7 | 244.3 | 28.9 | 92.8 | 45 | 24.5 | 100.1 | 63.6 | 171.2 | 94.5 | 48.5 | 233.1 | 113.2 | 145.8 | 86.1 | 102.3 | 111.7 | 89.3 | 103.2 | 84.5 | 113.6
2126 | 1981 | -6.9 | 0 | 0 | 100.2 | 89.5 | 83.3 | 82.6 | 112.6 | 20.6 | 21.3 | 26.5 | 6.9 | 246.4 | 28.7 | 92.7 | 44.9 | 24.5 | 100.1 | 63.6 | 170.9 | 94.3 | 48.3 | 232.7 | 113.1 | 145.7 | 86.1 | 102.3 | 111.7 | 89.2 | 103.1 | 84.4 | 113.6
2127 | 1982 | -6.9 | 0 | 0 | 100 | 89.5 | 83.2 | 82.5 | 112.5 | 20.5 | 21.3 | 26.4 | 6.6 | 250.7 | 27.2 | 92.7 | 45 | 24.6 | 100.1 | 63.6 | 170.6 | 94 | 48.2 | 232.2 | 112.8 | 145.5 | 86.2 | 102.2 | 111.6 | 89.1 | 103.1 | 84.3 | 113.5
2128 | 1983 | -6.8 | 0 | 0 | 99.8 | 89.5 | 83.1 | 82.4 | 112.4 | 20.5 | 21.3 | 26.3 | 6 | 245.6 | 25.2 | 92.6 | 44.4 | 24.6 | 100 | 63.5 | 170.3 | 93.8 | 48.1 | 231.6 | 112.7 | 145.4 | 86.2 | 102.2 | 111.4 | 89 | 103 | 84.1 | 113.4
2129 | 1984 | -6.7 | 0 | 0 | 99.7 | 89.2 | 83 | 82.3 | 112.3 | 20.4 | 21.3 | 26.2 | 6.1 | 244.7 | 21 | 92.5 | 44.2 | 24.6 | 100 | 63.5 | 170 | 93.6 | 48.1 | 231.2 | 112.5 | 145.3 | 86 | 102.2 | 111.2 | 89 | 102.9 | 84 | 113.3
2130 | 1985 | -6.5 | 0 | 0 | 99.6 | 88.9 | 83 | 82.2 | 112.2 | 20.4 | 21.3 | 26.1 | 5.4 | 253.7 | 20.1 | 92.4 | 44.3 | 24.5 | 99.9 | 63.4 | 169.7 | 93.4 | 48 | 230.9 | 112.4 | 145.2 | 86 | 102 | 111.1 | 88.9 | 102.9 | 83.9 | 113.2
2131 | 1986 | -6.2 | 0 | 0 | 99.8 | 88.7 | 82.9 | 82.2 | 112.1 | 20.4 | 21.3 | 26.1 | 6.7 | 273.6 | 18.5 | 92.4 | 44.5 | 24.5 | 99.9 | 63.3 | 169.4 | 93.2 | 48 | 230.6 | 112.2 | 145.1 | 86 | 101.8 | 111.1 | 88.8 | 102.8 | 83.8 | 113.1
2132 | 1987 | -6.1 | 0 | 0 | 99.8 | 88.5 | 82.8 | 82.1 | 112 | 20.3 | 21.3 | 26.1 | 9.7 | 263.7 | 17.9 | 92.4 | 44.7 | 24.5 | 99.8 | 63.3 | 169.1 | 93.1 | 47.9 | 229.9 | 112 | 145 | 86.1 | 101.7 | 111.1 | 88.7 | 102.7 | 83.6 | 113.1
2133 | 1988 | -6.4 | 0 | 0 | 99.7 | 88.3 | 82.8 | 82 | 111.8 | 20.4 | 21.3 | 26.2 | 11 | 251.2 | 18.5 | 92.3 | 44.7 | 24.5 | 99.7 | 63.3 | 168.7 | 92.7 | 47.8 | 229.4 | 111.9 | 144.9 | 86 | 101.7 | 111 | 88.6 | 102.6 | 83.5 | 113
2134 | 1989 | -6.3 | 0 | 0 | 99.5 | 88.2 | 82.8 | 81.8 | 111.8 | 20.5 | 21.3 | 26.2 | 13.2 | 252.9 | 17.1 | 92.2 | 44.6 | 24.4 | 99.5 | 63.2 | 168.4 | 92.4 | 47.7 | 228.9 | 111.9 | 144.7 | 85.9 | 101.6 | 110.8 | 88.6 | 102.5 | 83.6 | 112.9
2135 | 1990 | -6.3 | 0 | 0 | 99.4 | 88.1 | 82.7 | 81.7 | 111.7 | 20.5 | 21.3 | 26.3 | 14.1 | 249.4 | 15.7 | 92 | 44.7 | 24.4 | 99.4 | 63.1 | 168.1 | 92.2 | 47.6 | 228.6 | 111.7 | 144.6 | 85.7 | 101.4 | 110.7 | 88.5 | 102.4 | 83.6 | 112.8
2136 | 1991 | -6.4 | 0 | 0 | 99.2 | 88.1 | 82.5 | 81.6 | 111.7 | 20.5 | 21.3 | 26.4 | 11.1 | 246.6 | 19.2 | 91.9 | 44.7 | 24.3 | 99.2 | 63.1 | 167.8 | 92.2 | 47.5 | 228.3 | 111.6 | 144.5 | 85.6 | 101.2 | 110.7 | 88.5 | 102.3 | 83.5 | 112.8
2137 | 1992 | -6.4 | 0 | 0 | 99.1 | 88.2 | 82.3 | 81.7 | 111.7 | 20.5 | 21.3 | 26.5 | 9.4 | 236.9 | 19.4 | 91.6 | 45.1 | 24.3 | 99.1 | 63.1 | 167.4 | 92.2 | 47.4 | 228 | 111.4 | 144.4 | 85.5 | 101.1 | 110.6 | 88.4 | 102.3 | 83.3 | 112.7
2138 | 1993 | -6.4 | 0 | 0 | 99 | 88.1 | 82.3 | 81.8 | 111.6 | 20.5 | 21.4 | 26.6 | 12.6 | 237.5 | 18.8 | 91.4 | 45.1 | 24.3 | 99.1 | 63 | 167.1 | 92.1 | 47.3 | 227.8 | 111.3 | 144.3 | 85.4 | 101.1 | 110.6 | 88.3 | 102.3 | 83.4 | 112.6
2139 | 1994 | -6.3 | 0 | 0 | 99 | 88 | 82.3 | 81.7 | 111.5 | 20.5 | 21.4 | 26.5 | 11.3 | 237.7 | 22.2 | 91.3 | 44.9 | 24.3 | 99.1 | 62.9 | 166.8 | 91.9 | 47.2 | 227.7 | 111.1 | 144.2 | 85.3 | 101 | 110.5 | 88.3 | 102.2 | 83.4 | 112.6
2140 | 1995 | -6.3 | 0 | 0 | 99.1 | 87.9 | 82.3 | 81.6 | 111.5 | 20.4 | 21.3 | 26.5 | 9.6 | 239.4 | 25.1 | 91.3 | 44.6 | 24.3 | 98.9 | 62.9 | 166.5 | 91.8 | 47.2 | 227.5 | 110.9 | 144 | 85.3 | 100.9 | 110.5 | 88.2 | 102.1 | 83.3 | 112.5
2141 | 1996 | -6.4 | 0 | 0 | 99.1 | 87.7 | 82.3 | 81.5 | 111.4 | 20.3 | 21.4 | 26.4 | 9.7 | 242.8 | 21.7 | 91.1 | 44.5 | 24.3 | 98.6 | 62.7 | 166.2 | 91.6 | 47.3 | 227.4 | 110.8 | 143.9 | 85.3 | 100.9 | 110.4 | 88.1 | 102.1 | 83.1 | 112.4
2142 | 1997 | -6.4 | 0 | 0 | 99.3 | 87.6 | 82.3 | 81.4 | 111.4 | 20.3 | 21.4 | 26.4 | 12.4 | 241.5 | 19.9 | 90.9 | 44.4 | 24.3 | 98.4 | 62.7 | 165.9 | 91.8 | 47.3 | 227.2 | 110.8 | 143.8 | 85.2 | 100.9 | 110.3 | 88 | 101.9 | 83 | 112.3
2143 | 1998 | -6.5 | 0 | 0 | 99.3 | 87.5 | 82.1 | 81.3 | 111.3 | 20.3 | 21.4 | 26.3 | 11.6 | 241.8 | 17.1 | 90.6 | 44.2 | 24.3 | 98.3 | 62.6 | 165.6 | 91.7 | 47.5 | 227.1 | 110.7 | 143.7 | 85.1 | 100.8 | 110.2 | 87.9 | 101.8 | 82.9 | 112.2
2144 | 1999 | -6.4 | 0 | 0 | 99.3 | 87.3 | 81.9 | 81.2 | 111.2 | 20.3 | 21.4 | 26.3 | 9 | 253.7 | 17.8 | 90.4 | 44 | 24.3 | 98 | 62.5 | 165.3 | 91.3 | 47.7 | 227 | 110.5 | 143.6 | 85.1 | 100.8 | 110.1 | 87.8 | 101.7 | 82.8 | 112.1
2145 | 2000 | -6.5 | 0 | 0 | 99.3 | 87 | 81.8 | 81.1 | 111.1 | 20.4 | 21.4 | 26.3 | 11.1 | 241.1 | 17.4 | 90.2 | 44 | 24.4 | 98 | 62.5 | 165.1 | 90.9 | 47.8 | 226.8 | 110.4 | 143.5 | 85.1 | 100.7 | 110 | 87.8 | 101.6 | 82.7 | 112
2146 | 2001 | -6.8 | 0 | 0 | 99.2 | 86.8 | 81.7 | 81 | 110.9 | 20.4 | 21.4 | 26.3 | 7.7 | 242.9 | 18.1 | 90 | 44 | 24.4 | 98 | 62.4 | 164.8 | 90.7 | 47.8 | 226.5 | 110.3 | 143.3 | 85.1 | 100.7 | 109.9 | 87.7 | 101.6 | 82.6 | 111.9
2147 | 2002 | -6.8 | 0 | 0 | 99.1 | 86.7 | 81.8 | 80.9 | 110.9 | 20.5 | 21.4 | 26.3 | 6.5 | 232.7 | 19.7 | 89.9 | 44.1 | 24.4 | 97.9 | 62.3 | 164.6 | 90.3 | 47.8 | 226.4 | 110.1 | 143.2 | 85 | 100.6 | 109.8 | 87.6 | 101.5 | 82.5 | 111.8
2148 | 2003 | -6.6 | 0 | 0 | 98.8 | 86.7 | 81.8 | 80.9 | 110.8 | 20.5 | 21.4 | 26.4 | 5.5 | 252.6 | 17.1 | 89.8 | 44.1 | 24.5 | 97.8 | 62.2 | 164.4 | 90 | 47.7 | 226.3 | 109.9 | 143.1 | 84.9 | 100.5 | 109.7 | 87.6 | 101.4 | 82.6 | 111.7
2149 | 2004 | -6.6 | 0 | 0 | 98.5 | 86.7 | 81.8 | 80.8 | 110.7 | 20.6 | 21.4 | 26.4 | 5.6 | 249.7 | 19.5 | 89.6 | 43.9 | 24.5 | 97.7 | 62.1 | 164.1 | 89.8 | 47.6 | 226.2 | 109.8 | 143 | 84.9 | 100.4 | 109.6 | 87.5 | 101.3 | 82.6 | 111.6
2150 | 2005 | -6.4 | 0 | 0 | 98.3 | 86.7 | 81.7 | 80.6 | 110.6 | 20.6 | 21.4 | 26.4 | 6.6 | 245.8 | 22.2 | 89.4 | 43.8 | 24.5 | 97.6 | 62 | 163.9 | 89.3 | 47.5 | 226 | 109.7 | 142.9 | 84.8 | 100.3 | 109.5 | 87.4 | 101.3 | 82.4 | 111.5
2151 | 2006 | -6.4 | 0 | 0 | 98.2 | 86.7 | 81.6 | 80.6 | 110.5 | 20.7 | 21.4 | 26.4 | 10.9 | 249.7 | 21.5 | 89.1 | 43.9 | 24.6 | 97.7 | 62 | 163.6 | 89 | 47.6 | 225.8 | 109.6 | 142.8 | 84.8 | 100.3 | 109.4 | 87.3 | 101.2 | 82.3 | 111.4
2152 | 2007 | -6.6 | 0 | 0 | 98 | 86.7 | 81.6 | 80.5 | 110.4 | 20.7 | 21.4 | 26.4 | 11.7 | 257.4 | 21 | 89 | 43.6 | 24.6 | 97.1 | 61.9 | 163.4 | 88.8 | 47.7 | 225.5 | 109.5 | 142.7 | 84.7 | 100.3 | 109.3 | 87.2 | 101.2 | 82.2 | 111.4
2153 | 2008 | -6.7 | 0 | 0 | 97.9 | 86.6 | 81.5 | 80.4 | 110.4 | 20.7 | 21.4 | 26.3 | 9.6 | 251.5 | 24.3 | 88.9 | 43.2 | 24.6 | 96.6 | 61.8 | 163.2 | 88.5 | 47.9 | 225.3 | 109.3 | 142.5 | 84.6 | 100.2 | 109.2 | 87.2 | 101.1 | 82.3 | 111.3
2154 | 2009 | -6.6 | 0 | 0 | 97.7 | 86.6 | 81.5 | 80.4 | 110.3 | 20.8 | 21.4 | 26.4 | 6.6 | 256.7 | 26.8 | 88.8 | 42.9 | 24.7 | 96.6 | 61.7 | 162.9 | 88.5 | 48 | 225.1 | 109.1 | 142.4 | 84.5 | 100.2 | 109.1 | 87.1 | 101 | 82.2 | 111.2
2155 | 2010 | -6.5 | 0 | 0 | 97.5 | 86.6 | 81.5 | 80.3 | 110.3 | 20.7 | 21.4 | 26.4 | 3.9 | 262.7 | 23.9 | 88.8 | 42.7 | 24.7 | 96.7 | 61.6 | 162.7 | 88.3 | 48 | 224.9 | 109 | 142.3 | 84.4 | 100.1 | 109.1 | 87 | 101 | 82.2 | 111.1
2156 | 2011 | -6.5 | 0 | 0 | 97.4 | 86.6 | 81.2 | 80.2 | 110.1 | 20.7 | 21.4 | 26.4 | 3.7 | 257 | 23.6 | 88.8 | 42.8 | 24.7 | 96.8 | 61.5 | 162.5 | 88.2 | 48.1 | 224.6 | 109 | 142.2 | 84.4 | 100 | 109 | 86.9 | 100.9 | 82.1 | 111
2157 | 2012 | -6.5 | 0 | 0 | 97.6 | 86.5 | 81 | 80.1 | 110 | 20.7 | 21.4 | 26.4 | 4.7 | 254.7 | 18.8 | 88.8 | 42.9 | 24.7 | 96.8 | 61.5 | 162.2 | 88.2 | 47.9 | 224.3 | 108.9 | 142.1 | 84.3 | 99.9 | 108.9 | 86.9 | 100.8 | 82 | 111
2158 | 2013 | -6.5 | 0 | 0 | 97.6 | 86.4 | 80.9 | 80.1 | 109.9 | 20.8 | 21.4 | 26.4 | 5.2 | 269.6 | 15.6 | 88.8 | 42.6 | 24.6 | 96.7 | 61.4 | 161.9 | 88.2 | 47.8 | 223.9 | 108.7 | 142 | 84.2 | 99.8 | 108.8 | 86.8 | 100.8 | 82.1 | 110.9
2159 | 2014 | -6.4 | 0 | 0 | 97.6 | 86.2 | 80.9 | 80 | 109.8 | 20.9 | 21.4 | 26.5 | 6 | 271.1 | 16.4 | 88.8 | 42.6 | 24.5 | 96.4 | 61.3 | 161.7 | 88.2 | 47.6 | 223.7 | 108.6 | 141.8 | 84.1 | 99.7 | 108.7 | 86.7 | 100.7 | 82.1 | 110.8
2160 | 2015 | -6.4 | 0 | 0 | 97.7 | 86 | 80.9 | 79.9 | 109.7 | 20.9 | 21.4 | 26.6 | 9.5 | 252.1 | 15.7 | 88.7 | 42.8 | 24.5 | 95.9 | 61.2 | 161.5 | 88.1 | 47.4 | 223.3 | 108.6 | 141.7 | 84 | 99.6 | 108.7 | 86.7 | 100.7 | 82 | 110.7
2161 | 2016 | -6.4 | 0 | 0 | 97.9 | 85.8 | 80.9 | 79.8 | 109.7 | 20.9 | 21.4 | 26.5 | 10.7 | 277 | 15.2 | 88.5 | 43.1 | 24.5 | 95.4 | 61.1 | 161.3 | 87.8 | 47.1 | 223 | 108.4 | 141.6 | 83.9 | 99.5 | 108.6 | 86.6 | 100.6 | 82 | 110.6
2162 | 2017 | -6.5 | 0 | 0 | 98.1 | 85.7 | 80.9 | 79.8 | 109.6 | 20.9 | 21.4 | 26.5 | 12.1 | 247.9 | 13.5 | 88.3 | 43.3 | 24.5 | 95 | 60.9 | 161.1 | 87.6 | 46.9 | 222.6 | 108.2 | 141.5 | 83.8 | 99.5 | 108.5 | 86.5 | 100.6 | 81.9 | 110.6
2163 | 2018 | -6.5 | 0 | 0 | 98 | 85.7 | 80.8 | 79.7 | 109.6 | 20.9 | 21.4 | 26.4 | 9 | 230.9 | 11.7 | 88.1 | 43.6 | 24.5 | 94.7 | 60.9 | 160.8 | 87.5 | 46.7 | 222.3 | 108.2 | 141.4 | 83.8 | 99.4 | 108.4 | 86.5 | 100.5 | 81.8 | 110.5
2164 | 2019 | -6.5 | 0 | 0 | 97.6 | 85.8 | 80.7 | 79.8 | 109.5 | 20.9 | 21.4 | 26.4 | 8.1 | 229.3 | 11.8 | 88 | 43.4 | 24.5 | 94.7 | 60.8 | 160.6 | 87.2 | 46.6 | 222 | 108 | 141.3 | 83.7 | 99.3 | 108.3 | 86.4 | 100.4 | 82 | 110.4
2165 | 2020 | -6.4 | 0 | 0 | 97.4 | 85.9 | 80.6 | 80 | 109.5 | 20.8 | 21.4 | 26.3 | 10.4 | 245.3 | 14.4 | 87.9 | 43.2 | 24.5 | 94.6 | 60.8 | 160.4 | 87.2 | 46.5 | 221.7 | 107.8 | 141.2 | 83.7 | 99.2 | 108.2 | 86.4 | 100.4 | 81.9 | 110.3
2166 | 2021 | -6.4 | 0 | 0 | 97.1 | 85.8 | 80.6 | 80.1 | 109.5 | 20.9 | 21.4 | 26.3 | 11.6 | 228.9 | 13.4 | 87.8 | 42.7 | 24.4 | 94.5 | 60.7 | 160.1 | 87.2 | 46.3 | 221.1 | 107.7 | 141.1 | 83.6 | 99.1 | 108.1 | 86.3 | 100.3 | 81.8 | 110.2
2167 | 2022 | -6.4 | 0 | 0 | 96.8 | 85.9 | 80.6 | 80.1 | 109.5 | 21 | 21.4 | 26.3 | 11.8 | 244.7 | 17.3 | 87.7 | 42.8 | 24.3 | 94.3 | 60.6 | 159.9 | 87 | 46.3 | 220.8 | 107.6 | 140.9 | 83.4 | 99.1 | 108.1 | 86.2 | 100.3 | 81.7 | 110.1
2168 | 2023 | -6.4 | 0 | 0 | 96.5 | 85.9 | 80.4 | 80.1 | 109.4 | 21 | 21.4 | 26.4 | 11.5 | 248.7 | 21.3 | 87.6 | 42.8 | 24.3 | 94.3 | 60.6 | 159.6 | 87.2 | 46.2 | 220.6 | 107.4 | 140.8 | 83.4 | 99 | 108.1 | 86.2 | 100.2 | 81.6 | 110
2169 | 2024 | -6.4 | 0 | 0 | 96.4 | 85.8 | 80.3 | 80 | 109.3 | 21 | 21.4 | 26.4 | 11.8 | 254.7 | 23.9 | 87.6 | 42.6 | 24.2 | 94.2 | 60.5 | 159.4 | 87.4 | 46.3 | 220.3 | 107.2 | 140.7 | 83.4 | 98.9 | 108 | 86.1 | 100.2 | 81.5 | 109.9
2170 | 2025 | -6.4 | 0 | 0 | 96.5 | 85.7 | 80.2 | 80 | 109.2 | 21 | 21.4 | 26.5 | 14.6 | 229.5 | 22 | 87.3 | 42.3 | 24.2 | 94 | 60.4 | 159.2 | 87.4 | 46.3 | 220.1 | 107.1 | 140.6 | 83.3 | 98.9 | 108 | 86 | 100.1 | 81.4 | 109.9
2171 | 2026 | -6.5 | 0 | 0 | 96.7 | 85.6 | 80.5 | 79.9 | 109.1 | 20.9 | 21.4 | 26.5 | 12.8 | 238.8 | 18.9 | 87 | 42.3 | 24.2 | 93.9 | 60.3 | 159 | 87.4 | 46.2 | 219.8 | 107 | 140.5 | 83.3 | 98.9 | 107.9 | 85.9 | 100 | 81.3 | 109.8
2172 | 2027 | -6.5 | 0 | 0 | 96.8 | 85.6 | 80.7 | 79.7 | 109.1 | 21 | 21.4 | 26.5 | 9.7 | 224.2 | 19 | 86.8 | 42.2 | 24.1 | 93.8 | 60.3 | 158.8 | 87 | 46 | 219.5 | 106.9 | 140.4 | 83.2 | 98.8 | 107.8 | 85.9 | 99.9 | 81.2 | 109.7
2173 | 2028 | -6.5 | 0 | 0 | 96.5 | 85.5 | 80.5 | 79.5 | 109 | 20.9 | 21.4 | 26.5 | 9.7 | 231.2 | 15.4 | 86.6 | 42.3 | 24.2 | 93.9 | 60.2 | 158.6 | 86.8 | 45.9 | 219.2 | 106.9 | 140.3 | 83.1 | 98.8 | 107.7 | 85.8 | 99.8 | 81.1 | 109.6
2174 | 2029 | -6.5 | 0 | 0 | 96.3 | 85.5 | 80.2 | 79.4 | 108.9 | 20.8 | 21.4 | 26.4 | 14.1 | 216.5 | 21.4 | 86.5 | 42.4 | 24.2 | 93.9 | 60.1 | 158.3 | 86.6 | 45.8 | 219 | 106.9 | 140.1 | 83.1 | 98.7 | 107.6 | 85.7 | 99.7 | 80.9 | 109.5
2175 | 2030 | -6.4 | 0 | 0 | 96.3 | 85.5 | 80 | 79.4 | 108.9 | 20.8 | 21.4 | 26.4 | 12.8 | 229.6 | 19.6 | 86.4 | 42.4 | 24.2 | 93.9 | 60.1 | 158.1 | 86.4 | 45.7 | 218.7 | 106.7 | 140 | 83.1 | 98.7 | 107.6 | 85.7 | 99.6 | 80.8 | 109.5
2176 | 2031 | -6.4 | 0 | 0 | 96.4 | 85.4 | 79.9 | 79.4 | 108.7 | 20.8 | 21.4 | 26.3 | 15 | 238.6 | 15.7 | 86.3 | 42.5 | 24.1 | 93.7 | 60 | 157.9 | 86.4 | 45.7 | 218.5 | 106.6 | 139.9 | 83 | 98.7 | 107.4 | 85.6 | 99.6 | 80.7 | 109.4
2177 | 2032 | -6.5 | 0 | 0 | 96.4 | 85.3 | 80 | 79.3 | 108.6 | 20.8 | 21.4 | 26.3 | 15.7 | 220 | 23.5 | 86.3 | 42.5 | 24.1 | 93.6 | 59.9 | 157.7 | 86.3 | 45.7 | 218.3 | 106.4 | 139.8 | 82.9 | 98.6 | 107.4 | 85.5 | 99.5 | 80.6 | 109.3
2178 | 2033 | -6.6 | 0 | 0 | 96.3 | 85.2 | 80 | 79.1 | 108.5 | 20.8 | 21.4 | 26.2 | 13.8 | 242.3 | 22.8 | 86.2 | 42.4 | 24.1 | 93.5 | 59.9 | 157.5 | 86.1 | 45.6 | 218 | 106.2 | 139.7 | 82.9 | 98.6 | 107.3 | 85.4 | 99.4 | 80.6 | 109.2
2179 | 2034 | -6.6 | 0 | 0 | 96.1 | 85.1 | 79.9 | 79.1 | 108.5 | 20.7 | 21.4 | 26.2 | 13.2 | 233.4 | 26 | 86.1 | 42.4 | 24.1 | 93.3 | 59.8 | 157.2 | 86.1 | 45.5 | 217.6 | 106 | 139.6 | 82.8 | 98.5 | 107.2 | 85.4 | 99.4 | 80.5 | 109.1
2180 | 2035 | -6.8 | 0 | 0 | 95.9 | 85.2 | 79.8 | 79.1 | 108.6 | 20.7 | 21.4 | 26.2 | 12.1 | 238.4 | 20.2 | 86 | 42.3 | 24.1 | 93 | 59.7 | 157 | 85.9 | 45.5 | 217.4 | 105.9 | 139.5 | 82.6 | 98.5 | 107.1 | 85.3 | 99.3 | 80.6 | 109.1
2181 | 2036 | -6.9 | 0 | 0 | 95.6 | 85.1 | 79.7 | 79.1 | 108.6 | 20.6 | 21.4 | 26.2 | 10 | 241.4 | 20.3 | 85.9 | 42.1 | 24.1 | 92.9 | 59.7 | 156.8 | 85.9 | 45.3 | 216.9 | 105.8 | 139.4 | 82.5 | 98.4 | 107 | 85.2 | 99.3 | 80.7 | 109
2182 | 2037 | -6.9 | 0 | 0 | 95.4 | 85 | 79.7 | 79.1 | 108.5 | 20.6 | 21.4 | 26.2 | 14 | 234.1 | 22 | 85.9 | 42.1 | 24.1 | 92.7 | 59.6 | 156.6 | 85.7 | 45.2 | 216.3 | 105.6 | 139.2 | 82.4 | 98.3 | 106.9 | 85.2 | 99.2 | 80.7 | 108.9
2183 | 2038 | -6.9 | 0 | 0 | 95.1 | 84.8 | 79.6 | 79.2 | 108.4 | 20.6 | 21.4 | 26.2 | 11.2 | 244 | 20.8 | 85.8 | 42 | 24 | 92.2 | 59.5 | 156.4 | 85.4 | 44.9 | 215.9 | 105.5 | 139.1 | 82.2 | 98.2 | 106.7 | 85.1 | 99.2 | 80.6 | 108.8
2184 | 2039 | -6.9 | 0 | 0 | 94.7 | 84.8 | 79.4 | 79.2 | 108.4 | 20.6 | 21.4 | 26.3 | 9.9 | 242.6 | 27.8 | 85.6 | 42.1 | 24 | 91.8 | 59.4 | 156.1 | 85.3 | 44.7 | 215.7 | 105.3 | 139 | 82.1 | 98 | 106.6 | 85 | 99.1 | 80.5 | 108.8
2185 | 2040 | -6.9 | 0 | 0 | 94.8 | 84.8 | 79.2 | 79 | 108.3 | 20.5 | 21.4 | 26.3 | 12.4 | 241.4 | 30.2 | 85.4 | 42.1 | 23.9 | 91.6 | 59.4 | 155.9 | 85.4 | 44.5 | 215.4 | 105.2 | 138.9 | 82 | 97.9 | 106.6 | 85 | 99.1 | 80.4 | 108.7
2186 | 2041 | -6.9 | 0 | 0 | 95.2 | 84.8 | 79.1 | 78.9 | 108.3 | 20.6 | 21.4 | 26.4 | 6.5 | 241.2 | 28.6 | 85.3 | 42.1 | 23.9 | 91.6 | 59.3 | 155.7 | 85.5 | 44.3 | 215 | 105.1 | 138.8 | 82 | 97.8 | 106.5 | 84.9 | 99.1 | 80.4 | 108.6
2187 | 2042 | -6.8 | 0 | 0 | 95.3 | 84.8 | 79.1 | 78.8 | 108.2 | 20.6 | 21.4 | 26.4 | 5.7 | 227.9 | 28.9 | 85.2 | 42 | 24 | 91.7 | 59.2 | 155.4 | 85.5 | 43.9 | 214.6 | 104.9 | 138.7 | 82 | 97.7 | 106.5 | 84.9 | 99 | 80.5 | 108.5
2188 | 2043 | -6.8 | 0 | 0 | 95.5 | 84.7 | 79.1 | 78.7 | 108.1 | 20.6 | 21.4 | 26.4 | 16.4 | 228.7 | 28.5 | 85.1 | 41.8 | 24 | 91.6 | 59.1 | 155.2 | 85.6 | 43.9 | 214.4 | 104.8 | 138.6 | 81.9 | 97.7 | 106.4 | 84.8 | 99 | 80.5 | 108.4
2189 | 2044 | -6.8 | 0 | 0 | 95.5 | 84.5 | 79.1 | 78.7 | 108 | 20.6 | 21.4 | 26.4 | 19.8 | 223.3 | 24.8 | 85.1 | 41.4 | 24 | 91.6 | 59 | 154.9 | 85.8 | 43.8 | 214.1 | 104.8 | 138.5 | 81.7 | 97.6 | 106.3 | 84.8 | 98.9 | 80.6 | 108.4
2190 | 2045 | -6.8 | 0 | 0 | 95.5 | 84.3 | 79 | 78.7 | 107.9 | 20.5 | 21.4 | 26.4 | 21.2 | 207.9 | 29.7 | 85 | 41.3 | 23.9 | 91.5 | 59 | 154.7 | 85.9 | 43.4 | 213.9 | 104.7 | 138.4 | 81.7 | 97.5 | 106.2 | 84.7 | 98.9 | 80.4 | 108.3
2191 | 2046 | -6.9 | 0 | 0 | 95.6 | 84.2 | 78.8 | 78.6 | 107.8 | 20.5 | 21.4 | 26.2 | 16 | 246.5 | 23.5 | 85 | 41.5 | 23.9 | 91.3 | 58.9 | 154.4 | 86 | 43 | 213.5 | 104.7 | 138.3 | 81.6 | 97.5 | 106.1 | 84.6 | 98.8 | 80.3 | 108.3
2192 | 2047 | -6.8 | 0 | 0 | 95.7 | 84.2 | 78.7 | 78.5 | 107.7 | 20.5 | 21.4 | 26.1 | 24.2 | 250.1 | 36.8 | 85 | 41.6 | 23.9 | 91.1 | 58.8 | 154.2 | 86.3 | 42.7 | 213.2 | 104.7 | 138.2 | 81.6 | 97.4 | 106.1 | 84.6 | 98.7 | 80.2 | 108.2
2193 | 2048 | -6.9 | 0 | 0 | 95.8 | 84.2 | 78.7 | 78.5 | 107.6 | 20.5 | 21.4 | 26.1 | 16.7 | 247.6 | 39.7 | 84.9 | 41.7 | 23.8 | 91 | 58.8 | 153.9 | 86.5 | 42.4 | 212.7 | 104.6 | 138 | 81.6 | 97.4 | 106 | 84.5 | 98.6 | 80.1 | 108.1
2194 | 2049 | -6.5 | 0 | 0 | 95.8 | 84.3 | 78.7 | 78.4 | 107.6 | 20.5 | 21.4 | 26.1 | 10.5 | 250.5 | 31.7 | 84.8 | 41.5 | 23.8 | 90.9 | 58.7 | 153.7 | 86.8 | 42.4 | 212.5 | 104.5 | 137.9 | 81.5 | 97.3 | 106 | 84.4 | 98.5 | 80.1 | 108
2195 | 2050 | -6.6 | 0 | 0 | 95.6 | 84.4 | 78.8 | 78.3 | 107.5 | 20.6 | 21.4 | 26.1 | 6.7 | 251.9 | 25.3 | 84.7 | 41.3 | 23.8 | 90.9 | 58.6 | 153.5 | 87.1 | 42.3 | 212.2 | 104.4 | 137.8 | 81.4 | 97.3 | 105.9 | 84.4 | 98.4 | 80.1 | 107.9
2196 | 2051 | -6.8 | 0 | 0 | 95.4 | 84.2 | 78.8 | 78.3 | 107.4 | 20.6 | 21.4 | 26.2 | 8.5 | 250.1 | 29.4 | 84.6 | 41 | 23.8 | 90.9 | 58.5 | 153.3 | 87.3 | 42.2 | 211.9 | 104.2 | 137.7 | 81.3 | 97.3 | 105.8 | 84.3 | 98.4 | 80 | 107.8
2197 | 2052 | -6.8 | 0 | 0 | 95.1 | 84.1 | 78.7 | 78.2 | 107.3 | 20.5 | 21.4 | 26.2 | 12 | 257.2 | 31.3 | 84.5 | 40.9 | 23.8 | 91 | 58.5 | 153.1 | 87.3 | 42.2 | 211.6 | 104.2 | 137.6 | 81.3 | 97.2 | 105.7 | 84.2 | 98.3 | 79.9 | 107.7
2198 | 2053 | -6.7 | 0 | 0 | 94.8 | 84 | 78.5 | 78.2 | 107.2 | 20.5 | 21.4 | 26.2 | 17 | 255 | 29.1 | 84.4 | 40.9 | 23.8 | 91 | 58.4 | 152.9 | 87.2 | 42.2 | 211.3 | 104.1 | 137.5 | 81.3 | 97.2 | 105.7 | 84.1 | 98.2 | 79.8 | 107.6
2199 | 2054 | -6.5 | 0 | 0 | 94.9 | 83.8 | 78.3 | 78.2 | 107.1 | 20.5 | 21.4 | 26.2 | 13.3 | 250.7 | 25.9 | 84.3 | 40.9 | 23.8 | 91 | 58.3 | 152.7 | 87.3 | 42 | 211.1 | 104 | 137.4 | 81.1 | 97.2 | 105.6 | 84.1 | 98.1 | 79.7 | 107.6
2200 | 2055 | -6.3 | 0 | 0 | 95.1 | 83.6 | 78.2 | 78.1 | 107 | 20.6 | 21.4 | 26.1 | 17.4 | 250.2 | 28.6 | 84.3 | 40.7 | 23.8 | 91.1 | 58.3 | 152.6 | 87.7 | 42.2 | 210.9 | 103.8 | 137.3 | 81 | 97.1 | 105.5 | 84 | 98 | 79.5 | 107.5
2201 | 2056 | -6.4 | 0 | 0 | 95.3 | 83.4 | 78.1 | 77.9 | 106.9 | 20.6 | 21.4 | 26 | 15.6 | 246.1 | 25 | 84.2 | 40.7 | 23.8 | 91.2 | 58.3 | 152.4 | 87.6 | 42.3 | 210.5 | 103.6 | 137.2 | 81 | 97.1 | 105.4 | 83.9 | 97.9 | 79.5 | 107.4
2202 | 2057 | -6.4 | 0 | 0 | 95.2 | 83.2 | 78.2 | 77.8 | 106.9 | 20.5 | 21.4 | 25.9 | 11.9 | 229.8 | 19.5 | 84.2 | 40.8 | 23.8 | 91.2 | 58.2 | 152.3 | 87.2 | 42.3 | 210.2 | 103.4 | 137.1 | 80.9 | 97 | 105.3 | 83.8 | 97.8 | 79.4 | 107.3
2203 | 2058 | -6.5 | 0 | 0 | 94.6 | 83.1 | 78.2 | 77.7 | 106.8 | 20.4 | 21.4 | 25.9 | 8.6 | 245.3 | 22.4 | 84.2 | 40.8 | 23.8 | 91.2 | 58.2 | 152.1 | 87 | 42.3 | 209.7 | 103.3 | 137 | 80.8 | 97 | 105.2 | 83.8 | 97.7 | 79.3 | 107.2
2204 | 2059 | -6.5 | 0 | 0 | 94.2 | 83.1 | 78.1 | 77.6 | 106.8 | 20.4 | 21.4 | 25.9 | 9.8 | 235 | 29.7 | 84.1 | 40.6 | 23.8 | 91.1 | 58 | 151.9 | 86.9 | 42.3 | 209.1 | 103.1 | 136.8 | 80.8 | 97 | 105.1 | 83.7 | 97.6 | 79.2 | 107.1
2205 | 2060 | -6.5 | 0 | 0 | 93.9 | 83.2 | 77.9 | 77.5 | 106.8 | 20.5 | 21.4 | 25.9 | 13.4 | 229.1 | 28.1 | 83.9 | 40.6 | 23.7 | 91 | 58.1 | 151.7 | 86.8 | 42.3 | 208.5 | 103 | 136.7 | 80.8 | 96.9 | 105 | 83.7 | 97.5 | 79.2 | 107
2206 | 2061 | -6.5 | 0 | 0 | 93.8 | 83.2 | 77.8 | 77.4 | 106.8 | 20.5 | 21.4 | 26 | 12.4 | 237.9 | 24.3 | 83.6 | 40.5 | 23.7 | 91 | 58 | 151.5 | 86.4 | 42.2 | 208.2 | 102.9 | 136.6 | 80.8 | 96.9 | 104.9 | 83.6 | 97.4 | 79.1 | 106.9
2207 | 2062 | -6.5 | 0 | 0 | 93.7 | 83.1 | 77.9 | 77.3 | 106.6 | 20.6 | 21.4 | 26 | 14.4 | 234.5 | 24 | 83.4 | 40.5 | 23.7 | 91 | 58 | 151.4 | 86.2 | 42.2 | 207.9 | 102.8 | 136.5 | 80.6 | 96.8 | 104.7 | 83.5 | 97.3 | 79 | 106.9
2208 | 2063 | -6.5 | 0 | 0 | 93.6 | 82.9 | 77.9 | 77.3 | 106.5 | 20.5 | 21.4 | 25.9 | 12.9 | 236.2 | 25.7 | 83.1 | 40.4 | 23.7 | 91 | 58 | 151.2 | 86.2 | 42.3 | 207.4 | 102.7 | 136.4 | 80.5 | 96.6 | 104.7 | 83.4 | 97.2 | 78.8 | 106.8
2209 | 2064 | -6.5 | 0 | 0 | 93.5 | 82.9 | 77.9 | 77.3 | 106.4 | 20.6 | 21.4 | 25.8 | 7.1 | 241.4 | 26.2 | 83 | 40.3 | 23.7 | 90.9 | 57.9 | 151 | 86.1 | 42.4 | 206.9 | 102.6 | 136.3 | 80.5 | 96.5 | 104.7 | 83.4 | 97.2 | 78.7 | 106.7
2210 | 2065 | -6.6 | 0 | 0 | 93.7 | 82.9 | 77.9 | 77.2 | 106.3 | 20.6 | 21.4 | 25.8 | 9 | 232.3 | 28.4 | 83 | 40.2 | 23.7 | 90.9 | 57.9 | 150.8 | 86.2 | 42.4 | 206.7 | 102.6 | 136.2 | 80.5 | 96.3 | 104.6 | 83.3 | 97.2 | 78.7 | 106.7
2211 | 2066 | -6.6 | 0 | 0 | 93.9 | 82.9 | 77.9 | 77 | 106.3 | 20.6 | 21.4 | 25.9 | 10.8 | 234.6 | 24.5 | 83 | 40.2 | 23.7 | 90.8 | 57.8 | 150.6 | 86.3 | 42.4 | 206.5 | 102.5 | 136.1 | 80.4 | 96.2 | 104.5 | 83.2 | 97.1 | 78.6 | 106.6
2212 | 2067 | -6.4 | 0 | 0 | 94 | 82.9 | 77.8 | 76.9 | 106.2 | 20.6 | 21.4 | 25.9 | 12 | 230.3 | 21.8 | 83 | 40.4 | 23.8 | 90.8 | 57.7 | 150.4 | 86.2 | 42.4 | 206.2 | 102.3 | 136 | 80.3 | 96.1 | 104.4 | 83.2 | 97.1 | 78.5 | 106.5
2213 | 2068 | -6.6 | 0 | 0 | 93.9 | 82.9 | 77.8 | 76.9 | 106.1 | 20.6 | 21.4 | 25.7 | 11.4 | 235.3 | 24.2 | 83 | 40.4 | 23.7 | 90.6 | 57.6 | 150.2 | 86.4 | 42.5 | 205.9 | 102.3 | 135.9 | 80.2 | 95.9 | 104.3 | 83.1 | 97 | 78.4 | 106.4
2214 | 2069 | -6.8 | 0 | 0 | 93.9 | 82.8 | 77.8 | 77 | 106 | 20.6 | 21.4 | 25.6 | 9.8 | 230.7 | 25.4 | 82.9 | 40.3 | 23.7 | 90.4 | 57.5 | 150 | 86.6 | 42.5 | 205.6 | 102.2 | 135.8 | 80.3 | 95.8 | 104.3 | 83 | 97 | 78.4 | 106.4
2215 | 2070 | -6.8 | 0 | 0 | 93.8 | 82.6 | 77.7 | 77 | 105.9 | 20.6 | 21.4 | 25.4 | 12 | 241.2 | 27.4 | 82.8 | 40.2 | 23.7 | 90.2 | 57.4 | 149.8 | 86.8 | 42.6 | 205.3 | 102 | 135.7 | 80.3 | 95.7 | 104.2 | 83 | 97 | 78.4 | 106.3
2216 | 2071 | -6.8 | 0 | 0 | 93.8 | 82.5 | 77.6 | 76.8 | 105.8 | 20.7 | 21.4 | 25.3 | 10 | 241.1 | 25.8 | 82.7 | 40.2 | 23.7 | 90.1 | 57.4 | 149.6 | 86.7 | 42.7 | 205 | 102 | 135.6 | 80.2 | 95.6 | 104.1 | 82.9 | 96.9 | 78.3 | 106.2
2217 | 2072 | -6.6 | 0 | 0 | 93.8 | 82.4 | 77.6 | 76.4 | 105.8 | 20.6 | 21.4 | 25.2 | 11 | 242.1 | 23.9 | 82.6 | 40.2 | 23.7 | 89.9 | 57.3 | 149.4 | 86.5 | 42.9 | 204.7 | 102 | 135.5 | 80.2 | 95.6 | 104.1 | 82.8 | 96.8 | 78.1 | 106.2
2218 | 2073 | -6.6 | 0 | 0 | 93.8 | 82.3 | 77.6 | 76.2 | 105.7 | 20.6 | 21.4 | 25.1 | 7.2 | 238.4 | 24.2 | 82.5 | 40.3 | 23.7 | 89.8 | 57.2 | 149.2 | 86.3 | 43.1 | 204.5 | 101.9 | 135.3 | 80.3 | 95.5 | 104.1 | 82.7 | 96.7 | 78 | 106.1
2219 | 2074 | -6.5 | 0 | 0 | 93.7 | 82.3 | 77.6 | 76.1 | 105.6 | 20.6 | 21.4 | 25 | 12.4 | 242.4 | 21.2 | 82.4 | 40.4 | 23.7 | 89.7 | 57.1 | 149 | 86.2 | 43 | 204.1 | 101.8 | 135.2 | 80.2 | 95.5 | 104 | 82.7 | 96.6 | 77.9 | 106
2220 | 2075 | -6.5 | 0 | 0 | 93.7 | 82.1 | 77.6 | 76.1 | 105.5 | 20.5 | 21.4 | 24.9 | 11.2 | 248 | 21.3 | 82.3 | 40.5 | 23.6 | 89.6 | 57.1 | 148.9 | 85.9 | 43 | 203.8 | 101.7 | 135.1 | 80.1 | 95.5 | 103.9 | 82.6 | 96.5 | 77.9 | 105.9
2221 | 2076 | -6.5 | 0 | 0 | 93.5 | 82 | 77.5 | 76 | 105.3 | 20.4 | 21.4 | 24.8 | 14.4 | 255.2 | 19.3 | 82.2 | 40.5 | 23.6 | 89.5 | 57 | 148.7 | 85.9 | 43 | 203.5 | 101.6 | 135 | 80.1 | 95.4 | 103.8 | 82.5 | 96.5 | 77.9 | 105.9
2222 | 2077 | -6.6 | 0 | 0 | 93.3 | 82.1 | 77.4 | 75.9 | 105.3 | 20.4 | 21.4 | 24.6 | 14.7 | 246.1 | 17.5 | 82.1 | 40.4 | 23.5 | 89.3 | 56.9 | 148.5 | 85.8 | 43 | 203.1 | 101.5 | 134.9 | 80 | 95.3 | 103.8 | 82.4 | 96.4 | 77.8 | 105.8
2223 | 2078 | -6.7 | 0 | 0 | 93.3 | 82.1 | 77.3 | 75.9 | 105.2 | 20.4 | 21.4 | 24.7 | 16.5 | 243 | 17.6 | 82 | 40.3 | 23.5 | 89.1 | 56.8 | 148.3 | 85.6 | 43 | 202.8 | 101.4 | 134.8 | 80.1 | 95.3 | 103.7 | 82.4 | 96.4 | 77.7 | 105.7
2224 | 2079 | -6.7 | 0 | 0 | 93.2 | 82.1 | 77.2 | 75.9 | 105.2 | 20.4 | 21.4 | 24.8 | 14.5 | 244.2 | 18 | 81.8 | 40.4 | 23.5 | 88.9 | 56.7 | 148.2 | 85.4 | 43 | 202.5 | 101.3 | 134.7 | 80 | 95.2 | 103.6 | 82.3 | 96.3 | 77.6 | 105.6
2225 | 2080 | -6.6 | 0 | 0 | 93 | 82 | 77.2 | 76 | 105.1 | 20.5 | 21.4 | 24.8 | 13.1 | 251.1 | 22.6 | 81.6 | 40.3 | 23.5 | 88.7 | 56.6 | 148 | 85 | 43.1 | 202.2 | 101.1 | 134.6 | 80 | 95.2 | 103.6 | 82.3 | 96.2 | 77.5 | 105.5
2226 | 2081 | -6.6 | 0 | 0 | 92.7 | 81.9 | 77.3 | 75.9 | 105 | 20.5 | 21.4 | 24.9 | 9.9 | 252.7 | 22.1 | 81.4 | 40.1 | 23.5 | 88.5 | 56.5 | 147.9 | 84.8 | 43.1 | 202 | 100.9 | 134.5 | 79.8 | 95.1 | 103.5 | 82.2 | 96.1 | 77.5 | 105.4
2227 | 2082 | -6.5 | 0 | 0 | 92.3 | 81.8 | 77.2 | 75.6 | 105 | 20.5 | 21.4 | 25 | 9.9 | 255.7 | 20.6 | 81.3 | 39.9 | 23.4 | 88.3 | 56.5 | 147.7 | 84.4 | 43 | 201.4 | 100.8 | 134.4 | 79.7 | 94.9 | 103.3 | 82.1 | 96 | 77.5 | 105.4
2228 | 2083 | -6.5 | 0 | 0 | 92 | 81.7 | 77.1 | 75.4 | 105 | 20.4 | 21.4 | 25 | 8 | 266.9 | 19.1 | 81.2 | 40 | 23.5 | 88.3 | 56.4 | 147.5 | 84 | 42.9 | 200.9 | 100.7 | 134.3 | 79.7 | 94.8 | 103.2 | 82 | 95.9 | 77.5 | 105.3
2229 | 2084 | -6.5 | 0 | 0 | 92.1 | 81.7 | 77 | 75.2 | 104.9 | 20.3 | 21.4 | 25 | 9.6 | 246.4 | 15.1 | 81.1 | 40 | 23.5 | 88.2 | 56.4 | 147.3 | 83.7 | 42.9 | 200.6 | 100.5 | 134.2 | 79.6 | 94.6 | 103.2 | 82 | 95.9 | 77.4 | 105.2
2230 | 2085 | -6.5 | 0 | 0 | 92.3 | 81.7 | 76.8 | 75.3 | 104.9 | 20.4 | 21.4 | 25 | 9.2 | 240 | 15.2 | 81.1 | 40.1 | 23.5 | 88.2 | 56.3 | 147.1 | 83.6 | 42.8 | 200.2 | 100.4 | 134 | 79.5 | 94.6 | 103.2 | 81.9 | 95.8 | 77.4 | 105.1
2231 | 2086 | -6.4 | 0 | 0 | 92.5 | 81.7 | 76.8 | 75.4 | 104.8 | 20.4 | 21.4 | 25 | 7.9 | 260 | 19.4 | 81 | 40.2 | 23.5 | 88.2 | 56.3 | 146.9 | 83.6 | 42.7 | 199.8 | 100.3 | 133.9 | 79.4 | 94.5 | 103.1 | 81.9 | 95.8 | 77.4 | 105.1
2232 | 2087 | -6.4 | 0 | 0 | 92.6 | 81.5 | 76.8 | 75.5 | 104.7 | 20.4 | 21.4 | 24.9 | 5.3 | 248.4 | 22.1 | 81 | 40.1 | 23.5 | 88.1 | 56.2 | 146.7 | 83.7 | 42.7 | 199.5 | 100.3 | 133.8 | 79.3 | 94.5 | 102.9 | 81.8 | 95.7 | 77.4 | 105
2233 | 2088 | -6.2 | 0 | 0 | 92.4 | 81.4 | 76.7 | 75.5 | 104.7 | 20.5 | 21.4 | 24.9 | 6.2 | 245.2 | 18.9 | 81 | 39.8 | 23.5 | 87.9 | 56.1 | 146.5 | 83.4 | 42.6 | 199.4 | 100.2 | 133.7 | 79.2 | 94.5 | 102.8 | 81.8 | 95.6 | 77.3 | 104.9
2234 | 2089 | -6.1 | 0 | 0 | 92.2 | 81.3 | 76.4 | 75.4 | 104.5 | 20.5 | 21.4 | 24.8 | 6.7 | 249.5 | 21.7 | 80.9 | 39.9 | 23.5 | 87.7 | 56.1 | 146.3 | 83.2 | 42.5 | 199.1 | 100.2 | 133.6 | 79.1 | 94.4 | 102.8 | 81.7 | 95.5 | 77.2 | 104.9
2235 | 2090 | -6.3 | 0 | 0 | 92.1 | 81.4 | 76.1 | 75.4 | 104.4 | 20.4 | 21.4 | 24.8 | 4.9 | 255.8 | 17.9 | 80.8 | 39.9 | 23.5 | 87.6 | 56 | 146.1 | 83.1 | 42.5 | 198.7 | 100 | 133.5 | 79 | 94.3 | 102.8 | 81.7 | 95.5 | 77.1 | 104.8
2236 | 2091 | -6.3 | 0 | 0 | 92.1 | 81.4 | 76 | 75.5 | 104.2 | 20.4 | 21.4 | 24.9 | 5.6 | 252.5 | 13.6 | 80.7 | 39.8 | 23.5 | 87.4 | 55.9 | 146 | 83 | 42.5 | 198.5 | 99.8 | 133.4 | 79 | 94.3 | 102.7 | 81.6 | 95.4 | 77 | 104.7
2237 | 2092 | -6.3 | 0 | 0 | 92.2 | 81.4 | 76.2 | 75.7 | 104.1 | 20.4 | 21.4 | 25 | 6 | 250.5 | 14.1 | 80.6 | 39.7 | 23.5 | 87.3 | 55.9 | 145.8 | 83 | 42.8 | 198.1 | 99.7 | 133.3 | 78.8 | 94.2 | 102.6 | 81.6 | 95.3 | 77.1 | 104.6
2238 | 2093 | -6.3 | 0 | 0 | 92.3 | 81.2 | 76.4 | 75.5 | 104.1 | 20.4 | 21.4 | 25.1 | 5.6 | 263.3 | 19.1 | 80.5 | 39.7 | 23.6 | 87.1 | 55.8 | 145.6 | 82.7 | 42.9 | 197.7 | 99.5 | 133.2 | 78.7 | 94.1 | 102.5 | 81.5 | 95.2 | 77 | 104.5
2239 | 2094 | -6.3 | 0 | 0 | 92.4 | 81.1 | 76.3 | 75.1 | 104 | 20.5 | 21.4 | 25.2 | 7.9 | 258.6 | 22.1 | 80.3 | 39.6 | 23.6 | 86.9 | 55.8 | 145.4 | 82.8 | 42.9 | 197.4 | 99.4 | 133.1 | 78.7 | 94.1 | 102.4 | 81.5 | 95.2 | 76.9 | 104.4
2240 | 2095 | -6.3 | 0 | 0 | 92.4 | 81 | 76 | 74.9 | 104 | 20.5 | 21.4 | 25.3 | 8.5 | 262.8 | 23.1 | 80.2 | 39.4 | 23.6 | 86.9 | 55.7 | 145.2 | 82.9 | 43 | 197 | 99.4 | 133 | 78.7 | 94 | 102.4 | 81.4 | 95.1 | 76.7 | 104.4
2241 | 2096 | -6.3 | 0 | 0 | 92.3 | 80.9 | 75.8 | 75 | 103.9 | 20.4 | 21.4 | 25.3 | 7.6 | 267.7 | 22.1 | 80.1 | 39.5 | 23.6 | 86.8 | 55.6 | 145 | 82.8 | 43 | 196.5 | 99.4 | 132.9 | 78.7 | 93.9 | 102.3 | 81.3 | 95 | 76.7 | 104.3
2242 | 2097 | -6.4 | 0 | 0 | 92.2 | 81 | 75.8 | 75 | 103.9 | 20.3 | 21.4 | 25.3 | 8 | 239.3 | 19.7 | 80.1 | 39.6 | 23.7 | 86.6 | 55.5 | 144.7 | 82.6 | 42.9 | 196.1 | 99.3 | 132.8 | 78.6 | 93.9 | 102.2 | 81.2 | 94.9 | 76.6 | 104.2
2243.1 | 2098.1 | -6.4 | 0 | 0 | 91.9 | 80.9 | 75.9 | 75 | 103.8 | 20.3 | 21.4 | 25.4 | 7.7 | 243.7 | 19.7 | 79.9 | 39.6 | 23.7 | 86.5 | 55.5 | 144.5 | 82.6 | 42.8 | 195.6 | 99.3 | 132.7 | 78.6 | 93.8 | 102.2 | 81.1 | 94.9 | 76.5 | 104.1
2244.1 | 2099.1 | -6.4 | 0 | 0 | 91.7 | 80.7 | 76.1 | 74.9 | 103.7 | 20.3 | 21.5 | 25.4 | 9.9 | 241 | 22.9 | 79.8 | 39.5 | 23.6 | 86.3 | 55.4 | 144.2 | 82.4 | 42.7 | 195.4 | 99.2 | 132.6 | 78.7 | 93.8 | 102.1 | 81 | 94.8 | 76.4 | 104
2245.1 | 2100.1 | -6.4 | 0 | 0 | 91.6 | 80.7 | 76 | 74.8 | 103.6 | 20.4 | 21.5 | 25.3 | 7.7 | 241.8 | 23.4 | 79.7 | 39.5 | 23.6 | 86.1 | 55.4 | 144 | 82.3 | 42.6 | 195.1 | 99.1 | 132.5 | 78.7 | 93.7 | 102.1 | 81 | 94.7 | 76.3 | 103.9
2246.1 | 2101.1 | -6.5 | 0 | 0 | 91.6 | 80.7 | 75.9 | 74.7 | 103.5 | 20.5 | 21.5 | 25.3 | 7.9 | 245.4 | 20.1 | 79.6 | 39.5 | 23.6 | 86 | 55.3 | 143.8 | 82.2 | 42.6 | 194.7 | 99 | 132.4 | 78.8 | 93.7 | 102.1 | 80.9 | 94.6 | 76.3 | 103.8
2247.1 | 2102.1 | -6.5 | 0 | 0 | 91.6 | 80.7 | 75.9 | 74.7 | 103.5 | 20.5 | 21.5 | 25.4 | 8.4 | 240.7 | 19.5 | 79.6 | 39.6 | 23.6 | 85.8 | 55.2 | 143.6 | 82.1 | 42.4 | 194.4 | 99 | 132.3 | 78.7 | 93.7 | 102 | 80.8 | 94.5 | 76.2 | 103.7
2248.1 | 2103.1 | -6.5 | 0 | 0 | 91.8 | 80.7 | 75.9 | 74.7 | 103.4 | 20.6 | 21.4 | 25.4 | 6.9 | 241 | 19.7 | 79.5 | 39.7 | 23.6 | 85.7 | 55.1 | 143.4 | 81.9 | 42.4 | 194 | 98.9 | 132.2 | 78.6 | 93.6 | 101.8 | 80.8 | 94.5 | 76.2 | 103.7
2249.1 | 2104.1 | -6.5 | 0 | 0 | 91.7 | 80.7 | 75.8 | 74.7 | 103.3 | 20.5 | 21.4 | 25.4 | 5.6 | 249.6 | 16.6 | 79.5 | 39.6 | 23.5 | 85.7 | 55.1 | 143.2 | 81.8 | 42.5 | 193.7 | 98.9 | 132.1 | 78.5 | 93.5 | 101.6 | 80.7 | 94.4 | 76.2 | 103.6
2250.1 | 2105.1 | -6.5 | 0 | 0 | 91.5 | 80.6 | 75.5 | 74.8 | 103.3 | 20.5 | 21.5 | 25.3 | 5.8 | 260.1 | 16.5 | 79.5 | 39.1 | 23.5 | 85.2 | 55 | 143 | 81.8 | 42.6 | 193.4 | 99 | 132 | 78.4 | 93.3 | 101.5 | 80.7 | 94.4 | 76.3 | 103.6
2251.1 | 2106.1 | -6.4 | 0 | 0 | 91.3 | 80.5 | 75.3 | 74.8 | 103.2 | 20.4 | 21.5 | 25.3 | 4.8 | 262.7 | 13.8 | 79.4 | 39 | 23.4 | 85.2 | 55 | 142.8 | 81.7 | 42.6 | 193 | 99 | 131.8 | 78.3 | 93.2 | 101.5 | 80.6 | 94.3 | 76.3 | 103.6
2252.1 | 2107.1 | -6.5 | 0 | 0 | 91.2 | 80.5 | 75.1 | 74.8 | 103.2 | 20.4 | 21.4 | 25.3 | 5.6 | 253.3 | 15.9 | 79.3 | 39 | 23.4 | 85.2 | 54.9 | 142.6 | 81.5 | 42.8 | 192.5 | 98.9 | 131.7 | 78.1 | 93.1 | 101.4 | 80.6 | 94.2 | 76.3 | 103.5
2253.1 | 2108.1 | -6.5 | 0 | 0 | 91.5 | 80.4 | 75.1 | 74.8 | 103.1 | 20.4 | 21.5 | 25.4 | 6.1 | 258.1 | 23 | 79.3 | 39 | 23.3 | 85.3 | 54.8 | 142.4 | 81.4 | 42.8 | 192.1 | 98.9 | 131.6 | 78 | 93 | 101.4 | 80.5 | 94.1 | 76.3 | 103.4
2254.1 | 2109.1 | -6.5 | 0 | 0 | 91.8 | 80.2 | 75.1 | 74.7 | 103.1 | 20.4 | 21.5 | 25.4 | 7.8 | 253.8 | 26 | 79.2 | 39.1 | 23.3 | 85.3 | 54.8 | 142.3 | 81.4 | 42.8 | 191.7 | 98.8 | 131.5 | 77.8 | 92.9 | 101.2 | 80.5 | 94.1 | 76.3 | 103.3
2255.1 | 2110.1 | -6.5 | 0 | 0 | 91.7 | 80.1 | 75.1 | 74.7 | 103 | 20.4 | 21.5 | 25.4 | 6.3 | 261.5 | 26.5 | 79.1 | 39.1 | 23.3 | 85.2 | 54.7 | 142.1 | 81.3 | 42.8 | 191.1 | 98.8 | 131.4 | 77.7 | 92.8 | 101 | 80.4 | 94 | 76.2 | 103.2
2256.1 | 2111.1 | -6.5 | 0 | 0 | 91.7 | 80 | 75.2 | 74.6 | 103 | 20.5 | 21.5 | 25.4 | 5.8 | 264.3 | 23.8 | 79 | 39 | 23.3 | 85.2 | 54.7 | 142 | 81.3 | 42.8 | 190.5 | 98.7 | 131.3 | 77.6 | 92.8 | 100.9 | 80.4 | 93.9 | 76.1 | 103.2
2257.1 | 2112.1 | -6.4 | 0 | 0 | 91.4 | 80 | 75.3 | 74.5 | 102.9 | 20.5 | 21.5 | 25.5 | 7.6 | 258.9 | 22.2 | 78.9 | 39.2 | 23.3 | 85.2 | 54.6 | 141.8 | 81.3 | 42.7 | 190 | 98.5 | 131.2 | 77.4 | 92.7 | 100.9 | 80.3 | 93.9 | 76 | 103.1
2258.1 | 2113.1 | -6.5 | 0 | 0 | 91.3 | 80.1 | 75.3 | 74.3 | 102.9 | 20.5 | 21.5 | 25.5 | 9 | 254.3 | 20.3 | 78.8 | 39.3 | 23.3 | 85.2 | 54.6 | 141.7 | 81.2 | 42.7 | 189.7 | 98.4 | 131.1 | 77.4 | 92.6 | 100.9 | 80.2 | 93.8 | 75.9 | 103
2259.1 | 2114.1 | -6.5 | 0 | 0 | 91.2 | 80.1 | 75.3 | 74.2 | 102.8 | 20.4 | 21.4 | 25.6 | 9.3 | 257.2 | 21 | 78.8 | 39.2 | 23.3 | 85.2 | 54.5 | 141.5 | 81.3 | 42.6 | 189.2 | 98.2 | 131 | 77.4 | 92.6 | 100.9 | 80.2 | 93.7 | 75.9 | 103
2260.1 | 2115.1 | -6.5 | 0 | 0 | 91.2 | 80.1 | 75.2 | 74.1 | 102.8 | 20.4 | 21.4 | 25.6 | 6.9 | 249.2 | 23.8 | 78.7 | 39.2 | 23.2 | 85.2 | 54.4 | 141.4 | 81.2 | 42.4 | 188.7 | 98.1 | 130.9 | 77.4 | 92.6 | 100.9 | 80.1 | 93.7 | 75.9 | 102.9
2261.1 | 2116.1 | -6.4 | 0 | 0 | 91.1 | 80.1 | 75.1 | 74.1 | 102.7 | 20.3 | 21.5 | 25.6 | 4.2 | 255.6 | 24.1 | 78.7 | 39.1 | 23.2 | 85.2 | 54.4 | 141.2 | 81.1 | 42.3 | 188.1 | 97.9 | 130.8 | 77.3 | 92.6 | 100.8 | 80.1 | 93.6 | 76 | 102.8
2262.1 | 2117.1 | -6.4 | 0 | 0 | 91.1 | 80 | 75.1 | 74.1 | 102.6 | 20.2 | 21.5 | 25.6 | 5 | 255.9 | 25.4 | 78.6 | 38.9 | 23.2 | 85.1 | 54.4 | 141.1 | 81 | 42.2 | 187.7 | 97.9 | 130.7 | 77.3 | 92.6 | 100.8 | 80 | 93.6 | 75.9 | 102.7
2263.1 | 2118.1 | -6.4 | 0 | 0 | 91.1 | 79.9 | 75.1 | 74.1 | 102.6 | 20.2 | 21.5 | 25.6 | 6 | 257 | 23.9 | 78.6 | 38.7 | 23.2 | 85.1 | 54.4 | 141 | 80.9 | 42.1 | 187.3 | 97.8 | 130.6 | 77.2 | 92.5 | 100.7 | 79.9 | 93.4 | 75.8 | 102.6
2264.1 | 2119.1 | -6.5 | 0 | 0 | 91.2 | 79.8 | 75 | 74 | 102.5 | 20.3 | 21.5 | 25.5 | 8.6 | 256.9 | 23.1 | 78.5 | 38.7 | 23.2 | 85 | 54.4 | 140.8 | 81 | 41.9 | 186.8 | 97.7 | 130.5 | 77.2 | 92.5 | 100.6 | 79.8 | 93.3 | 75.6 | 102.5
2265.1 | 2120.1 | -6.4 | 0 | 0 | 91.1 | 79.7 | 75 | 74 | 102.4 | 20.4 | 21.5 | 25.5 | 13.1 | 264.3 | 22.7 | 78.5 | 38.8 | 23.2 | 84.9 | 54.3 | 140.6 | 80.9 | 41.8 | 186.6 | 97.6 | 130.4 | 77.1 | 92.4 | 100.5 | 79.8 | 93.2 | 75.6 | 102.4
2266.1 | 2121.1 | -6.4 | 0 | 0 | 91 | 79.6 | 74.9 | 74.1 | 102.3 | 20.5 | 21.5 | 25.4 | 10.8 | 257.6 | 22.7 | 78.4 | 38.9 | 23.2 | 84.8 | 54.3 | 140.5 | 80.9 | 41.7 | 186.1 | 97.5 | 130.3 | 77.1 | 92.4 | 100.5 | 79.8 | 93.1 | 75.7 | 102.4
2267.1 | 2122.1 | -6.3 | 0 | 0 | 90.8 | 79.6 | 74.8 | 74.1 | 102.2 | 20.6 | 21.5 | 25.4 | 9.4 | 242.3 | 24.5 | 78.4 | 38.8 | 23.2 | 84.8 | 54.2 | 140.4 | 80.9 | 41.7 | 185.7 | 97.4 | 130.2 | 77.1 | 92.3 | 100.4 | 79.7 | 93 | 75.7 | 102.3
2268.1 | 2123.1 | -6.4 | 0 | 0 | 90.6 | 79.5 | 74.6 | 74.1 | 102.1 | 20.7 | 21.5 | 25.3 | 11 | 245.2 | 24.6 | 78.3 | 38.9 | 23.2 | 84.7 | 54.1 | 140.2 | 80.8 | 41.7 | 185.3 | 97.3 | 130.1 | 77 | 92.3 | 100.2 | 79.7 | 92.9 | 75.7 | 102.1
2269.1 | 2124.1 | -6.5 | 0 | 0 | 90.4 | 79.5 | 74.5 | 73.9 | 102.1 | 20.6 | 21.5 | 25.3 | 9.3 | 254.2 | 22.1 | 78.3 | 38.8 | 23.2 | 84.7 | 54.1 | 140.1 | 80.9 | 41.8 | 184.9 | 97.2 | 130 | 76.9 | 92.2 | 100.1 | 79.6 | 92.9 | 75.7 | 102.1
2270.1 | 2125.1 | -6.5 | 0 | 0 | 90.3 | 79.6 | 74.4 | 73.7 | 102.1 | 20.6 | 21.5 | 25.2 | 9.1 | 259.6 | 24.5 | 78.2 | 38.4 | 23.2 | 84.7 | 54 | 139.9 | 80.8 | 41.8 | 184.5 | 97 | 129.9 | 76.8 | 92 | 100 | 79.6 | 92.9 | 75.6 | 102
2271.1 | 2126.1 | -6.5 | 0 | 0 | 90.4 | 79.7 | 74.4 | 73.6 | 102 | 20.6 | 21.5 | 25.1 | 13.5 | 259.5 | 24.5 | 78.2 | 38.1 | 23.2 | 84.7 | 54 | 139.8 | 81 | 41.7 | 184 | 97 | 129.8 | 76.7 | 91.9 | 100 | 79.5 | 92.8 | 75.5 | 102
2272.1 | 2127.1 | -6.5 | 0 | 0 | 90.5 | 79.8 | 74.4 | 73.6 | 101.9 | 20.5 | 21.5 | 25.1 | 10.4 | 255.3 | 21 | 78.1 | 37.9 | 23.2 | 84.8 | 53.9 | 139.6 | 81.1 | 41.8 | 183.6 | 96.9 | 129.7 | 76.7 | 91.8 | 99.9 | 79.4 | 92.8 | 75.4 | 101.9
2273.1 | 2128.1 | -6.4 | 0 | 0 | 90.6 | 79.7 | 74.4 | 73.6 | 101.9 | 20.5 | 21.5 | 25.1 | 13.2 | 231.7 | 19.2 | 78.1 | 37.7 | 23.2 | 84.6 | 53.9 | 139.5 | 81.3 | 41.8 | 183.1 | 96.7 | 129.6 | 76.8 | 91.8 | 99.8 | 79.4 | 92.7 | 75.3 | 101.9
2274.1 | 2129.1 | -6.4 | 0 | 0 | 90.6 | 79.6 | 74.5 | 73.6 | 101.8 | 20.5 | 21.5 | 25 | 10.5 | 258.2 | 19.6 | 78.1 | 37.5 | 23.2 | 84.7 | 53.9 | 139.3 | 81.1 | 41.7 | 182.7 | 96.6 | 129.5 | 76.7 | 91.7 | 99.8 | 79.3 | 92.7 | 75.2 | 101.8
2275.1 | 2130.1 | -6.3 | 0 | 0 | 90.3 | 79.3 | 74.4 | 73.6 | 101.7 | 20.5 | 21.5 | 25 | 8 | 248.7 | 23.9 | 78.1 | 37.5 | 23.3 | 84.7 | 53.9 | 139.2 | 81 | 41.7 | 182.3 | 96.5 | 129.4 | 76.7 | 91.7 | 99.7 | 79.3 | 92.6 | 75 | 101.7
2276.1 | 2131.1 | -6.2 | 0 | 0 | 90 | 79.1 | 74.3 | 73.5 | 101.6 | 20.4 | 21.5 | 25 | 12.9 | 262.9 | 23.6 | 77.9 | 37.6 | 23.3 | 84.7 | 53.8 | 139.1 | 80.7 | 41.8 | 181.8 | 96.3 | 129.3 | 76.6 | 91.7 | 99.7 | 79.2 | 92.5 | 74.9 | 101.6
2277.1 | 2132.1 | -6.2 | 0 | 0 | 89.8 | 79 | 74.2 | 73.5 | 101.5 | 20.4 | 21.5 | 24.9 | 12.5 | 251.7 | 18.8 | 77.7 | 37.6 | 23.4 | 84.6 | 53.8 | 138.9 | 80.5 | 41.8 | 181.3 | 96.2 | 129.2 | 76.6 | 91.7 | 99.7 | 79.2 | 92.4 | 74.9 | 101.6
2278.1 | 2133.1 | -6.3 | 0 | 0 | 89.7 | 79 | 74.2 | 73.4 | 101.5 | 20.3 | 21.5 | 24.8 | 12 | 240.3 | 19.1 | 77.6 | 37.6 | 23.4 | 84.5 | 53.8 | 138.8 | 80.4 | 41.9 | 180.9 | 96.1 | 129.1 | 76.5 | 91.6 | 99.5 | 79.1 | 92.4 | 74.9 | 101.5
2279.1 | 2134.1 | -6.4 | 0 | 0 | 89.7 | 79 | 74.2 | 73.4 | 101.4 | 20.2 | 21.5 | 24.7 | 13 | 249.2 | 27.7 | 77.4 | 37.7 | 23.4 | 84.4 | 53.7 | 138.6 | 80.3 | 41.9 | 180.5 | 96 | 129 | 76.4 | 91.4 | 99.4 | 79.1 | 92.3 | 74.9 | 101.5
2280.1 | 2135.1 | -6.5 | 0 | 0 | 89.6 | 78.9 | 74.2 | 73.4 | 101.3 | 20.2 | 21.5 | 24.6 | 16 | 256.3 | 30.1 | 77.3 | 37.7 | 23.5 | 84.3 | 53.7 | 138.4 | 80.3 | 41.8 | 180 | 96 | 128.9 | 76.3 | 91.3 | 99.4 | 79 | 92.3 | 74.8 | 101.4
2281.1 | 2136.1 | -6.6 | 0 | 0 | 89.4 | 78.8 | 74.1 | 73.2 | 101.3 | 20.2 | 21.5 | 24.5 | 15.8 | 254 | 28 | 77.2 | 37.9 | 23.5 | 84.3 | 53.7 | 138.3 | 79.9 | 41.9 | 179.5 | 95.8 | 128.8 | 76.2 | 91.2 | 99.3 | 78.9 | 92.2 | 74.7 | 101.3
2282.1 | 2137.1 | -6.5 | 0 | 0 | 89.2 | 78.8 | 74.1 | 73 | 101.2 | 20.2 | 21.5 | 24.4 | 12.3 | 264.1 | 25.2 | 77 | 38 | 23.6 | 84.3 | 53.6 | 138.1 | 79.7 | 41.8 | 179 | 95.6 | 128.7 | 76.2 | 91.2 | 99.3 | 78.8 | 92.1 | 74.6 | 101.2
2283.1 | 2138.1 | -6.4 | 0 | 0 | 89 | 78.7 | 74.1 | 72.8 | 101.1 | 20.3 | 21.5 | 24.2 | 11.3 | 261.6 | 21 | 76.9 | 38.1 | 23.6 | 84.3 | 53.6 | 137.9 | 79.5 | 41.8 | 178.7 | 95.5 | 128.6 | 76.2 | 91.2 | 99.2 | 78.8 | 92 | 74.6 | 101.1
2284.1 | 2139.1 | -6.2 | 0 | 0 | 88.7 | 78.8 | 74 | 72.9 | 101 | 20.3 | 21.5 | 24.2 | 10.1 | 249.3 | 19.7 | 76.8 | 38.2 | 23.6 | 84.3 | 53.5 | 137.7 | 79.4 | 41.8 | 178.3 | 95.5 | 128.5 | 76.1 | 91.1 | 99.1 | 78.7 | 91.9 | 74.6 | 101
2285.1 | 2140.1 | -6.2 | 0 | 0 | 88.7 | 78.8 | 73.9 | 73.2 | 100.8 | 20.2 | 21.5 | 24.1 | 7 | 247.3 | 24.3 | 76.6 | 38.2 | 23.6 | 84.1 | 53.4 | 137.5 | 79.3 | 41.9 | 177.9 | 95.5 | 128.4 | 76.1 | 91.1 | 99 | 78.6 | 91.8 | 74.4 | 100.9
2286.1 | 2141.1 | -6.2 | 0 | 0 | 88.9 | 78.6 | 73.9 | 73.2 | 100.7 | 20.2 | 21.5 | 24.2 | 7.3 | 255.6 | 28.3 | 76.3 | 38.1 | 23.6 | 84.1 | 53.4 | 137.3 | 79.2 | 42 | 177.6 | 95.4 | 128.3 | 76 | 91.1 | 98.9 | 78.5 | 91.7 | 74.4 | 100.8
2287.1 | 2142.1 | -6.3 | 0 | 0 | 88.8 | 78.4 | 74 | 73 | 100.6 | 20.2 | 21.5 | 24.2 | 9.9 | 259.6 | 28.5 | 76.2 | 37.9 | 23.6 | 84.1 | 53.3 | 137 | 79.1 | 42.1 | 177.2 | 95.4 | 128.2 | 75.9 | 91 | 98.9 | 78.5 | 91.6 | 74.4 | 100.8
2288.1 | 2143.1 | -6.4 | 0 | 0 | 88.7 | 78.3 | 74 | 72.9 | 100.5 | 20.2 | 21.5 | 24.3 | 8.7 | 247.5 | 29.6 | 76.1 | 38 | 23.7 | 84.1 | 53.3 | 136.8 | 79.1 | 42.2 | 176.8 | 95.3 | 128.1 | 75.8 | 91 | 98.9 | 78.4 | 91.6 | 74.4 | 100.7
2289.1 | 2144.1 | -6.3 | 0 | 0 | 88.4 | 78.3 | 73.8 | 72.8 | 100.4 | 20.2 | 21.5 | 24.2 | 10.1 | 249.6 | 30.2 | 76.1 | 38 | 23.7 | 84 | 53.3 | 136.6 | 79.1 | 42.3 | 176.5 | 95.3 | 128 | 75.7 | 90.9 | 98.9 | 78.4 | 91.5 | 74.5 | 100.6
2290.1 | 2145.1 | -6.3 | 0 | 0 | 88.3 | 78.5 | 73.6 | 72.8 | 100.4 | 20.3 | 21.5 | 24.2 | 10 | 252 | 29.7 | 76 | 37.9 | 23.7 | 83.9 | 53.3 | 136.4 | 79.1 | 42.3 | 176.1 | 95.2 | 127.9 | 75.6 | 90.7 | 98.7 | 78.3 | 91.5 | 74.3 | 100.6
2291.1 | 2146.1 | -6.4 | 0 | 0 | 88.4 | 78.6 | 73.5 | 73 | 100.3 | 20.2 | 21.5 | 24.3 | 9.7 | 244.7 | 30.8 | 75.9 | 38.1 | 23.8 | 83.9 | 53.2 | 136.2 | 79.2 | 42.3 | 175.8 | 95.1 | 127.8 | 75.5 | 90.6 | 98.5 | 78.3 | 91.5 | 74.3 | 100.5
2292.1 | 2147.1 | -6.4 | 0 | 0 | 88.3 | 78.6 | 73.5 | 73.2 | 100.2 | 20.2 | 21.5 | 24.3 | 9.8 | 250.3 | 29.5 | 75.8 | 38.1 | 23.7 | 84 | 53.2 | 136.1 | 79.3 | 42.1 | 175.2 | 95 | 127.7 | 75.4 | 90.5 | 98.5 | 78.2 | 91.5 | 74.2 | 100.4
2293.1 | 2148.1 | -6.4 | 0 | 0 | 88 | 78.6 | 73.5 | 73.2 | 100.1 | 20.2 | 21.5 | 24.3 | 12.5 | 249.5 | 20.9 | 75.7 | 38.1 | 23.7 | 84 | 53.1 | 135.9 | 79.1 | 42.1 | 174.7 | 94.9 | 127.6 | 75.3 | 90.4 | 98.4 | 78.1 | 91.4 | 74.2 | 100.4
2294.1 | 2149.1 | -6.4 | 0 | 0 | 88 | 78.5 | 73.5 | 73.1 | 100 | 20.2 | 21.5 | 24.3 | 9.9 | 250.8 | 21.9 | 75.7 | 38.2 | 23.7 | 84 | 53.1 | 135.7 | 78.8 | 42 | 174.3 | 94.8 | 127.5 | 75.3 | 90.3 | 98.4 | 78.1 | 91.4 | 74.1 | 100.3
2295.1 | 2150.1 | -6.5 | 0 | 0 | 88.2 | 78.4 | 73.5 | 72.9 | 99.9 | 20.2 | 21.5 | 24.3 | 7.5 | 254 | 22.1 | 75.6 | 38.4 | 23.7 | 84.1 | 53.1 | 135.5 | 78.5 | 42.1 | 173.9 | 94.6 | 127.4 | 75.3 | 90.3 | 98.3 | 78 | 91.3 | 74 | 100.2
2296.1 | 2151.1 | -6.5 | 0 | 0 | 88.4 | 78.2 | 73.4 | 72.8 | 99.8 | 20.2 | 21.5 | 24.3 | 7.4 | 248.1 | 21.7 | 75.6 | 38.4 | 23.7 | 84.1 | 53 | 135.4 | 78.5 | 42 | 173.4 | 94.6 | 127.3 | 75.3 | 90.3 | 98.3 | 78 | 91.2 | 74 | 100.1
2297.1 | 2152.1 | -6.4 | 0 | 0 | 88.4 | 78 | 73.3 | 72.8 | 99.8 | 20.2 | 21.5 | 24.4 | 8.1 | 260.8 | 20.3 | 75.5 | 38.5 | 23.7 | 83.9 | 52.9 | 135.2 | 78.5 | 41.8 | 172.9 | 94.5 | 127.2 | 75.2 | 90.2 | 98.2 | 77.9 | 91.2 | 73.9 | 100.1
2298.1 | 2153.1 | -6.5 | 0 | 0 | 88.2 | 77.7 | 73.2 | 72.7 | 99.7 | 20.1 | 21.5 | 24.5 | 8.1 | 268.1 | 17.4 | 75.5 | 38.7 | 23.7 | 83.7 | 52.8 | 135 | 78.5 | 41.7 | 172.5 | 94.4 | 127.1 | 75.2 | 90 | 98 | 77.9 | 91.1 | 73.8 | 100
2299.1 | 2154.1 | -6.6 | 0 | 0 | 87.8 | 77.5 | 73.2 | 72.6 | 99.7 | 20.1 | 21.5 | 24.6 | 8.3 | 257.5 | 15.4 | 75.6 | 38.7 | 23.6 | 83.5 | 52.8 | 134.8 | 78.4 | 41.5 | 172 | 94.3 | 127 | 75 | 89.9 | 97.9 | 77.8 | 91.1 | 73.7 | 99.9
2300.1 | 2155.1 | -6.5 | 0 | 0 | 87.5 | 77.3 | 73.1 | 72.6 | 99.6 | 20.1 | 21.5 | 24.7 | 7.4 | 257.9 | 15.7 | 75.6 | 38.7 | 23.6 | 83.3 | 52.7 | 134.6 | 78.4 | 41.5 | 171.4 | 94.2 | 126.9 | 75 | 89.7 | 97.8 | 77.8 | 91.1 | 73.7 | 99.9
2301.1 | 2156.1 | -6.3 | 0 | 0 | 87.5 | 77.2 | 73 | 72.7 | 99.6 | 20.1 | 21.5 | 24.8 | 7 | 249.5 | 21 | 75.6 | 38.8 | 23.6 | 82.9 | 52.7 | 134.4 | 78.1 | 41.5 | 170.9 | 94.1 | 126.8 | 75.1 | 89.6 | 97.8 | 77.7 | 91 | 73.7 | 99.8
2302.1 | 2157.1 | -6.1 | 0 | 0 | 87.6 | 77 | 72.9 | 72.6 | 99.6 | 20.1 | 21.5 | 24.8 | 7.9 | 248 | 22.4 | 75.5 | 39 | 23.5 | 82.6 | 52.5 | 134.2 | 78 | 41.5 | 170.3 | 94 | 126.7 | 75.1 | 89.5 | 97.8 | 77.7 | 90.9 | 73.6 | 99.7
2303.1 | 2158.1 | -6.1 | 0 | 0 | 87.7 | 76.8 | 72.9 | 72.4 | 99.5 | 20.1 | 21.5 | 24.8 | 7.1 | 249.6 | 21.9 | 75.5 | 39.2 | 23.5 | 82.5 | 52.5 | 134 | 77.9 | 41.5 | 169.7 | 93.8 | 126.6 | 75.2 | 89.5 | 97.8 | 77.6 | 90.8 | 73.4 | 99.7
2304.1 | 2159.1 | -6.2 | 0 | 0 | 87.7 | 76.8 | 72.8 | 72.3 | 99.4 | 20.2 | 21.5 | 24.8 | 6.8 | 232.8 | 19.5 | 75.4 | 39.3 | 23.5 | 82.3 | 52.4 | 133.8 | 77.6 | 41.4 | 169.2 | 93.6 | 126.5 | 75.2 | 89.4 | 97.7 | 77.5 | 90.6 | 73.3 | 99.6
2305.1 | 2160.1 | -6.1 | 0 | 0 | 87.6 | 77 | 72.8 | 72.3 | 99.3 | 20.1 | 21.5 | 24.8 | 6.7 | 246.5 | 17.4 | 75.4 | 39.3 | 23.4 | 82.1 | 52.4 | 133.6 | 77.2 | 41.1 | 168.7 | 93.5 | 126.4 | 75.1 | 89.4 | 97.6 | 77.4 | 90.5 | 73.3 | 99.5
2306.1 | 2161.1 | -6.2 | 0 | 0 | 87.5 | 77.1 | 72.8 | 72.3 | 99.3 | 20.2 | 21.5 | 24.9 | 4.9 | 249.7 | 17.1 | 75.2 | 39.3 | 23.4 | 82 | 52.3 | 133.4 | 77.1 | 41 | 168.2 | 93.4 | 126.3 | 75 | 89.3 | 97.5 | 77.4 | 90.4 | 73.4 | 99.4
2307.1 | 2162.1 | -6.2 | 0 | 0 | 87.5 | 77.2 | 72.7 | 72.3 | 99.2 | 20.2 | 21.5 | 25 | 3.8 | 228.8 | 14.4 | 75.1 | 39.1 | 23.4 | 82.1 | 52.2 | 133.2 | 76.9 | 40.8 | 167.6 | 93.4 | 126.2 | 74.9 | 89.3 | 97.4 | 77.4 | 90.4 | 73.5 | 99.4
2308.1 | 2163.1 | -6.3 | 0 | 0 | 87.5 | 77.3 | 72.4 | 72.3 | 99.2 | 20.1 | 21.5 | 25.1 | 6.6 | 244.1 | 14.2 | 75.1 | 39.1 | 23.3 | 82.1 | 52.2 | 133 | 77.1 | 40.7 | 167.1 | 93.2 | 126.1 | 74.8 | 89.1 | 97.3 | 77.4 | 90.3 | 73.6 | 99.3
2309.1 | 2164.1 | -6.2 | 0 | 0 | 87.6 | 77.3 | 72.1 | 72.2 | 99.1 | 20 | 21.5 | 25.2 | 7.2 | 237.6 | 17.2 | 75 | 39 | 23.3 | 82 | 52.1 | 132.8 | 76.9 | 40.6 | 166.6 | 93.1 | 126 | 74.8 | 89 | 97.3 | 77.3 | 90.3 | 73.5 | 99.2
2310.1 | 2165.1 | -6.3 | 0 | 0 | 87.3 | 77.3 | 71.9 | 72.2 | 98.9 | 20 | 21.5 | 25.2 | 6.5 | 240.3 | 18.8 | 74.9 | 39 | 23.2 | 81.7 | 52 | 132.6 | 76.7 | 40.4 | 166.2 | 93.1 | 125.9 | 74.7 | 89 | 97.2 | 77.3 | 90.3 | 73.4 | 99.2
2311.1 | 2166.1 | -6.3 | 0 | 0 | 87.1 | 77.3 | 71.9 | 72.1 | 98.8 | 20 | 21.5 | 25.1 | 7.1 | 251 | 18 | 74.9 | 38.9 | 23.2 | 81.2 | 52 | 132.4 | 76.7 | 40.4 | 165.7 | 93 | 125.8 | 74.7 | 88.9 | 97.2 | 77.2 | 90.2 | 73.3 | 99.1
2312.1 | 2167.1 | -6.2 | 0 | 0 | 86.9 | 77.2 | 72 | 72 | 98.8 | 20 | 21.5 | 25.1 | 10.9 | 254.2 | 17 | 74.8 | 38.8 | 23.1 | 80.9 | 51.9 | 132.1 | 76.8 | 40.1 | 165.1 | 92.9 | 125.7 | 74.7 | 88.9 | 97.1 | 77.1 | 90.1 | 73.1 | 99
2313.1 | 2168.1 | -6.2 | 0 | 0 | 86.7 | 77.3 | 72.1 | 71.8 | 98.7 | 20 | 21.5 | 25.1 | 9.3 | 254 | 16.8 | 74.8 | 38.7 | 23.1 | 80.8 | 51.8 | 131.9 | 76.9 | 39.9 | 164.7 | 92.8 | 125.7 | 74.7 | 88.9 | 97 | 77.1 | 90 | 73 | 98.9
2314.1 | 2169.1 | -6.2 | 0 | 0 | 86.6 | 77.2 | 72 | 71.6 | 98.5 | 20.1 | 21.5 | 25 | 7.2 | 253.6 | 14.6 | 74.6 | 38.7 | 23 | 80.7 | 51.8 | 131.7 | 77.1 | 39.9 | 164.2 | 92.7 | 125.6 | 74.6 | 88.9 | 97 | 77 | 89.9 | 72.9 | 98.8
2315.1 | 2170.1 | -6.3 | 0 | 0 | 86.5 | 77.1 | 71.9 | 71.4 | 98.4 | 20.2 | 21.5 | 25 | 6.5 | 241.8 | 14.9 | 74.6 | 38.8 | 23 | 80.5 | 51.7 | 131.5 | 77.4 | 39.7 | 163.8 | 92.6 | 125.5 | 74.5 | 88.9 | 96.9 | 77 | 89.8 | 72.9 | 98.8
2316.1 | 2171.1 | -6.3 | 0 | 0 | 86.6 | 77 | 71.8 | 71.3 | 98.3 | 20.1 | 21.5 | 25 | 7.7 | 242.3 | 15.2 | 74.5 | 38.8 | 23 | 80.3 | 51.7 | 131.3 | 77.5 | 39.5 | 163.3 | 92.5 | 125.4 | 74.5 | 88.9 | 96.9 | 76.9 | 89.8 | 72.9 | 98.7
2317.1 | 2172.1 | -6.4 | 0 | 0 | 86.7 | 76.9 | 71.5 | 71.4 | 98.3 | 20.1 | 21.5 | 25 | 14.2 | 240.9 | 19 | 74.5 | 38.9 | 23 | 80 | 51.6 | 131.1 | 77.5 | 39.4 | 162.8 | 92.4 | 125.3 | 74.4 | 88.8 | 96.9 | 76.9 | 89.7 | 72.9 | 98.6
2318.1 | 2173.1 | -6.4 | 0 | 0 | 86.9 | 76.7 | 71.4 | 71.5 | 98.3 | 20 | 21.5 | 24.9 | 14.5 | 238.9 | 19.2 | 74.3 | 38.8 | 22.9 | 79.8 | 51.5 | 130.9 | 77.4 | 39.1 | 162.3 | 92.4 | 125.2 | 74.4 | 88.8 | 96.8 | 76.8 | 89.7 | 72.9 | 98.6
2319.1 | 2174.1 | -6.4 | 0 | 0 | 86.8 | 76.6 | 71.4 | 71.5 | 98.3 | 20 | 21.5 | 24.8 | 7.3 | 246 | 20 | 74.2 | 38.7 | 22.9 | 79.6 | 51.4 | 130.7 | 77.4 | 38.8 | 162 | 92.3 | 125.1 | 74.3 | 88.7 | 96.6 | 76.7 | 89.6 | 72.8 | 98.5
2320.1 | 2175.1 | -6.6 | 0 | 0 | 86.6 | 76.5 | 71.5 | 71.5 | 98.2 | 19.9 | 21.5 | 24.7 | 11.3 | 237.5 | 25.3 | 74.2 | 38.8 | 22.9 | 79.5 | 51.4 | 130.5 | 77.5 | 38.5 | 161.6 | 92.2 | 125 | 74.2 | 88.6 | 96.5 | 76.6 | 89.5 | 72.6 | 98.4
2321.1 | 2176.1 | -6.9 | 0 | 0 | 86.5 | 76.5 | 71.4 | 71.4 | 98.2 | 19.8 | 21.5 | 24.7 | 18.3 | 249.2 | 24.4 | 74.1 | 38.7 | 22.9 | 79.3 | 51.4 | 130.3 | 77.6 | 38.3 | 161.1 | 92 | 124.9 | 74.2 | 88.5 | 96.5 | 76.6 | 89.4 | 72.5 | 98.4
2322.1 | 2177.1 | -6.9 | 0 | 0 | 86.5 | 76.5 | 71.3 | 71.3 | 98.1 | 19.8 | 21.5 | 24.5 | 17.6 | 246.8 | 29.7 | 74.1 | 38.6 | 22.8 | 79.4 | 51.3 | 130.1 | 77.6 | 38.2 | 160.8 | 92 | 124.8 | 74.1 | 88.4 | 96.5 | 76.5 | 89.3 | 72.4 | 98.3
2323.1 | 2178.1 | -6.8 | 0 | 0 | 86.4 | 76.5 | 71.2 | 71.2 | 98 | 19.7 | 21.5 | 24.3 | 17.5 | 235 | 34.2 | 74 | 38.6 | 22.7 | 79.4 | 51.2 | 130 | 77.8 | 38.1 | 160.3 | 91.9 | 124.7 | 74 | 88.4 | 96.4 | 76.4 | 89.3 | 72.4 | 98.2
2324.1 | 2179.1 | -6.8 | 0 | 0 | 86.3 | 76.5 | 71.2 | 71.2 | 97.9 | 19.7 | 21.5 | 24 | 15.5 | 244.5 | 28.4 | 73.9 | 38.3 | 22.7 | 79.5 | 51.2 | 129.8 | 77.9 | 38.1 | 159.7 | 91.8 | 124.6 | 73.9 | 88.3 | 96.3 | 76.4 | 89.3 | 72.5 | 98.2
2325.1 | 2180.1 | -6.8 | 0 | 0 | 86.2 | 76.5 | 71.2 | 71.1 | 97.8 | 19.7 | 21.5 | 23.8 | 20.2 | 241 | 30.1 | 73.8 | 38.2 | 22.7 | 79.6 | 51.2 | 129.6 | 78.1 | 38.1 | 159.2 | 91.7 | 124.5 | 73.8 | 88.2 | 96.1 | 76.3 | 89.2 | 72.5 | 98.1
2326.1 | 2181.1 | -6.7 | 0 | 0 | 86.2 | 76.5 | 71.1 | 71 | 97.7 | 19.7 | 21.5 | 23.8 | 20.1 | 243 | 33.9 | 73.8 | 38.2 | 22.7 | 79.7 | 51.1 | 129.5 | 78.1 | 38 | 158.7 | 91.6 | 124.4 | 73.7 | 88 | 96.1 | 76.3 | 89.2 | 72.4 | 98
2327.1 | 2182.1 | -6.6 | 0 | 0 | 86.2 | 76.3 | 70.8 | 70.9 | 97.7 | 19.7 | 21.5 | 23.9 | 16.2 | 241.1 | 32.6 | 73.8 | 38.1 | 22.7 | 79.6 | 51 | 129.3 | 78.2 | 38.4 | 158.2 | 91.6 | 124.3 | 73.7 | 87.9 | 96.1 | 76.2 | 89.1 | 72.3 | 98
2328.1 | 2183.1 | -6.6 | 0 | 0 | 86.2 | 76.1 | 70.6 | 70.8 | 97.7 | 19.6 | 21.5 | 23.8 | 11.6 | 242.7 | 33.2 | 73.8 | 37.9 | 22.7 | 79.4 | 51 | 129.1 | 78.4 | 38.6 | 157.7 | 91.5 | 124.2 | 73.7 | 87.9 | 96 | 76.1 | 89 | 72.2 | 97.9
2329.1 | 2184.1 | -6.6 | 0 | 0 | 86.1 | 75.8 | 70.5 | 70.7 | 97.7 | 19.6 | 21.5 | 23.7 | 12.3 | 242.1 | 28.4 | 73.7 | 37.8 | 22.7 | 79.2 | 50.9 | 128.9 | 78.3 | 38.7 | 157 | 91.5 | 124.1 | 73.7 | 87.9 | 96 | 76 | 88.8 | 72 | 97.8
2330.1 | 2185.1 | -6.4 | 0 | 0 | 86 | 75.6 | 70.9 | 70.5 | 97.7 | 19.5 | 21.5 | 23.6 | 9.7 | 236.9 | 28.1 | 73.6 | 37.8 | 22.6 | 78.9 | 50.8 | 128.7 | 78.1 | 38.7 | 156.4 | 91.4 | 124 | 73.6 | 87.8 | 95.9 | 76 | 88.7 | 71.9 | 97.8
2331.1 | 2186.1 | -6.5 | 0 | 0 | 85.8 | 75.3 | 71.2 | 70.4 | 97.6 | 19.5 | 21.5 | 23.5 | 9.6 | 241.7 | 30.1 | 73.5 | 37.8 | 22.6 | 78.7 | 50.8 | 128.5 | 78.1 | 38.8 | 155.7 | 91.2 | 123.9 | 73.5 | 87.7 | 95.8 | 75.9 | 88.6 | 71.8 | 97.7
2332.1 | 2187.1 | -6.6 | 0 | 0 | 85.5 | 75.2 | 71.2 | 70.3 | 97.5 | 19.6 | 21.5 | 23.4 | 13.1 | 263.9 | 24.8 | 73.4 | 37.7 | 22.5 | 78.6 | 50.8 | 128.3 | 78.1 | 38.7 | 155.3 | 91.1 | 123.8 | 73.4 | 87.6 | 95.8 | 75.9 | 88.5 | 71.7 | 97.6
2333.1 | 2188.1 | -6.7 | 0 | 0 | 85.3 | 75.3 | 70.9 | 70.1 | 97.5 | 19.6 | 21.5 | 23.5 | 17.2 | 251 | 18.1 | 73.3 | 37.7 | 22.5 | 78.6 | 50.7 | 128.1 | 77.8 | 38.7 | 154.7 | 91 | 123.7 | 73.5 | 87.6 | 95.8 | 75.8 | 88.4 | 71.6 | 97.5
2334.1 | 2189.1 | -6.8 | 0 | 0 | 85.2 | 75.4 | 70.6 | 70.1 | 97.4 | 19.7 | 21.5 | 23.4 | 19.9 | 255.9 | 19.3 | 73.3 | 37.7 | 22.5 | 78.5 | 50.6 | 127.8 | 77.4 | 38.6 | 154.2 | 90.9 | 123.6 | 73.5 | 87.6 | 95.7 | 75.8 | 88.4 | 71.5 | 97.5
2335.1 | 2190.1 | -6.7 | 0 | 0 | 85.1 | 75.5 | 70.4 | 70 | 97.3 | 19.8 | 21.5 | 23.4 | 25.7 | 241.8 | 23.6 | 73.2 | 37.8 | 22.5 | 78.5 | 50.6 | 127.6 | 77.1 | 38.5 | 153.8 | 90.7 | 123.6 | 73.4 | 87.6 | 95.5 | 75.7 | 88.3 | 71.4 | 97.4
2336.1 | 2191.1 | -6.4 | 0 | 0 | 85.1 | 75.4 | 70.4 | 70 | 97.3 | 19.7 | 21.5 | 23.4 | 16.2 | 248 | 26.5 | 73.1 | 37.7 | 22.5 | 78.3 | 50.6 | 127.4 | 76.6 | 38.4 | 153.3 | 90.7 | 123.5 | 73.3 | 87.5 | 95.4 | 75.6 | 88.3 | 71.2 | 97.3
2337.1 | 2192.1 | -5.9 | 0 | 0 | 85 | 75.3 | 70.5 | 69.9 | 97.2 | 19.7 | 21.5 | 23.4 | 17 | 243.8 | 36.1 | 72.9 | 37.6 | 22.5 | 78 | 50.5 | 127.3 | 76.4 | 38.1 | 152.9 | 90.5 | 123.4 | 73.2 | 87.3 | 95.4 | 75.5 | 88.2 | 71.1 | 97.2
2338.1 | 2193.1 | -5.9 | 0 | 0 | 84.8 | 75.2 | 70.6 | 69.9 | 97.2 | 19.8 | 21.5 | 23.5 | 19.2 | 244.3 | 32 | 72.8 | 37.5 | 22.5 | 77.7 | 50.5 | 127.1 | 76.2 | 37.9 | 152.4 | 90.3 | 123.3 | 73.2 | 87.2 | 95.4 | 75.5 | 88.1 | 71.1 | 97.2
2339.1 | 2194.1 | -6.3 | 0 | 0 | 84.5 | 75.1 | 70.5 | 70 | 97.2 | 19.8 | 21.5 | 23.6 | 16.9 | 243.3 | 35.8 | 72.7 | 37.4 | 22.5 | 77.8 | 50.5 | 126.9 | 76 | 37.8 | 151.9 | 90.3 | 123.2 | 73.1 | 87.2 | 95.3 | 75.4 | 88.1 | 71.1 | 97.1
2340.1 | 2195.1 | -6.4 | 0 | 0 | 84.3 | 75 | 70.5 | 70 | 97.1 | 19.8 | 21.5 | 23.7 | 13.7 | 240 | 39.1 | 72.6 | 37.4 | 22.6 | 78 | 50.4 | 126.7 | 75.8 | 37.7 | 151.4 | 90.2 | 123.1 | 73 | 87.1 | 95.2 | 75.4 | 88 | 71.1 | 97
2341.1 | 2196.1 | -6.5 | 0 | 0 | 84.3 | 74.8 | 70.5 | 69.9 | 97.1 | 19.8 | 21.5 | 23.8 | 10 | 247.9 | 33.1 | 72.5 | 37.5 | 22.6 | 78 | 50.3 | 126.5 | 75.5 | 37.6 | 150.9 | 90.1 | 123 | 72.8 | 87 | 95.1 | 75.3 | 88 | 71.2 | 97
2342.1 | 2197.1 | -6.8 | 0 | 0 | 84.2 | 74.7 | 70.5 | 69.7 | 97 | 19.8 | 21.5 | 23.8 | 12 | 251.1 | 27.7 | 72.4 | 37.5 | 22.6 | 77.9 | 50.3 | 126.3 | 75.3 | 37.6 | 150.4 | 90 | 122.9 | 72.7 | 86.9 | 95 | 75.3 | 88 | 71.2 | 96.9
2343.1 | 2198.1 | -6.8 | 0 | 0 | 84 | 74.7 | 70.4 | 69.6 | 97 | 19.8 | 21.5 | 23.7 | 15.6 | 246.2 | 22.7 | 72.4 | 37.5 | 22.6 | 77.7 | 50.2 | 126.1 | 75.1 | 37.6 | 149.8 | 89.9 | 122.8 | 72.6 | 86.8 | 95 | 75.2 | 87.9 | 71.1 | 96.8
2344.1 | 2199.1 | -6.6 | 0 | 0 | 83.9 | 74.7 | 70.3 | 69.6 | 97 | 19.8 | 21.5 | 23.5 | 14 | 235.5 | 22.8 | 72.4 | 37.5 | 22.5 | 77.5 | 50.2 | 125.8 | 75 | 37.6 | 149.2 | 89.8 | 122.7 | 72.5 | 86.7 | 95 | 75.1 | 87.9 | 70.9 | 96.8
2345.1 | 2200.1 | -6.3 | 0 | 0 | 83.9 | 74.7 | 70.1 | 69.6 | 96.9 | 19.9 | 21.5 | 23.4 | 11.3 | 246.8 | 28.9 | 72.3 | 37.4 | 22.5 | 77.3 | 50.1 | 125.6 | 75 | 37.5 | 148.7 | 89.7 | 122.6 | 72.5 | 86.6 | 94.9 | 75.1 | 87.8 | 70.9 | 96.7
2346.1 | 2201.1 | -6.2 | 0 | 0 | 84 | 74.7 | 70.1 | 69.6 | 96.9 | 19.9 | 21.5 | 23.3 | 8.8 | 247 | 29.3 | 72.3 | 37.5 | 22.5 | 77.3 | 50.1 | 125.3 | 75.1 | 37.2 | 148.2 | 89.5 | 122.5 | 72.5 | 86.6 | 94.9 | 75 | 87.8 | 71 | 96.7
2347.1 | 2202.1 | -6.3 | 0 | 0 | 83.9 | 74.7 | 70.1 | 69.5 | 96.8 | 19.8 | 21.5 | 23.3 | 10.3 | 239.6 | 29.3 | 72.3 | 37.7 | 22.5 | 77.3 | 50.1 | 125.1 | 75 | 36.9 | 147.7 | 89.3 | 122.4 | 72.5 | 86.6 | 94.8 | 75 | 87.7 | 71 | 96.6
2348.1 | 2203.1 | -6.4 | 0 | 0 | 83.9 | 74.7 | 70.2 | 69.4 | 96.7 | 19.8 | 21.5 | 23.4 | 11.9 | 249.8 | 29.5 | 72.3 | 37.7 | 22.5 | 77.3 | 50.1 | 124.8 | 74.9 | 36.8 | 147.2 | 89.3 | 122.4 | 72.4 | 86.5 | 94.7 | 74.9 | 87.7 | 71 | 96.5
2349.1 | 2204.1 | -6.5 | 0 | 0 | 83.8 | 74.5 | 70 | 69.4 | 96.7 | 19.9 | 21.5 | 23.4 | 10.3 | 251.9 | 26.3 | 72.3 | 37.7 | 22.5 | 77.4 | 50 | 124.6 | 74.9 | 36.7 | 146.7 | 89.3 | 122.2 | 72.4 | 86.5 | 94.6 | 74.9 | 87.7 | 70.9 | 96.4
2350.1 | 2205.1 | -6.4 | 0 | 0 | 83.8 | 74.4 | 69.7 | 69.4 | 96.6 | 19.9 | 21.5 | 23.4 | 6.7 | 245.6 | 23 | 72.2 | 37.5 | 22.6 | 77.4 | 49.9 | 124.4 | 74.9 | 36.7 | 146.3 | 89.1 | 122.1 | 72.3 | 86.4 | 94.5 | 74.8 | 87.6 | 70.8 | 96.3
2351.1 | 2206.1 | -6.5 | 0 | 0 | 83.8 | 74.4 | 69.4 | 69.4 | 96.6 | 19.9 | 21.5 | 23.4 | 6.2 | 237.6 | 22.2 | 72 | 37.1 | 22.6 | 77.4 | 49.9 | 124.2 | 75 | 36.7 | 145.8 | 89 | 122.1 | 72.3 | 86.3 | 94.5 | 74.7 | 87.6 | 70.7 | 96.3
2352.1 | 2207.1 | -6.4 | 0 | 0 | 84.1 | 74.3 | 69.3 | 69.3 | 96.5 | 19.9 | 21.5 | 23.6 | 9.2 | 245.6 | 20 | 71.8 | 37 | 22.6 | 77.4 | 49.9 | 123.9 | 75.1 | 36.5 | 145.2 | 88.9 | 122 | 72.2 | 86.3 | 94.5 | 74.7 | 87.5 | 70.6 | 96.2
2353.1 | 2208.1 | -6.2 | 0 | 0 | 84.3 | 74.3 | 69.4 | 69.2 | 96.4 | 19.9 | 21.5 | 23.7 | 10.5 | 258.9 | 21.9 | 71.6 | 37 | 22.5 | 77.4 | 49.8 | 123.7 | 75 | 36.4 | 144.7 | 88.8 | 121.9 | 72.1 | 86.2 | 94.4 | 74.6 | 87.5 | 70.6 | 96.2
2354.1 | 2209.1 | -6 | 0 | 0 | 84.2 | 74.2 | 69.4 | 69.1 | 96.3 | 19.9 | 21.5 | 23.8 | 13.4 | 256.3 | 22 | 71.4 | 37.1 | 22.6 | 77.3 | 49.8 | 123.5 | 74.9 | 36.4 | 144 | 88.7 | 121.8 | 72.1 | 86.2 | 94.2 | 74.6 | 87.4 | 70.6 | 96.1
2355.1 | 2210.1 | -6 | 0 | 0 | 84.1 | 74.2 | 69.3 | 69 | 96.3 | 19.9 | 21.5 | 23.8 | 9.8 | 250.2 | 21.7 | 71.3 | 37.1 | 22.5 | 77.3 | 49.7 | 123.3 | 74.6 | 36.6 | 143.4 | 88.6 | 121.7 | 72 | 86 | 94.1 | 74.5 | 87.4 | 70.6 | 96
2356.1 | 2211.1 | -6.1 | 0 | 0 | 83.9 | 74.2 | 69.2 | 69 | 96.2 | 20 | 21.5 | 23.9 | 9.2 | 252.6 | 21.1 | 71.3 | 37.1 | 22.5 | 77.3 | 49.6 | 123.1 | 74.4 | 36.6 | 142.9 | 88.4 | 121.6 | 72 | 85.9 | 94.1 | 74.5 | 87.4 | 70.5 | 95.9
2357.1 | 2212.1 | -6.2 | 0 | 0 | 83.9 | 74.2 | 69.2 | 69 | 96.2 | 20 | 21.5 | 23.9 | 12.3 | 244.8 | 18.1 | 71.2 | 37.1 | 22.5 | 77.3 | 49.6 | 122.9 | 74.1 | 36.6 | 142.4 | 88.3 | 121.5 | 72.1 | 85.9 | 94.1 | 74.4 | 87.3 | 70.4 | 95.8
2358.1 | 2213.1 | -6.2 | 0 | 0 | 84 | 74.2 | 69.2 | 69 | 96.1 | 19.9 | 21.5 | 23.9 | 14.2 | 247 | 17.9 | 71.1 | 37.1 | 22.6 | 77.2 | 49.5 | 122.7 | 73.9 | 36.6 | 141.9 | 88.2 | 121.4 | 72.3 | 85.9 | 94.1 | 74.3 | 87.2 | 70.3 | 95.8
2359.1 | 2214.1 | -6.3 | 0 | 0 | 83.9 | 74.2 | 69.2 | 68.9 | 96 | 19.9 | 21.5 | 23.9 | 10.8 | 247.9 | 20.5 | 71 | 37 | 22.6 | 77.2 | 49.5 | 122.5 | 73.8 | 36.6 | 141.3 | 88.1 | 121.3 | 72.2 | 85.9 | 94 | 74.3 | 87.1 | 70.1 | 95.7
2360.1 | 2215.1 | -6.4 | 0 | 0 | 83.8 | 74.3 | 69.1 | 68.8 | 95.9 | 19.9 | 21.5 | 23.9 | 12.7 | 245.3 | 27.2 | 70.9 | 37.1 | 22.6 | 77.2 | 49.4 | 122.3 | 73.6 | 36.7 | 140.8 | 88 | 121.2 | 72.1 | 85.9 | 93.8 | 74.2 | 86.9 | 70 | 95.7
2361.1 | 2216.1 | -6.4 | 0 | 0 | 83.7 | 74.3 | 69.1 | 68.7 | 95.8 | 19.9 | 21.5 | 23.9 | 8.6 | 240.8 | 27.5 | 70.8 | 37 | 22.6 | 77.2 | 49.4 | 122.1 | 73.5 | 36.6 | 140.4 | 87.9 | 121.1 | 72 | 85.7 | 93.8 | 74.1 | 86.8 | 70 | 95.6
2362.1 | 2217.1 | -6.5 | 0 | 0 | 83.5 | 74.3 | 69 | 68.7 | 95.7 | 20 | 21.5 | 23.9 | 4.1 | 241.3 | 29.3 | 70.7 | 36.9 | 22.6 | 77.1 | 49.3 | 121.9 | 73.5 | 36.6 | 140 | 87.8 | 121 | 72 | 85.6 | 93.7 | 74.1 | 86.8 | 70.1 | 95.5
2363.1 | 2218.1 | -6.5 | 0 | 0 | 83.6 | 74.2 | 68.8 | 68.7 | 95.7 | 20 | 21.6 | 23.9 | 5.1 | 244.7 | 29.5 | 70.6 | 36.7 | 22.5 | 77 | 49.3 | 121.7 | 73.5 | 36.6 | 139.6 | 87.8 | 120.9 | 71.9 | 85.5 | 93.7 | 74.1 | 86.7 | 70.1 | 95.4
2364.1 | 2219.1 | -6.5 | 0 | 0 | 83.9 | 74.1 | 68.7 | 68.7 | 95.6 | 20 | 21.5 | 23.9 | 8.7 | 250.2 | 26.6 | 70.5 | 36.7 | 22.4 | 76.8 | 49.2 | 121.5 | 73.5 | 36.6 | 139 | 87.7 | 120.8 | 71.8 | 85.5 | 93.6 | 74 | 86.7 | 70 | 95.4
2365.1 | 2220.1 | -6.5 | 0 | 0 | 84.1 | 74 | 68.5 | 68.7 | 95.6 | 20 | 21.6 | 23.8 | 10.6 | 244.9 | 26.3 | 70.2 | 36.6 | 22.4 | 76.7 | 49.1 | 121.3 | 73.6 | 36.8 | 138.5 | 87.7 | 120.8 | 71.6 | 85.4 | 93.6 | 73.9 | 86.6 | 69.9 | 95.3
2366.1 | 2221.1 | -6.6 | 0 | 0 | 84 | 73.8 | 68.5 | 68.7 | 95.6 | 20 | 21.6 | 23.8 | 8.4 | 235.9 | 25.3 | 70 | 36.6 | 22.4 | 76.6 | 49.1 | 121.1 | 73.7 | 37 | 138 | 87.7 | 120.7 | 71.5 | 85.4 | 93.5 | 73.9 | 86.6 | 69.8 | 95.3
2367.1 | 2222.1 | -6.6 | 0 | 0 | 83.8 | 73.6 | 68.6 | 68.6 | 95.6 | 20 | 21.6 | 23.8 | 8.6 | 239.5 | 24.1 | 69.9 | 36.6 | 22.4 | 76.7 | 49.1 | 120.9 | 73.6 | 37.1 | 137.5 | 87.7 | 120.6 | 71.5 | 85.4 | 93.4 | 73.8 | 86.5 | 69.8 | 95.2
2368.1 | 2223.1 | -6.5 | 0 | 0 | 83.6 | 73.4 | 68.6 | 68.5 | 95.6 | 20 | 21.6 | 23.9 | 7.2 | 247.3 | 24.4 | 69.8 | 36.6 | 22.5 | 76.6 | 49.1 | 120.7 | 73.4 | 37.3 | 137.1 | 87.6 | 120.5 | 71.5 | 85.4 | 93.2 | 73.8 | 86.4 | 69.7 | 95.2
2369.1 | 2224.1 | -6.7 | 0 | 0 | 83.4 | 73.2 | 68.6 | 68.4 | 95.6 | 19.9 | 21.6 | 24 | 8.7 | 256.3 | 23.8 | 69.7 | 36.6 | 22.5 | 76.7 | 49.1 | 120.5 | 73.4 | 37.4 | 136.6 | 87.6 | 120.4 | 71.4 | 85.4 | 93.1 | 73.7 | 86.4 | 69.7 | 95.1
2370.1 | 2225.1 | -6.7 | 0 | 0 | 83.3 | 73.2 | 68.6 | 68.2 | 95.6 | 19.9 | 21.5 | 24.1 | 7 | 243.3 | 21.3 | 69.6 | 36.5 | 22.5 | 76.6 | 49 | 120.3 | 73.3 | 37.5 | 136.2 | 87.5 | 120.3 | 71.3 | 85.3 | 93 | 73.7 | 86.4 | 69.5 | 95.1
2371.1 | 2226.1 | -6.7 | 0 | 0 | 83.3 | 73.3 | 68.6 | 68.2 | 95.5 | 19.9 | 21.5 | 24.2 | 6.3 | 238.7 | 20.4 | 69.6 | 36.4 | 22.5 | 76.5 | 49 | 120.1 | 73.2 | 37.5 | 135.7 | 87.5 | 120.2 | 71.2 | 85.2 | 93 | 73.6 | 86.3 | 69.4 | 95
2372.1 | 2227.1 | -6.7 | 0 | 0 | 83.3 | 73.4 | 68.6 | 68.1 | 95.4 | 19.9 | 21.5 | 24.2 | 6.8 | 249.5 | 25 | 69.5 | 36.3 | 22.5 | 76.5 | 48.9 | 119.9 | 73.1 | 37.5 | 135.2 | 87.4 | 120.1 | 71.2 | 85.2 | 93 | 73.5 | 86.2 | 69.3 | 94.9
2373.1 | 2228.1 | -6.6 | 0 | 0 | 83.4 | 73.5 | 68.6 | 68.1 | 95.3 | 19.9 | 21.5 | 24.1 | 6.9 | 256.8 | 23.7 | 69.5 | 36.3 | 22.5 | 76.5 | 48.9 | 119.7 | 72.8 | 37.5 | 134.7 | 87.3 | 120 | 71.1 | 85.2 | 93 | 73.5 | 86.1 | 69.2 | 94.9

## First Electrical Failures
First electrical failures observed for the two cables present extracted from the corresponding IRMS and SCDU data files
IRMS-1 Location C, Inter-cable 6-cable bundle - all cables in bundle in order of observed failures.
Cable D - XLPE/CSPE |  |  | Cable E - EPR/CPE |  |  | Cable F - XLPE/CSPE |  |  | Cable B - EPR/CPE |  |  | Cable C - EPR/CPE |  |  | Cable A - XLPE/CSPE
Time | Offset Time | D7-D8 | Time | Offset Time | E9-E10 | Time | Offset Time | F11-G | Time | Offset Time | B3-G | Time | Offset Time | C5-G | Time | Offset Time | A1-A2
143 | -2 | 261137.9994 | 168 | 23 | 261237.9994 | 157.6 | 12.6 | 257838 | 56.2778 | -88.7222 | 234238 | 86.1111 | -58.8889 | 234538 | 0.5 | -144.5 | 254237.9994
328 | 183 | 261137.9994 | 353 | 208 | 261237.9994 | 342.4 | 197.4 | 257838 | 240.9444 | 95.9444 | 234238 | 270.8889 | 125.8889 | 234538 | 185 | 40 | 254237.9994
512.5 | 367.5 | 79.7129 | 538 | 393 | 25.6055 | 527.1 | 382.1 | 148.3377 | 425.7222 | 280.7222 | 234238 | 455.6111 | 310.6111 | 234538 | 370 | 225 | 254237.9994
697.5 | 552.5 | 6.427 | 722.5 | 577.5 | 0.95474 | 711.9 | 566.9 | 0.63488 | 610.6667 | 465.6667 | 234238 | 640.4444 | 495.4444 | 234538 | 554.5 | 409.5 | 254237.9994
882 | 737 | 0.95389 | 907.5 | 762.5 | 11.3277 | 896.6 | 751.6 | 0.63909 | 795.2778 | 650.2778 | 28.6875 | 825.1111 | 680.1111 | 6.2554 | 739.5 | 594.5 | 254237.9994
1067 | 922 | 25.4948 | 1092 | 947 | 19.9549 | 1081.5 | 936.5 | 0.62615 | 980.1111 | 835.1111 | 0.64514 | 1009.9444 | 864.9444 | 0.63562 | 924 | 779 | 64.7189
1251.5 | 1106.5 | 5.798 | 1277 | 1132 | 13.2809 | 1266.3 | 1121.3 | 3.6778 | 1164.8333 | 1019.8333 | 0.66209 | 1194.8333 | 1049.8333 | 0.84707 | 1109 | 964 | 0.41588
1436.5 | 1291.5 | 30.5282 | 1461.5 | 1316.5 | 28.2067 | 1451 | 1306 | 14.1319 | 1349.7222 | 1204.7222 | 1.8938 | 1379.5556 | 1234.5556 | 6.3362 | 1293.5 | 1148.5 | 17.4309
1621.5 | 1476.5 | 141.1734 | 1646.5 | 1501.5 | 12.5722 | 1635.8 | 1490.8 | 21.8885 | 1534.5 | 1389.5 | 11.8558 | 1564.3889 | 1419.3889 | 0.703 | 1478.5 | 1333.5 | 95.0642
SCDU1 - IC Location A |  |  |  | SCDU2 - IC Location A |  |  |  | SCDU3 - IC Location C |  |  |  | SCDU4 - AC-1 Location G
Time | Offset Time | C1 V1 | C1 V5 | Time | Offset Time | C2 V1 | C2 V6 | Time | Offset Time | C3 V1 | C3 V4 | Time | Offset Time | C4 V1
0 | -145 | 130.2441 | 0.046168 | 0 | -145 | 130.002 | 0.017929 | 0 | -145 | 131.1962 | -0.092337 | 0 | -145 | 127.3588
60 | -85 | 129.4764 | 0.046168 | 60 | -85 | 129.3303 | 0.017929 | 60 | -85 | 130.6204 | 0.099605 | 60 | -85 | 126.687
120 | -25 | 129.5724 | 0.23811 | 120 | -25 | 129.3303 | 0.017929 | 120 | -25 | 130.5244 | 0.099605 | 120 | -25 | 126.5911
150 | 5 | 129.6683 | 0.33406 | 150 | 5 | 129.3303 | 0.017929 | 150 | 5 | 130.4284 | 0.099605 | 150 | 5 | 126.5911
160 | 15 | 129.5724 | 0.33406 | 160 | 15 | 129.1384 | 0.017929 | 160 | 15 | 130.3325 | 0.003654 | 160 | 15 | 126.4951
160.2 | 15.2 | 79.7654 | -0.049822 | 160.2 | 15.2 | 129.3303 | 0.017929 | 160.2 | 15.2 | 130.5244 | 0.099605 | 160.2 | 15.2 | 126.5911
160.4 | 15.4 | -73.4943 | -72.601 | 160.4 | 15.4 | 129.4263 | 0.017929 | 160.4 | 15.4 | 130.6204 | 0.099605 | 160.4 | 15.4 | 126.687
160.6 | 15.6 | -73.4943 | -73.3688 | 160.6 | 15.6 | 47.4702 | -0.078023 | 160.6 | 15.6 | 130.7164 | 0.099605 | 160.6 | 15.6 | 126.879
160.8 | 15.8 | -73.4943 | -73.3688 | 160.8 | 15.8 | -73.4485 | -73.493 | 160.8 | 15.8 | 130.8123 | 0.099605 | 160.8 | 15.8 | 126.9749
161 | 16 | -73.4943 | -73.3688 | 161 | 16 | -73.4485 | -73.493 | 161 | 16 | 37.6281 | 0.29155 | 161 | 16 | 127.1668
161.2 | 16.2 | -73.4943 | -73.3688 | 161.2 | 16.2 | -73.4485 | -73.493 | 161.2 | 16.2 | -73.31 | -73.4113 | 161.2 | 16.2 | 123.7121
161.4 | 16.4 | -73.4943 | -73.3688 | 161.4 | 16.4 | -73.4485 | -73.493 | 161.4 | 16.4 | -73.31 | -73.4113 | 161.4 | 16.4 | -73.5006
161.6 | 16.6 | -73.4943 | -73.3688 | 161.6 | 16.6 | -73.4485 | -73.493 | 161.6 | 16.6 | -73.31 | -73.4113 | 161.6 | 16.6 | -73.5006
161.8 | 16.8 | -73.4943 | -73.3688 | 161.8 | 16.8 | -73.4485 | -73.493 | 161.8 | 16.8 | -73.31 | -73.4113 | 161.8 | 16.8 | -73.5006
162 | 17 | -73.4943 | -73.3688 | 162 | 17 | -73.4485 | -73.493 | 162 | 17 | -73.31 | -73.4113 | 162 | 17 | -73.5006
162.2 | 17.2 | -73.4943 | -73.3688 | 162.2 | 17.2 | -73.4485 | -73.493 | 162.2 | 17.2 | -73.31 | -73.4113 | 162.2 | 17.2 | -73.5006
162.4 | 17.4 | -73.4943 | -73.3688 | 162.4 | 17.4 | -73.4485 | -73.493 | 162.4 | 17.4 | -73.31 | -73.4113 | 162.4 | 17.4 | -73.5006
162.6 | 17.6 | -73.4943 | -73.3688 | 162.6 | 17.6 | -73.4485 | -73.493 | 162.6 | 17.6 | -73.31 | -73.4113 | 162.6 | 17.6 | -73.5006
162.8 | 17.8 | -73.4943 | -73.3688 | 162.8 | 17.8 | -73.4485 | -73.493 | 162.8 | 17.8 | -73.31 | -73.4113 | 162.8 | 17.8 | -73.5006
163 | 18 | -73.4943 | -73.3688 | 163 | 18 | -73.4485 | -73.493 | 163 | 18 | -73.31 | -73.4113 | 163 | 18 | -73.5006
168 | 23 | -73.4943 | -73.3688 | 168 | 23 | -73.4485 | -73.493 | 168 | 23 | -73.31 | -73.4113 | 168 | 23 | -73.5006
168.2 | 23.2 | -73.4943 | -73.3688 | 168.2 | 23.2 | -73.4485 | -73.493 | 168.2 | 23.2 | -73.31 | -73.4113 | 168.2 | 23.2 | -73.5006
168.4 | 23.4 | -73.4943 | -73.3688 | 168.4 | 23.4 | -73.4485 | -73.493 | 168.4 | 23.4 | -73.31 | -73.4113 | 168.4 | 23.4 | -73.5006
168.6 | 23.6 | 111.2426 | 0.23811 | 168.6 | 23.6 | -73.4485 | -73.493 | 168.6 | 23.6 | -73.31 | -73.4113 | 168.6 | 23.6 | -73.5006
168.8 | 23.8 | 128.6127 | 0.23811 | 168.8 | 23.8 | -73.4485 | -73.493 | 168.8 | 23.8 | -73.31 | -73.4113 | 168.8 | 23.8 | -73.5006
169 | 24 | 130.0522 | 0.23811 | 169 | 24 | -73.3525 | -73.493 | 169 | 24 | -73.31 | -73.4113 | 169 | 24 | -73.5006
169.2 | 24.2 | 130.2441 | 0.23811 | 169.2 | 24.2 | -73.4485 | -73.493 | 169.2 | 24.2 | -73.31 | -73.4113 | 169.2 | 24.2 | -73.5006
169.4 | 24.4 | 130.3401 | 0.23811 | 169.4 | 24.4 | -73.4485 | -73.493 | 169.4 | 24.4 | -73.31 | -73.4113 | 169.4 | 24.4 | -73.5006
169.6 | 24.6 | 130.3401 | 0.23811 | 169.6 | 24.6 | -73.4485 | -73.493 | 169.6 | 24.6 | -73.31 | -73.4113 | 169.6 | 24.6 | -73.5006
169.8 | 24.8 | 130.3401 | 0.23811 | 169.8 | 24.8 | -73.4485 | -73.493 | 169.8 | 24.8 | -73.31 | -73.4113 | 169.8 | 24.8 | -73.5006
170 | 25 | 130.3401 | 0.23811 | 170 | 25 | -73.3525 | -73.493 | 170 | 25 | -73.31 | -73.4113 | 170 | 25 | -73.5006
170.2 | 25.2 | 130.1482 | 0.23811 | 170.2 | 25.2 | 105.6264 | 0.017929 | 170.2 | 25.2 | -73.31 | -73.4113 | 170.2 | 25.2 | -73.5006
170.4 | 25.4 | 130.1482 | 0.23811 | 170.4 | 25.4 | 127.7948 | 0.017929 | 170.4 | 25.4 | -73.214 | -73.4113 | 170.4 | 25.4 | -73.5006
170.6 | 25.6 | 130.1482 | 0.23811 | 170.6 | 25.6 | 129.3303 | 0.017929 | 170.6 | 25.6 | -73.31 | -73.4113 | 170.6 | 25.6 | -73.5006
170.8 | 25.8 | 130.2441 | 0.23811 | 170.8 | 25.8 | 129.6182 | 0.017929 | 170.8 | 25.8 | -73.31 | -73.4113 | 170.8 | 25.8 | -73.5006
171 | 26 | 130.1482 | 0.23811 | 171 | 26 | 129.6182 | 0.017929 | 171 | 26 | -73.31 | -73.4113 | 171 | 26 | -73.5006
171.2 | 26.2 | 130.1482 | 0.23811 | 171.2 | 26.2 | 129.6182 | 0.017929 | 171.2 | 26.2 | 8.0702 | -0.18829 | 171.2 | 26.2 | -73.4047
171.4 | 26.4 | 129.9562 | 0.23811 | 171.4 | 26.4 | 129.5222 | 0.017929 | 171.4 | 26.4 | 123.1349 | 0.003654 | 171.4 | 26.4 | -73.5006
171.6 | 26.6 | 129.9562 | 0.14212 | 171.6 | 26.6 | 129.5222 | 0.017929 | 171.6 | 26.6 | 129.8526 | 0.003654 | 171.6 | 26.6 | -73.5006
171.8 | 26.8 | 130.0522 | 0.23811 | 171.8 | 26.8 | 129.5222 | 0.017929 | 171.8 | 26.8 | 130.5244 | 0.003654 | 171.8 | 26.8 | -73.5006
172 | 27 | 130.0522 | 0.23811 | 172 | 27 | 129.5222 | 0.017929 | 172 | 27 | 130.5244 | 0.003654 | 172 | 27 | -73.5006
172.2 | 27.2 | 130.0522 | 0.23811 | 172.2 | 27.2 | 129.6182 | 0.017929 | 172.2 | 27.2 | 130.7164 | 0.003654 | 172.2 | 27.2 | -73.5006
172.4 | 27.4 | 129.7643 | 0.23811 | 172.4 | 27.4 | 129.3303 | 0.017929 | 172.4 | 27.4 | 130.3325 | 0.003654 | 172.4 | 27.4 | 113.9234
172.6 | 27.6 | 129.8603 | 0.23811 | 172.6 | 27.6 | 129.3303 | 0.017929 | 172.6 | 27.6 | 130.4284 | 0.003654 | 172.6 | 27.6 | 125.3435
400 | 255 | 130.0522 | 0.71795 | 400 | 255 | 129.2343 | 0.017929 | 400 | 255 | 130.5244 | 0.099605 | 400 | 255 | 126.5911
400.2 | 255.2 | 130.1482 | 0.71795 | 400.2 | 255.2 | 129.3303 | 0.017929 | 400.2 | 255.2 | 130.6204 | 0.099605 | 400.2 | 255.2 | 126.687
400.4 | 255.4 | 130.1482 | 0.71795 | 400.4 | 255.4 | 129.3303 | -0.078023 | 400.4 | 255.4 | 130.5244 | 0.1956 | 400.4 | 255.4 | 126.687
400.6 | 255.6 | 130.2441 | 0.8139 | 400.6 | 255.6 | 129.4263 | 0.017929 | 400.6 | 255.6 | 130.6204 | 0.099605 | 400.6 | 255.6 | 126.687
400.8 | 255.8 | 130.1482 | 0.71795 | 400.8 | 255.8 | 129.2343 | 0.017929 | 400.8 | 255.8 | 130.6204 | 0.1956 | 400.8 | 255.8 | 126.687
401 | 256 | 130.1482 | 0.8139 | 401 | 256 | 129.3303 | 0.017929 | 401 | 256 | 130.6204 | 0.1956 | 401 | 256 | 126.687
401.2 | 256.2 | 130.2441 | 0.71795 | 401.2 | 256.2 | 129.3303 | 0.017929 | 401.2 | 256.2 | 130.6204 | 0.099605 | 401.2 | 256.2 | 126.687
401.4 | 256.4 | 130.3401 | 0.71795 | 401.4 | 256.4 | 129.3303 | 0.017929 | 401.4 | 256.4 | 130.6204 | 0.1956 | 401.4 | 256.4 | 126.687
401.6 | 256.6 | 130.2441 | 0.71795 | 401.6 | 256.6 | 129.4263 | 0.017929 | 401.6 | 256.6 | 130.6204 | 0.1956 | 401.6 | 256.6 | 126.687
401.8 | 256.8 | 130.2441 | 0.8139 | 401.8 | 256.8 | 129.3303 | 0.017929 | 401.8 | 256.8 | 130.6204 | 0.1956 | 401.8 | 256.8 | 126.687
402 | 257 | 130.2441 | 0.8139 | 402 | 257 | 129.3303 | 0.017929 | 402 | 257 | 130.6204 | 0.099605 | 402 | 257 | 126.687
402.2 | 257.2 | 130.3401 | 0.8139 | 402.2 | 257.2 | 129.3303 | 0.017929 | 402.2 | 257.2 | 130.6204 | 0.1956 | 402.2 | 257.2 | 126.687
402.4 | 257.4 | 130.3401 | 0.8139 | 402.4 | 257.4 | 129.3303 | 0.017929 | 402.4 | 257.4 | 130.5244 | 0.1956 | 402.4 | 257.4 | 126.687
402.6 | 257.6 | 130.3401 | 0.8139 | 402.6 | 257.6 | 129.3303 | 0.017929 | 402.6 | 257.6 | 130.6204 | 0.1956 | 402.6 | 257.6 | 126.687
402.8 | 257.8 | 130.3401 | 0.8139 | 402.8 | 257.8 | 129.3303 | 0.017929 | 402.8 | 257.8 | 130.6204 | 0.1956 | 402.8 | 257.8 | 126.687
403 | 258 | 130.3401 | 0.8139 | 403 | 258 | 129.4263 | 0.017929 | 403 | 258 | 130.6204 | 0.1956 | 403 | 258 | 126.783
403.2 | 258.2 | 130.3401 | 0.8139 | 403.2 | 258.2 | 129.3303 | 0.017929 | 403.2 | 258.2 | 130.6204 | 0.099605 | 403.2 | 258.2 | 126.687
403.4 | 258.4 | 130.3401 | 0.8139 | 403.4 | 258.4 | 129.4263 | 0.017929 | 403.4 | 258.4 | 130.6204 | 0.099605 | 403.4 | 258.4 | 126.687
403.6 | 258.6 | 130.3401 | 0.8139 | 403.6 | 258.6 | 129.4263 | 0.017929 | 403.6 | 258.6 | 130.6204 | 0.1956 | 403.6 | 258.6 | 126.783
403.8 | 258.8 | 130.4361 | 0.8139 | 403.8 | 258.8 | 129.4263 | 0.017929 | 403.8 | 258.8 | 130.6204 | 0.1956 | 403.8 | 258.8 | 126.687
404 | 259 | 130.3401 | 0.8139 | 404 | 259 | 129.3303 | 0.017929 | 404 | 259 | 130.6204 | 0.1956 | 404 | 259 | 126.687
404.2 | 259.2 | 130.3401 | 0.8139 | 404.2 | 259.2 | 129.3303 | 0.017929 | 404.2 | 259.2 | 130.6204 | 0.1956 | 404.2 | 259.2 | 126.687
404.4 | 259.4 | 130.3401 | 0.8139 | 404.4 | 259.4 | 129.4263 | 0.017929 | 404.4 | 259.4 | 130.6204 | 0.1956 | 404.4 | 259.4 | 126.783
404.6 | 259.6 | 130.3401 | 0.8139 | 404.6 | 259.6 | 129.4263 | -0.078023 | 404.6 | 259.6 | 130.6204 | 0.1956 | 404.6 | 259.6 | 126.687
404.8 | 259.8 | 130.3401 | 0.8139 | 404.8 | 259.8 | 129.4263 | 0.017929 | 404.8 | 259.8 | 130.6204 | 0.1956 | 404.8 | 259.8 | 126.687
405 | 260 | 130.4361 | 0.90985 | 405 | 260 | 129.4263 | 0.017929 | 405 | 260 | 130.6204 | 0.1956 | 405 | 260 | 126.687
405.2 | 260.2 | 130.3401 | 0.90985 | 405.2 | 260.2 | 129.3303 | 0.017929 | 405.2 | 260.2 | 130.6204 | 0.1956 | 405.2 | 260.2 | 126.687
405.4 | 260.4 | 130.4361 | 0.90985 | 405.4 | 260.4 | 129.4263 | 0.017929 | 405.4 | 260.4 | 130.6204 | 0.1956 | 405.4 | 260.4 | 126.783
405.6 | 260.6 | 130.3401 | 0.8139 | 405.6 | 260.6 | 129.3303 | 0.017929 | 405.6 | 260.6 | 130.6204 | 0.1956 | 405.6 | 260.6 | 126.687
405.8 | 260.8 | 130.4361 | 0.8139 | 405.8 | 260.8 | 129.3303 | 0.017929 | 405.8 | 260.8 | 130.6204 | 0.099605 | 405.8 | 260.8 | 126.687
406 | 261 | 130.4361 | 0.8139 | 406 | 261 | 129.3303 | 0.017929 | 406 | 261 | 130.6204 | 0.1956 | 406 | 261 | 126.687
406.2 | 261.2 | 130.4361 | 0.90985 | 406.2 | 261.2 | 129.4263 | 0.017929 | 406.2 | 261.2 | 130.6204 | 0.1956 | 406.2 | 261.2 | 126.687
406.4 | 261.4 | 130.4361 | 0.90985 | 406.4 | 261.4 | 129.4263 | 0.017929 | 406.4 | 261.4 | 130.6204 | 0.099605 | 406.4 | 261.4 | 126.783
406.6 | 261.6 | 130.3401 | 0.90985 | 406.6 | 261.6 | 129.3303 | 0.017929 | 406.6 | 261.6 | 130.5244 | 0.099605 | 406.6 | 261.6 | 126.5911
406.8 | 261.8 | 130.4361 | 0.90985 | 406.8 | 261.8 | 129.4263 | 0.017929 | 406.8 | 261.8 | 130.6204 | 0.1956 | 406.8 | 261.8 | 126.687
407 | 262 | 130.4361 | 0.90985 | 407 | 262 | 129.3303 | 0.017929 | 407 | 262 | 130.6204 | 0.099605 | 407 | 262 | 126.687
407.2 | 262.2 | 130.4361 | 0.90985 | 407.2 | 262.2 | 129.3303 | 0.017929 | 407.2 | 262.2 | 130.6204 | 0.099605 | 407.2 | 262.2 | 126.687
407.4 | 262.4 | 130.4361 | 0.8139 | 407.4 | 262.4 | 129.3303 | 0.017929 | 407.4 | 262.4 | 130.6204 | 0.1956 | 407.4 | 262.4 | 126.687
407.6 | 262.6 | 130.3401 | 0.90985 | 407.6 | 262.6 | 129.3303 | 0.017929 | 407.6 | 262.6 | 130.6204 | 0.1956 | 407.6 | 262.6 | 126.687
407.8 | 262.8 | 130.4361 | 0.90985 | 407.8 | 262.8 | 129.4263 | 0.017929 | 407.8 | 262.8 | 130.6204 | 0.1956 | 407.8 | 262.8 | 126.687
408 | 263 | 130.3401 | 0.90985 | 408 | 263 | 129.3303 | 0.017929 | 408 | 263 | 130.5244 | 0.1956 | 408 | 263 | 126.687
408.2 | 263.2 | 130.532 | 0.90985 | 408.2 | 263.2 | 129.4263 | 0.017929 | 408.2 | 263.2 | 130.7164 | 0.1956 | 408.2 | 263.2 | 126.687
408.4 | 263.4 | 130.4361 | 0.90985 | 408.4 | 263.4 | 129.3303 | 0.017929 | 408.4 | 263.4 | 130.7164 | 0.1956 | 408.4 | 263.4 | 126.687
408.6 | 263.6 | 130.4361 | 0.90985 | 408.6 | 263.6 | 129.3303 | 0.017929 | 408.6 | 263.6 | 130.5244 | 0.099605 | 408.6 | 263.6 | 126.687
408.8 | 263.8 | 130.4361 | 1.0058 | 408.8 | 263.8 | 129.3303 | 0.017929 | 408.8 | 263.8 | 130.6204 | 0.1956 | 408.8 | 263.8 | 126.687
409 | 264 | 130.4361 | 0.90985 | 409 | 264 | 129.3303 | 0.017929 | 409 | 264 | 130.6204 | 0.099605 | 409 | 264 | 126.687
409.2 | 264.2 | 130.532 | 0.90985 | 409.2 | 264.2 | 129.4263 | 0.017929 | 409.2 | 264.2 | 130.7164 | 0.1956 | 409.2 | 264.2 | 126.783
409.4 | 264.4 | 130.532 | 0.90985 | 409.4 | 264.4 | 129.3303 | 0.017929 | 409.4 | 264.4 | 130.6204 | 0.1956 | 409.4 | 264.4 | 126.687
409.6 | 264.6 | 130.532 | 0.90985 | 409.6 | 264.6 | 129.3303 | 0.017929 | 409.6 | 264.6 | 130.6204 | 0.1956 | 409.6 | 264.6 | 126.687
409.8 | 264.8 | 130.4361 | 0.90985 | 409.8 | 264.8 | 129.3303 | 0.017929 | 409.8 | 264.8 | 130.6204 | 0.1956 | 409.8 | 264.8 | 126.687
410 | 265 | 130.4361 | 1.0058 | 410 | 265 | 129.2343 | 0.017929 | 410 | 265 | 130.6204 | 0.1956 | 410 | 265 | 126.5911
410.2 | 265.2 | 130.532 | 0.90985 | 410.2 | 265.2 | 129.4263 | 0.017929 | 410.2 | 265.2 | 130.6204 | 0.1956 | 410.2 | 265.2 | 126.783
410.4 | 265.4 | 130.532 | 0.90985 | 410.4 | 265.4 | 129.3303 | 0.017929 | 410.4 | 265.4 | 130.6204 | 0.1956 | 410.4 | 265.4 | 126.687
410.6 | 265.6 | 130.532 | 1.0058 | 410.6 | 265.6 | 129.4263 | 0.017929 | 410.6 | 265.6 | 130.6204 | 0.1956 | 410.6 | 265.6 | 126.783
410.8 | 265.8 | 130.532 | 0.90985 | 410.8 | 265.8 | 129.3303 | 0.017929 | 410.8 | 265.8 | 130.7164 | 0.1956 | 410.8 | 265.8 | 126.783
411 | 266 | 130.532 | 1.0058 | 411 | 266 | 129.3303 | 0.017929 | 411 | 266 | 130.7164 | 0.099605 | 411 | 266 | 126.687
411.2 | 266.2 | 130.628 | 1.0058 | 411.2 | 266.2 | 129.4263 | 0.017929 | 411.2 | 266.2 | 130.6204 | 0.099605 | 411.2 | 266.2 | 126.783
411.4 | 266.4 | 130.628 | 1.0058 | 411.4 | 266.4 | 129.3303 | 0.017929 | 411.4 | 266.4 | 130.7164 | 0.099605 | 411.4 | 266.4 | 126.687
411.6 | 266.6 | 130.628 | 1.0058 | 411.6 | 266.6 | 129.4263 | 0.017929 | 411.6 | 266.6 | 130.7164 | 0.099605 | 411.6 | 266.6 | 126.783
411.8 | 266.8 | 130.532 | 1.0058 | 411.8 | 266.8 | 129.4263 | 0.017929 | 411.8 | 266.8 | 130.6204 | 0.1956 | 411.8 | 266.8 | 126.783
412 | 267 | 130.532 | 1.0058 | 412 | 267 | 129.4263 | 0.017929 | 412 | 267 | 130.6204 | 0.099605 | 412 | 267 | 126.687
412.2 | 267.2 | 130.532 | 1.0058 | 412.2 | 267.2 | 129.4263 | 0.017929 | 412.2 | 267.2 | 130.7164 | 0.1956 | 412.2 | 267.2 | 126.687
412.4 | 267.4 | 130.628 | 1.0058 | 412.4 | 267.4 | 129.3303 | 0.017929 | 412.4 | 267.4 | 130.7164 | 0.099605 | 412.4 | 267.4 | 126.687
412.6 | 267.6 | 130.628 | 1.0058 | 412.6 | 267.6 | 129.4263 | 0.017929 | 412.6 | 267.6 | 130.7164 | 0.1956 | 412.6 | 267.6 | 126.783
412.8 | 267.8 | 130.532 | 1.0058 | 412.8 | 267.8 | 129.4263 | 0.017929 | 412.8 | 267.8 | 130.7164 | 0.099605 | 412.8 | 267.8 | 126.783
413 | 268 | 130.628 | 1.0058 | 413 | 268 | 129.4263 | 0.017929 | 413 | 268 | 130.7164 | 0.1956 | 413 | 268 | 126.783
413.2 | 268.2 | 130.628 | 1.0058 | 413.2 | 268.2 | 129.4263 | 0.017929 | 413.2 | 268.2 | 130.6204 | 0.099605 | 413.2 | 268.2 | 126.783
413.4 | 268.4 | 130.628 | 1.0058 | 413.4 | 268.4 | 129.4263 | 0.017929 | 413.4 | 268.4 | 130.6204 | 0.1956 | 413.4 | 268.4 | 126.783
413.6 | 268.6 | 130.7239 | 1.0058 | 413.6 | 268.6 | 129.4263 | 0.017929 | 413.6 | 268.6 | 130.7164 | 0.1956 | 413.6 | 268.6 | 126.783
413.8 | 268.8 | 130.7239 | 1.0058 | 413.8 | 268.8 | 129.4263 | 0.017929 | 413.8 | 268.8 | 130.7164 | 0.1956 | 413.8 | 268.8 | 126.783
414 | 269 | 130.628 | 1.0058 | 414 | 269 | 129.4263 | 0.017929 | 414 | 269 | 130.7164 | 0.099605 | 414 | 269 | 126.783
414.2 | 269.2 | 130.628 | 1.0058 | 414.2 | 269.2 | 129.4263 | 0.017929 | 414.2 | 269.2 | 130.7164 | 0.1956 | 414.2 | 269.2 | 126.783
414.4 | 269.4 | 130.628 | 1.0058 | 414.4 | 269.4 | 129.4263 | 0.017929 | 414.4 | 269.4 | 130.8123 | 0.1956 | 414.4 | 269.4 | 126.783
414.6 | 269.6 | 130.7239 | 1.0058 | 414.6 | 269.6 | 129.5222 | 0.017929 | 414.6 | 269.6 | 130.7164 | 0.1956 | 414.6 | 269.6 | 126.783
414.8 | 269.8 | 130.628 | 1.0058 | 414.8 | 269.8 | 129.4263 | 0.017929 | 414.8 | 269.8 | 130.7164 | 0.1956 | 414.8 | 269.8 | 126.783
415 | 270 | 130.7239 | 1.0058 | 415 | 270 | 129.5222 | 0.017929 | 415 | 270 | 130.8123 | 0.1956 | 415 | 270 | 126.879
415.2 | 270.2 | 130.7239 | 1.0058 | 415.2 | 270.2 | 129.5222 | 0.017929 | 415.2 | 270.2 | 130.7164 | 0.099605 | 415.2 | 270.2 | 126.783
415.4 | 270.4 | 130.8199 | 1.0058 | 415.4 | 270.4 | 129.5222 | 0.017929 | 415.4 | 270.4 | 130.8123 | 0.099605 | 415.4 | 270.4 | 126.879
415.6 | 270.6 | 130.7239 | 1.0058 | 415.6 | 270.6 | 129.5222 | 0.017929 | 415.6 | 270.6 | 130.8123 | 0.1956 | 415.6 | 270.6 | 126.879
415.8 | 270.8 | 130.628 | 1.1018 | 415.8 | 270.8 | 129.5222 | 0.017929 | 415.8 | 270.8 | 130.7164 | 0.099605 | 415.8 | 270.8 | 126.879
416 | 271 | 130.7239 | 1.1018 | 416 | 271 | 129.4263 | 0.017929 | 416 | 271 | 130.7164 | 0.1956 | 416 | 271 | 126.783
416.2 | 271.2 | 130.7239 | 1.1018 | 416.2 | 271.2 | 129.4263 | 0.017929 | 416.2 | 271.2 | 130.7164 | 0.099605 | 416.2 | 271.2 | 126.783
416.4 | 271.4 | 130.7239 | 1.0058 | 416.4 | 271.4 | 129.5222 | 0.017929 | 416.4 | 271.4 | 130.7164 | 0.1956 | 416.4 | 271.4 | 126.879
416.6 | 271.6 | 130.7239 | 1.0058 | 416.6 | 271.6 | 129.5222 | 0.017929 | 416.6 | 271.6 | 130.8123 | 0.099605 | 416.6 | 271.6 | 126.783
416.8 | 271.8 | 130.7239 | 1.0058 | 416.8 | 271.8 | 129.5222 | 0.017929 | 416.8 | 271.8 | 130.7164 | 0.099605 | 416.8 | 271.8 | 126.783
417 | 272 | 130.7239 | 1.0058 | 417 | 272 | 129.5222 | 0.017929 | 417 | 272 | 130.8123 | 0.1956 | 417 | 272 | 126.879
417.2 | 272.2 | 130.8199 | 1.0058 | 417.2 | 272.2 | 129.5222 | 0.017929 | 417.2 | 272.2 | 130.8123 | 0.1956 | 417.2 | 272.2 | 126.879
417.4 | 272.4 | 130.8199 | 1.0058 | 417.4 | 272.4 | 129.5222 | 0.017929 | 417.4 | 272.4 | 130.8123 | 0.099605 | 417.4 | 272.4 | 126.879
417.6 | 272.6 | 130.8199 | 1.1018 | 417.6 | 272.6 | 129.5222 | 0.017929 | 417.6 | 272.6 | 130.8123 | 0.1956 | 417.6 | 272.6 | 126.879
417.8 | 272.8 | 130.8199 | 1.1018 | 417.8 | 272.8 | 129.5222 | 0.017929 | 417.8 | 272.8 | 130.8123 | 0.1956 | 417.8 | 272.8 | 126.879
418 | 273 | 130.7239 | 1.1018 | 418 | 273 | 129.4263 | 0.017929 | 418 | 273 | 130.7164 | 0.099605 | 418 | 273 | 126.783
418.2 | 273.2 | 130.7239 | 1.1018 | 418.2 | 273.2 | 129.4263 | 0.017929 | 418.2 | 273.2 | 130.7164 | 0.099605 | 418.2 | 273.2 | 126.783
418.4 | 273.4 | 130.8199 | 1.1018 | 418.4 | 273.4 | 129.5222 | 0.017929 | 418.4 | 273.4 | 130.8123 | 0.099605 | 418.4 | 273.4 | 126.879
418.6 | 273.6 | 130.9159 | 1.1018 | 418.6 | 273.6 | 129.5222 | 0.017929 | 418.6 | 273.6 | 130.8123 | 0.1956 | 418.6 | 273.6 | 126.783
418.8 | 273.8 | 130.8199 | 1.1018 | 418.8 | 273.8 | 129.5222 | 0.017929 | 418.8 | 273.8 | 130.8123 | 0.1956 | 418.8 | 273.8 | 126.879
419 | 274 | 130.9159 | 1.1018 | 419 | 274 | 129.5222 | 0.017929 | 419 | 274 | 130.8123 | 0.1956 | 419 | 274 | 126.879
419.2 | 274.2 | 130.9159 | 1.1978 | 419.2 | 274.2 | 129.5222 | -0.078023 | 419.2 | 274.2 | 130.8123 | 0.1956 | 419.2 | 274.2 | 126.879
419.4 | 274.4 | 130.9159 | 1.1978 | 419.4 | 274.4 | 129.4263 | 0.017929 | 419.4 | 274.4 | 130.7164 | 0.099605 | 419.4 | 274.4 | 126.783
419.6 | 274.6 | 130.8199 | 1.1018 | 419.6 | 274.6 | 129.5222 | 0.017929 | 419.6 | 274.6 | 130.7164 | 0.099605 | 419.6 | 274.6 | 126.879
419.8 | 274.8 | 130.8199 | 1.1978 | 419.8 | 274.8 | 129.5222 | 0.017929 | 419.8 | 274.8 | 130.7164 | 0.1956 | 419.8 | 274.8 | 126.879
420 | 275 | 130.8199 | 1.1978 | 420 | 275 | 129.4263 | 0.017929 | 420 | 275 | 130.7164 | 0.099605 | 420 | 275 | 126.783
420.2 | 275.2 | 130.9159 | 1.1018 | 420.2 | 275.2 | 129.5222 | -0.078023 | 420.2 | 275.2 | 130.8123 | 0.1956 | 420.2 | 275.2 | 126.879
420.4 | 275.4 | 130.9159 | 1.1978 | 420.4 | 275.4 | 129.5222 | 0.017929 | 420.4 | 275.4 | 130.8123 | 0.1956 | 420.4 | 275.4 | 126.879
420.6 | 275.6 | 130.9159 | 1.1018 | 420.6 | 275.6 | 129.5222 | 0.017929 | 420.6 | 275.6 | 130.8123 | 0.099605 | 420.6 | 275.6 | 126.879
420.8 | 275.8 | 130.9159 | 1.1978 | 420.8 | 275.8 | 129.5222 | 0.017929 | 420.8 | 275.8 | 130.8123 | 0.1956 | 420.8 | 275.8 | 126.879
421 | 276 | 130.9159 | 1.1978 | 421 | 276 | 129.5222 | 0.017929 | 421 | 276 | 130.8123 | 0.1956 | 421 | 276 | 126.879
421.2 | 276.2 | 130.9159 | 1.1978 | 421.2 | 276.2 | 129.6182 | 0.017929 | 421.2 | 276.2 | 130.8123 | 0.1956 | 421.2 | 276.2 | 126.879
421.4 | 276.4 | 130.9159 | 1.1018 | 421.4 | 276.4 | 129.5222 | 0.017929 | 421.4 | 276.4 | 130.8123 | 0.1956 | 421.4 | 276.4 | 126.879
421.6 | 276.6 | 130.9159 | 1.1018 | 421.6 | 276.6 | 129.5222 | 0.017929 | 421.6 | 276.6 | 130.8123 | 0.1956 | 421.6 | 276.6 | 126.879
421.8 | 276.8 | 130.8199 | 1.1978 | 421.8 | 276.8 | 129.5222 | 0.017929 | 421.8 | 276.8 | 130.8123 | 0.099605 | 421.8 | 276.8 | 126.879
422 | 277 | 130.8199 | 1.1978 | 422 | 277 | 129.4263 | 0.017929 | 422 | 277 | 130.8123 | 0.1956 | 422 | 277 | 126.783
422.2 | 277.2 | 130.9159 | 1.1978 | 422.2 | 277.2 | 129.6182 | 0.017929 | 422.2 | 277.2 | 130.8123 | 0.099605 | 422.2 | 277.2 | 126.9749
422.4 | 277.4 | 130.9159 | 1.1978 | 422.4 | 277.4 | 129.6182 | 0.017929 | 422.4 | 277.4 | 130.9083 | 0.099605 | 422.4 | 277.4 | 126.9749
422.6 | 277.6 | 131.0119 | 1.1978 | 422.6 | 277.6 | 129.6182 | 0.017929 | 422.6 | 277.6 | 130.9083 | 0.1956 | 422.6 | 277.6 | 126.9749
422.8 | 277.8 | 130.9159 | 1.1978 | 422.8 | 277.8 | 129.6182 | -0.078023 | 422.8 | 277.8 | 130.9083 | 0.1956 | 422.8 | 277.8 | 126.9749
423 | 278 | 131.0119 | 1.1018 | 423 | 278 | 129.6182 | 0.017929 | 423 | 278 | 130.9083 | 0.099605 | 423 | 278 | 126.9749
423.2 | 278.2 | 131.0119 | 1.1978 | 423.2 | 278.2 | 129.5222 | 0.017929 | 423.2 | 278.2 | 130.9083 | 0.1956 | 423.2 | 278.2 | 126.9749
423.4 | 278.4 | 130.9159 | 1.1018 | 423.4 | 278.4 | 129.5222 | 0.017929 | 423.4 | 278.4 | 130.8123 | 0.1956 | 423.4 | 278.4 | 126.879
423.6 | 278.6 | 130.9159 | 1.1978 | 423.6 | 278.6 | 129.6182 | 0.017929 | 423.6 | 278.6 | 130.9083 | 0.1956 | 423.6 | 278.6 | 126.9749
423.8 | 278.8 | 130.9159 | 1.1978 | 423.8 | 278.8 | 129.5222 | 0.017929 | 423.8 | 278.8 | 130.9083 | 0.099605 | 423.8 | 278.8 | 126.9749
424 | 279 | 130.9159 | 1.1018 | 424 | 279 | 129.6182 | 0.017929 | 424 | 279 | 130.8123 | 0.099605 | 424 | 279 | 126.9749
424.2 | 279.2 | 131.0119 | 1.1978 | 424.2 | 279.2 | 129.5222 | 0.017929 | 424.2 | 279.2 | 130.9083 | 0.099605 | 424.2 | 279.2 | 126.9749
424.4 | 279.4 | 131.0119 | 1.1018 | 424.4 | 279.4 | 129.6182 | 0.017929 | 424.4 | 279.4 | 130.9083 | 0.1956 | 424.4 | 279.4 | 126.9749
424.6 | 279.6 | 130.9159 | 1.1978 | 424.6 | 279.6 | 129.6182 | 0.017929 | 424.6 | 279.6 | 130.9083 | 0.1956 | 424.6 | 279.6 | 126.9749
424.8 | 279.8 | 130.628 | 1.1978 | 424.8 | 279.8 | 129.6182 | 0.017929 | 424.8 | 279.8 | 130.9083 | 0.099605 | 424.8 | 279.8 | 126.9749
425 | 280 | 130.3401 | 1.2937 | 425 | 280 | 129.6182 | 0.017929 | 425 | 280 | 130.9083 | 0.1956 | 425 | 280 | 126.9749
425.2 | 280.2 | 130.4361 | 1.1978 | 425.2 | 280.2 | 129.6182 | 0.017929 | 425.2 | 280.2 | 130.9083 | 0.099605 | 425.2 | 280.2 | 126.879
425.4 | 280.4 | 130.0522 | 1.1018 | 425.4 | 280.4 | 129.7141 | 0.017929 | 425.4 | 280.4 | 130.9083 | 0.099605 | 425.4 | 280.4 | 126.9749
425.6 | 280.6 | 130.1482 | 1.2937 | 425.6 | 280.6 | 129.9061 | 0.017929 | 425.6 | 280.6 | 130.9083 | 0.099605 | 425.6 | 280.6 | 126.9749
425.8 | 280.8 | 130.2441 | 1.1978 | 425.8 | 280.8 | 130.194 | 0.017929 | 425.8 | 280.8 | 130.9083 | 0.1956 | 425.8 | 280.8 | 126.9749
426 | 281 | 130.3401 | 1.0058 | 426 | 281 | 130.194 | 0.017929 | 426 | 281 | 131.0042 | 0.1956 | 426 | 281 | 126.9749
426.2 | 281.2 | 130.532 | 1.0058 | 426.2 | 281.2 | 129.8101 | 0.017929 | 426.2 | 281.2 | 131.0042 | 0.1956 | 426.2 | 281.2 | 126.9749
426.4 | 281.4 | 130.7239 | 1.1978 | 426.4 | 281.4 | 129.8101 | 0.017929 | 426.4 | 281.4 | 131.0042 | 0.1956 | 426.4 | 281.4 | 126.9749
426.6 | 281.6 | 130.9159 | 1.1018 | 426.6 | 281.6 | 129.8101 | 0.017929 | 426.6 | 281.6 | 131.1002 | 0.099605 | 426.6 | 281.6 | 126.9749
426.8 | 281.8 | 130.9159 | 1.1018 | 426.8 | 281.8 | 129.7141 | 0.017929 | 426.8 | 281.8 | 131.3881 | 0.1956 | 426.8 | 281.8 | 126.9749
427 | 282 | 130.9159 | 1.1018 | 427 | 282 | 129.7141 | 0.017929 | 427 | 282 | 131.1002 | 0.1956 | 427 | 282 | 127.0709
427.2 | 282.2 | 130.9159 | 1.1018 | 427.2 | 282.2 | 129.7141 | 0.017929 | 427.2 | 282.2 | 131.1002 | 0.1956 | 427.2 | 282.2 | 127.0709
427.4 | 282.4 | 131.1078 | 1.1978 | 427.4 | 282.4 | 129.7141 | 0.017929 | 427.4 | 282.4 | 131.1002 | 0.1956 | 427.4 | 282.4 | 127.1668
427.6 | 282.6 | 131.0119 | 1.1978 | 427.6 | 282.6 | 129.7141 | 0.017929 | 427.6 | 282.6 | 131.1002 | 0.1956 | 427.6 | 282.6 | 127.2628
427.8 | 282.8 | 131.0119 | 1.1018 | 427.8 | 282.8 | 129.7141 | 0.017929 | 427.8 | 282.8 | 131.1002 | 0.1956 | 427.8 | 282.8 | 127.4548
428 | 283 | 130.9159 | 1.1018 | 428 | 283 | 129.6182 | 0.017929 | 428 | 283 | 131.0042 | 0.1956 | 428 | 283 | 127.6467
428.2 | 283.2 | 131.0119 | 1.1018 | 428.2 | 283.2 | 129.6182 | 0.017929 | 428.2 | 283.2 | 131.0042 | 0.099605 | 428.2 | 283.2 | 127.2628
428.4 | 283.4 | 131.0119 | 1.1978 | 428.4 | 283.4 | 129.5222 | 0.017929 | 428.4 | 283.4 | 131.0042 | 0.1956 | 428.4 | 283.4 | 127.2628
428.6 | 283.6 | 130.9159 | 1.1018 | 428.6 | 283.6 | 129.6182 | 0.017929 | 428.6 | 283.6 | 130.9083 | 0.1956 | 428.6 | 283.6 | 127.1668
428.8 | 283.8 | 131.0119 | 1.1978 | 428.8 | 283.8 | 129.6182 | 0.11392 | 428.8 | 283.8 | 131.0042 | 0.099605 | 428.8 | 283.8 | 127.2628
429 | 284 | 131.0119 | 1.1978 | 429 | 284 | 129.6182 | 0.017929 | 429 | 284 | 131.0042 | 0.1956 | 429 | 284 | 127.1668
429.2 | 284.2 | 130.9159 | 1.1978 | 429.2 | 284.2 | 129.5222 | 0.017929 | 429.2 | 284.2 | 130.9083 | 0.1956 | 429.2 | 284.2 | 127.1668
429.4 | 284.4 | 131.0119 | 1.1978 | 429.4 | 284.4 | 129.6182 | 0.017929 | 429.4 | 284.4 | 130.9083 | 0.1956 | 429.4 | 284.4 | 127.0709
429.6 | 284.6 | 130.9159 | 1.1018 | 429.6 | 284.6 | 129.6182 | 0.017929 | 429.6 | 284.6 | 130.9083 | 0.1956 | 429.6 | 284.6 | 127.0709
429.8 | 284.8 | 131.0119 | 1.1018 | 429.8 | 284.8 | 129.7141 | 0.017929 | 429.8 | 284.8 | 131.0042 | 0.1956 | 429.8 | 284.8 | 127.0709
430 | 285 | 131.0119 | 1.1018 | 430 | 285 | 129.7141 | 0.017929 | 430 | 285 | 131.0042 | 0.1956 | 430 | 285 | 127.0709
430.2 | 285.2 | 131.0119 | 1.1978 | 430.2 | 285.2 | 129.7141 | 0.017929 | 430.2 | 285.2 | 131.1002 | 0.099605 | 430.2 | 285.2 | 127.1668
430.4 | 285.4 | 131.0119 | 1.1978 | 430.4 | 285.4 | 129.7141 | 0.017929 | 430.4 | 285.4 | 131.1002 | 0.1956 | 430.4 | 285.4 | 127.0709
430.6 | 285.6 | 130.9159 | 1.1978 | 430.6 | 285.6 | 129.7141 | 0.017929 | 430.6 | 285.6 | 131.0042 | 0.1956 | 430.6 | 285.6 | 127.0709
430.8 | 285.8 | 130.9159 | 1.1018 | 430.8 | 285.8 | 129.7141 | 0.017929 | 430.8 | 285.8 | 131.0042 | 0.099605 | 430.8 | 285.8 | 127.1668
431 | 286 | 130.9159 | 1.1018 | 431 | 286 | 129.7141 | 0.017929 | 431 | 286 | 131.0042 | 0.1956 | 431 | 286 | 127.0709
431.2 | 286.2 | 130.8199 | 1.1018 | 431.2 | 286.2 | 129.7141 | 0.017929 | 431.2 | 286.2 | 131.0042 | 0.1956 | 431.2 | 286.2 | 127.0709
431.4 | 286.4 | 130.7239 | 1.0058 | 431.4 | 286.4 | 129.6182 | 0.017929 | 431.4 | 286.4 | 130.9083 | 0.1956 | 431.4 | 286.4 | 127.0709
431.6 | 286.6 | 130.7239 | 1.1018 | 431.6 | 286.6 | 129.6182 | 0.11392 | 431.6 | 286.6 | 130.9083 | 0.1956 | 431.6 | 286.6 | 127.0709
431.8 | 286.8 | 130.7239 | 1.0058 | 431.8 | 286.8 | 129.6182 | 0.017929 | 431.8 | 286.8 | 130.9083 | 0.1956 | 431.8 | 286.8 | 127.0709
432 | 287 | 130.7239 | 1.1018 | 432 | 287 | 129.6182 | 0.017929 | 432 | 287 | 130.9083 | 0.1956 | 432 | 287 | 126.9749
432.2 | 287.2 | 130.8199 | 1.0058 | 432.2 | 287.2 | 129.7141 | 0.11392 | 432.2 | 287.2 | 131.0042 | 0.1956 | 432.2 | 287.2 | 127.1668
432.4 | 287.4 | 130.8199 | 1.0058 | 432.4 | 287.4 | 129.7141 | 0.017929 | 432.4 | 287.4 | 131.1002 | 0.1956 | 432.4 | 287.4 | 127.1668
432.6 | 287.6 | 130.9159 | 1.0058 | 432.6 | 287.6 | 129.7141 | 0.017929 | 432.6 | 287.6 | 131.1002 | 0.099605 | 432.6 | 287.6 | 127.1668
432.8 | 287.8 | 130.7239 | 1.0058 | 432.8 | 287.8 | 129.7141 | 0.017929 | 432.8 | 287.8 | 131.0042 | 0.1956 | 432.8 | 287.8 | 127.0709
433 | 288 | 130.7239 | 1.0058 | 433 | 288 | 129.6182 | 0.017929 | 433 | 288 | 130.9083 | 0.1956 | 433 | 288 | 127.0709
433.2 | 288.2 | 130.7239 | 1.0058 | 433.2 | 288.2 | 129.6182 | 0.11392 | 433.2 | 288.2 | 130.9083 | 0.1956 | 433.2 | 288.2 | 127.0709
433.4 | 288.4 | 130.628 | 1.0058 | 433.4 | 288.4 | 129.6182 | 0.017929 | 433.4 | 288.4 | 130.9083 | 0.1956 | 433.4 | 288.4 | 126.9749
433.6 | 288.6 | 130.7239 | 1.0058 | 433.6 | 288.6 | 129.6182 | 0.017929 | 433.6 | 288.6 | 130.9083 | 0.1956 | 433.6 | 288.6 | 126.9749
433.8 | 288.8 | 130.7239 | 1.0058 | 433.8 | 288.8 | 129.6182 | 0.017929 | 433.8 | 288.8 | 130.9083 | 0.1956 | 433.8 | 288.8 | 127.0709
434 | 289 | 130.7239 | 1.0058 | 434 | 289 | 129.6182 | 0.017929 | 434 | 289 | 130.9083 | 0.1956 | 434 | 289 | 126.9749
434.2 | 289.2 | 130.7239 | 1.0058 | 434.2 | 289.2 | 129.6182 | 0.017929 | 434.2 | 289.2 | 130.9083 | 0.099605 | 434.2 | 289.2 | 127.0709
434.4 | 289.4 | 130.7239 | 1.0058 | 434.4 | 289.4 | 129.6182 | 0.017929 | 434.4 | 289.4 | 130.9083 | 0.1956 | 434.4 | 289.4 | 127.0709
434.6 | 289.6 | 130.7239 | 1.0058 | 434.6 | 289.6 | 129.6182 | 0.017929 | 434.6 | 289.6 | 130.9083 | 0.1956 | 434.6 | 289.6 | 127.0709
434.8 | 289.8 | 130.7239 | 1.0058 | 434.8 | 289.8 | 129.6182 | 0.017929 | 434.8 | 289.8 | 131.0042 | 0.1956 | 434.8 | 289.8 | 127.0709
435 | 290 | 130.7239 | 1.0058 | 435 | 290 | 129.6182 | 0.11392 | 435 | 290 | 131.0042 | 0.1956 | 435 | 290 | 127.0709
435.2 | 290.2 | 130.7239 | 1.0058 | 435.2 | 290.2 | 129.6182 | 0.017929 | 435.2 | 290.2 | 131.0042 | 0.1956 | 435.2 | 290.2 | 127.0709
435.4 | 290.4 | 130.7239 | 1.0058 | 435.4 | 290.4 | 129.5222 | 0.017929 | 435.4 | 290.4 | 131.0042 | 0.1956 | 435.4 | 290.4 | 127.0709
435.6 | 290.6 | 130.7239 | 1.1018 | 435.6 | 290.6 | 129.6182 | 0.11392 | 435.6 | 290.6 | 130.9083 | 0.099605 | 435.6 | 290.6 | 127.0709
435.8 | 290.8 | 130.628 | 1.0058 | 435.8 | 290.8 | 129.6182 | 0.11392 | 435.8 | 290.8 | 130.9083 | 0.1956 | 435.8 | 290.8 | 126.9749
436 | 291 | 130.628 | 1.0058 | 436 | 291 | 129.5222 | 0.017929 | 436 | 291 | 130.9083 | 0.1956 | 436 | 291 | 127.0709
436.2 | 291.2 | 130.628 | 1.0058 | 436.2 | 291.2 | 129.5222 | 0.017929 | 436.2 | 291.2 | 130.9083 | 0.1956 | 436.2 | 291.2 | 127.0709
436.4 | 291.4 | 130.628 | 1.0058 | 436.4 | 291.4 | 129.6182 | 0.11392 | 436.4 | 291.4 | 130.9083 | 0.1956 | 436.4 | 291.4 | 127.0709
436.6 | 291.6 | 130.7239 | 1.0058 | 436.6 | 291.6 | 129.6182 | 0.11392 | 436.6 | 291.6 | 131.0042 | 0.1956 | 436.6 | 291.6 | 126.9749
436.8 | 291.8 | 130.7239 | 1.0058 | 436.8 | 291.8 | 129.5222 | 0.017929 | 436.8 | 291.8 | 130.9083 | 0.1956 | 436.8 | 291.8 | 127.0709
437 | 292 | 130.7239 | 1.0058 | 437 | 292 | 129.5222 | 0.017929 | 437 | 292 | 130.9083 | 0.1956 | 437 | 292 | 127.0709
437.2 | 292.2 | 130.628 | 1.1018 | 437.2 | 292.2 | 129.5222 | 0.017929 | 437.2 | 292.2 | 130.8123 | 0.1956 | 437.2 | 292.2 | 126.9749
437.4 | 292.4 | 130.628 | 1.0058 | 437.4 | 292.4 | 129.5222 | 0.017929 | 437.4 | 292.4 | 130.9083 | 0.1956 | 437.4 | 292.4 | 127.0709
437.6 | 292.6 | 130.628 | 1.0058 | 437.6 | 292.6 | 129.5222 | 0.017929 | 437.6 | 292.6 | 130.8123 | 0.1956 | 437.6 | 292.6 | 126.879
437.8 | 292.8 | 130.7239 | 1.1018 | 437.8 | 292.8 | 129.6182 | 0.017929 | 437.8 | 292.8 | 131.0042 | 0.099605 | 437.8 | 292.8 | 127.0709
438 | 293 | 130.628 | 1.1018 | 438 | 293 | 129.4263 | 0.017929 | 438 | 293 | 130.8123 | 0.1956 | 438 | 293 | 126.9749
438.2 | 293.2 | 130.628 | 1.1018 | 438.2 | 293.2 | 129.5222 | 0.017929 | 438.2 | 293.2 | 130.8123 | 0.1956 | 438.2 | 293.2 | 126.879
438.4 | 293.4 | 130.628 | 1.0058 | 438.4 | 293.4 | 129.4263 | 0.017929 | 438.4 | 293.4 | 130.9083 | 0.1956 | 438.4 | 293.4 | 126.9749
438.6 | 293.6 | 130.628 | 1.1018 | 438.6 | 293.6 | 129.4263 | 0.017929 | 438.6 | 293.6 | 130.8123 | 0.1956 | 438.6 | 293.6 | 126.9749
438.8 | 293.8 | 130.628 | 1.1978 | 438.8 | 293.8 | 129.5222 | 0.11392 | 438.8 | 293.8 | 130.9083 | 0.1956 | 438.8 | 293.8 | 126.9749
439 | 294 | 130.628 | 1.0058 | 439 | 294 | 129.4263 | 0.017929 | 439 | 294 | 130.8123 | 0.1956 | 439 | 294 | 126.9749
439.2 | 294.2 | 130.532 | 1.0058 | 439.2 | 294.2 | 129.4263 | 0.11392 | 439.2 | 294.2 | 130.8123 | 0.1956 | 439.2 | 294.2 | 126.9749
439.4 | 294.4 | 130.532 | 1.0058 | 439.4 | 294.4 | 129.4263 | 0.017929 | 439.4 | 294.4 | 130.9083 | 0.1956 | 439.4 | 294.4 | 126.9749
439.6 | 294.6 | 130.532 | 1.0058 | 439.6 | 294.6 | 129.3303 | 0.017929 | 439.6 | 294.6 | 130.8123 | 0.1956 | 439.6 | 294.6 | 126.879
439.8 | 294.8 | 130.532 | 1.0058 | 439.8 | 294.8 | 129.4263 | 0.017929 | 439.8 | 294.8 | 130.9083 | 0.1956 | 439.8 | 294.8 | 126.9749
440 | 295 | 130.532 | 0.90985 | 440 | 295 | 129.4263 | 0.017929 | 440 | 295 | 130.8123 | 0.1956 | 440 | 295 | 126.9749
440.2 | 295.2 | 130.4361 | 1.0058 | 440.2 | 295.2 | 129.5222 | 0.11392 | 440.2 | 295.2 | 130.9083 | 0.1956 | 440.2 | 295.2 | 127.0709
440.4 | 295.4 | 130.4361 | 1.0058 | 440.4 | 295.4 | 129.4263 | 0.017929 | 440.4 | 295.4 | 130.9083 | 0.1956 | 440.4 | 295.4 | 126.9749
440.6 | 295.6 | 130.4361 | 0.90985 | 440.6 | 295.6 | 129.4263 | 0.017929 | 440.6 | 295.6 | 130.8123 | 0.1956 | 440.6 | 295.6 | 126.9749
440.8 | 295.8 | 130.4361 | 1.0058 | 440.8 | 295.8 | 129.4263 | 0.11392 | 440.8 | 295.8 | 130.9083 | 0.29155 | 440.8 | 295.8 | 126.9749
441 | 296 | 130.4361 | 0.90985 | 441 | 296 | 129.4263 | 0.11392 | 441 | 296 | 130.8123 | 0.1956 | 441 | 296 | 126.9749
441.2 | 296.2 | 130.4361 | 0.8139 | 441.2 | 296.2 | 129.4263 | 0.017929 | 441.2 | 296.2 | 130.8123 | 0.1956 | 441.2 | 296.2 | 126.9749
441.4 | 296.4 | 130.4361 | 0.90985 | 441.4 | 296.4 | 129.4263 | 0.017929 | 441.4 | 296.4 | 130.8123 | 0.1956 | 441.4 | 296.4 | 126.9749
441.6 | 296.6 | 130.4361 | 0.90985 | 441.6 | 296.6 | 129.4263 | 0.017929 | 441.6 | 296.6 | 130.8123 | 0.1956 | 441.6 | 296.6 | 126.9749
441.8 | 296.8 | 130.3401 | 0.8139 | 441.8 | 296.8 | 129.4263 | 0.11392 | 441.8 | 296.8 | 130.8123 | 0.1956 | 441.8 | 296.8 | 126.9749
442 | 297 | 130.3401 | 0.90985 | 442 | 297 | 129.3303 | 0.017929 | 442 | 297 | 130.7164 | 0.099605 | 442 | 297 | 126.879
442.2 | 297.2 | 130.3401 | 0.8139 | 442.2 | 297.2 | 129.4263 | 0.017929 | 442.2 | 297.2 | 130.8123 | 0.1956 | 442.2 | 297.2 | 126.9749
442.4 | 297.4 | 130.3401 | 0.8139 | 442.4 | 297.4 | 129.3303 | 0.017929 | 442.4 | 297.4 | 130.7164 | 0.099605 | 442.4 | 297.4 | 126.879
442.6 | 297.6 | 130.3401 | 0.8139 | 442.6 | 297.6 | 129.3303 | 0.017929 | 442.6 | 297.6 | 130.8123 | 0.1956 | 442.6 | 297.6 | 126.9749
442.8 | 297.8 | 130.3401 | 0.8139 | 442.8 | 297.8 | 129.3303 | 0.017929 | 442.8 | 297.8 | 130.8123 | 0.1956 | 442.8 | 297.8 | 126.879
443 | 298 | 130.3401 | 0.8139 | 443 | 298 | 129.3303 | 0.017929 | 443 | 298 | 130.8123 | 0.099605 | 443 | 298 | 126.879
443.2 | 298.2 | 130.2441 | 0.8139 | 443.2 | 298.2 | 129.3303 | 0.11392 | 443.2 | 298.2 | 130.8123 | 0.1956 | 443.2 | 298.2 | 126.879
443.4 | 298.4 | 130.2441 | 0.8139 | 443.4 | 298.4 | 129.2343 | 0.11392 | 443.4 | 298.4 | 130.8123 | 0.1956 | 443.4 | 298.4 | 126.879
443.6 | 298.6 | 130.2441 | 0.8139 | 443.6 | 298.6 | 129.3303 | 0.017929 | 443.6 | 298.6 | 130.8123 | 0.1956 | 443.6 | 298.6 | 126.879
443.8 | 298.8 | 130.1482 | 0.8139 | 443.8 | 298.8 | 129.1384 | 0.017929 | 443.8 | 298.8 | 130.7164 | 0.1956 | 443.8 | 298.8 | 126.783
444 | 299 | 130.0522 | 0.8139 | 444 | 299 | 129.1384 | 0.017929 | 444 | 299 | 130.7164 | 0.1956 | 444 | 299 | 126.783
444.2 | 299.2 | 130.1482 | 0.71795 | 444.2 | 299.2 | 129.2343 | 0.017929 | 444.2 | 299.2 | 130.7164 | 0.1956 | 444.2 | 299.2 | 126.783
444.4 | 299.4 | 130.1482 | 0.71795 | 444.4 | 299.4 | 129.2343 | 0.017929 | 444.4 | 299.4 | 130.7164 | 0.1956 | 444.4 | 299.4 | 126.783
444.6 | 299.6 | 130.0522 | 0.71795 | 444.6 | 299.6 | 129.2343 | 0.11392 | 444.6 | 299.6 | 130.7164 | 0.1956 | 444.6 | 299.6 | 126.783
444.8 | 299.8 | 130.0522 | 0.71795 | 444.8 | 299.8 | 129.1384 | 0.11392 | 444.8 | 299.8 | 130.7164 | 0.1956 | 444.8 | 299.8 | 126.879
445 | 300 | 130.0522 | 0.71795 | 445 | 300 | 129.2343 | 0.11392 | 445 | 300 | 130.7164 | 0.1956 | 445 | 300 | 126.879
445.2 | 300.2 | 129.9562 | 0.62195 | 445.2 | 300.2 | 129.1384 | 0.017929 | 445.2 | 300.2 | 130.7164 | 0.1956 | 445.2 | 300.2 | 126.783
445.4 | 300.4 | 129.8603 | 0.62195 | 445.4 | 300.4 | 129.1384 | 0.017929 | 445.4 | 300.4 | 130.6204 | 0.1956 | 445.4 | 300.4 | 126.783
445.6 | 300.6 | 129.8603 | 0.62195 | 445.6 | 300.6 | 129.1384 | 0.017929 | 445.6 | 300.6 | 130.7164 | 0.1956 | 445.6 | 300.6 | 126.783
445.8 | 300.8 | 129.9562 | 0.62195 | 445.8 | 300.8 | 129.1384 | 0.11392 | 445.8 | 300.8 | 130.7164 | 0.1956 | 445.8 | 300.8 | 126.783
446 | 301 | 129.8603 | 0.526 | 446 | 301 | 129.1384 | 0.017929 | 446 | 301 | 130.6204 | 0.1956 | 446 | 301 | 126.783
446.2 | 301.2 | 129.8603 | 0.526 | 446.2 | 301.2 | 129.1384 | 0.017929 | 446.2 | 301.2 | 130.6204 | 0.099605 | 446.2 | 301.2 | 126.783
446.4 | 301.4 | 129.8603 | 0.526 | 446.4 | 301.4 | 129.0424 | 0.017929 | 446.4 | 301.4 | 130.7164 | 0.1956 | 446.4 | 301.4 | 126.783
446.6 | 301.6 | 129.5724 | 0.526 | 446.6 | 301.6 | 128.8504 | 0.017929 | 446.6 | 301.6 | 130.4284 | 0.099605 | 446.6 | 301.6 | 126.5911
446.8 | 301.8 | 129.2844 | 0.43001 | 446.8 | 301.8 | 128.5625 | 0.017929 | 446.8 | 301.8 | 130.2365 | 0.1956 | 446.8 | 301.8 | 126.3991
447 | 302 | 129.3804 | 0.43001 | 447 | 302 | 128.5625 | 0.017929 | 447 | 302 | 130.2365 | 0.1956 | 447 | 302 | 126.3991
447.2 | 302.2 | 129.5724 | 0.43001 | 447.2 | 302.2 | 128.7545 | 0.017929 | 447.2 | 302.2 | 130.4284 | 0.1956 | 447.2 | 302.2 | 126.5911
447.4 | 302.4 | 129.4764 | 0.526 | 447.4 | 302.4 | 128.9464 | 0.20987 | 447.4 | 302.4 | 130.5244 | 0.29155 | 447.4 | 302.4 | 126.687
447.6 | 302.6 | 129.5724 | 0.33406 | 447.6 | 302.6 | 128.8504 | -0.078023 | 447.6 | 302.6 | 130.5244 | 0.1956 | 447.6 | 302.6 | 126.5911
447.8 | 302.8 | 129.5724 | 0.33406 | 447.8 | 302.8 | 128.7545 | 0.11392 | 447.8 | 302.8 | 130.5244 | 0.1956 | 447.8 | 302.8 | 126.5911
448 | 303 | 129.3804 | 0.43001 | 448 | 303 | 128.6585 | 0.017929 | 448 | 303 | 130.4284 | 0.1956 | 448 | 303 | 126.5911
448.2 | 303.2 | 129.3804 | 0.33406 | 448.2 | 303.2 | 128.6585 | 0.11392 | 448.2 | 303.2 | 130.5244 | 0.1956 | 448.2 | 303.2 | 126.5911
448.4 | 303.4 | 129.4764 | 0.23811 | 448.4 | 303.4 | 128.4666 | 0.017929 | 448.4 | 303.4 | 130.4284 | 0.1956 | 448.4 | 303.4 | 126.687
448.6 | 303.6 | 129.4764 | 0.33406 | 448.6 | 303.6 | 128.3706 | 0.017929 | 448.6 | 303.6 | 130.4284 | 0.1956 | 448.6 | 303.6 | 126.5911
448.8 | 303.8 | 129.4764 | 0.33406 | 448.8 | 303.8 | 127.9867 | 0.017929 | 448.8 | 303.8 | 130.4284 | 0.1956 | 448.8 | 303.8 | 126.5911
449 | 304 | 129.2844 | 0.33406 | 449 | 304 | 127.6029 | 0.017929 | 449 | 304 | 130.3325 | 0.29155 | 449 | 304 | 126.3991
449.2 | 304.2 | 129.2844 | 0.23811 | 449.2 | 304.2 | 127.315 | 0.017929 | 449.2 | 304.2 | 130.3325 | 0.1956 | 449.2 | 304.2 | 126.3991
449.4 | 304.4 | 129.2844 | 0.23811 | 449.4 | 304.4 | 126.9311 | 0.017929 | 449.4 | 304.4 | 130.3325 | 0.1956 | 449.4 | 304.4 | 126.3991
449.6 | 304.6 | 129.3804 | 0.23811 | 449.6 | 304.6 | 128.1787 | 0.017929 | 449.6 | 304.6 | 130.4284 | 0.1956 | 449.6 | 304.6 | 126.4951
449.8 | 304.8 | 129.2844 | 0.23811 | 449.8 | 304.8 | 127.8908 | 0.017929 | 449.8 | 304.8 | 130.4284 | 0.1956 | 449.8 | 304.8 | 126.4951
450 | 305 | 129.1885 | 0.23811 | 450 | 305 | 127.0271 | 0.017929 | 450 | 305 | 130.2365 | 0.1956 | 450 | 305 | 126.3991
450.2 | 305.2 | 129.1885 | 0.14212 | 450.2 | 305.2 | 126.7391 | 0.017929 | 450.2 | 305.2 | 130.3325 | 0.1956 | 450.2 | 305.2 | 126.3991
450.4 | 305.4 | 129.0925 | 0.23811 | 450.4 | 305.4 | 126.3553 | 0.017929 | 450.4 | 305.4 | 130.3325 | 0.1956 | 450.4 | 305.4 | 126.3032
450.6 | 305.6 | 129.0925 | 0.23811 | 450.6 | 305.6 | 126.2593 | 0.017929 | 450.6 | 305.6 | 130.3325 | 0.1956 | 450.6 | 305.6 | 126.3032
450.8 | 305.8 | 129.0925 | 0.23811 | 450.8 | 305.8 | 126.0674 | 0.017929 | 450.8 | 305.8 | 130.2365 | 0.099605 | 450.8 | 305.8 | 126.3991
451 | 306 | 128.9966 | 0.23811 | 451 | 306 | 125.7795 | 0.017929 | 451 | 306 | 130.1405 | 0.1956 | 451 | 306 | 126.2072
451.2 | 306.2 | 128.9966 | 0.14212 | 451.2 | 306.2 | 125.3956 | 0.017929 | 451.2 | 306.2 | 130.1405 | 0.099605 | 451.2 | 306.2 | 126.3032
451.4 | 306.4 | 128.9966 | 0.23811 | 451.4 | 306.4 | 125.1077 | 0.017929 | 451.4 | 306.4 | 130.1405 | 0.1956 | 451.4 | 306.4 | 126.3032
451.6 | 306.6 | 129.0925 | 0.23811 | 451.6 | 306.6 | 127.219 | 0.017929 | 451.6 | 306.6 | 130.4284 | 0.1956 | 451.6 | 306.6 | 126.3991
451.8 | 306.8 | 129.2844 | 0.23811 | 451.8 | 306.8 | 128.4666 | 0.017929 | 451.8 | 306.8 | 130.4284 | 0.1956 | 451.8 | 306.8 | 126.5911
452 | 307 | 129.2844 | 0.14212 | 452 | 307 | 128.1787 | 0.017929 | 452 | 307 | 130.4284 | 0.1956 | 452 | 307 | 126.4951
452.2 | 307.2 | 129.2844 | 0.14212 | 452.2 | 307.2 | 128.1787 | 0.017929 | 452.2 | 307.2 | 130.4284 | 0.1956 | 452.2 | 307.2 | 126.5911
452.4 | 307.4 | 129.2844 | 0.43001 | 452.4 | 307.4 | 127.123 | 0.017929 | 452.4 | 307.4 | 130.3325 | 0.1956 | 452.4 | 307.4 | 126.3032
452.6 | 307.6 | 129.1885 | 0.23811 | 452.6 | 307.6 | 128.0827 | 0.017929 | 452.6 | 307.6 | 130.4284 | 0.1956 | 452.6 | 307.6 | 126.5911
452.8 | 307.8 | 129.1885 | 0.14212 | 452.8 | 307.8 | 128.0827 | 0.017929 | 452.8 | 307.8 | 130.4284 | 0.1956 | 452.8 | 307.8 | 126.4951
453 | 308 | 129.1885 | 0.23811 | 453 | 308 | 128.0827 | 0.017929 | 453 | 308 | 130.4284 | 0.1956 | 453 | 308 | 126.4951
453.2 | 308.2 | 129.2844 | 0.23811 | 453.2 | 308.2 | 128.3706 | 0.017929 | 453.2 | 308.2 | 130.5244 | 0.1956 | 453.2 | 308.2 | 126.5911
453.4 | 308.4 | 129.1885 | 0.23811 | 453.4 | 308.4 | 128.0827 | 0.017929 | 453.4 | 308.4 | 130.4284 | 0.1956 | 453.4 | 308.4 | 126.5911
453.6 | 308.6 | 129.1885 | 0.23811 | 453.6 | 308.6 | 128.0827 | 0.017929 | 453.6 | 308.6 | 130.5244 | 0.1956 | 453.6 | 308.6 | 126.5911
453.8 | 308.8 | 129.1885 | 0.23811 | 453.8 | 308.8 | 128.1787 | 0.017929 | 453.8 | 308.8 | 130.5244 | 0.099605 | 453.8 | 308.8 | 126.4951
454 | 309 | 128.9966 | 0.23811 | 454 | 309 | 126.9311 | 0.017929 | 454 | 309 | 130.4284 | 0.1956 | 454 | 309 | 126.3991
454.2 | 309.2 | 128.9966 | 0.23811 | 454.2 | 309.2 | 127.5069 | 0.017929 | 454.2 | 309.2 | 130.4284 | 0.1956 | 454.2 | 309.2 | 126.4951
454.4 | 309.4 | 128.9966 | 0.14212 | 454.4 | 309.4 | 127.123 | 0.017929 | 454.4 | 309.4 | 130.4284 | 0.1956 | 454.4 | 309.4 | 126.4951
454.6 | 309.6 | 128.8046 | 0.046168 | 454.6 | 309.6 | 126.4513 | 0.017929 | 454.6 | 309.6 | 130.3325 | 0.099605 | 454.6 | 309.6 | 126.3991
454.8 | 309.8 | 128.9966 | 0.33406 | 454.8 | 309.8 | 127.123 | 0.017929 | 454.8 | 309.8 | 130.4284 | 0.1956 | 454.8 | 309.8 | 126.3991
455 | 310 | 128.9006 | 0.14212 | 455 | 310 | 126.2593 | -0.078023 | 455 | 310 | 130.4284 | 0.003654 | 455 | 310 | 126.3032
455.2 | 310.2 | 128.9006 | 0.23811 | 455.2 | 310.2 | 126.5472 | 0.11392 | 455.2 | 310.2 | 130.5244 | 0.29155 | 455.2 | 310.2 | 126.3991
455.4 | 310.4 | 128.9006 | 0.14212 | 455.4 | 310.4 | 126.5472 | -0.078023 | 455.4 | 310.4 | 130.3325 | 0.099605 | 455.4 | 310.4 | 126.3991
455.6 | 310.6 | 128.9966 | 0.23811 | 455.6 | 310.6 | 127.5069 | 0.017929 | 455.6 | 310.6 | 130.5244 | 2.1149 | 455.6 | 310.6 | 126.5911
455.8 | 310.8 | 128.9966 | 0.23811 | 455.8 | 310.8 | 127.7948 | 0.017929 | 455.8 | 310.8 | 130.5244 | 0.1956 | 455.8 | 310.8 | 126.5911
456 | 311 | 128.9006 | 0.23811 | 456 | 311 | 127.123 | 0.017929 | 456 | 311 | 130.4284 | 0.1956 | 456 | 311 | 126.5911
456.2 | 311.2 | 128.9006 | 0.14212 | 456.2 | 311.2 | 127.4109 | 0.11392 | 456.2 | 311.2 | 130.7164 | 0.1956 | 456.2 | 311.2 | 126.4951
456.4 | 311.4 | 128.9006 | 0.14212 | 456.4 | 311.4 | 126.2593 | 0.017929 | 456.4 | 311.4 | 130.4284 | 0.1956 | 456.4 | 311.4 | 126.4951
456.6 | 311.6 | 128.8046 | 0.23811 | 456.6 | 311.6 | 126.2593 | 23.9138 | 456.6 | 311.6 | 130.4284 | 0.1956 | 456.6 | 311.6 | 126.4951
456.8 | 311.8 | 128.9966 | 0.23811 | 456.8 | 311.8 | 128.8504 | 3.7607 | 456.8 | 311.8 | 130.6204 | 0.1956 | 456.8 | 311.8 | 126.687
457 | 312 | 128.9006 | 0.33406 | 457 | 312 | 127.123 | 26.6968 | 457 | 312 | 130.5244 | 0.3875 | 457 | 312 | 126.687
457.2 | 312.2 | 128.9006 | 0.23811 | 457.2 | 312.2 | 127.8908 | 13.8372 | 457.2 | 312.2 | 130.5244 | 0.1956 | 457.2 | 312.2 | 126.5911
457.4 | 312.4 | 128.9966 | 0.23811 | 457.4 | 312.4 | 128.9464 | 2.1292 | 457.4 | 312.4 | 130.6204 | 0.1956 | 457.4 | 312.4 | 126.687
457.6 | 312.6 | 128.9966 | 0.23811 | 457.6 | 312.6 | 129.0424 | 0.78566 | 457.6 | 312.6 | 130.6204 | 0.1956 | 457.6 | 312.6 | 126.783
457.8 | 312.8 | 128.9966 | 0.23811 | 457.8 | 312.8 | 129.0424 | 0.49776 | 457.8 | 312.8 | 130.7164 | 0.1956 | 457.8 | 312.8 | 126.783
458 | 313 | 128.9006 | 0.23811 | 458 | 313 | 128.6585 | 0.40181 | 458 | 313 | 130.5244 | 0.1956 | 458 | 313 | 126.687
458.2 | 313.2 | 128.8046 | 0.23811 | 458.2 | 313.2 | 127.9867 | 1.0736 | 458.2 | 313.2 | 130.5244 | 0.1956 | 458.2 | 313.2 | 126.5911
458.4 | 313.4 | 128.8046 | 0.23811 | 458.4 | 313.4 | 127.6988 | 2.2252 | 458.4 | 313.4 | 130.5244 | 0.099605 | 458.4 | 313.4 | 126.5911
458.6 | 313.6 | 128.8046 | 0.23811 | 458.6 | 313.6 | 127.5069 | 3.0889 | 458.6 | 313.6 | 130.5244 | 0.1956 | 458.6 | 313.6 | 126.687
458.8 | 313.8 | 128.8046 | 0.23811 | 458.8 | 313.8 | 127.315 | 3.4728 | 458.8 | 313.8 | 130.5244 | 0.1956 | 458.8 | 313.8 | 126.5911
459 | 314 | 128.8046 | 0.23811 | 459 | 314 | 127.123 | 3.7607 | 459 | 314 | 130.5244 | 0.1956 | 459 | 314 | 126.5911
459.2 | 314.2 | 128.8046 | 0.23811 | 459.2 | 314.2 | 126.9311 | 3.7607 | 459.2 | 314.2 | 130.5244 | 0.1956 | 459.2 | 314.2 | 126.5911
459.4 | 314.4 | 128.8046 | 0.23811 | 459.4 | 314.4 | 126.7391 | 3.9526 | 459.4 | 314.4 | 130.5244 | 0.099605 | 459.4 | 314.4 | 126.5911
459.6 | 314.6 | 128.8046 | 0.23811 | 459.6 | 314.6 | 126.5472 | 4.3364 | 459.6 | 314.6 | 130.4284 | 0.1956 | 459.6 | 314.6 | 126.5911
459.8 | 314.8 | 128.8046 | 0.14212 | 459.8 | 314.8 | 126.3553 | 4.5284 | 459.8 | 314.8 | 130.5244 | 0.1956 | 459.8 | 314.8 | 126.5911
460 | 315 | 128.8046 | 0.23811 | 460 | 315 | 126.1634 | 4.8163 | 460 | 315 | 130.4284 | 0.099605 | 460 | 315 | 126.4951
460.2 | 315.2 | 128.8046 | 0.33406 | 460.2 | 315.2 | 125.9714 | 4.9123 | 460.2 | 315.2 | 130.5244 | 0.099605 | 460.2 | 315.2 | 126.4951
460.4 | 315.4 | 128.7087 | 0.23811 | 460.4 | 315.4 | 125.7795 | 5.1042 | 460.4 | 315.4 | 130.3325 | 0.1956 | 460.4 | 315.4 | 126.4951
460.6 | 315.6 | 128.7087 | 0.23811 | 460.6 | 315.6 | 125.4916 | 5.1042 | 460.6 | 315.6 | 130.4284 | 0.1956 | 460.6 | 315.6 | 126.4951
460.8 | 315.8 | 128.7087 | 0.23811 | 460.8 | 315.8 | 125.3956 | 5.2962 | 460.8 | 315.8 | 130.4284 | 0.099605 | 460.8 | 315.8 | 126.4951
461 | 316 | 128.7087 | 0.23811 | 461 | 316 | 125.1077 | 5.2962 | 461 | 316 | 130.4284 | 0.1956 | 461 | 316 | 126.4951
461.2 | 316.2 | 128.7087 | 0.23811 | 461.2 | 316.2 | 125.0117 | 5.4881 | 461.2 | 316.2 | 130.4284 | 0.1956 | 461.2 | 316.2 | 126.4951
461.4 | 316.4 | 128.7087 | 0.43001 | 461.4 | 316.4 | 125.2996 | 4.8163 | 461.4 | 316.4 | 130.4284 | 0.3875 | 461.4 | 316.4 | 126.4951
461.6 | 316.6 | 128.7087 | 0.23811 | 461.6 | 316.6 | 125.7795 | 4.6244 | 461.6 | 316.6 | 130.5244 | 0.1956 | 461.6 | 316.6 | 126.4951
461.8 | 316.8 | 128.6127 | 0.43001 | 461.8 | 316.8 | 125.6835 | 4.4324 | 461.8 | 316.8 | 130.6204 | 0.1956 | 461.8 | 316.8 | 126.4951
462 | 317 | 128.7087 | 0.33406 | 462 | 317 | 125.8755 | 4.3364 | 462 | 317 | 130.4284 | 0.3875 | 462 | 317 | 126.783
462.2 | 317.2 | 128.9966 | 0.23811 | 462.2 | 317.2 | 127.5069 | 2.9929 | 462.2 | 317.2 | 130.6204 | 0.1956 | 462.2 | 317.2 | 126.687
462.4 | 317.4 | 128.9966 | 0.23811 | 462.4 | 317.4 | 128.8504 | 0.9776 | 462.4 | 317.4 | 130.8123 | 0.1956 | 462.4 | 317.4 | 126.879
462.6 | 317.6 | 128.9006 | 0.14212 | 462.6 | 317.6 | 128.1787 | 0.78566 | 462.6 | 317.6 | 130.8123 | 0.1956 | 462.6 | 317.6 | 126.879
462.8 | 317.8 | 128.8046 | 0.23811 | 462.8 | 317.8 | 126.6432 | 2.5131 | 462.8 | 317.8 | 130.7164 | 0.1956 | 462.8 | 317.8 | 126.687
463 | 318 | 128.7087 | 0.046168 | 463 | 318 | 125.4916 | 3.7607 | 463 | 318 | 130.4284 | 0.099605 | 463 | 318 | 126.4951
463.2 | 318.2 | 128.7087 | 0.23811 | 463.2 | 318.2 | 125.2037 | 3.9526 | 463.2 | 318.2 | 130.4284 | 0.3875 | 463.2 | 318.2 | 126.5911
463.4 | 318.4 | 128.9006 | 0.23811 | 463.4 | 318.4 | 128.6585 | 1.3615 | 463.4 | 318.4 | 130.7164 | 0.1956 | 463.4 | 318.4 | 126.783
463.6 | 318.6 | 128.9966 | 0.23811 | 463.6 | 318.6 | 128.9464 | 0.78566 | 463.6 | 318.6 | 130.8123 | 0.1956 | 463.6 | 318.6 | 126.879
463.8 | 318.8 | 128.9006 | 0.23811 | 463.8 | 318.8 | 128.9464 | 0.59375 | 463.8 | 318.8 | 130.8123 | 0.1956 | 463.8 | 318.8 | 126.879
464 | 319 | 128.9006 | 0.23811 | 464 | 319 | 129.0424 | 0.68971 | 464 | 319 | 130.8123 | 0.1956 | 464 | 319 | 126.879
464.2 | 319.2 | 128.9006 | 0.23811 | 464.2 | 319.2 | 128.7545 | 8.2711 | 464.2 | 319.2 | 130.8123 | 0.099605 | 464.2 | 319.2 | 126.879
464.4 | 319.4 | 128.9006 | 0.23811 | 464.4 | 319.4 | 128.3706 | 12.8776 | 464.4 | 319.4 | 130.8123 | 0.1956 | 464.4 | 319.4 | 126.879
464.6 | 319.6 | 128.9006 | 0.23811 | 464.6 | 319.6 | 127.7948 | 18.3477 | 464.6 | 319.6 | 130.8123 | 0.1956 | 464.6 | 319.6 | 126.783
464.8 | 319.8 | 128.8046 | 0.23811 | 464.8 | 319.8 | 126.8351 | 27.1767 | 464.8 | 319.8 | 130.7164 | 0.1956 | 464.8 | 319.8 | 126.783
465 | 320 | 128.7087 | 0.14212 | 465 | 320 | 125.5876 | 34.8541 | 465 | 320 | 130.6204 | 0.1956 | 465 | 320 | 126.687
465.2 | 320.2 | 128.8046 | 0.23811 | 465.2 | 320.2 | 126.9311 | 27.9444 | 465.2 | 320.2 | 130.7164 | 0.099605 | 465.2 | 320.2 | 126.783
465.4 | 320.4 | 128.8046 | 0.23811 | 465.4 | 320.4 | 127.0271 | 22.7622 | 465.4 | 320.4 | 130.7164 | 0.099605 | 465.4 | 320.4 | 126.687
465.6 | 320.6 | 128.8046 | 0.23811 | 465.6 | 320.6 | 127.123 | 21.4186 | 465.6 | 320.6 | 130.6204 | 0.29155 | 465.6 | 320.6 | 126.687
465.8 | 320.8 | 128.8046 | 0.23811 | 465.8 | 320.8 | 126.7391 | 20.7469 | 465.8 | 320.8 | 130.6204 | 0.1956 | 465.8 | 320.8 | 126.687
466 | 321 | 128.7087 | 0.23811 | 466 | 321 | 126.1634 | 27.4645 | 466 | 321 | 130.6204 | 0.1956 | 466 | 321 | 126.687
466.2 | 321.2 | 128.6127 | 0.23811 | 466.2 | 321.2 | 125.7795 | 33.0307 | 466.2 | 321.2 | 130.6204 | 0.099605 | 466.2 | 321.2 | 126.5911
466.4 | 321.4 | 128.7087 | 0.23811 | 466.4 | 321.4 | 125.5876 | 31.4952 | 466.4 | 321.4 | 130.5244 | 0.1956 | 466.4 | 321.4 | 126.687
466.6 | 321.6 | 128.4208 | 0.23811 | 466.6 | 321.6 | 122.9005 | 48.7693 | 466.6 | 321.6 | 130.3325 | 0.099605 | 466.6 | 321.6 | 126.3991
466.8 | 321.8 | 128.2288 | 0.23811 | 466.8 | 321.8 | 121.269 | 55.7749 | 466.8 | 321.8 | 130.1405 | 0.1956 | 466.8 | 321.8 | 126.2072
467 | 322 | 128.2288 | 0.14212 | 467 | 322 | 120.6932 | 65.3716 | 467 | 322 | 130.1405 | 0.099605 | 467 | 322 | 126.2072
467.2 | 322.2 | 128.1329 | 0.23811 | 467.2 | 322.2 | 120.8852 | 74.8724 | 467.2 | 322.2 | 130.1405 | 0.1956 | 467.2 | 322.2 | 126.2072
467.4 | 322.4 | 128.3248 | 0.23811 | 467.4 | 322.4 | 122.0368 | 85.3328 | 467.4 | 322.4 | 130.3325 | 0.1956 | 467.4 | 322.4 | 126.3991
467.6 | 322.6 | 128.5167 | 0.14212 | 467.6 | 322.6 | 123.4763 | 95.6013 | 467.6 | 322.6 | 130.3325 | 0.29155 | 467.6 | 322.6 | 126.3032
467.8 | 322.8 | 128.4208 | 0.046168 | 467.8 | 322.8 | 122.4206 | 90.8989 | 467.8 | 322.8 | 130.3325 | 0.1956 | 467.8 | 322.8 | 126.4951
468 | 323 | 128.3248 | 0.23811 | 468 | 323 | 122.2287 | 91.7626 | 468 | 323 | 130.2365 | 0.1956 | 468 | 323 | 126.2072
468.2 | 323.2 | 128.3248 | 0.23811 | 468.2 | 323.2 | 121.8448 | 90.611 | 468.2 | 323.2 | 130.2365 | 0.1956 | 468.2 | 323.2 | 126.2072
468.4 | 323.4 | 128.6127 | 0.33406 | 468.4 | 323.4 | 123.8601 | 101.5513 | 468.4 | 323.4 | 130.4284 | 0.099605 | 468.4 | 323.4 | 126.5911
468.6 | 323.6 | 128.6127 | 0.23811 | 468.6 | 323.6 | 123.9561 | 101.9351 | 468.6 | 323.6 | 130.5244 | 0.099605 | 468.6 | 323.6 | 126.4951
468.8 | 323.8 | 128.7087 | 0.23811 | 468.8 | 323.8 | 124.5319 | 105.198 | 468.8 | 323.8 | 130.5244 | 0.1956 | 468.8 | 323.8 | 126.687
469 | 324 | 128.6127 | 0.23811 | 469 | 324 | 123.6682 | 101.2634 | 469 | 324 | 130.5244 | 0.099605 | 469 | 324 | 126.5911
469.2 | 324.2 | 128.4208 | 0.23811 | 469.2 | 324.2 | 123.0924 | 99.248 | 469.2 | 324.2 | 130.4284 | 0.1956 | 469.2 | 324.2 | 126.4951
469.4 | 324.4 | 128.1329 | 0.23811 | 469.4 | 324.4 | 118.7739 | 80.7264 | 469.4 | 324.4 | 129.9486 | 0.1956 | 469.4 | 324.4 | 126.1112
469.6 | 324.6 | 127.653 | 0.23811 | 469.6 | 324.6 | 113.4957 | 64.0281 | 469.6 | 324.6 | 129.5647 | 0.1956 | 469.6 | 324.6 | 125.6314
469.8 | 324.8 | 127.2692 | 0.14212 | 469.8 | 324.8 | 109.0812 | 47.1379 | 469.8 | 324.8 | 129.1809 | 0.099605 | 469.8 | 324.8 | 125.6314
470 | 325 | 127.2692 | 0.23811 | 470 | 325 | 110.6167 | 26.8888 | 470 | 325 | 129.2768 | 0.1956 | 470 | 325 | 125.3435
470.2 | 325.2 | 128.2288 | 0.23811 | 470.2 | 325.2 | 119.9255 | 11.9179 | 470.2 | 325.2 | 130.1405 | 0.1956 | 470.2 | 325.2 | 126.2072
470.4 | 325.4 | 128.9006 | 0.23811 | 470.4 | 325.4 | 126.8351 | 2.801 | 470.4 | 325.4 | 130.7164 | 0.1956 | 470.4 | 325.4 | 126.879
470.6 | 325.6 | 129.0925 | 0.23811 | 470.6 | 325.6 | 127.6029 | 1.8413 | 470.6 | 325.6 | 130.9083 | 0.1956 | 470.6 | 325.6 | 126.879
470.8 | 325.8 | 129.2844 | 0.23811 | 470.8 | 325.8 | 128.0827 | 0.88165 | 470.8 | 325.8 | 130.9083 | 0.1956 | 470.8 | 325.8 | 126.9749
471 | 326 | 129.4764 | 0.23811 | 471 | 326 | 127.4109 | 0.88165 | 471 | 326 | 130.8123 | 0.1956 | 471 | 326 | 126.879
471.2 | 326.2 | 129.5724 | 0.23811 | 471.2 | 326.2 | 126.2593 | 2.3212 | 471.2 | 326.2 | 130.7164 | 0.1956 | 471.2 | 326.2 | 126.783
471.4 | 326.4 | 129.0925 | 0.23811 | 471.4 | 326.4 | 126.1634 | 2.2252 | 471.4 | 326.4 | 130.7164 | 0.1956 | 471.4 | 326.4 | 126.783
471.6 | 326.6 | 129.7643 | 0.23811 | 471.6 | 326.6 | 126.2593 | 2.2252 | 471.6 | 326.6 | 130.7164 | 0.1956 | 471.6 | 326.6 | 126.687
471.8 | 326.8 | 129.6683 | 0.14212 | 471.8 | 326.8 | 125.4916 | 2.609 | 471.8 | 326.8 | 130.6204 | 0.1956 | 471.8 | 326.8 | 126.783
472 | 327 | 129.4764 | 0.23811 | 472 | 327 | 124.436 | 3.4728 | 472 | 327 | 130.5244 | 0.1956 | 472 | 327 | 126.687
472.2 | 327.2 | 129.4764 | 0.23811 | 472.2 | 327.2 | 124.0521 | 4.1445 | 472.2 | 327.2 | 130.5244 | 0.1956 | 472.2 | 327.2 | 126.687
472.4 | 327.4 | 129.3804 | 0.23811 | 472.4 | 327.4 | 123.9561 | 3.6647 | 472.4 | 327.4 | 130.5244 | 0.099605 | 472.4 | 327.4 | 126.5911
472.6 | 327.6 | 129.2844 | 0.14212 | 472.6 | 327.6 | 123.9561 | 4.0485 | 472.6 | 327.6 | 130.5244 | 0.1956 | 472.6 | 327.6 | 126.5911
472.8 | 327.8 | 129.1885 | 0.14212 | 472.8 | 327.8 | 124.436 | 3.8566 | 472.8 | 327.8 | 130.5244 | 0.1956 | 472.8 | 327.8 | 126.687
473 | 328 | 128.9966 | 0.23811 | 473 | 328 | 124.148 | 3.8566 | 473 | 328 | 130.4284 | 0.1956 | 473 | 328 | 126.687
473.2 | 328.2 | 128.9006 | 0.14212 | 473.2 | 328.2 | 123.8601 | 4.1445 | 473.2 | 328.2 | 130.5244 | 0.29155 | 473.2 | 328.2 | 126.687
473.4 | 328.4 | 128.7087 | 0.23811 | 473.4 | 328.4 | 123.3803 | 4.2405 | 473.4 | 328.4 | 130.3325 | 0.1956 | 473.4 | 328.4 | 126.5911
473.6 | 328.6 | 128.6127 | 0.23811 | 473.6 | 328.6 | 123.0924 | 4.4324 | 473.6 | 328.6 | 130.1405 | 0.1956 | 473.6 | 328.6 | 126.4951
473.8 | 328.8 | 128.5167 | 0.23811 | 473.8 | 328.8 | 122.8045 | 4.5284 | 473.8 | 328.8 | 129.8526 | 0.099605 | 473.8 | 328.8 | 126.4951
474 | 329 | 128.4208 | 0.23811 | 474 | 329 | 122.6126 | 4.5284 | 474 | 329 | 130.0446 | 0.1956 | 474 | 329 | 126.4951
474.2 | 329.2 | 128.4208 | 0.23811 | 474.2 | 329.2 | 122.4206 | 4.9123 | 474.2 | 329.2 | 130.1405 | 0.099605 | 474.2 | 329.2 | 126.3991
474.4 | 329.4 | 128.5167 | 0.23811 | 474.4 | 329.4 | 122.4206 | 4.9123 | 474.4 | 329.4 | 130.2365 | 0.1956 | 474.4 | 329.4 | 126.4951
474.6 | 329.6 | 128.5167 | 0.23811 | 474.6 | 329.6 | 122.3247 | 5.0082 | 474.6 | 329.6 | 130.3325 | 0.1956 | 474.6 | 329.6 | 126.3991
474.8 | 329.8 | 128.4208 | 0.23811 | 474.8 | 329.8 | 121.5569 | 5.4881 | 474.8 | 329.8 | 130.1405 | 0.099605 | 474.8 | 329.8 | 126.3032
475 | 330 | 128.4208 | 0.23811 | 475 | 330 | 121.5569 | 5.3921 | 475 | 330 | 130.2365 | 0.1956 | 475 | 330 | 126.2072
475.2 | 330.2 | 128.3248 | 0.23811 | 475.2 | 330.2 | 121.0771 | 5.4881 | 475.2 | 330.2 | 130.1405 | 0.29155 | 475.2 | 330.2 | 126.0153
475.4 | 330.4 | 128.2288 | 0.23811 | 475.4 | 330.4 | 120.2134 | 5.776 | 475.4 | 330.4 | 130.0446 | 0.099605 | 475.4 | 330.4 | 125.8233
475.6 | 330.6 | 128.3248 | 0.23811 | 475.6 | 330.6 | 120.8852 | 5.1042 | 475.6 | 330.6 | 130.1405 | 0.1956 | 475.6 | 330.6 | 125.6314
475.8 | 330.8 | 128.6127 | 0.23811 | 475.8 | 330.8 | 123.8601 | 2.8969 | 475.8 | 330.8 | 130.4284 | 0.099605 | 475.8 | 330.8 | 126.0153
476 | 331 | 128.7087 | 0.23811 | 476 | 331 | 125.4916 | 0.9776 | 476 | 331 | 130.5244 | 0.1956 | 476 | 331 | 126.3991
476.2 | 331.2 | 128.7087 | 0.526 | 476.2 | 331.2 | 124.9158 | 0.68971 | 476.2 | 331.2 | 130.4284 | 0.1956 | 476.2 | 331.2 | 126.3991
476.4 | 331.4 | 128.6127 | 0.62195 | 476.4 | 331.4 | 124.244 | 0.68971 | 476.4 | 331.4 | 130.5244 | 0.099605 | 476.4 | 331.4 | 126.4951
476.6 | 331.6 | 128.6127 | 0.8139 | 476.6 | 331.6 | 123.4763 | 0.9776 | 476.6 | 331.6 | 130.4284 | 0.099605 | 476.6 | 331.6 | 126.3032
476.8 | 331.8 | 128.4208 | 1.2937 | 476.8 | 331.8 | 122.2287 | 5.2962 | 476.8 | 331.8 | 130.3325 | 0.1956 | 476.8 | 331.8 | 126.2072
477 | 332 | 128.5167 | 2.0615 | 477 | 332 | 122.1327 | 3.6647 | 477 | 332 | 130.3325 | 0.1956 | 477 | 332 | 126.3032
477.2 | 332.2 | 128.5167 | 2.1574 | 477.2 | 332.2 | 122.8045 | 1.6494 | 477.2 | 332.2 | 130.4284 | 0.1956 | 477.2 | 332.2 | 126.3032
477.4 | 332.4 | 128.3248 | 2.0615 | 477.4 | 332.4 | 123.4763 | 1.2655 | 477.4 | 332.4 | 130.4284 | 0.1956 | 477.4 | 332.4 | 126.3991
477.6 | 332.6 | 128.6127 | 2.0615 | 477.6 | 332.6 | 123.4763 | 1.6494 | 477.6 | 332.6 | 130.4284 | 0.1956 | 477.6 | 332.6 | 126.3991
477.8 | 332.8 | 128.5167 | 2.4453 | 477.8 | 332.8 | 123.1884 | 3.0889 | 477.8 | 332.8 | 130.4284 | 0.1956 | 477.8 | 332.8 | 126.3991
478 | 333 | 128.4208 | 2.4453 | 478 | 333 | 121.8448 | 5.776 | 478 | 333 | 130.2365 | 0.1956 | 478 | 333 | 126.2072
478.2 | 333.2 | 128.3248 | 2.6373 | 478.2 | 333.2 | 120.9811 | 8.559 | 478.2 | 333.2 | 130.2365 | 0.29155 | 478.2 | 333.2 | 126.2072
478.4 | 333.4 | 128.2288 | 3.597 | 478.4 | 333.4 | 120.5972 | 12.5896 | 478.4 | 333.4 | 130.1405 | 0.1956 | 478.4 | 333.4 | 126.2072
478.6 | 333.6 | 128.1329 | 3.1171 | 478.6 | 333.6 | 120.5972 | 13.6453 | 478.6 | 333.6 | 130.1405 | 0.1956 | 478.6 | 333.6 | 126.2072
478.8 | 333.8 | 128.3248 | 1.8695 | 478.8 | 333.8 | 121.7489 | 9.3268 | 478.8 | 333.8 | 130.3325 | 0.1956 | 478.8 | 333.8 | 126.3032
479 | 334 | 128.4208 | 1.7736 | 479 | 334 | 122.2287 | 3.8566 | 479 | 334 | 130.3325 | 0.1956 | 479 | 334 | 126.3991
479.2 | 334.2 | 128.4208 | 1.6776 | 479.2 | 334.2 | 122.6126 | 2.1292 | 479.2 | 334.2 | 130.4284 | 0.1956 | 479.2 | 334.2 | 126.4951
479.4 | 334.4 | 128.8046 | 4.8445 | 479.4 | 334.4 | 124.244 | 0.9776 | 479.4 | 334.4 | 130.5244 | 0.1956 | 479.4 | 334.4 | 126.687
479.6 | 334.6 | 128.4208 | 4.0768 | 479.6 | 334.6 | 124.6279 | 0.68971 | 479.6 | 334.6 | 130.5244 | 0.1956 | 479.6 | 334.6 | 126.5911
479.8 | 334.8 | 128.6127 | 2.1574 | 479.8 | 334.8 | 125.2037 | 0.59375 | 479.8 | 334.8 | 130.6204 | 0.1956 | 479.8 | 334.8 | 126.687
480 | 335 | 128.6127 | 3.8848 | 480 | 335 | 124.8198 | 0.68971 | 480 | 335 | 130.6204 | 0.1956 | 480 | 335 | 126.5911
480.2 | 335.2 | 128.3248 | 6.9558 | 480.2 | 335.2 | 123.3803 | 1.7453 | 480.2 | 335.2 | 130.4284 | 0.099605 | 480.2 | 335.2 | 126.5911
480.4 | 335.4 | 128.3248 | 9.451 | 480.4 | 335.4 | 124.244 | 3.5687 | 480.4 | 335.4 | 130.5244 | 0.1956 | 480.4 | 335.4 | 126.5911
480.6 | 335.6 | 128.1329 | 13.7695 | 480.6 | 335.6 | 124.148 | 4.7203 | 480.6 | 335.6 | 130.4284 | 0.1956 | 480.6 | 335.6 | 126.5911
480.8 | 335.8 | 128.0369 | 13.6735 | 480.8 | 335.8 | 123.0924 | 5.3921 | 480.8 | 335.8 | 130.4284 | 0.1956 | 480.8 | 335.8 | 126.4951
481 | 336 | 127.749 | 11.6582 | 481 | 336 | 122.6126 | 5.68 | 481 | 336 | 130.3325 | 0.1956 | 481 | 336 | 126.4951
481.2 | 336.2 | 127.8449 | 11.4663 | 481.2 | 336.2 | 121.9408 | 5.8719 | 481.2 | 336.2 | 130.3325 | 0.1956 | 481.2 | 336.2 | 126.3991
481.4 | 336.4 | 127.8449 | 10.4106 | 481.4 | 336.4 | 121.365 | 6.1598 | 481.4 | 336.4 | 130.2365 | 0.1956 | 481.4 | 336.4 | 126.3032
481.6 | 336.6 | 127.9409 | 14.7291 | 481.6 | 336.6 | 123.1884 | 5.0082 | 481.6 | 336.6 | 130.3325 | 0.1956 | 481.6 | 336.6 | 126.4951
481.8 | 336.8 | 127.557 | 17.7041 | 481.8 | 336.8 | 121.8448 | 5.3921 | 481.8 | 336.8 | 130.2365 | 0.1956 | 481.8 | 336.8 | 126.3032
482 | 337 | 127.4611 | 19.6235 | 482 | 337 | 121.365 | 5.584 | 482 | 337 | 130.1405 | 0.1956 | 482 | 337 | 126.3032
482.2 | 337.2 | 127.4611 | 20.5832 | 482.2 | 337.2 | 120.2134 | 5.9679 | 482.2 | 337.2 | 130.1405 | 0.1956 | 482.2 | 337.2 | 126.2072
482.4 | 337.4 | 127.1732 | 21.9267 | 482.4 | 337.4 | 118.9658 | 6.6397 | 482.4 | 337.4 | 129.9486 | 0.1956 | 482.4 | 337.4 | 126.1112
482.6 | 337.6 | 126.5014 | 24.3259 | 482.6 | 337.6 | 116.0868 | 8.2711 | 482.6 | 337.6 | 129.6607 | 0.1956 | 482.6 | 337.6 | 125.8233
482.8 | 337.8 | 126.4054 | 26.7251 | 482.8 | 337.8 | 111.8642 | 8.655 | 482.8 | 337.8 | 129.3728 | 0.099605 | 482.8 | 337.8 | 125.4394
483 | 338 | 126.3095 | 28.9323 | 483 | 338 | 113.6876 | 8.655 | 483 | 338 | 129.4687 | 0.1956 | 483 | 338 | 125.5354
483.2 | 338.2 | 126.4054 | 31.0436 | 483.2 | 338.2 | 117.4303 | 5.9679 | 483.2 | 338.2 | 129.8526 | 0.1956 | 483.2 | 338.2 | 125.9193
483.4 | 338.4 | 126.5974 | 33.5387 | 483.4 | 338.4 | 118.7739 | 3.0889 | 483.4 | 338.4 | 129.8526 | 0.1956 | 483.4 | 338.4 | 126.0153
483.6 | 338.6 | 126.7893 | 35.1701 | 483.6 | 338.6 | 121.269 | 4.0485 | 483.6 | 338.6 | 130.1405 | 0.1956 | 483.6 | 338.6 | 126.2072
483.8 | 338.8 | 126.5974 | 37.2814 | 483.8 | 338.8 | 120.2134 | 6.7357 | 483.8 | 338.8 | 130.0446 | 0.1956 | 483.8 | 338.8 | 126.1112
484 | 339 | 126.6933 | 39.2968 | 484 | 339 | 122.3247 | 2.2252 | 484 | 339 | 130.1405 | 0.1956 | 484 | 339 | 126.3032
484.2 | 339.2 | 126.6933 | 41.408 | 484.2 | 339.2 | 123.4763 | 2.705 | 484.2 | 339.2 | 130.3325 | 0.1956 | 484.2 | 339.2 | 126.3991
484.4 | 339.4 | 126.5974 | 43.2314 | 484.4 | 339.4 | 122.2287 | 2.5131 | 484.4 | 339.4 | 130.2365 | 0.1956 | 484.4 | 339.4 | 126.3032
484.6 | 339.6 | 126.5974 | 45.0548 | 484.6 | 339.6 | 122.9005 | 1.7453 | 484.6 | 339.6 | 130.2365 | 0.1956 | 484.6 | 339.6 | 126.3991
484.8 | 339.8 | 126.2135 | 45.8225 | 484.8 | 339.8 | 120.2134 | 1.3615 | 484.8 | 339.8 | 129.9486 | 0.1956 | 484.8 | 339.8 | 126.2072
485 | 340 | 126.5014 | 47.5499 | 485 | 340 | 123.0924 | 1.1695 | 485 | 340 | 130.2365 | 0.1956 | 485 | 340 | 126.3032
485.2 | 340.2 | 126.3095 | 48.9894 | 485.2 | 340.2 | 122.9965 | 1.1695 | 485.2 | 340.2 | 130.1405 | 0.29155 | 485.2 | 340.2 | 126.2072
485.4 | 340.4 | 126.2135 | 50.237 | 485.4 | 340.4 | 122.8045 | 1.5534 | 485.4 | 340.4 | 130.2365 | 0.099605 | 485.4 | 340.4 | 126.3032
485.6 | 340.6 | 126.0216 | 50.9088 | 485.6 | 340.6 | 120.3094 | 4.4324 | 485.6 | 340.6 | 130.1405 | 0.29155 | 485.6 | 340.6 | 126.1112
485.8 | 340.8 | 125.7337 | 52.4443 | 485.8 | 340.8 | 119.2537 | 5.0082 | 485.8 | 340.8 | 129.8526 | 0.1956 | 485.8 | 340.8 | 126.0153
486 | 341 | 125.7337 | 53.7878 | 486 | 341 | 120.3094 | 2.5131 | 486 | 341 | 129.8526 | 0.099605 | 486 | 341 | 126.0153
486.2 | 341.2 | 125.9256 | 53.6918 | 486.2 | 341.2 | 121.269 | 1.6494 | 486.2 | 341.2 | 129.9486 | 0.1956 | 486.2 | 341.2 | 126.1112
486.4 | 341.4 | 126.0216 | 54.7475 | 486.4 | 341.4 | 123.1884 | 2.5131 | 486.4 | 341.4 | 130.1405 | 0.1956 | 486.4 | 341.4 | 126.3991
486.6 | 341.6 | 126.0216 | 55.6112 | 486.6 | 341.6 | 123.5722 | 4.9123 | 486.6 | 341.6 | 130.3325 | 0.1956 | 486.6 | 341.6 | 126.3991
486.8 | 341.8 | 125.9256 | 56.091 | 486.8 | 341.8 | 122.9005 | 6.7357 | 486.8 | 341.8 | 130.1405 | 0.1956 | 486.8 | 341.8 | 126.3991
487 | 342 | 126.1175 | 45.5346 | 487 | 342 | 120.5013 | 10.9582 | 487 | 342 | 130.1405 | 0.1956 | 487 | 342 | 126.3032
487.2 | 342.2 | 126.4054 | 39.3927 | 487.2 | 342.2 | 119.9255 | 17.484 | 487.2 | 342.2 | 129.9486 | 0.1956 | 487.2 | 342.2 | 126.1112
487.4 | 342.4 | 126.6933 | 42.8475 | 487.4 | 342.4 | 121.6529 | 7.5993 | 487.4 | 342.4 | 130.1405 | 0.1956 | 487.4 | 342.4 | 126.2072
487.6 | 342.6 | 126.3095 | 44.8628 | 487.6 | 342.6 | 122.3247 | 7.7913 | 487.6 | 342.6 | 130.1405 | 0.1956 | 487.6 | 342.6 | 126.3032
487.8 | 342.8 | 126.2135 | 46.9741 | 487.8 | 342.8 | 121.8448 | 7.4074 | 487.8 | 342.8 | 130.1405 | 0.1956 | 487.8 | 342.8 | 126.2072
488 | 343 | 126.2135 | 47.454 | 488 | 343 | 123.5722 | 5.3921 | 488 | 343 | 130.1405 | 0.099605 | 488 | 343 | 126.2072
488.2 | 343.2 | 126.5974 | 47.358 | 488.2 | 343.2 | 125.0117 | 2.5131 | 488.2 | 343.2 | 130.3325 | 0.099605 | 488.2 | 343.2 | 126.4951
488.4 | 343.4 | 126.2135 | 48.6056 | 488.4 | 343.4 | 122.6126 | 2.5131 | 488.4 | 343.4 | 130.1405 | 0.1956 | 488.4 | 343.4 | 126.3032
488.6 | 343.6 | 126.3095 | 48.8935 | 488.6 | 343.6 | 121.7489 | 2.705 | 488.6 | 343.6 | 130.0446 | 0.1956 | 488.6 | 343.6 | 125.8233
488.8 | 343.8 | 125.9256 | 49.7572 | 488.8 | 343.8 | 122.1327 | 3.0889 | 488.8 | 343.8 | 130.0446 | 0.1956 | 488.8 | 343.8 | 126.3032
489 | 344 | 126.0216 | 50.7168 | 489 | 344 | 120.9811 | 2.705 | 489 | 344 | 129.9486 | 0.1956 | 489 | 344 | 126.1112
489.2 | 344.2 | 125.8296 | 51.0047 | 489.2 | 344.2 | 120.2134 | 3.9526 | 489.2 | 344.2 | 129.8526 | 0.1956 | 489.2 | 344.2 | 126.0153
489.4 | 344.4 | 126.0216 | 50.6209 | 489.4 | 344.4 | 120.7892 | 4.8163 | 489.4 | 344.4 | 129.8526 | 0.003654 | 489.4 | 344.4 | 126.1112
489.6 | 344.6 | 126.0216 | 48.9894 | 489.6 | 344.6 | 120.9811 | 4.2405 | 489.6 | 344.6 | 129.9486 | 0.1956 | 489.6 | 344.6 | 126.2072
489.8 | 344.8 | 125.8296 | 49.1814 | 489.8 | 344.8 | 120.3094 | 3.7607 | 489.8 | 344.8 | 130.0446 | 0.099605 | 489.8 | 344.8 | 126.2072
490 | 345 | 126.0216 | 49.0854 | 490 | 345 | 122.0368 | 7.1195 | 490 | 345 | 129.8526 | 0.48349 | 490 | 345 | 126.2072
490.2 | 345.2 | 126.0216 | 49.9491 | 490.2 | 345.2 | 122.6126 | 5.4881 | 490.2 | 345.2 | 130.1405 | 0.1956 | 490.2 | 345.2 | 126.2072
490.4 | 345.4 | 125.8296 | 50.8128 | 490.4 | 345.4 | 121.461 | 5.584 | 490.4 | 345.4 | 129.9486 | 0.1956 | 490.4 | 345.4 | 126.1112
490.6 | 345.6 | 125.5418 | 53.0201 | 490.6 | 345.6 | 119.6376 | 4.1445 | 490.6 | 345.6 | 129.7567 | 0.67543 | 490.6 | 345.6 | 126.0153
490.8 | 345.8 | 125.2538 | 54.0757 | 490.8 | 345.8 | 117.3344 | 6.8316 | 490.8 | 345.8 | 129.6607 | 0.099605 | 490.8 | 345.8 | 125.8233
491 | 346 | 125.2538 | 55.0354 | 491 | 346 | 117.5263 | 7.7913 | 491 | 346 | 129.6607 | 0.1956 | 491 | 346 | 125.6314
491.2 | 346.2 | 125.0619 | 55.6112 | 491.2 | 346.2 | 117.3344 | 8.559 | 491.2 | 346.2 | 129.3728 | 0.099605 | 491.2 | 346.2 | 125.2475
491.4 | 346.4 | 124.9659 | 56.8587 | 491.4 | 346.4 | 117.0465 | 8.4631 | 491.4 | 346.4 | 129.3728 | 0.1956 | 491.4 | 346.4 | 125.3435
491.6 | 346.6 | 124.87 | 57.4346 | 491.6 | 346.6 | 116.1828 | 9.3268 | 491.6 | 346.6 | 129.2768 | 0.1956 | 491.6 | 346.6 | 125.4394
491.8 | 346.8 | 124.678 | 58.4902 | 491.8 | 346.8 | 114.6473 | 10.5743 | 491.8 | 346.8 | 128.9889 | 0.1956 | 491.8 | 346.8 | 125.4394
492 | 347 | 124.4861 | 58.8741 | 492 | 347 | 113.3038 | 9.9985 | 492 | 347 | 128.9889 | 0.29155 | 492 | 347 | 124.9596
492.2 | 347.2 | 124.582 | 59.162 | 492.2 | 347.2 | 111.9602 | 9.0388 | 492.2 | 347.2 | 128.893 | 0.099605 | 492.2 | 347.2 | 125.1516
492.4 | 347.4 | 124.4861 | 60.2176 | 492.4 | 347.4 | 111.7683 | 10.6703 | 492.4 | 347.4 | 128.9889 | -0.092337 | 492.4 | 347.4 | 125.0556
492.6 | 347.6 | 124.3901 | 60.6015 | 492.6 | 347.6 | 111.1925 | 15.8525 | 492.6 | 347.6 | 128.797 | 0.1956 | 492.6 | 347.6 | 125.1516
492.8 | 347.8 | 124.774 | 61.6571 | 492.8 | 347.8 | 114.9352 | 10.2864 | 492.8 | 347.8 | 129.1809 | 0.29155 | 492.8 | 347.8 | 125.3435
493 | 348 | 125.2538 | 71.2538 | 493 | 348 | 116.6626 | 8.2711 | 493 | 348 | 129.3728 | 0.099605 | 493 | 348 | 125.4394
493.2 | 348.2 | 127.3651 | 115.3028 | 493.2 | 348.2 | 117.4303 | 8.4631 | 493.2 | 348.2 | 129.5647 | 0.1956 | 493.2 | 348.2 | 125.6314
493.4 | 348.4 | 127.557 | 118.2778 | 493.4 | 348.4 | 118.39 | 10.2864 | 493.4 | 348.4 | 129.6607 | 0.1956 | 493.4 | 348.4 | 125.7273
493.6 | 348.6 | 127.749 | 118.8536 | 493.6 | 348.6 | 119.8295 | 9.4227 | 493.6 | 348.6 | 129.7567 | 0.3875 | 493.6 | 348.6 | 125.5354
493.8 | 348.8 | 127.749 | 118.6617 | 493.8 | 348.8 | 119.6376 | 13.0695 | 493.8 | 348.8 | 129.7567 | 0.3875 | 493.8 | 348.8 | 125.8233
494 | 349 | 127.557 | 118.7576 | 494 | 349 | 119.4457 | 6.5437 | 494 | 349 | 129.6607 | 0.099605 | 494 | 349 | 125.8233
494.2 | 349.2 | 127.4611 | 118.4697 | 494.2 | 349.2 | 116.1828 | 8.3671 | 494.2 | 349.2 | 129.4687 | 0.1956 | 494.2 | 349.2 | 125.6314
494.4 | 349.4 | 127.3651 | 118.4697 | 494.4 | 349.4 | 115.415 | 8.3671 | 494.4 | 349.4 | 129.3728 | 0.003654 | 494.4 | 349.4 | 125.3435
494.6 | 349.6 | 127.4611 | 118.2778 | 494.6 | 349.6 | 112.9199 | 7.4074 | 494.6 | 349.6 | 129.1809 | 0.099605 | 494.6 | 349.6 | 125.2475
494.8 | 349.8 | 127.1732 | 117.606 | 494.8 | 349.8 | 113.0158 | 4.9123 | 494.8 | 349.8 | 129.0849 | -0.092337 | 494.8 | 349.8 | 125.4394
495 | 350 | 127.0772 | 118.1818 | 495 | 350 | 112.4401 | 5.3921 | 495 | 350 | 128.9889 | 0.1956 | 495 | 350 | 125.1516
495.2 | 350.2 | 126.7893 | 117.7979 | 495.2 | 350.2 | 108.0255 | 5.584 | 495.2 | 350.2 | 128.701 | 0.1956 | 495.2 | 350.2 | 124.8637
495.4 | 350.4 | 126.3095 | 117.2222 | 495.4 | 350.4 | 101.4038 | 6.0639 | 495.4 | 350.4 | 128.1252 | 0.1956 | 495.4 | 350.4 | 124.2878
495.6 | 350.6 | 125.7337 | 116.8383 | 495.6 | 350.6 | 96.3176 | 6.2558 | 495.6 | 350.6 | 127.6454 | 0.1956 | 495.6 | 350.6 | 123.808
495.8 | 350.8 | 125.5418 | 116.7423 | 495.8 | 350.8 | 93.8224 | 5.4881 | 495.8 | 350.8 | 127.4535 | 0.099605 | 495.8 | 350.8 | 123.6161
496 | 351 | 125.0619 | 116.3584 | 496 | 351 | 88.8321 | 4.6244 | 496 | 351 | 126.9736 | 0.1956 | 496 | 351 | 123.1362
496.2 | 351.2 | 125.5418 | 116.4544 | 496.2 | 351.2 | 93.3426 | 5.8719 | 496.2 | 351.2 | 127.3575 | 0.099605 | 496.2 | 351.2 | 123.7121
496.4 | 351.4 | 125.4458 | 116.3584 | 496.4 | 351.4 | 90.3676 | 5.3921 | 496.4 | 351.4 | 127.1656 | 0.1956 | 496.4 | 351.4 | 123.1362
496.6 | 351.6 | 124.678 | 115.8786 | 496.6 | 351.6 | 86.4329 | 3.9526 | 496.6 | 351.6 | 126.7817 | 0.099605 | 496.6 | 351.6 | 122.8483
496.8 | 351.8 | 125.4458 | 116.7423 | 496.8 | 351.8 | 92.095 | 4.4324 | 496.8 | 351.8 | 127.4535 | -0.18829 | 496.8 | 351.8 | 123.6161
497 | 352 | 124.582 | 115.7826 | 497 | 352 | 80.291 | 4.8163 | 497 | 352 | 126.3018 | 0.1956 | 497 | 352 | 122.6564
497.2 | 352.2 | 124.1022 | 112.9996 | 497.2 | 352.2 | 76.0685 | 5.3921 | 497.2 | 352.2 | 126.014 | 0.099605 | 497.2 | 352.2 | 122.2725
497.4 | 352.4 | 127.557 | 115.3028 | 497.4 | 352.4 | 20.6954 | 2.705 | 497.4 | 352.4 | 129.4687 | 0.099605 | 497.4 | 352.4 | 125.5354
497.6 | 352.6 | 128.5167 | 115.9746 | 497.6 | 352.6 | 3.1334 | 0.78566 | 497.6 | 352.6 | 130.4284 | 0.1956 | 497.6 | 352.6 | 126.5911
497.8 | 352.8 | 128.6127 | 115.6867 | 497.8 | 352.8 | 1.214 | 0.49776 | 497.8 | 352.8 | 130.5244 | 0.099605 | 497.8 | 352.8 | 126.5911
498 | 353 | 128.7087 | 115.3988 | 498 | 353 | 0.83014 | 0.30582 | 498 | 353 | 130.4284 | 0.1956 | 498 | 353 | 126.5911
498.2 | 353.2 | 128.7087 | 115.3028 | 498.2 | 353.2 | 0.63824 | 0.20987 | 498.2 | 353.2 | 130.4284 | 0.1956 | 498.2 | 353.2 | 126.5911
498.4 | 353.4 | 128.7087 | 115.3028 | 498.4 | 353.4 | 0.54225 | 0.20987 | 498.4 | 353.4 | 130.4284 | 0.1956 | 498.4 | 353.4 | 126.4951
498.6 | 353.6 | 128.6127 | 115.3028 | 498.6 | 353.6 | 0.4463 | 0.20987 | 498.6 | 353.6 | 130.4284 | 0.1956 | 498.6 | 353.6 | 126.5911
498.8 | 353.8 | 128.7087 | 115.3988 | 498.8 | 353.8 | 0.4463 | 0.11392 | 498.8 | 353.8 | 130.4284 | 0.1956 | 498.8 | 353.8 | 126.5911
499 | 354 | 128.8046 | 115.3988 | 499 | 354 | 0.4463 | 0.11392 | 499 | 354 | 130.5244 | 0.29155 | 499 | 354 | 126.5911
499.2 | 354.2 | 128.8046 | 115.3028 | 499.2 | 354.2 | 0.35031 | 0.017929 | 499.2 | 354.2 | 130.4284 | 0.1956 | 499.2 | 354.2 | 126.5911
499.4 | 354.4 | 128.8046 | 115.2068 |  |  |  |  | 499.4 | 354.4 | 130.5244 | 0.1956 | 499.4 | 354.4 | 126.5911
499.6 | 354.6 | 128.8046 | 114.823 |  |  |  |  | 499.6 | 354.6 | 130.5244 | 0.099605 | 499.6 | 354.6 | 126.5911
499.8 | 354.8 | 128.8046 | 114.727 |  |  |  |  | 499.8 | 354.8 | 130.4284 | 0.1956 | 499.8 | 354.8 | 126.5911
500 | 355 | 128.7087 | 114.535 |  |  |  |  | 500 | 355 | 130.4284 | 0.1956 | 500 | 355 | 126.4951
500.2 | 355.2 | 128.8046 | 114.535 |  |  |  |  | 500.2 | 355.2 | 130.4284 | 0.1956 | 500.2 | 355.2 | 126.5911
500.4 | 355.4 | 128.7087 | 114.535 |  |  |  |  | 500.4 | 355.4 | 130.4284 | 0.1956 | 500.4 | 355.4 | 126.4951
500.6 | 355.6 | 128.7087 | 114.535 |  |  |  |  | 500.6 | 355.6 | 130.4284 | 0.1956 | 500.6 | 355.6 | 126.4951
500.8 | 355.8 | 128.7087 | 114.535 |  |  |  |  | 500.8 | 355.8 | 130.4284 | 0.1956 | 500.8 | 355.8 | 126.4951
501 | 356 | 128.7087 | 114.4391 |  |  |  |  | 501 | 356 | 130.4284 | 0.1956 | 501 | 356 | 126.5911
501.2 | 356.2 | 128.8046 | 114.2472 |  |  |  |  | 501.2 | 356.2 | 130.4284 | 0.1956 | 501.2 | 356.2 | 126.5911
501.4 | 356.4 | 128.8046 | 114.0552 |  |  |  |  | 501.4 | 356.4 | 130.4284 | 0.1956 | 501.4 | 356.4 | 126.5911
501.6 | 356.6 | 128.8046 | 114.1512 |  |  |  |  | 501.6 | 356.6 | 130.4284 | 0.1956 | 501.6 | 356.6 | 126.5911
501.8 | 356.8 | 128.9006 | 114.1512 |  |  |  |  | 501.8 | 356.8 | 130.4284 | 0.1956 | 501.8 | 356.8 | 126.5911
502 | 357 | 128.8046 | 114.0552 |  |  |  |  | 502 | 357 | 130.4284 | 0.1956 | 502 | 357 | 126.4951
502.2 | 357.2 | 128.9006 | 113.9593 |  |  |  |  | 502.2 | 357.2 | 130.4284 | 0.099605 | 502.2 | 357.2 | 126.4951
502.4 | 357.4 | 128.9006 | 113.1915 |  |  |  |  | 502.4 | 357.4 | 130.4284 | 0.1956 | 502.4 | 357.4 | 126.4951
502.6 | 357.6 | 128.9006 | 113.5754 |  |  |  |  | 502.6 | 357.6 | 130.4284 | 0.1956 | 502.6 | 357.6 | 126.4951
502.8 | 357.8 | 128.8046 | 113.6714 |  |  |  |  | 502.8 | 357.8 | 130.3325 | 0.1956 | 502.8 | 357.8 | 126.4951
503 | 358 | 128.8046 | 113.8633 |  |  |  |  | 503 | 358 | 130.4284 | 0.1956 | 503 | 358 | 126.4951
503.2 | 358.2 | 128.9006 | 113.4794 |  |  |  |  | 503.2 | 358.2 | 130.4284 | 0.1956 | 503.2 | 358.2 | 126.4951
503.4 | 358.4 | 128.9006 | 113.4794 |  |  |  |  | 503.4 | 358.4 | 130.3325 | 0.1956 | 503.4 | 358.4 | 126.4951
503.6 | 358.6 | 128.8046 | 113.3835 |  |  |  |  | 503.6 | 358.6 | 130.3325 | 0.099605 | 503.6 | 358.6 | 126.4951
503.8 | 358.8 | 128.7087 | 113.4794 |  |  |  |  | 503.8 | 358.8 | 130.3325 | 0.099605 | 503.8 | 358.8 | 126.3991
504 | 359 | 128.8046 | 113.2875 |  |  |  |  | 504 | 359 | 130.3325 | 0.1956 | 504 | 359 | 126.3991
504.2 | 359.2 | 128.9006 | 112.8076 |  |  |  |  | 504.2 | 359.2 | 130.4284 | 0.1956 | 504.2 | 359.2 | 126.4951
504.4 | 359.4 | 128.9006 | 113.3835 |  |  |  |  | 504.4 | 359.4 | 130.3325 | 0.1956 | 504.4 | 359.4 | 126.3991
504.6 | 359.6 | 128.9966 | 113.7673 |  |  |  |  | 504.6 | 359.6 | 130.4284 | 0.1956 | 504.6 | 359.6 | 126.4951
504.8 | 359.8 | 128.9006 | 113.6714 |  |  |  |  | 504.8 | 359.8 | 130.4284 | 0.1956 | 504.8 | 359.8 | 126.4951
505 | 360 | 128.9006 | 113.6714 |  |  |  |  | 505 | 360 | 130.4284 | 0.1956 | 505 | 360 | 126.4951
505.2 | 360.2 | 128.9966 | 113.7673 |  |  |  |  | 505.2 | 360.2 | 130.4284 | 0.1956 | 505.2 | 360.2 | 126.3991
505.4 | 360.4 | 128.9006 | 113.7673 |  |  |  |  | 505.4 | 360.4 | 130.3325 | 0.1956 | 505.4 | 360.4 | 126.3991
505.6 | 360.6 | 128.9966 | 114.0552 |  |  |  |  | 505.6 | 360.6 | 130.3325 | 0.099605 | 505.6 | 360.6 | 126.4951
505.8 | 360.8 | 128.8046 | 113.9593 |  |  |  |  | 505.8 | 360.8 | 130.3325 | 0.1956 | 505.8 | 360.8 | 126.3991
506 | 361 | 128.9006 | 113.9593 |  |  |  |  | 506 | 361 | 130.3325 | 0.1956 | 506 | 361 | 126.4951
506.2 | 361.2 | 128.9006 | 113.7673 |  |  |  |  | 506.2 | 361.2 | 130.3325 | 0.1956 | 506.2 | 361.2 | 126.3991
506.4 | 361.4 | 128.9006 | 112.9996 |  |  |  |  | 506.4 | 361.4 | 130.3325 | 0.1956 | 506.4 | 361.4 | 126.4951
506.6 | 361.6 | 128.9966 | 113.0955 |  |  |  |  | 506.6 | 361.6 | 130.4284 | 0.1956 | 506.6 | 361.6 | 126.4951
506.8 | 361.8 | 128.9966 | 113.0955 |  |  |  |  | 506.8 | 361.8 | 130.3325 | 0.1956 | 506.8 | 361.8 | 126.4951
507 | 362 | 129.0925 | 113.1915 |  |  |  |  | 507 | 362 | 130.4284 | 0.1956 | 507 | 362 | 126.4951
507.2 | 362.2 | 128.9966 | 113.0955 |  |  |  |  | 507.2 | 362.2 | 130.3325 | 0.1956 | 507.2 | 362.2 | 126.4951
507.4 | 362.4 | 128.9966 | 113.0955 |  |  |  |  | 507.4 | 362.4 | 130.4284 | 0.1956 | 507.4 | 362.4 | 126.4951
507.6 | 362.6 | 128.9966 | 113.1915 |  |  |  |  | 507.6 | 362.6 | 130.4284 | 0.1956 | 507.6 | 362.6 | 126.4951
507.8 | 362.8 | 129.0925 | 112.9036 |  |  |  |  | 507.8 | 362.8 | 130.4284 | 0.1956 | 507.8 | 362.8 | 126.3991
508 | 363 | 129.0925 | 100.14 |  |  |  |  | 508 | 363 | 130.3325 | 0.1956 | 508 | 363 | 126.4951
508.2 | 363.2 | 129.2844 | 102.7311 |  |  |  |  | 508.2 | 363.2 | 130.4284 | 0.1956 | 508.2 | 363.2 | 126.4951
508.4 | 363.4 | 129.2844 | 105.5141 |  |  |  |  | 508.4 | 363.4 | 130.4284 | 0.099605 | 508.4 | 363.4 | 126.4951
508.6 | 363.6 | 129.2844 | 106.4738 |  |  |  |  | 508.6 | 363.6 | 130.3325 | 0.1956 | 508.6 | 363.6 | 126.4951
508.8 | 363.8 | 129.2844 | 106.9536 |  |  |  |  | 508.8 | 363.8 | 130.3325 | 0.1956 | 508.8 | 363.8 | 126.4951
509 | 364 | 129.2844 | 107.2416 |  |  |  |  | 509 | 364 | 130.4284 | 0.1956 | 509 | 364 | 126.4951
509.2 | 364.2 | 129.3804 | 107.6254 |  |  |  |  | 509.2 | 364.2 | 130.4284 | 0.1956 | 509.2 | 364.2 | 126.4951
509.4 | 364.4 | 129.4764 | 107.9133 |  |  |  |  | 509.4 | 364.4 | 130.4284 | 0.1956 | 509.4 | 364.4 | 126.5911
509.6 | 364.6 | 129.3804 | 107.9133 |  |  |  |  | 509.6 | 364.6 | 130.4284 | 0.099605 | 509.6 | 364.6 | 126.4951
509.8 | 364.8 | 129.3804 | 108.1052 |  |  |  |  | 509.8 | 364.8 | 130.4284 | 0.099605 | 509.8 | 364.8 | 126.4951
510 | 365 | 129.3804 | 108.2012 |  |  |  |  | 510 | 365 | 130.3325 | 0.1956 | 510 | 365 | 126.4951
510.2 | 365.2 | 129.3804 | 108.2972 |  |  |  |  | 510.2 | 365.2 | 130.4284 | 0.1956 | 510.2 | 365.2 | 126.4951
510.4 | 365.4 | 129.5724 | 108.3931 |  |  |  |  | 510.4 | 365.4 | 130.4284 | 0.1956 | 510.4 | 365.4 | 126.4951
510.6 | 365.6 | 129.4764 | 108.3931 |  |  |  |  | 510.6 | 365.6 | 130.4284 | 0.1956 | 510.6 | 365.6 | 126.5911
510.8 | 365.8 | 129.5724 | 108.5851 |  |  |  |  | 510.8 | 365.8 | 130.4284 | 0.1956 | 510.8 | 365.8 | 126.4951
511 | 366 | 129.4764 | 108.5851 |  |  |  |  | 511 | 366 | 130.4284 | 0.1956 | 511 | 366 | 126.4951
511.2 | 366.2 | 129.5724 | 108.777 |  |  |  |  | 511.2 | 366.2 | 130.4284 | 0.1956 | 511.2 | 366.2 | 126.5911
511.4 | 366.4 | 129.5724 | 108.969 |  |  |  |  | 511.4 | 366.4 | 130.5244 | 0.1956 | 511.4 | 366.4 | 126.4951
511.6 | 366.6 | 129.5724 | 108.969 |  |  |  |  | 511.6 | 366.6 | 130.4284 | 0.1956 | 511.6 | 366.6 | 126.4951
511.8 | 366.8 | 129.5724 | 108.969 |  |  |  |  | 511.8 | 366.8 | 130.4284 | 0.1956 | 511.8 | 366.8 | 126.4951
512 | 367 | 129.4764 | 109.0649 |  |  |  |  | 512 | 367 | 130.3325 | 0.099605 | 512 | 367 | 126.3991
512.2 | 367.2 | 129.5724 | 109.3528 |  |  |  |  | 512.2 | 367.2 | 130.4284 | 0.1956 | 512.2 | 367.2 | 126.4951
512.4 | 367.4 | 129.4764 | 108.969 |  |  |  |  | 512.4 | 367.4 | 130.4284 | 0.1956 | 512.4 | 367.4 | 126.4951
512.6 | 367.6 | 129.5724 | 108.5851 |  |  |  |  | 512.6 | 367.6 | 130.4284 | 0.1956 | 512.6 | 367.6 | 126.4951
512.8 | 367.8 | 129.5724 | 107.3375 |  |  |  |  | 512.8 | 367.8 | 130.5244 | 0.1956 | 512.8 | 367.8 | 126.5911
513 | 368 | 129.5724 | 106.9536 |  |  |  |  | 513 | 368 | 130.5244 | 0.1956 | 513 | 368 | 126.5911
513.2 | 368.2 | 129.6683 | 107.4335 |  |  |  |  | 513.2 | 368.2 | 130.5244 | 0.1956 | 513.2 | 368.2 | 126.5911
513.4 | 368.4 | 129.6683 | 107.6254 |  |  |  |  | 513.4 | 368.4 | 130.5244 | 0.1956 | 513.4 | 368.4 | 126.5911
513.6 | 368.6 | 129.6683 | 107.9133 |  |  |  |  | 513.6 | 368.6 | 130.5244 | 0.099605 | 513.6 | 368.6 | 126.5911
513.8 | 368.8 | 129.6683 | 107.8174 |  |  |  |  | 513.8 | 368.8 | 130.5244 | 0.1956 | 513.8 | 368.8 | 126.5911
514 | 369 | 129.5724 | 107.9133 |  |  |  |  | 514 | 369 | 130.5244 | 0.1956 | 514 | 369 | 126.5911
514.2 | 369.2 | 129.6683 | 108.2012 |  |  |  |  | 514.2 | 369.2 | 130.6204 | 0.1956 | 514.2 | 369.2 | 126.5911
514.4 | 369.4 | 129.6683 | 108.2012 |  |  |  |  | 514.4 | 369.4 | 130.6204 | 0.1956 | 514.4 | 369.4 | 126.5911
514.6 | 369.6 | 129.6683 | 108.1052 |  |  |  |  | 514.6 | 369.6 | 130.6204 | 0.1956 | 514.6 | 369.6 | 126.5911
514.8 | 369.8 | 129.6683 | 108.0093 |  |  |  |  | 514.8 | 369.8 | 130.5244 | 0.1956 | 514.8 | 369.8 | 126.5911
515 | 370 | 129.5724 | 107.5295 |  |  |  |  | 515 | 370 | 130.5244 | 0.1956 | 515 | 370 | 126.5911
515.2 | 370.2 | 129.6683 | 107.5295 |  |  |  |  | 515.2 | 370.2 | 130.5244 | 0.1956 | 515.2 | 370.2 | 126.5911
515.4 | 370.4 | 129.6683 | 107.6254 |  |  |  |  | 515.4 | 370.4 | 130.5244 | 0.099605 | 515.4 | 370.4 | 126.5911
515.6 | 370.6 | 129.6683 | 107.8174 |  |  |  |  | 515.6 | 370.6 | 130.5244 | 0.1956 | 515.6 | 370.6 | 126.5911
515.8 | 370.8 | 129.7643 | 107.9133 |  |  |  |  | 515.8 | 370.8 | 130.5244 | 0.1956 | 515.8 | 370.8 | 126.5911
516 | 371 | 129.6683 | 107.3375 |  |  |  |  | 516 | 371 | 130.5244 | 0.1956 | 516 | 371 | 126.5911
516.2 | 371.2 | 129.7643 | 107.2416 |  |  |  |  | 516.2 | 371.2 | 130.6204 | 0.1956 | 516.2 | 371.2 | 126.687
516.4 | 371.4 | 129.8603 | 107.4335 |  |  |  |  | 516.4 | 371.4 | 130.5244 | 0.099605 | 516.4 | 371.4 | 126.687
516.6 | 371.6 | 129.8603 | 107.4335 |  |  |  |  | 516.6 | 371.6 | 130.6204 | 0.1956 | 516.6 | 371.6 | 126.783
516.8 | 371.8 | 129.9562 | 107.3375 |  |  |  |  | 516.8 | 371.8 | 130.6204 | 0.1956 | 516.8 | 371.8 | 126.687
517 | 372 | 129.9562 | 107.6254 |  |  |  |  | 517 | 372 | 130.7164 | 0.1956 | 517 | 372 | 126.783
517.2 | 372.2 | 129.9562 | 107.9133 |  |  |  |  | 517.2 | 372.2 | 130.6204 | 0.1956 | 517.2 | 372.2 | 126.687
517.4 | 372.4 | 129.9562 | 108.0093 |  |  |  |  | 517.4 | 372.4 | 130.6204 | 0.1956 | 517.4 | 372.4 | 126.687
517.6 | 372.6 | 129.9562 | 108.0093 |  |  |  |  | 517.6 | 372.6 | 130.6204 | 0.1956 | 517.6 | 372.6 | 126.783
517.8 | 372.8 | 129.9562 | 107.4335 |  |  |  |  | 517.8 | 372.8 | 130.7164 | 0.1956 | 517.8 | 372.8 | 126.687
518 | 373 | 129.8603 | 107.5295 |  |  |  |  | 518 | 373 | 130.6204 | 0.1956 | 518 | 373 | 126.687
518.2 | 373.2 | 129.9562 | 107.5295 |  |  |  |  | 518.2 | 373.2 | 130.6204 | 0.1956 | 518.2 | 373.2 | 126.783
518.4 | 373.4 | 129.9562 | 107.5295 |  |  |  |  | 518.4 | 373.4 | 130.7164 | 0.1956 | 518.4 | 373.4 | 126.783
518.6 | 373.6 | 129.9562 | 103.5948 |  |  |  |  | 518.6 | 373.6 | 130.6204 | 0.1956 | 518.6 | 373.6 | 126.687
518.8 | 373.8 | 129.9562 | 103.019 |  |  |  |  | 518.8 | 373.8 | 130.6204 | 0.1956 | 518.8 | 373.8 | 126.687
519 | 374 | 129.8603 | 102.4432 |  |  |  |  | 519 | 374 | 130.6204 | 0.1956 | 519 | 374 | 126.687
519.2 | 374.2 | 130.1482 | 103.2109 |  |  |  |  | 519.2 | 374.2 | 130.7164 | 0.099605 | 519.2 | 374.2 | 126.687
519.4 | 374.4 | 130.0522 | 102.5392 |  |  |  |  | 519.4 | 374.4 | 130.7164 | 0.1956 | 519.4 | 374.4 | 126.783
519.6 | 374.6 | 129.9562 | 106.5698 |  |  |  |  | 519.6 | 374.6 | 130.6204 | 0.1956 | 519.6 | 374.6 | 126.687
519.8 | 374.8 | 129.9562 | 103.4988 |  |  |  |  | 519.8 | 374.8 | 130.6204 | 0.1956 | 519.8 | 374.8 | 126.687
520 | 375 | 129.8603 | 105.1303 |  |  |  |  | 520 | 375 | 130.6204 | 0.1956 | 520 | 375 | 126.687
520.2 | 375.2 | 129.8603 | 106.5698 |  |  |  |  | 520.2 | 375.2 | 130.6204 | 0.1956 | 520.2 | 375.2 | 126.687
520.4 | 375.4 | 129.8603 | 106.6657 |  |  |  |  | 520.4 | 375.4 | 130.7164 | 0.099605 | 520.4 | 375.4 | 126.783
520.6 | 375.6 | 129.8603 | 106.8577 |  |  |  |  | 520.6 | 375.6 | 130.7164 | 0.1956 | 520.6 | 375.6 | 126.783
520.8 | 375.8 | 129.7643 | 104.5545 |  |  |  |  | 520.8 | 375.8 | 130.7164 | 0.1956 | 520.8 | 375.8 | 126.687
521 | 376 | 129.7643 | 104.3625 |  |  |  |  | 521 | 376 | 130.6204 | 0.1956 | 521 | 376 | 126.687
521.2 | 376.2 | 129.6683 | 98.7964 |  |  |  |  | 521.2 | 376.2 | 130.6204 | 0.1956 | 521.2 | 376.2 | 126.687
521.4 | 376.4 | 129.6683 | 98.8924 |  |  |  |  | 521.4 | 376.4 | 130.6204 | 0.1956 | 521.4 | 376.4 | 126.687
521.6 | 376.6 | 129.6683 | 99.4682 |  |  |  |  | 521.6 | 376.6 | 130.6204 | 0.1956 | 521.6 | 376.6 | 126.687
521.8 | 376.8 | 129.6683 | 104.5545 |  |  |  |  | 521.8 | 376.8 | 130.6204 | 0.1956 | 521.8 | 376.8 | 126.783
522 | 377 | 129.5724 | 105.0343 |  |  |  |  | 522 | 377 | 130.6204 | 0.099605 | 522 | 377 | 126.687
522.2 | 377.2 | 129.6683 | 101.2916 |  |  |  |  | 522.2 | 377.2 | 130.7164 | 0.1956 | 522.2 | 377.2 | 126.687
522.4 | 377.4 | 129.3804 | 99.0843 |  |  |  |  | 522.4 | 377.4 | 130.7164 | 0.1956 | 522.4 | 377.4 | 126.783
522.6 | 377.6 | 129.1885 | 103.6908 |  |  |  |  | 522.6 | 377.6 | 130.7164 | 0.1956 | 522.6 | 377.6 | 126.783
522.8 | 377.8 | 129.1885 | 97.3569 |  |  |  |  | 522.8 | 377.8 | 130.7164 | 0.1956 | 522.8 | 377.8 | 126.783
523 | 378 | 128.5167 | 95.4376 |  |  |  |  | 523 | 378 | 130.6204 | 0.1956 | 523 | 378 | 126.687
523.2 | 378.2 | 128.7087 | 96.1093 |  |  |  |  | 523.2 | 378.2 | 130.7164 | 0.1956 | 523.2 | 378.2 | 126.783
523.4 | 378.4 | 128.9006 | 100.6198 |  |  |  |  | 523.4 | 378.4 | 130.7164 | 0.1956 | 523.4 | 378.4 | 126.783
523.6 | 378.6 | 129.1885 | 99.4682 |  |  |  |  | 523.6 | 378.6 | 130.8123 | 0.1956 | 523.6 | 378.6 | 126.783
523.8 | 378.8 | 129.1885 | 98.4126 |  |  |  |  | 523.8 | 378.8 | 130.7164 | 0.1956 | 523.8 | 378.8 | 126.783
524 | 379 | 129.3804 | 99.4682 |  |  |  |  | 524 | 379 | 130.7164 | 0.1956 | 524 | 379 | 126.783
524.2 | 379.2 | 129.6683 | 101.6755 |  |  |  |  | 524.2 | 379.2 | 130.8123 | 0.1956 | 524.2 | 379.2 | 126.783
524.4 | 379.4 | 129.4764 | 96.9731 |  |  |  |  | 524.4 | 379.4 | 131.0042 | 0.1956 | 524.4 | 379.4 | 126.783
524.6 | 379.6 | 129.3804 | 100.2359 |  |  |  |  | 524.6 | 379.6 | 131.1962 | 0.1956 | 524.6 | 379.6 | 126.879
524.8 | 379.8 | 129.5724 | 103.4029 |  |  |  |  | 524.8 | 379.8 | 130.9083 | 0.1956 | 524.8 | 379.8 | 126.783
525 | 380 | 129.6683 | 105.6101 |  |  |  |  | 525 | 380 | 130.9083 | 0.1956 | 525 | 380 | 126.879
525.2 | 380.2 | 129.6683 | 105.4182 |  |  |  |  | 525.2 | 380.2 | 130.9083 | 0.1956 | 525.2 | 380.2 | 126.879
525.4 | 380.4 | 129.6683 | 105.7061 |  |  |  |  | 525.4 | 380.4 | 130.8123 | 0.1956 | 525.4 | 380.4 | 126.879
525.6 | 380.6 | 129.4764 | 103.3069 |  |  |  |  | 525.6 | 380.6 | 130.8123 | 0.099605 | 525.6 | 380.6 | 127.0709
525.8 | 380.8 | 129.5724 | 105.0343 |  |  |  |  | 525.8 | 380.8 | 130.7164 | 0.099605 | 525.8 | 380.8 | 127.0709
526 | 381 | 129.6683 | 106.3779 |  |  |  |  | 526 | 381 | 130.8123 | 0.1956 | 526 | 381 | 127.4548
526.2 | 381.2 | 129.7643 | 107.6254 |  |  |  |  | 526.2 | 381.2 | 130.8123 | 0.1956 | 526.2 | 381.2 | 127.2628
526.4 | 381.4 | 129.8603 | 109.1609 |  |  |  |  | 526.4 | 381.4 | 130.7164 | 0.1956 | 526.4 | 381.4 | 126.9749
526.6 | 381.6 | 129.8603 | 108.1052 |  |  |  |  | 526.6 | 381.6 | 130.8123 | 0.1956 | 526.6 | 381.6 | 126.9749
526.8 | 381.8 | 129.6683 | 107.0496 |  |  |  |  | 526.8 | 381.8 | 130.7164 | 0.1956 | 526.8 | 381.8 | 126.9749
527 | 382 | 129.7643 | 107.0496 |  |  |  |  | 527 | 382 | 130.7164 | 0.1956 | 527 | 382 | 126.9749
527.2 | 382.2 | 129.7643 | 106.9536 |  |  |  |  | 527.2 | 382.2 | 130.7164 | 0.1956 | 527.2 | 382.2 | 126.9749
527.4 | 382.4 | 129.6683 | 105.898 |  |  |  |  | 527.4 | 382.4 | 130.7164 | 0.1956 | 527.4 | 382.4 | 126.9749
527.6 | 382.6 | 129.7643 | 107.1456 |  |  |  |  | 527.6 | 382.6 | 130.7164 | 0.1956 | 527.6 | 382.6 | 126.9749
527.8 | 382.8 | 129.7643 | 107.0496 |  |  |  |  | 527.8 | 382.8 | 130.7164 | 0.1956 | 527.8 | 382.8 | 126.879
528 | 383 | 129.6683 | 106.1859 |  |  |  |  | 528 | 383 | 130.6204 | 0.1956 | 528 | 383 | 126.879
528.2 | 383.2 | 129.6683 | 106.09 |  |  |  |  | 528.2 | 383.2 | 130.6204 | 0.1956 | 528.2 | 383.2 | 126.783
528.4 | 383.4 | 129.6683 | 106.7617 |  |  |  |  | 528.4 | 383.4 | 130.7164 | 0.1956 | 528.4 | 383.4 | 126.783
528.6 | 383.6 | 129.5724 | 104.3625 |  |  |  |  | 528.6 | 383.6 | 130.7164 | 0.1956 | 528.6 | 383.6 | 126.687
528.8 | 383.8 | 129.4764 | 103.6908 |  |  |  |  | 528.8 | 383.8 | 130.7164 | 0.1956 | 528.8 | 383.8 | 126.783
529 | 384 | 129.3804 | 102.0593 |  |  |  |  | 529 | 384 | 130.7164 | 0.099605 | 529 | 384 | 126.783
529.2 | 384.2 | 129.1885 | 97.7408 |  |  |  |  | 529.2 | 384.2 | 130.7164 | 0.1956 | 529.2 | 384.2 | 126.783
529.4 | 384.4 | 129.3804 | 89.6795 |  |  |  |  | 529.4 | 384.4 | 130.7164 | 0.1956 | 529.4 | 384.4 | 126.879
529.6 | 384.6 | 129.2844 | 90.0634 |  |  |  |  | 529.6 | 384.6 | 130.7164 | 0.1956 | 529.6 | 384.6 | 126.783
529.8 | 384.8 | 129.2844 | 91.8868 |  |  |  |  | 529.8 | 384.8 | 130.7164 | 0.1956 | 529.8 | 384.8 | 126.783
530 | 385 | 129.2844 | 93.6142 |  |  |  |  | 530 | 385 | 130.6204 | 0.1956 | 530 | 385 | 126.783
530.2 | 385.2 | 129.1885 | 93.0384 |  |  |  |  | 530.2 | 385.2 | 130.7164 | 0.29155 | 530.2 | 385.2 | 126.879
530.4 | 385.4 | 129.1885 | 93.3263 |  |  |  |  | 530.4 | 385.4 | 130.7164 | 0.1956 | 530.4 | 385.4 | 126.879
530.6 | 385.6 | 128.9966 | 93.9981 |  |  |  |  | 530.6 | 385.6 | 130.8123 | 0.1956 | 530.6 | 385.6 | 126.783
530.8 | 385.8 | 129.0925 | 93.7102 |  |  |  |  | 530.8 | 385.8 | 130.8123 | 0.1956 | 530.8 | 385.8 | 126.879
531 | 386 | 128.9966 | 92.4626 |  |  |  |  | 531 | 386 | 130.7164 | 0.1956 | 531 | 386 | 126.879
531.2 | 386.2 | 128.2288 | 82.9619 |  |  |  |  | 531.2 | 386.2 | 130.6204 | 0.1956 | 531.2 | 386.2 | 126.687
531.4 | 386.4 | 127.8449 | 71.1579 |  |  |  |  | 531.4 | 386.4 | 130.7164 | 0.1956 | 531.4 | 386.4 | 126.783
531.6 | 386.6 | 128.1329 | 60.9854 |  |  |  |  | 531.6 | 386.6 | 130.7164 | 0.1956 | 531.6 | 386.6 | 126.783
531.8 | 386.8 | 128.1329 | 60.2176 |  |  |  |  | 531.8 | 386.8 | 130.6204 | 0.1956 | 531.8 | 386.8 | 126.783
532 | 387 | 127.9409 | 64.824 |  |  |  |  | 532 | 387 | 130.6204 | 0.29155 | 532 | 387 | 126.687
532.2 | 387.2 | 127.653 | 69.5264 |  |  |  |  | 532.2 | 387.2 | 130.6204 | 0.1956 | 532.2 | 387.2 | 126.687
532.4 | 387.4 | 127.557 | 68.8547 |  |  |  |  | 532.4 | 387.4 | 130.6204 | 0.1956 | 532.4 | 387.4 | 126.783
532.6 | 387.6 | 127.4611 | 70.87 |  |  |  |  | 532.6 | 387.6 | 130.5244 | 0.1956 | 532.6 | 387.6 | 126.687
532.8 | 387.8 | 127.3651 | 74.3248 |  |  |  |  | 532.8 | 387.8 | 130.6204 | 0.1956 | 532.8 | 387.8 | 126.687
533 | 388 | 127.3651 | 69.1426 |  |  |  |  | 533 | 388 | 130.6204 | 0.1956 | 533 | 388 | 126.687
533.2 | 388.2 | 127.3651 | 68.6627 |  |  |  |  | 533.2 | 388.2 | 130.6204 | 0.1956 | 533.2 | 388.2 | 126.783
533.4 | 388.4 | 127.1732 | 72.0216 |  |  |  |  | 533.4 | 388.4 | 130.5244 | 0.1956 | 533.4 | 388.4 | 126.687
533.6 | 388.6 | 127.0772 | 74.6127 |  |  |  |  | 533.6 | 388.6 | 130.4284 | 0.1956 | 533.6 | 388.6 | 126.5911
533.8 | 388.8 | 126.9813 | 73.3651 |  |  |  |  | 533.8 | 388.8 | 130.5244 | 0.1956 | 533.8 | 388.8 | 126.687
534 | 389 | 126.9813 | 73.3651 |  |  |  |  | 534 | 389 | 130.4284 | 0.099605 | 534 | 389 | 126.5911
534.2 | 389.2 | 127.3651 | 69.0466 |  |  |  |  | 534.2 | 389.2 | 130.5244 | 0.1956 | 534.2 | 389.2 | 126.4951
534.4 | 389.4 | 126.9813 | 73.1732 |  |  |  |  | 534.4 | 389.4 | 130.5244 | 0.1956 | 534.4 | 389.4 | 126.5911
534.6 | 389.6 | 127.9409 | 87.3763 |  |  |  |  | 534.6 | 389.6 | 130.6204 | 0.1956 | 534.6 | 389.6 | 126.687
534.8 | 389.8 | 129.3804 | 106.6657 |  |  |  |  | 534.8 | 389.8 | 130.7164 | 0.1956 | 534.8 | 389.8 | 126.783
535 | 390 | 129.4764 | 107.9133 |  |  |  |  | 535 | 390 | 130.7164 | 0.1956 | 535 | 390 | 126.879
535.2 | 390.2 | 129.4764 | 108.0093 |  |  |  |  | 535.2 | 390.2 | 130.7164 | 0.1956 | 535.2 | 390.2 | 126.879
535.4 | 390.4 | 129.4764 | 107.9133 |  |  |  |  | 535.4 | 390.4 | 130.7164 | 0.29155 | 535.4 | 390.4 | 126.879
535.6 | 390.6 | 129.5724 | 107.9133 |  |  |  |  | 535.6 | 390.6 | 130.7164 | 0.1956 | 535.6 | 390.6 | 126.879
535.8 | 390.8 | 129.4764 | 108.0093 |  |  |  |  | 535.8 | 390.8 | 130.8123 | 0.1956 | 535.8 | 390.8 | 126.879
536 | 391 | 129.4764 | 107.9133 |  |  |  |  | 536 | 391 | 130.7164 | 0.1956 | 536 | 391 | 126.783
536.2 | 391.2 | 129.4764 | 106.6657 |  |  |  |  | 536.2 | 391.2 | 130.8123 | 0.1956 | 536.2 | 391.2 | 126.879
536.4 | 391.4 | 129.4764 | 106.2819 |  |  |  |  | 536.4 | 391.4 | 130.8123 | 0.1956 | 536.4 | 391.4 | 126.879
536.6 | 391.6 | 129.4764 | 107.5295 |  |  |  |  | 536.6 | 391.6 | 130.7164 | 0.1956 | 536.6 | 391.6 | 126.879
536.8 | 391.8 | 129.4764 | 106.4738 |  |  |  |  | 536.8 | 391.8 | 130.7164 | 0.1956 | 536.8 | 391.8 | 126.783
537 | 392 | 129.3804 | 106.5698 |  |  |  |  | 537 | 392 | 130.7164 | 0.1956 | 537 | 392 | 126.879
537.2 | 392.2 | 129.3804 | 106.5698 |  |  |  |  | 537.2 | 392.2 | 130.7164 | 0.1956 | 537.2 | 392.2 | 126.783
537.4 | 392.4 | 129.4764 | 106.5698 |  |  |  |  | 537.4 | 392.4 | 130.7164 | 0.1956 | 537.4 | 392.4 | 126.879
537.6 | 392.6 | 129.4764 | 106.5698 |  |  |  |  | 537.6 | 392.6 | 130.6204 | 0.1956 | 537.6 | 392.6 | 126.783
537.8 | 392.8 | 129.3804 | 106.4738 |  |  |  |  | 537.8 | 392.8 | 130.6204 | 0.1956 | 537.8 | 392.8 | 126.783
538 | 393 | 129.3804 | 107.1456 |  |  |  |  | 538 | 393 | 130.6204 | 0.1956 | 538 | 393 | 126.783
538.2 | 393.2 | 129.4764 | 106.7617 |  |  |  |  | 538.2 | 393.2 | 130.6204 | 0.1956 | 538.2 | 393.2 | 126.783
538.4 | 393.4 | 129.3804 | 107.2416 |  |  |  |  | 538.4 | 393.4 | 130.7164 | 0.1956 | 538.4 | 393.4 | 126.783
538.6 | 393.6 | 129.4764 | 108.0093 |  |  |  |  | 538.6 | 393.6 | 130.7164 | 0.1956 | 538.6 | 393.6 | 126.783
538.8 | 393.8 | 129.4764 | 107.4335 |  |  |  |  | 538.8 | 393.8 | 130.6204 | 0.1956 | 538.8 | 393.8 | 126.783
539 | 394 | 129.4764 | 108.1052 |  |  |  |  | 539 | 394 | 130.7164 | 0.1956 | 539 | 394 | 126.783
539.2 | 394.2 | 129.4764 | 108.5851 |  |  |  |  | 539.2 | 394.2 | 130.6204 | 0.1956 | 539.2 | 394.2 | 126.783
539.4 | 394.4 | 129.3804 | 109.0649 |  |  |  |  | 539.4 | 394.4 | 130.6204 | 0.1956 | 539.4 | 394.4 | 126.687
539.6 | 394.6 | 129.3804 | 109.0649 |  |  |  |  | 539.6 | 394.6 | 130.6204 | 0.1956 | 539.6 | 394.6 | 126.783
539.8 | 394.8 | 129.3804 | 109.1609 |  |  |  |  | 539.8 | 394.8 | 130.6204 | 0.1956 | 539.8 | 394.8 | 126.687
540 | 395 | 129.3804 | 109.4488 |  |  |  |  | 540 | 395 | 130.6204 | 0.1956 | 540 | 395 | 126.687
540.2 | 395.2 | 129.3804 | 109.7367 |  |  |  |  | 540.2 | 395.2 | 130.6204 | 0.1956 | 540.2 | 395.2 | 126.783
540.4 | 395.4 | 129.4764 | 109.9286 |  |  |  |  | 540.4 | 395.4 | 130.6204 | 0.1956 | 540.4 | 395.4 | 126.783
540.6 | 395.6 | 129.3804 | 110.2165 |  |  |  |  | 540.6 | 395.6 | 130.6204 | 0.1956 | 540.6 | 395.6 | 126.687
540.8 | 395.8 | 129.2844 | 110.2165 |  |  |  |  | 540.8 | 395.8 | 130.6204 | 0.29155 | 540.8 | 395.8 | 126.687
541 | 396 | 129.2844 | 110.4085 |  |  |  |  | 541 | 396 | 130.6204 | 0.1956 | 541 | 396 | 126.783
541.2 | 396.2 | 129.2844 | 110.6964 |  |  |  |  | 541.2 | 396.2 | 130.6204 | 0.1956 | 541.2 | 396.2 | 126.783
541.4 | 396.4 | 129.3804 | 109.9286 |  |  |  |  | 541.4 | 396.4 | 130.6204 | 0.29155 | 541.4 | 396.4 | 126.783
541.6 | 396.6 | 129.2844 | 109.9286 |  |  |  |  | 541.6 | 396.6 | 130.6204 | 0.1956 | 541.6 | 396.6 | 126.783
541.8 | 396.8 | 129.2844 | 109.7367 |  |  |  |  | 541.8 | 396.8 | 130.6204 | 0.1956 | 541.8 | 396.8 | 126.783
542 | 397 | 129.1885 | 109.7367 |  |  |  |  | 542 | 397 | 130.5244 | 0.1956 | 542 | 397 | 126.783
542.2 | 397.2 | 129.1885 | 109.9286 |  |  |  |  | 542.2 | 397.2 | 130.6204 | 0.1956 | 542.2 | 397.2 | 126.687
542.4 | 397.4 | 129.1885 | 110.4085 |  |  |  |  | 542.4 | 397.4 | 130.6204 | 0.1956 | 542.4 | 397.4 | 126.687
542.6 | 397.6 | 129.2844 | 110.2165 |  |  |  |  | 542.6 | 397.6 | 130.6204 | 0.1956 | 542.6 | 397.6 | 126.783
542.8 | 397.8 | 129.1885 | 109.8327 |  |  |  |  | 542.8 | 397.8 | 130.6204 | 0.29155 | 542.8 | 397.8 | 126.783
543 | 398 | 129.1885 | 109.9286 |  |  |  |  | 543 | 398 | 130.6204 | 0.1956 | 543 | 398 | 126.687
543.2 | 398.2 | 129.1885 | 110.3125 |  |  |  |  | 543.2 | 398.2 | 130.6204 | 0.1956 | 543.2 | 398.2 | 126.783
543.4 | 398.4 | 129.0925 | 110.5044 |  |  |  |  | 543.4 | 398.4 | 130.6204 | 0.1956 | 543.4 | 398.4 | 126.783
543.6 | 398.6 | 129.0925 | 109.7367 |  |  |  |  | 543.6 | 398.6 | 130.6204 | 0.1956 | 543.6 | 398.6 | 126.687
543.8 | 398.8 | 129.0925 | 108.2012 |  |  |  |  | 543.8 | 398.8 | 130.6204 | 0.1956 | 543.8 | 398.8 | 126.687
544 | 399 | 129.0925 | 108.4891 |  |  |  |  | 544 | 399 | 130.5244 | 0.1956 | 544 | 399 | 126.687
544.2 | 399.2 | 129.1885 | 108.873 |  |  |  |  | 544.2 | 399.2 | 130.6204 | 0.1956 | 544.2 | 399.2 | 126.783
544.4 | 399.4 | 129.0925 | 109.1609 |  |  |  |  | 544.4 | 399.4 | 130.5244 | 0.29155 | 544.4 | 399.4 | 126.687
544.6 | 399.6 | 129.4764 | 109.8327 |  |  |  |  | 544.6 | 399.6 | 130.5244 | 0.1956 | 544.6 | 399.6 | 126.687
544.8 | 399.8 | 128.9966 | 111.3681 |  |  |  |  | 544.8 | 399.8 | 130.6204 | 0.1956 | 544.8 | 399.8 | 126.687
545 | 400 | 128.9006 | 111.656 |  |  |  |  | 545 | 400 | 130.5244 | 0.1956 | 545 | 400 | 126.5911
545.2 | 400.2 | 128.9966 | 111.5601 |  |  |  |  | 545.2 | 400.2 | 130.5244 | 0.1956 | 545.2 | 400.2 | 126.687
545.4 | 400.4 | 128.9006 | 111.848 |  |  |  |  | 545.4 | 400.4 | 130.5244 | 0.29155 | 545.4 | 400.4 | 126.687
545.6 | 400.6 | 128.9006 | 112.2319 |  |  |  |  | 545.6 | 400.6 | 130.6204 | 0.1956 | 545.6 | 400.6 | 126.687
545.8 | 400.8 | 128.8046 | 111.752 |  |  |  |  | 545.8 | 400.8 | 130.5244 | 0.29155 | 545.8 | 400.8 | 126.5911
546 | 401 | 128.7087 | 111.9439 |  |  |  |  | 546 | 401 | 130.4284 | 0.1956 | 546 | 401 | 126.5911
546.2 | 401.2 | 128.8046 | 112.2319 |  |  |  |  | 546.2 | 401.2 | 130.5244 | 0.1956 | 546.2 | 401.2 | 126.687
546.4 | 401.4 | 128.8046 | 112.7117 |  |  |  |  | 546.4 | 401.4 | 130.4284 | 0.1956 | 546.4 | 401.4 | 126.5911
546.6 | 401.6 | 128.9006 | 112.9036 |  |  |  |  | 546.6 | 401.6 | 130.5244 | 0.1956 | 546.6 | 401.6 | 126.5911
546.8 | 401.8 | 128.7087 | 112.9036 |  |  |  |  | 546.8 | 401.8 | 130.4284 | 0.1956 | 546.8 | 401.8 | 126.4951
547 | 402 | 128.6127 | 113.1915 |  |  |  |  | 547 | 402 | 130.5244 | 0.1956 | 547 | 402 | 126.5911
547.2 | 402.2 | 128.6127 | 113.2875 |  |  |  |  | 547.2 | 402.2 | 130.5244 | 0.1956 | 547.2 | 402.2 | 126.5911
547.4 | 402.4 | 128.7087 | 115.4947 |  |  |  |  | 547.4 | 402.4 | 130.4284 | 0.29155 | 547.4 | 402.4 | 126.687
547.6 | 402.6 | 128.8046 | 114.9189 |  |  |  |  | 547.6 | 402.6 | 130.5244 | 0.1956 | 547.6 | 402.6 | 126.687
547.8 | 402.8 | 128.7087 | 114.823 |  |  |  |  | 547.8 | 402.8 | 130.4284 | 0.1956 | 547.8 | 402.8 | 126.4951
548 | 403 | 128.6127 | 114.3431 |  |  |  |  | 548 | 403 | 130.4284 | 0.1956 | 548 | 403 | 126.4951
548.2 | 403.2 | 128.5167 | 114.1512 |  |  |  |  | 548.2 | 403.2 | 130.4284 | 0.1956 | 548.2 | 403.2 | 126.4951
548.4 | 403.4 | 128.6127 | 113.9593 |  |  |  |  | 548.4 | 403.4 | 130.4284 | 0.1956 | 548.4 | 403.4 | 126.5911
548.6 | 403.6 | 128.6127 | 113.6714 |  |  |  |  | 548.6 | 403.6 | 130.4284 | 0.29155 | 548.6 | 403.6 | 126.4951
548.8 | 403.8 | 128.5167 | 113.5754 |  |  |  |  | 548.8 | 403.8 | 130.3325 | 0.1956 | 548.8 | 403.8 | 126.4951
549 | 404 | 128.5167 | 113.6714 |  |  |  |  | 549 | 404 | 130.3325 | 0.1956 | 549 | 404 | 126.4951
549.2 | 404.2 | 128.6127 | 114.2472 |  |  |  |  | 549.2 | 404.2 | 130.3325 | 0.1956 | 549.2 | 404.2 | 126.4951
549.4 | 404.4 | 128.6127 | 114.3431 |  |  |  |  | 549.4 | 404.4 | 130.3325 | 0.1956 | 549.4 | 404.4 | 126.4951
549.6 | 404.6 | 128.4208 | 114.1512 |  |  |  |  | 549.6 | 404.6 | 130.3325 | 0.1956 | 549.6 | 404.6 | 126.4951
549.8 | 404.8 | 128.3248 | 113.7673 |  |  |  |  | 549.8 | 404.8 | 130.3325 | 0.1956 | 549.8 | 404.8 | 126.4951
550 | 405 | 128.2288 | 113.6714 |  |  |  |  | 550 | 405 | 130.2365 | 0.1956 | 550 | 405 | 126.3991
550.2 | 405.2 | 128.2288 | 113.8633 |  |  |  |  | 550.2 | 405.2 | 130.2365 | 0.1956 | 550.2 | 405.2 | 126.4951
550.4 | 405.4 | 128.3248 | 113.3835 |  |  |  |  | 550.4 | 405.4 | 130.3325 | 0.1956 | 550.4 | 405.4 | 126.4951
550.6 | 405.6 | 128.2288 | 113.4794 |  |  |  |  | 550.6 | 405.6 | 130.3325 | 0.1956 | 550.6 | 405.6 | 126.3991
550.8 | 405.8 | 128.2288 | 113.1915 |  |  |  |  | 550.8 | 405.8 | 130.2365 | 0.1956 | 550.8 | 405.8 | 126.3991
551 | 406 | 128.1329 | 113.7673 |  |  |  |  | 551 | 406 | 130.3325 | 0.29155 | 551 | 406 | 126.3991
551.2 | 406.2 | 128.2288 | 113.9593 |  |  |  |  | 551.2 | 406.2 | 130.3325 | 0.1956 | 551.2 | 406.2 | 126.3991
551.4 | 406.4 | 128.1329 | 114.1512 |  |  |  |  | 551.4 | 406.4 | 130.3325 | 0.1956 | 551.4 | 406.4 | 126.3991
551.6 | 406.6 | 128.2288 | 113.1915 |  |  |  |  | 551.6 | 406.6 | 130.3325 | 0.1956 | 551.6 | 406.6 | 126.3991
551.8 | 406.8 | 128.2288 | 113.1915 |  |  |  |  | 551.8 | 406.8 | 130.3325 | 0.1956 | 551.8 | 406.8 | 126.3991
552 | 407 | 128.1329 | 113.1915 |  |  |  |  | 552 | 407 | 130.2365 | 0.1956 | 552 | 407 | 126.3032
552.2 | 407.2 | 128.1329 | 113.1915 |  |  |  |  | 552.2 | 407.2 | 130.3325 | 0.1956 | 552.2 | 407.2 | 126.3991
552.4 | 407.4 | 128.1329 | 113.3835 |  |  |  |  | 552.4 | 407.4 | 130.3325 | 0.1956 | 552.4 | 407.4 | 126.3991
552.6 | 407.6 | 127.749 | 113.0955 |  |  |  |  | 552.6 | 407.6 | 129.9486 | 0.1956 | 552.6 | 407.6 | 126.0153
552.8 | 407.8 | 127.749 | 113.0955 |  |  |  |  | 552.8 | 407.8 | 129.9486 | 0.1956 | 552.8 | 407.8 | 126.1112
553 | 408 | 127.8449 | 113.2875 |  |  |  |  | 553 | 408 | 130.0446 | 0.1956 | 553 | 408 | 126.1112
553.2 | 408.2 | 128.1329 | 113.5754 |  |  |  |  | 553.2 | 408.2 | 130.2365 | 0.1956 | 553.2 | 408.2 | 126.3032
553.4 | 408.4 | 128.0369 | 113.7673 |  |  |  |  | 553.4 | 408.4 | 130.2365 | 0.1956 | 553.4 | 408.4 | 126.3991
553.6 | 408.6 | 128.0369 | 113.7673 |  |  |  |  | 553.6 | 408.6 | 130.3325 | 0.099605 | 553.6 | 408.6 | 126.3991
553.8 | 408.8 | 128.0369 | 113.8633 |  |  |  |  | 553.8 | 408.8 | 130.3325 | 0.1956 | 553.8 | 408.8 | 126.3991
554 | 409 | 128.0369 | 113.6714 |  |  |  |  | 554 | 409 | 130.1405 | 0.29155 | 554 | 409 | 126.2072
554.2 | 409.2 | 128.0369 | 113.8633 |  |  |  |  | 554.2 | 409.2 | 130.2365 | 0.1956 | 554.2 | 409.2 | 126.3032
554.4 | 409.4 | 127.8449 | 113.8633 |  |  |  |  | 554.4 | 409.4 | 130.1405 | 0.1956 | 554.4 | 409.4 | 126.3032
554.6 | 409.6 | 127.9409 | 113.9593 |  |  |  |  | 554.6 | 409.6 | 130.1405 | 0.1956 | 554.6 | 409.6 | 126.3032
554.8 | 409.8 | 127.8449 | 114.0552 |  |  |  |  | 554.8 | 409.8 | 130.2365 | 0.1956 | 554.8 | 409.8 | 126.3032
555 | 410 | 127.749 | 114.1512 |  |  |  |  | 555 | 410 | 130.2365 | 0.1956 | 555 | 410 | 126.3032
555.2 | 410.2 | 127.8449 | 114.0552 |  |  |  |  | 555.2 | 410.2 | 130.2365 | 0.1956 | 555.2 | 410.2 | 126.3032
555.4 | 410.4 | 127.749 | 113.1915 |  |  |  |  | 555.4 | 410.4 | 130.1405 | 0.1956 | 555.4 | 410.4 | 126.3032
555.6 | 410.6 | 127.8449 | 112.7117 |  |  |  |  | 555.6 | 410.6 | 130.3325 | 0.1956 | 555.6 | 410.6 | 126.3032
555.8 | 410.8 | 127.749 | 112.4238 |  |  |  |  | 555.8 | 410.8 | 130.2365 | 0.1956 | 555.8 | 410.8 | 126.3032
556 | 411 | 127.653 | 112.0399 |  |  |  |  | 556 | 411 | 130.2365 | 0.1956 | 556 | 411 | 126.3032
556.2 | 411.2 | 127.749 | 112.3278 |  |  |  |  | 556.2 | 411.2 | 130.2365 | 0.1956 | 556.2 | 411.2 | 126.3032
556.4 | 411.4 | 127.749 | 112.7117 |  |  |  |  | 556.4 | 411.4 | 130.2365 | 0.099605 | 556.4 | 411.4 | 126.3032
556.6 | 411.6 | 127.8449 | 112.8076 |  |  |  |  | 556.6 | 411.6 | 130.2365 | 0.1956 | 556.6 | 411.6 | 126.3991
556.8 | 411.8 | 127.8449 | 112.9036 |  |  |  |  | 556.8 | 411.8 | 130.3325 | 0.1956 | 556.8 | 411.8 | 126.3991
557 | 412 | 127.8449 | 112.7117 |  |  |  |  | 557 | 412 | 130.3325 | 0.1956 | 557 | 412 | 126.3991
557.2 | 412.2 | 127.749 | 112.7117 |  |  |  |  | 557.2 | 412.2 | 130.2365 | 0.1956 | 557.2 | 412.2 | 126.3032
557.4 | 412.4 | 127.749 | 113.0955 |  |  |  |  | 557.4 | 412.4 | 130.3325 | 0.1956 | 557.4 | 412.4 | 126.3991
557.6 | 412.6 | 127.749 | 112.9036 |  |  |  |  | 557.6 | 412.6 | 130.3325 | 0.1956 | 557.6 | 412.6 | 126.3991
557.8 | 412.8 | 127.749 | 113.0955 |  |  |  |  | 557.8 | 412.8 | 130.3325 | 0.1956 | 557.8 | 412.8 | 126.3991
558 | 413 | 127.749 | 113.0955 |  |  |  |  | 558 | 413 | 130.3325 | 0.1956 | 558 | 413 | 126.3991
558.2 | 413.2 | 127.749 | 113.1915 |  |  |  |  | 558.2 | 413.2 | 130.3325 | 0.1956 | 558.2 | 413.2 | 126.3991
558.4 | 413.4 | 127.749 | 113.0955 |  |  |  |  | 558.4 | 413.4 | 130.3325 | 0.1956 | 558.4 | 413.4 | 126.3991
558.6 | 413.6 | 127.749 | 113.1915 |  |  |  |  | 558.6 | 413.6 | 130.3325 | 0.1956 | 558.6 | 413.6 | 126.3991
558.8 | 413.8 | 127.749 | 113.3835 |  |  |  |  | 558.8 | 413.8 | 130.3325 | 0.1956 | 558.8 | 413.8 | 126.3991
559 | 414 | 127.749 | 113.4794 |  |  |  |  | 559 | 414 | 130.4284 | 0.1956 | 559 | 414 | 126.4951
559.2 | 414.2 | 127.8449 | 113.6714 |  |  |  |  | 559.2 | 414.2 | 130.3325 | 0.1956 | 559.2 | 414.2 | 126.3991
559.4 | 414.4 | 127.8449 | 113.8633 |  |  |  |  | 559.4 | 414.4 | 130.4284 | 0.1956 | 559.4 | 414.4 | 126.4951
559.6 | 414.6 | 127.8449 | 113.7673 |  |  |  |  | 559.6 | 414.6 | 130.3325 | 0.1956 | 559.6 | 414.6 | 126.4951
559.8 | 414.8 | 127.8449 | 114.0552 |  |  |  |  | 559.8 | 414.8 | 130.3325 | 0.1956 | 559.8 | 414.8 | 126.4951
560 | 415 | 127.8449 | 114.3431 |  |  |  |  | 560 | 415 | 130.4284 | 0.29155 | 560 | 415 | 126.4951
560.2 | 415.2 | 127.8449 | 114.535 |  |  |  |  | 560.2 | 415.2 | 130.4284 | 0.1956 | 560.2 | 415.2 | 126.4951
560.4 | 415.4 | 127.9409 | 114.727 |  |  |  |  | 560.4 | 415.4 | 130.4284 | 0.1956 | 560.4 | 415.4 | 126.4951
560.6 | 415.6 | 127.8449 | 114.727 |  |  |  |  | 560.6 | 415.6 | 130.4284 | 0.1956 | 560.6 | 415.6 | 126.4951
560.8 | 415.8 | 127.8449 | 114.631 |  |  |  |  | 560.8 | 415.8 | 130.4284 | 0.1956 | 560.8 | 415.8 | 126.4951
561 | 416 | 127.9409 | 114.823 |  |  |  |  | 561 | 416 | 130.4284 | 0.1956 | 561 | 416 | 126.4951
561.2 | 416.2 | 127.8449 | 114.9189 |  |  |  |  | 561.2 | 416.2 | 130.3325 | 0.1956 | 561.2 | 416.2 | 126.4951
561.4 | 416.4 | 127.8449 | 115.0149 |  |  |  |  | 561.4 | 416.4 | 130.5244 | 0.1956 | 561.4 | 416.4 | 126.4951
561.6 | 416.6 | 127.8449 | 115.0149 |  |  |  |  | 561.6 | 416.6 | 130.5244 | 0.1956 | 561.6 | 416.6 | 126.4951
561.8 | 416.8 | 127.8449 | 115.1109 |  |  |  |  | 561.8 | 416.8 | 130.4284 | 0.1956 | 561.8 | 416.8 | 126.5911
562 | 417 | 127.8449 | 115.6867 |  |  |  |  | 562 | 417 | 130.4284 | 0.29155 | 562 | 417 | 126.4951
562.2 | 417.2 | 127.9409 | 115.7826 |  |  |  |  | 562.2 | 417.2 | 130.5244 | 0.1956 | 562.2 | 417.2 | 126.4951
562.4 | 417.4 | 127.8449 | 115.9746 |  |  |  |  | 562.4 | 417.4 | 130.5244 | 0.1956 | 562.4 | 417.4 | 126.5911
562.6 | 417.6 | 127.8449 | 116.0705 |  |  |  |  | 562.6 | 417.6 | 130.5244 | 0.1956 | 562.6 | 417.6 | 126.4951
562.8 | 417.8 | 127.9409 | 116.2625 |  |  |  |  | 562.8 | 417.8 | 130.5244 | 0.1956 | 562.8 | 417.8 | 126.5911
563 | 418 | 127.8449 | 116.3584 |  |  |  |  | 563 | 418 | 130.5244 | 0.1956 | 563 | 418 | 126.4951
563.2 | 418.2 | 127.749 | 116.4544 |  |  |  |  | 563.2 | 418.2 | 130.5244 | 0.1956 | 563.2 | 418.2 | 126.4951
563.4 | 418.4 | 127.653 | 116.3584 |  |  |  |  | 563.4 | 418.4 | 130.4284 | 0.1956 | 563.4 | 418.4 | 126.5911
563.6 | 418.6 | 127.749 | 116.4544 |  |  |  |  | 563.6 | 418.6 | 130.5244 | 0.1956 | 563.6 | 418.6 | 126.5911
563.8 | 418.8 | 127.653 | 116.5504 |  |  |  |  | 563.8 | 418.8 | 130.5244 | 0.1956 | 563.8 | 418.8 | 126.4951
564 | 419 | 127.653 | 116.6463 |  |  |  |  | 564 | 419 | 130.5244 | 0.1956 | 564 | 419 | 126.4951
564.2 | 419.2 | 127.749 | 116.3584 |  |  |  |  | 564.2 | 419.2 | 130.5244 | 0.29155 | 564.2 | 419.2 | 126.5911
564.4 | 419.4 | 127.653 | 116.5504 |  |  |  |  | 564.4 | 419.4 | 130.5244 | 0.1956 | 564.4 | 419.4 | 126.5911
564.6 | 419.6 | 127.653 | 114.2472 |  |  |  |  | 564.6 | 419.6 | 130.5244 | 0.1956 | 564.6 | 419.6 | 126.5911
564.8 | 419.8 | 127.557 | 114.0552 |  |  |  |  | 564.8 | 419.8 | 130.5244 | 0.1956 | 564.8 | 419.8 | 126.687
565 | 420 | 127.557 | 114.2472 |  |  |  |  | 565 | 420 | 130.5244 | 0.1956 | 565 | 420 | 126.5911
565.2 | 420.2 | 127.653 | 114.535 |  |  |  |  | 565.2 | 420.2 | 130.6204 | 0.1956 | 565.2 | 420.2 | 126.687
565.4 | 420.4 | 127.653 | 114.823 |  |  |  |  | 565.4 | 420.4 | 130.6204 | 0.1956 | 565.4 | 420.4 | 126.687
565.6 | 420.6 | 127.749 | 114.0552 |  |  |  |  | 565.6 | 420.6 | 130.7164 | 0.1956 | 565.6 | 420.6 | 126.687
565.8 | 420.8 | 127.749 | 110.6004 |  |  |  |  | 565.8 | 420.8 | 130.6204 | 0.1956 | 565.8 | 420.8 | 126.687
566 | 421 | 127.749 | 110.1206 |  |  |  |  | 566 | 421 | 130.6204 | 0.1956 | 566 | 421 | 126.687
566.2 | 421.2 | 127.749 | 110.3125 |  |  |  |  | 566.2 | 421.2 | 130.7164 | 0.1956 | 566.2 | 421.2 | 126.783
566.4 | 421.4 | 127.749 | 110.4085 |  |  |  |  | 566.4 | 421.4 | 130.6204 | 0.1956 | 566.4 | 421.4 | 126.687
566.6 | 421.6 | 127.8449 | 105.2262 |  |  |  |  | 566.6 | 421.6 | 130.7164 | 0.29155 | 566.6 | 421.6 | 126.783
566.8 | 421.8 | 127.749 | 102.0593 |  |  |  |  | 566.8 | 421.8 | 130.6204 | 0.1956 | 566.8 | 421.8 | 126.687
567 | 422 | 127.749 | 101.7714 |  |  |  |  | 567 | 422 | 130.7164 | 0.1956 | 567 | 422 | 126.783
567.2 | 422.2 | 127.749 | 102.1553 |  |  |  |  | 567.2 | 422.2 | 130.6204 | 0.1956 | 567.2 | 422.2 | 126.687
567.4 | 422.4 | 127.8449 | 102.3472 |  |  |  |  | 567.4 | 422.4 | 130.7164 | 0.1956 | 567.4 | 422.4 | 126.783
567.6 | 422.6 | 127.8449 | 104.7464 |  |  |  |  | 567.6 | 422.6 | 130.7164 | 0.1956 | 567.6 | 422.6 | 126.783
567.8 | 422.8 | 127.749 | 106.2819 |  |  |  |  | 567.8 | 422.8 | 130.6204 | 0.1956 | 567.8 | 422.8 | 126.687
568 | 423 | 127.749 | 107.0496 |  |  |  |  | 568 | 423 | 130.6204 | 0.1956 | 568 | 423 | 126.687
568.2 | 423.2 | 127.749 | 107.5295 |  |  |  |  | 568.2 | 423.2 | 130.6204 | 0.1956 | 568.2 | 423.2 | 126.687
568.4 | 423.4 | 127.749 | 108.0093 |  |  |  |  | 568.4 | 423.4 | 130.7164 | 0.1956 | 568.4 | 423.4 | 126.783
568.6 | 423.6 | 127.8449 | 108.3931 |  |  |  |  | 568.6 | 423.6 | 130.7164 | 0.1956 | 568.6 | 423.6 | 126.879
568.8 | 423.8 | 127.749 | 108.6811 |  |  |  |  | 568.8 | 423.8 | 130.7164 | 0.1956 | 568.8 | 423.8 | 126.783
569 | 424 | 127.749 | 108.969 |  |  |  |  | 569 | 424 | 130.7164 | 0.1956 | 569 | 424 | 126.783
569.2 | 424.2 | 127.749 | 109.1609 |  |  |  |  | 569.2 | 424.2 | 130.7164 | 0.1956 | 569.2 | 424.2 | 126.687
569.4 | 424.4 | 127.8449 | 109.2569 |  |  |  |  | 569.4 | 424.4 | 130.6204 | 0.1956 | 569.4 | 424.4 | 126.783
569.6 | 424.6 | 127.9409 | 109.5448 |  |  |  |  | 569.6 | 424.6 | 130.6204 | 0.1956 | 569.6 | 424.6 | 126.783
569.8 | 424.8 | 128.2288 | 109.4488 |  |  |  |  | 569.8 | 424.8 | 130.7164 | 0.1956 | 569.8 | 424.8 | 126.783
570 | 425 | 128.1329 | 109.7367 |  |  |  |  | 570 | 425 | 130.7164 | 0.1956 | 570 | 425 | 126.783
570.2 | 425.2 | 128.7087 | 110.0246 |  |  |  |  | 570.2 | 425.2 | 130.7164 | 0.1956 | 570.2 | 425.2 | 126.783
570.4 | 425.4 | 128.7087 | 110.0246 |  |  |  |  | 570.4 | 425.4 | 130.7164 | 0.1956 | 570.4 | 425.4 | 126.783
570.6 | 425.6 | 128.6127 | 110.4085 |  |  |  |  | 570.6 | 425.6 | 130.7164 | 0.1956 | 570.6 | 425.6 | 126.783
570.8 | 425.8 | 128.5167 | 110.8883 |  |  |  |  | 570.8 | 425.8 | 130.7164 | 0.1956 | 570.8 | 425.8 | 126.783
571 | 426 | 128.3248 | 111.0802 |  |  |  |  | 571 | 426 | 130.7164 | 0.1956 | 571 | 426 | 126.783
571.2 | 426.2 | 128.2288 | 111.0802 |  |  |  |  | 571.2 | 426.2 | 130.7164 | 0.29155 | 571.2 | 426.2 | 126.879
571.4 | 426.4 | 128.0369 | 110.9843 |  |  |  |  | 571.4 | 426.4 | 130.5244 | 0.1956 | 571.4 | 426.4 | 126.783
571.6 | 426.6 | 127.8449 | 110.6964 |  |  |  |  | 571.6 | 426.6 | 130.5244 | 0.099605 | 571.6 | 426.6 | 126.879
571.8 | 426.8 | 127.749 | 110.8883 |  |  |  |  | 571.8 | 426.8 | 130.3325 | 0.1956 | 571.8 | 426.8 | 126.783
572 | 427 | 127.653 | 110.9843 |  |  |  |  | 572 | 427 | 130.3325 | 0.1956 | 572 | 427 | 126.687
572.2 | 427.2 | 127.653 | 111.0802 |  |  |  |  | 572.2 | 427.2 | 130.5244 | 0.099605 | 572.2 | 427.2 | 126.783
572.4 | 427.4 | 127.749 | 111.1762 |  |  |  |  | 572.4 | 427.4 | 130.6204 | 0.1956 | 572.4 | 427.4 | 126.783
572.6 | 427.6 | 127.653 | 110.9843 |  |  |  |  | 572.6 | 427.6 | 130.5244 | 0.1956 | 572.6 | 427.6 | 126.783
572.8 | 427.8 | 127.749 | 110.9843 |  |  |  |  | 572.8 | 427.8 | 130.6204 | 0.1956 | 572.8 | 427.8 | 126.783
573 | 428 | 127.749 | 111.2722 |  |  |  |  | 573 | 428 | 130.6204 | 0.1956 | 573 | 428 | 126.5911
573.2 | 428.2 | 127.749 | 111.656 |  |  |  |  | 573.2 | 428.2 | 130.7164 | 0.29155 | 573.2 | 428.2 | 126.4951
573.4 | 428.4 | 127.749 | 111.848 |  |  |  |  | 573.4 | 428.4 | 130.7164 | 0.1956 | 573.4 | 428.4 | 126.3032
573.6 | 428.6 | 127.8449 | 112.0399 |  |  |  |  | 573.6 | 428.6 | 130.7164 | 0.1956 | 573.6 | 428.6 | 126.2072
573.8 | 428.8 | 127.749 | 112.6157 |  |  |  |  | 573.8 | 428.8 | 130.7164 | 0.1956 | 573.8 | 428.8 | 126.3032
574 | 429 | 127.749 | 112.0399 |  |  |  |  | 574 | 429 | 130.7164 | 0.1956 | 574 | 429 | 126.3032
574.2 | 429.2 | 127.8449 | 103.3069 |  |  |  |  | 574.2 | 429.2 | 130.7164 | 0.1956 | 574.2 | 429.2 | 126.5911
574.4 | 429.4 | 127.9409 | 98.4126 |  |  |  |  | 574.4 | 429.4 | 130.8123 | 0.1956 | 574.4 | 429.4 | 126.687
574.6 | 429.6 | 127.9409 | 98.4126 |  |  |  |  | 574.6 | 429.6 | 130.8123 | 0.1956 | 574.6 | 429.6 | 126.687
574.8 | 429.8 | 127.8449 | 98.3166 |  |  |  |  | 574.8 | 429.8 | 130.8123 | 0.1956 | 574.8 | 429.8 | 126.783
575 | 430 | 127.8449 | 98.8924 |  |  |  |  | 575 | 430 | 130.8123 | 0.1956 | 575 | 430 | 126.687
575.2 | 430.2 | 127.8449 | 99.6601 |  |  |  |  | 575.2 | 430.2 | 130.7164 | 0.29155 | 575.2 | 430.2 | 126.687
575.4 | 430.4 | 127.8449 | 104.0746 |  |  |  |  | 575.4 | 430.4 | 130.8123 | 0.1956 | 575.4 | 430.4 | 126.687
575.6 | 430.6 | 127.8449 | 105.4182 |  |  |  |  | 575.6 | 430.6 | 130.7164 | 0.1956 | 575.6 | 430.6 | 126.687
575.8 | 430.8 | 127.749 | 106.4738 |  |  |  |  | 575.8 | 430.8 | 130.7164 | 0.1956 | 575.8 | 430.8 | 126.687
576 | 431 | 127.749 | 106.8577 |  |  |  |  | 576 | 431 | 130.7164 | 0.1956 | 576 | 431 | 126.687
576.2 | 431.2 | 127.749 | 107.3375 |  |  |  |  | 576.2 | 431.2 | 130.8123 | 0.1956 | 576.2 | 431.2 | 126.783
576.4 | 431.4 | 127.749 | 107.7214 |  |  |  |  | 576.4 | 431.4 | 130.8123 | 0.1956 | 576.4 | 431.4 | 126.783
576.6 | 431.6 | 127.749 | 108.1052 |  |  |  |  | 576.6 | 431.6 | 130.8123 | 0.29155 | 576.6 | 431.6 | 126.783
576.8 | 431.8 | 127.749 | 108.2012 |  |  |  |  | 576.8 | 431.8 | 130.8123 | 0.1956 | 576.8 | 431.8 | 126.783
577 | 432 | 127.749 | 108.3931 |  |  |  |  | 577 | 432 | 130.8123 | 0.1956 | 577 | 432 | 126.783
577.2 | 432.2 | 127.8449 | 108.5851 |  |  |  |  | 577.2 | 432.2 | 130.8123 | 0.1956 | 577.2 | 432.2 | 126.879
577.4 | 432.4 | 127.749 | 108.6811 |  |  |  |  | 577.4 | 432.4 | 130.8123 | 0.1956 | 577.4 | 432.4 | 126.879
577.6 | 432.6 | 127.749 | 108.969 |  |  |  |  | 577.6 | 432.6 | 130.8123 | 0.1956 | 577.6 | 432.6 | 126.879
577.8 | 432.8 | 127.749 | 109.0649 |  |  |  |  | 577.8 | 432.8 | 130.8123 | 0.1956 | 577.8 | 432.8 | 126.879
578 | 433 | 127.8449 | 107.1456 |  |  |  |  | 578 | 433 | 130.8123 | 0.1956 | 578 | 433 | 126.783
578.2 | 433.2 | 127.749 | 110.5044 |  |  |  |  | 578.2 | 433.2 | 130.8123 | 0.1956 | 578.2 | 433.2 | 126.783
578.4 | 433.4 | 127.749 | 110.2165 |  |  |  |  | 578.4 | 433.4 | 130.7164 | 0.1956 | 578.4 | 433.4 | 126.879
578.6 | 433.6 | 127.749 | 109.9286 |  |  |  |  | 578.6 | 433.6 | 130.8123 | 0.1956 | 578.6 | 433.6 | 126.879
578.8 | 433.8 | 127.749 | 110.0246 |  |  |  |  | 578.8 | 433.8 | 130.8123 | 0.1956 | 578.8 | 433.8 | 126.783
579 | 434 | 127.749 | 110.4085 |  |  |  |  | 579 | 434 | 130.8123 | 0.1956 | 579 | 434 | 126.879
579.2 | 434.2 | 127.749 | 110.4085 |  |  |  |  | 579.2 | 434.2 | 130.8123 | 0.29155 | 579.2 | 434.2 | 126.879
579.4 | 434.4 | 127.749 | 110.4085 |  |  |  |  | 579.4 | 434.4 | 130.8123 | 0.1956 | 579.4 | 434.4 | 126.879
579.6 | 434.6 | 127.749 | 110.6004 |  |  |  |  | 579.6 | 434.6 | 130.8123 | 0.1956 | 579.6 | 434.6 | 126.879
579.8 | 434.8 | 127.749 | 107.0496 |  |  |  |  | 579.8 | 434.8 | 130.7164 | 0.1956 | 579.8 | 434.8 | 126.879
580 | 435 | 127.749 | 108.777 |  |  |  |  | 580 | 435 | 130.8123 | 0.1956 | 580 | 435 | 126.879
580.2 | 435.2 | 127.749 | 110.7924 |  |  |  |  | 580.2 | 435.2 | 130.7164 | 0.1956 | 580.2 | 435.2 | 126.879
580.4 | 435.4 | 127.749 | 111.2722 |  |  |  |  | 580.4 | 435.4 | 130.8123 | 0.1956 | 580.4 | 435.4 | 126.9749
580.6 | 435.6 | 127.749 | 111.3681 |  |  |  |  | 580.6 | 435.6 | 130.7164 | 0.1956 | 580.6 | 435.6 | 126.879
580.8 | 435.8 | 127.749 | 111.4641 |  |  |  |  | 580.8 | 435.8 | 130.8123 | 0.1956 | 580.8 | 435.8 | 126.9749
581 | 436 | 127.749 | 111.5601 |  |  |  |  | 581 | 436 | 130.8123 | 0.1956 | 581 | 436 | 126.879
581.2 | 436.2 | 127.749 | 111.4641 |  |  |  |  | 581.2 | 436.2 | 130.7164 | 0.1956 | 581.2 | 436.2 | 126.879
581.4 | 436.4 | 127.8449 | 111.5601 |  |  |  |  | 581.4 | 436.4 | 130.8123 | 0.1956 | 581.4 | 436.4 | 126.879
581.6 | 436.6 | 127.749 | 111.752 |  |  |  |  | 581.6 | 436.6 | 130.8123 | 0.1956 | 581.6 | 436.6 | 126.879
581.8 | 436.8 | 127.749 | 111.9439 |  |  |  |  | 581.8 | 436.8 | 130.7164 | 0.099605 | 581.8 | 436.8 | 126.879
582 | 437 | 127.749 | 106.7617 |  |  |  |  | 582 | 437 | 130.8123 | 0.1956 | 582 | 437 | 126.879
582.2 | 437.2 | 127.8449 | 104.2666 |  |  |  |  | 582.2 | 437.2 | 130.7164 | 0.29155 | 582.2 | 437.2 | 126.9749
582.4 | 437.4 | 127.8449 | 102.923 |  |  |  |  | 582.4 | 437.4 | 130.8123 | 0.1956 | 582.4 | 437.4 | 126.879
582.6 | 437.6 | 127.8449 | 103.2109 |  |  |  |  | 582.6 | 437.6 | 130.7164 | 0.1956 | 582.6 | 437.6 | 126.879
582.8 | 437.8 | 127.749 | 103.4988 |  |  |  |  | 582.8 | 437.8 | 130.7164 | 0.1956 | 582.8 | 437.8 | 126.879
583 | 438 | 127.8449 | 103.7867 |  |  |  |  | 583 | 438 | 130.7164 | 0.1956 | 583 | 438 | 126.783
583.2 | 438.2 | 127.749 | 104.2666 |  |  |  |  | 583.2 | 438.2 | 130.7164 | 0.1956 | 583.2 | 438.2 | 126.783
583.4 | 438.4 | 127.749 | 104.7464 |  |  |  |  | 583.4 | 438.4 | 130.7164 | 0.1956 | 583.4 | 438.4 | 126.783
583.6 | 438.6 | 127.8449 | 105.802 |  |  |  |  | 583.6 | 438.6 | 130.7164 | 0.1956 | 583.6 | 438.6 | 126.879
583.8 | 438.8 | 127.8449 | 107.7214 |  |  |  |  | 583.8 | 438.8 | 130.7164 | 0.1956 | 583.8 | 438.8 | 126.879
584 | 439 | 127.749 | 109.7367 |  |  |  |  | 584 | 439 | 130.6204 | 0.1956 | 584 | 439 | 126.783
584.2 | 439.2 | 127.749 | 110.9843 |  |  |  |  | 584.2 | 439.2 | 130.7164 | 0.29155 | 584.2 | 439.2 | 126.879
584.4 | 439.4 | 127.8449 | 112.0399 |  |  |  |  | 584.4 | 439.4 | 130.7164 | 0.1956 | 584.4 | 439.4 | 126.879
584.6 | 439.6 | 127.8449 | 112.6157 |  |  |  |  | 584.6 | 439.6 | 130.7164 | 0.1956 | 584.6 | 439.6 | 126.879
584.8 | 439.8 | 127.8449 | 112.6157 |  |  |  |  | 584.8 | 439.8 | 130.8123 | 0.1956 | 584.8 | 439.8 | 126.783
585 | 440 | 127.8449 | 112.6157 |  |  |  |  | 585 | 440 | 130.7164 | 0.29155 | 585 | 440 | 127.1668
585.2 | 440.2 | 127.8449 | 113.1915 |  |  |  |  | 585.2 | 440.2 | 130.8123 | 0.1956 | 585.2 | 440.2 | 126.9749
585.4 | 440.4 | 127.9409 | 113.5754 |  |  |  |  | 585.4 | 440.4 | 130.8123 | 0.1956 | 585.4 | 440.4 | 126.879
585.6 | 440.6 | 127.8449 | 113.7673 |  |  |  |  | 585.6 | 440.6 | 130.8123 | 0.1956 | 585.6 | 440.6 | 126.879
585.8 | 440.8 | 127.9409 | 114.2472 |  |  |  |  | 585.8 | 440.8 | 130.8123 | 0.1956 | 585.8 | 440.8 | 126.879
586 | 441 | 127.8449 | 114.3431 |  |  |  |  | 586 | 441 | 130.7164 | 0.1956 | 586 | 441 | 126.783
586.2 | 441.2 | 127.8449 | 114.631 |  |  |  |  | 586.2 | 441.2 | 130.8123 | 0.1956 | 586.2 | 441.2 | 126.9749
586.4 | 441.4 | 127.9409 | 115.0149 |  |  |  |  | 586.4 | 441.4 | 130.8123 | 0.29155 | 586.4 | 441.4 | 126.9749
586.6 | 441.6 | 127.9409 | 115.2068 |  |  |  |  | 586.6 | 441.6 | 130.8123 | 0.1956 | 586.6 | 441.6 | 126.879
586.8 | 441.8 | 127.8449 | 115.1109 |  |  |  |  | 586.8 | 441.8 | 130.7164 | 0.1956 | 586.8 | 441.8 | 126.9749
587 | 442 | 127.8449 | 115.3988 |  |  |  |  | 587 | 442 | 130.7164 | 0.1956 | 587 | 442 | 126.879
587.2 | 442.2 | 127.8449 | 115.5907 |  |  |  |  | 587.2 | 442.2 | 130.8123 | 0.1956 | 587.2 | 442.2 | 126.879
587.4 | 442.4 | 127.9409 | 115.0149 |  |  |  |  | 587.4 | 442.4 | 130.8123 | 0.1956 | 587.4 | 442.4 | 126.879
587.6 | 442.6 | 127.9409 | 114.823 |  |  |  |  | 587.6 | 442.6 | 130.8123 | 0.1956 | 587.6 | 442.6 | 126.9749
587.8 | 442.8 | 127.8449 | 115.0149 |  |  |  |  | 587.8 | 442.8 | 130.8123 | 0.1956 | 587.8 | 442.8 | 126.9749
588 | 443 | 127.8449 | 115.0149 |  |  |  |  | 588 | 443 | 130.7164 | 0.1956 | 588 | 443 | 126.879
588.2 | 443.2 | 127.9409 | 115.2068 |  |  |  |  | 588.2 | 443.2 | 130.8123 | 0.1956 | 588.2 | 443.2 | 126.9749
588.4 | 443.4 | 127.9409 | 115.3028 |  |  |  |  | 588.4 | 443.4 | 130.8123 | 0.1956 | 588.4 | 443.4 | 126.879
588.6 | 443.6 | 127.9409 | 115.4947 |  |  |  |  | 588.6 | 443.6 | 130.8123 | 0.1956 | 588.6 | 443.6 | 126.879
588.8 | 443.8 | 127.8449 | 115.3028 |  |  |  |  | 588.8 | 443.8 | 130.7164 | 0.1956 | 588.8 | 443.8 | 126.879
589 | 444 | 127.749 | 115.2068 |  |  |  |  | 589 | 444 | 130.7164 | 0.1956 | 589 | 444 | 126.879
589.2 | 444.2 | 127.8449 | 115.1109 |  |  |  |  | 589.2 | 444.2 | 130.7164 | 0.1956 | 589.2 | 444.2 | 126.879
589.4 | 444.4 | 127.8449 | 115.2068 |  |  |  |  | 589.4 | 444.4 | 130.7164 | 0.1956 | 589.4 | 444.4 | 126.783
589.6 | 444.6 | 127.8449 | 115.3988 |  |  |  |  | 589.6 | 444.6 | 130.8123 | 0.1956 | 589.6 | 444.6 | 126.879
589.8 | 444.8 | 127.8449 | 115.1109 |  |  |  |  | 589.8 | 444.8 | 130.7164 | 0.1956 | 589.8 | 444.8 | 126.879
590 | 445 | 127.8449 | 114.823 |  |  |  |  | 590 | 445 | 130.7164 | 0.1956 | 590 | 445 | 126.783
590.2 | 445.2 | 127.749 | 115.0149 |  |  |  |  | 590.2 | 445.2 | 130.7164 | 0.1956 | 590.2 | 445.2 | 126.879
590.4 | 445.4 | 127.749 | 115.0149 |  |  |  |  | 590.4 | 445.4 | 130.6204 | 0.1956 | 590.4 | 445.4 | 126.783
590.6 | 445.6 | 127.8449 | 111.9439 |  |  |  |  | 590.6 | 445.6 | 130.7164 | 0.1956 | 590.6 | 445.6 | 126.783
590.8 | 445.8 | 127.749 | 113.7673 |  |  |  |  | 590.8 | 445.8 | 130.6204 | 0.1956 | 590.8 | 445.8 | 126.783
591 | 446 | 127.8449 | 115.3988 |  |  |  |  | 591 | 446 | 130.7164 | 0.1956 | 591 | 446 | 126.783
591.2 | 446.2 | 127.8449 | 115.8786 |  |  |  |  | 591.2 | 446.2 | 130.7164 | 0.1956 | 591.2 | 446.2 | 126.783
591.4 | 446.4 | 127.8449 | 116.5504 |  |  |  |  | 591.4 | 446.4 | 130.7164 | 0.1956 | 591.4 | 446.4 | 126.783
591.6 | 446.6 | 127.8449 | 116.9343 |  |  |  |  | 591.6 | 446.6 | 130.6204 | 0.1956 | 591.6 | 446.6 | 126.783
591.8 | 446.8 | 127.9409 | 113.0955 |  |  |  |  | 591.8 | 446.8 | 130.6204 | 0.1956 | 591.8 | 446.8 | 126.783
592 | 447 | 127.9409 | 114.0552 |  |  |  |  | 592 | 447 | 130.7164 | 0.1956 | 592 | 447 | 126.783
592.2 | 447.2 | 127.8449 | 115.3028 |  |  |  |  | 592.2 | 447.2 | 130.7164 | 0.1956 | 592.2 | 447.2 | 126.879
592.4 | 447.4 | 127.9409 | 116.0705 |  |  |  |  | 592.4 | 447.4 | 130.7164 | 0.1956 | 592.4 | 447.4 | 126.879
592.6 | 447.6 | 127.8449 | 116.4544 |  |  |  |  | 592.6 | 447.6 | 130.7164 | 0.1956 | 592.6 | 447.6 | 126.783
592.8 | 447.8 | 127.9409 | 117.8939 |  |  |  |  | 592.8 | 447.8 | 130.7164 | 0.1956 | 592.8 | 447.8 | 126.783
593 | 448 | 127.9409 | 118.6617 |  |  |  |  | 593 | 448 | 130.8123 | 0.1956 | 593 | 448 | 126.879
593.2 | 448.2 | 127.9409 | 118.7576 |  |  |  |  | 593.2 | 448.2 | 130.7164 | 0.29155 | 593.2 | 448.2 | 126.783
593.4 | 448.4 | 127.9409 | 118.9495 |  |  |  |  | 593.4 | 448.4 | 130.7164 | 0.1956 | 593.4 | 448.4 | 126.879
593.6 | 448.6 | 127.8449 | 119.0455 |  |  |  |  | 593.6 | 448.6 | 130.6204 | 0.1956 | 593.6 | 448.6 | 126.879
593.8 | 448.8 | 127.8449 | 119.3334 |  |  |  |  | 593.8 | 448.8 | 130.7164 | 0.1956 | 593.8 | 448.8 | 126.783
594 | 449 | 127.8449 | 117.606 |  |  |  |  | 594 | 449 | 130.7164 | 0.1956 | 594 | 449 | 126.783
594.2 | 449.2 | 127.8449 | 117.3181 |  |  |  |  | 594.2 | 449.2 | 130.7164 | 0.1956 | 594.2 | 449.2 | 126.783
594.4 | 449.4 | 127.9409 | 117.4141 |  |  |  |  | 594.4 | 449.4 | 130.8123 | 0.1956 | 594.4 | 449.4 | 126.879
594.6 | 449.6 | 127.8449 | 117.606 |  |  |  |  | 594.6 | 449.6 | 130.7164 | 0.1956 | 594.6 | 449.6 | 126.879
594.8 | 449.8 | 127.8449 | 117.8939 |  |  |  |  | 594.8 | 449.8 | 130.7164 | 0.099605 | 594.8 | 449.8 | 126.879
595 | 450 | 127.8449 | 117.9899 |  |  |  |  | 595 | 450 | 130.7164 | 0.1956 | 595 | 450 | 126.783
595.2 | 450.2 | 127.8449 | 118.1818 |  |  |  |  | 595.2 | 450.2 | 130.6204 | 0.1956 | 595.2 | 450.2 | 126.879
595.4 | 450.4 | 127.8449 | 118.4697 |  |  |  |  | 595.4 | 450.4 | 130.7164 | 0.1956 | 595.4 | 450.4 | 126.783
595.6 | 450.6 | 127.8449 | 118.5657 |  |  |  |  | 595.6 | 450.6 | 130.6204 | 0.1956 | 595.6 | 450.6 | 126.783
595.8 | 450.8 | 127.9409 | 118.8536 |  |  |  |  | 595.8 | 450.8 | 130.7164 | 0.1956 | 595.8 | 450.8 | 126.783
596 | 451 | 127.8449 | 118.7576 |  |  |  |  | 596 | 451 | 130.6204 | 0.1956 | 596 | 451 | 126.783
596.2 | 451.2 | 127.8449 | 118.9495 |  |  |  |  | 596.2 | 451.2 | 130.6204 | 0.099605 | 596.2 | 451.2 | 126.879
596.4 | 451.4 | 127.8449 | 119.0455 |  |  |  |  | 596.4 | 451.4 | 130.7164 | 0.1956 | 596.4 | 451.4 | 126.783
596.6 | 451.6 | 127.749 | 119.0455 |  |  |  |  | 596.6 | 451.6 | 130.6204 | 0.1956 | 596.6 | 451.6 | 126.783
596.8 | 451.8 | 127.8449 | 119.3334 |  |  |  |  | 596.8 | 451.8 | 130.6204 | 0.1956 | 596.8 | 451.8 | 126.783
597 | 452 | 127.8449 | 119.4294 |  |  |  |  | 597 | 452 | 130.6204 | 0.1956 | 597 | 452 | 126.783
597.2 | 452.2 | 127.8449 | 119.5254 |  |  |  |  | 597.2 | 452.2 | 130.6204 | 0.1956 | 597.2 | 452.2 | 126.783
597.4 | 452.4 | 127.8449 | 119.5254 |  |  |  |  | 597.4 | 452.4 | 130.6204 | 0.1956 | 597.4 | 452.4 | 126.879
597.6 | 452.6 | 127.8449 | 119.6213 |  |  |  |  | 597.6 | 452.6 | 130.6204 | 0.1956 | 597.6 | 452.6 | 126.783
597.8 | 452.8 | 127.8449 | 119.7173 |  |  |  |  | 597.8 | 452.8 | 130.7164 | 0.29155 | 597.8 | 452.8 | 126.783
598 | 453 | 127.749 | 119.6213 |  |  |  |  | 598 | 453 | 130.6204 | 0.1956 | 598 | 453 | 126.783
598.2 | 453.2 | 127.8449 | 119.0455 |  |  |  |  | 598.2 | 453.2 | 130.7164 | 0.1956 | 598.2 | 453.2 | 126.783
598.4 | 453.4 | 127.749 | 119.3334 |  |  |  |  | 598.4 | 453.4 | 130.6204 | 0.1956 | 598.4 | 453.4 | 126.783
598.6 | 453.6 | 127.8449 | 119.4294 |  |  |  |  | 598.6 | 453.6 | 130.6204 | 0.1956 | 598.6 | 453.6 | 126.783
598.8 | 453.8 | 127.749 | 119.4294 |  |  |  |  | 598.8 | 453.8 | 130.6204 | 0.29155 | 598.8 | 453.8 | 126.687
599 | 454 | 127.8449 | 118.9495 |  |  |  |  | 599 | 454 | 130.7164 | 0.1956 | 599 | 454 | 126.783
599.2 | 454.2 | 127.8449 | 116.2625 |  |  |  |  | 599.2 | 454.2 | 130.6204 | 0.1956 | 599.2 | 454.2 | 126.783
599.4 | 454.4 | 127.8449 | 117.9899 |  |  |  |  | 599.4 | 454.4 | 130.6204 | 0.1956 | 599.4 | 454.4 | 126.783
599.6 | 454.6 | 127.8449 | 118.3738 |  |  |  |  | 599.6 | 454.6 | 130.7164 | 0.1956 | 599.6 | 454.6 | 126.783
599.8 | 454.8 | 127.749 | 118.4697 |  |  |  |  | 599.8 | 454.8 | 130.6204 | 0.099605 | 599.8 | 454.8 | 126.783
600 | 455 | 127.653 | 118.7576 |  |  |  |  | 600 | 455 | 130.5244 | 0.1956 | 600 | 455 | 126.687
600.2 | 455.2 | 127.749 | 118.9495 |  |  |  |  | 600.2 | 455.2 | 130.6204 | 0.29155 | 600.2 | 455.2 | 126.687
600.4 | 455.4 | 127.749 | 118.9495 |  |  |  |  | 600.4 | 455.4 | 130.5244 | 0.1956 | 600.4 | 455.4 | 126.687
600.6 | 455.6 | 127.749 | 118.6617 |  |  |  |  | 600.6 | 455.6 | 130.6204 | 0.1956 | 600.6 | 455.6 | 126.783
600.8 | 455.8 | 127.653 | 118.8536 |  |  |  |  | 600.8 | 455.8 | 130.6204 | 0.099605 | 600.8 | 455.8 | 126.783
601 | 456 | 127.653 | 119.0455 |  |  |  |  | 601 | 456 | 130.6204 | 0.1956 | 601 | 456 | 126.783
601.2 | 456.2 | 127.749 | 119.1415 |  |  |  |  | 601.2 | 456.2 | 130.6204 | 0.1956 | 601.2 | 456.2 | 126.783
601.4 | 456.4 | 127.653 | 119.2374 |  |  |  |  | 601.4 | 456.4 | 130.5244 | 0.1956 | 601.4 | 456.4 | 126.783
601.6 | 456.6 | 127.653 | 119.1415 |  |  |  |  | 601.6 | 456.6 | 130.6204 | 0.1956 | 601.6 | 456.6 | 126.783
601.8 | 456.8 | 127.653 | 119.2374 |  |  |  |  | 601.8 | 456.8 | 130.6204 | 0.1956 | 601.8 | 456.8 | 126.687
602 | 457 | 127.653 | 119.3334 |  |  |  |  | 602 | 457 | 130.6204 | 0.1956 | 602 | 457 | 126.687
602.2 | 457.2 | 127.749 | 119.4294 |  |  |  |  | 602.2 | 457.2 | 130.6204 | 0.1956 | 602.2 | 457.2 | 126.783
602.4 | 457.4 | 127.653 | 119.4294 |  |  |  |  | 602.4 | 457.4 | 130.5244 | 0.1956 | 602.4 | 457.4 | 126.687
602.6 | 457.6 | 127.749 | 119.6213 |  |  |  |  | 602.6 | 457.6 | 130.6204 | 0.1956 | 602.6 | 457.6 | 126.687
602.8 | 457.8 | 127.653 | 119.6213 |  |  |  |  | 602.8 | 457.8 | 130.6204 | 0.1956 | 602.8 | 457.8 | 126.687
603 | 458 | 127.749 | 119.8133 |  |  |  |  | 603 | 458 | 130.6204 | 0.1956 | 603 | 458 | 126.783
603.2 | 458.2 | 127.749 | 119.8133 |  |  |  |  | 603.2 | 458.2 | 130.5244 | 0.1956 | 603.2 | 458.2 | 126.687
603.4 | 458.4 | 127.749 | 119.6213 |  |  |  |  | 603.4 | 458.4 | 130.6204 | 0.1956 | 603.4 | 458.4 | 126.783
603.6 | 458.6 | 127.749 | 119.6213 |  |  |  |  | 603.6 | 458.6 | 130.5244 | 0.1956 | 603.6 | 458.6 | 126.687
603.8 | 458.8 | 127.749 | 119.7173 |  |  |  |  | 603.8 | 458.8 | 130.6204 | 0.1956 | 603.8 | 458.8 | 126.687
604 | 459 | 127.749 | 119.7173 |  |  |  |  | 604 | 459 | 130.5244 | 0.1956 | 604 | 459 | 126.687
604.2 | 459.2 | 127.8449 | 119.8133 |  |  |  |  | 604.2 | 459.2 | 130.6204 | 0.1956 | 604.2 | 459.2 | 126.687
604.4 | 459.4 | 127.8449 | 120.0052 |  |  |  |  | 604.4 | 459.4 | 130.6204 | 0.1956 | 604.4 | 459.4 | 126.783
604.6 | 459.6 | 127.8449 | 120.1012 |  |  |  |  | 604.6 | 459.6 | 130.5244 | 0.1956 | 604.6 | 459.6 | 126.687
604.8 | 459.8 | 127.749 | 120.1971 |  |  |  |  | 604.8 | 459.8 | 130.5244 | 0.1956 | 604.8 | 459.8 | 126.687
605 | 460 | 127.9409 | 120.6769 |  |  |  |  | 605 | 460 | 130.6204 | 0.1956 | 605 | 460 | 126.783
605.2 | 460.2 | 127.8449 | 120.9649 |  |  |  |  | 605.2 | 460.2 | 130.5244 | 0.1956 | 605.2 | 460.2 | 126.687
605.4 | 460.4 | 127.9409 | 121.0608 |  |  |  |  | 605.4 | 460.4 | 130.6204 | 0.1956 | 605.4 | 460.4 | 126.687
605.6 | 460.6 | 127.8449 | 121.2528 |  |  |  |  | 605.6 | 460.6 | 130.5244 | 0.1956 | 605.6 | 460.6 | 126.687
605.8 | 460.8 | 127.9409 | 121.3487 |  |  |  |  | 605.8 | 460.8 | 130.5244 | 0.1956 | 605.8 | 460.8 | 126.687
606 | 461 | 127.8449 | 121.3487 |  |  |  |  | 606 | 461 | 130.5244 | 0.1956 | 606 | 461 | 126.5911
606.2 | 461.2 | 127.8449 | 121.5407 |  |  |  |  | 606.2 | 461.2 | 130.5244 | 0.1956 | 606.2 | 461.2 | 126.687
606.4 | 461.4 | 127.8449 | 121.4447 |  |  |  |  | 606.4 | 461.4 | 130.5244 | 0.1956 | 606.4 | 461.4 | 126.687
606.6 | 461.6 | 127.8449 | 121.5407 |  |  |  |  | 606.6 | 461.6 | 130.5244 | 0.1956 | 606.6 | 461.6 | 126.687
606.8 | 461.8 | 127.8449 | 121.5407 |  |  |  |  | 606.8 | 461.8 | 130.5244 | 0.1956 | 606.8 | 461.8 | 126.687
607 | 462 | 127.749 | 121.4447 |  |  |  |  | 607 | 462 | 130.5244 | 0.1956 | 607 | 462 | 126.687
607.2 | 462.2 | 127.8449 | 121.5407 |  |  |  |  | 607.2 | 462.2 | 130.5244 | 0.1956 | 607.2 | 462.2 | 126.687
607.4 | 462.4 | 127.8449 | 121.7326 |  |  |  |  | 607.4 | 462.4 | 130.5244 | 0.1956 | 607.4 | 462.4 | 126.687
607.6 | 462.6 | 127.8449 | 121.9245 |  |  |  |  | 607.6 | 462.6 | 130.5244 | 0.29155 | 607.6 | 462.6 | 126.687
607.8 | 462.8 | 127.9409 | 122.1165 |  |  |  |  | 607.8 | 462.8 | 130.5244 | 0.1956 | 607.8 | 462.8 | 126.783
608 | 463 | 127.8449 | 122.1165 |  |  |  |  | 608 | 463 | 130.4284 | 0.1956 | 608 | 463 | 126.5911
608.2 | 463.2 | 127.9409 | 122.2124 |  |  |  |  | 608.2 | 463.2 | 130.5244 | 0.1956 | 608.2 | 463.2 | 126.687
608.4 | 463.4 | 127.9409 | 122.2124 |  |  |  |  | 608.4 | 463.4 | 130.4284 | 0.1956 | 608.4 | 463.4 | 126.687
608.6 | 463.6 | 127.9409 | 122.4044 |  |  |  |  | 608.6 | 463.6 | 130.5244 | 0.1956 | 608.6 | 463.6 | 126.687
608.8 | 463.8 | 127.9409 | 122.5963 |  |  |  |  | 608.8 | 463.8 | 130.6204 | 0.1956 | 608.8 | 463.8 | 126.687
609 | 464 | 127.9409 | 122.6923 |  |  |  |  | 609 | 464 | 130.5244 | 0.1956 | 609 | 464 | 126.5911
609.2 | 464.2 | 127.9409 | 122.6923 |  |  |  |  | 609.2 | 464.2 | 130.5244 | 0.1956 | 609.2 | 464.2 | 126.5911
609.4 | 464.4 | 127.9409 | 122.7882 |  |  |  |  | 609.4 | 464.4 | 130.5244 | 0.1956 | 609.4 | 464.4 | 126.5911
609.6 | 464.6 | 127.9409 | 122.7882 |  |  |  |  | 609.6 | 464.6 | 130.4284 | 0.1956 | 609.6 | 464.6 | 126.5911
609.8 | 464.8 | 127.8449 | 122.8842 |  |  |  |  | 609.8 | 464.8 | 130.5244 | 0.1956 | 609.8 | 464.8 | 126.5911
610 | 465 | 127.8449 | 122.9802 |  |  |  |  | 610 | 465 | 130.4284 | 0.1956 | 610 | 465 | 126.5911
610.2 | 465.2 | 127.9409 | 123.1721 |  |  |  |  | 610.2 | 465.2 | 130.5244 | 0.1956 | 610.2 | 465.2 | 126.687
610.4 | 465.4 | 127.9409 | 123.0762 |  |  |  |  | 610.4 | 465.4 | 130.5244 | 0.1956 | 610.4 | 465.4 | 126.687
610.6 | 465.6 | 127.9409 | 123.1721 |  |  |  |  | 610.6 | 465.6 | 130.5244 | 0.1956 | 610.6 | 465.6 | 126.687
610.8 | 465.8 | 127.8449 | 123.1721 |  |  |  |  | 610.8 | 465.8 | 130.4284 | 0.1956 | 610.8 | 465.8 | 126.5911
611 | 466 | 127.8449 | 123.1721 |  |  |  |  | 611 | 466 | 130.3325 | 0.1956 | 611 | 466 | 126.5911
611.2 | 466.2 | 127.9409 | 123.2681 |  |  |  |  | 611.2 | 466.2 | 130.4284 | 0.1956 | 611.2 | 466.2 | 126.5911
611.4 | 466.4 | 127.9409 | 123.3641 |  |  |  |  | 611.4 | 466.4 | 130.4284 | 0.1956 | 611.4 | 466.4 | 126.5911
611.6 | 466.6 | 127.9409 | 123.3641 |  |  |  |  | 611.6 | 466.6 | 130.5244 | 0.1956 | 611.6 | 466.6 | 126.5911
611.8 | 466.8 | 128.0369 | 123.46 |  |  |  |  | 611.8 | 466.8 | 130.4284 | 0.1956 | 611.8 | 466.8 | 126.5911
612 | 467 | 127.8449 | 123.3641 |  |  |  |  | 612 | 467 | 130.3325 | 0.29155 | 612 | 467 | 126.4951
612.2 | 467.2 | 127.9409 | 123.46 |  |  |  |  | 612.2 | 467.2 | 130.4284 | 0.1956 | 612.2 | 467.2 | 126.4951
612.4 | 467.4 | 128.0369 | 123.556 |  |  |  |  | 612.4 | 467.4 | 130.4284 | 0.1956 | 612.4 | 467.4 | 126.5911
612.6 | 467.6 | 128.0369 | 123.6519 |  |  |  |  | 612.6 | 467.6 | 130.4284 | 0.1956 | 612.6 | 467.6 | 126.5911
612.8 | 467.8 | 128.0369 | 123.6519 |  |  |  |  | 612.8 | 467.8 | 130.4284 | 0.1956 | 612.8 | 467.8 | 126.5911
613 | 468 | 128.1329 | 123.7479 |  |  |  |  | 613 | 468 | 130.5244 | 0.1956 | 613 | 468 | 126.5911
613.2 | 468.2 | 128.1329 | 123.8439 |  |  |  |  | 613.2 | 468.2 | 130.4284 | 0.1956 | 613.2 | 468.2 | 126.687
613.4 | 468.4 | 128.0369 | 123.8439 |  |  |  |  | 613.4 | 468.4 | 130.4284 | 0.1956 | 613.4 | 468.4 | 126.5911
613.6 | 468.6 | 128.1329 | 123.9398 |  |  |  |  | 613.6 | 468.6 | 130.4284 | 0.1956 | 613.6 | 468.6 | 126.5911
613.8 | 468.8 | 128.1329 | 124.0358 |  |  |  |  | 613.8 | 468.8 | 130.4284 | 0.1956 | 613.8 | 468.8 | 126.5911
614 | 469 | 128.1329 | 124.0358 |  |  |  |  | 614 | 469 | 130.4284 | 0.1956 | 614 | 469 | 126.5911
614.2 | 469.2 | 128.1329 | 124.0358 |  |  |  |  | 614.2 | 469.2 | 130.4284 | 0.099605 | 614.2 | 469.2 | 126.5911
614.4 | 469.4 | 128.1329 | 124.0358 |  |  |  |  | 614.4 | 469.4 | 130.4284 | 0.1956 | 614.4 | 469.4 | 126.5911
614.6 | 469.6 | 128.1329 | 124.2277 |  |  |  |  | 614.6 | 469.6 | 130.4284 | 0.29155 | 614.6 | 469.6 | 126.5911
614.8 | 469.8 | 128.1329 | 124.2277 |  |  |  |  | 614.8 | 469.8 | 130.4284 | 0.29155 | 614.8 | 469.8 | 126.5911
615 | 470 | 128.1329 | 124.3237 |  |  |  |  | 615 | 470 | 130.4284 | 0.1956 | 615 | 470 | 126.5911
615.2 | 470.2 | 128.1329 | 124.3237 |  |  |  |  | 615.2 | 470.2 | 130.4284 | 0.1956 | 615.2 | 470.2 | 126.5911
615.4 | 470.4 | 128.1329 | 124.4197 |  |  |  |  | 615.4 | 470.4 | 130.5244 | 0.099605 | 615.4 | 470.4 | 126.5911
615.6 | 470.6 | 128.1329 | 124.3237 |  |  |  |  | 615.6 | 470.6 | 130.4284 | 0.1956 | 615.6 | 470.6 | 126.5911
615.8 | 470.8 | 128.0369 | 124.5157 |  |  |  |  | 615.8 | 470.8 | 130.4284 | 0.1956 | 615.8 | 470.8 | 126.5911
616 | 471 | 128.1329 | 124.3237 |  |  |  |  | 616 | 471 | 130.4284 | 0.1956 | 616 | 471 | 126.4951
616.2 | 471.2 | 128.1329 | 124.4197 |  |  |  |  | 616.2 | 471.2 | 130.3325 | 0.1956 | 616.2 | 471.2 | 126.4951
616.4 | 471.4 | 128.2288 | 124.5157 |  |  |  |  | 616.4 | 471.4 | 130.4284 | 0.1956 | 616.4 | 471.4 | 126.5911
616.6 | 471.6 | 128.1329 | 124.6116 |  |  |  |  | 616.6 | 471.6 | 130.4284 | 0.1956 | 616.6 | 471.6 | 126.5911
616.8 | 471.8 | 128.2288 | 124.6116 |  |  |  |  | 616.8 | 471.8 | 130.4284 | 0.099605 | 616.8 | 471.8 | 126.5911
617 | 472 | 128.2288 | 124.7076 |  |  |  |  | 617 | 472 | 130.4284 | 0.1956 | 617 | 472 | 126.5911
617.2 | 472.2 | 128.2288 | 124.7076 |  |  |  |  | 617.2 | 472.2 | 130.4284 | 0.1956 | 617.2 | 472.2 | 126.5911
617.4 | 472.4 | 128.3248 | 124.8036 |  |  |  |  | 617.4 | 472.4 | 130.4284 | 0.1956 | 617.4 | 472.4 | 126.5911
617.6 | 472.6 | 128.3248 | 124.8036 |  |  |  |  | 617.6 | 472.6 | 130.4284 | 0.1956 | 617.6 | 472.6 | 126.4951
617.8 | 472.8 | 128.3248 | 124.8995 |  |  |  |  | 617.8 | 472.8 | 130.4284 | 0.1956 | 617.8 | 472.8 | 126.5911
618 | 473 | 128.2288 | 124.8995 |  |  |  |  | 618 | 473 | 130.3325 | 0.1956 | 618 | 473 | 126.4951
618.2 | 473.2 | 128.3248 | 124.9955 |  |  |  |  | 618.2 | 473.2 | 130.4284 | 0.1956 | 618.2 | 473.2 | 126.5911
618.4 | 473.4 | 128.3248 | 125.0915 |  |  |  |  | 618.4 | 473.4 | 130.4284 | 0.1956 | 618.4 | 473.4 | 126.5911
618.6 | 473.6 | 128.3248 | 125.0915 |  |  |  |  | 618.6 | 473.6 | 130.4284 | 0.1956 | 618.6 | 473.6 | 126.4951
618.8 | 473.8 | 128.3248 | 125.1874 |  |  |  |  | 618.8 | 473.8 | 130.4284 | 0.1956 | 618.8 | 473.8 | 126.4951
619 | 474 | 128.3248 | 125.1874 |  |  |  |  | 619 | 474 | 130.4284 | 0.1956 | 619 | 474 | 126.5911
619.2 | 474.2 | 128.4208 | 125.2834 |  |  |  |  | 619.2 | 474.2 | 130.4284 | 0.29155 | 619.2 | 474.2 | 126.5911
619.4 | 474.4 | 128.3248 | 125.2834 |  |  |  |  | 619.4 | 474.4 | 130.4284 | 0.29155 | 619.4 | 474.4 | 126.5911
619.6 | 474.6 | 128.3248 | 125.1874 |  |  |  |  | 619.6 | 474.6 | 130.3325 | 0.1956 | 619.6 | 474.6 | 126.4951
619.8 | 474.8 | 128.3248 | 125.2834 |  |  |  |  | 619.8 | 474.8 | 130.4284 | 0.29155 | 619.8 | 474.8 | 126.4951
620 | 475 | 128.2288 | 125.2834 |  |  |  |  | 620 | 475 | 130.3325 | 0.1956 | 620 | 475 | 126.4951
620.2 | 475.2 | 128.3248 | 125.2834 |  |  |  |  | 620.2 | 475.2 | 130.4284 | 0.1956 | 620.2 | 475.2 | 126.5911
620.4 | 475.4 | 128.3248 | 125.2834 |  |  |  |  | 620.4 | 475.4 | 130.3325 | 0.1956 | 620.4 | 475.4 | 126.3991
620.6 | 475.6 | 128.3248 | 125.2834 |  |  |  |  | 620.6 | 475.6 | 130.3325 | 0.1956 | 620.6 | 475.6 | 126.4951
620.8 | 475.8 | 128.3248 | 125.3793 |  |  |  |  | 620.8 | 475.8 | 130.3325 | 0.1956 | 620.8 | 475.8 | 126.4951
621 | 476 | 128.3248 | 125.4753 |  |  |  |  | 621 | 476 | 130.3325 | 0.1956 | 621 | 476 | 126.4951
621.2 | 476.2 | 128.4208 | 125.4753 |  |  |  |  | 621.2 | 476.2 | 130.3325 | 0.1956 | 621.2 | 476.2 | 126.5911
621.4 | 476.4 | 128.3248 | 125.5713 |  |  |  |  | 621.4 | 476.4 | 130.3325 | 0.1956 | 621.4 | 476.4 | 126.3991
621.6 | 476.6 | 128.3248 | 125.5713 |  |  |  |  | 621.6 | 476.6 | 130.3325 | 0.29155 | 621.6 | 476.6 | 126.4951
621.8 | 476.8 | 128.3248 | 125.5713 |  |  |  |  | 621.8 | 476.8 | 130.3325 | 0.1956 | 621.8 | 476.8 | 126.4951
622 | 477 | 128.4208 | 125.5713 |  |  |  |  | 622 | 477 | 130.3325 | 0.1956 | 622 | 477 | 126.4951
622.2 | 477.2 | 128.4208 | 125.6673 |  |  |  |  | 622.2 | 477.2 | 130.3325 | 0.1956 | 622.2 | 477.2 | 126.4951
622.4 | 477.4 | 128.3248 | 125.5713 |  |  |  |  | 622.4 | 477.4 | 130.3325 | 0.1956 | 622.4 | 477.4 | 126.4951
622.6 | 477.6 | 128.3248 | 125.6673 |  |  |  |  | 622.6 | 477.6 | 130.3325 | 0.1956 | 622.6 | 477.6 | 126.3991
622.8 | 477.8 | 128.3248 | 125.6673 |  |  |  |  | 622.8 | 477.8 | 130.2365 | 0.1956 | 622.8 | 477.8 | 126.3991
623 | 478 | 128.3248 | 125.6673 |  |  |  |  | 623 | 478 | 130.3325 | 0.1956 | 623 | 478 | 126.3991
623.2 | 478.2 | 128.3248 | 125.7632 |  |  |  |  | 623.2 | 478.2 | 130.3325 | 0.1956 | 623.2 | 478.2 | 126.4951
623.4 | 478.4 | 128.3248 | 125.7632 |  |  |  |  | 623.4 | 478.4 | 130.3325 | 0.1956 | 623.4 | 478.4 | 126.4951
623.6 | 478.6 | 128.3248 | 125.7632 |  |  |  |  | 623.6 | 478.6 | 130.3325 | 0.1956 | 623.6 | 478.6 | 126.3991
623.8 | 478.8 | 128.2288 | 125.7632 |  |  |  |  | 623.8 | 478.8 | 130.2365 | 0.1956 | 623.8 | 478.8 | 126.3991
624 | 479 | 128.2288 | 125.7632 |  |  |  |  | 624 | 479 | 130.3325 | 0.1956 | 624 | 479 | 126.3991
624.2 | 479.2 | 128.3248 | 125.8592 |  |  |  |  | 624.2 | 479.2 | 130.3325 | 0.1956 | 624.2 | 479.2 | 126.4951
624.4 | 479.4 | 128.3248 | 125.9552 |  |  |  |  | 624.4 | 479.4 | 130.3325 | 0.1956 | 624.4 | 479.4 | 126.4951
624.6 | 479.6 | 128.4208 | 125.8592 |  |  |  |  | 624.6 | 479.6 | 130.3325 | 0.29155 | 624.6 | 479.6 | 126.4951
624.8 | 479.8 | 128.3248 | 125.9552 |  |  |  |  | 624.8 | 479.8 | 130.3325 | 0.1956 | 624.8 | 479.8 | 126.4951
625 | 480 | 128.3248 | 125.9552 |  |  |  |  | 625 | 480 | 130.3325 | 0.1956 | 625 | 480 | 126.4951
625.2 | 480.2 | 128.4208 | 125.9552 |  |  |  |  | 625.2 | 480.2 | 130.3325 | 0.1956 | 625.2 | 480.2 | 126.3991
625.4 | 480.4 | 128.4208 | 125.9552 |  |  |  |  | 625.4 | 480.4 | 130.3325 | 0.1956 | 625.4 | 480.4 | 126.3991
625.6 | 480.6 | 128.4208 | 126.0511 |  |  |  |  | 625.6 | 480.6 | 130.3325 | 0.1956 | 625.6 | 480.6 | 126.4951
625.8 | 480.8 | 128.4208 | 126.0511 |  |  |  |  | 625.8 | 480.8 | 130.4284 | 0.1956 | 625.8 | 480.8 | 126.3991
626 | 481 | 128.4208 | 125.9552 |  |  |  |  | 626 | 481 | 130.3325 | 0.1956 | 626 | 481 | 126.4951
626.2 | 481.2 | 128.4208 | 126.0511 |  |  |  |  | 626.2 | 481.2 | 130.3325 | 0.1956 | 626.2 | 481.2 | 126.4951
626.4 | 481.4 | 128.5167 | 126.1471 |  |  |  |  | 626.4 | 481.4 | 130.3325 | 0.1956 | 626.4 | 481.4 | 126.4951
626.6 | 481.6 | 128.5167 | 126.1471 |  |  |  |  | 626.6 | 481.6 | 130.4284 | 0.1956 | 626.6 | 481.6 | 126.4951
626.8 | 481.8 | 128.5167 | 126.1471 |  |  |  |  | 626.8 | 481.8 | 130.3325 | 0.1956 | 626.8 | 481.8 | 126.4951
627 | 482 | 128.5167 | 126.2431 |  |  |  |  | 627 | 482 | 130.4284 | 0.1956 | 627 | 482 | 126.5911
627.2 | 482.2 | 128.4208 | 126.2431 |  |  |  |  | 627.2 | 482.2 | 130.4284 | 0.1956 | 627.2 | 482.2 | 126.4951
627.4 | 482.4 | 128.5167 | 126.2431 |  |  |  |  | 627.4 | 482.4 | 130.4284 | 0.1956 | 627.4 | 482.4 | 126.4951
627.6 | 482.6 | 128.5167 | 126.2431 |  |  |  |  | 627.6 | 482.6 | 130.3325 | 0.1956 | 627.6 | 482.6 | 126.4951
627.8 | 482.8 | 128.5167 | 126.339 |  |  |  |  | 627.8 | 482.8 | 130.3325 | 0.1956 | 627.8 | 482.8 | 126.4951
628 | 483 | 128.5167 | 126.2431 |  |  |  |  | 628 | 483 | 130.3325 | 0.1956 | 628 | 483 | 126.4951
628.2 | 483.2 | 128.5167 | 126.339 |  |  |  |  | 628.2 | 483.2 | 130.3325 | 0.1956 | 628.2 | 483.2 | 126.3991
628.4 | 483.4 | 128.5167 | 126.339 |  |  |  |  | 628.4 | 483.4 | 130.3325 | 0.1956 | 628.4 | 483.4 | 126.4951
628.6 | 483.6 | 128.5167 | 126.339 |  |  |  |  | 628.6 | 483.6 | 130.3325 | 0.099605 | 628.6 | 483.6 | 126.3991
628.8 | 483.8 | 128.5167 | 126.339 |  |  |  |  | 628.8 | 483.8 | 130.3325 | 0.29155 | 628.8 | 483.8 | 126.4951
629 | 484 | 128.5167 | 126.339 |  |  |  |  | 629 | 484 | 130.3325 | 0.1956 | 629 | 484 | 126.4951
629.2 | 484.2 | 128.5167 | 126.339 |  |  |  |  | 629.2 | 484.2 | 130.3325 | 0.1956 | 629.2 | 484.2 | 126.4951
629.4 | 484.4 | 128.5167 | 126.339 |  |  |  |  | 629.4 | 484.4 | 130.4284 | 0.1956 | 629.4 | 484.4 | 126.4951
629.6 | 484.6 | 128.6127 | 126.435 |  |  |  |  | 629.6 | 484.6 | 130.4284 | 0.29155 | 629.6 | 484.6 | 126.4951
629.8 | 484.8 | 128.6127 | 126.435 |  |  |  |  | 629.8 | 484.8 | 130.4284 | 0.1956 | 629.8 | 484.8 | 126.4951
630 | 485 | 128.5167 | 126.435 |  |  |  |  | 630 | 485 | 130.3325 | 0.1956 | 630 | 485 | 126.4951
630.2 | 485.2 | 128.5167 | 126.435 |  |  |  |  | 630.2 | 485.2 | 130.4284 | 0.29155 | 630.2 | 485.2 | 126.4951
630.4 | 485.4 | 128.5167 | 126.435 |  |  |  |  | 630.4 | 485.4 | 130.4284 | 0.1956 | 630.4 | 485.4 | 126.5911
630.6 | 485.6 | 128.5167 | 126.435 |  |  |  |  | 630.6 | 485.6 | 130.3325 | 0.1956 | 630.6 | 485.6 | 126.4951
630.8 | 485.8 | 128.5167 | 126.531 |  |  |  |  | 630.8 | 485.8 | 130.4284 | 0.1956 | 630.8 | 485.8 | 126.4951
631 | 486 | 128.5167 | 126.531 |  |  |  |  | 631 | 486 | 130.3325 | 0.29155 | 631 | 486 | 126.4951
631.2 | 486.2 | 128.5167 | 126.435 |  |  |  |  | 631.2 | 486.2 | 130.3325 | 0.1956 | 631.2 | 486.2 | 126.4951
631.4 | 486.4 | 128.4208 | 126.435 |  |  |  |  | 631.4 | 486.4 | 130.3325 | 0.1956 | 631.4 | 486.4 | 126.3991
631.6 | 486.6 | 128.5167 | 126.435 |  |  |  |  | 631.6 | 486.6 | 130.3325 | 0.1956 | 631.6 | 486.6 | 126.3991
631.8 | 486.8 | 128.6127 | 126.531 |  |  |  |  | 631.8 | 486.8 | 130.3325 | 0.1956 | 631.8 | 486.8 | 126.4951
632 | 487 | 128.5167 | 126.531 |  |  |  |  | 632 | 487 | 130.3325 | 0.29155 | 632 | 487 | 126.3991
632.2 | 487.2 | 128.5167 | 126.6269 |  |  |  |  | 632.2 | 487.2 | 130.3325 | 0.1956 | 632.2 | 487.2 | 126.4951
632.4 | 487.4 | 128.5167 | 126.531 |  |  |  |  | 632.4 | 487.4 | 130.3325 | 0.1956 | 632.4 | 487.4 | 126.4951
632.6 | 487.6 | 128.5167 | 126.531 |  |  |  |  | 632.6 | 487.6 | 130.3325 | 0.1956 | 632.6 | 487.6 | 126.4951
632.8 | 487.8 | 128.5167 | 126.6269 |  |  |  |  | 632.8 | 487.8 | 130.3325 | 0.1956 | 632.8 | 487.8 | 126.4951
633 | 488 | 128.5167 | 126.531 |  |  |  |  | 633 | 488 | 130.3325 | 0.1956 | 633 | 488 | 126.4951
633.2 | 488.2 | 128.5167 | 126.6269 |  |  |  |  | 633.2 | 488.2 | 130.3325 | 0.1956 | 633.2 | 488.2 | 126.4951
633.4 | 488.4 | 128.5167 | 126.6269 |  |  |  |  | 633.4 | 488.4 | 130.3325 | 0.1956 | 633.4 | 488.4 | 126.3991
633.6 | 488.6 | 128.6127 | 126.6269 |  |  |  |  | 633.6 | 488.6 | 130.4284 | 0.1956 | 633.6 | 488.6 | 126.4951
633.8 | 488.8 | 128.5167 | 126.531 |  |  |  |  | 633.8 | 488.8 | 130.3325 | 0.29155 | 633.8 | 488.8 | 126.4951
634 | 489 | 128.4208 | 126.531 |  |  |  |  | 634 | 489 | 130.3325 | 0.1956 | 634 | 489 | 126.3991
634.2 | 489.2 | 128.5167 | 126.7229 |  |  |  |  | 634.2 | 489.2 | 130.3325 | 0.1956 | 634.2 | 489.2 | 126.4951
634.4 | 489.4 | 128.5167 | 126.6269 |  |  |  |  | 634.4 | 489.4 | 130.3325 | 0.1956 | 634.4 | 489.4 | 126.4951
634.6 | 489.6 | 128.5167 | 126.6269 |  |  |  |  | 634.6 | 489.6 | 130.3325 | 0.1956 | 634.6 | 489.6 | 126.4951
634.8 | 489.8 | 128.5167 | 126.6269 |  |  |  |  | 634.8 | 489.8 | 130.3325 | 0.1956 | 634.8 | 489.8 | 126.4951
635 | 490 | 128.5167 | 126.6269 |  |  |  |  | 635 | 490 | 130.3325 | 0.1956 | 635 | 490 | 126.4951
635.2 | 490.2 | 128.5167 | 126.6269 |  |  |  |  | 635.2 | 490.2 | 130.3325 | 0.1956 | 635.2 | 490.2 | 126.4951
635.4 | 490.4 | 128.6127 | 126.7229 |  |  |  |  | 635.4 | 490.4 | 130.3325 | 0.1956 | 635.4 | 490.4 | 126.4951
635.6 | 490.6 | 128.6127 | 126.7229 |  |  |  |  | 635.6 | 490.6 | 130.3325 | 0.1956 | 635.6 | 490.6 | 126.5911
635.8 | 490.8 | 128.6127 | 126.7229 |  |  |  |  | 635.8 | 490.8 | 130.3325 | 0.29155 | 635.8 | 490.8 | 126.4951
636 | 491 | 128.5167 | 126.6269 |  |  |  |  | 636 | 491 | 130.3325 | 0.29155 | 636 | 491 | 126.3991
636.2 | 491.2 | 128.6127 | 126.7229 |  |  |  |  | 636.2 | 491.2 | 130.4284 | 0.1956 | 636.2 | 491.2 | 126.4951
636.4 | 491.4 | 128.5167 | 126.7229 |  |  |  |  | 636.4 | 491.4 | 130.3325 | 0.1956 | 636.4 | 491.4 | 126.4951
636.6 | 491.6 | 128.5167 | 126.7229 |  |  |  |  | 636.6 | 491.6 | 130.3325 | 0.29155 | 636.6 | 491.6 | 126.4951
636.8 | 491.8 | 128.5167 | 126.7229 |  |  |  |  | 636.8 | 491.8 | 130.3325 | 0.1956 | 636.8 | 491.8 | 126.3991
637 | 492 | 128.5167 | 126.6269 |  |  |  |  | 637 | 492 | 130.3325 | 0.1956 | 637 | 492 | 126.3991
637.2 | 492.2 | 128.5167 | 126.7229 |  |  |  |  | 637.2 | 492.2 | 130.3325 | 0.1956 | 637.2 | 492.2 | 126.4951
637.4 | 492.4 | 128.5167 | 126.7229 |  |  |  |  | 637.4 | 492.4 | 130.3325 | 0.1956 | 637.4 | 492.4 | 126.4951
637.6 | 492.6 | 128.5167 | 126.8188 |  |  |  |  | 637.6 | 492.6 | 130.3325 | 0.1956 | 637.6 | 492.6 | 126.4951
637.8 | 492.8 | 128.4208 | 126.6269 |  |  |  |  | 637.8 | 492.8 | 130.3325 | 0.29155 | 637.8 | 492.8 | 126.4951
638 | 493 | 128.5167 | 126.7229 |  |  |  |  | 638 | 493 | 130.3325 | 0.1956 | 638 | 493 | 126.3991
638.2 | 493.2 | 128.5167 | 126.7229 |  |  |  |  | 638.2 | 493.2 | 130.3325 | 0.1956 | 638.2 | 493.2 | 126.3991
638.4 | 493.4 | 128.5167 | 126.7229 |  |  |  |  | 638.4 | 493.4 | 130.3325 | 0.29155 | 638.4 | 493.4 | 126.4951
638.6 | 493.6 | 128.5167 | 126.7229 |  |  |  |  | 638.6 | 493.6 | 130.4284 | 0.1956 | 638.6 | 493.6 | 126.4951
638.8 | 493.8 | 128.5167 | 126.6269 |  |  |  |  | 638.8 | 493.8 | 130.3325 | 0.1956 | 638.8 | 493.8 | 126.4951
639 | 494 | 128.5167 | 126.7229 |  |  |  |  | 639 | 494 | 130.3325 | 0.1956 | 639 | 494 | 126.4951
639.2 | 494.2 | 128.4208 | 126.6269 |  |  |  |  | 639.2 | 494.2 | 130.3325 | 0.1956 | 639.2 | 494.2 | 126.4951
639.4 | 494.4 | 128.4208 | 126.7229 |  |  |  |  | 639.4 | 494.4 | 130.3325 | 0.1956 | 639.4 | 494.4 | 126.5911
639.6 | 494.6 | 128.4208 | 126.7229 |  |  |  |  | 639.6 | 494.6 | 130.4284 | 0.1956 | 639.6 | 494.6 | 126.4951
639.8 | 494.8 | 128.4208 | 126.7229 |  |  |  |  | 639.8 | 494.8 | 130.3325 | 0.1956 | 639.8 | 494.8 | 126.4951
640 | 495 | 128.3248 | 126.6269 |  |  |  |  | 640 | 495 | 130.3325 | 0.1956 | 640 | 495 | 126.3991
640.2 | 495.2 | 128.4208 | 126.6269 |  |  |  |  | 640.2 | 495.2 | 130.3325 | 0.29155 | 640.2 | 495.2 | 126.4951
640.4 | 495.4 | 128.4208 | 126.7229 |  |  |  |  | 640.4 | 495.4 | 130.3325 | 0.1956 | 640.4 | 495.4 | 126.4951
640.6 | 495.6 | 128.4208 | 126.7229 |  |  |  |  | 640.6 | 495.6 | 130.4284 | 0.1956 | 640.6 | 495.6 | 126.5911
640.8 | 495.8 | 128.3248 | 126.6269 |  |  |  |  | 640.8 | 495.8 | 130.4284 | 0.1956 | 640.8 | 495.8 | 126.4951
641 | 496 | 128.3248 | 126.7229 |  |  |  |  | 641 | 496 | 130.3325 | 0.1956 | 641 | 496 | 126.4951
641.2 | 496.2 | 128.4208 | 126.7229 |  |  |  |  | 641.2 | 496.2 | 130.3325 | 0.29155 | 641.2 | 496.2 | 126.5911
641.4 | 496.4 | 128.4208 | 126.8188 |  |  |  |  | 641.4 | 496.4 | 130.4284 | 0.1956 | 641.4 | 496.4 | 126.5911
641.6 | 496.6 | 128.4208 | 126.8188 |  |  |  |  | 641.6 | 496.6 | 130.3325 | 0.1956 | 641.6 | 496.6 | 126.5911
641.8 | 496.8 | 128.5167 | 126.8188 |  |  |  |  | 641.8 | 496.8 | 130.4284 | 0.29155 | 641.8 | 496.8 | 126.5911
642 | 497 | 128.4208 | 126.7229 |  |  |  |  | 642 | 497 | 130.4284 | 0.29155 | 642 | 497 | 126.5911
642.2 | 497.2 | 128.4208 | 126.7229 |  |  |  |  | 642.2 | 497.2 | 130.4284 | 0.1956 | 642.2 | 497.2 | 126.5911
642.4 | 497.4 | 128.4208 | 126.8188 |  |  |  |  | 642.4 | 497.4 | 130.5244 | 0.1956 | 642.4 | 497.4 | 126.5911
642.6 | 497.6 | 128.5167 | 126.8188 |  |  |  |  | 642.6 | 497.6 | 130.3325 | 0.1956 | 642.6 | 497.6 | 126.5911
642.8 | 497.8 | 128.4208 | 126.7229 |  |  |  |  | 642.8 | 497.8 | 130.4284 | 0.1956 | 642.8 | 497.8 | 126.5911
643 | 498 | 128.4208 | 126.7229 |  |  |  |  | 643 | 498 | 130.4284 | 0.1956 | 643 | 498 | 126.5911
643.2 | 498.2 | 128.4208 | 126.7229 |  |  |  |  | 643.2 | 498.2 | 130.4284 | 0.1956 | 643.2 | 498.2 | 126.5911
643.4 | 498.4 | 128.5167 | 126.8188 |  |  |  |  | 643.4 | 498.4 | 130.4284 | 0.1956 | 643.4 | 498.4 | 126.5911
643.6 | 498.6 | 128.4208 | 126.7229 |  |  |  |  | 643.6 | 498.6 | 130.4284 | 0.29155 | 643.6 | 498.6 | 126.5911
643.8 | 498.8 | 128.3248 | 126.7229 |  |  |  |  | 643.8 | 498.8 | 130.4284 | 0.1956 | 643.8 | 498.8 | 126.5911
644 | 499 | 128.3248 | 126.7229 |  |  |  |  | 644 | 499 | 130.4284 | 0.1956 | 644 | 499 | 126.4951
644.2 | 499.2 | 128.4208 | 126.7229 |  |  |  |  | 644.2 | 499.2 | 130.4284 | 0.1956 | 644.2 | 499.2 | 126.4951
644.4 | 499.4 | 128.4208 | 126.7229 |  |  |  |  | 644.4 | 499.4 | 130.5244 | 0.1956 | 644.4 | 499.4 | 126.5911
644.6 | 499.6 | 128.3248 | 126.7229 |  |  |  |  | 644.6 | 499.6 | 130.4284 | 0.1956 | 644.6 | 499.6 | 126.5911
644.8 | 499.8 | 128.3248 | 126.6269 |  |  |  |  | 644.8 | 499.8 | 130.3325 | 0.29155 | 644.8 | 499.8 | 126.5911
645 | 500 | 128.2288 | 126.7229 |  |  |  |  | 645 | 500 | 130.3325 | 0.1956 | 645 | 500 | 126.5911
645.2 | 500.2 | 128.3248 | 126.6269 |  |  |  |  | 645.2 | 500.2 | 130.3325 | 0.1956 | 645.2 | 500.2 | 126.4951
645.4 | 500.4 | 128.3248 | 126.6269 |  |  |  |  | 645.4 | 500.4 | 130.4284 | 0.29155 | 645.4 | 500.4 | 126.5911
645.6 | 500.6 | 128.3248 | 126.6269 |  |  |  |  | 645.6 | 500.6 | 130.3325 | 0.1956 | 645.6 | 500.6 | 126.5911
645.8 | 500.8 | 128.3248 | 126.6269 |  |  |  |  | 645.8 | 500.8 | 130.4284 | 0.1956 | 645.8 | 500.8 | 126.5911
646 | 501 | 128.2288 | 126.531 |  |  |  |  | 646 | 501 | 130.4284 | 0.1956 | 646 | 501 | 126.5911
646.2 | 501.2 | 128.3248 | 126.6269 |  |  |  |  | 646.2 | 501.2 | 130.4284 | 0.29155 | 646.2 | 501.2 | 126.5911
646.4 | 501.4 | 128.2288 | 126.531 |  |  |  |  | 646.4 | 501.4 | 130.4284 | 0.1956 | 646.4 | 501.4 | 126.5911
646.6 | 501.6 | 128.2288 | 126.531 |  |  |  |  | 646.6 | 501.6 | 130.4284 | 0.1956 | 646.6 | 501.6 | 126.5911
646.8 | 501.8 | 128.2288 | 126.531 |  |  |  |  | 646.8 | 501.8 | 130.4284 | 0.1956 | 646.8 | 501.8 | 126.5911
647 | 502 | 128.1329 | 126.6269 |  |  |  |  | 647 | 502 | 130.3325 | 0.29155 | 647 | 502 | 126.4951
647.2 | 502.2 | 128.1329 | 126.6269 |  |  |  |  | 647.2 | 502.2 | 130.3325 | 0.29155 | 647.2 | 502.2 | 126.5911
647.4 | 502.4 | 128.1329 | 126.531 |  |  |  |  | 647.4 | 502.4 | 130.3325 | 0.1956 | 647.4 | 502.4 | 126.4951
647.6 | 502.6 | 128.2288 | 126.531 |  |  |  |  | 647.6 | 502.6 | 130.3325 | 0.1956 | 647.6 | 502.6 | 126.4951
647.8 | 502.8 | 128.1329 | 126.6269 |  |  |  |  | 647.8 | 502.8 | 130.3325 | 0.1956 | 647.8 | 502.8 | 126.5911
648 | 503 | 128.0369 | 126.6269 |  |  |  |  | 648 | 503 | 130.3325 | 0.1956 | 648 | 503 | 126.4951
648.2 | 503.2 | 128.2288 | 126.7229 |  |  |  |  | 648.2 | 503.2 | 130.4284 | 0.1956 | 648.2 | 503.2 | 126.5911
648.4 | 503.4 | 128.1329 | 126.6269 |  |  |  |  | 648.4 | 503.4 | 130.4284 | 0.1956 | 648.4 | 503.4 | 126.5911
648.6 | 503.6 | 128.2288 | 126.7229 |  |  |  |  | 648.6 | 503.6 | 130.4284 | 0.1956 | 648.6 | 503.6 | 126.5911
648.8 | 503.8 | 128.2288 | 126.7229 |  |  |  |  | 648.8 | 503.8 | 130.4284 | 0.29155 | 648.8 | 503.8 | 126.5911
649 | 504 | 128.1329 | 126.7229 |  |  |  |  | 649 | 504 | 130.4284 | 0.29155 | 649 | 504 | 126.5911
649.2 | 504.2 | 128.2288 | 126.7229 |  |  |  |  | 649.2 | 504.2 | 130.5244 | 0.1956 | 649.2 | 504.2 | 126.5911
649.4 | 504.4 | 128.2288 | 126.7229 |  |  |  |  | 649.4 | 504.4 | 130.4284 | 0.1956 | 649.4 | 504.4 | 126.5911
649.6 | 504.6 | 128.2288 | 126.7229 |  |  |  |  | 649.6 | 504.6 | 130.4284 | 0.1956 | 649.6 | 504.6 | 126.687
649.8 | 504.8 | 128.1329 | 126.6269 |  |  |  |  | 649.8 | 504.8 | 130.4284 | 0.1956 | 649.8 | 504.8 | 126.5911
650 | 505 | 128.1329 | 126.6269 |  |  |  |  | 650 | 505 | 130.3325 | 0.1956 | 650 | 505 | 126.5911
650.2 | 505.2 | 128.2288 | 126.7229 |  |  |  |  | 650.2 | 505.2 | 130.4284 | 0.1956 | 650.2 | 505.2 | 126.5911
650.4 | 505.4 | 128.1329 | 126.6269 |  |  |  |  | 650.4 | 505.4 | 130.4284 | 0.1956 | 650.4 | 505.4 | 126.5911
650.6 | 505.6 | 128.2288 | 126.7229 |  |  |  |  | 650.6 | 505.6 | 130.4284 | 0.1956 | 650.6 | 505.6 | 126.5911
650.8 | 505.8 | 128.1329 | 126.6269 |  |  |  |  | 650.8 | 505.8 | 130.4284 | 0.1956 | 650.8 | 505.8 | 126.5911
651 | 506 | 128.2288 | 126.6269 |  |  |  |  | 651 | 506 | 130.4284 | 0.29155 | 651 | 506 | 126.5911
651.2 | 506.2 | 128.2288 | 126.6269 |  |  |  |  | 651.2 | 506.2 | 130.4284 | 0.1956 | 651.2 | 506.2 | 126.687
651.4 | 506.4 | 128.1329 | 126.6269 |  |  |  |  | 651.4 | 506.4 | 130.4284 | 0.1956 | 651.4 | 506.4 | 126.687
651.6 | 506.6 | 128.2288 | 126.7229 |  |  |  |  | 651.6 | 506.6 | 130.5244 | 0.1956 | 651.6 | 506.6 | 126.687
651.8 | 506.8 | 128.1329 | 126.6269 |  |  |  |  | 651.8 | 506.8 | 130.4284 | 0.1956 | 651.8 | 506.8 | 126.5911
652 | 507 | 128.1329 | 126.6269 |  |  |  |  | 652 | 507 | 130.4284 | 0.29155 | 652 | 507 | 126.5911
652.2 | 507.2 | 128.1329 | 126.6269 |  |  |  |  | 652.2 | 507.2 | 130.4284 | 0.1956 | 652.2 | 507.2 | 126.687
652.4 | 507.4 | 128.1329 | 126.6269 |  |  |  |  | 652.4 | 507.4 | 130.4284 | 0.29155 | 652.4 | 507.4 | 126.687
652.6 | 507.6 | 128.1329 | 126.6269 |  |  |  |  | 652.6 | 507.6 | 130.4284 | 0.1956 | 652.6 | 507.6 | 126.5911
652.8 | 507.8 | 128.1329 | 126.6269 |  |  |  |  | 652.8 | 507.8 | 130.3325 | 0.1956 | 652.8 | 507.8 | 126.5911
653 | 508 | 128.1329 | 126.6269 |  |  |  |  | 653 | 508 | 130.4284 | 0.1956 | 653 | 508 | 126.687
653.2 | 508.2 | 128.0369 | 126.6269 |  |  |  |  | 653.2 | 508.2 | 130.4284 | 0.1956 | 653.2 | 508.2 | 126.5911
653.4 | 508.4 | 128.2288 | 126.7229 |  |  |  |  | 653.4 | 508.4 | 130.4284 | 0.29155 | 653.4 | 508.4 | 126.5911
653.6 | 508.6 | 128.1329 | 126.7229 |  |  |  |  | 653.6 | 508.6 | 130.4284 | 0.1956 | 653.6 | 508.6 | 126.687
653.8 | 508.8 | 128.1329 | 126.6269 |  |  |  |  | 653.8 | 508.8 | 130.4284 | 0.1956 | 653.8 | 508.8 | 126.5911
654 | 509 | 128.1329 | 126.6269 |  |  |  |  | 654 | 509 | 130.4284 | 0.1956 | 654 | 509 | 126.5911
654.2 | 509.2 | 128.1329 | 126.7229 |  |  |  |  | 654.2 | 509.2 | 130.4284 | 0.1956 | 654.2 | 509.2 | 126.687
654.4 | 509.4 | 128.1329 | 126.7229 |  |  |  |  | 654.4 | 509.4 | 130.4284 | 0.29155 | 654.4 | 509.4 | 126.5911
654.6 | 509.6 | 128.1329 | 126.6269 |  |  |  |  | 654.6 | 509.6 | 130.4284 | 0.1956 | 654.6 | 509.6 | 126.687
654.8 | 509.8 | 128.1329 | 126.6269 |  |  |  |  | 654.8 | 509.8 | 130.4284 | 0.1956 | 654.8 | 509.8 | 126.687
655 | 510 | 128.1329 | 126.7229 |  |  |  |  | 655 | 510 | 130.5244 | 0.1956 | 655 | 510 | 126.687
655.2 | 510.2 | 128.0369 | 126.7229 |  |  |  |  | 655.2 | 510.2 | 130.4284 | 0.1956 | 655.2 | 510.2 | 126.687
655.4 | 510.4 | 128.1329 | 126.6269 |  |  |  |  | 655.4 | 510.4 | 130.5244 | 0.1956 | 655.4 | 510.4 | 126.687
655.6 | 510.6 | 128.0369 | 126.6269 |  |  |  |  | 655.6 | 510.6 | 130.4284 | 0.1956 | 655.6 | 510.6 | 126.687
655.8 | 510.8 | 128.0369 | 126.6269 |  |  |  |  | 655.8 | 510.8 | 130.4284 | 0.1956 | 655.8 | 510.8 | 126.5911
656 | 511 | 128.0369 | 126.6269 |  |  |  |  | 656 | 511 | 130.3325 | 0.1956 | 656 | 511 | 126.5911
656.2 | 511.2 | 128.0369 | 126.7229 |  |  |  |  | 656.2 | 511.2 | 130.4284 | 0.1956 | 656.2 | 511.2 | 126.5911
656.4 | 511.4 | 128.1329 | 126.7229 |  |  |  |  | 656.4 | 511.4 | 130.4284 | 0.1956 | 656.4 | 511.4 | 126.687
656.6 | 511.6 | 128.1329 | 126.7229 |  |  |  |  | 656.6 | 511.6 | 130.4284 | 0.1956 | 656.6 | 511.6 | 126.687
656.8 | 511.8 | 128.1329 | 126.6269 |  |  |  |  | 656.8 | 511.8 | 130.4284 | 0.1956 | 656.8 | 511.8 | 126.687
657 | 512 | 128.0369 | 126.7229 |  |  |  |  | 657 | 512 | 130.4284 | 0.1956 | 657 | 512 | 126.687
657.2 | 512.2 | 128.0369 | 126.7229 |  |  |  |  | 657.2 | 512.2 | 130.4284 | 0.1956 | 657.2 | 512.2 | 126.5911
657.4 | 512.4 | 128.1329 | 126.6269 |  |  |  |  | 657.4 | 512.4 | 130.4284 | 0.1956 | 657.4 | 512.4 | 126.687
657.6 | 512.6 | 128.1329 | 126.6269 |  |  |  |  | 657.6 | 512.6 | 130.4284 | 0.1956 | 657.6 | 512.6 | 126.687
657.8 | 512.8 | 128.0369 | 126.7229 |  |  |  |  | 657.8 | 512.8 | 130.5244 | 0.1956 | 657.8 | 512.8 | 126.687
658 | 513 | 128.0369 | 126.6269 |  |  |  |  | 658 | 513 | 130.4284 | 0.1956 | 658 | 513 | 126.687
658.2 | 513.2 | 128.0369 | 126.7229 |  |  |  |  | 658.2 | 513.2 | 130.4284 | 0.1956 | 658.2 | 513.2 | 126.687
658.4 | 513.4 | 127.9409 | 126.6269 |  |  |  |  | 658.4 | 513.4 | 130.3325 | 0.1956 | 658.4 | 513.4 | 126.4951
658.6 | 513.6 | 127.9409 | 126.6269 |  |  |  |  | 658.6 | 513.6 | 130.3325 | 0.1956 | 658.6 | 513.6 | 126.5911
658.8 | 513.8 | 128.0369 | 126.7229 |  |  |  |  | 658.8 | 513.8 | 130.4284 | 0.29155 | 658.8 | 513.8 | 126.687
659 | 514 | 128.0369 | 126.7229 |  |  |  |  | 659 | 514 | 130.4284 | 0.1956 | 659 | 514 | 126.687
659.2 | 514.2 | 128.0369 | 126.7229 |  |  |  |  | 659.2 | 514.2 | 130.4284 | 0.1956 | 659.2 | 514.2 | 126.687
659.4 | 514.4 | 128.0369 | 126.7229 |  |  |  |  | 659.4 | 514.4 | 130.4284 | 0.1956 | 659.4 | 514.4 | 126.5911
659.6 | 514.6 | 128.0369 | 126.7229 |  |  |  |  | 659.6 | 514.6 | 130.2365 | 0.1956 | 659.6 | 514.6 | 126.5911
659.8 | 514.8 | 128.0369 | 126.7229 |  |  |  |  | 659.8 | 514.8 | 130.2365 | 0.1956 | 659.8 | 514.8 | 126.5911
660 | 515 | 127.3651 | 126.531 |  |  |  |  | 660 | 515 | 129.8526 | 0.1956 | 660 | 515 | 126.5911
660.2 | 515.2 | 127.9409 | 126.7229 |  |  |  |  | 660.2 | 515.2 | 130.0446 | 0.1956 | 660.2 | 515.2 | 126.687
660.4 | 515.4 | 128.0369 | 126.7229 |  |  |  |  | 660.4 | 515.4 | 129.7567 | 0.1956 | 660.4 | 515.4 | 126.5911
660.6 | 515.6 | 128.0369 | 126.7229 |  |  |  |  | 660.6 | 515.6 | 130.3325 | 0.1956 | 660.6 | 515.6 | 126.687
660.8 | 515.8 | 128.0369 | 126.7229 |  |  |  |  | 660.8 | 515.8 | 130.4284 | 0.1956 | 660.8 | 515.8 | 126.687
661 | 516 | 128.0369 | 126.8188 |  |  |  |  | 661 | 516 | 130.4284 | 0.1956 | 661 | 516 | 126.5911
661.2 | 516.2 | 128.1329 | 126.8188 |  |  |  |  | 661.2 | 516.2 | 130.5244 | 0.1956 | 661.2 | 516.2 | 126.687
661.4 | 516.4 | 128.1329 | 126.7229 |  |  |  |  | 661.4 | 516.4 | 130.4284 | 0.1956 | 661.4 | 516.4 | 126.687
661.6 | 516.6 | 128.1329 | 126.8188 |  |  |  |  | 661.6 | 516.6 | 130.5244 | 0.1956 | 661.6 | 516.6 | 126.5911
661.8 | 516.8 | 128.1329 | 126.7229 |  |  |  |  | 661.8 | 516.8 | 130.4284 | 0.1956 | 661.8 | 516.8 | 126.687
662 | 517 | 128.0369 | 126.7229 |  |  |  |  | 662 | 517 | 130.4284 | 0.1956 | 662 | 517 | 126.5911
662.2 | 517.2 | 128.1329 | 126.9148 |  |  |  |  | 662.2 | 517.2 | 130.4284 | 0.29155 | 662.2 | 517.2 | 126.5911
662.4 | 517.4 | 128.0369 | 126.8188 |  |  |  |  | 662.4 | 517.4 | 130.4284 | 0.1956 | 662.4 | 517.4 | 126.5911
662.6 | 517.6 | 128.0369 | 126.9148 |  |  |  |  | 662.6 | 517.6 | 130.4284 | 0.29155 | 662.6 | 517.6 | 126.5911
662.8 | 517.8 | 128.0369 | 126.7229 |  |  |  |  | 662.8 | 517.8 | 130.3325 | 0.1956 | 662.8 | 517.8 | 126.5911
663 | 518 | 128.0369 | 126.9148 |  |  |  |  | 663 | 518 | 130.3325 | 0.1956 | 663 | 518 | 126.5911
663.2 | 518.2 | 128.1329 | 127.0108 |  |  |  |  | 663.2 | 518.2 | 130.4284 | 0.1956 | 663.2 | 518.2 | 126.687
663.4 | 518.4 | 128.2288 | 126.9148 |  |  |  |  | 663.4 | 518.4 | 130.4284 | 0.1956 | 663.4 | 518.4 | 126.687
663.6 | 518.6 | 128.1329 | 126.9148 |  |  |  |  | 663.6 | 518.6 | 130.4284 | 0.1956 | 663.6 | 518.6 | 126.687
663.8 | 518.8 | 128.1329 | 126.9148 |  |  |  |  | 663.8 | 518.8 | 130.4284 | 0.1956 | 663.8 | 518.8 | 126.5911
664 | 519 | 128.1329 | 126.9148 |  |  |  |  | 664 | 519 | 130.3325 | 0.1956 | 664 | 519 | 126.5911
664.2 | 519.2 | 128.1329 | 126.9148 |  |  |  |  | 664.2 | 519.2 | 130.4284 | 0.1956 | 664.2 | 519.2 | 126.5911
664.4 | 519.4 | 128.1329 | 126.9148 |  |  |  |  | 664.4 | 519.4 | 130.4284 | 0.29155 | 664.4 | 519.4 | 126.4951
664.6 | 519.6 | 128.2288 | 127.0108 |  |  |  |  | 664.6 | 519.6 | 130.4284 | 0.1956 | 664.6 | 519.6 | 126.5911
664.8 | 519.8 | 128.1329 | 127.0108 |  |  |  |  | 664.8 | 519.8 | 130.4284 | 0.1956 | 664.8 | 519.8 | 126.5911
665 | 520 | 128.2288 | 127.0108 |  |  |  |  | 665 | 520 | 130.4284 | 0.1956 | 665 | 520 | 126.5911
665.2 | 520.2 | 128.1329 | 126.9148 |  |  |  |  | 665.2 | 520.2 | 130.4284 | 0.1956 | 665.2 | 520.2 | 126.687
665.4 | 520.4 | 128.2288 | 127.0108 |  |  |  |  | 665.4 | 520.4 | 130.4284 | 0.29155 | 665.4 | 520.4 | 126.5911
665.6 | 520.6 | 128.2288 | 127.0108 |  |  |  |  | 665.6 | 520.6 | 130.4284 | 0.1956 | 665.6 | 520.6 | 126.5911
665.8 | 520.8 | 128.1329 | 127.0108 |  |  |  |  | 665.8 | 520.8 | 130.4284 | 0.1956 | 665.8 | 520.8 | 126.687
666 | 521 | 128.1329 | 127.0108 |  |  |  |  | 666 | 521 | 130.4284 | 0.29155 | 666 | 521 | 126.5911
666.2 | 521.2 | 128.2288 | 127.0108 |  |  |  |  | 666.2 | 521.2 | 130.4284 | 0.1956 | 666.2 | 521.2 | 126.5911
666.4 | 521.4 | 128.2288 | 127.1068 |  |  |  |  | 666.4 | 521.4 | 130.4284 | 0.1956 | 666.4 | 521.4 | 126.5911
666.6 | 521.6 | 128.3248 | 127.0108 |  |  |  |  | 666.6 | 521.6 | 130.4284 | 0.1956 | 666.6 | 521.6 | 126.687
666.8 | 521.8 | 128.2288 | 127.0108 |  |  |  |  | 666.8 | 521.8 | 130.4284 | 0.1956 | 666.8 | 521.8 | 126.5911
667 | 522 | 128.3248 | 127.0108 |  |  |  |  | 667 | 522 | 130.2365 | 0.1956 | 667 | 522 | 126.5911
667.2 | 522.2 | 128.3248 | 127.0108 |  |  |  |  | 667.2 | 522.2 | 129.8526 | 0.29155 | 667.2 | 522.2 | 126.5911
667.4 | 522.4 | 128.3248 | 127.0108 |  |  |  |  | 667.4 | 522.4 | 129.5647 | 0.1956 | 667.4 | 522.4 | 126.4951
667.6 | 522.6 | 128.2288 | 127.0108 |  |  |  |  | 667.6 | 522.6 | 129.2768 | 0.1956 | 667.6 | 522.6 | 126.4951
667.8 | 522.8 | 128.3248 | 127.0108 |  |  |  |  | 667.8 | 522.8 | 129.7567 | 0.29155 | 667.8 | 522.8 | 126.4951
668 | 523 | 128.2288 | 127.0108 |  |  |  |  | 668 | 523 | 129.6607 | 0.1956 | 668 | 523 | 126.4951
668.2 | 523.2 | 128.1329 | 126.9148 |  |  |  |  | 668.2 | 523.2 | 128.5091 | 0.1956 | 668.2 | 523.2 | 126.3991
668.4 | 523.4 | 128.2288 | 126.9148 |  |  |  |  | 668.4 | 523.4 | 128.0292 | 0.1956 | 668.4 | 523.4 | 126.3991
668.6 | 523.6 | 128.1329 | 126.9148 |  |  |  |  | 668.6 | 523.6 | 127.4535 | 0.1956 | 668.6 | 523.6 | 126.3032
668.8 | 523.8 | 128.3248 | 127.1068 |  |  |  |  | 668.8 | 523.8 | 129.4687 | 0.1956 | 668.8 | 523.8 | 126.5911
669 | 524 | 128.5167 | 127.2987 |  |  |  |  | 669 | 524 | 130.4284 | 0.1956 | 669 | 524 | 126.5911
669.2 | 524.2 | 128.4208 | 127.2027 |  |  |  |  | 669.2 | 524.2 | 130.4284 | 0.1956 | 669.2 | 524.2 | 126.687
669.4 | 524.4 | 128.4208 | 127.2027 |  |  |  |  | 669.4 | 524.4 | 130.4284 | 0.1956 | 669.4 | 524.4 | 126.5911
669.6 | 524.6 | 128.4208 | 127.2027 |  |  |  |  | 669.6 | 524.6 | 130.4284 | 0.1956 | 669.6 | 524.6 | 126.5911
669.8 | 524.8 | 128.5167 | 127.2027 |  |  |  |  | 669.8 | 524.8 | 130.4284 | 0.1956 | 669.8 | 524.8 | 126.5911
670 | 525 | 128.3248 | 127.1068 |  |  |  |  | 670 | 525 | 130.3325 | 0.1956 | 670 | 525 | 126.4951
670.2 | 525.2 | 128.4208 | 127.2027 |  |  |  |  | 670.2 | 525.2 | 130.4284 | 0.1956 | 670.2 | 525.2 | 126.5911
670.4 | 525.4 | 128.4208 | 127.2027 |  |  |  |  | 670.4 | 525.4 | 130.4284 | 0.29155 | 670.4 | 525.4 | 126.5911
670.6 | 525.6 | 128.4208 | 127.2027 |  |  |  |  | 670.6 | 525.6 | 130.4284 | 0.1956 | 670.6 | 525.6 | 126.5911
670.8 | 525.8 | 128.5167 | 127.2027 |  |  |  |  | 670.8 | 525.8 | 130.4284 | 0.1956 | 670.8 | 525.8 | 126.687
671 | 526 | 128.4208 | 127.2027 |  |  |  |  | 671 | 526 | 130.2365 | 0.29155 | 671 | 526 | 126.5911
671.2 | 526.2 | 128.5167 | 127.2987 |  |  |  |  | 671.2 | 526.2 | 130.4284 | 0.1956 | 671.2 | 526.2 | 126.5911
671.4 | 526.4 | 128.4208 | 127.2987 |  |  |  |  | 671.4 | 526.4 | 130.4284 | 0.29155 | 671.4 | 526.4 | 126.5911
671.6 | 526.6 | 128.5167 | 127.2987 |  |  |  |  | 671.6 | 526.6 | 130.3325 | 0.1956 | 671.6 | 526.6 | 126.5911
671.8 | 526.8 | 128.5167 | 127.2987 |  |  |  |  | 671.8 | 526.8 | 130.4284 | 0.1956 | 671.8 | 526.8 | 126.5911
672 | 527 | 128.5167 | 127.2987 |  |  |  |  | 672 | 527 | 130.3325 | 0.1956 | 672 | 527 | 126.5911
672.2 | 527.2 | 128.5167 | 127.3947 |  |  |  |  | 672.2 | 527.2 | 130.4284 | 0.1956 | 672.2 | 527.2 | 126.5911
672.4 | 527.4 | 128.5167 | 127.2987 |  |  |  |  | 672.4 | 527.4 | 130.3325 | 0.29155 | 672.4 | 527.4 | 126.5911
672.6 | 527.6 | 128.4208 | 127.2027 |  |  |  |  | 672.6 | 527.6 | 130.3325 | 0.29155 | 672.6 | 527.6 | 126.5911
672.8 | 527.8 | 128.4208 | 127.2987 |  |  |  |  | 672.8 | 527.8 | 130.3325 | 0.1956 | 672.8 | 527.8 | 126.5911
673 | 528 | 128.4208 | 127.2027 |  |  |  |  | 673 | 528 | 130.3325 | 0.1956 | 673 | 528 | 126.5911
673.2 | 528.2 | 128.4208 | 127.2987 |  |  |  |  | 673.2 | 528.2 | 130.4284 | 0.1956 | 673.2 | 528.2 | 126.4951
673.4 | 528.4 | 128.4208 | 127.2987 |  |  |  |  | 673.4 | 528.4 | 130.4284 | 0.29155 | 673.4 | 528.4 | 126.4951
673.6 | 528.6 | 128.4208 | 127.2987 |  |  |  |  | 673.6 | 528.6 | 130.2365 | 0.1956 | 673.6 | 528.6 | 126.5911
673.8 | 528.8 | 128.3248 | 127.2987 |  |  |  |  | 673.8 | 528.8 | 130.2365 | 0.099605 | 673.8 | 528.8 | 126.4951
674 | 529 | 128.3248 | 127.2027 |  |  |  |  | 674 | 529 | 130.2365 | 0.1956 | 674 | 529 | 126.4951
674.2 | 529.2 | 128.4208 | 127.2987 |  |  |  |  | 674.2 | 529.2 | 130.4284 | 0.1956 | 674.2 | 529.2 | 126.4951
674.4 | 529.4 | 128.4208 | 127.2987 |  |  |  |  | 674.4 | 529.4 | 130.3325 | 0.1956 | 674.4 | 529.4 | 126.4951
674.6 | 529.6 | 128.5167 | 127.2987 |  |  |  |  | 674.6 | 529.6 | 130.4284 | 0.29155 | 674.6 | 529.6 | 126.5911
674.8 | 529.8 | 128.4208 | 127.2987 |  |  |  |  | 674.8 | 529.8 | 130.3325 | 0.1956 | 674.8 | 529.8 | 126.4951
675 | 530 | 128.4208 | 127.2987 |  |  |  |  | 675 | 530 | 130.3325 | 0.29155 | 675 | 530 | 126.4951
675.2 | 530.2 | 128.4208 | 127.2987 |  |  |  |  | 675.2 | 530.2 | 130.3325 | 0.29155 | 675.2 | 530.2 | 126.4951
675.4 | 530.4 | 128.4208 | 127.2987 |  |  |  |  | 675.4 | 530.4 | 130.3325 | 0.29155 | 675.4 | 530.4 | 126.5911
675.6 | 530.6 | 128.4208 | 127.3947 |  |  |  |  | 675.6 | 530.6 | 130.3325 | 0.3875 | 675.6 | 530.6 | 126.5911
675.8 | 530.8 | 128.4208 | 127.2987 |  |  |  |  | 675.8 | 530.8 | 130.3325 | 1.0593 | 675.8 | 530.8 | 126.4951
676 | 531 | 128.3248 | 127.2987 |  |  |  |  | 676 | 531 | 130.3325 | 1.2512 | 676 | 531 | 126.5911
676.2 | 531.2 | 128.4208 | 127.2987 |  |  |  |  | 676.2 | 531.2 | 130.3325 | 1.827 | 676.2 | 531.2 | 126.5911
676.4 | 531.4 | 128.4208 | 127.2987 |  |  |  |  | 676.4 | 531.4 | 130.3325 | 2.4988 | 676.4 | 531.4 | 126.5911
676.6 | 531.6 | 128.4208 | 127.2987 |  |  |  |  | 676.6 | 531.6 | 130.2365 | 2.9786 | 676.6 | 531.6 | 126.5911
676.8 | 531.8 | 128.3248 | 127.2987 |  |  |  |  | 676.8 | 531.8 | 130.3325 | 3.4584 | 676.8 | 531.8 | 126.4951
677 | 532 | 128.3248 | 127.2987 |  |  |  |  | 677 | 532 | 130.3325 | 4.0343 | 677 | 532 | 126.4951
677.2 | 532.2 | 128.4208 | 127.2987 |  |  |  |  | 677.2 | 532.2 | 130.3325 | 4.7061 | 677.2 | 532.2 | 126.4951
677.4 | 532.4 | 128.4208 | 127.3947 |  |  |  |  | 677.4 | 532.4 | 130.4284 | 5.1859 | 677.4 | 532.4 | 126.5911
677.6 | 532.6 | 128.4208 | 127.3947 |  |  |  |  | 677.6 | 532.6 | 130.3325 | 5.9536 | 677.6 | 532.6 | 126.5911
677.8 | 532.8 | 128.4208 | 127.2987 |  |  |  |  | 677.8 | 532.8 | 130.3325 | 7.3931 | 677.8 | 532.8 | 126.4951
678 | 533 | 128.4208 | 127.2987 |  |  |  |  | 678 | 533 | 130.3325 | 4.4181 | 678 | 533 | 126.4951
678.2 | 533.2 | 128.4208 | 127.3947 |  |  |  |  | 678.2 | 533.2 | 130.3325 | 2.0189 | 678.2 | 533.2 | 126.5911
678.4 | 533.4 | 128.4208 | 127.2987 |  |  |  |  | 678.4 | 533.4 | 130.3325 | 2.0189 | 678.4 | 533.4 | 126.4951
678.6 | 533.6 | 128.4208 | 127.2987 |  |  |  |  | 678.6 | 533.6 | 130.2365 | 9.6963 | 678.6 | 533.6 | 126.5911
678.8 | 533.8 | 128.4208 | 127.2987 |  |  |  |  | 678.8 | 533.8 | 130.2365 | 11.5197 | 678.8 | 533.8 | 126.4951
679 | 534 | 128.4208 | 127.2987 |  |  |  |  | 679 | 534 | 130.3325 | 11.9996 | 679 | 534 | 126.5911
679.2 | 534.2 | 128.4208 | 127.2987 |  |  |  |  | 679.2 | 534.2 | 130.0446 | 12.5754 | 679.2 | 534.2 | 126.4951
679.4 | 534.4 | 128.4208 | 127.2987 |  |  |  |  | 679.4 | 534.4 | 130.2365 | 13.631 | 679.4 | 534.4 | 126.5911
679.6 | 534.6 | 128.4208 | 127.2987 |  |  |  |  | 679.6 | 534.6 | 130.1405 | 13.1511 | 679.6 | 534.6 | 126.4951
679.8 | 534.8 | 128.4208 | 127.2987 |  |  |  |  | 679.8 | 534.8 | 130.2365 | 9.5044 | 679.8 | 534.8 | 126.4951
680 | 535 | 128.4208 | 127.2987 |  |  |  |  | 680 | 535 | 130.2365 | 3.3625 | 680 | 535 | 126.5911
680.2 | 535.2 | 128.4208 | 127.2987 |  |  |  |  | 680.2 | 535.2 | 130.0446 | 2.8827 | 680.2 | 535.2 | 126.4951
680.4 | 535.4 | 128.5167 | 127.3947 |  |  |  |  | 680.4 | 535.4 | 130.3325 | 5.4738 | 680.4 | 535.4 | 126.5911
680.6 | 535.6 | 128.4208 | 127.2987 |  |  |  |  | 680.6 | 535.6 | 130.2365 | 11.1358 | 680.6 | 535.6 | 126.4951
680.8 | 535.8 | 128.3248 | 127.2987 |  |  |  |  | 680.8 | 535.8 | 130.1405 | 13.0552 | 680.8 | 535.8 | 126.4951
681 | 536 | 128.4208 | 127.2987 |  |  |  |  | 681 | 536 | 130.1405 | 14.0149 | 681 | 536 | 126.4951
681.2 | 536.2 | 128.3248 | 127.2027 |  |  |  |  | 681.2 | 536.2 | 129.5647 | 12.8632 | 681.2 | 536.2 | 126.4951
681.4 | 536.4 | 128.4208 | 127.2987 |  |  |  |  | 681.4 | 536.4 | 130.0446 | 14.8786 | 681.4 | 536.4 | 126.4951
681.6 | 536.6 | 128.3248 | 127.2027 |  |  |  |  | 681.6 | 536.6 | 129.8526 | 14.8786 | 681.6 | 536.6 | 126.4951
681.8 | 536.8 | 128.4208 | 127.2987 |  |  |  |  | 681.8 | 536.8 | 130.0446 | 16.606 | 681.8 | 536.8 | 126.5911
682 | 537 | 128.3248 | 127.2027 |  |  |  |  | 682 | 537 | 129.9486 | 17.2777 | 682 | 537 | 126.4951
682.2 | 537.2 | 128.4208 | 127.2027 |  |  |  |  | 682.2 | 537.2 | 129.9486 | 16.7019 | 682.2 | 537.2 | 126.4951
682.4 | 537.4 | 128.4208 | 127.2987 |  |  |  |  | 682.4 | 537.4 | 130.1405 | 16.9899 | 682.4 | 537.4 | 126.5911
682.6 | 537.6 | 128.5167 | 127.2987 |  |  |  |  | 682.6 | 537.6 | 130.0446 | 17.1818 | 682.6 | 537.6 | 126.4951
682.8 | 537.8 | 128.5167 | 127.2987 |  |  |  |  | 682.8 | 537.8 | 130.0446 | 17.1818 | 682.8 | 537.8 | 126.5911
683 | 538 | 128.5167 | 127.3947 |  |  |  |  | 683 | 538 | 130.1405 | 17.9495 | 683 | 538 | 126.4951
683.2 | 538.2 | 128.5167 | 127.3947 |  |  |  |  | 683.2 | 538.2 | 130.0446 | 18.0455 | 683.2 | 538.2 | 126.4951
683.4 | 538.4 | 128.6127 | 127.2987 |  |  |  |  | 683.4 | 538.4 | 130.0446 | 18.2374 | 683.4 | 538.4 | 126.4951
683.6 | 538.6 | 128.4208 | 127.4906 |  |  |  |  | 683.6 | 538.6 | 130.0446 | 9.6963 | 683.6 | 538.6 | 126.4951
683.8 | 538.8 | 128.5167 | 127.2987 |  |  |  |  | 683.8 | 538.8 | 130.0446 | 11.6157 | 683.8 | 538.8 | 126.4951
684 | 539 | 128.2288 | 127.2027 |  |  |  |  | 684 | 539 | 129.5647 | 14.2068 | 684 | 539 | 126.4951
684.2 | 539.2 | 128.6127 | 126.8188 |  |  |  |  | 684.2 | 539.2 | 128.9889 | 13.4391 | 684.2 | 539.2 | 126.4951
684.4 | 539.4 | 128.4208 | 127.2987 |  |  |  |  | 684.4 | 539.4 | 129.9486 | 15.6463 | 684.4 | 539.4 | 126.4951
684.6 | 539.6 | 128.5167 | 127.3947 |  |  |  |  | 684.6 | 539.6 | 130.0446 | 16.7979 | 684.6 | 539.6 | 126.4951
684.8 | 539.8 | 128.5167 | 127.3947 |  |  |  |  | 684.8 | 539.8 | 130.0446 | 16.8939 | 684.8 | 539.8 | 126.4951
685 | 540 | 128.5167 | 127.2987 |  |  |  |  | 685 | 540 | 129.8526 | 16.9899 | 685 | 540 | 126.4951
685.2 | 540.2 | 128.6127 | 127.3947 |  |  |  |  | 685.2 | 540.2 | 130.1405 | 19.7729 | 685.2 | 540.2 | 126.5911
685.4 | 540.4 | 128.4208 | 127.3947 |  |  |  |  | 685.4 | 540.4 | 130.0446 | 19.9648 | 685.4 | 540.4 | 126.4951
685.6 | 540.6 | 128.5167 | 127.3947 |  |  |  |  | 685.6 | 540.6 | 130.1405 | 19.7729 | 685.6 | 540.6 | 126.4951
685.8 | 540.8 | 128.5167 | 127.3947 |  |  |  |  | 685.8 | 540.8 | 130.0446 | 20.9245 | 685.8 | 540.8 | 126.4951
686 | 541 | 128.5167 | 127.3947 |  |  |  |  | 686 | 541 | 130.1405 | 21.5003 | 686 | 541 | 126.3991
686.2 | 541.2 | 128.5167 | 127.3947 |  |  |  |  | 686.2 | 541.2 | 130.1405 | 21.6923 | 686.2 | 541.2 | 126.4951
686.4 | 541.4 | 128.5167 | 127.3947 |  |  |  |  | 686.4 | 541.4 | 130.1405 | 22.364 | 686.4 | 541.4 | 126.4951
686.6 | 541.6 | 128.6127 | 127.4906 |  |  |  |  | 686.6 | 541.6 | 130.1405 | 22.0761 | 686.6 | 541.6 | 126.5911
686.8 | 541.8 | 128.5167 | 127.3947 |  |  |  |  | 686.8 | 541.8 | 129.9486 | 21.7882 | 686.8 | 541.8 | 126.4951
687 | 542 | 128.5167 | 127.3947 |  |  |  |  | 687 | 542 | 130.0446 | 21.7882 | 687 | 542 | 126.4951
687.2 | 542.2 | 128.5167 | 127.3947 |  |  |  |  | 687.2 | 542.2 | 130.0446 | 18.6213 | 687.2 | 542.2 | 126.4951
687.4 | 542.4 | 128.5167 | 127.3947 |  |  |  |  | 687.4 | 542.4 | 130.0446 | 18.4294 | 687.4 | 542.4 | 126.4951
687.6 | 542.6 | 128.5167 | 127.3947 |  |  |  |  | 687.6 | 542.6 | 130.1405 | 18.7173 | 687.6 | 542.6 | 126.3991
687.8 | 542.8 | 128.5167 | 127.3947 |  |  |  |  | 687.8 | 542.8 | 130.0446 | 20.0608 | 687.8 | 542.8 | 126.4951
688 | 543 | 128.4208 | 127.2987 |  |  |  |  | 688 | 543 | 129.8526 | 24.2834 | 688 | 543 | 126.3991
688.2 | 543.2 | 128.6127 | 127.3947 |  |  |  |  | 688.2 | 543.2 | 129.9486 | 26.1067 | 688.2 | 543.2 | 126.4951
688.4 | 543.4 | 128.5167 | 127.3947 |  |  |  |  | 688.4 | 543.4 | 129.8526 | 28.6978 | 688.4 | 543.4 | 126.4951
688.6 | 543.6 | 128.5167 | 127.2987 |  |  |  |  | 688.6 | 543.6 | 129.7567 | 31.4809 | 688.6 | 543.6 | 126.4951
688.8 | 543.8 | 128.5167 | 127.4906 |  |  |  |  | 688.8 | 543.8 | 129.7567 | 23.9954 | 688.8 | 543.8 | 126.5911
689 | 544 | 128.5167 | 127.2987 |  |  |  |  | 689 | 544 | 129.5647 | 16.8939 | 689 | 544 | 126.1112
689.2 | 544.2 | 128.5167 | 127.2987 |  |  |  |  | 689.2 | 544.2 | 129.9486 | 16.8939 | 689.2 | 544.2 | 126.4951
689.4 | 544.4 | 128.5167 | 127.3947 |  |  |  |  | 689.4 | 544.4 | 129.7567 | 18.4294 | 689.4 | 544.4 | 126.4951
689.6 | 544.6 | 128.5167 | 127.4906 |  |  |  |  | 689.6 | 544.6 | 129.7567 | 17.6616 | 689.6 | 544.6 | 126.4951
689.8 | 544.8 | 128.5167 | 127.2987 |  |  |  |  | 689.8 | 544.8 | 128.9889 | 33.1123 | 689.8 | 544.8 | 126.3991
690 | 545 | 128.4208 | 127.0108 |  |  |  |  | 690 | 545 | 128.5091 | 62.7662 | 690 | 545 | 126.4951
690.2 | 545.2 | 128.4208 | 127.2987 |  |  |  |  | 690.2 | 545.2 | 128.797 | 44.1486 | 690.2 | 545.2 | 126.3991
690.4 | 545.4 | 128.4208 | 127.2987 |  |  |  |  | 690.4 | 545.4 | 129.0849 | 63.0541 | 690.4 | 545.4 | 126.4951
690.6 | 545.6 | 128.2288 | 127.2027 |  |  |  |  | 690.6 | 545.6 | 128.3172 | 55.8566 | 690.6 | 545.6 | 126.3991
690.8 | 545.8 | 128.3248 | 127.2027 |  |  |  |  | 690.8 | 545.8 | 127.2615 | 20.6366 | 690.8 | 545.8 | 126.3991
691 | 546 | 128.3248 | 127.2027 |  |  |  |  | 691 | 546 | 127.7414 | 8.3528 | 691 | 546 | 126.4951
691.2 | 546.2 | 128.5167 | 127.4906 |  |  |  |  | 691.2 | 546.2 | 129.5647 | 2.8827 | 691.2 | 546.2 | 126.4951
691.4 | 546.4 | 128.5167 | 127.4906 |  |  |  |  | 691.4 | 546.4 | 129.8526 | 1.2512 | 691.4 | 546.4 | 126.3991
691.6 | 546.6 | 128.7087 | 127.4906 |  |  |  |  | 691.6 | 546.6 | 129.9486 | 0.86733 | 691.6 | 546.6 | 126.4951
691.8 | 546.8 | 128.6127 | 127.3947 |  |  |  |  | 691.8 | 546.8 | 129.9486 | 0.77138 | 691.8 | 546.8 | 126.5911
692 | 547 | 128.5167 | 127.2987 |  |  |  |  | 692 | 547 | 129.6607 | 0.67543 | 692 | 547 | 126.3991
692.2 | 547.2 | 128.5167 | 127.0108 |  |  |  |  | 692.2 | 547.2 | 129.9486 | 0.77138 | 692.2 | 547.2 | 126.3991
692.4 | 547.4 | 128.6127 | 127.3947 |  |  |  |  | 692.4 | 547.4 | 129.9486 | 0.57944 | 692.4 | 547.4 | 126.4951
692.6 | 547.6 | 128.5167 | 127.3947 |  |  |  |  | 692.6 | 547.6 | 130.1405 | 0.57944 | 692.6 | 547.6 | 126.4951
692.8 | 547.8 | 128.5167 | 127.3947 |  |  |  |  | 692.8 | 547.8 | 130.1405 | 0.3875 | 692.8 | 547.8 | 126.4951
693 | 548 | 128.5167 | 127.3947 |  |  |  |  | 693 | 548 | 130.1405 | 0.3875 | 693 | 548 | 126.5911
693.2 | 548.2 | 128.5167 | 127.3947 |  |  |  |  | 693.2 | 548.2 | 130.0446 | 0.3875 | 693.2 | 548.2 | 126.4951
693.4 | 548.4 | 128.5167 | 127.2027 |  |  |  |  | 693.4 | 548.4 | 129.8526 | 0.3875 | 693.4 | 548.4 | 126.4951
693.6 | 548.6 | 128.0369 | 127.0108 |  |  |  |  | 693.6 | 548.6 | 128.701 | 0.1956 | 693.6 | 548.6 | 126.3032
693.8 | 548.8 | 128.3248 | 127.3947 |  |  |  |  | 693.8 | 548.8 | 127.9333 | 1.4432 | 693.8 | 548.8 | 126.4951
694 | 549 | 127.8449 | 126.9148 |  |  |  |  | 694 | 549 | 127.8373 | 1.1553 | 694 | 549 | 126.1112
694.2 | 549.2 | 128.5167 | 127.1068 |  |  |  |  | 694.2 | 549.2 | 129.0849 | 0.67543 | 694.2 | 549.2 | 126.4951
694.4 | 549.4 | 128.4208 | 127.4906 |  |  |  |  | 694.4 | 549.4 | 129.1809 | 1.0593 | 694.4 | 549.4 | 126.687
694.6 | 549.6 | 128.4208 | 127.1068 |  |  |  |  | 694.6 | 549.6 | 128.701 | 2.0189 | 694.6 | 549.6 | 127.0709
694.8 | 549.8 | 128.3248 | 127.1068 |  |  |  |  | 694.8 | 549.8 | 128.9889 | 1.7311 | 694.8 | 549.8 | 126.3032
695 | 550 | 128.5167 | 127.1068 |  |  |  |  | 695 | 550 | 128.9889 | 1.0593 | 695 | 550 | 126.3032
695.2 | 550.2 | 128.0369 | 127.0108 |  |  |  |  | 695.2 | 550.2 | 128.4131 | 0.96332 | 695.2 | 550.2 | 126.3032
695.4 | 550.4 | 128.4208 | 127.2027 |  |  |  |  | 695.4 | 550.4 | 128.2212 | 0.96332 | 695.4 | 550.4 | 126.783
695.6 | 550.6 | 128.4208 | 126.9148 |  |  |  |  | 695.6 | 550.6 | 128.1252 | 1.1553 | 695.6 | 550.6 | 126.2072
695.8 | 550.8 | 128.4208 | 127.7785 |  |  |  |  | 695.8 | 550.8 | 128.2212 | 2.0189 | 695.8 | 550.8 | 126.3032
696 | 551 | 128.1329 | 127.2027 |  |  |  |  | 696 | 551 | 127.1656 | 1.6351 | 696 | 551 | 126.3032
696.2 | 551.2 | 128.0369 | 126.6269 |  |  |  |  | 696.2 | 551.2 | 125.1502 | 1.3472 | 696.2 | 551.2 | 126.1112
696.4 | 551.4 | 128.1329 | 126.7229 |  |  |  |  | 696.4 | 551.4 | 124.3825 | 0.96332 | 696.4 | 551.4 | 126.2072
696.6 | 551.6 | 128.0369 | 126.7229 |  |  |  |  | 696.6 | 551.6 | 124.5744 | 1.0593 | 696.6 | 551.6 | 126.0153
696.8 | 551.8 | 128.0369 | 126.9148 |  |  |  |  | 696.8 | 551.8 | 126.014 | 0.57944 | 696.8 | 551.8 | 126.1112
697 | 552 | 128.1329 | 127.2027 |  |  |  |  | 697 | 552 | 126.9736 | 0.67543 | 697 | 552 | 126.0153
697.2 | 552.2 | 128.3248 | 127.2027 |  |  |  |  | 697.2 | 552.2 | 128.2212 | 0.48349 | 697.2 | 552.2 | 126.3032
697.4 | 552.4 | 128.1329 | 127.1068 |  |  |  |  | 697.4 | 552.4 | 128.5091 | 0.3875 | 697.4 | 552.4 | 125.8233
697.6 | 552.6 | 128.1329 | 127.1068 |  |  |  |  | 697.6 | 552.6 | 128.5091 | 0.77138 | 697.6 | 552.6 | 126.3032
697.8 | 552.8 | 128.0369 | 126.8188 |  |  |  |  | 697.8 | 552.8 | 127.1656 | 0.67543 | 697.8 | 552.8 | 126.2072
698 | 553 | 128.2288 | 127.0108 |  |  |  |  | 698 | 553 | 128.3172 | 0.67543 | 698 | 553 | 126.1112
698.2 | 553.2 | 128.3248 | 127.1068 |  |  |  |  | 698.2 | 553.2 | 128.893 | 0.67543 | 698.2 | 553.2 | 126.783
698.4 | 553.4 | 128.5167 | 127.3947 |  |  |  |  | 698.4 | 553.4 | 129.5647 | 0.67543 | 698.4 | 553.4 | 126.1112
698.6 | 553.6 | 128.4208 | 127.2987 |  |  |  |  | 698.6 | 553.6 | 129.2768 | 0.67543 | 698.6 | 553.6 | 126.3991
698.8 | 553.8 | 128.4208 | 127.2027 |  |  |  |  | 698.8 | 553.8 | 128.701 | 0.48349 | 698.8 | 553.8 | 126.2072
699 | 554 | 128.2288 | 127.2027 |  |  |  |  | 699 | 554 | 128.0292 | 0.3875 | 699 | 554 | 126.2072
699.2 | 554.2 | 128.4208 | 127.2027 |  |  |  |  | 699.2 | 554.2 | 127.9333 | 0.57944 | 699.2 | 554.2 | 126.3991
699.4 | 554.4 | 128.1329 | 127.2987 |  |  |  |  | 699.4 | 554.4 | 128.3172 | 0.48349 | 699.4 | 554.4 | 126.2072
699.6 | 554.6 | 128.3248 | 127.2987 |  |  |  |  | 699.6 | 554.6 | 127.7414 | 0.86733 | 699.6 | 554.6 | 126.3032
699.8 | 554.8 | 128.3248 | 127.2027 |  |  |  |  | 699.8 | 554.8 | 128.701 | 1.3472 | 699.8 | 554.8 | 126.3991
700 | 555 | 128.3248 | 127.1068 |  |  |  |  | 700 | 555 | 128.1252 | 1.2512 | 700 | 555 | 126.3991
700.2 | 555.2 | 128.3248 | 127.0108 |  |  |  |  | 700.2 | 555.2 | 126.7817 | 0.57944 | 700.2 | 555.2 | 126.1112
700.4 | 555.4 | 127.8449 | 126.7229 |  |  |  |  | 700.4 | 555.4 | 123.8067 | 7.1052 | 700.4 | 555.4 | 125.8233
700.6 | 555.6 | 126.8853 | 126.0511 |  |  |  |  | 700.6 | 555.6 | 115.1697 | 15.0705 | 700.6 | 555.6 | 125.2475
700.8 | 555.8 | 126.9813 | 126.1471 |  |  |  |  | 700.8 | 555.8 | 116.6092 | 8.8326 | 700.8 | 555.8 | 125.0556
701 | 556 | 127.653 | 126.531 |  |  |  |  | 701 | 556 | 119.8721 | 3.8423 | 701 | 556 | 125.4394
701.2 | 556.2 | 127.8449 | 126.435 |  |  |  |  | 701.2 | 556.2 | 122.1753 | 3.7464 | 701.2 | 556.2 | 125.8233
701.4 | 556.4 | 127.9409 | 127.0108 |  |  |  |  | 701.4 | 556.4 | 123.9027 | 2.9786 | 701.4 | 556.4 | 126.0153
701.6 | 556.6 | 128.2288 | 126.8188 |  |  |  |  | 701.6 | 556.6 | 126.1099 | 2.3069 | 701.6 | 556.6 | 126.2072
701.8 | 556.8 | 128.3248 | 127.3947 |  |  |  |  | 701.8 | 556.8 | 126.3978 | 6.0496 | 701.8 | 556.8 | 126.783
702 | 557 | 127.749 | 126.531 |  |  |  |  | 702 | 557 | 123.8067 | 3.8423 | 702 | 557 | 125.9193
702.2 | 557.2 | 127.8449 | 126.8188 |  |  |  |  | 702.2 | 557.2 | 121.2156 | 5.9536 | 702.2 | 557.2 | 125.7273
702.4 | 557.4 | 127.9409 | 127.1068 |  |  |  |  | 702.4 | 557.4 | 126.5897 | 6.3375 | 702.4 | 557.4 | 126.2072
702.6 | 557.6 | 128.1329 | 126.8188 |  |  |  |  | 702.6 | 557.6 | 126.7817 | 4.4181 | 702.6 | 557.6 | 126.5911
702.8 | 557.8 | 127.9409 | 125.5713 |  |  |  |  | 702.8 | 557.8 | 126.8776 | 2.0189 | 702.8 | 557.8 | 126.2072
703 | 558 | 128.2288 | 127.0108 |  |  |  |  | 703 | 558 | 127.0696 | 2.4028 | 703 | 558 | 126.3991
703.2 | 558.2 | 128.2288 | 127.2987 |  |  |  |  | 703.2 | 558.2 | 127.3575 | 4.5141 | 703.2 | 558.2 | 126.2072
703.4 | 558.4 | 128.3248 | 127.3947 |  |  |  |  | 703.4 | 558.4 | 128.3172 | 4.3222 | 703.4 | 558.4 | 126.0153
703.6 | 558.6 | 128.4208 | 127.4906 |  |  |  |  | 703.6 | 558.6 | 128.5091 | 3.3625 | 703.6 | 558.6 | 126.3991
703.8 | 558.8 | 127.8449 | 126.531 |  |  |  |  | 703.8 | 558.8 | 127.2615 | 4.2262 | 703.8 | 558.8 | 126.1112
704 | 559 | 128.3248 | 126.9148 |  |  |  |  | 704 | 559 | 126.8776 | 3.3625 | 704 | 559 | 126.0153
704.2 | 559.2 | 128.1329 | 127.1068 |  |  |  |  | 704.2 | 559.2 | 125.6301 | 2.9786 | 704.2 | 559.2 | 125.3435
704.4 | 559.4 | 128.0369 | 126.9148 |  |  |  |  | 704.4 | 559.4 | 123.8067 | 3.6504 | 704.4 | 559.4 | 125.9193
704.6 | 559.6 | 128.1329 | 127.0108 |  |  |  |  | 704.6 | 559.6 | 124.5744 | 3.8423 | 704.6 | 559.6 | 126.2072
704.8 | 559.8 | 128.0369 | 127.0108 |  |  |  |  | 704.8 | 559.8 | 124.8623 | 4.3222 | 704.8 | 559.8 | 125.9193
705 | 560 | 127.9409 | 126.6269 |  |  |  |  | 705 | 560 | 121.5994 | 4.9939 | 705 | 560 | 125.6314
705.2 | 560.2 | 128.0369 | 127.1068 |  |  |  |  | 705.2 | 560.2 | 124.0946 | 4.4181 | 705.2 | 560.2 | 125.7273
705.4 | 560.4 | 127.749 | 126.7229 |  |  |  |  | 705.4 | 560.4 | 124.2865 | 4.7061 | 705.4 | 560.4 | 126.1112
705.6 | 560.6 | 128.0369 | 126.531 |  |  |  |  | 705.6 | 560.6 | 124.7664 | 1.923 | 705.6 | 560.6 | 125.9193
705.8 | 560.8 | 128.0369 | 126.531 |  |  |  |  | 705.8 | 560.8 | 124.5744 | 1.4432 | 705.8 | 560.8 | 126.3991
706 | 561 | 128.0369 | 127.0108 |  |  |  |  | 706 | 561 | 123.8067 | 0.96332 | 706 | 561 | 125.7273
706.2 | 561.2 | 128.3248 | 126.9148 |  |  |  |  | 706.2 | 561.2 | 125.822 | 0.3875 | 706.2 | 561.2 | 126.0153
706.4 | 561.4 | 128.2288 | 127.3947 |  |  |  |  | 706.4 | 561.4 | 126.014 | 0.57944 | 706.4 | 561.4 | 126.3032
706.6 | 561.6 | 128.3248 | 126.8188 |  |  |  |  | 706.6 | 561.6 | 127.7414 | 0.29155 | 706.6 | 561.6 | 126.4951
706.8 | 561.8 | 128.4208 | 127.0108 |  |  |  |  | 706.8 | 561.8 | 127.4535 | 0.57944 | 706.8 | 561.8 | 126.4951
707 | 562 | 128.5167 | 127.2987 |  |  |  |  | 707 | 562 | 127.8373 | 0.57944 | 707 | 562 | 126.1112
707.2 | 562.2 | 128.3248 | 127.2987 |  |  |  |  | 707.2 | 562.2 | 127.9333 | 0.29155 | 707.2 | 562.2 | 126.5911
707.4 | 562.4 | 128.5167 | 127.2987 |  |  |  |  | 707.4 | 562.4 | 126.3018 | 0.3875 | 707.4 | 562.4 | 126.3032
707.6 | 562.6 | 128.6127 | 127.2027 |  |  |  |  | 707.6 | 562.6 | 128.0292 | 0.3875 | 707.6 | 562.6 | 126.2072
707.8 | 562.8 | 128.5167 | 127.5866 |  |  |  |  | 707.8 | 562.8 | 128.4131 | 1.1553 | 707.8 | 562.8 | 126.3032
708 | 563 | 128.5167 | 127.3947 |  |  |  |  | 708 | 563 | 127.6454 | 0.3875 | 708 | 563 | 126.3032
708.2 | 563.2 | 128.6127 | 127.2987 |  |  |  |  | 708.2 | 563.2 | 127.1656 | 0.48349 | 708.2 | 563.2 | 126.1112
708.4 | 563.4 | 128.3248 | 127.4906 |  |  |  |  | 708.4 | 563.4 | 126.8776 | 0.1956 | 708.4 | 563.4 | 126.1112
708.6 | 563.6 | 128.4208 | 127.2987 |  |  |  |  | 708.6 | 563.6 | 126.2059 | 0.48349 | 708.6 | 563.6 | 126.2072
708.8 | 563.8 | 128.5167 | 127.3947 |  |  |  |  | 708.8 | 563.8 | 126.5897 | 0.3875 | 708.8 | 563.8 | 126.3032
709 | 564 | 128.6127 | 127.2987 |  |  |  |  | 709 | 564 | 126.4938 | 0.29155 | 709 | 564 | 126.1112
709.2 | 564.2 | 128.4208 | 127.2027 |  |  |  |  | 709.2 | 564.2 | 125.6301 | 0.3875 | 709.2 | 564.2 | 126.1112
709.4 | 564.4 | 128.4208 | 127.2027 |  |  |  |  | 709.4 | 564.4 | 124.8623 | 0.3875 | 709.4 | 564.4 | 126.0153
709.6 | 564.6 | 128.4208 | 127.2027 |  |  |  |  | 709.6 | 564.6 | 124.5744 | 0.29155 | 709.6 | 564.6 | 125.9193
709.8 | 564.8 | 128.3248 | 127.2027 |  |  |  |  | 709.8 | 564.8 | 123.9986 | 0.48349 | 709.8 | 564.8 | 125.9193
710 | 565 | 128.3248 | 127.0108 |  |  |  |  | 710 | 565 | 123.8067 | 0.48349 | 710 | 565 | 125.9193
710.2 | 565.2 | 128.2288 | 127.2027 |  |  |  |  | 710.2 | 565.2 | 122.7511 | 0.57944 | 710.2 | 565.2 | 125.9193
710.4 | 565.4 | 128.3248 | 127.2027 |  |  |  |  | 710.4 | 565.4 | 123.5188 | 0.67543 | 710.4 | 565.4 | 125.9193
710.6 | 565.6 | 128.2288 | 127.2987 |  |  |  |  | 710.6 | 565.6 | 123.1349 | 0.57944 | 710.6 | 565.6 | 125.8233
710.8 | 565.8 | 128.5167 | 127.2987 |  |  |  |  | 710.8 | 565.8 | 124.0946 | 0.57944 | 710.8 | 565.8 | 125.6314
711 | 566 | 128.1329 | 127.1068 |  |  |  |  | 711 | 566 | 121.8873 | 0.3875 | 711 | 566 | 125.5354
711.2 | 566.2 | 128.0369 | 126.9148 |  |  |  |  | 711.2 | 566.2 | 119.1043 | 0.48349 | 711.2 | 566.2 | 125.5354
711.4 | 566.4 | 127.9409 | 126.9148 |  |  |  |  | 711.4 | 566.4 | 119.2962 | 0.48349 | 711.4 | 566.4 | 125.5354
711.6 | 566.6 | 127.9409 | 126.9148 |  |  |  |  | 711.6 | 566.6 | 119.8721 | 0.48349 | 711.6 | 566.6 | 125.6314
711.8 | 566.8 | 127.9409 | 126.8188 |  |  |  |  | 711.8 | 566.8 | 119.2962 | 0.48349 | 711.8 | 566.8 | 125.5354
712 | 567 | 127.9409 | 126.7229 |  |  |  |  | 712 | 567 | 118.3366 | 0.57944 | 712 | 567 | 125.3435
712.2 | 567.2 | 127.749 | 126.7229 |  |  |  |  | 712.2 | 567.2 | 116.4172 | 0.57944 | 712.2 | 567.2 | 125.2475
712.4 | 567.4 | 127.557 | 126.435 |  |  |  |  | 712.4 | 567.4 | 115.1697 | 0.48349 | 712.4 | 567.4 | 125.0556
712.6 | 567.6 | 127.557 | 126.339 |  |  |  |  | 712.6 | 567.6 | 113.3463 | 0.1956 | 712.6 | 567.6 | 125.0556
712.8 | 567.8 | 127.4611 | 126.339 |  |  |  |  | 712.8 | 567.8 | 113.5382 | 0.3875 | 712.8 | 567.8 | 124.9596
713 | 568 | 127.4611 | 126.339 |  |  |  |  | 713 | 568 | 114.6898 | 0.1956 | 713 | 568 | 124.9596
713.2 | 568.2 | 127.557 | 126.339 |  |  |  |  | 713.2 | 568.2 | 113.7301 | 0.57944 | 713.2 | 568.2 | 124.9596
713.4 | 568.4 | 127.557 | 126.531 |  |  |  |  | 713.4 | 568.4 | 114.3059 | 0.29155 | 713.4 | 568.4 | 125.1516
713.6 | 568.6 | 127.653 | 126.531 |  |  |  |  | 713.6 | 568.6 | 114.114 | 0.29155 | 713.6 | 568.6 | 125.1516
713.8 | 568.8 | 127.557 | 126.435 |  |  |  |  | 713.8 | 568.8 | 113.2503 | 0.29155 | 713.8 | 568.8 | 124.9596
714 | 569 | 127.4611 | 126.339 |  |  |  |  | 714 | 569 | 112.6745 | 0.29155 | 714 | 569 | 124.9596
714.2 | 569.2 | 127.3651 | 126.2431 |  |  |  |  | 714.2 | 569.2 | 112.3866 | 0.3875 | 714.2 | 569.2 | 124.9596
714.4 | 569.4 | 127.4611 | 126.2431 |  |  |  |  | 714.4 | 569.4 | 112.2906 | 0.29155 | 714.4 | 569.4 | 124.8637
714.6 | 569.6 | 127.4611 | 126.2431 |  |  |  |  | 714.6 | 569.6 | 112.2906 | 0.3875 | 714.6 | 569.6 | 124.8637
714.8 | 569.8 | 127.3651 | 126.2431 |  |  |  |  | 714.8 | 569.8 | 111.7148 | 0.29155 | 714.8 | 569.8 | 124.7677
715 | 570 | 127.2692 | 126.0511 |  |  |  |  | 715 | 570 | 110.8511 | 0.29155 | 715 | 570 | 124.7677
715.2 | 570.2 | 127.749 | 126.0511 |  |  |  |  | 715.2 | 570.2 | 110.7551 | 0.29155 | 715.2 | 570.2 | 124.7677
715.4 | 570.4 | 127.3651 | 126.1471 |  |  |  |  | 715.4 | 570.4 | 110.8511 | 0.29155 | 715.4 | 570.4 | 125.0556
715.6 | 570.6 | 127.749 | 126.9148 |  |  |  |  | 715.6 | 570.6 | 116.4172 | 0.099605 | 715.6 | 570.6 | 125.6314
715.8 | 570.8 | 128.9006 | 127.6826 |  |  |  |  | 715.8 | 570.8 | 126.9736 | 0.29155 | 715.8 | 570.8 | 126.2072
716 | 571 | 128.9006 | 127.6826 |  |  |  |  | 716 | 571 | 126.3978 | 3.7464 | 716 | 571 | 126.2072
716.2 | 571.2 | 128.8046 | 127.5866 |  |  |  |  | 716.2 | 571.2 | 126.7817 | 4.5141 | 716.2 | 571.2 | 126.2072
716.4 | 571.4 | 128.9006 | 127.8745 |  |  |  |  | 716.4 | 571.4 | 127.7414 | 2.4988 | 716.4 | 571.4 | 126.3032
716.6 | 571.6 | 128.9006 | 127.7785 |  |  |  |  | 716.6 | 571.6 | 127.1656 | 0.77138 | 716.6 | 571.6 | 126.3032
716.8 | 571.8 | 128.9006 | 127.9705 |  |  |  |  | 716.8 | 571.8 | 126.9736 | 0.3875 | 716.8 | 571.8 | 126.2072
717 | 572 | 128.5167 | 127.3947 |  |  |  |  | 717 | 572 | 123.5188 | 1.5391 | 717 | 572 | 125.9193
717.2 | 572.2 | 128.1329 | 127.0108 |  |  |  |  | 717.2 | 572.2 | 120.7357 | 5.7617 | 717.2 | 572.2 | 125.6314
717.4 | 572.4 | 127.8449 | 126.6269 |  |  |  |  | 717.4 | 572.4 | 117.8567 | 2.6907 | 717.4 | 572.4 | 125.4394
717.6 | 572.6 | 128.1329 | 127.3947 |  |  |  |  | 717.6 | 572.6 | 122.1753 | 2.4988 | 717.6 | 572.6 | 125.8233
717.8 | 572.8 | 128.6127 | 127.2027 |  |  |  |  | 717.8 | 572.8 | 123.6148 | 4.0343 | 717.8 | 572.8 | 126.3032
718 | 573 | 128.4208 | 127.6826 |  |  |  |  | 718 | 573 | 126.7817 | 2.0189 | 718 | 573 | 126.0153
718.2 | 573.2 | 128.7087 | 127.4906 |  |  |  |  | 718.2 | 573.2 | 126.3978 | 1.4432 | 718.2 | 573.2 | 126.3032
718.4 | 573.4 | 128.9966 | 127.7785 |  |  |  |  | 718.4 | 573.4 | 127.0696 | 1.1553 | 718.4 | 573.4 | 126.3032
718.6 | 573.6 | 128.4208 | 127.1068 |  |  |  |  | 718.6 | 573.6 | 121.5035 | 0.77138 | 718.6 | 573.6 | 126.2072
718.8 | 573.8 | 128.3248 | 128.3543 |  |  |  |  | 718.8 | 573.8 | 127.6454 | 0.77138 | 718.8 | 573.8 | 126.0153
719 | 574 | 128.8046 | 127.4906 |  |  |  |  | 719 | 574 | 125.918 | 0.57944 | 719 | 574 | 126.0153
719.2 | 574.2 | 128.1329 | 126.9148 |  |  |  |  | 719.2 | 574.2 | 121.8873 | 0.57944 | 719.2 | 574.2 | 125.6314
719.4 | 574.4 | 128.5167 | 127.3947 |  |  |  |  | 719.4 | 574.4 | 122.5591 | 0.57944 | 719.4 | 574.4 | 125.8233
719.6 | 574.6 | 128.3248 | 127.0108 |  |  |  |  | 719.6 | 574.6 | 125.822 | 1.0593 | 719.6 | 574.6 | 126.783
719.8 | 574.8 | 128.9966 | 127.6826 |  |  |  |  | 719.8 | 574.8 | 127.7414 | 0.96332 | 719.8 | 574.8 | 126.4951
720 | 575 | 129.0925 | 127.6826 |  |  |  |  | 720 | 575 | 128.9889 | 2.9786 | 720 | 575 | 126.3991
720.2 | 575.2 | 128.7087 | 127.3947 |  |  |  |  | 720.2 | 575.2 | 125.822 | 1.0593 | 720.2 | 575.2 | 125.9193
720.4 | 575.4 | 126.3095 | 125.0915 |  |  |  |  | 720.4 | 575.4 | 100.3907 | 0.57944 | 720.4 | 575.4 | 123.6161
720.6 | 575.6 | 124.678 | 123.9398 |  |  |  |  | 720.6 | 575.6 | 83.6924 | 0.77138 | 720.6 | 575.6 | 122.4645
720.8 | 575.8 | 128.0369 | 126.9148 |  |  |  |  | 720.8 | 575.8 | 21.9855 | 0.77138 | 720.8 | 575.8 | 125.5354
721 | 576 | 129.0925 | 127.9705 |  |  |  |  | 721 | 576 | 3.5597 | 0.57944 | 721 | 576 | 126.5911
721.2 | 576.2 | 129.2844 | 128.0665 |  |  |  |  | 721.2 | 576.2 | 1.4485 | 0.48349 | 721.2 | 576.2 | 126.5911
721.4 | 576.4 | 129.1885 | 128.0665 |  |  |  |  | 721.4 | 576.4 | 0.96863 | 0.3875 | 721.4 | 576.4 | 126.5911
721.6 | 576.6 | 129.0925 | 128.0665 |  |  |  |  | 721.6 | 576.6 | 0.77673 | 0.3875 | 721.6 | 576.6 | 126.5911
721.8 | 576.8 | 129.0925 | 128.0665 |  |  |  |  | 721.8 | 576.8 | 0.68074 | 0.3875 | 721.8 | 576.8 | 126.5911
722 | 577 | 129.0925 | 127.9705 |  |  |  |  | 722 | 577 | 0.58479 | 0.29155 | 722 | 577 | 126.5911
722.2 | 577.2 | 129.1885 | 128.0665 |  |  |  |  | 722.2 | 577.2 | 0.58479 | 0.29155 | 722.2 | 577.2 | 126.5911
722.4 | 577.4 | 129.1885 | 128.0665 | [8 empty] | 722.4 | 577.4 | 126.4951
722.6 | 577.6 | 129.1885 | 127.9705 | [8 empty] | 722.6 | 577.6 | 126.5911
722.8 | 577.8 | 129.1885 | 127.9705 | [8 empty] | 722.8 | 577.8 | 126.5911
723 | 578 | 129.0925 | 127.9705 | [8 empty] | 723 | 578 | 126.5911
723.2 | 578.2 | 129.1885 | 127.9705 | [8 empty] | 723.2 | 578.2 | 126.4951
723.4 | 578.4 | 129.1885 | 127.9705 | [8 empty] | 723.4 | 578.4 | 126.4951
723.6 | 578.6 | 129.1885 | 127.9705 | [8 empty] | 723.6 | 578.6 | 126.5911
723.8 | 578.8 | 129.1885 | 128.0665 | [8 empty] | 723.8 | 578.8 | 126.5911
724 | 579 | 129.0925 | 127.9705 | [8 empty] | 724 | 579 | 126.4951
724.2 | 579.2 | 129.0925 | 127.9705 | [8 empty] | 724.2 | 579.2 | 126.4951
724.4 | 579.4 | 129.0925 | 127.9705 | [8 empty] | 724.4 | 579.4 | 126.4951
724.6 | 579.6 | 129.1885 | 127.9705 | [8 empty] | 724.6 | 579.6 | 126.5911
724.8 | 579.8 | 129.1885 | 127.9705 | [8 empty] | 724.8 | 579.8 | 126.4951
725 | 580 | 129.1885 | 128.0665 | [8 empty] | 725 | 580 | 126.3032
725.2 | 580.2 | 129.1885 | 127.9705 | [8 empty] | 725.2 | 580.2 | 126.4951
725.4 | 580.4 | 129.0925 | 127.9705 | [8 empty] | 725.4 | 580.4 | 126.3991
725.6 | 580.6 | 129.1885 | 128.0665 | [8 empty] | 725.6 | 580.6 | 126.4951
725.8 | 580.8 | 129.1885 | 127.9705 | [8 empty] | 725.8 | 580.8 | 126.5911
726 | 581 | 129.0925 | 127.9705 | [8 empty] | 726 | 581 | 126.4951
726.2 | 581.2 | 129.1885 | 127.9705 | [8 empty] | 726.2 | 581.2 | 126.4951
726.4 | 581.4 | 129.1885 | 127.9705 | [8 empty] | 726.4 | 581.4 | 126.4951
726.6 | 581.6 | 129.1885 | 128.0665 | [8 empty] | 726.6 | 581.6 | 126.5911
726.8 | 581.8 | 129.2844 | 128.0665 | [8 empty] | 726.8 | 581.8 | 126.5911
727 | 582 | 129.2844 | 128.1624 | [8 empty] | 727 | 582 | 126.5911
727.2 | 582.2 | 129.2844 | 128.0665 | [8 empty] | 727.2 | 582.2 | 126.5911
727.4 | 582.4 | 129.3804 | 128.1624 | [8 empty] | 727.4 | 582.4 | 126.5911
727.6 | 582.6 | 129.4764 | 128.2584 | [8 empty] | 727.6 | 582.6 | 126.687
727.8 | 582.8 | 129.4764 | 128.3543 | [8 empty] | 727.8 | 582.8 | 126.687
728 | 583 | 129.4764 | 128.3543 | [8 empty] | 728 | 583 | 126.783
728.2 | 583.2 | 129.4764 | 128.2584 | [8 empty] | 728.2 | 583.2 | 126.783
728.4 | 583.4 | 129.5724 | 128.3543 | [8 empty] | 728.4 | 583.4 | 126.783
728.6 | 583.6 | 129.4764 | 128.3543 | [8 empty] | 728.6 | 583.6 | 126.783
728.8 | 583.8 | 129.5724 | 128.3543 | [8 empty] | 728.8 | 583.8 | 126.783
729 | 584 | 129.4764 | 128.3543 | [8 empty] | 729 | 584 | 126.783
729.2 | 584.2 | 129.4764 | 128.3543 | [8 empty] | 729.2 | 584.2 | 126.783
729.4 | 584.4 | 129.5724 | 128.3543 | [8 empty] | 729.4 | 584.4 | 126.879
729.6 | 584.6 | 129.5724 | 128.3543 | [8 empty] | 729.6 | 584.6 | 126.783
729.8 | 584.8 | 129.4764 | 128.3543 | [8 empty] | 729.8 | 584.8 | 126.783
730 | 585 | 129.4764 | 128.2584 | [8 empty] | 730 | 585 | 126.687
730.2 | 585.2 | 129.4764 | 128.3543 | [8 empty] | 730.2 | 585.2 | 126.783
730.4 | 585.4 | 129.4764 | 128.3543 | [8 empty] | 730.4 | 585.4 | 126.783
730.6 | 585.6 | 129.5724 | 128.3543 | [8 empty] | 730.6 | 585.6 | 126.783
730.8 | 585.8 | 129.4764 | 128.3543 | [8 empty] | 730.8 | 585.8 | 126.783
731 | 586 | 129.4764 | 128.3543 | [8 empty] | 731 | 586 | 126.783
731.2 | 586.2 | 129.5724 | 128.4503 | [8 empty] | 731.2 | 586.2 | 126.783
731.4 | 586.4 | 129.4764 | 128.3543 | [8 empty] | 731.4 | 586.4 | 126.783
731.6 | 586.6 | 129.5724 | 128.3543 | [8 empty] | 731.6 | 586.6 | 126.687
731.8 | 586.8 | 129.5724 | 128.3543 | [8 empty] | 731.8 | 586.8 | 126.879
732 | 587 | 129.4764 | 128.3543 | [8 empty] | 732 | 587 | 126.687
732.2 | 587.2 | 129.5724 | 128.3543 | [8 empty] | 732.2 | 587.2 | 126.783
732.4 | 587.4 | 129.5724 | 128.3543 | [8 empty] | 732.4 | 587.4 | 126.879
732.6 | 587.6 | 129.4764 | 128.3543 | [8 empty] | 732.6 | 587.6 | 126.783
732.8 | 587.8 | 129.5724 | 128.4503 | [8 empty] | 732.8 | 587.8 | 126.783
733 | 588 | 129.5724 | 128.3543 | [8 empty] | 733 | 588 | 126.687
733.2 | 588.2 | 129.5724 | 128.3543 | [8 empty] | 733.2 | 588.2 | 126.879
733.4 | 588.4 | 129.5724 | 128.4503 | [8 empty] | 733.4 | 588.4 | 126.783
733.6 | 588.6 | 129.4764 | 128.3543 | [8 empty] | 733.6 | 588.6 | 126.783
733.8 | 588.8 | 129.5724 | 128.4503 | [8 empty] | 733.8 | 588.8 | 126.783
734 | 589 | 129.4764 | 128.2584 | [8 empty] | 734 | 589 | 126.687
734.2 | 589.2 | 129.5724 | 128.3543 | [8 empty] | 734.2 | 589.2 | 126.783
734.4 | 589.4 | 129.4764 | 128.3543 | [8 empty] | 734.4 | 589.4 | 126.783
734.6 | 589.6 | 129.4764 | 128.3543 | [8 empty] | 734.6 | 589.6 | 126.783
734.8 | 589.8 | 129.4764 | 128.3543 | [8 empty] | 734.8 | 589.8 | 126.687
735 | 590 | 129.4764 | 128.3543 | [8 empty] | 735 | 590 | 126.783
735.2 | 590.2 | 129.4764 | 128.3543 | [8 empty] | 735.2 | 590.2 | 126.783
735.4 | 590.4 | 129.4764 | 128.3543 | [8 empty] | 735.4 | 590.4 | 126.783
735.6 | 590.6 | 129.5724 | 128.3543 | [8 empty] | 735.6 | 590.6 | 126.783
735.8 | 590.8 | 129.5724 | 128.3543 | [8 empty] | 735.8 | 590.8 | 126.783
736 | 591 | 129.4764 | 128.3543 | [8 empty] | 736 | 591 | 126.687
736.2 | 591.2 | 129.5724 | 128.3543 | [8 empty] | 736.2 | 591.2 | 126.783
736.4 | 591.4 | 129.5724 | 128.3543 | [8 empty] | 736.4 | 591.4 | 126.783
736.6 | 591.6 | 129.5724 | 128.3543 | [8 empty] | 736.6 | 591.6 | 126.783
736.8 | 591.8 | 129.4764 | 128.3543 | [8 empty] | 736.8 | 591.8 | 126.783
737 | 592 | 129.4764 | 128.3543 | [8 empty] | 737 | 592 | 126.783
737.2 | 592.2 | 129.4764 | 128.2584 | [8 empty] | 737.2 | 592.2 | 126.687
737.4 | 592.4 | 129.4764 | 128.2584 | [8 empty] | 737.4 | 592.4 | 126.687
737.6 | 592.6 | 129.5724 | 128.3543 | [8 empty] | 737.6 | 592.6 | 126.783
737.8 | 592.8 | 129.4764 | 128.3543 | [8 empty] | 737.8 | 592.8 | 126.783
738 | 593 | 129.4764 | 128.2584 | [8 empty] | 738 | 593 | 126.687
738.2 | 593.2 | 129.4764 | 128.2584 | [8 empty] | 738.2 | 593.2 | 126.687
738.4 | 593.4 | 129.4764 | 128.2584 | [8 empty] | 738.4 | 593.4 | 126.687
738.6 | 593.6 | 129.4764 | 128.2584 | [8 empty] | 738.6 | 593.6 | 126.783
738.8 | 593.8 | 129.4764 | 128.2584 | [8 empty] | 738.8 | 593.8 | 126.687
739 | 594 | 129.4764 | 128.4503 | [8 empty] | 739 | 594 | 126.783
739.2 | 594.2 | 129.5724 | 128.3543 | [8 empty] | 739.2 | 594.2 | 126.783
739.4 | 594.4 | 129.4764 | 128.3543 | [8 empty] | 739.4 | 594.4 | 126.783
739.6 | 594.6 | 129.4764 | 128.2584 | [8 empty] | 739.6 | 594.6 | 126.783
739.8 | 594.8 | 129.4764 | 128.2584 | [8 empty] | 739.8 | 594.8 | 126.687
740 | 595 | 129.4764 | 128.3543 | [8 empty] | 740 | 595 | 126.783
740.2 | 595.2 | 129.4764 | 128.3543 | [8 empty] | 740.2 | 595.2 | 126.783
740.4 | 595.4 | 129.5724 | 128.3543 | [8 empty] | 740.4 | 595.4 | 126.783
740.6 | 595.6 | 129.4764 | 128.3543 | [8 empty] | 740.6 | 595.6 | 126.783
740.8 | 595.8 | 129.4764 | 128.3543 | [8 empty] | 740.8 | 595.8 | 126.783
741 | 596 | 129.4764 | 128.3543 | [8 empty] | 741 | 596 | 126.783
741.2 | 596.2 | 129.3804 | 128.3543 | [8 empty] | 741.2 | 596.2 | 126.783
741.4 | 596.4 | 129.5724 | 128.3543 | [8 empty] | 741.4 | 596.4 | 126.783
741.6 | 596.6 | 129.5724 | 128.3543 | [8 empty] | 741.6 | 596.6 | 126.687
741.8 | 596.8 | 129.4764 | 128.3543 | [8 empty] | 741.8 | 596.8 | 126.783
742 | 597 | 129.5724 | 128.3543 | [8 empty] | 742 | 597 | 126.783
742.2 | 597.2 | 129.5724 | 128.3543 | [8 empty] | 742.2 | 597.2 | 126.783
742.4 | 597.4 | 129.5724 | 128.3543 | [8 empty] | 742.4 | 597.4 | 126.783
742.6 | 597.6 | 129.4764 | 128.2584 | [8 empty] | 742.6 | 597.6 | 126.687
742.8 | 597.8 | 129.4764 | 128.2584 | [8 empty] | 742.8 | 597.8 | 126.783
743 | 598 | 129.5724 | 128.3543 | [8 empty] | 743 | 598 | 126.783
743.2 | 598.2 | 129.4764 | 128.2584 | [8 empty] | 743.2 | 598.2 | 126.783
743.4 | 598.4 | 129.4764 | 128.3543 | [8 empty] | 743.4 | 598.4 | 126.687
743.6 | 598.6 | 129.4764 | 128.3543 | [8 empty] | 743.6 | 598.6 | 126.783
743.8 | 598.8 | 129.5724 | 128.3543 | [8 empty] | 743.8 | 598.8 | 126.783
744 | 599 | 129.4764 | 128.3543 | [8 empty] | 744 | 599 | 126.687
744.2 | 599.2 | 129.4764 | 128.4503 | [8 empty] | 744.2 | 599.2 | 126.783
744.4 | 599.4 | 129.5724 | 128.4503 | [8 empty] | 744.4 | 599.4 | 126.879
744.6 | 599.6 | 129.5724 | 128.3543 | [8 empty] | 744.6 | 599.6 | 126.783
744.8 | 599.8 | 129.5724 | 128.3543 | [8 empty] | 744.8 | 599.8 | 126.783
745 | 600 | 129.5724 | 128.4503 | [8 empty] | 745 | 600 | 126.783
745.2 | 600.2 | 129.5724 | 128.4503 | [8 empty] | 745.2 | 600.2 | 126.783
745.4 | 600.4 | 129.5724 | 128.3543 | [8 empty] | 745.4 | 600.4 | 126.783
745.6 | 600.6 | 129.5724 | 128.4503 | [8 empty] | 745.6 | 600.6 | 126.783
745.8 | 600.8 | 129.5724 | 128.3543 | [8 empty] | 745.8 | 600.8 | 126.783
746 | 601 | 129.4764 | 128.4503 | [8 empty] | 746 | 601 | 126.783
746.2 | 601.2 | 129.5724 | 128.3543 | [8 empty] | 746.2 | 601.2 | 126.783
746.4 | 601.4 | 129.4764 | 128.3543 | [8 empty] | 746.4 | 601.4 | 126.783
746.6 | 601.6 | 129.5724 | 128.3543 | [8 empty] | 746.6 | 601.6 | 126.783
746.8 | 601.8 | 129.5724 | 128.3543 | [8 empty] | 746.8 | 601.8 | 126.783
747 | 602 | 129.5724 | 128.3543 | [8 empty] | 747 | 602 | 126.783
747.2 | 602.2 | 129.5724 | 128.4503 | [8 empty] | 747.2 | 602.2 | 126.879
747.4 | 602.4 | 129.5724 | 128.3543 | [8 empty] | 747.4 | 602.4 | 126.783
747.6 | 602.6 | 129.5724 | 128.4503 | [8 empty] | 747.6 | 602.6 | 126.783
747.8 | 602.8 | 129.5724 | 128.4503 | [8 empty] | 747.8 | 602.8 | 126.783
748 | 603 | 129.4764 | 128.3543 | [8 empty] | 748 | 603 | 126.783
748.2 | 603.2 | 129.5724 | 128.4503 | [8 empty] | 748.2 | 603.2 | 126.783
748.4 | 603.4 | 129.5724 | 128.3543 | [8 empty] | 748.4 | 603.4 | 126.783
748.6 | 603.6 | 129.5724 | 128.4503 | [8 empty] | 748.6 | 603.6 | 126.783
748.8 | 603.8 | 129.5724 | 128.4503 | [8 empty] | 748.8 | 603.8 | 126.783
749 | 604 | 129.5724 | 128.4503 | [8 empty] | 749 | 604 | 126.783
749.2 | 604.2 | 129.5724 | 128.4503 | [8 empty] | 749.2 | 604.2 | 126.783
749.4 | 604.4 | 129.5724 | 128.4503 | [8 empty] | 749.4 | 604.4 | 126.879
749.6 | 604.6 | 129.5724 | 128.4503 | [8 empty] | 749.6 | 604.6 | 126.879
749.8 | 604.8 | 129.5724 | 128.3543 | [8 empty] | 749.8 | 604.8 | 126.879
750 | 605 | 129.5724 | 128.4503 | [8 empty] | 750 | 605 | 126.783
750.2 | 605.2 | 129.5724 | 128.4503 | [8 empty] | 750.2 | 605.2 | 126.879
750.4 | 605.4 | 129.6683 | 128.5463 | [8 empty] | 750.4 | 605.4 | 126.879
750.6 | 605.6 | 129.5724 | 128.4503 | [8 empty] | 750.6 | 605.6 | 126.783
750.8 | 605.8 | 129.4764 | 128.3543 | [8 empty] | 750.8 | 605.8 | 126.783
751 | 606 | 129.5724 | 128.3543 | [8 empty] | 751 | 606 | 126.783
751.2 | 606.2 | 129.5724 | 128.3543 | [8 empty] | 751.2 | 606.2 | 126.783
751.4 | 606.4 | 129.4764 | 128.3543 | [8 empty] | 751.4 | 606.4 | 126.783
751.6 | 606.6 | 129.5724 | 128.4503 | [8 empty] | 751.6 | 606.6 | 126.783
751.8 | 606.8 | 129.5724 | 128.3543 | [8 empty] | 751.8 | 606.8 | 126.687
752 | 607 | 129.5724 | 128.4503 | [8 empty] | 752 | 607 | 126.783
752.2 | 607.2 | 129.5724 | 128.3543 | [8 empty] | 752.2 | 607.2 | 126.783
752.4 | 607.4 | 129.5724 | 128.3543 | [8 empty] | 752.4 | 607.4 | 126.783
752.6 | 607.6 | 129.5724 | 128.3543 | [8 empty] | 752.6 | 607.6 | 126.783
752.8 | 607.8 | 129.5724 | 128.3543 | [8 empty] | 752.8 | 607.8 | 126.783
753 | 608 | 129.5724 | 128.4503 | [8 empty] | 753 | 608 | 126.783
753.2 | 608.2 | 129.5724 | 128.3543 | [8 empty] | 753.2 | 608.2 | 126.783
753.4 | 608.4 | 129.5724 | 128.4503 | [8 empty] | 753.4 | 608.4 | 126.783
753.6 | 608.6 | 129.5724 | 128.4503 | [8 empty] | 753.6 | 608.6 | 126.783
753.8 | 608.8 | 129.5724 | 128.3543 | [8 empty] | 753.8 | 608.8 | 126.783
754 | 609 | 129.5724 | 128.3543 | [8 empty] | 754 | 609 | 126.783
754.2 | 609.2 | 129.4764 | 128.3543 | [8 empty] | 754.2 | 609.2 | 126.783
754.4 | 609.4 | 129.5724 | 128.4503 | [8 empty] | 754.4 | 609.4 | 126.783
754.6 | 609.6 | 129.5724 | 128.3543 | [8 empty] | 754.6 | 609.6 | 126.783
754.8 | 609.8 | 129.5724 | 128.4503 | [8 empty] | 754.8 | 609.8 | 126.783
755 | 610 | 129.5724 | 128.3543 | [8 empty] | 755 | 610 | 126.783
755.2 | 610.2 | 129.6683 | 128.3543 | [8 empty] | 755.2 | 610.2 | 126.783
755.4 | 610.4 | 129.6683 | 128.4503 | [8 empty] | 755.4 | 610.4 | 126.879
755.6 | 610.6 | 129.6683 | 128.4503 | [8 empty] | 755.6 | 610.6 | 126.783
755.8 | 610.8 | 129.6683 | 128.4503 | [8 empty] | 755.8 | 610.8 | 126.879
756 | 611 | 129.5724 | 128.3543 | [8 empty] | 756 | 611 | 126.687
756.2 | 611.2 | 129.5724 | 128.4503 | [8 empty] | 756.2 | 611.2 | 126.783
756.4 | 611.4 | 129.5724 | 128.4503 | [8 empty] | 756.4 | 611.4 | 126.783
756.6 | 611.6 | 129.5724 | 128.4503 | [8 empty] | 756.6 | 611.6 | 126.783
756.8 | 611.8 | 129.5724 | 128.4503 | [8 empty] | 756.8 | 611.8 | 126.879
757 | 612 | 129.5724 | 128.3543 | [8 empty] | 757 | 612 | 126.783
757.2 | 612.2 | 129.5724 | 128.4503 | [8 empty] | 757.2 | 612.2 | 126.879
757.4 | 612.4 | 129.5724 | 128.3543 | [8 empty] | 757.4 | 612.4 | 126.783
757.6 | 612.6 | 129.5724 | 128.4503 | [8 empty] | 757.6 | 612.6 | 126.879
757.8 | 612.8 | 129.5724 | 128.4503 | [8 empty] | 757.8 | 612.8 | 126.879
758 | 613 | 129.5724 | 128.3543 | [8 empty] | 758 | 613 | 126.783
758.2 | 613.2 | 129.6683 | 128.4503 | [8 empty] | 758.2 | 613.2 | 126.879
758.4 | 613.4 | 129.6683 | 128.4503 | [8 empty] | 758.4 | 613.4 | 126.783
758.6 | 613.6 | 129.6683 | 128.4503 | [8 empty] | 758.6 | 613.6 | 126.783
758.8 | 613.8 | 129.6683 | 128.4503 | [8 empty] | 758.8 | 613.8 | 126.879
759 | 614 | 129.6683 | 128.4503 | [8 empty] | 759 | 614 | 126.879
759.2 | 614.2 | 129.5724 | 128.3543 | [8 empty] | 759.2 | 614.2 | 126.783
759.4 | 614.4 | 129.5724 | 128.4503 | [8 empty] | 759.4 | 614.4 | 126.783
759.6 | 614.6 | 129.6683 | 128.4503 | [8 empty] | 759.6 | 614.6 | 126.783
759.8 | 614.8 | 129.5724 | 128.4503 | [8 empty] | 759.8 | 614.8 | 126.783
760 | 615 | 129.5724 | 128.3543 | [8 empty] | 760 | 615 | 126.783
760.2 | 615.2 | 129.5724 | 128.3543 | [8 empty] | 760.2 | 615.2 | 126.783
760.4 | 615.4 | 129.5724 | 128.3543 | [8 empty] | 760.4 | 615.4 | 126.783
760.6 | 615.6 | 129.6683 | 128.4503 | [8 empty] | 760.6 | 615.6 | 126.783
760.8 | 615.8 | 129.6683 | 128.4503 | [8 empty] | 760.8 | 615.8 | 126.783
761 | 616 | 129.6683 | 128.4503 | [8 empty] | 761 | 616 | 126.783
761.2 | 616.2 | 129.6683 | 128.4503 | [8 empty] | 761.2 | 616.2 | 126.879
761.4 | 616.4 | 129.6683 | 128.4503 | [8 empty] | 761.4 | 616.4 | 126.783
761.6 | 616.6 | 129.6683 | 128.4503 | [8 empty] | 761.6 | 616.6 | 126.879
761.8 | 616.8 | 129.6683 | 128.4503 | [8 empty] | 761.8 | 616.8 | 126.879
762 | 617 | 129.6683 | 128.4503 | [8 empty] | 762 | 617 | 126.783
762.2 | 617.2 | 129.6683 | 128.4503 | [8 empty] | 762.2 | 617.2 | 126.879
762.4 | 617.4 | 129.6683 | 128.4503 | [8 empty] | 762.4 | 617.4 | 126.879
762.6 | 617.6 | 129.6683 | 128.4503 | [8 empty] | 762.6 | 617.6 | 126.879
762.8 | 617.8 | 129.6683 | 128.4503 | [8 empty] | 762.8 | 617.8 | 126.879
763 | 618 | 129.6683 | 128.4503 | [8 empty] | 763 | 618 | 126.879
763.2 | 618.2 | 129.6683 | 128.4503 | [8 empty] | 763.2 | 618.2 | 126.879
763.4 | 618.4 | 129.6683 | 128.4503 | [8 empty] | 763.4 | 618.4 | 126.879
763.6 | 618.6 | 129.6683 | 128.4503 | [8 empty] | 763.6 | 618.6 | 126.879
763.8 | 618.8 | 129.6683 | 128.4503 | [8 empty] | 763.8 | 618.8 | 126.879
764 | 619 | 129.6683 | 128.4503 | [8 empty] | 764 | 619 | 126.879
764.2 | 619.2 | 129.7643 | 128.4503 | [8 empty] | 764.2 | 619.2 | 126.879
764.4 | 619.4 | 129.6683 | 128.4503 | [8 empty] | 764.4 | 619.4 | 126.879
764.6 | 619.6 | 129.6683 | 128.3543 | [8 empty] | 764.6 | 619.6 | 126.879
764.8 | 619.8 | 129.6683 | 128.3543 | [8 empty] | 764.8 | 619.8 | 126.783
765 | 620 | 129.6683 | 128.4503 | [8 empty] | 765 | 620 | 126.879
765.2 | 620.2 | 129.6683 | 128.3543 | [8 empty] | 765.2 | 620.2 | 126.783
765.4 | 620.4 | 129.7643 | 128.3543 | [8 empty] | 765.4 | 620.4 | 126.879
765.6 | 620.6 | 129.6683 | 128.3543 | [8 empty] | 765.6 | 620.6 | 126.783
765.8 | 620.8 | 129.6683 | 128.4503 | [8 empty] | 765.8 | 620.8 | 126.783
766 | 621 | 129.6683 | 128.3543 | [8 empty] | 766 | 621 | 126.783
766.2 | 621.2 | 129.6683 | 128.4503 | [8 empty] | 766.2 | 621.2 | 126.879
766.4 | 621.4 | 129.7643 | 128.3543 | [8 empty] | 766.4 | 621.4 | 126.783
766.6 | 621.6 | 129.7643 | 128.4503 | [8 empty] | 766.6 | 621.6 | 126.783
766.8 | 621.8 | 129.8603 | 128.5463 | [8 empty] | 766.8 | 621.8 | 126.879
767 | 622 | 129.7643 | 128.4503 | [8 empty] | 767 | 622 | 126.879
767.2 | 622.2 | 129.7643 | 128.4503 | [8 empty] | 767.2 | 622.2 | 126.879
767.4 | 622.4 | 129.7643 | 128.3543 | [8 empty] | 767.4 | 622.4 | 126.879
767.6 | 622.6 | 129.7643 | 128.4503 | [8 empty] | 767.6 | 622.6 | 126.879
767.8 | 622.8 | 129.8603 | 128.4503 | [8 empty] | 767.8 | 622.8 | 126.783
768 | 623 | 129.6683 | 128.3543 | [8 empty] | 768 | 623 | 126.783
768.2 | 623.2 | 129.7643 | 128.3543 | [8 empty] | 768.2 | 623.2 | 126.783
768.4 | 623.4 | 129.8603 | 128.4503 | [8 empty] | 768.4 | 623.4 | 126.879
768.6 | 623.6 | 129.7643 | 128.4503 | [8 empty] | 768.6 | 623.6 | 126.783
768.8 | 623.8 | 129.8603 | 128.4503 | [8 empty] | 768.8 | 623.8 | 126.783
769 | 624 | 129.8603 | 128.4503 | [8 empty] | 769 | 624 | 126.879
769.2 | 624.2 | 129.8603 | 128.4503 | [8 empty] | 769.2 | 624.2 | 126.783
769.4 | 624.4 | 129.8603 | 128.5463 | [8 empty] | 769.4 | 624.4 | 126.783
769.6 | 624.6 | 129.8603 | 128.4503 | [8 empty] | 769.6 | 624.6 | 126.879
769.8 | 624.8 | 129.9562 | 128.5463 | [8 empty] | 769.8 | 624.8 | 126.879
770 | 625 | 129.8603 | 128.5463 | [8 empty] | 770 | 625 | 126.783
770.2 | 625.2 | 129.8603 | 128.6422 | [8 empty] | 770.2 | 625.2 | 126.879
770.4 | 625.4 | 129.9562 | 128.6422 | [8 empty] | 770.4 | 625.4 | 126.879
770.6 | 625.6 | 129.9562 | 128.6422 | [8 empty] | 770.6 | 625.6 | 126.879
770.8 | 625.8 | 129.8603 | 128.6422 | [8 empty] | 770.8 | 625.8 | 126.879
771 | 626 | 129.8603 | 128.5463 | [8 empty] | 771 | 626 | 126.879
771.2 | 626.2 | 129.9562 | 128.5463 | [8 empty] | 771.2 | 626.2 | 126.879
771.4 | 626.4 | 129.8603 | 128.6422 | [8 empty] | 771.4 | 626.4 | 126.783
771.6 | 626.6 | 129.8603 | 128.6422 | [8 empty] | 771.6 | 626.6 | 126.687
771.8 | 626.8 | 129.0925 | 127.7785 | [8 empty] | 771.8 | 626.8 | 13.8296
772 | 627 | 129.7643 | 128.4503 | [8 empty] | 772 | 627 | 2.6014
772.2 | 627.2 | 129.8603 | 128.5463 | [8 empty] | 772.2 | 627.2 | 1.1619
772.4 | 627.4 | 129.9562 | 128.6422 | [8 empty] | 772.4 | 627.4 | 0.77801
772.6 | 627.6 | 129.9562 | 128.6422 | [8 empty] | 772.6 | 627.6 | 0.58611
772.8 | 627.8 | 129.9562 | 128.5463 | [8 empty] | 772.8 | 627.8 | 0.49012
773 | 628 | 129.9562 | 128.6422 | [8 empty] | 773 | 628 | 0.49012
773.2 | 628.2 | 129.9562 | 128.5463 | [8 empty] | 773.2 | 628.2 | 0.39416
773.4 | 628.4 | 129.9562 | 128.5463 | [8 empty] | 773.4 | 628.4 | 0.39416
773.6 | 628.6 | 130.0522 | 128.6422 | [8 empty] | 773.6 | 628.6 | 0.39416
773.8 | 628.8 | 129.9562 | 128.6422 | [8 empty] | 773.8 | 628.8 | 0.29817
774 | 629 | 129.9562 | 128.4503 | [8 empty] | 774 | 629 | 0.29817
774.2 | 629.2 | 130.0522 | 128.6422 | [8 empty] | 774.2 | 629.2 | 0.29817
774.4 | 629.4 | 129.9562 | 128.5463 | [8 empty] | 774.4 | 629.4 | 0.29817
774.6 | 629.6 | 130.0522 | 128.6422
774.8 | 629.8 | 129.9562 | 128.5463
775 | 630 | 129.9562 | 128.6422
775.2 | 630.2 | 129.9562 | 128.6422
775.4 | 630.4 | 129.9562 | 128.6422
775.6 | 630.6 | 129.9562 | 128.5463
775.8 | 630.8 | 129.9562 | 128.5463
776 | 631 | 129.9562 | 128.6422
776.2 | 631.2 | 129.9562 | 128.5463
776.4 | 631.4 | 129.9562 | 128.5463
776.6 | 631.6 | 129.9562 | 128.6422
776.8 | 631.8 | 129.9562 | 128.5463
777 | 632 | 129.9562 | 128.5463
777.2 | 632.2 | 129.9562 | 128.5463
777.4 | 632.4 | 129.9562 | 128.6422
777.6 | 632.6 | 129.9562 | 128.5463
777.8 | 632.8 | 129.9562 | 128.6422
778 | 633 | 129.9562 | 128.5463
778.2 | 633.2 | 129.7643 | 128.6422
778.4 | 633.4 | 129.8603 | 128.7382
778.6 | 633.6 | 129.5724 | 128.7382
778.8 | 633.8 | 130.0522 | 128.8342
779 | 634 | 129.5724 | 128.9301
779.2 | 634.2 | 128.9966 | 129.1221
779.4 | 634.4 | 128.9966 | 129.1221
779.6 | 634.6 | 128.9966 | 129.506
779.8 | 634.8 | 129.0925 | 129.8898
780 | 635 | 128.9966 | 129.6019
780.2 | 635.2 | 129.1885 | 128.8342
780.4 | 635.4 | 129.2844 | 128.7382
780.6 | 635.6 | 129.3804 | 128.6422
780.8 | 635.8 | 129.4764 | 128.4503
781 | 636 | 129.4764 | 128.3543
781.2 | 636.2 | 129.7643 | 128.4503
781.4 | 636.4 | 129.7643 | 128.4503
781.6 | 636.6 | 129.8603 | 128.4503
781.8 | 636.8 | 129.9562 | 128.5463
782 | 637 | 129.9562 | 128.5463
782.2 | 637.2 | 130.0522 | 128.6422
782.4 | 637.4 | 130.0522 | 128.5463
782.6 | 637.6 | 130.0522 | 128.5463
782.8 | 637.8 | 130.0522 | 128.6422
783 | 638 | 130.0522 | 128.6422
783.2 | 638.2 | 130.0522 | 128.6422
783.4 | 638.4 | 130.0522 | 128.7382
783.6 | 638.6 | 130.1482 | 128.6422
783.8 | 638.8 | 130.0522 | 128.6422
784 | 639 | 129.9562 | 128.6422
784.2 | 639.2 | 130.1482 | 128.7382
784.4 | 639.4 | 130.1482 | 128.6422
784.6 | 639.6 | 130.1482 | 128.6422
784.8 | 639.8 | 130.0522 | 128.6422
785 | 640 | 130.1482 | 128.6422
785.2 | 640.2 | 130.0522 | 128.6422
785.4 | 640.4 | 130.0522 | 128.6422
785.6 | 640.6 | 130.0522 | 128.6422
785.8 | 640.8 | 130.0522 | 128.6422
786 | 641 | 129.9562 | 128.5463
786.2 | 641.2 | 130.0522 | 128.5463
786.4 | 641.4 | 130.0522 | 128.5463
786.6 | 641.6 | 130.0522 | 128.5463
786.8 | 641.8 | 129.9562 | 128.5463
787 | 642 | 129.8603 | 128.4503
787.2 | 642.2 | 129.7643 | 128.5463
787.4 | 642.4 | 129.5724 | 128.3543
787.6 | 642.6 | 129.5724 | 128.4503
787.8 | 642.8 | 129.4764 | 128.5463
788 | 643 | 129.3804 | 128.6422
788.2 | 643.2 | 129.2844 | 128.8342
788.4 | 643.4 | 129.2844 | 129.2181
788.6 | 643.6 | 129.0925 | 129.8898
788.8 | 643.8 | 129.0925 | 129.2181
789 | 644 | 129.0925 | 129.0261
789.2 | 644.2 | 129.9562 | 128.8342
789.4 | 644.4 | 129.6683 | 128.8342
789.6 | 644.6 | 129.8603 | 128.7382
789.8 | 644.8 | 129.9562 | 128.7382
790 | 645 | 130.0522 | 128.6422
790.2 | 645.2 | 129.9562 | 128.6422
790.4 | 645.4 | 130.0522 | 128.6422
790.6 | 645.6 | 130.0522 | 128.5463
790.8 | 645.8 | 129.9562 | 128.4503
791 | 646 | 129.9562 | 128.6422
791.2 | 646.2 | 129.9562 | 128.5463
791.4 | 646.4 | 130.0522 | 128.6422
791.6 | 646.6 | 129.9562 | 128.5463
791.8 | 646.8 | 129.9562 | 128.6422
792 | 647 | 129.9562 | 128.6422
792.2 | 647.2 | 130.0522 | 128.4503
792.4 | 647.4 | 129.9562 | 128.5463
792.6 | 647.6 | 129.9562 | 128.5463
792.8 | 647.8 | 130.0522 | 128.5463
793 | 648 | 130.0522 | 128.5463
793.2 | 648.2 | 129.9562 | 128.5463
793.4 | 648.4 | 130.0522 | 128.6422
793.6 | 648.6 | 130.0522 | 128.5463
793.8 | 648.8 | 130.0522 | 128.5463
794 | 649 | 129.9562 | 128.5463
794.2 | 649.2 | 129.9562 | 128.5463
794.4 | 649.4 | 129.9562 | 128.6422
794.6 | 649.6 | 130.0522 | 128.5463
794.8 | 649.8 | 130.0522 | 128.5463
795 | 650 | 129.9562 | 128.5463
795.2 | 650.2 | 129.9562 | 128.5463
795.4 | 650.4 | 129.9562 | 128.4503
795.6 | 650.6 | 129.9562 | 128.4503
795.8 | 650.8 | 129.8603 | 128.4503
796 | 651 | 129.7643 | 128.2584
796.2 | 651.2 | 129.9562 | 128.3543
796.4 | 651.4 | 129.9562 | 128.3543
796.6 | 651.6 | 129.8603 | 128.3543
796.8 | 651.8 | 129.8603 | 128.3543
797 | 652 | 129.7643 | 128.3543
797.2 | 652.2 | 129.8603 | 128.3543
797.4 | 652.4 | 129.7643 | 128.2584
797.6 | 652.6 | 129.7643 | 128.3543
797.8 | 652.8 | 129.8603 | 128.3543
798 | 653 | 129.6683 | 128.2584
798.2 | 653.2 | 129.7643 | 128.3543
798.4 | 653.4 | 129.7643 | 128.3543
798.6 | 653.6 | 129.7643 | 128.2584
798.8 | 653.8 | 129.6683 | 128.2584
799 | 654 | 129.6683 | 128.2584
799.2 | 654.2 | 129.7643 | 128.2584
799.4 | 654.4 | 129.6683 | 128.3543
799.6 | 654.6 | 129.6683 | 128.1624
799.8 | 654.8 | 129.6683 | 128.2584
800 | 655 | 129.5724 | 128.2584
800.2 | 655.2 | 129.7643 | 128.2584
800.4 | 655.4 | 129.6683 | 128.2584
800.6 | 655.6 | 129.6683 | 128.2584
800.8 | 655.8 | 129.6683 | 128.2584
801 | 656 | 129.6683 | 128.2584
801.2 | 656.2 | 129.6683 | 128.2584
801.4 | 656.4 | 129.6683 | 128.2584
801.6 | 656.6 | 129.7643 | 128.3543
801.8 | 656.8 | 129.6683 | 128.2584
802 | 657 | 129.5724 | 128.1624
802.2 | 657.2 | 129.6683 | 128.1624
802.4 | 657.4 | 129.6683 | 128.2584
802.6 | 657.6 | 129.6683 | 128.2584
802.8 | 657.8 | 129.5724 | 128.1624
803 | 658 | 129.6683 | 128.1624
803.2 | 658.2 | 129.6683 | 128.1624
803.4 | 658.4 | 129.6683 | 128.1624
803.6 | 658.6 | 129.6683 | 128.2584
803.8 | 658.8 | 129.5724 | 128.1624
804 | 659 | 129.5724 | 128.1624
804.2 | 659.2 | 129.6683 | 128.1624
804.4 | 659.4 | 129.5724 | 128.1624
804.6 | 659.6 | 129.5724 | 128.1624
804.8 | 659.8 | 129.6683 | 128.1624
805 | 660 | 129.6683 | 128.2584
840 | 695 | 130.0522 | 128.6422
900 | 755 | 129.8603 | 128.7382
950 | 805 | 129.4764 | 128.2584
1000 | 855 | 129.8603 | 128.3543
1050 | 905 | 129.6683 | 128.3543
1100 | 955 | 128.9006 | 127.7785
1200 | 1055 | 128.8046 | 127.3947
1250 | 1105 | 127.8449 | 126.531
1300 | 1155 | 128.6127 | 126.7229
1350 | 1205 | 130.2441 | 127.5866
1350.2 | 1205.2 | 130.3401 | 127.6826
1350.4 | 1205.4 | 130.3401 | 127.7785
1350.6 | 1205.6 | 130.3401 | 127.7785
1350.8 | 1205.8 | 130.3401 | 127.7785
1351 | 1206 | 130.3401 | 127.7785
1351.2 | 1206.2 | 130.2441 | 127.7785
1351.4 | 1206.4 | 130.3401 | 127.7785
1351.6 | 1206.6 | 130.2441 | 127.7785
1351.8 | 1206.8 | 130.3401 | 127.7785
1352 | 1207 | 130.3401 | 127.7785
1352.2 | 1207.2 | 130.3401 | 127.7785
1352.4 | 1207.4 | 130.3401 | 127.7785
1352.6 | 1207.6 | 130.3401 | 127.7785
1352.8 | 1207.8 | 130.3401 | 127.8745
1353 | 1208 | 130.3401 | 127.7785
1353.2 | 1208.2 | 130.4361 | 127.7785
1353.4 | 1208.4 | 130.3401 | 127.7785
1353.6 | 1208.6 | 130.3401 | 127.7785
1353.8 | 1208.8 | 130.4361 | 127.7785
1354 | 1209 | 130.3401 | 127.7785
1354.2 | 1209.2 | 130.3401 | 127.6826
1354.4 | 1209.4 | 130.2441 | 127.6826
1354.6 | 1209.6 | 130.3401 | 127.6826
1354.8 | 1209.8 | 130.2441 | 127.6826
1355 | 1210 | 130.2441 | 127.6826
1355.2 | 1210.2 | 130.2441 | 127.6826
1355.4 | 1210.4 | 130.1482 | 127.6826
1355.6 | 1210.6 | 130.1482 | 127.5866
1355.8 | 1210.8 | 130.1482 | 127.5866
1356 | 1211 | 130.0522 | 127.4906
1356.2 | 1211.2 | 130.1482 | 127.4906
1356.4 | 1211.4 | 130.0522 | 127.4906
1356.6 | 1211.6 | 130.1482 | 127.4906
1356.8 | 1211.8 | 130.0522 | 127.3947
1357 | 1212 | 130.0522 | 127.4906
1357.2 | 1212.2 | 129.9562 | 127.3947
1357.4 | 1212.4 | 130.0522 | 127.3947
1357.6 | 1212.6 | 130.0522 | 127.4906
1357.8 | 1212.8 | 130.0522 | 127.3947
1358 | 1213 | 129.9562 | 127.3947
1358.2 | 1213.2 | 130.0522 | 127.2027
1358.4 | 1213.4 | 130.0522 | 127.2987
1358.6 | 1213.6 | 130.0522 | 127.2987
1358.8 | 1213.8 | 129.9562 | 127.2987
1359 | 1214 | 129.9562 | 127.2987
1359.2 | 1214.2 | 129.9562 | 127.2987
1359.4 | 1214.4 | 130.0522 | 127.2987
1359.6 | 1214.6 | 130.0522 | 127.2027
1359.8 | 1214.8 | 129.9562 | 127.2987
1360 | 1215 | 129.9562 | 127.2987
1360.2 | 1215.2 | 129.9562 | 127.2987
1360.4 | 1215.4 | 129.9562 | 127.2987
1360.6 | 1215.6 | 129.9562 | 127.2987
1360.8 | 1215.8 | 129.9562 | 127.2027
1361 | 1216 | 129.9562 | 127.2987
1361.2 | 1216.2 | 129.9562 | 127.2027
1361.4 | 1216.4 | 129.9562 | 127.2027
1361.6 | 1216.6 | 129.9562 | 127.2027
1361.8 | 1216.8 | 129.9562 | 127.2987
1362 | 1217 | 130.0522 | 127.1068
1362.2 | 1217.2 | 129.9562 | 127.2027
1362.4 | 1217.4 | 129.9562 | 127.2027
1362.6 | 1217.6 | 129.9562 | 127.2027
1362.8 | 1217.8 | 130.0522 | 127.2987
1363 | 1218 | 130.0522 | 127.2027
1363.2 | 1218.2 | 130.0522 | 127.2027
1363.4 | 1218.4 | 129.9562 | 127.2027
1363.6 | 1218.6 | 129.9562 | 127.2027
1363.8 | 1218.8 | 129.9562 | 127.2027
1364 | 1219 | 129.8603 | 127.1068
1364.2 | 1219.2 | 129.8603 | 127.2027
1364.4 | 1219.4 | 129.8603 | 127.2027
1364.6 | 1219.6 | 129.9562 | 127.1068
1364.8 | 1219.8 | 129.9562 | 127.1068
1365 | 1220 | 129.9562 | 127.1068
1365.2 | 1220.2 | 129.8603 | 127.1068
1365.4 | 1220.4 | 129.8603 | 127.1068
1365.6 | 1220.6 | 129.7643 | 127.0108
1365.8 | 1220.8 | 129.8603 | 127.0108
1366 | 1221 | 129.6683 | 126.9148
1366.2 | 1221.2 | 129.6683 | 127.0108
1366.4 | 1221.4 | 129.7643 | 127.0108
1366.6 | 1221.6 | 129.7643 | 127.0108
1366.8 | 1221.8 | 129.6683 | 126.8188
1367 | 1222 | 129.7643 | 126.8188
1367.2 | 1222.2 | 129.6683 | 126.9148
1367.4 | 1222.4 | 129.6683 | 126.9148
1367.6 | 1222.6 | 129.6683 | 126.9148
1367.8 | 1222.8 | 129.6683 | 126.9148
1368 | 1223 | 129.5724 | 126.8188
1368.2 | 1223.2 | 129.6683 | 126.8188
1368.4 | 1223.4 | 129.5724 | 126.7229
1368.6 | 1223.6 | 129.6683 | 126.8188
1368.8 | 1223.8 | 129.5724 | 126.7229
1369 | 1224 | 129.6683 | 126.7229
1369.2 | 1224.2 | 129.5724 | 126.6269
1369.4 | 1224.4 | 129.6683 | 126.7229
1369.6 | 1224.6 | 129.5724 | 126.6269
1369.8 | 1224.8 | 129.5724 | 126.531
1370 | 1225 | 129.5724 | 126.7229
1370.2 | 1225.2 | 129.5724 | 126.7229
1370.4 | 1225.4 | 129.4764 | 126.6269
1370.6 | 1225.6 | 129.4764 | 126.6269
1370.8 | 1225.8 | 129.3804 | 126.531
1371 | 1226 | 129.3804 | 126.531
1371.2 | 1226.2 | 129.3804 | 126.531
1371.4 | 1226.4 | 129.3804 | 126.531
1371.6 | 1226.6 | 129.3804 | 126.435
1371.8 | 1226.8 | 129.3804 | 126.435
1372 | 1227 | 129.2844 | 126.339
1372.2 | 1227.2 | 129.2844 | 126.339
1372.4 | 1227.4 | 129.2844 | 126.435
1372.6 | 1227.6 | 129.1885 | 126.435
1372.8 | 1227.8 | 129.1885 | 126.435
1373 | 1228 | 129.1885 | 126.339
1373.2 | 1228.2 | 129.1885 | 126.1471
1373.4 | 1228.4 | 129.1885 | 126.2431
1373.6 | 1228.6 | 129.1885 | 126.2431
1373.8 | 1228.8 | 129.1885 | 126.2431
1374 | 1229 | 128.9966 | 125.8592
1374.2 | 1229.2 | 128.9966 | 125.9552
1374.4 | 1229.4 | 128.9966 | 125.9552
1374.6 | 1229.6 | 128.9966 | 125.9552
1374.8 | 1229.8 | 128.9006 | 125.8592
1375 | 1230 | 128.9966 | 125.7632
1375.2 | 1230.2 | 128.9966 | 125.7632
1375.4 | 1230.4 | 128.9966 | 125.7632
1375.6 | 1230.6 | 128.9006 | 125.6673
1375.8 | 1230.8 | 128.9006 | 125.6673
1376 | 1231 | 128.7087 | 125.5713
1376.2 | 1231.2 | 128.8046 | 125.5713
1376.4 | 1231.4 | 128.8046 | 125.4753
1376.6 | 1231.6 | 128.8046 | 125.4753
1376.8 | 1231.8 | 128.8046 | 125.4753
1377 | 1232 | 128.8046 | 125.3793
1377.2 | 1232.2 | 128.9006 | 125.3793
1377.4 | 1232.4 | 128.8046 | 125.7632
1377.6 | 1232.6 | 128.8046 | 125.7632
1377.8 | 1232.8 | 128.8046 | 125.7632
1378 | 1233 | 128.7087 | 125.6673
1378.2 | 1233.2 | 128.7087 | 125.7632
1378.4 | 1233.4 | 128.7087 | 125.7632
1378.6 | 1233.6 | 128.7087 | 125.6673
1378.8 | 1233.8 | 128.7087 | 125.6673
1379 | 1234 | 128.7087 | 125.6673
1379.2 | 1234.2 | 128.6127 | 125.6673
1379.4 | 1234.4 | 128.6127 | 125.5713
1379.6 | 1234.6 | 128.7087 | 125.5713
1379.8 | 1234.8 | 128.7087 | 125.6673
1380 | 1235 | 128.7087 | 125.5713
1380.2 | 1235.2 | 128.6127 | 125.5713
1380.4 | 1235.4 | 128.6127 | 125.5713
1380.6 | 1235.6 | 128.7087 | 125.5713
1380.8 | 1235.8 | 128.6127 | 125.5713
1381 | 1236 | 128.6127 | 125.5713
1381.2 | 1236.2 | 128.6127 | 125.4753
1381.4 | 1236.4 | 128.6127 | 125.5713
1381.6 | 1236.6 | 128.5167 | 125.4753
1381.8 | 1236.8 | 128.6127 | 125.5713
1382 | 1237 | 128.6127 | 125.4753
1382.2 | 1237.2 | 128.5167 | 125.4753
1382.4 | 1237.4 | 128.4208 | 125.4753
1382.6 | 1237.6 | 128.4208 | 125.3793
1382.8 | 1237.8 | 128.4208 | 125.3793
1383 | 1238 | 128.3248 | 125.2834
1383.2 | 1238.2 | 128.3248 | 125.2834
1383.4 | 1238.4 | 128.3248 | 125.2834
1383.6 | 1238.6 | 128.3248 | 125.2834
1383.8 | 1238.8 | 128.3248 | 125.2834
1384 | 1239 | 128.3248 | 125.1874
1384.2 | 1239.2 | 128.3248 | 125.2834
1384.4 | 1239.4 | 128.2288 | 125.1874
1384.6 | 1239.6 | 128.2288 | 125.1874
1384.8 | 1239.8 | 128.1329 | 125.0915
1385 | 1240 | 128.1329 | 125.0915
1385.2 | 1240.2 | 128.1329 | 125.0915
1385.4 | 1240.4 | 128.2288 | 125.0915
1385.6 | 1240.6 | 128.2288 | 125.1874
1385.8 | 1240.8 | 128.2288 | 125.0915
1386 | 1241 | 128.2288 | 125.0915
1386.2 | 1241.2 | 128.2288 | 125.1874
1386.4 | 1241.4 | 128.2288 | 125.0915
1386.6 | 1241.6 | 128.3248 | 125.1874
1386.8 | 1241.8 | 128.2288 | 125.1874
1387 | 1242 | 128.3248 | 125.1874
1387.2 | 1242.2 | 128.2288 | 124.9955
1387.4 | 1242.4 | 128.2288 | 125.1874
1387.6 | 1242.6 | 128.3248 | 125.1874
1387.8 | 1242.8 | 128.2288 | 125.1874
1388 | 1243 | 128.3248 | 125.1874
1388.2 | 1243.2 | 128.3248 | 125.1874
1388.4 | 1243.4 | 128.2288 | 125.2834
1388.6 | 1243.6 | 128.3248 | 125.1874
1388.8 | 1243.8 | 128.3248 | 125.1874
1389 | 1244 | 128.3248 | 125.1874
1389.2 | 1244.2 | 128.2288 | 125.1874
1389.4 | 1244.4 | 128.2288 | 125.0915
1389.6 | 1244.6 | 128.1329 | 125.0915
1389.8 | 1244.8 | 128.2288 | 124.9955
1390 | 1245 | 128.2288 | 124.9955
1390.2 | 1245.2 | 128.2288 | 124.8995
1390.4 | 1245.4 | 128.2288 | 124.8995
1390.6 | 1245.6 | 128.2288 | 124.8995
1390.8 | 1245.8 | 128.2288 | 124.9955
1391 | 1246 | 128.2288 | 124.9955
1391.2 | 1246.2 | 128.2288 | 124.8995
1391.4 | 1246.4 | 128.3248 | 124.9955
1391.6 | 1246.6 | 128.2288 | 124.9955
1391.8 | 1246.8 | 128.2288 | 124.8995
1392 | 1247 | 128.2288 | 124.8995
1392.2 | 1247.2 | 128.2288 | 124.8036
1392.4 | 1247.4 | 128.2288 | 124.8995
1392.6 | 1247.6 | 128.3248 | 124.8995
1392.8 | 1247.8 | 128.2288 | 124.8995
1393 | 1248 | 128.2288 | 124.8995
1393.2 | 1248.2 | 128.2288 | 124.8995
1393.4 | 1248.4 | 128.2288 | 124.8995
1393.6 | 1248.6 | 128.2288 | 124.8036
1393.8 | 1248.8 | 128.2288 | 124.8995
1394 | 1249 | 128.2288 | 124.8036
1394.2 | 1249.2 | 128.2288 | 124.8036
1394.4 | 1249.4 | 128.2288 | 124.8036
1394.6 | 1249.6 | 128.2288 | 124.7076
1394.8 | 1249.8 | 128.3248 | 124.8036
1395 | 1250 | 128.2288 | 124.8036
1395.2 | 1250.2 | 128.2288 | 124.8036
1395.4 | 1250.4 | 128.2288 | 124.8036
1395.6 | 1250.6 | 128.3248 | 124.8036
1395.8 | 1250.8 | 128.2288 | 124.8995
1396 | 1251 | 128.1329 | 124.8036
1396.2 | 1251.2 | 128.1329 | 124.8036
1396.4 | 1251.4 | 128.2288 | 124.8036
1396.6 | 1251.6 | 128.2288 | 124.8036
1396.8 | 1251.8 | 128.2288 | 124.7076
1397 | 1252 | 128.2288 | 124.7076
1397.2 | 1252.2 | 128.2288 | 124.8036
1397.4 | 1252.4 | 128.2288 | 124.7076
1397.6 | 1252.6 | 128.2288 | 124.7076
1397.8 | 1252.8 | 128.1329 | 124.7076
1398 | 1253 | 128.2288 | 124.6116
1398.2 | 1253.2 | 128.1329 | 124.6116
1398.4 | 1253.4 | 128.1329 | 124.7076
1398.6 | 1253.6 | 128.2288 | 124.7076
1398.8 | 1253.8 | 128.2288 | 124.6116
1399 | 1254 | 128.2288 | 124.5157
1399.2 | 1254.2 | 128.2288 | 124.6116
1399.4 | 1254.4 | 128.2288 | 124.5157
1399.6 | 1254.6 | 128.2288 | 124.5157
1399.8 | 1254.8 | 128.2288 | 124.5157
1400 | 1255 | 128.1329 | 124.4197
1400.2 | 1255.2 | 128.1329 | 124.4197
1400.4 | 1255.4 | 128.2288 | 124.5157
1400.6 | 1255.6 | 128.2288 | 124.4197
1400.8 | 1255.8 | 128.2288 | 124.4197
1401 | 1256 | 128.2288 | 124.5157
1401.2 | 1256.2 | 128.2288 | 124.4197
1401.4 | 1256.4 | 128.2288 | 124.4197
1401.6 | 1256.6 | 128.3248 | 124.4197
1401.8 | 1256.8 | 128.2288 | 124.3237
1402 | 1257 | 128.2288 | 124.3237
1402.2 | 1257.2 | 128.2288 | 124.2277
1402.4 | 1257.4 | 128.2288 | 124.3237
1402.6 | 1257.6 | 128.3248 | 124.3237
1402.8 | 1257.8 | 128.3248 | 124.5157
1403 | 1258 | 128.3248 | 124.3237
1403.2 | 1258.2 | 128.2288 | 124.2277
1403.4 | 1258.4 | 128.3248 | 124.3237
1403.6 | 1258.6 | 128.3248 | 124.2277
1403.8 | 1258.8 | 128.3248 | 124.3237
1404 | 1259 | 128.2288 | 124.1318
1404.2 | 1259.2 | 128.2288 | 124.2277
1404.4 | 1259.4 | 128.4208 | 124.2277
1404.6 | 1259.6 | 128.2288 | 124.2277
1404.8 | 1259.8 | 128.3248 | 124.2277
1405 | 1260 | 128.3248 | 124.2277
1405.2 | 1260.2 | 128.3248 | 124.2277
1405.4 | 1260.4 | 128.3248 | 124.2277
1405.6 | 1260.6 | 128.2288 | 124.1318
1405.8 | 1260.8 | 128.3248 | 124.1318
1406 | 1261 | 128.2288 | 124.1318
1406.2 | 1261.2 | 128.2288 | 124.2277
1406.4 | 1261.4 | 128.2288 | 124.1318
1406.6 | 1261.6 | 128.3248 | 124.1318
1406.8 | 1261.8 | 128.3248 | 124.3237
1407 | 1262 | 128.3248 | 124.1318
1407.2 | 1262.2 | 128.4208 | 124.1318
1407.4 | 1262.4 | 128.4208 | 124.0358
1407.6 | 1262.6 | 128.4208 | 124.0358
1407.8 | 1262.8 | 128.5167 | 124.0358
1408 | 1263 | 128.3248 | 123.9398
1408.2 | 1263.2 | 128.7087 | 124.0358
1408.4 | 1263.4 | 128.7087 | 123.9398
1408.6 | 1263.6 | 128.8046 | 124.0358
1408.8 | 1263.8 | 128.4208 | 123.9398
1409 | 1264 | 128.3248 | 123.9398
1409.2 | 1264.2 | 129.2844 | 123.8439
1409.4 | 1264.4 | 129.2844 | 123.8439
1409.6 | 1264.6 | 129.2844 | 123.8439
1409.8 | 1264.8 | 129.1885 | 123.3641
1410 | 1265 | 129.0925 | 123.9398
1410.2 | 1265.2 | 128.9966 | 123.8439
1410.4 | 1265.4 | 128.9006 | 123.6519
1410.6 | 1265.6 | 128.8046 | 123.6519
1410.8 | 1265.8 | 128.6127 | 123.46
1411 | 1266 | 128.5167 | 123.6519
1411.2 | 1266.2 | 128.4208 | 123.8439
1411.4 | 1266.4 | 128.2288 | 124.1318
1411.6 | 1266.6 | 128.2288 | 124.2277
1411.8 | 1266.8 | 128.2288 | 124.2277
1412 | 1267 | 128.2288 | 124.1318
1412.2 | 1267.2 | 128.3248 | 124.2277
1412.4 | 1267.4 | 128.2288 | 124.1318
1412.6 | 1267.6 | 128.2288 | 124.0358
1412.8 | 1267.8 | 128.1329 | 123.9398
1413 | 1268 | 128.2288 | 124.0358
1413.2 | 1268.2 | 128.1329 | 123.9398
1413.4 | 1268.4 | 128.2288 | 123.9398
1413.6 | 1268.6 | 128.1329 | 123.8439
1413.8 | 1268.8 | 128.2288 | 123.9398
1414 | 1269 | 128.2288 | 123.8439
1414.2 | 1269.2 | 128.2288 | 123.9398
1414.4 | 1269.4 | 128.2288 | 123.9398
1414.6 | 1269.6 | 128.2288 | 123.9398
1414.8 | 1269.8 | 128.3248 | 123.9398
1415 | 1270 | 128.2288 | 123.9398
1415.2 | 1270.2 | 128.2288 | 123.9398
1415.4 | 1270.4 | 128.3248 | 123.9398
1415.6 | 1270.6 | 128.2288 | 123.9398
1415.8 | 1270.8 | 128.3248 | 123.9398
1416 | 1271 | 128.2288 | 123.8439
1416.2 | 1271.2 | 128.3248 | 123.9398
1416.4 | 1271.4 | 128.2288 | 123.9398
1416.6 | 1271.6 | 128.3248 | 123.9398
1416.8 | 1271.8 | 128.3248 | 123.8439
1417 | 1272 | 128.3248 | 123.9398
1417.2 | 1272.2 | 128.3248 | 123.9398
1417.4 | 1272.4 | 128.3248 | 123.8439
1417.6 | 1272.6 | 128.3248 | 123.9398
1417.8 | 1272.8 | 128.5167 | 124.0358
1418 | 1273 | 128.3248 | 123.9398
1418.2 | 1273.2 | 128.4208 | 124.0358
1418.4 | 1273.4 | 128.4208 | 123.9398
1418.6 | 1273.6 | 128.4208 | 123.9398
1418.8 | 1273.8 | 128.4208 | 123.9398
1419 | 1274 | 128.4208 | 124.0358
1419.2 | 1274.2 | 128.4208 | 123.9398
1419.4 | 1274.4 | 128.4208 | 124.0358
1419.6 | 1274.6 | 128.5167 | 124.0358
1419.8 | 1274.8 | 128.4208 | 124.0358
1420 | 1275 | 128.4208 | 123.9398
1420.2 | 1275.2 | 128.5167 | 124.0358
1420.4 | 1275.4 | 128.4208 | 124.0358
1420.6 | 1275.6 | 128.4208 | 124.0358
1420.8 | 1275.8 | 128.4208 | 123.9398
1421 | 1276 | 128.3248 | 123.9398
1421.2 | 1276.2 | 128.4208 | 123.9398
1421.4 | 1276.4 | 128.4208 | 123.9398
1421.6 | 1276.6 | 128.3248 | 123.9398
1421.8 | 1276.8 | 128.4208 | 123.9398
1422 | 1277 | 128.3248 | 123.9398
1422.2 | 1277.2 | 128.4208 | 123.9398
1422.4 | 1277.4 | 128.4208 | 123.9398
1422.6 | 1277.6 | 128.4208 | 123.9398
1422.8 | 1277.8 | 128.3248 | 123.9398
1423 | 1278 | 128.4208 | 123.9398
1423.2 | 1278.2 | 128.3248 | 123.8439
1423.4 | 1278.4 | 128.3248 | 123.8439
1423.6 | 1278.6 | 128.3248 | 123.8439
1423.8 | 1278.8 | 128.3248 | 123.8439
1424 | 1279 | 128.2288 | 123.7479
1424.2 | 1279.2 | 128.2288 | 123.7479
1424.4 | 1279.4 | 128.2288 | 123.8439
1424.6 | 1279.6 | 128.2288 | 123.6519
1424.8 | 1279.8 | 128.2288 | 123.7479
1425 | 1280 | 128.2288 | 123.7479
1425.2 | 1280.2 | 128.2288 | 123.7479
1425.4 | 1280.4 | 128.3248 | 123.7479
1425.6 | 1280.6 | 128.3248 | 123.6519
1425.8 | 1280.8 | 128.3248 | 123.7479
1426 | 1281 | 128.2288 | 123.7479
1426.2 | 1281.2 | 128.3248 | 123.7479
1426.4 | 1281.4 | 128.3248 | 123.8439
1426.6 | 1281.6 | 128.4208 | 123.8439
1426.8 | 1281.8 | 128.4208 | 123.8439
1427 | 1282 | 128.5167 | 123.8439
1427.2 | 1282.2 | 128.4208 | 123.8439
1427.4 | 1282.4 | 128.4208 | 123.8439
1427.6 | 1282.6 | 128.3248 | 123.8439
1427.8 | 1282.8 | 128.4208 | 123.8439
1428 | 1283 | 128.4208 | 123.7479
1428.2 | 1283.2 | 128.5167 | 123.8439
1428.4 | 1283.4 | 128.5167 | 123.8439
1428.6 | 1283.6 | 128.4208 | 123.7479
1428.8 | 1283.8 | 128.4208 | 123.8439
1429 | 1284 | 128.4208 | 123.9398
1429.2 | 1284.2 | 128.5167 | 123.9398
1429.4 | 1284.4 | 128.5167 | 123.9398
1429.6 | 1284.6 | 128.6127 | 123.9398
1429.8 | 1284.8 | 128.5167 | 123.9398
1430 | 1285 | 128.5167 | 123.8439
1430.2 | 1285.2 | 128.6127 | 123.9398
1430.4 | 1285.4 | 128.6127 | 123.9398
1430.6 | 1285.6 | 128.6127 | 123.9398
1430.8 | 1285.8 | 128.6127 | 123.8439
1431 | 1286 | 128.6127 | 123.8439
1431.2 | 1286.2 | 128.6127 | 123.8439
1431.4 | 1286.4 | 128.6127 | 123.8439
1431.6 | 1286.6 | 128.7087 | 123.9398
1431.8 | 1286.8 | 128.7087 | 124.0358
1432 | 1287 | 128.6127 | 123.9398
1432.2 | 1287.2 | 128.7087 | 124.0358
1432.4 | 1287.4 | 128.7087 | 124.0358
1432.6 | 1287.6 | 128.7087 | 124.0358
1432.8 | 1287.8 | 128.7087 | 123.9398
1433 | 1288 | 128.7087 | 123.9398
1433.2 | 1288.2 | 128.7087 | 123.9398
1433.4 | 1288.4 | 128.7087 | 123.9398
1433.6 | 1288.6 | 128.7087 | 123.8439
1433.8 | 1288.8 | 128.7087 | 123.7479
1434 | 1289 | 128.7087 | 123.9398
1434.2 | 1289.2 | 128.8046 | 123.9398
1434.4 | 1289.4 | 128.8046 | 123.9398
1434.6 | 1289.6 | 128.8046 | 123.9398
1434.8 | 1289.8 | 128.9006 | 124.0358
1435 | 1290 | 128.9006 | 124.0358
1435.2 | 1290.2 | 128.9006 | 124.0358
1435.4 | 1290.4 | 128.8046 | 124.0358
1435.6 | 1290.6 | 128.9006 | 124.0358
1435.8 | 1290.8 | 128.9006 | 124.0358
1436 | 1291 | 128.9006 | 124.0358
1436.2 | 1291.2 | 128.8046 | 124.0358
1436.4 | 1291.4 | 128.9006 | 124.0358
1436.6 | 1291.6 | 128.9006 | 124.0358
1436.8 | 1291.8 | 128.9006 | 124.3237
1437 | 1292 | 128.9006 | 124.5157
1437.2 | 1292.2 | 128.8046 | 124.5157
1437.4 | 1292.4 | 128.9006 | 124.1318
1437.6 | 1292.6 | 128.8046 | 124.0358
1437.8 | 1292.8 | 128.9006 | 124.0358
1438 | 1293 | 128.8046 | 123.9398
1438.2 | 1293.2 | 128.9966 | 123.9398
1438.4 | 1293.4 | 128.9006 | 123.6519
1438.6 | 1293.6 | 128.9006 | 123.6519
1438.8 | 1293.8 | 128.9006 | 123.6519
1439 | 1294 | 128.9966 | 123.6519
1439.2 | 1294.2 | 128.9966 | 124.0358
1439.4 | 1294.4 | 128.9966 | 124.0358
1439.6 | 1294.6 | 128.9966 | 124.1318
1439.8 | 1294.8 | 128.9966 | 124.1318
1440 | 1295 | 128.9966 | 124.0358
1440.2 | 1295.2 | 128.9966 | 124.1318
1440.4 | 1295.4 | 129.0925 | 124.0358
1440.6 | 1295.6 | 129.0925 | 124.1318
1440.8 | 1295.8 | 129.0925 | 124.1318
1441 | 1296 | 129.0925 | 124.1318
1441.2 | 1296.2 | 129.1885 | 124.1318
1441.4 | 1296.4 | 129.0925 | 124.1318
1441.6 | 1296.6 | 129.1885 | 124.2277
1441.8 | 1296.8 | 129.0925 | 124.1318
1442 | 1297 | 129.1885 | 124.1318
1442.2 | 1297.2 | 129.1885 | 124.1318
1442.4 | 1297.4 | 129.1885 | 124.1318
1442.6 | 1297.6 | 129.1885 | 124.2277
1442.8 | 1297.8 | 129.1885 | 124.1318
1443 | 1298 | 129.3804 | 124.2277
1443.2 | 1298.2 | 129.3804 | 124.3237
1443.4 | 1298.4 | 129.3804 | 124.3237
1443.6 | 1298.6 | 129.3804 | 124.3237
1443.8 | 1298.8 | 129.4764 | 124.4197
1444 | 1299 | 129.3804 | 124.3237
1444.2 | 1299.2 | 129.4764 | 124.4197
1444.4 | 1299.4 | 129.5724 | 124.4197
1444.6 | 1299.6 | 129.5724 | 124.4197
1444.8 | 1299.8 | 129.5724 | 124.4197
1445 | 1300 | 129.5724 | 124.4197
1445.2 | 1300.2 | 129.5724 | 124.4197
1445.4 | 1300.4 | 129.6683 | 124.5157
1445.6 | 1300.6 | 129.6683 | 124.4197
1445.8 | 1300.8 | 129.6683 | 124.4197
1446 | 1301 | 129.6683 | 124.4197
1446.2 | 1301.2 | 129.6683 | 124.4197
1446.4 | 1301.4 | 129.7643 | 124.5157
1446.6 | 1301.6 | 129.7643 | 124.5157
1446.8 | 1301.8 | 129.7643 | 124.5157
1447 | 1302 | 129.7643 | 124.6116
1447.2 | 1302.2 | 129.8603 | 124.5157
1447.4 | 1302.4 | 129.7643 | 124.5157
1447.6 | 1302.6 | 129.7643 | 124.5157
1447.8 | 1302.8 | 129.8603 | 124.5157
1448 | 1303 | 129.6683 | 124.4197
1448.2 | 1303.2 | 129.7643 | 124.5157
1448.4 | 1303.4 | 129.7643 | 124.5157
1448.6 | 1303.6 | 129.8603 | 124.5157
1448.8 | 1303.8 | 129.8603 | 124.4197
1449 | 1304 | 129.8603 | 124.5157
1449.2 | 1304.2 | 129.9562 | 124.5157
1449.4 | 1304.4 | 129.8603 | 124.4197
1449.6 | 1304.6 | 129.8603 | 124.4197
1449.8 | 1304.8 | 129.9562 | 124.4197
1450 | 1305 | 129.8603 | 124.4197
1450.2 | 1305.2 | 129.9562 | 124.5157
1450.4 | 1305.4 | 129.9562 | 124.5157
1450.6 | 1305.6 | 129.9562 | 124.5157
1450.8 | 1305.8 | 130.0522 | 124.5157
1451 | 1306 | 130.1482 | 124.5157
1451.2 | 1306.2 | 130.1482 | 124.6116
1451.4 | 1306.4 | 130.0522 | 124.6116
1451.6 | 1306.6 | 130.1482 | 124.7076
1451.8 | 1306.8 | 130.1482 | 124.7076
1452 | 1307 | 130.0522 | 124.6116
1452.2 | 1307.2 | 130.1482 | 124.7076
1452.4 | 1307.4 | 130.1482 | 124.7076
1452.6 | 1307.6 | 130.1482 | 124.8036
1452.8 | 1307.8 | 130.2441 | 124.8036
1453 | 1308 | 130.1482 | 124.8036
1453.2 | 1308.2 | 130.1482 | 124.7076
1453.4 | 1308.4 | 130.1482 | 124.7076
1453.6 | 1308.6 | 130.1482 | 124.7076
1453.8 | 1308.8 | 130.2441 | 124.6116
1454 | 1309 | 130.1482 | 124.7076
1454.2 | 1309.2 | 130.1482 | 124.8036
1454.4 | 1309.4 | 129.7643 | 125.0915
1454.6 | 1309.6 | 129.2844 | 125.1874
1454.8 | 1309.8 | 129.2844 | 125.2834
1455 | 1310 | 129.4764 | 124.6116
1455.2 | 1310.2 | 129.6683 | 124.9955
1455.4 | 1310.4 | 129.9562 | 125.3793
1455.6 | 1310.6 | 130.1482 | 125.0915
1455.8 | 1310.8 | 130.2441 | 124.7076
1456 | 1311 | 130.2441 | 124.6116
1456.2 | 1311.2 | 130.3401 | 124.7076
1456.4 | 1311.4 | 130.3401 | 124.7076
1456.6 | 1311.6 | 130.2441 | 124.7076
1456.8 | 1311.8 | 130.3401 | 124.8995
1457 | 1312 | 130.3401 | 124.8036
1457.2 | 1312.2 | 130.3401 | 124.8036
1457.4 | 1312.4 | 130.3401 | 124.8036
1457.6 | 1312.6 | 130.2441 | 124.8036
1457.8 | 1312.8 | 130.3401 | 124.7076
1458 | 1313 | 130.1482 | 124.6116
1458.2 | 1313.2 | 130.3401 | 124.7076
1458.4 | 1313.4 | 130.2441 | 124.7076
1458.6 | 1313.6 | 130.2441 | 124.7076
1458.8 | 1313.8 | 130.2441 | 124.8036
1459 | 1314 | 130.2441 | 124.7076
1459.2 | 1314.2 | 130.1482 | 124.6116
1459.4 | 1314.4 | 130.1482 | 124.5157
1459.6 | 1314.6 | 130.1482 | 124.4197
1459.8 | 1314.8 | 130.1482 | 124.4197
1460 | 1315 | 130.0522 | 124.3237
1460.2 | 1315.2 | 130.0522 | 124.5157
1460.4 | 1315.4 | 130.0522 | 124.4197
1460.6 | 1315.6 | 130.0522 | 124.3237
1460.8 | 1315.8 | 129.9562 | 124.4197
1461 | 1316 | 130.0522 | 124.3237
1461.2 | 1316.2 | 130.0522 | 124.3237
1461.4 | 1316.4 | 129.9562 | 124.3237
1461.6 | 1316.6 | 129.9562 | 124.2277
1461.8 | 1316.8 | 130.0522 | 124.3237
1462 | 1317 | 130.0522 | 124.2277
1462.2 | 1317.2 | 129.9562 | 124.2277
1462.4 | 1317.4 | 130.0522 | 124.2277
1462.6 | 1317.6 | 130.0522 | 124.1318
1462.8 | 1317.8 | 130.0522 | 124.2277
1463 | 1318 | 130.0522 | 124.2277
1463.2 | 1318.2 | 129.9562 | 124.1318
1463.4 | 1318.4 | 129.9562 | 124.1318
1463.6 | 1318.6 | 129.9562 | 124.1318
1463.8 | 1318.8 | 129.9562 | 124.0358
1464 | 1319 | 129.9562 | 123.9398
1464.2 | 1319.2 | 129.9562 | 123.9398
1464.4 | 1319.4 | 130.0522 | 123.9398
1464.6 | 1319.6 | 130.0522 | 123.9398
1464.8 | 1319.8 | 130.0522 | 123.9398
1465 | 1320 | 129.9562 | 123.8439
1465.2 | 1320.2 | 129.9562 | 123.9398
1465.4 | 1320.4 | 129.9562 | 123.8439
1465.6 | 1320.6 | 130.0522 | 123.8439
1465.8 | 1320.8 | 130.0522 | 123.9398
1466 | 1321 | 129.9562 | 123.8439
1466.2 | 1321.2 | 130.0522 | 123.8439
1466.4 | 1321.4 | 129.9562 | 123.8439
1466.6 | 1321.6 | 129.8603 | 123.8439
1466.8 | 1321.8 | 129.9562 | 123.7479
1467 | 1322 | 129.8603 | 123.7479
1467.2 | 1322.2 | 129.8603 | 123.6519
1467.4 | 1322.4 | 129.8603 | 123.6519
1467.6 | 1322.6 | 129.8603 | 123.6519
1467.8 | 1322.8 | 129.8603 | 123.556
1468 | 1323 | 129.7643 | 123.556
1468.2 | 1323.2 | 129.7643 | 123.6519
1468.4 | 1323.4 | 129.7643 | 123.46
1468.6 | 1323.6 | 129.7643 | 123.46
1468.8 | 1323.8 | 129.7643 | 123.46
1469 | 1324 | 129.6683 | 123.3641
1469.2 | 1324.2 | 129.6683 | 123.3641
1469.4 | 1324.4 | 129.6683 | 123.3641
1469.6 | 1324.6 | 129.7643 | 123.2681
1469.8 | 1324.8 | 129.6683 | 123.2681
1470 | 1325 | 129.5724 | 123.1721
1470.2 | 1325.2 | 129.7643 | 123.1721
1470.4 | 1325.4 | 129.6683 | 123.1721
1470.6 | 1325.6 | 129.6683 | 123.1721
1470.8 | 1325.8 | 129.6683 | 123.0762
1471 | 1326 | 129.5724 | 123.0762
1471.2 | 1326.2 | 129.6683 | 123.0762
1471.4 | 1326.4 | 129.5724 | 123.0762
1471.6 | 1326.6 | 129.5724 | 122.9802
1471.8 | 1326.8 | 129.5724 | 122.9802
1472 | 1327 | 129.4764 | 122.9802
1472.2 | 1327.2 | 129.5724 | 122.8842
1472.4 | 1327.4 | 129.5724 | 122.8842
1472.6 | 1327.6 | 129.5724 | 122.8842
1472.8 | 1327.8 | 129.6683 | 122.9802
1473 | 1328 | 129.6683 | 122.9802
1473.2 | 1328.2 | 129.5724 | 122.8842
1473.4 | 1328.4 | 129.6683 | 122.9802
1473.6 | 1328.6 | 129.5724 | 122.9802
1473.8 | 1328.8 | 129.5724 | 122.9802
1474 | 1329 | 129.5724 | 122.9802
1474.2 | 1329.2 | 129.5724 | 123.0762
1474.4 | 1329.4 | 129.4764 | 122.9802
1474.6 | 1329.6 | 129.4764 | 122.9802
1474.8 | 1329.8 | 129.4764 | 122.9802
1475 | 1330 | 129.4764 | 122.9802
1475.2 | 1330.2 | 129.4764 | 122.9802
1475.4 | 1330.4 | 129.5724 | 122.9802
1475.6 | 1330.6 | 129.4764 | 123.6519
1475.8 | 1330.8 | 129.5724 | 122.9802
1476 | 1331 | 129.4764 | 122.8842
1476.2 | 1331.2 | 129.4764 | 122.7882
1476.4 | 1331.4 | 129.4764 | 122.7882
1476.6 | 1331.6 | 129.4764 | 122.8842
1476.8 | 1331.8 | 129.4764 | 122.8842
1477 | 1332 | 129.4764 | 122.8842
1477.2 | 1332.2 | 129.3804 | 122.7882
1477.4 | 1332.4 | 129.3804 | 122.7882
1477.6 | 1332.6 | 129.3804 | 122.6923
1477.8 | 1332.8 | 129.3804 | 122.6923
1478 | 1333 | 129.2844 | 122.5003
1478.2 | 1333.2 | 129.3804 | 122.6923
1478.4 | 1333.4 | 129.2844 | 122.5963
1478.6 | 1333.6 | 129.2844 | 122.5963
1478.8 | 1333.8 | 129.2844 | 122.5003
1479 | 1334 | 129.1885 | 122.5003
1479.2 | 1334.2 | 129.1885 | 122.5963
1479.4 | 1334.4 | 129.1885 | 122.5003
1479.6 | 1334.6 | 129.1885 | 122.4044
1479.8 | 1334.8 | 129.1885 | 122.4044
1480 | 1335 | 129.0925 | 122.3084
1480.2 | 1335.2 | 129.0925 | 122.4044
1480.4 | 1335.4 | 129.0925 | 122.3084
1480.6 | 1335.6 | 129.1885 | 122.4044
1480.8 | 1335.8 | 129.0925 | 122.3084
1481 | 1336 | 128.9966 | 122.3084
1481.2 | 1336.2 | 128.9966 | 122.3084
1481.4 | 1336.4 | 128.9966 | 122.4044
1481.6 | 1336.6 | 129.0925 | 122.3084
1481.8 | 1336.8 | 128.9966 | 122.2124
1482 | 1337 | 128.9966 | 122.2124
1482.2 | 1337.2 | 128.9966 | 122.1165
1482.4 | 1337.4 | 128.9966 | 122.2124
1482.6 | 1337.6 | 128.9966 | 122.1165
1482.8 | 1337.8 | 128.9006 | 122.1165
1483 | 1338 | 128.9006 | 122.1165
1483.2 | 1338.2 | 128.9006 | 122.1165
1483.4 | 1338.4 | 128.9966 | 122.0205
1483.6 | 1338.6 | 128.9966 | 122.0205
1483.8 | 1338.8 | 128.9006 | 122.0205
1484 | 1339 | 128.9006 | 121.9245
1484.2 | 1339.2 | 128.9006 | 122.0205
1484.4 | 1339.4 | 128.9966 | 122.0205
1484.6 | 1339.6 | 128.9006 | 122.0205
1484.8 | 1339.8 | 128.9006 | 121.9245
1485 | 1340 | 128.9006 | 121.9245
1485.2 | 1340.2 | 128.9006 | 121.9245
1485.4 | 1340.4 | 128.9006 | 121.9245
1485.6 | 1340.6 | 128.9966 | 121.9245
1485.8 | 1340.8 | 128.9006 | 121.9245
1486 | 1341 | 128.9006 | 121.9245
1486.2 | 1341.2 | 128.9006 | 121.9245
1486.4 | 1341.4 | 128.9006 | 121.9245
1486.6 | 1341.6 | 128.9006 | 122.6923
1486.8 | 1341.8 | 128.9006 | 122.7882
1487 | 1342 | 128.9006 | 122.8842
1487.2 | 1342.2 | 128.9006 | 122.8842
1487.4 | 1342.4 | 128.9006 | 122.8842
1487.6 | 1342.6 | 128.9006 | 122.8842
1487.8 | 1342.8 | 128.9006 | 122.4044
1488 | 1343 | 128.9006 | 121.9245
1488.2 | 1343.2 | 128.9006 | 121.9245
1488.4 | 1343.4 | 128.9966 | 121.7326
1488.6 | 1343.6 | 128.9006 | 121.5407
1488.8 | 1343.8 | 128.9006 | 121.5407
1489 | 1344 | 128.9006 | 121.4447
1489.2 | 1344.2 | 128.9006 | 121.5407
1489.4 | 1344.4 | 128.9006 | 121.5407
1489.6 | 1344.6 | 128.9006 | 121.4447
1489.8 | 1344.8 | 128.9966 | 121.4447
1490 | 1345 | 128.9006 | 121.3487
1490.2 | 1345.2 | 128.9006 | 121.3487
1490.4 | 1345.4 | 128.9006 | 121.3487
1490.6 | 1345.6 | 128.9966 | 121.2528
1490.8 | 1345.8 | 128.9966 | 121.3487
1491 | 1346 | 128.9006 | 121.3487
1491.2 | 1346.2 | 128.9966 | 121.3487
1491.4 | 1346.4 | 128.9966 | 121.2528
1491.6 | 1346.6 | 128.9966 | 121.2528
1491.8 | 1346.8 | 128.9966 | 121.3487
1492 | 1347 | 128.9006 | 121.2528
1492.2 | 1347.2 | 128.9966 | 121.2528
1492.4 | 1347.4 | 128.9006 | 121.2528
1492.6 | 1347.6 | 128.9006 | 121.1568
1492.8 | 1347.8 | 128.9966 | 121.2528
1493 | 1348 | 128.9006 | 121.1568
1493.2 | 1348.2 | 128.9966 | 121.2528
1493.4 | 1348.4 | 128.9966 | 121.1568
1493.6 | 1348.6 | 128.9966 | 121.1568
1493.8 | 1348.8 | 128.9006 | 121.1568
1494 | 1349 | 128.9006 | 121.2528
1494.2 | 1349.2 | 128.9966 | 121.1568
1494.4 | 1349.4 | 128.9006 | 121.0608
1494.6 | 1349.6 | 128.9006 | 121.1568
1494.8 | 1349.8 | 128.9006 | 121.0608
1495 | 1350 | 128.9006 | 121.0608
1495.2 | 1350.2 | 128.9966 | 121.1568
1495.4 | 1350.4 | 128.9966 | 121.1568
1495.6 | 1350.6 | 128.9966 | 121.1568
1495.8 | 1350.8 | 128.9006 | 121.0608
1496 | 1351 | 128.9006 | 121.0608
1496.2 | 1351.2 | 128.9006 | 121.0608
1496.4 | 1351.4 | 128.9966 | 121.0608
1496.6 | 1351.6 | 128.9966 | 121.0608
1496.8 | 1351.8 | 128.9966 | 121.0608
1497 | 1352 | 128.9006 | 121.0608
1497.2 | 1352.2 | 128.9006 | 120.9649
1497.4 | 1352.4 | 128.9006 | 121.0608
1497.6 | 1352.6 | 128.9966 | 121.0608
1497.8 | 1352.8 | 128.9966 | 120.8689
1498 | 1353 | 128.9006 | 120.9649
1498.2 | 1353.2 | 128.9006 | 120.9649
1498.4 | 1353.4 | 128.9966 | 120.9649
1498.6 | 1353.6 | 128.9966 | 121.0608
1498.8 | 1353.8 | 128.9966 | 121.0608
1499 | 1354 | 128.9966 | 120.9649
1499.2 | 1354.2 | 128.9966 | 120.9649
1499.4 | 1354.4 | 128.9966 | 120.9649
1499.6 | 1354.6 | 128.9966 | 120.9649
1499.8 | 1354.8 | 128.9966 | 120.9649
1500 | 1355 | 128.9006 | 120.9649
1500.2 | 1355.2 | 128.9966 | 120.8689
1500.4 | 1355.4 | 128.9966 | 120.9649
1500.6 | 1355.6 | 128.9006 | 120.8689
1500.8 | 1355.8 | 128.9006 | 120.8689
1501 | 1356 | 128.9966 | 120.8689
1501.2 | 1356.2 | 128.9966 | 120.7729
1501.4 | 1356.4 | 128.9006 | 120.8689
1501.6 | 1356.6 | 128.9006 | 120.7729
1501.8 | 1356.8 | 128.9006 | 120.8689
1502 | 1357 | 128.9006 | 120.7729
1502.2 | 1357.2 | 128.9006 | 120.7729
1502.4 | 1357.4 | 128.9966 | 120.8689
1502.6 | 1357.6 | 128.9006 | 120.8689
1502.8 | 1357.8 | 128.9966 | 120.8689
1503 | 1358 | 128.9006 | 120.8689
1503.2 | 1358.2 | 128.9006 | 120.8689
1503.4 | 1358.4 | 128.9006 | 120.8689
1503.6 | 1358.6 | 128.8046 | 120.7729
1503.8 | 1358.8 | 128.9006 | 120.8689
1504 | 1359 | 128.8046 | 120.7729
1504.2 | 1359.2 | 128.9006 | 120.8689
1504.4 | 1359.4 | 128.9006 | 120.485
1504.6 | 1359.6 | 128.9006 | 120.3891
1504.8 | 1359.8 | 128.9006 | 120.2931
1505 | 1360 | 128.8046 | 120.485
1505.2 | 1360.2 | 128.9006 | 120.3891
1505.4 | 1360.4 | 128.9006 | 120.1971
1505.6 | 1360.6 | 128.9006 | 120.1971
1505.8 | 1360.8 | 128.9006 | 120.1971
1506 | 1361 | 128.9006 | 120.1971
1506.2 | 1361.2 | 128.9006 | 120.1971
1506.4 | 1361.4 | 128.9006 | 120.1971
1506.6 | 1361.6 | 128.9966 | 120.1971
1506.8 | 1361.8 | 128.9006 | 120.1971
1507 | 1362 | 128.9006 | 120.1971
1507.2 | 1362.2 | 128.9006 | 120.1971
1507.4 | 1362.4 | 128.9006 | 120.1971
1507.6 | 1362.6 | 128.9966 | 120.1971
1507.8 | 1362.8 | 128.9006 | 120.1012
1508 | 1363 | 128.9006 | 120.1012
1508.2 | 1363.2 | 128.9006 | 120.1971
1508.4 | 1363.4 | 128.9006 | 120.1012
1508.6 | 1363.6 | 128.9006 | 120.1012
1508.8 | 1363.8 | 128.8046 | 120.1012
1509 | 1364 | 128.8046 | 120.1012
1509.2 | 1364.2 | 128.9006 | 120.1012
1509.4 | 1364.4 | 128.8046 | 120.1012
1509.6 | 1364.6 | 128.8046 | 120.1012
1509.8 | 1364.8 | 128.8046 | 120.1012
1510 | 1365 | 128.8046 | 120.1012
1510.2 | 1365.2 | 128.8046 | 120.1012
1510.4 | 1365.4 | 128.9006 | 120.1012
1510.6 | 1365.6 | 128.8046 | 120.0052
1510.8 | 1365.8 | 128.8046 | 120.0052
1511 | 1366 | 128.8046 | 120.1012
1511.2 | 1366.2 | 128.8046 | 120.0052
1511.4 | 1366.4 | 128.8046 | 120.0052
1511.6 | 1366.6 | 128.8046 | 120.0052
1511.8 | 1366.8 | 128.8046 | 120.0052
1512 | 1367 | 128.8046 | 120.0052
1512.2 | 1367.2 | 128.8046 | 120.0052
1512.4 | 1367.4 | 128.8046 | 120.0052
1512.6 | 1367.6 | 128.8046 | 120.1012
1512.8 | 1367.8 | 128.9006 | 120.0052
1513 | 1368 | 128.8046 | 120.0052
1513.2 | 1368.2 | 128.8046 | 120.0052
1513.4 | 1368.4 | 128.8046 | 120.0052
1513.6 | 1368.6 | 128.8046 | 119.9092
1513.8 | 1368.8 | 128.8046 | 119.9092
1514 | 1369 | 128.7087 | 119.8133
1514.2 | 1369.2 | 128.8046 | 120.0052
1514.4 | 1369.4 | 128.8046 | 120.1012
1514.6 | 1369.6 | 128.8046 | 119.9092
1514.8 | 1369.8 | 128.8046 | 119.9092
1515 | 1370 | 128.8046 | 120.0052
1515.2 | 1370.2 | 128.8046 | 119.9092
1515.4 | 1370.4 | 128.8046 | 119.9092
1515.6 | 1370.6 | 128.8046 | 119.9092
1515.8 | 1370.8 | 128.8046 | 119.9092
1516 | 1371 | 128.8046 | 119.8133
1516.2 | 1371.2 | 128.8046 | 119.8133
1516.4 | 1371.4 | 128.7087 | 119.8133
1516.6 | 1371.6 | 128.8046 | 119.8133
1516.8 | 1371.8 | 128.7087 | 119.8133
1517 | 1372 | 128.7087 | 119.7173
1517.2 | 1372.2 | 128.8046 | 119.8133
1517.4 | 1372.4 | 128.8046 | 119.7173
1517.6 | 1372.6 | 128.8046 | 119.7173
1517.8 | 1372.8 | 128.7087 | 119.7173
1518 | 1373 | 128.7087 | 119.6213
1518.2 | 1373.2 | 128.7087 | 119.7173
1518.4 | 1373.4 | 128.7087 | 119.6213
1518.6 | 1373.6 | 128.7087 | 119.7173
1518.8 | 1373.8 | 128.8046 | 119.6213
1519 | 1374 | 128.7087 | 119.7173
1519.2 | 1374.2 | 128.7087 | 119.6213
1519.4 | 1374.4 | 128.7087 | 119.6213
1519.6 | 1374.6 | 128.7087 | 119.6213
1519.8 | 1374.8 | 128.7087 | 119.6213
1520 | 1375 | 128.8046 | 119.5254
1520.2 | 1375.2 | 128.7087 | 119.4294
1520.4 | 1375.4 | 128.7087 | 119.4294
1520.6 | 1375.6 | 128.7087 | 119.4294
1520.8 | 1375.8 | 128.7087 | 119.4294
1521 | 1376 | 128.7087 | 119.4294
1521.2 | 1376.2 | 128.7087 | 119.4294
1521.4 | 1376.4 | 128.7087 | 119.4294
1521.6 | 1376.6 | 128.7087 | 119.4294
1521.8 | 1376.8 | 128.7087 | 119.4294
1522 | 1377 | 128.7087 | 119.3334
1522.2 | 1377.2 | 128.7087 | 119.3334
1522.4 | 1377.4 | 128.7087 | 119.3334
1522.6 | 1377.6 | 128.6127 | 119.3334
1522.8 | 1377.8 | 128.7087 | 119.2374
1523 | 1378 | 128.7087 | 119.3334
1523.2 | 1378.2 | 128.7087 | 119.3334
1523.4 | 1378.4 | 128.7087 | 119.4294
1523.6 | 1378.6 | 128.6127 | 119.2374
1523.8 | 1378.8 | 128.7087 | 119.3334
1524 | 1379 | 128.6127 | 119.2374
1524.2 | 1379.2 | 128.6127 | 119.1415
1524.4 | 1379.4 | 128.7087 | 119.1415
1524.6 | 1379.6 | 128.6127 | 119.1415
1524.8 | 1379.8 | 128.7087 | 119.2374
1525 | 1380 | 128.6127 | 119.1415
1525.2 | 1380.2 | 128.6127 | 119.2374
1525.4 | 1380.4 | 128.7087 | 119.1415
1525.6 | 1380.6 | 128.6127 | 119.1415
1525.8 | 1380.8 | 128.7087 | 119.1415
1526 | 1381 | 128.6127 | 119.1415
1526.2 | 1381.2 | 128.7087 | 119.1415
1526.4 | 1381.4 | 128.6127 | 119.0455
1526.6 | 1381.6 | 128.6127 | 119.0455
1526.8 | 1381.8 | 128.7087 | 119.0455
1527 | 1382 | 128.6127 | 119.0455
1527.2 | 1382.2 | 128.6127 | 119.0455
1527.4 | 1382.4 | 128.6127 | 118.9495
1527.6 | 1382.6 | 128.5167 | 118.9495
1527.8 | 1382.8 | 128.7087 | 119.0455
1528 | 1383 | 128.5167 | 118.8536
1528.2 | 1383.2 | 128.5167 | 118.8536
1528.4 | 1383.4 | 128.6127 | 118.8536
1528.6 | 1383.6 | 128.5167 | 118.7576
1528.8 | 1383.8 | 128.5167 | 118.7576
1529 | 1384 | 128.4208 | 118.7576
1529.2 | 1384.2 | 128.5167 | 118.7576
1529.4 | 1384.4 | 128.4208 | 118.6617
1529.6 | 1384.6 | 128.4208 | 118.4697
1529.8 | 1384.8 | 128.4208 | 118.5657
1530 | 1385 | 128.4208 | 118.4697
1530.2 | 1385.2 | 128.4208 | 118.5657
1530.4 | 1385.4 | 128.4208 | 118.7576
1530.6 | 1385.6 | 128.4208 | 118.5657
1530.8 | 1385.8 | 128.3248 | 118.4697
1531 | 1386 | 128.4208 | 118.4697
1531.2 | 1386.2 | 128.3248 | 118.4697
1531.4 | 1386.4 | 128.4208 | 118.4697
1531.6 | 1386.6 | 128.4208 | 118.4697
1531.8 | 1386.8 | 128.4208 | 118.3738
1532 | 1387 | 128.3248 | 118.2778
1532.2 | 1387.2 | 128.3248 | 118.2778
1532.4 | 1387.4 | 128.4208 | 118.2778
1532.6 | 1387.6 | 128.3248 | 118.2778
1532.8 | 1387.8 | 128.3248 | 118.2778
1533 | 1388 | 128.4208 | 118.2778
1533.2 | 1388.2 | 128.3248 | 118.2778
1533.4 | 1388.4 | 128.2288 | 118.1818
1533.6 | 1388.6 | 128.2288 | 118.1818
1533.8 | 1388.8 | 128.2288 | 118.0858
1534 | 1389 | 128.2288 | 118.0858
1534.2 | 1389.2 | 128.2288 | 118.0858
1534.4 | 1389.4 | 128.2288 | 117.9899
1534.6 | 1389.6 | 128.3248 | 117.8939
1534.8 | 1389.8 | 128.2288 | 117.9899
1535 | 1390 | 128.2288 | 117.8939
1535.2 | 1390.2 | 128.2288 | 117.8939
1535.4 | 1390.4 | 128.2288 | 117.8939
1535.6 | 1390.6 | 128.2288 | 117.7979
1535.8 | 1390.8 | 128.3248 | 117.7979
1536 | 1391 | 128.2288 | 117.7979
1536.2 | 1391.2 | 128.2288 | 117.7979
1536.4 | 1391.4 | 128.2288 | 117.7979
1536.6 | 1391.6 | 128.2288 | 117.702
1536.8 | 1391.8 | 128.2288 | 117.7979
1537 | 1392 | 128.3248 | 117.702
1537.2 | 1392.2 | 128.2288 | 117.7979
1537.4 | 1392.4 | 128.2288 | 117.7979
1537.6 | 1392.6 | 128.2288 | 117.702
1537.8 | 1392.8 | 128.2288 | 117.702
1538 | 1393 | 128.2288 | 117.606
1538.2 | 1393.2 | 128.2288 | 117.702
1538.4 | 1393.4 | 128.2288 | 117.702
1538.6 | 1393.6 | 128.2288 | 117.702
1538.8 | 1393.8 | 128.3248 | 117.702
1539 | 1394 | 128.2288 | 117.606
1539.2 | 1394.2 | 128.2288 | 117.606
1539.4 | 1394.4 | 128.2288 | 117.606
1539.6 | 1394.6 | 128.2288 | 117.606
1539.8 | 1394.8 | 128.2288 | 117.606
1540 | 1395 | 128.2288 | 117.7979
1540.2 | 1395.2 | 128.3248 | 117.702
1540.4 | 1395.4 | 128.3248 | 117.8939
1540.6 | 1395.6 | 128.2288 | 120.8689
1540.8 | 1395.8 | 128.2288 | 120.9649
1541 | 1396 | 128.2288 | 120.8689
1541.2 | 1396.2 | 128.3248 | 119.3334
1541.4 | 1396.4 | 128.3248 | 117.606
1541.6 | 1396.6 | 128.3248 | 117.4141
1541.8 | 1396.8 | 128.2288 | 117.3181
1542 | 1397 | 128.2288 | 117.3181
1542.2 | 1397.2 | 128.3248 | 117.3181
1542.4 | 1397.4 | 128.2288 | 117.3181
1542.6 | 1397.6 | 128.2288 | 117.3181
1542.8 | 1397.8 | 128.2288 | 117.2222
1543 | 1398 | 128.2288 | 117.2222
1543.2 | 1398.2 | 128.1329 | 117.2222
1543.4 | 1398.4 | 128.2288 | 117.1262
1543.6 | 1398.6 | 128.2288 | 117.2222
1543.8 | 1398.8 | 128.2288 | 117.1262
1544 | 1399 | 128.1329 | 117.1262
1544.2 | 1399.2 | 128.1329 | 117.1262
1544.4 | 1399.4 | 128.2288 | 117.1262
1544.6 | 1399.6 | 128.2288 | 117.1262
1544.8 | 1399.8 | 128.2288 | 117.1262
1545 | 1400 | 128.3248 | 117.1262
1545.2 | 1400.2 | 128.2288 | 117.1262
1545.4 | 1400.4 | 128.2288 | 116.9343
1545.6 | 1400.6 | 128.1329 | 117.1262
1545.8 | 1400.8 | 128.2288 | 117.2222
1546 | 1401 | 128.1329 | 117.0302
1546.2 | 1401.2 | 128.1329 | 116.9343
1546.4 | 1401.4 | 128.2288 | 117.0302
1546.6 | 1401.6 | 128.2288 | 116.9343
1546.8 | 1401.8 | 128.2288 | 116.9343
1547 | 1402 | 128.2288 | 116.8383
1547.2 | 1402.2 | 128.2288 | 116.8383
1547.4 | 1402.4 | 128.2288 | 116.8383
1547.6 | 1402.6 | 128.1329 | 116.7423
1547.8 | 1402.8 | 128.2288 | 116.7423
1548 | 1403 | 128.1329 | 116.7423
1548.2 | 1403.2 | 128.2288 | 116.7423
1548.4 | 1403.4 | 128.2288 | 116.7423
1548.6 | 1403.6 | 128.2288 | 116.7423
1548.8 | 1403.8 | 128.2288 | 116.7423
1549 | 1404 | 128.2288 | 116.6463
1549.2 | 1404.2 | 128.2288 | 116.6463
1549.4 | 1404.4 | 128.2288 | 116.6463
1549.6 | 1404.6 | 128.2288 | 116.5504
1549.8 | 1404.8 | 128.3248 | 116.6463
1550 | 1405 | 128.1329 | 116.7423
1550.2 | 1405.2 | 128.2288 | 116.5504
1550.4 | 1405.4 | 128.2288 | 116.5504
1550.6 | 1405.6 | 128.2288 | 116.4544
1550.8 | 1405.8 | 128.2288 | 116.8383
1551 | 1406 | 128.3248 | 116.6463
1551.2 | 1406.2 | 128.2288 | 116.5504
1551.4 | 1406.4 | 128.2288 | 116.5504
1551.6 | 1406.6 | 128.2288 | 116.5504
1551.8 | 1406.8 | 128.2288 | 116.5504
1552 | 1407 | 128.2288 | 116.5504
1552.2 | 1407.2 | 128.3248 | 116.5504
1552.4 | 1407.4 | 128.2288 | 116.4544
1552.6 | 1407.6 | 128.2288 | 116.4544
1552.8 | 1407.8 | 128.2288 | 116.4544
1553 | 1408 | 128.2288 | 116.3584
1553.2 | 1408.2 | 128.2288 | 116.3584
1553.4 | 1408.4 | 128.3248 | 116.3584
1553.6 | 1408.6 | 128.2288 | 116.3584
1553.8 | 1408.8 | 128.2288 | 116.4544
1554 | 1409 | 128.2288 | 116.3584
1554.2 | 1409.2 | 128.2288 | 116.4544
1554.4 | 1409.4 | 128.3248 | 116.3584
1554.6 | 1409.6 | 128.2288 | 116.3584
1554.8 | 1409.8 | 128.3248 | 116.3584
1555 | 1410 | 128.3248 | 116.4544
1555.2 | 1410.2 | 128.3248 | 116.3584
1555.4 | 1410.4 | 128.2288 | 116.4544
1555.6 | 1410.6 | 128.3248 | 116.7423
1555.8 | 1410.8 | 128.3248 | 116.3584
1556 | 1411 | 128.2288 | 116.2625
1556.2 | 1411.2 | 128.3248 | 116.2625
1556.4 | 1411.4 | 128.3248 | 116.2625
1556.6 | 1411.6 | 128.4208 | 116.4544
1556.8 | 1411.8 | 128.4208 | 116.3584
1557 | 1412 | 128.4208 | 116.3584
1557.2 | 1412.2 | 128.3248 | 116.2625
1557.4 | 1412.4 | 128.3248 | 116.2625
1557.6 | 1412.6 | 128.3248 | 116.3584
1557.8 | 1412.8 | 128.4208 | 116.2625
1558 | 1413 | 128.3248 | 116.2625
1558.2 | 1413.2 | 128.4208 | 116.2625
1558.4 | 1413.4 | 128.4208 | 116.2625
1558.6 | 1413.6 | 128.4208 | 116.2625
1558.8 | 1413.8 | 128.4208 | 116.2625
1559 | 1414 | 128.4208 | 116.2625
1559.2 | 1414.2 | 128.4208 | 116.2625
1559.4 | 1414.4 | 128.4208 | 116.2625
1559.6 | 1414.6 | 128.4208 | 116.3584
1559.8 | 1414.8 | 128.4208 | 116.4544
1560 | 1415 | 128.5167 | 116.6463
1560.2 | 1415.2 | 128.6127 | 116.4544
1560.4 | 1415.4 | 128.6127 | 116.4544
1560.6 | 1415.6 | 128.7087 | 116.3584
1560.8 | 1415.8 | 128.7087 | 116.2625
1561 | 1416 | 128.7087 | 116.3584
1561.2 | 1416.2 | 128.7087 | 116.3584
1561.4 | 1416.4 | 128.7087 | 116.3584
1561.6 | 1416.6 | 128.7087 | 116.2625
1561.8 | 1416.8 | 128.6127 | 116.2625
1562 | 1417 | 128.7087 | 116.2625
1562.2 | 1417.2 | 128.7087 | 116.0705
1562.4 | 1417.4 | 128.7087 | 116.1665
1562.6 | 1417.6 | 128.7087 | 116.1665
1562.8 | 1417.8 | 128.7087 | 116.7423
1563 | 1418 | 128.8046 | 116.1665
1563.2 | 1418.2 | 128.8046 | 116.0705
1563.4 | 1418.4 | 128.8046 | 116.0705
1563.6 | 1418.6 | 128.7087 | 116.0705
1563.8 | 1418.8 | 128.8046 | 116.0705
1564 | 1419 | 128.7087 | 116.0705
1564.2 | 1419.2 | 128.8046 | 115.9746
1564.4 | 1419.4 | 128.8046 | 116.1665
1564.6 | 1419.6 | 128.9006 | 116.1665
1564.8 | 1419.8 | 128.9006 | 116.1665
1565 | 1420 | 128.8046 | 116.0705
1565.2 | 1420.2 | 128.9006 | 116.1665
1565.4 | 1420.4 | 128.9966 | 116.1665
1565.6 | 1420.6 | 128.9966 | 116.0705
1565.8 | 1420.8 | 128.9966 | 116.0705
1566 | 1421 | 128.9006 | 115.9746
1566.2 | 1421.2 | 128.9006 | 116.0705
1566.4 | 1421.4 | 128.9006 | 116.0705
1566.6 | 1421.6 | 128.9006 | 120.0052
1566.8 | 1421.8 | 128.9006 | 120.6769
1567 | 1422 | 128.9006 | 120.1012
1567.2 | 1422.2 | 128.9006 | 118.0858
1567.4 | 1422.4 | 128.9006 | 115.6867
1567.6 | 1422.6 | 128.9966 | 115.5907
1567.8 | 1422.8 | 129.0925 | 115.5907
1568 | 1423 | 128.9006 | 115.6867
1568.2 | 1423.2 | 129.0925 | 115.6867
1568.4 | 1423.4 | 129.0925 | 115.6867
1568.6 | 1423.6 | 129.1885 | 115.6867
1568.8 | 1423.8 | 129.1885 | 115.7826
1569 | 1424 | 129.0925 | 115.7826
1569.2 | 1424.2 | 129.0925 | 115.6867
1569.4 | 1424.4 | 129.0925 | 115.5907
1569.6 | 1424.6 | 129.1885 | 115.6867
1569.8 | 1424.8 | 129.1885 | 115.7826
1570 | 1425 | 129.1885 | 115.7826
1570.2 | 1425.2 | 129.2844 | 115.8786
1570.4 | 1425.4 | 129.2844 | 115.8786
1570.6 | 1425.6 | 129.3804 | 115.8786
1570.8 | 1425.8 | 129.3804 | 115.8786
1571 | 1426 | 129.2844 | 115.8786
1571.2 | 1426.2 | 129.3804 | 115.8786
1571.4 | 1426.4 | 129.3804 | 115.8786
1571.6 | 1426.6 | 129.3804 | 116.0705
1571.8 | 1426.8 | 129.3804 | 115.8786
1572 | 1427 | 129.2844 | 115.8786
1572.2 | 1427.2 | 129.3804 | 115.9746
1572.4 | 1427.4 | 129.4764 | 115.9746
1572.6 | 1427.6 | 129.4764 | 115.8786
1572.8 | 1427.8 | 129.3804 | 115.8786
1573 | 1428 | 129.4764 | 115.9746
1573.2 | 1428.2 | 129.4764 | 115.8786
1573.4 | 1428.4 | 129.4764 | 115.8786
1573.6 | 1428.6 | 129.4764 | 115.8786
1573.8 | 1428.8 | 129.4764 | 115.7826
1574 | 1429 | 129.5724 | 115.8786
1574.2 | 1429.2 | 129.4764 | 115.8786
1574.4 | 1429.4 | 129.6683 | 115.8786
1574.6 | 1429.6 | 129.5724 | 115.7826
1574.8 | 1429.8 | 129.4764 | 115.7826
1575 | 1430 | 129.4764 | 115.7826
1575.2 | 1430.2 | 129.4764 | 118.7576
1575.4 | 1430.4 | 129.4764 | 116.1665
1575.6 | 1430.6 | 129.5724 | 115.8786
1575.8 | 1430.8 | 129.5724 | 115.7826
1576 | 1431 | 129.4764 | 115.6867
1576.2 | 1431.2 | 129.5724 | 115.7826
1576.4 | 1431.4 | 129.5724 | 115.8786
1576.6 | 1431.6 | 129.5724 | 119.5254
1576.8 | 1431.8 | 129.5724 | 119.6213
1577 | 1432 | 129.5724 | 120.8689
1577.2 | 1432.2 | 129.4764 | 120.581
1577.4 | 1432.4 | 129.5724 | 122.7882
1577.6 | 1432.6 | 129.5724 | 122.8842
1577.8 | 1432.8 | 129.6683 | 122.3084
1578 | 1433 | 129.6683 | 121.1568
1578.2 | 1433.2 | 129.5724 | 121.4447
1578.4 | 1433.4 | 129.7643 | 121.2528
1578.6 | 1433.6 | 129.5724 | 120.8689
1578.8 | 1433.8 | 129.5724 | 119.2374
1579 | 1434 | 129.6683 | 115.5907
1579.2 | 1434.2 | 129.6683 | 115.2068
1579.4 | 1434.4 | 129.6683 | 115.2068
1579.6 | 1434.6 | 129.6683 | 115.0149
1579.8 | 1434.8 | 129.7643 | 115.1109
1580 | 1435 | 129.6683 | 114.9189
1580.2 | 1435.2 | 129.6683 | 115.0149
1580.4 | 1435.4 | 129.6683 | 115.0149
1580.6 | 1435.6 | 129.6683 | 114.9189
1580.8 | 1435.8 | 129.6683 | 114.9189
1581 | 1436 | 129.7643 | 114.823
1581.2 | 1436.2 | 129.6683 | 114.727
1581.4 | 1436.4 | 129.7643 | 114.727
1581.6 | 1436.6 | 129.6683 | 114.631
1581.8 | 1436.8 | 129.7643 | 114.535
1582 | 1437 | 129.6683 | 114.535
1582.2 | 1437.2 | 129.7643 | 114.3431
1582.4 | 1437.4 | 129.6683 | 114.2472
1582.6 | 1437.6 | 129.7643 | 114.0552
1582.8 | 1437.8 | 129.7643 | 121.3487
1583 | 1438 | 129.6683 | 123.1721
1583.2 | 1438.2 | 129.7643 | 123.46
1583.4 | 1438.4 | 129.7643 | 123.6519
1583.6 | 1438.6 | 129.6683 | 123.556
1583.8 | 1438.8 | 129.7643 | 123.46
1584 | 1439 | 129.6683 | 123.2681
1584.2 | 1439.2 | 129.7643 | 123.2681
1584.4 | 1439.4 | 129.7643 | 123.0762
1584.6 | 1439.6 | 129.6683 | 123.46
1584.8 | 1439.8 | 129.8603 | 123.2681
1585 | 1440 | 129.8603 | 123.0762
1585.2 | 1440.2 | 129.8603 | 122.8842
1585.4 | 1440.4 | 129.8603 | 122.5963
1585.6 | 1440.6 | 129.7643 | 121.5407
1585.8 | 1440.8 | 129.8603 | 117.702
1586 | 1441 | 129.7643 | 114.0552
1586.2 | 1441.2 | 129.7643 | 113.5754
1586.4 | 1441.4 | 129.8603 | 113.0955
1586.6 | 1441.6 | 129.8603 | 112.8076
1586.8 | 1441.8 | 129.8603 | 112.9996
1587 | 1442 | 129.8603 | 113.3835
1587.2 | 1442.2 | 129.8603 | 112.9036
1587.4 | 1442.4 | 129.8603 | 112.5198
1587.6 | 1442.6 | 129.8603 | 112.5198
1587.8 | 1442.8 | 129.8603 | 112.5198
1588 | 1443 | 129.7643 | 112.3278
1588.2 | 1443.2 | 129.8603 | 112.3278
1588.4 | 1443.4 | 129.8603 | 111.9439
1588.6 | 1443.6 | 129.9562 | 111.5601
1588.8 | 1443.8 | 130.0522 | 111.3681
1589 | 1444 | 130.0522 | 111.5601
1589.2 | 1444.2 | 129.8603 | 111.2722
1589.4 | 1444.4 | 129.7643 | 111.4641
1589.6 | 1444.6 | 129.8603 | 111.0802
1589.8 | 1444.8 | 129.9562 | 111.0802
1590 | 1445 | 129.9562 | 111.0802
1590.2 | 1445.2 | 129.9562 | 111.0802
1590.4 | 1445.4 | 129.9562 | 111.0802
1590.6 | 1445.6 | 129.9562 | 110.7924
1590.8 | 1445.8 | 129.9562 | 110.9843
1591 | 1446 | 129.9562 | 110.7924
1591.2 | 1446.2 | 129.7643 | 110.6004
1591.4 | 1446.4 | 129.8603 | 110.6004
1591.6 | 1446.6 | 129.8603 | 110.6964
1591.8 | 1446.8 | 129.9562 | 110.8883
1592 | 1447 | 129.9562 | 110.7924
1592.2 | 1447.2 | 129.9562 | 110.6004
1592.4 | 1447.4 | 130.0522 | 110.5044
1592.6 | 1447.6 | 129.9562 | 110.6964
1592.8 | 1447.8 | 129.8603 | 110.6964
1593 | 1448 | 129.9562 | 110.1206
1593.2 | 1448.2 | 129.9562 | 110.6964
1593.4 | 1448.4 | 129.9562 | 110.3125
1593.6 | 1448.6 | 130.0522 | 109.9286
1593.8 | 1448.8 | 129.9562 | 109.8327
1594 | 1449 | 129.8603 | 110.3125
1594.2 | 1449.2 | 129.8603 | 110.3125
1594.4 | 1449.4 | 129.9562 | 110.3125
1594.6 | 1449.6 | 129.9562 | 110.0246
1594.8 | 1449.8 | 129.8603 | 110.0246
1595 | 1450 | 129.8603 | 110.0246
1595.2 | 1450.2 | 129.8603 | 110.0246
1595.4 | 1450.4 | 129.9562 | 110.4085
1595.6 | 1450.6 | 129.8603 | 110.2165
1595.8 | 1450.8 | 129.8603 | 110.3125
1596 | 1451 | 129.8603 | 110.1206
1596.2 | 1451.2 | 129.8603 | 110.2165
1596.4 | 1451.4 | 129.9562 | 110.2165
1596.6 | 1451.6 | 129.8603 | 110.2165
1596.8 | 1451.8 | 129.9562 | 110.1206
1597 | 1452 | 129.9562 | 110.0246
1597.2 | 1452.2 | 129.9562 | 110.1206
1597.4 | 1452.4 | 129.7643 | 110.1206
1597.6 | 1452.6 | 129.7643 | 110.2165
1597.8 | 1452.8 | 129.6683 | 110.2165
1598 | 1453 | 129.6683 | 109.9286
1598.2 | 1453.2 | 129.5724 | 110.2165
1598.4 | 1453.4 | 129.5724 | 110.1206
1598.6 | 1453.6 | 129.5724 | 110.0246
1598.8 | 1453.8 | 129.5724 | 109.7367
1599 | 1454 | 129.6683 | 109.8327
1599.2 | 1454.2 | 129.6683 | 109.6407
1599.4 | 1454.4 | 129.5724 | 109.5448
1599.6 | 1454.6 | 129.5724 | 109.5448
1599.8 | 1454.8 | 129.4764 | 109.5448
1600 | 1455 | 129.4764 | 109.5448
1600.2 | 1455.2 | 129.5724 | 110.7924
1600.4 | 1455.4 | 129.5724 | 109.9286
1600.6 | 1455.6 | 129.5724 | 109.6407
1600.8 | 1455.8 | 129.5724 | 110.1206
1601 | 1456 | 129.4764 | 110.1206
1601.2 | 1456.2 | 129.5724 | 109.9286
1601.4 | 1456.4 | 129.5724 | 109.8327
1601.6 | 1456.6 | 129.5724 | 109.8327
1601.8 | 1456.8 | 129.4764 | 109.7367
1602 | 1457 | 129.4764 | 109.8327
1602.2 | 1457.2 | 129.5724 | 109.8327
1602.4 | 1457.4 | 129.4764 | 110.2165
1602.6 | 1457.6 | 129.5724 | 110.2165
1602.8 | 1457.8 | 129.4764 | 110.4085
1603 | 1458 | 129.5724 | 110.4085
1603.2 | 1458.2 | 129.5724 | 110.5044
1603.4 | 1458.4 | 129.5724 | 110.4085
1603.6 | 1458.6 | 129.5724 | 110.4085
1603.8 | 1458.8 | 129.5724 | 110.3125
1604 | 1459 | 129.5724 | 110.4085
1604.2 | 1459.2 | 129.5724 | 110.5044
1604.4 | 1459.4 | 129.5724 | 110.6964
1604.6 | 1459.6 | 129.4764 | 110.4085
1604.8 | 1459.8 | 129.4764 | 110.3125
1605 | 1460 | 129.4764 | 110.3125
1605.2 | 1460.2 | 129.4764 | 110.5044
1605.4 | 1460.4 | 129.5724 | 110.5044
1605.6 | 1460.6 | 129.5724 | 110.4085
1605.8 | 1460.8 | 129.5724 | 110.4085
1606 | 1461 | 129.5724 | 110.5044
1606.2 | 1461.2 | 129.6683 | 110.4085
1606.4 | 1461.4 | 129.7643 | 110.4085
1606.6 | 1461.6 | 129.6683 | 110.3125
1606.8 | 1461.8 | 129.6683 | 110.2165
1607 | 1462 | 129.7643 | 110.2165
1607.2 | 1462.2 | 129.6683 | 110.1206
1607.4 | 1462.4 | 129.6683 | 110.2165
1607.6 | 1462.6 | 129.6683 | 109.8327
1607.8 | 1462.8 | 129.7643 | 109.9286
1608 | 1463 | 129.6683 | 110.0246
1608.2 | 1463.2 | 129.6683 | 109.8327
1608.4 | 1463.4 | 129.6683 | 109.7367
1608.6 | 1463.6 | 129.7643 | 109.6407
1608.8 | 1463.8 | 129.7643 | 109.6407
1609 | 1464 | 129.6683 | 109.7367
1609.2 | 1464.2 | 129.5724 | 109.1609
1609.4 | 1464.4 | 129.6683 | 109.3528
1609.6 | 1464.6 | 129.6683 | 109.3528
1609.8 | 1464.8 | 129.7643 | 109.3528
1610 | 1465 | 129.5724 | 109.9286
1610.2 | 1465.2 | 129.7643 | 109.5448
1610.4 | 1465.4 | 129.6683 | 109.5448
1610.6 | 1465.6 | 129.7643 | 109.5448
1610.8 | 1465.8 | 129.7643 | 109.5448
1611 | 1466 | 129.6683 | 109.5448
1611.2 | 1466.2 | 129.8603 | 109.9286
1611.4 | 1466.4 | 129.8603 | 109.6407
1611.6 | 1466.6 | 129.7643 | 109.7367
1611.8 | 1466.8 | 129.8603 | 109.5448
1612 | 1467 | 129.7643 | 110.0246
1612.2 | 1467.2 | 129.7643 | 110.0246
1612.4 | 1467.4 | 129.7643 | 110.0246
1612.6 | 1467.6 | 129.6683 | 110.0246
1612.8 | 1467.8 | 129.7643 | 110.1206
1613 | 1468 | 129.7643 | 110.1206
1613.2 | 1468.2 | 129.6683 | 110.2165
1613.4 | 1468.4 | 129.6683 | 110.2165
1613.6 | 1468.6 | 129.7643 | 110.3125
1613.8 | 1468.8 | 129.7643 | 110.3125
1614 | 1469 | 129.6683 | 110.4085
1614.2 | 1469.2 | 129.7643 | 110.4085
1614.4 | 1469.4 | 129.7643 | 110.4085
1614.6 | 1469.6 | 129.8603 | 110.5044
1614.8 | 1469.8 | 129.6683 | 110.3125
1615 | 1470 | 129.6683 | 110.5044
1615.2 | 1470.2 | 129.7643 | 110.4085
1615.4 | 1470.4 | 129.7643 | 110.6964
1615.6 | 1470.6 | 129.6683 | 110.4085
1615.8 | 1470.8 | 129.6683 | 110.6004
1616 | 1471 | 129.6683 | 110.6004
1616.2 | 1471.2 | 129.6683 | 110.6964
1616.4 | 1471.4 | 129.7643 | 110.6964
1616.6 | 1471.6 | 129.7643 | 110.6964
1616.8 | 1471.8 | 129.6683 | 110.7924
1617 | 1472 | 129.6683 | 110.8883
1617.2 | 1472.2 | 129.7643 | 110.7924
1617.4 | 1472.4 | 129.7643 | 110.8883
1617.6 | 1472.6 | 129.7643 | 110.8883
1617.8 | 1472.8 | 129.7643 | 110.6964
1618 | 1473 | 129.6683 | 110.7924
1618.2 | 1473.2 | 129.7643 | 110.5044
1618.4 | 1473.4 | 129.8603 | 110.6964
1618.6 | 1473.6 | 129.8603 | 110.9843
1618.8 | 1473.8 | 129.7643 | 110.9843
1619 | 1474 | 129.7643 | 110.4085
1619.2 | 1474.2 | 129.7643 | 109.7367
1619.4 | 1474.4 | 129.7643 | 109.6407
1619.6 | 1474.6 | 129.7643 | 109.4488
1619.8 | 1474.8 | 129.8603 | 109.0649
1620 | 1475 | 129.7643 | 108.873
1620.2 | 1475.2 | 129.8603 | 109.2569
1620.4 | 1475.4 | 129.6683 | 109.1609
1620.6 | 1475.6 | 129.8603 | 109.2569
1620.8 | 1475.8 | 129.8603 | 109.3528
1621 | 1476 | 129.8603 | 109.8327
1621.2 | 1476.2 | 129.7643 | 109.8327
1621.4 | 1476.4 | 129.8603 | 109.9286
1621.6 | 1476.6 | 129.7643 | 109.8327
1621.8 | 1476.8 | 129.7643 | 109.8327
1622 | 1477 | 129.7643 | 110.1206
1622.2 | 1477.2 | 129.7643 | 110.2165
1622.4 | 1477.4 | 129.7643 | 110.2165
1622.6 | 1477.6 | 129.7643 | 110.3125
1622.8 | 1477.8 | 129.7643 | 110.5044
1623 | 1478 | 129.7643 | 110.5044
1623.2 | 1478.2 | 129.7643 | 110.6004
1623.4 | 1478.4 | 129.7643 | 110.6004
1623.6 | 1478.6 | 129.7643 | 110.6964
1623.8 | 1478.8 | 129.7643 | 110.7924
1624 | 1479 | 129.6683 | 110.8883
1624.2 | 1479.2 | 129.7643 | 110.9843
1624.4 | 1479.4 | 129.6683 | 111.0802
1624.6 | 1479.6 | 129.7643 | 111.0802
1624.8 | 1479.8 | 129.7643 | 111.1762
1625 | 1480 | 129.7643 | 111.3681
1625.2 | 1480.2 | 129.7643 | 111.2722
1625.4 | 1480.4 | 129.7643 | 111.5601
1625.6 | 1480.6 | 129.7643 | 111.5601
1625.8 | 1480.8 | 129.7643 | 111.5601
1626 | 1481 | 129.6683 | 111.3681
1626.2 | 1481.2 | 129.7643 | 111.5601
1626.4 | 1481.4 | 129.6683 | 111.4641
1626.6 | 1481.6 | 129.7643 | 111.848
1626.8 | 1481.8 | 129.6683 | 111.5601
1627 | 1482 | 129.7643 | 111.752
1627.2 | 1482.2 | 129.6683 | 111.5601
1627.4 | 1482.4 | 129.6683 | 112.2319
1627.6 | 1482.6 | 129.7643 | 112.2319
1627.8 | 1482.8 | 129.6683 | 112.2319
1628 | 1483 | 129.6683 | 112.1359
1628.2 | 1483.2 | 129.7643 | 112.1359
1628.4 | 1483.4 | 129.7643 | 112.4238
1628.6 | 1483.6 | 129.7643 | 112.1359
1628.8 | 1483.8 | 129.7643 | 112.1359
1629 | 1484 | 129.6683 | 112.1359
1629.2 | 1484.2 | 129.6683 | 112.1359
1629.4 | 1484.4 | 129.7643 | 112.1359
1629.6 | 1484.6 | 129.7643 | 111.9439
1629.8 | 1484.8 | 129.7643 | 111.848
1630 | 1485 | 129.7643 | 112.3278
1630.2 | 1485.2 | 129.7643 | 112.5198
1630.4 | 1485.4 | 129.7643 | 112.5198
1630.6 | 1485.6 | 129.7643 | 112.7117
1630.8 | 1485.8 | 129.7643 | 112.6157
1631 | 1486 | 129.7643 | 112.5198
1631.2 | 1486.2 | 129.7643 | 112.6157
1631.4 | 1486.4 | 129.7643 | 112.2319
1631.6 | 1486.6 | 129.7643 | 112.2319
1631.8 | 1486.8 | 129.8603 | 112.6157
1632 | 1487 | 129.6683 | 112.7117
1632.2 | 1487.2 | 129.7643 | 112.9996
1632.4 | 1487.4 | 129.7643 | 113.0955
1632.6 | 1487.6 | 129.7643 | 112.9036
1632.8 | 1487.8 | 129.8603 | 112.8076
1633 | 1488 | 129.8603 | 112.9036
1633.2 | 1488.2 | 129.7643 | 112.9996
1633.4 | 1488.4 | 129.8603 | 113.1915
1633.6 | 1488.6 | 129.8603 | 113.1915
1633.8 | 1488.8 | 129.7643 | 113.2875
1634 | 1489 | 129.7643 | 113.0955
1634.2 | 1489.2 | 129.7643 | 113.0955
1634.4 | 1489.4 | 129.7643 | 113.1915
1634.6 | 1489.6 | 129.7643 | 113.2875
1634.8 | 1489.8 | 129.7643 | 113.4794
1635 | 1490 | 129.7643 | 113.5754
1635.2 | 1490.2 | 129.7643 | 113.3835
1635.4 | 1490.4 | 129.7643 | 113.3835
1635.6 | 1490.6 | 129.7643 | 113.2875
1635.8 | 1490.8 | 129.8603 | 113.3835
1636 | 1491 | 129.6683 | 113.2875
1636.2 | 1491.2 | 129.8603 | 113.3835
1636.4 | 1491.4 | 129.7643 | 113.3835
1636.6 | 1491.6 | 129.7643 | 113.3835
1636.8 | 1491.8 | 129.7643 | 113.4794
1637 | 1492 | 129.6683 | 113.3835
1637.2 | 1492.2 | 129.7643 | 113.3835
1637.4 | 1492.4 | 129.6683 | 113.4794
1637.6 | 1492.6 | 129.6683 | 113.4794
1637.8 | 1492.8 | 129.6683 | 113.5754
1638 | 1493 | 129.6683 | 113.3835
1638.2 | 1493.2 | 129.7643 | 113.5754
1638.4 | 1493.4 | 129.6683 | 113.5754
1638.6 | 1493.6 | 129.6683 | 113.5754
1638.8 | 1493.8 | 129.6683 | 113.4794
1639 | 1494 | 129.6683 | 115.1109
1639.2 | 1494.2 | 129.7643 | 115.3988
1639.4 | 1494.4 | 129.6683 | 115.4947
1639.6 | 1494.6 | 129.7643 | 115.4947
1639.8 | 1494.8 | 129.7643 | 115.4947
1640 | 1495 | 129.5724 | 115.3988
1640.2 | 1495.2 | 129.7643 | 115.3988
1640.4 | 1495.4 | 129.6683 | 115.3988
1640.6 | 1495.6 | 129.8603 | 115.3988
1640.8 | 1495.8 | 129.7643 | 115.4947
1641 | 1496 | 129.7643 | 115.5907
1641.2 | 1496.2 | 129.7643 | 115.3988
1641.4 | 1496.4 | 129.7643 | 115.3988
1641.6 | 1496.6 | 129.7643 | 115.8786
1641.8 | 1496.8 | 129.7643 | 115.4947
1642 | 1497 | 129.6683 | 115.4947
1642.2 | 1497.2 | 129.7643 | 115.3988
1642.4 | 1497.4 | 129.7643 | 115.3988
1642.6 | 1497.6 | 129.7643 | 115.3028
1642.8 | 1497.8 | 129.7643 | 116.0705
1643 | 1498 | 129.8603 | 116.7423
1643.2 | 1498.2 | 129.7643 | 115.3988
1643.4 | 1498.4 | 129.7643 | 115.3028
1643.6 | 1498.6 | 129.7643 | 115.3028
1643.8 | 1498.8 | 129.7643 | 115.2068
1644 | 1499 | 129.6683 | 115.2068
1644.2 | 1499.2 | 129.6683 | 115.1109
1644.4 | 1499.4 | 129.6683 | 115.1109
1644.6 | 1499.6 | 129.6683 | 115.0149
1644.8 | 1499.8 | 129.7643 | 115.2068
1645 | 1500 | 129.6683 | 115.0149
1645.2 | 1500.2 | 129.4764 | 114.9189
1645.4 | 1500.4 | 129.6683 | 114.9189
1645.6 | 1500.6 | 129.5724 | 114.727
1645.8 | 1500.8 | 129.6683 | 114.727
1646 | 1501 | 129.5724 | 114.535
1646.2 | 1501.2 | 129.5724 | 114.535
1646.4 | 1501.4 | 129.6683 | 114.4391
1646.6 | 1501.6 | 129.6683 | 114.2472
1646.8 | 1501.8 | 129.5724 | 114.1512
1647 | 1502 | 129.5724 | 113.8633
1647.2 | 1502.2 | 129.4764 | 114.1512
1647.4 | 1502.4 | 129.4764 | 114.1512
1647.6 | 1502.6 | 129.4764 | 113.9593
1647.8 | 1502.8 | 129.5724 | 113.8633
1648 | 1503 | 129.4764 | 113.7673
1648.2 | 1503.2 | 129.5724 | 113.7673
1648.4 | 1503.4 | 129.4764 | 113.8633
1648.6 | 1503.6 | 129.5724 | 113.9593
1648.8 | 1503.8 | 129.5724 | 113.8633
1649 | 1504 | 129.4764 | 113.8633
1649.2 | 1504.2 | 129.4764 | 113.8633
1649.4 | 1504.4 | 129.3804 | 113.9593
1649.6 | 1504.6 | 129.3804 | 113.8633
1649.8 | 1504.8 | 129.4764 | 113.9593
1650 | 1505 | 129.3804 | 113.8633
1650.2 | 1505.2 | 129.3804 | 113.8633
1650.4 | 1505.4 | 129.3804 | 113.8633
1650.6 | 1505.6 | 129.3804 | 113.8633
1650.8 | 1505.8 | 129.4764 | 113.7673
1651 | 1506 | 129.3804 | 113.8633
1651.2 | 1506.2 | 129.3804 | 113.9593
1651.4 | 1506.4 | 129.3804 | 113.9593
1651.6 | 1506.6 | 129.3804 | 113.8633
1651.8 | 1506.8 | 129.3804 | 113.7673
1652 | 1507 | 129.2844 | 113.5754
1652.2 | 1507.2 | 129.3804 | 113.4794
1652.4 | 1507.4 | 129.2844 | 117.0302
1652.6 | 1507.6 | 129.2844 | 118.9495
1652.8 | 1507.8 | 129.2844 | 115.2068
1653 | 1508 | 129.2844 | 114.631
1653.2 | 1508.2 | 129.2844 | 113.1915
1653.4 | 1508.4 | 128.9966 | 112.7117
1653.6 | 1508.6 | 129.3804 | 112.8076
1653.8 | 1508.8 | 129.2844 | 113.7673
1654 | 1509 | 129.2844 | 113.8633
1654.2 | 1509.2 | 129.2844 | 113.9593
1654.4 | 1509.4 | 129.1885 | 113.9593
1654.6 | 1509.6 | 129.2844 | 113.9593
1654.8 | 1509.8 | 129.2844 | 113.9593
1655 | 1510 | 129.3804 | 113.9593
1655.2 | 1510.2 | 129.2844 | 113.8633
1655.4 | 1510.4 | 129.2844 | 113.7673
1655.6 | 1510.6 | 129.1885 | 113.6714
1655.8 | 1510.8 | 129.1885 | 113.7673
1656 | 1511 | 129.1885 | 113.8633
1656.2 | 1511.2 | 129.1885 | 113.8633
1656.4 | 1511.4 | 129.2844 | 113.8633
1656.6 | 1511.6 | 129.2844 | 113.8633
1656.8 | 1511.8 | 129.2844 | 113.9593
1657 | 1512 | 129.2844 | 113.9593
1657.2 | 1512.2 | 129.3804 | 113.8633
1657.4 | 1512.4 | 129.3804 | 113.8633
1657.6 | 1512.6 | 129.2844 | 113.8633
1657.8 | 1512.8 | 129.2844 | 113.8633
1658 | 1513 | 129.1885 | 113.6714
1658.2 | 1513.2 | 129.1885 | 113.6714
1658.4 | 1513.4 | 129.2844 | 113.7673
1658.6 | 1513.6 | 129.2844 | 113.8633
1658.8 | 1513.8 | 129.2844 | 113.8633
1659 | 1514 | 129.2844 | 113.8633
1659.2 | 1514.2 | 129.2844 | 113.6714
1659.4 | 1514.4 | 129.2844 | 113.7673
1659.6 | 1514.6 | 129.1885 | 113.7673
1659.8 | 1514.8 | 129.2844 | 113.6714
1660 | 1515 | 129.2844 | 114.0552
1660.2 | 1515.2 | 129.3804 | 113.9593
1660.4 | 1515.4 | 129.2844 | 113.7673
1660.6 | 1515.6 | 129.2844 | 113.7673
1660.8 | 1515.8 | 129.3804 | 113.7673
1661 | 1516 | 129.2844 | 113.6714
1661.2 | 1516.2 | 129.2844 | 113.7673
1661.4 | 1516.4 | 129.2844 | 113.6714
1661.6 | 1516.6 | 129.2844 | 113.4794
1661.8 | 1516.8 | 129.2844 | 113.3835
1662 | 1517 | 129.2844 | 113.1915
1662.2 | 1517.2 | 129.2844 | 113.1915
1662.4 | 1517.4 | 129.2844 | 113.2875
1662.6 | 1517.6 | 129.2844 | 113.5754
1662.8 | 1517.8 | 129.2844 | 113.6714
1663 | 1518 | 129.2844 | 113.4794
1663.2 | 1518.2 | 129.3804 | 113.6714
1663.4 | 1518.4 | 129.2844 | 113.5754
1663.6 | 1518.6 | 129.1885 | 113.6714
1663.8 | 1518.8 | 129.2844 | 113.4794
1664 | 1519 | 129.1885 | 112.9996
1664.2 | 1519.2 | 129.2844 | 112.9996
1664.4 | 1519.4 | 129.2844 | 112.9036
1664.6 | 1519.6 | 129.2844 | 112.9996
1664.8 | 1519.8 | 129.2844 | 112.9996
1665 | 1520 | 129.2844 | 113.2875
1665.2 | 1520.2 | 129.1885 | 113.4794
1665.4 | 1520.4 | 129.1885 | 113.3835
1665.6 | 1520.6 | 129.1885 | 113.3835
1665.8 | 1520.8 | 129.1885 | 113.5754
1666 | 1521 | 129.0925 | 113.4794
1666.2 | 1521.2 | 129.2844 | 113.3835
1666.4 | 1521.4 | 129.1885 | 113.1915
1666.6 | 1521.6 | 129.1885 | 113.1915
1666.8 | 1521.8 | 129.1885 | 113.0955
1667 | 1522 | 129.1885 | 113.0955
1667.2 | 1522.2 | 129.0925 | 113.0955
1667.4 | 1522.4 | 129.1885 | 113.3835
1667.6 | 1522.6 | 129.1885 | 113.0955
1667.8 | 1522.8 | 129.1885 | 113.0955
1668 | 1523 | 129.1885 | 113.0955
1668.2 | 1523.2 | 129.1885 | 112.9996
1668.4 | 1523.4 | 129.2844 | 113.0955
1668.6 | 1523.6 | 129.1885 | 112.9996
1668.8 | 1523.8 | 129.1885 | 112.9996
1669 | 1524 | 129.1885 | 113.0955
1669.2 | 1524.2 | 129.1885 | 112.9996
1669.4 | 1524.4 | 129.1885 | 112.9996
1669.6 | 1524.6 | 129.1885 | 112.8076
1669.8 | 1524.8 | 129.1885 | 113.0955
1670 | 1525 | 129.1885 | 112.9996
1670.2 | 1525.2 | 129.1885 | 113.0955
1670.4 | 1525.4 | 129.2844 | 113.0955
1670.6 | 1525.6 | 129.1885 | 112.9036
1670.8 | 1525.8 | 129.2844 | 112.7117
1671 | 1526 | 129.2844 | 112.5198
1671.2 | 1526.2 | 129.2844 | 113.0955
1671.4 | 1526.4 | 129.2844 | 112.8076
1671.6 | 1526.6 | 129.3804 | 112.5198
1671.8 | 1526.8 | 127.9409 | 111.4641
1672 | 1527 | 129.0925 | 115.7826
1672.2 | 1527.2 | 128.1329 | 116.7423
1672.4 | 1527.4 | 128.5167 | 115.3028
1672.6 | 1527.6 | 129.5724 | 115.0149
1672.8 | 1527.8 | 128.9966 | 114.535
1673 | 1528 | 130.2441 | 111.1762
1673.2 | 1528.2 | 129.2844 | 108.873
1673.4 | 1528.4 | 129.2844 | 111.1762
1673.6 | 1528.6 | 131.2038 | 114.9189
1673.8 | 1528.8 | 129.4764 | 115.1109
1674 | 1529 | 129.2844 | 107.8174
1674.2 | 1529.2 | 128.7087 | 113.3835
1674.4 | 1529.4 | 129.3804 | 114.823
1674.6 | 1529.6 | 128.6127 | 113.6714
1674.8 | 1529.8 | 129.3804 | 109.4488
1675 | 1530 | 129.8603 | 106.8577
1675.2 | 1530.2 | 129.3804 | 106.7617
1675.4 | 1530.4 | 129.0925 | 104.5545
1675.6 | 1530.6 | 129.6683 | 110.0246
1675.8 | 1530.8 | 129.7643 | 104.0746
1676 | 1531 | 128.7087 | 110.7924
1676.2 | 1531.2 | 129.0925 | 106.3779
1676.4 | 1531.4 | 128.7087 | 102.923
1676.6 | 1531.6 | 130.2441 | 102.4432
1676.8 | 1531.8 | 128.7087 | 102.8271
1677 | 1532 | 129.2844 | 110.2165
1677.2 | 1532.2 | 128.2288 | 110.5044
1677.4 | 1532.4 | 128.6127 | 104.6505
1677.6 | 1532.6 | 129.1885 | 100.8117
1677.8 | 1532.8 | 129.4764 | 99.3722
1678 | 1533 | 129.2844 | 99.6601
1678.2 | 1533.2 | 129.2844 | 99.6601
1678.4 | 1533.4 | 128.5167 | 99.9481
1678.6 | 1533.6 | 129.6683 | 99.0843
1678.8 | 1533.8 | 129.3804 | 98.0287
1679 | 1534 | 129.9562 | 98.7005
1679.2 | 1534.2 | 130.2441 | 93.9981
1679.4 | 1534.4 | 128.8046 | 108.6811
1679.6 | 1534.6 | 128.8046 | 109.3528
1679.8 | 1534.8 | 129.5724 | 111.3681
1680 | 1535 | 129.2844 | 113.2875
1680.2 | 1535.2 | 129.4764 | 110.6964
1680.4 | 1535.4 | 128.4208 | 112.8076
1680.6 | 1535.6 | 129.0925 | 109.2569
1680.8 | 1535.8 | 129.6683 | 108.6811
1681 | 1536 | 125.8296 | 109.9286
1681.2 | 1536.2 | 128.8046 | 112.6157
1681.4 | 1536.4 | 129.5724 | 112.8076
1681.6 | 1536.6 | 128.9006 | 102.923
1681.8 | 1536.8 | 128.8046 | 112.8076
1682 | 1537 | 129.4764 | 111.752
1682.2 | 1537.2 | 127.0772 | 111.9439
1682.4 | 1537.4 | 124.1982 | 112.9996
1682.6 | 1537.6 | 129.5724 | 113.4794
1682.8 | 1537.8 | 130.2441 | 106.8577
1683 | 1538 | 129.6683 | 110.7924
1683.2 | 1538.2 | 128.8046 | 108.3931
1683.4 | 1538.4 | 127.0772 | 111.3681
1683.6 | 1538.6 | 129.2844 | 112.4238
1683.8 | 1538.8 | 129.2844 | 107.9133
1684 | 1539 | 129.2844 | 110.7924
1684.2 | 1539.2 | 128.5167 | 109.9286
1684.4 | 1539.4 | 129.3804 | 109.6407
1684.6 | 1539.6 | 129.3804 | 111.5601
1684.8 | 1539.8 | 129.1885 | 111.656
1685 | 1540 | 129.1885 | 111.2722
1685.2 | 1540.2 | 129.2844 | 113.6714
1685.4 | 1540.4 | 128.6127 | 114.4391
1685.6 | 1540.6 | 129.3804 | 113.9593
1685.8 | 1540.8 | 128.9966 | 113.7673
1686 | 1541 | 129.1885 | 113.1915
1686.2 | 1541.2 | 128.3248 | 111.3681
1686.4 | 1541.4 | 129.7643 | 111.752
1686.6 | 1541.6 | 96.0798 | 92.9424
1686.8 | 1541.8 | 129.2844 | 110.9843
1687 | 1542 | 123.1425 | 98.5086
1687.2 | 1542.2 | 129.8603 | 101.2916
1687.4 | 1542.4 | 129.2844 | 100.9077
1687.6 | 1542.6 | 129.1885 | 106.3779
1687.8 | 1542.8 | 129.2844 | 98.9884
1688 | 1543 | 129.0925 | 94.286
1688.2 | 1543.2 | 128.8046 | 99.8521
1688.4 | 1543.4 | 129.0925 | 101.1956
1688.6 | 1543.6 | 127.1732 | 99.0843
1688.8 | 1543.8 | 128.9966 | 99.0843
1689 | 1544 | 129.2844 | 99.7561
1689.2 | 1544.2 | 129.6683 | 100.2359
1689.4 | 1544.4 | 129.2844 | 100.6198
1689.6 | 1544.6 | 129.1885 | 95.2457
1689.8 | 1544.8 | 125.1579 | 94.6698
1690 | 1545 | 128.9966 | 95.9174
1690.2 | 1545.2 | 129.5724 | 96.6852
1690.4 | 1545.4 | 129.6683 | 93.0384
1690.6 | 1545.6 | 128.9006 | 95.3416
1690.8 | 1545.8 | 129.7643 | 99.7561
1691 | 1546 | 126.9813 | 98.2206
1691.2 | 1546.2 | 129.1885 | 95.2457
1691.4 | 1546.4 | 129.0925 | 94.19
1691.6 | 1546.6 | 129.5724 | 94.7658
1691.8 | 1546.8 | 131.3957 | 93.9021
1692 | 1547 | 129.3804 | 93.6142
1692.2 | 1547.2 | 128.1329 | 93.3263
1692.4 | 1547.4 | 129.1885 | 96.0134
1692.6 | 1547.6 | 129.3804 | 95.3416
1692.8 | 1547.8 | 129.4764 | 93.6142
1693 | 1548 | 129.4764 | 95.5336
1693.2 | 1548.2 | 127.0772 | 92.6545
1693.4 | 1548.4 | 129.1885 | 92.7505
1693.6 | 1548.6 | 128.2288 | 93.6142
1693.8 | 1548.8 | 130.7239 | 87.6643
1694 | 1549 | 128.9966 | 94.3819
1694.2 | 1549.2 | 128.9966 | 97.2609
1694.4 | 1549.4 | 129.2844 | 97.069
1694.6 | 1549.6 | 129.2844 | 98.1247
1694.8 | 1549.8 | 128.9966 | 100.6198
1695 | 1550 | 129.1885 | 104.3625
1695.2 | 1550.2 | 129.3804 | 108.2012
1695.4 | 1550.4 | 129.1885 | 111.4641
1695.6 | 1550.6 | 129.1885 | 113.6714
1695.8 | 1550.8 | 129.0925 | 115.4947
1696 | 1551 | 129.1885 | 116.5504
1696.2 | 1551.2 | 129.0925 | 117.51
1696.4 | 1551.4 | 129.1885 | 117.7979
1696.6 | 1551.6 | 129.0925 | 118.4697
1696.8 | 1551.8 | 129.1885 | 118.6617
1697 | 1552 | 129.0925 | 118.4697
1697.2 | 1552.2 | 129.0925 | 118.7576
1697.4 | 1552.4 | 129.1885 | 118.7576
1697.6 | 1552.6 | 129.1885 | 118.7576
1697.8 | 1552.8 | 129.0925 | 118.9495
1698 | 1553 | 129.0925 | 118.9495
1698.2 | 1553.2 | 129.0925 | 119.1415
1698.4 | 1553.4 | 129.1885 | 119.4294
1698.6 | 1553.6 | 129.1885 | 119.5254
1698.8 | 1553.8 | 129.0925 | 119.6213
1699 | 1554 | 129.0925 | 119.5254
1699.2 | 1554.2 | 129.0925 | 119.5254
1699.4 | 1554.4 | 129.0925 | 119.5254
1699.6 | 1554.6 | 129.0925 | 119.5254
1699.8 | 1554.8 | 129.0925 | 119.8133
1700 | 1555 | 128.9966 | 119.6213
1700.2 | 1555.2 | 129.0925 | 119.9092
1700.4 | 1555.4 | 128.9966 | 119.9092
1700.6 | 1555.6 | 128.9966 | 119.7173
1700.8 | 1555.8 | 128.9966 | 119.7173
1701 | 1556 | 128.9966 | 119.5254
1701.2 | 1556.2 | 128.9966 | 119.5254
1701.4 | 1556.4 | 128.9966 | 119.6213
1701.6 | 1556.6 | 128.9006 | 119.5254
1701.8 | 1556.8 | 128.9966 | 119.5254
1702 | 1557 | 128.9006 | 119.3334
1702.2 | 1557.2 | 128.9966 | 119.3334
1702.4 | 1557.4 | 128.9006 | 119.2374
1702.6 | 1557.6 | 128.9006 | 119.2374
1702.8 | 1557.8 | 128.9006 | 119.2374
1703 | 1558 | 128.9006 | 119.2374
1703.2 | 1558.2 | 128.9006 | 118.9495
1703.4 | 1558.4 | 128.9006 | 119.0455
1703.6 | 1558.6 | 128.9006 | 118.8536
1703.8 | 1558.8 | 128.9006 | 118.4697
1704 | 1559 | 128.9006 | 118.8536
1704.2 | 1559.2 | 128.9006 | 119.0455
1704.4 | 1559.4 | 128.8046 | 118.8536
1704.6 | 1559.6 | 128.8046 | 118.7576
1704.8 | 1559.8 | 128.8046 | 118.8536
1705 | 1560 | 128.8046 | 119.0455
1705.2 | 1560.2 | 128.8046 | 118.8536
1705.4 | 1560.4 | 128.8046 | 118.9495
1705.6 | 1560.6 | 128.8046 | 119.0455
1705.8 | 1560.8 | 128.8046 | 119.1415
1706 | 1561 | 128.8046 | 118.8536
1706.2 | 1561.2 | 128.7087 | 118.6617
1706.4 | 1561.4 | 128.8046 | 118.4697
1706.6 | 1561.6 | 128.8046 | 118.8536
1706.8 | 1561.8 | 128.8046 | 118.9495
1707 | 1562 | 128.9006 | 118.8536
1707.2 | 1562.2 | 128.8046 | 118.8536
1707.4 | 1562.4 | 128.8046 | 119.1415
1707.6 | 1562.6 | 128.8046 | 119.4294
1707.8 | 1562.8 | 128.7087 | 119.2374
1708 | 1563 | 128.7087 | 118.9495
1708.2 | 1563.2 | 128.8046 | 119.0455
1708.4 | 1563.4 | 128.9006 | 119.3334
1708.6 | 1563.6 | 128.9006 | 119.3334
1708.8 | 1563.8 | 128.8046 | 119.3334
1709 | 1564 | 128.8046 | 119.2374
1709.2 | 1564.2 | 128.9006 | 119.0455
1709.4 | 1564.4 | 128.9966 | 119.2374
1709.6 | 1564.6 | 128.9966 | 119.1415
1709.8 | 1564.8 | 128.9966 | 119.0455
1710 | 1565 | 128.9006 | 118.8536
1710.2 | 1565.2 | 128.9006 | 118.9495
1710.4 | 1565.4 | 128.9006 | 118.8536
1710.6 | 1565.6 | 128.9006 | 118.7576
1710.8 | 1565.8 | 128.9966 | 119.0455
1711 | 1566 | 128.9966 | 118.9495
1711.2 | 1566.2 | 128.9006 | 118.9495
1711.4 | 1566.4 | 128.9006 | 118.7576
1711.6 | 1566.6 | 128.9006 | 118.7576
1711.8 | 1566.8 | 128.9966 | 118.6617
1712 | 1567 | 128.9006 | 118.6617
1712.2 | 1567.2 | 128.9966 | 118.6617
1712.4 | 1567.4 | 128.9966 | 118.8536
1712.6 | 1567.6 | 128.9966 | 118.3738
1712.8 | 1567.8 | 128.9966 | 118.7576
1713 | 1568 | 128.9966 | 118.9495
1713.2 | 1568.2 | 129.0925 | 118.8536
1713.4 | 1568.4 | 128.9966 | 118.7576
1713.6 | 1568.6 | 129.0925 | 119.1415
1713.8 | 1568.8 | 129.0925 | 118.4697
1714 | 1569 | 128.9966 | 118.3738
1714.2 | 1569.2 | 129.0925 | 117.9899
1714.4 | 1569.4 | 129.0925 | 117.4141
1714.6 | 1569.6 | 129.1885 | 117.51
1714.8 | 1569.8 | 129.1885 | 116.6463
1715 | 1570 | 129.1885 | 118.3738
1715.2 | 1570.2 | 129.1885 | 118.9495
1715.4 | 1570.4 | 129.1885 | 119.1415
1715.6 | 1570.6 | 129.1885 | 119.1415
1715.8 | 1570.8 | 129.1885 | 119.0455
1716 | 1571 | 129.0925 | 119.1415
1716.2 | 1571.2 | 129.1885 | 119.2374
1716.4 | 1571.4 | 129.1885 | 119.2374
1716.6 | 1571.6 | 129.1885 | 119.3334
1716.8 | 1571.8 | 129.1885 | 119.2374
1717 | 1572 | 129.2844 | 119.3334
1717.2 | 1572.2 | 129.1885 | 119.4294
1717.4 | 1572.4 | 129.2844 | 119.4294
1717.6 | 1572.6 | 129.2844 | 119.4294
1717.8 | 1572.8 | 129.1885 | 119.4294
1718 | 1573 | 129.1885 | 119.4294
1718.2 | 1573.2 | 129.2844 | 119.5254
1718.4 | 1573.4 | 129.3804 | 119.5254
1718.6 | 1573.6 | 129.3804 | 119.5254
1718.8 | 1573.8 | 129.2844 | 119.2374
1719 | 1574 | 129.3804 | 119.2374
1719.2 | 1574.2 | 129.3804 | 119.1415
1719.4 | 1574.4 | 129.2844 | 119.2374
1719.6 | 1574.6 | 129.3804 | 119.1415
1719.8 | 1574.8 | 129.3804 | 119.2374
1720 | 1575 | 129.5724 | 119.2374
1720.2 | 1575.2 | 129.4764 | 119.2374
1720.4 | 1575.4 | 129.4764 | 119.2374
1720.6 | 1575.6 | 129.5724 | 119.2374
1720.8 | 1575.8 | 129.4764 | 119.2374
1721 | 1576 | 129.5724 | 119.9092
1721.2 | 1576.2 | 129.5724 | 119.0455
1721.4 | 1576.4 | 129.6683 | 118.9495
1721.6 | 1576.6 | 129.6683 | 118.8536
1721.8 | 1576.8 | 129.6683 | 118.9495
1722 | 1577 | 129.6683 | 119.0455
1722.2 | 1577.2 | 129.6683 | 119.2374
1722.4 | 1577.4 | 129.6683 | 119.2374
1722.6 | 1577.6 | 129.6683 | 119.2374
1722.8 | 1577.8 | 129.5724 | 119.2374
1723 | 1578 | 129.6683 | 119.2374
1723.2 | 1578.2 | 129.5724 | 119.4294
1723.4 | 1578.4 | 129.5724 | 119.1415
1723.6 | 1578.6 | 129.5724 | 119.0455
1723.8 | 1578.8 | 129.5724 | 119.0455
1724 | 1579 | 129.5724 | 119.1415
1724.2 | 1579.2 | 129.6683 | 119.3334
1724.4 | 1579.4 | 129.6683 | 120.0052
1724.6 | 1579.6 | 129.6683 | 120.0052
1724.8 | 1579.8 | 129.6683 | 119.5254
1725 | 1580 | 129.5724 | 119.6213
1725.2 | 1580.2 | 129.5724 | 119.6213
1725.4 | 1580.4 | 129.7643 | 119.7173
1725.6 | 1580.6 | 129.6683 | 119.5254
1725.8 | 1580.8 | 129.6683 | 119.5254
1726 | 1581 | 129.6683 | 119.3334
1726.2 | 1581.2 | 129.6683 | 119.5254
1726.4 | 1581.4 | 129.7643 | 119.1415
1726.6 | 1581.6 | 129.6683 | 118.9495
1726.8 | 1581.8 | 129.7643 | 118.9495
1727 | 1582 | 129.7643 | 119.0455
1727.2 | 1582.2 | 129.7643 | 118.9495
1727.4 | 1582.4 | 129.7643 | 119.1415
1727.6 | 1582.6 | 129.7643 | 118.9495
1727.8 | 1582.8 | 129.8603 | 119.1415
1728 | 1583 | 129.5724 | 119.2374
1728.2 | 1583.2 | 129.7643 | 119.0455
1728.4 | 1583.4 | 129.8603 | 118.8536
1728.6 | 1583.6 | 129.7643 | 119.5254
1728.8 | 1583.8 | 129.8603 | 119.0455
1729 | 1584 | 129.7643 | 119.2374
1729.2 | 1584.2 | 129.7643 | 119.4294
1729.4 | 1584.4 | 129.7643 | 119.1415
1729.6 | 1584.6 | 129.7643 | 119.5254
1729.8 | 1584.8 | 129.7643 | 119.2374
1730 | 1585 | 129.7643 | 118.9495
1730.2 | 1585.2 | 129.8603 | 119.0455
1730.4 | 1585.4 | 130.0522 | 118.7576
1730.6 | 1585.6 | 129.8603 | 119.1415
1730.8 | 1585.8 | 129.7643 | 119.0455
1731 | 1586 | 129.8603 | 119.0455
1731.2 | 1586.2 | 129.8603 | 119.2374
1731.4 | 1586.4 | 129.8603 | 119.2374
1731.6 | 1586.6 | 129.8603 | 119.6213
1731.8 | 1586.8 | 129.8603 | 119.2374
1732 | 1587 | 129.8603 | 119.0455
1732.2 | 1587.2 | 129.9562 | 119.0455
1732.4 | 1587.4 | 129.8603 | 119.4294
1732.6 | 1587.6 | 129.9562 | 119.7173
1732.8 | 1587.8 | 129.8603 | 119.8133
1733 | 1588 | 129.8603 | 119.9092
1733.2 | 1588.2 | 129.9562 | 120.1971
1733.4 | 1588.4 | 129.8603 | 120.2931
1733.6 | 1588.6 | 129.8603 | 120.3891
1733.8 | 1588.8 | 129.8603 | 120.485
1734 | 1589 | 129.8603 | 120.581
1734.2 | 1589.2 | 129.9562 | 120.581
1734.4 | 1589.4 | 129.8603 | 120.7729
1734.6 | 1589.6 | 129.9562 | 120.485
1734.8 | 1589.8 | 129.8603 | 120.1971
1735 | 1590 | 129.8603 | 120.1012
1735.2 | 1590.2 | 129.8603 | 120.2931
1735.4 | 1590.4 | 129.8603 | 120.3891
1735.6 | 1590.6 | 129.9562 | 120.2931
1735.8 | 1590.8 | 129.8603 | 120.1971
1736 | 1591 | 129.8603 | 120.1012
1736.2 | 1591.2 | 129.8603 | 120.0052
1736.4 | 1591.4 | 129.7643 | 120.0052
1736.6 | 1591.6 | 129.8603 | 120.1012
1736.8 | 1591.8 | 129.7643 | 119.9092
1737 | 1592 | 129.8603 | 120.0052
1737.2 | 1592.2 | 129.8603 | 120.3891
1737.4 | 1592.4 | 129.8603 | 119.5254
1737.6 | 1592.6 | 129.8603 | 115.2068
1737.8 | 1592.8 | 129.7643 | 107.9133
1738 | 1593 | 129.5724 | 107.6254
1738.2 | 1593.2 | 128.9966 | 98.7964
1738.4 | 1593.4 | 129.4764 | 94.8618
1738.6 | 1593.6 | 128.9006 | 101.4835
1738.8 | 1593.8 | 129.5724 | 107.6254
1739 | 1594 | 128.9966 | 104.4585
1739.2 | 1594.2 | 128.9006 | 107.2416
1739.4 | 1594.4 | 124.2942 | 89.5836
1739.6 | 1594.6 | 128.9966 | 92.6545
1739.8 | 1594.8 | 129.1885 | 89.5836
1740 | 1595 | 128.9966 | 89.9674
1740.2 | 1595.2 | 129.0925 | 88.432
1740.4 | 1595.4 | 129.3804 | 89.1038
1740.6 | 1595.6 | 128.9966 | 88.6239
1740.8 | 1595.8 | 128.8046 | 88.336
1741 | 1596 | 128.6127 | 88.9118
1741.2 | 1596.2 | 129.8603 | 88.5279
1741.4 | 1596.4 | 129.3804 | 86.2247
1741.6 | 1596.6 | 129.0925 | 86.8005
1741.8 | 1596.8 | 129.0925 | 85.9368
1742 | 1597 | 129.0925 | 82.9619
1742.2 | 1597.2 | 129.1885 | 83.3457
1742.4 | 1597.4 | 127.1732 | 82.0022
1742.6 | 1597.6 | 129.8603 | 85.0731
1742.8 | 1597.8 | 128.7087 | 84.9771
1743 | 1598 | 127.8449 | 83.2497
1743.2 | 1598.2 | 129.7643 | 104.5545
1743.4 | 1598.4 | 129.3804 | 93.9021
1743.6 | 1598.6 | 129.7643 | 86.8965
1743.8 | 1598.8 | 129.4764 | 86.5126
1744 | 1599 | 129.3804 | 86.1288
1744.2 | 1599.2 | 128.9966 | 81.8102
1744.4 | 1599.4 | 129.4764 | 82.674
1744.6 | 1599.6 | 131.3957 | 83.7296
1744.8 | 1599.8 | 128.1329 | 82.674
1745 | 1600 | 129.0925 | 80.8506
1745.2 | 1600.2 | 129.9562 | 87.6643
1745.4 | 1600.4 | 129.7643 | 89.1997
1745.6 | 1600.6 | 129.2844 | 84.2094
1745.8 | 1600.8 | 129.6683 | 80.0828
1746 | 1601 | 131.0119 | 80.1788
1746.2 | 1601.2 | 129.6683 | 76.9159
1746.4 | 1601.4 | 129.0925 | 79.9869
1746.6 | 1601.6 | 130.2441 | 80.7546
1746.8 | 1601.8 | 129.9562 | 75.5723
1747 | 1602 | 130.0522 | 78.1635
1747.2 | 1602.2 | 129.3804 | 77.8756
1747.4 | 1602.4 | 129.4764 | 75.6683
1747.6 | 1602.6 | 128.5167 | 82.7699
1747.8 | 1602.8 | 125.8296 | 87.7602
1748 | 1603 | 127.1732 | 84.8812
1748.2 | 1603.2 | 129.0925 | 80.1788
1748.4 | 1603.4 | 125.6377 | 78.2595
1748.6 | 1603.6 | 129.4764 | 74.9006
1748.8 | 1603.8 | 129.3804 | 74.1328
1749 | 1604 | 129.6683 | 77.7796
1749.2 | 1604.2 | 128.9966 | 82.0981
1749.4 | 1604.4 | 125.6377 | 51.2927
1749.6 | 1604.6 | 123.5264 | 38.1451
1749.8 | 1604.8 | 125.6377 | 34.0186
1750 | 1605 | 125.6377 | 34.0186
1750.2 | 1605.2 | 127.1732 | 26.2452
1750.4 | 1605.4 | 127.8449 | 22.0227
1750.6 | 1605.6 | 127.653 | 22.8863
1750.8 | 1605.8 | 127.1732 | 26.3412
1751 | 1606 | 124.1982 | 41.0242
1751.2 | 1606.2 | 127.0772 | 27.4928
1751.4 | 1606.4 | 127.0772 | 23.2702
1751.6 | 1606.6 | 126.9813 | 24.2299
1751.8 | 1606.8 | 126.7893 | 23.0783
1752 | 1607 | 128.1329 | 20.1993
1752.2 | 1607.2 | 127.8449 | 20.4872
1752.4 | 1607.4 | 127.653 | 16.0727
1752.6 | 1607.6 | 128.5167 | 15.9767
1752.8 | 1607.8 | 128.1329 | 15.017
1753 | 1608 | 128.2288 | 18.088
1753.2 | 1608.2 | 128.5167 | 14.1533
1753.4 | 1608.4 | 128.9966 | 13.0977
1753.6 | 1608.6 | 128.3248 | 12.9058
1753.8 | 1608.8 | 128.4208 | 14.7291
1754 | 1609 | 128.4208 | 16.6485
1754.2 | 1609.2 | 128.3248 | 18.5678
1754.4 | 1609.4 | 127.749 | 20.6791
1754.6 | 1609.6 | 127.749 | 21.8307
1754.8 | 1609.8 | 127.9409 | 17.7041
1755 | 1610 | 127.653 | 17.6082
1755.2 | 1610.2 | 127.749 | 17.4162
1755.4 | 1610.4 | 127.1732 | 20.5832
1755.6 | 1610.6 | 127.8449 | 19.9114
1755.8 | 1610.8 | 128.3248 | 17.1283
1756 | 1611 | 128.9006 | 15.113
1756.2 | 1611.2 | 128.5167 | 14.5372
1756.4 | 1611.4 | 128.4208 | 14.8251
1756.6 | 1611.6 | 128.2288 | 10.9864
1756.8 | 1611.8 | 128.6127 | 11.7541
1757 | 1612 | 128.1329 | 13.0977
1757.2 | 1612.2 | 129.8603 | 7.2437
1757.4 | 1612.4 | 128.7087 | 7.3397
1757.6 | 1612.6 | 128.5167 | 8.9711
1757.8 | 1612.8 | 128.5167 | 10.3146
1758 | 1613 | 128.4208 | 8.1074
1758.2 | 1613.2 | 129.3804 | 7.5316
1758.4 | 1613.4 | 129.1885 | 5.4203
1758.6 | 1613.6 | 130.9159 | 7.1477
1758.8 | 1613.8 | 127.1732 | 6.1881
1759 | 1614 | 129.1885 | 4.7486
1759.2 | 1614.2 | 128.9006 | 7.0518
1759.4 | 1614.4 | 129.3804 | 4.6526
1759.6 | 1614.6 | 129.0925 | 3.7889
1759.8 | 1614.8 | 129.0925 | 4.6526
1760 | 1615 | 130.1482 | 5.3244
1760.2 | 1615.2 | 128.9966 | 9.259
1760.4 | 1615.4 | 126.8853 | 6.8598
1760.6 | 1615.6 | 126.6933 | 6.6679
1760.8 | 1615.8 | 126.4054 | 6.9558
1761 | 1616 | 129.0925 | 5.9002
1761.2 | 1616.2 | 128.5167 | 4.5566
1761.4 | 1616.4 | 130.9159 | 3.597
1761.6 | 1616.6 | 128.3248 | 6.1881
1761.8 | 1616.8 | 129.0925 | 4.6526
1762 | 1617 | 129.6683 | 4.8445
1762.2 | 1617.2 | 129.8603 | 5.2284
1762.4 | 1617.4 | 130.532 | 4.0768
1762.6 | 1617.6 | 129.6683 | 3.1171
1762.8 | 1617.8 | 128.7087 | 3.0211
1763 | 1618 | 130.0522 | 5.1324
1763.2 | 1618.2 | 128.4208 | 18.3759
1763.4 | 1618.4 | 127.3651 | 6.6679
1763.6 | 1618.6 | 129.4764 | 3.6929
1763.8 | 1618.8 | 129.9562 | 3.597
1764 | 1619 | 127.653 | 4.1727
1764.2 | 1619.2 | 132.5473 | 3.405
1764.4 | 1619.4 | 129.6683 | 6.7639
1764.6 | 1619.6 | 130.532 | 3.0211
1764.8 | 1619.8 | 129.0925 | 3.1171
1765 | 1620 | 129.0925 | 5.9002
1765.2 | 1620.2 | 128.0369 | 3.6929
1765.4 | 1620.4 | 128.5167 | 4.4606
1765.6 | 1620.6 | 128.4208 | 5.6122
1765.8 | 1620.8 | 130.8199 | 4.0768
1766 | 1621 | 129.7643 | 4.0768
1766.2 | 1621.2 | 131.3957 | 3.1171
1766.4 | 1621.4 | 128.1329 | 4.6526
1766.6 | 1621.6 | 129.7643 | 2.9252
1766.8 | 1621.8 | 129.6683 | 4.1727
1767 | 1622 | 130.9159 | 8.6832
1767.2 | 1622.2 | 129.8603 | 3.9808
1767.4 | 1622.4 | 129.3804 | 3.501
1767.6 | 1622.6 | 129.0925 | 5.9002
1767.8 | 1622.8 | 131.4917 | 3.405
1768 | 1623 | 128.9006 | 3.2131
1768.2 | 1623.2 | 129.2844 | 2.7332
1768.4 | 1623.4 | 128.5167 | 7.4356
1768.6 | 1623.6 | 128.3248 | 10.7945
1768.8 | 1623.8 | 128.0369 | 10.0268
1769 | 1624 | 128.5167 | 10.3146
1769.2 | 1624.2 | 126.8853 | 8.5872
1769.4 | 1624.4 | 138.1135 | 9.0671
1769.6 | 1624.6 | 128.8046 | 6.1881
1769.8 | 1624.8 | 128.8046 | 4.9405
1770 | 1625 | 129.4764 | 5.0365
1770.2 | 1625.2 | 131.9716 | 3.597
1770.4 | 1625.4 | 128.9006 | 3.501
1770.6 | 1625.6 | 128.3248 | 4.8445
1770.8 | 1625.8 | 127.1732 | 6.6679
1771 | 1626 | 130.8199 | 3.7889
1771.2 | 1626.2 | 129.1885 | 4.3647
1771.4 | 1626.4 | 130.3401 | 2.7332
1771.6 | 1626.6 | 129.6683 | 2.9252
1771.8 | 1626.8 | 130.2441 | 3.6929
1772 | 1627 | 125.1579 | 6.38
1772.2 | 1627.2 | 128.7087 | 3.2131
1772.4 | 1627.4 | 130.9159 | 3.6929
1772.6 | 1627.6 | 129.8603 | 3.2131
1772.8 | 1627.8 | 128.9006 | 3.2131
1773 | 1628 | 129.3804 | 3.2131
1773.2 | 1628.2 | 134.6586 | 5.9002
1773.4 | 1628.4 | 128.4208 | 4.6526
1773.6 | 1628.6 | 129.3804 | 5.7082
1773.8 | 1628.8 | 131.4917 | 6.284
1774 | 1629 | 131.5877 | 2.3494
1774.2 | 1629.2 | 129.8603 | 3.597
1774.4 | 1629.4 | 127.8449 | 17.992
1774.6 | 1629.6 | 127.749 | 3.2131
1774.8 | 1629.8 | 129.3804 | 3.0211
1775 | 1630 | 132.4514 | 3.1171
1775.2 | 1630.2 | 127.4611 | 5.0365
1775.4 | 1630.4 | 128.0369 | 8.4913
1775.6 | 1630.6 | 126.5974 | 13.0018
1775.8 | 1630.8 | 129.5724 | 4.4606
1776 | 1631 | 127.8449 | 4.6526
1776.2 | 1631.2 | 127.4611 | 5.0365
1776.4 | 1631.4 | 130.4361 | 2.3494
1776.6 | 1631.6 | 128.6127 | 3.405
1776.8 | 1631.8 | 132.5473 | 3.597
1777 | 1632 | 130.0522 | 3.501
1777.2 | 1632.2 | 128.5167 | 2.9252
1777.4 | 1632.4 | 127.3651 | 5.1324
1777.6 | 1632.6 | 131.5877 | 3.0211
1777.8 | 1632.8 | 131.3957 | 3.501
1778 | 1633 | 129.6683 | 3.3091
1778.2 | 1633.2 | 129.1885 | 3.501
1778.4 | 1633.4 | 130.628 | 1.8695
1778.6 | 1633.6 | 129.3804 | 2.3494
1778.8 | 1633.8 | 129.1885 | 3.3091
1779 | 1634 | 129.3804 | 3.405
1779.2 | 1634.2 | 131.0119 | 1.9655
1779.4 | 1634.4 | 129.2844 | 3.0211
1779.6 | 1634.6 | 129.7643 | 2.7332
1779.8 | 1634.8 | 129.0925 | 2.5413
1780 | 1635 | 129.2844 | 2.8292
1780.2 | 1635.2 | 129.2844 | 2.7332
1780.4 | 1635.4 | 129.2844 | 2.1574
1780.6 | 1635.6 | 129.1885 | 2.6373
1780.8 | 1635.8 | 129.2844 | 2.4453
1781 | 1636 | 127.653 | 4.5566
1781.2 | 1636.2 | 127.9409 | 3.501
1781.4 | 1636.4 | 128.9966 | 3.405
1781.6 | 1636.6 | 128.5167 | 3.0211
1781.8 | 1636.8 | 128.2288 | 3.501
1782 | 1637 | 128.5167 | 2.9252
1782.2 | 1637.2 | 129.0925 | 3.597
1782.4 | 1637.4 | 128.9966 | 3.9808
1782.6 | 1637.6 | 129.5724 | 3.597
1782.8 | 1637.8 | 128.9966 | 3.7889
1783 | 1638 | 128.9966 | 3.597
1783.2 | 1638.2 | 129.0925 | 3.2131
1783.4 | 1638.4 | 128.9966 | 3.9808
1783.6 | 1638.6 | 128.9966 | 2.9252
1783.8 | 1638.8 | 128.9966 | 4.2687
1784 | 1639 | 128.9966 | 3.7889
1784.2 | 1639.2 | 128.9966 | 4.4606
1784.4 | 1639.4 | 129.0925 | 3.9808
1784.6 | 1639.6 | 128.8046 | 4.7486
1784.8 | 1639.8 | 128.9966 | 4.1727
1785 | 1640 | 128.8046 | 4.0768
1785.2 | 1640.2 | 129.0925 | 5.4203
1785.4 | 1640.4 | 129.0925 | 4.4606
1785.6 | 1640.6 | 129.9562 | 3.3091
1785.8 | 1640.8 | 129.2844 | 2.3494
1786 | 1641 | 127.4611 | 2.2534
1786.2 | 1641.2 | 128.7087 | 2.1574
1786.4 | 1641.4 | 129.3804 | 1.6776
1786.6 | 1641.6 | 129.3804 | 1.3897
1786.8 | 1641.8 | 129.2844 | 1.1978
1787 | 1642 | 129.1885 | 1.2937
1787.2 | 1642.2 | 129.1885 | 1.2937
1787.4 | 1642.4 | 128.2288 | 1.4857
1787.6 | 1642.6 | 129.3804 | 1.2937
1787.8 | 1642.8 | 128.9966 | 1.0058
1788 | 1643 | 128.9966 | 1.7736
1788.2 | 1643.2 | 129.1885 | 2.0615
1788.4 | 1643.4 | 129.2844 | 1.4857
1788.6 | 1643.6 | 129.5724 | 1.0058
1788.8 | 1643.8 | 129.3804 | 1.2937
1789 | 1644 | 129.0925 | 1.0058
1789.2 | 1644.2 | 129.2844 | 1.3897
1789.4 | 1644.4 | 130.4361 | 0.8139
1789.6 | 1644.6 | 129.3804 | 3.405
1789.8 | 1644.8 | 129.3804 | 2.3494
1790 | 1645 | 129.2844 | 1.4857
1790.2 | 1645.2 | 129.3804 | 1.2937
1790.4 | 1645.4 | 129.2844 | 0.8139
1790.6 | 1645.6 | 128.4208 | 1.7736
1790.8 | 1645.8 | 129.7643 | 1.8695
1791 | 1646 | 128.4208 | 17.7041
1791.2 | 1646.2 | 129.1885 | 4.8445
1791.4 | 1646.4 | 129.1885 | 3.0211
1791.6 | 1646.6 | 129.2844 | 1.6776
1791.8 | 1646.8 | 129.5724 | 1.3897
1792 | 1647 | 129.2844 | 1.1018
1792.2 | 1647.2 | 129.3804 | 1.1978
1792.4 | 1647.4 | 129.3804 | 1.1978
1792.6 | 1647.6 | 128.9966 | 1.5816
1792.8 | 1647.8 | 129.7643 | 1.2937
1793 | 1648 | 130.7239 | 1.1978
1793.2 | 1648.2 | 129.2844 | 1.1978
1793.4 | 1648.4 | 128.2288 | 2.5413
1793.6 | 1648.6 | 128.8046 | 5.6122
1793.8 | 1648.8 | 128.3248 | 3.7889
1794 | 1649 | 128.9966 | 1.8695
1794.2 | 1649.2 | 129.1885 | 1.6776
1794.4 | 1649.4 | 129.2844 | 1.2937
1794.6 | 1649.6 | 129.2844 | 1.1018
1794.8 | 1649.8 | 129.3804 | 1.0058
1795 | 1650 | 129.2844 | 1.1018
1795.2 | 1650.2 | 129.3804 | 1.1018
1795.4 | 1650.4 | 129.2844 | 1.1018
1795.6 | 1650.6 | 129.2844 | 1.1978
1795.8 | 1650.8 | 129.3804 | 1.1978
1796 | 1651 | 129.4764 | 1.9655
1796.2 | 1651.2 | 128.4208 | 2.6373
1796.4 | 1651.4 | 128.7087 | 1.6776
1796.6 | 1651.6 | 134.9465 | 2.0615
1796.8 | 1651.8 | 129.3804 | 1.4857
1797 | 1652 | 127.4611 | 3.501
1797.2 | 1652.2 | 128.5167 | 3.405
1797.4 | 1652.4 | 129.2844 | 1.8695
1797.6 | 1652.6 | 129.3804 | 1.1978
1797.8 | 1652.8 | 129.3804 | 1.1018
1798 | 1653 | 129.3804 | 1.0058
1798.2 | 1653.2 | 129.2844 | 1.0058
1798.4 | 1653.4 | 129.2844 | 1.0058
1798.6 | 1653.6 | 129.3804 | 1.0058
1798.8 | 1653.8 | 129.2844 | 0.90985
1799 | 1654 | 129.3804 | 0.90985
1799.2 | 1654.2 | 129.3804 | 1.0058
1799.4 | 1654.4 | 129.3804 | 1.0058
1799.6 | 1654.6 | 129.3804 | 0.90985
1799.8 | 1654.8 | 129.5724 | 0.90985
1800 | 1655 | 129.4764 | 0.90985
1800.2 | 1655.2 | 129.4764 | 1.1018
1800.4 | 1655.4 | 129.5724 | 1.1018
1800.6 | 1655.6 | 129.6683 | 1.1018
1800.8 | 1655.8 | 129.4764 | 1.0058
1801 | 1656 | 129.2844 | 0.90985
1801.2 | 1656.2 | 129.2844 | 1.2937
1801.4 | 1656.4 | 129.3804 | 1.4857
1801.6 | 1656.6 | 129.3804 | 1.1978
1801.8 | 1656.8 | 129.3804 | 1.1018
1802 | 1657 | 129.2844 | 1.0058
1802.2 | 1657.2 | 129.3804 | 1.1978
1802.4 | 1657.4 | 129.3804 | 1.1978
1802.6 | 1657.6 | 129.2844 | 1.1018
1802.8 | 1657.8 | 129.2844 | 1.1978
1803 | 1658 | 129.3804 | 1.0058
1803.2 | 1658.2 | 129.3804 | 1.2937
1803.4 | 1658.4 | 129.3804 | 1.1978
1803.6 | 1658.6 | 129.2844 | 1.1018
1803.8 | 1658.8 | 128.9006 | 1.0058
1804 | 1659 | 129.2844 | 1.0058
1804.2 | 1659.2 | 129.2844 | 1.0058
1804.4 | 1659.4 | 128.7087 | 1.4857
1804.6 | 1659.6 | 129.0925 | 1.1978
1804.8 | 1659.8 | 129.3804 | 1.2937
1805 | 1660 | 129.3804 | 1.1978
1805.2 | 1660.2 | 129.4764 | 1.0058
1805.4 | 1660.4 | 129.3804 | 1.0058
1805.6 | 1660.6 | 129.5724 | 1.2937
1805.8 | 1660.8 | 129.2844 | 1.2937
1806 | 1661 | 128.9006 | 1.5816
1806.2 | 1661.2 | 129.3804 | 1.1978
1806.4 | 1661.4 | 128.9006 | 5.0365
1806.6 | 1661.6 | 129.6683 | 3.9808
1806.8 | 1661.8 | 129.8603 | 2.0615
1807 | 1662 | 129.3804 | 2.1574
1807.2 | 1662.2 | 129.2844 | 1.4857
1807.4 | 1662.4 | 129.6683 | 2.0615
1807.6 | 1662.6 | 128.5167 | 1.8695
1807.8 | 1662.8 | 128.0369 | 2.0615
1808 | 1663 | 127.8449 | 2.7332
1808.2 | 1663.2 | 131.2998 | 1.7736
1808.4 | 1663.4 | 129.6683 | 1.7736
1808.6 | 1663.6 | 129.3804 | 1.3897
1808.8 | 1663.8 | 129.3804 | 1.4857
1809 | 1664 | 129.0925 | 1.1978
1809.2 | 1664.2 | 129.9562 | 2.6373
1809.4 | 1664.4 | 128.7087 | 1.5816
1809.6 | 1664.6 | 129.1885 | 1.4857
1809.8 | 1664.8 | 129.3804 | 1.5816
1810 | 1665 | 128.7087 | 1.4857
1810.2 | 1665.2 | 129.3804 | 1.1978
1810.4 | 1665.4 | 129.9562 | 0.90985
1810.6 | 1665.6 | 129.3804 | 2.2534
1810.8 | 1665.8 | 129.4764 | 1.5816
1811 | 1666 | 130.3401 | 1.2937
1811.2 | 1666.2 | 129.1885 | 1.3897
1811.4 | 1666.4 | 128.9966 | 1.3897
1811.6 | 1666.6 | 129.1885 | 1.2937
1811.8 | 1666.8 | 129.7643 | 1.3897
1812 | 1667 | 129.2844 | 1.3897
1812.2 | 1667.2 | 128.9966 | 0.8139
1812.4 | 1667.4 | 129.9562 | 3.3091
1812.6 | 1667.6 | 126.2135 | 7.3397
1812.8 | 1667.8 | 128.8046 | 5.8042
1813 | 1668 | 128.4208 | 7.3397
1813.2 | 1668.2 | 129.2844 | 3.1171
1813.4 | 1668.4 | 129.1885 | 1.8695
1813.6 | 1668.6 | 129.3804 | 1.7736
1813.8 | 1668.8 | 129.1885 | 1.4857
1814 | 1669 | 129.1885 | 1.2937
1814.2 | 1669.2 | 129.0925 | 1.1978
1814.4 | 1669.4 | 129.2844 | 1.1978
1814.6 | 1669.6 | 129.2844 | 1.1018
1814.8 | 1669.8 | 129.1885 | 1.1978
1815 | 1670 | 129.1885 | 1.1018
1815.2 | 1670.2 | 129.3804 | 1.1018
1815.4 | 1670.4 | 129.1885 | 1.1018
1815.6 | 1670.6 | 129.2844 | 1.3897
1815.8 | 1670.8 | 129.2844 | 1.1978
1816 | 1671 | 129.0925 | 1.1978
1816.2 | 1671.2 | 129.1885 | 1.1018
1816.4 | 1671.4 | 129.3804 | 1.1978
1816.6 | 1671.6 | 129.4764 | 1.0058
1816.8 | 1671.8 | 129.2844 | 1.3897
1817 | 1672 | 129.1885 | 0.8139
1817.2 | 1672.2 | 129.3804 | 1.3897
1817.4 | 1672.4 | 129.6683 | 1.5816
1817.6 | 1672.6 | 128.5167 | 1.8695
1817.8 | 1672.8 | 128.1329 | 1.5816
1818 | 1673 | 129.2844 | 1.4857
1818.2 | 1673.2 | 128.7087 | 1.7736
1818.4 | 1673.4 | 129.2844 | 2.4453
1818.6 | 1673.6 | 129.7643 | 4.0768
1818.8 | 1673.8 | 130.628 | 5.6122
1819 | 1674 | 130.532 | 0.90985
1819.2 | 1674.2 | 126.5014 | 9.451
1819.4 | 1674.4 | 129.2844 | 3.7889
1819.6 | 1674.6 | 128.9966 | 2.7332
1819.8 | 1674.8 | 130.532 | 3.8848
1820 | 1675 | 129.7643 | 1.8695
1820.2 | 1675.2 | 129.9562 | 2.2534
1820.4 | 1675.4 | 129.7643 | 1.2937
1820.6 | 1675.6 | 128.1329 | 2.6373
1820.8 | 1675.8 | 129.8603 | 1.4857
1821 | 1676 | 126.7893 | 3.597
1821.2 | 1676.2 | 128.1329 | 2.4453
1821.4 | 1676.4 | 128.8046 | 1.5816
1821.6 | 1676.6 | 127.2692 | 2.6373
1821.8 | 1676.8 | 122.0869 | 1.8695
1822 | 1677 | 128.7087 | 2.9252
1822.2 | 1677.2 | 128.9966 | 2.2534
1822.4 | 1677.4 | 129.7643 | 2.1574
1822.6 | 1677.6 | 129.2844 | 1.8695
1822.8 | 1677.8 | 128.7087 | 1.7736
1823 | 1678 | 129.6683 | 1.2937
1823.2 | 1678.2 | 128.4208 | 1.4857
1823.4 | 1678.4 | 129.2844 | 1.3897
1823.6 | 1678.6 | 126.5014 | 2.5413
1823.8 | 1678.8 | 129.1885 | 1.2937
1824 | 1679 | 129.2844 | 1.1018
1824.2 | 1679.2 | 129.0925 | 2.6373
1824.4 | 1679.4 | 128.9966 | 1.6776
1824.6 | 1679.6 | 128.5167 | 1.4857
1824.8 | 1679.8 | 126.3095 | 2.5413
1825 | 1680 | 129.1885 | 1.3897
1825.2 | 1680.2 | 129.2844 | 1.2937
1825.4 | 1680.4 | 129.6683 | 1.4857
1825.6 | 1680.6 | 129.2844 | 1.7736
1825.8 | 1680.8 | 129.2844 | 1.4857
1826 | 1681 | 129.2844 | 1.4857
1826.2 | 1681.2 | 129.2844 | 1.5816
1826.4 | 1681.4 | 129.2844 | 1.3897
1826.6 | 1681.6 | 128.7087 | 2.4453
1826.8 | 1681.8 | 129.2844 | 1.5816
1827 | 1682 | 127.653 | 2.5413
1827.2 | 1682.2 | 131.2998 | 1.7736
1827.4 | 1682.4 | 129.1885 | 1.4857
1827.6 | 1682.6 | 129.0925 | 2.6373
1827.8 | 1682.8 | 128.5167 | 3.501
1828 | 1683 | 129.6683 | 2.1574
1828.2 | 1683.2 | 127.1732 | 2.4453
1828.4 | 1683.4 | 129.3804 | 1.6776
1828.6 | 1683.6 | 129.3804 | 1.3897
1828.8 | 1683.8 | 129.3804 | 1.1978
1829 | 1684 | 129.3804 | 1.4857
1829.2 | 1684.2 | 129.3804 | 1.2937
1829.4 | 1684.4 | 129.3804 | 1.1978
1829.6 | 1684.6 | 129.3804 | 1.1018
1829.8 | 1684.8 | 129.3804 | 1.1018
1830 | 1685 | 129.1885 | 1.6776
1830.2 | 1685.2 | 129.2844 | 1.3897
1830.4 | 1685.4 | 129.2844 | 2.1574
1830.6 | 1685.6 | 129.3804 | 1.5816
1830.8 | 1685.8 | 129.1885 | 1.7736
1831 | 1686 | 129.3804 | 1.3897
1831.2 | 1686.2 | 129.3804 | 1.2937
1831.4 | 1686.4 | 129.2844 | 1.1018
1831.6 | 1686.6 | 129.3804 | 1.1018
1831.8 | 1686.8 | 129.3804 | 1.1018
1832 | 1687 | 129.2844 | 1.1978
1832.2 | 1687.2 | 129.5724 | 1.1018
1832.4 | 1687.4 | 129.2844 | 1.1018
1832.6 | 1687.6 | 129.4764 | 1.1978
1832.8 | 1687.8 | 129.4764 | 1.3897
1833 | 1688 | 129.4764 | 1.2937
1833.2 | 1688.2 | 129.4764 | 1.3897
1833.4 | 1688.4 | 129.4764 | 1.2937
1833.6 | 1688.6 | 129.5724 | 1.1978
1833.8 | 1688.8 | 129.5724 | 1.1978
1834 | 1689 | 129.3804 | 1.1018
1834.2 | 1689.2 | 129.4764 | 1.1978
1834.4 | 1689.4 | 129.5724 | 1.1978
1834.6 | 1689.6 | 129.5724 | 1.1018
1834.8 | 1689.8 | 129.5724 | 1.1018
1835 | 1690 | 129.4764 | 1.3897
1835.2 | 1690.2 | 129.4764 | 1.3897
1835.4 | 1690.4 | 129.6683 | 1.1978
1835.6 | 1690.6 | 129.4764 | 1.2937
1835.8 | 1690.8 | 129.4764 | 1.4857
1836 | 1691 | 129.4764 | 1.3897
1836.2 | 1691.2 | 129.4764 | 1.5816
1836.4 | 1691.4 | 129.5724 | 1.6776
1836.6 | 1691.6 | 129.4764 | 1.3897
1836.8 | 1691.8 | 129.5724 | 1.2937
1837 | 1692 | 129.5724 | 1.9655
1837.2 | 1692.2 | 129.5724 | 1.5816
1837.4 | 1692.4 | 129.6683 | 1.2937
1837.6 | 1692.6 | 129.6683 | 1.2937
1837.8 | 1692.8 | 129.6683 | 1.2937
1838 | 1693 | 129.8603 | 1.2937
1838.2 | 1693.2 | 130.3401 | 1.1978
1838.4 | 1693.4 | 130.0522 | 1.8695
1838.6 | 1693.6 | 129.6683 | 1.6776
1838.8 | 1693.8 | 129.0925 | 2.3494
1839 | 1694 | 129.6683 | 2.5413
1839.2 | 1694.2 | 129.9562 | 3.3091
1839.4 | 1694.4 | 129.4764 | 2.0615
1839.6 | 1694.6 | 130.0522 | 1.6776
1839.8 | 1694.8 | 129.8603 | 1.5816
1840 | 1695 | 129.8603 | 1.4857
1840.2 | 1695.2 | 129.7643 | 1.4857
1840.4 | 1695.4 | 129.9562 | 1.5816
1840.6 | 1695.6 | 129.6683 | 1.8695
1840.8 | 1695.8 | 129.6683 | 1.5816
1841 | 1696 | 129.8603 | 1.8695
1841.2 | 1696.2 | 129.8603 | 1.7736
1841.4 | 1696.4 | 129.9562 | 1.4857
1841.6 | 1696.6 | 129.9562 | 1.4857
1841.8 | 1696.8 | 129.8603 | 1.4857
1842 | 1697 | 129.9562 | 1.3897
1842.2 | 1697.2 | 129.7643 | 5.2284
1842.4 | 1697.4 | 129.8603 | 3.8848
1842.6 | 1697.6 | 129.8603 | 2.2534
1842.8 | 1697.8 | 129.8603 | 2.8292
1843 | 1698 | 130.1482 | 2.0615
1843.2 | 1698.2 | 130.2441 | 1.3897
1843.4 | 1698.4 | 130.2441 | 1.7736
1843.6 | 1698.6 | 130.2441 | 1.7736
1843.8 | 1698.8 | 131.2038 | 1.9655
1844 | 1699 | 130.2441 | 1.4857
1844.2 | 1699.2 | 129.8603 | 2.5413
1844.4 | 1699.4 | 129.9562 | 1.9655
1844.6 | 1699.6 | 129.8603 | 1.4857
1844.8 | 1699.8 | 129.8603 | 1.7736
1845 | 1700 | 129.8603 | 1.5816
1845.2 | 1700.2 | 129.8603 | 1.5816
1845.4 | 1700.4 | 129.7643 | 1.7736
1845.6 | 1700.6 | 129.7643 | 2.2534
1845.8 | 1700.8 | 129.0925 | 5.1324
1846 | 1701 | 129.6683 | 3.8848
1846.2 | 1701.2 | 129.7643 | 1.8695
1846.4 | 1701.4 | 129.7643 | 1.4857
1846.6 | 1701.6 | 129.7643 | 1.2937
1846.8 | 1701.8 | 129.8603 | 1.3897
1847 | 1702 | 129.7643 | 1.4857
1847.2 | 1702.2 | 129.7643 | 1.4857
1847.4 | 1702.4 | 129.8603 | 1.4857
1847.6 | 1702.6 | 129.7643 | 1.4857
1847.8 | 1702.8 | 129.7643 | 1.2937
1848 | 1703 | 129.6683 | 1.2937
1848.2 | 1703.2 | 129.7643 | 1.2937
1848.4 | 1703.4 | 129.7643 | 1.2937
1848.6 | 1703.6 | 129.7643 | 1.3897
1848.8 | 1703.8 | 129.7643 | 1.2937
1849 | 1704 | 129.6683 | 1.2937
1849.2 | 1704.2 | 129.6683 | 1.2937
1849.4 | 1704.4 | 129.6683 | 1.1978
1849.6 | 1704.6 | 129.7643 | 1.1978
1849.8 | 1704.8 | 129.7643 | 1.3897
1850 | 1705 | 129.6683 | 1.4857
1850.2 | 1705.2 | 129.6683 | 1.2937
1850.4 | 1705.4 | 129.6683 | 1.2937
1850.6 | 1705.6 | 129.7643 | 1.0058
1850.8 | 1705.8 | 129.6683 | 1.3897
1851 | 1706 | 129.6683 | 1.3897
1851.2 | 1706.2 | 129.6683 | 1.2937
1851.4 | 1706.4 | 129.6683 | 1.3897
1851.6 | 1706.6 | 129.6683 | 1.2937
1851.8 | 1706.8 | 129.6683 | 1.7736
1852 | 1707 | 129.5724 | 1.7736
1852.2 | 1707.2 | 129.6683 | 1.4857
1852.4 | 1707.4 | 129.5724 | 1.4857
1852.6 | 1707.6 | 129.6683 | 1.3897
1852.8 | 1707.8 | 129.5724 | 1.2937
1853 | 1708 | 129.5724 | 1.1978
1853.2 | 1708.2 | 129.5724 | 1.2937
1853.4 | 1708.4 | 129.5724 | 1.1978
1853.6 | 1708.6 | 129.5724 | 1.4857
1853.8 | 1708.8 | 129.5724 | 1.6776
1854 | 1709 | 129.5724 | 1.3897
1854.2 | 1709.2 | 129.6683 | 1.3897
1854.4 | 1709.4 | 129.5724 | 1.2937
1854.6 | 1709.6 | 129.5724 | 1.4857
1854.8 | 1709.8 | 129.5724 | 1.4857
1855 | 1710 | 129.6683 | 2.1574
1855.2 | 1710.2 | 129.6683 | 1.6776
1855.4 | 1710.4 | 129.5724 | 2.0615
1855.6 | 1710.6 | 129.6683 | 2.2534
1855.8 | 1710.8 | 129.6683 | 2.0615
1856 | 1711 | 129.6683 | 1.5816
1856.2 | 1711.2 | 129.5724 | 1.4857
1856.4 | 1711.4 | 129.5724 | 1.5816
1856.6 | 1711.6 | 129.4764 | 2.1574
1856.8 | 1711.8 | 131.2998 | 2.6373
1857 | 1712 | 129.3804 | 2.1574
1857.2 | 1712.2 | 129.5724 | 1.7736
1857.4 | 1712.4 | 129.4764 | 3.2131
1857.6 | 1712.6 | 129.4764 | 2.5413
1857.8 | 1712.8 | 128.2288 | 2.3494
1858 | 1713 | 128.2288 | 2.5413
1858.2 | 1713.2 | 130.4361 | 2.5413
1858.4 | 1713.4 | 129.5724 | 3.3091
1858.6 | 1713.6 | 130.0522 | 1.5816
1858.8 | 1713.8 | 129.4764 | 3.7889
1859 | 1714 | 130.2441 | 2.3494
1859.2 | 1714.2 | 129.6683 | 2.1574
1859.4 | 1714.4 | 129.5724 | 2.1574
1859.6 | 1714.6 | 129.6683 | 1.6776
1859.8 | 1714.8 | 129.5724 | 1.3897
1860 | 1715 | 129.5724 | 1.3897
1860.2 | 1715.2 | 129.5724 | 1.3897
1860.4 | 1715.4 | 129.5724 | 1.3897
1860.6 | 1715.6 | 129.3804 | 1.5816
1860.8 | 1715.8 | 129.5724 | 1.6776
1861 | 1716 | 129.8603 | 1.4857
1861.2 | 1716.2 | 129.2844 | 1.7736
1861.4 | 1716.4 | 129.6683 | 1.5816
1861.6 | 1716.6 | 129.5724 | 1.7736
1861.8 | 1716.8 | 129.5724 | 1.5816
1862 | 1717 | 129.4764 | 1.2937
1862.2 | 1717.2 | 129.3804 | 1.5816
1862.4 | 1717.4 | 129.5724 | 2.1574
1862.6 | 1717.6 | 129.3804 | 1.8695
1862.8 | 1717.8 | 128.8046 | 2.8292
1863 | 1718 | 130.0522 | 3.1171
1863.2 | 1718.2 | 131.1078 | 2.0615
1863.4 | 1718.4 | 129.4764 | 3.0211
1863.6 | 1718.6 | 129.4764 | 2.0615
1863.8 | 1718.8 | 130.532 | 1.0058
1864 | 1719 | 129.4764 | 1.3897
1864.2 | 1719.2 | 129.4764 | 1.3897
1864.4 | 1719.4 | 129.5724 | 1.3897
1864.6 | 1719.6 | 129.4764 | 1.3897
1864.8 | 1719.8 | 129.5724 | 1.3897
1865 | 1720 | 129.5724 | 1.2937
1865.2 | 1720.2 | 128.4208 | 1.6776
1865.4 | 1720.4 | 129.4764 | 1.5816
1865.6 | 1720.6 | 129.5724 | 1.5816
1865.8 | 1720.8 | 129.4764 | 1.5816
1866 | 1721 | 129.5724 | 1.3897
1866.2 | 1721.2 | 129.5724 | 1.3897
1866.4 | 1721.4 | 129.5724 | 1.4857
1866.6 | 1721.6 | 129.3804 | 1.2937
1866.8 | 1721.8 | 129.5724 | 1.3897
1867 | 1722 | 129.4764 | 1.2937
1867.2 | 1722.2 | 129.5724 | 1.3897
1867.4 | 1722.4 | 129.5724 | 1.3897
1867.6 | 1722.6 | 129.5724 | 1.3897
1867.8 | 1722.8 | 129.4764 | 1.2937
1868 | 1723 | 129.4764 | 1.3897
1868.2 | 1723.2 | 129.4764 | 1.3897
1868.4 | 1723.4 | 129.6683 | 1.5816
1868.6 | 1723.6 | 129.7643 | 2.1574
1868.8 | 1723.8 | 129.3804 | 2.4453
1869 | 1724 | 128.9966 | 3.0211
1869.2 | 1724.2 | 129.5724 | 2.0615
1869.4 | 1724.4 | 129.4764 | 2.0615
1869.6 | 1724.6 | 129.5724 | 1.6776
1869.8 | 1724.8 | 129.5724 | 1.3897
1870 | 1725 | 129.3804 | 1.3897
1870.2 | 1725.2 | 129.5724 | 1.3897
1870.4 | 1725.4 | 129.2844 | 4.0768
1870.6 | 1725.6 | 127.4611 | 1.5816
1870.8 | 1725.8 | 129.4764 | 1.9655
1871 | 1726 | 129.5724 | 1.6776
1871.2 | 1726.2 | 129.4764 | 1.4857
1871.4 | 1726.4 | 130.628 | 9.451
1871.6 | 1726.6 | 129.4764 | 1.3897
1871.8 | 1726.8 | 129.3804 | 1.4857
1872 | 1727 | 129.4764 | 1.7736
1872.2 | 1727.2 | 129.4764 | 1.4857
1872.4 | 1727.4 | 129.4764 | 1.4857
1872.6 | 1727.6 | 129.3804 | 1.3897
1872.8 | 1727.8 | 129.4764 | 1.2937
1873 | 1728 | 129.5724 | 1.3897
1873.2 | 1728.2 | 129.4764 | 1.4857
1873.4 | 1728.4 | 129.4764 | 1.5816
1873.6 | 1728.6 | 129.3804 | 1.4857
1873.8 | 1728.8 | 129.7643 | 1.3897
1874 | 1729 | 129.5724 | 1.3897
1874.2 | 1729.2 | 129.4764 | 1.3897
1874.4 | 1729.4 | 129.4764 | 1.4857
1874.6 | 1729.6 | 129.4764 | 1.5816
1874.8 | 1729.8 | 129.8603 | 1.9655
1875 | 1730 | 129.5724 | 1.4857
1875.2 | 1730.2 | 129.3804 | 1.5816
1875.4 | 1730.4 | 129.5724 | 1.4857
1875.6 | 1730.6 | 129.4764 | 1.3897
1875.8 | 1730.8 | 129.4764 | 1.3897
1876 | 1731 | 129.4764 | 1.4857
1876.2 | 1731.2 | 129.6683 | 1.5816
1876.4 | 1731.4 | 129.3804 | 1.5816
1876.6 | 1731.6 | 129.3804 | 1.2937
1876.8 | 1731.8 | 129.3804 | 1.6776
1877 | 1732 | 129.4764 | 1.4857
1877.2 | 1732.2 | 130.532 | 1.2937
1877.4 | 1732.4 | 129.4764 | 1.9655
1877.6 | 1732.6 | 129.1885 | 1.5816
1877.8 | 1732.8 | 130.7239 | 2.1574
1878 | 1733 | 129.2844 | 1.6776
1878.2 | 1733.2 | 129.3804 | 1.6776
1878.4 | 1733.4 | 128.9006 | 6.9558
1878.6 | 1733.6 | 129.4764 | 2.5413
1878.8 | 1733.8 | 129.5724 | 1.7736
1879 | 1734 | 129.6683 | 1.5816
1879.2 | 1734.2 | 129.3804 | 1.4857
1879.4 | 1734.4 | 129.4764 | 1.5816
1879.6 | 1734.6 | 129.4764 | 1.5816
1879.8 | 1734.8 | 129.4764 | 1.3897
1880 | 1735 | 128.6127 | 1.3897
1880.2 | 1735.2 | 129.5724 | 1.4857
1880.4 | 1735.4 | 129.3804 | 1.6776
1880.6 | 1735.6 | 129.4764 | 1.6776
1880.8 | 1735.8 | 130.0522 | 1.7736
1881 | 1736 | 129.3804 | 1.5816
1881.2 | 1736.2 | 129.4764 | 1.4857
1881.4 | 1736.4 | 129.4764 | 1.4857
1881.6 | 1736.6 | 129.4764 | 1.4857
1881.8 | 1736.8 | 129.6683 | 1.5816
1882 | 1737 | 129.1885 | 1.8695
1882.2 | 1737.2 | 129.3804 | 1.9655
1882.4 | 1737.4 | 129.7643 | 2.1574
1882.6 | 1737.6 | 130.9159 | 5.7082
1882.8 | 1737.8 | 129.3804 | 4.3647
1883 | 1738 | 129.6683 | 3.597
1883.2 | 1738.2 | 129.6683 | 3.0211
1883.4 | 1738.4 | 130.8199 | 3.7889
1883.6 | 1738.6 | 129.4764 | 2.6373
1883.8 | 1738.8 | 129.5724 | 1.9655
1884 | 1739 | 129.4764 | 1.7736
1884.2 | 1739.2 | 129.6683 | 1.5816
1884.4 | 1739.4 | 129.6683 | 1.4857
1884.6 | 1739.6 | 129.6683 | 1.5816
1884.8 | 1739.8 | 129.4764 | 1.5816
1885 | 1740 | 129.5724 | 1.5816
1885.2 | 1740.2 | 129.4764 | 1.4857
1885.4 | 1740.4 | 129.6683 | 1.4857
1885.6 | 1740.6 | 129.5724 | 1.6776
1885.8 | 1740.8 | 129.4764 | 1.5816
1886 | 1741 | 130.2441 | 2.6373
1886.2 | 1741.2 | 129.3804 | 1.6776
1886.4 | 1741.4 | 129.5724 | 1.5816
1886.6 | 1741.6 | 129.6683 | 1.7736
1886.8 | 1741.8 | 129.5724 | 1.7736
1887 | 1742 | 129.5724 | 1.7736
1887.2 | 1742.2 | 129.4764 | 1.5816
1887.4 | 1742.4 | 129.4764 | 1.7736
1887.6 | 1742.6 | 129.4764 | 1.6776
1887.8 | 1742.8 | 129.5724 | 1.5816
1888 | 1743 | 129.3804 | 1.7736
1888.2 | 1743.2 | 127.749 | 1.1978
1888.4 | 1743.4 | 129.4764 | 2.1574
1888.6 | 1743.6 | 129.2844 | 2.2534
1888.8 | 1743.8 | 129.8603 | 2.5413
1889 | 1744 | 129.4764 | 2.1574
1889.2 | 1744.2 | 129.2844 | 1.8695
1889.4 | 1744.4 | 129.6683 | 1.7736
1889.6 | 1744.6 | 129.5724 | 1.9655
1889.8 | 1744.8 | 129.6683 | 1.6776
1890 | 1745 | 129.4764 | 1.5816
1890.2 | 1745.2 | 129.4764 | 1.7736
1890.4 | 1745.4 | 129.4764 | 1.6776
1890.6 | 1745.6 | 129.4764 | 1.6776
1890.8 | 1745.8 | 129.6683 | 1.6776
1891 | 1746 | 129.6683 | 1.7736
1891.2 | 1746.2 | 129.6683 | 1.6776
1891.4 | 1746.4 | 129.7643 | 1.6776
1891.6 | 1746.6 | 129.4764 | 3.2131
1891.8 | 1746.8 | 129.4764 | 2.1574
1892 | 1747 | 129.4764 | 1.8695
1892.2 | 1747.2 | 129.6683 | 1.8695
1892.4 | 1747.4 | 129.5724 | 1.7736
1892.6 | 1747.6 | 129.4764 | 1.8695
1892.8 | 1747.8 | 129.5724 | 1.7736
1893 | 1748 | 129.5724 | 1.7736
1893.2 | 1748.2 | 129.1885 | 5.2284
1893.4 | 1748.4 | 129.1885 | 3.2131
1893.6 | 1748.6 | 129.5724 | 2.0615
1893.8 | 1748.8 | 129.5724 | 1.8695
1894 | 1749 | 129.5724 | 1.7736
1894.2 | 1749.2 | 129.6683 | 1.6776
1894.4 | 1749.4 | 129.6683 | 1.6776
1894.6 | 1749.6 | 129.5724 | 1.7736
1894.8 | 1749.8 | 129.5724 | 1.7736
1895 | 1750 | 129.5724 | 2.0615
1895.2 | 1750.2 | 129.5724 | 1.9655
1895.4 | 1750.4 | 129.6683 | 1.8695
1895.6 | 1750.6 | 129.6683 | 1.6776
1895.8 | 1750.8 | 129.6683 | 1.9655
1896 | 1751 | 129.5724 | 2.1574
1896.2 | 1751.2 | 129.5724 | 1.9655
1896.4 | 1751.4 | 129.5724 | 1.9655
1896.6 | 1751.6 | 129.6683 | 1.8695
1896.8 | 1751.8 | 129.7643 | 1.8695
1897 | 1752 | 129.6683 | 1.8695
1897.2 | 1752.2 | 129.6683 | 2.0615
1897.4 | 1752.4 | 129.5724 | 2.0615
1897.6 | 1752.6 | 129.6683 | 1.8695
1897.8 | 1752.8 | 129.6683 | 1.8695
1898 | 1753 | 129.5724 | 1.7736
1898.2 | 1753.2 | 129.6683 | 1.5816
1898.4 | 1753.4 | 129.5724 | 1.2937
1898.6 | 1753.6 | 129.7643 | 1.9655
1898.8 | 1753.8 | 129.6683 | 1.7736
1899 | 1754 | 129.6683 | 1.7736
1899.2 | 1754.2 | 129.8603 | 1.6776
1899.4 | 1754.4 | 129.6683 | 1.7736
1899.6 | 1754.6 | 129.6683 | 1.7736
1899.8 | 1754.8 | 129.6683 | 1.8695
1900 | 1755 | 129.4764 | 2.0615
1900.2 | 1755.2 | 129.6683 | 2.0615
1900.4 | 1755.4 | 129.6683 | 2.0615
1900.6 | 1755.6 | 129.6683 | 1.9655
1900.8 | 1755.8 | 129.6683 | 1.8695
1901 | 1756 | 129.6683 | 1.8695
1901.2 | 1756.2 | 129.6683 | 1.8695
1901.4 | 1756.4 | 129.5724 | 2.0615
1901.6 | 1756.6 | 129.6683 | 2.1574
1901.8 | 1756.8 | 129.6683 | 1.9655
1902 | 1757 | 129.6683 | 1.7736
1902.2 | 1757.2 | 129.6683 | 1.6776
1902.4 | 1757.4 | 129.6683 | 1.7736
1902.6 | 1757.6 | 129.6683 | 1.8695
1902.8 | 1757.8 | 129.6683 | 1.7736
1903 | 1758 | 129.7643 | 2.0615
1903.2 | 1758.2 | 129.6683 | 1.9655
1903.4 | 1758.4 | 129.4764 | 1.8695
1903.6 | 1758.6 | 129.7643 | 1.7736
1903.8 | 1758.8 | 129.5724 | 1.9655
1904 | 1759 | 129.7643 | 2.2534
1904.2 | 1759.2 | 129.7643 | 2.9252
1904.4 | 1759.4 | 129.5724 | 3.3091
1904.6 | 1759.6 | 129.6683 | 2.5413
1904.8 | 1759.8 | 129.5724 | 2.0615
1905 | 1760 | 129.6683 | 1.9655
1905.2 | 1760.2 | 129.6683 | 1.8695
1905.4 | 1760.4 | 129.7643 | 1.8695
1905.6 | 1760.6 | 129.6683 | 1.9655
1905.8 | 1760.8 | 129.6683 | 1.6776
1906 | 1761 | 129.6683 | 1.5816
1906.2 | 1761.2 | 129.6683 | 1.8695
1906.4 | 1761.4 | 129.7643 | 1.9655
1906.6 | 1761.6 | 129.6683 | 1.5816
1906.8 | 1761.8 | 129.6683 | 2.0615
1907 | 1762 | 129.6683 | 2.0615
1907.2 | 1762.2 | 129.6683 | 2.1574
1907.4 | 1762.4 | 129.6683 | 1.8695
1907.6 | 1762.6 | 129.6683 | 1.6776
1907.8 | 1762.8 | 129.6683 | 1.5816
1908 | 1763 | 129.5724 | 1.7736
1908.2 | 1763.2 | 129.6683 | 1.6776
1908.4 | 1763.4 | 129.6683 | 1.5816
1908.6 | 1763.6 | 129.6683 | 1.7736
1908.8 | 1763.8 | 129.6683 | 1.7736
1909 | 1764 | 129.6683 | 1.6776
1909.2 | 1764.2 | 129.5724 | 1.9655
1909.4 | 1764.4 | 129.8603 | 1.9655
1909.6 | 1764.6 | 129.5724 | 2.5413
1909.8 | 1764.8 | 129.7643 | 2.0615
1910 | 1765 | 129.5724 | 1.6776
1910.2 | 1765.2 | 129.6683 | 1.6776
1910.4 | 1765.4 | 129.6683 | 1.5816
1910.6 | 1765.6 | 129.0925 | 2.1574
1910.8 | 1765.8 | 129.6683 | 2.3494
1911 | 1766 | 130.1482 | 2.8292
1911.2 | 1766.2 | 129.6683 | 2.1574
1911.4 | 1766.4 | 129.6683 | 1.8695
1911.6 | 1766.6 | 129.6683 | 1.8695
1911.8 | 1766.8 | 129.6683 | 1.7736
1912 | 1767 | 129.5724 | 1.7736
1912.2 | 1767.2 | 128.6127 | 13.3856
1912.4 | 1767.4 | 129.3804 | 3.405
1912.6 | 1767.6 | 129.6683 | 2.3494
1912.8 | 1767.8 | 130.4361 | 1.9655
1913 | 1768 | 129.2844 | 2.2534
1913.2 | 1768.2 | 129.0925 | 1.8695
1913.4 | 1768.4 | 128.8046 | 2.6373
1913.6 | 1768.6 | 129.6683 | 1.9655
1913.8 | 1768.8 | 129.6683 | 1.8695
1914 | 1769 | 129.5724 | 1.8695
1914.2 | 1769.2 | 129.6683 | 1.8695
1914.4 | 1769.4 | 129.5724 | 1.6776
1914.6 | 1769.6 | 129.1885 | 1.6776
1914.8 | 1769.8 | 129.4764 | 2.8292
1915 | 1770 | 129.6683 | 2.3494
1915.2 | 1770.2 | 129.5724 | 1.8695
1915.4 | 1770.4 | 129.3804 | 2.1574
1915.6 | 1770.6 | 129.4764 | 1.8695
1915.8 | 1770.8 | 129.5724 | 1.3897
1916 | 1771 | 129.7643 | 1.7736
1916.2 | 1771.2 | 129.6683 | 1.7736
1916.4 | 1771.4 | 129.3804 | 1.6776
1916.6 | 1771.6 | 129.5724 | 1.7736
1916.8 | 1771.8 | 129.6683 | 1.6776
1917 | 1772 | 129.6683 | 1.6776
1917.2 | 1772.2 | 129.6683 | 1.6776
1917.4 | 1772.4 | 129.5724 | 1.6776
1917.6 | 1772.6 | 129.6683 | 1.5816
1917.8 | 1772.8 | 129.1885 | 1.7736
1918 | 1773 | 129.5724 | 1.6776
1918.2 | 1773.2 | 129.7643 | 1.6776
1918.4 | 1773.4 | 129.7643 | 2.3494
1918.6 | 1773.6 | 129.6683 | 1.8695
1918.8 | 1773.8 | 127.557 | 1.5816
1919 | 1774 | 129.5724 | 2.0615
1919.2 | 1774.2 | 129.3804 | 2.0615
1919.4 | 1774.4 | 129.5724 | 1.9655
1919.6 | 1774.6 | 129.5724 | 1.7736
1919.8 | 1774.8 | 129.5724 | 1.6776
1920 | 1775 | 129.5724 | 1.8695
1920.2 | 1775.2 | 129.3804 | 1.9655
1920.4 | 1775.4 | 129.6683 | 1.8695
1920.6 | 1775.6 | 129.6683 | 1.7736
1920.8 | 1775.8 | 130.1482 | 1.6776
1921 | 1776 | 128.9966 | 2.1574
1921.2 | 1776.2 | 130.2441 | 1.1018
1921.4 | 1776.4 | 129.6683 | 1.8695
1921.6 | 1776.6 | 129.1885 | 1.8695
1921.8 | 1776.8 | 129.5724 | 1.7736
1922 | 1777 | 129.4764 | 1.5816
1922.2 | 1777.2 | 129.5724 | 2.1574
1922.4 | 1777.4 | 129.5724 | 2.9252
1922.6 | 1777.6 | 129.6683 | 1.7736
1922.8 | 1777.8 | 129.1885 | 2.1574
1923 | 1778 | 129.4764 | 3.3091
1923.2 | 1778.2 | 129.6683 | 2.2534
1923.4 | 1778.4 | 129.5724 | 1.8695
1923.6 | 1778.6 | 129.5724 | 1.8695
1923.8 | 1778.8 | 129.5724 | 1.8695
1924 | 1779 | 129.4764 | 1.7736
1924.2 | 1779.2 | 129.5724 | 1.6776
1924.4 | 1779.4 | 129.4764 | 1.8695
1924.6 | 1779.6 | 129.4764 | 1.6776
1924.8 | 1779.8 | 129.5724 | 1.7736
1925 | 1780 | 129.4764 | 1.7736
1925.2 | 1780.2 | 129.5724 | 1.7736
1925.4 | 1780.4 | 129.4764 | 1.7736
1925.6 | 1780.6 | 129.5724 | 1.6776
1925.8 | 1780.8 | 129.5724 | 1.7736
1926 | 1781 | 129.3804 | 1.8695
1926.2 | 1781.2 | 129.4764 | 2.0615
1926.4 | 1781.4 | 129.4764 | 1.8695
1926.6 | 1781.6 | 129.5724 | 1.8695
1926.8 | 1781.8 | 129.5724 | 1.6776
1927 | 1782 | 129.5724 | 1.7736
1927.2 | 1782.2 | 129.5724 | 1.7736
1927.4 | 1782.4 | 129.4764 | 1.7736
1927.6 | 1782.6 | 129.5724 | 1.7736
1927.8 | 1782.8 | 129.5724 | 1.8695
1928 | 1783 | 129.4764 | 1.8695
1928.2 | 1783.2 | 128.9006 | 1.9655
1928.4 | 1783.4 | 129.5724 | 2.1574
1928.6 | 1783.6 | 129.5724 | 1.9655
1928.8 | 1783.8 | 129.5724 | 1.7736
1929 | 1784 | 129.5724 | 1.8695
1929.2 | 1784.2 | 129.4764 | 1.8695
1929.4 | 1784.4 | 129.5724 | 1.7736
1929.6 | 1784.6 | 129.4764 | 1.7736
1929.8 | 1784.8 | 129.5724 | 1.8695
1930 | 1785 | 129.6683 | 1.8695
1930.2 | 1785.2 | 129.5724 | 1.7736
1930.4 | 1785.4 | 129.6683 | 1.6776
1930.6 | 1785.6 | 129.5724 | 1.7736
1930.8 | 1785.8 | 129.8603 | 1.9655
1931 | 1786 | 129.6683 | 1.8695
1931.2 | 1786.2 | 129.9562 | 1.7736
1931.4 | 1786.4 | 129.8603 | 1.9655
1931.6 | 1786.6 | 129.7643 | 1.8695
1931.8 | 1786.8 | 129.8603 | 1.9655
1932 | 1787 | 129.4764 | 1.7736
1932.2 | 1787.2 | 129.5724 | 2.2534
1932.4 | 1787.4 | 129.5724 | 1.8695
1932.6 | 1787.6 | 129.5724 | 1.8695
1932.8 | 1787.8 | 129.5724 | 1.8695
1933 | 1788 | 129.6683 | 1.7736
1933.2 | 1788.2 | 129.6683 | 1.7736
1933.4 | 1788.4 | 129.5724 | 1.7736
1933.6 | 1788.6 | 129.5724 | 1.6776
1933.8 | 1788.8 | 129.5724 | 1.7736
1934 | 1789 | 129.7643 | 1.7736
1934.2 | 1789.2 | 129.5724 | 1.7736
1934.4 | 1789.4 | 129.5724 | 1.7736
1934.6 | 1789.6 | 129.4764 | 1.8695
1934.8 | 1789.8 | 129.5724 | 1.8695
1935 | 1790 | 130.1482 | 2.1574
1935.2 | 1790.2 | 130.2441 | 2.1574
1935.4 | 1790.4 | 130.0522 | 1.9655
1935.6 | 1790.6 | 130.0522 | 1.9655
1935.8 | 1790.8 | 130.0522 | 2.0615
1936 | 1791 | 130.2441 | 2.3494
1936.2 | 1791.2 | 129.9562 | 2.0615
1936.4 | 1791.4 | 129.7643 | 2.0615
1936.6 | 1791.6 | 130.0522 | 2.0615
1936.8 | 1791.8 | 130.532 | 1.5816
1937 | 1792 | 130.1482 | 2.3494
1937.2 | 1792.2 | 130.0522 | 2.1574
1937.4 | 1792.4 | 129.9562 | 2.2534
1937.6 | 1792.6 | 130.0522 | 8.2034
1937.8 | 1792.8 | 130.1482 | 6.7639
1938 | 1793 | 129.6683 | 2.2534
1938.2 | 1793.2 | 130.0522 | 2.3494
1938.4 | 1793.4 | 130.1482 | 2.5413
1938.6 | 1793.6 | 130.2441 | 2.2534
1938.8 | 1793.8 | 130.1482 | 2.2534
1939 | 1794 | 130.0522 | 2.1574
1939.2 | 1794.2 | 130.0522 | 2.0615
1939.4 | 1794.4 | 129.5724 | 2.0615
1939.6 | 1794.6 | 129.0925 | 2.0615
1939.8 | 1794.8 | 129.7643 | 2.0615
1940 | 1795 | 129.3804 | 2.1574
1940.2 | 1795.2 | 129.6683 | 1.7736
1940.4 | 1795.4 | 129.5724 | 2.2534
1940.6 | 1795.6 | 129.7643 | 1.9655
1940.8 | 1795.8 | 129.8603 | 1.5816
1941 | 1796 | 129.3804 | 1.9655
1941.2 | 1796.2 | 129.5724 | 1.5816
1941.4 | 1796.4 | 129.0925 | 1.9655
1941.6 | 1796.6 | 129.4764 | 1.9655
1941.8 | 1796.8 | 129.8603 | 2.2534
1942 | 1797 | 130.2441 | 1.8695
1942.2 | 1797.2 | 130.1482 | 1.8695
1942.4 | 1797.4 | 129.8603 | 1.8695
1942.6 | 1797.6 | 130.2441 | 1.6776
1942.8 | 1797.8 | 129.4764 | 1.3897
1943 | 1798 | 128.9966 | 2.4453
1943.2 | 1798.2 | 129.9562 | 1.5816
1943.4 | 1798.4 | 129.7643 | 2.4453
1943.6 | 1798.6 | 129.7643 | 1.8695
1943.8 | 1798.8 | 129.7643 | 1.8695
1944 | 1799 | 129.7643 | 1.8695
1944.2 | 1799.2 | 129.5724 | 1.5816
1944.4 | 1799.4 | 129.6683 | 1.8695
1944.6 | 1799.6 | 130.3401 | 2.0615
1944.8 | 1799.8 | 129.6683 | 2.3494
1945 | 1800 | 129.5724 | 2.2534
1945.2 | 1800.2 | 129.6683 | 2.0615
1945.4 | 1800.4 | 129.9562 | 1.8695
1945.6 | 1800.6 | 129.6683 | 2.0615
1945.8 | 1800.8 | 129.6683 | 2.0615
1946 | 1801 | 129.0925 | 2.0615
1946.2 | 1801.2 | 128.8046 | 5.8042
1946.4 | 1801.4 | 129.8603 | 2.7332
1946.6 | 1801.6 | 129.7643 | 2.6373
1946.8 | 1801.8 | 129.7643 | 2.2534
1947 | 1802 | 129.6683 | 2.0615
1947.2 | 1802.2 | 129.7643 | 1.9655
1947.4 | 1802.4 | 129.6683 | 1.9655
1947.6 | 1802.6 | 129.6683 | 2.0615
1947.8 | 1802.8 | 129.6683 | 1.9655
1948 | 1803 | 129.6683 | 2.0615
1948.2 | 1803.2 | 129.5724 | 2.0615
1948.4 | 1803.4 | 129.7643 | 1.9655
1948.6 | 1803.6 | 129.7643 | 1.9655
1948.8 | 1803.8 | 129.8603 | 1.9655
1949 | 1804 | 129.6683 | 1.8695
1949.2 | 1804.2 | 129.7643 | 1.8695
1949.4 | 1804.4 | 129.5724 | 1.9655
1949.6 | 1804.6 | 129.6683 | 1.8695
1949.8 | 1804.8 | 129.7643 | 1.7736
1950 | 1805 | 129.5724 | 1.9655
1950.2 | 1805.2 | 129.3804 | 1.9655
1950.4 | 1805.4 | 129.2844 | 1.8695
1950.6 | 1805.6 | 129.3804 | 1.9655
1950.8 | 1805.8 | 129.6683 | 1.8695
1951 | 1806 | 129.6683 | 1.8695
1951.2 | 1806.2 | 129.6683 | 1.8695
1951.4 | 1806.4 | 129.5724 | 1.9655
1951.6 | 1806.6 | 129.5724 | 1.8695
1951.8 | 1806.8 | 129.5724 | 1.9655
1952 | 1807 | 129.6683 | 1.8695
1952.2 | 1807.2 | 129.5724 | 1.8695
1952.4 | 1807.4 | 129.5724 | 1.8695
1952.6 | 1807.6 | 129.5724 | 1.8695
1952.8 | 1807.8 | 129.4764 | 1.9655
1953 | 1808 | 129.5724 | 1.8695
1953.2 | 1808.2 | 129.5724 | 1.9655
1953.4 | 1808.4 | 129.5724 | 1.8695
1953.6 | 1808.6 | 129.5724 | 1.8695
1953.8 | 1808.8 | 129.5724 | 1.8695
1954 | 1809 | 129.5724 | 1.8695
1954.2 | 1809.2 | 129.5724 | 1.8695
1954.4 | 1809.4 | 129.5724 | 1.8695
1954.6 | 1809.6 | 129.5724 | 1.9655
1954.8 | 1809.8 | 129.4764 | 2.0615
1955 | 1810 | 129.4764 | 2.0615
1955.2 | 1810.2 | 129.5724 | 1.9655
1955.4 | 1810.4 | 129.5724 | 2.4453
1955.6 | 1810.6 | 129.5724 | 2.1574
1955.8 | 1810.8 | 129.5724 | 1.9655
1956 | 1811 | 129.5724 | 1.9655
1956.2 | 1811.2 | 129.5724 | 1.9655
1956.4 | 1811.4 | 129.6683 | 1.9655
1956.6 | 1811.6 | 129.5724 | 1.9655
1956.8 | 1811.8 | 129.6683 | 1.9655
1957 | 1812 | 129.5724 | 2.0615
1957.2 | 1812.2 | 129.4764 | 2.1574
1957.4 | 1812.4 | 129.6683 | 2.0615
1957.6 | 1812.6 | 130.3401 | 1.6776
1957.8 | 1812.8 | 129.1885 | 2.6373
1958 | 1813 | 129.4764 | 2.0615
1958.2 | 1813.2 | 129.5724 | 1.9655
1958.4 | 1813.4 | 129.6683 | 1.8695
1958.6 | 1813.6 | 129.5724 | 1.9655
1958.8 | 1813.8 | 129.6683 | 1.8695
1959 | 1814 | 129.5724 | 1.9655
1959.2 | 1814.2 | 129.6683 | 2.0615
1959.4 | 1814.4 | 129.5724 | 1.9655
1959.6 | 1814.6 | 129.4764 | 1.9655
1959.8 | 1814.8 | 129.5724 | 2.0615
1960 | 1815 | 128.8046 | 2.3494
1960.2 | 1815.2 | 129.4764 | 2.6373
1960.4 | 1815.4 | 129.4764 | 2.0615
1960.6 | 1815.6 | 129.4764 | 2.2534
1960.8 | 1815.8 | 129.4764 | 2.2534
1961 | 1816 | 129.5724 | 2.0615
1961.2 | 1816.2 | 129.4764 | 2.0615
1961.4 | 1816.4 | 129.4764 | 1.9655
1961.6 | 1816.6 | 129.3804 | 1.9655
1961.8 | 1816.8 | 129.4764 | 2.0615
1962 | 1817 | 129.4764 | 1.9655
1962.2 | 1817.2 | 129.4764 | 1.9655
1962.4 | 1817.4 | 129.4764 | 2.3494
1962.6 | 1817.6 | 129.5724 | 2.3494
1962.8 | 1817.8 | 129.4764 | 2.1574
1963 | 1818 | 129.5724 | 1.8695
1963.2 | 1818.2 | 129.5724 | 1.9655
1963.4 | 1818.4 | 129.4764 | 1.8695
1963.6 | 1818.6 | 129.5724 | 1.9655
1963.8 | 1818.8 | 129.4764 | 2.0615
1964 | 1819 | 129.5724 | 1.9655
1964.2 | 1819.2 | 129.0925 | 1.9655
1964.4 | 1819.4 | 129.8603 | 1.7736
1964.6 | 1819.6 | 129.2844 | 2.3494
1964.8 | 1819.8 | 129.6683 | 2.9252
1965 | 1820 | 129.4764 | 2.4453
1965.2 | 1820.2 | 129.0925 | 1.7736
1965.4 | 1820.4 | 129.4764 | 2.4453
1965.6 | 1820.6 | 129.7643 | 2.7332
1965.8 | 1820.8 | 129.3804 | 2.0615
1966 | 1821 | 128.9006 | 2.2534
1966.2 | 1821.2 | 129.4764 | 2.1574
1966.4 | 1821.4 | 129.5724 | 2.0615
1966.6 | 1821.6 | 129.1885 | 2.1574
1966.8 | 1821.8 | 129.2844 | 2.3494
1967 | 1822 | 129.4764 | 2.2534
1967.2 | 1822.2 | 129.4764 | 2.2534
1967.4 | 1822.4 | 129.5724 | 2.0615
1967.6 | 1822.6 | 129.4764 | 2.0615
1967.8 | 1822.8 | 129.5724 | 2.0615
1968 | 1823 | 129.1885 | 2.2534
1968.2 | 1823.2 | 129.4764 | 3.0211
1968.4 | 1823.4 | 129.4764 | 1.5816
1968.6 | 1823.6 | 129.7643 | 2.5413
1968.8 | 1823.8 | 129.4764 | 2.0615
1969 | 1824 | 129.3804 | 2.1574
1969.2 | 1824.2 | 129.5724 | 1.9655
1969.4 | 1824.4 | 129.3804 | 1.9655
1969.6 | 1824.6 | 129.3804 | 2.6373
1969.8 | 1824.8 | 129.5724 | 2.5413
1970 | 1825 | 129.2844 | 2.3494
1970.2 | 1825.2 | 128.5167 | 2.8292
1970.4 | 1825.4 | 129.4764 | 2.5413
1970.6 | 1825.6 | 129.4764 | 2.1574
1970.8 | 1825.8 | 129.4764 | 2.1574
1971 | 1826 | 129.3804 | 2.0615
1971.2 | 1826.2 | 129.5724 | 2.0615
1971.4 | 1826.4 | 129.4764 | 2.1574
1971.6 | 1826.6 | 129.5724 | 2.0615
1971.8 | 1826.8 | 129.4764 | 2.0615
1972 | 1827 | 129.3804 | 2.0615
1972.2 | 1827.2 | 129.4764 | 2.1574
1972.4 | 1827.4 | 129.4764 | 2.1574
1972.6 | 1827.6 | 129.5724 | 2.0615
1972.8 | 1827.8 | 129.5724 | 2.2534
1973 | 1828 | 129.4764 | 2.7332
1973.2 | 1828.2 | 129.5724 | 2.1574
1973.4 | 1828.4 | 129.4764 | 2.1574
1973.6 | 1828.6 | 129.5724 | 2.0615
1973.8 | 1828.8 | 129.5724 | 2.0615
1974 | 1829 | 129.5724 | 2.0615
1974.2 | 1829.2 | 129.5724 | 2.0615
1974.4 | 1829.4 | 129.5724 | 2.4453
1974.6 | 1829.6 | 129.5724 | 2.2534
1974.8 | 1829.8 | 129.5724 | 2.2534
1975 | 1830 | 129.5724 | 2.1574
1975.2 | 1830.2 | 129.4764 | 2.0615
1975.4 | 1830.4 | 129.5724 | 2.1574
1975.6 | 1830.6 | 129.5724 | 2.1574
1975.8 | 1830.8 | 129.4764 | 2.0615
1976 | 1831 | 129.4764 | 2.1574
1976.2 | 1831.2 | 129.5724 | 2.1574
1976.4 | 1831.4 | 129.5724 | 2.1574
1976.6 | 1831.6 | 129.5724 | 2.0615
1976.8 | 1831.8 | 129.4764 | 2.0615
1977 | 1832 | 129.5724 | 2.1574
1977.2 | 1832.2 | 129.5724 | 2.1574
1977.4 | 1832.4 | 129.6683 | 2.0615
1977.6 | 1832.6 | 129.3804 | 2.1574
1977.8 | 1832.8 | 129.3804 | 2.0615
1978 | 1833 | 129.4764 | 2.7332
1978.2 | 1833.2 | 129.5724 | 2.3494
1978.4 | 1833.4 | 129.5724 | 2.2534
1978.6 | 1833.6 | 129.5724 | 2.1574
1978.8 | 1833.8 | 129.5724 | 2.1574
1979 | 1834 | 129.5724 | 2.1574
1979.2 | 1834.2 | 129.4764 | 2.5413
1979.4 | 1834.4 | 129.4764 | 2.3494
1979.6 | 1834.6 | 129.5724 | 2.2534
1979.8 | 1834.8 | 129.4764 | 2.1574
1980 | 1835 | 129.4764 | 2.2534
1980.2 | 1835.2 | 129.2844 | 2.2534
1980.4 | 1835.4 | 129.5724 | 2.1574
1980.6 | 1835.6 | 129.5724 | 2.2534
1980.8 | 1835.8 | 129.4764 | 2.1574
1981 | 1836 | 129.4764 | 2.2534
1981.2 | 1836.2 | 129.4764 | 2.2534
1981.4 | 1836.4 | 129.7643 | 2.1574
1981.6 | 1836.6 | 129.3804 | 2.7332
1981.8 | 1836.8 | 129.6683 | 2.3494
1982 | 1837 | 129.4764 | 2.2534
1982.2 | 1837.2 | 129.4764 | 2.2534
1982.4 | 1837.4 | 129.3804 | 2.2534
1982.6 | 1837.6 | 129.2844 | 2.1574
1982.8 | 1837.8 | 129.3804 | 3.501
1983 | 1838 | 129.4764 | 2.8292
1983.2 | 1838.2 | 129.4764 | 2.3494
1983.4 | 1838.4 | 129.4764 | 2.2534
1983.6 | 1838.6 | 129.3804 | 2.2534
1983.8 | 1838.8 | 129.4764 | 2.2534
1984 | 1839 | 129.4764 | 2.2534
1984.2 | 1839.2 | 129.4764 | 2.2534
1984.4 | 1839.4 | 129.5724 | 2.2534
1984.6 | 1839.6 | 129.4764 | 2.2534
1984.8 | 1839.8 | 129.4764 | 2.3494
1985 | 1840 | 129.5724 | 2.3494
1985.2 | 1840.2 | 129.5724 | 2.2534
1985.4 | 1840.4 | 129.5724 | 2.2534
1985.6 | 1840.6 | 129.5724 | 2.2534
1985.8 | 1840.8 | 129.5724 | 2.2534
1986 | 1841 | 129.6683 | 300.6155
1986.2 | 1841.2 | 128.7087 | 14.3453
1986.4 | 1841.4 | 129.2844 | 5.9002
1986.6 | 1841.6 | 129.3804 | 4.2687
1986.8 | 1841.8 | 129.3804 | 4.0768
1987 | 1842 | 129.5724 | 3.501
1987.2 | 1842.2 | 129.7643 | 1.6776
1987.4 | 1842.4 | 129.9562 | 1.1018
1987.6 | 1842.6 | 130.1482 | 0.8139
1987.8 | 1842.8 | 129.6683 | 1.0058
1988 | 1843 | 129.7643 | 1.0058
1988.2 | 1843.2 | 129.7643 | 0.90985
1988.4 | 1843.4 | 129.4764 | 1.3897
1988.6 | 1843.6 | 129.7643 | 0.90985
1988.8 | 1843.8 | 129.7643 | 1.0058
1989 | 1844 | 129.7643 | 1.0058
1989.2 | 1844.2 | 129.6683 | 1.1018
1989.4 | 1844.4 | 129.6683 | 0.90985
1989.6 | 1844.6 | 129.7643 | 1.0058
1989.8 | 1844.8 | 129.7643 | 1.0058
1990 | 1845 | 129.7643 | 1.0058
1990.2 | 1845.2 | 129.6683 | 0.90985
1990.4 | 1845.4 | 129.7643 | 1.0058
1990.6 | 1845.6 | 129.8603 | 1.0058
1990.8 | 1845.8 | 127.4611 | 2.4453
1991 | 1846 | 129.7643 | 1.1018
1991.2 | 1846.2 | 129.6683 | 0.90985
1991.4 | 1846.4 | 129.6683 | 3.8848
1991.6 | 1846.6 | 129.6683 | 1.4857
1991.8 | 1846.8 | 129.8603 | 1.0058
1992 | 1847 | 129.7643 | 0.90985
1992.2 | 1847.2 | 129.7643 | 0.8139
1992.4 | 1847.4 | 129.8603 | 0.8139
1992.6 | 1847.6 | 130.0522 | 0.71795
1992.8 | 1847.8 | 129.8603 | 0.8139
1993 | 1848 | 129.7643 | 0.71795
1993.2 | 1848.2 | 129.8603 | 0.71795
1993.4 | 1848.4 | 129.8603 | 0.8139
1993.6 | 1848.6 | 129.7643 | 0.71795
1993.8 | 1848.8 | 129.8603 | 0.71795
1994 | 1849 | 129.7643 | 0.8139
1994.2 | 1849.2 | 130.2441 | 0.71795
1994.4 | 1849.4 | 129.9562 | 0.71795
1994.6 | 1849.6 | 129.8603 | 0.8139
1994.8 | 1849.8 | 128.7087 | 1.3897
1995 | 1850 | 129.4764 | 1.1018
1995.2 | 1850.2 | 129.0925 | 0.71795
1995.4 | 1850.4 | 130.0522 | 1.0058
1995.6 | 1850.6 | 129.6683 | 0.90985
1995.8 | 1850.8 | 129.6683 | 1.1018
1996 | 1851 | 129.8603 | 1.1018
1996.2 | 1851.2 | 129.9562 | 1.1978
1996.4 | 1851.4 | 129.7643 | 0.8139
1996.6 | 1851.6 | 129.9562 | 0.90985
1996.8 | 1851.8 | 129.8603 | 0.8139
1997 | 1852 | 129.9562 | 0.71795
1997.2 | 1852.2 | 129.2844 | 0.90985
1997.4 | 1852.4 | 129.8603 | 0.8139
1997.6 | 1852.6 | 129.9562 | 0.62195
1997.8 | 1852.8 | 129.8603 | 0.71795
1998 | 1853 | 129.8603 | 0.71795
1998.2 | 1853.2 | 130.0522 | 0.71795
1998.4 | 1853.4 | 129.8603 | 0.71795
1998.6 | 1853.6 | 129.7643 | 1.0058
1998.8 | 1853.8 | 129.8603 | 0.90985
1999 | 1854 | 129.9562 | 0.8139
1999.2 | 1854.2 | 129.9562 | 0.8139
1999.4 | 1854.4 | 129.9562 | 0.8139
1999.6 | 1854.6 | 129.9562 | 0.71795
1999.8 | 1854.8 | 129.9562 | 0.71795
2000 | 1855 | 129.9562 | 0.8139
2000.2 | 1855.2 | 129.9562 | 0.8139
2000.4 | 1855.4 | 129.9562 | 0.71795
2000.6 | 1855.6 | 129.8603 | 0.71795
2000.8 | 1855.8 | 129.9562 | 0.71795
2001 | 1856 | 129.9562 | 0.71795
2001.2 | 1856.2 | 129.8603 | 0.71795
2001.4 | 1856.4 | 129.9562 | 0.8139
2001.6 | 1856.6 | 128.9006 | 1.4857
2001.8 | 1856.8 | 130.2441 | 0.8139
2002 | 1857 | 129.9562 | 0.90985
2002.2 | 1857.2 | 129.8603 | 0.90985
2002.4 | 1857.4 | 129.9562 | 0.8139
2002.6 | 1857.6 | 129.9562 | 0.8139
2002.8 | 1857.8 | 129.9562 | 0.71795
2003 | 1858 | 129.9562 | 0.8139
2003.2 | 1858.2 | 129.9562 | 0.71795
2003.4 | 1858.4 | 129.9562 | 0.8139
2003.6 | 1858.6 | 129.8603 | 0.71795
2003.8 | 1858.8 | 129.8603 | 0.8139
2004 | 1859 | 129.6683 | 0.90985
2004.2 | 1859.2 | 131.8756 | 1.0058
2004.4 | 1859.4 | 129.7643 | 2.8292
2004.6 | 1859.6 | 129.9562 | 2.1574
2004.8 | 1859.8 | 130.4361 | 1.1018
2005 | 1860 | 129.9562 | 1.0058
2005.2 | 1860.2 | 129.3804 | 4.1727
2005.4 | 1860.4 | 129.6683 | 3.2131
2005.6 | 1860.6 | 131.0119 | 1.2937
2005.8 | 1860.8 | 130.9159 | 2.4453
2006 | 1861 | 129.7643 | 1.5816
2006.2 | 1861.2 | 129.5724 | 1.6776
2006.4 | 1861.4 | 129.1885 | 1.5816
2006.6 | 1861.6 | 129.8603 | 1.3897
2006.8 | 1861.8 | 129.1885 | 1.5816
2007 | 1862 | 130.3401 | 1.0058
2007.2 | 1862.2 | 130.0522 | 1.0058
2007.4 | 1862.4 | 129.7643 | 1.1018
2007.6 | 1862.6 | 128.9966 | 1.5816
2007.8 | 1862.8 | 130.8199 | 1.0058
2008 | 1863 | 130.0522 | 0.71795
2008.2 | 1863.2 | 130.532 | 0.71795
2008.4 | 1863.4 | 129.3804 | 0.526
2008.6 | 1863.6 | 129.5724 | 1.1978
2008.8 | 1863.8 | 129.4764 | 3.405
2009 | 1864 | 129.8603 | 1.1018
2009.2 | 1864.2 | 129.6683 | 1.0058
2009.4 | 1864.4 | 130.0522 | 0.90985
2009.6 | 1864.6 | 129.8603 | 0.90985
2009.8 | 1864.8 | 130.2441 | 1.1978
2010 | 1865 | 129.7643 | 0.8139
2010.2 | 1865.2 | 128.7087 | 1.3897
2010.4 | 1865.4 | 130.2441 | 0.8139
2010.6 | 1865.6 | 129.4764 | 1.1978
2010.8 | 1865.8 | 129.8603 | 0.8139
2011 | 1866 | 129.4764 | 0.71795
2011.2 | 1866.2 | 129.8603 | 0.62195
2011.4 | 1866.4 | 129.9562 | 1.3897
2011.6 | 1866.6 | 130.0522 | 0.8139
2011.8 | 1866.8 | 130.0522 | 0.90985
2012 | 1867 | 130.532 | 1.0058
2012.2 | 1867.2 | 129.4764 | 0.8139
2012.4 | 1867.4 | 129.9562 | 0.71795
2012.6 | 1867.6 | 129.4764 | 1.1018
2012.8 | 1867.8 | 129.6683 | 0.8139
2013 | 1868 | 129.5724 | 0.90985
2013.2 | 1868.2 | 129.3804 | 1.5816
2013.4 | 1868.4 | 129.6683 | 0.90985
2013.6 | 1868.6 | 129.7643 | 0.71795
2013.8 | 1868.8 | 129.4764 | 0.71795
2014 | 1869 | 129.7643 | 0.71795
2014.2 | 1869.2 | 129.8603 | 0.8139
2014.4 | 1869.4 | 129.6683 | 0.71795
2014.6 | 1869.6 | 129.7643 | 0.71795
2014.8 | 1869.8 | 129.8603 | 0.71795
2015 | 1870 | 129.8603 | 0.71795
2015.2 | 1870.2 | 129.6683 | 0.8139
2015.4 | 1870.4 | 129.7643 | 0.71795
2015.6 | 1870.6 | 129.7643 | 0.8139
2015.8 | 1870.8 | 130.4361 | 1.1978
2016 | 1871 | 129.7643 | 0.8139
2016.2 | 1871.2 | 130.4361 | 1.8695
2016.4 | 1871.4 | 129.7643 | 0.8139
2016.6 | 1871.6 | 129.7643 | 0.8139
2016.8 | 1871.8 | 129.7643 | 0.71795
2017 | 1872 | 129.7643 | 0.71795
2017.2 | 1872.2 | 129.7643 | 0.71795
2017.4 | 1872.4 | 129.9562 | 0.71795
2017.6 | 1872.6 | 129.6683 | 0.71795
2017.8 | 1872.8 | 129.6683 | 1.1978
2018 | 1873 | 129.6683 | 1.1018
2018.2 | 1873.2 | 129.8603 | 1.1978
2018.4 | 1873.4 | 129.7643 | 1.0058
2018.6 | 1873.6 | 129.9562 | 0.90985
2018.8 | 1873.8 | 129.7643 | 0.8139
2019 | 1874 | 129.8603 | 0.8139
2019.2 | 1874.2 | 129.6683 | 0.8139
2019.4 | 1874.4 | 129.7643 | 0.8139
2019.6 | 1874.6 | 129.8603 | 0.8139
2019.8 | 1874.8 | 129.6683 | 0.71795
2020 | 1875 | 129.6683 | 0.71795
2020.2 | 1875.2 | 130.1482 | 0.62195
2020.4 | 1875.4 | 129.8603 | 0.71795
2020.6 | 1875.6 | 129.7643 | 0.71795
2020.8 | 1875.8 | 129.7643 | 0.62195
2021 | 1876 | 129.8603 | 0.71795
2021.2 | 1876.2 | 129.8603 | 0.62195
2021.4 | 1876.4 | 129.8603 | 0.71795
2021.6 | 1876.6 | 129.7643 | 0.62195
2021.8 | 1876.8 | 129.7643 | 0.71795
2022 | 1877 | 129.7643 | 0.71795
2022.2 | 1877.2 | 129.7643 | 0.71795
2022.4 | 1877.4 | 129.7643 | 0.71795
2022.6 | 1877.6 | 129.7643 | 0.71795
2022.8 | 1877.8 | 129.8603 | 0.71795
2023 | 1878 | 129.7643 | 0.8139
2023.2 | 1878.2 | 129.7643 | 0.71795
2023.4 | 1878.4 | 129.8603 | 0.62195
2023.6 | 1878.6 | 129.4764 | 0.8139
2023.8 | 1878.8 | 129.9562 | 0.62195
2024 | 1879 | 129.6683 | 0.71795
2024.2 | 1879.2 | 131.2998 | 0.71795
2024.4 | 1879.4 | 129.8603 | 0.71795
2024.6 | 1879.6 | 129.6683 | 0.526
2024.8 | 1879.8 | 129.7643 | 0.71795
2025 | 1880 | 129.6683 | 0.71795
2025.2 | 1880.2 | 129.9562 | 0.62195
2025.4 | 1880.4 | 129.7643 | 0.62195
2025.6 | 1880.6 | 129.8603 | 0.62195
2025.8 | 1880.8 | 129.8603 | 0.71795
2026 | 1881 | 129.6683 | 0.62195
2026.2 | 1881.2 | 129.7643 | 0.62195
2026.4 | 1881.4 | 129.7643 | 0.62195
2026.6 | 1881.6 | 129.8603 | 0.62195
2026.8 | 1881.8 | 129.7643 | 0.526
2027 | 1882 | 129.7643 | 0.62195
2027.2 | 1882.2 | 129.7643 | 0.71795
2027.4 | 1882.4 | 129.7643 | 0.71795
2027.6 | 1882.6 | 129.8603 | 0.62195
2027.8 | 1882.8 | 129.7643 | 0.62195
2028 | 1883 | 129.8603 | 0.71795
2028.2 | 1883.2 | 129.7643 | 0.71795
2028.4 | 1883.4 | 129.9562 | 0.71795
2028.6 | 1883.6 | 73.9114 | 0.43001