## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 3, Location C, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE and EPR control cables (Items 10 & 2). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 145 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
145 | 0 | Ignited Gas Burner
489-494 | 344-349 | Conductors D7 & D8 both short to ground (237 & 36) | Cable D shorts to ground
506-509 | 361-634 | Conductors E9 & E10 both short to ground at less than 100 ohms (1 & 2) | Cable E shorts to ground
513 | 368 | Conductors D7 & D8 short together at less than 100 ohms (80) | Cable D shorted internally
527-530 | 382-385 | Conductors F11 & F12 both short to ground (148 & 37) | Cable F shorts to ground
538 | 393 | Conductors E9 & E10 short together at less than 100 ohms (26) | Cable E shorted internally
552 | 407 | Conductors F11 & F12 short together at less than 1000 ohms (148) | Cable F shorted internally
673 | 528 | The existing ground fault on conductor D7 decreases to less than 100 ohms (4)
712 | 567 | The existing ground fault on conductor F11 decreases to less than 100 ohms (1)
737 | 592 | The existing internal fault on conductors F11 & F12 decreases to less than 100 ohms (10)
795 | 650 | Conductor B3 shorts to ground at less than 100 ohms (29)
798 | 653 | Conductors B3 & B4 short together at less than 100 ohms (82) | Cable B shorted internally
811 | 666 | Conductor B4 shorts to ground at less than 100 ohms (1) | Cable B shorts to ground
825-833 | 680-688 | Conductors C5 & C6 both short to ground at less than 100 ohms (6 & 14) | Cable C shorts to ground
846 | 701 | Conductors C5 & C6 short together at less than 100 ohms (60) | Cable C shorted internally
924 | 779 | Conductors A1 & A2 short toether at less than 100 ohms (65) | Cable A shorted internally
930-952 | 785-807 | Conductors A1 & A2 both short to ground at less than 100 ohms (53 & 19) | Cable A shorts to ground
1072 | 927 | Gas burner is shut off
Additional Observations
Observation 1 | The progression of cable failure began with the bottom three cables (D, E & F) and moved up the bundle to the top cables.
Observation 2 | No cable to cable interactions took place during this test.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | EPR | (Item #2)
|  |  |  | Cable D = | XLPE | (Item #10)
|  |  |  | Cable E = | EPR | (Item #2)
|  |  |  | Cable F = | XLPE | (Item #10)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | EPR | (Item #2)
|  |  |  | Cable C = | EPR | (Item #2)
|  |  |  | Cable D = | XLPE | (Item #10)
|  |  |  | Cable E = | EPR | (Item #2)
|  |  |  | Cable F = | XLPE | (Item #10)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 3 |  |  | 2006-10-26 | 13:08
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-144.5 | 254237.9994 | -142 | 234237.9994 | -139 | 256637.9994 | -136.5 | 234537.9994 | -133.5 | 239137.9994 | -114 | 248937.9994 | -111 | 245937.9994 | -108.5 | 253637.9994 | -105.5 | 231037.9994 | -86 | 255437.9994 | -83 | 247237.9994 | -80.5 | 254237.9994 | -77.5 | 263837.9994 | -74.5 | 259437.9994 | -72 | 249437.9994 | -69 | 257637.9994 | -60.5 | 251937.9994 | -58 | 223737.9994 | -55 | 254937.9994 | -52.5 | 258137.9994 | -49.5 | 264637.9994 | -46.5 | 255537.9994 | -38.5 | 254437.9994 | -30 | 263837.9994 | -27 | 260637.9994 | -24.5 | 257937.9994 | -21.5 | 518575.9997 | -13 | 264537.9994 | -10.5 | 263837.9994 | -7.5 | 515775.9997 | -4.5 | 257837.9994 | -2 | 261137.9994 | 0.5 | 261837.9994 | 3.5 | 254537.9994 | 12 | 257437.9994 | 15 | 264537.9994 | 23 | 261237.9994 | 26 | 262237.9994 | 29 | 249137.9994 | 31.5 | 259537.9994 | 34.5 | 260137.9994 | 37.5 | 263137.9994
40 | 254237.9994 | 43 | 234237.9994 | 45.5 | 256637.9994 | 48.5 | 234537.9994 | 51 | 239137.9994 | 70.5 | 248937.9994 | 73.5 | 245937.9994 | 76.5 | 253637.9994 | 79.5 | 231037.9994 | 98.5 | 255437.9994 | 101.5 | 247237.9994 | 104.5 | 254237.9994 | 107 | 263837.9994 | 110 | 518975.9997 | 113 | 249437.9994 | 115.5 | 257637.9994 | 124 | 251937.9994 | 126.5 | 223737.9994 | 129.5 | 254937.9994 | 132.5 | 258137.9994 | 135 | 264637.9994 | 138 | 255537.9994 | 146.5 | 254437.9994 | 155 | 263837.9994 | 157.5 | 260637.9994 | 160.5 | 257937.9994 | 163 | 259237.9994 | 171.5 | 264537.9994 | 174.5 | 263837.9994 | 177.5 | 257837.9994 | 180 | 257837.9994 | 183 | 261137.9994 | 185.5 | 261837.9994 | 188.5 | 254537.9994 | 197 | 257437.9994 | 199.5 | 264537.9994 | 208 | 261237.9994 | 210.5 | 262237.9994 | 213.5 | 249137.9994 | 216.5 | 259537.9994 | 219.5 | 260137.9994 | 222 | 263137.9994
225 | 254237.9994 | 227.5 | 468575.9997 | 230.5 | 256637.9994 | 233.5 | 234537.9994 | 236 | 239137.9994 | 255.5 | 248937.9994 | 258.5 | 245937.9994 | 261 | 253637.9994 | 264 | 231037.9994 | 283.5 | 255437.9994 | 286.5 | 247237.9994 | 289 | 254237.9994 | 292 | 263837.9994 | 294.5 | 259437.9994 | 297.5 | 249437.9994 | 300.5 | 257637.9994 | 308.5 | 251937.9994 | 311.5 | 223737.9994 | 314.5 | 254937.9994 | 317.5 | 258137.9994 | 320 | 264637.9994 | 322.5 | 255537.9994 | 331 | 254437.9994 | 339.5 | 263837.9994 | 342.5 | 260637.9994 | 345 | 257937.9994 | 348 | 259237.9994 | 356.5 | 264537.9994 | 359 | 263837.9994 | 362 | 257837.9994 | 365 | 257837.9994 | 367.5 | 79.7129 | 370.5 | 1634.5966 | 373 | 236.3612 | 381.5 | 34.4584 | 384.5 | 37.1688 | 393 | 25.6055 | 395.5 | 25.2227 | 398.5 | 0.51887 | 401 | 9.8167 | 404 | 4.1118 | 407 | 147.6906
409.5 | 254237.9994 | 412.5 | 234237.9994 | 415.5 | 256637.9994 | 418 | 234537.9994 | 420.5 | 239137.9994 | 440.5 | 248937.9994 | 443 | 245937.9994 | 446 | 507375.9997 | 448.5 | 231037.9994 | 468.5 | 255437.9994 | 471 | 247237.9994 | 474 | 254237.9994 | 477 | 263837.9994 | 479.5 | 259437.9994 | 482.5 | 249437.9994 | 485.5 | 257637.9994 | 493.5 | 251937.9994 | 496.5 | 223737.9994 | 499 | 254937.9994 | 502 | 258137.9994 | 504.5 | 264637.9994 | 507.5 | 255537.9994 | 516 | 254437.9994 | 524.5 | 263837.9994 | 527 | 260637.9994 | 530 | 257937.9994 | 533 | 259237.9994 | 541 | 264537.9994 | 544 | 263837.9994 | 546.5 | 257837.9994 | 549.5 | 257837.9994 | 552.5 | 6.427 | 555 | 24.907 | 558 | 6.5494 | 566.5 | 13.3457 | 569 | 32.4468 | 577.5 | 0.95474 | 580.5 | 8.3989 | 583.5 | 0.22735 | 586 | 7.5458 | 588.5 | 14.444 | 591.5 | 10.3406
594.5 | 254237.9994 | 597 | 234237.9994 | 600 | 256637.9994 | 602.5 | 234537.9994 | 605.5 | 239137.9994 | 625 | 248937.9994 | 628 | 245937.9994 | 630.5 | 253637.9994 | 633.5 | 231037.9994 | 653 | 82.3898 | 656 | 30.7689 | 658.5 | 46.7343 | 661.5 | 27.4353 | 664.5 | 51.1808 | 667 | 39.581 | 670 | 93.4159 | 678.5 | 39.5522 | 681 | 0.61936 | 684 | 10.3676 | 686.5 | 24.4087 | 689.5 | 28.0163 | 692.5 | 24.8161 | 700.5 | 60.4204 | 709 | 12.8486 | 712 | 21.8715 | 714.5 | 17.9758 | 717.5 | 21.975 | 726 | 85.3661 | 728.5 | 12.999 | 731.5 | 46.6649 | 734.5 | 52.5089 | 737 | 0.95389 | 740 | 29.6159 | 742.5 | 24.7622 | 751 | 0.92218 | 754 | 19.1684 | 762.5 | 11.3277 | 765 | 11.0712 | 768 | 4.2593 | 770.5 | 10.2528 | 773.5 | 7.1967 | 776.5 | 6.9353
779 | 64.7189 | 782 | 95.6992 | 784.5 | 87.6692 | 787.5 | 61.2714 | 790.5 | 52.4053 | 810 | 36.5617 | 812.5 | 28.6785 | 815.5 | 49.9184 | 818.5 | 18.1453 | 838 | 0.90493 | 840.5 | 12.0217 | 843.5 | 1.5476 | 846.5 | 5.9672 | 849 | 20.3753 | 852 | 2.509 | 854.5 | 7.443 | 863 | 9.3478 | 866 | 10.0232 | 868.5 | 0.9006 | 871.5 | 22.1636 | 874.5 | 10.3525 | 877 | 14.2183 | 885.5 | 4.013 | 894 | 6.3233 | 896.5 | 20.3613 | 899.5 | 17.9758 | 902.5 | 0.93764 | 910.5 | 19.3351 | 913.5 | 33.535 | 916.5 | 15.0983 | 919 | 7.3412 | 922 | 25.4948 | 924.5 | 1.2868 | 927.5 | 11.9517 | 936 | 25.943 | 938.5 | 0.9828 | 947 | 19.9549 | 950 | 18.7848 | 952.5 | 12.208 | 955.5 | 19.9624 | 958.5 | 15.2843 | 961 | 0.97092
964 | 0.41588 | 966.5 | 17.6287 | 969.5 | 29.188 | 972.5 | 0.25388 | 975 | 12.0405 | 994.5 | 18.9271 | 997.5 | 0.82185 | 1000.5 | 12.5776 | 1003 | 2.8084 | 1022.5 | 0.64747 | 1025.5 | 0.83333 | 1028.5 | 0.12045 | 1031 | 30.1513 | 1034 | 22.6055 | 1036.5 | 0.35652 | 1039.5 | 23.9807 | 1048 | 0.87454 | 1050.5 | 4.0382 | 1053.5 | 13.947 | 1056.5 | 10.1366 | 1059 | 10.0663 | 1062 | 8.9652 | 1070.5 | 0.69384 | 1078.5 | 27.372 | 1081.5 | 13.7848 | 1084.5 | 0.3251 | 1087 | 1.8732 | 1095.5 | 3.6036 | 1098.5 | 22.0873 | 1101 | 1.1903 | 1104 | 0.85913 | 1106.5 | 5.798 | 1109.5 | 20.1194 | 1112.5 | 0.89714 | 1120.5 | 13.6568 | 1123.5 | 0.27612 | 1132 | 13.2809 | 1134.5 | 9.2443 | 1137.5 | 6.2489 | 1140.5 | 11.4323 | 1143 | 0.94534 | 1146 | 2.1278
1148.5 | 17.4309 | 1151.5 | 3.4847 | 1154.5 | 30.1303 | 1157 | 17.1141 | 1160 | 0.45936 | 1179.5 | 0.51685 | 1182.5 | 23.9462 | 1185 | 6.4459 | 1188 | 0.68737 | 1207.5 | 10781.7845 | 1210.5 | 26.8423 | 1213 | 29.9859 | 1216 | 37.3138 | 1218.5 | 14.9706 | 1221.5 | 0.39872 | 1224.5 | 3.7906 | 1232.5 | 11.7628 | 1235.5 | 9.7443 | 1238.5 | 3.8661 | 1241 | 18.0125 | 1244 | 40.0489 | 1246.5 | 9.9389 | 1255 | 4.9068 | 1263.5 | 35.7919 | 1266.5 | 16.1478 | 1269 | 17.476 | 1272 | 17.8526 | 1280.5 | 39.5417 | 1283 | 35.5772 | 1286 | 11.8896 | 1288.5 | 29.0629 | 1291.5 | 30.5282 | 1294.5 | 24.7843 | 1297 | 0.45315 | 1305.5 | 1.3219 | 1308.5 | 21.6593 | 1316.5 | 28.2067 | 1319.5 | 4.7018 | 1322.5 | 0.060033 | 1325 | 20.7112 | 1328 | 18.3218 | 1330.5 | 28.2414
1333.5 | 95.0642 | 1336.5 | 0.71672 | 1339 | 10.7146 | 1342 | 16.3951 | 1344.5 | 4.9065 | 1364 | 8.6662 | 1367 | 18.3543 | 1370 | 24.129 | 1372.5 | 5.79 | 1392.5 | 209.085 | 1395 | 23.6457 | 1398 | 29.2393 | 1400.5 | 26.4919 | 1403.5 | 21.4218 | 1406.5 | 24.2447 | 1409 | 27.8434 | 1417.5 | 38.8439 | 1420.5 | 8.4247 | 1423 | 15.4964 | 1426 | 9.3611 | 1428.5 | 21.648 | 1431.5 | 24.5656 | 1440 | 11.5512 | 1448.5 | 45.0425 | 1451 | 35.9251 | 1454 | 29.714 | 1456.5 | 18.019 | 1465 | 36.5878 | 1467.5 | 15.4593 | 1470.5 | 44.8963 | 1473.5 | 40.1437 | 1476.5 | 141.1734 | 1479 | 29.2869 | 1482 | 2.3522 | 1490.5 | 17.7447 | 1493 | 27.0188 | 1501.5 | 12.5722 | 1504.5 | 26.5294 | 1507 | 20.6885 | 1510 | 27.4935 | 1512.5 | 5.121 | 1515 | 26.0908

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 3 |  |  | 2006-10-26 | 13:08
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-139.1 | 234238 |  | -116.7 | 231038 | -88.7222 | 234238 | -73.1111 | 223738 | -58.8889 | 234538 | -50.1667 | 223738 | -26.1 | 254538 | -20.4 | 257438 | -8.2222 | 249138 | -5.0556 | 254538 | 12.6 | 257838 | 15 | 249138
45.6 | 234238 |  | 68 | 231038 | 95.9444 | 234238 | 111.4444 | 223738 | 125.8889 | 234538 | 134.6111 | 223738 | 158.7 | 254538 | 164.4 | 257438 | 176.5556 | 249138 | 179.7222 | 254538 | 197.4 | 257838 | 199.6 | 249138
230.5 | 234538 |  | 252.8 | 231038 | 280.7222 | 234238 | 296.3333 | 223738 | 310.6111 | 234538 | 319.3333 | 223738 | 343.5 | 236.8228 | 349.1 | 35.6177 | 361.3889 | 0.98784 | 364.4444 | 1.811 | 382.1 | 148.3377 | 384.5 | 37.3894
415.2 | 234238 |  | 437.5 | 231038 | 465.6667 | 234238 | 481.1111 | 223738 | 495.4444 | 234538 | 504.0556 | 223738 | 528.3 | 4.1176 | 533.9 | 1.7282 | 546.1667 | 0.63073 | 549.2222 | 0.63219 | 566.9 | 0.63488 | 569.2 | 0.66155
599.9 | 234238 |  | 622.3 | 231038 | 650.2778 | 28.6875 | 665.8889 | 0.73717 | 680.1111 | 6.2554 | 688.8333 | 14.4075 | 713 | 0.63097 | 718.6 | 0.63513 | 730.8889 | 3.9003 | 734 | 0.92667 | 751.6 | 0.63909 | 754 | 1.3039
784.7 | 53.3577 |  | 807.1 | 19.3278 | 835.1111 | 0.64514 | 850.6111 | 0.64641 | 864.9444 | 0.63562 | 873.7222 | 0.64769 | 897.8 | 2.8418 | 903.4 | 0.62281 | 915.6667 | 0.62281 | 918.7222 | 6.2061 | 936.5 | 0.62615 | 938.7 | 1.9378
969.5 | 1.6629 |  | 991.9 | 0.67021 | 1019.8333 | 0.66209 | 1035.4444 | 0.6421 | 1049.8333 | 0.84707 | 1058.5 | 0.6482 | 1082.6 | 0.62448 | 1088.2 | 1.8622 | 1100.3889 | 0.62258 | 1103.6667 | 0.63341 | 1121.3 | 3.6778 | 1123.5 | 5.7228
1154.3 | 0.98691 |  | 1176.7 | 0.6482 | 1204.7222 | 1.8938 | 1220.2778 | 3.6906 | 1234.5556 | 6.3362 | 1243.2778 | 2.8459 | 1267.5 | 1.9776 | 1273 | 2.2206 | 1285.3333 | 0.66075 | 1288.3889 | 0.62448 | 1306 | 14.1319 | 1308.3 | 0.63909
1339.1 | 0.70391 |  | 1361.4 | 7.1075 | 1389.5 | 11.8558 | 1405.0556 | 9.6707 | 1419.3889 | 0.703 | 1428 | 1.0296 | 1452.2 | 3.8491 | 1457.9 | 19.0652 | 1470.1111 | 8.6809 | 1473.1111 | 1.3198 | 1490.8 | 21.8885 | 1492.9 | 22.1156

## F11-F12
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 160.707 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39016.5481 | 1 | 0 | 39016.5481 | 1 | 0 |  | 37.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39016.5502 | 1 | 0 | 39016.5502 | 1 | 0 |  | 222 | 367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39016.5523 | 1060 | 0 | 39016.5523 | 1916 | 0 |  | 407 | 552 | 64.7131 | 0 | 116.9719 | 0 | 0.64713 | 0 | 1.1697 | 0 | 0.64713 | 1.1697 | 148.3377 | 37.3894 | 147.6906
39016.5545 | 2355 | 0 | 39016.5545 | 2412 | 0 |  | 591.5 | 736.5 | 143.7729 | 0 | 147.2527 | 0 | 1.4377 | 0 | 1.4725 | 0 | 1.4377 | 1.4725 | 11.7783 | 9.1368 | 10.3406
39016.5566 | 2428 | 0 | 39016.5566 | 2516 | 0 |  | 776.5 | 921.5 | 148.2295 | 0 | 153.602 | 0 | 1.4823 | 0 | 1.536 | 0 | 1.4823 | 1.536 | 8.4176 | 4.6256 | 6.9353
39016.5587 | 2616 | 0 | 39016.5588 | 2493 | 0 |  | 961 | 1106 | 159.707 | 0 | 152.1978 | 0 | 1.5971 | 0 | 1.522 | 0 | 1.5971 | 1.522 | 0.62615 | 5.5909 | 0.97092
39016.5609 | 2539 | 0 | 39016.5609 | 2128 | 0 |  | 1146 | 1291 | 155.0061 | 0 | 129.9145 | 0 | 1.5501 | 0 | 1.2991 | 0 | 1.5501 | 1.2991 | 3.6778 | 23.7021 | 2.1278
39016.563 | 2033 | 0 | 39016.563 | 1972 | 0 |  | 1330.5 | 1475.5 | 124.1148 | 0 | 120.3907 | 0 | 1.2411 | 0 | 1.2039 | 0 | 1.2411 | 1.2039 | 29.4825 | 33.4878 | 28.2414
39016.5652 | 2067 | 0 |  | 2005 | 0 |  | 1515 | 1660 | 126.1905 | 0 | 122.4054 | 0 | 1.2619 | 0 | 1.2241 | 0 | 1.2619 | 1.2241 | 27.3527 | 31.2908 | 26.0908

## E10-F12
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 158.8755 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39016.548 | 1 | 0 | 39016.548 | 1 | 0 |  | 34.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
39016.5502 | 1 | 0 | 39016.5502 | 1 | 0 |  | 219.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
39016.5523 | 2464 | 0 | 39016.5523 | 1783 | 0 |  | 404 | 549 | 150.4274 | 0 | 108.8523 | 0 | 1.5043 | 0 | 1.0885 | 0 | 1.5043 | 1.0885 | 5.6161 | 45.9551 | 4.1118
39016.5544 | 2247 | 0 | 39016.5544 | 2116 | 0 |  | 588.5 | 733.5 | 137.1795 | 0 | 129.1819 | 0 | 1.3718 | 0 | 1.2918 | 0 | 1.3718 | 1.2918 | 15.8158 | 22.9858 | 14.444
39016.5566 | 2395 | 0 | 39016.5566 | 2498 | 0 |  | 773.5 | 918.5 | 146.2149 | 0 | 152.5031 | 0 | 1.4621 | 0 | 1.525 | 0 | 1.4621 | 1.525 | 8.6589 | 4.1785 | 7.1967
39016.5587 | 2231 | 0 | 39016.5587 | 2430 | 0 |  | 958.5 | 1103.5 | 136.2027 | 0 | 148.3516 | 0 | 1.362 | 0 | 1.4835 | 0 | 1.362 | 1.4835 | 16.6463 | 7.0938 | 15.2843
39016.5608 | 2586 | 0 | 39016.5609 | 2381 | 0 |  | 1143 | 1288 | 157.8755 | 0 | 145.3602 | 0 | 1.5788 | 0 | 1.4536 | 0 | 1.5788 | 1.4536 | 0.63341 | 9.2978 | 0.94534
39016.563 | 2175 | 0 | 39016.563 | 2227 | 0 |  | 1328 | 1473 | 132.7839 | 0 | 135.9585 | 0 | 1.3278 | 0 | 1.3596 | 0 | 1.3278 | 1.3596 | 19.6497 | 16.8559 | 18.3218
39016.5651 | 2441 | 0 | 39016.5651 | 2119 | 0 |  | 1512.5 | 1657.5 | 149.0232 | 0 | 129.3651 | 0 | 1.4902 | 0 | 1.2937 | 0 | 1.4902 | 1.2937 | 6.6112 | 22.8117 | 5.121

## E10-F11
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 158.5092 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39016.548 | 1 | 0 | 39016.548 | 1 | 0 |  | 31.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39016.5501 | 1 | 0 | 39016.5501 | 1 | 0 |  | 216.5 | 361.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39016.5523 | 2334 | 0 | 39016.5523 | 767 | 0 |  | 401 | 546 | 142.4908 | 0 | 46.8254 | 0 | 1.4249 | 0 | 0.46825 | 0 | 1.4249 | 0.46825 | 11.2416 | 238.5111 | 9.8167
39016.5544 | 2382 | 0 | 39016.5544 | 2580 | 0 |  | 586 | 731 | 145.4212 | 0 | 157.5092 | 0 | 1.4542 | 0 | 1.5751 | 0 | 1.4542 | 1.5751 | 9 | 0.63488 | 7.5458
39016.5565 | 2325 | 0 | 39016.5566 | 2158 | 0 |  | 770.5 | 915.5 | 141.9414 | 0 | 131.746 | 0 | 1.4194 | 0 | 1.3175 | 0 | 1.4194 | 1.3175 | 11.6723 | 20.3142 | 10.2528
39016.5587 | 2141 | 0 | 39016.5587 | 2355 | 0 |  | 955.5 | 1100.5 | 130.7082 | 0 | 143.7729 | 0 | 1.3071 | 0 | 1.4377 | 0 | 1.3071 | 1.4377 | 21.2695 | 10.2497 | 19.9624
39016.5608 | 2301 | 0 | 39016.5608 | 2286 | 0 |  | 1140.5 | 1285.5 | 140.4762 | 0 | 139.5604 | 0 | 1.4048 | 0 | 1.3956 | 0 | 1.4048 | 1.3956 | 12.837 | 13.5774 | 11.4323
39016.563 | 2128 | 0 | 39016.563 | 2207 | 0 |  | 1325 | 1470 | 129.9145 | 0 | 134.7375 | 0 | 1.2991 | 0 | 1.3474 | 0 | 1.2991 | 1.3474 | 22.0103 | 17.643 | 20.7112
39016.5651 | 2017 | 0 | 39016.5651 | 2110 | 0 |  | 1510 | 1655 | 123.138 | 0 | 128.8156 | 0 | 1.2314 | 0 | 1.2882 | 0 | 1.2314 | 1.2882 | 28.7248 | 23.0512 | 27.4935

## E9-F12
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 152.16 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39016.548 | 1 | 0 | 39016.548 | 1 | 0 |  | 29 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39016.5501 | 1 | 0 | 39016.5501 | 1 | 0 |  | 213.5 | 358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249138 | 249138 | 249137.9994
39016.5522 | 2468 | 0 | 39016.5522 | 1078 | 0 |  | 398.5 | 543.5 | 150.6716 | 0 | 65.812 | 0 | 1.5067 | 0 | 0.65812 | 0 | 1.5067 | 0.65812 | 0.98784 | 131.2041 | 0.51887
39016.5544 | 2461 | 0 | 39016.5544 | 2476 | 0 |  | 583.5 | 728.5 | 150.2442 | 0 | 151.16 | 0 | 1.5024 | 0 | 1.5116 | 0 | 1.5024 | 1.5116 | 1.2751 | 0.66155 | 0.22735
39016.5565 | 2358 | 0 | 39016.5565 | 2435 | 0 |  | 768 | 913 | 143.956 | 0 | 148.6569 | 0 | 1.4396 | 0 | 1.4866 | 0 | 1.4396 | 1.4866 | 5.6989 | 2.3565 | 4.2593
39016.5586 | 2195 | 0 | 39016.5587 | 2445 | 0 |  | 952.5 | 1097.5 | 134.0049 | 0 | 149.2674 | 0 | 1.34 | 0 | 1.4927 | 0 | 1.34 | 1.4927 | 13.5481 | 1.9378 | 12.208
39016.5608 | 2315 | 0 | 39016.5608 | 2188 | 0 |  | 1137.5 | 1282.5 | 141.3309 | 0 | 133.5775 | 0 | 1.4133 | 0 | 1.3358 | 0 | 1.4133 | 1.3358 | 7.6622 | 13.9113 | 6.2489
39016.5629 | 2457 | 0 | 39016.5629 | 2200 | 0 |  | 1322.5 | 1467.5 | 150 | 0 | 134.3101 | 0 | 1.5 | 0 | 1.3431 | 0 | 1.5 | 1.3431 | 1.44 | 13.29 | 0.060033
39016.5651 | 2044 | 0 | 39016.5651 | 2041 | 0 |  | 1507 | 1652 | 124.7863 | 0 | 124.6032 | 0 | 1.2479 | 0 | 1.246 | 0 | 1.2479 | 1.246 | 21.9364 | 22.1156 | 20.6885

## E9-F11
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 160.1575 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39016.5479 | 1 | 0 | 39016.5479 | 1 | 0 |  | 26 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39016.5501 | 1 | 0 | 39016.5501 | 1 | 0 |  | 210.5 | 355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39016.5522 | 2074 | 0 | 39016.5522 | 604 | 0 |  | 395.5 | 540.5 | 126.6178 | 0 | 36.8742 | 0 | 1.2662 | 0 | 0.36874 | 0 | 1.2662 | 0.36874 | 26.4889 | 334.3344 | 25.2227
39016.5543 | 2388 | 0 | 39016.5544 | 2542 | 0 |  | 580.5 | 725.5 | 145.7875 | 0 | 155.1893 | 0 | 1.4579 | 0 | 1.5519 | 0 | 1.4579 | 1.5519 | 9.8568 | 3.2014 | 8.3989
39016.5565 | 2332 | 0 | 39016.5565 | 2587 | 0 |  | 765 | 910 | 142.3687 | 0 | 157.9365 | 0 | 1.4237 | 0 | 1.5794 | 0 | 1.4237 | 1.5794 | 12.4949 | 1.4063 | 11.0712
39016.5586 | 2184 | 0 | 39016.5586 | 2607 | 0 |  | 950 | 1095 | 133.3333 | 0 | 159.1575 | 0 | 1.3333 | 0 | 1.5916 | 0 | 1.3333 | 1.5916 | 20.1181 | 0.62831 | 18.7848
39016.5608 | 2370 | 0 | 39016.5608 | 2230 | 0 |  | 1134.5 | 1279.5 | 144.6886 | 0 | 136.1416 | 0 | 1.4469 | 0 | 1.3614 | 0 | 1.4469 | 1.3614 | 10.6911 | 17.6404 | 9.2443
39016.5629 | 2470 | 0 | 39016.5629 | 2194 | 0 |  | 1319.5 | 1464.5 | 150.7937 | 0 | 133.9438 | 0 | 1.5079 | 0 | 1.3394 | 0 | 1.5079 | 1.3394 | 6.2097 | 19.5706 | 4.7018
39016.565 | 2053 | 0 | 39016.565 | 1925 | 0 |  | 1504.5 | 1649.5 | 125.3358 | 0 | 117.5214 | 0 | 1.2534 | 0 | 1.1752 | 0 | 1.2534 | 1.1752 | 27.7828 | 36.2795 | 26.5294

## E9-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 159.547 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39016.5479 | 1 | 0 | 39016.5479 | 1 | 0 |  | 23 | 168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39016.55 | 1 | 0 | 39016.55 | 1 | 0 |  | 208 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261238 | 261238 | 261237.9994
39016.5522 | 2060 | 0 | 39016.5522 | 2388 | 0 |  | 393 | 538 | 125.7631 | 0 | 145.7875 | 0 | 1.2576 | 0 | 1.4579 | 0 | 1.2576 | 1.4579 | 26.8631 | 9.438 | 25.6055
39016.5543 | 2597 | 0 | 39016.5543 | 2552 | 0 |  | 577.5 | 722.5 | 158.547 | 0 | 155.7998 | 0 | 1.5855 | 0 | 1.558 | 0 | 1.5855 | 1.558 | 0.63073 | 2.4052 | 0.95474
39016.5564 | 2318 | 0 | 39016.5565 | 2500 | 0 |  | 762.5 | 907.5 | 141.514 | 0 | 152.6252 | 0 | 1.4151 | 0 | 1.5263 | 0 | 1.4151 | 1.5263 | 12.7429 | 4.5352 | 11.3277
39016.5586 | 2155 | 0 | 39016.5586 | 2449 | 0 |  | 947 | 1092 | 131.5629 | 0 | 149.5116 | 0 | 1.3156 | 0 | 1.4951 | 0 | 1.3156 | 1.4951 | 21.2705 | 6.7121 | 19.9549
39016.5607 | 2279 | 0 | 39016.5607 | 2152 | 0 |  | 1132 | 1277 | 139.1331 | 0 | 131.3797 | 0 | 1.3913 | 0 | 1.3138 | 0 | 1.3913 | 1.3138 | 14.6722 | 21.4396 | 13.2809
39016.5629 | 2019 | 0 | 39016.5629 | 2111 | 0 |  | 1316.5 | 1461.5 | 123.2601 | 0 | 128.8767 | 0 | 1.2326 | 0 | 1.2888 | 0 | 1.2326 | 1.2888 | 29.4393 | 23.7982 | 28.2067
39016.565 | 2293 | 0 | 39016.565 | 2578 | 0 |  | 1501.5 | 1646.5 | 139.9878 | 0 | 157.3871 | 0 | 1.3999 | 0 | 1.5739 | 0 | 1.3999 | 1.5739 | 13.9721 | 1.3724 | 12.5722

## D8-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 161.5617 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39016.5478 | 1 | 0 | 39016.5478 | 1 | 0 |  | 15 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39016.5499 | 1 | 0 | 39016.5499 | 1 | 0 |  | 199.5 | 344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39016.5521 | 1913 | 0 | 39016.5521 | 2517 | 0 |  | 384.5 | 529.5 | 116.7888 | 0 | 153.663 | 0 | 1.1679 | 0 | 1.5366 | 0 | 1.1679 | 1.5366 | 38.3366 | 5.1402 | 37.1688
39016.5542 | 1980 | 0 | 39016.5542 | 2160 | 0 |  | 569 | 714 | 120.8791 | 0 | 131.8681 | 0 | 1.2088 | 0 | 1.3187 | 0 | 1.2088 | 1.3187 | 33.6556 | 22.5176 | 32.4468
39016.5563 | 2196 | 0 | 39016.5564 | 2305 | 0 |  | 754 | 899 | 134.0659 | 0 | 140.7204 | 0 | 1.3407 | 0 | 1.4072 | 0 | 1.3407 | 1.4072 | 20.5091 | 14.8104 | 19.1684
39016.5585 | 2630 | 0 | 39016.5585 | 2488 | 0 |  | 938.5 | 1083.5 | 160.5617 | 0 | 151.8926 | 0 | 1.6056 | 0 | 1.5189 | 0 | 1.6056 | 1.5189 | 0.62281 | 6.3658 | 0.9828
39016.5606 | 2598 | 0 | 39016.5606 | 2123 | 0 |  | 1123.5 | 1268.5 | 158.6081 | 0 | 129.6093 | 0 | 1.5861 | 0 | 1.2961 | 0 | 1.5861 | 1.2961 | 1.8622 | 24.6528 | 0.27612
39016.5628 | 2152 | 0 | 39016.5628 | 2538 | 0 |  | 1308.5 | 1453.5 | 131.3797 | 0 | 154.9451 | 0 | 1.3138 | 0 | 1.5495 | 0 | 1.3138 | 1.5495 | 22.973 | 4.2703 | 21.6593
39016.5649 | 2063 | 0 | 39016.5649 | 2472 | 0 |  | 1493 | 1638 | 125.9463 | 0 | 150.9158 | 0 | 1.2595 | 0 | 1.5092 | 0 | 1.2595 | 1.5092 | 28.2782 | 7.0542 | 27.0188

## D8-E9
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 157.2271 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39016.5478 | 1 | 0 | 39016.5478 | 1 | 0 |  | 12 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
| 1 | 0 | 39016.5499 | 1 | 0 |  | 197 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257438 | 257438 | 257437.9994
39016.552 | 1899 | 0 | 39016.552 | 2110 | 0 |  | 381.5 | 526.5 | 115.9341 | 0 | 128.8156 | 0 | 1.1593 | 0 | 1.2882 | 0 | 1.1593 | 1.2882 | 35.6177 | 22.0559 | 34.4584
39016.5542 | 2245 | 0 | 39016.5542 | 2206 | 0 |  | 566.5 | 711.5 | 137.0574 | 0 | 134.6764 | 0 | 1.3706 | 0 | 1.3468 | 0 | 1.3706 | 1.3468 | 14.7163 | 16.7443 | 13.3457
39016.5563 | 2559 | 0 | 39016.5563 | 2264 | 0 |  | 751 | 896 | 156.2271 | 0 | 138.2173 | 0 | 1.5623 | 0 | 1.3822 | 0 | 1.5623 | 1.3822 | 0.64009 | 13.7535 | 0.92218
39016.5584 | 2025 | 0 | 39016.5585 | 2536 | 0 |  | 936 | 1081 | 123.6264 | 0 | 154.823 | 0 | 1.2363 | 0 | 1.5482 | 0 | 1.2363 | 1.5482 | 27.1793 | 1.5528 | 25.943
39016.5606 | 2239 | 0 | 39016.5606 | 2397 | 0 |  | 1120.5 | 1265.5 | 136.6911 | 0 | 146.337 | 0 | 1.3669 | 0 | 1.4634 | 0 | 1.3669 | 1.4634 | 15.0237 | 7.4418 | 13.6568
39016.5627 | 2504 | 0 | 39016.5627 | 2038 | 0 |  | 1305.5 | 1450.5 | 152.8694 | 0 | 124.42 | 0 | 1.5287 | 0 | 1.2442 | 0 | 1.5287 | 1.2442 | 2.8506 | 26.368 | 1.3219
39016.5649 | 2163 | 0 | 39016.5649 | 2291 | 0 |  | 1490.5 | 1635.5 | 132.0513 | 0 | 139.8657 | 0 | 1.3205 | 0 | 1.3987 | 0 | 1.3205 | 1.3987 | 19.0652 | 12.4129 | 17.7447

## D7-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 155.4567 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39016.5477 | 1 | 0 | 39016.5477 | 1 | 0 |  | 3.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
39016.5498 | 1 | 0 | 39016.5498 | 1 | 0 |  | 188.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254538 | 254538 | 254537.9994
39016.5519 | 756 | 0 | 39016.552 | 2157 | 0 |  | 373 | 518 | 46.1538 | 0 | 131.685 | 0 | 0.46154 | 0 | 1.3168 | 0 | 0.46154 | 1.3168 | 236.8228 | 18.0519 | 236.3612
39016.5541 | 2358 | 0 | 39016.5541 | 2496 | 0 |  | 558 | 703 | 143.956 | 0 | 152.381 | 0 | 1.4396 | 0 | 1.5238 | 0 | 1.4396 | 1.5238 | 7.989 | 2.0184 | 6.5494
39016.5562 | 2021 | 0 | 39016.5562 | 2523 | 0 |  | 742.5 | 887.5 | 123.3822 | 0 | 154.0293 | 0 | 1.2338 | 0 | 1.5403 | 0 | 1.2338 | 1.5403 | 25.996 | 0.92667 | 24.7622
39016.5584 | 2247 | 0 | 39016.5584 | 2139 | 0 |  | 927.5 | 1072.5 | 137.1795 | 0 | 130.5861 | 0 | 1.3718 | 0 | 1.3059 | 0 | 1.3718 | 1.3059 | 13.3235 | 19.0453 | 11.9517
39016.5605 | 2530 | 0 | 39016.5605 | 2389 | 0 |  | 1112.5 | 1257.5 | 154.4567 | 0 | 145.8486 | 0 | 1.5446 | 0 | 1.4585 | 0 | 1.5446 | 1.4585 | 0.64743 | 6.5877 | 0.89714
39016.5626 | 2497 | 0 | 39016.5627 | 2069 | 0 |  | 1297 | 1442 | 152.442 | 0 | 126.3126 | 0 | 1.5244 | 0 | 1.2631 | 0 | 1.5244 | 1.2631 | 1.9776 | 23.073 | 0.45315
39016.5648 | 2452 | 0 | 39016.5648 | 2369 | 0 |  | 1482 | 1627 | 149.6947 | 0 | 144.6276 | 0 | 1.4969 | 0 | 1.4463 | 0 | 1.4969 | 1.4463 | 3.8491 | 7.4875 | 2.3522

## D7-E9
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 159.9133 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39016.5476 | 1 | 0 | 39016.5476 | 1 | 0 |  | 0.5 | 145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39016.5498 | 1 | 0 | 39016.5498 | 1 | 0 |  | 185.5 | 330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39016.5519 | 151 | 0 | 39016.5519 | 1869 | 0 |  | 370.5 | 515.5 | 9.2186 | 0 | 114.1026 | 0 | 0.092186 | 0 | 1.141 | 0 | 0.092186 | 1.141 | 1634.6887 | 40.1487 | 1634.5966
39016.554 | 2076 | 0 | 39016.5541 | 2280 | 0 |  | 555 | 700 | 126.7399 | 0 | 139.1941 | 0 | 1.2674 | 0 | 1.3919 | 0 | 1.2674 | 1.3919 | 26.1744 | 14.8851 | 24.907
39016.5562 | 2002 | 0 | 39016.5562 | 2100 | 0 |  | 740 | 885 | 122.2222 | 0 | 128.2051 | 0 | 1.2222 | 0 | 1.2821 | 0 | 1.2222 | 1.2821 | 30.8382 | 24.7324 | 29.6159
39016.5583 | 2547 | 0 | 39016.5583 | 2603 | 0 |  | 924.5 | 1069.5 | 155.4945 | 0 | 158.9133 | 0 | 1.5549 | 0 | 1.5891 | 0 | 1.5549 | 1.5891 | 2.8418 | 0.62927 | 1.2868
39016.5605 | 2157 | 0 | 39016.5605 | 2467 | 0 |  | 1109.5 | 1254.5 | 131.685 | 0 | 150.6105 | 0 | 1.3168 | 0 | 1.5061 | 0 | 1.3168 | 1.5061 | 21.4363 | 6.1767 | 20.1194
39016.5626 | 2078 | 0 | 39016.5626 | 2221 | 0 |  | 1294.5 | 1439.5 | 126.862 | 0 | 135.5922 | 0 | 1.2686 | 0 | 1.3559 | 0 | 1.2686 | 1.3559 | 26.0529 | 17.937 | 24.7843
39016.5647 | 2007 | 0 | 39016.5648 | 2273 | 0 |  | 1479 | 1624 | 122.5275 | 0 | 138.7668 | 0 | 1.2253 | 0 | 1.3877 | 0 | 1.2253 | 1.3877 | 30.5122 | 15.2389 | 29.2869

## D7-D8
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 159.486 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39016.5476 | 1 | 0 | 39016.5476 | 1 | 0 |  | -2 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261138 | 261138 | 261137.9994
39016.5497 | 1 | 0 | 39016.5498 | 1 | 0 |  | 183 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261138 | 261138 | 261137.9994
39016.5519 | 998 | 843 | 39016.5519 | 1020 | 770 |  | 367.5 | 512.5 | 60.928 | 51.4652 | 62.2711 | 47.0085 | 0.60928 | 0.51465 | 0.62271 | 0.47009 | 0.094628 | 0.15263 | 5327.5715 | 676.0353 | 79.7129
39016.554 | 2421 | 0 | 39016.554 | 2568 | 0 |  | 552.5 | 697.5 | 147.8022 | 0 | 156.7766 | 0 | 1.478 | 0 | 1.5678 | 0 | 1.478 | 1.5678 | 7.905 | 1.7282 | 6.427
39016.5561 | 2596 | 0 | 39016.5562 | 2543 | 0 |  | 737 | 882 | 158.486 | 0 | 155.2503 | 0 | 1.5849 | 0 | 1.5525 | 0 | 1.5849 | 1.5525 | 0.63097 | 2.7283 | 0.95389
39016.5583 | 2061 | 0 | 39016.5583 | 2484 | 0 |  | 922 | 1067 | 125.8242 | 0 | 151.6484 | 0 | 1.2582 | 0 | 1.5165 | 0 | 1.2582 | 1.5165 | 26.753 | 5.1683 | 25.4948
39016.5604 | 2435 | 0 | 39016.5604 | 2187 | 0 |  | 1106.5 | 1251.5 | 148.6569 | 0 | 133.5165 | 0 | 1.4866 | 0 | 1.3352 | 0 | 1.4866 | 1.3352 | 7.2846 | 19.4504 | 5.798
39016.5626 | 1983 | 0 | 39016.5626 | 2096 | 0 |  | 1291.5 | 1436.5 | 121.0623 | 0 | 127.9609 | 0 | 1.2106 | 0 | 1.2796 | 0 | 1.2106 | 1.2796 | 31.7388 | 24.6365 | 30.5282
39016.5647 | 1957 | 114 | 39016.5647 | 1947 | 110 |  | 1476.5 | 1621.5 | 119.475 | 6.9597 | 118.8645 | 6.7155 | 1.1947 | 0.069597 | 1.1886 | 0.067155 | 1.1252 | 1.1215 | 41.6507 | 42.3028 | 141.1734

## C6-F12
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 157.4713 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39016.5476 | 1 | 0 | 39016.5476 | 1 | 0 |  | -4.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
39016.5497 | 1 | 0 | 39016.5497 | 1 | 0 |  | 180 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
39016.5518 | 1 | 0 | 39016.5519 | 1 | 0 |  | 365 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
39016.554 | 1 | 0 | 39016.554 | 2204 | 0 |  | 549.5 | 694.5 | 0.06105 | 0 | 134.5543 | 0 | 0.0006105 | 0 | 1.3455 | 0 | 0.0006105 | 1.3455 | 257838 | 17.0318 | 257837.9994
39016.5561 | 1680 | 0 | 39016.5561 | 2338 | 0 |  | 734.5 | 879.5 | 102.5641 | 0 | 142.735 | 0 | 1.0256 | 0 | 1.4274 | 0 | 1.0256 | 1.4274 | 53.5345 | 10.3242 | 52.5089
39016.5583 | 2371 | 0 | 39016.5583 | 2163 | 0 |  | 919 | 1064 | 144.7497 | 0 | 132.0513 | 0 | 1.4475 | 0 | 1.3205 | 0 | 1.4475 | 1.3205 | 8.7887 | 19.2501 | 7.3412
39016.5604 | 2519 | 0 | 39016.5604 | 2328 | 0 |  | 1104 | 1249 | 153.7851 | 0 | 142.1245 | 0 | 1.5379 | 0 | 1.4212 | 0 | 1.5379 | 1.4212 | 2.397 | 10.7981 | 0.85913
39016.5625 | 1980 | 0 | 39016.5625 | 2563 | 0 |  | 1288.5 | 1433.5 | 120.8791 | 0 | 156.4713 | 0 | 1.2088 | 0 | 1.5647 | 0 | 1.2088 | 1.5647 | 30.2717 | 0.63909 | 29.0629
39016.5647 | 1826 | 0 | 39016.5647 | 2049 | 0 |  | 1473.5 | 1618.5 | 111.4774 | 0 | 125.0916 | 0 | 1.1148 | 0 | 1.2509 | 0 | 1.1148 | 1.2509 | 41.2585 | 25.8848 | 40.1437

## C6-F11
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 157.4713 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39016.5475 | 0 | 0 | 39016.5475 | 1 | 0 |  | -7.5 | 137.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 515776 | 257838 | 515775.9997
39016.5497 | 1 | 0 | 39016.5497 | 1 | 0 |  | 177.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257838 | 257838 | 257837.9994
39016.5518 | 1 | 0 | 39016.5518 | 40 | 0 |  | 362 | 507 | 0.06105 | 0 | 2.442 | 0 | 0.0006105 | 0 | 0.02442 | 0 | 0.0006105 | 0.02442 | 257838 | 6348.45 | 257837.9994
39016.5539 | 1 | 0 | 39016.554 | 2541 | 0 |  | 546.5 | 691.5 | 0.06105 | 0 | 155.1282 | 0 | 0.0006105 | 0 | 1.5513 | 0 | 0.0006105 | 1.5513 | 257838 | 1.5104 | 257837.9994
39016.5561 | 1746 | 0 | 39016.5561 | 2563 | 0 |  | 731.5 | 876.5 | 106.5934 | 0 | 156.4713 | 0 | 1.0659 | 0 | 1.5647 | 0 | 1.0659 | 1.5647 | 47.7308 | 0.63909 | 46.6649
39016.5582 | 2215 | 0 | 39016.5582 | 2095 | 0 |  | 916.5 | 1061.5 | 135.2259 | 0 | 127.8999 | 0 | 1.3523 | 0 | 1.279 | 0 | 1.3523 | 1.279 | 16.4506 | 23.1208 | 15.0983
39016.5604 | 2511 | 0 | 39016.5604 | 2034 | 0 |  | 1101 | 1246 | 153.2967 | 0 | 124.1758 | 0 | 1.533 | 0 | 1.2418 | 0 | 1.533 | 1.2418 | 2.7232 | 26.8132 | 1.1903
39016.5625 | 2277 | 0 | 39016.5625 | 2260 | 0 |  | 1286 | 1431 | 139.011 | 0 | 137.9731 | 0 | 1.3901 | 0 | 1.3797 | 0 | 1.3901 | 1.3797 | 13.2798 | 14.1319 | 11.8896
39016.5646 | 1767 | 0 | 39016.5647 | 2095 | 0 |  | 1470.5 | 1615.5 | 107.8755 | 0 | 127.8999 | 0 | 1.0788 | 0 | 1.279 | 0 | 1.0788 | 1.279 | 45.9751 | 23.1208 | 44.8963

## C6-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 161.1343 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39016.5475 | 1 | 0 | 39016.5475 | 1 | 0 |  | -10.5 | 134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.5496 | 1 | 0 | 39016.5497 | 1 | 0 |  | 174.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.5518 | 1 | 0 | 39016.5518 | 2548 | 0 |  | 359 | 504 | 0.06105 | 0 | 155.5556 | 0 | 0.0006105 | 0 | 1.5556 | 0 | 0.0006105 | 1.5556 | 263838 | 3.5863 | 263837.9994
39016.5539 | 1 | 0 | 39016.5539 | 2532 | 0 |  | 544 | 689 | 0.06105 | 0 | 154.5788 | 0 | 0.0006105 | 0 | 1.5458 | 0 | 0.0006105 | 1.5458 | 263838 | 4.2409 | 263837.9994
39016.5561 | 2307 | 0 | 39016.5561 | 2525 | 0 |  | 728.5 | 873.5 | 140.8425 | 0 | 154.1514 | 0 | 1.4084 | 0 | 1.5415 | 0 | 1.4084 | 1.5415 | 14.4075 | 4.5299 | 12.999
39016.5582 | 1959 | 0 | 39016.5582 | 2151 | 0 |  | 913.5 | 1058.5 | 119.5971 | 0 | 131.3187 | 0 | 1.196 | 0 | 1.3132 | 0 | 1.196 | 1.3132 | 34.731 | 22.7048 | 33.535
39016.5603 | 2139 | 0 | 39016.5603 | 2431 | 0 |  | 1098.5 | 1243.5 | 130.5861 | 0 | 148.4127 | 0 | 1.3059 | 0 | 1.4841 | 0 | 1.3059 | 1.4841 | 23.3932 | 8.5718 | 22.0873
39016.5625 | 1930 | 0 | 39016.5625 | 2623 | 0 |  | 1283 | 1428 | 117.8266 | 0 | 160.1343 | 0 | 1.1783 | 0 | 1.6013 | 0 | 1.1783 | 1.6013 | 36.7554 | 0.62448 | 35.5772
39016.5646 | 2259 | 0 | 39016.5646 | 2605 | 0 |  | 1467.5 | 1612.5 | 137.9121 | 0 | 159.0354 | 0 | 1.3791 | 0 | 1.5904 | 0 | 1.3791 | 1.5904 | 16.8384 | 1.3198 | 15.4593

## C6-E9
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 161.5617 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39016.5475 | 1 | 0 | 39016.5475 | 1 | 0 |  | -13 | 132 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39016.5496 | 1 | 0 | 39016.5496 | 1 | 0 |  | 171.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264538 | 264538 | 264537.9994
39016.5517 | 1 | 0 | 39016.5518 | 2213 | 0 |  | 356.5 | 501.5 | 0.06105 | 0 | 135.1038 | 0 | 0.0006105 | 0 | 1.351 | 0 | 0.0006105 | 1.351 | 264538 | 19.5834 | 264537.9994
39016.5539 | 1 | 0 | 39016.5539 | 2354 | 0 |  | 541 | 686 | 0.06105 | 0 | 143.7118 | 0 | 0.0006105 | 0 | 1.4371 | 0 | 0.0006105 | 1.4371 | 264538 | 12.4206 | 264537.9994
39016.556 | 1421 | 0 | 39016.556 | 2172 | 0 |  | 726 | 871 | 86.7521 | 0 | 132.6007 | 0 | 0.86752 | 0 | 1.326 | 0 | 0.86752 | 1.326 | 86.2336 | 21.8407 | 85.3661
39016.5582 | 2193 | 0 | 39016.5582 | 2630 | 0 |  | 910.5 | 1055.5 | 133.8828 | 0 | 160.5617 | 0 | 1.3388 | 0 | 1.6056 | 0 | 1.3388 | 1.6056 | 20.674 | 0.62281 | 19.3351
39016.5603 | 2517 | 0 | 39016.5603 | 2615 | 0 |  | 1095.5 | 1240.5 | 153.663 | 0 | 159.6459 | 0 | 1.5366 | 0 | 1.5965 | 0 | 1.5366 | 1.5965 | 5.1402 | 1.2 | 3.6036
39016.5624 | 1881 | 0 | 39016.5625 | 2045 | 0 |  | 1280.5 | 1425.5 | 114.8352 | 0 | 124.8474 | 0 | 1.1484 | 0 | 1.2485 | 0 | 1.1484 | 1.2485 | 40.6901 | 29.4073 | 39.5417
39016.5646 | 1921 | 0 | 39016.5646 | 2435 | 0 |  | 1465 | 1610 | 117.2772 | 0 | 148.6569 | 0 | 1.1728 | 0 | 1.4866 | 0 | 1.1728 | 1.4866 | 37.7605 | 8.6809 | 36.5878

## C5-F12
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 158.326 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39016.5474 | 0 | 0 | 39016.5474 | 0 | 0 |  | -21.5 | 123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518576 | 518576 | 518575.9997
39016.5495 | 1 | 0 | 39016.5495 | 1 | 0 |  | 163 | 308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
39016.5516 | 1 | 0 | 39016.5517 | 1 | 0 |  | 348 | 493 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259238 | 259238 | 259237.9994
39016.5538 | 1 | 0 | 39016.5538 | 2399 | 0 |  | 533 | 678 | 0.06105 | 0 | 146.4591 | 0 | 0.0006105 | 0 | 1.4646 | 0 | 0.0006105 | 1.4646 | 259238 | 8.1025 | 259237.9994
39016.5559 | 2104 | 0 | 39016.5559 | 2560 | 0 |  | 717.5 | 862.5 | 128.4493 | 0 | 156.2882 | 0 | 1.2845 | 0 | 1.5629 | 0 | 1.2845 | 1.5629 | 23.2595 | 1.3039 | 21.975
39016.5581 | 2577 | 0 | 39016.5581 | 2066 | 0 |  | 902.5 | 1047.5 | 157.326 | 0 | 126.1294 | 0 | 1.5733 | 0 | 1.2613 | 0 | 1.5733 | 1.2613 | 0.63562 | 25.5266 | 0.93764
39016.5602 | 2508 | 0 | 39016.5602 | 2453 | 0 |  | 1087 | 1232 | 153.1136 | 0 | 149.7558 | 0 | 1.5311 | 0 | 1.4976 | 0 | 1.5311 | 1.4976 | 3.4043 | 5.7228 | 1.8732
39016.5623 | 2176 | 0 | 39016.5624 | 2400 | 0 |  | 1272 | 1417 | 132.8449 | 0 | 146.5201 | 0 | 1.3284 | 0 | 1.4652 | 0 | 1.3284 | 1.4652 | 19.1811 | 8.0575 | 17.8526
39016.5645 | 2173 | 0 | 39016.5645 | 2050 | 0 |  | 1456.5 | 1601.5 | 132.6618 | 0 | 125.1526 | 0 | 1.3266 | 0 | 1.2515 | 0 | 1.3266 | 1.2515 | 19.3456 | 26.5063 | 18.019

## C5-F11
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 157.5324 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39016.5473 | 1 | 0 | 39016.5473 | 1 | 0 |  | -24.5 | 120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39016.5495 | 1 | 0 | 39016.5495 | 1 | 0 |  | 160.5 | 305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39016.5516 | 1 | 0 | 39016.5516 | 1 | 0 |  | 345 | 490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257938 | 257938 | 257937.9994
39016.5537 | 1 | 0 | 39016.5538 | 2564 | 0 |  | 530 | 675 | 0.06105 | 0 | 156.5324 | 0 | 0.0006105 | 0 | 1.5653 | 0 | 0.0006105 | 1.5653 | 257938 | 0.63885 | 257937.9994
39016.5559 | 2163 | 0 | 39016.5559 | 2005 | 0 |  | 714.5 | 859.5 | 132.0513 | 0 | 122.4054 | 0 | 1.3205 | 0 | 1.2241 | 0 | 1.3205 | 1.2241 | 19.2963 | 28.6973 | 17.9758
39016.558 | 2163 | 0 | 39016.558 | 2083 | 0 |  | 899.5 | 1044.5 | 132.0513 | 0 | 127.1673 | 0 | 1.3205 | 0 | 1.2717 | 0 | 1.3205 | 1.2717 | 19.2963 | 23.8781 | 17.9758
39016.5602 | 2549 | 0 | 39016.5602 | 2083 | 0 |  | 1084.5 | 1229.5 | 155.6166 | 0 | 127.1673 | 0 | 1.5562 | 0 | 1.2717 | 0 | 1.5562 | 1.2717 | 1.2311 | 23.8781 | 0.3251
39016.5623 | 2172 | 0 | 39016.5623 | 2155 | 0 |  | 1269 | 1414 | 132.6007 | 0 | 131.5629 | 0 | 1.326 | 0 | 1.3156 | 0 | 1.326 | 1.3156 | 18.802 | 19.7392 | 17.476
39016.5644 | 1971 | 0 | 39016.5645 | 2117 | 0 |  | 1454 | 1599 | 120.3297 | 0 | 129.243 | 0 | 1.2033 | 0 | 1.2924 | 0 | 1.2033 | 1.2924 | 30.9173 | 21.8885 | 29.714

## C5-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 159.1807 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39016.5473 | 1 | 0 | 39016.5473 | 1 | 0 |  | -27 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39016.5494 | 1 | 0 | 39016.5495 | 1 | 0 |  | 157.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260638 | 260638 | 260637.9994
39016.5516 | 1 | 0 | 39016.5516 | 2561 | 0 |  | 342.5 | 487.5 | 0.06105 | 0 | 156.3492 | 0 | 0.0006105 | 0 | 1.5635 | 0 | 0.0006105 | 1.5635 | 260638 | 1.811 | 260637.9994
39016.5537 | 1 | 0 | 39016.5537 | 2591 | 0 |  | 527 | 672 | 0.06105 | 0 | 158.1807 | 0 | 0.0006105 | 0 | 1.5818 | 0 | 0.0006105 | 1.5818 | 260638 | 0.63219 | 260637.9994
39016.5559 | 2117 | 0 | 39016.5559 | 2100 | 0 |  | 712 | 857 | 129.243 | 0 | 128.2051 | 0 | 1.2924 | 0 | 1.2821 | 0 | 1.2924 | 1.2821 | 23.1639 | 24.161 | 21.8715
39016.558 | 2143 | 0 | 39016.558 | 2127 | 0 |  | 896.5 | 1041.5 | 130.8303 | 0 | 129.8535 | 0 | 1.3083 | 0 | 1.2985 | 0 | 1.3083 | 1.2985 | 21.6696 | 22.5849 | 20.3613
39016.5601 | 2264 | 0 | 39016.5602 | 2382 | 0 |  | 1081.5 | 1226.5 | 138.2173 | 0 | 145.4212 | 0 | 1.3822 | 0 | 1.4542 | 0 | 1.3822 | 1.4542 | 15.167 | 9.4618 | 13.7848
39016.5623 | 2219 | 0 | 39016.5623 | 2444 | 0 |  | 1266.5 | 1411.5 | 135.4701 | 0 | 149.2063 | 0 | 1.3547 | 0 | 1.4921 | 0 | 1.3547 | 1.4921 | 17.5025 | 6.6849 | 16.1478
39016.5644 | 1902 | 0 | 39016.5644 | 2175 | 0 |  | 1451 | 1596 | 116.1172 | 0 | 132.7839 | 0 | 1.1612 | 0 | 1.3278 | 0 | 1.1612 | 1.3278 | 37.0862 | 19.8795 | 35.9251

## C5-E9
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 161.1343 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39016.5473 | 1 | 0 | 39016.5473 | 1 | 0 |  | -30 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.5494 | 1 | 0 | 39016.5494 | 1 | 0 |  | 155 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.5516 | 1 | 0 | 39016.5516 | 1270 | 0 |  | 339.5 | 484.5 | 0.06105 | 0 | 77.5336 | 0 | 0.0006105 | 0 | 0.77534 | 0 | 0.0006105 | 0.77534 | 263838 | 107.8252 | 263837.9994
39016.5537 | 1 | 0 | 39016.5537 | 2608 | 0 |  | 524.5 | 669.5 | 0.06105 | 0 | 159.2186 | 0 | 0.0006105 | 0 | 1.5922 | 0 | 0.0006105 | 1.5922 | 263838 | 1.2032 | 263837.9994
39016.5558 | 2310 | 0 | 39016.5558 | 2316 | 0 |  | 709 | 854 | 141.0256 | 0 | 141.3919 | 0 | 1.4103 | 0 | 1.4139 | 0 | 1.4103 | 1.4139 | 14.2589 | 13.9629 | 12.8486
39016.558 | 2448 | 0 | 39016.558 | 2623 | 0 |  | 894 | 1039 | 149.4505 | 0 | 160.1343 | 0 | 1.4945 | 0 | 1.6013 | 0 | 1.4945 | 1.6013 | 7.8178 | 0.62448 | 6.3233
39016.5601 | 2052 | 0 | 39016.5601 | 2023 | 0 |  | 1078.5 | 1223.5 | 125.2747 | 0 | 123.5043 | 0 | 1.2527 | 0 | 1.235 | 0 | 1.2527 | 1.235 | 28.6248 | 30.4686 | 27.372
39016.5622 | 1927 | 0 | 39016.5623 | 2547 | 0 |  | 1263.5 | 1408.5 | 117.6435 | 0 | 155.4945 | 0 | 1.1764 | 0 | 1.5549 | 0 | 1.1764 | 1.5549 | 36.9683 | 3.627 | 35.7919
39016.5644 | 1806 | 0 | 39016.5644 | 2024 | 0 |  | 1448.5 | 1593.5 | 110.2564 | 0 | 123.5653 | 0 | 1.1026 | 0 | 1.2357 | 0 | 1.1026 | 1.2357 | 46.1451 | 30.4042 | 45.0425

## C5-C6
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 155.3956 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39016.5472 | 1 | 0 | 39016.5472 | 1 | 0 |  | -38.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
39016.5493 | 1 | 0 | 39016.5493 | 1 | 0 |  | 146.5 | 291.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
39016.5514 | 1 | 0 | 39016.5515 | 1 | 0 |  | 331 | 476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
39016.5536 | 1 | 0 | 39016.5536 | 1 | 0 |  | 516 | 661 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254438 | 254438 | 254437.9994
39016.5557 | 1831 | 211 | 39016.5557 | 1993 | 152 |  | 700.5 | 845.5 | 111.7827 | 12.8816 | 121.6728 | 9.2796 | 1.1178 | 0.12882 | 1.2167 | 0.092796 | 0.98901 | 1.1239 | 71.5904 | 33.9158 | 60.4204
39016.5579 | 2413 | 0 | 39016.5579 | 2529 | 0 |  | 885.5 | 1030.5 | 147.3138 | 0 | 154.3956 | 0 | 1.4731 | 0 | 1.544 | 0 | 1.4731 | 1.544 | 5.4861 | 0.64769 | 4.013
39016.56 | 2524 | 0 | 39016.56 | 2149 | 0 |  | 1070.5 | 1215.5 | 154.0904 | 0 | 131.1966 | 0 | 1.5409 | 0 | 1.312 | 0 | 1.5409 | 1.312 | 0.84707 | 18.4449 | 0.69384
39016.5621 | 2393 | 0 | 39016.5622 | 2431 | 0 |  | 1255 | 1400 | 146.0928 | 0 | 148.4127 | 0 | 1.4609 | 0 | 1.4841 | 0 | 1.4609 | 1.4841 | 6.3677 | 4.7051 | 4.9068
39016.5643 | 2254 | 0 | 39016.5643 | 2091 | 0 |  | 1440 | 1585 | 137.6068 | 0 | 127.6557 | 0 | 1.3761 | 0 | 1.2766 | 0 | 1.3761 | 1.2766 | 12.9272 | 21.7303 | 11.5512

## B4-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 156.0672 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39016.5471 | 1 | 0 | 39016.5471 | 1 | 0 |  | -46.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39016.5492 | 1 | 0 | 39016.5492 | 1 | 0 |  | 138 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255538 | 255538 | 255537.9994
39016.5514 | 1 | 0 | 39016.5514 | 2110 | 0 |  | 322.5 | 467.5 | 0.06105 | 0 | 128.8156 | 0 | 0.0006105 | 0 | 1.2882 | 0 | 0.0006105 | 1.2882 | 255538 | 21.1555 | 255537.9994
39016.5535 | 1 | 0 | 39016.5535 | 2540 | 0 |  | 507.5 | 652.5 | 0.06105 | 0 | 155.0672 | 0 | 0.0006105 | 0 | 1.5507 | 0 | 0.0006105 | 1.5507 | 255538 | 0.64488 | 255537.9994
39016.5556 | 2028 | 0 | 39016.5556 | 2034 | 0 |  | 692.5 | 837.5 | 123.8095 | 0 | 124.1758 | 0 | 1.2381 | 0 | 1.2418 | 0 | 1.2381 | 1.2418 | 26.0542 | 25.6824 | 24.8161
39016.5578 | 2212 | 0 | 39016.5578 | 2407 | 0 |  | 877 | 1022 | 135.0427 | 0 | 146.9475 | 0 | 1.3504 | 0 | 1.4695 | 0 | 1.3504 | 1.4695 | 15.5687 | 6.2061 | 14.2183
39016.5599 | 2316 | 0 | 39016.5599 | 2410 | 0 |  | 1062 | 1207 | 141.3919 | 0 | 147.1306 | 0 | 1.4139 | 0 | 1.4713 | 0 | 1.4139 | 1.4713 | 10.3791 | 6.0739 | 8.9652
39016.562 | 2296 | 0 | 39016.5621 | 2334 | 0 |  | 1246.5 | 1391.5 | 140.1709 | 0 | 142.4908 | 0 | 1.4017 | 0 | 1.4249 | 0 | 1.4017 | 1.4249 | 11.3406 | 9.5278 | 9.9389
39016.5642 | 2032 | 0 | 39016.5642 | 2360 | 0 |  | 1431.5 | 1576.5 | 124.0537 | 0 | 144.0781 | 0 | 1.2405 | 0 | 1.4408 | 0 | 1.2405 | 1.4408 | 25.8061 | 8.3212 | 24.5656

## B4-E9
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 161.6227 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39016.547 | 1 | 0 | 39016.5471 | 1 | 0 |  | -49.5 | 95.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39016.5492 | 1 | 0 | 39016.5492 | 1 | 0 |  | 135 | 280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39016.5513 | 1 | 0 | 39016.5513 | 1727 | 0 |  | 320 | 465 | 0.06105 | 0 | 105.4335 | 0 | 0.0006105 | 0 | 1.0543 | 0 | 0.0006105 | 1.0543 | 264638 | 53.2936 | 264637.9994
39016.5535 | 1 | 0 | 39016.5535 | 2578 | 0 |  | 504.5 | 649.5 | 0.06105 | 0 | 157.3871 | 0 | 0.0006105 | 0 | 1.5739 | 0 | 0.0006105 | 1.5739 | 264638 | 2.6912 | 264637.9994
39016.5556 | 2048 | 0 | 39016.5556 | 2548 | 0 |  | 689.5 | 834.5 | 125.0305 | 0 | 155.5556 | 0 | 1.2503 | 0 | 1.5556 | 0 | 1.2503 | 1.5556 | 29.2666 | 3.9003 | 28.0163
39016.5577 | 2368 | 0 | 39016.5578 | 2198 | 0 |  | 874.5 | 1019.5 | 144.5665 | 0 | 134.188 | 0 | 1.4457 | 0 | 1.3419 | 0 | 1.4457 | 1.3419 | 11.7981 | 20.4449 | 10.3525
39016.5599 | 2374 | 0 | 39016.5599 | 2631 | 0 |  | 1059 | 1204 | 144.9328 | 0 | 160.6227 | 0 | 1.4493 | 0 | 1.6062 | 0 | 1.4493 | 1.6062 | 11.5156 | 0.62258 | 10.0663
39016.562 | 1875 | 0 | 39016.562 | 2371 | 0 |  | 1244 | 1389 | 114.4689 | 0 | 144.7497 | 0 | 1.1447 | 0 | 1.4475 | 0 | 1.1447 | 1.4475 | 41.1936 | 11.6567 | 40.0489
39016.5642 | 2153 | 0 | 39016.5642 | 2208 | 0 |  | 1428.5 | 1573.5 | 131.4408 | 0 | 134.7985 | 0 | 1.3144 | 0 | 1.348 | 0 | 1.3144 | 1.348 | 22.9624 | 19.8995 | 21.648

## B4-D8
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 157.6545 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39016.547 | 1 | 0 | 39016.547 | 1 | 0 |  | -52.5 | 92.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
39016.5492 | 1 | 0 | 39016.5492 | 1 | 0 |  | 132.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
39016.5513 | 1 | 0 | 39016.5513 | 1 | 0 |  | 317.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258138 | 258138 | 258137.9994
39016.5534 | 1 | 0 | 39016.5534 | 2428 | 0 |  | 502 | 647 | 0.06105 | 0 | 148.2295 | 0 | 0.0006105 | 0 | 1.4823 | 0 | 0.0006105 | 1.4823 | 258138 | 6.3583 | 258137.9994
39016.5556 | 2055 | 0 | 39016.5556 | 2566 | 0 |  | 686.5 | 831.5 | 125.4579 | 0 | 156.6545 | 0 | 1.2546 | 0 | 1.5665 | 0 | 1.2546 | 1.5665 | 25.6633 | 0.63835 | 24.4087
39016.5577 | 2092 | 0 | 39016.5577 | 2372 | 0 |  | 871.5 | 1016.5 | 127.7167 | 0 | 144.8107 | 0 | 1.2772 | 0 | 1.4481 | 0 | 1.2772 | 1.4481 | 23.4407 | 8.8693 | 22.1636
39016.5598 | 2315 | 0 | 39016.5599 | 2506 | 0 |  | 1056.5 | 1201.5 | 141.3309 | 0 | 152.9915 | 0 | 1.4133 | 0 | 1.5299 | 0 | 1.4133 | 1.5299 | 11.5499 | 3.0479 | 10.1366
39016.562 | 2164 | 0 | 39016.562 | 2032 | 0 |  | 1241 | 1386 | 132.1123 | 0 | 124.0537 | 0 | 1.3211 | 0 | 1.2405 | 0 | 1.3211 | 1.2405 | 19.3336 | 27.0856 | 18.0125
39016.5641 | 2331 | 0 | 39016.5641 | 2014 | 0 |  | 1426 | 1571 | 142.3077 | 0 | 122.9548 | 0 | 1.4231 | 0 | 1.2295 | 0 | 1.4231 | 1.2295 | 10.7842 | 28.2214 | 9.3611

## B4-D7
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 155.7009 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39016.547 | 1 | 0 | 39016.547 | 1 | 0 |  | -55 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
39016.5491 | 1 | 0 | 39016.5491 | 1 | 0 |  | 129.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
39016.5513 | 1 | 0 | 39016.5513 | 1 | 0 |  | 314.5 | 459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254938 | 254938 | 254937.9994
39016.5534 | 1 | 0 | 39016.5534 | 2195 | 0 |  | 499 | 644 | 0.06105 | 0 | 134.0049 | 0 | 0.0006105 | 0 | 1.34 | 0 | 0.0006105 | 1.34 | 254938 | 16.1904 | 254937.9994
39016.5555 | 2282 | 0 | 39016.5556 | 2144 | 0 |  | 684 | 829 | 139.3162 | 0 | 130.8913 | 0 | 1.3932 | 0 | 1.3089 | 0 | 1.3932 | 1.3089 | 11.7607 | 18.9543 | 10.3676
39016.5577 | 2534 | 0 | 39016.5577 | 2441 | 0 |  | 868.5 | 1013.5 | 154.7009 | 0 | 149.0232 | 0 | 1.547 | 0 | 1.4902 | 0 | 1.547 | 1.4902 | 0.64641 | 4.481 | 0.9006
39016.5598 | 2212 | 0 | 39016.5598 | 2110 | 0 |  | 1053.5 | 1198.5 | 135.0427 | 0 | 128.8156 | 0 | 1.3504 | 0 | 1.2882 | 0 | 1.3504 | 1.2882 | 15.2975 | 20.8711 | 13.947
39016.562 | 2421 | 0 | 39016.562 | 2311 | 0 |  | 1238.5 | 1383.5 | 147.8022 | 0 | 141.0867 | 0 | 1.478 | 0 | 1.4109 | 0 | 1.478 | 1.4109 | 5.3441 | 10.3583 | 3.8661
39016.5641 | 2183 | 0 | 39016.5641 | 1841 | 0 |  | 1423 | 1568 | 133.2723 | 0 | 112.3932 | 0 | 1.3327 | 0 | 1.1239 | 0 | 1.3327 | 1.1239 | 16.8291 | 38.5323 | 15.4964

## B4-C6
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 136.6532 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39016.5469 | 1 | 0 | 39016.547 | 1 | 0 |  | -58 | 87 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223738 | 223738 | 223737.9994
39016.5491 | 1 | 0 | 39016.5491 | 1 | 0 |  | 126.5 | 271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223738 | 223738 | 223737.9994
39016.5512 | 1 | 0 | 39016.5512 | 1 | 0 |  | 311.5 | 456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223738 | 223738 | 223737.9994
39016.5534 | 1 | 0 | 39016.5534 | 1 | 0 |  | 496.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 223738 | 223738 | 223737.9994
39016.5555 | 2222 | 0 | 39016.5555 | 1939 | 0 |  | 681 | 826 | 135.6532 | 0 | 118.3761 | 0 | 1.3565 | 0 | 1.1838 | 0 | 1.3565 | 1.1838 | 0.73717 | 15.4399 | 0.61936
39016.5576 | 2012 | 0 | 39016.5577 | 2121 | 0 |  | 866 | 1011 | 122.8327 | 0 | 129.4872 | 0 | 1.2283 | 0 | 1.2949 | 0 | 1.2283 | 1.2949 | 11.2515 | 5.5342 | 10.0232
39016.5598 | 2125 | 0 | 39016.5598 | 2013 | 0 |  | 1050.5 | 1195.5 | 129.7314 | 0 | 122.8938 | 0 | 1.2973 | 0 | 1.2289 | 0 | 1.2973 | 1.2289 | 5.3355 | 11.1962 | 4.0382
39016.5619 | 2017 | 0 | 39016.5619 | 1912 | 0 |  | 1235.5 | 1380.5 | 123.138 | 0 | 116.7277 | 0 | 1.2314 | 0 | 1.1673 | 0 | 1.2314 | 1.1673 | 10.9757 | 17.0701 | 9.7443
39016.5641 | 2041 | 0 | 39016.5641 | 1967 | 0 |  | 1420.5 | 1565.5 | 124.6032 | 0 | 120.0855 | 0 | 1.246 | 0 | 1.2009 | 0 | 1.246 | 1.2009 | 9.6707 | 13.7966 | 8.4247

## B4-C5
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 153.8694 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39016.5469 | 1 | 0 | 39016.5469 | 1 | 0 |  | -60.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39016.5491 | 1 | 0 | 39016.5491 | 1 | 0 |  | 124 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39016.5512 | 1 | 0 | 39016.5512 | 0 | 0 |  | 308.5 | 453.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 251938 | 503976 | 251937.9994
39016.5533 | 1 | 0 | 39016.5533 | 1 | 0 |  | 493.5 | 638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 251938 | 251938 | 251937.9994
39016.5555 | 1792 | 0 | 39016.5555 | 1831 | 0 |  | 678.5 | 823.5 | 109.4017 | 0 | 111.7827 | 0 | 1.094 | 0 | 1.1178 | 0 | 1.094 | 1.1178 | 40.6462 | 37.6505 | 39.5522
39016.5576 | 2276 | 0 | 39016.5576 | 2106 | 0 |  | 863 | 1008 | 138.9499 | 0 | 128.5714 | 0 | 1.3895 | 0 | 1.2857 | 0 | 1.3895 | 1.2857 | 10.7373 | 19.6762 | 9.3478
39016.5597 | 2504 | 0 | 39016.5598 | 2142 | 0 |  | 1048 | 1193 | 152.8694 | 0 | 130.7692 | 0 | 1.5287 | 0 | 1.3077 | 0 | 1.5287 | 1.3077 | 0.65415 | 17.6648 | 0.87454
39016.5619 | 2228 | 0 | 39016.5619 | 2174 | 0 |  | 1232.5 | 1377.5 | 136.0195 | 0 | 132.7228 | 0 | 1.3602 | 0 | 1.3272 | 0 | 1.3602 | 1.3272 | 13.123 | 15.9328 | 11.7628
39016.564 | 1801 | 0 | 39016.564 | 2216 | 0 |  | 1417.5 | 1562.5 | 109.9512 | 0 | 135.2869 | 0 | 1.0995 | 0 | 1.3529 | 0 | 1.0995 | 1.3529 | 39.9434 | 13.7356 | 38.8439

## B3-E10
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 157.3492 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39016.5468 | 1 | 0 | 39016.5468 | 1 | 0 |  | -69 | 76 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39016.549 | 1 | 0 | 39016.549 | 1 | 0 |  | 115.5 | 260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 257638 | 257638 | 257637.9994
39016.5511 | 1 | 0 | 39016.5511 | 578 | 0 |  | 300.5 | 445.5 | 0.06105 | 0 | 35.2869 | 0 | 0.0006105 | 0 | 0.35287 | 0 | 0.0006105 | 0.35287 | 257638 | 345.9135 | 257637.9994
39016.5532 | 1 | 0 | 39016.5533 | 2314 | 0 |  | 485.5 | 630.5 | 0.06105 | 0 | 141.2698 | 0 | 0.0006105 | 0 | 1.4127 | 0 | 0.0006105 | 1.4127 | 257638 | 11.382 | 257637.9994
39016.5554 | 1327 | 0 | 39016.5554 | 2325 | 0 |  | 670 | 815 | 81.0134 | 0 | 141.9414 | 0 | 0.81013 | 0 | 1.4194 | 0 | 0.81013 | 1.4194 | 94.2261 | 10.8551 | 93.4159
39016.5575 | 2367 | 0 | 39016.5575 | 2373 | 0 |  | 854.5 | 999.5 | 144.5055 | 0 | 144.8718 | 0 | 1.4451 | 0 | 1.4487 | 0 | 1.4451 | 1.4487 | 8.888 | 8.6127 | 7.443
39016.5597 | 2058 | 0 | 39016.5597 | 2561 | 0 |  | 1039.5 | 1184.5 | 125.641 | 0 | 156.3492 | 0 | 1.2564 | 0 | 1.5635 | 0 | 1.2564 | 1.5635 | 25.2371 | 0.63959 | 23.9807
39016.5618 | 2448 | 0 | 39016.5618 | 2457 | 0 |  | 1224.5 | 1369.5 | 149.4505 | 0 | 150 | 0 | 1.4945 | 0 | 1.5 | 0 | 1.4945 | 1.5 | 5.2851 | 4.8995 | 3.7906
39016.5639 | 1997 | 0 | 39016.5639 | 2124 | 0 |  | 1409 | 1554 | 121.917 | 0 | 129.6703 | 0 | 1.2192 | 0 | 1.2967 | 0 | 1.2192 | 1.2967 | 29.0626 | 21.3456 | 27.8434

## B3-E9
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 152.3431 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39016.5468 | 1 | 0 | 39016.5468 | 1 | 0 |  | -72 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39016.5489 | 1 | 0 | 39016.5489 | 1 | 0 |  | 113 | 258 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 249438 | 249438 | 249437.9994
39016.5511 | 1 | 0 | 39016.5511 | 1560 | 0 |  | 297.5 | 442.5 | 0.06105 | 0 | 95.2381 | 0 | 0.0006105 | 0 | 0.95238 | 0 | 0.0006105 | 0.95238 | 249438 | 59.9603 | 249437.9994
39016.5532 | 1 | 0 | 39016.5532 | 2136 | 0 |  | 482.5 | 627.5 | 0.06105 | 0 | 130.4029 | 0 | 0.0006105 | 0 | 1.304 | 0 | 0.0006105 | 1.304 | 249438 | 16.8249 | 249437.9994
39016.5553 | 1774 | 0 | 39016.5554 | 2220 | 0 |  | 667 | 812 | 108.3028 | 0 | 135.5311 | 0 | 1.083 | 0 | 1.3553 | 0 | 1.083 | 1.3553 | 40.664 | 12.4045 | 39.581
39016.5575 | 2400 | 0 | 39016.5575 | 2062 | 0 |  | 852 | 997 | 146.5201 | 0 | 125.8852 | 0 | 1.4652 | 0 | 1.2589 | 0 | 1.4652 | 1.2589 | 3.9742 | 21.0175 | 2.509
39016.5596 | 2450 | 0 | 39016.5596 | 2360 | 0 |  | 1036.5 | 1181.5 | 149.5726 | 0 | 144.0781 | 0 | 1.4957 | 0 | 1.4408 | 0 | 1.4957 | 1.4408 | 1.8522 | 5.7364 | 0.35652
39016.5618 | 2449 | 0 | 39016.5618 | 2479 | 0 |  | 1221.5 | 1366.5 | 149.5116 | 0 | 151.3431 | 0 | 1.4951 | 0 | 1.5134 | 0 | 1.4951 | 1.5134 | 1.8938 | 0.66075 | 0.39872
39016.5639 | 1989 | 0 | 39016.5639 | 2148 | 0 |  | 1406.5 | 1551.5 | 121.4286 | 0 | 131.1355 | 0 | 1.2143 | 0 | 1.3114 | 0 | 1.2143 | 1.3114 | 25.459 | 16.1723 | 24.2447

## B3-D8
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 158.4481 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39016.5468 | 1 | 0 | 39016.5468 | 1 | 0 |  | -74.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
39016.5489 | 0 | 0 | 39016.5489 | 1 | 0 |  | 110 | 255 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 518976 | 259438 | 518975.9997
39016.551 | 1 | 0 | 39016.551 | 1 | 0 |  | 294.5 | 439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259438 | 259438 | 259437.9994
39016.5532 | 1 | 0 | 39016.5532 | 2528 | 0 |  | 479.5 | 624.5 | 0.06105 | 0 | 154.3346 | 0 | 0.0006105 | 0 | 1.5433 | 0 | 0.0006105 | 1.5433 | 259438 | 2.6653 | 259437.9994
39016.5553 | 1705 | 0 | 39016.5553 | 2579 | 0 |  | 664.5 | 809.5 | 104.0904 | 0 | 157.4481 | 0 | 1.0409 | 0 | 1.5745 | 0 | 1.0409 | 1.5745 | 52.2217 | 0.63513 | 51.1808
39016.5574 | 2133 | 0 | 39016.5575 | 2386 | 0 |  | 849 | 994 | 130.2198 | 0 | 145.6654 | 0 | 1.3022 | 0 | 1.4567 | 0 | 1.3022 | 1.4567 | 21.6774 | 8.7754 | 20.3753
39016.5596 | 2095 | 0 | 39016.5596 | 2240 | 0 |  | 1034 | 1179 | 127.8999 | 0 | 136.7521 | 0 | 1.279 | 0 | 1.3675 | 0 | 1.279 | 1.3675 | 23.8845 | 15.8652 | 22.6055
39016.5617 | 2231 | 0 | 39016.5617 | 2539 | 0 |  | 1218.5 | 1363.5 | 136.2027 | 0 | 155.0061 | 0 | 1.362 | 0 | 1.5501 | 0 | 1.362 | 1.5501 | 16.3326 | 2.2206 | 14.9706
39016.5639 | 2115 | 0 | 39016.5639 | 2159 | 0 |  | 1403.5 | 1548.5 | 129.1209 | 0 | 131.8071 | 0 | 1.2912 | 0 | 1.3181 | 0 | 1.2912 | 1.3181 | 22.713 | 20.2121 | 21.4218

## B3-D7
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 161.1343 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39016.5467 | 1 | 0 | 39016.5467 | 1 | 0 |  | -77.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.5489 | 1 | 0 | 39016.5489 | 1 | 0 |  | 107 | 252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.551 | 1 | 0 | 39016.551 | 1 | 0 |  | 292 | 437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263838 | 263838 | 263837.9994
39016.5531 | 1 | 0 | 39016.5532 | 2535 | 0 |  | 477 | 622 | 0.06105 | 0 | 154.7619 | 0 | 0.0006105 | 0 | 1.5476 | 0 | 0.0006105 | 1.5476 | 263838 | 4.1176 | 263837.9994
39016.5553 | 2051 | 0 | 39016.5553 | 2340 | 0 |  | 661.5 | 806.5 | 125.2137 | 0 | 142.8571 | 0 | 1.2521 | 0 | 1.4286 | 0 | 1.2521 | 1.4286 | 28.6875 | 12.794 | 27.4353
39016.5574 | 2456 | 0 | 39016.5574 | 2034 | 0 |  | 846.5 | 991.5 | 149.9389 | 0 | 124.1758 | 0 | 1.4994 | 0 | 1.2418 | 0 | 1.4994 | 1.2418 | 7.4666 | 29.763 | 5.9672
39016.5595 | 2009 | 0 | 39016.5596 | 2623 | 0 |  | 1031 | 1176 | 122.6496 | 0 | 160.1343 | 0 | 1.2265 | 0 | 1.6013 | 0 | 1.2265 | 1.6013 | 31.3778 | 0.62448 | 30.1513
39016.5617 | 1906 | 0 | 39016.5617 | 2572 | 0 |  | 1216 | 1361 | 116.3614 | 0 | 157.0208 | 0 | 1.1636 | 0 | 1.5702 | 0 | 1.1636 | 1.5702 | 38.4774 | 2.6198 | 37.3138
39016.5638 | 2066 | 0 | 39016.5638 | 2422 | 0 |  | 1400.5 | 1545.5 | 126.1294 | 0 | 147.8632 | 0 | 1.2613 | 0 | 1.4786 | 0 | 1.2613 | 1.4786 | 27.7531 | 8.9752 | 26.4919

## B3-C6
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 155.2735 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39016.5467 | 1 | 0 | 39016.5467 | 1 | 0 |  | -80.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5488 | 1 | 0 | 39016.5488 | 1 | 0 |  | 104.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.551 | 1 | 0 | 39016.551 | 1 | 0 |  | 289 | 434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5531 | 1 | 0 | 39016.5531 | 1 | 0 |  | 474 | 619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5552 | 1721 | 0 | 39016.5553 | 1689 | 0 |  | 658.5 | 803.5 | 105.0672 | 0 | 103.1136 | 0 | 1.0507 | 0 | 1.0311 | 0 | 1.0507 | 1.0311 | 47.785 | 50.585 | 46.7343
39016.5574 | 2468 | 0 | 39016.5574 | 2016 | 0 |  | 843.5 | 988.5 | 150.6716 | 0 | 123.0769 | 0 | 1.5067 | 0 | 1.2308 | 0 | 1.5067 | 1.2308 | 3.0543 | 26.1597 | 1.5476
39016.5595 | 2508 | 0 | 39016.5595 | 2527 | 0 |  | 1028.5 | 1173.5 | 153.1136 | 0 | 154.2735 | 0 | 1.5311 | 0 | 1.5427 | 0 | 1.5311 | 1.5427 | 1.4107 | 0.6482 | 0.12045
39016.5617 | 1939 | 0 | 39016.5617 | 2473 | 0 |  | 1213 | 1358 | 118.3761 | 0 | 150.9768 | 0 | 1.1838 | 0 | 1.5098 | 0 | 1.1838 | 1.5098 | 31.1697 | 2.8459 | 29.9859
39016.5638 | 1950 | 0 | 39016.5638 | 2162 | 0 |  | 1398 | 1543 | 119.0476 | 0 | 131.9902 | 0 | 1.1905 | 0 | 1.3199 | 0 | 1.1905 | 1.3199 | 30.4297 | 17.6401 | 29.2393

## B3-C5
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 151 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39016.5467 | 1 | 0 | 39016.5467 | 1 | 0 |  | -83 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
39016.5488 | 1 | 0 | 39016.5488 | 1 | 0 |  | 101.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
39016.5509 | 1 | 0 | 39016.5509 | 1 | 0 |  | 286.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
39016.5531 | 1 | 0 | 39016.5531 | 1 | 0 |  | 471 | 616 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 247238 | 247238 | 247237.9994
39016.5552 | 1875 | 0 | 39016.5552 | 1605 | 0 |  | 656 | 801 | 114.4689 | 0 | 97.9853 | 0 | 1.1447 | 0 | 0.97985 | 0 | 1.1447 | 0.97985 | 31.9136 | 54.1047 | 30.7689
39016.5573 | 2182 | 0 | 39016.5574 | 2368 | 0 |  | 840.5 | 985.5 | 133.2112 | 0 | 144.5665 | 0 | 1.3321 | 0 | 1.4457 | 0 | 1.3321 | 1.4457 | 13.3538 | 4.4502 | 12.0217
39016.5595 | 2457 | 0 | 39016.5595 | 2423 | 0 |  | 1025.5 | 1170.5 | 150 | 0 | 147.9243 | 0 | 1.5 | 0 | 1.4792 | 0 | 1.5 | 1.4792 | 0.66667 | 2.0792 | 0.83333
39016.5616 | 1932 | 0 | 39016.5616 | 2326 | 0 |  | 1210.5 | 1355.5 | 117.9487 | 0 | 142.0024 | 0 | 1.1795 | 0 | 1.42 | 0 | 1.1795 | 1.42 | 28.0217 | 6.3362 | 26.8423
39016.5638 | 1981 | 0 | 39016.5638 | 1867 | 0 |  | 1395 | 1540 | 120.9402 | 0 | 113.9805 | 0 | 1.2094 | 0 | 1.1398 | 0 | 1.2094 | 1.1398 | 24.8551 | 32.4788 | 23.6457

## B3-B4
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 156.0061 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39016.5466 | 1 | 0 | 39016.5466 | 1 | 0 |  | -86 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39016.5488 | 1 | 0 | 39016.5488 | 1 | 0 |  | 98.5 | 243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39016.5509 | 1 | 0 | 39016.5509 | 1 | 0 |  | 283.5 | 428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39016.553 | 1 | 0 | 39016.5531 | 1 | 0 |  | 468.5 | 613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255438 | 255438 | 255437.9994
39016.5552 | 1583 | 387 | 39016.5552 | 1550 | 374 |  | 653 | 798 | 96.6422 | 23.6264 | 94.6276 | 22.8327 | 0.96642 | 0.23626 | 0.94628 | 0.22833 | 0.73016 | 0.71795 | 111.4477 | 119.6288 | 82.3898
39016.5573 | 2539 | 0 | 39016.5573 | 2263 | 0 |  | 838 | 983 | 155.0061 | 0 | 138.1563 | 0 | 1.5501 | 0 | 1.3816 | 0 | 1.5501 | 1.3816 | 0.64514 | 12.92 | 0.90493
39016.5595 | 2501 | 0 | 39016.5595 | 2026 | 0 |  | 1022.5 | 1167.5 | 152.6862 | 0 | 123.6874 | 0 | 1.5269 | 0 | 1.2369 | 0 | 1.5269 | 1.2369 | 2.1743 | 26.1293 | 0.64747
39016.5616 | 2098 | 1 | 39016.5616 | 1953 | 1 |  | 1207.5 | 1352.5 | 128.083 | 0.06105 | 119.2308 | 0.06105 | 1.2808 | 0.0006105 | 1.1923 | 0.0006105 | 1.2802 | 1.1917 | 21.8448 | 30.9322 | 10781.7845
39016.5637 | 2040 | 65 | 39016.5638 | 1861 | 56 |  | 1392.5 | 1537.5 | 124.5421 | 3.9683 | 113.6142 | 3.4188 | 1.2454 | 0.039683 | 1.1361 | 0.034188 | 1.2057 | 1.102 | 28.2463 | 43.2166 | 209.085

## A2-C6
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 141.1099 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39016.5464 | 1 | 0 | 39016.5464 | 1 | 0 |  | -105.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231038 | 231038 | 231037.9994
39016.5485 | 1 | 0 | 39016.5486 | 1 | 0 |  | 79.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231038 | 231038 | 231037.9994
39016.5507 | 1 | 0 | 39016.5507 | 1 | 0 |  | 264 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231038 | 231038 | 231037.9994
39016.5528 | 1 | 0 | 39016.5528 | 1 | 0 |  | 448.5 | 593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231038 | 231038 | 231037.9994
39016.555 | 1 | 0 | 39016.555 | 1 | 0 |  | 633.5 | 778.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 231038 | 231038 | 231037.9994
39016.5571 | 1937 | 0 | 39016.5571 | 2255 | 0 |  | 818.5 | 963.5 | 118.254 | 0 | 137.6679 | 0 | 1.1825 | 0 | 1.3767 | 0 | 1.1825 | 1.3767 | 19.3278 | 2.5002 | 18.1453
39016.5592 | 2219 | 0 | 39016.5592 | 2115 | 0 |  | 1003 | 1148 | 135.4701 | 0 | 129.1209 | 0 | 1.3547 | 0 | 1.2912 | 0 | 1.3547 | 1.2912 | 4.1631 | 9.2851 | 2.8084
39016.5614 | 2295 | 0 | 39016.5614 | 2058 | 0 |  | 1188 | 1333 | 140.1099 | 0 | 125.641 | 0 | 1.4011 | 0 | 1.2564 | 0 | 1.4011 | 1.2564 | 0.71373 | 12.312 | 0.68737
39016.5635 | 2158 | 0 | 39016.5635 | 1893 | 0 |  | 1372.5 | 1517.5 | 131.746 | 0 | 115.5678 | 0 | 1.3175 | 0 | 1.1557 | 0 | 1.3175 | 1.1557 | 7.1075 | 22.1014 | 5.79

## A2-C5
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 154.9072 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39016.5464 | 1 | 0 | 39016.5464 | 1 | 0 |  | -108.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39016.5485 | 1 | 0 | 39016.5485 | 1 | 0 |  | 76.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39016.5506 | 1 | 0 | 39016.5507 | 1 | 0 |  | 261 | 406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253638 | 253638 | 253637.9994
39016.5528 | 0 | 0 | 39016.5528 | 1 | 0 |  | 446 | 591 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 507376 | 253638 | 507375.9997
39016.5549 | 1 | 0 | 39016.5549 | 2388 | 0 |  | 630.5 | 775.5 | 0.06105 | 0 | 145.7875 | 0 | 0.0006105 | 0 | 1.4579 | 0 | 0.0006105 | 1.4579 | 253638 | 6.2554 | 253637.9994
39016.5571 | 1681 | 0 | 39016.5571 | 2521 | 0 |  | 815.5 | 960.5 | 102.6252 | 0 | 153.9072 | 0 | 1.0263 | 0 | 1.5391 | 0 | 1.0263 | 1.5391 | 50.9447 | 0.64974 | 49.9184
39016.5592 | 2227 | 0 | 39016.5592 | 2106 | 0 |  | 1000.5 | 1145.5 | 135.9585 | 0 | 128.5714 | 0 | 1.3596 | 0 | 1.2857 | 0 | 1.3596 | 1.2857 | 13.9371 | 20.4834 | 12.5776
39016.5613 | 2352 | 0 | 39016.5614 | 2186 | 0 |  | 1185 | 1330 | 143.5897 | 0 | 133.4554 | 0 | 1.4359 | 0 | 1.3346 | 0 | 1.4359 | 1.3346 | 7.8818 | 16.0741 | 6.4459
39016.5635 | 2024 | 0 | 39016.5635 | 2239 | 0 |  | 1370 | 1515 | 123.5653 | 0 | 136.6911 | 0 | 1.2357 | 0 | 1.3669 | 0 | 1.2357 | 1.3669 | 25.3646 | 13.3265 | 24.129

## A2-B4
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 150.2063 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39016.5463 | 1 | 0 | 39016.5464 | 1 | 0 |  | -111 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
39016.5485 | 1 | 0 | 39016.5485 | 1 | 0 |  | 73.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
39016.5506 | 1 | 0 | 39016.5506 | 1 | 0 |  | 258.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
39016.5527 | 1 | 0 | 39016.5528 | 1 | 0 |  | 443 | 588 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
39016.5549 | 1 | 0 | 39016.5549 | 1 | 0 |  | 628 | 773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 245938 | 245938 | 245937.9994
39016.557 | 1895 | 0 | 39016.557 | 1957 | 0 |  | 812.5 | 957.5 | 115.6899 | 0 | 119.475 | 0 | 1.1569 | 0 | 1.1947 | 0 | 1.1569 | 1.1947 | 29.8354 | 25.722 | 28.6785
39016.5592 | 2444 | 0 | 39016.5592 | 2097 | 0 |  | 997.5 | 1142.5 | 149.2063 | 0 | 128.022 | 0 | 1.4921 | 0 | 1.2802 | 0 | 1.4921 | 1.2802 | 0.67021 | 17.3286 | 0.82185
39016.5613 | 1966 | 0 | 39016.5613 | 2104 | 0 |  | 1182.5 | 1327.5 | 120.0244 | 0 | 128.4493 | 0 | 1.2002 | 0 | 1.2845 | 0 | 1.2002 | 1.2845 | 25.1465 | 16.9382 | 23.9462
39016.5634 | 2057 | 0 | 39016.5635 | 2240 | 0 |  | 1367 | 1512 | 125.58 | 0 | 136.7521 | 0 | 1.2558 | 0 | 1.3675 | 0 | 1.2558 | 1.3675 | 19.6101 | 9.8384 | 18.3543

## A2-B3
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 152.0379 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39016.5463 | 1 | 0 | 39016.5463 | 1 | 0 |  | -114 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
39016.5484 | 1 | 0 | 39016.5484 | 1 | 0 |  | 70.5 | 215.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
39016.5506 | 1 | 0 | 39016.5506 | 1 | 0 |  | 255.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
39016.5527 | 1 | 0 | 39016.5527 | 1 | 0 |  | 440.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 248938 | 248938 | 248937.9994
39016.5548 | 1 | 0 | 39016.5549 | 1063 | 0 |  | 625 | 770 | 0.06105 | 0 | 64.8962 | 0 | 0.0006105 | 0 | 0.64896 | 0 | 0.0006105 | 0.64896 | 248938 | 134.2785 | 248937.9994
39016.557 | 1809 | 0 | 39016.557 | 2400 | 0 |  | 810 | 955 | 110.4396 | 0 | 146.5201 | 0 | 1.1044 | 0 | 1.4652 | 0 | 1.1044 | 1.4652 | 37.6661 | 3.7658 | 36.5617
39016.5591 | 2072 | 0 | 39016.5591 | 2474 | 0 |  | 994.5 | 1139.5 | 126.4957 | 0 | 151.0379 | 0 | 1.265 | 0 | 1.5104 | 0 | 1.265 | 1.5104 | 20.1921 | 0.66209 | 18.9271
39016.5613 | 2466 | 0 | 39016.5613 | 2125 | 0 |  | 1179.5 | 1324.5 | 150.5495 | 0 | 129.7314 | 0 | 1.5055 | 0 | 1.2973 | 0 | 1.5055 | 1.2973 | 0.98865 | 17.1944 | 0.51685
39016.5634 | 2263 | 0 | 39016.5634 | 2133 | 0 |  | 1364 | 1509 | 138.1563 | 0 | 130.2198 | 0 | 1.3816 | 0 | 1.3022 | 0 | 1.3816 | 1.3022 | 10.0477 | 16.7548 | 8.6662

## A1-C6
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 146.0549 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39016.5461 | 1 | 0 | 39016.5461 | 1 | 0 |  | -133.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
39016.5482 | 1 | 0 | 39016.5482 | 1 | 0 |  | 51 | 196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
39016.5503 | 1 | 0 | 39016.5504 | 1 | 0 |  | 236 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
39016.5525 | 1 | 0 | 39016.5525 | 1 | 0 |  | 420.5 | 565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 239138 | 239138 | 239137.9994
39016.5546 | 1 | 0 | 39016.5546 | 811 | 0 |  | 605.5 | 750.5 | 0.06105 | 0 | 49.5116 | 0 | 0.0006105 | 0 | 0.49512 | 0 | 0.0006105 | 0.49512 | 239138 | 194.9914 | 239137.9994
39016.5568 | 1560 | 0 | 39016.5568 | 2195 | 0 |  | 790.5 | 935.5 | 95.2381 | 0 | 134.0049 | 0 | 0.95238 | 0 | 1.34 | 0 | 0.95238 | 1.34 | 53.3577 | 8.9923 | 52.4053
39016.5589 | 2111 | 0 | 39016.5589 | 2376 | 0 |  | 975 | 1120 | 128.8767 | 0 | 145.0549 | 0 | 1.2888 | 0 | 1.4505 | 0 | 1.2888 | 1.4505 | 13.3292 | 0.68939 | 12.0405
39016.561 | 2369 | 0 | 39016.5611 | 2231 | 0 |  | 1160 | 1305 | 144.6276 | 0 | 136.2027 | 0 | 1.4463 | 0 | 1.362 | 0 | 1.4463 | 1.362 | 0.98691 | 7.2335 | 0.45936
39016.5632 | 2251 | 0 | 39016.5632 | 2368 | 0 |  | 1344.5 | 1489.5 | 137.4237 | 0 | 144.5665 | 0 | 1.3742 | 0 | 1.4457 | 0 | 1.3742 | 1.4457 | 6.2808 | 1.0296 | 4.9065

## A1-C5
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 143.2466 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39016.546 | 1 | 0 | 39016.5461 | 1 | 0 |  | -136.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
39016.5482 | 1 | 0 | 39016.5482 | 1 | 0 |  | 48.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
39016.5503 | 1 | 0 | 39016.5503 | 1 | 0 |  | 233.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
39016.5525 | 1 | 0 | 39016.5525 | 1 | 0 |  | 418 | 563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234538 | 234538 | 234537.9994
39016.5546 | 1 | 0 | 39016.5546 | 1701 | 0 |  | 602.5 | 747.5 | 0.06105 | 0 | 103.8462 | 0 | 0.0006105 | 0 | 1.0385 | 0 | 0.0006105 | 1.0385 | 234538 | 37.9412 | 234537.9994
39016.5567 | 1447 | 0 | 39016.5567 | 2294 | 0 |  | 787.5 | 932.5 | 88.3394 | 0 | 140.0488 | 0 | 0.88339 | 0 | 1.4005 | 0 | 0.88339 | 1.4005 | 62.1548 | 2.2833 | 61.2714
39016.5589 | 2308 | 0 | 39016.5589 | 2287 | 0 |  | 972.5 | 1117.5 | 140.9035 | 0 | 139.6215 | 0 | 1.409 | 0 | 1.3962 | 0 | 1.409 | 1.3962 | 1.6629 | 2.5964 | 0.25388
39016.561 | 1983 | 0 | 39016.561 | 2070 | 0 |  | 1157 | 1302 | 121.0623 | 0 | 126.3736 | 0 | 1.2106 | 0 | 1.2637 | 0 | 1.2106 | 1.2637 | 18.3248 | 13.3517 | 17.1141
39016.5631 | 1995 | 0 | 39016.5632 | 2330 | 0 |  | 1342 | 1487 | 121.7949 | 0 | 142.2466 | 0 | 1.2179 | 0 | 1.4225 | 0 | 1.2179 | 1.4225 | 17.613 | 0.703 | 16.3951

## A1-B4
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 156.7387 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39016.546 | 1 | 0 | 39016.546 | 1 | 0 |  | -139 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39016.5481 | 1 | 0 | 39016.5482 | 1 | 0 |  | 45.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39016.5503 | 1 | 0 | 39016.5503 | 0 | 0 |  | 230.5 | 375.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 256638 | 513376 | 256637.9994
39016.5524 | 1 | 0 | 39016.5524 | 1 | 0 |  | 415.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256638 | 256638 | 256637.9994
39016.5546 | 1 | 0 | 39016.5546 | 538 | 0 |  | 600 | 745 | 0.06105 | 0 | 32.8449 | 0 | 0.0006105 | 0 | 0.32845 | 0 | 0.0006105 | 0.32845 | 256638 | 377.2082 | 256637.9994
39016.5567 | 1362 | 0 | 39016.5567 | 2152 | 0 |  | 784.5 | 929.5 | 83.1502 | 0 | 131.3797 | 0 | 0.8315 | 0 | 1.3138 | 0 | 0.8315 | 1.3138 | 88.5007 | 19.302 | 87.6692
39016.5588 | 1969 | 0 | 39016.5589 | 2551 | 0 |  | 969.5 | 1114.5 | 120.2076 | 0 | 155.7387 | 0 | 1.2021 | 0 | 1.5574 | 0 | 1.2021 | 1.5574 | 30.39 | 0.6421 | 29.188
39016.561 | 1955 | 0 | 39016.561 | 2476 | 0 |  | 1154.5 | 1299.5 | 119.3529 | 0 | 151.16 | 0 | 1.1935 | 0 | 1.5116 | 0 | 1.1935 | 1.5116 | 31.3238 | 3.6906 | 30.1303
39016.5631 | 2290 | 0 | 39016.5631 | 1949 | 0 |  | 1339 | 1484 | 139.8046 | 0 | 118.9866 | 0 | 1.398 | 0 | 1.1899 | 0 | 1.398 | 1.1899 | 12.1127 | 31.7281 | 10.7146

## A1-B3
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 143.0635 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39016.546 | 1 | 0 | 39016.546 | 1 | 0 |  | -142 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234238 | 234238 | 234237.9994
39016.5481 | 1 | 0 | 39016.5481 | 1 | 0 |  | 43 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234238 | 234238 | 234237.9994
39016.5503 | 0 | 0 | 39016.5503 | 1 | 0 |  | 227.5 | 372.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 468576 | 234238 | 468575.9997
39016.5524 | 1 | 0 | 39016.5524 | 1 | 0 |  | 412.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 234238 | 234238 | 234237.9994
39016.5545 | 1 | 0 | 39016.5545 | 438 | 0 |  | 597 | 742 | 0.06105 | 0 | 26.7399 | 0 | 0.0006105 | 0 | 0.2674 | 0 | 0.0006105 | 0.2674 | 234238 | 435.0183 | 234237.9994
39016.5567 | 1193 | 0 | 39016.5567 | 2301 | 0 |  | 782 | 927 | 72.8327 | 0 | 140.4762 | 0 | 0.72833 | 0 | 1.4048 | 0 | 0.72833 | 1.4048 | 96.4275 | 1.8418 | 95.6992
39016.5588 | 1972 | 0 | 39016.5588 | 1999 | 0 |  | 966.5 | 1111.5 | 120.3907 | 0 | 122.0391 | 0 | 1.2039 | 0 | 1.2204 | 0 | 1.2039 | 1.2204 | 18.8327 | 17.2276 | 17.6287
39016.5609 | 2235 | 0 | 39016.561 | 1961 | 0 |  | 1151.5 | 1296.5 | 136.4469 | 0 | 119.7192 | 0 | 1.3645 | 0 | 1.1972 | 0 | 1.3645 | 1.1972 | 4.8492 | 19.4992 | 3.4847
39016.5631 | 2327 | 0 | 39016.5631 | 2095 | 0 |  | 1336.5 | 1481.5 | 142.0635 | 0 | 127.8999 | 0 | 1.4206 | 0 | 1.279 | 0 | 1.4206 | 1.279 | 0.70391 | 11.8558 | 0.71672

## A1-A2
Open Burn Test 3 |  |  | 2006-10-26 | 13:08 |  |  | Vs = |  | 155.2735 |  | R = | 100
Mixed TS | 7-C | Tray C | IRMS | 1
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39016.5459 | 1 | 0 | 39016.546 | 1 | 0 |  | -144.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5481 | 1 | 0 | 39016.5481 | 1 | 0 |  | 40 | 185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5502 | 1 | 0 | 39016.5502 | 1 | 0 |  | 225 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5524 | 1 | 0 | 39016.5524 | 1 | 0 |  | 409.5 | 554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5545 | 1 | 0 | 39016.5545 | 1 | 0 |  | 594.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254238 | 254238 | 254237.9994
39016.5566 | 1359 | 601 | 39016.5567 | 1356 | 550 |  | 779 | 924 | 82.967 | 36.6911 | 82.7839 | 33.5775 | 0.82967 | 0.36691 | 0.82784 | 0.33578 | 0.46276 | 0.49206 | 258.8274 | 200.063 | 64.7189
39016.5588 | 2495 | 0 | 39016.5588 | 1971 | 0 |  | 964 | 1109 | 152.3199 | 0 | 120.3297 | 0 | 1.5232 | 0 | 1.2033 | 0 | 1.5232 | 1.2033 | 1.9391 | 29.0401 | 0.41588
39016.5609 | 2142 | 0 | 39016.5609 | 2527 | 0 |  | 1148.5 | 1293.5 | 130.7692 | 0 | 154.2735 | 0 | 1.3077 | 0 | 1.5427 | 0 | 1.3077 | 1.5427 | 18.7386 | 0.6482 | 17.4309
39016.5631 | 2437 | 27 | 39016.5631 | 1878 | 21 |  | 1333.5 | 1478.5 | 148.779 | 1.6484 | 114.652 | 1.2821 | 1.4878 | 0.016484 | 1.1465 | 0.012821 | 1.4713 | 1.1337 | 4.5201 | 47.7863 | 95.0642

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 3 |  |  | 2006-10-26 | 13:08
39016.5459 | 1 | 0 | 1 | Mixed TS | 7-C | Tray C | IRMS | 1
39016.5481 | 1 | 0 | 1 |  | 250 kW |  | Bundle
39016.5502 | 1 | 0 | 1
39016.5524 | 1 | 0 | 1
39016.5545 | 1 | 0 | 1
39016.5566 | 1359 | 601 | 1
39016.5588 | 2495 | 0 | 1
39016.5609 | 2142 | 0 | 1
39016.5631 | 2437 | 27 | 1
1
39016.546 | 1 | 0 | 2
39016.5481 | 1 | 0 | 2
39016.5502 | 1 | 0 | 2
39016.5524 | 1 | 0 | 2
39016.5545 | 1 | 0 | 2
39016.5567 | 1356 | 550 | 2
39016.5588 | 1971 | 0 | 2
39016.5609 | 2527 | 0 | 2
39016.5631 | 1878 | 21 | 2
2
39016.546 | 1 | 0 | 3
39016.5481 | 1 | 0 | 3
39016.5503 | 0 | 0 | 3
39016.5524 | 1 | 0 | 3
39016.5545 | 1 | 0 | 3
39016.5567 | 1193 | 0 | 3
39016.5588 | 1972 | 0 | 3
39016.5609 | 2235 | 0 | 3
39016.5631 | 2327 | 0 | 3
3
39016.546 | 1 | 0 | 4
39016.5481 | 1 | 0 | 4
39016.5503 | 1 | 0 | 4
39016.5524 | 1 | 0 | 4
39016.5545 | 438 | 0 | 4
39016.5567 | 2301 | 0 | 4
39016.5588 | 1999 | 0 | 4
39016.561 | 1961 | 0 | 4
39016.5631 | 2095 | 0 | 4
4
39016.546 | 1 | 0 | 5
39016.5481 | 1 | 0 | 5
39016.5503 | 1 | 0 | 5
39016.5524 | 1 | 0 | 5
39016.5546 | 1 | 0 | 5
39016.5567 | 1362 | 0 | 5
39016.5588 | 1969 | 0 | 5
39016.561 | 1955 | 0 | 5
39016.5631 | 2290 | 0 | 5
5
39016.546 | 1 | 0 | 6
39016.5482 | 1 | 0 | 6
39016.5503 | 0 | 0 | 6
39016.5524 | 1 | 0 | 6
39016.5546 | 538 | 0 | 6
39016.5567 | 2152 | 0 | 6
39016.5589 | 2551 | 0 | 6
39016.561 | 2476 | 0 | 6
39016.5631 | 1949 | 0 | 6
6
39016.546 | 1 | 0 | 7
39016.5482 | 1 | 0 | 7
39016.5503 | 1 | 0 | 7
39016.5525 | 1 | 0 | 7
39016.5546 | 1 | 0 | 7
39016.5567 | 1447 | 0 | 7
39016.5589 | 2308 | 0 | 7
39016.561 | 1983 | 0 | 7
39016.5631 | 1995 | 0 | 7
7
39016.5461 | 1 | 0 | 8
39016.5482 | 1 | 0 | 8
39016.5503 | 1 | 0 | 8
39016.5525 | 1 | 0 | 8
39016.5546 | 1701 | 0 | 8
39016.5567 | 2294 | 0 | 8
39016.5589 | 2287 | 0 | 8
39016.561 | 2070 | 0 | 8
39016.5632 | 2330 | 0 | 8
8
39016.5461 | 1 | 0 | 9
39016.5482 | 1 | 0 | 9
39016.5503 | 1 | 0 | 9
39016.5525 | 1 | 0 | 9
39016.5546 | 1 | 0 | 9
39016.5568 | 1560 | 0 | 9
39016.5589 | 2111 | 0 | 9
39016.561 | 2369 | 0 | 9
39016.5632 | 2251 | 0 | 9
9
39016.5461 | 1 | 0 | 10
39016.5482 | 1 | 0 | 10
39016.5504 | 1 | 0 | 10
39016.5525 | 1 | 0 | 10
39016.5546 | 811 | 0 | 10
39016.5568 | 2195 | 0 | 10
39016.5589 | 2376 | 0 | 10
39016.5611 | 2231 | 0 | 10
39016.5632 | 2368 | 0 | 10
10
39016.5461 | 1 | 0 | 11
39016.5482 | 1 | 0 | 11
39016.5504 | 1 | 0 | 11
39016.5525 | 0 | 0 | 11
39016.5547 | 1 | 0 | 11
39016.5568 | 1794 | 0 | 11
39016.5589 | 2528 | 0 | 11
39016.5611 | 2402 | 0 | 11
39016.5632 | 1925 | 0 | 11
11
39016.5461 | 1 | 0 | 12
39016.5483 | 1 | 0 | 12
39016.5504 | 1 | 0 | 12
39016.5525 | 2342 | 0 | 12
39016.5547 | 2568 | 0 | 12
39016.5568 | 2201 | 0 | 12
39016.559 | 2317 | 0 | 12
39016.5611 | 2528 | 0 | 12
39016.5632 | 1944 | 0 | 12
12
39016.5461 | 1 | 0 | 13
39016.5483 | 1 | 0 | 13
39016.5504 | 1 | 0 | 13
39016.5526 | 1 | 0 | 13
39016.5547 | 1 | 0 | 13
39016.5568 | 1746 | 0 | 13
39016.559 | 2502 | 0 | 13
39016.5611 | 2112 | 0 | 13
39016.5633 | 1939 | 0 | 13
13
39016.5462 | 1 | 0 | 14
39016.5483 | 1 | 0 | 14
39016.5504 | 1 | 0 | 14
39016.5526 | 2021 | 0 | 14
39016.5547 | 2031 | 0 | 14
39016.5569 | 2576 | 0 | 14
39016.559 | 2490 | 0 | 14
39016.5611 | 2237 | 0 | 14
39016.5633 | 1991 | 0 | 14
14
39016.5462 | 1 | 0 | 15
39016.5483 | 1 | 0 | 15
39016.5505 | 1 | 0 | 15
39016.5526 | 1 | 0 | 15
39016.5547 | 1 | 0 | 15
39016.5569 | 1584 | 0 | 15
39016.559 | 2047 | 0 | 15
39016.5611 | 2208 | 0 | 15
39016.5633 | 2155 | 0 | 15
15
39016.5462 | 1 | 0 | 16
39016.5483 | 1 | 0 | 16
39016.5505 | 2074 | 0 | 16
39016.5526 | 2135 | 0 | 16
39016.5547 | 2027 | 0 | 16
39016.5569 | 2261 | 0 | 16
39016.559 | 2159 | 0 | 16
39016.5612 | 2554 | 0 | 16
39016.5633 | 2609 | 0 | 16
16
39016.5462 | 1 | 0 | 17
39016.5483 | 1 | 0 | 17
39016.5505 | 1 | 0 | 17
39016.5526 | 1 | 0 | 17
39016.5569 | 1671 | 0 | 17
39016.559 | 2102 | 0 | 17
39016.5612 | 2523 | 0 | 17
39016.5633 | 2257 | 0 | 17
17
39016.5462 | 1 | 0 | 18
39016.5484 | 1 | 0 | 18
39016.5505 | 1 | 0 | 18
39016.5526 | 2275 | 0 | 18
39016.5548 | 2537 | 0 | 18
39016.5569 | 2635 | 0 | 18
39016.5591 | 2392 | 0 | 18
39016.5612 | 2577 | 0 | 18
39016.5633 | 2415 | 0 | 18
18
39016.5462 | 1 | 0 | 19
39016.5484 | 1 | 0 | 19
39016.5505 | 1 | 0 | 19
39016.5527 | 1 | 0 | 19
39016.5548 | 1 | 0 | 19
39016.5569 | 1702 | 0 | 19
39016.5591 | 2307 | 0 | 19
39016.5612 | 2016 | 0 | 19
39016.5633 | 2264 | 0 | 19
19
39016.5462 | 1 | 0 | 20
39016.5484 | 1 | 0 | 20
39016.5505 | 1 | 0 | 20
39016.5527 | 1417 | 0 | 20
39016.5548 | 2009 | 0 | 20
39016.5569 | 2210 | 0 | 20
39016.5591 | 2384 | 0 | 20
39016.5612 | 2116 | 0 | 20
39016.5634 | 2332 | 0 | 20
20
39016.5463 | 1 | 0 | 21
39016.5484 | 1 | 0 | 21
39016.5505 | 1 | 0 | 21
39016.5527 | 1 | 0 | 21
39016.5548 | 1 | 0 | 21
39016.557 | 1494 | 0 | 21
39016.5591 | 2040 | 0 | 21
39016.5612 | 2357 | 0 | 21
39016.5634 | 2036 | 0 | 21
21
39016.5463 | 1 | 0 | 22
39016.5484 | 1 | 0 | 22
39016.5506 | 1 | 0 | 22
39016.5527 | 1936 | 0 | 22
39016.5548 | 2577 | 0 | 22
39016.557 | 2284 | 0 | 22
39016.5591 | 2220 | 0 | 22
39016.5612 | 2332 | 0 | 22
39016.5634 | 2276 | 0 | 22
22
39016.5463 | 1 | 0 | 23
39016.5484 | 1 | 0 | 23
39016.5506 | 1 | 0 | 23
39016.5527 | 1 | 0 | 23
39016.5548 | 1 | 0 | 23
39016.557 | 1809 | 0 | 23
39016.5591 | 2072 | 0 | 23
39016.5613 | 2466 | 0 | 23
39016.5634 | 2263 | 0 | 23
23
39016.5463 | 1 | 0 | 24
39016.5484 | 1 | 0 | 24
39016.5506 | 1 | 0 | 24
39016.5527 | 1 | 0 | 24
39016.5549 | 1063 | 0 | 24
39016.557 | 2400 | 0 | 24
39016.5591 | 2474 | 0 | 24
39016.5613 | 2125 | 0 | 24
39016.5634 | 2133 | 0 | 24
24
39016.5463 | 1 | 0 | 25
39016.5485 | 1 | 0 | 25
39016.5506 | 1 | 0 | 25
39016.5527 | 1 | 0 | 25
39016.5549 | 1 | 0 | 25
39016.557 | 1895 | 0 | 25
39016.5592 | 2444 | 0 | 25
39016.5613 | 1966 | 0 | 25
39016.5634 | 2057 | 0 | 25
25
39016.5464 | 1 | 0 | 26
39016.5485 | 1 | 0 | 26
39016.5506 | 1 | 0 | 26
39016.5528 | 1 | 0 | 26
39016.5549 | 1 | 0 | 26
39016.557 | 1957 | 0 | 26
39016.5592 | 2097 | 0 | 26
39016.5613 | 2104 | 0 | 26
39016.5635 | 2240 | 0 | 26
26
39016.5464 | 1 | 0 | 27
39016.5485 | 1 | 0 | 27
39016.5506 | 1 | 0 | 27
39016.5528 | 0 | 0 | 27
39016.5549 | 1 | 0 | 27
39016.5571 | 1681 | 0 | 27
39016.5592 | 2227 | 0 | 27
39016.5613 | 2352 | 0 | 27
39016.5635 | 2024 | 0 | 27
27
39016.5464 | 1 | 0 | 28
39016.5485 | 1 | 0 | 28
39016.5507 | 1 | 0 | 28
39016.5528 | 1 | 0 | 28
39016.5549 | 2388 | 0 | 28
39016.5571 | 2521 | 0 | 28
39016.5592 | 2106 | 0 | 28
39016.5614 | 2186 | 0 | 28
39016.5635 | 2239 | 0 | 28
28
39016.5464 | 1 | 0 | 29
39016.5485 | 1 | 0 | 29
39016.5507 | 1 | 0 | 29
39016.5528 | 1 | 0 | 29
39016.555 | 1 | 0 | 29
39016.5571 | 1937 | 0 | 29
39016.5592 | 2219 | 0 | 29
39016.5614 | 2295 | 0 | 29
39016.5635 | 2158 | 0 | 29
29
39016.5464 | 1 | 0 | 30
39016.5486 | 1 | 0 | 30
39016.5507 | 1 | 0 | 30
39016.5528 | 1 | 0 | 30
39016.555 | 1 | 0 | 30
39016.5571 | 2255 | 0 | 30
39016.5592 | 2115 | 0 | 30
39016.5614 | 2058 | 0 | 30
39016.5635 | 1893 | 0 | 30
30
39016.5464 | 1 | 0 | 31
39016.5486 | 1 | 0 | 31
39016.5507 | 1 | 0 | 31
39016.5528 | 1 | 0 | 31
39016.555 | 1 | 0 | 31
39016.5571 | 1706 | 0 | 31
39016.5593 | 2199 | 0 | 31
39016.5614 | 1999 | 0 | 31
39016.5635 | 1873 | 0 | 31
31
39016.5464 | 1 | 0 | 32
39016.5486 | 1 | 0 | 32
39016.5507 | 1 | 0 | 32
39016.5529 | 2426 | 0 | 32
39016.555 | 2281 | 0 | 32
39016.5571 | 2242 | 0 | 32
39016.5593 | 2384 | 0 | 32
39016.5614 | 2338 | 0 | 32
39016.5636 | 2021 | 0 | 32
32
39016.5465 | 1 | 0 | 33
39016.5486 | 1 | 0 | 33
39016.5507 | 0 | 0 | 33
39016.5529 | 1 | 0 | 33
39016.555 | 1 | 0 | 33
39016.5572 | 2035 | 0 | 33
39016.5593 | 2197 | 0 | 33
39016.5614 | 2292 | 0 | 33
39016.5636 | 1859 | 0 | 33
33
39016.5465 | 1 | 0 | 34
39016.5486 | 1 | 0 | 34
39016.5508 | 1 | 0 | 34
39016.5529 | 1989 | 0 | 34
39016.555 | 2151 | 0 | 34
39016.5572 | 2583 | 0 | 34
39016.5593 | 2515 | 0 | 34
39016.5614 | 2295 | 0 | 34
39016.5636 | 2014 | 0 | 34
34
39016.5465 | 1 | 0 | 35
39016.5486 | 1 | 0 | 35
39016.5508 | 1 | 0 | 35
39016.5529 | 1 | 0 | 35
39016.555 | 1 | 0 | 35
39016.5572 | 1716 | 0 | 35
39016.5593 | 2178 | 0 | 35
39016.5615 | 1973 | 0 | 35
39016.5636 | 2106 | 0 | 35
35
39016.5465 | 1 | 0 | 36
39016.5486 | 1 | 0 | 36
39016.5508 | 2155 | 0 | 36
39016.5529 | 2408 | 0 | 36
39016.5551 | 2076 | 0 | 36
39016.5572 | 2282 | 0 | 36
39016.5593 | 2240 | 0 | 36
39016.5615 | 2113 | 0 | 36
39016.5636 | 2278 | 0 | 36
36
39016.5465 | 1 | 0 | 37
39016.5487 | 1 | 0 | 37
39016.5508 | 1 | 0 | 37
39016.5529 | 1 | 0 | 37
39016.5551 | 1 | 0 | 37
39016.5572 | 1620 | 0 | 37
39016.5594 | 2130 | 0 | 37
39016.5615 | 2120 | 0 | 37
39016.5636 | 1846 | 0 | 37
37
39016.5465 | 1 | 0 | 38
39016.5487 | 1 | 0 | 38
39016.5508 | 177 | 0 | 38
39016.553 | 2591 | 0 | 38
39016.5551 | 2299 | 0 | 38
39016.5572 | 2237 | 0 | 38
39016.5594 | 2598 | 0 | 38
39016.5615 | 2446 | 0 | 38
39016.5637 | 2258 | 0 | 38
38
39016.5466 | 0 | 0 | 39
39016.5487 | 1 | 0 | 39
39016.5508 | 1 | 0 | 39
39016.553 | 1 | 0 | 39
39016.5551 | 1 | 0 | 39
39016.5573 | 1636 | 0 | 39
39016.5594 | 2061 | 0 | 39
39016.5615 | 2190 | 0 | 39
39016.5637 | 2214 | 0 | 39
39
39016.5466 | 1 | 0 | 40
39016.5487 | 1 | 0 | 40
39016.5509 | 1 | 0 | 40
39016.553 | 2171 | 0 | 40
39016.5551 | 2185 | 0 | 40
39016.5573 | 2391 | 0 | 40
39016.5594 | 2402 | 0 | 40
39016.5616 | 2101 | 0 | 40
39016.5637 | 2074 | 0 | 40
40
39016.5466 | 1 | 0 | 41
39016.5487 | 1 | 0 | 41
39016.5509 | 1 | 0 | 41
39016.553 | 1 | 0 | 41
39016.5552 | 1 | 0 | 41
39016.5573 | 1958 | 0 | 41
39016.5594 | 2092 | 0 | 41
39016.5616 | 1937 | 0 | 41
39016.5637 | 2196 | 0 | 41
41
39016.5466 | 1 | 0 | 42
39016.5488 | 1 | 0 | 42
39016.5509 | 1 | 0 | 42
39016.553 | 2165 | 0 | 42
39016.5552 | 2155 | 0 | 42
39016.5573 | 2043 | 0 | 42
39016.5594 | 2254 | 0 | 42
39016.5616 | 2135 | 0 | 42
39016.5637 | 2554 | 0 | 42
42
39016.5466 | 1 | 0 | 43
39016.5488 | 1 | 0 | 43
39016.5509 | 1 | 0 | 43
39016.553 | 1 | 0 | 43
39016.5552 | 1583 | 387 | 43
39016.5573 | 2539 | 0 | 43
39016.5595 | 2501 | 0 | 43
39016.5616 | 2098 | 1 | 43
39016.5637 | 2040 | 65 | 43
43
39016.5466 | 1 | 0 | 44
39016.5488 | 1 | 0 | 44
39016.5509 | 1 | 0 | 44
39016.5531 | 1 | 0 | 44
39016.5552 | 1550 | 374 | 44
39016.5573 | 2263 | 0 | 44
39016.5595 | 2026 | 0 | 44
39016.5616 | 1953 | 1 | 44
39016.5638 | 1861 | 56 | 44
44
39016.5467 | 1 | 0 | 45
39016.5488 | 1 | 0 | 45
39016.5509 | 1 | 0 | 45
39016.5531 | 1 | 0 | 45
39016.5552 | 1875 | 0 | 45
39016.5573 | 2182 | 0 | 45
39016.5595 | 2457 | 0 | 45
39016.5616 | 1932 | 0 | 45
39016.5638 | 1981 | 0 | 45
45
39016.5467 | 1 | 0 | 46
39016.5488 | 1 | 0 | 46
39016.5509 | 1 | 0 | 46
39016.5531 | 1 | 0 | 46
39016.5552 | 1605 | 0 | 46
39016.5574 | 2368 | 0 | 46
39016.5595 | 2423 | 0 | 46
39016.5616 | 2326 | 0 | 46
39016.5638 | 1867 | 0 | 46
46
39016.5467 | 1 | 0 | 47
39016.5488 | 1 | 0 | 47
39016.551 | 1 | 0 | 47
39016.5531 | 1 | 0 | 47
39016.5552 | 1721 | 0 | 47
39016.5574 | 2468 | 0 | 47
39016.5595 | 2508 | 0 | 47
39016.5617 | 1939 | 0 | 47
39016.5638 | 1950 | 0 | 47
47
39016.5467 | 1 | 0 | 48
39016.5488 | 1 | 0 | 48
39016.551 | 1 | 0 | 48
39016.5531 | 1 | 0 | 48
39016.5553 | 1689 | 0 | 48
39016.5574 | 2016 | 0 | 48
39016.5595 | 2527 | 0 | 48
39016.5617 | 2473 | 0 | 48
39016.5638 | 2162 | 0 | 48
48
39016.5467 | 1 | 0 | 49
39016.5489 | 1 | 0 | 49
39016.551 | 1 | 0 | 49
39016.5531 | 1 | 0 | 49
39016.5553 | 2051 | 0 | 49
39016.5574 | 2456 | 0 | 49
39016.5595 | 2009 | 0 | 49
39016.5617 | 1906 | 0 | 49
39016.5638 | 2066 | 0 | 49
49
39016.5467 | 1 | 0 | 50
39016.5489 | 1 | 0 | 50
39016.551 | 1 | 0 | 50
39016.5532 | 2535 | 0 | 50
39016.5553 | 2340 | 0 | 50
39016.5574 | 2034 | 0 | 50
39016.5596 | 2623 | 0 | 50
39016.5617 | 2572 | 0 | 50
39016.5638 | 2422 | 0 | 50
50
39016.5468 | 1 | 0 | 51
39016.5489 | 0 | 0 | 51
39016.551 | 1 | 0 | 51
39016.5532 | 1 | 0 | 51
39016.5553 | 1705 | 0 | 51
39016.5574 | 2133 | 0 | 51
39016.5596 | 2095 | 0 | 51
39016.5617 | 2231 | 0 | 51
39016.5639 | 2115 | 0 | 51
51
39016.5468 | 1 | 0 | 52
39016.5489 | 1 | 0 | 52
39016.551 | 1 | 0 | 52
39016.5532 | 2528 | 0 | 52
39016.5553 | 2579 | 0 | 52
39016.5575 | 2386 | 0 | 52
39016.5596 | 2240 | 0 | 52
39016.5617 | 2539 | 0 | 52
39016.5639 | 2159 | 0 | 52
52
39016.5468 | 1 | 0 | 53
39016.5489 | 1 | 0 | 53
39016.5511 | 1 | 0 | 53
39016.5532 | 1 | 0 | 53
39016.5553 | 1774 | 0 | 53
39016.5575 | 2400 | 0 | 53
39016.5596 | 2450 | 0 | 53
39016.5618 | 2449 | 0 | 53
39016.5639 | 1989 | 0 | 53
53
39016.5468 | 1 | 0 | 54
39016.5489 | 1 | 0 | 54
39016.5511 | 1560 | 0 | 54
39016.5532 | 2136 | 0 | 54
39016.5554 | 2220 | 0 | 54
39016.5575 | 2062 | 0 | 54
39016.5596 | 2360 | 0 | 54
39016.5618 | 2479 | 0 | 54
39016.5639 | 2148 | 0 | 54
54
39016.5468 | 1 | 0 | 55
39016.549 | 1 | 0 | 55
39016.5511 | 1 | 0 | 55
39016.5532 | 1 | 0 | 55
39016.5554 | 1327 | 0 | 55
39016.5575 | 2367 | 0 | 55
39016.5597 | 2058 | 0 | 55
39016.5618 | 2448 | 0 | 55
39016.5639 | 1997 | 0 | 55
55
39016.5468 | 1 | 0 | 56
39016.549 | 1 | 0 | 56
39016.5511 | 578 | 0 | 56
39016.5533 | 2314 | 0 | 56
39016.5554 | 2325 | 0 | 56
39016.5575 | 2373 | 0 | 56
39016.5597 | 2561 | 0 | 56
39016.5618 | 2457 | 0 | 56
39016.5639 | 2124 | 0 | 56
56
39016.5469 | 0 | 0 | 57
39016.549 | 1 | 0 | 57
39016.5511 | 1 | 0 | 57
39016.5533 | 1 | 0 | 57
39016.5554 | 1702 | 0 | 57
39016.5575 | 1986 | 0 | 57
39016.5597 | 2346 | 0 | 57
39016.5618 | 2446 | 0 | 57
39016.564 | 1888 | 0 | 57
57
39016.5469 | 1 | 0 | 58
39016.549 | 1 | 0 | 58
39016.5511 | 1 | 0 | 58
39016.5533 | 2540 | 0 | 58
39016.5554 | 2215 | 0 | 58
39016.5576 | 2579 | 0 | 58
39016.5597 | 2387 | 0 | 58
39016.5618 | 2286 | 0 | 58
39016.564 | 2263 | 0 | 58
58
39016.5469 | 1 | 0 | 59
39016.549 | 1 | 0 | 59
39016.5512 | 1 | 0 | 59
39016.5533 | 1 | 0 | 59
39016.5554 | 1892 | 0 | 59
39016.5576 | 2082 | 0 | 59
39016.5597 | 2470 | 0 | 59
39016.5619 | 2251 | 0 | 59
39016.564 | 1982 | 0 | 59
59
39016.5469 | 1 | 0 | 60
39016.549 | 1 | 0 | 60
39016.5512 | 1 | 0 | 60
39016.5533 | 2327 | 0 | 60
39016.5555 | 2242 | 0 | 60
39016.5576 | 2162 | 0 | 60
39016.5597 | 2300 | 0 | 60
39016.5619 | 2070 | 0 | 60
39016.564 | 2008 | 0 | 60
60
39016.5469 | 1 | 0 | 61
39016.5491 | 1 | 0 | 61
39016.5512 | 1 | 0 | 61
39016.5533 | 1 | 0 | 61
39016.5555 | 1792 | 0 | 61
39016.5576 | 2276 | 0 | 61
39016.5597 | 2504 | 0 | 61
39016.5619 | 2228 | 0 | 61
39016.564 | 1801 | 0 | 61
61
39016.5469 | 1 | 0 | 62
39016.5491 | 1 | 0 | 62
39016.5512 | 0 | 0 | 62
39016.5533 | 1 | 0 | 62
39016.5555 | 1831 | 0 | 62
39016.5576 | 2106 | 0 | 62
39016.5598 | 2142 | 0 | 62
39016.5619 | 2174 | 0 | 62
39016.564 | 2216 | 0 | 62
62
39016.5469 | 1 | 0 | 63
39016.5491 | 1 | 0 | 63
39016.5512 | 1 | 0 | 63
39016.5534 | 1 | 0 | 63
39016.5555 | 2222 | 0 | 63
39016.5576 | 2012 | 0 | 63
39016.5598 | 2125 | 0 | 63
39016.5619 | 2017 | 0 | 63
39016.5641 | 2041 | 0 | 63
63
39016.547 | 1 | 0 | 64
39016.5491 | 1 | 0 | 64
39016.5512 | 1 | 0 | 64
39016.5534 | 1 | 0 | 64
39016.5555 | 1939 | 0 | 64
39016.5577 | 2121 | 0 | 64
39016.5598 | 2013 | 0 | 64
39016.5619 | 1912 | 0 | 64
39016.5641 | 1967 | 0 | 64
64
39016.547 | 1 | 0 | 65
39016.5491 | 1 | 0 | 65
39016.5513 | 1 | 0 | 65
39016.5534 | 1 | 0 | 65
39016.5555 | 2282 | 0 | 65
39016.5577 | 2534 | 0 | 65
39016.5598 | 2212 | 0 | 65
39016.562 | 2421 | 0 | 65
39016.5641 | 2183 | 0 | 65
65
39016.547 | 1 | 0 | 66
39016.5491 | 1 | 0 | 66
39016.5513 | 1 | 0 | 66
39016.5534 | 2195 | 0 | 66
39016.5556 | 2144 | 0 | 66
39016.5577 | 2441 | 0 | 66
39016.5598 | 2110 | 0 | 66
39016.562 | 2311 | 0 | 66
39016.5641 | 1841 | 0 | 66
66
39016.547 | 1 | 0 | 67
39016.5492 | 1 | 0 | 67
39016.5513 | 1 | 0 | 67
39016.5534 | 1 | 0 | 67
39016.5556 | 2055 | 0 | 67
39016.5577 | 2092 | 0 | 67
39016.5598 | 2315 | 0 | 67
39016.562 | 2164 | 0 | 67
39016.5641 | 2331 | 0 | 67
67
39016.547 | 1 | 0 | 68
39016.5492 | 1 | 0 | 68
39016.5513 | 1 | 0 | 68
39016.5534 | 2428 | 0 | 68
39016.5556 | 2566 | 0 | 68
39016.5577 | 2372 | 0 | 68
39016.5599 | 2506 | 0 | 68
39016.562 | 2032 | 0 | 68
39016.5641 | 2014 | 0 | 68
68
39016.547 | 1 | 0 | 69
39016.5492 | 1 | 0 | 69
39016.5513 | 1 | 0 | 69
39016.5535 | 1 | 0 | 69
39016.5556 | 2048 | 0 | 69
39016.5577 | 2368 | 0 | 69
39016.5599 | 2374 | 0 | 69
39016.562 | 1875 | 0 | 69
39016.5642 | 2153 | 0 | 69
69
39016.5471 | 1 | 0 | 70
39016.5492 | 1 | 0 | 70
39016.5513 | 1727 | 0 | 70
39016.5535 | 2578 | 0 | 70
39016.5556 | 2548 | 0 | 70
39016.5578 | 2198 | 0 | 70
39016.5599 | 2631 | 0 | 70
39016.562 | 2371 | 0 | 70
39016.5642 | 2208 | 0 | 70
70
39016.5471 | 1 | 0 | 71
39016.5492 | 1 | 0 | 71
39016.5514 | 1 | 0 | 71
39016.5535 | 1 | 0 | 71
39016.5556 | 2028 | 0 | 71
39016.5578 | 2212 | 0 | 71
39016.5599 | 2316 | 0 | 71
39016.562 | 2296 | 0 | 71
39016.5642 | 2032 | 0 | 71
71
39016.5471 | 1 | 0 | 72
39016.5492 | 1 | 0 | 72
39016.5514 | 2110 | 0 | 72
39016.5535 | 2540 | 0 | 72
39016.5556 | 2034 | 0 | 72
39016.5578 | 2407 | 0 | 72
39016.5599 | 2410 | 0 | 72
39016.5621 | 2334 | 0 | 72
39016.5642 | 2360 | 0 | 72
72
39016.5471 | 0 | 0 | 73
39016.5492 | 1 | 0 | 73
39016.5514 | 1 | 0 | 73
39016.5535 | 1 | 0 | 73
39016.5557 | 2283 | 0 | 73
39016.5578 | 2546 | 0 | 73
39016.5599 | 1990 | 0 | 73
39016.5621 | 2375 | 0 | 73
39016.5642 | 2367 | 0 | 73
73
39016.5471 | 1 | 0 | 74
39016.5493 | 1 | 0 | 74
39016.5514 | 1 | 0 | 74
39016.5535 | 2211 | 0 | 74
39016.5557 | 2104 | 0 | 74
39016.5578 | 2220 | 0 | 74
39016.56 | 2041 | 0 | 74
39016.5621 | 2441 | 0 | 74
39016.5642 | 2085 | 0 | 74
74
39016.5471 | 1 | 0 | 75
39016.5493 | 1 | 0 | 75
39016.5514 | 1 | 0 | 75
39016.5536 | 1 | 0 | 75
39016.5557 | 1916 | 0 | 75
39016.5578 | 2297 | 0 | 75
39016.56 | 2452 | 0 | 75
39016.5621 | 2147 | 0 | 75
39016.5642 | 1976 | 0 | 75
75
39016.5472 | 1 | 0 | 76
39016.5493 | 1 | 0 | 76
39016.5514 | 1 | 0 | 76
39016.5536 | 2236 | 0 | 76
39016.5557 | 2346 | 0 | 76
39016.5578 | 2079 | 0 | 76
39016.56 | 2451 | 0 | 76
39016.5621 | 2419 | 0 | 76
39016.5643 | 2167 | 0 | 76
76
39016.5472 | 1 | 0 | 77
39016.5493 | 1 | 0 | 77
39016.5514 | 1 | 0 | 77
39016.5536 | 1 | 0 | 77
39016.5557 | 1831 | 211 | 77
39016.5579 | 2413 | 0 | 77
39016.56 | 2524 | 0 | 77
39016.5621 | 2393 | 0 | 77
39016.5643 | 2254 | 0 | 77
77
39016.5472 | 1 | 0 | 78
39016.5493 | 1 | 0 | 78
39016.5515 | 1 | 0 | 78
39016.5536 | 1 | 0 | 78
39016.5557 | 1993 | 152 | 78
39016.5579 | 2529 | 0 | 78
39016.56 | 2149 | 0 | 78
39016.5622 | 2431 | 0 | 78
39016.5643 | 2091 | 0 | 78
78
39016.5472 | 1 | 0 | 79
39016.5493 | 1 | 0 | 79
39016.5515 | 1 | 0 | 79
39016.5536 | 1 | 0 | 79
39016.5558 | 2023 | 0 | 79
39016.5579 | 2337 | 0 | 79
39016.56 | 2512 | 0 | 79
39016.5622 | 2203 | 0 | 79
39016.5643 | 2308 | 0 | 79
79
39016.5472 | 1 | 0 | 80
39016.5494 | 1 | 0 | 80
39016.5515 | 1 | 0 | 80
39016.5536 | 2378 | 0 | 80
39016.5558 | 2016 | 0 | 80
39016.5579 | 2293 | 0 | 80
39016.5601 | 2471 | 0 | 80
39016.5622 | 2102 | 0 | 80
39016.5643 | 2350 | 0 | 80
80
39016.5472 | 1 | 0 | 81
39016.5494 | 1 | 0 | 81
39016.5515 | 1 | 0 | 81
39016.5537 | 2 | 0 | 81
39016.5558 | 1974 | 0 | 81
39016.5579 | 2019 | 0 | 81
39016.5601 | 2499 | 0 | 81
39016.5622 | 2484 | 0 | 81
39016.5644 | 2259 | 0 | 81
81
39016.5473 | 1 | 0 | 82
39016.5494 | 1 | 0 | 82
39016.5515 | 1 | 0 | 82
39016.5537 | 2060 | 0 | 82
39016.5558 | 2429 | 0 | 82
39016.558 | 2265 | 0 | 82
39016.5601 | 2423 | 0 | 82
39016.5622 | 2444 | 0 | 82
39016.5644 | 2380 | 0 | 82
82
39016.5473 | 1 | 0 | 83
39016.5494 | 1 | 0 | 83
39016.5516 | 1 | 0 | 83
39016.5537 | 1 | 0 | 83
39016.5558 | 2310 | 0 | 83
39016.558 | 2448 | 0 | 83
39016.5601 | 2052 | 0 | 83
39016.5622 | 1927 | 0 | 83
39016.5644 | 1806 | 0 | 83
83
39016.5473 | 1 | 0 | 84
39016.5494 | 1 | 0 | 84
39016.5516 | 1270 | 0 | 84
39016.5537 | 2608 | 0 | 84
39016.5558 | 2316 | 0 | 84
39016.558 | 2623 | 0 | 84
39016.5601 | 2023 | 0 | 84
39016.5623 | 2547 | 0 | 84
39016.5644 | 2024 | 0 | 84
84
39016.5473 | 1 | 0 | 85
39016.5494 | 1 | 0 | 85
39016.5516 | 1 | 0 | 85
39016.5537 | 1 | 0 | 85
39016.5559 | 2117 | 0 | 85
39016.558 | 2143 | 0 | 85
39016.5601 | 2264 | 0 | 85
39016.5623 | 2219 | 0 | 85
39016.5644 | 1902 | 0 | 85
85
39016.5473 | 1 | 0 | 86
39016.5495 | 1 | 0 | 86
39016.5516 | 2561 | 0 | 86
39016.5537 | 2591 | 0 | 86
39016.5559 | 2100 | 0 | 86
39016.558 | 2127 | 0 | 86
39016.5602 | 2382 | 0 | 86
39016.5623 | 2444 | 0 | 86
39016.5644 | 2175 | 0 | 86
86
39016.5473 | 1 | 0 | 87
39016.5495 | 1 | 0 | 87
39016.5516 | 1 | 0 | 87
39016.5537 | 1 | 0 | 87
39016.5559 | 2163 | 0 | 87
39016.558 | 2163 | 0 | 87
39016.5602 | 2549 | 0 | 87
39016.5623 | 2172 | 0 | 87
39016.5644 | 1971 | 0 | 87
87
39016.5473 | 1 | 0 | 88
39016.5495 | 1 | 0 | 88
39016.5516 | 1 | 0 | 88
39016.5538 | 2564 | 0 | 88
39016.5559 | 2005 | 0 | 88
39016.558 | 2083 | 0 | 88
39016.5602 | 2083 | 0 | 88
39016.5623 | 2155 | 0 | 88
39016.5645 | 2117 | 0 | 88
88
39016.5474 | 0 | 0 | 89
39016.5495 | 1 | 0 | 89
39016.5516 | 1 | 0 | 89
39016.5538 | 1 | 0 | 89
39016.5559 | 2104 | 0 | 89
39016.5581 | 2577 | 0 | 89
39016.5602 | 2508 | 0 | 89
39016.5623 | 2176 | 0 | 89
39016.5645 | 2173 | 0 | 89
89
39016.5474 | 0 | 0 | 90
39016.5495 | 1 | 0 | 90
39016.5517 | 1 | 0 | 90
39016.5538 | 2399 | 0 | 90
39016.5559 | 2560 | 0 | 90
39016.5581 | 2066 | 0 | 90
39016.5602 | 2453 | 0 | 90
39016.5624 | 2400 | 0 | 90
39016.5645 | 2050 | 0 | 90
90
39016.5474 | 1 | 0 | 91
39016.5495 | 1 | 0 | 91
39016.5517 | 1 | 0 | 91
39016.5538 | 1 | 0 | 91
39016.556 | 1838 | 0 | 91
39016.5581 | 2137 | 0 | 91
39016.5602 | 2441 | 0 | 91
39016.5624 | 2079 | 0 | 91
39016.5645 | 1835 | 0 | 91
91
39016.5474 | 1 | 0 | 92
39016.5496 | 1 | 0 | 92
39016.5517 | 1 | 0 | 92
39016.5538 | 2234 | 0 | 92
39016.556 | 2309 | 0 | 92
39016.5581 | 2054 | 0 | 92
39016.5603 | 2097 | 0 | 92
39016.5624 | 1972 | 0 | 92
39016.5645 | 1828 | 0 | 92
92
39016.5474 | 1 | 0 | 93
39016.5496 | 1 | 0 | 93
39016.5517 | 1 | 0 | 93
39016.5539 | 1 | 0 | 93
39016.556 | 1845 | 0 | 93
39016.5581 | 2195 | 0 | 93
39016.5603 | 2396 | 0 | 93
39016.5624 | 2042 | 0 | 93
39016.5645 | 1863 | 0 | 93
93
39016.5475 | 1 | 0 | 94
39016.5496 | 1 | 0 | 94
39016.5517 | 1 | 0 | 94
39016.5539 | 2347 | 0 | 94
39016.556 | 2171 | 0 | 94
39016.5581 | 2218 | 0 | 94
39016.5603 | 2210 | 0 | 94
39016.5624 | 2144 | 0 | 94
39016.5646 | 1922 | 0 | 94
94
39016.5475 | 1 | 0 | 95
39016.5496 | 1 | 0 | 95
39016.5517 | 1 | 0 | 95
39016.5539 | 1 | 0 | 95
39016.556 | 1421 | 0 | 95
39016.5582 | 2193 | 0 | 95
39016.5603 | 2517 | 0 | 95
39016.5624 | 1881 | 0 | 95
39016.5646 | 1921 | 0 | 95
95
39016.5475 | 1 | 0 | 96
39016.5496 | 1 | 0 | 96
39016.5518 | 2213 | 0 | 96
39016.5539 | 2354 | 0 | 96
39016.556 | 2172 | 0 | 96
39016.5582 | 2630 | 0 | 96
39016.5603 | 2615 | 0 | 96
39016.5625 | 2045 | 0 | 96
39016.5646 | 2435 | 0 | 96
96
39016.5475 | 1 | 0 | 97
39016.5496 | 1 | 0 | 97
39016.5518 | 1 | 0 | 97
39016.5539 | 1 | 0 | 97
39016.5561 | 2307 | 0 | 97
39016.5582 | 1959 | 0 | 97
39016.5603 | 2139 | 0 | 97
39016.5625 | 1930 | 0 | 97
39016.5646 | 2259 | 0 | 97
97
39016.5475 | 1 | 0 | 98
39016.5497 | 1 | 0 | 98
39016.5518 | 2548 | 0 | 98
39016.5539 | 2532 | 0 | 98
39016.5561 | 2525 | 0 | 98
39016.5582 | 2151 | 0 | 98
39016.5603 | 2431 | 0 | 98
39016.5625 | 2623 | 0 | 98
39016.5646 | 2605 | 0 | 98
98
39016.5475 | 0 | 0 | 99
39016.5497 | 1 | 0 | 99
39016.5518 | 1 | 0 | 99
39016.5539 | 1 | 0 | 99
39016.5561 | 1746 | 0 | 99
39016.5582 | 2215 | 0 | 99
39016.5604 | 2511 | 0 | 99
39016.5625 | 2277 | 0 | 99
39016.5646 | 1767 | 0 | 99
99
39016.5475 | 1 | 0 | 100
39016.5497 | 1 | 0 | 100
39016.5518 | 40 | 0 | 100
39016.554 | 2541 | 0 | 100
39016.5561 | 2563 | 0 | 100
39016.5582 | 2095 | 0 | 100
39016.5604 | 2034 | 0 | 100
39016.5625 | 2260 | 0 | 100
39016.5647 | 2095 | 0 | 100
100
39016.5476 | 1 | 0 | 101
39016.5497 | 1 | 0 | 101
39016.5518 | 1 | 0 | 101
39016.554 | 1 | 0 | 101
39016.5561 | 1680 | 0 | 101
39016.5583 | 2371 | 0 | 101
39016.5604 | 2519 | 0 | 101
39016.5625 | 1980 | 0 | 101
39016.5647 | 1826 | 0 | 101
101
39016.5476 | 1 | 0 | 102
39016.5497 | 1 | 0 | 102
39016.5519 | 1 | 0 | 102
39016.554 | 2204 | 0 | 102
39016.5561 | 2338 | 0 | 102
39016.5583 | 2163 | 0 | 102
39016.5604 | 2328 | 0 | 102
39016.5625 | 2563 | 0 | 102
39016.5647 | 2049 | 0 | 102
102
39016.5476 | 1 | 0 | 103
39016.5497 | 1 | 0 | 103
39016.5519 | 998 | 843 | 103
39016.554 | 2421 | 0 | 103
39016.5561 | 2596 | 0 | 103
39016.5583 | 2061 | 0 | 103
39016.5604 | 2435 | 0 | 103
39016.5626 | 1983 | 0 | 103
39016.5647 | 1957 | 114 | 103
103
39016.5476 | 1 | 0 | 104
39016.5498 | 1 | 0 | 104
39016.5519 | 1020 | 770 | 104
39016.554 | 2568 | 0 | 104
39016.5562 | 2543 | 0 | 104
39016.5583 | 2484 | 0 | 104
39016.5604 | 2187 | 0 | 104
39016.5626 | 2096 | 0 | 104
39016.5647 | 1947 | 110 | 104
104
39016.5476 | 1 | 0 | 105
39016.5498 | 1 | 0 | 105
39016.5519 | 151 | 0 | 105
39016.554 | 2076 | 0 | 105
39016.5562 | 2002 | 0 | 105
39016.5583 | 2547 | 0 | 105
39016.5605 | 2157 | 0 | 105
39016.5626 | 2078 | 0 | 105
39016.5647 | 2007 | 0 | 105
105
39016.5476 | 1 | 0 | 106
39016.5498 | 1 | 0 | 106
39016.5519 | 1869 | 0 | 106
39016.5541 | 2280 | 0 | 106
39016.5562 | 2100 | 0 | 106
39016.5583 | 2603 | 0 | 106
39016.5605 | 2467 | 0 | 106
39016.5626 | 2221 | 0 | 106
39016.5648 | 2273 | 0 | 106
106
39016.5477 | 1 | 0 | 107
39016.5498 | 1 | 0 | 107
39016.5519 | 756 | 0 | 107
39016.5541 | 2358 | 0 | 107
39016.5562 | 2021 | 0 | 107
39016.5584 | 2247 | 0 | 107
39016.5605 | 2530 | 0 | 107
39016.5626 | 2497 | 0 | 107
39016.5648 | 2452 | 0 | 107
107
39016.5477 | 1 | 0 | 108
39016.5498 | 1 | 0 | 108
39016.552 | 2157 | 0 | 108
39016.5541 | 2496 | 0 | 108
39016.5562 | 2523 | 0 | 108
39016.5584 | 2139 | 0 | 108
39016.5605 | 2389 | 0 | 108
39016.5627 | 2069 | 0 | 108
39016.5648 | 2369 | 0 | 108
108
39016.5477 | 1 | 0 | 109
39016.5498 | 1 | 0 | 109
39016.552 | 1325 | 0 | 109
39016.5541 | 2343 | 0 | 109
39016.5563 | 2375 | 0 | 109
39016.5584 | 2106 | 0 | 109
39016.5605 | 2578 | 0 | 109
39016.5627 | 2081 | 0 | 109
39016.5648 | 2435 | 0 | 109
109
39016.5477 | 1 | 0 | 110
39016.5498 | 1 | 0 | 110
39016.552 | 102 | 0 | 110
39016.5541 | 1997 | 0 | 110
39016.5563 | 2562 | 0 | 110
39016.5584 | 2595 | 0 | 110
39016.5605 | 2163 | 0 | 110
39016.5627 | 2282 | 0 | 110
39016.5648 | 2473 | 0 | 110
110
39016.5477 | 1 | 0 | 111
39016.5499 | 1 | 0 | 111
39016.552 | 1416 | 0 | 111
39016.5541 | 2053 | 0 | 111
39016.5563 | 2126 | 0 | 111
39016.5584 | 2424 | 0 | 111
39016.5606 | 2570 | 0 | 111
39016.5627 | 2271 | 0 | 111
39016.5648 | 2276 | 0 | 111
111
39016.5477 | 1 | 0 | 112
39016.5499 | 1 | 0 | 112
39016.552 | 41 | 0 | 112
39016.5542 | 2574 | 0 | 112
39016.5563 | 2587 | 0 | 112
39016.5584 | 2550 | 0 | 112
39016.5606 | 2117 | 0 | 112
39016.5627 | 2331 | 0 | 112
39016.5648 | 2149 | 0 | 112
112
39016.5478 | 1 | 0 | 113
39016.552 | 1899 | 0 | 113
39016.5542 | 2245 | 0 | 113
39016.5563 | 2559 | 0 | 113
39016.5584 | 2025 | 0 | 113
39016.5606 | 2239 | 0 | 113
39016.5627 | 2504 | 0 | 113
39016.5649 | 2163 | 0 | 113
113
39016.5478 | 1 | 0 | 114
39016.5499 | 1 | 0 | 114
39016.552 | 2110 | 0 | 114
39016.5542 | 2206 | 0 | 114
39016.5563 | 2264 | 0 | 114
39016.5585 | 2536 | 0 | 114
39016.5606 | 2397 | 0 | 114
39016.5627 | 2038 | 0 | 114
39016.5649 | 2291 | 0 | 114
114
39016.5478 | 1 | 0 | 115
39016.5499 | 1 | 0 | 115
39016.5521 | 1913 | 0 | 115
39016.5542 | 1980 | 0 | 115
39016.5563 | 2196 | 0 | 115
39016.5585 | 2630 | 0 | 115
39016.5606 | 2598 | 0 | 115
39016.5628 | 2152 | 0 | 115
39016.5649 | 2063 | 0 | 115
115
39016.5478 | 1 | 0 | 116
39016.5499 | 1 | 0 | 116
39016.5521 | 2517 | 0 | 116
39016.5542 | 2160 | 0 | 116
39016.5564 | 2305 | 0 | 116
39016.5585 | 2488 | 0 | 116
39016.5606 | 2123 | 0 | 116
39016.5628 | 2538 | 0 | 116
39016.5649 | 2472 | 0 | 116
116
39016.5478 | 1 | 0 | 117
39016.55 | 1 | 0 | 117
39016.5521 | 1966 | 0 | 117
39016.5542 | 2035 | 0 | 117
39016.5564 | 2240 | 0 | 117
39016.5585 | 2453 | 0 | 117
39016.5607 | 2151 | 0 | 117
39016.5628 | 2319 | 0 | 117
39016.5649 | 2143 | 0 | 117
117
39016.5478 | 0 | 0 | 118
39016.55 | 1 | 0 | 118
39016.5521 | 464 | 0 | 118
39016.5543 | 2201 | 0 | 118
39016.5564 | 2115 | 0 | 118
39016.5585 | 2037 | 0 | 118
39016.5607 | 2481 | 0 | 118
39016.5628 | 2070 | 0 | 118
39016.565 | 2227 | 0 | 118
118
39016.5479 | 1 | 0 | 119
39016.55 | 0 | 0 | 119
39016.5521 | 1961 | 0 | 119
39016.5543 | 2257 | 0 | 119
39016.5564 | 2252 | 0 | 119
39016.5586 | 2062 | 0 | 119
39016.5607 | 2495 | 0 | 119
39016.5628 | 2326 | 0 | 119
39016.565 | 2163 | 0 | 119
119
39016.5479 | 1 | 0 | 120
39016.55 | 1 | 0 | 120
39016.5522 | 663 | 0 | 120
39016.5543 | 2023 | 0 | 120
39016.5564 | 2516 | 0 | 120
39016.5586 | 2545 | 0 | 120
39016.5607 | 2453 | 0 | 120
39016.5628 | 2573 | 0 | 120
39016.565 | 2370 | 0 | 120
120
39016.5479 | 1 | 0 | 121
39016.55 | 1 | 0 | 121
39016.5522 | 2060 | 0 | 121
39016.5543 | 2597 | 0 | 121
39016.5564 | 2318 | 0 | 121
39016.5586 | 2155 | 0 | 121
39016.5607 | 2279 | 0 | 121
39016.5629 | 2019 | 0 | 121
39016.565 | 2293 | 0 | 121
121
39016.5479 | 1 | 0 | 122
39016.55 | 1 | 0 | 122
39016.5522 | 2388 | 0 | 122
39016.5543 | 2552 | 0 | 122
39016.5565 | 2500 | 0 | 122
39016.5586 | 2449 | 0 | 122
39016.5607 | 2152 | 0 | 122
39016.5629 | 2111 | 0 | 122
39016.565 | 2578 | 0 | 122
122
39016.5479 | 1 | 0 | 123
39016.5501 | 1 | 0 | 123
39016.5522 | 2074 | 0 | 123
39016.5543 | 2388 | 0 | 123
39016.5565 | 2332 | 0 | 123
39016.5586 | 2184 | 0 | 123
39016.5608 | 2370 | 0 | 123
39016.5629 | 2470 | 0 | 123
39016.565 | 2053 | 0 | 123
123
39016.5479 | 1 | 0 | 124
39016.5501 | 1 | 0 | 124
39016.5522 | 604 | 0 | 124
39016.5544 | 2542 | 0 | 124
39016.5565 | 2587 | 0 | 124
39016.5586 | 2607 | 0 | 124
39016.5608 | 2230 | 0 | 124
39016.5629 | 2194 | 0 | 124
39016.565 | 1925 | 0 | 124
124
39016.548 | 1 | 0 | 125
39016.5501 | 1 | 0 | 125
39016.5522 | 2468 | 0 | 125
39016.5544 | 2461 | 0 | 125
39016.5565 | 2358 | 0 | 125
39016.5586 | 2195 | 0 | 125
39016.5608 | 2315 | 0 | 125
39016.5629 | 2457 | 0 | 125
39016.5651 | 2044 | 0 | 125
125
39016.548 | 1 | 0 | 126
39016.5501 | 1 | 0 | 126
39016.5522 | 1078 | 0 | 126
39016.5544 | 2476 | 0 | 126
39016.5565 | 2435 | 0 | 126
39016.5587 | 2445 | 0 | 126
39016.5608 | 2188 | 0 | 126
39016.5629 | 2200 | 0 | 126
39016.5651 | 2041 | 0 | 126
126
39016.548 | 1 | 0 | 127
39016.5501 | 1 | 0 | 127
39016.5523 | 2334 | 0 | 127
39016.5544 | 2382 | 0 | 127
39016.5565 | 2325 | 0 | 127
39016.5587 | 2141 | 0 | 127
39016.5608 | 2301 | 0 | 127
39016.563 | 2128 | 0 | 127
39016.5651 | 2017 | 0 | 127
127
39016.548 | 1 | 0 | 128
39016.5501 | 1 | 0 | 128
39016.5523 | 767 | 0 | 128
39016.5544 | 2580 | 0 | 128
39016.5566 | 2158 | 0 | 128
39016.5587 | 2355 | 0 | 128
39016.5608 | 2286 | 0 | 128
39016.563 | 2207 | 0 | 128
39016.5651 | 2110 | 0 | 128
128
39016.548 | 1 | 0 | 129
39016.5502 | 1 | 0 | 129
39016.5523 | 2464 | 0 | 129
39016.5544 | 2247 | 0 | 129
39016.5566 | 2395 | 0 | 129
39016.5587 | 2231 | 0 | 129
39016.5608 | 2586 | 0 | 129
39016.563 | 2175 | 0 | 129
39016.5651 | 2441 | 0 | 129
129
39016.548 | 1 | 0 | 130
39016.5502 | 1 | 0 | 130
39016.5523 | 1783 | 0 | 130
39016.5544 | 2116 | 0 | 130
39016.5566 | 2498 | 0 | 130
39016.5587 | 2430 | 0 | 130
39016.5609 | 2381 | 0 | 130
39016.563 | 2227 | 0 | 130
39016.5651 | 2119 | 0 | 130
130
39016.5481 | 1 | 0 | 131
39016.5502 | 1 | 0 | 131
39016.5523 | 1060 | 1 | 131
39016.5545 | 2355 | 0 | 131
39016.5566 | 2428 | 0 | 131
39016.5587 | 2616 | 0 | 131
39016.5609 | 2539 | 0 | 131
39016.563 | 2033 | 0 | 131
39016.5652 | 2067 | 1 | 131
131
39016.5481 | 1 | 0 | 132
39016.5502 | 1 | 0 | 132
39016.5523 | 1916 | 0 | 132
39016.5545 | 2412 | 0 | 132
39016.5566 | 2516 | 0 | 132
39016.5588 | 2493 | 0 | 132
39016.5609 | 2128 | 0 | 132
39016.563 | 1972 | 0 | 132
132

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -145 | 13.2 | 11.9 | 11.9 | 13.1 | 13.8
1 | -144 | 13.1 | 11.9 | 11.9 | 13 | 13.8
2 | -143 | 13.2 | 11.9 | 11.9 | 13.1 | 13.8
3 | -142 | 13.2 | 11.9 | 11.9 | 13 | 13.7
4 | -141 | 13.2 | 11.9 | 11.9 | 13 | 13.8
5 | -140 | 13.2 | 11.9 | 11.9 | 13 | 13.8
6 | -139 | 13.2 | 11.9 | 11.9 | 13 | 13.8
7 | -138 | 13.2 | 11.9 | 11.9 | 13 | 13.8
8 | -137 | 13.2 | 11.9 | 11.9 | 13 | 13.8
9 | -136 | 13.2 | 11.9 | 11.9 | 13 | 13.8
10 | -135 | 13.1 | 11.9 | 12 | 13 | 13.8
11 | -134 | 13.1 | 11.9 | 12 | 13 | 13.8
12 | -133 | 13.2 | 11.9 | 12 | 13.1 | 13.8
13 | -132 | 13.2 | 11.9 | 12 | 13 | 13.8
14 | -131 | 13.2 | 11.9 | 12 | 13 | 13.8
15 | -130 | 13.2 | 11.9 | 12 | 13.1 | 13.8
16 | -129 | 13.2 | 11.9 | 12 | 13 | 13.8
17 | -128 | 13.1 | 11.9 | 12 | 13 | 13.8
18 | -127 | 13.1 | 11.9 | 12 | 13 | 13.8
19 | -126 | 13.1 | 11.9 | 12 | 13 | 13.8
20 | -125 | 13.1 | 11.9 | 12 | 13 | 13.8
21 | -124 | 13.1 | 11.9 | 12 | 13 | 13.8
22 | -123 | 13.1 | 11.9 | 12 | 13 | 13.7
23 | -122 | 13.1 | 11.9 | 12 | 13 | 13.7
24 | -121 | 13.1 | 11.9 | 12 | 13 | 13.7
25 | -120 | 13.1 | 11.9 | 12 | 13 | 13.7
26 | -119 | 13.1 | 11.9 | 12 | 13 | 13.7
27 | -118 | 13.1 | 11.9 | 12 | 13 | 13.7
28 | -117 | 13.1 | 11.9 | 12 | 13 | 13.7
29 | -116 | 13.1 | 11.9 | 11.9 | 13 | 13.7
30 | -115 | 13.1 | 11.9 | 12 | 13 | 13.8
31 | -114 | 13.1 | 11.9 | 11.9 | 13 | 13.7
32 | -113 | 13.1 | 11.9 | 11.9 | 13 | 13.7
33 | -112 | 13.1 | 11.9 | 11.9 | 13 | 13.7
34 | -111 | 13.1 | 11.9 | 11.9 | 13 | 13.8
35 | -110 | 13.1 | 11.9 | 11.9 | 13 | 13.7
36 | -109 | 13.1 | 11.9 | 11.9 | 13 | 13.7
37 | -108 | 13.1 | 11.9 | 11.9 | 13 | 13.7
38 | -107 | 13.1 | 11.9 | 11.9 | 13 | 13.7
39 | -106 | 13.1 | 11.9 | 11.9 | 13 | 13.7
40 | -105 | 13.1 | 11.9 | 11.9 | 13 | 13.7
41 | -104 | 13.1 | 11.9 | 11.9 | 13 | 13.7
42 | -103 | 13.1 | 11.9 | 11.9 | 13 | 13.7
43 | -102 | 13.1 | 11.8 | 11.9 | 13 | 13.7
44 | -101 | 13.1 | 11.8 | 11.9 | 13 | 13.7
45 | -100 | 13.1 | 11.8 | 11.9 | 13 | 13.7
46 | -99 | 13.1 | 11.8 | 11.9 | 13 | 13.7
47 | -98 | 13.1 | 11.8 | 11.9 | 13 | 13.7
48 | -97 | 13.1 | 11.8 | 11.9 | 13 | 13.7
49 | -96 | 13.1 | 11.8 | 11.9 | 13 | 13.7
50 | -95 | 13.1 | 11.8 | 11.9 | 13 | 13.7
51 | -94 | 13.1 | 11.8 | 11.9 | 13 | 13.7
52 | -93 | 13.1 | 11.8 | 11.9 | 13 | 13.7
53 | -92 | 13.1 | 11.8 | 11.9 | 13 | 13.7
54 | -91 | 13.1 | 11.7 | 11.9 | 13 | 13.7
55 | -90 | 13.1 | 11.7 | 11.9 | 13 | 13.7
56 | -89 | 13.2 | 11.7 | 11.9 | 13 | 13.7
57 | -88 | 13.1 | 11.7 | 11.9 | 13 | 13.7
58 | -87 | 13.1 | 11.7 | 11.9 | 13 | 13.7
59 | -86 | 13.1 | 11.7 | 11.9 | 13 | 13.7
60 | -85 | 13.1 | 11.7 | 11.9 | 13 | 13.7
61 | -84 | 13.1 | 11.7 | 11.9 | 13 | 13.7
62 | -83 | 13.1 | 11.7 | 11.9 | 13 | 13.7
63 | -82 | 13.1 | 11.7 | 11.9 | 13 | 13.7
64 | -81 | 13.1 | 11.7 | 11.9 | 13 | 13.7
65 | -80 | 13.1 | 11.7 | 11.9 | 13 | 13.7
66 | -79 | 13.1 | 11.7 | 11.9 | 13 | 13.7
67 | -78 | 13.1 | 11.7 | 12 | 13 | 13.7
68 | -77 | 13.1 | 11.7 | 12 | 13 | 13.7
69 | -76 | 13.1 | 11.7 | 12 | 13 | 13.7
70 | -75 | 13.1 | 11.7 | 12 | 13 | 13.7
71 | -74 | 13.1 | 11.7 | 12 | 13 | 13.7
72 | -73 | 13.1 | 11.7 | 12 | 13 | 13.7
73 | -72 | 13.1 | 11.7 | 11.9 | 13 | 13.7
74 | -71 | 13.1 | 11.7 | 12 | 13 | 13.7
75 | -70 | 13.1 | 11.7 | 11.9 | 13 | 13.7
76 | -69 | 13.1 | 11.7 | 12 | 13 | 13.7
77 | -68 | 13.1 | 11.7 | 11.9 | 13 | 13.8
78 | -67 | 13.1 | 11.7 | 12 | 13 | 13.7
79 | -66 | 13.1 | 11.7 | 11.9 | 13 | 13.7
80 | -65 | 13.1 | 11.7 | 11.9 | 13 | 13.7
81 | -64 | 13.1 | 11.7 | 11.9 | 13 | 13.7
82 | -63 | 13.1 | 11.7 | 11.9 | 13 | 13.7
83 | -62 | 13.1 | 11.7 | 11.9 | 13 | 13.7
84 | -61 | 13.1 | 11.7 | 11.9 | 13 | 13.8
85 | -60 | 13.1 | 11.7 | 11.9 | 13 | 13.7
86 | -59 | 13.1 | 11.7 | 11.9 | 13 | 13.7
87 | -58 | 13.1 | 11.7 | 11.9 | 13 | 13.7
88 | -57 | 13.1 | 11.7 | 11.9 | 13 | 13.7
89 | -56 | 13.1 | 11.7 | 11.9 | 13 | 13.7
90 | -55 | 13.1 | 11.7 | 11.9 | 13 | 13.7
91 | -54 | 13.1 | 11.7 | 11.9 | 13 | 13.8
92 | -53 | 13.1 | 11.7 | 11.9 | 13 | 13.7
93 | -52 | 13.1 | 11.7 | 11.9 | 13 | 13.7
94 | -51 | 13.1 | 11.7 | 11.9 | 13 | 13.7
95 | -50 | 13.1 | 11.7 | 11.9 | 13 | 13.7
96 | -49 | 13.1 | 11.7 | 11.9 | 13 | 13.7
97 | -48 | 13.1 | 11.7 | 11.9 | 13 | 13.7
98 | -47 | 13.1 | 11.7 | 11.9 | 13 | 13.7
99 | -46 | 13.1 | 11.7 | 11.9 | 13 | 13.7
100 | -45 | 13.1 | 11.7 | 11.9 | 13 | 13.7
101 | -44 | 13.1 | 11.7 | 11.9 | 13 | 13.7
102 | -43 | 13.1 | 11.7 | 11.9 | 13 | 13.7
103 | -42 | 13.1 | 11.8 | 11.9 | 13 | 13.7
104 | -41 | 13.1 | 11.8 | 11.9 | 13 | 13.7
105 | -40 | 13.1 | 11.8 | 11.9 | 13 | 13.7
106 | -39 | 13.1 | 11.8 | 11.9 | 13 | 13.7
107 | -38 | 13.1 | 11.8 | 11.9 | 13 | 13.7
108 | -37 | 13.1 | 11.8 | 11.9 | 13 | 13.7
109 | -36 | 13.1 | 11.8 | 11.9 | 13 | 13.7
110 | -35 | 13.1 | 11.8 | 11.9 | 13 | 13.7
111 | -34 | 13.1 | 11.8 | 11.9 | 13 | 13.7
112 | -33 | 13.1 | 11.8 | 11.9 | 13 | 13.7
113 | -32 | 13.1 | 11.8 | 11.9 | 13 | 13.7
114 | -31 | 13.1 | 11.8 | 11.9 | 13 | 13.7
115 | -30 | 13.1 | 11.8 | 11.9 | 13 | 13.7
116 | -29 | 13.1 | 11.8 | 11.9 | 13 | 13.7
117 | -28 | 13.1 | 11.8 | 11.9 | 13 | 13.7
118 | -27 | 13.1 | 11.8 | 11.9 | 13 | 13.7
119 | -26 | 13.1 | 11.8 | 11.9 | 13 | 13.7
120 | -25 | 13.1 | 11.8 | 12 | 13 | 13.7
121 | -24 | 13.1 | 11.8 | 12 | 13 | 13.8
122 | -23 | 13.1 | 11.8 | 12 | 13 | 13.7
123 | -22 | 13.1 | 11.8 | 12 | 13 | 13.7
124 | -21 | 13.1 | 11.8 | 12 | 13 | 13.8
125 | -20 | 13.1 | 11.8 | 11.9 | 13 | 13.8
126 | -19 | 13.1 | 11.8 | 11.9 | 13 | 13.8
127 | -18 | 13.1 | 11.8 | 11.9 | 13 | 13.8
128 | -17 | 13.1 | 11.8 | 11.9 | 13 | 13.8
129 | -16 | 13.1 | 11.8 | 11.9 | 13 | 13.7
130 | -15 | 13.1 | 11.8 | 11.9 | 13 | 13.7
131 | -14 | 13.1 | 11.8 | 11.9 | 13 | 13.8
132 | -13 | 13.1 | 11.8 | 11.9 | 13 | 13.8
133 | -12 | 13.1 | 11.8 | 11.9 | 13 | 13.8
134 | -11 | 13.1 | 11.8 | 11.9 | 13 | 13.8
135 | -10 | 13.1 | 11.8 | 11.9 | 13 | 13.7
136 | -9 | 13.1 | 11.8 | 11.9 | 13 | 13.8
137 | -8 | 13.1 | 11.8 | 11.9 | 13 | 13.8
138 | -7 | 13.1 | 11.8 | 12 | 13 | 13.8
139 | -6 | 13.1 | 11.8 | 12 | 13 | 13.8
140 | -5 | 13.1 | 11.9 | 12 | 13 | 13.8
141 | -4 | 13.1 | 11.9 | 12 | 13 | 13.8
142 | -3 | 13.1 | 11.9 | 12 | 13 | 13.8
143 | -2 | 13.1 | 11.9 | 12 | 13 | 13.8
144 | -1 | 13.1 | 11.9 | 11.9 | 13 | 13.8
145 | 0 | 13.1 | 11.9 | 12 | 13 | 13.8
146 | 1 | 13.1 | 11.9 | 12 | 13 | 13.8
147 | 2 | 13.1 | 11.9 | 12 | 13 | 13.8
148 | 3 | 13.1 | 11.9 | 12 | 13 | 13.8
149 | 4 | 13.1 | 11.9 | 12.2 | 13 | 13.8
150 | 5 | 13.1 | 14.4 | 23.1 | 13.1 | 14.6
151 | 6 | 13.1 | 25.3 | 51.6 | 13.3 | 17.9
152 | 7 | 13.1 | 41.2 | 89.4 | 13.7 | 22.2
153 | 8 | 13.1 | 56 | 113.2 | 14 | 27.3
154 | 9 | 13.1 | 82.4 | 164 | 14.6 | 35.3
155 | 10 | 13.1 | 108.3 | 210.2 | 15.4 | 44.5
156 | 11 | 13.2 | 123 | 236.4 | 15.9 | 48.6
157 | 12 | 13.2 | 143.2 | 268.8 | 16.3 | 55.1
158 | 13 | 13.2 | 161 | 294.5 | 16.8 | 62.6
159 | 14 | 13.3 | 188.7 | 330.3 | 17.2 | 74.2
160 | 15 | 13.3 | 218 | 379.5 | 17.8 | 85.4
161 | 16 | 13.4 | 259.4 | 431.9 | 18.7 | 99.5
162 | 17 | 13.5 | 291.3 | 456.8 | 19.6 | 109.9
163 | 18 | 13.6 | 304.3 | 467.2 | 20.1 | 114.3
164 | 19 | 13.7 | 326.8 | 510.2 | 20.8 | 127.6
165 | 20 | 13.9 | 350.4 | 546.7 | 21.6 | 143.8
166 | 21 | 14 | 374 | 564.8 | 22.4 | 155.6
167 | 22 | 14.2 | 391.3 | 576.6 | 23.3 | 162.4
168 | 23 | 14.5 | 400.6 | 585.1 | 24.2 | 167.1
169 | 24 | 14.8 | 409.2 | 604.3 | 25.1 | 173
170 | 25 | 15.1 | 413.5 | 607.2 | 27.3 | 177.4
171 | 26 | 15.5 | 419 | 613.5 | 30.1 | 183.1
172 | 27 | 15.9 | 435.5 | 630.6 | 34 | 192.9
173 | 28 | 16.4 | 443.6 | 643.2 | 36.8 | 199.9
174 | 29 | 16.9 | 458.8 | 667.1 | 39.8 | 209.2
175 | 30 | 17.5 | 461.8 | 672.9 | 41.6 | 217.9
176 | 31 | 18.1 | 458.8 | 657.6 | 42.3 | 221.1
177 | 32 | 18.8 | 452.1 | 645.3 | 42.9 | 224.6
178 | 33 | 19.5 | 447.7 | 640 | 43.6 | 227.4
179 | 34 | 20.2 | 449.9 | 659.2 | 45.7 | 233.2
180 | 35 | 21 | 452.2 | 657.2 | 47.8 | 239.5
181 | 36 | 21.7 | 450.1 | 644.8 | 48.3 | 241.6
182 | 37 | 22.5 | 448.2 | 631.1 | 49.2 | 244
183 | 38 | 23.2 | 444.4 | 627.3 | 50.4 | 247.6
184 | 39 | 24 | 444.2 | 630.6 | 51.9 | 252.7
185 | 40 | 24.8 | 443.7 | 634.8 | 53.1 | 256.6
186 | 41 | 25.6 | 447.5 | 650.2 | 55.2 | 261.8
187 | 42 | 26.4 | 454.7 | 670.5 | 57.2 | 266.6
188 | 43 | 27.3 | 464.2 | 696.4 | 60 | 272.3
189 | 44 | 28.2 | 478.7 | 719.4 | 64.5 | 281.8
190 | 45 | 29.1 | 492 | 736.4 | 69.5 | 292
191 | 46 | 30.1 | 501.7 | 748.8 | 74.2 | 299
192 | 47 | 31.1 | 509.1 | 754.1 | 79 | 307.8
193 | 48 | 32.3 | 510.9 | 757.2 | 83.2 | 313.4
194 | 49 | 33.5 | 513.9 | 758.5 | 87.1 | 321.1
195 | 50 | 34.7 | 516.6 | 764.2 | 90.3 | 328
196 | 51 | 35.9 | 517.2 | 767.9 | 92.9 | 335
197 | 52 | 37.2 | 521.1 | 776.4 | 95.4 | 342.8
198 | 53 | 38.5 | 526 | 778.2 | 98 | 350.9
199 | 54 | 39.9 | 530.5 | 781 | 100.7 | 359.1
200 | 55 | 41.2 | 531.1 | 777.7 | 102.3 | 366
201 | 56 | 42.7 | 531.1 | 778.5 | 103.7 | 372
202 | 57 | 44.1 | 535.8 | 788.9 | 105 | 380.1
203 | 58 | 45.5 | 542.8 | 796.2 | 105.7 | 390.3
204 | 59 | 47 | 547.5 | 792.7 | 105.9 | 397.2
205 | 60 | 48.4 | 547.9 | 792.6 | 105.9 | 402.7
206 | 61 | 49.8 | 551.8 | 796.7 | 105.9 | 409.8
207 | 62 | 51.3 | 550.5 | 784.6 | 106 | 413.6
208 | 63 | 52.7 | 547.2 | 783.3 | 106 | 419
209 | 64 | 54.1 | 546.1 | 786.1 | 106 | 424.5
210 | 65 | 55.5 | 546 | 793.9 | 105.9 | 432.5
211 | 66 | 56.8 | 551.5 | 804.2 | 105.9 | 444.1
212 | 67 | 58 | 562.7 | 812.3 | 105.7 | 455.8
213 | 68 | 59.2 | 566.4 | 813.9 | 105.3 | 462.9
214 | 69 | 60.4 | 564.9 | 811.3 | 104.8 | 470.7
215 | 70 | 61.5 | 562.8 | 806.3 | 104.2 | 478.3
216 | 71 | 62.5 | 560.1 | 803.9 | 103.6 | 485.3
217 | 72 | 63.5 | 557.8 | 804.2 | 103 | 490.4
218 | 73 | 64.4 | 559.2 | 812.8 | 102.5 | 497.2
219 | 74 | 65.3 | 556.6 | 812.2 | 102.1 | 502.9
220 | 75 | 66.3 | 558 | 816.4 | 101.8 | 511.2
221 | 76 | 67.3 | 560.3 | 818.3 | 101.6 | 519.6
222 | 77 | 68.2 | 559.9 | 819.2 | 101.4 | 526.3
223 | 78 | 69 | 555 | 815.4 | 101.3 | 529.9
224 | 79 | 69.8 | 553.9 | 821 | 101.2 | 535.2
225 | 80 | 70.6 | 555.8 | 820.5 | 101.1 | 541.5
226 | 81 | 71.3 | 560.6 | 830.6 | 101 | 550.1
227 | 82 | 72.1 | 562.4 | 829.8 | 100.9 | 557.7
228 | 83 | 72.9 | 554.6 | 816.1 | 100.7 | 561.7
229 | 84 | 73.6 | 553.6 | 815.9 | 100.4 | 568
230 | 85 | 74.4 | 549.5 | 807.8 | 99.9 | 572
231 | 86 | 75.2 | 542.6 | 790.7 | 99.4 | 574
232 | 87 | 76 | 537.4 | 784.1 | 99.2 | 577.2
233 | 88 | 76.9 | 536.1 | 788.7 | 99 | 582.6
234 | 89 | 77.8 | 533.7 | 789.2 | 99.1 | 587.1
235 | 90 | 78.7 | 532.1 | 786.7 | 99.2 | 589.8
236 | 91 | 79.6 | 532.8 | 795.1 | 99.5 | 593.4
237 | 92 | 80.6 | 533.6 | 794.7 | 100 | 596.4
238 | 93 | 81.6 | 532.2 | 795.4 | 100.9 | 598.5
239 | 94 | 82.7 | 531.6 | 792.2 | 101.9 | 600.1
240 | 95 | 83.7 | 531 | 784.9 | 102.9 | 602.5
241 | 96 | 84.8 | 526.9 | 771.3 | 103.9 | 601.8
242 | 97 | 85.8 | 525.1 | 772.4 | 105.2 | 603.8
243 | 98 | 86.8 | 523.6 | 767.8 | 106.9 | 605.2
244 | 99 | 87.8 | 524.2 | 773.3 | 109.2 | 606.3
245 | 100 | 88.8 | 524 | 773.8 | 112.5 | 608.1
246 | 101 | 89.8 | 528.5 | 782 | 116.4 | 611.1
247 | 102 | 90.8 | 530.4 | 787.9 | 120.2 | 614.5
248 | 103 | 91.8 | 530.7 | 794.3 | 123.9 | 616.4
249 | 104 | 92.8 | 529.7 | 789.5 | 127 | 616.6
250 | 105 | 93.8 | 525.7 | 773.6 | 130.5 | 616.3
251 | 106 | 94.8 | 518.8 | 756.6 | 133.9 | 615.6
252 | 107 | 95.8 | 513.5 | 746 | 138.1 | 614.6
253 | 108 | 96.8 | 512.4 | 747.4 | 145.8 | 616.3
254 | 109 | 97.8 | 509.9 | 744.5 | 154.5 | 616.3
255 | 110 | 98.8 | 506.5 | 737.7 | 163.8 | 616
256 | 111 | 99.9 | 505.1 | 737.4 | 174.1 | 615.9
257 | 112 | 100.9 | 502.9 | 740 | 182.4 | 616.1
258 | 113 | 102 | 501.1 | 737.4 | 190.1 | 615.7
259 | 114 | 103.1 | 498.2 | 738.1 | 197.3 | 615.2
260 | 115 | 104.1 | 496.9 | 735.3 | 204 | 614.5
261 | 116 | 105.2 | 495.5 | 735 | 211 | 614.1
262 | 117 | 106.2 | 495.2 | 730.3 | 217.6 | 614.6
263 | 118 | 107.2 | 496.9 | 736.2 | 223.7 | 614.9
264 | 119 | 108.2 | 501.2 | 749.6 | 230 | 617.7
265 | 120 | 109.2 | 509.4 | 763 | 236.4 | 621.2
266 | 121 | 110.1 | 512.8 | 765.4 | 241.8 | 623.3
267 | 122 | 111 | 512.8 | 753.6 | 246 | 624.1
268 | 123 | 111.9 | 511.4 | 748.5 | 250 | 623.9
269 | 124 | 112.8 | 508.1 | 736.8 | 253.5 | 622.5
270 | 125 | 113.7 | 508 | 743.6 | 257 | 622.3
271 | 126 | 114.6 | 511.3 | 747.4 | 260.3 | 623.6
272 | 127 | 115.5 | 516.2 | 751.7 | 263.8 | 625.1
273 | 128 | 116.4 | 515.6 | 747.5 | 265.9 | 625
274 | 129 | 117.3 | 520.6 | 758.7 | 268.6 | 626.9
275 | 130 | 118.3 | 519 | 752.2 | 270.8 | 626.4
276 | 131 | 119.3 | 515.4 | 744.9 | 272.6 | 624.8
277 | 132 | 120.2 | 517.6 | 755.6 | 274.6 | 626.7
278 | 133 | 121.2 | 518.4 | 757.2 | 276.1 | 626.2
279 | 134 | 122.2 | 518.4 | 746.6 | 276.9 | 625.4
280 | 135 | 123.2 | 517.3 | 741.3 | 277.5 | 624.5
281 | 136 | 124.2 | 514.5 | 728.7 | 277.8 | 622.3
282 | 137 | 125.2 | 510.3 | 722.8 | 277.9 | 619.9
283 | 138 | 126.2 | 508.3 | 719.4 | 278 | 617.9
284 | 139 | 127.3 | 507.7 | 714.9 | 278.1 | 616.1
285 | 140 | 128.3 | 506.2 | 704.3 | 278 | 613.6
286 | 141 | 129.4 | 503.3 | 701.5 | 277.9 | 611.7
287 | 142 | 130.4 | 500.4 | 696.6 | 278 | 610
288 | 143 | 131.5 | 498.8 | 692.6 | 278 | 608.4
289 | 144 | 132.6 | 500.5 | 701.7 | 278.8 | 609.2
290 | 145 | 133.7 | 506.8 | 724.2 | 280.4 | 613.2
291 | 146 | 134.8 | 514 | 730.9 | 281.9 | 617
292 | 147 | 135.9 | 515.4 | 727.6 | 282.8 | 618.1
293 | 148 | 137 | 518.6 | 742.3 | 284.2 | 620.4
294 | 149 | 138.1 | 522.5 | 752.4 | 285.7 | 622.4
295 | 150 | 139.2 | 523.8 | 752.2 | 286.7 | 623.6
296 | 151 | 140.3 | 526.9 | 753.8 | 287.6 | 625.2
297 | 152 | 141.4 | 526.9 | 750.8 | 288 | 625
298 | 153 | 142.5 | 526.8 | 749.7 | 288.7 | 625.1
299 | 154 | 143.6 | 525.1 | 746.6 | 289.1 | 624
300 | 155 | 144.7 | 521.9 | 743 | 289.5 | 623.3
301 | 156 | 145.8 | 518.3 | 731 | 290 | 622.7
302 | 157 | 146.9 | 513.7 | 716.9 | 290.1 | 620.8
303 | 158 | 148 | 511.7 | 721.3 | 290.4 | 620.4
304 | 159 | 149.1 | 511.3 | 720.2 | 290.7 | 620.3
305 | 160 | 150.2 | 510.9 | 726.3 | 290.9 | 621
306 | 161 | 151.3 | 511.6 | 728.5 | 291.2 | 621.8
307 | 162 | 152.4 | 512.1 | 725.9 | 291.4 | 622
308 | 163 | 153.5 | 511.7 | 724.4 | 291.3 | 621.8
309 | 164 | 154.6 | 513 | 727.3 | 291.4 | 622.8
310 | 165 | 155.8 | 513.9 | 734.7 | 291.9 | 624.8
311 | 166 | 156.9 | 515.2 | 737.8 | 293 | 628.2
312 | 167 | 158.1 | 519.6 | 752.8 | 294.2 | 633.2
313 | 168 | 159.3 | 525.2 | 753.1 | 295.1 | 635.7
314 | 169 | 160.4 | 528.8 | 749.1 | 295.7 | 636.6
315 | 170 | 161.6 | 534.7 | 760.2 | 296.7 | 640.3
316 | 171 | 162.8 | 536.7 | 764 | 297.4 | 641.2
317 | 172 | 164 | 537.3 | 763.1 | 297.6 | 641.3
318 | 173 | 165.2 | 539.6 | 769 | 298.1 | 642.7
319 | 174 | 166.4 | 541.5 | 769.4 | 298.7 | 645.2
320 | 175 | 167.6 | 545.8 | 786 | 299.7 | 648.7
321 | 176 | 168.8 | 550.5 | 789.6 | 300.5 | 650.9
322 | 177 | 170 | 550.4 | 779.9 | 301 | 651.4
323 | 178 | 171.2 | 550.5 | 789 | 301.7 | 652.2
324 | 179 | 172.5 | 554.7 | 793.9 | 302.5 | 655.1
325 | 180 | 173.7 | 558.2 | 795.2 | 303.3 | 659
326 | 181 | 175 | 562.3 | 798.9 | 304.2 | 662.4
327 | 182 | 176.2 | 562.6 | 799.8 | 304.7 | 663.1
328 | 183 | 177.5 | 563.2 | 804.2 | 305.2 | 663.7
329 | 184 | 178.7 | 565 | 804.5 | 305.8 | 664.7
330 | 185 | 180 | 566.8 | 805.6 | 306.2 | 666.2
331 | 186 | 181.3 | 565.8 | 803.6 | 306.6 | 666
332 | 187 | 182.7 | 565 | 802.9 | 307.2 | 666.9
333 | 188 | 184.2 | 564.4 | 804.7 | 307.8 | 667.9
334 | 189 | 185.9 | 564.9 | 803.7 | 308.5 | 669.6
335 | 190 | 187.6 | 568.7 | 811.3 | 309.5 | 672.6
336 | 191 | 189.4 | 571.1 | 817.5 | 310.6 | 674.3
337 | 192 | 191.5 | 571.9 | 821.1 | 311.7 | 677.3
338 | 193 | 194.6 | 570.6 | 817.6 | 312.8 | 679.2
339 | 194 | 198.3 | 570.3 | 818.6 | 314 | 681.4
340 | 195 | 202.3 | 570.9 | 822.7 | 315 | 684.2
341 | 196 | 206.2 | 571.2 | 821.7 | 316.1 | 685.3
342 | 197 | 210 | 571.5 | 825.5 | 317.3 | 688.2
343 | 198 | 213.2 | 570.7 | 818.2 | 318.3 | 691.2
344 | 199 | 216.1 | 568.4 | 816.1 | 319.2 | 692.3
345 | 200 | 218.6 | 566.2 | 809.2 | 320 | 692
346 | 201 | 220.8 | 564.8 | 811.1 | 320.6 | 692.7
347 | 202 | 222.9 | 564.7 | 808.9 | 321.3 | 693.7
348 | 203 | 224.8 | 565.9 | 812.7 | 322.1 | 696
349 | 204 | 226.6 | 567.9 | 815.9 | 323 | 698.6
350 | 205 | 228.2 | 568.6 | 812.7 | 323.7 | 699.6
351 | 206 | 229.8 | 569.5 | 813.4 | 324.3 | 701.4
352 | 207 | 231.2 | 570.8 | 807.7 | 324.9 | 700.9
353 | 208 | 232.6 | 571.6 | 806.4 | 325.4 | 702.5
354 | 209 | 233.8 | 573.7 | 811.8 | 326.1 | 705
355 | 210 | 235 | 574.7 | 816.4 | 326.9 | 707.3
356 | 211 | 236.1 | 576 | 821 | 327.6 | 709.7
357 | 212 | 237.2 | 576.2 | 817.8 | 328.3 | 709.6
358 | 213 | 238.2 | 575.5 | 822.4 | 328.9 | 711.1
359 | 214 | 239.3 | 577.8 | 825.9 | 329.7 | 713.4
360 | 215 | 240.3 | 580.8 | 832.9 | 330.6 | 716.2
361 | 216 | 241.4 | 582.6 | 830.2 | 331.4 | 719
362 | 217 | 242.5 | 583 | 823.7 | 332.2 | 719.5
363 | 218 | 243.6 | 585.4 | 825.8 | 333.1 | 719.6
364 | 219 | 244.7 | 586.6 | 824.6 | 334 | 720.3
365 | 220 | 245.9 | 585.8 | 825.1 | 334.9 | 721.1
366 | 221 | 247.1 | 586.4 | 824.3 | 335.8 | 720.9
367 | 222 | 248.4 | 585.9 | 816.2 | 336.5 | 720.1
368 | 223 | 249.6 | 585.4 | 818.9 | 337.1 | 720.2
369 | 224 | 250.9 | 585.4 | 820.7 | 337.9 | 721.4
370 | 225 | 252.3 | 584.5 | 818.6 | 338.7 | 721.4
371 | 226 | 253.7 | 581.6 | 807.2 | 339.4 | 719.3
372 | 227 | 255 | 577.8 | 801.4 | 339.9 | 717.8
373 | 228 | 256.4 | 574.8 | 799.5 | 340.5 | 717.3
374 | 229 | 257.9 | 573.9 | 795.8 | 341.1 | 716.4
375 | 230 | 259.3 | 573.1 | 802.8 | 341.8 | 717.6
376 | 231 | 260.8 | 577.8 | 817.7 | 342.8 | 721.1
377 | 232 | 262.4 | 581.2 | 827.7 | 343.9 | 723.1
378 | 233 | 263.9 | 584.3 | 833.9 | 345 | 724.7
379 | 234 | 265.5 | 589 | 842.1 | 346.2 | 727.4
380 | 235 | 267 | 593.4 | 844.6 | 347.4 | 729.6
381 | 236 | 268.6 | 595.2 | 845.7 | 348.4 | 730.8
382 | 237 | 270.1 | 597 | 843.2 | 349.3 | 731.1
383 | 238 | 271.7 | 599.7 | 847.6 | 350.4 | 733.4
384 | 239 | 273.3 | 601.5 | 850 | 351.6 | 734.9
385 | 240 | 274.9 | 600.8 | 846.5 | 352.8 | 735.6
386 | 241 | 276.6 | 597.8 | 831.8 | 353.9 | 734.3
387 | 242 | 278.1 | 593.6 | 812.6 | 354.6 | 731.9
388 | 243 | 279.6 | 587.2 | 801.5 | 355.2 | 730.3
389 | 244 | 281.2 | 583.7 | 800.1 | 355.8 | 729.6
390 | 245 | 282.8 | 581.4 | 795.2 | 356.5 | 728
391 | 246 | 284.4 | 580.5 | 793 | 357.3 | 727.5
392 | 247 | 285.9 | 576.6 | 778.8 | 357.9 | 726.2
393 | 248 | 287.5 | 574.8 | 778.8 | 358.6 | 725.2
394 | 249 | 288.9 | 570.9 | 770.5 | 359.1 | 723
395 | 250 | 290.3 | 568.5 | 769.3 | 359.6 | 722.3
396 | 251 | 291.7 | 566 | 767.1 | 360.1 | 720.9
397 | 252 | 293.2 | 565.5 | 773 | 360.7 | 721
398 | 253 | 294.7 | 566.3 | 781.9 | 361.5 | 720.6
399 | 254 | 296.2 | 566 | 781.1 | 362.2 | 719.4
400 | 255 | 297.7 | 565.6 | 780.3 | 363.1 | 719.4
401 | 256 | 299.2 | 564.4 | 774.4 | 363.8 | 717.4
402 | 257 | 300.5 | 562.9 | 767.5 | 364.4 | 714.4
403 | 258 | 301.7 | 564.5 | 779.7 | 365 | 714.8
404 | 259 | 303 | 567.6 | 788.7 | 365.9 | 716.9
405 | 260 | 304.2 | 567.5 | 789 | 367 | 716.1
406 | 261 | 305.3 | 569.5 | 798.1 | 368 | 716
407 | 262 | 306.3 | 571.3 | 800.1 | 369.3 | 717.9
408 | 263 | 307.2 | 572.1 | 806 | 370.6 | 718.1
409 | 264 | 308 | 570.8 | 797.3 | 371.7 | 716.2
410 | 265 | 308.6 | 570.4 | 797.9 | 372.6 | 715.8
411 | 266 | 309.3 | 570.2 | 792.5 | 373.6 | 715.7
412 | 267 | 310 | 571.3 | 797.1 | 374.7 | 717.5
413 | 268 | 310.7 | 573.3 | 808.3 | 376 | 720.2
414 | 269 | 311.4 | 575.2 | 816.5 | 377.3 | 720.9
415 | 270 | 312.1 | 575.7 | 818.4 | 378.4 | 720.6
416 | 271 | 312.8 | 577.6 | 817.8 | 379.5 | 721.3
417 | 272 | 313.6 | 576.8 | 813.7 | 380.5 | 720.9
418 | 273 | 314.5 | 575.9 | 805.6 | 381 | 720.4
419 | 274 | 315.3 | 573.9 | 790.5 | 381.1 | 718.4
420 | 275 | 316.2 | 574.3 | 784.1 | 381.1 | 717.7
421 | 276 | 317.2 | 575.3 | 795.4 | 381.3 | 718.3
422 | 277 | 318.3 | 579.6 | 804.8 | 381.7 | 719.5
423 | 278 | 319.4 | 581.6 | 804.4 | 382.3 | 719.3
424 | 279 | 320.6 | 582.2 | 794.2 | 382.7 | 719.5
425 | 280 | 321.7 | 584.6 | 797 | 383.3 | 720.8
426 | 281 | 322.9 | 585 | 800.2 | 383.7 | 721.9
427 | 282 | 324.1 | 584.8 | 805.6 | 384 | 722.9
428 | 283 | 325.3 | 585.7 | 815 | 384.3 | 723.3
429 | 284 | 326.5 | 587.6 | 820.4 | 384.6 | 724.6
430 | 285 | 327.7 | 590.6 | 827.2 | 385 | 727.1
431 | 286 | 328.9 | 591.5 | 826.4 | 385.4 | 728.6
432 | 287 | 330.2 | 590.2 | 823 | 385.9 | 728.5
433 | 288 | 331.4 | 591.1 | 826.1 | 386.3 | 729.7
434 | 289 | 332.6 | 593.2 | 834.8 | 386.6 | 730.9
435 | 290 | 333.9 | 594.5 | 836.9 | 387 | 731.8
436 | 291 | 335.1 | 595.6 | 840.5 | 387.3 | 732.4
437 | 292 | 336.3 | 596.5 | 842.6 | 387.2 | 733.3
438 | 293 | 337.5 | 599.6 | 840.6 | 388.2 | 735.4
439 | 294 | 338.7 | 603.2 | 843.4 | 391 | 736.9
440 | 295 | 339.8 | 605.1 | 846.5 | 394.3 | 738.9
441 | 296 | 341.1 | 605.1 | 852 | 397.7 | 739.3
442 | 297 | 342.4 | 605.5 | 849.5 | 400.5 | 739.9
443 | 298 | 343.8 | 607.8 | 847.3 | 403.1 | 738.8
444 | 299 | 344.8 | 606.7 | 837 | 405.6 | 738.6
445 | 300 | 345.8 | 607.1 | 823 | 407.6 | 738.1
446 | 301 | 346.6 | 608.2 | 824.7 | 410.8 | 738.8
447 | 302 | 347.4 | 609.8 | 819.2 | 414.2 | 740.8
448 | 303 | 348 | 610.8 | 823.8 | 418.6 | 743.1
449 | 304 | 348.5 | 611.5 | 825.1 | 423.5 | 743.6
450 | 305 | 349 | 611.5 | 830 | 428.3 | 745.6
451 | 306 | 349.4 | 611.5 | 821.3 | 432.6 | 745.8
452 | 307 | 349.8 | 610.5 | 824.4 | 437.9 | 745.9
453 | 308 | 350.3 | 607 | 824.4 | 444.3 | 746.8
454 | 309 | 350.9 | 604.8 | 819.7 | 450.2 | 746.9
455 | 310 | 351.7 | 600.8 | 808.8 | 454.3 | 745.8
456 | 311 | 352.7 | 598.7 | 798.3 | 457.4 | 745.4
457 | 312 | 354 | 595.7 | 791.5 | 459.5 | 744.1
458 | 313 | 355.6 | 593.6 | 796.8 | 462.3 | 744.3
459 | 314 | 357.6 | 590.9 | 797.4 | 463.9 | 744.4
460 | 315 | 359.9 | 587.1 | 792.5 | 465.2 | 743.5
461 | 316 | 362.5 | 584.1 | 803.8 | 465.7 | 744
462 | 317 | 365.2 | 581.6 | 794.2 | 464.8 | 742.7
463 | 318 | 368.2 | 579.4 | 776.1 | 462.9 | 741.2
464 | 319 | 371.2 | 578.5 | 782.7 | 461 | 740.8
465 | 320 | 374.2 | 577.4 | 786 | 458.8 | 741.3
466 | 321 | 377.1 | 575.2 | 778.5 | 456.5 | 739.4
467 | 322 | 380.1 | 572.2 | 766.5 | 454.3 | 738
468 | 323 | 383.3 | 569.6 | 766.1 | 452.4 | 736.5
469 | 324 | 386.6 | 567.9 | 755.6 | 450.4 | 734.4
470 | 325 | 390 | 565.4 | 749.8 | 448.2 | 732
471 | 326 | 393.1 | 564.7 | 752.5 | 446.3 | 731.7
472 | 327 | 396.1 | 563.3 | 756.6 | 444.5 | 731.2
473 | 328 | 399.1 | 562.1 | 764 | 443 | 731.3
474 | 329 | 402.5 | 560.6 | 757.1 | 441.5 | 730
475 | 330 | 406 | 560.1 | 760.7 | 439.9 | 729.7
476 | 331 | 409.9 | 558.6 | 760.2 | 438.6 | 728.6
477 | 332 | 414.2 | 558.4 | 758 | 437.5 | 727.2
478 | 333 | 418.7 | 558.1 | 758.7 | 436.7 | 725.8
479 | 334 | 423.4 | 558.2 | 767.6 | 436.3 | 725.9
480 | 335 | 428.1 | 558.9 | 767 | 436.2 | 725.6
481 | 336 | 433.9 | 559.9 | 766.1 | 436.2 | 725.7
482 | 337 | 441.4 | 560.8 | 767.3 | 436.4 | 725.3
483 | 338 | 445.4 | 559.5 | 757 | 436.5 | 723.3
484 | 339 | 448.2 | 561.5 | 748.2 | 436.6 | 721.8
485 | 340 | 451 | 564.7 | 737.2 | 436.6 | 720.1
486 | 341 | 454.5 | 567.5 | 724.8 | 436.4 | 718.3
487 | 342 | 458.7 | 568.1 | 721.6 | 435.8 | 716.7
488 | 343 | 463.1 | 567.5 | 267 | 285.5 | 715.1
489 | 344 | 467.5 | 566.5 | 627 | 397.5 | 713.9
490 | 345 | 471.3 | 566 | 736.3 | 432.7 | 715
491 | 346 | 474.7 | 564.3 | 202.6 | 294 | 714.3
492 | 347 | 477.9 | 563.2 | 745.3 | 428.9 | 714.2
493 | 348 | 480.8 | 562.2 | 762.4 | 430.5 | 714.2
494 | 349 | 483.4 | 561.1 | 769.2 | 429.9 | 714.1
495 | 350 | 486.1 | 560.6 | 779.3 | 429.3 | 714.3
496 | 351 | 488.7 | 559.8 | 556.1 | 417.3 | 715.4
497 | 352 | 491.2 | 558.8 | 411.6 | 413.4 | 716.3
498 | 353 | 493.6 | 558.6 | 794.8 | 427.8 | 716.1
499 | 354 | 495.7 | 557.2 | 435.6 | 427.4 | 715.4
500 | 355 | 497.7 | 556.6 | 539.9 | 427.1 | 713.6
501 | 356 | 499.8 | 557 | 761 | 427.2 | 712.2
502 | 357 | 501.9 | 557.3 | 328.7 | 424.2 | 711.4
503 | 358 | 504.2 | 558.2 | 657 | 426.3 | 711.7
504 | 359 | 506.4 | 556.3 | 753.4 | 428.8 | 710.8
505 | 360 | 508.7 | 557.6 | 272.3 | 429.6 | 710.4
506 | 361 | 511.2 | 560.5 | 468.7 | 430.5 | 711.1
507 | 362 | 513.8 | 564.1 | 571.3 | 431.5 | 711.2
508 | 363 | 516.7 | 565.7 | 711.3 | 432.5 | 709.3
509 | 364 | 519.5 | 564.4 | 725.9 | 433.8 | 708.6
510 | 365 | 522.1 | 565 | 725 | 435.2 | 709.2
511 | 366 | 524.7 | 563.2 | 726 | 436.6 | 708
512 | 367 | 527.1 | 561.6 | 731.8 | 438 | 706.9
513 | 368 | 529.3 | 560.2 | 734.1 | 439.4 | 706.1
514 | 369 | 531 | 559 | 734.7 | 440.8 | 705.9
515 | 370 | 532.7 | 558.4 | 744 | 442.3 | 705.7
516 | 371 | 534.8 | 558.4 | 750.2 | 444 | 706
517 | 372 | 536.9 | 557.9 | 749.1 | 445.9 | 705.5
518 | 373 | 538.9 | 557.6 | 757.2 | 447.9 | 705.2
519 | 374 | 540.9 | 558 | 767.3 | 450 | 705
520 | 375 | 542.5 | 558.5 | 768.9 | 452.1 | 705.3
521 | 376 | 544.2 | 558.3 | 775.3 | 454.2 | 705.5
522 | 377 | 546.2 | 559.5 | 781.6 | 456.4 | 706
523 | 378 | 548.5 | 559.1 | 776.7 | 458.1 | 705.5
524 | 379 | 550.9 | 558.5 | 776.5 | 459.8 | 704.7
525 | 380 | 553.3 | 558.8 | 760.7 | 461.1 | 702.4
526 | 381 | 555.9 | 559 | 741.9 | 462.4 | 700.9
527 | 382 | 558.3 | 559.3 | 726.2 | 463.5 | 698.5
528 | 383 | 561 | 559.3 | 721.5 | 465 | 697.3
529 | 384 | 563.7 | 559.8 | 719.6 | 466.5 | 696.6
530 | 385 | 566.3 | 559.5 | 715.8 | 468.1 | 695.2
531 | 386 | 568.4 | 561 | 715.9 | 470 | 694.8
532 | 387 | 568.7 | 562.1 | 716.1 | 472 | 694
533 | 388 | 568.2 | 562.1 | 713.8 | 474.2 | 692
534 | 389 | 569 | 561.9 | 707.5 | 476 | 690.8
535 | 390 | 570.3 | 561.8 | 696.5 | 478.3 | 690.4
536 | 391 | 571.6 | 560.7 | 685 | 480.8 | 689.4
537 | 392 | 573.1 | 559.9 | 705.4 | 483.1 | 688.9
538 | 393 | 574.9 | 559.2 | 704.1 | 485.4 | 688.7
539 | 394 | 576.6 | 559.3 | 710.7 | 487.9 | 689
540 | 395 | 578.5 | 558.7 | 707 | 489.6 | 687.6
541 | 396 | 580.7 | 557.9 | 703 | 491.4 | 686.6
542 | 397 | 582.7 | 559.3 | 710.3 | 493.5 | 686.7
543 | 398 | 584.6 | 560.2 | 711.1 | 495.5 | 686.2
544 | 399 | 586.5 | 561.7 | 715.3 | 497.5 | 686.1
545 | 400 | 588.4 | 562.9 | 716 | 499.6 | 685.5
546 | 401 | 590.3 | 564.7 | 733 | 502.4 | 685.7
547 | 402 | 591.9 | 567.1 | 752.2 | 505.2 | 686.8
548 | 403 | 593.4 | 567.3 | 760.8 | 507.3 | 687.4
549 | 404 | 595.1 | 569.7 | 768.7 | 509.2 | 689.6
550 | 405 | 596.9 | 570.4 | 773.9 | 510.7 | 690.9
551 | 406 | 598.6 | 571.3 | 781.2 | 512.5 | 692.4
552 | 407 | 600.2 | 570.3 | 777.3 | 513.8 | 691.8
553 | 408 | 602 | 569.1 | 766.3 | 515.4 | 690.7
554 | 409 | 603.9 | 568.5 | 748.7 | 516.2 | 689.1
555 | 410 | 606.1 | 567.3 | 729.5 | 516.5 | 687.4
556 | 411 | 608.4 | 568.1 | 721.1 | 516.5 | 686.6
557 | 412 | 611 | 569.2 | 706.9 | 516.2 | 684.5
558 | 413 | 613.8 | 571.3 | 694.3 | 516.4 | 682.3
559 | 414 | 616.4 | 572 | 697.9 | 517.4 | 682.3
560 | 415 | 618.1 | 573.8 | 709.9 | 519.7 | 682.7
561 | 416 | 619.6 | 574.2 | 715.2 | 521.6 | 682.5
562 | 417 | 621.2 | 574.7 | 710.7 | 522.7 | 681.7
563 | 418 | 622.9 | 577.2 | 718.4 | 524.6 | 681.9
564 | 419 | 624.5 | 578.1 | 735.7 | 527.4 | 682.8
565 | 420 | 626.3 | 577.5 | 734.1 | 529.4 | 683.4
566 | 421 | 628.4 | 577.3 | 719.7 | 530.2 | 681.8
567 | 422 | 630.7 | 577.6 | 703.9 | 530.5 | 680.3
568 | 423 | 632.7 | 578.4 | 697.2 | 531.3 | 679.2
569 | 424 | 634.3 | 579 | 701.7 | 534.1 | 679.6
570 | 425 | 635.2 | 581.2 | 707.8 | 537.1 | 680.2
571 | 426 | 636.2 | 580.9 | 705.6 | 538.5 | 679.5
572 | 427 | 636.9 | 579.5 | 700 | 539.8 | 678.6
573 | 428 | 637.7 | 578 | 699.7 | 541.5 | 677.4
574 | 429 | 638.2 | 576.5 | 697 | 542.9 | 676.6
575 | 430 | 639.5 | 577.7 | 688.3 | 543 | 675.5
576 | 431 | 640.7 | 578.8 | 680 | 543.5 | 674
577 | 432 | 642.1 | 578.4 | 667.1 | 543.8 | 672
578 | 433 | 643.5 | 578.2 | 660.7 | 544.7 | 670.8
579 | 434 | 645.3 | 580.5 | 650.4 | 545.1 | 669.5
580 | 435 | 647.3 | 584.9 | 646.2 | 545.3 | 669
581 | 436 | 648.6 | 588.4 | 648.6 | 546.4 | 669.3
582 | 437 | 649.9 | 590 | 652.3 | 547.7 | 669.4
583 | 438 | 651.1 | 591.1 | 650.4 | 549.5 | 668.5
584 | 439 | 652.2 | 589.8 | 643.3 | 551.1 | 666.9
585 | 440 | 653.3 | 589.8 | 638.6 | 551.5 | 665.1
586 | 441 | 655 | 589.4 | 636.2 | 552.6 | 664.8
587 | 442 | 656.5 | 589.5 | 635.9 | 554.7 | 664.4
588 | 443 | 657.6 | 587.3 | 623.9 | 555.1 | 662.6
589 | 444 | 658.4 | 585.4 | 615.6 | 555.7 | 660.7
590 | 445 | 659.7 | 583.5 | 616.2 | 557 | 659.5
591 | 446 | 660.7 | 592.3 | 622.5 | 559 | 658.9
592 | 447 | 662 | 594.7 | 629.6 | 560.5 | 658.6
593 | 448 | 663.1 | 593.7 | 641.9 | 562.5 | 658.7
594 | 449 | 664.5 | 592.8 | 644.1 | 564.1 | 658.8
595 | 450 | 665.8 | 590.6 | 645.7 | 566 | 658.7
596 | 451 | 666.7 | 588.7 | 642.7 | 567.3 | 658.3
597 | 452 | 667.2 | 586.3 | 637.3 | 568.2 | 657.8
598 | 453 | 667.9 | 583.2 | 630.4 | 569.1 | 657.5
599 | 454 | 668.9 | 582.9 | 635.3 | 570.9 | 657.1
600 | 455 | 669.6 | 583.9 | 641.3 | 572.1 | 657.4
601 | 456 | 669.8 | 583.6 | 659.2 | 573.8 | 657.9
602 | 457 | 669.7 | 582.6 | 668.8 | 575.6 | 658.9
603 | 458 | 669.2 | 579.3 | 657.7 | 575.4 | 657
604 | 459 | 669.3 | 575.6 | 647.1 | 573.7 | 655.6
605 | 460 | 670.2 | 572 | 634.9 | 572.1 | 653.9
606 | 461 | 671.5 | 569.5 | 633.6 | 572.5 | 653.5
607 | 462 | 672.7 | 569.4 | 629.8 | 572.2 | 653
608 | 463 | 673.7 | 568.1 | 627.7 | 572.5 | 652.1
609 | 464 | 674.3 | 566.2 | 629.1 | 573.4 | 650.6
610 | 465 | 674.9 | 565.5 | 631 | 573.8 | 650.8
611 | 466 | 675.3 | 565.2 | 635 | 574.4 | 650.6
612 | 467 | 675.3 | 566.7 | 652.1 | 575.7 | 651.2
613 | 468 | 674.7 | 567.9 | 667.5 | 577.7 | 651.7
614 | 469 | 674.2 | 568.5 | 670.9 | 578.9 | 651.8
615 | 470 | 674.1 | 567.9 | 668.4 | 580 | 650.7
616 | 471 | 674.5 | 566.8 | 659.5 | 579.1 | 650.2
617 | 472 | 675.1 | 566.4 | 656.1 | 579.3 | 649.9
618 | 473 | 675.4 | 565.5 | 649.8 | 579 | 649.1
619 | 474 | 676.1 | 565 | 640.2 | 579 | 647.8
620 | 475 | 676.8 | 564.4 | 634.5 | 579.7 | 646.8
621 | 476 | 677.7 | 564.1 | 638.9 | 580.2 | 646.5
622 | 477 | 677.9 | 564.2 | 638.6 | 581.1 | 647
623 | 478 | 678.6 | 566 | 637.9 | 582.3 | 646.4
624 | 479 | 679.3 | 571.3 | 650.6 | 584.1 | 648.7
625 | 480 | 679.7 | 572.9 | 667.3 | 586.8 | 649.9
626 | 481 | 680.4 | 574.3 | 667.4 | 589 | 650
627 | 482 | 681.5 | 578 | 675.1 | 590.9 | 650.7
628 | 483 | 682 | 579.1 | 678.7 | 592.5 | 650.8
629 | 484 | 682.4 | 580.3 | 682 | 594 | 651
630 | 485 | 683 | 583.2 | 686 | 595.5 | 653.4
631 | 486 | 683.3 | 585.4 | 698.2 | 597.3 | 655.5
632 | 487 | 683.6 | 583.8 | 692.1 | 598.6 | 653.9
633 | 488 | 684.6 | 580.3 | 685.6 | 598.9 | 653.2
634 | 489 | 685.3 | 578.2 | 674.7 | 598.7 | 652.8
635 | 490 | 686.1 | 575.7 | 666.7 | 598 | 651.5
636 | 491 | 686.9 | 572.7 | 656.3 | 597.1 | 649.9
637 | 492 | 687.9 | 571.3 | 648 | 596.2 | 648.8
638 | 493 | 689.8 | 572.2 | 636.1 | 595.3 | 647.5
639 | 494 | 691 | 573.9 | 631.6 | 594.7 | 646.7
640 | 495 | 692 | 571.9 | 626.1 | 595.3 | 646.3
641 | 496 | 692.5 | 571.1 | 622.3 | 596.5 | 646.6
642 | 497 | 693.3 | 575.1 | 626.9 | 597.8 | 647.1
643 | 498 | 693.6 | 575.8 | 624.6 | 598.5 | 646.7
644 | 499 | 694.6 | 574.8 | 614.2 | 597.8 | 645
645 | 500 | 695.7 | 583.5 | 610.8 | 597.4 | 643.5
646 | 501 | 696.2 | 579.9 | 607.8 | 596.8 | 642
647 | 502 | 696.2 | 577.6 | 616.5 | 597.6 | 642.4
648 | 503 | 695.7 | 578.7 | 641.4 | 599.7 | 645.1
649 | 504 | 695.6 | 577.2 | 638.2 | 600.5 | 643.7
650 | 505 | 696 | 579 | 624.2 | 599.4 | 641.6
651 | 506 | 696.4 | 579.3 | 621.7 | 599.1 | 641.1
652 | 507 | 696.7 | 579.1 | 609.8 | 598.7 | 639.4
653 | 508 | 697.7 | 576.3 | 604.9 | 598.6 | 638.2
654 | 509 | 698.8 | 576.2 | 596.7 | 597.9 | 636.8
655 | 510 | 699.5 | 573.4 | 592.2 | 598.1 | 635.3
656 | 511 | 699.5 | 571.8 | 600.5 | 598.7 | 634.9
657 | 512 | 698.7 | 570.3 | 605.4 | 599.8 | 634.3
658 | 513 | 698.1 | 579.8 | 603.5 | 599.8 | 633.1
659 | 514 | 697.6 | 577.3 | 599.3 | 599.9 | 632
660 | 515 | 697.6 | 572.6 | 592.5 | 599.8 | 630.1
661 | 516 | 697.3 | 569.5 | 593.4 | 599.7 | 628.6
662 | 517 | 696.7 | 573.4 | 586.1 | 599.3 | 627.1
663 | 518 | 697 | 576.7 | 579.2 | 599.1 | 626.3
664 | 519 | 697.7 | 576.2 | 571 | 598.9 | 625
665 | 520 | 698 | 592.6 | 576 | 599 | 623.8
666 | 521 | 697.7 | 588 | 581 | 599.6 | 623.1
667 | 522 | 697.5 | 587.5 | 589.5 | 600.6 | 622.6
668 | 523 | 697.6 | 585.6 | 587.3 | 601.9 | 621.9
669 | 524 | 698 | 582.4 | 590.6 | 603.8 | 621.5
670 | 525 | 698.1 | 579.3 | 587.5 | 605.1 | 621.2
671 | 526 | 698.5 | 574 | 582.4 | 605.1 | 620.1
672 | 527 | 698.6 | 579.9 | 586.6 | 605.6 | 619.9
673 | 528 | 698.7 | 578 | 588.7 | 606 | 619.5
674 | 529 | 698.9 | 573.7 | 584.8 | 606.7 | 617.9
675 | 530 | 699 | 568.3 | 583.6 | 607.7 | 616.3
676 | 531 | 698.8 | 567.6 | 570.9 | 607.7 | 615.2
677 | 532 | 698.7 | 586.7 | 567.8 | 607.3 | 614.1
678 | 533 | 698.3 | 580.6 | 565.1 | 607.7 | 613.2
679 | 534 | 698 | 575.6 | 569.4 | 608.4 | 612.9
680 | 535 | 697.6 | 571.8 | 571.7 | 609.1 | 612.4
681 | 536 | 697.1 | 569.4 | 577.2 | 610.1 | 612.6
682 | 537 | 696.6 | 565.9 | 584 | 611.7 | 612.8
683 | 538 | 696.4 | 563.5 | 589.4 | 613.4 | 613.3
684 | 539 | 696.2 | 561 | 597.8 | 614.8 | 613.9
685 | 540 | 695.9 | 559 | 603.7 | 616.6 | 613.8
686 | 541 | 695.7 | 556 | 597.2 | 617.6 | 612.5
687 | 542 | 695.8 | 555 | 597.5 | 618.6 | 611.9
688 | 543 | 696 | 555.7 | 597.7 | 619.8 | 611.5
689 | 544 | 695.6 | 556.5 | 612.1 | 621.5 | 612.8
690 | 545 | 694.9 | 557.1 | 618.9 | 623.5 | 613.9
691 | 546 | 694.9 | 556.4 | 616.7 | 625.4 | 614
692 | 547 | 695.2 | 552.6 | 603.3 | 626.6 | 612.3
693 | 548 | 696 | 549.7 | 604.5 | 627.5 | 612.1
694 | 549 | 696.2 | 550.9 | 610.9 | 629.3 | 612.9
695 | 550 | 696.3 | 551.5 | 607.6 | 630.2 | 613.1
696 | 551 | 697.3 | 550.5 | 612.3 | 632.7 | 613.2
697 | 552 | 698.4 | 553.5 | 616.5 | 634.6 | 613
698 | 553 | 699.4 | 555.7 | 625.4 | 636.3 | 613.3
699 | 554 | 700.3 | 556.2 | 634.7 | 637.6 | 613.3
700 | 555 | 701.4 | 562 | 634.3 | 638.7 | 613
701 | 556 | 702.8 | 569.7 | 624.5 | 639.8 | 611.8
702 | 557 | 704.4 | 576.1 | 614.8 | 640.8 | 610.5
703 | 558 | 706 | 586.9 | 609.8 | 641.7 | 609.7
704 | 559 | 707.4 | 585.4 | 615.8 | 643 | 609.4
705 | 560 | 708.7 | 585.7 | 608.9 | 643.7 | 608.1
706 | 561 | 710.3 | 613.3 | 598 | 644.1 | 606.5
707 | 562 | 712 | 632 | 587.6 | 644.5 | 605.4
708 | 563 | 713.6 | 646.6 | 582.4 | 644.4 | 604.4
709 | 564 | 714.8 | 646.9 | 591.1 | 646.1 | 605.2
710 | 565 | 715.6 | 641.9 | 584.7 | 647.2 | 604.5
711 | 566 | 716.6 | 641 | 581.2 | 648.4 | 603.8
712 | 567 | 717.8 | 648.6 | 582.5 | 649.2 | 603.5
713 | 568 | 719.1 | 644.2 | 588.3 | 651.4 | 603.2
714 | 569 | 720.3 | 636.8 | 612.7 | 653.8 | 604.6
715 | 570 | 721 | 632.8 | 627.4 | 656.7 | 606.3
716 | 571 | 721.6 | 628.5 | 639.6 | 660.1 | 608.8
717 | 572 | 721.9 | 620.5 | 651.8 | 661.7 | 610.3
718 | 573 | 722.5 | 619 | 633.5 | 662.4 | 608.2
719 | 574 | 723.5 | 615 | 626.4 | 662.4 | 607.7
720 | 575 | 724.7 | 610.1 | 618.9 | 663.3 | 607.2
721 | 576 | 725.9 | 606.1 | 611.4 | 664.1 | 606.3
722 | 577 | 727.1 | 605.3 | 610.2 | 665.1 | 605.9
723 | 578 | 727.8 | 600.6 | 604.1 | 664.8 | 604.8
724 | 579 | 728.5 | 605.9 | 593.3 | 664.8 | 603.4
725 | 580 | 729.4 | 612 | 591.7 | 665.4 | 602.8
726 | 581 | 730.3 | 611.9 | 587.9 | 665.8 | 601.8
727 | 582 | 731.3 | 613.6 | 587.1 | 666.8 | 601.7
728 | 583 | 732 | 609.7 | 587.8 | 668 | 601.2
729 | 584 | 732.8 | 611.6 | 586.7 | 669.4 | 600.5
730 | 585 | 733.5 | 608.7 | 589.1 | 670.9 | 601
731 | 586 | 733.9 | 605.7 | 586.8 | 671.3 | 600
732 | 587 | 734.4 | 604.2 | 586.6 | 671.7 | 599.9
733 | 588 | 734.8 | 607.6 | 581.3 | 671.6 | 598.7
734 | 589 | 735.3 | 617.1 | 575.7 | 671.8 | 597.6
735 | 590 | 736 | 622.1 | 569.3 | 671.6 | 596.5
736 | 591 | 737.7 | 626.2 | 564 | 672.1 | 595.5
737 | 592 | 740.1 | 632.1 | 556.3 | 672.2 | 594.6
738 | 593 | 741.2 | 643.7 | 551.6 | 672.8 | 593.9
739 | 594 | 742.2 | 646.8 | 550.6 | 674.1 | 593
740 | 595 | 742.7 | 650.6 | 548.3 | 675.9 | 592.5
741 | 596 | 742.9 | 653.1 | 543 | 676.6 | 591.9
742 | 597 | 743 | 654.9 | 542.5 | 677.7 | 592.1
743 | 598 | 742.9 | 654 | 541 | 678.6 | 591.8
744 | 599 | 743 | 651.8 | 545.5 | 679.9 | 591.7
745 | 600 | 743.1 | 646.2 | 548.1 | 680.9 | 591.3
746 | 601 | 742.9 | 644.4 | 563.2 | 682.9 | 592.5
747 | 602 | 742.5 | 637.6 | 579 | 685.3 | 594.1
748 | 603 | 742.4 | 628.7 | 577.8 | 686.5 | 593.3
749 | 604 | 742.4 | 621.5 | 571.8 | 686.5 | 592.5
750 | 605 | 742.5 | 620.2 | 567.2 | 686.5 | 592.5
751 | 606 | 742.8 | 627.5 | 562.5 | 687.5 | 591.5
752 | 607 | 742.9 | 628.2 | 570.2 | 689.7 | 591.6
753 | 608 | 743 | 627.3 | 568.1 | 691 | 590.9
754 | 609 | 743.4 | 631.4 | 563.7 | 691.2 | 590.3
755 | 610 | 743.6 | 633.3 | 559 | 691.7 | 589.4
756 | 611 | 743.9 | 634.8 | 553 | 692.5 | 588.4
757 | 612 | 744 | 647.2 | 548.8 | 692.7 | 587.5
758 | 613 | 744.1 | 648.6 | 545.2 | 693.4 | 586.7
759 | 614 | 744.3 | 652.8 | 539.5 | 693.6 | 585.7
760 | 615 | 744.6 | 657.6 | 536.2 | 693.8 | 584.7
761 | 616 | 744.9 | 658 | 539.4 | 694.8 | 584.2
762 | 617 | 745 | 654.9 | 550.2 | 696.6 | 584
763 | 618 | 744.8 | 650.3 | 554.8 | 698.4 | 583.7
764 | 619 | 744.8 | 659.2 | 549.1 | 699.2 | 582.9
765 | 620 | 745 | 661.2 | 546.4 | 699.8 | 582.4
766 | 621 | 745.2 | 660 | 551.2 | 701.3 | 582.4
767 | 622 | 745.4 | 657.7 | 563.5 | 703 | 583
768 | 623 | 745.3 | 651.4 | 575.3 | 706.2 | 583.6
769 | 624 | 745.4 | 647.9 | 573.5 | 707.8 | 582.8
770 | 625 | 745.6 | 653.2 | 564.6 | 708.1 | 581.9
771 | 626 | 746 | 657.5 | 563.1 | 707.4 | 581.3
772 | 627 | 746.3 | 653.1 | 560.4 | 706.5 | 580.6
773 | 628 | 746.4 | 654.2 | 553.8 | 706.3 | 579.4
774 | 629 | 746.6 | 658.8 | 551.3 | 706.5 | 578.4
775 | 630 | 747 | 662.3 | 549.3 | 707.2 | 577.8
776 | 631 | 747.4 | 672.2 | 547.7 | 708 | 577.1
777 | 632 | 747.8 | 673.7 | 555.8 | 709.9 | 577
778 | 633 | 748.1 | 670.2 | 557.7 | 711.6 | 577.3
779 | 634 | 748.3 | 662.6 | 556.5 | 712.5 | 576.8
780 | 635 | 748.5 | 661.6 | 553.2 | 712.7 | 575.8
781 | 636 | 748.7 | 663.5 | 553.3 | 713.4 | 575.2
782 | 637 | 749 | 662.7 | 560.4 | 714.3 | 575.3
783 | 638 | 749 | 656.1 | 568.6 | 715.1 | 575.9
784 | 639 | 749 | 653.1 | 569.3 | 715.2 | 575.9
785 | 640 | 749 | 656.3 | 565.1 | 715.1 | 575.1
786 | 641 | 749 | 660.7 | 568 | 716.5 | 574.9
787 | 642 | 749.1 | 658.5 | 572.2 | 718 | 574.9
788 | 643 | 749.1 | 652.1 | 573.9 | 718.7 | 574.3
789 | 644 | 749.1 | 652.9 | 576.1 | 720.2 | 573.9
790 | 645 | 749.2 | 646.7 | 585.7 | 721.6 | 576
791 | 646 | 749 | 635.6 | 589 | 722.6 | 575.4
792 | 647 | 748.9 | 629.5 | 598.6 | 723.8 | 576.5
793 | 648 | 748.9 | 622.9 | 606.1 | 725 | 577
794 | 649 | 749 | 619.4 | 624.1 | 726.5 | 579.2
795 | 650 | 748.8 | 613.5 | 628.6 | 727.6 | 580.5
796 | 651 | 748.7 | 609.4 | 632.6 | 728.6 | 581
797 | 652 | 748.9 | 603.7 | 629.2 | 728.9 | 580.6
798 | 653 | 749.2 | 599.1 | 632.1 | 729.5 | 581.7
799 | 654 | 749.5 | 596.7 | 627.9 | 729.8 | 581.6
800 | 655 | 749.7 | 595.2 | 625.2 | 730.3 | 581.8
801 | 656 | 750 | 592.7 | 622.2 | 731.1 | 581.7
802 | 657 | 750.5 | 600.2 | 614.9 | 731.4 | 581.3
803 | 658 | 751.1 | 597.8 | 617.3 | 732.7 | 581.4
804 | 659 | 751.8 | 592.8 | 615.1 | 733.9 | 581
805 | 660 | 752.3 | 591.7 | 604.7 | 733.8 | 579.8
806 | 661 | 752.8 | 607.8 | 596.2 | 733.8 | 578.2
807 | 662 | 753.4 | 611.3 | 591.8 | 734.1 | 577.5
808 | 663 | 753.9 | 613 | 590.5 | 734.5 | 577.1
809 | 664 | 754.5 | 618.4 | 589.8 | 735.3 | 576.6
810 | 665 | 755 | 624.1 | 591.6 | 736 | 576.6
811 | 666 | 755.4 | 626.5 | 589.9 | 736.5 | 576
812 | 667 | 755.6 | 625.6 | 588.9 | 737.4 | 575.6
813 | 668 | 755.8 | 623.1 | 592.2 | 738.1 | 575.7
814 | 669 | 756 | 620.3 | 603.4 | 739.1 | 576.5
815 | 670 | 756 | 614.6 | 609.5 | 740.1 | 576.8
816 | 671 | 755.7 | 615.7 | 603.1 | 739.8 | 576.2
817 | 672 | 755.5 | 615.7 | 602.7 | 739.6 | 576.3
818 | 673 | 755.5 | 611.7 | 600.7 | 739.3 | 576
819 | 674 | 755.3 | 607.4 | 600.5 | 738.6 | 575.4
820 | 675 | 755 | 602.7 | 613.4 | 738.8 | 576
821 | 676 | 754.7 | 598.1 | 618 | 739.1 | 576.7
822 | 677 | 754.4 | 596.8 | 617 | 739.7 | 576.2
823 | 678 | 754.2 | 600.7 | 612.7 | 740 | 576.1
824 | 679 | 754 | 599.9 | 607.9 | 739.9 | 575.6
825 | 680 | 753.9 | 599 | 597.2 | 739.4 | 574.5
826 | 681 | 754 | 610.3 | 589.8 | 739.2 | 573.1
827 | 682 | 754.4 | 607.9 | 591.2 | 739.4 | 573.1
828 | 683 | 755 | 605.1 | 603.2 | 740.3 | 574.6
829 | 684 | 755.2 | 604.3 | 601.7 | 740.8 | 574.6
830 | 685 | 755.3 | 607.3 | 594.8 | 741.2 | 573.5
831 | 686 | 755.2 | 611.2 | 588.5 | 741 | 572.2
832 | 687 | 755.1 | 610 | 582.3 | 740.6 | 571.4
833 | 688 | 755.1 | 621.3 | 574.4 | 739.9 | 570.1
834 | 689 | 755 | 633.9 | 567.3 | 739.5 | 568.9
835 | 690 | 754.8 | 637.4 | 566.8 | 739.3 | 568
836 | 691 | 754.8 | 631.4 | 573.3 | 739.7 | 567.8
837 | 692 | 754.7 | 623 | 579 | 740.4 | 567.8
838 | 693 | 754.3 | 617.6 | 577 | 740.3 | 567.3
839 | 694 | 753.9 | 610.7 | 578.2 | 740.5 | 566.6
840 | 695 | 753.7 | 604.9 | 582.3 | 740.8 | 567
841 | 696 | 753.4 | 602.3 | 578.3 | 740.4 | 566.4
842 | 697 | 752.9 | 607.6 | 571.6 | 740.1 | 565.6
843 | 698 | 752.7 | 611.4 | 573.1 | 740.6 | 565.2
844 | 699 | 752.5 | 614.2 | 570.8 | 740.6 | 564.8
845 | 700 | 752.2 | 611.9 | 569.5 | 741.1 | 564.4
846 | 701 | 751.9 | 619 | 564.9 | 740.5 | 563.3
847 | 702 | 751.6 | 633.3 | 558.7 | 740.3 | 562.3
848 | 703 | 751.3 | 648.4 | 556.4 | 740 | 561.3
849 | 704 | 751.3 | 644 | 564.9 | 739.9 | 561.5
850 | 705 | 751.2 | 638.9 | 578.6 | 740.5 | 562.1
851 | 706 | 751 | 635.8 | 584 | 740.8 | 562.1
852 | 707 | 750.7 | 627.9 | 587.4 | 740.9 | 561.9
853 | 708 | 750.4 | 621.9 | 582.6 | 740.9 | 561.3
854 | 709 | 750 | 616.8 | 579 | 740.6 | 560.8
855 | 710 | 749.7 | 618.8 | 584 | 740.9 | 560.8
856 | 711 | 749.4 | 613.7 | 588.9 | 741.4 | 561.4
857 | 712 | 749.1 | 612.5 | 593.3 | 742.1 | 561.4
858 | 713 | 748.8 | 610.5 | 598.2 | 743.2 | 562.4
859 | 714 | 748.5 | 604.9 | 601.9 | 743.8 | 562.6
860 | 715 | 748.1 | 599.4 | 599.8 | 743.5 | 562.5
861 | 716 | 747.8 | 594.2 | 599 | 743.9 | 561.8
862 | 717 | 747.5 | 594.7 | 603.2 | 744.2 | 562.3
863 | 718 | 747.4 | 593.7 | 605.7 | 744.5 | 562.7
864 | 719 | 747.3 | 594.8 | 608.2 | 744.3 | 563.1
865 | 720 | 747.3 | 595.7 | 603.7 | 744.5 | 562.9
866 | 721 | 747.1 | 593.2 | 597.7 | 744.8 | 562.6
867 | 722 | 747.2 | 594.8 | 598.9 | 745.4 | 562.9
868 | 723 | 747.2 | 592 | 595.5 | 745.6 | 562.6
869 | 724 | 746.9 | 591 | 591.3 | 744.9 | 561.9
870 | 725 | 746.5 | 604 | 585.2 | 744.1 | 560.9
871 | 726 | 746.4 | 605.1 | 588 | 743.4 | 560.5
872 | 727 | 746.4 | 604.9 | 598.3 | 743.6 | 561.1
873 | 728 | 746.3 | 606.4 | 600.6 | 743.8 | 561.3
874 | 729 | 745.8 | 611.4 | 592.7 | 743.3 | 559.8
875 | 730 | 745.5 | 613.1 | 591.2 | 743.6 | 559.1
876 | 731 | 745.3 | 609.6 | 592.1 | 744 | 558.8
877 | 732 | 745.2 | 606.7 | 592.1 | 744.2 | 558.6
878 | 733 | 744.6 | 603.3 | 586 | 744.3 | 557.4
879 | 734 | 744.5 | 613.9 | 579.1 | 744.2 | 556.3
880 | 735 | 744.2 | 636.6 | 573.9 | 743.6 | 555.4
881 | 736 | 743.6 | 647.9 | 571.4 | 743.5 | 554.4
882 | 737 | 742.8 | 661.8 | 568.7 | 743.2 | 553.4
883 | 738 | 742.5 | 659.7 | 570 | 743.1 | 553.1
884 | 739 | 742.3 | 660.6 | 568.3 | 742.8 | 552.9
885 | 740 | 741.9 | 656.8 | 566.9 | 742.2 | 552.4
886 | 741 | 741.3 | 661.9 | 565.1 | 742.1 | 551.3
887 | 742 | 740.8 | 660.1 | 563.4 | 742.5 | 550.7
888 | 743 | 740.4 | 655.5 | 561.4 | 742.5 | 549.8
889 | 744 | 740.4 | 650.7 | 564.7 | 741.9 | 550
890 | 745 | 739.5 | 651.4 | 561.3 | 741.3 | 549
891 | 746 | 739 | 650 | 562.2 | 740.8 | 548.5
892 | 747 | 738.3 | 644.3 | 561.7 | 740.5 | 547.9
893 | 748 | 737.6 | 640.2 | 563.4 | 740.5 | 547.5
894 | 749 | 737.3 | 635.2 | 569.1 | 740.8 | 547.6
895 | 750 | 736.8 | 632.8 | 569.7 | 741.1 | 547.4
896 | 751 | 736.7 | 634.3 | 573.7 | 741.9 | 547.5
897 | 752 | 736.5 | 633.1 | 577.1 | 742.3 | 547.4
898 | 753 | 735.9 | 635.3 | 577.9 | 742.3 | 547.3
899 | 754 | 736 | 637.3 | 587.4 | 743.3 | 548.1
900 | 755 | 736.8 | 634.7 | 603.3 | 744.6 | 551
901 | 756 | 737 | 628.1 | 623.6 | 745.6 | 554.8
902 | 757 | 736.2 | 619.8 | 634.5 | 746.6 | 557.5
903 | 758 | 735.6 | 612.3 | 640.1 | 747.3 | 558.3
904 | 759 | 735.6 | 607 | 655.1 | 747.8 | 561.2
905 | 760 | 735.1 | 599.2 | 655.1 | 747.8 | 561.1
906 | 761 | 735 | 593.8 | 655 | 747.8 | 561.8
907 | 762 | 735 | 589.8 | 660.9 | 748.2 | 563.7
908 | 763 | 735.1 | 589.4 | 666.1 | 749 | 565.4
909 | 764 | 735.2 | 586.7 | 668.1 | 749.6 | 566.4
910 | 765 | 734.7 | 581.6 | 660.5 | 750.5 | 566.4
911 | 766 | 734.5 | 577 | 656.2 | 750.4 | 566.5
912 | 767 | 734.3 | 576.4 | 650 | 750.1 | 565.9
913 | 768 | 734.5 | 583.5 | 644.1 | 750.1 | 565.6
914 | 769 | 734.7 | 586.7 | 645.5 | 750.8 | 565.1
915 | 770 | 734.7 | 586.1 | 640.2 | 750.8 | 564.9
916 | 771 | 734.8 | 590.4 | 641.9 | 750.9 | 565
917 | 772 | 734.7 | 585.4 | 636 | 750.6 | 564.2
918 | 773 | 735.1 | 587.8 | 636.2 | 750.8 | 564.1
919 | 774 | 735 | 597 | 628.5 | 750.9 | 563.5
920 | 775 | 734.6 | 611.6 | 623.7 | 750.9 | 562.4
921 | 776 | 734.7 | 609.1 | 623.7 | 750.6 | 561.9
922 | 777 | 734.6 | 610.2 | 622.1 | 750.8 | 561
923 | 778 | 735.1 | 610.8 | 630.3 | 751.5 | 562.3
924 | 779 | 735.4 | 605.6 | 630.2 | 751.9 | 561.9
925 | 780 | 735.7 | 610.3 | 631.9 | 752.5 | 562.2
926 | 781 | 735.9 | 607.6 | 631.3 | 752.4 | 562
927 | 782 | 735.3 | 603.1 | 622.2 | 752.4 | 560.6
928 | 783 | 735 | 616.7 | 619.7 | 752.7 | 559.7
929 | 784 | 734.7 | 618.1 | 615.2 | 752.5 | 558.7
930 | 785 | 734.2 | 633.1 | 609.5 | 752.3 | 557.5
931 | 786 | 734.1 | 641.6 | 603.3 | 752 | 556.2
932 | 787 | 733.8 | 650.6 | 598 | 751.3 | 555
933 | 788 | 733.6 | 657.4 | 595.1 | 751 | 553.9
934 | 789 | 733.4 | 661.8 | 591.4 | 751 | 552.6
935 | 790 | 733.3 | 659.9 | 592.7 | 752 | 552.2
936 | 791 | 733.4 | 657.8 | 593.3 | 752.9 | 551.4
937 | 792 | 734.2 | 650.7 | 595.6 | 752.9 | 551.3
938 | 793 | 733.7 | 645.9 | 591.9 | 752.8 | 550
939 | 794 | 733.3 | 645.6 | 589.1 | 752.8 | 549
940 | 795 | 733.1 | 647 | 589.6 | 753.1 | 548.2
941 | 796 | 733.4 | 644.3 | 593.8 | 753.6 | 548.5
942 | 797 | 733.4 | 646.7 | 593.4 | 753.9 | 547.6
943 | 798 | 733.2 | 643.7 | 590.8 | 753.8 | 546.6
944 | 799 | 732.5 | 642.2 | 588 | 753.4 | 545.4
945 | 800 | 731.9 | 646.3 | 584.9 | 752.7 | 544.3
946 | 801 | 731.5 | 647.7 | 585 | 752.5 | 543.4
947 | 802 | 731.1 | 653 | 582.9 | 751.8 | 542.7
948 | 803 | 730.1 | 653 | 579.3 | 751.8 | 541.9
949 | 804 | 729.2 | 654.9 | 577.5 | 751.5 | 541
950 | 805 | 728.5 | 662 | 577.1 | 750.4 | 540.1
951 | 806 | 727.8 | 664.6 | 574.2 | 749.7 | 539.2
952 | 807 | 727 | 670.1 | 572.9 | 748.6 | 538.1
953 | 808 | 727.1 | 669.1 | 577.3 | 748 | 537.8
954 | 809 | 727.1 | 659.4 | 580.9 | 748.2 | 537.6
955 | 810 | 726.9 | 655 | 582.2 | 748.4 | 537.4
956 | 811 | 726.8 | 649.5 | 584.6 | 748 | 537.5
957 | 812 | 726.5 | 635.5 | 585.3 | 747.8 | 537.2
958 | 813 | 725.9 | 634.3 | 584.4 | 747.6 | 536.8
959 | 814 | 725.2 | 630.3 | 588.8 | 747.3 | 537.2
960 | 815 | 724.5 | 619.7 | 590.7 | 746.9 | 537
961 | 816 | 724.1 | 609.6 | 597.8 | 746.3 | 537.3
962 | 817 | 723.7 | 602.7 | 603 | 746 | 538.3
963 | 818 | 723 | 594.3 | 601.3 | 745.9 | 537.2
964 | 819 | 722.3 | 597.9 | 605.4 | 745.6 | 537.1
965 | 820 | 721.3 | 591.4 | 602.6 | 745 | 536.7
966 | 821 | 720.3 | 589.4 | 598.7 | 744.3 | 536
967 | 822 | 719.6 | 594.9 | 600.8 | 743.8 | 535.9
968 | 823 | 719.2 | 592.6 | 604.8 | 743.7 | 536.3
969 | 824 | 718.4 | 584.5 | 600.6 | 743.5 | 535.8
970 | 825 | 717.4 | 579.9 | 600.6 | 743.9 | 535.4
971 | 826 | 716.8 | 580.4 | 605 | 744.2 | 536.2
972 | 827 | 716 | 572.3 | 607.8 | 744.9 | 536.1
973 | 828 | 715.4 | 567.8 | 611.2 | 745.3 | 536.5
974 | 829 | 714.7 | 563.4 | 604.9 | 746.2 | 535.9
975 | 830 | 713.7 | 565.8 | 602.7 | 747.6 | 535.3
976 | 831 | 713.2 | 571.1 | 600.8 | 748.4 | 535.2
977 | 832 | 712.5 | 571.6 | 595.5 | 749.2 | 534.1
978 | 833 | 712 | 575.4 | 594.7 | 749.1 | 533.6
979 | 834 | 711.6 | 581.1 | 594.9 | 748.8 | 533.2
980 | 835 | 711.5 | 586.3 | 600.5 | 748.5 | 533.6
981 | 836 | 711.5 | 585 | 610.9 | 748.4 | 534.8
982 | 837 | 711.3 | 580.8 | 618.3 | 748.9 | 535.2
983 | 838 | 711 | 576.5 | 623.3 | 749.2 | 536
984 | 839 | 710 | 571.4 | 615 | 749.4 | 535.3
985 | 840 | 709.1 | 572.2 | 611.7 | 750.2 | 534.7
986 | 841 | 708.8 | 576.3 | 611.5 | 750.5 | 534.6
987 | 842 | 708.4 | 580.8 | 614.4 | 750 | 534.6
988 | 843 | 708 | 587.7 | 619.8 | 750.1 | 535.3
989 | 844 | 707.8 | 587.6 | 621.6 | 750.8 | 535.7
990 | 845 | 707.5 | 583.5 | 625.8 | 750.8 | 536.5
991 | 846 | 707.1 | 579.1 | 622.7 | 750.6 | 536.4
992 | 847 | 706.7 | 575.1 | 620 | 750.8 | 536.4
993 | 848 | 706.1 | 570 | 617.2 | 750.7 | 535.9
994 | 849 | 705.4 | 566.2 | 614 | 751 | 535.5
995 | 850 | 704.3 | 561.7 | 608.8 | 750.7 | 534.8
996 | 851 | 703.7 | 559.4 | 606.3 | 750.5 | 534.5
997 | 852 | 702.9 | 556.1 | 601.4 | 750.7 | 533.7
998 | 853 | 702.3 | 553 | 596.7 | 750.8 | 533.2
999 | 854 | 701.9 | 551.2 | 594.2 | 751 | 532.4
1000 | 855 | 702.1 | 551 | 599.9 | 751 | 533.1
1001 | 856 | 701.7 | 547.8 | 600.4 | 750.5 | 532.8
1002 | 857 | 701.1 | 545 | 597.3 | 750.1 | 532.5
1003 | 858 | 700.6 | 543.2 | 597.6 | 749.7 | 532.3
1004 | 859 | 700 | 540.7 | 595.8 | 749.3 | 532.1
1005 | 860 | 699.2 | 537.9 | 590.9 | 749.2 | 531.6
1006 | 861 | 698.6 | 537.3 | 589.4 | 748.7 | 531.4
1007 | 862 | 698.2 | 535.7 | 589.8 | 748.1 | 531.1
1008 | 863 | 697.4 | 533.9 | 588.8 | 747.3 | 530.6
1009 | 864 | 697.1 | 533.2 | 587 | 746.9 | 530.2
1010 | 865 | 696.3 | 532.6 | 579.7 | 746.6 | 529.2
1011 | 866 | 695.5 | 538.2 | 574.7 | 746.3 | 528.3
1012 | 867 | 694.7 | 542 | 568.1 | 745.9 | 527.6
1013 | 868 | 693.7 | 540.7 | 561.1 | 745.8 | 527
1014 | 869 | 692.7 | 543.8 | 559.1 | 745.5 | 526.2
1015 | 870 | 692 | 547.9 | 561.9 | 744.8 | 526.4
1016 | 871 | 691.8 | 550.5 | 570.9 | 743.8 | 526.9
1017 | 872 | 692.2 | 549.5 | 581.9 | 744.3 | 528.1
1018 | 873 | 691.9 | 546.1 | 575.1 | 744 | 527.1
1019 | 874 | 690.9 | 541.9 | 566.2 | 743.3 | 526.2
1020 | 875 | 689.7 | 536.7 | 560.3 | 742.8 | 525.4
1021 | 876 | 688.9 | 535 | 557.9 | 741.9 | 524.7
1022 | 877 | 688.2 | 532.1 | 554.3 | 741.1 | 524.1
1023 | 878 | 687.9 | 529.9 | 555 | 740.7 | 523.6
1024 | 879 | 687.7 | 527.9 | 555.5 | 740.3 | 523.6
1025 | 880 | 687.3 | 525.2 | 552.5 | 740.1 | 523.4
1026 | 881 | 686.9 | 522.2 | 554.3 | 740.2 | 523.1
1027 | 882 | 686.7 | 521.6 | 564.7 | 740.5 | 524.4
1028 | 883 | 686.5 | 521.3 | 570.2 | 740.4 | 525.7
1029 | 884 | 686.4 | 521.8 | 585.4 | 740.6 | 526.6
1030 | 885 | 687.1 | 527.1 | 618.2 | 742.3 | 532.5
1031 | 886 | 687.6 | 530.8 | 619.4 | 742.2 | 533
1032 | 887 | 687.9 | 532 | 618.2 | 741.6 | 533.2
1033 | 888 | 688 | 532.4 | 612.6 | 741.2 | 533.7
1034 | 889 | 687.7 | 531 | 603.1 | 740 | 533.4
1035 | 890 | 686.8 | 527.2 | 590.6 | 739.1 | 532.5
1036 | 891 | 685.8 | 521.7 | 579.9 | 738.3 | 531.5
1037 | 892 | 684.9 | 518 | 571.6 | 737.2 | 530.8
1038 | 893 | 684.5 | 516.1 | 569 | 736.3 | 530.2
1039 | 894 | 684.7 | 516.8 | 570 | 735.6 | 530.4
1040 | 895 | 684.8 | 516 | 565.6 | 735.3 | 529.8
1041 | 896 | 684.4 | 513.7 | 562 | 734.8 | 529.3
1042 | 897 | 684.1 | 512.4 | 557.9 | 734.7 | 528.8
1043 | 898 | 683.8 | 512 | 557.8 | 734.8 | 528.3
1044 | 899 | 683.3 | 510.4 | 554.5 | 734.5 | 527.7
1045 | 900 | 682.8 | 508.2 | 549.9 | 734 | 526.7
1046 | 901 | 682.4 | 507 | 546.9 | 733.9 | 526.2
1047 | 902 | 682.3 | 506.4 | 549.5 | 733.9 | 526.2
1048 | 903 | 682.1 | 505.7 | 551.3 | 733.2 | 525.9
1049 | 904 | 682.4 | 506.9 | 558.7 | 733.1 | 526.2
1050 | 905 | 682.8 | 509.4 | 563.9 | 733.1 | 526.6
1051 | 906 | 682.6 | 509.2 | 558.2 | 732.7 | 525.9
1052 | 907 | 682.3 | 508.5 | 559.3 | 732.5 | 525.9
1053 | 908 | 681.9 | 507.7 | 559.9 | 732.1 | 525.6
1054 | 909 | 682.2 | 511.3 | 581.5 | 732.9 | 528.4
1055 | 910 | 682.2 | 513 | 581.6 | 732.9 | 528.5
1056 | 911 | 682 | 513.6 | 576.2 | 732.4 | 528.1
1057 | 912 | 681.4 | 511.1 | 568.8 | 731.4 | 527
1058 | 913 | 681.3 | 511 | 569.5 | 730.9 | 526.7
1059 | 914 | 681.3 | 511.4 | 568.8 | 730.3 | 526.5
1060 | 915 | 681.8 | 513.2 | 571.5 | 729.9 | 526.7
1061 | 916 | 682.3 | 513.9 | 576.4 | 730 | 526.7
1062 | 917 | 682.7 | 514.6 | 577.4 | 729.6 | 526.8
1063 | 918 | 682.8 | 514.8 | 576.2 | 729.4 | 526.9
1064 | 919 | 682.5 | 513.1 | 571.2 | 728.7 | 526.2
1065 | 920 | 682 | 510.7 | 566.2 | 728.4 | 525.5
1066 | 921 | 681.8 | 510.5 | 568.7 | 727.9 | 525.9
1067 | 922 | 681.8 | 510.6 | 568.9 | 727.8 | 525.7
1068 | 923 | 681.7 | 510.9 | 568.1 | 727.6 | 525.3
1069 | 924 | 681.5 | 510.6 | 569.2 | 727.3 | 525.1
1070 | 925 | 681.6 | 512 | 577.3 | 727.2 | 525.7
1071 | 926 | 682.1 | 514.5 | 588.2 | 727.4 | 527
1072 | 927 | 682.1 | 515.6 | 592.2 | 727.4 | 527.7
1073 | 928 | 682.2 | 516.1 | 590.2 | 727.2 | 528
1074 | 929 | 682 | 514.2 | 580.2 | 726.6 | 526.7
1075 | 930 | 681.1 | 510 | 567.5 | 725.9 | 525
1076 | 931 | 680.4 | 504.4 | 553.3 | 724.4 | 523.3
1077 | 932 | 679.8 | 497 | 540.6 | 723.3 | 521.9
1078 | 933 | 679.1 | 491.2 | 528.6 | 721.5 | 520
1079 | 934 | 678.5 | 486.2 | 520 | 719.7 | 518.3
1080 | 935 | 677.6 | 481.4 | 511.7 | 718.2 | 516.8
1081 | 936 | 677 | 476.8 | 502.8 | 715.6 | 515.2
1082 | 937 | 676.3 | 472.9 | 494.7 | 713.5 | 513.5
1083 | 938 | 675.3 | 469 | 488.2 | 711.7 | 511.7
1084 | 939 | 674.6 | 466.4 | 481.6 | 710.1 | 510.5
1085 | 940 | 673.9 | 463.7 | 475.6 | 708.9 | 509.3
1086 | 941 | 673.3 | 460.3 | 470.6 | 707 | 507.9
1087 | 942 | 672.6 | 457.6 | 466 | 705.5 | 506.4
1088 | 943 | 672 | 455 | 461.9 | 704.1 | 504.9
1089 | 944 | 671.5 | 451.8 | 457 | 702.6 | 503.3
1090 | 945 | 670.8 | 449.1 | 452.5 | 701.3 | 501.6
1091 | 946 | 670.3 | 446.7 | 449.3 | 700.3 | 499.6
1092 | 947 | 669.7 | 443.9 | 445.6 | 699.1 | 498.3
1093 | 948 | 669.3 | 441 | 441.9 | 698.6 | 497
1094 | 949 | 668.8 | 438.2 | 438 | 698.2 | 495.8
1095 | 950 | 668.3 | 436.1 | 435.5 | 697.1 | 494.2
1096 | 951 | 667.6 | 434.5 | 433.3 | 696.4 | 492.3
1097 | 952 | 667 | 433.5 | 430.5 | 695.2 | 490.6
1098 | 953 | 666.4 | 432 | 427.3 | 694.9 | 489.4
1099 | 954 | 665.9 | 430.3 | 424.4 | 694.2 | 488.4
1100 | 955 | 665.6 | 428.2 | 421.3 | 693.4 | 487.2
1101 | 956 | 665.3 | 427.1 | 419.1 | 692.9 | 486.2
1102 | 957 | 665.1 | 424.6 | 417.7 | 691.4 | 485.1
1103 | 958 | 664.8 | 423 | 415.8 | 690 | 484.1
1104 | 959 | 664.6 | 422 | 413.4 | 688.3 | 482.7
1105 | 960 | 664.3 | 421.5 | 411.1 | 687.1 | 481.4
1106 | 961 | 663.9 | 420.6 | 409.4 | 686.2 | 480
1107 | 962 | 663.6 | 419.6 | 406.6 | 685.4 | 478.9
1108 | 963 | 663.5 | 418.7 | 404.5 | 684.1 | 478
1109 | 964 | 663.4 | 416.9 | 402.7 | 684.1 | 476.7
1110 | 965 | 663.2 | 415.5 | 401.3 | 682.7 | 475.5
1111 | 966 | 663 | 415 | 399.8 | 681.6 | 474.6
1112 | 967 | 662.7 | 414.4 | 398.2 | 681 | 473.6
1113 | 968 | 662.5 | 413.1 | 397.2 | 679.7 | 472.7
1114 | 969 | 662.4 | 413.6 | 395.5 | 678.7 | 471.6
1115 | 970 | 662.1 | 412.3 | 392.8 | 677.7 | 470.6
1116 | 971 | 661.8 | 412.5 | 391.7 | 676.2 | 469.7
1117 | 972 | 661.6 | 412.2 | 391.2 | 675.5 | 468.6
1118 | 973 | 661.5 | 411.4 | 389.7 | 673.7 | 467.5
1119 | 974 | 661.5 | 410.4 | 388.4 | 672.3 | 466.8
1120 | 975 | 661.5 | 410.5 | 387.1 | 671.5 | 465.8
1121 | 976 | 661.6 | 410.6 | 385.5 | 670.2 | 464.9
1122 | 977 | 661.6 | 409.4 | 384.1 | 668.4 | 463.9
1123 | 978 | 661.5 | 408.6 | 382.8 | 666.8 | 462.8
1124 | 979 | 661.4 | 408.1 | 381.6 | 665.4 | 461.8
1125 | 980 | 661.2 | 407.6 | 380.5 | 663.7 | 460.7
1126 | 981 | 660.9 | 407.5 | 379.8 | 662.4 | 459.8
1127 | 982 | 660.7 | 407.3 | 379.3 | 661.4 | 458.8
1128 | 983 | 660.5 | 406.5 | 379.5 | 659.7 | 457.9
1129 | 984 | 660.2 | 406 | 378.8 | 658.6 | 457.1
1130 | 985 | 660 | 405.3 | 377.2 | 657.5 | 456.3
1131 | 986 | 659.6 | 404.9 | 375.7 | 656 | 455.5
1132 | 987 | 659.2 | 404.2 | 373.9 | 654.8 | 454.7
1133 | 988 | 658.7 | 403.2 | 372.3 | 654.2 | 453.8
1134 | 989 | 658.2 | 402.7 | 370.9 | 652.7 | 452.9
1135 | 990 | 657.9 | 402.2 | 369.3 | 651.8 | 452
1136 | 991 | 657.5 | 402.1 | 368.1 | 651 | 450.9
1137 | 992 | 657.3 | 401.5 | 366.8 | 650.1 | 449.6
1138 | 993 | 657 | 401.4 | 365.9 | 648.7 | 448.9
1139 | 994 | 656.7 | 401 | 365.2 | 647.4 | 448.1
1140 | 995 | 656.4 | 400.4 | 364.3 | 646.8 | 447.2
1141 | 996 | 656.1 | 399.9 | 363.5 | 645.1 | 446.5
1142 | 997 | 656 | 399.7 | 362.8 | 643.9 | 445.6
1143 | 998 | 655.8 | 399.9 | 362.2 | 642.8 | 445
1144 | 999 | 655.7 | 399.2 | 362 | 642 | 444.5
1145 | 1000 | 655.4 | 398.6 | 361.5 | 640.7 | 443.7
1146 | 1001 | 655.2 | 398 | 360.4 | 639.5 | 443.1
1147 | 1002 | 654.8 | 397.5 | 359.6 | 638.1 | 442.4
1148 | 1003 | 654.2 | 396.5 | 358.5 | 637.2 | 441.6
1149 | 1004 | 653.7 | 396.1 | 357.3 | 636.1 | 441.1
1150 | 1005 | 653.4 | 395.5 | 357.1 | 635.3 | 440.4
1151 | 1006 | 653 | 394.3 | 356.1 | 634.6 | 439.5
1152 | 1007 | 652.6 | 393.2 | 355.1 | 633.2 | 438.7
1153 | 1008 | 652.2 | 393 | 354.4 | 632.6 | 437.9
1154 | 1009 | 651.7 | 392.6 | 353.6 | 631.7 | 437.3
1155 | 1010 | 651.1 | 391.4 | 352.4 | 630.5 | 436.4
1156 | 1011 | 650.4 | 390.3 | 351.9 | 630.3 | 435.5
1157 | 1012 | 649.9 | 389.6 | 351 | 629.8 | 434.7
1158 | 1013 | 649.4 | 388.9 | 350.7 | 629.3 | 434
1159 | 1014 | 649 | 387.6 | 349.8 | 628.7 | 433.3
1160 | 1015 | 648.4 | 387.1 | 348.5 | 628.1 | 432.4
1161 | 1016 | 647.9 | 386.4 | 347.2 | 627.2 | 431.6
1162 | 1017 | 647.5 | 386 | 346.5 | 626.7 | 430.7
1163 | 1018 | 647 | 385.8 | 345.3 | 626.1 | 429.6
1164 | 1019 | 646.4 | 384.7 | 344.2 | 625 | 428.8
1165 | 1020 | 646 | 384.4 | 343.2 | 624.1 | 427.9
1166 | 1021 | 645.4 | 383.7 | 342.6 | 623.7 | 427.2
1167 | 1022 | 644.9 | 383.1 | 342 | 623 | 426.5
1168 | 1023 | 644.4 | 382.3 | 341.6 | 622.4 | 425.7
1169 | 1024 | 643.9 | 382 | 340.8 | 621.4 | 425
1170 | 1025 | 643.4 | 381.1 | 339.9 | 620.1 | 424.1
1171 | 1026 | 642.8 | 380.7 | 338.9 | 619.2 | 423.2
1172 | 1027 | 642 | 380.3 | 338.3 | 618.6 | 422.5
1173 | 1028 | 641.3 | 378.9 | 337.6 | 618.2 | 421.6
1174 | 1029 | 640.7 | 378.2 | 337.1 | 617.6 | 420.7
1175 | 1030 | 640 | 378 | 335.9 | 616.4 | 420
1176 | 1031 | 639.3 | 377.8 | 335.2 | 615.5 | 419.1
1177 | 1032 | 638.7 | 377.4 | 334.6 | 614.4 | 418.3
1178 | 1033 | 638.1 | 377.3 | 333.9 | 613.9 | 417.5
1179 | 1034 | 637.4 | 377.8 | 333.1 | 613.3 | 416.7
1180 | 1035 | 636.7 | 377.6 | 331.9 | 613 | 416
1181 | 1036 | 636 | 377.3 | 330.5 | 612.6 | 415.1
1182 | 1037 | 635.4 | 376.5 | 329.9 | 612.4 | 414.2
1183 | 1038 | 634.6 | 375.5 | 329.5 | 611.9 | 413.5
1184 | 1039 | 633.7 | 374.4 | 329.2 | 611.6 | 412.7
1185 | 1040 | 633 | 374.4 | 327.8 | 611.3 | 412.1
1186 | 1041 | 632.1 | 372.9 | 327 | 610.7 | 411.1
1187 | 1042 | 631.4 | 372.3 | 326.4 | 610.4 | 410.2
1188 | 1043 | 630.7 | 371.7 | 325 | 609.5 | 409.2
1189 | 1044 | 630 | 371.7 | 323.6 | 609.2 | 408.3
1190 | 1045 | 629.4 | 371.7 | 322.6 | 608.6 | 407.6
1191 | 1046 | 628.8 | 371.6 | 321.7 | 608.1 | 406.8
1192 | 1047 | 628.2 | 371.5 | 321.2 | 607.4 | 406.2
1193 | 1048 | 627.5 | 370.7 | 320.3 | 607.1 | 405.4
1194 | 1049 | 627.1 | 370.4 | 319.4 | 606.5 | 404.6
1195 | 1050 | 626.7 | 370.5 | 318.3 | 606 | 403.8
1196 | 1051 | 626.2 | 370.2 | 317.8 | 605.2 | 402.8
1197 | 1052 | 625.8 | 370.1 | 316.6 | 604.4 | 402
1198 | 1053 | 625.3 | 369.5 | 315.5 | 604.1 | 401.3
1199 | 1054 | 624.8 | 369.1 | 314.5 | 603.3 | 400.5
1200 | 1055 | 624.3 | 368.7 | 313.4 | 602.8 | 399.7
1201 | 1056 | 623.9 | 368.9 | 312.7 | 602.5 | 399
1202 | 1057 | 623.6 | 367.8 | 311.9 | 602.1 | 398.1
1203 | 1058 | 623.2 | 367 | 310.6 | 601.7 | 397.3
1204 | 1059 | 622.8 | 366.4 | 309.4 | 601.4 | 396.6
1205 | 1060 | 622.5 | 366 | 308.7 | 601.1 | 396
1206 | 1061 | 622.1 | 365.6 | 308.2 | 600.6 | 395.4
1207 | 1062 | 621.7 | 365.1 | 307.1 | 599.8 | 394.7
1208 | 1063 | 621.4 | 365 | 306.3 | 599 | 393.8
1209 | 1064 | 621 | 364.3 | 305.5 | 598.7 | 392.9
1210 | 1065 | 620.5 | 364 | 304.4 | 598.4 | 392.1
1211 | 1066 | 620 | 363.5 | 303.3 | 598.1 | 391.1
1212 | 1067 | 619.5 | 362.9 | 302.1 | 597.8 | 390.6
1213 | 1068 | 619 | 361.9 | 301.1 | 597.1 | 389.8
1214 | 1069 | 618.5 | 361.3 | 300.8 | 597.6 | 388.9
1215 | 1070 | 617.9 | 360.1 | 300 | 597.7 | 388.4
1216 | 1071 | 617.3 | 358.7 | 299.2 | 597.8 | 387.7
1217 | 1072 | 616.5 | 357.5 | 297.8 | 598.2 | 386.9
1218 | 1073 | 615.8 | 355.9 | 297.2 | 598.3 | 386.3
1219 | 1074 | 615.2 | 354.4 | 296.4 | 597.4 | 385.7
1220 | 1075 | 614.5 | 353.6 | 295.4 | 597.7 | 385.1
1221 | 1076 | 613.9 | 352.5 | 294.8 | 597.6 | 384.6
1222 | 1077 | 613.4 | 351.5 | 293.4 | 597 | 384
1223 | 1078 | 612.8 | 350.3 | 292.4 | 596.6 | 383.4
1224 | 1079 | 612.2 | 348.7 | 291.2 | 596.4 | 382.6
1225 | 1080 | 611.5 | 347.1 | 290 | 595.9 | 381.9
1226 | 1081 | 610.8 | 346.1 | 289 | 595.3 | 381.2
1227 | 1082 | 610.3 | 345.2 | 288 | 595.4 | 380.6
1228 | 1083 | 609.7 | 344.2 | 287.1 | 594.8 | 379.7
1229 | 1084 | 609.1 | 342.9 | 287 | 594.5 | 379.1
1230 | 1085 | 608.5 | 342.3 | 286.9 | 593.7 | 378.3
1231 | 1086 | 607.7 | 340.9 | 286 | 593 | 377.5
1232 | 1087 | 607.2 | 339.3 | 285.3 | 592.8 | 376.9
1233 | 1088 | 606.6 | 337.8 | 284.3 | 592.2 | 376.3
1234 | 1089 | 606.1 | 336.5 | 283.2 | 591.4 | 375.8
1235 | 1090 | 605.6 | 335.4 | 282.2 | 590.7 | 375.2
1236 | 1091 | 605.1 | 334.9 | 281.5 | 590.1 | 374.6
1237 | 1092 | 604.7 | 333.8 | 280.9 | 589 | 374
1238 | 1093 | 604.2 | 332.6 | 279.9 | 587.7 | 373.3
1239 | 1094 | 603.8 | 332.1 | 278.8 | 586.8 | 372.7
1240 | 1095 | 603.5 | 331.4 | 278.3 | 586.6 | 371.5
1241 | 1096 | 602.9 | 330.7 | 277.5 | 586.2 | 370.6
1242 | 1097 | 602.3 | 329.4 | 276.9 | 586.1 | 370.1
1243 | 1098 | 601.8 | 328 | 275.9 | 585.3 | 369.3
1244 | 1099 | 601.2 | 326.7 | 274.9 | 584.6 | 368.5
1245 | 1100 | 600.5 | 326.1 | 274.1 | 584.7 | 367.7
1246 | 1101 | 599.8 | 325.3 | 273.5 | 583.9 | 367.3
1247 | 1102 | 599 | 324 | 272.7 | 584.3 | 366.8
1248 | 1103 | 598.4 | 323.5 | 271.5 | 583.8 | 365.9
1249 | 1104 | 597.7 | 322.7 | 270.9 | 583.8 | 365.3
1250 | 1105 | 596.9 | 322.1 | 270.1 | 582.9 | 364.6
1251 | 1106 | 596.2 | 321 | 269.6 | 581.9 | 364.2
1252 | 1107 | 595.4 | 320.5 | 269.1 | 581.1 | 363.4
1253 | 1108 | 594.6 | 319.3 | 268.4 | 580.8 | 363.1
1254 | 1109 | 593.9 | 318.3 | 267.5 | 580 | 362.7
1255 | 1110 | 593.2 | 317.4 | 266.5 | 578.6 | 362.3
1256 | 1111 | 592.5 | 317.1 | 265.4 | 578.3 | 361.9
1257 | 1112 | 591.8 | 316.2 | 264.1 | 577.4 | 361.4
1258 | 1113 | 591.1 | 315.5 | 263.1 | 576.8 | 360.9
1259 | 1114 | 590.5 | 314.5 | 262.3 | 575.4 | 360.2
1260 | 1115 | 590.1 | 313.3 | 261.6 | 574.6 | 359.6
1261 | 1116 | 589.7 | 312.9 | 260.8 | 574.1 | 358.9
1262 | 1117 | 589.1 | 312 | 259.8 | 573 | 358.4
1263 | 1118 | 588.5 | 311.1 | 258.6 | 572.4 | 357.9
1264 | 1119 | 588 | 309.8 | 257.6 | 571.3 | 357.5
1265 | 1120 | 587.6 | 309.6 | 256.6 | 570.6 | 357.1
1266 | 1121 | 587.1 | 308.6 | 255.6 | 570.3 | 356.5
1267 | 1122 | 586.7 | 307.8 | 254.7 | 569.7 | 356.1
1268 | 1123 | 586.2 | 307.4 | 253.6 | 569 | 355.5
1269 | 1124 | 585.7 | 306.8 | 252.5 | 568.6 | 355
1270 | 1125 | 585.2 | 306.1 | 251.7 | 567.7 | 354.5
1271 | 1126 | 584.6 | 305.7 | 250.9 | 567.3 | 354
1272 | 1127 | 584 | 305.1 | 249.9 | 566.4 | 353.3
1273 | 1128 | 583.5 | 304.3 | 248.9 | 565.6 | 352.6
1274 | 1129 | 583 | 303.5 | 248.1 | 565.7 | 352.1
1275 | 1130 | 582.5 | 302.7 | 247.6 | 563.5 | 351.7
1276 | 1131 | 582 | 301.8 | 246.5 | 563.5 | 351.3
1277 | 1132 | 581.5 | 301.2 | 245.5 | 563 | 350.5
1278 | 1133 | 581 | 300.8 | 244.3 | 563.5 | 350
1279 | 1134 | 580.4 | 300.1 | 243.2 | 563.9 | 349.8
1280 | 1135 | 579.9 | 298.9 | 241.9 | 563.6 | 349.3
1281 | 1136 | 579.3 | 298.4 | 240.8 | 562.2 | 348.7
1282 | 1137 | 578.9 | 297.3 | 239.8 | 562.3 | 348
1283 | 1138 | 578.3 | 296.3 | 238.8 | 562.3 | 347.4
1284 | 1139 | 577.6 | 295.6 | 237.9 | 562.2 | 346.8
1285 | 1140 | 577 | 295.3 | 236.9 | 562 | 346.1
1286 | 1141 | 576.3 | 294.9 | 235.8 | 560.3 | 345.7
1287 | 1142 | 575.5 | 294.4 | 235.1 | 561 | 345
1288 | 1143 | 574.6 | 293.6 | 234 | 560.7 | 344.3
1289 | 1144 | 573.6 | 293 | 233 | 560.3 | 343.8
1290 | 1145 | 572.6 | 291.7 | 231.6 | 558.8 | 343.3
1291 | 1146 | 571.7 | 290.7 | 230.6 | 559.1 | 342.6
1292 | 1147 | 570.7 | 289.6 | 229.5 | 558.3 | 342
1293 | 1148 | 569.5 | 289.2 | 228.1 | 558 | 341.5
1294 | 1149 | 568.3 | 288.6 | 226.6 | 557.2 | 340.8
1295 | 1150 | 567.2 | 288.2 | 224.9 | 556.3 | 339.9
1296 | 1151 | 566.1 | 287.8 | 223.5 | 555.5 | 339.3
1297 | 1152 | 565.2 | 286.7 | 222.3 | 555 | 339
1298 | 1153 | 564.3 | 285.7 | 221.3 | 555.5 | 338.3
1299 | 1154 | 563.4 | 285.5 | 219.9 | 555.3 | 338
1300 | 1155 | 562.6 | 285 | 218.7 | 555 | 337.9
1301 | 1156 | 561.9 | 284.6 | 217.7 | 554.9 | 337.6
1302 | 1157 | 561.3 | 284.5 | 217.4 | 554.7 | 337.4
1303 | 1158 | 560.6 | 284.6 | 216.1 | 554.7 | 337.2
1304 | 1159 | 560.1 | 284.8 | 214.8 | 554 | 336.8
1305 | 1160 | 559.5 | 284.2 | 213.6 | 553.7 | 336
1306 | 1161 | 558.9 | 284.3 | 212.1 | 553.4 | 335.5
1307 | 1162 | 558.1 | 283.8 | 210.7 | 553.1 | 335.2
1308 | 1163 | 557.1 | 283.6 | 209.5 | 552.7 | 334.6
1309 | 1164 | 556 | 283.2 | 208 | 553 | 333.9
1310 | 1165 | 555.1 | 282.4 | 206.5 | 552.3 | 333.4
1311 | 1166 | 554.2 | 281.3 | 205.4 | 551.3 | 333.1
1312 | 1167 | 553.3 | 279.9 | 204.5 | 551 | 332.4
1313 | 1168 | 552.2 | 278.6 | 203.3 | 550.2 | 331.4
1314 | 1169 | 551.3 | 277.4 | 202 | 549.7 | 330.7
1315 | 1170 | 550.4 | 276.6 | 200.7 | 548.7 | 330.2
1316 | 1171 | 549.6 | 276 | 199.7 | 548.5 | 329.3
1317 | 1172 | 548.7 | 275.7 | 198.6 | 547.9 | 328.7
1318 | 1173 | 548 | 275.3 | 197.4 | 547.5 | 328
1319 | 1174 | 547.5 | 274.6 | 196 | 546.8 | 327.7
1320 | 1175 | 546.8 | 274 | 194.7 | 546.1 | 327
1321 | 1176 | 546.1 | 274 | 193.9 | 545.9 | 326.2
1322 | 1177 | 545.6 | 274.1 | 192.9 | 545.7 | 325.7
1323 | 1178 | 545.1 | 273.5 | 191.7 | 545.3 | 325.6
1324 | 1179 | 544.5 | 273 | 190.8 | 544.5 | 325.1
1325 | 1180 | 544.1 | 272.5 | 189.9 | 543.7 | 324.4
1326 | 1181 | 543.6 | 271.8 | 188.9 | 543.1 | 323.7
1327 | 1182 | 543 | 270.6 | 187.9 | 542.5 | 323.4
1328 | 1183 | 542.5 | 269.5 | 187 | 542.1 | 322.8
1329 | 1184 | 542 | 268.6 | 186.1 | 541.6 | 322.2
1330 | 1185 | 541.6 | 267.9 | 185.5 | 541 | 321.7
1331 | 1186 | 541.2 | 267.2 | 184.8 | 540.7 | 320.9
1332 | 1187 | 540.7 | 265.8 | 183.7 | 540.5 | 320.3
1333 | 1188 | 540.2 | 265.2 | 182.8 | 540.2 | 319.8
1334 | 1189 | 539.8 | 265 | 182 | 539.8 | 319.4
1335 | 1190 | 539.2 | 264.7 | 180.7 | 539.5 | 318.8
1336 | 1191 | 538.5 | 264.5 | 179.4 | 539.1 | 318.3
1337 | 1192 | 537.7 | 264.4 | 178.2 | 539 | 317.8
1338 | 1193 | 537 | 263.7 | 177 | 538.8 | 317.5
1339 | 1194 | 536.3 | 263.5 | 175.9 | 538.6 | 316.9
1340 | 1195 | 535.6 | 262.7 | 175.1 | 538.5 | 316.3
1341 | 1196 | 534.9 | 262.1 | 174.1 | 538 | 315.9
1342 | 1197 | 534.2 | 261.8 | 172.9 | 537.4 | 315.3
1343 | 1198 | 533.5 | 260.9 | 171.7 | 537 | 314.8
1344 | 1199 | 532.6 | 260.2 | 170.9 | 536.7 | 314.3
1345 | 1200 | 531.8 | 258.9 | 169.7 | 535.8 | 313.8
1346 | 1201 | 531.1 | 258.3 | 168.9 | 536 | 313.5
1347 | 1202 | 530.3 | 257.8 | 168 | 535.8 | 312.8
1348 | 1203 | 529.6 | 257.2 | 167.2 | 534.9 | 312.2
1349 | 1204 | 528.9 | 256.4 | 166.7 | 534.6 | 311.4
1350 | 1205 | 528.2 | 255.7 | 165.8 | 534.3 | 310.8
1351 | 1206 | 527.5 | 255.2 | 164.7 | 534.3 | 310.5
1352 | 1207 | 526.8 | 254.8 | 163.7 | 534.3 | 310
1353 | 1208 | 526.1 | 254.2 | 162.8 | 533.9 | 309.4
1354 | 1209 | 525.4 | 253.9 | 162 | 533.3 | 308.8
1355 | 1210 | 524.8 | 253.4 | 161.3 | 532.6 | 308.4
1356 | 1211 | 524.2 | 253.4 | 160.6 | 531.5 | 307.7
1357 | 1212 | 523.5 | 253.5 | 159.9 | 531.8 | 307
1358 | 1213 | 522.9 | 253.1 | 159.1 | 531.9 | 306.7
1359 | 1214 | 522.3 | 251.9 | 158.4 | 531 | 306.4
1360 | 1215 | 521.8 | 251.7 | 157.6 | 529.5 | 305.9
1361 | 1216 | 521.3 | 251.1 | 156.7 | 529.1 | 305.3
1362 | 1217 | 520.7 | 250.1 | 155.8 | 530.5 | 305
1363 | 1218 | 520.1 | 250 | 154.8 | 531 | 304.5
1364 | 1219 | 519.5 | 249.8 | 154 | 531 | 304.3
1365 | 1220 | 518.8 | 249.2 | 153.1 | 530.8 | 304.1
1366 | 1221 | 517.9 | 248.6 | 152.4 | 530.3 | 303.4
1367 | 1222 | 517.1 | 248.4 | 151.8 | 529.6 | 303
1368 | 1223 | 516.3 | 248 | 151.1 | 529 | 302.6
1369 | 1224 | 515.7 | 248.2 | 150.4 | 528.2 | 302.1
1370 | 1225 | 514.9 | 247.9 | 150.2 | 526.7 | 301.8
1371 | 1226 | 514.2 | 247.2 | 149.6 | 524.6 | 301.2
1372 | 1227 | 513.6 | 247.4 | 149.2 | 526.1 | 300.3
1373 | 1228 | 513.1 | 247.4 | 148.4 | 525.1 | 299.9
1374 | 1229 | 512.4 | 246.8 | 148.1 | 523.6 | 299.5
1375 | 1230 | 511.7 | 246.3 | 147.5 | 522.5 | 299.1
1376 | 1231 | 511.1 | 245.6 | 146.6 | 520.8 | 298.8
1377 | 1232 | 510.4 | 244.6 | 145.9 | 521.7 | 298.3
1378 | 1233 | 509.5 | 243.9 | 145.7 | 521.7 | 297.6
1379 | 1234 | 508.6 | 242.9 | 145.2 | 520.8 | 297.3
1380 | 1235 | 507.7 | 242.6 | 144.6 | 521.2 | 296.5
1381 | 1236 | 506.7 | 241.9 | 144.2 | 521.5 | 296.1
1382 | 1237 | 505.8 | 241.5 | 144 | 521.5 | 295.8
1383 | 1238 | 504.9 | 241.5 | 143.7 | 521.6 | 294.8
1384 | 1239 | 504 | 241.5 | 143.3 | 521.6 | 294.2
1385 | 1240 | 503 | 241.2 | 142.8 | 521.3 | 293.8
1386 | 1241 | 502.2 | 240.7 | 142.6 | 520.5 | 293.6
1387 | 1242 | 501.5 | 240.3 | 142.3 | 520 | 293.1
1388 | 1243 | 500.9 | 239.7 | 141.8 | 519 | 292.7
1389 | 1244 | 500.4 | 239.8 | 141.8 | 519.3 | 292.2
1390 | 1245 | 499.9 | 239.9 | 141.5 | 518.3 | 292
1391 | 1246 | 499.4 | 240.2 | 141.1 | 516.2 | 291.6
1392 | 1247 | 498.8 | 240.4 | 140.9 | 514.7 | 290.7
1393 | 1248 | 498.3 | 240 | 140.4 | 514.8 | 290.4
1394 | 1249 | 497.9 | 238.7 | 140.1 | 514.3 | 289.9
1395 | 1250 | 497.5 | 237.6 | 140 | 514.3 | 289.5
1396 | 1251 | 497.1 | 237.5 | 140.1 | 513.3 | 289.1
1397 | 1252 | 496.6 | 236.7 | 139.9 | 512.2 | 289
1398 | 1253 | 496.1 | 236.5 | 139.6 | 511.3 | 288.6
1399 | 1254 | 495.6 | 236 | 139.4 | 512.3 | 288.2
1400 | 1255 | 495.1 | 234.9 | 139.2 | 512.1 | 288.1
1401 | 1256 | 494.4 | 234.1 | 138.6 | 511.8 | 287.4
1402 | 1257 | 493.6 | 233.5 | 137.9 | 511.5 | 287.1
1403 | 1258 | 492.9 | 233.1 | 137.4 | 511.4 | 286.9
1404 | 1259 | 492.2 | 232.9 | 137.1 | 511.1 | 286.7
1405 | 1260 | 491.5 | 232.2 | 136.9 | 510.8 | 286.1
1406 | 1261 | 490.8 | 231.7 | 136.8 | 510.3 | 285.9
1407 | 1262 | 490.1 | 231.4 | 136.2 | 509.5 | 285.6
1408 | 1263 | 489.5 | 231.3 | 135.9 | 508.9 | 285.2
1409 | 1264 | 488.9 | 231.1 | 136.4 | 508.6 | 284.8
1410 | 1265 | 488.4 | 230.7 | 136.4 | 507.6 | 284.4
1411 | 1266 | 487.9 | 230 | 136 | 506.6 | 283.7
1412 | 1267 | 487.5 | 229 | 135.5 | 505.7 | 283.3
1413 | 1268 | 487.1 | 229.4 | 135.1 | 504.8 | 282.8
1414 | 1269 | 486.6 | 229.2 | 134.5 | 504.5 | 282.6
1415 | 1270 | 486.1 | 229.1 | 134.5 | 505 | 281.9
1416 | 1271 | 485.4 | 228.6 | 134 | 504.8 | 281.4
1417 | 1272 | 484.7 | 227.9 | 133.8 | 504.9 | 281.2
1418 | 1273 | 484 | 227 | 133.1 | 504 | 280.9
1419 | 1274 | 483.3 | 226.6 | 132.5 | 503.5 | 280.3
1420 | 1275 | 482.6 | 226.6 | 131.9 | 502.8 | 279.8
1421 | 1276 | 481.8 | 226.1 | 131.6 | 502.2 | 279.4
1422 | 1277 | 481.1 | 225.5 | 131.7 | 501.5 | 278.6
1423 | 1278 | 480.2 | 224.6 | 131.4 | 500.9 | 278.2
1424 | 1279 | 479.5 | 223.8 | 131 | 500.4 | 278
1425 | 1280 | 478.7 | 223.6 | 130.7 | 500 | 277.6
1426 | 1281 | 478 | 223.1 | 130.4 | 500 | 277.2
1427 | 1282 | 477.2 | 222.3 | 130.1 | 499.6 | 276.7
1428 | 1283 | 476.6 | 221.7 | 129.9 | 499.1 | 276.4
1429 | 1284 | 475.9 | 221.7 | 129.5 | 498.4 | 275.9
1430 | 1285 | 475.2 | 221.8 | 128.9 | 498.1 | 275.5
1431 | 1286 | 474.4 | 221.4 | 128.7 | 497.3 | 275
1432 | 1287 | 473.7 | 220.7 | 128.5 | 496.8 | 274.7
1433 | 1288 | 472.9 | 220.1 | 127.8 | 496.1 | 274.3
1434 | 1289 | 472.2 | 219.4 | 127.4 | 495.6 | 274.1
1435 | 1290 | 471.4 | 218.9 | 126.8 | 494.9 | 273.8
1436 | 1291 | 470.4 | 218.5 | 126.5 | 493.8 | 273.3
1437 | 1292 | 469.5 | 217.9 | 126 | 493.1 | 273
1438 | 1293 | 468.7 | 217.5 | 125.6 | 492.4 | 272.5
1439 | 1294 | 467.8 | 217.3 | 124.9 | 491.7 | 272.3
1440 | 1295 | 467.1 | 217.1 | 124.8 | 491.4 | 271.9
1441 | 1296 | 466.4 | 217.1 | 125.4 | 490.6 | 271.5
1442 | 1297 | 465.7 | 217 | 125.4 | 490.1 | 271.1
1443 | 1298 | 465 | 216.4 | 124.9 | 489 | 270.8
1444 | 1299 | 464.4 | 215.7 | 124.5 | 487.5 | 270.4
1445 | 1300 | 463.7 | 215.1 | 124.3 | 486.9 | 269.8
1446 | 1301 | 463 | 215.3 | 124.1 | 486.6 | 269.3
1447 | 1302 | 462.3 | 215.1 | 123.7 | 486 | 269.2
1448 | 1303 | 461.7 | 214.5 | 123.2 | 485.2 | 268.8
1449 | 1304 | 461 | 214.1 | 123.2 | 484.3 | 268.2
1450 | 1305 | 460.3 | 214 | 122.7 | 483.5 | 267.9
1451 | 1306 | 459.7 | 213.5 | 122.1 | 482.8 | 267.4
1452 | 1307 | 459.1 | 213.1 | 121.5 | 482 | 267
1453 | 1308 | 458.6 | 212.4 | 120.8 | 481.3 | 266.7
1454 | 1309 | 458.1 | 212.3 | 120.7 | 480.8 | 266.3
1455 | 1310 | 457.5 | 211.9 | 120.3 | 480.2 | 265.7
1456 | 1311 | 457.1 | 211.9 | 119.9 | 479.9 | 265.2
1457 | 1312 | 456.6 | 211.5 | 120.1 | 479.2 | 265
1458 | 1313 | 456.1 | 211.3 | 119.8 | 478.9 | 264.8
1459 | 1314 | 455.6 | 210.7 | 119.2 | 478.4 | 264.2
1460 | 1315 | 455 | 210.7 | 118.9 | 477.8 | 263.7
1461 | 1316 | 454.4 | 210.8 | 118.7 | 477 | 263.3
1462 | 1317 | 453.7 | 210.6 | 118.5 | 476.2 | 263.3
1463 | 1318 | 453.1 | 210.1 | 118.4 | 475.6 | 262.8
1464 | 1319 | 452.5 | 209.6 | 118.3 | 474.8 | 262.6
1465 | 1320 | 451.8 | 209.3 | 118.1 | 473.7 | 261.8
1466 | 1321 | 451 | 208.7 | 118.1 | 472.5 | 261.2
1467 | 1322 | 450.2 | 208.4 | 117.8 | 471.3 | 260.9
1468 | 1323 | 449.4 | 207.9 | 117.6 | 470.8 | 260.4
1469 | 1324 | 448.6 | 207.5 | 117.3 | 470.1 | 260.3
1470 | 1325 | 448 | 207.3 | 117.1 | 469.5 | 259.9
1471 | 1326 | 447.3 | 207 | 116.8 | 469 | 259.5
1472 | 1327 | 446.6 | 206.5 | 116.7 | 468.3 | 258.9
1473 | 1328 | 445.9 | 205.8 | 116.8 | 467.7 | 258.3
1474 | 1329 | 445.3 | 205.5 | 116.7 | 467.2 | 257.8
1475 | 1330 | 444.6 | 205.2 | 116.5 | 466.6 | 257.4
1476 | 1331 | 444 | 205.2 | 116.3 | 465.7 | 256.8
1477 | 1332 | 443.5 | 204.7 | 116 | 465.5 | 256.3
1478 | 1333 | 442.8 | 204.2 | 115.9 | 465.4 | 255.9
1479 | 1334 | 442.2 | 204.2 | 115.9 | 465 | 255.5
1480 | 1335 | 441.6 | 204 | 116 | 464.6 | 255.2
1481 | 1336 | 441 | 203.6 | 116.1 | 464.3 | 254.7
1482 | 1337 | 440.4 | 203.4 | 115.4 | 463.8 | 254.7
1483 | 1338 | 439.8 | 203.1 | 115 | 463.2 | 254.1
1484 | 1339 | 439.2 | 203.2 | 115.1 | 462.7 | 253.6
1485 | 1340 | 438.6 | 202.8 | 115.2 | 462.3 | 253.4
1486 | 1341 | 437.9 | 202.3 | 115.3 | 461.8 | 252.9
1487 | 1342 | 437.3 | 201.8 | 115 | 461.3 | 252.5
1488 | 1343 | 436.7 | 201.6 | 114.9 | 460.8 | 252.1
1489 | 1344 | 436.1 | 201.3 | 114.4 | 459.6 | 251.8
1490 | 1345 | 435.5 | 201 | 113.8 | 458.3 | 251.2
1491 | 1346 | 435 | 200.5 | 113.3 | 458 | 250.7
1492 | 1347 | 434.4 | 200.1 | 113.1 | 457.7 | 250.4
1493 | 1348 | 433.8 | 199.5 | 112.8 | 457.6 | 250.1
1494 | 1349 | 433.1 | 199.1 | 112.8 | 457.6 | 249.7
1495 | 1350 | 432.2 | 198.3 | 112.6 | 457.6 | 249.6
1496 | 1351 | 431.4 | 197.7 | 112.9 | 457.3 | 248.9
1497 | 1352 | 430.7 | 197.3 | 112.7 | 456.8 | 248.6
1498 | 1353 | 430 | 197 | 112.5 | 456.4 | 248.2
1499 | 1354 | 429.3 | 197.1 | 112.3 | 456 | 248
1500 | 1355 | 428.7 | 197.1 | 111.9 | 454.9 | 247.7
1501 | 1356 | 428.2 | 196.3 | 111.9 | 454.4 | 247
1502 | 1357 | 427.5 | 195.7 | 111.7 | 453.6 | 246.7
1503 | 1358 | 427 | 195.2 | 111.5 | 452.8 | 246.4
1504 | 1359 | 426.4 | 194.7 | 111.5 | 452.3 | 245.8
1505 | 1360 | 426 | 194.2 | 111.5 | 451.6 | 245.4
1506 | 1361 | 425.6 | 193 | 111.3 | 451.4 | 244.9
1507 | 1362 | 425 | 192.7 | 111.1 | 450.8 | 244.4
1508 | 1363 | 424.4 | 192.7 | 111.3 | 450 | 244.2
1509 | 1364 | 423.8 | 192.7 | 111 | 449.1 | 244.1
1510 | 1365 | 423.1 | 192.5 | 110.8 | 448.6 | 243.5
1511 | 1366 | 422.5 | 192.2 | 110.6 | 447.9 | 243.1
1512 | 1367 | 421.9 | 192.1 | 110.2 | 447.8 | 242.7
1513 | 1368 | 421.2 | 191.7 | 110 | 447.3 | 242.3
1514 | 1369 | 420.3 | 191.3 | 109.6 | 446.7 | 242
1515 | 1370 | 419.4 | 190.9 | 109.2 | 446.1 | 241.7
1516 | 1371 | 418.6 | 190.3 | 109 | 445.3 | 241.1
1517 | 1372 | 417.7 | 189.9 | 108.9 | 444.6 | 240.6
1518 | 1373 | 416.9 | 189.7 | 108.7 | 444.4 | 240.1
1519 | 1374 | 416.1 | 189.4 | 108.5 | 444.2 | 239.9
1520 | 1375 | 415.3 | 188.8 | 108.1 | 443.7 | 239.8
1521 | 1376 | 414.6 | 188.4 | 107.8 | 443.4 | 239.3
1522 | 1377 | 413.9 | 188.5 | 107.8 | 442.9 | 238.7
1523 | 1378 | 413.2 | 188.7 | 107.6 | 442.9 | 238.4
1524 | 1379 | 412.5 | 188.1 | 107.8 | 442.7 | 238.2
1525 | 1380 | 411.6 | 187.9 | 107.9 | 441.9 | 237.6
1526 | 1381 | 410.7 | 187.3 | 107.1 | 441 | 237.1
1527 | 1382 | 409.8 | 187.1 | 106.8 | 440.1 | 237.1
1528 | 1383 | 409 | 186.6 | 106.5 | 439.9 | 236.5
1529 | 1384 | 408.2 | 186.3 | 106.3 | 439.5 | 236.4
1530 | 1385 | 407.6 | 186.3 | 106.1 | 438.9 | 236.1
1531 | 1386 | 407 | 185.8 | 105.9 | 438.3 | 235.6
1532 | 1387 | 406.3 | 185.5 | 105.6 | 437.6 | 235
1533 | 1388 | 405.6 | 185.5 | 105.4 | 437.1 | 234.7
1534 | 1389 | 404.9 | 185 | 105.3 | 436.6 | 234.4
1535 | 1390 | 404.2 | 184.5 | 105.1 | 436.4 | 234
1536 | 1391 | 403.5 | 184.3 | 104.9 | 436 | 233.4
1537 | 1392 | 402.7 | 184.1 | 104.9 | 435.3 | 233.1
1538 | 1393 | 401.9 | 183.8 | 104.9 | 434.9 | 232.7
1539 | 1394 | 401.1 | 183.3 | 104.7 | 434.3 | 232.3
1540 | 1395 | 400.4 | 182.9 | 104.3 | 433.5 | 232.1
1541 | 1396 | 399.6 | 182.8 | 103.9 | 433 | 231.8
1542 | 1397 | 398.8 | 182.4 | 103.7 | 432.5 | 231.3
1543 | 1398 | 398.1 | 182.3 | 103.3 | 432.1 | 231
1544 | 1399 | 397.4 | 181.9 | 103 | 431.7 | 230.6
1545 | 1400 | 396.7 | 181.5 | 103 | 431.3 | 230.3
1546 | 1401 | 395.9 | 181.2 | 103 | 431 | 229.9
1547 | 1402 | 395.2 | 181 | 103.1 | 430.9 | 229.6
1548 | 1403 | 394.5 | 181.2 | 103.1 | 430.7 | 229.2
1549 | 1404 | 393.7 | 181.2 | 103.4 | 430.4 | 228.8
1550 | 1405 | 393.1 | 180.9 | 103.3 | 430.1 | 228.4
1551 | 1406 | 392.5 | 180.8 | 102.8 | 429.7 | 228.1
1552 | 1407 | 391.9 | 181 | 102.1 | 429.2 | 227.8
1553 | 1408 | 391.4 | 181.1 | 101.8 | 428.7 | 227.6
1554 | 1409 | 390.9 | 181.1 | 101.6 | 428.2 | 227.3
1555 | 1410 | 390.3 | 181.1 | 101.3 | 428 | 227
1556 | 1411 | 389.7 | 181.1 | 101.2 | 427.3 | 226.7
1557 | 1412 | 389.1 | 180.9 | 101.1 | 426.8 | 226.3
1558 | 1413 | 388.3 | 180.2 | 100.9 | 426.4 | 226.1
1559 | 1414 | 387.6 | 180 | 100.7 | 426 | 225.6
1560 | 1415 | 387.1 | 179.6 | 100.1 | 425.3 | 225.5
1561 | 1416 | 386.5 | 179.7 | 100 | 424.9 | 225.4
1562 | 1417 | 385.9 | 179.1 | 99.5 | 424.2 | 224.9
1563 | 1418 | 385.4 | 178.7 | 99.3 | 423.3 | 224.4
1564 | 1419 | 384.8 | 178.6 | 99.3 | 422.7 | 224.2
1565 | 1420 | 384.1 | 178.3 | 99.1 | 422.2 | 224.1
1566 | 1421 | 383.6 | 178.4 | 99.2 | 421.6 | 223.8
1567 | 1422 | 383.1 | 178.7 | 98.9 | 421.5 | 223.3
1568 | 1423 | 382.6 | 178.6 | 98.9 | 421.1 | 223
1569 | 1424 | 382.1 | 178.2 | 98.7 | 420.2 | 222.8
1570 | 1425 | 381.5 | 177.6 | 98.6 | 419.7 | 222.6
1571 | 1426 | 380.9 | 177.2 | 98.7 | 419.2 | 222.1
1572 | 1427 | 380.2 | 177.1 | 98.6 | 418.6 | 221.8
1573 | 1428 | 379.6 | 177.3 | 98.3 | 418.2 | 221.5
1574 | 1429 | 379 | 176.7 | 98.2 | 417.9 | 221.1
1575 | 1430 | 378.4 | 176.6 | 98.1 | 417.8 | 220.6
1576 | 1431 | 377.6 | 176.5 | 98 | 417.7 | 220.2
1577 | 1432 | 376.9 | 176 | 98 | 417.3 | 219.9
1578 | 1433 | 376.1 | 175.5 | 97.7 | 416.7 | 219.6
1579 | 1434 | 375.2 | 174.6 | 97.4 | 416.1 | 219.4
1580 | 1435 | 374.3 | 173.9 | 97.1 | 415.8 | 219.1
1581 | 1436 | 373.6 | 173.4 | 96.7 | 415.1 | 218.8
1582 | 1437 | 372.8 | 173.5 | 96.6 | 414.7 | 218.6
1583 | 1438 | 372.1 | 173.9 | 96.6 | 414.6 | 218.2
1584 | 1439 | 371.3 | 174.2 | 96.4 | 414.5 | 217.8
1585 | 1440 | 370.5 | 174.2 | 96.2 | 414.2 | 217.5
1586 | 1441 | 369.7 | 173.8 | 96.1 | 413.4 | 217.1
1587 | 1442 | 368.9 | 173.6 | 95.8 | 412.9 | 216.7
1588 | 1443 | 368.2 | 173.7 | 95.7 | 412.4 | 216.4
1589 | 1444 | 367.5 | 173.5 | 95.5 | 412 | 216.1
1590 | 1445 | 366.8 | 173.1 | 95.3 | 411.7 | 216
1591 | 1446 | 366.1 | 172.9 | 95.1 | 411 | 215.7
1592 | 1447 | 365.5 | 172.5 | 94.9 | 410.3 | 215.4
1593 | 1448 | 365 | 172 | 94.7 | 409.6 | 215
1594 | 1449 | 364.4 | 171.9 | 94.7 | 409 | 214.6
1595 | 1450 | 363.6 | 171.8 | 94.6 | 408.6 | 214.2
1596 | 1451 | 363 | 171.3 | 94.5 | 408.2 | 213.9
1597 | 1452 | 362.1 | 170.7 | 94.5 | 408.1 | 213.7
1598 | 1453 | 361.3 | 170.5 | 94.5 | 407.9 | 213.1
1599 | 1454 | 360.7 | 170.3 | 94.2 | 407.8 | 212.7
1600 | 1455 | 360.1 | 171.4 | 94.1 | 407.4 | 212.4
1601 | 1456 | 359.5 | 172 | 94 | 407.2 | 212.2
1602 | 1457 | 358.8 | 172 | 93.8 | 406.6 | 211.7
1603 | 1458 | 358.2 | 171.4 | 93.5 | 406.4 | 211.5
1604 | 1459 | 357.7 | 171 | 93.2 | 406.2 | 211.3
1605 | 1460 | 357.1 | 170.8 | 93.1 | 406.1 | 211
1606 | 1461 | 356.4 | 171 | 93.1 | 406 | 210.8
1607 | 1462 | 355.8 | 170.9 | 93.1 | 405.6 | 210.5
1608 | 1463 | 355.2 | 170.6 | 92.8 | 405.2 | 210.1
1609 | 1464 | 354.6 | 169.8 | 92.7 | 404.9 | 210
1610 | 1465 | 354 | 169.4 | 92.7 | 404.6 | 209.6
1611 | 1466 | 353.3 | 168.7 | 92.6 | 404.4 | 209.3
1612 | 1467 | 352.7 | 168.4 | 92.5 | 403.7 | 209
1613 | 1468 | 352.1 | 168.3 | 92.2 | 403.1 | 208.7
1614 | 1469 | 351.4 | 167.7 | 92 | 402.5 | 208.4
1615 | 1470 | 350.8 | 167.2 | 91.8 | 402.2 | 208.1
1616 | 1471 | 350.1 | 166.6 | 91.7 | 401.5 | 207.9
1617 | 1472 | 349.4 | 166.2 | 91.7 | 400.7 | 207.3
1618 | 1473 | 348.7 | 166 | 91.7 | 400.3 | 207
1619 | 1474 | 348 | 165.7 | 91.5 | 399.4 | 206.8
1620 | 1475 | 347.4 | 165.5 | 91.1 | 398.8 | 206.4
1621 | 1476 | 346.8 | 165.3 | 90.8 | 398.6 | 206.1
1622 | 1477 | 346 | 165 | 90.9 | 398.6 | 205.8
1623 | 1478 | 345.3 | 164.9 | 91 | 398.5 | 205.5
1624 | 1479 | 344.5 | 164.9 | 91 | 398.4 | 205.2
1625 | 1480 | 343.7 | 164.5 | 91 | 398.5 | 204.8
1626 | 1481 | 343 | 164.1 | 90.7 | 398.1 | 204.7
1627 | 1482 | 342.2 | 164.2 | 90.6 | 397.7 | 204.4
1628 | 1483 | 341.5 | 163.6 | 90.3 | 397.3 | 204.1
1629 | 1484 | 340.6 | 163.3 | 90.3 | 396.7 | 203.8
1630 | 1485 | 339.9 | 163 | 89.9 | 396.4 | 203.5
1631 | 1486 | 339.3 | 163 | 89.6 | 395.8 | 203.1
1632 | 1487 | 338.7 | 162.7 | 89.5 | 395.3 | 202.9
1633 | 1488 | 338.1 | 162.4 | 89.2 | 394.5 | 202.7
1634 | 1489 | 337.5 | 162.1 | 89.3 | 394.4 | 202.3
1635 | 1490 | 337 | 161.6 | 89.2 | 393.9 | 202.2
1636 | 1491 | 336.5 | 161.7 | 89.2 | 393.6 | 201.9
1637 | 1492 | 335.9 | 161.5 | 89.1 | 393.6 | 201.6
1638 | 1493 | 335.3 | 161.1 | 89.2 | 393.5 | 201.3
1639 | 1494 | 334.5 | 160.5 | 89.3 | 393.2 | 201
1640 | 1495 | 333.8 | 160.1 | 89.4 | 393.1 | 200.7
1641 | 1496 | 333 | 160 | 89.8 | 393 | 200.6
1642 | 1497 | 332.4 | 160 | 89.7 | 392.7 | 200.4
1643 | 1498 | 331.7 | 160 | 89.3 | 392.3 | 199.9
1644 | 1499 | 331.1 | 159.8 | 89.2 | 392.3 | 199.6
1645 | 1500 | 330.6 | 160 | 89.1 | 392.2 | 199.3
1646 | 1501 | 330.1 | 159.6 | 88.8 | 391.9 | 198.9
1647 | 1502 | 329.5 | 159.5 | 88.5 | 391.6 | 198.8
1648 | 1503 | 329 | 159.4 | 88.2 | 391.2 | 198.6
1649 | 1504 | 328.4 | 159.5 | 88 | 390.8 | 198.2
1650 | 1505 | 327.9 | 159.4 | 87.6 | 390.2 | 197.7
1651 | 1506 | 327.4 | 159.1 | 87.4 | 389.4 | 197.5
1652 | 1507 | 326.8 | 158.8 | 87.2 | 388.8 | 197.4
1653 | 1508 | 326.3 | 158.6 | 87.1 | 388.2 | 197.2
1654 | 1509 | 325.7 | 158.5 | 87 | 387.7 | 197.1
1655 | 1510 | 325.1 | 158.6 | 86.8 | 387.7 | 196.8
1656 | 1511 | 324.6 | 158.9 | 86.6 | 387.1 | 196.5
1657 | 1512 | 324 | 158.6 | 86.3 | 386.6 | 196.3
1658 | 1513 | 323.5 | 158.4 | 86 | 386.2 | 196.1
1659 | 1514 | 322.9 | 158.3 | 85.9 | 385.8 | 196
1660 | 1515 | 322.2 | 158.1 | 85.6 | 385.5 | 195.6
1661 | 1516 | 321.7 | 158.1 | 85.1 | 385.3 | 195.6
1662 | 1517 | 321.1 | 158.3 | 84.9 | 385.3 | 195.5
1663 | 1518 | 320.6 | 158 | 84.8 | 385.3 | 195.5
1664 | 1519 | 319.9 | 157.4 | 85 | 385.1 | 195.3
1665 | 1520 | 319.4 | 157 | 84.9 | 384.9 | 195.2
1666 | 1521 | 318.7 | 156.9 | 84.4 | 384.4 | 195.1
1667 | 1522 | 318.1 | 156.8 | 84.3 | 383.6 | 194.9
1668 | 1523 | 317.6 | 156.8 | 84.2 | 383.1 | 194.8
1669 | 1524 | 317.2 | 156.5 | 84.1 | 382.3 | 194.7
1670 | 1525 | 316.8 | 156 | 83.9 | 381.6 | 194.4
1671 | 1526 | 316.3 | 155.5 | 83.8 | 381 | 193.9
1672 | 1527 | 315.8 | 155.3 | 83.6 | 380.4 | 193.7
1673 | 1528 | 315.4 | 155.1 | 83.5 | 379.5 | 193.5
1674 | 1529 | 314.8 | 154.9 | 83.3 | 378.9 | 193
1675 | 1530 | 314.3 | 154.5 | 83.3 | 378.3 | 192.6
1676 | 1531 | 313.8 | 154.3 | 83.5 | 378 | 192.5
1677 | 1532 | 313.4 | 154.3 | 83.4 | 377.7 | 192.2
1678 | 1533 | 313 | 154.4 | 83.1 | 377.4 | 192
1679 | 1534 | 312.6 | 154.4 | 82.9 | 377.3 | 191.6
1680 | 1535 | 312.2 | 154 | 82.6 | 377.1 | 191.4
1681 | 1536 | 311.9 | 153.5 | 82.3 | 376.8 | 191
1682 | 1537 | 311.5 | 153.4 | 82.3 | 376.4 | 190.8
1683 | 1538 | 311.1 | 153.2 | 82.2 | 375.7 | 190.5
1684 | 1539 | 310.6 | 153 | 82.2 | 375.1 | 190.5
1685 | 1540 | 310.1 | 153 | 82 | 374.7 | 190.1
1686 | 1541 | 309.7 | 153 | 81.8 | 374.4 | 189.7
1687 | 1542 | 309.3 | 152.8 | 81.7 | 374.1 | 189.2
1688 | 1543 | 308.9 | 152.6 | 81.7 | 373.4 | 189
1689 | 1544 | 308.5 | 152.3 | 81.6 | 372.8 | 188.9
1690 | 1545 | 308.1 | 152.1 | 81.5 | 372.7 | 188.6
1691 | 1546 | 307.7 | 152 | 81.4 | 372.2 | 188.4
1692 | 1547 | 307.3 | 151.9 | 81.2 | 372 | 188.1
1693 | 1548 | 307 | 151.6 | 81 | 371.7 | 187.9
1694 | 1549 | 306.6 | 151.2 | 80.8 | 371.3 | 187.6
1695 | 1550 | 306.3 | 151.1 | 80.7 | 370.7 | 187.5
1696 | 1551 | 306 | 151.1 | 80.6 | 370.2 | 187.3
1697 | 1552 | 305.6 | 151.4 | 80.5 | 370 | 187
1698 | 1553 | 305.3 | 151 | 80.4 | 369.8 | 186.7
1699 | 1554 | 305 | 150.6 | 80.3 | 369.3 | 186.3
1700 | 1555 | 304.7 | 150.7 | 80.3 | 368.9 | 186.1
1701 | 1556 | 304.3 | 150.5 | 80.2 | 368.5 | 185.8
1702 | 1557 | 303.8 | 150.3 | 80.3 | 368.3 | 185.6
1703 | 1558 | 303.4 | 150.1 | 80.1 | 368 | 185.3
1704 | 1559 | 302.9 | 150.1 | 80 | 367.6 | 185.1
1705 | 1560 | 302.5 | 149.8 | 79.8 | 367.5 | 185
1706 | 1561 | 302.2 | 149.5 | 79.8 | 367.4 | 184.6
1707 | 1562 | 301.8 | 149.4 | 79.6 | 366.7 | 184.3
1708 | 1563 | 301.4 | 149.2 | 79.4 | 366.3 | 184
1709 | 1564 | 300.9 | 148.8 | 79.4 | 366.1 | 184
1710 | 1565 | 300.5 | 148.4 | 79.2 | 365.9 | 183.7
1711 | 1566 | 300.2 | 148.1 | 79.2 | 365.5 | 183.4
1712 | 1567 | 299.7 | 148.1 | 79.4 | 365.1 | 183.3
1713 | 1568 | 299.3 | 148 | 79.5 | 364.7 | 183.1
1714 | 1569 | 298.9 | 147.9 | 79.3 | 364.5 | 182.9
1715 | 1570 | 298.5 | 147.5 | 79.1 | 364.3 | 182.7
1716 | 1571 | 298.2 | 147.1 | 79.1 | 364 | 182.2
1717 | 1572 | 297.9 | 146.7 | 78.6 | 363.8 | 182
1718 | 1573 | 297.5 | 146.6 | 78.5 | 363.6 | 181.7
1719 | 1574 | 297.3 | 146.6 | 78.3 | 363.4 | 181.5
1720 | 1575 | 297 | 146.6 | 77.9 | 363.1 | 181.3
1721 | 1576 | 296.7 | 146.2 | 77.7 | 362.2 | 181.2
1722 | 1577 | 296.4 | 145.8 | 77.6 | 361.8 | 180.9
1723 | 1578 | 296.1 | 145.5 | 77.4 | 361.1 | 180.5
1724 | 1579 | 295.8 | 145.4 | 77.6 | 360.7 | 180.3
1725 | 1580 | 295.5 | 145.2 | 77.5 | 360.2 | 180.1
1726 | 1581 | 295.2 | 144.8 | 77.4 | 359.6 | 179.7
1727 | 1582 | 294.8 | 144.2 | 77.2 | 359 | 179.5
1728 | 1583 | 294.4 | 143.8 | 77.2 | 358.6 | 179.4
1729 | 1584 | 294 | 143.6 | 77 | 358.1 | 179.1
1730 | 1585 | 293.6 | 143.7 | 76.7 | 357.8 | 178.7
1731 | 1586 | 293.1 | 143.2 | 76.6 | 357.4 | 178.5
1732 | 1587 | 292.6 | 142.8 | 76.6 | 356.9 | 178.3
1733 | 1588 | 292.1 | 142.5 | 76.5 | 356.4 | 177.9
1734 | 1589 | 291.7 | 142.3 | 76.3 | 356.1 | 177.5
1735 | 1590 | 291.3 | 142 | 76.4 | 355.8 | 177.4
1736 | 1591 | 290.8 | 141.9 | 76.5 | 355.5 | 177.1
1737 | 1592 | 290.3 | 142 | 76.1 | 355.2 | 176.7
1738 | 1593 | 290 | 142 | 76.2 | 354.8 | 176.5
1739 | 1594 | 289.6 | 141.9 | 76.3 | 354.7 | 176.4
1740 | 1595 | 289.2 | 141.7 | 76.3 | 354.4 | 176.3
1741 | 1596 | 288.8 | 141.6 | 76.1 | 353.9 | 176
1742 | 1597 | 288.4 | 141.6 | 76.1 | 353.7 | 175.8
1743 | 1598 | 288 | 141.3 | 76 | 353.3 | 175.5
1744 | 1599 | 287.7 | 141.2 | 75.7 | 353 | 175.1
1745 | 1600 | 287.3 | 140.9 | 75.4 | 352.2 | 174.9
1746 | 1601 | 286.8 | 141 | 75.2 | 351.4 | 174.6
1747 | 1602 | 286.4 | 140.4 | 75 | 351.1 | 174.4
1748 | 1603 | 285.9 | 139.8 | 74.8 | 350.5 | 174.1
1749 | 1604 | 285.5 | 139.3 | 74.8 | 350.4 | 173.9
1750 | 1605 | 285.2 | 139.3 | 74.8 | 350.1 | 173.5
1751 | 1606 | 284.8 | 139.3 | 74.3 | 349.3 | 173.2
1752 | 1607 | 284.4 | 139.1 | 74 | 348.6 | 173
1753 | 1608 | 284 | 138.7 | 73.8 | 348.2 | 172.7
1754 | 1609 | 283.6 | 138.4 | 73.5 | 347.9 | 172.6
1755 | 1610 | 283.2 | 138.1 | 73.2 | 347.7 | 172.4
1756 | 1611 | 282.9 | 137.8 | 73.1 | 347.1 | 172.1
1757 | 1612 | 282.5 | 137.9 | 73 | 346.8 | 172.1
1758 | 1613 | 282 | 137.9 | 73.1 | 346.8 | 171.9
1759 | 1614 | 281.5 | 137.9 | 73.3 | 346.7 | 171.8
1760 | 1615 | 281 | 137.6 | 73.2 | 346.4 | 171.7
1761 | 1616 | 280.6 | 137.5 | 73 | 346 | 171.5
1762 | 1617 | 280.3 | 137.2 | 72.8 | 345.4 | 171.2
1763 | 1618 | 279.9 | 137.2 | 72.5 | 345.1 | 171.1
1764 | 1619 | 279.5 | 137.2 | 72.3 | 345 | 170.9
1765 | 1620 | 279.3 | 136.9 | 72.1 | 344.8 | 170.8
1766 | 1621 | 279 | 136.6 | 72.1 | 344.5 | 170.5
1767 | 1622 | 278.8 | 136.4 | 71.9 | 344.4 | 170.1
1768 | 1623 | 278.5 | 136.2 | 71.9 | 344.2 | 170.1
1769 | 1624 | 278.3 | 136.4 | 71.7 | 343.9 | 169.8
1770 | 1625 | 278 | 136 | 71.8 | 343.1 | 169.6
1771 | 1626 | 277.7 | 135.8 | 71.8 | 342.4 | 169.3
1772 | 1627 | 277.2 | 135.6 | 71.5 | 342.2 | 169.1
1773 | 1628 | 276.9 | 135.3 | 71.4 | 341.7 | 168.8
1774 | 1629 | 276.5 | 135.2 | 71.2 | 341.3 | 168.6
1775 | 1630 | 276.1 | 134.9 | 71.1 | 340.8 | 168.4
1776 | 1631 | 275.6 | 134.7 | 71.1 | 340.5 | 168.3
1777 | 1632 | 275 | 134.3 | 71 | 340.3 | 168.2
1778 | 1633 | 274.5 | 134.2 | 71 | 340 | 168.2
1779 | 1634 | 274 | 134.1 | 70.9 | 339.5 | 168
1780 | 1635 | 273.5 | 134 | 70.8 | 339.3 | 167.9
1781 | 1636 | 273.1 | 134.1 | 70.7 | 338.8 | 167.5
1782 | 1637 | 272.7 | 134 | 70.7 | 338.5 | 167.2
1783 | 1638 | 272.4 | 134.1 | 70.7 | 338.1 | 166.9
1784 | 1639 | 272.1 | 133.7 | 70.5 | 337.6 | 166.5
1785 | 1640 | 271.8 | 133.3 | 70.4 | 337.3 | 166.3
1786 | 1641 | 271.5 | 133.1 | 70.4 | 337.1 | 166.1
1787 | 1642 | 271.2 | 133.1 | 70.5 | 337 | 165.8
1788 | 1643 | 270.9 | 133.3 | 70.5 | 336.9 | 165.6
1789 | 1644 | 270.6 | 133.3 | 70.6 | 336.9 | 165.3
1790 | 1645 | 270.3 | 133.1 | 70.6 | 336.8 | 165.2
1791 | 1646 | 270 | 132.7 | 70.5 | 336.6 | 164.9
1792 | 1647 | 269.7 | 132.7 | 70.3 | 336.4 | 164.7
1793 | 1648 | 269.3 | 133 | 70 | 336.3 | 164.4
1794 | 1649 | 269 | 133.3 | 69.9 | 336.3 | 164.4
1795 | 1650 | 268.7 | 133.4 | 70 | 336.1 | 164.2
1796 | 1651 | 268.3 | 133.4 | 70 | 335.7 | 164.1
1797 | 1652 | 268 | 133.4 | 70 | 335.4 | 163.9
1798 | 1653 | 267.8 | 133 | 70.1 | 335.1 | 163.7
1799 | 1654 | 267.5 | 133 | 70 | 334.7 | 163.4
1800 | 1655 | 267.2 | 133.3 | 69.9 | 334.3 | 163.1
1801 | 1656 | 266.9 | 133.3 | 69.8 | 334 | 162.9
1802 | 1657 | 266.6 | 132.9 | 69.7 | 333.9 | 162.7
1803 | 1658 | 266.3 | 132.6 | 69.6 | 333.6 | 162.6
1804 | 1659 | 266 | 132.1 | 69.6 | 333.3 | 162.3
1805 | 1660 | 265.7 | 132.1 | 69.5 | 332.6 | 162
1806 | 1661 | 265.3 | 131.9 | 69.3 | 332.1 | 161.7
1807 | 1662 | 264.8 | 131.8 | 69.4 | 331.8 | 161.4
1808 | 1663 | 264.5 | 131.5 | 69.4 | 331.7 | 161.2
1809 | 1664 | 264.2 | 131.3 | 69.4 | 331.6 | 161.2
1810 | 1665 | 263.8 | 131 | 69 | 331.5 | 161.1
1811 | 1666 | 263.5 | 131.1 | 68.9 | 331.3 | 161
1812 | 1667 | 263.2 | 131.1 | 68.9 | 331.1 | 160.7
1813 | 1668 | 262.9 | 131.1 | 68.8 | 330.9 | 160.5
1814 | 1669 | 262.6 | 130.8 | 68.6 | 330.7 | 160.5
1815 | 1670 | 262.3 | 130.6 | 68.3 | 330.1 | 160.5
1816 | 1671 | 261.9 | 130.5 | 68.1 | 329.7 | 160.1
1817 | 1672 | 261.6 | 130.4 | 67.7 | 329.8 | 160
1818 | 1673 | 261.3 | 130.6 | 67.5 | 329.9 | 160.1
1819 | 1674 | 261 | 130.7 | 67.3 | 329.9 | 160
1820 | 1675 | 260.6 | 130.7 | 67.2 | 329.6 | 159.9
1821 | 1676 | 260.2 | 130.5 | 67.2 | 329.4 | 159.7
1822 | 1677 | 259.9 | 130.5 | 67.1 | 329 | 159.5
1823 | 1678 | 259.5 | 130.2 | 67.1 | 328.6 | 159.4
1824 | 1679 | 259.2 | 129.8 | 67 | 328.2 | 159.1
1825 | 1680 | 258.9 | 129.7 | 67 | 327.9 | 158.9
1826 | 1681 | 258.6 | 129.3 | 66.9 | 327.4 | 158.5
1827 | 1682 | 258.3 | 129.1 | 66.8 | 327.1 | 158.3
1828 | 1683 | 258 | 128.7 | 66.8 | 326.9 | 158.1
1829 | 1684 | 257.6 | 128.3 | 66.7 | 326.5 | 157.9
1830 | 1685 | 257.2 | 128.3 | 66.5 | 326.2 | 157.7
1831 | 1686 | 256.9 | 128.1 | 66.3 | 325.8 | 157.4
1832 | 1687 | 256.5 | 127.8 | 66.4 | 325.4 | 157.2
1833 | 1688 | 256.1 | 127.4 | 66.4 | 325 | 156.9
1834 | 1689 | 255.8 | 127 | 66.3 | 324.6 | 156.6
1835 | 1690 | 255.3 | 126.6 | 66.6 | 324.5 | 156.5
1836 | 1691 | 254.9 | 126.3 | 66.7 | 324.2 | 156.4
1837 | 1692 | 254.4 | 126.2 | 66.6 | 324 | 156.2
1838 | 1693 | 254 | 126.2 | 66.4 | 323.6 | 156
1839 | 1694 | 253.7 | 126 | 66.3 | 323.1 | 155.9
1840 | 1695 | 253.2 | 125.8 | 66.3 | 322.9 | 155.5
1841 | 1696 | 252.9 | 125.9 | 66.3 | 322.7 | 155.4
1842 | 1697 | 252.5 | 126 | 66.2 | 322.4 | 155.4
1843 | 1698 | 252.2 | 125.9 | 66.2 | 322.1 | 155.1
1844 | 1699 | 251.8 | 125.8 | 66.1 | 321.2 | 154.8
1845 | 1700 | 251.4 | 125.4 | 66.1 | 320.4 | 154.5
1846 | 1701 | 251.1 | 125.2 | 66.1 | 320.3 | 154.2
1847 | 1702 | 250.8 | 124.8 | 66.1 | 319.9 | 154.2
1848 | 1703 | 250.5 | 124.4 | 66.1 | 319.7 | 154
1849 | 1704 | 250.2 | 124.1 | 66 | 319.6 | 153.7
1850 | 1705 | 249.9 | 124 | 66 | 319.4 | 153.5
1851 | 1706 | 249.5 | 123.7 | 65.9 | 319.1 | 153.3
1852 | 1707 | 249.1 | 123.4 | 65.7 | 318.9 | 153.1
1853 | 1708 | 248.7 | 123.4 | 65.7 | 318.7 | 152.9
1854 | 1709 | 248.3 | 123.4 | 65.5 | 318.3 | 152.8
1855 | 1710 | 247.9 | 123.5 | 65.4 | 317.6 | 152.4
1856 | 1711 | 247.4 | 123.4 | 65.2 | 317.4 | 152.2
1857 | 1712 | 247.1 | 123.2 | 65.1 | 317.3 | 151.9
1858 | 1713 | 246.8 | 123.1 | 65 | 317.2 | 151.9
1859 | 1714 | 246.4 | 122.9 | 65 | 317 | 151.6
1860 | 1715 | 246.1 | 122.9 | 64.9 | 316.7 | 151.5
1861 | 1716 | 245.7 | 122.9 | 64.6 | 316.5 | 151.1
1862 | 1717 | 245.3 | 122.7 | 64.5 | 316.1 | 150.9
1863 | 1718 | 245 | 122.6 | 64.4 | 315.8 | 150.7
1864 | 1719 | 244.6 | 122.6 | 64.2 | 315.3 | 150.5
1865 | 1720 | 244.1 | 122.3 | 64.4 | 314.9 | 150.3
1866 | 1721 | 243.7 | 122.2 | 64.7 | 314.7 | 150.1
1867 | 1722 | 243.2 | 121.8 | 64.8 | 314.5 | 149.9
1868 | 1723 | 242.9 | 121.3 | 64.5 | 314.3 | 149.9
1869 | 1724 | 242.5 | 120.9 | 64.5 | 314.2 | 149.8
1870 | 1725 | 242 | 120.8 | 64.4 | 314.1 | 149.6
1871 | 1726 | 241.5 | 120.8 | 64.2 | 313.7 | 149.5
1872 | 1727 | 241.2 | 120.7 | 64 | 313.5 | 149.3
1873 | 1728 | 240.8 | 120.6 | 63.8 | 313.3 | 149.1
1874 | 1729 | 240.3 | 120.3 | 64 | 313.2 | 148.9
1875 | 1730 | 239.9 | 120 | 64.1 | 313 | 148.9
1876 | 1731 | 239.5 | 119.7 | 63.8 | 312.7 | 148.8
1877 | 1732 | 239.2 | 119.5 | 63.5 | 312.3 | 148.5
1878 | 1733 | 238.9 | 119.7 | 63.4 | 311.7 | 148.2
1879 | 1734 | 238.6 | 119.8 | 63.2 | 311.5 | 147.9
1880 | 1735 | 238.3 | 120.1 | 63 | 311 | 147.9
1881 | 1736 | 238 | 120 | 62.9 | 310.5 | 147.8
1882 | 1737 | 237.7 | 119.8 | 63 | 310.4 | 147.6
1883 | 1738 | 237.5 | 119.5 | 62.8 | 310.1 | 147.5
1884 | 1739 | 237.1 | 119.7 | 62.8 | 309.8 | 147.5
1885 | 1740 | 236.8 | 119.7 | 62.8 | 309.3 | 147.3
1886 | 1741 | 236.5 | 119.6 | 62.9 | 308.6 | 147
1887 | 1742 | 236.3 | 119.2 | 62.8 | 308.1 | 146.8
1888 | 1743 | 235.9 | 118.7 | 62.7 | 308.1 | 146.7
1889 | 1744 | 235.6 | 118.4 | 62.8 | 307.9 | 146.4
1890 | 1745 | 235.3 | 118.4 | 62.8 | 307.5 | 146.2
1891 | 1746 | 234.9 | 118.3 | 62.7 | 307.2 | 146.1
1892 | 1747 | 234.5 | 118 | 62.5 | 306.4 | 146
1893 | 1748 | 234.2 | 117.8 | 62.4 | 305.8 | 145.8
1894 | 1749 | 233.8 | 117.7 | 62.5 | 305.3 | 145.6
1895 | 1750 | 233.5 | 117.4 | 62.4 | 304.9 | 145.3
1896 | 1751 | 233.2 | 117.6 | 62.4 | 304.7 | 145.2
1897 | 1752 | 232.9 | 117.8 | 62.4 | 304.4 | 144.9
1898 | 1753 | 232.7 | 117.7 | 62.1 | 304 | 144.7
1899 | 1754 | 232.4 | 117.6 | 61.9 | 303.5 | 144.5
1900 | 1755 | 232.2 | 117.7 | 61.9 | 302.4 | 144.4
1901 | 1756 | 231.9 | 117.7 | 61.7 | 302.1 | 144.2
1902 | 1757 | 231.5 | 117.6 | 61.7 | 301.3 | 144.1
1903 | 1758 | 231.2 | 117.4 | 61.5 | 300.6 | 143.7
1904 | 1759 | 230.8 | 117.1 | 61.2 | 300.5 | 143.5
1905 | 1760 | 230.5 | 116.7 | 61.1 | 300.2 | 143.4
1906 | 1761 | 230.3 | 116.6 | 61 | 299.9 | 143.2
1907 | 1762 | 230 | 116.7 | 60.9 | 299.8 | 143
1908 | 1763 | 229.7 | 116.8 | 60.8 | 299.6 | 142.8
1909 | 1764 | 229.4 | 117 | 60.8 | 299.4 | 142.8
1910 | 1765 | 229.2 | 116.9 | 60.8 | 299.2 | 142.7
1911 | 1766 | 228.9 | 116.8 | 60.5 | 298.8 | 142.4
1912 | 1767 | 228.6 | 116.7 | 60.4 | 298.6 | 142.1
1913 | 1768 | 228.4 | 116.7 | 60.3 | 298.2 | 142
1914 | 1769 | 228.1 | 116.8 | 60.2 | 297.8 | 141.7
1915 | 1770 | 227.8 | 116.5 | 60 | 297.5 | 141.6
1916 | 1771 | 227.6 | 116.1 | 59.8 | 297.3 | 141.4
1917 | 1772 | 227.3 | 115.8 | 59.8 | 296.9 | 141.1
1918 | 1773 | 227.1 | 115.8 | 59.8 | 296.3 | 140.9
1919 | 1774 | 226.8 | 115.8 | 59.7 | 295.7 | 140.9
1920 | 1775 | 226.5 | 115.9 | 59.7 | 295.6 | 140.8
1921 | 1776 | 226.2 | 115.8 | 59.5 | 295.3 | 140.7
1922 | 1777 | 226 | 115.7 | 59.3 | 295 | 140.4
1923 | 1778 | 225.7 | 115.3 | 59.2 | 294.9 | 140.2
1924 | 1779 | 225.4 | 115 | 59 | 294.7 | 140
1925 | 1780 | 225.1 | 115 | 58.9 | 294.5 | 139.8
1926 | 1781 | 224.8 | 114.9 | 58.8 | 294.1 | 139.8
1927 | 1782 | 224.5 | 115 | 58.7 | 293.7 | 139.9
1928 | 1783 | 224.2 | 114.8 | 58.8 | 293.4 | 139.8
1929 | 1784 | 223.9 | 114.4 | 59 | 293.1 | 139.6
1930 | 1785 | 223.7 | 114.1 | 59.1 | 292.7 | 139.3
1931 | 1786 | 223.4 | 114.1 | 59.1 | 292 | 139.1
1932 | 1787 | 223.1 | 114.2 | 59 | 291.5 | 138.9
1933 | 1788 | 222.8 | 114.2 | 59 | 291.2 | 138.8
1934 | 1789 | 222.5 | 114.2 | 59 | 290.8 | 138.6
1935 | 1790 | 222.3 | 114 | 59.1 | 290.5 | 138.4
1936 | 1791 | 222 | 113.8 | 59.3 | 290.3 | 138.2
1937 | 1792 | 221.7 | 113.7 | 59.5 | 290.1 | 138
1938 | 1793 | 221.4 | 113.8 | 59.2 | 289.9 | 137.9
1939 | 1794 | 221.2 | 113.8 | 58.9 | 289.4 | 137.8
1940 | 1795 | 220.9 | 113.8 | 58.7 | 288.9 | 137.6
1941 | 1796 | 220.7 | 113.6 | 58.5 | 288.6 | 137.5
1942 | 1797 | 220.4 | 113.1 | 58.2 | 288.2 | 137.4
1943 | 1798 | 220.1 | 113.2 | 58 | 288 | 137.5
1944 | 1799 | 219.8 | 113.1 | 57.9 | 287.7 | 137.4
1945 | 1800 | 219.5 | 113.2 | 58 | 287.6 | 137.4
1946 | 1801 | 219.2 | 113.4 | 57.8 | 287.4 | 137.3
1947 | 1802 | 218.9 | 113.3 | 57.7 | 287.1 | 137.1
1948 | 1803 | 218.6 | 113.1 | 57.8 | 286.8 | 136.8
1949 | 1804 | 218.4 | 112.8 | 57.7 | 286.5 | 136.6
1950 | 1805 | 218.1 | 112.6 | 57.6 | 286.3 | 136.5
1951 | 1806 | 217.8 | 112.8 | 57.4 | 286 | 136.5
1952 | 1807 | 217.5 | 112.9 | 57.3 | 285.7 | 136.4
1953 | 1808 | 217.2 | 112.9 | 57.1 | 285.3 | 136.3
1954 | 1809 | 217 | 112.8 | 57 | 284.9 | 136.1
1955 | 1810 | 216.7 | 112.5 | 56.9 | 284.4 | 135.9
1956 | 1811 | 216.4 | 112.1 | 56.8 | 284 | 135.7
1957 | 1812 | 216.2 | 112.2 | 56.7 | 283.6 | 135.6
1958 | 1813 | 215.9 | 112.3 | 56.6 | 283.2 | 135.4
1959 | 1814 | 215.6 | 112.2 | 56.6 | 282.7 | 135.3
1960 | 1815 | 215.3 | 112 | 56.6 | 282.2 | 135.1
1961 | 1816 | 215 | 111.8 | 56.5 | 281.7 | 134.9
1962 | 1817 | 214.6 | 111.7 | 56.4 | 281.1 | 134.8
1963 | 1818 | 214.3 | 111.4 | 56.5 | 280.7 | 134.5
1964 | 1819 | 213.9 | 111.3 | 56.6 | 280.3 | 134.3
1965 | 1820 | 213.5 | 111.1 | 56.6 | 279.8 | 134.1
1966 | 1821 | 213.2 | 110.6 | 56.6 | 279.5 | 133.8
1967 | 1822 | 212.8 | 110.3 | 56.9 | 279.2 | 133.6
1968 | 1823 | 212.4 | 110.3 | 56.8 | 279 | 133.5
1969 | 1824 | 212.1 | 110.2 | 56.7 | 278.6 | 133.5
1970 | 1825 | 211.7 | 110.1 | 56.6 | 278.5 | 133.4
1971 | 1826 | 211.4 | 109.9 | 56.6 | 278.1 | 133.1
1972 | 1827 | 211 | 109.6 | 56.5 | 277.9 | 132.9
1973 | 1828 | 210.6 | 109.3 | 56.3 | 277.6 | 132.8
1974 | 1829 | 210.2 | 109.1 | 56.2 | 277.2 | 132.6
1975 | 1830 | 209.9 | 109.1 | 56.2 | 277.2 | 132.5
1976 | 1831 | 209.5 | 109 | 56.3 | 277.1 | 132.6
1977 | 1832 | 209.2 | 108.9 | 56.5 | 276.8 | 132.6
1978 | 1833 | 208.8 | 108.8 | 56.8 | 276.5 | 132.6
1979 | 1834 | 208.5 | 108.4 | 57.1 | 276.2 | 132.5
1980 | 1835 | 208.2 | 108.2 | 57.3 | 276 | 132.5
1981 | 1836 | 207.9 | 108.1 | 57.3 | 275.7 | 132.4
1982 | 1837 | 207.6 | 108.2 | 57 | 275.4 | 132.3
1983 | 1838 | 207.3 | 108.2 | 57 | 275.1 | 132.2
1984 | 1839 | 207 | 108.1 | 56.8 | 274.8 | 131.9
1985 | 1840 | 206.8 | 108.1 | 56.4 | 274.5 | 131.7
1986 | 1841 | 206.5 | 107.9 | 56.2 | 274.3 | 131.6
1987 | 1842 | 206.3 | 108 | 56 | 274 | 131.4
1988 | 1843 | 206.1 | 108.1 | 55.9 | 273.5 | 131.4
1989 | 1844 | 205.8 | 108.2 | 56 | 273 | 131.2
1990 | 1845 | 205.5 | 108 | 56 | 272.6 | 130.9
1991 | 1846 | 205.2 | 107.8 | 55.9 | 272 | 130.7
1992 | 1847 | 204.9 | 107.7 | 55.8 | 271.6 | 130.6
1993 | 1848 | 204.6 | 107.4 | 55.8 | 271.4 | 130.3
1994 | 1849 | 204.3 | 107.2 | 55.8 | 271.2 | 130.1
1995 | 1850 | 204 | 107 | 55.6 | 271 | 130
1996 | 1851 | 203.7 | 106.8 | 55.5 | 270.8 | 129.8
1997 | 1852 | 203.4 | 106.6 | 55.4 | 270.7 | 129.6
1998 | 1853 | 203.1 | 106.4 | 55.2 | 270.4 | 129.5
1999 | 1854 | 202.7 | 106.2 | 55.2 | 270.2 | 129.3
2000 | 1855 | 202.4 | 106.2 | 55 | 270 | 129.2
2001 | 1856 | 202 | 106.4 | 54.7 | 269.9 | 129
2002 | 1857 | 201.7 | 106.8 | 54.5 | 269.7 | 128.9
2003 | 1858 | 201.4 | 106.9 | 54.4 | 269.5 | 128.9
2004 | 1859 | 201.1 | 106.8 | 54.3 | 269.2 | 128.8
2005 | 1860 | 200.8 | 106.5 | 54.2 | 268.9 | 128.8
2006 | 1861 | 200.5 | 106.3 | 54.1 | 268.6 | 128.6
2007 | 1862 | 200.2 | 106.1 | 54 | 268.3 | 128.4
2008 | 1863 | 199.9 | 106.2 | 53.9 | 267.8 | 128.1
2009 | 1864 | 199.6 | 106.1 | 53.8 | 267.2 | 127.9
2010 | 1865 | 199.2 | 106.1 | 53.8 | 267 | 127.9
2011 | 1866 | 198.9 | 105.8 | 53.8 | 266.7 | 127.8
2012 | 1867 | 198.6 | 105.7 | 53.6 | 266.4 | 127.7
2013 | 1868 | 198.3 | 105.7 | 53.3 | 266.3 | 127.6
2014 | 1869 | 198.1 | 105.6 | 53.2 | 266 | 127.3
2015 | 1870 | 197.8 | 105.5 | 53.1 | 265.5 | 126.9
2016 | 1871 | 197.5 | 105.1 | 52.8 | 265.2 | 126.9
2017 | 1872 | 197.2 | 104.8 | 52.5 | 264.8 | 126.7
2018 | 1873 | 196.8 | 104.5 | 52.1 | 264.6 | 126.5
2019 | 1874 | 196.5 | 104.3 | 51.8 | 264.5 | 126.4
2020 | 1875 | 196.1 | 103.9 | 51.7 | 264.1 | 126.4
2021 | 1876 | 195.8 | 103.5 | 51.6 | 263.9 | 126.2
2022 | 1877 | 195.5 | 103.3 | 51.3 | 263.8 | 126.1
2023 | 1878 | 195.3 | 103.3 | 51.1 | 263.8 | 126
2024 | 1879 | 195 | 103.3 | 51 | 263.6 | 125.9
2025 | 1880 | 194.7 | 103.2 | 51 | 263 | 125.8
2026 | 1881 | 194.4 | 103.1 | 51.1 | 262.5 | 125.7
2027 | 1882 | 194.1 | 103 | 51.1 | 262.3 | 125.6
2028 | 1883 | 193.8 | 102.8 | 51 | 262.4 | 125.4
2029 | 1884 | 193.5 | 102.5 | 50.7 | 262.2 | 125.2
2030 | 1885 | 193.2 | 102.3 | 50.8 | 262.1 | 125.2
2031 | 1886 | 192.8 | 102.2 | 50.8 | 261.9 | 125.2
2032 | 1887 | 192.6 | 102 | 50.9 | 261.6 | 125.2
2033 | 1888 | 192.3 | 101.6 | 51 | 261.3 | 125.2
2034 | 1889 | 192 | 101.3 | 51.1 | 261 | 125.2
2035 | 1890 | 191.7 | 101.1 | 51.3 | 260.9 | 125.1
2036 | 1891 | 191.5 | 101 | 51.3 | 260.5 | 125.1
2037 | 1892 | 191.2 | 100.9 | 51.1 | 260.2 | 125.1
2038 | 1893 | 191 | 100.9 | 51 | 259.9 | 125.1
2039 | 1894 | 190.7 | 100.7 | 51.1 | 259.5 | 124.9
2040 | 1895 | 190.4 | 100.3 | 51.2 | 259.3 | 124.7
2041 | 1896 | 190.2 | 100.1 | 51.2 | 259.1 | 124.5
2042 | 1897 | 189.9 | 100.1 | 51.2 | 258.9 | 124.4
2043 | 1898 | 189.7 | 100 | 51.1 | 258.7 | 124.3
2044 | 1899 | 189.4 | 99.9 | 50.9 | 258.6 | 124.1
2045 | 1900 | 189.2 | 99.8 | 50.8 | 258.3 | 123.9
2046 | 1901 | 189 | 99.7 | 50.7 | 257.8 | 123.7
2047 | 1902 | 188.7 | 99.6 | 50.5 | 257.6 | 123.6
2048 | 1903 | 188.5 | 99.6 | 50.5 | 257.6 | 123.5
2049 | 1904 | 188.3 | 99.8 | 50.6 | 257.5 | 123.2
2050 | 1905 | 188.1 | 99.7 | 50.6 | 257.5 | 123.2
2051 | 1906 | 187.8 | 99.6 | 50.6 | 257.4 | 123.1
2052 | 1907 | 187.6 | 99.3 | 50.8 | 257.1 | 123.1
2053 | 1908 | 187.4 | 99 | 50.8 | 256.9 | 123.1
2054 | 1909 | 187.2 | 98.9 | 50.9 | 256.8 | 123
2055 | 1910 | 187 | 98.5 | 51 | 256.6 | 123
2056 | 1911 | 186.8 | 98.4 | 50.9 | 256.4 | 122.9
2057 | 1912 | 186.6 | 98.6 | 51 | 256.1 | 122.9
2058 | 1913 | 186.3 | 98.7 | 51.1 | 255.9 | 122.8
2059 | 1914 | 186.1 | 98.8 | 51 | 255.6 | 122.7
2060 | 1915 | 185.9 | 98.7 | 50.9 | 255.2 | 122.5
2061 | 1916 | 185.8 | 98.9 | 50.8 | 255.1 | 122.3
2062 | 1917 | 185.6 | 99 | 50.7 | 254.9 | 122.2
2063 | 1918 | 185.4 | 99.3 | 50.5 | 254.5 | 122.1
2064 | 1919 | 185.2 | 99.4 | 50.4 | 254.3 | 121.9
2065 | 1920 | 185.1 | 99.7 | 50.2 | 254.1 | 121.6
2066 | 1921 | 184.9 | 99.6 | 50.2 | 253.8 | 121.6
2067 | 1922 | 184.8 | 99.4 | 50.2 | 253.5 | 121.5
2068 | 1923 | 184.6 | 99 | 50.1 | 253.1 | 121.3
2069 | 1924 | 184.4 | 98.9 | 50 | 252.6 | 121.1
2070 | 1925 | 184.2 | 99 | 49.9 | 252.2 | 121
2071 | 1926 | 184 | 98.8 | 49.8 | 251.9 | 120.9
2072 | 1927 | 183.8 | 98.7 | 49.8 | 251.5 | 120.6
2073 | 1928 | 183.6 | 98.6 | 49.7 | 251.4 | 120.4
2074 | 1929 | 183.4 | 98.4 | 49.7 | 251.2 | 120.3
2075 | 1930 | 183.2 | 98.2 | 49.8 | 250.9 | 120.1
2076 | 1931 | 183 | 98.2 | 49.8 | 250.6 | 119.9
2077 | 1932 | 182.8 | 98.1 | 49.8 | 250.5 | 119.7
2078 | 1933 | 182.6 | 97.8 | 49.8 | 250.4 | 119.5
2079 | 1934 | 182.4 | 97.6 | 50 | 250.1 | 119.3
2080 | 1935 | 182.1 | 97.4 | 50 | 249.8 | 119.3
2081 | 1936 | 181.9 | 97 | 49.9 | 249.5 | 119
2082 | 1937 | 181.6 | 96.9 | 49.9 | 249.2 | 118.8
2083 | 1938 | 181.4 | 96.7 | 49.9 | 248.7 | 118.5
2084 | 1939 | 181.1 | 96.7 | 49.8 | 248.1 | 118.3
2085 | 1940 | 180.8 | 96.5 | 49.8 | 247.8 | 118.2
2086 | 1941 | 180.5 | 96.1 | 49.9 | 247.6 | 118.1
2087 | 1942 | 180.2 | 95.9 | 50.2 | 247.4 | 118.1
2088 | 1943 | 179.9 | 96 | 50.2 | 247 | 118.1
2089 | 1944 | 179.6 | 96.1 | 50.1 | 246.7 | 118.1
2090 | 1945 | 179.3 | 95.9 | 49.9 | 246.4 | 118.1
2091 | 1946 | 179 | 95.4 | 49.8 | 246.1 | 118
2092 | 1947 | 178.7 | 95.3 | 49.9 | 245.7 | 117.9
2093 | 1948 | 178.5 | 95.1 | 49.8 | 245.5 | 117.8
2094 | 1949 | 178.2 | 95.2 | 49.7 | 245.1 | 117.7
2095 | 1950 | 178 | 95.6 | 49.6 | 244.6 | 117.6
2096 | 1951 | 177.8 | 95.8 | 49.3 | 244.3 | 117.4
2097 | 1952 | 177.5 | 95.9 | 49.2 | 243.8 | 117.2
2098 | 1953 | 177.3 | 95.7 | 49.2 | 243.4 | 116.9
2099 | 1954 | 177.1 | 95.4 | 49.1 | 242.9 | 116.8
2100 | 1955 | 176.8 | 95.4 | 49 | 242.4 | 116.7
2101 | 1956 | 176.6 | 95.4 | 48.7 | 242 | 116.6
2102 | 1957 | 176.4 | 95.5 | 48.5 | 241.8 | 116.5
2103 | 1958 | 176.2 | 95.6 | 48.4 | 241.5 | 116.4
2104 | 1959 | 176 | 95.5 | 48.4 | 241.1 | 116.3
2105 | 1960 | 175.8 | 95.6 | 48.6 | 241 | 116.1
2106 | 1961 | 175.5 | 95.4 | 48.7 | 240.8 | 115.9
2107 | 1962 | 175.4 | 95 | 48.9 | 240.4 | 115.7
2108 | 1963 | 175.1 | 94.8 | 49 | 240.1 | 115.6
2109 | 1964 | 174.9 | 94.7 | 48.8 | 239.7 | 115.4
2110 | 1965 | 174.6 | 94.8 | 48.8 | 239.4 | 115.3
2111 | 1966 | 174.4 | 94.8 | 48.9 | 239.1 | 115.2
2112 | 1967 | 174.1 | 94.9 | 48.7 | 238.7 | 115.2
2113 | 1968 | 173.9 | 95 | 48.6 | 238.5 | 114.9
2114 | 1969 | 173.6 | 95.1 | 48.5 | 238.2 | 115
2115 | 1970 | 173.4 | 95.1 | 48.6 | 237.9 | 114.9
2116 | 1971 | 173.2 | 95 | 48.7 | 237.7 | 114.8
2117 | 1972 | 173 | 94.9 | 48.7 | 237.4 | 114.6
2118 | 1973 | 172.8 | 95.1 | 48.7 | 236.9 | 114.4
2119 | 1974 | 172.6 | 95.3 | 48.8 | 236 | 114.3
2120 | 1975 | 172.4 | 95.6 | 48.7 | 235.6 | 114.1
2121 | 1976 | 172.2 | 95.6 | 48.6 | 235.1 | 113.9
2122 | 1977 | 171.9 | 95.7 | 48.4 | 234.7 | 113.7
2123 | 1978 | 171.7 | 95.4 | 48.6 | 234 | 113.4
2124 | 1979 | 171.4 | 95.1 | 48.6 | 233.4 | 113.3
2125 | 1980 | 171.2 | 94.5 | 48.5 | 233.1 | 113.2
2126 | 1981 | 170.9 | 94.3 | 48.3 | 232.7 | 113.1
2127 | 1982 | 170.6 | 94 | 48.2 | 232.2 | 112.8
2128 | 1983 | 170.3 | 93.8 | 48.1 | 231.6 | 112.7
2129 | 1984 | 170 | 93.6 | 48.1 | 231.2 | 112.5
2130 | 1985 | 169.7 | 93.4 | 48 | 230.9 | 112.4
2131 | 1986 | 169.4 | 93.2 | 48 | 230.6 | 112.2
2132 | 1987 | 169.1 | 93.1 | 47.9 | 229.9 | 112
2133 | 1988 | 168.7 | 92.7 | 47.8 | 229.4 | 111.9
2134 | 1989 | 168.4 | 92.4 | 47.7 | 228.9 | 111.9
2135 | 1990 | 168.1 | 92.2 | 47.6 | 228.6 | 111.7
2136 | 1991 | 167.8 | 92.2 | 47.5 | 228.3 | 111.6
2137 | 1992 | 167.4 | 92.2 | 47.4 | 228 | 111.4
2138 | 1993 | 167.1 | 92.1 | 47.3 | 227.8 | 111.3
2139 | 1994 | 166.8 | 91.9 | 47.2 | 227.7 | 111.1
2140 | 1995 | 166.5 | 91.8 | 47.2 | 227.5 | 110.9
2141 | 1996 | 166.2 | 91.6 | 47.3 | 227.4 | 110.8
2142 | 1997 | 165.9 | 91.8 | 47.3 | 227.2 | 110.8
2143 | 1998 | 165.6 | 91.7 | 47.5 | 227.1 | 110.7
2144 | 1999 | 165.3 | 91.3 | 47.7 | 227 | 110.5
2145 | 2000 | 165.1 | 90.9 | 47.8 | 226.8 | 110.4
2146 | 2001 | 164.8 | 90.7 | 47.8 | 226.5 | 110.3
2147 | 2002 | 164.6 | 90.3 | 47.8 | 226.4 | 110.1
2148 | 2003 | 164.4 | 90 | 47.7 | 226.3 | 109.9
2149 | 2004 | 164.1 | 89.8 | 47.6 | 226.2 | 109.8
2150 | 2005 | 163.9 | 89.3 | 47.5 | 226 | 109.7
2151 | 2006 | 163.6 | 89 | 47.6 | 225.8 | 109.6
2152 | 2007 | 163.4 | 88.8 | 47.7 | 225.5 | 109.5
2153 | 2008 | 163.2 | 88.5 | 47.9 | 225.3 | 109.3
2154 | 2009 | 162.9 | 88.5 | 48 | 225.1 | 109.1
2155 | 2010 | 162.7 | 88.3 | 48 | 224.9 | 109
2156 | 2011 | 162.5 | 88.2 | 48.1 | 224.6 | 109
2157 | 2012 | 162.2 | 88.2 | 47.9 | 224.3 | 108.9
2158 | 2013 | 161.9 | 88.2 | 47.8 | 223.9 | 108.7
2159 | 2014 | 161.7 | 88.2 | 47.6 | 223.7 | 108.6
2160 | 2015 | 161.5 | 88.1 | 47.4 | 223.3 | 108.6
2161 | 2016 | 161.3 | 87.8 | 47.1 | 223 | 108.4
2162 | 2017 | 161.1 | 87.6 | 46.9 | 222.6 | 108.2
2163 | 2018 | 160.8 | 87.5 | 46.7 | 222.3 | 108.2
2164 | 2019 | 160.6 | 87.2 | 46.6 | 222 | 108
2165 | 2020 | 160.4 | 87.2 | 46.5 | 221.7 | 107.8
2166 | 2021 | 160.1 | 87.2 | 46.3 | 221.1 | 107.7
2167 | 2022 | 159.9 | 87 | 46.3 | 220.8 | 107.6
2168 | 2023 | 159.6 | 87.2 | 46.2 | 220.6 | 107.4
2169 | 2024 | 159.4 | 87.4 | 46.3 | 220.3 | 107.2
2170 | 2025 | 159.2 | 87.4 | 46.3 | 220.1 | 107.1
2171 | 2026 | 159 | 87.4 | 46.2 | 219.8 | 107
2172 | 2027 | 158.8 | 87 | 46 | 219.5 | 106.9
2173 | 2028 | 158.6 | 86.8 | 45.9 | 219.2 | 106.9
2174 | 2029 | 158.3 | 86.6 | 45.8 | 219 | 106.9
2175 | 2030 | 158.1 | 86.4 | 45.7 | 218.7 | 106.7
2176 | 2031 | 157.9 | 86.4 | 45.7 | 218.5 | 106.6
2177 | 2032 | 157.7 | 86.3 | 45.7 | 218.3 | 106.4
2178 | 2033 | 157.5 | 86.1 | 45.6 | 218 | 106.2
2179 | 2034 | 157.2 | 86.1 | 45.5 | 217.6 | 106
2180 | 2035 | 157 | 85.9 | 45.5 | 217.4 | 105.9
2181 | 2036 | 156.8 | 85.9 | 45.3 | 216.9 | 105.8
2182 | 2037 | 156.6 | 85.7 | 45.2 | 216.3 | 105.6
2183 | 2038 | 156.4 | 85.4 | 44.9 | 215.9 | 105.5
2184 | 2039 | 156.1 | 85.3 | 44.7 | 215.7 | 105.3
2185 | 2040 | 155.9 | 85.4 | 44.5 | 215.4 | 105.2
2186 | 2041 | 155.7 | 85.5 | 44.3 | 215 | 105.1
2187 | 2042 | 155.4 | 85.5 | 43.9 | 214.6 | 104.9
2188 | 2043 | 155.2 | 85.6 | 43.9 | 214.4 | 104.8
2189 | 2044 | 154.9 | 85.8 | 43.8 | 214.1 | 104.8
2190 | 2045 | 154.7 | 85.9 | 43.4 | 213.9 | 104.7
2191 | 2046 | 154.4 | 86 | 43 | 213.5 | 104.7
2192 | 2047 | 154.2 | 86.3 | 42.7 | 213.2 | 104.7
2193 | 2048 | 153.9 | 86.5 | 42.4 | 212.7 | 104.6
2194 | 2049 | 153.7 | 86.8 | 42.4 | 212.5 | 104.5
2195 | 2050 | 153.5 | 87.1 | 42.3 | 212.2 | 104.4
2196 | 2051 | 153.3 | 87.3 | 42.2 | 211.9 | 104.2
2197 | 2052 | 153.1 | 87.3 | 42.2 | 211.6 | 104.2
2198 | 2053 | 152.9 | 87.2 | 42.2 | 211.3 | 104.1
2199 | 2054 | 152.7 | 87.3 | 42 | 211.1 | 104
2200 | 2055 | 152.6 | 87.7 | 42.2 | 210.9 | 103.8
2201 | 2056 | 152.4 | 87.6 | 42.3 | 210.5 | 103.6
2202 | 2057 | 152.3 | 87.2 | 42.3 | 210.2 | 103.4
2203 | 2058 | 152.1 | 87 | 42.3 | 209.7 | 103.3
2204 | 2059 | 151.9 | 86.9 | 42.3 | 209.1 | 103.1
2205 | 2060 | 151.7 | 86.8 | 42.3 | 208.5 | 103
2206 | 2061 | 151.5 | 86.4 | 42.2 | 208.2 | 102.9
2207 | 2062 | 151.4 | 86.2 | 42.2 | 207.9 | 102.8
2208 | 2063 | 151.2 | 86.2 | 42.3 | 207.4 | 102.7
2209 | 2064 | 151 | 86.1 | 42.4 | 206.9 | 102.6
2210 | 2065 | 150.8 | 86.2 | 42.4 | 206.7 | 102.6
2211 | 2066 | 150.6 | 86.3 | 42.4 | 206.5 | 102.5
2212 | 2067 | 150.4 | 86.2 | 42.4 | 206.2 | 102.3
2213 | 2068 | 150.2 | 86.4 | 42.5 | 205.9 | 102.3
2214 | 2069 | 150 | 86.6 | 42.5 | 205.6 | 102.2
2215 | 2070 | 149.8 | 86.8 | 42.6 | 205.3 | 102
2216 | 2071 | 149.6 | 86.7 | 42.7 | 205 | 102
2217 | 2072 | 149.4 | 86.5 | 42.9 | 204.7 | 102
2218 | 2073 | 149.2 | 86.3 | 43.1 | 204.5 | 101.9
2219 | 2074 | 149 | 86.2 | 43 | 204.1 | 101.8
2220 | 2075 | 148.9 | 85.9 | 43 | 203.8 | 101.7
2221 | 2076 | 148.7 | 85.9 | 43 | 203.5 | 101.6
2222 | 2077 | 148.5 | 85.8 | 43 | 203.1 | 101.5
2223 | 2078 | 148.3 | 85.6 | 43 | 202.8 | 101.4
2224 | 2079 | 148.2 | 85.4 | 43 | 202.5 | 101.3
2225 | 2080 | 148 | 85 | 43.1 | 202.2 | 101.1
2226 | 2081 | 147.9 | 84.8 | 43.1 | 202 | 100.9
2227 | 2082 | 147.7 | 84.4 | 43 | 201.4 | 100.8
2228 | 2083 | 147.5 | 84 | 42.9 | 200.9 | 100.7
2229 | 2084 | 147.3 | 83.7 | 42.9 | 200.6 | 100.5
2230 | 2085 | 147.1 | 83.6 | 42.8 | 200.2 | 100.4
2231 | 2086 | 146.9 | 83.6 | 42.7 | 199.8 | 100.3
2232 | 2087 | 146.7 | 83.7 | 42.7 | 199.5 | 100.3
2233 | 2088 | 146.5 | 83.4 | 42.6 | 199.4 | 100.2
2234 | 2089 | 146.3 | 83.2 | 42.5 | 199.1 | 100.2
2235 | 2090 | 146.1 | 83.1 | 42.5 | 198.7 | 100
2236 | 2091 | 146 | 83 | 42.5 | 198.5 | 99.8
2237 | 2092 | 145.8 | 83 | 42.8 | 198.1 | 99.7
2238 | 2093 | 145.6 | 82.7 | 42.9 | 197.7 | 99.5
2239 | 2094 | 145.4 | 82.8 | 42.9 | 197.4 | 99.4
2240 | 2095 | 145.2 | 82.9 | 43 | 197 | 99.4
2241 | 2096 | 145 | 82.8 | 43 | 196.5 | 99.4
2242 | 2097 | 144.7 | 82.6 | 42.9 | 196.1 | 99.3
2243.1 | 2098.1 | 144.5 | 82.6 | 42.8 | 195.6 | 99.3
2244.1 | 2099.1 | 144.2 | 82.4 | 42.7 | 195.4 | 99.2
2245.1 | 2100.1 | 144 | 82.3 | 42.6 | 195.1 | 99.1
2246.1 | 2101.1 | 143.8 | 82.2 | 42.6 | 194.7 | 99
2247.1 | 2102.1 | 143.6 | 82.1 | 42.4 | 194.4 | 99
2248.1 | 2103.1 | 143.4 | 81.9 | 42.4 | 194 | 98.9
2249.1 | 2104.1 | 143.2 | 81.8 | 42.5 | 193.7 | 98.9
2250.1 | 2105.1 | 143 | 81.8 | 42.6 | 193.4 | 99
2251.1 | 2106.1 | 142.8 | 81.7 | 42.6 | 193 | 99
2252.1 | 2107.1 | 142.6 | 81.5 | 42.8 | 192.5 | 98.9
2253.1 | 2108.1 | 142.4 | 81.4 | 42.8 | 192.1 | 98.9
2254.1 | 2109.1 | 142.3 | 81.4 | 42.8 | 191.7 | 98.8
2255.1 | 2110.1 | 142.1 | 81.3 | 42.8 | 191.1 | 98.8
2256.1 | 2111.1 | 142 | 81.3 | 42.8 | 190.5 | 98.7
2257.1 | 2112.1 | 141.8 | 81.3 | 42.7 | 190 | 98.5
2258.1 | 2113.1 | 141.7 | 81.2 | 42.7 | 189.7 | 98.4
2259.1 | 2114.1 | 141.5 | 81.3 | 42.6 | 189.2 | 98.2
2260.1 | 2115.1 | 141.4 | 81.2 | 42.4 | 188.7 | 98.1
2261.1 | 2116.1 | 141.2 | 81.1 | 42.3 | 188.1 | 97.9
2262.1 | 2117.1 | 141.1 | 81 | 42.2 | 187.7 | 97.9
2263.1 | 2118.1 | 141 | 80.9 | 42.1 | 187.3 | 97.8
2264.1 | 2119.1 | 140.8 | 81 | 41.9 | 186.8 | 97.7
2265.1 | 2120.1 | 140.6 | 80.9 | 41.8 | 186.6 | 97.6
2266.1 | 2121.1 | 140.5 | 80.9 | 41.7 | 186.1 | 97.5
2267.1 | 2122.1 | 140.4 | 80.9 | 41.7 | 185.7 | 97.4
2268.1 | 2123.1 | 140.2 | 80.8 | 41.7 | 185.3 | 97.3
2269.1 | 2124.1 | 140.1 | 80.9 | 41.8 | 184.9 | 97.2
2270.1 | 2125.1 | 139.9 | 80.8 | 41.8 | 184.5 | 97
2271.1 | 2126.1 | 139.8 | 81 | 41.7 | 184 | 97
2272.1 | 2127.1 | 139.6 | 81.1 | 41.8 | 183.6 | 96.9
2273.1 | 2128.1 | 139.5 | 81.3 | 41.8 | 183.1 | 96.7
2274.1 | 2129.1 | 139.3 | 81.1 | 41.7 | 182.7 | 96.6
2275.1 | 2130.1 | 139.2 | 81 | 41.7 | 182.3 | 96.5
2276.1 | 2131.1 | 139.1 | 80.7 | 41.8 | 181.8 | 96.3
2277.1 | 2132.1 | 138.9 | 80.5 | 41.8 | 181.3 | 96.2
2278.1 | 2133.1 | 138.8 | 80.4 | 41.9 | 180.9 | 96.1
2279.1 | 2134.1 | 138.6 | 80.3 | 41.9 | 180.5 | 96
2280.1 | 2135.1 | 138.4 | 80.3 | 41.8 | 180 | 96
2281.1 | 2136.1 | 138.3 | 79.9 | 41.9 | 179.5 | 95.8
2282.1 | 2137.1 | 138.1 | 79.7 | 41.8 | 179 | 95.6
2283.1 | 2138.1 | 137.9 | 79.5 | 41.8 | 178.7 | 95.5
2284.1 | 2139.1 | 137.7 | 79.4 | 41.8 | 178.3 | 95.5
2285.1 | 2140.1 | 137.5 | 79.3 | 41.9 | 177.9 | 95.5
2286.1 | 2141.1 | 137.3 | 79.2 | 42 | 177.6 | 95.4
2287.1 | 2142.1 | 137 | 79.1 | 42.1 | 177.2 | 95.4
2288.1 | 2143.1 | 136.8 | 79.1 | 42.2 | 176.8 | 95.3
2289.1 | 2144.1 | 136.6 | 79.1 | 42.3 | 176.5 | 95.3
2290.1 | 2145.1 | 136.4 | 79.1 | 42.3 | 176.1 | 95.2
2291.1 | 2146.1 | 136.2 | 79.2 | 42.3 | 175.8 | 95.1
2292.1 | 2147.1 | 136.1 | 79.3 | 42.1 | 175.2 | 95
2293.1 | 2148.1 | 135.9 | 79.1 | 42.1 | 174.7 | 94.9
2294.1 | 2149.1 | 135.7 | 78.8 | 42 | 174.3 | 94.8
2295.1 | 2150.1 | 135.5 | 78.5 | 42.1 | 173.9 | 94.6
2296.1 | 2151.1 | 135.4 | 78.5 | 42 | 173.4 | 94.6
2297.1 | 2152.1 | 135.2 | 78.5 | 41.8 | 172.9 | 94.5
2298.1 | 2153.1 | 135 | 78.5 | 41.7 | 172.5 | 94.4
2299.1 | 2154.1 | 134.8 | 78.4 | 41.5 | 172 | 94.3
2300.1 | 2155.1 | 134.6 | 78.4 | 41.5 | 171.4 | 94.2
2301.1 | 2156.1 | 134.4 | 78.1 | 41.5 | 170.9 | 94.1
2302.1 | 2157.1 | 134.2 | 78 | 41.5 | 170.3 | 94
2303.1 | 2158.1 | 134 | 77.9 | 41.5 | 169.7 | 93.8
2304.1 | 2159.1 | 133.8 | 77.6 | 41.4 | 169.2 | 93.6
2305.1 | 2160.1 | 133.6 | 77.2 | 41.1 | 168.7 | 93.5
2306.1 | 2161.1 | 133.4 | 77.1 | 41 | 168.2 | 93.4
2307.1 | 2162.1 | 133.2 | 76.9 | 40.8 | 167.6 | 93.4
2308.1 | 2163.1 | 133 | 77.1 | 40.7 | 167.1 | 93.2
2309.1 | 2164.1 | 132.8 | 76.9 | 40.6 | 166.6 | 93.1
2310.1 | 2165.1 | 132.6 | 76.7 | 40.4 | 166.2 | 93.1
2311.1 | 2166.1 | 132.4 | 76.7 | 40.4 | 165.7 | 93
2312.1 | 2167.1 | 132.1 | 76.8 | 40.1 | 165.1 | 92.9
2313.1 | 2168.1 | 131.9 | 76.9 | 39.9 | 164.7 | 92.8
2314.1 | 2169.1 | 131.7 | 77.1 | 39.9 | 164.2 | 92.7
2315.1 | 2170.1 | 131.5 | 77.4 | 39.7 | 163.8 | 92.6
2316.1 | 2171.1 | 131.3 | 77.5 | 39.5 | 163.3 | 92.5
2317.1 | 2172.1 | 131.1 | 77.5 | 39.4 | 162.8 | 92.4
2318.1 | 2173.1 | 130.9 | 77.4 | 39.1 | 162.3 | 92.4
2319.1 | 2174.1 | 130.7 | 77.4 | 38.8 | 162 | 92.3
2320.1 | 2175.1 | 130.5 | 77.5 | 38.5 | 161.6 | 92.2
2321.1 | 2176.1 | 130.3 | 77.6 | 38.3 | 161.1 | 92
2322.1 | 2177.1 | 130.1 | 77.6 | 38.2 | 160.8 | 92
2323.1 | 2178.1 | 130 | 77.8 | 38.1 | 160.3 | 91.9
2324.1 | 2179.1 | 129.8 | 77.9 | 38.1 | 159.7 | 91.8
2325.1 | 2180.1 | 129.6 | 78.1 | 38.1 | 159.2 | 91.7
2326.1 | 2181.1 | 129.5 | 78.1 | 38 | 158.7 | 91.6
2327.1 | 2182.1 | 129.3 | 78.2 | 38.4 | 158.2 | 91.6
2328.1 | 2183.1 | 129.1 | 78.4 | 38.6 | 157.7 | 91.5
2329.1 | 2184.1 | 128.9 | 78.3 | 38.7 | 157 | 91.5
2330.1 | 2185.1 | 128.7 | 78.1 | 38.7 | 156.4 | 91.4
2331.1 | 2186.1 | 128.5 | 78.1 | 38.8 | 155.7 | 91.2
2332.1 | 2187.1 | 128.3 | 78.1 | 38.7 | 155.3 | 91.1
2333.1 | 2188.1 | 128.1 | 77.8 | 38.7 | 154.7 | 91
2334.1 | 2189.1 | 127.8 | 77.4 | 38.6 | 154.2 | 90.9
2335.1 | 2190.1 | 127.6 | 77.1 | 38.5 | 153.8 | 90.7
2336.1 | 2191.1 | 127.4 | 76.6 | 38.4 | 153.3 | 90.7
2337.1 | 2192.1 | 127.3 | 76.4 | 38.1 | 152.9 | 90.5
2338.1 | 2193.1 | 127.1 | 76.2 | 37.9 | 152.4 | 90.3
2339.1 | 2194.1 | 126.9 | 76 | 37.8 | 151.9 | 90.3
2340.1 | 2195.1 | 126.7 | 75.8 | 37.7 | 151.4 | 90.2
2341.1 | 2196.1 | 126.5 | 75.5 | 37.6 | 150.9 | 90.1
2342.1 | 2197.1 | 126.3 | 75.3 | 37.6 | 150.4 | 90
2343.1 | 2198.1 | 126.1 | 75.1 | 37.6 | 149.8 | 89.9
2344.1 | 2199.1 | 125.8 | 75 | 37.6 | 149.2 | 89.8
2345.1 | 2200.1 | 125.6 | 75 | 37.5 | 148.7 | 89.7
2346.1 | 2201.1 | 125.3 | 75.1 | 37.2 | 148.2 | 89.5
2347.1 | 2202.1 | 125.1 | 75 | 36.9 | 147.7 | 89.3
2348.1 | 2203.1 | 124.8 | 74.9 | 36.8 | 147.2 | 89.3
2349.1 | 2204.1 | 124.6 | 74.9 | 36.7 | 146.7 | 89.3
2350.1 | 2205.1 | 124.4 | 74.9 | 36.7 | 146.3 | 89.1
2351.1 | 2206.1 | 124.2 | 75 | 36.7 | 145.8 | 89
2352.1 | 2207.1 | 123.9 | 75.1 | 36.5 | 145.2 | 88.9
2353.1 | 2208.1 | 123.7 | 75 | 36.4 | 144.7 | 88.8
2354.1 | 2209.1 | 123.5 | 74.9 | 36.4 | 144 | 88.7
2355.1 | 2210.1 | 123.3 | 74.6 | 36.6 | 143.4 | 88.6
2356.1 | 2211.1 | 123.1 | 74.4 | 36.6 | 142.9 | 88.4
2357.1 | 2212.1 | 122.9 | 74.1 | 36.6 | 142.4 | 88.3
2358.1 | 2213.1 | 122.7 | 73.9 | 36.6 | 141.9 | 88.2
2359.1 | 2214.1 | 122.5 | 73.8 | 36.6 | 141.3 | 88.1
2360.1 | 2215.1 | 122.3 | 73.6 | 36.7 | 140.8 | 88
2361.1 | 2216.1 | 122.1 | 73.5 | 36.6 | 140.4 | 87.9
2362.1 | 2217.1 | 121.9 | 73.5 | 36.6 | 140 | 87.8
2363.1 | 2218.1 | 121.7 | 73.5 | 36.6 | 139.6 | 87.8
2364.1 | 2219.1 | 121.5 | 73.5 | 36.6 | 139 | 87.7
2365.1 | 2220.1 | 121.3 | 73.6 | 36.8 | 138.5 | 87.7
2366.1 | 2221.1 | 121.1 | 73.7 | 37 | 138 | 87.7
2367.1 | 2222.1 | 120.9 | 73.6 | 37.1 | 137.5 | 87.7
2368.1 | 2223.1 | 120.7 | 73.4 | 37.3 | 137.1 | 87.6
2369.1 | 2224.1 | 120.5 | 73.4 | 37.4 | 136.6 | 87.6
2370.1 | 2225.1 | 120.3 | 73.3 | 37.5 | 136.2 | 87.5
2371.1 | 2226.1 | 120.1 | 73.2 | 37.5 | 135.7 | 87.5
2372.1 | 2227.1 | 119.9 | 73.1 | 37.5 | 135.2 | 87.4
2373.1 | 2228.1 | 119.7 | 72.8 | 37.5 | 134.7 | 87.3

## Test Facts
Last row in IRMS data sheets: | 14
Time when Penlight power was initiated: | 145