## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-4 - Circuit Simulator Data Only
Test Date: | 2006-10-30
Circuit Simulator Configurations and connections:
|  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 150 VA | 150 VA | 200 VA | 100 VA
| CPT Grounding: | NOT Grounded | Grounded | Grounded | Grounded
| General Config. | Inter-Cable in a mixed bundle of TS&TP cables | Inter-Cable in a mixed bundle of TS&TP cables | Inter-Cable in a mixed bundle of TS&TP cables | Inter-Cable in a mixed bundle of TS&TP cables
| Cable Type VERIFY | Mixed bundle - XLPE (cable item 3), PE (15) and TEF (12) | Mixed bundle - XLPE (cable item 3), PE (15) and TEF (12) | Mixed bundle - XLPE (cable item 3), PE (15) and TEF (12) | Mixed bundle - XLPE (cable item 3), PE (15) and TEF (12)
| Wiring Config: | XLPE as Source 1 Tefzel as Source 2 PE as Targets 4,5,6 Three cables in lower row (next to rungs) not connected | XLPE as Source 1 PE as Source 2 TEF as Targets 4,5,6 Three cables in lower row (next to rungs) not connected | XLPE as Source 1 PE as Source 2 TEF as Targets 4,5,6 Three cables in lower row (next to rungs) not connected | XLPE as Source 1 Tefzel as Source 2 PE as Targets 4,5,6 Three cables in lower row (next to rungs) not connected
| Circuit Path 1: | Switch Closed: Energized source (XLPE). | Switch Closed: Energized source to XLPE cable | Switch Closed: Energized source to XLPE cable | Switch Closed: Energized source (XLPE).
| Circuit Path 2: | Switch Closed: Energized source (TEF). | Switch Closed: Energized source to PE cable | Switch Closed: Energized source to PE cable | Switch Closed: Energized source (TEF).
| Circuit Path 3: | no connection | no connection | no connection | no connection
| Circuit Path 4: | Passive Target: Connects 1.75 k-ohm to PE cable. | Passive Target: Connects 1.75 k-ohm to TEF cable. | Passive Target: Connects 1.75 k-ohm to TEF cable. | Passive Target: Connects 1.75 k-ohm to PE cable.
| Circuit Path 5: | Active Target: Connects Motor contactor and PE cable | Active Target: Connects Motor contactor and TEF cable | Active Target: Connects Motor contactor and TEF cable | Active Target: Connects Motor contactor and PE cable
| Circuit Path 6: | Active Target: Connects Motor contactor and PE cable | Active Target: Connects Motor contactor and TEF cable | Active Target: Connects Motor contactor and TEF cable | Active Target: Connects Motor contactor and PE cable
| Circuit Path 7: | no connection | no connection | no connection | no connection
| Circuit Path 8: | no connection | no connection | no connection | no connection
| Circuit Path 9: | no connection | no connection | no connection | no connection
A Note on Data Conversion and Accuracy:
Each of the voltage and current transducers used produces a 4-20mA signal which is routed through 477ohm precision resistors converting the signal to a nominal 2-10 VDC signal. This DC voltage signal was monitored using a National Instruments PCI-6071E data aquisition (DAQ) card. These data as recorded are presented in the "Raw Test Data" worksheet. The raw data were converted to actual values as shown on the "Converted Test Data" worksheet. The conversion is based on the fact that the 4-20 mA signal corresponds to a full scale reading on the voltage transducers of 0-300 VAC and on the current transducers of 0-5A. Nominal zero point readings for each transducer were taken in a separate test run in order to establish more accurately the zero points for current and voltage measurement. The Zero Point values are provided, and the full run is documented in a separate data file (see 'Zero Points' worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Circuit Fault Summary
Summary of Circuit Faulting Beharior for all Tested Circuits
Circuit 1 | This circuit was set up to look for intercable hot shorts in a mixed bundle of TS and TP cables. The configuration does not allow for a fuse blow failure. Spurious actuations are observed. However, given the behavior (slowly building voltages and never reaching full source potential) these were likely due to multiple ground faults rather than conductor-to-conductor interactions. The Tefzel cable acted as the main source for the hot shorts based on measured current data indicating mainly TP-to-TP interactions if inter-cable interactions did occur. Some indication of current leakage from the XLPE cable is seen late in the test, but at a minor level.
Circuit 2 | The energized PE cable experienced a short to ground causing a circuit fuse blow. No signs of source voltage degradation prior to FB are noted.
Circuit 3 | The energized PE cable experienced a short to ground causing a circuit fuse blow. No signs of source voltage degradation prior to FB are noted.
Circuit 4 | The energized Tefzel cable experiences short to ground over an extended period that first degrades CPT voltage and eventually leads to a fuse blow failure. No indications of inter-cable interactions. Minimum voltage degradation prior to fuse blow is about 80V
Note:

## Circuit 1 Faulting
Summary of Observed Faulting Behavior for Circuit #1
DAQ Time | Burner Time | Event | Discussion
276 | 0 | Ignited Gas Burner
538 | 262 | Spike to T6 | a short duration voltage spike is observed to target 6
553-572 | 277-296 | V4 increasing | an increasing voltage is indicated on passive target 4 that abruptly drops off at 572 s
575 | 299 | SA-T5 and HS-T4 | T5 spurious actuates and T4 hot shorts to source.
578 | 302 | SA-T6 | Spurious actuation of T6
Summary observations |  | This circuit was set up to look for intercable hot shorts in a mixed bundle of TS and TP cables. The configuration does not allow for a fuse blow failure. Spurious actuations are observed. However, given the behavior (slowly building voltages and never reaching full source potential) these were likely due to multiple ground faults rather than conductor-to-conductor interactions. The Tefzel cable acted as the main source for the hot shorts based on measured current data indicating mainly TP-to-TP interactions if inter-cable interactions did occur. Some indication of current leakage from the XLPE cable is seen late in the test, but at a minor level.

## Converted Data C1
DAQ Time | Burner Time | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6
0 | -276 | 132.2813 | 0.010711 | 131.7836 | 0.0097225 | 0.67706 | 0.0071055 | 0.53384 | 0.0066219 | 0.58066 | 0.0051674
30 | -246 | 131.21 | 0.002595 | 130.7122 | 0.0016062 | 0.19008 | 0.00061214 | 0.14424 | 0.0017522 | 0.28848 | 0.00029777
60 | -216 | 130.9178 | 0.0090883 | 130.6148 | 0.0048528 | -0.0047195 | 0.00061214 | 0.14424 | 0.00012922 | 0.19109 | -0.0013259
90 | -186 | 131.0152 | 0.002595 | 130.7122 | 0.0016062 | 0.28746 | 0.0022351 | 0.24166 | 0.0017522 | 0.38586 | 0.0019208
120 | -156 | 130.6256 | 0.0042186 | 130.2252 | 0.0016062 | 0.092701 | 0.00061214 | 0.14424 | 0.00012922 | 0.19109 | 0.00029777
150 | -126 | 131.0152 | 0.0090883 | 130.6148 | 0.0048528 | 0.092701 | 0.00061214 | 0.24166 | 0.00012922 | 0.19109 | 0.00029777
180 | -96 | 131.1126 | 0.002595 | 130.6148 | 0.0016062 | 0.28746 | 0.00061214 | 0.33904 | 0.0017522 | 0.38586 | 0.0019208
210 | -66 | 131.4048 | 0.0042186 | 131.0044 | 0.0016062 | 0.48226 | 0.0022351 | 0.43642 | 0.0017522 | 0.48328 | 0.0019208
240 | -36 | 131.4048 | 0.0058416 | 131.0044 | 0.0016062 | 0.57968 | 0.0022351 | 0.53384 | 0.0033759 | 0.58066 | 0.0019208
270 | -6 | 131.0152 | 0.0042186 | 130.5174 | 0.0032298 | 0.48226 | 0.0022351 | 0.43642 | 0.0033759 | 0.48328 | 0.0019208
300 | 24 | 130.723 | 0.0058416 | 130.3226 | 0.0016062 | 0.19008 | 0.00061214 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777
330 | 54 | 131.21 | 0.0042186 | 130.7122 | 0.0016062 | 0.48226 | 0.0022351 | 0.53384 | -0.0014944 | 0.58066 | 0.0051674
360 | 84 | 130.8204 | 0.0074646 | 130.42 | 0.0032298 | 0.19008 | 0.00061214 | 0.33904 | -0.0014944 | 0.28848 | 0.00029777
390 | 114 | 127.8011 | 0.0058416 | 127.4981 | 0.0032298 | 0.092701 | -0.0010109 | 0.24166 | -0.0014944 | 0.28848 | 0.00029777
420 | 144 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.19008 | 0.00061214 | 0.33904 | 0.00012922 | 0.28848 | 0.00029777
450 | 174 | 131.5022 | 0.0058416 | 130.907 | 0.0032298 | 1.0667 | 0.0071055 | 1.0208 | 0.0066219 | 1.1651 | 0.0051674
480 | 204 | 132.0865 | 0.0074646 | 131.394 | 0.0016062 | 1.5536 | 0.0087285 | 1.313 | 0.0066219 | 1.4572 | 0.0084141
510 | 234 | 130.8204 | 0.0058416 | 130.42 | 0.0016062 | 0.48226 | 0.0022351 | 0.43642 | 0.0017522 | 0.48328 | 0.0019208
511 | 235 | 130.8204 | 0.0058416 | 130.42 | 0.0016062 | 0.38488 | 0.0022351 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
512 | 236 | 130.723 | 0.0074646 | 130.3226 | 0.0016062 | 0.38488 | 0.0022351 | 0.43642 | 0.0017522 | 0.48328 | 0.0019208
513 | 237 | 130.8204 | 0.0058416 | 130.42 | 0.0016062 | 0.38488 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
514 | 238 | 130.723 | 0.0058416 | 130.3226 | 0.0016062 | 0.38488 | 0.0022351 | 0.53384 | 0.0017522 | 0.38586 | 0.0019208
515 | 239 | 130.8204 | 0.0074646 | 130.3226 | 0.0016062 | 0.38488 | 0.0022351 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
516 | 240 | 130.723 | 0.0058416 | 130.3226 | 0.0016062 | 0.38488 | 0.0022351 | 0.43642 | 0.00012922 | 0.48328 | 0.00029777
517 | 241 | 130.8204 | 0.0058416 | 130.3226 | 0.0016062 | 0.38488 | 0.00061214 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777
518 | 242 | 130.8204 | 0.0058416 | 130.3226 | 0.0016062 | 0.38488 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.00029777
519 | 243 | 130.9178 | 0.0074646 | 130.42 | 0.0016062 | 0.38488 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
520 | 244 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.57968 | 0.00061214 | 0.43642 | 0.00012922 | 0.48328 | 0.00029777
521 | 245 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.57968 | 0.0022351 | 0.33904 | 0.0017522 | 0.48328 | 0.0019208
522 | 246 | 130.8204 | 0.0058416 | 130.42 | 0.0016062 | 0.48226 | 0.0022351 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
523 | 247 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.48226 | 0.0022351 | 0.43642 | 0.0017522 | 0.48328 | 0.00029777
524 | 248 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.48226 | 0.0022351 | 0.33904 | 0.0017522 | 0.38586 | 0.0019208
525 | 249 | 131.0152 | 0.0058416 | 130.5174 | 0.0032298 | 0.38488 | 0.00061214 | 0.43642 | 0.0017522 | 0.48328 | 0.0019208
526 | 250 | 131.0152 | 0.0058416 | 130.5174 | 0.0016062 | 0.48226 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
527 | 251 | 130.8204 | 0.0058416 | 130.3226 | 0.0016062 | 0.48226 | 0.0022351 | 0.82602 | 0.0017522 | 0.38586 | 0.0019208
527.2 | 251.2 | 130.8204 | 0.0058416 | 130.3226 | 0.0016062 | 0.48226 | 0.00061214 | 2.3844 | 0.0017522 | 0.38586 | 0.00029777
527.4 | 251.4 | 130.9178 | 0.0058416 | 130.5174 | 0.0032298 | 0.48226 | 0.00061214 | 1.8 | 0.016362 | 0.38586 | 0.0035444
527.6 | 251.6 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.48226 | 0.0022351 | 0.9234 | 0.0033759 | 0.38586 | 0.00029777
527.8 | 251.8 | 131.0152 | 0.0058416 | 130.5174 | 0.0032298 | 0.48226 | 0.0022351 | 0.63122 | 0.0033759 | 0.48328 | 0.00029777
528 | 252 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.48226 | 0.0022351 | 0.63122 | 0.0033759 | 0.48328 | 0.0019208
529 | 253 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.48226 | 0.0022351 | 0.43642 | 0.0017522 | 0.38586 | 0.00029777
530 | 254 | 130.9178 | 0.0058416 | 130.42 | 0.0032298 | 0.67706 | 0.00061214 | 1.1182 | 0.0017522 | 0.48328 | 0.00029777
530.2 | 254.2 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.67706 | 0.0022351 | 1.313 | 0.0017522 | 0.38586 | 0.0019208
530.4 | 254.4 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.57968 | 0.00061214 | 1.6052 | 0.0017522 | 0.38586 | 0.00029777
530.6 | 254.6 | 131.0152 | 0.0058416 | 130.6148 | 0.0064758 | 0.77444 | 0.021715 | 4.1375 | 0.3329 | 0.67808 | 0.0067905
530.8 | 254.8 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.57968 | 0.0022351 | 3.4557 | 0.0033759 | 0.48328 | 0.0019208
531 | 255 | 130.9178 | 0.0058416 | 130.42 | 0.0016062 | 0.67706 | 0.0022351 | 7.0594 | 0.0033759 | 0.38586 | 0.00029777
531.2 | 255.2 | 130.723 | 0.0058416 | 130.2252 | 0.0032298 | 0.67706 | 0.0022351 | 5.0141 | 0.011492 | 0.48328 | 0.00029777
531.4 | 255.4 | 130.6256 | 0.0058416 | 130.1278 | 0.040565 | 0.57968 | 0.0022351 | 6.962 | 0.05045 | 0.48328 | 0.0019208
531.6 | 255.6 | 130.9178 | 0.0058416 | 130.5174 | 0.017839 | 0.57968 | 0.00061214 | 1.7026 | 0.017985 | 0.38586 | 0.00029777
531.8 | 255.8 | 130.9178 | 0.0058416 | 130.5174 | 0.0097225 | 0.57968 | 0.00061214 | 0.82602 | 0.0082456 | 0.38586 | 0.00029777
532 | 256 | 130.8204 | 0.0058416 | 130.42 | 0.0064758 | 0.67706 | 0.00061214 | 0.63122 | 0.0049989 | 0.38586 | 0.00029777
532.2 | 256.2 | 130.9178 | 0.0058416 | 130.5174 | 0.0048528 | 0.67706 | 0.00061214 | 0.53384 | 0.0033759 | 0.38586 | 0.00029777
532.4 | 256.4 | 130.9178 | 0.0058416 | 130.5174 | 0.0048528 | 0.67706 | 0.00061214 | 0.53384 | 0.0033759 | 0.48328 | 0.0019208
532.6 | 256.6 | 131.0152 | 0.0058416 | 130.5174 | 0.0048528 | 0.67706 | 0.00061214 | 0.43642 | 0.0033759 | 0.38586 | 0.0019208
532.8 | 256.8 | 131.0152 | 0.0074646 | 130.5174 | 0.0032298 | 0.67706 | 0.00061214 | 0.43642 | 0.0033759 | 0.38586 | 0.00029777
533 | 257 | 130.9178 | 0.0058416 | 130.5174 | 0.0032298 | 0.57968 | 0.0022351 | 0.43642 | 0.0017522 | 0.38586 | 0.00029777
533.2 | 257.2 | 130.9178 | 0.0058416 | 130.5174 | 0.0032298 | 0.67706 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.00029777
533.4 | 257.4 | 130.9178 | 0.0058416 | 130.5174 | 0.0032298 | 0.67706 | 0.00061214 | 0.33904 | 0.0017522 | 0.28848 | 0.00029777
533.6 | 257.6 | 131.0152 | 0.0058416 | 130.5174 | 0.0032298 | 0.67706 | 0.0022351 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777
533.8 | 257.8 | 131.0152 | 0.0058416 | 130.5174 | 0.0016062 | 0.67706 | 0.00061214 | 0.33904 | 0.0033759 | 0.38586 | 0.00029777
534 | 258 | 130.8204 | 0.0058416 | 130.42 | 0.0032298 | 0.67706 | 0.00061214 | 0.43642 | 0.0017522 | 0.38586 | 0.0019208
534.2 | 258.2 | 130.9178 | 0.0058416 | 130.5174 | 0.0032298 | 0.67706 | 0.00061214 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777
534.4 | 258.4 | 130.9178 | 0.0058416 | 130.42 | 0.0032298 | 0.77444 | -0.0010109 | 0.43642 | 0.0017522 | 0.38586 | 0.00029777
534.6 | 258.6 | 130.8204 | 0.0058416 | 130.5174 | 0.0016062 | 0.77444 | 0.00061214 | 0.33904 | 0.0017522 | 0.38586 | 0.0019208
534.8 | 258.8 | 130.8204 | 0.0074646 | 130.42 | 0.0016062 | 0.87186 | 0.00061214 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777
535 | 259 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.77444 | 0.0022351 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777
535.2 | 259.2 | 130.9178 | 0.0058416 | 130.42 | 0.0032298 | 0.77444 | 0.0022351 | 0.33904 | 0.0017522 | 0.48328 | 0.00029777
535.4 | 259.4 | 130.9178 | 0.0058416 | 130.5174 | 0.0016062 | 0.77444 | 0.00061214 | 0.33904 | 0.00012922 | 0.48328 | 0.00029777
535.6 | 259.6 | 130.9178 | 0.0058416 | 130.5174 | 0.0032298 | 0.77444 | 0.00061214 | 0.43642 | 0.00012922 | 0.58066 | 0.00029777
535.8 | 259.8 | 130.8204 | 0.0058416 | 130.42 | 0.0016062 | 0.87186 | 0.00061214 | 0.33904 | 0.00012922 | 1.0676 | 0.0019208
536 | 260 | 130.8204 | 0.0058416 | 130.42 | 0.0016062 | 0.96924 | 0.00061214 | 0.33904 | 0.0017522 | 1.0676 | 0.00029777
536.2 | 260.2 | 130.8204 | 0.0058416 | 130.42 | 0.0032298 | 0.96924 | 0.00061214 | 0.24166 | 0.0017522 | 1.5546 | 0.0019208
536.4 | 260.4 | 130.723 | 0.0058416 | 130.2252 | 0.0032298 | 1.0667 | 0.00061214 | 0.046856 | 0.00012922 | 5.1583 | 0.0067905
536.6 | 260.6 | 130.723 | 0.0058416 | 130.3226 | 0.0097225 | 1.164 | 0.00061214 | 0.33904 | 0.0017522 | 6.7167 | 0.0067905
536.8 | 260.8 | 130.3334 | 0.0058416 | 129.933 | 0.060044 | 1.0667 | 0.00061214 | 0.33904 | 0.0017522 | 8.8594 | 0.058735
537 | 261 | 129.8464 | 0.0058416 | 129.4461 | 0.14445 | 0.96924 | 0.00061214 | 0.33904 | 0.00012922 | 18.4042 | 0.1399
537.2 | 261.2 | 129.3595 | 0.0058416 | 128.9591 | 0.22075 | 0.87186 | 0.00061214 | 0.33904 | 0.00012922 | 29.7022 | 0.17074
537.4 | 261.4 | 129.8464 | 0.0058416 | 129.5434 | 0.18828 | 1.0667 | -0.0010109 | 0.33904 | 0.00012922 | 28.1439 | 0.20321
537.6 | 261.6 | 130.5282 | 0.0058416 | 130.2252 | 0.056798 | 1.7484 | 0.00061214 | 0.63122 | 0.00012922 | 7.9828 | 0.079838
537.8 | 261.8 | 130.723 | 0.0042186 | 130.3226 | 0.017839 | 1.2614 | 0.00061214 | 0.53384 | 0.00012922 | 2.9182 | 0.019777
538 | 262 | 130.0412 | 0.0058416 | 129.6409 | 0.14283 | 1.3588 | 0.00061214 | 0.43642 | 0.00012922 | 90.8673 | 0.15451
538.2 | 262.2 | 130.3334 | 0.0058416 | 122.2387 | 0.071407 | 7.0078 | 0.00061214 | 1.4104 | 0.0082456 | 58.629 | 0.22918
538.4 | 262.4 | 129.8464 | 0.0058416 | 129.7382 | 0.022709 | 1.5536 | 0.00061214 | 0.53384 | 0.011492 | 7.6906 | 0.074968
538.6 | 262.6 | 130.723 | 0.0058416 | 130.42 | 0.011346 | 1.2614 | 0.00061214 | 0.43642 | 0.00012922 | 4.7687 | 0.010037
538.8 | 262.8 | 130.723 | 0.0058416 | 130.42 | 0.0080995 | 1.164 | 0.00061214 | 0.33904 | 0.0017522 | 2.7234 | 0.0051674
539 | 263 | 130.5282 | 0.0058416 | 130.2252 | 0.011346 | 1.164 | 0.0022351 | 0.33904 | 0.0017522 | 7.4958 | 0.048996
539.2 | 263.2 | 130.6256 | 0.0058416 | 130.2252 | 0.030826 | 1.2614 | 0.00061214 | 0.24166 | 0.00012922 | 6.7167 | 0.027894
539.4 | 263.4 | 130.723 | 0.0058416 | 130.42 | 0.012969 | 1.2614 | 0.00061214 | 0.33904 | 0.00012922 | 2.2364 | 0.013284
539.6 | 263.6 | 130.723 | 0.0074646 | 130.3226 | 0.0097225 | 0.87186 | 0.00061214 | 0.33904 | 0.0033759 | 2.7234 | 0.12367
539.8 | 263.8 | 130.723 | 0.0058416 | 130.3226 | 0.0048528 | 1.2614 | 0.00061214 | 0.43642 | 0.00012922 | 2.2364 | 0.0035444
540 | 264 | 130.723 | 0.0074646 | 130.3226 | 0.0048528 | 1.2614 | 0.00061214 | 0.33904 | 0.0017522 | 1.4572 | 0.013284
540.2 | 264.2 | 130.6256 | 0.0074646 | 130.3226 | 0.0048528 | 1.9432 | 0.00061214 | 0.33904 | 0.00012922 | 1.7494 | 0.00029777
540.4 | 264.4 | 130.9178 | 0.0058416 | 130.3226 | 0.0048528 | 2.138 | 0.00061214 | 0.33904 | 0.0017522 | 4.0869 | 0.053866
540.6 | 264.6 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 2.5276 | 0.00061214 | 0.33904 | 0.00012922 | 7.2036 | 0.00029777
540.8 | 264.8 | 130.5282 | 0.0058416 | 130.2252 | 0.0064758 | 2.625 | 0.00061214 | 0.24166 | 0.00012922 | 1.5546 | 0.0019208
541 | 265 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 2.8198 | 0.00061214 | 0.33904 | 0.0033759 | 1.5546 | 0.019777
541.2 | 265.2 | 130.5282 | 0.0058416 | 130.3226 | 0.0032298 | 1.3588 | 0.00061214 | 0.33904 | 0.00012922 | 1.5546 | 0.0019208
541.4 | 265.4 | 130.6256 | 0.0058416 | 130.2252 | 0.0048528 | 1.8458 | -0.0010109 | 0.33904 | 0.0017522 | 0.77546 | 0.0019208
541.6 | 265.6 | 130.6256 | 0.0058416 | 130.2252 | 0.0032298 | 1.5536 | 0.00061214 | 0.24166 | 0.00012922 | 0.38586 | 0.00029777
541.8 | 265.8 | 130.5282 | 0.0058416 | 130.2252 | 0.0032298 | 2.625 | 0.00061214 | 0.33904 | 0.0017522 | 0.67808 | 0.024647
542 | 266 | 130.5282 | 0.0042186 | 130.1278 | 0.0032298 | 1.4562 | 0.00061214 | 0.24166 | 0.00012922 | 3.2104 | 0.0019208
542.2 | 266.2 | 130.4308 | 0.0058416 | 130.2252 | 0.0032298 | 1.5536 | 0.00061214 | 0.24166 | 0.00012922 | 5.0609 | 0.0067905
542.4 | 266.4 | 130.6256 | 0.0058416 | 130.3226 | 0.0032298 | 1.651 | 0.00061214 | 0.24166 | 0.00012922 | 2.9182 | 0.00029777
542.6 | 266.6 | 130.5282 | 0.0058416 | 130.1278 | 0.0032298 | 1.4562 | 0.0022351 | 0.43642 | 0.0033759 | 3.113 | 0.12042
542.8 | 266.8 | 130.3334 | 0.0042186 | 130.0304 | 0.0097225 | 2.0406 | 0.00061214 | 1.8974 | 0.00012922 | 2.3338 | 0.00029777
543 | 267 | 130.236 | 0.0058416 | 129.933 | 0.045435 | 2.0406 | -0.0010109 | 5.8906 | 0.017985 | 4.2817 | 0.00029777
543.2 | 267.2 | 130.6256 | 0.0058416 | 130.3226 | 0.019463 | 2.0406 | 0.00061214 | 1.8974 | 0.013115 | 1.8468 | 0.00029777
543.4 | 267.4 | 130.6256 | 0.0058416 | 130.3226 | 0.011346 | 2.2354 | 0.00061214 | 1.0208 | 0.0049989 | 2.9182 | 0.00029777
543.6 | 267.6 | 130.6256 | 0.0058416 | 130.3226 | 0.0080995 | 2.3328 | 0.0022351 | 0.53384 | 0.0033759 | 1.8468 | 0.00029777
543.8 | 267.8 | 130.6256 | 0.0058416 | 130.3226 | 0.0064758 | 2.3328 | 0.00061214 | 0.43642 | 0.0017522 | 2.626 | 0.0019208
544 | 268 | 130.4308 | 0.0074646 | 130.1278 | 0.030826 | 2.8198 | 0.00061214 | 0.33904 | 0.0017522 | 8.3724 | 0.0214
544.2 | 268.2 | 130.236 | 0.0058416 | 129.933 | 0.063291 | 2.7224 | 0.00061214 | 0.43642 | 0.00012922 | 12.5604 | 0.066852
544.4 | 268.4 | 130.4308 | 0.0058416 | 130.2252 | 0.024332 | 2.4302 | 0.00061214 | 0.33904 | 0.0017522 | 7.3984 | 0.013284
544.6 | 268.6 | 130.5282 | 0.0058416 | 130.0304 | 0.012969 | 1.651 | 0.00061214 | 0.33904 | 0.0017522 | 2.7234 | 0.091201
544.8 | 268.8 | 130.4308 | 0.0058416 | 130.2252 | 0.0080995 | 2.625 | 0.00061214 | 0.33904 | 0.0017522 | 4.7687 | 0.0084141
545 | 269 | 130.5282 | 0.0074646 | 130.2252 | 0.0064758 | 2.2354 | 0.00061214 | 0.33904 | 0.00012922 | 5.1583 | 0.0051674
545.2 | 269.2 | 130.5282 | 0.0058416 | 130.3226 | 0.0064758 | 2.2354 | 0.00061214 | 0.24166 | 0.00012922 | 5.7427 | 0.0019208
545.4 | 269.4 | 130.5282 | 0.0058416 | 130.2252 | 0.0064758 | 2.138 | 0.00061214 | 0.33904 | 0.00012922 | 2.7234 | 0.0035444
545.6 | 269.6 | 129.9438 | 0.0058416 | 129.6409 | 0.0097225 | 1.3588 | 0.00061214 | 0.33904 | 0.0017522 | 10.9047 | 0.00029777
545.8 | 269.8 | 130.4308 | 0.0058416 | 130.0304 | 0.043812 | 2.7224 | 0.00061214 | 0.33904 | 0.00012922 | 8.8594 | 0.047373
546 | 270 | 130.5282 | 0.0074646 | 130.2252 | 0.016216 | 2.4302 | 0.00061214 | 0.24166 | 0.00012922 | 2.3338 | 0.014907
546.2 | 270.2 | 130.5282 | 0.0058416 | 130.2252 | 0.0097225 | 2.3328 | 0.00061214 | 0.33904 | 0.00012922 | 2.4312 | 0.0051674
546.4 | 270.4 | 130.4308 | 0.0058416 | 130.2252 | 0.0064758 | 2.5276 | 0.00061214 | 0.24166 | 0.00012922 | 5.4505 | 0.0035444
546.6 | 270.6 | 130.5282 | 0.0058416 | 130.2252 | 0.0080995 | 2.4302 | 0.00061214 | 0.33904 | 0.00012922 | 3.9895 | 0.0051674
546.8 | 270.8 | 130.6256 | 0.0058416 | 130.3226 | 0.0048528 | 2.138 | 0.00061214 | 0.24166 | -0.0014944 | 0.97026 | 0.0035444
547 | 271 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 2.138 | 0.00061214 | 0.24166 | 0.00012922 | 1.2624 | 0.00029777
547.2 | 271.2 | 130.5282 | 0.0058416 | 130.3226 | 0.0048528 | 2.4302 | -0.0010109 | 0.24166 | 0.0017522 | 2.626 | 0.0051674
547.4 | 271.4 | 130.5282 | 0.0058416 | 130.2252 | 0.0032298 | 2.4302 | 0.00061214 | 0.24166 | 0.00012922 | 4.0869 | 0.0035444
547.6 | 271.6 | 130.5282 | 0.0042186 | 130.2252 | 0.0048528 | 2.138 | 0.00061214 | 0.24166 | 0.00012922 | 3.7948 | 0.0019208
547.8 | 271.8 | 130.5282 | 0.0058416 | 130.2252 | 0.0032298 | 2.138 | 0.00061214 | 0.33904 | 0.0017522 | 1.0676 | 0.0019208
548 | 272 | 130.4308 | 0.0074646 | 130.1278 | 0.0048528 | 2.2354 | 0.00061214 | 0.33904 | 0.00012922 | 2.8208 | 0.0019208
548.2 | 272.2 | 130.5282 | 0.0074646 | 130.2252 | 0.0064758 | 2.5276 | 0.00061214 | 0.33904 | 0.0017522 | 3.4052 | 0.0051674
548.4 | 272.4 | 130.4308 | 0.0058416 | 130.2252 | 0.0048528 | 2.7224 | 0.00061214 | 0.33904 | 0.00012922 | 0.87284 | 0.0035444
548.6 | 272.6 | 130.5282 | 0.0058416 | 130.3226 | 0.0048528 | 2.3328 | -0.0010109 | 0.33904 | 0.00012922 | 0.38586 | 0.03601
548.8 | 272.8 | 130.4308 | 0.0058416 | 130.2252 | 0.0048528 | 2.7224 | 0.00061214 | 0.24166 | 0.00012922 | 0.87284 | 0.0035444
549 | 273 | 130.5282 | 0.0058416 | 130.3226 | 0.0048528 | 3.0146 | 0.00061214 | 0.33904 | 0.00012922 | 0.38586 | 0.00029777
549.2 | 273.2 | 130.6256 | 0.0058416 | 130.3226 | 0.0048528 | 3.2094 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777
549.4 | 273.4 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 3.2094 | 0.00061214 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777
549.6 | 273.6 | 130.5282 | 0.0058416 | 130.3226 | 0.0032298 | 3.5016 | 0.00061214 | 0.33904 | 0.00012922 | 3.6 | 0.0035444
549.8 | 273.8 | 130.5282 | 0.0058416 | 130.2252 | 0.0032298 | 3.599 | 0.00061214 | 0.53384 | 0.00012922 | 1.3598 | 0.00029777
550 | 274 | 130.5282 | 0.0058416 | 130.2252 | 0.0032298 | 3.7938 | 0.00061214 | 0.53384 | 0.00012922 | 1.9442 | 0.00029777
550.2 | 274.2 | 130.5282 | 0.0042186 | 130.2252 | 0.0048528 | 3.599 | 0.00061214 | 0.53384 | 0.00012922 | 0.58066 | -0.0013259
550.4 | 274.4 | 130.5282 | -0.00065172 | 130.5174 | 0.0032298 | 1.8458 | 0.0022351 | 0.14424 | 0.0049989 | 2.5286 | 0.67396
550.6 | 274.6 | 130.5282 | 0.0058416 | 130.6148 | 0.0048528 | 3.8911 | 0.00061214 | 0.82602 | 0.00012922 | 1.5546 | 0.027894
550.8 | 274.8 | 130.4308 | 0.0058416 | 130.3226 | 0.0064758 | 4.3781 | 0.00061214 | 0.33904 | 0.00012922 | 2.2364 | 0.0019208
551 | 275 | 130.5282 | 0.0074646 | 130.1278 | 0.0064758 | 4.6703 | 0.00061214 | 0.33904 | 0.00012922 | 1.7494 | 0.0019208
551.2 | 275.2 | 130.4308 | 0.0058416 | 130.1278 | 0.0064758 | 4.7677 | 0.00061214 | 0.63122 | 0.0033759 | 1.4572 | 0.0019208
551.4 | 275.4 | 130.4308 | 0.0058416 | 130.2252 | 0.0064758 | 5.0599 | 0.00061214 | 0.63122 | 0.00012922 | 1.7494 | 0.0067905
551.6 | 275.6 | 130.5282 | 0.0074646 | 130.3226 | 0.0048528 | 5.4495 | 0.00061214 | 0.43642 | 0.00012922 | 1.4572 | 0.0019208
551.8 | 275.8 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 5.3521 | 0.00061214 | 0.33904 | 0.0017522 | 2.626 | 0.0035444
552 | 276 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 5.5469 | -0.0010109 | 0.33904 | 0.00012922 | 2.3338 | 0.00029777
552.2 | 276.2 | 130.5282 | 0.0058416 | 130.2252 | 0.0048528 | 5.9365 | 0.00061214 | 0.24166 | 0.00012922 | 1.3598 | 0.0019208
552.4 | 276.4 | 130.5282 | 0.0058416 | 130.1278 | 0.0048528 | 5.9365 | -0.0010109 | 0.43642 | 0.00012922 | 1.652 | 0.00029777
552.6 | 276.6 | 130.5282 | 0.0058416 | 130.1278 | 0.0048528 | 6.5208 | 0.00061214 | 0.72864 | 0.00012922 | 2.2364 | 0.00029777
552.8 | 276.8 | 130.5282 | 0.0058416 | 130.0304 | 0.0048528 | 6.5208 | -0.0010109 | 0.63122 | 0.0033759 | 0.77546 | 0.00029777
553 | 277 | 130.5282 | 0.0058416 | 130.1278 | 0.0048528 | 6.8131 | 0.00061214 | 0.82602 | 0.00012922 | 2.139 | -0.0013259
553.2 | 277.2 | 130.3334 | 0.0058416 | 130.1278 | 0.0048528 | 7.2026 | 0.0054818 | 0.82602 | 0.024478 | 1.5546 | 0.00029777
553.4 | 277.4 | 130.3334 | 0.0074646 | 130.1278 | 0.0048528 | 9.3453 | 0.00061214 | 0.82602 | 0.00012922 | 0.87284 | 0.0019208
553.6 | 277.6 | 130.4308 | 0.0058416 | 130.1278 | 0.0064758 | 14.7022 | 0.00061214 | 0.43642 | 0.00012922 | 1.5546 | 0.00029777
553.8 | 277.8 | 130.4308 | 0.0058416 | 130.0304 | 0.0080995 | 16.8449 | 0.00061214 | 0.63122 | 0.0017522 | 1.1651 | 0.00029777
554 | 278 | 130.3334 | 0.0058416 | 130.0304 | 0.0097225 | 18.5006 | 0.00061214 | 0.63122 | -0.0031175 | 1.5546 | 0.0084141
554.2 | 278.2 | 130.3334 | 0.0058416 | 130.1278 | 0.014592 | 21.2277 | 0.00061214 | 0.82602 | 0.00012922 | 2.9182 | 0.0035444
554.4 | 278.4 | 130.3334 | 0.0058416 | 130.0304 | 0.019463 | 22.4939 | 0.00061214 | 1.1182 | 0.00012922 | 1.5546 | 0.00029777
554.6 | 278.6 | 130.236 | 0.0058416 | 129.933 | 0.025955 | 25.221 | 0.00061214 | 0.9234 | 0.00012922 | 2.2364 | 0.00029777
554.8 | 278.8 | 130.236 | 0.0074646 | 129.933 | 0.035695 | 25.8054 | 0.0022351 | 0.9234 | 0.00012922 | 4.4765 | 0.0019208
555 | 279 | 130.236 | 0.0074646 | 129.933 | 0.038942 | 29.6038 | 0.00061214 | 0.72864 | 0.00012922 | 2.626 | 0.0067905
555.2 | 279.2 | 130.3334 | 0.0058416 | 129.933 | 0.038942 | 33.3049 | 0.013598 | 1.6052 | 0.1024 | 5.2557 | 0.013284
555.4 | 279.4 | 130.236 | 0.0042186 | 129.933 | 0.038942 | 38.4669 | 0.0054818 | 1.7026 | 0.017985 | 1.652 | 0.0051674
555.6 | 279.6 | 129.9438 | 0.0058416 | 129.6409 | 0.076277 | 30.6752 | 0.0071055 | 4.9167 | 0.0033759 | 1.5546 | 0.0067905
555.8 | 279.8 | 129.749 | 0.0058416 | 129.4461 | 0.13147 | 29.1169 | 0.0071055 | 9.4943 | 0.074799 | 2.2364 | 0.011661
556 | 280 | 129.8464 | 0.0058416 | 129.6409 | 0.10874 | 31.4543 | 0.0054818 | 1.6052 | 0.016362 | 9.1516 | 0.074968
556.2 | 280.2 | 129.8464 | 0.0058416 | 129.5434 | 0.063291 | 32.7205 | 0.0071055 | 0.43642 | 0.0033759 | 5.2557 | 0.032763
556.4 | 280.4 | 130.0412 | 0.0058416 | 129.7382 | 0.081147 | 34.2789 | 0.0071055 | 0.24166 | 0.0017522 | 6.2297 | 0.052243
556.6 | 280.6 | 129.9438 | 0.0058416 | 129.7382 | 0.066537 | 38.0773 | 0.0087285 | 0.14424 | 0.00012922 | 4.1843 | 0.032763
556.8 | 280.8 | 130.236 | 0.0058416 | 129.933 | 0.037318 | 40.0253 | 0.011975 | 0.24166 | 0.00012922 | 1.9442 | 0.013284
557 | 281 | 130.236 | 0.0058416 | 129.933 | 0.029202 | 40.707 | 0.011975 | 0.33904 | 0.00012922 | 0.77546 | 0.0051674
557.2 | 281.2 | 130.1386 | 0.0042186 | 129.933 | 0.024332 | 41.194 | 0.013598 | 0.33904 | 0.0017522 | 0.87284 | 0.0019208
557.4 | 281.4 | 130.236 | 0.0042186 | 130.0304 | 0.027579 | 41.681 | 0.013598 | 0.63122 | 0.00012922 | 0.58066 | 0.00029777
557.6 | 281.6 | 130.1386 | 0.0058416 | 129.8357 | 0.050304 | 43.7263 | 0.015222 | 0.33904 | 0.00012922 | 3.5025 | 0.0051674
557.8 | 281.8 | 130.236 | 0.0058416 | 129.933 | 0.032449 | 44.8951 | 0.015222 | 0.33904 | 0.00012922 | 0.97026 | 0.0019208
558 | 282 | 130.0412 | 0.0058416 | 129.7382 | 0.032449 | 44.0185 | 0.015222 | 0.63122 | 0.0033759 | 2.8208 | 0.21457
558.2 | 282.2 | 130.0412 | 0.0074646 | 129.7382 | 0.060044 | 45.5768 | 0.015222 | 0.9234 | 0.00012922 | 5.2557 | 0.011661
558.4 | 282.4 | 130.1386 | 0.0058416 | 129.8357 | 0.056798 | 45.5768 | 0.016845 | 0.63122 | 0.00012922 | 4.1843 | 0.01653
558.6 | 282.6 | 130.1386 | 0.0058416 | 129.8357 | 0.047058 | 46.843 | 0.016845 | 1.5078 | 0.0098686 | 2.7234 | 0.0084141
558.8 | 282.8 | 130.236 | 0.0058416 | 130.0304 | 0.038942 | 46.7456 | 0.018468 | 1.7026 | 0.0017522 | 1.652 | 0.0051674
559 | 283 | 130.236 | 0.0042186 | 129.933 | 0.037318 | 48.6935 | 0.018468 | 1.1182 | 0.0017522 | 1.2624 | 0.0019208
559.2 | 283.2 | 130.1386 | 0.0058416 | 130.0304 | 0.042188 | 48.4014 | 0.018468 | 2.4818 | 0.0033759 | 1.0676 | 0.00029777
559.4 | 283.4 | 130.236 | 0.0058416 | 130.0304 | 0.037318 | 48.0118 | 0.016845 | 1.7026 | 0.0033759 | 0.77546 | 0.00029777
559.6 | 283.6 | 129.6516 | 0.0058416 | 129.3486 | 0.10712 | 48.2066 | 0.020092 | 11.15 | 0.037464 | 0.87284 | 0.00029777
559.8 | 283.8 | 130.0412 | 0.0074646 | 129.7382 | 0.097379 | 49.2779 | 0.018468 | 7.1568 | 0.066683 | 0.77546 | 0.00029777
560 | 284 | 130.1386 | 0.0058416 | 129.933 | 0.042188 | 49.6675 | 0.020092 | 1.313 | 0.013115 | 0.58066 | 0.00029777
560.2 | 284.2 | 130.1386 | 0.0058416 | 129.933 | 0.047058 | 50.9337 | 0.020092 | 0.43642 | 0.0049989 | 1.652 | 0.00029777
560.4 | 284.4 | 129.9438 | 0.0058416 | 129.7382 | 0.090887 | 53.2712 | 0.021715 | 1.313 | 0.0049989 | 6.3271 | 0.011661
560.6 | 284.6 | 130.1386 | 0.0074646 | 129.933 | 0.063291 | 52.005 | 0.021715 | 1.0208 | 0.0033759 | 5.5479 | 0.01653
560.8 | 284.8 | 129.9438 | 0.0058416 | 129.7382 | 0.089263 | 50.6415 | 0.021715 | 1.5078 | 0.0049989 | 5.3531 | 0.03601
561 | 285 | 129.8464 | 0.0058416 | 129.6409 | 0.11037 | 50.5441 | 0.021715 | 0.43642 | 0.0033759 | 8.1776 | 0.066852
561.2 | 285.2 | 130.0412 | 0.0058416 | 129.8357 | 0.089263 | 53.466 | 0.021715 | 0.53384 | 0.0017522 | 6.3271 | 0.047373
561.4 | 285.4 | 130.236 | 0.0058416 | 129.933 | 0.047058 | 54.5374 | 0.023338 | 0.53384 | 0.00012922 | 1.1651 | 0.011661
561.6 | 285.6 | 130.1386 | 0.0058416 | 129.933 | 0.051928 | 54.1478 | 0.021715 | 0.63122 | 0.00012922 | 1.1651 | 0.0051674
561.8 | 285.8 | 129.9438 | 0.0058416 | 129.7382 | 0.074653 | 53.953 | 0.021715 | 0.63122 | 0.00012922 | 4.1843 | 0.014907
562 | 286 | 129.9438 | 0.0074646 | 129.7382 | 0.0779 | 53.5634 | 0.023338 | 1.8974 | 0.0033759 | 3.8921 | 0.018153
562.2 | 286.2 | 130.236 | 0.0058416 | 129.933 | 0.055175 | 56.8748 | 0.023338 | 1.1182 | 0.0033759 | 1.4572 | 0.0084141
562.4 | 286.4 | 129.8464 | 0.0058416 | 129.5434 | 0.11199 | 57.2644 | 0.024961 | 0.82602 | 0.0017522 | 10.0281 | 0.050619
562.6 | 286.6 | 130.1386 | 0.0058416 | 129.933 | 0.063291 | 55.4139 | 0.024961 | 0.53384 | 0.0017522 | 2.4312 | 0.019777
562.8 | 286.8 | 129.4568 | 0.0058416 | 129.3486 | 0.13958 | 55.6087 | 0.024961 | 0.72864 | 0.0017522 | 13.3396 | 0.070098
563 | 287 | 129.6516 | 0.0058416 | 129.4461 | 0.13958 | 57.7514 | 0.024961 | 0.53384 | 0.0017522 | 10.3203 | 0.087955
563.2 | 287.2 | 129.9438 | 0.0058416 | 129.7382 | 0.09251 | 62.7187 | 0.028208 | 0.43642 | 0.00012922 | 5.0609 | 0.039257
563.4 | 287.4 | 130.0412 | 0.0058416 | 129.8357 | 0.064914 | 60.9655 | 0.028208 | 0.9234 | 0.00012922 | 1.2624 | 0.010037
563.6 | 287.6 | 130.1386 | 0.0058416 | 129.933 | 0.055175 | 59.7968 | 0.026584 | 0.82602 | 0.00012922 | 0.38586 | 0.0035444
563.8 | 287.8 | 130.1386 | 0.0058416 | 129.933 | 0.051928 | 62.1343 | 0.029831 | 0.24166 | 0.00012922 | 0.28848 | 0.0019208
564 | 288 | 130.0412 | 0.0058416 | 129.8357 | 0.050304 | 61.6473 | 0.028208 | 0.24166 | 0.00012922 | 0.28848 | 0.00029777
564.2 | 288.2 | 130.1386 | 0.0058416 | 129.933 | 0.050304 | 61.9395 | 0.029831 | 0.33904 | 0.00012922 | 0.19109 | 0.00029777
564.4 | 288.4 | 129.9438 | 0.0074646 | 129.7382 | 0.071407 | 61.8421 | 0.028208 | 1.1182 | 0.00012922 | 1.0676 | 0.0067905
564.6 | 288.6 | 130.0412 | 0.0042186 | 129.8357 | 0.058421 | 62.7187 | 0.028208 | 0.33904 | 0.00012922 | 0.58066 | 0.00029777
564.8 | 288.8 | 130.0412 | 0.0058416 | 129.7382 | 0.064914 | 63.4978 | 0.029831 | 0.33904 | 0.0017522 | 0.38586 | 0.00029777
565 | 289 | 129.9438 | 0.0058416 | 129.7382 | 0.071407 | 63.4978 | 0.031455 | 0.53384 | 0.00012922 | 0.77546 | 0.0019208
565.2 | 289.2 | 129.9438 | 0.0058416 | 129.7382 | 0.081147 | 63.79 | 0.029831 | 2.8714 | 0.0049989 | 0.87284 | 0.00029777
565.4 | 289.4 | 130.0412 | 0.0058416 | 129.7382 | 0.060044 | 64.5692 | 0.031455 | 0.43642 | 0.0017522 | 0.77546 | 0.00029777
565.6 | 289.6 | 130.0412 | 0.0058416 | 129.933 | 0.064914 | 65.1536 | 0.031455 | 0.24166 | 0.00012922 | 1.4572 | 0.0051674
565.8 | 289.8 | 129.8464 | 0.0074646 | 129.6409 | 0.08277 | 67.1015 | 0.031455 | 0.33904 | 0.00012922 | 3.9895 | 0.011661
566 | 290 | 129.749 | 0.0058416 | 129.5434 | 0.094133 | 70.9973 | 0.034701 | 0.24166 | 0.00012922 | 5.0609 | 0.032763
566.2 | 290.2 | 129.3595 | 0.0058416 | 129.1539 | 0.14932 | 89.3079 | 0.046064 | 0.33904 | 0.00012922 | 11.2943 | 0.078215
566.4 | 290.4 | 129.4568 | 0.0074646 | 129.2513 | 0.13472 | 94.3725 | 0.052557 | 0.24166 | 0.00012922 | 10.5151 | 0.065229
566.6 | 290.6 | 129.0672 | 0.0058416 | 128.8617 | 0.20452 | 94.6647 | 0.052557 | 0.24166 | 0.00012922 | 18.8912 | 0.13016
566.8 | 290.8 | 128.5803 | 0.0074646 | 128.2773 | 0.27594 | 94.4699 | 0.050934 | 0.33904 | 0.00012922 | 27.1699 | 0.20645
567 | 291 | 128.9699 | 0.0058416 | 128.7643 | 0.22562 | 95.0543 | 0.052557 | 0.33904 | 0.00012922 | 19.086 | 0.161
567.2 | 291.2 | 129.5542 | 0.0058416 | 129.3486 | 0.11686 | 99.6319 | 0.05418 | 0.33904 | 0.0017522 | 8.9568 | 0.0214
567.4 | 291.4 | 129.8464 | 0.0074646 | 129.5434 | 0.0779 | 100.5085 | 0.055804 | 0.24166 | 0.0017522 | 1.8468 | 0.018153
567.6 | 291.6 | 129.5542 | 0.0058416 | 129.4461 | 0.1055 | 100.8981 | 0.055804 | 3.7479 | 0.0017522 | 0.48328 | 0.0051674
567.8 | 291.8 | 129.749 | 0.0058416 | 129.6409 | 0.090887 | 100.4111 | 0.055804 | 2.8714 | 0.019609 | 0.38586 | 0.01653
568 | 292 | 129.4568 | 0.0058416 | 129.2513 | 0.13796 | 100.5085 | 0.055804 | 2.9687 | 0.0066219 | 16.0667 | 0.027894
568.2 | 292.2 | 129.4568 | 0.0058416 | 129.3486 | 0.12822 | 96.5153 | 0.055804 | 11.7344 | 0.035841 | 2.9182 | 0.018153
568.4 | 292.4 | 129.749 | 0.0058416 | 129.5434 | 0.089263 | 102.7486 | 0.055804 | 3.2609 | 0.024478 | 0.77546 | 0.0051674
568.6 | 292.6 | 128.9699 | 0.0058416 | 128.7643 | 0.17854 | 95.1517 | 0.05418 | 6.2802 | 0.026101 | 7.8854 | 0.0035444
568.8 | 292.8 | 129.1647 | 0.0058416 | 128.9591 | 0.17854 | 103.0408 | 0.057427 | 2.0922 | 0.021232 | 16.6511 | 0.092824
569 | 293 | 129.1647 | 0.0058416 | 128.9591 | 0.18828 | 104.0148 | 0.05905 | 5.7933 | 0.021232 | 17.0407 | 0.053866
569.2 | 293.2 | 129.1647 | 0.002595 | 128.9591 | 0.19478 | 104.4044 | 0.05905 | 1.1182 | 0.0082456 | 17.7225 | 0.10256
569.4 | 293.4 | 128.8725 | 0.0058416 | 128.8617 | 0.16718 | 104.4044 | 0.05905 | 0.63122 | 0.0066219 | 19.7678 | 0.089578
569.6 | 293.6 | 129.1647 | 0.0074646 | 129.1539 | 0.15744 | 104.6966 | 0.05905 | 0.24166 | 0.0017522 | 17.7225 | 0.091201
569.8 | 293.8 | 129.262 | 0.0074646 | 128.8617 | 0.18666 | 104.5018 | 0.060673 | 0.72864 | 0.0017522 | 21.3261 | 0.096071
570 | 294 | 128.9699 | 0.0058416 | 128.7643 | 0.2175 | 104.5991 | 0.05905 | 0.82602 | 0.0017522 | 25.0272 | 0.12204
570.2 | 294.2 | 129.5542 | 0.0058416 | 129.1539 | 0.15095 | 105.2809 | 0.060673 | 0.33904 | 0.00012922 | 15.9693 | 0.01653
570.4 | 294.4 | 129.0672 | 0.0058416 | 128.7643 | 0.18666 | 104.9887 | 0.05905 | 0.53384 | 0.0017522 | 20.6444 | 0.091201
570.6 | 294.6 | 129.262 | 0.0058416 | 128.9591 | 0.18666 | 105.2809 | 0.05905 | 1.1182 | 0.0017522 | 20.06 | 0.1188
570.8 | 294.8 | 129.1647 | 0.0058416 | 128.8617 | 0.19802 | 105.0862 | 0.05905 | 0.24166 | 0.00012922 | 23.1766 | 0.11393
571 | 295 | 129.262 | 0.0058416 | 128.9591 | 0.20452 | 105.2809 | 0.05905 | 0.43642 | 0.00012922 | 24.5402 | 0.13016
571.2 | 295.2 | 129.3595 | 0.0058416 | 128.5695 | 0.2386 | 105.6705 | 0.060673 | 1.9948 | 0.0017522 | 27.6569 | 0.13341
571.4 | 295.4 | 129.5542 | 0.0058416 | 128.8617 | 0.22886 | 105.7679 | 0.060673 | 1.313 | 0.0017522 | 29.5074 | 0.074968
571.6 | 295.6 | 129.6516 | 0.0058416 | 128.9591 | 0.23373 | 104.8914 | 0.05905 | 0.82602 | 0.00012922 | 29.3126 | 0.15451
571.8 | 295.8 | 129.9438 | 0.0058416 | 129.1539 | 0.19315 | 103.7226 | 0.05905 | 0.43642 | 0.0017522 | 23.1766 | 0.091201
572 | 296 | 129.8464 | 0.0058416 | 128.6669 | 0.22075 | 103.82 | 0.060673 | 0.72864 | 0.0017522 | 24.3454 | 0.13016
572.2 | 296.2 | 129.749 | 0.0058416 | 128.5695 | 0.13958 | 101.4824 | 0.05905 | 0.43642 | 0.00012922 | 12.2682 | 0.052243
572.4 | 296.4 | 129.8464 | 0.0058416 | 128.4721 | 0.19478 | 46.3561 | 0.033078 | 13.2928 | 0.076423 | 10.3203 | 0.039257
572.6 | 296.6 | 129.6516 | 0.0058416 | 128.8617 | 0.14445 | 14.3126 | 0.0087285 | 6.0854 | 0.047204 | 14.6058 | 0.045749
572.8 | 296.8 | 129.5542 | 0.0058416 | 128.9591 | 0.15744 | 18.3059 | 0.0022351 | 9.7865 | 0.061813 | 16.3589 | 0.052243
573 | 297 | 128.3855 | 0.0058416 | 127.9851 | 0.30354 | 21.5199 | 0.0022351 | 11.15 | 0.084539 | 31.4554 | 0.19347
573.2 | 297.2 | 127.1193 | 0.0074646 | 126.9137 | 0.48859 | 53.466 | 0.0071055 | 39.9794 | 0.28096 | 30.4814 | 0.18373
573.4 | 297.4 | 128.7751 | 0.0058416 | 128.5695 | 0.24672 | 53.2712 | 0.016845 | 11.0527 | 0.078046 | 29.0205 | 0.084708
573.6 | 297.6 | 127.9959 | 0.0058416 | 127.6929 | 0.33113 | 57.0696 | 0.018468 | 17.8704 | 0.081293 | 33.8903 | 0.1123
573.8 | 297.8 | 127.3141 | 0.0058416 | 127.1085 | 0.43827 | 36.7138 | 0.0038588 | 28.584 | 0.17382 | 36.52 | 0.22431
574 | 298 | 127.4115 | 0.0058416 | 127.2059 | 0.43015 | 17.6241 | 0.0087285 | 13.8771 | 0.11051 | 45.3831 | 0.29898
574.2 | 298.2 | 127.5089 | 0.0058416 | 127.3033 | 0.41879 | 25.9028 | 0.0054818 | 20.4027 | 0.15759 | 39.6367 | 0.23243
574.4 | 298.4 | 126.9245 | 0.0058416 | 126.2319 | 0.58599 | 62.4265 | 0.013598 | 58.1926 | 0.32478 | 37.8835 | 0.23892
574.6 | 298.6 | 127.9959 | 0.0074646 | 127.6929 | 0.33925 | 98.5606 | 0.04931 | 107.183 | 0.10077 | 37.3966 | 0.17561
574.8 | 298.8 | 128.0933 | 0.0058416 | 127.8877 | 0.32626 | 97.0996 | 0.055804 | 99.1965 | 0.073176 | 37.4939 | 0.2308
575 | 299 | 127.7037 | 0.0058416 | 127.4981 | 0.37658 | 105.3783 | 0.05905 | 108.157 | 0.076423 | 40.5132 | 0.21457
575.2 | 299.2 | 127.7037 | 0.0058416 | 127.4981 | 0.38145 | 109.5664 | 0.062296 | 112.7346 | 0.07967 | 40.3184 | 0.16262
575.4 | 299.4 | 127.9959 | 0.0058416 | 127.7903 | 0.33113 | 111.5143 | 0.06392 | 114.9747 | 0.082916 | 36.3252 | 0.19509
575.6 | 299.6 | 127.9959 | 0.0074646 | 127.7903 | 0.36197 | 112.2935 | 0.065543 | 115.6565 | 0.082916 | 36.7148 | 0.23567
575.8 | 299.8 | 128.3855 | 0.0058416 | 128.2773 | 0.30029 | 111.2221 | 0.067167 | 116.7279 | 0.086162 | 27.6569 | 0.18048
576 | 300 | 128.2881 | 0.0058416 | 128.1799 | 0.28568 | 111.4169 | 0.06392 | 117.0201 | 0.082916 | 27.1699 | 0.13828
576.2 | 300.2 | 128.4829 | 0.0058416 | 128.2773 | 0.2873 | 111.0273 | 0.06392 | 117.3123 | 0.084539 | 26.7803 | 0.16262
576.4 | 300.4 | 128.3855 | 0.0058416 | 128.1799 | 0.2938 | 110.7351 | 0.062296 | 117.4096 | 0.084539 | 30.384 | 0.15613
576.6 | 300.6 | 128.0933 | 0.0074646 | 127.9851 | 0.34412 | 112.4883 | 0.06392 | 117.7992 | 0.089409 | 35.9356 | 0.22918
576.8 | 300.8 | 128.4829 | 0.0058416 | 128.2773 | 0.2873 | 113.2675 | 0.065543 | 118.968 | 0.087786 | 26.0011 | 0.15289
577 | 301 | 128.6777 | 0.0058416 | 128.5695 | 0.23536 | 117.4555 | 0.06879 | 120.2342 | 0.087786 | 17.2355 | 0.084708
577.2 | 301.2 | 127.8985 | 0.0058416 | 127.6929 | 0.35223 | 117.1633 | 0.06879 | 119.6498 | 0.087786 | 33.5981 | 0.19834
577.4 | 301.4 | 127.9959 | 0.0058416 | 127.7903 | 0.33762 | 117.5529 | 0.06879 | 119.942 | 0.086162 | 33.5981 | 0.19184
577.6 | 301.6 | 127.8985 | 0.0058416 | 127.7903 | 0.38957 | 117.5529 | 0.06879 | 119.8446 | 0.086162 | 88.6271 | 0.26651
577.8 | 301.8 | 128.9699 | 0.0058416 | 128.7643 | 0.23536 | 120.8644 | 0.070413 | 121.8899 | 0.089409 | 121.1576 | 0.10419
578 | 302 | 128.9699 | 0.0058416 | 128.8617 | 0.22724 | 120.9618 | 0.070413 | 121.9873 | 0.089409 | 123.4951 | 0.091201
578.2 | 302.2 | 129.0672 | 0.0058416 | 128.8617 | 0.22562 | 120.9618 | 0.070413 | 122.0847 | 0.089409 | 124.1769 | 0.091201
578.4 | 302.4 | 129.0672 | 0.0058416 | 128.8617 | 0.22562 | 121.0592 | 0.070413 | 122.1821 | 0.089409 | 124.6638 | 0.092824
578.6 | 302.6 | 129.0672 | 0.0058416 | 128.8617 | 0.22562 | 121.0592 | 0.072036 | 122.1821 | 0.089409 | 125.8326 | 0.094447
578.8 | 302.8 | 129.1647 | 0.0058416 | 128.8617 | 0.22724 | 121.1566 | 0.072036 | 122.1821 | 0.091033 | 126.2222 | 0.094447
579 | 303 | 129.1647 | 0.0058416 | 128.8617 | 0.22724 | 121.0592 | 0.072036 | 122.3769 | 0.089409 | 126.3196 | 0.094447
579.2 | 303.2 | 129.1647 | 0.0058416 | 128.9591 | 0.22724 | 121.0592 | 0.070413 | 122.2795 | 0.089409 | 126.2222 | 0.094447
579.4 | 303.4 | 129.0672 | 0.0058416 | 128.8617 | 0.22724 | 121.0592 | 0.072036 | 122.2795 | 0.089409 | 126.2222 | 0.092824
579.6 | 303.6 | 129.0672 | 0.0074646 | 128.8617 | 0.22724 | 121.0592 | 0.072036 | 122.2795 | 0.089409 | 126.1248 | 0.094447
579.8 | 303.8 | 129.0672 | 0.0058416 | 128.8617 | 0.22724 | 121.0592 | 0.072036 | 122.3769 | 0.091033 | 126.2222 | 0.094447
580 | 304 | 128.9699 | 0.0058416 | 128.7643 | 0.22724 | 120.9618 | 0.070413 | 122.2795 | 0.089409 | 126.1248 | 0.092824
590 | 314 | 129.262 | 0.0074646 | 128.8617 | 0.22886 | 122.2279 | 0.072036 | 124.8118 | 0.091033 | 126.904 | 0.092824
600 | 324 | 129.0672 | 0.0058416 | 128.8617 | 0.22562 | 118.5269 | 0.070413 | 121.6951 | 0.086162 | 127.0014 | 0.094447
610 | 334 | 129.0672 | 0.0058416 | 128.8617 | 0.22237 | 112.2935 | 0.065543 | 123.9352 | 0.089409 | 126.8066 | 0.094447
620 | 344 | 129.1647 | 0.0058416 | 128.9591 | 0.22724 | 122.8123 | 0.072036 | 125.8832 | 0.091033 | 127.2936 | 0.094447
630 | 354 | 129.1647 | 0.0058416 | 128.9591 | 0.22724 | 123.2993 | 0.072036 | 126.7597 | 0.092656 | 127.3909 | 0.092824
640 | 364 | 129.3595 | 0.0058416 | 129.1539 | 0.22886 | 125.7342 | 0.073659 | 127.5389 | 0.092656 | 127.6831 | 0.091201
650 | 374 | 129.4568 | 0.0058416 | 129.1539 | 0.22886 | 127.5847 | 0.075283 | 127.9285 | 0.092656 | 127.8779 | 0.092824
660 | 384 | 129.4568 | 0.0058416 | 129.1539 | 0.22886 | 128.0717 | 0.075283 | 128.1233 | 0.094279 | 128.1701 | 0.094447
670 | 394 | 129.3595 | 0.0058416 | 128.9591 | 0.22886 | 128.0717 | 0.076906 | 128.1233 | 0.094279 | 128.2675 | 0.094447
680 | 404 | 129.8464 | 0.0058416 | 128.7643 | 0.22724 | 128.1691 | 0.076906 | 128.1233 | 0.094279 | 128.3649 | 0.094447
690 | 414 | 129.4568 | 0.0074646 | 129.2513 | 0.22724 | 128.7535 | 0.075283 | 128.7076 | 0.094279 | 128.9493 | 0.094447
700 | 424 | 129.4568 | 0.0074646 | 129.3486 | 0.22724 | 128.7535 | 0.075283 | 128.6103 | 0.094279 | 128.8519 | 0.094447
710 | 434 | 129.749 | 0.0074646 | 129.4461 | 0.22562 | 129.0457 | 0.076906 | 128.8051 | 0.094279 | 129.1441 | 0.096071
720 | 444 | 129.3595 | 0.0074646 | 129.1539 | 0.22562 | 128.8509 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
730 | 454 | 129.1647 | 0.0074646 | 129.0565 | 0.224 | 128.5587 | 0.075283 | 128.4155 | 0.094279 | 128.6571 | 0.094447
740 | 464 | 129.4568 | 0.0090883 | 129.1539 | 0.224 | 128.7535 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
750 | 474 | 129.262 | 0.0090883 | 129.0565 | 0.224 | 128.6561 | 0.076906 | 128.5129 | 0.094279 | 128.7545 | 0.094447
760 | 484 | 129.3595 | 0.010711 | 129.1539 | 0.22237 | 128.8509 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
770 | 494 | 129.3595 | 0.010711 | 129.1539 | 0.22237 | 128.7535 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
780 | 504 | 129.749 | 0.012335 | 129.4461 | 0.22075 | 129.2405 | 0.076906 | 128.9999 | 0.094279 | 129.2415 | 0.094447
790 | 514 | 130.1386 | 0.013958 | 129.7382 | 0.22075 | 129.6301 | 0.076906 | 129.292 | 0.094279 | 129.5337 | 0.094447
800 | 524 | 129.9438 | 0.015581 | 129.6409 | 0.21913 | 129.5326 | 0.076906 | 129.1946 | 0.094279 | 129.5337 | 0.094447
810 | 534 | 129.5542 | 0.015581 | 129.2513 | 0.2175 | 128.9483 | 0.076906 | 128.8051 | 0.094279 | 129.0467 | 0.094447
820 | 544 | 129.4568 | 0.018828 | 129.2513 | 0.21588 | 128.8509 | 0.076906 | 128.7076 | 0.094279 | 129.0467 | 0.096071
830 | 554 | 129.3595 | 0.020451 | 129.1539 | 0.21426 | 128.7535 | 0.076906 | 128.5129 | 0.094279 | 128.8519 | 0.094447
840 | 564 | 129.3595 | 0.020451 | 129.1539 | 0.21263 | 128.8509 | 0.076906 | 128.7076 | 0.094279 | 128.8519 | 0.094447
850 | 574 | 129.262 | 0.022074 | 129.1539 | 0.21426 | 128.7535 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
860 | 584 | 129.3595 | 0.020451 | 129.1539 | 0.21426 | 128.7535 | 0.076906 | 128.5129 | 0.094279 | 128.8519 | 0.094447
870 | 594 | 129.3595 | 0.020451 | 129.0565 | 0.21426 | 128.7535 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
880 | 604 | 129.262 | 0.022074 | 129.0565 | 0.21263 | 128.7535 | 0.076906 | 128.5129 | 0.094279 | 128.7545 | 0.094447
890 | 614 | 129.262 | 0.020451 | 129.1539 | 0.21426 | 128.7535 | 0.076906 | 128.7076 | 0.094279 | 128.8519 | 0.092824
900 | 624 | 129.3595 | 0.022074 | 129.1539 | 0.21426 | 128.7535 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
910 | 634 | 129.262 | 0.022074 | 129.1539 | 0.21263 | 128.8509 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
920 | 644 | 129.3595 | 0.022074 | 129.0565 | 0.21263 | 128.9483 | 0.076906 | 128.7076 | 0.094279 | 128.9493 | 0.094447
930 | 654 | 129.4568 | 0.022074 | 129.1539 | 0.21263 | 128.9483 | 0.076906 | 128.7076 | 0.092656 | 129.0467 | 0.094447
940 | 664 | 129.5542 | 0.022074 | 129.2513 | 0.21263 | 129.0457 | 0.076906 | 128.8051 | 0.094279 | 129.1441 | 0.094447
950 | 674 | 129.5542 | 0.022074 | 129.2513 | 0.21426 | 129.0457 | 0.076906 | 128.8051 | 0.094279 | 129.0467 | 0.094447
960 | 684 | 129.262 | 0.020451 | 129.0565 | 0.21426 | 128.7535 | 0.076906 | 128.6103 | 0.092656 | 128.7545 | 0.094447
970 | 694 | 129.1647 | 0.020451 | 129.0565 | 0.21426 | 128.6561 | 0.076906 | 128.5129 | 0.094279 | 128.6571 | 0.094447
980 | 704 | 129.5542 | 0.020451 | 129.2513 | 0.21426 | 129.0457 | 0.076906 | 128.8051 | 0.094279 | 129.0467 | 0.094447
990 | 714 | 130.0412 | 0.020451 | 129.6409 | 0.21426 | 129.6301 | 0.076906 | 129.292 | 0.094279 | 129.631 | 0.094447
1000 | 724 | 130.723 | 0.022074 | 130.1278 | 0.21426 | 130.3118 | 0.078529 | 129.8764 | 0.094279 | 130.1181 | 0.096071
1010 | 734 | 131.1126 | 0.022074 | 130.5174 | 0.21588 | 130.7014 | 0.078529 | 130.266 | 0.094279 | 130.605 | 0.096071
1020 | 744 | 131.5022 | 0.022074 | 130.8096 | 0.21426 | 131.091 | 0.078529 | 130.5582 | 0.094279 | 130.8972 | 0.094447
1030 | 754 | 131.0152 | 0.022074 | 130.42 | 0.21263 | 130.604 | 0.078529 | 130.0712 | 0.094279 | 130.4102 | 0.094447
1040 | 764 | 130.723 | 0.022074 | 130.1278 | 0.21426 | 130.2144 | 0.076906 | 129.8764 | 0.094279 | 130.1181 | 0.096071
1050 | 774 | 130.3334 | 0.022074 | 129.8357 | 0.21426 | 129.9222 | 0.076906 | 129.5842 | 0.094279 | 129.8258 | 0.094447
1060 | 784 | 130.0412 | 0.022074 | 129.6409 | 0.21426 | 129.4353 | 0.076906 | 129.1946 | 0.094279 | 129.4363 | 0.094447
1070 | 794 | 129.5542 | 0.020451 | 129.3486 | 0.21426 | 128.8509 | 0.076906 | 128.8051 | 0.092656 | 129.0467 | 0.092824
1080 | 804 | 129.3595 | 0.022074 | 129.3486 | 0.21426 | 128.9483 | 0.076906 | 128.7076 | 0.092656 | 128.9493 | 0.094447
1090 | 814 | 129.262 | 0.022074 | 129.1539 | 0.21426 | 128.6561 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
1100 | 824 | 129.5542 | 0.022074 | 129.3486 | 0.21263 | 129.0457 | 0.075283 | 128.8051 | 0.092656 | 129.0467 | 0.092824
1110 | 834 | 130.4308 | 0.022074 | 129.933 | 0.21426 | 129.9222 | 0.078529 | 129.5842 | 0.094279 | 129.9233 | 0.096071
1120 | 844 | 131.0152 | 0.023697 | 130.42 | 0.21426 | 130.604 | 0.076906 | 130.0712 | 0.094279 | 130.4102 | 0.096071
1130 | 854 | 131.5022 | 0.022074 | 130.8096 | 0.21426 | 131.091 | 0.078529 | 130.5582 | 0.094279 | 130.8972 | 0.096071
1140 | 864 | 131.1126 | 0.022074 | 130.5174 | 0.21426 | 130.7014 | 0.076906 | 130.266 | 0.094279 | 130.605 | 0.096071
1160 | 884 | 130.0412 | 0.022074 | 129.6409 | 0.21426 | 129.5326 | 0.076906 | 129.292 | 0.094279 | 129.5337 | 0.094447
1180 | 904 | 129.749 | 0.022074 | 129.4461 | 0.21426 | 129.1431 | 0.076906 | 128.9024 | 0.094279 | 129.1441 | 0.096071
1200 | 924 | 129.3595 | 0.022074 | 129.1539 | 0.21426 | 128.6561 | 0.076906 | 128.6103 | 0.094279 | 128.8519 | 0.094447
1220 | 944 | 129.262 | 0.022074 | 129.1539 | 0.21263 | 128.6561 | 0.076906 | 128.5129 | 0.094279 | 128.7545 | 0.094447
1240 | 964 | 129.4568 | 0.020451 | 129.1539 | 0.21426 | 128.6561 | 0.076906 | 128.6103 | 0.092656 | 128.8519 | 0.094447
1260 | 984 | 129.9438 | 0.022074 | 129.5434 | 0.21426 | 129.1431 | 0.076906 | 128.9024 | 0.094279 | 129.1441 | 0.094447
1280 | 1004 | 129.749 | 0.020451 | 129.4461 | 0.21426 | 129.0457 | 0.076906 | 128.9999 | 0.094279 | 129.2415 | 0.094447
1300 | 1024 | 129.749 | 0.018828 | 129.5434 | 0.21588 | 129.0457 | 0.076906 | 128.9999 | 0.094279 | 129.2415 | 0.094447
1320 | 1044 | 130.0412 | 0.020451 | 129.6409 | 0.21588 | 129.3379 | 0.078529 | 129.0972 | 0.094279 | 129.4363 | 0.094447
1340 | 1064 | 130.4308 | 0.020451 | 129.933 | 0.21588 | 129.8249 | 0.076906 | 129.4868 | 0.094279 | 129.7285 | 0.094447
1360 | 1084 | 130.236 | 0.020451 | 129.7382 | 0.2175 | 129.7274 | 0.078529 | 129.4868 | 0.094279 | 129.7285 | 0.094447
1380 | 1104 | 129.8464 | 0.018828 | 129.4461 | 0.2175 | 129.2405 | 0.078529 | 129.1946 | 0.094279 | 129.3389 | 0.094447
1400 | 1124 | 130.5282 | 0.020451 | 130.0304 | 0.2175 | 130.117 | 0.078529 | 129.8764 | 0.094279 | 130.1181 | 0.096071
1420 | 1144 | 130.3334 | 0.020451 | 129.8357 | 0.21588 | 129.8249 | 0.078529 | 129.5842 | 0.095902 | 129.9233 | 0.096071
1440 | 1164 | 129.9438 | 0.018828 | 129.4461 | 0.21588 | 129.2405 | 0.076906 | 129.0972 | 0.094279 | 129.3389 | 0.094447
1460 | 1184 | 129.9438 | 0.020451 | 129.5434 | 0.21588 | 129.5326 | 0.078529 | 129.292 | 0.094279 | 129.5337 | 0.094447
1480 | 1204 | 129.6516 | 0.026944 | 129.2513 | 0.20939 | 128.9483 | 0.078529 | 128.7076 | 0.094279 | 129.0467 | 0.094447
1500 | 1224 | 129.0672 | 0.026944 | 129.0565 | 0.20939 | 128.2665 | 0.076906 | 128.2207 | 0.092656 | 128.6571 | 0.094447
1520 | 1244 | 129.749 | 0.026944 | 129.1539 | 0.20939 | 128.4613 | 0.078529 | 128.4155 | 0.094279 | 128.7545 | 0.094447
1540 | 1264 | 129.1647 | 0.025321 | 128.9591 | 0.21263 | 128.3639 | 0.078529 | 128.3181 | 0.092656 | 128.7545 | 0.094447
1560 | 1284 | 130.1386 | 0.023697 | 129.7382 | 0.21426 | 129.3379 | 0.078529 | 129.292 | 0.095902 | 129.7285 | 0.094447
1580 | 1304 | 130.6256 | 0.023697 | 130.1278 | 0.21426 | 129.8249 | 0.078529 | 129.779 | 0.094279 | 130.2154 | 0.096071
1600 | 1324 | 131.21 | 0.022074 | 130.6148 | 0.21588 | 130.7014 | 0.080153 | 130.3634 | 0.095902 | 130.7998 | 0.096071
1620 | 1344 | 131.5996 | 0.022074 | 130.907 | 0.21588 | 130.9936 | 0.078529 | 130.6556 | 0.094279 | 131.1894 | 0.096071
1640 | 1364 | 131.5996 | 0.022074 | 131.1018 | 0.2175 | 131.1884 | 0.078529 | 130.8504 | 0.094279 | 131.1894 | 0.096071
1660 | 1384 | 130.6256 | 0.018828 | 130.1278 | 0.2175 | 130.0197 | 0.078529 | 129.779 | 0.094279 | 130.2154 | 0.096071
1680 | 1404 | 130.1386 | 0.017205 | 129.8357 | 0.21913 | 129.4353 | 0.080153 | 129.3894 | 0.094279 | 129.7285 | 0.096071
1700 | 1424 | 131.0152 | 0.018828 | 130.42 | 0.22075 | 130.4092 | 0.080153 | 130.266 | 0.095902 | 130.605 | 0.096071
1720 | 1444 | 129.9438 | 0.017205 | 129.7382 | 0.21913 | 129.2405 | 0.080153 | 129.292 | 0.094279 | 129.5337 | 0.094447
1740 | 1464 | 129.5542 | 0.015581 | 129.3486 | 0.21913 | 128.8509 | 0.078529 | 129.0972 | 0.094279 | 129.2415 | 0.096071
1760 | 1484 | 130.5282 | 0.017205 | 130.1278 | 0.22075 | 130.117 | 0.078529 | 129.9738 | 0.095902 | 130.2154 | 0.096071
1780 | 1504 | 131.5996 | 0.015581 | 131.0044 | 0.22237 | 131.3832 | 0.080153 | 130.9478 | 0.094279 | 131.2868 | 0.096071
1800 | 1524 | 130.5282 | 0.017205 | 130.0304 | 0.22075 | 130.117 | 0.080153 | 129.9738 | 0.094279 | 130.2154 | 0.094447
1820 | 1544 | 129.6516 | 0.015581 | 129.5434 | 0.22075 | 129.2405 | 0.080153 | 129.1946 | 0.094279 | 129.3389 | 0.094447
1840 | 1564 | 129.749 | 0.013958 | 129.5434 | 0.22075 | 129.2405 | 0.078529 | 129.1946 | 0.094279 | 129.3389 | 0.094447
1860 | 1584 | 129.8464 | 0.013958 | 129.6409 | 0.22075 | 129.4353 | 0.078529 | 129.1946 | 0.094279 | 129.4363 | 0.094447
1880 | 1604 | 129.9438 | 0.015581 | 129.7382 | 0.22237 | 129.5326 | 0.080153 | 129.292 | 0.094279 | 129.631 | 0.096071
1900 | 1624 | 130.236 | 0.013958 | 129.8357 | 0.22075 | 129.8249 | 0.080153 | 129.5842 | 0.094279 | 129.9233 | 0.096071
1920 | 1644 | 130.723 | 0.015581 | 130.2252 | 0.22237 | 130.2144 | 0.080153 | 129.8764 | 0.095902 | 130.2154 | 0.094447
1940 | 1664 | 131.4048 | 0.013958 | 130.7122 | 0.22237 | 131.091 | 0.080153 | 130.5582 | 0.095902 | 130.9946 | 0.094447
1960 | 1684 | 131.3074 | 0.013958 | 130.8096 | 0.22237 | 131.091 | 0.080153 | 130.5582 | 0.094279 | 131.092 | 0.096071
1980 | 1704 | 131.3074 | 0.013958 | 130.7122 | 0.22237 | 130.9936 | 0.080153 | 130.4608 | 0.094279 | 130.9946 | 0.096071
2000 | 1724 | 130.5282 | 0.015581 | 130.1278 | 0.224 | 130.3118 | 0.081776 | 129.8764 | 0.095902 | 130.4102 | 0.096071
2020 | 1744 | 129.6516 | 0.013958 | 129.3486 | 0.22237 | 129.2405 | 0.080153 | 128.9999 | 0.094279 | 129.4363 | 0.096071
2040 | 1764 | 129.4568 | 0.012335 | 129.4461 | 0.224 | 128.9483 | 0.080153 | 128.9024 | 0.095902 | 129.1441 | 0.096071
2060 | 1784 | 129.4568 | 0.012335 | 129.4461 | 0.224 | 129.0457 | 0.080153 | 128.9024 | 0.095902 | 129.2415 | 0.096071
2080 | 1804 | 129.5542 | 0.010711 | 129.4461 | 0.224 | 129.2405 | 0.080153 | 128.9999 | 0.094279 | 129.2415 | 0.094447
2100 | 1824 | 131.0152 | 0.012335 | 130.5174 | 0.22562 | 130.7014 | 0.081776 | 130.1686 | 0.095902 | 130.5076 | 0.096071
2120 | 1844 | 131.0152 | 0.012335 | 130.5174 | 0.22562 | 130.7014 | 0.081776 | 130.266 | 0.095902 | 130.605 | 0.097694
2140 | 1864 | 129.4568 | 0.010711 | 129.3486 | 0.22562 | 129.0457 | 0.080153 | 128.8051 | 0.095902 | 129.2415 | 0.096071
2160 | 1884 | 129.5542 | 0.010711 | 129.3486 | 0.224 | 128.8509 | 0.080153 | 128.6103 | 0.095902 | 129.0467 | 0.096071
2180 | 1904 | 131.3074 | 0.012335 | 130.7122 | 0.22562 | 130.7988 | 0.081776 | 130.1686 | 0.095902 | 130.7998 | 0.096071
2200 | 1924 | 130.723 | 0.010711 | 130.2252 | 0.22562 | 130.0197 | 0.080153 | 129.6816 | 0.095902 | 130.2154 | 0.097694
2220 | 1944 | 130.5282 | 0.012335 | 130.0304 | 0.22562 | 129.8249 | 0.081776 | 129.4868 | 0.095902 | 130.0206 | 0.096071
2240 | 1964 | 129.749 | 0.010711 | 129.4461 | 0.22562 | 128.7535 | 0.080153 | 128.7076 | 0.095902 | 129.2415 | 0.096071
2260 | 1984 | 129.262 | 0.0090883 | 129.2513 | 0.22562 | 127.8769 | 0.080153 | 128.1233 | 0.095902 | 128.6571 | 0.096071
2277.8 | 2001.8 | 129.4568 | 0.0090883 | 129.4461 | 0.22724 | 127.8769 | 0.080153 | 128.2207 | 0.094279 | 128.8519 | 0.096071

## Circuit 2 Faulting
Summary of Observed Faulting Behavior for Circuit #2
DAQ Time | Burner Time | Event | Discussion
276 | 0 | Burner on
319 | 43 | FB | Fuse Blow
Summary Observations |  | The energized PE cable experienced a short to ground causing a circuit fuse blow. No signs of source voltage degradation prior to FB are noted.

## Converted Data C2
DAQ Time | Burner Time | C2 V1 | C2 A1 | C2 V2 | C2 A2 | C2 V4 | C2 A4 | C2 V5 | C2 A5 | C2 V6 | C2 A6
0 | -276 | 131.3539 | 0.0057127 | 130.6974 | 0.0048085 | 0.27094 | 0.0035836 | 0.21468 | 0.0022635 | 0.213 | 0.0029322
30 | -246 | 130.7695 | 0.0024661 | 130.113 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085
60 | -216 | 130.8669 | 0.0073357 | 130.2104 | 0.0080546 | 0.076183 | 0.00033696 | 0.01988 | 0.00064048 | 0.018196 | -0.00031449
90 | -186 | 130.6721 | 0.0024661 | 130.0156 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085
120 | -156 | 130.3799 | 0.0024661 | 129.7234 | 0.0031849 | 0.076183 | 0.00033696 | 0.01988 | 0.00064048 | 0.018196 | 0.0013085
150 | -126 | 130.8669 | 0.0089587 | 130.2104 | 0.0096782 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449
180 | -96 | 130.6721 | 0.0024661 | 130.0156 | 0.0015619 | 0.076183 | 0.0019606 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085
210 | -66 | 130.9643 | 0.00084239 | 130.2104 | 0.0015619 | 0.076183 | 0.00033696 | 0.11726 | 0.0022635 | 0.018196 | 0.0013085
240 | -36 | 130.9643 | 0.0024661 | 130.2104 | 0.0015619 | -0.021237 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
250 | -26 | 130.8669 | 0.0024661 | 130.113 | 0.0015619 | 0.076183 | 0.00033696 | 0.11726 | 0.0022635 | 0.018196 | -0.00031449
260 | -16 | 130.8669 | 0.0024661 | 130.113 | 0.0015619 | -0.021237 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
270 | -6 | 130.4773 | 0.0024661 | 129.8208 | 0.0015619 | -0.021237 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
280 | 4 | 130.3799 | 0.00084239 | 129.7234 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
290 | 14 | 130.3799 | 0.0040891 | 129.8208 | 0.0031849 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
300 | 24 | 130.4773 | 0.0057127 | 129.8208 | 0.0048085 | -0.021237 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
310 | 34 | 130.4773 | 0.0024661 | 129.9182 | 0.0031849 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
311 | 35 | 130.4773 | 0.0024661 | 129.9182 | 0.0031849 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085
312 | 36 | 130.5747 | 0.0024661 | 129.8208 | 0.0031849 | 0.076183 | 0.00033696 | -0.0775 | 0.0022635 | 0.018196 | 0.0013085
313 | 37 | 130.4773 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
314 | 38 | 130.4773 | 0.0024661 | 129.8208 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
315 | 39 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
316 | 40 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.11726 | 0.0022635 | 0.018196 | 0.0013085
317 | 41 | 130.4773 | 0.0024661 | 129.8208 | 0.0031849 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
318 | 42 | 130.4773 | 0.0024661 | 129.8208 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
318.2 | 42.2 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085
318.4 | 42.4 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449
318.6 | 42.6 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.0019606 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
318.8 | 42.8 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085
319 | 43 | 130.5747 | 0.0024661 | 129.9182 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0038865 | 0.018196 | 0.0013085
319.2 | 43.2 | 120.7377 | 0.0024661 | 120.4707 | 0.57458 | 0.17356 | 0.00033696 | 0.01988 | 0.00064048 | 0.11562 | 0.0013085
319.4 | 43.4 | 13.6989 | 0.0024661 | 14.0163 | 1.0177 | 0.17356 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
319.6 | 43.6 | 2.6931 | 0.0024661 | 2.5235 | 0.084349 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
319.8 | 43.8 | 1.2321 | 0.0024661 | 1.16 | 0.019418 | 0.076183 | 0.0019606 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
320 | 44 | 0.84251 | 0.00084239 | 0.7704 | 0.0096782 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
320.2 | 44.2 | 0.64775 | 0.0024661 | 0.5756 | 0.0064315 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085
320.4 | 44.4 | 0.74513 | 0.0024661 | 0.47822 | 0.0048085 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
320.6 | 44.6 | 0.55033 | 0.00084239 | 0.3808 | 0.0048085 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
320.8 | 44.8 | 0.55033 | 0.00084239 | 0.3808 | 0.0048085 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
321 | 45 | 0.45295 | 0.00084239 | 0.3808 | 0.0031849 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
322 | 46 | 0.45295 | 0.0024661 | 0.28342 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
323 | 47 | 0.35553 | 0.0024661 | 0.18604 | 0.0015619 | 0.076183 | 0.00033696 | 0.11726 | 0.0022635 | 0.018196 | 0.0013085
324 | 48 | 0.35553 | 0.00084239 | 0.28342 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
325 | 49 | 0.35553 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085
326 | 50 | 0.35553 | 0.0024661 | 0.18604 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
330 | 54 | 0.25815 | 0.00084239 | 0.18604 | -6.1803e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085
340 | 64 | 0.25815 | 0.00084239 | 0.088619 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | -0.00031449
350 | 74 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.018196 | 0.0013085
360 | 84 | 0.16077 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | 0.0013085
370 | 94 | 0.25815 | 0.00084239 | 0.088619 | -6.1803e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0038865 | 0.11562 | -0.00031449
380 | 104 | 0.25815 | 0.00084239 | 0.088619 | 0.0015619 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | 0.11562 | -0.00031449
390 | 114 | 1.4269 | -0.00078062 | 1.2574 | -6.1803e-05 | 0.076183 | 0.00033696 | 0.01988 | 0.0022635 | -0.079185 | 0.0013085
400 | 124 | 0.93993 | 0.00084239 | 0.5756 | 0.0015619 | 0.076183 | 0.00033696 | 0.11726 | 0.0038865 | 0.018196 | -0.00031449

## Circuit 3 Faulting
Summary of Observed Faulting Behavior for Circuit #3
DAQ Time | Burner Time | Event | Discussion
276 | 0 | Burner on
411 | 135 | FB
Summary Observations |  | The energized PE cable experienced a short to ground causing a circuit fuse blow. No signs of source voltage degradation prior to FB are noted.

## Converted Data C3
DAQ Time | Burner Time | C3 V1 | C3 A1 | C3 V2 | C3 A2 | C3 V4 | C3 A4 | C3 V5 | C3 A5 | C3 V6 | C3 A6
0 | -276 | 132.371 | 0.0047237 | 131.9703 | 0.0098916 | 0.10109 | 0.0030389 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
30 | -246 | 131.884 | 0.001477 | 131.4833 | 0.0082679 | 0.19851 | -0.00020779 | 0.078174 | -0.00011232 | -0.011119 | -0.0006346
60 | -216 | 132.0788 | 0.0079703 | 131.5807 | 0.014761 | 0.10109 | 0.0014152 | 0.078174 | -0.00011232 | -0.011119 | 0.0009884
90 | -186 | 131.884 | 0.001477 | 131.3859 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884
120 | -156 | 131.5918 | 0.0031007 | 131.0937 | 0.0098916 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
150 | -126 | 132.0788 | 0.0079703 | 131.5807 | 0.014761 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884
180 | -96 | 131.884 | 0.0031007 | 131.3859 | 0.0082679 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
210 | -66 | 132.1762 | 0.001477 | 131.6781 | 0.0082679 | 0.10109 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0026121
240 | -36 | 132.371 | 0.001477 | 131.8729 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
270 | -6 | 131.6892 | 0.001477 | 131.0937 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
300 | 24 | 131.7866 | 0.0047237 | 131.2885 | 0.011515 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
330 | 54 | 131.7866 | 0.0031007 | 131.2885 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
360 | 84 | 132.1762 | 0.0079703 | 131.6781 | 0.013138 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
390 | 114 | 129.5465 | 0.0079703 | 128.951 | 0.014761 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | -0.0006346
400 | 124 | 130.2283 | 0.0079703 | 129.5353 | 0.014761 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
401 | 125 | 129.9361 | 0.0079703 | 129.3406 | 0.013138 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
402 | 126 | 130.6178 | 0.0079703 | 130.1197 | 0.014761 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
403 | 127 | 131.2996 | 0.011217 | 130.7041 | 0.016384 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
404 | 128 | 130.0335 | 0.0063473 | 129.5353 | 0.014761 | 0.29589 | 0.0014152 | 0.37035 | 0.0015107 | 0.18368 | 0.0009884
405 | 129 | 130.91 | 0.0079703 | 130.4119 | 0.013138 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
406 | 130 | 130.91 | 0.0095933 | 130.3145 | 0.014761 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
407 | 131 | 130.423 | 0.0079703 | 129.8276 | 0.014761 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
407.2 | 131.2 | 130.423 | 0.0079703 | 129.9249 | 0.014761 | 0.29589 | -0.00020779 | 0.078174 | 0.0015107 | 0.086261 | 0.0026121
407.4 | 131.4 | 130.5205 | 0.0079703 | 129.9249 | 0.013138 | -0.093712 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0042351
407.6 | 131.6 | 130.2283 | 0.0079703 | 129.7301 | 0.014761 | 0.10109 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
407.8 | 131.8 | 130.3257 | 0.0063473 | 129.8276 | 0.014761 | 0.29589 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | -0.0006346
408 | 132 | 129.9361 | 0.0079703 | 129.438 | 0.013138 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884
408.2 | 132.2 | 129.9361 | 0.0079703 | 129.438 | 0.014761 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
408.4 | 132.4 | 129.2543 | 0.0079703 | 128.7562 | 0.014761 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
408.6 | 132.6 | 128.7673 | 0.0079703 | 128.1718 | 0.013138 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884
408.8 | 132.8 | 128.9621 | 0.0079703 | 128.464 | 0.014761 | 0.29589 | -0.00020779 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
409 | 133 | 113.5735 | 0.0079703 | 112.6858 | 2.3166 | 0.19851 | -0.00020779 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
409.2 | 133.2 | 121.3652 | 0.0079703 | 121.0619 | 1.3004 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
409.4 | 133.4 | 128.9621 | 0.0079703 | 128.464 | 0.11053 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
409.6 | 133.6 | 129.4491 | 0.0063473 | 128.951 | 0.034241 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0026121
409.8 | 133.8 | 129.5465 | 0.0095933 | 129.1458 | 0.022878 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | -0.011119 | -0.0006346
410 | 134 | 130.1309 | 0.0079703 | 129.6328 | 0.019631 | 0.29589 | 0.0046619 | 0.27297 | 0.0015107 | 0.18368 | 0.0009884
410.2 | 134.2 | 108.801 | 0.0079703 | 107.4263 | 3.4025 | 0.39327 | -0.0067011 | -0.11663 | 0.0031344 | 0.18368 | 0.0026121
410.4 | 134.4 | 93.7046 | 0.0047237 | 92.8169 | 5.4073 | 0.29589 | 0.0030389 | 0.27297 | 0.0015107 | -0.10854 | 0.0026121
410.6 | 134.6 | 90.9775 | 0.0079703 | 90.1871 | 5.4073 | 0.10109 | 0.0014152 | 0.27297 | 0.0031344 | 0.086261 | 0.020468
410.8 | 134.8 | 96.9187 | 0.0079703 | 96.1283 | 5.0437 | 0.39327 | 0.0030389 | 0.56516 | 0.0015107 | 0.28106 | 0.0009884
411 | 135 | 92.9254 | 0.0063473 | 92.1351 | 5.4073 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.18368 | 0.0074818
411.2 | 135.2 | 86.9842 | 0.0031007 | 86.1939 | 5.4073 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0026121
411.4 | 135.4 | 12.7681 | 0.001477 | 11.5882 | 0.65433 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | 0.18368 | -0.0022576
411.6 | 135.6 | 3.3206 | 0.0031007 | 2.8225 | 0.076445 | -0.093712 | 0.0062856 | 0.078174 | 0.0047574 | -0.011119 | -0.0006346
411.8 | 135.8 | 2.0544 | 0.001477 | 1.6537 | 0.021255 | 0.19851 | 0.0014152 | 0.27297 | -0.0017353 | 0.086261 | -0.0006346
412 | 136 | 1.6648 | 0.001477 | 1.6537 | 0.018008 | 0.19851 | 0.0014152 | 0.37035 | -0.0017353 | -0.10854 | 0.0009884
412.2 | 136.2 | 1.957 | -0.00014601 | 1.7511 | 0.014761 | 0.29589 | -0.00020779 | 0.17559 | 0.0015107 | -0.10854 | 0.0009884
412.4 | 136.4 | 2.0544 | 0.0031007 | 1.9459 | 0.014761 | 0.29589 | 0.0014152 | -0.11663 | 0.0015107 | 0.18368 | 0.0009884
412.6 | 136.6 | 2.3466 | 0.001477 | 2.0433 | 0.011515 | 0.19851 | 0.0014152 | 0.37035 | 0.0015107 | 0.18368 | 0.0009884
412.8 | 136.8 | 2.931 | 0.001477 | 2.4329 | 0.0098916 | 0.19851 | -0.00020779 | 0.17559 | -0.0017353 | -0.011119 | 0.0009884
413 | 137 | 2.931 | 0.001477 | 2.6277 | 0.011515 | 0.19851 | 0.0030389 | 0.078174 | 0.0015107 | 0.086261 | 0.0026121
413.2 | 137.2 | 3.2232 | -0.00014601 | 3.0173 | 0.0098916 | 0.29589 | 0.0014152 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884
413.4 | 137.4 | 2.2492 | 0.001477 | 2.0433 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0009884
413.6 | 137.6 | 1.8596 | -0.00014601 | 1.6537 | 0.0082679 | 0.10109 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
413.8 | 137.8 | 1.5675 | 0.001477 | 1.4589 | 0.0082679 | 0.19851 | -0.00020779 | 0.27297 | -0.00011232 | 0.086261 | 0.0009884
414 | 138 | 0.98306 | 0.001477 | 0.87456 | 0.0082679 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
414.2 | 138.2 | 0.7883 | 0.001477 | 0.67976 | 0.0082679 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884
414.4 | 138.4 | 0.5935 | 0.001477 | 0.58238 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
414.6 | 138.6 | 0.5935 | 0.001477 | 0.48496 | 0.0082679 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884
414.8 | 138.8 | 0.49608 | 0.001477 | 0.48496 | 0.0082679 | 0.19851 | -0.00020779 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
415 | 139 | 0.5935 | 0.001477 | 0.38758 | 0.0082679 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | -0.011119 | 0.0009884
415.2 | 139.2 | 0.49608 | 0.001477 | 0.38758 | 0.0082679 | 0.19851 | 0.0014152 | 0.17559 | 0.0015107 | -0.011119 | 0.0009884
415.4 | 139.4 | 0.49608 | -0.00014601 | 0.38758 | 0.0066449 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
415.6 | 139.6 | 0.49608 | 0.001477 | 0.29015 | 0.0082679 | 0.19851 | -0.00020779 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
415.8 | 139.8 | 0.3987 | -0.00014601 | 0.38758 | 0.0082679 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
416 | 140 | 0.49608 | 0.001477 | 0.38758 | 0.0066449 | 0.29589 | 0.0014152 | 0.17559 | -0.00011232 | 0.086261 | 0.0026121
417 | 141 | 0.3987 | 0.001477 | 0.29015 | 0.0066449 | 0.29589 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
418 | 142 | 0.3987 | 0.001477 | 0.29015 | 0.0082679 | 0.29589 | 0.0014152 | 0.17559 | 0.0015107 | 0.086261 | 0.0009884
419 | 143 | 0.3987 | 0.001477 | 0.29015 | 0.0066449 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884
420 | 144 | 0.3987 | 0.001477 | 0.29015 | 0.0066449 | 0.19851 | 0.0014152 | 0.27297 | 0.0015107 | 0.086261 | 0.0009884

## Circuit 4 Faulting
Summary of Observed Faulting Behavior for Circuit #4
DAQ Time | Burner Time | Event | Discussion
276 | 0 | Burner on
362 | 86 | I2 increasing | current flow on Circuit Path 2 (the energized TEF cable). This appears to be a short to ground as there are no indications of any current to the target conductors.
362-414 | 86-138 | V2 Degrades | Source voltage experiences progressive degradation consistent with increasing current draw.
414 | 138 | FB
Summary Observations |  | The energized Tefzel cable experiences short to ground over an extended period that first degrades CPT voltage and eventually leads to a fuse blow failure. No indications of inter-cable interactions. Minimum voltage degradation prior to fuse blow is about 80V

## Converted Data C4
DAQ Time | Burner Time | C4 V1 | C4 A1 | C4 V2 | C4 A2 | C4 V4 | C4 A4 | C4 V5 | C4 A5 | C4 V6 | C4 A6
0 | -276 | 128.2817 | 0.0031231 | 128.3528 | 0.0026002 | 0.10379 | 0.0011681 | 0.064722 | 0.0011513 | 0.11153 | 0.0012748
30 | -246 | 127.8921 | 0.0015001 | 127.9632 | 0.0026002 | 0.0064052 | 0.0011681 | 0.064722 | -0.00047174 | 0.11153 | 0.0012748
60 | -216 | 128.1843 | 0.0063697 | 128.2554 | 0.0090935 | 0.0064052 | 0.0011681 | 0.064722 | 0.0011513 | 0.014152 | -0.00034817
90 | -186 | 127.8921 | 0.0015001 | 127.9632 | 0.0026002 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
120 | -156 | 127.6973 | 0.0031231 | 127.671 | 0.0026002 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
150 | -126 | 128.0869 | 0.0096164 | 128.0606 | 0.010717 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
180 | -96 | 127.9895 | 0.0031231 | 127.9632 | 0.00097717 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
210 | -66 | 128.1843 | 0.0015001 | 128.0606 | 0.0026002 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817
240 | -36 | 128.0869 | 0.0015001 | 128.0606 | 0.0026002 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
270 | -6 | 127.5999 | 0.0015001 | 127.671 | 0.00097717 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
300 | 24 | 127.7947 | 0.0063697 | 127.7684 | 0.0058469 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
330 | 54 | 127.6973 | 0.0047461 | 127.671 | 0.0090935 | 0.10379 | 0.0011681 | 0.1621 | 0.0060216 | 0.014152 | 0.0012748
331 | 55 | 127.5999 | 0.0079928 | 127.671 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
331.2 | 55.2 | 127.5999 | 0.0015001 | 127.5736 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
331.4 | 55.4 | 127.4051 | 0.0031231 | 127.2814 | 0.028573 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
331.6 | 55.6 | 127.0155 | 0.0031231 | 126.8918 | 0.088634 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748
331.8 | 55.8 | 126.7233 | 0.0031231 | 126.697 | 0.13409 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
332 | 56 | 126.3337 | 0.0031231 | 126.4048 | 0.16493 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
332.2 | 56.2 | 126.2364 | 0.0031231 | 126.1126 | 0.1909 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
332.4 | 56.4 | 126.1389 | 0.0031231 | 126.0153 | 0.21525 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817
332.6 | 56.6 | 126.2364 | 0.0031231 | 126.2101 | 0.20064 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817
332.8 | 56.8 | 127.0155 | 0.0031231 | 127.0866 | 0.080518 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
333 | 57 | 127.6973 | 0.0031231 | 127.5736 | 0.039936 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
333.2 | 57.2 | 127.7947 | 0.0031231 | 127.7684 | 0.015587 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
333.4 | 57.4 | 127.7947 | 0.0031231 | 127.7684 | 0.010717 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
333.6 | 57.6 | 127.7947 | 0.0031231 | 127.7684 | 0.0090935 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817
333.8 | 57.8 | 127.7947 | 0.0031231 | 127.7684 | 0.0074705 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.30633 | 0.0012748
334 | 58 | 127.6973 | 0.0031231 | 127.671 | 0.0058469 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.11153 | 0.0012748
335 | 59 | 127.7947 | 0.0047461 | 127.7684 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
336 | 60 | 127.7947 | 0.0031231 | 127.7684 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
337 | 61 | 127.8921 | 0.0031231 | 127.8658 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
337.2 | 61.2 | 127.8921 | 0.0047461 | 127.8658 | 0.010717 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
337.4 | 61.4 | 127.8921 | 0.0031231 | 127.8658 | 0.0074705 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
337.6 | 61.6 | 127.5999 | 0.0015001 | 127.4762 | 0.0090935 | 0.0064052 | -0.00045489 | 0.1621 | 0.0011513 | 0.30633 | 0.0028978
337.8 | 61.8 | 119.3212 | 0.3992 | 120.9507 | 1.0707 | 0.10379 | 0.56607 | 0.25952 | 0.49138 | 0.20895 | 0.32918
338 | 62 | 126.8207 | 0.13298 | 126.9892 | 0.14058 | 0.10379 | 0.0027911 | 0.25952 | 0.0027749 | 0.20895 | 0.0028978
338.2 | 62.2 | 127.7947 | 0.0031231 | 127.7684 | 0.035066 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
338.4 | 62.4 | 127.8921 | 0.0047461 | 127.7684 | 0.015587 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
338.6 | 62.6 | 127.8921 | 0.0047461 | 127.8658 | 0.010717 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
338.8 | 62.8 | 127.8921 | 0.0047461 | 127.8658 | 0.0074705 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
339 | 63 | 127.8921 | 0.0047461 | 127.8658 | 0.0090935 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
340 | 64 | 127.8921 | 0.0047461 | 127.8658 | 0.0074705 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817
341 | 65 | 127.8921 | 0.0047461 | 127.7684 | 0.0074705 | 0.10379 | -0.00045489 | 0.1621 | -0.00047174 | 0.11153 | 0.0012748
342 | 66 | 127.8921 | 0.0063697 | 127.7684 | 0.0074705 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
342.2 | 66.2 | 127.7947 | 0.0063697 | 127.8658 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
342.4 | 66.4 | 127.8921 | 0.0063697 | 127.7684 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817
342.6 | 66.6 | 127.8921 | 0.0047461 | 127.7684 | 0.0058469 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
342.8 | 66.8 | 127.6973 | 0.0063697 | 127.5736 | 0.0074705 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817
343 | 67 | 127.6973 | 0.0063697 | 127.5736 | 0.023703 | 0.0064052 | -0.00045489 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817
343.2 | 67.2 | 127.1129 | 0.0047461 | 127.0866 | 0.099997 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817
343.4 | 67.4 | 127.8921 | 0.0063697 | 127.7684 | 0.030196 | 0.0064052 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817
343.6 | 67.6 | 127.8921 | 0.0063697 | 127.8658 | 0.015587 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748
343.8 | 67.8 | 127.8921 | 0.0063697 | 127.8658 | 0.01234 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
344 | 68 | 127.8921 | 0.0063697 | 127.8658 | 0.0090935 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817
345 | 69 | 127.9895 | 0.0063697 | 127.9632 | 0.0090935 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
346 | 70 | 127.8921 | 0.0063697 | 127.8658 | 0.0074705 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817
347 | 71 | 127.9895 | 0.0063697 | 127.8658 | 0.0074705 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | -0.00034817
348 | 72 | 127.8921 | 0.0063697 | 127.8658 | 0.0090935 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | -0.0019718
349 | 73 | 127.9895 | 0.0063697 | 127.8658 | 0.0090935 | 0.0064052 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817
350 | 74 | 127.9895 | 0.0063697 | 127.8658 | 0.013963 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
351 | 75 | 127.9895 | 0.0063697 | 127.9632 | 0.010717 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
352 | 76 | 127.9895 | 0.0063697 | 127.8658 | 0.0090935 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
353 | 77 | 127.9895 | 0.0063697 | 127.8658 | 0.010717 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
354 | 78 | 127.8921 | 0.0063697 | 127.8658 | 0.01234 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748
355 | 79 | 127.8921 | 0.0079928 | 127.8658 | 0.013963 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817
355.2 | 79.2 | 127.8921 | 0.0063697 | 127.8658 | 0.01721 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
355.4 | 79.4 | 127.8921 | 0.0063697 | 127.8658 | 0.018833 | 0.0064052 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748
355.6 | 79.6 | 127.8921 | 0.0063697 | 127.8658 | 0.020457 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
355.8 | 79.8 | 127.8921 | 0.0079928 | 127.8658 | 0.020457 | 0.0064052 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817
356 | 80 | 127.7947 | 0.0079928 | 127.7684 | 0.02208 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
356.2 | 80.2 | 127.8921 | 0.0063697 | 127.8658 | 0.023703 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
356.4 | 80.4 | 127.8921 | 0.0063697 | 127.7684 | 0.025326 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817
356.6 | 80.6 | 127.8921 | 0.0063697 | 127.8658 | 0.028573 | 0.0064052 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817
356.8 | 80.8 | 127.7947 | 0.0079928 | 127.7684 | 0.030196 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
357 | 81 | 127.5999 | 0.0063697 | 127.5736 | 0.056169 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
357.2 | 81.2 | 127.5999 | 0.0063697 | 127.5736 | 0.062661 | 0.10379 | -0.00045489 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817
357.4 | 81.4 | 127.5999 | 0.0096164 | 127.5736 | 0.072401 | 0.0064052 | -0.0020786 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
357.6 | 81.6 | 127.5999 | 0.0079928 | 127.671 | 0.065908 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
357.8 | 81.8 | 127.5025 | 0.0063697 | 127.4762 | 0.077271 | 0.0064052 | -0.00045489 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817
358 | 82 | 127.4051 | 0.0063697 | 127.2814 | 0.099997 | 0.0064052 | 0.0011681 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817
358.2 | 82.2 | 127.0155 | 0.0063697 | 126.8918 | 0.14383 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
358.4 | 82.4 | 126.4311 | 0.0079928 | 126.3074 | 0.21687 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817
358.6 | 82.6 | 126.2364 | 0.0063697 | 126.3074 | 0.23473 | 0.29859 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | -0.0019718
358.8 | 82.8 | 126.0416 | 0.0079928 | 126.0153 | 0.25908 | -0.091015 | -0.00045489 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817
359 | 83 | 126.0416 | 0.0063697 | 125.9178 | 0.27856 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
359.2 | 83.2 | 125.9441 | 0.046952 | 125.7231 | 0.27531 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
359.4 | 83.4 | 127.4051 | 0.0079928 | 127.3788 | 0.10649 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
359.6 | 83.6 | 127.4051 | 0.0079928 | 127.3788 | 0.10162 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
359.8 | 83.8 | 127.2103 | 0.0079928 | 127.0866 | 0.12759 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
360 | 84 | 126.8207 | 0.0079928 | 126.7944 | 0.17629 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748
360.2 | 84.2 | 127.0155 | 0.0063697 | 126.9892 | 0.15843 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.11153 | -0.00034817
360.4 | 84.4 | 126.7233 | 0.0079928 | 126.7944 | 0.18278 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817
360.6 | 84.6 | 127.0155 | 0.0079928 | 126.9892 | 0.1633 | -0.091015 | -0.0037016 | 0.1621 | 0.0027749 | 0.014152 | 0.0045215
360.8 | 84.8 | 126.9181 | 0.0079928 | 126.8918 | 0.16168 | 0.0064052 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | -0.0019718
361 | 85 | 126.9181 | 0.0096164 | 126.8918 | 0.15843 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | -0.0084645
361.2 | 85.2 | 126.9181 | 0.0063697 | 127.0866 | 0.14545 | 0.10379 | -0.00045489 | 0.1621 | -0.0020947 | 0.20895 | -0.00034817
361.4 | 85.4 | 127.1129 | 0.0079928 | 127.0866 | 0.14383 | 0.0064052 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | -0.00034817
361.6 | 85.6 | 126.7233 | 0.0096164 | 126.697 | 0.18116 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
361.8 | 85.8 | 126.5285 | 0.0079928 | 126.4048 | 0.22986 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
362 | 86 | 126.2364 | 0.0079928 | 126.2101 | 0.24934 | 0.10379 | -0.00045489 | 0.1621 | 0.0027749 | 0.20895 | -0.00034817
362.2 | 86.2 | 126.2364 | 0.0079928 | 126.2101 | 0.25258 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
362.4 | 86.4 | 126.0416 | 0.0079928 | 125.9178 | 0.28343 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
362.6 | 86.6 | 125.652 | 0.0079928 | 125.6257 | 0.31914 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.11153 | -0.00034817
362.8 | 86.8 | 125.4571 | 0.0079928 | 125.3335 | 0.34836 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
363 | 87 | 125.0676 | 0.0079928 | 125.0413 | 0.39219 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
363.2 | 87.2 | 124.678 | 0.0063697 | 124.5543 | 0.44088 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
363.4 | 87.4 | 124.0936 | 0.0079928 | 124.0673 | 0.51231 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
363.6 | 87.6 | 123.5092 | 0.0079928 | 123.4829 | 0.57886 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
363.8 | 87.8 | 122.8274 | 0.0079928 | 122.8012 | 0.6649 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
364 | 88 | 121.9509 | 0.0096164 | 121.8272 | 0.76554 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
364.2 | 88.2 | 121.3665 | 0.0079928 | 121.3402 | 0.83372 | 0.0064052 | -0.00045489 | 0.25952 | -0.00047174 | 0.20895 | -0.00034817
364.4 | 88.4 | 120.5873 | 0.0079928 | 120.4637 | 0.93761 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
364.6 | 88.6 | 123.217 | 0.0079928 | 123.0934 | 0.62594 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
364.8 | 88.8 | 123.9962 | 0.0079928 | 124.0673 | 0.50582 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
365 | 89 | 126.9181 | 0.0079928 | 126.7944 | 0.17791 | 0.10379 | -0.00045489 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748
365.2 | 89.2 | 127.1129 | 0.0096164 | 126.9892 | 0.15681 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
365.4 | 89.4 | 126.3337 | 0.0079928 | 126.3074 | 0.23798 | 0.10379 | 0.0011681 | 0.1621 | -0.00047174 | 0.20895 | 0.0012748
365.6 | 89.6 | 125.652 | 0.0096164 | 125.6257 | 0.31752 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
365.8 | 89.8 | 125.165 | 0.0079928 | 125.1387 | 0.38894 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
366 | 90 | 124.4832 | 0.0096164 | 124.4569 | 0.45062 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
366.2 | 90.2 | 123.704 | 0.0079928 | 123.5804 | 0.55289 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
366.4 | 90.4 | 122.5353 | 0.0079928 | 122.4116 | 0.70061 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
366.6 | 90.6 | 121.5613 | 0.0079928 | 121.4376 | 0.81424 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
366.8 | 90.8 | 120.6848 | 0.0079928 | 120.561 | 0.92137 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
367 | 91 | 119.9056 | 0.0079928 | 119.7819 | 1.0139 | 0.10379 | -0.00045489 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748
367.2 | 91.2 | 124.2884 | 0.0079928 | 124.0673 | 0.5399 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
367.4 | 91.4 | 126.5285 | 0.0079928 | 126.4048 | 0.22337 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
367.6 | 91.6 | 127.5999 | 0.0096164 | 127.5736 | 0.098373 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
367.8 | 91.8 | 127.5999 | 0.0096164 | 127.671 | 0.078894 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
368 | 92 | 127.6973 | 0.0096164 | 127.5736 | 0.078894 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
368.2 | 92.2 | 126.6259 | 0.0079928 | 126.4048 | 0.22824 | 0.10379 | -0.00045489 | -0.032698 | 0.0043979 | 0.20895 | -0.00034817
368.4 | 92.4 | 126.8207 | 0.0096164 | 126.7944 | 0.1698 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
368.6 | 92.6 | 126.9181 | 0.0096164 | 126.7944 | 0.19577 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
368.8 | 92.8 | 126.0416 | 0.0096164 | 126.0153 | 0.23148 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
369 | 93 | 126.8207 | 0.0096164 | 126.7944 | 0.19415 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
369.2 | 93.2 | 124.9702 | 0.0079928 | 124.8465 | 0.40193 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
369.4 | 93.4 | 126.2364 | 0.0096164 | 126.2101 | 0.2607 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
369.6 | 93.6 | 125.4571 | 0.0079928 | 125.4309 | 0.36621 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
369.8 | 93.8 | 126.4311 | 0.0079928 | 126.4048 | 0.24772 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
370 | 94 | 127.5025 | 0.0079928 | 127.3788 | 0.10649 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
370.2 | 94.2 | 126.3337 | 0.0096164 | 126.3074 | 0.24934 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0028978
370.4 | 94.4 | 125.8468 | 0.0079928 | 125.8205 | 0.30615 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
370.6 | 94.6 | 127.0155 | 0.0079928 | 126.8918 | 0.16168 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
370.8 | 94.8 | 125.3598 | 0.0096164 | 125.3335 | 0.34349 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
371 | 95 | 125.0676 | 0.0079928 | 125.0413 | 0.39056 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
371.2 | 95.2 | 126.1389 | 0.0079928 | 126.0153 | 0.26232 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
371.4 | 95.4 | 127.3077 | 0.0096164 | 127.184 | 0.13084 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
371.6 | 95.6 | 127.1129 | 0.0079928 | 126.9892 | 0.15681 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
371.8 | 95.8 | 127.0155 | 0.0096164 | 126.8918 | 0.15519 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
372 | 96 | 126.8207 | 0.0096164 | 126.5996 | 0.17791 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
372.2 | 96.2 | 126.4311 | 0.0079928 | 126.4048 | 0.21038 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
372.4 | 96.4 | 126.1389 | 0.0079928 | 126.0153 | 0.25745 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
372.6 | 96.6 | 125.9441 | 0.0096164 | 125.9178 | 0.2818 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
372.8 | 96.8 | 125.652 | 0.0096164 | 125.6257 | 0.32726 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
373 | 97 | 126.2364 | 0.0096164 | 126.2101 | 0.24934 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
373.2 | 97.2 | 126.7233 | 0.0096164 | 126.5996 | 0.1909 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
373.4 | 97.4 | 125.652 | 0.012862 | 125.6257 | 0.31589 | 0.20121 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
373.6 | 97.6 | 124.191 | 0.0096164 | 124.1647 | 0.50582 | 0.10379 | 0.0011681 | 0.3569 | 0.0011513 | 0.20895 | 0.0012748
373.8 | 97.8 | 124.9702 | 0.0079928 | 124.8465 | 0.41816 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
374 | 98 | 125.2624 | 0.0096164 | 125.1387 | 0.37108 | 0.20121 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
374.2 | 98.2 | 126.9181 | 0.0096164 | 126.8918 | 0.18928 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
374.4 | 98.4 | 127.1129 | 0.0096164 | 127.184 | 0.14707 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
374.6 | 98.6 | 126.8207 | 0.0096164 | 126.697 | 0.18928 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
374.8 | 98.8 | 126.1389 | 0.0096164 | 126.0153 | 0.28018 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
375 | 99 | 125.8468 | 0.0079928 | 125.9178 | 0.29641 | 0.10379 | 0.0011681 | 0.3569 | 0.0011513 | 0.20895 | 0.0012748
375.2 | 99.2 | 126.4311 | 0.0096164 | 126.3074 | 0.23473 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
375.4 | 99.4 | 125.5546 | 0.0079928 | 125.5283 | 0.33375 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
375.6 | 99.6 | 124.3858 | 0.0096164 | 124.2621 | 0.49121 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
375.8 | 99.8 | 123.8988 | 0.0096164 | 123.8725 | 0.53016 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
376 | 100 | 124.678 | 0.0096164 | 124.5543 | 0.46361 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
376.2 | 100.2 | 124.4832 | 0.0096164 | 124.4569 | 0.48147 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
376.4 | 100.4 | 123.704 | 0.0096164 | 123.6777 | 0.56101 | 0.10379 | 0.0027911 | 0.25952 | 0.0011513 | 0.20895 | 0.0028978
376.6 | 100.6 | 124.191 | 0.0079928 | 124.0673 | 0.51231 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
376.8 | 100.8 | 124.3858 | 0.0096164 | 124.3595 | 0.44413 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0028978
377 | 101 | 124.3858 | 0.0096164 | 124.3595 | 0.47335 | 0.10379 | 0.0011681 | 0.3569 | 0.0011513 | 0.20895 | 0.0012748
377.2 | 101.2 | 124.191 | 0.0096164 | 124.0673 | 0.4766 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
377.4 | 101.4 | 123.704 | 0.020979 | 123.2881 | 0.57562 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0045215
377.6 | 101.6 | 123.0222 | 0.0096164 | 122.996 | 0.63405 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
377.8 | 101.8 | 123.9962 | 0.0079928 | 123.9699 | 0.53016 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
378 | 102 | 124.5806 | 0.0096164 | 124.5543 | 0.44575 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
378.2 | 102.2 | 122.6327 | 0.0079928 | 122.509 | 0.68762 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
378.4 | 102.4 | 120.8795 | 0.0096164 | 120.7558 | 0.90027 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
378.6 | 102.6 | 120.6848 | 0.0096164 | 120.6585 | 0.90027 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
378.8 | 102.8 | 120.1004 | 0.0079928 | 119.9767 | 0.99442 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
379 | 103 | 121.5613 | 0.0096164 | 121.4376 | 0.80125 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
379.2 | 103.2 | 124.0936 | 0.0096164 | 123.9699 | 0.52043 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
379.4 | 103.4 | 124.4832 | 0.0079928 | 124.3595 | 0.46036 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
379.6 | 103.6 | 123.1197 | 0.0079928 | 123.0934 | 0.64542 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0028978
379.8 | 103.8 | 123.3144 | 0.0096164 | 123.1908 | 0.59185 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
380 | 104 | 123.0222 | 0.0096164 | 122.8986 | 0.64217 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
381 | 105 | 121.3665 | 0.0096164 | 121.3402 | 0.83047 | 0.10379 | 0.0011681 | 0.45428 | 0.0011513 | 0.20895 | 0.0028978
382 | 106 | 113.867 | 0.0079928 | 113.8407 | 1.7087 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
383 | 107 | 106.5623 | 0.0096164 | 106.4385 | 2.5787 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
384 | 108 | 102.8612 | 0.0079928 | 102.7375 | 3.0057 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
385 | 109 | 98.9653 | 0.0063697 | 98.8416 | 3.4537 | 0.10379 | -0.00045489 | 0.3569 | 0.0011513 | 0.20895 | 0.0045215
386 | 110 | 102.1794 | 0.0047461 | 102.0557 | 3.0625 | -0.091015 | -0.0020786 | 0.1621 | -0.0020947 | 0.11153 | -0.0035948
387 | 111 | 96.433 | 0.0063697 | 96.2119 | 3.7329 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
388 | 112 | 93.9007 | 0.0063697 | 93.6796 | 4.0413 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
389 | 113 | 87.5699 | 0.0063697 | 87.2514 | 4.728 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | 0.0028978
390 | 114 | 88.5439 | 0.0047461 | 88.3228 | 4.5851 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | 0.0028978
391 | 115 | 87.8621 | 0.0047461 | 87.641 | 4.6598 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.11153 | 0.0012748
392 | 116 | 88.1543 | 0.0063697 | 87.8358 | 4.5673 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
393 | 117 | 82.7001 | 0.0047461 | 82.479 | 5.1841 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
394 | 118 | 82.2131 | 0.0063697 | 81.992 | 5.1906 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | -0.00034817
395 | 119 | 83.4793 | 0.0063697 | 83.2582 | 5.0494 | 0.0064052 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
396 | 120 | 83.6741 | 0.0063697 | 83.453 | 4.9942 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
397 | 121 | 82.7001 | 0.0063697 | 82.479 | 5.0964 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
398 | 122 | 87.2777 | 0.0079928 | 87.1541 | 4.5802 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
399 | 123 | 100.3289 | 0.0063697 | 100.1078 | 3.1501 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
400 | 124 | 94.5825 | 0.0063697 | 94.4588 | 3.7848 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
400.2 | 124.2 | 95.0695 | 0.0079928 | 94.8484 | 3.7296 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
400.4 | 124.4 | 96.2382 | 0.0079928 | 96.1145 | 3.5965 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
400.6 | 124.6 | 93.8033 | 0.0079928 | 93.6796 | 3.8416 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
400.8 | 124.8 | 94.6799 | 0.0079928 | 94.4588 | 3.7313 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0028978
401 | 125 | 91.271 | 0.0063697 | 91.1473 | 4.1014 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
401.2 | 125.2 | 87.2777 | 0.0063697 | 87.1541 | 4.577 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
401.4 | 125.4 | 84.0637 | 0.0063697 | 83.8426 | 4.9146 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
401.6 | 125.6 | 92.1475 | 0.0063697 | 91.9265 | 4.0381 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
401.8 | 125.8 | 100.2315 | 0.0063697 | 100.1078 | 3.1355 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
402 | 126 | 103.8351 | 0.0079928 | 103.7115 | 2.7232 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
402.2 | 126.2 | 109.8737 | 0.0079928 | 109.6527 | 2.0512 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.20895 | 0.0012748
402.4 | 126.4 | 112.0164 | 0.0079928 | 111.8928 | 1.7703 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0028978
402.6 | 126.6 | 101.8872 | 0.0079928 | 102.0557 | 2.8693 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748
402.8 | 126.8 | 111.7243 | 0.0079928 | 111.698 | 1.8385 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
403 | 127 | 114.1592 | 0.0079928 | 114.0355 | 1.5187 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
403.2 | 127.2 | 97.3096 | 0.0079928 | 97.2833 | 3.4618 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
403.4 | 127.4 | 106.757 | 0.0079928 | 106.536 | 2.4294 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
403.6 | 127.6 | 102.1794 | 0.0079928 | 102.0557 | 2.8855 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.20895 | 0.0012748
403.8 | 127.8 | 93.6085 | 0.0063697 | 93.4848 | 3.8757 | 0.10379 | -0.00045489 | 0.3569 | 0.0011513 | 0.20895 | 0.0012748
404 | 128 | 95.8486 | 0.0047461 | 95.725 | 3.5998 | 0.10379 | 0.0027911 | 0.3569 | 0.0011513 | 0.20895 | 0.0012748
404.2 | 128.2 | 105.0039 | 0.0079928 | 104.8802 | 2.5966 | 0.0064052 | 0.0027911 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
404.4 | 128.4 | 110.0685 | 0.0079928 | 109.9448 | 2.0122 | 0.0064052 | -0.00045489 | 0.064722 | 0.0027749 | 0.30633 | -0.00034817
404.6 | 128.6 | 108.8997 | 0.0079928 | 108.6787 | 2.1697 | 0.20121 | 0.0011681 | 0.25952 | 0.0027749 | 0.30633 | 0.0012748
404.8 | 128.8 | 110.1659 | 0.0079928 | 110.1396 | 2.0057 | 0.10379 | -0.00045489 | 0.1621 | 0.0011513 | 0.20895 | 0.0028978
405 | 129 | 106.757 | 0.0063697 | 106.6333 | 2.418 | 0.10379 | 0.0011681 | 0.25952 | 0.0027749 | 0.30633 | 0.0012748
405.2 | 129.2 | 103.7377 | 0.0079928 | 103.614 | 2.7378 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | -0.0019718
405.4 | 129.4 | 104.8091 | 0.0079928 | 104.588 | 2.6388 | 0.0064052 | 0.0011681 | 0.25952 | 0.0043979 | 0.20895 | 0.0012748
405.6 | 129.6 | 107.5362 | 0.0079928 | 107.3151 | 2.3417 | 0.10379 | 0.0011681 | 0.3569 | 0.0027749 | 0.20895 | 0.0028978
405.8 | 129.8 | 108.705 | 0.0079928 | 108.4839 | 2.194 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | -0.00034817
406 | 130 | 107.3414 | 0.0079928 | 107.3151 | 2.3401 | 0.10379 | 0.0027911 | 0.3569 | -0.0020947 | 0.30633 | 0.0012748
406.2 | 130.2 | 104.9065 | 0.0096164 | 104.8802 | 2.6015 | 0.10379 | -0.00045489 | 0.5517 | 0.0027749 | 0.40375 | 0.0012748
406.4 | 130.4 | 103.3481 | 0.0096164 | 103.0297 | 2.8157 | 0.20121 | 0.0044148 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
406.6 | 130.6 | 102.1794 | 0.0096164 | 101.9583 | 2.9326 | 0.20121 | 0.0027911 | 0.064722 | 0.0027749 | 0.20895 | 0.0045215
406.8 | 130.8 | 100.4263 | 0.0079928 | 100.0104 | 3.1323 | 0.0064052 | 0.0027911 | 0.25952 | -0.00047174 | 0.30633 | -0.00034817
407 | 131 | 98.5757 | 0.0079928 | 98.3546 | 3.3141 | 0.0064052 | 0.0044148 | 0.1621 | 0.0011513 | 0.30633 | 0.0012748
407.2 | 131.2 | 101.3028 | 0.0047461 | 101.1791 | 2.9943 | 0.0064052 | -0.00045489 | 0.25952 | -0.00047174 | 0.11153 | -0.00034817
407.4 | 131.4 | 100.8159 | 0.011239 | 100.4 | 3.0657 | 0.0064052 | -0.00045489 | 0.45428 | 0.0011513 | 0.11153 | 0.0045215
407.6 | 131.6 | 97.6018 | 0.0047461 | 97.3807 | 3.4147 | 0.0064052 | 0.0011681 | 0.3569 | 0.0027749 | 0.30633 | -0.00034817
407.8 | 131.8 | 97.5044 | 0.0079928 | 97.3807 | 3.4082 | 0.20121 | -0.00045489 | 0.3569 | -0.0020947 | 0.20895 | 0.0028978
408 | 132 | 94.7772 | 0.0063697 | 94.4588 | 3.7426 | 0.10379 | 0.0044148 | 0.3569 | 0.0011513 | 0.20895 | -0.00034817
408.2 | 132.2 | 93.8033 | 0.0063697 | 93.5822 | 3.8108 | 0.20121 | 0.0011681 | 0.3569 | 0.0027749 | 0.20895 | 0.0028978
408.4 | 132.4 | 83.4793 | 0.0063697 | 83.3556 | 4.8741 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
408.6 | 132.6 | 75.1031 | 0.0047461 | 74.8821 | 5.4016 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
408.8 | 132.8 | 78.4146 | 0.0063697 | 78.0962 | 5.4016 | 0.10379 | 0.0027911 | 0.25952 | 0.0027749 | 0.20895 | 0.0028978
409 | 133 | 79.0964 | 0.0063697 | 78.778 | 5.249 | 0.20121 | 0.0011681 | -0.032698 | -0.00047174 | 0.014152 | -0.0019718
409.2 | 133.2 | 84.2585 | 0.0063697 | 84.1347 | 4.6841 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.40375 | 0.0012748
409.4 | 133.4 | 87.6673 | 0.0047461 | 87.3489 | 4.4374 | 0.10379 | 0.0011681 | 0.3569 | 0.0011513 | 0.11153 | 0.0012748
409.6 | 133.6 | 89.0308 | 0.0079928 | 88.7124 | 4.2962 | 0.0064052 | -0.00045489 | 0.1621 | 0.0011513 | 0.11153 | 0.0028978
409.8 | 133.8 | 88.6413 | 0.0031231 | 88.4202 | 4.314 | 0.10379 | 0.0011681 | 0.25952 | -0.00047174 | 0.30633 | 0.0028978
410 | 134 | 96.92 | 0.0047461 | 96.4067 | 3.4456 | 0.10379 | -0.00045489 | 0.25952 | -0.00047174 | 0.014152 | 0.0028978
410.2 | 134.2 | 96.92 | 0.0063697 | 97.2833 | 3.1534 | 0.10379 | -0.0037016 | 0.25952 | 0.0027749 | 0.11153 | 0.0028978
410.4 | 134.4 | 98.5757 | 0.0063697 | 98.452 | 2.8498 | 0.0064052 | 0.0011681 | 0.45428 | 0.0011513 | 0.79331 | 0.0045215
410.6 | 134.6 | 90.8814 | 0.0047461 | 90.7577 | 3.6615 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
410.8 | 134.8 | 95.459 | 0.014486 | 95.5302 | 3.241 | 0.0064052 | 0.0011681 | 0.25952 | 0.0027749 | 0.40375 | 0.0012748
411 | 135 | 94.1929 | 0.0047461 | 94.0692 | 3.3368 | 0.29859 | 0.0027911 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
411.2 | 135.2 | 92.0502 | 0.0047461 | 91.7317 | 3.5673 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0028978
411.4 | 135.4 | 89.7126 | 0.0047461 | 89.8811 | 4.1095 | 0.10379 | 0.0011681 | 0.3569 | 0.0076446 | 0.20895 | 0.0012748
411.6 | 135.6 | 94.1929 | 0.0079928 | 93.9718 | 3.7085 | 0.10379 | -0.0053252 | 0.064722 | 0.0092676 | 0.30633 | 0.012638
411.8 | 135.8 | 93.1215 | 0.0063697 | 93.29 | 3.8189 | 0.0064052 | 0.0027911 | 0.1621 | 0.0027749 | 0.20895 | 0.0061445
412 | 136 | 92.1475 | 0.0047461 | 92.4135 | 3.892 | 0.0064052 | -0.0020786 | 0.3569 | -0.00047174 | 0.30633 | 0.0093912
412.2 | 136.2 | 87.5699 | 0.0047461 | 87.3489 | 4.4536 | 0.20121 | 0.0011681 | 0.1621 | 0.0011513 | 0.11153 | 0.0012748
412.4 | 136.4 | 86.7907 | 0.0031231 | 86.3749 | 4.5315 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.59851 | -0.00034817
412.6 | 136.6 | 84.9402 | 0.0047461 | 84.7191 | 4.6939 | 0.0064052 | 0.0011681 | 0.45428 | 0.0011513 | 0.014152 | 0.0012748
412.8 | 136.8 | 77.9277 | 0.0031231 | 77.5118 | 5.4016 | 0.10379 | -0.00045489 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
413 | 137 | 80.7522 | 0.0047461 | 80.4337 | 5.1419 | -0.28578 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
413.2 | 137.2 | 77.7329 | 0.0063697 | 77.5118 | 5.4016 | 0.20121 | 0.0011681 | 0.25952 | 0.0027749 | 0.11153 | 0.0012748
413.4 | 137.4 | 74.7136 | 0.0031231 | 74.4925 | 5.4016 | 0.10379 | 0.0011681 | 0.45428 | 0.0011513 | 0.30633 | 0.0012748
413.6 | 137.6 | 74.0318 | 0.0031231 | 74.0055 | 5.4016 | 0.10379 | 0.0011681 | 0.1621 | 0.0027749 | 0.11153 | -0.00034817
413.8 | 137.8 | 42.7675 | 0.0015001 | 42.8386 | 3.5332 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
414 | 138 | 5.075 | 0.0015001 | 5.2436 | 0.23473 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.11153 | 0.0012748
414.2 | 138.2 | 1.4714 | 0.0031231 | 1.5425 | 0.041559 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
414.4 | 138.4 | 0.7896 | 0.0015001 | 0.86073 | 0.020457 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
414.6 | 138.6 | 0.59484 | 0.0031231 | 0.66593 | 0.013963 | 0.10379 | 0.0011681 | 0.1621 | 0.0011513 | 0.20895 | 0.0012748
414.8 | 138.8 | 0.49742 | 0.0015001 | 0.56855 | 0.010717 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
415 | 139 | 0.49742 | 0.0015001 | 0.47113 | 0.0090935 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
416 | 140 | 0.20523 | 0.0015001 | 0.27633 | 0.0058469 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
417 | 141 | 0.30262 | 0.0015001 | 0.27633 | 0.0042238 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
418 | 142 | 0.30262 | 0.0015001 | 0.27633 | 0.0042238 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
419 | 143 | 0.20523 | 0.0015001 | 0.27633 | 0.0026002 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
420 | 144 | 0.20523 | 0.0015001 | 0.27633 | 0.0042238 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
430 | 154 | 0.10785 | 0.0015001 | 0.17895 | 0.0026002 | 0.20121 | 0.0011681 | 0.3569 | 0.0011513 | 0.20895 | 0.0012748
440 | 164 | 0.20523 | 0.0015001 | 0.17895 | 0.00097717 | 0.20121 | 0.0011681 | 0.3569 | 0.0027749 | 0.30633 | 0.0012748
450 | 174 | 0.10785 | 0.0031231 | 0.17895 | 0.00097717 | 0.10379 | 0.0011681 | 0.3569 | 0.0027749 | 0.20895 | 0.0012748
460 | 184 | 0.10785 | 0.0031231 | 0.17895 | 0.00097717 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.30633 | 0.0012748
470 | 194 | 0.10785 | 0.0015001 | 0.17895 | 0.00097717 | 0.20121 | 0.0011681 | 0.3569 | 0.0027749 | 0.30633 | 0.0012748
480 | 204 | 0.10785 | 0.0031231 | 0.17895 | 0.00097717 | 0.10379 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748
490 | 214 | 0.10785 | 0.0015001 | 0.17895 | 0.00097717 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | -0.00034817
500 | 224 | 0.10785 | 0.0015001 | 0.17895 | 0.00097717 | 0.20121 | 0.0011681 | 0.25952 | 0.0011513 | 0.20895 | 0.0012748