## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-4
Test Date: | 2006-10-30
Ignition Time Relative to Thermal Data: | 276 | s
Ignition Time Relative to Electrical Data: | 276 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
3/C cable temperatures for location G - no electrical failure
Template plot

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable thermal bundle configuration 4-1 |  |  |  | Location A | Location C - 6-cable thermal Bundle configuration 4-2 |  |  |  | Location C | Air Drop Location A-C - single 7/C XLPE/CPSE |  |  | Location E - single 3/C XLPE/CSPE |  |  | Location E | Location G - single 3/C XLPE/CSPE |  |  | Location G
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | TC-1 Cable | TC-2 Above Cable | TC-3 Below Cable | TC-1 Cable | TC-2 Above Cable | TC-3 Below Cable | Tray Rung | TC-1 Cable | TC-2 Above Cable | TC-3 Below Cable | Tray Rung
0 | -276 | -6.5 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.4 | 248.7 | 17.8 | 15.4 | 14.9 | 15 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
1 | -275 | -5.9 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.4 | 248.4 | 17.1 | 15.4 | 14.9 | 15 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
2 | -274 | -6.2 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.4 | 266.2 | 15.5 | 15.4 | 14.9 | 15 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
3 | -273 | -6.6 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 1.8 | 248.3 | 14.7 | 15.4 | 14.9 | 15 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 15.9 | 17.4
4 | -272 | -6.8 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 1.9 | 234 | 13.2 | 15.4 | 14.9 | 15 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
5 | -271 | -6.9 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.6 | 249.8 | 13.3 | 15.4 | 14.9 | 15 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 15.9 | 17.4
6 | -270 | -6.8 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.8 | 263.7 | 10.8 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 15.9 | 17.4
7 | -269 | -6.5 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.8 | 244.2 | 10.1 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 15.9 | 17.4
8 | -268 | -6.5 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 3.1 | 248.6 | 13 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
9 | -267 | -6.7 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.4 | 253 | 14.3 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
10 | -266 | -6.9 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.7 | 248.5 | 14 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
11 | -265 | -6.9 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2 | 250.3 | 15 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 15.9 | 17.4
12 | -264 | -6.7 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2 | 250.4 | 16.5 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
13 | -263 | -6.7 | 0 | 0 | 16.5 | 16.8 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.5 | 250.2 | 17 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 15.9 | 17.4
14 | -262 | -6.9 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.7 | 264.3 | 16.7 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.6 | 15.7 | 17.2 | 16 | 15.9 | 16 | 17.4
15 | -261 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.9 | 260.9 | 15.4 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
16 | -260 | -6.6 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.3 | 261.6 | 14.3 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.5
17 | -259 | -6.6 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.6 | 265 | 13.5 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
18 | -258 | -6.7 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.3 | 257 | 15.1 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
19 | -257 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.1 | 252.7 | 16.1 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
20 | -256 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.5 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.6 | 254.8 | 15.5 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
21 | -255 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.5 | 240.3 | 15 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
22 | -254 | -6.7 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.7 | 241.4 | 14.3 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
23 | -253 | -6.4 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.1 | 243.7 | 12.6 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
24 | -252 | -6.7 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 3.1 | 239.9 | 12.4 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
25 | -251 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.5 | 229 | 11.5 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
26 | -250 | -6.9 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.7 | 243.7 | 10.6 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 15.9 | 15.9 | 17.4
27 | -249 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.4 | 245.7 | 10.4 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
28 | -248 | -6.9 | 0 | 0 | 16.5 | 16.7 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.9 | 238 | 9.3 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
29 | -247 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.6 | 2.9 | 236.5 | 8.2 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
30 | -246 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.7 | 2.9 | 231 | 8.5 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
31 | -245 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.7 | 3.1 | 231.6 | 9 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
32 | -244 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 3.2 | 254.4 | 9 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
33 | -243 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.9 | 247.9 | 9.6 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 15.9 | 17.4
34 | -242 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.7 | 253.9 | 13 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
35 | -241 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.4 | 250.9 | 13.3 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
36 | -240 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2 | 241.4 | 13 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
37 | -239 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.2 | 237 | 10.9 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
38 | -238 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 1.9 | 253 | 11.7 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
39 | -237 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.4 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 1.9 | 224.7 | 11.5 | 15.4 | 15 | 15.1 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.5
40 | -236 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 1.6 | 214.9 | 11.2 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
41 | -235 | -6.5 | 0 | 0 | 16.5 | 16.6 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 1.8 | 225.7 | 10.3 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
42 | -234 | -6.2 | 0 | 0 | 16.5 | 16.6 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.3 | 222.4 | 8.7 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
43 | -233 | -6.3 | 0 | 0 | 16.5 | 16.5 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.3 | 220.2 | 8 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.4 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
44 | -232 | -6.3 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 3.1 | 223.6 | 7.6 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
45 | -231 | -6.4 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 3.5 | 251.7 | 6.9 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
46 | -230 | -6.6 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 3.4 | 232.7 | 7.5 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
47 | -229 | -6.7 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 2.9 | 254.8 | 7.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.5
48 | -228 | -6.6 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 2.3 | 237.4 | 6.2 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
49 | -227 | -6.6 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 2.3 | 254.7 | 6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
50 | -226 | -6.7 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 2.8 | 235.3 | 8 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
51 | -225 | -6.7 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.5 | 22 | 15.6 | 2.8 | 238.5 | 9.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
52 | -224 | -6.6 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 2.6 | 233.7 | 9.5 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
53 | -223 | -6.5 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.7 | 2.3 | 226.7 | 10.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
54 | -222 | -6.7 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.7 | 2.7 | 228.3 | 10.5 | 15.4 | 15 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
55 | -221 | -6.9 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.7 | 2.2 | 227.1 | 8.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
56 | -220 | -6.9 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.7 | 2.3 | 261.3 | 8.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.5
57 | -219 | -6.8 | 0 | 0 | 16.6 | 16.5 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.7 | 2.3 | 240.1 | 7.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
58 | -218 | -6 | 0 | 0 | 16.5 | 16.6 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.7 | 1.9 | 245 | 7.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
59 | -217 | -5.6 | 0 | 0 | 16.6 | 16.6 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 1.8 | 251.4 | 8.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.1 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
60 | -216 | -6.4 | 0 | 0 | 16.6 | 16.6 | 16.3 | 16.6 | 16.9 | 15.4 | 22 | 15.6 | 2.1 | 222.6 | 10.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.1 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
61 | -215 | -6.3 | 0 | 0 | 16.6 | 16.6 | 16.3 | 16.5 | 16.9 | 15.4 | 22 | 15.6 | 2.7 | 224.4 | 9.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
62 | -214 | -6.1 | 0 | 0 | 16.6 | 16.6 | 16.3 | 16.5 | 16.9 | 15.4 | 22 | 15.6 | 2.8 | 243.7 | 9.8 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
63 | -213 | -6.4 | 0 | 0 | 16.6 | 16.6 | 16.2 | 16.5 | 16.9 | 15.4 | 22 | 15.7 | 2.9 | 245.9 | 10.2 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.5
64 | -212 | -6.8 | 0 | 0 | 16.6 | 16.6 | 16.2 | 16.5 | 16.9 | 15.4 | 22 | 15.7 | 3.6 | 243.1 | 10.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
65 | -211 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 4.4 | 239.1 | 10.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
66 | -210 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 5.2 | 241.9 | 10.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
67 | -209 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 4.1 | 241.5 | 10.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
68 | -208 | -6.5 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.4 | 245.4 | 11 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
69 | -207 | -6.2 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.4 | 241.4 | 11.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
70 | -206 | -6.6 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.5 | 230.9 | 12.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
71 | -205 | -6.7 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.4 | 237.8 | 11.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
72 | -204 | -6.7 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.5 | 238.1 | 9.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.5
73 | -203 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.6 | 234.9 | 9.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
74 | -202 | -6.7 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.8 | 247.2 | 10.8 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
75 | -201 | -6.4 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.5 | 246.6 | 13.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
76 | -200 | -6.1 | 0 | 0 | 16.6 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.9 | 233.4 | 14.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
77 | -199 | -5.9 | 0 | 0 | 16.6 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.9 | 213.6 | 10.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
78 | -198 | -5.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.3 | 239.3 | 9.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.5
79 | -197 | -6.1 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.3 | 240.9 | 8.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
80 | -196 | -6.1 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.1 | 232 | 9.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
81 | -195 | -6 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.4 | 235.3 | 8.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
82 | -194 | -6.3 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.3 | 261.2 | 7.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.7 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
83 | -193 | -6.3 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.6 | 209.8 | 7.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.1 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
84 | -192 | -5.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.1 | 228.6 | 7.2 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
85 | -191 | -6.6 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.1 | 253.1 | 7.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
86 | -190 | -6.7 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.1 | 256 | 8.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
87 | -189 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.4 | 226.7 | 8.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
88 | -188 | -6.7 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.5 | 262.8 | 10 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
89 | -187 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.3 | 224.9 | 9.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
90 | -186 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.4 | 249.4 | 10 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
91 | -185 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.1 | 241.2 | 10.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
92 | -184 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.8 | 251.6 | 11.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
93 | -183 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.7 | 240.5 | 12.8 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
94 | -182 | -6.9 | 0 | 0 | 16.5 | 16.7 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3 | 242.8 | 12.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
95 | -181 | -6.8 | 0 | 0 | 16.5 | 16.7 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2.4 | 238.8 | 13.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
96 | -180 | -6.7 | 0 | 0 | 16.5 | 16.7 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 1.7 | 249.5 | 13.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
97 | -179 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 1.8 | 236.6 | 13.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
98 | -178 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 2 | 245 | 12.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.5 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
99 | -177 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.6 | 226.6 | 10 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
100 | -176 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.9 | 244.8 | 9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
101 | -175 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.8 | 233.3 | 9.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
102 | -174 | -6.6 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.6 | 243.5 | 9.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.5
103 | -173 | -6.6 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.3 | 254.3 | 10.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
104 | -172 | -6.7 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.6 | 236.6 | 10.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
105 | -171 | -6.7 | 0 | 0 | 16.5 | 16.7 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.2 | 250.7 | 10.8 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
106 | -170 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.3 | 260.3 | 10 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
107 | -169 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.9 | 250 | 9.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
108 | -168 | -6.9 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.5 | 22 | 15.7 | 3.1 | 241.9 | 11.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
109 | -167 | -6.8 | 0 | 0 | 16.5 | 16.6 | 16.2 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 3 | 252.9 | 11.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
110 | -166 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.7 | 2.8 | 250.2 | 11.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
111 | -165 | -6.6 | 0 | 0 | 16.4 | 16.7 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.7 | 3.1 | 250.1 | 10.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
112 | -164 | -6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.8 | 255.4 | 10 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
113 | -163 | -5.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 2.1 | 253.5 | 9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 16 | 16 | 17.4
114 | -162 | -5.9 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 1.8 | 241.5 | 9.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 16 | 16 | 17.4
115 | -161 | -6.3 | 0 | 0 | 16.3 | 16.6 | 16.3 | 16.5 | 16.9 | 15.5 | 22 | 15.7 | 2.4 | 208.8 | 8.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
116 | -160 | -6.3 | 0 | 0 | 16.2 | 16.7 | 16.4 | 16.5 | 16.8 | 15.6 | 22 | 15.7 | 2.5 | 235.1 | 7.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.9 | 15.4 | 15.6 | 17.2 | 16 | 15.9 | 16 | 17.4
117 | -159 | -6.5 | 0 | 0 | 16.3 | 16.7 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 2.4 | 222.2 | 7.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 16 | 17.4
118 | -158 | -6.7 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.5 | 22 | 15.8 | 2.4 | 233.9 | 7.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 16 | 17.4
119 | -157 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.5 | 22 | 15.8 | 2.8 | 229.1 | 7.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
120 | -156 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.8 | 15.5 | 22 | 15.8 | 2.9 | 235.5 | 8.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
121 | -155 | -6.7 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.5 | 22 | 15.8 | 2.7 | 195.9 | 11.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
122 | -154 | -6.7 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.5 | 22 | 15.8 | 3 | 199.1 | 12.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.5
123 | -153 | -6.7 | 0 | 0 | 16.2 | 16.7 | 16.4 | 16.5 | 16.8 | 15.6 | 22 | 15.8 | 2.5 | 213.8 | 12.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
124 | -152 | -6.8 | 0 | 0 | 16.3 | 16.6 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 2.8 | 207.4 | 14.1 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
125 | -151 | -6.8 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.7 | 3.6 | 223.2 | 14 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
126 | -150 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 21.9 | 15.8 | 3.6 | 244.8 | 11.9 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
127 | -149 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.7 | 3.5 | 237.6 | 10 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
128 | -148 | -6.9 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.6 | 21.9 | 15.8 | 2.8 | 242.3 | 9.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
129 | -147 | -6.9 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 2.3 | 244.2 | 10.8 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
130 | -146 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 2 | 250.4 | 11.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
131 | -145 | -6.6 | 0 | 0 | 16.3 | 16.6 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 2.1 | 247.6 | 12 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
132 | -144 | -6.3 | 0 | 0 | 16.4 | 16.6 | 16.3 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 2.4 | 236.1 | 11.4 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
133 | -143 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 3.5 | 243.5 | 12.2 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
134 | -142 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 3.4 | 231.8 | 13.2 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
135 | -141 | -6.7 | 0 | 0 | 16.4 | 16.6 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3 | 214.1 | 11.3 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
136 | -140 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.4 | 237 | 9.7 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
137 | -139 | -6.6 | 0 | 0 | 16.2 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.1 | 240.1 | 9.6 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
138 | -138 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.8 | 238.1 | 10.5 | 15.4 | 15.1 | 15.2 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 16 | 17.4
139 | -137 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.8 | 246.2 | 10.2 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.7 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
140 | -136 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.4 | 247.3 | 11.5 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
141 | -135 | -6.4 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.3 | 246.8 | 10.6 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
142 | -134 | -6.5 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.3 | 255.3 | 9.4 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
143 | -133 | -6.5 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 1.8 | 250.1 | 8.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
144 | -132 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.4 | 250.8 | 10.3 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
145 | -131 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 2.6 | 265.6 | 9.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
146 | -130 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 2.7 | 252.5 | 10.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
147 | -129 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 3.1 | 263.3 | 10.7 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
148 | -128 | -6.4 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3.2 | 235 | 9.4 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.5
149 | -127 | -6.2 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3 | 238.5 | 7.6 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
150 | -126 | -5.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3.6 | 259.5 | 9.1 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
151 | -125 | -6.2 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.7 | 3 | 245 | 10.7 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
152 | -124 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.1 | 245.9 | 11.2 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
153 | -123 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.1 | 243.3 | 10.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
154 | -122 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.4 | 232.5 | 9.1 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
155 | -121 | -6.5 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.9 | 250.9 | 8.1 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
156 | -120 | -6.2 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3.7 | 237.4 | 9.1 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
157 | -119 | -6.2 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 4 | 229.2 | 10.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
158 | -118 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3.1 | 212.7 | 10.1 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
159 | -117 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.9 | 238 | 8.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.5
160 | -116 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.4 | 233.6 | 9.2 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
161 | -115 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3 | 226.5 | 10.2 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
162 | -114 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 4.1 | 221.8 | 8.5 | 15.4 | 15.1 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
163 | -113 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 4.1 | 231.9 | 7.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
164 | -112 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3 | 232.5 | 8.4 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
165 | -111 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4.3 | 214.2 | 11.5 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.4
166 | -110 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 6.3 | 209.7 | 14.3 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
167 | -109 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 6.2 | 211.8 | 16.3 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
168 | -108 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 5 | 238.2 | 14.9 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
169 | -107 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4.8 | 229.7 | 14.8 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
170 | -106 | -6.6 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 5.4 | 237.4 | 18.6 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
171 | -105 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 5.7 | 239.8 | 19.2 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
172 | -104 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4.4 | 242.8 | 19.5 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
173 | -103 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4 | 228.8 | 17.6 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.5 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
174 | -102 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4.5 | 243.9 | 16 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
175 | -101 | -6.3 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.8 | 236.4 | 15.8 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
176 | -100 | -6.5 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 5.2 | 239.9 | 17.2 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
177 | -99 | -6.2 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4.1 | 247 | 18.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
178 | -98 | -5.5 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.3 | 246.5 | 18.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
179 | -97 | -6.3 | 0 | 0 | 16.2 | 16.8 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.2 | 230.1 | 15.5 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
180 | -96 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.5 | 228.3 | 13.3 | 15.4 | 15.1 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
181 | -95 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.4 | 239.1 | 12.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
182 | -94 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.7 | 238.1 | 13.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
183 | -93 | -6.8 | 0 | 0 | 16.3 | 16.8 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.3 | 251.9 | 12.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
184 | -92 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.9 | 232.4 | 14 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
185 | -91 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.9 | 246 | 16.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
186 | -90 | -6.9 | 0 | 0 | 16.2 | 16.8 | 16.4 | 16.6 | 16.9 | 15.7 | 22 | 15.8 | 4.4 | 248.6 | 19.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
187 | -89 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.5 | 234.9 | 19.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
188 | -88 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.3 | 231.3 | 16.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
189 | -87 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.6 | 240 | 13.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
190 | -86 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3 | 244.1 | 13.2 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
191 | -85 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 2.4 | 242.4 | 14.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
192 | -84 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 2.9 | 244.2 | 16.2 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
193 | -83 | -6.8 | 0 | 0 | 16.2 | 16.7 | 16.5 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.9 | 249.8 | 15.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
194 | -82 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.8 | 244.8 | 16.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.5 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
195 | -81 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.5 | 241.3 | 18.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
196 | -80 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 2.7 | 246.5 | 16 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
197 | -79 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3 | 250.7 | 13.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
198 | -78 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3.2 | 240.2 | 12.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
199 | -77 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3 | 259 | 11.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
200 | -76 | -6.9 | 0 | 0 | 16.2 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 2.6 | 258.4 | 11.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
201 | -75 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 2.5 | 261.4 | 8.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
202 | -74 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3.4 | 206.3 | 10.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
203 | -73 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 4.5 | 245.7 | 11 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
204 | -72 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 5.5 | 247 | 7.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
205 | -71 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 5 | 212.2 | 9.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
206 | -70 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 4.5 | 258.7 | 8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
207 | -69 | -6.8 | 0 | 0 | 16.3 | 16.8 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.5 | 247.1 | 8.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
208 | -68 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 3.4 | 252.8 | 13.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
209 | -67 | -6.3 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.6 | 22 | 15.8 | 2.5 | 242.2 | 15.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.4 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
210 | -66 | -6.5 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 2.8 | 246.2 | 16.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
211 | -65 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.2 | 224.2 | 14.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
212 | -64 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3.1 | 244 | 12.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
213 | -63 | -6.6 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3 | 249 | 13.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.7 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
214 | -62 | -6.1 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.5 | 230.4 | 11.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
215 | -61 | -5.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3.6 | 236.1 | 11 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.4 | 17.1 | 16 | 15.9 | 15.9 | 17.4
216 | -60 | -5.4 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 4.7 | 242.7 | 13.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
217 | -59 | -6.4 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.7 | 248.3 | 14.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
218 | -58 | -6.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 4.3 | 246.3 | 13.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.3 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
219 | -57 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 3.8 | 231.8 | 12.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
220 | -56 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 4.4 | 228.7 | 10.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
221 | -55 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 5 | 228.5 | 9.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
222 | -54 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 5.6 | 237.8 | 10.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
223 | -53 | -6.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.4 | 16.9 | 15.7 | 22 | 15.8 | 6.8 | 247.3 | 12.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
224 | -52 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 6.9 | 235.4 | 13.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
225 | -51 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 5.7 | 240.4 | 15.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
226 | -50 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 5.5 | 250.6 | 15.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
227 | -49 | -6.5 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 7.4 | 242.6 | 14.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
228 | -48 | -6.6 | 0 | 0 | 16.2 | 16.7 | 16.5 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 7.7 | 245.5 | 15.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
229 | -47 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 7.5 | 244.4 | 19.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
230 | -46 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 6 | 239.9 | 21 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
231 | -45 | -6.8 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 21.9 | 15.9 | 7.1 | 233.6 | 22.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
232 | -44 | -6.4 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 5.1 | 239 | 21.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
233 | -43 | -5.8 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 5 | 235 | 20.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
234 | -42 | -6.1 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 5.4 | 238.1 | 18.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
235 | -41 | -6.7 | 0 | 0 | 16.2 | 16.7 | 16.5 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 4.4 | 241.9 | 20.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
236 | -40 | -1.2 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 4.6 | 236.1 | 18.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
237 | -39 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 3.8 | 242.6 | 16.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
238 | -38 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.8 | 3.5 | 241.1 | 18 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
239 | -37 | -6.7 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.8 | 3.1 | 240 | 17.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
240 | -36 | -3.7 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.2 | 235.3 | 16.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
241 | -35 | -2.6 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.9 | 238.2 | 16.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
242 | -34 | -2.4 | 0 | 0 | 16.2 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 3.6 | 251.9 | 14.2 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
243 | -33 | -4.2 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 3.1 | 247.2 | 11.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
244 | -32 | -5.3 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.9 | 249.4 | 10.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
245 | -31 | -6.2 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 3.7 | 242.4 | 10.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
246 | -30 | -6.5 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.7 | 249.4 | 11.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
247 | -29 | -6.7 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 1.8 | 259.9 | 12.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
248 | -28 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 1.6 | 243.4 | 14 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
249 | -27 | -6.9 | 0 | 0 | 16.2 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 1.7 | 243.9 | 14.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
250 | -26 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 1.8 | 253.3 | 13.9 | 15.4 | 15.2 | 15.4 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
251 | -25 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 21.9 | 15.9 | 2.1 | 258.2 | 12.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
252 | -24 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 21.9 | 15.9 | 2 | 251.9 | 12.9 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
253 | -23 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.7 | 21.9 | 15.9 | 2.1 | 246.4 | 13.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
254 | -22 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.7 | 22 | 15.9 | 2.1 | 257.8 | 13.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
255 | -21 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.3 | 239.5 | 14.2 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
256 | -20 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 3.3 | 237.9 | 12.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
257 | -19 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 4.1 | 251.9 | 12.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
258 | -18 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 4.2 | 247.3 | 13.1 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
259 | -17 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 3.9 | 239.4 | 12.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
260 | -16 | -6.9 | 0 | 0 | 16.3 | 16.8 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 2.8 | 247.2 | 14.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.7 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
261 | -15 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.4 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.6 | 237.8 | 17.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
262 | -14 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 4 | 237.5 | 15.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
263 | -13 | -6.9 | 0 | 0 | 16.3 | 16.8 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 4.8 | 271.1 | 15 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
264 | -12 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 3.8 | 274.8 | 18.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
265 | -11 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 3.1 | 264.2 | 17.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
266 | -10 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.7 | 249.3 | 17.5 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
267 | -9 | -6.9 | 0 | 0 | 16.3 | 16.8 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 2.1 | 248.4 | 16.8 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
268 | -8 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 1.6 | 273.3 | 15.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.6 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 16 | 17.4
269 | -7 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 1.8 | 271.4 | 14.7 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
270 | -6 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.8 | 15.6 | 22 | 15.9 | 2.8 | 278.8 | 14.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.7 | 15.5 | 16.6 | 15.7 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
271 | -5 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.8 | 15.6 | 22 | 15.9 | 3.9 | 258.2 | 14.6 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
272 | -4 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 4.7 | 267.9 | 16.3 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.7 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
273 | -3 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.8 | 15.6 | 21.9 | 15.9 | 5 | 264.1 | 18.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
274 | -2 | -6.9 | 0 | 0 | 16.3 | 16.7 | 16.5 | 16.5 | 16.8 | 15.6 | 21.9 | 15.9 | 4.7 | 258 | 18 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
275 | -1 | -6.9 | 0 | 0 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 22 | 15.9 | 4.3 | 260.3 | 16.4 | 15.4 | 15.2 | 15.3 | 15.7 | 16.5 | 15.6 | 15.2 | 15.7 | 15.6 | 16.6 | 15.8 | 15.2 | 15.2 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
276 | 0 | 129.8 | 51.92 | 60.6915 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 4 | 263.2 | 15.4 | 15.4 | 15.2 | 15.4 | 15.7 | 16.5 | 15.6 | 15.2 | 15.7 | 15.6 | 16.6 | 15.8 | 15.2 | 15.2 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
277 | 1 | 429.2 | 171.68 | 200.684 | 16.3 | 16.7 | 16.6 | 16.5 | 16.8 | 15.6 | 22 | 15.9 | 5.1 | 256.3 | 16.6 | 15.4 | 15.2 | 15.4 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
278 | 2 | 530.3 | 212.12 | 247.9561 | 16.3 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.9 | 4.8 | 254.9 | 16.7 | 15.4 | 15.2 | 15.4 | 15.7 | 16.5 | 15.6 | 15.2 | 15.6 | 15.5 | 16.6 | 15.8 | 15.2 | 15.1 | 15.8 | 15.4 | 15.5 | 17.1 | 16 | 15.9 | 15.9 | 17.4
279 | 3 | 531.4 | 212.56 | 248.4704 | 16.4 | 16.7 | 16.5 | 16.5 | 16.9 | 15.6 | 21.9 | 15.8 | 4 | 255.3 | 18.3 | 15.4 | 15.2 | 15.4 | 15.7 | 16.5 | 15.6 | 15.2 | 15.7 | 15.5 | 16.6 | 15.8 | 15.2 | 15.2 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
280 | 4 | 506.3 | 202.52 | 236.7342 | 16.3 | 16.7 | 16.6 | 16.5 | 16.9 | 15.6 | 21.9 | 15.8 | 4.1 | 248 | 19.5 | 15.4 | 15.5 | 16.3 | 15.7 | 16.6 | 15.6 | 15.2 | 15.7 | 15.5 | 16.6 | 15.7 | 15.2 | 15.2 | 15.8 | 15.4 | 15.5 | 17.1 | 15.9 | 15.9 | 15.9 | 17.4
281 | 5 | 481.8 | 192.72 | 225.2786 | 16.3 | 16.7 | 16.6 | 16.6 | 16.9 | 15.6 | 21.9 | 15.8 | 3.6 | 245.9 | 17.8 | 15.4 | 20.8 | 26 | 15.7 | 17.3 | 15.6 | 15.7 | 19.3 | 15.6 | 17 | 15.8 | 15.2 | 15.2 | 15.8 | 15.4 | 15.5 | 17.2 | 16 | 15.9 | 15.9 | 17.5
282 | 6 | 469.2 | 187.68 | 219.3871 | 16.4 | 16.7 | 16.7 | 16.7 | 17 | 15.7 | 22 | 15.8 | 4.7 | 239.3 | 14.7 | 15.4 | 36.1 | 58.4 | 15.8 | 19.6 | 15.6 | 20.9 | 33.8 | 15.7 | 19.1 | 15.8 | 15.2 | 15.2 | 15.8 | 15.5 | 15.5 | 17.3 | 15.9 | 16 | 16 | 17.5
283 | 7 | 467.2 | 186.88 | 218.452 | 16.5 | 16.8 | 16.9 | 16.9 | 21.3 | 15.7 | 22 | 15.8 | 6.2 | 238.8 | 13.5 | 15.4 | 58.6 | 87.9 | 15.9 | 22.6 | 15.6 | 30.6 | 56.4 | 15.9 | 21.5 | 15.8 | 15.3 | 15.4 | 15.8 | 15.5 | 15.7 | 17.5 | 15.9 | 16.1 | 16 | 17.6
284 | 8 | 458.4 | 183.36 | 214.3373 | 16.5 | 16.9 | 17.2 | 17.2 | 29.7 | 15.7 | 22 | 15.9 | 6.1 | 241.6 | 13.7 | 15.5 | 85.5 | 131.7 | 16.1 | 26.6 | 15.7 | 41.8 | 78.6 | 16.1 | 24.4 | 15.8 | 15.4 | 15.7 | 15.8 | 15.6 | 16.1 | 17.8 | 16 | 16.2 | 16.2 | 17.7
285 | 9 | 449.7 | 179.88 | 210.2694 | 16.7 | 16.9 | 17.5 | 17.6 | 39.2 | 15.8 | 21.9 | 15.9 | 5.8 | 248.1 | 13 | 15.5 | 129.2 | 196.2 | 16.4 | 33.8 | 15.7 | 60.2 | 117.1 | 16.6 | 30.3 | 15.8 | 15.8 | 16.2 | 15.8 | 15.8 | 16.2 | 18.1 | 15.9 | 16.3 | 16.3 | 17.8
286 | 10 | 443.7 | 177.48 | 207.4639 | 16.9 | 17 | 18.2 | 18.7 | 52.4 | 15.8 | 21.9 | 15.9 | 4 | 242.2 | 13.5 | 15.5 | 167.4 | 226.2 | 16.6 | 40.1 | 15.8 | 77.1 | 144.7 | 17.1 | 35.4 | 15.8 | 16.4 | 16.8 | 15.8 | 16 | 16.4 | 18.5 | 16 | 16.5 | 16.4 | 17.9
287 | 11 | 440 | 176 | 205.7339 | 17.5 | 17.7 | 19.6 | 20.2 | 64.8 | 15.8 | 22 | 15.9 | 3.8 | 239.8 | 14.7 | 15.6 | 200.2 | 266.6 | 16.9 | 45.9 | 16 | 88.7 | 164 | 17.5 | 39.8 | 15.8 | 17.3 | 17.5 | 15.8 | 16.4 | 17.1 | 18.9 | 16 | 16.8 | 16.6 | 18.1
288 | 12 | 439.1 | 175.64 | 205.313 | 18.3 | 18.6 | 21.2 | 22.3 | 76.3 | 15.9 | 22 | 15.8 | 2.8 | 235.9 | 14.6 | 15.7 | 222.3 | 285.6 | 17.2 | 51.5 | 16.2 | 101 | 181.7 | 17.8 | 43 | 15.8 | 18.6 | 18.6 | 15.8 | 17.3 | 18.7 | 19.5 | 16 | 17.4 | 18.2 | 18.3
289 | 13 | 438.4 | 175.36 | 204.9857 | 19.3 | 18.7 | 22.9 | 24.6 | 89.6 | 16 | 21.9 | 15.9 | 2.7 | 244.7 | 12.3 | 15.8 | 252.3 | 315.2 | 17.6 | 55.8 | 16.4 | 111 | 206.9 | 18.2 | 46.5 | 15.9 | 20.1 | 20 | 15.8 | 19.4 | 19.9 | 20.3 | 16 | 19.4 | 21.4 | 18.5
290 | 14 | 438.2 | 175.28 | 204.8922 | 20.9 | 19.7 | 25 | 27.2 | 111.5 | 16 | 21.9 | 15.9 | 3.5 | 219.4 | 11 | 15.9 | 303.9 | 371.8 | 18 | 63.9 | 16.7 | 137.1 | 274.7 | 19.2 | 54.2 | 15.9 | 22.1 | 21.7 | 15.8 | 21.9 | 21.3 | 21.1 | 16 | 22.7 | 28.8 | 18.9
291 | 15 | 438.7 | 175.48 | 205.126 | 22.8 | 21.7 | 27.8 | 29.9 | 129 | 16.1 | 21.9 | 15.9 | 3.4 | 228.8 | 10.7 | 16.1 | 355.4 | 426.6 | 18.6 | 76.9 | 17 | 161.6 | 321.3 | 20.2 | 66.3 | 16 | 24.4 | 23.6 | 15.8 | 23.7 | 23.3 | 21.6 | 16.1 | 25.8 | 31.6 | 19.3
292 | 16 | 438.6 | 175.44 | 205.0793 | 25 | 24.2 | 31.2 | 33.7 | 138.3 | 16.1 | 22 | 15.9 | 3.1 | 236.7 | 9.7 | 16.2 | 384.9 | 463.8 | 19.3 | 91.6 | 17.4 | 177.5 | 340.9 | 20.9 | 75.5 | 16.1 | 27.1 | 25.6 | 15.8 | 25.3 | 26 | 22.1 | 16.2 | 27.8 | 36.4 | 19.7
293 | 17 | 438.9 | 175.56 | 205.2195 | 27.8 | 26.2 | 34.6 | 37.7 | 151.8 | 16.2 | 22 | 15.9 | 3.1 | 216.8 | 8.2 | 16.5 | 445 | 515.1 | 20.2 | 104.6 | 17.8 | 202 | 390.2 | 21.9 | 85.7 | 16.2 | 30 | 27.6 | 15.8 | 27 | 28.6 | 22.5 | 16.3 | 30.5 | 40.8 | 20.1
294 | 18 | 439.5 | 175.8 | 205.5001 | 30.8 | 30.9 | 38.4 | 41.7 | 168.1 | 16.2 | 21.9 | 16 | 3.1 | 248.4 | 8.2 | 16.7 | 488.9 | 547.9 | 21.5 | 117 | 18.2 | 236.5 | 430 | 23.3 | 98.8 | 16.3 | 33 | 29.9 | 15.9 | 29.2 | 31.4 | 22.9 | 16.4 | 34.4 | 43.3 | 20.5
295 | 19 | 439.7 | 175.88 | 205.5936 | 34.4 | 35.7 | 42.4 | 45.2 | 183.6 | 16.3 | 21.9 | 16 | 3.9 | 236.9 | 9.1 | 16.9 | 518.5 | 578.2 | 22.9 | 129.9 | 18.7 | 257.8 | 448.5 | 24.4 | 105.5 | 16.5 | 36.1 | 32.2 | 15.9 | 31.2 | 34.6 | 23.5 | 16.6 | 37.2 | 47.6 | 21.2
296 | 20 | 441 | 176.4 | 206.2014 | 37.6 | 40 | 46 | 48.3 | 196.7 | 16.3 | 22 | 16.1 | 3.7 | 247.6 | 10.6 | 17.1 | 559.4 | 610.1 | 24.9 | 137.4 | 19.2 | 275.3 | 478.9 | 25.5 | 115.6 | 16.7 | 39.1 | 35.1 | 15.9 | 33.2 | 38.2 | 24.2 | 16.8 | 39.5 | 51.2 | 21.7
297 | 21 | 443.6 | 177.44 | 207.4171 | 39.7 | 45.7 | 49.6 | 52.2 | 201.8 | 16.4 | 22 | 16.2 | 3.1 | 277.9 | 10.2 | 17.4 | 593.8 | 632 | 27.2 | 145.8 | 19.7 | 290.7 | 510.6 | 27 | 125.1 | 16.9 | 42.2 | 37.9 | 16 | 35.9 | 41.8 | 24.9 | 17.1 | 41.3 | 54.1 | 22
298 | 22 | 444 | 177.6 | 207.6042 | 41.9 | 50.7 | 53.4 | 56.5 | 213 | 16.4 | 22 | 16.3 | 3.1 | 272.1 | 9.9 | 17.7 | 622.8 | 656.8 | 29.6 | 153.6 | 20.2 | 304.8 | 532.8 | 29.8 | 134.8 | 17.1 | 45.5 | 40.6 | 16.1 | 38.5 | 45.2 | 25.5 | 17.3 | 43.7 | 57.2 | 22.4
299 | 23 | 444.3 | 177.72 | 207.7444 | 45.2 | 53.7 | 57 | 60.5 | 225.3 | 16.5 | 21.9 | 16.4 | 3.3 | 256.8 | 9.2 | 18 | 660.4 | 677.5 | 32.2 | 159.9 | 20.7 | 326.5 | 573.3 | 35.5 | 146.4 | 17.4 | 48.9 | 43.7 | 16.1 | 41.4 | 48.7 | 26.2 | 17.6 | 46.9 | 60 | 22.9
300 | 24 | 444.7 | 177.88 | 207.9315 | 48.2 | 56.4 | 61.2 | 64.5 | 242 | 16.5 | 21.9 | 16.6 | 3.8 | 255.6 | 10.9 | 18.4 | 696 | 694.2 | 34.7 | 169.9 | 21.1 | 349 | 606.5 | 42.4 | 159.8 | 17.7 | 52.3 | 46.8 | 16.2 | 44.2 | 52 | 26.9 | 17.9 | 49.6 | 63.6 | 23.4
301 | 25 | 445.7 | 178.28 | 208.399 | 51.4 | 60.5 | 65.7 | 68.6 | 254.6 | 16.5 | 21.9 | 16.9 | 3.9 | 259.7 | 10.8 | 18.8 | 722.6 | 704.5 | 36.8 | 181.6 | 21.6 | 361.2 | 621.3 | 46.6 | 169 | 17.9 | 55.4 | 49.3 | 16.4 | 46.4 | 56.1 | 27.7 | 18.3 | 52.3 | 69.6 | 24
302 | 26 | 446.8 | 178.72 | 208.9134 | 54.4 | 65.5 | 70.7 | 72.8 | 264.5 | 16.5 | 22 | 17.2 | 4.3 | 254.4 | 10.1 | 19.3 | 745.4 | 716.6 | 38.6 | 187.4 | 22.1 | 375.8 | 646.4 | 50.6 | 180.6 | 18.3 | 58.3 | 52.2 | 16.5 | 48.9 | 60.5 | 28.5 | 18.7 | 56.2 | 73.3 | 24.7
303 | 27 | 446.6 | 178.64 | 208.8199 | 57.8 | 69.4 | 75.1 | 77 | 277.5 | 16.6 | 22 | 17.6 | 4.8 | 252.5 | 10.7 | 19.8 | 769.2 | 733.6 | 40.6 | 193.2 | 22.6 | 392.2 | 678.2 | 56.1 | 196.1 | 18.6 | 61.3 | 55.6 | 16.6 | 51.6 | 64.4 | 29 | 19 | 59.6 | 76.3 | 25.5
304 | 28 | 448.3 | 179.32 | 209.6147 | 60.6 | 73.9 | 79 | 81.5 | 281.3 | 16.6 | 22 | 18.2 | 5 | 243.8 | 12.3 | 20.3 | 790.3 | 744.6 | 42.7 | 202.6 | 23.2 | 403.7 | 706.6 | 61.7 | 208.3 | 18.9 | 64.1 | 59.2 | 16.8 | 54.4 | 68.5 | 29.1 | 19.4 | 62.9 | 78.5 | 25.9
305 | 29 | 447.6 | 179.04 | 209.2874 | 62.9 | 77.1 | 83 | 85.4 | 287.9 | 16.6 | 22 | 18.9 | 4.6 | 262.7 | 12.3 | 20.9 | 800.6 | 747.8 | 44.6 | 211.4 | 23.9 | 408.3 | 717.1 | 66.5 | 216.7 | 19.3 | 66.9 | 62.7 | 17 | 57.4 | 73.3 | 29.8 | 19.8 | 65.9 | 82.4 | 26.6
306 | 30 | 445.8 | 178.32 | 208.4458 | 65.6 | 80.9 | 87.6 | 89.6 | 292.7 | 16.7 | 22 | 19.6 | 5.2 | 253.8 | 13.3 | 21.5 | 807.3 | 754.6 | 46.7 | 224.6 | 24.7 | 417.5 | 733 | 71.5 | 229.8 | 19.6 | 69.7 | 66.1 | 17.2 | 60.5 | 77.6 | 30.6 | 20.2 | 68.8 | 89.2 | 27.2
307 | 31 | 446.1 | 178.44 | 208.5861 | 68 | 84.6 | 91.6 | 94 | 301.5 | 16.7 | 22 | 20.4 | 5.1 | 245.6 | 15 | 22.2 | 812.4 | 747 | 48.7 | 232.4 | 25.6 | 426 | 744 | 75.7 | 238.8 | 20.1 | 72.7 | 69.5 | 17.4 | 63.9 | 82.2 | 31.5 | 20.6 | 70.5 | 93 | 27.9
308 | 32 | 448.4 | 179.36 | 209.6615 | 69.5 | 89.2 | 95.9 | 98.2 | 310.2 | 16.8 | 22 | 21 | 3.8 | 257.1 | 13.6 | 22.8 | 825.4 | 757.5 | 50.7 | 236.8 | 26.6 | 436.7 | 757.8 | 80.2 | 250.1 | 20.5 | 76.1 | 73 | 17.6 | 67.1 | 86.4 | 32.4 | 21 | 72.8 | 98.2 | 28.3
309 | 33 | 449.4 | 179.76 | 210.1291 | 71.7 | 93 | 100.4 | 102.6 | 316.6 | 16.8 | 22 | 21.5 | 3.4 | 234.6 | 12.2 | 23.5 | 839.8 | 768.2 | 52.9 | 244.8 | 27.7 | 450.3 | 768.2 | 85.1 | 263.1 | 21 | 79.8 | 76.8 | 17.8 | 70.1 | 90.3 | 32.9 | 21.5 | 75.4 | 101.6 | 28.9
310 | 34 | 451.7 | 180.68 | 211.2045 | 74.2 | 96.5 | 104.1 | 106.9 | 318 | 16.8 | 22 | 22 | 3.5 | 238.2 | 12.5 | 24.3 | 850.1 | 759.7 | 55 | 249.2 | 28.8 | 460.7 | 779.7 | 88.9 | 273.2 | 21.5 | 83.9 | 80.4 | 18.1 | 73.9 | 93.7 | 32.9 | 22 | 77.7 | 104.1 | 29.5
311 | 35 | 451.9 | 180.76 | 211.298 | 76.2 | 100.3 | 107.3 | 111.2 | 320.8 | 17 | 21.9 | 22.6 | 3.3 | 248.8 | 13.1 | 25 | 863.3 | 763.9 | 57.1 | 252.7 | 30.1 | 468 | 787.6 | 92.4 | 283.3 | 22 | 87.8 | 84.2 | 18.3 | 77.6 | 97.3 | 33.3 | 22.5 | 80.3 | 107.6 | 30.2
312 | 36 | 451.8 | 180.72 | 211.2513 | 76.7 | 105.2 | 110.5 | 114.8 | 323.9 | 17 | 21.9 | 23.2 | 3.7 | 232.2 | 11.1 | 25.7 | 873 | 768.5 | 59.4 | 256.9 | 31.3 | 475.1 | 787.6 | 95.8 | 293 | 22.5 | 91.8 | 88 | 18.6 | 81.7 | 100.7 | 33.9 | 23 | 84 | 111.4 | 31
313 | 37 | 452.2 | 180.88 | 211.4383 | 78.1 | 110.3 | 114 | 117.9 | 331.6 | 17 | 21.9 | 23.7 | 5 | 247.7 | 8.3 | 26.5 | 879.5 | 762.1 | 61.7 | 262.9 | 32.7 | 484.3 | 795.6 | 99.8 | 304 | 23 | 95.8 | 91.9 | 18.9 | 85 | 103.7 | 34.7 | 23.5 | 87.4 | 113 | 31.7
314 | 38 | 452.8 | 181.12 | 211.7188 | 80.9 | 113.4 | 117.7 | 120.7 | 345.1 | 17.1 | 22 | 24.4 | 4.7 | 248.8 | 7.6 | 27.3 | 885.7 | 775.5 | 64.5 | 272.7 | 34.1 | 494.4 | 806 | 104.9 | 319.9 | 23.6 | 99.9 | 95.8 | 19.2 | 87.7 | 107.3 | 35.7 | 24.1 | 89.6 | 115.2 | 32.2
315 | 39 | 453.2 | 181.28 | 211.9059 | 83.7 | 116.2 | 121.2 | 124.2 | 351 | 17.3 | 21.9 | 25.1 | 5 | 254.1 | 6.1 | 28.1 | 885.8 | 790.6 | 67.1 | 284 | 35.6 | 498.6 | 810.8 | 108.7 | 330 | 24.1 | 104.6 | 99.5 | 19.5 | 90.5 | 111.2 | 36.9 | 24.6 | 92.4 | 117.7 | 32.9
316 | 40 | 454.7 | 181.88 | 212.6072 | 86.9 | 119.7 | 124.7 | 127.7 | 354.3 | 17.5 | 21.9 | 25.6 | 3.9 | 241.4 | 6.4 | 28.9 | 892.1 | 795.9 | 69.4 | 291.8 | 37.2 | 503.7 | 816.3 | 112.1 | 341.4 | 24.8 | 110.2 | 103.2 | 19.8 | 93.4 | 114.7 | 37.5 | 25.1 | 94.6 | 120.6 | 33.6
317 | 41 | 454.4 | 181.76 | 212.467 | 90.1 | 121.8 | 127.7 | 130.8 | 354.3 | 17.7 | 21.9 | 26.1 | 3.9 | 263.9 | 7.5 | 29.8 | 893.6 | 802.5 | 71.8 | 302.6 | 39.1 | 505.5 | 818.7 | 113.9 | 354.8 | 25.4 | 117.9 | 106.8 | 20.1 | 96.3 | 118 | 38.4 | 25.7 | 96.9 | 123 | 34.3
318 | 42 | 455.4 | 182.16 | 212.9345 | 91.9 | 124.1 | 130.5 | 133.4 | 351.9 | 17.8 | 21.9 | 26.5 | 4.8 | 232.4 | 10 | 30.6 | 897.5 | 799 | 74.2 | 309 | 41.1 | 513 | 825.4 | 116.8 | 364.5 | 26 | 126.7 | 110.3 | 20.5 | 98.7 | 121 | 39.3 | 26.2 | 99.3 | 125.6 | 35.1
319 | 43 | 454.5 | 181.8 | 212.5137 | 93.5 | 126 | 133.7 | 135.9 | 350.4 | 17.9 | 21.9 | 26.9 | 4.3 | 204.1 | 10.1 | 31.5 | 892.7 | 794.4 | 76.5 | 312.2 | 43.4 | 511.1 | 813.9 | 118.8 | 369.3 | 26.7 | 135.8 | 113.4 | 20.8 | 101.7 | 123.7 | 39.9 | 26.8 | 102.1 | 128 | 35.7
320 | 44 | 456 | 182.4 | 213.2151 | 95.7 | 128.6 | 137 | 138.2 | 345.2 | 17.9 | 21.9 | 27.3 | 5.4 | 235.3 | 6.8 | 32.4 | 895.9 | 789.8 | 78.9 | 317.4 | 46.1 | 511.8 | 804.1 | 120.4 | 375.7 | 27.3 | 143.3 | 116.7 | 21.2 | 104.9 | 126.7 | 41.2 | 27.3 | 104.6 | 131 | 36.4
321 | 45 | 457.2 | 182.88 | 213.7762 | 97.3 | 131.3 | 139.7 | 141.2 | 343.4 | 17.9 | 21.9 | 27.7 | 5.1 | 274.4 | 5.6 | 33.3 | 893.8 | 764.1 | 80.9 | 319.1 | 49 | 508.8 | 794.6 | 122 | 378.3 | 28 | 149.9 | 119.9 | 21.5 | 107.4 | 129.3 | 42.2 | 27.9 | 107.4 | 133.4 | 37.2
322 | 46 | 458.5 | 183.4 | 214.384 | 97.7 | 133.8 | 142.5 | 144.2 | 341 | 17.9 | 21.9 | 28.1 | 4.4 | 230.2 | 7.5 | 34.2 | 891 | 763.4 | 82.6 | 322.9 | 52.3 | 507.2 | 790 | 123.1 | 380.5 | 28.7 | 156.4 | 123.2 | 21.9 | 109.6 | 131.7 | 43.2 | 28.5 | 109.3 | 135.4 | 37.8
323 | 47 | 458.4 | 183.36 | 214.3373 | 99.9 | 135.7 | 145.4 | 146.6 | 341.7 | 17.9 | 21.9 | 28.4 | 5.4 | 251.2 | 10.1 | 35.2 | 885.7 | 768.9 | 84.2 | 328.3 | 55.9 | 502.1 | 781.6 | 124.2 | 384.4 | 29.5 | 163 | 126.6 | 22.3 | 111.7 | 134.4 | 44.3 | 29.1 | 111.1 | 137.7 | 38.4
324 | 48 | 459.6 | 183.84 | 214.8984 | 102.8 | 137.7 | 147.6 | 148.8 | 339.4 | 18 | 21.9 | 28.8 | 5.9 | 243.4 | 11.4 | 36.1 | 890.6 | 756 | 85.6 | 330.4 | 59.8 | 497.8 | 777.1 | 125.4 | 389 | 30.2 | 170.4 | 130.1 | 22.6 | 113.5 | 137 | 45.5 | 29.7 | 112.7 | 140.1 | 39
325 | 49 | 461.3 | 184.52 | 215.6932 | 104.4 | 141.3 | 149.8 | 150.4 | 340.2 | 18.1 | 21.9 | 29 | 4.2 | 267.1 | 9.7 | 37 | 892.1 | 744.1 | 86.9 | 329.3 | 64 | 497.9 | 779.8 | 127.2 | 393.5 | 30.9 | 179.1 | 133.7 | 23.1 | 115.6 | 139.4 | 45.8 | 30.3 | 114.6 | 142.2 | 39.9
326 | 50 | 459.8 | 183.92 | 214.9919 | 106.9 | 143.1 | 151.7 | 152.3 | 340 | 18.2 | 21.9 | 29.3 | 3.7 | 252.2 | 8.9 | 38 | 887 | 721.6 | 88.1 | 328.7 | 68.3 | 498 | 775.4 | 129.5 | 396 | 31.6 | 187.2 | 138.2 | 23.4 | 118.2 | 141.8 | 46.1 | 30.9 | 117 | 145.2 | 40.5
327 | 51 | 458.8 | 183.52 | 214.5243 | 109.4 | 145.4 | 152.6 | 154.4 | 339.7 | 18.2 | 21.9 | 29.7 | 4.9 | 261.6 | 10.1 | 38.9 | 893.4 | 717.2 | 89.4 | 328.8 | 72.8 | 498.7 | 775.7 | 132.7 | 401.6 | 32.4 | 193.4 | 144.5 | 23.8 | 120.7 | 143.9 | 46.4 | 31.5 | 120.2 | 147.5 | 41.3
328 | 52 | 459.2 | 183.68 | 214.7113 | 111.3 | 147.9 | 153.9 | 156.4 | 338 | 18.2 | 21.9 | 30 | 4.5 | 245.5 | 9.6 | 39.9 | 898.6 | 714.1 | 90.6 | 329.7 | 77.5 | 501.8 | 776.8 | 136.2 | 406.5 | 33.1 | 198.4 | 151.4 | 24.2 | 123.3 | 145.3 | 47.2 | 32.2 | 123 | 150 | 42.2
329 | 53 | 461.9 | 184.76 | 215.9738 | 111.9 | 149.9 | 155.5 | 158.4 | 339.5 | 18.2 | 21.9 | 30.3 | 4.9 | 246.9 | 12.6 | 40.8 | 904.4 | 707.6 | 92.1 | 330.9 | 82.3 | 501.6 | 779.3 | 140.2 | 413.3 | 33.9 | 202.8 | 157.9 | 24.6 | 125.5 | 146.4 | 48.6 | 32.8 | 124.6 | 153 | 42.9
330 | 54 | 461.5 | 184.6 | 215.7868 | 112.7 | 151.9 | 156.4 | 160.8 | 340.2 | 18.2 | 21.9 | 30.6 | 4.9 | 275 | 12.6 | 41.8 | 905.1 | 712 | 93.5 | 333.3 | 87.2 | 500 | 775 | 143.6 | 418.2 | 34.7 | 207.4 | 163.7 | 25 | 127.1 | 147.9 | 49.3 | 33.5 | 127.1 | 154.5 | 43.7
331 | 55 | 460.2 | 184.08 | 215.1789 | 115 | 153.6 | 158.5 | 162.9 | 345.3 | 18.2 | 21.9 | 30.9 | 3.6 | 259.7 | 15.1 | 42.8 | 901.6 | 718.6 | 94 | 337.7 | 92.5 | 498.6 | 775.3 | 147.1 | 422.9 | 35.4 | 212.5 | 169.5 | 25.5 | 128.9 | 149.7 | 50.2 | 34.1 | 128.8 | 156.6 | 44.1
332 | 56 | 461.5 | 184.6 | 215.7868 | 118.2 | 154.9 | 161.2 | 165.2 | 348.2 | 18.2 | 21.9 | 31.1 | 2.5 | 253.7 | 16.3 | 43.8 | 897.9 | 718.1 | 94.5 | 344.8 | 97.8 | 498.2 | 782 | 149.9 | 429.7 | 36.2 | 217.8 | 175.1 | 25.9 | 130.8 | 151.6 | 51.4 | 34.8 | 131.1 | 159 | 44.7
333 | 57 | 462.6 | 185.04 | 216.3011 | 120.1 | 156.5 | 163.3 | 166.9 | 351.8 | 18.2 | 21.9 | 31.3 | 3 | 257.4 | 14.1 | 44.8 | 901.7 | 729.8 | 95 | 352.2 | 103.4 | 499.5 | 789 | 153.5 | 438.9 | 37 | 225 | 180.2 | 26.3 | 132.3 | 153.6 | 53.1 | 35.5 | 132.4 | 161.1 | 45.5
334 | 58 | 461.9 | 184.76 | 215.9738 | 122.2 | 158.1 | 164.8 | 168.1 | 355.7 | 18.2 | 21.9 | 31.6 | 3.3 | 265.4 | 12.1 | 45.8 | 897.3 | 746.3 | 95.9 | 360.8 | 109.2 | 504.5 | 797.1 | 158.6 | 449.3 | 37.8 | 230.1 | 184.8 | 26.7 | 134.2 | 156 | 53.8 | 36.2 | 134.6 | 162.8 | 46.3
335 | 59 | 462.5 | 185 | 216.2543 | 123.5 | 160.3 | 166.3 | 170.1 | 357 | 18.3 | 21.9 | 31.9 | 3.7 | 283.1 | 10.1 | 46.8 | 901.5 | 747.2 | 97.3 | 366.4 | 115.2 | 508.7 | 804.5 | 164.1 | 459.2 | 38.7 | 232.9 | 188.9 | 27.1 | 136.1 | 158.3 | 54 | 36.8 | 136 | 164.4 | 47.1
336 | 60 | 464.6 | 185.84 | 217.2363 | 125.3 | 162 | 167.5 | 171.8 | 357.7 | 18.4 | 21.9 | 32.2 | 4.1 | 262 | 11.9 | 47.9 | 900.6 | 750.4 | 98.1 | 372.2 | 121.5 | 508.2 | 802.6 | 168.4 | 466.3 | 39.5 | 236.2 | 192.6 | 27.5 | 137.9 | 160.4 | 54 | 37.5 | 137.7 | 166.4 | 47.9
337 | 61 | 466.3 | 186.52 | 218.0311 | 127.1 | 164.2 | 168.9 | 173.2 | 356.7 | 18.4 | 21.9 | 32.6 | 4.8 | 273.5 | 14.1 | 48.9 | 899.7 | 752.4 | 98.6 | 377.1 | 128.1 | 506.3 | 801.4 | 172.5 | 471.6 | 40.4 | 239.1 | 196.2 | 28 | 139.7 | 162.5 | 54.3 | 38.2 | 140 | 167.8 | 48.7
338 | 62 | 468 | 187.2 | 218.826 | 128.3 | 165.1 | 170.7 | 174.3 | 355.5 | 18.3 | 21.9 | 32.8 | 4.9 | 268.4 | 13.7 | 50 | 901.9 | 743.2 | 98.6 | 380 | 135 | 510 | 800.9 | 176.9 | 478.6 | 41.4 | 239.6 | 199.8 | 28.4 | 140.9 | 163.9 | 54.8 | 38.9 | 141.3 | 169.1 | 49.6
339 | 63 | 467.2 | 186.88 | 218.452 | 129.3 | 164.8 | 172.2 | 175.6 | 355.9 | 18.4 | 21.9 | 33 | 4.6 | 260 | 13.2 | 51.1 | 902.1 | 737.3 | 98.5 | 384.7 | 142.4 | 508.8 | 792.9 | 180.2 | 482.7 | 42.3 | 240.2 | 203.4 | 28.8 | 142.4 | 165.8 | 55.1 | 39.6 | 142.4 | 170.3 | 50.2
340 | 64 | 467.1 | 186.84 | 218.4052 | 130.1 | 164.4 | 173.3 | 176.5 | 354.1 | 18.4 | 21.8 | 33.3 | 5.6 | 249.3 | 13.3 | 52.2 | 906 | 733.8 | 98.6 | 387.8 | 150.6 | 502.6 | 787.6 | 182.2 | 486.5 | 43.2 | 239.5 | 206.4 | 29.3 | 143.8 | 167.1 | 55.4 | 40.3 | 143.5 | 171.5 | 50.9
341 | 65 | 467.7 | 187.08 | 218.6857 | 130 | 164.4 | 174.6 | 177.2 | 350.2 | 18.4 | 21.8 | 33.6 | 5.7 | 266.5 | 13.9 | 53.3 | 906.5 | 734.9 | 98.7 | 392.2 | 158.7 | 505.2 | 796.5 | 185.2 | 493.9 | 44.2 | 239.2 | 209.7 | 29.7 | 145 | 168.6 | 56.3 | 41 | 144.6 | 172.6 | 51.5
342 | 66 | 467.7 | 187.08 | 218.6857 | 130.7 | 163.8 | 175.4 | 178.2 | 351.8 | 18.5 | 21.8 | 33.8 | 5.2 | 266.4 | 15.5 | 54.4 | 909.3 | 719.9 | 99.2 | 393 | 166 | 506.6 | 797.2 | 188.6 | 500.3 | 45.1 | 239.5 | 213.3 | 30.2 | 146.5 | 170 | 57.1 | 41.7 | 146.3 | 173.6 | 52.2
343 | 67 | 467.9 | 187.16 | 218.7793 | 132.2 | 162.9 | 175.9 | 179 | 350.2 | 18.4 | 21.8 | 34 | 4.4 | 269.4 | 14.7 | 55.5 | 907.6 | 717.1 | 100.3 | 394.3 | 173.3 | 506.9 | 801.8 | 191.5 | 505.3 | 46 | 238.6 | 216.7 | 30.6 | 148.2 | 171.6 | 57.6 | 42.4 | 147.3 | 174.6 | 53
344 | 68 | 467.6 | 187.04 | 218.639 | 133.2 | 162.6 | 176.9 | 180.1 | 349.1 | 18.4 | 21.8 | 34.2 | 3.8 | 256.5 | 14.1 | 56.7 | 907.8 | 731.7 | 102 | 399.8 | 180.4 | 507.4 | 804.3 | 194.3 | 510.8 | 47 | 242.4 | 220.4 | 31.1 | 149.7 | 172.7 | 58.6 | 43.1 | 148.7 | 175.7 | 53.6
345 | 69 | 468.9 | 187.56 | 219.2468 | 132.8 | 163.5 | 177.5 | 180.8 | 349 | 18.4 | 21.8 | 34.4 | 3.4 | 243.6 | 13.8 | 57.8 | 907.3 | 753 | 104.2 | 412.3 | 187 | 506.4 | 810.4 | 197 | 517.4 | 47.9 | 248.3 | 223.4 | 31.6 | 151.6 | 173.8 | 59.6 | 43.7 | 150.2 | 177 | 54.3
346 | 70 | 468.6 | 187.44 | 219.1066 | 132.3 | 163.7 | 178.1 | 181.6 | 350.5 | 18.5 | 21.8 | 34.5 | 3 | 257.6 | 11.6 | 59 | 898.9 | 763.5 | 106.8 | 419.5 | 193.9 | 510.1 | 807 | 200 | 522.7 | 48.9 | 251.6 | 225.9 | 32.1 | 153.1 | 175.3 | 61.1 | 44.4 | 152.1 | 177.8 | 54.9
347 | 71 | 469.9 | 187.96 | 219.7144 | 132.5 | 164.7 | 178.9 | 182.5 | 351.7 | 18.5 | 21.8 | 34.6 | 3.4 | 236.9 | 10.9 | 60.2 | 899.1 | 774.5 | 110.1 | 425.1 | 201.6 | 507.3 | 803.6 | 202.8 | 525.9 | 49.9 | 256.3 | 228.2 | 32.5 | 154.6 | 176.5 | 61.7 | 45 | 153.8 | 178.5 | 55.5
348 | 72 | 469.4 | 187.76 | 219.4806 | 133.6 | 167 | 180.1 | 184 | 351.8 | 18.6 | 21.8 | 34.7 | 3.2 | 228.1 | 10.5 | 61.4 | 896.6 | 784.2 | 114 | 433.1 | 208.7 | 504.4 | 801.2 | 205.4 | 529.1 | 50.9 | 262 | 229.8 | 33 | 156.3 | 178 | 62.4 | 45.7 | 154.4 | 179.5 | 56.1
349 | 73 | 469.1 | 187.64 | 219.3403 | 135.1 | 168.9 | 181.2 | 184.9 | 354.4 | 18.6 | 21.8 | 34.7 | 2.3 | 244.7 | 10 | 62.6 | 898.5 | 791 | 118.9 | 441.2 | 215.2 | 502 | 802.6 | 207.9 | 535.3 | 51.9 | 268 | 230.8 | 33.5 | 157.8 | 179 | 62.9 | 46.3 | 155.2 | 180.4 | 56.7
350 | 74 | 469.1 | 187.64 | 219.3403 | 135.5 | 170.2 | 181.9 | 185.5 | 354.6 | 18.6 | 21.8 | 34.8 | 2.6 | 244.6 | 11 | 63.8 | 904 | 795 | 124.5 | 449.6 | 220.5 | 503.4 | 804.7 | 210.9 | 542.1 | 53 | 271.7 | 231.7 | 34 | 158.9 | 179.8 | 63.4 | 46.9 | 156 | 181.4 | 57.2
351 | 75 | 469.1 | 187.64 | 219.3403 | 135.3 | 172.1 | 182.5 | 186.2 | 356.2 | 18.6 | 21.8 | 35 | 3.1 | 248.7 | 11.4 | 65 | 907.6 | 795.7 | 130.7 | 458.5 | 225.3 | 505 | 804 | 214.6 | 547 | 54.1 | 273.7 | 232.4 | 34.4 | 159.8 | 180.9 | 64 | 47.5 | 156.8 | 182.2 | 58.1
352 | 76 | 470.5 | 188.2 | 219.995 | 135.1 | 172.2 | 182.8 | 186.8 | 354 | 18.7 | 21.8 | 35.2 | 4 | 241.3 | 11.2 | 66.2 | 901.6 | 786.3 | 137.4 | 462.2 | 229.9 | 509 | 812.3 | 218.9 | 553 | 55.2 | 275.5 | 232.9 | 34.9 | 161.1 | 183.1 | 64.5 | 48.1 | 157.6 | 183 | 58.7
353 | 77 | 470.4 | 188.16 | 219.9482 | 135.6 | 172.4 | 183.1 | 187.7 | 353 | 18.7 | 21.8 | 35.5 | 5.3 | 256.8 | 10.9 | 67.5 | 897.2 | 773 | 144.6 | 464.8 | 234.3 | 506.7 | 815.9 | 222.9 | 556.8 | 56.4 | 278.3 | 233.4 | 35.4 | 162.9 | 184.8 | 65.3 | 48.7 | 158.4 | 183.6 | 59.4
354 | 78 | 467.5 | 187 | 218.5922 | 136.8 | 171.1 | 184.3 | 188.8 | 354.3 | 18.7 | 21.8 | 35.8 | 6 | 246.6 | 10.3 | 68.8 | 901.6 | 781.3 | 151.7 | 471.9 | 238.3 | 508.7 | 815.3 | 227 | 561.3 | 57.7 | 280 | 234.3 | 35.8 | 164.8 | 185.3 | 66.1 | 49.3 | 159.5 | 184.2 | 60
355 | 79 | 466.6 | 186.64 | 218.1714 | 137.4 | 171.1 | 185.2 | 189.2 | 351.4 | 18.7 | 21.8 | 36.1 | 5.3 | 246.9 | 10.4 | 70.1 | 900.3 | 796.4 | 158.7 | 479.6 | 241.8 | 507.1 | 812.8 | 230.4 | 564.9 | 59 | 283.4 | 235.4 | 36.3 | 166.1 | 186 | 67.1 | 49.9 | 160.4 | 185 | 60.7
356 | 80 | 469.4 | 187.76 | 219.4806 | 138 | 172.1 | 185.8 | 189.4 | 352.9 | 18.8 | 21.8 | 36.3 | 6.2 | 249 | 11 | 71.4 | 901.1 | 809.8 | 166.3 | 489.9 | 244.8 | 511.9 | 820.4 | 233.9 | 573 | 61.4 | 286.4 | 237.1 | 36.8 | 166.6 | 186.4 | 68.1 | 50.4 | 162 | 185.7 | 61.2
357 | 81 | 468.3 | 187.32 | 218.9663 | 139.2 | 173.5 | 186.1 | 189.8 | 354.6 | 18.8 | 21.8 | 36.5 | 6.4 | 238.4 | 11.8 | 72.7 | 892.7 | 819.8 | 173.8 | 498.2 | 247.9 | 516 | 819.6 | 236.8 | 578.4 | 62.6 | 288.3 | 238 | 37.3 | 167.3 | 187.1 | 69.2 | 51 | 163.8 | 186 | 61.8
358 | 82 | 469.7 | 187.88 | 219.6209 | 140.6 | 175 | 187 | 189.9 | 355 | 18.9 | 21.8 | 36.9 | 6.3 | 244.1 | 14.4 | 74 | 888.6 | 830.7 | 181.1 | 505.9 | 250.6 | 518.9 | 817.4 | 238.9 | 582.7 | 63.5 | 291.1 | 238.7 | 37.7 | 168.3 | 187.9 | 69.3 | 51.6 | 164.4 | 186.4 | 62.3
359 | 83 | 468 | 187.2 | 218.826 | 142.2 | 175.2 | 187.4 | 189.9 | 355.2 | 19 | 21.8 | 37.2 | 6.5 | 246.6 | 13 | 75.3 | 894.7 | 819 | 188.2 | 512.7 | 253.1 | 517.2 | 812.7 | 240.3 | 586 | 64.8 | 293 | 239.7 | 38.2 | 169.2 | 188.8 | 69.7 | 52.1 | 165.4 | 186.7 | 62.9
360 | 84 | 469.1 | 187.64 | 219.3403 | 143.2 | 175.7 | 187.5 | 190.3 | 353 | 19 | 21.8 | 37.3 | 5 | 240.7 | 12.1 | 76.7 | 882.2 | 826.3 | 195.1 | 518.4 | 255.1 | 521.2 | 819.7 | 242.1 | 591.7 | 66.1 | 295.7 | 241.2 | 38.7 | 170.2 | 190.4 | 70.6 | 52.7 | 166 | 187.2 | 63.5
361 | 85 | 469.6 | 187.84 | 219.5741 | 142.6 | 178 | 187.2 | 191.5 | 354.4 | 19.1 | 21.8 | 37.5 | 3.7 | 231.9 | 14.7 | 78 | 869.6 | 833.9 | 200.7 | 521.2 | 256.9 | 527.8 | 821.5 | 244.7 | 597.5 | 67.5 | 298.8 | 242 | 39.1 | 171.5 | 192.5 | 71.6 | 53.2 | 167.3 | 187.9 | 63.9
362 | 86 | 469.7 | 187.88 | 219.6209 | 141.6 | 179 | 187.2 | 192.3 | 360.9 | 19.2 | 21.8 | 37.5 | 4.2 | 234.2 | 15.3 | 79.5 | 869.4 | 828.7 | 205.3 | 525.5 | 259 | 530.9 | 826.8 | 247.7 | 601.5 | 69 | 302.5 | 243.8 | 39.6 | 172.7 | 193.4 | 72.1 | 53.8 | 168.9 | 188.7 | 64.5
363.1 | 87.1 | 469.2 | 187.68 | 219.3871 | 141.5 | 180.8 | 188.5 | 192.9 | 366.9 | 19.2 | 21.8 | 37.7 | 6.3 | 232.3 | 17.5 | 80.9 | 867.3 | 839.3 | 210.5 | 532.8 | 261 | 531.4 | 828.6 | 249.9 | 606.4 | 70.7 | 308.2 | 245.7 | 40.2 | 173.6 | 193.9 | 72.6 | 54.4 | 169.9 | 189.4 | 65.1
364.1 | 88.1 | 469.6 | 187.84 | 219.5741 | 141.6 | 181.5 | 190 | 193.5 | 368.8 | 19.2 | 21.8 | 37.8 | 6.5 | 228.9 | 17.4 | 82.3 | 868 | 840 | 216.9 | 538.8 | 262.7 | 532.9 | 832.4 | 251.8 | 610.9 | 72.3 | 312.1 | 247 | 40.6 | 174.7 | 194.7 | 73.7 | 54.9 | 170.7 | 190.3 | 65.8
365.1 | 89.1 | 469.7 | 187.88 | 219.6209 | 142.3 | 183.6 | 190.9 | 193.6 | 370.8 | 19.3 | 21.7 | 37.9 | 6 | 242.5 | 16.2 | 83.7 | 875.5 | 834.5 | 222.4 | 543.3 | 264.8 | 533.2 | 836 | 253.2 | 615.6 | 73.9 | 316.7 | 248.7 | 41.1 | 175.9 | 195.4 | 74.8 | 55.5 | 171.9 | 190.8 | 66.5
366.1 | 90.1 | 470 | 188 | 219.7612 | 143.6 | 185.3 | 192 | 193.5 | 371.5 | 19.3 | 21.7 | 37.9 | 5.6 | 248.9 | 17.1 | 85.2 | 885.2 | 830.9 | 226.7 | 546.1 | 267.2 | 530.9 | 832 | 254.1 | 618.3 | 75.5 | 322.8 | 250.4 | 41.6 | 176.8 | 196.3 | 75.4 | 56.1 | 172.7 | 191.3 | 67.2
367.1 | 91.1 | 470.1 | 188.04 | 219.8079 | 144.1 | 186.4 | 192.4 | 194.5 | 368.6 | 19.3 | 21.7 | 37.9 | 5.7 | 250.2 | 17.8 | 86.7 | 892 | 829.3 | 230.2 | 549.5 | 269.3 | 529.6 | 829.2 | 254.9 | 620.6 | 77.2 | 327.4 | 251.9 | 42.1 | 177.5 | 197.1 | 75.9 | 56.7 | 173.3 | 191.3 | 67.6
368.1 | 92.1 | 468.7 | 187.48 | 219.1533 | 145.8 | 187.2 | 193.1 | 195.4 | 366.8 | 19.4 | 21.7 | 37.9 | 6.7 | 256.5 | 17.6 | 88.2 | 897.3 | 816.3 | 232.8 | 550.9 | 271.1 | 531.4 | 827.3 | 256.1 | 624 | 78.8 | 327.2 | 253.1 | 42.6 | 178.4 | 198.1 | 76.5 | 57.3 | 174.4 | 191 | 68.2
369.1 | 93.1 | 470 | 188 | 219.7612 | 146.2 | 187.6 | 193.3 | 196 | 367.7 | 19.5 | 21.7 | 37.8 | 5.9 | 256.3 | 18.3 | 89.8 | 902.9 | 809.8 | 234.7 | 553.3 | 273.1 | 534.1 | 826.6 | 257.5 | 626.8 | 80.6 | 326.6 | 254.3 | 43.1 | 179.2 | 198.9 | 77.1 | 57.8 | 175.2 | 192.1 | 68.8
370.1 | 94.1 | 467.6 | 187.04 | 218.639 | 147.6 | 188 | 193.9 | 195.6 | 367.1 | 19.5 | 21.7 | 37.8 | 6.1 | 249.5 | 16.3 | 91.4 | 900.7 | 797.2 | 236.8 | 553.2 | 275.1 | 533.1 | 821.7 | 258.9 | 628.3 | 83 | 325.7 | 256.4 | 43.6 | 180.2 | 199.7 | 78 | 58.4 | 176.1 | 193.2 | 69.4
371.1 | 95.1 | 467.6 | 187.04 | 218.639 | 148.4 | 188.5 | 194.5 | 195.5 | 364.9 | 19.6 | 21.7 | 37.8 | 5.5 | 235.5 | 15.9 | 93.1 | 894.4 | 795.6 | 238.1 | 555 | 276.5 | 529.6 | 813.6 | 260.4 | 629.2 | 88.2 | 327.1 | 258.1 | 44.1 | 181 | 200.5 | 78.7 | 58.9 | 176.8 | 193.4 | 70.1
372.1 | 96.1 | 467.9 | 187.16 | 218.7793 | 149.3 | 189.1 | 195.7 | 195.9 | 364.5 | 19.7 | 21.7 | 37.9 | 6.1 | 247 | 17.5 | 94.8 | 894.2 | 783.5 | 240.1 | 553.8 | 277.6 | 527.9 | 817.2 | 261.8 | 631 | 93.4 | 328.1 | 260.3 | 44.6 | 181.7 | 201 | 79.3 | 59.5 | 176.6 | 194.1 | 70.8
373.1 | 97.1 | 467.7 | 187.08 | 218.6857 | 151.9 | 190 | 196.8 | 196.3 | 363.5 | 19.7 | 21.7 | 38.1 | 4.5 | 233.7 | 16.9 | 96.6 | 895.3 | 786.9 | 241.7 | 556.5 | 278.4 | 526.7 | 815.6 | 263.5 | 631.9 | 95.9 | 330.5 | 262.1 | 45 | 182.7 | 201.6 | 79.9 | 60 | 176.8 | 194.8 | 71.3
374.1 | 98.1 | 465.7 | 186.28 | 217.7506 | 153.6 | 190.5 | 198 | 196.6 | 362.6 | 19.8 | 21.7 | 38.2 | 5.4 | 243.8 | 16 | 98.3 | 896 | 799 | 243.2 | 561.9 | 279.6 | 524 | 813.8 | 265.6 | 634.4 | 97.9 | 335.1 | 264.8 | 45.5 | 183.7 | 202.4 | 80.7 | 60.6 | 177.3 | 195.7 | 72
375.1 | 99.1 | 466.1 | 186.44 | 217.9376 | 154.8 | 190.4 | 199 | 196.9 | 365.8 | 19.8 | 21.7 | 38.4 | 5.2 | 251.1 | 14.4 | 100 | 896.7 | 800.1 | 245.6 | 565.3 | 280.3 | 523.5 | 817.7 | 267.4 | 637.9 | 100.1 | 339.4 | 267.8 | 46 | 184.2 | 202.7 | 81.7 | 61.1 | 178.2 | 196.6 | 72.6
376.1 | 100.1 | 468.6 | 187.44 | 219.1066 | 155.2 | 190.5 | 199.5 | 197.3 | 367 | 19.9 | 21.7 | 38.7 | 5.7 | 248.7 | 14.1 | 101.4 | 902.2 | 781.7 | 247.5 | 563.4 | 281.1 | 522.9 | 817 | 269 | 638 | 101 | 342.2 | 269.7 | 46.5 | 184.9 | 203.4 | 82.1 | 61.7 | 179.4 | 198.1 | 73.2
377.1 | 101.1 | 468.3 | 187.32 | 218.9663 | 156.7 | 191.3 | 200.2 | 197.1 | 367.3 | 19.9 | 21.7 | 39 | 4.7 | 257.9 | 15.1 | 103 | 903.5 | 790.3 | 249.8 | 564.4 | 281.7 | 523.1 | 815.5 | 270.2 | 637.9 | 101.5 | 345.7 | 273.8 | 47 | 185.9 | 204.3 | 82.8 | 62.3 | 180.1 | 198.7 | 73.9
378.1 | 102.1 | 467.8 | 187.12 | 218.7325 | 155.1 | 191.6 | 200.7 | 197.7 | 369.7 | 19.9 | 21.7 | 39.2 | 4.5 | 253.8 | 18 | 104.6 | 900.7 | 805.8 | 251.5 | 566.3 | 282.9 | 522.1 | 815.1 | 271.1 | 639.3 | 102.1 | 349.2 | 277.9 | 47.5 | 186.8 | 205.7 | 83.5 | 62.9 | 180.3 | 199.4 | 74.5
379.1 | 103.1 | 466.4 | 186.56 | 218.0779 | 154.6 | 192.3 | 201.9 | 199.3 | 369.3 | 20 | 21.7 | 39.4 | 6.4 | 243.6 | 19.3 | 106.3 | 889.5 | 813.4 | 253.3 | 573.2 | 283.9 | 517.9 | 812 | 272.3 | 639.4 | 102.3 | 352.6 | 280.1 | 48 | 188 | 206.6 | 83.9 | 63.5 | 180.9 | 200 | 75.3
380.1 | 104.1 | 468.3 | 187.32 | 218.9663 | 154.8 | 193.4 | 202.8 | 200.3 | 369.6 | 20 | 21.7 | 39.6 | 8.5 | 246.7 | 19.4 | 108 | 886.7 | 826.8 | 254.7 | 580.6 | 285 | 516.9 | 818.1 | 273.5 | 642.1 | 102.3 | 356 | 281.9 | 48.5 | 188.7 | 207.5 | 84.6 | 64 | 182 | 200.6 | 75.8
381.1 | 105.1 | 469.3 | 187.72 | 219.4339 | 153.3 | 194.6 | 203.7 | 200.3 | 370.9 | 20.1 | 21.7 | 39.8 | 7.4 | 258.9 | 18.6 | 109.9 | 883.9 | 829.6 | 256.7 | 585.8 | 286.3 | 516.7 | 819.3 | 274.7 | 644.6 | 103.5 | 361 | 283.3 | 48.9 | 189.9 | 208.2 | 85.2 | 64.6 | 182.5 | 201.4 | 76.4
382.1 | 106.1 | 469 | 187.6 | 219.2936 | 152.9 | 196 | 204.5 | 200.6 | 378.4 | 20.1 | 21.7 | 39.9 | 6.4 | 241.5 | 19.9 | 111.8 | 881.8 | 822.6 | 258.2 | 586.4 | 288 | 515.7 | 819.5 | 276.2 | 645.7 | 103.6 | 365.9 | 285 | 49.4 | 191 | 209 | 86.6 | 65.2 | 183.3 | 202.1 | 77.2
383.1 | 107.1 | 468.5 | 187.4 | 219.0598 | 155.1 | 196.4 | 204.7 | 201.7 | 380.1 | 20.2 | 21.7 | 40.1 | 5.8 | 245.6 | 19.3 | 113.8 | 887 | 827.8 | 259.8 | 586.5 | 289.8 | 516.4 | 820.6 | 277.7 | 647.3 | 103.9 | 370.6 | 286.8 | 49.9 | 191.9 | 209.5 | 87.8 | 65.8 | 184.2 | 203 | 77.9
384.1 | 108.1 | 468.7 | 187.48 | 219.1533 | 157.4 | 197 | 204.3 | 202.5 | 380.2 | 20.2 | 21.6 | 40.2 | 6.5 | 250.5 | 18.7 | 115.7 | 892.8 | 819.7 | 261.9 | 586.7 | 291.3 | 518.4 | 820.1 | 279.1 | 649.8 | 104.3 | 373.6 | 289.9 | 50.4 | 192.6 | 210 | 88.5 | 66.4 | 185.2 | 203.5 | 78.4
385.1 | 109.1 | 469.1 | 187.64 | 219.3403 | 159.2 | 198 | 203.8 | 203.2 | 378.3 | 20.1 | 21.6 | 40.3 | 4.5 | 266.9 | 19.6 | 117.7 | 885.4 | 809.5 | 263.5 | 585.3 | 292.7 | 518 | 822.6 | 280.5 | 651.9 | 104.9 | 379.2 | 292.8 | 50.9 | 193.2 | 210.4 | 89 | 67 | 186 | 203.9 | 79.1
386.1 | 110.1 | 469 | 187.6 | 219.2936 | 160.7 | 198.3 | 204.2 | 204.6 | 379.5 | 20.1 | 21.6 | 40.4 | 3.5 | 256.4 | 17.9 | 119.7 | 880.2 | 806.5 | 264.5 | 585.7 | 294.1 | 517.3 | 818.9 | 281.5 | 653.5 | 105.8 | 385.3 | 296 | 51.4 | 194.1 | 211 | 89.9 | 67.6 | 186.9 | 204.9 | 79.7
387.1 | 111.1 | 469.1 | 187.64 | 219.3403 | 159.7 | 196.7 | 204.6 | 205.9 | 379.8 | 20.2 | 21.6 | 40.5 | 4.6 | 254 | 20.5 | 121.7 | 871.5 | 798.6 | 266.3 | 585.7 | 295.5 | 515.4 | 814.4 | 282.4 | 653.2 | 106.8 | 389.7 | 298.1 | 51.9 | 194.8 | 212.1 | 91.2 | 68.2 | 187.4 | 205.6 | 80.3
388.1 | 112.1 | 469.9 | 187.96 | 219.7144 | 160.8 | 195 | 205 | 206.9 | 379.8 | 20.1 | 21.6 | 40.8 | 7 | 258.1 | 22.2 | 123.6 | 880.4 | 789.3 | 268 | 584.3 | 296.4 | 516.9 | 817.6 | 283.5 | 654.6 | 108.7 | 394.7 | 301.8 | 52.4 | 195.5 | 212.6 | 91.7 | 68.8 | 188.1 | 206.4 | 81
389.1 | 113.1 | 469.6 | 187.84 | 219.5741 | 162.5 | 195 | 206.2 | 208.3 | 381.6 | 20.2 | 21.6 | 41.2 | 8.8 | 253 | 22.1 | 125.5 | 885.5 | 778.1 | 269.9 | 582.9 | 297.6 | 518.3 | 820.8 | 284.8 | 656.3 | 111.9 | 399.1 | 306.2 | 52.9 | 196.4 | 213.1 | 92.5 | 69.4 | 188.8 | 207 | 81.6
390.1 | 114.1 | 468.1 | 187.24 | 218.8728 | 163.4 | 195.5 | 207.8 | 209.4 | 383.7 | 20.2 | 21.6 | 41.6 | 6.7 | 250.3 | 21.7 | 127.5 | 885.6 | 771.9 | 271.7 | 581.6 | 298.6 | 516.1 | 815.8 | 286.1 | 656.3 | 114.4 | 402.6 | 309.6 | 53.4 | 197.8 | 213.8 | 93.5 | 70 | 189.2 | 207.6 | 82.2
391.1 | 115.1 | 468.3 | 187.32 | 218.9663 | 164.2 | 194.6 | 208.7 | 210.4 | 385.1 | 20.2 | 21.6 | 41.8 | 7.1 | 252.8 | 24.5 | 129.4 | 887.9 | 767.2 | 272 | 579.8 | 299.3 | 517.2 | 822.4 | 287.6 | 659.2 | 116.6 | 407 | 313.2 | 53.9 | 198.8 | 214.8 | 94.3 | 70.6 | 189.4 | 208.2 | 83
392.1 | 116.1 | 469 | 187.6 | 219.2936 | 164.4 | 194.4 | 208.6 | 210.8 | 384.8 | 20.2 | 21.6 | 42 | 8.1 | 260.7 | 24 | 131.3 | 889.5 | 758.4 | 274.4 | 579.4 | 300.3 | 518.9 | 824.4 | 289.6 | 661.9 | 118.6 | 409.4 | 317.4 | 54.4 | 199.7 | 215.7 | 94.9 | 71.2 | 190.3 | 208.6 | 83.6
393.1 | 117.1 | 470.4 | 188.16 | 219.9482 | 166.5 | 194.9 | 209.7 | 211.5 | 384.1 | 20.3 | 21.6 | 42.1 | 7.8 | 268 | 21.7 | 133.3 | 892.6 | 742.2 | 276.5 | 577.2 | 301.5 | 517.9 | 813.4 | 292.1 | 660.9 | 120.5 | 412.2 | 322 | 54.8 | 200.4 | 216.7 | 95.5 | 71.7 | 190.9 | 209.4 | 84.2
394.1 | 118.1 | 470.2 | 188.08 | 219.8547 | 168.9 | 195.8 | 211.4 | 212.3 | 383.5 | 20.4 | 21.6 | 42.1 | 6.8 | 269.3 | 21.4 | 135.3 | 891.5 | 743.9 | 278 | 575.5 | 302.5 | 516.7 | 813.8 | 295.1 | 661.3 | 122.2 | 414.6 | 326.1 | 55.3 | 201.3 | 217.7 | 95.9 | 72.3 | 190.9 | 210.4 | 84.8
395.1 | 119.1 | 470.4 | 188.16 | 219.9482 | 170.9 | 196.9 | 212.5 | 213.3 | 382.5 | 20.4 | 21.6 | 42.2 | 7.6 | 270.2 | 20.5 | 137.3 | 892.1 | 731.8 | 279.4 | 573.6 | 303.5 | 516.4 | 818.1 | 298.3 | 663.2 | 123.9 | 417.5 | 330.6 | 55.8 | 202.3 | 218.2 | 96.7 | 72.8 | 191.2 | 211.4 | 85.6
396.1 | 120.1 | 470.1 | 188.04 | 219.8079 | 173.7 | 197 | 213.6 | 213.9 | 381.4 | 20.5 | 21.6 | 42.2 | 6.6 | 258.6 | 20.3 | 139.2 | 894.2 | 716.1 | 282.8 | 570.8 | 304.6 | 519.6 | 823.7 | 301.9 | 665.9 | 125.5 | 417.2 | 335.8 | 56.4 | 202.5 | 218.6 | 97.4 | 73.4 | 191.6 | 212.2 | 86.2
397.1 | 121.1 | 470.1 | 188.04 | 219.8079 | 175 | 196.4 | 214.6 | 215.4 | 379.3 | 20.4 | 21.6 | 42.3 | 8.8 | 248.7 | 19.4 | 141.2 | 897.1 | 712.3 | 285.3 | 569.8 | 305.5 | 519.1 | 816.6 | 305.8 | 666.1 | 127.1 | 417.9 | 340.5 | 56.9 | 202.8 | 219.6 | 97.9 | 74 | 192.6 | 212.7 | 87
398.1 | 122.1 | 470 | 188 | 219.7612 | 176.1 | 195 | 215.5 | 216.1 | 377.9 | 20.5 | 21.6 | 42.3 | 8.5 | 265.5 | 16.5 | 143.2 | 899.3 | 718.7 | 287.3 | 569.9 | 306.6 | 519.9 | 820.4 | 309.6 | 667.7 | 128.7 | 418.9 | 346.1 | 57.4 | 203 | 220.3 | 98.4 | 74.5 | 193.7 | 213.4 | 87.6
399.1 | 123.1 | 470 | 188 | 219.7612 | 176.1 | 194.5 | 215.9 | 216.8 | 376 | 20.5 | 21.5 | 42.4 | 7.2 | 258.6 | 15.9 | 145.1 | 900.4 | 721.9 | 289.8 | 568.7 | 307.9 | 519.9 | 822 | 313.7 | 669.3 | 130.2 | 419.1 | 351.7 | 57.9 | 203.4 | 221 | 99.1 | 75.1 | 195 | 214.2 | 88.2
400.1 | 124.1 | 469.1 | 187.64 | 219.3403 | 175.1 | 194.7 | 216.1 | 217.4 | 375.1 | 20.5 | 21.5 | 42.5 | 6.3 | 247.3 | 18.5 | 147.1 | 899.6 | 725.7 | 292.5 | 571.1 | 308.8 | 520.6 | 827 | 317.7 | 671.3 | 131.8 | 421.2 | 357 | 58.4 | 204.3 | 221.5 | 99.6 | 75.7 | 195.9 | 215.4 | 88.8
401.1 | 125.1 | 467.6 | 187.04 | 218.639 | 174.6 | 194.5 | 216.7 | 217.4 | 376.8 | 20.6 | 21.5 | 42.6 | 6.3 | 232.1 | 16.5 | 149 | 904.6 | 726.2 | 296.3 | 570.1 | 310 | 520.4 | 828.3 | 321.9 | 672.5 | 133.3 | 427.5 | 362.3 | 58.9 | 204.7 | 222.2 | 100.4 | 76.2 | 197.1 | 215.9 | 89.7
402.1 | 126.1 | 470 | 188 | 219.7612 | 173.9 | 196.4 | 217.3 | 217.2 | 376.1 | 20.6 | 21.5 | 42.7 | 4.6 | 230.4 | 13.4 | 151 | 901.9 | 742.9 | 297 | 570.8 | 311.1 | 521.5 | 827.8 | 325.9 | 673.6 | 134.8 | 430 | 367.3 | 59.4 | 205.3 | 222.8 | 101.2 | 76.8 | 197.6 | 216.3 | 90.4
403.1 | 127.1 | 469.2 | 187.68 | 219.3871 | 175.3 | 196.3 | 218.2 | 217.5 | 376.4 | 20.7 | 21.5 | 42.8 | 4.9 | 227.5 | 12.8 | 153 | 898.4 | 757.3 | 299.5 | 573.2 | 312 | 523.3 | 829.5 | 330.2 | 676.6 | 136.4 | 431.4 | 372.2 | 59.9 | 205.8 | 223.4 | 102.1 | 77.4 | 198 | 216.7 | 91.1
404.1 | 128.1 | 468.6 | 187.44 | 219.1066 | 176.1 | 195.7 | 218.8 | 218.2 | 379 | 20.7 | 21.5 | 43 | 5.7 | 248.5 | 11.9 | 155 | 895.3 | 775 | 302.8 | 573.4 | 313.2 | 525.3 | 833.6 | 335 | 679.4 | 138.1 | 432.5 | 377.3 | 60.4 | 206.4 | 223.8 | 103 | 77.9 | 198 | 216.8 | 91.6
405.1 | 129.1 | 469.8 | 187.92 | 219.6677 | 177.3 | 196.7 | 219 | 219.1 | 378.8 | 20.7 | 21.5 | 43.2 | 5.5 | 256.3 | 10.9 | 157.1 | 891.4 | 786.4 | 304.7 | 576.2 | 314.4 | 528 | 837.9 | 340.2 | 682.1 | 139.7 | 434.2 | 382.9 | 60.9 | 207.1 | 223.9 | 104.1 | 78.5 | 198.3 | 217.3 | 92.2
406.1 | 130.1 | 470 | 188 | 219.7612 | 177.6 | 197.6 | 220.4 | 219.8 | 378.6 | 20.7 | 21.5 | 43.3 | 5.4 | 249.6 | 15.1 | 159.1 | 888.1 | 797.8 | 307.1 | 579.6 | 315.7 | 528.7 | 840.1 | 346.1 | 683.8 | 141.4 | 438.2 | 388.2 | 61.4 | 207.9 | 223.8 | 105.1 | 79 | 198.7 | 217.5 | 92.9
407.1 | 131.1 | 469 | 187.6 | 219.2936 | 176.3 | 198.2 | 221.1 | 220.9 | 380.2 | 20.7 | 21.5 | 43.5 | 6.1 | 251.8 | 16 | 161 | 887.8 | 789.7 | 310.2 | 580.7 | 316.9 | 529.6 | 839.3 | 352.7 | 685.6 | 143.1 | 442.5 | 393.1 | 61.9 | 208.6 | 224.5 | 106.3 | 79.6 | 198.9 | 217.5 | 93.5
408.1 | 132.1 | 469.5 | 187.8 | 219.5274 | 175.2 | 198.7 | 221.8 | 221.3 | 380.3 | 20.7 | 21.5 | 43.6 | 6 | 246.1 | 14.1 | 163 | 889 | 786.7 | 313 | 583.1 | 317.9 | 529.6 | 839.2 | 359 | 686.7 | 144.7 | 443 | 397.7 | 62.4 | 209.1 | 225.3 | 107.1 | 80.2 | 199 | 217.4 | 94.2
409.1 | 133.1 | 470.4 | 188.16 | 219.9482 | 174.7 | 198.1 | 222.7 | 221.5 | 380.1 | 20.8 | 21.5 | 43.8 | 6.3 | 255.8 | 12.8 | 165 | 885 | 798 | 316.3 | 587.1 | 319.1 | 528.3 | 839.1 | 364.6 | 686.8 | 146.3 | 444.6 | 402.1 | 62.9 | 209.2 | 225.5 | 107.4 | 80.8 | 199.3 | 217.5 | 94.9
410.1 | 134.1 | 469.6 | 187.84 | 219.5741 | 175.1 | 198.1 | 222.6 | 221.8 | 377.5 | 20.8 | 21.5 | 43.8 | 5.5 | 258.6 | 14.9 | 166.9 | 891.5 | 795.9 | 320.7 | 588.2 | 320 | 526.8 | 830.9 | 369.4 | 687.5 | 148 | 449.4 | 407.2 | 63.5 | 209.7 | 226 | 108.1 | 81.3 | 199.6 | 217.6 | 95.5
411.1 | 135.1 | 469.6 | 187.84 | 219.5741 | 175.6 | 198.4 | 222.6 | 221.5 | 380.7 | 20.8 | 21.5 | 43.9 | 5.5 | 250.3 | 17.2 | 168.9 | 893.7 | 803.3 | 323.1 | 591 | 320.9 | 524.6 | 819.4 | 372.9 | 686.9 | 149.6 | 455.8 | 410.7 | 64 | 210.4 | 226.5 | 108.7 | 81.9 | 200.1 | 218 | 96.2
412.1 | 136.1 | 468.9 | 187.56 | 219.2468 | 174.9 | 199.7 | 223.1 | 220.9 | 386.1 | 20.8 | 21.5 | 43.9 | 5.5 | 244.5 | 15.5 | 170.9 | 892.2 | 787.9 | 325.6 | 590.5 | 321.7 | 523.3 | 807 | 376.1 | 686.3 | 151.3 | 460.4 | 415 | 64.5 | 210.9 | 226.9 | 109.3 | 82.5 | 200.6 | 218.3 | 97
413.1 | 137.1 | 469.4 | 187.76 | 219.4806 | 175.8 | 201.5 | 223.6 | 221 | 390.8 | 20.8 | 21.5 | 44 | 5.8 | 243.9 | 16.8 | 172.9 | 889.3 | 795.2 | 329.1 | 587.5 | 322.3 | 522.3 | 812 | 379 | 688.1 | 153 | 464.1 | 419 | 65 | 211.5 | 227.3 | 110.5 | 83 | 200.9 | 219 | 97.6
414.1 | 138.1 | 469.8 | 187.92 | 219.6677 | 177.2 | 203 | 224.3 | 222.2 | 395.5 | 20.8 | 21.5 | 44.1 | 5.2 | 262.1 | 17.1 | 175 | 890.6 | 795.8 | 332.1 | 587.7 | 322.8 | 522.8 | 812.6 | 382 | 688.8 | 154.7 | 471.6 | 423.6 | 65.5 | 212.2 | 228 | 111.5 | 83.6 | 201.3 | 219.1 | 98.1
415.1 | 139.1 | 471 | 188.4 | 220.2287 | 178.7 | 204.6 | 224.4 | 222.7 | 398.5 | 20.9 | 21.5 | 44.3 | 5.1 | 255.6 | 15.7 | 177 | 889.2 | 797.6 | 335 | 590 | 323.3 | 522.1 | 813.8 | 384.7 | 689.4 | 156.5 | 478 | 427 | 66 | 213 | 228.9 | 112.3 | 84.1 | 201.4 | 219.6 | 98.8
416.1 | 140.1 | 470.8 | 188.32 | 220.1352 | 179.8 | 205.6 | 224.8 | 223.3 | 397.7 | 21 | 21.5 | 44.6 | 6 | 259 | 16.6 | 179 | 885 | 796 | 339.4 | 590.7 | 324.1 | 521.8 | 812.6 | 387.3 | 690.2 | 158.3 | 482.9 | 430.5 | 66.5 | 213.6 | 229.5 | 112.7 | 84.7 | 201.7 | 220.3 | 99.5
417.1 | 141.1 | 470.4 | 188.16 | 219.9482 | 177.9 | 205.7 | 225.8 | 223.9 | 394.6 | 21 | 21.5 | 44.8 | 6.1 | 266.4 | 20.2 | 181 | 884.1 | 801.6 | 343.5 | 591.9 | 324.9 | 523.6 | 817.2 | 390 | 692.5 | 160.1 | 487.7 | 434 | 66.9 | 214.1 | 230.3 | 113 | 85.2 | 202 | 221.5 | 100.1
418.1 | 142.1 | 470.5 | 188.2 | 219.995 | 176.7 | 204.4 | 226.9 | 224.4 | 393.4 | 21 | 21.5 | 45 | 7.7 | 255.8 | 18.1 | 183.1 | 886.5 | 802.2 | 346.3 | 593.5 | 325.8 | 522.8 | 813.7 | 392.9 | 691.9 | 162 | 493.9 | 437.8 | 67.4 | 215.1 | 231.1 | 113.8 | 85.7 | 202.6 | 222.4 | 100.9
419.1 | 143.1 | 469.2 | 187.68 | 219.3871 | 178.1 | 204.5 | 228 | 225.1 | 395 | 21.1 | 21.5 | 45.2 | 9 | 248.4 | 16 | 185.3 | 887.6 | 793.5 | 349.1 | 593.9 | 326.8 | 521.8 | 809.9 | 395.4 | 691.4 | 164 | 501 | 441.5 | 67.9 | 215.7 | 231.5 | 114.5 | 86.3 | 202.6 | 222.8 | 101.5
420.1 | 144.1 | 469.5 | 187.8 | 219.5274 | 177.9 | 204 | 228.5 | 226.1 | 397.4 | 21.1 | 21.5 | 45.5 | 6.8 | 253.3 | 16.9 | 187.5 | 889.1 | 779 | 354 | 591.4 | 327.7 | 521.1 | 813.5 | 397.7 | 692.3 | 165.9 | 507.6 | 445.4 | 68.4 | 216.1 | 231.5 | 115.3 | 86.8 | 203.3 | 222.8 | 102.1
421.1 | 145.1 | 468.8 | 187.52 | 219.2001 | 178 | 203.3 | 229.1 | 226.8 | 399.7 | 21.1 | 21.5 | 45.6 | 5.8 | 254.4 | 21.3 | 189.7 | 887 | 787.2 | 356.5 | 591.6 | 328.6 | 522.1 | 817.1 | 400.2 | 692.8 | 167.8 | 516.2 | 448.9 | 68.9 | 216.6 | 231.8 | 116.5 | 87.3 | 203.8 | 222.8 | 102.9
422.1 | 146.1 | 467.7 | 187.08 | 218.6857 | 180.2 | 204 | 229.1 | 227.5 | 405.8 | 21.1 | 21.5 | 45.8 | 6.4 | 249.2 | 21.5 | 191.9 | 883.4 | 785.8 | 359.3 | 592.6 | 329.6 | 524.2 | 817.8 | 402.7 | 694.1 | 169.5 | 524.5 | 452.3 | 69.3 | 217.2 | 232.3 | 117.4 | 87.9 | 204.6 | 222.8 | 103.5
423.1 | 147.1 | 468.6 | 187.44 | 219.1066 | 181.4 | 205.1 | 229.6 | 228.4 | 408.4 | 21.1 | 21.5 | 45.9 | 7.2 | 261.7 | 22.5 | 194.2 | 880.2 | 794.8 | 362 | 595.6 | 330.7 | 525 | 817.4 | 405.2 | 694.8 | 171.1 | 529.2 | 454.7 | 69.8 | 217.7 | 233.1 | 117.9 | 88.4 | 205 | 223.7 | 104.1
424.1 | 148.1 | 468 | 187.2 | 218.826 | 181.8 | 205.9 | 230.5 | 229.6 | 407.5 | 21.2 | 21.5 | 46.2 | 9.4 | 255.5 | 23.2 | 196.5 | 879.7 | 799.1 | 366.7 | 596.7 | 331.8 | 525.6 | 821.8 | 407.9 | 696.4 | 172.7 | 533.1 | 456.5 | 70.3 | 218.1 | 234.4 | 118.6 | 89 | 205.1 | 224.4 | 104.7
425.1 | 149.1 | 469.4 | 187.76 | 219.4806 | 181.3 | 207 | 231.4 | 230.7 | 410.1 | 21.2 | 21.4 | 46.5 | 8.1 | 261.2 | 22.1 | 198.7 | 878.1 | 787.3 | 371 | 596.1 | 332.9 | 524 | 820.7 | 410.6 | 697 | 174.5 | 538.9 | 459.2 | 70.8 | 218.7 | 235.4 | 119.6 | 89.5 | 205.3 | 225.1 | 105.3
426.1 | 150.1 | 469.8 | 187.92 | 219.6677 | 181.1 | 207.8 | 231.7 | 230.9 | 409.6 | 21.2 | 21.4 | 46.6 | 8.7 | 238.3 | 21.4 | 201 | 875.3 | 799.8 | 374.3 | 597.2 | 334.1 | 524.1 | 825.3 | 413.1 | 698.3 | 176.2 | 547.4 | 461.4 | 71.2 | 219.6 | 235.7 | 120.6 | 90 | 205.8 | 225.8 | 106
427.1 | 151.1 | 468.9 | 187.56 | 219.2468 | 181.3 | 207.9 | 231.1 | 231 | 414.4 | 21.3 | 21.4 | 46.8 | 7.1 | 240.1 | 20.6 | 203.3 | 874.4 | 813.7 | 376.5 | 599.6 | 335.3 | 525.2 | 825.4 | 415.6 | 699.3 | 177.9 | 559.3 | 464.2 | 71.7 | 220.9 | 236.2 | 121.4 | 90.5 | 206.4 | 226.4 | 106.6
428.1 | 152.1 | 469.8 | 187.92 | 219.6677 | 182.2 | 209 | 231.6 | 232 | 420.7 | 21.3 | 21.4 | 47 | 9.8 | 230.8 | 20.1 | 205.7 | 869.6 | 816.6 | 379.6 | 600.3 | 336.6 | 525.4 | 822.5 | 417.6 | 699.5 | 179.5 | 568.7 | 467.1 | 72.2 | 222.2 | 236.5 | 122.5 | 91.1 | 206.8 | 226.6 | 107.2
429.1 | 153.1 | 468.8 | 187.52 | 219.2001 | 183.1 | 211.2 | 232.3 | 232.9 | 432.2 | 21.3 | 21.4 | 47.2 | 10.6 | 255.7 | 16.4 | 208 | 860.5 | 813.2 | 382.8 | 599.3 | 337.7 | 525.4 | 814 | 419.3 | 699.3 | 181.2 | 574.5 | 469.5 | 72.7 | 223.3 | 236.9 | 124.2 | 91.6 | 207.3 | 227 | 107.9
430.1 | 154.1 | 469.4 | 187.76 | 219.4806 | 183.6 | 213.2 | 232.6 | 233 | 438.3 | 21.3 | 21.4 | 47.2 | 8.1 | 258 | 14.4 | 210.3 | 854.1 | 820.6 | 383.4 | 601.6 | 338.8 | 523.8 | 806.6 | 420.4 | 698.4 | 182.8 | 581.9 | 471.1 | 73.2 | 224 | 237.2 | 124.7 | 92.1 | 207.9 | 227.5 | 108.5
431.1 | 155.1 | 467.8 | 187.12 | 218.7325 | 184.5 | 215.1 | 232.2 | 233.4 | 435.1 | 21.4 | 21.4 | 47.2 | 6.1 | 245.8 | 13.3 | 212.7 | 858.3 | 821.8 | 387 | 603 | 339.9 | 523.7 | 810.4 | 421.3 | 700.1 | 184.3 | 585.6 | 473.2 | 73.7 | 224.1 | 237.4 | 125 | 92.7 | 209.1 | 227.9 | 109.3
432.1 | 156.1 | 468.6 | 187.44 | 219.1066 | 184.9 | 215.8 | 232.2 | 233.6 | 431.8 | 21.4 | 21.4 | 47.2 | 7 | 233.4 | 19.3 | 214.9 | 864.9 | 815.7 | 390.7 | 603.2 | 341 | 523.2 | 809.1 | 422.9 | 700.3 | 185.9 | 588.3 | 476.2 | 74.2 | 224.7 | 238.3 | 125.3 | 93.2 | 209.3 | 228.6 | 109.9
433.1 | 157.1 | 468.8 | 187.52 | 219.2001 | 184.9 | 214.8 | 232.8 | 233.8 | 425.2 | 21.5 | 21.4 | 47.3 | 6.7 | 250.4 | 24.6 | 217.2 | 869.5 | 817.1 | 393.2 | 606 | 342.2 | 525.1 | 814.7 | 424.9 | 701.3 | 187.5 | 592.6 | 478.4 | 74.7 | 225.2 | 238.9 | 125.7 | 93.8 | 209.4 | 229.1 | 110.6
434.1 | 158.1 | 468.8 | 187.52 | 219.2001 | 186.3 | 212.8 | 233.5 | 233.9 | 423.1 | 21.5 | 21.4 | 47.4 | 6.4 | 248.5 | 22.6 | 219.6 | 870.9 | 821.6 | 396.4 | 607.4 | 343.3 | 526.3 | 815 | 427.1 | 701 | 189.1 | 595.5 | 482.2 | 75.2 | 225.9 | 239.1 | 126.2 | 94.3 | 210.1 | 229.6 | 111.2
435.1 | 159.1 | 467.9 | 187.16 | 218.7793 | 186.8 | 212.4 | 233.7 | 233.9 | 420.7 | 21.5 | 21.4 | 47.6 | 9.2 | 250.6 | 19.7 | 222.1 | 870.9 | 818.9 | 399.4 | 606.5 | 344.5 | 527 | 814.9 | 429.3 | 701.2 | 190.7 | 601 | 485.1 | 75.6 | 226.8 | 239.1 | 127.4 | 94.9 | 210.7 | 230.2 | 111.9
436.1 | 160.1 | 468.5 | 187.4 | 219.0598 | 188.9 | 212.8 | 233.5 | 233.9 | 419.1 | 21.6 | 21.4 | 47.8 | 8.9 | 243.7 | 20.1 | 224.7 | 870.1 | 807.8 | 402.3 | 604.3 | 345.7 | 526 | 813.3 | 431.1 | 702.4 | 192.3 | 604.5 | 487.3 | 76.1 | 227.2 | 239.4 | 128.7 | 95.4 | 211.1 | 230.3 | 112.4
437.1 | 161.1 | 469.1 | 187.64 | 219.3403 | 190 | 214.5 | 234.1 | 234.3 | 417.2 | 21.6 | 21.4 | 47.9 | 7.5 | 239.1 | 20.2 | 227 | 872.7 | 798.3 | 403.3 | 602.5 | 346.9 | 527.7 | 819.8 | 432.8 | 704.2 | 193.9 | 609 | 489.8 | 76.6 | 227.4 | 239.7 | 129.5 | 95.9 | 211.1 | 230.6 | 113
438.1 | 162.1 | 468.6 | 187.44 | 219.1066 | 188.9 | 215.7 | 234.9 | 234.8 | 420.4 | 21.6 | 21.4 | 47.9 | 6.3 | 242.1 | 18.3 | 229.4 | 872 | 798 | 403.5 | 600.8 | 348.1 | 529.8 | 821.2 | 434.8 | 704.5 | 195.6 | 613.5 | 493.3 | 77.1 | 228 | 239.7 | 130 | 96.5 | 211.6 | 230.9 | 113.6
439.1 | 163.1 | 469 | 187.6 | 219.2936 | 187.9 | 215.4 | 235.5 | 235.1 | 417.8 | 21.6 | 21.4 | 47.9 | 5.1 | 245.1 | 20.6 | 232 | 869.3 | 806.2 | 404.2 | 601.6 | 349.4 | 530.5 | 824 | 436.7 | 705.4 | 197.2 | 618.9 | 495.9 | 77.6 | 228.7 | 239.9 | 130.5 | 97 | 212.1 | 231.1 | 114.4
440.1 | 164.1 | 468.7 | 187.48 | 219.1533 | 187.1 | 215.7 | 236.1 | 235.3 | 414.4 | 21.5 | 21.4 | 48 | 6.1 | 247.2 | 20.4 | 234.6 | 869 | 809.9 | 404.8 | 603.3 | 350.6 | 528.1 | 820.9 | 438.7 | 706 | 198.7 | 621.6 | 499 | 78.1 | 228.8 | 240.4 | 131.1 | 97.5 | 212.2 | 231.9 | 115.1
441.1 | 165.1 | 468.6 | 187.44 | 219.1066 | 186.6 | 216.6 | 235.7 | 235.6 | 406.3 | 21.5 | 21.4 | 48 | 5.7 | 249.5 | 17.9 | 237.2 | 870.2 | 826.4 | 407.4 | 604.8 | 352 | 530.4 | 829.5 | 440.8 | 709 | 200.2 | 622.7 | 501.6 | 78.5 | 228.8 | 240.7 | 131.6 | 98 | 212.7 | 232.4 | 115.6
442.1 | 166.1 | 468.8 | 187.52 | 219.2001 | 184.7 | 217.4 | 235.1 | 236 | 404.2 | 21.5 | 21.4 | 48 | 6.9 | 241.7 | 17.8 | 239.6 | 871.6 | 828.7 | 409.7 | 609.6 | 353.4 | 532.9 | 833 | 443.7 | 710.7 | 201.7 | 623.7 | 505 | 79 | 229 | 240.8 | 132.1 | 98.5 | 213 | 233 | 116.2
443.1 | 167.1 | 469.6 | 187.84 | 219.5741 | 182.2 | 217.2 | 235.1 | 235.8 | 401.9 | 21.6 | 21.4 | 48.1 | 5.8 | 240.2 | 18.8 | 241.8 | 873.5 | 817.4 | 412.3 | 611.1 | 354.8 | 534.6 | 836.9 | 446.5 | 712.6 | 203.2 | 621.3 | 508.6 | 79.5 | 229.2 | 240.9 | 132.9 | 99.1 | 213.4 | 233.4 | 116.9
444.1 | 168.1 | 469.6 | 187.84 | 219.5741 | 180.8 | 217.3 | 235.1 | 235.5 | 398.7 | 21.6 | 21.3 | 48.1 | 6.7 | 248.2 | 18.9 | 243.9 | 869.2 | 820.4 | 413.7 | 612.2 | 356.2 | 535.8 | 837.4 | 449.5 | 713.2 | 204.6 | 619.4 | 511.5 | 80 | 229.1 | 241.1 | 133.5 | 99.6 | 213.6 | 233.7 | 117.3
445.1 | 169.1 | 469 | 187.6 | 219.2936 | 181.7 | 216.7 | 234.5 | 235.1 | 398.3 | 21.6 | 21.3 | 48.3 | 6 | 265 | 17.9 | 245.9 | 866.4 | 816.7 | 414.5 | 612.1 | 357.6 | 535.8 | 838 | 452.1 | 712.5 | 206 | 620.8 | 514.1 | 80.4 | 229 | 241.2 | 133.9 | 100.1 | 213.6 | 233.7 | 117.9
446.1 | 170.1 | 470.9 | 188.36 | 220.182 | 185.4 | 217.6 | 234.1 | 234.2 | 397.5 | 21.7 | 21.3 | 48.3 | 4.5 | 257.3 | 16.6 | 247.9 | 862.5 | 809.6 | 414.3 | 609.9 | 359.1 | 538.7 | 843 | 454.6 | 714.6 | 207.4 | 621 | 515.8 | 80.9 | 229 | 241.1 | 134.8 | 100.6 | 213.8 | 233.5 | 118.4
447.1 | 171.1 | 472.4 | 188.96 | 220.8834 | 186.8 | 217.7 | 233.7 | 233.6 | 400.2 | 21.8 | 21.3 | 48.4 | 4.8 | 245.6 | 16 | 249.8 | 866.3 | 811.9 | 412.3 | 611.3 | 360.5 | 543.2 | 843.7 | 457.3 | 717.1 | 208.8 | 627.8 | 518.4 | 81.4 | 229.1 | 241.4 | 135.9 | 101.1 | 214.1 | 233.5 | 119.1
448.1 | 172.1 | 470.6 | 188.24 | 220.0417 | 185.4 | 217.3 | 234.1 | 232.9 | 406.7 | 21.9 | 21.3 | 48.6 | 4.7 | 255.9 | 16 | 251.7 | 868.7 | 820.5 | 414.7 | 613 | 362 | 544.8 | 843.9 | 459.6 | 717.9 | 210.2 | 635.5 | 520.9 | 81.9 | 229.7 | 241.7 | 136.4 | 101.6 | 214.3 | 233.9 | 119.6
449.1 | 173.1 | 470.3 | 188.12 | 219.9014 | 183.1 | 217.6 | 235.1 | 233 | 419 | 22 | 21.3 | 48.7 | 4.5 | 250.9 | 17 | 253.5 | 868.3 | 833.5 | 416.1 | 614.8 | 363.5 | 546.9 | 845.3 | 461.4 | 719.4 | 211.6 | 644.3 | 523.8 | 82.3 | 230.4 | 242.2 | 137 | 102.1 | 214.5 | 233.9 | 120.1
450.1 | 174.1 | 469.7 | 187.88 | 219.6209 | 183.1 | 216.3 | 236 | 233.5 | 429.1 | 22 | 21.3 | 48.8 | 4.9 | 255.3 | 16.9 | 255.4 | 864.9 | 828.4 | 419 | 615.3 | 365.1 | 548.9 | 845.1 | 463.5 | 720.9 | 213.1 | 649.3 | 526.4 | 82.8 | 231 | 242.7 | 137.7 | 102.6 | 214.7 | 234.1 | 120.5
451.1 | 175.1 | 470.7 | 188.28 | 220.0885 | 182.7 | 217.2 | 236.7 | 234 | 431.5 | 22.1 | 21.3 | 48.9 | 5.8 | 258.8 | 15.6 | 257.4 | 862.6 | 817.3 | 421.6 | 614.4 | 366.6 | 548.6 | 846.8 | 465.4 | 720.9 | 214.7 | 653.9 | 529.2 | 83.2 | 231.2 | 243.2 | 138.5 | 103.1 | 215.1 | 235.1 | 121
452.1 | 176.1 | 469.7 | 187.88 | 219.6209 | 182.2 | 217.8 | 235.4 | 235.2 | 435.8 | 22.1 | 21.3 | 48.9 | 6.5 | 257.5 | 14.9 | 259.3 | 860.3 | 824.8 | 422.6 | 615.7 | 368.3 | 547.7 | 836.7 | 466.8 | 720.3 | 216.3 | 662 | 531.5 | 83.7 | 231.4 | 243.8 | 139.6 | 103.5 | 215.9 | 235.7 | 121.7
453.1 | 177.1 | 470 | 188 | 219.7612 | 183.7 | 217.4 | 236.4 | 235.8 | 437.8 | 22.2 | 21.3 | 49 | 5.5 | 259 | 16.3 | 261.3 | 861.2 | 823.6 | 425.6 | 617.5 | 369.9 | 547.3 | 832.9 | 468 | 721.1 | 217.9 | 666.5 | 533.7 | 84.2 | 231.4 | 244.3 | 140.6 | 104 | 216.5 | 236.1 | 122.4
454.1 | 178.1 | 470.2 | 188.08 | 219.8547 | 183.5 | 216.9 | 237 | 237 | 433.2 | 22.4 | 21.3 | 49.1 | 4.7 | 251.3 | 17.1 | 263.4 | 857.6 | 833.8 | 428.5 | 620.6 | 371.5 | 546.9 | 834.2 | 469.6 | 721.2 | 219.5 | 668.3 | 536.1 | 84.7 | 231.7 | 244.7 | 141.3 | 104.5 | 216.8 | 236.7 | 122.9
455.1 | 179.1 | 469.3 | 187.72 | 219.4339 | 183.5 | 217.5 | 237.1 | 237.6 | 431.7 | 22.5 | 21.3 | 49.1 | 5.8 | 248.7 | 17.7 | 265.5 | 855 | 834.1 | 431.8 | 622.4 | 373.3 | 545.2 | 828.6 | 471.4 | 720.9 | 221 | 670.5 | 537.8 | 85.1 | 232.2 | 244.9 | 141.9 | 105 | 217.3 | 237.3 | 123.5
456.1 | 180.1 | 469.9 | 187.96 | 219.7144 | 182.4 | 219.8 | 237.9 | 237.5 | 431.4 | 22.5 | 21.3 | 49.2 | 6.4 | 262.3 | 15.8 | 267.6 | 850 | 824.7 | 436.9 | 624.1 | 375 | 545.1 | 829.5 | 472.9 | 721.7 | 222.6 | 674.7 | 538.5 | 85.6 | 232.7 | 245.1 | 142.3 | 105.5 | 217.9 | 237.5 | 124.2
457.1 | 181.1 | 469.4 | 187.76 | 219.4806 | 182 | 221.7 | 238.6 | 237.5 | 426.7 | 22.5 | 21.3 | 49.4 | 6.4 | 236.5 | 13.9 | 269.6 | 848.8 | 810.9 | 439.9 | 625 | 376.8 | 544.7 | 831.1 | 474.5 | 721.5 | 224.1 | 673.8 | 539.9 | 86.1 | 233.5 | 245 | 142.7 | 106 | 218.3 | 237.8 | 124.7
458.1 | 182.1 | 469.9 | 187.96 | 219.7144 | 184.2 | 221.7 | 238.5 | 237.7 | 422 | 22.5 | 21.3 | 49.6 | 8.1 | 253.3 | 12.3 | 271.7 | 844 | 799.9 | 444.2 | 624.8 | 378.5 | 542.1 | 823.1 | 476.2 | 720.2 | 225.4 | 673.1 | 541.7 | 86.5 | 233.7 | 245.1 | 143.2 | 106.5 | 218.8 | 238.1 | 125.3
459.1 | 183.1 | 471.5 | 188.6 | 220.4625 | 186.9 | 222.9 | 238.1 | 237.8 | 419.3 | 22.6 | 21.3 | 49.7 | 8.5 | 257.5 | 11.6 | 273.7 | 843 | 798 | 445.4 | 624.8 | 380.3 | 541.7 | 823.3 | 477.7 | 720.7 | 226.7 | 676.2 | 542.7 | 87 | 233.8 | 245.2 | 143.7 | 107.1 | 218.8 | 238.1 | 125.8
460.1 | 184.1 | 469.4 | 187.76 | 219.4806 | 188 | 223.9 | 237.8 | 237.7 | 415 | 22.6 | 21.3 | 49.9 | 8.4 | 241.4 | 11.3 | 275.8 | 848.5 | 782.8 | 448.7 | 622.8 | 382.2 | 542.7 | 821.8 | 479.6 | 720.9 | 227.9 | 672.4 | 544.2 | 87.5 | 234 | 245.4 | 144.3 | 107.6 | 219.1 | 237.9 | 126.5
461.1 | 185.1 | 470.6 | 188.24 | 220.0417 | 188.6 | 223.6 | 237.9 | 237.4 | 411.1 | 22.7 | 21.3 | 50.1 | 8.3 | 233.5 | 11.3 | 278 | 852.3 | 789.9 | 447.2 | 625 | 384.1 | 545.5 | 828.8 | 481.9 | 722.1 | 228.9 | 670.8 | 546.1 | 87.9 | 234.3 | 245.4 | 144.9 | 108.1 | 219.6 | 237.9 | 127.1
462.1 | 186.1 | 470.4 | 188.16 | 219.9482 | 188.6 | 222.7 | 237.3 | 237.5 | 408.9 | 22.8 | 21.3 | 50.3 | 6.8 | 242 | 13 | 280 | 852.8 | 795.3 | 444.8 | 628.5 | 386 | 548.2 | 834.2 | 484.7 | 724.6 | 230 | 672 | 548.9 | 88.4 | 234.6 | 245.7 | 145.6 | 108.6 | 220.2 | 237.7 | 127.8
463.1 | 187.1 | 470.7 | 188.28 | 220.0885 | 189.2 | 223.5 | 237.5 | 237.7 | 409.2 | 22.8 | 21.3 | 50.4 | 7.6 | 242 | 15.2 | 282 | 853.1 | 794.3 | 447.8 | 631.8 | 388.2 | 548.4 | 836.5 | 487.8 | 723.8 | 230.9 | 676.5 | 551.2 | 88.9 | 234.9 | 246.4 | 146.5 | 109.1 | 220.3 | 237.5 | 128.4
464.1 | 188.1 | 469.8 | 187.92 | 219.6677 | 188.8 | 224.4 | 238.1 | 237.7 | 412.3 | 22.8 | 21.3 | 50.5 | 9 | 251.1 | 19.3 | 284 | 851.4 | 808.4 | 450.5 | 632.4 | 390.4 | 550.2 | 841.9 | 490.9 | 725.9 | 231.9 | 682 | 554 | 89.3 | 235.2 | 246.8 | 147.2 | 109.6 | 220.4 | 237.7 | 129
465.1 | 189.1 | 469.9 | 187.96 | 219.7144 | 187.9 | 224.9 | 238.4 | 238 | 418.1 | 22.9 | 21.3 | 50.6 | 6.7 | 256.9 | 19.8 | 286.1 | 853.3 | 809 | 452.7 | 633.4 | 392.7 | 546.4 | 828.9 | 493.3 | 724.8 | 232.8 | 686.2 | 557 | 89.8 | 235.5 | 247.3 | 148 | 110.1 | 220.5 | 237.9 | 129.4
466.1 | 190.1 | 470.2 | 188.08 | 219.8547 | 188.4 | 225.9 | 238.9 | 237.7 | 414.6 | 22.9 | 21.2 | 50.6 | 5.2 | 246.6 | 19.9 | 288.2 | 852.4 | 809.1 | 457.2 | 634.1 | 395 | 546.1 | 832.6 | 495.6 | 724.8 | 233.7 | 689.1 | 558.6 | 90.2 | 235.9 | 247.7 | 148.7 | 110.5 | 220.7 | 238 | 130
467.1 | 191.1 | 470.8 | 188.32 | 220.1352 | 189.6 | 227.5 | 239.2 | 237.9 | 412.1 | 22.9 | 21.2 | 50.6 | 4.3 | 244.5 | 21.4 | 290.3 | 851.1 | 815.4 | 459.7 | 637.6 | 397.5 | 545.4 | 835.7 | 498.1 | 725.6 | 234.4 | 692.3 | 560.7 | 90.7 | 236.3 | 247.8 | 149.2 | 110.9 | 221 | 238.1 | 130.6
468.1 | 192.1 | 471 | 188.4 | 220.2287 | 189.1 | 228.3 | 239.5 | 237.9 | 409.1 | 23 | 21.2 | 50.6 | 5.6 | 239.2 | 20.5 | 292.5 | 847.7 | 817.9 | 460.7 | 643.2 | 400 | 545.8 | 841.7 | 500.8 | 726.6 | 234.9 | 690 | 563.2 | 91.1 | 236.4 | 248 | 149.6 | 111.4 | 221.6 | 238 | 131.2
469.1 | 193.1 | 470.8 | 188.32 | 220.1352 | 188.1 | 227.6 | 239.6 | 237.6 | 407.1 | 23 | 21.2 | 50.8 | 6.9 | 236.1 | 19.3 | 294.6 | 847.3 | 821 | 462.8 | 647.1 | 402.7 | 546.2 | 831.3 | 504.1 | 726.9 | 235.4 | 689.7 | 565.9 | 91.6 | 236.5 | 248.2 | 150.2 | 111.8 | 222 | 237.6 | 131.9
470.1 | 194.1 | 469.8 | 187.92 | 219.6677 | 187.8 | 228.3 | 239.6 | 237.1 | 406.5 | 23 | 21.2 | 51 | 9.2 | 250.3 | 16.2 | 296.9 | 848.8 | 818.9 | 466.2 | 648 | 405.5 | 544.9 | 829.6 | 507 | 726.4 | 235.6 | 689.6 | 567.9 | 92.1 | 236.6 | 248.4 | 150.8 | 112.2 | 222 | 237.3 | 132.5
471.1 | 195.1 | 470.4 | 188.16 | 219.9482 | 189.4 | 227.2 | 238.6 | 236.9 | 404.9 | 23.2 | 21.2 | 51.2 | 7 | 244.9 | 16.8 | 299.1 | 851.8 | 813.8 | 470 | 647.1 | 408.2 | 544.5 | 816.6 | 509.7 | 724.8 | 235.8 | 690 | 570.1 | 92.5 | 236.9 | 248.8 | 151.4 | 112.7 | 222.2 | 237.1 | 133
472.1 | 196.1 | 469.8 | 187.92 | 219.6677 | 190.2 | 226.5 | 237.2 | 236.7 | 407.6 | 23.2 | 21.2 | 51.2 | 4.1 | 236.4 | 18.1 | 301.2 | 853.3 | 811.2 | 472.2 | 647.4 | 411 | 543.3 | 814 | 512.1 | 724.5 | 235.9 | 692.9 | 571.9 | 93 | 237.1 | 249.4 | 151.9 | 113.1 | 222.4 | 236.8 | 133.5
473.1 | 197.1 | 470.5 | 188.2 | 219.995 | 191.1 | 227.3 | 237.5 | 236.5 | 408.1 | 23.3 | 21.2 | 51.3 | 4.8 | 246.4 | 16.3 | 303.3 | 853.3 | 810.2 | 474.9 | 647.8 | 413.9 | 542.7 | 805.7 | 514.2 | 723.8 | 236 | 695.3 | 574.1 | 93.4 | 237.3 | 250 | 152.6 | 113.5 | 222.5 | 236.8 | 134
474.1 | 198.1 | 469.9 | 187.96 | 219.7144 | 191.5 | 227.9 | 237.9 | 237 | 406.4 | 23.3 | 21.2 | 51.5 | 3.7 | 255.1 | 13.5 | 305.4 | 847.9 | 811 | 476.7 | 647.4 | 416.6 | 543.5 | 808.6 | 516.7 | 724.2 | 236.1 | 695.8 | 576.4 | 93.9 | 237.3 | 250.3 | 153 | 113.9 | 222.6 | 236.8 | 134.5
475.1 | 199.1 | 470.7 | 188.28 | 220.0885 | 192.8 | 228.6 | 238.2 | 237.2 | 405.3 | 23.3 | 21.2 | 51.5 | 3 | 229.6 | 12.1 | 307.4 | 847.7 | 818 | 477 | 647.1 | 419.5 | 540.8 | 802.5 | 519 | 722.9 | 236.1 | 700.8 | 578.8 | 94.4 | 237.5 | 250.7 | 153.8 | 114.3 | 222.7 | 236.7 | 135.1
476.1 | 200.1 | 469.6 | 187.84 | 219.5741 | 194.2 | 229.9 | 237.2 | 236.9 | 406.9 | 23.4 | 21.2 | 51.7 | 4 | 246.2 | 11.6 | 309.4 | 847 | 824.6 | 478.3 | 645.8 | 422.3 | 540.2 | 803.3 | 520.7 | 722.1 | 236.4 | 705.8 | 580.4 | 94.8 | 237.8 | 251 | 155.1 | 114.6 | 222.8 | 236.9 | 135.7
477.1 | 201.1 | 470.3 | 188.12 | 219.9014 | 195 | 230.7 | 237.4 | 236.5 | 409.8 | 23.4 | 21.2 | 51.9 | 6.9 | 254.3 | 10.6 | 311.5 | 846 | 833.7 | 478 | 648.6 | 425.2 | 541.9 | 815.9 | 522.6 | 723.8 | 236.9 | 708.1 | 582.3 | 95.3 | 238.3 | 251.1 | 156.9 | 115 | 222.9 | 237 | 136.1
478.1 | 202.1 | 470.1 | 188.04 | 219.8079 | 196.1 | 231.8 | 237.7 | 236.6 | 411.7 | 23.4 | 21.2 | 52.2 | 8.6 | 276.8 | 10.1 | 313.7 | 844.5 | 837.1 | 478.2 | 650.5 | 428.1 | 542 | 814.6 | 525.1 | 723.9 | 237.5 | 709 | 585.2 | 95.7 | 239 | 251.5 | 157.7 | 115.4 | 223 | 237.2 | 136.7
479.1 | 203.1 | 469.3 | 187.72 | 219.4339 | 196.3 | 232.3 | 238.4 | 236.7 | 410.3 | 23.5 | 21.2 | 52.5 | 10.4 | 255 | 10.6 | 316 | 843.6 | 834.2 | 479.1 | 652.3 | 431 | 541.2 | 813.6 | 527.5 | 724.2 | 238.1 | 711.7 | 587.7 | 96.2 | 240 | 251.9 | 157.9 | 115.8 | 222.9 | 237.3 | 137.2
480.1 | 204.1 | 468.6 | 187.44 | 219.1066 | 194.9 | 233.6 | 239.8 | 237 | 413.3 | 23.5 | 21.2 | 52.7 | 12.7 | 246.6 | 10.2 | 318.2 | 841.7 | 851.5 | 481.7 | 656.3 | 434 | 540.5 | 815.9 | 529.8 | 725 | 238.7 | 715.8 | 590.3 | 96.6 | 240.7 | 252.1 | 158.2 | 116.2 | 223 | 237.4 | 137.8
481.1 | 205.1 | 468.8 | 187.52 | 219.2001 | 194.3 | 234.3 | 241.5 | 237.4 | 412.4 | 23.6 | 21.2 | 53 | 10.1 | 250.2 | 9.4 | 320.5 | 838.7 | 860.4 | 481.3 | 664.6 | 436.9 | 539.6 | 819.4 | 532.2 | 725.5 | 239.4 | 718.4 | 592.4 | 97.1 | 240.8 | 252.2 | 158.3 | 116.6 | 223.7 | 237.3 | 138.4
482.1 | 206.1 | 468.8 | 187.52 | 219.2001 | 195.6 | 235 | 241.5 | 237.4 | 410.2 | 23.6 | 21.2 | 53.2 | 9.5 | 240.8 | 15.7 | 322.6 | 835.1 | 850.9 | 484.2 | 667.7 | 439.9 | 540.1 | 817.6 | 534.8 | 726.1 | 240.1 | 717.1 | 593.9 | 97.6 | 240.9 | 252.3 | 158.7 | 116.9 | 223.9 | 237.5 | 138.9
483.1 | 207.1 | 469.2 | 187.68 | 219.3871 | 196.8 | 235.1 | 241.3 | 236.9 | 407.2 | 23.6 | 21.2 | 53.5 | 8.4 | 250.7 | 20.7 | 324.8 | 832.5 | 839.3 | 486.2 | 669.8 | 442.9 | 542.4 | 819 | 537.3 | 727.5 | 240.9 | 714.3 | 595.3 | 98 | 241 | 252.4 | 159.5 | 117.3 | 224.2 | 237.6 | 139.4
484.1 | 208.1 | 469.5 | 187.8 | 219.5274 | 196.3 | 233.7 | 240.3 | 237 | 405.1 | 23.7 | 21.2 | 53.5 | 8.4 | 241 | 21.5 | 326.9 | 834.1 | 844.9 | 487.5 | 673 | 446 | 542 | 815.3 | 539.8 | 727.1 | 241.9 | 714 | 597.1 | 98.5 | 241.1 | 252.5 | 159.9 | 117.7 | 224.4 | 237.6 | 140.1
485.1 | 209.1 | 469.5 | 187.8 | 219.5274 | 196.9 | 232.3 | 239 | 236.6 | 402.3 | 23.7 | 21.2 | 53.5 | 7.8 | 241.5 | 18.9 | 328.9 | 832.1 | 844.2 | 489.2 | 673.5 | 449.1 | 542.6 | 816.5 | 542.4 | 727.5 | 243 | 715.4 | 598.5 | 98.9 | 241.3 | 252.8 | 160.4 | 118.1 | 224.5 | 238.7 | 140.7
486.1 | 210.1 | 468.8 | 187.52 | 219.2001 | 198.2 | 233 | 237.7 | 236.5 | 400.9 | 23.8 | 21.2 | 53.4 | 5.9 | 243.1 | 18.2 | 330.9 | 826.1 | 852.6 | 491.7 | 676.6 | 452.3 | 543.6 | 824 | 545.1 | 728.8 | 244.2 | 717.9 | 599.8 | 99.4 | 241.6 | 252.9 | 161.3 | 118.5 | 224.7 | 239.3 | 141.2
487.1 | 211.1 | 468.8 | 187.52 | 219.2001 | 197.3 | 233.9 | 237.2 | 237.7 | 402.5 | 23.8 | 21.2 | 53.4 | 4.9 | 244.4 | 16.5 | 333 | 824.2 | 852.8 | 492.8 | 679.7 | 455.5 | 543 | 822.5 | 547.2 | 729.2 | 245.8 | 720.8 | 601.2 | 99.8 | 241.7 | 252.8 | 161.7 | 118.9 | 224.6 | 239.2 | 141.8
488.1 | 212.1 | 468.7 | 187.48 | 219.1533 | 195.4 | 235.5 | 237.8 | 238.5 | 404.1 | 23.8 | 21.2 | 53.5 | 7.3 | 237.9 | 19.5 | 334.8 | 825.1 | 853.2 | 494.2 | 681.3 | 458.8 | 542.9 | 825.6 | 549 | 729.5 | 247.6 | 721.1 | 603 | 100.3 | 241.9 | 253 | 162.4 | 119.3 | 224.5 | 239 | 142.3
489.1 | 213.1 | 468.2 | 187.28 | 218.9195 | 193.8 | 235.6 | 239.1 | 238.4 | 405.9 | 23.9 | 21.2 | 53.6 | 7.9 | 243.6 | 22 | 336.6 | 827.5 | 844.9 | 496.7 | 682.2 | 462 | 543.1 | 822.5 | 551.2 | 730.9 | 249.1 | 720.3 | 605.2 | 100.7 | 242.5 | 253.2 | 163.5 | 119.7 | 224.6 | 238.8 | 142.8
490.1 | 214.1 | 469.5 | 187.8 | 219.5274 | 192.2 | 236.2 | 240 | 238.6 | 402.2 | 23.9 | 21.2 | 53.8 | 6.6 | 238.6 | 20.7 | 338.2 | 831.8 | 827.5 | 500 | 681.8 | 465.2 | 544 | 818 | 553.9 | 730 | 250.7 | 716.5 | 607.6 | 101.2 | 242.9 | 253.2 | 164.2 | 120.1 | 225.6 | 238.7 | 143.5
491.1 | 215.1 | 469.6 | 187.84 | 219.5741 | 193.4 | 235.8 | 240.3 | 239.5 | 399.9 | 23.9 | 21.2 | 54 | 8.5 | 245.2 | 20.6 | 339.9 | 829.7 | 822.5 | 501.7 | 681.8 | 468.4 | 544.6 | 818.8 | 556.5 | 730.9 | 251.8 | 714.1 | 609.8 | 101.6 | 243.4 | 253 | 164.8 | 120.5 | 226.1 | 238.4 | 144
492.1 | 216.1 | 470.5 | 188.2 | 219.995 | 192.2 | 235.7 | 240.2 | 239.7 | 398.4 | 23.9 | 21.2 | 54 | 7 | 248.9 | 19.6 | 341.3 | 829.7 | 807.2 | 505.6 | 680.7 | 471.6 | 546.6 | 817.5 | 558.9 | 730.5 | 252.4 | 711.8 | 612.1 | 102 | 243.8 | 252.7 | 164.7 | 120.9 | 226.7 | 238.5 | 144.5
493.1 | 217.1 | 481.4 | 192.56 | 225.0915 | 193 | 235.8 | 240.4 | 239.9 | 397.9 | 24 | 21.2 | 54.1 | 7.9 | 235.1 | 18.4 | 342.6 | 829.8 | 789.3 | 509.1 | 678.1 | 474.8 | 549 | 817.4 | 561.4 | 731.6 | 253.2 | 707.4 | 615.6 | 102.5 | 243.9 | 252.8 | 164.7 | 121.2 | 226.8 | 238.7 | 145
494.1 | 218.1 | 484.1 | 193.64 | 226.354 | 193.9 | 235.3 | 240.9 | 239.5 | 403.7 | 24.1 | 21.2 | 54.1 | 7.8 | 224.7 | 17.2 | 343.8 | 837 | 768.8 | 509.7 | 675.7 | 478 | 554.6 | 812.2 | 564.5 | 730.8 | 253.9 | 704.1 | 619.7 | 102.9 | 243.8 | 253 | 165.4 | 121.6 | 227.5 | 239.1 | 145.7
495.1 | 219.1 | 483.3 | 193.32 | 225.9799 | 194.4 | 235.7 | 240.7 | 239.9 | 406 | 24.1 | 21.2 | 54.2 | 7.4 | 231.5 | 12.5 | 345 | 838.8 | 755.1 | 512.9 | 674.8 | 481.1 | 558.1 | 808.7 | 566.6 | 730.1 | 254.6 | 700.4 | 623.9 | 103.3 | 243.7 | 253.3 | 166 | 121.9 | 228.3 | 239.2 | 146.4
496.1 | 220.1 | 482.2 | 192.88 | 225.4656 | 196.2 | 235.1 | 240.9 | 240.3 | 407.3 | 24.1 | 21.2 | 54.2 | 5.3 | 232.6 | 11.1 | 346.1 | 831.7 | 777.4 | 512.8 | 678.6 | 484.2 | 561.3 | 814.5 | 568.7 | 732.3 | 255.1 | 699.2 | 627.4 | 103.8 | 243.7 | 253.3 | 166.3 | 122.3 | 228.2 | 239.6 | 146.9
497.1 | 221.1 | 480.3 | 192.12 | 224.5772 | 199.5 | 234.5 | 240.7 | 240.7 | 411.1 | 24.2 | 21.2 | 54.2 | 4.5 | 249.8 | 16.3 | 346.9 | 807.1 | 786.4 | 505.8 | 680.1 | 487.4 | 562.7 | 821.4 | 571 | 733.8 | 255.6 | 704.6 | 630.4 | 104.2 | 244 | 253.6 | 166.9 | 122.6 | 229 | 240.7 | 147.5
498.1 | 222.1 | 476.6 | 190.64 | 222.8472 | 201 | 234.2 | 241.4 | 240.9 | 417.4 | 24.2 | 21.1 | 54.3 | 5.9 | 246.6 | 18.1 | 347.6 | 523.4 | 784.7 | 338.1 | 680.7 | 490.5 | 560.5 | 819.4 | 573.7 | 732.4 | 256.1 | 708.7 | 633.5 | 104.6 | 244.6 | 253.8 | 167.4 | 123 | 230.3 | 241.4 | 147.9
499.1 | 223.1 | 476.6 | 190.64 | 222.8472 | 202.1 | 233.3 | 242.1 | 240.9 | 416 | 24.3 | 21.1 | 54.5 | 6.1 | 264.5 | 15 | 317.1 | 319.6 | 781.8 | 207.6 | 679.7 | 493.6 | 559.8 | 818.4 | 576.1 | 731.8 | 256.6 | 706.3 | 636 | 105 | 245.4 | 254.1 | 168 | 123.3 | 230.7 | 241.8 | 148.3
500.1 | 224.1 | 475.8 | 190.32 | 222.4731 | 205.2 | 233.7 | 242.9 | 241.2 | 415.5 | 24.3 | 21.1 | 54.6 | 5.9 | 262.6 | 12.1 | 321.5 | 426 | 766.4 | 275.8 | 677 | 496.6 | 564.2 | 822.8 | 578.1 | 733.3 | 257 | 702.4 | 638.4 | 105.4 | 245.8 | 254.7 | 168.4 | 123.7 | 230.7 | 242.3 | 148.8
501.1 | 225.1 | 474.3 | 189.72 | 221.7717 | 207.5 | 234.4 | 243.3 | 241.4 | 416.8 | 24.3 | 21.1 | 54.6 | 6.5 | 249.6 | 13.7 | 323.9 | 491.5 | 766.3 | 339.3 | 676 | 499.6 | 566.4 | 819.5 | 580.1 | 733.5 | 257.4 | 698.3 | 641.9 | 105.8 | 246.4 | 255.2 | 169 | 124 | 231.1 | 242.7 | 149.4
502.1 | 226.1 | 473.1 | 189.24 | 221.2107 | 208.6 | 234.3 | 242.9 | 241.4 | 416.9 | 24.4 | 21.1 | 54.6 | 6.4 | 241.4 | 17.7 | 272.5 | 406.2 | 753.5 | 276 | 674.5 | 502.4 | 571.1 | 817.6 | 582.4 | 734.9 | 257.8 | 696 | 645.3 | 106.3 | 247 | 255.7 | 169.3 | 124.4 | 231.6 | 243.1 | 150.1
503.1 | 227.1 | 472.6 | 189.04 | 220.9769 | 210.8 | 233.8 | 243.1 | 241.5 | 417.1 | 24.4 | 21.1 | 54.6 | 6.5 | 254.8 | 17.1 | 344.5 | 451.5 | 740.8 | 311 | 672.8 | 505.4 | 570.9 | 816.9 | 584.4 | 734.3 | 258.2 | 695.3 | 648.9 | 106.7 | 247.3 | 256.3 | 169.7 | 124.8 | 231.9 | 243.4 | 150.5
504.1 | 228.1 | 471.3 | 188.52 | 220.369 | 211.9 | 234.3 | 244.4 | 241.5 | 417.1 | 24.5 | 21.1 | 54.7 | 5.2 | 256.8 | 17 | 309.7 | 465.7 | 756.4 | 305.1 | 673.7 | 508.2 | 569.8 | 815.2 | 586.3 | 733.8 | 258.5 | 694.7 | 652.6 | 107.1 | 247.4 | 256.8 | 170.4 | 125.2 | 232.3 | 244.1 | 151
505.1 | 229.1 | 470.1 | 188.04 | 219.8079 | 212.2 | 234.4 | 245.5 | 242 | 413.3 | 24.6 | 21.1 | 54.6 | 5.1 | 244.4 | 19.9 | 230.4 | 304.5 | 760.4 | 196.4 | 676.4 | 511.1 | 569.5 | 809.2 | 588.5 | 734.3 | 258.8 | 695.7 | 656 | 107.5 | 247.5 | 257.3 | 171.1 | 125.6 | 232.6 | 244.4 | 151.6
506.1 | 230.1 | 470.3 | 188.12 | 219.9014 | 213.1 | 233.5 | 246.2 | 241.8 | 409.7 | 24.7 | 21.1 | 54.5 | 5.8 | 252.1 | 19.6 | 243.5 | 211.1 | 756 | 137.5 | 677 | 513.9 | 571.6 | 795.1 | 591.6 | 734.6 | 259.2 | 696.1 | 658.8 | 107.9 | 247.8 | 258 | 171.7 | 126 | 232.8 | 244.6 | 152.3
507.1 | 231.1 | 471 | 188.4 | 220.2287 | 212.8 | 233.7 | 246 | 241.1 | 411.5 | 24.7 | 21.1 | 54.5 | 5.6 | 250.3 | 18.9 | 244.8 | 207.3 | 761.2 | 136.1 | 678.7 | 516.9 | 573.7 | 800.5 | 593.8 | 735.9 | 259.5 | 694.8 | 661.3 | 108.4 | 248.3 | 258.1 | 172.4 | 126.4 | 233 | 245 | 152.8
508.1 | 232.1 | 471.6 | 188.64 | 220.5093 | 211.1 | 234.1 | 246.9 | 240.3 | 411.4 | 24.8 | 21.1 | 54.5 | 5.1 | 251.6 | 17.9 | 289.4 | 270.2 | 777.1 | 176.5 | 680.4 | 519.8 | 573.4 | 806.3 | 596.6 | 736.8 | 259.9 | 697.1 | 663.9 | 108.8 | 248.5 | 258.3 | 172.9 | 126.8 | 232.9 | 245.4 | 153.4
509.1 | 233.1 | 471.6 | 188.64 | 220.5093 | 210.6 | 234.3 | 246.9 | 240 | 413.8 | 24.8 | 21.1 | 54.6 | 5.3 | 250.5 | 17.4 | 350.4 | 527.5 | 794.1 | 350.7 | 682.4 | 522.9 | 575.3 | 815.9 | 599.9 | 739 | 260.4 | 704.1 | 666 | 109.2 | 248.8 | 258.6 | 173.6 | 127.2 | 233.3 | 245.9 | 153.8
510.1 | 234.1 | 471.5 | 188.6 | 220.4625 | 212.1 | 234.2 | 246.9 | 239.6 | 413.5 | 24.9 | 21.1 | 54.7 | 4.8 | 257.8 | 17.3 | 351.4 | 581.6 | 799.7 | 385.6 | 686 | 526.1 | 574.3 | 819.5 | 603 | 739.4 | 261 | 709.2 | 668.3 | 109.6 | 249.2 | 259.1 | 174.4 | 127.6 | 233.5 | 246.5 | 154.3
511.1 | 235.1 | 471.2 | 188.48 | 220.3223 | 213.4 | 235.6 | 248.1 | 239.9 | 418.7 | 25 | 21.1 | 54.8 | 4 | 260.1 | 17 | 352.2 | 748 | 807.9 | 489.1 | 689.7 | 529.3 | 575.4 | 826.5 | 605.3 | 741.1 | 261.8 | 711.3 | 669.7 | 110 | 249.3 | 259.4 | 175.4 | 128 | 234.1 | 247.3 | 154.8
512.1 | 236.1 | 471 | 188.4 | 220.2287 | 214.5 | 236.5 | 248.7 | 240.3 | 419.3 | 25.1 | 21.1 | 54.9 | 4 | 266.6 | 15.7 | 353.2 | 496.6 | 807.7 | 330.5 | 691 | 532.6 | 575 | 827.6 | 607 | 740.8 | 262.7 | 713.2 | 670.3 | 110.4 | 249.5 | 259.8 | 176 | 128.4 | 235.2 | 247.6 | 155.4
513.1 | 237.1 | 469.2 | 187.68 | 219.3871 | 215.2 | 238 | 248.7 | 240.6 | 417 | 25.1 | 21.1 | 55 | 4.3 | 265.5 | 15 | 354.3 | 406.6 | 807.7 | 275 | 692.8 | 536 | 572.6 | 827 | 609.1 | 741.3 | 263.5 | 715.4 | 671.5 | 110.8 | 249.9 | 260.2 | 176.3 | 128.8 | 235.9 | 247.6 | 156
514.1 | 238.1 | 470.4 | 188.16 | 219.9482 | 216.2 | 240.1 | 249.4 | 241 | 414.2 | 25.2 | 21.1 | 55.2 | 4.7 | 261.3 | 14.4 | 354.9 | 492.7 | 808.2 | 336.9 | 693 | 539.4 | 572.9 | 827.2 | 611.9 | 741.9 | 264.2 | 717.3 | 673.1 | 111.2 | 250.2 | 261.1 | 176.8 | 129.3 | 236.2 | 247.8 | 156.4
515.1 | 239.1 | 470 | 188 | 219.7612 | 216.5 | 240.9 | 250.3 | 241 | 414.4 | 25.2 | 21.1 | 55.5 | 4.7 | 262.4 | 14.4 | 355.4 | 509.2 | 805.2 | 356.3 | 692.1 | 542.9 | 572.6 | 822.6 | 614 | 741.2 | 265 | 718.4 | 673.8 | 111.6 | 250.3 | 261.4 | 177.4 | 129.7 | 236.3 | 247.8 | 156.9
516.1 | 240.1 | 469.9 | 187.96 | 219.7144 | 214.6 | 242.1 | 251.1 | 240.1 | 414.2 | 25.3 | 21.1 | 55.7 | 4.2 | 264.2 | 14.6 | 356 | 675.6 | 813 | 461.5 | 695.4 | 546.5 | 574.8 | 824.7 | 615.3 | 742.9 | 265.6 | 717.8 | 674.7 | 112 | 250.4 | 261.6 | 177.9 | 130.1 | 236.5 | 247.7 | 157.4
517.1 | 241.1 | 469.5 | 187.8 | 219.5274 | 215.1 | 242.1 | 251.1 | 239.7 | 414.5 | 25.4 | 21.1 | 55.7 | 4 | 258.8 | 14.5 | 356.8 | 455.6 | 822.6 | 322.3 | 699 | 550.1 | 576.7 | 836.3 | 616 | 745.8 | 266.4 | 718.6 | 675.4 | 112.4 | 250.6 | 261.8 | 178.4 | 130.5 | 237.2 | 247.4 | 157.9
518.1 | 242.1 | 469.3 | 187.72 | 219.4339 | 216 | 241.4 | 250.1 | 239.2 | 418.2 | 25.4 | 21.1 | 55.8 | 4.9 | 270.3 | 12.3 | 357.9 | 678.4 | 829.9 | 476 | 701 | 553.9 | 576.9 | 847.6 | 617.3 | 747.1 | 267.3 | 723.3 | 676.8 | 112.8 | 250.9 | 262.3 | 178.8 | 130.9 | 237.7 | 247.6 | 158.4
519.1 | 243.1 | 469.2 | 187.68 | 219.3871 | 216.1 | 242.3 | 250.2 | 239.3 | 421.6 | 25.4 | 21.1 | 56 | 4.6 | 267.3 | 13.6 | 359.1 | 608.9 | 832.1 | 449.5 | 702.6 | 557.6 | 578.2 | 850.2 | 618.8 | 748 | 268.3 | 724.7 | 678.2 | 113.2 | 251.2 | 262.7 | 179.3 | 131.3 | 238.7 | 247.6 | 159
520.1 | 244.1 | 468.7 | 187.48 | 219.1533 | 216.4 | 242.9 | 250.6 | 240 | 426.6 | 25.3 | 21.1 | 56.2 | 5.3 | 277 | 14.8 | 360.4 | 534 | 841.8 | 423.7 | 705.7 | 561.4 | 580.3 | 855.3 | 619.2 | 749.2 | 269.3 | 727.5 | 679.5 | 113.6 | 251.7 | 263.4 | 180 | 131.7 | 239.2 | 247.8 | 159.6
521.1 | 245.1 | 468.3 | 187.32 | 218.9663 | 216.4 | 243.1 | 250.9 | 240.2 | 429.8 | 25.3 | 21.1 | 56.3 | 5 | 266.8 | 14 | 361.9 | 664.3 | 854.6 | 490.1 | 709.8 | 565 | 580.6 | 857.8 | 619.7 | 750.9 | 270.4 | 730.9 | 681 | 114 | 251.9 | 264 | 180.6 | 132 | 239.4 | 247.9 | 160.1
522.1 | 246.1 | 469.6 | 187.84 | 219.5741 | 217 | 244 | 251.3 | 240.2 | 434.7 | 25.4 | 21.1 | 56.4 | 5.5 | 268.5 | 12.9 | 363.9 | 654.9 | 849.7 | 466.1 | 712.5 | 568.5 | 581.7 | 859 | 620.3 | 751.8 | 271.7 | 733.8 | 682.8 | 114.5 | 252 | 264.4 | 181.3 | 132.4 | 239.8 | 248.2 | 160.5
523.1 | 247.1 | 468.9 | 187.56 | 219.2468 | 217.5 | 244.3 | 251.5 | 241.2 | 435.4 | 25.4 | 21.1 | 56.4 | 6.3 | 265.9 | 12 | 365.6 | 767.6 | 845.8 | 535 | 716 | 571.9 | 583.4 | 855.5 | 621.6 | 752.1 | 273 | 734.6 | 684.4 | 114.9 | 252.2 | 265.1 | 181.8 | 132.8 | 240.5 | 248.6 | 161.2
524.1 | 248.1 | 469.8 | 187.92 | 219.6677 | 217.7 | 244.5 | 251.4 | 241.9 | 434.6 | 25.5 | 21.1 | 56.5 | 6.3 | 262 | 10.9 | 367.6 | 691 | 848.2 | 501.8 | 719 | 575.2 | 584.9 | 849.7 | 622.7 | 753.1 | 274.6 | 735.8 | 686.1 | 115.3 | 252.7 | 265.5 | 182.3 | 133.1 | 241.3 | 249.5 | 161.8
525.1 | 249.1 | 469.9 | 187.96 | 219.7144 | 218.5 | 244.8 | 250.5 | 242.4 | 436.5 | 25.6 | 21.1 | 56.6 | 5.5 | 261 | 9.1 | 369.5 | 580.7 | 844.1 | 437.6 | 721.4 | 578.5 | 586.3 | 844.1 | 623.8 | 754.2 | 276 | 734.9 | 687.8 | 115.7 | 252.9 | 265.8 | 182.9 | 133.5 | 241.9 | 249.7 | 162.4
526.1 | 250.1 | 469.9 | 187.96 | 219.7144 | 218.4 | 246.9 | 249.3 | 243.1 | 437.6 | 25.6 | 21.1 | 56.6 | 5 | 253.3 | 8.9 | 372 | 454.8 | 842.9 | 344.6 | 723.6 | 581.9 | 589.9 | 842.2 | 624.3 | 755 | 277.4 | 734.9 | 689.4 | 116.1 | 253.2 | 266.3 | 183.5 | 133.8 | 242.4 | 250 | 163
527.1 | 251.1 | 470 | 188 | 219.7612 | 219.5 | 249.7 | 249.2 | 244 | 439.7 | 25.6 | 21 | 56.6 | 6.6 | 242.5 | 9 | 326.5 | 353.4 | 851.7 | 261.3 | 726.8 | 585 | 590.9 | 843.8 | 623.9 | 756.4 | 278.8 | 734 | 690.2 | 116.5 | 253.4 | 266.7 | 184 | 134.2 | 242.4 | 250 | 163.4
528.1 | 252.1 | 469.9 | 187.96 | 219.7144 | 220.2 | 251.7 | 249.4 | 244.3 | 439.8 | 25.6 | 21 | 56.7 | 7 | 264.5 | 11.5 | 378.5 | 805.1 | 846.4 | 571.6 | 725.6 | 588 | 594.4 | 843.8 | 623.9 | 757.6 | 280.2 | 734.7 | 692.7 | 116.9 | 253.5 | 266.9 | 184.8 | 134.5 | 243.1 | 250.1 | 163.8
529.1 | 253.1 | 470.3 | 188.12 | 219.9014 | 219.3 | 251.9 | 249.3 | 244.4 | 442.5 | 25.7 | 21 | 56.8 | 7.2 | 261.2 | 13.3 | 384.7 | 805.6 | 843.2 | 576.7 | 724 | 590.8 | 594.5 | 850.1 | 623.5 | 758.1 | 281.7 | 736 | 695.1 | 117.3 | 253.8 | 267.2 | 185.6 | 134.9 | 243.9 | 250 | 164.4
530.1 | 254.1 | 470.2 | 188.08 | 219.8547 | 220 | 251 | 249.2 | 245.6 | 441.1 | 25.7 | 21 | 57 | 6.6 | 265.7 | 13.8 | 391.1 | 805.5 | 823.8 | 578.6 | 725.7 | 593.6 | 593.8 | 849.5 | 623.6 | 758.9 | 283.1 | 735 | 698.5 | 117.7 | 254.3 | 267.4 | 186.3 | 135.3 | 243.9 | 250.6 | 164.9
531.1 | 255.1 | 470.4 | 188.16 | 219.9482 | 219.1 | 252.3 | 248.8 | 246.6 | 441.8 | 25.9 | 21 | 57.2 | 6.7 | 271.7 | 12.9 | 398.4 | 805.1 | 837.6 | 580.2 | 729.8 | 596.3 | 594.4 | 847 | 624.1 | 758.3 | 284.6 | 740.4 | 700.4 | 118.2 | 254.8 | 267.5 | 187 | 135.6 | 244.1 | 251.4 | 165.3
532.1 | 256.1 | 469.7 | 187.88 | 219.6209 | 217.8 | 254.5 | 248.7 | 247.7 | 445.9 | 26 | 21 | 57.3 | 5.3 | 254.1 | 11.7 | 406.6 | 804.7 | 842.2 | 581.8 | 731 | 599 | 594.6 | 848.9 | 625.4 | 758.9 | 286.1 | 744.8 | 702.1 | 118.6 | 255.4 | 267.7 | 188.5 | 136 | 244.5 | 252.1 | 166
533.1 | 257.1 | 469.8 | 187.92 | 219.6677 | 217.8 | 255 | 249.2 | 249.1 | 449 | 26.2 | 21 | 57.3 | 4.5 | 250.3 | 11.4 | 415.5 | 806.1 | 844 | 584.1 | 731.7 | 601.7 | 594 | 848.1 | 626.4 | 759.8 | 287.5 | 748.2 | 703.6 | 118.9 | 256.2 | 268 | 189.7 | 136.4 | 244.8 | 252.3 | 166.7
534.1 | 258.1 | 469.7 | 187.88 | 219.6209 | 218.3 | 255.5 | 248.3 | 250.1 | 450.8 | 26.4 | 21 | 57.4 | 4.6 | 248 | 10.7 | 424 | 805.1 | 846.7 | 586.1 | 730.6 | 604.3 | 591.6 | 838.3 | 627.2 | 758.5 | 288.9 | 750.8 | 704.1 | 119.3 | 257 | 268.2 | 190.4 | 136.8 | 245.3 | 252.3 | 167.2
535.1 | 259.1 | 470.1 | 188.04 | 219.8079 | 216.8 | 256.5 | 248.7 | 251.1 | 455.7 | 26.5 | 21 | 57.6 | 6 | 246 | 10.4 | 430 | 806 | 852.2 | 587.9 | 729.1 | 606.8 | 590.3 | 837.7 | 627.9 | 759.1 | 290.3 | 754 | 704.5 | 119.7 | 257.6 | 268.5 | 190.9 | 137.1 | 246 | 252.2 | 167.8
536.1 | 260.1 | 470 | 188 | 219.7612 | 216.2 | 256.1 | 249.2 | 252 | 461 | 26.8 | 21 | 57.8 | 5.5 | 253.6 | 9.5 | 435.4 | 805 | 856.3 | 589.6 | 729.1 | 609.4 | 590.4 | 839.7 | 628.4 | 758.8 | 291.5 | 758.4 | 705 | 120.1 | 258.3 | 268.9 | 192.1 | 137.5 | 245.8 | 252.5 | 168.2
537.1 | 261.1 | 469.4 | 187.76 | 219.4806 | 216 | 255.2 | 249.3 | 252.8 | 464 | 27 | 21 | 57.9 | 5.7 | 270.3 | 10 | 441.4 | 806.6 | 858.3 | 591.5 | 729 | 611.9 | 590.1 | 841.9 | 629.7 | 759.6 | 292.9 | 761.4 | 704.8 | 120.5 | 259.6 | 269.2 | 193.6 | 137.9 | 245.6 | 253 | 168.7
538.1 | 262.1 | 469.5 | 187.8 | 219.5274 | 214.8 | 254.4 | 249.2 | 254.2 | 460.4 | 27.2 | 21 | 58.2 | 5.8 | 271.9 | 11 | 448 | 804.2 | 858.7 | 594.2 | 731.2 | 614.5 | 591.5 | 845 | 631.2 | 761.6 | 294.3 | 763.6 | 704.9 | 120.9 | 260.9 | 269.4 | 194.5 | 138.3 | 246.3 | 253.6 | 169.4
539.1 | 263.1 | 469.2 | 187.68 | 219.3871 | 215.3 | 252.1 | 249 | 255 | 460.6 | 27.3 | 21 | 58.5 | 5.1 | 251.8 | 13.8 | 454 | 803.4 | 865.5 | 597.4 | 730.3 | 617.4 | 591.2 | 845.8 | 632.2 | 761.4 | 295.7 | 768.5 | 705.5 | 121.3 | 262.1 | 270.3 | 194.7 | 138.6 | 247.1 | 254.3 | 169.9
540.1 | 264.1 | 469 | 187.6 | 219.2936 | 214.4 | 253.1 | 249.9 | 255.4 | 470 | 27.4 | 21 | 58.8 | 4.1 | 242.2 | 14.9 | 460.2 | 805 | 868.3 | 599.7 | 729.8 | 620.3 | 591.4 | 851.2 | 632.3 | 763.3 | 297.1 | 774.1 | 706.2 | 121.7 | 263 | 270.9 | 195.1 | 139 | 247.6 | 255.1 | 170.4
541.1 | 265.1 | 469 | 187.6 | 219.2936 | 215.1 | 255 | 252 | 255.5 | 485.4 | 27.5 | 21 | 59.1 | 3.8 | 253.5 | 12.9 | 464.9 | 807.3 | 861.6 | 602.3 | 730.9 | 623.3 | 593.4 | 854.2 | 632.1 | 764.8 | 298.6 | 775.8 | 707.3 | 122.1 | 264 | 271.5 | 196 | 139.4 | 248.4 | 256 | 171
542.1 | 266.1 | 469.3 | 187.72 | 219.4339 | 214.9 | 256.6 | 253.8 | 256.5 | 490.9 | 27.5 | 21 | 59.2 | 3.7 | 251 | 10.3 | 470.5 | 810.1 | 865.4 | 605.2 | 732.7 | 626.4 | 597.3 | 854.7 | 632.9 | 764.9 | 300.1 | 776.9 | 708.6 | 122.5 | 264.4 | 272.2 | 196.2 | 139.8 | 248.8 | 257.1 | 171.5
543.1 | 267.1 | 469.8 | 187.92 | 219.6677 | 214.8 | 257.3 | 254.5 | 258 | 494.2 | 27.6 | 21 | 59.3 | 5.1 | 250.2 | 8.7 | 477.6 | 808.5 | 869.2 | 607.5 | 734.1 | 629.5 | 600.5 | 856 | 634.1 | 766.1 | 301.5 | 778.8 | 709.1 | 122.9 | 265.1 | 272.8 | 197.4 | 140.2 | 249.2 | 258.1 | 172.1
544.1 | 268.1 | 469.4 | 187.76 | 219.4806 | 215.1 | 257 | 255.3 | 258.2 | 491.8 | 27.6 | 21 | 59.4 | 5.2 | 275.3 | 10.9 | 482.2 | 806.5 | 874.4 | 610.2 | 737.1 | 632.5 | 601.3 | 859 | 634.8 | 767.7 | 302.9 | 779.1 | 710 | 123.3 | 265.6 | 273.5 | 197.9 | 140.5 | 249.8 | 258.9 | 172.8
545.1 | 269.1 | 469.2 | 187.68 | 219.3871 | 212.9 | 258.8 | 255.8 | 258.3 | 487.5 | 27.8 | 21 | 59.4 | 5.2 | 264 | 14.7 | 486.3 | 804.6 | 870.7 | 613.4 | 737.6 | 635.4 | 607.3 | 857.1 | 635.7 | 768.3 | 304.2 | 779.5 | 710.7 | 123.7 | 266 | 274.1 | 198.1 | 140.9 | 250.2 | 260 | 173.3
546.1 | 270.1 | 469.7 | 187.88 | 219.6209 | 210.6 | 260.4 | 257 | 258.9 | 485.3 | 27.9 | 21 | 59.5 | 5.4 | 256.3 | 18.2 | 492.5 | 803.8 | 847.6 | 616.7 | 739.7 | 638.2 | 609.2 | 859.1 | 635.7 | 769.7 | 305.6 | 774.6 | 711.5 | 124.1 | 266.8 | 274.5 | 198.1 | 141.3 | 251 | 260.7 | 173.8
547.1 | 271.1 | 470.1 | 188.04 | 219.8079 | 210.4 | 261.7 | 257.9 | 258.7 | 486.2 | 28.1 | 21 | 59.6 | 6.9 | 262.7 | 18.2 | 502.1 | 802.1 | 834.8 | 620.1 | 738.6 | 640.7 | 611.7 | 858.7 | 634.4 | 770.1 | 307 | 770.5 | 711.5 | 124.5 | 267.1 | 275.5 | 198.4 | 141.7 | 251.9 | 261.2 | 174.4
548.1 | 272.1 | 468.6 | 187.44 | 219.1066 | 212 | 262.2 | 258 | 258.4 | 484.4 | 28.2 | 21 | 59.7 | 5.9 | 257.5 | 17.5 | 507.9 | 801.6 | 839.6 | 622.7 | 741.7 | 643.1 | 612.5 | 865.9 | 633.5 | 770.2 | 308.4 | 771.4 | 711 | 124.9 | 267.4 | 276 | 198.6 | 142.2 | 252.1 | 261.8 | 174.9
549.1 | 273.1 | 468.7 | 187.48 | 219.1533 | 213.7 | 261.4 | 258.5 | 258.1 | 488.1 | 28.4 | 21 | 59.8 | 4.5 | 256.8 | 17.4 | 510 | 802.9 | 843.1 | 625.8 | 744.3 | 645.4 | 612 | 862.7 | 634.1 | 770.8 | 309.7 | 771.6 | 710.3 | 125.3 | 268.2 | 276.6 | 199.2 | 142.6 | 252.3 | 262.4 | 175.3
550.1 | 274.1 | 469 | 187.6 | 219.2936 | 214.1 | 261.9 | 259.4 | 257.6 | 489.3 | 28.6 | 21 | 59.9 | 4.3 | 254.6 | 17.8 | 511.7 | 800.5 | 833.7 | 628.2 | 745.8 | 647.7 | 614.2 | 858 | 635.3 | 772.5 | 310.9 | 767 | 710.4 | 125.7 | 268.6 | 277 | 199.7 | 143 | 252.4 | 262.7 | 175.8
551.1 | 275.1 | 468.9 | 187.56 | 219.2468 | 214.3 | 263.5 | 259.5 | 258.4 | 496.1 | 28.8 | 21 | 60 | 4.6 | 274.1 | 15.7 | 515.2 | 799.4 | 829.1 | 631 | 747.9 | 650 | 616.7 | 856.7 | 636.5 | 772.9 | 312 | 761.6 | 710.5 | 126.2 | 268.6 | 277.8 | 200 | 143.4 | 252.9 | 263.2 | 176.4
552.1 | 276.1 | 469.3 | 187.72 | 219.4339 | 215.2 | 265.2 | 259.9 | 258.4 | 498.7 | 29 | 21 | 60 | 5.6 | 273.9 | 11.7 | 522.1 | 799.6 | 821.5 | 634.8 | 749.3 | 652.1 | 618.2 | 854.7 | 637.1 | 774.3 | 313.1 | 758.5 | 709.9 | 126.6 | 268.7 | 278.6 | 200.4 | 143.8 | 253.7 | 263.7 | 177
553.1 | 277.1 | 470.6 | 188.24 | 220.0417 | 216.1 | 266.6 | 261.2 | 258.4 | 494.2 | 29.1 | 21 | 60.1 | 5.2 | 264.6 | 10.2 | 530.4 | 800.2 | 837.2 | 638.2 | 751 | 654.2 | 622.5 | 858.1 | 638.5 | 773.5 | 314.1 | 758.9 | 709.5 | 127 | 268.8 | 279.1 | 200.9 | 144.2 | 253.9 | 264.1 | 177.6
554.1 | 278.1 | 470.9 | 188.36 | 220.182 | 216 | 266.8 | 262 | 258.9 | 490.6 | 29.1 | 21 | 60.2 | 5.1 | 248.1 | 9 | 536.7 | 798.7 | 849.3 | 640.6 | 752.3 | 656.5 | 622.2 | 858.2 | 639.8 | 774.1 | 315.1 | 759.1 | 708.9 | 127.4 | 268.7 | 279.6 | 201.2 | 144.6 | 254.2 | 264.5 | 178
555.1 | 279.1 | 469.9 | 187.96 | 219.7144 | 216.5 | 266.8 | 262 | 259.7 | 490.7 | 29.2 | 20.9 | 60.4 | 5.2 | 267.7 | 12.7 | 544.4 | 797.8 | 855.3 | 642.7 | 752 | 658.7 | 620.9 | 860.5 | 640 | 774.3 | 316.1 | 760.1 | 708.5 | 127.8 | 268.8 | 279.7 | 201.5 | 145 | 254.4 | 265 | 178.4
556.1 | 280.1 | 470 | 188 | 219.7612 | 216.9 | 266.2 | 262.4 | 259.6 | 489.8 | 29.2 | 20.9 | 60.4 | 4.6 | 258.7 | 15.3 | 550.5 | 797.8 | 858.9 | 646.2 | 750.9 | 660.7 | 619.4 | 863 | 639.6 | 774.4 | 317 | 760.6 | 709 | 128.2 | 268.9 | 279.6 | 202.5 | 145.4 | 255.4 | 265.5 | 178.9
557.1 | 281.1 | 469.4 | 187.76 | 219.4806 | 215.4 | 266.1 | 262.4 | 259.2 | 484.2 | 29.3 | 20.9 | 60.5 | 5.2 | 260.1 | 13.9 | 554.3 | 797 | 866.6 | 649.3 | 752.8 | 662.6 | 617.2 | 863.4 | 638.8 | 775.3 | 317.9 | 762.6 | 710.2 | 128.6 | 269.1 | 279.5 | 202.9 | 145.9 | 255.7 | 265.7 | 179.4
558.1 | 282.1 | 469.1 | 187.64 | 219.3403 | 213.7 | 266.1 | 262 | 258.9 | 478.9 | 29.4 | 20.9 | 60.7 | 6 | 267.8 | 15.4 | 559.1 | 795.7 | 870.2 | 650.9 | 753.4 | 664.4 | 616.3 | 868.9 | 638.1 | 775.3 | 318.8 | 764.6 | 710.5 | 129 | 269.5 | 279.7 | 203.5 | 146.3 | 255.8 | 265.9 | 179.9
559.1 | 283.1 | 467.1 | 186.84 | 218.4052 | 213.2 | 266.6 | 261.7 | 258.9 | 475.4 | 29.6 | 20.9 | 60.8 | 6.2 | 272.5 | 16.4 | 563.9 | 794.2 | 865.7 | 653.2 | 752.3 | 666.2 | 617.2 | 866.4 | 637.8 | 776.2 | 319.7 | 765.7 | 711.1 | 129.4 | 269.7 | 279.8 | 204.3 | 146.7 | 256 | 266.2 | 180.4
560.1 | 284.1 | 468.2 | 187.28 | 218.9195 | 213 | 266.2 | 262.1 | 259.3 | 470 | 29.7 | 20.9 | 60.9 | 7 | 283.3 | 17.4 | 566.6 | 793.4 | 863.5 | 656.3 | 754.6 | 668 | 620.1 | 866.2 | 637.8 | 778 | 320.5 | 765.5 | 712.4 | 129.8 | 270 | 279.6 | 205.4 | 147.1 | 256.2 | 266.5 | 180.8
561.1 | 285.1 | 468.8 | 187.52 | 219.2001 | 213 | 266.3 | 262 | 259.6 | 469.3 | 29.8 | 20.9 | 60.9 | 7.5 | 290.2 | 16.5 | 572.9 | 794 | 862.2 | 659.4 | 754.5 | 669.7 | 623.3 | 868.3 | 637.9 | 779.7 | 321.4 | 763.6 | 714.4 | 130.2 | 270.2 | 279.5 | 206.2 | 147.5 | 256.1 | 266.3 | 181.2
562.1 | 286.1 | 469.3 | 187.72 | 219.4339 | 212.2 | 266.6 | 262.7 | 259.3 | 464.7 | 29.9 | 20.9 | 61 | 7 | 285.9 | 15.1 | 579.3 | 794.5 | 858.3 | 663.3 | 754.2 | 671.5 | 626.3 | 869.1 | 637.6 | 780.2 | 322.3 | 762.7 | 716.4 | 130.6 | 270.4 | 279.4 | 206.4 | 147.9 | 256 | 266.6 | 181.7
563.1 | 287.1 | 469.9 | 187.96 | 219.7144 | 212.5 | 265.6 | 262.9 | 258.5 | 461.4 | 30 | 20.9 | 61 | 5.2 | 266.8 | 14.1 | 580.9 | 795.7 | 858 | 667.1 | 755.5 | 673.1 | 626.9 | 870.7 | 636.3 | 781.3 | 323.1 | 764.2 | 718.8 | 131 | 270.6 | 279.8 | 206.5 | 148.2 | 256.2 | 266.7 | 182.4
564.1 | 288.1 | 469.6 | 187.84 | 219.5741 | 212.6 | 265.9 | 262.7 | 258.3 | 462.6 | 30.1 | 20.9 | 61 | 5.3 | 251.5 | 12.8 | 583.8 | 797.9 | 857.3 | 669.9 | 755.9 | 674.7 | 630 | 872 | 635.4 | 781.6 | 323.8 | 762 | 721.2 | 131.4 | 270.9 | 280.1 | 207.1 | 148.6 | 256.4 | 267.1 | 182.8
565.1 | 289.1 | 469.3 | 187.72 | 219.4339 | 213.5 | 264.4 | 263.5 | 258.6 | 463.9 | 30.2 | 20.9 | 61.1 | 5.7 | 245.4 | 12.9 | 588.3 | 797.8 | 866.3 | 672.5 | 759.6 | 676.2 | 630.3 | 874.6 | 634.4 | 783.5 | 324.6 | 761.1 | 723 | 131.7 | 271 | 280 | 207.6 | 149 | 256.6 | 267.4 | 183.3
566.1 | 290.1 | 469.8 | 187.92 | 219.6677 | 214.1 | 263.1 | 263.5 | 258.7 | 462.1 | 30.3 | 20.9 | 61.2 | 6 | 260.6 | 13.4 | 593.2 | 795.2 | 872.3 | 673.9 | 761.5 | 677.7 | 631.7 | 870.5 | 632.2 | 784.3 | 325.3 | 761 | 724.7 | 132.1 | 271.1 | 279.8 | 207.9 | 149.4 | 256.7 | 267.7 | 183.7
567.1 | 291.1 | 469.9 | 187.96 | 219.7144 | 214.2 | 263.8 | 263.6 | 258.7 | 462.8 | 30.3 | 20.9 | 61.3 | 9.2 | 269.9 | 14.7 | 601.1 | 794.2 | 872.5 | 675.8 | 762 | 679.2 | 635.1 | 864.3 | 627.8 | 785.6 | 326 | 759.9 | 726.7 | 132.5 | 271.3 | 279.8 | 208.6 | 149.8 | 257 | 268.3 | 184.2
568.1 | 292.1 | 469.7 | 187.88 | 219.6209 | 214.7 | 265.1 | 263.8 | 258.5 | 462.7 | 30.4 | 20.9 | 61.6 | 8.7 | 263.4 | 12 | 608.8 | 792.7 | 877 | 678.5 | 764.8 | 680.3 | 633.4 | 866.3 | 625.1 | 785.8 | 326.9 | 760.7 | 728.2 | 132.9 | 271.4 | 279.7 | 209 | 150.1 | 257.1 | 268.5 | 184.7
569.1 | 293.1 | 469.3 | 187.72 | 219.4339 | 215.3 | 265.6 | 264.5 | 257.9 | 460.7 | 30.5 | 20.9 | 61.7 | 8.6 | 255.7 | 9.7 | 616.9 | 793.4 | 876.6 | 680.1 | 766.7 | 681.4 | 629.6 | 863.8 | 622.6 | 785.2 | 327.8 | 759.4 | 729.7 | 133.2 | 271.6 | 279.6 | 209.4 | 150.5 | 256.8 | 268.5 | 185.1
570.1 | 294.1 | 470.2 | 188.08 | 219.8547 | 215.7 | 266.8 | 264.2 | 257.9 | 455.3 | 30.6 | 20.9 | 61.8 | 10.5 | 253.3 | 10.8 | 620.6 | 795.2 | 875.2 | 681.9 | 767.4 | 682.2 | 627.1 | 856.3 | 617.4 | 786.1 | 328.6 | 757.2 | 731.3 | 133.6 | 271.6 | 279.5 | 209.9 | 150.9 | 256.9 | 268.2 | 185.7
571.1 | 295.1 | 469.5 | 187.8 | 219.5274 | 214.9 | 267.8 | 263.3 | 258.6 | 451.3 | 30.7 | 20.9 | 61.8 | 10.5 | 258 | 11.2 | 625.2 | 797 | 875.9 | 685 | 768.5 | 683.1 | 626.6 | 854.5 | 615.8 | 786 | 329.6 | 760.2 | 733 | 133.9 | 271.8 | 279.8 | 210.3 | 151.3 | 257.4 | 267.9 | 186.2
572.1 | 296.1 | 469.5 | 187.8 | 219.5274 | 214.9 | 268.2 | 262.7 | 258.5 | 449.6 | 30.8 | 20.9 | 61.8 | 11.1 | 256.1 | 13 | 634.6 | 796.8 | 874.2 | 687.3 | 769.1 | 684.2 | 629 | 852.6 | 614.8 | 786.4 | 330.6 | 761.3 | 734.3 | 134.3 | 272 | 280 | 210.8 | 151.7 | 257.7 | 267.9 | 186.6
573.1 | 297.1 | 469.6 | 187.84 | 219.5741 | 214.3 | 269.2 | 263.7 | 258.4 | 448.8 | 30.9 | 20.9 | 61.8 | 7.5 | 253.5 | 13 | 642.1 | 796 | 874.2 | 689.4 | 769.1 | 685.3 | 630.6 | 856.5 | 615.8 | 787.3 | 331.6 | 762.3 | 736.1 | 134.6 | 272.2 | 280.2 | 211.3 | 152.1 | 257.9 | 268.1 | 187
574.1 | 298.1 | 470.1 | 188.04 | 219.8079 | 213 | 270.2 | 263.5 | 258.7 | 448.4 | 30.9 | 20.9 | 61.8 | 6.2 | 246.5 | 16.7 | 649.1 | 796.5 | 871.2 | 692.3 | 767.3 | 686.4 | 631.4 | 858.3 | 616.7 | 787.6 | 332.6 | 762.2 | 737.8 | 135 | 272.7 | 280.1 | 211.8 | 152.5 | 258.4 | 267.9 | 187.5
575.1 | 299.1 | 468.7 | 187.48 | 219.1533 | 212.7 | 270.6 | 263 | 258.9 | 448.6 | 31 | 20.9 | 61.8 | 5.3 | 231.3 | 17.7 | 656.9 | 796.4 | 865.7 | 694.6 | 769 | 687.4 | 631.6 | 860.8 | 617.7 | 789.3 | 333.7 | 761.2 | 739.4 | 135.3 | 273 | 280 | 212.5 | 152.8 | 258.5 | 268 | 187.9
576.1 | 300.1 | 469.9 | 187.96 | 219.7144 | 213 | 270.4 | 261.7 | 258.9 | 447 | 31.1 | 20.9 | 61.9 | 7.6 | 237.3 | 18.4 | 666.8 | 797.3 | 852.2 | 697.3 | 768 | 688.4 | 632.3 | 861.3 | 618.3 | 789.5 | 334.9 | 757.9 | 741.4 | 135.7 | 273.4 | 279.9 | 213.5 | 153.2 | 259 | 268.2 | 188.4
577.1 | 301.1 | 470.6 | 188.24 | 220.0417 | 213.2 | 269.4 | 261.2 | 258.8 | 446.9 | 31.1 | 20.9 | 61.9 | 9.2 | 248.9 | 16.8 | 679.7 | 796.3 | 835.8 | 698.6 | 766.3 | 689.3 | 632.1 | 857.2 | 619 | 789.7 | 336.2 | 753.2 | 742.7 | 136 | 273.6 | 280.1 | 214.2 | 153.6 | 259.3 | 268.1 | 188.9
578.1 | 302.1 | 472 | 188.8 | 220.6963 | 213.9 | 269.2 | 261.2 | 259.1 | 449.3 | 31.2 | 20.9 | 61.9 | 8.7 | 251.3 | 17 | 692.4 | 795.5 | 828.9 | 700.5 | 765.3 | 690.1 | 629.6 | 852.4 | 618.8 | 790.3 | 337.4 | 751.2 | 743.3 | 136.4 | 273.6 | 280.1 | 214.7 | 153.9 | 259.4 | 268.3 | 189.4
579.1 | 303.1 | 471 | 188.4 | 220.2287 | 212.4 | 269.2 | 261 | 259 | 449.3 | 31.2 | 20.9 | 62 | 8.9 | 244.9 | 20.4 | 702.5 | 795.9 | 826 | 702.8 | 765.4 | 691 | 628.2 | 851.1 | 618.6 | 791.1 | 338.6 | 750.1 | 744.9 | 136.7 | 273.6 | 280 | 214.7 | 154.3 | 259.6 | 268.7 | 189.9
580.1 | 304.1 | 470.3 | 188.12 | 219.9014 | 211.8 | 269.4 | 261.3 | 259 | 449.3 | 31.3 | 20.8 | 62.2 | 10.2 | 258 | 19.4 | 715.7 | 795.5 | 822.7 | 705.3 | 764.3 | 691.8 | 628.4 | 849.9 | 618.4 | 791 | 339.8 | 746.6 | 746.4 | 137 | 273.5 | 280 | 214.8 | 154.6 | 259.4 | 269 | 190.3
581.1 | 305.1 | 470.2 | 188.08 | 219.8547 | 212.9 | 269.2 | 261.4 | 259.1 | 451.1 | 31.2 | 20.8 | 62.4 | 7 | 233.3 | 17.4 | 722.3 | 796 | 825.1 | 707.3 | 764.7 | 692.6 | 627.3 | 843 | 617.7 | 791.4 | 341 | 745.1 | 746.6 | 137.4 | 273.4 | 280.1 | 215 | 155 | 259.6 | 269.4 | 190.6
582.1 | 306.1 | 470.9 | 188.36 | 220.182 | 213.3 | 270.1 | 262.4 | 259.4 | 449.9 | 31.2 | 20.8 | 62.5 | 5.5 | 239.7 | 17.3 | 729 | 796.2 | 825.4 | 710.3 | 765.8 | 693.5 | 627.3 | 846.8 | 617.5 | 792.6 | 342.1 | 744.2 | 748 | 137.7 | 273.5 | 280.1 | 215.4 | 155.3 | 259.9 | 269.5 | 191.1
583.1 | 307.1 | 470.7 | 188.28 | 220.0885 | 214 | 270.3 | 263 | 259.6 | 450 | 31.2 | 20.8 | 62.6 | 6.1 | 238.2 | 15.2 | 729.9 | 796.9 | 828.2 | 712.9 | 765.8 | 694.3 | 624.9 | 845.8 | 617.5 | 792 | 343.4 | 743.2 | 750.3 | 138.1 | 273.5 | 280.1 | 215.9 | 155.7 | 260.2 | 269.2 | 191.6
584.1 | 308.1 | 470.7 | 188.28 | 220.0885 | 214.3 | 269.4 | 263.7 | 259.7 | 450 | 31.2 | 20.8 | 62.8 | 8.8 | 240.3 | 16.5 | 736.3 | 798.2 | 819.9 | 716 | 765.3 | 695.2 | 624.4 | 840 | 617.4 | 792.8 | 344.6 | 740.2 | 752.1 | 138.4 | 273.3 | 279.8 | 216.4 | 156 | 260.3 | 268.8 | 192.1
585.1 | 309.1 | 470 | 188 | 219.7612 | 214.3 | 268.3 | 264.6 | 259.6 | 453.4 | 31.1 | 20.8 | 62.9 | 8.3 | 247.2 | 13.6 | 739.5 | 798.3 | 814.8 | 719.2 | 765.5 | 695.8 | 622 | 840.4 | 616.2 | 793 | 345.9 | 736.8 | 753.6 | 138.7 | 273.1 | 280 | 216.6 | 156.4 | 260.3 | 268.9 | 192.6
586.1 | 310.1 | 471.2 | 188.48 | 220.3223 | 215.1 | 268.4 | 264.9 | 259.5 | 457.6 | 31.1 | 20.8 | 63 | 8.3 | 247.9 | 10.9 | 744.8 | 798.7 | 821.9 | 722 | 765.3 | 696.4 | 619 | 842 | 615 | 794.1 | 347.1 | 735.7 | 755.1 | 139.1 | 272.8 | 280 | 216.6 | 156.7 | 260.6 | 268.8 | 193
587.1 | 311.1 | 471.1 | 188.44 | 220.2755 | 213.8 | 268.5 | 265.7 | 259.5 | 456.4 | 31.1 | 20.8 | 63 | 9.6 | 241.2 | 11.1 | 751.2 | 799.8 | 824 | 725.4 | 765.4 | 697.1 | 618.9 | 839.6 | 614 | 794.8 | 348.3 | 734.4 | 756.7 | 139.4 | 272.5 | 280.2 | 216.8 | 157 | 261.1 | 268.9 | 193.5
588.1 | 312.1 | 469.6 | 187.84 | 219.5741 | 214 | 268.6 | 266.3 | 259.6 | 461.6 | 31 | 20.8 | 63 | 7.5 | 259.7 | 12.4 | 757.6 | 801.5 | 816.8 | 728.5 | 762.8 | 697.7 | 618.4 | 837.1 | 612.9 | 794.9 | 349.5 | 730.7 | 757.8 | 139.7 | 272.5 | 280.5 | 217.3 | 157.3 | 261.5 | 269.2 | 194.1
589.1 | 313.1 | 470.3 | 188.12 | 219.9014 | 213.7 | 268.5 | 267.2 | 259.6 | 466.5 | 31 | 20.8 | 62.9 | 10.2 | 256.4 | 11.9 | 768.1 | 803.1 | 807.9 | 731.5 | 760.4 | 698.2 | 619.5 | 830.6 | 611.7 | 794.4 | 350.7 | 727.6 | 759 | 140.1 | 273 | 281 | 217.7 | 157.7 | 261.9 | 269.5 | 194.6
590.1 | 314.1 | 470.2 | 188.08 | 219.8547 | 214.1 | 267.7 | 268 | 259.8 | 470.4 | 31 | 20.8 | 62.9 | 9.4 | 240.5 | 15.8 | 778.6 | 807 | 800.9 | 734.7 | 758.6 | 698.7 | 619.7 | 825.4 | 611.1 | 793.9 | 351.8 | 724.9 | 760.3 | 140.4 | 273.4 | 280.9 | 217.8 | 158 | 262 | 269.8 | 195.1
591.1 | 315.1 | 470.3 | 188.12 | 219.9014 | 215.3 | 267.9 | 268.3 | 259.9 | 467.5 | 31 | 20.8 | 62.9 | 8.5 | 237.7 | 18.1 | 785.4 | 808.7 | 794.7 | 736.9 | 756.6 | 699.2 | 618.5 | 822.4 | 610.5 | 794 | 352.9 | 722.7 | 761.8 | 140.7 | 273.2 | 280.8 | 217.9 | 158.3 | 262.3 | 270.2 | 195.6
592.1 | 316.1 | 470.2 | 188.08 | 219.8547 | 216.8 | 268.3 | 269.1 | 260.1 | 470.5 | 31.1 | 20.8 | 62.9 | 7.4 | 257.2 | 16.4 | 789.2 | 808.8 | 788.5 | 739.4 | 755.5 | 699.6 | 618.5 | 817.3 | 609.8 | 794.6 | 353.9 | 720.5 | 762.6 | 141 | 273 | 280.9 | 218.1 | 158.6 | 262.8 | 270.7 | 195.9
593.1 | 317.1 | 470 | 188 | 219.7612 | 217.9 | 268.1 | 269.7 | 260.5 | 477.1 | 31.2 | 20.8 | 63 | 6.9 | 249.6 | 17.2 | 792.8 | 808.1 | 789.1 | 741.3 | 756.8 | 699.9 | 618.7 | 816.6 | 609.2 | 794.6 | 355 | 718.3 | 762.8 | 141.3 | 272.9 | 281.1 | 218.5 | 158.9 | 263.1 | 271.4 | 196.5
594.1 | 318.1 | 470.1 | 188.04 | 219.8079 | 218.7 | 268.7 | 270.1 | 260.5 | 482.5 | 31.2 | 20.8 | 63.2 | 6.9 | 252.9 | 16 | 796.3 | 809.7 | 786.6 | 744.4 | 756.8 | 700.1 | 621.5 | 819.7 | 609.9 | 795.6 | 356.1 | 717.1 | 764.1 | 141.7 | 272.8 | 281.3 | 219.2 | 159.3 | 264.3 | 271.9 | 197.3
595.1 | 319.1 | 470.2 | 188.08 | 219.8547 | 218.3 | 269.4 | 270.5 | 261.2 | 488.1 | 31.3 | 20.8 | 63.3 | 5.8 | 250.1 | 14.1 | 800.7 | 810.9 | 789.7 | 747.7 | 757.4 | 700.5 | 620.4 | 817.4 | 610.3 | 796.5 | 357.1 | 715.3 | 764.5 | 142 | 272.7 | 281.8 | 219.7 | 159.6 | 265 | 272.4 | 197.9
596.1 | 320.1 | 470.1 | 188.04 | 219.8079 | 217.3 | 269 | 271.9 | 261.8 | 483 | 31.3 | 20.8 | 63.5 | 7 | 259.4 | 13.2 | 803.6 | 811.2 | 801.1 | 751.4 | 758.7 | 700.8 | 620.1 | 812.7 | 610.4 | 796.4 | 358.2 | 715.5 | 764.8 | 142.3 | 273.1 | 282.1 | 220.2 | 160 | 265.2 | 272.8 | 198.4
597.1 | 321.1 | 470.2 | 188.08 | 219.8547 | 216.6 | 269.1 | 272.6 | 261.9 | 478.2 | 31.4 | 20.8 | 63.7 | 7.4 | 253 | 14.2 | 809.3 | 810.8 | 807.1 | 754.4 | 758.6 | 701.2 | 620.7 | 815.5 | 610.6 | 795.9 | 359.4 | 715.4 | 764.8 | 142.6 | 273.1 | 282.2 | 220.7 | 160.3 | 265.3 | 273.3 | 198.9
598.1 | 322.1 | 469.4 | 187.76 | 219.4806 | 216.5 | 270.1 | 272.7 | 261.7 | 474.7 | 31.5 | 20.8 | 63.8 | 6.2 | 248.1 | 15.7 | 810 | 810.9 | 821.9 | 757.6 | 762.7 | 701.6 | 622.7 | 823 | 611.8 | 797.4 | 360.5 | 718.5 | 765 | 143 | 273.4 | 282.4 | 221.1 | 160.7 | 265.9 | 273.4 | 199.4
599.1 | 323.1 | 469.2 | 187.68 | 219.3871 | 215.7 | 269.6 | 273 | 262.2 | 471.5 | 31.7 | 20.8 | 64 | 4.9 | 258.9 | 14.5 | 812.4 | 810.3 | 827.8 | 760.2 | 763.6 | 702 | 620.5 | 824.8 | 613.5 | 797.4 | 361.7 | 719.8 | 765.1 | 143.3 | 273.9 | 282.4 | 221.5 | 161 | 266.1 | 273.6 | 199.8
600.1 | 324.1 | 469.1 | 187.64 | 219.3403 | 214.4 | 270.1 | 272.9 | 262.9 | 465.4 | 31.9 | 20.8 | 64.1 | 4.3 | 253.9 | 14.9 | 817 | 811.7 | 836.4 | 763.2 | 765.6 | 702.5 | 618.7 | 824.8 | 615.7 | 797.5 | 363 | 722.6 | 765.6 | 143.6 | 274.1 | 282.4 | 222 | 161.4 | 266.2 | 274 | 200.2
601.1 | 325.1 | 470.8 | 188.32 | 220.1352 | 214.9 | 270.2 | 272.7 | 263 | 463.6 | 32 | 20.8 | 64.1 | 4.9 | 246.3 | 16.1 | 820 | 812.8 | 837 | 765.8 | 767.1 | 703 | 618.9 | 823.1 | 617.7 | 798.3 | 364.2 | 724.5 | 766.1 | 143.9 | 274.3 | 282.5 | 222.4 | 161.7 | 266.2 | 274.3 | 200.7
602.1 | 326.1 | 471 | 188.4 | 220.2287 | 214.8 | 269.9 | 271.8 | 262.4 | 461.5 | 32.3 | 20.8 | 64.2 | 6.1 | 253 | 17.2 | 822.6 | 814.4 | 838.9 | 768.6 | 766.7 | 703.5 | 619.1 | 823.2 | 619.1 | 799.7 | 365.4 | 727.4 | 767.3 | 144.2 | 274.4 | 282.4 | 222.9 | 162.1 | 266.6 | 274.6 | 201.1
603.1 | 327.1 | 470.7 | 188.28 | 220.0885 | 215.7 | 269.2 | 272 | 261.9 | 460.9 | 32.5 | 20.8 | 64.3 | 6.2 | 239.5 | 17.7 | 825.6 | 815.8 | 847.3 | 771.6 | 769.6 | 704.1 | 619.3 | 827.1 | 619 | 800.2 | 366.6 | 730.1 | 768.7 | 144.6 | 274.5 | 283.9 | 223.6 | 162.5 | 266.8 | 274.6 | 201.5
604.1 | 328.1 | 470.2 | 188.08 | 219.8547 | 216.2 | 270 | 271.7 | 261.8 | 462.4 | 32.6 | 20.8 | 64.4 | 5.2 | 256.2 | 16.4 | 830.1 | 816.9 | 847.8 | 773.3 | 771 | 704.7 | 619.8 | 827 | 619.2 | 800.3 | 367.9 | 729.7 | 769.4 | 144.9 | 275 | 284.3 | 224.4 | 162.8 | 266.8 | 274.5 | 201.8
605.1 | 329.1 | 470.1 | 188.04 | 219.8079 | 216.2 | 270.1 | 272.1 | 261.9 | 462.9 | 32.7 | 20.8 | 64.6 | 4.6 | 245.5 | 14.4 | 832.1 | 818.5 | 849.8 | 775.8 | 771.6 | 705.4 | 619.9 | 824.9 | 619.6 | 800.8 | 369.2 | 732.5 | 769.2 | 145.2 | 275.2 | 284.5 | 224.9 | 163.2 | 266.5 | 274.7 | 202.3
606.1 | 330.1 | 470 | 188 | 219.7612 | 217.4 | 269.7 | 271.5 | 262 | 459.1 | 32.7 | 20.8 | 64.6 | 4.6 | 246.1 | 14.6 | 836.9 | 817.5 | 865.8 | 777.2 | 772.9 | 706 | 617.6 | 826 | 621 | 800.5 | 370.5 | 739.1 | 768.6 | 145.5 | 275.5 | 284.6 | 225.1 | 163.5 | 266.7 | 274.7 | 202.9
607.1 | 331.1 | 468 | 187.2 | 218.826 | 217 | 270.9 | 271.2 | 262.5 | 463.5 | 32.8 | 20.7 | 64.7 | 6.3 | 239.9 | 15.6 | 841.3 | 816.8 | 869.2 | 778 | 770.3 | 706.9 | 615.9 | 828.5 | 622.3 | 799.1 | 371.8 | 742.8 | 768.6 | 145.8 | 275.7 | 284.5 | 225.7 | 163.9 | 266.8 | 274.8 | 203.2
608.1 | 332.1 | 468.5 | 187.4 | 219.0598 | 215 | 271.9 | 271.1 | 263.2 | 469.2 | 32.7 | 20.7 | 64.8 | 6.1 | 245 | 16.5 | 845.3 | 816.7 | 869 | 778.9 | 769.7 | 707.9 | 615.5 | 826.8 | 624.3 | 797.4 | 373 | 748.2 | 768.6 | 146.1 | 276.1 | 284.7 | 226.5 | 164.2 | 266.7 | 275 | 203.5
609.1 | 333.1 | 468.3 | 187.32 | 218.9663 | 214.3 | 273 | 271.9 | 263.8 | 479.1 | 32.8 | 20.7 | 64.9 | 6.1 | 243.2 | 15.9 | 849.5 | 816.2 | 872 | 779.5 | 771.1 | 709.2 | 616.9 | 826.5 | 626.9 | 797.3 | 374.4 | 752.1 | 769.2 | 146.5 | 276.6 | 285.1 | 227.2 | 164.5 | 266.9 | 275 | 203.9
610.1 | 334.1 | 468.1 | 187.24 | 218.8728 | 214.4 | 274 | 272.8 | 264.3 | 476.6 | 32.8 | 20.7 | 65.1 | 5.5 | 250.2 | 15 | 852 | 817.8 | 870.2 | 781.5 | 773.5 | 710.3 | 618.1 | 823.5 | 629.5 | 798.7 | 375.8 | 753.2 | 769.8 | 146.8 | 277.3 | 285.3 | 228.2 | 164.9 | 267.2 | 274.8 | 204.3
611.1 | 335.1 | 468.4 | 187.36 | 219.013 | 213.7 | 274.6 | 272.5 | 264.6 | 470.9 | 32.8 | 20.7 | 65.1 | 5.9 | 246.2 | 13.4 | 854.6 | 818.8 | 865.1 | 783.4 | 774.4 | 711.4 | 618.1 | 815.7 | 632.6 | 798.5 | 377.2 | 752.5 | 770.3 | 147.1 | 278.2 | 285.6 | 229.2 | 165.2 | 267.1 | 275.1 | 204.9
612.1 | 336.1 | 468.5 | 187.4 | 219.0598 | 214.9 | 275.9 | 271.4 | 265.2 | 465 | 32.9 | 20.7 | 65.2 | 5.5 | 246.6 | 13.9 | 857.4 | 819.7 | 851.3 | 784.8 | 773.8 | 712.4 | 618.8 | 808.6 | 634.7 | 798.3 | 378.7 | 749.7 | 770.8 | 147.4 | 278.7 | 286.1 | 229.8 | 165.6 | 267.3 | 275.5 | 205.3
613.1 | 337.1 | 469.5 | 187.8 | 219.5274 | 216.4 | 276.9 | 270.8 | 265.3 | 461.9 | 32.9 | 20.7 | 65.4 | 6.5 | 260.1 | 13.8 | 862.4 | 820.8 | 836.5 | 787.5 | 773.7 | 713.2 | 621.1 | 802.8 | 636.8 | 799.4 | 380.2 | 745 | 770.5 | 147.8 | 279.1 | 286.1 | 229.6 | 165.9 | 267.2 | 275.6 | 205.8
614.1 | 338.1 | 470.2 | 188.08 | 219.8547 | 217.2 | 277.8 | 270.3 | 264.8 | 460.1 | 33 | 20.7 | 65.4 | 6.3 | 247.7 | 13.5 | 867.3 | 821.7 | 833.1 | 794.2 | 772.1 | 713.7 | 621.5 | 799.4 | 640.5 | 799.1 | 381.7 | 742.2 | 770.2 | 148.1 | 279.2 | 286.1 | 229.7 | 166.2 | 267.7 | 275.7 | 206.4
615.1 | 339.1 | 469.3 | 187.72 | 219.4339 | 217.6 | 278.1 | 270.2 | 264.9 | 459 | 33 | 20.7 | 65.6 | 7.5 | 265.2 | 12.7 | 870.5 | 823.6 | 837.1 | 804.4 | 769.9 | 714.1 | 621.7 | 802.3 | 646 | 798.8 | 383.1 | 743.6 | 770.1 | 148.4 | 279.5 | 286.1 | 229.9 | 166.6 | 268.2 | 276 | 206.9
616.1 | 340.1 | 467.8 | 187.12 | 218.7325 | 217 | 278 | 270.9 | 265.5 | 458.6 | 33 | 20.7 | 65.7 | 7.4 | 255.9 | 14.2 | 873 | 824.2 | 839.8 | 813 | 772.1 | 714.5 | 621.5 | 799.1 | 653.8 | 798 | 384.6 | 743.4 | 769.6 | 148.7 | 279.4 | 286 | 230 | 166.9 | 268.3 | 275.4 | 207.2
617.1 | 341.1 | 468.7 | 187.48 | 219.1533 | 216 | 278.2 | 271.6 | 265.8 | 454.7 | 33.1 | 20.7 | 65.9 | 8.3 | 246.2 | 17.3 | 875.3 | 823.8 | 854.8 | 819 | 774.9 | 715.3 | 622.3 | 809.3 | 662.2 | 799.1 | 386.1 | 747.6 | 769.6 | 149.1 | 279.2 | 285.9 | 230.2 | 167.2 | 269 | 275.5 | 207.5
618.1 | 342.1 | 468.3 | 187.32 | 218.9663 | 215.8 | 278.7 | 272.3 | 265.8 | 453.2 | 33.2 | 20.7 | 66.1 | 7.8 | 250.8 | 23.1 | 876.8 | 822.2 | 865.7 | 822.7 | 776.5 | 716.1 | 622.1 | 807.9 | 670.8 | 797.6 | 387.6 | 752.1 | 769.8 | 149.4 | 279.2 | 286.2 | 230.6 | 167.6 | 269.1 | 275.8 | 207.9
619.1 | 343.1 | 469.1 | 187.64 | 219.3403 | 216.7 | 278.9 | 273.1 | 265.8 | 458.4 | 33.3 | 20.7 | 66.3 | 5.9 | 245.5 | 24.7 | 875.9 | 820.8 | 873.7 | 826.2 | 780.2 | 717.3 | 623.2 | 803.8 | 679.2 | 798.1 | 389.2 | 755.5 | 769.8 | 149.7 | 279.5 | 286.3 | 231.3 | 167.9 | 269.1 | 275.6 | 208.2
620.1 | 344.1 | 468.3 | 187.32 | 218.9663 | 216.1 | 277.4 | 273.3 | 265.9 | 461.4 | 33.3 | 20.7 | 66.4 | 4.6 | 240.5 | 21.4 | 875.2 | 819.4 | 878.7 | 827.8 | 781.6 | 718.1 | 624 | 804.7 | 685.7 | 797.7 | 391 | 759.1 | 769.7 | 150 | 279.9 | 286.4 | 231.9 | 168.2 | 268.8 | 275.5 | 208.6
621.1 | 345.1 | 468.3 | 187.32 | 218.9663 | 216.7 | 277.9 | 272.9 | 266.4 | 465 | 33.4 | 20.7 | 66.4 | 5.2 | 251.1 | 18.1 | 881.1 | 819.7 | 870.5 | 830.3 | 782.1 | 719.1 | 626.5 | 801.5 | 692.3 | 797.3 | 392.7 | 757.1 | 769.2 | 150.3 | 280.7 | 286.7 | 232.5 | 168.5 | 269 | 275.5 | 209
622.1 | 346.1 | 468.7 | 187.48 | 219.1533 | 217.6 | 279.5 | 273.1 | 266.9 | 463.2 | 33.5 | 20.7 | 66.5 | 6.2 | 270.5 | 16 | 887 | 820.3 | 860.7 | 832.4 | 781.8 | 719.6 | 630.3 | 800.3 | 696.5 | 799.1 | 394.5 | 751.2 | 769.3 | 150.7 | 280.8 | 287.2 | 232.7 | 168.8 | 269.4 | 276.3 | 209.5
623.2 | 347.2 | 469.9 | 187.96 | 219.7144 | 218.5 | 280.2 | 273.2 | 267.5 | 461.5 | 33.5 | 20.7 | 66.6 | 5.9 | 262.8 | 15.1 | 888.7 | 820.2 | 856.8 | 833.6 | 780.3 | 720 | 630.8 | 801.1 | 699.4 | 799.3 | 396.3 | 748.4 | 769.6 | 151 | 280.9 | 288 | 233 | 169.1 | 269.8 | 276.4 | 210
624.2 | 348.2 | 468.9 | 187.56 | 219.2468 | 217.3 | 280.1 | 273.3 | 268 | 456.9 | 33.6 | 20.7 | 66.7 | 7.2 | 258.1 | 18.5 | 887 | 821.7 | 859.9 | 835.4 | 782.1 | 720.5 | 630.4 | 802.8 | 702.8 | 800.3 | 398 | 748 | 769.8 | 151.3 | 281.2 | 289.3 | 233.5 | 169.4 | 270.1 | 276.3 | 210.4
625.2 | 349.2 | 468.3 | 187.32 | 218.9663 | 217.2 | 279.9 | 272.7 | 268.3 | 453.5 | 33.7 | 20.7 | 66.7 | 8.7 | 255.3 | 18.4 | 887.1 | 823.1 | 864.3 | 837.9 | 782.7 | 720.9 | 627.9 | 804.6 | 707.4 | 799.9 | 399.7 | 748.8 | 770 | 151.6 | 281.6 | 289.8 | 233.9 | 169.7 | 270.5 | 276.3 | 210.8
626.2 | 350.2 | 469.4 | 187.76 | 219.4806 | 215.8 | 279.6 | 272.8 | 267.9 | 450.2 | 33.8 | 20.7 | 66.7 | 8.8 | 253.5 | 20.6 | 888.7 | 823.3 | 864.3 | 840 | 783.5 | 721.5 | 627.1 | 801.9 | 710.7 | 801 | 401.4 | 746.7 | 770 | 151.9 | 281.8 | 289.5 | 234.1 | 170 | 271 | 276.6 | 211.1
627.2 | 351.2 | 470.6 | 188.24 | 220.0417 | 216.5 | 280.1 | 271.8 | 267.6 | 449.4 | 33.9 | 20.7 | 66.7 | 9.1 | 245.6 | 21.6 | 890.4 | 822.6 | 863.5 | 840.6 | 782.8 | 721.8 | 627.4 | 801.2 | 712.9 | 801.2 | 403 | 743.8 | 770.1 | 152.3 | 281.6 | 289.4 | 234.4 | 170.3 | 271.2 | 276.7 | 211.5
628.2 | 352.2 | 469.8 | 187.92 | 219.6677 | 217.1 | 279.6 | 271.2 | 266.9 | 450.3 | 34 | 20.7 | 66.6 | 7.2 | 246.2 | 22.6 | 892.4 | 822.7 | 858.8 | 842.2 | 780 | 721.9 | 627.6 | 795.9 | 715 | 801.9 | 404.7 | 741 | 770.6 | 152.6 | 281.5 | 289.2 | 234.7 | 170.6 | 271.6 | 276.9 | 212
629.2 | 353.2 | 469.8 | 187.92 | 219.6677 | 217.9 | 280.1 | 271.5 | 266.9 | 451.5 | 34 | 20.7 | 66.5 | 5.8 | 264.3 | 19.5 | 892.9 | 822.6 | 858.5 | 844.2 | 780.8 | 722 | 628.7 | 794.3 | 716.7 | 802.3 | 406.3 | 738.5 | 771.5 | 152.9 | 281.3 | 288.8 | 235 | 170.9 | 272 | 277 | 212.4
630.2 | 354.2 | 469.5 | 187.8 | 219.5274 | 218.3 | 280.3 | 272 | 267 | 450.8 | 34.1 | 20.7 | 66.4 | 4.9 | 273.6 | 16 | 893.2 | 822.9 | 858.5 | 845.9 | 780.5 | 722.2 | 629.8 | 794.2 | 718.4 | 803.5 | 408 | 736.3 | 772 | 153.3 | 281 | 288.5 | 235.3 | 171.2 | 272.5 | 277.1 | 212.8
631.2 | 355.2 | 469.9 | 187.96 | 219.7144 | 217.6 | 279.6 | 272.7 | 267.2 | 450.8 | 34.1 | 20.7 | 66.3 | 5.7 | 263.7 | 13.1 | 894.7 | 822.6 | 862 | 847.1 | 781.7 | 722.4 | 630.3 | 797.8 | 720.8 | 803.7 | 409.6 | 736.3 | 772.2 | 153.6 | 280.8 | 288.5 | 235.5 | 171.5 | 272.8 | 277.3 | 213.1
632.2 | 356.2 | 467.9 | 187.16 | 218.7793 | 217.1 | 279.8 | 272.7 | 267.4 | 447.4 | 34.2 | 20.7 | 66.4 | 5.6 | 260.8 | 12.2 | 896.9 | 822.3 | 859.1 | 847.5 | 779.4 | 722.9 | 628.9 | 792.8 | 723.6 | 803.4 | 411.2 | 736.2 | 772.6 | 153.9 | 280.6 | 288.3 | 235.6 | 171.8 | 272.4 | 277.3 | 213.4
633.2 | 357.2 | 467.2 | 186.88 | 218.452 | 217.1 | 279.6 | 272.4 | 267.7 | 444.6 | 34.2 | 20.7 | 66.5 | 6.5 | 245.1 | 13.2 | 898.4 | 823.1 | 854.1 | 849.2 | 777.2 | 723.1 | 627.5 | 787.2 | 726.6 | 802.3 | 412.9 | 734.9 | 772.9 | 154.3 | 280.4 | 288.1 | 235.7 | 172 | 272.2 | 277.1 | 213.7
634.2 | 358.2 | 467.2 | 186.88 | 218.452 | 216.4 | 279.1 | 272.4 | 267.6 | 442.6 | 34.3 | 20.7 | 66.7 | 7.7 | 254.3 | 14.1 | 899.8 | 824 | 859.9 | 851.6 | 775.1 | 724 | 625.7 | 791.1 | 731.1 | 801.3 | 414.4 | 736.7 | 774.2 | 154.6 | 280.3 | 288 | 235.9 | 172.3 | 271.9 | 277 | 214.1
635.2 | 359.2 | 468.2 | 187.28 | 218.9195 | 215.5 | 277.2 | 272.7 | 267.4 | 439.1 | 34.4 | 20.7 | 67 | 7.6 | 257.9 | 16.5 | 901.6 | 825.2 | 865.8 | 853.3 | 775 | 725.3 | 625.2 | 798.9 | 734 | 801.7 | 415.9 | 740.4 | 776 | 154.9 | 280.4 | 287.7 | 236.2 | 172.6 | 271.3 | 276.8 | 214.4
636.2 | 360.2 | 468.3 | 187.32 | 218.9663 | 215.3 | 276.7 | 272.9 | 267.3 | 440.2 | 34.5 | 20.7 | 67.1 | 5.5 | 251.4 | 18 | 905.2 | 826 | 864.2 | 854.6 | 772.1 | 726.1 | 625.9 | 792.6 | 736 | 801.3 | 417.4 | 737.9 | 777.3 | 155.3 | 280.4 | 287.6 | 236.6 | 172.9 | 270.9 | 277.3 | 214.8
637.2 | 361.2 | 468.7 | 187.48 | 219.1533 | 215.3 | 276.3 | 272.9 | 267.3 | 441.2 | 34.6 | 20.7 | 67.1 | 4.4 | 242.5 | 18.6 | 906.6 | 824.5 | 859.7 | 854.9 | 769.5 | 727.3 | 625.2 | 788.9 | 738.4 | 799.8 | 418.9 | 736.1 | 777.3 | 155.6 | 280.1 | 287.5 | 236.9 | 173.1 | 270.9 | 277.4 | 215.2
638.2 | 362.2 | 469.8 | 187.92 | 219.6677 | 215.5 | 274.6 | 273.1 | 267.6 | 441.8 | 34.7 | 20.7 | 67.2 | 4.2 | 256.8 | 16.7 | 907.7 | 822.3 | 862.1 | 854.8 | 766.8 | 728.2 | 623.4 | 791.5 | 739.8 | 798.2 | 420.3 | 739.1 | 777.6 | 155.9 | 280.1 | 287.5 | 237.4 | 173.4 | 270.7 | 277.5 | 215.5
639.2 | 363.2 | 468.8 | 187.52 | 219.2001 | 217.1 | 273.6 | 273.8 | 268.5 | 445.5 | 34.7 | 20.7 | 67.2 | 4.2 | 258.8 | 14.8 | 907.5 | 819.5 | 866.4 | 854.3 | 765.7 | 729.5 | 622.5 | 789.1 | 741.7 | 796.1 | 421.7 | 743.9 | 779 | 156.3 | 280.6 | 287.5 | 238 | 173.7 | 270.2 | 277.7 | 215.8
640.2 | 364.2 | 468.5 | 187.4 | 219.0598 | 218.5 | 273.1 | 274.1 | 269 | 453.2 | 34.6 | 20.7 | 67.3 | 4.5 | 265.6 | 12.4 | 907.9 | 817.3 | 871.1 | 854.8 | 763.6 | 731.1 | 622.9 | 788.6 | 744.1 | 794.2 | 423.2 | 748.8 | 780.5 | 156.6 | 281.1 | 287.7 | 238.7 | 174 | 269.9 | 278.1 | 216.1
641.2 | 365.2 | 468.3 | 187.32 | 218.9663 | 220.2 | 275 | 274.4 | 270.2 | 453.4 | 34.6 | 20.7 | 67.4 | 5.1 | 259.1 | 12.2 | 909.7 | 817.3 | 872 | 855.5 | 763.2 | 732.7 | 623.7 | 789.1 | 746.3 | 794.3 | 424.6 | 747.6 | 782 | 156.9 | 281.3 | 288.3 | 239 | 174.3 | 270.1 | 278.4 | 216.7
642.2 | 366.2 | 468.1 | 187.24 | 218.8728 | 222 | 275.8 | 274.4 | 271.4 | 451.5 | 34.6 | 20.6 | 67.5 | 5.1 | 256.6 | 15.9 | 911.6 | 817.4 | 874.7 | 856.1 | 764.1 | 734.3 | 624.4 | 788.7 | 748.7 | 794 | 426.1 | 746.2 | 783.3 | 157.2 | 281.6 | 288.6 | 239.3 | 174.6 | 270.4 | 278.6 | 217.1
643.2 | 367.2 | 468.5 | 187.4 | 219.0598 | 224.2 | 276.1 | 273.7 | 271.8 | 454.2 | 34.6 | 20.6 | 67.5 | 7.1 | 263.9 | 16.8 | 911.2 | 815.8 | 876.4 | 856 | 761.2 | 735.9 | 623.9 | 781.3 | 752.1 | 791.1 | 427.5 | 746.4 | 783.2 | 157.5 | 282.1 | 289 | 240.2 | 174.9 | 270.5 | 278.8 | 217.4
644.2 | 368.2 | 469.7 | 187.88 | 219.6209 | 226.1 | 275.6 | 273.5 | 271.4 | 457.2 | 34.6 | 20.6 | 67.7 | 7.3 | 277.3 | 14.3 | 911.4 | 814.3 | 876.1 | 856.8 | 758.7 | 738.1 | 624.7 | 782 | 755.6 | 789.1 | 428.8 | 749.8 | 784.2 | 157.9 | 282.9 | 289.5 | 241.1 | 175.2 | 270.4 | 279.3 | 217.7
645.2 | 369.2 | 469 | 187.6 | 219.2936 | 227.1 | 275.3 | 274.5 | 271 | 459 | 34.6 | 20.6 | 67.8 | 7.5 | 266.5 | 12.8 | 912.7 | 814 | 881 | 858.3 | 757.2 | 740.7 | 625.2 | 786.7 | 758.7 | 788.2 | 430.2 | 752.7 | 785.2 | 158.2 | 283.6 | 290.2 | 241.4 | 175.4 | 270.5 | 279.8 | 218.1
646.2 | 370.2 | 469.2 | 187.68 | 219.3871 | 229 | 275.7 | 275.6 | 271 | 463.5 | 34.6 | 20.6 | 68 | 7.2 | 258.7 | 14.7 | 913.2 | 814.8 | 886.6 | 860.4 | 756.5 | 742.7 | 625.7 | 789.5 | 760.4 | 788.4 | 431.6 | 756.2 | 786.5 | 158.5 | 284.1 | 290.7 | 241.9 | 175.7 | 270.7 | 280.1 | 218.6
647.2 | 371.2 | 468.7 | 187.48 | 219.1533 | 227.9 | 275.4 | 275.9 | 271.5 | 467.2 | 34.7 | 20.6 | 68.2 | 6 | 270.6 | 13.8 | 913.9 | 814.1 | 888.3 | 861.5 | 754.9 | 744.4 | 624.9 | 790.9 | 762.6 | 787.1 | 433 | 757.2 | 788.1 | 158.8 | 284.9 | 291.1 | 242 | 176 | 270.8 | 280.1 | 218.9
648.2 | 372.2 | 468.6 | 187.44 | 219.1066 | 229.1 | 275.3 | 275.6 | 272.2 | 465 | 34.8 | 20.6 | 68.2 | 5 | 247.5 | 12.5 | 914.9 | 813.7 | 886 | 862.4 | 755 | 746.1 | 623.8 | 789 | 764.2 | 786 | 434.3 | 757.4 | 788.8 | 159.2 | 285.7 | 291.4 | 242.1 | 176.3 | 270.8 | 280.1 | 219.2
649.2 | 373.2 | 470 | 188 | 219.7612 | 229.9 | 275.9 | 275.7 | 272.3 | 465.2 | 34.8 | 20.6 | 68.2 | 4.7 | 247 | 13.7 | 915.5 | 812.7 | 884.8 | 863 | 752.7 | 748.1 | 623 | 781.5 | 766.4 | 784.1 | 435.7 | 759.3 | 789 | 159.5 | 286.9 | 291.8 | 242.7 | 176.6 | 270.9 | 280.4 | 219.6
650.2 | 374.2 | 470.4 | 188.16 | 219.9482 | 228.5 | 276.7 | 276.2 | 272.1 | 466.7 | 34.9 | 20.6 | 68.2 | 4.8 | 260.1 | 12.8 | 915.3 | 811.2 | 881.3 | 863.4 | 749.7 | 750.3 | 623.3 | 776 | 769.1 | 781.3 | 437.1 | 760.4 | 788.6 | 159.8 | 288 | 292.7 | 243.7 | 176.9 | 271.3 | 280.4 | 219.9
651.2 | 375.2 | 470.4 | 188.16 | 219.9482 | 228 | 278.3 | 277.5 | 272.4 | 470 | 35 | 20.6 | 68.3 | 5.5 | 220.6 | 10.5 | 916.9 | 809.9 | 884 | 863.8 | 749.3 | 752.7 | 623.4 | 776.9 | 771.5 | 780.3 | 438.5 | 761.1 | 788.2 | 160.2 | 289 | 293.5 | 244.1 | 177.3 | 271.8 | 280.3 | 220.2
652.2 | 376.2 | 470.3 | 188.12 | 219.9014 | 229.4 | 278.4 | 277.9 | 273.1 | 469.8 | 35 | 20.6 | 68.4 | 6.5 | 258.3 | 9.4 | 917.3 | 810 | 891.3 | 864.5 | 749.2 | 753.9 | 623.1 | 778.8 | 772.2 | 780.9 | 439.8 | 763.5 | 789.1 | 160.5 | 290 | 294.1 | 244.5 | 177.5 | 271.9 | 280.2 | 220.6
653.2 | 377.2 | 469.7 | 187.88 | 219.6209 | 230.9 | 279.1 | 276.8 | 273.7 | 480 | 35 | 20.6 | 68.6 | 7.3 | 244.2 | 10.2 | 916.8 | 810.1 | 894.6 | 865.2 | 747.9 | 755.5 | 622.7 | 778 | 774 | 778.7 | 441.2 | 768.7 | 789.7 | 160.9 | 291.3 | 295 | 245.3 | 177.8 | 271.8 | 280.5 | 220.9
654.2 | 378.2 | 470.4 | 188.16 | 219.9482 | 231.4 | 279.7 | 276.8 | 274.5 | 486.7 | 35.1 | 20.6 | 68.9 | 7.7 | 248.3 | 10.5 | 915.8 | 809.4 | 896.8 | 865.4 | 747.2 | 757 | 622.7 | 778.2 | 776.5 | 777.7 | 442.5 | 772.4 | 789.2 | 161.3 | 292.4 | 295.6 | 246 | 178.1 | 271.8 | 280.8 | 221.3
655.2 | 379.2 | 470.1 | 188.04 | 219.8079 | 232.1 | 278.2 | 275.9 | 275.1 | 497 | 35.1 | 20.6 | 69.1 | 7.2 | 251.6 | 11.6 | 915 | 809.1 | 896.7 | 865.3 | 745.9 | 758.3 | 623 | 778.6 | 778.2 | 776.5 | 443.9 | 775.8 | 788.9 | 161.6 | 293.9 | 296.2 | 246.6 | 178.4 | 271.7 | 281.1 | 221.7
656.2 | 380.2 | 470.1 | 188.04 | 219.8079 | 232.9 | 276 | 275.6 | 275.6 | 521.4 | 35.2 | 20.6 | 69.2 | 7.5 | 247.7 | 12.2 | 915.2 | 808.3 | 896.2 | 865.1 | 743.6 | 759.5 | 622.4 | 779.6 | 780 | 775.1 | 445.3 | 778.2 | 788.2 | 162 | 294.9 | 296.7 | 247.3 | 178.7 | 271.8 | 282.1 | 222
657.2 | 381.2 | 469.6 | 187.84 | 219.5741 | 233.4 | 274 | 276.8 | 277 | 531.3 | 35.2 | 20.6 | 69.4 | 7.9 | 254.1 | 12.5 | 916.5 | 809.8 | 893.3 | 865.6 | 741.6 | 760.4 | 623.2 | 785 | 780.8 | 774.9 | 446.7 | 779.5 | 788 | 162.3 | 295.9 | 297.2 | 247.7 | 179 | 272.1 | 283 | 222.4
658.2 | 382.2 | 469.9 | 187.96 | 219.7144 | 234.9 | 272.7 | 277.4 | 278 | 524.9 | 35.3 | 20.6 | 69.6 | 8.7 | 254.3 | 18.8 | 916.3 | 811.7 | 889.9 | 866.2 | 739.9 | 761.5 | 623.9 | 786 | 781.3 | 773.5 | 448.2 | 776.8 | 788.2 | 162.7 | 296.7 | 297.8 | 248.4 | 179.2 | 272.6 | 283.7 | 222.7
659.2 | 383.2 | 468.2 | 187.28 | 218.9195 | 235.9 | 271.8 | 277.6 | 278.4 | 518.4 | 35.4 | 20.6 | 69.7 | 7 | 249.9 | 20.9 | 917.1 | 813.2 | 882.2 | 867 | 738.1 | 762.9 | 624.4 | 778.7 | 782.5 | 772.7 | 449.9 | 771.2 | 788 | 163.1 | 297.2 | 298.1 | 248.5 | 179.5 | 272.8 | 284.6 | 223.2
660.2 | 384.2 | 470.8 | 188.32 | 220.1352 | 237 | 270 | 277.2 | 278.9 | 506.8 | 35.4 | 20.6 | 69.8 | 6.3 | 250 | 18.8 | 917.8 | 814 | 878.6 | 867.6 | 737.3 | 764.2 | 623.4 | 777.5 | 783.4 | 772 | 451.5 | 767 | 788.7 | 163.5 | 297.5 | 298.3 | 248.5 | 179.8 | 273.1 | 285 | 223.6
661.2 | 385.2 | 468.4 | 187.36 | 219.013 | 237 | 270.2 | 276.2 | 279.2 | 499.6 | 35.4 | 20.6 | 69.8 | 6.2 | 248.3 | 20.1 | 917.8 | 816.1 | 878.3 | 868.6 | 737.7 | 765.1 | 624.3 | 783.1 | 783.6 | 772.3 | 452.9 | 767.7 | 790.1 | 163.9 | 297.9 | 298.5 | 248.5 | 180.2 | 273.4 | 285.4 | 224.1
662.2 | 386.2 | 467.7 | 187.08 | 218.6857 | 236.3 | 271.1 | 275.7 | 279.5 | 497.7 | 35.4 | 20.6 | 69.9 | 8.3 | 254.9 | 19 | 916.8 | 816 | 876.5 | 868.9 | 736.7 | 766.5 | 624.8 | 782.3 | 785.4 | 770.3 | 454.1 | 769.3 | 791 | 164.2 | 298.4 | 298.6 | 248.9 | 180.5 | 273.9 | 285.7 | 224.5
663.2 | 387.2 | 468 | 187.2 | 218.826 | 235.3 | 271.7 | 276 | 279.3 | 498.6 | 35.5 | 20.6 | 70 | 7.2 | 251.2 | 19.8 | 915.9 | 815.1 | 883 | 869.2 | 736.1 | 768.1 | 625.2 | 785.1 | 788 | 769.6 | 455.3 | 772.2 | 791.7 | 164.6 | 299 | 298.9 | 249.3 | 180.8 | 274.3 | 285.9 | 224.8
664.2 | 388.2 | 468.4 | 187.36 | 219.013 | 235.1 | 272.7 | 276.5 | 278.5 | 512 | 35.5 | 20.6 | 70 | 7.9 | 243.7 | 19.6 | 915.8 | 813.7 | 887.5 | 869.9 | 737.9 | 769.3 | 626.1 | 788.7 | 789.9 | 770.2 | 456.5 | 773 | 792.5 | 165 | 298.9 | 299.1 | 249.5 | 181.1 | 274.3 | 286.1 | 225.1
665.2 | 389.2 | 468.3 | 187.32 | 218.9663 | 235.8 | 272.6 | 277.1 | 278.2 | 513.3 | 35.6 | 20.6 | 70.1 | 7 | 250.3 | 18.6 | 915.1 | 815 | 891.7 | 870.8 | 741.1 | 769.8 | 627 | 793.2 | 790.7 | 771.3 | 457.7 | 777 | 793.2 | 165.4 | 299.2 | 299.6 | 249.8 | 181.4 | 274.4 | 286.3 | 225.4
666.2 | 390.2 | 467.8 | 187.12 | 218.7325 | 235.7 | 273.6 | 277.3 | 278.7 | 513.1 | 35.6 | 20.6 | 70.1 | 6.4 | 260 | 17.5 | 914 | 816.3 | 893.2 | 871.9 | 741.9 | 770.2 | 627.3 | 798.3 | 792.1 | 772.2 | 459 | 780.7 | 793.1 | 165.8 | 299.6 | 300.2 | 250.2 | 181.7 | 274.8 | 286.6 | 225.7
667.2 | 391.2 | 470 | 188 | 219.7612 | 236.3 | 274.7 | 277.2 | 279 | 507.7 | 35.7 | 20.6 | 70.2 | 7.3 | 269.5 | 18 | 913.6 | 818.8 | 892.3 | 873 | 744.3 | 770.8 | 629.5 | 806.4 | 792.8 | 775.4 | 460.4 | 778.7 | 793.5 | 166.1 | 300.1 | 300.7 | 250.4 | 182 | 275.3 | 287 | 226.1
668.2 | 392.2 | 470.3 | 188.12 | 219.9014 | 235.2 | 274.3 | 276.6 | 279.3 | 501.3 | 35.7 | 20.6 | 70.2 | 7.6 | 256 | 18.9 | 913.2 | 819.7 | 893.2 | 873.2 | 746.2 | 770.6 | 629 | 807.5 | 792.9 | 777 | 461.8 | 777.2 | 793.6 | 166.5 | 300.3 | 301.1 | 250.6 | 182.3 | 275.5 | 287.2 | 226.5
669.2 | 393.2 | 470.6 | 188.24 | 220.0417 | 235.2 | 274.8 | 276.2 | 279.3 | 493.1 | 35.8 | 20.6 | 70.1 | 5.7 | 255.1 | 18.7 | 914 | 821.5 | 895.2 | 872.9 | 745.3 | 770.3 | 627.4 | 809.9 | 792.6 | 777.7 | 463.1 | 775.9 | 793.4 | 166.9 | 300.4 | 301.4 | 250.8 | 182.6 | 275.8 | 287.1 | 226.9
670.2 | 394.2 | 470.7 | 188.28 | 220.0885 | 235.8 | 274 | 275 | 279.3 | 494.3 | 35.9 | 20.6 | 70 | 5.7 | 249.9 | 17.9 | 914.2 | 820.6 | 894.4 | 872.6 | 741.8 | 770.9 | 625.9 | 801.6 | 793.7 | 775.3 | 464.5 | 780 | 793.4 | 167.3 | 300.9 | 302 | 251.6 | 182.9 | 275.9 | 287.4 | 227.3
671.2 | 395.2 | 467.1 | 186.84 | 218.4052 | 235.7 | 273.5 | 274.1 | 278.8 | 512.8 | 35.9 | 20.5 | 69.9 | 5.1 | 249.6 | 16.2 | 912.9 | 818.2 | 892.8 | 872.1 | 739.9 | 772.2 | 623.9 | 794.7 | 796.2 | 773.2 | 466 | 781.7 | 792.7 | 167.7 | 301.1 | 302.5 | 252.5 | 183.2 | 275.9 | 287.7 | 227.6
672.2 | 396.2 | 468.1 | 187.24 | 218.8728 | 235.9 | 272.6 | 275.1 | 279.1 | 520 | 36 | 20.6 | 69.8 | 6.4 | 262.9 | 14.6 | 912.6 | 818.5 | 888.9 | 872.6 | 738.1 | 773.3 | 624.4 | 797.1 | 797.6 | 773.4 | 467.4 | 777.1 | 792.8 | 168.1 | 301.2 | 303.1 | 253 | 183.5 | 276 | 287.8 | 227.9
673.2 | 397.2 | 468.3 | 187.32 | 218.9663 | 236.3 | 272.3 | 275.7 | 280 | 511.6 | 36 | 20.5 | 69.9 | 6.7 | 248.9 | 15.2 | 913 | 817.5 | 887.1 | 872.5 | 738.4 | 774.1 | 624.9 | 803.9 | 798.6 | 774.5 | 468.8 | 778.1 | 792.9 | 168.5 | 301.7 | 303.7 | 253.4 | 183.7 | 275.8 | 288.1 | 228.1
674.2 | 398.2 | 467.9 | 187.16 | 218.7793 | 236.9 | 272.9 | 276.3 | 280.7 | 514.8 | 36.1 | 20.5 | 70 | 5.6 | 247.8 | 16.2 | 912.6 | 815.5 | 885.7 | 872.2 | 736.5 | 775.2 | 622.9 | 803.5 | 801 | 773 | 470.2 | 779.6 | 792.7 | 168.8 | 302.5 | 304.8 | 253.9 | 184 | 275.7 | 288.7 | 228.5
675.2 | 399.2 | 468 | 187.2 | 218.826 | 236.1 | 274.2 | 276.9 | 281.5 | 510.9 | 36.2 | 20.5 | 70.1 | 6.1 | 246.1 | 16.3 | 912.2 | 815 | 889.5 | 872.1 | 738.7 | 776 | 622.9 | 807.9 | 802.1 | 774.1 | 471.6 | 779.1 | 792.8 | 169.2 | 302.9 | 305.3 | 254.5 | 184.3 | 275.8 | 288.7 | 228.9
676.2 | 400.2 | 468.3 | 187.32 | 218.9663 | 236.3 | 274.7 | 277 | 282 | 507.3 | 36.3 | 20.5 | 70.2 | 6.5 | 247.2 | 16.1 | 912.2 | 815.3 | 890.3 | 871.7 | 739.1 | 776.2 | 624.4 | 814 | 801.6 | 775.9 | 473 | 778.8 | 794.1 | 169.6 | 303.2 | 305.4 | 254.7 | 184.6 | 275.9 | 289.1 | 229.2
677.2 | 401.2 | 469.2 | 187.68 | 219.3871 | 236.8 | 275.1 | 277 | 282.2 | 504.5 | 36.4 | 20.5 | 70.3 | 5.7 | 245.2 | 16.1 | 911.1 | 816.1 | 893.5 | 871.4 | 739.5 | 776.4 | 625 | 818.4 | 801.6 | 776.8 | 474.4 | 779.4 | 795.7 | 170 | 303.5 | 305.5 | 254.9 | 184.8 | 276 | 289.6 | 229.6
678.2 | 402.2 | 468.4 | 187.36 | 219.013 | 238.6 | 275.7 | 275.8 | 282.9 | 505.3 | 36.5 | 20.5 | 70.4 | 4.9 | 244.7 | 15.9 | 911.8 | 817.7 | 891.6 | 871.7 | 739.3 | 776.8 | 625.6 | 820.9 | 802.2 | 777.1 | 475.8 | 779.5 | 797.3 | 170.4 | 303.6 | 305.5 | 255.1 | 185.1 | 276.6 | 290 | 229.9
679.2 | 403.2 | 468.9 | 187.56 | 219.2468 | 239 | 277 | 275.9 | 283 | 506.7 | 36.5 | 20.5 | 70.4 | 5.3 | 242.3 | 14.9 | 912.1 | 818.6 | 887.7 | 872.3 | 738.9 | 777.3 | 626.8 | 823.3 | 802.6 | 778.1 | 477.1 | 778.6 | 798.8 | 170.8 | 303.5 | 305.6 | 255.3 | 185.4 | 277 | 290 | 230.3
680.2 | 404.2 | 469.9 | 187.96 | 219.7144 | 238.4 | 277.6 | 276.5 | 282.8 | 507.7 | 36.6 | 20.5 | 70.4 | 5.5 | 238.9 | 14.2 | 911.6 | 820.2 | 880.6 | 872.6 | 736.5 | 777.6 | 625.5 | 820.8 | 802.1 | 777.2 | 478.4 | 775.7 | 800.1 | 171.2 | 303.3 | 305.6 | 255.6 | 185.7 | 276.8 | 289.9 | 230.6
681.2 | 405.2 | 469.7 | 187.88 | 219.6209 | 238.1 | 278.9 | 277.3 | 282.5 | 509.8 | 36.6 | 20.5 | 70.3 | 5.3 | 252.5 | 13.3 | 910.8 | 819 | 878.5 | 872.7 | 734 | 778.5 | 625.5 | 812.6 | 803.3 | 775.2 | 479.5 | 776.4 | 801.3 | 171.6 | 303.5 | 305.8 | 255.9 | 186 | 276.8 | 290 | 230.9
682.2 | 406.2 | 470.3 | 188.12 | 219.9014 | 239.8 | 279.3 | 278.2 | 282.8 | 523.9 | 36.7 | 20.5 | 70.2 | 5.3 | 239.7 | 13.8 | 910.1 | 816.2 | 878.6 | 872.5 | 731.7 | 779.8 | 624.7 | 806.9 | 804.7 | 773.1 | 480.6 | 777.5 | 802.3 | 172 | 303.5 | 306.2 | 256.2 | 186.2 | 276.9 | 290.6 | 231.1
683.2 | 407.2 | 470.1 | 188.04 | 219.8079 | 240.9 | 278.9 | 279.6 | 283.5 | 532.8 | 36.7 | 20.5 | 70.2 | 4.5 | 250.3 | 12.9 | 909.5 | 813.9 | 883.2 | 873 | 731.9 | 781.1 | 624.2 | 805.4 | 806.4 | 772.5 | 481.7 | 782 | 802.2 | 172.4 | 303.6 | 306.7 | 256.4 | 186.5 | 277.4 | 291.1 | 231.5
684.2 | 408.2 | 468.8 | 187.52 | 219.2001 | 240.7 | 277.8 | 280.2 | 283.6 | 528.7 | 36.6 | 20.5 | 70.1 | 4.6 | 253.1 | 13.6 | 909 | 813.9 | 884.1 | 873.5 | 731.8 | 781.7 | 623 | 804.4 | 807.2 | 772.7 | 482.9 | 783.1 | 802.4 | 172.8 | 303.8 | 307.1 | 256.7 | 186.8 | 277.6 | 291.4 | 231.9
685.2 | 409.2 | 470.8 | 188.32 | 220.1352 | 242.5 | 274.9 | 280 | 284.1 | 524.5 | 36.6 | 20.5 | 70.1 | 5.3 | 250.8 | 14.3 | 907.8 | 812.4 | 873.7 | 872.7 | 729.2 | 782.2 | 622 | 796.9 | 808.4 | 770 | 483.9 | 777.1 | 801.8 | 173.2 | 304.2 | 307.2 | 257.1 | 187.1 | 277.6 | 292.1 | 232.2
686.2 | 410.2 | 468.2 | 187.28 | 218.9195 | 243.6 | 272.7 | 279.1 | 284.4 | 513 | 36.6 | 20.5 | 70 | 4.1 | 247.1 | 14.4 | 906.5 | 811.9 | 869.1 | 871.4 | 728.1 | 782.4 | 623.7 | 791.3 | 809 | 769.6 | 484.8 | 770 | 802.3 | 173.6 | 304.4 | 307.5 | 257.2 | 187.3 | 278.2 | 292.7 | 232.6
687.2 | 411.2 | 469.2 | 187.68 | 219.3871 | 243 | 272.4 | 278.8 | 284.4 | 507.9 | 36.8 | 20.5 | 69.9 | 4.3 | 248.6 | 13.3 | 906.3 | 811.1 | 871.9 | 872.4 | 727.1 | 782.6 | 622.3 | 793.7 | 808.9 | 769 | 485.7 | 774.6 | 803.8 | 174 | 304.7 | 307.9 | 257.6 | 187.6 | 278.7 | 292.9 | 233
688.2 | 412.2 | 468.9 | 187.56 | 219.2468 | 243.2 | 273.5 | 278.1 | 284.3 | 509 | 36.9 | 20.5 | 69.8 | 4.9 | 237.1 | 11.7 | 906.1 | 809.3 | 873.3 | 872.7 | 727.1 | 783 | 619.7 | 789.6 | 809.8 | 767 | 486.7 | 774.2 | 804.4 | 174.5 | 305.3 | 308.4 | 258.2 | 187.9 | 279.6 | 292.9 | 233.5
689.2 | 413.2 | 467.6 | 187.04 | 218.639 | 242.9 | 276.3 | 278 | 283.9 | 503.8 | 37.1 | 20.5 | 69.9 | 6.2 | 248.6 | 12.8 | 905.6 | 809.2 | 873.3 | 873.2 | 727.6 | 783.5 | 621 | 793.4 | 811.3 | 767.7 | 487.7 | 773.4 | 805.1 | 174.9 | 305.4 | 308.5 | 258.5 | 188.2 | 280.4 | 292.9 | 233.8
690.2 | 414.2 | 468.6 | 187.44 | 219.1066 | 242.2 | 277.6 | 279.1 | 284 | 511.2 | 37.1 | 20.5 | 70 | 6.1 | 253.9 | 11.4 | 904.3 | 808.1 | 870.8 | 873.4 | 726 | 784.3 | 620.6 | 790.9 | 813.9 | 765.8 | 488.6 | 773.9 | 804.7 | 175.3 | 306 | 308.7 | 259 | 188.5 | 280.1 | 293.3 | 234.3
691.2 | 415.2 | 468.2 | 187.28 | 218.9195 | 242.5 | 278.2 | 279.4 | 284.4 | 519.5 | 37.2 | 20.5 | 70.1 | 7.3 | 260.4 | 10.9 | 903.9 | 808.8 | 870.3 | 873.6 | 727.1 | 784.9 | 620.6 | 790.8 | 816 | 765.2 | 489.5 | 773.5 | 804.9 | 175.8 | 306.5 | 308.8 | 259.5 | 188.8 | 280 | 293.5 | 234.6
692.2 | 416.2 | 469.8 | 187.92 | 219.6677 | 243.9 | 278.8 | 279.6 | 285.2 | 512.3 | 37.2 | 20.5 | 70.3 | 7.1 | 252.3 | 13 | 902.3 | 809.2 | 867.9 | 874.2 | 724.8 | 785.1 | 618.4 | 787.6 | 817.4 | 764.2 | 490.3 | 772.1 | 804.9 | 176.2 | 306.7 | 309 | 259.9 | 189 | 279.8 | 293.6 | 234.8
693.2 | 417.2 | 470.3 | 188.12 | 219.9014 | 244.5 | 279.2 | 279.2 | 285.8 | 507.9 | 37.3 | 20.5 | 70.5 | 6.3 | 248.2 | 13.5 | 901.2 | 807.4 | 862.8 | 873.8 | 720.6 | 785.4 | 616.9 | 776.2 | 819 | 761.4 | 491 | 768.5 | 804.5 | 176.6 | 307.3 | 309.3 | 260.8 | 189.3 | 280.1 | 293.7 | 235.2
694.2 | 418.2 | 470.1 | 188.04 | 219.8079 | 244.8 | 278.6 | 279.6 | 286.4 | 509.5 | 37.4 | 20.5 | 70.6 | 7 | 245.2 | 13.5 | 900 | 804.7 | 858.5 | 872.9 | 718.7 | 785.8 | 614.9 | 768.6 | 820.4 | 759.5 | 491.7 | 765.1 | 804.3 | 177.1 | 307.7 | 309.9 | 261.8 | 189.6 | 280.5 | 293.7 | 235.4
695.2 | 419.2 | 470.2 | 188.08 | 219.8547 | 246.4 | 276.9 | 281.4 | 287 | 506.7 | 37.5 | 20.5 | 70.8 | 6.8 | 243.3 | 14.4 | 899.1 | 801.6 | 852.1 | 871.7 | 716.5 | 786 | 611.6 | 760.3 | 822 | 757.1 | 492.4 | 760.3 | 803.7 | 177.5 | 308.3 | 310.1 | 262.1 | 189.8 | 281.2 | 293.6 | 235.8
696.2 | 420.2 | 469.4 | 187.76 | 219.4806 | 247.9 | 274.4 | 282.4 | 287.5 | 508 | 37.6 | 20.5 | 70.9 | 5.5 | 233.2 | 14.4 | 898.4 | 800.4 | 848.2 | 871.3 | 714.5 | 786.1 | 612.5 | 758.6 | 822.8 | 756.2 | 493.2 | 757.5 | 803.8 | 177.9 | 308.4 | 310.5 | 262.6 | 190.1 | 282.1 | 294.1 | 236.1
697.2 | 421.2 | 468.2 | 187.28 | 218.9195 | 249.3 | 272.6 | 281.9 | 288.1 | 504.8 | 37.6 | 20.5 | 71 | 5.2 | 239.4 | 16.3 | 896.9 | 797 | 841.4 | 870.5 | 711.5 | 786 | 611.8 | 755.1 | 823.1 | 754 | 493.9 | 754.7 | 804.6 | 178.4 | 308.8 | 310.7 | 263.2 | 190.3 | 283.3 | 294.4 | 236.5
698.2 | 422.2 | 468.4 | 187.36 | 219.013 | 249.7 | 273.5 | 281.6 | 288.7 | 501.9 | 37.6 | 20.5 | 71.3 | 6.5 | 249.7 | 18.5 | 895.9 | 796 | 835.3 | 869.2 | 709 | 785.7 | 611.2 | 750.6 | 822.7 | 752.4 | 494.7 | 749.3 | 804.8 | 178.8 | 309.7 | 310.7 | 263.4 | 190.6 | 284.2 | 294.4 | 237
699.2 | 423.2 | 468.9 | 187.56 | 219.2468 | 250 | 275 | 281.4 | 288.9 | 492.6 | 37.6 | 20.5 | 71.5 | 5 | 243.8 | 17.6 | 894.2 | 794.2 | 822.6 | 867.8 | 705 | 785.4 | 611.8 | 740.3 | 822.3 | 750 | 495.4 | 743.5 | 804.9 | 179.2 | 309.2 | 310.4 | 263.3 | 190.8 | 284.8 | 294.3 | 237.5
700.2 | 424.2 | 470.1 | 188.04 | 219.8079 | 249 | 274.5 | 280.6 | 288.5 | 483.3 | 37.6 | 20.5 | 71.7 | 4.3 | 242 | 15.4 | 892.3 | 791.1 | 813.9 | 866.3 | 701.2 | 785.2 | 612.4 | 728.4 | 822.2 | 747.4 | 496.1 | 739.3 | 805.2 | 179.6 | 308.1 | 309.8 | 263.2 | 191.1 | 284.4 | 294.3 | 237.9
701.2 | 425.2 | 468.3 | 187.32 | 218.9663 | 247.6 | 273.4 | 279.4 | 288.4 | 475.4 | 37.7 | 20.5 | 71.8 | 6 | 244.4 | 15.3 | 893.1 | 791.6 | 817.9 | 866.5 | 701.7 | 785 | 612.1 | 737.9 | 822 | 747.2 | 496.8 | 742 | 807.1 | 180.1 | 307.6 | 309.3 | 263.6 | 191.3 | 284.6 | 294.3 | 238.2
702.2 | 426.2 | 467 | 186.8 | 218.3584 | 247.6 | 272.4 | 277.9 | 288.1 | 475.2 | 37.7 | 20.5 | 72 | 6 | 257.9 | 14 | 894.2 | 792.6 | 820.7 | 867.7 | 701.4 | 784.9 | 613.6 | 750.9 | 822.1 | 747.5 | 497.7 | 745.1 | 809.8 | 180.5 | 307.1 | 308.9 | 264.1 | 191.5 | 284.8 | 294.2 | 238.5
703.2 | 427.2 | 468.3 | 187.32 | 218.9663 | 246.9 | 270.7 | 276.5 | 287.6 | 474.1 | 37.7 | 20.5 | 72.4 | 6.7 | 250.6 | 13.7 | 894.6 | 794.2 | 822.4 | 868.7 | 700.7 | 784.6 | 614.3 | 760.3 | 821.9 | 747.6 | 498.5 | 745.4 | 812.5 | 180.9 | 306.7 | 308.8 | 264.3 | 191.8 | 284.9 | 294.4 | 238.7
704.2 | 428.2 | 468 | 187.2 | 218.826 | 246.7 | 270.1 | 276.4 | 287 | 468.1 | 37.8 | 20.5 | 72.8 | 8.3 | 225.9 | 14.9 | 893.3 | 791.1 | 815.9 | 868.5 | 697.6 | 784.3 | 611.8 | 748.8 | 821.5 | 744.9 | 499.1 | 741.2 | 812.9 | 181.3 | 306.7 | 309.1 | 264.5 | 192 | 285.3 | 294.2 | 238.9
705.2 | 429.2 | 467.3 | 186.92 | 218.4987 | 247.7 | 269 | 276.8 | 286.7 | 469.9 | 37.8 | 20.4 | 73.1 | 7.4 | 245.9 | 13.9 | 891.5 | 786.6 | 812.6 | 867.6 | 694.8 | 784.3 | 611.6 | 738.4 | 821.4 | 742.4 | 499.9 | 739.1 | 812.2 | 181.7 | 306.5 | 309.4 | 264.9 | 192.2 | 285.6 | 294.3 | 239.1
706.2 | 430.2 | 468.1 | 187.24 | 218.8728 | 248.2 | 267.4 | 278.2 | 286.3 | 478.5 | 37.9 | 20.4 | 73.3 | 6.5 | 233.2 | 15.4 | 892.5 | 788 | 823.9 | 867.9 | 698 | 784.4 | 614.7 | 747 | 821.4 | 743.4 | 501.1 | 741.6 | 812.5 | 182.2 | 306.4 | 309.5 | 265.2 | 192.4 | 285.8 | 294.8 | 239.5
707.2 | 431.2 | 469.3 | 187.72 | 219.4339 | 247.8 | 268 | 279.1 | 286.6 | 484.4 | 38 | 20.4 | 73.4 | 6.4 | 247.2 | 15.6 | 893.3 | 788.5 | 831.3 | 868.6 | 699 | 784.3 | 614.8 | 755.4 | 821.2 | 743 | 501.9 | 743.6 | 813.7 | 182.6 | 306.4 | 309.7 | 265.6 | 192.7 | 285.6 | 294.7 | 239.8
708.2 | 432.2 | 467.7 | 187.08 | 218.6857 | 246.3 | 268 | 279.2 | 286.4 | 485.8 | 38.1 | 20.4 | 73.6 | 7.3 | 243.2 | 16.9 | 892.8 | 785.8 | 832.4 | 869 | 697.3 | 784.1 | 612.6 | 753.5 | 820.8 | 741.1 | 502.5 | 743.3 | 813.9 | 183 | 306.8 | 310.1 | 266.3 | 192.9 | 285.3 | 294.3 | 240.1
709.2 | 433.2 | 469.5 | 187.8 | 219.5274 | 245.6 | 266.9 | 278.5 | 286.2 | 492.1 | 38.2 | 20.4 | 73.7 | 7 | 244 | 18 | 891.9 | 781.7 | 833.9 | 868.6 | 697.1 | 784.2 | 611.1 | 748.4 | 821 | 738.9 | 503 | 742.4 | 813.7 | 183.4 | 307.4 | 310.4 | 266.6 | 193.1 | 284.8 | 294.2 | 240.2
710.2 | 434.2 | 469.9 | 187.96 | 219.7144 | 245.3 | 265.9 | 277.1 | 286.3 | 490.3 | 38.3 | 20.4 | 73.9 | 5.8 | 245.4 | 18.1 | 892 | 781.9 | 826.8 | 867.9 | 695.7 | 784.1 | 611.7 | 746.8 | 821.1 | 738.3 | 503.6 | 738.8 | 813.2 | 183.8 | 308.2 | 310.9 | 266.9 | 193.3 | 284.5 | 293.8 | 240.4
711.2 | 435.2 | 468.8 | 187.52 | 219.2001 | 246.3 | 265.8 | 276.4 | 286.5 | 483.1 | 38.4 | 20.4 | 73.9 | 7.8 | 240.3 | 16.4 | 891.7 | 785.3 | 821.8 | 868.8 | 694.1 | 783.5 | 612.5 | 751.2 | 819.6 | 738.6 | 504.2 | 734.5 | 814.1 | 184.2 | 308.4 | 311.2 | 267 | 193.5 | 284.3 | 293.7 | 240.7
712.2 | 436.2 | 468.9 | 187.56 | 219.2468 | 247.1 | 265.2 | 275.5 | 286.3 | 478.5 | 38.4 | 20.4 | 74 | 6.7 | 243.4 | 13.8 | 890.7 | 785.7 | 813.8 | 868.9 | 692.5 | 783.1 | 611.8 | 745.4 | 818.6 | 736.8 | 504.6 | 729.6 | 814.8 | 184.6 | 308.4 | 311.3 | 267.2 | 193.7 | 284.1 | 293.7 | 240.9
713.2 | 437.2 | 465.8 | 186.32 | 217.7973 | 247.9 | 264.7 | 276 | 286.3 | 473.1 | 38.4 | 20.4 | 74 | 6.3 | 254.9 | 12.1 | 890.5 | 784.5 | 811.4 | 869.1 | 690.6 | 783.1 | 611.4 | 739.2 | 818.1 | 735 | 505 | 729.1 | 816.2 | 185.1 | 308.5 | 311.5 | 267.4 | 194 | 283.8 | 293.7 | 241.1
714.2 | 438.2 | 464.1 | 185.64 | 217.0025 | 246.4 | 265.1 | 277 | 286.4 | 477.2 | 38.5 | 20.4 | 74 | 6.6 | 245.9 | 12.8 | 890.2 | 784.1 | 813.2 | 869.8 | 690.8 | 783.1 | 612.5 | 742.7 | 817.8 | 734.8 | 505.3 | 733.2 | 817.6 | 185.5 | 308.9 | 311.6 | 267.5 | 194.2 | 283.5 | 294 | 241.3
715.2 | 439.2 | 464.6 | 185.84 | 217.2363 | 246.3 | 266 | 277.8 | 286.2 | 476 | 38.4 | 20.4 | 73.9 | 5.6 | 246.6 | 14.5 | 890.6 | 787 | 813.6 | 870.8 | 690.9 | 782.6 | 613.6 | 746 | 817 | 735.7 | 505.5 | 731.8 | 819.1 | 185.9 | 309.3 | 311.6 | 267.7 | 194.4 | 283.1 | 294.2 | 241.6
716.2 | 440.2 | 467.2 | 186.88 | 218.452 | 247.2 | 265.3 | 279 | 286 | 475.4 | 38.5 | 20.4 | 73.9 | 5.7 | 242.5 | 13.9 | 891.3 | 788 | 822.6 | 871.1 | 692.7 | 782.2 | 613.9 | 750.7 | 816.4 | 734.7 | 505.7 | 733.6 | 820.1 | 186.3 | 309.7 | 312 | 267.9 | 194.6 | 283 | 294.8 | 241.9
717.2 | 441.2 | 466.8 | 186.72 | 218.2649 | 250 | 264.2 | 280 | 286.1 | 476.9 | 38.5 | 20.4 | 73.9 | 5.1 | 253.8 | 12.8 | 891.2 | 787.9 | 826 | 870.7 | 692.5 | 782.3 | 613.2 | 748.3 | 816.6 | 733.8 | 505.9 | 734.4 | 820.2 | 186.7 | 310.1 | 312.2 | 268.4 | 194.8 | 283 | 295.2 | 242.1
718.2 | 442.2 | 468.3 | 187.32 | 218.9663 | 250.9 | 265.6 | 280.7 | 286.8 | 474.4 | 38.5 | 20.4 | 74 | 4.5 | 242.4 | 11.7 | 891.3 | 788.3 | 827.3 | 870.5 | 691.5 | 782.3 | 612.3 | 744.2 | 816.3 | 732.2 | 506 | 731.5 | 820.7 | 187.1 | 310.3 | 312.2 | 268.9 | 195 | 283.2 | 295.2 | 242.4
719.2 | 443.2 | 469.3 | 187.72 | 219.4339 | 251.4 | 267.3 | 280.2 | 287.4 | 475.4 | 38.6 | 20.4 | 74.1 | 5.1 | 244.5 | 12.7 | 890.8 | 787.2 | 823.7 | 870.1 | 690.5 | 782.2 | 612.8 | 747.2 | 816.4 | 731.6 | 506.1 | 732.2 | 820.8 | 187.5 | 310.3 | 312.3 | 269.4 | 195.2 | 283.8 | 295.6 | 242.7
720.2 | 444.2 | 470 | 188 | 219.7612 | 252.1 | 267.9 | 279.3 | 287.4 | 475.1 | 38.6 | 20.4 | 74.2 | 5.4 | 237.6 | 12.6 | 888.3 | 781.7 | 814.2 | 868.5 | 686.9 | 782.4 | 610.6 | 730.9 | 816.5 | 728.3 | 506.2 | 725.9 | 820.5 | 187.9 | 310.2 | 312.6 | 269.4 | 195.5 | 284.2 | 295.7 | 243
721.2 | 445.2 | 469.7 | 187.88 | 219.6209 | 253.4 | 269 | 279.9 | 287.2 | 467.9 | 38.6 | 20.4 | 74.4 | 4.7 | 262.9 | 10.8 | 885.7 | 779.3 | 802.9 | 867 | 684.6 | 782.3 | 615.1 | 721.7 | 816.5 | 726.3 | 506.3 | 720.4 | 820.3 | 188.3 | 309.7 | 312.7 | 269.5 | 195.7 | 284.5 | 296.1 | 243.3
722.2 | 446.2 | 468.9 | 187.56 | 219.2468 | 253.6 | 269.8 | 280.5 | 286.3 | 466.7 | 38.7 | 20.4 | 74.5 | 4.3 | 249.1 | 11.6 | 884.1 | 778.3 | 798 | 865.9 | 683.5 | 782.1 | 616.3 | 727.7 | 816.2 | 725.9 | 506.3 | 717.8 | 821.1 | 188.7 | 309.4 | 312.6 | 269.6 | 195.9 | 285 | 296.1 | 243.7
723.2 | 447.2 | 466.1 | 186.44 | 217.9376 | 253.4 | 270 | 280.8 | 286.2 | 465.7 | 38.8 | 20.4 | 74.6 | 4.5 | 240.5 | 11.6 | 882.7 | 773.9 | 789.1 | 865.1 | 680.1 | 782.1 | 614.4 | 717.8 | 816.3 | 723.1 | 506.4 | 713.9 | 822.6 | 189 | 309.3 | 312.4 | 270.1 | 196.1 | 285.7 | 296.1 | 244
724.2 | 448.2 | 466.7 | 186.68 | 218.2182 | 252.7 | 268.3 | 281.7 | 285.8 | 461.9 | 38.9 | 20.4 | 74.7 | 3.8 | 236.4 | 11.6 | 882.2 | 772.5 | 782.9 | 863.3 | 677.6 | 781.8 | 613.3 | 709.8 | 816.1 | 721.2 | 506.4 | 710.3 | 824.5 | 189.4 | 309.5 | 312.4 | 270.4 | 196.3 | 286.2 | 296.2 | 244.2
725.2 | 449.2 | 468.9 | 187.56 | 219.2468 | 254.3 | 267.9 | 282.6 | 285.4 | 460.6 | 39 | 20.4 | 74.8 | 4.6 | 230.7 | 12.3 | 882.8 | 770.4 | 785.2 | 863.1 | 676.4 | 781.7 | 611.6 | 711.1 | 816.1 | 719.8 | 506.3 | 712.9 | 826.2 | 189.8 | 309.9 | 312.4 | 270.8 | 196.5 | 286.2 | 296.2 | 244.4
726.2 | 450.2 | 467.9 | 187.16 | 218.7793 | 255.4 | 269 | 283.2 | 285.3 | 462.8 | 39.1 | 20.4 | 74.9 | 5 | 247.1 | 13.6 | 883.5 | 767.7 | 795.6 | 862.8 | 675.6 | 781.7 | 610.9 | 708.3 | 816.3 | 717.6 | 506.4 | 713.5 | 826.8 | 190.2 | 310 | 312.6 | 271.3 | 196.8 | 285.9 | 296.4 | 244.6
727.2 | 451.2 | 468.5 | 187.4 | 219.0598 | 255.5 | 269 | 284 | 284.9 | 469 | 39.1 | 20.4 | 75.1 | 4 | 265.3 | 13.1 | 884.9 | 768.2 | 803.4 | 862.9 | 678.7 | 781.7 | 611.1 | 719.4 | 816.4 | 718 | 506.5 | 718.4 | 827.7 | 190.6 | 310.1 | 312.9 | 271.7 | 197 | 286.7 | 296.5 | 244.9
728.2 | 452.2 | 470.9 | 188.36 | 220.182 | 256.9 | 269.1 | 283.9 | 285.3 | 474.3 | 39.1 | 20.4 | 75.3 | 4.6 | 257.6 | 15.5 | 884.1 | 766.5 | 810.8 | 864.2 | 680 | 781.8 | 609.3 | 719.1 | 816.7 | 716.6 | 506.6 | 721.7 | 827.3 | 191 | 310.5 | 313.5 | 271.8 | 197.2 | 287.4 | 296.6 | 245.3
729.2 | 453.2 | 470.9 | 188.36 | 220.182 | 258.1 | 269.3 | 283.5 | 285.9 | 479.7 | 39.2 | 20.4 | 75.5 | 5.3 | 239.9 | 14 | 883.2 | 762.5 | 810.7 | 865.1 | 679 | 782 | 613.1 | 713 | 817.2 | 714.2 | 506.9 | 722.4 | 827.2 | 191.4 | 311.1 | 313.9 | 272.2 | 197.4 | 287.3 | 297 | 245.5
730.2 | 454.2 | 468.7 | 187.48 | 219.1533 | 258.8 | 269.5 | 284.5 | 286 | 487.6 | 39.3 | 20.4 | 75.7 | 5.8 | 264.7 | 11.3 | 883.2 | 761.9 | 813.5 | 865.4 | 677.4 | 782.6 | 623.4 | 714.7 | 817.9 | 712.7 | 507.7 | 720.5 | 826.8 | 191.7 | 311.6 | 314.2 | 272.5 | 197.6 | 287.2 | 297.8 | 245.8
731.2 | 455.2 | 469.2 | 187.68 | 219.3871 | 258.8 | 268.9 | 285.7 | 286.1 | 492.7 | 39.4 | 20.4 | 75.9 | 7.1 | 246.9 | 10.4 | 884 | 761.8 | 816.4 | 865.4 | 677.3 | 783 | 627.1 | 724.1 | 818.5 | 711.8 | 508.3 | 720.8 | 826.9 | 192.1 | 312 | 314.8 | 273 | 197.8 | 287.6 | 298.2 | 246.1
732.2 | 456.2 | 469.4 | 187.76 | 219.4806 | 258.7 | 271.2 | 286.6 | 286.9 | 497.5 | 39.5 | 20.4 | 76.1 | 9.2 | 253.2 | 9.7 | 884.7 | 761.3 | 825.6 | 866.3 | 678.4 | 783.3 | 624.5 | 735.7 | 819 | 711.2 | 508.7 | 725.8 | 826.7 | 192.5 | 312.5 | 315.4 | 273.3 | 198 | 288.2 | 298.6 | 246.5
733.2 | 457.2 | 470.4 | 188.16 | 219.9482 | 257.2 | 271 | 286.7 | 287.4 | 502.7 | 39.6 | 20.4 | 76.3 | 7.1 | 255 | 9.6 | 885.5 | 762.7 | 833 | 868.4 | 679.5 | 783.4 | 621.4 | 741.4 | 819 | 711.3 | 509.2 | 730.8 | 826.1 | 192.9 | 313.1 | 315.9 | 274 | 198.3 | 289.1 | 298.7 | 246.8
734.2 | 458.2 | 469.7 | 187.88 | 219.6209 | 257 | 270.7 | 287.1 | 287.9 | 509 | 39.7 | 20.4 | 76.5 | 8.3 | 237.6 | 11.6 | 886.4 | 762.5 | 837.9 | 870.1 | 681.3 | 783.6 | 627.7 | 732.3 | 818.8 | 709.8 | 509.6 | 731.9 | 825.7 | 193.3 | 313.8 | 316.4 | 274.3 | 198.5 | 289.4 | 299.1 | 247.1
735.2 | 459.2 | 468.6 | 187.44 | 219.1066 | 258.3 | 271.1 | 287.2 | 288.6 | 507.4 | 39.7 | 20.4 | 76.6 | 7.4 | 241.4 | 13.7 | 887.7 | 766.9 | 841.2 | 871.3 | 683.8 | 783.8 | 629.4 | 742.1 | 819.1 | 711 | 510.1 | 733.7 | 825.3 | 193.6 | 314 | 317.4 | 274.6 | 198.7 | 289.4 | 299.7 | 247.3
736.2 | 460.2 | 470.2 | 188.08 | 219.8547 | 258.9 | 271.8 | 288.3 | 289.6 | 503.6 | 39.7 | 20.4 | 76.6 | 6.9 | 244.9 | 16.6 | 889.7 | 772.2 | 844.1 | 872.5 | 684 | 783.3 | 629.2 | 759.9 | 818.6 | 712.8 | 510.9 | 733.8 | 824.9 | 194 | 314.3 | 317.7 | 274.7 | 199 | 289.6 | 300.1 | 247.6
737.2 | 461.2 | 470.8 | 188.32 | 220.1352 | 259.1 | 271.2 | 288.9 | 290 | 498.2 | 39.7 | 20.4 | 76.6 | 7.8 | 241.9 | 15.8 | 890.7 | 776.8 | 845.8 | 874.1 | 686.1 | 782.9 | 629 | 765.6 | 818 | 713.3 | 511.4 | 735 | 825.1 | 194.4 | 314.6 | 318 | 274.8 | 199.2 | 290 | 300.3 | 248
738.2 | 462.2 | 470.2 | 188.08 | 219.8547 | 259.2 | 271 | 289.1 | 289.9 | 496.6 | 39.8 | 20.4 | 76.6 | 6.8 | 232 | 13.5 | 890.9 | 778.3 | 839.7 | 875.1 | 684.8 | 782.9 | 627.7 | 763.4 | 817.7 | 712.9 | 511.8 | 734.4 | 825.6 | 194.8 | 314.7 | 318.1 | 274.9 | 199.5 | 290.4 | 300.4 | 248.2
739.2 | 463.2 | 466.7 | 186.68 | 218.2182 | 259.5 | 271.5 | 290 | 289.9 | 494.7 | 39.8 | 20.4 | 76.5 | 6.4 | 229.3 | 10.7 | 892.5 | 782.6 | 840.6 | 875.9 | 686.6 | 782.7 | 629.2 | 776.2 | 816.6 | 714.9 | 512.2 | 735.9 | 825.8 | 195.2 | 315 | 318.1 | 275.3 | 199.7 | 290.6 | 300.2 | 248.6
740.2 | 464.2 | 464.5 | 185.8 | 217.1895 | 260.6 | 270.6 | 290.8 | 289.9 | 493.5 | 39.9 | 20.4 | 76.6 | 6.2 | 231.2 | 8 | 893.5 | 786.7 | 837.2 | 875.6 | 687.3 | 782.2 | 629.8 | 782.3 | 815.5 | 716.8 | 512.7 | 730.2 | 826.2 | 195.6 | 315.1 | 318.1 | 275.3 | 199.9 | 291.4 | 300 | 248.8
741.2 | 465.2 | 469.2 | 187.68 | 219.3871 | 261.4 | 269.9 | 291.5 | 289.6 | 487.2 | 39.9 | 20.4 | 76.7 | 6.6 | 246.2 | 11 | 894.3 | 791.8 | 837.9 | 877 | 689.6 | 782.3 | 628.5 | 787.4 | 815.1 | 718 | 513.3 | 730.1 | 826.7 | 196 | 315 | 318.1 | 275.4 | 200.2 | 292 | 300 | 249.2
742.2 | 466.2 | 468.1 | 187.24 | 218.8728 | 259.9 | 270.5 | 291.5 | 289.5 | 485.3 | 40 | 20.4 | 76.9 | 7.8 | 244.8 | 16.8 | 894.9 | 795.4 | 836.3 | 878.3 | 688.6 | 782.4 | 628.5 | 787.6 | 815.1 | 718.1 | 513.9 | 728.5 | 827.2 | 196.4 | 314.8 | 317.9 | 275.5 | 200.4 | 292.1 | 299.8 | 249.4
743.2 | 467.2 | 469.8 | 187.92 | 219.6677 | 257 | 271.6 | 292.1 | 289.6 | 483.9 | 40 | 20.4 | 76.9 | 9.4 | 234.7 | 18.1 | 895.8 | 798.7 | 836.9 | 879.1 | 688.3 | 782.1 | 630 | 789.3 | 813.9 | 718.6 | 514.4 | 728.7 | 827 | 196.7 | 314.4 | 317.6 | 275.7 | 200.6 | 292.6 | 299.6 | 249.6
744.2 | 468.2 | 467.8 | 187.12 | 218.7325 | 255.2 | 274.2 | 293.2 | 289.1 | 488.4 | 40.1 | 20.3 | 76.9 | 7.2 | 243.3 | 18.5 | 895 | 794.6 | 830.6 | 880.6 | 687.1 | 782.2 | 628 | 784.5 | 813.2 | 717.5 | 514.8 | 729.9 | 827.3 | 197.1 | 314.3 | 317.4 | 276.3 | 200.9 | 292.9 | 299.7 | 249.8
745.2 | 469.2 | 468.4 | 187.36 | 219.013 | 256 | 276.7 | 293.5 | 288 | 493.7 | 40.1 | 20.3 | 76.9 | 6.9 | 244.9 | 18.9 | 895.2 | 793.8 | 828.8 | 880.9 | 687.1 | 782.2 | 627.5 | 780.8 | 812.7 | 716.4 | 515.2 | 725.1 | 828.2 | 197.5 | 313.9 | 317.2 | 276.8 | 201.1 | 292.6 | 299.7 | 250.1
746.2 | 470.2 | 469.2 | 187.68 | 219.3871 | 257.5 | 277.1 | 294 | 287.4 | 488.9 | 40.1 | 20.4 | 76.9 | 6.8 | 243.4 | 17 | 895.4 | 795.4 | 830.1 | 881.2 | 688.5 | 781.8 | 627.9 | 779.2 | 811.6 | 717.1 | 515.7 | 722.9 | 829 | 197.9 | 313.3 | 317.2 | 276.8 | 201.3 | 292.8 | 299.5 | 250.3
747.2 | 471.2 | 468.6 | 187.44 | 219.1066 | 258.8 | 277.5 | 293.4 | 287.5 | 483.3 | 40.2 | 20.4 | 76.9 | 6.7 | 242.6 | 18 | 895.4 | 795.1 | 821.5 | 881.4 | 685.8 | 781.4 | 628 | 779 | 810.5 | 716.4 | 516.1 | 720.5 | 830.1 | 198.2 | 312.9 | 317.6 | 277 | 201.6 | 292.8 | 299.5 | 250.6
748.2 | 472.2 | 468.1 | 187.24 | 218.8728 | 260.2 | 278.6 | 292 | 288 | 477.8 | 40.3 | 20.4 | 76.9 | 5.6 | 256.7 | 18.8 | 896.5 | 798.1 | 821.9 | 881.4 | 686.2 | 780.9 | 629.2 | 769.6 | 809.1 | 717.2 | 516.5 | 716.2 | 830.5 | 198.6 | 312.7 | 318 | 277.4 | 201.8 | 292.9 | 299.4 | 250.9
749.2 | 473.2 | 468.5 | 187.4 | 219.0598 | 261.3 | 278.4 | 290.7 | 287.7 | 475.2 | 40.4 | 20.3 | 76.9 | 5.6 | 255.2 | 18.1 | 897.4 | 802.3 | 824.7 | 881.9 | 688.2 | 780.6 | 628.9 | 772.2 | 808.3 | 718 | 516.9 | 714.2 | 830.9 | 199 | 312.4 | 317.8 | 277.7 | 202 | 293.1 | 299.1 | 251.1
750.2 | 474.2 | 469.4 | 187.76 | 219.4806 | 260.8 | 278 | 289.2 | 287.2 | 470.7 | 40.3 | 20.3 | 76.7 | 6.2 | 263.6 | 17.7 | 898.6 | 804.8 | 831.1 | 883.3 | 691 | 779.9 | 629.2 | 780 | 807 | 719.8 | 517.1 | 714.9 | 832 | 199.3 | 312 | 317.6 | 277.9 | 202.2 | 293.2 | 298.9 | 251.4
751.2 | 475.2 | 469.6 | 187.84 | 219.5741 | 260.8 | 277.3 | 287.8 | 287.2 | 471.2 | 40.4 | 20.3 | 76.7 | 6.3 | 274.5 | 17.6 | 899.6 | 807.5 | 824.6 | 884.1 | 690 | 779.8 | 628.7 | 781.2 | 805.9 | 720.3 | 517.4 | 716.1 | 832 | 199.7 | 311.5 | 317.3 | 277.9 | 202.5 | 292.7 | 298.8 | 251.6
752.2 | 476.2 | 469 | 187.6 | 219.2936 | 261 | 277.5 | 287.3 | 286.6 | 470.9 | 40.4 | 20.3 | 76.7 | 7.8 | 274.9 | 18.6 | 899.9 | 806.3 | 829.8 | 886.4 | 691.1 | 780 | 628.6 | 786.8 | 805.7 | 721.4 | 517.8 | 722.2 | 831.6 | 200.1 | 311.3 | 317.1 | 278 | 202.7 | 292.3 | 298.7 | 251.8
753.2 | 477.2 | 468.2 | 187.28 | 218.9195 | 259.2 | 277.7 | 286.8 | 285.8 | 472.8 | 40.5 | 20.3 | 76.7 | 8 | 275 | 17.7 | 898.9 | 799.4 | 816 | 887.5 | 687.9 | 780.3 | 625.3 | 775.2 | 806 | 719.3 | 518.2 | 721.4 | 831.6 | 200.4 | 311.4 | 316.9 | 278.2 | 202.9 | 291.9 | 298.9 | 251.9
754.2 | 478.2 | 468.2 | 187.28 | 218.9195 | 257.7 | 278.7 | 286.4 | 286.1 | 476.9 | 40.5 | 20.3 | 76.8 | 7.2 | 275.6 | 16.3 | 897.2 | 791 | 806.3 | 888.1 | 685.9 | 780.6 | 622 | 753.1 | 806.5 | 716.6 | 518.4 | 717.3 | 831.7 | 200.8 | 312.1 | 317.1 | 278.7 | 203.1 | 292.1 | 298.8 | 252
755.2 | 479.2 | 469.9 | 187.96 | 219.7144 | 259.2 | 280.1 | 286.6 | 286.1 | 483.2 | 40.6 | 20.3 | 76.8 | 9.2 | 265.8 | 15.7 | 894.9 | 783.6 | 798.1 | 888.9 | 682.8 | 780.8 | 624.1 | 737.7 | 807.1 | 714.6 | 518.6 | 714.2 | 831.5 | 201.1 | 312.5 | 317.1 | 279.1 | 203.4 | 292.1 | 298.6 | 252.1
756.2 | 480.2 | 469.2 | 187.68 | 219.3871 | 259.4 | 280.6 | 286.4 | 285.7 | 483.4 | 40.6 | 20.3 | 76.9 | 8.3 | 256.8 | 15.1 | 893.4 | 775.9 | 790.7 | 889.9 | 679.8 | 781.1 | 622.1 | 729.6 | 807.7 | 712.2 | 518.7 | 713.5 | 830.9 | 201.5 | 313.6 | 317.4 | 279.6 | 203.6 | 291.6 | 299 | 252.3
757.2 | 481.2 | 468.6 | 187.44 | 219.1066 | 258.9 | 281.6 | 286 | 285.5 | 485.6 | 40.7 | 20.3 | 76.9 | 8.5 | 245 | 16.7 | 892.5 | 768.4 | 781.5 | 890.4 | 676.7 | 781.5 | 618.5 | 718.8 | 808.2 | 709.8 | 518.9 | 713.3 | 830.1 | 201.8 | 314.2 | 317.7 | 280.4 | 203.8 | 291.3 | 299.5 | 252.5
758.2 | 482.2 | 469.5 | 187.8 | 219.5274 | 259 | 281.8 | 287.3 | 285.7 | 479.6 | 40.8 | 20.3 | 76.8 | 7.3 | 243.5 | 17.5 | 891.2 | 758.6 | 770 | 889.8 | 673.2 | 781.3 | 613.7 | 698 | 808.1 | 706.4 | 518.9 | 707.4 | 828.8 | 202.1 | 314.7 | 318.3 | 280.5 | 204.1 | 290.8 | 299.8 | 252.7
759.2 | 483.2 | 468.7 | 187.48 | 219.1533 | 260.3 | 281.5 | 288.4 | 285.3 | 476 | 40.8 | 20.3 | 76.8 | 6.3 | 236.4 | 17.6 | 890.3 | 751.8 | 766.3 | 888.8 | 671.7 | 781.2 | 610.1 | 693.1 | 808 | 704 | 519 | 704.7 | 828.1 | 202.4 | 315.3 | 318.6 | 280.7 | 204.3 | 290.9 | 300.7 | 252.9
760.2 | 484.2 | 468.8 | 187.52 | 219.2001 | 260.7 | 279.7 | 288.9 | 285.9 | 481.7 | 40.9 | 20.3 | 76.7 | 7.2 | 236.8 | 16.7 | 890 | 748 | 771.6 | 888.8 | 672.3 | 781.1 | 608.2 | 698.8 | 807.9 | 702.9 | 519 | 708.7 | 827.2 | 202.7 | 315.7 | 319.1 | 281.3 | 204.6 | 291.2 | 301.2 | 253.2
761.2 | 485.2 | 470.2 | 188.08 | 219.8547 | 260.6 | 277.9 | 289.2 | 286.2 | 487.6 | 40.9 | 20.3 | 76.8 | 8.1 | 231.2 | 15.3 | 889 | 743.1 | 774.6 | 889.5 | 671.4 | 781.3 | 605.9 | 698.3 | 807.6 | 701.1 | 519.2 | 712.3 | 826.2 | 203 | 316.3 | 319.6 | 281.9 | 204.9 | 291.4 | 301.8 | 253.4
762.2 | 486.2 | 470 | 188 | 219.7612 | 261 | 277 | 288.6 | 286.5 | 495.6 | 41 | 20.3 | 77 | 6.9 | 225.7 | 14 | 887 | 734.8 | 762.8 | 890.4 | 668.4 | 781.5 | 605.2 | 685 | 806.9 | 698 | 519.3 | 712.8 | 824.6 | 203.3 | 316.9 | 320.2 | 282.3 | 205.2 | 291.9 | 302.3 | 253.7
763.2 | 487.2 | 470.1 | 188.04 | 219.8079 | 261.5 | 278 | 289.7 | 287.7 | 503.9 | 41.1 | 20.3 | 77.3 | 7.2 | 238.2 | 14.6 | 885.7 | 729.3 | 759.5 | 890.5 | 666.8 | 781.8 | 608.6 | 679.9 | 806.6 | 696.5 | 520 | 713.7 | 823 | 203.6 | 317.7 | 321 | 282.6 | 205.4 | 292.8 | 303 | 254
764.2 | 488.2 | 468.8 | 187.52 | 219.2001 | 261.5 | 279.3 | 291.1 | 288.5 | 510.8 | 41.1 | 20.3 | 77.5 | 6.5 | 238.4 | 14.3 | 885.3 | 724.8 | 757.7 | 890.6 | 664.9 | 782.4 | 607.1 | 682.8 | 806.3 | 694.9 | 521.4 | 717.4 | 821.3 | 203.9 | 318.7 | 321.8 | 282.9 | 205.7 | 293.9 | 303.8 | 254.3
765.2 | 489.2 | 469.8 | 187.92 | 219.6677 | 262.2 | 278.9 | 292.5 | 289.4 | 519.6 | 41.2 | 20.3 | 77.6 | 6.1 | 241.9 | 18 | 885.1 | 724.4 | 763.6 | 890.8 | 664.5 | 782.6 | 607.5 | 686.9 | 805.9 | 694.1 | 523 | 719.6 | 820.2 | 204.2 | 319.1 | 322.2 | 283.3 | 206 | 294.7 | 305.2 | 254.6
766.2 | 490.2 | 469.2 | 187.68 | 219.3871 | 261.7 | 279.6 | 293.3 | 291 | 517.4 | 41.3 | 20.3 | 77.8 | 6.5 | 243.7 | 18.7 | 885.9 | 725.9 | 771.3 | 890.7 | 666.7 | 782.5 | 605.6 | 698.6 | 805.2 | 693.7 | 524 | 721.6 | 819.4 | 204.5 | 319.4 | 322.7 | 283.6 | 206.4 | 295.6 | 305.9 | 255
767.2 | 491.2 | 468.9 | 187.56 | 219.2468 | 261.5 | 281.3 | 293.8 | 291.7 | 512.3 | 41.3 | 20.3 | 77.9 | 5.8 | 244.5 | 19.1 | 885.8 | 727.9 | 776.7 | 890.2 | 666.6 | 782.2 | 604.8 | 713.5 | 804.5 | 694.1 | 524.5 | 722.9 | 819.3 | 204.8 | 319.8 | 323.3 | 283.9 | 206.7 | 295.9 | 307.2 | 255.3
768.2 | 492.2 | 468.9 | 187.56 | 219.2468 | 260.8 | 281.4 | 294.7 | 291.9 | 516.6 | 41.4 | 20.3 | 78.1 | 8 | 244.9 | 19.3 | 887.7 | 732.1 | 791.1 | 890.4 | 669.7 | 782.2 | 607 | 733.2 | 804.3 | 696.1 | 525.3 | 730.2 | 819.1 | 205.1 | 320.6 | 324.3 | 284.5 | 207 | 296.2 | 308.1 | 255.7
769.2 | 493.2 | 467 | 186.8 | 218.3584 | 259.9 | 281.1 | 295.4 | 292.2 | 517.8 | 41.4 | 20.3 | 78.3 | 8.8 | 249.6 | 20.2 | 889.2 | 735.9 | 802.3 | 890.7 | 671.6 | 782.1 | 608 | 744.3 | 803.7 | 697.4 | 526.3 | 735.1 | 818.8 | 205.5 | 321.1 | 324.4 | 284.6 | 207.4 | 297.1 | 308.6 | 256
770.2 | 494.2 | 469.3 | 187.72 | 219.4339 | 259.4 | 280.5 | 295.8 | 292.7 | 515.1 | 41.5 | 20.3 | 78.5 | 8.1 | 246.6 | 20.7 | 888.6 | 736.9 | 800.6 | 891 | 672.6 | 781.8 | 606.4 | 744.9 | 802.7 | 696.8 | 526.8 | 733.1 | 819.1 | 205.8 | 321.2 | 324.4 | 284.7 | 207.7 | 297.6 | 308.9 | 256.2
771.2 | 495.2 | 470.1 | 188.04 | 219.8079 | 259.8 | 280.2 | 295.3 | 293.7 | 510 | 41.5 | 20.3 | 78.5 | 7.1 | 244.6 | 18.4 | 888.5 | 741.9 | 795.6 | 891.3 | 671.2 | 781.5 | 607.4 | 751.7 | 802.4 | 697.6 | 527.4 | 734.3 | 819.3 | 206.1 | 321.3 | 324.3 | 285 | 208 | 298 | 309.1 | 256.5
772.2 | 496.2 | 467.3 | 186.92 | 218.4987 | 260.6 | 279.5 | 294.7 | 294.2 | 518.7 | 41.6 | 20.3 | 78.6 | 8.2 | 256 | 16.8 | 889.7 | 750.5 | 796 | 891.4 | 670.9 | 781.6 | 609.1 | 762.7 | 802.3 | 698.1 | 528.7 | 735.4 | 819.4 | 206.4 | 321.2 | 324.3 | 285.2 | 208.4 | 298.4 | 309.4 | 256.8
773.2 | 497.2 | 468.9 | 187.56 | 219.2468 | 259.3 | 280.3 | 293.7 | 294.7 | 514 | 41.7 | 20.3 | 78.6 | 7.7 | 255.4 | 16 | 890.7 | 757.9 | 803 | 892 | 673.5 | 781.4 | 609.4 | 772.1 | 801.4 | 699.9 | 530.1 | 736.4 | 818.8 | 206.7 | 321 | 324.2 | 285.2 | 208.8 | 298 | 310.4 | 257
774.2 | 498.2 | 468.1 | 187.24 | 218.8728 | 259.8 | 281.2 | 292.8 | 295.3 | 507.8 | 41.7 | 20.3 | 78.7 | 7 | 257.9 | 18.1 | 891.4 | 765 | 816.4 | 892.9 | 676.6 | 781.1 | 608.7 | 776.5 | 800.9 | 701.7 | 531.1 | 739.2 | 818 | 207.1 | 320.7 | 323.9 | 285.3 | 209.1 | 298.1 | 310.4 | 257.2
775.2 | 499.2 | 469.5 | 187.8 | 219.5274 | 258.4 | 283 | 291.3 | 295.9 | 502.9 | 41.7 | 20.3 | 78.5 | 6.9 | 262.6 | 21.3 | 892.1 | 771.8 | 819 | 893.1 | 678 | 780.8 | 607.7 | 778.1 | 800.4 | 702.8 | 531.7 | 738.4 | 817.6 | 207.4 | 320.5 | 324.1 | 285.6 | 209.5 | 297.7 | 310.5 | 257.5
776.2 | 500.2 | 469.7 | 187.88 | 219.6209 | 258.4 | 282.3 | 290.9 | 295.9 | 497.7 | 41.7 | 20.3 | 78.4 | 8.5 | 266 | 22.8 | 891.9 | 770.4 | 812.1 | 894.1 | 677.8 | 780.6 | 606 | 765.2 | 799.1 | 701.8 | 532.1 | 735.1 | 817.2 | 207.7 | 320.2 | 324.2 | 285.6 | 209.8 | 297.5 | 311.6 | 257.7
777.2 | 501.2 | 470 | 188 | 219.7612 | 257.4 | 281.3 | 291.3 | 296.4 | 490.2 | 41.7 | 20.3 | 78.5 | 7.8 | 274.8 | 22.6 | 891 | 768.6 | 806.5 | 895.8 | 677 | 780.5 | 603.5 | 748.6 | 798.1 | 700.5 | 532.4 | 731.7 | 817.6 | 208.1 | 320 | 324.5 | 285.8 | 210.2 | 297.4 | 312.2 | 258
778.2 | 502.2 | 469.5 | 187.8 | 219.5274 | 259.4 | 280.8 | 292 | 296.2 | 485.5 | 41.8 | 20.3 | 78.4 | 7.1 | 267.8 | 21.8 | 889.1 | 762.9 | 798.6 | 897.8 | 675.1 | 780.4 | 601.8 | 733.2 | 796.9 | 698.1 | 532.5 | 727.1 | 817.5 | 208.4 | 320.1 | 324.6 | 286.1 | 210.5 | 297.6 | 311.5 | 258.4
779.2 | 503.2 | 468.8 | 187.52 | 219.2001 | 261 | 280.2 | 292.8 | 296 | 485.7 | 41.8 | 20.3 | 78.4 | 6.4 | 267.2 | 21.1 | 889.4 | 767.2 | 790.4 | 899.1 | 674.3 | 779.9 | 601.5 | 729.6 | 795.9 | 698 | 532.6 | 721.9 | 818.2 | 208.8 | 319.9 | 324.5 | 286.3 | 210.9 | 297.7 | 311 | 258.6
780.2 | 504.2 | 469.1 | 187.64 | 219.3403 | 262 | 278.6 | 293.3 | 296 | 481.9 | 41.8 | 20.3 | 78.4 | 7.5 | 271.7 | 18.9 | 890.2 | 772.2 | 787.1 | 900.3 | 673.5 | 779.5 | 602.2 | 728.5 | 795.1 | 698 | 532.6 | 717.6 | 819.2 | 209.1 | 319.6 | 324.1 | 286.4 | 211.2 | 297.8 | 310.9 | 258.7
781.2 | 505.2 | 468.9 | 187.56 | 219.2468 | 262.4 | 278.3 | 293.3 | 295.9 | 481 | 41.8 | 20.3 | 78.5 | 7.1 | 270.2 | 18.2 | 891.7 | 774.2 | 784.5 | 901.8 | 673.5 | 779.1 | 602.6 | 731.5 | 794.9 | 698.9 | 532.6 | 717.6 | 819.8 | 209.4 | 319.5 | 323.8 | 286.6 | 211.5 | 298.3 | 310.4 | 258.9
782.2 | 506.2 | 468.5 | 187.4 | 219.0598 | 261.2 | 278.9 | 293.4 | 295.8 | 479 | 41.9 | 20.3 | 78.5 | 7.6 | 271.7 | 18.6 | 890.7 | 767.8 | 784.6 | 904.4 | 672.1 | 779.2 | 602.3 | 725.7 | 794.8 | 696.9 | 533.2 | 717.9 | 820.2 | 209.8 | 319.5 | 323.7 | 286.8 | 211.9 | 298.5 | 310 | 259.2
783.2 | 507.2 | 469.2 | 187.68 | 219.3871 | 260.8 | 278.9 | 293.6 | 295.8 | 484.1 | 41.9 | 20.3 | 78.5 | 8.7 | 269.5 | 16 | 890.9 | 761.6 | 787.7 | 905.3 | 672.9 | 779.1 | 601.4 | 728 | 794.4 | 695.5 | 534.4 | 718.4 | 820.6 | 210.1 | 319.5 | 323.8 | 287 | 212.2 | 298.4 | 309.9 | 259.4
784.2 | 508.2 | 469.2 | 187.68 | 219.3871 | 260.9 | 278.7 | 293.9 | 296.2 | 486.9 | 42 | 20.3 | 78.6 | 8.1 | 285.9 | 14.2 | 891.2 | 762.6 | 779.9 | 905.8 | 670.6 | 778.7 | 602.5 | 727 | 793.8 | 694.5 | 535.5 | 716.3 | 821.4 | 210.4 | 319.2 | 323.6 | 287.1 | 212.5 | 298.2 | 310.1 | 259.6
785.2 | 509.2 | 470.6 | 188.24 | 220.0417 | 261.8 | 277.3 | 293.1 | 296.8 | 487.5 | 42.1 | 20.3 | 78.6 | 9 | 266.1 | 12.8 | 890.4 | 760.5 | 770.1 | 907.2 | 669.4 | 778.2 | 601.4 | 717 | 792.7 | 693.5 | 536.7 | 712.4 | 822.3 | 210.8 | 319.1 | 323.3 | 287.3 | 212.8 | 297.9 | 310.1 | 259.9
786.2 | 510.2 | 470.1 | 188.04 | 219.8079 | 262.6 | 278.2 | 292.2 | 296.9 | 486.1 | 42.1 | 20.3 | 78.7 | 8.8 | 273.8 | 13.5 | 889.1 | 753.3 | 761.7 | 908.3 | 668.2 | 778 | 598.1 | 699.3 | 791.4 | 690.6 | 538.1 | 707.5 | 823.3 | 211.1 | 318.5 | 322.6 | 287.5 | 213.2 | 298.5 | 310.1 | 260.1
787.2 | 511.2 | 470.5 | 188.2 | 219.995 | 262.1 | 278.8 | 291.3 | 296.7 | 481.6 | 42.2 | 20.3 | 78.7 | 9.5 | 257.9 | 15.4 | 888.7 | 752.6 | 765.4 | 908.9 | 668.6 | 777.7 | 597.5 | 700 | 790.3 | 689.2 | 539.7 | 705.8 | 823.3 | 211.4 | 318.2 | 322 | 287.6 | 213.5 | 299.1 | 310.2 | 260.4
788.2 | 512.2 | 470.8 | 188.32 | 220.1352 | 261.5 | 278.2 | 290.2 | 297.2 | 478.7 | 42.2 | 20.2 | 78.8 | 9.2 | 264.2 | 15.9 | 889.7 | 767.5 | 776.3 | 908.7 | 674.7 | 777.2 | 601.4 | 719.6 | 789.8 | 692.6 | 541.1 | 706 | 823 | 211.7 | 317.8 | 321.4 | 287.6 | 213.8 | 299.2 | 310.4 | 260.6
789.2 | 513.2 | 470 | 188 | 219.7612 | 261.6 | 277.9 | 288.8 | 297.5 | 479.6 | 42.2 | 20.2 | 79 | 9.2 | 266.4 | 14.9 | 889.9 | 775.3 | 780.6 | 909.3 | 677.4 | 776.6 | 605.1 | 726.6 | 788.7 | 694.4 | 541.5 | 702.4 | 822.8 | 212 | 317.3 | 321.3 | 287.4 | 214.1 | 299 | 310.6 | 260.9
790.2 | 514.2 | 469.7 | 187.88 | 219.6209 | 260.4 | 278.2 | 288.1 | 298.2 | 480.4 | 42.2 | 20.2 | 79.3 | 9.8 | 258.2 | 14.6 | 890.3 | 772.4 | 780.7 | 909.4 | 676.2 | 776.3 | 605.7 | 731.2 | 788.1 | 693.7 | 541.6 | 702.1 | 822.5 | 212.3 | 317.3 | 321.6 | 287.5 | 214.4 | 299 | 310.6 | 261
791.2 | 515.2 | 470.5 | 188.2 | 219.995 | 260.4 | 277.8 | 288.3 | 298.2 | 486.7 | 42.2 | 20.2 | 79.6 | 9 | 252.3 | 16.6 | 889.4 | 766.2 | 780.2 | 911.1 | 674.9 | 776.6 | 609.7 | 722.2 | 787.8 | 692.1 | 541.8 | 701.3 | 821.4 | 212.6 | 317.8 | 321.8 | 288 | 214.7 | 299.1 | 310.4 | 261.2
792.2 | 516.2 | 470.9 | 188.36 | 220.182 | 260.1 | 277.7 | 289.5 | 297.8 | 489 | 42.2 | 20.2 | 79.8 | 6.4 | 248.3 | 15.6 | 888.2 | 767 | 776.1 | 912.3 | 676.2 | 777 | 613 | 715.2 | 787.4 | 692.1 | 542.6 | 701.3 | 819.9 | 212.9 | 318.1 | 321.9 | 288.4 | 215 | 299.3 | 310 | 261.3
793.2 | 517.2 | 470.2 | 188.08 | 219.8547 | 261.1 | 277.4 | 290.6 | 296.9 | 492.8 | 42.2 | 20.2 | 79.9 | 6.6 | 257.2 | 15.9 | 889 | 767.8 | 790 | 912.5 | 680.2 | 777.3 | 611.3 | 733.7 | 787.6 | 692.7 | 543.9 | 711.6 | 817.9 | 213.3 | 318.3 | 322.1 | 288.7 | 215.3 | 299.1 | 310 | 261.5
794.2 | 518.2 | 470.4 | 188.16 | 219.9482 | 260.9 | 276.5 | 290.8 | 296.3 | 494.7 | 42.2 | 20.2 | 80 | 7.5 | 262.2 | 18.4 | 891 | 779.8 | 801.8 | 912.1 | 685.7 | 777 | 613 | 749 | 787.9 | 695.8 | 544.8 | 716.2 | 816.4 | 213.6 | 319 | 322.3 | 289.1 | 215.5 | 299.4 | 310 | 261.7
795.2 | 519.2 | 471 | 188.4 | 220.2287 | 260.4 | 276.4 | 290.7 | 296.6 | 493.4 | 42.2 | 20.2 | 80.1 | 7.2 | 274.4 | 19.2 | 890.4 | 783.6 | 809.6 | 913.7 | 689.6 | 776.8 | 612.1 | 749.8 | 788.3 | 696 | 545.5 | 721.6 | 814.1 | 213.9 | 319.3 | 322.5 | 289.5 | 215.8 | 299.3 | 310.1 | 261.9
796.2 | 520.2 | 470.6 | 188.24 | 220.0417 | 259.2 | 275.8 | 291.1 | 296.7 | 499.8 | 42.2 | 20.2 | 80.1 | 5.2 | 276 | 17.8 | 890.1 | 772.9 | 816.8 | 914.7 | 690 | 777.3 | 614.4 | 738.4 | 788.2 | 694.9 | 546.2 | 728 | 810.7 | 214.2 | 319.4 | 323.6 | 290 | 216.1 | 299.2 | 310.4 | 262.1
797.2 | 521.2 | 470.8 | 188.32 | 220.1352 | 259.8 | 276.8 | 292.3 | 296.9 | 504.3 | 42.3 | 20.2 | 80 | 4.2 | 276.1 | 16.5 | 890.9 | 767.5 | 817.9 | 914.2 | 690.2 | 777.6 | 614.2 | 737.5 | 788.1 | 694.4 | 546.7 | 731.5 | 808.4 | 214.6 | 319.7 | 324.2 | 290.4 | 216.4 | 299.2 | 310.4 | 262.3
798.2 | 522.2 | 470.8 | 188.32 | 220.1352 | 259.2 | 277.3 | 293.4 | 297.6 | 504.2 | 42.3 | 20.2 | 79.8 | 5.4 | 274.7 | 15.9 | 892.8 | 774.9 | 817.7 | 913.2 | 693.1 | 777 | 613 | 750.5 | 788.3 | 696.3 | 547.1 | 732.4 | 807.3 | 214.9 | 319.6 | 324.2 | 290.6 | 216.7 | 299 | 310.5 | 262.5
799.2 | 523.2 | 468.7 | 187.48 | 219.1533 | 258.8 | 277.1 | 293.9 | 298.5 | 497.6 | 42.3 | 20.2 | 79.8 | 5.4 | 267 | 16.6 | 893.7 | 779.6 | 811.5 | 913.4 | 694.5 | 776.1 | 612.4 | 758.1 | 787.5 | 696.9 | 547.7 | 730.7 | 806.4 | 215.3 | 319.1 | 324.1 | 290.5 | 217 | 298.8 | 310.6 | 262.7
800.2 | 524.2 | 469.6 | 187.84 | 219.5741 | 258.9 | 277.6 | 293.6 | 298.9 | 488.5 | 42.3 | 20.2 | 79.7 | 4.9 | 260.3 | 20.2 | 892.8 | 784.1 | 801.2 | 915.2 | 693.7 | 775 | 611.5 | 751.6 | 786 | 696.2 | 548.6 | 725.2 | 807 | 215.6 | 318.8 | 324.2 | 290.6 | 217.2 | 299 | 310.5 | 263
801.2 | 525.2 | 470.1 | 188.04 | 219.8079 | 259.2 | 278.3 | 292.6 | 298.9 | 483.9 | 42.3 | 20.2 | 79.8 | 5.3 | 264.5 | 19.3 | 893.1 | 788.2 | 794.6 | 916.5 | 693.2 | 774.2 | 612.5 | 753.6 | 785.1 | 697.1 | 549.9 | 723.4 | 808.5 | 215.9 | 318.6 | 324.1 | 290.7 | 217.5 | 299.1 | 311 | 263.2
802.2 | 526.2 | 469.9 | 187.96 | 219.7144 | 259.2 | 279 | 292 | 299.1 | 480.8 | 42.4 | 20.2 | 79.9 | 6.3 | 279.7 | 16.9 | 892.4 | 781 | 783.9 | 918.1 | 690.5 | 773.6 | 609.1 | 738.9 | 783.6 | 695.2 | 550.6 | 717.6 | 810.5 | 216.3 | 318.2 | 323.6 | 290.7 | 217.8 | 299.2 | 311.1 | 263.4
803.2 | 527.2 | 470.2 | 188.08 | 219.8547 | 257.8 | 279.3 | 291 | 299.9 | 479.6 | 42.4 | 20.2 | 80.2 | 6.3 | 269.2 | 15.1 | 891.6 | 778 | 778.5 | 919.1 | 688.9 | 773.4 | 606.4 | 724.7 | 782.1 | 694.1 | 550.8 | 713.6 | 810.6 | 216.6 | 317.9 | 323.2 | 290.8 | 218.1 | 299 | 310.9 | 263.7
804.2 | 528.2 | 469.3 | 187.72 | 219.4339 | 257.5 | 278.5 | 290.4 | 299.7 | 477.4 | 42.4 | 20.2 | 80.4 | 4.9 | 288 | 16.3 | 892.7 | 780.1 | 776.1 | 918.9 | 689.6 | 773.4 | 604.2 | 723 | 781.4 | 693.9 | 550.9 | 710.9 | 811.1 | 217 | 317.9 | 323.1 | 290.9 | 218.3 | 298.8 | 311.3 | 263.8
805.2 | 529.2 | 470.3 | 188.12 | 219.9014 | 257.5 | 277.1 | 290 | 299.5 | 473.9 | 42.4 | 20.2 | 80.6 | 5.5 | 293.7 | 17.6 | 892.3 | 776.1 | 769.5 | 920.1 | 687.3 | 773.2 | 602.7 | 717 | 781 | 691.8 | 551.1 | 707.7 | 813.1 | 217.3 | 317.8 | 323.1 | 291.1 | 218.6 | 298.4 | 310.8 | 263.9
806.2 | 530.2 | 469.4 | 187.76 | 219.4806 | 257.7 | 275.5 | 290 | 299.3 | 472.7 | 42.4 | 20.2 | 80.7 | 6.2 | 296.7 | 16.2 | 892.9 | 776.2 | 772 | 920 | 686.6 | 772.9 | 600.4 | 720.3 | 780.6 | 691.5 | 552.1 | 703.4 | 813.6 | 217.7 | 317.4 | 323 | 291.2 | 218.9 | 298 | 310.8 | 264.1
807.2 | 531.2 | 469.2 | 187.68 | 219.3871 | 259 | 275.3 | 289.5 | 299.1 | 468.5 | 42.5 | 20.2 | 80.9 | 6.9 | 281.8 | 14.6 | 893.5 | 780.8 | 778.1 | 920.2 | 688.5 | 772.4 | 601.3 | 724 | 780.1 | 692.8 | 553.4 | 704.1 | 813.7 | 218.1 | 317.3 | 322.8 | 291.3 | 219.2 | 298 | 310.8 | 264.4
808.2 | 532.2 | 470 | 188 | 219.7612 | 259.8 | 275.2 | 288.4 | 298.9 | 465.6 | 42.7 | 20.2 | 81 | 6.2 | 283.8 | 13.1 | 893.5 | 779.5 | 775 | 921.2 | 686.6 | 771.8 | 600.1 | 721.2 | 778.9 | 691.8 | 553.9 | 701.1 | 813.4 | 218.4 | 317 | 322.7 | 291.4 | 219.4 | 297.9 | 310.6 | 264.6
809.2 | 533.2 | 471.9 | 188.76 | 220.6496 | 260.2 | 275.1 | 287.5 | 298.7 | 466.7 | 42.8 | 20.2 | 81 | 7 | 256.3 | 10.9 | 894.2 | 785.2 | 773.4 | 921.3 | 685.7 | 771.1 | 601.8 | 731.9 | 777.8 | 692.7 | 554.2 | 701.6 | 813.6 | 218.8 | 316.9 | 322.6 | 291.6 | 219.7 | 297.8 | 310.3 | 264.7
810.2 | 534.2 | 471.5 | 188.6 | 220.4625 | 259.8 | 274.2 | 287.8 | 298.2 | 471.9 | 42.9 | 20.2 | 81.1 | 7.2 | 262.6 | 9.3 | 893.6 | 779.1 | 771.6 | 921.5 | 685.4 | 770.8 | 599.1 | 725.9 | 776.6 | 690.7 | 554.2 | 702.6 | 814.4 | 219.2 | 317.3 | 322.7 | 291.9 | 220 | 298.1 | 310.1 | 264.8
811.2 | 535.2 | 469.5 | 187.8 | 219.5274 | 259.4 | 273.1 | 287.9 | 297.8 | 472.2 | 42.9 | 20.2 | 81.1 | 6.6 | 271 | 8.4 | 893.4 | 780.2 | 776.8 | 921.6 | 685.5 | 770.5 | 597.6 | 726.7 | 775.6 | 690.9 | 554.4 | 703.3 | 815.7 | 219.6 | 317.5 | 322.7 | 292.1 | 220.3 | 298.6 | 309.8 | 265
812.2 | 536.2 | 470.6 | 188.24 | 220.0417 | 260.3 | 272.9 | 287.7 | 297.7 | 471.7 | 42.9 | 20.2 | 81 | 7 | 258.4 | 10.1 | 893.8 | 784 | 780.5 | 920.7 | 686.2 | 770 | 598.8 | 733.5 | 775.4 | 691.6 | 555.1 | 704.5 | 817.1 | 219.9 | 317.5 | 322.6 | 292.2 | 220.6 | 299.2 | 309.4 | 265.3
813.2 | 537.2 | 470.3 | 188.12 | 219.9014 | 259.1 | 273.5 | 287.2 | 297.5 | 471.9 | 43 | 20.2 | 81 | 6.8 | 254 | 11.6 | 893.1 | 788.8 | 772 | 920.5 | 684.8 | 769.6 | 597.6 | 733.8 | 774.6 | 690.8 | 556.4 | 701.3 | 817.6 | 220.3 | 317.4 | 322.6 | 292.2 | 220.8 | 299.4 | 309.3 | 265.5
814.2 | 538.2 | 471.2 | 188.48 | 220.3223 | 258 | 274.1 | 287 | 297.7 | 469.1 | 43 | 20.2 | 81.1 | 6.3 | 261.2 | 12.6 | 893.6 | 802.1 | 775.4 | 920.6 | 688 | 768.7 | 600.2 | 741.4 | 773.9 | 692.3 | 557.7 | 696.3 | 816.6 | 220.7 | 317.1 | 322.5 | 292.1 | 221.1 | 299.4 | 309.5 | 265.7
815.2 | 539.2 | 469.7 | 187.88 | 219.6209 | 258.2 | 275.1 | 287.9 | 298 | 468.5 | 43.1 | 20.2 | 81 | 6.1 | 268.2 | 13.3 | 894.1 | 814.1 | 778.7 | 920.6 | 689.9 | 768.2 | 605 | 753.9 | 773.6 | 694.9 | 558.7 | 694.6 | 815.5 | 221.1 | 316.9 | 322.3 | 292.1 | 221.4 | 299.9 | 309.5 | 266.1
816.2 | 540.2 | 469.5 | 187.8 | 219.5274 | 258 | 275.3 | 288.1 | 297.8 | 468.7 | 43 | 20.2 | 81.1 | 6.4 | 257.3 | 12.5 | 894 | 817.9 | 780.7 | 920.9 | 693.9 | 768 | 607.4 | 752.5 | 773 | 696.3 | 559 | 693.5 | 814.2 | 221.5 | 316.7 | 322.2 | 292.1 | 221.7 | 300.3 | 309.6 | 266.3
817.2 | 541.2 | 468.5 | 187.4 | 219.0598 | 258.1 | 275.6 | 288 | 297 | 469.2 | 43 | 20.2 | 81.2 | 6.6 | 268.5 | 12.6 | 892 | 806.2 | 769.5 | 922.1 | 690.3 | 768.2 | 608.4 | 743.4 | 772.7 | 694.4 | 559.1 | 690.6 | 812.3 | 221.9 | 316.4 | 322.1 | 292.2 | 222 | 300.8 | 309.5 | 266.5
818.2 | 542.2 | 469.1 | 187.64 | 219.3403 | 258.8 | 275.1 | 287.4 | 296.3 | 470.8 | 43 | 20.2 | 81.2 | 5.2 | 254.9 | 13.9 | 888.5 | 790.8 | 756.2 | 923.9 | 686 | 768.6 | 614.9 | 714.7 | 772.7 | 691.2 | 560.2 | 683.3 | 811.6 | 222.3 | 316.4 | 322 | 292.3 | 222.3 | 301.2 | 309.6 | 266.8
819.2 | 543.2 | 469.3 | 187.72 | 219.4339 | 260.7 | 274.4 | 287.5 | 296.2 | 471.3 | 43 | 20.2 | 81.1 | 5.2 | 238.1 | 11.8 | 886.9 | 792 | 752.4 | 925.1 | 683.6 | 769.3 | 628.7 | 705.1 | 772.6 | 690.2 | 561.8 | 679.3 | 811.1 | 222.7 | 316.8 | 321.7 | 292.3 | 222.6 | 301.9 | 309.6 | 267.1
820.2 | 544.2 | 468.6 | 187.44 | 219.1066 | 262.1 | 274.1 | 287.6 | 296.3 | 471.8 | 42.9 | 20.2 | 81.2 | 6.8 | 254.5 | 11.5 | 888 | 797.3 | 749.9 | 924.9 | 684.8 | 769 | 627.8 | 717.2 | 772.6 | 692.1 | 563.1 | 677.7 | 810.7 | 223.1 | 317.2 | 321.7 | 292.7 | 222.8 | 302.9 | 309.7 | 267.5
821.2 | 545.2 | 468.5 | 187.4 | 219.0598 | 262.5 | 272.7 | 287.1 | 296.3 | 470.3 | 42.9 | 20.2 | 81.3 | 8.5 | 262.9 | 12.6 | 887.6 | 794.6 | 748.6 | 924.8 | 683.9 | 768.8 | 628.9 | 707.6 | 771.7 | 690.4 | 564.3 | 674.1 | 810.3 | 223.5 | 317.4 | 321.6 | 293.1 | 223.1 | 304.1 | 309.9 | 267.9
822.2 | 546.2 | 468.8 | 187.52 | 219.2001 | 262.7 | 271.4 | 287.4 | 296.3 | 471.2 | 42.9 | 20.2 | 81.4 | 9.4 | 246.4 | 12.6 | 887.2 | 799.7 | 742.6 | 925.2 | 683.3 | 768.7 | 628.5 | 707.6 | 770.9 | 690.3 | 565.8 | 672.6 | 809.3 | 223.9 | 317.5 | 321.4 | 293.3 | 223.4 | 304.8 | 310 | 268.4
823.2 | 547.2 | 469.7 | 187.88 | 219.6209 | 264.1 | 270.2 | 287.6 | 296.8 | 473.1 | 42.9 | 20.2 | 81.5 | 8.2 | 259 | 11.8 | 885.8 | 798.9 | 738.8 | 925.5 | 681.4 | 768.4 | 630.7 | 698.4 | 770.1 | 689 | 567.4 | 666.3 | 807.6 | 224.3 | 317.4 | 321.2 | 293.3 | 223.6 | 305.8 | 310.6 | 268.8
824.2 | 548.2 | 469.8 | 187.92 | 219.6677 | 265.5 | 270.4 | 288 | 297.4 | 477.8 | 43 | 20.2 | 81.6 | 7.1 | 251.5 | 12 | 883.4 | 788 | 739.3 | 925.9 | 679.1 | 768.4 | 635.4 | 691.2 | 769.3 | 687.6 | 569.2 | 664.4 | 806.6 | 224.8 | 317.4 | 321.1 | 293.4 | 223.9 | 306 | 311.1 | 269.2
825.2 | 549.2 | 469.6 | 187.84 | 219.5741 | 266.6 | 271.1 | 289.1 | 298.1 | 476.1 | 43 | 20.2 | 81.7 | 6.5 | 254.2 | 12.3 | 880.9 | 768.1 | 726 | 926 | 674.5 | 768.4 | 633 | 669.7 | 767.8 | 684.2 | 570.7 | 660.7 | 806 | 225.2 | 317.4 | 321 | 293.5 | 224.2 | 307.2 | 311.8 | 269.5
826.2 | 550.2 | 469.1 | 187.64 | 219.3403 | 268 | 272.2 | 290.1 | 298.9 | 471.6 | 43.2 | 20.2 | 81.9 | 8.1 | 247.8 | 15.7 | 879.4 | 762.2 | 719 | 925.1 | 672.2 | 768.5 | 641.7 | 661.4 | 767.2 | 682.1 | 572.3 | 657.7 | 806.4 | 225.6 | 317.2 | 320.7 | 293.5 | 224.4 | 307.7 | 312.9 | 269.8
827.2 | 551.2 | 469.8 | 187.92 | 219.6677 | 268.3 | 272.3 | 290 | 300 | 467 | 43.3 | 20.2 | 82.1 | 8.8 | 271.1 | 17.4 | 877.9 | 760.4 | 718 | 923.6 | 670 | 768.2 | 637.9 | 657.5 | 765.9 | 680.6 | 573.7 | 655.4 | 807.2 | 226.1 | 317 | 320.5 | 293.6 | 224.7 | 307.9 | 314.1 | 270.1
828.2 | 552.2 | 469.9 | 187.96 | 219.7144 | 267.9 | 271.8 | 289.1 | 300.8 | 464 | 43.4 | 20.2 | 82.3 | 9.7 | 266 | 21.4 | 877 | 757.5 | 717.7 | 921.9 | 669.8 | 767.5 | 632.4 | 658.6 | 764.7 | 679.3 | 575.2 | 655.2 | 806.3 | 226.5 | 316.6 | 319.6 | 293.8 | 225 | 308.4 | 315 | 270.3
829.2 | 553.2 | 468.8 | 187.52 | 219.2001 | 267.2 | 272 | 288.4 | 301.7 | 461.4 | 43.4 | 20.2 | 82.5 | 11.1 | 271.4 | 22.3 | 875.2 | 756.4 | 712.1 | 920.5 | 667.8 | 767.1 | 629.4 | 650.6 | 763.3 | 677.9 | 576.6 | 652.6 | 806.3 | 227 | 316.1 | 318.9 | 294 | 225.3 | 309.1 | 315.2 | 270.6
830.2 | 554.2 | 470.2 | 188.08 | 219.8547 | 266.7 | 272.9 | 288.5 | 301.9 | 461.6 | 43.4 | 20.2 | 82.7 | 10.5 | 265.6 | 21.4 | 873.3 | 752.9 | 708.1 | 919.3 | 666 | 766.8 | 629.2 | 643.1 | 762 | 675.8 | 578.1 | 648.8 | 806.3 | 227.5 | 315.7 | 318.3 | 294.1 | 225.6 | 309.7 | 315.4 | 270.8
831.2 | 555.2 | 469.6 | 187.84 | 219.5741 | 266.5 | 274.3 | 288.2 | 302.3 | 458.9 | 43.4 | 20.1 | 82.8 | 8.7 | 270.4 | 20.6 | 872.2 | 767.2 | 713.1 | 918.2 | 666.4 | 766.7 | 634.2 | 656.1 | 761.2 | 676.7 | 579.5 | 647.7 | 805.2 | 227.9 | 315.4 | 318.5 | 294.1 | 225.8 | 310.2 | 315.9 | 271.2
832.2 | 556.2 | 469.3 | 187.72 | 219.4339 | 267.3 | 275 | 288.5 | 302.4 | 464.5 | 43.4 | 20.1 | 83 | 8.5 | 268.8 | 19.7 | 871.5 | 771.8 | 718.9 | 916.7 | 667.7 | 766.7 | 635.5 | 658.3 | 760.4 | 676.4 | 580.9 | 649.6 | 803.2 | 228.4 | 315.5 | 318.7 | 294.1 | 226.2 | 310.8 | 316 | 271.5
833.2 | 557.2 | 469 | 187.6 | 219.2936 | 266.2 | 275.1 | 289.3 | 302.4 | 471.6 | 43.5 | 20.1 | 83.3 | 8.7 | 266.5 | 18.1 | 871.9 | 776.4 | 731.2 | 914.4 | 670 | 766.1 | 633.8 | 674.2 | 760 | 678.2 | 582 | 652.9 | 802 | 228.8 | 315.5 | 319 | 294.2 | 226.5 | 310.8 | 316 | 271.7
834.2 | 558.2 | 469.5 | 187.8 | 219.5274 | 264.7 | 275.9 | 289.8 | 302.6 | 469.6 | 43.5 | 20.1 | 83.5 | 8.6 | 259.4 | 16.1 | 871 | 775.6 | 735 | 913 | 669.9 | 765.6 | 629.4 | 684.9 | 759.5 | 676.9 | 582.5 | 656.2 | 800.9 | 229.3 | 316.2 | 319.6 | 294.5 | 226.8 | 310.1 | 315.9 | 271.8
835.2 | 559.2 | 469.9 | 187.96 | 219.7144 | 263.5 | 276.7 | 290.6 | 302.8 | 466.2 | 43.6 | 20.1 | 83.6 | 10.4 | 264.9 | 13.9 | 870.6 | 773.9 | 747.3 | 912.3 | 671.9 | 765.8 | 628 | 685.6 | 758.7 | 675.3 | 583.5 | 657.9 | 798.8 | 229.8 | 316.8 | 320.5 | 295 | 227.1 | 309.8 | 315.9 | 272
836.2 | 560.2 | 469.8 | 187.92 | 219.6677 | 263.6 | 277.5 | 291 | 303 | 471.4 | 43.7 | 20.1 | 83.7 | 9.3 | 265.9 | 14.3 | 871.3 | 768.6 | 762.4 | 911.4 | 674.3 | 766.2 | 632.9 | 692.5 | 758.8 | 674.3 | 584.6 | 666.7 | 796.6 | 230.3 | 317.1 | 321.1 | 295.4 | 227.5 | 310.1 | 316.6 | 272.1
837.2 | 561.2 | 469.9 | 187.96 | 219.7144 | 263.7 | 277.6 | 291 | 303.7 | 481.4 | 43.8 | 20.1 | 83.8 | 7 | 266.7 | 17.2 | 871.8 | 761.3 | 775.9 | 910.5 | 677.3 | 767.2 | 648 | 706.1 | 758.8 | 674.7 | 585.7 | 679.8 | 794.2 | 230.8 | 317.2 | 321.5 | 295.7 | 227.8 | 309.9 | 316.4 | 272.5
838.2 | 562.2 | 470.3 | 188.12 | 219.9014 | 263.8 | 278.2 | 291.1 | 304 | 484.9 | 43.9 | 20.1 | 83.9 | 7.7 | 268.6 | 20.6 | 873.7 | 775.6 | 780.2 | 909.6 | 679.1 | 767.1 | 648.9 | 728.5 | 758.9 | 677.8 | 586.7 | 685.9 | 792.9 | 231.2 | 317.7 | 322.1 | 295.7 | 228.1 | 309.6 | 316.3 | 272.6
839.2 | 563.2 | 469.6 | 187.84 | 219.5741 | 263.8 | 279.6 | 291.1 | 304.3 | 483 | 44 | 20.1 | 84 | 8.6 | 270.6 | 21.5 | 874.9 | 791.4 | 776.1 | 909.6 | 679.1 | 766 | 646.9 | 748.5 | 759.3 | 679.8 | 587.3 | 685.8 | 794.4 | 231.7 | 318 | 322.6 | 295.8 | 228.4 | 309.9 | 316.7 | 272.8
840.2 | 564.2 | 470.5 | 188.2 | 219.995 | 263.8 | 280.8 | 292.1 | 304.7 | 483.5 | 44.1 | 20.1 | 84 | 8.8 | 271.8 | 21.3 | 874.9 | 787.4 | 768.2 | 909.4 | 678.2 | 765.6 | 644 | 755.6 | 759.2 | 679.7 | 588.4 | 687.1 | 795.1 | 232.1 | 318.9 | 323.1 | 296.2 | 228.7 | 309.6 | 316.9 | 273
841.2 | 565.2 | 470.5 | 188.2 | 219.995 | 264.3 | 280.3 | 292.7 | 304.6 | 486.3 | 44.2 | 20.1 | 84 | 8.1 | 277.5 | 21.1 | 875.4 | 796.1 | 771.4 | 909.5 | 678.6 | 765.8 | 643.3 | 763.9 | 759.5 | 680.2 | 589.5 | 690.4 | 795.9 | 232.5 | 319.7 | 323.6 | 296.7 | 228.9 | 309.2 | 317.1 | 273.1
842.2 | 566.2 | 470.7 | 188.28 | 220.0885 | 263.5 | 281.4 | 293.3 | 305.1 | 486.1 | 44.3 | 20.1 | 83.9 | 6.1 | 277.7 | 20.2 | 876.4 | 806 | 773.5 | 909.5 | 681.8 | 766 | 643.3 | 769.6 | 759.6 | 682.9 | 590.2 | 688.6 | 796.1 | 233 | 319.9 | 324.1 | 296.8 | 229.2 | 309 | 317.2 | 273.4
843.2 | 567.2 | 470 | 188 | 219.7612 | 263 | 282.7 | 294 | 305.1 | 484.7 | 44.4 | 20.1 | 83.8 | 5.8 | 275.2 | 19.9 | 876.2 | 806.7 | 770.9 | 909.9 | 681.4 | 766 | 638.9 | 762.7 | 759.2 | 682.6 | 590.7 | 687 | 796.4 | 233.5 | 320.1 | 324.9 | 296.9 | 229.5 | 308.8 | 317 | 273.5
844.2 | 568.2 | 470.1 | 188.04 | 219.8079 | 262.1 | 283.7 | 293.9 | 304.2 | 480.5 | 44.4 | 20.1 | 83.6 | 5.4 | 272.5 | 18.8 | 875.4 | 800.3 | 770.1 | 910.8 | 681.3 | 766.2 | 637.8 | 759.4 | 759.2 | 682.2 | 591.3 | 688.9 | 797.3 | 234 | 320.3 | 325.6 | 297.1 | 229.8 | 308.4 | 316.9 | 273.6
845.2 | 569.2 | 470.3 | 188.12 | 219.9014 | 261.3 | 285.3 | 293.2 | 303.6 | 482.2 | 44.4 | 20.1 | 83.5 | 5.5 | 272.8 | 17.2 | 875 | 790.6 | 771 | 911.6 | 680.7 | 766.8 | 645.1 | 757.7 | 759.2 | 681.2 | 591.9 | 694.5 | 796.4 | 234.4 | 321.2 | 326.2 | 297.5 | 230 | 308.2 | 317.2 | 273.7
846.2 | 570.2 | 470.1 | 188.04 | 219.8079 | 261.4 | 286.8 | 293.3 | 303.6 | 489.3 | 44.4 | 20.1 | 83.3 | 4.7 | 276.1 | 16.3 | 876.9 | 794.6 | 777.8 | 911.4 | 682.3 | 767 | 643.6 | 774.1 | 759.4 | 682.9 | 592.5 | 701.5 | 794.9 | 235 | 322 | 326.6 | 297.8 | 230.3 | 308.1 | 317 | 273.9
847.2 | 571.2 | 470.1 | 188.04 | 219.8079 | 262.1 | 287.9 | 294.5 | 303.9 | 492 | 44.4 | 20.1 | 83.1 | 4.3 | 277.8 | 15.1 | 879 | 795.8 | 776.9 | 911 | 683.9 | 766.7 | 642.7 | 787.8 | 759.6 | 684.8 | 593 | 705.5 | 796.2 | 235.5 | 322.2 | 326.9 | 298 | 230.5 | 307.7 | 317.1 | 274
848.2 | 572.2 | 470.1 | 188.04 | 219.8079 | 262.2 | 289.1 | 294.6 | 304.3 | 493.7 | 44.3 | 20.1 | 83 | 4 | 278.1 | 14.1 | 878.4 | 784.3 | 771.8 | 910.9 | 681.9 | 766.7 | 640.6 | 783.4 | 759.5 | 683.8 | 593.4 | 709.1 | 794.6 | 236 | 322.5 | 327.9 | 298.2 | 230.8 | 307.4 | 317.4 | 274.1
849.2 | 573.2 | 469.7 | 187.88 | 219.6209 | 262.5 | 288.5 | 295.4 | 304.7 | 501.5 | 44.3 | 20.1 | 82.9 | 4.8 | 281.1 | 13.6 | 876.7 | 774.1 | 768.8 | 911.5 | 680.9 | 767.1 | 644.8 | 767.2 | 759.3 | 681.6 | 594.3 | 709.8 | 792 | 236.5 | 323.2 | 328.9 | 298.9 | 231.1 | 307.3 | 318 | 274.3
850.2 | 574.2 | 469.8 | 187.92 | 219.6677 | 264.4 | 289.4 | 297.5 | 305.7 | 502.8 | 44.3 | 20.1 | 82.9 | 5.2 | 287.6 | 12.7 | 876.4 | 770.2 | 767.4 | 911.9 | 681.3 | 767.4 | 656.9 | 753 | 759 | 680.6 | 595.2 | 708.7 | 788.7 | 237 | 323.6 | 329.6 | 299.1 | 231.3 | 307.7 | 318.4 | 274.5
851.2 | 575.2 | 470.1 | 188.04 | 219.8079 | 265.9 | 289.9 | 299.7 | 307.2 | 500.5 | 44.3 | 20.1 | 83 | 5.9 | 286.1 | 12.1 | 875.7 | 768.9 | 763.7 | 912.6 | 680.6 | 767.1 | 658 | 739.1 | 758.4 | 679.2 | 596 | 703.3 | 786.6 | 237.5 | 323.7 | 330.5 | 299.3 | 231.6 | 308.2 | 319 | 274.7
852.2 | 576.2 | 469 | 187.6 | 219.2936 | 266.9 | 290.5 | 301.3 | 308.5 | 495.4 | 44.3 | 20.1 | 83.1 | 5.7 | 282.6 | 12.1 | 876.7 | 773.6 | 773.3 | 913.5 | 684.6 | 766.4 | 654.9 | 740.7 | 757.9 | 679.1 | 596.8 | 705.9 | 785.7 | 237.9 | 324.1 | 331.5 | 299.6 | 231.8 | 308.9 | 319.8 | 275
853.2 | 577.2 | 471.8 | 188.72 | 220.6028 | 267.8 | 291.8 | 302.7 | 309.3 | 497.6 | 44.4 | 20.1 | 83.1 | 5.9 | 280.4 | 11.7 | 875.6 | 775.2 | 766 | 914.9 | 682.3 | 765.2 | 650.9 | 734.9 | 757.5 | 678.7 | 597.3 | 703.1 | 784.3 | 238.3 | 324.4 | 332.1 | 299.8 | 232.1 | 309.5 | 320.1 | 275.2
854.2 | 578.2 | 473.7 | 189.48 | 221.4912 | 268.8 | 291.9 | 304 | 309.7 | 495.9 | 44.5 | 20.1 | 83.2 | 5.1 | 280.6 | 11.6 | 875.7 | 781.3 | 763.5 | 915.6 | 683 | 763.8 | 648.8 | 741.4 | 757.2 | 679.1 | 598 | 701 | 783.4 | 238.8 | 324.4 | 332.3 | 299.9 | 232.4 | 310.2 | 320.5 | 275.5
855.2 | 579.2 | 472.4 | 188.96 | 220.8834 | 269.3 | 292.2 | 303.8 | 309.9 | 491.7 | 44.6 | 20.1 | 83.1 | 4.9 | 279.2 | 11.4 | 876 | 796.8 | 759.2 | 916.1 | 684.4 | 761.9 | 649.3 | 755.6 | 757.3 | 683.9 | 598.7 | 697.1 | 781.9 | 239.3 | 324.2 | 332.6 | 299.9 | 232.7 | 311 | 320.5 | 275.8
856.2 | 580.2 | 471.8 | 188.72 | 220.6028 | 268.4 | 291.5 | 303.6 | 309.8 | 491.8 | 44.7 | 20.1 | 83.2 | 4.9 | 280.1 | 12.3 | 875.8 | 801.6 | 748.6 | 916.9 | 682.2 | 759.1 | 650 | 749.4 | 756.9 | 686.8 | 599.2 | 688.2 | 780.1 | 239.7 | 324.1 | 332.6 | 299.6 | 233 | 311.7 | 320.9 | 276.2
857.2 | 581.2 | 471.7 | 188.68 | 220.556 | 269.3 | 290.9 | 304.1 | 309.4 | 497 | 44.7 | 20.1 | 83.4 | 5.4 | 283.7 | 12.7 | 875.5 | 811.5 | 750 | 917.5 | 683.6 | 757 | 651.9 | 739.7 | 757.4 | 686.8 | 600.3 | 681.8 | 777.5 | 240.1 | 324.2 | 332.9 | 299.4 | 233.3 | 313.1 | 321.4 | 276.6
858.2 | 582.2 | 471.4 | 188.56 | 220.4158 | 269.4 | 290.2 | 305 | 309.2 | 500.6 | 44.7 | 20.1 | 83.5 | 5.1 | 279.2 | 12.7 | 876.2 | 820.7 | 755.7 | 917.3 | 688.7 | 755.5 | 653.9 | 749.1 | 758.4 | 689.4 | 601.1 | 678.6 | 775.3 | 240.5 | 324.3 | 333.2 | 299.5 | 233.6 | 314.1 | 321.8 | 276.9
859.2 | 583.2 | 469.7 | 187.88 | 219.6209 | 268.9 | 289.5 | 306.4 | 309.3 | 498.8 | 44.7 | 20.1 | 83.5 | 4.8 | 286.4 | 14.5 | 876.1 | 827.4 | 756.3 | 917 | 690.4 | 754.3 | 656.1 | 756.9 | 759.3 | 692.6 | 601.4 | 676.2 | 773.6 | 240.9 | 324.6 | 333.4 | 299.6 | 233.9 | 315.4 | 322.2 | 277.4
860.2 | 584.2 | 470 | 188 | 219.7612 | 268.4 | 288.8 | 307 | 309.3 | 500.8 | 44.7 | 20 | 83.4 | 5.1 | 289.1 | 17.9 | 874.4 | 828.2 | 748.5 | 917.2 | 690.4 | 753.2 | 658.5 | 744.8 | 761.1 | 693.9 | 602.1 | 670.5 | 771 | 241.3 | 324.6 | 333.4 | 299.7 | 234.2 | 316.6 | 323 | 277.8
861.2 | 585.2 | 469.8 | 187.92 | 219.6677 | 268.5 | 289.4 | 308.4 | 309.3 | 507.8 | 44.7 | 20 | 83.4 | 5.8 | 295.8 | 17.8 | 873.8 | 829.6 | 750.3 | 917.4 | 693.6 | 752.5 | 660.5 | 739.2 | 762.4 | 696.1 | 603.2 | 667.4 | 767.8 | 241.7 | 324.6 | 333.5 | 299.8 | 234.5 | 317.2 | 323.8 | 278.3
862.2 | 586.2 | 469.8 | 187.92 | 219.6677 | 268.8 | 291.5 | 309.2 | 309.6 | 507.6 | 44.7 | 20 | 83.5 | 5.9 | 292.9 | 17.4 | 873.7 | 826.8 | 763.6 | 917.4 | 698.6 | 752.1 | 661.6 | 737.5 | 761.9 | 696.6 | 603.8 | 671.2 | 764.3 | 242 | 324.6 | 333.9 | 299.9 | 234.8 | 317.9 | 324.2 | 278.6
863.2 | 587.2 | 470.5 | 188.2 | 219.995 | 269.5 | 293.2 | 310.4 | 310.3 | 504.5 | 44.7 | 20 | 83.5 | 6.1 | 286.1 | 19.3 | 874.2 | 822.2 | 774.9 | 917.4 | 702.2 | 752.3 | 670.9 | 738.6 | 760.4 | 696.3 | 604.3 | 679.2 | 760.9 | 242.4 | 324.8 | 334.1 | 300.4 | 235.1 | 318.2 | 324.4 | 278.8
864.2 | 588.2 | 471.2 | 188.48 | 220.3223 | 269.6 | 293.3 | 311 | 310.3 | 506.8 | 44.8 | 20 | 83.5 | 5.4 | 295.8 | 18.5 | 873.1 | 801.8 | 777.4 | 917.3 | 700.6 | 752.6 | 678 | 720.4 | 758.1 | 692.7 | 605.2 | 687.1 | 757.4 | 242.8 | 325.7 | 334.6 | 301.5 | 235.4 | 318.2 | 324.5 | 279
865.2 | 589.2 | 469.9 | 187.96 | 219.7144 | 268.8 | 293.3 | 311.4 | 310.1 | 507.5 | 44.9 | 20 | 83.6 | 4.4 | 281.6 | 18.2 | 873.2 | 795.2 | 779.5 | 917.3 | 701.7 | 752.8 | 684.4 | 723.1 | 756.2 | 692.4 | 606.4 | 695.5 | 755.8 | 243.2 | 326.3 | 334.9 | 302 | 235.7 | 318.3 | 324.6 | 279.2
866.2 | 590.2 | 470.6 | 188.24 | 220.0417 | 269.2 | 293.8 | 312.1 | 309.8 | 508.5 | 44.9 | 20 | 83.6 | 3.7 | 276.3 | 17.9 | 873.1 | 790.1 | 774.6 | 917.3 | 700.7 | 753 | 683.7 | 721.8 | 755.7 | 691.5 | 607.3 | 699.2 | 755.1 | 243.6 | 326.6 | 335.3 | 302.3 | 236 | 318.3 | 325 | 279.4
867.2 | 591.2 | 470.6 | 188.24 | 220.0417 | 269.8 | 293.7 | 312.3 | 310.6 | 503.7 | 44.9 | 20 | 83.5 | 2.8 | 271.4 | 15.4 | 871 | 775.4 | 767 | 917 | 696.7 | 753.2 | 689.5 | 706.6 | 754.3 | 688.6 | 608.5 | 695.4 | 754.6 | 244 | 327.1 | 336 | 302.4 | 236.3 | 318.4 | 325.2 | 279.6
868.2 | 592.2 | 470.4 | 188.16 | 219.9482 | 270.7 | 293.8 | 312.6 | 312.1 | 499.5 | 45 | 20 | 83.5 | 3.3 | 283.2 | 14.2 | 870.1 | 762.1 | 758.3 | 916.3 | 693.5 | 753.2 | 688.9 | 702.9 | 752 | 685.5 | 609.6 | 693.6 | 755.7 | 244.3 | 327.9 | 336.4 | 302.8 | 236.6 | 318.3 | 325.8 | 279.8
869.2 | 593.2 | 467.7 | 187.08 | 218.6857 | 272.7 | 294.5 | 313 | 312.9 | 496.8 | 45 | 20 | 83.5 | 3.2 | 288.6 | 12.9 | 868.3 | 753.6 | 746.1 | 915.2 | 689.1 | 752.7 | 690.6 | 687.7 | 749.8 | 682.8 | 610.6 | 687.3 | 759.1 | 244.6 | 328.2 | 336.7 | 303 | 236.9 | 318 | 326.3 | 280
870.2 | 594.2 | 467.8 | 187.12 | 218.7325 | 273.1 | 294.3 | 312.5 | 313.9 | 493.6 | 45 | 20 | 83.5 | 2.6 | 290.7 | 13.7 | 865.9 | 741.8 | 733.7 | 914.1 | 684.2 | 752.7 | 696.7 | 668.6 | 748.1 | 679.7 | 611.7 | 681.9 | 763.7 | 244.9 | 328.4 | 336.7 | 303.1 | 237.2 | 318.4 | 327.5 | 280.2
871.2 | 595.2 | 468.7 | 187.48 | 219.1533 | 273.5 | 294.3 | 311.2 | 314.8 | 495.3 | 45.1 | 20 | 83.5 | 3.4 | 292 | 13.9 | 863.8 | 734.8 | 724.4 | 912.7 | 681.4 | 752.9 | 702.8 | 658.8 | 746.4 | 676.9 | 612.8 | 678 | 770.5 | 245.2 | 328.2 | 336.8 | 303.3 | 237.5 | 318.6 | 328 | 280.5
872.2 | 596.2 | 468 | 187.2 | 218.826 | 273.6 | 295 | 310.3 | 315.5 | 495.8 | 45.1 | 20 | 83.6 | 3.9 | 293 | 14.3 | 861.9 | 736.4 | 718.6 | 911.2 | 679.8 | 752.5 | 700.6 | 657.8 | 744.5 | 675.6 | 613.9 | 674 | 774.7 | 245.6 | 327.9 | 336.3 | 303.2 | 237.8 | 318.3 | 328.3 | 280.8
873.2 | 597.2 | 468.5 | 187.4 | 219.0598 | 272.5 | 296.2 | 309.9 | 315.8 | 494.2 | 45.2 | 20 | 83.8 | 4.1 | 295.4 | 15.2 | 858.5 | 724.4 | 709.9 | 910.1 | 674.9 | 751.9 | 703.3 | 642 | 742.9 | 672.5 | 614.7 | 668.4 | 777.4 | 246 | 327.3 | 335.7 | 303.1 | 238.1 | 317.9 | 328.8 | 280.9
874.2 | 598.2 | 468.5 | 187.4 | 219.0598 | 272.5 | 295.8 | 309.2 | 315.4 | 487.7 | 45.2 | 20 | 84 | 4.8 | 282.2 | 17.1 | 857.3 | 721.5 | 701.8 | 909 | 672 | 751.4 | 704.5 | 635.3 | 741 | 670.2 | 615.6 | 664.4 | 780.9 | 246.4 | 326.5 | 334.9 | 303 | 238.4 | 317.8 | 329.2 | 281.2
875.2 | 599.2 | 469.2 | 187.68 | 219.3871 | 272.2 | 295.7 | 308.2 | 315 | 479.9 | 45.3 | 20 | 84.3 | 5.8 | 273 | 18.8 | 855.6 | 733.1 | 695.8 | 907.4 | 669.2 | 750.8 | 699.3 | 636.6 | 740.1 | 668.7 | 616.5 | 659.9 | 783.1 | 246.8 | 325.8 | 334.9 | 302.9 | 238.7 | 317.5 | 328.8 | 281.4
876.2 | 600.2 | 468.7 | 187.48 | 219.1533 | 272.2 | 296.3 | 307.1 | 314.4 | 478.9 | 45.3 | 20 | 84.6 | 5.2 | 275.7 | 17.2 | 852.6 | 727.4 | 691 | 906.1 | 666.4 | 750.5 | 694.8 | 631.8 | 739.4 | 666.5 | 617.9 | 656.3 | 784.3 | 247.1 | 325.2 | 334.6 | 302.9 | 239 | 317.2 | 328.5 | 281.7
877.2 | 601.2 | 469.7 | 187.88 | 219.6209 | 272.7 | 294.6 | 306.1 | 313.1 | 476.2 | 45.4 | 20 | 84.8 | 4.4 | 277.6 | 16.9 | 850 | 725.4 | 689.3 | 904.7 | 664 | 750.2 | 697.7 | 626.1 | 738.4 | 664.6 | 619 | 652.6 | 786.2 | 247.4 | 324.7 | 333.9 | 303 | 239.4 | 316.7 | 328.1 | 281.8
878.2 | 602.2 | 469.3 | 187.72 | 219.4339 | 273.5 | 293.5 | 305.2 | 312.3 | 476.9 | 45.4 | 20 | 85.1 | 5.4 | 273.5 | 15.5 | 846.8 | 720.4 | 683.5 | 902.9 | 661.2 | 749.6 | 693.4 | 622.3 | 738.3 | 663.2 | 620.2 | 648 | 789.4 | 247.7 | 324.2 | 333.2 | 303 | 239.7 | 316.4 | 327.8 | 282
879.2 | 603.2 | 469 | 187.6 | 219.2936 | 273.1 | 292.3 | 304.5 | 311.5 | 474.3 | 45.5 | 20 | 85.1 | 4.4 | 289.1 | 13.6 | 844.7 | 715.5 | 678.7 | 901 | 658.1 | 749.4 | 698.2 | 610.1 | 736.7 | 660.4 | 621.3 | 643.4 | 790.8 | 248 | 323.8 | 332.4 | 303 | 240.1 | 316.2 | 327.6 | 282.2
880.2 | 604.2 | 469.2 | 187.68 | 219.3871 | 274.3 | 291 | 303.5 | 311 | 469.3 | 45.5 | 20 | 85.1 | 4.2 | 310.4 | 12.2 | 842 | 713 | 677.3 | 899.5 | 655.6 | 749.2 | 702.4 | 604.1 | 735.1 | 658.8 | 622.1 | 639.7 | 793.2 | 248.3 | 323.5 | 331.7 | 303 | 240.4 | 315.8 | 328 | 282.4
881.2 | 605.2 | 469.5 | 187.8 | 219.5274 | 275.1 | 289.4 | 302.8 | 310.7 | 467.1 | 45.6 | 20 | 85.1 | 4.7 | 294.3 | 11.7 | 839.8 | 714.5 | 673.4 | 897.9 | 652.2 | 748.6 | 700.6 | 599.1 | 734.6 | 657.5 | 622.8 | 636.4 | 794.6 | 248.5 | 323.4 | 331.1 | 303.1 | 240.6 | 315.6 | 327.7 | 282.6
882.2 | 606.2 | 468.9 | 187.56 | 219.2468 | 276.2 | 288.5 | 301.9 | 310.3 | 464.8 | 45.7 | 20 | 85.3 | 5.9 | 290 | 13.4 | 838.8 | 733 | 679.1 | 896 | 652.6 | 748 | 697 | 618.2 | 734.8 | 658.5 | 623.7 | 636.1 | 793.9 | 248.8 | 323 | 330.6 | 303.2 | 240.9 | 315.5 | 327.5 | 282.8
883.2 | 607.2 | 469.7 | 187.88 | 219.6209 | 275.6 | 287.4 | 300.9 | 310.1 | 464.4 | 45.8 | 20 | 85.6 | 5.5 | 274.9 | 14.3 | 838.5 | 743.3 | 682.8 | 894 | 652.3 | 747.6 | 689.6 | 631.4 | 734.6 | 657.7 | 624.4 | 636.7 | 792.2 | 249.1 | 322.7 | 330.2 | 303.2 | 241.1 | 315.7 | 327 | 283
884.2 | 608.2 | 469.7 | 187.88 | 219.6209 | 275.1 | 286.7 | 300.1 | 309.5 | 465.8 | 45.9 | 20 | 85.8 | 5.2 | 279.2 | 12.5 | 838 | 750.1 | 688.5 | 892.1 | 653.3 | 747 | 684.9 | 639.7 | 734.9 | 658.6 | 625.1 | 634.5 | 789.9 | 249.3 | 322.9 | 330 | 303.3 | 241.4 | 316 | 326.6 | 283.2
885.2 | 609.2 | 469.9 | 187.96 | 219.7144 | 274.7 | 286.5 | 299.8 | 308.8 | 468 | 46 | 20 | 85.9 | 4.9 | 267.2 | 11.8 | 836.7 | 747.1 | 690.9 | 890 | 651.8 | 746.8 | 681.4 | 641.4 | 734.4 | 657.9 | 625.7 | 633.2 | 788.5 | 249.6 | 322.8 | 329.9 | 303.4 | 241.7 | 316.2 | 326.3 | 283.4
886.2 | 610.2 | 470.3 | 188.12 | 219.9014 | 274.5 | 285.8 | 300.1 | 308.8 | 463 | 46 | 20 | 86.1 | 5.5 | 278 | 10.9 | 832.8 | 732.5 | 684.2 | 887.8 | 648.4 | 746.8 | 691 | 626.5 | 732.1 | 654.7 | 626.2 | 630.3 | 787.6 | 249.9 | 322.8 | 330 | 303.5 | 242 | 316.2 | 326.1 | 283.6
887.2 | 611.2 | 469.5 | 187.8 | 219.5274 | 275.8 | 284.9 | 300 | 309.4 | 464.2 | 46 | 20 | 86.3 | 6.2 | 286.6 | 11.5 | 830.5 | 726.2 | 685.9 | 885.8 | 648.1 | 746.6 | 696.4 | 620.4 | 730.2 | 653.3 | 626.9 | 628.5 | 787.6 | 250.1 | 322.8 | 329.7 | 303.7 | 242.3 | 316.8 | 326.7 | 283.9
888.2 | 612.2 | 468.6 | 187.44 | 219.1066 | 277.5 | 285.2 | 299.3 | 309.8 | 465.4 | 46.1 | 20 | 86.4 | 4.7 | 274.7 | 11.5 | 828.3 | 718 | 680.6 | 883.8 | 645.7 | 746.3 | 700.5 | 613.8 | 728.1 | 651.5 | 627.5 | 627 | 785.7 | 250.4 | 322.9 | 329.5 | 303.7 | 242.5 | 317.3 | 326.6 | 284.2
889.2 | 613.2 | 469.9 | 187.96 | 219.7144 | 278.2 | 285.3 | 299.4 | 309.8 | 461.9 | 46.1 | 20 | 86.4 | 5.3 | 294.4 | 10.2 | 827 | 708.9 | 685.1 | 881.9 | 644.6 | 746.1 | 710 | 609.9 | 726.8 | 649.4 | 628.4 | 627.2 | 783.6 | 250.7 | 323.3 | 329.6 | 303.9 | 242.8 | 317.5 | 326.3 | 284.5
890.2 | 614.2 | 469.6 | 187.84 | 219.5741 | 277.3 | 285 | 299.7 | 309.4 | 463.7 | 46.2 | 20 | 86.5 | 5.5 | 294.7 | 9.4 | 824.6 | 708.5 | 685.4 | 879.9 | 642.1 | 745.8 | 711.2 | 613.8 | 725.4 | 648.5 | 629.2 | 626.6 | 783.4 | 250.9 | 323.6 | 329.5 | 304.2 | 243 | 317.2 | 326.2 | 284.7
891.2 | 615.2 | 468.7 | 187.48 | 219.1533 | 277.1 | 285.5 | 298.9 | 309.1 | 465.6 | 46.2 | 20 | 86.6 | 5.3 | 261.8 | 9.6 | 824.8 | 723.2 | 688.6 | 878.3 | 641.5 | 744.9 | 701.8 | 621.1 | 724.7 | 648.3 | 629.9 | 626.1 | 784 | 251.2 | 323.8 | 329.6 | 304.4 | 243.3 | 316.8 | 326.2 | 284.9
892.2 | 616.2 | 467.5 | 187 | 218.5922 | 277.9 | 287.2 | 298.2 | 309 | 465 | 46.3 | 20 | 86.8 | 5.9 | 275 | 10 | 825.1 | 733.7 | 698.4 | 877.2 | 642.2 | 744 | 694.3 | 636.5 | 725.4 | 649.2 | 630.5 | 628 | 784.6 | 251.5 | 323.8 | 329.5 | 304.6 | 243.5 | 316.4 | 325.8 | 285.1
893.2 | 617.2 | 469.1 | 187.64 | 219.3403 | 278.9 | 287.9 | 297.4 | 309.1 | 466.2 | 46.3 | 20 | 87 | 6.1 | 268.3 | 11.5 | 824.6 | 736.1 | 704.8 | 875.7 | 642.8 | 743.4 | 682.5 | 644.3 | 725.4 | 649.1 | 630.8 | 628.9 | 785.8 | 251.7 | 323.8 | 329.4 | 304.6 | 243.7 | 316.3 | 325.4 | 285.2
894.2 | 618.2 | 469.4 | 187.76 | 219.4806 | 280.2 | 288.1 | 297.7 | 309.2 | 468 | 46.3 | 20 | 87.1 | 5.3 | 261.5 | 13.2 | 824.1 | 734.1 | 705.6 | 874.4 | 642.9 | 742.6 | 672.8 | 651.2 | 725.3 | 648.7 | 631 | 628.6 | 785.3 | 252 | 324.2 | 329.4 | 304.9 | 244 | 316.5 | 325.2 | 285.2
895.2 | 619.2 | 467.5 | 187 | 218.5922 | 281.8 | 288.1 | 298.7 | 309 | 467.6 | 46.4 | 20 | 87.2 | 6.4 | 261 | 13.9 | 822.4 | 726.3 | 702.8 | 873 | 641.4 | 742 | 676 | 643.1 | 723.3 | 647.2 | 631.4 | 627.9 | 783.3 | 252.4 | 324.2 | 329.6 | 305.2 | 244.2 | 316.4 | 325.1 | 285.4
896.2 | 620.2 | 468 | 187.2 | 218.826 | 283.3 | 288.4 | 299.2 | 309.1 | 470.8 | 46.4 | 20 | 87.4 | 7.6 | 262.6 | 14.2 | 820.6 | 713.2 | 700.3 | 871.2 | 639.3 | 741.7 | 685.9 | 635.7 | 721.2 | 645.6 | 631.8 | 629.8 | 783 | 252.6 | 324.5 | 330.2 | 305.5 | 244.5 | 316.3 | 325.2 | 285.5
897.2 | 621.2 | 468.8 | 187.52 | 219.2001 | 284.7 | 289 | 299 | 309.6 | 477.1 | 46.4 | 19.9 | 87.5 | 7.9 | 262.4 | 14.6 | 818.4 | 703.2 | 701 | 869.4 | 638.2 | 741.5 | 690.5 | 624.5 | 718.5 | 643.6 | 632.3 | 630 | 781.4 | 252.9 | 325.5 | 330.6 | 306 | 244.7 | 316 | 325.3 | 285.6
898.2 | 622.2 | 468.9 | 187.56 | 219.2468 | 285.6 | 290 | 298.2 | 310.3 | 475.7 | 46.4 | 19.9 | 87.6 | 5.3 | 248.8 | 14.4 | 817.4 | 700.3 | 706.5 | 867.8 | 638.3 | 741 | 691.9 | 620.6 | 714.6 | 642.5 | 632.9 | 632.6 | 780.4 | 253.2 | 327.1 | 331.4 | 306.9 | 244.9 | 316 | 325.3 | 285.7
899.2 | 623.2 | 468.8 | 187.52 | 219.2001 | 285.9 | 290.6 | 297.4 | 310.8 | 476.8 | 46.4 | 19.9 | 87.5 | 4.8 | 254.5 | 12.9 | 816.9 | 699.3 | 705.7 | 866.3 | 637.7 | 740.5 | 688.4 | 631.2 | 713.7 | 641.8 | 633.3 | 635.9 | 781.4 | 253.5 | 327.2 | 331.5 | 307.1 | 245.2 | 316.1 | 325.8 | 285.8
900.2 | 624.2 | 469.1 | 187.64 | 219.3403 | 283.5 | 290.2 | 297.4 | 311.2 | 480.2 | 46.4 | 19.9 | 87.5 | 7 | 257.4 | 12.8 | 817.1 | 695.6 | 706.2 | 865 | 636.8 | 739.9 | 690.3 | 632.8 | 713.2 | 640.7 | 633.8 | 638 | 782.8 | 253.7 | 326.8 | 331.2 | 307.1 | 245.4 | 316.4 | 326.2 | 286
901.2 | 625.2 | 468.8 | 187.52 | 219.2001 | 283.5 | 290.5 | 297.6 | 311.2 | 483.3 | 46.5 | 19.9 | 87.6 | 6.1 | 260.7 | 14.5 | 817.1 | 693.3 | 712.1 | 864.1 | 636.6 | 739.8 | 693.2 | 639 | 712.9 | 639.9 | 634.3 | 642.4 | 782.6 | 254 | 326.9 | 331.2 | 307.1 | 245.6 | 316.5 | 326.9 | 286.2
902.2 | 626.2 | 469.5 | 187.8 | 219.5274 | 282.7 | 291.4 | 297.5 | 311.3 | 493 | 46.5 | 19.9 | 87.7 | 5.5 | 262.2 | 16.4 | 815.6 | 683.2 | 712.7 | 862.5 | 634.7 | 739.9 | 694.2 | 628.4 | 709.2 | 637.8 | 634.8 | 645.5 | 778.7 | 254.3 | 327.2 | 331.4 | 307.4 | 245.9 | 316.2 | 327 | 286.3
903.2 | 627.2 | 469.6 | 187.84 | 219.5741 | 281.4 | 291.4 | 297.4 | 312.2 | 502.3 | 46.5 | 19.9 | 87.9 | 5.2 | 264.7 | 16.9 | 814.5 | 674.4 | 716 | 860.5 | 634.1 | 740.4 | 692.7 | 627.4 | 706.7 | 636.2 | 635.4 | 651 | 773.9 | 254.7 | 327.8 | 332.3 | 307.7 | 246.1 | 316.3 | 327.4 | 286.4
904.2 | 628.2 | 468.5 | 187.4 | 219.0598 | 280.8 | 291.4 | 299.9 | 313.2 | 507.2 | 46.4 | 19.9 | 88 | 5.8 | 270.4 | 15.5 | 815 | 680 | 713.4 | 859 | 633.9 | 740.4 | 686.4 | 634.9 | 705.9 | 635.8 | 636.1 | 652.9 | 771 | 255 | 328.5 | 333.3 | 308 | 246.3 | 316.1 | 327.7 | 286.6
905.2 | 629.2 | 468.8 | 187.52 | 219.2001 | 281.9 | 292.7 | 302.2 | 314.2 | 505 | 46.4 | 19.9 | 88 | 6.3 | 275.2 | 13.5 | 814.3 | 692.4 | 713.9 | 857.9 | 634.4 | 740.3 | 682.6 | 646.4 | 706.2 | 636.4 | 636.5 | 653.3 | 770.4 | 255.3 | 329.3 | 334.3 | 308.1 | 246.6 | 315.9 | 328.3 | 286.8
906.2 | 630.2 | 468 | 187.2 | 218.826 | 283.3 | 293.4 | 304.1 | 314.7 | 504.8 | 46.3 | 19.9 | 88.2 | 6.8 | 267 | 12.3 | 813.9 | 690.8 | 715.1 | 857.1 | 634 | 740.2 | 672.9 | 650.8 | 706 | 635.8 | 636.6 | 654.6 | 769.1 | 255.6 | 330.3 | 335.2 | 308.5 | 246.9 | 315.9 | 329.9 | 287.1
907.2 | 631.2 | 467.6 | 187.04 | 218.639 | 284.5 | 295.2 | 305.3 | 316.2 | 501.7 | 46.2 | 19.9 | 88.4 | 6.7 | 257.6 | 12.7 | 812.5 | 692.5 | 708.6 | 855.8 | 631.1 | 740 | 673.7 | 639.6 | 704 | 634.3 | 636.7 | 650.6 | 767.6 | 255.8 | 330.9 | 335.8 | 308.6 | 247.1 | 316.4 | 332.6 | 287.4
908.2 | 632.2 | 469.4 | 187.76 | 219.4806 | 286 | 296.2 | 306.7 | 318.2 | 498.1 | 46.1 | 19.9 | 88.4 | 6.7 | 273 | 13.9 | 811.7 | 695.9 | 705.8 | 855.1 | 630.5 | 739.7 | 667.1 | 633.5 | 703.3 | 634.1 | 637.1 | 647.6 | 768.5 | 256.1 | 331.4 | 336.2 | 308.5 | 247.4 | 316.9 | 332.9 | 287.7
909.2 | 633.2 | 469.2 | 187.68 | 219.3871 | 288.1 | 296.8 | 307 | 318.5 | 492.9 | 46.2 | 19.9 | 88.3 | 6.4 | 252.9 | 17.7 | 810.1 | 692 | 697.4 | 854.1 | 628.2 | 739.2 | 660.3 | 622.8 | 702.5 | 632.5 | 637.3 | 644 | 772 | 256.4 | 331.8 | 336.4 | 308.4 | 247.6 | 317.9 | 332.9 | 288
910.2 | 634.2 | 468.3 | 187.32 | 218.9663 | 288.4 | 297.3 | 306 | 319 | 487.4 | 46.2 | 19.9 | 88.1 | 5.7 | 257.2 | 18.3 | 805.6 | 686.1 | 686.1 | 852.6 | 625 | 738.7 | 657.8 | 613.8 | 702.7 | 630.6 | 637.4 | 637.9 | 775.2 | 256.7 | 331.6 | 336.2 | 308.3 | 247.9 | 318.8 | 333 | 288.3
911.2 | 635.2 | 466.3 | 186.52 | 218.0311 | 289.4 | 297.3 | 304.6 | 319.1 | 482.9 | 46.2 | 19.9 | 88.1 | 6.5 | 252.9 | 17.8 | 803.7 | 679.1 | 680.4 | 850.9 | 622.9 | 738.3 | 657.4 | 600.5 | 701.1 | 628.4 | 637.7 | 632.3 | 777 | 257 | 331 | 335.5 | 308.1 | 248.2 | 319.8 | 333 | 288.7
912.2 | 636.2 | 466.1 | 186.44 | 217.9376 | 290.1 | 296.7 | 303.7 | 319.3 | 479 | 46.3 | 19.9 | 88.2 | 7.5 | 252.8 | 17.9 | 801.5 | 673 | 668.5 | 849.1 | 619.7 | 737.7 | 654.2 | 591.7 | 699.9 | 626.7 | 638 | 627.8 | 776.8 | 257.3 | 330.2 | 334.4 | 307.9 | 248.5 | 320.3 | 332.9 | 289
913.2 | 637.2 | 468.4 | 187.36 | 219.013 | 291.3 | 296.3 | 303.3 | 319.2 | 475.8 | 46.3 | 19.9 | 88.5 | 8.3 | 256.1 | 16.4 | 798.4 | 664.5 | 658.6 | 847 | 616.9 | 737.3 | 654.2 | 578.9 | 697.9 | 624.3 | 638.2 | 623.2 | 775.9 | 257.6 | 329.4 | 334 | 307.7 | 248.8 | 321.2 | 333.1 | 289.3
914.2 | 638.2 | 468.5 | 187.4 | 219.0598 | 291.6 | 294.4 | 302.8 | 319.1 | 472.8 | 46.4 | 19.9 | 88.7 | 6.6 | 253.9 | 16.9 | 796.8 | 670.6 | 655.5 | 845 | 615.9 | 737 | 652.6 | 581.3 | 698 | 624.2 | 638.4 | 620.8 | 776.2 | 258 | 328.7 | 333.9 | 307.6 | 249.1 | 322 | 333 | 289.8
915.2 | 639.2 | 466.2 | 186.48 | 217.9844 | 290.2 | 292.3 | 302.6 | 318.7 | 473.9 | 46.5 | 19.9 | 88.8 | 4.5 | 264.8 | 17 | 796.5 | 679.3 | 657 | 843.3 | 615.1 | 736.3 | 644 | 593.7 | 698 | 624.2 | 638.7 | 621.2 | 777.6 | 258.4 | 328.3 | 334.1 | 307.8 | 249.4 | 322 | 332.8 | 290.1
916.2 | 640.2 | 465.6 | 186.24 | 217.7038 | 291.3 | 290.8 | 302.8 | 318.2 | 471.8 | 46.5 | 19.9 | 88.8 | 4 | 278.4 | 14.6 | 795.3 | 685 | 655.8 | 841.5 | 614.5 | 735.7 | 636.8 | 600 | 697.2 | 623.7 | 638.8 | 618.5 | 778.5 | 258.7 | 327.9 | 333.8 | 307.8 | 249.6 | 322.1 | 332.8 | 290.2
917.2 | 641.2 | 467.1 | 186.84 | 218.4052 | 290.8 | 289.5 | 302.9 | 317.3 | 470.1 | 46.6 | 19.9 | 88.8 | 4.7 | 272.4 | 13.7 | 796.1 | 693.8 | 663.2 | 840 | 616.7 | 735 | 632.8 | 609.4 | 697.6 | 623.7 | 638.8 | 619.2 | 779.4 | 259.1 | 328.3 | 333.7 | 307.8 | 249.9 | 321.8 | 332.7 | 290.3
918.2 | 642.2 | 465.8 | 186.32 | 217.7973 | 288.4 | 288.8 | 302.7 | 316.2 | 469.4 | 46.6 | 19.9 | 88.9 | 5 | 287.6 | 13.7 | 796.1 | 694.1 | 679 | 838.7 | 616.3 | 734.6 | 627.4 | 616.6 | 697.5 | 623.7 | 638.8 | 624.7 | 778.8 | 259.5 | 328.8 | 334.1 | 308.1 | 250.1 | 321.2 | 332.3 | 290.4
919.2 | 643.2 | 467.4 | 186.96 | 218.5455 | 288 | 288.4 | 302.8 | 315.2 | 468.4 | 46.7 | 19.9 | 88.9 | 5.7 | 280.2 | 13.8 | 795.7 | 697.1 | 687.5 | 837.6 | 617.1 | 734.2 | 620 | 619.1 | 696.5 | 623.3 | 638.6 | 627.2 | 778.2 | 259.9 | 329.4 | 334.5 | 308.4 | 250.3 | 320.6 | 331.9 | 290.5
920.2 | 644.2 | 468.2 | 187.28 | 218.9195 | 290.6 | 287.8 | 302.3 | 314.5 | 470 | 46.7 | 19.9 | 88.9 | 7.2 | 281.9 | 14.7 | 795.7 | 695.2 | 690 | 836.4 | 618 | 733.7 | 613.2 | 629.4 | 695.7 | 623.2 | 638.4 | 631.8 | 777.5 | 260.2 | 329.7 | 334.7 | 308.7 | 250.5 | 320.1 | 331.7 | 290.5
921.2 | 645.2 | 469 | 187.6 | 219.2936 | 292.1 | 287.2 | 301.2 | 313.9 | 473.3 | 46.9 | 19.9 | 88.9 | 7.4 | 276.2 | 13.8 | 797.7 | 707.7 | 698.4 | 836.4 | 620.4 | 732.9 | 611.2 | 648.9 | 697.6 | 624.3 | 638 | 636.7 | 777 | 260.4 | 330.1 | 334.8 | 309 | 250.7 | 319.6 | 331.7 | 290.6
922.2 | 646.2 | 468.8 | 187.52 | 219.2001 | 293.4 | 287.2 | 301.5 | 313.7 | 475.4 | 47 | 19.9 | 89.2 | 8 | 279.8 | 11.7 | 797.7 | 715.1 | 698.2 | 836.4 | 620.1 | 732.3 | 609.8 | 649.5 | 698.8 | 624.9 | 637.7 | 634.7 | 777.4 | 260.6 | 330.3 | 334.9 | 309.2 | 251 | 319.4 | 331.7 | 290.7
923.2 | 647.2 | 468.3 | 187.32 | 218.9663 | 293.9 | 288.5 | 301.8 | 313.5 | 469.9 | 47.1 | 19.9 | 89.4 | 7.5 | 276.1 | 11.7 | 798.2 | 724.7 | 702.9 | 836.4 | 621.9 | 731.8 | 606.4 | 654.5 | 699.2 | 625.3 | 637.4 | 633.6 | 778.4 | 260.7 | 330.3 | 334.9 | 309.4 | 251.2 | 319.3 | 331.9 | 290.8
924.2 | 648.2 | 468.1 | 187.24 | 218.8728 | 294 | 290.4 | 301.1 | 313.4 | 470.9 | 47.2 | 19.9 | 89.5 | 7.5 | 269.9 | 11.6 | 798.1 | 720.1 | 704.7 | 836.5 | 621.2 | 731.1 | 604.1 | 658.6 | 699.2 | 625.3 | 637 | 633 | 779.6 | 261 | 329.7 | 334.9 | 309.5 | 251.4 | 319 | 331.8 | 290.9
925.2 | 649.2 | 468.1 | 187.24 | 218.8728 | 295.5 | 290.7 | 300.2 | 313.2 | 474.4 | 47.3 | 19.8 | 89.5 | 6.1 | 275.2 | 12.1 | 797.6 | 711.3 | 703.1 | 836.4 | 620.2 | 730.5 | 603 | 664.3 | 699.4 | 625.1 | 636.7 | 637.1 | 779.9 | 261.3 | 330 | 335 | 309.8 | 251.6 | 318.8 | 332 | 291.1
926.2 | 650.2 | 469.1 | 187.64 | 219.3403 | 294.6 | 292.3 | 300.2 | 313.5 | 483.5 | 47.4 | 19.8 | 89.5 | 5.5 | 258.3 | 12.2 | 795.3 | 695.1 | 699.5 | 835.1 | 617.7 | 730.7 | 600.3 | 649.9 | 695.2 | 622.8 | 636.6 | 637.1 | 776.7 | 261.6 | 331.2 | 335.4 | 310.3 | 251.9 | 318.8 | 332.7 | 291.1
927.2 | 651.2 | 468.9 | 187.56 | 219.2468 | 294.4 | 292.5 | 300.5 | 314.4 | 491.4 | 47.4 | 19.8 | 89.5 | 6.6 | 253.9 | 11.1 | 793.8 | 682.5 | 693.7 | 833.4 | 616.1 | 731.2 | 601.7 | 644.8 | 692.8 | 621.8 | 636.8 | 641.1 | 772.5 | 262 | 332.9 | 336.4 | 311 | 252.1 | 318.8 | 333.3 | 291.3
928.2 | 652.2 | 469.1 | 187.64 | 219.3403 | 295.6 | 292.5 | 302.2 | 314.9 | 501 | 47.5 | 19.8 | 89.6 | 5.9 | 254.9 | 10.4 | 794.5 | 678.1 | 690.4 | 832.3 | 615.2 | 731.8 | 603.7 | 650.8 | 692.4 | 621.1 | 637.3 | 645.6 | 769 | 262.3 | 334.2 | 337.8 | 311.5 | 252.3 | 318.9 | 334.1 | 291.5
929.2 | 653.2 | 468.7 | 187.48 | 219.1533 | 298 | 292.7 | 303.5 | 316.3 | 507.4 | 47.5 | 19.8 | 89.5 | 5.9 | 252.2 | 9.6 | 795.2 | 672.2 | 702.7 | 831.5 | 615.7 | 732.5 | 603 | 656.8 | 692 | 621.6 | 637.8 | 653.8 | 764.9 | 262.6 | 335.5 | 338.9 | 312 | 252.6 | 319.9 | 334.8 | 291.6
930.2 | 654.2 | 468.8 | 187.52 | 219.2001 | 299.5 | 293.1 | 305.6 | 317.1 | 509.9 | 47.5 | 19.8 | 89.5 | 6.1 | 240.4 | 10.6 | 795.6 | 665.5 | 708.4 | 830.4 | 617.4 | 732.6 | 602.1 | 660.9 | 691.7 | 620.6 | 637.9 | 660.4 | 760.5 | 262.8 | 336.9 | 340 | 312.9 | 252.8 | 320.5 | 335.9 | 291.8
931.2 | 655.2 | 469.5 | 187.8 | 219.5274 | 302.1 | 293.2 | 306.6 | 318.4 | 513.9 | 47.5 | 19.8 | 89.4 | 6.6 | 248 | 12.4 | 795.5 | 658 | 710.4 | 829.1 | 617.6 | 732.9 | 602.4 | 661.8 | 690.3 | 620.2 | 638.1 | 666.1 | 756 | 263.2 | 338.1 | 341.1 | 313.3 | 253.1 | 320.6 | 336.9 | 292
932.2 | 656.2 | 469.2 | 187.68 | 219.3871 | 305.9 | 293.8 | 308.3 | 320 | 513.7 | 47.5 | 19.8 | 89.4 | 6.9 | 230.2 | 12.5 | 796.1 | 665.5 | 716.8 | 828.4 | 619.2 | 732.9 | 602.4 | 676.8 | 691.4 | 622 | 638.5 | 671.5 | 753.3 | 263.5 | 339.1 | 342.3 | 313.3 | 253.4 | 320.8 | 337.5 | 292.3
933.2 | 657.2 | 469.5 | 187.8 | 219.5274 | 308.8 | 295.1 | 309.9 | 321.2 | 519.4 | 47.5 | 19.8 | 89.4 | 6.7 | 239.5 | 11.9 | 795.7 | 667 | 711.3 | 828 | 617.9 | 733.1 | 601.8 | 680.2 | 692.5 | 621.9 | 638.8 | 670.1 | 753.6 | 263.7 | 339.8 | 343.3 | 313.3 | 253.7 | 321.6 | 339 | 292.6
934.2 | 658.2 | 469.6 | 187.84 | 219.5741 | 311.2 | 296.3 | 311.3 | 322.6 | 519.5 | 47.5 | 19.8 | 89.4 | 6.9 | 237.4 | 11.4 | 794.5 | 668.5 | 706.8 | 827.3 | 616.7 | 733.4 | 602.6 | 681.7 | 694.3 | 621.5 | 639.1 | 668.1 | 753.8 | 263.9 | 340.7 | 344.5 | 313.6 | 254.2 | 322.4 | 340.2 | 292.9
935.2 | 659.2 | 468.8 | 187.52 | 219.2001 | 313.1 | 297.7 | 313.6 | 324.2 | 521.1 | 47.6 | 19.8 | 89.3 | 5.9 | 259.9 | 10.1 | 795.5 | 670.9 | 715.3 | 827.3 | 619.3 | 733.6 | 601.3 | 694.6 | 696.1 | 622.3 | 639.6 | 672.5 | 753 | 264.2 | 341.2 | 345.7 | 313.7 | 254.7 | 323 | 341 | 293.2
936.2 | 660.2 | 469.2 | 187.68 | 219.3871 | 317.4 | 299.1 | 315.3 | 325.4 | 520.5 | 47.6 | 19.8 | 89.3 | 5.9 | 235 | 9.9 | 798.1 | 676.5 | 725.9 | 828.3 | 622.6 | 733.2 | 601.7 | 718.4 | 701.2 | 625.4 | 639.8 | 679.9 | 752.4 | 264.5 | 341.5 | 347.2 | 313.8 | 255.1 | 323.3 | 341.3 | 293.5
937.2 | 661.2 | 469.6 | 187.84 | 219.5741 | 320.4 | 301.7 | 316.5 | 326 | 525.9 | 47.6 | 19.8 | 89.2 | 5.8 | 244.5 | 11.5 | 800.9 | 687.5 | 737.2 | 829.6 | 627.1 | 733.4 | 603.5 | 732.1 | 704.1 | 629.3 | 639.8 | 687.3 | 751.6 | 264.8 | 341.9 | 348.8 | 314.1 | 255.6 | 323.5 | 343.7 | 293.8
938.2 | 662.2 | 469.6 | 187.84 | 219.5741 | 321 | 304.6 | 317.2 | 326.8 | 532.8 | 47.6 | 19.8 | 89 | 4.9 | 250 | 12.5 | 799.7 | 678.4 | 728.2 | 830.1 | 625.8 | 733.9 | 602.8 | 720.6 | 702.6 | 629.3 | 639.8 | 688.8 | 749.2 | 265.1 | 343 | 350.1 | 314.5 | 256.1 | 324.2 | 343.5 | 294.1
939.2 | 663.2 | 469.2 | 187.68 | 219.3871 | 321.5 | 305.2 | 318.6 | 327.7 | 543.7 | 47.6 | 19.8 | 88.9 | 3.9 | 255.4 | 11.3 | 797.9 | 665.9 | 717.7 | 829.2 | 621.6 | 734.6 | 600.3 | 701.7 | 700.7 | 627.3 | 640.2 | 689.7 | 745 | 265.3 | 344.6 | 351.8 | 315 | 256.6 | 325 | 344.8 | 294.4
940.2 | 664.2 | 468.4 | 187.36 | 219.013 | 321.6 | 305.7 | 320.1 | 329.1 | 547.5 | 47.6 | 19.8 | 88.8 | 4.6 | 240.1 | 10.4 | 795.4 | 654.4 | 704 | 827.7 | 618.6 | 734.9 | 595.3 | 680.4 | 698.5 | 625.4 | 640.7 | 688.3 | 739.7 | 265.6 | 346 | 353.3 | 315.7 | 257.1 | 325.9 | 345.3 | 294.7
941.2 | 665.2 | 468 | 187.2 | 218.826 | 323 | 306.6 | 322.2 | 330.4 | 547 | 47.7 | 19.8 | 88.7 | 4.2 | 246.8 | 10.4 | 792.8 | 643 | 694.8 | 825.7 | 616.1 | 735.3 | 589.7 | 670.9 | 695.4 | 624 | 641.1 | 689.3 | 734.5 | 266 | 347.3 | 354.8 | 316.2 | 257.7 | 326.4 | 345.7 | 295
942.2 | 666.2 | 467.4 | 186.96 | 218.5455 | 322.1 | 306.9 | 323.9 | 331.8 | 550.1 | 47.7 | 19.8 | 88.7 | 4.5 | 244.4 | 11 | 790.5 | 632.3 | 685.5 | 823.3 | 613.6 | 735.5 | 586.3 | 657.8 | 694.1 | 622.2 | 641.8 | 688.9 | 728.8 | 266.5 | 348.5 | 356.3 | 316.8 | 258.2 | 326.8 | 346.9 | 295.3
943.2 | 667.2 | 466.7 | 186.68 | 218.2182 | 322.3 | 307.2 | 325.6 | 333.2 | 550.5 | 47.7 | 19.8 | 88.6 | 4.7 | 244.9 | 10.2 | 788.2 | 623.8 | 682.7 | 820.8 | 611.6 | 736 | 584.2 | 643 | 690.6 | 620.6 | 642.5 | 689.4 | 723.8 | 266.9 | 349.5 | 357.3 | 317.5 | 258.7 | 327.6 | 347.9 | 295.7
944.2 | 668.2 | 468.5 | 187.4 | 219.0598 | 322.2 | 307.7 | 328 | 334.8 | 552.8 | 47.8 | 19.8 | 88.6 | 5.6 | 241.5 | 10.6 | 786.4 | 621.5 | 681.3 | 818.1 | 610.4 | 736.7 | 583.7 | 635.7 | 687.5 | 619.5 | 643.3 | 691.2 | 719.7 | 267.3 | 350.4 | 358.5 | 318 | 259.2 | 328.3 | 348.4 | 296
945.2 | 669.2 | 469.2 | 187.68 | 219.3871 | 322.9 | 308.5 | 329.4 | 336.2 | 549.2 | 47.8 | 19.8 | 88.7 | 5.6 | 258 | 9.9 | 786.6 | 631.9 | 697.5 | 816.3 | 613.5 | 736.8 | 582.9 | 646.9 | 686.8 | 619.7 | 643.9 | 692.3 | 717.4 | 267.7 | 351 | 359.3 | 318.1 | 259.7 | 328.8 | 349.3 | 296.3
946.2 | 670.2 | 468.3 | 187.32 | 218.9663 | 322.5 | 309.6 | 330.6 | 337.7 | 540.7 | 47.8 | 19.8 | 88.6 | 5.7 | 267.3 | 10.2 | 787.9 | 645.2 | 712.9 | 815.8 | 617.6 | 736.7 | 583.4 | 660.7 | 688.5 | 621 | 644 | 693.8 | 716.9 | 268 | 351.2 | 359.5 | 318 | 260.2 | 329.2 | 349.8 | 296.6
947.2 | 671.2 | 469.1 | 187.64 | 219.3403 | 321.4 | 310.4 | 330.3 | 338.5 | 535.4 | 47.8 | 19.8 | 88.6 | 5.8 | 259.6 | 12.1 | 788.5 | 644.2 | 717.3 | 815.5 | 618.8 | 736.8 | 584.1 | 663.5 | 687.6 | 621.1 | 643.9 | 693.5 | 715.4 | 268.4 | 351.6 | 359.8 | 318.2 | 260.7 | 329.5 | 350.7 | 296.9
948.2 | 672.2 | 468.8 | 187.52 | 219.2001 | 322 | 310.9 | 330.4 | 338.7 | 531 | 47.8 | 19.8 | 88.6 | 5.8 | 243.9 | 11.1 | 788.3 | 642.3 | 711.6 | 815 | 617.9 | 736.6 | 581.2 | 660 | 686.1 | 619.4 | 643.9 | 688.9 | 715 | 268.8 | 352.1 | 360.1 | 318.5 | 261.1 | 329.6 | 351.4 | 297.2
949.2 | 673.2 | 469.6 | 187.84 | 219.5741 | 321.4 | 310.5 | 331 | 339.6 | 521.5 | 47.9 | 19.8 | 88.5 | 5.7 | 241.4 | 10.1 | 788.7 | 646.2 | 708.1 | 814.6 | 617.2 | 736.1 | 576.4 | 647.4 | 683.1 | 618.3 | 643.9 | 683.8 | 715.7 | 269.1 | 352.3 | 360.4 | 318.7 | 261.6 | 329.7 | 351.7 | 297.5
950.2 | 674.2 | 469.7 | 187.88 | 219.6209 | 322.7 | 310.5 | 331 | 340.7 | 511.9 | 48 | 19.8 | 88.5 | 5.3 | 247.5 | 10.3 | 788.6 | 664 | 707.5 | 814.7 | 616.1 | 735.3 | 577.9 | 653.3 | 685.3 | 619.6 | 643.8 | 679.7 | 718.5 | 269.5 | 352.1 | 360.3 | 318.8 | 262 | 330 | 352.2 | 297.8
951.2 | 675.2 | 468.5 | 187.4 | 219.0598 | 326 | 310.3 | 329.8 | 340.9 | 505.3 | 48 | 19.8 | 88.6 | 4.3 | 225.4 | 11.1 | 789.1 | 669.6 | 708.9 | 815.3 | 616.8 | 734.3 | 580.4 | 662.6 | 689.3 | 620.1 | 643.7 | 679.8 | 721.6 | 269.8 | 351.9 | 360 | 319 | 262.5 | 330.4 | 352.7 | 298
952.2 | 676.2 | 468.9 | 187.56 | 219.2468 | 328.6 | 311.4 | 328.2 | 340.9 | 500.1 | 48.1 | 19.8 | 88.6 | 4.3 | 236.8 | 10.5 | 789.5 | 674.3 | 707.3 | 816.4 | 616.9 | 733.6 | 578.9 | 671.4 | 689.3 | 620.5 | 643.6 | 678.4 | 724.4 | 270.2 | 351.4 | 359.5 | 319 | 263 | 330.6 | 354.5 | 298.4
953.2 | 677.2 | 470.4 | 188.16 | 219.9482 | 329 | 311.3 | 326.9 | 340.7 | 493.7 | 48.1 | 19.8 | 88.8 | 5.7 | 235.7 | 9.3 | 789.2 | 676.7 | 696.8 | 817.1 | 616.2 | 733.3 | 578.2 | 667.5 | 689.7 | 620 | 643.5 | 675.9 | 726.7 | 270.5 | 351 | 359.3 | 319.1 | 263.6 | 331 | 354 | 298.7
954.2 | 678.2 | 469.9 | 187.96 | 219.7144 | 328.6 | 311.3 | 326.7 | 340 | 489 | 48.2 | 19.8 | 88.9 | 6.7 | 197.7 | 7.2 | 789.8 | 685.5 | 698.3 | 817.3 | 617.7 | 732.8 | 579.2 | 671 | 689.8 | 620.7 | 643.5 | 677 | 727.9 | 270.9 | 350.4 | 358.5 | 319.3 | 264.2 | 331 | 353.9 | 298.9
955.2 | 679.2 | 469.6 | 187.84 | 219.5741 | 327.7 | 311.1 | 325.4 | 338.8 | 488.4 | 48.2 | 19.8 | 89 | 6.9 | 186.6 | 6.8 | 789 | 679 | 700.3 | 816.8 | 617.2 | 732.5 | 576.9 | 664 | 687.4 | 619.7 | 643.5 | 677.9 | 727.9 | 271.2 | 350.2 | 358.1 | 319.7 | 264.7 | 330.9 | 353.2 | 299.1
956.2 | 680.2 | 469.9 | 187.96 | 219.7144 | 326.9 | 309.6 | 323.6 | 338.1 | 486.7 | 48.2 | 19.8 | 89.3 | 6.5 | 193 | 6.1 | 789.7 | 684.7 | 714.7 | 816.9 | 620.3 | 732.2 | 574.4 | 665.1 | 686.3 | 619.7 | 643.5 | 678.8 | 727.9 | 271.6 | 349.7 | 357.9 | 319.8 | 265.3 | 330.6 | 352.3 | 299.3
957.2 | 681.2 | 469.9 | 187.96 | 219.7144 | 328.1 | 308 | 322.1 | 337 | 484.5 | 48.3 | 19.8 | 89.5 | 5.8 | 206.3 | 5.4 | 790.6 | 697.5 | 707.8 | 817.7 | 620.1 | 731.1 | 576.4 | 664.5 | 692 | 621.1 | 643.3 | 673.4 | 727.5 | 271.9 | 349.2 | 357.6 | 319.7 | 265.8 | 330.2 | 351.6 | 299.4
958.2 | 682.2 | 470 | 188 | 219.7612 | 329.3 | 307.3 | 321.4 | 336.5 | 477.9 | 48.3 | 19.8 | 89.7 | 5.6 | 228.1 | 4.7 | 790.8 | 711 | 708.7 | 818.4 | 619.8 | 730.5 | 577.7 | 667.6 | 695.1 | 621.9 | 643.2 | 669.9 | 725.6 | 272.1 | 348.7 | 357.2 | 319.6 | 266.3 | 330.1 | 350.7 | 299.6
959.2 | 683.2 | 469.9 | 187.96 | 219.7144 | 329.5 | 308.1 | 320.5 | 335.7 | 475.8 | 48.3 | 19.8 | 90 | 5.9 | 266.7 | 5.2 | 791.2 | 724.8 | 711.2 | 819.2 | 621.6 | 729.9 | 581.7 | 679.1 | 699.6 | 623.7 | 643.2 | 667.5 | 724.8 | 272.4 | 348.4 | 356.6 | 319.7 | 266.8 | 330.2 | 350.1 | 299.9
960.2 | 684.2 | 469.7 | 187.88 | 219.6209 | 330.7 | 308.1 | 320.4 | 334.2 | 473.9 | 48.4 | 19.8 | 90.2 | 5.6 | 271 | 6.8 | 790.3 | 715.2 | 709.9 | 819.3 | 621.8 | 729.9 | 578.4 | 667.4 | 695.6 | 621.5 | 643.1 | 663.9 | 724.4 | 272.7 | 348.1 | 356.2 | 319.9 | 267.2 | 329.8 | 349.6 | 300
961.2 | 685.2 | 469.3 | 187.72 | 219.4339 | 331.8 | 306.8 | 319.2 | 333.1 | 472.3 | 48.4 | 19.8 | 90.3 | 5.7 | 240.3 | 8.2 | 789.9 | 707.2 | 708.3 | 819.6 | 620.9 | 729.6 | 576.3 | 659.3 | 692.3 | 620.3 | 643 | 662 | 724.4 | 273.1 | 347.9 | 355.8 | 320.1 | 267.7 | 329.2 | 349.1 | 300.1
962.2 | 686.2 | 468.6 | 187.44 | 219.1066 | 332.1 | 306.3 | 317.8 | 332 | 469 | 48.5 | 19.8 | 90.4 | 5.5 | 253.1 | 9.9 | 790.5 | 708.3 | 708.7 | 819.9 | 621.7 | 729.2 | 574.3 | 661 | 690.7 | 619.6 | 643.1 | 659.9 | 725.8 | 273.4 | 347.6 | 355.2 | 320.3 | 268.1 | 328.9 | 348.3 | 300.2
963.2 | 687.2 | 469.9 | 187.96 | 219.7144 | 329.9 | 306.4 | 316.2 | 330.8 | 466.8 | 48.5 | 19.8 | 90.4 | 4.8 | 244.2 | 10.9 | 790.5 | 706.6 | 707.4 | 820.2 | 621.6 | 728.7 | 575 | 664.1 | 692.3 | 619.7 | 643.2 | 658.2 | 726.2 | 273.8 | 347.4 | 354.8 | 320.5 | 268.5 | 329.2 | 349.2 | 300.3
964.2 | 688.2 | 470.3 | 188.12 | 219.9014 | 329.9 | 306.3 | 315.1 | 329.7 | 468.5 | 48.5 | 19.8 | 90.4 | 4.8 | 242.6 | 11.9 | 790.4 | 704.7 | 696.2 | 820.4 | 620.3 | 728.5 | 574.1 | 657.1 | 690.5 | 618.6 | 643.4 | 655.5 | 726.9 | 274.1 | 347.3 | 354.7 | 320.7 | 268.8 | 329.5 | 348.8 | 300.5
965.2 | 689.2 | 468.4 | 187.36 | 219.013 | 330.4 | 305.3 | 314.5 | 328.6 | 465.7 | 48.6 | 19.8 | 90.5 | 4.6 | 251 | 10.2 | 790.5 | 702.4 | 692.7 | 820.6 | 619.3 | 727.9 | 573.4 | 657.3 | 690.2 | 618.3 | 643.5 | 654.8 | 726.4 | 274.4 | 347.1 | 355 | 320.8 | 269.1 | 329.6 | 348 | 300.7
966.2 | 690.2 | 470 | 188 | 219.7612 | 329.5 | 305.1 | 315.4 | 327.2 | 465 | 48.6 | 19.8 | 90.7 | 6 | 261.7 | 8.3 | 789.7 | 690.9 | 689.7 | 819.9 | 617.4 | 727.9 | 571 | 645.7 | 686.7 | 616.6 | 643.7 | 654.7 | 725.5 | 274.7 | 347 | 354.8 | 320.9 | 269.5 | 330 | 347.5 | 300.8
967.2 | 691.2 | 469.7 | 187.88 | 219.6209 | 327.5 | 304.9 | 315.9 | 325.9 | 464.9 | 48.6 | 19.7 | 90.8 | 5.7 | 253.9 | 8.3 | 788.3 | 686.8 | 685.9 | 818.8 | 616.1 | 727.5 | 570.7 | 638.6 | 685.4 | 615.3 | 643.9 | 651.4 | 725.4 | 275.1 | 346.7 | 354.3 | 321 | 269.8 | 330.3 | 347.2 | 301
968.2 | 692.2 | 468.9 | 187.56 | 219.2468 | 326 | 304.5 | 315.2 | 324.9 | 467.2 | 48.7 | 19.7 | 91.1 | 5.4 | 253.2 | 10.7 | 787.3 | 690 | 678.3 | 817.5 | 615.3 | 727.2 | 571.7 | 634.5 | 686.6 | 614.7 | 644.1 | 647.3 | 725.3 | 275.4 | 346.1 | 353.5 | 321 | 270.1 | 330.8 | 346.9 | 301.4
969.2 | 693.2 | 470.2 | 188.08 | 219.8547 | 324.7 | 304.7 | 313.9 | 325 | 464.5 | 48.7 | 19.7 | 91.1 | 5.3 | 275.6 | 9.6 | 785.9 | 684.3 | 673.3 | 816 | 613.7 | 727 | 569.5 | 625.7 | 685.1 | 613.5 | 644.1 | 644.9 | 725.3 | 275.7 | 345.8 | 352.9 | 320.9 | 270.4 | 331 | 346.5 | 301.6
970.2 | 694.2 | 470.5 | 188.2 | 219.995 | 323.9 | 303.7 | 312.7 | 324.3 | 459.7 | 48.7 | 19.7 | 91.2 | 6.2 | 261 | 8.6 | 783.2 | 674.3 | 666.1 | 813.5 | 610.5 | 726.7 | 566.4 | 612.8 | 681.8 | 611.2 | 644.1 | 639.9 | 724.8 | 276 | 345.2 | 352.2 | 320.8 | 270.7 | 331.2 | 346.3 | 301.8
971.2 | 695.2 | 470.6 | 188.24 | 220.0417 | 323.8 | 302.8 | 311.6 | 322.4 | 457.1 | 48.8 | 19.7 | 91.4 | 5.6 | 261.5 | 9.4 | 781.2 | 670.1 | 659.9 | 811.3 | 609.8 | 726.3 | 563.5 | 606.7 | 678.8 | 610 | 644.2 | 637.3 | 724.2 | 276.3 | 344.3 | 351.4 | 320.8 | 271 | 331.5 | 345.8 | 302.1
972.2 | 696.2 | 470.9 | 188.36 | 220.182 | 323.2 | 302.1 | 310.5 | 320.9 | 452.7 | 48.8 | 19.7 | 91.5 | 5 | 259.4 | 10.5 | 780.1 | 662.4 | 658.4 | 808.8 | 607.9 | 725.6 | 563 | 603.9 | 677.6 | 608.7 | 643.9 | 635.4 | 724.2 | 276.5 | 343.5 | 350.8 | 320.8 | 271.2 | 331.7 | 345.5 | 302.3
973.2 | 697.2 | 470.9 | 188.36 | 220.182 | 322.5 | 302.1 | 309.5 | 320.3 | 451.1 | 48.8 | 19.7 | 91.6 | 4.9 | 270.9 | 9.5 | 780.5 | 664.3 | 662.1 | 807.3 | 608.1 | 724.8 | 564.6 | 612.6 | 679.3 | 609.1 | 643.6 | 634 | 724.7 | 276.7 | 342.9 | 350.2 | 320.8 | 271.5 | 331.4 | 345 | 302.5
974.2 | 698.2 | 471 | 188.4 | 220.2287 | 322.6 | 301.9 | 308.9 | 319.6 | 449.2 | 48.8 | 19.7 | 91.7 | 5.1 | 259.7 | 9.3 | 779.5 | 654.9 | 657.9 | 805.4 | 606.7 | 724 | 563.7 | 604.4 | 678.8 | 607.4 | 643.2 | 630.3 | 726.7 | 277 | 342.3 | 349.6 | 320.9 | 271.8 | 331.2 | 344.2 | 302.5
975.2 | 699.2 | 469.9 | 187.96 | 219.7144 | 322.8 | 300.7 | 308.7 | 318.4 | 447.7 | 48.8 | 19.7 | 91.9 | 5.5 | 275.2 | 10.5 | 776.8 | 644.6 | 646.5 | 802.8 | 603.2 | 723.3 | 560.7 | 589.1 | 675.4 | 605 | 642.6 | 625.2 | 727.5 | 277.4 | 341.6 | 348.7 | 320.8 | 272.1 | 331 | 344.2 | 302.7
976.2 | 700.2 | 470.2 | 188.08 | 219.8547 | 321 | 300.2 | 308.2 | 317.2 | 445 | 48.8 | 19.7 | 92.1 | 5.8 | 254.4 | 10.3 | 773.7 | 635.1 | 635.9 | 799.6 | 600.6 | 722.8 | 557.2 | 573.8 | 670.8 | 602.4 | 642 | 619.2 | 727.6 | 277.7 | 340.3 | 347.7 | 320.7 | 272.4 | 330.9 | 344 | 302.9
977.2 | 701.2 | 470.5 | 188.2 | 219.995 | 319.4 | 300 | 307.3 | 317.4 | 443.2 | 48.9 | 19.7 | 92.2 | 5.8 | 246.4 | 10.4 | 770.1 | 626.5 | 625.2 | 796.3 | 597.3 | 722.1 | 553 | 560.7 | 665.9 | 600 | 641.6 | 614.7 | 727.3 | 277.9 | 339.3 | 346.4 | 320.6 | 272.6 | 330.7 | 343.6 | 303.1
978.2 | 702.2 | 470 | 188 | 219.7612 | 318.1 | 299.4 | 305.5 | 317.1 | 442.6 | 48.9 | 19.7 | 92.2 | 5.5 | 245.7 | 9.7 | 766.9 | 618.4 | 614.8 | 792.5 | 593.9 | 721.3 | 549.6 | 550.7 | 661.6 | 597.5 | 640.9 | 609.7 | 728.6 | 278.1 | 338.3 | 345 | 320.4 | 272.9 | 330.6 | 343 | 303.2
979.2 | 703.2 | 470.4 | 188.16 | 219.9482 | 317.2 | 298.1 | 304.2 | 316.1 | 441.6 | 48.9 | 19.7 | 92.3 | 6.2 | 257 | 9.5 | 763.6 | 612 | 606.1 | 788.6 | 591.5 | 720.4 | 545.8 | 541.9 | 656.1 | 595.1 | 640 | 604.7 | 729.7 | 278.3 | 337.2 | 344.3 | 320.1 | 273.1 | 330.8 | 342.7 | 303.4
980.2 | 704.2 | 470 | 188 | 219.7612 | 316.6 | 297.1 | 303 | 315 | 440.1 | 49 | 19.7 | 92.4 | 6.7 | 251 | 8.6 | 760.7 | 611.1 | 603 | 785.5 | 590 | 719.7 | 543.5 | 541.9 | 653.3 | 593.4 | 639.2 | 600.9 | 730.1 | 278.4 | 336.2 | 343.4 | 320 | 273.3 | 330.6 | 342.2 | 303.6
981.2 | 705.2 | 470.7 | 188.28 | 220.0885 | 315.5 | 295.8 | 302.2 | 314.4 | 440.2 | 49 | 19.7 | 92.6 | 6.4 | 252 | 7.6 | 757.5 | 608 | 599.1 | 782.1 | 587.2 | 718.8 | 542.3 | 537.1 | 651 | 591.8 | 638.7 | 596.4 | 730.4 | 278.5 | 335.4 | 342.5 | 319.9 | 273.6 | 330.5 | 342 | 303.7
982.2 | 706.2 | 470.6 | 188.24 | 220.0417 | 314.6 | 294.5 | 301.7 | 313.7 | 440.9 | 49 | 19.7 | 92.7 | 5.4 | 252.3 | 7.8 | 754.8 | 604.6 | 601.1 | 778.7 | 585.1 | 717.8 | 540.2 | 529.9 | 649.7 | 589.8 | 638.3 | 593.2 | 731.4 | 278.6 | 334.4 | 341.6 | 319.7 | 273.8 | 330.2 | 341.3 | 303.8
983.2 | 707.2 | 470.5 | 188.2 | 219.995 | 313.7 | 294.1 | 301.7 | 312.6 | 438.4 | 49.1 | 19.7 | 92.7 | 4 | 248.2 | 7.8 | 753.6 | 606 | 614 | 775.7 | 585.4 | 716.8 | 540.3 | 537.6 | 651 | 588.9 | 637.8 | 592.2 | 732.1 | 278.7 | 333.4 | 340.6 | 319.7 | 274 | 329.7 | 340.6 | 303.8
984.2 | 708.2 | 469.9 | 187.96 | 219.7144 | 311.9 | 293.2 | 301.8 | 312 | 439.7 | 49.1 | 19.7 | 92.6 | 3.9 | 252.9 | 7.5 | 753.9 | 620.3 | 629.3 | 773.7 | 588.7 | 715.9 | 542 | 559 | 654 | 589.9 | 637.4 | 595 | 732.3 | 278.8 | 332.6 | 339.8 | 319.7 | 274.2 | 329 | 340.1 | 303.9
985.2 | 709.2 | 469.8 | 187.92 | 219.6677 | 311.4 | 292.1 | 301.3 | 311 | 442.7 | 49.2 | 19.7 | 92.6 | 3.7 | 261.1 | 6.9 | 753.9 | 629.5 | 627.1 | 772.4 | 587.3 | 714.9 | 542.5 | 562.9 | 656.2 | 589.8 | 636.9 | 592.4 | 734.1 | 278.8 | 332.2 | 339.1 | 319.8 | 274.3 | 328.3 | 339.7 | 303.9
986.2 | 710.2 | 470.3 | 188.12 | 219.9014 | 312.1 | 291.3 | 299.8 | 310.7 | 442.1 | 49.2 | 19.7 | 92.7 | 5 | 257.4 | 6.9 | 754.2 | 633.5 | 629.4 | 771.3 | 587.2 | 714 | 541.6 | 570.4 | 656.1 | 589.2 | 636.4 | 593.9 | 736 | 279.1 | 332.3 | 338.8 | 319.8 | 274.4 | 328 | 339.5 | 303.9
987.2 | 711.2 | 469.6 | 187.84 | 219.5741 | 312.2 | 291 | 299.3 | 310.7 | 442.3 | 49.3 | 19.7 | 92.8 | 4.9 | 222.1 | 6.1 | 754.1 | 630.9 | 643.8 | 771 | 588.3 | 713.4 | 540.4 | 580.9 | 655.9 | 589.2 | 636.2 | 597.9 | 735 | 279.4 | 332.5 | 338.8 | 320 | 274.5 | 327.8 | 339.1 | 303.9
988.2 | 712.2 | 467.5 | 187 | 218.5922 | 311.1 | 290.7 | 299.8 | 310.8 | 443 | 49.3 | 19.6 | 93 | 5.2 | 192 | 5.9 | 753.7 | 640.9 | 649.1 | 771.2 | 589 | 712.7 | 540.8 | 589.2 | 656.3 | 589.9 | 635.8 | 599 | 735.8 | 279.6 | 332.3 | 338.7 | 320.1 | 274.6 | 327.6 | 338.6 | 304
989.2 | 713.2 | 469 | 187.6 | 219.2936 | 310.5 | 290.6 | 300.3 | 310.9 | 442.2 | 49.3 | 19.6 | 93 | 5.7 | 217.3 | 6.5 | 755.5 | 656.6 | 648.8 | 772.3 | 590.2 | 711.7 | 542.7 | 610.2 | 659.6 | 592.2 | 635.6 | 600 | 739 | 279.7 | 331.9 | 338.4 | 320.1 | 274.7 | 327.6 | 338.5 | 304.1
990.2 | 714.2 | 468.9 | 187.56 | 219.2468 | 310.5 | 290.1 | 300.8 | 310.8 | 444.6 | 49.3 | 19.6 | 93 | 6.3 | 212.2 | 8.1 | 756.4 | 675.5 | 653.7 | 773.9 | 591.6 | 710.9 | 545 | 628.4 | 663.7 | 593.9 | 635.4 | 600.3 | 740.6 | 280 | 331.8 | 338.5 | 320.2 | 274.8 | 327.5 | 338.5 | 304.1
991.2 | 715.2 | 468.4 | 187.36 | 219.013 | 309.4 | 290.2 | 301.1 | 311.1 | 445.5 | 49.3 | 19.6 | 93 | 6 | 233.3 | 8.9 | 757.6 | 693.7 | 664.5 | 776.1 | 593.4 | 710 | 548.6 | 652.9 | 667.8 | 596.9 | 635.2 | 603.1 | 741.6 | 280.2 | 331.7 | 338.5 | 320.2 | 274.8 | 327.4 | 337.9 | 304.2
992.2 | 716.2 | 468 | 187.2 | 218.826 | 309.2 | 290.6 | 301.7 | 310.8 | 444.7 | 49.4 | 19.6 | 93.1 | 5.2 | 252.5 | 9.1 | 759.4 | 715.1 | 672 | 779.1 | 596.1 | 709.6 | 552.3 | 674.9 | 674.6 | 601 | 634.8 | 605.7 | 741.7 | 280.3 | 331.9 | 338.4 | 320.2 | 274.9 | 327.1 | 337.3 | 304.3
993.2 | 717.2 | 468.6 | 187.44 | 219.1066 | 308.7 | 291.3 | 302.5 | 310.2 | 447 | 49.5 | 19.6 | 93.2 | 5.3 | 243.9 | 11 | 761.3 | 727.2 | 678.8 | 782.1 | 598.7 | 709.3 | 554.9 | 684.8 | 678.7 | 604.3 | 634.3 | 606 | 742.1 | 280.4 | 332.1 | 338.4 | 320.2 | 274.9 | 326.4 | 336.7 | 304.3
994.2 | 718.2 | 469.6 | 187.84 | 219.5741 | 309.2 | 292.3 | 303.2 | 310.1 | 451 | 49.5 | 19.6 | 93.2 | 5 | 256 | 12.5 | 763.7 | 735.5 | 688.4 | 784.9 | 600.8 | 709.1 | 555.5 | 690.9 | 680.2 | 605.9 | 633.8 | 611.4 | 741.3 | 280.5 | 332.5 | 338.4 | 320.5 | 275 | 326.1 | 336.6 | 304.3
995.2 | 719.2 | 469.2 | 187.68 | 219.3871 | 308.3 | 292.8 | 303.7 | 310.5 | 453.8 | 49.5 | 19.6 | 93.2 | 6.7 | 246.4 | 12.8 | 764.3 | 733.3 | 683.9 | 787.5 | 599.8 | 708.8 | 553.7 | 676.4 | 678.3 | 605.2 | 633.4 | 607.9 | 743.8 | 280.5 | 332.5 | 338.5 | 320.6 | 275 | 325.6 | 336.3 | 304.3
996.2 | 720.2 | 470.4 | 188.16 | 219.9482 | 307.1 | 293.2 | 304 | 311 | 451.1 | 49.5 | 19.6 | 93.4 | 7.4 | 231.3 | 13.4 | 764.6 | 740 | 680.9 | 789.8 | 598.6 | 708.1 | 555 | 677 | 681 | 606.4 | 633.2 | 607.5 | 746.8 | 280.7 | 332.5 | 338.3 | 320.6 | 275 | 325.5 | 336.2 | 304.4
997.2 | 721.2 | 470.5 | 188.2 | 219.995 | 307.2 | 293.8 | 303.8 | 311.2 | 452 | 49.5 | 19.6 | 93.5 | 7.1 | 256 | 12.4 | 766.5 | 752.5 | 685.2 | 792.5 | 600 | 707.9 | 556.9 | 686 | 683.7 | 609 | 633.2 | 608.7 | 746.8 | 280.7 | 332.4 | 338.2 | 320.7 | 275 | 325.3 | 336.1 | 304.5
998.2 | 722.2 | 469.2 | 187.68 | 219.3871 | 306.2 | 294 | 302.8 | 311.4 | 452.5 | 49.5 | 19.6 | 93.5 | 9.6 | 243 | 12.5 | 769.6 | 761.4 | 688.7 | 795.9 | 602.8 | 707.7 | 563.6 | 711.2 | 692.9 | 615.3 | 633.2 | 612 | 747.8 | 280.8 | 332.5 | 338.2 | 320.7 | 275 | 325.1 | 335.5 | 304.7
999.2 | 723.2 | 470.6 | 188.24 | 220.0417 | 306.1 | 294.3 | 302.6 | 311.5 | 457.1 | 49.6 | 19.6 | 93.5 | 7.5 | 235.6 | 13.1 | 770.4 | 770.5 | 689.5 | 799.1 | 603.4 | 707.4 | 568.1 | 711.9 | 697.3 | 616.8 | 633.1 | 612.9 | 749.7 | 280.8 | 332.6 | 338.9 | 320.6 | 275 | 325.1 | 335 | 304.8
1000.2 | 724.2 | 471 | 188.4 | 220.2287 | 305.9 | 294.2 | 302.4 | 311.1 | 456.1 | 49.7 | 19.6 | 93.4 | 7.6 | 242.9 | 14.4 | 774.5 | 772.5 | 701.3 | 802.6 | 605.8 | 707.8 | 569.4 | 731.3 | 699.3 | 620 | 632.9 | 624.4 | 751.4 | 280.9 | 332.7 | 339.2 | 320.7 | 275 | 325 | 334.6 | 304.8
1001.2 | 725.2 | 470.7 | 188.28 | 220.0885 | 307 | 294.7 | 303.6 | 310.7 | 461.3 | 49.8 | 19.6 | 93.4 | 7.7 | 244.3 | 16.6 | 778.2 | 764.8 | 706.7 | 806 | 605.9 | 708.2 | 570.4 | 740.8 | 701.5 | 623.3 | 632.5 | 633.3 | 753 | 280.9 | 333 | 339.3 | 321 | 275 | 324.8 | 334.3 | 304.8
1002.2 | 726.2 | 470 | 188 | 219.7612 | 308.1 | 295.5 | 304.4 | 310.4 | 463.6 | 49.7 | 19.6 | 93.3 | 6.7 | 244.1 | 17.4 | 780.5 | 767.4 | 700.4 | 809.6 | 604.6 | 708.3 | 570.9 | 747.9 | 704.5 | 625.4 | 632.4 | 633.3 | 757.7 | 281 | 332.9 | 339.4 | 321 | 275 | 324.6 | 334.2 | 304.8
1003.2 | 727.2 | 470.4 | 188.16 | 219.9482 | 307.8 | 296.3 | 303.8 | 310.7 | 460.3 | 49.7 | 19.6 | 93.2 | 7.9 | 245.3 | 17.5 | 783.4 | 777.7 | 698.5 | 813.5 | 604.7 | 708.4 | 574.7 | 753.1 | 711.4 | 627.9 | 632.4 | 630.4 | 760.3 | 281.1 | 332.9 | 339.5 | 320.9 | 275 | 324.7 | 334.2 | 304.9
1004.2 | 728.2 | 469.4 | 187.76 | 219.4806 | 307.8 | 297 | 303.9 | 311.3 | 458.3 | 49.6 | 19.6 | 93.1 | 7.4 | 242 | 15.7 | 786.5 | 789.5 | 706.6 | 817.8 | 608.3 | 708.7 | 579.6 | 762.3 | 715.7 | 632.2 | 632.4 | 629.9 | 758.9 | 281.3 | 332.9 | 339.8 | 320.8 | 275.1 | 324.6 | 334.1 | 305
1005.2 | 729.2 | 469.3 | 187.72 | 219.4339 | 308.1 | 297.2 | 304.6 | 311.8 | 461.4 | 49.6 | 19.6 | 92.9 | 7.9 | 237.7 | 14.4 | 789 | 798 | 714.5 | 821.7 | 611.2 | 709.2 | 585 | 768 | 719.6 | 636.2 | 632.3 | 633 | 755.3 | 281.5 | 333.2 | 340.2 | 320.8 | 275.1 | 324.6 | 334.2 | 305.2
1006.2 | 730.2 | 469.3 | 187.72 | 219.4339 | 307.7 | 297.4 | 305.6 | 311.9 | 461.1 | 49.7 | 19.6 | 92.7 | 7.2 | 243 | 13.8 | 790.2 | 796.3 | 721.7 | 825 | 614.7 | 710.3 | 584.3 | 763.8 | 718.4 | 636.6 | 632 | 640.7 | 752.1 | 281.5 | 333.7 | 340.9 | 320.9 | 275.2 | 324.3 | 334.1 | 305.2
1007.2 | 731.2 | 469 | 187.6 | 219.2936 | 307.9 | 297.7 | 306.4 | 311.7 | 457.7 | 49.8 | 19.6 | 92.5 | 7.1 | 252.6 | 13.1 | 792.7 | 791.6 | 731.7 | 828.2 | 617.9 | 711.2 | 580.6 | 761 | 713.4 | 637.5 | 631.6 | 643.5 | 749.6 | 281.6 | 334.1 | 341.3 | 321.1 | 275.2 | 324 | 334.2 | 305.3
1008.2 | 732.2 | 470 | 188 | 219.7612 | 306.5 | 298 | 307.6 | 311.1 | 455.5 | 49.9 | 19.6 | 92.3 | 8.7 | 243.4 | 10.9 | 793.9 | 785.4 | 728.8 | 831 | 618.7 | 711.9 | 579.4 | 751.6 | 710.2 | 637.3 | 631.5 | 642.4 | 747.2 | 281.6 | 334.3 | 341.5 | 321.5 | 275.3 | 324 | 334.4 | 305.4
1009.2 | 733.2 | 470.2 | 188.08 | 219.8547 | 305.7 | 297.4 | 307.9 | 310.6 | 456.3 | 50 | 19.6 | 92.2 | 8.9 | 232.9 | 10.3 | 795.8 | 782.9 | 732.6 | 833.4 | 621.9 | 712.7 | 578.2 | 743 | 708.6 | 637.8 | 631.3 | 639.9 | 743.5 | 281.7 | 334.3 | 341.6 | 321.6 | 275.4 | 324 | 334.4 | 305.5
1010.2 | 734.2 | 470.4 | 188.16 | 219.9482 | 305.8 | 297.7 | 308.7 | 310 | 459.3 | 50.1 | 19.6 | 92 | 7.2 | 249.2 | 11.4 | 797.7 | 784.4 | 733.4 | 835.8 | 623.2 | 712.9 | 580.4 | 737.9 | 711.7 | 639.1 | 631.1 | 639.1 | 739.7 | 281.7 | 334.3 | 341.8 | 321.6 | 275.5 | 324 | 334.5 | 305.6
1011.2 | 735.2 | 470.2 | 188.08 | 219.8547 | 307.6 | 298.5 | 308.5 | 308.9 | 463.1 | 50.1 | 19.6 | 92 | 7.2 | 245.5 | 10.9 | 799.7 | 788.6 | 727.9 | 838.2 | 623.5 | 713.4 | 579.1 | 732 | 712.9 | 639 | 630.9 | 635.4 | 738.6 | 281.9 | 334.3 | 342.2 | 321.5 | 275.7 | 324.1 | 334.6 | 305.7
1012.2 | 736.2 | 470 | 188 | 219.7612 | 308.1 | 298.6 | 307.5 | 309.2 | 464.1 | 50.2 | 19.6 | 92.1 | 6.6 | 237.3 | 9.6 | 801 | 782.3 | 722 | 840.4 | 622.9 | 713.7 | 576.9 | 722.9 | 711.2 | 638.2 | 630.7 | 634 | 741.1 | 282.1 | 334.2 | 342.8 | 321.5 | 275.8 | 324.4 | 334.9 | 305.9
1013.2 | 737.2 | 469.8 | 187.92 | 219.6677 | 309.1 | 298.3 | 307.7 | 309.8 | 462.6 | 50.2 | 19.6 | 92.2 | 7.9 | 244 | 9.7 | 799.1 | 765.5 | 715.3 | 841 | 620.6 | 714 | 572.3 | 697.4 | 704.4 | 635.1 | 630.7 | 629.3 | 741.5 | 282.2 | 334 | 343 | 321.5 | 275.8 | 324.8 | 335.3 | 306.1
1014.2 | 738.2 | 469.4 | 187.76 | 219.4806 | 309.3 | 298.3 | 308 | 309.8 | 456.5 | 50.1 | 19.6 | 92.3 | 8 | 241.5 | 12.1 | 797.8 | 759.2 | 705.4 | 840.4 | 618.4 | 714.1 | 568.4 | 685 | 698.7 | 632.9 | 630.6 | 625.8 | 738.5 | 282.4 | 333.8 | 343.1 | 321.4 | 275.9 | 325.1 | 335.4 | 306.2
1015.2 | 739.2 | 470 | 188 | 219.7612 | 309.7 | 298.7 | 308.2 | 309.5 | 454.8 | 50.1 | 19.6 | 92.3 | 7.8 | 238 | 12.8 | 796.5 | 763.6 | 694.7 | 839.9 | 617.7 | 714.3 | 566.7 | 678.6 | 696.4 | 631.8 | 630.7 | 622.4 | 737.3 | 282.6 | 333.6 | 343.1 | 321.3 | 276 | 325.3 | 335.7 | 306.3
1016.2 | 740.2 | 469.9 | 187.96 | 219.7144 | 308.7 | 298.8 | 307.9 | 309.4 | 455.8 | 50.1 | 19.6 | 92.3 | 7.7 | 248 | 14.2 | 794.4 | 753.5 | 679.8 | 838.5 | 614.8 | 714.4 | 566.6 | 665.4 | 695 | 630.7 | 630.7 | 616.2 | 734.8 | 282.9 | 333.6 | 343.5 | 321.3 | 276.1 | 326 | 335.7 | 306.6
1017.2 | 741.2 | 469.9 | 187.96 | 219.7144 | 309.9 | 298.3 | 308.6 | 309.8 | 458.3 | 50.2 | 19.6 | 92.4 | 9.1 | 240.8 | 15.8 | 790.8 | 737.6 | 670.2 | 835.2 | 611.9 | 714.6 | 562.5 | 638.3 | 687.3 | 626.7 | 630.7 | 610.3 | 729.7 | 283 | 333.5 | 344 | 321.2 | 276.1 | 326.7 | 336.1 | 306.9
1018.2 | 742.2 | 470.2 | 188.08 | 219.8547 | 310.5 | 296.9 | 309.7 | 310.7 | 457.3 | 50.2 | 19.6 | 92.5 | 7.1 | 244 | 17 | 787.3 | 724 | 654.8 | 831.4 | 609.2 | 714.4 | 558.9 | 618.7 | 680.9 | 623.7 | 630.6 | 605.3 | 726.8 | 283.1 | 333.5 | 344.5 | 321.3 | 276.2 | 327.1 | 336.4 | 307.1
1019.2 | 743.2 | 469.8 | 187.92 | 219.6677 | 311 | 296.2 | 310 | 311.4 | 454.7 | 50.3 | 19.6 | 92.7 | 6.1 | 243.4 | 15.7 | 784 | 718.4 | 647.5 | 827.2 | 607.1 | 714.1 | 555.9 | 604.1 | 676.4 | 621.3 | 630.8 | 600.3 | 723 | 283.3 | 333.6 | 345.5 | 321.5 | 276.3 | 327.7 | 337.2 | 307.4
1020.2 | 744.2 | 470 | 188 | 219.7612 | 315.7 | 297.3 | 311.3 | 311.5 | 454.7 | 50.3 | 19.6 | 92.9 | 7.5 | 235.9 | 15.3 | 780.4 | 707.7 | 638.7 | 822.4 | 604.7 | 713.9 | 553.4 | 588.7 | 672.1 | 618.3 | 630.8 | 595.6 | 718.8 | 283.4 | 333.7 | 346.2 | 321.6 | 276.4 | 328.3 | 338.2 | 307.6
1021.2 | 745.2 | 470.2 | 188.08 | 219.8547 | 316.8 | 299.1 | 313 | 311.4 | 454.8 | 50.3 | 19.6 | 93.1 | 7.1 | 235.2 | 15.3 | 777.8 | 696.1 | 631.8 | 817.5 | 602.4 | 713.4 | 551.8 | 578.1 | 668.8 | 615.9 | 630.7 | 592.2 | 716 | 283.5 | 333.9 | 346.5 | 321.7 | 276.4 | 328.8 | 338.6 | 307.8
1022.2 | 746.2 | 470.1 | 188.04 | 219.8079 | 317.4 | 299.6 | 314 | 311.9 | 452.9 | 50.3 | 19.6 | 93.2 | 8.8 | 243.9 | 16.1 | 774.9 | 683.9 | 620.3 | 812.3 | 599.4 | 712.8 | 547.9 | 564.5 | 663.4 | 612.9 | 630.5 | 588.1 | 713.1 | 283.6 | 334.1 | 346.8 | 321.7 | 276.3 | 329.9 | 339.1 | 308
1023.2 | 747.2 | 468.7 | 187.48 | 219.1533 | 317.6 | 300.1 | 315.5 | 312.7 | 449.9 | 50.4 | 19.6 | 93.4 | 9.2 | 244.1 | 17 | 774.2 | 681.3 | 621.1 | 808.2 | 599.3 | 712 | 548 | 565.3 | 662.6 | 611.5 | 630.4 | 584.7 | 713.2 | 283.7 | 334.3 | 346.7 | 321.7 | 276.3 | 330.7 | 339.4 | 308.3
1024.2 | 748.2 | 468.6 | 187.44 | 219.1066 | 319 | 300.9 | 316.2 | 312.5 | 452.1 | 50.5 | 19.6 | 93.6 | 6.4 | 244.8 | 16.3 | 772.7 | 679.3 | 616.4 | 804.4 | 596.9 | 711.2 | 548.2 | 562.7 | 662 | 609.8 | 630.3 | 580.8 | 713.6 | 283.7 | 334.3 | 346.8 | 321.7 | 276.4 | 331.2 | 339.6 | 308.5
1025.2 | 749.2 | 468.2 | 187.28 | 218.9195 | 321.6 | 301.7 | 316.1 | 311.7 | 453.3 | 50.6 | 19.6 | 93.6 | 7.1 | 241.9 | 17 | 770.4 | 680.5 | 605.2 | 800.3 | 593.9 | 710.4 | 548 | 561.8 | 661 | 608.1 | 630 | 576.9 | 712.2 | 283.8 | 334.5 | 347.1 | 321.7 | 276.4 | 332 | 339.9 | 308.7
1026.2 | 750.2 | 468.4 | 187.36 | 219.013 | 321.2 | 301.6 | 316.6 | 312.2 | 455 | 50.7 | 19.6 | 93.8 | 7.7 | 239.1 | 16.6 | 769 | 682.6 | 601.3 | 796.7 | 591.8 | 709.7 | 549 | 559.1 | 660.9 | 607.3 | 630.1 | 573.2 | 708.5 | 283.9 | 334.5 | 347.2 | 321.7 | 276.4 | 332.5 | 340.7 | 309
1027.2 | 751.2 | 468.1 | 187.24 | 218.8728 | 321.2 | 301.1 | 318 | 312.3 | 458.7 | 50.8 | 19.6 | 94 | 7.1 | 248.4 | 15.5 | 769.2 | 693.1 | 614.2 | 793.7 | 595 | 709 | 550.8 | 568.8 | 662.9 | 607.9 | 630 | 573.1 | 705.3 | 284 | 334.4 | 347.4 | 321.7 | 276.6 | 332.9 | 341.3 | 309.3
1028.2 | 752.2 | 469.3 | 187.72 | 219.4339 | 322.9 | 301.1 | 318.7 | 312.2 | 458 | 50.8 | 19.5 | 94 | 6.1 | 240.5 | 15.2 | 771.6 | 710.5 | 637.9 | 792.9 | 600.3 | 708.4 | 551.1 | 600.4 | 664.8 | 609.5 | 629.8 | 579.5 | 704.1 | 284.1 | 334.4 | 347.5 | 321.8 | 276.7 | 333.3 | 341.6 | 309.4
1029.2 | 753.2 | 469.2 | 187.68 | 219.3871 | 322.7 | 302.3 | 318.7 | 311.8 | 455 | 50.9 | 19.5 | 93.8 | 4.7 | 237.7 | 15 | 773.9 | 725.7 | 658.3 | 793 | 604.5 | 707.8 | 556.1 | 634.3 | 673.3 | 613 | 629.2 | 591.3 | 703.6 | 284.3 | 334.6 | 347.6 | 322 | 276.7 | 333.2 | 341.6 | 309.5
1030.2 | 754.2 | 470 | 188 | 219.7612 | 321.5 | 301.1 | 319.2 | 311.6 | 457.6 | 51 | 19.6 | 93.7 | 5.1 | 236.3 | 14.9 | 776.3 | 731 | 677.3 | 793.7 | 607.5 | 707.6 | 558.6 | 655.1 | 678.1 | 615.1 | 628.8 | 602.3 | 703.7 | 284.4 | 334.9 | 347.7 | 322.3 | 276.8 | 333 | 341.5 | 309.6
1031.2 | 755.2 | 469.4 | 187.76 | 219.4806 | 321.8 | 300.1 | 320.2 | 311.5 | 461.2 | 51 | 19.5 | 93.6 | 6.4 | 221.8 | 13.6 | 778.3 | 732.4 | 687.2 | 794.6 | 610.9 | 707.5 | 559.5 | 667 | 678.6 | 616.9 | 628.1 | 613.7 | 702.7 | 284.7 | 335.3 | 347.9 | 322.7 | 277 | 333.1 | 341.5 | 309.7
1032.2 | 756.2 | 469.6 | 187.84 | 219.5741 | 322.9 | 300.2 | 321.1 | 311.4 | 464.1 | 51.1 | 19.5 | 93.5 | 5.7 | 230.8 | 12.1 | 779.2 | 725.2 | 687.2 | 796.3 | 611 | 707.3 | 558.3 | 664.6 | 676.2 | 615.8 | 627.6 | 617.6 | 703.1 | 284.9 | 335.8 | 348.1 | 323.1 | 277.2 | 333 | 341.7 | 309.7
1033.2 | 757.2 | 469.6 | 187.84 | 219.5741 | 322.6 | 300.2 | 321.5 | 311.5 | 466.3 | 51.2 | 19.5 | 93.4 | 5.8 | 221.3 | 10.2 | 781.2 | 733.9 | 702.2 | 797.6 | 614.7 | 707 | 560.1 | 677.2 | 679.8 | 617 | 627.4 | 625.8 | 700.8 | 285.1 | 336.1 | 348.2 | 323.2 | 277.3 | 333.1 | 342 | 309.8
1034.2 | 758.2 | 469.6 | 187.84 | 219.5741 | 324.8 | 300.3 | 321.8 | 312.1 | 471.3 | 51.1 | 19.5 | 93.4 | 6.5 | 244.6 | 9.3 | 782.9 | 739.6 | 712.4 | 799.6 | 618.1 | 707 | 563.4 | 691.9 | 685.4 | 619.7 | 627.1 | 633.7 | 698.2 | 285.3 | 336.5 | 348.4 | 323.4 | 277.4 | 332.9 | 342.1 | 309.8
1035.2 | 759.2 | 469.9 | 187.96 | 219.7144 | 325.6 | 300 | 321.8 | 311.9 | 473.5 | 51 | 19.5 | 93.3 | 8 | 234.2 | 10.1 | 782.7 | 736.1 | 726 | 800.7 | 621 | 707.2 | 562.5 | 687.2 | 681.4 | 618.3 | 626.6 | 636.6 | 696.1 | 285.4 | 337 | 349.1 | 323.6 | 277.6 | 332.8 | 342.3 | 309.9
1036.2 | 760.2 | 469.4 | 187.76 | 219.4806 | 325.9 | 300.7 | 321.8 | 312.1 | 473.6 | 50.8 | 19.5 | 93.2 | 6.6 | 236.4 | 11 | 783.4 | 734.5 | 735.6 | 801.9 | 623 | 707.1 | 561.2 | 688 | 679.8 | 617.6 | 626.1 | 639.9 | 695.4 | 285.6 | 337.7 | 349.9 | 323.9 | 277.7 | 332.9 | 342.5 | 310
1037.2 | 761.2 | 468.2 | 187.28 | 218.9195 | 327.5 | 301.8 | 322.3 | 311.8 | 474.7 | 50.7 | 19.5 | 93 | 4.8 | 245 | 11.9 | 784.6 | 735.4 | 738.7 | 802.9 | 623.3 | 707 | 559.9 | 689.2 | 678.8 | 617.5 | 625.6 | 641 | 692.5 | 285.7 | 338.3 | 350.3 | 324.2 | 277.8 | 332.8 | 342.7 | 310.1
1038.2 | 762.2 | 469.1 | 187.64 | 219.3403 | 328.8 | 302 | 323.2 | 312.1 | 474 | 50.6 | 19.5 | 92.8 | 5.8 | 242.6 | 13.5 | 784.4 | 736.5 | 733.5 | 803.9 | 624.8 | 706.8 | 559.3 | 683.3 | 677.7 | 616.6 | 625.1 | 640 | 690.9 | 285.8 | 339 | 350.5 | 324.5 | 278 | 332.9 | 342.7 | 310.2
1039.2 | 763.2 | 468.7 | 187.48 | 219.1533 | 329 | 301.9 | 323.8 | 313.1 | 470.4 | 50.5 | 19.5 | 92.7 | 6.7 | 212.4 | 13.8 | 785.2 | 744.1 | 722.4 | 805 | 624.9 | 706.4 | 559.7 | 681.4 | 678.4 | 616.7 | 624.6 | 638.4 | 694.7 | 285.9 | 339.5 | 350.9 | 324.7 | 278.1 | 333.2 | 343.1 | 310.3
1040.2 | 764.2 | 467.9 | 187.16 | 218.7793 | 330.3 | 302.1 | 324.5 | 313.7 | 469.5 | 50.5 | 19.5 | 92.7 | 6.8 | 236.4 | 11.2 | 786.4 | 749.5 | 716.6 | 807.1 | 625.1 | 705.9 | 563.5 | 684.7 | 684.1 | 619 | 624.4 | 635.7 | 698.4 | 286.1 | 339.9 | 351.1 | 324.6 | 278.2 | 333.4 | 343.4 | 310.5
1041.2 | 765.2 | 468.6 | 187.44 | 219.1066 | 332.6 | 302.5 | 324 | 314 | 467.7 | 50.6 | 19.5 | 92.8 | 6 | 249.4 | 10 | 784.6 | 742.2 | 697.9 | 808.3 | 622.5 | 705.6 | 562.8 | 671.6 | 683 | 616.9 | 624.1 | 629.2 | 705.4 | 286.3 | 340 | 351.2 | 324.5 | 278.4 | 333.4 | 343 | 310.7
1042.2 | 766.2 | 469.6 | 187.84 | 219.5741 | 332.5 | 301.9 | 322.6 | 314 | 466.8 | 50.6 | 19.5 | 92.9 | 6.8 | 249.6 | 12.3 | 780.5 | 733.4 | 677.6 | 807.7 | 619.1 | 705.2 | 561.6 | 650.3 | 681 | 615.1 | 623.9 | 620.3 | 710.8 | 286.5 | 340 | 351.3 | 324.4 | 278.4 | 333.6 | 342.9 | 310.9
1043.2 | 767.2 | 468.7 | 187.48 | 219.1533 | 331.9 | 301.5 | 322.3 | 313.2 | 466.9 | 50.6 | 19.5 | 92.9 | 6.2 | 260.3 | 13.1 | 776.5 | 724 | 662.1 | 805.8 | 615.1 | 704.7 | 559.3 | 632.6 | 676.7 | 613.1 | 623.9 | 612.1 | 712.6 | 286.7 | 339.9 | 352.1 | 324.3 | 278.5 | 333.7 | 343 | 311.1
1044.2 | 768.2 | 467.7 | 187.08 | 218.6857 | 330.9 | 301.3 | 323.2 | 312.5 | 468.9 | 50.6 | 19.5 | 93.1 | 6.3 | 266.6 | 11.4 | 774.8 | 731.1 | 659.2 | 803.6 | 614.7 | 704.1 | 560.4 | 629.9 | 678.5 | 613 | 623.9 | 605.5 | 711.5 | 286.9 | 339.7 | 351.9 | 324.3 | 278.6 | 333.7 | 343.1 | 311.3
1045.2 | 769.2 | 467.8 | 187.12 | 218.7325 | 329.7 | 300.5 | 323.8 | 312.6 | 472 | 50.5 | 19.5 | 93.3 | 6.3 | 264.6 | 11.5 | 774.7 | 749 | 656.6 | 801.9 | 615.3 | 703.7 | 566.9 | 641.6 | 685.5 | 616.6 | 623.8 | 599.2 | 709.7 | 287.1 | 339.5 | 351.9 | 324.2 | 278.8 | 333.8 | 343.3 | 311.4
1046.2 | 770.2 | 467.9 | 187.16 | 218.7793 | 329.6 | 301.1 | 324.6 | 313.7 | 471.9 | 50.4 | 19.5 | 93.6 | 6.1 | 266.3 | 13.7 | 775.5 | 760.8 | 656.2 | 801.1 | 615.4 | 703.6 | 573 | 649.5 | 692.4 | 618.7 | 623.7 | 594.4 | 709.5 | 287.3 | 339.4 | 352 | 324.2 | 278.9 | 334 | 343.2 | 311.6
1047.2 | 771.2 | 470.2 | 188.08 | 219.8547 | 330.5 | 302.1 | 325.7 | 314.4 | 475.1 | 50.4 | 19.5 | 93.7 | 6.3 | 243.3 | 14.1 | 777.2 | 768.5 | 663.6 | 800.8 | 618.2 | 703.6 | 578.2 | 659.1 | 697.9 | 621.4 | 623.6 | 594 | 710.2 | 287.4 | 339.4 | 352.3 | 324.2 | 279 | 334 | 343.2 | 311.7
1048.2 | 772.2 | 470.2 | 188.08 | 219.8547 | 331.7 | 301.6 | 326.6 | 314.6 | 473 | 50.4 | 19.5 | 93.7 | 6 | 275.2 | 11.8 | 780.7 | 769.7 | 683 | 801.4 | 623 | 703.8 | 581 | 683.1 | 700.3 | 623.5 | 623.2 | 603.5 | 710.5 | 287.6 | 339.5 | 352.4 | 324.3 | 279.2 | 333.8 | 343.1 | 311.9
1049.2 | 773.2 | 468.2 | 187.28 | 218.9195 | 331.4 | 300.9 | 327 | 314.2 | 475.9 | 50.5 | 19.5 | 93.6 | 5.5 | 273 | 11.2 | 784.6 | 760.4 | 700.3 | 802.8 | 624.5 | 704.3 | 579.7 | 700.3 | 697.4 | 623.8 | 622.6 | 619.4 | 708.3 | 287.8 | 339.9 | 352.5 | 324.7 | 279.4 | 333.8 | 343.1 | 311.9
1050.2 | 774.2 | 467.8 | 187.12 | 218.7325 | 330.4 | 300.2 | 327.4 | 313.3 | 482 | 50.6 | 19.5 | 93.5 | 5.8 | 277.8 | 13.6 | 787.7 | 750.6 | 715.8 | 804.2 | 627.2 | 704.9 | 578.1 | 711.1 | 695.5 | 624.7 | 622.6 | 633.9 | 704.2 | 287.9 | 340.5 | 352.5 | 325.2 | 279.5 | 334.1 | 343.4 | 312
1051.2 | 775.2 | 468.5 | 187.4 | 219.0598 | 331.2 | 300.9 | 327.6 | 313.1 | 492.2 | 50.6 | 19.5 | 93.5 | 5.5 | 262.3 | 15.2 | 786.6 | 735.2 | 713.9 | 804.8 | 626 | 705.4 | 573.9 | 695.5 | 688.3 | 622.8 | 622.3 | 642.4 | 698.2 | 288.1 | 341 | 352.7 | 325.7 | 279.6 | 334.5 | 344.8 | 312.1
1052.2 | 776.2 | 468.7 | 187.48 | 219.1533 | 334.3 | 302.3 | 327.6 | 314.2 | 504.4 | 50.6 | 19.5 | 93.5 | 6 | 257.9 | 15.3 | 784.3 | 720.6 | 703.1 | 804.3 | 623.3 | 705.8 | 569 | 690.8 | 683.7 | 621.6 | 621.7 | 646.3 | 691.9 | 288.2 | 341.8 | 353.5 | 326.1 | 279.8 | 334.9 | 346.7 | 312.1
1053.2 | 777.2 | 468.7 | 187.48 | 219.1533 | 334.4 | 304.6 | 327.7 | 316.4 | 511.2 | 50.6 | 19.5 | 93.6 | 5.8 | 257.9 | 13.7 | 780.8 | 706.7 | 695.5 | 803 | 620.6 | 705.9 | 565.2 | 677.3 | 680.5 | 619.1 | 621.4 | 647.7 | 685.7 | 288.5 | 342.8 | 354.5 | 326.6 | 279.9 | 335.1 | 348.1 | 312.4
1054.2 | 778.2 | 468.7 | 187.48 | 219.1533 | 333.6 | 306.9 | 329.1 | 318.9 | 515.8 | 50.6 | 19.5 | 93.6 | 6.4 | 254.4 | 12.5 | 777 | 693.2 | 689.8 | 800.5 | 618 | 705.9 | 560.4 | 661 | 675.4 | 616.5 | 621.5 | 648.5 | 679.6 | 288.6 | 343.6 | 355.6 | 327 | 280 | 334.8 | 348.1 | 312.5
1055.2 | 779.2 | 468.2 | 187.28 | 218.9195 | 335.8 | 307.8 | 329.7 | 321 | 511.6 | 50.7 | 19.5 | 93.7 | 6 | 258.1 | 12.3 | 774.8 | 683.3 | 680.3 | 797.8 | 616 | 705.7 | 556.4 | 647.8 | 669.9 | 614.1 | 621.4 | 644.8 | 677.9 | 288.8 | 344.3 | 356.8 | 327.3 | 280.2 | 334.6 | 350 | 312.5
1056.2 | 780.2 | 468.9 | 187.56 | 219.2468 | 338.3 | 307.9 | 330.1 | 323.4 | 502.8 | 50.7 | 19.5 | 93.8 | 6.3 | 254 | 11.5 | 774.8 | 677.7 | 675.9 | 795.5 | 614.7 | 705.3 | 554.3 | 650.3 | 667.2 | 612.6 | 621.2 | 641 | 682.8 | 288.9 | 344.7 | 357.2 | 327.3 | 280.4 | 334.6 | 351 | 312.7
1057.2 | 781.2 | 469.2 | 187.68 | 219.3871 | 339.7 | 308 | 330.6 | 324.6 | 496.9 | 50.7 | 19.5 | 93.8 | 6.7 | 258.7 | 11.5 | 775.9 | 684.8 | 671.7 | 794.7 | 614.6 | 704.9 | 554.3 | 660.4 | 668 | 613 | 620.9 | 636.9 | 690.6 | 289 | 344.7 | 357.3 | 327.2 | 280.6 | 335 | 351.4 | 312.9
1058.2 | 782.2 | 466.6 | 186.64 | 218.1714 | 339.1 | 307.6 | 330 | 324.6 | 491.8 | 50.8 | 19.5 | 93.9 | 6.7 | 244.4 | 11.1 | 774.7 | 687 | 662.5 | 794.1 | 613 | 704.3 | 554.1 | 650 | 667.3 | 611.4 | 620.5 | 631.8 | 694.7 | 289.1 | 344.7 | 357.3 | 327.1 | 280.7 | 335.2 | 351.3 | 313.2
1059.2 | 783.2 | 468.7 | 187.48 | 219.1533 | 339.7 | 306.8 | 329.2 | 324.6 | 487.7 | 50.8 | 19.5 | 93.8 | 6.9 | 251.9 | 11.5 | 772.8 | 685.4 | 657.2 | 793.2 | 611 | 703.5 | 551.5 | 644.2 | 665.5 | 610.2 | 620.5 | 627.7 | 700.6 | 289.3 | 344.6 | 356.9 | 327.1 | 280.9 | 335.1 | 350.9 | 313.3
1060.2 | 784.2 | 469 | 187.6 | 219.2936 | 340.2 | 306.3 | 328.7 | 324.1 | 483.5 | 50.9 | 19.5 | 93.8 | 7.3 | 248.9 | 10.8 | 773 | 708.8 | 655.5 | 793 | 610.7 | 702.8 | 556.5 | 661.6 | 673.9 | 614.4 | 620.5 | 624.8 | 704.4 | 289.4 | 344.5 | 356.5 | 326.9 | 281 | 335.1 | 351 | 313.5
1061.2 | 785.2 | 468.4 | 187.36 | 219.013 | 339.1 | 306.9 | 328.7 | 323.2 | 483.2 | 51 | 19.4 | 93.7 | 8.7 | 246.6 | 9.4 | 772.5 | 718.1 | 654.5 | 792.7 | 610.5 | 702.5 | 559.4 | 660.5 | 677.6 | 614.6 | 620.6 | 620.5 | 706.4 | 289.6 | 344.3 | 356.4 | 326.8 | 281.1 | 335.1 | 350.8 | 313.7
1062.2 | 786.2 | 468.9 | 187.56 | 219.2468 | 338.1 | 306.8 | 328.5 | 322.4 | 479.3 | 51.1 | 19.4 | 93.7 | 7.5 | 242.1 | 9.3 | 773.5 | 720.4 | 655.5 | 792.7 | 610.3 | 702.1 | 559.3 | 663.1 | 679.7 | 614.4 | 620.6 | 619.5 | 709.8 | 289.8 | 344.2 | 356.5 | 326.8 | 281.2 | 334.9 | 350.9 | 313.8
1063.2 | 787.2 | 468.7 | 187.48 | 219.1533 | 337.5 | 306.6 | 328.8 | 322.3 | 473.5 | 51.2 | 19.4 | 93.8 | 6.8 | 233.4 | 9.2 | 776.3 | 719.6 | 664.7 | 793.3 | 611.2 | 701.9 | 560.6 | 684.3 | 681.8 | 615.9 | 620.5 | 627.5 | 711 | 289.9 | 344.3 | 356.3 | 326.9 | 281.4 | 334.6 | 350.8 | 313.9
1064.2 | 788.2 | 468.5 | 187.4 | 219.0598 | 337.9 | 306.6 | 328.3 | 322 | 475.7 | 51.2 | 19.4 | 93.9 | 5.2 | 250.3 | 8.8 | 779.6 | 733.3 | 672.2 | 795.2 | 613.6 | 701.9 | 563.8 | 695.6 | 687.7 | 619.2 | 620.5 | 630.7 | 713.3 | 290.1 | 344.5 | 356 | 327.1 | 281.4 | 334.5 | 350.4 | 314
1065.2 | 789.2 | 468.9 | 187.56 | 219.2468 | 336.5 | 306.3 | 328 | 321.4 | 473.3 | 51.3 | 19.4 | 93.9 | 5.3 | 239.1 | 8.8 | 780 | 746.2 | 670.4 | 797.2 | 613.9 | 701.6 | 567 | 695.7 | 691.4 | 621.6 | 620.3 | 626.7 | 712.2 | 290.3 | 344.2 | 355.9 | 327.3 | 281.4 | 334.7 | 349.9 | 314.2
1066.2 | 790.2 | 469.5 | 187.8 | 219.5274 | 335.8 | 306.4 | 327.9 | 320.7 | 472.2 | 51.4 | 19.4 | 93.9 | 6.3 | 239.9 | 10.1 | 779.8 | 750 | 664.8 | 798.3 | 613.3 | 701.4 | 567.2 | 688.1 | 688.1 | 621 | 620.2 | 619.1 | 711.2 | 290.5 | 344.1 | 355.8 | 327.3 | 281.7 | 335.1 | 349.6 | 314.4
1067.2 | 791.2 | 469.7 | 187.88 | 219.6209 | 336.4 | 306 | 327.4 | 320.2 | 476 | 51.4 | 19.4 | 93.9 | 6.3 | 228.1 | 8.7 | 777.3 | 744.8 | 656.8 | 798.5 | 610.7 | 701.1 | 567 | 672.8 | 687.4 | 621 | 620.1 | 612.3 | 710.3 | 290.7 | 344.1 | 355.9 | 327.3 | 281.9 | 335.4 | 349.6 | 314.7
1068.2 | 792.2 | 470 | 188 | 219.7612 | 337.9 | 305.5 | 327.3 | 319.8 | 474.5 | 51.5 | 19.4 | 94 | 5.9 | 247.5 | 9.7 | 775.8 | 743 | 652.4 | 798.4 | 609.7 | 700.6 | 564.8 | 665.3 | 684.8 | 619.3 | 619.7 | 607.7 | 710.6 | 290.9 | 344 | 356.1 | 327.3 | 282.1 | 335.7 | 350 | 314.8
1069.2 | 793.2 | 470 | 188 | 219.7612 | 338.4 | 305.3 | 327.9 | 319 | 478 | 51.5 | 19.4 | 94.1 | 8.8 | 254.6 | 10 | 772.1 | 733.7 | 635.5 | 797.3 | 607.1 | 700.2 | 563.6 | 652.4 | 682.7 | 618.2 | 619.7 | 601.6 | 706.9 | 291.2 | 344 | 355.9 | 327.3 | 282.3 | 336.7 | 350.8 | 315.2
1070.2 | 794.2 | 469.9 | 187.96 | 219.7144 | 339.3 | 305.1 | 328.7 | 319.1 | 480.1 | 51.5 | 19.4 | 94.1 | 8.9 | 231.1 | 10.7 | 768 | 721 | 622.1 | 794.8 | 604.1 | 699.8 | 559 | 631 | 675 | 615.1 | 619.5 | 596.1 | 701.4 | 291.4 | 343.9 | 356 | 327.3 | 282.4 | 338.6 | 351.9 | 315.7
1071.2 | 795.2 | 469.2 | 187.68 | 219.3871 | 340.4 | 304.5 | 329.7 | 320 | 479.5 | 51.5 | 19.4 | 94.1 | 8.1 | 241.7 | 13.4 | 765.6 | 725.3 | 626.9 | 792 | 604.4 | 699.2 | 556.6 | 629.6 | 674.5 | 614.8 | 619.3 | 593.2 | 695.3 | 291.5 | 344.1 | 356.5 | 327.3 | 282.5 | 340 | 352.7 | 316.2
1072.2 | 796.2 | 469.6 | 187.84 | 219.5741 | 341.6 | 304.6 | 330.7 | 320.8 | 477 | 51.4 | 19.4 | 94.1 | 6.2 | 240.2 | 18.6 | 767.8 | 742.6 | 648.9 | 790.1 | 608.4 | 698.8 | 562.9 | 649.8 | 682.5 | 619.2 | 619.1 | 599 | 690.3 | 291.7 | 344.2 | 356.6 | 327.5 | 282.6 | 340.2 | 352.9 | 316.4
1073.2 | 797.2 | 468.9 | 187.56 | 219.2468 | 341.6 | 305.2 | 331.5 | 321.2 | 474.6 | 51.4 | 19.4 | 94.1 | 6.3 | 251.1 | 20.8 | 771.5 | 755.5 | 664 | 790.5 | 614 | 698.7 | 567 | 675.6 | 689.5 | 623.4 | 619 | 605.8 | 687.2 | 292 | 344.5 | 356.6 | 327.7 | 282.8 | 340.2 | 352.6 | 316.5
1074.2 | 798.2 | 470.3 | 188.12 | 219.9014 | 341 | 306.5 | 331.8 | 321.2 | 474.5 | 51.3 | 19.4 | 94 | 5.4 | 250.3 | 18.2 | 771.9 | 763.2 | 670.5 | 790.7 | 615.6 | 698.5 | 570.8 | 681.7 | 695.5 | 625.9 | 618.6 | 602.6 | 683.9 | 292.1 | 344.4 | 356.5 | 327.8 | 282.9 | 340.4 | 352.4 | 316.7
1075.2 | 799.2 | 468.3 | 187.32 | 218.9663 | 340.8 | 307.1 | 332.1 | 321.1 | 474.6 | 51.3 | 19.4 | 93.9 | 6.3 | 251.2 | 17.3 | 773.6 | 771 | 690.7 | 791.5 | 618.1 | 698.4 | 574.9 | 687.4 | 700.5 | 627.3 | 618.2 | 605.8 | 681.2 | 292.2 | 344.3 | 356.2 | 327.9 | 283 | 340.6 | 352.6 | 316.8
1076.2 | 800.2 | 469.6 | 187.84 | 219.5741 | 341.6 | 307 | 331.9 | 320.6 | 474.3 | 51.2 | 19.4 | 93.9 | 5.7 | 252.2 | 16.2 | 777.2 | 781.1 | 714 | 792.8 | 622.3 | 698.5 | 577.1 | 705.5 | 705.2 | 629.7 | 617.8 | 619 | 678.7 | 292.4 | 344.2 | 355.9 | 328 | 283.2 | 341 | 353.4 | 317
1077.2 | 801.2 | 468.8 | 187.52 | 219.2001 | 343.3 | 307.8 | 330.8 | 320.7 | 474.7 | 51.3 | 19.4 | 94 | 6.3 | 239.9 | 15.1 | 779.8 | 792 | 710.1 | 794.8 | 623.2 | 698.7 | 581.9 | 717.5 | 711.8 | 634.7 | 617.5 | 616.6 | 676.4 | 292.7 | 344 | 355.5 | 328.1 | 283.3 | 341.4 | 353.9 | 317.2
1078.2 | 802.2 | 468 | 187.2 | 218.826 | 343.9 | 309.8 | 329.3 | 321.5 | 477.7 | 51.4 | 19.4 | 94.2 | 6.2 | 244.6 | 14.6 | 780.3 | 805.2 | 710.7 | 796.7 | 625.3 | 699.3 | 585.5 | 714.8 | 713.7 | 635.8 | 616.9 | 611.7 | 675.3 | 292.9 | 343.8 | 355.6 | 328.1 | 283.4 | 341.8 | 354.1 | 317.5
1079.2 | 803.2 | 469.6 | 187.84 | 219.5741 | 344.9 | 311.5 | 328.6 | 321.8 | 481.1 | 51.4 | 19.4 | 94.4 | 7.4 | 246.2 | 13.5 | 780.6 | 813.1 | 710.1 | 798.3 | 626.1 | 699.7 | 584.8 | 716.8 | 714.8 | 637.5 | 616.7 | 614.4 | 676.3 | 293.1 | 343.7 | 355.9 | 328.2 | 283.5 | 341.9 | 354.4 | 317.6
1080.2 | 804.2 | 469.8 | 187.92 | 219.6677 | 345.5 | 312.4 | 328.9 | 320.9 | 479.9 | 51.3 | 19.4 | 94.6 | 7.6 | 254 | 11.4 | 782.7 | 814.6 | 718.5 | 799.9 | 628.3 | 700.2 | 584.3 | 726.9 | 713.8 | 638.8 | 616.6 | 620 | 679.4 | 293.2 | 343.5 | 356 | 328.3 | 283.8 | 341.9 | 354.5 | 317.7
1081.2 | 805.2 | 469.9 | 187.96 | 219.7144 | 345.9 | 312.5 | 329.1 | 320.5 | 478.5 | 51.4 | 19.4 | 94.6 | 8.2 | 270.4 | 10.4 | 785.3 | 822.3 | 716.1 | 802.1 | 629.5 | 700.8 | 585.1 | 728.8 | 715.6 | 642 | 616.2 | 619 | 683.1 | 293.4 | 343.4 | 355.9 | 328.5 | 284 | 342.2 | 354.6 | 317.9
1082.2 | 806.2 | 470.3 | 188.12 | 219.9014 | 346.6 | 312.1 | 329.1 | 321.1 | 475.7 | 51.4 | 19.4 | 94.4 | 7.1 | 253.9 | 12.4 | 788.4 | 825.5 | 717.4 | 805.4 | 631.8 | 701.4 | 586.1 | 735 | 716.2 | 644.4 | 616 | 621.7 | 689.4 | 293.6 | 343.3 | 355.8 | 328.6 | 284.3 | 342.6 | 355.3 | 318.1
1083.2 | 807.2 | 467.6 | 187.04 | 218.639 | 348.8 | 311.3 | 328.2 | 321.7 | 475.8 | 51.5 | 19.4 | 94.4 | 6.7 | 251.3 | 17 | 791.1 | 815.4 | 718.3 | 808.5 | 632.5 | 702 | 585.3 | 738.6 | 716.4 | 645.3 | 615.2 | 627.6 | 693.8 | 293.7 | 343.5 | 356 | 328.8 | 284.5 | 342.7 | 355.3 | 318.2
1084.2 | 808.2 | 466.4 | 186.56 | 218.0779 | 350.5 | 311.1 | 328 | 321.9 | 477.9 | 51.5 | 19.4 | 94.5 | 6.4 | 255.3 | 16.7 | 793 | 814.7 | 728.8 | 811.8 | 635.1 | 702.5 | 585.4 | 741.4 | 718.1 | 647.3 | 614.7 | 631.2 | 696.1 | 293.9 | 343.9 | 355.9 | 329.2 | 284.7 | 342.5 | 355.2 | 318.3
1085.2 | 809.2 | 467.8 | 187.12 | 218.7325 | 349.8 | 310.6 | 328.4 | 322.2 | 478 | 51.5 | 19.4 | 94.5 | 7.2 | 245.3 | 14.8 | 789.9 | 794 | 720.3 | 813 | 631.6 | 702.9 | 582.8 | 724.2 | 712.6 | 644.3 | 614.7 | 633 | 696.2 | 294.1 | 344.1 | 355.8 | 329.4 | 284.8 | 342.1 | 355.2 | 318.4
1086.2 | 810.2 | 468.9 | 187.56 | 219.2468 | 351.1 | 310.4 | 328.3 | 322.1 | 481.3 | 51.5 | 19.4 | 94.6 | 6.9 | 237.2 | 13.9 | 787.8 | 775.3 | 712.1 | 812.4 | 629.1 | 703.3 | 577 | 704.9 | 703.3 | 641.1 | 614.4 | 631.9 | 694.4 | 294.3 | 344.5 | 355.8 | 329.7 | 284.8 | 341.9 | 354.9 | 318.4
1087.2 | 811.2 | 471.4 | 188.56 | 220.4158 | 352.5 | 310.1 | 328.2 | 322.3 | 481.8 | 51.6 | 19.4 | 94.6 | 6.8 | 261.6 | 13.4 | 787.9 | 764.8 | 711.4 | 812 | 628.4 | 703.3 | 572.2 | 688.5 | 698.9 | 639.2 | 614.1 | 632.4 | 694.6 | 294.4 | 345 | 355.9 | 330 | 285 | 341.8 | 354.9 | 318.6
1088.2 | 812.2 | 471.1 | 188.44 | 220.2755 | 354.3 | 310.5 | 328.7 | 323.1 | 479 | 51.6 | 19.4 | 94.6 | 7.6 | 252.5 | 12.1 | 786.8 | 751.5 | 696 | 810.9 | 625.5 | 703.3 | 567.9 | 673.5 | 692.6 | 636.4 | 613.9 | 626.8 | 695.3 | 294.4 | 345.5 | 356.1 | 330.2 | 285.3 | 341.7 | 354.7 | 318.7
1089.2 | 813.2 | 470.7 | 188.28 | 220.0885 | 357.4 | 311.2 | 328.9 | 323.1 | 477.8 | 51.7 | 19.4 | 94.5 | 7.5 | 287 | 9.8 | 785.2 | 738.8 | 685.7 | 809 | 622.7 | 703.8 | 561.6 | 662.6 | 685.1 | 633.5 | 613.8 | 625.7 | 695.1 | 294.5 | 346.4 | 356.6 | 330.5 | 285.5 | 341.2 | 354.4 | 318.8
1090.2 | 814.2 | 470.4 | 188.16 | 219.9482 | 360 | 311.9 | 329.1 | 323.1 | 472.5 | 51.7 | 19.4 | 94.6 | 7.2 | 246.1 | 9.2 | 785.8 | 736.4 | 683.2 | 808 | 622.2 | 704.3 | 558.6 | 664.4 | 685.5 | 632.4 | 613.7 | 622.7 | 694.8 | 294.7 | 346.8 | 357.1 | 330.7 | 285.7 | 340.9 | 354.2 | 319
1091.2 | 815.2 | 470.5 | 188.2 | 219.995 | 361.4 | 312.4 | 329.8 | 323.6 | 468.7 | 51.7 | 19.4 | 94.8 | 6.9 | 256.8 | 11.3 | 786.3 | 739.9 | 688.2 | 807.4 | 623.3 | 704.7 | 557.2 | 661.4 | 686.2 | 631.3 | 613.6 | 619 | 693.2 | 295 | 346.8 | 357.5 | 330.6 | 285.8 | 341 | 353.9 | 319.2
1092.2 | 816.2 | 469.8 | 187.92 | 219.6677 | 361.1 | 312.3 | 329.4 | 323.8 | 467.8 | 51.8 | 19.4 | 94.9 | 6.5 | 258.8 | 14.4 | 785.6 | 735.4 | 682.1 | 806.5 | 621.6 | 705 | 557.3 | 656.4 | 686.5 | 630.4 | 613.5 | 616.3 | 692.1 | 295.3 | 346.8 | 358.2 | 330.5 | 286 | 341.1 | 354 | 319.3
1093.2 | 817.2 | 469.9 | 187.96 | 219.7144 | 361.6 | 312.1 | 329.2 | 323.5 | 465.8 | 51.9 | 19.4 | 95 | 5.9 | 261.8 | 13.1 | 784 | 732.7 | 684.3 | 805.3 | 620.3 | 705.3 | 555.9 | 652.2 | 684 | 628.4 | 613.3 | 614.9 | 691.4 | 295.6 | 346.8 | 358.5 | 330.6 | 286.2 | 341.1 | 354.3 | 319.4
1094.2 | 818.2 | 469.2 | 187.68 | 219.3871 | 361.2 | 311.4 | 329 | 323.1 | 464.7 | 51.9 | 19.4 | 95.1 | 6.2 | 248.8 | 11.1 | 784.3 | 734.4 | 694.6 | 804.4 | 621.7 | 705.2 | 556.8 | 662.1 | 687.7 | 628.9 | 613.1 | 616.9 | 692.3 | 295.7 | 346.7 | 358.2 | 330.7 | 286.2 | 341.2 | 354.7 | 319.6
1095.2 | 819.2 | 470.1 | 188.04 | 219.8079 | 361.5 | 311.2 | 328.7 | 322.6 | 462 | 52 | 19.4 | 95.3 | 6.8 | 261.3 | 11.5 | 784.2 | 732.4 | 701.9 | 804 | 622 | 705.1 | 554.4 | 659 | 687 | 627.6 | 613.2 | 616.4 | 693.2 | 295.8 | 346.3 | 357.9 | 330.6 | 286.4 | 341.7 | 354.8 | 319.8
1096.2 | 820.2 | 470.7 | 188.28 | 220.0885 | 361.7 | 311.8 | 328.6 | 322.7 | 461.8 | 52 | 19.4 | 95.5 | 7.3 | 252.5 | 12.3 | 783.8 | 738.8 | 706.1 | 803.9 | 623.9 | 704.3 | 553.7 | 655.7 | 686.1 | 627 | 613.1 | 613.6 | 693.1 | 295.8 | 345.9 | 357.4 | 330.5 | 286.5 | 342.1 | 354.8 | 320.1
1097.2 | 821.2 | 470.7 | 188.28 | 220.0885 | 363.4 | 311.9 | 328.3 | 323.2 | 460.9 | 52 | 19.4 | 95.6 | 8.3 | 247.8 | 13 | 786.4 | 755.5 | 701.5 | 804.6 | 624.8 | 703.3 | 557.1 | 665.7 | 692.1 | 628.9 | 612.5 | 613.4 | 693 | 295.8 | 345.7 | 357 | 330.4 | 286.5 | 342.3 | 354.8 | 320.2
1098.2 | 822.2 | 469.9 | 187.96 | 219.7144 | 364.5 | 310.7 | 328 | 323.2 | 462.4 | 52 | 19.4 | 95.7 | 7.9 | 260.7 | 11.4 | 789.2 | 763.9 | 703.3 | 805.5 | 627.4 | 702.3 | 558.8 | 675.9 | 694.7 | 630.1 | 612.4 | 618.3 | 692.8 | 295.9 | 346 | 357 | 330.5 | 286.6 | 342.5 | 355.4 | 320.3
1099.2 | 823.2 | 470 | 188 | 219.7612 | 364.7 | 309.6 | 328.3 | 323.6 | 462.5 | 52.1 | 19.3 | 95.8 | 7.3 | 247.7 | 12.4 | 787.5 | 763.3 | 697.9 | 805.3 | 626.9 | 701.1 | 557.9 | 664.7 | 690.8 | 627.9 | 612.2 | 615.8 | 693.1 | 296 | 345.9 | 356.8 | 330.6 | 286.7 | 342.9 | 355.7 | 320.5
1100.2 | 824.2 | 470.1 | 188.04 | 219.8079 | 366.8 | 309.4 | 328.4 | 324.3 | 461.2 | 52 | 19.3 | 95.8 | 7.7 | 240.5 | 14.7 | 787.2 | 761.3 | 690.7 | 805.1 | 627.4 | 699.6 | 556.8 | 653.6 | 686.8 | 626.8 | 612.2 | 611.6 | 692.6 | 296.2 | 345.6 | 356.6 | 330.5 | 286.8 | 343.2 | 356.4 | 320.7
1101.2 | 825.2 | 469.1 | 187.64 | 219.3403 | 370.7 | 309.6 | 328.2 | 324.8 | 463 | 52 | 19.3 | 95.8 | 6.9 | 257 | 14.9 | 786.8 | 767.2 | 680.1 | 804.9 | 626.2 | 698.2 | 558 | 649.3 | 687 | 626.5 | 612.1 | 606.9 | 691.6 | 296.5 | 345.5 | 356.9 | 330.5 | 286.9 | 343.5 | 356.7 | 321
1102.2 | 826.2 | 469.9 | 187.96 | 219.7144 | 372.1 | 310.6 | 327.7 | 324.7 | 463.4 | 51.9 | 19.3 | 95.7 | 7 | 236.3 | 13.4 | 786 | 758 | 679.1 | 804 | 625.5 | 697 | 557.2 | 642.9 | 685.7 | 625.1 | 612.1 | 602.6 | 690.9 | 296.6 | 345.4 | 356.8 | 330.6 | 287.1 | 343.7 | 356.7 | 321.2
1103.2 | 827.2 | 470.1 | 188.04 | 219.8079 | 373 | 310.7 | 327.3 | 324.4 | 460.2 | 51.9 | 19.3 | 95.7 | 6.2 | 213.8 | 13.1 | 784.9 | 744.6 | 672.3 | 803.1 | 624 | 696 | 554.8 | 633.2 | 681.2 | 622.6 | 611.9 | 599.5 | 688.3 | 296.8 | 345.5 | 356.9 | 330.7 | 287.2 | 343.8 | 356.8 | 321.4
1104.2 | 828.2 | 469.9 | 187.96 | 219.7144 | 374.8 | 310.4 | 327.3 | 323.6 | 459.8 | 52 | 19.3 | 95.7 | 6.6 | 228.5 | 12.7 | 784.4 | 741.6 | 668 | 802.9 | 623.4 | 695.1 | 552.5 | 627.6 | 679.6 | 621.2 | 612 | 595.7 | 687.3 | 297 | 345.5 | 357.1 | 330.7 | 287.3 | 344.1 | 357.3 | 321.6
1105.2 | 829.2 | 470 | 188 | 219.7612 | 377.1 | 310.2 | 327.5 | 322.6 | 459.7 | 52.1 | 19.3 | 95.8 | 6.6 | 208.7 | 10.5 | 782.9 | 740.3 | 669.7 | 802.6 | 622.8 | 694.3 | 550.8 | 628.8 | 678.2 | 619.9 | 612.4 | 594.9 | 686.6 | 297.2 | 345.6 | 356.9 | 330.7 | 287.5 | 344.3 | 357.1 | 321.8
1106.2 | 830.2 | 469.5 | 187.8 | 219.5274 | 379.4 | 310 | 327.7 | 322.5 | 457.3 | 52.1 | 19.3 | 96.1 | 6.7 | 233.3 | 8.7 | 781.1 | 735.7 | 669.7 | 801.2 | 620.8 | 693.6 | 548.8 | 624.9 | 675.7 | 618 | 612.4 | 594.9 | 686.4 | 297.4 | 345.5 | 356.6 | 330.7 | 287.7 | 344.6 | 357.1 | 322
1107.2 | 831.2 | 469.8 | 187.92 | 219.6677 | 381.1 | 309.3 | 327.6 | 322.7 | 457.1 | 52.1 | 19.3 | 96.2 | 5.7 | 232.2 | 9.3 | 779.5 | 733.3 | 666.7 | 799.8 | 619.9 | 692.9 | 548.4 | 624.9 | 675.9 | 616.8 | 612.1 | 593.5 | 686.1 | 297.5 | 345.3 | 356.4 | 330.8 | 287.9 | 345.6 | 357.3 | 322.2
1108.2 | 832.2 | 469.1 | 187.64 | 219.3403 | 381.4 | 308.3 | 327.8 | 322.5 | 455.4 | 52.2 | 19.3 | 96.2 | 5 | 239.8 | 9.4 | 778.3 | 730.3 | 656.9 | 798.4 | 617.9 | 692.3 | 547.6 | 621.2 | 673.3 | 615.8 | 612.1 | 592 | 686.6 | 297.6 | 345.3 | 356.4 | 330.9 | 288 | 345.9 | 357.3 | 322.4
1109.2 | 833.2 | 469.5 | 187.8 | 219.5274 | 382.2 | 308.7 | 328 | 321.6 | 454.5 | 52.2 | 19.3 | 96.3 | 5.8 | 239.1 | 9.8 | 775.9 | 731.6 | 649.8 | 796.6 | 616.1 | 691.7 | 546.2 | 613.6 | 670.2 | 614.4 | 611.9 | 586.1 | 685.1 | 297.7 | 345.2 | 356.4 | 331 | 288.1 | 346.1 | 357.3 | 322.6
1110.2 | 834.2 | 469.6 | 187.84 | 219.5741 | 383.7 | 309.1 | 328.1 | 321.4 | 458.2 | 52.3 | 19.3 | 96.4 | 7.4 | 234.1 | 9.6 | 772.7 | 725.5 | 645.2 | 793.7 | 613.7 | 691 | 545.9 | 610.1 | 667.3 | 612.6 | 611.8 | 583.8 | 681.2 | 298 | 345 | 356.2 | 331 | 288.2 | 346.4 | 357.6 | 323
1111.2 | 835.2 | 469.3 | 187.72 | 219.4339 | 385.6 | 309.1 | 328.2 | 322.5 | 461.8 | 52.3 | 19.3 | 96.6 | 7.8 | 221.4 | 8.2 | 773 | 730.1 | 656 | 791.9 | 614.6 | 690.7 | 545.4 | 632 | 668.5 | 613.4 | 611.8 | 594.1 | 679.6 | 298.1 | 344.9 | 356 | 331.2 | 288.3 | 346.2 | 357.6 | 323.2
1112.2 | 836.2 | 469 | 187.6 | 219.2936 | 390.1 | 308.2 | 327.7 | 322.6 | 463.2 | 52.3 | 19.3 | 96.8 | 8.4 | 223.1 | 7.4 | 776.2 | 737.5 | 682.9 | 791.4 | 617.4 | 690.2 | 546.3 | 651.6 | 673 | 614.9 | 611.7 | 602.1 | 678.4 | 298.3 | 345 | 356 | 331.3 | 288.5 | 346.2 | 357.5 | 323.3
1113.2 | 837.2 | 470.3 | 188.12 | 219.9014 | 390 | 308.6 | 327.6 | 322.1 | 464 | 52.3 | 19.3 | 97 | 7.2 | 212.1 | 8.6 | 780.6 | 748.2 | 705 | 792.4 | 622.6 | 689.7 | 548.4 | 668.7 | 679.9 | 617.6 | 611.5 | 606.8 | 680.2 | 298.6 | 345 | 356.3 | 331.5 | 288.8 | 346.4 | 357.5 | 323.5
1114.2 | 838.2 | 469.5 | 187.8 | 219.5274 | 393.1 | 309.8 | 328.2 | 322.5 | 465.7 | 52.3 | 19.3 | 97.1 | 6.5 | 253.1 | 8.1 | 784.6 | 755.3 | 724.2 | 794.3 | 628.6 | 689.3 | 551 | 681.5 | 684.9 | 618.6 | 611.1 | 615.6 | 680.6 | 298.8 | 345.3 | 356.5 | 331.6 | 288.9 | 346.7 | 357.4 | 323.6
1115.2 | 839.2 | 470.6 | 188.24 | 220.0417 | 393.4 | 310.4 | 328.4 | 322.2 | 464.9 | 52.3 | 19.3 | 97.2 | 5 | 252 | 10.5 | 788.4 | 765.8 | 742.9 | 797.4 | 635 | 689.1 | 554.5 | 704.9 | 691.5 | 621.5 | 610.9 | 628.4 | 678.5 | 299 | 345.5 | 356.6 | 331.9 | 289.1 | 346.9 | 357.2 | 323.8
1116.2 | 840.2 | 470.7 | 188.28 | 220.0885 | 393.2 | 311.3 | 328.1 | 321.7 | 465.4 | 52.4 | 19.3 | 97.4 | 6.5 | 255.2 | 11.3 | 790.4 | 778.2 | 738.8 | 800.8 | 636.6 | 689.1 | 559.7 | 717.3 | 700.5 | 624.3 | 610.5 | 630.2 | 676.2 | 299.2 | 345.6 | 356.8 | 332 | 289.2 | 346.8 | 357 | 324
1117.2 | 841.2 | 470.6 | 188.24 | 220.0417 | 394.7 | 311.9 | 328.3 | 321.9 | 464.9 | 52.4 | 19.3 | 97.5 | 6.6 | 219.6 | 9.8 | 789.3 | 783.8 | 730.1 | 803.5 | 637.7 | 689.1 | 564.1 | 711.2 | 701.4 | 625.6 | 610.1 | 622.4 | 673.4 | 299.6 | 345.7 | 357 | 332 | 289.4 | 346.6 | 356.8 | 324.1
1118.2 | 842.2 | 470.3 | 188.12 | 219.9014 | 399.2 | 312.4 | 328.4 | 322.4 | 463.4 | 52.4 | 19.3 | 97.6 | 6.4 | 241.5 | 10.1 | 788.3 | 782.8 | 713.7 | 805.6 | 637.5 | 688.9 | 564.8 | 702.5 | 702.9 | 624.7 | 609.6 | 616.6 | 675.1 | 299.8 | 345.8 | 357.1 | 332 | 289.6 | 346.3 | 357.2 | 324.2
1119.2 | 843.2 | 470.6 | 188.24 | 220.0417 | 401.9 | 313.2 | 328.9 | 322.8 | 464.4 | 52.3 | 19.3 | 97.5 | 7.1 | 258.1 | 10.7 | 786.8 | 763.3 | 701.4 | 806.5 | 634.7 | 688.6 | 560.6 | 682.4 | 695.9 | 621.9 | 609.2 | 612.4 | 676.9 | 299.8 | 346 | 357.2 | 332.2 | 289.8 | 346.6 | 357.1 | 324.3
1120.2 | 844.2 | 470.4 | 188.16 | 219.9482 | 400.5 | 314.1 | 329.4 | 323 | 463.3 | 52.3 | 19.3 | 97.4 | 7.8 | 244.3 | 11.1 | 786.8 | 754.3 | 694.8 | 807 | 633.7 | 688.2 | 556.9 | 675.7 | 690.5 | 620.3 | 608.9 | 612.1 | 678.8 | 299.9 | 346.1 | 357 | 332.2 | 289.9 | 347.6 | 357.3 | 324.6
1121.2 | 845.2 | 470.3 | 188.12 | 219.9014 | 402 | 314.8 | 329.6 | 322.8 | 459.7 | 52.3 | 19.3 | 97.4 | 8.6 | 240.2 | 10.6 | 788.3 | 754 | 693.6 | 808 | 633.3 | 687.8 | 557 | 682.8 | 692.9 | 620.5 | 608.7 | 614.4 | 681.1 | 299.9 | 346.3 | 357 | 332.4 | 290 | 347.6 | 357 | 324.8
1122.2 | 846.2 | 470.3 | 188.12 | 219.9014 | 403.6 | 315.3 | 329.4 | 322.5 | 461.7 | 52.4 | 19.3 | 97.3 | 9.6 | 251.9 | 10.2 | 786.9 | 756.8 | 684.3 | 808.4 | 631.3 | 687.7 | 556.6 | 679.3 | 693 | 619.6 | 608.8 | 611.8 | 686.9 | 300.1 | 346.5 | 357.1 | 332.5 | 290.1 | 347.3 | 356.6 | 324.9
1123.2 | 847.2 | 470.2 | 188.08 | 219.8547 | 406.9 | 314.6 | 329.6 | 322.7 | 461 | 52.4 | 19.3 | 97.3 | 9.2 | 275.1 | 9.1 | 786.4 | 760.1 | 673.3 | 808.7 | 629.3 | 687.3 | 555 | 671.4 | 689.9 | 618.6 | 608.8 | 607.4 | 691 | 300.5 | 346.3 | 356.8 | 332.4 | 290.3 | 346.7 | 356.1 | 325
1124.2 | 848.2 | 469.6 | 187.84 | 219.5741 | 408.9 | 313.7 | 330 | 322.3 | 459.8 | 52.5 | 19.3 | 97.3 | 8.4 | 259.1 | 10.3 | 784.3 | 755.3 | 660.3 | 807.7 | 626.9 | 686.8 | 553.4 | 652.2 | 685.4 | 617 | 608.6 | 599.9 | 691.9 | 300.7 | 346 | 356.9 | 332.2 | 290.4 | 346.4 | 355.9 | 325.1
1125.2 | 849.2 | 470.5 | 188.2 | 219.995 | 408.2 | 313.4 | 330 | 322.3 | 460.7 | 52.5 | 19.3 | 97.3 | 8.4 | 259.5 | 13 | 781.2 | 751.9 | 640 | 806 | 622.5 | 686.3 | 551.3 | 637.1 | 680.1 | 615 | 608.6 | 593.3 | 691.1 | 300.9 | 345.8 | 357.3 | 332.1 | 290.5 | 346.3 | 355.9 | 325.4
1126.2 | 850.2 | 469.8 | 187.92 | 219.6677 | 409.3 | 312.7 | 330.5 | 323 | 460.3 | 52.4 | 19.3 | 97.3 | 7.1 | 266.1 | 13.1 | 778 | 741 | 624.7 | 803.7 | 619.4 | 685.8 | 547.5 | 622.5 | 673.6 | 612.4 | 608.7 | 588 | 690.6 | 301 | 345.6 | 357.7 | 332 | 290.7 | 346.6 | 356.2 | 325.5
1127.2 | 851.2 | 469.8 | 187.92 | 219.6677 | 409 | 312.3 | 331.8 | 323.6 | 460.4 | 52.4 | 19.3 | 97.2 | 7.8 | 236.4 | 13.6 | 777.7 | 747 | 620.5 | 802.2 | 617.9 | 685.3 | 546.1 | 625.5 | 674 | 613.6 | 608.8 | 584.7 | 689.8 | 301.2 | 346 | 358 | 332.1 | 290.8 | 346.6 | 356.3 | 325.7
1128.2 | 852.2 | 469.7 | 187.88 | 219.6209 | 409.3 | 312.1 | 332.7 | 323.4 | 460.6 | 52.4 | 19.3 | 97.2 | 7 | 240.4 | 14.8 | 777.6 | 759.2 | 622.4 | 800.6 | 618 | 684.9 | 549 | 625.9 | 678.4 | 615.1 | 608.9 | 583.7 | 689.5 | 301.3 | 346.1 | 358.1 | 332.1 | 290.9 | 346.8 | 356.6 | 325.8
1129.2 | 853.2 | 469.9 | 187.96 | 219.7144 | 410.9 | 311.2 | 333.5 | 323.3 | 462 | 52.5 | 19.3 | 97.3 | 6 | 250.9 | 15 | 776.2 | 751.8 | 622.6 | 798.6 | 617.9 | 684.4 | 549.8 | 619.9 | 676.6 | 613.2 | 609 | 580.2 | 688.9 | 301.4 | 346 | 358.2 | 332.1 | 291 | 347.5 | 357 | 326
1130.2 | 854.2 | 470.1 | 188.04 | 219.8079 | 411.5 | 310.4 | 334.1 | 323.3 | 461.6 | 52.5 | 19.3 | 97.4 | 5.7 | 247 | 15 | 776.5 | 763.3 | 638.1 | 796.9 | 621.8 | 684 | 550.1 | 628.7 | 677.9 | 615.4 | 609 | 579.6 | 686.7 | 301.5 | 345.9 | 358.2 | 332.1 | 291.2 | 348.7 | 357.6 | 326.3
1131.2 | 855.2 | 470.4 | 188.16 | 219.9482 | 413.3 | 310.4 | 334.1 | 323.9 | 458.5 | 52.5 | 19.3 | 97.5 | 6.3 | 247.3 | 14.2 | 778.4 | 782 | 649.8 | 796.8 | 623 | 683.7 | 555.9 | 645.6 | 685.1 | 619.3 | 608.8 | 582.4 | 684.4 | 301.6 | 346 | 358.5 | 332.2 | 291.3 | 349 | 358.1 | 326.5
1132.2 | 856.2 | 470.2 | 188.08 | 219.8547 | 413.8 | 310.1 | 334.3 | 324 | 459.3 | 52.6 | 19.3 | 97.4 | 6.9 | 255.9 | 12.9 | 779.6 | 787.7 | 653.5 | 796.9 | 623.8 | 683.6 | 560.1 | 654.1 | 690.1 | 620.2 | 608.8 | 584.4 | 684 | 301.7 | 346.1 | 358.6 | 332.4 | 291.3 | 348.9 | 358.5 | 326.7
1133.2 | 857.2 | 469.8 | 187.92 | 219.6677 | 417.3 | 310.4 | 334.4 | 324.6 | 457.8 | 52.6 | 19.3 | 97.4 | 8.6 | 258.2 | 12 | 779.4 | 785.9 | 661.5 | 796.2 | 623 | 683.3 | 558.4 | 655.3 | 687.9 | 619.7 | 608.7 | 587 | 683.2 | 301.8 | 346 | 358.4 | 332.6 | 291.3 | 349.1 | 359.3 | 326.8
1134.2 | 858.2 | 469.5 | 187.8 | 219.5274 | 421.5 | 311.4 | 334.7 | 324.1 | 460.3 | 52.6 | 19.2 | 97.6 | 7.6 | 256.6 | 11.5 | 782.3 | 785 | 674.6 | 796.3 | 623.4 | 683.4 | 560 | 679.8 | 689.8 | 621.1 | 608.8 | 599.8 | 683.6 | 302 | 346.5 | 358.3 | 332.9 | 291.5 | 349.1 | 359.5 | 326.9
1135.2 | 859.2 | 469.7 | 187.88 | 219.6209 | 421 | 311.9 | 334.8 | 323.2 | 466.9 | 52.6 | 19.2 | 97.6 | 5.5 | 240.6 | 10.8 | 784.1 | 798.2 | 676.1 | 798.2 | 625.4 | 683.4 | 562 | 698.6 | 696.1 | 623.8 | 608.9 | 602.3 | 685.3 | 302.2 | 346.8 | 358.1 | 333.2 | 291.7 | 349.1 | 359.4 | 327
1136.2 | 860.2 | 470.2 | 188.08 | 219.8547 | 422 | 313.2 | 335.2 | 323.1 | 467.4 | 52.6 | 19.2 | 97.5 | 5.8 | 247.8 | 12 | 786.2 | 804.2 | 692.9 | 800.5 | 629.7 | 683.7 | 567 | 715.7 | 701.6 | 627.9 | 608.8 | 611.9 | 685.5 | 302.3 | 347 | 358.2 | 333.3 | 291.8 | 349 | 359.3 | 327.2
1137.2 | 861.2 | 470.5 | 188.2 | 219.995 | 425.1 | 313.8 | 334.6 | 323.3 | 470.5 | 52.7 | 19.2 | 97.5 | 5.9 | 250.2 | 11.6 | 789.1 | 803.7 | 705.1 | 803.3 | 632.5 | 684.1 | 566.7 | 717.2 | 697.9 | 628.5 | 608.7 | 623.2 | 685.4 | 302.6 | 347.4 | 358.7 | 333.6 | 291.9 | 348.8 | 359.2 | 327.3
1138.2 | 862.2 | 468.9 | 187.56 | 219.2468 | 426.9 | 314.8 | 334.2 | 323.9 | 467.2 | 52.7 | 19.2 | 97.4 | 6.3 | 241.7 | 11.6 | 793 | 816.1 | 710.6 | 806.5 | 634.5 | 684.1 | 572.6 | 730.6 | 706.4 | 632.6 | 608.6 | 625.9 | 684.3 | 302.8 | 347.5 | 359 | 333.6 | 292.1 | 348.9 | 359.1 | 327.4
1139.2 | 863.2 | 471 | 188.4 | 220.2287 | 425.6 | 315.3 | 334.2 | 324.8 | 470.6 | 52.7 | 19.2 | 97.2 | 6.6 | 246.6 | 16.5 | 792.2 | 829.3 | 694 | 809.6 | 632.3 | 684.5 | 578.9 | 731.9 | 715.9 | 635.4 | 608.5 | 619.3 | 683.1 | 302.9 | 347.6 | 359.4 | 333.5 | 292.3 | 348.9 | 359 | 327.6
1140.2 | 864.2 | 469.1 | 187.64 | 219.3403 | 428.9 | 315.2 | 334.3 | 324.9 | 472.4 | 52.8 | 19.2 | 97.1 | 6.9 | 245.2 | 17.5 | 793.4 | 839.3 | 696.1 | 811.8 | 634 | 685.1 | 581.1 | 737.4 | 720.7 | 637.4 | 608.6 | 617.1 | 682.2 | 303 | 347.7 | 359.7 | 333.6 | 292.4 | 348.7 | 359 | 327.8
1141.2 | 865.2 | 467.8 | 187.12 | 218.7325 | 434.6 | 314.7 | 335.6 | 325.4 | 475.5 | 52.9 | 19.2 | 96.9 | 6.8 | 260 | 16.6 | 792.1 | 842.1 | 683.5 | 813.9 | 632.1 | 685.5 | 585.6 | 733.6 | 725.7 | 639.9 | 608.5 | 611 | 680.2 | 303.2 | 347.9 | 360 | 333.7 | 292.5 | 348.8 | 359.2 | 327.9
1142.2 | 866.2 | 467.3 | 186.92 | 218.4987 | 438.5 | 314.6 | 336.6 | 326 | 482.7 | 53 | 19.2 | 96.8 | 6.9 | 249.3 | 15.2 | 790.2 | 840.1 | 665.7 | 813.5 | 630.3 | 686 | 585.1 | 718.9 | 721.1 | 638.7 | 608.7 | 603.2 | 677 | 303.2 | 347.9 | 360.3 | 333.7 | 292.7 | 349 | 359.3 | 328.1
1143.2 | 867.2 | 469.6 | 187.84 | 219.5741 | 440.4 | 313.9 | 337.1 | 326.4 | 484.5 | 53.1 | 19.2 | 96.8 | 7.2 | 245.2 | 15.8 | 787.8 | 832 | 658.6 | 813.2 | 629.3 | 686.2 | 584 | 702.1 | 717.8 | 638 | 608.7 | 598.2 | 672.7 | 303.3 | 348 | 360.8 | 333.6 | 292.8 | 349.4 | 359.9 | 328.3
1144.2 | 868.2 | 466.1 | 186.44 | 217.9376 | 441.3 | 313.8 | 338.1 | 327.7 | 483.9 | 53.1 | 19.2 | 96.9 | 7.3 | 248.2 | 16.1 | 789.1 | 832.8 | 659.1 | 812.3 | 631.1 | 686.3 | 586.7 | 700.5 | 721.2 | 640.1 | 608.8 | 597.8 | 668.7 | 303.6 | 348.2 | 361.1 | 333.7 | 293 | 349.9 | 360.4 | 328.5
1145.2 | 869.2 | 468.7 | 187.48 | 219.1533 | 443.3 | 313.6 | 338.9 | 328.2 | 481.7 | 53.2 | 19.2 | 96.9 | 6.8 | 243.5 | 15.9 | 791 | 825.6 | 665.3 | 812.9 | 633 | 686.6 | 586.2 | 699.1 | 721 | 639.8 | 608.7 | 600.5 | 666.7 | 303.9 | 348.5 | 361.3 | 333.9 | 293.2 | 349.9 | 360.9 | 328.7
1146.2 | 870.2 | 471.4 | 188.56 | 220.4158 | 443.5 | 314.1 | 339.6 | 328.2 | 476 | 53.3 | 19.2 | 96.9 | 6.4 | 245.8 | 14.6 | 790 | 810.6 | 674.6 | 812.8 | 631.6 | 686.8 | 582 | 685.8 | 715.1 | 637.6 | 608.3 | 601 | 666.3 | 304.2 | 349 | 361.2 | 334.2 | 293.4 | 350.2 | 361.4 | 328.8
1147.2 | 871.2 | 469.1 | 187.64 | 219.3403 | 444.3 | 314.1 | 339.6 | 328.7 | 470 | 53.3 | 19.2 | 96.8 | 8.1 | 247.6 | 13.6 | 791.9 | 814.4 | 682.9 | 813.2 | 632.6 | 687 | 579.2 | 692.1 | 714.9 | 639 | 608.2 | 604.1 | 666.5 | 304.4 | 349.4 | 361.2 | 334.4 | 293.7 | 350.5 | 362 | 329.1
1148.2 | 872.2 | 467.3 | 186.92 | 218.4987 | 443.9 | 313.6 | 338.8 | 329 | 465.9 | 53.3 | 19.2 | 97 | 8.1 | 241.2 | 11.3 | 794.2 | 814.3 | 685.8 | 813.6 | 633.4 | 687.2 | 579 | 690.2 | 714.8 | 638.5 | 608.3 | 603.9 | 667 | 304.4 | 349.6 | 361 | 334.7 | 293.8 | 350.7 | 362.1 | 329.3
1149.2 | 873.2 | 467.6 | 187.04 | 218.639 | 443.6 | 314.7 | 338 | 328.4 | 461 | 53.4 | 19.2 | 97 | 8.3 | 267.9 | 12.9 | 795.9 | 807.6 | 688.3 | 814.8 | 633.5 | 687.4 | 575.6 | 689.2 | 710.7 | 638.1 | 608.2 | 604.1 | 668.1 | 304.5 | 349.7 | 360.8 | 334.8 | 293.9 | 350.6 | 362.2 | 329.4
1150.2 | 874.2 | 468.3 | 187.32 | 218.9663 | 444.4 | 316.3 | 337.6 | 328.6 | 460.7 | 53.4 | 19.2 | 97 | 7.3 | 262.3 | 14.4 | 794.9 | 800.4 | 685.5 | 815.4 | 633.4 | 687.5 | 571.8 | 673.9 | 703.3 | 636.3 | 608.2 | 602.1 | 670.7 | 304.7 | 349.8 | 360.5 | 334.9 | 294 | 350.5 | 362.3 | 329.5
1151.2 | 875.2 | 468.6 | 187.44 | 219.1066 | 444.4 | 316.6 | 337.5 | 328.5 | 459.5 | 53.4 | 19.2 | 97.1 | 7.7 | 266.3 | 13.9 | 793.3 | 792.6 | 675.9 | 815.3 | 632.2 | 687.3 | 567.4 | 664.4 | 697.1 | 634.1 | 608.2 | 599.5 | 673.2 | 305 | 349.7 | 360 | 335 | 294.3 | 350.3 | 361.8 | 329.6
1152.2 | 876.2 | 467.8 | 187.12 | 218.7325 | 443.5 | 316.6 | 337.2 | 328.1 | 458.9 | 53.4 | 19.2 | 97.1 | 6.5 | 255.2 | 11.9 | 791.6 | 782.1 | 670.9 | 814 | 629.8 | 687.2 | 563 | 656.1 | 690.7 | 631.6 | 608.2 | 596.4 | 675.8 | 305.2 | 349.6 | 359.6 | 335 | 294.4 | 349.9 | 361.4 | 329.6
1153.2 | 877.2 | 468.5 | 187.4 | 219.0598 | 443.7 | 316.5 | 336.6 | 327.8 | 457 | 53.3 | 19.2 | 97 | 6.1 | 241.2 | 13.9 | 794.4 | 781.9 | 683.8 | 813.8 | 632.7 | 687.1 | 562.4 | 668.4 | 694.3 | 632.6 | 608.2 | 599.4 | 679.4 | 305.5 | 349.6 | 359.5 | 335.1 | 294.7 | 349.7 | 361.1 | 329.6
1154.2 | 878.2 | 467.7 | 187.08 | 218.6857 | 443.3 | 316.4 | 336.3 | 327.1 | 455.8 | 53.2 | 19.2 | 97.1 | 6.7 | 240.7 | 16.8 | 794.3 | 777 | 690.5 | 814 | 633.2 | 687 | 560.5 | 668.4 | 692.9 | 631.2 | 608.1 | 600.5 | 682.7 | 305.7 | 349.8 | 359.7 | 335.3 | 294.9 | 349.2 | 360.9 | 329.7
1155.2 | 879.2 | 469.1 | 187.64 | 219.3403 | 445.5 | 316.1 | 336.2 | 326.9 | 457.3 | 53.2 | 19.2 | 97.1 | 6.2 | 245.8 | 16.2 | 793.9 | 771.7 | 698 | 813.6 | 632.7 | 686.9 | 559.1 | 666.8 | 689.5 | 629.7 | 608.2 | 601.9 | 686.6 | 305.8 | 350.1 | 360.2 | 335.6 | 295.2 | 348.8 | 360.5 | 329.7
1156.2 | 880.2 | 468.7 | 187.48 | 219.1533 | 445.8 | 316.1 | 336.2 | 326.7 | 457.3 | 53.2 | 19.2 | 97.1 | 5.8 | 243.4 | 15.4 | 796.6 | 783.2 | 713.7 | 814.4 | 636.8 | 687 | 561.1 | 689.9 | 696.7 | 632.1 | 608.6 | 610.3 | 687.8 | 305.9 | 350.2 | 360.4 | 335.7 | 295.5 | 348.8 | 360.4 | 329.8
1157.2 | 881.2 | 469.6 | 187.84 | 219.5741 | 445.4 | 316.5 | 335.8 | 326.8 | 457.8 | 53.2 | 19.2 | 97.1 | 6.8 | 247.9 | 14.9 | 799.8 | 794.4 | 712.9 | 816.4 | 638.5 | 687.2 | 566.7 | 712.2 | 707.8 | 635.6 | 608.6 | 618.4 | 689 | 306.2 | 350.4 | 361.2 | 335.6 | 295.7 | 349 | 360.3 | 329.9
1158.2 | 882.2 | 470.6 | 188.24 | 220.0417 | 448.4 | 317.8 | 335.6 | 326.6 | 462.4 | 53.2 | 19.2 | 97.2 | 7.1 | 253.8 | 14.6 | 798 | 792.4 | 696.7 | 818 | 636.4 | 687.4 | 569 | 704 | 708.4 | 634.4 | 608.1 | 611.3 | 689.5 | 306.4 | 350.5 | 361.3 | 335.5 | 295.9 | 349.3 | 360.1 | 330
1159.2 | 883.2 | 470.6 | 188.24 | 220.0417 | 452.3 | 318.6 | 335.3 | 326.6 | 470.3 | 53.2 | 19.2 | 97.4 | 6.3 | 253.2 | 14.6 | 795.6 | 793.2 | 688.4 | 817.7 | 635.5 | 687.3 | 569.3 | 682 | 705.1 | 634.2 | 608.2 | 602.9 | 685.1 | 306.6 | 350.4 | 361.4 | 335.4 | 295.9 | 349.7 | 360.5 | 330.3
1160.2 | 884.2 | 470.1 | 188.04 | 219.8079 | 453.3 | 319.8 | 335.4 | 327.3 | 472.1 | 53.2 | 19.2 | 97.5 | 6.2 | 251.6 | 14.3 | 796.4 | 793.2 | 692.1 | 816.9 | 640.1 | 687.2 | 574 | 680.9 | 707.9 | 636.9 | 608.3 | 597.1 | 679.4 | 306.9 | 350.3 | 361.8 | 335.3 | 296 | 350.1 | 360.8 | 330.5
1161.2 | 885.2 | 469.2 | 187.68 | 219.3871 | 450.1 | 320.9 | 336.5 | 328.3 | 474.9 | 53.3 | 19.2 | 97.5 | 5.3 | 254.6 | 13.7 | 798.5 | 798.2 | 704.1 | 817.5 | 644.9 | 687.6 | 579.7 | 697.9 | 715.4 | 639.5 | 608.4 | 596.5 | 674.8 | 307 | 350.2 | 362.1 | 335.3 | 296.1 | 350.1 | 361.2 | 330.7
1162.2 | 886.2 | 468.5 | 187.4 | 219.0598 | 446.4 | 320.7 | 337 | 329.1 | 477.9 | 53.3 | 19.2 | 97.5 | 4.2 | 240.5 | 11.8 | 801.6 | 807.3 | 708.6 | 819.6 | 648.4 | 688 | 584.3 | 716.1 | 723.1 | 643.2 | 608 | 599.8 | 673.1 | 307.1 | 350.1 | 362.1 | 335.4 | 296.3 | 350.1 | 361.2 | 330.8
1163.2 | 887.2 | 470.1 | 188.04 | 219.8079 | 447 | 322.4 | 337.7 | 329.5 | 477.3 | 53.3 | 19.2 | 97.5 | 4.8 | 242.4 | 10.2 | 804.4 | 813.4 | 727.1 | 821.7 | 652.8 | 688.4 | 590 | 731 | 732.6 | 647.3 | 607.6 | 606 | 672.1 | 307.2 | 350 | 362 | 335.5 | 296.4 | 350.3 | 361.1 | 331
1164.2 | 888.2 | 470.3 | 188.12 | 219.9014 | 452.3 | 323.6 | 338.2 | 329.4 | 476.6 | 53.3 | 19.2 | 97.5 | 4.9 | 248.8 | 9.4 | 807.9 | 818.7 | 736.3 | 824.1 | 656.2 | 689 | 591.7 | 742.2 | 733.3 | 651 | 607.5 | 612.6 | 670.6 | 307.4 | 349.9 | 361.9 | 335.6 | 296.5 | 350.3 | 361.1 | 331.1
1165.2 | 889.2 | 470.6 | 188.24 | 220.0417 | 451.2 | 324.9 | 338.5 | 329.1 | 473 | 53.4 | 19.2 | 97.7 | 5.7 | 263.6 | 11.2 | 811.5 | 822.1 | 738.2 | 826.9 | 658.1 | 689.5 | 591.7 | 753.2 | 734.2 | 652.9 | 607.1 | 618.3 | 671.4 | 307.6 | 349.9 | 361.7 | 335.7 | 296.7 | 350.4 | 361 | 331.2
1166.2 | 890.2 | 470 | 188 | 219.7612 | 450.6 | 326.2 | 338.3 | 328.7 | 472.5 | 53.4 | 19.2 | 97.7 | 5.6 | 255.4 | 12.4 | 812.9 | 820.8 | 729.6 | 829.5 | 656.5 | 690.1 | 590.3 | 752.7 | 731.9 | 652.1 | 607 | 623.2 | 673.5 | 307.8 | 350.1 | 361.5 | 336 | 296.9 | 350.3 | 361.1 | 331.2
1167.2 | 891.2 | 470.7 | 188.28 | 220.0885 | 451.5 | 326.9 | 338 | 328.5 | 474 | 53.4 | 19.1 | 97.7 | 6.9 | 271.2 | 11.4 | 815.6 | 816.7 | 740.9 | 830.5 | 656.9 | 691.1 | 590.7 | 764 | 734.2 | 654.4 | 607.1 | 634.9 | 675.6 | 307.9 | 350.3 | 361.4 | 336.2 | 297 | 350.2 | 361.1 | 331.3
1168.2 | 892.2 | 470.7 | 188.28 | 220.0885 | 450.7 | 326.9 | 338.5 | 328.8 | 479.8 | 53.4 | 19.1 | 97.7 | 7.5 | 269.9 | 10.4 | 820.3 | 810.4 | 763.5 | 832.6 | 660.8 | 692.3 | 591.6 | 773.8 | 738.3 | 655.2 | 607.2 | 647.3 | 678 | 308.2 | 350.6 | 361.2 | 336.5 | 297.2 | 350.3 | 361.5 | 331.3
1169.2 | 893.2 | 471.3 | 188.52 | 220.369 | 448.6 | 326.7 | 338.3 | 330.2 | 485.8 | 53.4 | 19.1 | 97.7 | 7.3 | 254.3 | 10.1 | 822.1 | 795.4 | 758.3 | 835 | 661.7 | 693.5 | 591.4 | 778.4 | 738.7 | 658.1 | 607.3 | 659.1 | 679.3 | 308.3 | 351.2 | 361.2 | 336.9 | 297.3 | 350.5 | 363.5 | 331.4
1170.2 | 894.2 | 470.9 | 188.36 | 220.182 | 449.4 | 327 | 337.9 | 332.3 | 497.8 | 53.4 | 19.1 | 97.7 | 5.9 | 251.1 | 11.4 | 823.9 | 790 | 758.6 | 836.2 | 662 | 694.8 | 589.2 | 779.1 | 734.8 | 657.9 | 607.5 | 668.9 | 678.2 | 308.4 | 351.9 | 361.7 | 337.3 | 297.5 | 350.5 | 363.6 | 331.5
1171.2 | 895.2 | 470.3 | 188.12 | 219.9014 | 448 | 327.2 | 338.5 | 333.6 | 503.1 | 53.4 | 19.1 | 97.8 | 6.4 | 234.3 | 12.5 | 826 | 794.2 | 764 | 836.7 | 665.6 | 696 | 586.8 | 785 | 732.2 | 660.4 | 608.1 | 681.1 | 675.1 | 308.5 | 352.4 | 362.1 | 337.5 | 297.6 | 350.5 | 363.6 | 331.5
1172.2 | 896.2 | 470.5 | 188.2 | 219.995 | 447.1 | 327.9 | 339.4 | 334.2 | 510.7 | 53.4 | 19.1 | 97.7 | 5.8 | 259.3 | 12 | 825.3 | 781.5 | 769.4 | 837 | 667.7 | 697.2 | 585 | 780 | 728.4 | 660.7 | 608.6 | 691.1 | 671 | 308.6 | 353 | 362.8 | 337.8 | 297.8 | 350.3 | 364.7 | 331.6
1173.2 | 897.2 | 469.5 | 187.8 | 219.5274 | 447.7 | 328.2 | 340.2 | 335.4 | 515.8 | 53.4 | 19.1 | 97.7 | 6.7 | 227.5 | 12.1 | 825.7 | 777.6 | 769.8 | 837.8 | 667.5 | 698 | 581.8 | 769.7 | 720.4 | 658.7 | 609 | 689.2 | 668.7 | 308.8 | 353.6 | 363.7 | 338.1 | 298 | 350.3 | 365.8 | 331.7
1174.2 | 898.2 | 471 | 188.4 | 220.2287 | 447.9 | 329.4 | 340.6 | 337 | 509.9 | 53.4 | 19.1 | 97.7 | 6.1 | 261.5 | 10 | 828.3 | 793.1 | 767.9 | 838.7 | 669.8 | 698.4 | 580.4 | 772.9 | 721.3 | 661.2 | 609.4 | 685.4 | 668.6 | 309 | 354.3 | 364.6 | 338.3 | 298.2 | 350.5 | 366.1 | 331.8
1175.2 | 899.2 | 470.3 | 188.12 | 219.9014 | 450.5 | 331 | 340.3 | 338.2 | 502 | 53.4 | 19.1 | 97.7 | 7.1 | 256.5 | 11 | 828.9 | 789.2 | 765.1 | 839.6 | 668.3 | 699 | 579.7 | 764.8 | 719.6 | 660.1 | 609.8 | 686.2 | 667.6 | 309.2 | 355 | 365.4 | 338.4 | 298.3 | 350.7 | 366.2 | 332
1176.2 | 900.2 | 471 | 188.4 | 220.2287 | 450.2 | 332.6 | 340.7 | 338.1 | 503.7 | 53.4 | 19.1 | 97.7 | 7.2 | 254.8 | 13.6 | 831.8 | 785.6 | 770.2 | 840.6 | 670.7 | 699.4 | 575.8 | 756.7 | 716 | 658.9 | 610.3 | 687 | 666.1 | 309.4 | 355.7 | 366.1 | 338.7 | 298.4 | 351.2 | 366.2 | 332.1
1177.2 | 901.2 | 470 | 188 | 219.7612 | 449.2 | 333.4 | 340.8 | 337.7 | 496.6 | 53.5 | 19.1 | 97.8 | 6.6 | 257.1 | 15.5 | 831.8 | 796.2 | 763.4 | 842 | 672.9 | 699.4 | 576.8 | 754 | 723.9 | 660.8 | 610.7 | 684 | 664.2 | 309.4 | 356.1 | 366.4 | 338.7 | 298.5 | 351.6 | 366.2 | 332.3
1178.2 | 902.2 | 466.5 | 186.6 | 218.1246 | 449.4 | 332.7 | 340.6 | 338.3 | 490.9 | 53.4 | 19.1 | 97.9 | 6.6 | 270.5 | 16.2 | 834.6 | 803.6 | 774.2 | 843.4 | 676.7 | 699.7 | 582.4 | 761.5 | 734.6 | 662.3 | 611.3 | 686.2 | 661.4 | 309.6 | 356.2 | 366.8 | 338.6 | 298.8 | 351.8 | 366.1 | 332.5
1179.2 | 903.2 | 468.4 | 187.36 | 219.013 | 449.3 | 332.8 | 340.3 | 338.4 | 490.2 | 53.4 | 19.1 | 98 | 5.9 | 261.2 | 14.7 | 837.5 | 815.4 | 786.2 | 844.9 | 681.3 | 700.3 | 586 | 772.8 | 739.8 | 665.2 | 611.8 | 692.4 | 658.9 | 309.8 | 356.2 | 366.9 | 338.6 | 298.9 | 351.6 | 365.6 | 332.6
1180.2 | 904.2 | 469.1 | 187.64 | 219.3403 | 450.2 | 332.2 | 340.6 | 338.2 | 488.8 | 53.5 | 19.1 | 98.1 | 5.8 | 256.8 | 13.2 | 841.4 | 822 | 797.1 | 846.6 | 687.1 | 701.1 | 591.2 | 779.3 | 745.8 | 669.2 | 612 | 695 | 655.6 | 309.9 | 356.1 | 366.8 | 338.6 | 299.1 | 351.5 | 365.4 | 332.7
1181.2 | 905.2 | 469.8 | 187.92 | 219.6677 | 447.9 | 332.1 | 340.6 | 337.6 | 490.2 | 53.5 | 19.1 | 98.1 | 5.3 | 247 | 12.9 | 846.5 | 820.3 | 794.4 | 849.4 | 690.3 | 701.7 | 596.5 | 786.4 | 749.2 | 672.2 | 612.3 | 701.1 | 653 | 310.1 | 356.1 | 367 | 338.7 | 299.4 | 351.4 | 365.5 | 332.8
1182.2 | 906.2 | 468.2 | 187.28 | 218.9195 | 449.5 | 333 | 340.4 | 337.1 | 494.1 | 53.4 | 19.1 | 98 | 5.2 | 259.2 | 14.4 | 848.9 | 823.1 | 793.3 | 852.3 | 690.3 | 702.7 | 599.9 | 795.4 | 752.1 | 674.5 | 612.7 | 707.8 | 653 | 310.5 | 356.3 | 367.6 | 338.8 | 299.5 | 351.3 | 365.4 | 332.8
1183.2 | 907.2 | 469.5 | 187.8 | 219.5274 | 450.4 | 333.5 | 340.5 | 337.1 | 497.6 | 53.4 | 19.1 | 98.1 | 5.5 | 248.7 | 13.5 | 852.6 | 830.3 | 794.7 | 854.6 | 693.3 | 703.5 | 604.1 | 798.4 | 759.7 | 676.8 | 613 | 709 | 652.5 | 310.6 | 356.3 | 368 | 338.9 | 299.7 | 351 | 365.5 | 332.9
1184.2 | 908.2 | 470.1 | 188.04 | 219.8079 | 448.5 | 335.2 | 340.9 | 337.1 | 497.3 | 53.3 | 19.1 | 98.3 | 5.1 | 259.7 | 12.4 | 854.6 | 832.8 | 802.8 | 856.3 | 700.1 | 704.1 | 607.4 | 793.4 | 765.6 | 680 | 613.3 | 711 | 649.8 | 310.8 | 356.2 | 367.8 | 339 | 299.8 | 351 | 365.6 | 333.1
1185.2 | 909.2 | 469.8 | 187.92 | 219.6677 | 448.1 | 335.9 | 340.9 | 337.2 | 494.7 | 53.3 | 19.1 | 98.4 | 5.2 | 254.5 | 12.4 | 856.8 | 833.1 | 808.3 | 858.6 | 705.1 | 704.7 | 610.6 | 792.3 | 770.3 | 682.8 | 613.4 | 712.4 | 646.2 | 311.1 | 356.1 | 367.9 | 339 | 299.9 | 350.9 | 365.9 | 333.1
1186.2 | 910.2 | 469.7 | 187.88 | 219.6209 | 447.6 | 337.2 | 340.1 | 337.2 | 497.7 | 53.3 | 19.1 | 98.5 | 5.5 | 254.5 | 12.4 | 858.8 | 818 | 814.6 | 860.7 | 707.7 | 705.7 | 608.5 | 797.3 | 766.8 | 684.6 | 613.5 | 719.9 | 643.1 | 311.3 | 356.3 | 367.9 | 339.3 | 300.1 | 350.6 | 365.5 | 333.2
1187.2 | 911.2 | 468.9 | 187.56 | 219.2468 | 446.3 | 338.1 | 339.6 | 337 | 501 | 53.4 | 19.1 | 98.5 | 5.4 | 261.1 | 12.5 | 861.1 | 810.8 | 807.6 | 862.4 | 707.2 | 706.7 | 607.3 | 798.3 | 765.6 | 685.7 | 613.6 | 724.8 | 641.2 | 311.5 | 356.5 | 368 | 339.6 | 300.3 | 350.4 | 365.3 | 333.3
1188.2 | 912.2 | 469.8 | 187.92 | 219.6677 | 445.4 | 339.2 | 340.2 | 336.9 | 517.1 | 53.4 | 19.1 | 98.5 | 5.9 | 259.7 | 13.9 | 860.9 | 800.1 | 797.7 | 863.8 | 705.3 | 708.2 | 604.8 | 792.5 | 759.1 | 683.8 | 614.1 | 727 | 639.2 | 311.8 | 357.1 | 368.4 | 340 | 300.5 | 350.3 | 365.8 | 333.4
1189.2 | 913.2 | 469.8 | 187.92 | 219.6677 | 443.3 | 340.4 | 341.3 | 337.3 | 522.8 | 53.4 | 19.1 | 98.4 | 5.4 | 253.6 | 13.3 | 862.3 | 796.8 | 805.1 | 864.2 | 707.8 | 709.2 | 603.6 | 795.7 | 759.1 | 685.1 | 614.9 | 730 | 638.1 | 312 | 357.5 | 368.7 | 340.3 | 300.6 | 350.4 | 366.1 | 333.5
1190.2 | 914.2 | 469.8 | 187.92 | 219.6677 | 444.1 | 340.1 | 342.2 | 338.7 | 519.8 | 53.4 | 19.1 | 98.3 | 4.6 | 239.1 | 12.5 | 863.8 | 800.5 | 812.1 | 864.9 | 711 | 709.9 | 605.1 | 794.7 | 761.7 | 688.6 | 615.6 | 733.3 | 636.2 | 312.1 | 357.7 | 369.1 | 340.5 | 300.8 | 350.4 | 365.7 | 333.6
1191.2 | 915.2 | 469.8 | 187.92 | 219.6677 | 444.9 | 340.9 | 342.2 | 339.8 | 517 | 53.4 | 19.1 | 98.2 | 5 | 235.6 | 11 | 861.2 | 789.1 | 797.8 | 865 | 709.9 | 710.6 | 602.4 | 781.3 | 753.9 | 687.1 | 616 | 731.5 | 633.4 | 312.3 | 358.2 | 369.6 | 340.7 | 301 | 350.2 | 365.4 | 333.6
1192.2 | 916.2 | 469.7 | 187.88 | 219.6209 | 444.6 | 342.6 | 342.2 | 340.3 | 518.8 | 53.5 | 19.1 | 98 | 5.3 | 262.6 | 9.8 | 858.3 | 771.7 | 770.6 | 863 | 704.4 | 711.1 | 592.9 | 747.8 | 738.6 | 681.8 | 616.3 | 721.6 | 630.9 | 312.5 | 358.9 | 370.2 | 341 | 301.1 | 350.2 | 365.4 | 333.6
1193.2 | 917.2 | 469.8 | 187.92 | 219.6677 | 445.4 | 342.2 | 342.3 | 340.1 | 511.3 | 53.5 | 19.1 | 97.9 | 6.3 | 234.8 | 10.1 | 859.3 | 775.6 | 765.8 | 861.6 | 703.4 | 711.2 | 588.4 | 747.2 | 733.5 | 681.3 | 616.8 | 720.3 | 631.1 | 312.7 | 359.1 | 370.5 | 341.1 | 301.2 | 350.2 | 365.2 | 333.7
1194.2 | 918.2 | 469.4 | 187.76 | 219.4806 | 446.5 | 341.5 | 342.9 | 339.5 | 504.9 | 53.5 | 19.1 | 97.9 | 6.1 | 260.2 | 9.5 | 861.8 | 792.1 | 769.6 | 860.5 | 705 | 711.3 | 593 | 765.8 | 744.5 | 684.1 | 617.6 | 723 | 631.3 | 312.8 | 359.1 | 370.5 | 341 | 301.4 | 350.3 | 365.1 | 333.8
1195.2 | 919.2 | 468.9 | 187.56 | 219.2468 | 445.5 | 341.1 | 343 | 339.4 | 507.6 | 53.4 | 19.1 | 97.8 | 6.7 | 251.3 | 11.4 | 863.7 | 786 | 774.7 | 860.6 | 706.5 | 712.3 | 593.9 | 771.5 | 744.5 | 685.2 | 618.3 | 726.8 | 630.8 | 313 | 359.3 | 370.7 | 341.1 | 301.5 | 350.2 | 366 | 333.9
1196.2 | 920.2 | 469.1 | 187.64 | 219.3403 | 445.9 | 341 | 342.8 | 339.1 | 519.5 | 53.4 | 19.1 | 97.9 | 6.7 | 244.9 | 13 | 862.3 | 778.5 | 772.2 | 859.9 | 705.1 | 713.1 | 591 | 762 | 736.2 | 683.1 | 618.6 | 725.5 | 628.9 | 313.2 | 359.8 | 371.2 | 341.4 | 301.6 | 350 | 365.9 | 334
1197.2 | 921.2 | 469.4 | 187.76 | 219.4806 | 444.5 | 340.5 | 342.6 | 338.8 | 519.2 | 53.4 | 19.1 | 97.9 | 6.1 | 251.9 | 14.4 | 859.4 | 770.5 | 774.5 | 858 | 704.9 | 713.3 | 586.2 | 753.8 | 729.2 | 681.2 | 618.9 | 725.8 | 626.7 | 313.5 | 360.3 | 371.9 | 341.7 | 301.7 | 349.8 | 365.7 | 334
1198.2 | 922.2 | 469.8 | 187.92 | 219.6677 | 444.1 | 341.1 | 343.7 | 338.3 | 518.4 | 53.3 | 19.1 | 97.9 | 5.7 | 254.5 | 13.8 | 858.5 | 769.9 | 771.8 | 856.3 | 705.8 | 713.4 | 584.9 | 751.4 | 725.6 | 681.1 | 619.2 | 725 | 624.8 | 313.7 | 360.5 | 372.4 | 341.9 | 301.8 | 349.6 | 365.4 | 334.1
1199.2 | 923.2 | 469.3 | 187.72 | 219.4339 | 444.7 | 341.4 | 344.4 | 338.5 | 513.8 | 53.4 | 19.1 | 98 | 5.6 | 258.7 | 12.8 | 859.4 | 770.7 | 775.7 | 855.1 | 707.7 | 713.4 | 583.2 | 752.6 | 723.5 | 679.8 | 619.3 | 723.6 | 624.9 | 314 | 360.7 | 372.6 | 342 | 302 | 349.4 | 365.6 | 334.2
1200.2 | 924.2 | 471.7 | 188.68 | 220.556 | 446.1 | 341.1 | 344.1 | 338.9 | 507 | 53.4 | 19.1 | 98.1 | 6.5 | 253.5 | 11 | 860.8 | 782.3 | 770.2 | 854.8 | 706.9 | 713.4 | 583.6 | 756.3 | 727.9 | 680.7 | 619.6 | 719.8 | 627.1 | 314.2 | 360.9 | 373 | 342.1 | 302.1 | 349.5 | 365.8 | 334.3
1201.2 | 925.2 | 472.4 | 188.96 | 220.8834 | 448.7 | 341 | 343.7 | 338.9 | 503.7 | 53.5 | 19.1 | 98.3 | 6.2 | 259.3 | 9.8 | 864.6 | 792.8 | 775.5 | 855.5 | 709 | 713.5 | 587.2 | 770.4 | 735.5 | 683.4 | 619.6 | 724.4 | 627.6 | 314.3 | 361.1 | 373.2 | 342.2 | 302.3 | 350 | 365.5 | 334.3
1202.2 | 926.2 | 471.2 | 188.48 | 220.3223 | 456.1 | 341.3 | 342.8 | 338 | 500.3 | 53.5 | 19.1 | 98.4 | 6 | 258 | 10.2 | 868.1 | 803.5 | 780.3 | 856.4 | 710.7 | 713.8 | 590.7 | 779.7 | 738.4 | 686.7 | 619.4 | 725.8 | 628.1 | 314.5 | 361.1 | 373.2 | 342.2 | 302.5 | 350.3 | 365.2 | 334.4
1203.2 | 927.2 | 470.3 | 188.12 | 219.9014 | 458.2 | 340.1 | 341.9 | 337.3 | 498.3 | 53.5 | 19.1 | 98.5 | 6.5 | 246.7 | 11 | 869.4 | 806.6 | 777 | 858.8 | 711.3 | 714.2 | 593 | 775.1 | 738.8 | 687.1 | 619.5 | 723.5 | 629.8 | 314.6 | 361 | 373.1 | 342.2 | 302.6 | 350.3 | 364.7 | 334.5
1204.2 | 928.2 | 469.7 | 187.88 | 219.6209 | 459.3 | 338.5 | 341 | 336.6 | 494.7 | 53.5 | 19.1 | 98.6 | 5.7 | 261.5 | 9.9 | 868.3 | 815.5 | 773.4 | 861.1 | 711.6 | 714.2 | 595.5 | 766.5 | 739.8 | 687.9 | 619.4 | 715.6 | 632.9 | 314.8 | 360.6 | 372.9 | 342.2 | 302.7 | 350.3 | 364.3 | 334.6
1205.2 | 929.2 | 470.1 | 188.04 | 219.8079 | 464.6 | 337.3 | 340.7 | 336.4 | 490.9 | 53.6 | 19.1 | 98.7 | 5.2 | 228.8 | 8.6 | 867.1 | 821.4 | 766.9 | 862.5 | 711.7 | 714 | 597 | 764.8 | 741 | 689.1 | 619.5 | 711.6 | 635.1 | 315 | 360.3 | 372.6 | 342 | 302.8 | 350.2 | 363.8 | 334.7
1206.2 | 930.2 | 469.7 | 187.88 | 219.6209 | 471.2 | 336.5 | 340.8 | 336.6 | 489.6 | 53.7 | 19.1 | 98.8 | 6.1 | 255.8 | 10 | 866 | 834 | 752.6 | 863.6 | 709.4 | 713.9 | 601.2 | 762.1 | 745.3 | 691 | 619.2 | 703.4 | 636.6 | 315.3 | 360 | 372.2 | 342 | 303 | 350.1 | 363.5 | 334.8
1207.2 | 931.2 | 470.5 | 188.2 | 219.995 | 476.1 | 336.5 | 340.8 | 336.2 | 489.1 | 53.8 | 19.1 | 98.9 | 5.8 | 243.5 | 10.8 | 863.1 | 831.9 | 733.8 | 863.1 | 706.4 | 713.6 | 600.9 | 736 | 742.1 | 688.1 | 619.5 | 690.3 | 636.9 | 315.5 | 359.6 | 371.8 | 341.9 | 303.2 | 350.3 | 363.3 | 335
1208.2 | 932.2 | 470.7 | 188.28 | 220.0885 | 475.5 | 336.4 | 340.7 | 335.7 | 490.2 | 53.9 | 19 | 99 | 5.7 | 249.6 | 10.2 | 860 | 831.9 | 721 | 860.7 | 704.4 | 713.5 | 600.5 | 717.9 | 738.9 | 687.3 | 619.8 | 678.8 | 637.1 | 315.6 | 359.2 | 371.6 | 341.8 | 303.3 | 350.8 | 363.4 | 335.2
1209.2 | 933.2 | 471.1 | 188.44 | 220.2755 | 478.8 | 337.2 | 340.7 | 335.5 | 489.1 | 54.1 | 19 | 99.1 | 6.1 | 249.2 | 9.6 | 860.3 | 835.1 | 730 | 859.5 | 706 | 713.5 | 601.7 | 725 | 743 | 688.9 | 620.1 | 675.9 | 637.6 | 315.9 | 358.8 | 371.3 | 341.8 | 303.5 | 350.8 | 363.6 | 335.3
1210.2 | 934.2 | 471.2 | 188.48 | 220.3223 | 479 | 337.4 | 341.2 | 335.2 | 487.3 | 54.1 | 19.1 | 99.2 | 6.2 | 242 | 10.8 | 860.9 | 825 | 726.9 | 859.1 | 706.2 | 713.2 | 602.4 | 730.5 | 743.4 | 688.5 | 620.1 | 675.6 | 639.7 | 316 | 358.5 | 371.2 | 341.9 | 303.8 | 351 | 363.9 | 335.3
1211.2 | 935.2 | 470.5 | 188.2 | 219.995 | 473.6 | 336.6 | 341.8 | 335.3 | 485.7 | 54.2 | 19 | 99.3 | 6.3 | 241.4 | 11 | 858.4 | 818.8 | 716 | 857.6 | 702 | 712.2 | 597.2 | 716.3 | 734.9 | 685.4 | 620 | 669.3 | 644.2 | 316.3 | 358.3 | 370.9 | 342 | 304 | 351 | 364 | 335.4
1212.2 | 936.2 | 469.9 | 187.96 | 219.7144 | 474.1 | 335.9 | 342.3 | 334.6 | 479.4 | 54.2 | 19 | 99.5 | 6.6 | 261.3 | 11 | 857.2 | 826.2 | 712.7 | 856.8 | 698.9 | 712.3 | 594 | 713.4 | 733.8 | 685.3 | 620.2 | 665.9 | 650.4 | 316.4 | 358.2 | 370.7 | 342.1 | 304.1 | 351.2 | 364 | 335.5
1213.2 | 937.2 | 469.5 | 187.8 | 219.5274 | 474.1 | 334.5 | 342 | 334.1 | 480 | 54.1 | 19 | 99.8 | 6.4 | 264.1 | 9.3 | 856.5 | 839.8 | 702.6 | 855.7 | 695.7 | 712.2 | 595.1 | 717.7 | 739.7 | 686.3 | 620.8 | 660 | 655.5 | 316.6 | 358.1 | 370.5 | 342.2 | 304.3 | 351.5 | 364 | 335.6
1214.2 | 938.2 | 470.2 | 188.08 | 219.8547 | 471.3 | 332.6 | 341.5 | 333.5 | 481.2 | 54.1 | 19 | 99.9 | 6.2 | 235.9 | 7.1 | 855 | 836.9 | 698 | 855 | 693.8 | 711.7 | 592.9 | 710.3 | 737.1 | 684.5 | 620.7 | 654.9 | 657.8 | 316.6 | 357.9 | 370.4 | 342.2 | 304.4 | 351.7 | 364.3 | 335.8
1215.2 | 939.2 | 470.7 | 188.28 | 220.0885 | 468.7 | 330.5 | 342 | 333.4 | 477 | 54.1 | 19 | 100 | 7.2 | 254.9 | 9.9 | 854.3 | 827.4 | 697.1 | 853.6 | 692.7 | 711.2 | 589.2 | 704.6 | 734.1 | 683 | 620.6 | 654.8 | 660.1 | 316.8 | 357.7 | 370.1 | 342.3 | 304.6 | 351.8 | 364.5 | 335.8
1216.2 | 940.2 | 469.6 | 187.84 | 219.5741 | 470 | 329 | 342.6 | 333.2 | 472.6 | 54.1 | 19 | 100.1 | 7.5 | 251 | 11.6 | 852.9 | 816.6 | 695.1 | 852.1 | 691 | 710.8 | 585.7 | 696 | 728.7 | 680.6 | 620.2 | 652.3 | 661.3 | 316.9 | 357.5 | 370.3 | 342.3 | 304.8 | 351.9 | 364.1 | 335.9
1217.2 | 941.2 | 470.6 | 188.24 | 220.0417 | 468.8 | 327.5 | 342.8 | 333.4 | 471.6 | 54.2 | 19 | 100.1 | 7.1 | 245.8 | 11.2 | 851 | 825.5 | 678.2 | 850.9 | 688.2 | 710.7 | 585.5 | 699.4 | 730.6 | 680.6 | 620 | 647 | 661.5 | 317 | 357.2 | 370.3 | 342.3 | 304.9 | 352.2 | 364.1 | 336.1
1218.2 | 942.2 | 470.7 | 188.28 | 220.0885 | 469.5 | 326.9 | 342.4 | 333.3 | 473.3 | 54.1 | 19 | 100.1 | 6.4 | 250.6 | 12.1 | 845.9 | 797.9 | 654.3 | 847.3 | 682.1 | 709.6 | 580.2 | 672.7 | 719.4 | 675.7 | 619.5 | 637.8 | 659 | 317.2 | 356.8 | 369.8 | 342.2 | 305.1 | 352.7 | 364.6 | 336.3
1219.2 | 943.2 | 469.5 | 187.8 | 219.5274 | 473.8 | 326.3 | 342.1 | 334 | 473.2 | 54.1 | 19 | 100.1 | 6.1 | 261 | 13.2 | 840.2 | 772.6 | 633.5 | 841.7 | 677.3 | 708.8 | 573.1 | 646.2 | 706.4 | 670.9 | 618.8 | 630.3 | 656.6 | 317.3 | 356.6 | 369.5 | 342.2 | 305.2 | 353.2 | 365.2 | 336.5
1220.2 | 944.2 | 469.7 | 187.88 | 219.6209 | 473.4 | 325.3 | 342.5 | 334.6 | 471.4 | 54.2 | 19 | 100.1 | 5.5 | 246.2 | 13.5 | 835.2 | 758.5 | 614.2 | 836 | 673 | 708.2 | 568.2 | 625.9 | 698.6 | 667 | 618 | 625.4 | 653.7 | 317.3 | 356.2 | 369.2 | 342.1 | 305.3 | 354.2 | 366.1 | 336.8
1221.2 | 945.2 | 471.1 | 188.44 | 220.2755 | 472.8 | 324.7 | 343.5 | 334.4 | 473.2 | 54.2 | 19 | 100.2 | 5.6 | 244.5 | 13.9 | 830.2 | 750.2 | 598.5 | 829.1 | 669.4 | 707.2 | 562.9 | 609.4 | 691.3 | 663.4 | 616.9 | 620.3 | 649.8 | 317.5 | 356 | 368.9 | 342.1 | 305.5 | 355.5 | 367.2 | 337.1
1222.2 | 946.2 | 469.6 | 187.84 | 219.5741 | 473 | 324.6 | 344.3 | 335.6 | 474.1 | 54.4 | 19 | 100.3 | 5.8 | 247 | 14.7 | 826 | 741.3 | 588.4 | 822.9 | 665.9 | 706.3 | 556.3 | 597.4 | 684.1 | 659.7 | 615.9 | 614.6 | 647.2 | 317.7 | 355.7 | 368.8 | 342.1 | 305.7 | 356 | 367.7 | 337.5
1223.2 | 947.2 | 468.6 | 187.44 | 219.1066 | 475.1 | 325.1 | 345.4 | 336.9 | 472.9 | 54.4 | 19 | 100.3 | 6.7 | 249.8 | 13.8 | 821.7 | 735.8 | 580.3 | 817.2 | 662.9 | 705.3 | 551.1 | 584.4 | 678.8 | 656.3 | 615 | 609.9 | 646.4 | 317.8 | 355.6 | 368.9 | 342.1 | 305.9 | 356.2 | 368 | 337.7
1224.2 | 948.2 | 468.4 | 187.36 | 219.013 | 477.2 | 324.9 | 346.1 | 337.1 | 473.1 | 54.5 | 19 | 100.4 | 8.1 | 254.5 | 13.4 | 817.1 | 726.6 | 573.5 | 810.7 | 658.9 | 704.3 | 547.2 | 573.1 | 675.8 | 653.4 | 614.2 | 604.9 | 642.7 | 317.8 | 355.3 | 368.7 | 342.1 | 306 | 356.6 | 368.3 | 337.9
1225.2 | 949.2 | 468 | 187.2 | 218.826 | 478.3 | 324.9 | 345.9 | 337.2 | 475 | 54.5 | 19 | 100.5 | 8.3 | 246 | 12.8 | 812.8 | 726.7 | 563.1 | 804.4 | 655.3 | 703.1 | 545.2 | 568.4 | 674 | 651 | 613.4 | 600.1 | 637.4 | 318 | 355.1 | 368.6 | 342.1 | 306.2 | 356.8 | 368.5 | 338.2
1226.2 | 950.2 | 469.7 | 187.88 | 219.6209 | 479.2 | 324.5 | 346.3 | 337.9 | 477 | 54.5 | 19 | 100.7 | 7 | 248.9 | 12.9 | 809.5 | 734.5 | 568.2 | 799 | 654.7 | 702.2 | 548.4 | 579 | 680.8 | 650.9 | 612.6 | 596.3 | 632.3 | 318.2 | 354.8 | 368.7 | 342.1 | 306.4 | 356.7 | 368.3 | 338.3
1227.2 | 951.2 | 472.6 | 189.04 | 220.9769 | 477 | 324 | 346.3 | 338.3 | 479.9 | 54.5 | 19 | 100.9 | 7 | 248.1 | 15 | 807 | 739.6 | 565.7 | 795.3 | 653.3 | 701 | 549.8 | 582.3 | 680.8 | 649.8 | 611.9 | 593.9 | 628.5 | 318.2 | 354.6 | 368.8 | 342.1 | 306.5 | 356.8 | 368.2 | 338.4
1228.2 | 952.2 | 473.7 | 189.48 | 221.4912 | 474 | 324.4 | 345.9 | 337.6 | 479.6 | 54.6 | 19 | 101.1 | 7.1 | 245.9 | 15.3 | 804 | 744.1 | 578.3 | 791.8 | 652.4 | 699.8 | 550.9 | 589.2 | 681.4 | 649 | 611.5 | 593 | 628.1 | 318.4 | 354.5 | 368.7 | 342.1 | 306.7 | 357.1 | 368.4 | 338.5
1229.2 | 953.2 | 473.7 | 189.48 | 221.4912 | 471.9 | 324.4 | 346.2 | 337.3 | 474.4 | 54.6 | 19 | 101.2 | 6.2 | 249.7 | 15.3 | 801.6 | 740.8 | 587.6 | 788.9 | 650.5 | 698.8 | 550.6 | 600.4 | 681.7 | 647.5 | 611.2 | 598 | 629.9 | 318.5 | 354.5 | 368.7 | 342.3 | 306.8 | 357 | 368.6 | 338.6
1230.2 | 954.2 | 473 | 189.2 | 221.1639 | 473.2 | 324.7 | 346 | 336.7 | 469.9 | 54.7 | 19 | 101.3 | 5.8 | 253.7 | 14.6 | 799.3 | 726.9 | 596.6 | 785.9 | 648.8 | 697.6 | 547.7 | 598.5 | 676.9 | 644.5 | 611 | 597.1 | 630 | 318.6 | 354.6 | 368.7 | 342.6 | 307 | 357.1 | 369.1 | 338.6
1231.2 | 955.2 | 472.1 | 188.84 | 220.7431 | 472.6 | 323.9 | 346 | 336.3 | 468.1 | 54.7 | 19 | 101.4 | 5.4 | 237.4 | 14.9 | 795.8 | 716.1 | 606.7 | 782.3 | 647.4 | 696.4 | 544.5 | 602.8 | 670.4 | 642.5 | 610.6 | 598.3 | 629.1 | 318.6 | 354.9 | 368.6 | 343 | 307.2 | 356.6 | 369 | 338.6
1232.2 | 956.2 | 472.5 | 189 | 220.9301 | 471.2 | 324.4 | 346.1 | 336.4 | 472.9 | 54.7 | 19 | 101.4 | 5.5 | 247.8 | 14.7 | 791.9 | 705.9 | 610.5 | 779.4 | 645.4 | 695.3 | 541.8 | 601.4 | 664.3 | 640.2 | 610.4 | 598 | 627.1 | 318.7 | 355.4 | 368.8 | 343.5 | 307.4 | 356.1 | 369.1 | 338.6
1233.2 | 957.2 | 470.6 | 188.24 | 220.0417 | 473.4 | 325.3 | 345.9 | 336.1 | 472 | 54.7 | 19 | 101.5 | 6 | 263 | 12 | 788.8 | 697.8 | 619.2 | 776.8 | 643.6 | 694 | 538.9 | 598.2 | 659.5 | 637.7 | 610 | 595.3 | 626.6 | 318.9 | 355.9 | 368.9 | 343.7 | 307.6 | 355.4 | 368.5 | 338.6
1234.2 | 958.2 | 469.1 | 187.64 | 219.3403 | 474.7 | 326 | 345.6 | 336.1 | 466.3 | 54.7 | 19 | 101.7 | 6.9 | 266.9 | 10 | 786.9 | 697.1 | 623 | 774.5 | 641.3 | 692.6 | 536.7 | 596.2 | 655.6 | 635.1 | 609.7 | 593.7 | 627.6 | 319 | 356 | 368.8 | 343.8 | 307.8 | 355 | 368.2 | 338.6
1235.2 | 959.2 | 469.2 | 187.68 | 219.3871 | 473.4 | 326.7 | 345.2 | 336.7 | 462.5 | 54.7 | 19 | 101.6 | 7.8 | 264.1 | 9.7 | 787.7 | 713.6 | 640.8 | 773.2 | 641.3 | 691.4 | 538.6 | 612.5 | 661.2 | 636.6 | 609.3 | 599.9 | 629.5 | 319.1 | 356 | 368.6 | 343.8 | 307.9 | 354.5 | 368.3 | 338.6
1236.2 | 960.2 | 469.4 | 187.76 | 219.4806 | 471.2 | 326.8 | 344.4 | 337.3 | 459.8 | 54.8 | 19 | 101.5 | 7.9 | 251.6 | 10.4 | 788 | 723.2 | 647.2 | 773 | 640.8 | 690.1 | 539.5 | 622.3 | 664 | 635.7 | 609.1 | 601.6 | 632.6 | 319.2 | 355.9 | 368.3 | 343.8 | 308.1 | 354.2 | 368.6 | 338.6
1237.2 | 961.2 | 470.4 | 188.16 | 219.9482 | 471.2 | 326.4 | 343.6 | 337.4 | 458.7 | 54.8 | 19 | 101.5 | 7.1 | 266.8 | 12.3 | 787.5 | 736.7 | 655 | 773.2 | 642.8 | 688.8 | 540.6 | 629 | 669.3 | 635 | 608.7 | 600.3 | 635 | 319.4 | 355.7 | 368.2 | 343.8 | 308.3 | 354.1 | 368.1 | 338.8
1238.2 | 962.2 | 470.2 | 188.08 | 219.8547 | 469 | 325.6 | 342.7 | 336.9 | 457.5 | 54.9 | 19 | 101.7 | 8.5 | 267.1 | 12.6 | 786 | 734.5 | 663.7 | 773.5 | 642.9 | 687.7 | 540 | 638 | 668.1 | 634.2 | 608.4 | 604.4 | 637.2 | 319.5 | 355.9 | 368.2 | 343.9 | 308.5 | 353.5 | 367.4 | 338.7
1239.2 | 963.2 | 469.9 | 187.96 | 219.7144 | 466.4 | 325.3 | 342.4 | 335.9 | 457.4 | 54.9 | 19 | 101.9 | 7.8 | 258.4 | 19.2 | 784.2 | 725.3 | 662 | 773.2 | 641.2 | 686.4 | 539.9 | 637.4 | 668 | 632.9 | 608.1 | 605.2 | 639 | 319.5 | 356.1 | 368.1 | 344.2 | 308.7 | 352.6 | 366.3 | 338.6
1240.2 | 964.2 | 470.4 | 188.16 | 219.9482 | 466.4 | 324.8 | 342 | 335 | 461 | 54.9 | 19 | 101.9 | 7.1 | 257.4 | 20.6 | 785.9 | 731.4 | 682.2 | 773.9 | 643.5 | 685.2 | 540.4 | 646.3 | 670.6 | 632.9 | 607.7 | 609.2 | 638.9 | 319.6 | 356.3 | 368 | 344.4 | 308.9 | 352.3 | 365.6 | 338.6
1241.2 | 965.2 | 470 | 188 | 219.7612 | 467.1 | 324 | 342 | 334.3 | 466.5 | 55 | 19 | 101.8 | 6.7 | 262 | 19.4 | 786.7 | 732.9 | 691.2 | 775.3 | 644.2 | 684.4 | 541.3 | 659.7 | 670.6 | 633.5 | 607.5 | 617 | 638.6 | 319.6 | 356.4 | 367.7 | 344.5 | 309 | 351.9 | 365.4 | 338.5
1242.2 | 966.2 | 470.5 | 188.2 | 219.995 | 465.9 | 323.5 | 341.8 | 334.1 | 470.2 | 55 | 19 | 101.8 | 5.4 | 262.9 | 18.7 | 786.5 | 732 | 701.7 | 777.4 | 646 | 683.4 | 544.8 | 669 | 673.5 | 634.1 | 607.3 | 623.2 | 640 | 319.7 | 356.4 | 367.3 | 344.5 | 309.2 | 351.4 | 365.1 | 338.5
1243.2 | 967.2 | 468.5 | 187.4 | 219.0598 | 464.3 | 323.7 | 341.2 | 334.9 | 475.4 | 55 | 19 | 101.8 | 5.8 | 259.2 | 17.6 | 785.4 | 730.4 | 698.3 | 778.4 | 645.4 | 682.6 | 544.4 | 670.8 | 671.1 | 633.5 | 607.2 | 627 | 640 | 319.8 | 356.4 | 367 | 344.5 | 309.5 | 351 | 364.7 | 338.4
1244.2 | 968.2 | 470.6 | 188.24 | 220.0417 | 463.2 | 324.5 | 340.1 | 335.6 | 475.1 | 55.1 | 18.9 | 101.9 | 7 | 253.1 | 17.6 | 784.7 | 730.2 | 690.9 | 779.4 | 643.4 | 681.5 | 544.9 | 667.8 | 672.1 | 632.6 | 607 | 625.7 | 641.3 | 319.9 | 356.4 | 366.6 | 344.6 | 309.6 | 350.7 | 364.6 | 338.4
1245.2 | 969.2 | 467.1 | 186.84 | 218.4052 | 460 | 326.3 | 338.3 | 336.1 | 473.5 | 55.1 | 18.9 | 102.1 | 7.8 | 242.5 | 16.6 | 784.4 | 738.1 | 684.2 | 780.3 | 644.1 | 680.6 | 546.8 | 671.5 | 675.4 | 633.6 | 606.7 | 623 | 643.8 | 320 | 356.3 | 366.1 | 344.5 | 309.7 | 350.4 | 364.3 | 338.5
1246.2 | 970.2 | 465.4 | 186.16 | 217.6103 | 456.5 | 328.4 | 337.5 | 336.5 | 474.2 | 55.2 | 18.9 | 102.2 | 7.3 | 252.5 | 15.3 | 784.1 | 742.2 | 683.8 | 781.5 | 643.3 | 679.6 | 547.2 | 671.9 | 674.6 | 632.6 | 606.5 | 621.6 | 643.7 | 320.2 | 355.9 | 365.6 | 344.5 | 310 | 350.1 | 364.1 | 338.4
1247.2 | 971.2 | 467.4 | 186.96 | 218.5455 | 453 | 328.2 | 336.6 | 336.4 | 470.6 | 55.2 | 18.9 | 102.1 | 6.8 | 250.6 | 14.5 | 783 | 745.4 | 685.3 | 782.3 | 643.1 | 678.6 | 546.7 | 669.8 | 673.6 | 631.8 | 606.3 | 622 | 642.4 | 320.1 | 355.3 | 365 | 344.4 | 310.2 | 349.8 | 364.1 | 338.4
1248.2 | 972.2 | 467.4 | 186.96 | 218.5455 | 449.4 | 327 | 335.9 | 336 | 467.1 | 55.2 | 18.9 | 102.2 | 6.3 | 251.1 | 15.6 | 782.2 | 733.1 | 691 | 782 | 643.1 | 677.9 | 544.5 | 670.7 | 668.3 | 630.8 | 606.3 | 629.7 | 640.7 | 320.2 | 355.4 | 365.2 | 344.5 | 310.4 | 349.5 | 363.7 | 338.4
1249.2 | 973.2 | 468.1 | 187.24 | 218.8728 | 446.2 | 326.7 | 336 | 334.9 | 472 | 55.2 | 18.9 | 102.1 | 5.2 | 245.9 | 16.2 | 781.6 | 719.8 | 700.5 | 781.5 | 643.5 | 677.2 | 541.7 | 668.9 | 663 | 628.9 | 606.2 | 631.7 | 638.2 | 320.4 | 355.7 | 365.9 | 344.7 | 310.5 | 349 | 363.1 | 338.3
1250.2 | 974.2 | 467.1 | 186.84 | 218.4052 | 444.8 | 327.2 | 336.7 | 334.2 | 472.2 | 55.3 | 18.9 | 102 | 5.7 | 244.8 | 15.8 | 782.4 | 713.1 | 705 | 781.4 | 642.3 | 676.5 | 539.9 | 673.8 | 661.4 | 627.6 | 606.3 | 635.5 | 636.1 | 320.2 | 355.8 | 365.7 | 344.8 | 310.8 | 348.5 | 362.7 | 338.2
1251.2 | 975.2 | 467.7 | 187.08 | 218.6857 | 445.5 | 327 | 336.8 | 333.1 | 474.1 | 55.3 | 18.9 | 102.1 | 6.6 | 247.8 | 15 | 784.5 | 718.5 | 715.4 | 781.3 | 643.3 | 676 | 540.7 | 683.6 | 666.8 | 628.4 | 606.4 | 637.6 | 635.1 | 320.5 | 356.1 | 365.8 | 344.8 | 310.9 | 348.3 | 362.5 | 338.2
1252.2 | 976.2 | 469.1 | 187.64 | 219.3403 | 444.3 | 327.4 | 335.9 | 333 | 471.7 | 55.3 | 18.9 | 102.2 | 7.1 | 241.8 | 15.1 | 787.9 | 732.4 | 719.7 | 783.5 | 645.5 | 675.6 | 545.7 | 704.6 | 679.6 | 632.8 | 606.6 | 640.7 | 637.4 | 320.8 | 356.2 | 365.9 | 344.7 | 311.1 | 348.1 | 362.1 | 338.2
1253.2 | 977.2 | 470 | 188 | 219.7612 | 443.6 | 328.1 | 336.1 | 333 | 472.5 | 55.3 | 18.9 | 102.4 | 6.3 | 264 | 14 | 790.1 | 747.5 | 716.2 | 786.7 | 646.5 | 675.7 | 555 | 723.6 | 693.5 | 637.7 | 606.9 | 641.7 | 640.6 | 321 | 356.1 | 366.8 | 344.6 | 311.2 | 348 | 361.6 | 338.2
1254.2 | 978.2 | 470 | 188 | 219.7612 | 440.3 | 328.2 | 336.6 | 332.7 | 473.6 | 55.3 | 18.9 | 102.4 | 5.9 | 251.3 | 13.1 | 789.9 | 759 | 705 | 789.5 | 647 | 675.3 | 560.9 | 711.7 | 700.6 | 639.4 | 606.9 | 635.7 | 643.2 | 321.2 | 355.9 | 367.8 | 344.4 | 311.4 | 347.8 | 361.3 | 338.3
1255.2 | 979.2 | 468.6 | 187.44 | 219.1066 | 439.8 | 327.2 | 336.9 | 332.1 | 471.4 | 55.3 | 18.9 | 102.4 | 7.3 | 256.2 | 13.4 | 790 | 771.4 | 691.9 | 792.9 | 645.5 | 674.9 | 565.1 | 707.4 | 704.8 | 640.1 | 606.9 | 631 | 646.8 | 321.4 | 355.6 | 367.5 | 344.3 | 311.5 | 347.8 | 361.1 | 338.3
1256.2 | 980.2 | 468.1 | 187.24 | 218.8728 | 439.8 | 327.1 | 336.5 | 332 | 470.9 | 55.3 | 18.9 | 102.4 | 8.1 | 250.3 | 13.3 | 789.6 | 781.2 | 685.5 | 795.2 | 646 | 674.7 | 567.3 | 705.3 | 709.1 | 641.4 | 606.8 | 624.3 | 650.3 | 321.7 | 355.5 | 367.2 | 344.2 | 311.6 | 347.7 | 360.9 | 338.4
1257.2 | 981.2 | 469 | 187.6 | 219.2936 | 439 | 327.3 | 336.5 | 331.4 | 471.4 | 55.3 | 18.9 | 102.4 | 8.7 | 247.7 | 12.7 | 787.8 | 776.5 | 668.1 | 796.1 | 644.8 | 674.3 | 566.7 | 695.3 | 705.8 | 641.1 | 606.7 | 616.9 | 650.6 | 322 | 355.2 | 366.8 | 344.1 | 311.8 | 348 | 360.8 | 338.5
1258.2 | 982.2 | 468.8 | 187.52 | 219.2001 | 439.8 | 327.8 | 336.5 | 331 | 475.1 | 55.4 | 18.9 | 102.2 | 9.3 | 242.3 | 11.3 | 785.6 | 777.4 | 652.9 | 795.4 | 641.3 | 673.9 | 566.1 | 680.4 | 699.4 | 639.9 | 606.3 | 608.3 | 648.7 | 322.1 | 355 | 366.5 | 344 | 312 | 348.5 | 361 | 338.7
1259.2 | 983.2 | 469 | 187.6 | 219.2936 | 441.8 | 327.8 | 337 | 330.5 | 475.1 | 55.4 | 18.9 | 102.2 | 8.4 | 248.7 | 11.6 | 783 | 776 | 650.2 | 794.1 | 640.2 | 673.4 | 565.3 | 669.7 | 695.5 | 638.4 | 605.9 | 602.7 | 646.6 | 322.3 | 354.8 | 366.4 | 344 | 312.2 | 348.8 | 361.3 | 338.8
1260.2 | 984.2 | 471.2 | 188.48 | 220.3223 | 443.1 | 327.8 | 338.5 | 331 | 477.3 | 55.5 | 18.9 | 102.1 | 8 | 246.2 | 14.4 | 781 | 775.7 | 648.8 | 792.5 | 638.1 | 672.9 | 562.8 | 657.7 | 691.7 | 636.5 | 605.7 | 599.8 | 644.8 | 322.3 | 354.6 | 366.3 | 343.9 | 312.5 | 349.6 | 362.2 | 338.9
1261.2 | 985.2 | 472 | 188.8 | 220.6963 | 442.7 | 327.5 | 339.7 | 331.7 | 476.8 | 55.5 | 18.9 | 102.1 | 8.1 | 240.4 | 15.1 | 782.5 | 788.4 | 662.4 | 791.8 | 640.9 | 672.6 | 566.7 | 670.3 | 697.9 | 640.6 | 605.4 | 603.2 | 644.3 | 322.5 | 354.5 | 366.2 | 343.9 | 312.7 | 350.4 | 362.9 | 339
1262.2 | 986.2 | 471.8 | 188.72 | 220.6028 | 442.1 | 327.6 | 340.4 | 332.2 | 475.9 | 55.5 | 18.9 | 102.2 | 7.8 | 241 | 16.2 | 781.7 | 784.1 | 664.5 | 791.1 | 639 | 672.2 | 566.9 | 672.4 | 698.3 | 640.1 | 605 | 604.6 | 645.3 | 322.6 | 354.7 | 366.4 | 344.1 | 312.8 | 351 | 363.5 | 339.1
1263.2 | 987.2 | 469.1 | 187.64 | 219.3403 | 443.2 | 327.1 | 341 | 333.1 | 472.1 | 55.6 | 18.9 | 102.2 | 6.3 | 239.9 | 15.7 | 781.7 | 778.3 | 663.1 | 790.6 | 637.7 | 671.9 | 564.9 | 671 | 695.2 | 638.3 | 604.8 | 608.5 | 648 | 322.5 | 354.9 | 366.4 | 344.3 | 313 | 351.4 | 363.8 | 339.2
1264.2 | 988.2 | 468.8 | 187.52 | 219.2001 | 442.4 | 326.3 | 341.3 | 332.9 | 469.8 | 55.6 | 18.9 | 102.2 | 5.6 | 248.2 | 18.2 | 780.8 | 770.9 | 656.9 | 789.4 | 636.4 | 671.6 | 560.5 | 666.4 | 689.6 | 636.6 | 604.5 | 608.8 | 649.5 | 322.7 | 355 | 366.1 | 344.4 | 313.1 | 351.5 | 363.9 | 339.3
1265.2 | 989.2 | 468.3 | 187.32 | 218.9663 | 441.5 | 325.1 | 341.1 | 331.5 | 467.1 | 55.6 | 18.9 | 102.2 | 6.2 | 246.7 | 20.8 | 782.3 | 776.9 | 674.6 | 788.5 | 638.8 | 671.5 | 559.3 | 678.3 | 691.8 | 638.9 | 604 | 614.5 | 650.5 | 322.9 | 355 | 365.9 | 344.5 | 313.2 | 351.5 | 363.7 | 339.2
1266.2 | 990.2 | 470.4 | 188.16 | 219.9482 | 440 | 323.8 | 340.7 | 330.6 | 469 | 55.5 | 18.9 | 102.2 | 7.9 | 250.4 | 20.7 | 785.3 | 769.4 | 691.2 | 788.4 | 641.8 | 671.9 | 560.7 | 700.3 | 694.1 | 640.4 | 603.6 | 627 | 651.6 | 323 | 355.1 | 365.7 | 344.7 | 313.2 | 351.3 | 363.4 | 339.2
1267.2 | 991.2 | 469.2 | 187.68 | 219.3871 | 437.9 | 323.9 | 340.4 | 330.4 | 474.7 | 55.5 | 18.9 | 102.2 | 7.6 | 249.6 | 18.4 | 786.9 | 761.2 | 697 | 789.2 | 641.2 | 672.4 | 562.6 | 714.2 | 695.3 | 642.2 | 603.5 | 635.5 | 652 | 323 | 355.2 | 365.6 | 344.8 | 313.3 | 351.1 | 363.4 | 339.1
1268.2 | 992.2 | 470 | 188 | 219.7612 | 436 | 324.9 | 340.4 | 330.7 | 477.9 | 55.5 | 18.9 | 102.1 | 7.3 | 272.1 | 17 | 785.9 | 754.6 | 691.4 | 790.2 | 639.3 | 672.7 | 562.7 | 718 | 694.2 | 641.3 | 603.4 | 636.7 | 654.7 | 323.2 | 355.5 | 366 | 345 | 313.4 | 351.4 | 363.5 | 339.1
1269.2 | 993.2 | 469.8 | 187.92 | 219.6677 | 434.6 | 325.4 | 341.1 | 331 | 484.6 | 55.5 | 18.9 | 102 | 7.6 | 251.7 | 16 | 784.6 | 746 | 686.6 | 789.7 | 637.1 | 672.9 | 561.1 | 711.9 | 692 | 639.2 | 603.5 | 631.5 | 657.4 | 323.4 | 356 | 366.6 | 345.3 | 313.6 | 351.5 | 363.9 | 339.2
1270.2 | 994.2 | 470 | 188 | 219.7612 | 433.3 | 325.3 | 341.8 | 331.9 | 483.9 | 55.6 | 18.9 | 101.9 | 7.3 | 243.8 | 16.7 | 784.6 | 744 | 686.1 | 790.1 | 638.2 | 672.8 | 557.1 | 700 | 688.4 | 637.4 | 603.6 | 627.5 | 660.1 | 323.5 | 356.3 | 367 | 345.5 | 313.7 | 351.2 | 364 | 339.1
1271.2 | 995.2 | 467.2 | 186.88 | 218.452 | 434.3 | 324.4 | 342.4 | 332.6 | 479 | 55.6 | 18.9 | 101.7 | 6.8 | 240.6 | 17 | 781.2 | 733.5 | 678.7 | 789 | 636.3 | 672.4 | 553.5 | 682.7 | 681.2 | 634.7 | 603.4 | 625.7 | 662.4 | 323.7 | 356.6 | 367.4 | 345.6 | 313.8 | 351.1 | 364 | 339.1
1272.2 | 996.2 | 466.8 | 186.72 | 218.2649 | 436.1 | 324.6 | 342.6 | 333.2 | 479.7 | 55.7 | 18.9 | 101.7 | 7.6 | 244.2 | 18 | 780.8 | 730.6 | 680.6 | 787.6 | 636.4 | 672.2 | 551.1 | 680.9 | 676.6 | 633.3 | 603 | 626.6 | 663 | 323.7 | 357.2 | 368.2 | 345.9 | 313.8 | 351.2 | 364.2 | 339.1
1273.2 | 997.2 | 466 | 186.4 | 217.8909 | 437.5 | 325.7 | 343.2 | 333.8 | 478.2 | 55.7 | 18.9 | 101.7 | 7.2 | 262.1 | 18.6 | 781 | 727.4 | 683.3 | 787.1 | 635.5 | 671.9 | 550.4 | 686.2 | 677.5 | 633 | 602.6 | 629.7 | 663.4 | 323.9 | 357.5 | 368.5 | 345.9 | 313.9 | 351 | 364.7 | 339.1
1274.2 | 998.2 | 466.9 | 186.76 | 218.3117 | 437.8 | 326.7 | 343.8 | 335 | 480.1 | 55.8 | 18.9 | 101.7 | 9.2 | 259.3 | 16 | 780.9 | 720.5 | 696.8 | 786.9 | 635.9 | 671.8 | 549.6 | 690.4 | 675.2 | 632.4 | 601.9 | 636.2 | 663 | 324.2 | 358 | 368.8 | 346.1 | 314 | 350.8 | 364.8 | 339.1
1275.2 | 999.2 | 468.8 | 187.52 | 219.2001 | 436.6 | 327.2 | 343.4 | 335.9 | 482.2 | 55.8 | 18.9 | 101.8 | 8.2 | 258.5 | 15.1 | 780.2 | 718.4 | 694.3 | 786.8 | 635.8 | 671.7 | 550.2 | 689 | 674.3 | 632 | 601.5 | 634.4 | 663.3 | 324.3 | 358.4 | 369.4 | 346.2 | 314.1 | 350.6 | 365.7 | 339.1
1276.2 | 1000.2 | 467.7 | 187.08 | 218.6857 | 438.4 | 327.5 | 343 | 336 | 480.9 | 55.9 | 18.9 | 101.8 | 6.8 | 252.7 | 18.4 | 779.6 | 717.4 | 686.6 | 786.7 | 634 | 671.2 | 548.6 | 680.2 | 672.6 | 630.2 | 601 | 631.3 | 665.7 | 324.2 | 358.8 | 370.3 | 346.2 | 314.2 | 350.6 | 365.5 | 339.1
1277.2 | 1001.2 | 467.4 | 186.96 | 218.5455 | 440.1 | 328.5 | 343.1 | 335.6 | 477.8 | 55.9 | 18.9 | 101.8 | 6.9 | 252 | 18.4 | 779.7 | 720.3 | 680.2 | 786.6 | 632.5 | 670.6 | 546.1 | 674 | 671.6 | 629.5 | 600.8 | 627.1 | 667.6 | 324.4 | 359 | 370.5 | 346.3 | 314.4 | 350.6 | 365.2 | 339.1
1278.2 | 1002.2 | 468.7 | 187.48 | 219.1533 | 444.4 | 328.9 | 343.1 | 334.9 | 472.1 | 55.9 | 18.9 | 101.8 | 6.7 | 254.6 | 18.1 | 778.1 | 718.2 | 675.7 | 786.3 | 630.9 | 669.9 | 542.9 | 665.4 | 668 | 627.4 | 600.5 | 619.3 | 669.4 | 324.7 | 358.9 | 370.4 | 346.2 | 314.6 | 350.5 | 364.8 | 339.2
1279.2 | 1003.2 | 469 | 187.6 | 219.2936 | 447.8 | 330 | 342.5 | 334.5 | 466.4 | 56 | 18.9 | 101.9 | 6.5 | 259.9 | 15.9 | 776.5 | 709 | 671.2 | 785.6 | 629.3 | 669 | 540 | 651.7 | 665 | 625.1 | 600 | 612.7 | 670.6 | 324.9 | 358.8 | 370.4 | 346.1 | 314.8 | 350.3 | 364.6 | 339.2
1280.2 | 1004.2 | 468.3 | 187.32 | 218.9663 | 449.1 | 331.1 | 341.8 | 334.5 | 462.9 | 55.9 | 18.9 | 102 | 6.8 | 269.5 | 14.2 | 774.2 | 708.4 | 655 | 784.6 | 626.9 | 668.2 | 534.8 | 638 | 659.2 | 622.8 | 599.7 | 606.2 | 673.2 | 325 | 358.7 | 370.4 | 346.2 | 315 | 350.2 | 364.3 | 339.2
1281.2 | 1005.2 | 468.3 | 187.32 | 218.9663 | 450.2 | 330.6 | 341.5 | 334.2 | 460.5 | 55.9 | 18.9 | 102.1 | 6.6 | 253.3 | 14.9 | 772.1 | 714.2 | 639.2 | 783.6 | 624.2 | 667.3 | 533.6 | 629.6 | 656.2 | 621.4 | 599 | 599.7 | 678.6 | 325.3 | 358.4 | 370.2 | 346.2 | 315.1 | 350 | 364.1 | 339.2
1282.2 | 1006.2 | 468.1 | 187.24 | 218.8728 | 454 | 329.6 | 341.3 | 333.3 | 460.1 | 55.9 | 18.9 | 102.1 | 6.5 | 263.2 | 16.1 | 771.1 | 709.3 | 636.7 | 782.4 | 621.9 | 666.4 | 532.1 | 622.5 | 654.2 | 619.3 | 598.4 | 594.7 | 684 | 325.6 | 358.1 | 370.1 | 346.1 | 315.2 | 349.7 | 363.9 | 339.2
1283.2 | 1007.2 | 467.5 | 187 | 218.5922 | 453.7 | 329.8 | 340.9 | 332.6 | 459.8 | 56 | 18.9 | 102 | 6.9 | 268.9 | 16.3 | 769.4 | 703 | 635.8 | 781.4 | 620.9 | 665.6 | 531.7 | 619.8 | 654.2 | 618 | 597.8 | 592.4 | 686 | 325.6 | 357.8 | 369.7 | 346 | 315.3 | 349.6 | 363.6 | 339.3
1284.2 | 1008.2 | 469.8 | 187.92 | 219.6677 | 452.7 | 329.7 | 340.7 | 332.5 | 458.1 | 56 | 18.9 | 102 | 6 | 262.1 | 15.3 | 770 | 711.7 | 654.5 | 779.7 | 620.9 | 664.6 | 531.1 | 616.1 | 652.7 | 617.1 | 597.2 | 590.6 | 685.5 | 325.7 | 357.4 | 369.1 | 345.9 | 315.4 | 349.5 | 363.9 | 339.3
1285.2 | 1009.2 | 469 | 187.6 | 219.2936 | 451.8 | 329.7 | 339.9 | 332.6 | 456.1 | 56 | 18.9 | 101.9 | 6.9 | 257 | 13.9 | 771.4 | 726.1 | 659.7 | 780 | 622.8 | 664.1 | 534.3 | 632.6 | 658.3 | 619 | 596.5 | 593.3 | 684.9 | 325.9 | 357 | 368.4 | 345.8 | 315.6 | 349.3 | 363.6 | 339.4
1286.2 | 1010.2 | 469.7 | 187.88 | 219.6209 | 449.1 | 329.7 | 338.6 | 332.9 | 456.8 | 56 | 18.9 | 101.9 | 6.5 | 260.2 | 15.4 | 772 | 744 | 658.6 | 781.1 | 623.3 | 663.5 | 540.7 | 643.1 | 667.6 | 622.6 | 595.8 | 589 | 683.7 | 326.1 | 356.8 | 367.9 | 345.7 | 315.6 | 349.2 | 363.5 | 339.4
1287.2 | 1011.2 | 468.1 | 187.24 | 218.8728 | 446.8 | 329.5 | 337.7 | 333 | 459.5 | 56 | 18.9 | 102 | 6.6 | 256.2 | 15.9 | 772.1 | 740.4 | 661.6 | 782.1 | 623.2 | 662.9 | 540.4 | 641.2 | 668.5 | 622.4 | 595.5 | 587.8 | 682.3 | 326.4 | 356.6 | 367.6 | 345.7 | 315.7 | 349.3 | 363.6 | 339.5
1288.2 | 1012.2 | 468 | 187.2 | 218.826 | 446.4 | 328.4 | 337.4 | 332.9 | 458.3 | 56 | 18.9 | 102.2 | 6.9 | 255.9 | 17.1 | 771 | 741.9 | 665.9 | 782.1 | 622.7 | 662.1 | 540 | 631.6 | 666.2 | 620.9 | 595.2 | 583.4 | 680.1 | 326.5 | 356.2 | 367.4 | 345.6 | 316 | 349.5 | 363.5 | 339.5
1289.2 | 1013.2 | 469.9 | 187.96 | 219.7144 | 446.7 | 327.7 | 337.1 | 332.4 | 455.9 | 55.9 | 18.9 | 102.4 | 7.5 | 237.4 | 13.4 | 768.8 | 731.8 | 660.9 | 781.7 | 621.3 | 661.1 | 536.3 | 618.4 | 658.8 | 618.3 | 594.8 | 581.7 | 679 | 326.6 | 355.9 | 367.2 | 345.7 | 316.1 | 349.9 | 363.6 | 339.6
1290.2 | 1014.2 | 468.1 | 187.24 | 218.8728 | 448 | 327.2 | 336.9 | 332.2 | 450.9 | 55.9 | 18.9 | 102.6 | 8.6 | 235.6 | 9.8 | 768.9 | 727 | 663.2 | 781.2 | 622.3 | 660.3 | 533.8 | 617.6 | 655 | 617.1 | 594.3 | 584.8 | 679 | 326.8 | 355.6 | 366.7 | 345.7 | 316.2 | 350 | 363.8 | 339.7
1291.2 | 1015.2 | 469.4 | 187.76 | 219.4806 | 450.2 | 326 | 336.5 | 332.3 | 450.3 | 55.8 | 18.9 | 102.8 | 7.5 | 268.8 | 11.1 | 766.4 | 718.8 | 648.4 | 779.7 | 618.8 | 659.5 | 532.1 | 610.2 | 652 | 615.2 | 594.3 | 580 | 679.7 | 326.9 | 355.3 | 366.1 | 345.7 | 316.3 | 350.4 | 363.9 | 339.8
1292.2 | 1016.2 | 469.4 | 187.76 | 219.4806 | 446.9 | 324.9 | 335.9 | 332.2 | 450.5 | 55.8 | 18.9 | 102.9 | 6.8 | 261.5 | 14.2 | 763.5 | 711.2 | 633.6 | 777.5 | 616.1 | 658.5 | 530.8 | 598.2 | 650 | 612.8 | 594 | 574.1 | 678.6 | 327.1 | 354.9 | 365.6 | 345.5 | 316.3 | 350.8 | 363.7 | 339.9
1293.2 | 1017.2 | 469.4 | 187.76 | 219.4806 | 447.3 | 323.7 | 335.5 | 332.1 | 450.7 | 55.8 | 18.9 | 103 | 8.7 | 258.1 | 14.1 | 760 | 706.2 | 620 | 774.5 | 613.2 | 657.5 | 529.3 | 585.3 | 646 | 610.3 | 593.6 | 569.7 | 677.3 | 327.3 | 354.6 | 365.3 | 345.3 | 316.4 | 351.4 | 364 | 340
1294.2 | 1018.2 | 469.1 | 187.64 | 219.3403 | 453.5 | 323.3 | 335.6 | 331.8 | 452.8 | 55.8 | 18.9 | 103 | 8 | 251.8 | 13.4 | 756.4 | 700.6 | 603 | 770.9 | 609.8 | 656.5 | 528.1 | 577.5 | 642 | 608.4 | 593.4 | 565.1 | 676.2 | 327.3 | 354.3 | 365.1 | 345.1 | 316.4 | 351.7 | 364.5 | 340.2
1295.2 | 1019.2 | 469.6 | 187.84 | 219.5741 | 453.4 | 323.2 | 336.3 | 332.3 | 450.2 | 55.9 | 18.9 | 103.1 | 7.7 | 240.9 | 13.2 | 752.2 | 685.2 | 590.8 | 766.2 | 606.4 | 655.4 | 522.6 | 562.1 | 633.1 | 604.8 | 592.9 | 560.4 | 674 | 327.4 | 354.3 | 365 | 345.1 | 316.5 | 351.7 | 364.7 | 340.2
1296.2 | 1020.2 | 469.5 | 187.8 | 219.5274 | 451.6 | 323.9 | 337.1 | 333.1 | 447.6 | 55.9 | 18.9 | 103.1 | 7.8 | 240.1 | 15.9 | 747.9 | 672.6 | 577.6 | 760.6 | 603.1 | 654.1 | 518 | 548.3 | 626.3 | 601.6 | 592.6 | 555.7 | 670.6 | 327.6 | 354 | 365.2 | 345 | 316.7 | 351.9 | 365.1 | 340.3
1297.2 | 1021.2 | 469.8 | 187.92 | 219.6677 | 451.8 | 324.7 | 337.7 | 333.2 | 443.9 | 55.9 | 18.8 | 103.2 | 7.2 | 245.2 | 18.4 | 743.7 | 663 | 564.8 | 754.9 | 599.8 | 652.8 | 514.8 | 538.2 | 623.3 | 599 | 592.3 | 551.6 | 666.5 | 327.8 | 353.3 | 365 | 344.9 | 316.8 | 352.2 | 365 | 340.5
1298.2 | 1022.2 | 469.6 | 187.84 | 219.5741 | 452 | 324.8 | 337.4 | 334.1 | 442.1 | 56 | 18.8 | 103.3 | 7.7 | 242 | 16.8 | 739.8 | 654.3 | 555.2 | 749.3 | 596.6 | 651.5 | 512.6 | 530.2 | 620.6 | 596.1 | 592 | 547 | 663 | 327.8 | 353 | 365.1 | 344.8 | 317 | 352.3 | 364.9 | 340.6
1299.2 | 1023.2 | 468.6 | 187.44 | 219.1066 | 450.9 | 325.4 | 336.9 | 334.8 | 441 | 56 | 18.8 | 103.5 | 7.3 | 241.1 | 15.9 | 735.4 | 642.8 | 547.4 | 743.2 | 593.6 | 650.1 | 509.1 | 522 | 616.9 | 593.1 | 591.3 | 542.4 | 660.6 | 328 | 352.7 | 365.1 | 344.8 | 317.1 | 352.2 | 364.4 | 340.6
1300.2 | 1024.2 | 469.8 | 187.92 | 219.6677 | 447.7 | 325.7 | 336.9 | 334.8 | 436.8 | 56 | 18.8 | 103.5 | 8.9 | 243.5 | 16.9 | 731.2 | 636.1 | 548.3 | 737.3 | 591.2 | 648.7 | 506 | 514.3 | 612.4 | 590.7 | 590.7 | 538.6 | 659.2 | 328 | 352.3 | 365.1 | 344.6 | 317.2 | 352 | 364 | 340.6
1301.2 | 1025.2 | 470.3 | 188.12 | 219.9014 | 446.2 | 324.7 | 337.2 | 334.1 | 433 | 56 | 18.8 | 103.7 | 7.4 | 241.8 | 17.2 | 727.9 | 644 | 556.9 | 732.3 | 589.4 | 647.4 | 504.9 | 521.5 | 614.3 | 589.2 | 589.9 | 536.1 | 661.5 | 328.1 | 351.7 | 364.1 | 344.6 | 317.3 | 351.8 | 363.5 | 340.7
1302.2 | 1026.2 | 470.7 | 188.28 | 220.0885 | 445.2 | 323.4 | 336.6 | 333.7 | 433.7 | 56 | 18.8 | 103.9 | 7 | 245.5 | 15.9 | 725.9 | 655.1 | 571.5 | 728.6 | 590.1 | 646.3 | 505.6 | 528.7 | 616.1 | 588.9 | 589.9 | 537 | 665.1 | 328.4 | 351.2 | 363.2 | 344.7 | 317.4 | 351.8 | 363.2 | 340.6
1303.2 | 1027.2 | 469.3 | 187.72 | 219.4339 | 442 | 322.8 | 335.6 | 333.3 | 434.5 | 56 | 18.8 | 104 | 7.3 | 254.6 | 14.2 | 726.2 | 661.3 | 583.2 | 725.7 | 589.8 | 645.1 | 505.8 | 538.3 | 615.8 | 587.9 | 589.4 | 542 | 668.8 | 328.6 | 350.7 | 362.3 | 344.7 | 317.6 | 351.5 | 362.5 | 340.6
1304.2 | 1028.2 | 469.3 | 187.72 | 219.4339 | 439.7 | 323.6 | 334.6 | 332.8 | 433.3 | 56 | 18.8 | 104.1 | 7.3 | 251.3 | 14.3 | 727.7 | 668.5 | 590.2 | 724.4 | 591.3 | 644 | 508.2 | 553.4 | 619.6 | 588.2 | 589 | 545.2 | 672.7 | 328.7 | 350.2 | 361.5 | 344.8 | 317.7 | 351.3 | 362 | 340.5
1305.2 | 1029.2 | 470.2 | 188.08 | 219.8547 | 442 | 325 | 333.5 | 331.8 | 434.2 | 56 | 18.8 | 104.4 | 6.8 | 237.8 | 14.3 | 727 | 677.3 | 604.8 | 724.4 | 593.4 | 643 | 510.3 | 573.4 | 624.3 | 588.9 | 588.7 | 549.9 | 675.9 | 328.6 | 349.7 | 360.6 | 344.7 | 317.8 | 350.9 | 361.6 | 340.4
1306.2 | 1030.2 | 470.2 | 188.08 | 219.8547 | 440.9 | 325.7 | 332.6 | 331.1 | 435.8 | 55.9 | 18.8 | 104.5 | 6.1 | 250.2 | 13.7 | 727.5 | 680.1 | 618.8 | 725.1 | 596.2 | 642 | 511.6 | 582.3 | 626.1 | 589.3 | 588.9 | 552.7 | 678.2 | 328.9 | 349.3 | 359.9 | 344.6 | 318 | 350.7 | 361.2 | 340.3
1307.2 | 1031.2 | 470.3 | 188.12 | 219.9014 | 437.3 | 326.8 | 331.3 | 331.1 | 435.6 | 56 | 18.8 | 104.6 | 6.7 | 252.6 | 13.1 | 729.9 | 692.1 | 636.6 | 727.3 | 600.5 | 641.1 | 515.6 | 601.4 | 632.5 | 592.3 | 589.5 | 558.2 | 677.9 | 329.1 | 348.9 | 359.4 | 344.5 | 318.1 | 350.4 | 360.7 | 340.3
1308.2 | 1032.2 | 470.7 | 188.28 | 220.0885 | 436.9 | 326.9 | 329.8 | 330.9 | 436.4 | 55.9 | 18.8 | 104.8 | 6.5 | 251.2 | 12.9 | 728.4 | 704.3 | 643.3 | 729.6 | 600.8 | 640.2 | 520 | 611.9 | 638.8 | 592.8 | 590.7 | 560 | 677.3 | 329.3 | 348.9 | 359.8 | 344.5 | 318.2 | 350 | 360.3 | 340.2
1309.2 | 1033.2 | 470.4 | 188.16 | 219.9482 | 433.2 | 327 | 329.2 | 330.5 | 439.6 | 55.9 | 18.8 | 105 | 6.8 | 261.4 | 11.2 | 727.3 | 714.6 | 646 | 731.2 | 601.6 | 639.4 | 522.6 | 610.8 | 641.3 | 593 | 591.2 | 558.4 | 676.6 | 329.3 | 349.3 | 359.9 | 344.5 | 318.3 | 349.7 | 359.8 | 340.2
1310.2 | 1034.2 | 470.9 | 188.36 | 220.182 | 431.2 | 327.1 | 329.8 | 330.4 | 441.2 | 55.9 | 18.8 | 105.1 | 7.3 | 250 | 11.6 | 728.5 | 719.6 | 653.4 | 733.4 | 603.7 | 638.6 | 524.6 | 617.3 | 644 | 593.7 | 591.8 | 561.3 | 674.8 | 329.3 | 349.5 | 360.1 | 344.6 | 318.3 | 349.4 | 359.5 | 340.2
1311.2 | 1035.2 | 470.1 | 188.04 | 219.8079 | 430.1 | 327.2 | 330 | 329.6 | 440.9 | 55.9 | 18.8 | 105.2 | 6.9 | 250.6 | 12.5 | 728.6 | 721 | 653.4 | 734.9 | 603.8 | 637.8 | 524.5 | 615.2 | 641.1 | 592.2 | 592.5 | 564.3 | 672.8 | 329.4 | 349.8 | 360.2 | 344.7 | 318.4 | 349.1 | 359.5 | 340.1
1312.2 | 1036.2 | 470.3 | 188.12 | 219.9014 | 429.1 | 328.9 | 329.9 | 329 | 441.9 | 56 | 18.8 | 105.4 | 6.4 | 248.2 | 14.2 | 728 | 718.4 | 663.8 | 736 | 605 | 637.2 | 525.1 | 623.6 | 641.7 | 592.4 | 593.7 | 569.9 | 670.6 | 329.6 | 350.1 | 360.2 | 344.9 | 318.5 | 348.9 | 359.4 | 340.1
1313.2 | 1037.2 | 470.4 | 188.16 | 219.9482 | 427.6 | 329.7 | 330.2 | 328.8 | 442.8 | 56 | 18.8 | 105.5 | 6.7 | 253.2 | 14.4 | 730.6 | 723.1 | 671.3 | 737.6 | 607.5 | 636.5 | 527.1 | 625.2 | 643.6 | 593 | 594.8 | 570.1 | 669.9 | 329.8 | 350.2 | 360.4 | 344.9 | 318.6 | 348.8 | 359.2 | 340
1314.2 | 1038.2 | 470.1 | 188.04 | 219.8079 | 428.2 | 330.5 | 330.7 | 328.8 | 440.6 | 56 | 18.8 | 105.6 | 6.5 | 263.5 | 15.2 | 733.4 | 731.1 | 674.5 | 740 | 608.9 | 635.9 | 528.1 | 634.4 | 646 | 593.4 | 596 | 573.1 | 669.8 | 329.9 | 350.3 | 360.6 | 345 | 318.6 | 348.6 | 359 | 340
1315.2 | 1039.2 | 470 | 188 | 219.7612 | 426.9 | 331.1 | 330.8 | 328.6 | 441 | 55.9 | 18.8 | 105.7 | 7.1 | 258.4 | 15.4 | 733.1 | 732 | 671.9 | 742.5 | 607.6 | 635.2 | 528.7 | 632.4 | 645.9 | 592.6 | 596.8 | 570.8 | 670.5 | 330 | 350.4 | 360.7 | 345 | 318.7 | 348.8 | 359.2 | 339.9
1316.2 | 1040.2 | 468.9 | 187.56 | 219.2468 | 425.8 | 331.6 | 330.7 | 328.6 | 440.5 | 55.9 | 18.8 | 105.6 | 8.1 | 262.5 | 13 | 731.8 | 728.5 | 670.5 | 744.1 | 607 | 634.6 | 528.7 | 627.6 | 646 | 592.4 | 597.7 | 569.2 | 671.8 | 330.1 | 350.5 | 360.7 | 345 | 318.9 | 349.1 | 359.5 | 339.9
1317.2 | 1041.2 | 469.8 | 187.92 | 219.6677 | 427.5 | 331.8 | 330.8 | 329.3 | 438.9 | 55.9 | 18.8 | 105.5 | 7.1 | 262.8 | 12.3 | 731.6 | 732.3 | 681.5 | 745.5 | 608.2 | 634 | 529.1 | 629.7 | 649.3 | 592.9 | 599.3 | 567.3 | 673.6 | 330.1 | 350.5 | 360.6 | 344.8 | 319 | 349.2 | 359.4 | 339.9
1318.2 | 1042.2 | 469.2 | 187.68 | 219.3871 | 428.5 | 331.1 | 330.7 | 329.4 | 441 | 56 | 18.8 | 105.3 | 5.6 | 254.1 | 12.6 | 733.2 | 735.9 | 686.8 | 748 | 610.8 | 633.8 | 532.5 | 644.2 | 655 | 595.3 | 600.2 | 574.2 | 674.2 | 330.2 | 350.5 | 360.4 | 344.8 | 319.1 | 349.2 | 359.2 | 340
1319.2 | 1043.2 | 469.7 | 187.88 | 219.6209 | 428.7 | 330.5 | 330.3 | 329.2 | 442.2 | 56 | 18.8 | 105.3 | 6.4 | 266.2 | 10.6 | 736.8 | 749 | 700 | 751.4 | 614 | 633.7 | 538.8 | 665.2 | 663.4 | 599.3 | 600.6 | 583 | 674.1 | 330.4 | 350.4 | 360.1 | 344.7 | 319.2 | 349.1 | 359.3 | 340
1320.2 | 1044.2 | 469.9 | 187.96 | 219.7144 | 428.2 | 331.3 | 330 | 329.7 | 445 | 56 | 18.8 | 105.3 | 7.8 | 256.4 | 9.5 | 738.9 | 755.7 | 702.7 | 755.3 | 615.7 | 634 | 547 | 680.9 | 675.2 | 603.6 | 602.4 | 584.8 | 673.8 | 330.6 | 350.3 | 359.9 | 344.7 | 319.3 | 349.2 | 359.1 | 340
1321.2 | 1045.2 | 469 | 187.6 | 219.2936 | 428.1 | 331.5 | 330 | 330.5 | 452.2 | 56 | 18.8 | 105.4 | 10.9 | 247.7 | 12.9 | 740.5 | 762.7 | 698.9 | 759.7 | 616.9 | 634.7 | 558.8 | 687.6 | 687.1 | 609.5 | 605.2 | 580.4 | 672.6 | 330.8 | 350.3 | 359.9 | 344.6 | 319.3 | 349.5 | 359.3 | 340.1
1322.2 | 1046.2 | 468.4 | 187.36 | 219.013 | 427.9 | 331.4 | 330.1 | 330.7 | 459.8 | 56 | 18.8 | 105.5 | 9.1 | 240.6 | 14.6 | 740.5 | 763.5 | 696.1 | 763.2 | 618 | 634.9 | 561.2 | 686.9 | 687.5 | 610.7 | 607.5 | 579.4 | 671.4 | 330.8 | 350.3 | 360.1 | 344.4 | 319.4 | 349.7 | 359.6 | 340.2
1323.2 | 1047.2 | 470 | 188 | 219.7612 | 431.9 | 331.3 | 331 | 331.2 | 457.6 | 56 | 18.8 | 105.4 | 8.4 | 240.5 | 13 | 739.6 | 756.1 | 687.7 | 765.3 | 616.3 | 634.8 | 558.5 | 669.9 | 680.4 | 609.4 | 609.8 | 577.9 | 670.8 | 330.9 | 350.3 | 360.3 | 344.3 | 319.5 | 349.8 | 359.9 | 340.3
1324.2 | 1048.2 | 470.6 | 188.24 | 220.0417 | 434.5 | 331.7 | 331.5 | 331.7 | 453.6 | 56.1 | 18.8 | 105.2 | 7 | 255.4 | 10 | 741 | 755.6 | 683.1 | 767.6 | 618.3 | 634.6 | 555.1 | 661.6 | 676 | 609.1 | 611.7 | 574.4 | 671 | 331 | 350.2 | 360.4 | 344.3 | 319.6 | 349.9 | 360.2 | 340.3
1325.2 | 1049.2 | 470 | 188 | 219.7612 | 434.1 | 332.1 | 331.5 | 331.9 | 451.3 | 56.1 | 18.8 | 105 | 6.2 | 241.8 | 11.4 | 740.7 | 756.5 | 670.8 | 769.1 | 616.8 | 634.5 | 553.6 | 654.1 | 674.8 | 608.4 | 613.9 | 570 | 671 | 331.1 | 350 | 360.3 | 344.2 | 319.7 | 350.2 | 360.2 | 340.3
1326.2 | 1050.2 | 469.3 | 187.72 | 219.4339 | 433.2 | 331.7 | 331.7 | 331.8 | 449.5 | 56.1 | 18.8 | 104.8 | 6.5 | 243.7 | 16.1 | 740.1 | 751.1 | 661.3 | 769.6 | 614.7 | 634.4 | 551 | 644 | 670.5 | 606.5 | 616.8 | 564 | 669.3 | 331.3 | 349.8 | 360.1 | 344.1 | 319.8 | 350.5 | 360.5 | 340.4
1327.2 | 1051.2 | 469.5 | 187.8 | 219.5274 | 432.8 | 331.9 | 331.4 | 331.9 | 449.5 | 56.1 | 18.8 | 104.8 | 7 | 249.5 | 15.8 | 737.9 | 740.8 | 646.2 | 768.3 | 612.2 | 634.1 | 547.7 | 622.8 | 663.2 | 603.7 | 618.3 | 557.4 | 666.9 | 331.4 | 349.7 | 360.1 | 344 | 319.9 | 350.9 | 360.8 | 340.6
1328.2 | 1052.2 | 470.7 | 188.28 | 220.0885 | 434.4 | 332.4 | 331.5 | 332 | 451.8 | 56.1 | 18.8 | 104.9 | 8.4 | 252.1 | 14 | 735.9 | 744.5 | 633.5 | 766.7 | 610 | 634 | 549.3 | 617.8 | 665.3 | 603.7 | 619.6 | 552.5 | 665.2 | 331.3 | 349.6 | 360.5 | 343.9 | 320 | 351.3 | 361.1 | 340.7
1329.2 | 1053.2 | 470.3 | 188.12 | 219.9014 | 435.1 | 333.3 | 332 | 331.8 | 457.4 | 56.1 | 18.8 | 105.1 | 8.2 | 253.8 | 12.5 | 737.5 | 751.6 | 637.6 | 766.2 | 611.5 | 634 | 550.3 | 619 | 667.1 | 604 | 621 | 550.3 | 664.1 | 331.5 | 349.4 | 361 | 343.8 | 320.1 | 351.7 | 361.7 | 340.9
1330.2 | 1054.2 | 470.3 | 188.12 | 219.9014 | 435.4 | 334.1 | 333.3 | 332.4 | 456.7 | 56.1 | 18.8 | 105.2 | 8 | 252.1 | 11.3 | 737.5 | 760.4 | 632.4 | 765.6 | 611.1 | 634 | 551.5 | 615.2 | 668.4 | 604.5 | 622 | 547 | 661.7 | 331.7 | 349.1 | 360.9 | 343.8 | 320.2 | 352.2 | 362.5 | 341
1331.2 | 1055.2 | 469.6 | 187.84 | 219.5741 | 433.8 | 335.4 | 334.1 | 333.3 | 458 | 56.1 | 18.8 | 105.3 | 6 | 239.2 | 10.4 | 737.4 | 761.7 | 622.6 | 765.5 | 609.2 | 634 | 553.3 | 618.5 | 669.4 | 604.8 | 622.1 | 545.7 | 658.5 | 331.9 | 349 | 361.1 | 343.7 | 320.3 | 352.8 | 363.3 | 341.1
1332.2 | 1056.2 | 469.9 | 187.96 | 219.7144 | 434 | 336.8 | 334.7 | 333.7 | 461.2 | 56.1 | 18.8 | 105.4 | 5.9 | 228 | 9.7 | 735.7 | 763.3 | 608.7 | 764.7 | 606.9 | 634.1 | 555.6 | 614.7 | 673.9 | 605.6 | 624.6 | 541.2 | 654.8 | 332.1 | 349 | 361.3 | 343.7 | 320.4 | 353.8 | 364.1 | 341.3
1333.2 | 1057.2 | 470.3 | 188.12 | 219.9014 | 434.4 | 337.6 | 335.5 | 334.4 | 473.2 | 56.1 | 18.8 | 105.3 | 7.4 | 242 | 11.4 | 735.9 | 768 | 608.3 | 763.9 | 606.8 | 634.2 | 559.4 | 615.8 | 674.8 | 607 | 625.4 | 539 | 650.6 | 332.2 | 349.1 | 361.5 | 343.6 | 320.5 | 354.8 | 365.6 | 341.5
1334.2 | 1058.2 | 469.3 | 187.72 | 219.4339 | 433.2 | 338.4 | 336.4 | 335 | 486.7 | 56.1 | 18.8 | 105.4 | 9.2 | 246.7 | 15.7 | 741.2 | 775.5 | 640.2 | 765.3 | 612.6 | 635.4 | 572.5 | 649.7 | 689 | 615.1 | 626.4 | 548.9 | 647 | 332.2 | 349.3 | 361.7 | 343.7 | 320.6 | 355.2 | 366.3 | 341.6
1335.2 | 1059.2 | 468.5 | 187.4 | 219.0598 | 431.4 | 338.5 | 337.1 | 335.2 | 488.2 | 56.2 | 18.8 | 105.5 | 8.1 | 246.3 | 16 | 746.4 | 782.6 | 679.9 | 767.6 | 620.7 | 636.9 | 579.4 | 684.2 | 698.4 | 619.8 | 625.6 | 568.1 | 643 | 332.3 | 349.6 | 361.9 | 343.9 | 320.7 | 355.3 | 367 | 341.6
1336.2 | 1060.2 | 469.7 | 187.88 | 219.6209 | 429.2 | 339.8 | 337.7 | 335.6 | 486.5 | 56.2 | 18.8 | 105.5 | 6.6 | 238 | 14.2 | 750.7 | 794.9 | 699.2 | 770.6 | 626.6 | 638.5 | 585.7 | 714.8 | 709.2 | 626.7 | 622.7 | 583.1 | 638.2 | 332.4 | 350 | 362 | 344.1 | 320.8 | 355.6 | 368.3 | 341.7
1337.2 | 1061.2 | 469.3 | 187.72 | 219.4339 | 426.7 | 341 | 338.1 | 335.8 | 484.7 | 56.2 | 18.8 | 105.3 | 5.6 | 244.5 | 13.2 | 756.5 | 796.7 | 725.3 | 773.7 | 633.1 | 640.1 | 591.6 | 737.2 | 717.7 | 633 | 618.4 | 597.6 | 633.5 | 332.5 | 350.3 | 362 | 344.2 | 321 | 355.3 | 368.4 | 341.8
1338.2 | 1062.2 | 469.7 | 187.88 | 219.6209 | 425.2 | 342.1 | 338.2 | 336 | 490 | 56.2 | 18.8 | 105 | 6.6 | 260.8 | 11.8 | 762 | 792.6 | 748.2 | 777.7 | 639.4 | 642.2 | 595.2 | 749.3 | 722.9 | 636.3 | 618.5 | 612.7 | 630.5 | 332.7 | 350.8 | 362.3 | 344.4 | 321.1 | 354.9 | 368.2 | 341.8
1339.2 | 1063.2 | 470 | 188 | 219.7612 | 425.4 | 344.1 | 338.6 | 336.1 | 498.1 | 56.3 | 18.8 | 104.7 | 7.2 | 232 | 11.6 | 765.6 | 787 | 755.5 | 782.2 | 642.9 | 644 | 593.4 | 762.4 | 723.9 | 638.3 | 616.5 | 624 | 629.2 | 332.9 | 351.3 | 363 | 344.6 | 321.2 | 354.6 | 368.1 | 341.7
1340.2 | 1064.2 | 470.7 | 188.28 | 220.0885 | 424.8 | 345.2 | 338.6 | 335.9 | 495.4 | 56.3 | 18.8 | 104.6 | 6.9 | 266.2 | 10.5 | 770.4 | 793.1 | 767.6 | 787.4 | 647.4 | 645.7 | 596.5 | 775.6 | 730.2 | 643.3 | 614.8 | 633.2 | 628.8 | 332.9 | 351.6 | 363.3 | 344.7 | 321.4 | 354.2 | 367.9 | 341.7
1341.2 | 1065.2 | 468.5 | 187.4 | 219.0598 | 424.2 | 345.4 | 339.2 | 336 | 493.6 | 56.3 | 18.8 | 104.5 | 6.3 | 234.3 | 9.7 | 774.8 | 796.8 | 775.3 | 792.7 | 650.1 | 647.8 | 601.4 | 782.4 | 737.3 | 647.6 | 610.2 | 639.7 | 629.8 | 332.8 | 352.1 | 364 | 344.8 | 321.5 | 354 | 367.9 | 341.7
1342.2 | 1066.2 | 467.4 | 186.96 | 218.5455 | 427.9 | 345.6 | 339.8 | 336.9 | 494.7 | 56.3 | 18.8 | 104.4 | 5.2 | 238 | 14.2 | 778.3 | 800.7 | 775.8 | 798.4 | 652.1 | 649.6 | 603.4 | 790.9 | 740.4 | 649.9 | 609.9 | 647.8 | 634.2 | 333.1 | 352.6 | 364.7 | 345 | 321.6 | 354 | 368 | 341.7
1343.2 | 1067.2 | 468.9 | 187.56 | 219.2468 | 427.7 | 345.7 | 340.2 | 338.1 | 495.7 | 56.3 | 18.8 | 104.2 | 5 | 243.1 | 15.4 | 782.4 | 806.9 | 781 | 804.1 | 657.5 | 651.5 | 606.2 | 794.8 | 742.1 | 653 | 610.8 | 653.4 | 638 | 333.3 | 353 | 365.6 | 345 | 321.8 | 354.3 | 368.1 | 341.8
1344.2 | 1068.2 | 469.1 | 187.64 | 219.3403 | 427.1 | 345.8 | 340.1 | 338.6 | 496.1 | 56.3 | 18.8 | 104.1 | 5.3 | 237.1 | 15 | 783.8 | 809.5 | 772.2 | 808.6 | 663.8 | 652.9 | 609.2 | 773.2 | 744.2 | 655.3 | 609.3 | 646 | 638.3 | 333.5 | 353.2 | 366 | 345 | 321.9 | 354.8 | 368.3 | 341.9
1345.2 | 1069.2 | 468.7 | 187.48 | 219.1533 | 427.2 | 346.8 | 340.5 | 339 | 496.4 | 56.4 | 18.8 | 104.1 | 6.2 | 260.9 | 13.3 | 784.5 | 810.9 | 772.3 | 811.2 | 671.8 | 654.2 | 607.7 | 767.6 | 742 | 656.8 | 605.1 | 646 | 635.6 | 333.5 | 353.4 | 366.2 | 345 | 322.1 | 354.9 | 368.3 | 342
1346.2 | 1070.2 | 469.4 | 187.76 | 219.4806 | 426.6 | 350.1 | 340.3 | 338.7 | 492 | 56.4 | 18.7 | 104 | 8.9 | 266.9 | 10.8 | 788.6 | 810.5 | 778.9 | 815.4 | 674.8 | 656 | 604.9 | 774.1 | 744.2 | 657.2 | 598.8 | 651.7 | 634.9 | 333.7 | 353.7 | 366.3 | 345.1 | 322.3 | 354.6 | 367.7 | 342
1347.2 | 1071.2 | 469.3 | 187.72 | 219.4339 | 428.3 | 351.3 | 340.6 | 338.2 | 492.3 | 56.4 | 18.7 | 104 | 9.5 | 271.1 | 10.2 | 792.9 | 813.5 | 779.2 | 820.3 | 674 | 658.1 | 603.4 | 785.6 | 744.1 | 659.3 | 594.3 | 659.5 | 636.8 | 333.9 | 354 | 366.4 | 345.2 | 322.5 | 354.3 | 367.1 | 342
1348.2 | 1072.2 | 471.3 | 188.52 | 220.369 | 427.8 | 351.2 | 340.6 | 337.6 | 490.5 | 56.3 | 18.7 | 104 | 8.1 | 274.9 | 11.7 | 798 | 815.3 | 788.1 | 824.8 | 676.7 | 660.3 | 604.7 | 791.3 | 745.4 | 661.9 | 593.3 | 664.9 | 638.7 | 334 | 354.3 | 366.3 | 345.4 | 322.7 | 354.1 | 366.7 | 342
1349.2 | 1073.2 | 469.9 | 187.96 | 219.7144 | 426.1 | 351.5 | 340.4 | 338 | 489.8 | 56.4 | 18.7 | 104.1 | 7.9 | 258.4 | 12.3 | 801.2 | 804.5 | 781.5 | 827.7 | 677.2 | 661.9 | 601.1 | 777.4 | 737.5 | 660.8 | 592.5 | 663.8 | 639.5 | 334.4 | 354.6 | 366.4 | 345.5 | 322.8 | 354 | 366.8 | 342
1350.2 | 1074.2 | 468.3 | 187.32 | 218.9663 | 426 | 351.8 | 340.8 | 338.4 | 485.9 | 56.4 | 18.7 | 104.2 | 7.2 | 266.3 | 11.7 | 800.2 | 800.6 | 762 | 829.6 | 675.3 | 662.6 | 597.3 | 748.3 | 728.9 | 658.1 | 591.2 | 652.7 | 639.8 | 334.6 | 354.6 | 366.4 | 345.4 | 323 | 354 | 366.6 | 342
1351.2 | 1075.2 | 470.5 | 188.2 | 219.995 | 429.4 | 351.5 | 341.5 | 339.1 | 482.9 | 56.4 | 18.7 | 104.1 | 7.2 | 253.5 | 10.6 | 800.6 | 805.6 | 755 | 830.6 | 675.1 | 663.4 | 596.9 | 732.8 | 730 | 658.1 | 589.8 | 642.8 | 640.4 | 334.7 | 354.5 | 366.6 | 345.3 | 323.2 | 353.9 | 366.5 | 342.2
1352.2 | 1076.2 | 469.8 | 187.92 | 219.6677 | 431.8 | 351.6 | 341.7 | 339.2 | 481 | 56.4 | 18.7 | 103.9 | 6.5 | 239.1 | 10.8 | 803.5 | 807.1 | 748.5 | 832.2 | 676.7 | 664.1 | 596.4 | 726.8 | 729.7 | 659.3 | 588.6 | 641.7 | 640.8 | 334.8 | 354.4 | 366.8 | 345.2 | 323.3 | 353.8 | 366.2 | 342.2
1353.2 | 1077.2 | 470.4 | 188.16 | 219.9482 | 434.6 | 352.2 | 342.4 | 339.1 | 476 | 56.5 | 18.7 | 103.8 | 7.5 | 238.4 | 10.3 | 803.6 | 792.8 | 730.4 | 832.8 | 673.1 | 664.9 | 592 | 717 | 723.7 | 656.3 | 587.2 | 638 | 642 | 334.9 | 354.5 | 367 | 345.3 | 323.4 | 353.5 | 365.8 | 342.2
1354.2 | 1078.2 | 470.6 | 188.24 | 220.0417 | 437 | 352 | 342.7 | 338.3 | 474.7 | 56.5 | 18.7 | 103.8 | 7.3 | 242.8 | 10.5 | 801.7 | 775.1 | 720.1 | 831.7 | 669.5 | 665.8 | 586.3 | 705.2 | 715.5 | 653.4 | 586.9 | 635.9 | 644.3 | 335.1 | 354.7 | 367.1 | 345.5 | 323.5 | 353.2 | 365.9 | 342.2
1355.2 | 1079.2 | 469.9 | 187.96 | 219.7144 | 434.1 | 351.3 | 342.6 | 336.9 | 470.3 | 56.5 | 18.7 | 103.9 | 7.7 | 250.1 | 10.6 | 802.6 | 777.3 | 730.2 | 830.3 | 671.3 | 666.1 | 581.1 | 696.8 | 709.9 | 652.1 | 586.7 | 635.2 | 644.4 | 335.4 | 354.8 | 367.1 | 345.5 | 323.7 | 353 | 365.7 | 342.2
1356.2 | 1080.2 | 469.1 | 187.64 | 219.3403 | 437.9 | 350.6 | 342.5 | 335.4 | 463.9 | 56.6 | 18.7 | 103.9 | 7.6 | 238.7 | 12.4 | 804.3 | 778.4 | 726 | 829.9 | 671.4 | 666.5 | 579 | 701 | 708.7 | 652.5 | 587 | 631.7 | 645.2 | 335.6 | 354.8 | 366.9 | 345.5 | 323.8 | 352.8 | 365.3 | 342.3
1357.2 | 1081.2 | 469.5 | 187.8 | 219.5274 | 445.6 | 350.4 | 341.6 | 334.6 | 461.4 | 56.6 | 18.7 | 103.9 | 7.9 | 240 | 12.2 | 805.2 | 787.2 | 719.2 | 830.4 | 671 | 667 | 581.8 | 702.4 | 713.1 | 654.7 | 587.4 | 625.1 | 644.6 | 335.6 | 354.7 | 366.7 | 345.3 | 323.9 | 353.2 | 366 | 342.4
1358.2 | 1082.2 | 468.3 | 187.32 | 218.9663 | 448 | 350 | 340.8 | 334.3 | 467.7 | 56.6 | 18.7 | 104.1 | 6.7 | 249.4 | 12.5 | 805.1 | 798.3 | 711.2 | 830.3 | 671.3 | 667.5 | 586.4 | 701.1 | 718.3 | 657.2 | 587.9 | 617.2 | 643.9 | 335.8 | 354.6 | 366.8 | 345.3 | 324 | 353.6 | 366 | 342.5
1359.2 | 1083.2 | 468.7 | 187.48 | 219.1533 | 448.8 | 349.6 | 340.4 | 334.2 | 474.4 | 56.7 | 18.7 | 104.4 | 6.8 | 233.3 | 13 | 807.7 | 801.8 | 719.2 | 830.9 | 673.4 | 668 | 587.5 | 700.4 | 721.7 | 657.4 | 587.6 | 618.5 | 643.7 | 335.9 | 354.6 | 367.1 | 345.1 | 324.2 | 353.7 | 366.3 | 342.6
1360.2 | 1084.2 | 469.6 | 187.84 | 219.5741 | 449.7 | 349.1 | 340.7 | 333.9 | 472.9 | 56.8 | 18.7 | 104.6 | 6.1 | 229.9 | 13.6 | 808.6 | 797.9 | 715.8 | 831.7 | 671.9 | 668.5 | 585.3 | 703.1 | 719.6 | 656.4 | 587 | 619.8 | 644.9 | 335.9 | 354.6 | 367 | 345.2 | 324.2 | 354.2 | 367.1 | 342.6
1361.2 | 1085.2 | 469.6 | 187.84 | 219.5741 | 447.8 | 349.3 | 340.9 | 334.1 | 471.1 | 56.8 | 18.7 | 104.8 | 6.7 | 246.8 | 11.4 | 807.6 | 792.2 | 715.4 | 831.5 | 671.2 | 668.5 | 581.4 | 688.5 | 713.8 | 653.7 | 587 | 615.7 | 647 | 336.1 | 354.5 | 366.9 | 345.2 | 324.3 | 354.5 | 367.3 | 342.7
1362.2 | 1086.2 | 469.6 | 187.84 | 219.5741 | 444.1 | 349.1 | 340.8 | 334.4 | 464.7 | 56.8 | 18.7 | 105 | 5 | 257.3 | 11.3 | 808.2 | 783.4 | 714.4 | 831.9 | 670.6 | 668.8 | 578.8 | 694.4 | 710.9 | 653 | 586.9 | 622.5 | 647.9 | 336.3 | 354.4 | 366.8 | 345.1 | 324.4 | 354.6 | 367 | 342.7
1363.2 | 1087.2 | 468.8 | 187.52 | 219.2001 | 442.1 | 349.1 | 340.3 | 334 | 466.1 | 56.8 | 18.7 | 105 | 5.4 | 228.1 | 9.4 | 810 | 779.1 | 719.4 | 832.4 | 670.3 | 669.1 | 576.4 | 694 | 708.5 | 651.3 | 586.6 | 625.1 | 647.4 | 336.5 | 354.6 | 366.8 | 345.3 | 324.5 | 354.7 | 366.7 | 342.8
1364.2 | 1088.2 | 469.8 | 187.92 | 219.6677 | 440.1 | 349.6 | 340.3 | 333 | 465.7 | 56.8 | 18.7 | 105 | 5.2 | 231 | 8.9 | 811.5 | 776.1 | 735.5 | 832.9 | 671.2 | 669.1 | 573.2 | 695 | 704.7 | 649.5 | 586.4 | 626.2 | 646.3 | 336.6 | 354.6 | 366.7 | 345.4 | 324.7 | 354.5 | 366.5 | 342.8
1365.2 | 1089.2 | 469 | 187.6 | 219.2936 | 437.6 | 350.5 | 339.9 | 332.7 | 462.7 | 56.8 | 18.7 | 104.9 | 5.8 | 220.8 | 9.3 | 814.9 | 788.7 | 739.2 | 834.8 | 673.6 | 669.5 | 573.7 | 709.2 | 708.4 | 652.5 | 586.3 | 632.8 | 647.4 | 336.5 | 354.5 | 366.5 | 345.4 | 324.9 | 354.3 | 366 | 342.7
1366.2 | 1090.2 | 469.2 | 187.68 | 219.3871 | 439 | 351.2 | 339.3 | 332.3 | 467.3 | 56.8 | 18.7 | 105 | 5.9 | 237.4 | 10.6 | 818.5 | 800.3 | 738.6 | 837.3 | 673.3 | 670.2 | 578.1 | 721.5 | 714.4 | 655.6 | 586.5 | 635.2 | 651.5 | 336.6 | 354.6 | 366.4 | 345.6 | 325 | 354.2 | 365.5 | 342.7
1367.2 | 1091.2 | 468.8 | 187.52 | 219.2001 | 444.4 | 351.2 | 339 | 331.6 | 469.1 | 56.8 | 18.7 | 105 | 7.1 | 239.4 | 12.3 | 818.4 | 791.4 | 732.2 | 838.8 | 671.4 | 670.3 | 576.7 | 717.6 | 710.8 | 654.3 | 586.5 | 635.9 | 656 | 336.9 | 354.7 | 366.7 | 345.7 | 325.1 | 354.1 | 365.2 | 342.6
1368.2 | 1092.2 | 470.5 | 188.2 | 219.995 | 449.6 | 350.8 | 338.6 | 331.2 | 470.5 | 56.8 | 18.7 | 105.2 | 6.7 | 242.8 | 10.8 | 815.5 | 776.2 | 718.8 | 838.3 | 668.1 | 670.3 | 572.6 | 709 | 703.2 | 651.1 | 586.4 | 635.2 | 660 | 337 | 354.9 | 367.1 | 345.8 | 325.2 | 354.1 | 365.4 | 342.7
1369.2 | 1093.2 | 471.4 | 188.56 | 220.4158 | 448.6 | 350.8 | 338.7 | 331.4 | 470.6 | 56.8 | 18.7 | 105.4 | 5.8 | 241.6 | 10.9 | 815.1 | 771 | 719.8 | 838.7 | 667.1 | 670.4 | 570.1 | 711.9 | 699.7 | 650.1 | 586.2 | 637.7 | 663 | 337 | 355.3 | 367.4 | 346.1 | 325.4 | 354 | 365.1 | 342.7
1370.2 | 1094.2 | 469.8 | 187.92 | 219.6677 | 453.7 | 350.7 | 339.5 | 332.2 | 476.1 | 56.8 | 18.7 | 105.6 | 6.8 | 243.3 | 12.1 | 816.2 | 757.2 | 720.7 | 838.6 | 667.3 | 670.8 | 568 | 710.9 | 695.7 | 649.6 | 586 | 644.3 | 663.3 | 337.1 | 356 | 367.9 | 346.4 | 325.6 | 353.8 | 365 | 342.7
1371.2 | 1095.2 | 468.9 | 187.56 | 219.2468 | 455.7 | 350.6 | 340 | 332.6 | 481 | 56.8 | 18.7 | 105.6 | 6.9 | 247.6 | 11.7 | 812.7 | 743.3 | 702.1 | 836.2 | 662.7 | 670.5 | 563.6 | 691 | 686.8 | 645.2 | 586 | 639.2 | 661.6 | 337.3 | 359.3 | 368.7 | 347 | 325.7 | 353.5 | 365.3 | 342.6
1372.2 | 1096.2 | 469.2 | 187.68 | 219.3871 | 456.5 | 351.4 | 340.8 | 333.8 | 479.5 | 56.8 | 18.7 | 105.6 | 6.9 | 245.1 | 13 | 813 | 743.9 | 710 | 834.7 | 663.9 | 670.2 | 561.2 | 691.3 | 683.4 | 643.6 | 585.7 | 641.5 | 659.2 | 337.5 | 359.7 | 369.4 | 347.1 | 325.7 | 353.3 | 365.9 | 342.6
1373.2 | 1097.2 | 469.3 | 187.72 | 219.4339 | 455.5 | 351.9 | 341.4 | 335 | 475.7 | 56.8 | 18.7 | 105.5 | 6.1 | 233.9 | 14.3 | 813.7 | 754.5 | 726.8 | 833.4 | 669.1 | 669.8 | 561.8 | 693.7 | 685.6 | 644.6 | 585 | 645.4 | 655.7 | 337.7 | 359.7 | 369.4 | 346.9 | 325.8 | 353.3 | 366.3 | 342.7
1374.2 | 1098.2 | 469.9 | 187.96 | 219.7144 | 451.9 | 353.4 | 340.8 | 336.4 | 471.7 | 56.9 | 18.7 | 105.6 | 5.6 | 244.1 | 11.7 | 816.3 | 762.2 | 738.9 | 832.8 | 675.3 | 669.5 | 568.2 | 701.7 | 695 | 648.5 | 584.3 | 646.2 | 651.2 | 337.9 | 359.6 | 369.4 | 346.7 | 325.8 | 353.3 | 366.2 | 342.7
1375.2 | 1099.2 | 471.1 | 188.44 | 220.2755 | 454.4 | 355.8 | 340.5 | 337.2 | 476.1 | 57 | 18.7 | 105.6 | 6.5 | 235.3 | 11.1 | 815.3 | 747.3 | 749.3 | 831 | 678.6 | 669.5 | 567 | 695.5 | 691.2 | 647.3 | 583.9 | 656.7 | 645.8 | 337.9 | 359.9 | 369.7 | 346.9 | 325.9 | 353.4 | 368 | 342.7
1376.2 | 1100.2 | 470.8 | 188.32 | 220.1352 | 461.5 | 359 | 340.2 | 337.7 | 479.7 | 57 | 18.7 | 105.7 | 6.4 | 230.6 | 9.3 | 815.8 | 740.2 | 758 | 829.7 | 682.5 | 669.5 | 564.6 | 701 | 687.8 | 646.6 | 583.4 | 666.6 | 640.3 | 338.2 | 360.1 | 370 | 347.1 | 326 | 353.5 | 368.4 | 342.8
1377.2 | 1101.2 | 470.9 | 188.36 | 220.182 | 463 | 361.4 | 340.8 | 338 | 480.6 | 57.1 | 18.7 | 105.7 | 7 | 236.8 | 8.2 | 817.1 | 736.3 | 772.3 | 829.5 | 686.6 | 669.5 | 563.7 | 706.7 | 686.5 | 647.3 | 583.2 | 673.4 | 636.4 | 338.4 | 360.2 | 370.4 | 347.1 | 326.1 | 353.4 | 368.5 | 342.8
1378.2 | 1102.2 | 471.9 | 188.76 | 220.6496 | 461 | 361.6 | 341.2 | 338.4 | 482.5 | 57.1 | 18.7 | 105.8 | 7 | 228 | 8.1 | 818.5 | 744.7 | 777 | 829.9 | 689 | 669.5 | 565.4 | 717.9 | 690 | 648.7 | 583 | 675 | 633.7 | 338.7 | 360.2 | 370.5 | 347.1 | 326.2 | 353.5 | 368.9 | 342.9
1379.2 | 1103.2 | 471.7 | 188.68 | 220.556 | 462.3 | 361.1 | 341 | 339.1 | 484 | 57.1 | 18.7 | 105.9 | 6.8 | 240.2 | 8.8 | 820.8 | 764.3 | 780 | 831.8 | 690.7 | 669.5 | 572.1 | 731 | 702 | 652.4 | 583.4 | 676.2 | 634.3 | 338.8 | 360.1 | 370.8 | 347 | 326.2 | 353.5 | 368.9 | 343
1380.2 | 1104.2 | 471.4 | 188.56 | 220.4158 | 464.6 | 360.5 | 340.6 | 339.4 | 485.5 | 57 | 18.7 | 105.9 | 6.6 | 244.3 | 10.8 | 823 | 769.8 | 780.4 | 834.3 | 692.3 | 669.8 | 575.4 | 745.1 | 707.6 | 655.1 | 584 | 680.2 | 635.4 | 338.9 | 360.2 | 371.3 | 347.1 | 326.4 | 353.6 | 368.7 | 343
1381.2 | 1105.2 | 471.2 | 188.48 | 220.3223 | 467.8 | 360.1 | 340.3 | 339.1 | 486.7 | 57 | 18.7 | 105.9 | 5.9 | 233.6 | 10.4 | 822.6 | 762.8 | 768.3 | 836.5 | 690.3 | 669.6 | 572.9 | 739.8 | 706.7 | 653.8 | 584.5 | 679.1 | 639.4 | 339.1 | 360.4 | 371.6 | 347.2 | 326.4 | 353.4 | 368.3 | 343
1382.2 | 1106.2 | 470.4 | 188.16 | 219.9482 | 465.8 | 360 | 340.1 | 338.6 | 485.3 | 57 | 18.7 | 105.9 | 5.7 | 228.8 | 11.4 | 825.3 | 768.8 | 765.3 | 839.4 | 689.2 | 669.8 | 574.3 | 751.3 | 713.1 | 656.4 | 584.9 | 679.1 | 644.2 | 339.4 | 360.4 | 371.6 | 347.3 | 326.5 | 353.3 | 368.5 | 343
1383.2 | 1107.2 | 469.1 | 187.64 | 219.3403 | 464.3 | 359.8 | 340.4 | 338.6 | 485.8 | 57 | 18.7 | 105.8 | 7.3 | 243.5 | 10.8 | 827.9 | 783.2 | 778.9 | 841.7 | 693.7 | 670 | 578.4 | 755.6 | 717.5 | 658.3 | 585 | 684.1 | 646.8 | 339.6 | 360.4 | 371.6 | 347.4 | 326.7 | 353.2 | 368.6 | 343.1
1384.2 | 1108.2 | 469.5 | 187.8 | 219.5274 | 462.9 | 360 | 340.2 | 339 | 482.6 | 56.9 | 18.7 | 105.8 | 8.7 | 213.2 | 10.7 | 829.5 | 789 | 784.2 | 843.9 | 695.9 | 670.3 | 582.3 | 763.8 | 720.7 | 662 | 584.8 | 690.2 | 646.8 | 339.8 | 360.4 | 371.4 | 347.4 | 326.8 | 353.1 | 368.3 | 343.1
1385.2 | 1109.2 | 470.8 | 188.32 | 220.1352 | 465.3 | 359.8 | 340 | 338.5 | 481.6 | 56.9 | 18.7 | 105.7 | 9.1 | 204.5 | 11.9 | 831.3 | 788.3 | 779.1 | 846.4 | 696 | 670.6 | 582.9 | 754.8 | 720.6 | 660.9 | 584.8 | 688.6 | 647.6 | 340 | 360.5 | 371.3 | 347.6 | 326.9 | 353 | 367.8 | 343
1386.2 | 1110.2 | 470.1 | 188.04 | 219.8079 | 467.1 | 359.5 | 339.9 | 337.4 | 483.3 | 56.9 | 18.7 | 105.8 | 7.3 | 252.4 | 9.1 | 829.5 | 782.9 | 763.8 | 847.9 | 693.6 | 670.9 | 582.7 | 749.5 | 716.8 | 659.5 | 585 | 683.1 | 649.5 | 340.3 | 360.7 | 371.4 | 347.7 | 327 | 352.8 | 367.8 | 343
1387.2 | 1111.2 | 469 | 187.6 | 219.2936 | 471.9 | 359.4 | 340.3 | 336.7 | 484.7 | 57 | 18.7 | 106 | 7.4 | 246.1 | 9 | 826.9 | 768.4 | 755.2 | 847.6 | 690.9 | 670.8 | 579.8 | 730.7 | 708.6 | 656.7 | 585.1 | 677.2 | 650.7 | 340.4 | 360.8 | 371.3 | 347.8 | 327.2 | 352.4 | 367.7 | 342.9
1388.2 | 1112.2 | 468.9 | 187.56 | 219.2468 | 472.7 | 359.3 | 341 | 336.6 | 479.6 | 57 | 18.7 | 106.2 | 7.6 | 248.8 | 13.6 | 825.7 | 759.6 | 734.3 | 847.6 | 688.7 | 670.2 | 576.7 | 718.8 | 704.3 | 655.3 | 585.3 | 669.2 | 652.3 | 340.5 | 360.6 | 371.3 | 347.7 | 327.4 | 352.1 | 367.4 | 343
1389.2 | 1113.2 | 469.1 | 187.64 | 219.3403 | 473.8 | 358.6 | 341.3 | 336.6 | 471.8 | 57.1 | 18.7 | 106.3 | 7.7 | 246 | 15.3 | 825.3 | 745.4 | 720 | 846.6 | 686.4 | 669.6 | 573.1 | 707.9 | 698.5 | 652.5 | 585.3 | 661.6 | 654 | 340.5 | 360.5 | 371 | 347.6 | 327.5 | 352.1 | 366.9 | 343
1390.2 | 1114.2 | 468.9 | 187.56 | 219.2468 | 473.4 | 358 | 340.9 | 336.2 | 470.4 | 57.1 | 18.7 | 106.5 | 8.3 | 240.9 | 15.6 | 823.3 | 745.3 | 719.3 | 845.2 | 684.3 | 669.4 | 570.8 | 706 | 693.4 | 651 | 585.1 | 662.1 | 655 | 340.7 | 360.6 | 370.8 | 347.8 | 327.6 | 352 | 366.4 | 343
1391.2 | 1115.2 | 469.4 | 187.76 | 219.4806 | 472.7 | 358 | 340.3 | 335.8 | 471.7 | 57.2 | 18.7 | 106.6 | 9.4 | 248 | 16.3 | 823.9 | 751.6 | 726.9 | 844.5 | 683.8 | 669.2 | 570.7 | 711.4 | 695.2 | 651.1 | 584.7 | 664.4 | 654.8 | 341.1 | 360.5 | 370.6 | 347.7 | 327.6 | 352.1 | 365.8 | 343
1392.2 | 1116.2 | 468.7 | 187.48 | 219.1533 | 472.9 | 358.7 | 339.9 | 335.3 | 470 | 57.2 | 18.7 | 106.6 | 9.2 | 246.7 | 16.8 | 826.8 | 758.4 | 735.7 | 845.5 | 685.5 | 669.3 | 573.3 | 730.5 | 703.1 | 653.6 | 584.5 | 670 | 654.4 | 341.2 | 360.3 | 370.4 | 347.7 | 327.7 | 352.1 | 365.3 | 343
1393.2 | 1117.2 | 468.2 | 187.28 | 218.9195 | 473.3 | 359.1 | 339.9 | 334.4 | 469.2 | 57.2 | 18.6 | 106.7 | 7.8 | 241.8 | 17.6 | 830.9 | 767.9 | 752.3 | 846.9 | 686.5 | 669.8 | 576.6 | 741 | 708.8 | 656.2 | 584.3 | 675.8 | 654.2 | 341.4 | 360.2 | 370.4 | 347.7 | 327.9 | 352.1 | 365.1 | 343
1394.2 | 1118.2 | 470.6 | 188.24 | 220.0417 | 475.2 | 358.9 | 339.8 | 333.8 | 467.3 | 57.2 | 18.6 | 107 | 7.6 | 243.9 | 17.1 | 834.8 | 777.2 | 774.3 | 849.2 | 689.2 | 670.5 | 581.2 | 752.5 | 716.6 | 658.4 | 584.2 | 683.3 | 653.3 | 341.6 | 360.1 | 370.9 | 347.8 | 328 | 352.4 | 365.2 | 343
1395.2 | 1119.2 | 470.5 | 188.2 | 219.995 | 476.8 | 358.4 | 339.8 | 333.9 | 470.4 | 57.1 | 18.6 | 107.3 | 6 | 237.8 | 17.6 | 837.5 | 774.9 | 792.3 | 851.7 | 694.8 | 671.1 | 583.8 | 758.5 | 718.8 | 661.1 | 584.2 | 691.4 | 651.3 | 341.6 | 360.2 | 370.8 | 347.8 | 328.1 | 352.6 | 365.1 | 343
1396.2 | 1120.2 | 469.4 | 187.76 | 219.4806 | 480.5 | 358.7 | 340.3 | 333.9 | 481.8 | 57.1 | 18.6 | 107.4 | 5.8 | 233.2 | 17.9 | 837.2 | 768.6 | 795 | 853.7 | 696.4 | 672 | 582.7 | 762.3 | 717.4 | 661.2 | 584.2 | 699 | 647.2 | 341.9 | 360.4 | 370.8 | 348 | 328.2 | 352.6 | 365.1 | 343
1397.2 | 1121.2 | 468.4 | 187.36 | 219.013 | 482.2 | 359.4 | 340.1 | 334.1 | 487.5 | 57.1 | 18.6 | 107.4 | 5.6 | 236.2 | 17.1 | 838.4 | 770.7 | 801.2 | 855.2 | 699.3 | 672.8 | 581.9 | 764.8 | 718.8 | 660.9 | 584.3 | 704.6 | 643.5 | 342.1 | 360.5 | 371.1 | 348.1 | 328.2 | 352.7 | 365.3 | 343.1
1398.2 | 1122.2 | 469.8 | 187.92 | 219.6677 | 480.5 | 359.6 | 339.8 | 334.6 | 488.3 | 57.1 | 18.6 | 107.5 | 6.8 | 257.9 | 15.4 | 841.7 | 780.1 | 803.9 | 856.9 | 706.5 | 673.3 | 586.8 | 770.1 | 725.9 | 665.9 | 584.5 | 706.5 | 639.3 | 342.4 | 360.5 | 371.4 | 348.1 | 328.3 | 353.2 | 365.5 | 343.2
1399.2 | 1123.2 | 469.7 | 187.88 | 219.6209 | 479.9 | 360.8 | 339.8 | 335.8 | 486.5 | 57.1 | 18.6 | 107.7 | 7.3 | 256.3 | 12.7 | 843.2 | 793.7 | 804.8 | 858.5 | 711.3 | 673.6 | 592.2 | 765 | 731.5 | 669.3 | 584.6 | 705 | 634.6 | 342.4 | 360.5 | 371.7 | 348 | 328.5 | 353.7 | 365.8 | 343.3
1400.2 | 1124.2 | 470.5 | 188.2 | 219.995 | 480.2 | 363.4 | 339.5 | 337 | 486.1 | 57.1 | 18.6 | 107.8 | 8.4 | 242.5 | 10.5 | 845.1 | 809.1 | 812.1 | 860 | 715.9 | 674.2 | 596.1 | 774.8 | 737.5 | 673.2 | 584.8 | 709.7 | 630.2 | 342.5 | 360.6 | 371.9 | 348.1 | 328.6 | 353.9 | 365.9 | 343.4
1401.2 | 1125.2 | 470 | 188 | 219.7612 | 481.2 | 364.7 | 339.5 | 337.4 | 484 | 57.1 | 18.6 | 107.8 | 10.7 | 252.6 | 9.7 | 844.9 | 805.9 | 798.7 | 861.5 | 715.3 | 674.8 | 597.6 | 764.3 | 737.8 | 673.1 | 585.1 | 709 | 627.8 | 342.4 | 361.1 | 372.3 | 348.3 | 328.6 | 354 | 365.8 | 343.5
1402.2 | 1126.2 | 469.8 | 187.92 | 219.6677 | 485.6 | 364.3 | 339.9 | 337.4 | 484.1 | 57.1 | 18.6 | 107.8 | 9.3 | 247.1 | 8.4 | 842.6 | 794.9 | 779.4 | 860.8 | 710.8 | 675.1 | 592.4 | 748.4 | 729.1 | 670 | 585.4 | 698.2 | 626.9 | 342.6 | 361.6 | 372.5 | 348.7 | 328.7 | 353.8 | 365.8 | 343.4
1403.2 | 1127.2 | 468.8 | 187.52 | 219.2001 | 487.2 | 363.8 | 341.1 | 336.8 | 482.5 | 57.1 | 18.6 | 107.7 | 8.6 | 240.9 | 7 | 842.2 | 793.7 | 762.5 | 860.6 | 708.4 | 675.1 | 589.2 | 746.6 | 726 | 670.2 | 585.8 | 692.3 | 627.5 | 342.9 | 361.6 | 372.4 | 348.7 | 328.8 | 353.5 | 365.9 | 343.4
1404.2 | 1128.2 | 466.6 | 186.64 | 218.1714 | 488.8 | 363.4 | 342.1 | 336.7 | 478.9 | 57 | 18.6 | 107.6 | 8.1 | 259 | 8 | 844.5 | 801.4 | 768.8 | 861.6 | 709.8 | 675.5 | 591.8 | 753 | 730.4 | 672.7 | 586.2 | 691.9 | 629.7 | 343.2 | 361.7 | 372.3 | 348.7 | 329 | 353.3 | 365.9 | 343.3
1405.2 | 1129.2 | 467.3 | 186.92 | 218.4987 | 491.7 | 362.6 | 342.4 | 337.2 | 478.8 | 57 | 18.6 | 107.5 | 7.6 | 244.3 | 10.5 | 845.1 | 793.4 | 768.4 | 862.2 | 710.4 | 675.9 | 591.8 | 754.3 | 728 | 671.9 | 586.4 | 697.7 | 630.2 | 343.4 | 361.8 | 372.4 | 348.9 | 329.1 | 353.2 | 366.2 | 343.4
1406.2 | 1130.2 | 467.8 | 187.12 | 218.7325 | 495.4 | 362.7 | 342.1 | 337.6 | 481.4 | 57 | 18.6 | 107.4 | 7.5 | 246 | 14.9 | 847.3 | 791.6 | 764.4 | 863.2 | 708 | 676.5 | 590.8 | 758.3 | 727.3 | 672.4 | 586.9 | 701.1 | 631.2 | 343.6 | 362 | 372.6 | 349 | 329.2 | 353.2 | 366.7 | 343.3
1407.2 | 1131.2 | 467.5 | 187 | 218.5922 | 497.1 | 363 | 342 | 337.9 | 482.9 | 57 | 18.6 | 107.2 | 7.3 | 247.9 | 17.7 | 850.9 | 797.2 | 779.9 | 864.5 | 711.6 | 677.3 | 592.3 | 764.3 | 732.6 | 674.8 | 587.3 | 703.7 | 631.7 | 343.7 | 362.2 | 373 | 349 | 329.3 | 353.2 | 367.2 | 343.4
1408.2 | 1132.2 | 468.1 | 187.24 | 218.8728 | 498.8 | 363.3 | 342.5 | 337.8 | 485.9 | 57 | 18.6 | 107.3 | 7.3 | 252.8 | 18.3 | 854.2 | 794.9 | 788.5 | 866.1 | 717 | 678.7 | 594.3 | 771 | 735 | 677.5 | 587.7 | 711.5 | 629.9 | 344 | 362.6 | 373.5 | 349.2 | 329.4 | 353.2 | 367.5 | 343.5
1409.2 | 1133.2 | 467.8 | 187.12 | 218.7325 | 501.1 | 364.4 | 343.1 | 337.9 | 488.1 | 57 | 18.6 | 107.1 | 6.1 | 248.6 | 18.4 | 853.3 | 796.3 | 789.3 | 866.8 | 719.5 | 679.3 | 593.8 | 767.7 | 732.8 | 677.4 | 588.2 | 716.2 | 627.4 | 344.1 | 362.8 | 373.9 | 349.4 | 329.5 | 353.2 | 367.4 | 343.5
1410.2 | 1134.2 | 469 | 187.6 | 219.2936 | 500.6 | 366.8 | 344.1 | 338 | 491.8 | 57 | 18.6 | 107.1 | 6.8 | 255.7 | 18.2 | 855.3 | 799.1 | 792.4 | 867.4 | 719.9 | 680 | 592.3 | 768.1 | 731 | 676.9 | 588.4 | 719.8 | 624.5 | 344.3 | 363 | 374.1 | 349.5 | 329.6 | 353.1 | 367.4 | 343.5
1411.2 | 1135.2 | 469.3 | 187.72 | 219.4339 | 499.6 | 368.5 | 344.2 | 338 | 494.7 | 57 | 18.6 | 107.1 | 6.6 | 253.6 | 17.3 | 855.6 | 795.7 | 794.5 | 868.7 | 720.3 | 680.8 | 591.1 | 766.1 | 728.9 | 677.4 | 588.5 | 721.8 | 622 | 344.5 | 363.3 | 374.2 | 349.8 | 329.7 | 353.3 | 367.4 | 343.5
1412.2 | 1136.2 | 470.2 | 188.08 | 219.8547 | 500.7 | 369 | 343.9 | 337.3 | 493.5 | 57.1 | 18.6 | 107.3 | 7 | 253.8 | 16.3 | 857.6 | 801 | 788.8 | 870.4 | 720.6 | 681.1 | 591.1 | 767.1 | 729.8 | 677.8 | 588.8 | 718.4 | 620.5 | 344.6 | 363.4 | 374.2 | 349.8 | 329.8 | 353.5 | 369.2 | 343.5
1413.2 | 1137.2 | 467.9 | 187.16 | 218.7793 | 504.7 | 368.6 | 343.1 | 337.8 | 491.2 | 57 | 18.6 | 107.5 | 6.5 | 256 | 16.9 | 858 | 801.4 | 777.6 | 872 | 718.3 | 681.5 | 589.9 | 766.3 | 728.1 | 677.1 | 589.1 | 711.8 | 621.3 | 344.6 | 363.4 | 374.2 | 349.8 | 330 | 353.7 | 369.5 | 343.5
1414.2 | 1138.2 | 467.8 | 187.12 | 218.7325 | 508.3 | 367.5 | 343 | 339 | 486.6 | 57 | 18.6 | 107.6 | 5.5 | 255.4 | 17.9 | 855.3 | 794.9 | 756.4 | 871.9 | 715 | 681.3 | 588.3 | 747.6 | 725.6 | 674.8 | 589.3 | 696.9 | 623.2 | 344.9 | 363.4 | 374.2 | 349.8 | 330.1 | 354 | 369.1 | 343.7
1415.2 | 1139.2 | 467.7 | 187.08 | 218.6857 | 511.6 | 366.6 | 343 | 339.9 | 480 | 56.9 | 18.6 | 107.8 | 5.1 | 256.5 | 19.6 | 851.6 | 781.6 | 729.9 | 869.4 | 709.2 | 680.7 | 583.4 | 717.3 | 717.1 | 671 | 589.3 | 683.2 | 624.5 | 345.2 | 363.2 | 374.2 | 349.7 | 330.3 | 354.4 | 369 | 343.8
1416.2 | 1140.2 | 469.2 | 187.68 | 219.3871 | 514.3 | 365.7 | 342.6 | 340.7 | 476.7 | 56.9 | 18.6 | 108 | 6 | 255.8 | 19.2 | 847.2 | 769 | 706.2 | 865 | 703.5 | 679.9 | 580.1 | 692.8 | 709.8 | 667.7 | 589.1 | 671.2 | 625.5 | 345.6 | 362.9 | 373.8 | 349.6 | 330.4 | 354.8 | 368.9 | 343.9
1417.2 | 1141.2 | 471.1 | 188.44 | 220.2755 | 509.5 | 364.8 | 341.9 | 341 | 475.8 | 56.9 | 18.6 | 108.1 | 5.1 | 253.6 | 17.7 | 844 | 767.5 | 698.6 | 860.2 | 700.1 | 679.1 | 577.8 | 677.6 | 704.6 | 664.9 | 588.9 | 660.1 | 626.6 | 345.8 | 362.5 | 373.2 | 349.5 | 330.5 | 354.9 | 369 | 344.1
1418.2 | 1142.2 | 470.2 | 188.08 | 219.8547 | 505.1 | 364.1 | 341.3 | 340.9 | 471.6 | 56.9 | 18.6 | 108.3 | 6 | 260.3 | 15.4 | 843.5 | 769.7 | 696.2 | 857.3 | 697.7 | 678.6 | 576.8 | 676.1 | 703.1 | 663.5 | 588.7 | 651.9 | 629.4 | 345.8 | 362.2 | 372.7 | 349.4 | 330.7 | 354.9 | 368.9 | 344.2
1419.2 | 1143.2 | 470.1 | 188.04 | 219.8079 | 500.4 | 363.5 | 341.1 | 340.6 | 468.5 | 56.9 | 18.6 | 108.3 | 7.1 | 261.8 | 15.1 | 843.1 | 778.1 | 704 | 854.7 | 696 | 678.1 | 577.4 | 684.5 | 704.6 | 663.4 | 588.5 | 651.8 | 634.3 | 345.8 | 362 | 372 | 349.3 | 330.8 | 355.1 | 368.7 | 344.2
1420.2 | 1144.2 | 469.1 | 187.64 | 219.3403 | 496.5 | 362.5 | 340.8 | 340.7 | 466.2 | 57 | 18.6 | 108.1 | 7.7 | 261.9 | 15.2 | 842.9 | 785.3 | 701.6 | 853 | 695.2 | 677.4 | 578.4 | 683.3 | 706.8 | 663.3 | 588.3 | 647.2 | 638.3 | 345.8 | 361.6 | 371.5 | 349.2 | 330.9 | 355.5 | 368.5 | 344.3
1421.2 | 1145.2 | 469.5 | 187.8 | 219.5274 | 495.3 | 361.7 | 340.2 | 340.9 | 468.1 | 57.1 | 18.6 | 108.2 | 7.3 | 278.1 | 16 | 842.3 | 791.5 | 696.7 | 851.9 | 693.7 | 676.8 | 580.3 | 677.4 | 707.2 | 663.1 | 588 | 641.3 | 639.4 | 345.9 | 361.1 | 371.2 | 349 | 331 | 355.8 | 368.9 | 344.4
1422.2 | 1146.2 | 469.3 | 187.72 | 219.4339 | 493.7 | 360.4 | 340.2 | 340.4 | 471.1 | 57.1 | 18.6 | 108.4 | 8 | 270.8 | 15.3 | 842.3 | 804.4 | 709.8 | 850.8 | 696.4 | 676.6 | 586.6 | 688.1 | 717.6 | 666.4 | 587.8 | 643.1 | 638.4 | 346.1 | 360.8 | 371.3 | 348.9 | 331.2 | 356.1 | 369.1 | 344.5
1423.2 | 1147.2 | 470.1 | 188.04 | 219.8079 | 493.7 | 359.4 | 341.2 | 340.5 | 473.9 | 57.2 | 18.6 | 108.5 | 7.9 | 263.2 | 14.4 | 844.9 | 812.8 | 728.9 | 850.8 | 701.3 | 676.5 | 592.8 | 709.1 | 725.9 | 670.5 | 587.8 | 653.3 | 635.9 | 346.2 | 360.6 | 371.4 | 348.9 | 331.3 | 356.1 | 369.2 | 344.6
1424.2 | 1148.2 | 470.7 | 188.28 | 220.0885 | 493.5 | 359.2 | 342 | 340.7 | 476.2 | 57.3 | 18.6 | 108.5 | 7.8 | 263.8 | 13.7 | 848.2 | 819.2 | 738.2 | 852.4 | 703 | 677 | 599.1 | 729.6 | 734.7 | 674.7 | 588 | 663.7 | 633.5 | 346.4 | 360.7 | 371.4 | 349.1 | 331.5 | 356.2 | 369.3 | 344.6
1425.2 | 1149.2 | 470.4 | 188.16 | 219.9482 | 493.7 | 359.6 | 342.2 | 340.6 | 480.1 | 57.3 | 18.6 | 108.5 | 8.4 | 252.1 | 13.5 | 847.4 | 810.9 | 746.2 | 852.6 | 702.7 | 677.8 | 597.3 | 730.8 | 732.8 | 673.5 | 588.3 | 672.5 | 630.9 | 346.6 | 360.9 | 371.4 | 349.4 | 331.6 | 356.2 | 369.2 | 344.6
1426.2 | 1150.2 | 470.6 | 188.24 | 220.0417 | 491.5 | 360.2 | 342.3 | 340.7 | 485.7 | 57.3 | 18.6 | 108.6 | 6.7 | 258.7 | 13.6 | 847.8 | 803.1 | 760 | 851.9 | 704.5 | 678 | 593.8 | 729.6 | 726 | 671.9 | 588.6 | 679.8 | 627.6 | 346.7 | 361.2 | 371.7 | 349.8 | 331.7 | 356.6 | 369.5 | 344.6
1427.2 | 1151.2 | 470.2 | 188.08 | 219.8547 | 490.7 | 360.9 | 342.8 | 341.5 | 495.8 | 57.4 | 18.6 | 108.6 | 6.7 | 260.3 | 12.5 | 848 | 784.1 | 771.7 | 851.2 | 704.9 | 678.4 | 591.3 | 729.7 | 719 | 669.5 | 588.8 | 687.8 | 624 | 346.8 | 361.8 | 372.3 | 350.2 | 331.8 | 356.9 | 369.7 | 344.6
1428.2 | 1152.2 | 470.1 | 188.04 | 219.8079 | 494.6 | 361.5 | 343.2 | 342.4 | 500.6 | 57.5 | 18.6 | 108.6 | 6.2 | 255.5 | 12.8 | 850.6 | 783.5 | 766 | 852 | 705.7 | 678.8 | 592 | 745.6 | 721.4 | 671.7 | 589.2 | 694.7 | 621 | 346.9 | 362.1 | 372.4 | 350.4 | 331.9 | 356.9 | 369.9 | 344.7
1429.2 | 1153.2 | 469.1 | 187.64 | 219.3403 | 497.7 | 362 | 343.7 | 343.1 | 505.2 | 57.7 | 18.6 | 108.6 | 6.6 | 253.2 | 13.3 | 850.9 | 775 | 753.5 | 852.6 | 703.6 | 679.1 | 592.8 | 745.3 | 721.9 | 671.5 | 589.7 | 696.9 | 618.6 | 346.9 | 362.6 | 372.9 | 350.6 | 332 | 356.8 | 370.2 | 344.7
1430.2 | 1154.2 | 470.1 | 188.04 | 219.8079 | 498.1 | 361.6 | 344.4 | 344 | 513 | 57.8 | 18.6 | 108.6 | 6 | 249.1 | 12.5 | 848.9 | 769.3 | 751.3 | 852.2 | 704 | 679.2 | 591.1 | 742.1 | 719.7 | 669.7 | 590 | 699.4 | 617.6 | 347 | 363.1 | 373.5 | 350.8 | 332.2 | 356.7 | 370.3 | 344.7
1431.2 | 1155.2 | 469.7 | 187.88 | 219.6209 | 498 | 361.8 | 345.2 | 344.6 | 513.1 | 57.9 | 18.6 | 108.6 | 5.3 | 257 | 11 | 848.4 | 766.1 | 759 | 851.9 | 704.1 | 679.5 | 589.2 | 747.5 | 718.4 | 669.8 | 590.3 | 703.5 | 615.2 | 347.2 | 363.8 | 374.2 | 351 | 332.3 | 356.6 | 370.6 | 344.8
1432.2 | 1156.2 | 469.1 | 187.64 | 219.3403 | 498.2 | 362.8 | 345.6 | 345.1 | 517.7 | 58 | 18.6 | 108.6 | 5.4 | 246.9 | 10 | 849.2 | 767.7 | 766.2 | 851.7 | 705.6 | 680 | 588.4 | 753.9 | 716.5 | 670.8 | 590.7 | 710.1 | 613.4 | 347.5 | 364.5 | 374.8 | 351.2 | 332.4 | 356.5 | 370.7 | 344.8
1433.2 | 1157.2 | 469 | 187.6 | 219.2936 | 499.7 | 363.1 | 346.6 | 345.9 | 520.2 | 58.1 | 18.6 | 108.6 | 7.2 | 269 | 9.4 | 851.5 | 770.1 | 770.5 | 852.8 | 707.8 | 680 | 588.6 | 761.3 | 720.9 | 673.8 | 591.1 | 713.9 | 611.6 | 347.8 | 364.9 | 375.1 | 351.3 | 332.6 | 356.4 | 370.8 | 344.8
1434.2 | 1158.2 | 470.3 | 188.12 | 219.9014 | 502.2 | 362.8 | 347.4 | 346.6 | 520.7 | 58.2 | 18.6 | 108.5 | 7.4 | 235.2 | 10.1 | 852.2 | 757.6 | 766.9 | 854.4 | 705.5 | 680.6 | 589.3 | 765.3 | 722.4 | 673.6 | 591.3 | 717.3 | 611.1 | 347.9 | 365.3 | 375.5 | 351.4 | 332.7 | 356.5 | 371 | 344.8
1435.2 | 1159.2 | 470.7 | 188.28 | 220.0885 | 505.4 | 363.8 | 347.9 | 347.7 | 530.7 | 58.2 | 18.6 | 108.6 | 7.2 | 261.5 | 10 | 851.9 | 750 | 762.9 | 855.2 | 704.4 | 681.4 | 587.5 | 758.8 | 716.6 | 673 | 591.4 | 717.3 | 610.7 | 347.9 | 365.9 | 375.9 | 351.5 | 332.8 | 356.6 | 371.2 | 344.9
1436.2 | 1160.2 | 470.8 | 188.32 | 220.1352 | 508.8 | 364.7 | 348.1 | 348.7 | 527.3 | 58.3 | 18.6 | 108.7 | 5.5 | 249.4 | 9.8 | 851.9 | 749.8 | 758.4 | 856.4 | 703.3 | 681.4 | 585.6 | 755.2 | 713.6 | 673.1 | 591.4 | 715.7 | 612.1 | 347.9 | 366.3 | 376.3 | 351.7 | 332.9 | 356.7 | 371.1 | 345
1437.2 | 1161.2 | 469.8 | 187.92 | 219.6677 | 514.5 | 365.3 | 348.2 | 349.7 | 525 | 58.2 | 18.6 | 108.7 | 6.2 | 245.6 | 10.7 | 851.6 | 747.9 | 745.9 | 857.3 | 700.8 | 681.3 | 584.9 | 750 | 710.7 | 671.9 | 591.3 | 707.4 | 616.4 | 348.1 | 366.4 | 377.4 | 351.7 | 333.1 | 356.6 | 371.1 | 345
1438.2 | 1162.2 | 470.6 | 188.24 | 220.0417 | 518.4 | 365.7 | 348.6 | 350 | 516.1 | 58.2 | 18.6 | 108.6 | 7.7 | 238.2 | 12.6 | 850.2 | 750.4 | 733.7 | 858.3 | 697.9 | 680.7 | 583.6 | 733.2 | 708.2 | 670 | 591.2 | 693.8 | 623.1 | 348.3 | 366.5 | 378 | 351.7 | 333.2 | 356.6 | 371.1 | 345
1439.2 | 1163.2 | 470.6 | 188.24 | 220.0417 | 519.5 | 365.2 | 348.4 | 350 | 508.7 | 58.2 | 18.6 | 108.6 | 7.4 | 249.9 | 15.4 | 848.8 | 753.2 | 715.5 | 858.9 | 695.3 | 680 | 582.1 | 720.5 | 705.7 | 668.2 | 591.1 | 682.7 | 630.9 | 348.5 | 366.7 | 378 | 351.8 | 333.3 | 356.5 | 371.1 | 345.1
1440.2 | 1164.2 | 470.8 | 188.32 | 220.1352 | 521.6 | 364.4 | 348.3 | 349.5 | 499.8 | 58.2 | 18.6 | 108.5 | 6.6 | 268.7 | 16 | 846.1 | 746.9 | 709.1 | 858.3 | 692.2 | 679 | 578.8 | 703.1 | 700.5 | 665.2 | 590.8 | 673.1 | 639.1 | 348.9 | 366.7 | 378 | 351.7 | 333.5 | 356.5 | 370.8 | 345.2
1441.2 | 1165.2 | 470.6 | 188.24 | 220.0417 | 519.8 | 364.2 | 348.9 | 348.3 | 490.1 | 58.2 | 18.6 | 108.4 | 6.7 | 251.6 | 15.4 | 845.3 | 743.8 | 706.7 | 857.9 | 689.9 | 678 | 577.8 | 700.5 | 701 | 664.2 | 590.2 | 668.3 | 646.7 | 349.3 | 366.6 | 377.7 | 351.7 | 333.7 | 356.3 | 370.2 | 345.3
1442.2 | 1166.2 | 469.8 | 187.92 | 219.6677 | 522.8 | 364.3 | 349 | 346.8 | 484.9 | 58.2 | 18.6 | 108.3 | 6.6 | 242.5 | 14 | 843 | 742.1 | 705.1 | 856.1 | 688.5 | 677.5 | 576.7 | 690.3 | 699 | 661.8 | 589.8 | 663.6 | 651 | 349.5 | 366.4 | 377.4 | 351.7 | 333.9 | 356.1 | 369.7 | 345.3
1443.2 | 1167.2 | 470.5 | 188.2 | 219.995 | 520.2 | 363.8 | 348.9 | 345.5 | 478.3 | 58.2 | 18.6 | 108.2 | 5.4 | 252.7 | 13.8 | 841.5 | 752.2 | 706.6 | 854.6 | 688.2 | 677.1 | 577.5 | 693.3 | 701.4 | 661.7 | 589.3 | 659.5 | 652.7 | 349.8 | 366 | 376.8 | 351.6 | 334 | 355.9 | 369.2 | 345.2
1444.2 | 1168.2 | 469.6 | 187.84 | 219.5741 | 517.2 | 362.7 | 348.8 | 344.6 | 474.2 | 58.3 | 18.6 | 108.2 | 7.2 | 253.9 | 13.6 | 840.9 | 771.2 | 716.8 | 854 | 690.9 | 676.5 | 580.4 | 695.3 | 706.4 | 663.9 | 588.9 | 653.9 | 653.9 | 349.9 | 365.6 | 376.4 | 351.4 | 334.2 | 355.7 | 368.6 | 345.3
1445.2 | 1169.2 | 469.7 | 187.88 | 219.6209 | 521.4 | 362.3 | 348.5 | 343.8 | 474.7 | 58.3 | 18.6 | 108.2 | 7.6 | 262.5 | 13 | 842.6 | 781.6 | 730.4 | 854.4 | 694.1 | 676.4 | 585.1 | 709.7 | 714.8 | 666.9 | 588.6 | 658 | 655 | 350.1 | 365.4 | 376.1 | 351.4 | 334.3 | 355.6 | 368.2 | 345.4
1446.2 | 1170.2 | 470.6 | 188.24 | 220.0417 | 522.1 | 363 | 348.1 | 343 | 476.9 | 58.3 | 18.6 | 108.3 | 8.3 | 257.2 | 11.6 | 842.8 | 785.2 | 740.8 | 854.7 | 696.4 | 676.9 | 586 | 717.4 | 717.9 | 667.6 | 588.1 | 664.1 | 654.7 | 350.1 | 365.4 | 376.1 | 351.4 | 334.4 | 355.3 | 368.5 | 345.3
1447.2 | 1171.2 | 470.3 | 188.12 | 219.9014 | 518.2 | 363.7 | 348.3 | 342.4 | 477.6 | 58.4 | 18.6 | 108.4 | 9.4 | 269.1 | 10 | 841.6 | 793.1 | 731.4 | 855.2 | 694.5 | 677.2 | 586.2 | 720.1 | 718.6 | 667.7 | 587.6 | 665.6 | 653.3 | 350 | 365.2 | 376 | 351.5 | 334.5 | 355 | 368.2 | 345.4
1448.2 | 1172.2 | 469.1 | 187.64 | 219.3403 | 513.9 | 363.6 | 348.3 | 342.1 | 476.8 | 58.4 | 18.5 | 108.3 | 8.6 | 270.9 | 10.2 | 842.1 | 797.1 | 734.1 | 855.6 | 695.3 | 677.5 | 587.7 | 732.3 | 721.3 | 668.9 | 587.3 | 668.6 | 652.9 | 350.2 | 364.9 | 375.8 | 351.5 | 334.6 | 354.8 | 367.8 | 345.4
1449.2 | 1173.2 | 470.8 | 188.32 | 220.1352 | 512.8 | 363.8 | 347.6 | 341.9 | 477.8 | 58.4 | 18.6 | 108.4 | 7.8 | 263.5 | 13.7 | 843.7 | 801 | 734.9 | 856.7 | 697.7 | 677.6 | 592 | 733.8 | 727.6 | 671.5 | 587 | 664.1 | 653.1 | 350.4 | 364.6 | 375.5 | 351.5 | 334.7 | 354.8 | 367.4 | 345.4
1450.2 | 1174.2 | 470.3 | 188.12 | 219.9014 | 512.3 | 363.4 | 347.2 | 341.2 | 477.1 | 58.4 | 18.6 | 108.7 | 7.7 | 263 | 15.6 | 846.3 | 804 | 760.7 | 858.1 | 701.7 | 677.5 | 594.2 | 740.7 | 729.1 | 673.2 | 586.6 | 672.6 | 653.4 | 350.4 | 364.3 | 375.3 | 351.4 | 334.8 | 355.3 | 367.4 | 345.4
1451.2 | 1175.2 | 470.6 | 188.24 | 220.0417 | 511.9 | 362.9 | 346.7 | 340.8 | 477.9 | 58.4 | 18.5 | 108.8 | 8 | 267.6 | 16.4 | 849.1 | 804.7 | 774.5 | 859.8 | 705.6 | 677.7 | 597.3 | 744.6 | 733.9 | 675.8 | 586.3 | 678.7 | 654 | 350.8 | 364.2 | 375.2 | 351.5 | 334.9 | 355.8 | 367.6 | 345.5
1452.2 | 1176.2 | 470.4 | 188.16 | 219.9482 | 510.4 | 362.7 | 346.3 | 340.5 | 475.7 | 58.4 | 18.5 | 108.8 | 9 | 259.5 | 16 | 850.5 | 809.7 | 779.9 | 861.9 | 707.6 | 678 | 597.2 | 748.1 | 734.5 | 675.2 | 586 | 682.5 | 655.8 | 350.9 | 364.1 | 375.2 | 351.6 | 335 | 355.9 | 367.4 | 345.5
1453.2 | 1177.2 | 469.8 | 187.92 | 219.6677 | 509.5 | 363.5 | 345.8 | 340.7 | 474.6 | 58.5 | 18.5 | 108.8 | 8.6 | 263.1 | 17.7 | 850.8 | 811.3 | 773 | 864.3 | 707.3 | 678.5 | 596.5 | 751.9 | 735.9 | 675.9 | 585.9 | 685.5 | 657.5 | 351 | 363.9 | 375.1 | 351.7 | 335.2 | 356.1 | 367.4 | 345.5
1454.2 | 1178.2 | 471 | 188.4 | 220.2287 | 508.8 | 363.6 | 345.9 | 340.8 | 473.9 | 58.5 | 18.5 | 108.8 | 8.4 | 268.2 | 19.4 | 849.7 | 812.7 | 764.4 | 865.7 | 704.8 | 678.4 | 593.1 | 741.1 | 732.3 | 674.1 | 585.6 | 678.8 | 658.8 | 351 | 363.7 | 374.9 | 351.7 | 335.2 | 356.3 | 367.9 | 345.6
1455.2 | 1179.2 | 470.6 | 188.24 | 220.0417 | 510.9 | 363.4 | 345.9 | 340.9 | 472.2 | 58.5 | 18.5 | 108.8 | 10.4 | 274.9 | 19.7 | 850.1 | 815.1 | 754.9 | 867.2 | 705.1 | 678.2 | 593.6 | 735 | 734.1 | 674.8 | 585.2 | 675 | 659.8 | 351.2 | 363.4 | 374.7 | 351.6 | 335.3 | 356.4 | 368 | 345.7
1456.2 | 1180.2 | 471.1 | 188.44 | 220.2755 | 511.1 | 363.3 | 346.3 | 341 | 472.1 | 58.6 | 18.5 | 108.7 | 9.1 | 252 | 19.1 | 848.3 | 803.9 | 743.7 | 866.8 | 701.9 | 677.9 | 592.5 | 724.6 | 730.7 | 672.6 | 584.9 | 670 | 661.7 | 351.2 | 363.2 | 374.4 | 351.6 | 335.4 | 356.3 | 367.6 | 345.7
1457.2 | 1181.2 | 470.5 | 188.2 | 219.995 | 507.2 | 363.2 | 346.5 | 340.6 | 468.2 | 58.7 | 18.5 | 108.6 | 8.2 | 264.2 | 16.9 | 845.3 | 792.3 | 729.7 | 864 | 698 | 677.4 | 588.7 | 703.4 | 721 | 668.9 | 584.5 | 663.2 | 662 | 351.4 | 363 | 374.1 | 351.6 | 335.5 | 356.1 | 367.3 | 345.7
1458.2 | 1182.2 | 470.7 | 188.28 | 220.0885 | 503.3 | 362.8 | 346.2 | 340 | 464.7 | 58.7 | 18.5 | 108.5 | 8.3 | 261.4 | 15 | 841.4 | 784.2 | 716.1 | 860.3 | 694.6 | 676.7 | 584.4 | 690.4 | 713.6 | 666.2 | 584.1 | 655.8 | 664.1 | 351.7 | 362.8 | 373.8 | 351.6 | 335.6 | 355.9 | 366.8 | 345.7
1459.2 | 1183.2 | 469.7 | 187.88 | 219.6209 | 504.7 | 362.1 | 345.6 | 339.6 | 459.7 | 58.7 | 18.5 | 108.5 | 8 | 261.9 | 14.7 | 839.3 | 773.4 | 702.4 | 856.4 | 692.6 | 676 | 580.1 | 680.4 | 707.5 | 663.5 | 583.6 | 648.9 | 665.7 | 352 | 362.6 | 374.2 | 351.6 | 335.7 | 355.5 | 366.2 | 345.6
1460.2 | 1184.2 | 470.3 | 188.12 | 219.9014 | 503.4 | 361.5 | 345.5 | 338.5 | 453.7 | 58.6 | 18.5 | 108.6 | 7.1 | 263.2 | 14.3 | 836.9 | 760.2 | 685.2 | 852.3 | 687.8 | 675.2 | 575.4 | 665.8 | 699.9 | 659.9 | 583.1 | 641.7 | 666.9 | 352.1 | 362.1 | 373.7 | 351.7 | 335.8 | 355.2 | 365.9 | 345.6
1461.2 | 1185.2 | 469 | 187.6 | 219.2936 | 500.1 | 361.2 | 345.5 | 337.3 | 449.7 | 58.6 | 18.5 | 108.8 | 7.5 | 267.7 | 15.7 | 834.4 | 773 | 686.6 | 848.6 | 684.7 | 674.4 | 572.2 | 663.5 | 697.8 | 659.1 | 582.5 | 638 | 667.5 | 352.1 | 361.5 | 373 | 351.6 | 335.9 | 355.2 | 365.7 | 345.5
1462.2 | 1186.2 | 470.3 | 188.12 | 219.9014 | 497.7 | 361.2 | 344.6 | 336.8 | 451.1 | 58.6 | 18.5 | 109.1 | 9.3 | 261.7 | 17.2 | 833.3 | 780.2 | 702.1 | 845.9 | 685.1 | 673.8 | 571.3 | 675 | 698.5 | 658.6 | 581.9 | 642.9 | 667.4 | 352.1 | 360.2 | 372.1 | 351.6 | 336 | 355.2 | 365.6 | 345.5
1463.2 | 1187.2 | 470.3 | 188.12 | 219.9014 | 495.3 | 361 | 343.3 | 336 | 455.4 | 58.7 | 18.5 | 109.1 | 9 | 267.1 | 18.5 | 831.1 | 783.7 | 708.9 | 843.1 | 686.4 | 673.5 | 571.6 | 677.3 | 700.1 | 659.1 | 581.4 | 644.8 | 666.5 | 352.4 | 359.7 | 371.3 | 351.5 | 336.1 | 355.5 | 365.3 | 345.6
1464.2 | 1188.2 | 470.4 | 188.16 | 219.9482 | 496.4 | 361 | 342.3 | 335.7 | 456.8 | 58.7 | 18.5 | 109.2 | 7.8 | 265.7 | 20.1 | 830.5 | 796.2 | 718.3 | 841.7 | 688.7 | 673 | 574.9 | 685.1 | 707.9 | 660.9 | 580.9 | 647.5 | 667.3 | 352.4 | 359.4 | 371 | 351.5 | 336.2 | 355.7 | 364.9 | 345.6
1465.2 | 1189.2 | 470.3 | 188.12 | 219.9014 | 496.6 | 361 | 341.6 | 335.7 | 457 | 58.7 | 18.5 | 109.3 | 7.6 | 264.2 | 19.6 | 829.8 | 799.1 | 716.5 | 841.2 | 688.3 | 672.8 | 578.2 | 685.8 | 711.2 | 661.8 | 580.5 | 644.5 | 667.2 | 352.5 | 359.1 | 371.3 | 351.4 | 336.2 | 356 | 364.6 | 345.5
1466.2 | 1190.2 | 470.1 | 188.04 | 219.8079 | 496.7 | 360.3 | 340.9 | 335 | 455.3 | 58.8 | 18.5 | 109.5 | 7.9 | 269.1 | 18.4 | 828.6 | 802 | 714.9 | 840.6 | 687.4 | 672.2 | 578.6 | 685.8 | 712.1 | 660.3 | 580 | 641.3 | 666.5 | 352.6 | 359.2 | 371.4 | 351.4 | 336.3 | 356.5 | 364.9 | 345.5
1467.2 | 1191.2 | 470.4 | 188.16 | 219.9482 | 495.7 | 359.4 | 340.7 | 334.9 | 457.6 | 58.8 | 18.5 | 109.6 | 8.2 | 266 | 17.6 | 829 | 799.7 | 712.6 | 840.4 | 687.1 | 671.9 | 580.4 | 689.6 | 712.4 | 659.8 | 579.5 | 642.9 | 666.1 | 352.6 | 359.2 | 370.8 | 351.5 | 336.3 | 357.1 | 365.2 | 345.6
1468.2 | 1192.2 | 469.3 | 187.72 | 219.4339 | 493.8 | 358.5 | 340.7 | 335.3 | 457.7 | 58.9 | 18.5 | 109.8 | 8.7 | 272.5 | 16.6 | 829.1 | 801.3 | 719.5 | 840.9 | 686.6 | 671.8 | 582.8 | 695.1 | 713.8 | 660.4 | 579.1 | 647.9 | 666 | 352.8 | 359.1 | 370.5 | 351.4 | 336.4 | 357.7 | 365 | 345.6
1469.2 | 1193.2 | 469.1 | 187.64 | 219.3403 | 490.7 | 357.8 | 340.2 | 335.3 | 459.1 | 58.9 | 18.5 | 110 | 7.9 | 272.9 | 16.1 | 829.9 | 806.9 | 726 | 841.8 | 688 | 671.6 | 585.3 | 707.7 | 717.5 | 662.1 | 578.8 | 651.1 | 666.1 | 352.9 | 359.1 | 370.6 | 351.4 | 336.5 | 358.1 | 365.1 | 345.6
1470.2 | 1194.2 | 469.6 | 187.84 | 219.5741 | 487.8 | 357.5 | 340 | 335.1 | 456.7 | 58.9 | 18.5 | 110.1 | 6.8 | 259 | 15.6 | 829.2 | 805 | 728.8 | 842.2 | 687.1 | 671.5 | 586 | 704.6 | 717.1 | 662.2 | 578.3 | 647.7 | 665.5 | 352.9 | 359 | 370.6 | 351.3 | 336.5 | 358.3 | 365 | 345.7
1471.2 | 1195.2 | 469.2 | 187.68 | 219.3871 | 485.3 | 357.3 | 340 | 334.7 | 456.1 | 58.9 | 18.5 | 110.2 | 7.5 | 263.5 | 15.4 | 827.8 | 801.8 | 730.6 | 841.8 | 687.4 | 670.9 | 584.6 | 697.8 | 714.5 | 660.4 | 577.8 | 642.8 | 664 | 353.2 | 358.8 | 370.5 | 351.2 | 336.6 | 358.5 | 365 | 345.7
1472.2 | 1196.2 | 469 | 187.6 | 219.2936 | 484.2 | 357 | 340.2 | 334.6 | 456.3 | 58.9 | 18.5 | 110.2 | 6.4 | 263.2 | 15.2 | 826.2 | 791.9 | 722.8 | 841 | 684.2 | 670.2 | 583.3 | 687.7 | 709.2 | 658.6 | 577.3 | 638.8 | 662.4 | 353.4 | 358.9 | 370.7 | 351.3 | 336.7 | 358.8 | 365.2 | 345.8
1473.2 | 1197.2 | 470.4 | 188.16 | 219.9482 | 486.3 | 357.1 | 340 | 335 | 457 | 58.9 | 18.5 | 110.3 | 6.1 | 261.1 | 14.8 | 823.8 | 784.1 | 704.3 | 839.5 | 679.7 | 669.4 | 580.2 | 675.9 | 703.9 | 655.8 | 576.7 | 631.6 | 661.2 | 353.4 | 358.7 | 370.5 | 351.2 | 336.7 | 359.1 | 365.6 | 345.8
1474.2 | 1198.2 | 470.4 | 188.16 | 219.9482 | 487.3 | 357 | 339.9 | 335 | 458.1 | 58.9 | 18.5 | 110.3 | 7.1 | 265 | 14.6 | 819 | 773.3 | 682.8 | 835.2 | 675.2 | 668.3 | 576.6 | 654.5 | 697.2 | 652.2 | 576 | 622.4 | 657.9 | 353.6 | 358.5 | 370.3 | 351 | 336.8 | 359.8 | 366.2 | 346.1
1475.2 | 1199.2 | 470.7 | 188.28 | 220.0885 | 489.1 | 356.9 | 339.7 | 335.1 | 460.8 | 58.8 | 18.5 | 110.3 | 7.5 | 267.8 | 14.3 | 814.4 | 768.1 | 677.2 | 830 | 673.2 | 667.2 | 572.8 | 640.5 | 691.8 | 649.5 | 575.1 | 615.4 | 655.2 | 353.7 | 358.3 | 370.3 | 350.9 | 336.9 | 360.5 | 367 | 346.2
1476.2 | 1200.2 | 470.8 | 188.32 | 220.1352 | 493.5 | 356.9 | 339.6 | 336.1 | 466.4 | 58.8 | 18.5 | 110.3 | 6.5 | 274.3 | 13.3 | 809.9 | 765.4 | 659.3 | 824.1 | 669.8 | 666.2 | 571.8 | 625.5 | 689.1 | 647.5 | 574.3 | 609 | 651.1 | 353.7 | 358 | 370.3 | 350.7 | 337 | 361.2 | 367.4 | 346.4
1477.2 | 1201.2 | 470.6 | 188.24 | 220.0417 | 493.6 | 357.1 | 340.2 | 337.6 | 471.3 | 58.8 | 18.5 | 110.3 | 7 | 271.8 | 12.9 | 806.2 | 764.9 | 653.1 | 818.7 | 666 | 664.9 | 570.6 | 615.9 | 685.7 | 645.5 | 573.6 | 603.6 | 647 | 353.6 | 357.7 | 370.4 | 350.6 | 337.1 | 361.9 | 367.9 | 346.6
1478.2 | 1202.2 | 470.5 | 188.2 | 219.995 | 494.5 | 357.5 | 341.3 | 338.7 | 467.6 | 58.8 | 18.5 | 110.3 | 6.4 | 272.4 | 13.2 | 804.5 | 770.1 | 663.9 | 814.8 | 666.2 | 663.9 | 570.1 | 618.2 | 686.5 | 644.3 | 573 | 602.8 | 643.8 | 353.8 | 357.5 | 370.7 | 350.5 | 337.2 | 362.3 | 368.3 | 346.7
1479.2 | 1203.2 | 467.7 | 187.08 | 218.6857 | 493.8 | 358.1 | 342.3 | 339.3 | 469.3 | 58.9 | 18.5 | 110.4 | 6.9 | 267.4 | 13.3 | 804.5 | 779.4 | 685.3 | 812.2 | 669.4 | 663.4 | 573.6 | 632.2 | 694.4 | 646.9 | 572.4 | 605.3 | 641.1 | 353.9 | 357.3 | 370.8 | 350.5 | 337.3 | 362.8 | 368.8 | 346.8
1480.2 | 1204.2 | 470.3 | 188.12 | 219.9014 | 491.8 | 358.6 | 343.1 | 339.5 | 475.1 | 58.9 | 18.5 | 110.5 | 6.5 | 266.1 | 13.7 | 803.6 | 786.9 | 694.4 | 810.7 | 670.9 | 663.1 | 580.3 | 639.6 | 705.4 | 650.7 | 571.9 | 605.2 | 637.8 | 354.1 | 357.2 | 370.6 | 350.5 | 337.4 | 363.3 | 369.1 | 346.9
1481.2 | 1205.2 | 470 | 188 | 219.7612 | 493.2 | 359 | 343.5 | 340 | 482.6 | 58.9 | 18.5 | 110.6 | 6.4 | 258 | 13.8 | 803.5 | 797.2 | 687.6 | 810.1 | 671.2 | 662.8 | 586.2 | 649.6 | 713.2 | 653.4 | 571.4 | 602.6 | 635.6 | 354.3 | 357.2 | 370.5 | 350.5 | 337.5 | 363.7 | 369.8 | 347
1482.2 | 1206.2 | 470 | 188 | 219.7612 | 493.6 | 359.3 | 343.3 | 340.2 | 484.8 | 59 | 18.5 | 110.7 | 6 | 265.4 | 13.7 | 802 | 800.9 | 684 | 809.5 | 669.8 | 662.4 | 588.9 | 650.5 | 713.3 | 653.1 | 570.9 | 600.4 | 633.2 | 354.4 | 357.1 | 370.4 | 350.5 | 337.6 | 364.1 | 370.2 | 347.1
1483.2 | 1207.2 | 469.5 | 187.8 | 219.5274 | 493.8 | 360.5 | 343 | 340.7 | 486.9 | 59 | 18.5 | 110.8 | 5.6 | 272.3 | 12.1 | 799.8 | 803.7 | 679.5 | 808.4 | 668 | 662.3 | 593 | 652.8 | 719 | 653.8 | 570.6 | 598.5 | 631.6 | 354.5 | 357.1 | 370.4 | 350.4 | 337.7 | 364.6 | 371.3 | 347.2
1484.2 | 1208.2 | 469.3 | 187.72 | 219.4339 | 493.8 | 361.2 | 343 | 341.9 | 491.1 | 59 | 18.5 | 110.7 | 6.1 | 260 | 11 | 797.6 | 798.3 | 671.2 | 806.8 | 665.3 | 661.8 | 592.6 | 652.1 | 716.1 | 653.1 | 570.2 | 595.8 | 631.9 | 354.7 | 357 | 370.5 | 350.3 | 337.8 | 365.1 | 372 | 347.2
1485.2 | 1209.2 | 469.9 | 187.96 | 219.7144 | 492.4 | 361.4 | 343.2 | 342.7 | 497.2 | 59 | 18.5 | 110.6 | 6 | 261.3 | 12.1 | 794.5 | 796.8 | 646.8 | 804.3 | 660.4 | 661.3 | 593.2 | 638 | 715.3 | 651.1 | 569.8 | 590.1 | 631.3 | 354.7 | 357 | 370.7 | 350.3 | 338 | 365.8 | 372.8 | 347.4
1486.2 | 1210.2 | 469.8 | 187.92 | 219.6677 | 492.8 | 361.3 | 343 | 343.4 | 499.5 | 59.1 | 18.5 | 110.4 | 6.3 | 258.6 | 11.5 | 791.5 | 804 | 635.5 | 801.2 | 657.8 | 660.9 | 594.4 | 634.3 | 715.9 | 652.1 | 569.4 | 585.7 | 628.6 | 354.7 | 357.1 | 370.9 | 350.2 | 338.1 | 366.6 | 373.8 | 347.7
1487.2 | 1211.2 | 469.8 | 187.92 | 219.6677 | 492.8 | 361.1 | 343.1 | 344.6 | 504.7 | 59.1 | 18.5 | 110.3 | 7.6 | 254.9 | 12 | 790.7 | 810.8 | 652.3 | 799.1 | 660.9 | 660.8 | 598.5 | 639.6 | 717.1 | 654.5 | 569.1 | 584.6 | 625.2 | 354.7 | 357.2 | 371.2 | 350.2 | 338.2 | 367.1 | 374.8 | 347.9
1488.2 | 1212.2 | 469.9 | 187.96 | 219.7144 | 492.5 | 362.1 | 343.7 | 345.6 | 506.8 | 59.2 | 18.5 | 110.1 | 7.7 | 262.3 | 12.2 | 791 | 816.4 | 679 | 797.9 | 666.6 | 660.6 | 601 | 643.9 | 718.3 | 656.9 | 568.9 | 591.9 | 621.8 | 354.8 | 357.2 | 371.3 | 350.2 | 338.3 | 367.5 | 375.5 | 348
1489.2 | 1213.2 | 469.7 | 187.88 | 219.6209 | 490.7 | 363.2 | 344.5 | 345.9 | 504 | 59.2 | 18.5 | 109.8 | 6.7 | 277.1 | 11 | 794.5 | 819.5 | 716.5 | 798.4 | 674.1 | 661.1 | 605.4 | 670.6 | 726.3 | 661.3 | 568.9 | 610.3 | 619.2 | 354.9 | 357.2 | 371.2 | 350.3 | 338.4 | 367.9 | 376.1 | 348
1490.2 | 1214.2 | 469.9 | 187.96 | 219.7144 | 487.9 | 364.6 | 345 | 345.9 | 503.4 | 59.2 | 18.5 | 109.5 | 5.9 | 259.3 | 9.6 | 797.9 | 819.3 | 739.7 | 800.3 | 680.4 | 662.2 | 607.1 | 698.8 | 732.5 | 665.4 | 568.9 | 627.2 | 616.4 | 355.1 | 357.5 | 371.3 | 350.5 | 338.6 | 367.9 | 376.3 | 348.1
1491.2 | 1215.2 | 469.9 | 187.96 | 219.7144 | 488.8 | 366 | 345.2 | 346 | 502.5 | 59.3 | 18.5 | 109.2 | 6.2 | 262.8 | 9.4 | 801 | 826.6 | 755.8 | 803.3 | 686.3 | 663.1 | 610.3 | 718.3 | 739.2 | 669.5 | 569.1 | 638.2 | 613.7 | 355.1 | 357.8 | 371.4 | 350.6 | 338.8 | 368.1 | 376.3 | 348.1
1492.2 | 1216.2 | 469.1 | 187.64 | 219.3403 | 484.3 | 367.3 | 345.1 | 346.1 | 500.9 | 59.3 | 18.5 | 108.9 | 6.1 | 271.4 | 9.6 | 803.4 | 835 | 764.7 | 807.1 | 689.8 | 664.2 | 612.7 | 735.5 | 742.6 | 673.1 | 569.4 | 647.2 | 611.7 | 355.1 | 357.9 | 371.4 | 350.7 | 339 | 368.3 | 376.3 | 348.2
1493.2 | 1217.2 | 470.6 | 188.24 | 220.0417 | 482.7 | 368.4 | 344.4 | 346 | 500 | 59.2 | 18.5 | 108.8 | 6.7 | 261.5 | 9.5 | 804.8 | 834.6 | 767.2 | 810.8 | 692.2 | 665.1 | 615 | 744.2 | 745.9 | 675.1 | 569.6 | 654.2 | 610.3 | 355.2 | 358.3 | 371.6 | 350.9 | 339.2 | 368.4 | 376 | 348.3
1494.2 | 1218.2 | 469.1 | 187.64 | 219.3403 | 482.9 | 369.6 | 344.2 | 346 | 499 | 59.3 | 18.5 | 108.9 | 6.4 | 264.6 | 10.5 | 807.9 | 836.1 | 772.4 | 815 | 695.2 | 665.9 | 615.6 | 752.9 | 746.9 | 678.2 | 569.8 | 661.6 | 609.3 | 355.5 | 358.7 | 371.7 | 351 | 339.3 | 368.3 | 375.8 | 348.2
1495.2 | 1219.2 | 469.1 | 187.64 | 219.3403 | 479.9 | 370.4 | 343.5 | 346.2 | 496.9 | 59.3 | 18.5 | 108.8 | 6.1 | 252.8 | 12 | 808.9 | 835.3 | 770.4 | 818.7 | 695.4 | 666.2 | 613.2 | 753.5 | 746.6 | 678.3 | 569.9 | 663.1 | 608.6 | 355.7 | 358.8 | 371.9 | 351 | 339.4 | 368.1 | 375.5 | 348.2
1496.2 | 1220.2 | 470.8 | 188.32 | 220.1352 | 475.5 | 369.8 | 343.2 | 345.9 | 492.7 | 59.3 | 18.5 | 108.8 | 5.2 | 250.6 | 12.4 | 812.1 | 834.3 | 771.6 | 822.5 | 698.2 | 666.9 | 611 | 758.5 | 746 | 678.8 | 569.9 | 664.4 | 608.9 | 355.8 | 358.8 | 371.8 | 351 | 339.6 | 368 | 374.9 | 348.2
1497.2 | 1221.2 | 467.7 | 187.08 | 218.6857 | 472.1 | 369.4 | 342.6 | 345.2 | 489.1 | 59.4 | 18.5 | 108.7 | 4.7 | 237 | 12.1 | 813.9 | 835.5 | 761.7 | 826.2 | 699.4 | 667.5 | 613.7 | 758.7 | 749.6 | 682.3 | 570 | 663 | 610.5 | 356 | 358.9 | 371.8 | 351 | 339.7 | 368 | 374.3 | 348.3
1498.2 | 1222.2 | 468.2 | 187.28 | 218.9195 | 469.6 | 369.3 | 342.3 | 344.4 | 487.5 | 59.4 | 18.5 | 108.6 | 5 | 249.6 | 11.7 | 816.1 | 835.5 | 760.9 | 829.4 | 701.4 | 668 | 613.9 | 755.8 | 747.6 | 683 | 570.1 | 665.2 | 614.1 | 356.1 | 358.9 | 371.9 | 351 | 339.9 | 367.8 | 373.8 | 348.3
1499.2 | 1223.2 | 469 | 187.6 | 219.2936 | 470 | 370 | 342.3 | 344.3 | 491.5 | 59.4 | 18.5 | 108.4 | 5.2 | 251.1 | 10.6 | 818.4 | 838.2 | 754.9 | 832.8 | 703.5 | 668.8 | 616.9 | 750 | 751.5 | 687.3 | 570.2 | 659.8 | 615.1 | 356.2 | 358.9 | 371.9 | 350.9 | 340 | 367.9 | 373.6 | 348.4
1500.2 | 1224.2 | 468.9 | 187.56 | 219.2468 | 468.8 | 371 | 342.3 | 344.1 | 498.1 | 59.4 | 18.5 | 108.3 | 5.9 | 250.8 | 9.5 | 820.2 | 838.1 | 755.3 | 835.1 | 706.8 | 669.6 | 618 | 753.9 | 755.3 | 690 | 570.4 | 659.2 | 615.9 | 356.4 | 358.8 | 371.8 | 350.9 | 340.2 | 367.6 | 373.3 | 348.4
1501.2 | 1225.2 | 468.7 | 187.48 | 219.1533 | 474.6 | 372.2 | 342.4 | 343.8 | 496.6 | 59.4 | 18.5 | 108.2 | 6.4 | 259 | 9.9 | 821 | 840.3 | 746 | 836.9 | 706.6 | 670.6 | 620.3 | 741.5 | 756.2 | 692.5 | 570.6 | 654.3 | 614.4 | 356.4 | 358.9 | 371.8 | 350.8 | 340.3 | 367.6 | 373.1 | 348.5
1502.2 | 1226.2 | 468.5 | 187.4 | 219.0598 | 475.8 | 373.3 | 342.7 | 343.3 | 494.9 | 59.4 | 18.5 | 108.3 | 6.7 | 263.8 | 8.9 | 822.7 | 839.7 | 753.2 | 838.9 | 709.8 | 671.4 | 620.8 | 741.4 | 757.8 | 693.7 | 570.9 | 654.8 | 613 | 356.4 | 358.8 | 371.8 | 350.7 | 340.4 | 367.3 | 373.1 | 348.5
1503.2 | 1227.2 | 469.2 | 187.68 | 219.3871 | 474.8 | 374.9 | 343.4 | 343.3 | 498.5 | 59.4 | 18.5 | 108.4 | 6.4 | 240.9 | 7.6 | 826.5 | 842.8 | 764 | 841.2 | 711.7 | 672.5 | 621.3 | 744.8 | 758.5 | 695.8 | 571.1 | 659.1 | 611.6 | 356.5 | 358.7 | 371.6 | 350.7 | 340.5 | 367.2 | 373.1 | 348.5
1504.2 | 1228.2 | 470.3 | 188.12 | 219.9014 | 476 | 375.8 | 344.3 | 343.8 | 495.9 | 59.4 | 18.5 | 108.6 | 7.1 | 251.8 | 7.1 | 830.3 | 844.9 | 768.5 | 844.1 | 713.1 | 673.5 | 622.4 | 748.9 | 761.9 | 697.5 | 571.3 | 662.3 | 612.8 | 356.7 | 358.7 | 371.5 | 350.8 | 340.7 | 367.2 | 373.1 | 348.6
1505.2 | 1229.2 | 471.3 | 188.52 | 220.369 | 477.2 | 377.8 | 344.7 | 344 | 494.1 | 59.5 | 18.5 | 108.8 | 8.2 | 257.6 | 9.1 | 832.8 | 847.2 | 768.5 | 847.1 | 713.5 | 674.8 | 622.4 | 757.6 | 764 | 699.3 | 571.6 | 671 | 614.7 | 356.9 | 358.7 | 371.5 | 350.9 | 340.8 | 367.2 | 372.9 | 348.6
1506.2 | 1230.2 | 469.4 | 187.76 | 219.4806 | 477.5 | 378.9 | 345 | 343.8 | 492.6 | 59.5 | 18.5 | 108.9 | 7.3 | 250.8 | 10.7 | 833.6 | 841.9 | 773.1 | 849.3 | 713.9 | 675.8 | 619.7 | 753.8 | 761.3 | 697.3 | 571.8 | 676.3 | 615.5 | 357 | 358.9 | 371.6 | 351 | 340.9 | 367.2 | 372.7 | 348.6
1507.2 | 1231.2 | 469.6 | 187.84 | 219.5741 | 476.4 | 378.6 | 345 | 343.6 | 494.7 | 59.5 | 18.5 | 108.9 | 6 | 244 | 10.7 | 835 | 822 | 758.3 | 850.7 | 711.3 | 676.8 | 615.1 | 750.9 | 754 | 694.9 | 572 | 680.2 | 616.3 | 357.2 | 359.3 | 371.8 | 351.4 | 341 | 367 | 372.4 | 348.5
1508.2 | 1232.2 | 470.2 | 188.08 | 219.8547 | 474.6 | 378.6 | 345.4 | 343.4 | 493.1 | 59.5 | 18.5 | 108.8 | 5.9 | 256.6 | 10.8 | 836.7 | 815.7 | 759.8 | 852.5 | 710.6 | 677.5 | 610.1 | 751.5 | 749.6 | 694.1 | 572.2 | 682.4 | 617.7 | 357.4 | 359.5 | 371.8 | 351.5 | 341.1 | 366.8 | 372.1 | 348.5
1509.2 | 1233.2 | 470.8 | 188.32 | 220.1352 | 472.6 | 377.9 | 345.6 | 343.3 | 489.1 | 59.5 | 18.5 | 108.8 | 6.3 | 252.7 | 14 | 838.5 | 821.6 | 762.5 | 854.1 | 711.1 | 678.1 | 609 | 751 | 749.3 | 693.5 | 572.1 | 683.7 | 618.1 | 357.7 | 359.6 | 372.1 | 351.5 | 341.2 | 366.7 | 371.9 | 348.4
1510.2 | 1234.2 | 470.6 | 188.24 | 220.0417 | 466.6 | 377.4 | 345.4 | 343.7 | 487.7 | 59.5 | 18.5 | 108.7 | 5.2 | 265.7 | 15.4 | 840.4 | 830.6 | 759.9 | 855.7 | 709.9 | 678.8 | 611.9 | 753.2 | 752.5 | 695.5 | 572.2 | 683.6 | 618.6 | 357.8 | 359.8 | 372.4 | 351.6 | 341.3 | 366.6 | 371.8 | 348.4
1511.2 | 1235.2 | 471 | 188.4 | 220.2287 | 464.9 | 377 | 344.9 | 343.6 | 488.5 | 59.5 | 18.5 | 108.7 | 4.3 | 259.6 | 16.7 | 842.5 | 838.9 | 760.5 | 857.7 | 712.7 | 679.6 | 613.6 | 756.5 | 754.8 | 697.6 | 572.5 | 684 | 620.6 | 357.7 | 360 | 372.4 | 351.6 | 341.4 | 366.5 | 371.5 | 348.4
1512.2 | 1236.2 | 470.3 | 188.12 | 219.9014 | 464.3 | 377.6 | 345.1 | 343 | 486.1 | 59.5 | 18.5 | 108.6 | 5 | 259.6 | 16.6 | 845.7 | 841.2 | 773.1 | 859.6 | 716.2 | 680.8 | 616 | 761.7 | 759.8 | 699.5 | 572.7 | 691.3 | 622.5 | 357.8 | 360.1 | 372.3 | 351.6 | 341.5 | 366.4 | 371.5 | 348.4
1513.2 | 1237.2 | 470.5 | 188.2 | 219.995 | 464.5 | 378 | 345.5 | 342.5 | 486.2 | 59.6 | 18.5 | 108.5 | 6.6 | 258.1 | 15.4 | 847.4 | 838.8 | 780.4 | 861.3 | 719.9 | 681.4 | 617.3 | 762 | 762.2 | 700.6 | 572.9 | 695.1 | 622.4 | 358 | 360 | 372.2 | 351.5 | 341.6 | 366.2 | 371.4 | 348.4
1514.2 | 1238.2 | 468.7 | 187.48 | 219.1533 | 462.4 | 378.2 | 345.6 | 342.7 | 487.2 | 59.6 | 18.4 | 108.6 | 8.6 | 275.6 | 14.2 | 847.8 | 837.4 | 780.5 | 862.5 | 720.7 | 681.8 | 615.3 | 761.4 | 758.2 | 699.5 | 573.2 | 697.7 | 622.2 | 358.2 | 360.1 | 372.1 | 351.6 | 341.7 | 365.9 | 372 | 348.4
1515.2 | 1239.2 | 471.8 | 188.72 | 220.6028 | 461.8 | 378.3 | 345.2 | 343.5 | 488.5 | 59.5 | 18.5 | 108.6 | 8.7 | 265.9 | 13.3 | 850.1 | 842.3 | 785.9 | 863.9 | 723.3 | 683 | 615.4 | 767.6 | 758.7 | 702.2 | 573.5 | 698.1 | 622.2 | 358.2 | 360.2 | 372 | 351.6 | 341.8 | 365.7 | 371.7 | 348.4
1516.2 | 1240.2 | 470.1 | 188.04 | 219.8079 | 459.6 | 378.6 | 344.6 | 343.8 | 491.2 | 59.5 | 18.5 | 108.8 | 7.6 | 256.5 | 14.3 | 852.5 | 847.4 | 787.2 | 865.7 | 726.3 | 683.7 | 619.1 | 767.3 | 765.2 | 704.7 | 573.7 | 696.3 | 621.2 | 358.3 | 360.3 | 371.9 | 351.6 | 341.9 | 365.7 | 371.6 | 348.4
1517.2 | 1241.2 | 468.8 | 187.52 | 219.2001 | 455 | 378.6 | 344 | 344.2 | 492.8 | 59.5 | 18.5 | 108.7 | 7.7 | 264.1 | 15.9 | 853.9 | 848.6 | 783.5 | 867.6 | 726.1 | 683.9 | 620.3 | 758.1 | 769.6 | 705 | 573.8 | 690.9 | 620.3 | 358.4 | 360.4 | 371.9 | 351.4 | 341.9 | 365.7 | 371.6 | 348.5
1518.2 | 1242.2 | 469.1 | 187.64 | 219.3403 | 452.7 | 378.7 | 343.6 | 344.6 | 489.7 | 59.5 | 18.4 | 108.7 | 7.1 | 262.5 | 16.4 | 854.7 | 847.8 | 787 | 867.9 | 729.8 | 684.2 | 619.8 | 751.9 | 769.8 | 705.5 | 573.9 | 692 | 619.9 | 358.6 | 360.4 | 371.9 | 351.4 | 342 | 365.7 | 371.7 | 348.6
1519.2 | 1243.2 | 469.6 | 187.84 | 219.5741 | 452.2 | 378.4 | 343.5 | 344.9 | 488.3 | 59.5 | 18.4 | 108.7 | 6.2 | 259 | 14.9 | 856.2 | 851.7 | 795.1 | 868.1 | 733.8 | 685 | 621.6 | 753.5 | 768.8 | 706.8 | 574 | 694.6 | 618.6 | 358.7 | 360.4 | 371.8 | 351.4 | 342.1 | 365.7 | 371.3 | 348.6
1520.2 | 1244.2 | 470.3 | 188.12 | 219.9014 | 452.1 | 378.8 | 343.1 | 344.6 | 487.3 | 59.5 | 18.5 | 108.7 | 5.9 | 261.6 | 13 | 857.1 | 852 | 790.3 | 868 | 735.1 | 685.8 | 620.8 | 750.9 | 768 | 707.6 | 574 | 691.8 | 617.4 | 358.9 | 360.3 | 371.7 | 351.4 | 342.2 | 365.6 | 371 | 348.6
1521.2 | 1245.2 | 469.7 | 187.88 | 219.6209 | 451.5 | 379.4 | 342.9 | 344.5 | 484.4 | 59.5 | 18.5 | 108.8 | 6.1 | 259.9 | 12.8 | 857.8 | 850.7 | 791.6 | 868.3 | 735.8 | 685.9 | 618.6 | 744.6 | 767.1 | 707.2 | 574 | 686.2 | 616.5 | 359.1 | 360.2 | 371.7 | 351.3 | 342.3 | 365.5 | 370.6 | 348.6
1522.2 | 1246.2 | 469 | 187.6 | 219.2936 | 450.1 | 379.9 | 342.6 | 344.1 | 481.2 | 59.5 | 18.5 | 108.9 | 6.6 | 258.5 | 11.6 | 858.9 | 846.9 | 793.8 | 868.2 | 738.4 | 686.1 | 617.5 | 740.2 | 766.2 | 707.6 | 574 | 686.4 | 615.2 | 359.2 | 359.9 | 371.6 | 351.2 | 342.4 | 365.4 | 370.3 | 348.6
1523.2 | 1247.2 | 468.8 | 187.52 | 219.2001 | 451.9 | 380.3 | 342.1 | 343.3 | 480.7 | 59.5 | 18.4 | 108.9 | 5 | 259 | 11.7 | 861.6 | 838.9 | 797.4 | 868.4 | 739.5 | 686.5 | 614.2 | 744.1 | 762 | 706.8 | 574 | 696 | 614.2 | 359.3 | 359.9 | 371.4 | 351.2 | 342.5 | 365.2 | 370.2 | 348.6
1524.2 | 1248.2 | 469.3 | 187.72 | 219.4339 | 452.8 | 380.8 | 342.1 | 342.5 | 484.5 | 59.6 | 18.4 | 108.9 | 4.9 | 263.2 | 11.8 | 862.8 | 833.7 | 789.8 | 868.4 | 739.5 | 687 | 609.6 | 737.3 | 753.5 | 705.2 | 573.9 | 698.7 | 613.4 | 359.5 | 359.9 | 371.5 | 351.4 | 342.6 | 364.9 | 370.3 | 348.5
1525.2 | 1249.2 | 468.7 | 187.48 | 219.1533 | 452 | 381 | 342.6 | 342.3 | 482.4 | 59.6 | 18.4 | 109 | 5.9 | 274 | 10.4 | 864.2 | 838.8 | 793.3 | 868.8 | 740.5 | 687.2 | 608.5 | 743.7 | 754.7 | 706.9 | 574.2 | 697.4 | 613.2 | 359.6 | 359.8 | 371.3 | 351.4 | 342.7 | 364.8 | 370 | 348.5
1526.2 | 1250.2 | 468.9 | 187.56 | 219.2468 | 448.6 | 381.6 | 343.1 | 342.4 | 480 | 59.6 | 18.4 | 109.2 | 5.7 | 257.1 | 9.2 | 864.4 | 830.3 | 794.6 | 868.4 | 740.7 | 687.2 | 605 | 737 | 749.2 | 704.9 | 574.2 | 698.5 | 613.7 | 359.7 | 359.7 | 371.1 | 351.4 | 342.7 | 364.6 | 369.5 | 348.5
1527.2 | 1251.2 | 469.5 | 187.8 | 219.5274 | 444.4 | 380.6 | 343.1 | 342.4 | 476.8 | 59.6 | 18.4 | 109.5 | 5.4 | 254 | 8.4 | 865 | 830.6 | 789.2 | 868.5 | 740.6 | 687.2 | 601 | 734.9 | 744 | 704.3 | 574.3 | 697.2 | 615.7 | 359.8 | 359.5 | 370.9 | 351.4 | 342.8 | 364.5 | 369.2 | 348.5
1528.2 | 1252.2 | 469.7 | 187.88 | 219.6209 | 440.4 | 379.6 | 342.3 | 342.3 | 476.4 | 59.6 | 18.4 | 109.8 | 5.6 | 243.4 | 7.6 | 866.1 | 835.1 | 788 | 868.5 | 741.1 | 687.2 | 600.4 | 740.2 | 743.7 | 704.7 | 574.4 | 698.7 | 617.8 | 359.8 | 359.6 | 370.7 | 351.5 | 342.9 | 364.4 | 369.1 | 348.5
1529.2 | 1253.2 | 469.3 | 187.72 | 219.4339 | 437.6 | 379 | 341.4 | 342.5 | 480.1 | 59.6 | 18.4 | 110.1 | 5.6 | 251.6 | 8.6 | 865.1 | 820.3 | 774.9 | 867.5 | 738.1 | 687.1 | 597 | 728.1 | 736.6 | 701.6 | 574.5 | 695.4 | 619.3 | 359.9 | 359.9 | 370.6 | 351.6 | 343 | 364.1 | 368.6 | 348.4
1530.2 | 1254.2 | 469.9 | 187.96 | 219.7144 | 436.8 | 378.4 | 341 | 342.2 | 481.2 | 59.5 | 18.4 | 110.4 | 5.7 | 253.2 | 9.2 | 863.4 | 808.2 | 763 | 865.4 | 735 | 686.7 | 591 | 715.7 | 726.8 | 697.9 | 574.6 | 692.3 | 620.8 | 360.3 | 360.2 | 370.9 | 351.8 | 343.1 | 363.9 | 368.2 | 348.4
1531.2 | 1255.2 | 470.1 | 188.04 | 219.8079 | 438.1 | 378.2 | 340.9 | 341.9 | 477.9 | 59.5 | 18.4 | 110.6 | 6.5 | 246 | 9.7 | 862.7 | 808.9 | 755.5 | 864 | 731.6 | 686.2 | 588.6 | 712.3 | 723.7 | 695.9 | 574.5 | 690.8 | 622.2 | 360.4 | 360.3 | 371.1 | 351.8 | 343.2 | 363.7 | 367.8 | 348.3
1532.2 | 1256.2 | 469.7 | 187.88 | 219.6209 | 438.3 | 377.5 | 341.2 | 341.6 | 473.8 | 59.4 | 18.4 | 110.7 | 5.4 | 248.8 | 10.5 | 862.3 | 810.8 | 762 | 862.4 | 731.1 | 685.8 | 588.5 | 715.4 | 726 | 695 | 574.4 | 693 | 622.9 | 360.4 | 360.3 | 371.3 | 351.8 | 343.3 | 363.5 | 367.6 | 348.2
1533.2 | 1257.2 | 469.2 | 187.68 | 219.3871 | 437 | 376.8 | 340.9 | 341.3 | 471.2 | 59.4 | 18.4 | 110.8 | 5.6 | 245.9 | 11.1 | 862.3 | 812.8 | 764.5 | 861.3 | 732.2 | 685.4 | 588.6 | 717.9 | 728.7 | 694.5 | 574.2 | 694.6 | 623.6 | 360.5 | 360.2 | 371.3 | 351.7 | 343.4 | 363.3 | 367.3 | 348.2
1534.2 | 1258.2 | 470.2 | 188.08 | 219.8547 | 436.3 | 376.6 | 340.4 | 341.1 | 468.6 | 59.4 | 18.4 | 110.9 | 5.7 | 253.1 | 10.9 | 861.6 | 817.6 | 758.2 | 859.9 | 731.4 | 685.1 | 589.3 | 716.6 | 727.8 | 693.5 | 574 | 690.2 | 624 | 360.5 | 360.1 | 371.5 | 351.7 | 343.4 | 363.2 | 366.8 | 348.2
1535.2 | 1259.2 | 469.8 | 187.92 | 219.6677 | 438.7 | 376.9 | 340.1 | 340.9 | 467.4 | 59.4 | 18.4 | 111 | 5 | 252.2 | 10.5 | 861.1 | 820.3 | 762.9 | 858.6 | 732.5 | 684.8 | 588.7 | 720.5 | 728.1 | 693.5 | 574.1 | 692.8 | 623.4 | 360.7 | 360.2 | 371.5 | 351.8 | 343.5 | 363.1 | 366.2 | 348.1
1536.2 | 1260.2 | 470.5 | 188.2 | 219.995 | 438.8 | 379.1 | 339.5 | 340.3 | 467.7 | 59.4 | 18.4 | 111 | 4.8 | 245.9 | 10.1 | 863.7 | 822.6 | 772.7 | 858.4 | 732.9 | 684.8 | 588 | 732.8 | 731.3 | 694.9 | 573.9 | 702.1 | 622.4 | 360.7 | 360.3 | 371.2 | 351.8 | 343.6 | 363 | 365.8 | 348
1537.2 | 1261.2 | 470.7 | 188.28 | 220.0885 | 438.4 | 380.2 | 339 | 340.1 | 467.2 | 59.4 | 18.4 | 111 | 4.8 | 227.9 | 10 | 865.4 | 828.1 | 775.8 | 860 | 734 | 685 | 590 | 743.4 | 737.9 | 696.9 | 573.8 | 706.1 | 622.3 | 360.6 | 360.3 | 370.9 | 351.7 | 343.7 | 363 | 365.8 | 348
1538.2 | 1262.2 | 470.5 | 188.2 | 219.995 | 435.1 | 380.3 | 338.9 | 340.2 | 466.1 | 59.5 | 18.4 | 111 | 6.9 | 209.1 | 8.9 | 867 | 833.6 | 774.8 | 862.1 | 734.6 | 685.2 | 591.9 | 750.4 | 743.5 | 698.7 | 573.8 | 705.1 | 623 | 360.7 | 360.2 | 370.6 | 351.7 | 343.7 | 362.9 | 366.1 | 348
1539.2 | 1263.2 | 469.7 | 187.88 | 219.6209 | 432 | 380.4 | 338.7 | 340.3 | 468 | 59.5 | 18.4 | 111 | 7.2 | 204.7 | 6.8 | 868.3 | 840.1 | 764.4 | 865.1 | 732.7 | 685.4 | 595.8 | 755.7 | 749.5 | 700.6 | 573.9 | 704.6 | 625 | 360.9 | 360.1 | 370.4 | 351.7 | 343.8 | 362.8 | 365.9 | 348
1540.2 | 1264.2 | 470.8 | 188.32 | 220.1352 | 431.3 | 380.3 | 338.3 | 340.1 | 470.4 | 59.4 | 18.4 | 111.1 | 7 | 235.1 | 6.2 | 868.7 | 843.7 | 767.3 | 867.4 | 732.5 | 685.2 | 596.8 | 751.2 | 752.8 | 700.9 | 573.9 | 700.6 | 627.6 | 361.1 | 360 | 370.3 | 351.7 | 343.8 | 362.8 | 365.6 | 348
1541.2 | 1265.2 | 470.7 | 188.28 | 220.0885 | 431.6 | 380.8 | 338.1 | 339.9 | 470.4 | 59.4 | 18.4 | 111.1 | 7.1 | 227.5 | 6.8 | 870.4 | 845 | 786.7 | 868.5 | 737.1 | 685.3 | 599.1 | 758.2 | 754.5 | 704.2 | 574.1 | 710.6 | 628.4 | 361.2 | 360.1 | 370.4 | 351.7 | 343.9 | 362.5 | 365.3 | 348
1542.2 | 1266.2 | 470.4 | 188.16 | 219.9482 | 432.2 | 381.1 | 338 | 339.7 | 474.1 | 59.4 | 18.4 | 111.2 | 6.5 | 261.3 | 5.1 | 872.2 | 844.1 | 797.1 | 870 | 739.8 | 686 | 602.2 | 765.6 | 756.2 | 706.2 | 574.5 | 717.5 | 627.7 | 361.3 | 360.3 | 370.3 | 351.8 | 343.9 | 362.4 | 365.4 | 347.9
1543.2 | 1267.2 | 470.4 | 188.16 | 219.9482 | 431.6 | 380.7 | 337.9 | 339.7 | 479.4 | 59.5 | 18.4 | 111.3 | 7.6 | 267.2 | 6.3 | 873.3 | 840.6 | 806.3 | 870.9 | 743.1 | 686.4 | 603.5 | 768.6 | 757.7 | 707.4 | 574.7 | 724.5 | 625.8 | 361.4 | 360.5 | 370.3 | 351.8 | 344 | 362.3 | 365.4 | 347.9
1544.2 | 1268.2 | 470.6 | 188.24 | 220.0417 | 432.2 | 381.4 | 337.6 | 339.8 | 482.9 | 59.6 | 18.4 | 111.4 | 9.7 | 243.1 | 8.1 | 874.3 | 834.1 | 800.2 | 871.4 | 743.1 | 686.3 | 601.3 | 774 | 754.5 | 708.4 | 575 | 729.5 | 623.8 | 361.5 | 360.6 | 370.4 | 352 | 344.1 | 362.3 | 365.2 | 347.8
1545.2 | 1269.2 | 470.1 | 188.04 | 219.8079 | 432.1 | 382.2 | 338 | 339.8 | 483.1 | 59.7 | 18.4 | 111.6 | 9.3 | 247.5 | 6.9 | 874.9 | 831.1 | 807.8 | 871.3 | 745.2 | 686 | 600 | 774.4 | 752.1 | 708.2 | 575.3 | 731.7 | 621.4 | 361.6 | 360.6 | 370.6 | 351.9 | 344.1 | 362.3 | 365.2 | 347.8
1546.2 | 1270.2 | 470 | 188 | 219.7612 | 430.5 | 383.1 | 338.3 | 340 | 485.2 | 59.8 | 18.4 | 111.6 | 7.9 | 261.5 | 7 | 876.8 | 838.5 | 813.7 | 872.1 | 748.2 | 685.7 | 603.8 | 777.2 | 756.6 | 710.6 | 575.6 | 732.5 | 619.5 | 361.7 | 360.5 | 370.6 | 351.9 | 344.2 | 362.3 | 365.2 | 347.8
1547.2 | 1271.2 | 470.7 | 188.28 | 220.0885 | 428.7 | 382.9 | 338.1 | 340.6 | 490.7 | 59.8 | 18.4 | 111.5 | 7.7 | 244.4 | 6.4 | 877 | 841.9 | 808.8 | 872.5 | 751.6 | 685.4 | 608.5 | 767.7 | 762.3 | 712.5 | 576 | 724.2 | 616.9 | 362 | 360.4 | 370.9 | 351.8 | 344.2 | 362.5 | 365.2 | 347.9
1548.2 | 1272.2 | 470.5 | 188.2 | 219.995 | 426.7 | 383.9 | 337.5 | 341.2 | 500.5 | 59.8 | 18.4 | 111.4 | 7 | 243.3 | 6.1 | 877.9 | 845.7 | 808.3 | 872.5 | 753.1 | 685.2 | 612.8 | 760.8 | 769 | 714.2 | 576.3 | 718 | 614.8 | 362.2 | 360.3 | 371.1 | 351.7 | 344.3 | 362.6 | 365.2 | 348
1549.2 | 1273.2 | 470.4 | 188.16 | 219.9482 | 426.3 | 387.7 | 337.6 | 341.7 | 505.8 | 59.8 | 18.4 | 111.3 | 7.1 | 255.3 | 7.7 | 879.2 | 849.3 | 807.7 | 873.3 | 755.5 | 685.1 | 614.2 | 757.8 | 772.6 | 715 | 576.5 | 714.5 | 612.8 | 362.4 | 360.2 | 371.3 | 351.6 | 344.3 | 362.7 | 365.2 | 348
1550.2 | 1274.2 | 470.1 | 188.04 | 219.8079 | 426.8 | 391.9 | 338.1 | 341.6 | 502.8 | 59.8 | 18.4 | 111.4 | 7.3 | 247.5 | 13.5 | 878.8 | 852.1 | 801 | 873.3 | 755.7 | 685 | 614.5 | 747.1 | 771.1 | 716.2 | 576.8 | 708.7 | 609.8 | 362.5 | 360.1 | 371.4 | 351.5 | 344.4 | 362.8 | 365 | 348.1
1551.2 | 1275.2 | 470.7 | 188.28 | 220.0885 | 428 | 396.8 | 338.8 | 341.8 | 498.4 | 59.9 | 18.4 | 111.5 | 7.7 | 234.4 | 14 | 880.5 | 852.2 | 803.8 | 874.2 | 756.2 | 685.2 | 613.6 | 749.3 | 772.2 | 716.3 | 577 | 709.7 | 607.9 | 362.6 | 360.1 | 371.4 | 351.6 | 344.5 | 362.8 | 365 | 348.1
1552.2 | 1276.2 | 470.6 | 188.24 | 220.0417 | 429.8 | 398.3 | 339.3 | 341.9 | 492.7 | 59.8 | 18.4 | 111.6 | 8.2 | 252.5 | 11.6 | 882.9 | 853.1 | 810.1 | 875.2 | 758.2 | 685.6 | 611.1 | 754.6 | 774.3 | 716.4 | 577.3 | 718 | 606.8 | 362.7 | 360.4 | 371.6 | 351.7 | 344.5 | 362.9 | 364.9 | 348
1553.2 | 1277.2 | 470.9 | 188.36 | 220.182 | 429.3 | 398 | 339.2 | 341.5 | 496.1 | 59.8 | 18.4 | 111.6 | 8.1 | 213.7 | 9.8 | 884.3 | 838.4 | 810.7 | 876.2 | 757.8 | 686.4 | 609.7 | 763.8 | 772.8 | 716.5 | 577.7 | 724.6 | 605.6 | 362.8 | 360.7 | 371.7 | 351.9 | 344.6 | 362.9 | 365.2 | 348
1554.2 | 1278.2 | 470.4 | 188.16 | 219.9482 | 428 | 398.7 | 340.3 | 341.1 | 509.1 | 59.8 | 18.4 | 111.7 | 8 | 240.8 | 11.2 | 884.7 | 817.7 | 799.9 | 876.7 | 755.7 | 687.1 | 605.7 | 766.5 | 766.6 | 715.2 | 578 | 728.4 | 605.9 | 363 | 361.1 | 371.9 | 352.3 | 344.7 | 363 | 365.3 | 347.9
1555.2 | 1279.2 | 470.7 | 188.28 | 220.0885 | 428 | 399.6 | 340.9 | 340.9 | 505.9 | 59.8 | 18.4 | 111.7 | 9.4 | 249.6 | 17.1 | 884.3 | 811.4 | 791.6 | 876.7 | 753.3 | 686.7 | 601.3 | 756.5 | 758.7 | 713.4 | 578.2 | 723.2 | 606 | 363 | 361.1 | 372 | 352.3 | 344.7 | 363 | 365.5 | 348
1556.2 | 1280.2 | 470.6 | 188.24 | 220.0417 | 427.5 | 399 | 341.9 | 340.8 | 502.8 | 59.8 | 18.4 | 111.7 | 7.9 | 250.3 | 19.9 | 884.5 | 816.4 | 779.5 | 877 | 750.4 | 686.5 | 599.4 | 752 | 757.3 | 712.8 | 578.3 | 717.6 | 606.8 | 363.2 | 361.1 | 371.9 | 352.3 | 344.8 | 363 | 365.5 | 347.9
1557.2 | 1281.2 | 470.8 | 188.32 | 220.1352 | 427.4 | 397.4 | 342.8 | 341.1 | 495 | 59.9 | 18.4 | 111.5 | 7.7 | 242.6 | 17.1 | 882.5 | 819.5 | 774.5 | 876.1 | 750 | 686.1 | 595.9 | 749.2 | 751.7 | 711.4 | 578.5 | 716.5 | 607.7 | 363.4 | 360.9 | 371.8 | 352.2 | 344.8 | 363 | 365.4 | 348
1558.2 | 1282.2 | 470.1 | 188.04 | 219.8079 | 427.4 | 396.8 | 342.9 | 341.7 | 488.3 | 59.9 | 18.4 | 111.4 | 7.6 | 239.4 | 13.3 | 881.9 | 820.1 | 765.3 | 875.3 | 748.1 | 685.6 | 593.8 | 743.6 | 747.9 | 711.4 | 578.5 | 715.4 | 609.7 | 363.6 | 360.8 | 371.8 | 352.1 | 344.9 | 363 | 365.8 | 348
1559.2 | 1283.2 | 470.7 | 188.28 | 220.0885 | 427.2 | 396.6 | 342.5 | 341.3 | 484.3 | 59.9 | 18.4 | 111.3 | 7.9 | 232.6 | 10 | 880.7 | 820.8 | 745.6 | 874.4 | 744.2 | 685.1 | 591.3 | 737.8 | 746.4 | 710.2 | 578.4 | 707.4 | 613.1 | 363.9 | 360.9 | 371.8 | 352 | 344.9 | 362.8 | 365.6 | 347.9
1560.2 | 1284.2 | 469.3 | 187.72 | 219.4339 | 425.6 | 396.6 | 342.4 | 340.7 | 482.2 | 59.9 | 18.4 | 111.3 | 8.5 | 253.3 | 9.5 | 880.3 | 819.8 | 738.9 | 873.9 | 741.5 | 684.9 | 589.9 | 746.5 | 747.5 | 709.7 | 578.3 | 705.4 | 617 | 364 | 361 | 371.8 | 352.2 | 345 | 362.7 | 365.4 | 347.9
1561.2 | 1285.2 | 470.1 | 188.04 | 219.8079 | 422.8 | 397.4 | 342.4 | 340.4 | 482.6 | 59.8 | 18.4 | 111.3 | 9.8 | 259.2 | 10.1 | 880.1 | 821.6 | 738.6 | 873.7 | 739.5 | 684.4 | 587.6 | 739.8 | 744.2 | 708.6 | 578.2 | 698.6 | 621.4 | 364 | 361 | 372 | 352.3 | 345 | 362.6 | 365 | 347.8
1562.2 | 1286.2 | 470.3 | 188.12 | 219.9014 | 420.1 | 397.3 | 342.5 | 339.9 | 478.2 | 59.8 | 18.4 | 111.2 | 10 | 255.8 | 13.1 | 879.6 | 830.9 | 744.9 | 873.9 | 739.2 | 684.1 | 588 | 746 | 748.7 | 709.5 | 577.9 | 697.4 | 624.7 | 364 | 360.8 | 371.8 | 352.1 | 345.1 | 362.6 | 364.8 | 347.7
1563.2 | 1287.2 | 469.6 | 187.84 | 219.5741 | 418.7 | 396.2 | 342.3 | 339.3 | 477.1 | 59.9 | 18.4 | 111.1 | 8.5 | 244.9 | 12.8 | 879.4 | 839.2 | 755.9 | 874.5 | 740.6 | 683.8 | 591.2 | 744.4 | 752.2 | 710.4 | 577.7 | 701.3 | 626.1 | 363.9 | 360.7 | 371.4 | 352 | 345.2 | 362.5 | 364.5 | 347.7
1564.2 | 1288.2 | 469.5 | 187.8 | 219.5274 | 420.1 | 395.4 | 341.8 | 338.8 | 475.4 | 60 | 18.4 | 110.9 | 7.8 | 220.5 | 12.1 | 879.2 | 832 | 770.8 | 874.9 | 742.6 | 683.4 | 590.7 | 742.4 | 748.7 | 709.9 | 577.5 | 710.8 | 626.8 | 364 | 360.6 | 371.2 | 352 | 345.3 | 362.6 | 364.4 | 347.7
1565.2 | 1289.2 | 469.9 | 187.96 | 219.7144 | 421.2 | 394.6 | 341.2 | 338.6 | 472.8 | 59.9 | 18.4 | 110.8 | 8.2 | 245.4 | 10.4 | 877.6 | 815.1 | 774.2 | 873.5 | 742.1 | 683.1 | 586.3 | 734.1 | 739.5 | 707.1 | 577.3 | 714.5 | 626.2 | 364.1 | 360.9 | 371.1 | 352.2 | 345.4 | 362.3 | 364.1 | 347.6
1566.2 | 1290.2 | 469.5 | 187.8 | 219.5274 | 421.1 | 395.6 | 341.1 | 338.9 | 472.9 | 59.9 | 18.4 | 110.9 | 7.4 | 248.2 | 13.8 | 875.1 | 814.5 | 755.2 | 871.7 | 741.1 | 682.6 | 582.7 | 727.7 | 734.3 | 705.7 | 577.2 | 708.5 | 624.6 | 364.2 | 361.2 | 371.4 | 352.4 | 345.4 | 362 | 363.7 | 347.5
1567.2 | 1291.2 | 469.3 | 187.72 | 219.4339 | 419.9 | 394.8 | 341.7 | 338.8 | 471 | 59.8 | 18.4 | 110.9 | 7.5 | 242.2 | 17.7 | 872.9 | 813 | 729.1 | 870.1 | 736.3 | 681.7 | 580.3 | 709.2 | 729.8 | 702.7 | 576.9 | 692.2 | 624.8 | 364.2 | 361.1 | 371.4 | 352.2 | 345.5 | 361.9 | 364 | 347.4
1568.2 | 1292.2 | 469 | 187.6 | 219.2936 | 419.4 | 392.9 | 341.8 | 338.5 | 466 | 59.8 | 18.4 | 111.1 | 7.8 | 244.3 | 17.7 | 870.1 | 801.8 | 717.6 | 868.2 | 733 | 680.6 | 576.6 | 691.9 | 722.1 | 699.2 | 576.4 | 680.5 | 627 | 364.3 | 360.9 | 371.3 | 352.2 | 345.5 | 361.6 | 363.8 | 347.4
1569.2 | 1293.2 | 469.7 | 187.88 | 219.6209 | 419.3 | 392.6 | 341.5 | 338.4 | 459.9 | 59.8 | 18.4 | 111.1 | 7.5 | 242 | 16.3 | 869.3 | 812.3 | 720.1 | 867.2 | 732.5 | 680.1 | 578.2 | 701.6 | 726.8 | 700.9 | 576.1 | 685.8 | 629.8 | 364.5 | 360.6 | 371.1 | 352.1 | 345.6 | 361.5 | 363.6 | 347.3
1570.2 | 1294.2 | 469.4 | 187.76 | 219.4806 | 418.3 | 392 | 340.8 | 337.9 | 459.3 | 59.8 | 18.4 | 111.2 | 7.1 | 258.8 | 13.4 | 868.1 | 807.4 | 729.5 | 865.8 | 732.1 | 679.7 | 576.5 | 703.9 | 724.2 | 699.1 | 575.7 | 688.3 | 631.3 | 364.5 | 360.4 | 370.7 | 352.1 | 345.7 | 361.4 | 363.2 | 347.3
1571.2 | 1295.2 | 470.6 | 188.24 | 220.0417 | 418.1 | 392.8 | 340 | 337.9 | 461 | 59.7 | 18.4 | 111.3 | 7.7 | 238.2 | 12 | 866.1 | 795.7 | 730 | 863.7 | 729.3 | 679.1 | 574.5 | 702.1 | 720.3 | 696.3 | 575.3 | 684.5 | 632 | 364.6 | 360.3 | 370.5 | 352 | 345.7 | 361.3 | 363 | 347.2
1572.2 | 1296.2 | 470.3 | 188.12 | 219.9014 | 417.6 | 393.1 | 339.8 | 337.8 | 466 | 59.5 | 18.4 | 111.4 | 8.3 | 247.3 | 13.1 | 864.2 | 800.5 | 726.5 | 862.6 | 727.1 | 678.3 | 573.2 | 696.1 | 719.9 | 694.7 | 574.8 | 677 | 632.2 | 364.7 | 360.2 | 370.3 | 352 | 345.8 | 361.2 | 362.9 | 347.2
1573.2 | 1297.2 | 470.8 | 188.32 | 220.1352 | 417 | 392.6 | 339.8 | 337.4 | 464.1 | 59.4 | 18.4 | 111.5 | 7.3 | 241.9 | 14.7 | 863 | 801.3 | 730.6 | 861.6 | 727.3 | 677.6 | 573.4 | 691.9 | 722.7 | 693.6 | 574.2 | 674.2 | 633 | 364.8 | 360.2 | 370.2 | 352 | 345.8 | 361.1 | 362.6 | 347.2
1574.2 | 1298.2 | 470 | 188 | 219.7612 | 417.2 | 392.1 | 339.6 | 337.4 | 463.1 | 59.4 | 18.4 | 111.5 | 7.1 | 251.1 | 15.1 | 862.6 | 808 | 730.6 | 861.2 | 725.7 | 677.3 | 576.4 | 697.7 | 729 | 694.7 | 573.5 | 668.9 | 633.7 | 365 | 360.3 | 370.1 | 352 | 345.9 | 361 | 362.4 | 347.1
1575.2 | 1299.2 | 469.1 | 187.64 | 219.3403 | 416.6 | 391.8 | 339.1 | 337.5 | 463.5 | 59.3 | 18.4 | 111.4 | 7.3 | 253.4 | 15.2 | 862.8 | 813.9 | 732.8 | 861.3 | 725 | 677 | 577.9 | 711.9 | 734.3 | 695.2 | 573 | 671.1 | 633.7 | 365 | 360.2 | 370 | 352 | 345.9 | 360.9 | 362.4 | 347.1
1576.2 | 1300.2 | 469 | 187.6 | 219.2936 | 415.2 | 392.1 | 338.9 | 337.4 | 464.1 | 59.3 | 18.4 | 111.5 | 7.6 | 244.4 | 13.4 | 862.8 | 821.3 | 745.1 | 861.6 | 725.7 | 676.5 | 578.1 | 710.1 | 735 | 695.4 | 572.6 | 673.3 | 634.8 | 365 | 360.4 | 369.9 | 352.1 | 345.9 | 360.8 | 362.5 | 347
1577.2 | 1301.2 | 470.1 | 188.04 | 219.8079 | 416.3 | 392.3 | 338.6 | 337.5 | 465.6 | 59.4 | 18.4 | 111.6 | 7.2 | 242.4 | 12.4 | 861.7 | 816.3 | 745.4 | 860.8 | 725 | 675.9 | 576.1 | 708.2 | 729.9 | 694.3 | 572.1 | 671.4 | 635 | 365 | 360.4 | 369.7 | 352.1 | 346 | 360.7 | 362.2 | 347
1578.2 | 1302.2 | 469.4 | 187.76 | 219.4806 | 416.7 | 392.4 | 338 | 337.5 | 463.3 | 59.4 | 18.4 | 111.7 | 6 | 245.9 | 13.2 | 861 | 819.2 | 737.3 | 860.8 | 722.9 | 675.4 | 577.2 | 711 | 735.9 | 694.4 | 571.5 | 665 | 636.5 | 365.2 | 360.3 | 369.8 | 352.1 | 346.1 | 360.5 | 362 | 346.9
1579.2 | 1303.2 | 469.8 | 187.92 | 219.6677 | 416.4 | 391.3 | 337.7 | 337.4 | 462.2 | 59.5 | 18.4 | 111.7 | 5.7 | 244.6 | 11.7 | 860.3 | 822.4 | 738.1 | 860.8 | 721.1 | 674.8 | 576.8 | 709 | 737.7 | 693.2 | 570.9 | 661.8 | 639.3 | 365.3 | 359.9 | 369.8 | 352 | 346.1 | 360.5 | 361.8 | 346.9
1580.2 | 1304.2 | 470 | 188 | 219.7612 | 415.9 | 390.9 | 337.2 | 337.2 | 461.2 | 59.6 | 18.4 | 111.7 | 6.1 | 242.5 | 12.4 | 860.1 | 819.1 | 751.1 | 860.7 | 721.9 | 674.5 | 576 | 709.9 | 735.7 | 692.1 | 570.3 | 666.8 | 640.4 | 365.4 | 360.1 | 369.9 | 352.1 | 346.2 | 360.6 | 361.6 | 346.9
1581.2 | 1305.2 | 470.2 | 188.08 | 219.8547 | 416.2 | 390.9 | 337.3 | 337.2 | 464 | 59.6 | 18.4 | 111.7 | 7.3 | 248.1 | 13.7 | 860.4 | 820 | 764.4 | 860.7 | 723.9 | 674.1 | 576.7 | 711.9 | 735.8 | 693.2 | 569.8 | 670.2 | 641.3 | 365.5 | 360.1 | 369.9 | 352.2 | 346.2 | 360.7 | 361.5 | 346.9
1582.2 | 1306.2 | 467.1 | 186.84 | 218.4052 | 414.9 | 390.2 | 337.6 | 337.2 | 462.1 | 59.7 | 18.4 | 111.6 | 8.1 | 264.6 | 13.3 | 859.4 | 818.2 | 758.1 | 861 | 723 | 673.5 | 575.7 | 710 | 735.3 | 692.5 | 569.3 | 664.2 | 644.1 | 365.5 | 360.1 | 369.7 | 352 | 346.2 | 360.7 | 361.5 | 347
1583.2 | 1307.2 | 468.9 | 187.56 | 219.2468 | 413.1 | 390.2 | 337.5 | 337.4 | 458.5 | 59.7 | 18.4 | 111.5 | 6.6 | 259.7 | 14.6 | 856.7 | 823.1 | 741.2 | 859.9 | 718.8 | 672.9 | 574.1 | 700 | 731.5 | 690.3 | 568.6 | 651.3 | 646.4 | 365.7 | 359.8 | 369.6 | 351.8 | 346.3 | 360.8 | 361.5 | 347
1584.2 | 1308.2 | 469 | 187.6 | 219.2936 | 413.1 | 389.9 | 337.3 | 337.7 | 458.7 | 59.7 | 18.4 | 111.4 | 6.8 | 247.2 | 17.8 | 855.5 | 829.8 | 734.5 | 859.1 | 717.7 | 672.4 | 574.7 | 702.5 | 734.4 | 690.2 | 568 | 650.6 | 649.4 | 365.8 | 359.5 | 369.2 | 351.7 | 346.3 | 360.7 | 361.4 | 347
1585.2 | 1309.2 | 468.9 | 187.56 | 219.2468 | 412.2 | 390.6 | 336.8 | 337.6 | 462.2 | 59.8 | 18.4 | 111.5 | 8 | 247.1 | 19.5 | 856.4 | 843 | 743 | 858.9 | 719.8 | 672.4 | 579.6 | 713.7 | 745.1 | 693.2 | 567.4 | 654.6 | 651.4 | 365.7 | 359 | 368.9 | 351.6 | 346.4 | 360.6 | 361.3 | 346.9
1586.2 | 1310.2 | 469.3 | 187.72 | 219.4339 | 411.8 | 388.8 | 335.8 | 337.3 | 466.1 | 59.8 | 18.4 | 111.5 | 10.5 | 267.6 | 19.1 | 857.6 | 849 | 741.5 | 859.5 | 720.4 | 672.2 | 582.9 | 718.9 | 749.7 | 694.8 | 566.8 | 654.4 | 651.3 | 365.6 | 358.8 | 368.6 | 351.4 | 346.4 | 360.5 | 361.4 | 346.9
1587.2 | 1311.2 | 468.8 | 187.52 | 219.2001 | 412.4 | 388.3 | 335.3 | 337.2 | 468.2 | 59.8 | 18.4 | 111.5 | 9.1 | 253.7 | 17.3 | 858.3 | 848.6 | 739.4 | 860.5 | 721 | 672.4 | 581.7 | 719.7 | 748.3 | 694.9 | 566.4 | 654.1 | 651.6 | 365.8 | 358.7 | 368.3 | 351.4 | 346.4 | 360.4 | 361.9 | 346.9
1588.2 | 1312.2 | 469.3 | 187.72 | 219.4339 | 411.4 | 389.3 | 335.2 | 337.4 | 469.3 | 59.8 | 18.4 | 111.4 | 9.7 | 248.4 | 17.2 | 860.9 | 849 | 751.6 | 861.5 | 723.3 | 672.3 | 582.7 | 727.4 | 750.1 | 696.2 | 566 | 662 | 652.3 | 365.8 | 358.9 | 368 | 351.5 | 346.4 | 360.3 | 361.6 | 346.9
1589.2 | 1313.2 | 469 | 187.6 | 219.2936 | 410.1 | 389.8 | 335.2 | 337.6 | 471.6 | 59.9 | 18.4 | 111.2 | 9.9 | 231 | 15.7 | 862.6 | 851.2 | 758.2 | 863.2 | 725.2 | 672.5 | 584.8 | 738.6 | 753.7 | 697.6 | 565.9 | 672.1 | 650.9 | 366 | 358.8 | 368.1 | 351.5 | 346.5 | 360.4 | 361.5 | 346.9
1590.2 | 1314.2 | 469.3 | 187.72 | 219.4339 | 410 | 391.2 | 335 | 337.2 | 473.9 | 59.9 | 18.4 | 111 | 9.5 | 262.8 | 14.7 | 862.4 | 847.2 | 762 | 864.1 | 726.9 | 672.3 | 586.3 | 732.5 | 755.9 | 698.5 | 565.7 | 669.8 | 648 | 366 | 358.5 | 368.1 | 351.5 | 346.5 | 360.5 | 361.4 | 346.9
1591.2 | 1315.2 | 468.3 | 187.32 | 218.9663 | 410.3 | 392.7 | 335.4 | 337.3 | 472.8 | 59.9 | 18.4 | 110.8 | 7.7 | 233.9 | 13.2 | 861 | 844.8 | 763 | 863.6 | 728.9 | 671.6 | 585.8 | 729 | 753.3 | 698.9 | 565.3 | 672.2 | 645.2 | 366 | 358.4 | 368.2 | 351.4 | 346.6 | 360.6 | 361.6 | 347
1592.2 | 1316.2 | 469.2 | 187.68 | 219.3871 | 409.5 | 393.7 | 336.1 | 337.9 | 469.9 | 60 | 18.4 | 110.7 | 7.4 | 239.8 | 13.9 | 860.8 | 844.2 | 768.1 | 862.8 | 729.9 | 671.3 | 583.6 | 726.6 | 745.7 | 698.7 | 565 | 675.1 | 642.2 | 366 | 358.6 | 368.5 | 351.5 | 346.7 | 360.5 | 361.6 | 347
1593.2 | 1317.2 | 469 | 187.6 | 219.2936 | 408.8 | 395.1 | 336.8 | 338 | 470.9 | 60.1 | 18.4 | 110.7 | 7.9 | 249.7 | 13.1 | 861.5 | 832.8 | 768.6 | 862.4 | 729.6 | 671 | 581.4 | 726.8 | 741.2 | 697.5 | 564.7 | 679.7 | 639.7 | 366.3 | 358.9 | 368.9 | 351.8 | 346.7 | 360.5 | 361.5 | 346.9
1594.2 | 1318.2 | 469.2 | 187.68 | 219.3871 | 409.2 | 397.9 | 337.6 | 337.9 | 477.2 | 60.2 | 18.4 | 110.7 | 10.1 | 239.9 | 16.3 | 864.1 | 825.5 | 780.3 | 863 | 731.2 | 670.9 | 579.6 | 727.4 | 737.2 | 697.9 | 564.5 | 683 | 637.9 | 366.5 | 358.9 | 369.2 | 352 | 346.8 | 360.5 | 361.7 | 346.8
1595.2 | 1319.2 | 468.6 | 187.44 | 219.1066 | 409.3 | 400.5 | 338.5 | 338.2 | 474 | 60.3 | 18.4 | 110.7 | 8.7 | 247.3 | 18 | 865 | 827.1 | 765.8 | 864 | 728.8 | 670.6 | 579.6 | 720.3 | 739.1 | 697.5 | 564.2 | 676.2 | 638.1 | 366.6 | 358.8 | 369.4 | 351.8 | 346.8 | 360.5 | 361.7 | 346.9
1596.2 | 1320.2 | 469 | 187.6 | 219.2936 | 407.3 | 399.4 | 339 | 338.7 | 469.3 | 60.3 | 18.3 | 110.6 | 8.1 | 244.7 | 16.4 | 864.3 | 824.8 | 750 | 864.2 | 728.2 | 670.1 | 577.8 | 708.1 | 733.7 | 695.9 | 563.7 | 668.6 | 639.6 | 366.6 | 358.8 | 369.4 | 351.6 | 346.9 | 360.4 | 361.6 | 346.9
1597.2 | 1321.2 | 469.2 | 187.68 | 219.3871 | 406.4 | 398 | 339 | 338.6 | 465.2 | 60.2 | 18.4 | 110.7 | 6.5 | 241.2 | 17 | 863.2 | 827.9 | 730.6 | 863.5 | 725.2 | 669.6 | 576.1 | 704.1 | 732.6 | 694.8 | 563.3 | 661.9 | 640.7 | 366.6 | 358.7 | 369.4 | 351.5 | 346.9 | 360.4 | 361.6 | 346.9
1598.2 | 1322.2 | 469.5 | 187.8 | 219.5274 | 405.8 | 396.5 | 338.4 | 338.5 | 465.9 | 60.1 | 18.4 | 110.7 | 8.2 | 240.7 | 16.8 | 861.2 | 831.6 | 721.6 | 862 | 723.1 | 669 | 578.3 | 696.6 | 735.1 | 694.2 | 562.7 | 653.7 | 641.3 | 366.6 | 358.4 | 369 | 351.3 | 346.9 | 360.5 | 361.5 | 346.9
1599.2 | 1323.2 | 469.3 | 187.72 | 219.4339 | 405.8 | 397.2 | 338 | 338.2 | 468 | 60.1 | 18.4 | 110.9 | 9.9 | 238.9 | 17.7 | 860.2 | 834.4 | 723.1 | 860.9 | 722.3 | 669.1 | 578.4 | 700.7 | 739.8 | 695.1 | 562.3 | 649.4 | 642 | 366.7 | 358.6 | 368.6 | 351.3 | 347 | 360.5 | 361.6 | 346.9
1600.2 | 1324.2 | 469.7 | 187.88 | 219.6209 | 405.5 | 398.7 | 337.9 | 338.4 | 465.8 | 60.1 | 18.3 | 111 | 7.6 | 252 | 17.5 | 858.7 | 832.6 | 723.9 | 859.5 | 720.6 | 668.9 | 576.7 | 698.8 | 736.2 | 692.9 | 561.9 | 646.1 | 643.2 | 366.8 | 358.7 | 368.5 | 351.4 | 347.1 | 360.6 | 361.5 | 346.9
1601.2 | 1325.2 | 470.1 | 188.04 | 219.8079 | 404.7 | 398.8 | 337.4 | 338.7 | 459.4 | 60.1 | 18.4 | 111.1 | 8 | 254 | 17.3 | 857.8 | 837.6 | 729 | 858.2 | 719.8 | 668.6 | 576.4 | 702.2 | 739 | 692.8 | 561.3 | 645.5 | 644.1 | 366.7 | 358.3 | 368.3 | 351.3 | 347.1 | 360.7 | 361.5 | 347
1602.2 | 1326.2 | 469.9 | 187.96 | 219.7144 | 404.4 | 399.3 | 337.1 | 338.2 | 459.7 | 60.1 | 18.4 | 111.2 | 8.1 | 255 | 16.9 | 855.9 | 837.8 | 721.8 | 855.9 | 717.7 | 668.6 | 578 | 698.7 | 740.2 | 693.4 | 560.9 | 640.5 | 644 | 366.6 | 357.7 | 368.1 | 351.1 | 347.2 | 361.1 | 361.7 | 347.1
1603.2 | 1327.2 | 469.5 | 187.8 | 219.5274 | 403.8 | 399.2 | 336.9 | 337.9 | 464.3 | 60.2 | 18.4 | 111.3 | 7.8 | 246.1 | 15.7 | 853.8 | 829.5 | 720.8 | 853.8 | 715.8 | 668.3 | 576.3 | 685.2 | 733.8 | 690.2 | 560.4 | 633.5 | 642.9 | 366.6 | 357.2 | 367.7 | 350.9 | 347.3 | 361.1 | 361.7 | 347.1
1604.2 | 1328.2 | 469.3 | 187.72 | 219.4339 | 402.2 | 398.9 | 336.4 | 338.1 | 463.7 | 60.3 | 18.4 | 111.5 | 6.4 | 254.1 | 15.1 | 851.2 | 826.3 | 709.9 | 851.4 | 713.8 | 667.8 | 573.2 | 679.2 | 727.3 | 688.4 | 559.8 | 627.6 | 641.8 | 366.5 | 356.9 | 367.5 | 350.8 | 347.3 | 361.1 | 361.7 | 347.1
1605.2 | 1329.2 | 469.7 | 187.88 | 219.6209 | 400.4 | 399.5 | 336.2 | 338.5 | 467.1 | 60.3 | 18.4 | 111.6 | 5.6 | 257 | 15.2 | 846.3 | 821.3 | 694.4 | 847 | 709 | 667.3 | 570.2 | 667.3 | 720.2 | 685.5 | 559.1 | 619.7 | 639.5 | 366.5 | 356.4 | 367.1 | 350.6 | 347.3 | 361.2 | 361.9 | 347.2
1606.2 | 1330.2 | 469 | 187.6 | 219.2936 | 398.9 | 399.5 | 336 | 338.9 | 468.4 | 60.4 | 18.4 | 111.7 | 6.3 | 251.4 | 14.8 | 843.2 | 816.4 | 693.7 | 843.8 | 707.8 | 666.7 | 569.3 | 663 | 716.6 | 684 | 558.4 | 614.6 | 636.9 | 366.6 | 356 | 366.8 | 350.5 | 347.4 | 361.3 | 362.1 | 347.3
1607.2 | 1331.2 | 469.4 | 187.76 | 219.4806 | 397.7 | 398.7 | 336.1 | 339.3 | 468.7 | 60.5 | 18.3 | 111.8 | 8.8 | 245.7 | 15 | 842.1 | 817.3 | 685.9 | 841.5 | 705.3 | 666.4 | 569.5 | 667.4 | 718.8 | 683.6 | 557.7 | 611 | 636.2 | 366.6 | 355.9 | 366.6 | 350.4 | 347.5 | 361.3 | 362.2 | 347.3
1608.2 | 1332.2 | 468.9 | 187.56 | 219.2468 | 396.9 | 398.1 | 335.6 | 339.4 | 466.7 | 60.5 | 18.3 | 111.8 | 9.2 | 251.1 | 14.2 | 838.5 | 796.7 | 674.1 | 837.3 | 700.2 | 665.9 | 565 | 651.1 | 709.5 | 679.4 | 557 | 604.6 | 635.5 | 366.6 | 355.7 | 366.4 | 350.3 | 347.5 | 361.4 | 362.3 | 347.4
1609.2 | 1333.2 | 469.7 | 187.88 | 219.6209 | 396.6 | 398.6 | 335.2 | 339.4 | 463.2 | 60.4 | 18.3 | 111.7 | 8.1 | 252.7 | 15.3 | 833.6 | 779.1 | 658 | 832.6 | 695.2 | 664.8 | 559.3 | 634.1 | 698.2 | 675.6 | 556.3 | 599.8 | 634.4 | 366.5 | 355.1 | 366.1 | 350.2 | 347.5 | 361.5 | 362.3 | 347.4
1610.2 | 1334.2 | 469.5 | 187.8 | 219.5274 | 396.5 | 401.7 | 335 | 339.4 | 461.4 | 60.2 | 18.3 | 111.7 | 5.7 | 248.4 | 14.8 | 829 | 778.4 | 651 | 827.9 | 692.4 | 664.1 | 553.9 | 626.7 | 689.4 | 672.6 | 555.5 | 594.9 | 633.3 | 366.5 | 354.6 | 365.6 | 350 | 347.6 | 362 | 362.6 | 347.5
1611.2 | 1335.2 | 469.8 | 187.92 | 219.6677 | 396.1 | 403.3 | 334.8 | 339.4 | 458.4 | 60.1 | 18.3 | 111.7 | 6.6 | 257 | 13.4 | 826.4 | 775.2 | 652.5 | 824.3 | 691.4 | 663.7 | 551.8 | 636.7 | 685.5 | 671.7 | 554.7 | 602.1 | 632.9 | 366.4 | 354.5 | 365.2 | 350.1 | 347.7 | 362.4 | 362.7 | 347.6
1612.2 | 1336.2 | 468.9 | 187.56 | 219.2468 | 396 | 401.8 | 334.5 | 339.1 | 456.1 | 60 | 18.3 | 111.8 | 7.4 | 227 | 14.4 | 823.5 | 770.6 | 661.6 | 821.1 | 689.6 | 662.9 | 549.9 | 633.3 | 680.1 | 668.7 | 553.9 | 599.1 | 632.1 | 366.5 | 354.4 | 364.9 | 350 | 347.7 | 362.5 | 362.7 | 347.6
1613.2 | 1337.2 | 471.5 | 188.6 | 220.4625 | 396.1 | 402.1 | 333.7 | 338.6 | 452.5 | 59.9 | 18.3 | 112 | 7.6 | 248.6 | 15 | 820.1 | 759.9 | 660.6 | 817.6 | 686.8 | 661.7 | 547.3 | 623.9 | 674.7 | 666.2 | 553 | 593.7 | 631.2 | 366.6 | 354.2 | 364.6 | 349.9 | 347.8 | 362.6 | 362.7 | 347.6
1614.2 | 1338.2 | 472 | 188.8 | 220.6963 | 395.2 | 404.7 | 332.8 | 338.2 | 454.4 | 59.9 | 18.3 | 112.2 | 8.2 | 262.4 | 15.9 | 815.7 | 746.2 | 655.6 | 813.8 | 683.3 | 660.3 | 544.4 | 612.8 | 668.8 | 663 | 552.1 | 588.1 | 631 | 366.5 | 353.7 | 364.3 | 349.8 | 347.9 | 362.6 | 362.7 | 347.6
1615.2 | 1339.2 | 472.5 | 189 | 220.9301 | 394.1 | 403.4 | 332.6 | 337.8 | 454.5 | 59.8 | 18.3 | 112.6 | 9.1 | 265.1 | 15.2 | 814.6 | 750.4 | 671.5 | 812.2 | 684.4 | 659 | 542.1 | 613.4 | 667.7 | 661.5 | 551.2 | 591.3 | 632.6 | 366.5 | 353.2 | 364.1 | 349.8 | 347.9 | 362.5 | 362.5 | 347.5
1616.2 | 1340.2 | 472.1 | 188.84 | 220.7431 | 394.8 | 402.9 | 332.6 | 337.4 | 454 | 59.7 | 18.3 | 112.8 | 8.9 | 258.4 | 14.2 | 815.2 | 768.2 | 688.2 | 812.3 | 686.3 | 657.9 | 545.3 | 636.6 | 679.9 | 664.8 | 550.6 | 602.9 | 635 | 366.5 | 352.9 | 363.7 | 349.8 | 348 | 362.1 | 361.9 | 347.4
1617.2 | 1341.2 | 471.1 | 188.44 | 220.2755 | 394.1 | 401 | 332.6 | 336.8 | 454.7 | 59.6 | 18.3 | 113.1 | 8.9 | 260.2 | 13.7 | 816.4 | 784.2 | 697.1 | 813.4 | 686.9 | 657.2 | 548.8 | 655.3 | 689.6 | 667 | 550 | 608.8 | 638.7 | 366.4 | 352.6 | 363.4 | 349.7 | 348 | 361.8 | 361.4 | 347.3
1618.2 | 1342.2 | 470.9 | 188.36 | 220.182 | 393.6 | 397.8 | 333.1 | 336.1 | 454.8 | 59.5 | 18.3 | 113.2 | 8.9 | 277.2 | 14.2 | 814.9 | 789.3 | 698.3 | 814.1 | 684 | 656.1 | 550.3 | 649 | 692.5 | 665.5 | 549.4 | 604.8 | 641.7 | 366.4 | 352.5 | 363.4 | 349.6 | 348.1 | 361.8 | 361.3 | 347.3
1619.2 | 1343.2 | 469.4 | 187.76 | 219.4806 | 391.6 | 395.6 | 333.2 | 335.9 | 455.7 | 59.6 | 18.3 | 113.2 | 7.5 | 255.5 | 11.8 | 812.2 | 772.4 | 698.2 | 812.7 | 682.3 | 654.9 | 546.2 | 637 | 681.2 | 661.4 | 548.7 | 600.9 | 643.7 | 366.3 | 352.4 | 363.2 | 349.5 | 348.2 | 361.6 | 361 | 347.2
1620.2 | 1344.2 | 469.9 | 187.96 | 219.7144 | 390.9 | 393.9 | 333.6 | 336.2 | 451.4 | 59.6 | 18.3 | 113.1 | 6.4 | 248.9 | 12.1 | 809.2 | 763.7 | 692 | 810.9 | 681 | 653.8 | 542.9 | 628.8 | 672.9 | 658.5 | 547.9 | 596.7 | 646.2 | 366.4 | 352.3 | 363.1 | 349.5 | 348.2 | 361.3 | 360.6 | 347.1
1621.2 | 1345.2 | 470.6 | 188.24 | 220.0417 | 390.5 | 393.5 | 334.3 | 335.9 | 449 | 59.7 | 18.3 | 112.9 | 7 | 245.7 | 11.5 | 805.1 | 760.2 | 678.1 | 807.9 | 676.1 | 652.6 | 541.4 | 620 | 669.9 | 656.2 | 547.1 | 588.3 | 648.2 | 366.4 | 352.1 | 362.8 | 349.4 | 348.2 | 361.1 | 360.2 | 347.1
1622.2 | 1346.2 | 471 | 188.4 | 220.2287 | 391.1 | 392.1 | 334.4 | 335.3 | 447.3 | 59.7 | 18.3 | 112.8 | 7.9 | 239.6 | 12.1 | 801 | 753.8 | 674.5 | 804.7 | 673.1 | 651.5 | 538 | 608.5 | 662.4 | 653 | 546.3 | 581 | 648.7 | 366.3 | 351.9 | 362.3 | 349.2 | 348.3 | 360.7 | 360 | 347
1623.2 | 1347.2 | 471 | 188.4 | 220.2287 | 391.6 | 390.7 | 334 | 334.7 | 444.4 | 59.8 | 18.3 | 112.6 | 9.4 | 256.4 | 13.7 | 797.5 | 754.3 | 668.4 | 801 | 671.2 | 650.7 | 538.1 | 610.7 | 664.5 | 651.5 | 545.5 | 578.3 | 649.5 | 366.2 | 352 | 361.9 | 349.1 | 348.3 | 360.4 | 359.8 | 347
1624.2 | 1348.2 | 469.8 | 187.92 | 219.6677 | 390.8 | 391.5 | 333.1 | 334.5 | 442.8 | 59.9 | 18.3 | 112.5 | 8.4 | 263.6 | 13.7 | 793.5 | 752 | 653.1 | 797.1 | 667.2 | 649.6 | 536.1 | 605.4 | 661.7 | 648.8 | 544.7 | 572.7 | 651.3 | 366.1 | 351.9 | 361.4 | 349 | 348.4 | 360.2 | 359.6 | 346.9
1625.2 | 1349.2 | 471.2 | 188.48 | 220.3223 | 389.1 | 391.4 | 332 | 334.4 | 441.8 | 59.9 | 18.3 | 112.6 | 9.1 | 261.5 | 12.8 | 791.3 | 759.9 | 649.1 | 794.1 | 664.8 | 648.7 | 535.9 | 612.1 | 664.9 | 647.6 | 543.8 | 572.2 | 655.4 | 366.1 | 351.4 | 360.9 | 348.9 | 348.4 | 360.1 | 359.5 | 346.8
1626.2 | 1350.2 | 468.7 | 187.48 | 219.1533 | 388 | 389.5 | 331.1 | 333.8 | 445.5 | 59.9 | 18.3 | 112.7 | 8.5 | 266 | 12.4 | 789.8 | 772.1 | 658.2 | 792.1 | 665.1 | 648.1 | 540.7 | 629.6 | 677.7 | 649.2 | 543.1 | 580.3 | 658.8 | 365.9 | 350.7 | 360.3 | 348.7 | 348.4 | 360.1 | 359.5 | 346.8
1627.2 | 1351.2 | 467 | 186.8 | 218.3584 | 387.7 | 388.4 | 330.1 | 333.6 | 450.7 | 59.9 | 18.3 | 112.7 | 7.2 | 242.8 | 11.9 | 790.6 | 780.8 | 674.3 | 792.4 | 666.5 | 647.1 | 543.8 | 642.6 | 686.4 | 650.7 | 542.4 | 588.6 | 662 | 365.8 | 350.2 | 359.8 | 348.7 | 348.5 | 360 | 359.6 | 346.7
1628.2 | 1352.2 | 466.8 | 186.72 | 218.2649 | 387.4 | 387 | 329.5 | 333.8 | 451.5 | 60 | 18.3 | 112.8 | 7.3 | 242.5 | 12.1 | 790.8 | 770.8 | 676.2 | 792.1 | 665.6 | 646.4 | 544.7 | 641.8 | 686.4 | 649.6 | 541.7 | 587.4 | 663.2 | 365.7 | 349.9 | 359.4 | 348.6 | 348.5 | 360 | 359.8 | 346.7
1629.2 | 1353.2 | 467.5 | 187 | 218.5922 | 387 | 385.1 | 329.3 | 334.1 | 449.6 | 60 | 18.3 | 112.7 | 7.5 | 243.9 | 13.3 | 787.1 | 755.4 | 663.9 | 790.1 | 662.2 | 645 | 540.7 | 627.7 | 675.3 | 645.8 | 540.8 | 579.8 | 663.4 | 365.7 | 349.5 | 359.2 | 348.4 | 348.6 | 359.9 | 359.8 | 346.7
1630.2 | 1354.2 | 468.2 | 187.28 | 218.9195 | 386.8 | 386.5 | 329.4 | 334.2 | 447.9 | 60 | 18.3 | 112.5 | 8.3 | 242.8 | 14.5 | 783.2 | 738.6 | 654.3 | 787.3 | 658.7 | 643.7 | 535.9 | 616.4 | 664.8 | 642.2 | 539.9 | 573.2 | 662.8 | 365.7 | 349.5 | 359.1 | 348.4 | 348.6 | 359.7 | 359.6 | 346.6
1631.2 | 1355.2 | 468.8 | 187.52 | 219.2001 | 386.1 | 385.5 | 329.3 | 333.7 | 447.6 | 60 | 18.3 | 112.6 | 8.4 | 247.4 | 12.6 | 779.2 | 732.7 | 640.8 | 783.7 | 655.7 | 642.4 | 531.7 | 605.8 | 654 | 639.1 | 538.9 | 568.3 | 661.3 | 365.8 | 349.6 | 359.3 | 348.5 | 348.7 | 359.3 | 359 | 346.5
1632.2 | 1356.2 | 469.3 | 187.72 | 219.4339 | 385.2 | 384.6 | 329.6 | 333.1 | 444.7 | 60 | 18.3 | 112.7 | 8.8 | 259.6 | 10.9 | 777 | 731.5 | 637.3 | 781.5 | 654.8 | 641.4 | 531 | 615 | 655.1 | 638.3 | 538.1 | 571 | 662.8 | 366 | 349.7 | 359.5 | 348.5 | 348.7 | 358.8 | 357.5 | 346.3
1633.2 | 1357.2 | 469.6 | 187.84 | 219.5741 | 384.8 | 384.3 | 330 | 332.4 | 443.9 | 60 | 18.3 | 112.7 | 8.4 | 260.3 | 12.4 | 774.8 | 723.2 | 632.1 | 779 | 653.3 | 640.5 | 529.6 | 610 | 651.5 | 635.8 | 537.2 | 571 | 665 | 366 | 349.8 | 359.5 | 348.4 | 348.8 | 358.3 | 356.6 | 346.2
1634.2 | 1358.2 | 468.9 | 187.56 | 219.2468 | 385.2 | 382.9 | 330.3 | 332 | 442.8 | 60 | 18.3 | 112.9 | 7.8 | 249.3 | 14.7 | 772.9 | 715.8 | 627.9 | 777.2 | 651.4 | 639.7 | 527.1 | 616.2 | 646.1 | 634 | 536.3 | 574.8 | 669.6 | 366.1 | 349.9 | 359.5 | 348.4 | 348.8 | 357.7 | 355.8 | 346
1635.2 | 1359.2 | 468.5 | 187.4 | 219.0598 | 385.3 | 383.6 | 330.7 | 331.8 | 442.9 | 59.9 | 18.3 | 113.1 | 7.3 | 259.4 | 14.8 | 772.1 | 713.1 | 637.6 | 776.1 | 651.1 | 639.2 | 528 | 630.9 | 649 | 634.2 | 535.6 | 581.9 | 675.2 | 366.2 | 349.9 | 359.4 | 348.4 | 348.8 | 357.2 | 355.6 | 345.9
1636.2 | 1360.2 | 468.9 | 187.56 | 219.2468 | 385.3 | 383.6 | 330.7 | 331.6 | 446.3 | 59.9 | 18.3 | 113.1 | 7.5 | 248.8 | 15.9 | 770.9 | 713.3 | 638.4 | 775.2 | 648.7 | 638.9 | 528.8 | 638.6 | 650.7 | 633.9 | 534.9 | 584.9 | 678.6 | 366.3 | 350 | 359.7 | 348.5 | 348.9 | 356.8 | 355.6 | 345.7
1637.2 | 1361.2 | 468.4 | 187.36 | 219.013 | 385.8 | 383.9 | 330.8 | 331.7 | 452.1 | 59.9 | 18.3 | 113.1 | 7.9 | 246.2 | 15.8 | 770.7 | 725.4 | 660.9 | 775.2 | 651.8 | 638.6 | 531.2 | 652.4 | 656.8 | 634.4 | 534.3 | 595.1 | 679.7 | 366.4 | 350.3 | 360 | 348.6 | 348.9 | 356.6 | 355.3 | 345.6
1638.2 | 1362.2 | 468.8 | 187.52 | 219.2001 | 386.1 | 385.1 | 331.1 | 331.5 | 453.3 | 59.9 | 18.3 | 113 | 8.6 | 241.1 | 13.7 | 771.6 | 746.9 | 669.9 | 776.7 | 653.3 | 638.1 | 537.6 | 667.9 | 671.2 | 638.1 | 533.9 | 602.1 | 680 | 366.5 | 350.7 | 360.4 | 348.6 | 348.9 | 356.3 | 355.1 | 345.5
1639.2 | 1363.2 | 469.2 | 187.68 | 219.3871 | 385.3 | 385.6 | 331.3 | 331.3 | 455.2 | 59.9 | 18.3 | 113 | 9.4 | 247.7 | 12.2 | 774.1 | 752 | 689 | 779 | 656.6 | 637.7 | 542.6 | 672.6 | 683.7 | 640.1 | 533.4 | 610 | 680.9 | 366.5 | 351.1 | 360.8 | 348.6 | 348.9 | 356.1 | 355 | 345.5
1640.2 | 1364.2 | 468.4 | 187.36 | 219.013 | 385.4 | 387.3 | 331.6 | 331.3 | 456.5 | 59.9 | 18.3 | 113 | 9.4 | 251.1 | 12.2 | 774.6 | 739.1 | 691.4 | 780.3 | 656.3 | 637.2 | 543.8 | 675.8 | 682.5 | 640.1 | 533.1 | 617.9 | 680.1 | 366.7 | 351.3 | 361 | 348.7 | 348.9 | 355.9 | 354.9 | 345.4
1641.2 | 1365.2 | 468.3 | 187.32 | 218.9663 | 385.1 | 389.4 | 332 | 331.6 | 455.3 | 59.9 | 18.3 | 112.9 | 8 | 249.5 | 15.1 | 775.3 | 737.3 | 701.3 | 781.8 | 657.7 | 636.4 | 542.4 | 676.3 | 676.3 | 638.8 | 532.6 | 619.7 | 677.8 | 366.8 | 351.8 | 361.4 | 348.7 | 348.9 | 355.7 | 355.1 | 345.3
1642.2 | 1366.2 | 468.6 | 187.44 | 219.1066 | 383.9 | 390.1 | 332.8 | 331.8 | 454.9 | 59.9 | 18.3 | 112.8 | 7.3 | 253.4 | 16.3 | 775.5 | 746.1 | 694.5 | 783.2 | 656.4 | 635.5 | 543.5 | 667.7 | 678.4 | 639.5 | 532.1 | 614.6 | 676.8 | 366.8 | 352.3 | 361.5 | 348.6 | 348.9 | 355.7 | 355.4 | 345.2
1643.2 | 1367.2 | 469.3 | 187.72 | 219.4339 | 383.4 | 389.3 | 333.2 | 331.9 | 453.6 | 59.9 | 18.3 | 112.6 | 7.4 | 259.3 | 14.6 | 773.8 | 750.2 | 683.8 | 783.6 | 653.2 | 634.4 | 541.1 | 654.1 | 675.1 | 637 | 531.3 | 602.9 | 675.9 | 366.8 | 352.1 | 361.4 | 348.4 | 349 | 355.5 | 355.4 | 345.2
1644.2 | 1368.2 | 470.2 | 188.08 | 219.8547 | 383.4 | 388.6 | 333.1 | 332 | 450.8 | 60 | 18.3 | 112.3 | 6.2 | 238.3 | 15.2 | 772.8 | 759.3 | 678.6 | 784.4 | 652.1 | 633.5 | 540.3 | 652.9 | 673.4 | 636.2 | 530.6 | 596.2 | 674.7 | 366.7 | 351.8 | 361 | 348.2 | 349 | 355.5 | 356 | 345.2
1645.2 | 1369.2 | 470.2 | 188.08 | 219.8547 | 382.9 | 389.4 | 332.6 | 332.2 | 449.3 | 60 | 18.3 | 112.1 | 6.6 | 235.8 | 15.9 | 772.8 | 769.8 | 677.4 | 785.7 | 651.8 | 633.3 | 542.5 | 658.2 | 679.3 | 636 | 529.9 | 593.4 | 673.8 | 366.7 | 351.5 | 360.7 | 348.1 | 349 | 355.4 | 356.1 | 345.3
1646.2 | 1370.2 | 470.5 | 188.2 | 219.995 | 381.8 | 389.7 | 332.2 | 332.5 | 449.6 | 60 | 18.3 | 112 | 6.8 | 245.2 | 15.8 | 774.7 | 778.6 | 675.5 | 788 | 653.1 | 633.4 | 546.5 | 675.1 | 689.4 | 639.2 | 529.5 | 594.1 | 674.1 | 366.6 | 351.2 | 360.3 | 347.9 | 349 | 355.6 | 356.3 | 345.3
1647.2 | 1371.2 | 469.9 | 187.96 | 219.7144 | 381.1 | 389.4 | 332.5 | 332.3 | 450.4 | 60 | 18.3 | 111.9 | 6.8 | 258.4 | 14.4 | 775.2 | 783 | 675.2 | 789.4 | 653.4 | 633 | 549.2 | 673.4 | 694.5 | 639.5 | 529 | 592.1 | 674.7 | 366.6 | 351.1 | 360.1 | 347.8 | 349 | 355.6 | 356.4 | 345.3
1648.2 | 1372.2 | 470.2 | 188.08 | 219.8547 | 380.7 | 388.7 | 332.7 | 332.1 | 450.9 | 60.1 | 18.3 | 111.7 | 5.7 | 249.2 | 12 | 774.7 | 774.9 | 674.9 | 790.2 | 650.9 | 632.3 | 547.1 | 665 | 689.5 | 637.6 | 528.4 | 586.2 | 676.2 | 366.5 | 351.6 | 359.9 | 347.7 | 349 | 355.6 | 356.5 | 345.3
1649.2 | 1373.2 | 468.5 | 187.4 | 219.0598 | 380 | 389.9 | 332.7 | 332.1 | 449.7 | 60.1 | 18.3 | 111.5 | 6.9 | 248.2 | 12.1 | 772.1 | 761.3 | 662 | 789.1 | 647.1 | 631.5 | 543.3 | 646.8 | 678.6 | 634.5 | 527.7 | 577.2 | 677.2 | 366.5 | 351.2 | 359.8 | 347.6 | 349 | 355.5 | 356.3 | 345.2
1650.2 | 1374.2 | 469.3 | 187.72 | 219.4339 | 379.3 | 390.6 | 332.4 | 332.4 | 448 | 60.2 | 18.3 | 111.4 | 8 | 258.1 | 15.4 | 769.6 | 754.4 | 647.6 | 787.9 | 644.7 | 630.7 | 538.5 | 637.5 | 669 | 631.7 | 526.9 | 571.1 | 677.5 | 366.5 | 351 | 359.7 | 347.5 | 349 | 355.3 | 356.1 | 345.1
1651.2 | 1375.2 | 469.9 | 187.96 | 219.7144 | 378.9 | 391.3 | 332 | 332.4 | 445.7 | 60.2 | 18.3 | 111.4 | 9.3 | 263 | 17 | 768.7 | 761.8 | 647 | 786.9 | 643 | 629.9 | 537.7 | 636.1 | 668.9 | 631.2 | 526.2 | 567.6 | 678.5 | 366.4 | 350.7 | 359.5 | 347.4 | 349.1 | 355.2 | 355.9 | 345.1
1652.2 | 1376.2 | 468.6 | 187.44 | 219.1066 | 378.9 | 390.6 | 331.4 | 331.9 | 446.3 | 60.2 | 18.3 | 111.4 | 9.3 | 256 | 17.3 | 767.8 | 766.5 | 650.9 | 786.1 | 642.7 | 629.1 | 538 | 630.8 | 668.6 | 630.1 | 525.4 | 566 | 679.3 | 366.4 | 350.7 | 359.2 | 347.2 | 349.1 | 355.3 | 355.8 | 345.1
1653.2 | 1377.2 | 470.2 | 188.08 | 219.8547 | 378.7 | 391.2 | 330.5 | 331.5 | 450.2 | 60.3 | 18.3 | 111.3 | 9 | 254.4 | 15.2 | 767.4 | 771 | 650.6 | 785.6 | 643.2 | 628.5 | 539.3 | 625.5 | 669.8 | 630.1 | 524.8 | 562.5 | 678 | 366.5 | 350.6 | 359.1 | 347.2 | 349.1 | 355.2 | 355.7 | 345.2
1654.2 | 1378.2 | 469.6 | 187.84 | 219.5741 | 379.8 | 391.9 | 329.5 | 331.6 | 450.1 | 60.3 | 18.3 | 111.2 | 8.5 | 255.5 | 13.9 | 767.9 | 773 | 652.8 | 785.9 | 642.7 | 627.9 | 539.1 | 625.7 | 669.7 | 629.5 | 524.1 | 562.8 | 676.4 | 366.5 | 350.1 | 358.8 | 347 | 349.2 | 355.1 | 355.8 | 345.1
1655.2 | 1379.2 | 468.5 | 187.4 | 219.0598 | 380.4 | 390.8 | 328.7 | 331.9 | 449.6 | 60.2 | 18.3 | 111.3 | 7.5 | 245.1 | 14.5 | 767.5 | 772.1 | 655.9 | 785.8 | 643.1 | 627.4 | 538.7 | 627.6 | 671.3 | 629.8 | 523.4 | 560.1 | 675.3 | 366.4 | 349.9 | 358.6 | 346.9 | 349.2 | 355.2 | 355.8 | 345.1
1656.2 | 1380.2 | 469.3 | 187.72 | 219.4339 | 381 | 389.2 | 328.3 | 332.5 | 449.8 | 60.2 | 18.3 | 111.3 | 7.3 | 251.3 | 14.5 | 764.3 | 762.4 | 638.6 | 783.4 | 638.9 | 626.6 | 536.1 | 614.3 | 664.3 | 627.1 | 522.6 | 552.6 | 671.4 | 366.3 | 349.7 | 358.5 | 346.8 | 349.3 | 355.3 | 356.1 | 345.3
1657.2 | 1381.2 | 470.3 | 188.12 | 219.9014 | 381.9 | 387.3 | 328.3 | 333.1 | 449.4 | 60.3 | 18.3 | 111.4 | 7 | 250.6 | 15 | 761.7 | 759.3 | 634.8 | 781.5 | 636.6 | 625.8 | 535.1 | 608.9 | 661.3 | 626.3 | 521.9 | 548.4 | 667.3 | 366.3 | 349.5 | 358.7 | 346.6 | 349.3 | 355.3 | 356.4 | 345.3
1658.2 | 1382.2 | 470.9 | 188.36 | 220.182 | 382.2 | 389.2 | 328.5 | 333.8 | 450.2 | 60.4 | 18.3 | 111.5 | 6.6 | 244.3 | 16.9 | 759.1 | 754 | 621.8 | 778.4 | 633.2 | 625.2 | 534.2 | 602.4 | 658.3 | 624 | 521.2 | 544.6 | 664.3 | 366.3 | 349.6 | 359.1 | 346.4 | 349.3 | 355.9 | 356.8 | 345.4
1659.2 | 1383.2 | 470.5 | 188.2 | 219.995 | 383.1 | 390 | 329.3 | 334.3 | 451.2 | 60.4 | 18.3 | 111.5 | 6.3 | 236.5 | 17.9 | 755.7 | 744.9 | 617.1 | 775 | 630.7 | 624.5 | 531.2 | 594.6 | 650.9 | 621.5 | 520.4 | 540.7 | 661 | 366.3 | 349.5 | 359.3 | 346.3 | 349.3 | 356.3 | 357.2 | 345.5
1660.2 | 1384.2 | 468.5 | 187.4 | 219.0598 | 383 | 390.9 | 330.1 | 334.6 | 452.8 | 60.4 | 18.3 | 111.5 | 5.8 | 239.5 | 17.4 | 754.1 | 753.5 | 620.8 | 773.2 | 632.1 | 623.9 | 533.4 | 603.9 | 654.9 | 622.8 | 519.7 | 542.6 | 657.5 | 366.3 | 349.4 | 359.3 | 346.1 | 349.3 | 356.7 | 357.4 | 345.6
1661.2 | 1385.2 | 468.7 | 187.48 | 219.1533 | 383.7 | 392 | 330.2 | 334.3 | 458.9 | 60.5 | 18.3 | 111.6 | 6 | 247.1 | 16.9 | 754.1 | 765.1 | 636 | 771.6 | 636.5 | 624 | 544.8 | 619.2 | 671.8 | 628.2 | 519.2 | 543.5 | 653.4 | 366.3 | 349.1 | 359.2 | 346 | 349.4 | 357.1 | 357.8 | 345.6
1662.2 | 1386.2 | 468.5 | 187.4 | 219.0598 | 383.2 | 392.1 | 330.2 | 334.5 | 465 | 60.5 | 18.3 | 111.8 | 6.3 | 247 | 15.5 | 755 | 774.7 | 658.7 | 771.2 | 640.9 | 624.1 | 554 | 636.2 | 684 | 633.1 | 518.8 | 553.6 | 649.4 | 366.3 | 349 | 359.2 | 346 | 349.4 | 357.2 | 358.1 | 345.6
1663.2 | 1387.2 | 468.7 | 187.48 | 219.1533 | 382.4 | 392.4 | 330.5 | 334.9 | 466.2 | 60.5 | 18.3 | 111.9 | 7.1 | 247.7 | 15.5 | 755.3 | 780.4 | 670.1 | 770.7 | 641.9 | 624.3 | 559.3 | 641.1 | 690.6 | 634.3 | 518.3 | 555.8 | 645.4 | 366.3 | 348.8 | 359.3 | 345.9 | 349.4 | 357.4 | 358.2 | 345.6
1664.2 | 1388.2 | 469.3 | 187.72 | 219.4339 | 381.7 | 390.7 | 331.1 | 335.3 | 469.7 | 60.6 | 18.3 | 112 | 7 | 259.1 | 15.3 | 757.6 | 782.1 | 697.2 | 771.7 | 647.2 | 624.7 | 561.3 | 663.5 | 694.8 | 637 | 518 | 577.5 | 641.7 | 366.3 | 348.7 | 359.5 | 345.9 | 349.6 | 357.4 | 358.3 | 345.5
1665.2 | 1389.2 | 468 | 187.2 | 218.826 | 380.5 | 391.2 | 331.6 | 335.1 | 472.9 | 60.7 | 18.3 | 112 | 8 | 252 | 14.8 | 757.8 | 772 | 708.4 | 772.2 | 648.5 | 625.2 | 558.7 | 668.7 | 686.9 | 635.7 | 517.8 | 592.2 | 638.7 | 366.4 | 349 | 359.9 | 346.2 | 349.6 | 357.2 | 358.3 | 345.4
1666.2 | 1390.2 | 469.1 | 187.64 | 219.3403 | 379.5 | 390 | 332.5 | 334.8 | 476 | 60.7 | 18.3 | 112.1 | 9.4 | 265 | 14.4 | 759.3 | 764.4 | 720 | 773.4 | 650.5 | 625.1 | 556.1 | 675.5 | 684.2 | 636.5 | 517.6 | 602.2 | 636.5 | 366.4 | 349.3 | 360.4 | 346.3 | 349.7 | 357 | 358.2 | 345.3
1667.2 | 1391.2 | 469.2 | 187.68 | 219.3871 | 379 | 391 | 333.3 | 334.7 | 474.5 | 60.7 | 18.3 | 112.2 | 8.3 | 256.4 | 12.5 | 761.8 | 761.7 | 734.7 | 774.7 | 654.6 | 624.7 | 553.3 | 682.1 | 682.7 | 636.1 | 517.4 | 611.6 | 635.3 | 366.6 | 349.7 | 360.8 | 346.5 | 349.7 | 356.9 | 358.1 | 345.2
1668.2 | 1392.2 | 468.8 | 187.52 | 219.2001 | 378.5 | 391.8 | 334 | 335 | 473.9 | 60.8 | 18.3 | 112.1 | 7.9 | 252.2 | 10.4 | 766.3 | 766.3 | 740.9 | 777.4 | 656.5 | 624.9 | 557 | 697.7 | 688.3 | 639.8 | 517.3 | 624.4 | 633.6 | 366.7 | 350.6 | 361.1 | 346.7 | 349.7 | 356.7 | 358.2 | 345.1
1669.2 | 1393.2 | 469.2 | 187.68 | 219.3871 | 378 | 391.5 | 334.8 | 335 | 476 | 60.8 | 18.3 | 112.1 | 8.3 | 253.8 | 9.7 | 769.5 | 772.5 | 737.4 | 781.2 | 657.8 | 624.9 | 558.3 | 706 | 694.9 | 641.8 | 517.2 | 629.6 | 632.8 | 366.7 | 351 | 361.3 | 346.8 | 349.8 | 356.6 | 358.1 | 345
1670.2 | 1394.2 | 468.9 | 187.56 | 219.2468 | 377.8 | 391 | 334.9 | 335 | 473 | 60.8 | 18.3 | 112.1 | 7.8 | 262.9 | 11.4 | 771.9 | 778.9 | 738.5 | 784.6 | 659.2 | 625.6 | 558.3 | 702.7 | 696.3 | 642.7 | 517 | 629.8 | 632.6 | 366.8 | 351.2 | 361.5 | 346.8 | 349.9 | 356.4 | 358 | 344.9
1671.2 | 1395.2 | 468.7 | 187.48 | 219.1533 | 377.2 | 390.4 | 334.9 | 335.3 | 471.9 | 60.8 | 18.3 | 112.1 | 6.6 | 239.3 | 12.1 | 775.4 | 785.9 | 751.3 | 788.2 | 664.4 | 626.4 | 563.5 | 711.6 | 705.2 | 645.8 | 516.9 | 639.5 | 632.2 | 366.8 | 351.2 | 361.6 | 346.7 | 349.9 | 356.3 | 357.8 | 344.9
1672.2 | 1396.2 | 468.2 | 187.28 | 218.9195 | 376.9 | 390.9 | 335.2 | 335.3 | 474.2 | 60.8 | 18.3 | 112.1 | 7.3 | 259 | 10.3 | 779.2 | 784.2 | 756.7 | 792.2 | 667 | 627.2 | 566.8 | 717.7 | 710.7 | 648.7 | 516.9 | 647.9 | 631.1 | 366.8 | 351.5 | 361.7 | 346.8 | 350 | 356.1 | 357.7 | 344.7
1673.2 | 1397.2 | 469 | 187.6 | 219.2936 | 376.4 | 391.3 | 335.4 | 335 | 481.1 | 60.8 | 18.3 | 112.1 | 6.8 | 235.7 | 11.4 | 782 | 773.2 | 762.9 | 795.1 | 668.9 | 628.8 | 565.8 | 725 | 708.4 | 650.1 | 517.1 | 659.7 | 628.7 | 367 | 352.2 | 362.3 | 347 | 350.1 | 355.9 | 357.6 | 344.6
1674.2 | 1398.2 | 469.4 | 187.76 | 219.4806 | 376 | 392.4 | 335.9 | 335.1 | 487.9 | 60.7 | 18.3 | 111.9 | 6.1 | 246.7 | 11.2 | 784.4 | 769 | 765.1 | 797.2 | 670.6 | 629.7 | 564.2 | 726.7 | 703 | 652.1 | 517.5 | 669.4 | 625.1 | 367.1 | 352.9 | 362.7 | 347.1 | 350.1 | 355.8 | 357.7 | 344.5
1675.2 | 1399.2 | 469.3 | 187.72 | 219.4339 | 375.7 | 393 | 337.1 | 335.5 | 499.4 | 60.7 | 18.3 | 111.6 | 6.5 | 254.9 | 11.9 | 787.9 | 769.9 | 767.6 | 799.5 | 674.3 | 630.6 | 565.1 | 733.4 | 701.3 | 654.1 | 517.9 | 677.5 | 621.5 | 367.2 | 353.5 | 363.3 | 347.3 | 350.2 | 355.6 | 357.9 | 344.5
1676.2 | 1400.2 | 468.7 | 187.48 | 219.1533 | 376 | 393.6 | 337.9 | 336.1 | 506.7 | 60.7 | 18.3 | 111.4 | 7.1 | 252 | 12 | 792.1 | 772.4 | 770.4 | 802.9 | 676.2 | 631.6 | 566.7 | 739.1 | 704.2 | 656 | 518.2 | 684.1 | 618.5 | 367.4 | 354.1 | 363.8 | 347.5 | 350.2 | 355.4 | 358 | 344.3
1677.2 | 1401.2 | 468.7 | 187.48 | 219.1533 | 376.1 | 394 | 338.4 | 336.9 | 513.2 | 60.8 | 18.3 | 111.4 | 6.7 | 261.3 | 12.6 | 795.7 | 776.8 | 777.1 | 806.7 | 680.9 | 632.5 | 570.3 | 743.2 | 708.6 | 659.7 | 518.6 | 691.7 | 615.4 | 367.7 | 354.5 | 364.3 | 347.6 | 350.3 | 355.4 | 358.2 | 344.3
1678.2 | 1402.2 | 469.6 | 187.84 | 219.5741 | 376.5 | 395.1 | 338.8 | 337.8 | 510.4 | 60.9 | 18.3 | 111.4 | 7.3 | 251.9 | 14.6 | 799.5 | 785.7 | 777.5 | 811 | 684.2 | 633.6 | 576.5 | 749 | 719.4 | 664.1 | 519.1 | 693.9 | 612.5 | 367.8 | 354.7 | 364.6 | 347.5 | 350.3 | 355.4 | 358.4 | 344.2
1679.2 | 1403.2 | 469.4 | 187.76 | 219.4806 | 376.3 | 394.9 | 339.1 | 338.4 | 509.4 | 60.9 | 18.3 | 111.2 | 8.7 | 257.8 | 14.1 | 804.6 | 794.7 | 783.1 | 815.2 | 687.4 | 634.9 | 582.6 | 755.4 | 726.7 | 667.5 | 519.5 | 699.7 | 610.1 | 367.9 | 354.8 | 365.1 | 347.4 | 350.4 | 355.3 | 358.7 | 344.2
1680.2 | 1404.2 | 469.3 | 187.72 | 219.4339 | 375.5 | 396 | 339 | 338.5 | 513.5 | 60.8 | 18.3 | 111.1 | 8.6 | 253.3 | 12.7 | 806.8 | 789.4 | 788.1 | 818 | 690.9 | 635.4 | 581.2 | 751.5 | 726.2 | 667.2 | 520.2 | 705.9 | 606.7 | 368.1 | 355 | 365.4 | 347.5 | 350.4 | 355.3 | 358.9 | 344.1
1681.2 | 1405.2 | 468.8 | 187.52 | 219.2001 | 375.1 | 396.4 | 339.3 | 338.6 | 515.6 | 60.8 | 18.3 | 111 | 8 | 256 | 13.4 | 808.1 | 782.4 | 785.5 | 819.9 | 692.2 | 636.5 | 579.1 | 752.2 | 721.6 | 667.2 | 521 | 711.2 | 603 | 368.3 | 355.2 | 365.8 | 347.6 | 350.5 | 355.3 | 359 | 344.1
1682.2 | 1406.2 | 469 | 187.6 | 219.2936 | 375.1 | 399.3 | 339.2 | 339 | 515.5 | 60.8 | 18.3 | 110.9 | 8.6 | 248.2 | 13.5 | 808.3 | 777 | 782.3 | 821.2 | 694.1 | 637.2 | 574.9 | 739.5 | 715.1 | 665.8 | 521.4 | 710.2 | 599.4 | 368.5 | 355.6 | 366.4 | 347.7 | 350.5 | 355.3 | 359.2 | 344
1683.2 | 1407.2 | 467.5 | 187 | 218.5922 | 374.6 | 398.6 | 339.7 | 339.4 | 513.1 | 60.7 | 18.3 | 110.8 | 8.2 | 252.8 | 14.9 | 811.6 | 772.3 | 787.6 | 822.8 | 698.3 | 637.4 | 569.6 | 729.3 | 707.9 | 664.6 | 521.8 | 710 | 596.2 | 368.7 | 356 | 367.2 | 347.8 | 350.6 | 355.1 | 359.3 | 344
1684.2 | 1408.2 | 468.5 | 187.4 | 219.0598 | 373.6 | 398.6 | 340.7 | 339.6 | 504.9 | 60.7 | 18.3 | 110.9 | 9.3 | 255.9 | 16.3 | 813.4 | 774.6 | 780.2 | 824.1 | 699.5 | 637.6 | 566.1 | 725 | 703.3 | 665.2 | 522.2 | 707.9 | 594.1 | 368.9 | 356.3 | 367.5 | 347.8 | 350.7 | 354.9 | 359.2 | 343.9
1685.2 | 1409.2 | 470.8 | 188.32 | 220.1352 | 372.9 | 398.7 | 341.5 | 339.6 | 498.7 | 60.6 | 18.3 | 111.1 | 7.4 | 247 | 17.6 | 813 | 774.7 | 774.7 | 824.7 | 699 | 638.3 | 563.6 | 720 | 700 | 663.3 | 522.5 | 706 | 592.9 | 369 | 356.4 | 367.6 | 347.8 | 350.7 | 354.6 | 358.8 | 343.9
1686.2 | 1410.2 | 469.8 | 187.92 | 219.6677 | 372.6 | 398.1 | 341.7 | 339.6 | 493.2 | 60.6 | 18.3 | 111.2 | 7.1 | 231.9 | 17.6 | 814.8 | 770.1 | 770.6 | 825 | 700.6 | 639 | 563.1 | 720.7 | 701 | 663.6 | 522.8 | 709 | 591.7 | 369.2 | 356.5 | 367.7 | 347.9 | 350.8 | 354.5 | 359.4 | 343.8
1687.2 | 1411.2 | 468.7 | 187.48 | 219.1533 | 372.9 | 399.9 | 341.6 | 339.5 | 494.6 | 60.6 | 18.3 | 111.3 | 8.5 | 244.5 | 17.3 | 815.2 | 756.4 | 764.6 | 823.9 | 702.4 | 639.2 | 559.1 | 712.2 | 692.5 | 661.9 | 523.2 | 712.8 | 589 | 369.4 | 357.2 | 368 | 348.1 | 350.9 | 354.1 | 359.2 | 343.7
1688.2 | 1412.2 | 469.1 | 187.64 | 219.3403 | 373.6 | 401.4 | 341.7 | 339.2 | 493.2 | 60.5 | 18.3 | 111.3 | 8.2 | 245.3 | 18.5 | 818.7 | 753.3 | 769.7 | 824.3 | 704 | 639.6 | 556.3 | 716.5 | 691.5 | 662.1 | 523.8 | 718.1 | 586.4 | 369.6 | 357.6 | 368.3 | 348.3 | 350.9 | 353.7 | 358.8 | 343.6
1689.2 | 1413.2 | 467.4 | 186.96 | 218.5455 | 373.8 | 401.5 | 342.2 | 338.5 | 491.6 | 60.5 | 18.3 | 111.2 | 7.6 | 242.7 | 17.8 | 821.4 | 746 | 764.5 | 825.2 | 705.3 | 640.3 | 554.4 | 724.9 | 692.8 | 663.5 | 524.2 | 719.5 | 584.2 | 369.7 | 358.2 | 368.4 | 348.4 | 351 | 353.3 | 359 | 343.5
1690.2 | 1414.2 | 468.3 | 187.32 | 218.9663 | 373.5 | 401.1 | 342.2 | 338.4 | 493.7 | 60.5 | 18.3 | 111.1 | 7.9 | 237.7 | 17.3 | 822.8 | 736.5 | 750.6 | 825.9 | 702.6 | 640.8 | 553.2 | 726 | 689.5 | 661.7 | 524.5 | 716.1 | 584.6 | 369.8 | 358.9 | 368.5 | 348.5 | 351.1 | 353.1 | 358.8 | 343.4
1691.2 | 1415.2 | 468.5 | 187.4 | 219.0598 | 373.6 | 399.1 | 342.3 | 338.9 | 497.5 | 60.5 | 18.3 | 111.2 | 9.1 | 232.8 | 16.3 | 822.3 | 728.4 | 744.1 | 826.4 | 700.9 | 641.1 | 551.5 | 717 | 687.3 | 659.7 | 524.7 | 705.6 | 587.7 | 370.1 | 359.3 | 369 | 348.7 | 351.2 | 352.8 | 358.8 | 343.3
1692.2 | 1416.2 | 468.6 | 187.44 | 219.1066 | 373.6 | 397.8 | 342.7 | 339.1 | 503.4 | 60.5 | 18.3 | 111.3 | 9.2 | 254.8 | 12.9 | 822 | 728.8 | 745.3 | 826.5 | 699.6 | 641.1 | 547.9 | 701.1 | 680.4 | 656.4 | 524.8 | 697.3 | 589.8 | 370.2 | 359.6 | 369.5 | 348.8 | 351.2 | 352.4 | 358.9 | 343.1
1693.2 | 1417.2 | 469.1 | 187.64 | 219.3403 | 373 | 398.4 | 343.2 | 339.1 | 501.9 | 60.5 | 18.3 | 111.3 | 8.6 | 269.7 | 12 | 824.9 | 739.8 | 758.1 | 827.8 | 703.1 | 641.5 | 548.7 | 706.7 | 682.5 | 658.1 | 524.9 | 703.3 | 590.5 | 370.5 | 359.7 | 370.1 | 348.9 | 351.3 | 352.2 | 358.9 | 343.1
1694.2 | 1418.2 | 469.2 | 187.68 | 219.3871 | 372.6 | 399.1 | 343.7 | 339.6 | 496.5 | 60.4 | 18.3 | 111.2 | 7.6 | 236.6 | 13.7 | 827.6 | 750.3 | 768.3 | 829.7 | 706.7 | 641.8 | 554.2 | 716.7 | 696.2 | 660.6 | 525.1 | 707.3 | 590.3 | 370.5 | 359.7 | 370.4 | 348.8 | 351.3 | 352.1 | 358.9 | 343.1
1695.2 | 1419.2 | 469.1 | 187.64 | 219.3403 | 372.1 | 396.9 | 344 | 339.7 | 489.4 | 60.3 | 18.3 | 111.1 | 5.3 | 240.1 | 15.2 | 829.8 | 760.3 | 766.3 | 831.5 | 707 | 642 | 561.4 | 721.7 | 705.1 | 663 | 525.3 | 710.4 | 591.2 | 370.6 | 359.7 | 370.4 | 348.6 | 351.4 | 352.2 | 358.9 | 343.1
1696.2 | 1420.2 | 468.9 | 187.56 | 219.2468 | 371.9 | 396.7 | 344 | 339.6 | 495 | 60.2 | 18.3 | 111.1 | 6.3 | 271 | 13.4 | 831.9 | 756.1 | 762.3 | 832.7 | 706.5 | 643.5 | 562.3 | 726 | 707.2 | 662.5 | 525.5 | 713.9 | 591.3 | 370.6 | 360.1 | 370.7 | 348.7 | 351.4 | 352.2 | 358.7 | 343.1
1697.2 | 1421.2 | 469.9 | 187.96 | 219.7144 | 372.3 | 398.9 | 343.8 | 339.5 | 500.9 | 60.2 | 18.3 | 111.2 | 8.8 | 277.4 | 11.5 | 830.8 | 738.4 | 748 | 832.4 | 703.1 | 644.3 | 559 | 720.7 | 700.1 | 660.3 | 525.6 | 714.1 | 589.7 | 370.7 | 360.5 | 371.4 | 349 | 351.4 | 352 | 358.5 | 342.9
1698.2 | 1422.2 | 469.7 | 187.88 | 219.6209 | 372.9 | 399.1 | 343.9 | 338.8 | 502.1 | 60.2 | 18.3 | 111.2 | 6.9 | 273.2 | 11.8 | 830 | 733.7 | 739.8 | 832.4 | 702.6 | 644 | 554.2 | 709.1 | 693.5 | 658.2 | 525.5 | 705.9 | 590.3 | 370.9 | 360.9 | 371.7 | 349 | 351.5 | 351.9 | 358.4 | 342.9
1699.2 | 1423.2 | 469.8 | 187.92 | 219.6677 | 372.7 | 397.8 | 344.4 | 338.6 | 495.7 | 60.2 | 18.3 | 111.1 | 5.6 | 270.9 | 13.2 | 830.9 | 748.6 | 741.4 | 833.6 | 703.1 | 643.5 | 553.8 | 709 | 696.5 | 659.1 | 525.3 | 697.8 | 593.5 | 370.9 | 361 | 371.7 | 348.9 | 351.5 | 351.9 | 358.4 | 342.8
1700.2 | 1424.2 | 469.8 | 187.92 | 219.6677 | 372.8 | 395.2 | 344.4 | 338.9 | 489.4 | 60.2 | 18.3 | 111.1 | 6.2 | 242.5 | 13.1 | 832.5 | 761.7 | 748.7 | 835.4 | 704.6 | 644 | 559.9 | 719.2 | 707.7 | 662.2 | 525.3 | 699.8 | 595.8 | 371 | 360.6 | 371.6 | 348.9 | 351.6 | 352 | 358.3 | 342.8
1701.2 | 1425.2 | 469.5 | 187.8 | 219.5274 | 372.5 | 395.4 | 343.9 | 339.1 | 488.4 | 60.3 | 18.3 | 111 | 5.9 | 241.1 | 10.5 | 835.1 | 763.7 | 753.9 | 837.5 | 706.3 | 644.3 | 560.9 | 726.8 | 708.2 | 663 | 525.3 | 707.2 | 597.1 | 371.1 | 360.4 | 371.5 | 348.9 | 351.6 | 351.9 | 358.2 | 342.7
1702.2 | 1426.2 | 469.8 | 187.92 | 219.6677 | 372.1 | 395.2 | 343.5 | 339 | 489.6 | 60.3 | 18.3 | 111 | 6.4 | 234.8 | 10.6 | 836.9 | 767.2 | 756.6 | 839.2 | 706.7 | 645.4 | 561.4 | 729.1 | 709.6 | 663.5 | 525.4 | 706.8 | 597.8 | 371.2 | 360.5 | 371.7 | 349 | 351.7 | 351.7 | 358.1 | 342.7
1703.2 | 1427.2 | 469.7 | 187.88 | 219.6209 | 371.8 | 394.2 | 343.7 | 339.1 | 486.5 | 60.4 | 18.3 | 110.9 | 6.5 | 252.1 | 11.3 | 838.4 | 774.5 | 759.2 | 841.4 | 708.1 | 646.1 | 563.7 | 733.8 | 715.3 | 665.3 | 525.3 | 706.3 | 599.2 | 371.3 | 360.2 | 371.4 | 349 | 351.7 | 351.6 | 358 | 342.7
1704.2 | 1428.2 | 469.9 | 187.96 | 219.7144 | 371.6 | 395.1 | 343.9 | 339.3 | 483 | 60.5 | 18.3 | 110.9 | 8.8 | 236.5 | 13 | 840.5 | 787.9 | 757.9 | 843.8 | 707.9 | 646.5 | 569.5 | 735.4 | 723.8 | 668.3 | 525.2 | 703.9 | 601.8 | 371.2 | 359.8 | 370.8 | 348.8 | 351.7 | 351.5 | 358 | 342.7
1705.2 | 1429.2 | 469.7 | 187.88 | 219.6209 | 371.2 | 396.2 | 343.5 | 339.2 | 477.7 | 60.6 | 18.3 | 110.9 | 9 | 229 | 12.9 | 841.6 | 795.4 | 759.8 | 846.3 | 708 | 647.1 | 574.1 | 735 | 730.8 | 670.2 | 525.1 | 698.8 | 605.5 | 371.2 | 359.3 | 370.4 | 348.7 | 351.8 | 351.5 | 357.8 | 342.6
1706.2 | 1430.2 | 469.3 | 187.72 | 219.4339 | 371.1 | 397.2 | 342.9 | 338.9 | 475 | 60.7 | 18.3 | 111 | 8.1 | 243.6 | 12.2 | 843.4 | 791.9 | 764.4 | 848.1 | 709.8 | 647.4 | 576.3 | 734.9 | 732.3 | 671.2 | 524.9 | 702.1 | 608 | 371.2 | 359 | 369.9 | 348.7 | 351.8 | 351.5 | 357.5 | 342.6
1707.2 | 1431.2 | 469.5 | 187.8 | 219.5274 | 370.9 | 397.6 | 342.6 | 338.6 | 476.6 | 60.7 | 18.3 | 111.1 | 7.3 | 258.9 | 13.1 | 843.6 | 783.3 | 753.7 | 848.5 | 707.9 | 648.1 | 575.1 | 727.6 | 728.7 | 670.5 | 524.8 | 695.3 | 609.7 | 371.2 | 358.7 | 369.7 | 348.7 | 351.9 | 351.6 | 357.5 | 342.5
1708.2 | 1432.2 | 470 | 188 | 219.7612 | 370.5 | 400.7 | 342.5 | 338.5 | 473.1 | 60.8 | 18.3 | 111.2 | 7.3 | 249.6 | 13.5 | 844 | 786.6 | 758.3 | 848.5 | 708.9 | 648.1 | 574.1 | 723.9 | 727.6 | 670.4 | 524.5 | 694.8 | 610.2 | 371.2 | 358.1 | 369 | 348.5 | 351.9 | 351.6 | 357.3 | 342.5
1709.2 | 1433.2 | 469.8 | 187.92 | 219.6677 | 370.3 | 401.9 | 342.3 | 338.7 | 471.5 | 60.9 | 18.3 | 111.2 | 7.3 | 256.3 | 15.3 | 844.9 | 792.1 | 761.5 | 849.5 | 709.6 | 648.6 | 575.8 | 723 | 727.3 | 671.5 | 524.2 | 694.8 | 611.5 | 371.2 | 357.7 | 368.5 | 348.3 | 351.9 | 351.6 | 357.1 | 342.6
1710.2 | 1434.2 | 469.8 | 187.92 | 219.6677 | 369.9 | 402 | 341.9 | 338.7 | 472.1 | 61 | 18.3 | 111 | 6.9 | 255.2 | 16.4 | 846.4 | 801.2 | 764.8 | 851 | 711.5 | 649.5 | 581.4 | 731.3 | 734.9 | 675.4 | 524.1 | 699.5 | 612.1 | 371.2 | 357.4 | 368.1 | 348.2 | 352 | 351.5 | 357 | 342.5
1711.2 | 1435.2 | 470.2 | 188.08 | 219.8547 | 369.5 | 404 | 341.3 | 338.1 | 478.1 | 61 | 18.3 | 110.8 | 6.8 | 249.2 | 16.5 | 848.9 | 807.5 | 774.4 | 852.7 | 714.4 | 651.2 | 591.4 | 737.3 | 744.1 | 679.4 | 524.2 | 703.4 | 611.2 | 371.1 | 357 | 367.7 | 348.2 | 352 | 351.5 | 357 | 342.5
1712.2 | 1436.2 | 469.7 | 187.88 | 219.6209 | 369.3 | 405.5 | 340.9 | 337.4 | 485.3 | 61 | 18.3 | 110.6 | 8 | 252.9 | 15.3 | 850.1 | 810 | 780.2 | 854.1 | 719.4 | 652 | 597.4 | 729.4 | 752 | 680.9 | 524.3 | 692.7 | 608.1 | 371.1 | 356.6 | 367.4 | 348.1 | 352 | 351.6 | 357.3 | 342.5
1713.2 | 1437.2 | 470.4 | 188.16 | 219.9482 | 369 | 406 | 340.8 | 337.6 | 489 | 61.1 | 18.3 | 110.6 | 8.7 | 256.4 | 14.8 | 852.4 | 809.2 | 787.8 | 855.2 | 722.7 | 652.7 | 600.7 | 733.6 | 757 | 684.1 | 524.7 | 696.8 | 604.4 | 371.1 | 356.3 | 367.1 | 348 | 352.1 | 351.7 | 357.3 | 342.6
1714.2 | 1438.2 | 469.5 | 187.8 | 219.5274 | 369.1 | 407.2 | 340.7 | 338 | 494.3 | 61.1 | 18.3 | 110.5 | 8.6 | 263.5 | 14.7 | 853.5 | 794.4 | 788.5 | 856.1 | 722.1 | 654.1 | 596.1 | 741.5 | 750.8 | 683 | 525 | 707.9 | 601.7 | 371.1 | 356.4 | 367.2 | 348.3 | 352.1 | 351.4 | 357.3 | 342.5
1715.2 | 1439.2 | 469.9 | 187.96 | 219.7144 | 369.1 | 407.6 | 341.1 | 338.4 | 500 | 61.1 | 18.3 | 110.5 | 10.5 | 249.7 | 17.3 | 856 | 792.3 | 791.2 | 857.7 | 724 | 655.8 | 594.1 | 747.4 | 750.8 | 685.2 | 525.5 | 714.7 | 599.6 | 371.2 | 356.5 | 367.1 | 348.4 | 352.1 | 351.3 | 357.5 | 342.4
1716.2 | 1440.2 | 469.5 | 187.8 | 219.5274 | 369.1 | 408.7 | 341.6 | 338.7 | 497.1 | 61.1 | 18.3 | 110.6 | 10.6 | 246.4 | 19.2 | 856.8 | 791.7 | 775.5 | 859.2 | 721.9 | 656.5 | 591.1 | 743.1 | 747.1 | 685.2 | 525.7 | 711.1 | 599.5 | 371.2 | 356.4 | 367 | 348.4 | 352.2 | 351.3 | 357.8 | 342.4
1717.2 | 1441.2 | 469.7 | 187.88 | 219.6209 | 368.9 | 408.8 | 341.5 | 338.9 | 492.6 | 61 | 18.3 | 110.4 | 9.1 | 248.2 | 19.7 | 857.8 | 793.3 | 771.7 | 860.6 | 721.6 | 657.3 | 590.5 | 744.6 | 748.2 | 686.1 | 525.8 | 705.3 | 603.3 | 371.2 | 356.3 | 366.9 | 348.4 | 352.2 | 351.4 | 357.8 | 342.4
1718.2 | 1442.2 | 469.7 | 187.88 | 219.6209 | 368.7 | 409 | 341.6 | 339.3 | 490.8 | 61 | 18.3 | 110.3 | 7.7 | 244.2 | 19.8 | 858.4 | 791.6 | 774.1 | 861.5 | 722 | 658.2 | 588.1 | 741.4 | 747.8 | 684.6 | 525.9 | 702.4 | 608.3 | 371.2 | 356.1 | 366.8 | 348.3 | 352.2 | 351.4 | 357.7 | 342.4
1719.2 | 1443.2 | 469.6 | 187.84 | 219.5741 | 368.7 | 408.2 | 341.9 | 339.1 | 487 | 61 | 18.3 | 110.1 | 7.2 | 245.4 | 19.4 | 859.3 | 797.9 | 778 | 862.5 | 721.7 | 658.7 | 588.6 | 740.2 | 751 | 685.4 | 525.8 | 700.1 | 611.5 | 371.1 | 355.8 | 366.6 | 348.1 | 352.3 | 351.4 | 357.6 | 342.4
1720.2 | 1444.2 | 469.3 | 187.72 | 219.4339 | 368.1 | 409.5 | 342.1 | 338.8 | 487.4 | 61.1 | 18.3 | 110 | 6.4 | 241.6 | 18.4 | 861.7 | 796.3 | 779.1 | 864 | 721.8 | 659.6 | 587.9 | 744.6 | 753 | 686.1 | 525.9 | 703.9 | 613.4 | 371.1 | 355.7 | 366.5 | 348.2 | 352.3 | 351.4 | 357.5 | 342.4
1721.2 | 1445.2 | 469.7 | 187.88 | 219.6209 | 367.8 | 408.6 | 342.1 | 338.3 | 486.6 | 61.1 | 18.3 | 110 | 6 | 269.4 | 15 | 862.7 | 799.4 | 773.2 | 865.1 | 720.5 | 660.8 | 587 | 741.3 | 755.6 | 686.4 | 525.9 | 697.3 | 614.6 | 371.1 | 355.8 | 366.4 | 348.2 | 352.3 | 351.2 | 357.3 | 342.3
1722.2 | 1446.2 | 470.5 | 188.2 | 219.995 | 367.9 | 405.7 | 342 | 338.1 | 483.7 | 61.1 | 18.3 | 110 | 5.4 | 258.5 | 13.5 | 862.3 | 792.7 | 765.9 | 865 | 718.9 | 661.3 | 585.9 | 733.5 | 753.8 | 685.7 | 525.8 | 695.4 | 615.8 | 371 | 355.8 | 366.4 | 348.3 | 352.4 | 351.1 | 357.1 | 342.2
1723.2 | 1447.2 | 471.3 | 188.52 | 220.369 | 368.2 | 403.1 | 341.9 | 338.2 | 486.5 | 61.1 | 18.3 | 110.1 | 4.7 | 265.6 | 12.2 | 858.1 | 780 | 750.9 | 863 | 714.5 | 660.9 | 578.7 | 713.5 | 737.9 | 681.1 | 525.5 | 685.9 | 615.2 | 371.1 | 355.9 | 366.4 | 348.5 | 352.4 | 350.9 | 357 | 342.2
1724.2 | 1448.2 | 469.7 | 187.88 | 219.6209 | 368.3 | 401.9 | 341.7 | 338.4 | 481.9 | 61.1 | 18.3 | 110.1 | 5.2 | 268.3 | 11.6 | 856.6 | 781 | 750.1 | 862.1 | 714.4 | 660.7 | 574.4 | 709.7 | 729.5 | 680.4 | 525.2 | 682.3 | 615.5 | 371.1 | 355.6 | 366.3 | 348.4 | 352.4 | 351 | 357 | 342.2
1725.2 | 1449.2 | 469.3 | 187.72 | 219.4339 | 368.1 | 399.5 | 341.4 | 338.6 | 477 | 61 | 18.3 | 110.2 | 6.7 | 282.5 | 13.2 | 857.3 | 786.8 | 749.5 | 861.6 | 714.6 | 660.9 | 575 | 711.1 | 733.3 | 680.9 | 524.9 | 682.1 | 616.3 | 371.1 | 355.7 | 366.2 | 348.4 | 352.5 | 351.1 | 357.1 | 342.2
1726.2 | 1450.2 | 469.7 | 187.88 | 219.6209 | 368 | 398.2 | 340.9 | 338.3 | 477.1 | 61 | 18.3 | 110.4 | 8.4 | 264 | 13.3 | 857.9 | 783.7 | 755.4 | 861.5 | 713.8 | 661.8 | 574.4 | 719.4 | 733.7 | 680.2 | 524.7 | 689.3 | 617.1 | 371.1 | 356 | 366.2 | 348.5 | 352.5 | 351.1 | 357.1 | 342.1
1727.2 | 1451.2 | 469.4 | 187.76 | 219.4806 | 367.9 | 400.2 | 340.8 | 337.9 | 479.2 | 61 | 18.3 | 110.5 | 10.1 | 254 | 14.2 | 858.3 | 777.9 | 757.6 | 861 | 713.9 | 662.3 | 572.6 | 722.1 | 731.9 | 679.6 | 524.5 | 690.5 | 618.5 | 371 | 356.1 | 366.3 | 348.6 | 352.5 | 351.1 | 357.1 | 342.1
1728.2 | 1452.2 | 471.1 | 188.44 | 220.2755 | 368 | 402.7 | 340.7 | 337.3 | 478.7 | 61 | 18.3 | 110.7 | 10.6 | 253.7 | 13.4 | 858 | 779.1 | 764.3 | 860.6 | 714.8 | 662.8 | 571.2 | 728.6 | 731.8 | 680.4 | 524.3 | 697.9 | 619.3 | 371 | 356.2 | 366.4 | 348.6 | 352.6 | 351.2 | 357 | 342.1
1729.2 | 1453.2 | 470.9 | 188.36 | 220.182 | 368.2 | 402.1 | 341.1 | 336.8 | 481.6 | 60.9 | 18.3 | 110.8 | 10 | 257.2 | 12.6 | 857.9 | 772.9 | 768.4 | 859.9 | 715.7 | 663.9 | 572.7 | 727.7 | 733.5 | 681.5 | 524.3 | 702.6 | 618.4 | 371 | 356.4 | 366.5 | 348.5 | 352.6 | 351.2 | 356.9 | 342
1730.2 | 1454.2 | 471.3 | 188.52 | 220.369 | 368.3 | 402 | 341.4 | 336.1 | 486.4 | 60.9 | 18.3 | 110.8 | 8.1 | 242.5 | 16.4 | 857.2 | 756.6 | 774.2 | 857.9 | 713.6 | 664 | 567.3 | 714.1 | 721.5 | 677.9 | 524.2 | 702.5 | 615.7 | 371.2 | 357 | 367 | 348.8 | 352.6 | 351.1 | 357 | 342
1731.2 | 1455.2 | 471 | 188.4 | 220.2287 | 368.3 | 402 | 341.8 | 336.5 | 490.7 | 61 | 18.3 | 110.7 | 6.8 | 240.1 | 18.7 | 856.4 | 745.8 | 770.7 | 856 | 714.6 | 663.9 | 562.7 | 710.8 | 712.6 | 676.6 | 524.4 | 706.6 | 611.8 | 371.3 | 357.6 | 367.6 | 349.1 | 352.6 | 351.2 | 357.4 | 341.9
1732.2 | 1456.2 | 469.9 | 187.96 | 219.7144 | 368.1 | 401.4 | 342.6 | 337.1 | 494.6 | 61 | 18.3 | 110.8 | 7.8 | 244.7 | 19.1 | 854.4 | 740.5 | 764.5 | 853.8 | 714.6 | 664.3 | 560.2 | 708.6 | 705.7 | 675.6 | 524.7 | 709.9 | 608 | 371.3 | 358.2 | 368.3 | 349.3 | 352.7 | 351.2 | 358 | 341.8
1733.2 | 1457.2 | 470.2 | 188.08 | 219.8547 | 368 | 400.1 | 343 | 337.6 | 496.6 | 61.1 | 18.3 | 110.8 | 8 | 244.5 | 19.1 | 852.5 | 742.5 | 748.5 | 851.5 | 711.5 | 663.6 | 556 | 695.8 | 698.8 | 673 | 524.7 | 701.9 | 604.5 | 371.3 | 358.6 | 368.8 | 349.6 | 352.7 | 351.2 | 358.3 | 341.7
1734.2 | 1458.2 | 470.5 | 188.2 | 219.995 | 367.9 | 396.7 | 343.4 | 338.3 | 491.5 | 61.2 | 18.3 | 110.9 | 9.3 | 244.1 | 18.6 | 852.4 | 750 | 747.3 | 850.4 | 710.8 | 662.4 | 553.6 | 691.7 | 696.5 | 672.4 | 524.6 | 699.1 | 602.9 | 371.3 | 358.8 | 369.3 | 349.6 | 352.7 | 351.1 | 358.4 | 341.7
1735.2 | 1459.2 | 470.6 | 188.24 | 220.0417 | 367.8 | 394.2 | 343.4 | 339.1 | 483.3 | 61.3 | 18.3 | 110.9 | 7.6 | 239.4 | 17.9 | 852.8 | 761.9 | 753.3 | 850.3 | 712.4 | 661.8 | 552.3 | 693.2 | 700 | 672.2 | 524.4 | 695.8 | 603.3 | 371.2 | 358.7 | 369.3 | 349.3 | 352.7 | 351 | 358.4 | 341.7
1736.2 | 1460.2 | 470.3 | 188.12 | 219.9014 | 367.3 | 391.5 | 343.2 | 339.2 | 481.1 | 61.3 | 18.3 | 110.9 | 7.2 | 240.8 | 16.8 | 854.1 | 769.7 | 768.6 | 851 | 713.9 | 661.8 | 553.8 | 702.3 | 703.6 | 673.8 | 524.2 | 700.8 | 603.7 | 371.2 | 358.5 | 369.3 | 349.3 | 352.8 | 350.9 | 358 | 341.7
1737.2 | 1461.2 | 470 | 188 | 219.7612 | 367 | 389.6 | 342.2 | 338.8 | 482.5 | 61.2 | 18.3 | 110.9 | 7.3 | 236.4 | 15.2 | 853.8 | 776.7 | 770.8 | 851.9 | 714.8 | 661.6 | 560.2 | 706.2 | 710.9 | 675.5 | 524.1 | 699.9 | 602.9 | 371.2 | 358.2 | 369 | 349.1 | 352.8 | 350.9 | 357.8 | 341.7
1738.2 | 1462.2 | 470.1 | 188.04 | 219.8079 | 366.8 | 390.2 | 340.9 | 338.4 | 478 | 61.1 | 18.3 | 110.9 | 7.4 | 243.2 | 14.9 | 851.4 | 779.4 | 766.7 | 851.8 | 716.3 | 661 | 562.7 | 704.3 | 712.9 | 675.2 | 523.9 | 699.3 | 602.8 | 371.1 | 358 | 368.7 | 348.9 | 352.9 | 350.9 | 357.7 | 341.7
1739.2 | 1463.2 | 470.3 | 188.12 | 219.9014 | 367.1 | 391.1 | 339.7 | 338.4 | 474.9 | 61 | 18.3 | 111 | 7.2 | 249.3 | 17.6 | 850.6 | 782 | 761.4 | 851.6 | 716.1 | 661 | 566.4 | 704.2 | 716.3 | 676.4 | 523.7 | 691.2 | 605.3 | 371.1 | 357.9 | 368.6 | 348.7 | 352.9 | 351 | 357.6 | 341.8
1740.2 | 1464.2 | 470.1 | 188.04 | 219.8079 | 367.3 | 392.8 | 338.8 | 338.5 | 475.3 | 60.9 | 18.3 | 111 | 8.1 | 247.5 | 18.8 | 847.8 | 776.8 | 752.9 | 849.3 | 715.1 | 660.3 | 565.8 | 689.2 | 713.7 | 673.8 | 523.2 | 677.6 | 606.7 | 371 | 357.8 | 368.3 | 348.7 | 352.9 | 351.2 | 358 | 341.8
1741.2 | 1465.2 | 469.8 | 187.92 | 219.6677 | 367.5 | 394.7 | 338.8 | 338.6 | 473.6 | 60.8 | 18.3 | 111.1 | 8.2 | 261.2 | 16.6 | 846.6 | 772.4 | 756.2 | 847.6 | 715.4 | 659.7 | 566.9 | 682.2 | 712 | 673.1 | 522.8 | 676.3 | 607.1 | 371 | 357.4 | 368 | 348.6 | 353 | 351.2 | 357.8 | 341.8
1742.2 | 1466.2 | 470.3 | 188.12 | 219.9014 | 367.8 | 395.8 | 338.9 | 338.9 | 467.9 | 60.8 | 18.3 | 111.1 | 7.7 | 257 | 15.9 | 844.7 | 767.2 | 751.4 | 845.6 | 713.5 | 659.5 | 564.3 | 689.7 | 706.6 | 672 | 522.4 | 680.5 | 609.7 | 370.9 | 357.2 | 367.7 | 348.7 | 353 | 351 | 357.6 | 341.8
1743.2 | 1467.2 | 469.7 | 187.88 | 219.6209 | 367.6 | 395.3 | 338.7 | 338.7 | 468.3 | 60.7 | 18.3 | 111 | 8.1 | 258 | 15.3 | 845.1 | 774 | 753.4 | 844.8 | 714.6 | 659.9 | 563.9 | 694.1 | 709.8 | 672 | 522.1 | 678.5 | 612.2 | 370.9 | 357 | 367.4 | 348.7 | 353.1 | 350.8 | 357.4 | 341.7
1744.2 | 1468.2 | 471 | 188.4 | 220.2287 | 367.1 | 395.1 | 338.6 | 338.5 | 465.7 | 60.7 | 18.3 | 110.8 | 7.1 | 268 | 15.5 | 845.4 | 779.1 | 743.3 | 844.8 | 713.8 | 659.2 | 563.8 | 696 | 711.7 | 671.7 | 521.7 | 675.7 | 615.7 | 370.9 | 356.6 | 367 | 348.5 | 353.1 | 350.7 | 357.1 | 341.7
1745.2 | 1469.2 | 472 | 188.8 | 220.6963 | 366.6 | 394.7 | 338.8 | 338.4 | 463.5 | 60.7 | 18.3 | 110.7 | 6.9 | 247.1 | 18.1 | 843.8 | 781.5 | 728.9 | 844.5 | 709.9 | 658.7 | 563.2 | 682.7 | 711.3 | 670.4 | 521.3 | 660.6 | 620.5 | 370.8 | 356.2 | 366.6 | 348.3 | 353.1 | 350.9 | 356.9 | 341.8
1746.2 | 1470.2 | 470.2 | 188.08 | 219.8547 | 366.3 | 394.5 | 338.5 | 338.3 | 463 | 60.7 | 18.3 | 110.5 | 6.4 | 244.5 | 20.7 | 842 | 783.7 | 722.5 | 843 | 708.6 | 657.9 | 561.6 | 674 | 707.5 | 669 | 520.7 | 649 | 623.7 | 370.7 | 355.6 | 366.2 | 348.2 | 353.2 | 351.1 | 356.8 | 341.9
1747.2 | 1471.2 | 469.4 | 187.76 | 219.4806 | 366.3 | 397.1 | 338.2 | 338.3 | 463.9 | 60.7 | 18.3 | 110.5 | 7.4 | 246.4 | 19.5 | 839 | 780.4 | 706.5 | 840.9 | 705 | 657.5 | 560.9 | 666.4 | 706.5 | 667.5 | 520.1 | 638.3 | 626.4 | 370.6 | 355 | 365.7 | 348 | 353.2 | 351.2 | 356.7 | 341.9
1748.2 | 1472.2 | 469.4 | 187.76 | 219.4806 | 366 | 397.4 | 338 | 338.4 | 463.4 | 60.7 | 18.3 | 110.4 | 8.6 | 251.4 | 18.6 | 835.9 | 773.9 | 691.7 | 838.3 | 701.1 | 656.4 | 555.8 | 650.3 | 697.9 | 664.1 | 519.4 | 627.5 | 627.8 | 370.5 | 354.4 | 365.2 | 347.8 | 353.2 | 351.3 | 356.6 | 342
1749.2 | 1473.2 | 470 | 188 | 219.7612 | 366.1 | 399.7 | 337.7 | 338.3 | 462.3 | 60.7 | 18.3 | 110.5 | 9.4 | 265.7 | 17.3 | 833.4 | 778.9 | 685.8 | 835.9 | 699.5 | 655.2 | 555.2 | 641.7 | 695.9 | 663.1 | 518.7 | 618.2 | 627.5 | 370.4 | 354 | 364.7 | 347.6 | 353.3 | 351.7 | 356.7 | 342.1
1750.2 | 1474.2 | 471.1 | 188.44 | 220.2755 | 366.1 | 403.1 | 337.4 | 338.4 | 463.3 | 60.7 | 18.3 | 110.8 | 9.3 | 261.5 | 16.2 | 832 | 785.3 | 679.9 | 834 | 698.5 | 654.7 | 557.6 | 638.7 | 696.5 | 663.1 | 518 | 609.8 | 626.8 | 370.4 | 353.5 | 364.2 | 347.4 | 353.3 | 352 | 357.1 | 342.2
1751.2 | 1475.2 | 471.4 | 188.56 | 220.4158 | 366.4 | 404.7 | 336.8 | 338.5 | 470.6 | 60.8 | 18.3 | 111 | 8.4 | 251.9 | 14.3 | 830 | 791.3 | 674.1 | 832 | 697.6 | 654.3 | 562.9 | 635 | 700 | 663.5 | 517.3 | 603.5 | 624.5 | 370.3 | 353.1 | 363.9 | 347.3 | 353.3 | 352.4 | 357.5 | 342.3
1752.2 | 1476.2 | 471 | 188.4 | 220.2287 | 366.4 | 404.7 | 336.7 | 338.7 | 473.3 | 60.8 | 18.3 | 111.1 | 8.6 | 249.3 | 16.3 | 826.9 | 791.7 | 663.2 | 829 | 694.7 | 653.6 | 563.7 | 626.6 | 702.5 | 662.5 | 516.6 | 597.6 | 621.8 | 370.3 | 352.5 | 363.7 | 347.1 | 353.3 | 352.9 | 357.8 | 342.4
1753.2 | 1477.2 | 470.9 | 188.36 | 220.182 | 366.5 | 406.1 | 336.9 | 338.7 | 482 | 60.8 | 18.3 | 111.2 | 7.6 | 247.3 | 18.1 | 823.5 | 788.6 | 659 | 825.8 | 692.2 | 652.7 | 562.1 | 615.9 | 698 | 660 | 515.9 | 593.6 | 617.9 | 370.2 | 352 | 363.5 | 347 | 353.3 | 353.4 | 358.2 | 342.5
1754.2 | 1478.2 | 470.6 | 188.24 | 220.0417 | 366.6 | 406 | 336.8 | 338.3 | 483.6 | 60.8 | 18.3 | 111.3 | 7.2 | 251.1 | 16.2 | 823.3 | 795.6 | 675.2 | 824.8 | 695 | 651.8 | 561 | 630.7 | 697.6 | 661.9 | 515.4 | 606.5 | 615.1 | 370.2 | 351.5 | 363.3 | 346.9 | 353.4 | 353.6 | 358.6 | 342.6
1755.2 | 1479.2 | 470.6 | 188.24 | 220.0417 | 366.3 | 407.2 | 337 | 338.2 | 484.2 | 60.8 | 18.3 | 111.2 | 8.2 | 227.1 | 13.8 | 823.1 | 796.3 | 697.1 | 824.3 | 696.6 | 651.3 | 563 | 643 | 700 | 662.9 | 514.8 | 612.4 | 612.1 | 370.2 | 351.1 | 363.3 | 346.8 | 353.4 | 354.1 | 358.7 | 342.7
1756.2 | 1480.2 | 470.8 | 188.32 | 220.1352 | 366.1 | 409.7 | 337.3 | 338.3 | 487.1 | 60.8 | 18.3 | 111.3 | 9.7 | 235.4 | 13.3 | 822.5 | 797.4 | 710.9 | 823.8 | 698.9 | 651 | 570.6 | 648.6 | 708.7 | 664.5 | 514.4 | 609.7 | 608.4 | 370.2 | 350.9 | 363.2 | 346.7 | 353.4 | 354.5 | 359.1 | 342.8
1757.2 | 1481.2 | 470.5 | 188.2 | 219.995 | 365.8 | 408.8 | 337.3 | 338.2 | 486.7 | 60.7 | 18.3 | 111.5 | 11.9 | 229.2 | 15.5 | 822 | 795.5 | 720.9 | 823.6 | 699.3 | 650.5 | 570.5 | 656.1 | 713 | 664.2 | 513.9 | 617.1 | 605.6 | 370.2 | 350.8 | 363.2 | 346.7 | 353.4 | 354.5 | 359.2 | 342.9
1758.2 | 1482.2 | 471 | 188.4 | 220.2287 | 365.4 | 409 | 337.3 | 338.3 | 483.4 | 60.6 | 18.3 | 111.6 | 10.9 | 229.5 | 16.1 | 821.4 | 802.2 | 724.4 | 822.9 | 701.1 | 650.8 | 573 | 664.5 | 718.4 | 664.2 | 513.5 | 618.9 | 602.8 | 370.1 | 350.8 | 363.1 | 346.6 | 353.5 | 354.4 | 359 | 342.9
1759.2 | 1483.2 | 470.8 | 188.32 | 220.1352 | 364.9 | 408.4 | 337.3 | 338.2 | 478.8 | 60.6 | 18.3 | 111.6 | 10.7 | 242.7 | 14 | 821.2 | 798.9 | 734.9 | 822.5 | 703.4 | 650.1 | 570.3 | 662.8 | 714.7 | 662.5 | 513 | 620.3 | 600.1 | 370.1 | 350.8 | 362.9 | 346.6 | 353.5 | 354.5 | 358.9 | 342.9
1760.2 | 1484.2 | 470.3 | 188.12 | 219.9014 | 364.3 | 407.7 | 337.3 | 338.2 | 474.2 | 60.6 | 18.3 | 111.6 | 9.7 | 242.8 | 18.3 | 821.7 | 796.6 | 749.3 | 822.4 | 705.6 | 649.8 | 570.7 | 675.5 | 714.2 | 663.5 | 512.7 | 632.3 | 598.4 | 370.1 | 350.9 | 362.8 | 346.7 | 353.5 | 354.4 | 358.8 | 342.9
1761.2 | 1485.2 | 470.6 | 188.24 | 220.0417 | 363.8 | 407.5 | 337 | 338.1 | 470.5 | 60.6 | 18.3 | 111.5 | 8.5 | 239.9 | 20.8 | 820.1 | 798.5 | 749.6 | 821.6 | 707 | 649.4 | 568.8 | 679.2 | 711.6 | 663.3 | 512.5 | 638.9 | 596.6 | 370 | 350.9 | 362.6 | 346.8 | 353.6 | 354.4 | 358.8 | 342.9
1762.2 | 1486.2 | 470.4 | 188.16 | 219.9482 | 363.7 | 409.2 | 336.3 | 337.9 | 466.5 | 60.6 | 18.3 | 111.5 | 8.3 | 241.7 | 20.9 | 818.6 | 799.6 | 751.6 | 820.9 | 706.1 | 649.4 | 571.3 | 680.2 | 711.6 | 663.7 | 512.3 | 640.5 | 594 | 370 | 350.9 | 362.5 | 346.8 | 353.6 | 354.5 | 359.3 | 342.9
1763.2 | 1487.2 | 469.2 | 187.68 | 219.3871 | 363.9 | 412.1 | 336.2 | 338.1 | 470.1 | 60.5 | 18.3 | 111.5 | 7.9 | 238.5 | 19.6 | 817.6 | 800.7 | 741.1 | 819.6 | 706 | 649.5 | 577.8 | 681.1 | 713.9 | 663.5 | 512 | 637.8 | 591.2 | 369.9 | 350.8 | 362.4 | 346.8 | 353.7 | 354.4 | 359.2 | 342.9
1764.2 | 1488.2 | 469.7 | 187.88 | 219.6209 | 364.2 | 414 | 336 | 338.4 | 469.1 | 60.4 | 18.3 | 111.7 | 7.3 | 244 | 19.6 | 817.1 | 800.4 | 740.2 | 819 | 708.6 | 650.3 | 584.2 | 689.2 | 717.4 | 666 | 511.9 | 637.2 | 589.5 | 369.9 | 350.7 | 362.2 | 346.7 | 353.7 | 354.4 | 359.3 | 342.9
1765.2 | 1489.2 | 469.6 | 187.84 | 219.5741 | 364.2 | 413.7 | 336 | 338.5 | 466.1 | 60.3 | 18.3 | 111.8 | 7.1 | 248.2 | 18 | 816.5 | 803.3 | 734.2 | 818.3 | 708.3 | 650.4 | 581.8 | 682.8 | 717.4 | 665.8 | 511.8 | 633 | 588.8 | 369.8 | 350.5 | 361.8 | 346.6 | 353.7 | 354.5 | 359.3 | 342.9
1766.2 | 1490.2 | 469.8 | 187.92 | 219.6677 | 364.3 | 411.4 | 335.6 | 338.3 | 468.1 | 60.3 | 18.3 | 111.9 | 7.1 | 247.6 | 17.3 | 815.6 | 808.4 | 726.8 | 817.4 | 706.7 | 650.3 | 581.8 | 678.8 | 721.2 | 664.9 | 511.4 | 622.6 | 587.9 | 369.7 | 350.3 | 361.4 | 346.5 | 353.8 | 354.6 | 360 | 343
1767.2 | 1491.2 | 469.9 | 187.96 | 219.7144 | 364.8 | 411 | 334.7 | 338.4 | 469 | 60.1 | 18.3 | 111.7 | 7 | 256.8 | 17.3 | 813.5 | 810.6 | 720.6 | 816 | 704.6 | 650.1 | 582.8 | 669.7 | 719.6 | 664.8 | 511 | 615 | 586.1 | 369.6 | 350.2 | 361.2 | 346.4 | 353.8 | 354.5 | 360 | 343
1768.2 | 1492.2 | 470 | 188 | 219.7612 | 364.8 | 412.3 | 334.7 | 338.6 | 466.2 | 60 | 18.3 | 111.7 | 7.3 | 261.6 | 17.2 | 813.6 | 815 | 729.7 | 815.5 | 706.4 | 649.4 | 585.1 | 674.7 | 727.3 | 667.8 | 510.7 | 620.4 | 585.4 | 369.6 | 350.1 | 361 | 346.4 | 353.9 | 354.4 | 359.9 | 343
1769.2 | 1493.2 | 469.6 | 187.84 | 219.5741 | 364.6 | 410.4 | 334.7 | 338.8 | 464.8 | 60 | 18.3 | 111.6 | 8.1 | 264.4 | 16.7 | 815.2 | 819.9 | 733 | 816.6 | 707.7 | 650.2 | 591.6 | 693.6 | 737.3 | 671.5 | 510.7 | 628.4 | 584.9 | 369.6 | 350 | 361 | 346.4 | 353.9 | 354.2 | 359.9 | 343
1770.2 | 1494.2 | 469 | 187.6 | 219.2936 | 364.2 | 409.7 | 334.6 | 338.7 | 463.1 | 60.1 | 18.3 | 111.5 | 8.8 | 261.3 | 16.8 | 815.3 | 822 | 736.6 | 817.1 | 707 | 650.2 | 591.1 | 694 | 739.5 | 670.9 | 510.5 | 632 | 585.6 | 369.5 | 350 | 361.1 | 346.4 | 354 | 354.2 | 359.9 | 343
1771.2 | 1495.2 | 469.9 | 187.96 | 219.7144 | 363.6 | 409.6 | 334.8 | 338.9 | 460.3 | 60.1 | 18.3 | 111.3 | 9.3 | 251.1 | 17.8 | 815 | 819.4 | 742.1 | 817.2 | 706.2 | 650.3 | 587 | 688.7 | 737.6 | 668.9 | 510.2 | 628.6 | 586.6 | 369.4 | 349.9 | 361 | 346.4 | 354 | 354 | 360 | 342.9
1772.2 | 1496.2 | 471.2 | 188.48 | 220.3223 | 363.3 | 407.3 | 335.3 | 338.7 | 457.7 | 60.1 | 18.3 | 111.2 | 8.1 | 246.8 | 18.9 | 814.3 | 818.5 | 738.3 | 816.7 | 704.5 | 650.3 | 581.5 | 686 | 732.7 | 667.7 | 509.9 | 629.9 | 588.2 | 369.4 | 349.6 | 360.7 | 346.2 | 354 | 353.8 | 359.8 | 342.9
1773.2 | 1497.2 | 470.9 | 188.36 | 220.182 | 363.2 | 410.4 | 335.4 | 338.4 | 454.4 | 60 | 18.3 | 111.1 | 7.8 | 239.2 | 18.2 | 813.8 | 815.6 | 733.9 | 816.7 | 703.4 | 650.2 | 578.5 | 689.6 | 728.7 | 666.7 | 509.5 | 635.4 | 590.7 | 369.3 | 349.6 | 360.4 | 346.2 | 354.1 | 353.4 | 359.4 | 342.8
1774.2 | 1498.2 | 471.3 | 188.52 | 220.369 | 362.9 | 411.6 | 335.2 | 337.9 | 452.8 | 60 | 18.3 | 111.1 | 7.2 | 243.2 | 17.3 | 812.8 | 808.2 | 731.1 | 816.3 | 702 | 649.9 | 576.1 | 681.7 | 724.2 | 665.1 | 509 | 628.8 | 592.9 | 369.2 | 349.5 | 360.3 | 346.2 | 354.1 | 353.1 | 358.9 | 342.7
1775.2 | 1499.2 | 471.2 | 188.48 | 220.3223 | 362.7 | 412.7 | 334.8 | 337.3 | 451.1 | 60 | 18.3 | 111 | 7.6 | 245.6 | 18.1 | 810.3 | 804.3 | 715.5 | 815 | 699.6 | 649.7 | 572.2 | 663.9 | 720.3 | 662.6 | 508.4 | 615.6 | 595.3 | 369.1 | 349 | 359.9 | 346 | 354.2 | 352.9 | 358.7 | 342.8
1776.2 | 1500.2 | 470.7 | 188.28 | 220.0885 | 362.8 | 413.8 | 334.5 | 336.8 | 450 | 59.9 | 18.3 | 111 | 6.3 | 240.4 | 16.2 | 807.8 | 806.5 | 699.5 | 813.8 | 695.2 | 649 | 568.2 | 655.4 | 714.4 | 660.9 | 507.8 | 606.8 | 598.6 | 368.9 | 348.6 | 359.6 | 345.8 | 354.2 | 352.6 | 358.5 | 342.8
1777.2 | 1501.2 | 469.7 | 187.88 | 219.6209 | 363.1 | 415.9 | 334 | 336.7 | 450.4 | 59.9 | 18.3 | 111.1 | 6.6 | 249.4 | 14.7 | 805.6 | 807.6 | 684.7 | 811.9 | 691.5 | 648.7 | 568.7 | 647.8 | 711.9 | 660 | 507.2 | 596 | 600.7 | 368.9 | 348.3 | 359.3 | 345.6 | 354.2 | 352.9 | 358.4 | 342.8
1778.2 | 1502.2 | 469.3 | 187.72 | 219.4339 | 363.6 | 418.3 | 333.9 | 336.7 | 456.7 | 59.9 | 18.3 | 111.2 | 7.2 | 265.7 | 15.3 | 801.6 | 799.7 | 660.2 | 808.9 | 687.1 | 648.5 | 568.3 | 628.5 | 706.7 | 657.7 | 506.6 | 587.1 | 600.2 | 368.8 | 348.1 | 359 | 345.4 | 354.2 | 353.4 | 358.8 | 343.1
1779.2 | 1503.2 | 471 | 188.4 | 220.2287 | 364 | 421.2 | 334 | 337.1 | 463.3 | 59.9 | 18.3 | 111.3 | 8.2 | 255.9 | 15.9 | 797.5 | 790.2 | 648.7 | 804.4 | 684.5 | 647.6 | 565 | 610 | 697.3 | 655.1 | 505.9 | 579.9 | 597 | 368.7 | 347.9 | 358.9 | 345.2 | 354.3 | 353.8 | 359.4 | 343.3
1780.2 | 1504.2 | 471.6 | 188.64 | 220.5093 | 364.1 | 420.4 | 334.2 | 338 | 470.9 | 59.8 | 18.3 | 111.4 | 8.4 | 259.2 | 13.6 | 794.4 | 783.9 | 641.4 | 801.1 | 681.3 | 646.8 | 561.7 | 601.5 | 690.3 | 653.1 | 505.2 | 574.3 | 593.3 | 368.7 | 347.7 | 358.8 | 345.1 | 354.3 | 353.9 | 359.4 | 343.4
1781.2 | 1505.2 | 471.5 | 188.6 | 220.4625 | 364.1 | 416.6 | 334.4 | 339 | 469.9 | 59.8 | 18.3 | 111.5 | 8.8 | 254.5 | 15.7 | 792.3 | 787.6 | 644.1 | 798.5 | 680 | 645.6 | 558.6 | 601.4 | 687.5 | 652.1 | 504.6 | 571.5 | 589.8 | 368.6 | 347.6 | 358.8 | 345 | 354.3 | 354 | 359.7 | 343.4
1782.2 | 1506.2 | 470.8 | 188.32 | 220.1352 | 364.2 | 413.6 | 334.9 | 339.5 | 469.2 | 59.9 | 18.3 | 111.6 | 8.7 | 246.2 | 15.9 | 790.1 | 788.4 | 654.1 | 795.4 | 679.4 | 644.8 | 558.8 | 600.1 | 686.6 | 651.7 | 504 | 569.4 | 587.3 | 368.5 | 347.5 | 359 | 344.9 | 354.3 | 354.5 | 360 | 343.6
1783.2 | 1507.2 | 470.9 | 188.36 | 220.182 | 363.9 | 412.5 | 335.2 | 339.9 | 471.5 | 60 | 18.3 | 111.7 | 8.3 | 240.3 | 16.8 | 789.7 | 788.3 | 669.2 | 793.8 | 682 | 644.5 | 561 | 604.5 | 688.8 | 651.6 | 503.4 | 567.9 | 587.1 | 368.3 | 347.4 | 359 | 344.8 | 354.4 | 354.7 | 359.9 | 343.6
1784.2 | 1508.2 | 469.5 | 187.8 | 219.5274 | 363.6 | 413.5 | 335.4 | 339.8 | 470.6 | 60.1 | 18.3 | 111.8 | 10.5 | 252.6 | 16.7 | 789.1 | 791.2 | 675.9 | 793.1 | 683.9 | 644.1 | 565.1 | 616.8 | 697.7 | 653.4 | 503.1 | 571 | 586.4 | 368.2 | 347.4 | 358.9 | 344.8 | 354.4 | 354.9 | 360.1 | 343.6
1785.2 | 1509.2 | 467.4 | 186.96 | 218.5455 | 363.8 | 411.5 | 335.5 | 339.5 | 472.8 | 60.1 | 18.3 | 111.7 | 9.4 | 238.6 | 15.9 | 788.8 | 795.3 | 673.1 | 792.7 | 681.6 | 644.2 | 566.8 | 627.1 | 703.3 | 653.9 | 502.7 | 572.8 | 585.6 | 368.2 | 347.5 | 358.9 | 344.7 | 354.5 | 355 | 360.3 | 343.6
1786.2 | 1510.2 | 466.9 | 186.76 | 218.3117 | 363.8 | 411.5 | 335.5 | 339.5 | 472.6 | 60.1 | 18.3 | 111.8 | 8.2 | 251.2 | 15 | 787.9 | 805.2 | 678.1 | 792.6 | 681 | 644.6 | 573.4 | 632.1 | 707.1 | 655 | 502.2 | 570.1 | 585.8 | 368.1 | 347.4 | 358.9 | 344.7 | 354.5 | 355.2 | 360.3 | 343.7
1787.2 | 1511.2 | 469.5 | 187.8 | 219.5274 | 363.5 | 412.5 | 335.5 | 339.5 | 471.4 | 60.2 | 18.3 | 111.8 | 6.1 | 236.9 | 14.3 | 787.3 | 808 | 684.9 | 792.4 | 682.2 | 644.2 | 578.9 | 641.6 | 713.4 | 657.2 | 501.9 | 576.2 | 584.9 | 368.1 | 347.4 | 359.1 | 344.6 | 354.5 | 355.3 | 360.4 | 343.7
1788.2 | 1512.2 | 469.3 | 187.72 | 219.4339 | 363.4 | 412.6 | 335.5 | 339.5 | 474.1 | 60.2 | 18.3 | 111.8 | 6.4 | 239.8 | 15.2 | 785.9 | 809.3 | 677.3 | 791.7 | 682.1 | 644 | 583.9 | 640.2 | 718.1 | 657.8 | 501.6 | 570.6 | 582.4 | 368 | 347.4 | 359.3 | 344.5 | 354.6 | 355.5 | 360.4 | 343.8
1789.2 | 1513.2 | 468.3 | 187.32 | 218.9663 | 363.5 | 413.5 | 335.8 | 339.6 | 478.7 | 60.2 | 18.3 | 111.7 | 5.8 | 236.6 | 16.4 | 783.1 | 802 | 665.9 | 789.4 | 684.1 | 643.7 | 583.4 | 626.3 | 714.4 | 657.6 | 501.1 | 562.7 | 579.3 | 368 | 347.4 | 359.4 | 344.4 | 354.6 | 355.7 | 360.7 | 343.8
1790.2 | 1514.2 | 468.3 | 187.32 | 218.9663 | 363.3 | 415.6 | 336.3 | 340.3 | 473.4 | 60.3 | 18.2 | 111.6 | 7.4 | 237.4 | 16.3 | 780.7 | 799.6 | 663.6 | 787.1 | 686 | 643.1 | 582.6 | 631.7 | 714.8 | 659.3 | 500.9 | 562.2 | 575.4 | 367.8 | 347.3 | 359.4 | 344.3 | 354.7 | 355.6 | 360.8 | 343.9
1791.2 | 1515.2 | 469.4 | 187.76 | 219.4806 | 363.1 | 414.7 | 336.2 | 340.7 | 475.6 | 60.3 | 18.3 | 111.7 | 8.6 | 242.1 | 14.2 | 777.4 | 788.4 | 656.2 | 783.8 | 687.1 | 642.8 | 580.8 | 623.5 | 708.6 | 658.7 | 500.8 | 557.4 | 570.8 | 367.7 | 347.3 | 359.4 | 344.2 | 354.7 | 355.7 | 360.7 | 344
1792.2 | 1516.2 | 470.1 | 188.04 | 219.8079 | 363.9 | 415.5 | 336.5 | 340.9 | 481.4 | 60.4 | 18.3 | 111.9 | 8.3 | 256.2 | 13.5 | 775.2 | 789.1 | 667.7 | 780.5 | 689.6 | 642.1 | 580 | 619.9 | 704.6 | 658.6 | 500.6 | 558.3 | 565.6 | 367.6 | 347.3 | 359.3 | 344.2 | 354.8 | 355.9 | 361.2 | 344.1
1793.2 | 1517.2 | 470.7 | 188.28 | 220.0885 | 364.1 | 420 | 336.5 | 341.2 | 481.9 | 60.4 | 18.2 | 111.9 | 7.1 | 256.6 | 11.6 | 775.3 | 794.9 | 683.6 | 778.4 | 696.4 | 642 | 580.4 | 631.5 | 707 | 661 | 500.9 | 568.5 | 560.5 | 367.5 | 347.3 | 359.3 | 344.1 | 354.8 | 355.9 | 361.3 | 344.1
1794.2 | 1518.2 | 467.2 | 186.88 | 218.452 | 363.8 | 418.7 | 336.5 | 341.2 | 482 | 60.4 | 18.3 | 111.8 | 7.1 | 260.2 | 11 | 775.9 | 801.5 | 697.8 | 776.5 | 699.2 | 641.9 | 580.8 | 640.2 | 710.1 | 662.7 | 501.1 | 576 | 556.2 | 367.4 | 347.2 | 359.4 | 344.1 | 354.8 | 355.9 | 361.3 | 344.1
1795.2 | 1519.2 | 468.6 | 187.44 | 219.1066 | 363.1 | 418.4 | 336.8 | 341 | 476.1 | 60.4 | 18.3 | 111.8 | 6.5 | 251.6 | 13.6 | 778.5 | 798.6 | 726 | 776.9 | 703.6 | 642.3 | 579.7 | 663.4 | 712.6 | 663.7 | 501.5 | 599.7 | 554 | 367.3 | 347.5 | 359.6 | 344.3 | 354.9 | 355.8 | 361.4 | 344
1796.2 | 1520.2 | 468.7 | 187.48 | 219.1533 | 362.9 | 419.4 | 336.8 | 340.9 | 484.2 | 60.5 | 18.3 | 111.8 | 5.6 | 235.9 | 12.3 | 777.2 | 778.8 | 726.6 | 774.9 | 703.8 | 642.8 | 575 | 664.6 | 704.7 | 662.2 | 502.4 | 616.1 | 551.7 | 367.4 | 348.2 | 360.3 | 344.6 | 354.9 | 355.6 | 361.4 | 343.9
1797.2 | 1521.2 | 468.6 | 187.44 | 219.1066 | 363.2 | 420.8 | 337.4 | 340.7 | 496.7 | 60.5 | 18.2 | 111.8 | 6.2 | 253.3 | 11.7 | 777.2 | 763.5 | 722.1 | 774.2 | 701.6 | 643.4 | 569.8 | 675.4 | 697.5 | 661.4 | 503.2 | 630 | 551.1 | 367.4 | 348.8 | 361 | 344.9 | 355 | 355.4 | 361.4 | 343.8
1798.2 | 1522.2 | 469.5 | 187.8 | 219.5274 | 363 | 419 | 338 | 340.3 | 503.9 | 60.5 | 18.2 | 111.8 | 6.3 | 246.4 | 13.4 | 779.4 | 755.5 | 731.7 | 774.1 | 702 | 644.3 | 567.1 | 693.3 | 694.9 | 662.6 | 503.8 | 644.7 | 551.9 | 367.6 | 349.5 | 361.7 | 345.1 | 355.1 | 355.2 | 361.5 | 343.7
1799.2 | 1523.2 | 471.3 | 188.52 | 220.369 | 362.5 | 414.7 | 338.1 | 340.5 | 506.6 | 60.5 | 18.2 | 111.8 | 6.4 | 244 | 11.5 | 782.6 | 760.1 | 753.4 | 776.3 | 705.6 | 645.3 | 571.2 | 709.9 | 701.3 | 665.1 | 504.4 | 656.1 | 552.9 | 367.6 | 349.9 | 362.3 | 345.2 | 355.1 | 354.9 | 361.4 | 343.7
1800.2 | 1524.2 | 472.2 | 188.88 | 220.7898 | 362.1 | 411.7 | 338.8 | 340.8 | 503.7 | 60.6 | 18.2 | 111.9 | 6.2 | 237.8 | 11.2 | 785.5 | 761.6 | 772.4 | 777.4 | 710.8 | 645.5 | 573.1 | 717.7 | 708.7 | 667.4 | 505.3 | 668.9 | 552.9 | 367.6 | 350.6 | 362.8 | 345.5 | 355.2 | 354.7 | 361.3 | 343.6
1801.2 | 1525.2 | 472.7 | 189.08 | 221.0236 | 361.9 | 408.9 | 339.5 | 340.8 | 502.8 | 60.7 | 18.2 | 111.9 | 7.4 | 241.6 | 11.3 | 785.3 | 754.5 | 772.3 | 778.8 | 709.9 | 646.2 | 569.1 | 724.3 | 705.4 | 666.5 | 506.1 | 676.9 | 552.9 | 367.8 | 351.7 | 363.8 | 345.8 | 355.2 | 354.4 | 361.2 | 343.5
1802.2 | 1526.2 | 469.9 | 187.96 | 219.7144 | 361.9 | 407.8 | 340.3 | 340.7 | 504.6 | 60.8 | 18.2 | 111.8 | 7.2 | 236.6 | 11.4 | 786.6 | 745.6 | 775.9 | 779.4 | 710.7 | 646.9 | 564.1 | 725.9 | 698.9 | 665.3 | 506.6 | 683.6 | 552.7 | 367.9 | 352.6 | 364.7 | 346 | 355.3 | 354.1 | 361.1 | 343.4
1803.2 | 1527.2 | 470.8 | 188.32 | 220.1352 | 361.9 | 410 | 341.3 | 340.7 | 503.2 | 60.9 | 18.2 | 111.6 | 7.5 | 268.6 | 9.6 | 788.2 | 742 | 774.1 | 780.7 | 711.1 | 647.6 | 562.9 | 735.8 | 699.3 | 665.7 | 507.2 | 691.1 | 555.1 | 368 | 353.2 | 365.2 | 346 | 355.4 | 353.8 | 361.1 | 343.4
1804.2 | 1528.2 | 470.6 | 188.24 | 220.0417 | 361.6 | 408.9 | 341.9 | 340.9 | 502.9 | 61 | 18.3 | 111.6 | 7.1 | 243.3 | 8.6 | 788.5 | 736.7 | 760.4 | 782.6 | 708.9 | 647.8 | 559.9 | 727.9 | 695.3 | 663.9 | 507.5 | 690.1 | 557.9 | 368.1 | 353.5 | 365.5 | 346.2 | 355.4 | 353.6 | 361.1 | 343.3
1805.2 | 1529.2 | 469.6 | 187.84 | 219.5741 | 361.5 | 406 | 342.1 | 341 | 504.8 | 61.1 | 18.2 | 111.6 | 5.3 | 257.1 | 9.5 | 790.9 | 740.1 | 761.9 | 784.5 | 708 | 647.8 | 560 | 733.7 | 696.1 | 664 | 507.8 | 691.2 | 561.4 | 368.2 | 353.9 | 366.1 | 346.3 | 355.5 | 353.3 | 361.1 | 343.2
1806.2 | 1530.2 | 469.4 | 187.76 | 219.4806 | 361.2 | 406.2 | 342.4 | 341.4 | 503.9 | 61.1 | 18.2 | 111.5 | 4.5 | 238.3 | 8.4 | 794 | 749.1 | 771.5 | 787.1 | 711.4 | 648.4 | 564.5 | 746.4 | 699.4 | 666 | 508.2 | 702.3 | 564.2 | 368.3 | 354 | 366.8 | 346.1 | 355.5 | 353 | 361.1 | 343.1
1807.2 | 1531.2 | 470.9 | 188.36 | 220.182 | 361.1 | 404.5 | 342.6 | 341.7 | 504.9 | 61.1 | 18.2 | 111.3 | 6.1 | 250.1 | 8.4 | 797.2 | 763.4 | 768.6 | 790.9 | 713 | 648.9 | 575.6 | 748.2 | 714.8 | 670.7 | 508.8 | 701.6 | 567 | 368.3 | 354 | 366.9 | 345.9 | 355.6 | 352.9 | 361.1 | 343.1
1808.2 | 1532.2 | 470.8 | 188.32 | 220.1352 | 361.2 | 403 | 342.6 | 341.6 | 503.5 | 61.2 | 18.2 | 111.2 | 5.7 | 237.7 | 8 | 799.3 | 775 | 779.3 | 794.2 | 716.3 | 650.2 | 585.7 | 752.1 | 728.8 | 674.5 | 509.1 | 700.9 | 568.7 | 368.4 | 354 | 366.9 | 345.8 | 355.6 | 352.7 | 361.1 | 343.1
1809.2 | 1533.2 | 470.3 | 188.12 | 219.9014 | 361.4 | 402.5 | 342.5 | 341.4 | 500.4 | 61.2 | 18.2 | 111.2 | 6.4 | 252.7 | 7.5 | 802.4 | 786.1 | 775.4 | 797.3 | 719.2 | 651.2 | 592.3 | 752.2 | 739.5 | 677.8 | 509.6 | 701.8 | 570.2 | 368.4 | 354 | 367.2 | 345.6 | 355.7 | 352.5 | 361.1 | 343
1810.2 | 1534.2 | 471 | 188.4 | 220.2287 | 361.6 | 404.5 | 342.2 | 341.3 | 503.1 | 61.2 | 18.2 | 111.1 | 6.5 | 246.4 | 7.8 | 802.2 | 790.2 | 775.9 | 799.4 | 722.8 | 651.4 | 596 | 730.3 | 741.1 | 677.8 | 509.7 | 686.6 | 569.7 | 368.4 | 353.8 | 367.2 | 345.4 | 355.7 | 352.6 | 361 | 343.1
1811.2 | 1535.2 | 470.6 | 188.24 | 220.0417 | 361.6 | 408.8 | 342.1 | 341.5 | 501.3 | 61.3 | 18.2 | 111.1 | 6.9 | 248.1 | 10.1 | 801.9 | 791.7 | 773.1 | 800.1 | 724.8 | 651.4 | 599.5 | 717.6 | 742.8 | 679.3 | 509.9 | 674.1 | 567.4 | 368.3 | 353.3 | 367 | 345.2 | 355.8 | 352.6 | 361.1 | 343.2
1812.2 | 1536.2 | 470.4 | 188.16 | 219.9482 | 361.5 | 410 | 341.8 | 341.5 | 500.6 | 61.4 | 18.2 | 111.1 | 6.6 | 252.2 | 12 | 803.4 | 791.7 | 775.2 | 801.2 | 727.9 | 651.6 | 597.7 | 711.9 | 739.4 | 679.6 | 510 | 674.2 | 565.5 | 368.3 | 353 | 366.9 | 345 | 355.8 | 352.6 | 361.1 | 343.2
1813.2 | 1537.2 | 468.8 | 187.52 | 219.2001 | 361.4 | 411.8 | 341.6 | 341.2 | 492.8 | 61.5 | 18.2 | 111.2 | 6.1 | 269 | 9 | 803.6 | 789.2 | 775.7 | 802.1 | 728.1 | 651.9 | 594.2 | 703.6 | 733.7 | 677.7 | 510 | 669.7 | 563.3 | 368.3 | 352.6 | 366.7 | 345 | 355.9 | 352.5 | 361.1 | 343.2
1814.2 | 1538.2 | 469.5 | 187.8 | 219.5274 | 361.1 | 412.5 | 341.4 | 340.9 | 486.3 | 61.6 | 18.2 | 111.2 | 5 | 247.2 | 9.7 | 803.6 | 783.4 | 776.2 | 802.3 | 727.4 | 651.7 | 589.9 | 698.7 | 728.8 | 676.9 | 510.1 | 668.4 | 561.7 | 368.2 | 352.4 | 366.5 | 345.1 | 356 | 352.5 | 360.8 | 343.2
1815.2 | 1539.2 | 469.5 | 187.8 | 219.5274 | 361 | 413.6 | 341 | 340.6 | 479 | 61.7 | 18.2 | 111.2 | 5.5 | 239 | 10.6 | 804.3 | 781.7 | 776.9 | 802.7 | 725.4 | 652.3 | 587.3 | 694.1 | 724.7 | 677.3 | 510.1 | 668.7 | 561.8 | 368.2 | 352.5 | 366.2 | 345.2 | 356 | 352.5 | 360.5 | 343.2
1816.2 | 1540.2 | 469.4 | 187.76 | 219.4806 | 360.8 | 414.2 | 340.9 | 340 | 473.5 | 61.8 | 18.2 | 111.2 | 4.7 | 258.8 | 10.5 | 805.6 | 787.4 | 777.2 | 803.1 | 724.9 | 653 | 586.3 | 701.7 | 725 | 678.3 | 510.1 | 666.3 | 564.2 | 368.2 | 352.2 | 365.9 | 345.2 | 356 | 352.6 | 360.2 | 343.2
1817.2 | 1541.2 | 469.1 | 187.64 | 219.3403 | 360.9 | 416.2 | 340.7 | 339.7 | 472.9 | 61.8 | 18.2 | 111.4 | 5.9 | 244.4 | 10.3 | 806.4 | 792.3 | 775.8 | 803 | 725.6 | 653.6 | 586.1 | 705.9 | 728.4 | 678.1 | 510 | 663.4 | 567.5 | 368.2 | 352.2 | 365.6 | 345.2 | 356.1 | 352.3 | 359.8 | 343.1
1818.2 | 1542.2 | 470.4 | 188.16 | 219.9482 | 360.9 | 418.1 | 340.4 | 339.4 | 474.2 | 61.8 | 18.2 | 111.6 | 5.7 | 255 | 10.7 | 808.8 | 789.6 | 780 | 803.7 | 726.4 | 653.6 | 582.1 | 707.2 | 723.8 | 677.9 | 509.9 | 669.5 | 569.6 | 368.1 | 352.4 | 365.3 | 345.3 | 356.2 | 352 | 359.4 | 343.1
1819.2 | 1543.2 | 469.4 | 187.76 | 219.4806 | 360.9 | 419 | 339.8 | 338.7 | 475.8 | 61.8 | 18.2 | 111.6 | 5.2 | 256.9 | 10.9 | 811 | 783.8 | 773.9 | 804.9 | 725.8 | 654.3 | 580 | 712.2 | 721.9 | 677.6 | 509.9 | 676.5 | 570.7 | 368.2 | 352.6 | 365.1 | 345.5 | 356.2 | 351.6 | 359.1 | 343
1820.2 | 1544.2 | 470 | 188 | 219.7612 | 361 | 417 | 339.4 | 338.4 | 481.7 | 61.8 | 18.2 | 111.6 | 4.9 | 249.4 | 11.3 | 811.9 | 773.7 | 768 | 806.2 | 724.9 | 655 | 575.9 | 710.9 | 715.6 | 675.7 | 509.9 | 681.8 | 571.3 | 368.3 | 353.1 | 365.3 | 345.7 | 356.2 | 351.4 | 358.8 | 342.8
1821.2 | 1545.2 | 469.5 | 187.8 | 219.5274 | 360.9 | 417.8 | 338.8 | 338.3 | 485.2 | 61.8 | 18.2 | 111.6 | 5.3 | 254.6 | 11.3 | 814.6 | 778.6 | 774.8 | 808.1 | 726.4 | 655.5 | 577.5 | 722.6 | 719.7 | 677.9 | 510.1 | 689.6 | 571.6 | 368.3 | 353.3 | 365.5 | 345.8 | 356.2 | 351.1 | 358.7 | 342.7
1822.2 | 1546.2 | 469.8 | 187.92 | 219.6677 | 360.8 | 415.1 | 338.7 | 338.4 | 485.8 | 61.7 | 18.2 | 111.6 | 5.6 | 238.4 | 11.4 | 817.2 | 784.6 | 784.8 | 810.7 | 730.3 | 656.7 | 588.1 | 730.8 | 731 | 680.1 | 510.1 | 691.9 | 571.4 | 368.3 | 353.4 | 365.6 | 345.6 | 356.3 | 350.9 | 358.4 | 342.7
1823.2 | 1547.2 | 470 | 188 | 219.7612 | 360.7 | 409.5 | 338.4 | 338.4 | 486.8 | 61.6 | 18.2 | 111.6 | 5.8 | 252.7 | 9.7 | 819 | 787.5 | 795.5 | 812.7 | 735 | 657.2 | 591.9 | 733.9 | 735.7 | 682.3 | 510.3 | 697.4 | 570.4 | 368.2 | 353.4 | 365.5 | 345.6 | 356.3 | 350.8 | 358.1 | 342.7
1824.2 | 1548.2 | 470.3 | 188.12 | 219.9014 | 360.3 | 406.6 | 338.3 | 338 | 483.2 | 61.6 | 18.2 | 111.7 | 6.1 | 225 | 8.5 | 821.2 | 787 | 800.4 | 815.4 | 737.3 | 658.1 | 592 | 738.8 | 738.6 | 685 | 510.8 | 699.7 | 571.1 | 368.2 | 353.4 | 365.6 | 345.5 | 356.3 | 350.6 | 357.9 | 342.7
1825.2 | 1549.2 | 470.7 | 188.28 | 220.0885 | 359.6 | 407.3 | 338.3 | 338.1 | 483.4 | 61.6 | 18.2 | 111.7 | 6 | 257.3 | 9.3 | 823.4 | 787.9 | 795 | 818.4 | 737.5 | 659.3 | 589.9 | 748.2 | 738.2 | 686.2 | 511.2 | 707.7 | 571.5 | 368.3 | 353.6 | 365.8 | 345.5 | 356.3 | 350.4 | 357.6 | 342.6
1826.2 | 1550.2 | 470.5 | 188.2 | 219.995 | 359 | 408.5 | 338 | 338.1 | 484.6 | 61.7 | 18.2 | 111.7 | 6.2 | 252.4 | 11.3 | 826.2 | 787 | 800.9 | 821.2 | 739.6 | 660.9 | 591.4 | 754.8 | 742.5 | 687.5 | 511.8 | 716.6 | 572.6 | 368.3 | 353.5 | 365.6 | 345.5 | 356.3 | 350.2 | 357.5 | 342.5
1827.2 | 1551.2 | 470.3 | 188.12 | 219.9014 | 358.7 | 410.5 | 338.1 | 338.2 | 488.8 | 61.7 | 18.2 | 111.6 | 8.2 | 253.4 | 13.6 | 828.3 | 787.3 | 808.1 | 823.7 | 741.9 | 662.4 | 595.8 | 758 | 745.4 | 689.4 | 512.4 | 721.6 | 574.9 | 368.3 | 353.5 | 365.7 | 345.5 | 356.4 | 350 | 357.7 | 342.4
1828.2 | 1552.2 | 470.4 | 188.16 | 219.9482 | 358.5 | 411.6 | 338.2 | 338 | 488.1 | 61.7 | 18.2 | 111.5 | 10.9 | 238.5 | 12.2 | 829.7 | 787.7 | 820 | 825.2 | 744.9 | 662.9 | 596 | 754.1 | 744.1 | 691.1 | 512.9 | 725.3 | 575.8 | 368.4 | 353.4 | 365.7 | 345.5 | 356.4 | 349.9 | 357.7 | 342.5
1829.2 | 1553.2 | 470.9 | 188.36 | 220.182 | 358.5 | 411.9 | 338.3 | 338.2 | 485.9 | 61.8 | 18.2 | 111.5 | 10 | 253.7 | 11.2 | 830.7 | 780.8 | 811.1 | 826.6 | 743.8 | 663.5 | 593.1 | 749.4 | 739.1 | 690.5 | 513.6 | 727.4 | 578.6 | 368.4 | 353.6 | 365.9 | 345.7 | 356.4 | 349.7 | 357.7 | 342.4
1830.2 | 1554.2 | 470.5 | 188.2 | 219.995 | 358.7 | 412.8 | 338.4 | 338.1 | 489.8 | 61.8 | 18.2 | 111.4 | 9.4 | 241.5 | 14.5 | 830.8 | 770.2 | 800.2 | 827.7 | 740.6 | 664.1 | 586.8 | 744.8 | 730.5 | 688 | 514 | 728.5 | 582.9 | 368.5 | 354 | 366.2 | 345.9 | 356.4 | 349.4 | 357.7 | 342.3
1831.2 | 1555.2 | 470.4 | 188.16 | 219.9482 | 358.6 | 412.9 | 339.2 | 338.3 | 490 | 61.8 | 18.2 | 111.1 | 8.4 | 235.7 | 17.6 | 833.1 | 768.3 | 808.4 | 829.5 | 742.5 | 665.1 | 585.1 | 753.5 | 730.6 | 688.1 | 514.3 | 730.9 | 588.4 | 368.6 | 353.9 | 366.2 | 345.9 | 356.4 | 349.2 | 357.8 | 342.2
1832.2 | 1556.2 | 470 | 188 | 219.7612 | 358.5 | 408.9 | 340.1 | 339.2 | 489.7 | 61.7 | 18.2 | 111 | 7.7 | 241.1 | 19.7 | 834.9 | 772 | 810.9 | 832.6 | 743.9 | 665.4 | 586.3 | 755.2 | 737 | 690.5 | 514.7 | 728.6 | 592.1 | 368.6 | 353.9 | 366.3 | 345.8 | 356.4 | 349.1 | 357.7 | 342.2
1833.2 | 1557.2 | 470.9 | 188.36 | 220.182 | 358.4 | 406.7 | 340 | 339.4 | 485.5 | 61.7 | 18.2 | 110.9 | 7.2 | 240.1 | 21.2 | 836.6 | 775.7 | 810.1 | 835.8 | 743.6 | 665.5 | 585.2 | 754.5 | 739 | 689.1 | 515 | 725 | 595.3 | 368.6 | 353.9 | 366.4 | 345.7 | 356.5 | 349 | 357.5 | 342.2
1834.2 | 1558.2 | 470.3 | 188.12 | 219.9014 | 358.3 | 404.6 | 339.7 | 339.3 | 479.6 | 61.7 | 18.2 | 111 | 9 | 256.7 | 20.7 | 837.5 | 777.2 | 796.2 | 838.6 | 741.1 | 666.1 | 582.5 | 750.8 | 735.7 | 687.1 | 515.2 | 717.8 | 598 | 368.6 | 353.9 | 366.5 | 345.6 | 356.5 | 348.8 | 357.3 | 342.2
1835.2 | 1559.2 | 468.9 | 187.56 | 219.2468 | 358 | 406 | 339.2 | 339.1 | 475.3 | 61.7 | 18.2 | 110.9 | 8.8 | 249.1 | 18.1 | 836.7 | 777.6 | 774.3 | 840.3 | 738.7 | 665.6 | 579.5 | 729.2 | 732.3 | 684.7 | 515 | 697.9 | 600.4 | 368.5 | 353.7 | 366.2 | 345.5 | 356.5 | 348.8 | 357 | 342.3
1836.2 | 1560.2 | 471.4 | 188.56 | 220.4158 | 357.8 | 409.9 | 339.1 | 339 | 474.8 | 61.7 | 18.2 | 110.8 | 9.1 | 248.2 | 15.5 | 835 | 777.6 | 764.6 | 840.7 | 736.8 | 665.9 | 578.2 | 714.2 | 728.7 | 684 | 514.7 | 679.5 | 603.1 | 368.5 | 353.3 | 365.8 | 345.3 | 356.5 | 348.8 | 356.9 | 342.3
1837.2 | 1561.2 | 468.8 | 187.52 | 219.2001 | 357.5 | 411 | 338.9 | 338.9 | 476.1 | 61.6 | 18.2 | 110.8 | 9.6 | 238.7 | 16 | 834.2 | 781.1 | 752.4 | 840.5 | 734.4 | 666.3 | 578.5 | 700.8 | 729.2 | 684 | 514.4 | 667.8 | 603.2 | 368.4 | 352.9 | 365.4 | 345.1 | 356.5 | 348.7 | 356.8 | 342.3
1838.2 | 1562.2 | 469.8 | 187.92 | 219.6677 | 357.2 | 411.1 | 338.7 | 338.8 | 471.9 | 61.7 | 18.2 | 110.7 | 10 | 234.2 | 17.5 | 835 | 778.2 | 764.9 | 840.4 | 735.7 | 666.3 | 576.6 | 701.2 | 728.9 | 683.3 | 514.1 | 677.2 | 602.9 | 368.4 | 352.8 | 365 | 345.1 | 356.5 | 348.5 | 356.7 | 342.3
1839.2 | 1563.2 | 470.7 | 188.28 | 220.0885 | 357.1 | 410.3 | 338.7 | 338.6 | 469.4 | 61.7 | 18.2 | 110.8 | 10 | 243.5 | 16.2 | 834.9 | 780.1 | 766.4 | 841.1 | 735.4 | 666.7 | 574.6 | 712.7 | 728.6 | 682.8 | 513.9 | 676.4 | 605.4 | 368.4 | 352.7 | 364.7 | 345.2 | 356.5 | 348.2 | 356.3 | 342.2
1840.2 | 1564.2 | 470.7 | 188.28 | 220.0885 | 357.1 | 411.2 | 338.7 | 338 | 463.7 | 61.7 | 18.2 | 111 | 9.5 | 249.3 | 14.5 | 834.4 | 784.5 | 752.1 | 841.7 | 731.3 | 667 | 573.5 | 709.4 | 728.7 | 682 | 513.6 | 665.9 | 609.6 | 368.3 | 352.4 | 364.3 | 345.1 | 356.5 | 348 | 356.5 | 342.1
1841.2 | 1565.2 | 470.7 | 188.28 | 220.0885 | 357.3 | 413.1 | 339.1 | 337.4 | 458.3 | 61.7 | 18.2 | 111.1 | 9.8 | 249.1 | 17.7 | 834.5 | 783.2 | 755.2 | 842.2 | 730.5 | 666.7 | 570.7 | 695.6 | 726.3 | 679.5 | 513.1 | 657.6 | 613.7 | 368.3 | 352.1 | 363.9 | 345 | 356.5 | 348 | 356.6 | 342.1
1842.2 | 1566.2 | 471.2 | 188.48 | 220.3223 | 357.3 | 415.9 | 339.1 | 336.8 | 455.7 | 61.6 | 18.2 | 111.2 | 9 | 251.2 | 18.1 | 835.1 | 785.7 | 766.5 | 843.5 | 732.5 | 666.9 | 572.4 | 703.8 | 730.3 | 680.2 | 512.6 | 658.7 | 618.4 | 368.2 | 352 | 363.4 | 345 | 356.5 | 347.9 | 356.2 | 342.1
1843.2 | 1567.2 | 469 | 187.6 | 219.2936 | 357.4 | 416.9 | 338.9 | 336.3 | 456.5 | 61.6 | 18.2 | 111.1 | 7.6 | 250.3 | 22.3 | 836.2 | 788.2 | 771.9 | 844.9 | 733.2 | 667.3 | 576.8 | 714.1 | 738.4 | 682.3 | 512.2 | 662.1 | 621 | 368.2 | 352 | 363.1 | 345 | 356.5 | 347.8 | 355.9 | 342
1844.2 | 1568.2 | 468.9 | 187.56 | 219.2468 | 357.5 | 417.4 | 338.4 | 335.7 | 456.4 | 61.6 | 18.2 | 111 | 7.8 | 252.2 | 22.8 | 836.4 | 789.2 | 771.5 | 846.3 | 732.6 | 667.8 | 580.2 | 711.3 | 740.8 | 682.1 | 511.8 | 662.9 | 621.6 | 368.1 | 351.7 | 362.8 | 344.9 | 356.5 | 347.6 | 355.6 | 342
1845.2 | 1569.2 | 469.2 | 187.68 | 219.3871 | 357.7 | 417.8 | 337.8 | 335.3 | 457.2 | 61.6 | 18.2 | 110.9 | 8.1 | 255.6 | 21.7 | 836.4 | 785.3 | 786.4 | 846.9 | 734.6 | 668 | 577.2 | 708.2 | 736.5 | 681.5 | 511.4 | 675.7 | 620.4 | 368.1 | 351.5 | 362.5 | 344.9 | 356.5 | 347.5 | 355.4 | 341.9
1846.2 | 1570.2 | 469.2 | 187.68 | 219.3871 | 357.9 | 418.8 | 337.9 | 335.3 | 458.4 | 61.6 | 18.2 | 111 | 7.6 | 257 | 20.2 | 835.7 | 785.8 | 791.5 | 847.1 | 737 | 668.3 | 575.9 | 714.8 | 732.6 | 681.8 | 511.3 | 683.6 | 618.4 | 368 | 351.3 | 362.5 | 344.9 | 356.5 | 347.4 | 355.6 | 341.9
1847.2 | 1571.2 | 468.8 | 187.52 | 219.2001 | 358.1 | 419 | 337.6 | 335 | 462.3 | 61.6 | 18.2 | 110.9 | 7.7 | 247.8 | 20.1 | 834.8 | 785.1 | 800.2 | 846.6 | 740.8 | 668.5 | 575 | 720.7 | 729.1 | 681.8 | 511.1 | 691.2 | 614.2 | 368 | 351.2 | 362.4 | 344.9 | 356.5 | 347.1 | 355.3 | 341.8
1848.2 | 1572.2 | 468 | 187.2 | 218.826 | 357.9 | 418 | 337.3 | 334.7 | 463.6 | 61.6 | 18.2 | 110.7 | 9.1 | 250 | 17.6 | 834.8 | 782.5 | 807 | 846.5 | 744.6 | 668.7 | 577 | 728.2 | 729.5 | 682.7 | 511 | 703 | 610.1 | 368 | 351.2 | 362.4 | 345 | 356.5 | 346.8 | 355 | 341.7
1849.2 | 1573.2 | 469.3 | 187.72 | 219.4339 | 357.5 | 418.5 | 337.5 | 334.3 | 468.5 | 61.5 | 18.2 | 110.6 | 10.2 | 252.9 | 17.8 | 835.7 | 773.3 | 803.6 | 846.4 | 745.4 | 669.3 | 573.2 | 736.1 | 723.2 | 681.3 | 511.2 | 713.1 | 607.1 | 368 | 351.4 | 362.5 | 345.1 | 356.5 | 346.7 | 354.8 | 341.6
1850.2 | 1574.2 | 468.5 | 187.4 | 219.0598 | 357.1 | 419.7 | 337.7 | 334.1 | 475.7 | 61.4 | 18.2 | 110.7 | 9.3 | 247.8 | 17.5 | 836.7 | 769.6 | 800.5 | 846.2 | 745.2 | 669.8 | 570.2 | 741 | 717.8 | 680.1 | 511.4 | 718 | 605.7 | 368.1 | 351.7 | 362.7 | 345.3 | 356.5 | 346.6 | 354.8 | 341.6
1851.2 | 1575.2 | 468.5 | 187.4 | 219.0598 | 357.1 | 421.1 | 338.3 | 334 | 487 | 61.5 | 18.2 | 110.7 | 10.3 | 245.8 | 15.8 | 838.3 | 772.5 | 802.4 | 847.6 | 745.4 | 670.6 | 571.1 | 748.7 | 721.4 | 680.3 | 511.6 | 723.5 | 604.7 | 368.2 | 352.1 | 363 | 345.5 | 356.5 | 346.6 | 354.8 | 341.5
1852.2 | 1576.2 | 470.2 | 188.08 | 219.8547 | 356.9 | 420.3 | 338.7 | 334.6 | 489.9 | 61.4 | 18.2 | 110.7 | 11.6 | 262.9 | 12.6 | 839.6 | 774.4 | 802.4 | 849.1 | 746.1 | 670.7 | 572 | 749.9 | 726.2 | 681.1 | 511.6 | 722.6 | 603.4 | 368.2 | 352.3 | 363.4 | 345.6 | 356.5 | 346.5 | 354.8 | 341.5
1853.2 | 1577.2 | 470.6 | 188.24 | 220.0417 | 356.5 | 418.1 | 339.2 | 335.3 | 485.8 | 61.4 | 18.2 | 110.6 | 10.1 | 231.3 | 12.3 | 839.3 | 780.6 | 794.2 | 850.2 | 745.4 | 670.6 | 575.8 | 735 | 732.6 | 681.4 | 511.5 | 711.2 | 602.8 | 368.1 | 352.4 | 363.7 | 345.7 | 356.5 | 346.6 | 354.8 | 341.6
1854.2 | 1578.2 | 470.6 | 188.24 | 220.0417 | 356.1 | 414 | 339.7 | 335.8 | 480.2 | 61.4 | 18.2 | 110.6 | 11.9 | 245.9 | 11.9 | 838.7 | 782.3 | 781 | 851.6 | 741.5 | 670 | 574.2 | 725.2 | 731.2 | 680 | 511.3 | 703.5 | 603.2 | 368.1 | 352.6 | 363.8 | 345.7 | 356.5 | 346.7 | 354.6 | 341.5
1855.2 | 1579.2 | 470.2 | 188.08 | 219.8547 | 356 | 414.9 | 339.5 | 335.6 | 476.6 | 61.4 | 18.2 | 110.6 | 10.3 | 235.3 | 9.4 | 838.6 | 784.2 | 767.1 | 852.7 | 738.4 | 670.3 | 573.1 | 726.5 | 730.6 | 679 | 511.1 | 698.6 | 605.4 | 368.2 | 352.8 | 363.7 | 345.7 | 356.5 | 346.7 | 354.7 | 341.5
1856.2 | 1580.2 | 470.4 | 188.16 | 219.9482 | 355.9 | 415.6 | 339.6 | 335.6 | 474.3 | 61.4 | 18.2 | 110.7 | 7.9 | 225.2 | 10.8 | 838.6 | 788.2 | 767.1 | 853.3 | 738.3 | 670 | 574.2 | 717 | 729.6 | 679.4 | 510.8 | 685.4 | 607.1 | 368.2 | 352.7 | 363.6 | 345.7 | 356.5 | 346.7 | 354.6 | 341.5
1857.2 | 1581.2 | 470.1 | 188.04 | 219.8079 | 355.9 | 415.1 | 339.7 | 335.5 | 468.4 | 61.5 | 18.2 | 110.7 | 8.2 | 240.2 | 13.2 | 838.6 | 787.5 | 753.3 | 854.6 | 737.2 | 670.2 | 574.7 | 715.5 | 727.9 | 680 | 510.7 | 682.2 | 609 | 368.2 | 352.8 | 363.5 | 345.7 | 356.5 | 346.7 | 354.6 | 341.5
1858.2 | 1582.2 | 470 | 188 | 219.7612 | 356.3 | 415 | 339.2 | 335 | 465.6 | 61.5 | 18.2 | 110.6 | 8.3 | 242.6 | 18.2 | 838.2 | 787.8 | 743.4 | 855.3 | 735.2 | 670 | 571.7 | 717.6 | 723.2 | 679.1 | 510.4 | 676 | 611.2 | 368.2 | 352.7 | 363.3 | 345.7 | 356.4 | 346.7 | 354.5 | 341.4
1859.2 | 1583.2 | 469.9 | 187.96 | 219.7144 | 356.1 | 415.8 | 339 | 334.6 | 463.8 | 61.5 | 18.2 | 110.5 | 9.8 | 240.4 | 19.1 | 838.8 | 790 | 738.2 | 855.5 | 735.3 | 669.5 | 568.9 | 722.6 | 719.1 | 679.1 | 510.1 | 674.7 | 614 | 368.2 | 352.6 | 363.1 | 345.6 | 356.4 | 346.6 | 354.3 | 341.3
1860.2 | 1584.2 | 470.2 | 188.08 | 219.8547 | 356 | 418.3 | 338.8 | 334.2 | 461.3 | 61.5 | 18.2 | 110.6 | 10.5 | 242.3 | 17 | 836.8 | 783.8 | 733.3 | 854.9 | 733.2 | 669 | 565.2 | 714.2 | 715.4 | 676.8 | 509.7 | 671 | 616 | 368.2 | 352.5 | 363 | 345.6 | 356.4 | 346.7 | 354.1 | 341.3
1861.2 | 1585.2 | 470.1 | 188.04 | 219.8079 | 355.9 | 419 | 338.4 | 333.7 | 458.4 | 61.5 | 18.2 | 110.6 | 9.9 | 247.4 | 14.8 | 834.1 | 778.3 | 726.2 | 852.7 | 729.2 | 668.2 | 560.3 | 700.9 | 706.8 | 674.2 | 509.3 | 660.6 | 616.8 | 368.1 | 352.3 | 362.9 | 345.5 | 356.4 | 346.5 | 353.9 | 341.2
1862.2 | 1586.2 | 469.6 | 187.84 | 219.5741 | 355.8 | 417.8 | 338.4 | 333.7 | 455.3 | 61.5 | 18.2 | 110.7 | 8.7 | 246.5 | 16.1 | 831.5 | 776.9 | 730.6 | 850 | 727.6 | 667.4 | 556.3 | 690.7 | 699.8 | 672.3 | 508.8 | 658.3 | 618.6 | 368.1 | 352 | 362.8 | 345.4 | 356.4 | 346.5 | 353.6 | 341.1
1863.2 | 1587.2 | 469.9 | 187.96 | 219.7144 | 355.3 | 415.3 | 338.5 | 333.6 | 454.1 | 61.5 | 18.2 | 110.8 | 7.1 | 229.1 | 19.7 | 830.5 | 785.1 | 732.7 | 848.8 | 726 | 666.5 | 557.6 | 692.3 | 703.3 | 671.9 | 508.3 | 650.9 | 621.8 | 368 | 351.6 | 362.4 | 345.4 | 356.4 | 346.4 | 353.3 | 341.1
1864.2 | 1588.2 | 469.7 | 187.88 | 219.6209 | 355 | 416.8 | 338.3 | 333.2 | 453.2 | 61.5 | 18.2 | 110.8 | 5.4 | 244.4 | 16.5 | 830.8 | 788.9 | 749.4 | 848.3 | 726.9 | 666.6 | 561.8 | 706.6 | 713.8 | 673.4 | 507.8 | 656.8 | 623.8 | 368 | 351.5 | 362 | 345.4 | 356.4 | 346.3 | 353 | 341
1865.2 | 1589.2 | 469.7 | 187.88 | 219.6209 | 355 | 416.7 | 337.8 | 332.9 | 454.5 | 61.5 | 18.2 | 110.8 | 5.3 | 237.3 | 18.5 | 830.4 | 793.5 | 750.9 | 848 | 725.9 | 667.2 | 567.8 | 715 | 720.8 | 674.1 | 507.4 | 657.9 | 624.1 | 367.9 | 351.3 | 361.6 | 345.4 | 356.4 | 346.2 | 352.8 | 340.9
1866.2 | 1590.2 | 469.5 | 187.8 | 219.5274 | 354.9 | 414.4 | 337.2 | 332.5 | 459.6 | 61.5 | 18.2 | 110.9 | 5.3 | 240.5 | 18.7 | 831.3 | 792.2 | 755.1 | 848.8 | 725 | 667.5 | 568.3 | 723.2 | 724.1 | 673.4 | 507.1 | 666.2 | 624.7 | 367.9 | 351.3 | 361.4 | 345.3 | 356.4 | 346.1 | 352.9 | 340.8
1867.2 | 1591.2 | 469.6 | 187.84 | 219.5741 | 354.7 | 413.5 | 336.6 | 332.3 | 463.6 | 61.4 | 18.2 | 111.1 | 7.5 | 250.2 | 17.3 | 831.5 | 784.7 | 745.2 | 848.9 | 723 | 667 | 563.8 | 718.5 | 717 | 671.6 | 506.7 | 670.1 | 624.6 | 367.9 | 351.4 | 361.3 | 345.4 | 356.3 | 345.9 | 352.7 | 340.7
1868.2 | 1592.2 | 472 | 188.8 | 220.6963 | 354.5 | 412.7 | 336.7 | 332.6 | 468.3 | 61.4 | 18.2 | 111.2 | 8 | 249.2 | 15.6 | 829.3 | 773.9 | 730.9 | 847.9 | 719.2 | 666.4 | 558.5 | 711.2 | 706.8 | 670.3 | 506.3 | 667.6 | 627.1 | 368 | 351.6 | 361.4 | 345.5 | 356.3 | 345.6 | 352.5 | 340.6
1869.2 | 1593.2 | 472.2 | 188.88 | 220.7898 | 354.5 | 412.4 | 337.2 | 332.6 | 473 | 61.3 | 18.2 | 111.2 | 8.8 | 246.6 | 15.2 | 826.9 | 765.1 | 725.4 | 846.4 | 717 | 665.7 | 552.3 | 696.5 | 696.4 | 667.5 | 505.8 | 662.8 | 630.9 | 368 | 351.6 | 361.5 | 345.6 | 356.3 | 345.5 | 352.5 | 340.6
1870.2 | 1594.2 | 473 | 189.2 | 221.1639 | 354.3 | 410.2 | 337.8 | 332.9 | 468.7 | 61.3 | 18.2 | 111.2 | 8.8 | 243.8 | 14.4 | 826.2 | 770.5 | 735.5 | 846.2 | 718.8 | 664.9 | 555.5 | 703.4 | 698.9 | 669.1 | 505.3 | 658.2 | 632.7 | 368 | 351.4 | 361.4 | 345.6 | 356.3 | 345.6 | 352.6 | 340.6
1871.2 | 1595.2 | 471.5 | 188.6 | 220.4625 | 354.2 | 409.1 | 337.6 | 333.4 | 467.6 | 61.3 | 18.2 | 111.2 | 8 | 249.6 | 12.1 | 825.9 | 776.5 | 742.2 | 846.5 | 719.1 | 664.7 | 560.8 | 699 | 703.6 | 669.8 | 504.9 | 655.8 | 632 | 367.9 | 351.5 | 361.4 | 345.5 | 356.3 | 345.8 | 353.1 | 340.6
1872.2 | 1596.2 | 470.7 | 188.28 | 220.0885 | 354 | 408.5 | 337.2 | 334 | 467.4 | 61.3 | 18.2 | 111.4 | 7.5 | 255.3 | 10 | 825.1 | 781.2 | 746.3 | 846.9 | 720.5 | 664.6 | 564.2 | 700.8 | 709 | 670.5 | 504.5 | 651.6 | 631 | 367.9 | 351.7 | 361.4 | 345.4 | 356.2 | 345.9 | 353.3 | 340.7
1873.2 | 1597.2 | 469.5 | 187.8 | 219.5274 | 353.8 | 409.2 | 337 | 334.6 | 466.3 | 61.3 | 18.2 | 111.4 | 7 | 250.9 | 10.3 | 823.2 | 778.9 | 746 | 846.3 | 720.2 | 664.1 | 566.1 | 693.3 | 708.9 | 670 | 504 | 647 | 628.9 | 367.8 | 351.5 | 361.5 | 345.2 | 356.2 | 346.1 | 353.5 | 340.8
1874.2 | 1598.2 | 469 | 187.6 | 219.2936 | 354 | 408 | 336.7 | 334.7 | 465.1 | 61.4 | 18.2 | 111.5 | 6.9 | 255.9 | 13.9 | 820.2 | 774.7 | 742.9 | 844.4 | 719.7 | 663.3 | 564.4 | 676.5 | 704.5 | 668.9 | 503.7 | 635.1 | 624.9 | 367.7 | 351.2 | 361.2 | 345 | 356.2 | 346.2 | 354 | 340.9
1875.2 | 1599.2 | 471.3 | 188.52 | 220.369 | 354.2 | 407.9 | 336.5 | 334.9 | 464.1 | 61.3 | 18.2 | 111.5 | 6.8 | 257.9 | 18 | 816.8 | 773 | 737.8 | 841.6 | 718.6 | 661.9 | 562.2 | 665.8 | 697.8 | 667.3 | 503.2 | 630.8 | 619.8 | 367.6 | 350.9 | 360.9 | 344.8 | 356.2 | 346.6 | 354.7 | 341
1876.2 | 1600.2 | 471.2 | 188.48 | 220.3223 | 354.2 | 408.9 | 336.4 | 335 | 465.4 | 61.2 | 18.2 | 111.4 | 6.7 | 250.9 | 18 | 813.9 | 773.6 | 726.6 | 838.8 | 718.6 | 661.2 | 564.3 | 658.9 | 700 | 668.8 | 502.9 | 623.8 | 615.2 | 367.5 | 350.7 | 360.7 | 344.6 | 356.2 | 347.1 | 355.2 | 341
1877.2 | 1601.2 | 471 | 188.4 | 220.2287 | 354.2 | 409.1 | 336.5 | 335.9 | 469.6 | 61.1 | 18.2 | 111.3 | 6.1 | 259.4 | 17.2 | 812.6 | 775.6 | 726.5 | 836.1 | 716.6 | 660.6 | 563.3 | 654.6 | 700.5 | 667.1 | 502.6 | 616.8 | 612.6 | 367.4 | 350.3 | 360.4 | 344.4 | 356.1 | 347.6 | 355.6 | 341.1
1878.2 | 1602.2 | 470.7 | 188.28 | 220.0885 | 354.3 | 409 | 336.3 | 336.3 | 466.6 | 61.1 | 18.2 | 111.3 | 5.6 | 252.2 | 16.6 | 811.3 | 782.5 | 717.1 | 833.8 | 712.4 | 659.7 | 568 | 647.7 | 705.5 | 666.8 | 502.2 | 609.9 | 611.5 | 367.3 | 350 | 360 | 344.2 | 356.1 | 347.9 | 355.9 | 341.2
1879.2 | 1603.2 | 469.1 | 187.64 | 219.3403 | 354.6 | 409.2 | 336.1 | 336.5 | 468.2 | 61.1 | 18.2 | 111.4 | 5.9 | 258.6 | 15.6 | 809.4 | 778.1 | 703.4 | 830.8 | 711 | 659.7 | 565.8 | 641.2 | 702.3 | 664.4 | 501.7 | 602.8 | 610.7 | 367.2 | 349.7 | 359.7 | 344.1 | 356.1 | 348.2 | 356 | 341.3
1880.2 | 1604.2 | 470.6 | 188.24 | 220.0417 | 354.7 | 410 | 336 | 336.6 | 466.5 | 61.2 | 18.2 | 111.4 | 6.5 | 263 | 14.1 | 806.2 | 777.6 | 685.2 | 827.5 | 706.9 | 658.9 | 566.4 | 638.6 | 698.7 | 663.7 | 501.2 | 596.7 | 608.7 | 367.1 | 349.3 | 359.5 | 344 | 356.1 | 348.8 | 356.2 | 341.4
1881.2 | 1605.2 | 470.1 | 188.04 | 219.8079 | 354.8 | 412.1 | 335.7 | 336.5 | 468.3 | 61.2 | 18.2 | 111.5 | 6 | 267.8 | 14.7 | 801.8 | 773.2 | 667.4 | 822.5 | 704.6 | 657.8 | 565.3 | 630.5 | 694.4 | 662.5 | 500.8 | 588 | 605 | 367 | 348.9 | 359.2 | 343.8 | 356.1 | 349.3 | 356.5 | 341.6
1882.2 | 1606.2 | 470.3 | 188.12 | 219.9014 | 355 | 413.6 | 335.4 | 336.8 | 468.1 | 61.1 | 18.2 | 111.4 | 5.9 | 275.3 | 17 | 797.8 | 769.5 | 656.6 | 817.1 | 703.9 | 657.2 | 565.1 | 621 | 689.9 | 662.3 | 500.3 | 580.6 | 600.1 | 366.9 | 348.6 | 359.2 | 343.7 | 356.1 | 350.4 | 357 | 341.8
1883.2 | 1607.2 | 470.3 | 188.12 | 219.9014 | 354.9 | 414.2 | 335.9 | 337.1 | 472.3 | 61.1 | 18.2 | 111.4 | 5.8 | 272.9 | 17.9 | 794.9 | 770.9 | 669.3 | 812.8 | 706.2 | 656.2 | 566.3 | 612 | 688.2 | 663 | 500 | 577.7 | 595.1 | 366.8 | 348.5 | 359.2 | 343.6 | 356.2 | 351.4 | 357.5 | 341.9
1884.2 | 1608.2 | 469.6 | 187.84 | 219.5741 | 354.8 | 414.3 | 336.2 | 337.6 | 473.9 | 61 | 18.2 | 111.4 | 6.2 | 281.7 | 17.1 | 793.4 | 772.4 | 694.3 | 809.2 | 708.9 | 655.4 | 567.4 | 613.2 | 689.8 | 663 | 500 | 580.4 | 589.9 | 366.7 | 348.3 | 359.3 | 343.6 | 356.2 | 351.6 | 357.9 | 342
1885.2 | 1609.2 | 469.9 | 187.96 | 219.7144 | 355 | 412.1 | 335.7 | 338.1 | 477.4 | 61 | 18.2 | 111.5 | 5.7 | 267.7 | 15.7 | 792.5 | 780.5 | 702.6 | 806.9 | 711.1 | 654.7 | 572.1 | 614.4 | 695.2 | 664.5 | 499.8 | 580.7 | 584.8 | 366.6 | 348.1 | 359.4 | 343.5 | 356.2 | 351.8 | 358.4 | 342
1886.2 | 1610.2 | 470.1 | 188.04 | 219.8079 | 355 | 412.5 | 335.5 | 338.4 | 480.9 | 61 | 18.2 | 111.7 | 6.2 | 276.5 | 14.1 | 791.5 | 785.4 | 715.7 | 805.2 | 712.6 | 654 | 576 | 620.5 | 702.1 | 665.5 | 499.7 | 579.8 | 580.7 | 366.5 | 348 | 359.4 | 343.5 | 356.2 | 351.9 | 358.6 | 342.1
1887.2 | 1611.2 | 470.1 | 188.04 | 219.8079 | 354.8 | 414.7 | 335.6 | 338.9 | 484.2 | 61 | 18.2 | 112 | 7.2 | 276.7 | 11.7 | 790.4 | 789.7 | 728.6 | 803.9 | 713.4 | 653.5 | 578.4 | 621.4 | 707.6 | 666.4 | 499.6 | 579.7 | 576.4 | 366.4 | 347.9 | 359.3 | 343.4 | 356.2 | 352.1 | 359 | 342.2
1888.2 | 1612.2 | 469.7 | 187.88 | 219.6209 | 354.4 | 414.9 | 335.7 | 339.4 | 489.8 | 61 | 18.2 | 112.1 | 8.1 | 259.7 | 10 | 789.4 | 788.5 | 735.2 | 802.7 | 716.5 | 652.9 | 578.3 | 617.1 | 708.7 | 667.3 | 499.4 | 578.4 | 572.2 | 366.3 | 347.7 | 359.1 | 343.5 | 356.2 | 352.1 | 359.2 | 342.2
1889.2 | 1613.2 | 470.7 | 188.28 | 220.0885 | 354.2 | 415.7 | 335.6 | 339.6 | 489.6 | 61 | 18.2 | 111.9 | 8.1 | 255.5 | 11.7 | 787.3 | 788.6 | 739.2 | 801.3 | 718.2 | 652.2 | 576.7 | 614.2 | 705.6 | 668 | 499.5 | 577.2 | 567.8 | 366.2 | 347.6 | 359.2 | 343.4 | 356.3 | 352.4 | 359.2 | 342.3
1890.2 | 1614.2 | 471.1 | 188.44 | 220.2755 | 353.8 | 414.4 | 336 | 340 | 484.6 | 61 | 18.2 | 111.8 | 7.1 | 248.8 | 14.8 | 786.7 | 782.7 | 755.8 | 800.1 | 721.1 | 651.5 | 574.8 | 621.9 | 700.1 | 667.5 | 499.5 | 589.7 | 564.3 | 366.1 | 347.5 | 359.4 | 343.3 | 356.3 | 352.7 | 359.4 | 342.4
1891.2 | 1615.2 | 470.8 | 188.32 | 220.1352 | 353.5 | 414.6 | 336.1 | 340.3 | 482.6 | 61 | 18.2 | 111.8 | 6.6 | 250.7 | 16.7 | 786.5 | 783.6 | 755.5 | 799.7 | 721.7 | 651.2 | 576.1 | 634.7 | 703.7 | 668.5 | 499.7 | 595.2 | 560.8 | 366 | 347.4 | 359.4 | 343.2 | 356.3 | 352.5 | 359.2 | 342.5
1892.2 | 1616.2 | 471 | 188.4 | 220.2287 | 353.4 | 417.4 | 335.9 | 340.6 | 484.8 | 60.9 | 18.2 | 111.6 | 6.4 | 249.3 | 16.8 | 786.3 | 785.7 | 748.8 | 799.7 | 719.1 | 651.3 | 580.3 | 644.5 | 711 | 668.6 | 499.7 | 595.5 | 558.6 | 366 | 347.2 | 359.4 | 343.2 | 356.4 | 352.6 | 359.2 | 342.5
1893.2 | 1617.2 | 471.8 | 188.72 | 220.6028 | 353.5 | 417.8 | 335.7 | 340.3 | 483.7 | 60.9 | 18.2 | 111.6 | 6.7 | 256.7 | 16.2 | 786.1 | 775.5 | 732.6 | 799.5 | 716 | 651.2 | 574.5 | 645.1 | 704.2 | 666.3 | 499.5 | 594.8 | 557.8 | 365.9 | 347.1 | 359.3 | 343.1 | 356.4 | 352.6 | 359.1 | 342.5
1894.2 | 1618.2 | 469.8 | 187.92 | 219.6677 | 353.3 | 416.8 | 335.6 | 340.1 | 477.6 | 60.9 | 18.2 | 111.5 | 6.7 | 257.3 | 17.1 | 785 | 773.8 | 722.9 | 798.9 | 713.2 | 651 | 572.9 | 652.4 | 696.8 | 666.1 | 499.3 | 590.4 | 558.9 | 365.8 | 346.9 | 359.1 | 343 | 356.4 | 352.4 | 359 | 342.5
1895.2 | 1619.2 | 468.4 | 187.36 | 219.013 | 353.2 | 418.2 | 335.4 | 339.9 | 472 | 61 | 18.2 | 111.4 | 7.8 | 258.2 | 16.3 | 785.9 | 777.4 | 737.2 | 799.1 | 714.9 | 650.6 | 573.7 | 659.7 | 696.2 | 666.7 | 499.2 | 592.7 | 561.4 | 365.7 | 346.7 | 358.9 | 342.9 | 356.5 | 352.3 | 358.7 | 342.5
1896.2 | 1620.2 | 469.3 | 187.72 | 219.4339 | 353.2 | 418.5 | 335.4 | 339.5 | 470.6 | 61 | 18.2 | 111.5 | 8.3 | 246.9 | 16.4 | 788.9 | 784 | 744.3 | 801 | 717 | 650.7 | 575 | 686.5 | 705.5 | 669.5 | 499.2 | 612.2 | 563.4 | 365.7 | 346.7 | 358.8 | 343 | 356.5 | 352.1 | 358.4 | 342.4
1897.2 | 1621.2 | 469.2 | 187.68 | 219.3871 | 353.1 | 418 | 335.2 | 338.9 | 471.1 | 61.1 | 18.2 | 111.5 | 8.3 | 251 | 18.3 | 792.3 | 791.1 | 767.1 | 804.4 | 718.9 | 650.5 | 581.5 | 713.7 | 713.1 | 672.6 | 499.5 | 632.9 | 564.6 | 365.7 | 346.7 | 358.7 | 343.1 | 356.5 | 351.8 | 357.9 | 342.4
1898.2 | 1622.2 | 469.4 | 187.76 | 219.4806 | 352.9 | 417.2 | 335.2 | 338.9 | 472.8 | 61.1 | 18.2 | 111.5 | 8.3 | 250.8 | 20.3 | 794.8 | 792.7 | 779.5 | 807.5 | 722.7 | 651.2 | 589.7 | 724.2 | 719.4 | 675.3 | 499.9 | 643.3 | 565.3 | 365.6 | 346.8 | 358.7 | 343.1 | 356.6 | 351.6 | 357.6 | 342.3
1899.2 | 1623.2 | 469.9 | 187.96 | 219.7144 | 352.6 | 416.1 | 335.2 | 338.7 | 471.2 | 61.1 | 18.2 | 111.6 | 8.1 | 249.6 | 20.1 | 796.1 | 793.4 | 789.7 | 809.6 | 726.6 | 651.2 | 588.5 | 731.7 | 718 | 676.2 | 500.3 | 658.1 | 564 | 365.6 | 347.1 | 358.8 | 343.4 | 356.6 | 351.4 | 357.5 | 342.3
1900.2 | 1624.2 | 470.7 | 188.28 | 220.0885 | 352.6 | 415.4 | 335.4 | 338.6 | 474.7 | 61.1 | 18.2 | 111.6 | 8.2 | 241.1 | 17.2 | 798.1 | 792.9 | 792.5 | 812.3 | 728.3 | 651.9 | 586.4 | 742.2 | 717.9 | 677.9 | 501 | 670.3 | 563.2 | 365.7 | 347.7 | 359 | 343.7 | 356.6 | 351.2 | 357.5 | 342.2
1901.2 | 1625.2 | 469.2 | 187.68 | 219.3871 | 352.5 | 414.8 | 335.6 | 338.8 | 478.3 | 61.1 | 18.2 | 111.6 | 8.4 | 255.9 | 15.6 | 800.6 | 798.1 | 791 | 816.5 | 728.9 | 653.3 | 594.7 | 757.2 | 727.2 | 682.4 | 501.7 | 676.5 | 563.3 | 365.7 | 347.9 | 359.2 | 343.7 | 356.6 | 350.8 | 357.4 | 342.1
1902.2 | 1626.2 | 468.8 | 187.52 | 219.2001 | 352.3 | 414 | 336.2 | 338.7 | 486.7 | 61.1 | 18.2 | 111.6 | 7.8 | 247.3 | 16.4 | 803.1 | 802.9 | 791.1 | 821.2 | 730.2 | 654.3 | 599.3 | 754.6 | 734.5 | 683.4 | 502.3 | 675.9 | 565.2 | 365.7 | 348.2 | 359.5 | 343.8 | 356.6 | 350.6 | 357.1 | 342
1903.2 | 1627.2 | 469 | 187.6 | 219.2936 | 352.3 | 411.4 | 336.3 | 338.2 | 487.7 | 61 | 18.2 | 111.5 | 7.7 | 255 | 16.4 | 805.2 | 804.9 | 802.6 | 825.2 | 732.6 | 655.8 | 606.3 | 769 | 743 | 687.1 | 502.9 | 685.4 | 568.6 | 365.7 | 348.5 | 359.8 | 344 | 356.7 | 350.4 | 357 | 342
1904.2 | 1628.2 | 469.2 | 187.68 | 219.3871 | 352.7 | 410.6 | 336.3 | 338.1 | 493.3 | 61 | 18.2 | 111.4 | 7.7 | 245.4 | 14.4 | 808.5 | 804.3 | 819.1 | 829 | 737.6 | 657.7 | 611.9 | 776.2 | 748.2 | 690.5 | 503.8 | 698.6 | 570.1 | 365.8 | 349 | 360.3 | 344 | 356.7 | 350.3 | 356.9 | 341.9
1905.2 | 1629.2 | 469 | 187.6 | 219.2936 | 352.8 | 409.6 | 337 | 338.2 | 493 | 61 | 18.2 | 111.3 | 6.5 | 259.2 | 14.5 | 810.7 | 797.1 | 829.2 | 832.3 | 739.8 | 658 | 607.5 | 768.5 | 744 | 691 | 504.9 | 704.6 | 570 | 365.8 | 349.5 | 360.5 | 344 | 356.7 | 350.2 | 356.8 | 341.9
1906.2 | 1630.2 | 471.7 | 188.68 | 220.556 | 352.7 | 410 | 337.7 | 338.4 | 484.9 | 61 | 18.2 | 111.3 | 6.7 | 259.9 | 15 | 811.5 | 789.5 | 830.2 | 834.1 | 740 | 658 | 600.8 | 751.3 | 737.1 | 689.4 | 506 | 708.2 | 568.8 | 365.8 | 349.8 | 360.6 | 343.9 | 356.7 | 350.1 | 356.6 | 341.8
1907.2 | 1631.2 | 472.4 | 188.96 | 220.8834 | 352.6 | 411.4 | 337.9 | 338.6 | 479.5 | 61 | 18.2 | 111.3 | 7 | 254.8 | 13.2 | 813.9 | 791.3 | 831.4 | 836.6 | 742.2 | 659.1 | 606.5 | 754.1 | 743.3 | 693.1 | 507.3 | 713.5 | 568.3 | 365.8 | 349.9 | 360.7 | 343.8 | 356.7 | 350 | 356.4 | 341.8
1908.2 | 1632.2 | 472.9 | 189.16 | 221.1171 | 352.4 | 410 | 337.6 | 338.5 | 481.9 | 60.9 | 18.2 | 111.3 | 7.3 | 257.1 | 14.3 | 816.6 | 790.3 | 838.9 | 839.5 | 744.2 | 660.5 | 609.3 | 761.9 | 746.8 | 694.7 | 508.5 | 717.6 | 569.1 | 365.9 | 350.1 | 360.8 | 344 | 356.7 | 349.8 | 356.2 | 341.8
1909.2 | 1633.2 | 472.2 | 188.88 | 220.7898 | 352.3 | 408.9 | 337.6 | 338.3 | 487.6 | 60.9 | 18.2 | 111.2 | 7.5 | 266.8 | 15.7 | 817.4 | 779.9 | 817 | 841.6 | 741.2 | 661.6 | 602.3 | 752.5 | 736.6 | 691.5 | 509.3 | 713.1 | 570.9 | 366 | 350.7 | 361.2 | 344.2 | 356.7 | 349.5 | 356.1 | 341.7
1910.2 | 1634.2 | 471.6 | 188.64 | 220.5093 | 352.5 | 412 | 338.3 | 338.2 | 500.1 | 60.9 | 18.2 | 111.3 | 8.2 | 269.2 | 17.2 | 816.6 | 765.6 | 807.8 | 841.5 | 739.1 | 662.7 | 594.2 | 746 | 721.8 | 688.1 | 510 | 714.1 | 570.6 | 366.2 | 351.6 | 361.9 | 344.6 | 356.7 | 349.2 | 356.1 | 341.5
1911.2 | 1635.2 | 469.8 | 187.92 | 219.6677 | 352.8 | 410.9 | 339.2 | 338.2 | 508.2 | 60.9 | 18.2 | 111.3 | 8.8 | 265.5 | 18.7 | 817.3 | 756.8 | 806.6 | 841.2 | 739.9 | 663.3 | 586.8 | 750.3 | 712.9 | 687.6 | 510.7 | 719.9 | 569.7 | 366.4 | 352.1 | 362.8 | 344.8 | 356.7 | 348.8 | 356.2 | 341.4
1912.2 | 1636.2 | 470.2 | 188.08 | 219.8547 | 352.9 | 409.8 | 340.3 | 338.7 | 504.3 | 60.9 | 18.2 | 111.3 | 7.8 | 263.2 | 16.3 | 819.2 | 760.5 | 816.4 | 842.2 | 741.8 | 663.2 | 582.7 | 752.4 | 713.7 | 687.7 | 511.4 | 721.5 | 569.3 | 366.5 | 352.2 | 363.2 | 344.7 | 356.7 | 348.5 | 356.2 | 341.4
1913.2 | 1637.2 | 470.6 | 188.24 | 220.0417 | 352.8 | 408.5 | 341.4 | 339.2 | 496.9 | 61 | 18.2 | 111.3 | 8.5 | 262.9 | 15.1 | 820 | 762.3 | 817.6 | 843.9 | 742.6 | 663.2 | 581.8 | 753.3 | 716.6 | 687.2 | 511.8 | 713.9 | 570.5 | 366.5 | 352.2 | 363.6 | 344.6 | 356.7 | 348.3 | 356.1 | 341.3
1914.2 | 1638.2 | 470.3 | 188.12 | 219.9014 | 352.9 | 405.2 | 341.7 | 339.3 | 489.4 | 61.1 | 18.2 | 111.2 | 8.6 | 259.4 | 16.5 | 819.5 | 755.8 | 810.7 | 844.7 | 740.7 | 663.2 | 576.5 | 746.3 | 709.8 | 685 | 512 | 709.8 | 574.9 | 366.6 | 352.4 | 363.9 | 344.5 | 356.7 | 348.2 | 356 | 341.4
1915.2 | 1639.2 | 470.3 | 188.12 | 219.9014 | 352.9 | 403.4 | 341.8 | 339.3 | 482.6 | 61.2 | 18.2 | 111.1 | 7.8 | 264.8 | 16 | 819.9 | 751.4 | 803.8 | 845 | 739.6 | 663.4 | 573.2 | 747.9 | 704.6 | 683.7 | 512.2 | 710.7 | 577.8 | 366.8 | 352.8 | 364.3 | 344.6 | 356.7 | 347.9 | 355.8 | 341.3
1916.2 | 1640.2 | 468.5 | 187.4 | 219.0598 | 353 | 405.8 | 342 | 339 | 483.3 | 61.2 | 18.2 | 110.8 | 6.1 | 257.2 | 12.9 | 820 | 747.5 | 802.8 | 844.5 | 738.6 | 663.8 | 569.4 | 746.7 | 700.2 | 681.1 | 512.3 | 709.2 | 579.2 | 366.9 | 353.2 | 364.7 | 344.8 | 356.7 | 347.7 | 355.5 | 341.2
1917.2 | 1641.2 | 468.7 | 187.48 | 219.1533 | 352.9 | 407.6 | 342 | 338.4 | 480.1 | 61.3 | 18.2 | 110.5 | 7.5 | 260.9 | 11.2 | 821 | 755.3 | 799 | 845.4 | 739 | 664.2 | 572 | 757.4 | 710.5 | 684.2 | 512.4 | 712.8 | 579.8 | 366.9 | 353.2 | 364.7 | 344.7 | 356.7 | 347.5 | 355.4 | 341.1
1918.2 | 1642.2 | 469.7 | 187.88 | 219.6209 | 352.9 | 406.1 | 342.5 | 337.6 | 482.4 | 61.4 | 18.2 | 110.4 | 8.6 | 240.9 | 12.3 | 822.3 | 758.8 | 810.1 | 846.5 | 740.8 | 665.5 | 575 | 768.1 | 717.3 | 684.7 | 512.6 | 720 | 580.9 | 367 | 353.4 | 364.8 | 344.7 | 356.8 | 347.3 | 355.3 | 341.1
1919.2 | 1643.2 | 470.2 | 188.08 | 219.8547 | 353 | 402.8 | 342.5 | 337.3 | 489.6 | 61.3 | 18.2 | 110.3 | 7.9 | 257 | 10.8 | 823.9 | 760 | 796 | 848.2 | 739.4 | 666.2 | 574.9 | 773 | 719.6 | 684.7 | 512.8 | 723.6 | 582.6 | 367.1 | 353.7 | 365.2 | 344.7 | 356.8 | 347.2 | 355.2 | 341
1920.2 | 1644.2 | 469.6 | 187.84 | 219.5741 | 353.1 | 401.7 | 342.4 | 337.6 | 490.5 | 61.3 | 18.2 | 110.3 | 8.9 | 246.1 | 12.9 | 825.6 | 768.5 | 793.8 | 850.3 | 739.4 | 666.5 | 583 | 773.5 | 727.2 | 685.7 | 512.8 | 715.8 | 584.5 | 367.2 | 353.6 | 365.2 | 344.7 | 356.8 | 347 | 355 | 340.9
1921.2 | 1645.2 | 470.2 | 188.08 | 219.8547 | 353.3 | 402.7 | 342.3 | 337.6 | 490.2 | 61.2 | 18.2 | 110.4 | 6.6 | 232.3 | 13.4 | 827.5 | 772.3 | 802.2 | 853.1 | 742.4 | 667.8 | 592.4 | 786.7 | 734.6 | 689.1 | 512.9 | 724.7 | 585.1 | 367.2 | 353.7 | 365.2 | 344.8 | 356.8 | 347 | 354.9 | 340.9
1922.2 | 1646.2 | 469.3 | 187.72 | 219.4339 | 353.4 | 402.9 | 342 | 337.6 | 493.7 | 61.2 | 18.2 | 110.3 | 5.9 | 249.7 | 14.6 | 829.7 | 775.8 | 799 | 856.1 | 743.4 | 669.1 | 599.8 | 791.5 | 744 | 692.7 | 513.2 | 728.2 | 585.9 | 367.3 | 354 | 365.2 | 344.9 | 356.8 | 346.8 | 354.7 | 340.8
1923.2 | 1647.2 | 470 | 188 | 219.7612 | 353.2 | 401.6 | 342 | 337.3 | 494.4 | 61.3 | 18.2 | 110.3 | 6.5 | 247.8 | 14.1 | 832.4 | 785.8 | 783.2 | 859.3 | 741.5 | 670.3 | 608.7 | 790.2 | 754.5 | 695 | 513.3 | 713.2 | 587.2 | 367.3 | 354 | 365.3 | 344.8 | 356.8 | 346.8 | 354.7 | 340.8
1924.2 | 1648.2 | 469.6 | 187.84 | 219.5741 | 353.2 | 400.1 | 341.7 | 337 | 499.3 | 61.2 | 18.2 | 110.4 | 8 | 257.6 | 13 | 833.9 | 789 | 798.4 | 862.8 | 745 | 671 | 613.8 | 791.3 | 763.4 | 697.5 | 513.3 | 712.5 | 587.9 | 367.3 | 353.9 | 365.4 | 344.6 | 356.7 | 346.8 | 355 | 340.9
1925.2 | 1649.2 | 469.6 | 187.84 | 219.5741 | 353.3 | 399.3 | 341.3 | 337.2 | 495.3 | 61.3 | 18.2 | 110.4 | 8.9 | 256 | 14.5 | 834.9 | 788.7 | 813.6 | 865.6 | 748.3 | 671.8 | 617.2 | 797.2 | 765.4 | 699.9 | 513.5 | 716.6 | 588 | 367.3 | 354 | 365.5 | 344.5 | 356.7 | 346.9 | 355.1 | 340.9
1926.2 | 1650.2 | 469 | 187.6 | 219.2936 | 353.3 | 400.9 | 340.9 | 337.7 | 493.2 | 61.3 | 18.2 | 110.4 | 8.9 | 262.6 | 14.9 | 836.4 | 784.3 | 830 | 867.7 | 751.2 | 672.9 | 614.8 | 799.7 | 765.3 | 701.2 | 513.9 | 724.9 | 587.1 | 367.4 | 354.1 | 365.6 | 344.5 | 356.7 | 346.9 | 355.3 | 340.9
1927.2 | 1651.2 | 470.5 | 188.2 | 219.995 | 353.2 | 402 | 340.6 | 338 | 491 | 61.3 | 18.2 | 110.6 | 7.3 | 270.5 | 15.1 | 837.2 | 785.8 | 832.1 | 869.6 | 751.5 | 674.1 | 613 | 802.9 | 765.9 | 702 | 514.3 | 728 | 586.3 | 367.4 | 354.1 | 365.8 | 344.5 | 356.7 | 346.8 | 355.3 | 340.8
1928.2 | 1652.2 | 470.8 | 188.32 | 220.1352 | 353.1 | 402 | 341 | 338.3 | 489.5 | 61.4 | 18.2 | 110.7 | 7.6 | 265.2 | 12.1 | 838 | 788.6 | 833.3 | 871.6 | 753.9 | 675.1 | 617.1 | 789.9 | 770.2 | 704.5 | 514.6 | 718.8 | 584.8 | 367.4 | 353.9 | 365.9 | 344.4 | 356.7 | 347 | 355.7 | 340.9
1929.2 | 1653.2 | 469.3 | 187.72 | 219.4339 | 353 | 400.8 | 341.3 | 338.4 | 487.5 | 61.5 | 18.2 | 110.9 | 7.1 | 271.5 | 11 | 839.6 | 790.4 | 828.3 | 873.3 | 753.8 | 675.5 | 614.6 | 789.7 | 765.6 | 704.2 | 514.9 | 721.2 | 585.6 | 367.3 | 353.8 | 366.1 | 344.4 | 356.7 | 347.1 | 356 | 340.9
1930.2 | 1654.2 | 469.6 | 187.84 | 219.5741 | 352.8 | 402.6 | 341.7 | 338.5 | 485 | 61.7 | 18.2 | 111 | 8.2 | 245.1 | 11.1 | 840.9 | 791 | 835.5 | 874.8 | 756 | 676.4 | 611.7 | 792.4 | 764.3 | 705.5 | 515.3 | 728 | 587.3 | 367.4 | 353.8 | 366.2 | 344.5 | 356.7 | 347 | 356 | 340.9
1931.2 | 1655.2 | 470.7 | 188.28 | 220.0885 | 352.8 | 403.9 | 341.6 | 338.8 | 483.8 | 61.8 | 18.2 | 111.1 | 7.7 | 241.9 | 14.8 | 840.7 | 789.7 | 815.3 | 875.8 | 754.6 | 677 | 608.8 | 779.1 | 761.2 | 705.2 | 515.6 | 719.9 | 587.7 | 367.4 | 353.8 | 366 | 344.5 | 356.7 | 347.1 | 356.1 | 341
1932.2 | 1656.2 | 470.9 | 188.36 | 220.182 | 352.9 | 405 | 341.7 | 338.9 | 480.2 | 61.8 | 18.2 | 111 | 7.6 | 239.3 | 16.3 | 839.9 | 791.2 | 800 | 875.1 | 752.8 | 677.1 | 604.9 | 758.2 | 751.9 | 702.4 | 515.5 | 706 | 587.1 | 367.3 | 353.5 | 365.8 | 344.4 | 356.7 | 347.3 | 356.4 | 341
1933.2 | 1657.2 | 470.7 | 188.28 | 220.0885 | 352.8 | 408.1 | 341.7 | 339.1 | 481.1 | 61.7 | 18.2 | 110.9 | 9.5 | 241.2 | 18 | 839.1 | 791.3 | 787.8 | 873.8 | 754 | 676.9 | 603.1 | 744.3 | 748.8 | 702.8 | 515.4 | 695.2 | 586.2 | 367.2 | 353.1 | 365.4 | 344.2 | 356.7 | 347.5 | 356.8 | 341.1
1934.2 | 1658.2 | 470.9 | 188.36 | 220.182 | 352.9 | 411.5 | 341 | 339.7 | 482.7 | 61.7 | 18.2 | 110.8 | 10.4 | 245.5 | 18.9 | 836.8 | 787.7 | 773 | 871.6 | 752.3 | 676.8 | 603.7 | 720.1 | 747.3 | 702.5 | 515.5 | 678.4 | 583.6 | 367.2 | 352.8 | 365.2 | 344 | 356.7 | 347.8 | 357.1 | 341.2
1935.2 | 1659.2 | 470.1 | 188.04 | 219.8079 | 353 | 413.3 | 340.5 | 340 | 483.6 | 61.7 | 18.2 | 110.9 | 12.7 | 243.2 | 18.3 | 836.3 | 788 | 778 | 869.4 | 751.4 | 676.4 | 601.1 | 716.9 | 744.5 | 701.2 | 515.4 | 677.1 | 580.9 | 367.1 | 352.6 | 365.1 | 343.9 | 356.7 | 347.9 | 357.6 | 341.3
1936.2 | 1660.2 | 470.3 | 188.12 | 219.9014 | 352.9 | 414.3 | 340.1 | 340.6 | 478.9 | 61.7 | 18.2 | 111 | 9.7 | 232.7 | 13.7 | 835.5 | 788.7 | 775 | 867.5 | 751.4 | 676.5 | 596.7 | 716.4 | 738.1 | 700.3 | 515.4 | 679.3 | 579.2 | 367.1 | 352.6 | 364.8 | 344 | 356.7 | 348.1 | 357.9 | 341.4
1937.2 | 1661.2 | 469.8 | 187.92 | 219.6677 | 352.6 | 414.3 | 339.9 | 340.7 | 475.5 | 61.8 | 18.2 | 111 | 8.7 | 236.1 | 12.4 | 835.6 | 784 | 752.3 | 866.5 | 748.2 | 676.5 | 591.4 | 713 | 731.2 | 698.2 | 515.2 | 674.8 | 580 | 367 | 352.6 | 364.5 | 344 | 356.7 | 348.4 | 357.8 | 341.3
1938.2 | 1662.2 | 469.2 | 187.68 | 219.3871 | 352.4 | 414.1 | 339.6 | 340.2 | 470.2 | 61.9 | 18.2 | 111 | 7.3 | 246.2 | 15.8 | 835.4 | 782.3 | 746.2 | 865.5 | 745.3 | 676.1 | 587.1 | 709.5 | 728.3 | 696 | 514.9 | 665.4 | 583.5 | 366.9 | 352.3 | 364.1 | 344 | 356.7 | 348.6 | 357.7 | 341.4
1939.2 | 1663.2 | 468.6 | 187.44 | 219.1066 | 352.3 | 415.3 | 339.6 | 339.7 | 469.1 | 61.7 | 18.2 | 111 | 6.7 | 253.7 | 12.8 | 833.5 | 789.3 | 728.4 | 863.5 | 741.1 | 675.8 | 589.2 | 700.6 | 730.8 | 696.4 | 514.5 | 652.3 | 586 | 366.9 | 351.9 | 363.7 | 343.9 | 356.7 | 348.9 | 357.6 | 341.6
1940.2 | 1664.2 | 469.3 | 187.72 | 219.4339 | 352.5 | 418.6 | 339.3 | 339.5 | 474.5 | 61.6 | 18.2 | 111 | 7.2 | 254.8 | 10.4 | 830.4 | 788.7 | 717.9 | 860.5 | 738.6 | 675.2 | 587.2 | 684.4 | 726 | 693.5 | 514.1 | 638.8 | 586.5 | 366.8 | 351.6 | 363.5 | 343.7 | 356.7 | 349.4 | 357.7 | 341.7
1941.2 | 1665.2 | 470 | 188 | 219.7612 | 352.5 | 420.3 | 339.1 | 339.4 | 474 | 61.5 | 18.2 | 110.8 | 7.9 | 251.3 | 10.9 | 829.7 | 791 | 736.4 | 858.1 | 740.1 | 674.9 | 588.3 | 687.5 | 726.4 | 693.2 | 513.6 | 637.5 | 586 | 366.7 | 351.4 | 363.2 | 343.6 | 356.7 | 349.7 | 358 | 341.8
1942.2 | 1666.2 | 469.6 | 187.84 | 219.5741 | 352.8 | 421.8 | 338.9 | 339.2 | 473 | 61.4 | 18.2 | 110.9 | 8.8 | 249.9 | 13.2 | 829.2 | 789.8 | 757.8 | 855.9 | 744.1 | 675.3 | 595.2 | 702.7 | 732.5 | 695.6 | 513.6 | 651.2 | 585 | 366.6 | 351.2 | 362.8 | 343.6 | 356.7 | 349.9 | 358.2 | 341.8
1943.2 | 1667.2 | 469.9 | 187.96 | 219.7144 | 352.9 | 421.8 | 338.8 | 339.1 | 472.3 | 61.3 | 18.2 | 110.9 | 8.2 | 254.5 | 13.5 | 828.7 | 788.2 | 779.6 | 853.8 | 746.4 | 675.2 | 595.4 | 703.8 | 734.6 | 695 | 513.6 | 664.2 | 583.4 | 366.5 | 351.1 | 362.5 | 343.6 | 356.7 | 350.1 | 358.2 | 341.8
1944.2 | 1668.2 | 469.3 | 187.72 | 219.4339 | 352.6 | 420 | 338.7 | 338.8 | 471.9 | 61.3 | 18.2 | 111 | 8.5 | 253.5 | 14.5 | 828.7 | 790.9 | 777.9 | 852.4 | 747.6 | 675.5 | 598.5 | 716.1 | 738.8 | 697 | 513.6 | 668.1 | 581.4 | 366.5 | 351 | 362.2 | 343.6 | 356.7 | 350.1 | 358.3 | 341.8
1945.2 | 1669.2 | 470.4 | 188.16 | 219.9482 | 352.6 | 418.6 | 338.7 | 338.6 | 476.2 | 61.3 | 18.2 | 111.1 | 8.3 | 252.7 | 14.8 | 828.4 | 789.4 | 778.2 | 851.3 | 747.9 | 675.6 | 600.7 | 712.9 | 737.6 | 696.4 | 513.5 | 669.8 | 579.3 | 366.5 | 351 | 362 | 343.6 | 356.8 | 350.2 | 358.4 | 341.8
1946.2 | 1670.2 | 470.9 | 188.36 | 220.182 | 352.4 | 420.3 | 338.9 | 338.2 | 473.3 | 61.3 | 18.2 | 111.1 | 7.5 | 260.6 | 15 | 829.2 | 790 | 788.8 | 851.1 | 749.8 | 675.9 | 602.1 | 729.6 | 741.5 | 697.7 | 513.5 | 682 | 578.7 | 366.5 | 350.9 | 361.8 | 343.7 | 356.8 | 350.2 | 358.3 | 341.8
1947.2 | 1671.2 | 471.7 | 188.68 | 220.556 | 352.2 | 420.9 | 338.8 | 337.9 | 471.5 | 61.2 | 18.2 | 111.2 | 7.5 | 246.6 | 16 | 830.8 | 790.4 | 806.8 | 851.8 | 752.3 | 676.3 | 605.4 | 743.4 | 745.3 | 698.7 | 513.7 | 689.1 | 578.4 | 366.4 | 350.7 | 361.7 | 343.7 | 356.8 | 350.1 | 358.3 | 341.8
1948.2 | 1672.2 | 471.4 | 188.56 | 220.4158 | 351.8 | 420.4 | 338.9 | 338 | 471.8 | 61.1 | 18.2 | 111.2 | 8.5 | 250.6 | 18.1 | 832 | 788.4 | 824.1 | 852.1 | 754.6 | 676.1 | 600.5 | 746.4 | 744.4 | 697.5 | 513.7 | 690.9 | 578.7 | 366.4 | 350.7 | 361.8 | 343.8 | 356.8 | 350 | 358.5 | 341.7
1949.2 | 1673.2 | 469.2 | 187.68 | 219.3871 | 351.5 | 419.5 | 338.8 | 338 | 470.2 | 61 | 18.2 | 111.1 | 10 | 241.4 | 19.4 | 831.4 | 784.7 | 832.7 | 852 | 754.9 | 676.2 | 595.2 | 746.1 | 740 | 696.6 | 513.8 | 696.5 | 579.1 | 366.5 | 350.8 | 361.9 | 344 | 356.8 | 349.8 | 358.2 | 341.7
1950.2 | 1674.2 | 469.4 | 187.76 | 219.4806 | 351.3 | 418.7 | 339.2 | 337.6 | 469.5 | 61.1 | 18.2 | 111.1 | 10.8 | 250.2 | 19.4 | 829.8 | 777.6 | 820.9 | 850.9 | 754.9 | 676.5 | 588.9 | 750 | 732.4 | 694.8 | 514 | 699.1 | 579.5 | 366.6 | 351.2 | 362.2 | 344.2 | 356.8 | 349.6 | 357.9 | 341.6
1951.2 | 1675.2 | 470.9 | 188.36 | 220.182 | 351.2 | 419.1 | 339.7 | 337.6 | 466.1 | 61.1 | 18.2 | 111.2 | 10.6 | 277.2 | 15.4 | 829.7 | 773.3 | 833.3 | 849.9 | 756.7 | 676.1 | 584 | 753.5 | 726.3 | 694 | 514.2 | 708.8 | 579.8 | 366.6 | 351.5 | 362.3 | 344.4 | 356.8 | 349.4 | 357.6 | 341.5
1952.2 | 1676.2 | 471 | 188.4 | 220.2287 | 351 | 416.5 | 339.7 | 338 | 464.9 | 61.1 | 18.2 | 111.1 | 9.6 | 227.4 | 13.3 | 831.3 | 775.3 | 846.4 | 850 | 760.7 | 676 | 582.1 | 760.6 | 728.5 | 694.9 | 514.5 | 716.6 | 580 | 366.6 | 351.7 | 362.4 | 344.4 | 356.8 | 349.1 | 357.3 | 341.4
1953.2 | 1677.2 | 470.7 | 188.28 | 220.0885 | 350.8 | 411.7 | 339.6 | 337.6 | 466.6 | 61.1 | 18.2 | 111.1 | 7.1 | 247.1 | 15.1 | 831.1 | 765.9 | 841.6 | 849.3 | 761.4 | 675.6 | 577.4 | 752.1 | 721.3 | 693.5 | 515.2 | 722.8 | 578.5 | 366.8 | 352.4 | 363 | 344.6 | 356.8 | 348.8 | 357 | 341.3
1954.2 | 1678.2 | 470 | 188 | 219.7612 | 350.6 | 408.7 | 339.8 | 337.2 | 478.1 | 61.1 | 18.2 | 111.2 | 6.9 | 254.4 | 14 | 829.3 | 753 | 825.5 | 847.2 | 758.1 | 675.6 | 570.4 | 746.3 | 709.3 | 691.4 | 516 | 726.1 | 577.1 | 366.9 | 353.1 | 363.7 | 344.9 | 356.8 | 348.5 | 356.8 | 341.2
1955.2 | 1679.2 | 470.4 | 188.16 | 219.9482 | 350.6 | 409.1 | 340.5 | 336.9 | 486.5 | 61.1 | 18.2 | 111.2 | 6.8 | 231.6 | 13.4 | 828.3 | 744.6 | 819.4 | 845.4 | 756.4 | 675.2 | 564.8 | 743.1 | 701.2 | 689.8 | 516.4 | 725.6 | 574.8 | 367.1 | 353.7 | 364.5 | 345.1 | 356.8 | 348.2 | 356.8 | 341.1
1956.2 | 1680.2 | 469.7 | 187.88 | 219.6209 | 350.9 | 409.3 | 341.1 | 337.6 | 491.6 | 61.2 | 18.2 | 111.3 | 6.9 | 238.6 | 12 | 827.5 | 741.3 | 823.5 | 844.2 | 755.3 | 675.1 | 563.4 | 742.3 | 697.7 | 687.9 | 516.7 | 721.6 | 572.8 | 367.3 | 354.5 | 365.3 | 345.5 | 356.8 | 347.9 | 356.7 | 341
1957.2 | 1681.2 | 470.2 | 188.08 | 219.8547 | 351.2 | 406.2 | 341.4 | 338.3 | 492.5 | 61.3 | 18.2 | 111.4 | 6.7 | 238.3 | 11.2 | 829 | 747.9 | 828.2 | 844.4 | 756.9 | 674.7 | 564.8 | 752.3 | 703.4 | 689.3 | 517.1 | 724.3 | 571.8 | 367.4 | 355 | 366.2 | 345.7 | 356.8 | 347.7 | 356.6 | 340.9
1958.2 | 1682.2 | 470.5 | 188.2 | 219.995 | 351.3 | 403 | 341.9 | 338.6 | 487.2 | 61.3 | 18.2 | 111.5 | 7.3 | 239.1 | 12.2 | 829.2 | 749.5 | 828.2 | 845.3 | 757.1 | 674.1 | 564.6 | 750.3 | 704.2 | 688.8 | 517.6 | 725.6 | 571.5 | 367.6 | 355.7 | 366.8 | 345.8 | 356.8 | 347.5 | 356.6 | 340.9
1959.2 | 1683.2 | 469.9 | 187.96 | 219.7144 | 351.1 | 402.2 | 342 | 338.9 | 481.1 | 61.3 | 18.2 | 111.5 | 6.6 | 247.6 | 14.3 | 829.1 | 754.7 | 823.4 | 846.4 | 757.1 | 673.6 | 566.9 | 750.6 | 705.5 | 688.8 | 517.9 | 724.2 | 571.5 | 367.7 | 356.2 | 367.1 | 345.8 | 356.8 | 347.4 | 356.7 | 340.9
1960.2 | 1684.2 | 469.8 | 187.92 | 219.6677 | 351.1 | 403 | 341.7 | 339.1 | 478.3 | 61.3 | 18.2 | 111.6 | 6.3 | 239.5 | 15.7 | 828.9 | 756.1 | 808.6 | 846.8 | 756.2 | 672.6 | 566.9 | 745.4 | 707.7 | 687.9 | 518.1 | 720.3 | 572.4 | 367.7 | 356 | 367.1 | 345.8 | 356.8 | 347.2 | 356.6 | 340.9
1961.2 | 1685.2 | 470.2 | 188.08 | 219.8547 | 351.3 | 405.1 | 341.7 | 339.3 | 474.1 | 61.3 | 18.2 | 111.6 | 6.6 | 242.9 | 14.1 | 829.5 | 758.9 | 812.5 | 846.6 | 757 | 672.2 | 567 | 750.8 | 708.9 | 687.6 | 518.2 | 717.8 | 572.7 | 367.7 | 355.9 | 367 | 345.8 | 356.7 | 347.1 | 356.5 | 340.8
1962.2 | 1686.2 | 470.1 | 188.04 | 219.8079 | 351.5 | 406.3 | 341.7 | 338.8 | 475 | 61.2 | 18.2 | 111.5 | 6.5 | 227.7 | 10.9 | 830 | 753.5 | 824 | 845.7 | 759.1 | 671.6 | 564.6 | 751.1 | 704 | 686.1 | 518.5 | 727 | 572 | 367.8 | 356 | 367 | 345.8 | 356.7 | 347.1 | 356.2 | 340.7
1963.2 | 1687.2 | 469.7 | 187.88 | 219.6209 | 351.5 | 405.8 | 341.4 | 338.6 | 478.4 | 61.2 | 18.2 | 111.6 | 7.5 | 253.2 | 9.3 | 831.8 | 760.3 | 842 | 846 | 761.9 | 671.6 | 568.2 | 767.5 | 709.8 | 689.7 | 519 | 734.3 | 571.4 | 367.8 | 355.9 | 367.1 | 345.9 | 356.7 | 347.1 | 356.1 | 340.7
1964.2 | 1688.2 | 470.3 | 188.12 | 219.9014 | 351.4 | 405.2 | 341.2 | 338.8 | 479.5 | 61.2 | 18.2 | 111.6 | 6.3 | 236.7 | 9 | 833.3 | 766.9 | 854 | 847.6 | 765.9 | 671.7 | 573.2 | 773 | 721.2 | 691.4 | 519.6 | 734.9 | 570.2 | 367.9 | 355.8 | 367.2 | 345.9 | 356.7 | 347.2 | 356.2 | 340.7
1965.2 | 1689.2 | 470.1 | 188.04 | 219.8079 | 351.2 | 403.3 | 341.3 | 338.9 | 477.2 | 61.2 | 18.2 | 111.4 | 5.9 | 242.7 | 9.9 | 833.3 | 771.5 | 863.3 | 849 | 767.6 | 671.4 | 577.3 | 774.8 | 727.5 | 692.7 | 520.3 | 738.9 | 569.5 | 367.9 | 355.8 | 367.3 | 346 | 356.7 | 347.1 | 356.1 | 340.7
1966.2 | 1690.2 | 469.6 | 187.84 | 219.5741 | 351.1 | 403 | 341.3 | 339 | 478.2 | 61.1 | 18.2 | 111.4 | 6.9 | 251 | 9.9 | 835.1 | 767.6 | 866.5 | 850.6 | 767.3 | 671.6 | 578.8 | 779.9 | 729.9 | 693.1 | 520.9 | 741.7 | 571.7 | 367.9 | 355.9 | 367.3 | 346 | 356.7 | 347 | 355.9 | 340.6
1967.2 | 1691.2 | 469.7 | 187.88 | 219.6209 | 350.9 | 403.7 | 341.4 | 339 | 480.4 | 61.1 | 18.2 | 111.3 | 7.5 | 261.6 | 9 | 835.8 | 764.6 | 860.8 | 851.6 | 767.5 | 671.8 | 577.4 | 779.8 | 730.8 | 692.9 | 521.3 | 743.3 | 574 | 367.9 | 356.2 | 367.4 | 346 | 356.7 | 346.8 | 355.7 | 340.5
1968.2 | 1692.2 | 470.2 | 188.08 | 219.8547 | 350.6 | 404.3 | 341.6 | 338.6 | 480 | 61 | 18.2 | 111.3 | 7.8 | 233.4 | 9.4 | 835.1 | 757.6 | 853.2 | 851.2 | 767.9 | 671.7 | 575.6 | 776.7 | 726.5 | 693.7 | 521.9 | 746.2 | 574.6 | 368 | 358.1 | 368.3 | 346 | 356.7 | 346.6 | 355.4 | 340.4
1969.2 | 1693.2 | 470 | 188 | 219.7612 | 350.5 | 404.1 | 341.9 | 338.6 | 478.7 | 61 | 18.2 | 111.3 | 7.4 | 242.7 | 11.2 | 836 | 756.3 | 851.1 | 851.9 | 766.3 | 671.8 | 573.2 | 772.8 | 725.2 | 692.1 | 522.4 | 744.9 | 575.6 | 368.1 | 358 | 368.5 | 346 | 356.7 | 346.4 | 355.4 | 340.4
1970.2 | 1694.2 | 470.1 | 188.04 | 219.8079 | 350.5 | 403.3 | 342.1 | 338.7 | 478.1 | 61.1 | 18.2 | 111.2 | 7.9 | 256.5 | 10.6 | 835.7 | 760.2 | 853 | 852 | 766.5 | 672 | 571.7 | 778 | 724.1 | 691.9 | 522.8 | 748 | 576.9 | 368.2 | 357.7 | 368.4 | 346 | 356.6 | 346.2 | 355.3 | 340.3
1971.2 | 1695.2 | 469.5 | 187.8 | 219.5274 | 350.5 | 400.9 | 342.3 | 338.7 | 478.8 | 61.1 | 18.2 | 111.2 | 6.9 | 241.4 | 9.7 | 835.9 | 764.6 | 850.5 | 852.5 | 766.5 | 672.1 | 574 | 779.4 | 724 | 691.6 | 523 | 747 | 578.8 | 368.2 | 357.4 | 368.2 | 346.1 | 356.6 | 346 | 355.1 | 340.3
1972.2 | 1696.2 | 470 | 188 | 219.7612 | 350.4 | 398.4 | 342.5 | 338.7 | 476.8 | 61.1 | 18.2 | 111.3 | 6.7 | 252.8 | 9.6 | 835 | 770.1 | 829.8 | 852.8 | 763.4 | 672.3 | 580 | 775 | 733.3 | 693.3 | 523.1 | 731.6 | 581.1 | 368.2 | 357.3 | 368 | 346.2 | 356.6 | 345.9 | 355.2 | 340.3
1973.2 | 1697.2 | 469.7 | 187.88 | 219.6209 | 350.5 | 399.4 | 342.3 | 338.9 | 475.9 | 61.2 | 18.2 | 111.2 | 6.8 | 233.1 | 12.1 | 834.4 | 771.7 | 824.6 | 852.9 | 763.5 | 671.9 | 581.8 | 752.3 | 733.6 | 691.8 | 523 | 714.5 | 583.4 | 368.1 | 357 | 367.7 | 346 | 356.6 | 345.9 | 355.4 | 340.3
1974.2 | 1698.2 | 469.4 | 187.76 | 219.4806 | 350.7 | 402.1 | 341.8 | 339.2 | 476.1 | 61.2 | 18.2 | 111.1 | 6.6 | 241.9 | 12.9 | 833.9 | 770.4 | 812.5 | 852.8 | 763.1 | 671.9 | 587.2 | 737.6 | 734.6 | 692.5 | 522.9 | 704.6 | 583.6 | 368.1 | 356.4 | 367.3 | 345.7 | 356.5 | 345.9 | 355.4 | 340.4
1975.2 | 1699.2 | 470.2 | 188.08 | 219.8547 | 351.2 | 405.8 | 341.6 | 339.7 | 474.8 | 61.2 | 18.2 | 111 | 6 | 237.7 | 13.4 | 832.8 | 771.5 | 811.3 | 852 | 761.3 | 671.3 | 587.8 | 724 | 730.9 | 690.6 | 522.8 | 695.3 | 582.5 | 368 | 355.8 | 367 | 345.4 | 356.5 | 346.1 | 355.5 | 340.4
1976.2 | 1700.2 | 470.3 | 188.12 | 219.9014 | 351.4 | 409.1 | 341.2 | 340.2 | 475 | 61.2 | 18.2 | 110.9 | 6.4 | 242.6 | 13.1 | 831.3 | 773.2 | 793.9 | 850.7 | 759.8 | 671.6 | 598.7 | 716.3 | 739.4 | 692.3 | 522.8 | 682.3 | 580.1 | 367.9 | 355.3 | 366.6 | 345.2 | 356.5 | 346.2 | 355.6 | 340.5
1977.2 | 1701.2 | 471.4 | 188.56 | 220.4158 | 351.7 | 410.5 | 340.8 | 340.5 | 475.9 | 61.2 | 18.2 | 110.9 | 6.8 | 239 | 11.3 | 830 | 775.3 | 801.6 | 848.2 | 762.3 | 672.1 | 605.7 | 716.6 | 743.6 | 693.5 | 522.7 | 681.5 | 577.9 | 367.8 | 354.8 | 366.2 | 345 | 356.5 | 346.3 | 356 | 340.5
1978.2 | 1702.2 | 469.9 | 187.96 | 219.7144 | 351.7 | 409.1 | 340.8 | 340.9 | 477 | 61.1 | 18.2 | 110.9 | 6.4 | 243.7 | 12.2 | 829.9 | 774.7 | 807.5 | 846.2 | 764.8 | 672.5 | 608.4 | 725 | 746.7 | 694.2 | 522.8 | 688.1 | 575.2 | 367.8 | 354.4 | 365.9 | 344.9 | 356.5 | 346.4 | 356.3 | 340.6
1979.2 | 1703.2 | 469.4 | 187.76 | 219.4806 | 351.5 | 410.1 | 341.2 | 341.2 | 475.7 | 61.1 | 18.2 | 111 | 6.9 | 259.6 | 11.4 | 830.4 | 771.2 | 816.9 | 845.1 | 765.4 | 672.7 | 604.4 | 740.5 | 745.1 | 693.7 | 523 | 699.6 | 575.4 | 367.8 | 354 | 365.7 | 344.9 | 356.4 | 346.5 | 356.4 | 340.6
1980.2 | 1704.2 | 468.4 | 187.36 | 219.013 | 351.4 | 412 | 341.5 | 341.1 | 473.4 | 61.1 | 18.2 | 111 | 7.7 | 257.8 | 10.8 | 832 | 773.9 | 814.7 | 845.7 | 762.6 | 673.2 | 604.8 | 757 | 748 | 693.7 | 523 | 705.7 | 577.8 | 367.7 | 353.7 | 365.5 | 344.9 | 356.4 | 346.7 | 356.5 | 340.6
1981.2 | 1705.2 | 469 | 187.6 | 219.2936 | 351.3 | 413.1 | 341.4 | 340.6 | 477.2 | 61.2 | 18.2 | 111 | 7.6 | 254.3 | 11.7 | 832 | 771.4 | 813.2 | 846 | 760.8 | 674.2 | 602.2 | 760.8 | 745 | 693.3 | 523 | 710.9 | 581 | 367.8 | 353.7 | 365.6 | 345.1 | 356.4 | 346.7 | 356.3 | 340.6
1982.2 | 1706.2 | 469.4 | 187.76 | 219.4806 | 351 | 412.3 | 341.3 | 340.2 | 481.3 | 61.3 | 18.2 | 111.1 | 7.3 | 235.3 | 11.3 | 833.1 | 772 | 808.3 | 847.1 | 760.5 | 674.8 | 599.6 | 769.7 | 743.3 | 693.4 | 523 | 711.5 | 586.4 | 367.8 | 353.6 | 365.6 | 345.2 | 356.4 | 346.7 | 356.1 | 340.5
1983.2 | 1707.2 | 469.4 | 187.76 | 219.4806 | 350.9 | 410 | 341.5 | 339.7 | 480.5 | 61.5 | 18.2 | 111.2 | 7.1 | 232.4 | 10.5 | 832.8 | 766.2 | 811.4 | 847.4 | 760.1 | 675.4 | 595.3 | 774.6 | 740.6 | 692.3 | 522.9 | 720.8 | 590.5 | 367.8 | 353.7 | 365.5 | 345.2 | 356.4 | 346.7 | 355.8 | 340.4
1984.2 | 1708.2 | 469.3 | 187.72 | 219.4339 | 351.3 | 408.7 | 341.6 | 339 | 485 | 61.5 | 18.2 | 111.2 | 6.5 | 246.5 | 9.7 | 831.1 | 758.8 | 792.5 | 846.6 | 756.1 | 675.4 | 589.5 | 759.9 | 731.2 | 689.6 | 522.7 | 715 | 595.5 | 367.9 | 353.8 | 365.7 | 345.4 | 356.4 | 346.7 | 355.7 | 340.4
1985.2 | 1709.2 | 469.3 | 187.72 | 219.4339 | 351.5 | 408.4 | 341.8 | 338.5 | 483.8 | 61.5 | 18.2 | 111.4 | 6.4 | 242.3 | 9.3 | 831.3 | 757.8 | 803.6 | 846.1 | 757.4 | 674.9 | 585.8 | 752 | 724.1 | 689.1 | 522.6 | 716.9 | 597.6 | 368 | 354 | 365.9 | 345.7 | 356.3 | 346.6 | 355.8 | 340.3
1986.2 | 1710.2 | 469.4 | 187.76 | 219.4806 | 351.4 | 407.8 | 341.9 | 338.5 | 487.8 | 61.5 | 18.2 | 111.5 | 6.1 | 230.3 | 8.6 | 832.7 | 755.4 | 820.2 | 846.7 | 759.8 | 675.8 | 588 | 767.3 | 730.4 | 691.2 | 522.9 | 729.3 | 598.8 | 368.1 | 354.3 | 366 | 345.8 | 356.3 | 346.4 | 355.6 | 340.3
1987.2 | 1711.2 | 468.9 | 187.56 | 219.2468 | 351.2 | 404.4 | 342.5 | 338.4 | 499.5 | 61.5 | 18.2 | 111.7 | 6.4 | 256.4 | 9.5 | 834.2 | 756.4 | 828.6 | 848.4 | 760.7 | 676.5 | 589.9 | 778.6 | 735.7 | 692.3 | 523.2 | 736.2 | 599.1 | 368.2 | 354.7 | 366.3 | 345.8 | 356.3 | 346.3 | 355.6 | 340.2
1988.2 | 1712.2 | 468.4 | 187.36 | 219.013 | 350.8 | 403.8 | 342.7 | 338.5 | 501.1 | 61.6 | 18.2 | 111.9 | 6.3 | 229.4 | 11.4 | 836.3 | 757.6 | 827.7 | 850.4 | 761.3 | 677.6 | 594.8 | 789.2 | 741.7 | 694.8 | 523.7 | 738.8 | 598 | 368.3 | 355.1 | 366.4 | 346 | 356.3 | 346.2 | 355.6 | 340.1
1989.2 | 1713.2 | 469.5 | 187.8 | 219.5274 | 350.5 | 403.7 | 343.1 | 338.6 | 507.1 | 61.6 | 18.2 | 111.9 | 6.4 | 242.4 | 11.4 | 837.4 | 750.9 | 832.1 | 851.9 | 761.2 | 678.2 | 591.7 | 789.9 | 735.6 | 694 | 523.9 | 742.2 | 595.7 | 368.5 | 355.7 | 366.7 | 346.3 | 356.3 | 346.1 | 355.8 | 340
1990.2 | 1714.2 | 468.9 | 187.56 | 219.2468 | 350.3 | 405.2 | 343.2 | 338.4 | 506.4 | 61.6 | 18.2 | 111.9 | 6 | 254.3 | 8.8 | 837.2 | 750.9 | 823.7 | 852.7 | 762.8 | 678.6 | 591.2 | 784.7 | 732.7 | 694.5 | 524.5 | 743.1 | 592.7 | 368.6 | 356.1 | 367.2 | 346.4 | 356.3 | 346.1 | 355.8 | 340
1991.2 | 1715.2 | 469.9 | 187.96 | 219.7144 | 350.2 | 404.5 | 343.5 | 338.9 | 502.5 | 61.6 | 18.2 | 111.8 | 6.2 | 257.5 | 8.2 | 836 | 756.8 | 813.4 | 852.3 | 762.4 | 678.2 | 603.9 | 761.3 | 740.7 | 695.8 | 524.8 | 721.2 | 589.5 | 368.6 | 355.8 | 367.1 | 346.1 | 356.3 | 346.4 | 355.9 | 340.1
1992.2 | 1716.2 | 470.3 | 188.12 | 219.9014 | 350.5 | 402.1 | 344.2 | 339.3 | 501 | 61.6 | 18.2 | 111.8 | 6.8 | 254.1 | 11.6 | 836 | 761.3 | 808 | 852.1 | 762.9 | 678.1 | 609.1 | 763.1 | 747.2 | 696.8 | 524.9 | 713.1 | 586.4 | 368.6 | 355.6 | 367.2 | 345.9 | 356.2 | 346.8 | 356.1 | 340.2
1993.2 | 1717.2 | 470.3 | 188.12 | 219.9014 | 350.7 | 405.1 | 344.1 | 339.9 | 498.2 | 61.6 | 18.2 | 111.9 | 6.5 | 261.1 | 15.1 | 835.7 | 767.4 | 797 | 851.3 | 763 | 678.5 | 616.2 | 754.4 | 755.3 | 698.4 | 525 | 698.9 | 582.9 | 368.6 | 355.5 | 367.3 | 345.9 | 356.2 | 347.3 | 356.4 | 340.3
1994.2 | 1718.2 | 470.5 | 188.2 | 219.995 | 351 | 407.6 | 343.8 | 340.4 | 504.9 | 61.6 | 18.2 | 111.9 | 6.8 | 263.5 | 15.7 | 835.6 | 769.9 | 795.5 | 851.1 | 764.5 | 678.5 | 622.2 | 741.2 | 759 | 700.5 | 525 | 688.5 | 579.4 | 368.6 | 355.3 | 367.3 | 345.8 | 356.2 | 347.7 | 357.3 | 340.5
1995.2 | 1719.2 | 470.6 | 188.24 | 220.0417 | 351.1 | 408.3 | 343.8 | 340.7 | 500.1 | 61.6 | 18.2 | 111.9 | 7.5 | 257.3 | 15.4 | 836.8 | 774.6 | 791.2 | 850.7 | 764.7 | 678.7 | 623.5 | 745.5 | 759 | 701.3 | 525.2 | 694.7 | 577.1 | 368.6 | 355.3 | 367.1 | 345.6 | 356.2 | 347.8 | 357.5 | 340.5
1996.2 | 1720.2 | 470.8 | 188.32 | 220.1352 | 351.3 | 410 | 343.9 | 341.3 | 495.3 | 61.7 | 18.2 | 112 | 6.9 | 271.6 | 11.4 | 836.8 | 775 | 796.1 | 850.1 | 765.7 | 679.3 | 625.8 | 749.5 | 756.7 | 702.4 | 525.4 | 700.7 | 574.8 | 368.6 | 355.3 | 367.2 | 345.6 | 356.2 | 347.9 | 357.6 | 340.4
1997.2 | 1721.2 | 470.7 | 188.28 | 220.0885 | 351.2 | 412 | 343.8 | 341.5 | 489.1 | 61.7 | 18.2 | 112 | 7.2 | 248 | 10 | 836.7 | 775 | 806.6 | 849.5 | 765 | 679.1 | 619.9 | 744.1 | 753 | 701.9 | 525.6 | 700.2 | 573.6 | 368.6 | 355.3 | 367.2 | 345.7 | 356.2 | 347.9 | 357.8 | 340.4
1998.2 | 1722.2 | 470.6 | 188.24 | 220.0417 | 351 | 416.2 | 343.8 | 341.3 | 481.3 | 61.7 | 18.2 | 111.9 | 6.7 | 249.5 | 10.2 | 836.3 | 771.8 | 811.7 | 849.3 | 764.2 | 678.5 | 610.4 | 730.6 | 743.6 | 698.7 | 525.6 | 694.6 | 572.4 | 368.6 | 355.3 | 367.1 | 345.9 | 356.2 | 347.9 | 358.1 | 340.5
1999.2 | 1723.2 | 470.5 | 188.2 | 219.995 | 350.8 | 416.7 | 344.1 | 341 | 476 | 61.7 | 18.2 | 111.8 | 7.8 | 246.3 | 10.1 | 835.1 | 769.4 | 801.5 | 848.8 | 761.6 | 678.2 | 602.8 | 722.9 | 738.5 | 696.6 | 525.3 | 690 | 571.8 | 368.6 | 355 | 366.8 | 345.9 | 356.2 | 348.1 | 358 | 340.5
2000.2 | 1724.2 | 470.1 | 188.04 | 219.8079 | 350.6 | 414.6 | 344.2 | 340.6 | 471.4 | 61.6 | 18.2 | 111.8 | 8.5 | 254.1 | 9.4 | 834 | 769.1 | 781.6 | 848.7 | 757.8 | 677.7 | 599.6 | 711.8 | 736 | 694.5 | 524.9 | 676.2 | 573 | 368.5 | 354.7 | 366.3 | 345.7 | 356.2 | 348.4 | 357.9 | 340.6
2001.2 | 1725.2 | 470.2 | 188.08 | 219.8547 | 350.5 | 411.3 | 343.5 | 340.1 | 465.9 | 61.6 | 18.2 | 111.8 | 7.2 | 238.5 | 11.7 | 834.3 | 765.4 | 790.4 | 849.1 | 756.6 | 677.2 | 594.9 | 707 | 731.1 | 692.7 | 524.5 | 670 | 576.1 | 368.5 | 354.6 | 366 | 345.8 | 356.2 | 348.5 | 357.6 | 340.6
2002.2 | 1726.2 | 470.1 | 188.04 | 219.8079 | 350.4 | 410.4 | 342.9 | 339.7 | 460.9 | 61.6 | 18.2 | 112 | 7.7 | 241.8 | 16.8 | 833.3 | 759.4 | 791.6 | 848.2 | 754.9 | 676.2 | 588.8 | 697.8 | 721.8 | 690.2 | 523.9 | 664.4 | 578.9 | 368.4 | 354.5 | 365.7 | 345.8 | 356.2 | 348.4 | 357.2 | 340.6
2003.2 | 1727.2 | 469.9 | 187.96 | 219.7144 | 350.3 | 409.5 | 342.2 | 339.2 | 457.9 | 61.6 | 18.2 | 112 | 7.8 | 241.1 | 17.8 | 832 | 762.7 | 781.2 | 848.2 | 753.3 | 675.8 | 584.6 | 703.8 | 721.8 | 689.6 | 523.5 | 658.6 | 581.4 | 368.3 | 354.1 | 365.2 | 345.8 | 356.2 | 348.3 | 356.8 | 340.5
2004.2 | 1728.2 | 469.8 | 187.92 | 219.6677 | 350 | 408.4 | 341.3 | 338.4 | 455.7 | 61.5 | 18.2 | 112 | 7.7 | 243.6 | 16.5 | 830.1 | 766.1 | 768.7 | 846.6 | 751.8 | 675.2 | 581.8 | 693.1 | 721.2 | 688.2 | 522.9 | 647.7 | 582.6 | 368.2 | 353.6 | 364.8 | 345.6 | 356.2 | 348.3 | 356.5 | 340.5
2005.2 | 1729.2 | 470.2 | 188.08 | 219.8547 | 349.9 | 406 | 340.7 | 337.7 | 452.3 | 61.5 | 18.2 | 112.2 | 8.5 | 236.6 | 16.3 | 828.5 | 764.4 | 776.9 | 845.1 | 752.8 | 674.4 | 580 | 687.4 | 717.8 | 686.6 | 522.4 | 645.6 | 583.4 | 368.1 | 353.1 | 364.2 | 345.4 | 356.2 | 348.2 | 356.2 | 340.5
2006.2 | 1730.2 | 470.3 | 188.12 | 219.9014 | 349.8 | 404.3 | 340.2 | 337.2 | 450 | 61.6 | 18.2 | 112.5 | 9.3 | 224.6 | 13.5 | 827 | 762.3 | 769.1 | 844 | 750 | 673.6 | 576 | 686.9 | 711.9 | 684.5 | 521.8 | 647.3 | 584.2 | 368 | 352.8 | 363.7 | 345.3 | 356.2 | 347.9 | 355.8 | 340.4
2007.2 | 1731.2 | 469.7 | 187.88 | 219.6209 | 349.6 | 406.5 | 339.4 | 336.6 | 449.8 | 61.6 | 18.2 | 112.7 | 7.6 | 243.2 | 15.7 | 825.8 | 764.9 | 760.1 | 843.2 | 746.8 | 673.3 | 575.1 | 696.6 | 712.6 | 684.3 | 521.3 | 646.6 | 586.2 | 367.9 | 352.5 | 363.3 | 345.3 | 356.2 | 348 | 355.4 | 340.4
2008.2 | 1732.2 | 469.8 | 187.92 | 219.6677 | 349.4 | 406.9 | 338.8 | 336.1 | 450.4 | 61.7 | 18.2 | 112.8 | 7.6 | 242.1 | 16.9 | 824.1 | 759.9 | 754.1 | 841.2 | 744.5 | 672.3 | 570.9 | 685.3 | 707.5 | 681 | 520.7 | 638 | 590.2 | 367.8 | 352 | 362.8 | 345.2 | 356.2 | 347.9 | 355.2 | 340.4
2009.2 | 1733.2 | 470.2 | 188.08 | 219.8547 | 349.2 | 408 | 338.2 | 335.6 | 448.7 | 61.8 | 18.2 | 112.9 | 7.2 | 240.8 | 16.3 | 822.3 | 764.3 | 743.8 | 839.3 | 742.9 | 671.6 | 571.2 | 690 | 708.9 | 680.7 | 519.9 | 635.1 | 592.8 | 367.7 | 351.6 | 362.2 | 345.1 | 356.1 | 347.7 | 354.9 | 340.4
2010.2 | 1734.2 | 470 | 188 | 219.7612 | 349.4 | 407.1 | 337.8 | 334.9 | 448.4 | 61.7 | 18.2 | 113 | 8.1 | 244.3 | 17 | 821.8 | 768.1 | 744.7 | 838.5 | 741.6 | 671 | 574.2 | 696.5 | 712 | 680.7 | 519.2 | 631.1 | 595.5 | 367.6 | 351.2 | 361.7 | 345 | 356.1 | 347.5 | 354.7 | 340.4
2011.2 | 1735.2 | 469.3 | 187.72 | 219.4339 | 349.3 | 405 | 337.2 | 334.4 | 445.7 | 61.7 | 18.2 | 113.1 | 7.9 | 243.7 | 15.5 | 820.9 | 769.6 | 745.4 | 837.9 | 739.9 | 670 | 571.8 | 685.4 | 711.2 | 677.9 | 518.5 | 623.8 | 599.2 | 367.5 | 350.9 | 361.3 | 344.9 | 356.1 | 347.2 | 354.2 | 340.3
2012.2 | 1736.2 | 470.2 | 188.08 | 219.8547 | 349.1 | 405.7 | 336.5 | 334 | 445.3 | 61.6 | 18.2 | 113.2 | 7.7 | 240 | 15.9 | 818.7 | 766 | 734.4 | 836.4 | 737.2 | 669.1 | 566.9 | 677.4 | 705 | 675.7 | 517.7 | 620.2 | 601.4 | 367.4 | 350.6 | 361.2 | 344.9 | 356.1 | 347 | 353.8 | 340.3
2013.2 | 1737.2 | 470.5 | 188.2 | 219.995 | 349 | 404.7 | 336.1 | 333.9 | 445 | 61.6 | 18.2 | 113.3 | 7.6 | 242.5 | 16 | 815.3 | 760 | 715.5 | 833.7 | 732.6 | 667.6 | 560.5 | 657.9 | 693.3 | 672.5 | 516.8 | 608.8 | 603.1 | 367.3 | 350.2 | 360.8 | 344.7 | 356 | 346.8 | 353.6 | 340.4
2014.2 | 1738.2 | 470.2 | 188.08 | 219.8547 | 348.9 | 402.9 | 336 | 333.8 | 444.7 | 61.6 | 18.2 | 113.4 | 7 | 248 | 16.4 | 812.5 | 753 | 703.2 | 831.1 | 729.4 | 666.3 | 556.6 | 649 | 687.8 | 669.9 | 515.9 | 601.1 | 606.2 | 367.2 | 349.8 | 360.2 | 344.5 | 356 | 346.7 | 353.4 | 340.3
2015.2 | 1739.2 | 470.5 | 188.2 | 219.995 | 348.8 | 403.9 | 335.6 | 333.7 | 446.3 | 61.5 | 18.2 | 113.4 | 6.9 | 249.8 | 16.1 | 811.2 | 753.3 | 711 | 829.7 | 728.2 | 665.3 | 555.2 | 652.5 | 686.5 | 668.8 | 515.1 | 601.3 | 609.7 | 367.1 | 349.6 | 359.7 | 344.5 | 355.9 | 346.5 | 353.5 | 340.3
2016.2 | 1740.2 | 470.4 | 188.16 | 219.9482 | 348.7 | 406.8 | 335.1 | 333.5 | 443.6 | 61.5 | 18.2 | 113.4 | 6 | 254.1 | 16 | 809.8 | 753.7 | 718.7 | 828.3 | 726.5 | 664.3 | 554.3 | 660 | 688.5 | 668.3 | 514.4 | 605.7 | 612.2 | 367 | 349.2 | 359.4 | 344.5 | 355.9 | 346.3 | 353.4 | 340.2
2017.2 | 1741.2 | 470 | 188 | 219.7612 | 348.5 | 409.9 | 334.8 | 333.6 | 441.8 | 61.6 | 18.2 | 113.4 | 7 | 255.2 | 15.6 | 808.8 | 756.6 | 722.7 | 827.6 | 726.9 | 663.5 | 556.4 | 669.7 | 692.2 | 668.2 | 513.6 | 608.5 | 613 | 366.9 | 349.1 | 359.1 | 344.4 | 355.8 | 346.1 | 353.2 | 340.2
2018.2 | 1742.2 | 470.8 | 188.32 | 220.1352 | 348.6 | 412.2 | 334.6 | 333.8 | 447.7 | 61.6 | 18.2 | 113.4 | 6.7 | 251.1 | 16.5 | 808.1 | 756.8 | 719.5 | 826.7 | 726.1 | 662.9 | 564.9 | 671.5 | 699.3 | 669 | 512.9 | 607.4 | 611.7 | 366.8 | 348.9 | 359 | 344.3 | 355.7 | 346.4 | 353.3 | 340.3
2019.2 | 1743.2 | 470.9 | 188.36 | 220.182 | 348.6 | 412.5 | 334.4 | 333.8 | 458.2 | 61.6 | 18.2 | 113.4 | 7 | 247 | 16.2 | 808.2 | 759.1 | 733.8 | 826.3 | 726.8 | 662.2 | 569 | 665.6 | 705.5 | 669.9 | 512.3 | 610.3 | 609.3 | 366.7 | 348.5 | 359 | 344.1 | 355.7 | 346.7 | 353.5 | 340.4
2020.2 | 1744.2 | 470 | 188 | 219.7612 | 348.7 | 414.6 | 334.4 | 334.3 | 458.7 | 61.6 | 18.2 | 113.2 | 7.7 | 240.7 | 15.5 | 808.2 | 762.8 | 743.1 | 826.2 | 727.8 | 661.3 | 570 | 666.4 | 707.2 | 670.3 | 511.7 | 615.2 | 607.3 | 366.7 | 348.3 | 359.1 | 344 | 355.6 | 346.8 | 353.8 | 340.4
2021.2 | 1745.2 | 470.1 | 188.04 | 219.8079 | 348.7 | 416.5 | 334.7 | 334.9 | 464.9 | 61.6 | 18.2 | 112.9 | 7.5 | 243.2 | 16.1 | 806.6 | 765.6 | 738 | 825.7 | 725.4 | 660.3 | 573.7 | 660.2 | 709.2 | 670.2 | 511.3 | 614.2 | 604.8 | 366.6 | 348.2 | 359.3 | 343.9 | 355.6 | 347.1 | 354.1 | 340.5
2022.2 | 1746.2 | 470.4 | 188.16 | 219.9482 | 348.7 | 417.8 | 334.9 | 335.2 | 469.1 | 61.6 | 18.2 | 112.8 | 7.4 | 246.5 | 15.4 | 806.8 | 764.6 | 759.4 | 825.8 | 728.6 | 659.8 | 576.1 | 674.1 | 713.8 | 671.3 | 510.8 | 624.6 | 602.9 | 366.6 | 348.1 | 359.3 | 343.9 | 355.5 | 347.2 | 354.3 | 340.5
2023.2 | 1747.2 | 467.6 | 187.04 | 218.639 | 348.5 | 420.3 | 335.1 | 335.7 | 466.6 | 61.6 | 18.2 | 112.7 | 6.8 | 247.1 | 15.2 | 809.2 | 763.5 | 789.2 | 826.7 | 730.4 | 660 | 574.7 | 701.5 | 712.1 | 673.4 | 510.5 | 643.2 | 601.7 | 366.5 | 348.1 | 359.4 | 343.9 | 355.5 | 347.4 | 354.3 | 340.4
2024.2 | 1748.2 | 467.3 | 186.92 | 218.4987 | 348.1 | 417.6 | 335.3 | 335.7 | 466.8 | 61.5 | 18.2 | 112.6 | 7.3 | 240.6 | 15 | 811.6 | 769.1 | 806.3 | 829 | 735.3 | 660.5 | 579.3 | 729.7 | 718.3 | 676.8 | 510.6 | 661.8 | 599.8 | 366.5 | 348.1 | 359.4 | 344 | 355.4 | 347.5 | 354.4 | 340.4
2025.2 | 1749.2 | 467.7 | 187.08 | 218.6857 | 347.8 | 415 | 335.4 | 335.5 | 473.9 | 61.5 | 18.2 | 112.8 | 7.6 | 236.6 | 13.1 | 813.5 | 773.7 | 813.6 | 832.2 | 737.6 | 661.6 | 592.3 | 749.2 | 728.4 | 680.7 | 511.1 | 667.9 | 598.2 | 366.5 | 348.1 | 359.5 | 344 | 355.4 | 347.6 | 354.4 | 340.4
2026.2 | 1750.2 | 468.3 | 187.32 | 218.9663 | 347.8 | 412.9 | 335.9 | 335.8 | 477.6 | 61.5 | 18.2 | 113 | 6.4 | 248.4 | 10.8 | 815.4 | 773.8 | 822.5 | 835.4 | 740.6 | 662.4 | 598 | 765.1 | 735.3 | 683.5 | 511.1 | 679.3 | 596.2 | 366.5 | 348.1 | 359.8 | 344 | 355.4 | 347.8 | 354.7 | 340.4
2027.2 | 1751.2 | 469 | 187.6 | 219.2936 | 347.7 | 413.6 | 336.2 | 336.1 | 476.7 | 61.6 | 18.2 | 113.1 | 7.2 | 239.5 | 9.4 | 817.3 | 775.9 | 824.1 | 838.1 | 742.6 | 663 | 597.8 | 774.5 | 739.1 | 684.7 | 511.1 | 690.9 | 593.4 | 366.6 | 348.2 | 360 | 344 | 355.4 | 347.7 | 355 | 340.4
2028.2 | 1752.2 | 469.5 | 187.8 | 219.5274 | 347.8 | 413.2 | 336.6 | 336.5 | 479.2 | 61.6 | 18.2 | 113 | 7.3 | 269.1 | 10.7 | 818.5 | 774.1 | 825.7 | 841 | 742.3 | 663.2 | 595.7 | 769.5 | 737.2 | 683.9 | 511.1 | 689.4 | 591.7 | 366.6 | 348.4 | 360.2 | 344.1 | 355.3 | 347.7 | 355.1 | 340.3
2029.2 | 1753.2 | 470 | 188 | 219.7612 | 347.9 | 412.9 | 337 | 336.6 | 475.2 | 61.7 | 18.2 | 112.7 | 8.8 | 260.7 | 12.6 | 820.3 | 772.6 | 832 | 843.7 | 743.5 | 663.3 | 594.6 | 766.5 | 734.7 | 684 | 510.9 | 691.1 | 591.4 | 366.6 | 348.7 | 360.3 | 344.3 | 355.3 | 347.6 | 355.1 | 340.3
2030.2 | 1754.2 | 468.4 | 187.36 | 219.013 | 347.8 | 410.8 | 337.5 | 336.8 | 470.8 | 61.7 | 18.2 | 112.5 | 8.4 | 253.6 | 13.4 | 820.9 | 767.3 | 825.7 | 845.3 | 742.2 | 663.1 | 589.2 | 751.7 | 728.6 | 682.8 | 510.8 | 685.7 | 592.5 | 366.7 | 349.1 | 360.5 | 344.4 | 355.3 | 347.6 | 355 | 340.2
2031.2 | 1755.2 | 468.6 | 187.44 | 219.1066 | 347.7 | 408.4 | 337.8 | 336.8 | 467.1 | 61.7 | 18.2 | 112.2 | 9.4 | 245.5 | 14.1 | 820.9 | 768.6 | 830.6 | 846.3 | 742.5 | 662.5 | 584 | 742.8 | 721.8 | 680.6 | 510.5 | 679.8 | 596.2 | 366.7 | 349.3 | 360.7 | 344.4 | 355.2 | 347.5 | 354.9 | 340.2
2032.2 | 1756.2 | 468.6 | 187.44 | 219.1066 | 347.7 | 407.1 | 338 | 336.7 | 464.1 | 61.5 | 18.2 | 112.1 | 8.6 | 238.4 | 13.4 | 823.3 | 769.3 | 842.6 | 847.7 | 746.3 | 663.2 | 586.8 | 759.8 | 728.9 | 682.8 | 510.3 | 690.9 | 599.3 | 366.7 | 349.6 | 360.9 | 344.5 | 355.2 | 347.5 | 354.7 | 340.1
2033.2 | 1757.2 | 469.4 | 187.76 | 219.4806 | 347.9 | 406 | 338.2 | 336.3 | 465.3 | 61.4 | 18.2 | 112.1 | 8.2 | 237 | 13.1 | 824.3 | 763.6 | 830.3 | 847.8 | 747.2 | 664 | 588.4 | 758.4 | 731 | 684.1 | 510.8 | 696.7 | 599.3 | 366.8 | 350 | 361.3 | 344.7 | 355.2 | 347.4 | 354.5 | 340
2034.2 | 1758.2 | 468.9 | 187.56 | 219.2468 | 348 | 407.1 | 338.7 | 336.1 | 468.6 | 61.4 | 18.2 | 112.1 | 7.6 | 238.4 | 14.7 | 825.1 | 754.5 | 836.4 | 848.1 | 746.9 | 664.3 | 582 | 760.3 | 721 | 682.7 | 511.4 | 706.7 | 598.6 | 367 | 353.3 | 361.9 | 345 | 355.2 | 347.2 | 354.4 | 339.9
2035.2 | 1759.2 | 468.7 | 187.48 | 219.1533 | 348.1 | 406 | 339.1 | 336.1 | 473.8 | 61.4 | 18.2 | 112.1 | 5.8 | 249 | 14.4 | 826 | 754.7 | 845.8 | 848.6 | 750.4 | 664.4 | 579.5 | 759.4 | 717.9 | 682.7 | 511.6 | 710.9 | 597.6 | 367.1 | 353.6 | 362.6 | 345.1 | 355.2 | 346.9 | 354.2 | 339.9
2036.2 | 1760.2 | 469 | 187.6 | 219.2936 | 348.2 | 403.5 | 339.5 | 336.6 | 473.5 | 61.4 | 18.2 | 112.1 | 6.2 | 244.1 | 16 | 827.4 | 762.7 | 857.5 | 848.9 | 753.4 | 664.4 | 579.8 | 765.2 | 719.9 | 683.5 | 511.8 | 715.2 | 596.3 | 367.2 | 353.2 | 362.8 | 345 | 355.1 | 346.7 | 354.1 | 339.8
2037.2 | 1761.2 | 470.4 | 188.16 | 219.9482 | 348.2 | 401.4 | 339.6 | 337 | 469.6 | 61.4 | 18.2 | 112 | 5.5 | 247.7 | 17.3 | 829.9 | 767.2 | 865.2 | 850.1 | 755.6 | 664.8 | 581.6 | 775.1 | 724.5 | 684.6 | 512.3 | 719.3 | 595.1 | 367.2 | 353 | 363 | 344.9 | 355.1 | 346.6 | 354 | 339.8
2038.2 | 1762.2 | 470.4 | 188.16 | 219.9482 | 348.1 | 402.5 | 339.7 | 337.3 | 471.8 | 61.5 | 18.2 | 111.9 | 4.9 | 246.2 | 17.7 | 831.8 | 767.1 | 865.4 | 851.9 | 757.5 | 665.7 | 586.9 | 782.6 | 729.5 | 686.1 | 512.8 | 726.2 | 594.2 | 367.3 | 353 | 363.3 | 345 | 355.1 | 346.4 | 354 | 339.8
2039.2 | 1763.2 | 470.1 | 188.04 | 219.8079 | 348 | 402.1 | 339.7 | 337.4 | 473.1 | 61.7 | 18.2 | 111.9 | 5.1 | 245.5 | 17.3 | 832.8 | 770.2 | 868.4 | 853.1 | 759 | 665.9 | 586.9 | 783.4 | 731.8 | 687 | 513.5 | 729.7 | 592.2 | 367.4 | 353 | 363.4 | 345 | 355.1 | 346.3 | 354.2 | 339.7
2040.2 | 1764.2 | 468.9 | 187.56 | 219.2468 | 347.8 | 400.8 | 339.7 | 337.6 | 471 | 61.8 | 18.2 | 111.8 | 5 | 255.1 | 17.8 | 835.2 | 773.7 | 862.6 | 854.6 | 760.4 | 666.3 | 593.2 | 779.1 | 735.7 | 688.4 | 514.1 | 725.7 | 590.1 | 367.4 | 353 | 363.4 | 344.9 | 355 | 346.2 | 354.3 | 339.8
2041.2 | 1765.2 | 469.7 | 187.88 | 219.6209 | 347.5 | 401.5 | 339.6 | 337.9 | 469.8 | 62 | 18.2 | 111.8 | 5.9 | 264.9 | 15.9 | 836.8 | 770.8 | 868 | 854.9 | 763.5 | 666.4 | 594.1 | 770.6 | 732.6 | 690 | 514.8 | 730.8 | 587.6 | 367.5 | 353.1 | 363.4 | 345 | 355 | 346.1 | 354.2 | 339.8
2042.2 | 1766.2 | 470 | 188 | 219.7612 | 347.2 | 402.3 | 339.3 | 337.5 | 467.4 | 62 | 18.2 | 111.8 | 6.7 | 276.8 | 13 | 839.2 | 769.6 | 861.5 | 855.9 | 763.1 | 666.8 | 593.6 | 785.7 | 736.9 | 692.5 | 515.5 | 735.9 | 585.5 | 367.5 | 353.2 | 363.5 | 345.1 | 355 | 346 | 354.1 | 339.7
2043.2 | 1767.2 | 469.9 | 187.96 | 219.7144 | 347.2 | 401.6 | 339.2 | 337.1 | 467.5 | 62 | 18.2 | 111.8 | 5.5 | 257.9 | 11.6 | 840.4 | 772.2 | 869 | 857.2 | 765.5 | 667.6 | 598.1 | 789.2 | 745.1 | 694.5 | 516.1 | 737.5 | 583 | 367.5 | 353.1 | 363.3 | 344.9 | 355 | 346 | 354 | 339.6
2044.2 | 1768.2 | 471 | 188.4 | 220.2287 | 347.3 | 400.9 | 339.4 | 337.3 | 465.5 | 61.9 | 18.2 | 111.9 | 5.1 | 270.6 | 10.5 | 841.4 | 775.3 | 868.6 | 858 | 768.2 | 667.7 | 597.8 | 777.5 | 746.6 | 694.1 | 516.6 | 734.5 | 580.7 | 367.5 | 352.9 | 363.2 | 344.8 | 354.9 | 346 | 353.9 | 339.7
2045.2 | 1769.2 | 471.4 | 188.56 | 220.4158 | 347.2 | 400 | 339.3 | 337.2 | 462.9 | 61.9 | 18.2 | 112 | 5.5 | 260.5 | 9.6 | 843.4 | 779 | 870.7 | 859.3 | 769.2 | 668.2 | 597.9 | 785.7 | 745.1 | 694.5 | 517.3 | 741.1 | 578.2 | 367.5 | 352.8 | 363.2 | 344.9 | 354.9 | 345.9 | 353.7 | 339.6
2046.2 | 1770.2 | 470.7 | 188.28 | 220.0885 | 347 | 399.2 | 339 | 336.9 | 464.4 | 61.8 | 18.2 | 112.2 | 6.6 | 255.4 | 9.8 | 844.8 | 777 | 876.7 | 860.1 | 772.8 | 668.7 | 598.2 | 781.6 | 747.3 | 696.3 | 518.1 | 745 | 575.8 | 367.5 | 352.8 | 363.2 | 345 | 354.9 | 345.8 | 353.7 | 339.6
2047.2 | 1771.2 | 470.2 | 188.08 | 219.8547 | 347 | 399.4 | 339 | 336.8 | 464.5 | 61.8 | 18.2 | 112.3 | 6.9 | 268.2 | 10.1 | 846.9 | 774 | 860.3 | 861.4 | 771.9 | 669.3 | 595.4 | 789.6 | 743.1 | 698 | 519.4 | 748.7 | 574.8 | 367.6 | 352.9 | 363.2 | 345.1 | 354.9 | 345.7 | 353.8 | 339.5
2048.2 | 1772.2 | 470.4 | 188.16 | 219.9482 | 347.1 | 398.9 | 339.2 | 336.6 | 471.1 | 61.7 | 18.2 | 112.4 | 6.8 | 265.2 | 11.2 | 848.4 | 768.2 | 829 | 862.5 | 768.1 | 670.2 | 592.7 | 789.2 | 737.7 | 696.5 | 520.2 | 747.9 | 576.3 | 367.7 | 353 | 363.3 | 345.2 | 354.8 | 345.6 | 353.7 | 339.4
2049.2 | 1773.2 | 470.4 | 188.16 | 219.9482 | 347 | 397.7 | 339.1 | 336.5 | 472.1 | 61.7 | 18.2 | 112.4 | 7.3 | 255.4 | 11.2 | 850 | 767.2 | 826.4 | 863.8 | 767.7 | 670.7 | 591.8 | 790.4 | 736.5 | 697.4 | 520.6 | 746.3 | 577.9 | 367.8 | 352.9 | 363.2 | 345.1 | 354.8 | 345.4 | 353.8 | 339.4
2050.2 | 1774.2 | 470.7 | 188.28 | 220.0885 | 347.1 | 396.3 | 339.3 | 336.5 | 475.3 | 61.7 | 18.2 | 112.5 | 7.4 | 249.1 | 12.1 | 850.6 | 765.2 | 823.8 | 864.2 | 766.3 | 671.3 | 590.7 | 786.1 | 735.3 | 695.5 | 520.9 | 743.2 | 579.8 | 367.9 | 352.9 | 363.5 | 345.1 | 354.8 | 345.4 | 353.8 | 339.4
2051.2 | 1775.2 | 470.5 | 188.2 | 219.995 | 347.5 | 395.4 | 339.7 | 336.2 | 484.4 | 61.7 | 18.2 | 112.6 | 6.1 | 248.5 | 11.7 | 851.4 | 764.2 | 827.8 | 864.6 | 766.4 | 672.6 | 590.2 | 792.9 | 735 | 695.2 | 521.1 | 743 | 580.8 | 368 | 353.2 | 363.9 | 345.3 | 354.7 | 345.5 | 353.7 | 339.4
2052.2 | 1776.2 | 470 | 188 | 219.7612 | 347.6 | 393.9 | 340.8 | 335.9 | 489 | 61.8 | 18.2 | 112.5 | 6.1 | 238.1 | 13.4 | 851.9 | 757.9 | 818.9 | 864.8 | 763.6 | 672.3 | 585.6 | 778.5 | 728.2 | 693.2 | 521.4 | 734.5 | 582.3 | 368.1 | 353.4 | 364.1 | 345.5 | 354.7 | 345.5 | 353.5 | 339.3
2053.2 | 1777.2 | 469.9 | 187.96 | 219.7144 | 347.6 | 393.2 | 341.6 | 335.4 | 487.6 | 61.8 | 18.2 | 112.3 | 7.5 | 239.7 | 14 | 850.3 | 751.3 | 791.9 | 863.9 | 759.6 | 671.8 | 579.9 | 763.5 | 718.5 | 690.4 | 521.4 | 727.3 | 584.5 | 368.1 | 353.8 | 364.1 | 345.6 | 354.7 | 345.5 | 353.5 | 339.3
2054.2 | 1778.2 | 470.1 | 188.04 | 219.8079 | 347.7 | 394.3 | 341.8 | 334.9 | 484.5 | 61.9 | 18.2 | 112.4 | 8.4 | 262.2 | 13.5 | 847.2 | 740.9 | 775.5 | 860.8 | 756.2 | 671.2 | 573.2 | 747.1 | 704.4 | 686.3 | 521.2 | 719 | 585.1 | 368.3 | 354.3 | 364.3 | 345.7 | 354.6 | 345.5 | 353.6 | 339.2
2055.2 | 1779.2 | 469.9 | 187.96 | 219.7144 | 347.9 | 395.5 | 341.8 | 335 | 480.7 | 62 | 18.2 | 112.4 | 8.3 | 260 | 12.2 | 846.8 | 745.4 | 756.3 | 859.4 | 754.1 | 670.3 | 570.6 | 746.5 | 700.9 | 687.7 | 521 | 711.3 | 587.4 | 368.3 | 354.4 | 364.8 | 345.7 | 354.6 | 345.5 | 353.6 | 339.2
2056.2 | 1780.2 | 470 | 188 | 219.7612 | 347.8 | 395.8 | 341.9 | 335.1 | 473.3 | 62 | 18.2 | 112.4 | 7.7 | 235.5 | 10.2 | 845.6 | 745.6 | 741.5 | 857.7 | 750.7 | 669.7 | 570.4 | 735.7 | 703.4 | 685.7 | 520.6 | 697.3 | 592.1 | 368.3 | 354.3 | 364.8 | 345.6 | 354.6 | 345.4 | 353.4 | 339.2
2057.2 | 1781.2 | 469.9 | 187.96 | 219.7144 | 347.6 | 394.5 | 341.6 | 334.8 | 468 | 62 | 18.2 | 112.5 | 8.1 | 247.6 | 10.9 | 842.7 | 747.7 | 733.2 | 854.5 | 745.9 | 668.9 | 567 | 732.7 | 699.9 | 683 | 520 | 692.8 | 598.6 | 368.3 | 353.9 | 364.4 | 345.4 | 354.6 | 345.2 | 353.4 | 339.1
2058.2 | 1782.2 | 470 | 188 | 219.7612 | 347.8 | 394.1 | 340.8 | 334.7 | 467.2 | 62 | 18.2 | 112.5 | 10.3 | 244.8 | 15.7 | 841.1 | 750 | 734.3 | 852.5 | 743.9 | 668.9 | 566.2 | 734.6 | 700.1 | 682.2 | 519.5 | 691.5 | 606.8 | 368.3 | 353.7 | 363.8 | 345.4 | 354.5 | 345.1 | 353.4 | 339
2059.2 | 1783.2 | 470.1 | 188.04 | 219.8079 | 347.8 | 393.2 | 340.1 | 334.8 | 468.8 | 62 | 18.2 | 112.5 | 7.4 | 246.6 | 16.6 | 840.3 | 744.8 | 752.1 | 849.8 | 743.6 | 668.5 | 562.1 | 725.2 | 695.2 | 679.9 | 518.9 | 692.5 | 611.8 | 368.3 | 353.6 | 363.7 | 345.4 | 354.5 | 344.9 | 353.2 | 338.9
2060.2 | 1784.2 | 469.4 | 187.76 | 219.4806 | 347.9 | 393 | 339.6 | 334.5 | 468 | 62 | 18.2 | 112.5 | 6 | 246.8 | 18.2 | 840.7 | 747.3 | 763.9 | 848.5 | 744.5 | 668.7 | 565.4 | 742.9 | 699.6 | 682.4 | 518.3 | 696.6 | 616.1 | 368.4 | 353.3 | 363.6 | 345.3 | 354.5 | 344.7 | 353.1 | 338.9
2061.2 | 1785.2 | 469.7 | 187.88 | 219.6209 | 348 | 391.2 | 339.8 | 334.8 | 466.9 | 62 | 18.2 | 112.4 | 7 | 249.6 | 17.1 | 839.1 | 747.3 | 755.1 | 846.2 | 741.4 | 667.9 | 563 | 737.5 | 699 | 680.2 | 517.8 | 691.2 | 620.5 | 368.3 | 353 | 363.4 | 345.1 | 354.4 | 344.6 | 352.9 | 338.8
2062.2 | 1786.2 | 469.2 | 187.68 | 219.3871 | 348.1 | 389 | 339.8 | 334.6 | 468.2 | 62 | 18.2 | 112.3 | 7.9 | 239.8 | 15.6 | 839.1 | 744.6 | 756.8 | 844.7 | 740.8 | 667.6 | 562.3 | 739.2 | 700.6 | 679.8 | 517.3 | 695.5 | 622.9 | 368.4 | 353.1 | 363.4 | 345.2 | 354.4 | 344.4 | 352.9 | 338.7
2063.2 | 1787.2 | 469.8 | 187.92 | 219.6677 | 348.2 | 388.8 | 339.9 | 334.5 | 477 | 62.1 | 18.2 | 112.4 | 8.1 | 248.8 | 12.8 | 837.3 | 734.1 | 746.1 | 841.7 | 737.4 | 667.7 | 560.2 | 734.3 | 695.5 | 677.4 | 516.8 | 695.3 | 623.3 | 368.6 | 353.5 | 363.7 | 345.5 | 354.4 | 344.4 | 352.9 | 338.6
2064.2 | 1788.2 | 470.2 | 188.08 | 219.8547 | 348.4 | 389.6 | 340.3 | 334.9 | 487.8 | 62.2 | 18.2 | 112.6 | 8.1 | 253.3 | 12.5 | 836 | 737.7 | 752.7 | 839.9 | 738 | 666.9 | 558.8 | 730.6 | 691.5 | 677 | 516.4 | 692 | 622.6 | 368.9 | 354.1 | 364.3 | 345.9 | 354.3 | 344.5 | 353 | 338.6
2065.2 | 1789.2 | 469.2 | 187.68 | 219.3871 | 348.5 | 390 | 341 | 335 | 482.7 | 62.3 | 18.2 | 112.7 | 6.9 | 256.7 | 12.8 | 836.5 | 744.8 | 755.2 | 840.2 | 737 | 666 | 564.4 | 732.6 | 697.4 | 679.1 | 515.8 | 687.7 | 624 | 368.9 | 354.2 | 364.5 | 345.8 | 354.3 | 344.6 | 353.4 | 338.6
2066.2 | 1790.2 | 470.3 | 188.12 | 219.9014 | 348.6 | 389.6 | 341.4 | 334.9 | 480.9 | 62.5 | 18.2 | 112.7 | 7.7 | 261.9 | 11.8 | 834.8 | 749.1 | 740.5 | 839.4 | 736.5 | 665.1 | 567.3 | 711.2 | 700.1 | 677.8 | 515 | 669.7 | 624.5 | 368.8 | 353.8 | 364.4 | 345.6 | 354.3 | 345 | 354 | 338.7
2067.2 | 1791.2 | 470.1 | 188.04 | 219.8079 | 349 | 389.6 | 341.6 | 335.4 | 482.1 | 62.6 | 18.2 | 112.7 | 7.7 | 244 | 12.5 | 832.3 | 751.7 | 725.3 | 837.1 | 734.6 | 664.8 | 578.5 | 697.9 | 708 | 677.8 | 514.3 | 655 | 622.2 | 368.8 | 353.5 | 364.6 | 345.3 | 354.2 | 345.5 | 354.6 | 338.9
2068.2 | 1792.2 | 470.1 | 188.04 | 219.8079 | 349.7 | 392.2 | 341.5 | 336.2 | 487.2 | 62.7 | 18.2 | 112.6 | 7.6 | 248.5 | 13.8 | 828.6 | 748.7 | 718.2 | 833.8 | 732 | 663.8 | 579.5 | 676 | 707.5 | 676.6 | 513.8 | 642.7 | 617.4 | 368.8 | 353.1 | 364.5 | 345 | 354.2 | 345.9 | 355.1 | 339
2069.2 | 1793.2 | 469.8 | 187.92 | 219.6677 | 349.9 | 393.5 | 341.4 | 336.7 | 481.9 | 62.7 | 18.2 | 112.4 | 6.8 | 259 | 14.8 | 828.3 | 750.2 | 746.3 | 832.5 | 734 | 663.1 | 576.8 | 693 | 707 | 677 | 513.4 | 656.2 | 613.8 | 368.7 | 353 | 364.4 | 344.8 | 354.2 | 346.2 | 355.8 | 339
2070.2 | 1794.2 | 470.2 | 188.08 | 219.8547 | 349.4 | 394.2 | 341.4 | 337.4 | 475.8 | 62.7 | 18.2 | 112.2 | 5.9 | 251.3 | 15.3 | 830.4 | 750.4 | 778.5 | 832.5 | 738.2 | 663.4 | 579.5 | 716.6 | 714 | 679.7 | 513.2 | 674.1 | 611.6 | 368.7 | 352.9 | 364.4 | 344.8 | 354.2 | 346.6 | 356 | 339
2071.2 | 1795.2 | 468.9 | 187.56 | 219.2468 | 349 | 395.9 | 341.4 | 337.7 | 477.7 | 62.6 | 18.2 | 112.1 | 7.7 | 247.2 | 14 | 831.6 | 742.8 | 804.3 | 832.4 | 742.3 | 663.5 | 575.5 | 727.5 | 711.2 | 678 | 513.1 | 688 | 610.4 | 368.7 | 353 | 364.3 | 344.9 | 354.1 | 346.8 | 356 | 339
2072.2 | 1796.2 | 469.9 | 187.96 | 219.7144 | 348.6 | 395.7 | 341.7 | 337.5 | 478.1 | 62.5 | 18.2 | 112.2 | 8.5 | 231.8 | 13 | 831.8 | 739.6 | 817.6 | 832.4 | 745.7 | 662.9 | 572 | 735.8 | 706.4 | 678.3 | 513 | 699.6 | 607.4 | 368.7 | 353.1 | 364.3 | 344.9 | 354.1 | 346.9 | 356 | 339
2073.2 | 1797.2 | 470.3 | 188.12 | 219.9014 | 348.3 | 394.8 | 342 | 337.3 | 477.7 | 62.5 | 18.2 | 112.3 | 7.3 | 231.1 | 12 | 831.4 | 733.7 | 807.4 | 831.9 | 745.8 | 662.9 | 568.3 | 739.9 | 702.4 | 677.3 | 513.2 | 708.6 | 603.6 | 368.9 | 353.7 | 364.7 | 345.2 | 354.1 | 346.9 | 356 | 338.9
2074.2 | 1798.2 | 469.6 | 187.84 | 219.5741 | 348.3 | 394.1 | 341.9 | 337.2 | 481 | 62.5 | 18.2 | 112.4 | 5.9 | 243.3 | 10.3 | 830.2 | 729 | 799.5 | 831 | 743.1 | 662.6 | 564.5 | 742.7 | 695.2 | 675 | 513.2 | 709.8 | 600.4 | 369 | 354.1 | 365.3 | 345.5 | 354.1 | 346.8 | 356 | 338.8
2075.2 | 1799.2 | 469 | 187.6 | 219.2936 | 348.2 | 393.1 | 342.1 | 336.9 | 476.6 | 62.4 | 18.2 | 112.5 | 5.7 | 237.1 | 10.2 | 831.3 | 737.3 | 792.4 | 831.6 | 743.2 | 662.4 | 568.2 | 754.4 | 699.3 | 677.1 | 513.1 | 704.4 | 599 | 369 | 354 | 365.5 | 345.4 | 354.1 | 346.7 | 355.8 | 338.8
2076.2 | 1800.2 | 469.6 | 187.84 | 219.5741 | 348.2 | 392.1 | 342.4 | 336.8 | 473.4 | 62.3 | 18.2 | 112.6 | 6.2 | 241.7 | 12.3 | 832.4 | 746.1 | 792.4 | 833.6 | 743.1 | 662.4 | 577.9 | 748.5 | 709.6 | 679.3 | 513 | 692.1 | 599.1 | 369 | 353.9 | 365.4 | 345.3 | 354.1 | 346.9 | 355.8 | 338.8
2077.2 | 1801.2 | 470.9 | 188.36 | 220.182 | 348.3 | 391.7 | 342.3 | 336.9 | 475.8 | 62.2 | 18.2 | 112.7 | 8 | 260.8 | 15.2 | 833 | 756.1 | 780.3 | 835.3 | 739.7 | 662.3 | 580.5 | 748.1 | 715 | 679.5 | 512.8 | 687.8 | 599.5 | 369 | 353.7 | 365.2 | 345.1 | 354.1 | 347 | 355.8 | 338.9
2078.2 | 1802.2 | 470.7 | 188.28 | 220.0885 | 348.4 | 391.7 | 342.1 | 337.1 | 476 | 62.2 | 18.2 | 112.7 | 7.1 | 255.2 | 14.8 | 833.9 | 761.5 | 768.5 | 836.9 | 738.7 | 662.6 | 587.6 | 750 | 723.9 | 680.7 | 512.6 | 680.3 | 601.2 | 368.9 | 353.4 | 365.1 | 345 | 354.1 | 347 | 355.8 | 338.9
2079.2 | 1803.2 | 469.1 | 187.64 | 219.3403 | 348.5 | 392.5 | 341.8 | 337.1 | 476 | 62.1 | 18.2 | 112.7 | 7.3 | 256 | 14 | 833 | 765.4 | 759 | 837.5 | 735.8 | 662.3 | 587.7 | 735.2 | 726.4 | 678.4 | 512.3 | 666.6 | 602.7 | 368.9 | 353 | 364.7 | 344.8 | 354.1 | 347 | 355.9 | 338.9
2080.2 | 1804.2 | 469.4 | 187.76 | 219.4806 | 348.2 | 392.5 | 341.9 | 337.2 | 471.7 | 62.1 | 18.2 | 112.6 | 7.6 | 260.6 | 14.4 | 833.3 | 768.4 | 759.1 | 837.8 | 734.1 | 662 | 586.3 | 736.2 | 729.1 | 678.2 | 511.8 | 658.6 | 605.3 | 368.8 | 352.6 | 364.3 | 344.7 | 354.1 | 347 | 355.8 | 338.9
2081.2 | 1805.2 | 470 | 188 | 219.7612 | 348.1 | 393.2 | 341.8 | 337.4 | 470.1 | 62 | 18.2 | 112.5 | 7.8 | 254.9 | 12.7 | 833.5 | 770.9 | 770.5 | 838.4 | 734.2 | 662 | 586.5 | 736.3 | 734 | 678.4 | 511.2 | 654.8 | 608 | 368.7 | 352.1 | 363.8 | 344.6 | 354.1 | 347.1 | 355.8 | 338.9
2082.2 | 1806.2 | 470 | 188 | 219.7612 | 348 | 393.9 | 341.4 | 337.3 | 470 | 62 | 18.2 | 112.4 | 8.1 | 255.5 | 12.8 | 833.3 | 771.2 | 778.4 | 838.5 | 734.1 | 661.6 | 586.6 | 725 | 731.8 | 677.1 | 510.7 | 650 | 609.6 | 368.6 | 351.7 | 363.5 | 344.4 | 354.1 | 347.1 | 355.7 | 338.9
2083.2 | 1807.2 | 468.7 | 187.48 | 219.1533 | 348.2 | 393.4 | 340.6 | 337.3 | 469.4 | 62 | 18.2 | 112.3 | 6.9 | 251.6 | 13 | 832.4 | 774.1 | 778.2 | 837.9 | 732.9 | 661.4 | 586.8 | 714.3 | 730 | 676.2 | 510.2 | 646.5 | 610.5 | 368.5 | 351.3 | 363.1 | 344.4 | 354.1 | 347.3 | 355.8 | 339
2084.2 | 1808.2 | 469.1 | 187.64 | 219.3403 | 348.1 | 390.4 | 340.1 | 337.6 | 468.8 | 62 | 18.2 | 112.4 | 6.9 | 248.1 | 12.1 | 832.4 | 773.2 | 766.9 | 838.5 | 731.8 | 661 | 584.3 | 717.6 | 727.1 | 676.1 | 509.6 | 650.3 | 611.3 | 368.4 | 350.9 | 362.6 | 344.3 | 354.1 | 347.5 | 356.1 | 339
2085.2 | 1809.2 | 469 | 187.6 | 219.2936 | 348.2 | 389.3 | 339.4 | 337.7 | 467.1 | 62 | 18.2 | 112.6 | 6.5 | 258 | 9.9 | 833.3 | 765 | 772.1 | 839 | 731.5 | 662 | 582.7 | 731.4 | 721.5 | 676.6 | 509.2 | 666.2 | 613.9 | 368.5 | 351.1 | 362.5 | 344.5 | 354.1 | 347.6 | 356.3 | 339
2086.2 | 1810.2 | 469 | 187.6 | 219.2936 | 348.2 | 388.8 | 338.9 | 337.5 | 474.9 | 61.9 | 18.2 | 112.7 | 6.8 | 240.2 | 8.9 | 832.7 | 754.3 | 765 | 838.4 | 728 | 663 | 578.7 | 747.1 | 715.2 | 676.1 | 508.9 | 682.2 | 615.3 | 368.6 | 351.4 | 362.7 | 344.8 | 354.1 | 347.7 | 356.3 | 338.9
2087.2 | 1811.2 | 468.1 | 187.24 | 218.8728 | 348.3 | 387 | 338.7 | 337.2 | 478.5 | 62 | 18.2 | 112.8 | 5.7 | 259.2 | 9.3 | 831.8 | 741.3 | 766.2 | 837 | 726.9 | 663.9 | 575 | 746.6 | 708.6 | 674.5 | 508.6 | 689.4 | 614.5 | 368.7 | 351.9 | 363 | 345.1 | 354.1 | 347.7 | 356.6 | 338.9
2088.2 | 1812.2 | 468.7 | 187.48 | 219.1533 | 348.6 | 387.6 | 339.7 | 337.6 | 488.5 | 62 | 18.2 | 112.8 | 5.3 | 242.5 | 11.9 | 831.7 | 735 | 778.4 | 835.8 | 727.1 | 665 | 571.5 | 760.6 | 704.9 | 674.1 | 508.5 | 703 | 613.2 | 368.9 | 352.4 | 363.5 | 345.3 | 354.1 | 347.6 | 356.8 | 338.9
2089.2 | 1813.2 | 469.6 | 187.84 | 219.5741 | 348.8 | 387.6 | 341 | 338.2 | 495.5 | 62 | 18.2 | 112.7 | 5.4 | 245 | 13.8 | 833.3 | 741 | 789 | 836.8 | 728.9 | 664.7 | 574.2 | 770.1 | 707.3 | 676.6 | 508.4 | 709.3 | 612.4 | 368.9 | 352.5 | 363.9 | 345.2 | 354.1 | 347.4 | 356.9 | 338.8
2090.2 | 1814.2 | 465 | 186 | 217.4233 | 348.6 | 386.5 | 341.5 | 339.1 | 492.9 | 61.9 | 18.2 | 112.7 | 6 | 241.6 | 13.6 | 836.1 | 747.1 | 800.1 | 839.4 | 731.2 | 665.3 | 584.8 | 782.7 | 720 | 680.6 | 508.2 | 713.7 | 612.5 | 368.9 | 352.5 | 364 | 345 | 354.1 | 347.3 | 356.9 | 338.8
2091.2 | 1815.2 | 141.3 | 56.52 | 66.0686 | 348.3 | 383.7 | 341.5 | 339.8 | 495.6 | 62 | 18.2 | 112.8 | 6.8 | 243.5 | 12.4 | 838.7 | 747.4 | 806 | 842.2 | 732.4 | 666.5 | 590.3 | 794.4 | 728.3 | 683.3 | 508.2 | 721 | 612 | 369 | 352.7 | 364 | 345 | 354 | 347.2 | 356.9 | 338.8
2092.2 | 1816.2 | -6.8 | 0 | 0 | 348.4 | 383.4 | 341.1 | 339.7 | 498.4 | 62.1 | 18.2 | 112.8 | 6.4 | 264.6 | 11.1 | 837.9 | 738.5 | 772.7 | 844.3 | 728.5 | 666 | 584.2 | 775.2 | 721.7 | 680.4 | 508.1 | 711.8 | 610.6 | 369 | 352.7 | 364.1 | 345 | 354 | 346.9 | 356.6 | 338.6
2093.2 | 1817.2 | -6.9 | 0 | 0 | 348 | 386 | 340.5 | 339.3 | 486.6 | 62.1 | 18.2 | 112.8 | 5.4 | 275.1 | 10.7 | 832.2 | 723.7 | 717.1 | 840.9 | 720.5 | 663.7 | 572.3 | 723.4 | 703.2 | 674.1 | 507.4 | 684.2 | 605.3 | 368.9 | 352 | 363.7 | 344.4 | 354 | 346.4 | 356.1 | 338.4
2094.2 | 1818.2 | -6.9 | 0 | 0 | 347.4 | 386.5 | 340.2 | 338.5 | 470.1 | 62.1 | 18.2 | 112.8 | 5 | 275.1 | 9 | 825.5 | 708.6 | 667.2 | 834.9 | 712.8 | 661.3 | 559.2 | 678.4 | 684.2 | 668 | 506.3 | 657.1 | 597.6 | 368.7 | 350.9 | 363.1 | 343.7 | 354 | 345.8 | 355.6 | 338.2
2095.2 | 1819.2 | -6.9 | 0 | 0 | 346.6 | 384.5 | 339.1 | 337.2 | 454.8 | 62 | 18.2 | 112.9 | 5.6 | 268.4 | 7.6 | 818.7 | 695.3 | 621.9 | 827.8 | 704.8 | 659 | 546.4 | 640.8 | 665.4 | 662 | 505.2 | 634.9 | 589.6 | 368.4 | 349.8 | 362.5 | 343.1 | 354 | 345.1 | 354.8 | 337.9
2096.2 | 1820.2 | -6.9 | 0 | 0 | 345.4 | 381.9 | 337.2 | 335.4 | 442 | 62 | 18.2 | 112.9 | 5.1 | 273.1 | 7.9 | 812.1 | 683.5 | 587.3 | 819.6 | 698.2 | 656.9 | 533.8 | 607.9 | 651.2 | 656.6 | 504 | 616.7 | 580.9 | 368.2 | 348.5 | 361.6 | 342.5 | 354.1 | 344.4 | 354.1 | 337.6
2097.2 | 1821.2 | -6.8 | 0 | 0 | 343.9 | 379.8 | 334.9 | 333.2 | 431 | 62 | 18.2 | 112.8 | 5.9 | 274.7 | 8.4 | 805.6 | 672.3 | 563.3 | 811 | 691.9 | 654.6 | 522.5 | 579.3 | 638.2 | 651 | 502.8 | 602.3 | 572.3 | 367.8 | 347 | 360.5 | 341.9 | 354 | 343.4 | 353.2 | 337.2
2098.2 | 1822.2 | -6.8 | 0 | 0 | 342.5 | 376.6 | 332.5 | 330.8 | 421 | 61.9 | 18.2 | 112.6 | 6 | 250 | 8.7 | 799.1 | 661.3 | 541.2 | 802.5 | 686.4 | 652.4 | 512.5 | 551.8 | 625.3 | 645.4 | 501.5 | 586.3 | 563.7 | 367.5 | 345.3 | 359.2 | 341.3 | 354 | 342.4 | 352.2 | 336.8
2099.2 | 1823.2 | -6.8 | 0 | 0 | 341.1 | 375 | 330.1 | 328.4 | 412.4 | 61.9 | 18.2 | 112.2 | 5.8 | 275.9 | 9.6 | 792.6 | 652.1 | 522.1 | 794 | 680.7 | 649.9 | 503.3 | 529.5 | 613.3 | 640.2 | 500.2 | 574.4 | 555.2 | 367.2 | 343.3 | 357.8 | 340.6 | 354 | 341.2 | 351 | 336.4
2100.2 | 1824.2 | -6.8 | 0 | 0 | 339.7 | 373.9 | 327.8 | 325.8 | 404.5 | 61.8 | 18.2 | 111.8 | 5.9 | 243 | 12.3 | 786.2 | 644.8 | 500 | 785.9 | 675 | 647.1 | 494.4 | 508.8 | 602 | 635.2 | 499 | 562.8 | 546.4 | 366.8 | 341.4 | 356.3 | 339.9 | 354 | 339.8 | 349.7 | 336
2101.2 | 1825.2 | -6.8 | 0 | 0 | 338 | 371.9 | 325.5 | 323.3 | 397 | 61.8 | 18.2 | 111.3 | 6.7 | 254.2 | 14.8 | 779.6 | 637.6 | 482.2 | 777.9 | 669.2 | 644.6 | 486.6 | 492.4 | 590.4 | 630.1 | 497.6 | 553.6 | 538.8 | 366.4 | 339.3 | 354.8 | 339.3 | 353.9 | 338.3 | 348.3 | 335.5
2102.2 | 1826.2 | -6.8 | 0 | 0 | 336 | 367.9 | 323.3 | 321.1 | 390 | 61.6 | 18.2 | 110.9 | 6.2 | 251.5 | 15.5 | 773.1 | 630.4 | 463 | 770.1 | 663.9 | 641.9 | 479 | 475.1 | 578.9 | 625.1 | 496.2 | 546.1 | 531.2 | 365.9 | 337.1 | 353.3 | 338.7 | 353.9 | 336.8 | 346.8 | 335.1
2103.2 | 1827.2 | -6.8 | 0 | 0 | 333.8 | 364.1 | 321.2 | 319 | 383.6 | 61.6 | 18.2 | 110.4 | 6.1 | 256.3 | 14.5 | 766.6 | 624 | 445.9 | 762.1 | 658.1 | 639.1 | 471.2 | 460 | 569 | 620.2 | 494.6 | 537.1 | 523.4 | 365.5 | 335 | 351.7 | 338.2 | 353.8 | 335.2 | 345.4 | 334.6
2104.2 | 1828.2 | -6.8 | 0 | 0 | 331.5 | 360.6 | 319.1 | 317 | 377.8 | 61.5 | 18.2 | 110 | 5 | 252.7 | 14.5 | 759.9 | 616.9 | 431.6 | 754.3 | 653.3 | 636.3 | 464.2 | 445.5 | 560 | 615.7 | 493 | 528.6 | 515.6 | 365.1 | 333 | 350.1 | 337.6 | 353.8 | 333.5 | 344 | 334.1
2105.2 | 1829.2 | -6.8 | 0 | 0 | 329.4 | 357.5 | 317 | 314.9 | 372.4 | 61.5 | 18.2 | 109.7 | 5.1 | 263.3 | 15.4 | 753.2 | 609.9 | 419 | 746.6 | 648.4 | 633.5 | 456.3 | 433 | 554.7 | 611 | 491.3 | 519.4 | 507.3 | 364.6 | 331.1 | 348.4 | 337 | 353.7 | 331.9 | 342.4 | 333.7
2106.2 | 1830.2 | -6.8 | 0 | 0 | 327.6 | 355.1 | 314.9 | 312.7 | 366.9 | 61.4 | 18.2 | 109.5 | 4.5 | 258 | 16.6 | 746.7 | 603 | 407.2 | 738.9 | 643.8 | 630.5 | 450.4 | 421.6 | 547.9 | 606.4 | 489.7 | 514.5 | 500.8 | 364.2 | 329.2 | 346.9 | 336.4 | 353.6 | 330.3 | 341 | 333.2
2107.2 | 1831.2 | -6.8 | 0 | 0 | 325.8 | 352 | 312.9 | 310.6 | 362.1 | 61.4 | 18.2 | 109.1 | 5 | 248.5 | 16.6 | 740.3 | 596.5 | 397 | 731.4 | 639.8 | 627.4 | 444.1 | 411.1 | 541.6 | 601.9 | 488.1 | 507.6 | 495.4 | 363.7 | 327.2 | 345.3 | 335.8 | 353.5 | 328.6 | 339.5 | 332.7
2108.2 | 1832.2 | -6.8 | 0 | 0 | 324.2 | 348.4 | 310.8 | 308.6 | 358.2 | 61.3 | 18.2 | 108.8 | 5.7 | 247.2 | 14.2 | 733.9 | 592.3 | 387 | 724.5 | 634.8 | 624.2 | 438.5 | 400.4 | 534.5 | 597.7 | 486.5 | 501.4 | 489.4 | 363.2 | 325.3 | 343.7 | 335.2 | 353.4 | 326.9 | 338 | 332.2
2109.2 | 1833.2 | -6.8 | 0 | 0 | 322.5 | 346 | 308.7 | 306.6 | 354.6 | 61.2 | 18.2 | 108.5 | 6.4 | 265.6 | 14.1 | 727.8 | 587.1 | 376.2 | 717.4 | 630.1 | 621 | 432.8 | 389 | 526.8 | 593.7 | 484.8 | 496.6 | 483.8 | 362.8 | 323.5 | 342.2 | 334.7 | 353.2 | 325.3 | 336.6 | 331.7
2110.2 | 1834.2 | -6.8 | 0 | 0 | 320.8 | 343.5 | 306.7 | 304.7 | 351.3 | 61.1 | 18.2 | 108.2 | 6 | 271.5 | 13.6 | 721.7 | 583.1 | 366.8 | 710.5 | 625.9 | 617.8 | 428.1 | 379.7 | 519.8 | 589.3 | 483.2 | 492.9 | 478.8 | 362.3 | 321.7 | 340.7 | 334.1 | 353.1 | 323.6 | 335.1 | 331.2
2111.2 | 1835.2 | -6.8 | 0 | 0 | 319.1 | 340.6 | 304.8 | 302.8 | 348.6 | 61.1 | 18.2 | 107.8 | 6.3 | 261 | 14.2 | 715.7 | 578.5 | 355.8 | 703.7 | 621.1 | 614.7 | 423.4 | 370.8 | 514 | 585.2 | 481.5 | 486.7 | 472.6 | 361.8 | 320 | 339.1 | 333.6 | 352.9 | 322 | 333.6 | 330.7
2112.2 | 1836.2 | -6.8 | 0 | 0 | 317.3 | 337.6 | 303 | 301 | 345.7 | 61 | 18.2 | 107.5 | 5.6 | 277.1 | 14.4 | 709.9 | 575 | 345.3 | 697 | 616.8 | 611.5 | 418.4 | 364.8 | 507.9 | 581.5 | 479.9 | 482.2 | 466.7 | 361.4 | 318.3 | 337.6 | 333 | 352.8 | 320.4 | 332.1 | 330.2
2113.2 | 1837.2 | -6.8 | 0 | 0 | 315.8 | 335.2 | 301.1 | 299.2 | 342.4 | 61 | 18.2 | 107.1 | 6.5 | 270.9 | 12.7 | 704 | 571.3 | 336.7 | 690.4 | 612.1 | 608.4 | 414.4 | 361.1 | 504.1 | 577.5 | 478.2 | 477.3 | 460 | 360.9 | 316.6 | 336.3 | 332.4 | 352.6 | 318.9 | 330.8 | 329.7
2114.2 | 1838.2 | -6.8 | 0 | 0 | 314.2 | 333.1 | 299.3 | 297.4 | 339 | 61 | 18.2 | 106.8 | 6.9 | 269.3 | 12 | 698.2 | 567.4 | 328.6 | 683.7 | 607.3 | 605.3 | 410 | 354.9 | 500.4 | 573.6 | 476.5 | 471.7 | 451.3 | 360.4 | 314.9 | 334.9 | 331.9 | 352.4 | 317.3 | 329.4 | 329.2
2115.2 | 1839.2 | -6.8 | 0 | 0 | 312.8 | 331.9 | 297.6 | 295.7 | 335.8 | 61 | 18.2 | 106.4 | 6.9 | 267.6 | 11.9 | 692.4 | 563.7 | 320.6 | 677.2 | 602.7 | 602.2 | 406.5 | 349.6 | 495 | 570 | 474.9 | 467.5 | 442.9 | 360 | 313.3 | 333.5 | 331.3 | 352.2 | 315.8 | 328.1 | 328.7
2116.2 | 1840.2 | -6.8 | 0 | 0 | 311.5 | 331 | 295.8 | 294.1 | 333.1 | 61 | 18.2 | 106 | 8.1 | 255.1 | 11.1 | 686.7 | 559.4 | 312.1 | 670.7 | 598.2 | 599.1 | 402.9 | 345.8 | 491.2 | 566.3 | 473.1 | 463.8 | 435.4 | 359.5 | 311.7 | 332 | 330.8 | 352 | 314.3 | 326.9 | 328.2
2117.2 | 1841.2 | -6.8 | 0 | 0 | 310.4 | 328.7 | 294.3 | 292.6 | 330.8 | 61 | 18.2 | 105.7 | 7.4 | 258.5 | 10 | 681.1 | 555.4 | 304.1 | 664.3 | 593.9 | 596 | 399.2 | 340 | 486.1 | 562.6 | 471.4 | 459.7 | 429.4 | 359.1 | 310.2 | 330.7 | 330.3 | 351.8 | 312.8 | 325.7 | 327.7
2118.2 | 1842.2 | -6.8 | 0 | 0 | 309 | 326.8 | 292.7 | 291.1 | 328.8 | 61 | 18.2 | 105.4 | 6.1 | 251.8 | 9.8 | 675.6 | 551.9 | 297.3 | 657.8 | 589.5 | 592.8 | 395.2 | 335.7 | 484.3 | 559.3 | 469.7 | 456.6 | 424.2 | 358.6 | 308.7 | 329.3 | 329.7 | 351.6 | 311.4 | 324.4 | 327.1
2119.2 | 1843.2 | -6.8 | 0 | 0 | 308 | 325.2 | 291.4 | 289.7 | 326.7 | 61 | 18.2 | 105.1 | 6.8 | 244.5 | 10.6 | 670.1 | 548.2 | 291.6 | 651.5 | 586.2 | 589.8 | 392.2 | 330.8 | 481.3 | 555.6 | 468.1 | 454.1 | 419.3 | 358.1 | 307.2 | 327.9 | 329.1 | 351.3 | 310 | 323.1 | 326.6
2120.2 | 1844.2 | -6.8 | 0 | 0 | 307.1 | 324.8 | 289.9 | 288.4 | 325.1 | 61 | 18.2 | 104.8 | 7.3 | 258.6 | 12.3 | 664.8 | 544.8 | 284.5 | 645.4 | 582.5 | 586.8 | 389.1 | 326.8 | 478.9 | 552.2 | 466.6 | 450.4 | 414 | 357.7 | 305.8 | 326.5 | 328.6 | 351.1 | 308.6 | 321.9 | 326.1
2121.2 | 1845.2 | -6.8 | 0 | 0 | 305.8 | 323.3 | 288.3 | 287.1 | 323.2 | 61 | 18.2 | 104.6 | 6.9 | 260.9 | 12.5 | 659.4 | 541.7 | 279.2 | 639.6 | 578.3 | 583.7 | 386.2 | 324.3 | 476.5 | 548.7 | 465.1 | 446.6 | 409.5 | 357.2 | 304.4 | 325.2 | 328 | 350.9 | 307.3 | 320.7 | 325.6
2122.2 | 1846.2 | -6.8 | 0 | 0 | 304.4 | 321.5 | 286.8 | 285.8 | 321.7 | 61 | 18.2 | 104.2 | 6.7 | 247.1 | 13.1 | 654.1 | 538.9 | 274.3 | 633.8 | 574.9 | 580.7 | 383.6 | 322.1 | 474.2 | 545.6 | 463.6 | 443.6 | 405.8 | 356.8 | 303 | 324 | 327.4 | 350.6 | 306 | 319.6 | 325.1
2123.2 | 1847.2 | -6.8 | 0 | 0 | 303.8 | 320.3 | 285.6 | 284.6 | 320.4 | 61 | 18.2 | 103.8 | 6.8 | 244.8 | 14.4 | 648.9 | 536 | 268.9 | 628.2 | 571.2 | 577.7 | 380.3 | 317.4 | 470.5 | 542.2 | 462.1 | 440 | 402.3 | 356.3 | 301.6 | 322.8 | 326.8 | 350.4 | 304.7 | 318.5 | 324.6
2124.2 | 1848.2 | -6.8 | 0 | 0 | 302.9 | 319.8 | 284.3 | 283.3 | 318.6 | 60.9 | 18.2 | 103.6 | 7.3 | 253 | 12.8 | 643.9 | 533.5 | 263.2 | 622.9 | 567.5 | 574.8 | 377.9 | 312.3 | 466.1 | 539.1 | 460.6 | 436.5 | 398.7 | 355.9 | 300.3 | 321.6 | 326.2 | 350.1 | 303.5 | 317.5 | 324.1
2125.2 | 1849.2 | -6.8 | 0 | 0 | 301.9 | 319.8 | 283.1 | 282.1 | 317.6 | 60.8 | 18.2 | 103.2 | 8 | 249.2 | 11.4 | 639 | 531.3 | 258.6 | 617.7 | 563.8 | 571.8 | 376 | 307.8 | 462.6 | 536.2 | 459 | 432.8 | 394.4 | 355.4 | 299.2 | 320.3 | 325.8 | 349.9 | 302.3 | 316.4 | 323.6
2126.2 | 1850.2 | -6.8 | 0 | 0 | 301.1 | 318.9 | 281.8 | 281 | 317.4 | 60.6 | 18.2 | 102.9 | 7.2 | 250.5 | 11.5 | 634.1 | 528.6 | 254.2 | 612.7 | 561.3 | 569 | 373.3 | 304.8 | 460 | 533.1 | 457.4 | 430.1 | 390.8 | 355 | 298.1 | 319 | 325.3 | 349.6 | 301.1 | 315.3 | 323.1
2127.2 | 1851.2 | -6.8 | 0 | 0 | 300.4 | 317.5 | 280.5 | 279.9 | 317.1 | 60.6 | 18.2 | 102.5 | 7.6 | 250.3 | 10.3 | 629.2 | 525.7 | 250.7 | 607.5 | 557.6 | 566.2 | 370.2 | 304.1 | 458.2 | 530.2 | 455.9 | 427 | 386.3 | 354.6 | 297 | 317.8 | 324.8 | 349.3 | 299.9 | 314.3 | 322.6
2128.2 | 1852.2 | -6.8 | 0 | 0 | 299.9 | 316.4 | 279.3 | 278.9 | 315.8 | 60.5 | 18.2 | 102.1 | 6.7 | 250.2 | 9.8 | 624.4 | 522.5 | 248.2 | 602.7 | 554.9 | 563.3 | 368 | 302.2 | 454.9 | 527.2 | 454.4 | 425.6 | 381.9 | 354.1 | 296 | 316.8 | 324.2 | 349.1 | 298.7 | 313.3 | 322.1
2129.2 | 1853.2 | -6.8 | 0 | 0 | 299.3 | 315.6 | 278.1 | 277.8 | 314 | 60.4 | 18.2 | 101.7 | 6.8 | 251.1 | 12 | 619.6 | 519.5 | 245.2 | 598 | 551.8 | 560.5 | 365.6 | 299.3 | 451.3 | 524.4 | 452.8 | 423.2 | 377.9 | 353.7 | 294.9 | 315.8 | 323.7 | 348.8 | 297.6 | 312.4 | 321.7
2130.2 | 1854.2 | -6.8 | 0 | 0 | 298.6 | 314.1 | 277 | 276.8 | 312.7 | 60.3 | 18.2 | 101.3 | 5.4 | 257.2 | 11.5 | 615.1 | 516.2 | 240.7 | 593.5 | 547.8 | 557.7 | 363.2 | 294.4 | 447.4 | 521.5 | 451.3 | 421 | 373.5 | 353.3 | 293.8 | 314.8 | 323.1 | 348.5 | 296.5 | 311.5 | 321.2
2131.2 | 1855.2 | -6.8 | 0 | 0 | 297.9 | 312.1 | 276 | 276 | 312.6 | 60.3 | 18.2 | 101 | 5.9 | 282.4 | 9.5 | 610.5 | 512.9 | 237.7 | 589.1 | 544.3 | 554.9 | 360.8 | 291.7 | 444.8 | 518.4 | 449.7 | 418.1 | 369 | 352.9 | 292.8 | 313.6 | 322.5 | 348.2 | 295.4 | 310.6 | 320.7
2132.2 | 1856.2 | -6.8 | 0 | 0 | 297 | 310.9 | 275 | 275 | 312.4 | 60.2 | 18.2 | 100.6 | 6.3 | 260.5 | 8.1 | 606 | 510.2 | 234.4 | 584.7 | 541.3 | 552.1 | 358.7 | 290.7 | 442.8 | 515.4 | 448.1 | 416.4 | 365.3 | 352.5 | 292 | 312.4 | 322 | 348 | 294.5 | 309.7 | 320.2
2133.2 | 1857.2 | -6.8 | 0 | 0 | 296.3 | 310.1 | 273.9 | 274 | 311.7 | 60.1 | 18.2 | 100.3 | 7.2 | 251.1 | 9.5 | 601.7 | 507.9 | 230.9 | 580.6 | 537.9 | 549.4 | 356 | 288.4 | 440.8 | 512.5 | 446.6 | 414.7 | 361.8 | 352.1 | 291.1 | 311.3 | 321.5 | 347.7 | 293.5 | 308.9 | 319.7
2134.2 | 1858.2 | -6.8 | 0 | 0 | 295.8 | 308.9 | 272.8 | 272.9 | 310.1 | 59.9 | 18.2 | 99.9 | 6.3 | 282.1 | 10.2 | 597.5 | 505.4 | 228.5 | 576.7 | 535 | 546.7 | 353.7 | 285.5 | 437.8 | 509.9 | 445.1 | 413.1 | 358.3 | 351.7 | 290.3 | 310.4 | 321 | 347.4 | 292.6 | 308.2 | 319.2
2135.2 | 1859.2 | -6.8 | 0 | 0 | 295.3 | 308.9 | 271.8 | 272 | 309.8 | 59.8 | 18.2 | 99.6 | 4.7 | 250.4 | 11.7 | 593.3 | 502.4 | 226.5 | 572.8 | 532.4 | 543.9 | 351.3 | 280.7 | 435.6 | 507.7 | 443.6 | 409.8 | 355.1 | 351.3 | 289.5 | 309.6 | 320.5 | 347.1 | 291.5 | 307.5 | 318.7
2136.2 | 1860.2 | -6.8 | 0 | 0 | 294.7 | 308.8 | 271 | 271.2 | 310 | 59.7 | 18.2 | 99.3 | 4 | 256.5 | 12.3 | 589.2 | 500 | 224.2 | 569.1 | 529.9 | 541.2 | 349.9 | 276.8 | 432.4 | 505.4 | 442.1 | 405.9 | 351.8 | 350.9 | 288.6 | 308.8 | 320 | 346.8 | 290.6 | 306.6 | 318.2
2137.2 | 1861.2 | -6.8 | 0 | 0 | 293.8 | 308 | 270.2 | 270.3 | 310.1 | 59.6 | 18.2 | 99 | 3.7 | 257.3 | 11.3 | 585.3 | 497.5 | 221.8 | 565.5 | 527 | 538.5 | 348.8 | 272.9 | 428.3 | 502.3 | 440.6 | 403.5 | 348.8 | 350.5 | 287.7 | 308 | 319.5 | 346.5 | 289.6 | 305.8 | 317.7
2138.2 | 1862.2 | -6.8 | 0 | 0 | 293.1 | 307.4 | 269.4 | 269.4 | 309 | 59.5 | 18.2 | 98.7 | 3.9 | 271.2 | 11.3 | 581.5 | 495.9 | 219 | 561.8 | 524.4 | 535.8 | 346.8 | 269.8 | 426.1 | 500.2 | 439.1 | 400.8 | 345.5 | 350 | 286.9 | 307.2 | 319.1 | 346.2 | 288.7 | 305 | 317.3
2139.2 | 1863.2 | -6.8 | 0 | 0 | 292.5 | 308.2 | 268.6 | 268.6 | 305.3 | 59.4 | 18.2 | 98.5 | 4 | 278 | 12 | 577.8 | 494 | 215.5 | 558.2 | 521.2 | 533.2 | 345.4 | 266.2 | 424.1 | 497.7 | 437.7 | 398 | 342.1 | 349.6 | 286.1 | 306.5 | 318.6 | 345.9 | 287.8 | 304.2 | 316.8
2140.2 | 1864.2 | -6.8 | 0 | 0 | 291.8 | 308.2 | 267.8 | 267.9 | 300.5 | 59.3 | 18.2 | 98.2 | 4.1 | 286.1 | 12.4 | 574.1 | 491.8 | 212.3 | 554.5 | 518.5 | 530.5 | 344.3 | 263.5 | 422.3 | 495.3 | 436.2 | 395.8 | 339 | 349.2 | 285.2 | 305.6 | 318.1 | 345.7 | 287 | 303.5 | 316.3
2141.2 | 1865.2 | -6.8 | 0 | 0 | 291.4 | 307.8 | 267 | 267.1 | 296.3 | 59.2 | 18.2 | 97.9 | 4.6 | 283.6 | 11.3 | 570.5 | 490.2 | 209.3 | 551 | 515.8 | 528 | 343.8 | 263.2 | 421.4 | 493 | 434.8 | 394.1 | 336.2 | 348.8 | 284.4 | 304.7 | 317.6 | 345.4 | 286.1 | 302.7 | 315.8
2142.2 | 1866.2 | -6.8 | 0 | 0 | 290.8 | 307.7 | 266.4 | 266.3 | 293.1 | 59.1 | 18.2 | 97.6 | 4.7 | 253.2 | 10.7 | 566.9 | 489 | 206.7 | 547.5 | 513 | 525.5 | 343.1 | 261.5 | 420.2 | 490.6 | 433.4 | 391.8 | 333.8 | 348.4 | 283.7 | 303.8 | 317 | 345.1 | 285.2 | 301.9 | 315.4
2143.2 | 1867.2 | -6.8 | 0 | 0 | 290.1 | 308.3 | 265.7 | 265.5 | 290.3 | 59 | 18.2 | 97.4 | 5.1 | 279.5 | 11 | 563.4 | 487.6 | 204.6 | 544 | 510.3 | 522.9 | 342 | 258.1 | 418.3 | 488 | 432 | 389.8 | 331 | 347.9 | 282.9 | 302.9 | 316.5 | 344.8 | 284.3 | 301.2 | 314.9
2144.2 | 1868.2 | -6.8 | 0 | 0 | 289.5 | 307.8 | 264.9 | 264.6 | 287.9 | 59 | 18.3 | 97.1 | 5 | 278.9 | 10.1 | 560 | 485.5 | 201.8 | 540.7 | 507 | 520.5 | 339.4 | 255.1 | 415.8 | 485.6 | 430.5 | 387.9 | 328.4 | 347.6 | 282.2 | 302.1 | 316 | 344.5 | 283.4 | 300.6 | 314.4
2145.2 | 1869.2 | -6.8 | 0 | 0 | 289 | 306 | 264.2 | 263.8 | 285.6 | 58.9 | 18.3 | 96.9 | 5 | 270.9 | 9.8 | 556.6 | 483.1 | 199.5 | 537.2 | 504.2 | 517.9 | 337.3 | 252.4 | 413.4 | 483.3 | 429.2 | 386.1 | 326.1 | 347.2 | 281.5 | 301.4 | 315.5 | 344.2 | 282.6 | 299.9 | 313.9
2146.2 | 1870.2 | -6.8 | 0 | 0 | 288.3 | 305.3 | 263.5 | 263.1 | 283.1 | 58.8 | 18.3 | 96.7 | 5 | 266.6 | 9.2 | 553.2 | 480.6 | 197.9 | 533.9 | 502.4 | 515.5 | 335.4 | 252.2 | 411.9 | 480.9 | 427.9 | 384.4 | 324 | 346.8 | 280.7 | 300.8 | 315 | 343.9 | 281.8 | 299.3 | 313.4
2147.2 | 1871.2 | -6.8 | 0 | 0 | 287.7 | 305.8 | 262.8 | 262.5 | 281 | 58.8 | 18.3 | 96.4 | 4.7 | 265.9 | 10 | 549.8 | 479.1 | 195.5 | 530.6 | 499.9 | 513 | 334.3 | 250 | 410.6 | 478.5 | 426.5 | 382.2 | 321.8 | 346.4 | 280 | 300.1 | 314.4 | 343.6 | 281 | 298.6 | 312.9
2148.2 | 1872.2 | -6.8 | 0 | 0 | 287.2 | 304.9 | 262.2 | 261.9 | 279 | 58.7 | 18.3 | 96.2 | 4.3 | 267.4 | 11.1 | 546.5 | 477.4 | 193.3 | 527.3 | 497.1 | 510.6 | 333.1 | 247.1 | 408.5 | 476.1 | 425.2 | 380.1 | 319.4 | 346 | 279.3 | 299.5 | 313.9 | 343.3 | 280.2 | 298 | 312.5
2149.2 | 1873.2 | -6.8 | 0 | 0 | 286.7 | 304.1 | 261.5 | 261.4 | 277.3 | 58.7 | 18.3 | 96 | 4.6 | 265.2 | 11.4 | 543.3 | 475.4 | 190.9 | 523.8 | 495.1 | 508.2 | 331.2 | 244.7 | 406.6 | 473.7 | 423.9 | 377.9 | 317.1 | 345.6 | 278.5 | 298.9 | 313.3 | 343 | 279.4 | 297.3 | 312
2150.2 | 1874.2 | -6.8 | 0 | 0 | 285.8 | 303.7 | 260.8 | 260.8 | 275.8 | 58.6 | 18.3 | 95.9 | 5.4 | 246.5 | 11.3 | 540.1 | 473.4 | 189.1 | 520.5 | 492.9 | 505.8 | 330.1 | 241.8 | 404.7 | 471.4 | 422.6 | 374.9 | 315.1 | 345.2 | 277.7 | 298.2 | 312.9 | 342.7 | 278.6 | 296.5 | 311.5
2151.2 | 1875.2 | -6.8 | 0 | 0 | 285.1 | 303.3 | 260.1 | 260.2 | 274.8 | 58.4 | 18.3 | 95.7 | 5 | 246.6 | 11.8 | 536.8 | 471.4 | 187.3 | 517.5 | 490.5 | 503.4 | 328.1 | 240.1 | 402.9 | 469.1 | 421.3 | 373.2 | 313.2 | 344.8 | 277 | 297.5 | 312.4 | 342.4 | 277.9 | 295.8 | 311
2152.2 | 1876.2 | -6.8 | 0 | 0 | 284.6 | 302.7 | 259.4 | 259.6 | 273.6 | 58.3 | 18.3 | 95.5 | 5.4 | 253.4 | 11 | 533.7 | 470.3 | 185.4 | 514.2 | 488.4 | 501.2 | 326.6 | 239.8 | 402.1 | 467 | 420.1 | 371 | 311.3 | 344.4 | 276.3 | 296.9 | 312 | 342.1 | 277.1 | 295.2 | 310.6
2153.2 | 1877.2 | -6.8 | 0 | 0 | 284.2 | 302 | 258.7 | 259 | 272.2 | 58.2 | 18.3 | 95.4 | 5.3 | 256.3 | 10 | 530.5 | 468.9 | 183.9 | 511.2 | 486.2 | 499 | 325.9 | 239.7 | 400.6 | 465.1 | 418.8 | 368.7 | 309.2 | 344 | 275.5 | 296.2 | 311.5 | 341.8 | 276.3 | 294.6 | 310.1
2154.2 | 1878.2 | -6.8 | 0 | 0 | 283.5 | 300.7 | 258.2 | 258.5 | 270.9 | 58.1 | 18.3 | 95.2 | 5.8 | 259 | 10.4 | 527.4 | 467.7 | 182.5 | 508 | 484.3 | 496.8 | 324.4 | 239.2 | 399.4 | 462.9 | 417.5 | 366.5 | 307.4 | 343.6 | 274.8 | 295.3 | 310.9 | 341.5 | 275.6 | 293.9 | 309.6
2155.2 | 1879.2 | -6.8 | 0 | 0 | 283 | 299.7 | 257.6 | 258 | 269.8 | 58.1 | 18.3 | 95 | 5.9 | 261.7 | 10.7 | 524.3 | 466.4 | 180.8 | 505.4 | 482.2 | 494.5 | 323.4 | 238.8 | 397.4 | 460.9 | 416.2 | 365 | 305.8 | 343.3 | 274.1 | 294.4 | 310.4 | 341.2 | 274.9 | 293.2 | 309.1
2156.2 | 1880.2 | -6.8 | 0 | 0 | 282.7 | 297.9 | 257 | 257.3 | 268.9 | 58 | 18.3 | 94.7 | 5.6 | 260.7 | 10.1 | 521.3 | 465.5 | 179.3 | 502.7 | 480 | 492.3 | 321.7 | 236.8 | 395.1 | 458.7 | 415 | 363 | 303.8 | 342.9 | 273.4 | 293.7 | 309.9 | 340.9 | 274.3 | 292.5 | 308.7
2157.2 | 1881.2 | -6.8 | 0 | 0 | 282.5 | 297.3 | 256.4 | 256.7 | 267.8 | 57.9 | 18.3 | 94.5 | 5.5 | 258 | 9.7 | 518.3 | 464.6 | 177.9 | 500.2 | 477.9 | 490.1 | 320.4 | 233.9 | 392.6 | 456.6 | 413.8 | 361.3 | 301.4 | 342.5 | 272.7 | 292.9 | 309.5 | 340.6 | 273.6 | 291.8 | 308.2
2158.2 | 1882.2 | -6.8 | 0 | 0 | 282.2 | 297.1 | 255.7 | 256 | 267 | 57.7 | 18.3 | 94.3 | 5.5 | 248.2 | 10.7 | 515.4 | 463.3 | 177 | 497.8 | 476.1 | 487.8 | 319.3 | 231.7 | 389.8 | 454.7 | 412.7 | 357.1 | 298.9 | 342.1 | 272.1 | 292.1 | 308.9 | 340.3 | 273 | 291.1 | 307.7
2159.2 | 1883.2 | -6.8 | 0 | 0 | 281.8 | 297.6 | 255 | 255.4 | 266.2 | 57.6 | 18.3 | 94.1 | 4.9 | 244.7 | 10.2 | 512.6 | 460.8 | 176.2 | 495 | 474.1 | 485.6 | 317.9 | 229.6 | 387.5 | 452.5 | 411.6 | 356.1 | 297 | 341.7 | 271.4 | 291.3 | 308.4 | 340 | 272.3 | 290.4 | 307.2
2160.2 | 1884.2 | -6.8 | 0 | 0 | 281.5 | 297.6 | 254.4 | 254.9 | 265.4 | 57.4 | 18.3 | 93.9 | 4.9 | 248.3 | 9.9 | 509.8 | 458.4 | 175.2 | 492.5 | 472.2 | 483.3 | 316.8 | 227.4 | 385.2 | 450.6 | 410.5 | 354.4 | 295.5 | 341.3 | 270.8 | 290.5 | 307.8 | 339.7 | 271.6 | 289.9 | 306.8
2161.2 | 1885.2 | -6.8 | 0 | 0 | 281 | 297.6 | 253.9 | 254.2 | 264.5 | 57.4 | 18.3 | 93.7 | 4.9 | 254.9 | 10 | 507 | 456.1 | 173.9 | 490 | 470 | 481.1 | 315.7 | 225.2 | 382.3 | 449 | 409.4 | 353 | 293.5 | 340.9 | 270.1 | 289.7 | 307.3 | 339.4 | 271 | 289.2 | 306.3
2162.2 | 1886.2 | -6.8 | 0 | 0 | 280.4 | 296.5 | 253.3 | 253.5 | 263.7 | 57.3 | 18.3 | 93.6 | 4.6 | 244.2 | 9.1 | 504.3 | 455.3 | 171.5 | 487.5 | 467.8 | 479 | 315.8 | 223.7 | 379.2 | 447.2 | 408.3 | 350.7 | 291.2 | 340.6 | 269.5 | 289 | 306.8 | 339.1 | 270.4 | 288.6 | 305.8
2163.2 | 1887.2 | -6.8 | 0 | 0 | 279.9 | 295.9 | 252.7 | 252.9 | 263 | 57.2 | 18.3 | 93.4 | 4.7 | 242 | 7.7 | 501.6 | 454 | 169.2 | 484.7 | 465.5 | 476.8 | 314.8 | 222.6 | 374.4 | 445.2 | 407.1 | 348.9 | 289.4 | 340.2 | 268.9 | 288.4 | 306.4 | 338.9 | 269.8 | 288 | 305.4
2164.2 | 1888.2 | -6.8 | 0 | 0 | 279.4 | 294.1 | 252.2 | 252.5 | 262.4 | 57.2 | 18.3 | 93.2 | 4.6 | 239.1 | 7.1 | 499.1 | 452.9 | 167.2 | 482 | 462.8 | 474.7 | 313.7 | 222.8 | 371.7 | 443.2 | 406 | 347.4 | 287.6 | 339.8 | 268.2 | 287.7 | 305.9 | 338.6 | 269.3 | 287.3 | 305
2165.2 | 1889.2 | -6.8 | 0 | 0 | 278.7 | 292.3 | 251.7 | 252 | 262 | 57.1 | 18.3 | 93 | 4.5 | 240.5 | 6.5 | 496.4 | 452 | 165.5 | 479.1 | 460.6 | 472.7 | 312.7 | 221.2 | 372 | 441.2 | 405 | 346.5 | 285.8 | 339.5 | 267.5 | 286.9 | 305.3 | 338.3 | 268.6 | 286.8 | 304.5
2166.2 | 1890.2 | -6.8 | 0 | 0 | 278 | 291.6 | 251.2 | 251.5 | 261.5 | 57 | 18.3 | 92.8 | 4.1 | 249.1 | 6.6 | 493.8 | 451.8 | 164 | 476.1 | 458.3 | 470.5 | 311.7 | 219.8 | 370.2 | 439.4 | 403.9 | 344.9 | 283.8 | 339.1 | 266.9 | 286.2 | 304.9 | 338 | 268.1 | 286.2 | 304
2167.2 | 1891.2 | -6.8 | 0 | 0 | 277.3 | 292 | 250.7 | 251 | 261 | 56.9 | 18.3 | 92.6 | 4.1 | 258.7 | 6.6 | 491.3 | 450.6 | 162.8 | 473.3 | 456 | 468.5 | 310.6 | 218.3 | 368 | 437.6 | 402.9 | 343.5 | 281.7 | 338.7 | 266.3 | 285.6 | 304.4 | 337.7 | 267.5 | 285.7 | 303.6
2168.2 | 1892.2 | -6.8 | 0 | 0 | 276.5 | 291.1 | 250.2 | 250.5 | 260.4 | 56.7 | 18.3 | 92.5 | 4.7 | 245.5 | 6.3 | 488.7 | 449.3 | 161.2 | 470.5 | 454.3 | 466.5 | 309.8 | 217.5 | 367.5 | 435.5 | 401.9 | 343 | 280.1 | 338.4 | 265.7 | 285.1 | 304 | 337.4 | 267 | 285.2 | 303.2
2169.2 | 1893.2 | -6.8 | 0 | 0 | 276.1 | 290 | 249.6 | 250 | 259.6 | 56.6 | 18.3 | 92.3 | 4.7 | 255.3 | 7.3 | 486.1 | 446.7 | 160 | 468 | 452.1 | 464.5 | 308.6 | 216.5 | 367.2 | 433.8 | 400.9 | 341 | 278.2 | 338 | 265.2 | 284.5 | 303.6 | 337.1 | 266.4 | 284.6 | 302.7
2170.2 | 1894.2 | -6.8 | 0 | 0 | 275.7 | 289 | 249.1 | 249.4 | 259 | 56.5 | 18.3 | 92.2 | 4.5 | 248.5 | 8.7 | 483.5 | 445 | 159.1 | 465.6 | 450.3 | 462.5 | 306.3 | 214.7 | 365.8 | 431.8 | 399.8 | 338.9 | 276.2 | 337.6 | 264.5 | 283.9 | 303 | 336.8 | 265.9 | 284.1 | 302.3
2171.2 | 1895.2 | -6.8 | 0 | 0 | 275.1 | 288.6 | 248.5 | 248.8 | 258.2 | 56.4 | 18.3 | 92.2 | 5 | 254.1 | 9.6 | 481 | 442.6 | 158.1 | 462.9 | 448.4 | 460.6 | 306.5 | 213.1 | 364 | 430 | 398.8 | 336.5 | 274.4 | 337.3 | 263.9 | 283.3 | 302.5 | 336.5 | 265.3 | 283.5 | 301.8
2172.2 | 1896.2 | -6.8 | 0 | 0 | 274.6 | 289.1 | 248 | 248.2 | 258 | 56.3 | 18.3 | 92.1 | 5.4 | 262.2 | 11.5 | 478.5 | 439.4 | 157.3 | 460.4 | 446.5 | 458.6 | 305.8 | 211.7 | 362.3 | 428.3 | 397.9 | 334.5 | 272.7 | 336.9 | 263.3 | 282.8 | 301.9 | 336.2 | 264.7 | 283 | 301.3
2173.2 | 1897.2 | -6.8 | 0 | 0 | 274.3 | 288.7 | 247.6 | 247.6 | 257.4 | 56.2 | 18.3 | 92 | 5.1 | 253.7 | 12.1 | 476 | 438.1 | 156.5 | 458 | 444.9 | 456.7 | 304.9 | 209.7 | 360.5 | 426.6 | 396.9 | 333.8 | 271.7 | 336.6 | 262.6 | 282.3 | 301.4 | 335.9 | 264.2 | 282.5 | 300.9
2174.2 | 1898.2 | -6.8 | 0 | 0 | 274.1 | 287.7 | 247.2 | 247 | 256.9 | 56.1 | 18.3 | 91.8 | 5.2 | 265.9 | 10.4 | 473.6 | 436.9 | 155.1 | 455.5 | 443.1 | 454.8 | 304.9 | 208.2 | 359.1 | 424.7 | 396 | 333.2 | 270.3 | 336.2 | 262.1 | 281.8 | 300.9 | 335.6 | 263.8 | 282 | 300.4
2175.2 | 1899.2 | -6.8 | 0 | 0 | 274.1 | 287.2 | 246.8 | 246.6 | 256.3 | 56 | 18.3 | 91.7 | 5.9 | 255.5 | 8.6 | 471.2 | 435.8 | 153.5 | 453 | 440.8 | 452.9 | 302.3 | 207.2 | 356.4 | 423.1 | 395.1 | 332.5 | 268.7 | 335.8 | 261.7 | 281.4 | 300.5 | 335.3 | 263.2 | 281.5 | 300
2176.2 | 1900.2 | -6.8 | 0 | 0 | 273.7 | 286.4 | 246.2 | 246.2 | 255.6 | 55.9 | 18.3 | 91.5 | 5.7 | 267.5 | 9.3 | 468.8 | 434.7 | 153 | 450.9 | 438.8 | 451 | 302.2 | 205.7 | 353.8 | 421.3 | 394.1 | 331.6 | 267.3 | 335.5 | 261.3 | 281 | 300.1 | 335 | 262.7 | 281 | 299.5
2177.2 | 1901.2 | -6.8 | 0 | 0 | 273.2 | 286.7 | 245.7 | 245.8 | 254.9 | 55.9 | 18.3 | 91.4 | 5.4 | 261.9 | 10 | 466.4 | 434 | 152.5 | 448.7 | 437.1 | 449 | 300.5 | 204.2 | 351.5 | 419.4 | 393.2 | 330.7 | 266 | 335.1 | 260.8 | 280.6 | 299.7 | 334.7 | 262.1 | 280.6 | 299.1
2178.2 | 1902.2 | -6.8 | 0 | 0 | 272.8 | 286.4 | 245.2 | 245.3 | 254.1 | 55.8 | 18.3 | 91.3 | 4.8 | 257 | 10.1 | 464.1 | 432.3 | 151.9 | 446.4 | 435.5 | 447.2 | 300 | 202.8 | 349.1 | 417.9 | 392.3 | 329.6 | 264.6 | 334.8 | 260.2 | 280.1 | 299.2 | 334.4 | 261.6 | 280.1 | 298.6
2179.2 | 1903.2 | -6.8 | 0 | 0 | 272.3 | 286.2 | 244.8 | 244.8 | 253.3 | 55.8 | 18.4 | 91.2 | 5.3 | 264.6 | 10.2 | 461.8 | 429.8 | 151.3 | 444.3 | 433.9 | 445.3 | 299.6 | 202 | 347.8 | 416.1 | 391.4 | 328.2 | 262.6 | 334.4 | 259.6 | 279.6 | 298.7 | 334.1 | 261 | 279.6 | 298.2
2180.2 | 1904.2 | -6.8 | 0 | 0 | 271.9 | 285.7 | 244.5 | 244.3 | 252.8 | 55.7 | 18.4 | 91.1 | 5.3 | 261.4 | 11.8 | 459.6 | 426.6 | 150.5 | 442.2 | 432.2 | 443.5 | 298.7 | 200.7 | 347.1 | 414.3 | 390.5 | 327.3 | 260.4 | 334 | 259.1 | 279.1 | 298.1 | 333.8 | 260.5 | 279 | 297.8
2181.2 | 1905.2 | -6.8 | 0 | 0 | 271.4 | 285.7 | 244.2 | 243.9 | 252.6 | 55.7 | 18.4 | 91 | 6.2 | 260 | 12 | 457.4 | 424.4 | 150 | 440.2 | 430.6 | 441.7 | 297.7 | 199.2 | 345.7 | 412.6 | 389.5 | 326.8 | 258.2 | 333.7 | 258.6 | 278.5 | 297.7 | 333.5 | 260 | 278.4 | 297.3
2182.2 | 1906.2 | -6.8 | 0 | 0 | 270.7 | 285 | 243.7 | 243.3 | 252.2 | 55.6 | 18.4 | 90.9 | 6.4 | 255.7 | 11.6 | 455.2 | 422.9 | 149.4 | 438.3 | 428.9 | 439.8 | 296.8 | 198.1 | 344.3 | 411.2 | 388.6 | 326.2 | 256.5 | 333.3 | 258.1 | 278.2 | 297.3 | 333.2 | 259.4 | 278 | 296.8
2183.2 | 1907.2 | -6.8 | 0 | 0 | 270.2 | 284 | 243.1 | 242.8 | 251.5 | 55.5 | 18.4 | 90.8 | 6.6 | 256 | 11.6 | 453.1 | 421.7 | 148.7 | 436.3 | 427.3 | 438 | 295.4 | 197.5 | 343.5 | 409.8 | 387.7 | 324.2 | 255.5 | 333 | 257.6 | 277.8 | 296.9 | 332.9 | 258.9 | 277.4 | 296.4
2184.2 | 1908.2 | -6.8 | 0 | 0 | 269.9 | 283 | 242.6 | 242.4 | 250.9 | 55.4 | 18.4 | 90.7 | 6.6 | 246.2 | 11.1 | 451 | 419.5 | 148.1 | 434.4 | 425.6 | 436.2 | 295.6 | 196.4 | 342.7 | 408.3 | 386.8 | 321.9 | 253.9 | 332.6 | 257.2 | 277.4 | 296.3 | 332.6 | 258.4 | 276.8 | 295.9
2185.2 | 1909.2 | -6.8 | 0 | 0 | 269.5 | 282.3 | 242.2 | 242 | 250.3 | 55.2 | 18.4 | 90.6 | 5.9 | 262.8 | 10.1 | 449 | 418.1 | 147.6 | 432.5 | 424 | 434.5 | 294.7 | 195.3 | 341.5 | 406.6 | 385.9 | 321.2 | 252.3 | 332.2 | 256.7 | 277 | 295.8 | 332.3 | 258 | 276.4 | 295.5
2186.2 | 1910.2 | -6.8 | 0 | 0 | 269.3 | 281.7 | 241.8 | 241.5 | 249.7 | 55.1 | 18.4 | 90.4 | 5.2 | 254.2 | 9.6 | 447 | 416.9 | 147 | 430.7 | 422.4 | 432.7 | 294.3 | 194 | 339.5 | 405 | 385.1 | 320.8 | 250.7 | 331.9 | 256.2 | 276.7 | 295.4 | 332 | 257.5 | 276 | 295
2187.2 | 1911.2 | -6.8 | 0 | 0 | 269.2 | 280.2 | 241.4 | 241.1 | 249.2 | 55 | 18.4 | 90.3 | 6.1 | 257.3 | 9.8 | 445 | 415.8 | 146.5 | 429 | 420.9 | 430.9 | 293.2 | 192.5 | 338.4 | 403.3 | 384.1 | 320.1 | 249 | 331.5 | 255.8 | 276.3 | 295 | 331.7 | 257.1 | 275.5 | 294.6
2188.2 | 1912.2 | -6.8 | 0 | 0 | 268.8 | 278.3 | 241.1 | 240.8 | 248.7 | 54.9 | 18.4 | 90.1 | 6.6 | 254.7 | 9.2 | 443.1 | 414.8 | 145.5 | 427.3 | 419.6 | 429.2 | 293.7 | 191.3 | 337.4 | 402.1 | 383.2 | 318.8 | 247.3 | 331.2 | 255.3 | 275.9 | 294.5 | 331.4 | 256.6 | 274.9 | 294.2
2189.2 | 1913.2 | -6.8 | 0 | 0 | 268.1 | 276.7 | 240.7 | 240.5 | 248.2 | 54.8 | 18.4 | 89.9 | 6.2 | 268.3 | 8.3 | 441.1 | 413 | 144.3 | 425.8 | 418.2 | 427.5 | 292.6 | 190.5 | 335.7 | 400.7 | 382.3 | 317.5 | 245.5 | 330.8 | 254.8 | 275.5 | 294 | 331.1 | 256.1 | 274.3 | 293.7
2190.2 | 1914.2 | -6.8 | 0 | 0 | 267.9 | 275.6 | 240.3 | 240 | 247.9 | 54.8 | 18.4 | 89.7 | 6.3 | 251.3 | 9.2 | 439.2 | 410.2 | 142.9 | 423.9 | 416.8 | 425.8 | 291.2 | 190 | 334.8 | 399.2 | 381.4 | 316.7 | 243.6 | 330.5 | 254.3 | 275.1 | 293.6 | 330.8 | 255.6 | 273.9 | 293.3
2191.2 | 1915.2 | -6.8 | 0 | 0 | 267.4 | 274.1 | 239.9 | 239.5 | 247.5 | 54.7 | 18.4 | 89.5 | 6.4 | 242.9 | 11.6 | 437.2 | 407.4 | 141.3 | 422.2 | 415.6 | 424.1 | 290 | 188 | 333.3 | 397.4 | 380.6 | 315.5 | 242.1 | 330.1 | 253.8 | 274.7 | 293.1 | 330.5 | 255.1 | 273.5 | 292.8
2192.2 | 1916.2 | -6.8 | 0 | 0 | 266.8 | 273 | 239.5 | 239 | 247 | 54.6 | 18.4 | 89.3 | 6.4 | 247.9 | 11.2 | 435.3 | 406.3 | 140.1 | 420.7 | 413.8 | 422.4 | 289.1 | 186.3 | 333.3 | 395.8 | 379.7 | 314.4 | 240.7 | 329.8 | 253.4 | 274.4 | 292.7 | 330.2 | 254.6 | 273.1 | 292.4
2193.2 | 1917.2 | -6.8 | 0 | 0 | 266 | 271.5 | 239.1 | 238.5 | 246.5 | 54.6 | 18.4 | 89.1 | 6.8 | 242.7 | 10.6 | 433.4 | 404.7 | 139 | 418.9 | 411.7 | 420.8 | 287.5 | 185.2 | 333.5 | 394.5 | 378.9 | 313.5 | 239.2 | 329.4 | 252.9 | 274 | 292.2 | 329.9 | 254.2 | 272.8 | 292
2194.2 | 1918.2 | -6.8 | 0 | 0 | 265.3 | 270.7 | 238.5 | 238 | 246.2 | 54.5 | 18.4 | 88.9 | 6.9 | 251.7 | 10.8 | 431.6 | 403.1 | 137.9 | 417.2 | 410.1 | 419.1 | 287.4 | 184.2 | 330.7 | 393.1 | 378.1 | 312.3 | 238 | 329 | 252.5 | 273.5 | 291.8 | 329.6 | 253.7 | 272.3 | 291.6
2195.2 | 1919.2 | -6.8 | 0 | 0 | 265.2 | 270.4 | 238 | 237.5 | 246 | 54.4 | 18.4 | 88.7 | 7.5 | 242.8 | 9.8 | 429.7 | 401.8 | 136.6 | 415.5 | 408.4 | 417.7 | 285.1 | 183.9 | 330.4 | 391.7 | 377.2 | 310.7 | 236.9 | 328.7 | 252 | 273.1 | 291.3 | 329.3 | 253.2 | 271.9 | 291.2
2196.2 | 1920.2 | -6.8 | 0 | 0 | 265.5 | 269.7 | 237.6 | 237.1 | 245.5 | 54.3 | 18.4 | 88.5 | 7.3 | 241.4 | 11.9 | 427.9 | 400.6 | 135.6 | 413.9 | 406.7 | 416.2 | 285.6 | 182.9 | 330.1 | 390.4 | 376.5 | 310.1 | 235.5 | 328.3 | 251.6 | 272.7 | 290.9 | 329 | 252.8 | 271.5 | 290.8
2197.2 | 1921.2 | -6.8 | 0 | 0 | 265.5 | 268.8 | 237.2 | 236.7 | 245 | 54.1 | 18.4 | 88.3 | 6.7 | 242.9 | 11.7 | 426 | 398.8 | 134.4 | 411.9 | 405.3 | 414.7 | 285.3 | 181.7 | 328.3 | 389.4 | 375.7 | 309.4 | 234 | 328 | 251.1 | 272.3 | 290.5 | 328.7 | 252.4 | 271 | 290.3
2198.2 | 1922.2 | -6.8 | 0 | 0 | 265.2 | 267.8 | 236.8 | 236.5 | 244.7 | 54 | 18.4 | 88.2 | 4.6 | 247.6 | 14.1 | 424 | 397.8 | 133.4 | 410 | 403.3 | 413.1 | 285.7 | 180.5 | 325.5 | 387.9 | 375 | 308.6 | 232.9 | 327.6 | 250.7 | 271.9 | 290 | 328.4 | 252 | 270.5 | 289.9
2199.2 | 1923.2 | -6.8 | 0 | 0 | 265.1 | 267.5 | 236.5 | 236.3 | 244.5 | 54 | 18.4 | 88.1 | 4.6 | 240.7 | 15.7 | 422.1 | 396.6 | 132.5 | 408.2 | 401.5 | 411.5 | 284.7 | 179.3 | 323.1 | 386.4 | 374.3 | 307.8 | 231.5 | 327.3 | 250.2 | 271.5 | 289.6 | 328.1 | 251.5 | 269.9 | 289.5
2200.2 | 1924.2 | -6.8 | 0 | 0 | 264.6 | 267.3 | 236.1 | 235.9 | 244.1 | 53.9 | 18.4 | 87.9 | 5.6 | 240.7 | 16.2 | 420.3 | 394.9 | 131.6 | 406.3 | 400 | 409.9 | 283.7 | 178.6 | 321.4 | 385.4 | 373.5 | 306.8 | 230.1 | 326.9 | 249.6 | 271 | 289.1 | 327.8 | 251.1 | 269.5 | 289.1
2201.2 | 1925.2 | -6.8 | 0 | 0 | 264.1 | 267.4 | 235.7 | 235.3 | 243.8 | 53.8 | 18.4 | 87.8 | 6.5 | 223.6 | 16 | 418.5 | 393.1 | 131 | 404.7 | 398.9 | 408.3 | 284.2 | 178.1 | 320.6 | 383.8 | 372.7 | 306 | 228.9 | 326.6 | 249.1 | 270.5 | 288.7 | 327.5 | 250.7 | 269 | 288.7
2202.2 | 1926.2 | -6.8 | 0 | 0 | 263.6 | 267.2 | 235.3 | 234.8 | 243.1 | 53.8 | 18.4 | 87.6 | 6.2 | 248.4 | 12.7 | 416.7 | 391.2 | 130.6 | 402.9 | 397.1 | 406.6 | 283.2 | 177.2 | 320.6 | 382.4 | 371.9 | 305.2 | 227.6 | 326.2 | 248.6 | 270.1 | 288.2 | 327.2 | 250.3 | 268.7 | 288.3
2203.2 | 1927.2 | -6.8 | 0 | 0 | 263 | 267.3 | 234.9 | 234.4 | 242.7 | 53.6 | 18.4 | 87.5 | 7.9 | 249.7 | 14.6 | 414.8 | 390.1 | 130.4 | 401.1 | 395.6 | 405.1 | 282.4 | 176.2 | 318.8 | 380.9 | 371.1 | 304.5 | 226.2 | 325.9 | 248.1 | 269.6 | 287.8 | 326.9 | 249.8 | 268.1 | 287.9
2204.2 | 1928.2 | -6.8 | 0 | 0 | 262.2 | 267.6 | 234.4 | 234 | 242.2 | 53.5 | 18.4 | 87.3 | 7.4 | 250.1 | 15.9 | 413.1 | 388.6 | 130 | 399.4 | 394.1 | 403.6 | 280.7 | 175.2 | 318.9 | 379.4 | 370.2 | 303.7 | 225.1 | 325.5 | 247.7 | 269.3 | 287.4 | 326.6 | 249.3 | 267.8 | 287.5
2205.2 | 1929.2 | -6.8 | 0 | 0 | 261.9 | 267.5 | 234 | 233.5 | 241.9 | 53.3 | 18.4 | 87.2 | 7.6 | 232.9 | 12.7 | 411.3 | 387.3 | 129.6 | 397.8 | 392.5 | 402.2 | 280.8 | 174.4 | 318 | 378.1 | 369.4 | 302.9 | 223.9 | 325.2 | 247.3 | 269 | 287 | 326.3 | 248.8 | 267.4 | 287
2206.2 | 1930.2 | -6.8 | 0 | 0 | 261.6 | 267.2 | 233.7 | 233.1 | 241.8 | 53.2 | 18.4 | 87 | 7.8 | 229.4 | 11.3 | 409.6 | 386.6 | 129.1 | 396 | 390.8 | 400.7 | 279.7 | 173.5 | 317.6 | 376.6 | 368.6 | 302.1 | 223 | 324.8 | 246.9 | 268.6 | 286.6 | 326.1 | 248.3 | 267 | 286.6
2207.2 | 1931.2 | -6.8 | 0 | 0 | 261.4 | 267.7 | 233.5 | 232.8 | 241.3 | 53.1 | 18.4 | 86.8 | 9.6 | 245.5 | 12.4 | 407.9 | 385.3 | 128.8 | 394.4 | 389.1 | 399.3 | 278.6 | 172.7 | 317 | 375.2 | 367.7 | 301 | 222 | 324.5 | 246.5 | 268.2 | 286.2 | 325.8 | 247.9 | 266.7 | 286.2
2208.2 | 1932.2 | -6.8 | 0 | 0 | 261.5 | 267.5 | 233.1 | 232.4 | 240.7 | 53 | 18.5 | 86.6 | 9 | 242.7 | 15.3 | 406.2 | 383.9 | 128.3 | 392.8 | 387.5 | 397.9 | 277.7 | 171.9 | 315.5 | 373.9 | 366.9 | 299.9 | 221 | 324.1 | 246.1 | 267.8 | 285.7 | 325.5 | 247.5 | 266.2 | 285.8
2209.2 | 1933.2 | -6.8 | 0 | 0 | 261.4 | 267.4 | 232.8 | 232.1 | 239.9 | 52.8 | 18.5 | 86.4 | 7.9 | 245.8 | 15.6 | 404.5 | 382.1 | 128 | 391.1 | 386 | 396.4 | 277 | 170.9 | 313.8 | 372.4 | 366 | 299.2 | 220.1 | 323.8 | 245.6 | 267.5 | 285.3 | 325.2 | 247.1 | 265.7 | 285.4
2210.2 | 1934.2 | -6.8 | 0 | 0 | 261.4 | 267.4 | 232.4 | 231.8 | 239.4 | 52.7 | 18.5 | 86.2 | 7.7 | 242.9 | 17.1 | 402.8 | 380.4 | 127.7 | 389.5 | 384.6 | 394.9 | 276 | 170.2 | 312.3 | 371.1 | 365.1 | 298.2 | 219.1 | 323.4 | 245.2 | 267 | 284.8 | 324.9 | 246.7 | 265.3 | 285
2211.2 | 1935.2 | -6.8 | 0 | 0 | 261 | 266.9 | 232.1 | 231.5 | 239.1 | 52.6 | 18.5 | 86.1 | 8.3 | 244.9 | 17.8 | 401.2 | 378.8 | 127.3 | 387.9 | 383.3 | 393.5 | 276 | 169.5 | 310.9 | 370 | 364.3 | 297.4 | 218 | 323.1 | 244.7 | 266.6 | 284.3 | 324.6 | 246.2 | 264.8 | 284.6
2212.2 | 1936.2 | -6.8 | 0 | 0 | 260.7 | 266.1 | 231.7 | 231.2 | 238.7 | 52.5 | 18.5 | 85.9 | 7.2 | 243.7 | 19.1 | 399.6 | 377.6 | 126.8 | 386.3 | 381.8 | 392.1 | 275.7 | 168.6 | 309.3 | 368.7 | 363.5 | 296.7 | 217 | 322.7 | 244.2 | 266.2 | 283.9 | 324.3 | 245.8 | 264.5 | 284.2
2213.2 | 1937.2 | -6.8 | 0 | 0 | 260.4 | 265.6 | 231.3 | 230.9 | 238.2 | 52.5 | 18.5 | 85.7 | 5.8 | 239.7 | 16.3 | 398 | 376.5 | 126.3 | 384.9 | 380.3 | 390.7 | 274.6 | 168 | 308.1 | 367.5 | 362.6 | 296 | 216.1 | 322.4 | 243.8 | 265.8 | 283.5 | 324 | 245.4 | 264.2 | 283.8
2214.2 | 1938.2 | -6.8 | 0 | 0 | 260 | 264.7 | 230.9 | 230.5 | 237.7 | 52.4 | 18.5 | 85.6 | 5.1 | 238 | 17.3 | 396.4 | 374.8 | 125.7 | 383.4 | 378.7 | 389.2 | 272.9 | 167.6 | 306.6 | 366 | 361.8 | 295.3 | 215.2 | 322 | 243.4 | 265.4 | 283.1 | 323.7 | 245 | 263.8 | 283.5
2215.2 | 1939.2 | -6.8 | 0 | 0 | 259.8 | 264.1 | 230.5 | 230.2 | 237.2 | 52.4 | 18.5 | 85.4 | 5.9 | 250.8 | 16.5 | 394.8 | 374.1 | 125.2 | 381.9 | 377.2 | 387.8 | 273.2 | 167.2 | 305.3 | 364.8 | 361 | 294.4 | 214.4 | 321.7 | 243 | 265.1 | 282.7 | 323.4 | 244.6 | 263.3 | 283
2216.2 | 1940.2 | -6.8 | 0 | 0 | 259.4 | 264 | 230.2 | 230 | 236.8 | 52.3 | 18.5 | 85.3 | 6.6 | 246 | 15.4 | 393.3 | 373.4 | 124.7 | 380.4 | 375.7 | 386.4 | 272.3 | 166.1 | 303.7 | 363.5 | 360.1 | 293.3 | 213.4 | 321.4 | 242.6 | 264.7 | 282.3 | 323.1 | 244.2 | 262.9 | 282.6
2217.2 | 1941.2 | -6.8 | 0 | 0 | 258.9 | 263.4 | 229.9 | 229.6 | 236.4 | 52.2 | 18.5 | 85.1 | 6.2 | 244.8 | 15.5 | 391.8 | 372.1 | 124 | 379 | 374.2 | 385 | 272.8 | 165.3 | 302.4 | 362.2 | 359.2 | 292.6 | 212.4 | 321.1 | 242.2 | 264.4 | 281.8 | 322.8 | 243.7 | 262.5 | 282.2
2218.2 | 1942.2 | -6.8 | 0 | 0 | 258.6 | 263.1 | 229.6 | 229.1 | 236 | 52.2 | 18.5 | 84.9 | 7.4 | 245.4 | 15.9 | 390.3 | 370.7 | 123.5 | 377.5 | 372.6 | 383.6 | 272.6 | 165.2 | 301.6 | 361 | 358.5 | 291.8 | 211.6 | 320.7 | 241.8 | 264 | 281.4 | 322.5 | 243.3 | 262 | 281.8
2219.2 | 1943.2 | -6.8 | 0 | 0 | 258.2 | 262.8 | 229.2 | 228.7 | 235.8 | 52.1 | 18.5 | 84.8 | 7.3 | 245.5 | 15.8 | 388.8 | 369.1 | 123 | 376 | 371.1 | 382.2 | 271.3 | 165 | 302.4 | 359.9 | 357.6 | 290.8 | 210.8 | 320.4 | 241.4 | 263.6 | 281 | 322.2 | 243 | 261.6 | 281.4
2220.2 | 1944.2 | -6.8 | 0 | 0 | 257.9 | 262.5 | 228.8 | 228.4 | 235.4 | 52.1 | 18.5 | 84.6 | 8.2 | 232.8 | 14.8 | 387.3 | 367.8 | 122.6 | 374.5 | 369.6 | 380.9 | 271 | 164 | 302.4 | 358.5 | 356.9 | 289.9 | 210.1 | 320 | 241 | 263.2 | 280.6 | 321.9 | 242.5 | 261.3 | 281
2221.2 | 1945.2 | -6.8 | 0 | 0 | 257.7 | 262 | 228.5 | 227.9 | 234.9 | 52 | 18.5 | 84.5 | 7.9 | 254.2 | 14.1 | 385.8 | 366.8 | 122 | 373 | 368.3 | 379.7 | 270.1 | 163.2 | 301.3 | 357.4 | 356.1 | 289.3 | 209.5 | 319.7 | 240.6 | 262.9 | 280.2 | 321.6 | 242.1 | 260.9 | 280.6
2222.2 | 1946.2 | -6.8 | 0 | 0 | 257.5 | 261.2 | 228.1 | 227.7 | 234.8 | 51.9 | 18.5 | 84.3 | 7.1 | 241.5 | 14.3 | 384.3 | 365.4 | 121.2 | 371.4 | 366.9 | 378.4 | 269 | 163.3 | 300.8 | 356.4 | 355.2 | 288.5 | 208.6 | 319.4 | 240.2 | 262.5 | 279.8 | 321.4 | 241.7 | 260.7 | 280.3
2223.2 | 1947.2 | -6.8 | 0 | 0 | 257.2 | 260.4 | 227.8 | 227.4 | 234.5 | 51.8 | 18.5 | 84.2 | 6.5 | 255.1 | 12.3 | 382.9 | 364.3 | 121.1 | 369.8 | 365.2 | 377.2 | 269.8 | 163 | 300.1 | 355.6 | 354.4 | 288 | 207.7 | 319 | 239.8 | 262.2 | 279.4 | 321.1 | 241.3 | 260.5 | 279.9
2224.2 | 1948.2 | -6.8 | 0 | 0 | 256.7 | 260 | 227.5 | 227 | 234.1 | 51.7 | 18.5 | 84 | 7.2 | 235.1 | 12.8 | 381.4 | 362.9 | 120.6 | 368.4 | 364 | 376 | 270.6 | 162.8 | 299.8 | 354.3 | 353.7 | 287.6 | 206.8 | 318.7 | 239.4 | 261.8 | 279 | 320.8 | 240.9 | 260.1 | 279.5
2225.2 | 1949.2 | -6.8 | 0 | 0 | 256.2 | 259.6 | 227.1 | 226.5 | 233.4 | 51.6 | 18.5 | 83.9 | 5.9 | 245.8 | 15.2 | 379.9 | 361.2 | 120.3 | 366.9 | 362.4 | 375 | 268.9 | 161.9 | 298.2 | 353.1 | 352.9 | 286.4 | 205.8 | 318.3 | 239 | 261.4 | 278.6 | 320.5 | 240.5 | 259.6 | 279.1
2226.2 | 1950.2 | -6.8 | 0 | 0 | 255.9 | 258.8 | 226.7 | 226.2 | 232.7 | 51.5 | 18.5 | 83.7 | 6 | 243.7 | 16.8 | 378.4 | 360.1 | 119.7 | 365.5 | 361.1 | 374.1 | 268.4 | 160.8 | 296.9 | 351.8 | 352.4 | 284.9 | 204.8 | 318 | 238.6 | 261 | 278.1 | 320.2 | 240.1 | 259.1 | 278.7
2227.2 | 1951.2 | -6.8 | 0 | 0 | 255.4 | 258 | 226.3 | 226 | 232.1 | 51.5 | 18.5 | 83.5 | 6 | 240 | 16.2 | 377 | 359.1 | 119.1 | 364.1 | 359.7 | 373.1 | 268.7 | 160.2 | 296.1 | 350.4 | 351.9 | 284.2 | 203.9 | 317.7 | 238.1 | 260.6 | 277.7 | 319.9 | 239.7 | 258.6 | 278.4
2228.2 | 1952.2 | -6.8 | 0 | 0 | 254.9 | 257.3 | 225.9 | 225.7 | 231.7 | 51.5 | 18.5 | 83.3 | 6.3 | 237.3 | 15.7 | 375.5 | 357.8 | 118.4 | 362.6 | 358.5 | 372 | 268.4 | 159.6 | 295.4 | 349.2 | 351.5 | 283.7 | 203.2 | 317.3 | 237.7 | 260.3 | 277.3 | 319.6 | 239.3 | 258.2 | 278
2229.2 | 1953.2 | -6.8 | 0 | 0 | 254.4 | 256.6 | 225.5 | 225.2 | 231.5 | 51.5 | 18.5 | 83.2 | 5.8 | 231.3 | 14.2 | 374 | 356.2 | 117.8 | 361 | 357.3 | 371 | 268 | 158.8 | 294.1 | 348.7 | 351.2 | 283.2 | 202.4 | 317 | 237.3 | 260 | 276.9 | 319.3 | 238.9 | 257.8 | 277.6
2230.2 | 1954.2 | -6.8 | 0 | 0 | 254 | 256.3 | 225.2 | 224.7 | 231.2 | 51.4 | 18.5 | 83 | 5.5 | 239.3 | 13.6 | 372.6 | 354 | 117.1 | 359.6 | 356.1 | 369.9 | 266.9 | 158.1 | 292.4 | 347.8 | 350.8 | 282.3 | 201.6 | 316.7 | 236.8 | 259.6 | 276.4 | 319 | 238.5 | 257.5 | 277.2
2231.2 | 1955.2 | -6.8 | 0 | 0 | 253.6 | 256 | 225 | 224.3 | 231.1 | 51.4 | 18.5 | 82.8 | 5.8 | 238.4 | 14.5 | 371.1 | 352.6 | 116.8 | 358.2 | 355.1 | 368.8 | 266.2 | 157.5 | 290.8 | 346.9 | 350.7 | 281.5 | 200.8 | 316.3 | 236.4 | 259.2 | 276.1 | 318.7 | 238.1 | 257.1 | 276.8
2232.2 | 1956.2 | -6.8 | 0 | 0 | 253.2 | 255.1 | 224.6 | 224 | 231 | 51.3 | 18.5 | 82.7 | 5.6 | 242 | 14.9 | 369.7 | 350.2 | 116.5 | 356.9 | 353.8 | 367.7 | 264.2 | 156.6 | 289 | 345.6 | 350.7 | 280.5 | 199.9 | 316 | 236 | 258.8 | 275.7 | 318.4 | 237.6 | 256.7 | 276.4
2233.2 | 1957.2 | -6.8 | 0 | 0 | 252.7 | 254.8 | 224.3 | 223.6 | 230.6 | 51.3 | 18.5 | 82.5 | 5.3 | 241.8 | 15.6 | 368.2 | 349.5 | 115.6 | 355.5 | 352.5 | 366.6 | 264.1 | 156.1 | 288.1 | 344.5 | 350.6 | 279.6 | 199 | 315.7 | 235.7 | 258.5 | 275.3 | 318.2 | 237.2 | 256.3 | 276.1
2234.2 | 1958.2 | -6.8 | 0 | 0 | 252.1 | 254.3 | 223.9 | 223.2 | 230 | 51.2 | 18.5 | 82.5 | 5.5 | 238.2 | 14.9 | 366.8 | 348.6 | 114.9 | 354.1 | 351.2 | 365.4 | 263.6 | 155.5 | 287.8 | 343.2 | 350.5 | 278.7 | 197.9 | 315.3 | 235.4 | 258.2 | 275 | 317.9 | 236.8 | 256.1 | 275.7
2235.2 | 1959.2 | -6.8 | 0 | 0 | 251.7 | 253.5 | 223.5 | 222.8 | 229.5 | 51.2 | 18.5 | 82.4 | 5.1 | 249.3 | 12.7 | 365.4 | 346.6 | 114.5 | 352.8 | 349.8 | 364.2 | 263.1 | 155 | 286.7 | 342.1 | 350.4 | 277.9 | 196.9 | 315 | 235 | 257.9 | 274.5 | 317.6 | 236.4 | 255.9 | 275.3
2236.2 | 1960.2 | -6.8 | 0 | 0 | 251.4 | 252.8 | 223.1 | 222.4 | 229.2 | 51.1 | 18.5 | 82.3 | 5.3 | 246.5 | 12.4 | 364 | 345.3 | 113.9 | 351.4 | 348.7 | 363.1 | 262.4 | 154.6 | 286 | 341.2 | 350.3 | 277.2 | 196 | 314.7 | 234.7 | 257.5 | 274.1 | 317.3 | 236.1 | 255.6 | 275
2237.2 | 1961.2 | -6.8 | 0 | 0 | 251 | 252.2 | 222.8 | 222 | 228.9 | 51 | 18.5 | 82.2 | 5.5 | 252.7 | 11.6 | 362.6 | 344.4 | 113.3 | 350.2 | 347.8 | 361.9 | 261.6 | 154 | 284.6 | 340.1 | 349.9 | 276.3 | 195.1 | 314.4 | 234.3 | 257.1 | 273.7 | 317 | 235.6 | 255.2 | 274.6
2238.2 | 1962.2 | -6.8 | 0 | 0 | 250.2 | 251.9 | 222.5 | 221.7 | 228.6 | 51 | 18.5 | 82.2 | 5.3 | 257.3 | 10.5 | 361.2 | 343.1 | 112.4 | 348.9 | 346.2 | 360.8 | 260.9 | 153.7 | 282.9 | 338.8 | 349.6 | 274.6 | 194.2 | 314 | 233.9 | 256.7 | 273.3 | 316.7 | 235.2 | 254.8 | 274.3
2239.2 | 1963.2 | -6.8 | 0 | 0 | 249.8 | 251.3 | 222.1 | 221.3 | 228.2 | 50.9 | 18.5 | 82.1 | 5.6 | 240.6 | 11.2 | 359.7 | 341.4 | 111.6 | 347.6 | 345 | 359.5 | 259.9 | 153.3 | 282.2 | 337.5 | 349.2 | 273.8 | 193.3 | 313.7 | 233.5 | 256.3 | 272.9 | 316.4 | 234.8 | 254.5 | 273.9
2240.2 | 1964.2 | -6.8 | 0 | 0 | 249.3 | 250.9 | 221.7 | 221 | 227.9 | 50.9 | 18.5 | 82 | 5.2 | 239.4 | 11.8 | 358.3 | 339.4 | 110.9 | 346.3 | 343.6 | 358.3 | 260.1 | 152.3 | 281.4 | 336.4 | 348.7 | 273.3 | 192.5 | 313.4 | 233.1 | 255.9 | 272.5 | 316.1 | 234.4 | 254 | 273.5
2241.2 | 1965.2 | -6.8 | 0 | 0 | 248.8 | 250.6 | 221.5 | 220.7 | 227.8 | 50.8 | 18.6 | 81.9 | 5.7 | 252.8 | 10.7 | 357 | 336.8 | 110.3 | 344.9 | 342.1 | 357.1 | 259.8 | 152.4 | 279.6 | 335.6 | 348.1 | 272.5 | 191.6 | 313.1 | 232.6 | 255.5 | 272 | 315.8 | 233.9 | 253.5 | 273.1
2242.2 | 1966.2 | -6.8 | 0 | 0 | 248.2 | 250.3 | 221.2 | 220.3 | 227.6 | 50.7 | 18.5 | 81.9 | 5.4 | 250.3 | 9.8 | 355.5 | 335.5 | 109.8 | 343.6 | 340.9 | 355.9 | 258.7 | 152.5 | 277.9 | 334.6 | 347.6 | 271.1 | 190.8 | 312.8 | 232.3 | 255.1 | 271.7 | 315.6 | 233.5 | 253.2 | 272.8
2243.2 | 1967.2 | -6.8 | 0 | 0 | 248 | 250.4 | 220.9 | 219.9 | 227.1 | 50.7 | 18.6 | 81.9 | 6 | 233 | 11.8 | 354.2 | 334.3 | 109.2 | 342.1 | 339.5 | 354.7 | 260.3 | 151.7 | 276.3 | 333.4 | 347 | 270.1 | 190.2 | 312.4 | 231.9 | 254.7 | 271.3 | 315.3 | 233.1 | 253 | 272.4
2244.2 | 1968.2 | -6.8 | 0 | 0 | 247.8 | 249.8 | 220.5 | 219.6 | 226.3 | 50.6 | 18.6 | 81.8 | 6.3 | 250.6 | 11.8 | 352.8 | 333.2 | 108.7 | 340.6 | 338.3 | 353.5 | 259.7 | 151.4 | 274.5 | 332.2 | 346.5 | 269.4 | 189.6 | 312.1 | 231.5 | 254.4 | 270.9 | 315 | 232.7 | 252.7 | 272.1
2245.2 | 1969.2 | -6.8 | 0 | 0 | 247.2 | 249.6 | 220.1 | 219.3 | 225.7 | 50.6 | 18.6 | 81.7 | 5.2 | 246.4 | 15.2 | 351.4 | 332.3 | 108.1 | 339.1 | 337.1 | 352.4 | 259.3 | 150.9 | 274 | 331.1 | 346.1 | 267.5 | 188.8 | 311.8 | 231.1 | 254 | 270.5 | 314.7 | 232.3 | 252.3 | 271.7
2246.2 | 1970.2 | -6.8 | 0 | 0 | 246.7 | 249.3 | 219.7 | 218.8 | 225.4 | 50.5 | 18.6 | 81.6 | 5.2 | 237.8 | 16.8 | 350 | 331.4 | 107.2 | 337.7 | 336 | 351.2 | 258 | 150.3 | 273.9 | 330.2 | 345.4 | 266.3 | 188.1 | 311.5 | 230.6 | 253.6 | 270.1 | 314.4 | 231.9 | 251.9 | 271.3
2247.2 | 1971.2 | -6.8 | 0 | 0 | 246.1 | 249.3 | 219.4 | 218.4 | 224.7 | 50.4 | 18.6 | 81.5 | 6.9 | 243.6 | 16.1 | 348.7 | 330.5 | 107 | 336.3 | 334.8 | 350 | 257 | 149.8 | 273.9 | 329.2 | 344.8 | 265.4 | 187.5 | 311.1 | 230.2 | 253.3 | 269.7 | 314.1 | 231.5 | 251.5 | 271
2248.2 | 1972.2 | -6.8 | 0 | 0 | 245.6 | 248.9 | 219.2 | 218.1 | 224 | 50.4 | 18.6 | 81.4 | 5.8 | 242.6 | 16.4 | 347.3 | 329.1 | 106.7 | 335 | 333.8 | 348.8 | 256.8 | 149.6 | 274.4 | 327.9 | 344.3 | 264 | 186.7 | 310.8 | 229.9 | 253 | 269.3 | 313.8 | 231.1 | 251.1 | 270.6
2249.2 | 1973.2 | -6.8 | 0 | 0 | 245.4 | 248.7 | 218.9 | 217.8 | 223.4 | 50.3 | 18.6 | 81.3 | 5.8 | 243 | 16.8 | 346 | 327.7 | 106.3 | 333.6 | 332.6 | 347.7 | 256 | 149 | 274.7 | 327.1 | 343.7 | 263.2 | 186 | 310.5 | 229.5 | 252.8 | 269 | 313.5 | 230.7 | 250.7 | 270.2
2250.2 | 1974.2 | -6.8 | 0 | 0 | 245.3 | 248.4 | 218.5 | 217.4 | 222.9 | 50.2 | 18.6 | 81.3 | 5.1 | 246.6 | 18.2 | 344.7 | 326.6 | 105.8 | 332.4 | 331.5 | 346.4 | 254.5 | 148.3 | 276.7 | 326.5 | 342.9 | 262.3 | 185.4 | 310.2 | 229.2 | 252.5 | 268.6 | 313.3 | 230.3 | 250.5 | 269.9
2251.2 | 1975.2 | -6.8 | 0 | 0 | 245.2 | 247.8 | 218.2 | 216.9 | 222.8 | 50.1 | 18.6 | 81.2 | 4.8 | 234.3 | 18.1 | 343.4 | 325.2 | 105.6 | 331.2 | 330.4 | 345.1 | 254.2 | 148 | 278.4 | 326 | 342.2 | 261.9 | 184.8 | 309.9 | 228.8 | 252.1 | 268.2 | 313 | 229.9 | 250.3 | 269.5
2252.2 | 1976.2 | -6.8 | 0 | 0 | 244.7 | 247.1 | 217.9 | 216.6 | 222.7 | 50.1 | 18.6 | 81.1 | 4.9 | 239 | 15.7 | 342 | 323.6 | 105.2 | 329.9 | 329.2 | 343.9 | 253.7 | 147.1 | 278.9 | 325.4 | 341.3 | 261.2 | 184 | 309.5 | 228.5 | 251.8 | 267.9 | 312.7 | 229.5 | 249.9 | 269.2
2253.2 | 1977.2 | -6.8 | 0 | 0 | 244.1 | 246.6 | 217.5 | 216.2 | 222.5 | 50 | 18.6 | 81 | 5.4 | 254.5 | 13.9 | 340.7 | 322.1 | 104.7 | 328.7 | 327.7 | 342.8 | 252.8 | 146.5 | 279.4 | 324.7 | 340.3 | 260.4 | 183.3 | 309.2 | 228.2 | 251.5 | 267.5 | 312.4 | 229.1 | 249.6 | 268.8
2254.2 | 1978.2 | -6.8 | 0 | 0 | 243.9 | 246.2 | 217.1 | 215.8 | 222.1 | 49.9 | 18.6 | 80.9 | 5.7 | 247.6 | 14.2 | 339.5 | 320.4 | 104 | 327.4 | 326.5 | 341.7 | 251.4 | 145.8 | 280.7 | 323.4 | 339.3 | 259.7 | 182.4 | 308.9 | 227.8 | 251.2 | 267.1 | 312.1 | 228.8 | 249.3 | 268.4
2255.2 | 1979.2 | -6.8 | 0 | 0 | 243.7 | 245.7 | 216.7 | 215.5 | 221.6 | 49.9 | 18.6 | 80.7 | 4.3 | 244.4 | 14.7 | 338.2 | 319.1 | 103.4 | 326.3 | 325.6 | 340.6 | 251.6 | 145.4 | 282.1 | 322.8 | 338.6 | 259.2 | 181.5 | 308.6 | 227.4 | 250.8 | 266.7 | 311.8 | 228.4 | 249.1 | 268.1
2256.2 | 1980.2 | -6.8 | 0 | 0 | 243.3 | 245.2 | 216.4 | 215.1 | 221.3 | 49.8 | 18.6 | 80.6 | 5.9 | 248.9 | 14.1 | 336.9 | 317.3 | 102.9 | 325.1 | 324.1 | 339.6 | 251.5 | 144.6 | 282.4 | 322.2 | 337.8 | 258.4 | 180.8 | 308.3 | 227 | 250.5 | 266.3 | 311.5 | 228.1 | 248.8 | 267.7
2257.2 | 1981.2 | -6.8 | 0 | 0 | 243.1 | 244.5 | 216.1 | 214.7 | 221 | 49.8 | 18.6 | 80.5 | 7.3 | 234.9 | 15.1 | 335.7 | 315.9 | 102.4 | 324 | 323.1 | 338.6 | 251 | 143.7 | 281.9 | 321.2 | 336.9 | 257.8 | 180.1 | 307.9 | 226.6 | 250.1 | 266 | 311.3 | 227.7 | 248.5 | 267.4
2258.2 | 1982.2 | -6.8 | 0 | 0 | 242.8 | 243.6 | 215.9 | 214.4 | 220.7 | 49.7 | 18.6 | 80.4 | 6.9 | 235.6 | 14.6 | 334.4 | 314.8 | 102.2 | 322.8 | 322 | 337.6 | 250.9 | 143.4 | 279.9 | 320.2 | 336 | 257.8 | 179.4 | 307.6 | 226.3 | 249.8 | 265.6 | 311 | 227.3 | 248.2 | 267
2259.2 | 1983.2 | -6.8 | 0 | 0 | 242.3 | 243.1 | 215.7 | 214.1 | 220.4 | 49.7 | 18.6 | 80.3 | 6.1 | 251.8 | 13.2 | 333.2 | 313.5 | 101.8 | 321.8 | 320.9 | 336.7 | 249.4 | 142.8 | 278.3 | 319.3 | 335.3 | 257.6 | 178.7 | 307.3 | 225.9 | 249.5 | 265.2 | 310.7 | 226.9 | 247.9 | 266.6
2260.2 | 1984.2 | -6.8 | 0 | 0 | 241.7 | 242.7 | 215.4 | 213.7 | 220.1 | 49.6 | 18.6 | 80.1 | 5.5 | 242.7 | 12.8 | 331.9 | 311.8 | 101.3 | 320.7 | 319.5 | 335.7 | 249.7 | 142 | 276.6 | 318.2 | 334.6 | 257 | 178 | 307 | 225.5 | 249.1 | 264.8 | 310.4 | 226.5 | 247.7 | 266.3
2261.2 | 1985.2 | -6.8 | 0 | 0 | 241.4 | 242.2 | 215.1 | 213.4 | 219.6 | 49.6 | 18.6 | 80 | 5.5 | 233 | 16.5 | 330.6 | 310.3 | 100.9 | 319.5 | 318.5 | 334.7 | 248.6 | 141.3 | 274.6 | 317.3 | 333.8 | 256.4 | 177.4 | 306.7 | 225.2 | 248.8 | 264.5 | 310.1 | 226 | 247.3 | 265.9
2262.2 | 1986.2 | -6.8 | 0 | 0 | 241.1 | 242.1 | 214.8 | 213 | 219 | 49.6 | 18.6 | 79.8 | 6.1 | 252.9 | 17.5 | 329.4 | 309.1 | 100.3 | 318.5 | 317 | 333.8 | 248.5 | 141.7 | 273.6 | 316.2 | 332.9 | 255.5 | 176.7 | 306.4 | 224.9 | 248.5 | 264.2 | 309.8 | 225.6 | 247.1 | 265.6
2263.2 | 1987.2 | -6.8 | 0 | 0 | 240.5 | 241.6 | 214.5 | 212.6 | 218.6 | 49.5 | 18.6 | 79.7 | 4.9 | 249.3 | 17.8 | 328.1 | 307.7 | 100 | 317.3 | 315.7 | 332.8 | 248.7 | 141.4 | 273.5 | 315.2 | 331.9 | 255.1 | 176.1 | 306.1 | 224.7 | 248.2 | 263.9 | 309.6 | 225.2 | 246.8 | 265.3
2264.2 | 1988.2 | -6.8 | 0 | 0 | 240.1 | 240.7 | 214 | 212.2 | 218.2 | 49.4 | 18.6 | 79.6 | 4.3 | 251.8 | 16.6 | 326.8 | 307.3 | 99.5 | 316.2 | 314.5 | 331.8 | 248.2 | 140.7 | 272.9 | 314.3 | 331 | 254.6 | 175.4 | 305.7 | 224.4 | 247.8 | 263.5 | 309.3 | 224.9 | 246.6 | 264.9
2265.2 | 1989.2 | -6.8 | 0 | 0 | 239.8 | 240.1 | 213.7 | 211.8 | 217.9 | 49.3 | 18.6 | 79.5 | 4.2 | 248.2 | 14.7 | 325.6 | 306.3 | 98.9 | 315.1 | 313.2 | 330.9 | 247.5 | 140.6 | 271.7 | 313.3 | 330 | 254 | 174.7 | 305.4 | 224 | 247.5 | 263.1 | 309 | 224.6 | 246.4 | 264.6
2266.2 | 1990.2 | -6.8 | 0 | 0 | 239.5 | 239.5 | 213.4 | 211.4 | 217.3 | 49.3 | 18.6 | 79.3 | 5.6 | 249.1 | 13.6 | 324.4 | 304.9 | 98.4 | 314 | 312.2 | 329.9 | 247.4 | 139.9 | 270.3 | 312.2 | 329 | 253.6 | 174.1 | 305.1 | 223.6 | 247.1 | 262.7 | 308.7 | 224.2 | 246.1 | 264.2
2267.2 | 1991.2 | -6.8 | 0 | 0 | 239.5 | 238.8 | 213 | 211.1 | 216.8 | 49.2 | 18.6 | 79.2 | 6.8 | 243.2 | 12.1 | 323.1 | 303.6 | 97.9 | 312.8 | 311 | 329 | 247.2 | 139.3 | 268.8 | 311.1 | 328.1 | 253 | 173.5 | 304.8 | 223.1 | 246.7 | 262.3 | 308.5 | 223.8 | 245.8 | 263.9
2268.2 | 1992.2 | -6.8 | 0 | 0 | 238.8 | 238.8 | 212.6 | 210.8 | 216.5 | 49.2 | 18.7 | 79.1 | 7.3 | 243 | 12.8 | 321.9 | 302.5 | 97.5 | 311.8 | 309.7 | 328 | 244.7 | 139.2 | 267.5 | 310.3 | 326.9 | 252.6 | 172.9 | 304.5 | 222.7 | 246.3 | 261.9 | 308.2 | 223.5 | 245.5 | 263.5
2269.2 | 1993.2 | -6.8 | 0 | 0 | 238.2 | 239.2 | 212.3 | 210.4 | 216.2 | 49.1 | 18.7 | 79 | 5.8 | 240 | 15.4 | 320.7 | 301.6 | 97.4 | 310.6 | 308.5 | 327.1 | 245.6 | 139.1 | 266.9 | 309.2 | 325.8 | 252.2 | 172.3 | 304.2 | 222.3 | 245.9 | 261.5 | 307.9 | 223.1 | 245.2 | 263.2
2270.2 | 1994.2 | -6.8 | 0 | 0 | 237.5 | 239.5 | 212.1 | 210.1 | 215.7 | 49 | 18.7 | 78.9 | 5.2 | 241.5 | 15.8 | 319.4 | 300.4 | 97.2 | 309.4 | 307.4 | 326.1 | 245 | 138.6 | 265.9 | 308.1 | 323.5 | 251.6 | 171.6 | 303.9 | 221.9 | 245.5 | 261.2 | 307.6 | 222.8 | 244.9 | 262.9
2271.2 | 1995.2 | -6.8 | 0 | 0 | 236.9 | 239.2 | 211.7 | 209.7 | 215.3 | 49 | 18.7 | 78.8 | 6 | 234.5 | 14.4 | 318.3 | 299.7 | 96.9 | 308.3 | 306.3 | 325 | 244.6 | 137.6 | 265.8 | 307.1 | 320 | 250.7 | 170.8 | 303.5 | 221.6 | 245.2 | 260.8 | 307.3 | 222.4 | 244.5 | 262.5
2272.2 | 1996.2 | -6.8 | 0 | 0 | 236.6 | 239 | 211.3 | 209.5 | 214.9 | 48.9 | 18.7 | 78.8 | 5.7 | 241.5 | 14.9 | 317.1 | 298.9 | 96.6 | 307.2 | 305.2 | 323.9 | 243.5 | 137.1 | 265 | 306.5 | 318.2 | 250.1 | 170 | 303.2 | 221.2 | 244.8 | 260.5 | 307.1 | 221.9 | 244.2 | 262.1
2273.2 | 1997.2 | -6.8 | 0 | 0 | 236.3 | 238.5 | 211 | 209.2 | 214.4 | 48.9 | 18.7 | 78.7 | 6 | 242.2 | 15.4 | 316 | 297.7 | 96.2 | 306 | 304.1 | 322.7 | 243.7 | 136.6 | 264.4 | 305.6 | 316.8 | 249.4 | 169.3 | 302.9 | 220.9 | 244.5 | 260.1 | 306.8 | 221.5 | 243.9 | 261.8
2274.2 | 1998.2 | -6.8 | 0 | 0 | 236 | 238 | 210.7 | 208.8 | 213.6 | 48.8 | 18.7 | 78.6 | 6.8 | 246.9 | 15.2 | 314.8 | 296.8 | 95.8 | 305.1 | 302.9 | 321.6 | 243.1 | 136.5 | 264 | 304.7 | 315.6 | 249.1 | 168.5 | 302.6 | 220.6 | 244.1 | 259.8 | 306.5 | 221.1 | 243.6 | 261.4
2275.2 | 1999.2 | -6.8 | 0 | 0 | 235.9 | 238 | 210.4 | 208.4 | 213 | 48.7 | 18.7 | 78.5 | 6.4 | 244 | 14.8 | 313.7 | 296.4 | 95.7 | 304.1 | 301.9 | 320.5 | 242.8 | 136.2 | 264.2 | 303.8 | 314.5 | 248.7 | 167.8 | 302.3 | 220.3 | 243.7 | 259.4 | 306.2 | 220.7 | 243.3 | 261.1
2276.2 | 2000.2 | -6.8 | 0 | 0 | 236.2 | 237.9 | 210.2 | 208 | 212.5 | 48.6 | 18.7 | 78.5 | 6.9 | 246.3 | 15.3 | 312.6 | 295.7 | 95.6 | 303 | 301 | 319.5 | 242.9 | 135.7 | 264.7 | 302.9 | 313.3 | 248 | 167 | 302 | 219.9 | 243.3 | 259 | 306 | 220.3 | 243.1 | 260.7
2277.2 | 2001.2 | -6.8 | 0 | 0 | 236.2 | 237.4 | 209.9 | 207.7 | 212.1 | 48.6 | 18.7 | 78.4 | 5.6 | 242.3 | 15.5 | 311.5 | 294.8 | 95.5 | 301.9 | 299.9 | 318.3 | 243.3 | 135.6 | 265.2 | 301.9 | 312.3 | 247.7 | 166.1 | 301.7 | 219.4 | 242.9 | 258.6 | 305.7 | 219.9 | 242.9 | 260.4
2278.2 | 2002.2 | -6.6 | 0 | 0 | 236.2 | 236.7 | 209.5 | 207.4 | 211.6 | 48.5 | 18.7 | 78.3 | 5.2 | 241.9 | 16 | 310.4 | 293.7 | 95.4 | 301 | 298.9 | 317.2 | 241.1 | 135.1 | 265.7 | 301.1 | 311.2 | 246.5 | 165.5 | 301.3 | 219 | 242.5 | 258.3 | 305.4 | 219.5 | 242.6 | 260.1
2279.2 | 2003.2 | -6.5 | 0 | 0 | 235.6 | 236.2 | 209.2 | 207.1 | 211.2 | 48.5 | 18.7 | 78.2 | 5.4 | 245.2 | 16.4 | 309.3 | 292 | 95.3 | 300 | 298 | 316.2 | 241.3 | 134.8 | 265.7 | 300.3 | 310.4 | 245 | 164.9 | 301 | 218.7 | 242.2 | 258 | 305.1 | 219.1 | 242.3 | 259.7
2280.2 | 2004.2 | -6.7 | 0 | 0 | 235.2 | 236.1 | 209 | 206.8 | 211 | 48.5 | 18.7 | 78.1 | 4.8 | 254 | 16 | 308.2 | 290.7 | 95 | 299.1 | 297 | 315.3 | 240.8 | 134 | 265 | 299.4 | 309.6 | 244.5 | 164.3 | 300.7 | 218.4 | 241.9 | 257.6 | 304.8 | 218.8 | 241.9 | 259.4
2281.2 | 2005.2 | -6.7 | 0 | 0 | 234.9 | 236.1 | 208.7 | 206.5 | 210.6 | 48.4 | 18.7 | 78.1 | 5.4 | 258.1 | 15.1 | 307.1 | 289 | 94.7 | 298.1 | 296.1 | 314.4 | 241 | 133.5 | 263.4 | 298.8 | 308.6 | 243.8 | 163.7 | 300.4 | 218.1 | 241.6 | 257.2 | 304.6 | 218.5 | 241.6 | 259.1
2282.2 | 2006.2 | -6.7 | 0 | 0 | 235 | 235.6 | 208.3 | 206.2 | 210.2 | 48.4 | 18.7 | 78 | 4.8 | 255.3 | 14.1 | 306.1 | 287.3 | 94.4 | 297.2 | 295.3 | 313.5 | 240.8 | 133 | 261.5 | 297.8 | 307.8 | 243 | 163 | 300.1 | 217.7 | 241.3 | 256.9 | 304.3 | 218.1 | 241.4 | 258.7
2283.2 | 2007.2 | -6.8 | 0 | 0 | 234.7 | 235.1 | 208.1 | 205.9 | 209.9 | 48.4 | 18.7 | 77.9 | 4.5 | 248.3 | 13.5 | 305 | 286 | 94 | 296.3 | 294.4 | 312.6 | 240.9 | 133 | 259.8 | 297 | 306.9 | 242.3 | 162.4 | 299.8 | 217.3 | 241 | 256.6 | 304 | 217.7 | 241.1 | 258.4
2284.2 | 2008.2 | -6.8 | 0 | 0 | 234.6 | 235 | 207.8 | 205.7 | 209.6 | 48.3 | 18.7 | 77.7 | 4.7 | 254.6 | 13.7 | 304 | 285.3 | 93.8 | 295.3 | 293.6 | 311.7 | 240 | 132.4 | 258.4 | 296.3 | 306.1 | 241.2 | 161.9 | 299.5 | 216.9 | 240.7 | 256.2 | 303.7 | 217.5 | 240.8 | 258
2285.2 | 2009.2 | -6.8 | 0 | 0 | 234.6 | 234.7 | 207.5 | 205.4 | 209.5 | 48.3 | 18.7 | 77.7 | 5.4 | 246.2 | 13.8 | 303 | 284.1 | 93.5 | 294.4 | 292.7 | 310.8 | 240.9 | 131.8 | 257 | 295.3 | 305.3 | 240.5 | 161.4 | 299.2 | 216.6 | 240.4 | 255.9 | 303.5 | 217.2 | 240.4 | 257.7
2286.2 | 2010.2 | -6.8 | 0 | 0 | 234.2 | 234.2 | 207.2 | 205 | 209.2 | 48.2 | 18.7 | 77.5 | 5.1 | 243.7 | 14.8 | 301.9 | 283.1 | 93.2 | 293.5 | 291.8 | 309.9 | 239.6 | 131.3 | 255.7 | 294.6 | 304.5 | 239.8 | 160.9 | 298.9 | 216.3 | 240.1 | 255.5 | 303.2 | 216.8 | 240 | 257.4
2287.2 | 2011.2 | -6.8 | 0 | 0 | 233.8 | 233.4 | 206.9 | 204.6 | 209.1 | 48.2 | 18.7 | 77.4 | 4.7 | 239.6 | 15.9 | 301 | 281 | 93.1 | 292.7 | 291.1 | 309 | 238 | 130.2 | 254.6 | 294.1 | 303.7 | 239 | 160.2 | 298.6 | 216.1 | 239.8 | 255.2 | 302.9 | 216.5 | 239.7 | 257
2288.2 | 2012.2 | -6.8 | 0 | 0 | 233.5 | 232.9 | 206.6 | 204.2 | 209.1 | 48.1 | 18.8 | 77.3 | 3.9 | 243 | 14.8 | 300 | 279.6 | 92.8 | 291.7 | 290.3 | 308.1 | 239.2 | 129.3 | 253.8 | 293.5 | 303.1 | 238.7 | 159.5 | 298.3 | 215.7 | 239.5 | 254.8 | 302.6 | 216.1 | 239.5 | 256.7
2289.2 | 2013.2 | -6.8 | 0 | 0 | 233.6 | 232.5 | 206.2 | 203.9 | 209 | 48.1 | 18.8 | 77.2 | 3.9 | 239.8 | 13.8 | 299 | 278.6 | 92.4 | 290.8 | 289.4 | 307.1 | 238.1 | 128.8 | 252.5 | 292.8 | 302.4 | 238.2 | 159.1 | 298 | 215.4 | 239.1 | 254.4 | 302.4 | 215.8 | 239.1 | 256.4
2290.2 | 2014.2 | -6.8 | 0 | 0 | 233.4 | 232.3 | 205.9 | 203.6 | 208.8 | 48.1 | 18.8 | 77.1 | 4.5 | 240.5 | 13 | 298 | 277.3 | 92.1 | 289.9 | 288.6 | 306.3 | 237.8 | 128.1 | 250.8 | 292.1 | 301.7 | 237.2 | 158.6 | 297.7 | 215 | 238.8 | 254 | 302.1 | 215.4 | 238.7 | 256.1
2291.2 | 2015.2 | -6.8 | 0 | 0 | 233 | 232 | 205.7 | 203.3 | 208.6 | 48.1 | 18.8 | 77.1 | 6.8 | 254.4 | 12.1 | 297 | 276.3 | 91.9 | 288.9 | 287.7 | 305.4 | 237.1 | 128.1 | 249.4 | 291.2 | 301.1 | 236.9 | 158.1 | 297.4 | 214.7 | 238.4 | 253.7 | 301.8 | 215.2 | 238.4 | 255.8
2292.2 | 2016.2 | -6.8 | 0 | 0 | 233 | 231.7 | 205.3 | 203 | 208.4 | 48 | 18.8 | 77 | 7.4 | 238.1 | 12.3 | 296 | 275.5 | 91.6 | 287.9 | 286.6 | 304.5 | 237.8 | 127.6 | 247.2 | 290.2 | 300.4 | 236.3 | 157.7 | 297.1 | 214.4 | 238.1 | 253.4 | 301.5 | 214.9 | 238.1 | 255.4
2293.2 | 2017.2 | -6.8 | 0 | 0 | 233 | 231.6 | 205 | 202.7 | 208.2 | 48 | 18.8 | 76.9 | 6.7 | 231.9 | 11.8 | 295 | 274.4 | 91.4 | 287.1 | 285.7 | 303.6 | 236.7 | 127.3 | 246.5 | 289.4 | 299.7 | 235.4 | 157.2 | 296.8 | 214.1 | 237.8 | 253.1 | 301.3 | 214.7 | 237.7 | 255.1
2294.2 | 2018.2 | -6.8 | 0 | 0 | 232.8 | 231.5 | 204.7 | 202.4 | 208.1 | 47.9 | 18.8 | 76.8 | 6.3 | 261.1 | 11.2 | 294 | 272.8 | 91.1 | 286.3 | 284.8 | 302.7 | 236.9 | 126.8 | 246.9 | 288.5 | 299 | 234.7 | 156.7 | 296.5 | 213.7 | 237.5 | 252.7 | 301 | 214.4 | 237.3 | 254.8
2295.2 | 2019.2 | -6.8 | 0 | 0 | 232.4 | 231.1 | 204.3 | 202.1 | 208 | 47.9 | 18.8 | 76.7 | 5 | 235.5 | 13.6 | 293 | 271.9 | 90.7 | 285.4 | 283.9 | 301.7 | 236.8 | 126.6 | 247.9 | 287.7 | 298.4 | 234.6 | 156.2 | 296.2 | 213.4 | 237.1 | 252.3 | 300.7 | 214.1 | 236.9 | 254.5
2296.2 | 2020.2 | -6.8 | 0 | 0 | 231.8 | 230.9 | 203.9 | 201.8 | 207.6 | 47.9 | 18.8 | 76.6 | 5.6 | 243.2 | 13.2 | 292.1 | 270.8 | 90.1 | 284.3 | 283 | 300.9 | 236.3 | 125.8 | 247.7 | 287 | 297.7 | 234 | 155.7 | 295.9 | 213 | 236.7 | 251.9 | 300.4 | 213.7 | 236.6 | 254.2
2297.2 | 2021.2 | -6.6 | 0 | 0 | 231.4 | 230.4 | 203.7 | 201.5 | 207.2 | 47.8 | 18.8 | 76.6 | 5.4 | 225.2 | 12.9 | 291.1 | 269.3 | 89.7 | 283.5 | 282 | 300.1 | 235.3 | 125.5 | 245.7 | 286.3 | 297.1 | 233.2 | 155.2 | 295.6 | 212.6 | 236.3 | 251.7 | 300.2 | 213.4 | 236.4 | 253.8
2298.2 | 2022.2 | -6.8 | 0 | 0 | 231.2 | 230.1 | 203.5 | 201.2 | 206.7 | 47.8 | 18.8 | 76.5 | 4.9 | 225.2 | 12 | 290.1 | 267.2 | 89.4 | 282.6 | 281.1 | 299.3 | 234.9 | 125.2 | 244.5 | 285.5 | 296.5 | 232.4 | 154.6 | 295.4 | 212.3 | 236.1 | 251.4 | 299.9 | 213 | 236.1 | 253.5
2299.2 | 2023.2 | -6.8 | 0 | 0 | 231.3 | 229.7 | 203.2 | 200.9 | 206.3 | 47.7 | 18.8 | 76.4 | 4.8 | 219.2 | 11.3 | 289.2 | 265.9 | 89.2 | 281.7 | 280 | 298.4 | 236.5 | 125.2 | 244 | 284.7 | 295.9 | 231.6 | 154 | 295.1 | 211.9 | 235.8 | 251 | 299.6 | 212.6 | 235.7 | 253.2
2300.2 | 2024.2 | -6.8 | 0 | 0 | 231 | 229.3 | 202.9 | 200.6 | 206.2 | 47.6 | 18.8 | 76.3 | 4.7 | 232.6 | 11.8 | 288.2 | 265.2 | 89 | 280.8 | 279.1 | 297.6 | 236.6 | 124.8 | 243.5 | 283.7 | 295.3 | 231.2 | 153.5 | 294.8 | 211.6 | 235.5 | 250.7 | 299.4 | 212.2 | 235.4 | 252.8
2301.2 | 2025.2 | -6.8 | 0 | 0 | 230.7 | 228.8 | 202.6 | 200.3 | 206 | 47.5 | 18.8 | 76.2 | 5.4 | 237.7 | 11 | 287.3 | 264.6 | 88.6 | 279.9 | 278.3 | 296.7 | 236.4 | 124.4 | 243.2 | 283 | 294.7 | 230.6 | 152.9 | 294.5 | 211.2 | 235.2 | 250.4 | 299.1 | 211.9 | 235.1 | 252.5
2302.2 | 2026.2 | -6.8 | 0 | 0 | 230.8 | 228.2 | 202.3 | 200.1 | 205.7 | 47.4 | 18.8 | 76.1 | 4.8 | 242.9 | 13.1 | 286.3 | 263.7 | 88.3 | 279 | 277.5 | 295.9 | 236.3 | 123.7 | 242.8 | 282.4 | 294 | 230.1 | 152.3 | 294.2 | 210.8 | 234.8 | 250 | 298.8 | 211.6 | 234.7 | 252.2
2303.2 | 2027.2 | -6.8 | 0 | 0 | 230.6 | 227.9 | 202 | 199.8 | 205.3 | 47.3 | 18.8 | 75.9 | 4.6 | 247.7 | 14.2 | 285.3 | 262.2 | 88 | 278.1 | 276.6 | 295.1 | 234.2 | 123.2 | 242.5 | 281.8 | 293.4 | 229.5 | 151.7 | 293.9 | 210.4 | 234.5 | 249.7 | 298.5 | 211.2 | 234.4 | 251.9
2304.2 | 2028.2 | -6.8 | 0 | 0 | 230.3 | 227.5 | 201.7 | 199.6 | 204.9 | 47.2 | 18.8 | 75.8 | 5.5 | 249.5 | 12.8 | 284.4 | 261.3 | 87.6 | 277.2 | 275.8 | 294.2 | 235 | 122.8 | 242.2 | 281.1 | 292.7 | 228.9 | 151.1 | 293.6 | 210.1 | 234.1 | 249.3 | 298.3 | 210.9 | 234.1 | 251.5
2305.2 | 2029.2 | -6.8 | 0 | 0 | 229.8 | 227.2 | 201.4 | 199.3 | 204.6 | 47.1 | 18.8 | 75.7 | 5.6 | 253.3 | 11.4 | 283.4 | 260.4 | 87.2 | 276.3 | 275 | 293.3 | 233.7 | 122.4 | 242.1 | 280.4 | 292.1 | 228.3 | 150.5 | 293.3 | 209.7 | 233.7 | 249 | 298 | 210.6 | 233.9 | 251.2
2306.2 | 2030.2 | -6.8 | 0 | 0 | 229.5 | 226.7 | 201 | 199 | 204.5 | 47.1 | 18.8 | 75.6 | 4.7 | 246.9 | 10.7 | 282.5 | 257.5 | 87.1 | 275.4 | 274.2 | 292.5 | 233.8 | 122.1 | 241.5 | 279.7 | 291.4 | 227.6 | 149.9 | 293 | 209.4 | 233.5 | 248.7 | 297.7 | 210.3 | 233.6 | 250.9
2307.2 | 2031.2 | -6.8 | 0 | 0 | 229 | 226.7 | 200.8 | 198.7 | 204.2 | 47 | 18.8 | 75.5 | 4.4 | 244.2 | 10.4 | 281.5 | 257 | 86.8 | 274.5 | 273.2 | 291.6 | 233.1 | 122.2 | 241.5 | 278.9 | 290.7 | 226.7 | 149.3 | 292.7 | 209 | 233.2 | 248.3 | 297.4 | 209.9 | 233.4 | 250.6
2308.2 | 2032.2 | -6.8 | 0 | 0 | 228.6 | 226.4 | 200.5 | 198.4 | 203.9 | 47 | 18.8 | 75.5 | 4.4 | 247.7 | 11.6 | 280.6 | 256.4 | 86.4 | 273.6 | 272.4 | 290.8 | 233 | 122.7 | 242 | 278 | 290 | 225.7 | 148.8 | 292.4 | 208.6 | 232.9 | 247.9 | 297.2 | 209.5 | 233.1 | 250.3
2309.2 | 2033.2 | -6.8 | 0 | 0 | 228.3 | 225.7 | 200.2 | 198.1 | 203.5 | 47 | 18.8 | 75.4 | 4.2 | 252.1 | 11.6 | 279.6 | 254.9 | 85.9 | 272.8 | 271.3 | 290 | 233.1 | 122.7 | 241.3 | 277.6 | 289.5 | 225.2 | 148.4 | 292.1 | 208.3 | 232.5 | 247.7 | 296.9 | 209.2 | 232.8 | 250
2310.2 | 2034.2 | -6.8 | 0 | 0 | 228 | 225.2 | 200 | 197.7 | 203.2 | 46.9 | 18.8 | 75.3 | 4.2 | 252.5 | 11.6 | 278.6 | 254.2 | 85.4 | 271.8 | 270.1 | 289.2 | 232.7 | 122.4 | 240 | 277.1 | 288.8 | 224.7 | 148 | 291.9 | 208 | 232.2 | 247.4 | 296.6 | 208.8 | 232.6 | 249.6
2311.2 | 2035.2 | -6.8 | 0 | 0 | 227.8 | 224.9 | 199.7 | 197.4 | 202.9 | 46.9 | 18.8 | 75.2 | 4.3 | 256.1 | 11.2 | 277.7 | 253.6 | 84.9 | 270.8 | 268.9 | 288.5 | 233.6 | 122 | 238.9 | 276.3 | 288.3 | 224.2 | 147.6 | 291.6 | 207.7 | 232 | 247.1 | 296.4 | 208.5 | 232.3 | 249.3
2312.2 | 2036.2 | -6.8 | 0 | 0 | 227.7 | 224.5 | 199.3 | 197.1 | 202.5 | 46.9 | 18.8 | 75 | 3.9 | 266.6 | 11.8 | 276.7 | 252.7 | 84.4 | 269.8 | 268 | 287.7 | 233 | 121.6 | 237.4 | 275.3 | 287.6 | 223.6 | 147.2 | 291.3 | 207.4 | 231.6 | 246.7 | 296.1 | 208.2 | 232.1 | 249
2313.2 | 2037.2 | -6.7 | 0 | 0 | 227.7 | 224 | 199 | 196.8 | 202.2 | 46.8 | 18.8 | 75 | 4.3 | 267.5 | 11.7 | 275.7 | 251.9 | 84 | 269 | 267.1 | 286.8 | 231.4 | 121.1 | 236.6 | 274.5 | 287 | 223.2 | 146.8 | 291 | 207.1 | 231.3 | 246.4 | 295.8 | 207.8 | 231.7 | 248.7
2314.2 | 2038.2 | -6.7 | 0 | 0 | 227.5 | 223.7 | 198.7 | 196.5 | 201.7 | 46.8 | 18.8 | 74.9 | 4.5 | 263.2 | 11.1 | 274.8 | 250.5 | 83.7 | 268.1 | 266.2 | 285.9 | 230.2 | 120.5 | 236.9 | 273.6 | 286.4 | 222.7 | 146.3 | 290.8 | 206.8 | 231 | 246.1 | 295.5 | 207.4 | 231.4 | 248.4
2315.2 | 2039.2 | -6.7 | 0 | 0 | 227.2 | 223.2 | 198.5 | 196.3 | 201.5 | 46.8 | 18.8 | 74.8 | 4.8 | 265.9 | 9.8 | 273.8 | 249.5 | 83.5 | 267 | 265.1 | 285.1 | 231.3 | 119.6 | 236.5 | 272.9 | 285.8 | 222.1 | 145.8 | 290.5 | 206.4 | 230.7 | 245.8 | 295.3 | 207.1 | 231.1 | 248.1
2316.2 | 2040.2 | -6.8 | 0 | 0 | 227.2 | 222.8 | 198 | 196 | 201.3 | 46.7 | 18.8 | 74.8 | 4.4 | 249.1 | 9.8 | 272.9 | 248.3 | 83.2 | 265.9 | 263.9 | 284.4 | 230.8 | 119.1 | 235.8 | 272.1 | 285.2 | 221.6 | 145.4 | 290.2 | 206.1 | 230.4 | 245.5 | 295 | 206.8 | 230.8 | 247.7
2317.2 | 2041.2 | -6.8 | 0 | 0 | 227 | 222.5 | 197.7 | 195.7 | 201.1 | 46.7 | 18.8 | 74.7 | 4.8 | 258.1 | 9.8 | 271.9 | 246.8 | 82.8 | 264.9 | 262.8 | 283.7 | 230.1 | 118.5 | 235.2 | 271.3 | 284.5 | 220.9 | 145 | 289.9 | 205.7 | 230 | 245.1 | 294.7 | 206.5 | 230.3 | 247.4
2318.2 | 2042.2 | -6.8 | 0 | 0 | 226.7 | 222.4 | 197.5 | 195.4 | 200.8 | 46.6 | 18.9 | 74.6 | 4.8 | 257.2 | 10.5 | 270.9 | 245.4 | 82.5 | 263.9 | 261.9 | 282.9 | 228.5 | 118.1 | 234.4 | 270.6 | 283.8 | 220.1 | 144.5 | 289.6 | 205.3 | 229.7 | 244.7 | 294.4 | 206.2 | 230 | 247.1
2319.2 | 2043.2 | -6.8 | 0 | 0 | 226 | 222.2 | 197.3 | 195.2 | 200.7 | 46.5 | 18.9 | 74.5 | 4.7 | 258.7 | 10.3 | 269.9 | 244.3 | 82.5 | 262.9 | 261.3 | 282.1 | 229.2 | 117.8 | 232.8 | 269.9 | 283.2 | 219.7 | 144.1 | 289.3 | 205 | 229.3 | 244.4 | 294.2 | 205.8 | 229.8 | 246.8
2320.2 | 2044.2 | -6.7 | 0 | 0 | 225.7 | 221.9 | 197 | 194.9 | 200.3 | 46.4 | 18.9 | 74.5 | 4.6 | 247.7 | 8.4 | 269 | 242 | 82.4 | 261.9 | 260.5 | 281.3 | 228.4 | 117.4 | 232 | 269 | 282.6 | 218.8 | 143.6 | 289 | 204.7 | 229 | 244.1 | 293.9 | 205.4 | 229.5 | 246.5
2321.2 | 2045.2 | -6.8 | 0 | 0 | 225.2 | 221.5 | 196.7 | 194.6 | 199.9 | 46.3 | 18.9 | 74.4 | 4.5 | 251.9 | 7.5 | 268 | 241.5 | 82.2 | 260.7 | 259.7 | 280.5 | 229 | 117.2 | 231.8 | 268.3 | 282 | 217.8 | 143.2 | 288.8 | 204.4 | 228.8 | 243.8 | 293.6 | 205.1 | 229.3 | 246.2
2322.2 | 2046.2 | -6.8 | 0 | 0 | 224.8 | 221.1 | 196.5 | 194.3 | 199.5 | 46.2 | 18.9 | 74.4 | 4.5 | 247.2 | 9.3 | 267 | 240.7 | 81.9 | 259.9 | 258.9 | 279.7 | 228.8 | 116.9 | 230 | 267.5 | 281.3 | 217.3 | 142.6 | 288.5 | 204.1 | 228.5 | 243.5 | 293.4 | 204.8 | 229.1 | 245.9
2323.2 | 2047.2 | -6.8 | 0 | 0 | 224.9 | 220.5 | 196.2 | 194 | 199 | 46.2 | 18.9 | 74.4 | 4.2 | 252.8 | 10 | 266.1 | 239.8 | 81.7 | 259.2 | 258.2 | 278.8 | 228.7 | 117 | 230 | 266.7 | 280.7 | 217 | 142.1 | 288.2 | 203.8 | 228.2 | 243.1 | 293.1 | 204.4 | 228.8 | 245.6
2324.2 | 2048.2 | -6.8 | 0 | 0 | 224.6 | 220.2 | 195.9 | 193.7 | 198.6 | 46.2 | 18.9 | 74.3 | 5.4 | 239.6 | 10 | 265.2 | 238.9 | 81.5 | 258.1 | 257.5 | 278 | 228.4 | 116.7 | 229.3 | 265.9 | 280 | 216.2 | 141.8 | 287.9 | 203.4 | 227.9 | 242.8 | 292.8 | 204.1 | 228.6 | 245.3
2325.2 | 2049.2 | -6.8 | 0 | 0 | 224 | 219.9 | 195.7 | 193.4 | 198.3 | 46.1 | 18.9 | 74.3 | 5.9 | 262.2 | 9.2 | 264.3 | 237.6 | 81.2 | 257.1 | 256.7 | 277.2 | 228.3 | 116.5 | 229 | 265.1 | 279.4 | 215.3 | 141.4 | 287.7 | 203 | 227.5 | 242.4 | 292.5 | 203.7 | 228.2 | 245
2326.2 | 2050.2 | -6.8 | 0 | 0 | 223.6 | 219.5 | 195.4 | 193.1 | 198.2 | 46.1 | 18.9 | 74.1 | 5.2 | 263.4 | 9.1 | 263.3 | 236.2 | 80.8 | 256.1 | 255.9 | 276.4 | 227.7 | 116.1 | 227.6 | 264.4 | 278.8 | 214.8 | 141.1 | 287.4 | 202.6 | 227.1 | 242.1 | 292.3 | 203.4 | 227.9 | 244.6
2327.2 | 2051.2 | -6.8 | 0 | 0 | 223.5 | 219 | 195.1 | 192.8 | 197.9 | 46.1 | 18.9 | 74.1 | 4.8 | 260.6 | 10.4 | 262.4 | 235 | 80.4 | 255 | 255.1 | 275.6 | 226.8 | 115.7 | 226.7 | 263.7 | 278.1 | 214 | 140.8 | 287.1 | 202.4 | 226.8 | 241.9 | 292 | 203.1 | 227.7 | 244.3
2328.2 | 2052.2 | -6.8 | 0 | 0 | 223 | 219.2 | 194.8 | 192.5 | 197.6 | 46.1 | 18.9 | 74.1 | 4.2 | 250.5 | 10.6 | 261.5 | 234.2 | 80.1 | 254.1 | 254.4 | 274.8 | 227.9 | 115.3 | 226.2 | 263 | 277.5 | 213.4 | 140.5 | 286.8 | 202.1 | 226.4 | 241.6 | 291.7 | 202.8 | 227.4 | 244
2329.2 | 2053.2 | -6.8 | 0 | 0 | 222.7 | 219 | 194.6 | 192.3 | 197.4 | 46.1 | 18.9 | 74.1 | 3.6 | 247.8 | 9.5 | 260.7 | 233.3 | 79.9 | 253.1 | 253.6 | 274 | 227.8 | 115.3 | 225.3 | 262.2 | 276.9 | 212.7 | 140.1 | 286.5 | 201.8 | 226.2 | 241.3 | 291.5 | 202.4 | 227.1 | 243.7
2330.2 | 2054.2 | -6.8 | 0 | 0 | 222.4 | 218.9 | 194.3 | 192 | 197.1 | 46 | 18.9 | 74.1 | 3.4 | 223.7 | 9.1 | 259.8 | 232.9 | 79.6 | 252.2 | 252.8 | 273.3 | 228 | 115.1 | 223.4 | 261.6 | 276.2 | 212.3 | 139.8 | 286.2 | 201.5 | 225.9 | 241 | 291.2 | 202 | 226.7 | 243.4
2331.2 | 2055.2 | -6.8 | 0 | 0 | 222.4 | 218.7 | 193.9 | 191.8 | 196.6 | 45.9 | 18.9 | 74 | 3.7 | 250.4 | 9.7 | 258.9 | 232.2 | 79.3 | 251.1 | 251.9 | 272.5 | 228.1 | 114.8 | 222 | 261 | 275.6 | 211.8 | 139.4 | 286 | 201.2 | 225.5 | 240.7 | 290.9 | 201.6 | 226.4 | 243.1
2332.2 | 2056.2 | -6.8 | 0 | 0 | 222.3 | 218.6 | 193.7 | 191.5 | 196 | 45.9 | 18.9 | 74 | 3.5 | 252.7 | 11.9 | 258.1 | 231.2 | 79 | 250.2 | 251.1 | 271.7 | 227.3 | 114.8 | 221 | 260.2 | 275 | 210.7 | 139 | 285.7 | 200.9 | 225.2 | 240.3 | 290.6 | 201.3 | 226.1 | 242.7
2333.2 | 2057.2 | -6.8 | 0 | 0 | 221.8 | 218.6 | 193.5 | 191.1 | 195.5 | 45.8 | 18.9 | 74 | 3.6 | 249.6 | 13.2 | 257.2 | 230.5 | 78.6 | 249.3 | 250.3 | 270.9 | 224.6 | 114.8 | 219.7 | 259.5 | 274.3 | 209.9 | 138.5 | 285.4 | 200.6 | 225.1 | 240 | 290.4 | 201 | 225.9 | 242.5
2334.2 | 2058.2 | -6.8 | 0 | 0 | 221.5 | 218.4 | 193.2 | 190.7 | 195.1 | 45.8 | 18.9 | 73.9 | 3.8 | 250.1 | 12.4 | 256.4 | 230.1 | 78.3 | 248.4 | 249.4 | 270.1 | 226.1 | 114.8 | 219.3 | 258.9 | 273.8 | 209.4 | 138.1 | 285.1 | 200.4 | 224.9 | 239.8 | 290.1 | 200.7 | 225.7 | 242.2
2335.2 | 2059.2 | -6.7 | 0 | 0 | 221 | 218.2 | 192.9 | 190.5 | 194.6 | 45.7 | 18.9 | 73.9 | 3.5 | 245.1 | 12.1 | 255.6 | 229.6 | 78.1 | 247.6 | 248.6 | 269.3 | 225.7 | 115.1 | 218.7 | 258.3 | 273.2 | 209.1 | 137.7 | 284.9 | 200.1 | 224.7 | 239.4 | 289.8 | 200.3 | 225.5 | 241.9
2336.2 | 2060.2 | -6.8 | 0 | 0 | 220.2 | 217.6 | 192.6 | 190.3 | 194 | 45.6 | 18.9 | 73.8 | 3.7 | 240.4 | 12.5 | 254.7 | 229.2 | 77.9 | 246.7 | 247.8 | 268.5 | 226.2 | 115.3 | 218.5 | 257.5 | 272.5 | 208.5 | 137.3 | 284.6 | 199.8 | 224.4 | 239.1 | 289.6 | 200.1 | 225.2 | 241.6
2337.2 | 2061.2 | -6.8 | 0 | 0 | 220.1 | 217.3 | 192.3 | 190 | 193.4 | 45.6 | 18.9 | 73.8 | 4.5 | 250.3 | 12.4 | 253.9 | 228.6 | 77.6 | 245.8 | 247.1 | 267.8 | 226.7 | 115 | 217.7 | 256.9 | 271.8 | 207.8 | 136.8 | 284.3 | 199.5 | 224 | 238.8 | 289.3 | 199.8 | 224.9 | 241.3
2338.2 | 2062.2 | -6.8 | 0 | 0 | 219.8 | 217.2 | 192 | 189.8 | 193 | 45.5 | 18.9 | 73.7 | 5 | 241.5 | 11.6 | 253.1 | 228.3 | 77.3 | 245 | 246.6 | 267 | 226.5 | 114.6 | 217.4 | 256.3 | 271.2 | 207.1 | 136.5 | 284 | 199.2 | 223.7 | 238.5 | 289 | 199.5 | 224.5 | 241
2339.2 | 2063.2 | -6.8 | 0 | 0 | 219.2 | 216.7 | 191.8 | 189.5 | 192.8 | 45.5 | 18.9 | 73.7 | 5 | 235.9 | 12.6 | 252.3 | 226.2 | 77.1 | 244.2 | 245.9 | 266.2 | 226.7 | 114.1 | 217.5 | 255.6 | 270.6 | 206.7 | 136.1 | 283.8 | 198.9 | 223.5 | 238.2 | 288.7 | 199.2 | 224.3 | 240.7
2340.2 | 2064.2 | -6.8 | 0 | 0 | 218.7 | 216.1 | 191.5 | 189.3 | 192.7 | 45.4 | 18.9 | 73.6 | 6.7 | 243.1 | 11.6 | 251.4 | 223.7 | 77 | 243.4 | 245.4 | 265.4 | 227.6 | 113.6 | 217.6 | 254.9 | 269.9 | 206.1 | 135.6 | 283.5 | 198.7 | 223.2 | 237.9 | 288.5 | 199 | 224 | 240.4
2341.2 | 2065.2 | -6.8 | 0 | 0 | 218.3 | 215.7 | 191.2 | 189 | 192.5 | 45.3 | 18.9 | 73.6 | 6.6 | 248.9 | 10.1 | 250.6 | 222.9 | 76.7 | 242.3 | 244.6 | 264.7 | 227.3 | 113.4 | 217.5 | 254.2 | 269.3 | 205.1 | 135 | 283.2 | 198.4 | 223 | 237.6 | 288.2 | 198.7 | 223.8 | 240.1
2342.2 | 2066.2 | -6.8 | 0 | 0 | 218 | 215.4 | 191 | 188.7 | 192.3 | 45.3 | 18.9 | 73.5 | 5.4 | 249.1 | 10.3 | 249.8 | 222.5 | 76.4 | 241.6 | 244 | 264 | 225.2 | 113.1 | 216.3 | 253.7 | 268.7 | 204.5 | 134.5 | 282.9 | 198.1 | 222.6 | 237.2 | 287.9 | 198.5 | 223.5 | 239.8
2343.2 | 2067.2 | -6.8 | 0 | 0 | 217.6 | 215.3 | 190.8 | 188.4 | 192 | 45.2 | 18.9 | 73.5 | 5.4 | 255.3 | 9.7 | 249 | 221.9 | 76.2 | 240.7 | 243.2 | 263.4 | 224.9 | 113.5 | 215.4 | 253 | 268.1 | 204 | 134 | 282.6 | 197.8 | 222.4 | 237 | 287.7 | 198.3 | 223.2 | 239.6
2344.2 | 2068.2 | -6.8 | 0 | 0 | 217.3 | 215 | 190.5 | 188.2 | 191.3 | 45.2 | 18.9 | 73.4 | 5.7 | 268.5 | 9.6 | 248.2 | 221.4 | 76.1 | 239.8 | 242.5 | 262.7 | 224.4 | 113.2 | 215.2 | 252.5 | 267.4 | 203.3 | 133.7 | 282.3 | 197.6 | 222.1 | 236.7 | 287.4 | 198 | 222.9 | 239.3
2345.2 | 2069.2 | -6.8 | 0 | 0 | 217.2 | 214.6 | 190.2 | 187.9 | 190.9 | 45.2 | 18.9 | 73.4 | 4.5 | 238.2 | 11.6 | 247.4 | 220.6 | 75.8 | 239 | 241.8 | 262 | 225.2 | 112.9 | 214.5 | 252.2 | 266.9 | 203.1 | 133.3 | 282.1 | 197.4 | 221.9 | 236.4 | 287.1 | 197.7 | 222.6 | 239
2346.2 | 2070.2 | -6.8 | 0 | 0 | 216.9 | 214.3 | 190 | 187.7 | 190.7 | 45.1 | 19 | 73.3 | 3.1 | 243.6 | 11.4 | 246.6 | 220.1 | 75.6 | 238.1 | 241.2 | 261.3 | 225.9 | 112.7 | 214 | 251.6 | 266.3 | 202.6 | 132.8 | 281.8 | 197.1 | 221.6 | 236.1 | 286.9 | 197.5 | 222.3 | 238.7
2347.2 | 2071.2 | -6.8 | 0 | 0 | 216.3 | 214.2 | 189.8 | 187.5 | 190.4 | 45.1 | 19 | 73.2 | 4.2 | 253.1 | 8.4 | 245.8 | 218.9 | 75.4 | 237.4 | 240.3 | 260.6 | 224.4 | 112.6 | 213.7 | 251 | 265.7 | 201.9 | 132.4 | 281.5 | 196.7 | 221.3 | 235.8 | 286.6 | 197.2 | 222 | 238.4
2348.2 | 2072.2 | -6.8 | 0 | 0 | 215.7 | 213.8 | 189.5 | 187.2 | 189.9 | 45.1 | 19 | 73.2 | 5.5 | 198.3 | 8.4 | 245 | 218.5 | 75.2 | 236.7 | 239.6 | 259.7 | 224.2 | 112.2 | 213.7 | 250.4 | 265.1 | 201.4 | 132 | 281.2 | 196.4 | 220.9 | 235.5 | 286.3 | 196.9 | 221.7 | 238.1
2349.2 | 2073.2 | -6.8 | 0 | 0 | 215.5 | 213.3 | 189.2 | 186.9 | 189.4 | 45.1 | 19 | 73.1 | 6.5 | 220.8 | 11 | 244.3 | 217.5 | 75.1 | 235.9 | 239.1 | 259.1 | 223.9 | 111.8 | 212.9 | 249.8 | 264.5 | 201 | 131.7 | 280.9 | 196.2 | 220.7 | 235.2 | 286.1 | 196.6 | 221.4 | 237.8
2350.2 | 2074.2 | -6.8 | 0 | 0 | 215.1 | 213.1 | 189 | 186.7 | 189 | 45.1 | 19 | 73.1 | 6.3 | 218.5 | 12.8 | 243.5 | 216.9 | 75 | 235.1 | 238.4 | 258.4 | 223.3 | 111.3 | 212.5 | 249.3 | 263.9 | 200.4 | 131.3 | 280.6 | 195.9 | 220.4 | 234.9 | 285.8 | 196.3 | 221.2 | 237.5
2351.2 | 2075.2 | -6.8 | 0 | 0 | 214.7 | 212.6 | 188.7 | 186.4 | 188.7 | 45.1 | 19 | 73 | 4.9 | 203.8 | 10.1 | 242.8 | 216.4 | 74.9 | 234.5 | 237.8 | 257.7 | 222.4 | 111.1 | 212.1 | 248.8 | 263.3 | 199.9 | 130.9 | 280.4 | 195.6 | 220.2 | 234.7 | 285.5 | 196 | 221 | 237.3
2352.2 | 2076.2 | -6.8 | 0 | 0 | 214.4 | 212 | 188.5 | 186.1 | 188.5 | 45 | 19 | 72.9 | 3.5 | 242.4 | 10 | 242.1 | 215.5 | 74.9 | 233.7 | 237.2 | 257.1 | 223.2 | 110.9 | 210.9 | 248.4 | 262.7 | 198.9 | 130.5 | 280.1 | 195.4 | 219.9 | 234.4 | 285.3 | 195.7 | 220.7 | 237
2353.2 | 2077.2 | -6.8 | 0 | 0 | 213.9 | 211.5 | 188.2 | 185.8 | 188.3 | 45 | 19 | 72.8 | 3.7 | 236.2 | 12.2 | 241.3 | 215.1 | 74.7 | 232.9 | 236.5 | 256.4 | 222.5 | 110.8 | 209.9 | 247.6 | 262.1 | 198 | 130 | 279.8 | 195.1 | 219.6 | 234.1 | 285 | 195.5 | 220.4 | 236.7
2354.2 | 2078.2 | -6.8 | 0 | 0 | 213.7 | 211.3 | 188.1 | 185.6 | 187.8 | 45 | 19 | 72.7 | 4 | 250.4 | 14 | 240.6 | 214.6 | 74.6 | 232.4 | 235.8 | 255.8 | 221.5 | 110.6 | 209.3 | 247.2 | 261.5 | 197 | 129.6 | 279.6 | 194.8 | 219.4 | 233.8 | 284.7 | 195.2 | 220.1 | 236.4
2355.2 | 2079.2 | -6.7 | 0 | 0 | 213.8 | 211 | 187.8 | 185.3 | 187.4 | 45 | 19 | 72.6 | 4.6 | 260.8 | 12.8 | 239.8 | 213.7 | 74.5 | 231.7 | 235.1 | 255.2 | 220.9 | 110.5 | 209.2 | 246.6 | 260.9 | 195.9 | 129.3 | 279.3 | 194.6 | 219.1 | 233.5 | 284.5 | 194.9 | 219.9 | 236.1
2356.2 | 2080.2 | -6.8 | 0 | 0 | 213.5 | 210.8 | 187.6 | 185 | 187.1 | 44.9 | 19 | 72.5 | 4.8 | 215.7 | 9.9 | 239.1 | 213 | 74.3 | 230.9 | 234.4 | 254.5 | 219.4 | 110.5 | 208.8 | 245.9 | 260.3 | 194.6 | 129 | 279 | 194.4 | 218.9 | 233.3 | 284.2 | 194.6 | 219.6 | 235.8
2357.2 | 2081.2 | -6.8 | 0 | 0 | 213.4 | 210.8 | 187.4 | 184.7 | 186.7 | 44.9 | 19 | 72.3 | 5.7 | 223.6 | 8.7 | 238.4 | 211.3 | 74 | 230.3 | 233.7 | 253.9 | 219 | 110.6 | 208.1 | 245.1 | 259.7 | 193.5 | 128.7 | 278.7 | 194.1 | 218.7 | 233 | 284 | 194.3 | 219.4 | 235.6
2358.2 | 2082.2 | -6.8 | 0 | 0 | 212.9 | 210.7 | 187.1 | 184.5 | 186.1 | 44.9 | 19 | 72.1 | 6.4 | 237.1 | 8.9 | 237.7 | 209.9 | 73.7 | 229.7 | 232.8 | 253.1 | 220.7 | 110.3 | 208.7 | 244.6 | 259.2 | 192.1 | 128.5 | 278.5 | 193.8 | 218.4 | 232.7 | 283.7 | 194.1 | 219.1 | 235.3
2359.2 | 2083.2 | -6.8 | 0 | 0 | 212.5 | 210.8 | 186.8 | 184.3 | 185.8 | 44.9 | 19 | 72 | 5.4 | 237 | 11.9 | 237 | 209.4 | 73.5 | 229 | 231.9 | 252.5 | 223 | 109.9 | 209.6 | 244.2 | 258.6 | 191 | 128.2 | 278.2 | 193.5 | 218.1 | 232.3 | 283.4 | 193.8 | 218.9 | 235
2360.2 | 2084.2 | -6.8 | 0 | 0 | 212.3 | 210.8 | 186.5 | 184.1 | 185.9 | 44.8 | 19 | 71.9 | 4.3 | 235.7 | 15.2 | 236.2 | 208 | 73.3 | 228.2 | 231.2 | 251.9 | 222.2 | 109.4 | 209.3 | 243.9 | 258 | 191.3 | 127.9 | 277.9 | 193.2 | 217.8 | 232 | 283.2 | 193.5 | 218.6 | 234.7
2361.2 | 2085.2 | -6.8 | 0 | 0 | 212.1 | 210.7 | 186.3 | 183.9 | 185.7 | 44.8 | 19 | 71.8 | 4.3 | 236.5 | 16.2 | 235.5 | 206.3 | 73.1 | 227.5 | 230.5 | 251.3 | 222.9 | 109.3 | 209.2 | 243 | 257.4 | 191.2 | 127.6 | 277.6 | 192.9 | 217.6 | 231.8 | 282.9 | 193.2 | 218.3 | 234.4
2362.2 | 2086.2 | -6.8 | 0 | 0 | 212.1 | 210.7 | 186 | 183.6 | 185.4 | 44.8 | 19 | 71.8 | 4.4 | 239.7 | 19.3 | 234.8 | 205.9 | 72.9 | 226.8 | 229.9 | 250.6 | 222.5 | 109.6 | 209.3 | 242.3 | 256.8 | 190.7 | 127.3 | 277.4 | 192.7 | 217.4 | 231.5 | 282.6 | 192.9 | 218 | 234.1
2363.2 | 2087.2 | -6.8 | 0 | 0 | 212 | 210.3 | 185.9 | 183.4 | 185.3 | 44.8 | 19 | 71.8 | 4.3 | 231.4 | 19.3 | 234.1 | 205.2 | 72.7 | 226.2 | 229.3 | 250.1 | 223.5 | 109.2 | 208.7 | 241.8 | 256.3 | 190.3 | 127.1 | 277.1 | 192.4 | 217.1 | 231.2 | 282.4 | 192.7 | 217.8 | 233.8
2364.2 | 2088.2 | -6.7 | 0 | 0 | 211.6 | 210 | 185.7 | 183.2 | 185.2 | 44.8 | 19 | 71.7 | 5.7 | 229.1 | 17.1 | 233.4 | 204.9 | 72.5 | 225.5 | 228.6 | 249.6 | 223.5 | 108.9 | 208 | 241.2 | 255.7 | 189.9 | 126.8 | 276.8 | 192.1 | 216.7 | 230.9 | 282.1 | 192.5 | 217.6 | 233.6
2365.2 | 2089.2 | -6.8 | 0 | 0 | 211.2 | 209.8 | 185.5 | 182.9 | 185.1 | 44.7 | 19 | 71.7 | 6.1 | 229.2 | 14.4 | 232.8 | 204.1 | 72.3 | 224.7 | 227.9 | 249 | 223.4 | 108.8 | 207.7 | 240.5 | 255.2 | 189.3 | 126.6 | 276.5 | 191.8 | 216.4 | 230.6 | 281.8 | 192.2 | 217.2 | 233.3
2366.2 | 2090.2 | -6.8 | 0 | 0 | 210.8 | 209.8 | 185.2 | 182.7 | 185.1 | 44.7 | 19 | 71.6 | 6.7 | 239.5 | 13.8 | 232.1 | 203.3 | 72 | 224 | 227.4 | 248.5 | 223.1 | 108.4 | 207.7 | 239.9 | 254.6 | 188.9 | 126.4 | 276.3 | 191.6 | 216.1 | 230.4 | 281.6 | 191.9 | 216.9 | 233
2367.2 | 2091.2 | -6.8 | 0 | 0 | 210.6 | 209.3 | 185.1 | 182.4 | 184.9 | 44.7 | 19 | 71.5 | 7.3 | 261.4 | 12.8 | 231.4 | 202.6 | 71.7 | 223.2 | 226.7 | 247.8 | 222.9 | 108 | 208.2 | 239.4 | 254.1 | 188.5 | 126.1 | 276 | 191.4 | 215.8 | 230.1 | 281.3 | 191.7 | 216.6 | 232.7
2368.2 | 2092.2 | -6.8 | 0 | 0 | 210.8 | 208.9 | 184.9 | 182.2 | 184.6 | 44.6 | 19 | 71.4 | 5.6 | 252.4 | 12.9 | 230.7 | 202.3 | 71.4 | 222.5 | 226.1 | 247.3 | 221.7 | 107.9 | 208.6 | 238.9 | 253.6 | 188 | 125.7 | 275.7 | 191.1 | 215.6 | 229.8 | 281.1 | 191.4 | 216.4 | 232.5
2369.2 | 2093.2 | -6.8 | 0 | 0 | 210.9 | 208.3 | 184.7 | 182 | 184.3 | 44.6 | 19 | 71.3 | 7 | 244.5 | 13.5 | 230.1 | 201.9 | 71 | 221.8 | 225.4 | 246.8 | 222.2 | 107.8 | 207.9 | 238.4 | 253 | 187.5 | 125.4 | 275.5 | 190.8 | 215.3 | 229.5 | 280.8 | 191.2 | 216.2 | 232.2
2370.2 | 2094.2 | -6.8 | 0 | 0 | 210.7 | 208.2 | 184.5 | 181.7 | 183.8 | 44.6 | 19.1 | 71.2 | 6 | 243.7 | 13.8 | 229.4 | 201.4 | 70.7 | 221 | 224.7 | 246.3 | 223.1 | 107.4 | 207 | 238.1 | 252.5 | 186.9 | 125 | 275.2 | 190.5 | 215 | 229.2 | 280.5 | 190.9 | 215.8 | 231.9
2371.2 | 2095.2 | -6.8 | 0 | 0 | 210.3 | 207.8 | 184.2 | 181.5 | 183.6 | 44.6 | 19.1 | 71.1 | 5.1 | 271.6 | 11 | 228.7 | 200.5 | 70.4 | 220.3 | 224.1 | 245.7 | 223.5 | 106.9 | 206.1 | 237.8 | 252 | 186.5 | 124.6 | 274.9 | 190.3 | 214.7 | 228.9 | 280.3 | 190.7 | 215.5 | 231.7
2372.2 | 2096.2 | -6.8 | 0 | 0 | 210.1 | 207.4 | 183.9 | 181.2 | 183.4 | 44.5 | 19.1 | 71.1 | 4 | 248.1 | 10.6 | 228.1 | 199 | 70.1 | 219.7 | 223.4 | 245.3 | 223.6 | 106.7 | 204.5 | 237.3 | 251.4 | 186 | 124.3 | 274.7 | 190 | 214.5 | 228.6 | 280 | 190.5 | 215.2 | 231.4
2373.2 | 2097.2 | -6.8 | 0 | 0 | 209.8 | 207.3 | 183.6 | 180.9 | 183.2 | 44.5 | 19.1 | 71 | 4 | 258.1 | 9.1 | 227.5 | 197.9 | 69.9 | 219.1 | 222.7 | 244.8 | 222.2 | 106.6 | 202.9 | 236.6 | 250.9 | 185.4 | 123.8 | 274.4 | 189.8 | 214.2 | 228.3 | 279.7 | 190.2 | 215 | 231.1
2374.2 | 2098.2 | -6.8 | 0 | 0 | 209.4 | 207.1 | 183.4 | 180.7 | 183.2 | 44.4 | 19.1 | 71 | 3.9 | 261.6 | 10.1 | 226.8 | 197.7 | 69.7 | 218.4 | 221.9 | 244.3 | 222.8 | 106.4 | 202 | 236.3 | 250.4 | 185 | 123.5 | 274.1 | 189.5 | 214 | 228.1 | 279.5 | 190 | 214.7 | 230.8
2375.2 | 2099.2 | -6.8 | 0 | 0 | 209.1 | 206.6 | 183.2 | 180.5 | 183.2 | 44.4 | 19.1 | 71 | 3.9 | 271.7 | 10.9 | 226.1 | 197.7 | 69.5 | 217.8 | 221.2 | 243.8 | 222.7 | 106.2 | 200.9 | 235.8 | 249.9 | 184.4 | 123.2 | 273.8 | 189.2 | 213.8 | 227.8 | 279.2 | 189.7 | 214.4 | 230.5
2376.2 | 2100.2 | -6.7 | 0 | 0 | 209 | 206 | 183 | 180.3 | 182.8 | 44.3 | 19.1 | 70.9 | 4.6 | 256.3 | 11.2 | 225.4 | 197.2 | 69.3 | 217.2 | 220.5 | 243.3 | 220.5 | 106 | 199.2 | 235 | 249.4 | 183.6 | 122.8 | 273.6 | 189 | 213.6 | 227.5 | 278.9 | 189.4 | 214.2 | 230.2
2377.2 | 2101.2 | -6.7 | 0 | 0 | 208.9 | 205.5 | 182.7 | 180.1 | 182.7 | 44.3 | 19.1 | 70.8 | 4.4 | 269.9 | 10.8 | 224.7 | 195.8 | 69 | 216.5 | 220 | 242.7 | 221.2 | 105.7 | 198.1 | 234.5 | 249 | 183 | 122.4 | 273.3 | 188.8 | 213.4 | 227.3 | 278.7 | 189.2 | 213.9 | 230
2378.2 | 2102.2 | -6.6 | 0 | 0 | 208.8 | 205.1 | 182.6 | 179.9 | 182.6 | 44.2 | 19.1 | 70.6 | 4.6 | 271.9 | 13.2 | 224.1 | 195.9 | 68.8 | 215.7 | 219.3 | 242.1 | 217 | 105.5 | 197.8 | 233.9 | 248.5 | 182.4 | 122 | 273.1 | 188.6 | 213.2 | 227 | 278.4 | 188.9 | 213.7 | 229.7
2379.2 | 2103.2 | -6.7 | 0 | 0 | 208.6 | 205.1 | 182.3 | 179.6 | 182.5 | 44.2 | 19.1 | 70.5 | 4.9 | 272.2 | 13.4 | 223.4 | 195.7 | 68.7 | 215 | 218.7 | 241.6 | 219.7 | 105.3 | 198.1 | 233.1 | 248.1 | 182 | 121.6 | 272.8 | 188.3 | 212.9 | 226.7 | 278.2 | 188.7 | 213.5 | 229.4
2380.2 | 2104.2 | -6.7 | 0 | 0 | 208.3 | 204.9 | 182.1 | 179.4 | 182.2 | 44.1 | 19.1 | 70.4 | 4.3 | 273.3 | 11.7 | 222.7 | 195.6 | 68.4 | 214.3 | 217.9 | 241 | 220.2 | 104.7 | 197.7 | 232.6 | 247.6 | 181.6 | 121.2 | 272.5 | 188 | 212.6 | 226.4 | 277.9 | 188.4 | 213.2 | 229.2
2381.2 | 2105.2 | -6.8 | 0 | 0 | 208 | 204.4 | 181.8 | 179.2 | 182.1 | 44.1 | 19.1 | 70.3 | 4.1 | 264.3 | 10.1 | 222 | 195.5 | 68.2 | 213.6 | 217.3 | 240.5 | 218.7 | 104.3 | 197 | 232 | 247.2 | 181.2 | 120.9 | 272.3 | 187.7 | 212.3 | 226.1 | 277.6 | 188.2 | 213 | 228.9
2382.2 | 2106.2 | -6.8 | 0 | 0 | 207.9 | 204.1 | 181.6 | 179 | 181.9 | 44.1 | 19.1 | 70.2 | 4.1 | 255.3 | 10.2 | 221.3 | 194.8 | 67.9 | 212.9 | 216.7 | 240 | 217.3 | 103.3 | 195.8 | 231.4 | 246.8 | 181.1 | 120.6 | 272 | 187.5 | 212 | 225.8 | 277.4 | 187.9 | 212.7 | 228.6
2383.2 | 2107.2 | -6.8 | 0 | 0 | 208 | 204.2 | 181.2 | 178.7 | 181.6 | 44 | 19.1 | 70.1 | 3.8 | 256.1 | 10.2 | 220.7 | 193.7 | 67.8 | 212.2 | 216.2 | 239.4 | 216.9 | 102.9 | 195.9 | 230.6 | 246.4 | 180.7 | 120.3 | 271.7 | 187.2 | 211.6 | 225.6 | 277.1 | 187.7 | 212.5 | 228.4
2384.2 | 2108.2 | -6.8 | 0 | 0 | 207.6 | 204 | 181 | 178.5 | 181.2 | 44 | 19.1 | 70 | 3.4 | 256.3 | 10.1 | 220 | 192.5 | 67.7 | 211.5 | 215.5 | 238.8 | 218.3 | 103.4 | 196.9 | 230 | 246 | 180.3 | 119.8 | 271.5 | 187 | 211.4 | 225.3 | 276.9 | 187.4 | 212.1 | 228.1
2385.2 | 2109.2 | -6.8 | 0 | 0 | 207 | 203.6 | 180.9 | 178.2 | 181 | 44 | 19.1 | 69.9 | 3.9 | 260.3 | 10.5 | 219.3 | 190.6 | 67.5 | 210.8 | 214.9 | 238.3 | 217.1 | 103.2 | 197.9 | 229.4 | 245.6 | 179.4 | 119.3 | 271.2 | 186.7 | 211.2 | 225 | 276.6 | 187.2 | 212 | 227.9
2386.2 | 2110.2 | -6.8 | 0 | 0 | 207 | 203.3 | 180.6 | 178 | 181 | 43.9 | 19.1 | 69.9 | 4 | 271.3 | 11.2 | 218.6 | 189.7 | 67.3 | 210.1 | 214.3 | 237.8 | 216.3 | 103.5 | 198.3 | 229.1 | 245.1 | 178.6 | 119 | 270.9 | 186.5 | 210.9 | 224.8 | 276.4 | 186.9 | 211.8 | 227.6
2387.2 | 2111.2 | -6.8 | 0 | 0 | 206.9 | 202.9 | 180.3 | 177.8 | 180.7 | 43.9 | 19.1 | 69.8 | 4.8 | 266 | 11.3 | 217.9 | 189.4 | 67.1 | 209.4 | 213.6 | 237.3 | 216.7 | 103.3 | 197.5 | 228.6 | 244.7 | 178 | 118.6 | 270.7 | 186.3 | 210.7 | 224.5 | 276.1 | 186.6 | 211.6 | 227.3
2388.2 | 2112.2 | -6.8 | 0 | 0 | 206.5 | 202.6 | 180.2 | 177.5 | 180.4 | 43.8 | 19.1 | 69.7 | 5 | 258.4 | 10.2 | 217.3 | 188.9 | 66.9 | 208.7 | 213 | 236.8 | 217.5 | 102.9 | 196.4 | 228 | 244.3 | 177.3 | 118.2 | 270.4 | 186 | 210.3 | 224.3 | 275.9 | 186.2 | 211.3 | 227.1
2389.2 | 2113.2 | -6.6 | 0 | 0 | 206.4 | 202.3 | 179.9 | 177.3 | 179.8 | 43.7 | 19.1 | 69.6 | 5.1 | 267.1 | 10.5 | 216.6 | 188.5 | 66.8 | 208.2 | 212.4 | 236.4 | 215.6 | 102.3 | 195.6 | 227.5 | 243.9 | 176.7 | 117.7 | 270.1 | 185.8 | 210.1 | 224 | 275.6 | 186 | 211.1 | 226.8
2390.2 | 2114.2 | -6.8 | 0 | 0 | 206.5 | 202 | 179.6 | 177 | 179.2 | 43.7 | 19.1 | 69.5 | 4.3 | 267.7 | 11.5 | 216 | 188.2 | 66.6 | 207.7 | 211.7 | 235.9 | 214.7 | 102.2 | 196 | 226.7 | 243.4 | 175.8 | 117.4 | 269.9 | 185.5 | 209.9 | 223.7 | 275.3 | 185.8 | 210.9 | 226.6
2391.2 | 2115.2 | -6.8 | 0 | 0 | 206.1 | 201.7 | 179.4 | 176.8 | 178.9 | 43.6 | 19.1 | 69.5 | 4 | 251.2 | 10.8 | 215.3 | 187.3 | 66.3 | 207 | 211.1 | 235.4 | 214.9 | 102.2 | 196.3 | 226.2 | 242.9 | 175.4 | 117 | 269.6 | 185.2 | 209.6 | 223.4 | 275.1 | 185.4 | 210.7 | 226.3
2392.2 | 2116.2 | -6.8 | 0 | 0 | 205.5 | 201.6 | 179.1 | 176.6 | 178.7 | 43.6 | 19.1 | 69.4 | 3.3 | 259.1 | 9.7 | 214.6 | 186.9 | 66.2 | 206.4 | 210.5 | 234.9 | 213.2 | 101.6 | 195.9 | 225.6 | 242.5 | 174.9 | 116.6 | 269.3 | 184.9 | 209.3 | 223.2 | 274.8 | 185.2 | 210.4 | 226
2393.2 | 2117.2 | -6.8 | 0 | 0 | 205.4 | 201.4 | 178.9 | 176.4 | 178.5 | 43.5 | 19.1 | 69.3 | 2.8 | 252.9 | 9.3 | 214 | 186.6 | 66 | 205.9 | 209.9 | 234.5 | 213.3 | 101 | 194.9 | 225.3 | 242 | 174.7 | 116.1 | 269.1 | 184.7 | 209 | 222.9 | 274.6 | 185 | 210.2 | 225.8
2394.2 | 2118.2 | -6.7 | 0 | 0 | 205.4 | 201.1 | 178.6 | 176.2 | 178.2 | 43.5 | 19.1 | 69.3 | 3 | 256.4 | 9.9 | 213.3 | 186.2 | 65.8 | 205.4 | 209.3 | 234 | 212.7 | 100.3 | 193.3 | 224.8 | 241.6 | 174.5 | 115.8 | 268.8 | 184.4 | 208.7 | 222.7 | 274.3 | 184.7 | 210 | 225.5
2395.2 | 2119.2 | -6.7 | 0 | 0 | 205.5 | 200.8 | 178.4 | 175.9 | 177.8 | 43.4 | 19.1 | 69.3 | 3.6 | 274.9 | 10.1 | 212.7 | 186 | 65.6 | 204.8 | 208.6 | 233.6 | 214.1 | 99.9 | 191.8 | 224.2 | 241.1 | 174.1 | 115.5 | 268.5 | 184.1 | 208.5 | 222.4 | 274.1 | 184.4 | 209.8 | 225.2
2396.2 | 2120.2 | -6.8 | 0 | 0 | 205.4 | 200.6 | 178.2 | 175.7 | 177.4 | 43.4 | 19.1 | 69.4 | 4.5 | 271.8 | 10.9 | 212 | 185.7 | 65.5 | 204.2 | 207.9 | 233.1 | 213.3 | 99.5 | 191.2 | 223.9 | 240.6 | 173.6 | 115.3 | 268.3 | 183.8 | 208.2 | 222.1 | 273.8 | 184.1 | 209.4 | 224.9
2397.2 | 2121.2 | -6.7 | 0 | 0 | 205.1 | 200.4 | 178 | 175.5 | 176.9 | 43.4 | 19.1 | 69.4 | 5 | 277.2 | 11.7 | 211.3 | 185.5 | 65.3 | 203.5 | 207.3 | 232.6 | 212.4 | 99.3 | 190.7 | 223.2 | 240.1 | 173.1 | 114.9 | 268 | 183.5 | 208 | 221.8 | 273.5 | 183.9 | 209.3 | 224.6
2398.2 | 2122.2 | -6.8 | 0 | 0 | 204.7 | 200.2 | 177.7 | 175.3 | 176.6 | 43.4 | 19.1 | 69.3 | 5.2 | 279.3 | 14.6 | 210.6 | 184.7 | 65.1 | 202.9 | 206.7 | 232.1 | 212.7 | 99 | 190.8 | 222.4 | 239.6 | 172.4 | 114.5 | 267.8 | 183.2 | 207.8 | 221.5 | 273.3 | 183.6 | 209.1 | 224.4
2399.2 | 2123.2 | -6.8 | 0 | 0 | 204.6 | 199.8 | 177.4 | 175.1 | 176.5 | 43.4 | 19.1 | 69.3 | 4.7 | 281.9 | 17.1 | 210 | 184.4 | 64.9 | 202.3 | 206.1 | 231.6 | 213.2 | 98.9 | 190.2 | 221.9 | 239.1 | 171.8 | 114.3 | 267.5 | 182.9 | 207.6 | 221.3 | 273 | 183.4 | 208.9 | 224.2
2400.2 | 2124.2 | -6.8 | 0 | 0 | 204.7 | 199.4 | 177.2 | 174.9 | 176.4 | 43.4 | 19.2 | 69.2 | 4.9 | 281.2 | 16.8 | 209.4 | 183.8 | 64.7 | 201.7 | 205.6 | 231.2 | 213 | 98.7 | 189.2 | 221.4 | 238.7 | 171.6 | 114 | 267.3 | 182.7 | 207.5 | 221.1 | 272.8 | 183.2 | 208.7 | 223.9
2401.2 | 2125.2 | -6.8 | 0 | 0 | 204.5 | 198.9 | 176.9 | 174.6 | 176.2 | 43.4 | 19.2 | 69.1 | 4.9 | 278.4 | 17.3 | 208.7 | 183.5 | 64.5 | 201.2 | 205.2 | 230.8 | 212.2 | 98.7 | 189.4 | 220.7 | 238.2 | 170.8 | 113.6 | 267 | 182.4 | 207.4 | 220.8 | 272.5 | 182.9 | 208.5 | 223.6
2402.2 | 2126.2 | -6.8 | 0 | 0 | 204 | 198.5 | 176.7 | 174.4 | 175.9 | 43.4 | 19.2 | 69.1 | 4.4 | 259.1 | 15.2 | 208.1 | 183.1 | 64.3 | 200.6 | 204.5 | 230.2 | 210.3 | 98.8 | 190.4 | 220.3 | 237.8 | 170.3 | 113.3 | 266.7 | 182.2 | 207.3 | 220.5 | 272.3 | 182.7 | 208.3 | 223.4
2403.2 | 2127.2 | -6.8 | 0 | 0 | 203.3 | 198.1 | 176.5 | 174.2 | 175.7 | 43.4 | 19.2 | 69.1 | 4.2 | 276.1 | 14.8 | 207.4 | 182.8 | 64.1 | 200 | 203.8 | 229.8 | 210.1 | 98.5 | 190.2 | 219.9 | 237.3 | 169.7 | 113 | 266.5 | 181.9 | 207 | 220.3 | 272 | 182.5 | 208.1 | 223.1
2404.2 | 2128.2 | -6.5 | 0 | 0 | 202.7 | 197.7 | 176.3 | 174 | 175.5 | 43.3 | 19.2 | 69.1 | 3.9 | 275.7 | 14.6 | 206.8 | 182.8 | 63.9 | 199.4 | 203.2 | 229.3 | 210.1 | 97.9 | 190.2 | 219.5 | 236.8 | 169 | 112.7 | 266.3 | 181.6 | 206.8 | 220 | 271.8 | 182.2 | 207.9 | 222.8
2405.2 | 2129.2 | -6.4 | 0 | 0 | 202.1 | 197.6 | 176.1 | 173.7 | 175.3 | 43.3 | 19.2 | 69.1 | 3.5 | 271.6 | 13.5 | 206.2 | 182.6 | 63.7 | 198.8 | 202.6 | 228.8 | 208.9 | 97.7 | 190.9 | 219.1 | 236.4 | 168.6 | 112.5 | 266 | 181.3 | 206.4 | 219.7 | 271.5 | 182 | 207.7 | 222.6
2406.2 | 2130.2 | -6.2 | 0 | 0 | 201.8 | 197.5 | 175.8 | 173.5 | 175.2 | 43.3 | 19.2 | 69 | 4 | 274.2 | 12.7 | 205.5 | 181.7 | 63.5 | 198.3 | 202.1 | 228.3 | 207.9 | 97.9 | 191 | 218.6 | 235.9 | 168.3 | 112.1 | 265.7 | 181 | 206.2 | 219.4 | 271.3 | 181.7 | 207.5 | 222.3
2407.2 | 2131.2 | -6.5 | 0 | 0 | 201.6 | 197.3 | 175.4 | 173.3 | 175 | 43.3 | 19.2 | 69 | 3.8 | 270.9 | 12.4 | 204.9 | 181.4 | 63.3 | 197.7 | 201.6 | 227.8 | 207.8 | 98.4 | 191.2 | 218.2 | 235.5 | 168.1 | 111.8 | 265.5 | 180.8 | 206 | 219.2 | 271 | 181.5 | 207.3 | 222
2408.2 | 2132.2 | -6.7 | 0 | 0 | 201.6 | 197.3 | 175.1 | 173.1 | 174.7 | 43.3 | 19.2 | 68.9 | 4.2 | 265.5 | 12.1 | 204.3 | 181.3 | 63.1 | 197.1 | 201 | 227.4 | 208.2 | 98.6 | 190.3 | 217.5 | 235 | 167.7 | 111.6 | 265.2 | 180.5 | 205.7 | 218.9 | 270.8 | 181.2 | 207.1 | 221.8
2409.2 | 2133.2 | -6.7 | 0 | 0 | 201.6 | 197.2 | 174.9 | 172.9 | 174.6 | 43.3 | 19.2 | 68.9 | 4.4 | 273.2 | 11.5 | 203.7 | 180.6 | 62.9 | 196.5 | 200.3 | 227 | 207.6 | 98.5 | 190 | 217.2 | 234.6 | 167.4 | 111.4 | 264.9 | 180.2 | 205.4 | 218.6 | 270.5 | 180.9 | 206.8 | 221.5
2410.2 | 2134.2 | -6.6 | 0 | 0 | 201.5 | 197.1 | 174.6 | 172.6 | 174.4 | 43.2 | 19.2 | 68.8 | 4.8 | 272.2 | 10.9 | 203 | 180.5 | 62.8 | 195.8 | 199.6 | 226.5 | 208.3 | 98.5 | 190.2 | 216.6 | 234.1 | 167 | 111.2 | 264.7 | 180 | 205.1 | 218.4 | 270.3 | 180.6 | 206.6 | 221.3
2411.2 | 2135.2 | -6.7 | 0 | 0 | 201.1 | 196.6 | 174.4 | 172.4 | 174.2 | 43.2 | 19.2 | 68.8 | 4.8 | 282 | 12.1 | 202.3 | 180.1 | 62.7 | 195.1 | 199 | 226.1 | 207.5 | 98.2 | 189.1 | 216 | 233.7 | 166.5 | 110.9 | 264.4 | 179.7 | 204.9 | 218.1 | 270 | 180.4 | 206.4 | 221
2412.2 | 2136.2 | -6.5 | 0 | 0 | 200.8 | 196.3 | 174.1 | 172.2 | 174.1 | 43.2 | 19.2 | 68.7 | 4.5 | 274.8 | 12 | 201.7 | 178.9 | 62.6 | 194.5 | 198.4 | 225.7 | 206.3 | 98.1 | 187.7 | 215.5 | 233.2 | 165.7 | 110.7 | 264.2 | 179.5 | 204.8 | 217.9 | 269.8 | 180.1 | 206.1 | 220.7
2413.2 | 2137.2 | -6.7 | 0 | 0 | 200.6 | 196 | 173.8 | 171.9 | 173.8 | 43.1 | 19.2 | 68.7 | 5 | 264.6 | 10.8 | 201.1 | 177.7 | 62.4 | 193.9 | 197.8 | 225.3 | 205.6 | 98 | 187.3 | 215 | 232.8 | 165.3 | 110.5 | 264 | 179.3 | 204.7 | 217.6 | 269.5 | 179.9 | 205.9 | 220.5
2414.2 | 2138.2 | -6.8 | 0 | 0 | 200.5 | 195.6 | 173.6 | 171.7 | 173.6 | 43.1 | 19.2 | 68.6 | 4.5 | 249.8 | 9.3 | 200.5 | 177.7 | 62.3 | 193.2 | 197.2 | 224.8 | 206 | 97.9 | 187.8 | 214.7 | 232.4 | 165.1 | 110.3 | 263.7 | 179.1 | 204.5 | 217.4 | 269.3 | 179.6 | 205.6 | 220.2

## First Electrical Failures
Note: The IRMS monitored cable at Location G did not experience electrical failure. | SCDU1: | Time (s) | Offset time (s) | C1 V1 | C1 V4 | C1 V5 | C1 V6 | SCDU2: | Time (s) | Offset time (s) | C2 V1 | SCDU3: | Time (s) | Offset time (s) | C3 V1 | SCDU4: | Time (s) | Offset time (s) | C4 V2 | C4 A2
|  | 0 | -276 | 132.2813 | 0.67706 | 0.53384 | 0.58066 |  | 0 | -276 | 131.3539 |  | 0 | -276 | 132.371 |  | 0 | -276 | 128.3528 | 0.0026002
|  | 30 | -246 | 131.21 | 0.19008 | 0.14424 | 0.28848 |  | 30 | -246 | 130.7695 |  | 30 | -246 | 131.884 |  | 30 | -246 | 127.9632 | 0.0026002
|  | 60 | -216 | 130.9178 | -0.0047195 | 0.14424 | 0.19109 |  | 60 | -216 | 130.8669 |  | 60 | -216 | 132.0788 |  | 60 | -216 | 128.2554 | 0.0090935
|  | 90 | -186 | 131.0152 | 0.28746 | 0.24166 | 0.38586 |  | 90 | -186 | 130.6721 |  | 90 | -186 | 131.884 |  | 90 | -186 | 127.9632 | 0.0026002
|  | 120 | -156 | 130.6256 | 0.092701 | 0.14424 | 0.19109 |  | 120 | -156 | 130.3799 |  | 120 | -156 | 131.5918 |  | 120 | -156 | 127.671 | 0.0026002
|  | 150 | -126 | 131.0152 | 0.092701 | 0.24166 | 0.19109 |  | 150 | -126 | 130.8669 |  | 150 | -126 | 132.0788 |  | 150 | -126 | 128.0606 | 0.010717
|  | 180 | -96 | 131.1126 | 0.28746 | 0.33904 | 0.38586 |  | 180 | -96 | 130.6721 |  | 180 | -96 | 131.884 |  | 180 | -96 | 127.9632 | 0.00097717
|  | 210 | -66 | 131.4048 | 0.48226 | 0.43642 | 0.48328 |  | 210 | -66 | 130.9643 |  | 210 | -66 | 132.1762 |  | 210 | -66 | 128.0606 | 0.0026002
|  | 240 | -36 | 131.4048 | 0.57968 | 0.53384 | 0.58066 |  | 240 | -36 | 130.9643 |  | 240 | -36 | 132.371 |  | 240 | -36 | 128.0606 | 0.0026002
|  | 270 | -6 | 131.0152 | 0.48226 | 0.43642 | 0.48328 |  | 250 | -26 | 130.8669 |  | 270 | -6 | 131.6892 |  | 270 | -6 | 127.671 | 0.00097717
|  | 300 | 24 | 130.723 | 0.19008 | 0.24166 | 0.38586 |  | 260 | -16 | 130.8669 |  | 300 | 24 | 131.7866 |  | 300 | 24 | 127.7684 | 0.0058469
|  | 330 | 54 | 131.21 | 0.48226 | 0.53384 | 0.58066 |  | 270 | -6 | 130.4773 |  | 330 | 54 | 131.7866 |  | 330 | 54 | 127.671 | 0.0090935
|  | 360 | 84 | 130.8204 | 0.19008 | 0.33904 | 0.28848 |  | 280 | 4 | 130.3799 |  | 360 | 84 | 132.1762 |  | 331 | 55 | 127.671 | 0.0058469
|  | 390 | 114 | 127.8011 | 0.092701 | 0.24166 | 0.28848 |  | 290 | 14 | 130.3799 |  | 390 | 114 | 129.5465 |  | 331.2 | 55.2 | 127.5736 | 0.0058469
|  | 420 | 144 | 130.9178 | 0.19008 | 0.33904 | 0.28848 |  | 300 | 24 | 130.4773 |  | 400 | 124 | 130.2283 |  | 331.4 | 55.4 | 127.2814 | 0.028573
|  | 450 | 174 | 131.5022 | 1.0667 | 1.0208 | 1.1651 |  | 310 | 34 | 130.4773 |  | 401 | 125 | 129.9361 |  | 331.6 | 55.6 | 126.8918 | 0.088634
|  | 480 | 204 | 132.0865 | 1.5536 | 1.313 | 1.4572 |  | 311 | 35 | 130.4773 |  | 402 | 126 | 130.6178 |  | 331.8 | 55.8 | 126.697 | 0.13409
|  | 510 | 234 | 130.8204 | 0.48226 | 0.43642 | 0.48328 |  | 312 | 36 | 130.5747 |  | 403 | 127 | 131.2996 |  | 332 | 56 | 126.4048 | 0.16493
|  | 511 | 235 | 130.8204 | 0.38488 | 0.43642 | 0.38586 |  | 313 | 37 | 130.4773 |  | 404 | 128 | 130.0335 |  | 332.2 | 56.2 | 126.1126 | 0.1909
|  | 512 | 236 | 130.723 | 0.38488 | 0.43642 | 0.48328 |  | 314 | 38 | 130.4773 |  | 405 | 129 | 130.91 |  | 332.4 | 56.4 | 126.0153 | 0.21525
|  | 513 | 237 | 130.8204 | 0.38488 | 0.43642 | 0.38586 |  | 315 | 39 | 130.5747 |  | 406 | 130 | 130.91 |  | 332.6 | 56.6 | 126.2101 | 0.20064
|  | 514 | 238 | 130.723 | 0.38488 | 0.53384 | 0.38586 |  | 316 | 40 | 130.5747 |  | 407 | 131 | 130.423 |  | 332.8 | 56.8 | 127.0866 | 0.080518
|  | 515 | 239 | 130.8204 | 0.38488 | 0.43642 | 0.38586 |  | 317 | 41 | 130.4773 |  | 407.2 | 131.2 | 130.423 |  | 333 | 57 | 127.5736 | 0.039936
|  | 516 | 240 | 130.723 | 0.38488 | 0.43642 | 0.48328 |  | 318 | 42 | 130.4773 |  | 407.4 | 131.4 | 130.5205 |  | 333.2 | 57.2 | 127.7684 | 0.015587
|  | 517 | 241 | 130.8204 | 0.38488 | 0.33904 | 0.38586 |  | 318.2 | 42.2 | 130.5747 |  | 407.6 | 131.6 | 130.2283 |  | 333.4 | 57.4 | 127.7684 | 0.010717
|  | 518 | 242 | 130.8204 | 0.38488 | 0.43642 | 0.38586 |  | 318.4 | 42.4 | 130.5747 |  | 407.8 | 131.8 | 130.3257 |  | 333.6 | 57.6 | 127.7684 | 0.0090935
|  | 519 | 243 | 130.9178 | 0.38488 | 0.43642 | 0.38586 |  | 318.6 | 42.6 | 130.5747 |  | 408 | 132 | 129.9361 |  | 333.8 | 57.8 | 127.7684 | 0.0074705
|  | 520 | 244 | 130.9178 | 0.57968 | 0.43642 | 0.48328 |  | 318.8 | 42.8 | 130.5747 |  | 408.2 | 132.2 | 129.9361 |  | 334 | 58 | 127.671 | 0.0058469
|  | 521 | 245 | 130.9178 | 0.57968 | 0.33904 | 0.48328 |  | 319 | 43 | 130.5747 |  | 408.4 | 132.4 | 129.2543 |  | 335 | 59 | 127.7684 | 0.0058469
|  | 522 | 246 | 130.8204 | 0.48226 | 0.43642 | 0.38586 |  | 319.2 | 43.2 | 120.7377 |  | 408.6 | 132.6 | 128.7673 |  | 336 | 60 | 127.7684 | 0.0058469
|  | 523 | 247 | 130.9178 | 0.48226 | 0.43642 | 0.48328 |  | 319.4 | 43.4 | 13.6989 |  | 408.8 | 132.8 | 128.9621 |  | 337 | 61 | 127.8658 | 0.0058469
|  | 524 | 248 | 130.9178 | 0.48226 | 0.33904 | 0.38586 |  | 319.6 | 43.6 | 2.6931 |  | 409 | 133 | 113.5735 |  | 337.2 | 61.2 | 127.8658 | 0.010717
|  | 525 | 249 | 131.0152 | 0.38488 | 0.43642 | 0.48328 |  | 319.8 | 43.8 | 1.2321 |  | 409.2 | 133.2 | 121.3652 |  | 337.4 | 61.4 | 127.8658 | 0.0074705
|  | 526 | 250 | 131.0152 | 0.48226 | 0.43642 | 0.38586 |  | 320 | 44 | 0.84251 |  | 409.4 | 133.4 | 128.9621 |  | 337.6 | 61.6 | 127.4762 | 0.0090935
|  | 527 | 251 | 130.8204 | 0.48226 | 0.82602 | 0.38586 |  | 320.2 | 44.2 | 0.64775 |  | 409.6 | 133.6 | 129.4491 |  | 337.8 | 61.8 | 120.9507 | 1.0707
|  | 527.2 | 251.2 | 130.8204 | 0.48226 | 2.3844 | 0.38586 |  | 320.4 | 44.4 | 0.74513 |  | 409.8 | 133.8 | 129.5465 |  | 338 | 62 | 126.9892 | 0.14058
|  | 527.4 | 251.4 | 130.9178 | 0.48226 | 1.8 | 0.38586 |  | 320.6 | 44.6 | 0.55033 |  | 410 | 134 | 130.1309 |  | 338.2 | 62.2 | 127.7684 | 0.035066
|  | 527.6 | 251.6 | 130.9178 | 0.48226 | 0.9234 | 0.38586 |  | 320.8 | 44.8 | 0.55033 |  | 410.2 | 134.2 | 108.801 |  | 338.4 | 62.4 | 127.7684 | 0.015587
|  | 527.8 | 251.8 | 131.0152 | 0.48226 | 0.63122 | 0.48328 |  | 321 | 45 | 0.45295 |  | 410.4 | 134.4 | 93.7046 |  | 338.6 | 62.6 | 127.8658 | 0.010717
|  | 528 | 252 | 130.9178 | 0.48226 | 0.63122 | 0.48328 |  | 322 | 46 | 0.45295 |  | 410.6 | 134.6 | 90.9775 |  | 338.8 | 62.8 | 127.8658 | 0.0074705
|  | 529 | 253 | 130.9178 | 0.48226 | 0.43642 | 0.38586 |  | 323 | 47 | 0.35553 |  | 410.8 | 134.8 | 96.9187 |  | 339 | 63 | 127.8658 | 0.0090935
|  | 530 | 254 | 130.9178 | 0.67706 | 1.1182 | 0.48328 |  | 324 | 48 | 0.35553 |  | 411 | 135 | 92.9254 |  | 340 | 64 | 127.8658 | 0.0074705
|  | 530.2 | 254.2 | 130.9178 | 0.67706 | 1.313 | 0.38586 |  | 325 | 49 | 0.35553 |  | 411.2 | 135.2 | 86.9842 |  | 341 | 65 | 127.7684 | 0.0074705
|  | 530.4 | 254.4 | 130.9178 | 0.57968 | 1.6052 | 0.38586 |  | 326 | 50 | 0.35553 |  | 411.4 | 135.4 | 12.7681 |  | 342 | 66 | 127.7684 | 0.0074705
|  | 530.6 | 254.6 | 131.0152 | 0.77444 | 4.1375 | 0.67808 |  | 330 | 54 | 0.25815 |  | 411.6 | 135.6 | 3.3206 |  | 342.2 | 66.2 | 127.8658 | 0.0058469
|  | 530.8 | 254.8 | 130.9178 | 0.57968 | 3.4557 | 0.48328 |  | 340 | 64 | 0.25815 |  | 411.8 | 135.8 | 2.0544 |  | 342.4 | 66.4 | 127.7684 | 0.0058469
|  | 531 | 255 | 130.9178 | 0.67706 | 7.0594 | 0.38586 |  | 350 | 74 | 0.25815 |  | 412 | 136 | 1.6648 |  | 342.6 | 66.6 | 127.7684 | 0.0058469
|  | 531.2 | 255.2 | 130.723 | 0.67706 | 5.0141 | 0.48328 |  | 360 | 84 | 0.16077 |  | 412.2 | 136.2 | 1.957 |  | 342.8 | 66.8 | 127.5736 | 0.0074705
|  | 531.4 | 255.4 | 130.6256 | 0.57968 | 6.962 | 0.48328 |  | 370 | 94 | 0.25815 |  | 412.4 | 136.4 | 2.0544 |  | 343 | 67 | 127.5736 | 0.023703
|  | 531.6 | 255.6 | 130.9178 | 0.57968 | 1.7026 | 0.38586 |  | 380 | 104 | 0.25815 |  | 412.6 | 136.6 | 2.3466 |  | 343.2 | 67.2 | 127.0866 | 0.099997
|  | 531.8 | 255.8 | 130.9178 | 0.57968 | 0.82602 | 0.38586 |  | 390 | 114 | 1.4269 |  | 412.8 | 136.8 | 2.931 |  | 343.4 | 67.4 | 127.7684 | 0.030196
|  | 532 | 256 | 130.8204 | 0.67706 | 0.63122 | 0.38586 |  | 400 | 124 | 0.93993 |  | 413 | 137 | 2.931 |  | 343.6 | 67.6 | 127.8658 | 0.015587
|  | 532.2 | 256.2 | 130.9178 | 0.67706 | 0.53384 | 0.38586 | [5 empty] | 413.2 | 137.2 | 3.2232 |  | 343.8 | 67.8 | 127.8658 | 0.01234
|  | 532.4 | 256.4 | 130.9178 | 0.67706 | 0.53384 | 0.48328 | [5 empty] | 413.4 | 137.4 | 2.2492 |  | 344 | 68 | 127.8658 | 0.0090935
|  | 532.6 | 256.6 | 131.0152 | 0.67706 | 0.43642 | 0.38586 | [5 empty] | 413.6 | 137.6 | 1.8596 |  | 345 | 69 | 127.9632 | 0.0090935
|  | 532.8 | 256.8 | 131.0152 | 0.67706 | 0.43642 | 0.38586 | [5 empty] | 413.8 | 137.8 | 1.5675 |  | 346 | 70 | 127.8658 | 0.0074705
|  | 533 | 257 | 130.9178 | 0.57968 | 0.43642 | 0.38586 | [5 empty] | 414 | 138 | 0.98306 |  | 347 | 71 | 127.8658 | 0.0074705
|  | 533.2 | 257.2 | 130.9178 | 0.67706 | 0.43642 | 0.38586 | [5 empty] | 414.2 | 138.2 | 0.7883 |  | 348 | 72 | 127.8658 | 0.0090935
|  | 533.4 | 257.4 | 130.9178 | 0.67706 | 0.33904 | 0.28848 | [5 empty] | 414.4 | 138.4 | 0.5935 |  | 349 | 73 | 127.8658 | 0.0090935
|  | 533.6 | 257.6 | 131.0152 | 0.67706 | 0.33904 | 0.38586 | [5 empty] | 414.6 | 138.6 | 0.5935 |  | 350 | 74 | 127.8658 | 0.013963
|  | 533.8 | 257.8 | 131.0152 | 0.67706 | 0.33904 | 0.38586 | [5 empty] | 414.8 | 138.8 | 0.49608 |  | 351 | 75 | 127.9632 | 0.010717
|  | 534 | 258 | 130.8204 | 0.67706 | 0.43642 | 0.38586 | [5 empty] | 415 | 139 | 0.5935 |  | 352 | 76 | 127.8658 | 0.0090935
|  | 534.2 | 258.2 | 130.9178 | 0.67706 | 0.33904 | 0.38586 | [5 empty] | 415.2 | 139.2 | 0.49608 |  | 353 | 77 | 127.8658 | 0.010717
|  | 534.4 | 258.4 | 130.9178 | 0.77444 | 0.43642 | 0.38586 | [5 empty] | 415.4 | 139.4 | 0.49608 |  | 354 | 78 | 127.8658 | 0.01234
|  | 534.6 | 258.6 | 130.8204 | 0.77444 | 0.33904 | 0.38586 | [5 empty] | 415.6 | 139.6 | 0.49608 |  | 355 | 79 | 127.8658 | 0.013963
|  | 534.8 | 258.8 | 130.8204 | 0.87186 | 0.33904 | 0.38586 | [5 empty] | 415.8 | 139.8 | 0.3987 |  | 355.2 | 79.2 | 127.8658 | 0.01721
|  | 535 | 259 | 130.9178 | 0.77444 | 0.33904 | 0.38586 | [5 empty] | 416 | 140 | 0.49608 |  | 355.4 | 79.4 | 127.8658 | 0.018833
|  | 535.2 | 259.2 | 130.9178 | 0.77444 | 0.33904 | 0.48328 | [5 empty] | 417 | 141 | 0.3987 |  | 355.6 | 79.6 | 127.8658 | 0.020457
|  | 535.4 | 259.4 | 130.9178 | 0.77444 | 0.33904 | 0.48328 | [5 empty] | 418 | 142 | 0.3987 |  | 355.8 | 79.8 | 127.8658 | 0.020457
|  | 535.6 | 259.6 | 130.9178 | 0.77444 | 0.43642 | 0.58066 | [5 empty] | 419 | 143 | 0.3987 |  | 356 | 80 | 127.7684 | 0.02208
|  | 535.8 | 259.8 | 130.8204 | 0.87186 | 0.33904 | 1.0676 | [5 empty] | 420 | 144 | 0.3987 |  | 356.2 | 80.2 | 127.8658 | 0.023703
|  | 536 | 260 | 130.8204 | 0.96924 | 0.33904 | 1.0676 | [9 empty] | 356.4 | 80.4 | 127.7684 | 0.025326
|  | 536.2 | 260.2 | 130.8204 | 0.96924 | 0.24166 | 1.5546 | [9 empty] | 356.6 | 80.6 | 127.8658 | 0.028573
|  | 536.4 | 260.4 | 130.723 | 1.0667 | 0.046856 | 5.1583 | [9 empty] | 356.8 | 80.8 | 127.7684 | 0.030196
|  | 536.6 | 260.6 | 130.723 | 1.164 | 0.33904 | 6.7167 | [9 empty] | 357 | 81 | 127.5736 | 0.056169
|  | 536.8 | 260.8 | 130.3334 | 1.0667 | 0.33904 | 8.8594 | [9 empty] | 357.2 | 81.2 | 127.5736 | 0.062661
|  | 537 | 261 | 129.8464 | 0.96924 | 0.33904 | 18.4042 | [9 empty] | 357.4 | 81.4 | 127.5736 | 0.072401
|  | 537.2 | 261.2 | 129.3595 | 0.87186 | 0.33904 | 29.7022 | [9 empty] | 357.6 | 81.6 | 127.671 | 0.065908
|  | 537.4 | 261.4 | 129.8464 | 1.0667 | 0.33904 | 28.1439 | [9 empty] | 357.8 | 81.8 | 127.4762 | 0.077271
|  | 537.6 | 261.6 | 130.5282 | 1.7484 | 0.63122 | 7.9828 | [9 empty] | 358 | 82 | 127.2814 | 0.099997
|  | 537.8 | 261.8 | 130.723 | 1.2614 | 0.53384 | 2.9182 | [9 empty] | 358.2 | 82.2 | 126.8918 | 0.14383
|  | 538 | 262 | 130.0412 | 1.3588 | 0.43642 | 90.8673 | [9 empty] | 358.4 | 82.4 | 126.3074 | 0.21687
|  | 538.2 | 262.2 | 130.3334 | 7.0078 | 1.4104 | 58.629 | [9 empty] | 358.6 | 82.6 | 126.3074 | 0.23473
|  | 538.4 | 262.4 | 129.8464 | 1.5536 | 0.53384 | 7.6906 | [9 empty] | 358.8 | 82.8 | 126.0153 | 0.25908
|  | 538.6 | 262.6 | 130.723 | 1.2614 | 0.43642 | 4.7687 | [9 empty] | 359 | 83 | 125.9178 | 0.27856
|  | 538.8 | 262.8 | 130.723 | 1.164 | 0.33904 | 2.7234 | [9 empty] | 359.2 | 83.2 | 125.7231 | 0.27531
|  | 539 | 263 | 130.5282 | 1.164 | 0.33904 | 7.4958 | [9 empty] | 359.4 | 83.4 | 127.3788 | 0.10649
|  | 539.2 | 263.2 | 130.6256 | 1.2614 | 0.24166 | 6.7167 | [9 empty] | 359.6 | 83.6 | 127.3788 | 0.10162
|  | 539.4 | 263.4 | 130.723 | 1.2614 | 0.33904 | 2.2364 | [9 empty] | 359.8 | 83.8 | 127.0866 | 0.12759
|  | 539.6 | 263.6 | 130.723 | 0.87186 | 0.33904 | 2.7234 | [9 empty] | 360 | 84 | 126.7944 | 0.17629
|  | 539.8 | 263.8 | 130.723 | 1.2614 | 0.43642 | 2.2364 | [9 empty] | 360.2 | 84.2 | 126.9892 | 0.15843
|  | 540 | 264 | 130.723 | 1.2614 | 0.33904 | 1.4572 | [9 empty] | 360.4 | 84.4 | 126.7944 | 0.18278
|  | 540.2 | 264.2 | 130.6256 | 1.9432 | 0.33904 | 1.7494 | [9 empty] | 360.6 | 84.6 | 126.9892 | 0.1633
|  | 540.4 | 264.4 | 130.9178 | 2.138 | 0.33904 | 4.0869 | [9 empty] | 360.8 | 84.8 | 126.8918 | 0.16168
|  | 540.6 | 264.6 | 130.5282 | 2.5276 | 0.33904 | 7.2036 | [9 empty] | 361 | 85 | 126.8918 | 0.15843
|  | 540.8 | 264.8 | 130.5282 | 2.625 | 0.24166 | 1.5546 | [9 empty] | 361.2 | 85.2 | 127.0866 | 0.14545
|  | 541 | 265 | 130.5282 | 2.8198 | 0.33904 | 1.5546 | [9 empty] | 361.4 | 85.4 | 127.0866 | 0.14383
|  | 541.2 | 265.2 | 130.5282 | 1.3588 | 0.33904 | 1.5546 | [9 empty] | 361.6 | 85.6 | 126.697 | 0.18116
|  | 541.4 | 265.4 | 130.6256 | 1.8458 | 0.33904 | 0.77546 | [9 empty] | 361.8 | 85.8 | 126.4048 | 0.22986
|  | 541.6 | 265.6 | 130.6256 | 1.5536 | 0.24166 | 0.38586 | [9 empty] | 362 | 86 | 126.2101 | 0.24934
|  | 541.8 | 265.8 | 130.5282 | 2.625 | 0.33904 | 0.67808 | [9 empty] | 362.2 | 86.2 | 126.2101 | 0.25258
|  | 542 | 266 | 130.5282 | 1.4562 | 0.24166 | 3.2104 | [9 empty] | 362.4 | 86.4 | 125.9178 | 0.28343
|  | 542.2 | 266.2 | 130.4308 | 1.5536 | 0.24166 | 5.0609 | [9 empty] | 362.6 | 86.6 | 125.6257 | 0.31914
|  | 542.4 | 266.4 | 130.6256 | 1.651 | 0.24166 | 2.9182 | [9 empty] | 362.8 | 86.8 | 125.3335 | 0.34836
|  | 542.6 | 266.6 | 130.5282 | 1.4562 | 0.43642 | 3.113 | [9 empty] | 363 | 87 | 125.0413 | 0.39219
|  | 542.8 | 266.8 | 130.3334 | 2.0406 | 1.8974 | 2.3338 | [9 empty] | 363.2 | 87.2 | 124.5543 | 0.44088
|  | 543 | 267 | 130.236 | 2.0406 | 5.8906 | 4.2817 | [9 empty] | 363.4 | 87.4 | 124.0673 | 0.51231
|  | 543.2 | 267.2 | 130.6256 | 2.0406 | 1.8974 | 1.8468 | [9 empty] | 363.6 | 87.6 | 123.4829 | 0.57886
|  | 543.4 | 267.4 | 130.6256 | 2.2354 | 1.0208 | 2.9182 | [9 empty] | 363.8 | 87.8 | 122.8012 | 0.6649
|  | 543.6 | 267.6 | 130.6256 | 2.3328 | 0.53384 | 1.8468 | [9 empty] | 364 | 88 | 121.8272 | 0.76554
|  | 543.8 | 267.8 | 130.6256 | 2.3328 | 0.43642 | 2.626 | [9 empty] | 364.2 | 88.2 | 121.3402 | 0.83372
|  | 544 | 268 | 130.4308 | 2.8198 | 0.33904 | 8.3724 | [9 empty] | 364.4 | 88.4 | 120.4637 | 0.93761
|  | 544.2 | 268.2 | 130.236 | 2.7224 | 0.43642 | 12.5604 | [9 empty] | 364.6 | 88.6 | 123.0934 | 0.62594
|  | 544.4 | 268.4 | 130.4308 | 2.4302 | 0.33904 | 7.3984 | [9 empty] | 364.8 | 88.8 | 124.0673 | 0.50582
|  | 544.6 | 268.6 | 130.5282 | 1.651 | 0.33904 | 2.7234 | [9 empty] | 365 | 89 | 126.7944 | 0.17791
|  | 544.8 | 268.8 | 130.4308 | 2.625 | 0.33904 | 4.7687 | [9 empty] | 365.2 | 89.2 | 126.9892 | 0.15681
|  | 545 | 269 | 130.5282 | 2.2354 | 0.33904 | 5.1583 | [9 empty] | 365.4 | 89.4 | 126.3074 | 0.23798
|  | 545.2 | 269.2 | 130.5282 | 2.2354 | 0.24166 | 5.7427 | [9 empty] | 365.6 | 89.6 | 125.6257 | 0.31752
|  | 545.4 | 269.4 | 130.5282 | 2.138 | 0.33904 | 2.7234 | [9 empty] | 365.8 | 89.8 | 125.1387 | 0.38894
|  | 545.6 | 269.6 | 129.9438 | 1.3588 | 0.33904 | 10.9047 | [9 empty] | 366 | 90 | 124.4569 | 0.45062
|  | 545.8 | 269.8 | 130.4308 | 2.7224 | 0.33904 | 8.8594 | [9 empty] | 366.2 | 90.2 | 123.5804 | 0.55289
|  | 546 | 270 | 130.5282 | 2.4302 | 0.24166 | 2.3338 | [9 empty] | 366.4 | 90.4 | 122.4116 | 0.70061
|  | 546.2 | 270.2 | 130.5282 | 2.3328 | 0.33904 | 2.4312 | [9 empty] | 366.6 | 90.6 | 121.4376 | 0.81424
|  | 546.4 | 270.4 | 130.4308 | 2.5276 | 0.24166 | 5.4505 | [9 empty] | 366.8 | 90.8 | 120.561 | 0.92137
|  | 546.6 | 270.6 | 130.5282 | 2.4302 | 0.33904 | 3.9895 | [9 empty] | 367 | 91 | 119.7819 | 1.0139
|  | 546.8 | 270.8 | 130.6256 | 2.138 | 0.24166 | 0.97026 | [9 empty] | 367.2 | 91.2 | 124.0673 | 0.5399
|  | 547 | 271 | 130.5282 | 2.138 | 0.24166 | 1.2624 | [9 empty] | 367.4 | 91.4 | 126.4048 | 0.22337
|  | 547.2 | 271.2 | 130.5282 | 2.4302 | 0.24166 | 2.626 | [9 empty] | 367.6 | 91.6 | 127.5736 | 0.098373
|  | 547.4 | 271.4 | 130.5282 | 2.4302 | 0.24166 | 4.0869 | [9 empty] | 367.8 | 91.8 | 127.671 | 0.078894
|  | 547.6 | 271.6 | 130.5282 | 2.138 | 0.24166 | 3.7948 | [9 empty] | 368 | 92 | 127.5736 | 0.078894
|  | 547.8 | 271.8 | 130.5282 | 2.138 | 0.33904 | 1.0676 | [9 empty] | 368.2 | 92.2 | 126.4048 | 0.22824
|  | 548 | 272 | 130.4308 | 2.2354 | 0.33904 | 2.8208 | [9 empty] | 368.4 | 92.4 | 126.7944 | 0.1698
|  | 548.2 | 272.2 | 130.5282 | 2.5276 | 0.33904 | 3.4052 | [9 empty] | 368.6 | 92.6 | 126.7944 | 0.19577
|  | 548.4 | 272.4 | 130.4308 | 2.7224 | 0.33904 | 0.87284 | [9 empty] | 368.8 | 92.8 | 126.0153 | 0.23148
|  | 548.6 | 272.6 | 130.5282 | 2.3328 | 0.33904 | 0.38586 | [9 empty] | 369 | 93 | 126.7944 | 0.19415
|  | 548.8 | 272.8 | 130.4308 | 2.7224 | 0.24166 | 0.87284 | [9 empty] | 369.2 | 93.2 | 124.8465 | 0.40193
|  | 549 | 273 | 130.5282 | 3.0146 | 0.33904 | 0.38586 | [9 empty] | 369.4 | 93.4 | 126.2101 | 0.2607
|  | 549.2 | 273.2 | 130.6256 | 3.2094 | 0.24166 | 0.28848 | [9 empty] | 369.6 | 93.6 | 125.4309 | 0.36621
|  | 549.4 | 273.4 | 130.5282 | 3.2094 | 0.24166 | 0.28848 | [9 empty] | 369.8 | 93.8 | 126.4048 | 0.24772
|  | 549.6 | 273.6 | 130.5282 | 3.5016 | 0.33904 | 3.6 | [9 empty] | 370 | 94 | 127.3788 | 0.10649
|  | 549.8 | 273.8 | 130.5282 | 3.599 | 0.53384 | 1.3598 | [9 empty] | 370.2 | 94.2 | 126.3074 | 0.24934
|  | 550 | 274 | 130.5282 | 3.7938 | 0.53384 | 1.9442 | [9 empty] | 370.4 | 94.4 | 125.8205 | 0.30615
|  | 550.2 | 274.2 | 130.5282 | 3.599 | 0.53384 | 0.58066 | [9 empty] | 370.6 | 94.6 | 126.8918 | 0.16168
|  | 550.4 | 274.4 | 130.5282 | 1.8458 | 0.14424 | 2.5286 | [9 empty] | 370.8 | 94.8 | 125.3335 | 0.34349
|  | 550.6 | 274.6 | 130.5282 | 3.8911 | 0.82602 | 1.5546 | [9 empty] | 371 | 95 | 125.0413 | 0.39056
|  | 550.8 | 274.8 | 130.4308 | 4.3781 | 0.33904 | 2.2364 | [9 empty] | 371.2 | 95.2 | 126.0153 | 0.26232
|  | 551 | 275 | 130.5282 | 4.6703 | 0.33904 | 1.7494 | [9 empty] | 371.4 | 95.4 | 127.184 | 0.13084
|  | 551.2 | 275.2 | 130.4308 | 4.7677 | 0.63122 | 1.4572 | [9 empty] | 371.6 | 95.6 | 126.9892 | 0.15681
|  | 551.4 | 275.4 | 130.4308 | 5.0599 | 0.63122 | 1.7494 | [9 empty] | 371.8 | 95.8 | 126.8918 | 0.15519
|  | 551.6 | 275.6 | 130.5282 | 5.4495 | 0.43642 | 1.4572 | [9 empty] | 372 | 96 | 126.5996 | 0.17791
|  | 551.8 | 275.8 | 130.5282 | 5.3521 | 0.33904 | 2.626 | [9 empty] | 372.2 | 96.2 | 126.4048 | 0.21038
|  | 552 | 276 | 130.5282 | 5.5469 | 0.33904 | 2.3338 | [9 empty] | 372.4 | 96.4 | 126.0153 | 0.25745
|  | 552.2 | 276.2 | 130.5282 | 5.9365 | 0.24166 | 1.3598 | [9 empty] | 372.6 | 96.6 | 125.9178 | 0.2818
|  | 552.4 | 276.4 | 130.5282 | 5.9365 | 0.43642 | 1.652 | [9 empty] | 372.8 | 96.8 | 125.6257 | 0.32726
|  | 552.6 | 276.6 | 130.5282 | 6.5208 | 0.72864 | 2.2364 | [9 empty] | 373 | 97 | 126.2101 | 0.24934
|  | 552.8 | 276.8 | 130.5282 | 6.5208 | 0.63122 | 0.77546 | [9 empty] | 373.2 | 97.2 | 126.5996 | 0.1909
|  | 553 | 277 | 130.5282 | 6.8131 | 0.82602 | 2.139 | [9 empty] | 373.4 | 97.4 | 125.6257 | 0.31589
|  | 553.2 | 277.2 | 130.3334 | 7.2026 | 0.82602 | 1.5546 | [9 empty] | 373.6 | 97.6 | 124.1647 | 0.50582
|  | 553.4 | 277.4 | 130.3334 | 9.3453 | 0.82602 | 0.87284 | [9 empty] | 373.8 | 97.8 | 124.8465 | 0.41816
|  | 553.6 | 277.6 | 130.4308 | 14.7022 | 0.43642 | 1.5546 | [9 empty] | 374 | 98 | 125.1387 | 0.37108
|  | 553.8 | 277.8 | 130.4308 | 16.8449 | 0.63122 | 1.1651 | [9 empty] | 374.2 | 98.2 | 126.8918 | 0.18928
|  | 554 | 278 | 130.3334 | 18.5006 | 0.63122 | 1.5546 | [9 empty] | 374.4 | 98.4 | 127.184 | 0.14707
|  | 554.2 | 278.2 | 130.3334 | 21.2277 | 0.82602 | 2.9182 | [9 empty] | 374.6 | 98.6 | 126.697 | 0.18928
|  | 554.4 | 278.4 | 130.3334 | 22.4939 | 1.1182 | 1.5546 | [9 empty] | 374.8 | 98.8 | 126.0153 | 0.28018
|  | 554.6 | 278.6 | 130.236 | 25.221 | 0.9234 | 2.2364 | [9 empty] | 375 | 99 | 125.9178 | 0.29641
|  | 554.8 | 278.8 | 130.236 | 25.8054 | 0.9234 | 4.4765 | [9 empty] | 375.2 | 99.2 | 126.3074 | 0.23473
|  | 555 | 279 | 130.236 | 29.6038 | 0.72864 | 2.626 | [9 empty] | 375.4 | 99.4 | 125.5283 | 0.33375
|  | 555.2 | 279.2 | 130.3334 | 33.3049 | 1.6052 | 5.2557 | [9 empty] | 375.6 | 99.6 | 124.2621 | 0.49121
|  | 555.4 | 279.4 | 130.236 | 38.4669 | 1.7026 | 1.652 | [9 empty] | 375.8 | 99.8 | 123.8725 | 0.53016
|  | 555.6 | 279.6 | 129.9438 | 30.6752 | 4.9167 | 1.5546 | [9 empty] | 376 | 100 | 124.5543 | 0.46361
|  | 555.8 | 279.8 | 129.749 | 29.1169 | 9.4943 | 2.2364 | [9 empty] | 376.2 | 100.2 | 124.4569 | 0.48147
|  | 556 | 280 | 129.8464 | 31.4543 | 1.6052 | 9.1516 | [9 empty] | 376.4 | 100.4 | 123.6777 | 0.56101
|  | 556.2 | 280.2 | 129.8464 | 32.7205 | 0.43642 | 5.2557 | [9 empty] | 376.6 | 100.6 | 124.0673 | 0.51231
|  | 556.4 | 280.4 | 130.0412 | 34.2789 | 0.24166 | 6.2297 | [9 empty] | 376.8 | 100.8 | 124.3595 | 0.44413
|  | 556.6 | 280.6 | 129.9438 | 38.0773 | 0.14424 | 4.1843 | [9 empty] | 377 | 101 | 124.3595 | 0.47335
|  | 556.8 | 280.8 | 130.236 | 40.0253 | 0.24166 | 1.9442 | [9 empty] | 377.2 | 101.2 | 124.0673 | 0.4766
|  | 557 | 281 | 130.236 | 40.707 | 0.33904 | 0.77546 | [9 empty] | 377.4 | 101.4 | 123.2881 | 0.57562
|  | 557.2 | 281.2 | 130.1386 | 41.194 | 0.33904 | 0.87284 | [9 empty] | 377.6 | 101.6 | 122.996 | 0.63405
|  | 557.4 | 281.4 | 130.236 | 41.681 | 0.63122 | 0.58066 | [9 empty] | 377.8 | 101.8 | 123.9699 | 0.53016
|  | 557.6 | 281.6 | 130.1386 | 43.7263 | 0.33904 | 3.5025 | [9 empty] | 378 | 102 | 124.5543 | 0.44575
|  | 557.8 | 281.8 | 130.236 | 44.8951 | 0.33904 | 0.97026 | [9 empty] | 378.2 | 102.2 | 122.509 | 0.68762
|  | 558 | 282 | 130.0412 | 44.0185 | 0.63122 | 2.8208 | [9 empty] | 378.4 | 102.4 | 120.7558 | 0.90027
|  | 558.2 | 282.2 | 130.0412 | 45.5768 | 0.9234 | 5.2557 | [9 empty] | 378.6 | 102.6 | 120.6585 | 0.90027
|  | 558.4 | 282.4 | 130.1386 | 45.5768 | 0.63122 | 4.1843 | [9 empty] | 378.8 | 102.8 | 119.9767 | 0.99442
|  | 558.6 | 282.6 | 130.1386 | 46.843 | 1.5078 | 2.7234 | [9 empty] | 379 | 103 | 121.4376 | 0.80125
|  | 558.8 | 282.8 | 130.236 | 46.7456 | 1.7026 | 1.652 | [9 empty] | 379.2 | 103.2 | 123.9699 | 0.52043
|  | 559 | 283 | 130.236 | 48.6935 | 1.1182 | 1.2624 | [9 empty] | 379.4 | 103.4 | 124.3595 | 0.46036
|  | 559.2 | 283.2 | 130.1386 | 48.4014 | 2.4818 | 1.0676 | [9 empty] | 379.6 | 103.6 | 123.0934 | 0.64542
|  | 559.4 | 283.4 | 130.236 | 48.0118 | 1.7026 | 0.77546 | [9 empty] | 379.8 | 103.8 | 123.1908 | 0.59185
|  | 559.6 | 283.6 | 129.6516 | 48.2066 | 11.15 | 0.87284 | [9 empty] | 380 | 104 | 122.8986 | 0.64217
|  | 559.8 | 283.8 | 130.0412 | 49.2779 | 7.1568 | 0.77546 | [9 empty] | 381 | 105 | 121.3402 | 0.83047
|  | 560 | 284 | 130.1386 | 49.6675 | 1.313 | 0.58066 | [9 empty] | 382 | 106 | 113.8407 | 1.7087
|  | 560.2 | 284.2 | 130.1386 | 50.9337 | 0.43642 | 1.652 | [9 empty] | 383 | 107 | 106.4385 | 2.5787
|  | 560.4 | 284.4 | 129.9438 | 53.2712 | 1.313 | 6.3271 | [9 empty] | 384 | 108 | 102.7375 | 3.0057
|  | 560.6 | 284.6 | 130.1386 | 52.005 | 1.0208 | 5.5479 | [9 empty] | 385 | 109 | 98.8416 | 3.4537
|  | 560.8 | 284.8 | 129.9438 | 50.6415 | 1.5078 | 5.3531 | [9 empty] | 386 | 110 | 102.0557 | 3.0625
|  | 561 | 285 | 129.8464 | 50.5441 | 0.43642 | 8.1776 | [9 empty] | 387 | 111 | 96.2119 | 3.7329
|  | 561.2 | 285.2 | 130.0412 | 53.466 | 0.53384 | 6.3271 | [9 empty] | 388 | 112 | 93.6796 | 4.0413
|  | 561.4 | 285.4 | 130.236 | 54.5374 | 0.53384 | 1.1651 | [9 empty] | 389 | 113 | 87.2514 | 4.728
|  | 561.6 | 285.6 | 130.1386 | 54.1478 | 0.63122 | 1.1651 | [9 empty] | 390 | 114 | 88.3228 | 4.5851
|  | 561.8 | 285.8 | 129.9438 | 53.953 | 0.63122 | 4.1843 | [9 empty] | 391 | 115 | 87.641 | 4.6598
|  | 562 | 286 | 129.9438 | 53.5634 | 1.8974 | 3.8921 | [9 empty] | 392 | 116 | 87.8358 | 4.5673
|  | 562.2 | 286.2 | 130.236 | 56.8748 | 1.1182 | 1.4572 | [9 empty] | 393 | 117 | 82.479 | 5.1841
|  | 562.4 | 286.4 | 129.8464 | 57.2644 | 0.82602 | 10.0281 | [9 empty] | 394 | 118 | 81.992 | 5.1906
|  | 562.6 | 286.6 | 130.1386 | 55.4139 | 0.53384 | 2.4312 | [9 empty] | 395 | 119 | 83.2582 | 5.0494
|  | 562.8 | 286.8 | 129.4568 | 55.6087 | 0.72864 | 13.3396 | [9 empty] | 396 | 120 | 83.453 | 4.9942
|  | 563 | 287 | 129.6516 | 57.7514 | 0.53384 | 10.3203 | [9 empty] | 397 | 121 | 82.479 | 5.0964
|  | 563.2 | 287.2 | 129.9438 | 62.7187 | 0.43642 | 5.0609 | [9 empty] | 398 | 122 | 87.1541 | 4.5802
|  | 563.4 | 287.4 | 130.0412 | 60.9655 | 0.9234 | 1.2624 | [9 empty] | 399 | 123 | 100.1078 | 3.1501
|  | 563.6 | 287.6 | 130.1386 | 59.7968 | 0.82602 | 0.38586 | [9 empty] | 400 | 124 | 94.4588 | 3.7848
|  | 563.8 | 287.8 | 130.1386 | 62.1343 | 0.24166 | 0.28848 | [9 empty] | 400.2 | 124.2 | 94.8484 | 3.7296
|  | 564 | 288 | 130.0412 | 61.6473 | 0.24166 | 0.28848 | [9 empty] | 400.4 | 124.4 | 96.1145 | 3.5965
|  | 564.2 | 288.2 | 130.1386 | 61.9395 | 0.33904 | 0.19109 | [9 empty] | 400.6 | 124.6 | 93.6796 | 3.8416
|  | 564.4 | 288.4 | 129.9438 | 61.8421 | 1.1182 | 1.0676 | [9 empty] | 400.8 | 124.8 | 94.4588 | 3.7313
|  | 564.6 | 288.6 | 130.0412 | 62.7187 | 0.33904 | 0.58066 | [9 empty] | 401 | 125 | 91.1473 | 4.1014
|  | 564.8 | 288.8 | 130.0412 | 63.4978 | 0.33904 | 0.38586 | [9 empty] | 401.2 | 125.2 | 87.1541 | 4.577
|  | 565 | 289 | 129.9438 | 63.4978 | 0.53384 | 0.77546 | [9 empty] | 401.4 | 125.4 | 83.8426 | 4.9146
|  | 565.2 | 289.2 | 129.9438 | 63.79 | 2.8714 | 0.87284 | [9 empty] | 401.6 | 125.6 | 91.9265 | 4.0381
|  | 565.4 | 289.4 | 130.0412 | 64.5692 | 0.43642 | 0.77546 | [9 empty] | 401.8 | 125.8 | 100.1078 | 3.1355
|  | 565.6 | 289.6 | 130.0412 | 65.1536 | 0.24166 | 1.4572 | [9 empty] | 402 | 126 | 103.7115 | 2.7232
|  | 565.8 | 289.8 | 129.8464 | 67.1015 | 0.33904 | 3.9895 | [9 empty] | 402.2 | 126.2 | 109.6527 | 2.0512
|  | 566 | 290 | 129.749 | 70.9973 | 0.24166 | 5.0609 | [9 empty] | 402.4 | 126.4 | 111.8928 | 1.7703
|  | 566.2 | 290.2 | 129.3595 | 89.3079 | 0.33904 | 11.2943 | [9 empty] | 402.6 | 126.6 | 102.0557 | 2.8693
|  | 566.4 | 290.4 | 129.4568 | 94.3725 | 0.24166 | 10.5151 | [9 empty] | 402.8 | 126.8 | 111.698 | 1.8385
|  | 566.6 | 290.6 | 129.0672 | 94.6647 | 0.24166 | 18.8912 | [9 empty] | 403 | 127 | 114.0355 | 1.5187
|  | 566.8 | 290.8 | 128.5803 | 94.4699 | 0.33904 | 27.1699 | [9 empty] | 403.2 | 127.2 | 97.2833 | 3.4618
|  | 567 | 291 | 128.9699 | 95.0543 | 0.33904 | 19.086 | [9 empty] | 403.4 | 127.4 | 106.536 | 2.4294
|  | 567.2 | 291.2 | 129.5542 | 99.6319 | 0.33904 | 8.9568 | [9 empty] | 403.6 | 127.6 | 102.0557 | 2.8855
|  | 567.4 | 291.4 | 129.8464 | 100.5085 | 0.24166 | 1.8468 | [9 empty] | 403.8 | 127.8 | 93.4848 | 3.8757
|  | 567.6 | 291.6 | 129.5542 | 100.8981 | 3.7479 | 0.48328 | [9 empty] | 404 | 128 | 95.725 | 3.5998
|  | 567.8 | 291.8 | 129.749 | 100.4111 | 2.8714 | 0.38586 | [9 empty] | 404.2 | 128.2 | 104.8802 | 2.5966
|  | 568 | 292 | 129.4568 | 100.5085 | 2.9687 | 16.0667 | [9 empty] | 404.4 | 128.4 | 109.9448 | 2.0122
|  | 568.2 | 292.2 | 129.4568 | 96.5153 | 11.7344 | 2.9182 | [9 empty] | 404.6 | 128.6 | 108.6787 | 2.1697
|  | 568.4 | 292.4 | 129.749 | 102.7486 | 3.2609 | 0.77546 | [9 empty] | 404.8 | 128.8 | 110.1396 | 2.0057
|  | 568.6 | 292.6 | 128.9699 | 95.1517 | 6.2802 | 7.8854 | [9 empty] | 405 | 129 | 106.6333 | 2.418
|  | 568.8 | 292.8 | 129.1647 | 103.0408 | 2.0922 | 16.6511 | [9 empty] | 405.2 | 129.2 | 103.614 | 2.7378
|  | 569 | 293 | 129.1647 | 104.0148 | 5.7933 | 17.0407 | [9 empty] | 405.4 | 129.4 | 104.588 | 2.6388
|  | 569.2 | 293.2 | 129.1647 | 104.4044 | 1.1182 | 17.7225 | [9 empty] | 405.6 | 129.6 | 107.3151 | 2.3417
|  | 569.4 | 293.4 | 128.8725 | 104.4044 | 0.63122 | 19.7678 | [9 empty] | 405.8 | 129.8 | 108.4839 | 2.194
|  | 569.6 | 293.6 | 129.1647 | 104.6966 | 0.24166 | 17.7225 | [9 empty] | 406 | 130 | 107.3151 | 2.3401
|  | 569.8 | 293.8 | 129.262 | 104.5018 | 0.72864 | 21.3261 | [9 empty] | 406.2 | 130.2 | 104.8802 | 2.6015
|  | 570 | 294 | 128.9699 | 104.5991 | 0.82602 | 25.0272 | [9 empty] | 406.4 | 130.4 | 103.0297 | 2.8157
|  | 570.2 | 294.2 | 129.5542 | 105.2809 | 0.33904 | 15.9693 | [9 empty] | 406.6 | 130.6 | 101.9583 | 2.9326
|  | 570.4 | 294.4 | 129.0672 | 104.9887 | 0.53384 | 20.6444 | [9 empty] | 406.8 | 130.8 | 100.0104 | 3.1323
|  | 570.6 | 294.6 | 129.262 | 105.2809 | 1.1182 | 20.06 | [9 empty] | 407 | 131 | 98.3546 | 3.3141
|  | 570.8 | 294.8 | 129.1647 | 105.0862 | 0.24166 | 23.1766 | [9 empty] | 407.2 | 131.2 | 101.1791 | 2.9943
|  | 571 | 295 | 129.262 | 105.2809 | 0.43642 | 24.5402 | [9 empty] | 407.4 | 131.4 | 100.4 | 3.0657
|  | 571.2 | 295.2 | 129.3595 | 105.6705 | 1.9948 | 27.6569 | [9 empty] | 407.6 | 131.6 | 97.3807 | 3.4147
|  | 571.4 | 295.4 | 129.5542 | 105.7679 | 1.313 | 29.5074 | [9 empty] | 407.8 | 131.8 | 97.3807 | 3.4082
|  | 571.6 | 295.6 | 129.6516 | 104.8914 | 0.82602 | 29.3126 | [9 empty] | 408 | 132 | 94.4588 | 3.7426
|  | 571.8 | 295.8 | 129.9438 | 103.7226 | 0.43642 | 23.1766 | [9 empty] | 408.2 | 132.2 | 93.5822 | 3.8108
|  | 572 | 296 | 129.8464 | 103.82 | 0.72864 | 24.3454 | [9 empty] | 408.4 | 132.4 | 83.3556 | 4.8741
|  | 572.2 | 296.2 | 129.749 | 101.4824 | 0.43642 | 12.2682 | [9 empty] | 408.6 | 132.6 | 74.8821 | 5.4016
|  | 572.4 | 296.4 | 129.8464 | 46.3561 | 13.2928 | 10.3203 | [9 empty] | 408.8 | 132.8 | 78.0962 | 5.4016
|  | 572.6 | 296.6 | 129.6516 | 14.3126 | 6.0854 | 14.6058 | [9 empty] | 409 | 133 | 78.778 | 5.249
|  | 572.8 | 296.8 | 129.5542 | 18.3059 | 9.7865 | 16.3589 | [9 empty] | 409.2 | 133.2 | 84.1347 | 4.6841
|  | 573 | 297 | 128.3855 | 21.5199 | 11.15 | 31.4554 | [9 empty] | 409.4 | 133.4 | 87.3489 | 4.4374
|  | 573.2 | 297.2 | 127.1193 | 53.466 | 39.9794 | 30.4814 | [9 empty] | 409.6 | 133.6 | 88.7124 | 4.2962
|  | 573.4 | 297.4 | 128.7751 | 53.2712 | 11.0527 | 29.0205 | [9 empty] | 409.8 | 133.8 | 88.4202 | 4.314
|  | 573.6 | 297.6 | 127.9959 | 57.0696 | 17.8704 | 33.8903 | [9 empty] | 410 | 134 | 96.4067 | 3.4456
|  | 573.8 | 297.8 | 127.3141 | 36.7138 | 28.584 | 36.52 | [9 empty] | 410.2 | 134.2 | 97.2833 | 3.1534
|  | 574 | 298 | 127.4115 | 17.6241 | 13.8771 | 45.3831 | [9 empty] | 410.4 | 134.4 | 98.452 | 2.8498
|  | 574.2 | 298.2 | 127.5089 | 25.9028 | 20.4027 | 39.6367 | [9 empty] | 410.6 | 134.6 | 90.7577 | 3.6615
|  | 574.4 | 298.4 | 126.9245 | 62.4265 | 58.1926 | 37.8835 | [9 empty] | 410.8 | 134.8 | 95.5302 | 3.241
|  | 574.6 | 298.6 | 127.9959 | 98.5606 | 107.183 | 37.3966 | [9 empty] | 411 | 135 | 94.0692 | 3.3368
|  | 574.8 | 298.8 | 128.0933 | 97.0996 | 99.1965 | 37.4939 | [9 empty] | 411.2 | 135.2 | 91.7317 | 3.5673
|  | 575 | 299 | 127.7037 | 105.3783 | 108.157 | 40.5132 | [9 empty] | 411.4 | 135.4 | 89.8811 | 4.1095
|  | 575.2 | 299.2 | 127.7037 | 109.5664 | 112.7346 | 40.3184 | [9 empty] | 411.6 | 135.6 | 93.9718 | 3.7085
|  | 575.4 | 299.4 | 127.9959 | 111.5143 | 114.9747 | 36.3252 | [9 empty] | 411.8 | 135.8 | 93.29 | 3.8189
|  | 575.6 | 299.6 | 127.9959 | 112.2935 | 115.6565 | 36.7148 | [9 empty] | 412 | 136 | 92.4135 | 3.892
|  | 575.8 | 299.8 | 128.3855 | 111.2221 | 116.7279 | 27.6569 | [9 empty] | 412.2 | 136.2 | 87.3489 | 4.4536
|  | 576 | 300 | 128.2881 | 111.4169 | 117.0201 | 27.1699 | [9 empty] | 412.4 | 136.4 | 86.3749 | 4.5315
|  | 576.2 | 300.2 | 128.4829 | 111.0273 | 117.3123 | 26.7803 | [9 empty] | 412.6 | 136.6 | 84.7191 | 4.6939
|  | 576.4 | 300.4 | 128.3855 | 110.7351 | 117.4096 | 30.384 | [9 empty] | 412.8 | 136.8 | 77.5118 | 5.4016
|  | 576.6 | 300.6 | 128.0933 | 112.4883 | 117.7992 | 35.9356 | [9 empty] | 413 | 137 | 80.4337 | 5.1419
|  | 576.8 | 300.8 | 128.4829 | 113.2675 | 118.968 | 26.0011 | [9 empty] | 413.2 | 137.2 | 77.5118 | 5.4016
|  | 577 | 301 | 128.6777 | 117.4555 | 120.2342 | 17.2355 | [9 empty] | 413.4 | 137.4 | 74.4925 | 5.4016
|  | 577.2 | 301.2 | 127.8985 | 117.1633 | 119.6498 | 33.5981 | [9 empty] | 413.6 | 137.6 | 74.0055 | 5.4016
|  | 577.4 | 301.4 | 127.9959 | 117.5529 | 119.942 | 33.5981 | [9 empty] | 413.8 | 137.8 | 42.8386 | 3.5332
|  | 577.6 | 301.6 | 127.8985 | 117.5529 | 119.8446 | 88.6271 | [9 empty] | 414 | 138 | 5.2436 | 0.23473
|  | 577.8 | 301.8 | 128.9699 | 120.8644 | 121.8899 | 121.1576 | [9 empty] | 414.2 | 138.2 | 1.5425 | 0.041559
|  | 578 | 302 | 128.9699 | 120.9618 | 121.9873 | 123.4951 | [9 empty] | 414.4 | 138.4 | 0.86073 | 0.020457
|  | 578.2 | 302.2 | 129.0672 | 120.9618 | 122.0847 | 124.1769 | [9 empty] | 414.6 | 138.6 | 0.66593 | 0.013963
|  | 578.4 | 302.4 | 129.0672 | 121.0592 | 122.1821 | 124.6638 | [9 empty] | 414.8 | 138.8 | 0.56855 | 0.010717
|  | 578.6 | 302.6 | 129.0672 | 121.0592 | 122.1821 | 125.8326 | [9 empty] | 415 | 139 | 0.47113 | 0.0090935
|  | 578.8 | 302.8 | 129.1647 | 121.1566 | 122.1821 | 126.2222 | [9 empty] | 416 | 140 | 0.27633 | 0.0058469
|  | 579 | 303 | 129.1647 | 121.0592 | 122.3769 | 126.3196 | [9 empty] | 417 | 141 | 0.27633 | 0.0042238
|  | 579.2 | 303.2 | 129.1647 | 121.0592 | 122.2795 | 126.2222 | [9 empty] | 418 | 142 | 0.27633 | 0.0042238
|  | 579.4 | 303.4 | 129.0672 | 121.0592 | 122.2795 | 126.2222 | [9 empty] | 419 | 143 | 0.27633 | 0.0026002
|  | 579.6 | 303.6 | 129.0672 | 121.0592 | 122.2795 | 126.1248 | [9 empty] | 420 | 144 | 0.27633 | 0.0042238
|  | 579.8 | 303.8 | 129.0672 | 121.0592 | 122.3769 | 126.2222 | [9 empty] | 430 | 154 | 0.17895 | 0.0026002
|  | 580 | 304 | 128.9699 | 120.9618 | 122.2795 | 126.1248 | [9 empty] | 440 | 164 | 0.17895 | 0.00097717
|  | 590 | 314 | 129.262 | 122.2279 | 124.8118 | 126.904 | [9 empty] | 450 | 174 | 0.17895 | 0.00097717
|  | 600 | 324 | 129.0672 | 118.5269 | 121.6951 | 127.0014 | [9 empty] | 460 | 184 | 0.17895 | 0.00097717
|  | 610 | 334 | 129.0672 | 112.2935 | 123.9352 | 126.8066 | [9 empty] | 470 | 194 | 0.17895 | 0.00097717
|  | 620 | 344 | 129.1647 | 122.8123 | 125.8832 | 127.2936 | [9 empty] | 480 | 204 | 0.17895 | 0.00097717
|  | 630 | 354 | 129.1647 | 123.2993 | 126.7597 | 127.3909 | [9 empty] | 490 | 214 | 0.17895 | 0.00097717
|  | 640 | 364 | 129.3595 | 125.7342 | 127.5389 | 127.6831 | [9 empty] | 500 | 224 | 0.17895 | 0.00097717
|  | 650 | 374 | 129.4568 | 127.5847 | 127.9285 | 127.8779
|  | 660 | 384 | 129.4568 | 128.0717 | 128.1233 | 128.1701
|  | 670 | 394 | 129.3595 | 128.0717 | 128.1233 | 128.2675
|  | 680 | 404 | 129.8464 | 128.1691 | 128.1233 | 128.3649
|  | 690 | 414 | 129.4568 | 128.7535 | 128.7076 | 128.9493
|  | 700 | 424 | 129.4568 | 128.7535 | 128.6103 | 128.8519
|  | 710 | 434 | 129.749 | 129.0457 | 128.8051 | 129.1441
|  | 720 | 444 | 129.3595 | 128.8509 | 128.6103 | 128.8519
|  | 730 | 454 | 129.1647 | 128.5587 | 128.4155 | 128.6571
|  | 740 | 464 | 129.4568 | 128.7535 | 128.6103 | 128.8519
|  | 750 | 474 | 129.262 | 128.6561 | 128.5129 | 128.7545
|  | 760 | 484 | 129.3595 | 128.8509 | 128.6103 | 128.8519
|  | 770 | 494 | 129.3595 | 128.7535 | 128.6103 | 128.8519
|  | 780 | 504 | 129.749 | 129.2405 | 128.9999 | 129.2415
|  | 790 | 514 | 130.1386 | 129.6301 | 129.292 | 129.5337
|  | 800 | 524 | 129.9438 | 129.5326 | 129.1946 | 129.5337
|  | 810 | 534 | 129.5542 | 128.9483 | 128.8051 | 129.0467
|  | 820 | 544 | 129.4568 | 128.8509 | 128.7076 | 129.0467
|  | 830 | 554 | 129.3595 | 128.7535 | 128.5129 | 128.8519
|  | 840 | 564 | 129.3595 | 128.8509 | 128.7076 | 128.8519
|  | 850 | 574 | 129.262 | 128.7535 | 128.6103 | 128.8519
|  | 860 | 584 | 129.3595 | 128.7535 | 128.5129 | 128.8519
|  | 870 | 594 | 129.3595 | 128.7535 | 128.6103 | 128.8519
|  | 880 | 604 | 129.262 | 128.7535 | 128.5129 | 128.7545
|  | 890 | 614 | 129.262 | 128.7535 | 128.7076 | 128.8519
|  | 900 | 624 | 129.3595 | 128.7535 | 128.6103 | 128.8519
|  | 910 | 634 | 129.262 | 128.8509 | 128.6103 | 128.8519
|  | 920 | 644 | 129.3595 | 128.9483 | 128.7076 | 128.9493
|  | 930 | 654 | 129.4568 | 128.9483 | 128.7076 | 129.0467
|  | 940 | 664 | 129.5542 | 129.0457 | 128.8051 | 129.1441
|  | 950 | 674 | 129.5542 | 129.0457 | 128.8051 | 129.0467
|  | 960 | 684 | 129.262 | 128.7535 | 128.6103 | 128.7545
|  | 970 | 694 | 129.1647 | 128.6561 | 128.5129 | 128.6571
|  | 980 | 704 | 129.5542 | 129.0457 | 128.8051 | 129.0467
|  | 990 | 714 | 130.0412 | 129.6301 | 129.292 | 129.631
|  | 1000 | 724 | 130.723 | 130.3118 | 129.8764 | 130.1181
|  | 1010 | 734 | 131.1126 | 130.7014 | 130.266 | 130.605
|  | 1020 | 744 | 131.5022 | 131.091 | 130.5582 | 130.8972
|  | 1030 | 754 | 131.0152 | 130.604 | 130.0712 | 130.4102
|  | 1040 | 764 | 130.723 | 130.2144 | 129.8764 | 130.1181
|  | 1050 | 774 | 130.3334 | 129.9222 | 129.5842 | 129.8258
|  | 1060 | 784 | 130.0412 | 129.4353 | 129.1946 | 129.4363
|  | 1070 | 794 | 129.5542 | 128.8509 | 128.8051 | 129.0467
|  | 1080 | 804 | 129.3595 | 128.9483 | 128.7076 | 128.9493
|  | 1090 | 814 | 129.262 | 128.6561 | 128.6103 | 128.8519
|  | 1100 | 824 | 129.5542 | 129.0457 | 128.8051 | 129.0467
|  | 1110 | 834 | 130.4308 | 129.9222 | 129.5842 | 129.9233
|  | 1120 | 844 | 131.0152 | 130.604 | 130.0712 | 130.4102
|  | 1130 | 854 | 131.5022 | 131.091 | 130.5582 | 130.8972
|  | 1140 | 864 | 131.1126 | 130.7014 | 130.266 | 130.605
|  | 1160 | 884 | 130.0412 | 129.5326 | 129.292 | 129.5337
|  | 1180 | 904 | 129.749 | 129.1431 | 128.9024 | 129.1441
|  | 1200 | 924 | 129.3595 | 128.6561 | 128.6103 | 128.8519
|  | 1220 | 944 | 129.262 | 128.6561 | 128.5129 | 128.7545
|  | 1240 | 964 | 129.4568 | 128.6561 | 128.6103 | 128.8519
|  | 1260 | 984 | 129.9438 | 129.1431 | 128.9024 | 129.1441
|  | 1280 | 1004 | 129.749 | 129.0457 | 128.9999 | 129.2415
|  | 1300 | 1024 | 129.749 | 129.0457 | 128.9999 | 129.2415
|  | 1320 | 1044 | 130.0412 | 129.3379 | 129.0972 | 129.4363
|  | 1340 | 1064 | 130.4308 | 129.8249 | 129.4868 | 129.7285
|  | 1360 | 1084 | 130.236 | 129.7274 | 129.4868 | 129.7285
|  | 1380 | 1104 | 129.8464 | 129.2405 | 129.1946 | 129.3389
|  | 1400 | 1124 | 130.5282 | 130.117 | 129.8764 | 130.1181
|  | 1420 | 1144 | 130.3334 | 129.8249 | 129.5842 | 129.9233
|  | 1440 | 1164 | 129.9438 | 129.2405 | 129.0972 | 129.3389
|  | 1460 | 1184 | 129.9438 | 129.5326 | 129.292 | 129.5337
|  | 1480 | 1204 | 129.6516 | 128.9483 | 128.7076 | 129.0467
|  | 1500 | 1224 | 129.0672 | 128.2665 | 128.2207 | 128.6571
|  | 1520 | 1244 | 129.749 | 128.4613 | 128.4155 | 128.7545
|  | 1540 | 1264 | 129.1647 | 128.3639 | 128.3181 | 128.7545
|  | 1560 | 1284 | 130.1386 | 129.3379 | 129.292 | 129.7285
|  | 1580 | 1304 | 130.6256 | 129.8249 | 129.779 | 130.2154
|  | 1600 | 1324 | 131.21 | 130.7014 | 130.3634 | 130.7998
|  | 1620 | 1344 | 131.5996 | 130.9936 | 130.6556 | 131.1894
|  | 1640 | 1364 | 131.5996 | 131.1884 | 130.8504 | 131.1894
|  | 1660 | 1384 | 130.6256 | 130.0197 | 129.779 | 130.2154
|  | 1680 | 1404 | 130.1386 | 129.4353 | 129.3894 | 129.7285
|  | 1700 | 1424 | 131.0152 | 130.4092 | 130.266 | 130.605
|  | 1720 | 1444 | 129.9438 | 129.2405 | 129.292 | 129.5337
|  | 1740 | 1464 | 129.5542 | 128.8509 | 129.0972 | 129.2415
|  | 1760 | 1484 | 130.5282 | 130.117 | 129.9738 | 130.2154
|  | 1780 | 1504 | 131.5996 | 131.3832 | 130.9478 | 131.2868
|  | 1800 | 1524 | 130.5282 | 130.117 | 129.9738 | 130.2154
|  | 1820 | 1544 | 129.6516 | 129.2405 | 129.1946 | 129.3389
|  | 1840 | 1564 | 129.749 | 129.2405 | 129.1946 | 129.3389
|  | 1860 | 1584 | 129.8464 | 129.4353 | 129.1946 | 129.4363
|  | 1880 | 1604 | 129.9438 | 129.5326 | 129.292 | 129.631
|  | 1900 | 1624 | 130.236 | 129.8249 | 129.5842 | 129.9233
|  | 1920 | 1644 | 130.723 | 130.2144 | 129.8764 | 130.2154
|  | 1940 | 1664 | 131.4048 | 131.091 | 130.5582 | 130.9946
|  | 1960 | 1684 | 131.3074 | 131.091 | 130.5582 | 131.092
|  | 1980 | 1704 | 131.3074 | 130.9936 | 130.4608 | 130.9946
|  | 2000 | 1724 | 130.5282 | 130.3118 | 129.8764 | 130.4102
|  | 2020 | 1744 | 129.6516 | 129.2405 | 128.9999 | 129.4363
|  | 2040 | 1764 | 129.4568 | 128.9483 | 128.9024 | 129.1441
|  | 2060 | 1784 | 129.4568 | 129.0457 | 128.9024 | 129.2415
|  | 2080 | 1804 | 129.5542 | 129.2405 | 128.9999 | 129.2415
|  | 2100 | 1824 | 131.0152 | 130.7014 | 130.1686 | 130.5076
|  | 2120 | 1844 | 131.0152 | 130.7014 | 130.266 | 130.605
|  | 2140 | 1864 | 129.4568 | 129.0457 | 128.8051 | 129.2415
|  | 2160 | 1884 | 129.5542 | 128.8509 | 128.6103 | 129.0467
|  | 2180 | 1904 | 131.3074 | 130.7988 | 130.1686 | 130.7998
|  | 2200 | 1924 | 130.723 | 130.0197 | 129.6816 | 130.2154
|  | 2220 | 1944 | 130.5282 | 129.8249 | 129.4868 | 130.0206
|  | 2240 | 1964 | 129.749 | 128.7535 | 128.7076 | 129.2415
|  | 2260 | 1984 | 129.262 | 127.8769 | 128.1233 | 128.6571
|  | 2277.8 | 2001.8 | 129.4568 | 127.8769 | 128.2207 | 128.8519