## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 4, Location G
Test conditions: Cable: 3-conductor plus drain wire, 8 AWG, XLPE insulated, Hypalon jacketed, Rockbestos Firewall III. (Item #14) Cable specimens present: One length of cable was monitored for electrical performance, a second length of cable monitored for temperature response, no other cable samples present. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position G in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate. Electrical repsonse monitoring: IRMS system using four channels - one for each insulated conductor and a fourth for the un-insulated drain wire (the drain was treated as a fourth conductor and was not grounded), cable tray was grounded. Thermal response monitoring: One cable temperature (see thermocouple map), air temperatures above and below the cable, and the cable tray rung temperature. Gas burner initiated: Following 276 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
276 | 0 | Ignited Gas Burner
2091 | 1815 | Extinguished Gas Burner
Additional Observations
Observation 1 | Note: For a light power cable of this type, the drain wire would normally be grounded. Using the IRMS system, the drain was treated as a fourth conductor independent of the external ground (the conduit).
Observation 2 | No indication of cable failure occurred during this test.
Observation 3 | Post-test visual examination indicated that this cable did not appear to be damaged during the test.
Observation 4 | Post-test check of the IRMS hook-up with a digital multimeter indicated that all connections were intact and no shorts were evident between conductors or between conductors and ground.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
Cable = XLPE, 3/C (Item #14)
Translation to data file names used in "Temperatures" WorkSheet:
| Map Name |  | Location
| G1 | = | Within cable just below cable jacket, center position
| G2 | = | Air above cable
| G3 | = | Air below cable

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 4 |  |  | 2006-10-30 | 10:40
XLPE | 3-C | Tray G
0 | 250 kW
Burner Time | C1-2 | Burner Time | C1-3 | Burner Time | C1-4 | Burner Time | C2-3 | Burner Time | C2-4 | Burner Time | C3-4 | Burner Time | Minimums
-275.5 | 211201.9994 | -272.5 | 211201.9994 | -269.5 | 211201.9994 | -267 | 211201.9994 | -264 | 211201.9994 | -261.5 | 211201.9994 | -275.5 | 211201.9994
-258.5 | 211201.9994 | -255.5 | 211201.9994 | -253 | 422503.9997 | -250 | 211201.9994 | -247.5 | 211201.9994 | -244.5 | 422503.9997 | -258.5 | 211201.9994
-241.5 | 422503.9997 | -239 | 211201.9994 | -236 | 211201.9994 | -233.5 | 211201.9994 | -230.5 | 422503.9997 | -227.5 | 211201.9994 | -241.5 | 211201.9994
-225 | 211201.9994 | -222 | 211201.9994 | -219.5 | 211201.9994 | -216.5 | 211201.9994 | -213.5 | 211201.9994 | -211 | 211201.9994 | -225 | 211201.9994
-208 | 422503.9997 | -205.5 | 211201.9994 | -202.5 | 211201.9994 | -199.5 | 211201.9994 | -197 | 211201.9994 | -194 | 211201.9994 | -208 | 211201.9994
-191.5 | 211201.9994 | -188.5 | 211201.9994 | -185.5 | 211201.9994 | -183 | 422503.9997 | -180 | 211201.9994 | -177.5 | 211201.9994 | -191.5 | 211201.9994
-174.5 | 211201.9994 | -172 | 211201.9994 | -169 | 211201.9994 | -166.5 | 211201.9994 | -163.5 | 211201.9994 | -160.5 | 211201.9994 | -174.5 | 211201.9994
-158 | 422503.9997 | -155 | 422503.9997 | -152 | 422503.9997 | -149.5 | 422503.9997 | -146.5 | 211201.9994 | -144 | 422503.9997 | -158 | 211201.9994
-141 | 211201.9994 | -138 | 211201.9994 | -135.5 | 211201.9994 | -132.5 | 422503.9997 | -129.5 | 211201.9994 | -127 | 211201.9994 | -141 | 211201.9994
-124 | 211201.9994 | -121.5 | 422503.9997 | -118.5 | 422503.9997 | -115.5 | 211201.9994 | -113 | 211201.9994 | -110 | 211201.9994 | -124 | 211201.9994
-107.5 | 211201.9994 | -104.5 | 211201.9994 | -102 | 211201.9994 | -99 | 422503.9997 | -96.5 | 211201.9994 | -93.5 | 211201.9994 | -107.5 | 211201.9994
-90.5 | 211201.9994 | -87.5 | 211201.9994 | -85 | 211201.9994 | -82 | 211201.9994 | -79.5 | 211201.9994 | -76.5 | 211201.9994 | -90.5 | 211201.9994
-73.5 | 211201.9994 | -71 | 211201.9994 | -68.5 | 211201.9994 | -65.5 | 211201.9994 | -62.5 | 211201.9994 | -59.5 | 211201.9994 | -73.5 | 211201.9994
-57 | 211201.9994 | -54 | 211201.9994 | -51.5 | 211201.9994 | -48.5 | 211201.9994 | -46 | 211201.9994 | -43 | 211201.9994 | -57 | 211201.9994
-40.5 | 211201.9994 | -37.5 | 211201.9994 | -34.5 | 211201.9994 | -31.5 | 211201.9994 | -29 | 211201.9994 | -26 | 211201.9994 | -40.5 | 211201.9994
-23.5 | 211201.9994 | -20.5 | 422503.9997 | -17.5 | 211201.9994 | -15 | 211201.9994 | -12.5 | 211201.9994 | -9.5 | 211201.9994 | -23.5 | 211201.9994
-6.5 | 211201.9994 | -3.5 | 211201.9994 | -1 | 211201.9994 | 2 | 211201.9994 | 4.5 | 211201.9994 | 7.5 | 211201.9994 | -6.5 | 211201.9994
10.5 | 211201.9994 | 13 | 211201.9994 | 16 | 422503.9997 | 18.5 | 211201.9994 | 21.5 | 211201.9994 | 24.5 | 211201.9994 | 10.5 | 211201.9994
27 | 211201.9994 | 30 | 211201.9994 | 32.5 | 211201.9994 | 35.5 | 211201.9994 | 38.5 | 211201.9994 | 41 | 211201.9994 | 27 | 211201.9994
44 | 422503.9997 | 46.5 | 211201.9994 | 49.5 | 211201.9994 | 52 | 211201.9994 | 55 | 211201.9994 | 57.5 | 211201.9994 | 44 | 211201.9994
60.5 | 422503.9997 | 63.5 | 422503.9997 | 66 | 211201.9994 | 69 | 211201.9994 | 71.5 | 211201.9994 | 74.5 | 211201.9994 | 60.5 | 211201.9994
77.5 | 422503.9997 | 80 | 211201.9994 | 83 | 211201.9994 | 85.5 | 211201.9994 | 88.5 | 211201.9994 | 91.5 | 211201.9994 | 77.5 | 211201.9994
94.5 | 211201.9994 | 97 | 211201.9994 | 99.5 | 422503.9997 | 102.5 | 211201.9994 | 105.5 | 211201.9994 | 108 | 211201.9994 | 94.5 | 211201.9994
111 | 211201.9994 | 114 | 211201.9994 | 116.5 | 211201.9994 | 119.5 | 211201.9994 | 122 | 211201.9994 | 125 | 211201.9994 | 111 | 211201.9994
127.5 | 422503.9997 | 130.5 | 211201.9994 | 133.5 | 211201.9994 | 136.5 | 211201.9994 | 139 | 211201.9994 | 142 | 422503.9997 | 127.5 | 211201.9994
144.5 | 211201.9994 | 147.5 | 422503.9997 | 150 | 211201.9994 | 153 | 422503.9997 | 155.5 | 211201.9994 | 158.5 | 211201.9994 | 144.5 | 211201.9994
161.5 | 211201.9994 | 164 | 211201.9994 | 167 | 211201.9994 | 169.5 | 211201.9994 | 172.5 | 211201.9994 | 175.5 | 211201.9994 | 161.5 | 211201.9994
178.5 | 211201.9994 | 181 | 211201.9994 | 184 | 211201.9994 | 186.5 | 211201.9994 | 189.5 | 211201.9994 | 192.5 | 211201.9994 | 178.5 | 211201.9994
195 | 211201.9994 | 197.5 | 211201.9994 | 200.5 | 211201.9994 | 203.5 | 211201.9994 | 206 | 211201.9994 | 209 | 422503.9997 | 195 | 211201.9994
211.5 | 211201.9994 | 214.5 | 211201.9994 | 217.5 | 211201.9994 | 220 | 422503.9997 | 223 | 211201.9994 | 225.5 | 211201.9994 | 211.5 | 211201.9994
228.5 | 211201.9994 | 231.5 | 211201.9994 | 234 | 211201.9994 | 237 | 211201.9994 | 240 | 211201.9994 | 242.5 | 211201.9994 | 228.5 | 211201.9994
245.5 | 211201.9994 | 248.5 | 211201.9994 | 251 | 211201.9994 | 254 | 211201.9994 | 256.5 | 211201.9994 | 259.5 | 211201.9994 | 245.5 | 211201.9994
262 | 211201.9994 | 265 | 211201.9994 | 267.5 | 211201.9994 | 270.5 | 422503.9997 | 273.5 | 211201.9994 | 276 | 211201.9994 | 262 | 211201.9994
279 | 211201.9994 | 281.5 | 211201.9994 | 284.5 | 211201.9994 | 287.5 | 211201.9994 | 290 | 211201.9994 | 293 | 211201.9994 | 279 | 211201.9994
295.5 | 211201.9994 | 298.5 | 211201.9994 | 301.5 | 211201.9994 | 304 | 211201.9994 | 307 | 211201.9994 | 309.5 | 211201.9994 | 295.5 | 211201.9994
312.5 | 211201.9994 | 315.5 | 211201.9994 | 318.5 | 211201.9994 | 321 | 211201.9994 | 323.5 | 211201.9994 | 326.5 | 211201.9994 | 312.5 | 211201.9994
329.5 | 211201.9994 | 332 | 211201.9994 | 335 | 211201.9994 | 338 | 211201.9994 | 340.5 | 211201.9994 | 343.5 | 211201.9994 | 329.5 | 211201.9994
346 | 211201.9994 | 349 | 211201.9994 | 351.5 | 211201.9994 | 354.5 | 211201.9994 | 357.5 | 211201.9994 | 360 | 211201.9994 | 346 | 211201.9994
363 | 211201.9994 | 365.5 | 211201.9994 | 368.5 | 211201.9994 | 371.5 | 422503.9997 | 374 | 211201.9994 | 377 | 211201.9994 | 363 | 211201.9994
379.5 | 211201.9994 | 382.5 | 211201.9994 | 385.5 | 211201.9994 | 388.5 | 211201.9994 | 391 | 211201.9994 | 394 | 211201.9994 | 379.5 | 211201.9994
396.5 | 211201.9994 | 399.5 | 211201.9994 | 402.5 | 211201.9994 | 405 | 211201.9994 | 407.5 | 211201.9994 | 410.5 | 211201.9994 | 396.5 | 211201.9994
413.5 | 211201.9994 | 416 | 211201.9994 | 419 | 211201.9994 | 421.5 | 211201.9994 | 424.5 | 211201.9994 | 427.5 | 211201.9994 | 413.5 | 211201.9994
430 | 211201.9994 | 433 | 211201.9994 | 435.5 | 211201.9994 | 438.5 | 211201.9994 | 441.5 | 211201.9994 | 444 | 211201.9994 | 430 | 211201.9994
447 | 211201.9994 | 449.5 | 211201.9994 | 452.5 | 211201.9994 | 455.5 | 211201.9994 | 458 | 211201.9994 | 461 | 211201.9994 | 447 | 211201.9994
463.5 | 211201.9994 | 466.5 | 211201.9994 | 469.5 | 211201.9994 | 472 | 211201.9994 | 475 | 422503.9997 | 477.5 | 211201.9994 | 463.5 | 211201.9994
480.5 | 211201.9994 | 483.5 | 211201.9994 | 486 | 211201.9994 | 489 | 211201.9994 | 491.5 | 422503.9997 | 494.5 | 422503.9997 | 480.5 | 211201.9994
497.5 | 211201.9994 | 500 | 211201.9994 | 503 | 211201.9994 | 506 | 211201.9994 | 508.5 | 211201.9994 | 511.5 | 211201.9994 | 497.5 | 211201.9994
514 | 211201.9994 | 517 | 211201.9994 | 519.5 | 211201.9994 | 522.5 | 211201.9994 | 525.5 | 422503.9997 | 528 | 211201.9994 | 514 | 211201.9994
531 | 211201.9994 | 533.5 | 211201.9994 | 536.5 | 211201.9994 | 539.5 | 211201.9994 | 542 | 211201.9994 | 545 | 211201.9994 | 531 | 211201.9994
547.5 | 211201.9994 | 550.5 | 422503.9997 | 553.5 | 211201.9994 | 556 | 211201.9994 | 559 | 211201.9994 | 561.5 | 211201.9994 | 547.5 | 211201.9994
564.5 | 211201.9994 | 567.5 | 211201.9994 | 570 | 211201.9994 | 573 | 211201.9994 | 575.5 | 211201.9994 | 578.5 | 211201.9994 | 564.5 | 211201.9994
581.5 | 211201.9994 | 584 | 211201.9994 | 587 | 211201.9994 | 589.5 | 211201.9994 | 592.5 | 211201.9994 | 595.5 | 211201.9994 | 581.5 | 211201.9994
598 | 211201.9994 | 601 | 211201.9994 | 603.5 | 211201.9994 | 606.5 | 211201.9994 | 609.5 | 211201.9994 | 612 | 211201.9994 | 598 | 211201.9994
615 | 211201.9994 | 617.5 | 211201.9994 | 620.5 | 211201.9994 | 623.5 | 211201.9994 | 626 | 211201.9994 | 629 | 211201.9994 | 615 | 211201.9994
631.5 | 211201.9994 | 634.5 | 211201.9994 | 637.5 | 211201.9994 | 640 | 211201.9994 | 643 | 211201.9994 | 645.5 | 211201.9994 | 631.5 | 211201.9994
648.5 | 211201.9994 | 651.5 | 211201.9994 | 654 | 211201.9994 | 657 | 211201.9994 | 659.5 | 211201.9994 | 662.5 | 211201.9994 | 648.5 | 211201.9994
665.5 | 211201.9994 | 668 | 422503.9997 | 671 | 422503.9997 | 673.5 | 211201.9994 | 676.5 | 211201.9994 | 679.5 | 211201.9994 | 665.5 | 211201.9994
682 | 211201.9994 | 685 | 211201.9994 | 687.5 | 211201.9994 | 690.5 | 211201.9994 | 693.5 | 211201.9994 | 696 | 211201.9994 | 682 | 211201.9994
699 | 211201.9994 | 701.5 | 211201.9994 | 704.5 | 211201.9994 | 707.5 | 211201.9994 | 710 | 211201.9994 | 713 | 211201.9994 | 699 | 211201.9994
715.5 | 211201.9994 | 718.5 | 211201.9994 | 721.5 | 211201.9994 | 724 | 211201.9994 | 727 | 211201.9994 | 729.5 | 211201.9994 | 715.5 | 211201.9994
732.5 | 211201.9994 | 735.5 | 211201.9994 | 738 | 211201.9994 | 741 | 211201.9994 | 743.5 | 211201.9994 | 746.5 | 211201.9994 | 732.5 | 211201.9994
749.5 | 211201.9994 | 752 | 211201.9994 | 755 | 211201.9994 | 758 | 211201.9994 | 760.5 | 211201.9994 | 763.5 | 211201.9994 | 749.5 | 211201.9994
766 | 211201.9994 | 769 | 211201.9994 | 771.5 | 211201.9994 | 774.5 | 211201.9994 | 777.5 | 211201.9994 | 780 | 211201.9994 | 766 | 211201.9994
783 | 211201.9994 | 785.5 | 211201.9994 | 788.5 | 211201.9994 | 791.5 | 211201.9994 | 794 | 211201.9994 | 797 | 211201.9994 | 783 | 211201.9994
799.5 | 211201.9994 | 802.5 | 211201.9994 | 805.5 | 211201.9994 | 808 | 211201.9994 | 811 | 211201.9994 | 813.5 | 211201.9994 | 799.5 | 211201.9994
816.5 | 211201.9994 | 819.5 | 211201.9994 | 822 | 211201.9994 | 825 | 211201.9994 | 827.5 | 211201.9994 | 830.5 | 211201.9994 | 816.5 | 211201.9994
833.5 | 211201.9994 | 836 | 211201.9994 | 839 | 211201.9994 | 841.5 | 211201.9994 | 844.5 | 211201.9994 | 847.5 | 211201.9994 | 833.5 | 211201.9994
850 | 211201.9994 | 853 | 211201.9994 | 855.5 | 211201.9994 | 858.5 | 211201.9994 | 861.5 | 211201.9994 | 864 | 211201.9994 | 850 | 211201.9994
867 | 211201.9994 | 869.5 | 211201.9994 | 872.5 | 211201.9994 | 875.5 | 211201.9994 | 878 | 211201.9994 | 881 | 211201.9994 | 867 | 211201.9994
883.5 | 211201.9994 | 886.5 | 211201.9994 | 889.5 | 211201.9994 | 892 | 211201.9994 | 895 | 211201.9994 | 897.5 | 211201.9994 | 883.5 | 211201.9994
900.5 | 211201.9994 | 903.5 | 211201.9994 | 906 | 211201.9994 | 909 | 211201.9994 | 911.5 | 211201.9994 | 914.5 | 211201.9994 | 900.5 | 211201.9994
917.5 | 211201.9994 | 920 | 211201.9994 | 923 | 211201.9994 | 925.5 | 211201.9994 | 928.5 | 211201.9994 | 931.5 | 211201.9994 | 917.5 | 211201.9994
934 | 211201.9994 | 937 | 211201.9994 | 939.5 | 211201.9994 | 942.5 | 211201.9994 | 945.5 | 211201.9994 | 948 | 211201.9994 | 934 | 211201.9994
951 | 211201.9994 | 953.5 | 211201.9994 | 956.5 | 211201.9994 | 959.5 | 211201.9994 | 962 | 211201.9994 | 965 | 211201.9994 | 951 | 211201.9994
967.5 | 211201.9994 | 970.5 | 422503.9997 | 973.5 | 211201.9994 | 976 | 211201.9994 | 979 | 211201.9994 | 981.5 | 211201.9994 | 967.5 | 211201.9994
984.5 | 211201.9994 | 987.5 | 211201.9994 | 990 | 211201.9994 | 993 | 211201.9994 | 995.5 | 211201.9994 | 998.5 | 211201.9994 | 984.5 | 211201.9994
1001.5 | 211201.9994 | 1004 | 211201.9994 | 1007 | 211201.9994 | 1009.5 | 422503.9997 | 1012.5 | 211201.9994 | 1015.5 | 211201.9994 | 1001.5 | 211201.9994
1018 | 211201.9994 | 1021 | 211201.9994 | 1023.5 | 211201.9994 | 1026.5 | 211201.9994 | 1029.5 | 211201.9994 | 1032 | 211201.9994 | 1018 | 211201.9994
1035 | 211201.9994 | 1037.5 | 211201.9994 | 1040.5 | 211201.9994 | 1043.5 | 211201.9994 | 1046 | 211201.9994 | 1049 | 211201.9994 | 1035 | 211201.9994
1051.5 | 211201.9994 | 1054.5 | 211201.9994 | 1057.5 | 211201.9994 | 1060 | 211201.9994 | 1063 | 211201.9994 | 1065.5 | 422503.9997 | 1051.5 | 211201.9994
1068.5 | 211201.9994 | 1071.5 | 211201.9994 | 1074 | 211201.9994 | 1077 | 211201.9994 | 1079.5 | 211201.9994 | 1082.5 | 211201.9994 | 1068.5 | 211201.9994
1085.5 | 211201.9994 | 1088 | 211201.9994 | 1091 | 211201.9994 | 1093.5 | 211201.9994 | 1096.5 | 211201.9994 | 1099 | 211201.9994 | 1085.5 | 211201.9994
1102 | 211201.9994 | 1104.5 | 211201.9994 | 1107.5 | 211201.9994 | 1110.5 | 211201.9994 | 1113.5 | 211201.9994 | 1116 | 211201.9994 | 1102 | 211201.9994
1119 | 211201.9994 | 1121.5 | 211201.9994 | 1124.5 | 211201.9994 | 1127.5 | 211201.9994 | 1130 | 211201.9994 | 1133 | 211201.9994 | 1119 | 211201.9994
1135.5 | 211201.9994 | 1138.5 | 211201.9994 | 1141.5 | 211201.9994 | 1144 | 211201.9994 | 1147 | 211201.9994 | 1149.5 | 211201.9994 | 1135.5 | 211201.9994
1152.5 | 211201.9994 | 1155.5 | 211201.9994 | 1158 | 211201.9994 | 1161 | 211201.9994 | 1163.5 | 211201.9994 | 1166.5 | 211201.9994 | 1152.5 | 211201.9994
1169.5 | 211201.9994 | 1172 | 211201.9994 | 1175 | 211201.9994 | 1178 | 211201.9994 | 1180.5 | 211201.9994 | 1183.5 | 211201.9994 | 1169.5 | 211201.9994
1186 | 211201.9994 | 1189 | 211201.9994 | 1191.5 | 211201.9994 | 1194.5 | 211201.9994 | 1197.5 | 211201.9994 | 1200 | 211201.9994 | 1186 | 211201.9994
1202.5 | 211201.9994 | 1205.5 | 211201.9994 | 1208.5 | 211201.9994 | 1211 | 211201.9994 | 1214 | 211201.9994 | 1216.5 | 211201.9994 | 1202.5 | 211201.9994
1219.5 | 211201.9994 | 1222.5 | 211201.9994 | 1225.5 | 211201.9994 | 1228 | 211201.9994 | 1230.5 | 211201.9994 | 1233.5 | 211201.9994 | 1219.5 | 211201.9994
1236.5 | 211201.9994 | 1239.5 | 211201.9994 | 1242 | 211201.9994 | 1245 | 211201.9994 | 1247.5 | 211201.9994 | 1250.5 | 211201.9994 | 1236.5 | 211201.9994
1253.5 | 211201.9994 | 1256 | 211201.9994 | 1259 | 211201.9994 | 1261.5 | 211201.9994 | 1264.5 | 211201.9994 | 1267 | 211201.9994 | 1253.5 | 211201.9994
1270 | 211201.9994 | 1272.5 | 211201.9994 | 1275.5 | 211201.9994 | 1278.5 | 211201.9994 | 1281 | 211201.9994 | 1284 | 211201.9994 | 1270 | 211201.9994
1287 | 211201.9994 | 1289.5 | 211201.9994 | 1292.5 | 211201.9994 | 1295.5 | 211201.9994 | 1298 | 211201.9994 | 1301 | 211201.9994 | 1287 | 211201.9994
1303.5 | 211201.9994 | 1306.5 | 211201.9994 | 1309.5 | 211201.9994 | 1312 | 422503.9997 | 1315 | 211201.9994 | 1317.5 | 211201.9994 | 1303.5 | 211201.9994
1320.5 | 211201.9994 | 1323.5 | 211201.9994 | 1326 | 211201.9994 | 1329 | 211201.9994 | 1331.5 | 211201.9994 | 1334.5 | 211201.9994 | 1320.5 | 211201.9994
1337.5 | 211201.9994 | 1340 | 211201.9994 | 1343 | 211201.9994 | 1345.5 | 422503.9997 | 1348.5 | 211201.9994 | 1351.5 | 211201.9994 | 1337.5 | 211201.9994
1354 | 211201.9994 | 1356.5 | 211201.9994 | 1359.5 | 211201.9994 | 1362.5 | 211201.9994 | 1365 | 211201.9994 | 1368 | 211201.9994 | 1354 | 211201.9994
1371 | 211201.9994 | 1373.5 | 211201.9994 | 1376.5 | 211201.9994 | 1379.5 | 211201.9994 | 1382 | 211201.9994 | 1384.5 | 211201.9994 | 1371 | 211201.9994
1387.5 | 211201.9994 | 1390.5 | 211201.9994 | 1393.5 | 211201.9994 | 1396 | 211201.9994 | 1399 | 211201.9994 | 1401.5 | 211201.9994 | 1387.5 | 211201.9994
1404.5 | 211201.9994 | 1407.5 | 211201.9994 | 1410 | 211201.9994 | 1413 | 211201.9994 | 1415.5 | 211201.9994 | 1418.5 | 211201.9994 | 1404.5 | 211201.9994
1421 | 211201.9994 | 1424 | 211201.9994 | 1426.5 | 211201.9994 | 1429.5 | 211201.9994 | 1432.5 | 211201.9994 | 1435 | 211201.9994 | 1421 | 211201.9994
1438 | 211201.9994 | 1440.5 | 211201.9994 | 1443.5 | 211201.9994 | 1446.5 | 211201.9994 | 1449 | 211201.9994 | 1452 | 211201.9994 | 1438 | 211201.9994
1455 | 211201.9994 | 1457.5 | 211201.9994 | 1460.5 | 211201.9994 | 1463.5 | 211201.9994 | 1466 | 211201.9994 | 1468.5 | 211201.9994 | 1455 | 211201.9994
1471.5 | 211201.9994 | 1474.5 | 211201.9994 | 1477 | 211201.9994 | 1480 | 211201.9994 | 1483 | 211201.9994 | 1485.5 | 211201.9994 | 1471.5 | 211201.9994
1488.5 | 211201.9994 | 1491 | 211201.9994 | 1494 | 211201.9994 | 1497 | 211201.9994 | 1499.5 | 211201.9994 | 1502.5 | 422503.9997 | 1488.5 | 211201.9994
1505.5 | 211201.9994 | 1508 | 211201.9994 | 1511 | 211201.9994 | 1513.5 | 211201.9994 | 1516.5 | 211201.9994 | 1519.5 | 211201.9994 | 1505.5 | 211201.9994
1522 | 211201.9994 | 1524.5 | 422503.9997 | 1527.5 | 211201.9994 | 1530.5 | 211201.9994 | 1533 | 211201.9994 | 1536 | 211201.9994 | 1522 | 211201.9994
1539 | 211201.9994 | 1541.5 | 211201.9994 | 1544.5 | 211201.9994 | 1547.5 | 211201.9994 | 1550 | 211201.9994 | 1552.5 | 211201.9994 | 1539 | 211201.9994
1555.5 | 211201.9994 | 1558.5 | 211201.9994 | 1561 | 211201.9994 | 1564 | 211201.9994 | 1566.5 | 211201.9994 | 1569.5 | 211201.9994 | 1555.5 | 211201.9994
1572.5 | 211201.9994 | 1575.5 | 211201.9994 | 1578 | 211201.9994 | 1580.5 | 211201.9994 | 1583.5 | 422503.9997 | 1586.5 | 211201.9994 | 1572.5 | 211201.9994
1589 | 211201.9994 | 1592 | 211201.9994 | 1594.5 | 211201.9994 | 1597.5 | 211201.9994 | 1600.5 | 211201.9994 | 1603.5 | 211201.9994 | 1589 | 211201.9994
1606 | 211201.9994 | 1608.5 | 211201.9994 | 1611.5 | 211201.9994 | 1614.5 | 211201.9994 | 1617 | 422503.9997 | 1620 | 211201.9994 | 1606 | 211201.9994
1622.5 | 211201.9994 | 1625.5 | 211201.9994 | 1628.5 | 211201.9994 | 1631 | 211201.9994 | 1634 | 211201.9994 | 1636.5 | 211201.9994 | 1622.5 | 211201.9994
1639.5 | 211201.9994 | 1642.5 | 211201.9994 | 1645 | 211201.9994 | 1648 | 211201.9994 | 1651 | 211201.9994 | 1653.5 | 211201.9994 | 1639.5 | 211201.9994
1656 | 211201.9994 | 1659 | 211201.9994 | 1662 | 211201.9994 | 1664.5 | 211201.9994 | 1667.5 | 211201.9994 | 1670.5 | 211201.9994 | 1656 | 211201.9994
1673.5 | 211201.9994 | 1676 | 211201.9994 | 1678.5 | 211201.9994 | 1681.5 | 211201.9994 | 1684.5 | 211201.9994 | 1687 | 422503.9997 | 1673.5 | 211201.9994
1690 | 211201.9994 | 1692.5 | 422503.9997 | 1695.5 | 211201.9994 | 1698.5 | 211201.9994 | 1701 | 211201.9994 | 1704 | 211201.9994 | 1690 | 211201.9994
1706.5 | 211201.9994 | 1709.5 | 211201.9994 | 1712.5 | 211201.9994 | 1715 | 211201.9994 | 1718 | 211201.9994 | 1720.5 | 211201.9994 | 1706.5 | 211201.9994
1723.5 | 211201.9994 | 1726.5 | 211201.9994 | 1729 | 211201.9994 | 1732 | 211201.9994 | 1734.5 | 211201.9994 | 1737.5 | 211201.9994 | 1723.5 | 211201.9994
1740.5 | 211201.9994 | 1743 | 211201.9994 | 1746 | 211201.9994 | 1748.5 | 211201.9994 | 1751.5 | 211201.9994 | 1754.5 | 422503.9997 | 1740.5 | 211201.9994
1757 | 211201.9994 | 1760 | 211201.9994 | 1762.5 | 211201.9994 | 1765.5 | 211201.9994 | 1768.5 | 211201.9994 | 1771 | 211201.9994 | 1757 | 211201.9994
1774 | 211201.9994 | 1776.5 | 211201.9994 | 1779.5 | 211201.9994 | 1782.5 | 211201.9994 | 1785 | 211201.9994 | 1788 | 211201.9994 | 1774 | 211201.9994
1790.5 | 211201.9994 | 1793.5 | 211201.9994 | 1796.5 | 422503.9997 | 1799 | 211201.9994 | 1802 | 211201.9994 | 1804.5 | 211201.9994 | 1790.5 | 211201.9994
1807.5 | 211201.9994 | 1810.5 | 211201.9994 | 1813 | 211201.9994 | 1816 | 211201.9994 | 1818.5 | 211201.9994 | 1821.5 | 211201.9994 | 1807.5 | 211201.9994
1824.5 | 211201.9994 | 1827 | 211201.9994 | 1830 | 211201.9994 | 1832.5 | 211201.9994 | 1835.5 | 211201.9994 | 1838.5 | 211201.9994 | 1824.5 | 211201.9994
1841 | 211201.9994 | 1844 | 211201.9994 | 1846.5 | 211201.9994 | 1849.5 | 211201.9994 | 1852.5 | 211201.9994 | 1855 | 211201.9994 | 1841 | 211201.9994
1858 | 211201.9994 | 1860.5 | 211201.9994 | 1863.5 | 211201.9994 | 1866.5 | 211201.9994 | 1869 | 211201.9994 | 1872 | 211201.9994 | 1858 | 211201.9994
1874.5 | 211201.9994 | 1877.5 | 211201.9994 | 1880.5 | 211201.9994 | 1883 | 211201.9994 | 1886 | 211201.9994 | 1888.5 | 211201.9994 | 1874.5 | 211201.9994
1891.5 | 211201.9994 | 1894.5 | 211201.9994 | 1897 | 211201.9994 | 1900 | 211201.9994 | 1902.5 | 211201.9994 | 1905.5 | 211201.9994 | 1891.5 | 211201.9994
1908.5 | 211201.9994 | 1911 | 211201.9994 | 1914 | 211201.9994 | 1916.5 | 211201.9994 | 1919.5 | 211201.9994 | 1922.5 | 211201.9994 | 1908.5 | 211201.9994
1925 | 211201.9994 | 1928 | 211201.9994 | 1930.5 | 211201.9994 | 1933.5 | 211201.9994 | 1936.5 | 211201.9994 | 1939 | 211201.9994 | 1925 | 211201.9994
1942 | 211201.9994 | 1944.5 | 211201.9994 | 1947.5 | 211201.9994 | 1950.5 | 211201.9994 | 1953 | 211201.9994 | 1956 | 211201.9994 | 1942 | 211201.9994
1958.5 | 211201.9994 | 1961.5 | 211201.9994 | 1964.5 | 211201.9994 | 1967 | 211201.9994 | 1970 | 211201.9994 | 1972.5 | 211201.9994 | 1958.5 | 211201.9994
1975.5 | 211201.9994 | 1978.5 | 211201.9994 | 1981 | 211201.9994 | 1984 | 211201.9994 | 1986.5 | 422503.9997 | 1989.5 | 211201.9994 | 1975.5 | 211201.9994
1992.5 | 211201.9994 | 1995 | 211201.9994 | 1998 | 211201.9994 | 2000.5 | 211201.9994 | 2003.5 | 211201.9994 | 2006.5 | 211201.9994 | 1992.5 | 211201.9994
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Average Conductor to Ground Resistances
Open Burn Test 4 |  |  | 2006-10-30 | 10:40
XLPE | 3-C | Tray G
0 | 250 kW
Burner Time | C1-G |  | Burner Time | C2-G | Burner Time | C3-G | Burner Time | C4-G | Burner Time | Minimums
-272.5 | 211202 |  | -268.8333 | 211202 | -267 | 211202 | -265 | 211202 | -272.5 | 211202
-255.6667 | 211202 |  | -252 | 211202 | -250 | 211202 | -248.3333 | 211202 | -255.6667 | 211202
-238.8333 | 211202 |  | -235.1667 | 211202 | -233.3333 | 211202 | -231.3333 | 211202 | -238.8333 | 211202
-222.1667 | 211202 |  | -218.3333 | 211202 | -216.5 | 211202 | -214.6667 | 211202 | -222.1667 | 211202
-205.3333 | 211202 |  | -201.5 | 211202 | -199.6667 | 211202 | -197.8333 | 211202 | -205.3333 | 211202
-188.5 | 211202 |  | -184.8333 | 211202 | -183 | 211202 | -181 | 211202 | -188.5 | 211202
-171.8333 | 211202 |  | -168.1667 | 211202 | -166.3333 | 211202 | -164.3333 | 211202 | -171.8333 | 211202
-155 | 422504 |  | -151.3333 | 211202 | -149.5 | 211202 | -147.5 | 211202 | -155 | 211202
-138.1667 | 211202 |  | -134.3333 | 211202 | -132.5 | 211202 | -130.6667 | 211202 | -138.1667 | 211202
-121.3333 | 211202 |  | -117.5 | 211202 | -115.6667 | 211202 | -113.8333 | 211202 | -121.3333 | 211202
-104.6667 | 211202 |  | -101 | 211202 | -99 | 211202 | -97.3333 | 211202 | -104.6667 | 211202
-87.6667 | 211202 |  | -84 | 211202 | -82 | 211202 | -80.3333 | 211202 | -87.6667 | 211202
-71 | 211202 |  | -67.1667 | 211202 | -65.3333 | 211202 | -63.5 | 211202 | -71 | 211202
-54.1667 | 211202 |  | -50.5 | 211202 | -48.5 | 211202 | -46.8333 | 211202 | -54.1667 | 211202
-37.5 | 211202 |  | -33.6667 | 211202 | -31.6667 | 211202 | -29.8333 | 211202 | -37.5 | 211202
-20.5 | 211202 |  | -17 | 211202 | -15 | 211202 | -13.1667 | 211202 | -20.5 | 211202
-3.6667 | 211202 |  | -2.2352e-08 | 211202 | 2 | 211202 | 3.6667 | 211202 | -3.6667 | 211202
13.1667 | 211202 |  | 16.8333 | 211202 | 18.6667 | 211202 | 20.6667 | 211202 | 13.1667 | 211202
29.8333 | 211202 |  | 33.6667 | 211202 | 35.5 | 211202 | 37.3333 | 105551 | 29.8333 | 105551
46.6667 | 211202 |  | 50.3333 | 211202 | 52 | 211202 | 54 | 211202 | 46.6667 | 211202
63.3333 | 211202 |  | 67 | 211202 | 69 | 211202 | 70.6667 | 211202 | 63.3333 | 211202
80.1667 | 211202 |  | 83.8333 | 211202 | 85.6667 | 211202 | 87.6667 | 211202 | 80.1667 | 211202
97 | 211202 |  | 100.8333 | 211202 | 102.5 | 211202 | 104.3333 | 211202 | 97 | 211202
113.8333 | 211202 |  | 117.5 | 211202 | 119.5 | 211202 | 121.1667 | 211202 | 113.8333 | 211202
130.5 | 211202 |  | 134.3333 | 211202 | 136.3333 | 211202 | 138.1667 | 211202 | 130.5 | 211202
147.3333 | 211202 |  | 151 | 211202 | 153 | 211202 | 154.6667 | 211202 | 147.3333 | 211202
164.1667 | 211202 |  | 167.8333 | 211202 | 169.6667 | 211202 | 171.6667 | 211202 | 164.1667 | 211202
181.1667 | 211202 |  | 184.8333 | 211202 | 186.6667 | 211202 | 188.6667 | 211202 | 181.1667 | 211202
197.6667 | 211202 |  | 201.5 | 211202 | 203.3333 | 211202 | 205.1667 | 211202 | 197.6667 | 211202
214.5 | 211202 |  | 218.1667 | 211202 | 220 | 211202 | 222 | 211202 | 214.5 | 211202
231.3333 | 211202 |  | 235.1667 | 211202 | 237 | 211202 | 238.8333 | 211202 | 231.3333 | 211202
248.3333 | 211202 |  | 252 | 211202 | 254 | 211202 | 255.6667 | 211202 | 248.3333 | 211202
264.8333 | 211202 |  | 268.6667 | 211202 | 270.5 | 211202 | 272.3333 | 211202 | 264.8333 | 211202
281.6667 | 211202 |  | 285.5 | 211202 | 287.3333 | 211202 | 289.1667 | 211202 | 281.6667 | 211202
298.5 | 211202 |  | 302.1667 | 211202 | 304 | 211202 | 306 | 211202 | 298.5 | 211202
315.5 | 211202 |  | 319 | 211202 | 321 | 211202 | 322.8333 | 211202 | 315.5 | 211202
332.1667 | 211202 |  | 336 | 211202 | 337.8333 | 211202 | 339.6667 | 211202 | 332.1667 | 211202
348.8333 | 211202 |  | 352.6667 | 211202 | 354.5 | 211202 | 356.3333 | 211202 | 348.8333 | 211202
365.6667 | 211202 |  | 369.5 | 211202 | 371.3333 | 211202 | 373.1667 | 211202 | 365.6667 | 211202
382.5 | 211202 |  | 386.3333 | 211202 | 388.3333 | 211202 | 390.1667 | 211202 | 382.5 | 211202
399.5 | 211202 |  | 403 | 211202 | 405 | 211202 | 406.8333 | 211202 | 399.5 | 211202
416.1667 | 211202 |  | 419.8333 | 211202 | 421.6667 | 211202 | 423.6667 | 211202 | 416.1667 | 211202
432.8333 | 211202 |  | 436.6667 | 211202 | 438.5 | 211202 | 440.3333 | 211202 | 432.8333 | 211202
449.6667 | 211202 |  | 453.5 | 211202 | 455.3333 | 211202 | 457.1667 | 211202 | 449.6667 | 211202
466.5 | 211202 |  | 470.1667 | 211202 | 472 | 211202 | 474 | 211202 | 466.5 | 211202
483.3333 | 211202 |  | 487 | 211202 | 489 | 211202 | 490.6667 | 211202 | 483.3333 | 211202
500.1667 | 211202 |  | 504 | 211202 | 505.8333 | 211202 | 507.6667 | 211202 | 500.1667 | 211202
516.8333 | 211202 |  | 520.6667 | 211202 | 522.5 | 211202 | 524.3333 | 211202 | 516.8333 | 211202
533.6667 | 211202 |  | 537.5 | 211202 | 539.3333 | 211202 | 541.1667 | 211202 | 533.6667 | 211202
550.5 | 211202 |  | 554.1667 | 211202 | 556 | 211202 | 558 | 211202 | 550.5 | 211202
567.3333 | 211202 |  | 571 | 211202 | 573 | 211202 | 574.6667 | 211202 | 567.3333 | 211202
584.1667 | 211202 |  | 587.8333 | 211202 | 589.6667 | 211202 | 591.6667 | 211202 | 584.1667 | 211202
600.8333 | 211202 |  | 604.6667 | 211202 | 606.5 | 211202 | 608.3333 | 211202 | 600.8333 | 211202
617.6667 | 211202 |  | 621.5 | 211202 | 623.3333 | 211202 | 625.1667 | 211202 | 617.6667 | 211202
634.5 | 211202 |  | 638.1667 | 211202 | 640 | 211202 | 642 | 211202 | 634.5 | 211202
651.3333 | 211202 |  | 655 | 211202 | 657 | 211202 | 658.6667 | 211202 | 651.3333 | 211202
668.1667 | 211202 |  | 671.8333 | 211202 | 673.6667 | 211202 | 675.6667 | 211202 | 668.1667 | 211202
684.8333 | 211202 |  | 688.6667 | 211202 | 690.5 | 211202 | 692.3333 | 211202 | 684.8333 | 211202
701.6667 | 211202 |  | 705.5 | 211202 | 707.3333 | 211202 | 709.1667 | 211202 | 701.6667 | 211202
718.5 | 211202 |  | 722.1667 | 211202 | 724 | 211202 | 726 | 211202 | 718.5 | 211202
735.3333 | 211202 |  | 739 | 211202 | 741 | 211202 | 742.6667 | 211202 | 735.3333 | 211202
752.1667 | 211202 |  | 756 | 211202 | 757.8333 | 211202 | 759.6667 | 211202 | 752.1667 | 211202
768.8333 | 211202 |  | 772.6667 | 211202 | 774.5 | 211202 | 776.3333 | 211202 | 768.8333 | 211202
785.6667 | 211202 |  | 789.5 | 211202 | 791.3333 | 211202 | 793.1667 | 211202 | 785.6667 | 211202
802.5 | 211202 |  | 806.1667 | 211202 | 808 | 211202 | 810 | 211202 | 802.5 | 211202
819.3333 | 211202 |  | 823 | 211202 | 825 | 211202 | 826.6667 | 211202 | 819.3333 | 211202
836.1667 | 211202 |  | 839.8333 | 211202 | 841.6667 | 211202 | 843.6667 | 211202 | 836.1667 | 211202
852.8333 | 211202 |  | 856.6667 | 211202 | 858.5 | 211202 | 860.3333 | 211202 | 852.8333 | 211202
869.6667 | 211202 |  | 873.5 | 211202 | 875.3333 | 211202 | 877.1667 | 211202 | 869.6667 | 211202
886.5 | 211202 |  | 890.1667 | 211202 | 892 | 211202 | 894 | 211202 | 886.5 | 211202
903.3333 | 211202 |  | 907 | 211202 | 909 | 211202 | 910.6667 | 211202 | 903.3333 | 211202
920.1667 | 211202 |  | 923.8333 | 211202 | 925.6667 | 211202 | 927.6667 | 211202 | 920.1667 | 211202
936.8333 | 211202 |  | 940.6667 | 211202 | 942.5 | 211202 | 944.3333 | 211202 | 936.8333 | 211202
953.6667 | 211202 |  | 957.5 | 211202 | 959.3333 | 211202 | 961.1667 | 211202 | 953.6667 | 211202
970.5 | 211202 |  | 974.1667 | 211202 | 976 | 211202 | 978 | 211202 | 970.5 | 211202
987.3333 | 211202 |  | 991 | 211202 | 993 | 211202 | 994.6667 | 211202 | 987.3333 | 211202
1004.1667 | 211202 |  | 1007.8333 | 211202 | 1009.6667 | 211202 | 1011.6667 | 211202 | 1004.1667 | 211202
1020.8333 | 211202 |  | 1024.6667 | 211202 | 1026.5 | 211202 | 1028.3333 | 211202 | 1020.8333 | 211202
1037.6667 | 211202 |  | 1041.5 | 211202 | 1043.3333 | 211202 | 1045.1667 | 211202 | 1037.6667 | 211202
1054.5 | 211202 |  | 1058.1667 | 211202 | 1060 | 211202 | 1062 | 211202 | 1054.5 | 211202
1071.3333 | 211202 |  | 1075 | 211202 | 1077 | 211202 | 1078.6667 | 211202 | 1071.3333 | 211202
1088.1667 | 211202 |  | 1091.8333 | 211202 | 1093.5 | 211202 | 1095.5 | 211202 | 1088.1667 | 211202
1104.6667 | 211202 |  | 1108.6667 | 211202 | 1110.3333 | 211202 | 1112.3333 | 211202 | 1104.6667 | 211202
1121.6667 | 211202 |  | 1125.5 | 211202 | 1127.3333 | 211202 | 1129.1667 | 211202 | 1121.6667 | 211202
1138.5 | 211202 |  | 1142.1667 | 211202 | 1144 | 211202 | 1146 | 211202 | 1138.5 | 211202
1155.3333 | 211202 |  | 1159 | 211202 | 1161 | 211202 | 1162.6667 | 211202 | 1155.3333 | 211202
1172.1667 | 211202 |  | 1176 | 211202 | 1177.8333 | 211202 | 1179.6667 | 211202 | 1172.1667 | 211202
1188.8333 | 211202 |  | 1192.6667 | 211202 | 1194.5 | 211202 | 1196.3333 | 211202 | 1188.8333 | 211202
1205.5 | 211202 |  | 1209.1667 | 211202 | 1211 | 211202 | 1213 | 211202 | 1205.5 | 211202
1222.5 | 211202 |  | 1226 | 211202 | 1228 | 211202 | 1229.8333 | 211202 | 1222.5 | 211202
1239.3333 | 211202 |  | 1243 | 211202 | 1245 | 211202 | 1246.6667 | 211202 | 1239.3333 | 211202
1256.1667 | 211202 |  | 1259.8333 | 211202 | 1261.5 | 211202 | 1263.5 | 211202 | 1256.1667 | 211202
1272.6667 | 211202 |  | 1276.5 | 211202 | 1278.3333 | 211202 | 1280.1667 | 211202 | 1272.6667 | 211202
1289.6667 | 211202 |  | 1293.5 | 211202 | 1295.3333 | 211202 | 1297.1667 | 211202 | 1289.6667 | 211202
1306.5 | 211202 |  | 1310.1667 | 211202 | 1312 | 211202 | 1314 | 211202 | 1306.5 | 211202
1323.3333 | 211202 |  | 1327 | 211202 | 1329 | 211202 | 1330.6667 | 211202 | 1323.3333 | 211202
1340.1667 | 211202 |  | 1343.8333 | 211202 | 1345.6667 | 211202 | 1347.6667 | 211202 | 1340.1667 | 211202
1356.6667 | 211202 |  | 1360.5 | 211202 | 1362.3333 | 211202 | 1364.1667 | 211202 | 1356.6667 | 211202
1373.6667 | 211202 |  | 1377.5 | 211202 | 1379.1667 | 211202 | 1381 | 211202 | 1373.6667 | 211202
1390.5 | 211202 |  | 1394.1667 | 211202 | 1396 | 211202 | 1398 | 211202 | 1390.5 | 211202
1407.3333 | 211202 |  | 1411 | 211202 | 1413 | 211202 | 1414.6667 | 211202 | 1407.3333 | 211202
1423.8333 | 211202 |  | 1427.6667 | 211202 | 1429.5 | 211202 | 1431.3333 | 211202 | 1423.8333 | 211202
1440.6667 | 211202 |  | 1444.5 | 211202 | 1446.3333 | 211202 | 1448.1667 | 211202 | 1440.6667 | 211202
1457.6667 | 211202 |  | 1461.5 | 211202 | 1463.1667 | 211202 | 1465 | 211202 | 1457.6667 | 211202
1474.3333 | 211202 |  | 1478.1667 | 211202 | 1480 | 211202 | 1481.8333 | 211202 | 1474.3333 | 211202
1491.1667 | 211202 |  | 1495 | 211202 | 1496.8333 | 211202 | 1498.6667 | 211202 | 1491.1667 | 211202
1508.1667 | 211202 |  | 1511.8333 | 211202 | 1513.6667 | 211202 | 1515.6667 | 211202 | 1508.1667 | 211202
1524.6667 | 211202 |  | 1528.5 | 211202 | 1530.3333 | 211202 | 1532.1667 | 211202 | 1524.6667 | 211202
1541.6667 | 211202 |  | 1545.5 | 211202 | 1547.1667 | 211202 | 1549 | 211202 | 1541.6667 | 211202
1558.3333 | 211202 |  | 1562 | 211202 | 1564 | 211202 | 1565.6667 | 211202 | 1558.3333 | 211202
1575.3333 | 211202 |  | 1578.8333 | 211202 | 1580.8333 | 211202 | 1582.6667 | 211202 | 1575.3333 | 211202
1591.8333 | 211202 |  | 1595.6667 | 211202 | 1597.6667 | 211202 | 1599.5 | 211202 | 1591.8333 | 211202
1608.6667 | 211202 |  | 1612.5 | 211202 | 1614.3333 | 105551 | 1616.1667 | 211202 | 1608.6667 | 105551
1625.5 | 211202 |  | 1629.1667 | 211202 | 1631 | 211202 | 1633 | 211202 | 1625.5 | 211202
1642.3333 | 211202 |  | 1646.1667 | 211202 | 1648 | 211202 | 1649.8333 | 211202 | 1642.3333 | 211202
1659 | 211202 |  | 1662.6667 | 211202 | 1664.6667 | 211202 | 1666.6667 | 211202 | 1659 | 211202
1676 | 211202 |  | 1679.8333 | 211202 | 1681.5 | 211202 | 1683.3333 | 211202 | 1676 | 211202
1692.6667 | 211202 |  | 1696.5 | 211202 | 1698.3333 | 211202 | 1700.1667 | 211202 | 1692.6667 | 211202
1709.5 | 211202 |  | 1713.1667 | 211202 | 1715 | 211202 | 1717 | 211202 | 1709.5 | 211202
1726.3333 | 211202 |  | 1730 | 211202 | 1732 | 211202 | 1733.6667 | 211202 | 1726.3333 | 211202
1743.1667 | 211202 |  | 1746.8333 | 211202 | 1748.6667 | 211202 | 1750.6667 | 211202 | 1743.1667 | 211202
1759.8333 | 211202 |  | 1763.6667 | 211202 | 1765.5 | 211202 | 1767.3333 | 211202 | 1759.8333 | 211202
1776.6667 | 211202 |  | 1780.5 | 211202 | 1782.3333 | 211202 | 1784.1667 | 211202 | 1776.6667 | 211202
1793.5 | 211202 |  | 1797.1667 | 211202 | 1799 | 211202 | 1801 | 211202 | 1793.5 | 211202
1810.3333 | 211202 |  | 1814 | 211202 | 1816 | 211202 | 1817.6667 | 211202 | 1810.3333 | 211202
1827.1667 | 211202 |  | 1830.8333 | 211202 | 1832.6667 | 211202 | 1834.6667 | 211202 | 1827.1667 | 211202
1843.8333 | 211202 |  | 1847.6667 | 211202 | 1849.5 | 211202 | 1851.3333 | 211202 | 1843.8333 | 211202
1860.6667 | 211202 |  | 1864.5 | 211202 | 1866.3333 | 211202 | 1868.1667 | 211202 | 1860.6667 | 211202
1877.5 | 211202 |  | 1881.1667 | 211202 | 1883 | 211202 | 1885 | 211202 | 1877.5 | 211202
1894.3333 | 211202 |  | 1898 | 211202 | 1900 | 211202 | 1901.6667 | 211202 | 1894.3333 | 211202
1911.1667 | 211202 |  | 1914.8333 | 211202 | 1916.6667 | 211202 | 1918.6667 | 211202 | 1911.1667 | 211202
1927.8333 | 211202 |  | 1931.6667 | 211202 | 1933.5 | 211202 | 1935.3333 | 211202 | 1927.8333 | 211202
1944.6667 | 211202 |  | 1948.5 | 211202 | 1950.3333 | 211202 | 1952.1667 | 211202 | 1944.6667 | 211202
1961.5 | 211202 |  | 1965.1667 | 211202 | 1967 | 211202 | 1969 | 211202 | 1961.5 | 211202
1978.3333 | 211202 |  | 1982 | 211202 | 1984 | 211202 | 1985.6667 | 211202 | 1978.3333 | 211202
1995.1667 | 211202 |  | 1998.8333 | 211202 | 2000.6667 | 211202 | 2002.6667 | 211202 | 1995.1667 | 211202

## C3-4
Open Burn Test 4 |  |  | 2006-10-30 | 10:40 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray G
0 | 250 kW |  | Bundle | 3 & 4
Time-11 | N11 | N12 | Time-12 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39020.4397 | 1 | 0 | 39020.4397 | 1 | 0 | -261.5 | 14.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4399 | 0 | 0 | 39020.4399 | 0 | 0 | -244.5 | 31.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 422504 | 422504 | 422503.9997
39020.4401 | 1 | 0 | 39020.4401 | 1 | 0 | -227.5 | 48.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4402 | 1 | 0 | 39020.4403 | 1 | 0 | -211 | 65 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4404 | 1 | 0 | 39020.4405 | 1 | 0 | -194 | 82 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4406 | 1 | 0 | 39020.4406 | 1 | 0 | -177.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4408 | 1 | 0 | 39020.4408 | 1 | 0 | -160.5 | 115.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.441 | 0 | 0 |  | 1 | 0 | -144 | 132 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4412 | 1 | 0 | 39020.4412 | 0 | 0 | -127 | 149 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4414 | 1 | 0 | 39020.4414 | 0 | 0 | -110 | 166 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4416 | 1 | 0 | 39020.4416 | 1 | 0 | -93.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4418 | 1 | 0 | 39020.4418 | 1 | 0 | -76.5 | 199.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.442 | 1 | 0 | 39020.442 | 1 | 0 | -59.5 | 216.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4422 | 1 | 0 | 39020.4422 | 1 | 0 | -43 | 233 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4424 | 1 | 0 | 39020.4424 | 0 | 0 | -26 | 250 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4426 | 1 | 0 | 39020.4426 | 1 | 0 | -9.5 | 266.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4428 | 1 | 0 | 39020.4428 | 1 | 0 | 7.5 | 283.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.443 | 1 | 0 | 39020.443 | 1 | 0 | 24.5 | 300.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4432 | 1 | 0 | 39020.4432 | 2 | 0 | 41 | 317 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
39020.4434 | 1 | 0 | 39020.4434 | 1 | 0 | 57.5 | 333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4436 | 1 | 0 | 39020.4436 | 1 | 0 | 74.5 | 350.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4437 | 1 | 0 | 39020.4438 | 1 | 0 | 91.5 | 367.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4439 | 1 | 0 | 39020.444 | 0 | 0 | 108 | 384 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4441 | 1 | 0 | 39020.4442 | 1 | 0 | 125 | 401 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4443 | 0 | 0 | 39020.4444 | 1 | 0 | 142 | 418 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4445 | 1 | 0 | 39020.4445 | 0 | 0 | 158.5 | 434.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4447 | 1 | 0 | 39020.4447 | 1 | 0 | 175.5 | 451.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4449 | 1 | 0 | 39020.4449 | 1 | 0 | 192.5 | 468.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4451 | 0 | 0 | 39020.4451 | 1 | 0 | 209 | 485 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4453 | 1 | 0 | 39020.4453 | 1 | 0 | 225.5 | 501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4455 | 1 | 0 | 39020.4455 | 1 | 0 | 242.5 | 518.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4457 | 1 | 0 | 39020.4457 | 0 | 0 | 259.5 | 535.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4459 | 1 | 0 | 39020.4459 | 1 | 0 | 276 | 552 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4461 | 1 | 0 | 39020.4461 | 1 | 0 | 293 | 569 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4463 | 1 | 0 | 39020.4463 | 1 | 0 | 309.5 | 585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4465 | 1 | 0 | 39020.4465 | 1 | 0 | 326.5 | 602.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4467 | 1 | 0 | 39020.4467 | 1 | 0 | 343.5 | 619.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4469 | 1 | 0 | 39020.4469 | 1 | 0 | 360 | 636 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.447 | 1 | 0 | 39020.4471 | 1 | 0 | 377 | 653 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4472 | 1 | 0 | 39020.4473 | 1 | 0 | 394 | 670 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4474 | 1 | 0 | 39020.4475 | 0 | 0 | 410.5 | 686.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4476 | 1 | 0 | 39020.4477 | 1 | 0 | 427.5 | 703.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4478 | 1 | 0 | 39020.4478 | 0 | 0 | 444 | 720 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.448 | 1 | 0 | 39020.448 | 1 | 0 | 461 | 737 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4482 | 1 | 0 | 39020.4482 | 1 | 0 | 477.5 | 753.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4484 | 0 | 0 | 39020.4484 | 1 | 0 | 494.5 | 770.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4486 | 1 | 0 | 39020.4486 | 1 | 0 | 511.5 | 787.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4488 | 1 | 0 | 39020.4488 | 1 | 0 | 528 | 804 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.449 | 1 | 0 | 39020.449 | 1 | 0 | 545 | 821 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4492 | 1 | 0 | 39020.4492 | 1 | 0 | 561.5 | 837.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4494 | 1 | 0 | 39020.4494 | 1 | 0 | 578.5 | 854.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4496 | 1 | 0 | 39020.4496 | 1 | 0 | 595.5 | 871.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4498 | 1 | 0 | 39020.4498 | 1 | 0 | 612 | 888 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.45 | 1 | 0 | 39020.45 | 1 | 0 | 629 | 905 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4502 | 1 | 0 | 39020.4502 | 1 | 0 | 645.5 | 921.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4504 | 1 | 0 | 39020.4504 | 1 | 0 | 662.5 | 938.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4506 | 1 | 0 | 39020.4506 | 1 | 0 | 679.5 | 955.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4507 | 1 | 0 | 39020.4508 | 1 | 0 | 696 | 972 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4509 | 1 | 0 | 39020.451 | 0 | 0 | 713 | 989 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4511 | 1 | 0 | 39020.4511 | 1 | 0 | 729.5 | 1005.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4513 | 1 | 0 | 39020.4513 | 1 | 0 | 746.5 | 1022.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4515 | 1 | 0 | 39020.4515 | 1 | 0 | 763.5 | 1039.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4517 | 1 | 0 | 39020.4517 | 1 | 0 | 780 | 1056 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4519 | 1 | 0 | 39020.4519 | 1 | 0 | 797 | 1073 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4521 | 1 | 0 | 39020.4521 | 1 | 0 | 813.5 | 1089.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4523 | 1 | 0 | 39020.4523 | 1 | 0 | 830.5 | 1106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4525 | 1 | 0 | 39020.4525 | 1 | 0 | 847.5 | 1123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4527 | 1 | 0 | 39020.4527 | 0 | 0 | 864 | 1140 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4529 | 1 | 0 | 39020.4529 | 1 | 0 | 881 | 1157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4531 | 1 | 0 | 39020.4531 | 1 | 0 | 897.5 | 1173.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4533 | 1 | 0 | 39020.4533 | 1 | 0 | 914.5 | 1190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4535 | 1 | 0 | 39020.4535 | 1 | 0 | 931.5 | 1207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4537 | 1 | 0 | 39020.4537 | 1 | 0 | 948 | 1224 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4539 | 1 | 0 | 39020.4539 | 1 | 0 | 965 | 1241 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4541 | 1 | 0 | 39020.4541 | 1 | 0 | 981.5 | 1257.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4542 | 1 | 0 | 39020.4543 | 1 | 0 | 998.5 | 1274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4544 | 1 | 0 | 39020.4545 | 0 | 0 | 1015.5 | 1291.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4546 | 1 | 0 | 39020.4547 | 1 | 0 | 1032 | 1308 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4548 | 1 | 0 | 39020.4548 | 1 | 0 | 1049 | 1325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.455 | 0 | 0 | 39020.455 | 1 | 0 | 1065.5 | 1341.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4552 | 1 | 0 | 39020.4552 | 1 | 0 | 1082.5 | 1358.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4554 | 1 | 0 | 39020.4554 | 1 | 0 | 1099 | 1375 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4556 | 1 | 0 | 39020.4556 | 1 | 0 | 1116 | 1392 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4558 | 1 | 0 | 39020.4558 | 1 | 0 | 1133 | 1409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.456 | 1 | 0 | 39020.456 | 1 | 0 | 1149.5 | 1425.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4562 | 1 | 0 | 39020.4562 | 1 | 0 | 1166.5 | 1442.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4564 | 1 | 0 | 39020.4564 | 1 | 0 | 1183.5 | 1459.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4566 | 1 | 0 | 39020.4566 | 1 | 0 | 1200 | 1476 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4568 | 1 | 0 | 39020.4568 | 0 | 0 | 1216.5 | 1492.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.457 | 1 | 0 | 39020.457 | 1 | 0 | 1233.5 | 1509.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4572 | 1 | 0 | 39020.4572 | 1 | 0 | 1250.5 | 1526.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4573 | 1 | 0 | 39020.4574 | 1 | 0 | 1267 | 1543 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4575 | 1 | 0 | 39020.4576 | 1 | 0 | 1284 | 1560 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4577 | 1 | 0 | 39020.4578 | 0 | 0 | 1301 | 1577 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4579 | 1 | 0 | 39020.458 | 1 | 0 | 1317.5 | 1593.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4581 | 1 | 0 | 39020.4581 | 1 | 0 | 1334.5 | 1610.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4583 | 1 | 0 | 39020.4583 | 1 | 0 | 1351.5 | 1627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4585 | 1 | 0 | 39020.4585 | 1 | 0 | 1368 | 1644 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4587 | 1 | 0 | 39020.4587 | 1 | 0 | 1384.5 | 1660.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4589 | 1 | 0 | 39020.4589 | 1 | 0 | 1401.5 | 1677.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4591 | 1 | 0 | 39020.4591 | 1 | 0 | 1418.5 | 1694.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4593 | 1 | 0 | 39020.4593 | 1 | 0 | 1435 | 1711 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4595 | 1 | 0 | 39020.4595 | 1 | 0 | 1452 | 1728 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4597 | 1 | 0 | 39020.4597 | 1 | 0 | 1468.5 | 1744.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4599 | 1 | 0 | 39020.4599 | 1 | 0 | 1485.5 | 1761.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4601 | 0 | 0 | 39020.4601 | 1 | 0 | 1502.5 | 1778.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4603 | 1 | 0 | 39020.4603 | 1 | 0 | 1519.5 | 1795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4605 | 1 | 0 | 39020.4605 | 1 | 0 | 1536 | 1812 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4607 | 1 | 0 | 39020.4607 | 1 | 0 | 1552.5 | 1828.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4609 | 1 | 0 | 39020.4609 | 1 | 0 | 1569.5 | 1845.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4611 | 1 | 0 | 39020.4611 | 1 | 0 | 1586.5 | 1862.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4613 | 1 | 0 | 39020.4613 | 1 | 0 | 1603.5 | 1879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4614 | 1 | 0 | 39020.4615 | 1 | 0 | 1620 | 1896 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4616 | 1 | 0 | 39020.4616 | 1 | 0 | 1636.5 | 1912.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4618 | 1 | 0 | 39020.4618 | 1 | 0 | 1653.5 | 1929.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.462 | 1 | 0 | 39020.462 | 1 | 0 | 1670.5 | 1946.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4622 | 0 | 0 | 39020.4622 | 1 | 0 | 1687 | 1963 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4624 | 1 | 0 | 39020.4624 | 1 | 0 | 1704 | 1980 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4626 | 1 | 0 | 39020.4626 | 1 | 0 | 1720.5 | 1996.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4628 | 1 | 0 | 39020.4628 | 1 | 0 | 1737.5 | 2013.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.463 | 0 | 0 | 39020.463 | 1 | 0 | 1754.5 | 2030.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4632 | 1 | 0 | 39020.4632 | 1 | 0 | 1771 | 2047 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4634 | 1 | 0 | 39020.4634 | 1 | 0 | 1788 | 2064 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4636 | 1 | 0 | 39020.4636 | 1 | 0 | 1804.5 | 2080.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4638 | 1 | 0 | 39020.4638 | 1 | 0 | 1821.5 | 2097.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.464 | 1 | 0 | 39020.464 | 1 | 0 | 1838.5 | 2114.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4642 | 1 | 0 | 39020.4642 | 0 | 0 | 1855 | 2131 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4644 | 1 | 0 | 39020.4644 | 1 | 0 | 1872 | 2148 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4645 | 1 | 0 | 39020.4646 | 1 | 0 | 1888.5 | 2164.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4647 | 1 | 0 | 39020.4648 | 1 | 0 | 1905.5 | 2181.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4649 | 1 | 0 | 39020.465 | 1 | 0 | 1922.5 | 2198.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4651 | 1 | 0 | 39020.4652 | 1 | 0 | 1939 | 2215 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4653 | 1 | 0 | 39020.4653 | 1 | 0 | 1956 | 2232 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4655 | 1 | 0 | 39020.4655 | 1 | 0 | 1972.5 | 2248.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4657 | 1 | 0 | 39020.4657 | 1 | 0 | 1989.5 | 2265.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4659 | 1 | 0 | 39020.4659 | 1 | 0 | 2006.5 | 2282.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-4
Open Burn Test 4 |  |  | 2006-10-30 | 10:40 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray G
0 | 250 kW |  | Bundle | 2 & 4
Time-9 | N11 | N12 | Time-10 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39020.4396 | 1 | 0 | 39020.4397 | 1 | 0 | -264 | 12 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4398 | 1 | 0 | 39020.4398 | 1 | 0 | -247.5 | 28.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.44 | 0 | 0 | 39020.44 | 1 | 0 | -230.5 | 45.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4402 | 1 | 0 | 39020.4402 | 1 | 0 | -213.5 | 62.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4404 | 1 | 0 | 39020.4404 | 1 | 0 | -197 | 79 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4406 | 1 | 0 | 39020.4406 | 1 | 0 | -180 | 96 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4408 | 1 | 0 | 39020.4408 | 1 | 0 | -163.5 | 112.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.441 | 1 | 0 | 39020.441 | 0 | 0 | -146.5 | 129.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4412 | 1 | 0 | 39020.4412 | 1 | 0 | -129.5 | 146.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4414 | 1 | 0 | 39020.4414 | 1 | 0 | -113 | 163 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4416 | 1 | 0 | 39020.4416 | 1 | 0 | -96.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4418 | 1 | 0 | 39020.4418 | 1 | 0 | -79.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.442 | 1 | 0 | 39020.442 | 1 | 0 | -62.5 | 213.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4422 | 1 | 0 | 39020.4422 | 1 | 0 | -46 | 230 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4423 | 1 | 0 | 39020.4424 | 1 | 0 | -29 | 247 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4425 | 1 | 0 | 39020.4426 | 1 | 0 | -12.5 | 263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4427 | 1 | 0 | 39020.4428 | 1 | 0 | 4.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4429 | 1 | 0 | 39020.443 | 1 | 0 | 21.5 | 297.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4431 | 1 | 0 | 39020.4431 | 1 | 0 | 38.5 | 314.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4433 | 1 | 0 | 39020.4433 | 1 | 0 | 55 | 331 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4435 | 1 | 0 | 39020.4435 | 1 | 0 | 71.5 | 347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4437 | 1 | 0 | 39020.4437 | 1 | 0 | 88.5 | 364.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4439 | 1 | 0 | 39020.4439 | 1 | 0 | 105.5 | 381.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4441 | 1 | 0 | 39020.4441 | 1 | 0 | 122 | 398 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4443 | 1 | 0 | 39020.4443 | 1 | 0 | 139 | 415 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4445 | 1 | 0 | 39020.4445 | 1 | 0 | 155.5 | 431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4447 | 1 | 0 | 39020.4447 | 1 | 0 | 172.5 | 448.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4449 | 1 | 0 | 39020.4449 | 1 | 0 | 189.5 | 465.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4451 | 1 | 0 | 39020.4451 | 1 | 0 | 206 | 482 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4453 | 1 | 0 | 39020.4453 | 1 | 0 | 223 | 499 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4455 | 1 | 0 | 39020.4455 | 0 | 0 | 240 | 516 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4457 | 1 | 0 | 39020.4457 | 1 | 0 | 256.5 | 532.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4459 | 1 | 0 | 39020.4459 | 1 | 0 | 273.5 | 549.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.446 | 1 | 0 | 39020.4461 | 1 | 0 | 290 | 566 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4462 | 1 | 0 | 39020.4463 | 1 | 0 | 307 | 583 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4464 | 1 | 0 | 39020.4464 | 1 | 0 | 323.5 | 599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4466 | 1 | 0 | 39020.4466 | 1 | 0 | 340.5 | 616.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4468 | 1 | 0 | 39020.4468 | 1 | 0 | 357.5 | 633.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.447 | 1 | 0 | 39020.447 | 1 | 0 | 374 | 650 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4472 | 1 | 0 | 39020.4472 | 1 | 0 | 391 | 667 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4474 | 1 | 0 | 39020.4474 | 0 | 0 | 407.5 | 683.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4476 | 1 | 0 | 39020.4476 | 1 | 0 | 424.5 | 700.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4478 | 1 | 0 | 39020.4478 | 1 | 0 | 441.5 | 717.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.448 | 1 | 0 | 39020.448 | 1 | 0 | 458 | 734 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4482 | 0 | 0 | 39020.4482 | 1 | 0 | 475 | 751 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4484 | 0 | 0 | 39020.4484 | 1 | 0 | 491.5 | 767.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4486 | 1 | 0 | 39020.4486 | 0 | 0 | 508.5 | 784.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4488 | 0 | 0 | 39020.4488 | 1 | 0 | 525.5 | 801.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.449 | 1 | 0 | 39020.449 | 1 | 0 | 542 | 818 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4492 | 1 | 0 | 39020.4492 | 1 | 0 | 559 | 835 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4494 | 1 | 0 | 39020.4494 | 1 | 0 | 575.5 | 851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4495 | 1 | 0 | 39020.4496 | 1 | 0 | 592.5 | 868.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4497 | 1 | 0 | 39020.4498 | 1 | 0 | 609.5 | 885.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4499 | 1 | 0 | 39020.45 | 1 | 0 | 626 | 902 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4501 | 1 | 0 | 39020.4502 | 1 | 0 | 643 | 919 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4503 | 1 | 0 | 39020.4503 | 1 | 0 | 659.5 | 935.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4505 | 1 | 0 | 39020.4505 | 1 | 0 | 676.5 | 952.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4507 | 1 | 0 | 39020.4507 | 1 | 0 | 693.5 | 969.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4509 | 1 | 0 | 39020.4509 | 1 | 0 | 710 | 986 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4511 | 1 | 0 | 39020.4511 | 1 | 0 | 727 | 1003 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4513 | 1 | 0 | 39020.4513 | 1 | 0 | 743.5 | 1019.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4515 | 1 | 0 | 39020.4515 | 1 | 0 | 760.5 | 1036.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4517 | 1 | 0 | 39020.4517 | 1 | 0 | 777.5 | 1053.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4519 | 1 | 0 | 39020.4519 | 1 | 0 | 794 | 1070 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4521 | 1 | 0 | 39020.4521 | 1 | 0 | 811 | 1087 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4523 | 1 | 0 | 39020.4523 | 1 | 0 | 827.5 | 1103.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4525 | 1 | 0 | 39020.4525 | 1 | 0 | 844.5 | 1120.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4527 | 1 | 0 | 39020.4527 | 1 | 0 | 861.5 | 1137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4528 | 1 | 0 | 39020.4529 | 1 | 0 | 878 | 1154 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.453 | 1 | 0 | 39020.4531 | 1 | 0 | 895 | 1171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4532 | 1 | 0 | 39020.4533 | 0 | 0 | 911.5 | 1187.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4534 | 1 | 0 | 39020.4534 | 1 | 0 | 928.5 | 1204.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4536 | 1 | 0 | 39020.4536 | 1 | 0 | 945.5 | 1221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4538 | 1 | 0 | 39020.4538 | 1 | 0 | 962 | 1238 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.454 | 1 | 0 | 39020.454 | 1 | 0 | 979 | 1255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4542 | 1 | 0 | 39020.4542 | 1 | 0 | 995.5 | 1271.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4544 | 1 | 0 | 39020.4544 | 1 | 0 | 1012.5 | 1288.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4546 | 1 | 0 | 39020.4546 | 1 | 0 | 1029.5 | 1305.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4548 | 1 | 0 | 39020.4548 | 1 | 0 | 1046 | 1322 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.455 | 1 | 0 | 39020.455 | 1 | 0 | 1063 | 1339 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4552 | 1 | 0 | 39020.4552 | 1 | 0 | 1079.5 | 1355.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4554 | 1 | 0 | 39020.4554 | 1 | 0 | 1096.5 | 1372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4556 | 1 | 0 | 39020.4556 | 1 | 0 | 1113.5 | 1389.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4558 | 1 | 0 | 39020.4558 | 1 | 0 | 1130 | 1406 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.456 | 1 | 0 | 39020.456 | 1 | 0 | 1147 | 1423 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4562 | 1 | 0 | 39020.4562 | 1 | 0 | 1163.5 | 1439.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4564 | 1 | 0 | 39020.4564 | 1 | 0 | 1180.5 | 1456.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4566 | 1 | 0 | 39020.4566 | 1 | 0 | 1197.5 | 1473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4567 | 1 | 0 | 39020.4568 | 1 | 0 | 1214 | 1490 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4569 | 1 | 0 | 39020.4569 | 0 | 0 | 1230.5 | 1506.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4571 | 1 | 0 | 39020.4571 | 1 | 0 | 1247.5 | 1523.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4573 | 1 | 0 | 39020.4573 | 1 | 0 | 1264.5 | 1540.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4575 | 1 | 0 | 39020.4575 | 1 | 0 | 1281 | 1557 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4577 | 1 | 0 | 39020.4577 | 1 | 0 | 1298 | 1574 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4579 | 1 | 0 | 39020.4579 | 1 | 0 | 1315 | 1591 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4581 | 1 | 0 | 39020.4581 | 1 | 0 | 1331.5 | 1607.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4583 | 1 | 0 | 39020.4583 | 1 | 0 | 1348.5 | 1624.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4585 | 1 | 0 | 39020.4585 | 1 | 0 | 1365 | 1641 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4587 | 1 | 0 | 39020.4587 | 1 | 0 | 1382 | 1658 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4589 | 1 | 0 | 39020.4589 | 1 | 0 | 1399 | 1675 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4591 | 1 | 0 | 39020.4591 | 1 | 0 | 1415.5 | 1691.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4593 | 1 | 0 | 39020.4593 | 1 | 0 | 1432.5 | 1708.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4595 | 1 | 0 | 39020.4595 | 1 | 0 | 1449 | 1725 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4597 | 1 | 0 | 39020.4597 | 1 | 0 | 1466 | 1742 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4598 | 1 | 0 | 39020.4599 | 0 | 0 | 1483 | 1759 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.46 | 1 | 0 | 39020.4601 | 1 | 0 | 1499.5 | 1775.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4602 | 1 | 0 | 39020.4603 | 1 | 0 | 1516.5 | 1792.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4604 | 1 | 0 | 39020.4605 | 1 | 0 | 1533 | 1809 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4606 | 1 | 0 | 39020.4606 | 1 | 0 | 1550 | 1826 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4608 | 1 | 0 | 39020.4608 | 1 | 0 | 1566.5 | 1842.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.461 | 0 | 0 | 39020.461 | 1 | 0 | 1583.5 | 1859.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4612 | 1 | 0 | 39020.4612 | 1 | 0 | 1600.5 | 1876.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4614 | 0 | 0 | 39020.4614 | 1 | 0 | 1617 | 1893 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4616 | 1 | 0 | 39020.4616 | 1 | 0 | 1634 | 1910 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4618 | 1 | 0 | 39020.4618 | 1 | 0 | 1651 | 1927 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.462 | 1 | 0 | 39020.462 | 1 | 0 | 1667.5 | 1943.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4622 | 1 | 0 | 39020.4622 | 1 | 0 | 1684.5 | 1960.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4624 | 1 | 0 | 39020.4624 | 1 | 0 | 1701 | 1977 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4626 | 1 | 0 | 39020.4626 | 1 | 0 | 1718 | 1994 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4628 | 1 | 0 | 39020.4628 | 1 | 0 | 1734.5 | 2010.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.463 | 1 | 0 | 39020.463 | 1 | 0 | 1751.5 | 2027.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4632 | 1 | 0 | 39020.4632 | 1 | 0 | 1768.5 | 2044.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4633 | 1 | 0 | 39020.4634 | 1 | 0 | 1785 | 2061 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4635 | 1 | 0 | 39020.4636 | 0 | 0 | 1802 | 2078 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4637 | 1 | 0 | 39020.4638 | 1 | 0 | 1818.5 | 2094.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4639 | 1 | 0 | 39020.4639 | 1 | 0 | 1835.5 | 2111.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4641 | 1 | 0 | 39020.4641 | 1 | 0 | 1852.5 | 2128.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4643 | 1 | 0 | 39020.4643 | 1 | 0 | 1869 | 2145 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4645 | 1 | 0 | 39020.4645 | 1 | 0 | 1886 | 2162 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4647 | 1 | 0 | 39020.4647 | 1 | 0 | 1902.5 | 2178.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4649 | 1 | 0 | 39020.4649 | 1 | 0 | 1919.5 | 2195.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4651 | 1 | 0 | 39020.4651 | 1 | 0 | 1936.5 | 2212.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4653 | 1 | 0 | 39020.4653 | 0 | 0 | 1953 | 2229 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4655 | 1 | 0 | 39020.4655 | 1 | 0 | 1970 | 2246 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4657 | 0 | 0 | 39020.4657 | 1 | 0 | 1986.5 | 2262.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4659 | 1 | 0 | 39020.4659 | 1 | 0 | 2003.5 | 2279.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C2-3
Open Burn Test 4 |  |  | 2006-10-30 | 10:40 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray G
0 | 250 kW |  | Bundle | 2 & 3
Time-7 | N11 | N12 | Time-8 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39020.4396 | 1 | 0 | 39020.4396 | 1 | 0 | -267 | 9 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4398 | 1 | 0 | 39020.4398 | 1 | 0 | -250 | 26 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.44 | 1 | 0 | 39020.44 | 1 | 0 | -233.5 | 42.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4402 | 1 | 0 | 39020.4402 | 1 | 0 | -216.5 | 59.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4404 | 1 | 0 | 39020.4404 | 1 | 0 | -199.5 | 76.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4406 | 0 | 0 | 39020.4406 | 1 | 0 | -183 | 93 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4408 | 1 | 0 | 39020.4408 | 1 | 0 | -166.5 | 109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.441 | 0 | 0 | 39020.441 | 0 | 0 | -149.5 | 126.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 422504 | 422504 | 422503.9997
39020.4412 | 0 | 0 | 39020.4412 | 1 | 0 | -132.5 | 143.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4414 | 1 | 0 | 39020.4414 | 1 | 0 | -115.5 | 160.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4415 | 0 | 0 | 39020.4416 | 1 | 0 | -99 | 177 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4417 | 1 | 0 | 39020.4418 | 1 | 0 | -82 | 194 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4419 | 1 | 0 | 39020.4419 | 1 | 0 | -65.5 | 210.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4421 | 1 | 0 | 39020.4421 | 1 | 0 | -48.5 | 227.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4423 | 1 | 0 | 39020.4423 | 1 | 0 | -31.5 | 244.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4425 | 1 | 0 | 39020.4425 | 1 | 0 | -15 | 261 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4427 | 1 | 0 | 39020.4427 | 0 | 0 | 2 | 278 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4429 | 1 | 0 | 39020.4429 | 1 | 0 | 18.5 | 294.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4431 | 1 | 0 | 39020.4431 | 1 | 0 | 35.5 | 311.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4433 | 1 | 0 | 39020.4433 | 1 | 0 | 52 | 328 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4435 | 1 | 0 | 39020.4435 | 1 | 0 | 69 | 345 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4437 | 1 | 0 | 39020.4437 | 0 | 0 | 85.5 | 361.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4439 | 1 | 0 | 39020.4439 | 1 | 0 | 102.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4441 | 1 | 0 | 39020.4441 | 1 | 0 | 119.5 | 395.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4443 | 1 | 0 | 39020.4443 | 1 | 0 | 136.5 | 412.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4445 | 0 | 0 | 39020.4445 | 1 | 0 | 153 | 429 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4447 | 1 | 0 | 39020.4447 | 1 | 0 | 169.5 | 445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4448 | 1 | 0 | 39020.4449 | 1 | 0 | 186.5 | 462.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.445 | 1 | 0 | 39020.4451 | 0 | 0 | 203.5 | 479.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4452 | 0 | 0 | 39020.4453 | 1 | 0 | 220 | 496 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4454 | 1 | 0 | 39020.4455 | 1 | 0 | 237 | 513 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4456 | 1 | 0 | 39020.4456 | 1 | 0 | 254 | 530 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4458 | 0 | 0 | 39020.4458 | 1 | 0 | 270.5 | 546.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.446 | 1 | 0 | 39020.446 | 1 | 0 | 287.5 | 563.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4462 | 1 | 0 | 39020.4462 | 0 | 0 | 304 | 580 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4464 | 1 | 0 | 39020.4464 | 1 | 0 | 321 | 597 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4466 | 1 | 0 | 39020.4466 | 1 | 0 | 338 | 614 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4468 | 1 | 0 | 39020.4468 | 1 | 0 | 354.5 | 630.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.447 | 0 | 0 | 39020.447 | 1 | 0 | 371.5 | 647.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4472 | 1 | 0 | 39020.4472 | 0 | 0 | 388.5 | 664.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4474 | 1 | 0 | 39020.4474 | 1 | 0 | 405 | 681 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4476 | 1 | 0 | 39020.4476 | 1 | 0 | 421.5 | 697.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4478 | 1 | 0 | 39020.4478 | 1 | 0 | 438.5 | 714.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.448 | 1 | 0 | 39020.448 | 1 | 0 | 455.5 | 731.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4481 | 1 | 0 | 39020.4482 | 0 | 0 | 472 | 748 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4483 | 1 | 0 | 39020.4484 | 1 | 0 | 489 | 765 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4485 | 1 | 0 | 39020.4486 | 1 | 0 | 506 | 782 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4487 | 1 | 0 | 39020.4488 | 0 | 0 | 522.5 | 798.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4489 | 1 | 0 | 39020.4489 | 1 | 0 | 539.5 | 815.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4491 | 1 | 0 | 39020.4491 | 1 | 0 | 556 | 832 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4493 | 1 | 0 | 39020.4493 | 1 | 0 | 573 | 849 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4495 | 1 | 0 | 39020.4495 | 1 | 0 | 589.5 | 865.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4497 | 1 | 0 | 39020.4497 | 1 | 0 | 606.5 | 882.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4499 | 1 | 0 | 39020.4499 | 1 | 0 | 623.5 | 899.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4501 | 1 | 0 | 39020.4501 | 1 | 0 | 640 | 916 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4503 | 1 | 0 | 39020.4503 | 1 | 0 | 657 | 933 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4505 | 1 | 0 | 39020.4505 | 1 | 0 | 673.5 | 949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4507 | 1 | 0 | 39020.4507 | 1 | 0 | 690.5 | 966.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4509 | 1 | 0 | 39020.4509 | 1 | 0 | 707.5 | 983.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4511 | 1 | 0 | 39020.4511 | 1 | 0 | 724 | 1000 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4513 | 1 | 0 | 39020.4513 | 1 | 0 | 741 | 1017 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 39020.4515 | 1 | 0 | 758 | 1034 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4517 | 1 | 0 | 39020.4517 | 1 | 0 | 774.5 | 1050.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4519 | 1 | 0 | 39020.4519 | 1 | 0 | 791.5 | 1067.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.452 | 1 | 0 | 39020.4521 | 1 | 0 | 808 | 1084 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4522 | 1 | 0 | 39020.4523 | 1 | 0 | 825 | 1101 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4524 | 1 | 0 | 39020.4524 | 1 | 0 | 841.5 | 1117.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4526 | 1 | 0 | 39020.4526 | 1 | 0 | 858.5 | 1134.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4528 | 1 | 0 | 39020.4528 | 1 | 0 | 875.5 | 1151.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.453 | 1 | 0 | 39020.453 | 1 | 0 | 892 | 1168 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4532 | 1 | 0 | 39020.4532 | 1 | 0 | 909 | 1185 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4534 | 1 | 0 | 39020.4534 | 1 | 0 | 925.5 | 1201.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4536 | 1 | 0 | 39020.4536 | 1 | 0 | 942.5 | 1218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4538 | 1 | 0 | 39020.4538 | 1 | 0 | 959.5 | 1235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.454 | 1 | 0 | 39020.454 | 1 | 0 | 976 | 1252 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4542 | 1 | 0 | 39020.4542 | 1 | 0 | 993 | 1269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4544 | 0 | 0 | 39020.4544 | 1 | 0 | 1009.5 | 1285.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4546 | 1 | 0 | 39020.4546 | 1 | 0 | 1026.5 | 1302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4548 | 1 | 0 | 39020.4548 | 1 | 0 | 1043.5 | 1319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.455 | 1 | 0 | 39020.455 | 1 | 0 | 1060 | 1336 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4552 | 1 | 0 | 39020.4552 | 0 | 0 | 1077 | 1353 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4553 | 1 | 0 | 39020.4554 | 1 | 0 | 1093.5 | 1369.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4555 | 1 | 0 | 39020.4556 | 1 | 0 | 1110.5 | 1386.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4557 | 1 | 0 | 39020.4558 | 1 | 0 | 1127.5 | 1403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4559 | 1 | 0 | 39020.4559 | 1 | 0 | 1144 | 1420 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4561 | 1 | 0 | 39020.4561 | 1 | 0 | 1161 | 1437 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
| 1 | 0 | 39020.4563 | 1 | 0 | 1178 | 1454 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4565 | 1 | 0 | 39020.4565 | 1 | 0 | 1194.5 | 1470.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4567 | 1 | 0 | 39020.4567 | 1 | 0 | 1211 | 1487 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4569 | 1 | 0 | 39020.4569 | 1 | 0 | 1228 | 1504 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4571 | 1 | 0 | 39020.4571 | 1 | 0 | 1245 | 1521 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4573 | 1 | 0 | 39020.4573 | 1 | 0 | 1261.5 | 1537.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4575 | 1 | 0 | 39020.4575 | 1 | 0 | 1278.5 | 1554.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4577 | 1 | 0 | 39020.4577 | 1 | 0 | 1295.5 | 1571.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4579 | 0 | 0 | 39020.4579 | 1 | 0 | 1312 | 1588 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4581 | 1 | 0 | 39020.4581 | 1 | 0 | 1329 | 1605 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4583 | 0 | 0 | 39020.4583 | 1 | 0 | 1345.5 | 1621.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4585 | 1 | 0 | 39020.4585 | 1 | 0 | 1362.5 | 1638.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4587 | 1 | 0 | 39020.4587 | 1 | 0 | 1379.5 | 1655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4588 | 1 | 0 | 39020.4589 | 1 | 0 | 1396 | 1672 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.459 | 1 | 0 | 39020.4591 | 1 | 0 | 1413 | 1689 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4592 | 1 | 0 | 39020.4592 | 1 | 0 | 1429.5 | 1705.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4594 | 1 | 0 | 39020.4594 | 1 | 0 | 1446.5 | 1722.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4596 | 1 | 0 | 39020.4596 | 1 | 0 | 1463.5 | 1739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4598 | 1 | 0 | 39020.4598 | 1 | 0 | 1480 | 1756 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.46 | 1 | 0 | 39020.46 | 1 | 0 | 1497 | 1773 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4602 | 1 | 0 | 39020.4602 | 1 | 0 | 1513.5 | 1789.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4604 | 1 | 0 | 39020.4604 | 1 | 0 | 1530.5 | 1806.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4606 | 1 | 0 | 39020.4606 | 1 | 0 | 1547.5 | 1823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4608 | 1 | 0 | 39020.4608 | 1 | 0 | 1564 | 1840 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.461 | 1 | 0 | 39020.461 | 1 | 0 | 1580.5 | 1856.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4612 | 1 | 0 | 39020.4612 | 1 | 0 | 1597.5 | 1873.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4614 | 1 | 0 | 39020.4614 | 2 | 0 | 1614.5 | 1890.5 | 0.06105 | 0 | 0.1221 | 0 | 0.0006105 | 0 | 0.001221 | 0 | 0.0006105 | 0.001221 | 211202 | 105551 | 211201.9994
39020.4616 | 1 | 0 | 39020.4616 | 1 | 0 | 1631 | 1907 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4618 | 1 | 0 | 39020.4618 | 1 | 0 | 1648 | 1924 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.462 | 1 | 0 | 39020.462 | 1 | 0 | 1664.5 | 1940.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4622 | 1 | 0 | 39020.4622 | 1 | 0 | 1681.5 | 1957.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4623 | 1 | 0 | 39020.4624 | 1 | 0 | 1698.5 | 1974.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4625 | 1 | 0 | 39020.4626 | 1 | 0 | 1715 | 1991 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4627 | 1 | 0 | 39020.4628 | 1 | 0 | 1732 | 2008 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4629 | 1 | 0 | 39020.4629 | 1 | 0 | 1748.5 | 2024.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4631 | 1 | 0 | 39020.4631 | 1 | 0 | 1765.5 | 2041.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4633 | 1 | 0 | 39020.4633 | 1 | 0 | 1782.5 | 2058.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4635 | 1 | 0 | 39020.4635 | 1 | 0 | 1799 | 2075 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4637 | 1 | 0 | 39020.4637 | 1 | 0 | 1816 | 2092 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4639 | 1 | 0 | 39020.4639 | 1 | 0 | 1832.5 | 2108.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4641 | 1 | 0 | 39020.4641 | 1 | 0 | 1849.5 | 2125.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4643 | 1 | 0 | 39020.4643 | 1 | 0 | 1866.5 | 2142.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4645 | 1 | 0 | 39020.4645 | 1 | 0 | 1883 | 2159 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4647 | 1 | 0 | 39020.4647 | 1 | 0 | 1900 | 2176 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4649 | 1 | 0 | 39020.4649 | 1 | 0 | 1916.5 | 2192.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4651 | 1 | 0 | 39020.4651 | 1 | 0 | 1933.5 | 2209.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4653 | 1 | 0 | 39020.4653 | 1 | 0 | 1950.5 | 2226.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4655 | 1 | 0 | 39020.4655 | 1 | 0 | 1967 | 2243 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4656 | 1 | 0 | 39020.4657 | 0 | 0 | 1984 | 2260 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4658 | 1 | 0 | 39020.4659 | 1 | 0 | 2000.5 | 2276.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-4
Open Burn Test 4 |  |  | 2006-10-30 | 10:40 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray G
0 | 250 kW |  | Bundle | 1 & 4
Time-5 | N11 | N12 | Time-6 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39020.4396 | 1 | 0 | 39020.4396 | 1 | 0 | -269.5 | 6.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4398 | 0 | 0 | 39020.4398 | 1 | 0 | -253 | 23 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.44 | 1 | 0 | 39020.44 | 1 | 0 | -236 | 40 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4402 | 1 | 0 | 39020.4402 | 1 | 0 | -219.5 | 56.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4403 | 1 | 0 | 39020.4404 | 0 | 0 | -202.5 | 73.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4405 | 1 | 0 | 39020.4406 | 1 | 0 | -185.5 | 90.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4407 | 1 | 0 | 39020.4408 | 0 | 0 | -169 | 107 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4409 | 0 | 0 | 39020.4409 | 1 | 0 | -152 | 124 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4411 | 1 | 0 | 39020.4411 | 1 | 0 | -135.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4413 | 0 | 0 | 39020.4413 | 0 | 0 | -118.5 | 157.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 422504 | 422504 | 422503.9997
39020.4415 | 1 | 0 | 39020.4415 | 1 | 0 | -102 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4417 | 1 | 0 | 39020.4417 | 1 | 0 | -85 | 191 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4419 | 1 | 0 | 39020.4419 | 1 | 0 | -68.5 | 207.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4421 | 1 | 0 | 39020.4421 | 1 | 0 | -51.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4423 | 1 | 0 | 39020.4423 | 1 | 0 | -34.5 | 241.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4425 | 1 | 0 | 39020.4425 | 1 | 0 | -17.5 | 258.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4427 | 1 | 0 | 39020.4427 | 1 | 0 | -1 | 275 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4429 | 0 | 0 | 39020.4429 | 1 | 0 | 16 | 292 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4431 | 1 | 0 | 39020.4431 | 1 | 0 | 32.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4433 | 1 | 0 | 39020.4433 | 1 | 0 | 49.5 | 325.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4434 | 1 | 0 | 39020.4435 | 1 | 0 | 66 | 342 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4436 | 1 | 0 | 39020.4437 | 1 | 0 | 83 | 359 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4438 | 0 | 0 | 39020.4439 | 1 | 0 | 99.5 | 375.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.444 | 1 | 0 | 39020.4441 | 1 | 0 | 116.5 | 392.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4442 | 1 | 0 | 39020.4442 | 0 | 0 | 133.5 | 409.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4444 | 1 | 0 | 39020.4444 | 1 | 0 | 150 | 426 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4446 | 1 | 0 | 39020.4446 | 1 | 0 | 167 | 443 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4448 | 1 | 0 | 39020.4448 | 1 | 0 | 184 | 460 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.445 | 1 | 0 | 39020.445 | 1 | 0 | 200.5 | 476.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4452 | 1 | 0 | 39020.4452 | 1 | 0 | 217.5 | 493.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4454 | 1 | 0 | 39020.4454 | 1 | 0 | 234 | 510 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4456 | 1 | 0 | 39020.4456 | 1 | 0 | 251 | 527 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4458 | 1 | 0 | 39020.4458 | 1 | 0 | 267.5 | 543.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.446 | 1 | 0 | 39020.446 | 1 | 0 | 284.5 | 560.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4462 | 1 | 0 | 39020.4462 | 1 | 0 | 301.5 | 577.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4464 | 1 | 0 | 39020.4464 | 1 | 0 | 318.5 | 594.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4466 | 1 | 0 | 39020.4466 | 1 | 0 | 335 | 611 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4468 | 1 | 0 | 39020.4468 | 1 | 0 | 351.5 | 627.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.447 | 1 | 0 | 39020.447 | 1 | 0 | 368.5 | 644.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4472 | 1 | 0 | 39020.4472 | 1 | 0 | 385.5 | 661.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4473 | 1 | 0 | 39020.4474 | 1 | 0 | 402.5 | 678.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4475 | 1 | 0 | 39020.4476 | 1 | 0 | 419 | 695 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4477 | 1 | 0 | 39020.4477 | 1 | 0 | 435.5 | 711.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4479 | 1 | 0 | 39020.4479 | 1 | 0 | 452.5 | 728.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4481 | 1 | 0 | 39020.4481 | 1 | 0 | 469.5 | 745.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4483 | 1 | 0 | 39020.4483 | 1 | 0 | 486 | 762 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4485 | 1 | 0 | 39020.4485 | 1 | 0 | 503 | 779 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4487 | 1 | 0 | 39020.4487 | 1 | 0 | 519.5 | 795.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4489 | 1 | 0 | 39020.4489 | 1 | 0 | 536.5 | 812.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4491 | 1 | 0 | 39020.4491 | 0 | 0 | 553.5 | 829.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4493 | 1 | 0 | 39020.4493 | 1 | 0 | 570 | 846 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4495 | 1 | 0 | 39020.4495 | 1 | 0 | 587 | 863 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4497 | 1 | 0 | 39020.4497 | 1 | 0 | 603.5 | 879.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4499 | 1 | 0 | 39020.4499 | 1 | 0 | 620.5 | 896.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4501 | 1 | 0 | 39020.4501 | 1 | 0 | 637.5 | 913.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4503 | 1 | 0 | 39020.4503 | 1 | 0 | 654 | 930 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4505 | 0 | 0 | 39020.4505 | 1 | 0 | 671 | 947 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4506 | 1 | 0 | 39020.4507 | 1 | 0 | 687.5 | 963.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4508 | 1 | 0 | 39020.4509 | 1 | 0 | 704.5 | 980.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.451 | 1 | 0 | 39020.4511 | 1 | 0 | 721.5 | 997.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4512 | 1 | 0 | 39020.4512 | 1 | 0 | 738 | 1014 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4514 | 1 | 0 | 39020.4514 | 1 | 0 | 755 | 1031 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4516 | 1 | 0 | 39020.4516 | 1 | 0 | 771.5 | 1047.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4518 | 1 | 0 | 39020.4518 | 1 | 0 | 788.5 | 1064.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.452 | 1 | 0 | 39020.452 | 1 | 0 | 805.5 | 1081.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4522 | 1 | 0 | 39020.4522 | 1 | 0 | 822 | 1098 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4524 | 1 | 0 | 39020.4524 | 1 | 0 | 839 | 1115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4526 | 1 | 0 | 39020.4526 | 1 | 0 | 855.5 | 1131.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4528 | 1 | 0 | 39020.4528 | 1 | 0 | 872.5 | 1148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.453 | 1 | 0 | 39020.453 | 1 | 0 | 889.5 | 1165.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4532 | 1 | 0 | 39020.4532 | 1 | 0 | 906 | 1182 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4534 | 1 | 0 | 39020.4534 | 1 | 0 | 923 | 1199 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4536 | 1 | 0 | 39020.4536 | 0 | 0 | 939.5 | 1215.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4538 | 1 | 0 | 39020.4538 | 1 | 0 | 956.5 | 1232.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.454 | 1 | 0 | 39020.454 | 1 | 0 | 973.5 | 1249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4541 | 1 | 0 | 39020.4542 | 1 | 0 | 990 | 1266 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4543 | 1 | 0 | 39020.4544 | 1 | 0 | 1007 | 1283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4545 | 1 | 0 | 39020.4545 | 1 | 0 | 1023.5 | 1299.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4547 | 1 | 0 | 39020.4547 | 1 | 0 | 1040.5 | 1316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4549 | 1 | 0 | 39020.4549 | 1 | 0 | 1057.5 | 1333.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4551 | 1 | 0 | 39020.4551 | 1 | 0 | 1074 | 1350 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4553 | 1 | 0 | 39020.4553 | 1 | 0 | 1091 | 1367 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4555 | 1 | 0 | 39020.4555 | 1 | 0 | 1107.5 | 1383.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4557 | 1 | 0 | 39020.4557 | 1 | 0 | 1124.5 | 1400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4559 | 1 | 0 | 39020.4559 | 1 | 0 | 1141.5 | 1417.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4561 | 1 | 0 | 39020.4561 | 1 | 0 | 1158 | 1434 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4563 | 1 | 0 | 39020.4563 | 1 | 0 | 1175 | 1451 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4565 | 1 | 0 | 39020.4565 | 1 | 0 | 1191.5 | 1467.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4567 | 1 | 0 | 39020.4567 | 1 | 0 | 1208.5 | 1484.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4569 | 1 | 0 | 39020.4569 | 1 | 0 | 1225.5 | 1501.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4571 | 1 | 0 | 39020.4571 | 1 | 0 | 1242 | 1518 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4573 | 1 | 0 | 39020.4573 | 1 | 0 | 1259 | 1535 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4575 | 1 | 0 | 39020.4575 | 1 | 0 | 1275.5 | 1551.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4577 | 1 | 0 | 39020.4577 | 1 | 0 | 1292.5 | 1568.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4578 | 1 | 0 | 39020.4579 | 1 | 0 | 1309.5 | 1585.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.458 | 1 | 0 | 39020.4581 | 1 | 0 | 1326 | 1602 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4582 | 1 | 0 | 39020.4583 | 1 | 0 | 1343 | 1619 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4584 | 1 | 0 | 39020.4584 | 1 | 0 | 1359.5 | 1635.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4586 | 1 | 0 | 39020.4586 | 1 | 0 | 1376.5 | 1652.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4588 | 1 | 0 | 39020.4588 | 1 | 0 | 1393.5 | 1669.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.459 | 1 | 0 | 39020.459 | 1 | 0 | 1410 | 1686 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4592 | 1 | 0 | 39020.4592 | 1 | 0 | 1426.5 | 1702.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4594 | 1 | 0 | 39020.4594 | 1 | 0 | 1443.5 | 1719.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4596 | 1 | 0 | 39020.4596 | 1 | 0 | 1460.5 | 1736.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4598 | 1 | 0 | 39020.4598 | 1 | 0 | 1477 | 1753 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.46 | 1 | 0 | 39020.46 | 1 | 0 | 1494 | 1770 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4602 | 1 | 0 | 39020.4602 | 1 | 0 | 1511 | 1787 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4604 | 1 | 0 | 39020.4604 | 1 | 0 | 1527.5 | 1803.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4606 | 1 | 0 | 39020.4606 | 1 | 0 | 1544.5 | 1820.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4608 | 1 | 0 | 39020.4608 | 0 | 0 | 1561 | 1837 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4609 | 1 | 0 | 39020.461 | 1 | 0 | 1578 | 1854 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4611 | 1 | 0 | 39020.4612 | 1 | 0 | 1594.5 | 1870.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4613 | 1 | 0 | 39020.4614 | 1 | 0 | 1611.5 | 1887.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4615 | 1 | 0 | 39020.4616 | 1 | 0 | 1628.5 | 1904.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4617 | 1 | 0 | 39020.4617 | 1 | 0 | 1645 | 1921 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4619 | 1 | 0 | 39020.4619 | 1 | 0 | 1662 | 1938 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4621 | 1 | 0 | 39020.4621 | 1 | 0 | 1678.5 | 1954.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4623 | 1 | 0 | 39020.4623 | 1 | 0 | 1695.5 | 1971.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4625 | 1 | 0 | 39020.4625 | 1 | 0 | 1712.5 | 1988.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4627 | 1 | 0 | 39020.4627 | 1 | 0 | 1729 | 2005 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4629 | 1 | 0 | 39020.4629 | 1 | 0 | 1746 | 2022 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4631 | 1 | 0 | 39020.4631 | 1 | 0 | 1762.5 | 2038.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4633 | 1 | 0 | 39020.4633 | 1 | 0 | 1779.5 | 2055.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4635 | 0 | 0 | 39020.4635 | 1 | 0 | 1796.5 | 2072.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4637 | 1 | 0 | 39020.4637 | 1 | 0 | 1813 | 2089 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4639 | 1 | 0 | 39020.4639 | 1 | 0 | 1830 | 2106 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4641 | 1 | 0 | 39020.4641 | 1 | 0 | 1846.5 | 2122.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4643 | 1 | 0 | 39020.4643 | 1 | 0 | 1863.5 | 2139.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4645 | 1 | 0 | 39020.4645 | 1 | 0 | 1880.5 | 2156.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4646 | 1 | 0 | 39020.4647 | 1 | 0 | 1897 | 2173 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4648 | 1 | 0 | 39020.4649 | 1 | 0 | 1914 | 2190 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.465 | 1 | 0 | 39020.465 | 1 | 0 | 1930.5 | 2206.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4652 | 1 | 0 | 39020.4652 | 1 | 0 | 1947.5 | 2223.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4654 | 1 | 0 | 39020.4654 | 1 | 0 | 1964.5 | 2240.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4656 | 1 | 0 | 39020.4656 | 1 | 0 | 1981 | 2257 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4658 | 1 | 0 | 39020.4658 | 1 | 0 | 1998 | 2274 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-3
Open Burn Test 4 |  |  | 2006-10-30 | 10:40 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray G
0 | 250 kW |  | Bundle | 1 & 3
Time-3 | N11 | N12 | Time-4 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39020.4395 | 1 | 0 | 39020.4395 | 1 | 0 | -272.5 | 3.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4397 | 1 | 0 | 39020.4397 | 1 | 0 | -255.5 | 20.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4399 | 1 | 0 | 39020.4399 | 1 | 0 | -239 | 37 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4401 | 1 | 0 | 39020.4401 | 1 | 0 | -222 | 54 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4403 | 1 | 0 | 39020.4403 | 1 | 0 | -205.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4405 | 1 | 0 | 39020.4405 | 0 | 0 | -188.5 | 87.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4407 | 1 | 0 | 39020.4407 | 1 | 0 | -172 | 104 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4409 | 0 | 0 | 39020.4409 | 1 | 0 | -155 | 121 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4411 | 1 | 0 | 39020.4411 | 1 | 0 | -138 | 138 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4413 | 0 | 0 | 39020.4413 | 1 | 0 | -121.5 | 154.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4415 | 1 | 0 | 39020.4415 | 1 | 0 | -104.5 | 171.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4417 | 1 | 0 | 39020.4417 | 1 | 0 | -87.5 | 188.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4419 | 1 | 0 | 39020.4419 | 1 | 0 | -71 | 205 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4421 | 1 | 0 | 39020.4421 | 1 | 0 | -54 | 222 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4423 | 1 | 0 | 39020.4423 | 1 | 0 | -37.5 | 238.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4425 | 0 | 0 | 39020.4425 | 0 | 0 | -20.5 | 255.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 422504 | 422504 | 422503.9997
39020.4427 | 1 | 0 | 39020.4427 | 1 | 0 | -3.5 | 272.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4428 | 1 | 0 | 39020.4429 | 1 | 0 | 13 | 289 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.443 | 1 | 0 | 39020.4431 | 1 | 0 | 30 | 306 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4432 | 1 | 0 | 39020.4432 | 1 | 0 | 46.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4434 | 0 | 0 | 39020.4434 | 0 | 0 | 63.5 | 339.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 422504 | 422504 | 422503.9997
39020.4436 | 1 | 0 | 39020.4436 | 1 | 0 | 80 | 356 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4438 | 1 | 0 | 39020.4438 | 1 | 0 | 97 | 373 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.444 | 1 | 0 | 39020.444 | 1 | 0 | 114 | 390 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4442 | 1 | 0 | 39020.4442 | 1 | 0 | 130.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4444 | 0 | 0 | 39020.4444 | 1 | 0 | 147.5 | 423.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4446 | 1 | 0 | 39020.4446 | 1 | 0 | 164 | 440 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4448 | 1 | 0 | 39020.4448 | 1 | 0 | 181 | 457 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.445 | 1 | 0 | 39020.445 | 1 | 0 | 197.5 | 473.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4452 | 1 | 0 | 39020.4452 | 1 | 0 | 214.5 | 490.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4454 | 1 | 0 | 39020.4454 | 1 | 0 | 231.5 | 507.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4456 | 1 | 0 | 39020.4456 | 1 | 0 | 248.5 | 524.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4458 | 1 | 0 | 39020.4458 | 1 | 0 | 265 | 541 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4459 | 1 | 0 | 39020.446 | 1 | 0 | 281.5 | 557.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4461 | 1 | 0 | 39020.4462 | 1 | 0 | 298.5 | 574.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4463 | 1 | 0 | 39020.4464 | 1 | 0 | 315.5 | 591.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4465 | 1 | 0 | 39020.4466 | 1 | 0 | 332 | 608 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4467 | 1 | 0 | 39020.4467 | 0 | 0 | 349 | 625 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4469 | 1 | 0 | 39020.4469 | 1 | 0 | 365.5 | 641.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4471 | 1 | 0 | 39020.4471 | 0 | 0 | 382.5 | 658.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4473 | 1 | 0 | 39020.4473 | 1 | 0 | 399.5 | 675.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4475 | 1 | 0 | 39020.4475 | 1 | 0 | 416 | 692 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4477 | 1 | 0 | 39020.4477 | 1 | 0 | 433 | 709 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4479 | 1 | 0 | 39020.4479 | 1 | 0 | 449.5 | 725.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4481 | 1 | 0 | 39020.4481 | 1 | 0 | 466.5 | 742.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4483 | 1 | 0 | 39020.4483 | 1 | 0 | 483.5 | 759.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4485 | 1 | 0 | 39020.4485 | 1 | 0 | 500 | 776 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4487 | 1 | 0 | 39020.4487 | 1 | 0 | 517 | 793 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4489 | 1 | 0 | 39020.4489 | 1 | 0 | 533.5 | 809.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4491 | 0 | 0 | 39020.4491 | 1 | 0 | 550.5 | 826.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4493 | 1 | 0 | 39020.4493 | 1 | 0 | 567.5 | 843.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4494 | 1 | 0 | 39020.4495 | 0 | 0 | 584 | 860 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4496 | 1 | 0 | 39020.4497 | 1 | 0 | 601 | 877 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4498 | 1 | 0 | 39020.4498 | 0 | 0 | 617.5 | 893.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.45 | 1 | 0 | 39020.45 | 1 | 0 | 634.5 | 910.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4502 | 1 | 0 | 39020.4502 | 1 | 0 | 651.5 | 927.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4504 | 0 | 0 | 39020.4504 | 1 | 0 | 668 | 944 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4506 | 1 | 0 | 39020.4506 | 1 | 0 | 685 | 961 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4508 | 1 | 0 | 39020.4508 | 1 | 0 | 701.5 | 977.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.451 | 1 | 0 | 39020.451 | 1 | 0 | 718.5 | 994.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4512 | 1 | 0 | 39020.4512 | 1 | 0 | 735.5 | 1011.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4514 | 1 | 0 | 39020.4514 | 1 | 0 | 752 | 1028 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4516 | 1 | 0 | 39020.4516 | 1 | 0 | 769 | 1045 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4518 | 1 | 0 | 39020.4518 | 1 | 0 | 785.5 | 1061.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.452 | 1 | 0 | 39020.452 | 1 | 0 | 802.5 | 1078.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4522 | 1 | 0 | 39020.4522 | 1 | 0 | 819.5 | 1095.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4524 | 1 | 0 | 39020.4524 | 1 | 0 | 836 | 1112 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4526 | 1 | 0 | 39020.4526 | 1 | 0 | 853 | 1129 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4528 | 1 | 0 | 39020.4528 | 1 | 0 | 869.5 | 1145.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.453 | 1 | 0 | 39020.453 | 1 | 0 | 886.5 | 1162.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4531 | 1 | 0 | 39020.4532 | 1 | 0 | 903.5 | 1179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4533 | 1 | 0 | 39020.4534 | 1 | 0 | 920 | 1196 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4535 | 1 | 0 | 39020.4536 | 1 | 0 | 937 | 1213 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4537 | 1 | 0 | 39020.4537 | 1 | 0 | 953.5 | 1229.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4539 | 0 | 0 | 39020.4539 | 1 | 0 | 970.5 | 1246.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4541 | 1 | 0 | 39020.4541 | 1 | 0 | 987.5 | 1263.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4543 | 1 | 0 | 39020.4543 | 1 | 0 | 1004 | 1280 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4545 | 1 | 0 | 39020.4545 | 1 | 0 | 1021 | 1297 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4547 | 1 | 0 | 39020.4547 | 1 | 0 | 1037.5 | 1313.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4549 | 1 | 0 | 39020.4549 | 1 | 0 | 1054.5 | 1330.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4551 | 1 | 0 | 39020.4551 | 1 | 0 | 1071.5 | 1347.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4553 | 1 | 0 | 39020.4553 | 1 | 0 | 1088 | 1364 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4555 | 1 | 0 | 39020.4555 | 1 | 0 | 1104.5 | 1380.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4557 | 1 | 0 | 39020.4557 | 1 | 0 | 1121.5 | 1397.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4559 | 1 | 0 | 39020.4559 | 1 | 0 | 1138.5 | 1414.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4561 | 1 | 0 | 39020.4561 | 1 | 0 | 1155.5 | 1431.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4563 | 1 | 0 | 39020.4563 | 1 | 0 | 1172 | 1448 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4564 | 1 | 0 | 39020.4565 | 1 | 0 | 1189 | 1465 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4566 | 1 | 0 | 39020.4567 | 1 | 0 | 1205.5 | 1481.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4568 | 1 | 0 | 39020.4569 | 1 | 0 | 1222.5 | 1498.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.457 | 1 | 0 | 39020.457 | 1 | 0 | 1239.5 | 1515.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4572 | 1 | 0 | 39020.4572 | 1 | 0 | 1256 | 1532 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4574 | 1 | 0 | 39020.4574 | 1 | 0 | 1272.5 | 1548.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4576 | 1 | 0 | 39020.4576 | 1 | 0 | 1289.5 | 1565.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4578 | 1 | 0 | 39020.4578 | 1 | 0 | 1306.5 | 1582.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.458 | 1 | 0 | 39020.458 | 1 | 0 | 1323.5 | 1599.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4582 | 1 | 0 | 39020.4582 | 0 | 0 | 1340 | 1616 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4584 | 1 | 0 | 39020.4584 | 1 | 0 | 1356.5 | 1632.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4586 | 1 | 0 | 39020.4586 | 1 | 0 | 1373.5 | 1649.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4588 | 1 | 0 | 39020.4588 | 1 | 0 | 1390.5 | 1666.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.459 | 1 | 0 | 39020.459 | 1 | 0 | 1407.5 | 1683.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4592 | 1 | 0 | 39020.4592 | 1 | 0 | 1424 | 1700 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4594 | 1 | 0 | 39020.4594 | 0 | 0 | 1440.5 | 1716.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4596 | 1 | 0 | 39020.4596 | 1 | 0 | 1457.5 | 1733.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4598 | 1 | 0 | 39020.4598 | 1 | 0 | 1474.5 | 1750.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4599 | 1 | 0 | 39020.46 | 1 | 0 | 1491 | 1767 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4601 | 1 | 0 | 39020.4602 | 1 | 0 | 1508 | 1784 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4603 | 0 | 0 | 39020.4603 | 1 | 0 | 1524.5 | 1800.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4605 | 1 | 0 | 39020.4605 | 1 | 0 | 1541.5 | 1817.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4607 | 1 | 0 | 39020.4607 | 1 | 0 | 1558.5 | 1834.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4609 | 1 | 0 | 39020.4609 | 1 | 0 | 1575.5 | 1851.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4611 | 1 | 0 | 39020.4611 | 1 | 0 | 1592 | 1868 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4613 | 1 | 0 | 39020.4613 | 1 | 0 | 1608.5 | 1884.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4615 | 1 | 0 | 39020.4615 | 1 | 0 | 1625.5 | 1901.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4617 | 1 | 0 | 39020.4617 | 1 | 0 | 1642.5 | 1918.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4619 | 1 | 0 | 39020.4619 | 1 | 0 | 1659 | 1935 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4621 | 1 | 0 | 39020.4621 | 1 | 0 | 1676 | 1952 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4623 | 0 | 0 | 39020.4623 | 1 | 0 | 1692.5 | 1968.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4625 | 1 | 0 | 39020.4625 | 1 | 0 | 1709.5 | 1985.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4627 | 1 | 0 | 39020.4627 | 1 | 0 | 1726.5 | 2002.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4629 | 1 | 0 | 39020.4629 | 1 | 0 | 1743 | 2019 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4631 | 1 | 0 | 39020.4631 | 1 | 0 | 1760 | 2036 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4633 | 1 | 0 | 39020.4633 | 0 | 0 | 1776.5 | 2052.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4634 | 1 | 0 | 39020.4635 | 1 | 0 | 1793.5 | 2069.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4636 | 1 | 0 | 39020.4637 | 1 | 0 | 1810.5 | 2086.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4638 | 1 | 0 | 39020.4639 | 0 | 0 | 1827 | 2103 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.464 | 1 | 0 | 39020.4641 | 1 | 0 | 1844 | 2120 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4642 | 1 | 0 | 39020.4642 | 1 | 0 | 1860.5 | 2136.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4644 | 1 | 0 | 39020.4644 | 1 | 0 | 1877.5 | 2153.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4646 | 1 | 0 | 39020.4646 | 1 | 0 | 1894.5 | 2170.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4648 | 1 | 0 | 39020.4648 | 1 | 0 | 1911 | 2187 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.465 | 1 | 0 | 39020.465 | 0 | 0 | 1928 | 2204 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4652 | 1 | 0 | 39020.4652 | 1 | 0 | 1944.5 | 2220.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4654 | 1 | 0 | 39020.4654 | 1 | 0 | 1961.5 | 2237.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4656 | 1 | 0 | 39020.4656 | 1 | 0 | 1978.5 | 2254.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4658 | 1 | 0 | 39020.4658 | 1 | 0 | 1995 | 2271 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## C1-2
Open Burn Test 4 |  |  | 2006-10-30 | 10:40 |  | Vs = |  | 129 |  | R = | 100
XLPE | 3-C | Tray G
0 | 250 kW |  | Bundle | 1 & 2
Time-1 | N11 | N12 | Time-2 | N21 | N22 | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39020.4395 | 1 | 0 | 39020.4395 | 0 | 0 | -275.5 | 0.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4397 | 1 | 0 | 39020.4397 | 1 | 0 | -258.5 | 17.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4399 | 0 | 0 | 39020.4399 | 1 | 0 | -241.5 | 34.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4401 | 1 | 0 | 39020.4401 | 1 | 0 | -225 | 51 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4403 | 0 | 0 | 39020.4403 | 1 | 0 | -208 | 68 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4405 | 1 | 0 | 39020.4405 | 1 | 0 | -191.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4407 | 1 | 0 | 39020.4407 | 1 | 0 | -174.5 | 101.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4409 | 0 | 0 | 39020.4409 | 1 | 0 | -158 | 118 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4411 | 1 | 0 | 39020.4411 | 1 | 0 | -141 | 135 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4413 | 1 | 0 | 39020.4413 | 1 | 0 | -124 | 152 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4414 | 1 | 0 | 39020.4415 | 1 | 0 | -107.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4416 | 1 | 0 | 39020.4417 | 1 | 0 | -90.5 | 185.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4418 | 1 | 0 | 39020.4419 | 1 | 0 | -73.5 | 202.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.442 | 1 | 0 | 39020.442 | 1 | 0 | -57 | 219 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4422 | 1 | 0 | 39020.4422 | 1 | 0 | -40.5 | 235.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4424 | 1 | 0 | 39020.4424 | 1 | 0 | -23.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4426 | 1 | 0 | 39020.4426 | 1 | 0 | -6.5 | 269.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4428 | 1 | 0 | 39020.4428 | 1 | 0 | 10.5 | 286.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.443 | 1 | 0 | 39020.443 | 1 | 0 | 27 | 303 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4432 | 0 | 0 | 39020.4432 | 1 | 0 | 44 | 320 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4434 | 0 | 0 | 39020.4434 | 1 | 0 | 60.5 | 336.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4436 | 0 | 0 | 39020.4436 | 1 | 0 | 77.5 | 353.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4438 | 1 | 0 | 39020.4438 | 0 | 0 | 94.5 | 370.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.444 | 1 | 0 | 39020.444 | 1 | 0 | 111 | 387 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4442 | 0 | 0 | 39020.4442 | 1 | 0 | 127.5 | 403.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 422504 | 211202 | 422503.9997
39020.4444 | 1 | 0 | 39020.4444 | 1 | 0 | 144.5 | 420.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4446 | 1 | 0 | 39020.4446 | 1 | 0 | 161.5 | 437.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4448 | 1 | 0 | 39020.4448 | 1 | 0 | 178.5 | 454.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4449 | 1 | 0 | 39020.445 | 1 | 0 | 195 | 471 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4451 | 1 | 0 | 39020.4452 | 1 | 0 | 211.5 | 487.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4453 | 1 | 0 | 39020.4453 | 1 | 0 | 228.5 | 504.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4455 | 1 | 0 | 39020.4455 | 1 | 0 | 245.5 | 521.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4457 | 1 | 0 | 39020.4457 | 1 | 0 | 262 | 538 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4459 | 1 | 0 | 39020.4459 | 1 | 0 | 279 | 555 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4461 | 1 | 0 | 39020.4461 | 0 | 0 | 295.5 | 571.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4463 | 1 | 0 | 39020.4463 | 1 | 0 | 312.5 | 588.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4465 | 1 | 0 | 39020.4465 | 1 | 0 | 329.5 | 605.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4467 | 1 | 0 | 39020.4467 | 1 | 0 | 346 | 622 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4469 | 1 | 0 | 39020.4469 | 1 | 0 | 363 | 639 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4471 | 1 | 0 | 39020.4471 | 1 | 0 | 379.5 | 655.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4473 | 1 | 0 | 39020.4473 | 1 | 0 | 396.5 | 672.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4475 | 1 | 0 | 39020.4475 | 1 | 0 | 413.5 | 689.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4477 | 1 | 0 | 39020.4477 | 1 | 0 | 430 | 706 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4479 | 1 | 0 | 39020.4479 | 1 | 0 | 447 | 723 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4481 | 1 | 0 | 39020.4481 | 1 | 0 | 463.5 | 739.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4483 | 1 | 0 | 39020.4483 | 1 | 0 | 480.5 | 756.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4484 | 1 | 0 | 39020.4485 | 0 | 0 | 497.5 | 773.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4486 | 1 | 0 | 39020.4487 | 1 | 0 | 514 | 790 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4488 | 1 | 0 | 39020.4489 | 1 | 0 | 531 | 807 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.449 | 1 | 0 | 39020.449 | 1 | 0 | 547.5 | 823.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4492 | 1 | 0 | 39020.4492 | 1 | 0 | 564.5 | 840.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4494 | 1 | 0 | 39020.4494 | 1 | 0 | 581.5 | 857.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4496 | 1 | 0 | 39020.4496 | 1 | 0 | 598 | 874 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4498 | 1 | 0 | 39020.4498 | 1 | 0 | 615 | 891 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.45 | 1 | 0 | 39020.45 | 1 | 0 | 631.5 | 907.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4502 | 1 | 0 | 39020.4502 | 1 | 0 | 648.5 | 924.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4504 | 1 | 0 | 39020.4504 | 0 | 0 | 665.5 | 941.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4506 | 1 | 0 | 39020.4506 | 1 | 0 | 682 | 958 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4508 | 1 | 0 | 39020.4508 | 1 | 0 | 699 | 975 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.451 | 1 | 0 | 39020.451 | 1 | 0 | 715.5 | 991.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4512 | 1 | 0 | 39020.4512 | 0 | 0 | 732.5 | 1008.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4514 | 1 | 0 | 39020.4514 | 1 | 0 | 749.5 | 1025.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4516 | 1 | 0 | 39020.4516 | 1 | 0 | 766 | 1042 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4517 | 1 | 0 | 39020.4518 | 1 | 0 | 783 | 1059 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4519 | 1 | 0 | 39020.452 | 1 | 0 | 799.5 | 1075.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4521 | 1 | 0 | 39020.4522 | 1 | 0 | 816.5 | 1092.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4523 | 1 | 0 | 39020.4523 | 1 | 0 | 833.5 | 1109.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4525 | 1 | 0 | 39020.4525 | 1 | 0 | 850 | 1126 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4527 | 1 | 0 | 39020.4527 | 1 | 0 | 867 | 1143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4529 | 1 | 0 | 39020.4529 | 1 | 0 | 883.5 | 1159.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4531 | 1 | 0 | 39020.4531 | 1 | 0 | 900.5 | 1176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4533 | 1 | 0 | 39020.4533 | 1 | 0 | 917.5 | 1193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4535 | 1 | 0 | 39020.4535 | 1 | 0 | 934 | 1210 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4537 | 1 | 0 | 39020.4537 | 1 | 0 | 951 | 1227 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4539 | 1 | 0 | 39020.4539 | 1 | 0 | 967.5 | 1243.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4541 | 1 | 0 | 39020.4541 | 1 | 0 | 984.5 | 1260.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4543 | 1 | 0 | 39020.4543 | 1 | 0 | 1001.5 | 1277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4545 | 1 | 0 | 39020.4545 | 1 | 0 | 1018 | 1294 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4547 | 1 | 0 | 39020.4547 | 1 | 0 | 1035 | 1311 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4549 | 1 | 0 | 39020.4549 | 1 | 0 | 1051.5 | 1327.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4551 | 1 | 0 | 39020.4551 | 1 | 0 | 1068.5 | 1344.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4553 | 1 | 0 | 39020.4553 | 0 | 0 | 1085.5 | 1361.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4554 | 1 | 0 | 39020.4555 | 1 | 0 | 1102 | 1378 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4556 | 1 | 0 | 39020.4557 | 0 | 0 | 1119 | 1395 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4558 | 1 | 0 | 39020.4558 | 1 | 0 | 1135.5 | 1411.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.456 | 1 | 0 | 39020.456 | 1 | 0 | 1152.5 | 1428.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4562 | 1 | 0 | 39020.4562 | 1 | 0 | 1169.5 | 1445.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4564 | 1 | 0 | 39020.4564 | 0 | 0 | 1186 | 1462 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4566 | 1 | 0 | 39020.4566 | 0 | 0 | 1202.5 | 1478.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 211202 | 422504 | 211201.9994
39020.4568 | 1 | 0 | 39020.4568 | 1 | 0 | 1219.5 | 1495.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.457 | 1 | 0 | 39020.457 | 1 | 0 | 1236.5 | 1512.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4572 | 1 | 0 | 39020.4572 | 1 | 0 | 1253.5 | 1529.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4574 | 1 | 0 | 39020.4574 | 1 | 0 | 1270 | 1546 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4576 | 1 | 0 | 39020.4576 | 1 | 0 | 1287 | 1563 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4578 | 1 | 0 | 39020.4578 | 1 | 0 | 1303.5 | 1579.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.458 | 1 | 0 | 39020.458 | 1 | 0 | 1320.5 | 1596.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4582 | 1 | 0 | 39020.4582 | 1 | 0 | 1337.5 | 1613.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4584 | 1 | 0 | 39020.4584 | 1 | 0 | 1354 | 1630 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4586 | 1 | 0 | 39020.4586 | 1 | 0 | 1371 | 1647 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4587 | 1 | 0 | 39020.4588 | 1 | 0 | 1387.5 | 1663.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4589 | 1 | 0 | 39020.459 | 1 | 0 | 1404.5 | 1680.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4591 | 1 | 0 | 39020.4592 | 1 | 0 | 1421 | 1697 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4593 | 1 | 0 | 39020.4594 | 1 | 0 | 1438 | 1714 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4595 | 1 | 0 | 39020.4595 | 1 | 0 | 1455 | 1731 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4597 | 1 | 0 | 39020.4597 | 1 | 0 | 1471.5 | 1747.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4599 | 1 | 0 | 39020.4599 | 1 | 0 | 1488.5 | 1764.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4601 | 1 | 0 | 39020.4601 | 1 | 0 | 1505.5 | 1781.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4603 | 1 | 0 | 39020.4603 | 1 | 0 | 1522 | 1798 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4605 | 1 | 0 | 39020.4605 | 1 | 0 | 1539 | 1815 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4607 | 1 | 0 | 39020.4607 | 1 | 0 | 1555.5 | 1831.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4609 | 1 | 0 | 39020.4609 | 1 | 0 | 1572.5 | 1848.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4611 | 1 | 0 | 39020.4611 | 1 | 0 | 1589 | 1865 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4613 | 1 | 0 | 39020.4613 | 1 | 0 | 1606 | 1882 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4615 | 1 | 0 | 39020.4615 | 1 | 0 | 1622.5 | 1898.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4617 | 1 | 0 | 39020.4617 | 1 | 0 | 1639.5 | 1915.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4619 | 1 | 0 |  | 1 | 0 | 1656 | 1932 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4621 | 1 | 0 | 39020.4621 | 1 | 0 | 1673.5 | 1949.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4622 | 1 | 0 | 39020.4623 | 1 | 0 | 1690 | 1966 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4624 | 1 | 0 | 39020.4625 | 1 | 0 | 1706.5 | 1982.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4626 | 1 | 0 | 39020.4627 | 1 | 0 | 1723.5 | 1999.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4628 | 1 | 0 | 39020.4628 | 1 | 0 | 1740.5 | 2016.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.463 | 1 | 0 | 39020.463 | 1 | 0 | 1757 | 2033 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4632 | 1 | 0 | 39020.4632 | 1 | 0 | 1774 | 2050 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4634 | 1 | 0 | 39020.4634 | 1 | 0 | 1790.5 | 2066.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4636 | 1 | 0 | 39020.4636 | 1 | 0 | 1807.5 | 2083.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4638 | 1 | 0 | 39020.4638 | 1 | 0 | 1824.5 | 2100.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.464 | 1 | 0 | 39020.464 | 1 | 0 | 1841 | 2117 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4642 | 1 | 0 | 39020.4642 | 1 | 0 | 1858 | 2134 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4644 | 1 | 0 | 39020.4644 | 1 | 0 | 1874.5 | 2150.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4646 | 1 | 0 | 39020.4646 | 1 | 0 | 1891.5 | 2167.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4648 | 1 | 0 | 39020.4648 | 1 | 0 | 1908.5 | 2184.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.465 | 1 | 0 | 39020.465 | 1 | 0 | 1925 | 2201 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4652 | 1 | 0 | 39020.4652 | 1 | 0 | 1942 | 2218 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4654 | 1 | 0 | 39020.4654 | 1 | 0 | 1958.5 | 2234.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4656 | 1 | 0 | 39020.4656 | 1 | 0 | 1975.5 | 2251.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994
39020.4658 | 1 | 0 | 39020.4658 | 1 | 0 | 1992.5 | 2268.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 211202 | 211202 | 211201.9994

## Temperatures
DAQ Time | Burner Time | Cable jacket | Air above cable | Air below cable | TRAY G
0 | -276 | 16 | 15.9 | 16 | 17.4
1 | -275 | 16 | 15.9 | 16 | 17.4
2 | -274 | 16 | 15.9 | 16 | 17.4
3 | -273 | 16 | 15.9 | 15.9 | 17.4
4 | -272 | 16 | 15.9 | 16 | 17.4
5 | -271 | 16 | 15.9 | 15.9 | 17.4
6 | -270 | 16 | 15.9 | 15.9 | 17.4
7 | -269 | 16 | 15.9 | 15.9 | 17.4
8 | -268 | 16 | 15.9 | 16 | 17.4
9 | -267 | 16 | 15.9 | 16 | 17.4
10 | -266 | 16 | 15.9 | 16 | 17.4
11 | -265 | 16 | 15.9 | 15.9 | 17.4
12 | -264 | 16 | 15.9 | 16 | 17.4
13 | -263 | 16 | 15.9 | 15.9 | 17.4
14 | -262 | 16 | 15.9 | 16 | 17.4
15 | -261 | 16 | 15.9 | 16 | 17.4
16 | -260 | 16 | 15.9 | 16 | 17.5
17 | -259 | 16 | 15.9 | 16 | 17.4
18 | -258 | 16 | 15.9 | 16 | 17.4
19 | -257 | 16 | 15.9 | 16 | 17.4
20 | -256 | 16 | 15.9 | 16 | 17.4
21 | -255 | 16 | 15.9 | 16 | 17.4
22 | -254 | 16 | 16 | 16 | 17.4
23 | -253 | 16 | 16 | 16 | 17.4
24 | -252 | 16 | 16 | 16 | 17.4
25 | -251 | 16 | 16 | 16 | 17.4
26 | -250 | 16 | 15.9 | 15.9 | 17.4
27 | -249 | 16 | 16 | 16 | 17.4
28 | -248 | 16 | 16 | 16 | 17.4
29 | -247 | 16 | 16 | 16 | 17.4
30 | -246 | 16 | 16 | 16 | 17.4
31 | -245 | 16 | 16 | 16 | 17.4
32 | -244 | 16 | 16 | 16 | 17.4
33 | -243 | 16 | 16 | 15.9 | 17.4
34 | -242 | 16 | 16 | 16 | 17.4
35 | -241 | 16 | 16 | 16 | 17.4
36 | -240 | 16 | 16 | 16 | 17.4
37 | -239 | 16 | 16 | 16 | 17.4
38 | -238 | 16 | 16 | 16 | 17.4
39 | -237 | 16 | 16 | 16 | 17.5
40 | -236 | 16 | 16 | 16 | 17.4
41 | -235 | 16 | 16 | 16 | 17.4
42 | -234 | 16 | 16 | 16 | 17.4
43 | -233 | 16 | 16 | 16 | 17.4
44 | -232 | 16 | 16 | 16 | 17.4
45 | -231 | 16 | 16 | 16 | 17.4
46 | -230 | 16 | 16 | 16 | 17.4
47 | -229 | 16 | 16 | 16 | 17.5
48 | -228 | 16 | 16 | 16 | 17.4
49 | -227 | 16 | 16 | 16 | 17.4
50 | -226 | 16 | 16 | 16 | 17.4
51 | -225 | 16 | 16 | 16 | 17.4
52 | -224 | 16 | 16 | 16 | 17.4
53 | -223 | 16 | 16 | 16 | 17.4
54 | -222 | 16 | 16 | 16 | 17.4
55 | -221 | 16 | 16 | 16 | 17.4
56 | -220 | 16 | 16 | 16 | 17.5
57 | -219 | 16 | 16 | 16 | 17.4
58 | -218 | 16 | 16 | 16 | 17.4
59 | -217 | 16 | 16 | 16 | 17.4
60 | -216 | 16 | 16 | 16 | 17.4
61 | -215 | 16 | 16 | 16 | 17.4
62 | -214 | 16 | 16 | 16 | 17.4
63 | -213 | 16 | 16 | 16 | 17.5
64 | -212 | 16 | 16 | 16 | 17.4
65 | -211 | 16 | 16 | 16 | 17.4
66 | -210 | 16 | 16 | 16 | 17.4
67 | -209 | 16 | 16 | 16 | 17.4
68 | -208 | 16 | 16 | 16 | 17.4
69 | -207 | 16 | 16 | 16 | 17.4
70 | -206 | 16 | 16 | 16 | 17.4
71 | -205 | 16 | 16 | 16 | 17.4
72 | -204 | 16 | 16 | 16 | 17.5
73 | -203 | 16 | 16 | 16 | 17.4
74 | -202 | 16 | 16 | 16 | 17.4
75 | -201 | 16 | 16 | 16 | 17.4
76 | -200 | 16 | 16 | 16 | 17.4
77 | -199 | 16 | 16 | 16 | 17.4
78 | -198 | 16 | 16 | 16 | 17.5
79 | -197 | 16 | 16 | 16 | 17.4
80 | -196 | 16 | 16 | 16 | 17.4
81 | -195 | 16 | 16 | 16 | 17.4
82 | -194 | 16 | 16 | 16 | 17.4
83 | -193 | 16 | 16 | 16 | 17.4
84 | -192 | 16 | 16 | 16 | 17.4
85 | -191 | 16 | 16 | 16 | 17.4
86 | -190 | 16 | 16 | 16 | 17.4
87 | -189 | 16 | 16 | 16 | 17.4
88 | -188 | 16 | 16 | 16 | 17.4
89 | -187 | 16 | 16 | 16 | 17.4
90 | -186 | 16 | 16 | 16 | 17.4
91 | -185 | 16 | 16 | 16 | 17.4
92 | -184 | 16 | 16 | 16 | 17.4
93 | -183 | 16 | 16 | 16 | 17.4
94 | -182 | 16 | 16 | 16 | 17.4
95 | -181 | 16 | 16 | 16 | 17.4
96 | -180 | 16 | 16 | 16 | 17.4
97 | -179 | 16 | 16 | 16 | 17.4
98 | -178 | 16 | 16 | 16 | 17.4
99 | -177 | 16 | 16 | 16 | 17.4
100 | -176 | 16 | 16 | 16 | 17.4
101 | -175 | 16 | 16 | 16 | 17.4
102 | -174 | 16 | 16 | 16 | 17.5
103 | -173 | 16 | 16 | 16 | 17.4
104 | -172 | 16 | 16 | 16 | 17.4
105 | -171 | 16 | 16 | 16 | 17.4
106 | -170 | 16 | 16 | 16 | 17.4
107 | -169 | 16 | 16 | 16 | 17.4
108 | -168 | 16 | 16 | 16 | 17.4
109 | -167 | 16 | 16 | 16 | 17.4
110 | -166 | 16 | 16 | 16 | 17.4
111 | -165 | 16 | 16 | 16 | 17.4
112 | -164 | 16 | 15.9 | 16 | 17.4
113 | -163 | 16 | 16 | 16 | 17.4
114 | -162 | 16 | 16 | 16 | 17.4
115 | -161 | 16 | 15.9 | 16 | 17.4
116 | -160 | 16 | 15.9 | 16 | 17.4
117 | -159 | 16 | 15.9 | 16 | 17.4
118 | -158 | 16 | 15.9 | 16 | 17.4
119 | -157 | 16 | 15.9 | 15.9 | 17.4
120 | -156 | 16 | 15.9 | 16 | 17.4
121 | -155 | 16 | 15.9 | 15.9 | 17.4
122 | -154 | 16 | 15.9 | 16 | 17.5
123 | -153 | 16 | 15.9 | 15.9 | 17.4
124 | -152 | 16 | 15.9 | 16 | 17.4
125 | -151 | 16 | 15.9 | 15.9 | 17.4
126 | -150 | 16 | 15.9 | 16 | 17.4
127 | -149 | 16 | 15.9 | 16 | 17.4
128 | -148 | 16 | 15.9 | 16 | 17.4
129 | -147 | 16 | 15.9 | 16 | 17.4
130 | -146 | 16 | 15.9 | 16 | 17.4
131 | -145 | 16 | 15.9 | 15.9 | 17.4
132 | -144 | 16 | 15.9 | 16 | 17.4
133 | -143 | 16 | 15.9 | 15.9 | 17.4
134 | -142 | 16 | 15.9 | 15.9 | 17.4
135 | -141 | 16 | 15.9 | 16 | 17.4
136 | -140 | 16 | 15.9 | 15.9 | 17.4
137 | -139 | 16 | 15.9 | 15.9 | 17.4
138 | -138 | 16 | 15.9 | 16 | 17.4
139 | -137 | 16 | 15.9 | 15.9 | 17.4
140 | -136 | 16 | 15.9 | 15.9 | 17.4
141 | -135 | 16 | 15.9 | 15.9 | 17.4
142 | -134 | 16 | 15.9 | 15.9 | 17.4
143 | -133 | 16 | 15.9 | 15.9 | 17.4
144 | -132 | 16 | 15.9 | 15.9 | 17.4
145 | -131 | 16 | 15.9 | 15.9 | 17.4
146 | -130 | 16 | 15.9 | 15.9 | 17.4
147 | -129 | 16 | 15.9 | 15.9 | 17.4
148 | -128 | 16 | 15.9 | 15.9 | 17.5
149 | -127 | 16 | 15.9 | 15.9 | 17.4
150 | -126 | 16 | 15.9 | 15.9 | 17.4
151 | -125 | 16 | 15.9 | 15.9 | 17.4
152 | -124 | 16 | 15.9 | 15.9 | 17.4
153 | -123 | 16 | 15.9 | 15.9 | 17.4
154 | -122 | 16 | 15.9 | 15.9 | 17.4
155 | -121 | 16 | 15.9 | 15.9 | 17.4
156 | -120 | 16 | 15.9 | 15.9 | 17.4
157 | -119 | 16 | 15.9 | 15.9 | 17.4
158 | -118 | 16 | 15.9 | 15.9 | 17.4
159 | -117 | 16 | 15.9 | 15.9 | 17.5
160 | -116 | 16 | 15.9 | 15.9 | 17.4
161 | -115 | 16 | 15.9 | 15.9 | 17.4
162 | -114 | 16 | 15.9 | 15.9 | 17.4
163 | -113 | 16 | 15.9 | 15.9 | 17.4
164 | -112 | 16 | 15.9 | 15.9 | 17.4
165 | -111 | 16 | 15.9 | 15.9 | 17.4
166 | -110 | 16 | 15.9 | 15.9 | 17.4
167 | -109 | 16 | 15.9 | 15.9 | 17.4
168 | -108 | 16 | 15.9 | 15.9 | 17.4
169 | -107 | 16 | 15.9 | 15.9 | 17.4
170 | -106 | 16 | 15.9 | 15.9 | 17.4
171 | -105 | 16 | 15.9 | 15.9 | 17.4
172 | -104 | 16 | 15.9 | 15.9 | 17.4
173 | -103 | 16 | 15.9 | 15.9 | 17.4
174 | -102 | 16 | 15.9 | 15.9 | 17.4
175 | -101 | 16 | 15.9 | 15.9 | 17.4
176 | -100 | 16 | 15.9 | 15.9 | 17.4
177 | -99 | 16 | 15.9 | 15.9 | 17.4
178 | -98 | 16 | 15.9 | 15.9 | 17.4
179 | -97 | 16 | 15.9 | 15.9 | 17.4
180 | -96 | 16 | 15.9 | 15.9 | 17.4
181 | -95 | 16 | 15.9 | 15.9 | 17.4
182 | -94 | 16 | 15.9 | 15.9 | 17.4
183 | -93 | 16 | 15.9 | 15.9 | 17.4
184 | -92 | 16 | 15.9 | 15.9 | 17.4
185 | -91 | 16 | 15.9 | 15.9 | 17.4
186 | -90 | 16 | 15.9 | 15.9 | 17.4
187 | -89 | 16 | 15.9 | 15.9 | 17.4
188 | -88 | 16 | 15.9 | 15.9 | 17.4
189 | -87 | 16 | 15.9 | 15.9 | 17.4
190 | -86 | 16 | 15.9 | 15.9 | 17.4
191 | -85 | 16 | 15.9 | 15.9 | 17.4
192 | -84 | 16 | 15.9 | 15.9 | 17.4
193 | -83 | 16 | 15.9 | 15.9 | 17.4
194 | -82 | 16 | 15.9 | 15.9 | 17.4
195 | -81 | 16 | 15.9 | 15.9 | 17.4
196 | -80 | 16 | 15.9 | 15.9 | 17.4
197 | -79 | 16 | 15.9 | 15.9 | 17.4
198 | -78 | 16 | 15.9 | 15.9 | 17.4
199 | -77 | 16 | 15.9 | 15.9 | 17.4
200 | -76 | 16 | 15.9 | 15.9 | 17.4
201 | -75 | 16 | 15.9 | 15.9 | 17.4
202 | -74 | 16 | 15.9 | 15.9 | 17.4
203 | -73 | 16 | 15.9 | 15.9 | 17.4
204 | -72 | 16 | 15.9 | 15.9 | 17.4
205 | -71 | 16 | 15.9 | 15.9 | 17.4
206 | -70 | 16 | 15.9 | 15.9 | 17.4
207 | -69 | 16 | 15.9 | 15.9 | 17.4
208 | -68 | 16 | 15.9 | 15.9 | 17.4
209 | -67 | 16 | 15.9 | 15.9 | 17.4
210 | -66 | 16 | 15.9 | 15.9 | 17.4
211 | -65 | 16 | 15.9 | 15.9 | 17.4
212 | -64 | 16 | 15.9 | 15.9 | 17.4
213 | -63 | 16 | 15.9 | 15.9 | 17.4
214 | -62 | 16 | 15.9 | 15.9 | 17.4
215 | -61 | 16 | 15.9 | 15.9 | 17.4
216 | -60 | 16 | 15.9 | 15.9 | 17.4
217 | -59 | 16 | 15.9 | 15.9 | 17.4
218 | -58 | 16 | 15.9 | 15.9 | 17.4
219 | -57 | 16 | 15.9 | 15.9 | 17.4
220 | -56 | 16 | 15.9 | 15.9 | 17.4
221 | -55 | 16 | 15.9 | 15.9 | 17.4
222 | -54 | 16 | 15.9 | 15.9 | 17.4
223 | -53 | 16 | 15.9 | 15.9 | 17.4
224 | -52 | 16 | 15.9 | 15.9 | 17.4
225 | -51 | 16 | 15.9 | 15.9 | 17.4
226 | -50 | 16 | 15.9 | 15.9 | 17.4
227 | -49 | 16 | 15.9 | 15.9 | 17.4
228 | -48 | 16 | 15.9 | 15.9 | 17.4
229 | -47 | 16 | 15.9 | 15.9 | 17.4
230 | -46 | 16 | 15.9 | 15.9 | 17.4
231 | -45 | 16 | 15.9 | 15.9 | 17.4
232 | -44 | 16 | 15.9 | 15.9 | 17.4
233 | -43 | 16 | 15.9 | 15.9 | 17.4
234 | -42 | 16 | 15.9 | 15.9 | 17.4
235 | -41 | 16 | 15.9 | 15.9 | 17.4
236 | -40 | 16 | 15.9 | 15.9 | 17.4
237 | -39 | 16 | 15.9 | 15.9 | 17.4
238 | -38 | 16 | 15.9 | 15.9 | 17.4
239 | -37 | 16 | 15.9 | 15.9 | 17.4
240 | -36 | 16 | 15.9 | 15.9 | 17.4
241 | -35 | 16 | 15.9 | 15.9 | 17.4
242 | -34 | 16 | 15.9 | 15.9 | 17.4
243 | -33 | 16 | 15.9 | 15.9 | 17.4
244 | -32 | 16 | 15.9 | 15.9 | 17.4
245 | -31 | 16 | 15.9 | 15.9 | 17.4
246 | -30 | 16 | 15.9 | 15.9 | 17.4
247 | -29 | 16 | 15.9 | 15.9 | 17.4
248 | -28 | 16 | 15.9 | 15.9 | 17.4
249 | -27 | 16 | 15.9 | 15.9 | 17.4
250 | -26 | 16 | 15.9 | 15.9 | 17.4
251 | -25 | 16 | 15.9 | 15.9 | 17.4
252 | -24 | 16 | 15.9 | 15.9 | 17.4
253 | -23 | 16 | 15.9 | 15.9 | 17.4
254 | -22 | 15.9 | 15.9 | 15.9 | 17.4
255 | -21 | 16 | 15.9 | 15.9 | 17.4
256 | -20 | 15.9 | 15.9 | 15.9 | 17.4
257 | -19 | 15.9 | 15.9 | 15.9 | 17.4
258 | -18 | 16 | 15.9 | 15.9 | 17.4
259 | -17 | 15.9 | 15.9 | 15.9 | 17.4
260 | -16 | 16 | 15.9 | 15.9 | 17.4
261 | -15 | 15.9 | 15.9 | 15.9 | 17.4
262 | -14 | 16 | 15.9 | 15.9 | 17.4
263 | -13 | 15.9 | 15.9 | 15.9 | 17.4
264 | -12 | 16 | 15.9 | 15.9 | 17.4
265 | -11 | 16 | 15.9 | 15.9 | 17.4
266 | -10 | 16 | 15.9 | 15.9 | 17.4
267 | -9 | 16 | 15.9 | 15.9 | 17.4
268 | -8 | 16 | 15.9 | 16 | 17.4
269 | -7 | 16 | 15.9 | 15.9 | 17.4
270 | -6 | 16 | 15.9 | 15.9 | 17.4
271 | -5 | 16 | 15.9 | 15.9 | 17.4
272 | -4 | 16 | 15.9 | 15.9 | 17.4
273 | -3 | 16 | 15.9 | 15.9 | 17.4
274 | -2 | 16 | 15.9 | 15.9 | 17.4
275 | -1 | 16 | 15.9 | 15.9 | 17.4
276 | 0 | 16 | 15.9 | 15.9 | 17.4
277 | 1 | 15.9 | 15.9 | 15.9 | 17.4
278 | 2 | 16 | 15.9 | 15.9 | 17.4
279 | 3 | 15.9 | 15.9 | 15.9 | 17.4
280 | 4 | 15.9 | 15.9 | 15.9 | 17.4
281 | 5 | 16 | 15.9 | 15.9 | 17.5
282 | 6 | 15.9 | 16 | 16 | 17.5
283 | 7 | 15.9 | 16.1 | 16 | 17.6
284 | 8 | 16 | 16.2 | 16.2 | 17.7
285 | 9 | 15.9 | 16.3 | 16.3 | 17.8
286 | 10 | 16 | 16.5 | 16.4 | 17.9
287 | 11 | 16 | 16.8 | 16.6 | 18.1
288 | 12 | 16 | 17.4 | 18.2 | 18.3
289 | 13 | 16 | 19.4 | 21.4 | 18.5
290 | 14 | 16 | 22.7 | 28.8 | 18.9
291 | 15 | 16.1 | 25.8 | 31.6 | 19.3
292 | 16 | 16.2 | 27.8 | 36.4 | 19.7
293 | 17 | 16.3 | 30.5 | 40.8 | 20.1
294 | 18 | 16.4 | 34.4 | 43.3 | 20.5
295 | 19 | 16.6 | 37.2 | 47.6 | 21.2
296 | 20 | 16.8 | 39.5 | 51.2 | 21.7
297 | 21 | 17.1 | 41.3 | 54.1 | 22
298 | 22 | 17.3 | 43.7 | 57.2 | 22.4
299 | 23 | 17.6 | 46.9 | 60 | 22.9
300 | 24 | 17.9 | 49.6 | 63.6 | 23.4
301 | 25 | 18.3 | 52.3 | 69.6 | 24
302 | 26 | 18.7 | 56.2 | 73.3 | 24.7
303 | 27 | 19 | 59.6 | 76.3 | 25.5
304 | 28 | 19.4 | 62.9 | 78.5 | 25.9
305 | 29 | 19.8 | 65.9 | 82.4 | 26.6
306 | 30 | 20.2 | 68.8 | 89.2 | 27.2
307 | 31 | 20.6 | 70.5 | 93 | 27.9
308 | 32 | 21 | 72.8 | 98.2 | 28.3
309 | 33 | 21.5 | 75.4 | 101.6 | 28.9
310 | 34 | 22 | 77.7 | 104.1 | 29.5
311 | 35 | 22.5 | 80.3 | 107.6 | 30.2
312 | 36 | 23 | 84 | 111.4 | 31
313 | 37 | 23.5 | 87.4 | 113 | 31.7
314 | 38 | 24.1 | 89.6 | 115.2 | 32.2
315 | 39 | 24.6 | 92.4 | 117.7 | 32.9
316 | 40 | 25.1 | 94.6 | 120.6 | 33.6
317 | 41 | 25.7 | 96.9 | 123 | 34.3
318 | 42 | 26.2 | 99.3 | 125.6 | 35.1
319 | 43 | 26.8 | 102.1 | 128 | 35.7
320 | 44 | 27.3 | 104.6 | 131 | 36.4
321 | 45 | 27.9 | 107.4 | 133.4 | 37.2
322 | 46 | 28.5 | 109.3 | 135.4 | 37.8
323 | 47 | 29.1 | 111.1 | 137.7 | 38.4
324 | 48 | 29.7 | 112.7 | 140.1 | 39
325 | 49 | 30.3 | 114.6 | 142.2 | 39.9
326 | 50 | 30.9 | 117 | 145.2 | 40.5
327 | 51 | 31.5 | 120.2 | 147.5 | 41.3
328 | 52 | 32.2 | 123 | 150 | 42.2
329 | 53 | 32.8 | 124.6 | 153 | 42.9
330 | 54 | 33.5 | 127.1 | 154.5 | 43.7
331 | 55 | 34.1 | 128.8 | 156.6 | 44.1
332 | 56 | 34.8 | 131.1 | 159 | 44.7
333 | 57 | 35.5 | 132.4 | 161.1 | 45.5
334 | 58 | 36.2 | 134.6 | 162.8 | 46.3
335 | 59 | 36.8 | 136 | 164.4 | 47.1
336 | 60 | 37.5 | 137.7 | 166.4 | 47.9
337 | 61 | 38.2 | 140 | 167.8 | 48.7
338 | 62 | 38.9 | 141.3 | 169.1 | 49.6
339 | 63 | 39.6 | 142.4 | 170.3 | 50.2
340 | 64 | 40.3 | 143.5 | 171.5 | 50.9
341 | 65 | 41 | 144.6 | 172.6 | 51.5
342 | 66 | 41.7 | 146.3 | 173.6 | 52.2
343 | 67 | 42.4 | 147.3 | 174.6 | 53
344 | 68 | 43.1 | 148.7 | 175.7 | 53.6
345 | 69 | 43.7 | 150.2 | 177 | 54.3
346 | 70 | 44.4 | 152.1 | 177.8 | 54.9
347 | 71 | 45 | 153.8 | 178.5 | 55.5
348 | 72 | 45.7 | 154.4 | 179.5 | 56.1
349 | 73 | 46.3 | 155.2 | 180.4 | 56.7
350 | 74 | 46.9 | 156 | 181.4 | 57.2
351 | 75 | 47.5 | 156.8 | 182.2 | 58.1
352 | 76 | 48.1 | 157.6 | 183 | 58.7
353 | 77 | 48.7 | 158.4 | 183.6 | 59.4
354 | 78 | 49.3 | 159.5 | 184.2 | 60
355 | 79 | 49.9 | 160.4 | 185 | 60.7
356 | 80 | 50.4 | 162 | 185.7 | 61.2
357 | 81 | 51 | 163.8 | 186 | 61.8
358 | 82 | 51.6 | 164.4 | 186.4 | 62.3
359 | 83 | 52.1 | 165.4 | 186.7 | 62.9
360 | 84 | 52.7 | 166 | 187.2 | 63.5
361 | 85 | 53.2 | 167.3 | 187.9 | 63.9
362 | 86 | 53.8 | 168.9 | 188.7 | 64.5
363.1 | 87.1 | 54.4 | 169.9 | 189.4 | 65.1
364.1 | 88.1 | 54.9 | 170.7 | 190.3 | 65.8
365.1 | 89.1 | 55.5 | 171.9 | 190.8 | 66.5
366.1 | 90.1 | 56.1 | 172.7 | 191.3 | 67.2
367.1 | 91.1 | 56.7 | 173.3 | 191.3 | 67.6
368.1 | 92.1 | 57.3 | 174.4 | 191 | 68.2
369.1 | 93.1 | 57.8 | 175.2 | 192.1 | 68.8
370.1 | 94.1 | 58.4 | 176.1 | 193.2 | 69.4
371.1 | 95.1 | 58.9 | 176.8 | 193.4 | 70.1
372.1 | 96.1 | 59.5 | 176.6 | 194.1 | 70.8
373.1 | 97.1 | 60 | 176.8 | 194.8 | 71.3
374.1 | 98.1 | 60.6 | 177.3 | 195.7 | 72
375.1 | 99.1 | 61.1 | 178.2 | 196.6 | 72.6
376.1 | 100.1 | 61.7 | 179.4 | 198.1 | 73.2
377.1 | 101.1 | 62.3 | 180.1 | 198.7 | 73.9
378.1 | 102.1 | 62.9 | 180.3 | 199.4 | 74.5
379.1 | 103.1 | 63.5 | 180.9 | 200 | 75.3
380.1 | 104.1 | 64 | 182 | 200.6 | 75.8
381.1 | 105.1 | 64.6 | 182.5 | 201.4 | 76.4
382.1 | 106.1 | 65.2 | 183.3 | 202.1 | 77.2
383.1 | 107.1 | 65.8 | 184.2 | 203 | 77.9
384.1 | 108.1 | 66.4 | 185.2 | 203.5 | 78.4
385.1 | 109.1 | 67 | 186 | 203.9 | 79.1
386.1 | 110.1 | 67.6 | 186.9 | 204.9 | 79.7
387.1 | 111.1 | 68.2 | 187.4 | 205.6 | 80.3
388.1 | 112.1 | 68.8 | 188.1 | 206.4 | 81
389.1 | 113.1 | 69.4 | 188.8 | 207 | 81.6
390.1 | 114.1 | 70 | 189.2 | 207.6 | 82.2
391.1 | 115.1 | 70.6 | 189.4 | 208.2 | 83
392.1 | 116.1 | 71.2 | 190.3 | 208.6 | 83.6
393.1 | 117.1 | 71.7 | 190.9 | 209.4 | 84.2
394.1 | 118.1 | 72.3 | 190.9 | 210.4 | 84.8
395.1 | 119.1 | 72.8 | 191.2 | 211.4 | 85.6
396.1 | 120.1 | 73.4 | 191.6 | 212.2 | 86.2
397.1 | 121.1 | 74 | 192.6 | 212.7 | 87
398.1 | 122.1 | 74.5 | 193.7 | 213.4 | 87.6
399.1 | 123.1 | 75.1 | 195 | 214.2 | 88.2
400.1 | 124.1 | 75.7 | 195.9 | 215.4 | 88.8
401.1 | 125.1 | 76.2 | 197.1 | 215.9 | 89.7
402.1 | 126.1 | 76.8 | 197.6 | 216.3 | 90.4
403.1 | 127.1 | 77.4 | 198 | 216.7 | 91.1
404.1 | 128.1 | 77.9 | 198 | 216.8 | 91.6
405.1 | 129.1 | 78.5 | 198.3 | 217.3 | 92.2
406.1 | 130.1 | 79 | 198.7 | 217.5 | 92.9
407.1 | 131.1 | 79.6 | 198.9 | 217.5 | 93.5
408.1 | 132.1 | 80.2 | 199 | 217.4 | 94.2
409.1 | 133.1 | 80.8 | 199.3 | 217.5 | 94.9
410.1 | 134.1 | 81.3 | 199.6 | 217.6 | 95.5
411.1 | 135.1 | 81.9 | 200.1 | 218 | 96.2
412.1 | 136.1 | 82.5 | 200.6 | 218.3 | 97
413.1 | 137.1 | 83 | 200.9 | 219 | 97.6
414.1 | 138.1 | 83.6 | 201.3 | 219.1 | 98.1
415.1 | 139.1 | 84.1 | 201.4 | 219.6 | 98.8
416.1 | 140.1 | 84.7 | 201.7 | 220.3 | 99.5
417.1 | 141.1 | 85.2 | 202 | 221.5 | 100.1
418.1 | 142.1 | 85.7 | 202.6 | 222.4 | 100.9
419.1 | 143.1 | 86.3 | 202.6 | 222.8 | 101.5
420.1 | 144.1 | 86.8 | 203.3 | 222.8 | 102.1
421.1 | 145.1 | 87.3 | 203.8 | 222.8 | 102.9
422.1 | 146.1 | 87.9 | 204.6 | 222.8 | 103.5
423.1 | 147.1 | 88.4 | 205 | 223.7 | 104.1
424.1 | 148.1 | 89 | 205.1 | 224.4 | 104.7
425.1 | 149.1 | 89.5 | 205.3 | 225.1 | 105.3
426.1 | 150.1 | 90 | 205.8 | 225.8 | 106
427.1 | 151.1 | 90.5 | 206.4 | 226.4 | 106.6
428.1 | 152.1 | 91.1 | 206.8 | 226.6 | 107.2
429.1 | 153.1 | 91.6 | 207.3 | 227 | 107.9
430.1 | 154.1 | 92.1 | 207.9 | 227.5 | 108.5
431.1 | 155.1 | 92.7 | 209.1 | 227.9 | 109.3
432.1 | 156.1 | 93.2 | 209.3 | 228.6 | 109.9
433.1 | 157.1 | 93.8 | 209.4 | 229.1 | 110.6
434.1 | 158.1 | 94.3 | 210.1 | 229.6 | 111.2
435.1 | 159.1 | 94.9 | 210.7 | 230.2 | 111.9
436.1 | 160.1 | 95.4 | 211.1 | 230.3 | 112.4
437.1 | 161.1 | 95.9 | 211.1 | 230.6 | 113
438.1 | 162.1 | 96.5 | 211.6 | 230.9 | 113.6
439.1 | 163.1 | 97 | 212.1 | 231.1 | 114.4
440.1 | 164.1 | 97.5 | 212.2 | 231.9 | 115.1
441.1 | 165.1 | 98 | 212.7 | 232.4 | 115.6
442.1 | 166.1 | 98.5 | 213 | 233 | 116.2
443.1 | 167.1 | 99.1 | 213.4 | 233.4 | 116.9
444.1 | 168.1 | 99.6 | 213.6 | 233.7 | 117.3
445.1 | 169.1 | 100.1 | 213.6 | 233.7 | 117.9
446.1 | 170.1 | 100.6 | 213.8 | 233.5 | 118.4
447.1 | 171.1 | 101.1 | 214.1 | 233.5 | 119.1
448.1 | 172.1 | 101.6 | 214.3 | 233.9 | 119.6
449.1 | 173.1 | 102.1 | 214.5 | 233.9 | 120.1
450.1 | 174.1 | 102.6 | 214.7 | 234.1 | 120.5
451.1 | 175.1 | 103.1 | 215.1 | 235.1 | 121
452.1 | 176.1 | 103.5 | 215.9 | 235.7 | 121.7
453.1 | 177.1 | 104 | 216.5 | 236.1 | 122.4
454.1 | 178.1 | 104.5 | 216.8 | 236.7 | 122.9
455.1 | 179.1 | 105 | 217.3 | 237.3 | 123.5
456.1 | 180.1 | 105.5 | 217.9 | 237.5 | 124.2
457.1 | 181.1 | 106 | 218.3 | 237.8 | 124.7
458.1 | 182.1 | 106.5 | 218.8 | 238.1 | 125.3
459.1 | 183.1 | 107.1 | 218.8 | 238.1 | 125.8
460.1 | 184.1 | 107.6 | 219.1 | 237.9 | 126.5
461.1 | 185.1 | 108.1 | 219.6 | 237.9 | 127.1
462.1 | 186.1 | 108.6 | 220.2 | 237.7 | 127.8
463.1 | 187.1 | 109.1 | 220.3 | 237.5 | 128.4
464.1 | 188.1 | 109.6 | 220.4 | 237.7 | 129
465.1 | 189.1 | 110.1 | 220.5 | 237.9 | 129.4
466.1 | 190.1 | 110.5 | 220.7 | 238 | 130
467.1 | 191.1 | 110.9 | 221 | 238.1 | 130.6
468.1 | 192.1 | 111.4 | 221.6 | 238 | 131.2
469.1 | 193.1 | 111.8 | 222 | 237.6 | 131.9
470.1 | 194.1 | 112.2 | 222 | 237.3 | 132.5
471.1 | 195.1 | 112.7 | 222.2 | 237.1 | 133
472.1 | 196.1 | 113.1 | 222.4 | 236.8 | 133.5
473.1 | 197.1 | 113.5 | 222.5 | 236.8 | 134
474.1 | 198.1 | 113.9 | 222.6 | 236.8 | 134.5
475.1 | 199.1 | 114.3 | 222.7 | 236.7 | 135.1
476.1 | 200.1 | 114.6 | 222.8 | 236.9 | 135.7
477.1 | 201.1 | 115 | 222.9 | 237 | 136.1
478.1 | 202.1 | 115.4 | 223 | 237.2 | 136.7
479.1 | 203.1 | 115.8 | 222.9 | 237.3 | 137.2
480.1 | 204.1 | 116.2 | 223 | 237.4 | 137.8
481.1 | 205.1 | 116.6 | 223.7 | 237.3 | 138.4
482.1 | 206.1 | 116.9 | 223.9 | 237.5 | 138.9
483.1 | 207.1 | 117.3 | 224.2 | 237.6 | 139.4
484.1 | 208.1 | 117.7 | 224.4 | 237.6 | 140.1
485.1 | 209.1 | 118.1 | 224.5 | 238.7 | 140.7
486.1 | 210.1 | 118.5 | 224.7 | 239.3 | 141.2
487.1 | 211.1 | 118.9 | 224.6 | 239.2 | 141.8
488.1 | 212.1 | 119.3 | 224.5 | 239 | 142.3
489.1 | 213.1 | 119.7 | 224.6 | 238.8 | 142.8
490.1 | 214.1 | 120.1 | 225.6 | 238.7 | 143.5
491.1 | 215.1 | 120.5 | 226.1 | 238.4 | 144
492.1 | 216.1 | 120.9 | 226.7 | 238.5 | 144.5
493.1 | 217.1 | 121.2 | 226.8 | 238.7 | 145
494.1 | 218.1 | 121.6 | 227.5 | 239.1 | 145.7
495.1 | 219.1 | 121.9 | 228.3 | 239.2 | 146.4
496.1 | 220.1 | 122.3 | 228.2 | 239.6 | 146.9
497.1 | 221.1 | 122.6 | 229 | 240.7 | 147.5
498.1 | 222.1 | 123 | 230.3 | 241.4 | 147.9
499.1 | 223.1 | 123.3 | 230.7 | 241.8 | 148.3
500.1 | 224.1 | 123.7 | 230.7 | 242.3 | 148.8
501.1 | 225.1 | 124 | 231.1 | 242.7 | 149.4
502.1 | 226.1 | 124.4 | 231.6 | 243.1 | 150.1
503.1 | 227.1 | 124.8 | 231.9 | 243.4 | 150.5
504.1 | 228.1 | 125.2 | 232.3 | 244.1 | 151
505.1 | 229.1 | 125.6 | 232.6 | 244.4 | 151.6
506.1 | 230.1 | 126 | 232.8 | 244.6 | 152.3
507.1 | 231.1 | 126.4 | 233 | 245 | 152.8
508.1 | 232.1 | 126.8 | 232.9 | 245.4 | 153.4
509.1 | 233.1 | 127.2 | 233.3 | 245.9 | 153.8
510.1 | 234.1 | 127.6 | 233.5 | 246.5 | 154.3
511.1 | 235.1 | 128 | 234.1 | 247.3 | 154.8
512.1 | 236.1 | 128.4 | 235.2 | 247.6 | 155.4
513.1 | 237.1 | 128.8 | 235.9 | 247.6 | 156
514.1 | 238.1 | 129.3 | 236.2 | 247.8 | 156.4
515.1 | 239.1 | 129.7 | 236.3 | 247.8 | 156.9
516.1 | 240.1 | 130.1 | 236.5 | 247.7 | 157.4
517.1 | 241.1 | 130.5 | 237.2 | 247.4 | 157.9
518.1 | 242.1 | 130.9 | 237.7 | 247.6 | 158.4
519.1 | 243.1 | 131.3 | 238.7 | 247.6 | 159
520.1 | 244.1 | 131.7 | 239.2 | 247.8 | 159.6
521.1 | 245.1 | 132 | 239.4 | 247.9 | 160.1
522.1 | 246.1 | 132.4 | 239.8 | 248.2 | 160.5
523.1 | 247.1 | 132.8 | 240.5 | 248.6 | 161.2
524.1 | 248.1 | 133.1 | 241.3 | 249.5 | 161.8
525.1 | 249.1 | 133.5 | 241.9 | 249.7 | 162.4
526.1 | 250.1 | 133.8 | 242.4 | 250 | 163
527.1 | 251.1 | 134.2 | 242.4 | 250 | 163.4
528.1 | 252.1 | 134.5 | 243.1 | 250.1 | 163.8
529.1 | 253.1 | 134.9 | 243.9 | 250 | 164.4
530.1 | 254.1 | 135.3 | 243.9 | 250.6 | 164.9
531.1 | 255.1 | 135.6 | 244.1 | 251.4 | 165.3
532.1 | 256.1 | 136 | 244.5 | 252.1 | 166
533.1 | 257.1 | 136.4 | 244.8 | 252.3 | 166.7
534.1 | 258.1 | 136.8 | 245.3 | 252.3 | 167.2
535.1 | 259.1 | 137.1 | 246 | 252.2 | 167.8
536.1 | 260.1 | 137.5 | 245.8 | 252.5 | 168.2
537.1 | 261.1 | 137.9 | 245.6 | 253 | 168.7
538.1 | 262.1 | 138.3 | 246.3 | 253.6 | 169.4
539.1 | 263.1 | 138.6 | 247.1 | 254.3 | 169.9
540.1 | 264.1 | 139 | 247.6 | 255.1 | 170.4
541.1 | 265.1 | 139.4 | 248.4 | 256 | 171
542.1 | 266.1 | 139.8 | 248.8 | 257.1 | 171.5
543.1 | 267.1 | 140.2 | 249.2 | 258.1 | 172.1
544.1 | 268.1 | 140.5 | 249.8 | 258.9 | 172.8
545.1 | 269.1 | 140.9 | 250.2 | 260 | 173.3
546.1 | 270.1 | 141.3 | 251 | 260.7 | 173.8
547.1 | 271.1 | 141.7 | 251.9 | 261.2 | 174.4
548.1 | 272.1 | 142.2 | 252.1 | 261.8 | 174.9
549.1 | 273.1 | 142.6 | 252.3 | 262.4 | 175.3
550.1 | 274.1 | 143 | 252.4 | 262.7 | 175.8
551.1 | 275.1 | 143.4 | 252.9 | 263.2 | 176.4
552.1 | 276.1 | 143.8 | 253.7 | 263.7 | 177
553.1 | 277.1 | 144.2 | 253.9 | 264.1 | 177.6
554.1 | 278.1 | 144.6 | 254.2 | 264.5 | 178
555.1 | 279.1 | 145 | 254.4 | 265 | 178.4
556.1 | 280.1 | 145.4 | 255.4 | 265.5 | 178.9
557.1 | 281.1 | 145.9 | 255.7 | 265.7 | 179.4
558.1 | 282.1 | 146.3 | 255.8 | 265.9 | 179.9
559.1 | 283.1 | 146.7 | 256 | 266.2 | 180.4
560.1 | 284.1 | 147.1 | 256.2 | 266.5 | 180.8
561.1 | 285.1 | 147.5 | 256.1 | 266.3 | 181.2
562.1 | 286.1 | 147.9 | 256 | 266.6 | 181.7
563.1 | 287.1 | 148.2 | 256.2 | 266.7 | 182.4
564.1 | 288.1 | 148.6 | 256.4 | 267.1 | 182.8
565.1 | 289.1 | 149 | 256.6 | 267.4 | 183.3
566.1 | 290.1 | 149.4 | 256.7 | 267.7 | 183.7
567.1 | 291.1 | 149.8 | 257 | 268.3 | 184.2
568.1 | 292.1 | 150.1 | 257.1 | 268.5 | 184.7
569.1 | 293.1 | 150.5 | 256.8 | 268.5 | 185.1
570.1 | 294.1 | 150.9 | 256.9 | 268.2 | 185.7
571.1 | 295.1 | 151.3 | 257.4 | 267.9 | 186.2
572.1 | 296.1 | 151.7 | 257.7 | 267.9 | 186.6
573.1 | 297.1 | 152.1 | 257.9 | 268.1 | 187
574.1 | 298.1 | 152.5 | 258.4 | 267.9 | 187.5
575.1 | 299.1 | 152.8 | 258.5 | 268 | 187.9
576.1 | 300.1 | 153.2 | 259 | 268.2 | 188.4
577.1 | 301.1 | 153.6 | 259.3 | 268.1 | 188.9
578.1 | 302.1 | 153.9 | 259.4 | 268.3 | 189.4
579.1 | 303.1 | 154.3 | 259.6 | 268.7 | 189.9
580.1 | 304.1 | 154.6 | 259.4 | 269 | 190.3
581.1 | 305.1 | 155 | 259.6 | 269.4 | 190.6
582.1 | 306.1 | 155.3 | 259.9 | 269.5 | 191.1
583.1 | 307.1 | 155.7 | 260.2 | 269.2 | 191.6
584.1 | 308.1 | 156 | 260.3 | 268.8 | 192.1
585.1 | 309.1 | 156.4 | 260.3 | 268.9 | 192.6
586.1 | 310.1 | 156.7 | 260.6 | 268.8 | 193
587.1 | 311.1 | 157 | 261.1 | 268.9 | 193.5
588.1 | 312.1 | 157.3 | 261.5 | 269.2 | 194.1
589.1 | 313.1 | 157.7 | 261.9 | 269.5 | 194.6
590.1 | 314.1 | 158 | 262 | 269.8 | 195.1
591.1 | 315.1 | 158.3 | 262.3 | 270.2 | 195.6
592.1 | 316.1 | 158.6 | 262.8 | 270.7 | 195.9
593.1 | 317.1 | 158.9 | 263.1 | 271.4 | 196.5
594.1 | 318.1 | 159.3 | 264.3 | 271.9 | 197.3
595.1 | 319.1 | 159.6 | 265 | 272.4 | 197.9
596.1 | 320.1 | 160 | 265.2 | 272.8 | 198.4
597.1 | 321.1 | 160.3 | 265.3 | 273.3 | 198.9
598.1 | 322.1 | 160.7 | 265.9 | 273.4 | 199.4
599.1 | 323.1 | 161 | 266.1 | 273.6 | 199.8
600.1 | 324.1 | 161.4 | 266.2 | 274 | 200.2
601.1 | 325.1 | 161.7 | 266.2 | 274.3 | 200.7
602.1 | 326.1 | 162.1 | 266.6 | 274.6 | 201.1
603.1 | 327.1 | 162.5 | 266.8 | 274.6 | 201.5
604.1 | 328.1 | 162.8 | 266.8 | 274.5 | 201.8
605.1 | 329.1 | 163.2 | 266.5 | 274.7 | 202.3
606.1 | 330.1 | 163.5 | 266.7 | 274.7 | 202.9
607.1 | 331.1 | 163.9 | 266.8 | 274.8 | 203.2
608.1 | 332.1 | 164.2 | 266.7 | 275 | 203.5
609.1 | 333.1 | 164.5 | 266.9 | 275 | 203.9
610.1 | 334.1 | 164.9 | 267.2 | 274.8 | 204.3
611.1 | 335.1 | 165.2 | 267.1 | 275.1 | 204.9
612.1 | 336.1 | 165.6 | 267.3 | 275.5 | 205.3
613.1 | 337.1 | 165.9 | 267.2 | 275.6 | 205.8
614.1 | 338.1 | 166.2 | 267.7 | 275.7 | 206.4
615.1 | 339.1 | 166.6 | 268.2 | 276 | 206.9
616.1 | 340.1 | 166.9 | 268.3 | 275.4 | 207.2
617.1 | 341.1 | 167.2 | 269 | 275.5 | 207.5
618.1 | 342.1 | 167.6 | 269.1 | 275.8 | 207.9
619.1 | 343.1 | 167.9 | 269.1 | 275.6 | 208.2
620.1 | 344.1 | 168.2 | 268.8 | 275.5 | 208.6
621.1 | 345.1 | 168.5 | 269 | 275.5 | 209
622.1 | 346.1 | 168.8 | 269.4 | 276.3 | 209.5
623.2 | 347.2 | 169.1 | 269.8 | 276.4 | 210
624.2 | 348.2 | 169.4 | 270.1 | 276.3 | 210.4
625.2 | 349.2 | 169.7 | 270.5 | 276.3 | 210.8
626.2 | 350.2 | 170 | 271 | 276.6 | 211.1
627.2 | 351.2 | 170.3 | 271.2 | 276.7 | 211.5
628.2 | 352.2 | 170.6 | 271.6 | 276.9 | 212
629.2 | 353.2 | 170.9 | 272 | 277 | 212.4
630.2 | 354.2 | 171.2 | 272.5 | 277.1 | 212.8
631.2 | 355.2 | 171.5 | 272.8 | 277.3 | 213.1
632.2 | 356.2 | 171.8 | 272.4 | 277.3 | 213.4
633.2 | 357.2 | 172 | 272.2 | 277.1 | 213.7
634.2 | 358.2 | 172.3 | 271.9 | 277 | 214.1
635.2 | 359.2 | 172.6 | 271.3 | 276.8 | 214.4
636.2 | 360.2 | 172.9 | 270.9 | 277.3 | 214.8
637.2 | 361.2 | 173.1 | 270.9 | 277.4 | 215.2
638.2 | 362.2 | 173.4 | 270.7 | 277.5 | 215.5
639.2 | 363.2 | 173.7 | 270.2 | 277.7 | 215.8
640.2 | 364.2 | 174 | 269.9 | 278.1 | 216.1
641.2 | 365.2 | 174.3 | 270.1 | 278.4 | 216.7
642.2 | 366.2 | 174.6 | 270.4 | 278.6 | 217.1
643.2 | 367.2 | 174.9 | 270.5 | 278.8 | 217.4
644.2 | 368.2 | 175.2 | 270.4 | 279.3 | 217.7
645.2 | 369.2 | 175.4 | 270.5 | 279.8 | 218.1
646.2 | 370.2 | 175.7 | 270.7 | 280.1 | 218.6
647.2 | 371.2 | 176 | 270.8 | 280.1 | 218.9
648.2 | 372.2 | 176.3 | 270.8 | 280.1 | 219.2
649.2 | 373.2 | 176.6 | 270.9 | 280.4 | 219.6
650.2 | 374.2 | 176.9 | 271.3 | 280.4 | 219.9
651.2 | 375.2 | 177.3 | 271.8 | 280.3 | 220.2
652.2 | 376.2 | 177.5 | 271.9 | 280.2 | 220.6
653.2 | 377.2 | 177.8 | 271.8 | 280.5 | 220.9
654.2 | 378.2 | 178.1 | 271.8 | 280.8 | 221.3
655.2 | 379.2 | 178.4 | 271.7 | 281.1 | 221.7
656.2 | 380.2 | 178.7 | 271.8 | 282.1 | 222
657.2 | 381.2 | 179 | 272.1 | 283 | 222.4
658.2 | 382.2 | 179.2 | 272.6 | 283.7 | 222.7
659.2 | 383.2 | 179.5 | 272.8 | 284.6 | 223.2
660.2 | 384.2 | 179.8 | 273.1 | 285 | 223.6
661.2 | 385.2 | 180.2 | 273.4 | 285.4 | 224.1
662.2 | 386.2 | 180.5 | 273.9 | 285.7 | 224.5
663.2 | 387.2 | 180.8 | 274.3 | 285.9 | 224.8
664.2 | 388.2 | 181.1 | 274.3 | 286.1 | 225.1
665.2 | 389.2 | 181.4 | 274.4 | 286.3 | 225.4
666.2 | 390.2 | 181.7 | 274.8 | 286.6 | 225.7
667.2 | 391.2 | 182 | 275.3 | 287 | 226.1
668.2 | 392.2 | 182.3 | 275.5 | 287.2 | 226.5
669.2 | 393.2 | 182.6 | 275.8 | 287.1 | 226.9
670.2 | 394.2 | 182.9 | 275.9 | 287.4 | 227.3
671.2 | 395.2 | 183.2 | 275.9 | 287.7 | 227.6
672.2 | 396.2 | 183.5 | 276 | 287.8 | 227.9
673.2 | 397.2 | 183.7 | 275.8 | 288.1 | 228.1
674.2 | 398.2 | 184 | 275.7 | 288.7 | 228.5
675.2 | 399.2 | 184.3 | 275.8 | 288.7 | 228.9
676.2 | 400.2 | 184.6 | 275.9 | 289.1 | 229.2
677.2 | 401.2 | 184.8 | 276 | 289.6 | 229.6
678.2 | 402.2 | 185.1 | 276.6 | 290 | 229.9
679.2 | 403.2 | 185.4 | 277 | 290 | 230.3
680.2 | 404.2 | 185.7 | 276.8 | 289.9 | 230.6
681.2 | 405.2 | 186 | 276.8 | 290 | 230.9
682.2 | 406.2 | 186.2 | 276.9 | 290.6 | 231.1
683.2 | 407.2 | 186.5 | 277.4 | 291.1 | 231.5
684.2 | 408.2 | 186.8 | 277.6 | 291.4 | 231.9
685.2 | 409.2 | 187.1 | 277.6 | 292.1 | 232.2
686.2 | 410.2 | 187.3 | 278.2 | 292.7 | 232.6
687.2 | 411.2 | 187.6 | 278.7 | 292.9 | 233
688.2 | 412.2 | 187.9 | 279.6 | 292.9 | 233.5
689.2 | 413.2 | 188.2 | 280.4 | 292.9 | 233.8
690.2 | 414.2 | 188.5 | 280.1 | 293.3 | 234.3
691.2 | 415.2 | 188.8 | 280 | 293.5 | 234.6
692.2 | 416.2 | 189 | 279.8 | 293.6 | 234.8
693.2 | 417.2 | 189.3 | 280.1 | 293.7 | 235.2
694.2 | 418.2 | 189.6 | 280.5 | 293.7 | 235.4
695.2 | 419.2 | 189.8 | 281.2 | 293.6 | 235.8
696.2 | 420.2 | 190.1 | 282.1 | 294.1 | 236.1
697.2 | 421.2 | 190.3 | 283.3 | 294.4 | 236.5
698.2 | 422.2 | 190.6 | 284.2 | 294.4 | 237
699.2 | 423.2 | 190.8 | 284.8 | 294.3 | 237.5
700.2 | 424.2 | 191.1 | 284.4 | 294.3 | 237.9
701.2 | 425.2 | 191.3 | 284.6 | 294.3 | 238.2
702.2 | 426.2 | 191.5 | 284.8 | 294.2 | 238.5
703.2 | 427.2 | 191.8 | 284.9 | 294.4 | 238.7
704.2 | 428.2 | 192 | 285.3 | 294.2 | 238.9
705.2 | 429.2 | 192.2 | 285.6 | 294.3 | 239.1
706.2 | 430.2 | 192.4 | 285.8 | 294.8 | 239.5
707.2 | 431.2 | 192.7 | 285.6 | 294.7 | 239.8
708.2 | 432.2 | 192.9 | 285.3 | 294.3 | 240.1
709.2 | 433.2 | 193.1 | 284.8 | 294.2 | 240.2
710.2 | 434.2 | 193.3 | 284.5 | 293.8 | 240.4
711.2 | 435.2 | 193.5 | 284.3 | 293.7 | 240.7
712.2 | 436.2 | 193.7 | 284.1 | 293.7 | 240.9
713.2 | 437.2 | 194 | 283.8 | 293.7 | 241.1
714.2 | 438.2 | 194.2 | 283.5 | 294 | 241.3
715.2 | 439.2 | 194.4 | 283.1 | 294.2 | 241.6
716.2 | 440.2 | 194.6 | 283 | 294.8 | 241.9
717.2 | 441.2 | 194.8 | 283 | 295.2 | 242.1
718.2 | 442.2 | 195 | 283.2 | 295.2 | 242.4
719.2 | 443.2 | 195.2 | 283.8 | 295.6 | 242.7
720.2 | 444.2 | 195.5 | 284.2 | 295.7 | 243
721.2 | 445.2 | 195.7 | 284.5 | 296.1 | 243.3
722.2 | 446.2 | 195.9 | 285 | 296.1 | 243.7
723.2 | 447.2 | 196.1 | 285.7 | 296.1 | 244
724.2 | 448.2 | 196.3 | 286.2 | 296.2 | 244.2
725.2 | 449.2 | 196.5 | 286.2 | 296.2 | 244.4
726.2 | 450.2 | 196.8 | 285.9 | 296.4 | 244.6
727.2 | 451.2 | 197 | 286.7 | 296.5 | 244.9
728.2 | 452.2 | 197.2 | 287.4 | 296.6 | 245.3
729.2 | 453.2 | 197.4 | 287.3 | 297 | 245.5
730.2 | 454.2 | 197.6 | 287.2 | 297.8 | 245.8
731.2 | 455.2 | 197.8 | 287.6 | 298.2 | 246.1
732.2 | 456.2 | 198 | 288.2 | 298.6 | 246.5
733.2 | 457.2 | 198.3 | 289.1 | 298.7 | 246.8
734.2 | 458.2 | 198.5 | 289.4 | 299.1 | 247.1
735.2 | 459.2 | 198.7 | 289.4 | 299.7 | 247.3
736.2 | 460.2 | 199 | 289.6 | 300.1 | 247.6
737.2 | 461.2 | 199.2 | 290 | 300.3 | 248
738.2 | 462.2 | 199.5 | 290.4 | 300.4 | 248.2
739.2 | 463.2 | 199.7 | 290.6 | 300.2 | 248.6
740.2 | 464.2 | 199.9 | 291.4 | 300 | 248.8
741.2 | 465.2 | 200.2 | 292 | 300 | 249.2
742.2 | 466.2 | 200.4 | 292.1 | 299.8 | 249.4
743.2 | 467.2 | 200.6 | 292.6 | 299.6 | 249.6
744.2 | 468.2 | 200.9 | 292.9 | 299.7 | 249.8
745.2 | 469.2 | 201.1 | 292.6 | 299.7 | 250.1
746.2 | 470.2 | 201.3 | 292.8 | 299.5 | 250.3
747.2 | 471.2 | 201.6 | 292.8 | 299.5 | 250.6
748.2 | 472.2 | 201.8 | 292.9 | 299.4 | 250.9
749.2 | 473.2 | 202 | 293.1 | 299.1 | 251.1
750.2 | 474.2 | 202.2 | 293.2 | 298.9 | 251.4
751.2 | 475.2 | 202.5 | 292.7 | 298.8 | 251.6
752.2 | 476.2 | 202.7 | 292.3 | 298.7 | 251.8
753.2 | 477.2 | 202.9 | 291.9 | 298.9 | 251.9
754.2 | 478.2 | 203.1 | 292.1 | 298.8 | 252
755.2 | 479.2 | 203.4 | 292.1 | 298.6 | 252.1
756.2 | 480.2 | 203.6 | 291.6 | 299 | 252.3
757.2 | 481.2 | 203.8 | 291.3 | 299.5 | 252.5
758.2 | 482.2 | 204.1 | 290.8 | 299.8 | 252.7
759.2 | 483.2 | 204.3 | 290.9 | 300.7 | 252.9
760.2 | 484.2 | 204.6 | 291.2 | 301.2 | 253.2
761.2 | 485.2 | 204.9 | 291.4 | 301.8 | 253.4
762.2 | 486.2 | 205.2 | 291.9 | 302.3 | 253.7
763.2 | 487.2 | 205.4 | 292.8 | 303 | 254
764.2 | 488.2 | 205.7 | 293.9 | 303.8 | 254.3
765.2 | 489.2 | 206 | 294.7 | 305.2 | 254.6
766.2 | 490.2 | 206.4 | 295.6 | 305.9 | 255
767.2 | 491.2 | 206.7 | 295.9 | 307.2 | 255.3
768.2 | 492.2 | 207 | 296.2 | 308.1 | 255.7
769.2 | 493.2 | 207.4 | 297.1 | 308.6 | 256
770.2 | 494.2 | 207.7 | 297.6 | 308.9 | 256.2
771.2 | 495.2 | 208 | 298 | 309.1 | 256.5
772.2 | 496.2 | 208.4 | 298.4 | 309.4 | 256.8
773.2 | 497.2 | 208.8 | 298 | 310.4 | 257
774.2 | 498.2 | 209.1 | 298.1 | 310.4 | 257.2
775.2 | 499.2 | 209.5 | 297.7 | 310.5 | 257.5
776.2 | 500.2 | 209.8 | 297.5 | 311.6 | 257.7
777.2 | 501.2 | 210.2 | 297.4 | 312.2 | 258
778.2 | 502.2 | 210.5 | 297.6 | 311.5 | 258.4
779.2 | 503.2 | 210.9 | 297.7 | 311 | 258.6
780.2 | 504.2 | 211.2 | 297.8 | 310.9 | 258.7
781.2 | 505.2 | 211.5 | 298.3 | 310.4 | 258.9
782.2 | 506.2 | 211.9 | 298.5 | 310 | 259.2
783.2 | 507.2 | 212.2 | 298.4 | 309.9 | 259.4
784.2 | 508.2 | 212.5 | 298.2 | 310.1 | 259.6
785.2 | 509.2 | 212.8 | 297.9 | 310.1 | 259.9
786.2 | 510.2 | 213.2 | 298.5 | 310.1 | 260.1
787.2 | 511.2 | 213.5 | 299.1 | 310.2 | 260.4
788.2 | 512.2 | 213.8 | 299.2 | 310.4 | 260.6
789.2 | 513.2 | 214.1 | 299 | 310.6 | 260.9
790.2 | 514.2 | 214.4 | 299 | 310.6 | 261
791.2 | 515.2 | 214.7 | 299.1 | 310.4 | 261.2
792.2 | 516.2 | 215 | 299.3 | 310 | 261.3
793.2 | 517.2 | 215.3 | 299.1 | 310 | 261.5
794.2 | 518.2 | 215.5 | 299.4 | 310 | 261.7
795.2 | 519.2 | 215.8 | 299.3 | 310.1 | 261.9
796.2 | 520.2 | 216.1 | 299.2 | 310.4 | 262.1
797.2 | 521.2 | 216.4 | 299.2 | 310.4 | 262.3
798.2 | 522.2 | 216.7 | 299 | 310.5 | 262.5
799.2 | 523.2 | 217 | 298.8 | 310.6 | 262.7
800.2 | 524.2 | 217.2 | 299 | 310.5 | 263
801.2 | 525.2 | 217.5 | 299.1 | 311 | 263.2
802.2 | 526.2 | 217.8 | 299.2 | 311.1 | 263.4
803.2 | 527.2 | 218.1 | 299 | 310.9 | 263.7
804.2 | 528.2 | 218.3 | 298.8 | 311.3 | 263.8
805.2 | 529.2 | 218.6 | 298.4 | 310.8 | 263.9
806.2 | 530.2 | 218.9 | 298 | 310.8 | 264.1
807.2 | 531.2 | 219.2 | 298 | 310.8 | 264.4
808.2 | 532.2 | 219.4 | 297.9 | 310.6 | 264.6
809.2 | 533.2 | 219.7 | 297.8 | 310.3 | 264.7
810.2 | 534.2 | 220 | 298.1 | 310.1 | 264.8
811.2 | 535.2 | 220.3 | 298.6 | 309.8 | 265
812.2 | 536.2 | 220.6 | 299.2 | 309.4 | 265.3
813.2 | 537.2 | 220.8 | 299.4 | 309.3 | 265.5
814.2 | 538.2 | 221.1 | 299.4 | 309.5 | 265.7
815.2 | 539.2 | 221.4 | 299.9 | 309.5 | 266.1
816.2 | 540.2 | 221.7 | 300.3 | 309.6 | 266.3
817.2 | 541.2 | 222 | 300.8 | 309.5 | 266.5
818.2 | 542.2 | 222.3 | 301.2 | 309.6 | 266.8
819.2 | 543.2 | 222.6 | 301.9 | 309.6 | 267.1
820.2 | 544.2 | 222.8 | 302.9 | 309.7 | 267.5
821.2 | 545.2 | 223.1 | 304.1 | 309.9 | 267.9
822.2 | 546.2 | 223.4 | 304.8 | 310 | 268.4
823.2 | 547.2 | 223.6 | 305.8 | 310.6 | 268.8
824.2 | 548.2 | 223.9 | 306 | 311.1 | 269.2
825.2 | 549.2 | 224.2 | 307.2 | 311.8 | 269.5
826.2 | 550.2 | 224.4 | 307.7 | 312.9 | 269.8
827.2 | 551.2 | 224.7 | 307.9 | 314.1 | 270.1
828.2 | 552.2 | 225 | 308.4 | 315 | 270.3
829.2 | 553.2 | 225.3 | 309.1 | 315.2 | 270.6
830.2 | 554.2 | 225.6 | 309.7 | 315.4 | 270.8
831.2 | 555.2 | 225.8 | 310.2 | 315.9 | 271.2
832.2 | 556.2 | 226.2 | 310.8 | 316 | 271.5
833.2 | 557.2 | 226.5 | 310.8 | 316 | 271.7
834.2 | 558.2 | 226.8 | 310.1 | 315.9 | 271.8
835.2 | 559.2 | 227.1 | 309.8 | 315.9 | 272
836.2 | 560.2 | 227.5 | 310.1 | 316.6 | 272.1
837.2 | 561.2 | 227.8 | 309.9 | 316.4 | 272.5
838.2 | 562.2 | 228.1 | 309.6 | 316.3 | 272.6
839.2 | 563.2 | 228.4 | 309.9 | 316.7 | 272.8
840.2 | 564.2 | 228.7 | 309.6 | 316.9 | 273
841.2 | 565.2 | 228.9 | 309.2 | 317.1 | 273.1
842.2 | 566.2 | 229.2 | 309 | 317.2 | 273.4
843.2 | 567.2 | 229.5 | 308.8 | 317 | 273.5
844.2 | 568.2 | 229.8 | 308.4 | 316.9 | 273.6
845.2 | 569.2 | 230 | 308.2 | 317.2 | 273.7
846.2 | 570.2 | 230.3 | 308.1 | 317 | 273.9
847.2 | 571.2 | 230.5 | 307.7 | 317.1 | 274
848.2 | 572.2 | 230.8 | 307.4 | 317.4 | 274.1
849.2 | 573.2 | 231.1 | 307.3 | 318 | 274.3
850.2 | 574.2 | 231.3 | 307.7 | 318.4 | 274.5
851.2 | 575.2 | 231.6 | 308.2 | 319 | 274.7
852.2 | 576.2 | 231.8 | 308.9 | 319.8 | 275
853.2 | 577.2 | 232.1 | 309.5 | 320.1 | 275.2
854.2 | 578.2 | 232.4 | 310.2 | 320.5 | 275.5
855.2 | 579.2 | 232.7 | 311 | 320.5 | 275.8
856.2 | 580.2 | 233 | 311.7 | 320.9 | 276.2
857.2 | 581.2 | 233.3 | 313.1 | 321.4 | 276.6
858.2 | 582.2 | 233.6 | 314.1 | 321.8 | 276.9
859.2 | 583.2 | 233.9 | 315.4 | 322.2 | 277.4
860.2 | 584.2 | 234.2 | 316.6 | 323 | 277.8
861.2 | 585.2 | 234.5 | 317.2 | 323.8 | 278.3
862.2 | 586.2 | 234.8 | 317.9 | 324.2 | 278.6
863.2 | 587.2 | 235.1 | 318.2 | 324.4 | 278.8
864.2 | 588.2 | 235.4 | 318.2 | 324.5 | 279
865.2 | 589.2 | 235.7 | 318.3 | 324.6 | 279.2
866.2 | 590.2 | 236 | 318.3 | 325 | 279.4
867.2 | 591.2 | 236.3 | 318.4 | 325.2 | 279.6
868.2 | 592.2 | 236.6 | 318.3 | 325.8 | 279.8
869.2 | 593.2 | 236.9 | 318 | 326.3 | 280
870.2 | 594.2 | 237.2 | 318.4 | 327.5 | 280.2
871.2 | 595.2 | 237.5 | 318.6 | 328 | 280.5
872.2 | 596.2 | 237.8 | 318.3 | 328.3 | 280.8
873.2 | 597.2 | 238.1 | 317.9 | 328.8 | 280.9
874.2 | 598.2 | 238.4 | 317.8 | 329.2 | 281.2
875.2 | 599.2 | 238.7 | 317.5 | 328.8 | 281.4
876.2 | 600.2 | 239 | 317.2 | 328.5 | 281.7
877.2 | 601.2 | 239.4 | 316.7 | 328.1 | 281.8
878.2 | 602.2 | 239.7 | 316.4 | 327.8 | 282
879.2 | 603.2 | 240.1 | 316.2 | 327.6 | 282.2
880.2 | 604.2 | 240.4 | 315.8 | 328 | 282.4
881.2 | 605.2 | 240.6 | 315.6 | 327.7 | 282.6
882.2 | 606.2 | 240.9 | 315.5 | 327.5 | 282.8
883.2 | 607.2 | 241.1 | 315.7 | 327 | 283
884.2 | 608.2 | 241.4 | 316 | 326.6 | 283.2
885.2 | 609.2 | 241.7 | 316.2 | 326.3 | 283.4
886.2 | 610.2 | 242 | 316.2 | 326.1 | 283.6
887.2 | 611.2 | 242.3 | 316.8 | 326.7 | 283.9
888.2 | 612.2 | 242.5 | 317.3 | 326.6 | 284.2
889.2 | 613.2 | 242.8 | 317.5 | 326.3 | 284.5
890.2 | 614.2 | 243 | 317.2 | 326.2 | 284.7
891.2 | 615.2 | 243.3 | 316.8 | 326.2 | 284.9
892.2 | 616.2 | 243.5 | 316.4 | 325.8 | 285.1
893.2 | 617.2 | 243.7 | 316.3 | 325.4 | 285.2
894.2 | 618.2 | 244 | 316.5 | 325.2 | 285.2
895.2 | 619.2 | 244.2 | 316.4 | 325.1 | 285.4
896.2 | 620.2 | 244.5 | 316.3 | 325.2 | 285.5
897.2 | 621.2 | 244.7 | 316 | 325.3 | 285.6
898.2 | 622.2 | 244.9 | 316 | 325.3 | 285.7
899.2 | 623.2 | 245.2 | 316.1 | 325.8 | 285.8
900.2 | 624.2 | 245.4 | 316.4 | 326.2 | 286
901.2 | 625.2 | 245.6 | 316.5 | 326.9 | 286.2
902.2 | 626.2 | 245.9 | 316.2 | 327 | 286.3
903.2 | 627.2 | 246.1 | 316.3 | 327.4 | 286.4
904.2 | 628.2 | 246.3 | 316.1 | 327.7 | 286.6
905.2 | 629.2 | 246.6 | 315.9 | 328.3 | 286.8
906.2 | 630.2 | 246.9 | 315.9 | 329.9 | 287.1
907.2 | 631.2 | 247.1 | 316.4 | 332.6 | 287.4
908.2 | 632.2 | 247.4 | 316.9 | 332.9 | 287.7
909.2 | 633.2 | 247.6 | 317.9 | 332.9 | 288
910.2 | 634.2 | 247.9 | 318.8 | 333 | 288.3
911.2 | 635.2 | 248.2 | 319.8 | 333 | 288.7
912.2 | 636.2 | 248.5 | 320.3 | 332.9 | 289
913.2 | 637.2 | 248.8 | 321.2 | 333.1 | 289.3
914.2 | 638.2 | 249.1 | 322 | 333 | 289.8
915.2 | 639.2 | 249.4 | 322 | 332.8 | 290.1
916.2 | 640.2 | 249.6 | 322.1 | 332.8 | 290.2
917.2 | 641.2 | 249.9 | 321.8 | 332.7 | 290.3
918.2 | 642.2 | 250.1 | 321.2 | 332.3 | 290.4
919.2 | 643.2 | 250.3 | 320.6 | 331.9 | 290.5
920.2 | 644.2 | 250.5 | 320.1 | 331.7 | 290.5
921.2 | 645.2 | 250.7 | 319.6 | 331.7 | 290.6
922.2 | 646.2 | 251 | 319.4 | 331.7 | 290.7
923.2 | 647.2 | 251.2 | 319.3 | 331.9 | 290.8
924.2 | 648.2 | 251.4 | 319 | 331.8 | 290.9
925.2 | 649.2 | 251.6 | 318.8 | 332 | 291.1
926.2 | 650.2 | 251.9 | 318.8 | 332.7 | 291.1
927.2 | 651.2 | 252.1 | 318.8 | 333.3 | 291.3
928.2 | 652.2 | 252.3 | 318.9 | 334.1 | 291.5
929.2 | 653.2 | 252.6 | 319.9 | 334.8 | 291.6
930.2 | 654.2 | 252.8 | 320.5 | 335.9 | 291.8
931.2 | 655.2 | 253.1 | 320.6 | 336.9 | 292
932.2 | 656.2 | 253.4 | 320.8 | 337.5 | 292.3
933.2 | 657.2 | 253.7 | 321.6 | 339 | 292.6
934.2 | 658.2 | 254.2 | 322.4 | 340.2 | 292.9
935.2 | 659.2 | 254.7 | 323 | 341 | 293.2
936.2 | 660.2 | 255.1 | 323.3 | 341.3 | 293.5
937.2 | 661.2 | 255.6 | 323.5 | 343.7 | 293.8
938.2 | 662.2 | 256.1 | 324.2 | 343.5 | 294.1
939.2 | 663.2 | 256.6 | 325 | 344.8 | 294.4
940.2 | 664.2 | 257.1 | 325.9 | 345.3 | 294.7
941.2 | 665.2 | 257.7 | 326.4 | 345.7 | 295
942.2 | 666.2 | 258.2 | 326.8 | 346.9 | 295.3
943.2 | 667.2 | 258.7 | 327.6 | 347.9 | 295.7
944.2 | 668.2 | 259.2 | 328.3 | 348.4 | 296
945.2 | 669.2 | 259.7 | 328.8 | 349.3 | 296.3
946.2 | 670.2 | 260.2 | 329.2 | 349.8 | 296.6
947.2 | 671.2 | 260.7 | 329.5 | 350.7 | 296.9
948.2 | 672.2 | 261.1 | 329.6 | 351.4 | 297.2
949.2 | 673.2 | 261.6 | 329.7 | 351.7 | 297.5
950.2 | 674.2 | 262 | 330 | 352.2 | 297.8
951.2 | 675.2 | 262.5 | 330.4 | 352.7 | 298
952.2 | 676.2 | 263 | 330.6 | 354.5 | 298.4
953.2 | 677.2 | 263.6 | 331 | 354 | 298.7
954.2 | 678.2 | 264.2 | 331 | 353.9 | 298.9
955.2 | 679.2 | 264.7 | 330.9 | 353.2 | 299.1
956.2 | 680.2 | 265.3 | 330.6 | 352.3 | 299.3
957.2 | 681.2 | 265.8 | 330.2 | 351.6 | 299.4
958.2 | 682.2 | 266.3 | 330.1 | 350.7 | 299.6
959.2 | 683.2 | 266.8 | 330.2 | 350.1 | 299.9
960.2 | 684.2 | 267.2 | 329.8 | 349.6 | 300
961.2 | 685.2 | 267.7 | 329.2 | 349.1 | 300.1
962.2 | 686.2 | 268.1 | 328.9 | 348.3 | 300.2
963.2 | 687.2 | 268.5 | 329.2 | 349.2 | 300.3
964.2 | 688.2 | 268.8 | 329.5 | 348.8 | 300.5
965.2 | 689.2 | 269.1 | 329.6 | 348 | 300.7
966.2 | 690.2 | 269.5 | 330 | 347.5 | 300.8
967.2 | 691.2 | 269.8 | 330.3 | 347.2 | 301
968.2 | 692.2 | 270.1 | 330.8 | 346.9 | 301.4
969.2 | 693.2 | 270.4 | 331 | 346.5 | 301.6
970.2 | 694.2 | 270.7 | 331.2 | 346.3 | 301.8
971.2 | 695.2 | 271 | 331.5 | 345.8 | 302.1
972.2 | 696.2 | 271.2 | 331.7 | 345.5 | 302.3
973.2 | 697.2 | 271.5 | 331.4 | 345 | 302.5
974.2 | 698.2 | 271.8 | 331.2 | 344.2 | 302.5
975.2 | 699.2 | 272.1 | 331 | 344.2 | 302.7
976.2 | 700.2 | 272.4 | 330.9 | 344 | 302.9
977.2 | 701.2 | 272.6 | 330.7 | 343.6 | 303.1
978.2 | 702.2 | 272.9 | 330.6 | 343 | 303.2
979.2 | 703.2 | 273.1 | 330.8 | 342.7 | 303.4
980.2 | 704.2 | 273.3 | 330.6 | 342.2 | 303.6
981.2 | 705.2 | 273.6 | 330.5 | 342 | 303.7
982.2 | 706.2 | 273.8 | 330.2 | 341.3 | 303.8
983.2 | 707.2 | 274 | 329.7 | 340.6 | 303.8
984.2 | 708.2 | 274.2 | 329 | 340.1 | 303.9
985.2 | 709.2 | 274.3 | 328.3 | 339.7 | 303.9
986.2 | 710.2 | 274.4 | 328 | 339.5 | 303.9
987.2 | 711.2 | 274.5 | 327.8 | 339.1 | 303.9
988.2 | 712.2 | 274.6 | 327.6 | 338.6 | 304
989.2 | 713.2 | 274.7 | 327.6 | 338.5 | 304.1
990.2 | 714.2 | 274.8 | 327.5 | 338.5 | 304.1
991.2 | 715.2 | 274.8 | 327.4 | 337.9 | 304.2
992.2 | 716.2 | 274.9 | 327.1 | 337.3 | 304.3
993.2 | 717.2 | 274.9 | 326.4 | 336.7 | 304.3
994.2 | 718.2 | 275 | 326.1 | 336.6 | 304.3
995.2 | 719.2 | 275 | 325.6 | 336.3 | 304.3
996.2 | 720.2 | 275 | 325.5 | 336.2 | 304.4
997.2 | 721.2 | 275 | 325.3 | 336.1 | 304.5
998.2 | 722.2 | 275 | 325.1 | 335.5 | 304.7
999.2 | 723.2 | 275 | 325.1 | 335 | 304.8
1000.2 | 724.2 | 275 | 325 | 334.6 | 304.8
1001.2 | 725.2 | 275 | 324.8 | 334.3 | 304.8
1002.2 | 726.2 | 275 | 324.6 | 334.2 | 304.8
1003.2 | 727.2 | 275 | 324.7 | 334.2 | 304.9
1004.2 | 728.2 | 275.1 | 324.6 | 334.1 | 305
1005.2 | 729.2 | 275.1 | 324.6 | 334.2 | 305.2
1006.2 | 730.2 | 275.2 | 324.3 | 334.1 | 305.2
1007.2 | 731.2 | 275.2 | 324 | 334.2 | 305.3
1008.2 | 732.2 | 275.3 | 324 | 334.4 | 305.4
1009.2 | 733.2 | 275.4 | 324 | 334.4 | 305.5
1010.2 | 734.2 | 275.5 | 324 | 334.5 | 305.6
1011.2 | 735.2 | 275.7 | 324.1 | 334.6 | 305.7
1012.2 | 736.2 | 275.8 | 324.4 | 334.9 | 305.9
1013.2 | 737.2 | 275.8 | 324.8 | 335.3 | 306.1
1014.2 | 738.2 | 275.9 | 325.1 | 335.4 | 306.2
1015.2 | 739.2 | 276 | 325.3 | 335.7 | 306.3
1016.2 | 740.2 | 276.1 | 326 | 335.7 | 306.6
1017.2 | 741.2 | 276.1 | 326.7 | 336.1 | 306.9
1018.2 | 742.2 | 276.2 | 327.1 | 336.4 | 307.1
1019.2 | 743.2 | 276.3 | 327.7 | 337.2 | 307.4
1020.2 | 744.2 | 276.4 | 328.3 | 338.2 | 307.6
1021.2 | 745.2 | 276.4 | 328.8 | 338.6 | 307.8
1022.2 | 746.2 | 276.3 | 329.9 | 339.1 | 308
1023.2 | 747.2 | 276.3 | 330.7 | 339.4 | 308.3
1024.2 | 748.2 | 276.4 | 331.2 | 339.6 | 308.5
1025.2 | 749.2 | 276.4 | 332 | 339.9 | 308.7
1026.2 | 750.2 | 276.4 | 332.5 | 340.7 | 309
1027.2 | 751.2 | 276.6 | 332.9 | 341.3 | 309.3
1028.2 | 752.2 | 276.7 | 333.3 | 341.6 | 309.4
1029.2 | 753.2 | 276.7 | 333.2 | 341.6 | 309.5
1030.2 | 754.2 | 276.8 | 333 | 341.5 | 309.6
1031.2 | 755.2 | 277 | 333.1 | 341.5 | 309.7
1032.2 | 756.2 | 277.2 | 333 | 341.7 | 309.7
1033.2 | 757.2 | 277.3 | 333.1 | 342 | 309.8
1034.2 | 758.2 | 277.4 | 332.9 | 342.1 | 309.8
1035.2 | 759.2 | 277.6 | 332.8 | 342.3 | 309.9
1036.2 | 760.2 | 277.7 | 332.9 | 342.5 | 310
1037.2 | 761.2 | 277.8 | 332.8 | 342.7 | 310.1
1038.2 | 762.2 | 278 | 332.9 | 342.7 | 310.2
1039.2 | 763.2 | 278.1 | 333.2 | 343.1 | 310.3
1040.2 | 764.2 | 278.2 | 333.4 | 343.4 | 310.5
1041.2 | 765.2 | 278.4 | 333.4 | 343 | 310.7
1042.2 | 766.2 | 278.4 | 333.6 | 342.9 | 310.9
1043.2 | 767.2 | 278.5 | 333.7 | 343 | 311.1
1044.2 | 768.2 | 278.6 | 333.7 | 343.1 | 311.3
1045.2 | 769.2 | 278.8 | 333.8 | 343.3 | 311.4
1046.2 | 770.2 | 278.9 | 334 | 343.2 | 311.6
1047.2 | 771.2 | 279 | 334 | 343.2 | 311.7
1048.2 | 772.2 | 279.2 | 333.8 | 343.1 | 311.9
1049.2 | 773.2 | 279.4 | 333.8 | 343.1 | 311.9
1050.2 | 774.2 | 279.5 | 334.1 | 343.4 | 312
1051.2 | 775.2 | 279.6 | 334.5 | 344.8 | 312.1
1052.2 | 776.2 | 279.8 | 334.9 | 346.7 | 312.1
1053.2 | 777.2 | 279.9 | 335.1 | 348.1 | 312.4
1054.2 | 778.2 | 280 | 334.8 | 348.1 | 312.5
1055.2 | 779.2 | 280.2 | 334.6 | 350 | 312.5
1056.2 | 780.2 | 280.4 | 334.6 | 351 | 312.7
1057.2 | 781.2 | 280.6 | 335 | 351.4 | 312.9
1058.2 | 782.2 | 280.7 | 335.2 | 351.3 | 313.2
1059.2 | 783.2 | 280.9 | 335.1 | 350.9 | 313.3
1060.2 | 784.2 | 281 | 335.1 | 351 | 313.5
1061.2 | 785.2 | 281.1 | 335.1 | 350.8 | 313.7
1062.2 | 786.2 | 281.2 | 334.9 | 350.9 | 313.8
1063.2 | 787.2 | 281.4 | 334.6 | 350.8 | 313.9
1064.2 | 788.2 | 281.4 | 334.5 | 350.4 | 314
1065.2 | 789.2 | 281.4 | 334.7 | 349.9 | 314.2
1066.2 | 790.2 | 281.7 | 335.1 | 349.6 | 314.4
1067.2 | 791.2 | 281.9 | 335.4 | 349.6 | 314.7
1068.2 | 792.2 | 282.1 | 335.7 | 350 | 314.8
1069.2 | 793.2 | 282.3 | 336.7 | 350.8 | 315.2
1070.2 | 794.2 | 282.4 | 338.6 | 351.9 | 315.7
1071.2 | 795.2 | 282.5 | 340 | 352.7 | 316.2
1072.2 | 796.2 | 282.6 | 340.2 | 352.9 | 316.4
1073.2 | 797.2 | 282.8 | 340.2 | 352.6 | 316.5
1074.2 | 798.2 | 282.9 | 340.4 | 352.4 | 316.7
1075.2 | 799.2 | 283 | 340.6 | 352.6 | 316.8
1076.2 | 800.2 | 283.2 | 341 | 353.4 | 317
1077.2 | 801.2 | 283.3 | 341.4 | 353.9 | 317.2
1078.2 | 802.2 | 283.4 | 341.8 | 354.1 | 317.5
1079.2 | 803.2 | 283.5 | 341.9 | 354.4 | 317.6
1080.2 | 804.2 | 283.8 | 341.9 | 354.5 | 317.7
1081.2 | 805.2 | 284 | 342.2 | 354.6 | 317.9
1082.2 | 806.2 | 284.3 | 342.6 | 355.3 | 318.1
1083.2 | 807.2 | 284.5 | 342.7 | 355.3 | 318.2
1084.2 | 808.2 | 284.7 | 342.5 | 355.2 | 318.3
1085.2 | 809.2 | 284.8 | 342.1 | 355.2 | 318.4
1086.2 | 810.2 | 284.8 | 341.9 | 354.9 | 318.4
1087.2 | 811.2 | 285 | 341.8 | 354.9 | 318.6
1088.2 | 812.2 | 285.3 | 341.7 | 354.7 | 318.7
1089.2 | 813.2 | 285.5 | 341.2 | 354.4 | 318.8
1090.2 | 814.2 | 285.7 | 340.9 | 354.2 | 319
1091.2 | 815.2 | 285.8 | 341 | 353.9 | 319.2
1092.2 | 816.2 | 286 | 341.1 | 354 | 319.3
1093.2 | 817.2 | 286.2 | 341.1 | 354.3 | 319.4
1094.2 | 818.2 | 286.2 | 341.2 | 354.7 | 319.6
1095.2 | 819.2 | 286.4 | 341.7 | 354.8 | 319.8
1096.2 | 820.2 | 286.5 | 342.1 | 354.8 | 320.1
1097.2 | 821.2 | 286.5 | 342.3 | 354.8 | 320.2
1098.2 | 822.2 | 286.6 | 342.5 | 355.4 | 320.3
1099.2 | 823.2 | 286.7 | 342.9 | 355.7 | 320.5
1100.2 | 824.2 | 286.8 | 343.2 | 356.4 | 320.7
1101.2 | 825.2 | 286.9 | 343.5 | 356.7 | 321
1102.2 | 826.2 | 287.1 | 343.7 | 356.7 | 321.2
1103.2 | 827.2 | 287.2 | 343.8 | 356.8 | 321.4
1104.2 | 828.2 | 287.3 | 344.1 | 357.3 | 321.6
1105.2 | 829.2 | 287.5 | 344.3 | 357.1 | 321.8
1106.2 | 830.2 | 287.7 | 344.6 | 357.1 | 322
1107.2 | 831.2 | 287.9 | 345.6 | 357.3 | 322.2
1108.2 | 832.2 | 288 | 345.9 | 357.3 | 322.4
1109.2 | 833.2 | 288.1 | 346.1 | 357.3 | 322.6
1110.2 | 834.2 | 288.2 | 346.4 | 357.6 | 323
1111.2 | 835.2 | 288.3 | 346.2 | 357.6 | 323.2
1112.2 | 836.2 | 288.5 | 346.2 | 357.5 | 323.3
1113.2 | 837.2 | 288.8 | 346.4 | 357.5 | 323.5
1114.2 | 838.2 | 288.9 | 346.7 | 357.4 | 323.6
1115.2 | 839.2 | 289.1 | 346.9 | 357.2 | 323.8
1116.2 | 840.2 | 289.2 | 346.8 | 357 | 324
1117.2 | 841.2 | 289.4 | 346.6 | 356.8 | 324.1
1118.2 | 842.2 | 289.6 | 346.3 | 357.2 | 324.2
1119.2 | 843.2 | 289.8 | 346.6 | 357.1 | 324.3
1120.2 | 844.2 | 289.9 | 347.6 | 357.3 | 324.6
1121.2 | 845.2 | 290 | 347.6 | 357 | 324.8
1122.2 | 846.2 | 290.1 | 347.3 | 356.6 | 324.9
1123.2 | 847.2 | 290.3 | 346.7 | 356.1 | 325
1124.2 | 848.2 | 290.4 | 346.4 | 355.9 | 325.1
1125.2 | 849.2 | 290.5 | 346.3 | 355.9 | 325.4
1126.2 | 850.2 | 290.7 | 346.6 | 356.2 | 325.5
1127.2 | 851.2 | 290.8 | 346.6 | 356.3 | 325.7
1128.2 | 852.2 | 290.9 | 346.8 | 356.6 | 325.8
1129.2 | 853.2 | 291 | 347.5 | 357 | 326
1130.2 | 854.2 | 291.2 | 348.7 | 357.6 | 326.3
1131.2 | 855.2 | 291.3 | 349 | 358.1 | 326.5
1132.2 | 856.2 | 291.3 | 348.9 | 358.5 | 326.7
1133.2 | 857.2 | 291.3 | 349.1 | 359.3 | 326.8
1134.2 | 858.2 | 291.5 | 349.1 | 359.5 | 326.9
1135.2 | 859.2 | 291.7 | 349.1 | 359.4 | 327
1136.2 | 860.2 | 291.8 | 349 | 359.3 | 327.2
1137.2 | 861.2 | 291.9 | 348.8 | 359.2 | 327.3
1138.2 | 862.2 | 292.1 | 348.9 | 359.1 | 327.4
1139.2 | 863.2 | 292.3 | 348.9 | 359 | 327.6
1140.2 | 864.2 | 292.4 | 348.7 | 359 | 327.8
1141.2 | 865.2 | 292.5 | 348.8 | 359.2 | 327.9
1142.2 | 866.2 | 292.7 | 349 | 359.3 | 328.1
1143.2 | 867.2 | 292.8 | 349.4 | 359.9 | 328.3
1144.2 | 868.2 | 293 | 349.9 | 360.4 | 328.5
1145.2 | 869.2 | 293.2 | 349.9 | 360.9 | 328.7
1146.2 | 870.2 | 293.4 | 350.2 | 361.4 | 328.8
1147.2 | 871.2 | 293.7 | 350.5 | 362 | 329.1
1148.2 | 872.2 | 293.8 | 350.7 | 362.1 | 329.3
1149.2 | 873.2 | 293.9 | 350.6 | 362.2 | 329.4
1150.2 | 874.2 | 294 | 350.5 | 362.3 | 329.5
1151.2 | 875.2 | 294.3 | 350.3 | 361.8 | 329.6
1152.2 | 876.2 | 294.4 | 349.9 | 361.4 | 329.6
1153.2 | 877.2 | 294.7 | 349.7 | 361.1 | 329.6
1154.2 | 878.2 | 294.9 | 349.2 | 360.9 | 329.7
1155.2 | 879.2 | 295.2 | 348.8 | 360.5 | 329.7
1156.2 | 880.2 | 295.5 | 348.8 | 360.4 | 329.8
1157.2 | 881.2 | 295.7 | 349 | 360.3 | 329.9
1158.2 | 882.2 | 295.9 | 349.3 | 360.1 | 330
1159.2 | 883.2 | 295.9 | 349.7 | 360.5 | 330.3
1160.2 | 884.2 | 296 | 350.1 | 360.8 | 330.5
1161.2 | 885.2 | 296.1 | 350.1 | 361.2 | 330.7
1162.2 | 886.2 | 296.3 | 350.1 | 361.2 | 330.8
1163.2 | 887.2 | 296.4 | 350.3 | 361.1 | 331
1164.2 | 888.2 | 296.5 | 350.3 | 361.1 | 331.1
1165.2 | 889.2 | 296.7 | 350.4 | 361 | 331.2
1166.2 | 890.2 | 296.9 | 350.3 | 361.1 | 331.2
1167.2 | 891.2 | 297 | 350.2 | 361.1 | 331.3
1168.2 | 892.2 | 297.2 | 350.3 | 361.5 | 331.3
1169.2 | 893.2 | 297.3 | 350.5 | 363.5 | 331.4
1170.2 | 894.2 | 297.5 | 350.5 | 363.6 | 331.5
1171.2 | 895.2 | 297.6 | 350.5 | 363.6 | 331.5
1172.2 | 896.2 | 297.8 | 350.3 | 364.7 | 331.6
1173.2 | 897.2 | 298 | 350.3 | 365.8 | 331.7
1174.2 | 898.2 | 298.2 | 350.5 | 366.1 | 331.8
1175.2 | 899.2 | 298.3 | 350.7 | 366.2 | 332
1176.2 | 900.2 | 298.4 | 351.2 | 366.2 | 332.1
1177.2 | 901.2 | 298.5 | 351.6 | 366.2 | 332.3
1178.2 | 902.2 | 298.8 | 351.8 | 366.1 | 332.5
1179.2 | 903.2 | 298.9 | 351.6 | 365.6 | 332.6
1180.2 | 904.2 | 299.1 | 351.5 | 365.4 | 332.7
1181.2 | 905.2 | 299.4 | 351.4 | 365.5 | 332.8
1182.2 | 906.2 | 299.5 | 351.3 | 365.4 | 332.8
1183.2 | 907.2 | 299.7 | 351 | 365.5 | 332.9
1184.2 | 908.2 | 299.8 | 351 | 365.6 | 333.1
1185.2 | 909.2 | 299.9 | 350.9 | 365.9 | 333.1
1186.2 | 910.2 | 300.1 | 350.6 | 365.5 | 333.2
1187.2 | 911.2 | 300.3 | 350.4 | 365.3 | 333.3
1188.2 | 912.2 | 300.5 | 350.3 | 365.8 | 333.4
1189.2 | 913.2 | 300.6 | 350.4 | 366.1 | 333.5
1190.2 | 914.2 | 300.8 | 350.4 | 365.7 | 333.6
1191.2 | 915.2 | 301 | 350.2 | 365.4 | 333.6
1192.2 | 916.2 | 301.1 | 350.2 | 365.4 | 333.6
1193.2 | 917.2 | 301.2 | 350.2 | 365.2 | 333.7
1194.2 | 918.2 | 301.4 | 350.3 | 365.1 | 333.8
1195.2 | 919.2 | 301.5 | 350.2 | 366 | 333.9
1196.2 | 920.2 | 301.6 | 350 | 365.9 | 334
1197.2 | 921.2 | 301.7 | 349.8 | 365.7 | 334
1198.2 | 922.2 | 301.8 | 349.6 | 365.4 | 334.1
1199.2 | 923.2 | 302 | 349.4 | 365.6 | 334.2
1200.2 | 924.2 | 302.1 | 349.5 | 365.8 | 334.3
1201.2 | 925.2 | 302.3 | 350 | 365.5 | 334.3
1202.2 | 926.2 | 302.5 | 350.3 | 365.2 | 334.4
1203.2 | 927.2 | 302.6 | 350.3 | 364.7 | 334.5
1204.2 | 928.2 | 302.7 | 350.3 | 364.3 | 334.6
1205.2 | 929.2 | 302.8 | 350.2 | 363.8 | 334.7
1206.2 | 930.2 | 303 | 350.1 | 363.5 | 334.8
1207.2 | 931.2 | 303.2 | 350.3 | 363.3 | 335
1208.2 | 932.2 | 303.3 | 350.8 | 363.4 | 335.2
1209.2 | 933.2 | 303.5 | 350.8 | 363.6 | 335.3
1210.2 | 934.2 | 303.8 | 351 | 363.9 | 335.3
1211.2 | 935.2 | 304 | 351 | 364 | 335.4
1212.2 | 936.2 | 304.1 | 351.2 | 364 | 335.5
1213.2 | 937.2 | 304.3 | 351.5 | 364 | 335.6
1214.2 | 938.2 | 304.4 | 351.7 | 364.3 | 335.8
1215.2 | 939.2 | 304.6 | 351.8 | 364.5 | 335.8
1216.2 | 940.2 | 304.8 | 351.9 | 364.1 | 335.9
1217.2 | 941.2 | 304.9 | 352.2 | 364.1 | 336.1
1218.2 | 942.2 | 305.1 | 352.7 | 364.6 | 336.3
1219.2 | 943.2 | 305.2 | 353.2 | 365.2 | 336.5
1220.2 | 944.2 | 305.3 | 354.2 | 366.1 | 336.8
1221.2 | 945.2 | 305.5 | 355.5 | 367.2 | 337.1
1222.2 | 946.2 | 305.7 | 356 | 367.7 | 337.5
1223.2 | 947.2 | 305.9 | 356.2 | 368 | 337.7
1224.2 | 948.2 | 306 | 356.6 | 368.3 | 337.9
1225.2 | 949.2 | 306.2 | 356.8 | 368.5 | 338.2
1226.2 | 950.2 | 306.4 | 356.7 | 368.3 | 338.3
1227.2 | 951.2 | 306.5 | 356.8 | 368.2 | 338.4
1228.2 | 952.2 | 306.7 | 357.1 | 368.4 | 338.5
1229.2 | 953.2 | 306.8 | 357 | 368.6 | 338.6
1230.2 | 954.2 | 307 | 357.1 | 369.1 | 338.6
1231.2 | 955.2 | 307.2 | 356.6 | 369 | 338.6
1232.2 | 956.2 | 307.4 | 356.1 | 369.1 | 338.6
1233.2 | 957.2 | 307.6 | 355.4 | 368.5 | 338.6
1234.2 | 958.2 | 307.8 | 355 | 368.2 | 338.6
1235.2 | 959.2 | 307.9 | 354.5 | 368.3 | 338.6
1236.2 | 960.2 | 308.1 | 354.2 | 368.6 | 338.6
1237.2 | 961.2 | 308.3 | 354.1 | 368.1 | 338.8
1238.2 | 962.2 | 308.5 | 353.5 | 367.4 | 338.7
1239.2 | 963.2 | 308.7 | 352.6 | 366.3 | 338.6
1240.2 | 964.2 | 308.9 | 352.3 | 365.6 | 338.6
1241.2 | 965.2 | 309 | 351.9 | 365.4 | 338.5
1242.2 | 966.2 | 309.2 | 351.4 | 365.1 | 338.5
1243.2 | 967.2 | 309.5 | 351 | 364.7 | 338.4
1244.2 | 968.2 | 309.6 | 350.7 | 364.6 | 338.4
1245.2 | 969.2 | 309.7 | 350.4 | 364.3 | 338.5
1246.2 | 970.2 | 310 | 350.1 | 364.1 | 338.4
1247.2 | 971.2 | 310.2 | 349.8 | 364.1 | 338.4
1248.2 | 972.2 | 310.4 | 349.5 | 363.7 | 338.4
1249.2 | 973.2 | 310.5 | 349 | 363.1 | 338.3
1250.2 | 974.2 | 310.8 | 348.5 | 362.7 | 338.2
1251.2 | 975.2 | 310.9 | 348.3 | 362.5 | 338.2
1252.2 | 976.2 | 311.1 | 348.1 | 362.1 | 338.2
1253.2 | 977.2 | 311.2 | 348 | 361.6 | 338.2
1254.2 | 978.2 | 311.4 | 347.8 | 361.3 | 338.3
1255.2 | 979.2 | 311.5 | 347.8 | 361.1 | 338.3
1256.2 | 980.2 | 311.6 | 347.7 | 360.9 | 338.4
1257.2 | 981.2 | 311.8 | 348 | 360.8 | 338.5
1258.2 | 982.2 | 312 | 348.5 | 361 | 338.7
1259.2 | 983.2 | 312.2 | 348.8 | 361.3 | 338.8
1260.2 | 984.2 | 312.5 | 349.6 | 362.2 | 338.9
1261.2 | 985.2 | 312.7 | 350.4 | 362.9 | 339
1262.2 | 986.2 | 312.8 | 351 | 363.5 | 339.1
1263.2 | 987.2 | 313 | 351.4 | 363.8 | 339.2
1264.2 | 988.2 | 313.1 | 351.5 | 363.9 | 339.3
1265.2 | 989.2 | 313.2 | 351.5 | 363.7 | 339.2
1266.2 | 990.2 | 313.2 | 351.3 | 363.4 | 339.2
1267.2 | 991.2 | 313.3 | 351.1 | 363.4 | 339.1
1268.2 | 992.2 | 313.4 | 351.4 | 363.5 | 339.1
1269.2 | 993.2 | 313.6 | 351.5 | 363.9 | 339.2
1270.2 | 994.2 | 313.7 | 351.2 | 364 | 339.1
1271.2 | 995.2 | 313.8 | 351.1 | 364 | 339.1
1272.2 | 996.2 | 313.8 | 351.2 | 364.2 | 339.1
1273.2 | 997.2 | 313.9 | 351 | 364.7 | 339.1
1274.2 | 998.2 | 314 | 350.8 | 364.8 | 339.1
1275.2 | 999.2 | 314.1 | 350.6 | 365.7 | 339.1
1276.2 | 1000.2 | 314.2 | 350.6 | 365.5 | 339.1
1277.2 | 1001.2 | 314.4 | 350.6 | 365.2 | 339.1
1278.2 | 1002.2 | 314.6 | 350.5 | 364.8 | 339.2
1279.2 | 1003.2 | 314.8 | 350.3 | 364.6 | 339.2
1280.2 | 1004.2 | 315 | 350.2 | 364.3 | 339.2
1281.2 | 1005.2 | 315.1 | 350 | 364.1 | 339.2
1282.2 | 1006.2 | 315.2 | 349.7 | 363.9 | 339.2
1283.2 | 1007.2 | 315.3 | 349.6 | 363.6 | 339.3
1284.2 | 1008.2 | 315.4 | 349.5 | 363.9 | 339.3
1285.2 | 1009.2 | 315.6 | 349.3 | 363.6 | 339.4
1286.2 | 1010.2 | 315.6 | 349.2 | 363.5 | 339.4
1287.2 | 1011.2 | 315.7 | 349.3 | 363.6 | 339.5
1288.2 | 1012.2 | 316 | 349.5 | 363.5 | 339.5
1289.2 | 1013.2 | 316.1 | 349.9 | 363.6 | 339.6
1290.2 | 1014.2 | 316.2 | 350 | 363.8 | 339.7
1291.2 | 1015.2 | 316.3 | 350.4 | 363.9 | 339.8
1292.2 | 1016.2 | 316.3 | 350.8 | 363.7 | 339.9
1293.2 | 1017.2 | 316.4 | 351.4 | 364 | 340
1294.2 | 1018.2 | 316.4 | 351.7 | 364.5 | 340.2
1295.2 | 1019.2 | 316.5 | 351.7 | 364.7 | 340.2
1296.2 | 1020.2 | 316.7 | 351.9 | 365.1 | 340.3
1297.2 | 1021.2 | 316.8 | 352.2 | 365 | 340.5
1298.2 | 1022.2 | 317 | 352.3 | 364.9 | 340.6
1299.2 | 1023.2 | 317.1 | 352.2 | 364.4 | 340.6
1300.2 | 1024.2 | 317.2 | 352 | 364 | 340.6
1301.2 | 1025.2 | 317.3 | 351.8 | 363.5 | 340.7
1302.2 | 1026.2 | 317.4 | 351.8 | 363.2 | 340.6
1303.2 | 1027.2 | 317.6 | 351.5 | 362.5 | 340.6
1304.2 | 1028.2 | 317.7 | 351.3 | 362 | 340.5
1305.2 | 1029.2 | 317.8 | 350.9 | 361.6 | 340.4
1306.2 | 1030.2 | 318 | 350.7 | 361.2 | 340.3
1307.2 | 1031.2 | 318.1 | 350.4 | 360.7 | 340.3
1308.2 | 1032.2 | 318.2 | 350 | 360.3 | 340.2
1309.2 | 1033.2 | 318.3 | 349.7 | 359.8 | 340.2
1310.2 | 1034.2 | 318.3 | 349.4 | 359.5 | 340.2
1311.2 | 1035.2 | 318.4 | 349.1 | 359.5 | 340.1
1312.2 | 1036.2 | 318.5 | 348.9 | 359.4 | 340.1
1313.2 | 1037.2 | 318.6 | 348.8 | 359.2 | 340
1314.2 | 1038.2 | 318.6 | 348.6 | 359 | 340
1315.2 | 1039.2 | 318.7 | 348.8 | 359.2 | 339.9
1316.2 | 1040.2 | 318.9 | 349.1 | 359.5 | 339.9
1317.2 | 1041.2 | 319 | 349.2 | 359.4 | 339.9
1318.2 | 1042.2 | 319.1 | 349.2 | 359.2 | 340
1319.2 | 1043.2 | 319.2 | 349.1 | 359.3 | 340
1320.2 | 1044.2 | 319.3 | 349.2 | 359.1 | 340
1321.2 | 1045.2 | 319.3 | 349.5 | 359.3 | 340.1
1322.2 | 1046.2 | 319.4 | 349.7 | 359.6 | 340.2
1323.2 | 1047.2 | 319.5 | 349.8 | 359.9 | 340.3
1324.2 | 1048.2 | 319.6 | 349.9 | 360.2 | 340.3
1325.2 | 1049.2 | 319.7 | 350.2 | 360.2 | 340.3
1326.2 | 1050.2 | 319.8 | 350.5 | 360.5 | 340.4
1327.2 | 1051.2 | 319.9 | 350.9 | 360.8 | 340.6
1328.2 | 1052.2 | 320 | 351.3 | 361.1 | 340.7
1329.2 | 1053.2 | 320.1 | 351.7 | 361.7 | 340.9
1330.2 | 1054.2 | 320.2 | 352.2 | 362.5 | 341
1331.2 | 1055.2 | 320.3 | 352.8 | 363.3 | 341.1
1332.2 | 1056.2 | 320.4 | 353.8 | 364.1 | 341.3
1333.2 | 1057.2 | 320.5 | 354.8 | 365.6 | 341.5
1334.2 | 1058.2 | 320.6 | 355.2 | 366.3 | 341.6
1335.2 | 1059.2 | 320.7 | 355.3 | 367 | 341.6
1336.2 | 1060.2 | 320.8 | 355.6 | 368.3 | 341.7
1337.2 | 1061.2 | 321 | 355.3 | 368.4 | 341.8
1338.2 | 1062.2 | 321.1 | 354.9 | 368.2 | 341.8
1339.2 | 1063.2 | 321.2 | 354.6 | 368.1 | 341.7
1340.2 | 1064.2 | 321.4 | 354.2 | 367.9 | 341.7
1341.2 | 1065.2 | 321.5 | 354 | 367.9 | 341.7
1342.2 | 1066.2 | 321.6 | 354 | 368 | 341.7
1343.2 | 1067.2 | 321.8 | 354.3 | 368.1 | 341.8
1344.2 | 1068.2 | 321.9 | 354.8 | 368.3 | 341.9
1345.2 | 1069.2 | 322.1 | 354.9 | 368.3 | 342
1346.2 | 1070.2 | 322.3 | 354.6 | 367.7 | 342
1347.2 | 1071.2 | 322.5 | 354.3 | 367.1 | 342
1348.2 | 1072.2 | 322.7 | 354.1 | 366.7 | 342
1349.2 | 1073.2 | 322.8 | 354 | 366.8 | 342
1350.2 | 1074.2 | 323 | 354 | 366.6 | 342
1351.2 | 1075.2 | 323.2 | 353.9 | 366.5 | 342.2
1352.2 | 1076.2 | 323.3 | 353.8 | 366.2 | 342.2
1353.2 | 1077.2 | 323.4 | 353.5 | 365.8 | 342.2
1354.2 | 1078.2 | 323.5 | 353.2 | 365.9 | 342.2
1355.2 | 1079.2 | 323.7 | 353 | 365.7 | 342.2
1356.2 | 1080.2 | 323.8 | 352.8 | 365.3 | 342.3
1357.2 | 1081.2 | 323.9 | 353.2 | 366 | 342.4
1358.2 | 1082.2 | 324 | 353.6 | 366 | 342.5
1359.2 | 1083.2 | 324.2 | 353.7 | 366.3 | 342.6
1360.2 | 1084.2 | 324.2 | 354.2 | 367.1 | 342.6
1361.2 | 1085.2 | 324.3 | 354.5 | 367.3 | 342.7
1362.2 | 1086.2 | 324.4 | 354.6 | 367 | 342.7
1363.2 | 1087.2 | 324.5 | 354.7 | 366.7 | 342.8
1364.2 | 1088.2 | 324.7 | 354.5 | 366.5 | 342.8
1365.2 | 1089.2 | 324.9 | 354.3 | 366 | 342.7
1366.2 | 1090.2 | 325 | 354.2 | 365.5 | 342.7
1367.2 | 1091.2 | 325.1 | 354.1 | 365.2 | 342.6
1368.2 | 1092.2 | 325.2 | 354.1 | 365.4 | 342.7
1369.2 | 1093.2 | 325.4 | 354 | 365.1 | 342.7
1370.2 | 1094.2 | 325.6 | 353.8 | 365 | 342.7
1371.2 | 1095.2 | 325.7 | 353.5 | 365.3 | 342.6
1372.2 | 1096.2 | 325.7 | 353.3 | 365.9 | 342.6
1373.2 | 1097.2 | 325.8 | 353.3 | 366.3 | 342.7
1374.2 | 1098.2 | 325.8 | 353.3 | 366.2 | 342.7
1375.2 | 1099.2 | 325.9 | 353.4 | 368 | 342.7
1376.2 | 1100.2 | 326 | 353.5 | 368.4 | 342.8
1377.2 | 1101.2 | 326.1 | 353.4 | 368.5 | 342.8
1378.2 | 1102.2 | 326.2 | 353.5 | 368.9 | 342.9
1379.2 | 1103.2 | 326.2 | 353.5 | 368.9 | 343
1380.2 | 1104.2 | 326.4 | 353.6 | 368.7 | 343
1381.2 | 1105.2 | 326.4 | 353.4 | 368.3 | 343
1382.2 | 1106.2 | 326.5 | 353.3 | 368.5 | 343
1383.2 | 1107.2 | 326.7 | 353.2 | 368.6 | 343.1
1384.2 | 1108.2 | 326.8 | 353.1 | 368.3 | 343.1
1385.2 | 1109.2 | 326.9 | 353 | 367.8 | 343
1386.2 | 1110.2 | 327 | 352.8 | 367.8 | 343
1387.2 | 1111.2 | 327.2 | 352.4 | 367.7 | 342.9
1388.2 | 1112.2 | 327.4 | 352.1 | 367.4 | 343
1389.2 | 1113.2 | 327.5 | 352.1 | 366.9 | 343
1390.2 | 1114.2 | 327.6 | 352 | 366.4 | 343
1391.2 | 1115.2 | 327.6 | 352.1 | 365.8 | 343
1392.2 | 1116.2 | 327.7 | 352.1 | 365.3 | 343
1393.2 | 1117.2 | 327.9 | 352.1 | 365.1 | 343
1394.2 | 1118.2 | 328 | 352.4 | 365.2 | 343
1395.2 | 1119.2 | 328.1 | 352.6 | 365.1 | 343
1396.2 | 1120.2 | 328.2 | 352.6 | 365.1 | 343
1397.2 | 1121.2 | 328.2 | 352.7 | 365.3 | 343.1
1398.2 | 1122.2 | 328.3 | 353.2 | 365.5 | 343.2
1399.2 | 1123.2 | 328.5 | 353.7 | 365.8 | 343.3
1400.2 | 1124.2 | 328.6 | 353.9 | 365.9 | 343.4
1401.2 | 1125.2 | 328.6 | 354 | 365.8 | 343.5
1402.2 | 1126.2 | 328.7 | 353.8 | 365.8 | 343.4
1403.2 | 1127.2 | 328.8 | 353.5 | 365.9 | 343.4
1404.2 | 1128.2 | 329 | 353.3 | 365.9 | 343.3
1405.2 | 1129.2 | 329.1 | 353.2 | 366.2 | 343.4
1406.2 | 1130.2 | 329.2 | 353.2 | 366.7 | 343.3
1407.2 | 1131.2 | 329.3 | 353.2 | 367.2 | 343.4
1408.2 | 1132.2 | 329.4 | 353.2 | 367.5 | 343.5
1409.2 | 1133.2 | 329.5 | 353.2 | 367.4 | 343.5
1410.2 | 1134.2 | 329.6 | 353.1 | 367.4 | 343.5
1411.2 | 1135.2 | 329.7 | 353.3 | 367.4 | 343.5
1412.2 | 1136.2 | 329.8 | 353.5 | 369.2 | 343.5
1413.2 | 1137.2 | 330 | 353.7 | 369.5 | 343.5
1414.2 | 1138.2 | 330.1 | 354 | 369.1 | 343.7
1415.2 | 1139.2 | 330.3 | 354.4 | 369 | 343.8
1416.2 | 1140.2 | 330.4 | 354.8 | 368.9 | 343.9
1417.2 | 1141.2 | 330.5 | 354.9 | 369 | 344.1
1418.2 | 1142.2 | 330.7 | 354.9 | 368.9 | 344.2
1419.2 | 1143.2 | 330.8 | 355.1 | 368.7 | 344.2
1420.2 | 1144.2 | 330.9 | 355.5 | 368.5 | 344.3
1421.2 | 1145.2 | 331 | 355.8 | 368.9 | 344.4
1422.2 | 1146.2 | 331.2 | 356.1 | 369.1 | 344.5
1423.2 | 1147.2 | 331.3 | 356.1 | 369.2 | 344.6
1424.2 | 1148.2 | 331.5 | 356.2 | 369.3 | 344.6
1425.2 | 1149.2 | 331.6 | 356.2 | 369.2 | 344.6
1426.2 | 1150.2 | 331.7 | 356.6 | 369.5 | 344.6
1427.2 | 1151.2 | 331.8 | 356.9 | 369.7 | 344.6
1428.2 | 1152.2 | 331.9 | 356.9 | 369.9 | 344.7
1429.2 | 1153.2 | 332 | 356.8 | 370.2 | 344.7
1430.2 | 1154.2 | 332.2 | 356.7 | 370.3 | 344.7
1431.2 | 1155.2 | 332.3 | 356.6 | 370.6 | 344.8
1432.2 | 1156.2 | 332.4 | 356.5 | 370.7 | 344.8
1433.2 | 1157.2 | 332.6 | 356.4 | 370.8 | 344.8
1434.2 | 1158.2 | 332.7 | 356.5 | 371 | 344.8
1435.2 | 1159.2 | 332.8 | 356.6 | 371.2 | 344.9
1436.2 | 1160.2 | 332.9 | 356.7 | 371.1 | 345
1437.2 | 1161.2 | 333.1 | 356.6 | 371.1 | 345
1438.2 | 1162.2 | 333.2 | 356.6 | 371.1 | 345
1439.2 | 1163.2 | 333.3 | 356.5 | 371.1 | 345.1
1440.2 | 1164.2 | 333.5 | 356.5 | 370.8 | 345.2
1441.2 | 1165.2 | 333.7 | 356.3 | 370.2 | 345.3
1442.2 | 1166.2 | 333.9 | 356.1 | 369.7 | 345.3
1443.2 | 1167.2 | 334 | 355.9 | 369.2 | 345.2
1444.2 | 1168.2 | 334.2 | 355.7 | 368.6 | 345.3
1445.2 | 1169.2 | 334.3 | 355.6 | 368.2 | 345.4
1446.2 | 1170.2 | 334.4 | 355.3 | 368.5 | 345.3
1447.2 | 1171.2 | 334.5 | 355 | 368.2 | 345.4
1448.2 | 1172.2 | 334.6 | 354.8 | 367.8 | 345.4
1449.2 | 1173.2 | 334.7 | 354.8 | 367.4 | 345.4
1450.2 | 1174.2 | 334.8 | 355.3 | 367.4 | 345.4
1451.2 | 1175.2 | 334.9 | 355.8 | 367.6 | 345.5
1452.2 | 1176.2 | 335 | 355.9 | 367.4 | 345.5
1453.2 | 1177.2 | 335.2 | 356.1 | 367.4 | 345.5
1454.2 | 1178.2 | 335.2 | 356.3 | 367.9 | 345.6
1455.2 | 1179.2 | 335.3 | 356.4 | 368 | 345.7
1456.2 | 1180.2 | 335.4 | 356.3 | 367.6 | 345.7
1457.2 | 1181.2 | 335.5 | 356.1 | 367.3 | 345.7
1458.2 | 1182.2 | 335.6 | 355.9 | 366.8 | 345.7
1459.2 | 1183.2 | 335.7 | 355.5 | 366.2 | 345.6
1460.2 | 1184.2 | 335.8 | 355.2 | 365.9 | 345.6
1461.2 | 1185.2 | 335.9 | 355.2 | 365.7 | 345.5
1462.2 | 1186.2 | 336 | 355.2 | 365.6 | 345.5
1463.2 | 1187.2 | 336.1 | 355.5 | 365.3 | 345.6
1464.2 | 1188.2 | 336.2 | 355.7 | 364.9 | 345.6
1465.2 | 1189.2 | 336.2 | 356 | 364.6 | 345.5
1466.2 | 1190.2 | 336.3 | 356.5 | 364.9 | 345.5
1467.2 | 1191.2 | 336.3 | 357.1 | 365.2 | 345.6
1468.2 | 1192.2 | 336.4 | 357.7 | 365 | 345.6
1469.2 | 1193.2 | 336.5 | 358.1 | 365.1 | 345.6
1470.2 | 1194.2 | 336.5 | 358.3 | 365 | 345.7
1471.2 | 1195.2 | 336.6 | 358.5 | 365 | 345.7
1472.2 | 1196.2 | 336.7 | 358.8 | 365.2 | 345.8
1473.2 | 1197.2 | 336.7 | 359.1 | 365.6 | 345.8
1474.2 | 1198.2 | 336.8 | 359.8 | 366.2 | 346.1
1475.2 | 1199.2 | 336.9 | 360.5 | 367 | 346.2
1476.2 | 1200.2 | 337 | 361.2 | 367.4 | 346.4
1477.2 | 1201.2 | 337.1 | 361.9 | 367.9 | 346.6
1478.2 | 1202.2 | 337.2 | 362.3 | 368.3 | 346.7
1479.2 | 1203.2 | 337.3 | 362.8 | 368.8 | 346.8
1480.2 | 1204.2 | 337.4 | 363.3 | 369.1 | 346.9
1481.2 | 1205.2 | 337.5 | 363.7 | 369.8 | 347
1482.2 | 1206.2 | 337.6 | 364.1 | 370.2 | 347.1
1483.2 | 1207.2 | 337.7 | 364.6 | 371.3 | 347.2
1484.2 | 1208.2 | 337.8 | 365.1 | 372 | 347.2
1485.2 | 1209.2 | 338 | 365.8 | 372.8 | 347.4
1486.2 | 1210.2 | 338.1 | 366.6 | 373.8 | 347.7
1487.2 | 1211.2 | 338.2 | 367.1 | 374.8 | 347.9
1488.2 | 1212.2 | 338.3 | 367.5 | 375.5 | 348
1489.2 | 1213.2 | 338.4 | 367.9 | 376.1 | 348
1490.2 | 1214.2 | 338.6 | 367.9 | 376.3 | 348.1
1491.2 | 1215.2 | 338.8 | 368.1 | 376.3 | 348.1
1492.2 | 1216.2 | 339 | 368.3 | 376.3 | 348.2
1493.2 | 1217.2 | 339.2 | 368.4 | 376 | 348.3
1494.2 | 1218.2 | 339.3 | 368.3 | 375.8 | 348.2
1495.2 | 1219.2 | 339.4 | 368.1 | 375.5 | 348.2
1496.2 | 1220.2 | 339.6 | 368 | 374.9 | 348.2
1497.2 | 1221.2 | 339.7 | 368 | 374.3 | 348.3
1498.2 | 1222.2 | 339.9 | 367.8 | 373.8 | 348.3
1499.2 | 1223.2 | 340 | 367.9 | 373.6 | 348.4
1500.2 | 1224.2 | 340.2 | 367.6 | 373.3 | 348.4
1501.2 | 1225.2 | 340.3 | 367.6 | 373.1 | 348.5
1502.2 | 1226.2 | 340.4 | 367.3 | 373.1 | 348.5
1503.2 | 1227.2 | 340.5 | 367.2 | 373.1 | 348.5
1504.2 | 1228.2 | 340.7 | 367.2 | 373.1 | 348.6
1505.2 | 1229.2 | 340.8 | 367.2 | 372.9 | 348.6
1506.2 | 1230.2 | 340.9 | 367.2 | 372.7 | 348.6
1507.2 | 1231.2 | 341 | 367 | 372.4 | 348.5
1508.2 | 1232.2 | 341.1 | 366.8 | 372.1 | 348.5
1509.2 | 1233.2 | 341.2 | 366.7 | 371.9 | 348.4
1510.2 | 1234.2 | 341.3 | 366.6 | 371.8 | 348.4
1511.2 | 1235.2 | 341.4 | 366.5 | 371.5 | 348.4
1512.2 | 1236.2 | 341.5 | 366.4 | 371.5 | 348.4
1513.2 | 1237.2 | 341.6 | 366.2 | 371.4 | 348.4
1514.2 | 1238.2 | 341.7 | 365.9 | 372 | 348.4
1515.2 | 1239.2 | 341.8 | 365.7 | 371.7 | 348.4
1516.2 | 1240.2 | 341.9 | 365.7 | 371.6 | 348.4
1517.2 | 1241.2 | 341.9 | 365.7 | 371.6 | 348.5
1518.2 | 1242.2 | 342 | 365.7 | 371.7 | 348.6
1519.2 | 1243.2 | 342.1 | 365.7 | 371.3 | 348.6
1520.2 | 1244.2 | 342.2 | 365.6 | 371 | 348.6
1521.2 | 1245.2 | 342.3 | 365.5 | 370.6 | 348.6
1522.2 | 1246.2 | 342.4 | 365.4 | 370.3 | 348.6
1523.2 | 1247.2 | 342.5 | 365.2 | 370.2 | 348.6
1524.2 | 1248.2 | 342.6 | 364.9 | 370.3 | 348.5
1525.2 | 1249.2 | 342.7 | 364.8 | 370 | 348.5
1526.2 | 1250.2 | 342.7 | 364.6 | 369.5 | 348.5
1527.2 | 1251.2 | 342.8 | 364.5 | 369.2 | 348.5
1528.2 | 1252.2 | 342.9 | 364.4 | 369.1 | 348.5
1529.2 | 1253.2 | 343 | 364.1 | 368.6 | 348.4
1530.2 | 1254.2 | 343.1 | 363.9 | 368.2 | 348.4
1531.2 | 1255.2 | 343.2 | 363.7 | 367.8 | 348.3
1532.2 | 1256.2 | 343.3 | 363.5 | 367.6 | 348.2
1533.2 | 1257.2 | 343.4 | 363.3 | 367.3 | 348.2
1534.2 | 1258.2 | 343.4 | 363.2 | 366.8 | 348.2
1535.2 | 1259.2 | 343.5 | 363.1 | 366.2 | 348.1
1536.2 | 1260.2 | 343.6 | 363 | 365.8 | 348
1537.2 | 1261.2 | 343.7 | 363 | 365.8 | 348
1538.2 | 1262.2 | 343.7 | 362.9 | 366.1 | 348
1539.2 | 1263.2 | 343.8 | 362.8 | 365.9 | 348
1540.2 | 1264.2 | 343.8 | 362.8 | 365.6 | 348
1541.2 | 1265.2 | 343.9 | 362.5 | 365.3 | 348
1542.2 | 1266.2 | 343.9 | 362.4 | 365.4 | 347.9
1543.2 | 1267.2 | 344 | 362.3 | 365.4 | 347.9
1544.2 | 1268.2 | 344.1 | 362.3 | 365.2 | 347.8
1545.2 | 1269.2 | 344.1 | 362.3 | 365.2 | 347.8
1546.2 | 1270.2 | 344.2 | 362.3 | 365.2 | 347.8
1547.2 | 1271.2 | 344.2 | 362.5 | 365.2 | 347.9
1548.2 | 1272.2 | 344.3 | 362.6 | 365.2 | 348
1549.2 | 1273.2 | 344.3 | 362.7 | 365.2 | 348
1550.2 | 1274.2 | 344.4 | 362.8 | 365 | 348.1
1551.2 | 1275.2 | 344.5 | 362.8 | 365 | 348.1
1552.2 | 1276.2 | 344.5 | 362.9 | 364.9 | 348
1553.2 | 1277.2 | 344.6 | 362.9 | 365.2 | 348
1554.2 | 1278.2 | 344.7 | 363 | 365.3 | 347.9
1555.2 | 1279.2 | 344.7 | 363 | 365.5 | 348
1556.2 | 1280.2 | 344.8 | 363 | 365.5 | 347.9
1557.2 | 1281.2 | 344.8 | 363 | 365.4 | 348
1558.2 | 1282.2 | 344.9 | 363 | 365.8 | 348
1559.2 | 1283.2 | 344.9 | 362.8 | 365.6 | 347.9
1560.2 | 1284.2 | 345 | 362.7 | 365.4 | 347.9
1561.2 | 1285.2 | 345 | 362.6 | 365 | 347.8
1562.2 | 1286.2 | 345.1 | 362.6 | 364.8 | 347.7
1563.2 | 1287.2 | 345.2 | 362.5 | 364.5 | 347.7
1564.2 | 1288.2 | 345.3 | 362.6 | 364.4 | 347.7
1565.2 | 1289.2 | 345.4 | 362.3 | 364.1 | 347.6
1566.2 | 1290.2 | 345.4 | 362 | 363.7 | 347.5
1567.2 | 1291.2 | 345.5 | 361.9 | 364 | 347.4
1568.2 | 1292.2 | 345.5 | 361.6 | 363.8 | 347.4
1569.2 | 1293.2 | 345.6 | 361.5 | 363.6 | 347.3
1570.2 | 1294.2 | 345.7 | 361.4 | 363.2 | 347.3
1571.2 | 1295.2 | 345.7 | 361.3 | 363 | 347.2
1572.2 | 1296.2 | 345.8 | 361.2 | 362.9 | 347.2
1573.2 | 1297.2 | 345.8 | 361.1 | 362.6 | 347.2
1574.2 | 1298.2 | 345.9 | 361 | 362.4 | 347.1
1575.2 | 1299.2 | 345.9 | 360.9 | 362.4 | 347.1
1576.2 | 1300.2 | 345.9 | 360.8 | 362.5 | 347
1577.2 | 1301.2 | 346 | 360.7 | 362.2 | 347
1578.2 | 1302.2 | 346.1 | 360.5 | 362 | 346.9
1579.2 | 1303.2 | 346.1 | 360.5 | 361.8 | 346.9
1580.2 | 1304.2 | 346.2 | 360.6 | 361.6 | 346.9
1581.2 | 1305.2 | 346.2 | 360.7 | 361.5 | 346.9
1582.2 | 1306.2 | 346.2 | 360.7 | 361.5 | 347
1583.2 | 1307.2 | 346.3 | 360.8 | 361.5 | 347
1584.2 | 1308.2 | 346.3 | 360.7 | 361.4 | 347
1585.2 | 1309.2 | 346.4 | 360.6 | 361.3 | 346.9
1586.2 | 1310.2 | 346.4 | 360.5 | 361.4 | 346.9
1587.2 | 1311.2 | 346.4 | 360.4 | 361.9 | 346.9
1588.2 | 1312.2 | 346.4 | 360.3 | 361.6 | 346.9
1589.2 | 1313.2 | 346.5 | 360.4 | 361.5 | 346.9
1590.2 | 1314.2 | 346.5 | 360.5 | 361.4 | 346.9
1591.2 | 1315.2 | 346.6 | 360.6 | 361.6 | 347
1592.2 | 1316.2 | 346.7 | 360.5 | 361.6 | 347
1593.2 | 1317.2 | 346.7 | 360.5 | 361.5 | 346.9
1594.2 | 1318.2 | 346.8 | 360.5 | 361.7 | 346.8
1595.2 | 1319.2 | 346.8 | 360.5 | 361.7 | 346.9
1596.2 | 1320.2 | 346.9 | 360.4 | 361.6 | 346.9
1597.2 | 1321.2 | 346.9 | 360.4 | 361.6 | 346.9
1598.2 | 1322.2 | 346.9 | 360.5 | 361.5 | 346.9
1599.2 | 1323.2 | 347 | 360.5 | 361.6 | 346.9
1600.2 | 1324.2 | 347.1 | 360.6 | 361.5 | 346.9
1601.2 | 1325.2 | 347.1 | 360.7 | 361.5 | 347
1602.2 | 1326.2 | 347.2 | 361.1 | 361.7 | 347.1
1603.2 | 1327.2 | 347.3 | 361.1 | 361.7 | 347.1
1604.2 | 1328.2 | 347.3 | 361.1 | 361.7 | 347.1
1605.2 | 1329.2 | 347.3 | 361.2 | 361.9 | 347.2
1606.2 | 1330.2 | 347.4 | 361.3 | 362.1 | 347.3
1607.2 | 1331.2 | 347.5 | 361.3 | 362.2 | 347.3
1608.2 | 1332.2 | 347.5 | 361.4 | 362.3 | 347.4
1609.2 | 1333.2 | 347.5 | 361.5 | 362.3 | 347.4
1610.2 | 1334.2 | 347.6 | 362 | 362.6 | 347.5
1611.2 | 1335.2 | 347.7 | 362.4 | 362.7 | 347.6
1612.2 | 1336.2 | 347.7 | 362.5 | 362.7 | 347.6
1613.2 | 1337.2 | 347.8 | 362.6 | 362.7 | 347.6
1614.2 | 1338.2 | 347.9 | 362.6 | 362.7 | 347.6
1615.2 | 1339.2 | 347.9 | 362.5 | 362.5 | 347.5
1616.2 | 1340.2 | 348 | 362.1 | 361.9 | 347.4
1617.2 | 1341.2 | 348 | 361.8 | 361.4 | 347.3
1618.2 | 1342.2 | 348.1 | 361.8 | 361.3 | 347.3
1619.2 | 1343.2 | 348.2 | 361.6 | 361 | 347.2
1620.2 | 1344.2 | 348.2 | 361.3 | 360.6 | 347.1
1621.2 | 1345.2 | 348.2 | 361.1 | 360.2 | 347.1
1622.2 | 1346.2 | 348.3 | 360.7 | 360 | 347
1623.2 | 1347.2 | 348.3 | 360.4 | 359.8 | 347
1624.2 | 1348.2 | 348.4 | 360.2 | 359.6 | 346.9
1625.2 | 1349.2 | 348.4 | 360.1 | 359.5 | 346.8
1626.2 | 1350.2 | 348.4 | 360.1 | 359.5 | 346.8
1627.2 | 1351.2 | 348.5 | 360 | 359.6 | 346.7
1628.2 | 1352.2 | 348.5 | 360 | 359.8 | 346.7
1629.2 | 1353.2 | 348.6 | 359.9 | 359.8 | 346.7
1630.2 | 1354.2 | 348.6 | 359.7 | 359.6 | 346.6
1631.2 | 1355.2 | 348.7 | 359.3 | 359 | 346.5
1632.2 | 1356.2 | 348.7 | 358.8 | 357.5 | 346.3
1633.2 | 1357.2 | 348.8 | 358.3 | 356.6 | 346.2
1634.2 | 1358.2 | 348.8 | 357.7 | 355.8 | 346
1635.2 | 1359.2 | 348.8 | 357.2 | 355.6 | 345.9
1636.2 | 1360.2 | 348.9 | 356.8 | 355.6 | 345.7
1637.2 | 1361.2 | 348.9 | 356.6 | 355.3 | 345.6
1638.2 | 1362.2 | 348.9 | 356.3 | 355.1 | 345.5
1639.2 | 1363.2 | 348.9 | 356.1 | 355 | 345.5
1640.2 | 1364.2 | 348.9 | 355.9 | 354.9 | 345.4
1641.2 | 1365.2 | 348.9 | 355.7 | 355.1 | 345.3
1642.2 | 1366.2 | 348.9 | 355.7 | 355.4 | 345.2
1643.2 | 1367.2 | 349 | 355.5 | 355.4 | 345.2
1644.2 | 1368.2 | 349 | 355.5 | 356 | 345.2
1645.2 | 1369.2 | 349 | 355.4 | 356.1 | 345.3
1646.2 | 1370.2 | 349 | 355.6 | 356.3 | 345.3
1647.2 | 1371.2 | 349 | 355.6 | 356.4 | 345.3
1648.2 | 1372.2 | 349 | 355.6 | 356.5 | 345.3
1649.2 | 1373.2 | 349 | 355.5 | 356.3 | 345.2
1650.2 | 1374.2 | 349 | 355.3 | 356.1 | 345.1
1651.2 | 1375.2 | 349.1 | 355.2 | 355.9 | 345.1
1652.2 | 1376.2 | 349.1 | 355.3 | 355.8 | 345.1
1653.2 | 1377.2 | 349.1 | 355.2 | 355.7 | 345.2
1654.2 | 1378.2 | 349.2 | 355.1 | 355.8 | 345.1
1655.2 | 1379.2 | 349.2 | 355.2 | 355.8 | 345.1
1656.2 | 1380.2 | 349.3 | 355.3 | 356.1 | 345.3
1657.2 | 1381.2 | 349.3 | 355.3 | 356.4 | 345.3
1658.2 | 1382.2 | 349.3 | 355.9 | 356.8 | 345.4
1659.2 | 1383.2 | 349.3 | 356.3 | 357.2 | 345.5
1660.2 | 1384.2 | 349.3 | 356.7 | 357.4 | 345.6
1661.2 | 1385.2 | 349.4 | 357.1 | 357.8 | 345.6
1662.2 | 1386.2 | 349.4 | 357.2 | 358.1 | 345.6
1663.2 | 1387.2 | 349.4 | 357.4 | 358.2 | 345.6
1664.2 | 1388.2 | 349.6 | 357.4 | 358.3 | 345.5
1665.2 | 1389.2 | 349.6 | 357.2 | 358.3 | 345.4
1666.2 | 1390.2 | 349.7 | 357 | 358.2 | 345.3
1667.2 | 1391.2 | 349.7 | 356.9 | 358.1 | 345.2
1668.2 | 1392.2 | 349.7 | 356.7 | 358.2 | 345.1
1669.2 | 1393.2 | 349.8 | 356.6 | 358.1 | 345
1670.2 | 1394.2 | 349.9 | 356.4 | 358 | 344.9
1671.2 | 1395.2 | 349.9 | 356.3 | 357.8 | 344.9
1672.2 | 1396.2 | 350 | 356.1 | 357.7 | 344.7
1673.2 | 1397.2 | 350.1 | 355.9 | 357.6 | 344.6
1674.2 | 1398.2 | 350.1 | 355.8 | 357.7 | 344.5
1675.2 | 1399.2 | 350.2 | 355.6 | 357.9 | 344.5
1676.2 | 1400.2 | 350.2 | 355.4 | 358 | 344.3
1677.2 | 1401.2 | 350.3 | 355.4 | 358.2 | 344.3
1678.2 | 1402.2 | 350.3 | 355.4 | 358.4 | 344.2
1679.2 | 1403.2 | 350.4 | 355.3 | 358.7 | 344.2
1680.2 | 1404.2 | 350.4 | 355.3 | 358.9 | 344.1
1681.2 | 1405.2 | 350.5 | 355.3 | 359 | 344.1
1682.2 | 1406.2 | 350.5 | 355.3 | 359.2 | 344
1683.2 | 1407.2 | 350.6 | 355.1 | 359.3 | 344
1684.2 | 1408.2 | 350.7 | 354.9 | 359.2 | 343.9
1685.2 | 1409.2 | 350.7 | 354.6 | 358.8 | 343.9
1686.2 | 1410.2 | 350.8 | 354.5 | 359.4 | 343.8
1687.2 | 1411.2 | 350.9 | 354.1 | 359.2 | 343.7
1688.2 | 1412.2 | 350.9 | 353.7 | 358.8 | 343.6
1689.2 | 1413.2 | 351 | 353.3 | 359 | 343.5
1690.2 | 1414.2 | 351.1 | 353.1 | 358.8 | 343.4
1691.2 | 1415.2 | 351.2 | 352.8 | 358.8 | 343.3
1692.2 | 1416.2 | 351.2 | 352.4 | 358.9 | 343.1
1693.2 | 1417.2 | 351.3 | 352.2 | 358.9 | 343.1
1694.2 | 1418.2 | 351.3 | 352.1 | 358.9 | 343.1
1695.2 | 1419.2 | 351.4 | 352.2 | 358.9 | 343.1
1696.2 | 1420.2 | 351.4 | 352.2 | 358.7 | 343.1
1697.2 | 1421.2 | 351.4 | 352 | 358.5 | 342.9
1698.2 | 1422.2 | 351.5 | 351.9 | 358.4 | 342.9
1699.2 | 1423.2 | 351.5 | 351.9 | 358.4 | 342.8
1700.2 | 1424.2 | 351.6 | 352 | 358.3 | 342.8
1701.2 | 1425.2 | 351.6 | 351.9 | 358.2 | 342.7
1702.2 | 1426.2 | 351.7 | 351.7 | 358.1 | 342.7
1703.2 | 1427.2 | 351.7 | 351.6 | 358 | 342.7
1704.2 | 1428.2 | 351.7 | 351.5 | 358 | 342.7
1705.2 | 1429.2 | 351.8 | 351.5 | 357.8 | 342.6
1706.2 | 1430.2 | 351.8 | 351.5 | 357.5 | 342.6
1707.2 | 1431.2 | 351.9 | 351.6 | 357.5 | 342.5
1708.2 | 1432.2 | 351.9 | 351.6 | 357.3 | 342.5
1709.2 | 1433.2 | 351.9 | 351.6 | 357.1 | 342.6
1710.2 | 1434.2 | 352 | 351.5 | 357 | 342.5
1711.2 | 1435.2 | 352 | 351.5 | 357 | 342.5
1712.2 | 1436.2 | 352 | 351.6 | 357.3 | 342.5
1713.2 | 1437.2 | 352.1 | 351.7 | 357.3 | 342.6
1714.2 | 1438.2 | 352.1 | 351.4 | 357.3 | 342.5
1715.2 | 1439.2 | 352.1 | 351.3 | 357.5 | 342.4
1716.2 | 1440.2 | 352.2 | 351.3 | 357.8 | 342.4
1717.2 | 1441.2 | 352.2 | 351.4 | 357.8 | 342.4
1718.2 | 1442.2 | 352.2 | 351.4 | 357.7 | 342.4
1719.2 | 1443.2 | 352.3 | 351.4 | 357.6 | 342.4
1720.2 | 1444.2 | 352.3 | 351.4 | 357.5 | 342.4
1721.2 | 1445.2 | 352.3 | 351.2 | 357.3 | 342.3
1722.2 | 1446.2 | 352.4 | 351.1 | 357.1 | 342.2
1723.2 | 1447.2 | 352.4 | 350.9 | 357 | 342.2
1724.2 | 1448.2 | 352.4 | 351 | 357 | 342.2
1725.2 | 1449.2 | 352.5 | 351.1 | 357.1 | 342.2
1726.2 | 1450.2 | 352.5 | 351.1 | 357.1 | 342.1
1727.2 | 1451.2 | 352.5 | 351.1 | 357.1 | 342.1
1728.2 | 1452.2 | 352.6 | 351.2 | 357 | 342.1
1729.2 | 1453.2 | 352.6 | 351.2 | 356.9 | 342
1730.2 | 1454.2 | 352.6 | 351.1 | 357 | 342
1731.2 | 1455.2 | 352.6 | 351.2 | 357.4 | 341.9
1732.2 | 1456.2 | 352.7 | 351.2 | 358 | 341.8
1733.2 | 1457.2 | 352.7 | 351.2 | 358.3 | 341.7
1734.2 | 1458.2 | 352.7 | 351.1 | 358.4 | 341.7
1735.2 | 1459.2 | 352.7 | 351 | 358.4 | 341.7
1736.2 | 1460.2 | 352.8 | 350.9 | 358 | 341.7
1737.2 | 1461.2 | 352.8 | 350.9 | 357.8 | 341.7
1738.2 | 1462.2 | 352.9 | 350.9 | 357.7 | 341.7
1739.2 | 1463.2 | 352.9 | 351 | 357.6 | 341.8
1740.2 | 1464.2 | 352.9 | 351.2 | 358 | 341.8
1741.2 | 1465.2 | 353 | 351.2 | 357.8 | 341.8
1742.2 | 1466.2 | 353 | 351 | 357.6 | 341.8
1743.2 | 1467.2 | 353.1 | 350.8 | 357.4 | 341.7
1744.2 | 1468.2 | 353.1 | 350.7 | 357.1 | 341.7
1745.2 | 1469.2 | 353.1 | 350.9 | 356.9 | 341.8
1746.2 | 1470.2 | 353.2 | 351.1 | 356.8 | 341.9
1747.2 | 1471.2 | 353.2 | 351.2 | 356.7 | 341.9
1748.2 | 1472.2 | 353.2 | 351.3 | 356.6 | 342
1749.2 | 1473.2 | 353.3 | 351.7 | 356.7 | 342.1
1750.2 | 1474.2 | 353.3 | 352 | 357.1 | 342.2
1751.2 | 1475.2 | 353.3 | 352.4 | 357.5 | 342.3
1752.2 | 1476.2 | 353.3 | 352.9 | 357.8 | 342.4
1753.2 | 1477.2 | 353.3 | 353.4 | 358.2 | 342.5
1754.2 | 1478.2 | 353.4 | 353.6 | 358.6 | 342.6
1755.2 | 1479.2 | 353.4 | 354.1 | 358.7 | 342.7
1756.2 | 1480.2 | 353.4 | 354.5 | 359.1 | 342.8
1757.2 | 1481.2 | 353.4 | 354.5 | 359.2 | 342.9
1758.2 | 1482.2 | 353.5 | 354.4 | 359 | 342.9
1759.2 | 1483.2 | 353.5 | 354.5 | 358.9 | 342.9
1760.2 | 1484.2 | 353.5 | 354.4 | 358.8 | 342.9
1761.2 | 1485.2 | 353.6 | 354.4 | 358.8 | 342.9
1762.2 | 1486.2 | 353.6 | 354.5 | 359.3 | 342.9
1763.2 | 1487.2 | 353.7 | 354.4 | 359.2 | 342.9
1764.2 | 1488.2 | 353.7 | 354.4 | 359.3 | 342.9
1765.2 | 1489.2 | 353.7 | 354.5 | 359.3 | 342.9
1766.2 | 1490.2 | 353.8 | 354.6 | 360 | 343
1767.2 | 1491.2 | 353.8 | 354.5 | 360 | 343
1768.2 | 1492.2 | 353.9 | 354.4 | 359.9 | 343
1769.2 | 1493.2 | 353.9 | 354.2 | 359.9 | 343
1770.2 | 1494.2 | 354 | 354.2 | 359.9 | 343
1771.2 | 1495.2 | 354 | 354 | 360 | 342.9
1772.2 | 1496.2 | 354 | 353.8 | 359.8 | 342.9
1773.2 | 1497.2 | 354.1 | 353.4 | 359.4 | 342.8
1774.2 | 1498.2 | 354.1 | 353.1 | 358.9 | 342.7
1775.2 | 1499.2 | 354.2 | 352.9 | 358.7 | 342.8
1776.2 | 1500.2 | 354.2 | 352.6 | 358.5 | 342.8
1777.2 | 1501.2 | 354.2 | 352.9 | 358.4 | 342.8
1778.2 | 1502.2 | 354.2 | 353.4 | 358.8 | 343.1
1779.2 | 1503.2 | 354.3 | 353.8 | 359.4 | 343.3
1780.2 | 1504.2 | 354.3 | 353.9 | 359.4 | 343.4
1781.2 | 1505.2 | 354.3 | 354 | 359.7 | 343.4
1782.2 | 1506.2 | 354.3 | 354.5 | 360 | 343.6
1783.2 | 1507.2 | 354.4 | 354.7 | 359.9 | 343.6
1784.2 | 1508.2 | 354.4 | 354.9 | 360.1 | 343.6
1785.2 | 1509.2 | 354.5 | 355 | 360.3 | 343.6
1786.2 | 1510.2 | 354.5 | 355.2 | 360.3 | 343.7
1787.2 | 1511.2 | 354.5 | 355.3 | 360.4 | 343.7
1788.2 | 1512.2 | 354.6 | 355.5 | 360.4 | 343.8
1789.2 | 1513.2 | 354.6 | 355.7 | 360.7 | 343.8
1790.2 | 1514.2 | 354.7 | 355.6 | 360.8 | 343.9
1791.2 | 1515.2 | 354.7 | 355.7 | 360.7 | 344
1792.2 | 1516.2 | 354.8 | 355.9 | 361.2 | 344.1
1793.2 | 1517.2 | 354.8 | 355.9 | 361.3 | 344.1
1794.2 | 1518.2 | 354.8 | 355.9 | 361.3 | 344.1
1795.2 | 1519.2 | 354.9 | 355.8 | 361.4 | 344
1796.2 | 1520.2 | 354.9 | 355.6 | 361.4 | 343.9
1797.2 | 1521.2 | 355 | 355.4 | 361.4 | 343.8
1798.2 | 1522.2 | 355.1 | 355.2 | 361.5 | 343.7
1799.2 | 1523.2 | 355.1 | 354.9 | 361.4 | 343.7
1800.2 | 1524.2 | 355.2 | 354.7 | 361.3 | 343.6
1801.2 | 1525.2 | 355.2 | 354.4 | 361.2 | 343.5
1802.2 | 1526.2 | 355.3 | 354.1 | 361.1 | 343.4
1803.2 | 1527.2 | 355.4 | 353.8 | 361.1 | 343.4
1804.2 | 1528.2 | 355.4 | 353.6 | 361.1 | 343.3
1805.2 | 1529.2 | 355.5 | 353.3 | 361.1 | 343.2
1806.2 | 1530.2 | 355.5 | 353 | 361.1 | 343.1
1807.2 | 1531.2 | 355.6 | 352.9 | 361.1 | 343.1
1808.2 | 1532.2 | 355.6 | 352.7 | 361.1 | 343.1
1809.2 | 1533.2 | 355.7 | 352.5 | 361.1 | 343
1810.2 | 1534.2 | 355.7 | 352.6 | 361 | 343.1
1811.2 | 1535.2 | 355.8 | 352.6 | 361.1 | 343.2
1812.2 | 1536.2 | 355.8 | 352.6 | 361.1 | 343.2
1813.2 | 1537.2 | 355.9 | 352.5 | 361.1 | 343.2
1814.2 | 1538.2 | 356 | 352.5 | 360.8 | 343.2
1815.2 | 1539.2 | 356 | 352.5 | 360.5 | 343.2
1816.2 | 1540.2 | 356 | 352.6 | 360.2 | 343.2
1817.2 | 1541.2 | 356.1 | 352.3 | 359.8 | 343.1
1818.2 | 1542.2 | 356.2 | 352 | 359.4 | 343.1
1819.2 | 1543.2 | 356.2 | 351.6 | 359.1 | 343
1820.2 | 1544.2 | 356.2 | 351.4 | 358.8 | 342.8
1821.2 | 1545.2 | 356.2 | 351.1 | 358.7 | 342.7
1822.2 | 1546.2 | 356.3 | 350.9 | 358.4 | 342.7
1823.2 | 1547.2 | 356.3 | 350.8 | 358.1 | 342.7
1824.2 | 1548.2 | 356.3 | 350.6 | 357.9 | 342.7
1825.2 | 1549.2 | 356.3 | 350.4 | 357.6 | 342.6
1826.2 | 1550.2 | 356.3 | 350.2 | 357.5 | 342.5
1827.2 | 1551.2 | 356.4 | 350 | 357.7 | 342.4
1828.2 | 1552.2 | 356.4 | 349.9 | 357.7 | 342.5
1829.2 | 1553.2 | 356.4 | 349.7 | 357.7 | 342.4
1830.2 | 1554.2 | 356.4 | 349.4 | 357.7 | 342.3
1831.2 | 1555.2 | 356.4 | 349.2 | 357.8 | 342.2
1832.2 | 1556.2 | 356.4 | 349.1 | 357.7 | 342.2
1833.2 | 1557.2 | 356.5 | 349 | 357.5 | 342.2
1834.2 | 1558.2 | 356.5 | 348.8 | 357.3 | 342.2
1835.2 | 1559.2 | 356.5 | 348.8 | 357 | 342.3
1836.2 | 1560.2 | 356.5 | 348.8 | 356.9 | 342.3
1837.2 | 1561.2 | 356.5 | 348.7 | 356.8 | 342.3
1838.2 | 1562.2 | 356.5 | 348.5 | 356.7 | 342.3
1839.2 | 1563.2 | 356.5 | 348.2 | 356.3 | 342.2
1840.2 | 1564.2 | 356.5 | 348 | 356.5 | 342.1
1841.2 | 1565.2 | 356.5 | 348 | 356.6 | 342.1
1842.2 | 1566.2 | 356.5 | 347.9 | 356.2 | 342.1
1843.2 | 1567.2 | 356.5 | 347.8 | 355.9 | 342
1844.2 | 1568.2 | 356.5 | 347.6 | 355.6 | 342
1845.2 | 1569.2 | 356.5 | 347.5 | 355.4 | 341.9
1846.2 | 1570.2 | 356.5 | 347.4 | 355.6 | 341.9
1847.2 | 1571.2 | 356.5 | 347.1 | 355.3 | 341.8
1848.2 | 1572.2 | 356.5 | 346.8 | 355 | 341.7
1849.2 | 1573.2 | 356.5 | 346.7 | 354.8 | 341.6
1850.2 | 1574.2 | 356.5 | 346.6 | 354.8 | 341.6
1851.2 | 1575.2 | 356.5 | 346.6 | 354.8 | 341.5
1852.2 | 1576.2 | 356.5 | 346.5 | 354.8 | 341.5
1853.2 | 1577.2 | 356.5 | 346.6 | 354.8 | 341.6
1854.2 | 1578.2 | 356.5 | 346.7 | 354.6 | 341.5
1855.2 | 1579.2 | 356.5 | 346.7 | 354.7 | 341.5
1856.2 | 1580.2 | 356.5 | 346.7 | 354.6 | 341.5
1857.2 | 1581.2 | 356.5 | 346.7 | 354.6 | 341.5
1858.2 | 1582.2 | 356.4 | 346.7 | 354.5 | 341.4
1859.2 | 1583.2 | 356.4 | 346.6 | 354.3 | 341.3
1860.2 | 1584.2 | 356.4 | 346.7 | 354.1 | 341.3
1861.2 | 1585.2 | 356.4 | 346.5 | 353.9 | 341.2
1862.2 | 1586.2 | 356.4 | 346.5 | 353.6 | 341.1
1863.2 | 1587.2 | 356.4 | 346.4 | 353.3 | 341.1
1864.2 | 1588.2 | 356.4 | 346.3 | 353 | 341
1865.2 | 1589.2 | 356.4 | 346.2 | 352.8 | 340.9
1866.2 | 1590.2 | 356.4 | 346.1 | 352.9 | 340.8
1867.2 | 1591.2 | 356.3 | 345.9 | 352.7 | 340.7
1868.2 | 1592.2 | 356.3 | 345.6 | 352.5 | 340.6
1869.2 | 1593.2 | 356.3 | 345.5 | 352.5 | 340.6
1870.2 | 1594.2 | 356.3 | 345.6 | 352.6 | 340.6
1871.2 | 1595.2 | 356.3 | 345.8 | 353.1 | 340.6
1872.2 | 1596.2 | 356.2 | 345.9 | 353.3 | 340.7
1873.2 | 1597.2 | 356.2 | 346.1 | 353.5 | 340.8
1874.2 | 1598.2 | 356.2 | 346.2 | 354 | 340.9
1875.2 | 1599.2 | 356.2 | 346.6 | 354.7 | 341
1876.2 | 1600.2 | 356.2 | 347.1 | 355.2 | 341
1877.2 | 1601.2 | 356.1 | 347.6 | 355.6 | 341.1
1878.2 | 1602.2 | 356.1 | 347.9 | 355.9 | 341.2
1879.2 | 1603.2 | 356.1 | 348.2 | 356 | 341.3
1880.2 | 1604.2 | 356.1 | 348.8 | 356.2 | 341.4
1881.2 | 1605.2 | 356.1 | 349.3 | 356.5 | 341.6
1882.2 | 1606.2 | 356.1 | 350.4 | 357 | 341.8
1883.2 | 1607.2 | 356.2 | 351.4 | 357.5 | 341.9
1884.2 | 1608.2 | 356.2 | 351.6 | 357.9 | 342
1885.2 | 1609.2 | 356.2 | 351.8 | 358.4 | 342
1886.2 | 1610.2 | 356.2 | 351.9 | 358.6 | 342.1
1887.2 | 1611.2 | 356.2 | 352.1 | 359 | 342.2
1888.2 | 1612.2 | 356.2 | 352.1 | 359.2 | 342.2
1889.2 | 1613.2 | 356.3 | 352.4 | 359.2 | 342.3
1890.2 | 1614.2 | 356.3 | 352.7 | 359.4 | 342.4
1891.2 | 1615.2 | 356.3 | 352.5 | 359.2 | 342.5
1892.2 | 1616.2 | 356.4 | 352.6 | 359.2 | 342.5
1893.2 | 1617.2 | 356.4 | 352.6 | 359.1 | 342.5
1894.2 | 1618.2 | 356.4 | 352.4 | 359 | 342.5
1895.2 | 1619.2 | 356.5 | 352.3 | 358.7 | 342.5
1896.2 | 1620.2 | 356.5 | 352.1 | 358.4 | 342.4
1897.2 | 1621.2 | 356.5 | 351.8 | 357.9 | 342.4
1898.2 | 1622.2 | 356.6 | 351.6 | 357.6 | 342.3
1899.2 | 1623.2 | 356.6 | 351.4 | 357.5 | 342.3
1900.2 | 1624.2 | 356.6 | 351.2 | 357.5 | 342.2
1901.2 | 1625.2 | 356.6 | 350.8 | 357.4 | 342.1
1902.2 | 1626.2 | 356.6 | 350.6 | 357.1 | 342
1903.2 | 1627.2 | 356.7 | 350.4 | 357 | 342
1904.2 | 1628.2 | 356.7 | 350.3 | 356.9 | 341.9
1905.2 | 1629.2 | 356.7 | 350.2 | 356.8 | 341.9
1906.2 | 1630.2 | 356.7 | 350.1 | 356.6 | 341.8
1907.2 | 1631.2 | 356.7 | 350 | 356.4 | 341.8
1908.2 | 1632.2 | 356.7 | 349.8 | 356.2 | 341.8
1909.2 | 1633.2 | 356.7 | 349.5 | 356.1 | 341.7
1910.2 | 1634.2 | 356.7 | 349.2 | 356.1 | 341.5
1911.2 | 1635.2 | 356.7 | 348.8 | 356.2 | 341.4
1912.2 | 1636.2 | 356.7 | 348.5 | 356.2 | 341.4
1913.2 | 1637.2 | 356.7 | 348.3 | 356.1 | 341.3
1914.2 | 1638.2 | 356.7 | 348.2 | 356 | 341.4
1915.2 | 1639.2 | 356.7 | 347.9 | 355.8 | 341.3
1916.2 | 1640.2 | 356.7 | 347.7 | 355.5 | 341.2
1917.2 | 1641.2 | 356.7 | 347.5 | 355.4 | 341.1
1918.2 | 1642.2 | 356.8 | 347.3 | 355.3 | 341.1
1919.2 | 1643.2 | 356.8 | 347.2 | 355.2 | 341
1920.2 | 1644.2 | 356.8 | 347 | 355 | 340.9
1921.2 | 1645.2 | 356.8 | 347 | 354.9 | 340.9
1922.2 | 1646.2 | 356.8 | 346.8 | 354.7 | 340.8
1923.2 | 1647.2 | 356.8 | 346.8 | 354.7 | 340.8
1924.2 | 1648.2 | 356.7 | 346.8 | 355 | 340.9
1925.2 | 1649.2 | 356.7 | 346.9 | 355.1 | 340.9
1926.2 | 1650.2 | 356.7 | 346.9 | 355.3 | 340.9
1927.2 | 1651.2 | 356.7 | 346.8 | 355.3 | 340.8
1928.2 | 1652.2 | 356.7 | 347 | 355.7 | 340.9
1929.2 | 1653.2 | 356.7 | 347.1 | 356 | 340.9
1930.2 | 1654.2 | 356.7 | 347 | 356 | 340.9
1931.2 | 1655.2 | 356.7 | 347.1 | 356.1 | 341
1932.2 | 1656.2 | 356.7 | 347.3 | 356.4 | 341
1933.2 | 1657.2 | 356.7 | 347.5 | 356.8 | 341.1
1934.2 | 1658.2 | 356.7 | 347.8 | 357.1 | 341.2
1935.2 | 1659.2 | 356.7 | 347.9 | 357.6 | 341.3
1936.2 | 1660.2 | 356.7 | 348.1 | 357.9 | 341.4
1937.2 | 1661.2 | 356.7 | 348.4 | 357.8 | 341.3
1938.2 | 1662.2 | 356.7 | 348.6 | 357.7 | 341.4
1939.2 | 1663.2 | 356.7 | 348.9 | 357.6 | 341.6
1940.2 | 1664.2 | 356.7 | 349.4 | 357.7 | 341.7
1941.2 | 1665.2 | 356.7 | 349.7 | 358 | 341.8
1942.2 | 1666.2 | 356.7 | 349.9 | 358.2 | 341.8
1943.2 | 1667.2 | 356.7 | 350.1 | 358.2 | 341.8
1944.2 | 1668.2 | 356.7 | 350.1 | 358.3 | 341.8
1945.2 | 1669.2 | 356.8 | 350.2 | 358.4 | 341.8
1946.2 | 1670.2 | 356.8 | 350.2 | 358.3 | 341.8
1947.2 | 1671.2 | 356.8 | 350.1 | 358.3 | 341.8
1948.2 | 1672.2 | 356.8 | 350 | 358.5 | 341.7
1949.2 | 1673.2 | 356.8 | 349.8 | 358.2 | 341.7
1950.2 | 1674.2 | 356.8 | 349.6 | 357.9 | 341.6
1951.2 | 1675.2 | 356.8 | 349.4 | 357.6 | 341.5
1952.2 | 1676.2 | 356.8 | 349.1 | 357.3 | 341.4
1953.2 | 1677.2 | 356.8 | 348.8 | 357 | 341.3
1954.2 | 1678.2 | 356.8 | 348.5 | 356.8 | 341.2
1955.2 | 1679.2 | 356.8 | 348.2 | 356.8 | 341.1
1956.2 | 1680.2 | 356.8 | 347.9 | 356.7 | 341
1957.2 | 1681.2 | 356.8 | 347.7 | 356.6 | 340.9
1958.2 | 1682.2 | 356.8 | 347.5 | 356.6 | 340.9
1959.2 | 1683.2 | 356.8 | 347.4 | 356.7 | 340.9
1960.2 | 1684.2 | 356.8 | 347.2 | 356.6 | 340.9
1961.2 | 1685.2 | 356.7 | 347.1 | 356.5 | 340.8
1962.2 | 1686.2 | 356.7 | 347.1 | 356.2 | 340.7
1963.2 | 1687.2 | 356.7 | 347.1 | 356.1 | 340.7
1964.2 | 1688.2 | 356.7 | 347.2 | 356.2 | 340.7
1965.2 | 1689.2 | 356.7 | 347.1 | 356.1 | 340.7
1966.2 | 1690.2 | 356.7 | 347 | 355.9 | 340.6
1967.2 | 1691.2 | 356.7 | 346.8 | 355.7 | 340.5
1968.2 | 1692.2 | 356.7 | 346.6 | 355.4 | 340.4
1969.2 | 1693.2 | 356.7 | 346.4 | 355.4 | 340.4
1970.2 | 1694.2 | 356.6 | 346.2 | 355.3 | 340.3
1971.2 | 1695.2 | 356.6 | 346 | 355.1 | 340.3
1972.2 | 1696.2 | 356.6 | 345.9 | 355.2 | 340.3
1973.2 | 1697.2 | 356.6 | 345.9 | 355.4 | 340.3
1974.2 | 1698.2 | 356.5 | 345.9 | 355.4 | 340.4
1975.2 | 1699.2 | 356.5 | 346.1 | 355.5 | 340.4
1976.2 | 1700.2 | 356.5 | 346.2 | 355.6 | 340.5
1977.2 | 1701.2 | 356.5 | 346.3 | 356 | 340.5
1978.2 | 1702.2 | 356.5 | 346.4 | 356.3 | 340.6
1979.2 | 1703.2 | 356.4 | 346.5 | 356.4 | 340.6
1980.2 | 1704.2 | 356.4 | 346.7 | 356.5 | 340.6
1981.2 | 1705.2 | 356.4 | 346.7 | 356.3 | 340.6
1982.2 | 1706.2 | 356.4 | 346.7 | 356.1 | 340.5
1983.2 | 1707.2 | 356.4 | 346.7 | 355.8 | 340.4
1984.2 | 1708.2 | 356.4 | 346.7 | 355.7 | 340.4
1985.2 | 1709.2 | 356.3 | 346.6 | 355.8 | 340.3
1986.2 | 1710.2 | 356.3 | 346.4 | 355.6 | 340.3
1987.2 | 1711.2 | 356.3 | 346.3 | 355.6 | 340.2
1988.2 | 1712.2 | 356.3 | 346.2 | 355.6 | 340.1
1989.2 | 1713.2 | 356.3 | 346.1 | 355.8 | 340
1990.2 | 1714.2 | 356.3 | 346.1 | 355.8 | 340
1991.2 | 1715.2 | 356.3 | 346.4 | 355.9 | 340.1
1992.2 | 1716.2 | 356.2 | 346.8 | 356.1 | 340.2
1993.2 | 1717.2 | 356.2 | 347.3 | 356.4 | 340.3
1994.2 | 1718.2 | 356.2 | 347.7 | 357.3 | 340.5
1995.2 | 1719.2 | 356.2 | 347.8 | 357.5 | 340.5
1996.2 | 1720.2 | 356.2 | 347.9 | 357.6 | 340.4
1997.2 | 1721.2 | 356.2 | 347.9 | 357.8 | 340.4
1998.2 | 1722.2 | 356.2 | 347.9 | 358.1 | 340.5
1999.2 | 1723.2 | 356.2 | 348.1 | 358 | 340.5
2000.2 | 1724.2 | 356.2 | 348.4 | 357.9 | 340.6
2001.2 | 1725.2 | 356.2 | 348.5 | 357.6 | 340.6
2002.2 | 1726.2 | 356.2 | 348.4 | 357.2 | 340.6
2003.2 | 1727.2 | 356.2 | 348.3 | 356.8 | 340.5
2004.2 | 1728.2 | 356.2 | 348.3 | 356.5 | 340.5
2005.2 | 1729.2 | 356.2 | 348.2 | 356.2 | 340.5
2006.2 | 1730.2 | 356.2 | 347.9 | 355.8 | 340.4
2007.2 | 1731.2 | 356.2 | 348 | 355.4 | 340.4
2008.2 | 1732.2 | 356.2 | 347.9 | 355.2 | 340.4
2009.2 | 1733.2 | 356.1 | 347.7 | 354.9 | 340.4
2010.2 | 1734.2 | 356.1 | 347.5 | 354.7 | 340.4
2011.2 | 1735.2 | 356.1 | 347.2 | 354.2 | 340.3
2012.2 | 1736.2 | 356.1 | 347 | 353.8 | 340.3
2013.2 | 1737.2 | 356 | 346.8 | 353.6 | 340.4
2014.2 | 1738.2 | 356 | 346.7 | 353.4 | 340.3
2015.2 | 1739.2 | 355.9 | 346.5 | 353.5 | 340.3
2016.2 | 1740.2 | 355.9 | 346.3 | 353.4 | 340.2
2017.2 | 1741.2 | 355.8 | 346.1 | 353.2 | 340.2
2018.2 | 1742.2 | 355.7 | 346.4 | 353.3 | 340.3
2019.2 | 1743.2 | 355.7 | 346.7 | 353.5 | 340.4
2020.2 | 1744.2 | 355.6 | 346.8 | 353.8 | 340.4
2021.2 | 1745.2 | 355.6 | 347.1 | 354.1 | 340.5
2022.2 | 1746.2 | 355.5 | 347.2 | 354.3 | 340.5
2023.2 | 1747.2 | 355.5 | 347.4 | 354.3 | 340.4
2024.2 | 1748.2 | 355.4 | 347.5 | 354.4 | 340.4
2025.2 | 1749.2 | 355.4 | 347.6 | 354.4 | 340.4
2026.2 | 1750.2 | 355.4 | 347.8 | 354.7 | 340.4
2027.2 | 1751.2 | 355.4 | 347.7 | 355 | 340.4
2028.2 | 1752.2 | 355.3 | 347.7 | 355.1 | 340.3
2029.2 | 1753.2 | 355.3 | 347.6 | 355.1 | 340.3
2030.2 | 1754.2 | 355.3 | 347.6 | 355 | 340.2
2031.2 | 1755.2 | 355.2 | 347.5 | 354.9 | 340.2
2032.2 | 1756.2 | 355.2 | 347.5 | 354.7 | 340.1
2033.2 | 1757.2 | 355.2 | 347.4 | 354.5 | 340
2034.2 | 1758.2 | 355.2 | 347.2 | 354.4 | 339.9
2035.2 | 1759.2 | 355.2 | 346.9 | 354.2 | 339.9
2036.2 | 1760.2 | 355.1 | 346.7 | 354.1 | 339.8
2037.2 | 1761.2 | 355.1 | 346.6 | 354 | 339.8
2038.2 | 1762.2 | 355.1 | 346.4 | 354 | 339.8
2039.2 | 1763.2 | 355.1 | 346.3 | 354.2 | 339.7
2040.2 | 1764.2 | 355 | 346.2 | 354.3 | 339.8
2041.2 | 1765.2 | 355 | 346.1 | 354.2 | 339.8
2042.2 | 1766.2 | 355 | 346 | 354.1 | 339.7
2043.2 | 1767.2 | 355 | 346 | 354 | 339.6
2044.2 | 1768.2 | 354.9 | 346 | 353.9 | 339.7
2045.2 | 1769.2 | 354.9 | 345.9 | 353.7 | 339.6
2046.2 | 1770.2 | 354.9 | 345.8 | 353.7 | 339.6
2047.2 | 1771.2 | 354.9 | 345.7 | 353.8 | 339.5
2048.2 | 1772.2 | 354.8 | 345.6 | 353.7 | 339.4
2049.2 | 1773.2 | 354.8 | 345.4 | 353.8 | 339.4
2050.2 | 1774.2 | 354.8 | 345.4 | 353.8 | 339.4
2051.2 | 1775.2 | 354.7 | 345.5 | 353.7 | 339.4
2052.2 | 1776.2 | 354.7 | 345.5 | 353.5 | 339.3
2053.2 | 1777.2 | 354.7 | 345.5 | 353.5 | 339.3
2054.2 | 1778.2 | 354.6 | 345.5 | 353.6 | 339.2
2055.2 | 1779.2 | 354.6 | 345.5 | 353.6 | 339.2
2056.2 | 1780.2 | 354.6 | 345.4 | 353.4 | 339.2
2057.2 | 1781.2 | 354.6 | 345.2 | 353.4 | 339.1
2058.2 | 1782.2 | 354.5 | 345.1 | 353.4 | 339
2059.2 | 1783.2 | 354.5 | 344.9 | 353.2 | 338.9
2060.2 | 1784.2 | 354.5 | 344.7 | 353.1 | 338.9
2061.2 | 1785.2 | 354.4 | 344.6 | 352.9 | 338.8
2062.2 | 1786.2 | 354.4 | 344.4 | 352.9 | 338.7
2063.2 | 1787.2 | 354.4 | 344.4 | 352.9 | 338.6
2064.2 | 1788.2 | 354.3 | 344.5 | 353 | 338.6
2065.2 | 1789.2 | 354.3 | 344.6 | 353.4 | 338.6
2066.2 | 1790.2 | 354.3 | 345 | 354 | 338.7
2067.2 | 1791.2 | 354.2 | 345.5 | 354.6 | 338.9
2068.2 | 1792.2 | 354.2 | 345.9 | 355.1 | 339
2069.2 | 1793.2 | 354.2 | 346.2 | 355.8 | 339
2070.2 | 1794.2 | 354.2 | 346.6 | 356 | 339
2071.2 | 1795.2 | 354.1 | 346.8 | 356 | 339
2072.2 | 1796.2 | 354.1 | 346.9 | 356 | 339
2073.2 | 1797.2 | 354.1 | 346.9 | 356 | 338.9
2074.2 | 1798.2 | 354.1 | 346.8 | 356 | 338.8
2075.2 | 1799.2 | 354.1 | 346.7 | 355.8 | 338.8
2076.2 | 1800.2 | 354.1 | 346.9 | 355.8 | 338.8
2077.2 | 1801.2 | 354.1 | 347 | 355.8 | 338.9
2078.2 | 1802.2 | 354.1 | 347 | 355.8 | 338.9
2079.2 | 1803.2 | 354.1 | 347 | 355.9 | 338.9
2080.2 | 1804.2 | 354.1 | 347 | 355.8 | 338.9
2081.2 | 1805.2 | 354.1 | 347.1 | 355.8 | 338.9
2082.2 | 1806.2 | 354.1 | 347.1 | 355.7 | 338.9
2083.2 | 1807.2 | 354.1 | 347.3 | 355.8 | 339
2084.2 | 1808.2 | 354.1 | 347.5 | 356.1 | 339
2085.2 | 1809.2 | 354.1 | 347.6 | 356.3 | 339
2086.2 | 1810.2 | 354.1 | 347.7 | 356.3 | 338.9
2087.2 | 1811.2 | 354.1 | 347.7 | 356.6 | 338.9
2088.2 | 1812.2 | 354.1 | 347.6 | 356.8 | 338.9
2089.2 | 1813.2 | 354.1 | 347.4 | 356.9 | 338.8
2090.2 | 1814.2 | 354.1 | 347.3 | 356.9 | 338.8
2091.2 | 1815.2 | 354 | 347.2 | 356.9 | 338.8
2092.2 | 1816.2 | 354 | 346.9 | 356.6 | 338.6
2093.2 | 1817.2 | 354 | 346.4 | 356.1 | 338.4
2094.2 | 1818.2 | 354 | 345.8 | 355.6 | 338.2
2095.2 | 1819.2 | 354 | 345.1 | 354.8 | 337.9
2096.2 | 1820.2 | 354.1 | 344.4 | 354.1 | 337.6
2097.2 | 1821.2 | 354 | 343.4 | 353.2 | 337.2
2098.2 | 1822.2 | 354 | 342.4 | 352.2 | 336.8
2099.2 | 1823.2 | 354 | 341.2 | 351 | 336.4
2100.2 | 1824.2 | 354 | 339.8 | 349.7 | 336
2101.2 | 1825.2 | 353.9 | 338.3 | 348.3 | 335.5
2102.2 | 1826.2 | 353.9 | 336.8 | 346.8 | 335.1
2103.2 | 1827.2 | 353.8 | 335.2 | 345.4 | 334.6
2104.2 | 1828.2 | 353.8 | 333.5 | 344 | 334.1
2105.2 | 1829.2 | 353.7 | 331.9 | 342.4 | 333.7
2106.2 | 1830.2 | 353.6 | 330.3 | 341 | 333.2
2107.2 | 1831.2 | 353.5 | 328.6 | 339.5 | 332.7
2108.2 | 1832.2 | 353.4 | 326.9 | 338 | 332.2
2109.2 | 1833.2 | 353.2 | 325.3 | 336.6 | 331.7
2110.2 | 1834.2 | 353.1 | 323.6 | 335.1 | 331.2
2111.2 | 1835.2 | 352.9 | 322 | 333.6 | 330.7
2112.2 | 1836.2 | 352.8 | 320.4 | 332.1 | 330.2
2113.2 | 1837.2 | 352.6 | 318.9 | 330.8 | 329.7
2114.2 | 1838.2 | 352.4 | 317.3 | 329.4 | 329.2
2115.2 | 1839.2 | 352.2 | 315.8 | 328.1 | 328.7
2116.2 | 1840.2 | 352 | 314.3 | 326.9 | 328.2
2117.2 | 1841.2 | 351.8 | 312.8 | 325.7 | 327.7
2118.2 | 1842.2 | 351.6 | 311.4 | 324.4 | 327.1
2119.2 | 1843.2 | 351.3 | 310 | 323.1 | 326.6
2120.2 | 1844.2 | 351.1 | 308.6 | 321.9 | 326.1
2121.2 | 1845.2 | 350.9 | 307.3 | 320.7 | 325.6
2122.2 | 1846.2 | 350.6 | 306 | 319.6 | 325.1
2123.2 | 1847.2 | 350.4 | 304.7 | 318.5 | 324.6
2124.2 | 1848.2 | 350.1 | 303.5 | 317.5 | 324.1
2125.2 | 1849.2 | 349.9 | 302.3 | 316.4 | 323.6
2126.2 | 1850.2 | 349.6 | 301.1 | 315.3 | 323.1
2127.2 | 1851.2 | 349.3 | 299.9 | 314.3 | 322.6
2128.2 | 1852.2 | 349.1 | 298.7 | 313.3 | 322.1
2129.2 | 1853.2 | 348.8 | 297.6 | 312.4 | 321.7
2130.2 | 1854.2 | 348.5 | 296.5 | 311.5 | 321.2
2131.2 | 1855.2 | 348.2 | 295.4 | 310.6 | 320.7
2132.2 | 1856.2 | 348 | 294.5 | 309.7 | 320.2
2133.2 | 1857.2 | 347.7 | 293.5 | 308.9 | 319.7
2134.2 | 1858.2 | 347.4 | 292.6 | 308.2 | 319.2
2135.2 | 1859.2 | 347.1 | 291.5 | 307.5 | 318.7
2136.2 | 1860.2 | 346.8 | 290.6 | 306.6 | 318.2
2137.2 | 1861.2 | 346.5 | 289.6 | 305.8 | 317.7
2138.2 | 1862.2 | 346.2 | 288.7 | 305 | 317.3
2139.2 | 1863.2 | 345.9 | 287.8 | 304.2 | 316.8
2140.2 | 1864.2 | 345.7 | 287 | 303.5 | 316.3
2141.2 | 1865.2 | 345.4 | 286.1 | 302.7 | 315.8
2142.2 | 1866.2 | 345.1 | 285.2 | 301.9 | 315.4
2143.2 | 1867.2 | 344.8 | 284.3 | 301.2 | 314.9
2144.2 | 1868.2 | 344.5 | 283.4 | 300.6 | 314.4
2145.2 | 1869.2 | 344.2 | 282.6 | 299.9 | 313.9
2146.2 | 1870.2 | 343.9 | 281.8 | 299.3 | 313.4
2147.2 | 1871.2 | 343.6 | 281 | 298.6 | 312.9
2148.2 | 1872.2 | 343.3 | 280.2 | 298 | 312.5
2149.2 | 1873.2 | 343 | 279.4 | 297.3 | 312
2150.2 | 1874.2 | 342.7 | 278.6 | 296.5 | 311.5
2151.2 | 1875.2 | 342.4 | 277.9 | 295.8 | 311
2152.2 | 1876.2 | 342.1 | 277.1 | 295.2 | 310.6
2153.2 | 1877.2 | 341.8 | 276.3 | 294.6 | 310.1
2154.2 | 1878.2 | 341.5 | 275.6 | 293.9 | 309.6
2155.2 | 1879.2 | 341.2 | 274.9 | 293.2 | 309.1
2156.2 | 1880.2 | 340.9 | 274.3 | 292.5 | 308.7
2157.2 | 1881.2 | 340.6 | 273.6 | 291.8 | 308.2
2158.2 | 1882.2 | 340.3 | 273 | 291.1 | 307.7
2159.2 | 1883.2 | 340 | 272.3 | 290.4 | 307.2
2160.2 | 1884.2 | 339.7 | 271.6 | 289.9 | 306.8
2161.2 | 1885.2 | 339.4 | 271 | 289.2 | 306.3
2162.2 | 1886.2 | 339.1 | 270.4 | 288.6 | 305.8
2163.2 | 1887.2 | 338.9 | 269.8 | 288 | 305.4
2164.2 | 1888.2 | 338.6 | 269.3 | 287.3 | 305
2165.2 | 1889.2 | 338.3 | 268.6 | 286.8 | 304.5
2166.2 | 1890.2 | 338 | 268.1 | 286.2 | 304
2167.2 | 1891.2 | 337.7 | 267.5 | 285.7 | 303.6
2168.2 | 1892.2 | 337.4 | 267 | 285.2 | 303.2
2169.2 | 1893.2 | 337.1 | 266.4 | 284.6 | 302.7
2170.2 | 1894.2 | 336.8 | 265.9 | 284.1 | 302.3
2171.2 | 1895.2 | 336.5 | 265.3 | 283.5 | 301.8
2172.2 | 1896.2 | 336.2 | 264.7 | 283 | 301.3
2173.2 | 1897.2 | 335.9 | 264.2 | 282.5 | 300.9
2174.2 | 1898.2 | 335.6 | 263.8 | 282 | 300.4
2175.2 | 1899.2 | 335.3 | 263.2 | 281.5 | 300
2176.2 | 1900.2 | 335 | 262.7 | 281 | 299.5
2177.2 | 1901.2 | 334.7 | 262.1 | 280.6 | 299.1
2178.2 | 1902.2 | 334.4 | 261.6 | 280.1 | 298.6
2179.2 | 1903.2 | 334.1 | 261 | 279.6 | 298.2
2180.2 | 1904.2 | 333.8 | 260.5 | 279 | 297.8
2181.2 | 1905.2 | 333.5 | 260 | 278.4 | 297.3
2182.2 | 1906.2 | 333.2 | 259.4 | 278 | 296.8
2183.2 | 1907.2 | 332.9 | 258.9 | 277.4 | 296.4
2184.2 | 1908.2 | 332.6 | 258.4 | 276.8 | 295.9
2185.2 | 1909.2 | 332.3 | 258 | 276.4 | 295.5
2186.2 | 1910.2 | 332 | 257.5 | 276 | 295
2187.2 | 1911.2 | 331.7 | 257.1 | 275.5 | 294.6
2188.2 | 1912.2 | 331.4 | 256.6 | 274.9 | 294.2
2189.2 | 1913.2 | 331.1 | 256.1 | 274.3 | 293.7
2190.2 | 1914.2 | 330.8 | 255.6 | 273.9 | 293.3
2191.2 | 1915.2 | 330.5 | 255.1 | 273.5 | 292.8
2192.2 | 1916.2 | 330.2 | 254.6 | 273.1 | 292.4
2193.2 | 1917.2 | 329.9 | 254.2 | 272.8 | 292
2194.2 | 1918.2 | 329.6 | 253.7 | 272.3 | 291.6
2195.2 | 1919.2 | 329.3 | 253.2 | 271.9 | 291.2
2196.2 | 1920.2 | 329 | 252.8 | 271.5 | 290.8
2197.2 | 1921.2 | 328.7 | 252.4 | 271 | 290.3
2198.2 | 1922.2 | 328.4 | 252 | 270.5 | 289.9
2199.2 | 1923.2 | 328.1 | 251.5 | 269.9 | 289.5
2200.2 | 1924.2 | 327.8 | 251.1 | 269.5 | 289.1
2201.2 | 1925.2 | 327.5 | 250.7 | 269 | 288.7
2202.2 | 1926.2 | 327.2 | 250.3 | 268.7 | 288.3
2203.2 | 1927.2 | 326.9 | 249.8 | 268.1 | 287.9
2204.2 | 1928.2 | 326.6 | 249.3 | 267.8 | 287.5
2205.2 | 1929.2 | 326.3 | 248.8 | 267.4 | 287
2206.2 | 1930.2 | 326.1 | 248.3 | 267 | 286.6
2207.2 | 1931.2 | 325.8 | 247.9 | 266.7 | 286.2
2208.2 | 1932.2 | 325.5 | 247.5 | 266.2 | 285.8
2209.2 | 1933.2 | 325.2 | 247.1 | 265.7 | 285.4
2210.2 | 1934.2 | 324.9 | 246.7 | 265.3 | 285
2211.2 | 1935.2 | 324.6 | 246.2 | 264.8 | 284.6
2212.2 | 1936.2 | 324.3 | 245.8 | 264.5 | 284.2
2213.2 | 1937.2 | 324 | 245.4 | 264.2 | 283.8
2214.2 | 1938.2 | 323.7 | 245 | 263.8 | 283.5
2215.2 | 1939.2 | 323.4 | 244.6 | 263.3 | 283
2216.2 | 1940.2 | 323.1 | 244.2 | 262.9 | 282.6
2217.2 | 1941.2 | 322.8 | 243.7 | 262.5 | 282.2
2218.2 | 1942.2 | 322.5 | 243.3 | 262 | 281.8
2219.2 | 1943.2 | 322.2 | 243 | 261.6 | 281.4
2220.2 | 1944.2 | 321.9 | 242.5 | 261.3 | 281
2221.2 | 1945.2 | 321.6 | 242.1 | 260.9 | 280.6
2222.2 | 1946.2 | 321.4 | 241.7 | 260.7 | 280.3
2223.2 | 1947.2 | 321.1 | 241.3 | 260.5 | 279.9
2224.2 | 1948.2 | 320.8 | 240.9 | 260.1 | 279.5
2225.2 | 1949.2 | 320.5 | 240.5 | 259.6 | 279.1
2226.2 | 1950.2 | 320.2 | 240.1 | 259.1 | 278.7
2227.2 | 1951.2 | 319.9 | 239.7 | 258.6 | 278.4
2228.2 | 1952.2 | 319.6 | 239.3 | 258.2 | 278
2229.2 | 1953.2 | 319.3 | 238.9 | 257.8 | 277.6
2230.2 | 1954.2 | 319 | 238.5 | 257.5 | 277.2
2231.2 | 1955.2 | 318.7 | 238.1 | 257.1 | 276.8
2232.2 | 1956.2 | 318.4 | 237.6 | 256.7 | 276.4
2233.2 | 1957.2 | 318.2 | 237.2 | 256.3 | 276.1
2234.2 | 1958.2 | 317.9 | 236.8 | 256.1 | 275.7
2235.2 | 1959.2 | 317.6 | 236.4 | 255.9 | 275.3
2236.2 | 1960.2 | 317.3 | 236.1 | 255.6 | 275
2237.2 | 1961.2 | 317 | 235.6 | 255.2 | 274.6
2238.2 | 1962.2 | 316.7 | 235.2 | 254.8 | 274.3
2239.2 | 1963.2 | 316.4 | 234.8 | 254.5 | 273.9
2240.2 | 1964.2 | 316.1 | 234.4 | 254 | 273.5
2241.2 | 1965.2 | 315.8 | 233.9 | 253.5 | 273.1
2242.2 | 1966.2 | 315.6 | 233.5 | 253.2 | 272.8
2243.2 | 1967.2 | 315.3 | 233.1 | 253 | 272.4
2244.2 | 1968.2 | 315 | 232.7 | 252.7 | 272.1
2245.2 | 1969.2 | 314.7 | 232.3 | 252.3 | 271.7
2246.2 | 1970.2 | 314.4 | 231.9 | 251.9 | 271.3
2247.2 | 1971.2 | 314.1 | 231.5 | 251.5 | 271
2248.2 | 1972.2 | 313.8 | 231.1 | 251.1 | 270.6
2249.2 | 1973.2 | 313.5 | 230.7 | 250.7 | 270.2
2250.2 | 1974.2 | 313.3 | 230.3 | 250.5 | 269.9
2251.2 | 1975.2 | 313 | 229.9 | 250.3 | 269.5
2252.2 | 1976.2 | 312.7 | 229.5 | 249.9 | 269.2
2253.2 | 1977.2 | 312.4 | 229.1 | 249.6 | 268.8
2254.2 | 1978.2 | 312.1 | 228.8 | 249.3 | 268.4
2255.2 | 1979.2 | 311.8 | 228.4 | 249.1 | 268.1
2256.2 | 1980.2 | 311.5 | 228.1 | 248.8 | 267.7
2257.2 | 1981.2 | 311.3 | 227.7 | 248.5 | 267.4
2258.2 | 1982.2 | 311 | 227.3 | 248.2 | 267
2259.2 | 1983.2 | 310.7 | 226.9 | 247.9 | 266.6
2260.2 | 1984.2 | 310.4 | 226.5 | 247.7 | 266.3
2261.2 | 1985.2 | 310.1 | 226 | 247.3 | 265.9
2262.2 | 1986.2 | 309.8 | 225.6 | 247.1 | 265.6
2263.2 | 1987.2 | 309.6 | 225.2 | 246.8 | 265.3
2264.2 | 1988.2 | 309.3 | 224.9 | 246.6 | 264.9
2265.2 | 1989.2 | 309 | 224.6 | 246.4 | 264.6
2266.2 | 1990.2 | 308.7 | 224.2 | 246.1 | 264.2
2267.2 | 1991.2 | 308.5 | 223.8 | 245.8 | 263.9
2268.2 | 1992.2 | 308.2 | 223.5 | 245.5 | 263.5
2269.2 | 1993.2 | 307.9 | 223.1 | 245.2 | 263.2
2270.2 | 1994.2 | 307.6 | 222.8 | 244.9 | 262.9
2271.2 | 1995.2 | 307.3 | 222.4 | 244.5 | 262.5
2272.2 | 1996.2 | 307.1 | 221.9 | 244.2 | 262.1
2273.2 | 1997.2 | 306.8 | 221.5 | 243.9 | 261.8
2274.2 | 1998.2 | 306.5 | 221.1 | 243.6 | 261.4
2275.2 | 1999.2 | 306.2 | 220.7 | 243.3 | 261.1
2276.2 | 2000.2 | 306 | 220.3 | 243.1 | 260.7
2277.2 | 2001.2 | 305.7 | 219.9 | 242.9 | 260.4
2278.2 | 2002.2 | 305.4 | 219.5 | 242.6 | 260.1
2279.2 | 2003.2 | 305.1 | 219.1 | 242.3 | 259.7
2280.2 | 2004.2 | 304.8 | 218.8 | 241.9 | 259.4
2281.2 | 2005.2 | 304.6 | 218.5 | 241.6 | 259.1
2282.2 | 2006.2 | 304.3 | 218.1 | 241.4 | 258.7
2283.2 | 2007.2 | 304 | 217.7 | 241.1 | 258.4
2284.2 | 2008.2 | 303.7 | 217.5 | 240.8 | 258
2285.2 | 2009.2 | 303.5 | 217.2 | 240.4 | 257.7
2286.2 | 2010.2 | 303.2 | 216.8 | 240 | 257.4
2287.2 | 2011.2 | 302.9 | 216.5 | 239.7 | 257
2288.2 | 2012.2 | 302.6 | 216.1 | 239.5 | 256.7
2289.2 | 2013.2 | 302.4 | 215.8 | 239.1 | 256.4
2290.2 | 2014.2 | 302.1 | 215.4 | 238.7 | 256.1
2291.2 | 2015.2 | 301.8 | 215.2 | 238.4 | 255.8
2292.2 | 2016.2 | 301.5 | 214.9 | 238.1 | 255.4
2293.2 | 2017.2 | 301.3 | 214.7 | 237.7 | 255.1
2294.2 | 2018.2 | 301 | 214.4 | 237.3 | 254.8
2295.2 | 2019.2 | 300.7 | 214.1 | 236.9 | 254.5
2296.2 | 2020.2 | 300.4 | 213.7 | 236.6 | 254.2
2297.2 | 2021.2 | 300.2 | 213.4 | 236.4 | 253.8
2298.2 | 2022.2 | 299.9 | 213 | 236.1 | 253.5
2299.2 | 2023.2 | 299.6 | 212.6 | 235.7 | 253.2
2300.2 | 2024.2 | 299.4 | 212.2 | 235.4 | 252.8
2301.2 | 2025.2 | 299.1 | 211.9 | 235.1 | 252.5
2302.2 | 2026.2 | 298.8 | 211.6 | 234.7 | 252.2
2303.2 | 2027.2 | 298.5 | 211.2 | 234.4 | 251.9
2304.2 | 2028.2 | 298.3 | 210.9 | 234.1 | 251.5
2305.2 | 2029.2 | 298 | 210.6 | 233.9 | 251.2
2306.2 | 2030.2 | 297.7 | 210.3 | 233.6 | 250.9
2307.2 | 2031.2 | 297.4 | 209.9 | 233.4 | 250.6
2308.2 | 2032.2 | 297.2 | 209.5 | 233.1 | 250.3
2309.2 | 2033.2 | 296.9 | 209.2 | 232.8 | 250
2310.2 | 2034.2 | 296.6 | 208.8 | 232.6 | 249.6
2311.2 | 2035.2 | 296.4 | 208.5 | 232.3 | 249.3
2312.2 | 2036.2 | 296.1 | 208.2 | 232.1 | 249
2313.2 | 2037.2 | 295.8 | 207.8 | 231.7 | 248.7
2314.2 | 2038.2 | 295.5 | 207.4 | 231.4 | 248.4
2315.2 | 2039.2 | 295.3 | 207.1 | 231.1 | 248.1
2316.2 | 2040.2 | 295 | 206.8 | 230.8 | 247.7
2317.2 | 2041.2 | 294.7 | 206.5 | 230.3 | 247.4
2318.2 | 2042.2 | 294.4 | 206.2 | 230 | 247.1
2319.2 | 2043.2 | 294.2 | 205.8 | 229.8 | 246.8
2320.2 | 2044.2 | 293.9 | 205.4 | 229.5 | 246.5
2321.2 | 2045.2 | 293.6 | 205.1 | 229.3 | 246.2
2322.2 | 2046.2 | 293.4 | 204.8 | 229.1 | 245.9
2323.2 | 2047.2 | 293.1 | 204.4 | 228.8 | 245.6
2324.2 | 2048.2 | 292.8 | 204.1 | 228.6 | 245.3
2325.2 | 2049.2 | 292.5 | 203.7 | 228.2 | 245
2326.2 | 2050.2 | 292.3 | 203.4 | 227.9 | 244.6
2327.2 | 2051.2 | 292 | 203.1 | 227.7 | 244.3
2328.2 | 2052.2 | 291.7 | 202.8 | 227.4 | 244
2329.2 | 2053.2 | 291.5 | 202.4 | 227.1 | 243.7
2330.2 | 2054.2 | 291.2 | 202 | 226.7 | 243.4
2331.2 | 2055.2 | 290.9 | 201.6 | 226.4 | 243.1
2332.2 | 2056.2 | 290.6 | 201.3 | 226.1 | 242.7
2333.2 | 2057.2 | 290.4 | 201 | 225.9 | 242.5
2334.2 | 2058.2 | 290.1 | 200.7 | 225.7 | 242.2
2335.2 | 2059.2 | 289.8 | 200.3 | 225.5 | 241.9
2336.2 | 2060.2 | 289.6 | 200.1 | 225.2 | 241.6
2337.2 | 2061.2 | 289.3 | 199.8 | 224.9 | 241.3
2338.2 | 2062.2 | 289 | 199.5 | 224.5 | 241
2339.2 | 2063.2 | 288.7 | 199.2 | 224.3 | 240.7
2340.2 | 2064.2 | 288.5 | 199 | 224 | 240.4
2341.2 | 2065.2 | 288.2 | 198.7 | 223.8 | 240.1
2342.2 | 2066.2 | 287.9 | 198.5 | 223.5 | 239.8
2343.2 | 2067.2 | 287.7 | 198.3 | 223.2 | 239.6
2344.2 | 2068.2 | 287.4 | 198 | 222.9 | 239.3
2345.2 | 2069.2 | 287.1 | 197.7 | 222.6 | 239
2346.2 | 2070.2 | 286.9 | 197.5 | 222.3 | 238.7
2347.2 | 2071.2 | 286.6 | 197.2 | 222 | 238.4
2348.2 | 2072.2 | 286.3 | 196.9 | 221.7 | 238.1
2349.2 | 2073.2 | 286.1 | 196.6 | 221.4 | 237.8
2350.2 | 2074.2 | 285.8 | 196.3 | 221.2 | 237.5
2351.2 | 2075.2 | 285.5 | 196 | 221 | 237.3
2352.2 | 2076.2 | 285.3 | 195.7 | 220.7 | 237
2353.2 | 2077.2 | 285 | 195.5 | 220.4 | 236.7
2354.2 | 2078.2 | 284.7 | 195.2 | 220.1 | 236.4
2355.2 | 2079.2 | 284.5 | 194.9 | 219.9 | 236.1
2356.2 | 2080.2 | 284.2 | 194.6 | 219.6 | 235.8
2357.2 | 2081.2 | 284 | 194.3 | 219.4 | 235.6
2358.2 | 2082.2 | 283.7 | 194.1 | 219.1 | 235.3
2359.2 | 2083.2 | 283.4 | 193.8 | 218.9 | 235
2360.2 | 2084.2 | 283.2 | 193.5 | 218.6 | 234.7
2361.2 | 2085.2 | 282.9 | 193.2 | 218.3 | 234.4
2362.2 | 2086.2 | 282.6 | 192.9 | 218 | 234.1
2363.2 | 2087.2 | 282.4 | 192.7 | 217.8 | 233.8
2364.2 | 2088.2 | 282.1 | 192.5 | 217.6 | 233.6
2365.2 | 2089.2 | 281.8 | 192.2 | 217.2 | 233.3
2366.2 | 2090.2 | 281.6 | 191.9 | 216.9 | 233
2367.2 | 2091.2 | 281.3 | 191.7 | 216.6 | 232.7
2368.2 | 2092.2 | 281.1 | 191.4 | 216.4 | 232.5
2369.2 | 2093.2 | 280.8 | 191.2 | 216.2 | 232.2
2370.2 | 2094.2 | 280.5 | 190.9 | 215.8 | 231.9
2371.2 | 2095.2 | 280.3 | 190.7 | 215.5 | 231.7
2372.2 | 2096.2 | 280 | 190.5 | 215.2 | 231.4
2373.2 | 2097.2 | 279.7 | 190.2 | 215 | 231.1
2374.2 | 2098.2 | 279.5 | 190 | 214.7 | 230.8
2375.2 | 2099.2 | 279.2 | 189.7 | 214.4 | 230.5
2376.2 | 2100.2 | 278.9 | 189.4 | 214.2 | 230.2
2377.2 | 2101.2 | 278.7 | 189.2 | 213.9 | 230
2378.2 | 2102.2 | 278.4 | 188.9 | 213.7 | 229.7
2379.2 | 2103.2 | 278.2 | 188.7 | 213.5 | 229.4
2380.2 | 2104.2 | 277.9 | 188.4 | 213.2 | 229.2
2381.2 | 2105.2 | 277.6 | 188.2 | 213 | 228.9
2382.2 | 2106.2 | 277.4 | 187.9 | 212.7 | 228.6
2383.2 | 2107.2 | 277.1 | 187.7 | 212.5 | 228.4
2384.2 | 2108.2 | 276.9 | 187.4 | 212.1 | 228.1
2385.2 | 2109.2 | 276.6 | 187.2 | 212 | 227.9
2386.2 | 2110.2 | 276.4 | 186.9 | 211.8 | 227.6
2387.2 | 2111.2 | 276.1 | 186.6 | 211.6 | 227.3
2388.2 | 2112.2 | 275.9 | 186.2 | 211.3 | 227.1
2389.2 | 2113.2 | 275.6 | 186 | 211.1 | 226.8
2390.2 | 2114.2 | 275.3 | 185.8 | 210.9 | 226.6
2391.2 | 2115.2 | 275.1 | 185.4 | 210.7 | 226.3
2392.2 | 2116.2 | 274.8 | 185.2 | 210.4 | 226
2393.2 | 2117.2 | 274.6 | 185 | 210.2 | 225.8
2394.2 | 2118.2 | 274.3 | 184.7 | 210 | 225.5
2395.2 | 2119.2 | 274.1 | 184.4 | 209.8 | 225.2
2396.2 | 2120.2 | 273.8 | 184.1 | 209.4 | 224.9
2397.2 | 2121.2 | 273.5 | 183.9 | 209.3 | 224.6
2398.2 | 2122.2 | 273.3 | 183.6 | 209.1 | 224.4
2399.2 | 2123.2 | 273 | 183.4 | 208.9 | 224.2
2400.2 | 2124.2 | 272.8 | 183.2 | 208.7 | 223.9
2401.2 | 2125.2 | 272.5 | 182.9 | 208.5 | 223.6
2402.2 | 2126.2 | 272.3 | 182.7 | 208.3 | 223.4
2403.2 | 2127.2 | 272 | 182.5 | 208.1 | 223.1
2404.2 | 2128.2 | 271.8 | 182.2 | 207.9 | 222.8
2405.2 | 2129.2 | 271.5 | 182 | 207.7 | 222.6
2406.2 | 2130.2 | 271.3 | 181.7 | 207.5 | 222.3
2407.2 | 2131.2 | 271 | 181.5 | 207.3 | 222
2408.2 | 2132.2 | 270.8 | 181.2 | 207.1 | 221.8
2409.2 | 2133.2 | 270.5 | 180.9 | 206.8 | 221.5
2410.2 | 2134.2 | 270.3 | 180.6 | 206.6 | 221.3
2411.2 | 2135.2 | 270 | 180.4 | 206.4 | 221
2412.2 | 2136.2 | 269.8 | 180.1 | 206.1 | 220.7
2413.2 | 2137.2 | 269.5 | 179.9 | 205.9 | 220.5
2414.2 | 2138.2 | 269.3 | 179.6 | 205.6 | 220.2

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 4 |  |  | 2006-10-30 | 10:40
39020.4395 | 1 | 0 | 1 | XLPE | 3-C | Tray G | IRMS | 1
39020.4397 | 1 | 0 | 1 |  | 250 kW |  | Bundle
39020.4399 | 0 | 0 | 1
39020.4401 | 1 | 0 | 1
39020.4403 | 0 | 0 | 1
39020.4405 | 1 | 0 | 1
39020.4407 | 1 | 0 | 1
39020.4409 | 0 | 0 | 1
39020.4411 | 1 | 0 | 1
39020.4413 | 1 | 0 | 1
39020.4414 | 1 | 0 | 1
39020.4416 | 1 | 0 | 1
39020.4418 | 1 | 0 | 1
39020.442 | 1 | 0 | 1
39020.4422 | 1 | 0 | 1
39020.4424 | 1 | 0 | 1
39020.4426 | 1 | 0 | 1
39020.4428 | 1 | 0 | 1
39020.443 | 1 | 0 | 1
39020.4432 | 0 | 0 | 1
39020.4434 | 0 | 0 | 1
39020.4436 | 0 | 0 | 1
39020.4438 | 1 | 0 | 1
39020.444 | 1 | 0 | 1
39020.4442 | 0 | 0 | 1
39020.4444 | 1 | 0 | 1
39020.4446 | 1 | 0 | 1
39020.4448 | 1 | 0 | 1
39020.4449 | 1 | 0 | 1
39020.4451 | 1 | 0 | 1
39020.4453 | 1 | 0 | 1
39020.4455 | 1 | 0 | 1
39020.4457 | 1 | 0 | 1
39020.4459 | 1 | 0 | 1
39020.4461 | 1 | 0 | 1
39020.4463 | 1 | 0 | 1
39020.4465 | 1 | 0 | 1
39020.4467 | 1 | 0 | 1
39020.4469 | 1 | 0 | 1
39020.4471 | 1 | 0 | 1
39020.4473 | 1 | 0 | 1
39020.4475 | 1 | 0 | 1
39020.4477 | 1 | 0 | 1
39020.4479 | 1 | 0 | 1
39020.4481 | 1 | 0 | 1
39020.4483 | 1 | 0 | 1
39020.4484 | 1 | 0 | 1
39020.4486 | 1 | 0 | 1
39020.4488 | 1 | 0 | 1
39020.449 | 1 | 0 | 1
39020.4492 | 1 | 0 | 1
39020.4494 | 1 | 0 | 1
39020.4496 | 1 | 0 | 1
39020.4498 | 1 | 0 | 1
39020.45 | 1 | 0 | 1
39020.4502 | 1 | 0 | 1
39020.4504 | 1 | 0 | 1
39020.4506 | 1 | 0 | 1
39020.4508 | 1 | 0 | 1
39020.451 | 1 | 0 | 1
39020.4512 | 1 | 0 | 1
39020.4514 | 1 | 0 | 1
39020.4516 | 1 | 0 | 1
39020.4517 | 1 | 0 | 1
39020.4519 | 1 | 0 | 1
39020.4521 | 1 | 0 | 1
39020.4523 | 1 | 0 | 1
39020.4525 | 1 | 0 | 1
39020.4527 | 1 | 0 | 1
39020.4529 | 1 | 0 | 1
39020.4531 | 1 | 0 | 1
39020.4533 | 1 | 0 | 1
39020.4535 | 1 | 0 | 1
39020.4537 | 1 | 0 | 1
39020.4539 | 1 | 0 | 1
39020.4541 | 1 | 0 | 1
39020.4543 | 1 | 0 | 1
39020.4545 | 1 | 0 | 1
39020.4547 | 1 | 0 | 1
39020.4549 | 1 | 0 | 1
39020.4551 | 1 | 0 | 1
39020.4553 | 1 | 0 | 1
39020.4554 | 1 | 0 | 1
39020.4556 | 1 | 0 | 1
39020.4558 | 1 | 0 | 1
39020.456 | 1 | 0 | 1
39020.4562 | 1 | 0 | 1
39020.4564 | 1 | 0 | 1
39020.4566 | 1 | 0 | 1
39020.4568 | 1 | 0 | 1
39020.457 | 1 | 0 | 1
39020.4572 | 1 | 0 | 1
39020.4574 | 1 | 0 | 1
39020.4576 | 1 | 0 | 1
39020.4578 | 1 | 0 | 1
39020.458 | 1 | 0 | 1
39020.4582 | 1 | 0 | 1
39020.4584 | 1 | 0 | 1
39020.4586 | 1 | 0 | 1
39020.4587 | 1 | 0 | 1
39020.4589 | 1 | 0 | 1
39020.4591 | 1 | 0 | 1
39020.4593 | 1 | 0 | 1
39020.4595 | 1 | 0 | 1
39020.4597 | 1 | 0 | 1
39020.4599 | 1 | 0 | 1
39020.4601 | 1 | 0 | 1
39020.4603 | 1 | 0 | 1
39020.4605 | 1 | 0 | 1
39020.4607 | 1 | 0 | 1
39020.4609 | 1 | 0 | 1
39020.4611 | 1 | 0 | 1
39020.4613 | 1 | 0 | 1
39020.4615 | 1 | 0 | 1
39020.4617 | 1 | 0 | 1
39020.4619 | 1 | 0 | 1
39020.4621 | 1 | 0 | 1
39020.4622 | 1 | 0 | 1
39020.4624 | 1 | 0 | 1
39020.4626 | 1 | 0 | 1
39020.4628 | 1 | 0 | 1
39020.463 | 1 | 0 | 1
39020.4632 | 1 | 0 | 1
39020.4634 | 1 | 0 | 1
39020.4636 | 1 | 0 | 1
39020.4638 | 1 | 0 | 1
39020.464 | 1 | 0 | 1
39020.4642 | 1 | 0 | 1
39020.4644 | 1 | 0 | 1
39020.4646 | 1 | 0 | 1
39020.4648 | 1 | 0 | 1
39020.465 | 1 | 0 | 1
39020.4652 | 1 | 0 | 1
39020.4654 | 1 | 0 | 1
39020.4656 | 1 | 0 | 1
39020.4658 | 1 | 0 | 1
1
39020.4395 | 0 | 0 | 2
39020.4397 | 1 | 0 | 2
39020.4399 | 1 | 0 | 2
39020.4401 | 1 | 0 | 2
39020.4403 | 1 | 0 | 2
39020.4405 | 1 | 0 | 2
39020.4407 | 1 | 0 | 2
39020.4409 | 1 | 0 | 2
39020.4411 | 1 | 0 | 2
39020.4413 | 1 | 0 | 2
39020.4415 | 1 | 0 | 2
39020.4417 | 1 | 0 | 2
39020.4419 | 1 | 0 | 2
39020.442 | 1 | 0 | 2
39020.4422 | 1 | 0 | 2
39020.4424 | 1 | 0 | 2
39020.4426 | 1 | 0 | 2
39020.4428 | 1 | 0 | 2
39020.443 | 1 | 0 | 2
39020.4432 | 1 | 0 | 2
39020.4434 | 1 | 0 | 2
39020.4436 | 1 | 0 | 2
39020.4438 | 0 | 0 | 2
39020.444 | 1 | 0 | 2
39020.4442 | 1 | 0 | 2
39020.4444 | 1 | 0 | 2
39020.4446 | 1 | 0 | 2
39020.4448 | 1 | 0 | 2
39020.445 | 1 | 0 | 2
39020.4452 | 1 | 0 | 2
39020.4453 | 1 | 0 | 2
39020.4455 | 1 | 0 | 2
39020.4457 | 1 | 0 | 2
39020.4459 | 1 | 0 | 2
39020.4461 | 0 | 0 | 2
39020.4463 | 1 | 0 | 2
39020.4465 | 1 | 0 | 2
39020.4467 | 1 | 0 | 2
39020.4469 | 1 | 0 | 2
39020.4471 | 1 | 0 | 2
39020.4473 | 1 | 0 | 2
39020.4475 | 1 | 0 | 2
39020.4477 | 1 | 0 | 2
39020.4479 | 1 | 0 | 2
39020.4481 | 1 | 0 | 2
39020.4483 | 1 | 0 | 2
39020.4485 | 0 | 0 | 2
39020.4487 | 1 | 0 | 2
39020.4489 | 1 | 0 | 2
39020.449 | 1 | 0 | 2
39020.4492 | 1 | 0 | 2
39020.4494 | 1 | 0 | 2
39020.4496 | 1 | 0 | 2
39020.4498 | 1 | 0 | 2
39020.45 | 1 | 0 | 2
39020.4502 | 1 | 0 | 2
39020.4504 | 0 | 0 | 2
39020.4506 | 1 | 0 | 2
39020.4508 | 1 | 0 | 2
39020.451 | 1 | 0 | 2
39020.4512 | 0 | 0 | 2
39020.4514 | 1 | 0 | 2
39020.4516 | 1 | 0 | 2
39020.4518 | 1 | 0 | 2
39020.452 | 1 | 0 | 2
39020.4522 | 1 | 0 | 2
39020.4523 | 1 | 0 | 2
39020.4525 | 1 | 0 | 2
39020.4527 | 1 | 0 | 2
39020.4529 | 1 | 0 | 2
39020.4531 | 1 | 0 | 2
39020.4533 | 1 | 0 | 2
39020.4535 | 1 | 0 | 2
39020.4537 | 1 | 0 | 2
39020.4539 | 1 | 0 | 2
39020.4541 | 1 | 0 | 2
39020.4543 | 1 | 0 | 2
39020.4545 | 1 | 0 | 2
39020.4547 | 1 | 0 | 2
39020.4549 | 1 | 0 | 2
39020.4551 | 1 | 0 | 2
39020.4553 | 0 | 0 | 2
39020.4555 | 1 | 0 | 2
39020.4557 | 0 | 0 | 2
39020.4558 | 1 | 0 | 2
39020.456 | 1 | 0 | 2
39020.4562 | 1 | 0 | 2
39020.4564 | 0 | 0 | 2
39020.4566 | 0 | 0 | 2
39020.4568 | 1 | 0 | 2
39020.457 | 1 | 0 | 2
39020.4572 | 1 | 0 | 2
39020.4574 | 1 | 0 | 2
39020.4576 | 1 | 0 | 2
39020.4578 | 1 | 0 | 2
39020.458 | 1 | 0 | 2
39020.4582 | 1 | 0 | 2
39020.4584 | 1 | 0 | 2
39020.4586 | 1 | 0 | 2
39020.4588 | 1 | 0 | 2
39020.459 | 1 | 0 | 2
39020.4592 | 1 | 0 | 2
39020.4594 | 1 | 0 | 2
39020.4595 | 1 | 0 | 2
39020.4597 | 1 | 0 | 2
39020.4599 | 1 | 0 | 2
39020.4601 | 1 | 0 | 2
39020.4603 | 1 | 0 | 2
39020.4605 | 1 | 0 | 2
39020.4607 | 1 | 0 | 2
39020.4609 | 1 | 0 | 2
39020.4611 | 1 | 0 | 2
39020.4613 | 1 | 0 | 2
39020.4615 | 1 | 0 | 2
39020.4617 | 1 | 0 | 2
39020.4621 | 1 | 0 | 2
39020.4623 | 1 | 0 | 2
39020.4625 | 1 | 0 | 2
39020.4627 | 1 | 0 | 2
39020.4628 | 1 | 0 | 2
39020.463 | 1 | 0 | 2
39020.4632 | 1 | 0 | 2
39020.4634 | 1 | 0 | 2
39020.4636 | 1 | 0 | 2
39020.4638 | 1 | 0 | 2
39020.464 | 1 | 0 | 2
39020.4642 | 1 | 0 | 2
39020.4644 | 1 | 0 | 2
39020.4646 | 1 | 0 | 2
39020.4648 | 1 | 0 | 2
39020.465 | 1 | 0 | 2
39020.4652 | 1 | 0 | 2
39020.4654 | 1 | 0 | 2
39020.4656 | 1 | 0 | 2
39020.4658 | 1 | 0 | 2
2
39020.4395 | 1 | 0 | 3
39020.4397 | 1 | 0 | 3
39020.4399 | 1 | 0 | 3
39020.4401 | 1 | 0 | 3
39020.4403 | 1 | 0 | 3
39020.4405 | 1 | 0 | 3
39020.4407 | 1 | 0 | 3
39020.4409 | 0 | 0 | 3
39020.4411 | 1 | 0 | 3
39020.4413 | 0 | 0 | 3
39020.4415 | 1 | 0 | 3
39020.4417 | 1 | 0 | 3
39020.4419 | 1 | 0 | 3
39020.4421 | 1 | 0 | 3
39020.4423 | 1 | 0 | 3
39020.4425 | 0 | 0 | 3
39020.4427 | 1 | 0 | 3
39020.4428 | 1 | 0 | 3
39020.443 | 1 | 0 | 3
39020.4432 | 1 | 0 | 3
39020.4434 | 0 | 0 | 3
39020.4436 | 1 | 0 | 3
39020.4438 | 1 | 0 | 3
39020.444 | 1 | 0 | 3
39020.4442 | 1 | 0 | 3
39020.4444 | 0 | 0 | 3
39020.4446 | 1 | 0 | 3
39020.4448 | 1 | 0 | 3
39020.445 | 1 | 0 | 3
39020.4452 | 1 | 0 | 3
39020.4454 | 1 | 0 | 3
39020.4456 | 1 | 0 | 3
39020.4458 | 1 | 0 | 3
39020.4459 | 1 | 0 | 3
39020.4461 | 1 | 0 | 3
39020.4463 | 1 | 0 | 3
39020.4465 | 1 | 0 | 3
39020.4467 | 1 | 0 | 3
39020.4469 | 1 | 0 | 3
39020.4471 | 1 | 0 | 3
39020.4473 | 1 | 0 | 3
39020.4475 | 1 | 0 | 3
39020.4477 | 1 | 0 | 3
39020.4479 | 1 | 0 | 3
39020.4481 | 1 | 0 | 3
39020.4483 | 1 | 0 | 3
39020.4485 | 1 | 0 | 3
39020.4487 | 1 | 0 | 3
39020.4489 | 1 | 0 | 3
39020.4491 | 0 | 0 | 3
39020.4493 | 1 | 0 | 3
39020.4494 | 1 | 0 | 3
39020.4496 | 1 | 0 | 3
39020.4498 | 1 | 0 | 3
39020.45 | 1 | 0 | 3
39020.4502 | 1 | 0 | 3
39020.4504 | 0 | 0 | 3
39020.4506 | 1 | 0 | 3
39020.4508 | 1 | 0 | 3
39020.451 | 1 | 0 | 3
39020.4512 | 1 | 0 | 3
39020.4514 | 1 | 0 | 3
39020.4516 | 1 | 0 | 3
39020.4518 | 1 | 0 | 3
39020.452 | 1 | 0 | 3
39020.4522 | 1 | 0 | 3
39020.4524 | 1 | 0 | 3
39020.4526 | 1 | 0 | 3
39020.4528 | 1 | 0 | 3
39020.453 | 1 | 0 | 3
39020.4531 | 1 | 0 | 3
39020.4533 | 1 | 0 | 3
39020.4535 | 1 | 0 | 3
39020.4537 | 1 | 0 | 3
39020.4539 | 0 | 0 | 3
39020.4541 | 1 | 0 | 3
39020.4543 | 1 | 0 | 3
39020.4545 | 1 | 0 | 3
39020.4547 | 1 | 0 | 3
39020.4549 | 1 | 0 | 3
39020.4551 | 1 | 0 | 3
39020.4553 | 1 | 0 | 3
39020.4555 | 1 | 0 | 3
39020.4557 | 1 | 0 | 3
39020.4559 | 1 | 0 | 3
39020.4561 | 1 | 0 | 3
39020.4563 | 1 | 0 | 3
39020.4564 | 1 | 0 | 3
39020.4566 | 1 | 0 | 3
39020.4568 | 1 | 0 | 3
39020.457 | 1 | 0 | 3
39020.4572 | 1 | 0 | 3
39020.4574 | 1 | 0 | 3
39020.4576 | 1 | 0 | 3
39020.4578 | 1 | 0 | 3
39020.458 | 1 | 0 | 3
39020.4582 | 1 | 0 | 3
39020.4584 | 1 | 0 | 3
39020.4586 | 1 | 0 | 3
39020.4588 | 1 | 0 | 3
39020.459 | 1 | 0 | 3
39020.4592 | 1 | 0 | 3
39020.4594 | 1 | 0 | 3
39020.4596 | 1 | 0 | 3
39020.4598 | 1 | 0 | 3
39020.4599 | 1 | 0 | 3
39020.4601 | 1 | 0 | 3
39020.4603 | 0 | 0 | 3
39020.4605 | 1 | 0 | 3
39020.4607 | 1 | 0 | 3
39020.4609 | 1 | 0 | 3
39020.4611 | 1 | 0 | 3
39020.4613 | 1 | 0 | 3
39020.4615 | 1 | 0 | 3
39020.4617 | 1 | 0 | 3
39020.4619 | 1 | 0 | 3
39020.4621 | 1 | 0 | 3
39020.4623 | 0 | 0 | 3
39020.4625 | 1 | 0 | 3
39020.4627 | 1 | 0 | 3
39020.4629 | 1 | 0 | 3
39020.4631 | 1 | 0 | 3
39020.4633 | 1 | 0 | 3
39020.4634 | 1 | 0 | 3
39020.4636 | 1 | 0 | 3
39020.4638 | 1 | 0 | 3
39020.464 | 1 | 0 | 3
39020.4642 | 1 | 0 | 3
39020.4644 | 1 | 0 | 3
39020.4646 | 1 | 0 | 3
39020.4648 | 1 | 0 | 3
39020.465 | 1 | 0 | 3
39020.4652 | 1 | 0 | 3
39020.4654 | 1 | 0 | 3
39020.4656 | 1 | 0 | 3
39020.4658 | 1 | 0 | 3
3
39020.4395 | 1 | 0 | 4
39020.4397 | 1 | 0 | 4
39020.4399 | 1 | 0 | 4
39020.4401 | 1 | 0 | 4
39020.4403 | 1 | 0 | 4
39020.4405 | 0 | 0 | 4
39020.4407 | 1 | 0 | 4
39020.4409 | 1 | 0 | 4
39020.4411 | 1 | 0 | 4
39020.4413 | 1 | 0 | 4
39020.4415 | 1 | 0 | 4
39020.4417 | 1 | 0 | 4
39020.4419 | 1 | 0 | 4
39020.4421 | 1 | 0 | 4
39020.4423 | 1 | 0 | 4
39020.4425 | 0 | 0 | 4
39020.4427 | 1 | 0 | 4
39020.4429 | 1 | 0 | 4
39020.4431 | 1 | 0 | 4
39020.4432 | 1 | 0 | 4
39020.4434 | 0 | 0 | 4
39020.4436 | 1 | 0 | 4
39020.4438 | 1 | 0 | 4
39020.444 | 1 | 0 | 4
39020.4442 | 1 | 0 | 4
39020.4444 | 1 | 0 | 4
39020.4446 | 1 | 0 | 4
39020.4448 | 1 | 0 | 4
39020.445 | 1 | 0 | 4
39020.4452 | 1 | 0 | 4
39020.4454 | 1 | 0 | 4
39020.4456 | 1 | 0 | 4
39020.4458 | 1 | 0 | 4
39020.446 | 1 | 0 | 4
39020.4462 | 1 | 0 | 4
39020.4464 | 1 | 0 | 4
39020.4466 | 1 | 0 | 4
39020.4467 | 0 | 0 | 4
39020.4469 | 1 | 0 | 4
39020.4471 | 0 | 0 | 4
39020.4473 | 1 | 0 | 4
39020.4475 | 1 | 0 | 4
39020.4477 | 1 | 0 | 4
39020.4479 | 1 | 0 | 4
39020.4481 | 1 | 0 | 4
39020.4483 | 1 | 0 | 4
39020.4485 | 1 | 0 | 4
39020.4487 | 1 | 0 | 4
39020.4489 | 1 | 0 | 4
39020.4491 | 1 | 0 | 4
39020.4493 | 1 | 0 | 4
39020.4495 | 0 | 0 | 4
39020.4497 | 1 | 0 | 4
39020.4498 | 0 | 0 | 4
39020.45 | 1 | 0 | 4
39020.4502 | 1 | 0 | 4
39020.4504 | 1 | 0 | 4
39020.4506 | 1 | 0 | 4
39020.4508 | 1 | 0 | 4
39020.451 | 1 | 0 | 4
39020.4512 | 1 | 0 | 4
39020.4514 | 1 | 0 | 4
39020.4516 | 1 | 0 | 4
39020.4518 | 1 | 0 | 4
39020.452 | 1 | 0 | 4
39020.4522 | 1 | 0 | 4
39020.4524 | 1 | 0 | 4
39020.4526 | 1 | 0 | 4
39020.4528 | 1 | 0 | 4
39020.453 | 1 | 0 | 4
39020.4532 | 1 | 0 | 4
39020.4534 | 1 | 0 | 4
39020.4536 | 1 | 0 | 4
39020.4537 | 1 | 0 | 4
39020.4539 | 1 | 0 | 4
39020.4541 | 1 | 0 | 4
39020.4543 | 1 | 0 | 4
39020.4545 | 1 | 0 | 4
39020.4547 | 1 | 0 | 4
39020.4549 | 1 | 0 | 4
39020.4551 | 1 | 0 | 4
39020.4553 | 1 | 0 | 4
39020.4555 | 1 | 0 | 4
39020.4557 | 1 | 0 | 4
39020.4559 | 1 | 0 | 4
39020.4561 | 1 | 0 | 4
39020.4563 | 1 | 0 | 4
39020.4565 | 1 | 0 | 4
39020.4567 | 1 | 0 | 4
39020.4569 | 1 | 0 | 4
39020.457 | 1 | 0 | 4
39020.4572 | 1 | 0 | 4
39020.4574 | 1 | 0 | 4
39020.4576 | 1 | 0 | 4
39020.4578 | 1 | 0 | 4
39020.458 | 1 | 0 | 4
39020.4582 | 0 | 0 | 4
39020.4584 | 1 | 0 | 4
39020.4586 | 1 | 0 | 4
39020.4588 | 1 | 0 | 4
39020.459 | 1 | 0 | 4
39020.4592 | 1 | 0 | 4
39020.4594 | 0 | 0 | 4
39020.4596 | 1 | 0 | 4
39020.4598 | 1 | 0 | 4
39020.46 | 1 | 0 | 4
39020.4602 | 1 | 0 | 4
39020.4603 | 1 | 0 | 4
39020.4605 | 1 | 0 | 4
39020.4607 | 1 | 0 | 4
39020.4609 | 1 | 0 | 4
39020.4611 | 1 | 0 | 4
39020.4613 | 1 | 0 | 4
39020.4615 | 1 | 0 | 4
39020.4617 | 1 | 0 | 4
39020.4619 | 1 | 0 | 4
39020.4621 | 1 | 0 | 4
39020.4623 | 1 | 0 | 4
39020.4625 | 1 | 0 | 4
39020.4627 | 1 | 0 | 4
39020.4629 | 1 | 0 | 4
39020.4631 | 1 | 0 | 4
39020.4633 | 0 | 0 | 4
39020.4635 | 1 | 0 | 4
39020.4637 | 1 | 0 | 4
39020.4639 | 0 | 0 | 4
39020.4641 | 1 | 0 | 4
39020.4642 | 1 | 0 | 4
39020.4644 | 1 | 0 | 4
39020.4646 | 1 | 0 | 4
39020.4648 | 1 | 0 | 4
39020.465 | 0 | 0 | 4
39020.4652 | 1 | 0 | 4
39020.4654 | 1 | 0 | 4
39020.4656 | 1 | 0 | 4
39020.4658 | 1 | 0 | 4
4
39020.4396 | 1 | 0 | 5
39020.4398 | 0 | 0 | 5
39020.44 | 1 | 0 | 5
39020.4402 | 1 | 0 | 5
39020.4403 | 1 | 0 | 5
39020.4405 | 1 | 0 | 5
39020.4407 | 1 | 0 | 5
39020.4409 | 0 | 0 | 5
39020.4411 | 1 | 0 | 5
39020.4413 | 0 | 0 | 5
39020.4415 | 1 | 0 | 5
39020.4417 | 1 | 0 | 5
39020.4419 | 1 | 0 | 5
39020.4421 | 1 | 0 | 5
39020.4423 | 1 | 0 | 5
39020.4425 | 1 | 0 | 5
39020.4427 | 1 | 0 | 5
39020.4429 | 0 | 0 | 5
39020.4431 | 1 | 0 | 5
39020.4433 | 1 | 0 | 5
39020.4434 | 1 | 0 | 5
39020.4436 | 1 | 0 | 5
39020.4438 | 0 | 0 | 5
39020.444 | 1 | 0 | 5
39020.4442 | 1 | 0 | 5
39020.4444 | 1 | 0 | 5
39020.4446 | 1 | 0 | 5
39020.4448 | 1 | 0 | 5
39020.445 | 1 | 0 | 5
39020.4452 | 1 | 0 | 5
39020.4454 | 1 | 0 | 5
39020.4456 | 1 | 0 | 5
39020.4458 | 1 | 0 | 5
39020.446 | 1 | 0 | 5
39020.4462 | 1 | 0 | 5
39020.4464 | 1 | 0 | 5
39020.4466 | 1 | 0 | 5
39020.4468 | 1 | 0 | 5
39020.447 | 1 | 0 | 5
39020.4472 | 1 | 0 | 5
39020.4473 | 1 | 0 | 5
39020.4475 | 1 | 0 | 5
39020.4477 | 1 | 0 | 5
39020.4479 | 1 | 0 | 5
39020.4481 | 1 | 0 | 5
39020.4483 | 1 | 0 | 5
39020.4485 | 1 | 0 | 5
39020.4487 | 1 | 0 | 5
39020.4489 | 1 | 0 | 5
39020.4491 | 1 | 0 | 5
39020.4493 | 1 | 0 | 5
39020.4495 | 1 | 0 | 5
39020.4497 | 1 | 0 | 5
39020.4499 | 1 | 0 | 5
39020.4501 | 1 | 0 | 5
39020.4503 | 1 | 0 | 5
39020.4505 | 0 | 0 | 5
39020.4506 | 1 | 0 | 5
39020.4508 | 1 | 0 | 5
39020.451 | 1 | 0 | 5
39020.4512 | 1 | 0 | 5
39020.4514 | 1 | 0 | 5
39020.4516 | 1 | 0 | 5
39020.4518 | 1 | 0 | 5
39020.452 | 1 | 0 | 5
39020.4522 | 1 | 0 | 5
39020.4524 | 1 | 0 | 5
39020.4526 | 1 | 0 | 5
39020.4528 | 1 | 0 | 5
39020.453 | 1 | 0 | 5
39020.4532 | 1 | 0 | 5
39020.4534 | 1 | 0 | 5
39020.4536 | 1 | 0 | 5
39020.4538 | 1 | 0 | 5
39020.454 | 1 | 0 | 5
39020.4541 | 1 | 0 | 5
39020.4543 | 1 | 0 | 5
39020.4545 | 1 | 0 | 5
39020.4547 | 1 | 0 | 5
39020.4549 | 1 | 0 | 5
39020.4551 | 1 | 0 | 5
39020.4553 | 1 | 0 | 5
39020.4555 | 1 | 0 | 5
39020.4557 | 1 | 0 | 5
39020.4559 | 1 | 0 | 5
39020.4561 | 1 | 0 | 5
39020.4563 | 1 | 0 | 5
39020.4565 | 1 | 0 | 5
39020.4567 | 1 | 0 | 5
39020.4569 | 1 | 0 | 5
39020.4571 | 1 | 0 | 5
39020.4573 | 1 | 0 | 5
39020.4575 | 1 | 0 | 5
39020.4577 | 1 | 0 | 5
39020.4578 | 1 | 0 | 5
39020.458 | 1 | 0 | 5
39020.4582 | 1 | 0 | 5
39020.4584 | 1 | 0 | 5
39020.4586 | 1 | 0 | 5
39020.4588 | 1 | 0 | 5
39020.459 | 1 | 0 | 5
39020.4592 | 1 | 0 | 5
39020.4594 | 1 | 0 | 5
39020.4596 | 1 | 0 | 5
39020.4598 | 1 | 0 | 5
39020.46 | 1 | 0 | 5
39020.4602 | 1 | 0 | 5
39020.4604 | 1 | 0 | 5
39020.4606 | 1 | 0 | 5
39020.4608 | 1 | 0 | 5
39020.4609 | 1 | 0 | 5
39020.4611 | 1 | 0 | 5
39020.4613 | 1 | 0 | 5
39020.4615 | 1 | 0 | 5
39020.4617 | 1 | 0 | 5
39020.4619 | 1 | 0 | 5
39020.4621 | 1 | 0 | 5
39020.4623 | 1 | 0 | 5
39020.4625 | 1 | 0 | 5
39020.4627 | 1 | 0 | 5
39020.4629 | 1 | 0 | 5
39020.4631 | 1 | 0 | 5
39020.4633 | 1 | 0 | 5
39020.4635 | 0 | 0 | 5
39020.4637 | 1 | 0 | 5
39020.4639 | 1 | 0 | 5
39020.4641 | 1 | 0 | 5
39020.4643 | 1 | 0 | 5
39020.4645 | 1 | 0 | 5
39020.4646 | 1 | 0 | 5
39020.4648 | 1 | 0 | 5
39020.465 | 1 | 0 | 5
39020.4652 | 1 | 0 | 5
39020.4654 | 1 | 0 | 5
39020.4656 | 1 | 0 | 5
39020.4658 | 1 | 0 | 5
5
39020.4396 | 1 | 0 | 6
39020.4398 | 1 | 0 | 6
39020.44 | 1 | 0 | 6
39020.4402 | 1 | 0 | 6
39020.4404 | 0 | 0 | 6
39020.4406 | 1 | 0 | 6
39020.4408 | 0 | 0 | 6
39020.4409 | 1 | 0 | 6
39020.4411 | 1 | 0 | 6
39020.4413 | 0 | 0 | 6
39020.4415 | 1 | 0 | 6
39020.4417 | 1 | 0 | 6
39020.4419 | 1 | 0 | 6
39020.4421 | 1 | 0 | 6
39020.4423 | 1 | 0 | 6
39020.4425 | 1 | 0 | 6
39020.4427 | 1 | 0 | 6
39020.4429 | 1 | 0 | 6
39020.4431 | 1 | 0 | 6
39020.4433 | 1 | 0 | 6
39020.4435 | 1 | 0 | 6
39020.4437 | 1 | 0 | 6
39020.4439 | 1 | 0 | 6
39020.4441 | 1 | 0 | 6
39020.4442 | 0 | 0 | 6
39020.4444 | 1 | 0 | 6
39020.4446 | 1 | 0 | 6
39020.4448 | 1 | 0 | 6
39020.445 | 1 | 0 | 6
39020.4452 | 1 | 0 | 6
39020.4454 | 1 | 0 | 6
39020.4456 | 1 | 0 | 6
39020.4458 | 1 | 0 | 6
39020.446 | 1 | 0 | 6
39020.4462 | 1 | 0 | 6
39020.4464 | 1 | 0 | 6
39020.4466 | 1 | 0 | 6
39020.4468 | 1 | 0 | 6
39020.447 | 1 | 0 | 6
39020.4472 | 1 | 0 | 6
39020.4474 | 1 | 0 | 6
39020.4476 | 1 | 0 | 6
39020.4477 | 1 | 0 | 6
39020.4479 | 1 | 0 | 6
39020.4481 | 1 | 0 | 6
39020.4483 | 1 | 0 | 6
39020.4485 | 1 | 0 | 6
39020.4487 | 1 | 0 | 6
39020.4489 | 1 | 0 | 6
39020.4491 | 0 | 0 | 6
39020.4493 | 1 | 0 | 6
39020.4495 | 1 | 0 | 6
39020.4497 | 1 | 0 | 6
39020.4499 | 1 | 0 | 6
39020.4501 | 1 | 0 | 6
39020.4503 | 1 | 0 | 6
39020.4505 | 1 | 0 | 6
39020.4507 | 1 | 0 | 6
39020.4509 | 1 | 0 | 6
39020.4511 | 1 | 0 | 6
39020.4512 | 1 | 0 | 6
39020.4514 | 1 | 0 | 6
39020.4516 | 1 | 0 | 6
39020.4518 | 1 | 0 | 6
39020.452 | 1 | 0 | 6
39020.4522 | 1 | 0 | 6
39020.4524 | 1 | 0 | 6
39020.4526 | 1 | 0 | 6
39020.4528 | 1 | 0 | 6
39020.453 | 1 | 0 | 6
39020.4532 | 1 | 0 | 6
39020.4534 | 1 | 0 | 6
39020.4536 | 0 | 0 | 6
39020.4538 | 1 | 0 | 6
39020.454 | 1 | 0 | 6
39020.4542 | 1 | 0 | 6
39020.4544 | 1 | 0 | 6
39020.4545 | 1 | 0 | 6
39020.4547 | 1 | 0 | 6
39020.4549 | 1 | 0 | 6
39020.4551 | 1 | 0 | 6
39020.4553 | 1 | 0 | 6
39020.4555 | 1 | 0 | 6
39020.4557 | 1 | 0 | 6
39020.4559 | 1 | 0 | 6
39020.4561 | 1 | 0 | 6
39020.4563 | 1 | 0 | 6
39020.4565 | 1 | 0 | 6
39020.4567 | 1 | 0 | 6
39020.4569 | 1 | 0 | 6
39020.4571 | 1 | 0 | 6
39020.4573 | 1 | 0 | 6
39020.4575 | 1 | 0 | 6
39020.4577 | 1 | 0 | 6
39020.4579 | 1 | 0 | 6
39020.4581 | 1 | 0 | 6
39020.4583 | 1 | 0 | 6
39020.4584 | 1 | 0 | 6
39020.4586 | 1 | 0 | 6
39020.4588 | 1 | 0 | 6
39020.459 | 1 | 0 | 6
39020.4592 | 1 | 0 | 6
39020.4594 | 1 | 0 | 6
39020.4596 | 1 | 0 | 6
39020.4598 | 1 | 0 | 6
39020.46 | 1 | 0 | 6
39020.4602 | 1 | 0 | 6
39020.4604 | 1 | 0 | 6
39020.4606 | 1 | 0 | 6
39020.4608 | 0 | 0 | 6
39020.461 | 1 | 0 | 6
39020.4612 | 1 | 0 | 6
39020.4614 | 1 | 0 | 6
39020.4616 | 1 | 0 | 6
39020.4617 | 1 | 0 | 6
39020.4619 | 1 | 0 | 6
39020.4621 | 1 | 0 | 6
39020.4623 | 1 | 0 | 6
39020.4625 | 1 | 0 | 6
39020.4627 | 1 | 0 | 6
39020.4629 | 1 | 0 | 6
39020.4631 | 1 | 0 | 6
39020.4633 | 1 | 0 | 6
39020.4635 | 1 | 0 | 6
39020.4637 | 1 | 0 | 6
39020.4639 | 1 | 0 | 6
39020.4641 | 1 | 0 | 6
39020.4643 | 1 | 0 | 6
39020.4645 | 1 | 0 | 6
39020.4647 | 1 | 0 | 6
39020.4649 | 1 | 0 | 6
39020.465 | 1 | 0 | 6
39020.4652 | 1 | 0 | 6
39020.4654 | 1 | 0 | 6
39020.4656 | 1 | 0 | 6
39020.4658 | 1 | 0 | 6
6
39020.4396 | 1 | 0 | 7
39020.4398 | 1 | 0 | 7
39020.44 | 1 | 0 | 7
39020.4402 | 1 | 0 | 7
39020.4404 | 1 | 0 | 7
39020.4406 | 0 | 0 | 7
39020.4408 | 1 | 0 | 7
39020.441 | 0 | 0 | 7
39020.4412 | 0 | 0 | 7
39020.4414 | 1 | 0 | 7
39020.4415 | 0 | 0 | 7
39020.4417 | 1 | 0 | 7
39020.4419 | 1 | 0 | 7
39020.4421 | 1 | 0 | 7
39020.4423 | 1 | 0 | 7
39020.4425 | 1 | 0 | 7
39020.4427 | 1 | 0 | 7
39020.4429 | 1 | 0 | 7
39020.4431 | 1 | 0 | 7
39020.4433 | 1 | 0 | 7
39020.4435 | 1 | 0 | 7
39020.4437 | 1 | 0 | 7
39020.4439 | 1 | 0 | 7
39020.4441 | 1 | 0 | 7
39020.4443 | 1 | 0 | 7
39020.4445 | 0 | 0 | 7
39020.4447 | 1 | 0 | 7
39020.4448 | 1 | 0 | 7
39020.445 | 1 | 0 | 7
39020.4452 | 0 | 0 | 7
39020.4454 | 1 | 0 | 7
39020.4456 | 1 | 0 | 7
39020.4458 | 0 | 0 | 7
39020.446 | 1 | 0 | 7
39020.4462 | 1 | 0 | 7
39020.4464 | 1 | 0 | 7
39020.4466 | 1 | 0 | 7
39020.4468 | 1 | 0 | 7
39020.447 | 0 | 0 | 7
39020.4472 | 1 | 0 | 7
39020.4474 | 1 | 0 | 7
39020.4476 | 1 | 0 | 7
39020.4478 | 1 | 0 | 7
39020.448 | 1 | 0 | 7
39020.4481 | 1 | 0 | 7
39020.4483 | 1 | 0 | 7
39020.4485 | 1 | 0 | 7
39020.4487 | 1 | 0 | 7
39020.4489 | 1 | 0 | 7
39020.4491 | 1 | 0 | 7
39020.4493 | 1 | 0 | 7
39020.4495 | 1 | 0 | 7
39020.4497 | 1 | 0 | 7
39020.4499 | 1 | 0 | 7
39020.4501 | 1 | 0 | 7
39020.4503 | 1 | 0 | 7
39020.4505 | 1 | 0 | 7
39020.4507 | 1 | 0 | 7
39020.4509 | 1 | 0 | 7
39020.4511 | 1 | 0 | 7
39020.4513 | 1 | 0 | 7
39020.4517 | 1 | 0 | 7
39020.4519 | 1 | 0 | 7
39020.452 | 1 | 0 | 7
39020.4522 | 1 | 0 | 7
39020.4524 | 1 | 0 | 7
39020.4526 | 1 | 0 | 7
39020.4528 | 1 | 0 | 7
39020.453 | 1 | 0 | 7
39020.4532 | 1 | 0 | 7
39020.4534 | 1 | 0 | 7
39020.4536 | 1 | 0 | 7
39020.4538 | 1 | 0 | 7
39020.454 | 1 | 0 | 7
39020.4542 | 1 | 0 | 7
39020.4544 | 0 | 0 | 7
39020.4546 | 1 | 0 | 7
39020.4548 | 1 | 0 | 7
39020.455 | 1 | 0 | 7
39020.4552 | 1 | 0 | 7
39020.4553 | 1 | 0 | 7
39020.4555 | 1 | 0 | 7
39020.4557 | 1 | 0 | 7
39020.4559 | 1 | 0 | 7
39020.4561 | 1 | 0 | 7
39020.4565 | 1 | 0 | 7
39020.4567 | 1 | 0 | 7
39020.4569 | 1 | 0 | 7
39020.4571 | 1 | 0 | 7
39020.4573 | 1 | 0 | 7
39020.4575 | 1 | 0 | 7
39020.4577 | 1 | 0 | 7
39020.4579 | 0 | 0 | 7
39020.4581 | 1 | 0 | 7
39020.4583 | 0 | 0 | 7
39020.4585 | 1 | 0 | 7
39020.4587 | 1 | 0 | 7
39020.4588 | 1 | 0 | 7
39020.459 | 1 | 0 | 7
39020.4592 | 1 | 0 | 7
39020.4594 | 1 | 0 | 7
39020.4596 | 1 | 0 | 7
39020.4598 | 1 | 0 | 7
39020.46 | 1 | 0 | 7
39020.4602 | 1 | 0 | 7
39020.4604 | 1 | 0 | 7
39020.4606 | 1 | 0 | 7
39020.4608 | 1 | 0 | 7
39020.461 | 1 | 0 | 7
39020.4612 | 1 | 0 | 7
39020.4614 | 1 | 0 | 7
39020.4616 | 1 | 0 | 7
39020.4618 | 1 | 0 | 7
39020.462 | 1 | 0 | 7
39020.4622 | 1 | 0 | 7
39020.4623 | 1 | 0 | 7
39020.4625 | 1 | 0 | 7
39020.4627 | 1 | 0 | 7
39020.4629 | 1 | 0 | 7
39020.4631 | 1 | 0 | 7
39020.4633 | 1 | 0 | 7
39020.4635 | 1 | 0 | 7
39020.4637 | 1 | 0 | 7
39020.4639 | 1 | 0 | 7
39020.4641 | 1 | 0 | 7
39020.4643 | 1 | 0 | 7
39020.4645 | 1 | 0 | 7
39020.4647 | 1 | 0 | 7
39020.4649 | 1 | 0 | 7
39020.4651 | 1 | 0 | 7
39020.4653 | 1 | 0 | 7
39020.4655 | 1 | 0 | 7
39020.4656 | 1 | 0 | 7
39020.4658 | 1 | 0 | 7
7
39020.4396 | 1 | 0 | 8
39020.4398 | 1 | 0 | 8
39020.44 | 1 | 0 | 8
39020.4402 | 1 | 0 | 8
39020.4404 | 1 | 0 | 8
39020.4406 | 1 | 0 | 8
39020.4408 | 1 | 0 | 8
39020.441 | 0 | 0 | 8
39020.4412 | 1 | 0 | 8
39020.4414 | 1 | 0 | 8
39020.4416 | 1 | 0 | 8
39020.4418 | 1 | 0 | 8
39020.4419 | 1 | 0 | 8
39020.4421 | 1 | 0 | 8
39020.4423 | 1 | 0 | 8
39020.4425 | 1 | 0 | 8
39020.4427 | 0 | 0 | 8
39020.4429 | 1 | 0 | 8
39020.4431 | 1 | 0 | 8
39020.4433 | 1 | 0 | 8
39020.4435 | 1 | 0 | 8
39020.4437 | 0 | 0 | 8
39020.4439 | 1 | 0 | 8
39020.4441 | 1 | 0 | 8
39020.4443 | 1 | 0 | 8
39020.4445 | 1 | 0 | 8
39020.4447 | 1 | 0 | 8
39020.4449 | 1 | 0 | 8
39020.4451 | 0 | 0 | 8
39020.4453 | 1 | 0 | 8
39020.4455 | 1 | 0 | 8
39020.4456 | 1 | 0 | 8
39020.4458 | 1 | 0 | 8
39020.446 | 1 | 0 | 8
39020.4462 | 0 | 0 | 8
39020.4464 | 1 | 0 | 8
39020.4466 | 1 | 0 | 8
39020.4468 | 1 | 0 | 8
39020.447 | 1 | 0 | 8
39020.4472 | 0 | 0 | 8
39020.4474 | 1 | 0 | 8
39020.4476 | 1 | 0 | 8
39020.4478 | 1 | 0 | 8
39020.448 | 1 | 0 | 8
39020.4482 | 0 | 0 | 8
39020.4484 | 1 | 0 | 8
39020.4486 | 1 | 0 | 8
39020.4488 | 0 | 0 | 8
39020.4489 | 1 | 0 | 8
39020.4491 | 1 | 0 | 8
39020.4493 | 1 | 0 | 8
39020.4495 | 1 | 0 | 8
39020.4497 | 1 | 0 | 8
39020.4499 | 1 | 0 | 8
39020.4501 | 1 | 0 | 8
39020.4503 | 1 | 0 | 8
39020.4505 | 1 | 0 | 8
39020.4507 | 1 | 0 | 8
39020.4509 | 1 | 0 | 8
39020.4511 | 1 | 0 | 8
39020.4513 | 1 | 0 | 8
39020.4515 | 1 | 0 | 8
39020.4517 | 1 | 0 | 8
39020.4519 | 1 | 0 | 8
39020.4521 | 1 | 0 | 8
39020.4523 | 1 | 0 | 8
39020.4524 | 1 | 0 | 8
39020.4526 | 1 | 0 | 8
39020.4528 | 1 | 0 | 8
39020.453 | 1 | 0 | 8
39020.4532 | 1 | 0 | 8
39020.4534 | 1 | 0 | 8
39020.4536 | 1 | 0 | 8
39020.4538 | 1 | 0 | 8
39020.454 | 1 | 0 | 8
39020.4542 | 1 | 0 | 8
39020.4544 | 1 | 0 | 8
39020.4546 | 1 | 0 | 8
39020.4548 | 1 | 0 | 8
39020.455 | 1 | 0 | 8
39020.4552 | 0 | 0 | 8
39020.4554 | 1 | 0 | 8
39020.4556 | 1 | 0 | 8
39020.4558 | 1 | 0 | 8
39020.4559 | 1 | 0 | 8
39020.4561 | 1 | 0 | 8
39020.4563 | 1 | 0 | 8
39020.4565 | 1 | 0 | 8
39020.4567 | 1 | 0 | 8
39020.4569 | 1 | 0 | 8
39020.4571 | 1 | 0 | 8
39020.4573 | 1 | 0 | 8
39020.4575 | 1 | 0 | 8
39020.4577 | 1 | 0 | 8
39020.4579 | 1 | 0 | 8
39020.4581 | 1 | 0 | 8
39020.4583 | 1 | 0 | 8
39020.4585 | 1 | 0 | 8
39020.4587 | 1 | 0 | 8
39020.4589 | 1 | 0 | 8
39020.4591 | 1 | 0 | 8
39020.4592 | 1 | 0 | 8
39020.4594 | 1 | 0 | 8
39020.4596 | 1 | 0 | 8
39020.4598 | 1 | 0 | 8
39020.46 | 1 | 0 | 8
39020.4602 | 1 | 0 | 8
39020.4604 | 1 | 0 | 8
39020.4606 | 1 | 0 | 8
39020.4608 | 1 | 0 | 8
39020.461 | 1 | 0 | 8
39020.4612 | 1 | 0 | 8
39020.4614 | 2 | 0 | 8
39020.4616 | 1 | 0 | 8
39020.4618 | 1 | 0 | 8
39020.462 | 1 | 0 | 8
39020.4622 | 1 | 0 | 8
39020.4624 | 1 | 0 | 8
39020.4626 | 1 | 0 | 8
39020.4628 | 1 | 0 | 8
39020.4629 | 1 | 0 | 8
39020.4631 | 1 | 0 | 8
39020.4633 | 1 | 0 | 8
39020.4635 | 1 | 0 | 8
39020.4637 | 1 | 0 | 8
39020.4639 | 1 | 0 | 8
39020.4641 | 1 | 0 | 8
39020.4643 | 1 | 0 | 8
39020.4645 | 1 | 0 | 8
39020.4647 | 1 | 0 | 8
39020.4649 | 1 | 0 | 8
39020.4651 | 1 | 0 | 8
39020.4653 | 1 | 0 | 8
39020.4655 | 1 | 0 | 8
39020.4657 | 0 | 0 | 8
39020.4659 | 1 | 0 | 8
8
39020.4396 | 1 | 0 | 9
39020.4398 | 1 | 0 | 9
39020.44 | 0 | 0 | 9
39020.4402 | 1 | 0 | 9
39020.4404 | 1 | 0 | 9
39020.4406 | 1 | 0 | 9
39020.4408 | 1 | 0 | 9
39020.441 | 1 | 0 | 9
39020.4412 | 1 | 0 | 9
39020.4414 | 1 | 0 | 9
39020.4416 | 1 | 0 | 9
39020.4418 | 1 | 0 | 9
39020.442 | 1 | 0 | 9
39020.4422 | 1 | 0 | 9
39020.4423 | 1 | 0 | 9
39020.4425 | 1 | 0 | 9
39020.4427 | 1 | 0 | 9
39020.4429 | 1 | 0 | 9
39020.4431 | 1 | 0 | 9
39020.4433 | 1 | 0 | 9
39020.4435 | 1 | 0 | 9
39020.4437 | 1 | 0 | 9
39020.4439 | 1 | 0 | 9
39020.4441 | 1 | 0 | 9
39020.4443 | 1 | 0 | 9
39020.4445 | 1 | 0 | 9
39020.4447 | 1 | 0 | 9
39020.4449 | 1 | 0 | 9
39020.4451 | 1 | 0 | 9
39020.4453 | 1 | 0 | 9
39020.4455 | 1 | 0 | 9
39020.4457 | 1 | 0 | 9
39020.4459 | 1 | 0 | 9
39020.446 | 1 | 0 | 9
39020.4462 | 1 | 0 | 9
39020.4464 | 1 | 0 | 9
39020.4466 | 1 | 0 | 9
39020.4468 | 1 | 0 | 9
39020.447 | 1 | 0 | 9
39020.4472 | 1 | 0 | 9
39020.4474 | 1 | 0 | 9
39020.4476 | 1 | 0 | 9
39020.4478 | 1 | 0 | 9
39020.448 | 1 | 0 | 9
39020.4482 | 0 | 0 | 9
39020.4484 | 0 | 0 | 9
39020.4486 | 1 | 0 | 9
39020.4488 | 0 | 0 | 9
39020.449 | 1 | 0 | 9
39020.4492 | 1 | 0 | 9
39020.4494 | 1 | 0 | 9
39020.4495 | 1 | 0 | 9
39020.4497 | 1 | 0 | 9
39020.4499 | 1 | 0 | 9
39020.4501 | 1 | 0 | 9
39020.4503 | 1 | 0 | 9
39020.4505 | 1 | 0 | 9
39020.4507 | 1 | 0 | 9
39020.4509 | 1 | 0 | 9
39020.4511 | 1 | 0 | 9
39020.4513 | 1 | 0 | 9
39020.4515 | 1 | 0 | 9
39020.4517 | 1 | 0 | 9
39020.4519 | 1 | 0 | 9
39020.4521 | 1 | 0 | 9
39020.4523 | 1 | 0 | 9
39020.4525 | 1 | 0 | 9
39020.4527 | 1 | 0 | 9
39020.4528 | 1 | 0 | 9
39020.453 | 1 | 0 | 9
39020.4532 | 1 | 0 | 9
39020.4534 | 1 | 0 | 9
39020.4536 | 1 | 0 | 9
39020.4538 | 1 | 0 | 9
39020.454 | 1 | 0 | 9
39020.4542 | 1 | 0 | 9
39020.4544 | 1 | 0 | 9
39020.4546 | 1 | 0 | 9
39020.4548 | 1 | 0 | 9
39020.455 | 1 | 0 | 9
39020.4552 | 1 | 0 | 9
39020.4554 | 1 | 0 | 9
39020.4556 | 1 | 0 | 9
39020.4558 | 1 | 0 | 9
39020.456 | 1 | 0 | 9
39020.4562 | 1 | 0 | 9
39020.4564 | 1 | 0 | 9
39020.4566 | 1 | 0 | 9
39020.4567 | 1 | 0 | 9
39020.4569 | 1 | 0 | 9
39020.4571 | 1 | 0 | 9
39020.4573 | 1 | 0 | 9
39020.4575 | 1 | 0 | 9
39020.4577 | 1 | 0 | 9
39020.4579 | 1 | 0 | 9
39020.4581 | 1 | 0 | 9
39020.4583 | 1 | 0 | 9
39020.4585 | 1 | 0 | 9
39020.4587 | 1 | 0 | 9
39020.4589 | 1 | 0 | 9
39020.4591 | 1 | 0 | 9
39020.4593 | 1 | 0 | 9
39020.4595 | 1 | 0 | 9
39020.4597 | 1 | 0 | 9
39020.4598 | 1 | 0 | 9
39020.46 | 1 | 0 | 9
39020.4602 | 1 | 0 | 9
39020.4604 | 1 | 0 | 9
39020.4606 | 1 | 0 | 9
39020.4608 | 1 | 0 | 9
39020.461 | 0 | 0 | 9
39020.4612 | 1 | 0 | 9
39020.4614 | 0 | 0 | 9
39020.4616 | 1 | 0 | 9
39020.4618 | 1 | 0 | 9
39020.462 | 1 | 0 | 9
39020.4622 | 1 | 0 | 9
39020.4624 | 1 | 0 | 9
39020.4626 | 1 | 0 | 9
39020.4628 | 1 | 0 | 9
39020.463 | 1 | 0 | 9
39020.4632 | 1 | 0 | 9
39020.4633 | 1 | 0 | 9
39020.4635 | 1 | 0 | 9
39020.4637 | 1 | 0 | 9
39020.4639 | 1 | 0 | 9
39020.4641 | 1 | 0 | 9
39020.4643 | 1 | 0 | 9
39020.4645 | 1 | 0 | 9
39020.4647 | 1 | 0 | 9
39020.4649 | 1 | 0 | 9
39020.4651 | 1 | 0 | 9
39020.4653 | 1 | 0 | 9
39020.4655 | 1 | 0 | 9
39020.4657 | 0 | 0 | 9
39020.4659 | 1 | 0 | 9
9
39020.4397 | 1 | 0 | 10
39020.4398 | 1 | 0 | 10
39020.44 | 1 | 0 | 10
39020.4402 | 1 | 0 | 10
39020.4404 | 1 | 0 | 10
39020.4406 | 1 | 0 | 10
39020.4408 | 1 | 0 | 10
39020.441 | 0 | 0 | 10
39020.4412 | 1 | 0 | 10
39020.4414 | 1 | 0 | 10
39020.4416 | 1 | 0 | 10
39020.4418 | 1 | 0 | 10
39020.442 | 1 | 0 | 10
39020.4422 | 1 | 0 | 10
39020.4424 | 1 | 0 | 10
39020.4426 | 1 | 0 | 10
39020.4428 | 1 | 0 | 10
39020.443 | 1 | 0 | 10
39020.4431 | 1 | 0 | 10
39020.4433 | 1 | 0 | 10
39020.4435 | 1 | 0 | 10
39020.4437 | 1 | 0 | 10
39020.4439 | 1 | 0 | 10
39020.4441 | 1 | 0 | 10
39020.4443 | 1 | 0 | 10
39020.4445 | 1 | 0 | 10
39020.4447 | 1 | 0 | 10
39020.4449 | 1 | 0 | 10
39020.4451 | 1 | 0 | 10
39020.4453 | 1 | 0 | 10
39020.4455 | 0 | 0 | 10
39020.4457 | 1 | 0 | 10
39020.4459 | 1 | 0 | 10
39020.4461 | 1 | 0 | 10
39020.4463 | 1 | 0 | 10
39020.4464 | 1 | 0 | 10
39020.4466 | 1 | 0 | 10
39020.4468 | 1 | 0 | 10
39020.447 | 1 | 0 | 10
39020.4472 | 1 | 0 | 10
39020.4474 | 0 | 0 | 10
39020.4476 | 1 | 0 | 10
39020.4478 | 1 | 0 | 10
39020.448 | 1 | 0 | 10
39020.4482 | 1 | 0 | 10
39020.4484 | 1 | 0 | 10
39020.4486 | 0 | 0 | 10
39020.4488 | 1 | 0 | 10
39020.449 | 1 | 0 | 10
39020.4492 | 1 | 0 | 10
39020.4494 | 1 | 0 | 10
39020.4496 | 1 | 0 | 10
39020.4498 | 1 | 0 | 10
39020.45 | 1 | 0 | 10
39020.4502 | 1 | 0 | 10
39020.4503 | 1 | 0 | 10
39020.4505 | 1 | 0 | 10
39020.4507 | 1 | 0 | 10
39020.4509 | 1 | 0 | 10
39020.4511 | 1 | 0 | 10
39020.4513 | 1 | 0 | 10
39020.4515 | 1 | 0 | 10
39020.4517 | 1 | 0 | 10
39020.4519 | 1 | 0 | 10
39020.4521 | 1 | 0 | 10
39020.4523 | 1 | 0 | 10
39020.4525 | 1 | 0 | 10
39020.4527 | 1 | 0 | 10
39020.4529 | 1 | 0 | 10
39020.4531 | 1 | 0 | 10
39020.4533 | 0 | 0 | 10
39020.4534 | 1 | 0 | 10
39020.4536 | 1 | 0 | 10
39020.4538 | 1 | 0 | 10
39020.454 | 1 | 0 | 10
39020.4542 | 1 | 0 | 10
39020.4544 | 1 | 0 | 10
39020.4546 | 1 | 0 | 10
39020.4548 | 1 | 0 | 10
39020.455 | 1 | 0 | 10
39020.4552 | 1 | 0 | 10
39020.4554 | 1 | 0 | 10
39020.4556 | 1 | 0 | 10
39020.4558 | 1 | 0 | 10
39020.456 | 1 | 0 | 10
39020.4562 | 1 | 0 | 10
39020.4564 | 1 | 0 | 10
39020.4566 | 1 | 0 | 10
39020.4568 | 1 | 0 | 10
39020.4569 | 0 | 0 | 10
39020.4571 | 1 | 0 | 10
39020.4573 | 1 | 0 | 10
39020.4575 | 1 | 0 | 10
39020.4577 | 1 | 0 | 10
39020.4579 | 1 | 0 | 10
39020.4581 | 1 | 0 | 10
39020.4583 | 1 | 0 | 10
39020.4585 | 1 | 0 | 10
39020.4587 | 1 | 0 | 10
39020.4589 | 1 | 0 | 10
39020.4591 | 1 | 0 | 10
39020.4593 | 1 | 0 | 10
39020.4595 | 1 | 0 | 10
39020.4597 | 1 | 0 | 10
39020.4599 | 0 | 0 | 10
39020.4601 | 1 | 0 | 10
39020.4603 | 1 | 0 | 10
39020.4605 | 1 | 0 | 10
39020.4606 | 1 | 0 | 10
39020.4608 | 1 | 0 | 10
39020.461 | 1 | 0 | 10
39020.4612 | 1 | 0 | 10
39020.4614 | 1 | 0 | 10
39020.4616 | 1 | 0 | 10
39020.4618 | 1 | 0 | 10
39020.462 | 1 | 0 | 10
39020.4622 | 1 | 0 | 10
39020.4624 | 1 | 0 | 10
39020.4626 | 1 | 0 | 10
39020.4628 | 1 | 0 | 10
39020.463 | 1 | 0 | 10
39020.4632 | 1 | 0 | 10
39020.4634 | 1 | 0 | 10
39020.4636 | 0 | 0 | 10
39020.4638 | 1 | 0 | 10
39020.4639 | 1 | 0 | 10
39020.4641 | 1 | 0 | 10
39020.4643 | 1 | 0 | 10
39020.4645 | 1 | 0 | 10
39020.4647 | 1 | 0 | 10
39020.4649 | 1 | 0 | 10
39020.4651 | 1 | 0 | 10
39020.4653 | 0 | 0 | 10
39020.4655 | 1 | 0 | 10
39020.4657 | 1 | 0 | 10
39020.4659 | 1 | 0 | 10
10
39020.4397 | 1 | 0 | 11
39020.4399 | 0 | 0 | 11
39020.4401 | 1 | 0 | 11
39020.4402 | 1 | 0 | 11
39020.4404 | 1 | 0 | 11
39020.4406 | 1 | 0 | 11
39020.4408 | 1 | 0 | 11
39020.441 | 0 | 0 | 11
39020.4412 | 1 | 0 | 11
39020.4414 | 1 | 0 | 11
39020.4416 | 1 | 0 | 11
39020.4418 | 1 | 0 | 11
39020.442 | 1 | 0 | 11
39020.4422 | 1 | 0 | 11
39020.4424 | 1 | 0 | 11
39020.4426 | 1 | 0 | 11
39020.4428 | 1 | 0 | 11
39020.443 | 1 | 0 | 11
39020.4432 | 1 | 0 | 11
39020.4434 | 1 | 0 | 11
39020.4436 | 1 | 0 | 11
39020.4437 | 1 | 0 | 11
39020.4439 | 1 | 0 | 11
39020.4441 | 1 | 0 | 11
39020.4443 | 0 | 0 | 11
39020.4445 | 1 | 0 | 11
39020.4447 | 1 | 0 | 11
39020.4449 | 1 | 0 | 11
39020.4451 | 0 | 0 | 11
39020.4453 | 1 | 0 | 11
39020.4455 | 1 | 0 | 11
39020.4457 | 1 | 0 | 11
39020.4459 | 1 | 0 | 11
39020.4461 | 1 | 0 | 11
39020.4463 | 1 | 0 | 11
39020.4465 | 1 | 0 | 11
39020.4467 | 1 | 0 | 11
39020.4469 | 1 | 0 | 11
39020.447 | 1 | 0 | 11
39020.4472 | 1 | 0 | 11
39020.4474 | 1 | 0 | 11
39020.4476 | 1 | 0 | 11
39020.4478 | 1 | 0 | 11
39020.448 | 1 | 0 | 11
39020.4482 | 1 | 0 | 11
39020.4484 | 0 | 0 | 11
39020.4486 | 1 | 0 | 11
39020.4488 | 1 | 0 | 11
39020.449 | 1 | 0 | 11
39020.4492 | 1 | 0 | 11
39020.4494 | 1 | 0 | 11
39020.4496 | 1 | 0 | 11
39020.4498 | 1 | 0 | 11
39020.45 | 1 | 0 | 11
39020.4502 | 1 | 0 | 11
39020.4504 | 1 | 0 | 11
39020.4506 | 1 | 0 | 11
39020.4507 | 1 | 0 | 11
39020.4509 | 1 | 0 | 11
39020.4511 | 1 | 0 | 11
39020.4513 | 1 | 0 | 11
39020.4515 | 1 | 0 | 11
39020.4517 | 1 | 0 | 11
39020.4519 | 1 | 0 | 11
39020.4521 | 1 | 0 | 11
39020.4523 | 1 | 0 | 11
39020.4525 | 1 | 0 | 11
39020.4527 | 1 | 0 | 11
39020.4529 | 1 | 0 | 11
39020.4531 | 1 | 0 | 11
39020.4533 | 1 | 0 | 11
39020.4535 | 1 | 0 | 11
39020.4537 | 1 | 0 | 11
39020.4539 | 1 | 0 | 11
39020.4541 | 1 | 0 | 11
39020.4542 | 1 | 0 | 11
39020.4544 | 1 | 0 | 11
39020.4546 | 1 | 0 | 11
39020.4548 | 1 | 0 | 11
39020.455 | 0 | 0 | 11
39020.4552 | 1 | 0 | 11
39020.4554 | 1 | 0 | 11
39020.4556 | 1 | 0 | 11
39020.4558 | 1 | 0 | 11
39020.456 | 1 | 0 | 11
39020.4562 | 1 | 0 | 11
39020.4564 | 1 | 0 | 11
39020.4566 | 1 | 0 | 11
39020.4568 | 1 | 0 | 11
39020.457 | 1 | 0 | 11
39020.4572 | 1 | 0 | 11
39020.4573 | 1 | 0 | 11
39020.4575 | 1 | 0 | 11
39020.4577 | 1 | 0 | 11
39020.4579 | 1 | 0 | 11
39020.4581 | 1 | 0 | 11
39020.4583 | 1 | 0 | 11
39020.4585 | 1 | 0 | 11
39020.4587 | 1 | 0 | 11
39020.4589 | 1 | 0 | 11
39020.4591 | 1 | 0 | 11
39020.4593 | 1 | 0 | 11
39020.4595 | 1 | 0 | 11
39020.4597 | 1 | 0 | 11
39020.4599 | 1 | 0 | 11
39020.4601 | 0 | 0 | 11
39020.4603 | 1 | 0 | 11
39020.4605 | 1 | 0 | 11
39020.4607 | 1 | 0 | 11
39020.4609 | 1 | 0 | 11
39020.4611 | 1 | 0 | 11
39020.4613 | 1 | 0 | 11
39020.4614 | 1 | 0 | 11
39020.4616 | 1 | 0 | 11
39020.4618 | 1 | 0 | 11
39020.462 | 1 | 0 | 11
39020.4622 | 0 | 0 | 11
39020.4624 | 1 | 0 | 11
39020.4626 | 1 | 0 | 11
39020.4628 | 1 | 0 | 11
39020.463 | 0 | 0 | 11
39020.4632 | 1 | 0 | 11
39020.4634 | 1 | 0 | 11
39020.4636 | 1 | 0 | 11
39020.4638 | 1 | 0 | 11
39020.464 | 1 | 0 | 11
39020.4642 | 1 | 0 | 11
39020.4644 | 1 | 0 | 11
39020.4645 | 1 | 0 | 11
39020.4647 | 1 | 0 | 11
39020.4649 | 1 | 0 | 11
39020.4651 | 1 | 0 | 11
39020.4653 | 1 | 0 | 11
39020.4655 | 1 | 0 | 11
39020.4657 | 1 | 0 | 11
39020.4659 | 1 | 0 | 11
11
39020.4397 | 1 | 0 | 12
39020.4399 | 0 | 0 | 12
39020.4401 | 1 | 0 | 12
39020.4403 | 1 | 0 | 12
39020.4405 | 1 | 0 | 12
39020.4406 | 1 | 0 | 12
39020.4408 | 1 | 0 | 12
39020.4412 | 0 | 0 | 12
39020.4414 | 0 | 0 | 12
39020.4416 | 1 | 0 | 12
39020.4418 | 1 | 0 | 12
39020.442 | 1 | 0 | 12
39020.4422 | 1 | 0 | 12
39020.4424 | 0 | 0 | 12
39020.4426 | 1 | 0 | 12
39020.4428 | 1 | 0 | 12
39020.443 | 1 | 0 | 12
39020.4432 | 2 | 0 | 12
39020.4434 | 1 | 0 | 12
39020.4436 | 1 | 0 | 12
39020.4438 | 1 | 0 | 12
39020.444 | 0 | 0 | 12
39020.4442 | 1 | 0 | 12
39020.4444 | 1 | 0 | 12
39020.4445 | 0 | 0 | 12
39020.4447 | 1 | 0 | 12
39020.4449 | 1 | 0 | 12
39020.4451 | 1 | 0 | 12
39020.4453 | 1 | 0 | 12
39020.4455 | 1 | 0 | 12
39020.4457 | 0 | 0 | 12
39020.4459 | 1 | 0 | 12
39020.4461 | 1 | 0 | 12
39020.4463 | 1 | 0 | 12
39020.4465 | 1 | 0 | 12
39020.4467 | 1 | 0 | 12
39020.4469 | 1 | 0 | 12
39020.4471 | 1 | 0 | 12
39020.4473 | 1 | 0 | 12
39020.4475 | 0 | 0 | 12
39020.4477 | 1 | 0 | 12
39020.4478 | 0 | 0 | 12
39020.448 | 1 | 0 | 12
39020.4482 | 1 | 0 | 12
39020.4484 | 1 | 0 | 12
39020.4486 | 1 | 0 | 12
39020.4488 | 1 | 0 | 12
39020.449 | 1 | 0 | 12
39020.4492 | 1 | 0 | 12
39020.4494 | 1 | 0 | 12
39020.4496 | 1 | 0 | 12
39020.4498 | 1 | 0 | 12
39020.45 | 1 | 0 | 12
39020.4502 | 1 | 0 | 12
39020.4504 | 1 | 0 | 12
39020.4506 | 1 | 0 | 12
39020.4508 | 1 | 0 | 12
39020.451 | 0 | 0 | 12
39020.4511 | 1 | 0 | 12
39020.4513 | 1 | 0 | 12
39020.4515 | 1 | 0 | 12
39020.4517 | 1 | 0 | 12
39020.4519 | 1 | 0 | 12
39020.4521 | 1 | 0 | 12
39020.4523 | 1 | 0 | 12
39020.4525 | 1 | 0 | 12
39020.4527 | 0 | 0 | 12
39020.4529 | 1 | 0 | 12
39020.4531 | 1 | 0 | 12
39020.4533 | 1 | 0 | 12
39020.4535 | 1 | 0 | 12
39020.4537 | 1 | 0 | 12
39020.4539 | 1 | 0 | 12
39020.4541 | 1 | 0 | 12
39020.4543 | 1 | 0 | 12
39020.4545 | 0 | 0 | 12
39020.4547 | 1 | 0 | 12
39020.4548 | 1 | 0 | 12
39020.455 | 1 | 0 | 12
39020.4552 | 1 | 0 | 12
39020.4554 | 1 | 0 | 12
39020.4556 | 1 | 0 | 12
39020.4558 | 1 | 0 | 12
39020.456 | 1 | 0 | 12
39020.4562 | 1 | 0 | 12
39020.4564 | 1 | 0 | 12
39020.4566 | 1 | 0 | 12
39020.4568 | 0 | 0 | 12
39020.457 | 1 | 0 | 12
39020.4572 | 1 | 0 | 12
39020.4574 | 1 | 0 | 12
39020.4576 | 1 | 0 | 12
39020.4578 | 0 | 0 | 12
39020.458 | 1 | 0 | 12
39020.4581 | 1 | 0 | 12
39020.4583 | 1 | 0 | 12
39020.4585 | 1 | 0 | 12
39020.4587 | 1 | 0 | 12
39020.4589 | 1 | 0 | 12
39020.4591 | 1 | 0 | 12
39020.4593 | 1 | 0 | 12
39020.4595 | 1 | 0 | 12
39020.4597 | 1 | 0 | 12
39020.4599 | 1 | 0 | 12
39020.4601 | 1 | 0 | 12
39020.4603 | 1 | 0 | 12
39020.4605 | 1 | 0 | 12
39020.4607 | 1 | 0 | 12
39020.4609 | 1 | 0 | 12
39020.4611 | 1 | 0 | 12
39020.4613 | 1 | 0 | 12
39020.4615 | 1 | 0 | 12
39020.4616 | 1 | 0 | 12
39020.4618 | 1 | 0 | 12
39020.462 | 1 | 0 | 12
39020.4622 | 1 | 0 | 12
39020.4624 | 1 | 0 | 12
39020.4626 | 1 | 0 | 12
39020.4628 | 1 | 0 | 12
39020.463 | 1 | 0 | 12
39020.4632 | 1 | 0 | 12
39020.4634 | 1 | 0 | 12
39020.4636 | 1 | 0 | 12
39020.4638 | 1 | 0 | 12
39020.464 | 1 | 0 | 12
39020.4642 | 0 | 0 | 12
39020.4644 | 1 | 0 | 12
39020.4646 | 1 | 0 | 12
39020.4648 | 1 | 0 | 12
39020.465 | 1 | 0 | 12
39020.4652 | 1 | 0 | 12
39020.4653 | 1 | 0 | 12
39020.4655 | 1 | 0 | 12
39020.4657 | 1 | 0 | 12
39020.4659 | 1 | 0 | 12
12

## Test Facts
Last row in IRMS data sheets: | 141
Time when gas burner was ignited: | 276