## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-5
Test Date: | 2006-11-01
Ignition Time Relative to Thermal Data: | 163 | s
Ignition Time Relative to Electrical Data: | 163 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Plot for 7/C cable on SCDU-3 at Location G

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 5-1 |  |  |  | Location A | Location C - 6-cable bundle 5-2 |  |  |  | Location C | Location A-C Air Drop 7/C XLPE cable |  |  | Location E - Single 7/C EPR Cable |  |  | Location E | Location G - Single 7/C EPR Cable |  |  | Location G
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable Temp | TC-2 Above Cable | TC3 Below Cable | TC-1 Cable Temp | TC-2 Above Cable | TC3 Below Cable | Tray Rung | TC-1 Cable Temp | TC-2 Above Cable | TC3 Below Cable | Tray Rung
0 | -163 | -6.1 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.5 | 15.3 | 14.2 | 21.5 | 14.5 | 2.2 | 244.5 | 3.9 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
1 | -162 | -5.5 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.5 | 15.3 | 14.2 | 21.5 | 14.5 | 2.1 | 233.9 | 3.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
2 | -161 | -5.2 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.5 | 15.3 | 14.2 | 21.5 | 14.5 | 1.8 | 206.9 | 3.5 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
3 | -160 | -5.6 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.5 | 15.3 | 14.2 | 21.5 | 14.5 | 1.7 | 219.1 | 3.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.7 | 15.5 | 15.5 | 14.8 | 17
4 | -159 | -6.3 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.5 | 15.3 | 14.2 | 21.5 | 14.5 | 1.9 | 227.8 | 3.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
5 | -158 | -5.9 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.5 | 15.3 | 14.2 | 21.5 | 14.5 | 2 | 229.9 | 3.4 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
6 | -157 | -5.9 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 2 | 230.7 | 3.2 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
7 | -156 | -6.3 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.9 | 235.8 | 3.3 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
8 | -155 | -6.1 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.9 | 238.4 | 4.1 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.7 | 15.5 | 15.5 | 14.8 | 17
9 | -154 | -4.6 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.9 | 223.3 | 4.6 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
10 | -153 | -4.6 | 0 | 0 | 15.3 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.8 | 205.7 | 4.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.7 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
11 | -152 | -4.9 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.9 | 216.3 | 4.6 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
12 | -151 | -5.3 | 0 | 0 | 15.3 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.8 | 255.9 | 5 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
13 | -150 | -5 | 0 | 0 | 15.3 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.8 | 244.3 | 6.1 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
14 | -149 | -4.7 | 0 | 0 | 15.3 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.6 | 231.4 | 7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
15 | -148 | -4.6 | 0 | 0 | 15.3 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.5 | 229.3 | 6.8 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
16 | -147 | -4.9 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.6 | 230.7 | 7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
17 | -146 | -5.8 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.4 | 236.2 | 6.6 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
18 | -145 | -6.4 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.3 | 245.5 | 6.3 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
19 | -144 | -6.6 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.3 | 248.4 | 6.2 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15 | 16.8 | 15.5 | 15.5 | 14.8 | 17
20 | -143 | -6.4 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.2 | 262.1 | 6.4 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
21 | -142 | -6.5 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.3 | 261.7 | 6 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
22 | -141 | -6.7 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.5 | 244.3 | 5.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
23 | -140 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.4 | 228.5 | 5.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
24 | -139 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.3 | 243.2 | 5.7 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
25 | -138 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.3 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.1 | 250.1 | 6 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
26 | -137 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.1 | 250.2 | 5.9 | 14.5 | 14.2 | 14.3 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.7 | 15.5 | 15.5 | 14.8 | 17
27 | -136 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1 | 249.5 | 5.7 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
28 | -135 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.1 | 247.9 | 5.5 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
29 | -134 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.6 | 15.3 | 14.2 | 21.5 | 14.5 | 1.1 | 253.6 | 5.3 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
30 | -133 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.2 | 256.5 | 5 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
31 | -132 | -6.6 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.4 | 258.6 | 4.8 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
32 | -131 | -6 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.4 | 257.9 | 4.5 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
33 | -130 | -5.2 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.4 | 253.6 | 4.1 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
34 | -129 | -5.2 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.6 | 254 | 3.8 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
35 | -128 | -6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.5 | 255.9 | 3.7 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
36 | -127 | -5.4 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.2 | 21.5 | 14.5 | 1.4 | 261.5 | 3.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
37 | -126 | -4.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.5 | 14.5 | 1.6 | 261.6 | 3.5 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
38 | -125 | -4.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.5 | 14.5 | 1.7 | 261.1 | 3.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
39 | -124 | -5.1 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.8 | 261.5 | 3.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
40 | -123 | -5.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.8 | 261.9 | 2.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
41 | -122 | -6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.5 | 14.5 | 1.7 | 261.9 | 2.7 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
42 | -121 | -6.1 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.5 | 14.5 | 1.5 | 264.7 | 2.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
43 | -120 | -6.5 | 0 | 0 | 15 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.5 | 14.5 | 1.4 | 268.3 | 2.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
44 | -119 | -6.4 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.5 | 14.5 | 1.5 | 268.4 | 2.4 | 14.5 | 14.2 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
45 | -118 | -5.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.4 | 268.7 | 2.3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
46 | -117 | -6.2 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 269.7 | 2.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
47 | -116 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 269.1 | 2.3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
48 | -115 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.6 | 267.5 | 2.3 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
49 | -114 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.4 | 258.9 | 2.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
50 | -113 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.1 | 21.5 | 14.5 | 1.6 | 248.5 | 2.5 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
51 | -112 | -6.4 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 242.7 | 2.5 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
52 | -111 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.3 | 220.6 | 2.5 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
53 | -110 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.4 | 202.1 | 2.6 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
54 | -109 | -5.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.5 | 14.5 | 1.4 | 207.5 | 2.8 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
55 | -108 | -5.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.1 | 21.5 | 14.5 | 1.1 | 210.4 | 3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
56 | -107 | -5.6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.1 | 21.5 | 14.5 | 1.3 | 212.3 | 3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
57 | -106 | -5.9 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.1 | 21.5 | 14.5 | 1.2 | 212.3 | 3.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
58 | -105 | -6.3 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.3 | 212.1 | 3.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
59 | -104 | -6.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.5 | 14.5 | 1.5 | 223.5 | 3.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
60 | -103 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.6 | 14.5 | 1.3 | 234.7 | 3.7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
61 | -102 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.3 | 216.6 | 4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
62 | -101 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.4 | 196.5 | 3.7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
63 | -100 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.5 | 14.5 | 1.5 | 203.9 | 3.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
64 | -99 | -6.6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.6 | 15.4 | 14.1 | 21.5 | 14.5 | 1.5 | 222.3 | 2.7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
65 | -98 | -6.6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.6 | 14.5 | 1.4 | 241.9 | 2.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
66 | -97 | -6.3 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.6 | 14.5 | 1.4 | 253.5 | 2.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
67 | -96 | -6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.2 | 21.6 | 14.5 | 1.4 | 253.8 | 2.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
68 | -95 | -5.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.2 | 21.6 | 14.5 | 1.5 | 250.9 | 2.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
69 | -94 | -5.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.2 | 21.6 | 14.5 | 1.7 | 250.2 | 2.3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
70 | -93 | -5.2 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.2 | 21.6 | 14.5 | 1.4 | 247.6 | 2.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
71 | -92 | -4.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.2 | 21.6 | 14.5 | 1.4 | 236.9 | 2.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
72 | -91 | -4.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.5 | 218.1 | 2.3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
73 | -90 | -4.3 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.7 | 203.7 | 2.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
74 | -89 | -4.2 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.5 | 200.2 | 3.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
75 | -88 | -4.3 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.7 | 204.4 | 4.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
76 | -87 | -5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.7 | 221 | 4.7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
77 | -86 | -4.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.6 | 214.8 | 4.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
78 | -85 | -4.2 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.4 | 216.7 | 4.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
79 | -84 | -4.1 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.4 | 228.7 | 3.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
80 | -83 | -4.6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.3 | 221.9 | 3.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
81 | -82 | -5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.3 | 202.2 | 3.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
82 | -81 | -5.4 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.2 | 203.5 | 3.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
83 | -80 | -6.1 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.2 | 209.1 | 4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
84 | -79 | -6.1 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.1 | 229.3 | 3.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
85 | -78 | -6.1 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.2 | 256.2 | 3.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
86 | -77 | -4.7 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.3 | 265.8 | 3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
87 | -76 | -5 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.3 | 251.5 | 2.9 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
88 | -75 | -5.3 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.4 | 240.7 | 3.1 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
89 | -74 | -5.2 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 236.4 | 3.2 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.9 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
90 | -73 | -5.5 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 215.9 | 3.2 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.9 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
91 | -72 | -6.5 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 219.2 | 3.4 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
92 | -71 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 248.3 | 3.9 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.9 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
93 | -70 | -6.5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 244.6 | 4.3 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
94 | -69 | -6.3 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 226.9 | 4.8 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
95 | -68 | -6.1 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14 | 21.6 | 14.5 | 1.7 | 244.9 | 5.1 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
96 | -67 | -5.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 229.5 | 5 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
97 | -66 | -5.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 237.3 | 4.4 | 14.5 | 14 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
98 | -65 | -5.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 252.7 | 3.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
99 | -64 | -6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14 | 21.6 | 14.5 | 1.4 | 261 | 3.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
100 | -63 | -6.2 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.4 | 277.1 | 3.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
101 | -62 | -5.9 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14 | 21.6 | 14.5 | 1.4 | 284.4 | 3.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
102 | -61 | -5.9 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 252.4 | 3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
103 | -60 | -5.9 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 219.1 | 3.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
104 | -59 | -6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 247.6 | 5.1 | 14.6 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
105 | -58 | -6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 246.5 | 6.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
106 | -57 | -6.3 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.8 | 248.8 | 6.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
107 | -56 | -6.2 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.8 | 248.9 | 7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
108 | -55 | -6 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.9 | 253.1 | 6.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
109 | -54 | -6 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.7 | 254.1 | 6.7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
110 | -53 | -6.4 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.7 | 250.2 | 6.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
111 | -52 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.5 | 241 | 6.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
112 | -51 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.5 | 14.1 | 21.6 | 14.5 | 1.6 | 236.9 | 6.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
113 | -50 | -6.7 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 251.2 | 6.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
114 | -49 | -6.6 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 2 | 233 | 5.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
115 | -48 | -6.2 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 227 | 5.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
116 | -47 | -6 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.9 | 251.9 | 5.4 | 14.6 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
117 | -46 | -6.3 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.8 | 251.5 | 5.4 | 14.6 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
118 | -45 | -6.4 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.7 | 227.6 | 5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
119 | -44 | -5.9 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.4 | 14.1 | 21.6 | 14.5 | 1.6 | 245.2 | 4.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.7 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
120 | -43 | -5.8 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.8 | 250.8 | 5.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
121 | -42 | -1.7 | 0 | 0 | 15.1 | 15.5 | 15.6 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.7 | 233.7 | 5.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
122 | -41 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.6 | 238.9 | 5.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
123 | -40 | -5.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.8 | 257.2 | 5.7 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
124 | -39 | -5 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.5 | 255.2 | 6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
125 | -38 | -4.7 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.4 | 266.2 | 5.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
126 | -37 | -4.6 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.7 | 253.6 | 6.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
127 | -36 | -4.9 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.6 | 245.4 | 5.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 15 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
128 | -35 | -5.3 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.8 | 230.8 | 5.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.4 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.8 | 17
129 | -34 | -6.3 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.7 | 216.3 | 5.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
130 | -33 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.3 | 234 | 5.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
131 | -32 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.3 | 260.5 | 5.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.9 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
132 | -31 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.5 | 253.4 | 4.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.9 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
133 | -30 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.5 | 208.4 | 3.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
134 | -29 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.5 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.7 | 178.1 | 3.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.8 | 17
135 | -28 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.6 | 185.5 | 2.8 | 14.5 | 14.1 | 14.1 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.2 | 16.8 | 15.5 | 15.5 | 14.7 | 17
136 | -27 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.9 | 225.7 | 2.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
137 | -26 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.8 | 259.4 | 2.8 | 14.5 | 14.1 | 14.1 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
138 | -25 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 2 | 241.2 | 2.8 | 14.5 | 14.1 | 14.1 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
139 | -24 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.8 | 208.5 | 2.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
140 | -23 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.6 | 205.2 | 2.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
141 | -22 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.6 | 222.1 | 2.8 | 14.5 | 14.1 | 14.1 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
142 | -21 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.6 | 243.5 | 3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
143 | -20 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.5 | 15.4 | 14.1 | 21.6 | 14.4 | 1.5 | 243.2 | 3.1 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
144 | -19 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.1 | 21.6 | 14.5 | 1.5 | 244.1 | 3.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
145 | -18 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.1 | 21.6 | 14.4 | 1.4 | 242 | 4.6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
146 | -17 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.5 | 1.4 | 240 | 4.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
147 | -16 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.5 | 1.5 | 237.2 | 5.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
148 | -15 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.5 | 1.5 | 267.2 | 5.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 14.9 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
149 | -14 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.5 | 1.5 | 269.5 | 5.2 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
150 | -13 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.5 | 1.6 | 255.3 | 5.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
151 | -12 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.4 | 1.6 | 262.3 | 6.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
152 | -11 | -6.8 | 0 | 0 | 15 | 15.5 | 15.4 | 15.6 | 15.4 | 14.2 | 21.6 | 14.4 | 1.7 | 251.2 | 6.5 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
153 | -10 | -6.8 | 0 | 0 | 15 | 15.5 | 15.3 | 15.6 | 15.4 | 14.2 | 21.6 | 14.4 | 1.7 | 253.8 | 6.9 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
154 | -9 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.3 | 15.6 | 15.5 | 14.2 | 21.6 | 14.4 | 1.7 | 263.6 | 6.8 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
155 | -8 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.3 | 15.6 | 15.5 | 14.2 | 21.6 | 14.4 | 1.7 | 259.8 | 6.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
156 | -7 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.3 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 2.1 | 259.5 | 5.4 | 14.6 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
157 | -6 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 1.9 | 260.4 | 4.7 | 14.6 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
158 | -5 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 1.8 | 257.1 | 4.3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.8 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
159 | -4 | -6.8 | 0 | 0 | 15.1 | 15.5 | 15.4 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 1.8 | 250.8 | 4.3 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.8 | 17
160 | -3 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.7 | 246.7 | 5.4 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
161 | -2 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 1.4 | 250.9 | 6 | 14.5 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
162 | -1 | -6.8 | 0 | 0 | 15.2 | 15.5 | 15.4 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 1.3 | 251.9 | 5.8 | 14.6 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
163 | 0 | 123.4 | 49.36 | 57.699 | 15.2 | 15.5 | 15.5 | 15.5 | 15.5 | 14.1 | 21.6 | 14.4 | 1.2 | 248.4 | 6.2 | 14.6 | 14.1 | 14.2 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
164 | 1 | 417 | 166.8 | 194.9796 | 15.2 | 15.5 | 15.5 | 15.4 | 15.5 | 14.1 | 21.6 | 14.4 | 1.3 | 239.9 | 6.9 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
165 | 2 | 518.4 | 207.36 | 242.3919 | 15.2 | 15.5 | 15.5 | 15.4 | 15.5 | 14.1 | 21.6 | 14.4 | 1.2 | 240.2 | 7.2 | 14.5 | 14.1 | 14.3 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
166 | 3 | 527.3 | 210.92 | 246.5533 | 15.2 | 15.5 | 15.5 | 15.4 | 15.5 | 14.2 | 21.6 | 14.4 | 1.2 | 247.5 | 7.2 | 14.5 | 14.1 | 14.4 | 14.9 | 15.8 | 15.5 | 14.3 | 14.8 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
167 | 4 | 510.3 | 204.12 | 238.6045 | 15.2 | 15.5 | 15.5 | 15.5 | 15.5 | 14.2 | 21.6 | 14.4 | 1.3 | 250.6 | 6 | 14.6 | 15.3 | 16.2 | 15 | 16.1 | 15.5 | 14.4 | 15 | 15 | 16 | 15.3 | 14.7 | 14.6 | 15.3 | 14.9 | 15.1 | 16.8 | 15.5 | 15.5 | 14.7 | 17
168 | 5 | 488.7 | 195.48 | 228.5049 | 15.3 | 15.5 | 15.6 | 15.6 | 15.7 | 14.2 | 21.6 | 14.4 | 1.6 | 256.3 | 5.1 | 14.7 | 19.5 | 23.2 | 15.2 | 17.3 | 15.5 | 16 | 20.6 | 15 | 16.5 | 15.3 | 14.8 | 14.6 | 15.3 | 15 | 15.1 | 16.9 | 15.5 | 15.5 | 14.8 | 17.1
169 | 6 | 473 | 189.2 | 221.1639 | 15.3 | 15.5 | 15.8 | 15.7 | 16.8 | 14.2 | 21.6 | 14.4 | 1.8 | 253.3 | 4.7 | 15.1 | 31.3 | 48.8 | 16.3 | 19.3 | 15.5 | 22.5 | 36.4 | 15 | 18.7 | 15.3 | 14.9 | 14.6 | 15.3 | 15 | 15.2 | 17 | 15.5 | 15.5 | 14.8 | 17.1
170 | 7 | 467.8 | 187.12 | 218.7325 | 15.4 | 15.6 | 16.1 | 16 | 17.8 | 14.2 | 21.6 | 14.4 | 1.7 | 262.2 | 4.6 | 16.1 | 51.1 | 87.1 | 17.7 | 23.2 | 15.5 | 36.8 | 63.2 | 15 | 22.2 | 15.3 | 15 | 14.7 | 15.3 | 15.1 | 15.5 | 17.2 | 15.5 | 15.7 | 14.9 | 17.2
171 | 8 | 462.2 | 184.88 | 216.1141 | 15.5 | 15.6 | 16.4 | 16.3 | 18.2 | 14.3 | 21.6 | 14.5 | 1.7 | 256.5 | 4.8 | 17.8 | 79.1 | 126.8 | 18.3 | 27.8 | 15.6 | 52.7 | 94.4 | 15.1 | 26.4 | 15.3 | 15.2 | 14.9 | 15.3 | 15.2 | 15.8 | 17.5 | 15.4 | 16.3 | 15.1 | 17.4
172 | 9 | 447.5 | 179 | 209.2407 | 15.6 | 15.7 | 16.8 | 16.7 | 18.7 | 14.3 | 21.6 | 14.4 | 2 | 249.5 | 4.3 | 19.9 | 105.6 | 162.7 | 19 | 33.1 | 15.6 | 70.1 | 122.3 | 15.1 | 31.4 | 15.3 | 15.4 | 15.3 | 15.3 | 15.4 | 16 | 17.8 | 15.4 | 16.5 | 15.4 | 17.5
173 | 10 | 440.9 | 176.36 | 206.1547 | 15.7 | 16.1 | 17.5 | 17.8 | 19.7 | 14.4 | 21.6 | 14.4 | 2 | 268.2 | 4.4 | 22 | 129.7 | 203.6 | 19.3 | 37.6 | 15.7 | 90.9 | 162 | 15.1 | 35.6 | 15.4 | 15.9 | 16 | 15.3 | 15.6 | 16.2 | 18.2 | 15.4 | 16.6 | 15.5 | 17.7
174 | 11 | 436.8 | 174.72 | 204.2376 | 16.1 | 16.9 | 18.8 | 19.6 | 20.1 | 14.5 | 21.6 | 14.4 | 2.1 | 265.4 | 5 | 24.1 | 149.3 | 241.8 | 19.5 | 45.2 | 15.8 | 111.6 | 183.2 | 15.2 | 40.8 | 15.5 | 16.5 | 17.1 | 15.3 | 15.9 | 16.6 | 18.6 | 15.4 | 17.2 | 15.8 | 17.9
175 | 12 | 435.1 | 174.04 | 203.4427 | 17.2 | 17.7 | 20.4 | 21.6 | 20.8 | 14.5 | 21.6 | 14.4 | 2.3 | 261.9 | 5.2 | 26.1 | 187.3 | 284.9 | 20.5 | 53 | 16 | 132.8 | 213.4 | 15.3 | 48.4 | 15.5 | 17.4 | 18.6 | 15.3 | 16.6 | 18 | 19 | 15.4 | 18.3 | 16.3 | 18.1
176 | 13 | 434.1 | 173.64 | 202.9752 | 18.9 | 18.7 | 22 | 23.7 | 22.3 | 14.6 | 21.6 | 14.4 | 2.6 | 247.9 | 4.8 | 28.1 | 229.1 | 330.2 | 21.9 | 62.5 | 16.1 | 162.2 | 260 | 15.3 | 58 | 15.7 | 18.3 | 20.6 | 15.4 | 18 | 19.6 | 19.6 | 15.4 | 20.8 | 17.9 | 18.4
177 | 14 | 433.4 | 173.36 | 202.6479 | 21.1 | 20.5 | 23.8 | 26.1 | 27.1 | 14.6 | 21.6 | 14.4 | 3 | 239.8 | 4.5 | 30.4 | 271.2 | 364.2 | 23.6 | 69.3 | 16.3 | 191.7 | 307.6 | 15.3 | 66.4 | 15.8 | 19.5 | 22.9 | 15.4 | 20.3 | 21.6 | 20.3 | 15.4 | 22.9 | 20.6 | 18.8
178 | 15 | 433.3 | 173.32 | 202.6011 | 24.1 | 23.2 | 26.1 | 28.8 | 32.4 | 14.7 | 21.6 | 14.4 | 2.8 | 246.3 | 4.3 | 33 | 314.3 | 399.9 | 24.4 | 76.8 | 16.6 | 222 | 343.7 | 15.4 | 74.1 | 16 | 21.2 | 25.5 | 15.4 | 22.3 | 23.1 | 21.2 | 15.5 | 25.2 | 22.8 | 19.2
179 | 16 | 434.3 | 173.72 | 203.0687 | 26.9 | 26 | 29.1 | 32.3 | 36.3 | 14.7 | 21.6 | 14.4 | 2.8 | 263.1 | 4.6 | 36 | 365.4 | 452.4 | 26.4 | 86.4 | 16.9 | 252.1 | 387.8 | 15.4 | 81.2 | 16.3 | 23.2 | 28.5 | 15.4 | 23.7 | 25.5 | 21.8 | 15.5 | 29.2 | 24.9 | 19.5
180 | 17 | 433.2 | 173.28 | 202.5543 | 30.7 | 28.4 | 32.5 | 35.7 | 39.5 | 14.7 | 21.6 | 14.4 | 2.4 | 264.1 | 5 | 39.6 | 416.1 | 501.2 | 29.8 | 100.9 | 17.2 | 283.3 | 434.7 | 15.5 | 94.5 | 16.6 | 25.6 | 31.9 | 15.5 | 25.6 | 28.1 | 22 | 15.6 | 33 | 27.4 | 20.1
181 | 18 | 433.5 | 173.4 | 202.6946 | 34.1 | 30.6 | 35.9 | 39 | 43.8 | 14.8 | 21.6 | 14.5 | 2.4 | 235.4 | 4.9 | 43.7 | 460.3 | 540.4 | 33.3 | 115.4 | 17.6 | 310.3 | 466.3 | 15.5 | 106.4 | 16.9 | 28.3 | 35.5 | 15.5 | 27.9 | 30.3 | 22.5 | 15.6 | 35.9 | 31 | 20.6
182 | 19 | 435.3 | 174.12 | 203.5362 | 36.9 | 33.6 | 39.1 | 42.9 | 51 | 14.8 | 21.6 | 14.5 | 2.2 | 236.2 | 5.5 | 48 | 481.3 | 568.4 | 34.7 | 127.2 | 18 | 317.3 | 466.3 | 15.5 | 115.3 | 17.3 | 31.4 | 39.2 | 15.6 | 30.1 | 34.2 | 23.3 | 15.7 | 40.1 | 33.8 | 21.1
183 | 20 | 436.4 | 174.56 | 204.0506 | 41 | 36.5 | 42.5 | 46.6 | 58.6 | 14.9 | 21.6 | 14.6 | 2.2 | 257.5 | 6.1 | 52.1 | 506 | 606.1 | 37.1 | 140.1 | 18.4 | 334 | 487.2 | 15.6 | 126.5 | 17.7 | 34.9 | 42.9 | 15.7 | 32.8 | 38 | 24 | 15.8 | 44.1 | 36.4 | 21.7
184 | 21 | 437.9 | 175.16 | 204.7519 | 45.8 | 40.5 | 46.5 | 50.1 | 64.9 | 14.9 | 21.6 | 14.7 | 2.4 | 250.9 | 6.8 | 56.2 | 526.6 | 632 | 39.1 | 152.7 | 18.9 | 344.1 | 500 | 15.6 | 136 | 18.1 | 38.7 | 46.7 | 15.8 | 35.3 | 42.6 | 24.5 | 16 | 46.8 | 39.2 | 22.3
185 | 22 | 439.8 | 175.92 | 205.6403 | 52 | 45.8 | 50.5 | 53.8 | 69.8 | 14.9 | 21.6 | 14.7 | 2.2 | 250.9 | 8.6 | 60.3 | 533 | 635.6 | 39.3 | 159.4 | 19.3 | 348.1 | 494.6 | 15.7 | 140 | 18.6 | 42.8 | 50.2 | 16 | 38.6 | 46.4 | 25.2 | 16.2 | 50.4 | 42 | 22.9
186 | 23 | 440.2 | 176.08 | 205.8274 | 57.2 | 51.1 | 54.9 | 57.3 | 76 | 15 | 21.6 | 14.8 | 2.1 | 247.1 | 8.5 | 64.1 | 533.5 | 636.9 | 40.7 | 168.5 | 19.7 | 351 | 495.4 | 15.8 | 144.6 | 19.1 | 47 | 53.6 | 16.2 | 41.8 | 50.4 | 25.6 | 16.4 | 54 | 44.5 | 23.4
187 | 24 | 440 | 176 | 205.7339 | 61.2 | 55.6 | 59.1 | 60.9 | 86.8 | 15 | 21.6 | 14.9 | 2.6 | 243.7 | 8 | 67.6 | 534.8 | 633.9 | 41.7 | 173.6 | 20.1 | 354.3 | 495 | 15.9 | 149.9 | 19.7 | 51.3 | 56.9 | 16.3 | 45.2 | 53.7 | 27 | 16.6 | 57.2 | 46.7 | 24.1
188 | 25 | 441.5 | 176.6 | 206.4352 | 66 | 60.4 | 62.8 | 64.1 | 93.6 | 15.1 | 21.6 | 15.1 | 2.4 | 248.8 | 7.6 | 70.8 | 530.4 | 638.5 | 42.4 | 179.1 | 20.5 | 351 | 485.5 | 16 | 153.3 | 20.4 | 55.5 | 60.4 | 16.6 | 49.5 | 56.5 | 27.8 | 16.9 | 60 | 48.7 | 24.6
189 | 26 | 442.9 | 177.16 | 207.0898 | 72.4 | 65.9 | 66.1 | 67.1 | 99.7 | 15.1 | 21.6 | 15.4 | 2.4 | 243.9 | 7.5 | 73.6 | 531.6 | 643 | 43.5 | 184.9 | 20.9 | 355.4 | 491.8 | 16.1 | 158.6 | 21 | 59.6 | 63.9 | 16.8 | 53 | 59.2 | 28.6 | 17.2 | 62.6 | 50.8 | 25.1
190 | 27 | 442.7 | 177.08 | 206.9963 | 78.2 | 70.9 | 69.8 | 70.2 | 107.6 | 15.1 | 21.6 | 15.7 | 2.3 | 244.2 | 7.7 | 76.4 | 532.4 | 648.8 | 44.5 | 188.8 | 21.3 | 358.7 | 496.7 | 16.3 | 164.2 | 21.7 | 63.6 | 67.3 | 17 | 55.4 | 62.5 | 29.3 | 17.5 | 65.7 | 53.8 | 25.6
191 | 28 | 443.1 | 177.24 | 207.1833 | 81.6 | 75.1 | 73.2 | 73 | 120.3 | 15.1 | 21.6 | 16.1 | 2.5 | 234.8 | 6.7 | 79.1 | 539.3 | 652 | 45.9 | 194.9 | 21.6 | 366.5 | 516.4 | 16.5 | 170.5 | 22.4 | 67.4 | 70.8 | 17.3 | 57.7 | 65.9 | 30.2 | 17.8 | 68.4 | 57.6 | 26.3
192 | 29 | 444.4 | 177.76 | 207.7912 | 84.4 | 79 | 76.7 | 76 | 132.7 | 15.2 | 21.6 | 16.5 | 3.2 | 245.3 | 6 | 82 | 545.7 | 659.6 | 47.4 | 202.7 | 21.6 | 375.3 | 526.2 | 16.9 | 179 | 23 | 71.2 | 74 | 17.6 | 59.9 | 68.9 | 31 | 18 | 71.1 | 59.8 | 27
193 | 30 | 448.9 | 179.56 | 209.8953 | 87.9 | 82.9 | 80.5 | 79.6 | 139.2 | 15.2 | 21.6 | 16.9 | 3 | 272.7 | 5.4 | 84.8 | 550.2 | 667.4 | 49.9 | 213 | 22 | 376.3 | 518 | 17.4 | 182.8 | 23.8 | 74.8 | 77.1 | 17.9 | 62.1 | 72.1 | 31.5 | 18.3 | 73.6 | 62.1 | 27.5
194 | 31 | 458.9 | 183.56 | 214.5711 | 90.3 | 87.2 | 84.1 | 83.3 | 145 | 15.3 | 21.6 | 17.5 | 2.8 | 238.5 | 5.2 | 87.8 | 556.1 | 682 | 53.4 | 222.9 | 22.3 | 382.9 | 530.2 | 17.9 | 187.2 | 24.5 | 78.4 | 80.3 | 18.2 | 65.1 | 76.1 | 31.7 | 18.6 | 77.3 | 64.4 | 28.1
195 | 32 | 462.7 | 185.08 | 216.3479 | 93.3 | 91.8 | 87.4 | 86.5 | 152.7 | 15.3 | 21.6 | 18 | 2.9 | 259.2 | 6.1 | 90.8 | 573 | 697.5 | 56.4 | 234.8 | 22.7 | 407.1 | 564.1 | 18.8 | 197.9 | 25.4 | 82 | 83.5 | 18.5 | 67.8 | 79.2 | 32.4 | 18.9 | 80.8 | 66.8 | 28.7
196 | 33 | 462.2 | 184.88 | 216.1141 | 95.8 | 95.2 | 90.8 | 89.7 | 162 | 15.3 | 21.6 | 18.5 | 2.7 | 257.3 | 6.9 | 94 | 585.6 | 712.2 | 59.5 | 247.9 | 22.9 | 432.4 | 601.4 | 19.8 | 212.7 | 26.1 | 85.6 | 86.6 | 18.8 | 70.7 | 82.2 | 33.2 | 19.2 | 83.8 | 69.2 | 29.3
197 | 34 | 460.6 | 184.24 | 215.3659 | 99 | 97.9 | 94.1 | 92.9 | 168.7 | 15.3 | 21.6 | 19.1 | 2.2 | 255.2 | 7.3 | 97.1 | 601.6 | 712 | 60.8 | 255.9 | 23.2 | 454.6 | 630.1 | 21 | 225.4 | 26.9 | 89.2 | 89.5 | 19.2 | 73 | 86 | 33.4 | 19.6 | 85.7 | 72.1 | 30.1
198 | 35 | 459.1 | 183.64 | 214.6646 | 101.8 | 100.4 | 97 | 96.5 | 172.5 | 15.3 | 21.6 | 19.6 | 1.7 | 253.1 | 7.5 | 100.3 | 616.9 | 718.4 | 62.4 | 264.5 | 23.8 | 467.7 | 647.6 | 22.3 | 235.6 | 27.8 | 92.9 | 92.3 | 19.6 | 76.1 | 89.7 | 34.2 | 19.9 | 88.3 | 74.9 | 30.9
199 | 36 | 457.4 | 182.96 | 213.8697 | 104.6 | 103.5 | 100.4 | 100.1 | 175.5 | 15.3 | 21.6 | 20.1 | 2 | 251.2 | 7.4 | 103.4 | 625.1 | 715.3 | 63.3 | 271.1 | 24.1 | 471.7 | 642.6 | 23.5 | 244.3 | 28.8 | 96.9 | 95 | 19.9 | 78.8 | 93 | 35 | 20.3 | 91.8 | 76.9 | 31.4
200 | 37 | 455.4 | 182.16 | 212.9345 | 106.9 | 106.5 | 103.9 | 103.5 | 180 | 15.4 | 21.6 | 20.6 | 2.6 | 245.4 | 7.3 | 106.5 | 628.7 | 703.7 | 63.7 | 274.4 | 24.6 | 463.5 | 617.3 | 24.3 | 244.3 | 29.8 | 101.3 | 97.6 | 20.3 | 81.4 | 96.3 | 35.6 | 20.6 | 95.8 | 79.6 | 32.1
201 | 38 | 454.9 | 181.96 | 212.7008 | 108.6 | 109.5 | 107.3 | 106.7 | 185.9 | 15.4 | 21.6 | 21.1 | 2.2 | 242.8 | 7.2 | 109.5 | 632.4 | 695.2 | 64.8 | 281.6 | 25.2 | 457.2 | 611.5 | 25.8 | 248.1 | 30.9 | 105.9 | 100.2 | 20.7 | 84.3 | 99.8 | 36.1 | 21 | 99.8 | 82.6 | 32.8
202 | 39 | 454.4 | 181.76 | 212.467 | 110.2 | 113 | 110.3 | 109.5 | 189.5 | 15.4 | 21.6 | 21.6 | 2.3 | 249.3 | 7.2 | 112.2 | 636.8 | 687.1 | 65.9 | 287.2 | 25.6 | 459.8 | 622.7 | 28.1 | 254.8 | 32 | 110.8 | 102.6 | 21.1 | 86.8 | 102.8 | 36.8 | 21.4 | 102.9 | 85.6 | 33.5
203 | 40 | 452.9 | 181.16 | 211.7656 | 111.6 | 116.9 | 113.3 | 112.3 | 194.2 | 15.5 | 21.6 | 22.2 | 2.3 | 257.7 | 7.2 | 115 | 640.5 | 689.3 | 67.3 | 294.6 | 26 | 459.9 | 635.6 | 31 | 263.2 | 33.1 | 115.8 | 105 | 21.6 | 89.7 | 105.8 | 37.6 | 21.8 | 105.2 | 88.4 | 34.3
204 | 41 | 452.3 | 180.92 | 211.4851 | 113.8 | 120.4 | 116.3 | 114.9 | 195.2 | 15.7 | 21.6 | 22.7 | 2.4 | 256.5 | 6.9 | 117.7 | 644.9 | 685.4 | 69 | 301.5 | 26.4 | 474.6 | 652.8 | 34.4 | 271.9 | 34.2 | 120.7 | 107.4 | 22 | 91.9 | 108.8 | 38 | 22.3 | 107.3 | 90.9 | 34.8
205 | 42 | 451.5 | 180.6 | 211.111 | 115.4 | 123.3 | 118.9 | 117.2 | 195.6 | 15.9 | 21.6 | 23.2 | 2.7 | 259.2 | 7.1 | 120.5 | 650.3 | 681.7 | 70.1 | 307.2 | 26.8 | 479.2 | 660.5 | 37.1 | 278.6 | 35.2 | 125.4 | 109.8 | 22.4 | 94.4 | 111.9 | 38.6 | 22.6 | 109.2 | 93 | 35.3
206 | 43 | 451.6 | 180.64 | 211.1578 | 118.7 | 124.6 | 121.4 | 119.4 | 196.6 | 16 | 21.6 | 23.7 | 2.5 | 270.2 | 7.3 | 123.2 | 655.9 | 690.2 | 71.5 | 310.4 | 27 | 494 | 682.1 | 41.3 | 287.4 | 36.3 | 130 | 112.1 | 22.9 | 97.2 | 114.8 | 39.4 | 23 | 111.6 | 94.8 | 36.1
207 | 44 | 452.6 | 181.04 | 211.6253 | 121.7 | 126.3 | 123.9 | 121.9 | 200.1 | 16.1 | 21.5 | 24.1 | 2.3 | 273.2 | 6.8 | 126 | 659.3 | 702.7 | 73 | 315.9 | 27.4 | 511.3 | 702.1 | 45.6 | 297.9 | 37.3 | 133.9 | 114.5 | 23.3 | 99.5 | 117.4 | 40.3 | 23.4 | 114.6 | 96.9 | 36.8
208 | 45 | 451.9 | 180.76 | 211.298 | 123.4 | 127.1 | 126.3 | 124.2 | 198.8 | 16.2 | 21.5 | 24.6 | 2.5 | 272.6 | 6.2 | 129.2 | 665 | 712.2 | 74.3 | 320.1 | 27.7 | 522.3 | 718.2 | 49 | 305.2 | 38.4 | 137.4 | 116.9 | 23.8 | 101.9 | 120.1 | 41 | 23.8 | 117.3 | 99.2 | 37.5
209 | 46 | 453.4 | 181.36 | 211.9994 | 126.8 | 128 | 129 | 126.9 | 197.1 | 16.2 | 21.5 | 25 | 2.3 | 268.8 | 5.8 | 132.5 | 666 | 706.5 | 75.3 | 325.3 | 28.2 | 520.6 | 711.9 | 50.3 | 311.7 | 39.5 | 140.3 | 119.1 | 24.3 | 104 | 122.9 | 41.8 | 24.2 | 120.3 | 101.5 | 38.4
210 | 47 | 453.6 | 181.44 | 212.0929 | 129.3 | 130 | 131.5 | 129.7 | 196.6 | 16.2 | 21.5 | 25.4 | 2.8 | 256.8 | 5.5 | 135.8 | 668.7 | 706.2 | 76.5 | 332 | 28.6 | 525.5 | 720 | 53.4 | 318.9 | 40.7 | 143.4 | 121.1 | 24.8 | 105.8 | 125 | 42.1 | 24.6 | 123.5 | 103.7 | 39.1
211 | 48 | 455 | 182 | 212.7475 | 131.4 | 132.5 | 134.2 | 132.4 | 197.6 | 16.3 | 21.5 | 25.7 | 2.7 | 259 | 5.6 | 139 | 669.6 | 699 | 77.5 | 337.1 | 29.1 | 531.1 | 721.7 | 56.8 | 326.5 | 41.8 | 146.9 | 122.9 | 25.2 | 107.7 | 127.7 | 42.2 | 25.1 | 126.2 | 106.1 | 39.9
212 | 49 | 455.1 | 182.04 | 212.7943 | 133.3 | 132.9 | 136.6 | 135 | 199.9 | 16.3 | 21.5 | 26 | 2.6 | 257.3 | 5.7 | 142.2 | 667.5 | 698.1 | 78.1 | 340.6 | 29.4 | 519.9 | 695.8 | 57.5 | 327.5 | 43.1 | 149.4 | 124.7 | 25.7 | 110.7 | 130.3 | 43.2 | 25.6 | 129.1 | 108.4 | 40.6
213 | 50 | 456.9 | 182.76 | 213.6359 | 135 | 134.2 | 138.4 | 137.3 | 201.9 | 16.4 | 21.5 | 26.3 | 2.9 | 257.9 | 5.8 | 145.3 | 665.3 | 709.4 | 79.4 | 348.4 | 29.9 | 508.5 | 683.7 | 60.2 | 328.9 | 44.2 | 151.3 | 126.5 | 26.2 | 115.1 | 132.3 | 44.2 | 26.1 | 131.4 | 110.2 | 41.2
214 | 51 | 457.5 | 183 | 213.9165 | 137.5 | 135.8 | 140.3 | 139.5 | 205.4 | 16.4 | 21.5 | 26.7 | 2.3 | 262.1 | 5.8 | 148.3 | 664.4 | 721.9 | 81.4 | 359.7 | 30.5 | 508 | 688 | 66.7 | 336.3 | 45.4 | 152.7 | 128.4 | 26.7 | 118.3 | 134 | 44.7 | 26.5 | 133.5 | 112.5 | 41.8
215 | 52 | 456.8 | 182.72 | 213.5892 | 139.4 | 137.5 | 141.9 | 141.6 | 208.3 | 16.5 | 21.5 | 26.9 | 2.4 | 263.8 | 5.3 | 151.5 | 666.4 | 737 | 83.3 | 367.9 | 31 | 509.9 | 694.1 | 74.9 | 344.7 | 46.6 | 154.1 | 130.1 | 27.1 | 120.5 | 135.9 | 45.3 | 27 | 135.3 | 114.3 | 42.5
216 | 53 | 457.1 | 182.84 | 213.7294 | 141.6 | 138.8 | 143.1 | 143.2 | 214.8 | 16.5 | 21.5 | 27.2 | 2.3 | 274.5 | 4.6 | 154.8 | 670.6 | 744 | 84.6 | 372.4 | 31.6 | 511.8 | 703.5 | 82.1 | 351.3 | 47.8 | 155.6 | 131.6 | 27.6 | 122.8 | 138.2 | 46.2 | 27.5 | 137.2 | 116.3 | 43.1
217 | 54 | 458.8 | 183.52 | 214.5243 | 143.7 | 139.4 | 144.3 | 144.9 | 213.8 | 16.6 | 21.5 | 27.4 | 2.5 | 258.3 | 4.4 | 158.4 | 672.6 | 735.9 | 85.2 | 374.6 | 32.2 | 507.4 | 690.1 | 87.5 | 356.3 | 49 | 156.9 | 132.8 | 28 | 125.2 | 139.5 | 46.7 | 27.9 | 139.3 | 118.4 | 43.7
218 | 55 | 459.5 | 183.8 | 214.8516 | 146.8 | 141.2 | 145.9 | 146.8 | 213.6 | 16.6 | 21.5 | 27.7 | 2.2 | 242.7 | 4.5 | 162 | 675.4 | 745.2 | 85.8 | 382.6 | 32.8 | 504.5 | 691.8 | 92.5 | 362.5 | 50.2 | 157.9 | 133.8 | 28.5 | 126.5 | 141 | 46.9 | 28.4 | 141.2 | 120.4 | 44.5
219 | 56 | 460.6 | 184.24 | 215.3659 | 149.3 | 143.4 | 147.2 | 148.3 | 218.7 | 16.6 | 21.5 | 28.1 | 2.1 | 242.3 | 4.5 | 165.2 | 677.7 | 745.1 | 87.1 | 390.8 | 33.4 | 501 | 693.8 | 97.4 | 366.8 | 51.3 | 159.2 | 134.7 | 28.9 | 127.8 | 142.7 | 47.4 | 28.9 | 142.2 | 122 | 45.3
220 | 57 | 458.8 | 183.52 | 214.5243 | 150.4 | 144.4 | 148.4 | 150 | 227.3 | 16.6 | 21.5 | 28.4 | 2.5 | 248.5 | 4.3 | 168.3 | 683.8 | 743 | 89 | 397.1 | 34 | 505.2 | 706.7 | 103.2 | 372.9 | 52.6 | 160.7 | 135.4 | 29.3 | 129.2 | 143.9 | 47.9 | 29.3 | 143.7 | 123.2 | 45.8
221 | 58 | 460.5 | 184.2 | 215.3192 | 152 | 144.3 | 149.6 | 151.5 | 234.6 | 16.6 | 21.5 | 28.7 | 2.5 | 253.7 | 4.3 | 171.3 | 691 | 749.4 | 90.9 | 403.8 | 34.6 | 506.9 | 716.9 | 107.3 | 380.9 | 53.8 | 162.1 | 135.7 | 29.8 | 130.7 | 145.3 | 48.5 | 29.8 | 145.4 | 124.6 | 46.5
222 | 59 | 460.7 | 184.28 | 215.4127 | 153.1 | 144.6 | 150.5 | 153.1 | 238.3 | 16.6 | 21.5 | 29 | 2.6 | 247.4 | 4.2 | 174.3 | 701.4 | 751.4 | 92.7 | 411.6 | 35.3 | 506.3 | 715.9 | 111.6 | 385.2 | 55 | 163 | 135.8 | 30.2 | 132.3 | 146.5 | 49.2 | 30.3 | 146.9 | 126.3 | 47.2
223 | 60 | 460 | 184 | 215.0854 | 152.8 | 145.8 | 151.6 | 154.4 | 242.3 | 16.5 | 21.5 | 29.3 | 2.6 | 245 | 4 | 177.2 | 704.6 | 751.4 | 93.1 | 413.8 | 35.9 | 507.2 | 708.6 | 116.5 | 389.9 | 56.3 | 163.8 | 136 | 30.7 | 133.6 | 147.7 | 50 | 30.8 | 148.5 | 127.8 | 47.7
224 | 61 | 461.4 | 184.56 | 215.74 | 152.4 | 147 | 152.9 | 155.8 | 239.8 | 16.5 | 21.5 | 29.6 | 2.7 | 248 | 3.8 | 180.2 | 712 | 741 | 93.5 | 414.7 | 36.6 | 505.6 | 708.5 | 121.5 | 393.3 | 57.5 | 164.9 | 135.9 | 31.1 | 134.9 | 148.8 | 50.6 | 31.3 | 149.9 | 129.7 | 48.3
225 | 62 | 463.7 | 185.48 | 216.8154 | 153.8 | 148.6 | 153.9 | 156.7 | 238.1 | 16.5 | 21.5 | 29.9 | 2.8 | 243.6 | 3.8 | 183 | 718.6 | 732.7 | 94.4 | 417.6 | 37.3 | 509.2 | 721.6 | 127.2 | 398.3 | 58.7 | 166.3 | 135.8 | 31.6 | 136.2 | 150.4 | 51.6 | 31.7 | 151.1 | 132.1 | 48.9
226 | 63 | 464.9 | 185.96 | 217.3765 | 157.3 | 151 | 155.3 | 157.8 | 235.2 | 16.5 | 21.5 | 30.1 | 2.8 | 239.4 | 3.8 | 185.8 | 730 | 742 | 95.9 | 425.1 | 38 | 512.7 | 733.1 | 131.8 | 405.4 | 59.9 | 168.1 | 135.6 | 32 | 137.4 | 152 | 52 | 32.2 | 153 | 133.8 | 49.7
227 | 64 | 464.5 | 185.8 | 217.1895 | 159.3 | 153.2 | 156.5 | 159 | 233 | 16.5 | 21.5 | 30.4 | 2.5 | 239.3 | 3.8 | 188.6 | 736.7 | 746.1 | 97.7 | 432.5 | 38.8 | 512.9 | 730.6 | 137.5 | 412.3 | 61 | 169.8 | 134.8 | 32.5 | 138.9 | 153.5 | 52.5 | 32.6 | 154.9 | 135.4 | 50.4
228 | 65 | 463.3 | 185.32 | 216.6284 | 160.6 | 154.9 | 157.6 | 160.3 | 229.8 | 16.5 | 21.5 | 30.7 | 2.5 | 239.6 | 3.9 | 191.3 | 741.1 | 752.6 | 99.4 | 437.7 | 39.5 | 514.2 | 731.8 | 147.8 | 417.9 | 62.2 | 171.1 | 133.4 | 32.9 | 140.5 | 155 | 53.4 | 33.1 | 156.4 | 136.6 | 51.2
229 | 66 | 463.1 | 185.24 | 216.5349 | 162.7 | 155.2 | 158.6 | 162 | 226.9 | 16.5 | 21.5 | 31 | 2.7 | 239.9 | 3.8 | 194 | 744.9 | 744.1 | 101 | 439.5 | 40.3 | 515.2 | 733.7 | 157 | 423.4 | 63.4 | 172.6 | 131.8 | 33.4 | 142 | 155.9 | 54.3 | 33.5 | 157.6 | 137.9 | 51.8
230 | 67 | 463.7 | 185.48 | 216.8154 | 166.7 | 155.2 | 159.8 | 163.2 | 224.3 | 16.5 | 21.5 | 31.2 | 2.3 | 236.5 | 3.7 | 196.7 | 746 | 734.7 | 102.9 | 441.4 | 41 | 522.9 | 745 | 166.1 | 429.6 | 64.6 | 174 | 130.5 | 33.9 | 142.9 | 157.2 | 54.9 | 34 | 159.6 | 139 | 52.5
231 | 68 | 464.5 | 185.8 | 217.1895 | 170.1 | 155.3 | 160.7 | 164.6 | 222.1 | 16.5 | 21.5 | 31.5 | 2.3 | 238.6 | 3.6 | 199.4 | 754.1 | 732.4 | 105.5 | 445.5 | 41.8 | 531.1 | 753.9 | 174.9 | 437.2 | 65.8 | 175.7 | 129.6 | 34.4 | 144.2 | 158.8 | 55.4 | 34.4 | 161.2 | 139.6 | 53.2
232 | 69 | 463.9 | 185.56 | 216.9089 | 171.7 | 155.4 | 162 | 166.3 | 221.7 | 16.6 | 21.5 | 31.8 | 2.6 | 243.1 | 3.6 | 202 | 766.7 | 736.1 | 107.8 | 448.6 | 42.6 | 531 | 752.2 | 181.8 | 441 | 67.1 | 177.3 | 128.9 | 34.9 | 145.8 | 159.8 | 56.1 | 34.9 | 162.2 | 140.9 | 54
233 | 70 | 462.2 | 184.88 | 216.1141 | 173.1 | 155.6 | 163.1 | 167.3 | 218.9 | 16.6 | 21.5 | 32 | 2.6 | 237.5 | 3.6 | 204.5 | 771.9 | 746.5 | 110.3 | 453.9 | 43.4 | 529.7 | 747.7 | 188.6 | 443.3 | 68.3 | 178.7 | 128.6 | 35.3 | 146.4 | 160.9 | 56.6 | 35.4 | 162.4 | 142.6 | 54.7
234 | 71 | 463.6 | 185.44 | 216.7687 | 173.7 | 153.9 | 163.8 | 168.1 | 216.6 | 16.6 | 21.5 | 32.2 | 2.5 | 235.4 | 3.8 | 207 | 777.7 | 762.8 | 114.7 | 462.5 | 44.2 | 524.8 | 741.4 | 195.9 | 447 | 69.6 | 179.3 | 128.9 | 35.8 | 147.7 | 161.5 | 57.3 | 35.8 | 162.9 | 143.7 | 55.5
235 | 72 | 464.6 | 185.84 | 217.2363 | 174 | 153.6 | 164.8 | 168.9 | 215.2 | 16.6 | 21.5 | 32.5 | 2.5 | 237.1 | 4 | 209.5 | 781.8 | 766.3 | 118 | 468.8 | 45 | 528.7 | 748.2 | 204 | 452.7 | 70.9 | 178.8 | 129.6 | 36.3 | 148.4 | 163 | 57.7 | 36.2 | 163.9 | 145.3 | 56.1
236 | 73 | 465.7 | 186.28 | 217.7506 | 174 | 153.5 | 165.7 | 169.7 | 215.8 | 16.7 | 21.5 | 32.7 | 2.8 | 229.4 | 4.2 | 212.2 | 787.1 | 766.1 | 121.1 | 475.6 | 45.9 | 527.7 | 745.5 | 210.4 | 456.7 | 72.1 | 179.1 | 130.4 | 36.7 | 149.4 | 165 | 58.2 | 36.6 | 164 | 147 | 56.9
237 | 74 | 465.1 | 186.04 | 217.47 | 174.2 | 153.3 | 166.5 | 170.2 | 218.3 | 16.6 | 21.5 | 32.9 | 2.4 | 228.7 | 4 | 215 | 790.8 | 764.7 | 125.3 | 482.7 | 46.7 | 529.4 | 738.8 | 216.7 | 460.2 | 73.4 | 180.1 | 131.7 | 37.1 | 150.5 | 166.5 | 59.2 | 37 | 164.8 | 148 | 57.5
238 | 75 | 464 | 185.6 | 216.9557 | 175.3 | 154.6 | 167.7 | 170.5 | 220.4 | 16.7 | 21.5 | 33.2 | 2.2 | 236 | 3.8 | 217.8 | 796.8 | 781 | 130.5 | 492 | 47.6 | 537.1 | 751.2 | 223.9 | 470.1 | 74.6 | 182 | 133.3 | 37.6 | 151.9 | 167.9 | 60 | 37.4 | 166 | 149.7 | 58.1
239 | 76 | 464.1 | 185.64 | 217.0025 | 175.7 | 157.2 | 169.5 | 170.5 | 227.2 | 16.7 | 21.5 | 33.4 | 2.3 | 239.2 | 3.8 | 220.7 | 804.5 | 776.8 | 135.3 | 498.3 | 48.5 | 544.5 | 762.7 | 230.5 | 477.3 | 75.9 | 184.1 | 134.8 | 38 | 153.2 | 168.9 | 60.8 | 37.8 | 166.9 | 150.9 | 58.8
240 | 77 | 465.8 | 186.32 | 217.7973 | 176.3 | 159.2 | 170.5 | 171 | 231.8 | 16.8 | 21.5 | 33.6 | 2.3 | 238.2 | 3.8 | 223.8 | 811.6 | 768.1 | 138.7 | 500.7 | 49.4 | 546.2 | 760.3 | 235.8 | 481.4 | 77.1 | 184.5 | 135.9 | 38.5 | 155.2 | 169.1 | 61.8 | 38.1 | 168.3 | 152.2 | 59.3
241 | 78 | 468.3 | 187.32 | 218.9663 | 176.1 | 160 | 171.1 | 171.8 | 235 | 16.8 | 21.4 | 33.9 | 2.6 | 214.2 | 3.9 | 227 | 818.9 | 771 | 142.7 | 508.4 | 50.3 | 546.9 | 761.1 | 240.6 | 486.8 | 78.3 | 184.8 | 137.5 | 38.9 | 156.7 | 169.3 | 62.9 | 38.5 | 169.8 | 153.1 | 59.9
242 | 79 | 466.9 | 186.76 | 218.3117 | 175.5 | 160.9 | 171.9 | 173.3 | 235.1 | 16.9 | 21.4 | 34.2 | 2.3 | 196.6 | 4 | 229.9 | 821.6 | 768.9 | 146.2 | 512.9 | 51.3 | 544.9 | 760 | 244.9 | 490.7 | 79.6 | 187 | 139.2 | 39.3 | 157.3 | 170.3 | 63.4 | 38.9 | 171.2 | 154.2 | 60.6
243 | 80 | 465.8 | 186.32 | 217.7973 | 175.5 | 161.6 | 173 | 174.5 | 235.5 | 16.9 | 21.4 | 34.4 | 2.2 | 219 | 3.8 | 232.9 | 818.7 | 776.3 | 150.5 | 520.2 | 52.2 | 543.2 | 758.4 | 250.2 | 492.9 | 80.8 | 189.6 | 141.2 | 39.8 | 158.3 | 170.9 | 63.8 | 39.3 | 172.7 | 155.1 | 61.3
244 | 81 | 466 | 186.4 | 217.8909 | 175.2 | 164.3 | 173.4 | 175.5 | 233 | 16.9 | 21.4 | 34.6 | 2.4 | 225 | 3.7 | 236 | 817.7 | 772.4 | 154.5 | 523.3 | 53.2 | 540.9 | 759.6 | 255 | 496.8 | 82.1 | 192.3 | 143.1 | 40.2 | 159.2 | 171.5 | 64.1 | 39.7 | 174.1 | 156.2 | 61.9
245 | 82 | 467.5 | 187 | 218.5922 | 176.2 | 165.6 | 173.8 | 176.4 | 230.6 | 17 | 21.4 | 34.9 | 2.6 | 200.5 | 3.7 | 239.6 | 817.6 | 783.2 | 158.1 | 530.4 | 54.1 | 538.5 | 754.3 | 259.2 | 499.2 | 83.4 | 195.1 | 145.1 | 40.6 | 160 | 172.5 | 64.7 | 40.1 | 175.3 | 157.4 | 62.5
246 | 83 | 466.4 | 186.56 | 218.0779 | 178.2 | 167 | 174.1 | 177.2 | 227.5 | 17 | 21.4 | 35.1 | 2.7 | 208.1 | 3.4 | 243.7 | 816.5 | 783.8 | 162.9 | 536.2 | 55.1 | 535.1 | 751.1 | 263.1 | 503.1 | 84.8 | 198.4 | 147.1 | 41 | 161.2 | 172.5 | 65.5 | 40.5 | 176.3 | 158.7 | 63.1
247 | 84 | 466.5 | 186.6 | 218.1246 | 178.5 | 169.3 | 174.6 | 178.2 | 225.5 | 17 | 21.4 | 35.4 | 2.6 | 235.6 | 3.1 | 247.9 | 815.8 | 789.3 | 168.2 | 543.8 | 56 | 537.5 | 756.4 | 267.1 | 508.4 | 86.1 | 202.3 | 149.3 | 41.4 | 162.4 | 172.9 | 66.2 | 40.9 | 176.9 | 159.9 | 63.8
248 | 85 | 466.2 | 186.48 | 217.9844 | 178.4 | 171.6 | 174.6 | 178.9 | 225.3 | 17.1 | 21.4 | 35.6 | 2.6 | 223 | 3 | 252.1 | 815.7 | 796.9 | 173.2 | 551.2 | 57 | 538.7 | 755.4 | 270.8 | 514.1 | 87.5 | 206.1 | 151.6 | 41.8 | 163.2 | 173.7 | 67.1 | 41.3 | 178 | 161.1 | 64.5
249 | 86 | 466 | 186.4 | 217.8909 | 179.8 | 172.4 | 175.3 | 179.6 | 228.5 | 17.1 | 21.4 | 35.8 | 2.2 | 200.8 | 3 | 256.1 | 816.2 | 796.8 | 176.7 | 558.8 | 58.1 | 539.9 | 759 | 274.5 | 518.8 | 88.8 | 209.5 | 153.6 | 42.2 | 164.3 | 174.5 | 67.7 | 41.6 | 178.8 | 162.1 | 65.2
250 | 87 | 466.2 | 186.48 | 217.9844 | 181.1 | 173.3 | 176.3 | 180.3 | 231.2 | 17.1 | 21.4 | 35.9 | 2.5 | 195.1 | 3.2 | 259.9 | 815.5 | 801.6 | 181.9 | 565.6 | 59.1 | 541.3 | 756.2 | 277.6 | 522.8 | 90.2 | 213.6 | 155.3 | 42.6 | 165 | 175.3 | 68.3 | 42 | 179.8 | 163.2 | 65.7
251 | 88 | 466.3 | 186.52 | 218.0311 | 182.6 | 173.6 | 177.3 | 180.8 | 233.2 | 17.2 | 21.4 | 36.1 | 2.4 | 198.1 | 3.5 | 263.6 | 811.8 | 793.5 | 186.4 | 569.5 | 60.1 | 539.5 | 748.1 | 280.2 | 523.8 | 91.5 | 217.5 | 156.7 | 43 | 165.3 | 176 | 68.9 | 42.3 | 180.9 | 164.3 | 66.4
252 | 89 | 467 | 186.8 | 218.3584 | 183.5 | 175.1 | 178 | 182 | 234.1 | 17.3 | 21.4 | 36.3 | 2.2 | 204.4 | 3.8 | 267.1 | 808.4 | 773.7 | 187.9 | 568.4 | 61.1 | 532.6 | 735.3 | 281.1 | 525.1 | 92.8 | 221.2 | 157.2 | 43.4 | 165.9 | 176.6 | 69.2 | 42.7 | 182 | 165.3 | 66.9
253 | 90 | 465.8 | 186.32 | 217.7973 | 184.3 | 176.6 | 178.5 | 182.9 | 233 | 17.3 | 21.4 | 36.4 | 2.3 | 207.7 | 3.9 | 270.4 | 800.9 | 764.7 | 189.8 | 568.9 | 62.1 | 531.7 | 740.4 | 283 | 527 | 94.2 | 225.2 | 158.2 | 43.8 | 167.1 | 177 | 69.8 | 43.1 | 183.1 | 166.5 | 67.4
254 | 91 | 465.9 | 186.36 | 217.8441 | 185.4 | 177.8 | 178.9 | 183.3 | 232.5 | 17.4 | 21.4 | 36.6 | 2.3 | 209.5 | 4 | 273.5 | 793.7 | 766.2 | 192.5 | 571.8 | 63.2 | 531.2 | 739.6 | 285.9 | 530.2 | 95.5 | 229.7 | 159.5 | 44.2 | 168.2 | 177.3 | 70.5 | 43.4 | 184.2 | 167.7 | 68.1
255 | 92 | 464.6 | 185.84 | 217.2363 | 186.3 | 179.1 | 179.8 | 184.2 | 232.4 | 17.4 | 21.4 | 36.7 | 2.5 | 215.5 | 4 | 276.3 | 789.1 | 761.1 | 195.1 | 572.3 | 64.2 | 526.7 | 734.5 | 287.3 | 532.3 | 96.8 | 234.1 | 160.8 | 44.6 | 168.8 | 178.4 | 70.7 | 43.8 | 185 | 168.4 | 68.7
256 | 93 | 465.6 | 186.24 | 217.7038 | 187.6 | 179.9 | 180.1 | 185.4 | 242.3 | 17.5 | 21.4 | 37 | 2.6 | 206.8 | 3.8 | 279.1 | 787.9 | 755.6 | 197.6 | 574 | 65.3 | 524.1 | 737.5 | 288.6 | 533.6 | 98.1 | 238.6 | 161.8 | 45 | 169.4 | 179.6 | 70.9 | 44.2 | 185.9 | 169 | 69.4
257 | 94 | 465.8 | 186.32 | 217.7973 | 189.2 | 179 | 181.1 | 186.1 | 251.9 | 17.5 | 21.4 | 37.2 | 2.7 | 186.1 | 3.7 | 281.8 | 785.7 | 753.1 | 200 | 574.6 | 66.3 | 521 | 726.1 | 290.6 | 533.2 | 99.3 | 242.2 | 162.4 | 45.4 | 169.9 | 180.5 | 71.5 | 44.6 | 186.6 | 169.8 | 69.9
258 | 95 | 467.1 | 186.84 | 218.4052 | 190.4 | 180.1 | 182.1 | 186.2 | 249.8 | 17.6 | 21.4 | 37.4 | 2.4 | 180.5 | 3.3 | 284.4 | 786 | 744.6 | 202.8 | 575.8 | 67.4 | 520.4 | 732.2 | 292.5 | 535.9 | 100.5 | 245.5 | 163 | 45.8 | 170.8 | 181.4 | 72.3 | 45 | 187.2 | 170.7 | 70.4
259 | 96 | 468.7 | 187.48 | 219.1533 | 191.9 | 180.9 | 182.8 | 186.4 | 247.7 | 17.7 | 21.3 | 37.5 | 2.6 | 178.8 | 3.1 | 286.5 | 782.6 | 741.9 | 205.6 | 576 | 68.4 | 521.3 | 728.7 | 294.7 | 538.1 | 101.6 | 248.6 | 163.4 | 46.2 | 172.4 | 181.4 | 73.4 | 45.5 | 187.5 | 171.5 | 70.8
260 | 97 | 469.6 | 187.84 | 219.5741 | 194.7 | 180.8 | 183.4 | 185.9 | 246 | 17.7 | 21.3 | 37.7 | 2.7 | 178.3 | 3.2 | 288.8 | 779.6 | 751.9 | 208.5 | 577.4 | 69.4 | 521.8 | 729.2 | 296.6 | 541.2 | 102.7 | 251.5 | 164.7 | 46.6 | 173.5 | 182 | 74.4 | 45.9 | 187.7 | 172.3 | 71.4
261 | 98 | 468.7 | 187.48 | 219.1533 | 195.4 | 180.5 | 183.8 | 185.2 | 244.1 | 17.8 | 21.3 | 37.9 | 2.6 | 185.8 | 3.6 | 291.2 | 783.5 | 749.7 | 210.8 | 579.4 | 70.5 | 523.1 | 734.7 | 299.2 | 544.4 | 103.8 | 254.5 | 165.7 | 47.1 | 174.5 | 182.1 | 75.5 | 46.3 | 188.6 | 172.9 | 72.1
262 | 99 | 466.9 | 186.76 | 218.3117 | 195.3 | 181.6 | 184.2 | 185.2 | 243.6 | 17.9 | 21.3 | 38.1 | 2.7 | 198.4 | 3.8 | 293.6 | 784.1 | 741.2 | 213 | 581.6 | 71.6 | 520.9 | 726.7 | 300.6 | 546.2 | 104.8 | 258.7 | 166.7 | 47.5 | 175.5 | 182.2 | 76.4 | 46.7 | 189.3 | 173.5 | 72.8
263 | 100 | 467.8 | 187.12 | 218.7325 | 196.4 | 181.2 | 185.1 | 186.4 | 241.8 | 17.9 | 21.3 | 38.4 | 2.5 | 198.6 | 3.8 | 295.9 | 779.6 | 744 | 215.6 | 585 | 72.6 | 521.2 | 733.9 | 302.2 | 548.6 | 105.8 | 262.1 | 168.5 | 47.9 | 175.9 | 183.3 | 76.9 | 47.2 | 190.1 | 173.9 | 73.3
264 | 101 | 467.9 | 187.16 | 218.7793 | 197.8 | 179.9 | 185.4 | 187.4 | 241.3 | 18 | 21.3 | 38.6 | 2.5 | 196 | 4 | 298.2 | 773.9 | 756.2 | 219 | 589.2 | 73.6 | 521.8 | 732.5 | 304.6 | 551.6 | 106.9 | 265.5 | 171 | 48.3 | 177.4 | 183.8 | 77.4 | 47.6 | 190.5 | 174.9 | 74.1
265 | 102 | 468 | 187.2 | 218.826 | 199.5 | 178.8 | 185.9 | 188 | 241 | 18.1 | 21.3 | 38.8 | 2.4 | 190.1 | 4 | 300.7 | 774.2 | 768.5 | 222.5 | 594.9 | 74.7 | 527.6 | 739.8 | 308.1 | 557.2 | 107.8 | 269 | 172.9 | 48.6 | 178.9 | 184.3 | 78 | 48.1 | 190.9 | 175.8 | 74.6
266 | 103 | 467.9 | 187.16 | 218.7793 | 200 | 179 | 186.7 | 188.5 | 241.5 | 18.1 | 21.3 | 39 | 2.4 | 182.6 | 3.9 | 303.5 | 771.5 | 773.3 | 225.1 | 597.5 | 75.8 | 528.6 | 737.5 | 311.3 | 559.7 | 108.8 | 272.8 | 174.6 | 49 | 180.5 | 184.8 | 78.9 | 48.5 | 191.2 | 176.1 | 75.1
267 | 104 | 468.2 | 187.28 | 218.9195 | 199.7 | 180.1 | 187 | 188.7 | 240.7 | 18.2 | 21.3 | 39.2 | 2.5 | 181.7 | 3.9 | 306.5 | 770.2 | 786.7 | 228.1 | 603 | 76.8 | 531.6 | 738 | 314.2 | 563.4 | 109.8 | 276.9 | 176.7 | 49.4 | 181 | 185.4 | 79.7 | 49 | 191.8 | 176.9 | 76
268 | 105 | 468.4 | 187.36 | 219.013 | 197.7 | 182.5 | 187.6 | 188.9 | 241 | 18.2 | 21.3 | 39.4 | 2.6 | 183.4 | 3.7 | 309.6 | 772.1 | 784.3 | 230.6 | 606.2 | 77.9 | 539.1 | 746.2 | 317.7 | 566.2 | 110.7 | 282.3 | 178.7 | 49.8 | 181.3 | 186.5 | 80.3 | 49.4 | 192.5 | 177.6 | 76.7
269 | 106 | 468.1 | 187.24 | 218.8728 | 197.5 | 184.6 | 188.3 | 188.6 | 244.1 | 18.2 | 21.3 | 39.6 | 2.8 | 189.5 | 3.7 | 312.6 | 772.7 | 780.1 | 232 | 608.7 | 78.9 | 537.3 | 740.9 | 319.7 | 567.4 | 111.7 | 288 | 180.2 | 50.1 | 182.5 | 187 | 80.9 | 49.9 | 193.2 | 178.4 | 77.2
270 | 107 | 468.7 | 187.48 | 219.1533 | 198.1 | 185.6 | 189 | 189 | 245.8 | 18.3 | 21.3 | 39.8 | 2.8 | 212.9 | 3.8 | 315.6 | 770.6 | 777.2 | 233.1 | 610.3 | 80 | 538.4 | 744.5 | 321.3 | 570.5 | 112.6 | 293.8 | 181.4 | 50.5 | 183.7 | 187.5 | 81.9 | 50.3 | 193.7 | 179 | 77.8
271 | 108 | 468.2 | 187.28 | 218.9195 | 198.4 | 185.6 | 189.6 | 189.4 | 246.6 | 18.3 | 21.3 | 39.9 | 2.9 | 214.3 | 3.6 | 318.5 | 767.4 | 783 | 234.7 | 614.2 | 81.1 | 544.3 | 752.6 | 324.9 | 575.4 | 113.6 | 299.9 | 182.9 | 50.9 | 184.6 | 188.5 | 82.6 | 50.7 | 194.4 | 179.4 | 78.2
272 | 109 | 466.8 | 186.72 | 218.2649 | 198.8 | 185.3 | 190.5 | 190.1 | 247.5 | 18.4 | 21.3 | 40 | 2.7 | 193.2 | 3.4 | 321.3 | 768.8 | 782.9 | 236.3 | 618.2 | 82.1 | 545.6 | 752.9 | 327.6 | 576.6 | 114.5 | 306.6 | 184.8 | 51.2 | 185.9 | 189.4 | 83.5 | 51.2 | 195.4 | 179.8 | 78.9
273 | 110 | 466.9 | 186.76 | 218.3117 | 199 | 185.6 | 191.3 | 191.1 | 249.2 | 18.5 | 21.3 | 40.1 | 3 | 178.9 | 3.5 | 324.1 | 771 | 780 | 237.7 | 618.4 | 83.2 | 541.2 | 748.5 | 329.1 | 576.7 | 115.5 | 313.6 | 186.4 | 51.6 | 186.7 | 190.1 | 84.4 | 51.6 | 196.3 | 180.2 | 79.6
274 | 111 | 465.8 | 186.32 | 217.7973 | 199.2 | 185.5 | 192.4 | 191.6 | 251.2 | 18.5 | 21.3 | 40.2 | 2.7 | 178.2 | 3.6 | 327 | 771.7 | 792.8 | 239.4 | 623.8 | 84.2 | 543.9 | 752.5 | 331.1 | 580.4 | 116.5 | 321.4 | 187.7 | 52 | 188.3 | 190.6 | 84.9 | 52.1 | 197 | 180.5 | 80.2
275 | 112 | 466.2 | 186.48 | 217.9844 | 198.9 | 185.6 | 193.2 | 192.6 | 252.5 | 18.7 | 21.3 | 40.3 | 2.5 | 190.1 | 3.6 | 330 | 771.7 | 800.6 | 241.2 | 626.9 | 85.3 | 544.9 | 758.2 | 333.1 | 583.8 | 117.4 | 330.2 | 188.5 | 52.4 | 189.3 | 191.2 | 85.7 | 52.5 | 197.5 | 181.3 | 80.8
276 | 113 | 466.1 | 186.44 | 217.9376 | 199.2 | 185.5 | 194.2 | 193.5 | 255.2 | 18.7 | 21.3 | 40.3 | 2.9 | 196.7 | 3.5 | 332.9 | 773.1 | 805.3 | 243.7 | 631.5 | 86.4 | 546.4 | 759.4 | 336.4 | 586.9 | 118.3 | 339.4 | 189.7 | 52.8 | 190.1 | 192 | 86.2 | 53 | 197.5 | 181.9 | 81.4
277 | 114 | 466.8 | 186.72 | 218.2649 | 199.5 | 185.2 | 194.6 | 193.8 | 255.7 | 18.7 | 21.3 | 40.4 | 2.8 | 198.1 | 3.7 | 335.6 | 769 | 812.6 | 246 | 634.4 | 87.4 | 547.9 | 760.9 | 339.3 | 588.8 | 119.2 | 349.1 | 191.9 | 53.2 | 190.9 | 193 | 86.5 | 53.5 | 197.4 | 182.5 | 82.1
278 | 115 | 467.4 | 186.96 | 218.5455 | 199.5 | 184.8 | 194.2 | 193.8 | 255.3 | 18.8 | 21.3 | 40.4 | 2.7 | 203.3 | 4.5 | 338.3 | 766.6 | 810.3 | 247.7 | 636.4 | 88.5 | 553 | 767.9 | 342.4 | 591.4 | 120 | 358.6 | 194.1 | 53.6 | 191.9 | 194.2 | 87.4 | 53.9 | 197.8 | 183 | 82.8
279 | 116 | 467.7 | 187.08 | 218.6857 | 199.5 | 185.7 | 194.3 | 194.3 | 256.9 | 18.9 | 21.2 | 40.5 | 2.6 | 211.5 | 4.9 | 340.7 | 767.4 | 807.6 | 249.6 | 639 | 89.5 | 556.8 | 766.1 | 344.9 | 593.2 | 120.9 | 368.1 | 197 | 54 | 192.8 | 195.4 | 88.3 | 54.4 | 198.1 | 183.8 | 83.5
280 | 117 | 467.5 | 187 | 218.5922 | 200.7 | 187.2 | 194.9 | 195.1 | 259.1 | 18.9 | 21.2 | 40.6 | 2.9 | 207.9 | 5.1 | 343 | 771.8 | 800.5 | 250.9 | 641.9 | 90.6 | 554.6 | 761.1 | 346 | 594.5 | 121.7 | 378.5 | 199.9 | 54.4 | 193.4 | 196.4 | 89.3 | 54.9 | 198.7 | 184.5 | 84.1
281 | 118 | 467.7 | 187.08 | 218.6857 | 201.5 | 186.7 | 195.1 | 195.6 | 259.5 | 19 | 21.2 | 40.6 | 2.8 | 198.2 | 5 | 345.2 | 770.9 | 797.3 | 251.9 | 643.6 | 91.6 | 554.5 | 764.5 | 348.3 | 595.9 | 122.5 | 391 | 203.3 | 54.8 | 194.2 | 197.5 | 90.1 | 55.3 | 199.8 | 185.2 | 84.6
282 | 119 | 468.3 | 187.32 | 218.9663 | 201.6 | 185.1 | 195.3 | 196.1 | 261.8 | 19 | 21.2 | 40.7 | 2.6 | 197.8 | 5 | 347.3 | 771.3 | 787.6 | 252.9 | 644.1 | 92.7 | 554.8 | 760.6 | 350 | 596.8 | 123.3 | 403 | 206.6 | 55.2 | 194.9 | 198.7 | 90.7 | 55.7 | 200.6 | 185.9 | 85.2
283 | 120 | 467.7 | 187.08 | 218.6857 | 201.4 | 183.7 | 196.4 | 196.4 | 263.9 | 19 | 21.2 | 40.8 | 2.7 | 203.5 | 5.5 | 349.5 | 773.3 | 775.2 | 254.1 | 645.8 | 93.8 | 552.8 | 755.2 | 350.4 | 598.8 | 124.1 | 413.6 | 209.3 | 55.6 | 195.8 | 199.6 | 91.7 | 56.2 | 201.2 | 186.5 | 86
284 | 121 | 467.6 | 187.04 | 218.639 | 201.6 | 183.5 | 197.6 | 196.6 | 264.4 | 19 | 21.2 | 40.9 | 2.7 | 199.4 | 5.8 | 351.6 | 773.7 | 767.4 | 255.4 | 645.4 | 95 | 547.2 | 747.9 | 351.3 | 597.5 | 124.8 | 423.5 | 211.9 | 56 | 196.4 | 200.2 | 92.5 | 56.6 | 201.9 | 186.9 | 86.6
285 | 122 | 468.1 | 187.24 | 218.8728 | 202.1 | 185 | 197.9 | 197 | 272.6 | 19.1 | 21.2 | 41 | 2.9 | 194.2 | 5.8 | 353.6 | 773.3 | 774.9 | 257.6 | 648 | 96.1 | 543.6 | 746.4 | 352.5 | 598.6 | 125.6 | 432.7 | 214.3 | 56.4 | 196.6 | 200.7 | 93.1 | 57.1 | 202.7 | 187.5 | 87.3
286 | 123 | 467.9 | 187.16 | 218.7793 | 202.7 | 186.9 | 197.9 | 197.6 | 278.8 | 19.3 | 21.2 | 41 | 3.1 | 200.1 | 5.9 | 355.6 | 772 | 774.8 | 259.6 | 649.1 | 97.3 | 542.5 | 742.1 | 353.9 | 598.7 | 126.3 | 441.7 | 216.4 | 56.9 | 197 | 201.3 | 93.6 | 57.5 | 203.4 | 188.1 | 87.9
287 | 124 | 468.3 | 187.32 | 218.9663 | 203.5 | 189.6 | 198.7 | 198.3 | 279 | 19.4 | 21.2 | 41 | 3.1 | 200.8 | 5.8 | 357.4 | 770.2 | 780.4 | 261.9 | 650.6 | 98.5 | 541.4 | 745.9 | 355.4 | 598.6 | 127.1 | 450.7 | 219 | 57.3 | 197.4 | 202.3 | 93.9 | 58 | 204.1 | 188.8 | 88.6
288 | 125 | 467.1 | 186.84 | 218.4052 | 203.6 | 192 | 200.2 | 198.8 | 280.6 | 19.4 | 21.2 | 41.1 | 2.3 | 184.8 | 5.4 | 359.1 | 771.1 | 784.4 | 264.5 | 652.8 | 99.8 | 542 | 744.5 | 356.9 | 601.2 | 127.9 | 459.6 | 221.7 | 57.7 | 197.9 | 203.4 | 94.2 | 58.4 | 204.7 | 189.2 | 89.2
289 | 126 | 468.2 | 187.28 | 218.9195 | 204.1 | 193.4 | 202 | 199.3 | 279.3 | 19.5 | 21.2 | 41.1 | 2.2 | 183.6 | 5 | 360.8 | 770.7 | 792.8 | 267 | 656.2 | 101.1 | 540.7 | 744.3 | 358.3 | 602.2 | 128.7 | 468.6 | 223.8 | 58.1 | 198.3 | 204.6 | 95.3 | 58.9 | 205.4 | 189.6 | 89.8
290 | 127 | 468 | 187.2 | 218.826 | 202.8 | 193.4 | 202.7 | 199.4 | 279 | 19.6 | 21.2 | 41.2 | 2.5 | 187.5 | 4.6 | 362.4 | 769 | 799.1 | 269.3 | 660.5 | 102.4 | 537.5 | 743.8 | 359.1 | 604 | 129.5 | 477.3 | 226.2 | 58.6 | 199 | 205.6 | 95.8 | 59.4 | 205.9 | 190 | 90.5
291 | 128 | 467.4 | 186.96 | 218.5455 | 202 | 193.2 | 203.1 | 199.9 | 278.7 | 19.6 | 21.2 | 41.4 | 2.7 | 191.7 | 4.4 | 364 | 766.8 | 804.4 | 272.1 | 663 | 103.8 | 537.9 | 749.9 | 360.6 | 605.2 | 130.3 | 486.1 | 228.8 | 59 | 200.1 | 206.2 | 96.6 | 59.8 | 206.5 | 190.6 | 91.2
292 | 129 | 467.6 | 187.04 | 218.639 | 201.2 | 193.4 | 204.1 | 200.6 | 279.6 | 19.7 | 21.2 | 41.5 | 2.6 | 209.1 | 4.2 | 365.6 | 762.8 | 806.6 | 276.5 | 665.2 | 105.2 | 539.3 | 746.7 | 362.9 | 607.5 | 131.1 | 494 | 231.5 | 59.5 | 201.1 | 206.7 | 97.5 | 60.3 | 207.1 | 191.2 | 91.8
293 | 130 | 468 | 187.2 | 218.826 | 202 | 193.7 | 204.5 | 200.8 | 282.3 | 19.7 | 21.2 | 41.7 | 2.8 | 203.7 | 4 | 367 | 763.9 | 794.2 | 280.2 | 666.4 | 106.6 | 539.8 | 736.5 | 364.3 | 608.4 | 132 | 501.6 | 234.9 | 59.9 | 201.8 | 207.4 | 98.2 | 60.8 | 207.5 | 192 | 92.5
294 | 131 | 467.8 | 187.12 | 218.7325 | 203 | 195 | 205.2 | 200.9 | 285.6 | 19.8 | 21.2 | 41.8 | 2.6 | 193.7 | 4.3 | 368.4 | 763.2 | 772.1 | 282.4 | 665 | 107.9 | 539.5 | 736.4 | 365 | 608.2 | 132.8 | 509.9 | 237.6 | 60.4 | 202.6 | 208.3 | 98.9 | 61.2 | 207.4 | 192.6 | 93
295 | 132 | 467.8 | 187.12 | 218.7325 | 203.3 | 197.4 | 206.3 | 201.5 | 286.3 | 19.9 | 21.2 | 42 | 2.8 | 191.7 | 4.4 | 369.7 | 761.8 | 749 | 285.1 | 661.6 | 109.2 | 533.5 | 724.3 | 365.5 | 605.8 | 133.7 | 518 | 240.3 | 60.9 | 203.4 | 209.4 | 99.5 | 61.7 | 207.8 | 192.9 | 93.6
296 | 133 | 467.7 | 187.08 | 218.6857 | 204.5 | 198.4 | 207.3 | 202.3 | 284.3 | 20 | 21.2 | 42.2 | 2.5 | 185 | 4.2 | 371.1 | 761 | 734 | 287.9 | 657.1 | 110.6 | 527.8 | 717.2 | 366.1 | 602.9 | 134.6 | 525.3 | 243.2 | 61.3 | 204 | 210.4 | 99.9 | 62.1 | 208.1 | 193.1 | 94.1
297 | 134 | 468.9 | 187.56 | 219.2468 | 207.9 | 199.3 | 208.7 | 203.5 | 284.8 | 20 | 21.2 | 42.3 | 2.6 | 182.1 | 4.8 | 372.4 | 759.6 | 733.8 | 290.5 | 655.2 | 111.9 | 522.2 | 714.5 | 366.3 | 601 | 135.5 | 542.9 | 245.9 | 61.8 | 204.9 | 211.9 | 100.5 | 62.6 | 208.7 | 193.2 | 94.8
298 | 135 | 468 | 187.2 | 218.826 | 210.9 | 200.3 | 210.5 | 204.7 | 282.1 | 20 | 21.2 | 42.4 | 2.9 | 184.9 | 5.5 | 373.8 | 758.8 | 729.7 | 294.2 | 655.7 | 113.2 | 515.1 | 711.4 | 366.4 | 600 | 136.4 | 584.7 | 248.6 | 62.3 | 205.7 | 212.7 | 101.1 | 63 | 209.7 | 193.7 | 95.5
299 | 136 | 468.5 | 187.4 | 219.0598 | 212.1 | 200.4 | 211.3 | 205.6 | 278.1 | 20.1 | 21.2 | 42.5 | 2.8 | 188.6 | 5.9 | 374.9 | 759 | 743.9 | 299.3 | 658.2 | 114.4 | 515.3 | 712 | 367.4 | 600.2 | 137.2 | 621.5 | 252 | 62.8 | 206.1 | 213.3 | 101.9 | 63.4 | 210.6 | 194.5 | 96.1
300 | 137 | 467.7 | 187.08 | 218.6857 | 212 | 199.5 | 211.3 | 206.2 | 276.2 | 20.2 | 21.2 | 42.7 | 2.6 | 191.9 | 5.9 | 376.1 | 759.4 | 760.8 | 303.9 | 661.5 | 115.8 | 514.9 | 713.4 | 368 | 600.7 | 138.1 | 655.3 | 255.5 | 63.2 | 206.7 | 213.8 | 102.7 | 63.9 | 210.9 | 195.1 | 96.7
301 | 138 | 467.6 | 187.04 | 218.639 | 211.6 | 196.6 | 210.5 | 206.5 | 279.1 | 20.2 | 21.2 | 42.8 | 2.8 | 195.6 | 6 | 377.1 | 760.3 | 771.2 | 307.6 | 665.2 | 117.1 | 517.6 | 719.1 | 369.5 | 602.2 | 139 | 684.1 | 259.5 | 63.7 | 207.6 | 214 | 103.6 | 64.3 | 211.1 | 195.5 | 97.5
302 | 139 | 468.7 | 187.48 | 219.1533 | 211.7 | 194.9 | 210.2 | 206.8 | 280.6 | 20.3 | 21.1 | 43 | 2.7 | 189.3 | 6 | 378 | 760 | 781.9 | 312.6 | 667.3 | 118.4 | 515.8 | 719.6 | 370.5 | 601.1 | 139.8 | 700.7 | 262.5 | 64.2 | 208.8 | 214.2 | 104.4 | 64.8 | 211.3 | 195.8 | 98.1
303 | 140 | 468.2 | 187.28 | 218.9195 | 212.2 | 195.5 | 210.8 | 207.4 | 279.2 | 20.4 | 21.1 | 43.2 | 2.8 | 186.2 | 5.9 | 378.8 | 756.4 | 777.4 | 317 | 667.4 | 119.6 | 516.5 | 718.1 | 372.1 | 601.4 | 140.6 | 723.7 | 265.8 | 64.7 | 209.4 | 214.4 | 105.4 | 65.2 | 211.9 | 196 | 98.7
304 | 141 | 467.4 | 186.96 | 218.5455 | 212.4 | 197.4 | 210.9 | 207.8 | 276.5 | 20.5 | 21.1 | 43.3 | 2.5 | 185.2 | 5.8 | 379.5 | 752.5 | 769.7 | 321 | 667 | 120.8 | 513.3 | 712.6 | 372.9 | 600 | 141.4 | 736.7 | 269.6 | 65.2 | 209.7 | 214.5 | 106.1 | 65.6 | 212.2 | 196.2 | 99.4
305 | 142 | 468.1 | 187.24 | 218.8728 | 215.6 | 198.3 | 211.1 | 208.1 | 275.7 | 20.6 | 21.1 | 43.4 | 3.1 | 180.2 | 6 | 380.1 | 752.9 | 779.8 | 326.1 | 668.3 | 122.1 | 517.4 | 729 | 375.1 | 601.3 | 142.2 | 748.4 | 274.2 | 65.7 | 209.5 | 214.8 | 106.4 | 66.1 | 212.5 | 196.6 | 100.1
306 | 143 | 468.3 | 187.32 | 218.9663 | 218.2 | 199.1 | 211 | 208.6 | 276.6 | 20.7 | 21.1 | 43.6 | 2.6 | 187.5 | 6.1 | 380.7 | 756.6 | 620.5 | 331.6 | 669.6 | 123.3 | 520 | 737.8 | 377.7 | 605.2 | 143.1 | 758.8 | 278.1 | 66.1 | 210 | 215.4 | 107.1 | 66.5 | 213 | 197.2 | 100.6
307 | 144 | 468.5 | 187.4 | 219.0598 | 220.1 | 200.2 | 211 | 209.4 | 277.5 | 20.8 | 21.1 | 43.7 | 2.4 | 193.6 | 5.9 | 375.9 | 555 | 272.1 | 289.4 | 670 | 124.6 | 518.9 | 730.6 | 379.1 | 606 | 143.9 | 761.3 | 282.2 | 66.6 | 210.5 | 216 | 108.1 | 67 | 213.7 | 197.7 | 101.2
308 | 145 | 468.8 | 187.52 | 219.2001 | 221.2 | 200.5 | 211.8 | 209.9 | 277.6 | 20.8 | 21.1 | 43.9 | 2.4 | 188.8 | 5.8 | 272.8 | 330 | 157.8 | 191 | 670.1 | 125.8 | 515.1 | 720.5 | 378.8 | 604.4 | 144.8 | 766.1 | 286 | 67.1 | 210.7 | 216.6 | 108.9 | 67.4 | 214.4 | 198.1 | 101.8
309 | 146 | 467.4 | 186.96 | 218.5455 | 222.8 | 200.7 | 212.3 | 210.1 | 283.5 | 20.9 | 21.1 | 44 | 2.6 | 187.2 | 5.6 | 258.1 | 303 | 151.9 | 182.9 | 672 | 127 | 514.7 | 720.1 | 379.5 | 605.5 | 145.7 | 763.7 | 289.8 | 67.5 | 210.9 | 217.1 | 109.5 | 67.9 | 214.8 | 198.5 | 102.5
310 | 147 | 468.5 | 187.4 | 219.0598 | 222 | 201.2 | 212.6 | 210.2 | 286.6 | 20.9 | 21.1 | 44.2 | 2.8 | 188.1 | 5.5 | 274.9 | 347.5 | 165.4 | 210.4 | 675.6 | 128.3 | 516.4 | 729.7 | 380.1 | 607.3 | 146.5 | 770.5 | 293.6 | 68 | 211.5 | 217.8 | 110.1 | 68.3 | 215.2 | 199.1 | 103.2
311 | 148 | 468.3 | 187.32 | 218.9663 | 221.2 | 200.8 | 212.4 | 210.4 | 290.3 | 20.9 | 21.1 | 44.3 | 2.5 | 187.6 | 5.3 | 306.5 | 411.6 | 172.5 | 209.8 | 679.4 | 129.6 | 515.9 | 732.9 | 380.6 | 608.9 | 147.3 | 771.1 | 297.3 | 68.4 | 212.6 | 218 | 110.8 | 68.7 | 214.6 | 199.6 | 103.8
312 | 149 | 467.8 | 187.12 | 218.7325 | 221.6 | 201.1 | 212.4 | 210.8 | 293.1 | 21 | 21.1 | 44.5 | 2.5 | 187.2 | 5.2 | 377.1 | 580 | 216.1 | 258.6 | 683.1 | 130.8 | 514.5 | 726.9 | 380.6 | 608 | 148.2 | 761.9 | 301.4 | 68.9 | 213.3 | 218.2 | 111.3 | 69.2 | 214.5 | 199.6 | 104.4
313 | 150 | 468.1 | 187.24 | 218.8728 | 220.6 | 202.2 | 212.2 | 211 | 295.1 | 21 | 21.1 | 44.7 | 2.6 | 187.1 | 5.1 | 383.7 | 727.1 | 248.1 | 317.6 | 684.5 | 132 | 512 | 724.7 | 381.3 | 608.2 | 149 | 758.6 | 304.8 | 69.3 | 213.7 | 218.6 | 111.6 | 69.6 | 214.5 | 200.1 | 105.1
314 | 151 | 467.6 | 187.04 | 218.639 | 220.8 | 203.3 | 212 | 211.5 | 296.5 | 21.1 | 21.1 | 44.9 | 2.9 | 187.3 | 5.2 | 384 | 762.3 | 226.7 | 373 | 686.5 | 133.2 | 509.4 | 726 | 382.3 | 610.3 | 149.9 | 755.5 | 308.8 | 69.8 | 213.8 | 218.8 | 112.3 | 70 | 214.2 | 200.6 | 105.8
315 | 152 | 466.8 | 186.72 | 218.2649 | 222.3 | 204.6 | 211.9 | 211.6 | 298.8 | 21.2 | 21.1 | 45 | 3 | 187.8 | 5.5 | 384.2 | 763.9 | 759.1 | 378.2 | 690.2 | 134.5 | 506.1 | 719.8 | 382.1 | 610.8 | 150.7 | 752.2 | 312.5 | 70.2 | 213.9 | 218.8 | 112.9 | 70.5 | 214.3 | 200.7 | 106.3
316 | 153 | 467.1 | 186.84 | 218.4052 | 224 | 206.6 | 212.4 | 211.5 | 298.7 | 21.3 | 21.1 | 45.2 | 3.1 | 186.4 | 5.8 | 384.2 | 765.7 | 829.3 | 383.7 | 692.2 | 135.7 | 503.7 | 721.3 | 382.8 | 613.2 | 151.5 | 751.9 | 315.8 | 70.7 | 214 | 218.8 | 113.6 | 70.9 | 215.2 | 200.6 | 106.8
317 | 154 | 467.1 | 186.84 | 218.4052 | 225.4 | 207.2 | 212.5 | 211.1 | 301.8 | 21.3 | 21.1 | 45.3 | 2.8 | 188.9 | 5.6 | 384.1 | 762.7 | 827.7 | 388.8 | 695.3 | 137 | 507.8 | 729.7 | 384.1 | 615 | 152.4 | 759 | 319.9 | 71.1 | 214.2 | 218.7 | 114.4 | 71.2 | 215.4 | 201.2 | 107.3
318 | 155 | 466.8 | 186.72 | 218.2649 | 225.7 | 207.3 | 212.7 | 210.7 | 300.9 | 21.4 | 21.1 | 45.5 | 3 | 189.5 | 5.4 | 384.1 | 761.2 | 824.7 | 393.7 | 697.8 | 138.1 | 506.7 | 729.3 | 384.5 | 615.6 | 153.2 | 768.6 | 324.1 | 71.6 | 214.9 | 218.7 | 115.6 | 71.6 | 215.4 | 202.2 | 108
319 | 156 | 466.2 | 186.48 | 217.9844 | 226.1 | 207.3 | 212.6 | 210.9 | 306.2 | 21.5 | 21.1 | 45.6 | 2.8 | 188.5 | 5.1 | 384.1 | 762.2 | 829.9 | 399.1 | 699.9 | 139.3 | 505.7 | 730.5 | 384.1 | 616 | 154.1 | 771.6 | 327.4 | 72 | 215.2 | 218.8 | 116.2 | 72 | 215.3 | 203 | 108.7
320 | 157 | 466.7 | 186.68 | 218.2182 | 226.7 | 207.8 | 212.9 | 210.6 | 308.7 | 21.5 | 21.1 | 45.8 | 2.7 | 187.3 | 5.3 | 384.2 | 762.1 | 838.3 | 404.8 | 702.1 | 140.5 | 507.8 | 733.7 | 384.2 | 618.3 | 154.9 | 779.4 | 331.4 | 72.5 | 215.3 | 219.1 | 116.9 | 72.3 | 214.8 | 203.2 | 109.3
321 | 158 | 466.9 | 186.76 | 218.3117 | 227.2 | 207.5 | 213.4 | 210.2 | 312.7 | 21.6 | 21.1 | 45.9 | 3.2 | 186.8 | 5.3 | 384.2 | 763.4 | 825.7 | 408.4 | 702.4 | 141.6 | 505.6 | 731.1 | 384.2 | 618.9 | 155.8 | 779.8 | 335 | 72.9 | 215.7 | 219.6 | 117.9 | 72.7 | 214.2 | 203.9 | 110
322 | 159 | 467.7 | 187.08 | 218.6857 | 226.9 | 207.5 | 214.1 | 209.9 | 320 | 21.7 | 21 | 46.1 | 3.4 | 183.7 | 5.1 | 384.2 | 763 | 822.3 | 411 | 702.6 | 142.7 | 504.5 | 730.1 | 384.9 | 619.3 | 156.7 | 764.4 | 337.3 | 73.4 | 216.2 | 220.4 | 118 | 73 | 214.5 | 204.1 | 110.5
323 | 160 | 467.2 | 186.88 | 218.452 | 226.1 | 206.9 | 214.4 | 210.3 | 320.6 | 21.8 | 21 | 46.3 | 3.3 | 183.3 | 5 | 384.4 | 760.5 | 839.4 | 415 | 706.3 | 143.8 | 506.9 | 736.2 | 384.9 | 620.3 | 157.7 | 770.2 | 340.7 | 73.8 | 217 | 221.3 | 118.6 | 73.4 | 215.3 | 204.3 | 111.1
324 | 161 | 467.9 | 187.16 | 218.7793 | 224.8 | 207.1 | 214.9 | 211 | 316.1 | 21.8 | 21 | 46.5 | 3.1 | 184.3 | 5.2 | 384.6 | 757.8 | 844.3 | 419.4 | 708 | 144.9 | 509.7 | 744.5 | 385 | 623 | 158.7 | 775.9 | 344.6 | 74.2 | 217.7 | 221.6 | 119.6 | 73.7 | 215.7 | 204.3 | 111.7
325 | 162 | 467.2 | 186.88 | 218.452 | 224.7 | 207.3 | 215.3 | 211.3 | 315.7 | 21.9 | 21 | 46.6 | 2.6 | 180 | 5.3 | 385 | 755.7 | 836.1 | 422.1 | 708.4 | 146.1 | 514.7 | 748.4 | 385 | 625 | 159.7 | 772.5 | 348.2 | 74.7 | 218.4 | 221.5 | 120.4 | 74.1 | 215.3 | 204.9 | 112.4
326 | 163 | 467 | 186.8 | 218.3584 | 225.2 | 207.4 | 215.2 | 211.2 | 318.4 | 21.9 | 21 | 46.8 | 2.8 | 179.1 | 5.2 | 385.5 | 753 | 834.4 | 424.1 | 709.6 | 147.2 | 516.5 | 747.1 | 385.1 | 624.5 | 160.8 | 776.3 | 351.6 | 75.1 | 218.5 | 221.6 | 121.5 | 74.4 | 215.4 | 205.8 | 112.9
327 | 164 | 466.6 | 186.64 | 218.1714 | 226.6 | 208.1 | 214.9 | 211.3 | 321.7 | 21.9 | 21 | 47 | 2.9 | 181.6 | 4.9 | 386.3 | 752.3 | 829.3 | 426.2 | 709.5 | 148.4 | 516.4 | 748 | 385.6 | 624.1 | 161.8 | 778.9 | 354.9 | 75.6 | 218.9 | 221.8 | 122.1 | 74.8 | 215.6 | 206.7 | 113.4
328 | 165 | 466.2 | 186.48 | 217.9844 | 228.2 | 209.3 | 214.9 | 211.8 | 332.6 | 22 | 21 | 47.2 | 3.1 | 186.9 | 4.5 | 387.3 | 752.5 | 825.4 | 428.1 | 711.2 | 149.5 | 517.5 | 752.3 | 386 | 625.8 | 162.9 | 778 | 358.2 | 76 | 219.3 | 221.7 | 122.9 | 75.1 | 215.8 | 206.6 | 113.8
329 | 166 | 466.7 | 186.68 | 218.2182 | 227.7 | 209.8 | 215.9 | 211.9 | 331.7 | 22 | 21 | 47.3 | 3.4 | 192.7 | 4.2 | 388.3 | 752.8 | 834.3 | 431 | 712.6 | 150.7 | 517.8 | 752.4 | 385.5 | 626.6 | 164 | 779.7 | 361.1 | 76.4 | 219.6 | 221.9 | 123.7 | 75.5 | 215.9 | 206.5 | 114.4
330 | 167 | 466.1 | 186.44 | 217.9376 | 225.7 | 211 | 216.6 | 211.8 | 330.4 | 22.2 | 21 | 47.5 | 3.7 | 191.4 | 4.3 | 389.3 | 749.7 | 828.9 | 434.3 | 712.3 | 151.8 | 517.5 | 744.5 | 385.3 | 628.1 | 165.2 | 795.2 | 364.5 | 76.9 | 219.6 | 222.2 | 124.1 | 75.8 | 216.2 | 206.6 | 115
331 | 168 | 467 | 186.8 | 218.3584 | 226 | 210.1 | 216.3 | 211.3 | 324.3 | 22.2 | 21 | 47.7 | 3.5 | 190.7 | 4.2 | 390.1 | 747 | 812.5 | 435.8 | 710.9 | 153 | 515 | 732.7 | 384.2 | 627.2 | 166.1 | 800.5 | 367.8 | 77.3 | 220 | 222.6 | 124.3 | 76.2 | 216.5 | 207 | 115.7
332 | 169 | 466.9 | 186.76 | 218.3117 | 226 | 209 | 216.6 | 211.7 | 318.2 | 22.2 | 21 | 47.9 | 3.7 | 193.8 | 4.1 | 391 | 746.2 | 801.8 | 436.1 | 709.5 | 154.1 | 513.9 | 728.6 | 383.8 | 627.9 | 167.2 | 795.1 | 370.8 | 77.7 | 220.6 | 222.3 | 124.9 | 76.5 | 216.7 | 207.7 | 116.4
333 | 170 | 467.2 | 186.88 | 218.452 | 226.5 | 210.3 | 216.6 | 212.8 | 314.4 | 22.4 | 21 | 48.1 | 3.2 | 202.4 | 4.2 | 391.9 | 745 | 804.2 | 437.3 | 710.5 | 155.2 | 512.3 | 726.6 | 382.8 | 627.4 | 168.4 | 792.5 | 373.4 | 78.1 | 221.2 | 222.4 | 125.4 | 76.9 | 216.9 | 208.2 | 117
334 | 171 | 467.3 | 186.92 | 218.4987 | 227.6 | 210.3 | 216.3 | 213.3 | 309 | 22.3 | 21 | 48.2 | 3.1 | 199 | 4.5 | 393 | 742.9 | 803 | 437.5 | 710.8 | 156.4 | 509.8 | 719.4 | 381.9 | 626.1 | 169.2 | 782.3 | 377.2 | 78.6 | 221.4 | 222.5 | 126 | 77.2 | 217.5 | 208.4 | 117.6
335 | 172 | 467.6 | 187.04 | 218.639 | 228.5 | 210.4 | 216.6 | 214 | 305.7 | 22.4 | 21 | 48.3 | 3.1 | 192.9 | 4.5 | 394.2 | 742.4 | 798.9 | 437.1 | 712.1 | 157.6 | 507.6 | 719.9 | 381.8 | 625.2 | 170.1 | 774.6 | 380.9 | 79 | 221.2 | 222.9 | 126.5 | 77.6 | 218 | 208.4 | 118.2
336 | 173 | 467.5 | 187 | 218.5922 | 229.4 | 210.5 | 216.3 | 214.6 | 305.9 | 22.5 | 21 | 48.4 | 3.6 | 192.2 | 4.4 | 395.4 | 739.3 | 785.4 | 435.9 | 710.2 | 158.7 | 508.1 | 727.8 | 381.3 | 625.6 | 171 | 764.3 | 384.8 | 79.4 | 221.5 | 223.2 | 127.5 | 77.9 | 218.1 | 208.7 | 118.7
337 | 174 | 467.7 | 187.08 | 218.6857 | 231.9 | 209.7 | 216.3 | 214.5 | 305.3 | 22.5 | 21 | 48.6 | 3.2 | 188.2 | 4.5 | 396.6 | 742.1 | 783.7 | 435.6 | 710 | 159.8 | 507.3 | 737.4 | 381.2 | 626.9 | 171.5 | 762.7 | 387.8 | 79.8 | 222.2 | 223.2 | 128.6 | 78.3 | 218.5 | 209 | 119.1
338 | 175 | 466.6 | 186.64 | 218.1714 | 234.2 | 210.5 | 216.9 | 214.6 | 305 | 22.6 | 21 | 48.7 | 3.2 | 182.2 | 4.5 | 397.6 | 744.1 | 768.5 | 435.7 | 707.9 | 160.9 | 507.7 | 742.2 | 381 | 628.7 | 172.2 | 759.2 | 389.6 | 80.2 | 222.5 | 223.5 | 129.1 | 78.7 | 219.4 | 209.4 | 119.7
339 | 176 | 466.9 | 186.76 | 218.3117 | 237.1 | 212.3 | 217.5 | 215.6 | 303.2 | 22.6 | 21 | 48.9 | 3.4 | 183.4 | 4.5 | 398.7 | 744.1 | 772.4 | 437 | 706.7 | 162 | 505.2 | 737.2 | 380.2 | 628.1 | 172.7 | 753.3 | 391.6 | 80.6 | 223.3 | 223.9 | 129.7 | 79.1 | 220 | 210 | 120.4
340 | 177 | 466.5 | 186.6 | 218.1246 | 239.4 | 212.8 | 218.1 | 216 | 301.9 | 22.7 | 21 | 49 | 3 | 183.3 | 4.2 | 399.8 | 742.7 | 775.3 | 438.1 | 705.6 | 163.1 | 502.6 | 730.6 | 379.8 | 628 | 173.3 | 752.4 | 393.8 | 81 | 224.8 | 224.4 | 130.4 | 79.4 | 220.5 | 210.5 | 121.1
341 | 178 | 467 | 186.8 | 218.3584 | 239.9 | 213 | 218.3 | 216.3 | 300.4 | 22.7 | 21 | 49.1 | 3.4 | 189.2 | 3.8 | 400.8 | 744.3 | 794.7 | 440.1 | 708.4 | 164.2 | 501.1 | 734.5 | 379.8 | 628.7 | 173.8 | 763.2 | 396.2 | 81.4 | 225.9 | 224.9 | 131.5 | 79.8 | 221 | 211.1 | 121.7
342 | 179 | 466.2 | 186.48 | 217.9844 | 238.7 | 213.3 | 218.6 | 216.6 | 297.9 | 22.8 | 21 | 49.3 | 3.2 | 190.5 | 3.4 | 401.9 | 746.1 | 810.2 | 443 | 711.3 | 165.3 | 503.8 | 740.4 | 380.1 | 631.5 | 174.3 | 772.8 | 399.5 | 81.9 | 226.3 | 225.4 | 132.2 | 80.2 | 221.7 | 211.4 | 122.4
343 | 180 | 466.8 | 186.72 | 218.2649 | 236.9 | 214.6 | 218.7 | 217 | 299.6 | 22.9 | 21 | 49.5 | 3.1 | 194.1 | 3.8 | 403.1 | 745.2 | 815 | 445.8 | 713.6 | 166.5 | 507.7 | 741.9 | 380.4 | 633.6 | 174.9 | 778.9 | 403.8 | 82.3 | 226.3 | 225.7 | 132.6 | 80.6 | 221.8 | 211.6 | 123
344 | 181 | 467.1 | 186.84 | 218.4052 | 235.1 | 215.9 | 218.8 | 217.1 | 305.9 | 23 | 21 | 49.7 | 3 | 201.1 | 4.4 | 404.1 | 747.1 | 815.9 | 448.6 | 714.2 | 167.6 | 508.2 | 739.3 | 380.5 | 635.4 | 175.5 | 780.3 | 407.2 | 82.7 | 226.4 | 226.2 | 133.2 | 80.9 | 221.8 | 211.7 | 123.6
345 | 182 | 467.6 | 187.04 | 218.639 | 233.5 | 216.3 | 219.4 | 217.2 | 303.7 | 23.2 | 21 | 49.8 | 3.3 | 187.8 | 5 | 405.1 | 748.9 | 814.2 | 450.5 | 711.9 | 168.7 | 508 | 737 | 380.7 | 635.1 | 176 | 775.4 | 408.8 | 83.1 | 227.3 | 226.6 | 133.7 | 81.3 | 221.8 | 212.2 | 124.2
346 | 183 | 466.7 | 186.68 | 218.2182 | 232.7 | 216.9 | 220 | 217.6 | 301.3 | 23.3 | 21 | 50 | 3 | 183.2 | 5.4 | 406.2 | 751.1 | 817.3 | 453.5 | 711.8 | 169.8 | 508 | 740.1 | 381.8 | 636.1 | 176.6 | 772.5 | 410.5 | 83.5 | 228 | 226.7 | 134.3 | 81.7 | 222.3 | 212.5 | 124.9
347 | 184 | 468 | 187.2 | 218.826 | 233.1 | 217.4 | 220.2 | 218.1 | 300.7 | 23.3 | 21 | 50.1 | 2.6 | 196.2 | 5.3 | 407.3 | 752.8 | 814.1 | 456.5 | 711.9 | 170.8 | 507.5 | 739.5 | 382.5 | 636.6 | 177.1 | 772.3 | 412.7 | 83.9 | 229 | 226.7 | 134.8 | 82.1 | 222.4 | 212.7 | 125.5
348 | 185 | 467.1 | 186.84 | 218.4052 | 235.4 | 217.8 | 220.2 | 218 | 304 | 23.4 | 21 | 50.2 | 3 | 200.2 | 5.4 | 408.4 | 755.3 | 793 | 458.5 | 710.3 | 171.9 | 508.1 | 736.5 | 383 | 636.3 | 177.7 | 770.3 | 414.5 | 84.3 | 229.6 | 227.5 | 135.8 | 82.4 | 222.4 | 213 | 125.9
349 | 186 | 465.9 | 186.36 | 217.8441 | 236 | 219.7 | 220.4 | 218 | 302.9 | 23.4 | 20.9 | 50.4 | 3.3 | 192.3 | 4.5 | 409.4 | 757.8 | 778.6 | 459.6 | 707 | 172.8 | 509.5 | 733.2 | 383.9 | 635.5 | 178.2 | 763.8 | 415.7 | 84.7 | 230.2 | 229 | 136.8 | 82.8 | 222.7 | 212.9 | 126.5
350 | 187 | 465.4 | 186.16 | 217.6103 | 237.9 | 221.4 | 221.2 | 218.2 | 301.3 | 23.5 | 20.9 | 50.5 | 3.3 | 187.8 | 4.3 | 410.5 | 759.3 | 760.6 | 461.5 | 704.9 | 173.8 | 506.8 | 723.4 | 384.1 | 633.7 | 178.9 | 757.4 | 416.1 | 85.1 | 231.1 | 229.5 | 137.9 | 83.2 | 223.2 | 213.2 | 127
351 | 188 | 467 | 186.8 | 218.3584 | 239.4 | 221.6 | 222.2 | 217.9 | 297.3 | 23.6 | 20.9 | 50.7 | 2.9 | 189.3 | 4.2 | 411.2 | 761.1 | 746.9 | 463 | 702.7 | 174.7 | 502.6 | 722.3 | 384.3 | 631.8 | 179.6 | 740.8 | 416.9 | 85.5 | 231.5 | 230.5 | 138.8 | 83.6 | 223 | 213 | 127.6
352 | 189 | 466.5 | 186.6 | 218.1246 | 239 | 222 | 222.9 | 217.5 | 296.4 | 23.6 | 20.9 | 50.8 | 3 | 202.6 | 3.6 | 412 | 762 | 762.9 | 465.6 | 703.2 | 175.6 | 505.6 | 734.6 | 385.3 | 633.3 | 180.3 | 753.4 | 418.4 | 85.9 | 232 | 231.5 | 139.9 | 83.9 | 222.9 | 213.2 | 128.1
353 | 190 | 467.5 | 187 | 218.5922 | 239.6 | 221.8 | 223.4 | 217.3 | 297 | 23.7 | 20.9 | 51 | 3.8 | 233.7 | 3.2 | 412.8 | 763.3 | 782.2 | 468.4 | 704.6 | 176.6 | 506.5 | 735.9 | 385.9 | 634 | 181 | 751.3 | 420.5 | 86.3 | 232.2 | 232.5 | 140.5 | 84.3 | 223.6 | 213.1 | 128.8
354 | 191 | 464.4 | 185.76 | 217.1427 | 239.8 | 220.9 | 224.4 | 217.6 | 296.9 | 23.7 | 20.9 | 51.2 | 3.1 | 271.6 | 2.9 | 413.6 | 762.3 | 778.7 | 470.6 | 705 | 177.4 | 505.8 | 738.8 | 386.3 | 633.4 | 181.6 | 753.4 | 422.8 | 86.7 | 232.4 | 233.4 | 140.8 | 84.7 | 224.3 | 213.4 | 129.3
355 | 192 | 463.6 | 185.44 | 216.7687 | 239.7 | 220.9 | 225.2 | 218.3 | 295.3 | 23.7 | 20.9 | 51.3 | 3 | 279.5 | 2.3 | 414.2 | 763.7 | 773.2 | 472.4 | 704 | 178.3 | 505.2 | 744.9 | 386.5 | 634.3 | 182.2 | 745.9 | 424.5 | 87.1 | 233.3 | 233.8 | 141.8 | 85 | 225.3 | 213.7 | 129.8
356 | 193 | 464.9 | 185.96 | 217.3765 | 240.4 | 221.6 | 225.5 | 219.2 | 297.8 | 23.7 | 20.9 | 51.4 | 3 | 238.1 | 1.7 | 414.9 | 765.2 | 776.7 | 474.3 | 704.4 | 179.1 | 505 | 743.8 | 386.9 | 634.8 | 182.8 | 735.1 | 425.8 | 87.6 | 233.6 | 233.9 | 142.7 | 85.4 | 226.1 | 214.2 | 130.3
357 | 194 | 466.2 | 186.48 | 217.9844 | 240.9 | 222.5 | 225.5 | 220.1 | 300.2 | 23.7 | 20.9 | 51.5 | 2.6 | 177.4 | 1.9 | 415.7 | 764.2 | 781.7 | 476 | 705.2 | 180.1 | 503.1 | 745.4 | 388.1 | 635.5 | 183.4 | 744.6 | 427.5 | 88 | 233.6 | 234.1 | 143 | 85.7 | 226.8 | 214.6 | 130.9
358 | 195 | 465.5 | 186.2 | 217.6571 | 241.6 | 223.2 | 225.6 | 220.5 | 295 | 23.8 | 20.9 | 51.6 | 2.9 | 177 | 2.4 | 416.4 | 764.2 | 781 | 477.9 | 705.1 | 181 | 507.1 | 745.6 | 389.3 | 638.2 | 184 | 757.1 | 429.2 | 88.4 | 233.7 | 234.5 | 143 | 86.1 | 227.4 | 215.2 | 131.6
359 | 196 | 464.9 | 185.96 | 217.3765 | 241.5 | 223.7 | 225.6 | 221.4 | 292.9 | 23.8 | 20.9 | 51.7 | 3.2 | 216.1 | 3.5 | 417.3 | 764.2 | 792 | 480 | 706.2 | 182 | 511.4 | 752 | 390.3 | 639.1 | 184.6 | 770.2 | 431.1 | 88.8 | 233.5 | 234.7 | 143.3 | 86.5 | 228.2 | 215.7 | 132.3
360 | 197 | 466.5 | 186.6 | 218.1246 | 241.4 | 223.3 | 225.5 | 222.1 | 293.2 | 23.9 | 20.9 | 51.8 | 3.3 | 215.4 | 4.5 | 418.5 | 765.2 | 795.6 | 481.6 | 707.2 | 183 | 515.5 | 754.8 | 391.3 | 641 | 185.2 | 776.2 | 433.4 | 89.2 | 233.7 | 234.8 | 144 | 86.9 | 228.5 | 216.2 | 132.9
361 | 198 | 464.2 | 185.68 | 217.0492 | 241.9 | 222.4 | 225.2 | 222.9 | 307.5 | 24.1 | 20.9 | 52 | 3.7 | 213.3 | 5 | 420.1 | 764.7 | 806 | 482.5 | 708.8 | 183.9 | 517.1 | 758.1 | 392.3 | 642.4 | 185.7 | 774 | 436.2 | 89.7 | 233.6 | 234.8 | 145 | 87.2 | 228.7 | 216.4 | 133.5
362 | 199 | 466.8 | 186.72 | 218.2649 | 240.4 | 221.9 | 224.8 | 223.5 | 312.6 | 24.3 | 20.9 | 52.1 | 3.1 | 217.8 | 5.2 | 421.8 | 763.2 | 805.1 | 483.7 | 710.3 | 184.9 | 518.8 | 761.6 | 393.3 | 644.4 | 186.2 | 779.9 | 438.5 | 90.1 | 233.6 | 235 | 145.8 | 87.6 | 228.9 | 216.9 | 133.9
363 | 200 | 466.4 | 186.56 | 218.0779 | 239.1 | 223.4 | 224.6 | 223.9 | 316.2 | 24.3 | 20.9 | 52.3 | 3.2 | 217.3 | 5.4 | 423.3 | 762.6 | 801.7 | 484.8 | 710.2 | 185.9 | 520.4 | 766.8 | 393.8 | 646 | 186.8 | 782.5 | 440.7 | 90.5 | 233.7 | 235.2 | 146 | 88 | 229.5 | 217.1 | 134.6
364 | 201 | 466.7 | 186.68 | 218.2182 | 240.2 | 225.1 | 225.1 | 224.1 | 319.9 | 24.4 | 20.9 | 52.5 | 3.2 | 203.3 | 5.5 | 424.8 | 761 | 804.5 | 485.8 | 711.5 | 186.9 | 519.2 | 766.3 | 394.7 | 646.6 | 187.3 | 781.1 | 443.7 | 90.9 | 233.7 | 235.1 | 146.1 | 88.4 | 229.8 | 217.4 | 135.2
365 | 202 | 467.2 | 186.88 | 218.452 | 241.5 | 225.3 | 225.6 | 224.3 | 318.1 | 24.5 | 20.9 | 52.8 | 3 | 198.9 | 5.4 | 426.3 | 759.4 | 807.6 | 486.3 | 712.6 | 187.9 | 521.3 | 770 | 395.4 | 648.1 | 187.9 | 786.5 | 446.6 | 91.4 | 233.8 | 235.1 | 146.5 | 88.8 | 229.8 | 217.5 | 135.8
366 | 203 | 467.2 | 186.88 | 218.452 | 241.7 | 225.5 | 225.8 | 224.7 | 315.4 | 24.6 | 20.9 | 53 | 3.1 | 212.1 | 6.1 | 427.6 | 759.2 | 797 | 486.8 | 711.3 | 189 | 520.7 | 769.5 | 396.4 | 648.7 | 188.5 | 785.7 | 448.9 | 91.8 | 234 | 235.3 | 147 | 89.2 | 230.5 | 217.8 | 136.4
367 | 204 | 467.3 | 186.92 | 218.4987 | 242.3 | 226.2 | 225.6 | 225.3 | 311.5 | 24.6 | 20.9 | 53.2 | 3.1 | 207.3 | 6.6 | 428.9 | 757.7 | 787.2 | 487.1 | 710.7 | 190.1 | 520.1 | 775.6 | 397 | 650.5 | 189.1 | 785.5 | 451.7 | 92.2 | 234.1 | 235.7 | 147.4 | 89.6 | 231 | 218.1 | 137
368 | 205 | 467.1 | 186.84 | 218.4052 | 243.6 | 226.5 | 225.7 | 225.3 | 308.2 | 24.6 | 20.9 | 53.3 | 2.7 | 203.7 | 6.8 | 430.1 | 755.4 | 784.3 | 487.3 | 710.8 | 191.3 | 518 | 782.6 | 397.7 | 651.6 | 189.7 | 782.9 | 454.5 | 92.7 | 234.2 | 236.1 | 148.2 | 89.9 | 231.3 | 218.6 | 137.6
369 | 206 | 465.9 | 186.36 | 217.8441 | 244 | 227.2 | 226 | 224.7 | 307.6 | 24.7 | 20.9 | 53.5 | 2.9 | 192.2 | 6.6 | 431 | 754.9 | 784.9 | 487.6 | 711.4 | 192.4 | 524.8 | 790.2 | 398.5 | 653.5 | 190.4 | 790.7 | 457.6 | 93.1 | 234.3 | 236.6 | 148.8 | 90.3 | 231.6 | 218.8 | 138.2
370 | 207 | 467.3 | 186.92 | 218.4987 | 243.5 | 227.5 | 225.9 | 224.3 | 303.1 | 24.8 | 20.9 | 53.6 | 2.8 | 182.8 | 6.5 | 431.7 | 754.3 | 796.7 | 488.1 | 713.4 | 193.6 | 525.4 | 789.4 | 399.7 | 653.8 | 191.1 | 799.2 | 460.4 | 93.6 | 235.2 | 237 | 150 | 90.7 | 231.9 | 219.1 | 138.8
371 | 208 | 465 | 186 | 217.4233 | 243.6 | 227.6 | 226.5 | 223.7 | 306.8 | 24.8 | 20.9 | 53.7 | 3.1 | 188 | 5.6 | 432.1 | 755.2 | 792.3 | 488.7 | 714.2 | 194.7 | 528.3 | 786.5 | 400.2 | 655.6 | 191.7 | 800.9 | 463.7 | 94 | 236.5 | 237.2 | 151.2 | 91.1 | 232.3 | 219.6 | 139.3
372 | 209 | 465.6 | 186.24 | 217.7038 | 244.9 | 228.9 | 227.9 | 223.7 | 307.1 | 24.8 | 20.9 | 53.9 | 2.8 | 191.6 | 4.7 | 432.3 | 754.8 | 784.4 | 489.1 | 713.5 | 195.9 | 528.8 | 779.6 | 400.1 | 656.6 | 192.4 | 800.1 | 465.4 | 94.5 | 237.4 | 237.5 | 152 | 91.5 | 232.7 | 219.9 | 140
373 | 210 | 466.5 | 186.6 | 218.1246 | 246.4 | 229.1 | 228.3 | 224.4 | 306.8 | 25 | 20.9 | 53.9 | 3.2 | 203.1 | 4.1 | 432.6 | 753.8 | 791.3 | 489.5 | 713.1 | 197 | 533.2 | 773.5 | 400.1 | 656.4 | 193.2 | 799.2 | 466.9 | 95 | 238.8 | 237.7 | 152.8 | 91.8 | 233 | 219.9 | 140.5
374 | 211 | 467.5 | 187 | 218.5922 | 249 | 230.3 | 228.5 | 224.8 | 312 | 25 | 20.9 | 54 | 3.2 | 216.7 | 3.2 | 433.5 | 752.5 | 796.8 | 490.1 | 713.2 | 198.2 | 536.6 | 783.2 | 400.6 | 657.6 | 193.9 | 800.2 | 468.5 | 95.5 | 239.6 | 237.8 | 153.5 | 92.2 | 232.9 | 220.2 | 141
375 | 212 | 466.7 | 186.68 | 218.2182 | 249.6 | 231 | 228.9 | 224.8 | 313.1 | 25.1 | 20.9 | 54 | 3 | 223.2 | 2.5 | 435.1 | 750.7 | 796.2 | 490.9 | 712.5 | 199.4 | 542.5 | 783.6 | 401.2 | 659.3 | 194.6 | 807.8 | 470.9 | 95.9 | 239.7 | 238.5 | 154 | 92.6 | 232.8 | 220.7 | 141.5
376 | 213 | 465.7 | 186.28 | 217.7506 | 249.6 | 230.6 | 229.5 | 224.4 | 312.7 | 25.3 | 20.9 | 54 | 3 | 219.7 | 2.2 | 437.1 | 750.4 | 792.5 | 491.7 | 713.9 | 200.6 | 543.3 | 784.3 | 401.7 | 660.2 | 195.3 | 811.6 | 472.9 | 96.4 | 240.2 | 239.3 | 154.4 | 92.9 | 232.7 | 221.5 | 142.2
377 | 214 | 466.4 | 186.56 | 218.0779 | 249 | 231.3 | 230.1 | 224.4 | 310.5 | 25.4 | 20.9 | 54.1 | 3 | 209.9 | 2.4 | 439 | 748.1 | 800.4 | 492.6 | 715.7 | 201.7 | 545 | 790.1 | 402 | 662.6 | 196.1 | 815.1 | 475.4 | 97 | 240.9 | 239.4 | 155 | 93.3 | 232.5 | 222 | 142.8
378 | 215 | 466.5 | 186.6 | 218.1246 | 249.5 | 231.7 | 230.8 | 224.1 | 307.9 | 25.5 | 20.9 | 54.2 | 3.1 | 187.1 | 2.6 | 442.7 | 744.8 | 806.8 | 493.7 | 716.9 | 202.9 | 547.1 | 791.4 | 402.3 | 663.6 | 196.8 | 813.7 | 478 | 97.4 | 241.4 | 239.6 | 155.6 | 93.6 | 232.8 | 222.2 | 143.4
379 | 216 | 465.9 | 186.36 | 217.8441 | 250 | 231.7 | 231.3 | 224.3 | 305.6 | 25.6 | 20.9 | 54.3 | 3 | 159.6 | 2.9 | 446.7 | 745.8 | 797.2 | 494.9 | 715.7 | 204 | 546.3 | 779 | 402.2 | 663.4 | 197.5 | 807.3 | 479.5 | 97.9 | 241.7 | 239.9 | 156.4 | 94 | 233 | 222.7 | 144.1
380 | 217 | 468.2 | 187.28 | 218.9195 | 250.6 | 231 | 232 | 225.2 | 311.5 | 25.7 | 20.8 | 54.4 | 2.8 | 180 | 4.3 | 450.7 | 744.6 | 802.8 | 496.5 | 717 | 205 | 549.7 | 779.8 | 402.5 | 665.9 | 198.3 | 813.8 | 481.3 | 98.4 | 241.9 | 240 | 157.1 | 94.3 | 233.4 | 223.5 | 144.7
381 | 218 | 468 | 187.2 | 218.826 | 251.1 | 231.7 | 232.8 | 225.8 | 316.2 | 25.8 | 20.8 | 54.5 | 3.2 | 188.8 | 5.6 | 454.9 | 744.2 | 799.9 | 498.3 | 716.7 | 206.1 | 554.4 | 775.8 | 402.5 | 667.6 | 199.1 | 818.6 | 483.3 | 98.9 | 242.4 | 240.2 | 157.5 | 94.6 | 233.7 | 224.2 | 145.3
382 | 219 | 467.6 | 187.04 | 218.639 | 251.1 | 233.3 | 233.4 | 225.6 | 315.2 | 25.9 | 20.8 | 54.6 | 3.4 | 176.5 | 5.9 | 458.3 | 741.9 | 789.1 | 500.1 | 715.9 | 207 | 552.3 | 774.4 | 402.6 | 667.1 | 199.9 | 814.9 | 485.2 | 99.3 | 242.4 | 240.6 | 157.9 | 95 | 233.9 | 224.7 | 146
383 | 220 | 466.9 | 186.76 | 218.3117 | 250.7 | 234.9 | 233.7 | 225.7 | 311.5 | 26 | 20.8 | 54.6 | 2.8 | 185.2 | 6 | 461.2 | 740.2 | 787 | 501.8 | 716.3 | 207.9 | 553.7 | 778.9 | 403.3 | 668.7 | 200.6 | 813.8 | 487.1 | 99.8 | 242.4 | 241.2 | 158.2 | 95.3 | 234 | 225.1 | 146.6
384 | 221 | 466.4 | 186.56 | 218.0779 | 250.3 | 234.8 | 234.1 | 225.9 | 313.8 | 26.1 | 20.8 | 54.6 | 3 | 185.6 | 6.1 | 464.8 | 739.9 | 799.2 | 503.3 | 718.4 | 208.8 | 552.6 | 784.6 | 403.7 | 669.1 | 201.4 | 816.6 | 488.8 | 100.3 | 243.1 | 241.7 | 158.8 | 95.6 | 233.8 | 225.5 | 147.1
385 | 222 | 465.7 | 186.28 | 217.7506 | 251.6 | 235 | 234.6 | 225.7 | 318.9 | 26.2 | 20.8 | 54.7 | 2.9 | 172.2 | 6.2 | 467.6 | 739.1 | 794.1 | 505.1 | 718 | 209.7 | 554.2 | 782.6 | 404.1 | 669.7 | 202.3 | 819.1 | 491 | 100.7 | 243.8 | 242.1 | 159.7 | 95.9 | 233.9 | 225.9 | 147.7
386 | 223 | 466.9 | 186.76 | 218.3117 | 252.1 | 235.3 | 235.2 | 225.4 | 318.6 | 26.2 | 20.8 | 54.8 | 3.1 | 177 | 6 | 470.2 | 738.5 | 798.3 | 507.6 | 718.8 | 210.4 | 556.5 | 782.7 | 405 | 670.5 | 203.1 | 824.6 | 493 | 101.2 | 244 | 242.5 | 160.4 | 96.2 | 234.6 | 226.1 | 148.1
387 | 224 | 466.9 | 186.76 | 218.3117 | 251.6 | 235.9 | 235.7 | 225.7 | 314.8 | 26.3 | 20.8 | 55 | 3.4 | 184.3 | 5.6 | 472.7 | 737.4 | 799.7 | 510.2 | 718.5 | 211.3 | 562.9 | 788.8 | 406.2 | 671.8 | 204 | 822.9 | 495.8 | 101.6 | 243.9 | 243 | 160.7 | 96.5 | 235.4 | 226.3 | 148.6
388 | 225 | 465.8 | 186.32 | 217.7973 | 252.1 | 236.5 | 236.1 | 226.1 | 310.8 | 26.4 | 20.8 | 55.1 | 3.3 | 193 | 5.2 | 475.7 | 734.3 | 816.2 | 513.4 | 721.5 | 212.2 | 571 | 791.3 | 407.5 | 673.3 | 204.8 | 821.8 | 498.8 | 102.1 | 244.2 | 243.1 | 161.5 | 96.8 | 235.9 | 226.7 | 149.1
389 | 226 | 466.9 | 186.76 | 218.3117 | 252.8 | 237.1 | 236.1 | 226.1 | 308.2 | 26.4 | 20.8 | 55.3 | 3 | 194 | 4.8 | 479.1 | 733.6 | 821.1 | 516.9 | 723.7 | 213.1 | 571.7 | 791.9 | 408.8 | 674.3 | 205.8 | 822.5 | 501.8 | 102.5 | 244.4 | 243.4 | 161.8 | 97.1 | 236.4 | 227.1 | 149.7
390 | 227 | 466.7 | 186.68 | 218.2182 | 253 | 237 | 236.4 | 226.2 | 307.1 | 26.4 | 20.8 | 55.4 | 3 | 187.4 | 4.8 | 483.3 | 734.3 | 822.6 | 520.3 | 724.1 | 214 | 573.1 | 794.2 | 410.2 | 676.3 | 206.7 | 825.5 | 504.4 | 103 | 245.1 | 243.6 | 162.4 | 97.5 | 236.9 | 227.4 | 150.4
391 | 228 | 467.7 | 187.08 | 218.6857 | 252.5 | 237.6 | 237 | 226.6 | 309 | 26.5 | 20.8 | 55.4 | 2.9 | 186.1 | 5.2 | 487 | 732.3 | 830.5 | 523.7 | 725.5 | 214.9 | 580.7 | 582.9 | 412.1 | 678.7 | 207.6 | 824.1 | 507.2 | 103.4 | 245.7 | 243.8 | 163 | 97.8 | 236.8 | 227.9 | 150.9
392 | 229 | 467.2 | 186.88 | 218.452 | 252.6 | 239.1 | 237.2 | 226.8 | 308.4 | 26.6 | 20.8 | 55.4 | 2.6 | 186.9 | 6 | 490.4 | 733.2 | 830.7 | 527.1 | 728.2 | 215.9 | 583.1 | 462.1 | 414.3 | 680.3 | 208.4 | 822.4 | 510.2 | 103.9 | 246.1 | 244.1 | 163.7 | 98.1 | 236.7 | 228.4 | 151.4
393 | 230 | 467.8 | 187.12 | 218.7325 | 252.6 | 238.7 | 237.3 | 227.3 | 308.2 | 26.8 | 20.8 | 55.4 | 2.5 | 185.5 | 6.4 | 493.8 | 734.3 | 826 | 530.3 | 727.9 | 216.9 | 587.5 | 781 | 415.8 | 681.5 | 209.3 | 826.2 | 512.9 | 104.3 | 246.4 | 244.2 | 164.4 | 98.5 | 237 | 229.3 | 152.1
394 | 231 | 467.3 | 186.92 | 218.4987 | 251.9 | 240.1 | 237.8 | 227.8 | 303.7 | 26.8 | 20.8 | 55.5 | 2.8 | 174.4 | 6.1 | 497.6 | 733.4 | 833.8 | 533.8 | 730.3 | 217.8 | 569.6 | 408 | 417.2 | 682 | 210.2 | 826.6 | 515.2 | 104.7 | 246.6 | 244.5 | 164.9 | 98.8 | 237 | 230.4 | 152.8
395 | 232 | 468 | 187.2 | 218.826 | 252.1 | 240.1 | 238.2 | 227.9 | 304 | 26.9 | 20.8 | 55.6 | 3 | 179.3 | 5.9 | 501.7 | 732 | 843.3 | 537.4 | 733.4 | 218.7 | 550.5 | 558.3 | 419 | 683.7 | 211 | 825.8 | 517.7 | 105.1 | 246.6 | 244.5 | 165.3 | 99.2 | 237.3 | 231.5 | 153.5
396 | 233 | 468.1 | 187.24 | 218.8728 | 253.6 | 240.3 | 238.4 | 227.9 | 304.1 | 26.9 | 20.8 | 55.8 | 2.7 | 190 | 6.1 | 505.9 | 731.5 | 846.6 | 541.1 | 734.9 | 219.6 | 586.2 | 794.8 | 420 | 684.8 | 211.9 | 833.4 | 520 | 105.6 | 246.8 | 244.5 | 165.8 | 99.5 | 237.4 | 231.8 | 154.2
397 | 234 | 468.1 | 187.24 | 218.8728 | 253.3 | 239.8 | 239.1 | 228.2 | 304.5 | 27 | 20.8 | 56 | 2.7 | 199.1 | 6.6 | 509.9 | 730 | 852.8 | 544.4 | 738.9 | 220.5 | 591.8 | 308 | 422.5 | 687 | 212.7 | 831.5 | 521.6 | 106 | 247.5 | 244.8 | 166.6 | 99.8 | 238 | 232.1 | 154.7
398 | 235 | 465.4 | 186.16 | 217.6103 | 252.8 | 240.6 | 239.1 | 228.2 | 304.5 | 27.1 | 20.8 | 56.2 | 2.9 | 198.1 | 7 | 514.1 | 729.2 | 863.4 | 548 | 741.9 | 221.4 | 593.8 | 713.6 | 424 | 688.7 | 213.5 | 832.1 | 523.6 | 106.4 | 248 | 245 | 167.4 | 100.2 | 238.5 | 232.8 | 155.4
399 | 236 | 465.7 | 186.28 | 217.7506 | 252.4 | 241.7 | 238.7 | 228.9 | 305.1 | 27.1 | 20.8 | 56.4 | 3.1 | 190.3 | 7.3 | 518.1 | 731.4 | 866.3 | 552 | 745.7 | 222.4 | 593.8 | 796.2 | 423.9 | 689.8 | 214.3 | 830.9 | 525.3 | 106.9 | 248.2 | 245.3 | 167.9 | 100.5 | 238.6 | 233.1 | 156
400 | 237 | 466.6 | 186.64 | 218.1714 | 253.1 | 243.9 | 239.2 | 230 | 313.9 | 27.2 | 20.8 | 56.5 | 3.1 | 183.9 | 7.9 | 522 | 732.2 | 870.3 | 556.7 | 748.9 | 223.4 | 546.9 | 195.8 | 424.1 | 693 | 215.1 | 829.7 | 526.8 | 107.3 | 248.1 | 245.8 | 168.3 | 100.8 | 239.3 | 233.3 | 156.5
401 | 238 | 467.4 | 186.96 | 218.5455 | 253.3 | 245.1 | 239.8 | 231.2 | 317.5 | 27.4 | 20.8 | 56.6 | 3.5 | 176.3 | 7.7 | 526.5 | 731.7 | 866 | 561.9 | 749.6 | 224.4 | 611.5 | 806 | 424 | 695.9 | 215.9 | 829.1 | 528.5 | 107.8 | 248.1 | 246.4 | 168.7 | 101.1 | 239.7 | 234 | 157.1
402 | 239 | 466.8 | 186.72 | 218.2649 | 252.4 | 246.7 | 240 | 232.1 | 322.3 | 27.5 | 20.8 | 56.8 | 2.8 | 178.5 | 7.7 | 532 | 729.9 | 868.7 | 567.1 | 750.6 | 225.3 | 600.2 | 697.2 | 422.9 | 696.5 | 216.7 | 831.5 | 529.8 | 108.2 | 248.5 | 247 | 169.4 | 101.5 | 239.7 | 234.4 | 157.6
403 | 240 | 467.1 | 186.84 | 218.4052 | 252.1 | 247.5 | 239.9 | 233.5 | 326.2 | 27.6 | 20.8 | 56.9 | 3 | 185.1 | 7.5 | 537.5 | 728.2 | 867 | 571.3 | 753.2 | 226.2 | 435.4 | 276 | 421.3 | 698.4 | 217.5 | 832.6 | 531.3 | 108.6 | 249.1 | 247.5 | 169.9 | 101.8 | 240.2 | 234.6 | 158
404 | 241 | 467.8 | 187.12 | 218.7325 | 252.7 | 246.9 | 239.2 | 234.6 | 341 | 27.7 | 20.8 | 57 | 3.1 | 186.1 | 7.4 | 542.7 | 728.6 | 857.7 | 576.4 | 753.5 | 227.1 | 617.6 | 818.5 | 419.4 | 699.9 | 218.3 | 828.5 | 532.7 | 109.1 | 249.5 | 248.6 | 170.5 | 102.1 | 241.3 | 234.9 | 158.7
405 | 242 | 467.3 | 186.92 | 218.4987 | 253.2 | 248 | 239.1 | 236.2 | 353 | 27.8 | 20.8 | 57.1 | 3.2 | 186.5 | 7.4 | 549 | 728.2 | 852.7 | 581.4 | 754 | 228.1 | 518.3 | 545.2 | 417.4 | 700.4 | 219.1 | 832.7 | 533.8 | 109.6 | 250.1 | 249 | 171 | 102.5 | 242.4 | 235.4 | 159.3
406 | 243 | 468.1 | 187.24 | 218.8728 | 253.7 | 249.3 | 239.2 | 237.1 | 355.5 | 27.8 | 20.8 | 57.1 | 3 | 185.5 | 7.4 | 555.9 | 727.7 | 838.2 | 588.1 | 752.3 | 229 | 468 | 422.4 | 415.5 | 702 | 219.9 | 828.1 | 535.1 | 110.1 | 250.2 | 249.5 | 171.4 | 102.8 | 243.1 | 235.6 | 159.9
407 | 244 | 467.5 | 187 | 218.5922 | 255.4 | 251.6 | 238.9 | 237.7 | 353.5 | 27.9 | 20.8 | 57.2 | 3.3 | 175.9 | 7.3 | 562.7 | 729.5 | 827.8 | 594.9 | 752.8 | 230 | 619.6 | 827 | 413.4 | 703.3 | 220.8 | 825 | 535.7 | 110.6 | 250.1 | 250.3 | 172.1 | 103.1 | 243.5 | 235.5 | 160.4
408 | 245 | 467.8 | 187.12 | 218.7325 | 255.8 | 253.3 | 238.9 | 238.2 | 355.9 | 27.9 | 20.8 | 57.3 | 3.3 | 178.6 | 7.2 | 569.9 | 730.3 | 833.5 | 600.7 | 753.4 | 230.9 | 622.6 | 423.5 | 411 | 704.7 | 221.7 | 818.3 | 536.3 | 111.1 | 250.3 | 251 | 173 | 103.5 | 244.1 | 235.6 | 161
409 | 246 | 467.8 | 187.12 | 218.7325 | 256.7 | 254.6 | 239.4 | 237.9 | 354.5 | 27.9 | 20.8 | 57.4 | 3.6 | 175.2 | 6.9 | 577.5 | 729.6 | 845.5 | 606.4 | 755.6 | 231.9 | 621.1 | 583.7 | 409 | 707 | 222.6 | 822.5 | 537.5 | 111.6 | 250.4 | 251.4 | 173.8 | 103.9 | 244.3 | 235.8 | 161.4
410 | 247 | 467.9 | 187.16 | 218.7793 | 256.3 | 255.7 | 239.6 | 237.8 | 356.4 | 28.1 | 20.8 | 57.6 | 3.2 | 164.7 | 6.3 | 585.1 | 726.7 | 833.3 | 611.9 | 753.6 | 232.9 | 619.2 | 832.3 | 407.2 | 707.7 | 223.5 | 825.2 | 538.2 | 112.2 | 250.6 | 251.7 | 174.6 | 104.3 | 244.8 | 236 | 161.8
411 | 248 | 467.9 | 187.16 | 218.7793 | 256.1 | 255.9 | 239.4 | 237.8 | 358 | 28.2 | 20.7 | 57.8 | 3.2 | 154.6 | 5.9 | 591.7 | 724.9 | 818 | 616.2 | 752.7 | 233.8 | 595.1 | 269.7 | 405.3 | 708 | 224.4 | 820.4 | 538.8 | 112.7 | 251.6 | 252.2 | 175.3 | 104.7 | 245.2 | 236.3 | 162.3
412 | 249 | 467.2 | 186.88 | 218.452 | 256.5 | 254.3 | 239.6 | 238.2 | 362.4 | 28.3 | 20.8 | 57.9 | 3.3 | 157.1 | 5.7 | 598.6 | 726.3 | 807.7 | 622.3 | 750.8 | 234.8 | 615.6 | 733 | 403.5 | 708.4 | 225.3 | 812.6 | 539.3 | 113.3 | 252.6 | 252.8 | 176.4 | 105 | 245.1 | 236.5 | 162.7
413 | 250 | 467.2 | 186.88 | 218.452 | 256.6 | 254.6 | 240.8 | 239.2 | 366.3 | 28.3 | 20.7 | 58 | 2.9 | 162.3 | 5.5 | 606 | 728.2 | 795.3 | 627.9 | 749.8 | 235.7 | 613.9 | 826.4 | 401.7 | 708.7 | 226.2 | 817.8 | 539.9 | 113.9 | 253.3 | 253.8 | 177.6 | 105.4 | 244.8 | 236.5 | 163.3
414 | 251 | 466.7 | 186.68 | 218.2182 | 257.5 | 255.8 | 242.5 | 239.8 | 365.7 | 28.3 | 20.7 | 58 | 2.5 | 167.9 | 4.8 | 613.6 | 730.8 | 792.9 | 633.3 | 749.2 | 236.7 | 529.1 | 176.1 | 400.1 | 708.9 | 227.2 | 809.8 | 540.3 | 114.5 | 253.7 | 255.1 | 178.3 | 105.8 | 244.6 | 236.6 | 163.8
415 | 252 | 467.4 | 186.96 | 218.5455 | 259.1 | 256.6 | 243.2 | 240.6 | 365 | 28.3 | 20.7 | 58.1 | 2.9 | 168.5 | 4.1 | 621.8 | 731.3 | 798.5 | 638.4 | 750 | 237.7 | 613 | 833.8 | 398.6 | 710.5 | 228.3 | 808.6 | 540.6 | 115.2 | 254.2 | 256.2 | 178.9 | 106.2 | 244.7 | 236.8 | 164.3
416 | 253 | 466 | 186.4 | 217.8909 | 260.2 | 257.8 | 243.9 | 241.8 | 366 | 28.4 | 20.7 | 58.1 | 2.8 | 175.4 | 3.8 | 630.8 | 734.5 | 815.2 | 642.6 | 752.4 | 238.6 | 608.6 | 707.8 | 397.6 | 711 | 229.4 | 815.4 | 541 | 115.8 | 254.9 | 257.2 | 179.6 | 106.6 | 244.8 | 237.1 | 164.8
417 | 254 | 467.1 | 186.84 | 218.4052 | 260.7 | 259.1 | 245.2 | 242.9 | 367.3 | 28.4 | 20.7 | 58.2 | 2.9 | 187.2 | 3.7 | 638.7 | 736.7 | 822.1 | 647.2 | 752.5 | 239.5 | 602 | 305.4 | 396.3 | 711.9 | 230.5 | 818.4 | 541.5 | 116.4 | 255.7 | 258.1 | 179.7 | 107 | 245.1 | 237.8 | 165.4
418 | 255 | 466.3 | 186.52 | 218.0311 | 260.4 | 259.2 | 246.4 | 244.4 | 362.6 | 28.5 | 20.7 | 58.2 | 2.6 | 184.3 | 3.4 | 644.8 | 733 | 837.1 | 650.1 | 754.7 | 240.4 | 614 | 836.3 | 395.6 | 712.3 | 231.6 | 810.3 | 541.9 | 117.1 | 256.1 | 259 | 179.8 | 107.4 | 245.5 | 238.4 | 166
419 | 256 | 467.1 | 186.84 | 218.4052 | 259.9 | 259 | 247.1 | 245.1 | 355.5 | 28.5 | 20.7 | 58.2 | 2.4 | 177.2 | 3.4 | 648.7 | 728.7 | 846.9 | 651.6 | 757.2 | 241.4 | 619.5 | 580.5 | 394.6 | 714.3 | 232.8 | 801 | 542.9 | 117.8 | 256.7 | 259.9 | 180.1 | 107.9 | 247.6 | 239 | 166.6
420 | 257 | 466.4 | 186.56 | 218.0779 | 259.2 | 259.5 | 247.3 | 245.2 | 353 | 28.6 | 20.7 | 58.3 | 2.9 | 175.7 | 3.8 | 652.8 | 728.7 | 849.6 | 654.8 | 758.1 | 242.4 | 625.9 | 469.8 | 393.8 | 715.8 | 233.9 | 806.4 | 544.4 | 118.5 | 257.3 | 260.6 | 181.1 | 108.3 | 248.9 | 240.1 | 167.4
421 | 258 | 465.2 | 186.08 | 217.5168 | 259.2 | 260.1 | 247.6 | 245.7 | 351 | 28.8 | 20.7 | 58.3 | 3.1 | 176.3 | 4.3 | 657.6 | 730.9 | 847 | 660.3 | 758.1 | 243.3 | 629.6 | 843.5 | 392.7 | 716.2 | 235 | 807.5 | 546.2 | 119.2 | 258.1 | 261.3 | 182 | 108.6 | 249.1 | 240.7 | 168
422 | 259 | 466.6 | 186.64 | 218.1714 | 259.1 | 261.1 | 248.7 | 246.2 | 348.2 | 28.8 | 20.7 | 58.4 | 2.9 | 157.3 | 4.5 | 661.4 | 734.5 | 841.5 | 667 | 758 | 244.2 | 631.9 | 436.4 | 391.5 | 717.3 | 236.1 | 816.3 | 547.8 | 120 | 258.2 | 261.6 | 182.6 | 109.1 | 249.4 | 241.3 | 168.5
423 | 260 | 467.1 | 186.84 | 218.4052 | 259.1 | 261.4 | 248.9 | 247.1 | 346.2 | 29 | 20.7 | 58.4 | 3.4 | 164.6 | 4.8 | 664.5 | 737.6 | 832.6 | 678.6 | 755.9 | 245.1 | 637 | 479.2 | 390 | 716.7 | 237.2 | 823.7 | 549.2 | 120.7 | 258.3 | 262.1 | 183.1 | 109.5 | 249.3 | 241.6 | 169.2
424 | 261 | 466.4 | 186.56 | 218.0779 | 258.9 | 260.3 | 248.9 | 247.1 | 353.5 | 29 | 20.7 | 58.5 | 3.4 | 181.8 | 4.8 | 669.1 | 741.3 | 828.5 | 689.3 | 757.3 | 245.9 | 639.6 | 326.3 | 388.3 | 716.6 | 238.4 | 826.1 | 550.6 | 121.5 | 258.5 | 262.5 | 183.3 | 109.9 | 249.2 | 241.7 | 169.9
425 | 262 | 466.2 | 186.48 | 217.9844 | 259.4 | 259.9 | 248.4 | 246.8 | 354.7 | 29 | 20.7 | 58.5 | 3.4 | 152.6 | 4.4 | 674.7 | 744.4 | 828 | 697 | 757.4 | 246.6 | 645 | 293.2 | 386.8 | 716.3 | 239.6 | 830.2 | 551.7 | 122.3 | 258.7 | 263 | 183.5 | 110.3 | 248.8 | 242.3 | 170.3
426 | 263 | 465.7 | 186.28 | 217.7506 | 261.2 | 260.4 | 248.5 | 246.5 | 351.1 | 29.1 | 20.7 | 58.6 | 3.5 | 147.5 | 3.9 | 679.9 | 747.3 | 831.5 | 704.2 | 758.9 | 247.6 | 648 | 729.3 | 385 | 716.3 | 240.7 | 837.7 | 553.1 | 123 | 259 | 263.2 | 183.9 | 110.8 | 248.4 | 242.8 | 170.9
427 | 264 | 465 | 186 | 217.4233 | 261.7 | 261.9 | 249 | 246.8 | 349.3 | 29.3 | 20.7 | 58.6 | 3.1 | 162.2 | 3.8 | 685.6 | 748.8 | 833.4 | 712.1 | 758.6 | 248.7 | 652.9 | 815.6 | 383.5 | 717.3 | 241.8 | 840.1 | 554.3 | 123.8 | 258.9 | 263.4 | 184.4 | 111.2 | 248.2 | 243.6 | 171.7
428 | 265 | 464.3 | 185.72 | 217.096 | 261.7 | 263 | 248.6 | 246.5 | 348.6 | 29.4 | 20.7 | 58.7 | 3.4 | 178.7 | 4.7 | 690.3 | 749.5 | 835.1 | 714.5 | 758.3 | 249.8 | 658.4 | 225.1 | 382 | 718.2 | 242.6 | 835.7 | 555.4 | 124.5 | 259.1 | 263.6 | 184.6 | 111.6 | 248.6 | 244.3 | 172.3
429 | 266 | 465.5 | 186.2 | 217.6571 | 261.7 | 263 | 248.7 | 245.6 | 359.8 | 29.4 | 20.7 | 58.7 | 3 | 176.7 | 5.8 | 695.7 | 752.3 | 832.1 | 718.1 | 758.6 | 250.8 | 664.8 | 822.7 | 380.6 | 718.9 | 243.4 | 838.8 | 556.6 | 125.2 | 259.2 | 263.9 | 185.2 | 112 | 249.1 | 244.7 | 172.9
430 | 267 | 466.6 | 186.64 | 218.1714 | 261.3 | 262.5 | 248.1 | 245 | 363.3 | 29.5 | 20.7 | 58.8 | 3.4 | 158.9 | 5.6 | 699.5 | 753.6 | 831.8 | 723.8 | 757.9 | 252.6 | 666.9 | 708.6 | 379.2 | 719.3 | 244.1 | 841.8 | 557.9 | 125.9 | 259.3 | 264.6 | 185.7 | 112.4 | 249.9 | 245.1 | 173.6
431 | 268 | 466.6 | 186.64 | 218.1714 | 260.7 | 262 | 248.8 | 245.7 | 358.3 | 29.5 | 20.7 | 59 | 3 | 155.4 | 5.1 | 702.8 | 751.8 | 832.2 | 724.5 | 759.5 | 254.1 | 668.9 | 361.9 | 378 | 720.9 | 244.9 | 830 | 559.3 | 126.6 | 259.4 | 264.7 | 186.2 | 112.8 | 251.1 | 245.7 | 174.2
432 | 269 | 467.2 | 186.88 | 218.452 | 261.1 | 263.2 | 249.3 | 246.2 | 354.3 | 29.6 | 20.7 | 59.1 | 3.2 | 194.6 | 5.1 | 706.6 | 751 | 834.7 | 725.1 | 759.4 | 255.5 | 669.5 | 831.6 | 377 | 723.2 | 245.7 | 828.1 | 560.7 | 127.2 | 259.6 | 265 | 186.7 | 113.2 | 251.6 | 246.2 | 174.8
433 | 270 | 467.1 | 186.84 | 218.4052 | 260.6 | 263.9 | 249 | 246.2 | 352.5 | 29.7 | 20.7 | 59.2 | 3.3 | 182 | 5.3 | 708.4 | 750.3 | 842.7 | 728.3 | 759.2 | 256.5 | 672.5 | 834.6 | 376.1 | 721.6 | 246.6 | 830.1 | 562.1 | 127.9 | 259.7 | 265.1 | 187.3 | 113.7 | 251.6 | 247 | 175.4
434 | 271 | 466.4 | 186.56 | 218.0779 | 260.5 | 262.9 | 249.7 | 246.8 | 348.3 | 29.7 | 20.7 | 59.3 | 3 | 189.6 | 5.4 | 712.5 | 748.5 | 854.7 | 726.6 | 760.8 | 257.5 | 673.4 | 833.9 | 375.3 | 723.4 | 247.5 | 826.5 | 563.3 | 128.5 | 259.7 | 265 | 187.9 | 114.1 | 251.7 | 248 | 176.1
435 | 272 | 465.8 | 186.32 | 217.7973 | 261.4 | 263 | 249.8 | 247.4 | 345.6 | 29.8 | 20.7 | 59.5 | 2.9 | 211.6 | 4.9 | 715.2 | 746.7 | 858.7 | 723.5 | 763.5 | 258.5 | 675.7 | 838.6 | 374.8 | 724.7 | 248.3 | 819.2 | 564.6 | 129.1 | 259.7 | 265.1 | 188.5 | 114.5 | 252.4 | 248.4 | 176.7
436 | 273 | 466.1 | 186.44 | 217.9376 | 261.5 | 262.7 | 250.3 | 248.4 | 346.6 | 30 | 20.7 | 59.6 | 2.9 | 210 | 4 | 718.5 | 746.2 | 860.6 | 720.8 | 764.3 | 259.4 | 679.1 | 843.1 | 374.2 | 725.8 | 249.1 | 817.8 | 566 | 129.7 | 259.7 | 265 | 189 | 115 | 253.5 | 248.9 | 177.2
437 | 274 | 468 | 187.2 | 218.826 | 260.6 | 263.2 | 250.8 | 249.3 | 346.5 | 30.2 | 20.7 | 59.6 | 2.9 | 186 | 3.8 | 722.4 | 746.6 | 857.3 | 720.2 | 764.3 | 260.2 | 682 | 845.2 | 373.7 | 725.2 | 249.9 | 817 | 567.4 | 130.4 | 260 | 264.8 | 189.5 | 115.4 | 254.9 | 249.2 | 177.8
438 | 275 | 465.1 | 186.04 | 217.47 | 259.6 | 263.3 | 251.5 | 249.6 | 346 | 30.3 | 20.7 | 59.7 | 3.4 | 172.8 | 4.1 | 728.9 | 748.7 | 849.9 | 722.2 | 763.9 | 261.1 | 689.1 | 845.2 | 373.2 | 725.8 | 250.7 | 817.2 | 569.1 | 131 | 260.1 | 264.9 | 190 | 115.9 | 256 | 249.8 | 178.4
439 | 276 | 466 | 186.4 | 217.8909 | 258.2 | 262.9 | 252 | 249.9 | 351.2 | 30.4 | 20.7 | 59.8 | 3.9 | 188.7 | 4.3 | 735.9 | 752.2 | 818.4 | 725.2 | 760.1 | 261.9 | 687.4 | 848.1 | 372.7 | 725.7 | 251.7 | 823.6 | 570.6 | 131.6 | 260.5 | 265.3 | 190.4 | 116.3 | 256.7 | 250.4 | 178.9
440 | 277 | 466.8 | 186.72 | 218.2649 | 257.3 | 262.9 | 253 | 250.2 | 365.2 | 30.4 | 20.7 | 59.8 | 3.7 | 193.7 | 4.6 | 737 | 755.4 | 789.4 | 730.5 | 756.7 | 262.7 | 684.2 | 845.6 | 372.1 | 725.5 | 252.6 | 818.3 | 571.7 | 132.1 | 261.4 | 266.7 | 191.1 | 116.8 | 257.4 | 250.7 | 179.5
441 | 278 | 466.5 | 186.6 | 218.1246 | 256.9 | 264.4 | 254.6 | 250.2 | 393.2 | 30.4 | 20.7 | 59.8 | 3.4 | 190 | 4.6 | 741.8 | 758.5 | 785.9 | 732.1 | 755.7 | 263.4 | 682.3 | 842.4 | 371.6 | 726.1 | 253.4 | 809.5 | 572.9 | 132.7 | 262.2 | 267.7 | 192 | 117.3 | 258.2 | 250.9 | 180
442 | 279 | 467.3 | 186.92 | 218.4987 | 258.5 | 268.1 | 255.1 | 250.8 | 405.2 | 30.4 | 20.7 | 59.8 | 3.5 | 190.5 | 4.7 | 745.7 | 760.7 | 770.7 | 733.1 | 752.7 | 264.2 | 680.8 | 836.1 | 371.1 | 725.4 | 254.3 | 806.9 | 573.8 | 133.3 | 263.4 | 268.6 | 193 | 117.8 | 258.9 | 251.5 | 180.7
443 | 280 | 466.5 | 186.6 | 218.1246 | 259.4 | 270.3 | 255.2 | 251.7 | 427.5 | 30.5 | 20.7 | 59.9 | 3.9 | 183.5 | 4.4 | 748.7 | 763.7 | 750.8 | 736.5 | 750.8 | 264.9 | 680.9 | 828.2 | 370.6 | 725.1 | 255.1 | 800.3 | 574.6 | 133.8 | 264.3 | 270.1 | 194.2 | 118.3 | 259.6 | 252 | 181.4
444 | 281 | 466.5 | 186.6 | 218.1246 | 259.9 | 272.7 | 256.2 | 253.3 | 443.7 | 30.5 | 20.7 | 60.1 | 3.4 | 181.1 | 4.6 | 751.9 | 766.1 | 744.9 | 739.4 | 749.8 | 265.7 | 674.1 | 831.3 | 370.1 | 726.9 | 255.9 | 804.6 | 575.7 | 134.5 | 265.3 | 272 | 194.9 | 118.8 | 260 | 252.8 | 181.9
445 | 282 | 466.6 | 186.64 | 218.1714 | 258.5 | 273.5 | 258 | 254.7 | 447.3 | 30.6 | 20.6 | 60.3 | 3.3 | 187.7 | 4.7 | 754 | 767.6 | 748.7 | 743.1 | 747.4 | 266.6 | 670.3 | 834.2 | 369.9 | 728.1 | 256.7 | 810.8 | 576.8 | 135 | 266.2 | 273 | 195.6 | 119.3 | 260.5 | 254.2 | 182.5
446 | 283 | 468.3 | 187.32 | 218.9663 | 256.8 | 273.1 | 259.7 | 256 | 440.8 | 30.7 | 20.6 | 60.4 | 3.6 | 191.9 | 4.3 | 755.8 | 769.7 | 755.1 | 745.3 | 744.9 | 267.3 | 668.7 | 830.4 | 369.3 | 728 | 257.5 | 813.8 | 577.8 | 135.6 | 267.1 | 273.4 | 196.3 | 119.8 | 260.6 | 255.2 | 183.1
447 | 284 | 466.9 | 186.76 | 218.3117 | 257.1 | 272.3 | 260.3 | 257 | 433 | 30.8 | 20.6 | 60.6 | 3.5 | 189.1 | 3.9 | 756.9 | 769.8 | 762.8 | 750.1 | 745.1 | 268.1 | 668.5 | 826.3 | 369.1 | 728.2 | 258.2 | 810.6 | 579.2 | 136.3 | 267.8 | 275.9 | 197.3 | 120.3 | 260.6 | 255.7 | 183.7
448 | 285 | 466.5 | 186.6 | 218.1246 | 258.2 | 271.7 | 260.3 | 257.5 | 420 | 30.9 | 20.6 | 60.7 | 3.4 | 179.8 | 3.8 | 757.6 | 769.5 | 763.1 | 753.3 | 743.9 | 268.8 | 672.3 | 819.3 | 368.8 | 727.2 | 259 | 810.2 | 581.3 | 136.9 | 268.5 | 275.8 | 197.9 | 120.8 | 260.3 | 256 | 184.2
449 | 286 | 468 | 187.2 | 218.826 | 259.7 | 271.4 | 260.4 | 257.9 | 405.5 | 31 | 20.6 | 60.9 | 3.4 | 177.9 | 3.6 | 759.2 | 769.7 | 756.7 | 755 | 743.4 | 269.5 | 667.3 | 825.4 | 368.5 | 728.5 | 259.9 | 810.3 | 583.6 | 137.5 | 269.2 | 275.6 | 198.1 | 121.3 | 260 | 255.9 | 184.6
450 | 287 | 468.2 | 187.28 | 218.9195 | 260.5 | 270.4 | 260 | 258 | 402 | 31 | 20.6 | 61 | 2.8 | 177.7 | 3.4 | 759.7 | 769.4 | 743.4 | 755.8 | 741.4 | 270.2 | 667.2 | 827 | 368.3 | 729.2 | 260.7 | 813.7 | 586.2 | 138 | 269.7 | 275.6 | 198.3 | 121.8 | 260 | 255.9 | 185.1
451 | 288 | 468 | 187.2 | 218.826 | 259.7 | 271.1 | 260.1 | 258 | 399.9 | 31 | 20.6 | 61.1 | 2.8 | 180.4 | 3.6 | 764.5 | 768.2 | 732.6 | 752.1 | 739.7 | 270.8 | 662.8 | 828.3 | 368.2 | 729.5 | 261.5 | 811.9 | 588.4 | 138.6 | 270.2 | 275.7 | 198.9 | 122.3 | 259.8 | 256.5 | 185.6
452 | 289 | 468.7 | 187.48 | 219.1533 | 258.7 | 272.1 | 260.9 | 257.5 | 393.6 | 31.1 | 20.6 | 61.3 | 2.6 | 182.1 | 3.7 | 766.3 | 768.5 | 729.8 | 749.8 | 739 | 271.5 | 662.3 | 830 | 368 | 729.1 | 262.3 | 803.8 | 590.6 | 139.2 | 270.6 | 275.8 | 199.8 | 122.7 | 259.7 | 256.9 | 186.1
453 | 290 | 468.5 | 187.4 | 219.0598 | 259.5 | 272.2 | 260.7 | 257.2 | 390.1 | 31.2 | 20.6 | 61.4 | 2.8 | 179.2 | 3.5 | 767.1 | 769.3 | 739.7 | 751 | 738.3 | 272.2 | 661.1 | 832.6 | 367.8 | 729.3 | 263.1 | 804 | 593 | 139.7 | 271.5 | 275.9 | 200.2 | 123.2 | 260 | 257 | 186.7
454 | 291 | 469.1 | 187.64 | 219.3403 | 260.7 | 272.6 | 261 | 257.3 | 388.2 | 31.3 | 20.6 | 61.5 | 3.1 | 185.3 | 3.3 | 767.9 | 770.6 | 761.4 | 753.4 | 742.1 | 272.9 | 663.9 | 834.9 | 367.8 | 731.2 | 263.8 | 809.8 | 595.1 | 140.3 | 272.1 | 276.5 | 200.6 | 123.6 | 260.6 | 256.9 | 187.3
455 | 292 | 468.5 | 187.4 | 219.0598 | 261.8 | 272.8 | 260.9 | 258.3 | 388.1 | 31.4 | 20.6 | 61.6 | 3.2 | 190.9 | 3 | 767.5 | 772.1 | 780 | 757.2 | 745.4 | 273.7 | 663.1 | 835.7 | 368 | 732.5 | 264.5 | 811.3 | 597.1 | 140.8 | 272.3 | 277 | 201.7 | 124.1 | 260.6 | 257.1 | 187.8
456 | 293 | 466.7 | 186.68 | 218.2182 | 261.4 | 272.8 | 261.2 | 258.4 | 387.3 | 31.5 | 20.6 | 61.7 | 2.8 | 191.3 | 2.6 | 767.9 | 771.2 | 779.5 | 757 | 745.4 | 274.3 | 659 | 831.2 | 368.1 | 732.5 | 265.3 | 810.3 | 598.9 | 141.3 | 272.4 | 277.3 | 202.4 | 124.5 | 260.3 | 257.7 | 188.4
457 | 294 | 469.1 | 187.64 | 219.3403 | 261.7 | 273.7 | 261.3 | 258.7 | 389.7 | 31.4 | 20.6 | 61.8 | 2.9 | 191.7 | 2.4 | 769.3 | 770.6 | 783.3 | 758.1 | 745.8 | 274.9 | 657.1 | 828.6 | 367.9 | 732.2 | 266.1 | 807.7 | 600.2 | 141.9 | 272.9 | 277.8 | 202.9 | 125 | 260.2 | 257.8 | 189
458 | 295 | 466.7 | 186.68 | 218.2182 | 264 | 275.8 | 262 | 258.7 | 397.9 | 31.3 | 20.6 | 61.9 | 3.1 | 191.2 | 2.8 | 770 | 769.8 | 778.7 | 760.6 | 744.9 | 275.5 | 660.1 | 831.2 | 367.9 | 732.5 | 266.8 | 808.1 | 601.3 | 142.4 | 273.5 | 278.3 | 203.8 | 125.5 | 260 | 257.9 | 189.5
459 | 296 | 464.3 | 185.72 | 217.096 | 265.6 | 277.7 | 262.3 | 258.8 | 400.1 | 31.3 | 20.6 | 62.1 | 2.9 | 190.5 | 3.5 | 773.2 | 769.3 | 775 | 763.1 | 744.9 | 276 | 663 | 827.2 | 367.9 | 731.6 | 267.6 | 807.8 | 602.5 | 143 | 273.9 | 278.7 | 204.3 | 125.9 | 260 | 257.8 | 190
460 | 297 | 463.8 | 185.52 | 216.8622 | 266 | 277.9 | 261.9 | 259.6 | 395.4 | 31.4 | 20.6 | 62.2 | 2.8 | 176 | 4.2 | 777.2 | 768.6 | 778.6 | 762.2 | 744.9 | 276.5 | 657.7 | 829.2 | 368 | 731.7 | 268.3 | 800 | 604.3 | 143.5 | 274 | 279.1 | 204.4 | 126.4 | 260 | 257.6 | 190.4
461 | 298 | 465.2 | 186.08 | 217.5168 | 265.6 | 277.8 | 262.4 | 259.7 | 386.8 | 31.6 | 20.6 | 62.3 | 3.3 | 174.7 | 4.5 | 776.7 | 769.6 | 765.5 | 762.8 | 743.4 | 277.1 | 651.1 | 827.3 | 368.2 | 731.9 | 269.1 | 795.3 | 607.3 | 144.1 | 274.2 | 279.6 | 204.7 | 126.9 | 259.9 | 257.4 | 190.8
462 | 299 | 465.4 | 186.16 | 217.6103 | 266.5 | 277.3 | 263.1 | 259.6 | 383.4 | 31.8 | 20.6 | 62.4 | 3.2 | 175.8 | 4.6 | 775.3 | 770.1 | 749.5 | 763.7 | 738.8 | 277.8 | 640.9 | 820.4 | 368.1 | 729.7 | 270 | 774.9 | 610.6 | 144.6 | 274.6 | 280.1 | 205.4 | 127.3 | 260.1 | 257.5 | 191.2
463 | 300 | 464.4 | 185.76 | 217.1427 | 266.6 | 277 | 263.6 | 259.5 | 380.4 | 31.8 | 20.6 | 62.5 | 3 | 173.5 | 4.6 | 778.9 | 770.8 | 752.5 | 768.1 | 738.4 | 278.3 | 639.6 | 815.3 | 367.8 | 727.1 | 270.9 | 762 | 613.6 | 145.2 | 275.2 | 280.9 | 205.9 | 127.8 | 260.5 | 257.8 | 191.7
464 | 301 | 465.8 | 186.32 | 217.7973 | 265.7 | 277 | 264.2 | 259.8 | 380.7 | 31.9 | 20.6 | 62.6 | 3.2 | 155.5 | 4.5 | 782.9 | 770.3 | 774.8 | 769.9 | 741.6 | 278.8 | 639.6 | 818.8 | 367.6 | 728.2 | 276.1 | 771.3 | 616.2 | 145.8 | 275.6 | 281.6 | 206.4 | 128.2 | 260.6 | 258.3 | 192.4
465 | 302 | 466.1 | 186.44 | 217.9376 | 265.5 | 277.2 | 264.8 | 260 | 384.9 | 31.9 | 20.6 | 62.7 | 3.2 | 151.4 | 4.1 | 783.5 | 769.9 | 780.7 | 770.3 | 741.6 | 279.5 | 640.6 | 820.8 | 367.6 | 728.6 | 286.3 | 771.1 | 618.1 | 146.3 | 276.1 | 282.2 | 206.9 | 128.7 | 260.7 | 258.6 | 193.1
466 | 303 | 468.1 | 187.24 | 218.8728 | 265.8 | 276.8 | 265.3 | 260.4 | 387.1 | 32 | 20.6 | 62.8 | 3.1 | 152.7 | 3.8 | 784.6 | 770.9 | 792 | 769.8 | 744.4 | 280.1 | 647.9 | 820.3 | 367.6 | 729.2 | 292.2 | 779.9 | 619.4 | 146.9 | 276.5 | 282.8 | 207.4 | 129.1 | 261.2 | 258.5 | 193.6
467 | 304 | 468 | 187.2 | 218.826 | 265.8 | 276.2 | 266 | 260.5 | 386.9 | 32 | 20.6 | 62.9 | 3.3 | 161.5 | 3.9 | 788.6 | 774 | 801.3 | 769.7 | 746.5 | 280.8 | 651.6 | 820 | 368.2 | 730.7 | 296.5 | 784.5 | 620 | 147.5 | 276.8 | 283.2 | 208.1 | 129.6 | 261.3 | 258.6 | 194
468 | 305 | 464.5 | 185.8 | 217.1895 | 265.3 | 276.5 | 266.7 | 260.5 | 399.7 | 32.1 | 20.6 | 62.9 | 3.6 | 170.2 | 3.9 | 790.3 | 776.1 | 808 | 769.5 | 749.9 | 281.5 | 655.3 | 820.1 | 369 | 731.1 | 299.9 | 789 | 620.5 | 148.1 | 277.3 | 283.6 | 208.7 | 130 | 261.3 | 259.1 | 194.5
469 | 306 | 466.7 | 186.68 | 218.2182 | 264.6 | 277.1 | 266.6 | 260.8 | 403 | 32.2 | 20.5 | 63 | 3.4 | 174.3 | 4.1 | 793.6 | 775.8 | 819.3 | 770 | 751.5 | 282.1 | 651.3 | 817.8 | 369.6 | 731.3 | 302.7 | 794.4 | 621.4 | 148.7 | 277.5 | 283.8 | 209.4 | 130.5 | 261.4 | 259.5 | 195.1
470 | 307 | 467.2 | 186.88 | 218.452 | 264.5 | 277.2 | 266.5 | 261.1 | 398.1 | 32.2 | 20.6 | 63.1 | 3.9 | 174.9 | 4.4 | 797.7 | 779.5 | 833.7 | 769.8 | 754.2 | 282.7 | 648 | 815.5 | 370.2 | 732.3 | 305.2 | 798 | 622.3 | 149.2 | 277.5 | 283.9 | 209.8 | 130.9 | 261.4 | 259.4 | 195.5
471 | 308 | 466.7 | 186.68 | 218.2182 | 263.7 | 277.1 | 266.5 | 261 | 389.1 | 32.3 | 20.5 | 63.2 | 3.4 | 175.9 | 4.6 | 801.6 | 777.5 | 840.6 | 769.6 | 756.4 | 283.2 | 645.5 | 817.9 | 370.9 | 734 | 307.6 | 801.3 | 623.4 | 149.8 | 277.5 | 283.9 | 210 | 131.4 | 261.4 | 259.4 | 195.9
472 | 309 | 467.3 | 186.92 | 218.4987 | 262.8 | 277.3 | 266.6 | 261 | 382.3 | 32.3 | 20.5 | 63.4 | 3 | 177.8 | 4.6 | 803.9 | 776.7 | 847.8 | 769.8 | 760.6 | 283.9 | 645.8 | 821.3 | 371.8 | 735.7 | 309.7 | 802.5 | 624.9 | 150.4 | 277.3 | 284.1 | 210.3 | 131.8 | 261.4 | 259.2 | 196.5
473 | 310 | 466.7 | 186.68 | 218.2182 | 262 | 275.8 | 266.2 | 261 | 376.5 | 32.3 | 20.6 | 63.4 | 2.7 | 179.7 | 4.6 | 807.1 | 777.6 | 850.7 | 770.8 | 763.1 | 284.6 | 643.8 | 819.6 | 372.9 | 736.7 | 311.8 | 798.6 | 626.8 | 150.9 | 277.1 | 284 | 210.5 | 132.2 | 261.8 | 259.2 | 196.9
474 | 311 | 466.1 | 186.44 | 217.9376 | 260.7 | 274.2 | 265.7 | 260.9 | 377.8 | 32.3 | 20.5 | 63.4 | 3.1 | 164.9 | 4.4 | 806.4 | 779.4 | 846.8 | 771.8 | 763.5 | 285.2 | 640.3 | 821.6 | 373.6 | 738.2 | 313.6 | 800.5 | 628.5 | 151.5 | 277 | 284.1 | 211.2 | 132.7 | 261.8 | 259.2 | 197.3
475 | 312 | 467.3 | 186.92 | 218.4987 | 259.8 | 275 | 265.3 | 260.7 | 386.4 | 32.4 | 20.5 | 63.5 | 3.7 | 148.4 | 3.9 | 810 | 782.8 | 854.4 | 772.7 | 767.9 | 285.8 | 637.3 | 818.5 | 374.1 | 737.6 | 315.4 | 797.5 | 630.2 | 152 | 277 | 284.1 | 211.8 | 133.1 | 262 | 259.4 | 197.8
476 | 313 | 467.2 | 186.88 | 218.452 | 258.5 | 275.8 | 264.5 | 260.4 | 384.8 | 32.4 | 20.5 | 63.6 | 3.6 | 155 | 3.5 | 815.6 | 782.1 | 858 | 772.4 | 769.4 | 286.4 | 640.6 | 821 | 374.7 | 739.1 | 317.4 | 795.2 | 632.1 | 152.6 | 277 | 284 | 212.5 | 133.5 | 262.1 | 259.4 | 198.2
477 | 314 | 468 | 187.2 | 218.826 | 256.6 | 276.6 | 264.8 | 260.2 | 386.9 | 32.4 | 20.5 | 63.7 | 3.3 | 176.5 | 3.4 | 821.9 | 779.9 | 862.3 | 771.6 | 771.7 | 287 | 644.1 | 826 | 375.6 | 740.7 | 319.1 | 795 | 633.7 | 153.1 | 277 | 283.5 | 212.9 | 134 | 262.5 | 259.6 | 198.6
478 | 315 | 466.6 | 186.64 | 218.1714 | 255.2 | 276.5 | 265 | 259.8 | 390.6 | 32.5 | 20.5 | 63.7 | 2.9 | 190 | 3.2 | 824.1 | 777.1 | 866.3 | 770.4 | 775.2 | 287.5 | 642.3 | 828.2 | 376.6 | 742.5 | 320.7 | 792.7 | 635.4 | 153.6 | 276.8 | 283.1 | 213.2 | 134.4 | 262.8 | 259.9 | 199
479 | 316 | 467.5 | 187 | 218.5922 | 254.1 | 276.3 | 264.7 | 260 | 396.4 | 32.5 | 20.5 | 63.7 | 3.5 | 188.1 | 2.9 | 823.6 | 777.3 | 863.7 | 771.1 | 776.1 | 288.1 | 639.6 | 829.6 | 377.5 | 743.4 | 322.4 | 793.8 | 636.6 | 154.1 | 276.8 | 283.1 | 213.8 | 134.9 | 263.4 | 259.9 | 199.4
480 | 317 | 468.4 | 187.36 | 219.013 | 253.8 | 276.2 | 265 | 260 | 399.4 | 32.5 | 20.5 | 63.8 | 3.2 | 189.9 | 3.1 | 819.3 | 779.2 | 849 | 772.4 | 775.5 | 288.7 | 636.7 | 832.2 | 378.2 | 743.7 | 324.1 | 798.1 | 637.6 | 154.6 | 277 | 283.2 | 214 | 135.4 | 263.7 | 259.8 | 199.8
481 | 318 | 468.3 | 187.32 | 218.9663 | 253.9 | 276.2 | 265.2 | 260.2 | 410.3 | 32.4 | 20.5 | 63.9 | 3 | 186.1 | 3.6 | 817.9 | 780.5 | 842 | 774.6 | 774.4 | 289.2 | 640.5 | 833.7 | 378.9 | 744.8 | 325.7 | 801.2 | 638.8 | 155.1 | 277.1 | 283.2 | 214.5 | 135.9 | 264.2 | 259.8 | 200.3
482 | 319 | 467.6 | 187.04 | 218.639 | 255.1 | 276 | 265.6 | 261 | 419.6 | 32.4 | 20.5 | 64 | 3.1 | 184.3 | 4.2 | 820.2 | 779.9 | 848.3 | 776 | 776.9 | 289.7 | 644.2 | 829.3 | 379.6 | 744.8 | 327.3 | 802.9 | 639.8 | 155.6 | 277.4 | 283.4 | 215 | 136.4 | 264.7 | 259.9 | 200.7
483 | 320 | 468.3 | 187.32 | 218.9663 | 255.3 | 277.1 | 266.3 | 261.7 | 426.2 | 32.5 | 20.5 | 64 | 3.5 | 193.8 | 5.1 | 822.6 | 785.3 | 855 | 777.2 | 781.2 | 290.4 | 656.5 | 826.1 | 380.2 | 745.6 | 328.9 | 804.2 | 640.3 | 156.1 | 277.6 | 283.8 | 215.7 | 136.8 | 264.7 | 260.1 | 201.2
484 | 321 | 468.9 | 187.56 | 219.2468 | 255.1 | 278.8 | 266.9 | 262.5 | 426.7 | 32.5 | 20.5 | 64.1 | 3.5 | 191.3 | 5.5 | 822.9 | 787 | 857.2 | 779.3 | 782.5 | 291.1 | 650.1 | 820 | 380.9 | 744.9 | 330.5 | 810.6 | 639.8 | 156.5 | 277.8 | 284.2 | 216.3 | 137.3 | 264.5 | 260.4 | 201.7
485 | 322 | 468.3 | 187.32 | 218.9663 | 255.6 | 279.1 | 266.8 | 263.7 | 427.8 | 32.6 | 20.5 | 64.2 | 3.5 | 199.8 | 6 | 825.9 | 784.5 | 844.8 | 780.8 | 782.8 | 291.7 | 656.7 | 823.1 | 381.5 | 746.7 | 332.2 | 810.1 | 639.5 | 157 | 278.2 | 284.6 | 216.8 | 137.9 | 264.9 | 260.6 | 202.2
486 | 323 | 468.5 | 187.4 | 219.0598 | 255.6 | 278.2 | 266.7 | 264.6 | 422.2 | 32.7 | 20.5 | 64.3 | 3.2 | 211.6 | 5.6 | 829.7 | 783.8 | 849.5 | 781.2 | 785.9 | 292.3 | 655.8 | 824.1 | 382.8 | 748 | 333.9 | 808.3 | 639.9 | 157.4 | 278.6 | 284.9 | 217 | 138.4 | 265.7 | 261 | 202.7
487 | 324 | 469 | 187.6 | 219.2936 | 255.7 | 278 | 266.8 | 265.3 | 416.3 | 32.9 | 20.5 | 64.4 | 3.1 | 198.2 | 5.2 | 832.3 | 784.8 | 859.7 | 781.1 | 789.6 | 293 | 652.7 | 823.1 | 383.8 | 748.1 | 335.7 | 807.6 | 640.4 | 157.9 | 279.2 | 285.1 | 217.4 | 138.9 | 266.3 | 261.5 | 203.3
488 | 325 | 469.4 | 187.76 | 219.4806 | 255.5 | 278.8 | 267.4 | 266.1 | 416.5 | 33 | 20.5 | 64.4 | 3.4 | 202.8 | 5.5 | 833.9 | 784.5 | 863.4 | 781.3 | 789.9 | 293.6 | 651.9 | 821.4 | 384.8 | 748.5 | 337.6 | 808.2 | 640.8 | 158.3 | 279.5 | 285.3 | 218.1 | 139.4 | 266.8 | 261.7 | 203.9
489 | 326 | 469 | 187.6 | 219.2936 | 255.1 | 279.2 | 267.6 | 266.6 | 409.9 | 33.1 | 20.5 | 64.5 | 3.7 | 199.4 | 5.8 | 838.6 | 782.6 | 861.8 | 780.6 | 791.2 | 294.1 | 646.2 | 821.2 | 385.6 | 749 | 339.3 | 806.6 | 640.9 | 158.8 | 279.6 | 285.2 | 218.7 | 139.8 | 266.9 | 261.7 | 204.3
490 | 327 | 469.3 | 187.72 | 219.4339 | 254.7 | 279.5 | 267.2 | 267.2 | 403.9 | 33.3 | 20.5 | 64.6 | 3.6 | 201.6 | 6.1 | 839.4 | 781.8 | 866.3 | 780.2 | 792.8 | 294.7 | 644.8 | 818.9 | 386 | 748.1 | 341.1 | 804.8 | 641.2 | 159.2 | 279.6 | 285.2 | 219 | 140.4 | 266.8 | 262.2 | 204.8
491 | 328 | 468.6 | 187.44 | 219.1066 | 254.6 | 280.6 | 267 | 267.6 | 427.5 | 33.4 | 20.5 | 64.7 | 3.6 | 207.8 | 6 | 833.7 | 784.9 | 847.4 | 780.4 | 793.1 | 295.3 | 644.6 | 816.4 | 386.4 | 748.9 | 342.9 | 807.7 | 641.2 | 159.6 | 279.6 | 285.4 | 219.3 | 140.9 | 266.6 | 262.5 | 205.2
492 | 329 | 468.4 | 187.36 | 219.013 | 255.4 | 281.5 | 266.5 | 267.5 | 447.2 | 33.4 | 20.5 | 64.7 | 3.7 | 204.3 | 5.9 | 830.9 | 788.6 | 840.5 | 780.3 | 794.6 | 295.9 | 650.1 | 816.8 | 387 | 749.5 | 344.8 | 812.5 | 640.9 | 160.1 | 280 | 285.8 | 219.8 | 141.4 | 266.6 | 262.6 | 205.8
493 | 330 | 469 | 187.6 | 219.2936 | 256 | 282.3 | 267.2 | 268.1 | 448.3 | 33.5 | 20.5 | 64.9 | 3.5 | 201.3 | 5.5 | 830.3 | 789.7 | 842.7 | 780.5 | 796.7 | 296.6 | 650 | 812.5 | 387.5 | 749.2 | 346.6 | 814.9 | 641.1 | 160.5 | 280.3 | 286.3 | 220.2 | 141.9 | 267 | 262.7 | 206.2
494 | 331 | 468.8 | 187.52 | 219.2001 | 255.8 | 282.8 | 267.9 | 269.4 | 451.5 | 33.5 | 20.5 | 65 | 3.8 | 208.1 | 5.1 | 833.5 | 790.4 | 849.2 | 779.9 | 799.8 | 297.2 | 656.3 | 810.5 | 388.2 | 749.6 | 348.5 | 811.2 | 641.6 | 160.9 | 280.5 | 286.7 | 220.8 | 142.4 | 267.5 | 262.9 | 206.7
495 | 332 | 468.5 | 187.4 | 219.0598 | 256.3 | 284 | 268.7 | 270.8 | 447.1 | 33.6 | 20.5 | 65.1 | 3.7 | 195.1 | 5 | 838 | 788.5 | 857.3 | 779.4 | 802.1 | 297.9 | 662.1 | 811.2 | 389.1 | 750.5 | 350.3 | 804.8 | 642.5 | 161.3 | 281 | 286.9 | 222.1 | 142.9 | 268.8 | 263.8 | 207.3
496 | 333 | 468.8 | 187.52 | 219.2001 | 256.7 | 285.1 | 268.6 | 271.5 | 434.9 | 33.6 | 20.5 | 65.2 | 3.3 | 195.8 | 5.7 | 839.4 | 785.4 | 854.1 | 780.7 | 802 | 298.5 | 658.5 | 809.8 | 389.9 | 750.5 | 352 | 802.2 | 643.1 | 161.7 | 281.3 | 287.1 | 222.8 | 143.3 | 270.1 | 264.9 | 208
497 | 334 | 468.3 | 187.32 | 218.9663 | 256.6 | 284.4 | 268.3 | 271.7 | 423.5 | 33.7 | 20.5 | 65.4 | 3.5 | 213.8 | 6 | 839 | 783.3 | 853.3 | 783.3 | 800.4 | 299.1 | 662.5 | 814.3 | 390.7 | 751.7 | 353.6 | 806.5 | 644.5 | 162.1 | 281.5 | 287.3 | 223.1 | 143.8 | 270.4 | 265.5 | 208.6
498 | 335 | 468.2 | 187.28 | 218.9195 | 256.5 | 283.6 | 268.4 | 271.8 | 410.3 | 33.8 | 20.4 | 65.5 | 3.6 | 219.5 | 5.8 | 834 | 784.4 | 840.7 | 788.1 | 797.8 | 299.6 | 657 | 807.8 | 391.5 | 750 | 355.1 | 811.4 | 646.3 | 162.5 | 281.6 | 287.5 | 223.6 | 144.3 | 270.4 | 266 | 209
499 | 336 | 468.5 | 187.4 | 219.0598 | 257.2 | 283.6 | 268.3 | 271.7 | 399.3 | 34 | 20.4 | 65.7 | 3.5 | 246.7 | 5.1 | 840.3 | 783.3 | 845.7 | 792.9 | 796.6 | 300 | 655.2 | 801.3 | 391.9 | 749.1 | 356.6 | 810.9 | 648.2 | 162.9 | 281.6 | 287.6 | 223.7 | 144.7 | 270.5 | 266.1 | 209.5
500 | 337 | 468.7 | 187.48 | 219.1533 | 256.9 | 283.7 | 268.6 | 271.7 | 389.4 | 34.1 | 20.4 | 65.8 | 3.8 | 253.1 | 4.6 | 845.1 | 783.4 | 849.7 | 794.2 | 798.4 | 300.4 | 649.1 | 800.4 | 392.3 | 748.8 | 358.2 | 812.1 | 650.2 | 163.4 | 281.5 | 287.4 | 223.7 | 145.2 | 270.7 | 266.1 | 210
501 | 338 | 468.6 | 187.44 | 219.1066 | 256 | 283.1 | 268.5 | 271.3 | 385 | 34.2 | 20.4 | 66 | 3.5 | 228.7 | 3.9 | 850.4 | 782 | 860.1 | 794.6 | 801.6 | 300.8 | 646.3 | 804.4 | 392.4 | 749.6 | 359.8 | 807.4 | 652.3 | 163.8 | 281.3 | 287.5 | 223.9 | 145.7 | 270.9 | 266.2 | 210.6
502 | 339 | 468.1 | 187.24 | 218.8728 | 255.9 | 283 | 268.1 | 270.9 | 394.5 | 34.3 | 20.4 | 66 | 3.7 | 247.2 | 3.9 | 850.1 | 781.1 | 857.8 | 794.7 | 802.5 | 301.3 | 647.5 | 804.5 | 393 | 750.8 | 361.4 | 808 | 654.4 | 164.2 | 281.5 | 287.9 | 224.2 | 146.2 | 271.3 | 266.3 | 211
503 | 340 | 468.8 | 187.52 | 219.2001 | 254.8 | 282.6 | 267.8 | 270.4 | 395.4 | 34.4 | 20.4 | 66.1 | 3.3 | 205.3 | 4.9 | 847.8 | 782.1 | 851.4 | 794.2 | 801.8 | 302 | 647.4 | 811.5 | 393.9 | 752.1 | 363 | 810.5 | 656.1 | 164.6 | 281.8 | 288.2 | 224.5 | 146.6 | 272.1 | 266.7 | 211.4
504 | 341 | 469.4 | 187.76 | 219.4806 | 252.8 | 283.4 | 268.7 | 269.9 | 403.1 | 34.4 | 20.4 | 66.2 | 3.7 | 220.6 | 5.8 | 839 | 783.4 | 838.5 | 796 | 800.4 | 302.7 | 646 | 814 | 394.9 | 752.4 | 364.9 | 813 | 657.4 | 165.1 | 282.2 | 288.3 | 224.8 | 147.1 | 272.2 | 266.8 | 211.9
505 | 342 | 468 | 187.2 | 218.826 | 251.1 | 284.7 | 269.3 | 270 | 414.5 | 34.4 | 20.4 | 66.2 | 3.5 | 232.7 | 5.4 | 837.3 | 784.9 | 831.6 | 797.8 | 798.4 | 303.2 | 650 | 809.5 | 395.3 | 752.3 | 366.5 | 817.3 | 659.2 | 165.5 | 282.6 | 288.7 | 225.4 | 147.6 | 272.6 | 266.8 | 212.4
506 | 343 | 468.9 | 187.56 | 219.2468 | 251.1 | 285.8 | 269.6 | 270 | 418.3 | 34.5 | 20.4 | 66.3 | 3.8 | 200.2 | 4.7 | 840.5 | 783 | 828.4 | 799.4 | 797.9 | 303.8 | 652.7 | 812.6 | 396.1 | 752.2 | 368.2 | 817.6 | 662.1 | 165.9 | 283.1 | 289 | 226 | 148 | 273.1 | 266.7 | 212.8
507 | 344 | 468 | 187.2 | 218.826 | 251.4 | 285.3 | 270.8 | 270.4 | 411.1 | 34.6 | 20.4 | 66.3 | 3.2 | 184.8 | 4.8 | 845.8 | 779.8 | 826.7 | 801.3 | 794.2 | 304.3 | 650 | 811 | 396.5 | 750.4 | 369.6 | 818.8 | 665.3 | 166.4 | 283.3 | 289.3 | 226.5 | 148.5 | 273.2 | 266.6 | 213.2
508 | 345 | 468.7 | 187.48 | 219.1533 | 252 | 285 | 270.8 | 270.6 | 412.4 | 34.7 | 20.4 | 66.3 | 3.1 | 212.7 | 5.5 | 847.4 | 778.7 | 841 | 804 | 795.7 | 304.6 | 649 | 815.5 | 396.7 | 751.2 | 370.9 | 818.6 | 668.1 | 166.8 | 283.8 | 290 | 227.4 | 149 | 273.5 | 266.7 | 213.6
509 | 346 | 469.7 | 187.88 | 219.6209 | 251.7 | 284.7 | 271.1 | 270.8 | 411.9 | 34.8 | 20.4 | 66.3 | 3.7 | 213.4 | 5.4 | 849.6 | 777.2 | 835.9 | 804.6 | 795.2 | 305.2 | 646.5 | 818.2 | 397.2 | 752.4 | 372.1 | 817.8 | 671.2 | 167.2 | 284.4 | 290.7 | 228.2 | 149.5 | 274 | 266.8 | 214.1
510 | 347 | 468.7 | 187.48 | 219.1533 | 252 | 284.8 | 271.6 | 271.4 | 415.5 | 34.9 | 20.4 | 66.4 | 4 | 175.4 | 5.3 | 839.3 | 776.9 | 806.5 | 805.6 | 790.6 | 305.8 | 647.6 | 813.8 | 397.7 | 751.9 | 373.2 | 819.9 | 673.2 | 167.7 | 285 | 291.5 | 229 | 150 | 274.3 | 267.1 | 214.6
511 | 348 | 468.6 | 187.44 | 219.1066 | 253.9 | 285.5 | 272.8 | 272.5 | 420.6 | 35.1 | 20.4 | 66.5 | 3.8 | 159.5 | 4.4 | 830.2 | 776.2 | 788.7 | 807.2 | 785.6 | 306.2 | 647.9 | 801.1 | 397.5 | 749.6 | 374.3 | 815.8 | 674.3 | 168.1 | 285.6 | 292.4 | 229.7 | 150.5 | 274.8 | 267.1 | 215.1
512 | 349 | 468.8 | 187.52 | 219.2001 | 255.8 | 286.8 | 274.2 | 273.4 | 423 | 35.1 | 20.4 | 66.5 | 4 | 181.7 | 4 | 838.4 | 777.3 | 801.8 | 808 | 786.3 | 306.8 | 647.7 | 799.4 | 397.6 | 750.6 | 375.3 | 815.4 | 674.4 | 168.5 | 286 | 293.2 | 230.1 | 150.9 | 275.1 | 267.3 | 215.6
513 | 350 | 468.7 | 187.48 | 219.1533 | 257.1 | 287.1 | 275.3 | 274.7 | 421.8 | 35.1 | 20.4 | 66.5 | 3.6 | 187.3 | 3.6 | 841.7 | 776.2 | 802.3 | 809.3 | 786.7 | 307.4 | 646.1 | 800.9 | 398.1 | 751 | 376.3 | 812 | 674.5 | 169 | 286.6 | 294 | 230.7 | 151.4 | 275.5 | 267.4 | 216.2
514 | 351 | 469.3 | 187.72 | 219.4339 | 259.4 | 287.9 | 275.7 | 275.7 | 421.7 | 35.2 | 20.4 | 66.6 | 3.8 | 157.3 | 3.8 | 833 | 776.5 | 793.4 | 811.5 | 782.4 | 307.9 | 642 | 795.1 | 398 | 749.9 | 377.3 | 810.4 | 674.2 | 169.4 | 287.6 | 295.3 | 231.6 | 151.9 | 275.6 | 267.7 | 216.7
515 | 352 | 468.3 | 187.32 | 218.9663 | 261.4 | 288.4 | 276 | 276.5 | 420.3 | 35.3 | 20.4 | 66.7 | 3.9 | 166.3 | 4.1 | 832.2 | 776.5 | 796.2 | 812.5 | 779.6 | 308.4 | 641.1 | 790.4 | 397.9 | 749 | 378.1 | 808.1 | 673.9 | 169.9 | 288.3 | 296.5 | 232.3 | 152.4 | 275.7 | 268 | 217.1
516 | 353 | 468.3 | 187.32 | 218.9663 | 262.8 | 287.6 | 277.2 | 277.3 | 418.2 | 35.3 | 20.4 | 66.9 | 3.6 | 198 | 4.2 | 834.5 | 774.7 | 787.6 | 812 | 776.5 | 308.9 | 638.3 | 791.5 | 398 | 749.2 | 379 | 808.2 | 674.3 | 170.4 | 289.5 | 297.3 | 233.1 | 152.9 | 276.3 | 268.6 | 217.6
517 | 354 | 468.1 | 187.24 | 218.8728 | 264.1 | 289.5 | 278.5 | 277.9 | 417.3 | 35.4 | 20.4 | 67 | 3.9 | 211.7 | 3.6 | 835.2 | 774.2 | 785.3 | 812.4 | 775.9 | 309.3 | 634.4 | 790.6 | 398 | 748.3 | 379.7 | 806.6 | 673.6 | 170.8 | 290.2 | 298.6 | 233.4 | 153.4 | 276.7 | 269 | 218.1
518 | 355 | 468.4 | 187.36 | 219.013 | 265.2 | 292 | 278.9 | 278.5 | 413.8 | 35.4 | 20.4 | 67.1 | 3.5 | 180.2 | 3.6 | 837.6 | 774.2 | 789.2 | 814.4 | 776 | 309.8 | 633.4 | 787.7 | 398.2 | 747.3 | 380.5 | 805.8 | 673.2 | 171.3 | 290.8 | 299.6 | 233.5 | 153.9 | 276.7 | 269.5 | 218.7
519 | 356 | 468.1 | 187.24 | 218.8728 | 266.4 | 291.7 | 279.7 | 279.4 | 409.3 | 35.4 | 20.4 | 67.1 | 3.7 | 189.6 | 5.1 | 847.6 | 771.8 | 797.7 | 813.9 | 776.7 | 310.2 | 632.8 | 787.4 | 398.1 | 746.1 | 381.2 | 801 | 674.8 | 171.9 | 291.3 | 300.4 | 233.8 | 154.4 | 277.3 | 269.9 | 219.1
520 | 357 | 468 | 187.2 | 218.826 | 267.2 | 290.6 | 279.2 | 279.4 | 406.9 | 35.5 | 20.4 | 67.1 | 3.8 | 188.9 | 6.1 | 853.1 | 770.3 | 813.9 | 813.6 | 780.3 | 310.7 | 629.5 | 788.5 | 398.4 | 746.1 | 381.8 | 798.8 | 677.2 | 172.4 | 291.7 | 300.6 | 234.3 | 154.9 | 277.9 | 270.3 | 219.6
521 | 358 | 468.4 | 187.36 | 219.013 | 266.4 | 290 | 278.3 | 279.6 | 400.8 | 35.7 | 20.4 | 67.1 | 3.5 | 167.9 | 6 | 857 | 769.2 | 829 | 812.9 | 785.7 | 311.3 | 624.8 | 782.6 | 399 | 745.4 | 382.3 | 798.9 | 678.9 | 173 | 291.8 | 300.3 | 234.5 | 155.4 | 277.9 | 270.6 | 220.2
522 | 359 | 468.5 | 187.4 | 219.0598 | 266 | 289.8 | 277.7 | 279.6 | 395 | 35.8 | 20.4 | 67.1 | 2.9 | 186.6 | 5.6 | 856.7 | 768.8 | 835.5 | 812.6 | 788.5 | 311.8 | 624.9 | 781.2 | 399.5 | 745.1 | 382.8 | 796.2 | 679.6 | 173.6 | 291.7 | 300.1 | 234.7 | 155.9 | 277.7 | 270.6 | 220.6
523 | 360 | 468.6 | 187.44 | 219.1066 | 266.3 | 288.3 | 277 | 278.9 | 396.1 | 35.9 | 20.4 | 67.1 | 3.3 | 187.3 | 6 | 858.4 | 771.5 | 842.6 | 813.4 | 792 | 312.4 | 622 | 777.9 | 400 | 744.3 | 383.2 | 792.8 | 679.4 | 174.1 | 291.5 | 299.8 | 234.9 | 156.4 | 277.5 | 270.9 | 221.1
524 | 361 | 468.5 | 187.4 | 219.0598 | 265.8 | 286.8 | 276.1 | 278.7 | 392.2 | 35.9 | 20.4 | 67.1 | 3.6 | 177.3 | 6.6 | 858.8 | 774.1 | 841.6 | 814.9 | 792.5 | 312.9 | 622.2 | 772.3 | 400.7 | 743.6 | 383.6 | 790.5 | 678.9 | 174.7 | 291.2 | 299.5 | 235 | 156.9 | 277.1 | 271.1 | 221.6
525 | 362 | 467.5 | 187 | 218.5922 | 264.3 | 286.3 | 275.4 | 278.1 | 389.2 | 35.9 | 20.4 | 67.1 | 3.8 | 184.6 | 6.8 | 858.6 | 775.1 | 843.7 | 816.3 | 793.4 | 313.3 | 620.2 | 775.4 | 401.2 | 743.7 | 383.8 | 790.1 | 677.9 | 175.2 | 291 | 298.9 | 235.2 | 157.4 | 276.5 | 271.2 | 222
526 | 363 | 467.8 | 187.12 | 218.7325 | 263.3 | 286.6 | 274.5 | 277.3 | 394.1 | 35.9 | 20.4 | 67.2 | 3.3 | 197.5 | 7 | 860.5 | 775.4 | 852.6 | 817.7 | 797.5 | 313.9 | 617.5 | 774.2 | 401.8 | 743.5 | 384.1 | 790.4 | 676.9 | 175.8 | 290.7 | 298.1 | 235.4 | 157.9 | 276.1 | 271.4 | 222.4
527 | 364 | 469.9 | 187.96 | 219.7144 | 263.4 | 286.7 | 273.7 | 276.9 | 399.1 | 35.8 | 20.4 | 67.3 | 3.5 | 200.2 | 6.5 | 859.1 | 775.4 | 850.6 | 819.9 | 796.8 | 314.4 | 615.3 | 772.5 | 402.1 | 743.2 | 384.3 | 791.1 | 676.5 | 176.3 | 290.5 | 297.5 | 235.8 | 158.3 | 275.6 | 271.3 | 222.7
528 | 365 | 470.9 | 188.36 | 220.182 | 262.3 | 287.9 | 273.3 | 276.5 | 400.6 | 35.8 | 20.4 | 67.4 | 3.8 | 190.9 | 5.8 | 862.4 | 773.2 | 851.2 | 820.4 | 796.8 | 315 | 613.9 | 771.7 | 402.5 | 743.1 | 384.5 | 789 | 676.8 | 176.8 | 290.3 | 297.3 | 236.1 | 158.8 | 275.3 | 271.2 | 222.9
529 | 366 | 469.9 | 187.96 | 219.7144 | 260.2 | 288.3 | 273.6 | 275.8 | 402.2 | 35.8 | 20.4 | 67.6 | 4 | 174.1 | 5.7 | 860.5 | 774.4 | 848.1 | 821.3 | 796.8 | 315.5 | 615.3 | 776.9 | 402.8 | 743.7 | 384.6 | 791.4 | 677.1 | 177.3 | 290.2 | 297.3 | 236.6 | 159.2 | 274.9 | 271.2 | 223.1
530 | 367 | 469.8 | 187.92 | 219.6677 | 259.4 | 288.5 | 273.9 | 275.5 | 409.6 | 35.9 | 20.4 | 67.7 | 3.8 | 179.4 | 5.5 | 864.1 | 774.4 | 856.2 | 820.4 | 797.6 | 315.8 | 614.4 | 780.8 | 402.9 | 744 | 384.8 | 793.5 | 677.8 | 177.8 | 290.4 | 297.2 | 237.2 | 159.6 | 274.8 | 271.1 | 223.4
531 | 368 | 469.3 | 187.72 | 219.4339 | 259.5 | 288.9 | 274 | 275.8 | 416 | 35.9 | 20.4 | 67.8 | 3.9 | 191.3 | 5.4 | 866.3 | 776.2 | 858.6 | 819.1 | 799.3 | 316.3 | 615.5 | 784.7 | 403.5 | 744.5 | 384.9 | 796.7 | 679.3 | 178.3 | 290.6 | 297.5 | 237.5 | 160 | 274.9 | 271.2 | 223.8
532 | 369 | 467.9 | 187.16 | 218.7793 | 259.8 | 289.5 | 274.3 | 276.2 | 412.5 | 35.9 | 20.3 | 67.8 | 4.1 | 191.5 | 5.6 | 866.1 | 778.6 | 859 | 819.8 | 800 | 316.8 | 618 | 785.4 | 403.8 | 745.2 | 385 | 799.7 | 680.5 | 178.7 | 291.1 | 297.6 | 238.1 | 160.4 | 275.1 | 271.5 | 224.2
533 | 370 | 469 | 187.6 | 219.2936 | 259.9 | 291 | 274.5 | 276.3 | 411 | 35.8 | 20.3 | 67.9 | 3.5 | 189.4 | 5.3 | 866.4 | 778.9 | 861.3 | 819.7 | 801.2 | 317.5 | 622.1 | 789.2 | 404.5 | 746.3 | 385.1 | 799.8 | 680.7 | 179.2 | 291.3 | 297.8 | 238.7 | 160.8 | 275.2 | 272.2 | 224.8
534 | 371 | 468.8 | 187.52 | 219.2001 | 260.8 | 292.7 | 274.3 | 276.1 | 414.1 | 35.8 | 20.3 | 67.9 | 3.9 | 189.4 | 5 | 866.1 | 779.4 | 865.6 | 819.1 | 803.5 | 318.1 | 621 | 790.3 | 405.3 | 746.9 | 385.2 | 800 | 680.1 | 179.6 | 291.5 | 298.2 | 239.1 | 161.2 | 275.1 | 272.5 | 225.1
535 | 372 | 469.5 | 187.8 | 219.5274 | 261.2 | 294 | 273.9 | 276 | 415 | 35.8 | 20.3 | 67.9 | 3.7 | 194.6 | 4.7 | 868 | 776.9 | 863.9 | 818 | 805.1 | 318.7 | 624.5 | 789.8 | 406.4 | 747 | 385.3 | 796.8 | 679.7 | 180 | 291.4 | 298.3 | 239.2 | 161.6 | 275 | 273 | 225.6
536 | 373 | 469.6 | 187.84 | 219.5741 | 261.1 | 294.2 | 274.2 | 275 | 405.7 | 35.8 | 20.3 | 67.9 | 3.8 | 204.6 | 4.4 | 864.4 | 773.6 | 855.7 | 817.7 | 802.9 | 319.3 | 629.4 | 790.5 | 407.5 | 746.1 | 385.5 | 794.9 | 680.8 | 180.4 | 291.2 | 298.2 | 239.4 | 162 | 275 | 273.7 | 226.1
537 | 374 | 468.3 | 187.32 | 218.9663 | 261.1 | 293.4 | 274.3 | 274.7 | 397 | 35.9 | 20.3 | 68 | 3.6 | 208.8 | 4.1 | 863.9 | 770.4 | 853.5 | 818 | 803.3 | 319.6 | 630.2 | 789.3 | 407.7 | 744.5 | 385.6 | 792.8 | 683.3 | 180.8 | 291 | 298.2 | 239.7 | 162.4 | 274.9 | 274.5 | 226.6
538 | 375 | 467.7 | 187.08 | 218.6857 | 261.8 | 292 | 274.4 | 275.4 | 390.7 | 36 | 20.3 | 68 | 2.8 | 217.4 | 4.1 | 863.9 | 768.5 | 854.6 | 817.4 | 804.8 | 320.1 | 632.4 | 789.6 | 408.5 | 745.4 | 385.7 | 786.6 | 684.3 | 181.2 | 290.9 | 298.2 | 240 | 162.8 | 275.1 | 274.9 | 227
539 | 376 | 468.3 | 187.32 | 218.9663 | 261.9 | 290.4 | 274.9 | 275.5 | 384.1 | 36.1 | 20.3 | 68 | 3.4 | 222.2 | 4.1 | 863.3 | 770.3 | 859.2 | 818.1 | 805.8 | 320.7 | 634.2 | 787.3 | 409.4 | 745.3 | 385.8 | 785.2 | 684.8 | 181.6 | 290.9 | 297.9 | 240.6 | 163.2 | 275.4 | 275.2 | 227.4
540 | 377 | 468 | 187.2 | 218.826 | 262.1 | 289.1 | 275.2 | 276 | 380.2 | 36.2 | 20.3 | 68.2 | 3.6 | 214.9 | 4.2 | 863.3 | 772.9 | 860.5 | 820.5 | 808.1 | 321.1 | 632.5 | 789.1 | 409.8 | 745.2 | 386 | 787.4 | 685 | 182 | 291 | 297.7 | 241 | 163.5 | 275.9 | 275.8 | 227.9
541 | 378 | 468.3 | 187.32 | 218.9663 | 263.6 | 289.6 | 275.2 | 276.5 | 377.5 | 36.1 | 20.3 | 68.3 | 3.6 | 204.7 | 4.6 | 864.3 | 773.1 | 860.2 | 821.7 | 807.5 | 321.6 | 630.5 | 783.6 | 410 | 744.1 | 386.1 | 786.9 | 685.7 | 182.4 | 291.1 | 297.7 | 241.2 | 163.9 | 275.9 | 276.3 | 228.4
542 | 379 | 468.2 | 187.28 | 218.9195 | 265.2 | 290.1 | 274.9 | 276.9 | 375 | 36.1 | 20.3 | 68.4 | 3.7 | 203.2 | 4.7 | 870.4 | 774.4 | 867.5 | 821.3 | 810.6 | 322 | 629.6 | 783.6 | 410.5 | 744 | 386.2 | 786.7 | 686.3 | 182.8 | 291 | 297.3 | 241.7 | 164.3 | 275.9 | 276.7 | 228.9
543 | 380 | 468.6 | 187.44 | 219.1066 | 266.5 | 289.6 | 274.8 | 276.7 | 384.4 | 36.2 | 20.3 | 68.5 | 4.3 | 200.3 | 4.7 | 873.6 | 776.1 | 867.8 | 820.6 | 813 | 322.5 | 639.8 | 779.8 | 410.9 | 743.7 | 386.2 | 788.9 | 686 | 183.2 | 290.9 | 296.8 | 242.1 | 164.7 | 275.9 | 276.8 | 229.1
544 | 381 | 468.1 | 187.24 | 218.8728 | 266.7 | 289.5 | 274.1 | 276.4 | 386.2 | 36.3 | 20.3 | 68.5 | 4 | 204.9 | 4.6 | 870.4 | 776.1 | 862.8 | 820.4 | 813 | 323 | 648.3 | 777.7 | 411.3 | 742.9 | 386.3 | 790.7 | 686.2 | 183.6 | 291 | 296.6 | 242.5 | 165.1 | 275.9 | 276.5 | 229.3
545 | 382 | 468.2 | 187.28 | 218.9195 | 264.9 | 289.9 | 273.2 | 276.3 | 389.7 | 36.3 | 20.3 | 68.6 | 3.6 | 211 | 5.2 | 871.6 | 775.1 | 862.3 | 820.1 | 814 | 323.4 | 646.4 | 782.2 | 411.6 | 743.9 | 386.3 | 792.9 | 686.2 | 184 | 291.2 | 296.4 | 242.9 | 165.4 | 276.2 | 276.1 | 229.6
546 | 383 | 469.8 | 187.92 | 219.6677 | 264 | 290.8 | 272.8 | 276.4 | 388.8 | 36.4 | 20.3 | 68.7 | 3.6 | 215.2 | 6.2 | 873.6 | 771.7 | 858 | 819.3 | 812.4 | 323.9 | 652.2 | 789.2 | 412.4 | 743.9 | 386.3 | 793.4 | 687.3 | 184.4 | 291.1 | 296.4 | 243.1 | 165.8 | 276.3 | 276 | 230
547 | 384 | 469.9 | 187.96 | 219.7144 | 262.9 | 289.8 | 272.2 | 276.7 | 383.8 | 36.4 | 20.3 | 68.9 | 3.6 | 204.4 | 6.6 | 875.5 | 768.8 | 861.6 | 817.3 | 813 | 324.3 | 650.4 | 793.6 | 412.8 | 744.4 | 386.3 | 789.4 | 688.4 | 184.8 | 290.8 | 296.3 | 243.4 | 166.2 | 277 | 276 | 230.4
548 | 385 | 469.5 | 187.8 | 219.5274 | 261.7 | 286.9 | 272.3 | 276.9 | 381.5 | 36.4 | 20.3 | 69.1 | 3.6 | 223.4 | 5.8 | 878.8 | 767.1 | 867.2 | 815.2 | 815.2 | 324.8 | 647.1 | 796.4 | 413.3 | 745.1 | 386.3 | 787.3 | 689.3 | 185.1 | 290.7 | 296.3 | 244 | 166.5 | 277.2 | 276 | 230.7
549 | 386 | 469.7 | 187.88 | 219.6209 | 261.2 | 284.2 | 272.2 | 277 | 385.1 | 36.4 | 20.3 | 69.3 | 3.5 | 221.6 | 4.9 | 879 | 766 | 864.2 | 814.3 | 814.6 | 325.2 | 643.9 | 798.7 | 413.4 | 744.2 | 386.3 | 787 | 690.3 | 185.5 | 290.7 | 296.6 | 244.3 | 166.9 | 277.3 | 276.2 | 231
550 | 387 | 469.2 | 187.68 | 219.3871 | 262.1 | 283.5 | 272 | 277 | 386 | 36.4 | 20.3 | 69.6 | 3.8 | 186.7 | 5.4 | 878.2 | 765.9 | 866.7 | 814.4 | 813.9 | 325.6 | 645.9 | 804.4 | 413.5 | 745.6 | 386.4 | 788.8 | 692 | 185.9 | 290.7 | 297 | 244.6 | 167.3 | 277.7 | 276.2 | 231.4
551 | 388 | 469 | 187.6 | 219.2936 | 262.3 | 284 | 272.3 | 277.3 | 387 | 36.4 | 20.3 | 69.8 | 3.9 | 205.9 | 5.5 | 876.8 | 765.9 | 864.7 | 815.9 | 813.9 | 326.2 | 641.9 | 804.5 | 414.3 | 745.8 | 386.5 | 790 | 695.1 | 186.2 | 290.8 | 297 | 245 | 167.6 | 277.9 | 276.4 | 231.7
552 | 389 | 468.6 | 187.44 | 219.1066 | 261.6 | 284.8 | 273 | 277.7 | 380.7 | 36.4 | 20.3 | 70 | 3.5 | 209.1 | 5.9 | 874.9 | 764.4 | 857.5 | 816.6 | 811.7 | 326.6 | 635.3 | 795.8 | 414.2 | 742.6 | 386.7 | 788.4 | 698.3 | 186.6 | 290.8 | 297 | 245.3 | 168 | 277.8 | 276.8 | 232
553 | 390 | 468.9 | 187.56 | 219.2468 | 262.2 | 284.3 | 273.5 | 278.5 | 373 | 36.4 | 20.3 | 70.2 | 3 | 200 | 6.1 | 872.2 | 763 | 851.8 | 815.7 | 810.9 | 326.8 | 634.4 | 793.7 | 414 | 741.5 | 386.9 | 784.7 | 700.9 | 187 | 290.5 | 296.9 | 245.5 | 168.3 | 277.6 | 277.1 | 232.4
554 | 391 | 469.2 | 187.68 | 219.3871 | 262.9 | 282.5 | 272.6 | 278.4 | 369.1 | 36.3 | 20.3 | 70.3 | 3.4 | 197.3 | 6 | 868.4 | 763.4 | 851.2 | 816.5 | 808.6 | 327.2 | 634.8 | 796.6 | 414 | 742.1 | 387 | 786.9 | 703.4 | 187.3 | 290.4 | 296.9 | 245.8 | 168.7 | 277.4 | 277.2 | 232.8
555 | 392 | 469.7 | 187.88 | 219.6209 | 263.6 | 281.2 | 271.6 | 278 | 370.5 | 36.2 | 20.3 | 70.3 | 3.6 | 197.9 | 5.9 | 869.5 | 764.8 | 857.1 | 816.7 | 810.3 | 327.7 | 634.3 | 801.8 | 414.6 | 743.5 | 387.2 | 791.6 | 706.2 | 187.7 | 290.3 | 296.9 | 246.3 | 169.1 | 277.4 | 276.9 | 232.9
556 | 393 | 469.6 | 187.84 | 219.5741 | 263.7 | 281.4 | 271.5 | 277 | 371.3 | 36.2 | 20.3 | 70.3 | 3.2 | 198.8 | 5.7 | 870.6 | 764.5 | 862.7 | 816.9 | 812.3 | 328.3 | 631.9 | 799.4 | 415 | 743.4 | 387.4 | 794.4 | 708.4 | 188.1 | 290.2 | 297.1 | 246.8 | 169.4 | 277.1 | 276.9 | 233.3
557 | 394 | 468.4 | 187.36 | 219.013 | 262.5 | 281.6 | 272.7 | 276.3 | 373.5 | 36.3 | 20.3 | 70.3 | 3.3 | 198.4 | 5.5 | 871.9 | 764.1 | 866 | 816.5 | 812.5 | 328.9 | 629.8 | 799.2 | 415.5 | 742.9 | 387.6 | 794 | 710.1 | 188.5 | 290.2 | 297.1 | 247.1 | 169.8 | 277 | 276.8 | 233.6
558 | 395 | 469.6 | 187.84 | 219.5741 | 263.7 | 281.6 | 273 | 275.9 | 377.1 | 36.4 | 20.3 | 70.3 | 3.2 | 201 | 5.2 | 873 | 765.2 | 868.6 | 816.4 | 812.6 | 329.4 | 629.8 | 802.2 | 416 | 743.5 | 387.8 | 800.5 | 711.8 | 188.9 | 290.3 | 297.1 | 247.5 | 170.2 | 277.2 | 276.5 | 233.9
559 | 396 | 468.5 | 187.4 | 219.0598 | 265.3 | 282 | 272.3 | 275.9 | 381 | 36.4 | 20.3 | 70.3 | 3.1 | 203.4 | 5.3 | 873.9 | 767 | 870.3 | 816.7 | 813.5 | 329.9 | 634.5 | 803.2 | 416.6 | 744.2 | 388.1 | 805.4 | 712.9 | 189.3 | 290.4 | 297.3 | 248.1 | 170.5 | 277.4 | 276.4 | 234.2
560 | 397 | 469 | 187.6 | 219.2936 | 266.4 | 282.7 | 271.5 | 275.6 | 379.6 | 36.4 | 20.3 | 70.2 | 2.9 | 191.5 | 5.3 | 875.9 | 767.2 | 866.1 | 816.6 | 811.6 | 330.3 | 630.5 | 801.7 | 416.9 | 743.2 | 388.4 | 808.3 | 713.8 | 189.7 | 290.7 | 297.4 | 248.6 | 170.9 | 277.5 | 276.3 | 234.5
561 | 398 | 466.1 | 186.44 | 217.9376 | 267.4 | 283.2 | 271.8 | 275.4 | 377.9 | 36.4 | 20.3 | 70.2 | 2.9 | 186.8 | 5 | 873.4 | 767.6 | 859.7 | 817.2 | 809.4 | 330.7 | 626.5 | 793.7 | 417.3 | 743 | 388.7 | 810.8 | 714 | 190.1 | 291.2 | 297.9 | 249.3 | 171.3 | 277.7 | 276 | 234.8
562 | 399 | 468.6 | 187.44 | 219.1066 | 268.7 | 283.9 | 272.9 | 275.1 | 377.7 | 36.5 | 20.3 | 70.2 | 2.9 | 194.5 | 4.9 | 866.4 | 768.1 | 845.5 | 818.8 | 805.3 | 331.1 | 630.7 | 795.3 | 417.9 | 743.5 | 389 | 810.2 | 714 | 190.4 | 291.6 | 298.3 | 249.7 | 171.7 | 278.2 | 275.9 | 235.2
563 | 400 | 467.4 | 186.96 | 218.5455 | 269.8 | 285.4 | 273.7 | 275.4 | 379.4 | 36.7 | 20.3 | 70.2 | 3.3 | 180.6 | 5.2 | 864.4 | 768.2 | 843.6 | 820.2 | 804.4 | 331.6 | 629.4 | 793.5 | 418.7 | 743.4 | 389.4 | 808 | 714 | 190.8 | 292.1 | 298.9 | 250.1 | 172.1 | 278.8 | 275.7 | 235.5
564 | 401 | 468.2 | 187.28 | 218.9195 | 269.1 | 288.1 | 274.3 | 276.7 | 386 | 36.7 | 20.3 | 70.3 | 3.5 | 179.7 | 5 | 864.1 | 768.2 | 848.1 | 821.4 | 804.6 | 332 | 635.1 | 790.2 | 419.5 | 742.5 | 389.8 | 807.4 | 713.8 | 191.2 | 292.6 | 299.5 | 250.5 | 172.5 | 278.9 | 275.9 | 235.8
565 | 402 | 468.3 | 187.32 | 218.9663 | 268.7 | 288.8 | 275.3 | 277.9 | 384.4 | 36.8 | 20.3 | 70.3 | 3.4 | 199.8 | 5 | 867.1 | 769.8 | 856 | 821.8 | 804.9 | 332.5 | 644.4 | 790.6 | 420.5 | 743.6 | 390.2 | 807.3 | 712.9 | 191.6 | 293 | 300.1 | 251.1 | 172.9 | 279 | 276.1 | 236.2
566 | 403 | 467 | 186.8 | 218.3584 | 269 | 287.9 | 275.7 | 278.3 | 385 | 36.9 | 20.3 | 70.4 | 3.2 | 201 | 5 | 870.1 | 771.5 | 860.9 | 821.5 | 805.6 | 333.1 | 641.8 | 790.3 | 421.4 | 743.5 | 390.5 | 806.9 | 713 | 192 | 293.5 | 300.4 | 251.5 | 173.3 | 279 | 276.3 | 236.5
567 | 404 | 467.5 | 187 | 218.5922 | 268.4 | 287.4 | 275.9 | 277.9 | 395.5 | 36.9 | 20.3 | 70.5 | 3 | 190 | 5 | 872.5 | 770.5 | 865.5 | 821.1 | 807.5 | 333.6 | 651.7 | 794.6 | 422.2 | 744 | 391 | 807.5 | 713.6 | 192.5 | 293.7 | 301.1 | 251.8 | 173.7 | 279.3 | 277 | 236.9
568 | 405 | 467.8 | 187.12 | 218.7325 | 268.4 | 287 | 276 | 278.2 | 402.1 | 37 | 20.3 | 70.6 | 3.4 | 200.7 | 5.1 | 871.2 | 769.3 | 865.9 | 820.4 | 806.3 | 334.1 | 655.8 | 789.8 | 423.1 | 743.1 | 391.5 | 808.2 | 713.5 | 192.9 | 294.4 | 301.9 | 252.3 | 174.1 | 279.2 | 277.7 | 237.3
569 | 406 | 467.5 | 187 | 218.5922 | 268.3 | 288.1 | 277.1 | 278.6 | 408.8 | 37.1 | 20.3 | 70.6 | 3.5 | 223.3 | 5.7 | 871.2 | 769.4 | 867.5 | 819.9 | 807 | 334.5 | 653.7 | 789.4 | 423.9 | 742.7 | 392 | 807.8 | 712.1 | 193.3 | 295.3 | 302.9 | 252.8 | 174.5 | 279.3 | 277.9 | 237.5
570 | 407 | 467.9 | 187.16 | 218.7793 | 269.3 | 290.6 | 278.7 | 279 | 411 | 37.2 | 20.3 | 70.6 | 3.6 | 218.9 | 5.8 | 869 | 768.8 | 864 | 821.2 | 805.9 | 335 | 653.1 | 784.8 | 425.1 | 742.1 | 392.6 | 807.8 | 710.6 | 193.8 | 295.9 | 303.8 | 253.4 | 174.9 | 279.2 | 278.2 | 238
571 | 408 | 468.2 | 187.28 | 218.9195 | 270.1 | 292.6 | 280 | 279.5 | 408.8 | 37.2 | 20.3 | 70.6 | 2.9 | 199.5 | 5.3 | 871.4 | 768.2 | 867.4 | 821.6 | 807.7 | 335.4 | 648 | 783.7 | 426.2 | 741.7 | 393.3 | 805.4 | 709.4 | 194.2 | 296.3 | 304.4 | 253.8 | 175.3 | 279.2 | 278.7 | 238.4
572 | 409 | 468 | 187.2 | 218.826 | 271.5 | 292.9 | 280.7 | 280 | 407.5 | 37.2 | 20.3 | 70.6 | 3.2 | 188.6 | 5.1 | 873.9 | 767.3 | 868.8 | 821.5 | 810 | 336 | 644.4 | 786.2 | 427.4 | 742.7 | 393.9 | 804.7 | 708 | 194.7 | 296.9 | 305.1 | 254.1 | 175.6 | 279.5 | 279.3 | 238.7
573 | 410 | 467.4 | 186.96 | 218.5455 | 272.5 | 292.6 | 280.9 | 280.8 | 409.2 | 37.3 | 20.3 | 70.6 | 3.6 | 193.6 | 4.8 | 875.2 | 767.4 | 871.2 | 821.1 | 811.5 | 336.5 | 638.1 | 786.7 | 428.6 | 743.2 | 394.5 | 806.4 | 705.3 | 195.2 | 297.4 | 305.7 | 254.4 | 176 | 279.5 | 279.8 | 239.2
574 | 411 | 468.2 | 187.28 | 218.9195 | 273 | 292.4 | 280.9 | 281.5 | 408.1 | 37.3 | 20.2 | 70.7 | 3.6 | 211.6 | 5.1 | 876.1 | 767.3 | 875 | 820.5 | 815.1 | 337.2 | 635.2 | 787.1 | 430.1 | 743.5 | 395.1 | 805.1 | 702.8 | 195.6 | 297.8 | 306.6 | 254.6 | 176.4 | 279.7 | 280.3 | 239.5
575 | 412 | 467.5 | 187 | 218.5922 | 273.4 | 294.4 | 280.3 | 281.6 | 409.3 | 37.3 | 20.2 | 70.8 | 3.4 | 216.1 | 5 | 875.5 | 766.7 | 877.3 | 820.5 | 814.6 | 337.8 | 630.5 | 784.5 | 431.2 | 743.1 | 395.6 | 804 | 701.4 | 196.1 | 298.1 | 307.1 | 255 | 176.7 | 279.6 | 280.6 | 239.9
576 | 413 | 468.2 | 187.28 | 218.9195 | 273.1 | 295.6 | 279.8 | 281.8 | 418.7 | 37.3 | 20.2 | 70.9 | 3.6 | 203.8 | 4.8 | 873.6 | 766.4 | 871.5 | 820.8 | 814.4 | 338.5 | 634.7 | 782.3 | 432.8 | 743.5 | 396.3 | 803 | 700.4 | 196.6 | 298.5 | 307.6 | 255.5 | 177.1 | 279.7 | 280.9 | 240.3
577 | 414 | 469.8 | 187.92 | 219.6677 | 273.6 | 296.2 | 280.2 | 281.8 | 432.1 | 37.5 | 20.2 | 71 | 4 | 201 | 4.9 | 868.8 | 767.5 | 858.9 | 821 | 813.9 | 339 | 636.9 | 773.9 | 434.2 | 742.8 | 397 | 797.2 | 700.2 | 197.1 | 299.1 | 308.1 | 256 | 177.4 | 279.6 | 281 | 240.6
578 | 415 | 469.2 | 187.68 | 219.3871 | 274.2 | 298 | 281 | 282.2 | 444.5 | 37.7 | 20.2 | 71.2 | 3.8 | 200.5 | 4.9 | 869.1 | 768.7 | 865.8 | 821.3 | 815 | 339.7 | 653.9 | 771.9 | 436.1 | 742.9 | 397.7 | 799.4 | 700.2 | 197.6 | 299.4 | 308.5 | 256.4 | 177.8 | 279.7 | 280.9 | 240.9
579 | 416 | 468.2 | 187.28 | 218.9195 | 274.4 | 299.2 | 281.6 | 283 | 444.1 | 37.8 | 20.2 | 71.2 | 3.4 | 199.7 | 4.8 | 870.7 | 769.7 | 867.7 | 821.4 | 816.1 | 340.4 | 663.7 | 773.7 | 437.8 | 743.8 | 398.4 | 800.5 | 700.5 | 198.1 | 299.8 | 308.5 | 257.3 | 178.2 | 279.9 | 281.1 | 241.2
580 | 417 | 468.6 | 187.44 | 219.1066 | 273.9 | 300.1 | 282.1 | 283.8 | 451.7 | 37.8 | 20.2 | 71.3 | 3.6 | 197.8 | 4.7 | 871.2 | 770.4 | 869.5 | 821.4 | 818.6 | 341.2 | 674.5 | 773.4 | 440.1 | 744.9 | 399.2 | 800.7 | 700.9 | 198.6 | 300.1 | 308.8 | 257.5 | 178.5 | 280.1 | 281.7 | 241.6
581 | 418 | 468.6 | 187.44 | 219.1066 | 273.5 | 300.1 | 282.5 | 283.8 | 444.8 | 37.8 | 20.2 | 71.3 | 3 | 194.6 | 4.4 | 873 | 769.1 | 874.2 | 820.6 | 820.4 | 342 | 676.4 | 777.5 | 442.5 | 745.8 | 399.9 | 801 | 702.2 | 199 | 300.3 | 309.1 | 257.6 | 178.9 | 280.5 | 283 | 242.2
582 | 419 | 468.4 | 187.36 | 219.013 | 273.7 | 300 | 282.7 | 283.9 | 432.3 | 37.8 | 20.2 | 71.4 | 3.3 | 193.1 | 4.1 | 874.5 | 767.8 | 874.2 | 820.5 | 820.9 | 342.6 | 671.9 | 779.3 | 444.5 | 745.4 | 400.6 | 803.4 | 704.2 | 199.5 | 300.6 | 308.8 | 257.7 | 179.2 | 280.8 | 283.5 | 242.7
583 | 420 | 469.2 | 187.68 | 219.3871 | 273.4 | 298.9 | 282.5 | 283.9 | 420.4 | 37.8 | 20.2 | 71.4 | 3.6 | 192.7 | 4.2 | 877.1 | 766.6 | 876.4 | 819.2 | 822.3 | 343.2 | 673 | 788.2 | 446.4 | 746.3 | 401.4 | 804.2 | 706.2 | 200 | 300.7 | 308.6 | 258.1 | 179.6 | 281.1 | 283.9 | 243
584 | 421 | 469.2 | 187.68 | 219.3871 | 273.1 | 296.9 | 283 | 282.9 | 414.9 | 37.7 | 20.2 | 71.5 | 3.8 | 195.9 | 4.4 | 880.6 | 766.1 | 880.3 | 818.4 | 820.9 | 343.8 | 665.9 | 786.7 | 448.3 | 746.2 | 402.2 | 806.3 | 708.9 | 200.5 | 301 | 308.5 | 258.7 | 179.9 | 281.1 | 284.3 | 243.3
585 | 422 | 469.1 | 187.64 | 219.3403 | 273 | 296.1 | 283.8 | 282.3 | 412.5 | 37.7 | 20.2 | 71.5 | 3.3 | 211.6 | 4.4 | 880.6 | 766.6 | 883 | 819.1 | 824 | 344.1 | 664 | 782.7 | 449.9 | 745 | 403 | 803.9 | 710.6 | 201 | 301.2 | 308.3 | 258.7 | 180.3 | 281.2 | 284.5 | 243.6
586 | 423 | 468.8 | 187.52 | 219.2001 | 273.2 | 296.6 | 284.3 | 282.7 | 408.9 | 37.8 | 20.2 | 71.6 | 3.4 | 199.7 | 4.6 | 881.2 | 768.2 | 883.4 | 818.9 | 825.6 | 344.7 | 663.1 | 784.6 | 451.8 | 746.5 | 403.7 | 803 | 712.4 | 201.4 | 301.3 | 308.1 | 258.8 | 180.6 | 281.3 | 284.7 | 244
587 | 424 | 468.8 | 187.52 | 219.2001 | 273.5 | 296.4 | 284.1 | 283.1 | 407.1 | 38 | 20.2 | 71.7 | 3.3 | 177.2 | 4.9 | 879.2 | 769.3 | 882.3 | 819.3 | 826.7 | 345.3 | 660.5 | 783.4 | 453.6 | 745 | 404.5 | 805 | 714.3 | 201.9 | 301.6 | 308 | 259.2 | 181 | 281.2 | 284.8 | 244.3
588 | 425 | 468.1 | 187.24 | 218.8728 | 272.9 | 295.2 | 283.5 | 283.6 | 406.1 | 38.1 | 20.2 | 71.9 | 3.4 | 186.6 | 5.1 | 878.8 | 770 | 882.2 | 820.1 | 828.9 | 345.8 | 651.5 | 778.5 | 455.3 | 744.1 | 405.4 | 802 | 715.9 | 202.3 | 301.6 | 308.3 | 259.5 | 181.3 | 280.8 | 285 | 244.7
589 | 426 | 467.7 | 187.08 | 218.6857 | 273.4 | 294.1 | 282.4 | 283.6 | 403.8 | 38.2 | 20.2 | 72.1 | 3.5 | 198.6 | 5.2 | 878.4 | 770.7 | 886 | 820.1 | 830.5 | 346.3 | 647.4 | 776 | 456.7 | 743.8 | 406.2 | 799.9 | 716.8 | 202.8 | 301.5 | 308.3 | 259.8 | 181.7 | 280.9 | 284.7 | 245
590 | 427 | 468.8 | 187.52 | 219.2001 | 273.9 | 294.3 | 282.4 | 283.2 | 402 | 38.2 | 20.2 | 72.2 | 3.8 | 193.1 | 5.5 | 878.3 | 770.4 | 883.1 | 820.3 | 830 | 347 | 647.7 | 776.8 | 458.7 | 744.9 | 407.1 | 800.9 | 718.3 | 203.2 | 301.5 | 308.4 | 260.3 | 182 | 281 | 284.5 | 245.2
591 | 428 | 467.2 | 186.88 | 218.452 | 274.1 | 294.8 | 282.1 | 282.4 | 403.8 | 38.2 | 20.2 | 72.4 | 3.8 | 187.8 | 5.5 | 876.6 | 771.3 | 879.2 | 820.9 | 830.2 | 347.7 | 650.3 | 776.1 | 460.9 | 743.8 | 407.9 | 799.3 | 720.4 | 203.6 | 301.7 | 308.8 | 260.6 | 182.3 | 281.1 | 284.4 | 245.5
592 | 429 | 467.8 | 187.12 | 218.7325 | 273.5 | 295.5 | 281.3 | 281.5 | 403.5 | 38.2 | 20.2 | 72.6 | 4.1 | 179.3 | 5.4 | 877.2 | 772.4 | 879.8 | 821.5 | 830.6 | 348.2 | 652.7 | 772.6 | 462.8 | 743.1 | 408.7 | 798.2 | 722.5 | 204.1 | 301.7 | 309.1 | 260.8 | 182.7 | 281.2 | 284.1 | 245.8
593 | 430 | 467.9 | 187.16 | 218.7793 | 273 | 297.3 | 280.7 | 281.6 | 398.9 | 38.4 | 20.2 | 72.7 | 3.7 | 177.5 | 5.4 | 880.5 | 772.7 | 886.8 | 821.9 | 832.8 | 348.8 | 652 | 774.5 | 465 | 743.1 | 409.5 | 798.9 | 725 | 204.5 | 301.7 | 309.2 | 260.9 | 183 | 281.2 | 283.8 | 246.2
594 | 431 | 468 | 187.2 | 218.826 | 273.1 | 298.1 | 280.1 | 281.4 | 392.8 | 38.5 | 20.2 | 72.8 | 3.4 | 175.3 | 5.3 | 882 | 772.5 | 886.1 | 821.7 | 833.5 | 349.5 | 650.7 | 777.5 | 467.1 | 743.4 | 410.3 | 797.5 | 727.7 | 204.9 | 301.6 | 309.1 | 261 | 183.4 | 281.3 | 283.7 | 246.5
595 | 432 | 468 | 187.2 | 218.826 | 273 | 297.6 | 280 | 281 | 389.2 | 38.4 | 20.2 | 72.8 | 3.8 | 174.4 | 5.3 | 882.8 | 772.3 | 882.7 | 820.9 | 832.7 | 350 | 654.4 | 780.2 | 469.1 | 743.5 | 411.1 | 800.7 | 730.8 | 205.3 | 301.4 | 309 | 261.2 | 183.7 | 281.5 | 283.8 | 246.8
596 | 433 | 468 | 187.2 | 218.826 | 273.3 | 296 | 279.8 | 280.7 | 391 | 38.4 | 20.2 | 73 | 4 | 175.2 | 5.1 | 881.6 | 773.1 | 879.4 | 821.4 | 831.4 | 350.6 | 656.1 | 782.8 | 471.2 | 743.8 | 412.2 | 801.9 | 734 | 205.7 | 301.4 | 308.9 | 261.4 | 184 | 281.7 | 284 | 247.1
597 | 434 | 467.1 | 186.84 | 218.4052 | 273.7 | 294.7 | 280.5 | 280.4 | 395.7 | 38.5 | 20.2 | 73.1 | 3.7 | 175.9 | 4.8 | 878.9 | 772.8 | 875.7 | 822.2 | 826.7 | 351.3 | 667.2 | 780.3 | 473.3 | 743.1 | 413.7 | 800.7 | 738.1 | 206.1 | 301.3 | 308.9 | 261.7 | 184.4 | 281.8 | 283.8 | 247.4
598 | 435 | 468.8 | 187.52 | 219.2001 | 273 | 295 | 281.5 | 280.2 | 396.4 | 38.7 | 20.2 | 73.3 | 3.7 | 173.3 | 4.5 | 877.3 | 772.7 | 875 | 823.6 | 826.1 | 351.8 | 671.1 | 775.6 | 475.4 | 742.5 | 415.1 | 797.5 | 742.8 | 206.5 | 301.3 | 308.9 | 262.4 | 184.7 | 282.3 | 283.8 | 247.7
599 | 436 | 470.8 | 188.32 | 220.1352 | 272.7 | 294.9 | 282.4 | 280.3 | 394 | 38.8 | 20.2 | 73.4 | 3.7 | 171.9 | 4.1 | 877.4 | 774.5 | 876.3 | 824.5 | 827.7 | 352.4 | 667.4 | 774.4 | 477.3 | 742.6 | 416.5 | 797.4 | 747.5 | 207 | 301.1 | 308.7 | 262.4 | 185.1 | 282.9 | 284 | 248
600 | 437 | 469.7 | 187.88 | 219.6209 | 272.1 | 294.8 | 282.9 | 280.5 | 393.1 | 38.8 | 20.2 | 73.5 | 3.5 | 169.5 | 3.9 | 878.9 | 776.2 | 876.1 | 824.3 | 827.1 | 353 | 670.4 | 774.4 | 479.1 | 743.1 | 417.7 | 800.2 | 751.8 | 207.4 | 301 | 308.8 | 262.7 | 185.4 | 283.1 | 283.9 | 248.4
601 | 438 | 469.6 | 187.84 | 219.5741 | 271.1 | 294.7 | 283 | 280.8 | 394.8 | 38.8 | 20.2 | 73.6 | 3.5 | 174.6 | 3.6 | 879 | 776.1 | 875.8 | 824.6 | 827.1 | 353.6 | 676.2 | 770.9 | 480.9 | 742.6 | 418.9 | 799.4 | 755.2 | 207.8 | 301 | 309.1 | 262.9 | 185.8 | 283 | 284 | 248.6
602 | 439 | 469.1 | 187.64 | 219.3403 | 270.6 | 295.2 | 282.7 | 281.3 | 396.7 | 38.9 | 20.2 | 73.7 | 3.4 | 192.5 | 3.6 | 878.8 | 776.8 | 876.3 | 824.7 | 825.7 | 354.2 | 684.9 | 771.8 | 482.6 | 742.5 | 419.9 | 796.1 | 757.5 | 208.2 | 301.3 | 309.1 | 263.3 | 186.2 | 283.1 | 284.1 | 248.9
603 | 440 | 468.6 | 187.44 | 219.1066 | 270.2 | 296.6 | 282.9 | 281.7 | 406.4 | 38.8 | 20.2 | 73.7 | 3.4 | 187.7 | 3.7 | 873.7 | 776.2 | 861.1 | 824.9 | 820.1 | 354.7 | 695.5 | 766.7 | 484.2 | 741.2 | 420.9 | 791.7 | 760.1 | 208.6 | 302 | 309.3 | 264 | 186.5 | 283.2 | 284 | 249.1
604 | 441 | 468.9 | 187.56 | 219.2468 | 270.1 | 298 | 283.4 | 282.3 | 408.9 | 38.8 | 20.2 | 73.7 | 3.6 | 169.5 | 3.9 | 864.2 | 775.6 | 833.5 | 825.3 | 810.9 | 354.9 | 697.5 | 755 | 485.4 | 738.2 | 421.8 | 778.4 | 763.5 | 209 | 303 | 309.7 | 264.9 | 186.9 | 283.5 | 284.1 | 249.4
605 | 442 | 468.5 | 187.4 | 219.0598 | 270.7 | 299.1 | 285.2 | 283.6 | 410.9 | 38.9 | 20.2 | 73.7 | 3.5 | 175.5 | 3.8 | 857.3 | 774 | 811.7 | 825.8 | 802.4 | 355.1 | 704.4 | 745.6 | 486.9 | 735.8 | 422.8 | 761.3 | 766.2 | 209.4 | 303.8 | 310.4 | 265.7 | 187.2 | 283.9 | 284.4 | 249.6
606 | 443 | 468.3 | 187.32 | 218.9663 | 272.4 | 301 | 287.5 | 284.7 | 411.8 | 39 | 20.2 | 73.8 | 3 | 188.5 | 4.2 | 853.4 | 772.9 | 807.6 | 826.2 | 796.4 | 355.3 | 712.8 | 736.8 | 488.3 | 733 | 423.8 | 753.6 | 768.6 | 209.8 | 304.6 | 311.8 | 266.5 | 187.6 | 284.8 | 284.7 | 249.9
607 | 444 | 468.5 | 187.4 | 219.0598 | 274.5 | 302.7 | 289.9 | 286.2 | 417.6 | 39.1 | 20.2 | 73.8 | 3 | 188.2 | 4.3 | 851 | 772.8 | 801.9 | 826.1 | 790.4 | 355.5 | 717 | 736.5 | 489.7 | 732.6 | 424.8 | 748.9 | 769.4 | 210.2 | 305.5 | 313.8 | 267.2 | 188 | 285.7 | 285.1 | 250.4
608 | 445 | 468.6 | 187.44 | 219.1066 | 277.1 | 303.3 | 292.5 | 287.6 | 423.2 | 39.1 | 20.2 | 73.9 | 3.3 | 185.4 | 4.1 | 852.8 | 772.6 | 807.8 | 826.1 | 787.1 | 355.9 | 717.5 | 739.7 | 491.1 | 732.1 | 425.9 | 749.8 | 768.5 | 210.6 | 306.6 | 315.8 | 267.7 | 188.3 | 287.2 | 285.5 | 250.8
609 | 446 | 470.1 | 188.04 | 219.8079 | 280.1 | 301.7 | 294.1 | 288.9 | 426.1 | 39 | 20.2 | 74 | 3.9 | 176.6 | 3.9 | 850.7 | 772.6 | 802.8 | 826.7 | 783.1 | 356.3 | 717.2 | 734.8 | 492.5 | 731.7 | 427 | 740.1 | 767.6 | 211 | 307.7 | 317.6 | 268.3 | 188.7 | 288.7 | 286.4 | 251.3
610 | 447 | 469.6 | 187.84 | 219.5741 | 282.8 | 301.4 | 295.5 | 289.8 | 431.9 | 38.9 | 20.2 | 74 | 3.9 | 174.5 | 3.9 | 851.8 | 773.4 | 805.5 | 826.8 | 782.3 | 356.7 | 717.7 | 735.1 | 493.8 | 730.9 | 428 | 736.8 | 767.7 | 211.5 | 308.7 | 319.6 | 268.9 | 189 | 289.9 | 287.4 | 251.7
611 | 448 | 469 | 187.6 | 219.2936 | 282.9 | 301.5 | 297.4 | 291.3 | 437.5 | 38.9 | 20.2 | 74.1 | 3.9 | 196 | 4 | 853.8 | 774 | 813.3 | 826.3 | 783.8 | 357.1 | 715 | 741.2 | 495.2 | 731.9 | 429.1 | 738.4 | 766.3 | 211.9 | 309.5 | 320.8 | 269.2 | 189.4 | 290.9 | 288.3 | 252.2
612 | 449 | 468.7 | 187.48 | 219.1533 | 283.7 | 302.7 | 299 | 292.6 | 441.3 | 39 | 20.2 | 74.2 | 4 | 193.2 | 4 | 857.9 | 773.8 | 822.6 | 825.1 | 789 | 357.7 | 714.9 | 749 | 496.9 | 733 | 430.3 | 744.9 | 765.3 | 212.4 | 310.2 | 321.6 | 269.3 | 189.8 | 292 | 289.1 | 252.6
613 | 450 | 468.4 | 187.36 | 219.013 | 285.2 | 304 | 299.6 | 293.9 | 443.6 | 39.1 | 20.2 | 74.3 | 4 | 185.6 | 3.8 | 861.8 | 774.9 | 833.5 | 824.7 | 791.5 | 358.2 | 721.1 | 758.4 | 498.3 | 733.4 | 431.5 | 753.1 | 765 | 212.9 | 310.8 | 322.4 | 269.6 | 190.2 | 293.7 | 289.9 | 253.1
614 | 451 | 469.3 | 187.72 | 219.4339 | 286.1 | 305.1 | 299.2 | 294.8 | 444.9 | 39.1 | 20.2 | 74.4 | 3.9 | 190.9 | 3.5 | 863.5 | 774.8 | 835.9 | 825.1 | 791.9 | 358.7 | 723.6 | 762 | 500 | 733.8 | 432.7 | 754.1 | 764.9 | 213.4 | 311.8 | 323.5 | 270.1 | 190.7 | 294.9 | 290.8 | 253.5
615 | 452 | 469.3 | 187.72 | 219.4339 | 287 | 307 | 299.3 | 295.4 | 446.1 | 39.1 | 20.2 | 74.5 | 3.8 | 188.2 | 3.4 | 865.8 | 774.1 | 838.9 | 824.7 | 792.6 | 359.2 | 725.9 | 758 | 501.8 | 733.2 | 433.9 | 758.5 | 766.9 | 213.9 | 312.7 | 324.4 | 270.7 | 191.1 | 295.6 | 291.6 | 253.9
616 | 453 | 468.9 | 187.56 | 219.2468 | 288.2 | 307.6 | 299.9 | 295.8 | 452.1 | 39.2 | 20.2 | 74.6 | 3.5 | 183.7 | 3.4 | 861.6 | 773.6 | 834.7 | 825.2 | 789.9 | 359.7 | 729 | 750.6 | 504 | 732.6 | 435.1 | 755.6 | 769.4 | 214.5 | 313.5 | 325.3 | 271.6 | 191.5 | 296.3 | 292.5 | 254.4
617 | 454 | 468.8 | 187.52 | 219.2001 | 289.2 | 308.2 | 300.3 | 296.7 | 448.7 | 39.3 | 20.2 | 74.8 | 3.3 | 184.9 | 3.4 | 861.6 | 774.2 | 835.3 | 826.3 | 789.3 | 360.1 | 726.6 | 755.7 | 506.4 | 732.3 | 436.3 | 756.8 | 771.9 | 215 | 314 | 326 | 272.1 | 191.9 | 297.4 | 293.6 | 254.9
618 | 455 | 469 | 187.6 | 219.2936 | 290.2 | 308.5 | 301 | 297.6 | 445.9 | 39.4 | 20.2 | 74.9 | 3.8 | 186 | 3.5 | 862.5 | 774.4 | 836.9 | 827.2 | 788.7 | 360.4 | 727.5 | 758.3 | 509.1 | 732.6 | 437.5 | 762.6 | 774.7 | 215.5 | 314.6 | 326.6 | 272.3 | 192.4 | 298 | 294.5 | 255.3
619 | 456 | 469 | 187.6 | 219.2936 | 290.3 | 307.1 | 301.8 | 298.1 | 444.4 | 39.5 | 20.2 | 75.1 | 3.8 | 187.1 | 3.5 | 865.3 | 774.9 | 843.8 | 827.9 | 789.2 | 360.9 | 726 | 760.9 | 511.9 | 732.6 | 438.8 | 766.5 | 776.6 | 216.1 | 314.8 | 327 | 272.3 | 192.8 | 298.4 | 295.2 | 255.7
620 | 457 | 469 | 187.6 | 219.2936 | 289.3 | 306.4 | 302 | 298.8 | 438.3 | 39.6 | 20.2 | 75.3 | 3.8 | 189.8 | 3.6 | 868.4 | 774.7 | 852.9 | 827.9 | 793.7 | 361.4 | 719.6 | 764.9 | 514.4 | 734.4 | 440 | 769.6 | 776.6 | 216.7 | 314.9 | 327.4 | 272.3 | 193.3 | 298.7 | 295.4 | 256.1
621 | 458 | 468.5 | 187.4 | 219.0598 | 288.5 | 305.9 | 302 | 299.1 | 443.7 | 39.6 | 20.2 | 75.5 | 4 | 191.4 | 3.9 | 871 | 773.7 | 859.8 | 827.2 | 795.5 | 362 | 722.2 | 760.7 | 516.6 | 734.2 | 441.1 | 766.7 | 775.6 | 217.2 | 315.2 | 327.8 | 272.6 | 193.7 | 298.5 | 295.5 | 256.4
622 | 459 | 472.2 | 188.88 | 220.7898 | 289.1 | 304.8 | 301.8 | 299.2 | 444.8 | 39.7 | 20.2 | 75.6 | 3.8 | 188.5 | 4 | 872.1 | 772.6 | 858.5 | 826.7 | 796.2 | 362.5 | 719.4 | 763 | 518.3 | 734.8 | 442.2 | 770 | 774.7 | 217.8 | 315.5 | 328 | 273 | 194.1 | 298.4 | 295.7 | 256.9
623 | 460 | 476.2 | 190.48 | 222.6601 | 289.4 | 305.3 | 301.3 | 299.5 | 444.9 | 39.7 | 20.2 | 75.9 | 3.7 | 181.9 | 3.8 | 873.3 | 772.2 | 866.8 | 826.5 | 798.2 | 363.1 | 713.7 | 767.5 | 519.6 | 735.3 | 443.2 | 775.6 | 775.2 | 218.3 | 315.7 | 328.2 | 273.3 | 194.6 | 298.3 | 295.8 | 257.2
624 | 461 | 474 | 189.6 | 221.6315 | 289.9 | 306.5 | 300.9 | 299.5 | 439.5 | 39.7 | 20.2 | 76 | 3.3 | 184.7 | 3.7 | 874.6 | 772.4 | 864.9 | 826.1 | 799.1 | 363.6 | 706.8 | 771.1 | 520.7 | 736.6 | 444.4 | 778.1 | 777.2 | 218.8 | 315.8 | 328.2 | 273.4 | 195 | 298.4 | 295.9 | 257.4
625 | 462 | 473 | 189.2 | 221.1639 | 290.5 | 306.5 | 301.1 | 299.6 | 438.3 | 39.7 | 20.2 | 76 | 3.7 | 181 | 3.1 | 872.6 | 773.2 | 858 | 826.4 | 800.1 | 364.3 | 705.5 | 778.9 | 521.7 | 737.4 | 445.5 | 780.4 | 778.9 | 219.4 | 316.1 | 328.5 | 273.7 | 195.5 | 298.8 | 296.3 | 257.7
626 | 463 | 472.5 | 189 | 220.9301 | 290.4 | 307.1 | 301.2 | 299.6 | 447.1 | 39.7 | 20.1 | 76.2 | 3.9 | 166.3 | 2.7 | 872.4 | 774.1 | 861.1 | 826.6 | 801.9 | 364.8 | 703.3 | 780.2 | 522.4 | 738.6 | 446.5 | 781.1 | 778.3 | 219.9 | 316.4 | 328.9 | 274.2 | 195.9 | 298.8 | 296.4 | 258.1
627 | 464 | 472 | 188.8 | 220.6963 | 290.4 | 307.3 | 302.1 | 300.2 | 457 | 39.9 | 20.1 | 76.4 | 3.6 | 165.2 | 2.9 | 874.9 | 775.6 | 868.3 | 826.8 | 804.8 | 365.6 | 706.1 | 781.3 | 523.4 | 740.4 | 447.5 | 784.9 | 779.1 | 220.4 | 316.6 | 329 | 274.5 | 196.3 | 299.3 | 296.6 | 258.5
628 | 465 | 471 | 188.4 | 220.2287 | 290.2 | 307.4 | 302.1 | 300.5 | 445 | 40.1 | 20.1 | 76.5 | 3.1 | 170 | 3.1 | 878.6 | 776.6 | 875.5 | 826.5 | 808.7 | 366.4 | 708 | 787.1 | 524.3 | 741.7 | 448.5 | 787.8 | 779.9 | 220.9 | 316.7 | 329.4 | 274.7 | 196.7 | 300.2 | 296.7 | 258.8
629 | 466 | 470.8 | 188.32 | 220.1352 | 289.9 | 308.4 | 301.3 | 300.4 | 438.4 | 40.2 | 20.1 | 76.6 | 3.5 | 173.3 | 3.3 | 880.1 | 777.2 | 875 | 825.6 | 810.7 | 367.1 | 705.2 | 793.6 | 525.2 | 743.4 | 449.6 | 789.4 | 781.4 | 221.5 | 317.1 | 329.5 | 275.2 | 197.1 | 300.3 | 296.9 | 259.2
630 | 467 | 470.9 | 188.36 | 220.182 | 289.3 | 308.8 | 300 | 300.4 | 435.4 | 40.3 | 20.1 | 76.6 | 3.3 | 174 | 3.4 | 882.4 | 777.4 | 873.9 | 825.1 | 812.6 | 367.8 | 704 | 796 | 526 | 743.5 | 452.4 | 789.5 | 782.2 | 222 | 317.2 | 329.7 | 275.5 | 197.5 | 300.6 | 297 | 259.6
631 | 468 | 469.6 | 187.84 | 219.5741 | 289.6 | 307.5 | 299.1 | 300.4 | 427.5 | 40.4 | 20.1 | 76.6 | 3.6 | 178.9 | 3.7 | 881.2 | 776.9 | 862.1 | 825.1 | 811 | 368.3 | 702.4 | 798.9 | 526.7 | 743.8 | 458.7 | 793.6 | 783.7 | 222.5 | 317.1 | 329.4 | 275.4 | 197.9 | 300.6 | 297.1 | 259.9
632 | 469 | 468.8 | 187.52 | 219.2001 | 289.1 | 306.5 | 298.6 | 300.3 | 417.5 | 40.6 | 20.1 | 76.7 | 3.9 | 177.7 | 3.8 | 878.7 | 777.2 | 851.5 | 825.6 | 809.2 | 368.5 | 698.9 | 797.8 | 527.2 | 742.9 | 465.5 | 791.6 | 785.1 | 223 | 316.9 | 329.2 | 275.5 | 198.3 | 300.5 | 297.3 | 260.3
633 | 470 | 470.2 | 188.08 | 219.8547 | 288.4 | 305.6 | 298.1 | 300.1 | 408.6 | 40.8 | 20.1 | 76.8 | 3.7 | 175.4 | 4 | 876.4 | 777.4 | 845 | 826.3 | 807.4 | 368.9 | 692 | 791 | 527.7 | 741.9 | 472.3 | 790.5 | 786.6 | 223.5 | 316.6 | 328.7 | 275.6 | 198.7 | 300.5 | 297.2 | 260.6
634 | 471 | 470.3 | 188.12 | 219.9014 | 287.4 | 305.7 | 298.1 | 299.3 | 400.5 | 41 | 20.1 | 76.8 | 3.9 | 175.4 | 4.3 | 878 | 779.3 | 846.7 | 827 | 807.5 | 369.3 | 689.2 | 790.5 | 528.2 | 742.8 | 478.7 | 794.7 | 789 | 224 | 316.3 | 328.5 | 275.7 | 199.1 | 300.7 | 297.2 | 260.9
635 | 472 | 469 | 187.6 | 219.2936 | 286.3 | 305.3 | 298.2 | 298.6 | 400.1 | 41.2 | 20.1 | 76.9 | 3.7 | 183.4 | 4.6 | 878.4 | 781.1 | 853 | 827.2 | 808.3 | 369.7 | 687.3 | 794.1 | 528.7 | 743.3 | 484.6 | 797.2 | 791.1 | 224.5 | 316.1 | 328.1 | 276 | 199.5 | 300.6 | 297.1 | 261.2
636 | 473 | 469.9 | 187.96 | 219.7144 | 286 | 305.7 | 297.7 | 297.9 | 399.9 | 41.3 | 20.1 | 76.9 | 4.1 | 186 | 4.9 | 879.6 | 782.8 | 859.7 | 826.7 | 810.6 | 370.2 | 688.3 | 803.2 | 529.5 | 744.7 | 490 | 799.3 | 791.6 | 225 | 315.7 | 327.6 | 276.3 | 199.9 | 300.4 | 297.2 | 261.5
637 | 474 | 469.5 | 187.8 | 219.5274 | 286 | 305.9 | 297.6 | 297 | 399.1 | 41.5 | 20.1 | 77 | 3.9 | 180.6 | 5.1 | 881.4 | 783.8 | 862.2 | 827.7 | 809.9 | 370.8 | 686.4 | 805 | 530.3 | 745.4 | 495.4 | 799.7 | 793.6 | 225.4 | 315.5 | 327.2 | 276.9 | 200.2 | 300.7 | 297.2 | 261.9
638 | 475 | 469.5 | 187.8 | 219.5274 | 285.3 | 304.7 | 297.6 | 297 | 396.6 | 41.6 | 20.1 | 77 | 3.7 | 173.3 | 5.2 | 881.7 | 782.7 | 860.9 | 827.6 | 811.4 | 371.2 | 681.5 | 802.2 | 531 | 744.9 | 500.5 | 797.8 | 795.5 | 225.9 | 315.2 | 326.8 | 277.1 | 200.6 | 300.9 | 297.2 | 262.3
639 | 476 | 469.8 | 187.92 | 219.6677 | 284.8 | 303.2 | 296.7 | 297.1 | 394.6 | 41.7 | 20.1 | 77.1 | 4.5 | 181.4 | 5.2 | 878.9 | 783.7 | 862.6 | 828.4 | 810.9 | 371.8 | 681.2 | 788.6 | 531.7 | 744.3 | 505.5 | 795.8 | 797.6 | 226.3 | 314.9 | 326.4 | 277.3 | 201 | 301 | 297.4 | 262.7
640 | 477 | 469.7 | 187.88 | 219.6209 | 284.4 | 302.1 | 295.6 | 296.9 | 390.5 | 41.6 | 20.1 | 77.1 | 3.8 | 188.4 | 4.9 | 877.6 | 784.8 | 868.4 | 828.8 | 814 | 372.2 | 683.7 | 787.1 | 532.3 | 744.5 | 510.7 | 795.4 | 798.7 | 226.8 | 314.7 | 326 | 277.5 | 201.3 | 301.2 | 297.6 | 262.9
641 | 478 | 468.9 | 187.56 | 219.2468 | 284.4 | 303.1 | 294.6 | 296.5 | 386.5 | 41.6 | 20.1 | 77.1 | 3.8 | 174.1 | 4.8 | 877.8 | 785.1 | 872.6 | 828.2 | 817.2 | 372.8 | 683.4 | 787.7 | 533 | 744.8 | 516 | 794.2 | 798.7 | 227.2 | 314.5 | 325.6 | 277.6 | 201.7 | 301.3 | 297.6 | 263.3
642 | 479 | 469.7 | 187.88 | 219.6209 | 284 | 304.2 | 294.5 | 295.8 | 381.9 | 41.8 | 20.1 | 77.2 | 3.4 | 164.1 | 4.6 | 878.5 | 785.3 | 874.7 | 828.2 | 818.2 | 373.5 | 684.1 | 793.3 | 533.9 | 746.1 | 521.1 | 794.6 | 798.5 | 227.6 | 314.2 | 325.3 | 277.9 | 202.1 | 301.3 | 297.7 | 263.6
643 | 480 | 469.7 | 187.88 | 219.6209 | 282.5 | 304.4 | 294.8 | 295 | 381.6 | 41.9 | 20.1 | 77.2 | 3.8 | 169.7 | 4.7 | 878.5 | 785.9 | 877.5 | 828.2 | 822.2 | 374.2 | 682.4 | 793.1 | 534.6 | 746.6 | 526 | 794.9 | 798.7 | 228 | 313.9 | 325 | 278 | 202.4 | 301.3 | 297.7 | 263.9
644 | 481 | 469.5 | 187.8 | 219.5274 | 282.2 | 305 | 294.5 | 295.1 | 378.7 | 42 | 20.1 | 77.2 | 3.5 | 167 | 4.8 | 879 | 785 | 875.5 | 828.4 | 825.1 | 374.9 | 680.2 | 790.4 | 535.4 | 746.5 | 531.8 | 795.2 | 799.3 | 228.5 | 313.6 | 324.7 | 278.2 | 202.7 | 301.4 | 297.7 | 264.2
645 | 482 | 468.7 | 187.48 | 219.1533 | 281.6 | 306.3 | 294.6 | 295.2 | 379.7 | 42.2 | 20.1 | 77.2 | 3 | 167.9 | 5.2 | 878.7 | 784.7 | 872.5 | 829.5 | 823.3 | 375.4 | 678 | 789 | 536 | 745.9 | 538.9 | 794.9 | 800.1 | 228.8 | 313.5 | 324.4 | 278.5 | 203.1 | 301.1 | 297.6 | 264.4
646 | 483 | 468.3 | 187.32 | 218.9663 | 280.7 | 306.7 | 294.6 | 295.3 | 382.1 | 42.2 | 20.1 | 77.2 | 3.1 | 163.6 | 5.3 | 878.4 | 784.1 | 872.6 | 830.1 | 821.6 | 375.8 | 679.7 | 783.2 | 536.6 | 744.8 | 545.7 | 792 | 801.1 | 229.2 | 313.4 | 324.4 | 278.9 | 203.4 | 301 | 297.5 | 264.6
647 | 484 | 468.2 | 187.28 | 218.9195 | 281.2 | 306.5 | 294.3 | 295.1 | 381.6 | 42.3 | 20.1 | 77.2 | 2.9 | 161.2 | 5 | 880.2 | 782.6 | 874.9 | 829.8 | 822 | 375.9 | 675 | 778.1 | 537.1 | 743.8 | 552.3 | 790.5 | 802.5 | 229.6 | 313.3 | 324.1 | 279.1 | 203.8 | 300.9 | 297.6 | 264.8
648 | 485 | 467.7 | 187.08 | 218.6857 | 282 | 306.5 | 293.5 | 294.9 | 380 | 42.4 | 20.1 | 77.2 | 3.7 | 172 | 4.8 | 884.3 | 781.4 | 881.9 | 828.7 | 825.1 | 376.2 | 672.5 | 782.2 | 537.8 | 744.8 | 558.1 | 788.8 | 803.2 | 230 | 312.9 | 323.7 | 279.4 | 204.1 | 300.9 | 297.8 | 265.1
649 | 486 | 468.6 | 187.44 | 219.1066 | 281.7 | 306 | 292.3 | 295 | 381.3 | 42.4 | 20.1 | 77.3 | 4.1 | 186.3 | 4.8 | 886 | 780.4 | 883.5 | 828 | 828.4 | 376.8 | 672.5 | 787.7 | 538.5 | 746.4 | 562.9 | 790.4 | 803.1 | 230.4 | 312.8 | 323.6 | 279.5 | 204.5 | 301 | 297.7 | 265.4
650 | 487 | 468.7 | 187.48 | 219.1533 | 283.1 | 306.3 | 291.1 | 295.8 | 382.3 | 42.4 | 20.1 | 77.3 | 3.9 | 171.7 | 5.2 | 888.1 | 780.1 | 885.8 | 827.8 | 830.9 | 377.5 | 673.3 | 790.1 | 539.3 | 747.4 | 567 | 792 | 802.9 | 230.8 | 312.7 | 323.6 | 279.7 | 204.8 | 300.8 | 297.5 | 265.7
651 | 488 | 468.8 | 187.52 | 219.2001 | 281.7 | 306.5 | 290.6 | 295.9 | 381.2 | 42.4 | 20.1 | 77.5 | 3.8 | 160.4 | 5.7 | 890.2 | 779.3 | 889.2 | 827.1 | 832.2 | 378.1 | 671.1 | 794.8 | 540.2 | 748.6 | 571.3 | 791.3 | 803.5 | 231.1 | 312.6 | 323.4 | 280 | 205.1 | 300.7 | 297.6 | 265.9
652 | 489 | 468.9 | 187.56 | 219.2468 | 281.6 | 307 | 290.7 | 295.6 | 380.9 | 42.5 | 20.1 | 77.6 | 3.8 | 159.4 | 5.5 | 892.2 | 778 | 883.9 | 826.6 | 830.8 | 378.7 | 667 | 795.6 | 541 | 747.7 | 576.9 | 791.8 | 804.1 | 231.5 | 312.5 | 323.3 | 280.3 | 205.5 | 300.5 | 297.7 | 266.3
653 | 490 | 469.4 | 187.76 | 219.4806 | 282.4 | 306.9 | 291 | 295.5 | 386.3 | 42.5 | 20.1 | 77.6 | 3.7 | 160.5 | 4.7 | 890.8 | 777.6 | 883.9 | 826.5 | 833.3 | 379 | 668.4 | 797.6 | 541.5 | 748.7 | 583.8 | 793.2 | 804.8 | 231.9 | 312.5 | 323.1 | 280.6 | 205.8 | 300.4 | 297.5 | 266.5
654 | 491 | 470.3 | 188.12 | 219.9014 | 285 | 306.7 | 290.9 | 295.3 | 392 | 42.5 | 20.1 | 77.6 | 4 | 165.4 | 4.1 | 890.1 | 777.7 | 883 | 826.1 | 834.4 | 379.4 | 675 | 801.8 | 542.2 | 750.3 | 589.2 | 801.8 | 805.3 | 232.2 | 312.6 | 323.3 | 280.9 | 206.1 | 300.3 | 297.5 | 266.7
655 | 492 | 470 | 188 | 219.7612 | 286.2 | 307.7 | 291.2 | 295.8 | 390 | 42.4 | 20.1 | 77.7 | 4.1 | 171.4 | 3.6 | 888.1 | 778.4 | 878.5 | 826.4 | 833 | 380.1 | 676.2 | 806.6 | 543 | 750.9 | 594 | 803.4 | 805.3 | 232.6 | 312.6 | 323.1 | 281.3 | 206.5 | 300.4 | 297.4 | 266.9
656 | 493 | 468.5 | 187.4 | 219.0598 | 288 | 308.3 | 291.4 | 296.1 | 386.2 | 42.4 | 20.1 | 77.7 | 3.4 | 177.3 | 2.8 | 887.9 | 779.6 | 877.1 | 827.5 | 833.1 | 380.5 | 674 | 804.9 | 543.6 | 750.7 | 599.1 | 804.6 | 805.6 | 232.9 | 312.6 | 323.1 | 281.6 | 206.8 | 300.1 | 297.3 | 267.2
657 | 494 | 468.7 | 187.48 | 219.1533 | 290.4 | 307.8 | 290.7 | 296.5 | 383.5 | 42.3 | 20.1 | 77.6 | 3.2 | 201.6 | 2.2 | 888.8 | 779.7 | 877.4 | 826.9 | 834.5 | 380.9 | 675.6 | 807.4 | 544.3 | 752.1 | 603.4 | 801 | 805.8 | 233.3 | 312.6 | 322.9 | 281.7 | 207.2 | 299.7 | 297.2 | 267.4
658 | 495 | 470.2 | 188.08 | 219.8547 | 292.5 | 306.8 | 290.4 | 296.3 | 386 | 42.3 | 20.1 | 77.6 | 3.4 | 219 | 1.9 | 888.5 | 779.2 | 877.1 | 826 | 836.2 | 381.4 | 674.8 | 811.9 | 545 | 753.8 | 606.1 | 797.3 | 805.6 | 233.6 | 312.6 | 322.6 | 281.9 | 207.5 | 299.4 | 297.3 | 267.7
659 | 496 | 469.4 | 187.76 | 219.4806 | 293.9 | 307 | 290 | 295.6 | 392.5 | 42.3 | 20.1 | 77.6 | 4 | 205.4 | 1.6 | 891.4 | 779.4 | 876.6 | 826.3 | 835.8 | 382.1 | 674 | 814.1 | 545.8 | 754.5 | 606.9 | 800.8 | 805.5 | 234 | 312.8 | 322.6 | 282.3 | 207.8 | 299.2 | 297.6 | 267.9
660 | 497 | 468.8 | 187.52 | 219.2001 | 294.9 | 307.5 | 289.9 | 295.1 | 394.7 | 42.4 | 20.1 | 77.7 | 3.7 | 178.1 | 1.6 | 893.7 | 779.2 | 875.1 | 826.6 | 832.2 | 382.6 | 675.6 | 812.5 | 546.4 | 754.4 | 610.5 | 802.3 | 805.4 | 234.3 | 312.9 | 322.7 | 282.6 | 208.1 | 299.2 | 297.9 | 268.1
661 | 498 | 468.6 | 187.44 | 219.1066 | 296.1 | 306.9 | 290.4 | 295.4 | 391.2 | 42.4 | 20.1 | 77.8 | 3.6 | 164.2 | 1.7 | 893.4 | 779.4 | 871.2 | 827.6 | 829.5 | 382.9 | 676.5 | 809.2 | 547.1 | 753.8 | 614.8 | 804.2 | 805.8 | 234.7 | 312.9 | 322.8 | 282.8 | 208.5 | 299.2 | 297.8 | 268.4
662 | 499 | 469.7 | 187.88 | 219.6209 | 297 | 306.4 | 291.4 | 296.3 | 390 | 42.5 | 20.1 | 77.7 | 3.4 | 186 | 2.1 | 892.8 | 780.3 | 874.3 | 828.6 | 826.8 | 383.1 | 677.4 | 805.3 | 547.7 | 752.8 | 619.1 | 805.3 | 805.8 | 235 | 313.1 | 322.8 | 283.1 | 208.8 | 299.3 | 298 | 268.7
663 | 500 | 469 | 187.6 | 219.2936 | 298.3 | 305.1 | 292 | 296.6 | 394.4 | 42.5 | 20 | 77.6 | 3.5 | 211.6 | 2.4 | 890.5 | 781.5 | 876 | 829.8 | 828 | 383.2 | 681.2 | 804.1 | 548.2 | 753.1 | 622.4 | 804 | 805.5 | 235.4 | 313.5 | 322.9 | 283.6 | 209.1 | 299.5 | 298.4 | 268.9
664 | 501 | 468.1 | 187.24 | 218.8728 | 298.7 | 304.7 | 293 | 297.3 | 415 | 42.6 | 20 | 77.5 | 3.8 | 213.8 | 2.3 | 886.9 | 782.3 | 874.2 | 831.3 | 825.4 | 383.6 | 687.3 | 802.8 | 548.8 | 753.4 | 624.7 | 801.8 | 804.8 | 235.7 | 314.1 | 323.2 | 284.2 | 209.4 | 299.7 | 298.9 | 269.2
665 | 502 | 469.2 | 187.68 | 219.3871 | 298.9 | 305.6 | 293.8 | 297.7 | 417.3 | 42.7 | 20 | 77.5 | 3.5 | 213.8 | 2.5 | 886.9 | 784.3 | 877.1 | 833 | 826.5 | 383.8 | 687.1 | 804.2 | 549.4 | 753.5 | 626.8 | 801.8 | 804.4 | 236.1 | 314.5 | 323.4 | 284.6 | 209.7 | 299.8 | 299.3 | 269.5
666 | 503 | 468.8 | 187.52 | 219.2001 | 299.6 | 306.4 | 294.8 | 297.8 | 411.4 | 42.7 | 20 | 77.5 | 3.8 | 213.4 | 3 | 888.6 | 786 | 882.9 | 833.1 | 829.7 | 384.3 | 683.4 | 807.7 | 550 | 755.1 | 628.2 | 801.2 | 804.4 | 236.4 | 314.7 | 323.5 | 284.8 | 210 | 299.9 | 299.5 | 269.8
667 | 504 | 468.5 | 187.4 | 219.0598 | 299.5 | 307.2 | 294.4 | 298.4 | 406.7 | 42.8 | 20 | 77.5 | 4 | 207.1 | 3.1 | 889.4 | 785.2 | 883.1 | 832 | 831.4 | 385.1 | 682.6 | 810.7 | 550.6 | 757 | 627.9 | 801.3 | 804.1 | 236.8 | 315.3 | 323.6 | 285 | 210.3 | 299.8 | 300.3 | 270.2
668 | 505 | 468.8 | 187.52 | 219.2001 | 298 | 308.3 | 293.8 | 298.6 | 403.7 | 42.9 | 20 | 77.4 | 4.3 | 190.7 | 3.2 | 891.1 | 783.1 | 883.7 | 831.3 | 831.9 | 385.7 | 687.3 | 807.5 | 551.2 | 757.9 | 629.6 | 799 | 804 | 237.1 | 315.7 | 323.7 | 285.4 | 210.6 | 299.9 | 300.9 | 270.5
669 | 506 | 468.4 | 187.36 | 219.013 | 297.5 | 308.6 | 294 | 297.8 | 399.7 | 42.9 | 20 | 77.5 | 3.9 | 194.6 | 3.2 | 893.2 | 782.2 | 881.2 | 831.6 | 831.9 | 386.5 | 684.8 | 806.1 | 551.8 | 757.7 | 633 | 802.1 | 803.9 | 237.5 | 315.8 | 323.7 | 285.7 | 210.9 | 300 | 300.8 | 270.8
670 | 507 | 468 | 187.2 | 218.826 | 297.4 | 308.8 | 294.1 | 297.7 | 394.5 | 43 | 20 | 77.5 | 3.7 | 208.4 | 3.1 | 892.7 | 783.6 | 887.1 | 832.1 | 832.5 | 387 | 684.8 | 804.6 | 552.3 | 758.6 | 637.1 | 804.7 | 803.4 | 237.8 | 315.6 | 323.7 | 285.7 | 211.3 | 300.4 | 300.9 | 271
671 | 508 | 469.1 | 187.64 | 219.3403 | 297.3 | 308.7 | 293.8 | 297.8 | 391.7 | 43.2 | 20 | 77.6 | 3.6 | 201.4 | 3.3 | 891.7 | 783.8 | 880.9 | 831.8 | 834.2 | 387.7 | 686 | 807.4 | 552.9 | 760 | 639.5 | 802.5 | 803.2 | 238.2 | 315.4 | 323.6 | 285.7 | 211.6 | 300.7 | 301.1 | 271.3
672 | 509 | 467.5 | 187 | 218.5922 | 298.4 | 307.9 | 293.1 | 298 | 391.2 | 43.4 | 20 | 77.6 | 4.2 | 183.9 | 3.8 | 891.1 | 782.1 | 880.4 | 831 | 834.9 | 388.4 | 685.8 | 812.1 | 553.4 | 761.2 | 640.9 | 800.8 | 803.1 | 238.5 | 315.1 | 323.5 | 285.8 | 211.9 | 301 | 301.2 | 271.5
673 | 510 | 469 | 187.6 | 219.2936 | 298.7 | 307.6 | 292.2 | 298 | 387.5 | 43.4 | 20 | 77.7 | 4.3 | 179.5 | 4.8 | 888.3 | 781 | 881.4 | 830.2 | 835.9 | 388.9 | 683.1 | 814.9 | 553.9 | 761.6 | 644.6 | 800.8 | 803 | 238.8 | 314.8 | 323.6 | 285.9 | 212.2 | 301.4 | 301.3 | 271.7
674 | 511 | 469.5 | 187.8 | 219.5274 | 298.7 | 307.2 | 291.8 | 298 | 382.7 | 43.4 | 20 | 77.7 | 3.9 | 172.6 | 5.4 | 883.4 | 780.2 | 877 | 828.6 | 838 | 389.4 | 683.3 | 817.8 | 554.4 | 763.2 | 648 | 800.5 | 802.5 | 239.2 | 314.7 | 323.5 | 286.1 | 212.5 | 301.9 | 301.5 | 272
675 | 512 | 469.2 | 187.68 | 219.3871 | 298.5 | 306.8 | 291.9 | 298.5 | 382 | 43.5 | 20 | 77.6 | 4.1 | 170.3 | 5.2 | 885.3 | 780.7 | 876.9 | 828.4 | 837.9 | 390.2 | 693 | 818.4 | 555 | 763.8 | 648.5 | 803.9 | 801.9 | 239.5 | 314.7 | 323.7 | 286.2 | 212.8 | 302.3 | 301.5 | 272.3
676 | 513 | 468.6 | 187.44 | 219.1066 | 297 | 307.5 | 292.2 | 299.2 | 383 | 43.5 | 20 | 77.7 | 4.1 | 165 | 4.8 | 893 | 781.2 | 874.4 | 829.4 | 835.7 | 390.9 | 695.8 | 817.6 | 555.5 | 762.8 | 650.6 | 804.2 | 802.3 | 239.9 | 314.6 | 323.8 | 286.5 | 213.2 | 302.5 | 301.3 | 272.5
677 | 514 | 469.4 | 187.76 | 219.4806 | 296 | 307.3 | 292.5 | 299.1 | 381.4 | 43.6 | 20 | 77.7 | 3.8 | 179.1 | 5.1 | 896.1 | 781.2 | 869.3 | 831.2 | 831.4 | 391.1 | 692.8 | 816.4 | 555.9 | 762 | 653.5 | 806.4 | 802.8 | 240.2 | 314.7 | 323.9 | 286.8 | 213.5 | 302.9 | 301.4 | 272.8
678 | 515 | 469.7 | 187.88 | 219.6209 | 296.3 | 306.4 | 292.5 | 298.5 | 383.1 | 43.7 | 20 | 77.7 | 3.7 | 193.4 | 5.6 | 897.7 | 782.2 | 867.9 | 832.8 | 827.7 | 391.3 | 698.5 | 812.8 | 556.2 | 761.2 | 655.1 | 806.6 | 803.1 | 240.5 | 314.9 | 323.9 | 287.2 | 213.8 | 303.1 | 301.6 | 273.1
679 | 516 | 469.6 | 187.84 | 219.5741 | 296.7 | 305.3 | 293.3 | 298.1 | 380 | 43.7 | 20 | 77.7 | 4.1 | 186.3 | 5.6 | 897 | 783.1 | 862.1 | 833.5 | 823.4 | 391.4 | 701 | 813 | 556.6 | 760.7 | 657.7 | 809.2 | 803.6 | 240.8 | 315.1 | 324 | 287.7 | 214.1 | 303.1 | 301.8 | 273.3
680 | 517 | 469.9 | 187.96 | 219.7144 | 298.4 | 304.5 | 294.1 | 298.6 | 376.9 | 43.8 | 20 | 77.7 | 4.2 | 185.1 | 5.1 | 894.5 | 784 | 859.9 | 834.2 | 820.3 | 391.4 | 696.5 | 809.5 | 557 | 759.9 | 660 | 810.9 | 804.7 | 241.2 | 315.3 | 324 | 288 | 214.5 | 303.2 | 302.5 | 273.7
681 | 518 | 469.3 | 187.72 | 219.4339 | 300.4 | 304.3 | 294.1 | 298.9 | 382.5 | 43.9 | 20 | 77.9 | 4 | 179.8 | 4.9 | 891.8 | 785.3 | 857.8 | 835.3 | 819 | 391.4 | 699.7 | 802.8 | 557.4 | 759.2 | 663 | 809.4 | 805.5 | 241.5 | 315.5 | 324.4 | 288.2 | 214.8 | 303.1 | 303 | 274
682 | 519 | 468.4 | 187.36 | 219.013 | 301.3 | 305.3 | 294.9 | 298.9 | 382.1 | 44 | 20 | 78 | 4 | 171.3 | 5 | 891 | 786.6 | 859.3 | 835.9 | 817.8 | 391.6 | 699.4 | 803.3 | 557.9 | 759.7 | 666 | 808.9 | 806.2 | 241.8 | 315.8 | 324.9 | 288.4 | 215.1 | 303 | 303.3 | 274.3
683 | 520 | 468.9 | 187.56 | 219.2468 | 302.3 | 306.1 | 295.4 | 299.5 | 382.2 | 44 | 20 | 78.1 | 3.7 | 171.6 | 5.1 | 891.6 | 786.5 | 861.3 | 835.4 | 817.2 | 391.7 | 691.4 | 804.2 | 558.2 | 759.3 | 667.9 | 806.7 | 806.8 | 242.2 | 316 | 325 | 288.7 | 215.4 | 302.8 | 303.3 | 274.6
684 | 521 | 468.8 | 187.52 | 219.2001 | 303 | 305.4 | 295.6 | 299.4 | 383 | 44.1 | 20 | 78.3 | 4.3 | 180.5 | 5.2 | 892.8 | 786.5 | 866.1 | 835.3 | 817.3 | 391.9 | 689.4 | 805.5 | 558.6 | 758.9 | 670 | 806.2 | 807.1 | 242.5 | 316 | 324.8 | 289 | 215.7 | 302.9 | 303.2 | 274.8
685 | 522 | 467.8 | 187.12 | 218.7325 | 304.1 | 305.3 | 295.9 | 298.8 | 388.4 | 44.2 | 20 | 78.5 | 4.7 | 180.5 | 5.1 | 893.1 | 786.6 | 872.4 | 835 | 820.5 | 392.1 | 688.7 | 806 | 558.9 | 759.6 | 671.4 | 802.6 | 806.8 | 242.8 | 316.1 | 324.9 | 289.2 | 216.1 | 303.1 | 303 | 275
686 | 523 | 468.3 | 187.32 | 218.9663 | 304 | 305.5 | 295.8 | 298.7 | 386.9 | 44.2 | 20 | 78.6 | 4.5 | 178.5 | 4.8 | 894.8 | 787.7 | 873.5 | 835.8 | 823.1 | 392.6 | 686.4 | 808.3 | 559.4 | 759.8 | 672.1 | 809.1 | 806.6 | 243.1 | 316 | 325 | 289.5 | 216.4 | 303.1 | 302.9 | 275.3
687 | 524 | 467.1 | 186.84 | 218.4052 | 303.7 | 306.7 | 296 | 298.6 | 384.1 | 44.3 | 20 | 78.7 | 3.4 | 173.4 | 4.6 | 894.2 | 788.1 | 874.8 | 836 | 826 | 393.1 | 685.7 | 809.3 | 559.8 | 761.1 | 673.9 | 809.2 | 806.5 | 243.4 | 316 | 325.1 | 289.7 | 216.8 | 303.3 | 302.8 | 275.5
688 | 525 | 467.7 | 187.08 | 218.6857 | 303.5 | 307.2 | 295.7 | 297.6 | 383.8 | 44.3 | 20 | 78.8 | 3.3 | 170.6 | 4.3 | 896.6 | 787.5 | 882.1 | 835.8 | 828.5 | 393.5 | 685.3 | 805.7 | 560.1 | 760.8 | 673.3 | 807.3 | 806 | 243.7 | 315.9 | 325.1 | 289.8 | 217.1 | 303 | 303 | 275.7
689 | 526 | 467.9 | 187.16 | 218.7793 | 303.5 | 306.6 | 295.8 | 296.5 | 394.4 | 44.3 | 20 | 79 | 3.5 | 188.9 | 4 | 895.9 | 787.4 | 879.8 | 836.3 | 826.3 | 394 | 689.4 | 801.2 | 560.4 | 760.2 | 673.8 | 806.7 | 805.1 | 244.1 | 316 | 325.4 | 290.1 | 217.4 | 303.1 | 303.1 | 275.9
690 | 527 | 468.4 | 187.36 | 219.013 | 303.9 | 306.3 | 296.1 | 295.9 | 399.2 | 44.4 | 20 | 79.1 | 3.5 | 215.1 | 3.9 | 893.3 | 787.5 | 873.2 | 836.7 | 824.3 | 394.3 | 690.1 | 802.2 | 560.7 | 759.9 | 674.4 | 808.1 | 803.9 | 244.4 | 316.2 | 325.6 | 290.6 | 217.8 | 303.3 | 303.1 | 276.1
691 | 528 | 467.5 | 187 | 218.5922 | 304.1 | 306.2 | 296.6 | 296.4 | 402.9 | 44.4 | 20 | 79.3 | 3.8 | 212.5 | 3.6 | 890.4 | 787.1 | 865.2 | 837.3 | 822.9 | 394.4 | 695.3 | 805.8 | 561.1 | 760.4 | 675.6 | 806.9 | 802.3 | 244.7 | 316.8 | 325.9 | 291.1 | 218.1 | 303.7 | 303.2 | 276.4
692 | 529 | 467.6 | 187.04 | 218.639 | 305 | 306.5 | 297 | 297.6 | 406.8 | 44.4 | 20 | 79.5 | 3.9 | 183.4 | 3.4 | 892 | 786.9 | 869.8 | 837.3 | 824.5 | 394.7 | 697.7 | 809.2 | 561.3 | 761.2 | 674.2 | 808.8 | 800.7 | 244.9 | 317.5 | 326.1 | 291.6 | 218.5 | 304.1 | 303.2 | 276.7
693 | 530 | 467.5 | 187 | 218.5922 | 305.7 | 306.4 | 296.9 | 298.5 | 408 | 44.4 | 20 | 79.6 | 4.2 | 168.5 | 3.6 | 893.5 | 785.7 | 875.5 | 837.3 | 828.7 | 395.1 | 692.8 | 804.4 | 561.4 | 761 | 671.1 | 806.8 | 798.8 | 245.1 | 317.8 | 326.5 | 291.9 | 218.8 | 304.6 | 303.4 | 277
694 | 531 | 467.9 | 187.16 | 218.7793 | 305.9 | 306.4 | 297.1 | 299.5 | 413.1 | 44.4 | 20 | 79.8 | 4.3 | 182.9 | 3.9 | 891.6 | 784.7 | 877.7 | 837.6 | 829.3 | 395.8 | 693.8 | 806.9 | 561.6 | 762.7 | 668.9 | 805.7 | 796.4 | 245.3 | 318.2 | 327.2 | 292.4 | 219.2 | 305 | 303.6 | 277.3
695 | 532 | 468.6 | 187.44 | 219.1066 | 305.8 | 307.8 | 297.2 | 300.4 | 423.2 | 44.3 | 20 | 79.9 | 4.1 | 185.2 | 4 | 889.9 | 784.3 | 882.9 | 838.3 | 830.3 | 396.5 | 694 | 807.2 | 561.8 | 763.5 | 666.9 | 804.8 | 794.1 | 245.6 | 318.7 | 327.7 | 292.7 | 219.5 | 305.6 | 303.7 | 277.5
696 | 533 | 468.8 | 187.52 | 219.2001 | 305.9 | 310 | 297.1 | 301.6 | 434.6 | 44.3 | 20 | 80 | 3.9 | 172.7 | 4.1 | 885.4 | 784.2 | 873.4 | 839.9 | 828.3 | 397.3 | 696.9 | 807.1 | 562 | 764 | 666.9 | 802 | 792.2 | 245.8 | 319.2 | 328.1 | 293.1 | 219.9 | 305.8 | 303.9 | 277.8
697 | 534 | 468.3 | 187.32 | 218.9663 | 305.7 | 310.7 | 297.5 | 302.4 | 433.3 | 44.4 | 20 | 80.1 | 4.6 | 155.1 | 3.9 | 882.7 | 783.8 | 871.6 | 840.9 | 830.4 | 397.9 | 707.9 | 805.2 | 562.1 | 764.7 | 666.4 | 798.1 | 790.1 | 246.2 | 319.5 | 328.4 | 293.4 | 220.2 | 306.2 | 304 | 278
698 | 535 | 468.3 | 187.32 | 218.9663 | 305.4 | 310.7 | 298 | 302.3 | 438.6 | 44.5 | 20 | 80.2 | 3.7 | 155.6 | 3.7 | 882.1 | 783.2 | 873.4 | 841 | 833.1 | 398.4 | 707.4 | 803.4 | 562.3 | 764.6 | 666.5 | 797.9 | 788 | 246.5 | 319.9 | 328.6 | 293.5 | 220.6 | 306.6 | 304.3 | 278.3
699 | 536 | 467.7 | 187.08 | 218.6857 | 304.2 | 311.6 | 298 | 302.3 | 454 | 44.6 | 20 | 80.3 | 3.9 | 187.1 | 3.6 | 885.6 | 783 | 873.5 | 840.7 | 833.3 | 398.9 | 708.8 | 803.8 | 562.4 | 765.5 | 665.5 | 801.2 | 786.1 | 246.8 | 320.4 | 329 | 293.8 | 221 | 306.9 | 304.6 | 278.6
700 | 537 | 467.5 | 187 | 218.5922 | 302.2 | 314.3 | 298.6 | 302.8 | 450.6 | 44.6 | 20 | 80.4 | 4 | 212.7 | 3.7 | 888.2 | 782.8 | 875.4 | 841.2 | 832.1 | 399.7 | 708.9 | 803.8 | 562.5 | 765.2 | 665 | 801.6 | 785.2 | 247.2 | 320.9 | 329.5 | 294 | 221.3 | 307.1 | 304.8 | 278.9
701 | 538 | 468.5 | 187.4 | 219.0598 | 301.6 | 316.2 | 298.9 | 302.9 | 449.3 | 44.6 | 20 | 80.5 | 4.6 | 178.6 | 4.2 | 886.6 | 782.4 | 873.7 | 842.1 | 831.1 | 400.3 | 720.4 | 798.4 | 562.7 | 764.6 | 666.7 | 797.9 | 785 | 247.5 | 321.4 | 330.1 | 294.3 | 221.7 | 307.5 | 305.1 | 279.2
702 | 539 | 468.6 | 187.44 | 219.1066 | 302 | 316.9 | 299.7 | 303.3 | 441.4 | 44.7 | 20 | 80.5 | 4.2 | 187.1 | 5.1 | 889.6 | 782.6 | 871.2 | 842.3 | 829.6 | 400.6 | 719.4 | 793.6 | 562.9 | 763.9 | 668.4 | 800.8 | 785.6 | 247.9 | 321.6 | 330.4 | 294.4 | 222 | 308 | 305.4 | 279.5
703 | 540 | 468.6 | 187.44 | 219.1066 | 302.4 | 316 | 300.3 | 303.6 | 440.3 | 44.8 | 20 | 80.5 | 4.4 | 190.8 | 5.4 | 890.5 | 782.8 | 866.7 | 842.1 | 828.6 | 400.8 | 711.7 | 796.8 | 563 | 764.2 | 668.8 | 799.7 | 786.9 | 248.2 | 321.9 | 330.5 | 294.6 | 222.4 | 308.5 | 305.9 | 279.7
704 | 541 | 468.5 | 187.4 | 219.0598 | 302.1 | 315.5 | 300.5 | 303.4 | 433.7 | 44.7 | 20 | 80.5 | 4 | 193 | 5.5 | 891.2 | 783.3 | 863.4 | 842.6 | 830 | 401.2 | 703.9 | 797.3 | 563.1 | 764.9 | 668.1 | 798.1 | 788.1 | 248.6 | 321.9 | 330.6 | 294.7 | 222.7 | 308.4 | 306.3 | 280.1
705 | 542 | 468.1 | 187.24 | 218.8728 | 301.1 | 314.4 | 300.5 | 303.1 | 427 | 44.8 | 20 | 80.7 | 3.7 | 199.9 | 5.6 | 887 | 783.9 | 853.1 | 843.7 | 827.1 | 401.8 | 698.1 | 792.3 | 563.3 | 764.2 | 667.7 | 796.4 | 788.9 | 248.9 | 322 | 330.6 | 294.9 | 223.1 | 308.7 | 306.7 | 280.5
706 | 543 | 467.2 | 186.88 | 218.452 | 299 | 313.9 | 300.3 | 303 | 419.6 | 44.9 | 20 | 80.8 | 4.6 | 199.5 | 6 | 886.6 | 784.4 | 852.9 | 844 | 826.7 | 402.1 | 694.7 | 789.9 | 563.5 | 763.1 | 669.9 | 798.9 | 789.3 | 249.3 | 321.9 | 330.8 | 295.1 | 223.5 | 308.9 | 307.1 | 280.8
707 | 544 | 467.7 | 187.08 | 218.6857 | 297.2 | 313.7 | 299.6 | 304.1 | 418.7 | 45 | 20 | 81 | 4.3 | 196.1 | 6 | 886.3 | 784.6 | 858.6 | 844.7 | 824.6 | 402.1 | 691.6 | 791.4 | 563.6 | 763.2 | 670.3 | 797.1 | 788.8 | 249.6 | 321.9 | 330.8 | 295.3 | 223.8 | 308.9 | 307.2 | 281
708 | 545 | 470.3 | 188.12 | 219.9014 | 296.7 | 313.2 | 299.5 | 304.4 | 415.2 | 45 | 20 | 81 | 4.1 | 185.1 | 5.8 | 885.9 | 785.8 | 864.8 | 845.5 | 825 | 402.4 | 693.9 | 797.7 | 563.7 | 764.3 | 668.8 | 800.3 | 788.3 | 250 | 321.8 | 330.6 | 295.4 | 224.2 | 309.1 | 307.2 | 281.2
709 | 546 | 471.2 | 188.48 | 220.3223 | 296 | 313.7 | 299.8 | 304.4 | 410.8 | 45 | 19.9 | 81 | 4.4 | 181 | 5.7 | 890 | 786.2 | 867.8 | 845.1 | 826.2 | 402.9 | 690.7 | 801.4 | 563.9 | 764.7 | 666.9 | 802.3 | 788.2 | 250.3 | 321.7 | 330.4 | 295.7 | 224.6 | 309 | 307.4 | 281.5
710 | 547 | 470.3 | 188.12 | 219.9014 | 294.6 | 313.1 | 299.4 | 304.5 | 409.2 | 45.2 | 20 | 81.1 | 3.8 | 170.1 | 5.7 | 893.2 | 786.9 | 871.6 | 845.5 | 827.3 | 403.3 | 690.1 | 802.7 | 564 | 765.2 | 665.1 | 801.7 | 787.9 | 250.7 | 321.7 | 330.7 | 295.8 | 224.9 | 309.1 | 307.5 | 281.7
711 | 548 | 468.3 | 187.32 | 218.9663 | 295.1 | 311.5 | 299.4 | 304.3 | 407.7 | 45.2 | 20 | 81.2 | 4.3 | 183.7 | 5.6 | 892.6 | 787.2 | 877.1 | 845.1 | 829.1 | 403.9 | 687.9 | 802.7 | 564.2 | 765.5 | 662.8 | 801 | 786.9 | 251 | 321.6 | 330.8 | 295.9 | 225.3 | 308.9 | 307.4 | 281.9
712 | 549 | 467.6 | 187.04 | 218.639 | 295 | 311.3 | 299.5 | 304.4 | 406.3 | 45.2 | 19.9 | 81.5 | 4.6 | 190.1 | 5.7 | 892 | 788 | 875.1 | 845.2 | 829.7 | 404.6 | 687.1 | 801.6 | 564.3 | 766.9 | 659.1 | 803.1 | 785.9 | 251.3 | 321.6 | 330.6 | 296 | 225.6 | 308.7 | 307.3 | 282.1
713 | 550 | 468.5 | 187.4 | 219.0598 | 295.2 | 312.4 | 299.4 | 304.4 | 415.8 | 45.2 | 19.9 | 81.6 | 4.9 | 169.1 | 5.5 | 889.9 | 789.2 | 867.7 | 846.9 | 828.5 | 405.4 | 690.1 | 801 | 564.5 | 766.4 | 658.5 | 804.1 | 785.1 | 251.6 | 321.8 | 330.8 | 296.4 | 226 | 308.5 | 307.4 | 282.2
714 | 551 | 468.3 | 187.32 | 218.9663 | 295.7 | 312.8 | 299.4 | 304.2 | 420.6 | 45.3 | 19.9 | 81.6 | 4.2 | 170.8 | 5.5 | 888.1 | 790.3 | 871.6 | 847.5 | 830 | 406 | 685.3 | 801.4 | 564.7 | 766.5 | 659.3 | 804.7 | 783.7 | 251.9 | 321.9 | 330.9 | 296.6 | 226.3 | 308.3 | 307.6 | 282.4
715 | 552 | 469.8 | 187.92 | 219.6677 | 297 | 313.2 | 299.4 | 303.6 | 415 | 45.4 | 19.9 | 81.7 | 4 | 184.1 | 5.3 | 888 | 790.4 | 875.2 | 847.2 | 832 | 406.6 | 691.5 | 801.6 | 564.8 | 767.5 | 659.9 | 804.9 | 782.2 | 252.2 | 321.8 | 330.8 | 296.7 | 226.7 | 308.3 | 307.5 | 282.7
716 | 553 | 469 | 187.6 | 219.2936 | 297.3 | 313.4 | 299.1 | 303.3 | 412 | 45.3 | 19.9 | 81.8 | 4.1 | 188.1 | 4.9 | 886 | 789.8 | 874.8 | 847.1 | 833.7 | 407.2 | 694.1 | 801.9 | 565 | 768 | 659.1 | 805.3 | 780.5 | 252.5 | 321.7 | 330.7 | 296.9 | 227 | 308.2 | 307.4 | 282.8
717 | 554 | 469.7 | 187.88 | 219.6209 | 298.2 | 314.4 | 298.6 | 303.2 | 423.6 | 45.3 | 19.9 | 81.9 | 3.9 | 189.7 | 4.8 | 880.6 | 789.2 | 867.5 | 847.3 | 831 | 407.9 | 702.7 | 804.2 | 565.2 | 769 | 657.5 | 800.1 | 778.3 | 252.7 | 321.8 | 330.7 | 297.1 | 227.3 | 308.1 | 307.2 | 282.9
718 | 555 | 468.7 | 187.48 | 219.1533 | 299.1 | 314.8 | 297.8 | 303 | 432.3 | 45.4 | 19.9 | 81.9 | 3.5 | 186.8 | 5.4 | 880 | 788.7 | 870.3 | 847.3 | 829.2 | 408.4 | 701.4 | 799.1 | 565.4 | 767.5 | 657.6 | 796.6 | 776 | 253 | 322 | 330.9 | 297.5 | 227.6 | 308.1 | 307.1 | 283
719 | 556 | 469.5 | 187.8 | 219.5274 | 298.6 | 315.7 | 297.6 | 303.6 | 445 | 45.4 | 19.9 | 81.8 | 3.7 | 181.5 | 5.4 | 884.1 | 788.9 | 873.2 | 847.3 | 828.4 | 408.8 | 706.6 | 801 | 565.6 | 768.7 | 657.2 | 798.6 | 775 | 253.3 | 322.1 | 331.3 | 297.9 | 228 | 308.4 | 307.1 | 283.2
720 | 557 | 468.9 | 187.56 | 219.2468 | 299.3 | 316.7 | 298.1 | 304.1 | 438.3 | 45.4 | 19.9 | 81.8 | 4.5 | 183.3 | 5.2 | 887.1 | 788.5 | 876.9 | 846.8 | 830.2 | 409.2 | 701 | 803 | 565.7 | 769.1 | 656.5 | 797.5 | 774.5 | 253.6 | 322.3 | 331.8 | 298.2 | 228.3 | 308.7 | 307 | 283.4
721 | 558 | 468.6 | 187.44 | 219.1066 | 301.5 | 315.6 | 298.5 | 304.3 | 439.5 | 45.5 | 19.9 | 81.8 | 4.4 | 195.5 | 5 | 888.1 | 788.8 | 876.3 | 846.2 | 829.5 | 409.7 | 697.3 | 802.3 | 565.9 | 769.4 | 655.5 | 800.1 | 775.4 | 253.9 | 322.6 | 331.9 | 298.4 | 228.6 | 309 | 307 | 283.7
722 | 559 | 469 | 187.6 | 219.2936 | 302.2 | 314.9 | 299.1 | 304.4 | 434.7 | 45.6 | 19.9 | 81.8 | 4.4 | 202.7 | 5 | 888.1 | 788.5 | 884.7 | 845.6 | 832.1 | 410.3 | 689.5 | 804.4 | 566.1 | 769.5 | 654.6 | 799.1 | 775.5 | 254.2 | 322.7 | 331.8 | 298.5 | 228.9 | 308.7 | 307.1 | 283.9
723 | 560 | 468.8 | 187.52 | 219.2001 | 303.2 | 314 | 298.9 | 304.9 | 438.1 | 45.6 | 19.9 | 81.7 | 4.4 | 211.2 | 5.1 | 885.3 | 788.5 | 881.1 | 845.9 | 830.3 | 410.9 | 692.4 | 804.3 | 566.3 | 769.5 | 654.8 | 797.4 | 775.2 | 254.6 | 322.8 | 331.9 | 298.7 | 229.2 | 308.6 | 307.1 | 284.1
724 | 561 | 468.4 | 187.36 | 219.013 | 304 | 314.1 | 298.7 | 304.5 | 443.3 | 45.6 | 19.9 | 81.6 | 4.2 | 213.5 | 5.4 | 885 | 789.1 | 875.2 | 846.2 | 829.6 | 411.2 | 696 | 804.3 | 566.5 | 769.3 | 655.4 | 794.8 | 775.2 | 254.9 | 323.1 | 332 | 299 | 229.6 | 308.8 | 307.2 | 284.3
725 | 562 | 468.5 | 187.4 | 219.0598 | 304.6 | 313.5 | 299.6 | 303.9 | 437.4 | 45.5 | 19.9 | 81.7 | 4.7 | 194.3 | 5 | 886.4 | 790 | 876.9 | 846.2 | 831.4 | 411.4 | 691.6 | 804.1 | 566.8 | 769.2 | 655.9 | 798.8 | 775.2 | 255.2 | 323.2 | 332.1 | 299.2 | 229.9 | 308.9 | 307.1 | 284.6
726 | 563 | 468.9 | 187.56 | 219.2468 | 305.5 | 314.1 | 300.2 | 303.3 | 431 | 45.5 | 19.9 | 81.8 | 3.9 | 184.4 | 4.8 | 888.3 | 790.2 | 879.9 | 845.8 | 834.3 | 411.8 | 685.1 | 804.9 | 567 | 769.7 | 656.5 | 799.5 | 774.8 | 255.5 | 323.2 | 332.2 | 299.2 | 230.2 | 308.9 | 306.9 | 284.7
727 | 564 | 468.8 | 187.52 | 219.2001 | 305.9 | 314.3 | 300.7 | 302.9 | 425.6 | 45.6 | 19.9 | 81.9 | 4.1 | 193.6 | 4.7 | 891 | 789.8 | 888.3 | 844.7 | 836.9 | 412.3 | 686.1 | 805.5 | 567.2 | 770.5 | 655.6 | 799.7 | 775.1 | 255.8 | 323 | 331.9 | 299.2 | 230.5 | 309 | 306.8 | 284.9
728 | 565 | 468.5 | 187.4 | 219.0598 | 305.5 | 314 | 300.9 | 302.4 | 419.5 | 45.6 | 19.9 | 82 | 4.2 | 203.5 | 4.7 | 892.9 | 789.3 | 889 | 844 | 840.1 | 413 | 682.1 | 803.3 | 567.4 | 770.6 | 654.6 | 802.4 | 775 | 256.1 | 323 | 331.7 | 299.3 | 230.8 | 308.9 | 306.7 | 285.1
729 | 566 | 468.5 | 187.4 | 219.0598 | 305.1 | 314.5 | 300.7 | 301.8 | 412.3 | 45.6 | 19.9 | 82.1 | 3.6 | 197.2 | 5.3 | 893.2 | 789 | 886.2 | 843.6 | 842.5 | 413.7 | 674.3 | 802.9 | 567.7 | 770.3 | 653 | 804.8 | 774.8 | 256.3 | 322.8 | 331.5 | 299.4 | 231.2 | 308.9 | 306.6 | 285.2
730 | 567 | 468.9 | 187.56 | 219.2468 | 304.5 | 314.3 | 300.3 | 301.5 | 410.2 | 45.7 | 19.9 | 82.1 | 3.6 | 189.1 | 5.3 | 891.9 | 789.3 | 883.2 | 844.2 | 844.3 | 414.3 | 670.9 | 801.3 | 568 | 771.1 | 652.5 | 806.7 | 774.6 | 256.6 | 322.6 | 331.1 | 299.5 | 231.5 | 309.1 | 306.8 | 285.4
731 | 568 | 468.5 | 187.4 | 219.0598 | 303.7 | 312.9 | 300 | 301.3 | 406.7 | 45.8 | 19.9 | 82.3 | 4 | 215.8 | 5.4 | 895.3 | 788.6 | 887.4 | 843.7 | 845 | 414.9 | 676.5 | 799.7 | 568.3 | 771.7 | 652.6 | 806.1 | 774.8 | 256.8 | 322.3 | 330.7 | 299.6 | 231.8 | 309.5 | 306.8 | 285.6
732 | 569 | 468.5 | 187.4 | 219.0598 | 303.6 | 312.5 | 299.4 | 301.6 | 404.1 | 45.8 | 19.9 | 82.3 | 4 | 200.6 | 6.8 | 895.2 | 788.5 | 887.5 | 844.3 | 844.5 | 415.6 | 679.9 | 800.1 | 568.6 | 773.1 | 652.3 | 806.3 | 774.6 | 257.1 | 322.1 | 330.4 | 299.8 | 232.1 | 309.9 | 306.9 | 285.8
733 | 570 | 468.3 | 187.32 | 218.9663 | 304 | 312.6 | 298.4 | 302 | 407.1 | 45.9 | 19.9 | 82.4 | 4.4 | 209.5 | 7.2 | 891.1 | 788.1 | 879.6 | 845.1 | 843.2 | 416.2 | 683.9 | 797.7 | 568.9 | 772.9 | 652.7 | 804.9 | 774.1 | 257.4 | 322.1 | 330.6 | 300.2 | 232.4 | 310 | 306.9 | 285.9
734 | 571 | 468.4 | 187.36 | 219.013 | 305.1 | 312.6 | 298.4 | 302.1 | 409.9 | 46 | 19.9 | 82.4 | 4 | 224.8 | 6.5 | 885.5 | 786.9 | 867.1 | 845.6 | 837.9 | 416.6 | 688 | 788.2 | 569.2 | 770.3 | 654.4 | 799.1 | 774.2 | 257.6 | 322.1 | 330.8 | 300.5 | 232.7 | 310.2 | 306.9 | 286
735 | 572 | 467.7 | 187.08 | 218.6857 | 305.9 | 312.7 | 299 | 302.1 | 410 | 46.1 | 19.9 | 82.5 | 4.4 | 214.6 | 5.7 | 880.6 | 786.1 | 862 | 846.1 | 835.3 | 416.5 | 690.2 | 789.9 | 569.6 | 770.4 | 655.8 | 797.6 | 773.8 | 257.9 | 322.4 | 331.2 | 300.9 | 233 | 310.5 | 307.1 | 286.2
736 | 573 | 467.5 | 187 | 218.5922 | 306.6 | 312.1 | 299.5 | 302.9 | 416.1 | 46.2 | 19.9 | 82.6 | 4.5 | 224.4 | 5.4 | 877 | 786.1 | 859.4 | 847.2 | 832.1 | 417 | 697.2 | 786.7 | 570 | 770.5 | 656 | 794.2 | 773.5 | 258.1 | 322.9 | 331.7 | 301.3 | 233.3 | 311 | 307.1 | 286.5
737 | 574 | 468.1 | 187.24 | 218.8728 | 305.8 | 311.7 | 300.3 | 304.3 | 415.5 | 46.3 | 19.9 | 82.6 | 4.8 | 225.7 | 4.9 | 873.6 | 786 | 851.8 | 848.1 | 828.5 | 417.2 | 697.3 | 782.3 | 570.4 | 769.1 | 656.2 | 791.1 | 773.1 | 258.3 | 323.6 | 332.1 | 301.6 | 233.7 | 311.4 | 307.4 | 286.8
738 | 575 | 468.5 | 187.4 | 219.0598 | 305.1 | 312.7 | 301.2 | 305.2 | 417.3 | 46.4 | 19.9 | 82.5 | 4.6 | 225.1 | 5 | 868.9 | 785.6 | 836.1 | 848.6 | 821.1 | 417.4 | 698.8 | 781.3 | 570.7 | 767.8 | 657.2 | 787.5 | 774 | 258.5 | 324.4 | 332.4 | 302 | 234 | 311.6 | 307.8 | 287
739 | 576 | 467.9 | 187.16 | 218.7793 | 305.7 | 313.3 | 301.5 | 305.6 | 418.8 | 46.5 | 19.9 | 82.5 | 4.4 | 207.4 | 6.3 | 869.8 | 786 | 840.1 | 849.1 | 818.2 | 417.6 | 695.3 | 788.3 | 571.1 | 768.4 | 658.6 | 790.1 | 773.2 | 258.7 | 324.8 | 333 | 302.4 | 234.3 | 311.9 | 308.1 | 287.2
740 | 577 | 468.9 | 187.56 | 219.2468 | 306.4 | 313.9 | 301.1 | 306.1 | 423.5 | 46.5 | 19.9 | 82.7 | 4.3 | 223 | 7 | 875.1 | 786.5 | 840.5 | 849 | 817.5 | 418 | 691.6 | 795.1 | 571.4 | 769.9 | 657.2 | 793.6 | 773 | 258.9 | 325 | 333.2 | 302.6 | 234.6 | 312 | 308.6 | 287.4
741 | 578 | 469.2 | 187.68 | 219.3871 | 307.5 | 315.3 | 301.4 | 306.8 | 420 | 46.5 | 19.9 | 82.8 | 4.4 | 213.2 | 7.1 | 877.4 | 786.5 | 841.3 | 849 | 816.4 | 418.6 | 686 | 796.3 | 571.7 | 769.6 | 656.5 | 793.7 | 772.9 | 259.1 | 325.3 | 333.7 | 302.7 | 234.9 | 312.1 | 308.8 | 287.6
742 | 579 | 469.5 | 187.8 | 219.5274 | 307.6 | 316.1 | 301.3 | 307.3 | 417.9 | 46.6 | 19.9 | 83 | 4.4 | 206.8 | 6.4 | 878 | 786.2 | 845.8 | 849.2 | 815.8 | 419.1 | 687.3 | 798.7 | 571.9 | 770.2 | 655.2 | 795.1 | 772.6 | 259.3 | 325.6 | 334.2 | 302.9 | 235.2 | 312 | 309 | 287.9
743 | 580 | 469.7 | 187.88 | 219.6209 | 306.4 | 315.3 | 302 | 308 | 415.4 | 46.7 | 19.9 | 83 | 4.1 | 180.5 | 5.6 | 870.6 | 785.6 | 835.2 | 849.5 | 810.3 | 419.6 | 692 | 788.8 | 572.2 | 767.8 | 655.2 | 786.9 | 772.8 | 259.6 | 326 | 334.7 | 303.3 | 235.6 | 312.1 | 309.1 | 288.2
744 | 581 | 468.9 | 187.56 | 219.2468 | 306.2 | 314.6 | 302.7 | 308.9 | 412.2 | 46.8 | 19.9 | 83.1 | 4.3 | 194.6 | 4.9 | 863.2 | 783.6 | 824.1 | 849.5 | 803 | 419.6 | 695.9 | 775.7 | 572.6 | 764 | 656.7 | 771.8 | 771.8 | 259.8 | 326.4 | 335.2 | 303.6 | 235.9 | 312.5 | 309.3 | 288.3
745 | 582 | 469.2 | 187.68 | 219.3871 | 307.4 | 314.7 | 303.6 | 309.1 | 416 | 46.9 | 19.9 | 83.2 | 4.8 | 222 | 5.5 | 858.9 | 782.4 | 817.7 | 849.7 | 798.3 | 419.6 | 700.5 | 766.8 | 572.9 | 762.8 | 658.1 | 763.4 | 770.6 | 260 | 327 | 335.8 | 304.1 | 236.2 | 313.2 | 309.7 | 288.5
746 | 583 | 469.7 | 187.88 | 219.6209 | 308.1 | 314 | 305.1 | 310 | 422 | 46.9 | 19.9 | 83.3 | 4.4 | 197.7 | 5.4 | 857.8 | 782 | 820 | 849.9 | 794.1 | 419.8 | 705.6 | 762.3 | 573.2 | 762 | 658.7 | 761.7 | 770.3 | 260.2 | 327.6 | 336.7 | 304.6 | 236.5 | 313.9 | 310.3 | 288.8
747 | 584 | 468.8 | 187.52 | 219.2001 | 306.7 | 312.9 | 306 | 311.8 | 425.1 | 46.9 | 19.9 | 83.4 | 4.4 | 179 | 4.4 | 859.5 | 782.1 | 826.2 | 849.8 | 792.6 | 420.1 | 706.7 | 768 | 573.5 | 762.6 | 658.7 | 765.5 | 769 | 260.5 | 328.2 | 337.7 | 304.9 | 236.8 | 314.2 | 310.9 | 289.1
748 | 585 | 469.5 | 187.8 | 219.5274 | 305.8 | 311.6 | 305.9 | 313.3 | 429.4 | 46.9 | 19.9 | 83.4 | 5.1 | 202.6 | 4.9 | 857.8 | 781.8 | 826.7 | 850 | 789.1 | 420.6 | 704.9 | 770.1 | 573.8 | 763.1 | 657.2 | 764 | 767.4 | 260.8 | 329.1 | 338.9 | 305.5 | 237.1 | 315 | 311.4 | 289.4
749 | 586 | 469.2 | 187.68 | 219.3871 | 305.2 | 312.4 | 307.2 | 314.4 | 430.5 | 46.9 | 19.9 | 83.5 | 5.1 | 212.3 | 5.4 | 859 | 781.5 | 826.5 | 849.9 | 788 | 421.2 | 711.7 | 773.6 | 574 | 762.5 | 656.5 | 767.8 | 765.7 | 261 | 330 | 339.8 | 306.1 | 237.4 | 316.3 | 312 | 289.7
750 | 587 | 469.2 | 187.68 | 219.3871 | 305.4 | 313.6 | 308.7 | 315.2 | 429.2 | 46.9 | 19.9 | 83.6 | 4.8 | 193.6 | 5 | 857.7 | 780.8 | 815.6 | 849.8 | 785.5 | 421.7 | 722 | 772.3 | 574.2 | 761.6 | 655.6 | 766.2 | 764.5 | 261.3 | 330.8 | 340.5 | 306.4 | 237.8 | 317.5 | 312.6 | 289.9
751 | 588 | 468.5 | 187.4 | 219.0598 | 306.5 | 315.2 | 309.5 | 315.9 | 427.3 | 46.9 | 19.9 | 83.7 | 4.5 | 181.3 | 4.6 | 860.2 | 780 | 807.2 | 849.2 | 784 | 422.3 | 717.5 | 776 | 574.3 | 761.9 | 653.8 | 768.7 | 766.2 | 261.6 | 331.2 | 341.2 | 306.6 | 238.1 | 319 | 313.4 | 290.3
752 | 589 | 468.3 | 187.32 | 218.9663 | 306.6 | 315.5 | 309.7 | 316.8 | 422.9 | 46.9 | 19.9 | 83.8 | 4.2 | 200.8 | 4.2 | 865.4 | 778.9 | 811.1 | 848 | 785.6 | 422.8 | 705.3 | 779.3 | 574.5 | 760.9 | 652.3 | 770.6 | 768.6 | 261.9 | 331.4 | 341.5 | 306.5 | 238.4 | 319.9 | 314 | 290.6
753 | 590 | 468.6 | 187.44 | 219.1066 | 307.1 | 315.7 | 309.9 | 317.1 | 420.5 | 46.9 | 19.9 | 83.8 | 4.2 | 193.6 | 3.6 | 868.8 | 778 | 827.9 | 847.3 | 789.1 | 423.4 | 698.9 | 784.8 | 574.7 | 762.8 | 650.3 | 778.3 | 768.5 | 262.2 | 331.9 | 341.8 | 306.6 | 238.8 | 320.1 | 314.4 | 290.9
754 | 591 | 468.6 | 187.44 | 219.1066 | 308.5 | 316.2 | 309.6 | 316.8 | 423.9 | 46.8 | 19.9 | 83.8 | 3.9 | 179.6 | 3.1 | 872.8 | 777.5 | 839.4 | 846.9 | 792 | 424.1 | 696 | 788.1 | 574.9 | 763.5 | 647.6 | 781.9 | 767.5 | 262.5 | 332.4 | 342.3 | 306.9 | 239.1 | 320.4 | 314.8 | 291.2
755 | 592 | 468.6 | 187.44 | 219.1066 | 309 | 317.5 | 309.2 | 316.8 | 421.5 | 46.8 | 19.9 | 83.9 | 4.2 | 166.6 | 3.5 | 876.1 | 777 | 842.7 | 846.4 | 794.6 | 425 | 696.2 | 790.2 | 575.1 | 764.3 | 645.6 | 784.1 | 767.4 | 262.8 | 332.4 | 342.3 | 306.9 | 239.5 | 321 | 314.9 | 291.4
756 | 593 | 468.2 | 187.28 | 218.9195 | 309 | 317.9 | 309 | 316.9 | 425 | 46.9 | 19.9 | 83.9 | 4.3 | 182 | 3.6 | 878.6 | 777.3 | 848.7 | 845.8 | 797.8 | 425.9 | 696.2 | 792.1 | 575.3 | 765.5 | 644.5 | 787.9 | 767.3 | 263.1 | 332.4 | 342.3 | 307 | 239.8 | 321.1 | 314.9 | 291.6
757 | 594 | 468 | 187.2 | 218.826 | 308.3 | 316.8 | 309 | 316.3 | 430.8 | 47 | 19.9 | 83.9 | 4.2 | 205 | 4.5 | 879.9 | 777.2 | 854.5 | 845.8 | 800.5 | 426.8 | 697.8 | 795.5 | 575.5 | 765.9 | 643.2 | 790.4 | 767 | 263.4 | 332.3 | 342.4 | 307 | 240.2 | 321 | 315.4 | 291.8
758 | 595 | 468 | 187.2 | 218.826 | 306.6 | 317 | 308.8 | 315.8 | 431.8 | 47.1 | 19.8 | 83.9 | 3.9 | 200.7 | 5 | 881.8 | 777.6 | 861.6 | 845.7 | 804.3 | 427.7 | 698.8 | 797.8 | 575.7 | 767.2 | 641.7 | 794.4 | 765.9 | 263.8 | 332.2 | 342.3 | 307.1 | 240.6 | 320.6 | 315.6 | 292.1
759 | 596 | 467.9 | 187.16 | 218.7793 | 305.4 | 317.8 | 308.5 | 315.4 | 428 | 47.2 | 19.8 | 84 | 4.3 | 172.7 | 4.7 | 884.4 | 778.2 | 869.4 | 845.3 | 808.3 | 428.9 | 697.6 | 795.9 | 576.1 | 767.4 | 640.7 | 794.3 | 765.6 | 264.1 | 332 | 342 | 307.1 | 240.9 | 320.3 | 315.8 | 292.3
760 | 597 | 468 | 187.2 | 218.826 | 304.5 | 318.2 | 307.6 | 315 | 419.6 | 47.3 | 19.8 | 84 | 4.5 | 185.6 | 5 | 886.4 | 778.2 | 866.8 | 845.4 | 810.6 | 429.8 | 692.1 | 795.1 | 576.4 | 767.7 | 640.1 | 795.2 | 766.2 | 264.4 | 331.8 | 341.9 | 307.2 | 241.3 | 319.7 | 315.9 | 292.5
761 | 598 | 468 | 187.2 | 218.826 | 304.5 | 318.1 | 306.6 | 314.6 | 414.2 | 47.3 | 19.8 | 84 | 3.5 | 204.7 | 6.1 | 887.2 | 778 | 866.5 | 845.3 | 811.6 | 430.7 | 688.5 | 796.4 | 576.7 | 768.5 | 639.3 | 795.7 | 768 | 264.7 | 331.7 | 341.8 | 307.4 | 241.6 | 319.1 | 315.8 | 292.6
762 | 599 | 468.1 | 187.24 | 218.8728 | 304.4 | 317.2 | 306.2 | 313.8 | 412.3 | 47.3 | 19.8 | 83.9 | 3.4 | 205.8 | 6.8 | 885.8 | 777.8 | 865.1 | 844.4 | 813.9 | 431.6 | 686.5 | 796.6 | 577 | 769.2 | 638.6 | 794 | 769.7 | 265 | 331.5 | 341.5 | 307.5 | 241.9 | 318.7 | 315.5 | 292.7
763 | 600 | 468 | 187.2 | 218.826 | 303.6 | 315.8 | 306.3 | 312.5 | 411 | 47.2 | 19.8 | 83.9 | 4.2 | 232.7 | 6.1 | 885.3 | 778.5 | 864.1 | 843.4 | 816.1 | 432.7 | 682.3 | 795.1 | 577.5 | 769.7 | 639 | 793.8 | 770 | 265.3 | 331.1 | 341.2 | 307.4 | 242.3 | 318.2 | 315.4 | 292.9
764 | 601 | 467.6 | 187.04 | 218.639 | 302.8 | 315.7 | 306.6 | 312.1 | 409.2 | 47.1 | 19.8 | 83.9 | 4.2 | 204.5 | 5.8 | 886.2 | 779.3 | 859.2 | 842.9 | 816.7 | 433.7 | 684.3 | 797 | 577.9 | 770.1 | 639 | 794.9 | 769.8 | 265.6 | 330.8 | 341 | 307.5 | 242.6 | 318.1 | 315.1 | 293.1
765 | 602 | 468.3 | 187.32 | 218.9663 | 301.4 | 315.9 | 306.5 | 312.2 | 406.5 | 47.1 | 19.8 | 83.9 | 4.2 | 197.5 | 6.4 | 887.9 | 780.6 | 861.2 | 844 | 816.3 | 434.7 | 680.2 | 796.3 | 578.4 | 769.8 | 639.5 | 795.7 | 770.1 | 265.8 | 330.6 | 340.8 | 307.7 | 242.9 | 317.9 | 314.9 | 293.3
766 | 603 | 469 | 187.6 | 219.2936 | 300.5 | 315.7 | 306.3 | 312 | 403.2 | 47.1 | 19.8 | 83.9 | 4.4 | 206.8 | 6.9 | 886 | 780.9 | 857.5 | 844.9 | 816.7 | 435.5 | 687.3 | 789 | 579 | 768.5 | 641.7 | 796.1 | 770.8 | 266.1 | 330.5 | 340.6 | 307.9 | 243.2 | 317.6 | 314.8 | 293.4
767 | 604 | 468.7 | 187.48 | 219.1533 | 300.1 | 315.4 | 306.6 | 311.8 | 402.6 | 47.2 | 19.8 | 84 | 4.3 | 196 | 6.6 | 885.9 | 781.6 | 860.5 | 844.9 | 819.2 | 436.2 | 684.9 | 787.1 | 579.6 | 768.3 | 643.8 | 798 | 770.9 | 266.4 | 330.2 | 340.2 | 307.9 | 243.5 | 317.4 | 314.7 | 293.6
768 | 605 | 469.2 | 187.68 | 219.3871 | 301.6 | 315.7 | 306.8 | 311.7 | 400.1 | 47.2 | 19.8 | 84 | 4.4 | 196.6 | 6.3 | 885.3 | 782.6 | 856.8 | 845.4 | 820.1 | 437 | 685.7 | 784.7 | 580.2 | 768.5 | 646 | 797.9 | 770.8 | 266.7 | 329.7 | 339.7 | 307.9 | 243.8 | 317.3 | 314.8 | 293.9
769 | 606 | 469 | 187.6 | 219.2936 | 302.5 | 315.8 | 305.9 | 311.3 | 394.3 | 47.3 | 19.8 | 84.1 | 4.5 | 203.2 | 6 | 884.5 | 783 | 863.3 | 845.9 | 822.1 | 437.9 | 686.7 | 788.6 | 580.8 | 770 | 647.3 | 797.9 | 770.1 | 266.9 | 329.4 | 339.3 | 307.9 | 244 | 317 | 315.2 | 294.1
770 | 607 | 468.2 | 187.28 | 218.9195 | 300.8 | 315.9 | 304.8 | 310.4 | 393.1 | 47.3 | 19.8 | 84.2 | 4.2 | 203.1 | 6 | 884.9 | 783 | 869.1 | 846.7 | 822.4 | 438.8 | 686.8 | 791.5 | 581.3 | 770.2 | 647.2 | 798.2 | 769.6 | 267.2 | 329.3 | 339.1 | 308.2 | 244.3 | 316.8 | 315.1 | 294.2
771 | 608 | 468.3 | 187.32 | 218.9663 | 299.7 | 315.5 | 304.2 | 310 | 392.4 | 47.4 | 19.8 | 84.3 | 3.6 | 193.8 | 6.3 | 886.5 | 783.9 | 869.9 | 847.2 | 823.8 | 440 | 697.6 | 790 | 581.9 | 770.1 | 647.1 | 799.3 | 771.2 | 267.5 | 329.2 | 338.9 | 308.4 | 244.6 | 316.7 | 315.1 | 294.4
772 | 609 | 468.1 | 187.24 | 218.8728 | 298.5 | 315.9 | 303.8 | 310.5 | 389.2 | 47.5 | 19.8 | 84.3 | 3.5 | 194.9 | 6.9 | 885.6 | 784.6 | 861.4 | 847 | 825.8 | 441 | 692.8 | 785.7 | 582.6 | 768.8 | 648.4 | 799.3 | 770.2 | 267.8 | 328.8 | 338.8 | 308.3 | 244.9 | 317.6 | 315.3 | 294.6
773 | 610 | 467.6 | 187.04 | 218.639 | 297.8 | 316.1 | 303.8 | 310.6 | 386.5 | 47.5 | 19.8 | 84.5 | 3.4 | 206.5 | 7.1 | 885.7 | 784.6 | 859.7 | 846.8 | 827.9 | 442.1 | 696.8 | 785 | 583.3 | 769.6 | 648.2 | 803.2 | 769.8 | 268 | 328.8 | 338.9 | 308.4 | 245.1 | 317.8 | 315.7 | 294.9
774 | 611 | 468.3 | 187.32 | 218.9663 | 296.9 | 316.4 | 304.8 | 310.4 | 387.3 | 47.5 | 19.8 | 84.5 | 3.8 | 200.5 | 6.7 | 883.5 | 784 | 856.2 | 847.2 | 826.7 | 443.2 | 694.3 | 784 | 583.9 | 769.7 | 647.6 | 799.2 | 768.9 | 268.3 | 328.9 | 339.1 | 308.7 | 245.4 | 318.6 | 315.9 | 295.1
775 | 612 | 468.9 | 187.56 | 219.2468 | 296.9 | 316.3 | 305.9 | 310.8 | 393.4 | 47.6 | 19.8 | 84.6 | 4.1 | 198.7 | 6.5 | 879.1 | 782.3 | 850.9 | 847.6 | 820.5 | 444 | 695.8 | 780.9 | 584.5 | 767.8 | 647.2 | 788.2 | 768 | 268.5 | 329 | 339.3 | 309 | 245.7 | 318.7 | 316 | 295.2
776 | 613 | 469.4 | 187.76 | 219.4806 | 297.7 | 316.6 | 306.3 | 310.5 | 393.4 | 47.6 | 19.8 | 84.6 | 4.2 | 201.6 | 6.3 | 878.2 | 780.1 | 855.8 | 847.3 | 818 | 444.3 | 699.6 | 779.9 | 585.2 | 766.7 | 647.6 | 784 | 768.2 | 268.8 | 329.1 | 339.2 | 309.5 | 245.9 | 318.9 | 316.2 | 295.4
777 | 614 | 467.3 | 186.92 | 218.4987 | 299.4 | 316.5 | 306.6 | 309.9 | 398.8 | 47.6 | 19.8 | 84.6 | 4.4 | 195.1 | 6.4 | 878.1 | 780.2 | 857.6 | 847.3 | 817.4 | 444.9 | 704.4 | 784.5 | 585.8 | 769.2 | 647.5 | 789.4 | 766.9 | 269.1 | 329.3 | 339 | 309.7 | 246.2 | 319.1 | 316.4 | 295.5
778 | 615 | 466.6 | 186.64 | 218.1714 | 301.1 | 316.9 | 306.4 | 310.2 | 412.9 | 47.6 | 19.8 | 84.6 | 4.3 | 193.5 | 6.4 | 879.3 | 781.3 | 862.4 | 847.3 | 819.4 | 446.1 | 708.1 | 788 | 586.4 | 769.9 | 647.6 | 793.7 | 766.3 | 269.3 | 329.4 | 338.9 | 309.8 | 246.5 | 319.3 | 316.5 | 295.8
779 | 616 | 467 | 186.8 | 218.3584 | 301.4 | 317.7 | 306 | 311.3 | 418 | 47.7 | 19.8 | 84.6 | 4.1 | 202.5 | 5.4 | 882.3 | 781.7 | 865.2 | 847 | 821.4 | 447.1 | 703.6 | 787.7 | 586.9 | 770 | 647.4 | 795.6 | 765.4 | 269.6 | 329.4 | 339 | 310 | 246.8 | 319.7 | 316.7 | 296.1
780 | 617 | 466.9 | 186.76 | 218.3117 | 302.1 | 319.5 | 305.5 | 311.9 | 415.5 | 47.7 | 19.8 | 84.6 | 4.3 | 206.1 | 5.2 | 884.2 | 781.8 | 864.4 | 846.8 | 821 | 447.9 | 700.2 | 785.7 | 587.5 | 768.7 | 646.6 | 794.6 | 765 | 269.8 | 329.4 | 339.2 | 310.1 | 247.1 | 319.7 | 316.8 | 296.2
781 | 618 | 467.3 | 186.92 | 218.4987 | 301.6 | 320.9 | 305.4 | 311.8 | 414.7 | 47.8 | 19.8 | 84.7 | 4 | 200.4 | 5.1 | 884.7 | 782.2 | 864 | 846.6 | 819.9 | 448.6 | 700.4 | 786.4 | 588 | 769.4 | 646.1 | 794.8 | 764.5 | 270.1 | 329.4 | 339.3 | 310.5 | 247.4 | 319.6 | 316.7 | 296.4
782 | 619 | 467.7 | 187.08 | 218.6857 | 301.9 | 320.6 | 305.1 | 311.5 | 415.3 | 47.8 | 19.8 | 84.7 | 3.9 | 187.6 | 4.6 | 884.9 | 782.3 | 860.2 | 846.4 | 817.9 | 449.4 | 695 | 790 | 588.6 | 770.1 | 645.4 | 795.7 | 766.2 | 270.4 | 329.7 | 339.4 | 310.9 | 247.7 | 319.9 | 316.7 | 296.5
783 | 620 | 469.4 | 187.76 | 219.4806 | 303.4 | 319.7 | 305 | 311.3 | 416 | 47.9 | 19.8 | 84.7 | 4.3 | 189.6 | 4.4 | 881.3 | 783 | 852.7 | 846.2 | 817.3 | 450.3 | 689.6 | 794.7 | 589.2 | 771.4 | 644.5 | 796.6 | 766.4 | 270.6 | 330 | 339.7 | 311.2 | 248 | 320.1 | 316.8 | 296.7
784 | 621 | 469.1 | 187.64 | 219.3403 | 306.6 | 319.9 | 304.5 | 312 | 425.5 | 48 | 19.8 | 84.8 | 4.8 | 195.6 | 4.2 | 871.2 | 782.6 | 838.3 | 846.5 | 810.5 | 451.3 | 692.9 | 789.4 | 589.8 | 770.1 | 643.8 | 782.6 | 763.6 | 270.9 | 330.8 | 340.6 | 311.8 | 248.2 | 320.5 | 316.8 | 296.8
785 | 622 | 468.5 | 187.4 | 219.0598 | 310.9 | 322.5 | 304.7 | 312.9 | 435.5 | 48 | 19.8 | 84.8 | 4.5 | 173.2 | 4.2 | 868.3 | 782.2 | 841.1 | 847 | 807 | 452 | 700.7 | 783.6 | 590.3 | 767.5 | 644.9 | 774.7 | 761.3 | 271.2 | 331.4 | 341.8 | 312.2 | 248.5 | 320.9 | 316.8 | 297
786 | 623 | 468.9 | 187.56 | 219.2468 | 312.6 | 323.4 | 305.5 | 314.3 | 445.2 | 48 | 19.8 | 84.9 | 3.9 | 176.3 | 4.5 | 870.1 | 782.9 | 843.9 | 847.3 | 809.7 | 452.6 | 704.2 | 786.6 | 591 | 768.8 | 646.6 | 777.2 | 759.5 | 271.4 | 331.8 | 342.5 | 312.3 | 248.8 | 320.9 | 316.9 | 297.2
787 | 624 | 468.9 | 187.56 | 219.2468 | 311.4 | 324.7 | 306.8 | 315.2 | 441.5 | 48.1 | 19.8 | 85.1 | 4 | 189.5 | 5.4 | 872.8 | 784.6 | 845.8 | 847.5 | 809.3 | 453.6 | 705.3 | 788.1 | 591.5 | 770.4 | 645.9 | 785.3 | 758.7 | 271.7 | 332.3 | 343 | 312.4 | 249.1 | 320.9 | 317 | 297.3
788 | 625 | 465.5 | 186.2 | 217.6571 | 310.5 | 324.9 | 307.1 | 315.6 | 435.1 | 48.1 | 19.8 | 85.2 | 4.3 | 175.7 | 6.5 | 875.6 | 785.6 | 851.7 | 847.1 | 813.6 | 454.7 | 704.5 | 790.7 | 592.1 | 771.7 | 644.4 | 787.6 | 759.5 | 272 | 332.7 | 343.7 | 312.6 | 249.4 | 320.8 | 317.4 | 297.6
789 | 626 | 466.7 | 186.68 | 218.2182 | 309.7 | 324.7 | 307.5 | 316 | 427.6 | 48.1 | 19.8 | 85.2 | 3.9 | 190.3 | 7 | 879.4 | 785.9 | 856.4 | 846.8 | 815.7 | 456 | 703.6 | 791.7 | 592.8 | 772.4 | 643.4 | 791 | 760.5 | 272.3 | 332.9 | 344 | 312.7 | 249.7 | 320.7 | 317.8 | 297.9
790 | 627 | 467.2 | 186.88 | 218.452 | 309.6 | 324.7 | 308.3 | 316.3 | 421.4 | 48.1 | 19.8 | 85.2 | 4.2 | 183.3 | 6.6 | 883.2 | 785.2 | 864.5 | 845.2 | 818.2 | 457.4 | 697.8 | 790.7 | 593.5 | 772.5 | 642.5 | 790 | 763.6 | 272.6 | 332.9 | 344.3 | 312.6 | 250 | 320.6 | 318.1 | 298.2
791 | 628 | 467.3 | 186.92 | 218.4987 | 309 | 324.5 | 308.3 | 316.1 | 415.5 | 48.1 | 19.8 | 85.3 | 4.5 | 180.6 | 6.8 | 883.4 | 784 | 866.2 | 843.4 | 819.6 | 458.5 | 690.1 | 789.9 | 594.1 | 773.4 | 643.1 | 785.8 | 764.3 | 272.9 | 332.7 | 344.4 | 312.4 | 250.3 | 320.5 | 318.6 | 298.4
792 | 629 | 467.2 | 186.88 | 218.452 | 308.2 | 325 | 308.4 | 315.6 | 410.9 | 48.1 | 19.8 | 85.3 | 4.2 | 190.4 | 7.1 | 884.2 | 784.1 | 869.3 | 842.5 | 823.4 | 459.9 | 685.3 | 786.8 | 594.8 | 773.5 | 644 | 787.4 | 763.9 | 273.3 | 332.5 | 344.3 | 312.3 | 250.6 | 320.4 | 318.7 | 298.6
793 | 630 | 467.2 | 186.88 | 218.452 | 306.8 | 325.7 | 308.4 | 315.6 | 408.4 | 48.1 | 19.8 | 85.3 | 4 | 190.3 | 7.8 | 884.6 | 783.4 | 862.7 | 842 | 823.1 | 460.9 | 680.8 | 785.7 | 595.5 | 772.7 | 645.1 | 787.7 | 765.3 | 273.6 | 332.3 | 344 | 312.2 | 250.9 | 320.5 | 318.8 | 298.8
794 | 631 | 468.7 | 187.48 | 219.1533 | 305.4 | 325.5 | 308.6 | 315.4 | 402.7 | 48.2 | 19.8 | 85.4 | 4.4 | 185.9 | 8.4 | 884.8 | 782.4 | 856.9 | 841.4 | 825.5 | 461.8 | 674.9 | 782.8 | 596.2 | 771.1 | 645.8 | 784.1 | 767.7 | 273.9 | 332.1 | 344.1 | 312.2 | 251.2 | 320.7 | 319 | 299
795 | 632 | 469.9 | 187.96 | 219.7144 | 303.8 | 324.5 | 309 | 315.4 | 398.3 | 48.2 | 19.8 | 85.4 | 4.5 | 190.8 | 8.3 | 887 | 782.4 | 865.9 | 840.6 | 829.4 | 462.6 | 671.1 | 781.8 | 596.9 | 771 | 646.8 | 785.9 | 768.5 | 274.2 | 331.9 | 343.9 | 312.3 | 251.4 | 320.6 | 319.1 | 299.3
796 | 633 | 469.8 | 187.92 | 219.6677 | 302.5 | 324.1 | 309.5 | 315.5 | 400.8 | 48.1 | 19.8 | 85.5 | 4.7 | 190.3 | 8 | 886.8 | 782.2 | 865.6 | 840.2 | 830.5 | 463.3 | 666.8 | 778.7 | 597.5 | 770.9 | 646.2 | 785.2 | 768.8 | 274.6 | 331.6 | 343.6 | 312.5 | 251.7 | 320.8 | 319 | 299.4
797 | 634 | 468.9 | 187.56 | 219.2468 | 300.9 | 324.5 | 309.4 | 315.3 | 405.8 | 48 | 19.8 | 85.5 | 4.1 | 183.5 | 7.7 | 885.5 | 782.7 | 867.6 | 840.5 | 831.5 | 464.1 | 663.3 | 781.2 | 598.1 | 771.8 | 646.2 | 791.7 | 768.3 | 274.9 | 331.2 | 343.2 | 312.5 | 252 | 320.8 | 318.9 | 299.5
798 | 635 | 467.4 | 186.96 | 218.5455 | 299.6 | 323.8 | 309.1 | 314.9 | 406.1 | 47.9 | 19.8 | 85.5 | 4.3 | 184 | 7.4 | 886.3 | 783.6 | 863.7 | 840.5 | 831.9 | 465.1 | 667.5 | 784.4 | 598.8 | 773.2 | 647 | 792.7 | 768.9 | 275.2 | 331 | 342.7 | 312.7 | 252.3 | 320.7 | 318.9 | 299.6
799 | 636 | 467.1 | 186.84 | 218.4052 | 299 | 322.8 | 308.4 | 314.4 | 407.4 | 47.9 | 19.8 | 85.5 | 3.8 | 183.6 | 7.3 | 886.7 | 783.7 | 866.8 | 840.4 | 831 | 466.1 | 674.1 | 787.7 | 599.4 | 773.2 | 646.6 | 793.8 | 771 | 275.5 | 330.9 | 342.4 | 312.8 | 252.5 | 320.6 | 318.7 | 299.7
800 | 637 | 468.5 | 187.4 | 219.0598 | 298.4 | 322.1 | 307.8 | 314.4 | 406.4 | 47.9 | 19.8 | 85.6 | 4 | 186.7 | 7.4 | 888 | 784 | 863.5 | 840.3 | 830.2 | 467 | 677.2 | 790.3 | 600 | 774.4 | 646.9 | 795.4 | 772.5 | 275.8 | 330.9 | 342.2 | 313.1 | 252.8 | 320.4 | 318.6 | 299.9
801 | 638 | 467.7 | 187.08 | 218.6857 | 298.2 | 321.5 | 308.2 | 314.5 | 408.8 | 48 | 19.8 | 85.7 | 4.3 | 187.8 | 7 | 884.6 | 784.5 | 857.2 | 841.1 | 826.6 | 468 | 682.9 | 791.3 | 600.7 | 774.6 | 646.8 | 795.1 | 774.5 | 276.1 | 331 | 342.2 | 313.2 | 253.1 | 320.2 | 318.4 | 300
802 | 639 | 468.3 | 187.32 | 218.9663 | 298.4 | 321.7 | 308.6 | 314.2 | 407 | 48 | 19.8 | 85.7 | 4.8 | 191.2 | 6.2 | 881.5 | 784.4 | 855.5 | 841.7 | 822.9 | 468.8 | 682.8 | 792.7 | 601.3 | 774.2 | 646.9 | 792.4 | 775.4 | 276.4 | 331.1 | 342.4 | 313.4 | 253.3 | 320.3 | 318.1 | 300
803 | 640 | 468.8 | 187.52 | 219.2001 | 298.4 | 321.8 | 308.8 | 314.6 | 408.5 | 48 | 19.8 | 85.7 | 5 | 174 | 6 | 877.9 | 784.6 | 853.5 | 842.7 | 823.2 | 469.6 | 682.7 | 794.6 | 601.9 | 775.3 | 646.5 | 790.9 | 773.3 | 276.7 | 331.6 | 342.7 | 313.9 | 253.6 | 320.5 | 318 | 300.2
804 | 641 | 468.9 | 187.56 | 219.2468 | 300.1 | 323.5 | 309.1 | 314.6 | 414.6 | 48.1 | 19.8 | 85.7 | 5 | 177.5 | 5.9 | 871.5 | 783.7 | 846.9 | 843.3 | 818.1 | 470.4 | 690 | 791.9 | 602.4 | 774.2 | 646.8 | 781.1 | 770.3 | 276.9 | 332.1 | 343.4 | 314.4 | 253.8 | 320.7 | 318 | 300.3
805 | 642 | 468.1 | 187.24 | 218.8728 | 301.4 | 325 | 309.2 | 314.7 | 419.3 | 48.1 | 19.8 | 85.7 | 4.8 | 192.9 | 5.9 | 867.4 | 782.8 | 842.2 | 843.7 | 814.6 | 471 | 694.4 | 794.1 | 603 | 774.4 | 647.2 | 778 | 768.4 | 277.2 | 332.7 | 344.6 | 314.8 | 254.1 | 320.8 | 318.2 | 300.5
806 | 643 | 468.8 | 187.52 | 219.2001 | 302 | 325.1 | 309.7 | 315.5 | 432.7 | 48.2 | 19.8 | 85.6 | 4 | 187.5 | 5.6 | 867 | 782.3 | 837.3 | 843.5 | 815.1 | 471.7 | 699.5 | 796.2 | 603.6 | 775.8 | 648.6 | 780 | 766.2 | 277.5 | 333.3 | 345.3 | 315.2 | 254.3 | 321.3 | 318.3 | 300.6
807 | 644 | 467.9 | 187.16 | 218.7793 | 302 | 326.3 | 310.9 | 316.7 | 442.6 | 48.1 | 19.7 | 85.6 | 4.3 | 174.1 | 5.6 | 868.6 | 783.3 | 839.5 | 843.8 | 816.7 | 472.7 | 703.2 | 797.2 | 604.2 | 777.5 | 648.4 | 789.1 | 764.1 | 277.7 | 333.9 | 345.8 | 315.5 | 254.6 | 322 | 318.6 | 300.9
808 | 645 | 468.9 | 187.56 | 219.2468 | 303.2 | 328.1 | 311 | 318 | 454.6 | 48.1 | 19.8 | 85.6 | 4.7 | 169.8 | 5.3 | 867.8 | 783.6 | 843.6 | 844.4 | 818.7 | 473.9 | 704 | 795 | 604.7 | 777.5 | 647.6 | 784.8 | 761.3 | 278 | 334.5 | 346.3 | 315.8 | 254.8 | 322.8 | 318.9 | 301.2
809 | 646 | 470 | 188 | 219.7612 | 304.7 | 328.3 | 310.5 | 318.7 | 457.2 | 48 | 19.7 | 85.7 | 4.5 | 181.8 | 5 | 867.9 | 783.6 | 844.8 | 845.1 | 815.6 | 475.1 | 706.5 | 789.5 | 605.3 | 777.6 | 647.6 | 778.4 | 759.5 | 278.3 | 335.1 | 347.1 | 316.1 | 255.1 | 323.7 | 319.4 | 301.3
810 | 647 | 469.6 | 187.84 | 219.5741 | 304.7 | 329.7 | 311 | 319.1 | 463.6 | 47.9 | 19.7 | 85.7 | 4.4 | 189.9 | 4.7 | 870.3 | 783.4 | 842.8 | 845.4 | 813.9 | 476 | 706.9 | 783 | 605.7 | 776 | 649 | 774.1 | 759.2 | 278.6 | 335.7 | 347.6 | 316.5 | 255.4 | 324.1 | 319.9 | 301.6
811 | 648 | 469.9 | 187.96 | 219.7144 | 304.5 | 330.2 | 311.3 | 319.6 | 455.6 | 47.9 | 19.7 | 85.6 | 4.4 | 183.7 | 4.5 | 873.9 | 783.5 | 845.4 | 845.5 | 813.8 | 476.9 | 706.7 | 787.4 | 606.2 | 777.4 | 650.2 | 781.4 | 759.5 | 278.9 | 336.1 | 347.9 | 316.6 | 255.6 | 324.4 | 320.4 | 301.8
812 | 649 | 469.2 | 187.68 | 219.3871 | 305.6 | 328.9 | 311.3 | 319.9 | 451.9 | 47.9 | 19.7 | 85.7 | 4.2 | 178.2 | 4.4 | 875.4 | 783.3 | 849 | 845.3 | 814.5 | 477.9 | 705.6 | 790.7 | 606.7 | 778.1 | 650.1 | 784.8 | 759.9 | 279.3 | 336.5 | 348 | 316.8 | 255.9 | 324.5 | 320.4 | 302
813 | 650 | 468.5 | 187.4 | 219.0598 | 305.3 | 328.8 | 311.5 | 319.8 | 450.9 | 48 | 19.7 | 85.8 | 4.3 | 191.8 | 3.8 | 874 | 782.9 | 854.9 | 845.5 | 816 | 478.8 | 703.5 | 788.8 | 607.1 | 778 | 649.8 | 786.5 | 759.8 | 279.6 | 336.8 | 348.1 | 317 | 256.1 | 324.5 | 320.6 | 302.2
814 | 651 | 469.7 | 187.88 | 219.6209 | 304.9 | 328.2 | 311.5 | 319.6 | 455.9 | 48.1 | 19.7 | 86 | 4.3 | 207 | 3.9 | 875.4 | 783.1 | 859.8 | 845.3 | 818 | 479.6 | 699.4 | 792.7 | 607.4 | 778.9 | 649.1 | 790.6 | 759.7 | 279.9 | 336.9 | 348.5 | 317 | 256.4 | 324.2 | 320.9 | 302.4
815 | 652 | 468.2 | 187.28 | 218.9195 | 305.3 | 327.5 | 311 | 319.6 | 459.7 | 48.2 | 19.7 | 86.1 | 4.2 | 203 | 4.5 | 876.3 | 782.9 | 862.2 | 845.4 | 818.1 | 480.7 | 702.2 | 795.4 | 607.8 | 779.8 | 648.3 | 791 | 758.7 | 280.2 | 337 | 348.6 | 317 | 256.7 | 325 | 321 | 302.5
816 | 653 | 467.3 | 186.92 | 218.4987 | 306.3 | 327.4 | 310.7 | 320.3 | 454.5 | 48.3 | 19.7 | 86.2 | 4.3 | 202.1 | 4.6 | 878.2 | 783.5 | 862.7 | 845.7 | 818.2 | 481.7 | 699.1 | 796.3 | 608.2 | 780.2 | 647.2 | 793.5 | 758.3 | 280.6 | 337.1 | 348.6 | 317 | 256.9 | 325.2 | 321.4 | 302.8
817 | 654 | 467.7 | 187.08 | 218.6857 | 306.4 | 327.9 | 310.7 | 321 | 451.7 | 48.4 | 19.7 | 86.2 | 3.6 | 227.6 | 4.5 | 880.5 | 784.4 | 861.2 | 845.5 | 820.8 | 482.6 | 696.5 | 797.8 | 608.6 | 781.1 | 646.6 | 796.1 | 759.1 | 280.9 | 337 | 348.6 | 317.1 | 257.2 | 325.1 | 321.7 | 303
818 | 655 | 468 | 187.2 | 218.826 | 305.7 | 328.1 | 311 | 321.1 | 445.9 | 48.5 | 19.7 | 86.3 | 3.8 | 255.5 | 4.3 | 879.1 | 785 | 857 | 845.4 | 823.8 | 483.8 | 700.9 | 793.2 | 609 | 781.2 | 646.6 | 795.1 | 759.1 | 281.2 | 337 | 348.7 | 317.1 | 257.4 | 325.2 | 321.8 | 303.1
819 | 656 | 469.2 | 187.68 | 219.3871 | 305.5 | 329.4 | 311.4 | 320.8 | 442.4 | 48.6 | 19.7 | 86.3 | 4.3 | 256.3 | 4.1 | 879.4 | 785.8 | 859.8 | 845.2 | 826.6 | 485 | 698.1 | 789.8 | 609.4 | 780.8 | 646.9 | 793.9 | 760 | 281.5 | 336.9 | 349.1 | 317.2 | 257.7 | 325 | 322.2 | 303.4
820 | 657 | 468.8 | 187.52 | 219.2001 | 305.7 | 329.7 | 311.4 | 320.6 | 437.7 | 48.7 | 19.7 | 86.4 | 4.7 | 247.4 | 4.2 | 880.1 | 785.5 | 860.7 | 844.2 | 828 | 486.1 | 696.1 | 787.1 | 609.9 | 781.4 | 647.1 | 791.8 | 761.4 | 281.9 | 336.9 | 348.9 | 317.2 | 257.9 | 324.7 | 322.6 | 303.7
821 | 658 | 469.2 | 187.68 | 219.3871 | 304.3 | 330.2 | 311.4 | 320.4 | 429.3 | 48.8 | 19.7 | 86.5 | 4.6 | 234.3 | 4.6 | 880.9 | 784.4 | 859.2 | 843 | 828.4 | 487.1 | 692.3 | 783.4 | 610.2 | 779.5 | 646.6 | 788.8 | 763.1 | 282.2 | 336.9 | 348.8 | 317.2 | 258.1 | 324.6 | 322.7 | 303.8
822 | 659 | 469.7 | 187.88 | 219.6209 | 302.4 | 330.3 | 311.9 | 320.4 | 424.1 | 48.8 | 19.7 | 86.5 | 4.5 | 234.2 | 4.8 | 881.5 | 783.8 | 859.7 | 842.3 | 829.8 | 487.7 | 693.5 | 782.3 | 610.6 | 779.2 | 646.7 | 787.5 | 764 | 282.5 | 336.8 | 348.7 | 317.4 | 258.4 | 324.4 | 322.7 | 304
823 | 660 | 466.6 | 186.64 | 218.1714 | 301.3 | 329.1 | 311.8 | 320.4 | 419.8 | 48.8 | 19.7 | 86.5 | 4.4 | 232 | 4.5 | 884.5 | 783 | 862.6 | 841.5 | 830.8 | 488.6 | 694.1 | 780.4 | 611 | 777.6 | 646.7 | 783.3 | 765.1 | 282.8 | 336.6 | 348.4 | 317.7 | 258.6 | 324.7 | 322.7 | 304.1
824 | 661 | 467.7 | 187.08 | 218.6857 | 301 | 328.2 | 311.1 | 319.5 | 417.5 | 48.8 | 19.7 | 86.5 | 4.3 | 220.4 | 4.3 | 885.2 | 782.3 | 863.2 | 841 | 830.6 | 489.4 | 698.9 | 784.1 | 611.3 | 778.1 | 645.7 | 784.4 | 765.7 | 283.1 | 336.5 | 348.1 | 317.7 | 258.9 | 324.6 | 322.7 | 304.2
825 | 662 | 467.1 | 186.84 | 218.4052 | 300.7 | 327.8 | 310.3 | 319 | 416.7 | 48.8 | 19.7 | 86.6 | 4.3 | 213.6 | 4.2 | 883.3 | 781.1 | 862.8 | 840.8 | 830.4 | 490.1 | 697.3 | 786.2 | 611.6 | 777.6 | 645.1 | 785.2 | 765.6 | 283.4 | 336.4 | 348.3 | 317.9 | 259.1 | 324.6 | 322.4 | 304.3
826 | 663 | 467.5 | 187 | 218.5922 | 300.4 | 326.6 | 309.9 | 318.3 | 413.7 | 48.8 | 19.7 | 86.7 | 4.5 | 210.9 | 3.9 | 880.6 | 780.5 | 860.1 | 840.6 | 831.2 | 491.1 | 696.3 | 788.7 | 611.9 | 777.8 | 644.5 | 788.1 | 765.5 | 283.7 | 336.2 | 348.4 | 317.8 | 259.3 | 325 | 322.2 | 304.4
827 | 664 | 468.4 | 187.36 | 219.013 | 300 | 325.7 | 309.4 | 317.7 | 409.4 | 48.8 | 19.7 | 86.9 | 4.7 | 211.2 | 3.9 | 880.1 | 779.2 | 856.6 | 839.8 | 831 | 491.8 | 694.3 | 782.6 | 612.3 | 775.3 | 644.8 | 785.2 | 766.2 | 284.1 | 335.9 | 348.3 | 317.8 | 259.5 | 325.2 | 322.2 | 304.5
828 | 665 | 470.9 | 188.36 | 220.182 | 299.2 | 325.3 | 308.8 | 317.7 | 409.6 | 48.8 | 19.7 | 87 | 4 | 204.5 | 3.8 | 879.9 | 778.7 | 857 | 839.7 | 830.1 | 492.5 | 690.9 | 784.8 | 612.6 | 775.7 | 645.3 | 784.6 | 766.1 | 284.4 | 335.7 | 348 | 317.9 | 259.7 | 325.1 | 322 | 304.7
829 | 666 | 468.9 | 187.56 | 219.2468 | 299 | 325.1 | 308.7 | 317.8 | 413.5 | 48.7 | 19.7 | 87.1 | 4.3 | 187 | 3.7 | 878.9 | 777.9 | 859.7 | 839.6 | 830 | 493.1 | 684.7 | 783.3 | 612.8 | 774.1 | 645.4 | 781.5 | 766 | 284.7 | 335.9 | 347.9 | 318.2 | 260 | 324.9 | 321.8 | 304.8
830 | 667 | 468.2 | 187.28 | 218.9195 | 298.3 | 325.8 | 308.5 | 317.5 | 414 | 48.7 | 19.7 | 87.1 | 4.3 | 195.7 | 3.4 | 875.7 | 775.9 | 851.8 | 839.2 | 826.1 | 493.6 | 687.6 | 775.5 | 613.1 | 770.7 | 646.1 | 768.5 | 766.3 | 285 | 336.1 | 348 | 318.5 | 260.2 | 324.9 | 321.7 | 304.9
831 | 668 | 467.8 | 187.12 | 218.7325 | 300.1 | 325.8 | 308 | 317.2 | 411.9 | 48.7 | 19.7 | 87.2 | 4.7 | 214.9 | 3.1 | 871.8 | 774.1 | 845.3 | 838.7 | 823.1 | 494 | 688.5 | 770.6 | 613.3 | 768.6 | 647.2 | 765.3 | 767.3 | 285.2 | 336.2 | 348 | 318.7 | 260.4 | 325.3 | 321.7 | 305
832 | 669 | 467.8 | 187.12 | 218.7325 | 302.7 | 325.2 | 307.7 | 317.9 | 410.6 | 48.8 | 19.7 | 87.3 | 4.5 | 217.5 | 2.8 | 871.7 | 773.7 | 848.8 | 838.9 | 822.7 | 494.7 | 686.1 | 774.2 | 613.5 | 769.7 | 648.5 | 770.3 | 767.6 | 285.5 | 336.4 | 348 | 318.8 | 260.6 | 325.3 | 321.7 | 305.1
833 | 670 | 468.8 | 187.52 | 219.2001 | 304.9 | 324.5 | 307.9 | 317.8 | 408.5 | 48.8 | 19.7 | 87.4 | 5.1 | 195.2 | 2.6 | 874.4 | 774 | 856.1 | 838.6 | 825.9 | 495.4 | 682.4 | 773.7 | 613.9 | 768.7 | 649.3 | 773.6 | 768 | 285.8 | 336.3 | 347.9 | 318.7 | 260.8 | 325.4 | 321.8 | 305.3
834 | 671 | 469.6 | 187.84 | 219.5741 | 305.2 | 323.9 | 307.9 | 318.1 | 410.5 | 48.8 | 19.7 | 87.5 | 4.4 | 174.7 | 3.1 | 874.4 | 774.5 | 856.7 | 838.3 | 826.1 | 496.3 | 680 | 774.3 | 614.2 | 768.7 | 649.8 | 773.6 | 767.6 | 286.1 | 336.3 | 347.6 | 318.8 | 261 | 325.6 | 321.8 | 305.5
835 | 672 | 468.3 | 187.32 | 218.9663 | 305.7 | 323.8 | 307.9 | 318.1 | 408.2 | 48.8 | 19.7 | 87.6 | 4.3 | 190 | 3.4 | 868.7 | 772.2 | 843.4 | 837.6 | 819.4 | 497 | 679.8 | 764.4 | 614.2 | 765.3 | 649.5 | 758.2 | 768.1 | 286.4 | 336.3 | 347.5 | 319 | 261.2 | 325.6 | 321.9 | 305.6
836 | 673 | 468.9 | 187.56 | 219.2468 | 306.2 | 323.7 | 308.3 | 317.8 | 406.8 | 48.8 | 19.7 | 87.7 | 4.6 | 199.1 | 3.7 | 865.4 | 768.6 | 830.6 | 836.3 | 813.3 | 497.4 | 682.6 | 753.5 | 614.3 | 761.6 | 650.1 | 745.3 | 770.4 | 286.6 | 336.3 | 347.3 | 319.2 | 261.5 | 325.5 | 322.1 | 305.8
837 | 674 | 468.5 | 187.4 | 219.0598 | 305.8 | 324 | 308.1 | 317.4 | 405.9 | 48.9 | 19.7 | 87.8 | 4.3 | 200.1 | 4.2 | 861.9 | 765.1 | 819.5 | 834.6 | 807.9 | 497.8 | 682.2 | 746.1 | 614.4 | 759.3 | 651.1 | 738.1 | 773.8 | 286.9 | 336.1 | 347 | 319.2 | 261.7 | 325.5 | 322.3 | 305.9
838 | 675 | 466.7 | 186.68 | 218.2182 | 305.7 | 325.4 | 307.8 | 317.3 | 401.7 | 49 | 19.7 | 87.9 | 4.7 | 203.3 | 4.3 | 858.6 | 762 | 813.8 | 833.1 | 802.8 | 498.2 | 679.1 | 740.5 | 614.4 | 756.5 | 651.1 | 729.8 | 776.7 | 287.2 | 335.8 | 346.6 | 319.1 | 261.9 | 325.4 | 322.3 | 306.1
839 | 676 | 468.6 | 187.44 | 219.1066 | 306 | 325.1 | 307.5 | 317.2 | 401 | 49 | 19.7 | 88 | 4.7 | 199.5 | 4 | 858.4 | 759 | 804.6 | 831.2 | 798 | 498.6 | 682.6 | 736 | 614.4 | 754.2 | 651.9 | 723.1 | 779.5 | 287.5 | 335.7 | 346 | 319.2 | 262.1 | 325.3 | 322.1 | 306.1
840 | 677 | 468 | 187.2 | 218.826 | 304.9 | 325 | 307.4 | 316.7 | 399.9 | 49 | 19.7 | 88.1 | 4.1 | 198 | 3.7 | 857.9 | 756.4 | 802.6 | 829.7 | 795 | 499.1 | 680.6 | 734.1 | 614.5 | 752.8 | 652.5 | 720.7 | 782.4 | 287.8 | 335.5 | 345.7 | 319.3 | 262.3 | 325.3 | 322.1 | 306.2
841 | 678 | 468.6 | 187.44 | 219.1066 | 304.4 | 324.8 | 307.1 | 316.7 | 400.7 | 49.1 | 19.7 | 88.2 | 4.1 | 206.1 | 3.4 | 858.1 | 754.5 | 805.5 | 828.6 | 794.3 | 499.6 | 678.8 | 731.2 | 614.5 | 751.7 | 652.7 | 725.3 | 783.2 | 288 | 335.5 | 345.4 | 319.5 | 262.5 | 325.1 | 322 | 306.3
842 | 679 | 468.3 | 187.32 | 218.9663 | 304.4 | 324.7 | 306.7 | 316.6 | 400.1 | 49.2 | 19.7 | 88.4 | 4.6 | 210.7 | 3 | 856.1 | 752.2 | 807.1 | 827.2 | 791.5 | 500 | 678.8 | 729.1 | 614.4 | 749.5 | 651.8 | 722.3 | 783.1 | 288.3 | 335.4 | 345.2 | 319.7 | 262.7 | 324.8 | 322 | 306.3
843 | 680 | 468.5 | 187.4 | 219.0598 | 305.6 | 324.4 | 305.7 | 316.3 | 399.1 | 49.2 | 19.7 | 88.4 | 4.7 | 209.7 | 2.7 | 853.7 | 750.3 | 811.6 | 825.9 | 789.6 | 500.5 | 681.8 | 725.5 | 614.4 | 746.9 | 650.3 | 720.7 | 783.2 | 288.6 | 335.3 | 344.9 | 320 | 262.9 | 324.4 | 321.8 | 306.3
844 | 681 | 468.3 | 187.32 | 218.9663 | 306.2 | 323.3 | 305.7 | 315.8 | 397.2 | 49.1 | 19.7 | 88.6 | 4.9 | 201.4 | 2.4 | 854.1 | 748.9 | 814.5 | 825.3 | 787.2 | 501 | 682.6 | 724.6 | 614.4 | 745.6 | 649.3 | 720.2 | 780.8 | 288.8 | 335.5 | 344.7 | 320.2 | 263.1 | 323.9 | 321.4 | 306.4
845 | 682 | 468.4 | 187.36 | 219.013 | 305 | 322 | 306 | 315.3 | 396.8 | 49 | 19.7 | 88.8 | 4.9 | 182.6 | 2.4 | 854.5 | 747.2 | 810.4 | 824.6 | 784.2 | 501.6 | 680.5 | 722.5 | 614.3 | 744.1 | 647.9 | 717.7 | 778.1 | 289.1 | 335.9 | 344.5 | 320.6 | 263.3 | 323.6 | 321.2 | 306.5
846 | 683 | 469 | 187.6 | 219.2936 | 304.1 | 320.5 | 306.4 | 315 | 397.6 | 48.9 | 19.7 | 89.2 | 5.1 | 173 | 2.5 | 855.7 | 745.7 | 812.1 | 823.9 | 783.4 | 502.2 | 676.7 | 723.3 | 614.2 | 742.3 | 647 | 715.7 | 777.2 | 289.4 | 335.6 | 344.3 | 320.5 | 263.5 | 323.2 | 321 | 306.5
847 | 684 | 468.2 | 187.28 | 218.9195 | 303.2 | 318.4 | 306.6 | 314.7 | 397.1 | 48.8 | 19.7 | 89.5 | 4.8 | 165.6 | 2.6 | 851.8 | 744.1 | 812 | 823.7 | 780.9 | 502.7 | 669.5 | 721 | 614.2 | 739.9 | 646.3 | 711.3 | 777.5 | 289.6 | 335.3 | 343.9 | 320.3 | 263.7 | 323.4 | 320.9 | 306.6
848 | 685 | 468.7 | 187.48 | 219.1533 | 302.5 | 316 | 306.4 | 314.9 | 392.3 | 48.8 | 19.6 | 89.9 | 5 | 169.6 | 3.3 | 853 | 743.3 | 817 | 823.3 | 780.1 | 503.3 | 664.5 | 723.3 | 614.2 | 737.9 | 645.7 | 714.4 | 778.9 | 289.9 | 334.9 | 343.6 | 320.1 | 263.9 | 323.7 | 321 | 306.8
849 | 686 | 469 | 187.6 | 219.2936 | 301.6 | 314.8 | 305.6 | 315.2 | 388.1 | 48.9 | 19.6 | 90.2 | 4.5 | 181.1 | 4.2 | 857 | 743.8 | 819.4 | 823.2 | 780.4 | 503.9 | 656.5 | 732.7 | 614.2 | 738.7 | 644.7 | 723.7 | 780.1 | 290.1 | 334.6 | 343.2 | 320 | 264.1 | 323.5 | 320.9 | 306.9
850 | 687 | 468.8 | 187.52 | 219.2001 | 301 | 314.4 | 304.5 | 314.9 | 384.8 | 49 | 19.6 | 90.5 | 4.7 | 177.3 | 4.8 | 860.2 | 744.5 | 821.2 | 823.2 | 780.2 | 504.6 | 652.3 | 738.7 | 614.2 | 739.1 | 643.3 | 731.1 | 779.4 | 290.4 | 334.5 | 343.2 | 320.2 | 264.3 | 323.3 | 321 | 307
851 | 688 | 468.6 | 187.44 | 219.1066 | 301.5 | 315 | 303.9 | 314.5 | 386.6 | 49 | 19.6 | 90.7 | 4.6 | 175.6 | 5.2 | 861.1 | 745.6 | 828.9 | 823.5 | 783 | 505.4 | 656.2 | 743.4 | 614.2 | 740.4 | 642.5 | 733.7 | 776.9 | 290.6 | 334.6 | 343.2 | 320.3 | 264.5 | 323.3 | 321 | 307.1
852 | 689 | 469.5 | 187.8 | 219.5274 | 301.6 | 315.3 | 303.5 | 314 | 390.6 | 49 | 19.6 | 90.7 | 4.7 | 179.6 | 5.4 | 855.9 | 745.5 | 824.9 | 824.6 | 781.4 | 506.2 | 659 | 742 | 614.2 | 739.2 | 641.9 | 732.3 | 774 | 290.9 | 334.6 | 343.3 | 320.5 | 264.7 | 323.4 | 321.3 | 307.1
853 | 690 | 468.8 | 187.52 | 219.2001 | 301.7 | 315.3 | 304.4 | 314.1 | 392 | 48.9 | 19.6 | 90.8 | 5.1 | 180.1 | 5.4 | 849.4 | 743.6 | 820.5 | 825.1 | 777.4 | 506.9 | 665.1 | 734 | 614.3 | 735.6 | 641.1 | 720.9 | 771 | 291.1 | 334.7 | 343.6 | 320.7 | 264.9 | 323.5 | 321.2 | 307.2
854 | 691 | 472.2 | 188.88 | 220.7898 | 301.4 | 315.6 | 305.4 | 314.1 | 392.1 | 48.9 | 19.6 | 91 | 4.9 | 182 | 5.2 | 849.9 | 743.6 | 821.8 | 825.5 | 776.7 | 507.5 | 667.7 | 735.7 | 614.3 | 735.1 | 641 | 724.4 | 769.8 | 291.3 | 335.2 | 343.9 | 321.1 | 265.1 | 323.5 | 321.2 | 307.3
855 | 692 | 473.8 | 189.52 | 221.538 | 300.9 | 316 | 305.3 | 314 | 393.2 | 48.9 | 19.6 | 91.2 | 4.5 | 190.3 | 4.7 | 854 | 745.4 | 826.8 | 825.7 | 779.5 | 508.3 | 664.4 | 743.4 | 614.3 | 737.7 | 641.1 | 734.9 | 769.7 | 291.6 | 335.5 | 344.2 | 321.4 | 265.3 | 323.8 | 321.1 | 307.3
856 | 693 | 472.6 | 189.04 | 220.9769 | 300.8 | 315.9 | 305.2 | 313.7 | 393.8 | 48.9 | 19.6 | 91.2 | 4.7 | 190.7 | 4.3 | 858.1 | 746.2 | 833.1 | 825.5 | 783.2 | 509.1 | 658.8 | 746.6 | 614.4 | 737.7 | 640.8 | 741.3 | 769.6 | 291.8 | 335.7 | 344.6 | 321.5 | 265.4 | 324.1 | 321.1 | 307.4
857 | 694 | 471.3 | 188.52 | 220.369 | 301.3 | 315.3 | 305.2 | 313.6 | 394.5 | 49 | 19.6 | 91.3 | 4.9 | 187.2 | 4.3 | 858 | 746.1 | 832.2 | 825 | 782.9 | 509.9 | 656.4 | 748.2 | 614.4 | 736.7 | 640.1 | 741.1 | 769 | 292.1 | 335.9 | 344.9 | 321.6 | 265.6 | 324.6 | 321.1 | 307.6
858 | 695 | 470.1 | 188.04 | 219.8079 | 302.7 | 314.6 | 304.8 | 314 | 397.3 | 49 | 19.6 | 91.4 | 4.1 | 179.5 | 4.1 | 857.7 | 746.6 | 831.9 | 825.2 | 782.7 | 510.6 | 660.7 | 754.8 | 614.5 | 736.8 | 639.7 | 741.2 | 767.3 | 292.3 | 336.3 | 345.3 | 321.8 | 265.8 | 324.7 | 321 | 307.6
859 | 696 | 469.4 | 187.76 | 219.4806 | 304.2 | 314.5 | 304.7 | 314.4 | 405.3 | 49.1 | 19.6 | 91.3 | 4.5 | 182.3 | 3.4 | 852.8 | 746.7 | 828.5 | 826.1 | 780.9 | 511.3 | 670.3 | 756.2 | 614.5 | 737.5 | 639.3 | 737.6 | 763.9 | 292.6 | 336.8 | 346.1 | 322.2 | 266 | 324.6 | 321 | 307.7
860 | 697 | 468.3 | 187.32 | 218.9663 | 306.1 | 314.6 | 305.1 | 314.3 | 417.6 | 49.2 | 19.6 | 91.3 | 4.8 | 190.2 | 3.2 | 853.2 | 748.6 | 830.8 | 827 | 780.1 | 512 | 676.4 | 757.6 | 614.6 | 738.3 | 639.5 | 741 | 763.2 | 292.8 | 337.2 | 346.9 | 322.4 | 266.2 | 324.9 | 321.2 | 307.8
861 | 698 | 469.6 | 187.84 | 219.5741 | 307.1 | 316 | 306.7 | 314.6 | 423 | 49.2 | 19.6 | 91.4 | 5 | 190.9 | 3.6 | 853.1 | 750.2 | 830.6 | 827.7 | 778.2 | 512.8 | 675.2 | 760.2 | 614.6 | 739 | 639.3 | 747.5 | 763.8 | 293.1 | 337.5 | 347.3 | 322.5 | 266.4 | 325.2 | 321.3 | 307.9
862 | 699 | 469.2 | 187.68 | 219.3871 | 307.1 | 317.1 | 307.4 | 315.5 | 419.4 | 49.3 | 19.6 | 91.4 | 4.8 | 189.5 | 3.8 | 854.3 | 752 | 832.7 | 828.7 | 779.9 | 513.6 | 678.5 | 761.9 | 614.7 | 738.8 | 639 | 748.9 | 763 | 293.3 | 338.2 | 348 | 323 | 266.6 | 325.1 | 321.6 | 308.1
863 | 700 | 470.3 | 188.12 | 219.9014 | 306.7 | 317.7 | 308.4 | 316.8 | 420 | 49.3 | 19.6 | 91.5 | 5.2 | 191.2 | 4 | 851.1 | 752.5 | 830.1 | 829.9 | 778.5 | 514.4 | 683.1 | 765.9 | 614.8 | 739.3 | 639.7 | 746 | 761.6 | 293.6 | 338.7 | 348.6 | 323.2 | 266.8 | 325.1 | 321.5 | 308.1
864 | 701 | 469.5 | 187.8 | 219.5274 | 308 | 320.3 | 309.5 | 317.4 | 420 | 49.4 | 19.6 | 91.5 | 4.8 | 190.7 | 4 | 845.7 | 752.3 | 824 | 830.6 | 775.6 | 515.2 | 686.9 | 767.7 | 614.9 | 739.5 | 641 | 738 | 761 | 293.9 | 339.2 | 349.1 | 323.4 | 267 | 325.3 | 321.5 | 308.2
865 | 702 | 469.5 | 187.8 | 219.5274 | 309.4 | 323.5 | 311 | 317.8 | 420.7 | 49.4 | 19.6 | 91.4 | 4.6 | 191.8 | 3.9 | 840.7 | 751 | 818.4 | 830.7 | 770.8 | 515.9 | 688.8 | 766 | 614.9 | 737.4 | 641.8 | 728.9 | 760.2 | 294.1 | 339.7 | 349.8 | 323.7 | 267.2 | 325.9 | 321.8 | 308.3
866 | 703 | 469 | 187.6 | 219.2936 | 310.3 | 326.2 | 311.9 | 318.5 | 419.3 | 49.4 | 19.6 | 91.4 | 4 | 198.4 | 3.9 | 843.4 | 750.8 | 821.8 | 830.5 | 769 | 516.6 | 688.5 | 765.2 | 615 | 737.4 | 642.4 | 727.6 | 759.9 | 294.4 | 340 | 350.5 | 323.8 | 267.4 | 326.7 | 322 | 308.5
867 | 704 | 469.3 | 187.72 | 219.4339 | 310.8 | 326.3 | 313.6 | 318.9 | 418.1 | 49.4 | 19.6 | 91.3 | 4.1 | 194.2 | 4.3 | 846.3 | 751.1 | 824.2 | 830.2 | 770.3 | 517.3 | 684.7 | 771.5 | 615.1 | 739.6 | 642.2 | 735.6 | 760.4 | 294.7 | 340.2 | 351.2 | 323.9 | 267.6 | 327 | 322.4 | 308.7
868 | 705 | 469.4 | 187.76 | 219.4806 | 311.4 | 325.4 | 315 | 319.7 | 415.9 | 49.5 | 19.6 | 91.2 | 4.6 | 194.7 | 4.6 | 849 | 751.3 | 826.4 | 829.9 | 771.6 | 518.2 | 680.3 | 775.3 | 615.1 | 740.4 | 641.8 | 737.9 | 760.2 | 295 | 340.6 | 351.8 | 323.9 | 267.8 | 327.5 | 322.7 | 308.8
869 | 706 | 468.4 | 187.36 | 219.013 | 311.7 | 325.2 | 315.4 | 320.1 | 413.6 | 49.5 | 19.6 | 91 | 4.8 | 215.4 | 5 | 852.2 | 751.2 | 828.2 | 829.4 | 772.9 | 519 | 676.4 | 775.6 | 615.2 | 740.3 | 641.5 | 742.8 | 759.8 | 295.3 | 340.9 | 352.3 | 323.9 | 268 | 328.4 | 323.2 | 309
870 | 707 | 469.1 | 187.64 | 219.3403 | 311.3 | 324.9 | 315.3 | 320.7 | 422 | 49.4 | 19.6 | 90.9 | 4.6 | 191 | 5.2 | 848.9 | 750.1 | 827 | 829.1 | 769.8 | 519.8 | 679.4 | 771 | 615.2 | 739.9 | 641.1 | 733.9 | 757.9 | 295.6 | 341.5 | 353.1 | 324.2 | 268.2 | 328.8 | 323.5 | 309.1
871 | 708 | 469.3 | 187.72 | 219.4339 | 311.2 | 324.2 | 315.5 | 321.5 | 426.5 | 49.4 | 19.6 | 90.9 | 5.1 | 186.8 | 5.3 | 847.6 | 748.5 | 826.8 | 828.4 | 768.6 | 520.6 | 691.1 | 763.4 | 615.3 | 737.1 | 641.1 | 728.7 | 756.8 | 296 | 342 | 353.8 | 324.6 | 268.4 | 329 | 323.8 | 309.3
872 | 709 | 467.1 | 186.84 | 218.4052 | 312.8 | 323.7 | 316.9 | 322.7 | 425.6 | 49.4 | 19.6 | 90.8 | 4.9 | 184 | 5.1 | 846.5 | 746.8 | 825.8 | 827.5 | 766.9 | 521.3 | 692 | 756.9 | 615.3 | 735.8 | 641.7 | 722 | 755.2 | 296.3 | 342.4 | 354.6 | 324.9 | 268.6 | 329.4 | 324.1 | 309.5
873 | 710 | 468.6 | 187.44 | 219.1066 | 313 | 323.2 | 318.6 | 323.3 | 425.6 | 49.6 | 19.6 | 90.8 | 4.5 | 183.2 | 5 | 845.4 | 746.4 | 825 | 827.4 | 766.4 | 522 | 692.4 | 757.6 | 615.4 | 736.1 | 642.6 | 724.3 | 753.5 | 296.6 | 343.1 | 355.5 | 325.7 | 268.9 | 329.8 | 324.6 | 309.6
874 | 711 | 468.3 | 187.32 | 218.9663 | 314.5 | 323.2 | 320.3 | 323.6 | 425 | 49.7 | 19.6 | 90.7 | 4.8 | 195.1 | 4.8 | 839.5 | 744 | 817.2 | 827 | 762.6 | 522.7 | 700.2 | 752.1 | 615.4 | 733 | 643.6 | 714.1 | 752.5 | 296.9 | 343.7 | 356.7 | 326.2 | 269.1 | 329.9 | 324.9 | 309.8
875 | 712 | 466.8 | 186.72 | 218.2649 | 315.7 | 323.2 | 321.3 | 324.7 | 423.8 | 49.7 | 19.6 | 90.6 | 5.2 | 188.7 | 4.9 | 835 | 741.5 | 815.7 | 826.4 | 759.1 | 523.3 | 709.7 | 743.6 | 615.4 | 730.5 | 644.6 | 706.5 | 751.1 | 297.3 | 344.3 | 357.7 | 326.4 | 269.3 | 330.5 | 325.1 | 309.9
876 | 713 | 468.6 | 187.44 | 219.1066 | 318.6 | 323.3 | 322.2 | 326.4 | 424 | 49.8 | 19.6 | 90.6 | 4.8 | 190.6 | 5.2 | 838.9 | 741.8 | 825.7 | 826.4 | 764 | 524 | 712 | 748.3 | 615.4 | 732.5 | 645.3 | 716.3 | 751.1 | 297.6 | 344.9 | 358.5 | 326.4 | 269.6 | 331.2 | 325.7 | 310.2
877 | 714 | 467.5 | 187 | 218.5922 | 319.9 | 322.9 | 323.6 | 327.4 | 424 | 49.9 | 19.6 | 90.6 | 4.3 | 188.5 | 5.3 | 842.5 | 743.1 | 829.6 | 826.2 | 765.9 | 524.9 | 707.2 | 756.2 | 615.5 | 734.7 | 644.9 | 727.1 | 750.4 | 298 | 345.3 | 359 | 326.5 | 269.8 | 332.1 | 326.1 | 310.4
878 | 715 | 467.2 | 186.88 | 218.452 | 319 | 322.9 | 324 | 327.7 | 425.2 | 49.9 | 19.6 | 90.6 | 4.5 | 189.8 | 5.5 | 847.1 | 744.5 | 834.4 | 826 | 766.1 | 525.8 | 701.2 | 761.9 | 615.4 | 736.3 | 643.5 | 734.1 | 750.1 | 298.3 | 346.1 | 359.2 | 326.6 | 270 | 332.5 | 326.7 | 310.6
879 | 716 | 469.1 | 187.64 | 219.3403 | 318.5 | 321.9 | 323.9 | 327.8 | 426.7 | 49.9 | 19.6 | 90.6 | 4 | 201.6 | 6.1 | 846.8 | 744.2 | 835.2 | 825.9 | 767.7 | 526.7 | 698.2 | 757.2 | 615.4 | 736 | 642.6 | 734.1 | 750 | 298.7 | 347.1 | 359.5 | 326.9 | 270.3 | 332.7 | 327.2 | 310.9
880 | 717 | 469.6 | 187.84 | 219.5741 | 319.6 | 321.7 | 324.4 | 328.1 | 425.3 | 50 | 19.6 | 90.6 | 3.8 | 196.4 | 6 | 843.7 | 742.7 | 830.8 | 825.5 | 766.1 | 527.5 | 698.4 | 749.9 | 615.3 | 733.3 | 642.1 | 722.8 | 748.7 | 299 | 347.6 | 360 | 327.3 | 270.5 | 332.8 | 327.4 | 311
881 | 718 | 468.7 | 187.48 | 219.1533 | 320.5 | 322 | 326.1 | 328.6 | 423.1 | 50 | 19.6 | 90.5 | 4.2 | 193.8 | 5.7 | 839.3 | 741.6 | 825.4 | 825.2 | 762.9 | 528.2 | 702.2 | 746.1 | 615.3 | 731.7 | 642 | 717.9 | 750.1 | 299.4 | 347.6 | 360.2 | 327.3 | 270.8 | 332.9 | 327.5 | 311.2
882 | 719 | 468.2 | 187.28 | 218.9195 | 321.2 | 321.8 | 326.8 | 328.7 | 422.7 | 50 | 19.6 | 90.6 | 4.4 | 190.3 | 5.5 | 839.3 | 742.1 | 826 | 825.4 | 763.9 | 529 | 700.1 | 752 | 615.3 | 733.1 | 642.3 | 725.7 | 752.3 | 299.8 | 347.7 | 360.3 | 327.2 | 271 | 332.9 | 327.5 | 311.3
883 | 720 | 468.6 | 187.44 | 219.1066 | 323.9 | 320.1 | 327.2 | 328.6 | 419 | 50 | 19.6 | 90.7 | 4.3 | 190.4 | 5.3 | 838.9 | 741.9 | 824.7 | 825.4 | 761.5 | 529.9 | 694.1 | 755.8 | 615.2 | 733.5 | 642.2 | 725.1 | 752.6 | 300.2 | 347.9 | 360.5 | 327.3 | 271.3 | 333.3 | 327.8 | 311.5
884 | 721 | 469.6 | 187.84 | 219.5741 | 324.5 | 319.6 | 326.8 | 328.6 | 418.5 | 50.1 | 19.6 | 90.7 | 4.3 | 194.5 | 5.1 | 840.6 | 741.8 | 824.3 | 825.1 | 761.8 | 530.7 | 691.3 | 761.8 | 615.2 | 734.9 | 641.7 | 727 | 752.2 | 300.5 | 348.1 | 360.6 | 327.6 | 271.5 | 333.5 | 328 | 311.6
885 | 722 | 468.9 | 187.56 | 219.2468 | 325.3 | 318.6 | 326.6 | 328.9 | 417.8 | 50.2 | 19.6 | 90.8 | 4.3 | 194.5 | 4.8 | 842.6 | 742.2 | 828.1 | 825 | 763.1 | 531.6 | 681.8 | 766 | 615.2 | 736.2 | 641 | 729.5 | 753.4 | 300.9 | 348.1 | 360.8 | 327.6 | 271.7 | 333.7 | 328 | 311.7
886 | 723 | 468.9 | 187.56 | 219.2468 | 325.8 | 318.3 | 326.5 | 328.9 | 421.2 | 50.2 | 19.6 | 90.8 | 4.5 | 193.5 | 4.6 | 841.8 | 743 | 830.1 | 825.4 | 764.5 | 532.5 | 677.3 | 770.8 | 615.2 | 736.7 | 640.2 | 734.5 | 754.9 | 301.3 | 348.1 | 360.9 | 327.6 | 272 | 334.2 | 328.1 | 311.9
887 | 724 | 469 | 187.6 | 219.2936 | 326.9 | 318.2 | 326.6 | 328.8 | 422.4 | 50.3 | 19.6 | 90.8 | 4.2 | 193.9 | 4.5 | 844.5 | 745.6 | 834.3 | 826.1 | 768.4 | 533.4 | 673.1 | 778.3 | 615.2 | 738.8 | 639.7 | 743.3 | 754.6 | 301.6 | 348.2 | 361.3 | 327.7 | 272.2 | 334.5 | 328.3 | 312
888 | 725 | 468.9 | 187.56 | 219.2468 | 327.4 | 318.9 | 326.8 | 328.1 | 418.6 | 50.3 | 19.6 | 90.7 | 3.6 | 192.9 | 4.5 | 844.4 | 748.1 | 834.8 | 826.2 | 768.3 | 534.4 | 671.2 | 778.6 | 615.3 | 739.1 | 639.4 | 746 | 753.5 | 302 | 348.3 | 361.4 | 327.7 | 272.5 | 334.6 | 328.4 | 312.2
889 | 726 | 468.7 | 187.48 | 219.1533 | 327.6 | 318.8 | 327.1 | 327.8 | 415.1 | 50.4 | 19.6 | 90.7 | 3.7 | 192 | 4.4 | 840.7 | 748.7 | 831.3 | 826.2 | 765.3 | 535.4 | 672.9 | 771.3 | 615.3 | 737.9 | 639.7 | 741.1 | 754.2 | 302.4 | 348.5 | 361.6 | 328.1 | 272.7 | 335 | 328.5 | 312.3
890 | 727 | 468.8 | 187.52 | 219.2001 | 327.9 | 318.9 | 327.5 | 327 | 414.6 | 50.5 | 19.6 | 90.7 | 4 | 190 | 4.4 | 837.9 | 749 | 831.6 | 826.3 | 765.3 | 536.2 | 676.9 | 766.6 | 615.4 | 737.1 | 640.1 | 740.8 | 754.3 | 302.7 | 348.8 | 361.9 | 328.5 | 273 | 335.3 | 328.6 | 312.5
891 | 728 | 469.1 | 187.64 | 219.3403 | 328.9 | 319.5 | 327.6 | 326.8 | 415.7 | 50.5 | 19.6 | 90.7 | 4.2 | 188 | 4.2 | 834.8 | 749.3 | 829 | 826.3 | 762.9 | 537.1 | 680.7 | 765.2 | 615.4 | 736.5 | 641.1 | 735.3 | 753.7 | 303.1 | 349 | 362.2 | 328.9 | 273.2 | 335.6 | 328.6 | 312.6
892 | 729 | 469.2 | 187.68 | 219.3871 | 330.6 | 320 | 328.3 | 326.8 | 415.4 | 50.4 | 19.6 | 90.8 | 4.3 | 189 | 3.7 | 828.2 | 748.3 | 820.8 | 826.4 | 759.7 | 537.9 | 690.4 | 759.1 | 615.4 | 735 | 641.4 | 718.3 | 753 | 303.4 | 349.3 | 362.6 | 329.4 | 273.5 | 335.8 | 328.6 | 312.7
893 | 730 | 468.4 | 187.36 | 219.013 | 331.5 | 320.1 | 329.3 | 327.5 | 415.2 | 50.3 | 19.6 | 90.9 | 5.1 | 189.2 | 3.3 | 821.3 | 746.9 | 811.9 | 825.8 | 756.6 | 538.8 | 699.4 | 751.7 | 615.5 | 732.4 | 642 | 710.4 | 751 | 303.8 | 349.8 | 363.1 | 329.9 | 273.8 | 335.9 | 328.6 | 312.9
894 | 731 | 468.3 | 187.32 | 218.9663 | 333.4 | 319.3 | 330.3 | 328.1 | 415.3 | 50.3 | 19.6 | 90.8 | 5.1 | 191.8 | 3 | 815.3 | 745.2 | 802.1 | 824.9 | 752 | 539.7 | 705.1 | 742.9 | 615.6 | 729.9 | 642.4 | 698.8 | 749 | 304.1 | 350.4 | 363.7 | 330.4 | 274 | 336.2 | 328.6 | 313
895 | 732 | 469.2 | 187.68 | 219.3871 | 335.1 | 318.8 | 331.9 | 328.4 | 414.8 | 50.2 | 19.6 | 90.7 | 5 | 204.5 | 2.9 | 812.7 | 743.6 | 796 | 824 | 747.4 | 540.5 | 713.2 | 732.3 | 615.6 | 727.1 | 642.7 | 688.2 | 749.4 | 304.5 | 350.7 | 364.2 | 330.6 | 274.3 | 336.9 | 328.9 | 313.2
896 | 733 | 469.4 | 187.76 | 219.4806 | 337.6 | 319.5 | 332.6 | 328.6 | 416.1 | 50.2 | 19.6 | 90.7 | 5.4 | 204.9 | 2.9 | 811.7 | 743.3 | 795.1 | 823.5 | 745.1 | 541.3 | 718.9 | 732.9 | 615.6 | 726 | 643.2 | 682.9 | 749.9 | 304.8 | 351 | 364.8 | 331 | 274.5 | 337.2 | 329.3 | 313.4
897 | 734 | 469.2 | 187.68 | 219.3871 | 339 | 319.6 | 332.6 | 328.5 | 419.2 | 50.3 | 19.6 | 90.7 | 5.2 | 190.5 | 3.4 | 808.7 | 742.9 | 791.7 | 823.4 | 741.6 | 542.2 | 719.2 | 735.7 | 615.6 | 726 | 643.6 | 676.3 | 749.6 | 305.2 | 351.5 | 365.8 | 331.3 | 274.8 | 338 | 329.6 | 313.6
898 | 735 | 469.9 | 187.96 | 219.7144 | 339.1 | 319.8 | 333.9 | 329.4 | 420.8 | 50.4 | 19.6 | 90.8 | 4.8 | 191.8 | 3.7 | 809.1 | 743.4 | 795 | 823.7 | 740.5 | 543 | 717.1 | 739.4 | 615.6 | 725.4 | 643.6 | 676.9 | 748.2 | 305.5 | 351.8 | 367.1 | 331.5 | 275.1 | 338.6 | 329.9 | 313.8
899 | 736 | 468.9 | 187.56 | 219.2468 | 339.7 | 319.9 | 335 | 330.7 | 424.1 | 50.5 | 19.6 | 90.9 | 4.7 | 194.6 | 3.7 | 811.7 | 745.9 | 800.9 | 824.2 | 742.5 | 544 | 716.9 | 754.7 | 615.6 | 728.8 | 643.4 | 690.9 | 747.2 | 305.9 | 352.1 | 367.6 | 331.5 | 275.3 | 339 | 330.4 | 314
900 | 737 | 468.9 | 187.56 | 219.2468 | 339.2 | 320.4 | 335.8 | 331.3 | 432.5 | 50.6 | 19.6 | 90.9 | 4.5 | 194.8 | 3.7 | 814.1 | 748.1 | 805.3 | 824.9 | 743.6 | 545.1 | 715.6 | 760.9 | 615.7 | 730.5 | 643.2 | 698.1 | 746 | 306.3 | 352.3 | 368.2 | 331.5 | 275.6 | 339.2 | 330.9 | 314.3
901 | 738 | 468.8 | 187.52 | 219.2001 | 338.6 | 320.3 | 336.2 | 332.2 | 431.5 | 50.7 | 19.6 | 91 | 4.7 | 196.8 | 3.4 | 817.1 | 750.6 | 811 | 825.3 | 743.1 | 546.1 | 708.5 | 764.8 | 615.6 | 731.4 | 642.3 | 704.7 | 745.8 | 306.7 | 352.6 | 368.5 | 331.6 | 275.9 | 339.1 | 331.4 | 314.5
902 | 739 | 469 | 187.6 | 219.2936 | 339.8 | 320.1 | 336.2 | 332.9 | 431.1 | 50.7 | 19.6 | 90.9 | 4.8 | 216.9 | 3 | 821 | 752.9 | 813.3 | 825.9 | 743.7 | 547.1 | 709.9 | 769.2 | 615.7 | 731.8 | 641.4 | 714.3 | 745.5 | 307 | 352.8 | 368.5 | 331.7 | 276.2 | 339.1 | 331.9 | 314.6
903 | 740 | 470 | 188 | 219.7612 | 340.1 | 319.5 | 336.4 | 332.8 | 429.2 | 50.8 | 19.6 | 91 | 4.7 | 238 | 2.9 | 827 | 755.9 | 815.1 | 825.8 | 748.4 | 548.2 | 705.2 | 773.9 | 615.7 | 733.8 | 641.2 | 730.9 | 747.5 | 307.4 | 352.6 | 368.4 | 331.7 | 276.4 | 339 | 332.4 | 314.9
904 | 741 | 469.4 | 187.76 | 219.4806 | 340.8 | 318.6 | 336.2 | 332.9 | 422.6 | 50.8 | 19.6 | 91 | 4.9 | 225.9 | 3.2 | 831.8 | 759 | 819.1 | 825.8 | 751.8 | 549.2 | 701.3 | 775.5 | 615.9 | 734.5 | 641.2 | 741.2 | 749.4 | 307.8 | 352.5 | 368.6 | 331.6 | 276.7 | 338.8 | 332.6 | 315.2
905 | 742 | 469.4 | 187.76 | 219.4806 | 340.1 | 317.8 | 335.2 | 332.7 | 419.5 | 50.9 | 19.6 | 91 | 4.8 | 180.1 | 3.1 | 835.9 | 761.5 | 825 | 825.6 | 756.6 | 550.4 | 695.7 | 779.3 | 616.1 | 737.1 | 641.3 | 747.5 | 750.1 | 308.2 | 352.4 | 368.3 | 331.5 | 277 | 338.8 | 332.8 | 315.4
906 | 743 | 469.1 | 187.64 | 219.3403 | 338.7 | 318.4 | 334.4 | 332.1 | 420.3 | 50.9 | 19.6 | 91 | 4.9 | 166.4 | 2.6 | 835.2 | 761.5 | 823.7 | 825.5 | 755.2 | 551.4 | 690.2 | 775.7 | 616.2 | 736.8 | 640.5 | 743.1 | 750.6 | 308.6 | 352.3 | 368.5 | 331.6 | 277.3 | 338.5 | 332.7 | 315.5
907 | 744 | 469.1 | 187.64 | 219.3403 | 336.9 | 319.1 | 333.7 | 330.8 | 417.3 | 50.9 | 19.6 | 91 | 5.4 | 194 | 3 | 833 | 759.8 | 820.7 | 825 | 754.1 | 552.4 | 686.5 | 767.1 | 616.3 | 735.4 | 639.9 | 738.4 | 750.5 | 309 | 352.2 | 368.5 | 331.9 | 277.5 | 338.6 | 332.7 | 315.6
908 | 745 | 469.2 | 187.68 | 219.3871 | 335.7 | 320.1 | 334.3 | 329 | 415.7 | 50.9 | 19.6 | 91 | 4.5 | 234 | 4 | 826.7 | 757.2 | 813.4 | 824.1 | 751.7 | 553.2 | 695.3 | 755.7 | 616.4 | 732.6 | 640 | 727.8 | 749.6 | 309.4 | 352.2 | 368.7 | 332.2 | 277.8 | 338.9 | 332.7 | 315.7
909 | 746 | 467.9 | 187.16 | 218.7793 | 334.5 | 320.2 | 335 | 328.4 | 414.3 | 50.9 | 19.6 | 91 | 4.8 | 216.5 | 4.7 | 828.3 | 756.4 | 811.8 | 823.3 | 752.5 | 554.1 | 696.5 | 750.7 | 616.6 | 731.4 | 640.5 | 730 | 750.4 | 309.8 | 352 | 368.5 | 332.5 | 278 | 338.6 | 332.6 | 315.8
910 | 747 | 468 | 187.2 | 218.826 | 333.7 | 320.3 | 334.7 | 328.9 | 409.5 | 50.9 | 19.6 | 91 | 4.7 | 200.2 | 5.2 | 832.6 | 755.6 | 812.9 | 822.5 | 752.9 | 555 | 693.1 | 751.6 | 616.9 | 731.5 | 640.8 | 734 | 753.3 | 310.2 | 352.1 | 368 | 332.9 | 278.3 | 338.9 | 332.4 | 316
911 | 748 | 468.8 | 187.52 | 219.2001 | 332.9 | 321.1 | 333.4 | 328.7 | 406.7 | 50.9 | 19.6 | 90.9 | 4.8 | 216.3 | 5.2 | 837.4 | 756.1 | 813.3 | 821.9 | 753.8 | 556 | 688.7 | 760 | 617.1 | 733.7 | 640.7 | 742.7 | 756.6 | 310.6 | 352.3 | 367.6 | 332.9 | 278.6 | 339.3 | 332.4 | 316.1
912 | 749 | 469 | 187.6 | 219.2936 | 332.7 | 321.1 | 331.7 | 327.8 | 403.9 | 50.9 | 19.6 | 91 | 4.7 | 230.9 | 5 | 842 | 756.4 | 817.6 | 821.4 | 756.7 | 557 | 683.7 | 762 | 617.3 | 733.7 | 640.4 | 746.7 | 759.2 | 311 | 352.3 | 367.6 | 332.9 | 278.8 | 339.1 | 332.4 | 316.3
913 | 750 | 469.6 | 187.84 | 219.5741 | 332.8 | 320.1 | 330.7 | 327.6 | 402.9 | 50.9 | 19.6 | 91.2 | 5 | 208.5 | 4.6 | 846.7 | 757.3 | 823.5 | 820.7 | 758.9 | 558 | 676.8 | 766.9 | 617.6 | 735.1 | 640 | 752.8 | 758.9 | 311.3 | 351.8 | 367.3 | 332.8 | 279.1 | 338.8 | 332.3 | 316.4
914 | 751 | 469 | 187.6 | 219.2936 | 333.6 | 319.9 | 330.7 | 327.3 | 407 | 50.9 | 19.6 | 91.2 | 4.7 | 204.7 | 4.3 | 844.8 | 758.3 | 826 | 820.9 | 759.5 | 559.1 | 671.4 | 771.8 | 617.8 | 736.2 | 638.8 | 754 | 756.8 | 311.7 | 351.7 | 367.1 | 332.9 | 279.3 | 338.7 | 332.3 | 316.4
915 | 752 | 469.7 | 187.88 | 219.6209 | 335.3 | 319.5 | 330.4 | 327.5 | 408 | 50.9 | 19.6 | 91.3 | 5 | 225.7 | 3.6 | 840.8 | 758.3 | 826.5 | 821.2 | 759.7 | 560 | 666 | 769.7 | 617.9 | 735.2 | 637.9 | 746.8 | 754.8 | 312.1 | 351.5 | 367.1 | 333.1 | 279.6 | 338.7 | 332.3 | 316.6
916 | 753 | 469.4 | 187.76 | 219.4806 | 334.7 | 318.4 | 331.2 | 328.2 | 407.7 | 51 | 19.5 | 91.5 | 5.6 | 222.7 | 3.5 | 840.8 | 758.4 | 829.2 | 821.8 | 760.1 | 560.9 | 660 | 768.5 | 618.1 | 734.8 | 637.5 | 742.5 | 753.5 | 312.5 | 351.4 | 366.9 | 333.3 | 279.9 | 338.8 | 332.2 | 316.6
917 | 754 | 469.5 | 187.8 | 219.5274 | 334.1 | 317.9 | 331.8 | 328.4 | 412.6 | 51 | 19.5 | 91.5 | 4.6 | 222.5 | 3.2 | 840.9 | 757.6 | 830.5 | 822.1 | 761.2 | 561.8 | 666.5 | 763.6 | 618.3 | 734.2 | 637.9 | 735.2 | 751.6 | 312.8 | 351.5 | 367 | 333.6 | 280.1 | 339 | 332.2 | 316.7
918 | 755 | 469 | 187.6 | 219.2936 | 334 | 318.7 | 331.7 | 328 | 414.2 | 51 | 19.5 | 91.5 | 4.5 | 238 | 3.1 | 839 | 756.4 | 829.6 | 821.7 | 759.4 | 562.7 | 664.9 | 758.7 | 618.5 | 733.4 | 638 | 732 | 750.2 | 313.2 | 352 | 367.5 | 334.1 | 280.4 | 339.5 | 332.5 | 316.9
919 | 756 | 469 | 187.6 | 219.2936 | 335.1 | 318.9 | 332.3 | 328.6 | 411.7 | 51.1 | 19.5 | 91.4 | 4.9 | 248.6 | 2.7 | 833.7 | 754.5 | 826.1 | 821 | 757.5 | 563.6 | 665.4 | 743.1 | 618.7 | 729.8 | 637.9 | 722.7 | 749.8 | 313.6 | 352.2 | 367.9 | 334.3 | 280.6 | 339.7 | 332.8 | 317.1
920 | 757 | 469.5 | 187.8 | 219.5274 | 337.5 | 319.8 | 332.9 | 329.3 | 411.1 | 51.1 | 19.5 | 91.3 | 4.8 | 247 | 2.5 | 835.7 | 754.6 | 830.5 | 820.4 | 759.6 | 564.5 | 669 | 742.7 | 618.9 | 729.5 | 638.2 | 724.5 | 747.9 | 313.9 | 352.4 | 368.1 | 334.4 | 280.9 | 340.3 | 332.9 | 317.2
921 | 758 | 469.1 | 187.64 | 219.3403 | 339.6 | 319.3 | 333.4 | 329.8 | 414.6 | 51.1 | 19.5 | 91.3 | 4.6 | 225.5 | 2.6 | 839.2 | 756.8 | 833.5 | 820.4 | 761.9 | 565.5 | 666.6 | 751.7 | 619.1 | 732.1 | 638 | 733.2 | 746.9 | 314.3 | 352.8 | 368.4 | 334.6 | 281.1 | 340.7 | 333.3 | 317.4
922 | 759 | 469.3 | 187.72 | 219.4339 | 341.4 | 320.9 | 333.9 | 330.5 | 421.7 | 51.2 | 19.5 | 91.3 | 4.4 | 201.5 | 2.9 | 834.9 | 758.4 | 829 | 821 | 761.4 | 566.5 | 668.7 | 756.8 | 619.2 | 733.1 | 637.1 | 734.9 | 745.2 | 314.7 | 352.9 | 368.6 | 334.8 | 281.3 | 341.2 | 333.4 | 317.5
923 | 760 | 469.3 | 187.72 | 219.4339 | 342.2 | 321.1 | 333.7 | 330.9 | 421.2 | 51.1 | 19.5 | 91.3 | 5.1 | 222.3 | 3 | 829.7 | 759.1 | 821.5 | 821.6 | 757.9 | 567.6 | 668.9 | 757.1 | 619.5 | 733.1 | 636.6 | 735.1 | 744 | 315 | 352.8 | 368.7 | 335 | 281.6 | 341.9 | 333.7 | 317.7
924 | 761 | 469.5 | 187.8 | 219.5274 | 341.9 | 321.1 | 333.4 | 331.4 | 417.6 | 51.1 | 19.5 | 91.3 | 5.3 | 244.8 | 3.3 | 821.5 | 758.2 | 811.6 | 822.1 | 753.5 | 568.6 | 674.7 | 753.5 | 619.7 | 731.6 | 636.5 | 723.1 | 742.4 | 315.3 | 353.1 | 369 | 335.3 | 281.8 | 342.5 | 333.9 | 317.9
925 | 762 | 469.4 | 187.76 | 219.4806 | 343.2 | 321 | 334.4 | 332.2 | 421 | 51 | 19.5 | 91.4 | 4.6 | 228.3 | 3.3 | 819.6 | 757.6 | 810.1 | 822.5 | 752.1 | 569.6 | 685.2 | 747.8 | 619.8 | 730.3 | 636.2 | 714.9 | 741.6 | 315.7 | 353.6 | 369.4 | 335.7 | 282.1 | 343.2 | 334.1 | 318.1
926 | 763 | 467.9 | 187.16 | 218.7793 | 344.6 | 321.4 | 335 | 332.5 | 421 | 51 | 19.5 | 91.5 | 4.6 | 217.9 | 3.3 | 820.6 | 758.4 | 811.3 | 823.2 | 751.3 | 570.6 | 688.3 | 756.5 | 620 | 730.4 | 636.3 | 711.3 | 741.1 | 316 | 354 | 370.5 | 336 | 282.4 | 344.1 | 334.4 | 318.2
927 | 764 | 469 | 187.6 | 219.2936 | 344.7 | 322.5 | 335.7 | 333.1 | 425.3 | 51.2 | 19.5 | 91.5 | 4.5 | 245.6 | 3.6 | 824.1 | 760.7 | 816.4 | 824.1 | 751.7 | 571.7 | 689.7 | 764.9 | 620.2 | 733.1 | 636.4 | 719.1 | 741.7 | 316.4 | 354.5 | 371.5 | 336.2 | 282.6 | 344.4 | 334.7 | 318.5
928 | 765 | 469.4 | 187.76 | 219.4806 | 344.7 | 322.7 | 336 | 333.2 | 422.7 | 51.3 | 19.5 | 91.6 | 4.9 | 264.4 | 3.9 | 832.4 | 762.8 | 820.9 | 823.9 | 755.3 | 572.8 | 685.3 | 768.7 | 620.5 | 734.2 | 636.5 | 731.2 | 745.3 | 316.7 | 354.7 | 371.7 | 336.2 | 282.9 | 344.8 | 335 | 318.7
929 | 766 | 467.4 | 186.96 | 218.5455 | 343.7 | 322.5 | 335.9 | 333.5 | 418.8 | 51.3 | 19.5 | 91.6 | 4.7 | 261.6 | 3.7 | 838.3 | 764 | 820.1 | 823.1 | 759 | 574 | 681.1 | 772.2 | 620.8 | 735.8 | 636.6 | 739 | 747.6 | 317.1 | 354.7 | 371.6 | 336.1 | 283.2 | 344.8 | 335.4 | 318.9
930 | 767 | 465.3 | 186.12 | 217.5636 | 341.5 | 321.9 | 336 | 333.7 | 414.8 | 51.3 | 19.5 | 91.6 | 4.7 | 264.1 | 3.8 | 845.6 | 765.3 | 820.5 | 822.7 | 761.5 | 575.1 | 674.8 | 776.9 | 621.1 | 737.4 | 636.6 | 749.2 | 751 | 317.4 | 354.5 | 371.2 | 336 | 283.4 | 345 | 335.7 | 319.1
931 | 768 | 464.7 | 185.88 | 217.283 | 340.1 | 321.5 | 335.8 | 333.2 | 411.1 | 51.4 | 19.5 | 91.6 | 4.4 | 257 | 4.2 | 849.7 | 765.6 | 821 | 822 | 760.4 | 576.2 | 667.2 | 780 | 621.4 | 737.7 | 636.5 | 752.8 | 753.7 | 317.8 | 354.3 | 370.8 | 335.9 | 283.7 | 344.8 | 335.8 | 319.2
932 | 769 | 466.2 | 186.48 | 217.9844 | 339.1 | 321.9 | 335.3 | 332.5 | 408.9 | 51.4 | 19.5 | 91.6 | 4 | 253.1 | 4.1 | 855.6 | 766.2 | 826.7 | 821.4 | 763.5 | 577.3 | 661 | 782.1 | 621.7 | 738.8 | 636.3 | 755 | 756 | 318.1 | 354.2 | 370.5 | 336.1 | 284 | 344.8 | 336.1 | 319.4
933 | 770 | 466.5 | 186.6 | 218.1246 | 337.6 | 321 | 334.8 | 332 | 405 | 51.5 | 19.5 | 91.6 | 4.2 | 259.4 | 4.1 | 857.9 | 766 | 827.8 | 820.6 | 764 | 578.3 | 655 | 782.7 | 622 | 739.3 | 636.2 | 753.4 | 757.8 | 318.5 | 354.1 | 370.4 | 336.1 | 284.2 | 344.9 | 336.2 | 319.5
934 | 771 | 466.8 | 186.72 | 218.2649 | 336.7 | 320.1 | 334.7 | 332 | 401.1 | 51.6 | 19.5 | 91.6 | 4.7 | 243.3 | 3.8 | 850.1 | 764.1 | 820.5 | 820.3 | 761.7 | 579.3 | 651.2 | 767.8 | 622.3 | 735.5 | 636.8 | 744.5 | 763.5 | 318.8 | 353.9 | 370.3 | 336 | 284.5 | 344.4 | 336.2 | 319.7
935 | 772 | 468 | 187.2 | 218.826 | 336.6 | 319 | 334.8 | 331.5 | 396.4 | 51.6 | 19.5 | 91.5 | 5 | 207.1 | 3.4 | 851.1 | 764.3 | 819.2 | 819.9 | 765.8 | 580.4 | 654.6 | 764.5 | 622.7 | 735.4 | 638.4 | 751.1 | 766.2 | 319.2 | 353.6 | 370 | 335.9 | 284.8 | 344 | 336.1 | 319.8
936 | 773 | 469.3 | 187.72 | 219.4339 | 335.8 | 318.3 | 334.8 | 330.5 | 393.5 | 51.6 | 19.5 | 91.4 | 4.8 | 189.2 | 3 | 855.1 | 764.9 | 824.3 | 819.9 | 767.8 | 581.6 | 656 | 771.7 | 623.1 | 737.4 | 638.8 | 758.8 | 767.7 | 319.5 | 353.3 | 369.8 | 336 | 285.1 | 343.7 | 336 | 319.9
937 | 774 | 468 | 187.2 | 218.826 | 335 | 318.4 | 334.8 | 329.5 | 391.8 | 51.7 | 19.5 | 91.4 | 5 | 202.7 | 2.6 | 857.8 | 766.3 | 826.5 | 820.4 | 769.4 | 582.8 | 652.3 | 778.3 | 623.4 | 739.4 | 637.8 | 763 | 768 | 319.8 | 353 | 369.5 | 336.2 | 285.4 | 343.6 | 336 | 320
938 | 775 | 466.8 | 186.72 | 218.2649 | 334.2 | 319.3 | 334.5 | 328.6 | 390.5 | 51.8 | 19.5 | 91.4 | 4.6 | 237.9 | 2.6 | 857.2 | 766.3 | 826.4 | 820.2 | 771.5 | 583.9 | 647.7 | 783.7 | 623.8 | 740.9 | 636.9 | 767.5 | 769.9 | 320.2 | 352.6 | 369 | 336.2 | 285.6 | 343.8 | 336.2 | 320.2
939 | 776 | 467.3 | 186.92 | 218.4987 | 333.7 | 319 | 334.5 | 327.7 | 390.1 | 51.7 | 19.5 | 91.6 | 4.5 | 256 | 2.7 | 853.6 | 767 | 824.2 | 820.4 | 769.5 | 585 | 647 | 786 | 624.2 | 741.1 | 636.8 | 765.7 | 770.8 | 320.5 | 352.3 | 368.6 | 336.3 | 285.9 | 343.6 | 336.2 | 320.2
940 | 777 | 467.4 | 186.96 | 218.5455 | 332.6 | 318.9 | 334.6 | 327.3 | 392 | 51.8 | 19.5 | 91.7 | 4.9 | 264.6 | 3 | 854.3 | 767.1 | 825 | 820.6 | 767.8 | 586.1 | 645 | 793.5 | 624.6 | 742.4 | 636.7 | 765.6 | 770.9 | 320.8 | 352 | 368.3 | 336.3 | 286.1 | 343.5 | 336 | 320.3
941 | 778 | 467.1 | 186.84 | 218.4052 | 331.7 | 319.1 | 334.8 | 326.8 | 391.7 | 51.8 | 19.5 | 91.8 | 5 | 263.7 | 3.1 | 850.1 | 767 | 818.5 | 821 | 766.6 | 587.2 | 642.5 | 791.8 | 625 | 742.1 | 636.8 | 763.3 | 771.9 | 321.1 | 351.8 | 368.1 | 336.4 | 286.4 | 343.6 | 335.8 | 320.5
942 | 779 | 467.8 | 187.12 | 218.7325 | 332.9 | 318.7 | 335.3 | 327.2 | 388.9 | 51.8 | 19.5 | 91.8 | 5.3 | 257 | 3 | 847.8 | 766.3 | 812 | 821.1 | 764.2 | 588.3 | 641.3 | 786.9 | 625.5 | 740.4 | 637.4 | 761.8 | 774.8 | 321.4 | 351.6 | 367.6 | 336.4 | 286.7 | 343.7 | 335.7 | 320.6
943 | 780 | 467.9 | 187.16 | 218.7793 | 334.4 | 318.4 | 335.4 | 327.2 | 387.2 | 51.8 | 19.5 | 91.7 | 4.9 | 244.1 | 2.9 | 849.5 | 766 | 811.1 | 820.7 | 764.1 | 589.4 | 640.4 | 787.7 | 625.8 | 742.2 | 637.6 | 764.9 | 776.6 | 321.7 | 351.4 | 366.9 | 336.5 | 286.9 | 343.4 | 335.6 | 320.7
944 | 781 | 467.7 | 187.08 | 218.6857 | 334 | 319.3 | 335.1 | 326.3 | 390.1 | 51.9 | 19.5 | 91.7 | 4.5 | 238.3 | 2.8 | 838.1 | 764.6 | 807.2 | 820.7 | 760.8 | 590.5 | 644.6 | 783.3 | 626.2 | 742.5 | 637.7 | 754.1 | 773.8 | 321.9 | 351.6 | 366.7 | 336.9 | 287.1 | 343.7 | 335.4 | 320.7
945 | 782 | 467.4 | 186.96 | 218.5455 | 335.5 | 320.1 | 334.9 | 325.7 | 396.9 | 51.9 | 19.5 | 91.6 | 4.3 | 243 | 2.7 | 835 | 764.2 | 812 | 821.3 | 760.5 | 591.5 | 652.5 | 784.4 | 626.5 | 742.6 | 637.8 | 747.9 | 768.1 | 322.2 | 351.6 | 366.8 | 337.3 | 287.4 | 343.6 | 335.5 | 320.8
946 | 783 | 467.7 | 187.08 | 218.6857 | 336.7 | 319.9 | 335.2 | 325.6 | 401.8 | 51.9 | 19.5 | 91.6 | 3.9 | 248 | 2.5 | 836.2 | 764.8 | 818.3 | 821.9 | 760.6 | 592.7 | 654.4 | 791.6 | 626.9 | 744.6 | 637.2 | 751 | 764 | 322.5 | 351.7 | 366.8 | 337.6 | 287.6 | 343.4 | 335.4 | 320.9
947 | 784 | 468.2 | 187.28 | 218.9195 | 337.2 | 320 | 335.1 | 326.6 | 405.3 | 51.9 | 19.5 | 91.6 | 4.6 | 248.8 | 2.5 | 838.6 | 766.1 | 823.5 | 822.4 | 765 | 593.9 | 654.9 | 792.5 | 627.3 | 746.1 | 636.4 | 754.4 | 760.3 | 322.8 | 352.2 | 367.1 | 338.1 | 287.9 | 343.6 | 335.5 | 321
948 | 785 | 468 | 187.2 | 218.826 | 337.6 | 321.1 | 334.7 | 326.7 | 408.2 | 51.9 | 19.5 | 91.6 | 4.6 | 248.4 | 2.7 | 845.2 | 767.4 | 829.5 | 822.4 | 768.3 | 595.1 | 657 | 795 | 627.7 | 747.8 | 635.7 | 763.4 | 757.3 | 323.1 | 352.7 | 367.7 | 338.4 | 288.1 | 344.2 | 335.7 | 321.2
949 | 786 | 468.1 | 187.24 | 218.8728 | 338.1 | 321 | 334.3 | 327.2 | 411.7 | 51.8 | 19.5 | 91.6 | 5.3 | 254.2 | 2.9 | 851 | 767.8 | 833.9 | 822.2 | 772.8 | 596.3 | 652.5 | 790.1 | 628.1 | 748 | 634.7 | 765.5 | 756.5 | 323.3 | 353 | 368 | 338.5 | 288.4 | 344.3 | 336 | 321.3
950 | 787 | 468 | 187.2 | 218.826 | 337.9 | 321.1 | 334.1 | 327.6 | 416.8 | 51.8 | 19.5 | 91.6 | 5.4 | 259.4 | 3 | 851.3 | 767.7 | 833.1 | 822.4 | 775.4 | 597.4 | 650.3 | 787.7 | 628.5 | 747.8 | 634.9 | 765.7 | 755.1 | 323.6 | 353.3 | 368.3 | 338.8 | 288.6 | 344.1 | 336.2 | 321.5
951 | 788 | 468.1 | 187.24 | 218.8728 | 337.2 | 321 | 333.7 | 328.1 | 416.7 | 51.8 | 19.5 | 91.5 | 4.9 | 240.3 | 2.8 | 847 | 767.1 | 830.6 | 822.6 | 774.5 | 598.6 | 650.3 | 786.2 | 628.8 | 747.7 | 635.4 | 761.6 | 753.4 | 323.9 | 353.6 | 368.8 | 338.8 | 288.8 | 343.9 | 336.2 | 321.6
952 | 789 | 467.9 | 187.16 | 218.7793 | 335.8 | 320 | 333.8 | 328.7 | 419.6 | 51.8 | 19.5 | 91.5 | 5.7 | 231.7 | 2.8 | 845.6 | 766.5 | 833.3 | 823.2 | 775.5 | 599.7 | 652.8 | 785.5 | 629.2 | 748.6 | 635.1 | 753.9 | 751.3 | 324.2 | 353.8 | 368.9 | 338.9 | 289.1 | 343.9 | 336.3 | 321.7
953 | 790 | 467.8 | 187.12 | 218.7325 | 335.7 | 320.4 | 334.3 | 328.2 | 423.2 | 51.7 | 19.5 | 91.5 | 5.2 | 241.1 | 2.8 | 841.3 | 764.9 | 831.3 | 824.1 | 774.2 | 600.9 | 656.2 | 780.5 | 629.5 | 747.8 | 635 | 748.8 | 749.8 | 324.5 | 354.1 | 368.9 | 339.1 | 289.3 | 343.7 | 336.4 | 321.8
954 | 791 | 468.1 | 187.24 | 218.8728 | 336 | 320.5 | 334.7 | 327.3 | 430.2 | 51.7 | 19.5 | 91.6 | 4.9 | 215 | 3.4 | 838.6 | 764.8 | 829.3 | 824.8 | 775.3 | 602.2 | 659.1 | 776.4 | 629.9 | 748.2 | 635.4 | 751.2 | 747.5 | 324.8 | 354.3 | 369.1 | 339.2 | 289.6 | 343.8 | 336.4 | 322
955 | 792 | 467.8 | 187.12 | 218.7325 | 336.2 | 321.2 | 335.1 | 327.6 | 428.6 | 51.7 | 19.5 | 91.7 | 4.9 | 224.2 | 3.7 | 837.3 | 765.6 | 830.2 | 825.5 | 775.5 | 603.5 | 664.2 | 772.9 | 630.2 | 748 | 636.3 | 753.4 | 745.2 | 325 | 354.6 | 369.2 | 339.4 | 289.8 | 343.9 | 336.4 | 322.1
956 | 793 | 468 | 187.2 | 218.826 | 336.6 | 322.1 | 335.1 | 328.4 | 424.2 | 51.6 | 19.4 | 91.7 | 4.8 | 219 | 3.7 | 842.4 | 767.6 | 835.5 | 825.5 | 778.4 | 604.9 | 662.6 | 777.4 | 630.7 | 749.3 | 636.4 | 762.6 | 743.3 | 325.3 | 354.6 | 369 | 339.5 | 290 | 343.9 | 336.5 | 322.2
957 | 794 | 468.6 | 187.44 | 219.1066 | 339.4 | 321.7 | 335 | 328.9 | 421.7 | 51.5 | 19.4 | 91.8 | 4.9 | 206.1 | 3.3 | 845.9 | 769.5 | 837.9 | 825.1 | 781.9 | 606.3 | 663.1 | 785.6 | 631.2 | 751.2 | 636.8 | 769.8 | 742.8 | 325.6 | 354.5 | 368.7 | 339.4 | 290.3 | 344.3 | 336.7 | 322.4
958 | 795 | 468.6 | 187.44 | 219.1066 | 340.3 | 321.4 | 334.5 | 328.7 | 421.9 | 51.5 | 19.4 | 91.8 | 4.8 | 239.7 | 3 | 850.9 | 771.5 | 839.9 | 825.4 | 784.3 | 607.8 | 660.2 | 795.3 | 631.6 | 753.9 | 636.8 | 776.3 | 742.8 | 325.9 | 354.5 | 368.4 | 339.6 | 290.5 | 344.7 | 336.8 | 322.5
959 | 796 | 467.8 | 187.12 | 218.7325 | 340.5 | 322.2 | 333.4 | 328.4 | 417.2 | 51.5 | 19.4 | 91.8 | 5.1 | 253.7 | 3 | 854.1 | 771.7 | 840.6 | 825.5 | 784 | 609 | 656.9 | 799.9 | 632.1 | 754.3 | 636.1 | 776.2 | 743.1 | 326.2 | 354.5 | 368.4 | 339.9 | 290.7 | 344.8 | 337 | 322.7
960 | 797 | 467.9 | 187.16 | 218.7793 | 340 | 323.6 | 333.5 | 327.8 | 415.6 | 51.6 | 19.4 | 91.9 | 5 | 223.4 | 2.8 | 853.3 | 771.9 | 840.6 | 825.9 | 784.8 | 610.3 | 652.1 | 804.4 | 632.5 | 755 | 636 | 775.2 | 743.1 | 326.5 | 354.3 | 368.4 | 339.9 | 291 | 344.3 | 337.1 | 322.8
961 | 798 | 467.6 | 187.04 | 218.639 | 338.6 | 325.6 | 333.9 | 327.1 | 413.9 | 51.7 | 19.4 | 92 | 4.6 | 224.7 | 3.2 | 855.3 | 771.8 | 841.6 | 826 | 786.9 | 611.5 | 649.8 | 805.4 | 632.9 | 756 | 635.4 | 778.6 | 742.9 | 326.8 | 354.1 | 368.4 | 339.8 | 291.2 | 343.9 | 337 | 322.9
962 | 799 | 467.4 | 186.96 | 218.5455 | 336.6 | 326.3 | 333.9 | 326.5 | 413.4 | 51.7 | 19.4 | 92.1 | 4.9 | 235.1 | 3.6 | 858.2 | 771.4 | 838 | 825.9 | 787.9 | 612.7 | 649.4 | 803.5 | 633.3 | 757.1 | 634.7 | 778.1 | 745.2 | 327.1 | 353.9 | 368.3 | 339.8 | 291.5 | 343.5 | 337 | 323
963 | 800 | 466.5 | 186.6 | 218.1246 | 335.3 | 325.6 | 333.7 | 326.2 | 412.7 | 51.7 | 19.4 | 92.2 | 5.1 | 219 | 4.1 | 859.8 | 770.3 | 834.7 | 825.4 | 788.7 | 613.9 | 646.3 | 801.6 | 633.8 | 756.7 | 634.9 | 779.6 | 749.5 | 327.3 | 353.7 | 368.3 | 339.8 | 291.7 | 343.5 | 337 | 323.2
964 | 801 | 466.9 | 186.76 | 218.3117 | 334.8 | 325.3 | 333.6 | 325.6 | 410.1 | 51.8 | 19.4 | 92.3 | 5.4 | 225.9 | 4.3 | 860.2 | 769.5 | 835.3 | 825.7 | 789.9 | 615.1 | 641.2 | 798.4 | 634.3 | 756.5 | 635.7 | 780.3 | 751.8 | 327.6 | 353.6 | 368.3 | 339.9 | 291.9 | 343.6 | 337.1 | 323.2
965 | 802 | 468 | 187.2 | 218.826 | 334.6 | 325.7 | 333.6 | 325.2 | 408.3 | 51.8 | 19.4 | 92.4 | 5 | 245.6 | 4.7 | 862.6 | 769.4 | 835.4 | 825.8 | 791.6 | 616.3 | 636.8 | 795.2 | 634.8 | 756.3 | 636.7 | 778.4 | 752.5 | 327.9 | 353.5 | 368.1 | 339.9 | 292.2 | 343.3 | 337.2 | 323.4
966 | 803 | 467.6 | 187.04 | 218.639 | 335.4 | 325.5 | 333.6 | 325.3 | 407.5 | 51.9 | 19.4 | 92.5 | 4.7 | 236 | 4.6 | 864.9 | 770.1 | 839.2 | 825.3 | 793.4 | 617.6 | 635.6 | 798.6 | 635.3 | 758.1 | 636.9 | 781.3 | 752.5 | 328.2 | 353.2 | 367.9 | 339.8 | 292.4 | 343.2 | 337.3 | 323.6
967 | 804 | 466.9 | 186.76 | 218.3117 | 336.4 | 325.1 | 333.7 | 325.2 | 407.8 | 51.9 | 19.4 | 92.6 | 4.6 | 239.6 | 4.4 | 866.1 | 771.5 | 843.5 | 825 | 796.3 | 618.9 | 636.5 | 801.9 | 635.8 | 758.8 | 636.4 | 784.5 | 752.9 | 328.4 | 352.9 | 367.6 | 339.8 | 292.6 | 343.5 | 337.3 | 323.7
968 | 805 | 467.7 | 187.08 | 218.6857 | 338.8 | 325.4 | 333.6 | 324.8 | 410.1 | 52 | 19.4 | 92.6 | 4.8 | 255.5 | 4.7 | 868.4 | 772.6 | 844 | 825.5 | 796.7 | 620.1 | 637.4 | 800.9 | 636.3 | 759.1 | 636.2 | 786.4 | 752.6 | 328.7 | 353 | 367.7 | 340 | 292.8 | 343.6 | 337.3 | 323.8
969 | 806 | 467.3 | 186.92 | 218.4987 | 340.5 | 326.7 | 333 | 323.8 | 407.4 | 52 | 19.4 | 92.7 | 4.6 | 249.1 | 5.5 | 866.1 | 773.1 | 842.6 | 826.3 | 797 | 621.3 | 636.3 | 803.8 | 636.8 | 759.4 | 636.2 | 782.7 | 752.5 | 329 | 352.9 | 367.8 | 340.1 | 293.1 | 343.7 | 337.3 | 323.9
970 | 807 | 468.2 | 187.28 | 218.9195 | 340.8 | 328 | 332.7 | 323.4 | 404.6 | 52.1 | 19.4 | 92.7 | 4.5 | 265.4 | 6 | 864.6 | 773.3 | 843.2 | 826.8 | 799.8 | 622.6 | 633.6 | 802.4 | 637.3 | 760.3 | 637.3 | 781.3 | 751.3 | 329.2 | 352.7 | 367.6 | 340.1 | 293.3 | 343.7 | 337.3 | 324
971 | 808 | 467.7 | 187.08 | 218.6857 | 341.1 | 329 | 332.6 | 322.7 | 404.8 | 52.1 | 19.4 | 92.8 | 4.6 | 253.7 | 6.5 | 865.4 | 774.2 | 846.2 | 826.9 | 803.7 | 623.8 | 634.1 | 800.6 | 637.9 | 760.6 | 637.5 | 783.7 | 750.1 | 329.5 | 352.5 | 367.3 | 340.1 | 293.5 | 343.9 | 337.4 | 324.1
972 | 809 | 467.6 | 187.04 | 218.639 | 340.7 | 329.7 | 332.4 | 322.3 | 407.2 | 52.1 | 19.4 | 92.8 | 4.9 | 239.1 | 6.5 | 865.3 | 775.6 | 849 | 827.5 | 805.5 | 625 | 634.9 | 804.6 | 638.4 | 762.2 | 636.6 | 786.7 | 750.4 | 329.7 | 352.6 | 367.2 | 340.3 | 293.8 | 344.1 | 337.4 | 324.2
973 | 810 | 468.3 | 187.32 | 218.9663 | 339.3 | 330 | 332.1 | 322.1 | 412.6 | 52.1 | 19.4 | 92.8 | 4.8 | 237.8 | 6.5 | 866.6 | 776.4 | 851.1 | 828.3 | 806.8 | 626.2 | 636.6 | 805.5 | 639 | 763.5 | 635.7 | 787 | 749.6 | 330 | 352.4 | 367 | 340.4 | 294 | 344.3 | 337.5 | 324.3
974 | 811 | 468.2 | 187.28 | 218.9195 | 338.3 | 330.1 | 332.1 | 322 | 414.9 | 52.1 | 19.4 | 92.8 | 4.8 | 248.7 | 6.9 | 862.2 | 775.9 | 850 | 829.1 | 808.2 | 627.3 | 636.3 | 805.9 | 639.5 | 763.7 | 635.8 | 784.6 | 749.2 | 330.2 | 352.4 | 367 | 340.5 | 294.2 | 344.3 | 337.6 | 324.4
975 | 812 | 468 | 187.2 | 218.826 | 337.4 | 330.8 | 331.9 | 321.5 | 416.2 | 52.1 | 19.4 | 92.8 | 5.2 | 238.7 | 6.7 | 861.8 | 776.6 | 850 | 829.4 | 811 | 628.4 | 635.1 | 803.2 | 640 | 763.5 | 635.7 | 783.8 | 748.5 | 330.5 | 352.2 | 367 | 340.6 | 294.5 | 344.2 | 337.5 | 324.4
976 | 813 | 467.9 | 187.16 | 218.7793 | 336.7 | 331 | 331.5 | 321.1 | 414.3 | 52.1 | 19.4 | 92.8 | 4.5 | 237 | 6.5 | 862.1 | 777 | 852.1 | 829.8 | 813.1 | 629.5 | 635.5 | 804.8 | 640.5 | 764.2 | 635.8 | 784.5 | 747.3 | 330.7 | 352.2 | 366.9 | 340.6 | 294.7 | 344.1 | 337.5 | 324.6
977 | 814 | 468.5 | 187.4 | 219.0598 | 335.9 | 331.1 | 331.6 | 320.8 | 414.2 | 52.2 | 19.4 | 92.8 | 4.4 | 245.2 | 6.9 | 861.2 | 776.7 | 853.5 | 830.3 | 815 | 630.5 | 635 | 803.4 | 641 | 764.3 | 636.6 | 782.2 | 746.6 | 330.9 | 352.4 | 367.2 | 340.8 | 294.9 | 344.1 | 337.4 | 324.6
978 | 815 | 468.6 | 187.44 | 219.1066 | 336.7 | 331.8 | 331.8 | 321.1 | 417.5 | 52.2 | 19.4 | 92.8 | 5.3 | 240.6 | 7.1 | 861.4 | 776.6 | 855 | 830.7 | 815.6 | 631.6 | 638.4 | 806.1 | 641.5 | 765.3 | 637 | 779.9 | 746 | 331.2 | 352.7 | 367.3 | 341 | 295.1 | 344.2 | 337.4 | 324.7
979 | 816 | 467.7 | 187.08 | 218.6857 | 336.5 | 332.1 | 331.7 | 321.5 | 419.6 | 52.3 | 19.4 | 92.8 | 5.3 | 249.3 | 6.9 | 864.4 | 776.5 | 856.9 | 830.5 | 815.2 | 632.7 | 642 | 806.5 | 642 | 765.2 | 636.4 | 780.7 | 746.4 | 331.4 | 352.8 | 367.5 | 341.2 | 295.4 | 344.5 | 337.3 | 324.8
980 | 817 | 467.5 | 187 | 218.5922 | 336.2 | 332.6 | 331.2 | 321.7 | 421.2 | 52.4 | 19.4 | 93 | 5 | 255.3 | 6.6 | 867.6 | 777 | 856.3 | 830.6 | 815.6 | 633.8 | 644 | 809.2 | 642.5 | 766.5 | 635.6 | 782 | 747.2 | 331.6 | 352.8 | 367.8 | 341.3 | 295.6 | 344.7 | 337.4 | 324.9
981 | 818 | 467.4 | 186.96 | 218.5455 | 336.2 | 331.8 | 331.4 | 321.6 | 418.4 | 52.4 | 19.4 | 93.1 | 4.7 | 249.2 | 6.6 | 869.8 | 776.2 | 853.6 | 830.5 | 813.5 | 634.9 | 644.7 | 809.8 | 643.1 | 766.2 | 634.7 | 780.5 | 749.8 | 331.9 | 352.8 | 368.1 | 341.3 | 295.8 | 344.6 | 337.4 | 325
982 | 819 | 468.8 | 187.52 | 219.2001 | 337.2 | 331.6 | 331.9 | 322.1 | 413.4 | 52.4 | 19.4 | 93.2 | 5.4 | 260.2 | 6.5 | 871.8 | 774.4 | 848.5 | 829.4 | 811.2 | 635.8 | 641 | 807.4 | 643.6 | 765.4 | 634.4 | 777.7 | 755.6 | 332.1 | 352.8 | 367.8 | 341.4 | 296 | 344.4 | 337.4 | 325.1
983 | 820 | 469.3 | 187.72 | 219.4339 | 340.8 | 331 | 332 | 322.2 | 408 | 52.5 | 19.4 | 93.2 | 5.1 | 273.3 | 6.5 | 870.8 | 773.5 | 845.8 | 829 | 810.8 | 636.8 | 638.2 | 807.1 | 644.1 | 765.2 | 634.9 | 776.6 | 760.5 | 332.3 | 352.7 | 367.6 | 341.3 | 296.2 | 344.2 | 337.4 | 325.2
984 | 821 | 468.6 | 187.44 | 219.1066 | 341.1 | 330.7 | 331.4 | 322.4 | 404.3 | 52.5 | 19.4 | 93.2 | 5.1 | 251.4 | 6.8 | 869.3 | 772.7 | 848.2 | 829.7 | 812.2 | 637.9 | 636.2 | 808.2 | 644.6 | 765.7 | 635.5 | 774.5 | 764.2 | 332.6 | 352.8 | 367.5 | 341.4 | 296.5 | 344 | 337.4 | 325.3
985 | 822 | 468 | 187.2 | 218.826 | 340 | 330.7 | 331.9 | 322.3 | 405.4 | 52.5 | 19.4 | 93.2 | 5.6 | 258.7 | 6.7 | 863.7 | 771.4 | 847 | 830.7 | 810 | 638.9 | 633.4 | 809.3 | 645.1 | 765.3 | 635.7 | 767.8 | 764.8 | 332.8 | 352.9 | 367.6 | 341.6 | 296.7 | 344.2 | 337.6 | 325.4
986 | 823 | 468.1 | 187.24 | 218.8728 | 340.5 | 330.1 | 333 | 322.4 | 411.2 | 52.6 | 19.4 | 93.2 | 5.3 | 264.9 | 6.6 | 860.9 | 771.5 | 845.8 | 831.8 | 810.8 | 640 | 632.8 | 805.5 | 645.5 | 765.3 | 635.3 | 764.2 | 764 | 333.1 | 353 | 367.7 | 341.7 | 296.9 | 344.7 | 337.9 | 325.5
987 | 824 | 469.4 | 187.76 | 219.4806 | 341.4 | 330.1 | 333.6 | 323.2 | 409.2 | 52.6 | 19.4 | 93.2 | 4.8 | 267.1 | 6.6 | 862.8 | 774.2 | 847.6 | 832.4 | 812.7 | 641.3 | 632.9 | 804.5 | 646 | 765.7 | 636.1 | 772.4 | 763.4 | 333.3 | 352.9 | 367.5 | 341.7 | 297.1 | 345 | 338.3 | 325.7
988 | 825 | 469.2 | 187.68 | 219.3871 | 342.3 | 331.3 | 333.7 | 324 | 405.6 | 52.5 | 19.4 | 93.3 | 4.6 | 275 | 6.8 | 867 | 774.5 | 847.4 | 832.5 | 812.9 | 642.4 | 632.4 | 801.6 | 646.6 | 765.2 | 636.5 | 769.3 | 765 | 333.6 | 352.8 | 367.4 | 341.7 | 297.3 | 345.2 | 338.7 | 325.9
989 | 826 | 469.6 | 187.84 | 219.5741 | 342.3 | 332.7 | 333.2 | 324.4 | 400.7 | 52.5 | 19.4 | 93.4 | 4.6 | 289 | 6.5 | 869.9 | 774.2 | 846.8 | 832.4 | 813 | 643.6 | 629.7 | 801.6 | 647.1 | 765.3 | 636.4 | 770.8 | 767.4 | 333.8 | 352.8 | 367.2 | 341.7 | 297.6 | 344.9 | 338.8 | 326
990 | 827 | 469 | 187.6 | 219.2936 | 343.4 | 332.8 | 333.3 | 324.2 | 397.9 | 52.4 | 19.4 | 93.4 | 4.1 | 252.5 | 5.9 | 871.2 | 774.3 | 852.1 | 832.5 | 815.8 | 644.7 | 630 | 803.4 | 647.7 | 766.6 | 636.3 | 774.4 | 768.3 | 334 | 352.5 | 366.9 | 341.7 | 297.8 | 344.6 | 338.7 | 326.1
991 | 828 | 469 | 187.6 | 219.2936 | 343.7 | 332 | 333.8 | 323.4 | 405.6 | 52.4 | 19.4 | 93.4 | 4.8 | 251.4 | 5.8 | 870.2 | 775.8 | 853.9 | 833 | 814.7 | 645.9 | 632.3 | 804.3 | 648.2 | 767 | 635.8 | 773.3 | 767.4 | 334.3 | 352.5 | 366.6 | 341.9 | 298 | 344.3 | 338.6 | 326.2
992 | 829 | 469.1 | 187.64 | 219.3403 | 345.6 | 331.2 | 334.1 | 322.6 | 406.9 | 52.3 | 19.4 | 93.4 | 4.9 | 285.6 | 6.7 | 868.4 | 775.7 | 852 | 833.6 | 814.8 | 647.1 | 635.8 | 803.9 | 648.8 | 765.9 | 635.8 | 768.5 | 767.8 | 334.5 | 352.5 | 366.4 | 342 | 298.2 | 344.4 | 338.5 | 326.2
993 | 830 | 469 | 187.6 | 219.2936 | 347.9 | 330.6 | 334.1 | 322.4 | 401.1 | 52.3 | 19.4 | 93.5 | 4.8 | 253.4 | 6.7 | 873.8 | 775 | 848.5 | 832.9 | 813.9 | 648.2 | 633.2 | 805.9 | 649.4 | 766.1 | 637.2 | 771.7 | 770.9 | 334.7 | 352.3 | 366.4 | 341.9 | 298.4 | 344.6 | 338.6 | 326.4
994 | 831 | 468.5 | 187.4 | 219.0598 | 348.5 | 329.9 | 334 | 323 | 397.2 | 52.3 | 19.4 | 93.5 | 5.1 | 245 | 6.8 | 870.9 | 774.7 | 842.1 | 833.2 | 812.2 | 649.3 | 631.2 | 804.3 | 649.9 | 766.4 | 637.5 | 774 | 771.3 | 334.9 | 352.3 | 366.5 | 341.9 | 298.7 | 344.8 | 338.7 | 326.5
995 | 832 | 468.7 | 187.48 | 219.1533 | 347.5 | 329.9 | 334.2 | 323.5 | 396.3 | 52.2 | 19.4 | 93.5 | 4.7 | 254.3 | 5.8 | 861.8 | 771.3 | 830.4 | 833.2 | 805.3 | 650.4 | 628.9 | 791.9 | 650.3 | 763.3 | 637.3 | 760.2 | 771.8 | 335.2 | 352.4 | 366.7 | 342.2 | 298.9 | 344.8 | 338.7 | 326.5
996 | 833 | 469.4 | 187.76 | 219.4806 | 347 | 330.4 | 334.9 | 323.3 | 395.9 | 52.1 | 19.4 | 93.6 | 4.7 | 245.3 | 5.7 | 855.5 | 768.8 | 829.7 | 833.1 | 801.2 | 651.5 | 626.5 | 784.2 | 650.7 | 761.1 | 637.1 | 748.1 | 772.2 | 335.4 | 352.6 | 367 | 342.5 | 299.1 | 344.7 | 338.7 | 326.6
997 | 834 | 468.6 | 187.44 | 219.1066 | 346.5 | 331 | 335.3 | 323.4 | 395.6 | 52.1 | 19.4 | 93.7 | 4.3 | 239.5 | 6 | 858.9 | 769.8 | 835.6 | 833.7 | 802.7 | 652.7 | 625.8 | 787 | 651.2 | 763.1 | 637 | 753.9 | 770.8 | 335.6 | 352.6 | 367.3 | 342.5 | 299.3 | 344.9 | 338.6 | 326.6
998 | 835 | 468.7 | 187.48 | 219.1533 | 346.9 | 331.1 | 335.9 | 323.7 | 399.5 | 52.2 | 19.4 | 93.7 | 4.9 | 253.8 | 6.2 | 861.2 | 771.8 | 837.8 | 834.7 | 803.9 | 654 | 625.4 | 793 | 651.8 | 764.3 | 637.1 | 761.8 | 769.2 | 335.8 | 353 | 367.5 | 342.7 | 299.5 | 345.2 | 338.6 | 326.8
999 | 836 | 469.1 | 187.64 | 219.3403 | 348.6 | 330.1 | 336.6 | 324.5 | 405.5 | 52.2 | 19.4 | 93.8 | 4.9 | 241.7 | 6.2 | 858.8 | 771.3 | 835 | 835 | 803 | 655.2 | 624.8 | 785.5 | 652.3 | 762.7 | 637.3 | 758.5 | 768.5 | 336.1 | 353.5 | 367.8 | 343.1 | 299.7 | 345.7 | 338.8 | 326.9
1000 | 837 | 468.9 | 187.56 | 219.2468 | 350.5 | 329.1 | 336.8 | 325.5 | 410.8 | 52.3 | 19.4 | 93.9 | 4.9 | 237.8 | 6.5 | 857.7 | 769.8 | 831.7 | 834.3 | 799 | 656.4 | 625.3 | 779.9 | 652.8 | 760.2 | 637.8 | 750.4 | 769.6 | 336.3 | 353.8 | 368.2 | 343.4 | 299.9 | 345.7 | 338.9 | 327
1001 | 838 | 469.2 | 187.68 | 219.3871 | 352.3 | 327 | 337.7 | 326.8 | 410.4 | 52.3 | 19.4 | 93.9 | 4 | 242.8 | 6 | 861 | 768.3 | 830.9 | 833.5 | 799.2 | 657.6 | 623.6 | 773.3 | 653.3 | 758.8 | 639.2 | 746.8 | 770.9 | 336.5 | 353.9 | 368.4 | 343.4 | 300.2 | 346.1 | 339 | 327.1
1002 | 839 | 468 | 187.2 | 218.826 | 352.6 | 326.2 | 338.2 | 327.6 | 405.6 | 52.4 | 19.4 | 94 | 4.2 | 261.5 | 6.2 | 863.7 | 767.5 | 828.8 | 832.6 | 797.5 | 658.9 | 622.2 | 772 | 653.7 | 758 | 640.5 | 751.8 | 773.7 | 336.7 | 353.9 | 368.3 | 343.4 | 300.4 | 346.5 | 339.2 | 327.2
1003 | 840 | 468.3 | 187.32 | 218.9663 | 352 | 325.8 | 338.1 | 328.1 | 402.1 | 52.5 | 19.4 | 94 | 4.3 | 261.7 | 6.7 | 868.5 | 768.4 | 832.7 | 832.7 | 798.7 | 660.3 | 621.4 | 780.6 | 654.3 | 760.8 | 640.6 | 761.6 | 775.5 | 337 | 353.9 | 368.3 | 343.4 | 300.6 | 347 | 339.4 | 327.4
1004 | 841 | 468 | 187.2 | 218.826 | 350.7 | 324.6 | 337.8 | 328.8 | 401.8 | 52.6 | 19.4 | 93.8 | 4.8 | 250.3 | 6.4 | 867.8 | 769.9 | 833.6 | 833.5 | 799.1 | 661.7 | 622 | 789.1 | 654.9 | 762.1 | 639.8 | 764.6 | 775.9 | 337.2 | 354.1 | 368.3 | 343.5 | 300.8 | 347.2 | 339.5 | 327.5
1005 | 842 | 467 | 186.8 | 218.3584 | 351.4 | 324.4 | 337.8 | 329 | 402.1 | 52.7 | 19.4 | 93.8 | 5.2 | 248.2 | 6 | 865.2 | 770.1 | 832.3 | 833.8 | 798.3 | 663 | 623.6 | 792.3 | 655.4 | 762.4 | 638.6 | 762.8 | 774.3 | 337.4 | 354.3 | 368.5 | 343.6 | 301 | 347.3 | 339.6 | 327.6
1006 | 843 | 467.2 | 186.88 | 218.452 | 352.6 | 324.4 | 337.5 | 329.4 | 401.1 | 52.9 | 19.4 | 93.8 | 5.1 | 256.5 | 6 | 861.1 | 769.5 | 831.7 | 834.4 | 796.2 | 664.2 | 625.3 | 797.8 | 655.9 | 762.5 | 638.5 | 757 | 772.2 | 337.7 | 354.6 | 368.8 | 343.8 | 301.3 | 347.4 | 339.7 | 327.7
1007 | 844 | 469 | 187.6 | 219.2936 | 352.5 | 324.1 | 337.7 | 330.1 | 400.1 | 53 | 19.4 | 93.8 | 4.8 | 261.8 | 5.8 | 858.3 | 769.2 | 831 | 835 | 793.2 | 665.3 | 627.4 | 798.8 | 656.3 | 761.6 | 638.6 | 752.7 | 770.8 | 337.9 | 354.8 | 369.3 | 344.1 | 301.5 | 347.9 | 339.9 | 327.8
1008 | 845 | 466.5 | 186.6 | 218.1246 | 351.8 | 324.4 | 338.3 | 330.4 | 401.5 | 53.1 | 19.3 | 93.8 | 4.7 | 256.6 | 5.6 | 859.1 | 770 | 834.5 | 835.5 | 792.5 | 666.6 | 627.5 | 803.3 | 656.8 | 763.2 | 638.3 | 757.5 | 769.4 | 338.2 | 355.1 | 370.2 | 344.3 | 301.7 | 348.8 | 340.3 | 328
1009 | 846 | 466.4 | 186.56 | 218.0779 | 351.3 | 324.3 | 339 | 331.3 | 405.7 | 53.2 | 19.3 | 93.9 | 5 | 251.1 | 5.4 | 859.2 | 771.2 | 835.1 | 836.5 | 793.7 | 667.9 | 626.5 | 808.9 | 657.3 | 764.2 | 637.9 | 761.1 | 766.8 | 338.4 | 355.5 | 370.9 | 344.5 | 301.9 | 349.1 | 340.6 | 328.1
1010 | 847 | 467 | 186.8 | 218.3584 | 351.3 | 324.1 | 339.4 | 332.2 | 415.2 | 53.2 | 19.3 | 93.9 | 5.3 | 262.6 | 5.1 | 864.2 | 774.1 | 842 | 837.1 | 797.3 | 669.3 | 628.8 | 811.7 | 657.8 | 765.9 | 637.5 | 768.4 | 764.1 | 338.7 | 355.9 | 371.4 | 344.7 | 302.2 | 349.2 | 340.8 | 328.3
1011 | 848 | 467.6 | 187.04 | 218.639 | 350.7 | 323.4 | 339.3 | 332.9 | 417.3 | 53.3 | 19.3 | 93.9 | 4.9 | 264.6 | 4.8 | 864.6 | 775.3 | 842.8 | 837.6 | 799.9 | 670.5 | 628.9 | 807.1 | 658.3 | 766 | 637.3 | 772.3 | 763.2 | 338.9 | 356.2 | 371.7 | 344.8 | 302.4 | 349.6 | 341.1 | 328.6
1012 | 849 | 467.5 | 187 | 218.5922 | 349.8 | 323.6 | 339.1 | 333.5 | 413.2 | 53.3 | 19.3 | 93.7 | 4.9 | 255.6 | 4.8 | 865.9 | 776 | 845.7 | 838 | 802.6 | 671.7 | 626.5 | 801.9 | 658.8 | 765.5 | 638.2 | 772.4 | 762.6 | 339.1 | 356.4 | 372.4 | 344.7 | 302.6 | 349.9 | 341.5 | 328.8
1013 | 850 | 467.9 | 187.16 | 218.7793 | 349.2 | 325.1 | 338.7 | 333.6 | 410.1 | 53.3 | 19.3 | 93.8 | 4.6 | 244 | 5.1 | 866.1 | 776.1 | 850.5 | 838.1 | 804 | 672.9 | 626.4 | 796.7 | 659.3 | 765.2 | 639.4 | 770.7 | 760.7 | 339.4 | 356.5 | 372.4 | 344.9 | 302.8 | 350 | 341.6 | 328.9
1014 | 851 | 467.6 | 187.04 | 218.639 | 347.9 | 327 | 338.5 | 333.1 | 409.2 | 53.4 | 19.3 | 93.8 | 5.2 | 244.6 | 5.3 | 866.4 | 775.3 | 848.8 | 838.2 | 803.4 | 674 | 625.6 | 790.7 | 659.8 | 764.7 | 640.7 | 768.5 | 759.4 | 339.7 | 356.7 | 372.4 | 345 | 303.1 | 349.9 | 341.8 | 329
1015 | 852 | 468.2 | 187.28 | 218.9195 | 347.2 | 327.8 | 338.6 | 332 | 406.7 | 53.4 | 19.3 | 93.9 | 5.8 | 251.1 | 5.4 | 868.3 | 774.5 | 845.5 | 837.9 | 801.9 | 675.2 | 621.9 | 794.7 | 660.3 | 765.1 | 641.6 | 766.5 | 761 | 339.9 | 356.7 | 372.3 | 345.1 | 303.3 | 349.6 | 341.9 | 329.1
1016 | 853 | 469.2 | 187.68 | 219.3871 | 346.6 | 328.8 | 338.9 | 330.8 | 408.5 | 53.3 | 19.3 | 94 | 6 | 241.8 | 5.3 | 861.1 | 772.4 | 841 | 837.8 | 798.5 | 676.3 | 620.9 | 790.2 | 660.7 | 763.2 | 641.8 | 758 | 760.2 | 340.2 | 356.9 | 372.5 | 345.3 | 303.5 | 349.5 | 342 | 329.2
1017 | 854 | 467.9 | 187.16 | 218.7793 | 347.4 | 329.6 | 339.5 | 330.2 | 415.8 | 53.3 | 19.3 | 94.1 | 5.5 | 256.6 | 5.3 | 857.6 | 771.3 | 840.6 | 838.1 | 799.5 | 677.6 | 622.3 | 790 | 661.2 | 762.8 | 641.8 | 754.5 | 758.3 | 340.4 | 357.1 | 372.8 | 345.5 | 303.7 | 349.5 | 342 | 329.3
1018 | 855 | 467.4 | 186.96 | 218.5455 | 349.6 | 328.9 | 339.9 | 330.5 | 420.1 | 53.3 | 19.3 | 94.2 | 5.7 | 227.3 | 4.8 | 855.4 | 771.3 | 840.8 | 838.3 | 799.6 | 678.7 | 622.1 | 791.9 | 661.6 | 763.1 | 641.8 | 756.5 | 757.1 | 340.7 | 357.4 | 373.2 | 345.5 | 304 | 349.8 | 342.1 | 329.3
1019 | 856 | 467.5 | 187 | 218.5922 | 349.5 | 329.5 | 340.1 | 330.8 | 423.3 | 53.3 | 19.3 | 94.2 | 5.3 | 238.4 | 4.7 | 858.8 | 771.3 | 836 | 837.7 | 798.2 | 679.9 | 621.2 | 791.4 | 662.1 | 763.7 | 641.2 | 755 | 757.6 | 340.9 | 357.5 | 373.3 | 345.7 | 304.2 | 350 | 342.2 | 329.4
1020 | 857 | 468.2 | 187.28 | 218.9195 | 348.5 | 329.5 | 340.6 | 331.6 | 421 | 53.3 | 19.3 | 94.2 | 5.5 | 257.1 | 4.9 | 849.1 | 766.9 | 823.9 | 836.3 | 792.5 | 681 | 617.9 | 771.4 | 662.4 | 759.2 | 641.4 | 738.5 | 758.3 | 341.2 | 357.7 | 373.7 | 345.8 | 304.4 | 350.4 | 342.3 | 329.5
1021 | 858 | 469 | 187.6 | 219.2936 | 348.6 | 328.8 | 340.9 | 332.7 | 417.8 | 53.4 | 19.3 | 94.1 | 4.7 | 245.6 | 4.9 | 850.9 | 766.8 | 826.8 | 835.5 | 793.8 | 682.2 | 614.1 | 759.2 | 662.8 | 756.9 | 642.2 | 739.9 | 759.3 | 341.4 | 357.6 | 373.9 | 345.9 | 304.6 | 350.7 | 342.3 | 329.7
1022 | 859 | 469.2 | 187.68 | 219.3871 | 349.7 | 328.1 | 340.8 | 333.7 | 417.8 | 53.4 | 19.3 | 94.1 | 4.6 | 229.4 | 5 | 849.2 | 767.4 | 827.7 | 835.8 | 791 | 683.3 | 613.3 | 761.5 | 663.2 | 757.2 | 643.2 | 739.5 | 759.8 | 341.7 | 357.7 | 374.2 | 346 | 304.8 | 350.7 | 342.3 | 329.8
1023 | 860 | 468 | 187.2 | 218.826 | 351.3 | 327.5 | 340.6 | 334.2 | 418.9 | 53.4 | 19.3 | 94 | 4.9 | 221.3 | 5.9 | 846.8 | 766.7 | 824 | 835.9 | 788 | 684.4 | 613.9 | 764.7 | 663.6 | 757.2 | 643.9 | 734.2 | 760.2 | 341.9 | 358 | 374.4 | 346.3 | 305.1 | 351 | 342.3 | 329.8
1024 | 861 | 469.4 | 187.76 | 219.4806 | 352.3 | 326.8 | 340.8 | 334.4 | 416.5 | 53.4 | 19.3 | 94 | 4.6 | 252.2 | 5.6 | 844.1 | 764.3 | 822.6 | 835.9 | 785.2 | 685.7 | 613.2 | 755.4 | 663.9 | 753.8 | 644.2 | 725.3 | 759.9 | 342.2 | 358.2 | 374.7 | 346.5 | 305.3 | 351.2 | 342.5 | 329.9
1025 | 862 | 467.8 | 187.12 | 218.7325 | 352.1 | 327.3 | 341.2 | 335.1 | 415 | 53.2 | 19.3 | 94 | 3.9 | 239.9 | 5.9 | 846.7 | 764.9 | 831.7 | 836.5 | 788.3 | 686.8 | 615.4 | 763.4 | 664.3 | 755.1 | 644.2 | 727.5 | 758.2 | 342.4 | 358.4 | 375.3 | 346.7 | 305.5 | 351.2 | 342.7 | 330.1
1026 | 863 | 468.1 | 187.24 | 218.8728 | 351.7 | 326.8 | 341.5 | 335.7 | 418.1 | 53.1 | 19.3 | 94 | 4.9 | 252 | 6.6 | 844 | 764.3 | 833.6 | 837.1 | 787.4 | 687.8 | 619 | 763 | 664.7 | 754.7 | 644.1 | 727.4 | 755.3 | 342.7 | 358.8 | 375.9 | 346.8 | 305.7 | 351.4 | 342.7 | 330.2
1027 | 864 | 468.3 | 187.32 | 218.9663 | 352.4 | 327.2 | 342 | 336.1 | 417.2 | 53.1 | 19.3 | 94 | 5.6 | 242.3 | 8.5 | 846.3 | 766.2 | 834.2 | 837.4 | 787.3 | 689 | 622.3 | 771.3 | 665.2 | 755.6 | 644.4 | 732.4 | 753 | 342.9 | 358.9 | 376.1 | 346.9 | 306 | 351.5 | 342.8 | 330.3
1028 | 865 | 468.4 | 187.36 | 219.013 | 351.6 | 327.9 | 342.6 | 336.8 | 416.2 | 53 | 19.3 | 94.1 | 6.4 | 245 | 9.6 | 846 | 764.7 | 830.8 | 837.2 | 783.7 | 690 | 621.3 | 766.6 | 665.6 | 753.4 | 645.2 | 725.6 | 753.9 | 343.2 | 359.3 | 376.4 | 347.2 | 306.2 | 351.5 | 342.8 | 330.4
1029 | 866 | 469.4 | 187.76 | 219.4806 | 353.3 | 328.5 | 342.2 | 337.1 | 414.4 | 53 | 19.3 | 94.3 | 7.9 | 247 | 9.3 | 842.6 | 763.5 | 825 | 837.1 | 780.1 | 691.1 | 618.2 | 766.9 | 666 | 751.7 | 646.4 | 722 | 755.4 | 343.5 | 359.7 | 376.6 | 347.5 | 306.4 | 351.7 | 342.8 | 330.5
1030 | 867 | 468.5 | 187.4 | 219.0598 | 355.7 | 327.7 | 341.8 | 337.3 | 411.3 | 53 | 19.3 | 94.4 | 6.9 | 251.9 | 8.7 | 837.2 | 763.6 | 822.2 | 837.4 | 777 | 692.3 | 617.1 | 766.8 | 666.4 | 750.6 | 647.2 | 716.8 | 755.4 | 343.7 | 360 | 376.7 | 347.7 | 306.7 | 352 | 342.9 | 330.6
1031 | 868 | 468.2 | 187.28 | 218.9195 | 357.5 | 327.4 | 342 | 337.3 | 412.9 | 53 | 19.3 | 94.5 | 5.8 | 254.8 | 8.6 | 830 | 761.9 | 818.9 | 837.8 | 774.8 | 693.3 | 618.4 | 765.9 | 666.7 | 749.8 | 647.4 | 709.8 | 752.1 | 344 | 360.4 | 377.1 | 348 | 306.9 | 352.3 | 343.1 | 330.7
1032 | 869 | 469.3 | 187.72 | 219.4339 | 358.2 | 326.1 | 342.5 | 337.2 | 414.1 | 52.9 | 19.3 | 94.6 | 5.6 | 246 | 8.3 | 831.6 | 762 | 817.6 | 837.7 | 772.5 | 694.4 | 623 | 767.6 | 667.1 | 749.2 | 647.6 | 708.2 | 749.7 | 344.3 | 360.5 | 377.6 | 348.1 | 307.1 | 352.7 | 343.2 | 330.8
1033 | 870 | 469.8 | 187.92 | 219.6677 | 358.4 | 324.6 | 343.4 | 337.3 | 418.4 | 53 | 19.3 | 94.6 | 5.5 | 252.9 | 9.2 | 835.5 | 763.8 | 822.8 | 838.1 | 772.3 | 695.5 | 625.2 | 766.5 | 667.5 | 750.2 | 647.3 | 715 | 749.5 | 344.5 | 360.7 | 377.9 | 348.2 | 307.3 | 353.1 | 343.4 | 331
1034 | 871 | 469.8 | 187.92 | 219.6677 | 358.2 | 323.7 | 344.2 | 337.6 | 421.8 | 53.1 | 19.3 | 94.5 | 5.4 | 255.9 | 10 | 838.7 | 764.8 | 825.3 | 838.2 | 772.8 | 696.5 | 623 | 769.6 | 668 | 750.2 | 647.2 | 719.2 | 749.6 | 344.8 | 361.2 | 379.5 | 348.3 | 307.6 | 353.4 | 343.6 | 331.1
1035 | 872 | 466.4 | 186.56 | 218.0779 | 358.3 | 323.1 | 344.9 | 338.6 | 420.1 | 53.2 | 19.3 | 94.4 | 5.1 | 232.2 | 10.6 | 834 | 762.8 | 818.9 | 838 | 769.5 | 697.4 | 618.5 | 764.2 | 668.3 | 747.8 | 647.6 | 707 | 749.1 | 345.1 | 361.9 | 380.6 | 348.7 | 307.8 | 353.6 | 343.7 | 331.3
1036 | 873 | 467.2 | 186.88 | 218.452 | 361 | 322.3 | 345.8 | 339.4 | 418.6 | 53.3 | 19.3 | 94.2 | 5 | 238 | 10.3 | 825.8 | 758.8 | 807.1 | 837.2 | 764.7 | 698.5 | 618.5 | 744.9 | 668.6 | 743.9 | 647.4 | 693.2 | 748.2 | 345.4 | 362.3 | 380.9 | 349 | 308 | 354 | 343.8 | 331.4
1037 | 874 | 467.5 | 187 | 218.5922 | 363.7 | 322.3 | 346.3 | 339.1 | 416.5 | 53.3 | 19.3 | 94.2 | 5.4 | 228.9 | 9.8 | 823.5 | 756.1 | 802.3 | 836.6 | 761.3 | 699.5 | 624.8 | 734.9 | 668.9 | 741.4 | 646.9 | 684.1 | 746.9 | 345.7 | 362.5 | 381 | 349.3 | 308.2 | 354.4 | 343.8 | 331.5
1038 | 875 | 467.7 | 187.08 | 218.6857 | 364.9 | 322.7 | 346.9 | 339.4 | 415.8 | 53.4 | 19.3 | 94.3 | 5.4 | 234.8 | 9.8 | 819.8 | 753.1 | 797.7 | 835.2 | 758.2 | 700.5 | 626.1 | 723.4 | 669.2 | 738.7 | 646.6 | 674.8 | 744.7 | 346 | 363.4 | 381.3 | 349.8 | 308.5 | 354.8 | 344.1 | 331.6
1039 | 876 | 467.8 | 187.12 | 218.7325 | 367 | 322.8 | 347.9 | 339.5 | 419.9 | 53.4 | 19.3 | 94.4 | 5.5 | 244.3 | 8.8 | 813.3 | 749.7 | 789.6 | 833.9 | 754.6 | 701.4 | 627.5 | 712.3 | 669.4 | 736 | 646.5 | 666.1 | 741.2 | 346.3 | 364.4 | 381.6 | 350.3 | 308.7 | 355 | 344.5 | 331.8
1040 | 877 | 467.4 | 186.96 | 218.5455 | 369 | 322.3 | 348.1 | 339.8 | 421 | 53.5 | 19.3 | 94.6 | 5.3 | 245.1 | 8.3 | 813.1 | 747.6 | 792.4 | 833.1 | 754.2 | 702.3 | 627.1 | 705 | 669.7 | 733.7 | 645.7 | 660.8 | 738.7 | 346.6 | 364.5 | 381.6 | 350.4 | 309 | 355.6 | 344.7 | 331.9
1041 | 878 | 467.7 | 187.08 | 218.6857 | 368.6 | 322.9 | 348.2 | 340.4 | 425.2 | 53.5 | 19.3 | 94.8 | 5.4 | 233.5 | 8.3 | 816.5 | 749.5 | 801.7 | 833.2 | 755 | 703.1 | 624.5 | 710.6 | 669.9 | 733.8 | 645.5 | 669.7 | 738.2 | 346.8 | 364.6 | 381.4 | 350.3 | 309.2 | 355.9 | 344.8 | 332.1
1042 | 879 | 467.8 | 187.12 | 218.7325 | 366.7 | 323.6 | 347.9 | 341.1 | 425.8 | 53.5 | 19.3 | 94.9 | 5.1 | 219 | 8 | 828 | 753.5 | 805.2 | 832.9 | 756 | 703.9 | 622.4 | 721.5 | 670.2 | 734.5 | 646.6 | 686.2 | 740.2 | 347.1 | 364.5 | 381.1 | 350.2 | 309.5 | 356 | 345 | 332.2
1043 | 880 | 467.3 | 186.92 | 218.4987 | 364.2 | 324 | 347.7 | 341.3 | 421.6 | 53.6 | 19.3 | 95.1 | 5.2 | 244.5 | 7.4 | 831.3 | 755.9 | 807.8 | 832.3 | 756.5 | 704.6 | 620.7 | 732.5 | 670.6 | 734.9 | 648.2 | 694.6 | 740.5 | 347.4 | 364.5 | 380.8 | 350.2 | 309.7 | 356 | 345.1 | 332.3
1044 | 881 | 468.1 | 187.24 | 218.8728 | 361.6 | 323.4 | 347 | 341.4 | 418.8 | 53.7 | 19.3 | 95.2 | 5.2 | 244.7 | 7 | 837.2 | 758 | 809.7 | 831.9 | 756.2 | 705.3 | 617.1 | 736.3 | 670.8 | 734 | 649.2 | 698.6 | 741.9 | 347.7 | 364.2 | 380.3 | 350.2 | 310 | 356 | 345.2 | 332.4
1045 | 882 | 467.9 | 187.16 | 218.7793 | 359.8 | 324.5 | 347 | 341.5 | 416.8 | 53.7 | 19.3 | 95.2 | 5.6 | 243.3 | 6.9 | 839 | 758.5 | 815.2 | 831.9 | 756.7 | 705.9 | 613.1 | 734.2 | 671.1 | 733.8 | 649.8 | 698.5 | 743.7 | 348 | 363.9 | 379.9 | 350.2 | 310.2 | 355.8 | 345.1 | 332.5
1046 | 883 | 467.6 | 187.04 | 218.639 | 358.9 | 325.4 | 346.3 | 341.6 | 415.1 | 53.7 | 19.3 | 95.1 | 5.7 | 238.1 | 7.7 | 840.9 | 760.7 | 820.8 | 832.4 | 759.3 | 706.6 | 612 | 741.3 | 671.4 | 734.4 | 651 | 710.1 | 745.1 | 348.3 | 363.8 | 379.7 | 350.1 | 310.4 | 355.8 | 345.2 | 332.7
1047 | 884 | 469 | 187.6 | 219.2936 | 357.5 | 325.5 | 345.7 | 341.4 | 414.3 | 53.7 | 19.3 | 95 | 5.7 | 231.3 | 7.5 | 837.9 | 763.6 | 819.8 | 833.3 | 760 | 707.3 | 610.5 | 751.5 | 671.8 | 736.4 | 652.1 | 720.5 | 746.1 | 348.6 | 363.7 | 379.8 | 350.2 | 310.7 | 355.7 | 345.3 | 332.8
1048 | 885 | 468.3 | 187.32 | 218.9663 | 356.3 | 325.9 | 345.3 | 341.3 | 415.1 | 53.8 | 19.3 | 95 | 5.4 | 235.2 | 7.7 | 835.9 | 763.3 | 818.5 | 833.7 | 758.4 | 707.8 | 607.3 | 753.1 | 672.1 | 735.8 | 653.2 | 714.2 | 748.1 | 348.9 | 363.7 | 379.9 | 350.4 | 310.9 | 355.5 | 345.2 | 332.8
1049 | 886 | 467.9 | 187.16 | 218.7793 | 357 | 325.6 | 345.3 | 340.7 | 409.8 | 53.8 | 19.3 | 95 | 5.1 | 220.3 | 7.2 | 833.3 | 761 | 809.9 | 833.2 | 756.3 | 708.4 | 604.5 | 739.1 | 672.3 | 732.5 | 654.3 | 703.8 | 752 | 349.2 | 363.4 | 379.8 | 350.4 | 311.2 | 355.2 | 345.1 | 332.9
1050 | 887 | 468.3 | 187.32 | 218.9663 | 356.8 | 325.7 | 345.2 | 340.4 | 406.1 | 53.8 | 19.3 | 95.1 | 5.2 | 242.7 | 7 | 837.2 | 762.1 | 814.4 | 832.7 | 757.2 | 709 | 602.5 | 736.5 | 672.7 | 731.5 | 656.1 | 707.7 | 755.4 | 349.4 | 363 | 379.6 | 350.3 | 311.4 | 354.9 | 344.9 | 333
1051 | 888 | 468.8 | 187.52 | 219.2001 | 356.3 | 326 | 345 | 339.1 | 405.3 | 53.8 | 19.3 | 95.1 | 5.1 | 245.1 | 7.6 | 844 | 763.4 | 817.8 | 832.3 | 758.5 | 709.5 | 600.2 | 743.8 | 673 | 733.2 | 656.9 | 716.8 | 756.7 | 349.7 | 362.6 | 379.1 | 350.1 | 311.6 | 354.5 | 344.7 | 333
1052 | 889 | 468.5 | 187.4 | 219.0598 | 358.6 | 325.8 | 344.4 | 336.7 | 404.9 | 53.8 | 19.3 | 95.3 | 4.5 | 238.6 | 8.8 | 853.9 | 765.7 | 823.5 | 831.6 | 763 | 710.1 | 599.9 | 750.6 | 673.4 | 735 | 657.8 | 730.5 | 758 | 350 | 362 | 378.3 | 350 | 311.8 | 354.4 | 344.7 | 333.1
1053 | 890 | 468.5 | 187.4 | 219.0598 | 360.6 | 325.8 | 343.4 | 335.1 | 404.2 | 53.8 | 19.3 | 95.4 | 5.1 | 237.1 | 8.6 | 858.8 | 766.2 | 824.6 | 831.1 | 765.9 | 710.5 | 600.1 | 750.5 | 673.8 | 735.7 | 658.8 | 735.7 | 759.2 | 350.2 | 361.5 | 377.7 | 349.9 | 312.1 | 354.3 | 344.9 | 333.2
1054 | 891 | 466.2 | 186.48 | 217.9844 | 360.8 | 324.7 | 342.2 | 334.6 | 401.6 | 53.8 | 19.3 | 95.4 | 5.6 | 249.2 | 7.8 | 861.1 | 767.3 | 822.9 | 830.6 | 766.7 | 710.9 | 598.3 | 748.5 | 674.1 | 734.5 | 660.2 | 736.5 | 761.2 | 350.5 | 361 | 377.1 | 349.7 | 312.3 | 354.3 | 344.8 | 333.3
1055 | 892 | 467.2 | 186.88 | 218.452 | 360.4 | 324.2 | 341.6 | 335 | 399.3 | 53.9 | 19.3 | 95.5 | 5.6 | 242.8 | 7.6 | 861.7 | 767.6 | 822.7 | 830.3 | 768 | 711.5 | 594.9 | 739.9 | 674.5 | 731.8 | 663.5 | 731.6 | 763.2 | 350.7 | 360.3 | 376.5 | 349.5 | 312.5 | 353.9 | 344.7 | 333.4
1056 | 893 | 467.6 | 187.04 | 218.639 | 359.5 | 323.1 | 341.1 | 334.2 | 398.1 | 53.9 | 19.3 | 95.6 | 5.1 | 247.3 | 7.3 | 865 | 768.9 | 827.2 | 829.7 | 770.8 | 712 | 593.3 | 742.8 | 674.9 | 732.2 | 666.3 | 735.8 | 763.1 | 351 | 359.5 | 375.8 | 349.4 | 312.7 | 353.6 | 344.6 | 333.5
1057 | 894 | 466.9 | 186.76 | 218.3117 | 360.2 | 321.9 | 340.5 | 333.1 | 396.7 | 54 | 19.3 | 95.6 | 4.5 | 240 | 7.1 | 862.8 | 768.4 | 827.9 | 829.9 | 771.3 | 712.4 | 591.5 | 742.4 | 675.3 | 731.7 | 667.6 | 734.7 | 763 | 351.2 | 358.9 | 375.1 | 349.4 | 312.9 | 353.3 | 344.3 | 333.5
1058 | 895 | 466.9 | 186.76 | 218.3117 | 360.3 | 321.2 | 339.8 | 332.6 | 394.9 | 54 | 19.3 | 95.5 | 5.1 | 236.5 | 6.5 | 856.5 | 766.8 | 829.4 | 830.2 | 772.1 | 712.9 | 589.9 | 740.6 | 675.7 | 730.6 | 669.2 | 728.8 | 761.6 | 351.4 | 358.5 | 374.5 | 349.5 | 313.1 | 353 | 344.2 | 333.5
1059 | 896 | 467.6 | 187.04 | 218.639 | 360.4 | 320.8 | 339.4 | 332.3 | 393.3 | 53.9 | 19.3 | 95.6 | 5.2 | 231.3 | 6.2 | 850.1 | 763.7 | 825.2 | 830.1 | 769.6 | 713.5 | 586.5 | 732.7 | 676 | 727.3 | 672.1 | 716 | 759.3 | 351.6 | 358.2 | 374.1 | 349.6 | 313.4 | 352.6 | 344.2 | 333.6
1060 | 897 | 466.6 | 186.64 | 218.1714 | 359.8 | 320.5 | 339.1 | 331.7 | 391.2 | 53.9 | 19.3 | 95.7 | 4.8 | 247 | 6.6 | 845.5 | 762.5 | 820.5 | 829.9 | 767.1 | 714.1 | 582.2 | 724.8 | 676.4 | 725.8 | 673.8 | 710.2 | 759.7 | 351.8 | 358 | 373.8 | 349.8 | 313.6 | 352.3 | 343.9 | 333.6
1061 | 898 | 467.1 | 186.84 | 218.4052 | 358.3 | 320.5 | 339.2 | 331.1 | 391.2 | 53.9 | 19.3 | 95.8 | 5.4 | 247.3 | 6.7 | 847.3 | 763.7 | 822 | 829.6 | 768.7 | 714.7 | 578.9 | 724.2 | 676.7 | 724.9 | 674.1 | 711.2 | 761.1 | 352 | 357.6 | 373.5 | 349.8 | 313.8 | 351.8 | 343.6 | 333.6
1062 | 899 | 468.7 | 187.48 | 219.1533 | 356.4 | 319.8 | 339 | 330.8 | 391.7 | 54 | 19.3 | 95.9 | 4.6 | 266.2 | 6.2 | 849.5 | 764.5 | 821.6 | 829.3 | 769.4 | 715.1 | 577.2 | 727.6 | 677.1 | 725.1 | 673.9 | 718.8 | 762.1 | 352.2 | 357.2 | 372.9 | 349.8 | 314 | 351.4 | 343.3 | 333.6
1063 | 900 | 469.5 | 187.8 | 219.5274 | 354.9 | 319.2 | 338.9 | 329.9 | 390.4 | 54 | 19.3 | 96.1 | 4.6 | 257.1 | 5.4 | 847.7 | 763.2 | 818.9 | 828.8 | 768.4 | 715.5 | 575.8 | 722.8 | 677.5 | 723.4 | 673.8 | 720.6 | 763 | 352.4 | 356.7 | 372.3 | 349.6 | 314.2 | 351 | 343.1 | 333.6
1064 | 901 | 467.9 | 187.16 | 218.7793 | 354 | 318.6 | 338.3 | 329.3 | 388.4 | 54 | 19.2 | 96.3 | 4.9 | 259.2 | 5.4 | 849.3 | 764.3 | 819.3 | 828.9 | 769.4 | 715.9 | 573 | 722.1 | 677.8 | 723.2 | 674.5 | 723.5 | 762.5 | 352.6 | 356.5 | 371.9 | 349.4 | 314.4 | 351.2 | 342.9 | 333.7
1065 | 902 | 468 | 187.2 | 218.826 | 352.9 | 318 | 337.3 | 329.7 | 386 | 54 | 19.3 | 96.4 | 5.2 | 252.1 | 5.7 | 843.3 | 762.9 | 815.6 | 829.2 | 765.6 | 716.2 | 570.5 | 724.3 | 678.2 | 722.7 | 674.6 | 714.4 | 762.5 | 352.8 | 356.2 | 371.7 | 349.4 | 314.6 | 351.2 | 342.9 | 333.8
1066 | 903 | 468 | 187.2 | 218.826 | 353 | 317 | 336.5 | 330.6 | 384.7 | 54.1 | 19.3 | 96.4 | 5.5 | 238.5 | 5.6 | 845 | 760.4 | 817.2 | 828.8 | 766.1 | 716.6 | 568.1 | 710.8 | 678.6 | 719.3 | 675.8 | 707.8 | 762.5 | 352.9 | 355.8 | 371.3 | 349.5 | 314.7 | 350.9 | 342.7 | 333.8
1067 | 904 | 467.4 | 186.96 | 218.5455 | 352.7 | 316.4 | 336.4 | 330.1 | 384 | 54 | 19.2 | 96.3 | 6.1 | 244.1 | 5.2 | 845.8 | 760 | 818.5 | 828.1 | 767.1 | 717.1 | 567.8 | 707.6 | 679 | 717.7 | 677.4 | 705.2 | 762.2 | 353.1 | 355.3 | 370.7 | 349.3 | 314.9 | 350.6 | 342.6 | 333.8
1068 | 905 | 467.1 | 186.84 | 218.4052 | 351.9 | 316.8 | 336.1 | 329.2 | 383.3 | 53.9 | 19.2 | 96.3 | 5.6 | 242.9 | 4.7 | 849.4 | 762.1 | 821.4 | 828 | 767.9 | 717.4 | 566 | 717.6 | 679.4 | 719.1 | 677 | 710.6 | 761.5 | 353.3 | 354.9 | 370.1 | 349.3 | 315.1 | 350.4 | 342.4 | 333.7
1069 | 906 | 466.6 | 186.64 | 218.1714 | 352.1 | 316.9 | 335.5 | 328.1 | 385.3 | 53.9 | 19.2 | 96.3 | 5.5 | 236.8 | 4.6 | 842.2 | 759.6 | 814.1 | 828.1 | 763.6 | 717.7 | 567.9 | 710.8 | 679.7 | 716.4 | 675.8 | 697.7 | 759.1 | 353.4 | 354.8 | 369.9 | 349.6 | 315.3 | 350.2 | 342 | 333.7
1070 | 907 | 466.1 | 186.44 | 217.9376 | 353 | 316.3 | 335.3 | 327.6 | 385.7 | 53.9 | 19.2 | 96.4 | 5.1 | 235.5 | 4 | 838.9 | 759.3 | 809.4 | 828.2 | 761.6 | 718 | 573.8 | 710.8 | 679.9 | 715 | 675 | 694 | 756.1 | 353.6 | 354.8 | 370 | 349.7 | 315.5 | 350 | 341.7 | 333.7
1071 | 908 | 466.9 | 186.76 | 218.3117 | 354 | 315.6 | 335.6 | 327.9 | 386.8 | 54 | 19.2 | 96.3 | 6.1 | 255.3 | 3.5 | 837.3 | 760.5 | 809.5 | 828.7 | 760.1 | 718.3 | 576.9 | 715.4 | 680.3 | 715 | 674.8 | 697.5 | 754.8 | 353.7 | 354.7 | 370.3 | 349.9 | 315.6 | 349.9 | 341.4 | 333.6
1072 | 909 | 467.4 | 186.96 | 218.5455 | 353.4 | 314.9 | 336.1 | 328.3 | 387.5 | 54.1 | 19.3 | 96.3 | 5.8 | 277.3 | 3.4 | 841.4 | 762.6 | 813.2 | 828.8 | 760.4 | 718.6 | 574.5 | 715.9 | 680.6 | 714.2 | 674.5 | 700.4 | 753.7 | 353.9 | 354.6 | 370.2 | 349.9 | 315.8 | 350 | 341.2 | 333.6
1073 | 910 | 467.4 | 186.96 | 218.5455 | 352.8 | 314.8 | 336.7 | 328.2 | 387.5 | 54.1 | 19.3 | 96.3 | 5.6 | 261.8 | 4.2 | 840.1 | 763.6 | 809.1 | 828.8 | 758.4 | 718.8 | 571.8 | 722.2 | 680.9 | 714 | 674 | 699.5 | 754.1 | 354 | 354.6 | 370.4 | 349.9 | 316 | 349.9 | 341 | 333.6
1074 | 911 | 466.8 | 186.72 | 218.2649 | 354.2 | 315 | 337.1 | 328.3 | 389.6 | 54.1 | 19.2 | 96.2 | 4.6 | 258.4 | 5.8 | 828.7 | 759.5 | 797.5 | 828.1 | 753.9 | 718.9 | 575 | 720.4 | 681.2 | 713.1 | 673.2 | 689.4 | 752.1 | 354.2 | 354.7 | 370.5 | 350 | 316.2 | 349.7 | 341 | 333.6
1075 | 912 | 466.7 | 186.68 | 218.2182 | 357 | 315 | 337 | 327.8 | 390.2 | 54.1 | 19.2 | 96.2 | 4.2 | 242.2 | 6.5 | 817.7 | 753.9 | 787 | 827.2 | 749.3 | 719.4 | 574.9 | 704.6 | 681.4 | 709.2 | 673.9 | 675.5 | 750.7 | 354.4 | 354.9 | 371 | 350.3 | 316.4 | 350 | 340.8 | 333.6
1076 | 913 | 466.9 | 186.76 | 218.3117 | 359.5 | 315.5 | 337.2 | 328 | 390 | 54 | 19.2 | 96.1 | 4.4 | 242.3 | 7.4 | 810.5 | 751.9 | 784 | 827.2 | 745.5 | 719.8 | 583.4 | 703 | 681.8 | 708.4 | 674.5 | 673.9 | 747.8 | 354.5 | 355.3 | 371.4 | 350.5 | 316.5 | 350.3 | 340.9 | 333.7
1077 | 914 | 466.4 | 186.56 | 218.0779 | 362.4 | 316 | 338.4 | 329.1 | 395.5 | 54 | 19.2 | 96.1 | 4.2 | 251.3 | 8.2 | 807.7 | 751.6 | 783.5 | 828.1 | 742.2 | 719.9 | 588.2 | 713.8 | 682.1 | 710 | 673.2 | 675.4 | 744.7 | 354.7 | 355.6 | 372.2 | 350.7 | 316.7 | 350.4 | 340.8 | 333.7
1078 | 915 | 467 | 186.8 | 218.3584 | 363 | 316.3 | 338.9 | 329.7 | 398.7 | 54 | 19.2 | 96.1 | 4 | 244.6 | 8.3 | 808 | 753.6 | 783.3 | 828.7 | 739.7 | 720.1 | 587.3 | 716.8 | 682.3 | 710 | 671.6 | 675.7 | 744.1 | 354.8 | 356.3 | 373.1 | 350.9 | 316.9 | 350.6 | 340.8 | 333.7
1079 | 916 | 466.9 | 186.76 | 218.3117 | 363.5 | 316.6 | 339.4 | 330.4 | 399.3 | 54 | 19.2 | 96.1 | 3.8 | 241.3 | 8.4 | 815.1 | 755.8 | 787.6 | 828.6 | 738.6 | 720.2 | 587.9 | 723.3 | 682.6 | 709.6 | 670.9 | 676.4 | 744.9 | 355 | 356.7 | 373.9 | 351.1 | 317.1 | 351 | 340.9 | 333.8
1080 | 917 | 467.5 | 187 | 218.5922 | 362.4 | 316.5 | 339.9 | 331.4 | 399.8 | 54 | 19.2 | 96.1 | 4.7 | 230.3 | 7.8 | 825.1 | 761.3 | 800.9 | 828.4 | 744 | 720.5 | 589 | 737.1 | 683 | 712.9 | 670.3 | 697.4 | 745.9 | 355.2 | 356.9 | 374.5 | 351.1 | 317.2 | 351.6 | 341.2 | 333.9
1081 | 918 | 468.7 | 187.48 | 219.1533 | 361 | 317.4 | 340.5 | 333.2 | 404.5 | 54 | 19.2 | 96.1 | 4.5 | 230.1 | 7.1 | 829.9 | 767.5 | 811.3 | 828.4 | 747.3 | 720.4 | 589.7 | 748.4 | 683.3 | 716.1 | 667.8 | 714.3 | 745 | 355.4 | 357.3 | 375 | 350.9 | 317.4 | 351.8 | 341.7 | 334.1
1082 | 919 | 468.6 | 187.44 | 219.1066 | 359.9 | 318.5 | 340.5 | 334.1 | 404.7 | 54 | 19.2 | 96.1 | 4.5 | 227.7 | 6.4 | 837.6 | 772.4 | 819.6 | 828 | 752.9 | 720.3 | 591.5 | 755.8 | 683.8 | 718.1 | 666.6 | 725.7 | 743.8 | 355.6 | 357.4 | 375.2 | 350.8 | 317.6 | 352.2 | 342.2 | 334.3
1083 | 920 | 469 | 187.6 | 219.2936 | 359.4 | 319.3 | 340.1 | 334.4 | 401.7 | 54 | 19.2 | 96.1 | 4.7 | 223.8 | 5.5 | 842.2 | 776.7 | 825.3 | 827.6 | 757.6 | 720.4 | 596.1 | 764.1 | 684.2 | 721.2 | 665.7 | 733.6 | 741.8 | 355.8 | 357.5 | 375.4 | 350.7 | 317.8 | 352.5 | 342.7 | 334.4
1084 | 921 | 469.3 | 187.72 | 219.4339 | 360.6 | 319.5 | 339.6 | 334.5 | 404.5 | 54 | 19.2 | 96.2 | 5.4 | 228.1 | 4.9 | 845.6 | 780.5 | 828.9 | 828.2 | 760.4 | 720.3 | 598.9 | 773.5 | 684.5 | 724.4 | 664 | 741.9 | 738.6 | 356 | 357.5 | 375.2 | 350.8 | 318 | 352.6 | 343 | 334.6
1085 | 922 | 466.8 | 186.72 | 218.2649 | 360.3 | 319.8 | 339.6 | 334.3 | 417.6 | 54 | 19.2 | 96.1 | 5.5 | 226.1 | 4.5 | 838.5 | 778.3 | 824.2 | 829.1 | 760.3 | 720.1 | 599.4 | 774.1 | 684.8 | 724.5 | 662.5 | 736.5 | 735 | 356.2 | 357.6 | 375.2 | 351.1 | 318.2 | 352.1 | 342.9 | 334.6
1086 | 923 | 466.2 | 186.48 | 217.9844 | 359.9 | 321.6 | 339.7 | 334.1 | 420.1 | 54 | 19.2 | 96 | 5.1 | 228.5 | 4 | 836.5 | 779.6 | 825 | 829.9 | 761.5 | 720.2 | 598.1 | 767.2 | 685 | 723.4 | 662.4 | 732.2 | 732.2 | 356.4 | 357.5 | 375.1 | 351.1 | 318.3 | 352 | 342.9 | 334.6
1087 | 924 | 467.1 | 186.84 | 218.4052 | 358.7 | 323.9 | 340 | 334 | 423 | 54.1 | 19.2 | 96 | 5.1 | 240.6 | 3.9 | 834.9 | 780.7 | 827.2 | 830.4 | 763.9 | 720.5 | 599.2 | 759.2 | 685.2 | 723.5 | 662.8 | 734.9 | 730.7 | 356.6 | 357.3 | 374.8 | 351.1 | 318.5 | 351.9 | 342.9 | 334.6
1088 | 925 | 466.6 | 186.64 | 218.1714 | 357.2 | 325.4 | 339.6 | 333.4 | 429.7 | 54 | 19.2 | 96 | 5.2 | 241.8 | 4 | 835.3 | 783.5 | 829.8 | 830.9 | 765.5 | 720.7 | 600.1 | 765.4 | 685.5 | 726.3 | 663 | 742.5 | 728.7 | 356.8 | 357.1 | 374.4 | 351.1 | 318.7 | 351.6 | 342.8 | 334.7
1089 | 926 | 468.2 | 187.28 | 218.9195 | 355.9 | 327 | 338.9 | 332.8 | 430.1 | 53.9 | 19.2 | 96 | 5.5 | 235.4 | 3.9 | 838.9 | 786.3 | 828.9 | 831.6 | 765.1 | 720.5 | 603.3 | 776.7 | 685.9 | 728.5 | 662.3 | 745 | 728.9 | 357 | 357.2 | 374.4 | 351.2 | 318.9 | 351.5 | 342.7 | 334.7
1090 | 927 | 469.4 | 187.76 | 219.4806 | 354.6 | 328.3 | 338.2 | 332 | 427.4 | 53.8 | 19.2 | 96.1 | 5.6 | 227.6 | 3.9 | 844 | 787.3 | 829.1 | 832.1 | 763.7 | 720.4 | 603.1 | 780.4 | 686.2 | 729.4 | 661.7 | 743 | 731.4 | 357.2 | 357.4 | 374.7 | 351.3 | 319.1 | 351.6 | 342.6 | 334.7
1091 | 928 | 468.4 | 187.36 | 219.013 | 353.8 | 328.9 | 338.5 | 331.2 | 422.1 | 53.8 | 19.2 | 96.2 | 5.8 | 192.2 | 3.9 | 850 | 787.6 | 830.4 | 831.9 | 764.8 | 720.3 | 601.7 | 785 | 686.5 | 729.6 | 661.9 | 745.5 | 737.2 | 357.4 | 357.3 | 374.5 | 351.2 | 319.3 | 351.2 | 342.4 | 334.7
1092 | 929 | 467.9 | 187.16 | 218.7793 | 353.7 | 328.9 | 339 | 330.5 | 416.3 | 53.8 | 19.2 | 96.2 | 5.5 | 182.3 | 3.8 | 854 | 788.5 | 834.8 | 831.7 | 768.9 | 720.2 | 600.3 | 789.9 | 686.9 | 731.1 | 662.1 | 751.9 | 740.7 | 357.6 | 357 | 374.1 | 351.1 | 319.5 | 350.9 | 342.3 | 334.8
1093 | 930 | 466.9 | 186.76 | 218.3117 | 354.4 | 329.9 | 338.9 | 330.1 | 410.3 | 53.8 | 19.2 | 96.1 | 5.4 | 193.6 | 3.5 | 856 | 791.5 | 837 | 832.2 | 770.5 | 720.2 | 603 | 792.2 | 687.3 | 731.8 | 662.8 | 756.3 | 742.6 | 357.8 | 356.8 | 373.5 | 350.9 | 319.7 | 350.7 | 342.2 | 334.9
1094 | 931 | 467.4 | 186.96 | 218.5455 | 354.6 | 330.9 | 338.5 | 330.1 | 402.4 | 53.8 | 19.2 | 95.9 | 4.9 | 214.9 | 3.4 | 859.3 | 794.4 | 837.1 | 832.9 | 773 | 720.3 | 608.6 | 791.2 | 687.9 | 733.4 | 663.7 | 759.9 | 745.1 | 358 | 356.4 | 373 | 350.8 | 319.8 | 350.7 | 342.4 | 335
1095 | 932 | 467.4 | 186.96 | 218.5455 | 354.3 | 331.9 | 338.1 | 329.9 | 395.9 | 53.8 | 19.2 | 95.8 | 4.4 | 212 | 4 | 861.1 | 795.1 | 838.6 | 832.8 | 776.5 | 720.4 | 611.1 | 792.6 | 688.4 | 734.4 | 664.5 | 759.7 | 747.7 | 358.2 | 356 | 372.5 | 350.6 | 320 | 350.7 | 342.5 | 335.1
1096 | 933 | 468 | 187.2 | 218.826 | 353.4 | 333.6 | 337.9 | 329.9 | 393 | 53.9 | 19.2 | 95.7 | 4.4 | 200.8 | 4.1 | 863.6 | 795.9 | 842.9 | 832.2 | 779.3 | 720.4 | 613 | 791.9 | 688.7 | 735.7 | 664.2 | 761.1 | 749 | 358.4 | 355.6 | 372.1 | 350.5 | 320.2 | 350.7 | 342.4 | 335.2
1097 | 934 | 467.2 | 186.88 | 218.452 | 351.8 | 334.2 | 337.5 | 329.5 | 392 | 53.9 | 19.2 | 95.7 | 4.5 | 210.5 | 3.8 | 864.5 | 799.3 | 844.9 | 832 | 782.9 | 720.5 | 614.5 | 795 | 689.1 | 737.3 | 663.7 | 764.5 | 749.2 | 358.6 | 355.2 | 371.6 | 350.4 | 320.3 | 350.6 | 342.3 | 335.2
1098 | 935 | 467.4 | 186.96 | 218.5455 | 350.6 | 334.7 | 337.2 | 329.5 | 391 | 53.9 | 19.2 | 95.7 | 4.8 | 236.6 | 3.4 | 866.2 | 802.3 | 843.9 | 832.6 | 784.1 | 720.5 | 614.6 | 797.4 | 689.4 | 738.7 | 662.8 | 763.9 | 749.2 | 358.7 | 354.9 | 371.1 | 350.4 | 320.5 | 350.5 | 342.4 | 335.3
1099 | 936 | 467.7 | 187.08 | 218.6857 | 349.6 | 335.1 | 337.1 | 329.3 | 392 | 53.9 | 19.2 | 95.8 | 4.9 | 267.6 | 3.2 | 864.5 | 803.5 | 842.6 | 834.3 | 785.3 | 720.5 | 615.3 | 799.3 | 689.8 | 740 | 662.1 | 760.6 | 747.2 | 358.9 | 354.9 | 370.8 | 350.6 | 320.7 | 350.3 | 342.3 | 335.3
1100 | 937 | 467.6 | 187.04 | 218.639 | 349.2 | 336.1 | 336.8 | 328.7 | 396.7 | 53.9 | 19.2 | 95.8 | 4.7 | 275.5 | 2.9 | 858.6 | 802.7 | 837.5 | 835.3 | 784.7 | 720.5 | 618.7 | 800.4 | 690 | 741.3 | 661.3 | 759.1 | 744.6 | 359.1 | 355 | 370.8 | 350.8 | 320.8 | 350.2 | 342.1 | 335.3
1101 | 938 | 467.3 | 186.92 | 218.4987 | 349.2 | 336.9 | 337 | 328.2 | 402.2 | 53.8 | 19.2 | 95.8 | 4.8 | 259.2 | 2.7 | 853.7 | 801.6 | 828 | 836.2 | 780.5 | 720.7 | 618.1 | 799.4 | 690.3 | 741 | 661.7 | 757.3 | 745.6 | 359.2 | 355.1 | 370.7 | 350.9 | 321 | 350.2 | 342 | 335.3
1102 | 939 | 468.6 | 187.44 | 219.1066 | 350.6 | 338.1 | 337.5 | 328.4 | 401.6 | 53.7 | 19.2 | 95.8 | 4.9 | 244.6 | 3.1 | 851.6 | 800.6 | 828.1 | 836.9 | 778.7 | 720.9 | 613.7 | 800.5 | 690.6 | 741.2 | 661.9 | 757.2 | 748.8 | 359.4 | 355.1 | 370.6 | 350.9 | 321.2 | 350.6 | 342.2 | 335.4
1103 | 940 | 468.7 | 187.48 | 219.1533 | 350.8 | 338.1 | 337.8 | 328.7 | 399.7 | 53.7 | 19.2 | 95.8 | 4.7 | 238.9 | 3.1 | 858.6 | 800.9 | 827.4 | 836.8 | 781 | 721 | 613.7 | 804.9 | 691.1 | 743.6 | 661.4 | 763.7 | 751.9 | 359.5 | 355 | 370.5 | 350.8 | 321.3 | 350.9 | 342.4 | 335.4
1104 | 941 | 468.8 | 187.52 | 219.2001 | 350.5 | 338.4 | 337.5 | 329.5 | 401.3 | 53.8 | 19.2 | 95.8 | 4.4 | 237.7 | 2.9 | 862.4 | 802 | 832.8 | 836.4 | 783.4 | 721.1 | 615.7 | 807 | 691.5 | 745.1 | 661 | 766.9 | 753.1 | 359.7 | 355.2 | 370.6 | 350.9 | 321.5 | 351.1 | 342.5 | 335.5
1105 | 942 | 469.5 | 187.8 | 219.5274 | 351.3 | 338.7 | 336.8 | 329.6 | 404.3 | 53.9 | 19.2 | 95.8 | 4.4 | 243.6 | 2.8 | 865.4 | 804.2 | 836.2 | 836.8 | 785.9 | 721.1 | 618.2 | 807.3 | 691.9 | 745.8 | 660.7 | 767.8 | 754.3 | 359.8 | 355.3 | 370.6 | 351 | 321.7 | 351.3 | 342.6 | 335.5
1106 | 943 | 467.7 | 187.08 | 218.6857 | 351.9 | 339.4 | 336.9 | 329 | 405.7 | 54 | 19.2 | 95.8 | 4.7 | 249.6 | 2.6 | 863.1 | 805.8 | 835.1 | 837.6 | 785.9 | 721.2 | 617 | 802.2 | 692.2 | 744.8 | 660.4 | 760 | 753.1 | 360 | 355.7 | 370.6 | 351.2 | 321.8 | 351.3 | 342.5 | 335.6
1107 | 944 | 466.9 | 186.76 | 218.3117 | 351.6 | 340 | 337.2 | 328.7 | 405.7 | 54.1 | 19.2 | 95.9 | 4.9 | 237.8 | 2.8 | 859.8 | 804.3 | 833.3 | 837.8 | 785.1 | 721.4 | 615.5 | 800.9 | 692.5 | 745.4 | 661 | 757.6 | 751 | 360.1 | 355.9 | 370.6 | 351.3 | 322 | 351.4 | 342.5 | 335.6
1108 | 945 | 467.1 | 186.84 | 218.4052 | 351.6 | 340.6 | 337.6 | 328.5 | 405.6 | 54.2 | 19.2 | 95.9 | 5.5 | 250.5 | 3.3 | 847.6 | 798.9 | 823.9 | 838.4 | 781.5 | 721.6 | 613.6 | 791.9 | 692.8 | 744.1 | 661.2 | 747.3 | 747.8 | 360.3 | 356.3 | 371 | 351.6 | 322.2 | 351.2 | 342.4 | 335.6
1109 | 946 | 468.9 | 187.56 | 219.2468 | 352.4 | 342 | 338.4 | 328.3 | 407.3 | 54.2 | 19.2 | 95.9 | 5.3 | 254 | 5 | 836.9 | 792.9 | 815.4 | 838.5 | 775.6 | 722.2 | 611.5 | 780.6 | 693 | 741.6 | 662.6 | 731.3 | 744.8 | 360.4 | 356.9 | 371.9 | 352.2 | 322.3 | 351.4 | 342.4 | 335.6
1110 | 947 | 470.1 | 188.04 | 219.8079 | 353.8 | 343.8 | 339 | 328.9 | 409.9 | 54.4 | 19.2 | 95.9 | 5.7 | 248.9 | 6.2 | 836.2 | 792.2 | 814.4 | 838.7 | 772.7 | 722.5 | 611.2 | 788.8 | 693.4 | 741.9 | 665.7 | 724.6 | 741.7 | 360.6 | 357.5 | 372.9 | 352.4 | 322.5 | 351.6 | 342.6 | 335.6
1111 | 948 | 469.5 | 187.8 | 219.5274 | 355.3 | 343.3 | 340.3 | 329.9 | 412.6 | 54.5 | 19.2 | 95.9 | 5.8 | 251.5 | 7.1 | 830.5 | 789.8 | 811.5 | 839.5 | 769.4 | 722.8 | 617.3 | 792.7 | 693.8 | 742 | 669.8 | 721.8 | 739.6 | 360.7 | 358.2 | 374.1 | 352.6 | 322.7 | 351.8 | 342.8 | 335.7
1112 | 949 | 468.9 | 187.56 | 219.2468 | 355.8 | 342.6 | 341.3 | 331 | 414.1 | 54.5 | 19.2 | 96 | 4.8 | 248.7 | 7.2 | 832.3 | 791 | 812 | 839.6 | 770 | 723 | 620.2 | 795.9 | 694.2 | 742.7 | 672.3 | 724.7 | 739.6 | 360.9 | 358.4 | 374.9 | 352.6 | 322.9 | 352 | 342.9 | 335.8
1113 | 950 | 468 | 187.2 | 218.826 | 355.1 | 341.5 | 342.1 | 332.3 | 411.4 | 54.5 | 19.2 | 96 | 5.1 | 244.4 | 6.3 | 833.4 | 791.6 | 813.8 | 840 | 770.8 | 723.3 | 616.2 | 793.3 | 694.5 | 741.5 | 674.8 | 721.7 | 740 | 361.1 | 358.5 | 375.6 | 352.6 | 323 | 352.3 | 343.1 | 335.8
1114 | 951 | 467.5 | 187 | 218.5922 | 354.4 | 341 | 342.1 | 333 | 415.3 | 54.5 | 19.2 | 96 | 5.2 | 249.9 | 5.9 | 834.2 | 792.8 | 818.5 | 840.3 | 773.8 | 723.5 | 617.2 | 794.4 | 694.9 | 742.1 | 677.8 | 727.7 | 738.1 | 361.3 | 359 | 376 | 352.7 | 323.2 | 352.8 | 343.2 | 335.9
1115 | 952 | 467.2 | 186.88 | 218.452 | 353.7 | 341.8 | 341.6 | 333.4 | 418.3 | 54.4 | 19.2 | 96 | 5.2 | 250.2 | 6.3 | 841.1 | 796.7 | 821.9 | 840 | 776.2 | 723.8 | 620.6 | 800.7 | 695.2 | 743.9 | 678.7 | 737.6 | 737.7 | 361.5 | 359.4 | 376.5 | 352.8 | 323.4 | 353 | 343.5 | 336
1116 | 953 | 467.4 | 186.96 | 218.5455 | 354.6 | 342 | 341.7 | 333.4 | 418.8 | 54.4 | 19.2 | 96 | 4.9 | 213.7 | 5.7 | 847.5 | 798.9 | 825.6 | 839.6 | 778 | 724 | 621.3 | 804.2 | 695.6 | 745.6 | 678 | 744.2 | 739.2 | 361.7 | 359.6 | 376.5 | 352.8 | 323.6 | 353.4 | 343.6 | 336.1
1117 | 954 | 467.6 | 187.04 | 218.639 | 356.8 | 340.7 | 342.2 | 333.6 | 417.9 | 54.4 | 19.2 | 96 | 5.1 | 210.5 | 4.8 | 854.4 | 799.6 | 829.7 | 839.1 | 780.1 | 724.1 | 617.1 | 806 | 695.8 | 746.9 | 679 | 749.4 | 739.3 | 361.9 | 359.5 | 376.4 | 352.7 | 323.7 | 353.7 | 343.8 | 336.1
1118 | 955 | 467.8 | 187.12 | 218.7325 | 358.4 | 339.1 | 342 | 333.6 | 421.8 | 54.3 | 19.2 | 96.1 | 4.9 | 252.7 | 4.6 | 856 | 800.2 | 829.4 | 838.7 | 779.6 | 724.3 | 615 | 802.9 | 696.1 | 746.6 | 680 | 747.7 | 739.6 | 362.1 | 359.4 | 376.5 | 352.6 | 323.9 | 353.8 | 343.8 | 336.2
1119 | 956 | 467.6 | 187.04 | 218.639 | 358.1 | 337.7 | 342.1 | 333.8 | 419.5 | 54.3 | 19.2 | 96.2 | 4.1 | 269 | 4.9 | 853.9 | 799.4 | 834.5 | 838.8 | 780.8 | 724.8 | 613.1 | 793.2 | 696.2 | 744.5 | 682 | 742.4 | 742 | 362.3 | 359.4 | 376.4 | 352.7 | 324.1 | 353.6 | 343.7 | 336.2
1120 | 957 | 468.2 | 187.28 | 218.9195 | 357 | 336.9 | 342.6 | 334 | 415.5 | 54.3 | 19.2 | 96.3 | 4.6 | 251.2 | 5 | 859.2 | 800.7 | 838 | 838.5 | 785.8 | 725 | 613.2 | 796.6 | 696.5 | 745.9 | 684.9 | 748.2 | 741.8 | 362.6 | 359.4 | 376.3 | 352.7 | 324.3 | 353.5 | 343.7 | 336.3
1121 | 958 | 467.5 | 187 | 218.5922 | 355.6 | 337.7 | 343 | 333.8 | 414 | 54.2 | 19.2 | 96.3 | 4.8 | 232.3 | 5.2 | 859.1 | 802.2 | 839.1 | 838.8 | 787 | 725.2 | 614.5 | 798.2 | 696.8 | 747.5 | 686 | 753 | 741.6 | 362.8 | 359.6 | 376.3 | 352.7 | 324.5 | 353.3 | 343.7 | 336.3
1122 | 959 | 467.4 | 186.96 | 218.5455 | 354.8 | 338.8 | 342.5 | 333.7 | 414.3 | 54.1 | 19.2 | 96.4 | 4.4 | 230.1 | 4.9 | 851.9 | 799.6 | 834.3 | 839.2 | 784.6 | 725.5 | 611.9 | 793.6 | 697.1 | 746.7 | 686.4 | 747.7 | 741.1 | 363 | 359.9 | 376.6 | 352.9 | 324.7 | 353.1 | 343.7 | 336.3
1123 | 960 | 468.4 | 187.36 | 219.013 | 353.8 | 339.2 | 342.3 | 333.3 | 414.7 | 54 | 19.2 | 96.4 | 4.3 | 231.1 | 4.9 | 848 | 797.5 | 829.7 | 839.3 | 782.2 | 726 | 608.6 | 791.4 | 697.3 | 745.8 | 687.1 | 739.4 | 740.7 | 363.2 | 360.2 | 376.8 | 353 | 324.8 | 353 | 343.5 | 336.2
1124 | 961 | 467.9 | 187.16 | 218.7793 | 352.6 | 338.9 | 342.9 | 332.8 | 415.6 | 54 | 19.2 | 96.4 | 4.4 | 248.8 | 4.8 | 843.4 | 797.6 | 823.3 | 839.3 | 780.2 | 726.3 | 612 | 792.7 | 697.5 | 747 | 688.5 | 744.7 | 740.4 | 363.4 | 360.3 | 377 | 353.1 | 325 | 352.8 | 343.3 | 336.2
1125 | 962 | 468.1 | 187.24 | 218.8728 | 351.7 | 339.6 | 343.1 | 332.3 | 416.3 | 54.1 | 19.2 | 96.5 | 5.2 | 263.2 | 4.6 | 844.9 | 799.5 | 824.1 | 839.4 | 777.9 | 726.5 | 618 | 796.2 | 697.8 | 746.8 | 689.7 | 744 | 740.5 | 363.6 | 360.3 | 377.2 | 353.2 | 325.2 | 352.7 | 343.1 | 336.2
1126 | 963 | 468.1 | 187.24 | 218.8728 | 352.1 | 340.3 | 342.8 | 332.7 | 417.5 | 54.2 | 19.2 | 96.6 | 4.6 | 229.8 | 4.3 | 846.2 | 799.3 | 821.9 | 839.2 | 776.8 | 726.8 | 619.1 | 797.9 | 698.1 | 746.5 | 692 | 741 | 741.9 | 363.8 | 360.5 | 377.6 | 353.3 | 325.4 | 352.7 | 343.1 | 336.2
1127 | 964 | 468.5 | 187.4 | 219.0598 | 353.4 | 340.8 | 342.2 | 333.2 | 416.2 | 54.2 | 19.2 | 96.7 | 4.5 | 229.7 | 4.4 | 841 | 795.8 | 816.9 | 839.4 | 772 | 727.2 | 618.4 | 795.7 | 698.4 | 744.8 | 693.3 | 731.1 | 742.8 | 364 | 360.8 | 378 | 353.4 | 325.6 | 352.8 | 343.3 | 336.3
1128 | 965 | 468.6 | 187.44 | 219.1066 | 353.8 | 340.9 | 342 | 333.5 | 413.7 | 54.3 | 19.1 | 96.7 | 4.4 | 248.3 | 4.9 | 839.8 | 794.1 | 816.8 | 839.5 | 769.7 | 727.9 | 616.8 | 789.5 | 698.7 | 742.9 | 694.3 | 722.6 | 742 | 364.2 | 361 | 378.3 | 353.5 | 325.7 | 353 | 343.5 | 336.3
1129 | 966 | 468.2 | 187.28 | 218.9195 | 352.9 | 341.5 | 342 | 333.2 | 412.5 | 54.4 | 19.1 | 96.7 | 5 | 237.3 | 5 | 842.1 | 795.1 | 820.6 | 839.4 | 770 | 728.4 | 618.6 | 789.6 | 699.1 | 743.2 | 696.4 | 723.5 | 742.2 | 364.4 | 361.5 | 378.7 | 353.6 | 325.9 | 353.2 | 343.6 | 336.4
1130 | 967 | 468.5 | 187.4 | 219.0598 | 351.7 | 341.9 | 341.9 | 333.5 | 411.3 | 54.4 | 19.1 | 96.8 | 4.6 | 213.2 | 4.3 | 838.1 | 793.1 | 816.2 | 839.1 | 767.7 | 728.7 | 615.7 | 782.9 | 699.4 | 741.7 | 696.5 | 720.1 | 744.4 | 364.5 | 361.8 | 379 | 353.7 | 326.1 | 353.2 | 343.6 | 336.5
1131 | 968 | 468.6 | 187.44 | 219.1066 | 352.6 | 341 | 342.4 | 333.7 | 410.9 | 54.4 | 19.1 | 96.8 | 4.5 | 213 | 3.7 | 835.6 | 790.6 | 810.7 | 838.6 | 765.5 | 729.4 | 611.4 | 773.2 | 699.7 | 739.5 | 697.2 | 714.3 | 744.1 | 364.7 | 362 | 379.3 | 353.9 | 326.2 | 353.3 | 343.6 | 336.5
1132 | 969 | 469.6 | 187.84 | 219.5741 | 355.7 | 339.7 | 342.6 | 334.3 | 410.8 | 54.5 | 19.1 | 96.8 | 4.8 | 222.2 | 3.3 | 821.8 | 781.9 | 797.8 | 838.1 | 760.5 | 730 | 608 | 758.8 | 699.9 | 736.4 | 697.9 | 701 | 742.6 | 364.9 | 362.1 | 379.4 | 354.1 | 326.4 | 353.6 | 343.5 | 336.5
1133 | 970 | 469.6 | 187.84 | 219.5741 | 359.5 | 338.5 | 342.6 | 335.2 | 409.6 | 54.4 | 19.1 | 96.7 | 4.9 | 230.1 | 3.2 | 814.1 | 773.9 | 787.9 | 837 | 757 | 730.8 | 603.2 | 740.8 | 700 | 731.9 | 698.1 | 688.1 | 742.9 | 365.1 | 362.1 | 379.4 | 354.2 | 326.6 | 353.7 | 343.4 | 336.5
1134 | 971 | 468.6 | 187.44 | 219.1066 | 359.4 | 337.3 | 343 | 335.9 | 408.5 | 54.5 | 19.1 | 96.7 | 4.1 | 220.3 | 3 | 814.5 | 774 | 786.6 | 836.1 | 755.7 | 731.4 | 599.8 | 732.7 | 700.3 | 730.4 | 698.1 | 689.1 | 746.3 | 365.3 | 362 | 379.5 | 354.1 | 326.7 | 354.1 | 343.5 | 336.6
1135 | 972 | 469.3 | 187.72 | 219.4339 | 357.7 | 336.2 | 343.7 | 336.8 | 405.5 | 54.6 | 19.1 | 96.6 | 4.1 | 192.1 | 2.9 | 821.8 | 776.9 | 792.8 | 835.6 | 757.2 | 731.9 | 599.4 | 727.6 | 700.9 | 728 | 698.9 | 697.6 | 750.9 | 365.5 | 361.8 | 379.4 | 354 | 326.9 | 354.4 | 343.6 | 336.7
1136 | 973 | 469.3 | 187.72 | 219.4339 | 356 | 335.3 | 343.9 | 337.5 | 402.9 | 54.8 | 19.1 | 96.5 | 4.1 | 194.4 | 3.4 | 828.9 | 783.1 | 798.7 | 835.4 | 758.6 | 732.3 | 597.3 | 734.2 | 701.4 | 728.5 | 699.9 | 709.3 | 752.5 | 365.7 | 361.7 | 379.2 | 353.9 | 327.1 | 354.7 | 343.8 | 336.8
1137 | 974 | 470.6 | 188.24 | 220.0417 | 357.5 | 334.3 | 343.6 | 337.8 | 402.5 | 55 | 19.1 | 96.5 | 4.4 | 212.8 | 3.7 | 830.1 | 782.5 | 797.2 | 835.1 | 756.2 | 732.6 | 598.4 | 741 | 701.9 | 727.8 | 699.7 | 708.5 | 752.2 | 365.9 | 361.8 | 379 | 353.9 | 327.3 | 354.8 | 343.9 | 336.8
1138 | 975 | 470 | 188 | 219.7612 | 360.3 | 333 | 343.2 | 337.8 | 403 | 55.1 | 19.1 | 96.5 | 4.4 | 222.8 | 3.5 | 831.9 | 785.3 | 797.6 | 835 | 755.4 | 733 | 605.2 | 746 | 702.3 | 726.6 | 699.9 | 712.9 | 749.6 | 366.1 | 361.8 | 378.8 | 354 | 327.4 | 354.8 | 344 | 336.9
1139 | 976 | 470 | 188 | 219.7612 | 361.4 | 332.6 | 343.2 | 337.4 | 405.4 | 55.2 | 19.1 | 96.6 | 4.5 | 221.1 | 3.3 | 832.7 | 787.1 | 801 | 834.9 | 754.9 | 733.3 | 606.2 | 758.1 | 702.7 | 728.2 | 700 | 714.5 | 747.7 | 366.3 | 361.8 | 378.9 | 354.3 | 327.6 | 354.7 | 344 | 336.9
1140 | 977 | 469.7 | 187.88 | 219.6209 | 361.3 | 333.9 | 343.6 | 336.7 | 408.9 | 55.1 | 19.1 | 96.6 | 3.6 | 204.4 | 3.3 | 837 | 790.5 | 805.3 | 834.8 | 756.7 | 733.5 | 610.7 | 771 | 703 | 730.2 | 699.4 | 718.5 | 745.4 | 366.5 | 361.6 | 378.8 | 354.3 | 327.8 | 354.7 | 344 | 337
1141 | 978 | 468.8 | 187.52 | 219.2001 | 363.3 | 335.1 | 343.9 | 337 | 411.4 | 55 | 19.1 | 96.6 | 3.7 | 201.7 | 3.3 | 845.9 | 795.2 | 810.9 | 834.5 | 760.2 | 733.5 | 607.5 | 781.7 | 703.3 | 732.4 | 697.9 | 730 | 744.3 | 366.7 | 361.4 | 378.6 | 354.2 | 328 | 354.4 | 344 | 337.1
1142 | 979 | 467.9 | 187.16 | 218.7793 | 364 | 336.3 | 344.2 | 337.4 | 411.5 | 55 | 19.1 | 96.7 | 4 | 211.1 | 3.6 | 849.4 | 798.9 | 810 | 834.3 | 761.9 | 733.4 | 607.2 | 783.7 | 703.6 | 732.7 | 696.2 | 737.2 | 744.6 | 366.9 | 361.4 | 378.8 | 354 | 328.1 | 354.4 | 344.1 | 337.1
1143 | 980 | 467.1 | 186.84 | 218.4052 | 363.2 | 337.3 | 343.5 | 337.2 | 409.5 | 54.9 | 19.1 | 96.7 | 4.8 | 223 | 3.5 | 843.8 | 791.9 | 803 | 833.7 | 759.2 | 733.6 | 605 | 766.6 | 703.8 | 729 | 694.8 | 722.2 | 745.7 | 367.1 | 361.7 | 378.7 | 354.1 | 328.3 | 354.7 | 344.2 | 337.2
1144 | 981 | 468.1 | 187.24 | 218.8728 | 364.3 | 337.9 | 342.7 | 337.1 | 407.9 | 54.8 | 19.1 | 96.7 | 5 | 214.4 | 3.1 | 842.2 | 789 | 802.1 | 832.9 | 757.8 | 733.9 | 607 | 754.3 | 704.2 | 726.7 | 694.3 | 713.9 | 746.4 | 367.3 | 361.9 | 378.4 | 354.3 | 328.5 | 354.4 | 344.3 | 337.2
1145 | 982 | 468.6 | 187.44 | 219.1066 | 365.8 | 338 | 342.2 | 336.5 | 407.1 | 54.7 | 19.1 | 96.8 | 4.3 | 203.5 | 3 | 839 | 790.3 | 798.2 | 832.3 | 755.6 | 734.1 | 608.3 | 751.5 | 704.4 | 726.4 | 694.6 | 712.5 | 745.5 | 367.4 | 361.8 | 378.3 | 354.5 | 328.7 | 354.1 | 344.3 | 337.2
1146 | 983 | 468.6 | 187.44 | 219.1066 | 366.5 | 337.8 | 341.3 | 335.7 | 406.4 | 54.7 | 19.1 | 96.9 | 4.7 | 196 | 3 | 835.4 | 787.8 | 793.7 | 831.6 | 752.6 | 734.3 | 606.5 | 743.3 | 704.7 | 724.1 | 694.5 | 706.7 | 744 | 367.6 | 361.7 | 378 | 354.6 | 328.8 | 353.9 | 344.1 | 337.2
1147 | 984 | 467.5 | 187 | 218.5922 | 366.5 | 337.1 | 341 | 335.1 | 405.9 | 54.8 | 19.1 | 97 | 4.3 | 196.8 | 3 | 829.9 | 787.5 | 791.1 | 831 | 750.6 | 734.8 | 607 | 740.4 | 705.1 | 723.1 | 695.1 | 705.6 | 743.7 | 367.8 | 361.6 | 377.6 | 354.6 | 329 | 353.8 | 344 | 337.2
1148 | 985 | 467.3 | 186.92 | 218.4987 | 365.4 | 336 | 341.1 | 335.2 | 409.2 | 54.7 | 19.1 | 97.1 | 4.8 | 190.4 | 2.7 | 825.4 | 788.1 | 780.3 | 830.9 | 747.3 | 734.9 | 611 | 742.6 | 705.5 | 722.7 | 695.7 | 707.3 | 744.3 | 368 | 361.4 | 377.4 | 354.7 | 329.2 | 354 | 343.9 | 337.2
1149 | 986 | 467.1 | 186.84 | 218.4052 | 364.4 | 336.3 | 341.1 | 335.9 | 409.5 | 54.6 | 19.1 | 97.2 | 4.8 | 182.7 | 2.9 | 824 | 790.1 | 783.9 | 830.6 | 746.7 | 735.1 | 610.2 | 751.3 | 705.9 | 723 | 695.8 | 705.2 | 744 | 368.1 | 361.3 | 377.4 | 354.8 | 329.3 | 354.2 | 343.9 | 337.2
1150 | 987 | 467.2 | 186.88 | 218.452 | 363.4 | 337 | 341.4 | 337.3 | 410.8 | 54.6 | 19.1 | 97.3 | 4.1 | 183 | 3.2 | 821.2 | 790.1 | 790.4 | 831 | 749.4 | 735.2 | 610.3 | 755.1 | 706.1 | 723.1 | 694.8 | 706.8 | 739.8 | 368.3 | 361.5 | 377.7 | 354.9 | 329.5 | 354.4 | 343.9 | 337.2
1151 | 988 | 466.5 | 186.6 | 218.1246 | 361.9 | 337.5 | 342.2 | 338.2 | 413.9 | 54.6 | 19.1 | 97.3 | 4.2 | 183.5 | 3.4 | 820.1 | 789.4 | 795 | 831.3 | 751 | 735.5 | 609.7 | 759.4 | 706.5 | 724.2 | 694.8 | 710.6 | 735.3 | 368.4 | 361.9 | 378.2 | 355.1 | 329.7 | 354.5 | 344 | 337.3
1152 | 989 | 467.6 | 187.04 | 218.639 | 360.4 | 337.5 | 342.7 | 339.1 | 418.5 | 54.6 | 19.1 | 97.3 | 4.5 | 189 | 3.3 | 815.4 | 788 | 796.8 | 831.7 | 750 | 735.5 | 608.1 | 757.8 | 706.8 | 725.3 | 693.6 | 711.1 | 730.8 | 368.6 | 362.2 | 378.3 | 355.3 | 329.8 | 354.8 | 344.4 | 337.4
1153 | 990 | 468.6 | 187.44 | 219.1066 | 359.5 | 338.1 | 343 | 339.3 | 424.2 | 54.7 | 19.1 | 97.2 | 3.9 | 202.6 | 3.2 | 811 | 782.7 | 789.4 | 831.8 | 747.8 | 735.7 | 605.9 | 748.6 | 707 | 724.7 | 692.2 | 705.4 | 726.3 | 368.8 | 362.8 | 378.6 | 355.6 | 330 | 355.1 | 344.5 | 337.4
1154 | 991 | 468.4 | 187.36 | 219.013 | 358.7 | 338.4 | 343.4 | 339.4 | 434.8 | 54.6 | 19.1 | 97.3 | 4.4 | 209.1 | 3 | 807.2 | 778.1 | 785.7 | 832.3 | 746.2 | 735.9 | 604.1 | 738.7 | 707.2 | 723.1 | 691.1 | 692.4 | 721.2 | 369 | 363.3 | 378.9 | 355.9 | 330.1 | 355.3 | 344.7 | 337.5
1155 | 992 | 467.4 | 186.96 | 218.5455 | 358.4 | 338.6 | 343.5 | 339.5 | 445.3 | 54.5 | 19.1 | 97.3 | 4.7 | 205.7 | 2.9 | 813.3 | 786.2 | 797.3 | 832.5 | 749.4 | 736.2 | 601.9 | 745.8 | 707.8 | 724.7 | 690.7 | 702.2 | 717.5 | 369.2 | 363.6 | 378.9 | 356 | 330.3 | 355.5 | 344.8 | 337.6
1156 | 993 | 467.3 | 186.92 | 218.4987 | 358 | 339.3 | 343.6 | 340.2 | 451.5 | 54.5 | 19.1 | 97.3 | 4.6 | 204 | 2.7 | 818.9 | 792.5 | 803 | 832.4 | 751.9 | 736.3 | 604.1 | 761.9 | 708.3 | 727.6 | 690.7 | 718 | 715.7 | 369.4 | 363.6 | 378.8 | 355.9 | 330.5 | 355.9 | 345.1 | 337.7
1157 | 994 | 467.3 | 186.92 | 218.4987 | 357.2 | 339.7 | 343.6 | 340.9 | 445.7 | 54.5 | 19.1 | 97.4 | 4.8 | 203.9 | 2.5 | 820.9 | 796.3 | 806 | 832.8 | 751.4 | 736.2 | 606.6 | 768.1 | 708.7 | 728.8 | 689.7 | 725.9 | 718.3 | 369.6 | 363.7 | 379.2 | 355.8 | 330.6 | 356.5 | 345.4 | 337.8
1158 | 995 | 469.7 | 187.88 | 219.6209 | 356.3 | 339.3 | 343.7 | 341.7 | 440.3 | 54.5 | 19.1 | 97.4 | 4.7 | 200.6 | 2.3 | 821.3 | 796.1 | 810.6 | 833.4 | 752.8 | 736.2 | 606.2 | 770.2 | 709 | 729 | 688.3 | 725.1 | 719.7 | 369.7 | 363.9 | 379.4 | 355.9 | 330.8 | 356.5 | 345.4 | 337.8
1159 | 996 | 467.9 | 187.16 | 218.7793 | 355.5 | 339.1 | 344.2 | 341.6 | 439.8 | 54.5 | 19.1 | 97.5 | 4.7 | 192.7 | 2 | 822.5 | 799.2 | 815.8 | 833.7 | 755.5 | 736.3 | 609.7 | 774.7 | 709.3 | 731.3 | 688.2 | 727.3 | 719 | 369.9 | 363.9 | 379.6 | 355.9 | 331 | 356.4 | 345.5 | 337.9
1160 | 997 | 467.7 | 187.08 | 218.6857 | 354.3 | 340.5 | 344.4 | 341 | 445.3 | 54.5 | 19.1 | 97.6 | 4.8 | 184.7 | 1.7 | 826.2 | 802.5 | 818.4 | 833.5 | 758.2 | 736.4 | 611.1 | 779 | 709.6 | 733.4 | 687.4 | 734.6 | 717.7 | 370.1 | 363.9 | 379.7 | 355.9 | 331.2 | 356.3 | 345.5 | 337.9
1161 | 998 | 468 | 187.2 | 218.826 | 353.6 | 342.5 | 344.3 | 340.8 | 440.7 | 54.6 | 19.1 | 97.7 | 4.9 | 182.8 | 1.4 | 830.2 | 806.4 | 822.9 | 832.9 | 760.6 | 736.3 | 613.9 | 787.9 | 709.7 | 735 | 686.5 | 742 | 716.8 | 370.3 | 363.8 | 379.8 | 355.8 | 331.3 | 356.3 | 345.6 | 337.9
1162 | 999 | 467.9 | 187.16 | 218.7793 | 353.1 | 344.1 | 344.3 | 340.6 | 437.9 | 54.7 | 19.1 | 97.8 | 4.3 | 188.8 | 1.2 | 837 | 811.9 | 829.1 | 832.9 | 761.9 | 736.2 | 614.6 | 794.1 | 709.7 | 736.7 | 685.5 | 750.3 | 716.4 | 370.5 | 363.8 | 379.9 | 355.7 | 331.5 | 356.4 | 345.5 | 338
1163 | 1000 | 468.7 | 187.48 | 219.1533 | 352.6 | 344.4 | 343.9 | 340.3 | 437.8 | 54.7 | 19.1 | 97.9 | 4.5 | 196.4 | 0.8 | 841.2 | 815.6 | 830.6 | 833 | 764.6 | 736.1 | 616.6 | 792.1 | 709.7 | 738 | 685 | 754.4 | 715 | 370.7 | 363.7 | 380.2 | 355.7 | 331.7 | 356.3 | 345.4 | 338
1164 | 1001 | 469.4 | 187.76 | 219.4806 | 352.6 | 344.1 | 343.3 | 340 | 431.8 | 54.8 | 19.1 | 97.9 | 4.8 | 201.1 | 0.6 | 848.5 | 815.8 | 831.4 | 832.9 | 765.4 | 736.1 | 617.8 | 794.6 | 709.9 | 740 | 685.2 | 759.8 | 716.7 | 370.9 | 363.3 | 379.8 | 355.6 | 331.9 | 356 | 345.4 | 338
1165 | 1002 | 469.3 | 187.72 | 219.4339 | 351.4 | 344.2 | 343 | 339.4 | 427.6 | 54.8 | 19.1 | 97.9 | 4.3 | 200.3 | 0.4 | 852.4 | 818.4 | 826.8 | 832.6 | 763.4 | 735.8 | 619.1 | 793.8 | 710.1 | 740.1 | 684.4 | 760.2 | 722.1 | 371.1 | 363 | 380.1 | 355.6 | 332 | 355.8 | 345.3 | 338.1
1166 | 1003 | 469.4 | 187.76 | 219.4806 | 350.9 | 344.8 | 342.4 | 338.6 | 423.5 | 54.9 | 19.1 | 97.9 | 4.2 | 197.3 | 0.3 | 856 | 817.8 | 827.7 | 832 | 767.3 | 735.9 | 618.1 | 796.8 | 710.4 | 740.6 | 684.9 | 762.6 | 728.2 | 371.2 | 362.7 | 380.1 | 355.5 | 332.2 | 355.6 | 345.1 | 338.1
1167 | 1004 | 468.8 | 187.52 | 219.2001 | 352.2 | 344.3 | 342 | 337.3 | 419.2 | 54.9 | 19.1 | 98 | 5.1 | 187.6 | 0.2 | 856.7 | 820.1 | 834.9 | 832.4 | 770.8 | 735.9 | 620.7 | 795.9 | 710.5 | 741.2 | 687 | 763.7 | 728.4 | 371.4 | 362.3 | 379.6 | 355.3 | 332.3 | 355.4 | 345 | 338.1
1168 | 1005 | 468.2 | 187.28 | 218.9195 | 352.4 | 344.4 | 341.6 | 336.4 | 421.2 | 54.9 | 19.1 | 97.9 | 5.1 | 165.5 | 0.3 | 854.2 | 822.3 | 835.9 | 833.6 | 772 | 736.2 | 623.7 | 800.9 | 710.8 | 744 | 688.5 | 769.3 | 724.8 | 371.6 | 362.1 | 379.2 | 355.3 | 332.5 | 355.3 | 345 | 338.2
1169 | 1006 | 468.9 | 187.56 | 219.2468 | 352.5 | 345.3 | 341 | 336 | 421.9 | 54.9 | 19.1 | 97.8 | 5.1 | 145.7 | 0.3 | 852.6 | 824.7 | 837.4 | 834.4 | 775.1 | 736.3 | 626 | 807 | 710.8 | 746.4 | 688.3 | 772.5 | 722 | 371.8 | 362 | 379.2 | 355.4 | 332.6 | 355.4 | 345.1 | 338.2
1170 | 1007 | 469.2 | 187.68 | 219.3871 | 352 | 346.3 | 340.8 | 335.7 | 421.3 | 55 | 19.1 | 97.8 | 5.3 | 138.9 | 0.1 | 855.3 | 823.6 | 839.2 | 834.2 | 777.8 | 736.1 | 626.7 | 806.4 | 710.9 | 747 | 687.7 | 774.4 | 720.8 | 372 | 361.8 | 378.8 | 355.3 | 332.8 | 355.4 | 345.2 | 338.2
1171 | 1008 | 468.9 | 187.56 | 219.2468 | 351.4 | 347.3 | 340.7 | 335.8 | 419.3 | 55 | 19.1 | 97.9 | 5.1 | 152 | 0.1 | 853.4 | 824.5 | 839.8 | 834 | 780.4 | 736.4 | 631.6 | 811.8 | 710.9 | 749.4 | 688.8 | 775.9 | 720 | 372.1 | 361.6 | 378.5 | 355.2 | 332.9 | 355.2 | 345.4 | 338.3
1172 | 1009 | 468.6 | 187.44 | 219.1066 | 350.1 | 347.9 | 340.7 | 335.2 | 421.4 | 55 | 19.1 | 98 | 4.5 | 185.5 | 0.9 | 857.4 | 827.7 | 843.8 | 833.9 | 784.3 | 736.3 | 634.5 | 810.6 | 710.9 | 750.3 | 688.8 | 776.9 | 718.7 | 372.3 | 361.5 | 378.3 | 355.4 | 333.1 | 355.2 | 345.5 | 338.3
1173 | 1010 | 468.5 | 187.4 | 219.0598 | 349.5 | 348.1 | 340.8 | 334.8 | 423.8 | 55 | 19.1 | 98.1 | 4.4 | 208.6 | 1.7 | 857 | 831.1 | 840.9 | 835 | 784.6 | 736.3 | 635.7 | 811.3 | 710.8 | 751.7 | 688.7 | 775 | 717.1 | 372.4 | 361.5 | 378.1 | 355.5 | 333.3 | 355.2 | 345.4 | 338.3
1174 | 1011 | 468.1 | 187.24 | 218.8728 | 349.3 | 348.9 | 341.4 | 335.1 | 427.5 | 55.1 | 19.1 | 98.1 | 4.3 | 210.7 | 2 | 840.8 | 819.7 | 823.3 | 835.6 | 778.1 | 736.4 | 636.6 | 795.7 | 710.7 | 749.5 | 687.9 | 754.6 | 714.1 | 372.6 | 361.7 | 378.3 | 355.9 | 333.4 | 355.3 | 345.4 | 338.3
1175 | 1012 | 468.6 | 187.44 | 219.1066 | 349.6 | 349.6 | 342 | 335.2 | 427.6 | 55.1 | 19.1 | 98.1 | 4.5 | 203.1 | 1.9 | 828.8 | 809.9 | 814.9 | 835.7 | 773.2 | 736.6 | 631.9 | 784.7 | 711 | 747.1 | 687.5 | 736.8 | 712.2 | 372.7 | 362 | 378.5 | 356.4 | 333.6 | 355.6 | 345.4 | 338.2
1176 | 1013 | 468.6 | 187.44 | 219.1066 | 349.9 | 350.4 | 342.6 | 335.8 | 427.2 | 55.1 | 19.1 | 98 | 4.7 | 208.4 | 1.8 | 828.5 | 809.4 | 816.7 | 836.3 | 773 | 736.8 | 628.6 | 789.1 | 711.6 | 747 | 687.7 | 738.3 | 711.6 | 372.9 | 362.4 | 378.7 | 356.6 | 333.7 | 355.5 | 345.3 | 338.3
1177 | 1014 | 467.9 | 187.16 | 218.7793 | 350.2 | 350.1 | 343.2 | 336.5 | 426.4 | 55.1 | 19.1 | 97.8 | 4 | 219.8 | 1.9 | 832.3 | 812.9 | 823.6 | 836.6 | 775 | 736.9 | 627.2 | 797.5 | 711.9 | 748.5 | 688.2 | 745.3 | 712.5 | 373 | 362.8 | 378.8 | 356.7 | 333.9 | 355.7 | 345.4 | 338.4
1178 | 1015 | 468.2 | 187.28 | 218.9195 | 349.7 | 350.4 | 344.1 | 337.5 | 427.9 | 55 | 19.1 | 97.8 | 4.5 | 220.7 | 2.2 | 838.1 | 816.2 | 828 | 837.3 | 777.4 | 737.1 | 629 | 804 | 712.2 | 750.8 | 688.6 | 754 | 714.9 | 373.2 | 363 | 379.1 | 356.6 | 334 | 355.9 | 345.7 | 338.5
1179 | 1016 | 469.3 | 187.72 | 219.4339 | 349.2 | 349.9 | 344.1 | 338.3 | 426.8 | 55.1 | 19.1 | 97.8 | 4.6 | 220.3 | 2.3 | 846 | 821.1 | 834.3 | 837.3 | 779.9 | 737.1 | 630.5 | 806.6 | 712.5 | 751.7 | 688.8 | 762.5 | 716.1 | 373.3 | 363.1 | 379.1 | 356.5 | 334.2 | 356.3 | 346 | 338.6
1180 | 1017 | 468.5 | 187.4 | 219.0598 | 348.6 | 348.9 | 343.8 | 338.5 | 423.3 | 55.2 | 19.1 | 97.9 | 5 | 218.1 | 2.3 | 849.4 | 824.5 | 836.5 | 837.4 | 783.1 | 737.3 | 630.7 | 806.9 | 712.7 | 753.5 | 689.2 | 770.1 | 715.3 | 373.5 | 363 | 378.9 | 356.4 | 334.3 | 356.2 | 346.2 | 338.8
1181 | 1018 | 469.6 | 187.84 | 219.5741 | 347.8 | 348.4 | 343.5 | 338.2 | 421.9 | 55.2 | 19.1 | 98 | 4.6 | 210.1 | 2.3 | 854.2 | 827 | 838.8 | 838 | 786.2 | 737.6 | 631.1 | 803.1 | 712.9 | 754.1 | 689.5 | 772.8 | 715 | 373.6 | 362.9 | 378.9 | 356.3 | 334.5 | 356 | 346.2 | 338.8
1182 | 1019 | 469.3 | 187.72 | 219.4339 | 347.7 | 348.3 | 343 | 337.5 | 419.4 | 55.3 | 19.1 | 98.1 | 4.8 | 205.9 | 2.4 | 854.6 | 828.4 | 838 | 838.8 | 786.2 | 737.6 | 630.8 | 804.5 | 713.1 | 755 | 689.3 | 773.8 | 716.3 | 373.8 | 362.7 | 378.8 | 356.2 | 334.6 | 355.9 | 346.2 | 338.8
1183 | 1020 | 469.3 | 187.72 | 219.4339 | 347.7 | 348.5 | 342.9 | 336.5 | 418.7 | 55.3 | 19.1 | 98 | 4.8 | 206 | 2.5 | 856.9 | 830.8 | 840 | 839.2 | 788.6 | 737.8 | 630.8 | 809.1 | 713.3 | 756.1 | 689 | 776.4 | 718.2 | 373.9 | 362.4 | 378.7 | 356.2 | 334.8 | 355.6 | 346 | 338.9
1184 | 1021 | 469.5 | 187.8 | 219.5274 | 346.6 | 349 | 342.2 | 336.1 | 416.7 | 55.3 | 19.1 | 97.8 | 4.4 | 205.8 | 2.6 | 860.3 | 833.1 | 844.3 | 839.2 | 792.1 | 737.9 | 631.8 | 808.8 | 713.4 | 756.6 | 688.5 | 777.8 | 720.4 | 374.1 | 362.1 | 378.6 | 356 | 334.9 | 355.6 | 346 | 338.9
1185 | 1022 | 469.2 | 187.68 | 219.3871 | 345.6 | 349 | 341.3 | 335.9 | 412.3 | 55.2 | 19.1 | 97.8 | 4.7 | 206.9 | 2.8 | 861.8 | 834.2 | 847.4 | 838.7 | 795.8 | 738 | 632.9 | 807.9 | 713.6 | 756.7 | 688.8 | 777.9 | 720.6 | 374.3 | 361.7 | 378.3 | 355.8 | 335.1 | 355.5 | 346 | 339
1186 | 1023 | 468.5 | 187.4 | 219.0598 | 345.4 | 349.2 | 340.9 | 335.7 | 410.1 | 55.1 | 19.1 | 97.8 | 4.7 | 209.2 | 2.9 | 864.1 | 835.9 | 846.1 | 839.2 | 796.6 | 738.1 | 637.5 | 808.8 | 713.7 | 756.5 | 689.1 | 774.9 | 721.7 | 374.4 | 361.6 | 378.1 | 355.8 | 335.2 | 355.3 | 345.8 | 339
1187 | 1024 | 469.1 | 187.64 | 219.3403 | 345.1 | 348.8 | 340 | 335.5 | 421.5 | 55 | 19.1 | 97.7 | 4.9 | 216.6 | 2.8 | 858.4 | 833.9 | 843.6 | 841 | 797.5 | 738.4 | 639.1 | 808.3 | 713.8 | 757.6 | 690.7 | 771.8 | 719.8 | 374.5 | 361.7 | 378 | 356 | 335.4 | 355.3 | 345.7 | 339
1188 | 1025 | 467.5 | 187 | 218.5922 | 345 | 350.6 | 339.9 | 335.4 | 422.2 | 55 | 19.1 | 97.7 | 5 | 227.5 | 2.7 | 856.3 | 834.7 | 846.3 | 841.1 | 802.7 | 738.7 | 640.8 | 808.8 | 714 | 758.5 | 691.5 | 775.9 | 717.3 | 374.7 | 361.5 | 377.9 | 356 | 335.5 | 355.3 | 345.9 | 339
1189 | 1026 | 469 | 187.6 | 219.2936 | 344.5 | 352.5 | 340.2 | 336 | 420.5 | 54.9 | 19.1 | 97.8 | 5.5 | 221 | 2.6 | 859 | 836.4 | 847.5 | 840.9 | 805.8 | 738.9 | 642.2 | 811.7 | 714.3 | 759.5 | 691.7 | 777.4 | 716.5 | 374.8 | 361.3 | 377.6 | 355.9 | 335.7 | 355.2 | 346.1 | 339.1
1190 | 1027 | 466.5 | 186.6 | 218.1246 | 344.7 | 353.3 | 340.4 | 336.2 | 424 | 54.9 | 19.1 | 97.8 | 4.8 | 201.8 | 2.7 | 865.2 | 837 | 849.7 | 840.9 | 806.6 | 739.1 | 644.3 | 815 | 714.4 | 760.2 | 691.3 | 779.1 | 718.2 | 374.9 | 361.4 | 377.4 | 356.1 | 335.8 | 355.2 | 346.1 | 339.2
1191 | 1028 | 467.9 | 187.16 | 218.7793 | 344.9 | 354.2 | 340.6 | 336.3 | 422.9 | 54.9 | 19.1 | 97.7 | 5 | 199.4 | 2.5 | 870.1 | 836.7 | 848.8 | 841.5 | 804.5 | 739 | 644.8 | 814.3 | 714.4 | 760 | 690.3 | 772 | 722.1 | 375 | 361.4 | 377.3 | 356.3 | 336 | 355.2 | 346 | 339.2
1192 | 1029 | 467.2 | 186.88 | 218.452 | 345 | 353.9 | 341.1 | 336.3 | 418.9 | 55 | 19.1 | 97.7 | 5.4 | 214.2 | 2.3 | 869.4 | 833.7 | 846.7 | 842 | 802.3 | 739 | 643.1 | 815.7 | 714.4 | 759.7 | 690.1 | 762.4 | 726 | 375.2 | 361.5 | 377.3 | 356.3 | 336.1 | 355.1 | 345.8 | 339.2
1193 | 1030 | 468 | 187.2 | 218.826 | 345.1 | 353.3 | 341.3 | 336.1 | 417.4 | 55.1 | 19.1 | 97.8 | 5.2 | 233.9 | 2.1 | 868.4 | 833.5 | 846.8 | 842.6 | 803.1 | 739.2 | 642.4 | 819.3 | 714.5 | 761 | 690.6 | 766.6 | 726.9 | 375.3 | 361.5 | 377.2 | 356.4 | 336.2 | 355.1 | 345.8 | 339.2
1194 | 1031 | 468.4 | 187.36 | 219.013 | 345.4 | 352.7 | 341.2 | 335.9 | 418.3 | 55.2 | 19.1 | 97.8 | 5.7 | 236.3 | 1.9 | 868.3 | 830.9 | 843 | 842.6 | 801.2 | 739.3 | 643.6 | 817.6 | 714.7 | 761.1 | 690.8 | 765.3 | 729.4 | 375.4 | 361.7 | 377.1 | 356.6 | 336.4 | 354.9 | 345.7 | 339.2
1195 | 1032 | 468 | 187.2 | 218.826 | 345.7 | 352.3 | 341 | 335.8 | 415.8 | 55.3 | 19 | 97.8 | 5.3 | 230.2 | 1.8 | 869.1 | 831.1 | 840.5 | 842.3 | 800.3 | 739.4 | 644.8 | 818.7 | 714.8 | 760.1 | 690.6 | 764.6 | 736.2 | 375.5 | 361.6 | 377.1 | 356.5 | 336.5 | 354.7 | 345.7 | 339.2
1196 | 1033 | 466.4 | 186.56 | 218.0779 | 345.2 | 353.1 | 341.4 | 335.7 | 412.8 | 55.3 | 19.1 | 97.8 | 5.4 | 213.6 | 1.8 | 868 | 829.6 | 840.3 | 842.1 | 800.2 | 739.5 | 641.7 | 816.5 | 715.1 | 760.5 | 691.5 | 767.9 | 739.6 | 375.7 | 361.4 | 377.1 | 356.4 | 336.7 | 354.8 | 345.6 | 339.2
1197 | 1034 | 467.1 | 186.84 | 218.4052 | 345.4 | 353.1 | 341.8 | 335.3 | 417.1 | 55.3 | 19.1 | 97.8 | 5.3 | 199.3 | 1.7 | 868.3 | 829.3 | 843.4 | 842 | 800.8 | 739.7 | 640.5 | 816.6 | 715.5 | 760.8 | 692.7 | 767.5 | 741.7 | 375.8 | 361.3 | 376.9 | 356.3 | 336.8 | 355 | 345.6 | 339.3
1198 | 1035 | 468.3 | 187.32 | 218.9663 | 346.9 | 354.1 | 342.1 | 335.2 | 425.8 | 55.4 | 19.1 | 97.8 | 5.4 | 190.7 | 1.6 | 868.8 | 830.5 | 844.3 | 842.5 | 804 | 740 | 641.6 | 812.4 | 716 | 761.7 | 694.1 | 772.6 | 740.8 | 375.9 | 361.1 | 376.7 | 356.2 | 336.9 | 355 | 345.7 | 339.3
1199 | 1036 | 468.7 | 187.48 | 219.1533 | 346.8 | 354.6 | 341.8 | 335.4 | 428.1 | 55.5 | 19 | 97.8 | 5.2 | 187.3 | 1.7 | 870.5 | 832.3 | 848.6 | 843.5 | 807.2 | 740.2 | 642.2 | 808.1 | 716.5 | 761.5 | 695.6 | 776.4 | 740.3 | 376 | 360.8 | 376.6 | 356.1 | 337.1 | 355.1 | 345.8 | 339.4
1200 | 1037 | 467.3 | 186.92 | 218.4987 | 347 | 355 | 341.6 | 335.3 | 423.3 | 55.6 | 19 | 97.8 | 4.9 | 192.3 | 1.7 | 869.8 | 831.1 | 854.1 | 843.1 | 809.1 | 740.4 | 642.1 | 808.4 | 716.9 | 761.3 | 695.8 | 776.8 | 742.1 | 376.1 | 360.5 | 376.4 | 356 | 337.2 | 355.1 | 345.8 | 339.4
1201 | 1038 | 467.5 | 187 | 218.5922 | 346.7 | 355.4 | 341.4 | 335 | 417.5 | 55.6 | 19 | 97.9 | 5.2 | 210.4 | 1.9 | 870.7 | 831.6 | 857.2 | 842.6 | 811.6 | 740.6 | 641.1 | 805.4 | 717.2 | 761.9 | 696.4 | 778.7 | 744.1 | 376.2 | 360.1 | 376.1 | 356 | 337.3 | 354.9 | 345.8 | 339.5
1202 | 1039 | 466.6 | 186.64 | 218.1714 | 346.2 | 355 | 340.8 | 334.4 | 413.5 | 55.7 | 19 | 97.9 | 4.7 | 215.5 | 2.1 | 873.8 | 836.1 | 858.8 | 842.7 | 814.6 | 740.9 | 640.8 | 801.7 | 717.8 | 762.6 | 697 | 780.7 | 744.9 | 376.3 | 359.8 | 375.7 | 355.9 | 337.5 | 354.8 | 345.8 | 339.5
1203 | 1040 | 467.3 | 186.92 | 218.4987 | 345.7 | 356 | 340.2 | 333.8 | 410.2 | 55.7 | 19 | 98 | 5.2 | 215.6 | 2.6 | 872.9 | 834.6 | 858.6 | 842.3 | 816.6 | 741.1 | 641.7 | 804 | 718.3 | 763.3 | 697.7 | 782 | 744.3 | 376.4 | 359.5 | 375.3 | 355.8 | 337.6 | 354.5 | 345.7 | 339.6
1204 | 1041 | 468 | 187.2 | 218.826 | 345.3 | 356.2 | 339.3 | 332.7 | 412.4 | 55.7 | 19 | 98.2 | 5.1 | 218.3 | 3.1 | 873.6 | 836.6 | 860.1 | 843 | 818.9 | 741.4 | 642.6 | 803.5 | 718.7 | 763.5 | 698.5 | 779.4 | 742.7 | 376.5 | 359.2 | 375 | 355.7 | 337.7 | 354.2 | 345.6 | 339.6
1205 | 1042 | 467.6 | 187.04 | 218.639 | 344.9 | 356.7 | 338.4 | 331.6 | 418.9 | 55.8 | 19 | 98.2 | 4.5 | 221.4 | 3.1 | 874.9 | 837.1 | 859.9 | 843.8 | 821.1 | 741.6 | 643.4 | 805.2 | 718.9 | 764.5 | 699.1 | 778.9 | 740.8 | 376.6 | 359.2 | 374.9 | 355.8 | 337.8 | 354 | 345.5 | 339.6
1206 | 1043 | 468.1 | 187.24 | 218.8728 | 344.9 | 357.1 | 337.6 | 330.9 | 420 | 55.7 | 19 | 98.1 | 4.7 | 224.5 | 3.2 | 877.6 | 835.5 | 858.9 | 844.4 | 822.8 | 741.8 | 643.2 | 807.4 | 719.2 | 764.8 | 699 | 778.6 | 739 | 376.7 | 359 | 374.6 | 355.8 | 338 | 353.9 | 345.7 | 339.7
1207 | 1044 | 468 | 187.2 | 218.826 | 345 | 356.5 | 337.6 | 330.6 | 414.6 | 55.6 | 19 | 98.2 | 4.4 | 224.7 | 3.2 | 881.7 | 834.2 | 854.6 | 844.4 | 823.3 | 741.8 | 642.6 | 804.8 | 719.7 | 764.8 | 699.2 | 778 | 738.4 | 376.8 | 358.7 | 374.4 | 355.7 | 338.1 | 353.9 | 345.8 | 339.7
1208 | 1045 | 468.7 | 187.48 | 219.1533 | 344.9 | 356.5 | 337.6 | 330.4 | 411.9 | 55.5 | 19 | 98.3 | 4.5 | 218.4 | 3.1 | 880 | 826.2 | 843.8 | 845 | 819.9 | 741.8 | 640.4 | 795.9 | 720.2 | 762.3 | 698.2 | 765.8 | 741.1 | 376.9 | 358.4 | 374.1 | 355.7 | 338.2 | 353.9 | 345.9 | 339.7
1209 | 1046 | 468.6 | 187.44 | 219.1066 | 344.4 | 356.1 | 337.8 | 330.2 | 409.8 | 55.5 | 19 | 98.4 | 4.9 | 213.5 | 3.1 | 880.8 | 820.6 | 838.1 | 844.1 | 819.7 | 741.9 | 640.2 | 788.3 | 721 | 760.2 | 697.5 | 763.2 | 747.1 | 376.9 | 358 | 373.8 | 355.6 | 338.3 | 353.8 | 346.1 | 339.7
1210 | 1047 | 468 | 187.2 | 218.826 | 344.1 | 355.3 | 338.2 | 329.9 | 408.3 | 55.6 | 19 | 98.5 | 4.9 | 216 | 3.4 | 881.4 | 819.9 | 838.5 | 843.5 | 819.3 | 742.2 | 639.4 | 789.2 | 721.8 | 760 | 698.6 | 766.8 | 751.4 | 377 | 357.8 | 373.5 | 355.6 | 338.5 | 353.5 | 345.9 | 339.7
1211 | 1048 | 469.3 | 187.72 | 219.4339 | 345.4 | 354.8 | 337.9 | 329.9 | 408.7 | 55.6 | 19 | 98.4 | 4.8 | 219.2 | 4.1 | 880.1 | 818.9 | 844.2 | 843.3 | 819.7 | 742.3 | 638.6 | 790.3 | 722.5 | 760.1 | 700.2 | 774.4 | 752.2 | 377 | 357.6 | 373.3 | 355.5 | 338.6 | 353.4 | 345.8 | 339.7
1212 | 1049 | 469.8 | 187.92 | 219.6677 | 348.3 | 354.6 | 337.4 | 329.5 | 407.5 | 55.7 | 19 | 98.5 | 4.9 | 230.3 | 4.3 | 881.6 | 822.3 | 851.7 | 842.8 | 823.5 | 742.5 | 639.1 | 792.8 | 723.1 | 760.9 | 702.7 | 780 | 751 | 377.1 | 357.2 | 373.2 | 355.4 | 338.7 | 353.4 | 345.5 | 339.7
1213 | 1050 | 468.7 | 187.48 | 219.1533 | 349.5 | 354.5 | 337.3 | 329.3 | 408.6 | 55.7 | 19 | 98.5 | 4.6 | 230.3 | 4.2 | 879.8 | 823.4 | 855 | 843.6 | 825.4 | 742.7 | 637.7 | 794.5 | 723.9 | 761.6 | 703.8 | 779.3 | 748.6 | 377.2 | 356.8 | 373 | 355.4 | 338.8 | 353.5 | 345.4 | 339.7
1214 | 1051 | 468.6 | 187.44 | 219.1066 | 349 | 354.7 | 337.3 | 329.1 | 407.3 | 55.6 | 19 | 98.6 | 4.9 | 197.7 | 5 | 879.3 | 822.8 | 857.5 | 844.9 | 826 | 742.9 | 636.1 | 791.2 | 724.6 | 761.5 | 704.1 | 780.4 | 746.1 | 377.3 | 356.7 | 372.8 | 355.3 | 339 | 353.5 | 345.5 | 339.8
1215 | 1052 | 468.2 | 187.28 | 218.9195 | 348 | 355 | 337.3 | 329.4 | 408.9 | 55.6 | 19 | 98.6 | 4.4 | 208.3 | 5 | 882.6 | 825 | 860.7 | 845 | 826.6 | 743 | 637.2 | 792.3 | 725.2 | 761.7 | 704 | 781.8 | 747 | 377.4 | 356.5 | 372.6 | 355.3 | 339.1 | 353.5 | 345.7 | 339.9
1216 | 1053 | 467.7 | 187.08 | 218.6857 | 347.7 | 355.2 | 336.8 | 330 | 409.6 | 55.7 | 19 | 98.5 | 4.8 | 221.9 | 5.4 | 884 | 826 | 860.6 | 845.4 | 826.8 | 743.1 | 638.3 | 798.1 | 726 | 763 | 704.5 | 782 | 747.2 | 377.5 | 356.5 | 372.4 | 355.4 | 339.2 | 353.5 | 345.8 | 339.9
1217 | 1054 | 469.3 | 187.72 | 219.4339 | 348 | 355.6 | 336.7 | 330.3 | 418.8 | 55.8 | 19 | 98.5 | 4.8 | 231 | 6.6 | 883.7 | 826.6 | 858 | 845.9 | 827.9 | 743.2 | 635.3 | 797 | 727.4 | 763.1 | 704 | 781.6 | 745.7 | 377.5 | 356.7 | 372.6 | 355.5 | 339.3 | 353.3 | 345.8 | 339.9
1218 | 1055 | 469.3 | 187.72 | 219.4339 | 349 | 356 | 337.3 | 330.7 | 419.9 | 55.9 | 19 | 98.5 | 5.1 | 238.1 | 5.9 | 884.8 | 827.5 | 861.4 | 846.2 | 828 | 743.4 | 635.7 | 799.6 | 728.2 | 763.9 | 703.5 | 781.9 | 745.9 | 377.6 | 356.6 | 372.4 | 355.5 | 339.4 | 353.4 | 345.8 | 339.9
1219 | 1056 | 469.8 | 187.92 | 219.6677 | 350.3 | 356.3 | 337.2 | 331.1 | 415.5 | 56 | 19 | 98.5 | 5 | 203.9 | 5.7 | 882.9 | 825.3 | 859.2 | 846.3 | 827.3 | 743.3 | 631.6 | 793.1 | 729.7 | 762.4 | 702.3 | 777.7 | 746.5 | 377.7 | 356.6 | 372.4 | 355.5 | 339.5 | 353.5 | 345.8 | 339.9
1220 | 1057 | 469.4 | 187.76 | 219.4806 | 350.9 | 356.7 | 336.5 | 331.2 | 418.4 | 56.1 | 19 | 98.5 | 5.3 | 211.4 | 6 | 881.2 | 822.1 | 855.2 | 846.8 | 826.2 | 743.5 | 629.4 | 784.5 | 731.6 | 760.8 | 700.9 | 771.3 | 745.4 | 377.7 | 356.6 | 372.1 | 355.5 | 339.6 | 353.5 | 345.9 | 339.9
1221 | 1058 | 470.3 | 188.12 | 219.9014 | 350.5 | 356.3 | 335.8 | 331.1 | 418.5 | 56.1 | 19 | 98.6 | 5.6 | 232.9 | 6 | 882.3 | 822 | 854.9 | 846.8 | 827 | 743.6 | 631.3 | 782.8 | 733.8 | 759.4 | 700.4 | 769.7 | 746.3 | 377.8 | 356.5 | 371.9 | 355.5 | 339.8 | 353.8 | 346 | 339.9
1222 | 1059 | 467.7 | 187.08 | 218.6857 | 349.7 | 354.9 | 335.5 | 330.6 | 417.2 | 56.1 | 19 | 98.7 | 5.1 | 220.9 | 5.9 | 885.3 | 822.6 | 854.3 | 846.6 | 826.6 | 743.8 | 631.1 | 782.3 | 735.8 | 759.2 | 701.3 | 773.3 | 749.8 | 377.8 | 356.4 | 371.7 | 355.5 | 339.9 | 353.8 | 346.1 | 340
1223 | 1060 | 465.4 | 186.16 | 217.6103 | 350.3 | 354.3 | 335 | 330.9 | 414.6 | 56.1 | 19 | 98.7 | 5.1 | 217.4 | 5.5 | 884.1 | 823.4 | 856.5 | 846.4 | 827.3 | 744.1 | 629.9 | 785.5 | 737.5 | 759.4 | 702.1 | 774.7 | 751.4 | 377.9 | 356.2 | 371.7 | 355.4 | 340 | 353.8 | 346 | 340
1224 | 1061 | 466.4 | 186.56 | 218.0779 | 350.8 | 354.7 | 334.2 | 331.1 | 412.1 | 56 | 19 | 98.7 | 5 | 224.9 | 5.3 | 881.8 | 824.1 | 854.6 | 846.8 | 825.6 | 744.2 | 629.6 | 791.4 | 738.4 | 759.9 | 701.8 | 773.3 | 753.6 | 378 | 356.2 | 371.6 | 355.4 | 340.1 | 353.5 | 345.8 | 340
1225 | 1062 | 467.1 | 186.84 | 218.4052 | 350.8 | 354.8 | 333.6 | 331.2 | 409.3 | 55.9 | 19 | 98.7 | 4.3 | 228.6 | 5.4 | 879.4 | 820.7 | 852.7 | 847.3 | 824.2 | 744.3 | 628.6 | 790.1 | 738.9 | 758.4 | 700.5 | 770.1 | 755.5 | 378 | 356 | 371.5 | 355.3 | 340.2 | 353.3 | 345.6 | 339.9
1226 | 1063 | 468.8 | 187.52 | 219.2001 | 351.9 | 354.4 | 333.3 | 331.3 | 407.5 | 55.9 | 19 | 98.7 | 4.6 | 205.2 | 5.9 | 882.9 | 822.3 | 855.6 | 847.3 | 825.4 | 744.4 | 630.4 | 792.7 | 739 | 760.1 | 702 | 774.5 | 756.8 | 378.1 | 356.1 | 371.4 | 355.3 | 340.4 | 353 | 345.3 | 339.9
1227 | 1064 | 469.7 | 187.88 | 219.6209 | 353.1 | 354.1 | 333 | 331.3 | 406.8 | 55.9 | 19 | 98.8 | 4.6 | 205.5 | 6.6 | 883.1 | 822.3 | 849.6 | 847.7 | 824 | 744.4 | 630.2 | 787.5 | 740.3 | 758.7 | 701.1 | 773.1 | 760.9 | 378.2 | 356.3 | 371.3 | 355.4 | 340.5 | 352.8 | 345.2 | 339.9
1228 | 1065 | 470 | 188 | 219.7612 | 353.5 | 354.2 | 332.6 | 331 | 404.1 | 55.9 | 19 | 98.8 | 4.2 | 222.5 | 7.2 | 883.5 | 822.1 | 851.6 | 847.7 | 824.4 | 744.6 | 629.7 | 788.5 | 741.5 | 758 | 701.7 | 772.8 | 763.7 | 378.2 | 356.3 | 371.2 | 355.4 | 340.6 | 352.6 | 345 | 339.9
1229 | 1066 | 470.1 | 188.04 | 219.8079 | 353.9 | 354.1 | 332.6 | 330.7 | 403.8 | 55.8 | 19 | 98.7 | 4.8 | 203.3 | 7.1 | 886.7 | 821.1 | 850.8 | 846.8 | 826.4 | 744.7 | 628.6 | 790.4 | 742 | 758.8 | 703 | 776.8 | 767.8 | 378.3 | 356.3 | 371 | 355.3 | 340.7 | 352.3 | 344.9 | 339.9
1230 | 1067 | 468.8 | 187.52 | 219.2001 | 355.2 | 353.9 | 332.7 | 330.1 | 401.9 | 55.8 | 19 | 98.7 | 4.8 | 204 | 6.6 | 890.9 | 821.2 | 846.2 | 846.5 | 825.7 | 744.7 | 628.7 | 790.8 | 742.2 | 758.1 | 704.4 | 774.3 | 772.3 | 378.4 | 356.2 | 370.9 | 355.2 | 340.8 | 352.3 | 344.9 | 339.9
1231 | 1068 | 467.3 | 186.92 | 218.4987 | 354.5 | 354 | 332.6 | 329.9 | 401 | 56 | 19 | 98.8 | 4.9 | 210.2 | 6.2 | 893.7 | 821 | 848.4 | 845.5 | 827 | 744.8 | 629.7 | 790.4 | 742.7 | 757.1 | 704.1 | 770.9 | 773.7 | 378.5 | 356.2 | 370.8 | 355.1 | 340.9 | 352.4 | 344.8 | 340
1232 | 1069 | 466.5 | 186.6 | 218.1246 | 353.6 | 353.9 | 332.5 | 330.4 | 400.9 | 56 | 19 | 98.8 | 4.8 | 226.8 | 5.6 | 889.5 | 818.1 | 846.5 | 845.2 | 826.1 | 744.9 | 628.2 | 785.4 | 743.2 | 756.3 | 704.3 | 766.6 | 772.1 | 378.6 | 356.1 | 370.8 | 355 | 341 | 352.4 | 344.7 | 339.9
1233 | 1070 | 467.7 | 187.08 | 218.6857 | 353.7 | 353.7 | 333.4 | 330.7 | 399.1 | 55.8 | 19 | 98.8 | 4.7 | 238.6 | 5.2 | 890.9 | 817.7 | 844.8 | 845 | 823.8 | 745 | 626.1 | 777 | 744.9 | 754.8 | 704 | 763.4 | 771.7 | 378.7 | 355.9 | 370.7 | 355 | 341.1 | 352.3 | 344.7 | 339.9
1234 | 1071 | 467.5 | 187 | 218.5922 | 355 | 353 | 334.3 | 330.7 | 397 | 55.7 | 19 | 98.7 | 5.7 | 212.4 | 5.5 | 887.5 | 815.5 | 841.1 | 845.3 | 821.9 | 745.2 | 624.7 | 770.5 | 746.2 | 753.3 | 704.2 | 764.7 | 773.9 | 378.8 | 355.6 | 370.5 | 354.8 | 341.2 | 352.5 | 344.9 | 340
1235 | 1072 | 467.1 | 186.84 | 218.4052 | 356.1 | 352.5 | 334.6 | 330.7 | 395 | 55.6 | 19 | 98.6 | 5.2 | 202.8 | 6.6 | 881.8 | 806.9 | 836.7 | 845.4 | 819.2 | 745.4 | 626.9 | 757.4 | 748.8 | 750.2 | 703.8 | 753.1 | 773.4 | 378.9 | 355.3 | 370.2 | 354.6 | 341.3 | 352.7 | 345.4 | 340.1
1236 | 1073 | 467.5 | 187 | 218.5922 | 357 | 352 | 334.1 | 331.1 | 393.8 | 55.5 | 19 | 98.6 | 5.6 | 212.9 | 7 | 881.3 | 806.2 | 835.1 | 845.1 | 818.4 | 745.7 | 629.8 | 755.5 | 751.4 | 748.8 | 704.9 | 746.1 | 770.7 | 379 | 355.1 | 370 | 354.5 | 341.4 | 353 | 345.7 | 340.3
1237 | 1074 | 467.3 | 186.92 | 218.4987 | 359.1 | 351.5 | 333.4 | 332.5 | 393.5 | 55.6 | 19 | 98.7 | 5.9 | 206.7 | 6.9 | 880.7 | 803.5 | 836.3 | 844.5 | 819 | 745.8 | 628.4 | 750.2 | 753.1 | 746.4 | 705.6 | 743.4 | 771.2 | 379.1 | 354.9 | 369.8 | 354.4 | 341.5 | 353.2 | 345.9 | 340.4
1238 | 1075 | 467 | 186.8 | 218.3584 | 361.4 | 351.3 | 333.9 | 333.5 | 393.9 | 55.7 | 19 | 98.6 | 4.9 | 210.6 | 6.9 | 882.4 | 801.8 | 841.1 | 843.5 | 821 | 746 | 628.6 | 752.1 | 754.2 | 746.1 | 707.3 | 747.6 | 773.9 | 379.2 | 354.9 | 369.5 | 354.4 | 341.6 | 353.3 | 346 | 340.4
1239 | 1076 | 468.2 | 187.28 | 218.9195 | 362.6 | 350.9 | 334.2 | 333.8 | 393.8 | 55.7 | 19 | 98.6 | 4.7 | 225.3 | 6.4 | 880.9 | 804 | 842.5 | 843.1 | 823.6 | 746.2 | 630 | 757.8 | 754.6 | 746.3 | 708.9 | 751.9 | 771.5 | 379.3 | 354.8 | 369.6 | 354.3 | 341.8 | 353.6 | 346.3 | 340.5
1240 | 1077 | 468.5 | 187.4 | 219.0598 | 363.8 | 351.2 | 334.2 | 334 | 393.6 | 55.7 | 19 | 98.6 | 5.2 | 227.5 | 5.9 | 877.6 | 803.5 | 842.6 | 843.2 | 825.2 | 746.3 | 630.6 | 758 | 755.3 | 746.6 | 709.6 | 750.4 | 766.8 | 379.4 | 354.9 | 369.6 | 354.4 | 341.9 | 353.7 | 346.5 | 340.6
1241 | 1078 | 468.3 | 187.32 | 218.9663 | 364.4 | 352.2 | 334.6 | 334.7 | 395.7 | 55.8 | 19 | 98.7 | 5.3 | 207.4 | 6.6 | 875.1 | 804.2 | 846.3 | 843.4 | 825.1 | 746.3 | 629.2 | 760 | 756.5 | 745.9 | 708.6 | 746.2 | 762.2 | 379.4 | 355.1 | 369.7 | 354.6 | 342 | 353.7 | 346.3 | 340.5
1242 | 1079 | 467.9 | 187.16 | 218.7793 | 363.7 | 353 | 334.4 | 335.1 | 396.7 | 55.9 | 19 | 98.7 | 5.5 | 217.3 | 6.9 | 877.2 | 807.7 | 853.4 | 843.3 | 827.3 | 746.3 | 629.4 | 771.1 | 756.7 | 747.4 | 708.3 | 751 | 761.2 | 379.5 | 355.3 | 369.8 | 354.8 | 342.1 | 353.8 | 346.2 | 340.5
1243 | 1080 | 468.4 | 187.36 | 219.013 | 363.5 | 353.2 | 334.2 | 334.8 | 397.5 | 56 | 19 | 98.8 | 5 | 217 | 6.8 | 879.9 | 810.3 | 857.3 | 842.9 | 828.4 | 746.2 | 627.6 | 774.4 | 756.5 | 747.7 | 707.7 | 754.4 | 762 | 379.6 | 355.3 | 369.7 | 354.8 | 342.2 | 353.8 | 346.4 | 340.5
1244 | 1081 | 468.6 | 187.44 | 219.1066 | 364.1 | 353.5 | 333.7 | 334.9 | 399.3 | 56.1 | 19 | 98.8 | 4.5 | 223.2 | 6.3 | 879.1 | 808.8 | 856.6 | 843.1 | 829.3 | 745.9 | 624.7 | 773.1 | 756.7 | 746.2 | 705.6 | 746.9 | 762.7 | 379.7 | 355.4 | 369.6 | 354.8 | 342.3 | 353.6 | 346.5 | 340.5
1245 | 1082 | 468.2 | 187.28 | 218.9195 | 366.1 | 353.3 | 333.6 | 334.7 | 398 | 56.2 | 19 | 98.9 | 4.7 | 260.7 | 5.6 | 878.5 | 805.9 | 855.8 | 843 | 827.5 | 745.9 | 622.3 | 762.4 | 757.7 | 743.5 | 703.6 | 736.1 | 766.3 | 379.7 | 355.3 | 369.7 | 354.8 | 342.4 | 353.5 | 346.4 | 340.5
1246 | 1083 | 468 | 187.2 | 218.826 | 365.8 | 353.3 | 334 | 334.3 | 397.3 | 56.1 | 19 | 98.8 | 5 | 288.3 | 4.9 | 877.6 | 805.1 | 853.3 | 843.1 | 824.8 | 746 | 621.8 | 758.2 | 759 | 741.4 | 702.6 | 730.6 | 769.2 | 379.8 | 355.3 | 369.8 | 354.8 | 342.5 | 353.4 | 346.2 | 340.5
1247 | 1084 | 469 | 187.6 | 219.2936 | 364.3 | 352.9 | 334.6 | 334.1 | 396.1 | 56.1 | 19 | 98.8 | 5.4 | 277.1 | 4.2 | 871 | 799 | 846.5 | 843.2 | 819.5 | 746.1 | 622.1 | 747.8 | 760.3 | 738.3 | 702.2 | 721.4 | 773.3 | 379.9 | 355.2 | 369.7 | 354.8 | 342.6 | 353.3 | 346.2 | 340.4
1248 | 1085 | 468.9 | 187.56 | 219.2468 | 362.7 | 352.5 | 334.6 | 333.6 | 394.6 | 56.1 | 19 | 98.7 | 5.3 | 238.7 | 4.4 | 870.7 | 799 | 839.3 | 842.9 | 816.3 | 746.3 | 621 | 757.1 | 761.6 | 737.9 | 702.2 | 720.7 | 778.1 | 380 | 355 | 369.6 | 354.7 | 342.8 | 353.3 | 346.1 | 340.4
1249 | 1086 | 468.7 | 187.48 | 219.1533 | 363.2 | 352.1 | 334.5 | 333.3 | 393.1 | 56.2 | 19 | 98.6 | 4.8 | 217.2 | 3.9 | 871.1 | 801.7 | 836.6 | 842.2 | 815 | 746.4 | 617.2 | 757.1 | 762.7 | 736.6 | 702 | 724.7 | 783.7 | 380 | 354.9 | 369.4 | 354.6 | 342.9 | 353.2 | 346 | 340.4
1250 | 1087 | 468.9 | 187.56 | 219.2468 | 362.8 | 352 | 334.2 | 333 | 392.9 | 56.3 | 19 | 98.6 | 4.5 | 210 | 3.2 | 876.1 | 804.3 | 834 | 841.3 | 814 | 746.5 | 615.4 | 756.3 | 764 | 736.8 | 702.9 | 735.5 | 786.6 | 380.1 | 354.8 | 369.3 | 354.5 | 343 | 353.2 | 346 | 340.4
1251 | 1088 | 469 | 187.6 | 219.2936 | 363.7 | 351.6 | 334.2 | 332.6 | 394 | 56.4 | 19 | 98.6 | 4.4 | 209.5 | 3.1 | 869.3 | 801.3 | 822.2 | 840.6 | 808.4 | 746.5 | 619.7 | 759.7 | 765.2 | 735.6 | 702.9 | 728.6 | 786.9 | 380.2 | 354.8 | 369.3 | 354.6 | 343.1 | 353.2 | 345.9 | 340.4
1252 | 1089 | 469 | 187.6 | 219.2936 | 364.7 | 351.6 | 334.5 | 331.9 | 394 | 56.4 | 19 | 98.6 | 4.3 | 225.4 | 3.4 | 869.9 | 802.4 | 820.9 | 839.5 | 806.2 | 746.6 | 616.5 | 756.5 | 766.2 | 733.4 | 702.6 | 729.8 | 788.7 | 380.2 | 354.8 | 369.5 | 354.6 | 343.2 | 353.2 | 345.9 | 340.4
1253 | 1090 | 468.7 | 187.48 | 219.1533 | 365 | 351.1 | 334.4 | 331.1 | 393.5 | 56.3 | 19 | 98.6 | 4.7 | 240.8 | 3.2 | 876.4 | 805.4 | 826.5 | 838.3 | 807 | 746.8 | 616.8 | 761.8 | 766.3 | 735.9 | 703.8 | 744 | 789 | 380.3 | 354.8 | 369.5 | 354.6 | 343.3 | 353.2 | 345.9 | 340.4
1254 | 1091 | 468.5 | 187.4 | 219.0598 | 364.4 | 350.8 | 334.8 | 330.8 | 395.1 | 56.3 | 19 | 98.7 | 4.9 | 219.6 | 2.8 | 871.3 | 803.8 | 822.9 | 838.1 | 803.7 | 746.6 | 617.6 | 762.4 | 766 | 734.5 | 702.1 | 739.7 | 785.8 | 380.4 | 355.1 | 369.7 | 354.7 | 343.4 | 353.4 | 346.1 | 340.4
1255 | 1092 | 468.1 | 187.24 | 218.8728 | 365.3 | 350.6 | 334.9 | 330.9 | 396 | 56.3 | 19 | 98.7 | 4.7 | 200.3 | 2.6 | 860.7 | 801.1 | 812.1 | 838.1 | 798 | 746.6 | 619.7 | 765.2 | 766.3 | 734.3 | 701.3 | 732.8 | 785 | 380.4 | 355.4 | 370 | 354.8 | 343.5 | 353.5 | 346.1 | 340.5
1256 | 1093 | 468.6 | 187.44 | 219.1066 | 367 | 350.6 | 335.2 | 331.2 | 396.4 | 56.4 | 18.9 | 98.8 | 4.3 | 195.3 | 2.3 | 854.9 | 794.1 | 804.4 | 837.6 | 793.4 | 746.6 | 617.8 | 751.9 | 767.5 | 731 | 699.6 | 717.7 | 783.4 | 380.5 | 355.6 | 370.3 | 355 | 343.6 | 353.5 | 346.2 | 340.5
1257 | 1094 | 468.3 | 187.32 | 218.9663 | 367.8 | 350.3 | 335.5 | 331.3 | 400.3 | 56.5 | 18.9 | 98.8 | 4.6 | 194.8 | 2.3 | 852.3 | 791.7 | 809.1 | 837.1 | 790 | 746.7 | 614 | 752.5 | 768 | 730.8 | 699 | 713.9 | 779.8 | 380.5 | 355.8 | 370.8 | 355.2 | 343.7 | 353.6 | 346.1 | 340.5
1258 | 1095 | 467.5 | 187 | 218.5922 | 368.1 | 351.3 | 336.8 | 332 | 401.2 | 56.5 | 18.9 | 98.8 | 4.6 | 197.3 | 3.3 | 849.7 | 785.1 | 798.6 | 836.3 | 785.3 | 746.8 | 609 | 743.5 | 768.6 | 728.1 | 697.8 | 704.4 | 780 | 380.6 | 356 | 371.2 | 355.2 | 343.8 | 353.9 | 346 | 340.5
1259 | 1096 | 467.6 | 187.04 | 218.639 | 368.5 | 352.7 | 338.1 | 333 | 400.3 | 56.4 | 18.9 | 98.8 | 5 | 205.2 | 4.9 | 843.9 | 779.2 | 796.3 | 834.8 | 781.8 | 746.9 | 607.3 | 733.1 | 769.7 | 725.3 | 696.5 | 696.2 | 778.5 | 380.6 | 356.6 | 371.7 | 355.5 | 343.9 | 354.2 | 346.1 | 340.5
1260 | 1097 | 467.4 | 186.96 | 218.5455 | 369 | 353.3 | 338.7 | 333.7 | 400.8 | 56.4 | 18.9 | 98.9 | 4.4 | 212.1 | 6 | 843.4 | 779.9 | 798 | 833.6 | 779.2 | 747.1 | 603.4 | 730.7 | 771.6 | 724.1 | 696.1 | 696.8 | 776 | 380.7 | 357.2 | 372.5 | 355.8 | 344 | 354.3 | 346.2 | 340.5
1261 | 1098 | 469.1 | 187.64 | 219.3403 | 370.2 | 353.4 | 339 | 333.8 | 404.1 | 56.5 | 19 | 99 | 4.6 | 218.8 | 6.7 | 843.2 | 787 | 807.4 | 832.7 | 778.3 | 747.3 | 604.6 | 737.6 | 772.6 | 725.3 | 697.1 | 706.1 | 770.8 | 380.8 | 357.9 | 373.3 | 356 | 344.1 | 354.6 | 346.2 | 340.5
1262 | 1099 | 469.4 | 187.76 | 219.4806 | 369 | 352.4 | 339.5 | 334.3 | 406.5 | 56.5 | 19 | 99.1 | 4.6 | 210.2 | 7.4 | 845.7 | 793.9 | 819.4 | 832.3 | 782 | 747.4 | 607 | 753.4 | 772.5 | 727.7 | 696.8 | 718.4 | 767.8 | 380.9 | 358.2 | 373.7 | 355.9 | 344.2 | 355 | 346.3 | 340.6
1263 | 1100 | 469.3 | 187.72 | 219.4339 | 368.5 | 353.2 | 340.1 | 335.6 | 406.9 | 56.6 | 19 | 99.3 | 4.3 | 190.6 | 7.6 | 845.7 | 798 | 815.4 | 831.9 | 778.8 | 747.3 | 609.9 | 763.4 | 771.4 | 729.2 | 697.4 | 725.2 | 767 | 380.9 | 358.8 | 374 | 355.9 | 344.4 | 355.2 | 346.4 | 340.6
1264 | 1101 | 469 | 187.6 | 219.2936 | 368.4 | 354.5 | 340.1 | 336.3 | 406.9 | 56.7 | 19 | 99.4 | 4.8 | 190.1 | 7.6 | 842.6 | 797.4 | 807.2 | 831.7 | 775.7 | 747.1 | 612.1 | 761.1 | 770.7 | 728.2 | 696.7 | 719.1 | 766.6 | 381 | 359.2 | 374.2 | 356 | 344.5 | 355.4 | 346.5 | 340.7
1265 | 1102 | 469.6 | 187.84 | 219.5741 | 369 | 355.7 | 340.4 | 336.5 | 408.2 | 56.7 | 18.9 | 99.6 | 4.3 | 180.8 | 7.2 | 834.4 | 791.8 | 798.4 | 831.6 | 770.3 | 747.1 | 615.8 | 753.5 | 771.4 | 726.4 | 695.5 | 710.9 | 763 | 381.1 | 359.9 | 374.8 | 356.4 | 344.6 | 355.7 | 346.5 | 340.7
1266 | 1103 | 469.3 | 187.72 | 219.4339 | 369.1 | 357.6 | 340.8 | 336.5 | 408.7 | 56.8 | 18.9 | 99.5 | 4.1 | 193.6 | 6.7 | 825 | 779.9 | 790.4 | 831.3 | 765.1 | 747.3 | 613.8 | 737.3 | 772.3 | 722 | 694.3 | 692.4 | 759.7 | 381.2 | 360.5 | 375.7 | 356.7 | 344.7 | 356 | 346.6 | 340.7
1267 | 1104 | 469 | 187.6 | 219.2936 | 370 | 357.9 | 341.9 | 337.3 | 408.4 | 56.8 | 18.9 | 99.5 | 4.3 | 208.1 | 6.6 | 827.1 | 779.7 | 797.2 | 830.9 | 765.3 | 747.3 | 611.2 | 731.8 | 773.6 | 721 | 693.7 | 693.7 | 757.3 | 381.3 | 360.7 | 376.1 | 356.7 | 344.8 | 356.2 | 346.7 | 340.7
1268 | 1105 | 469.1 | 187.64 | 219.3403 | 370.7 | 357 | 342.8 | 338.2 | 408.1 | 56.8 | 18.9 | 99.4 | 4.7 | 210.9 | 6.5 | 833.6 | 779.9 | 798.6 | 829.4 | 764 | 747.5 | 607.7 | 723.6 | 774.9 | 718.2 | 692.9 | 690.3 | 757.1 | 381.4 | 361.1 | 376.6 | 356.8 | 344.9 | 356.5 | 346.7 | 340.8
1269 | 1106 | 469.3 | 187.72 | 219.4339 | 370 | 356.1 | 343.6 | 338.8 | 408.7 | 56.8 | 18.9 | 99.4 | 4.5 | 210.3 | 6.8 | 832.8 | 777.3 | 798.5 | 828.2 | 763 | 747.7 | 605 | 715.5 | 776.3 | 716.2 | 692.4 | 685.5 | 756.9 | 381.5 | 361.5 | 376.9 | 357 | 345 | 357 | 346.9 | 340.8
1270 | 1107 | 468 | 187.2 | 218.826 | 369.6 | 358.1 | 343.9 | 339.4 | 412.1 | 56.7 | 18.9 | 99.3 | 4.6 | 207.9 | 7 | 827.7 | 775.7 | 800.7 | 827.3 | 762.1 | 747.8 | 606.3 | 714.8 | 777.5 | 714.7 | 691.9 | 683.9 | 753.1 | 381.6 | 361.9 | 377.4 | 357.1 | 345.2 | 357.4 | 347.3 | 340.9
1271 | 1108 | 469.2 | 187.68 | 219.3871 | 369.4 | 360.2 | 344.1 | 340.2 | 415.7 | 56.6 | 18.9 | 99.4 | 4.9 | 204.3 | 7 | 833.8 | 780.5 | 814.2 | 825.8 | 765.5 | 747.8 | 603.5 | 723.7 | 778.4 | 715.8 | 691.7 | 694.2 | 748.3 | 381.7 | 362.2 | 377.6 | 357.2 | 345.3 | 357.8 | 347.6 | 341
1272 | 1109 | 468.7 | 187.48 | 219.1533 | 368.4 | 359.7 | 344.7 | 341.3 | 420.3 | 56.6 | 18.9 | 99.5 | 4.2 | 206.8 | 6.9 | 838.5 | 785.7 | 814 | 824.5 | 765.7 | 747.6 | 601 | 731 | 778.5 | 716.5 | 691.7 | 704 | 747.9 | 381.8 | 362.1 | 377.6 | 357 | 345.4 | 357.8 | 347.8 | 341.1
1273 | 1110 | 469.1 | 187.64 | 219.3403 | 367.7 | 359.2 | 344.8 | 342.1 | 419.3 | 56.5 | 18.9 | 99.6 | 4.2 | 206.1 | 6.6 | 844.4 | 789.3 | 804.2 | 822.7 | 765 | 747.4 | 600.6 | 728 | 778.6 | 715.4 | 691 | 711.1 | 754.2 | 381.9 | 362 | 377.7 | 356.7 | 345.6 | 357.9 | 347.9 | 341.2
1274 | 1111 | 468.7 | 187.48 | 219.1533 | 367.3 | 358.9 | 344.8 | 341.8 | 417 | 56.4 | 18.9 | 99.8 | 4.8 | 202.5 | 6.2 | 843 | 790.4 | 801.5 | 821.5 | 764.6 | 747.3 | 599.9 | 723.7 | 778.7 | 713.3 | 690 | 709 | 763.2 | 382 | 361.7 | 377.5 | 356.5 | 345.7 | 358.1 | 348 | 341.2
1275 | 1112 | 468.9 | 187.56 | 219.2468 | 369.1 | 359 | 344.4 | 341.4 | 414.2 | 56.4 | 18.9 | 99.9 | 5.1 | 202.7 | 6.3 | 836 | 791.1 | 801.3 | 821.1 | 763.1 | 747.3 | 600.3 | 725.8 | 778.9 | 713 | 689.4 | 708.8 | 767.5 | 382.2 | 361.6 | 377.3 | 356.5 | 345.8 | 357.8 | 348 | 341.3
1276 | 1113 | 468.5 | 187.4 | 219.0598 | 370.9 | 359 | 344.1 | 340.9 | 413.5 | 56.5 | 18.9 | 100 | 4.9 | 201.2 | 6.2 | 830.5 | 787.9 | 797 | 820.8 | 759.1 | 747.2 | 604.2 | 723.6 | 779.2 | 711.4 | 688.8 | 699.4 | 765.8 | 382.3 | 361.6 | 377.3 | 356.6 | 345.9 | 357.5 | 347.9 | 341.2
1277 | 1114 | 468.6 | 187.44 | 219.1066 | 372.4 | 358.7 | 344 | 340.2 | 413.7 | 56.5 | 18.9 | 100.1 | 4.9 | 206.9 | 5.9 | 827.8 | 788 | 798.1 | 820.7 | 757.2 | 747.2 | 608.2 | 727.1 | 779 | 711.3 | 689.1 | 694.4 | 762.8 | 382.4 | 361.7 | 377.6 | 356.8 | 346.1 | 357.4 | 347.8 | 341.2
1278 | 1115 | 467.5 | 187 | 218.5922 | 373.6 | 357.9 | 343.4 | 339.8 | 413 | 56.7 | 18.9 | 100.1 | 4.7 | 203.6 | 5.1 | 836.3 | 793.6 | 806.1 | 819.4 | 760 | 747.1 | 611.2 | 737.9 | 778.2 | 713.4 | 689.8 | 703.8 | 760.8 | 382.5 | 361.5 | 377.6 | 356.7 | 346.2 | 357.5 | 347.6 | 341.3
1279 | 1116 | 468.5 | 187.4 | 219.0598 | 373.1 | 357.1 | 343.1 | 339.5 | 412.5 | 56.8 | 18.9 | 100 | 4.8 | 164.1 | 4.4 | 846.4 | 801.7 | 816 | 818.7 | 763.1 | 746.9 | 614.3 | 752.1 | 777.1 | 717 | 690.9 | 720.5 | 758.8 | 382.6 | 361.3 | 377.6 | 356.6 | 346.3 | 357.4 | 347.5 | 341.3
1280 | 1117 | 468.4 | 187.36 | 219.013 | 372.2 | 356.6 | 343.1 | 339.4 | 410.9 | 56.8 | 18.9 | 100.1 | 4.9 | 154 | 4.1 | 852.9 | 806.9 | 821.7 | 817.7 | 764.3 | 746.7 | 614.7 | 755.3 | 776.2 | 717.6 | 691.2 | 730.2 | 758.1 | 382.7 | 361.2 | 377.7 | 356.6 | 346.4 | 357.3 | 347.4 | 341.3
1281 | 1118 | 468.5 | 187.4 | 219.0598 | 372.6 | 356.5 | 343 | 340 | 408.5 | 57 | 18.9 | 100.2 | 4.6 | 195.9 | 3.9 | 852.6 | 808.5 | 827.5 | 818 | 766.7 | 746.4 | 617.3 | 760.3 | 775 | 719 | 690.5 | 732.1 | 757.9 | 382.8 | 361.4 | 377.7 | 356.7 | 346.6 | 357.2 | 347.5 | 341.4
1282 | 1119 | 469.4 | 187.76 | 219.4806 | 373.4 | 356.9 | 342.7 | 339.9 | 408.8 | 57.1 | 18.9 | 100.2 | 4.4 | 201.7 | 4.4 | 849.2 | 808.7 | 827.1 | 818.1 | 768.7 | 746.2 | 618.2 | 764.8 | 774.1 | 720.1 | 690 | 731.3 | 757 | 382.8 | 361.5 | 377.6 | 356.8 | 346.7 | 357.1 | 347.5 | 341.4
1283 | 1120 | 469.7 | 187.88 | 219.6209 | 374.4 | 357.7 | 342 | 339.8 | 412.6 | 57.2 | 18.9 | 100.1 | 5 | 169 | 5 | 842.8 | 804.7 | 818.1 | 817.8 | 765.3 | 745.9 | 621.6 | 762.9 | 773.1 | 719.8 | 688.8 | 717.2 | 753 | 382.9 | 361.7 | 377.8 | 357 | 346.8 | 357.1 | 347.5 | 341.4
1284 | 1121 | 469.9 | 187.96 | 219.7144 | 375 | 358.2 | 341.1 | 339.9 | 413.3 | 57.3 | 18.9 | 100.1 | 4.9 | 164 | 4.4 | 839.9 | 801.9 | 814.1 | 818.1 | 764.3 | 745.7 | 621.2 | 759.2 | 772.5 | 718.7 | 687.9 | 710.8 | 752.4 | 383 | 361.8 | 378.2 | 357 | 346.9 | 357 | 347.5 | 341.5
1285.1 | 1122.1 | 469 | 187.6 | 219.2936 | 373.4 | 357.7 | 340.7 | 340.2 | 411.5 | 57.4 | 18.9 | 100.1 | 5.2 | 175.3 | 4.2 | 843.5 | 808.3 | 818.3 | 818.4 | 766.1 | 745.7 | 619.6 | 768.2 | 772 | 720.3 | 687.4 | 718.4 | 751.8 | 383.1 | 361.9 | 378.2 | 356.9 | 347 | 357 | 347.4 | 341.5
1286.1 | 1123.1 | 467 | 186.8 | 218.3584 | 373.7 | 357.9 | 341.7 | 340.4 | 410.1 | 57.4 | 18.9 | 100.1 | 4.8 | 189.9 | 4.3 | 847.7 | 812.1 | 822.2 | 817.9 | 768.4 | 745.6 | 618.1 | 771.9 | 771.7 | 721 | 687.2 | 725.6 | 754 | 383.2 | 362 | 378.6 | 356.9 | 347.1 | 357.2 | 347.4 | 341.6
1287.1 | 1124.1 | 467.3 | 186.92 | 218.4987 | 374.3 | 357.8 | 342.4 | 340.4 | 408.3 | 57.5 | 18.9 | 100.1 | 4.8 | 197.1 | 4.2 | 853.1 | 817.8 | 825.7 | 817.5 | 770.2 | 745.6 | 619.8 | 776 | 771.8 | 722.3 | 687.3 | 734.7 | 757.8 | 383.3 | 362.2 | 378.8 | 356.8 | 347.3 | 357.3 | 347.6 | 341.7
1288.1 | 1125.1 | 467.5 | 187 | 218.5922 | 372.1 | 357.1 | 342.7 | 340.4 | 405.8 | 57.5 | 18.9 | 100.1 | 4.9 | 193.2 | 3.9 | 855.5 | 821.1 | 825.8 | 818.1 | 770.7 | 745.5 | 621 | 778.8 | 771.7 | 723.6 | 687.5 | 737.4 | 762.2 | 383.4 | 362.1 | 378.8 | 356.7 | 347.4 | 357.4 | 347.8 | 341.7
1289.1 | 1126.1 | 467.7 | 187.08 | 218.6857 | 372.1 | 356.7 | 343.2 | 339.7 | 403.5 | 57.4 | 18.9 | 100 | 4.9 | 180.9 | 3.5 | 856 | 823.6 | 830.2 | 818 | 773.8 | 745.5 | 622.1 | 777.8 | 771.6 | 723.9 | 688 | 741.8 | 764.6 | 383.5 | 362.1 | 378.5 | 356.7 | 347.5 | 357.4 | 348 | 341.8
1290.1 | 1127.1 | 467.5 | 187 | 218.5922 | 373.2 | 356.9 | 343.4 | 338.5 | 404 | 57.2 | 18.9 | 100 | 4.8 | 173.2 | 3.2 | 859.4 | 824.7 | 833.3 | 817.7 | 775.5 | 745.4 | 619 | 778.1 | 771 | 724.4 | 687.8 | 740 | 761.5 | 383.6 | 362 | 378.4 | 356.7 | 347.6 | 357.1 | 347.9 | 341.9
1291.1 | 1128.1 | 466.7 | 186.68 | 218.2182 | 373.4 | 357.8 | 343.4 | 337.5 | 404.1 | 57.1 | 18.9 | 99.9 | 4.8 | 190.7 | 3.4 | 861.5 | 816.2 | 830.3 | 817.8 | 776 | 745.3 | 615.5 | 763.2 | 771.1 | 722.1 | 687.6 | 730.3 | 761.9 | 383.7 | 361.9 | 378.1 | 356.6 | 347.7 | 356.9 | 348 | 341.9
1292.1 | 1129.1 | 468.1 | 187.24 | 218.8728 | 373.4 | 358.5 | 343 | 336.7 | 401.9 | 57.1 | 18.9 | 99.7 | 5 | 192.9 | 4.2 | 857.4 | 805.9 | 824.2 | 817.6 | 774.4 | 745.4 | 613.1 | 747.9 | 772.2 | 718.5 | 686.6 | 718.6 | 765 | 383.8 | 361.6 | 377.5 | 356.5 | 347.8 | 356.6 | 347.9 | 341.9
1293.1 | 1130.1 | 467.7 | 187.08 | 218.6857 | 374.3 | 358.5 | 342.1 | 336.1 | 399.8 | 57 | 18.9 | 99.7 | 5 | 193.4 | 5.1 | 853 | 799.3 | 814.9 | 816.8 | 773.8 | 745.5 | 609.8 | 738 | 773.1 | 716.3 | 686.4 | 713 | 768.9 | 383.9 | 361.1 | 376.9 | 356.4 | 347.9 | 356.2 | 347.8 | 342
1294.1 | 1131.1 | 467.9 | 187.16 | 218.7793 | 374.9 | 358.5 | 341 | 336 | 397.8 | 57 | 18.9 | 99.7 | 4.7 | 198.9 | 5.9 | 854.7 | 795 | 806.7 | 815.8 | 773.6 | 745.8 | 605.5 | 725.4 | 774.2 | 713 | 686.1 | 708.9 | 770.6 | 384 | 360.4 | 376.3 | 356.1 | 348 | 355.9 | 347.6 | 342
1295.1 | 1132.1 | 468.1 | 187.24 | 218.8728 | 375 | 357.4 | 340.9 | 335.6 | 395.8 | 57 | 18.9 | 99.7 | 4.8 | 199.5 | 5.8 | 852.6 | 788.6 | 800.3 | 815.6 | 771.7 | 745.9 | 603.7 | 714.2 | 775.3 | 710.6 | 686.3 | 702.6 | 776.1 | 384.1 | 359.9 | 375.6 | 355.9 | 348.1 | 355.6 | 347.7 | 342
1296.1 | 1133.1 | 467.7 | 187.08 | 218.6857 | 374.7 | 356.2 | 341.3 | 335.1 | 393.8 | 57 | 18.9 | 99.7 | 4.6 | 212.4 | 5.4 | 849.8 | 779.4 | 794 | 814.1 | 770.3 | 746.1 | 602.6 | 699.7 | 776.6 | 706.9 | 686 | 690.8 | 780.7 | 384.2 | 359.4 | 375.1 | 355.7 | 348.2 | 355.3 | 347.7 | 342.1
1297.1 | 1134.1 | 468.4 | 187.36 | 219.013 | 374.9 | 354.8 | 340.9 | 334.2 | 391.9 | 57 | 18.9 | 99.8 | 5.1 | 176.8 | 4.7 | 850 | 781.6 | 797.2 | 812.3 | 770.8 | 746.4 | 600.7 | 700.6 | 777.4 | 705.4 | 686.5 | 692.9 | 781.1 | 384.3 | 359 | 374.5 | 355.5 | 348.3 | 355.2 | 347.7 | 342.1
1298.1 | 1135.1 | 467.6 | 187.04 | 218.639 | 374 | 353.5 | 340.6 | 333.8 | 390.8 | 56.9 | 18.9 | 99.9 | 5.4 | 164.6 | 4 | 851.1 | 783.6 | 797.8 | 812 | 771.7 | 746.5 | 599.8 | 701.1 | 777.5 | 704.2 | 687.7 | 698.3 | 783.4 | 384.3 | 358.6 | 373.9 | 355.4 | 348.4 | 354.9 | 347.5 | 342.1
1299.1 | 1136.1 | 468.2 | 187.28 | 218.9195 | 374.3 | 352.5 | 340.3 | 333.5 | 390.1 | 56.9 | 18.9 | 100 | 5.3 | 201.3 | 3.9 | 852 | 789.8 | 799 | 811.1 | 772 | 746.4 | 602.5 | 712.8 | 776.8 | 705.2 | 689.1 | 707.7 | 783.7 | 384.4 | 358.2 | 373.5 | 355.3 | 348.5 | 354.7 | 347.4 | 342.1
1300.1 | 1137.1 | 468.5 | 187.4 | 219.0598 | 374.1 | 351.6 | 340 | 333.1 | 389.9 | 57 | 18.9 | 100.1 | 5.7 | 215.2 | 4.8 | 854.4 | 799.3 | 807.8 | 810.1 | 775.7 | 746.3 | 604.7 | 724.6 | 775.8 | 707.2 | 690.6 | 717.2 | 782.7 | 384.5 | 357.9 | 373.2 | 355.3 | 348.5 | 354.5 | 347.1 | 342.1
1301.1 | 1138.1 | 468 | 187.2 | 218.826 | 372.9 | 351.7 | 339.8 | 332.7 | 389.2 | 56.9 | 18.9 | 100.2 | 5.9 | 209.3 | 5.3 | 857.6 | 802.9 | 815.3 | 810.2 | 778.1 | 746 | 603.2 | 724.6 | 775 | 706.7 | 691.8 | 716.4 | 784.4 | 384.5 | 357.6 | 372.8 | 355.3 | 348.6 | 354.2 | 346.8 | 342
1302.1 | 1139.1 | 467.7 | 187.08 | 218.6857 | 373.2 | 351.4 | 339.8 | 332.5 | 388.2 | 56.8 | 18.9 | 100.3 | 5.8 | 212.6 | 5.4 | 861.2 | 808.9 | 816.1 | 810.6 | 779.3 | 745.9 | 604.8 | 732 | 774.7 | 708 | 692.1 | 721.4 | 782.2 | 384.6 | 357.4 | 372.3 | 355.3 | 348.7 | 354.2 | 346.7 | 342
1303.1 | 1140.1 | 467.6 | 187.04 | 218.639 | 372.9 | 350.9 | 339.5 | 331.9 | 387.1 | 56.9 | 18.9 | 100.4 | 6.2 | 201.5 | 5 | 861.9 | 811 | 819.2 | 811.2 | 780.1 | 745.6 | 601 | 733.5 | 774.2 | 707.7 | 691.6 | 720.9 | 776.7 | 384.6 | 357.2 | 371.8 | 355.3 | 348.8 | 354 | 346.6 | 342
1304.1 | 1141.1 | 467.8 | 187.12 | 218.7325 | 372.5 | 350.8 | 338.5 | 331.4 | 390.6 | 57.1 | 18.9 | 100.5 | 5.8 | 206.4 | 4.4 | 860.7 | 813.4 | 816.6 | 811.9 | 779.8 | 745.4 | 600.6 | 741.9 | 774.2 | 709.1 | 692 | 726.4 | 772.6 | 384.7 | 356.8 | 371.3 | 355.2 | 348.9 | 354 | 346.4 | 341.8
1305.1 | 1142.1 | 468.4 | 187.36 | 219.013 | 372.2 | 350.8 | 337.9 | 330.5 | 392.1 | 57.2 | 18.9 | 100.5 | 5.5 | 217.2 | 4.4 | 853.7 | 813.4 | 809.5 | 812.5 | 776.8 | 745.1 | 603.7 | 754.2 | 773.8 | 710.3 | 691.7 | 719.5 | 770.6 | 384.7 | 356.6 | 371 | 355.3 | 348.9 | 354.1 | 346.2 | 341.8
1306.1 | 1143.1 | 468.3 | 187.32 | 218.9663 | 370.6 | 350.2 | 337.6 | 329.8 | 394.9 | 57.3 | 18.9 | 100.7 | 6 | 210.1 | 4.8 | 855.5 | 818.7 | 816.9 | 813.1 | 780.4 | 745 | 601.9 | 762 | 773.3 | 713.6 | 692 | 727.9 | 765.2 | 384.7 | 356.5 | 370.9 | 355.3 | 349 | 354.3 | 346.3 | 341.7
1307.1 | 1144.1 | 468.1 | 187.24 | 218.8728 | 369.5 | 350.2 | 337.6 | 329.9 | 398.7 | 57 | 18.9 | 100.8 | 5.6 | 187.3 | 5 | 855.6 | 820 | 823.1 | 814.1 | 784.6 | 744.7 | 602.5 | 759.8 | 772.6 | 714.7 | 692.5 | 732.9 | 759.4 | 384.8 | 356.3 | 370.8 | 355.2 | 349.1 | 354.3 | 346.3 | 341.8
1308.1 | 1145.1 | 468.1 | 187.24 | 218.8728 | 369.2 | 350.3 | 337.7 | 330.4 | 401.5 | 56.8 | 18.9 | 100.8 | 5.4 | 197.9 | 5.4 | 854.5 | 822.8 | 825.4 | 815.4 | 785.1 | 744.4 | 604.1 | 763 | 772.7 | 716.2 | 692.1 | 739.1 | 754 | 384.8 | 356.1 | 370.8 | 355.1 | 349.2 | 354.4 | 346.3 | 341.8
1309.1 | 1146.1 | 468.5 | 187.4 | 219.0598 | 368.1 | 351.6 | 337.6 | 330.4 | 404.2 | 56.7 | 18.9 | 100.8 | 5.3 | 219.4 | 5.9 | 853 | 824.9 | 827 | 817 | 786.1 | 744.3 | 606 | 770 | 772.6 | 717.8 | 691.3 | 741.4 | 750.5 | 384.8 | 356.4 | 370.9 | 355.3 | 349.2 | 354.3 | 346.2 | 341.8
1310.1 | 1147.1 | 468.2 | 187.28 | 218.9195 | 367.1 | 352.9 | 337.5 | 330.3 | 404.5 | 56.7 | 18.9 | 100.7 | 5.3 | 208.1 | 4.8 | 857.2 | 828.4 | 830.2 | 817.6 | 787.9 | 744.1 | 605.3 | 776.5 | 772.2 | 720.4 | 691 | 747.6 | 747.5 | 384.8 | 356.6 | 371 | 355.3 | 349.3 | 354.1 | 346.1 | 341.7
1311.1 | 1148.1 | 468.1 | 187.24 | 218.8728 | 366.1 | 353.6 | 337.6 | 330.1 | 402.8 | 56.6 | 18.9 | 100.8 | 5.8 | 233 | 3.6 | 859.9 | 830.9 | 828.2 | 818.2 | 787.8 | 743.9 | 606 | 781.1 | 771.6 | 721.8 | 690.6 | 750.2 | 746.8 | 384.9 | 356.7 | 370.9 | 355.3 | 349.4 | 353.9 | 346 | 341.7
1312.1 | 1149.1 | 468.5 | 187.4 | 219.0598 | 366.3 | 354 | 337.1 | 329.7 | 401.9 | 56.7 | 18.9 | 100.7 | 4.8 | 267.9 | 3.5 | 864 | 835.6 | 832 | 819 | 790.5 | 743.6 | 608.5 | 785.8 | 770.7 | 724 | 690.5 | 757.8 | 747.5 | 384.9 | 356.6 | 370.8 | 355.3 | 349.5 | 353.9 | 345.9 | 341.7
1313.1 | 1150.1 | 468 | 187.2 | 218.826 | 365.8 | 354.1 | 336.8 | 329.9 | 402.6 | 56.7 | 18.9 | 100.7 | 5.1 | 274.9 | 3.3 | 867.9 | 839.8 | 835.5 | 820.3 | 791.9 | 743.4 | 609.6 | 789.6 | 769.6 | 726.1 | 690.5 | 761.9 | 746.2 | 384.9 | 356.5 | 370.7 | 355.2 | 349.5 | 353.8 | 345.9 | 341.7
1314.1 | 1151.1 | 467.2 | 186.88 | 218.452 | 365.5 | 354.1 | 336.6 | 330.1 | 399.8 | 56.8 | 18.9 | 100.7 | 6.5 | 232.2 | 2.8 | 868.7 | 845.3 | 837.9 | 821.4 | 794.8 | 743.3 | 608.9 | 795 | 768.8 | 729 | 691.4 | 768.5 | 744.6 | 385 | 356.4 | 370.6 | 355.1 | 349.6 | 353.9 | 345.9 | 341.7
1315.1 | 1152.1 | 467.3 | 186.92 | 218.4987 | 364.7 | 353.4 | 336.1 | 330.4 | 404.4 | 56.8 | 18.9 | 100.8 | 6.2 | 190.1 | 2.6 | 861.6 | 844.4 | 837 | 823 | 796.5 | 743.1 | 610.9 | 799.1 | 768.2 | 731.3 | 691.3 | 767 | 740.7 | 385 | 356.6 | 370.7 | 355.2 | 349.7 | 354.2 | 346 | 341.7
1316.1 | 1153.1 | 468.1 | 187.24 | 218.8728 | 363.6 | 353.8 | 335.5 | 330.6 | 424 | 56.9 | 18.9 | 100.9 | 6.1 | 190.3 | 2.3 | 856.6 | 835.6 | 836 | 823.8 | 796.6 | 742.8 | 609.4 | 790.9 | 768.3 | 731.5 | 689.5 | 756.9 | 735.4 | 385 | 356.9 | 371.1 | 355.4 | 349.7 | 354.5 | 345.9 | 341.7
1317.1 | 1154.1 | 467.2 | 186.88 | 218.452 | 363 | 354.8 | 335 | 331.2 | 427.9 | 57 | 18.9 | 100.9 | 5.5 | 221.9 | 2.3 | 855.8 | 834.2 | 834.7 | 824.5 | 795.6 | 742.7 | 606.4 | 786.8 | 769.5 | 731.2 | 688.1 | 754.8 | 731.7 | 385.1 | 357.2 | 371.3 | 355.6 | 349.8 | 354.6 | 345.9 | 341.7
1318.1 | 1155.1 | 467.7 | 187.08 | 218.6857 | 363.8 | 356 | 335.4 | 332.2 | 427.9 | 57 | 18.9 | 100.8 | 5.4 | 222.1 | 2.3 | 856.4 | 832.5 | 833.9 | 824.7 | 793.8 | 742.7 | 607 | 786.4 | 770.4 | 731.6 | 687.4 | 751.2 | 729.2 | 385.1 | 357.4 | 371.6 | 355.7 | 349.9 | 354.6 | 345.8 | 341.6
1319.1 | 1156.1 | 467.2 | 186.88 | 218.452 | 364.4 | 356.5 | 335.9 | 332.9 | 426.3 | 57.1 | 18.9 | 100.8 | 5.3 | 196.6 | 2.4 | 848.2 | 827.8 | 821.2 | 824.9 | 788.7 | 742.7 | 612.4 | 783.3 | 770.8 | 730.4 | 686.1 | 738.1 | 728.2 | 385.1 | 357.9 | 372 | 355.9 | 350 | 354.6 | 345.6 | 341.6
1320.1 | 1157.1 | 467.7 | 187.08 | 218.6857 | 365.4 | 356.2 | 336.7 | 333.6 | 424.1 | 57.2 | 18.9 | 100.8 | 5.2 | 181.5 | 2.6 | 840 | 817.8 | 813.7 | 825.2 | 784.7 | 742.8 | 616 | 778.6 | 771.3 | 728 | 684.5 | 726.2 | 726.6 | 385.2 | 358.5 | 372.7 | 356.2 | 350.1 | 354.5 | 345.6 | 341.6
1321.1 | 1158.1 | 467.5 | 187 | 218.5922 | 368.1 | 356.2 | 337.5 | 334.4 | 422.4 | 57.3 | 18.9 | 100.9 | 5.7 | 187.9 | 2.4 | 844.4 | 821.5 | 822.1 | 824.9 | 785.1 | 743 | 615.5 | 780.8 | 771.6 | 728.5 | 684.3 | 725.7 | 726.4 | 385.2 | 358.8 | 373.4 | 356.2 | 350.1 | 354.7 | 345.6 | 341.6
1322.1 | 1159.1 | 467.8 | 187.12 | 218.7325 | 369.2 | 356.3 | 338.3 | 335.5 | 418.3 | 57.3 | 18.9 | 101 | 6.9 | 216.5 | 3.3 | 852 | 827.5 | 830 | 824.3 | 787.6 | 743.1 | 618.1 | 791.3 | 771.1 | 730.8 | 685.1 | 730.8 | 729.9 | 385.3 | 358.9 | 374.1 | 356 | 350.2 | 354.9 | 345.7 | 341.7
1323.1 | 1160.1 | 467.3 | 186.92 | 218.4987 | 369.5 | 357.1 | 338.5 | 336.4 | 417.6 | 57.3 | 18.9 | 101.1 | 7.1 | 208.1 | 6.7 | 858.5 | 832.9 | 836.9 | 824.2 | 789.5 | 743.2 | 619.7 | 793.9 | 770.1 | 732.5 | 686.2 | 742.6 | 731.9 | 385.3 | 359.2 | 374.3 | 356 | 350.3 | 354.9 | 346 | 341.7
1324.1 | 1161.1 | 467.8 | 187.12 | 218.7325 | 369.7 | 357.5 | 339.2 | 336.7 | 421.4 | 57.2 | 18.9 | 101.1 | 6.9 | 215.4 | 9.2 | 860.7 | 836.8 | 840.4 | 824.6 | 792 | 743.3 | 619.9 | 792.8 | 769.5 | 734.2 | 686.8 | 750 | 732.3 | 385.4 | 359.4 | 374.4 | 355.9 | 350.4 | 354.8 | 346.2 | 341.8
1325.1 | 1162.1 | 467 | 186.8 | 218.3584 | 368.8 | 358.8 | 339.3 | 336.3 | 423.1 | 57.2 | 18.9 | 101 | 6.7 | 221.7 | 8.2 | 856.9 | 834.3 | 842.5 | 825 | 792 | 743.2 | 619.6 | 798 | 769.1 | 735.5 | 687.5 | 752.5 | 730.3 | 385.5 | 359.4 | 374.3 | 355.9 | 350.5 | 354.9 | 346.2 | 341.8
1326.1 | 1163.1 | 467.4 | 186.96 | 218.5455 | 368.7 | 359 | 339.2 | 335.6 | 422.4 | 57.2 | 18.9 | 100.9 | 6.4 | 219.5 | 7.4 | 859.5 | 835.1 | 847.5 | 824.8 | 795.9 | 743.3 | 617.3 | 799 | 768.6 | 736.6 | 687.7 | 755.9 | 728.1 | 385.5 | 359.3 | 374.3 | 355.8 | 350.5 | 354.8 | 346.1 | 341.8
1327.1 | 1164.1 | 467.9 | 187.16 | 218.7793 | 369.9 | 360.1 | 339.3 | 334.4 | 422.3 | 57.1 | 18.9 | 100.8 | 5.1 | 237.7 | 6.5 | 860.7 | 835.3 | 848 | 824.8 | 798 | 743.2 | 615.4 | 794.7 | 768 | 737.4 | 687.4 | 756.9 | 724.7 | 385.6 | 359.2 | 374.3 | 355.7 | 350.6 | 354.9 | 346.2 | 341.8
1328.1 | 1165.1 | 468 | 187.2 | 218.826 | 370.9 | 361.3 | 338.8 | 333.8 | 420.5 | 57.1 | 18.9 | 100.8 | 5.3 | 239.6 | 6.2 | 863.7 | 836.2 | 849 | 824.7 | 800.7 | 743.3 | 614.7 | 794 | 767.6 | 737.5 | 687.4 | 759 | 723.3 | 385.7 | 358.9 | 374.3 | 355.6 | 350.7 | 355.1 | 346.3 | 341.9
1329.1 | 1166.1 | 467 | 186.8 | 218.3584 | 371.9 | 361.3 | 338.9 | 333.4 | 417.8 | 57.1 | 18.9 | 100.7 | 5 | 230.8 | 6.4 | 866.9 | 839.8 | 847.1 | 825.2 | 800.9 | 743.3 | 615.1 | 796 | 767.6 | 737.5 | 686.9 | 755.8 | 727.5 | 385.7 | 358.9 | 374.2 | 355.6 | 350.8 | 355.1 | 346.3 | 341.9
1330.1 | 1167.1 | 467.9 | 187.16 | 218.7793 | 372.4 | 361.2 | 339 | 333.5 | 417.9 | 57 | 18.9 | 100.7 | 4.4 | 243.7 | 7.6 | 867.9 | 842.1 | 849.9 | 825.5 | 802.7 | 743.3 | 615.1 | 799.9 | 767.4 | 739.7 | 687.5 | 759.7 | 730.1 | 385.8 | 358.7 | 374.1 | 355.5 | 350.8 | 354.9 | 346.4 | 341.9
1331.1 | 1168.1 | 467.5 | 187 | 218.5922 | 372.6 | 360.3 | 338.6 | 333.3 | 415 | 57 | 18.9 | 100.7 | 4 | 238.4 | 8.3 | 866.7 | 843.7 | 843.8 | 826 | 802 | 743.3 | 616 | 798.7 | 767 | 740.2 | 687.7 | 757.2 | 733 | 385.9 | 358.7 | 374.1 | 355.5 | 350.9 | 354.7 | 346.6 | 341.9
1332.1 | 1169.1 | 466.8 | 186.72 | 218.2649 | 372.9 | 359.3 | 337.4 | 333 | 414.2 | 57 | 18.9 | 100.6 | 4.1 | 237.7 | 9.4 | 861.9 | 839.6 | 845 | 826.2 | 800.1 | 743.3 | 614.9 | 789 | 766.9 | 737.7 | 686.7 | 743.5 | 734.3 | 385.9 | 358.8 | 374.2 | 355.5 | 351 | 354.6 | 346.5 | 342
1333.1 | 1170.1 | 467.3 | 186.92 | 218.4987 | 370.8 | 358.3 | 337 | 332.6 | 412.6 | 57.1 | 18.9 | 100.6 | 4.1 | 225 | 10.1 | 861 | 835.5 | 845.6 | 826.4 | 799.5 | 743.4 | 613.3 | 787.3 | 767.2 | 737.7 | 686.2 | 743.7 | 738.1 | 386 | 358.7 | 374.2 | 355.5 | 351 | 354.5 | 346.3 | 341.9
1334.1 | 1171.1 | 467.6 | 187.04 | 218.639 | 369.2 | 357.8 | 337.4 | 332.4 | 409.1 | 57.1 | 18.9 | 100.6 | 4.6 | 230.9 | 9.6 | 862 | 832.8 | 838.4 | 826.3 | 797.1 | 743.6 | 614.1 | 782.4 | 767.6 | 735.4 | 685.6 | 737 | 747.8 | 386.1 | 358.4 | 373.9 | 355.4 | 351.1 | 354.2 | 346.2 | 341.9
1335.1 | 1172.1 | 467.7 | 187.08 | 218.6857 | 369.6 | 357.8 | 337.7 | 332.3 | 405.7 | 57.2 | 18.9 | 100.6 | 4.6 | 207.9 | 8.7 | 862.1 | 832.4 | 837.1 | 825.5 | 797.4 | 743.8 | 611.8 | 784.3 | 767.8 | 735.1 | 685.2 | 737.9 | 756.5 | 386.1 | 358.2 | 373.6 | 355.3 | 351.2 | 353.9 | 346 | 341.9
1336.1 | 1173.1 | 467.5 | 187 | 218.5922 | 372.3 | 358.1 | 337.8 | 331.7 | 403 | 57.3 | 18.9 | 100.7 | 4.7 | 229.9 | 8.6 | 859.1 | 833.7 | 829.6 | 825.4 | 794.4 | 744 | 611.1 | 789 | 767.7 | 736.5 | 686.5 | 743.7 | 759.5 | 386.2 | 358.1 | 373.3 | 355.3 | 351.2 | 353.6 | 345.8 | 341.8
1337.1 | 1174.1 | 467.8 | 187.12 | 218.7325 | 372.9 | 358.6 | 338 | 330.5 | 400.7 | 57.4 | 18.9 | 100.7 | 5.1 | 202.6 | 7.7 | 853.8 | 832.4 | 820.5 | 825.5 | 790.2 | 744.1 | 611.5 | 788.9 | 767.6 | 737.4 | 688 | 737.4 | 761.6 | 386.2 | 357.9 | 373 | 355.3 | 351.3 | 353.6 | 345.7 | 341.8
1338.1 | 1175.1 | 467.3 | 186.92 | 218.4987 | 373.1 | 358.4 | 338.6 | 329.8 | 400.5 | 57.5 | 18.9 | 100.7 | 5.7 | 209.3 | 7.1 | 842.1 | 824.6 | 804.5 | 826.1 | 784.5 | 744.1 | 611.6 | 780.9 | 767.7 | 736 | 687.7 | 721.8 | 765.5 | 386.2 | 357.9 | 372.8 | 355.4 | 351.4 | 353.7 | 345.7 | 341.8
1339.1 | 1176.1 | 468.1 | 187.24 | 218.8728 | 373.5 | 358.4 | 339.1 | 329.9 | 400.1 | 57.5 | 18.9 | 100.7 | 5.4 | 208.8 | 7.3 | 833.2 | 815.7 | 791.7 | 826.3 | 779.1 | 744.4 | 610.3 | 765.4 | 768.2 | 731.4 | 686.3 | 703.7 | 768 | 386.3 | 357.9 | 372.8 | 355.6 | 351.4 | 353.8 | 345.7 | 341.8
1340.1 | 1177.1 | 467.2 | 186.88 | 218.452 | 375.1 | 357.4 | 339.9 | 330.2 | 398.5 | 57.6 | 18.9 | 100.6 | 5.7 | 177.6 | 6.6 | 829.2 | 807.8 | 788.7 | 826.1 | 775.6 | 744.7 | 606.6 | 758.3 | 768.8 | 728.7 | 684.9 | 695.2 | 766.6 | 386.3 | 358 | 372.7 | 355.7 | 351.5 | 353.8 | 345.8 | 341.7
1341.1 | 1178.1 | 468 | 187.2 | 218.826 | 376.8 | 355.9 | 340.7 | 330.5 | 399.3 | 57.6 | 18.9 | 100.6 | 5.4 | 187.6 | 6.3 | 832.3 | 813.7 | 798.4 | 825.5 | 774.4 | 745 | 608.9 | 767 | 769.3 | 730.2 | 685 | 699.5 | 762.6 | 386.3 | 358.2 | 372.9 | 355.7 | 351.5 | 354 | 345.9 | 341.8
1342.1 | 1179.1 | 468 | 187.2 | 218.826 | 376.6 | 354.9 | 340.3 | 330.7 | 402 | 57.6 | 18.9 | 100.5 | 5.5 | 189.3 | 6.4 | 839.7 | 822 | 807.5 | 825 | 775.3 | 745.2 | 609 | 776.6 | 769.4 | 731.5 | 686 | 710.9 | 761.6 | 386.4 | 358.3 | 373.2 | 355.7 | 351.6 | 354.3 | 345.9 | 341.8
1343.1 | 1180.1 | 468.2 | 187.28 | 218.9195 | 376.5 | 355 | 340.4 | 330.9 | 401.6 | 57.6 | 18.9 | 100.5 | 5.2 | 194.4 | 6.7 | 851.1 | 829.7 | 814.4 | 824.3 | 778.3 | 745.3 | 608.4 | 787.8 | 768.8 | 733.8 | 687.6 | 726.5 | 761.3 | 386.4 | 358.5 | 373.3 | 355.7 | 351.7 | 354.5 | 346 | 341.9
1344.1 | 1181.1 | 467.9 | 187.16 | 218.7793 | 375.5 | 356.2 | 341 | 331.6 | 400.4 | 57.6 | 18.9 | 100.5 | 5.2 | 198.2 | 7.1 | 856.1 | 831.2 | 821.2 | 823.7 | 781 | 745.2 | 610.7 | 791.4 | 767.6 | 735.1 | 688.7 | 738 | 760.2 | 386.4 | 358.5 | 373.3 | 355.6 | 351.7 | 354.7 | 346.1 | 341.9
1345.1 | 1182.1 | 467.8 | 187.12 | 218.7325 | 376.3 | 358.1 | 341 | 331.9 | 400.4 | 57.5 | 18.9 | 100.5 | 5.7 | 198.9 | 7.1 | 859.2 | 836.6 | 830.1 | 823.8 | 785.2 | 745.3 | 614.7 | 797.1 | 766.5 | 737.3 | 689.2 | 747.9 | 756.1 | 386.5 | 358.4 | 373.5 | 355.4 | 351.8 | 355.1 | 346.3 | 342
1346.1 | 1183.1 | 467.5 | 187 | 218.5922 | 376.2 | 359.4 | 340.7 | 331.5 | 403.4 | 57.4 | 18.9 | 100.5 | 6 | 205.7 | 6.9 | 864 | 844.8 | 833.6 | 824.9 | 789.3 | 745.3 | 618.7 | 803.8 | 765.5 | 739.5 | 690.7 | 759.1 | 751.2 | 386.5 | 358.6 | 373.6 | 355.4 | 351.8 | 355.1 | 346.6 | 342.1
1347.1 | 1184.1 | 468.5 | 187.4 | 219.0598 | 375.5 | 360.2 | 341.2 | 331.3 | 402.3 | 57.3 | 18.9 | 100.5 | 5.9 | 201.6 | 7.4 | 867.4 | 854.1 | 836.9 | 825.8 | 791.6 | 745 | 618 | 806.3 | 764.7 | 741 | 691 | 765.2 | 747.9 | 386.6 | 358.6 | 373.7 | 355.4 | 351.9 | 355 | 346.9 | 342.2
1348.1 | 1185.1 | 468.5 | 187.4 | 219.0598 | 375.4 | 361 | 341.3 | 331.4 | 404.9 | 57.3 | 18.9 | 100.5 | 5.1 | 211.3 | 7.8 | 870.9 | 858.4 | 844.1 | 826.6 | 796.2 | 745 | 617.5 | 807.9 | 764.1 | 743.5 | 690.8 | 768.4 | 745.2 | 386.6 | 358.6 | 373.5 | 355.4 | 352 | 355 | 347 | 342.2
1349.1 | 1186.1 | 468.1 | 187.24 | 218.8728 | 375.4 | 361.5 | 341.2 | 331.4 | 403.7 | 57.3 | 18.9 | 100.6 | 4.3 | 206.2 | 8.7 | 875.9 | 858.6 | 844.2 | 826 | 798.3 | 744.8 | 616.5 | 806.4 | 763.8 | 743.6 | 690.3 | 770.3 | 744.8 | 386.7 | 358.5 | 373.3 | 355.3 | 352 | 355.2 | 347 | 342.3
1350.1 | 1187.1 | 468.1 | 187.24 | 218.8728 | 375.9 | 361.3 | 340.9 | 331.3 | 402.7 | 57.3 | 18.9 | 100.7 | 4.9 | 205.2 | 9.2 | 877.6 | 860.3 | 844.5 | 825.5 | 801.1 | 744.7 | 617.8 | 809.4 | 763.5 | 744.9 | 690.2 | 774.8 | 743.1 | 386.7 | 358.4 | 373.1 | 355.3 | 352.1 | 355.5 | 347.2 | 342.2
1351.1 | 1188.1 | 467.9 | 187.16 | 218.7793 | 376.6 | 360.8 | 340.6 | 330.6 | 403.7 | 57.4 | 18.9 | 100.8 | 5.8 | 203.2 | 8.8 | 879.1 | 866.5 | 843.9 | 826.6 | 801.2 | 744.7 | 620.5 | 810.5 | 763.2 | 746.2 | 689.5 | 776.5 | 740.2 | 386.8 | 358.6 | 373 | 355.5 | 352.2 | 355.7 | 347.3 | 342.3
1352.1 | 1189.1 | 468.4 | 187.36 | 219.013 | 379.1 | 361 | 340.5 | 330.4 | 406.2 | 57.6 | 18.9 | 100.9 | 6.1 | 197.3 | 8.1 | 875.2 | 858.5 | 840.5 | 827.3 | 800.2 | 744.5 | 621.2 | 804.3 | 763.3 | 745.5 | 688.6 | 764.7 | 736.5 | 386.8 | 358.7 | 373.2 | 355.7 | 352.2 | 355.8 | 347.3 | 342.3
1353.1 | 1190.1 | 467.9 | 187.16 | 218.7793 | 381.3 | 361.1 | 341.2 | 330 | 408.5 | 57.7 | 18.9 | 100.8 | 6 | 194.5 | 7.1 | 869.9 | 845.1 | 833.6 | 827.5 | 797.7 | 744.6 | 618.7 | 792.2 | 763.8 | 743 | 687.4 | 750.4 | 733.2 | 386.9 | 358.9 | 373.4 | 355.8 | 352.3 | 355.9 | 347.3 | 342.2
1354.1 | 1191.1 | 468.2 | 187.28 | 218.9195 | 381.1 | 360.2 | 342.1 | 331 | 408.1 | 57.8 | 18.9 | 100.8 | 5.6 | 189.9 | 6.5 | 866.4 | 842.1 | 837.7 | 827.2 | 797.2 | 744.8 | 618 | 794.6 | 764.5 | 744.2 | 687.2 | 746.7 | 729.5 | 386.9 | 359.1 | 373.5 | 355.9 | 352.4 | 355.8 | 347.4 | 342.3
1355.1 | 1192.1 | 468.4 | 187.36 | 219.013 | 380.9 | 359.9 | 342.5 | 332.2 | 412.5 | 57.8 | 18.9 | 100.8 | 5.8 | 202.9 | 5.9 | 865.1 | 845.6 | 838.2 | 827.6 | 797 | 744.9 | 619.9 | 798.9 | 764.8 | 746.4 | 687.7 | 749.8 | 728.2 | 387 | 359.4 | 373.6 | 356.1 | 352.4 | 355.9 | 347.5 | 342.3
1356.1 | 1193.1 | 467.6 | 187.04 | 218.639 | 381.2 | 359.4 | 342.6 | 332.6 | 416 | 57.7 | 18.9 | 100.9 | 5.6 | 213.9 | 5.2 | 864 | 847.5 | 839.7 | 828.1 | 796.2 | 745 | 619.1 | 800.5 | 765.2 | 746.5 | 687 | 749.8 | 731.1 | 387 | 359.8 | 374.1 | 356.1 | 352.5 | 356.1 | 347.6 | 342.3
1357.1 | 1194.1 | 468.2 | 187.28 | 218.9195 | 380.6 | 359.5 | 342.2 | 332.7 | 415 | 57.7 | 18.9 | 100.9 | 4.7 | 212.9 | 4.7 | 868 | 852.5 | 841 | 828.5 | 797.9 | 745.1 | 620.4 | 803.6 | 765.2 | 748.5 | 687.4 | 759.5 | 733.8 | 387.1 | 359.9 | 374.3 | 356 | 352.5 | 356.4 | 347.8 | 342.3
1358.1 | 1195.1 | 468.2 | 187.28 | 218.9195 | 380.1 | 359.5 | 342.3 | 333.1 | 409.2 | 57.8 | 18.9 | 100.8 | 4.4 | 211.3 | 4.6 | 873.4 | 854.1 | 839.3 | 828.4 | 798.8 | 745.2 | 622.4 | 803.5 | 765 | 748.8 | 688.3 | 765.6 | 739.1 | 387.1 | 359.9 | 374.4 | 355.9 | 352.6 | 356.6 | 347.9 | 342.4
1359.1 | 1196.1 | 468 | 187.2 | 218.826 | 380.5 | 359.6 | 341.9 | 333.5 | 405 | 57.8 | 18.9 | 100.9 | 4.9 | 191.2 | 5.5 | 878.1 | 856.3 | 839.6 | 828.9 | 799.9 | 745.3 | 622.6 | 799.4 | 764.8 | 749.1 | 688.4 | 771.1 | 744.4 | 387.2 | 360.1 | 374.3 | 356 | 352.7 | 356.6 | 348 | 342.5
1360.1 | 1197.1 | 468.1 | 187.24 | 218.8728 | 380.7 | 360.4 | 341.4 | 333.4 | 404.8 | 57.8 | 18.9 | 100.8 | 4.4 | 195.4 | 5.4 | 879.7 | 856.3 | 840.6 | 829.1 | 800.3 | 745.3 | 623.5 | 800.7 | 764.7 | 750.1 | 688.7 | 771.1 | 748.7 | 387.3 | 360.2 | 374.4 | 356 | 352.7 | 356.7 | 348 | 342.6
1361.1 | 1198.1 | 467.8 | 187.12 | 218.7325 | 381 | 361.1 | 340.8 | 333.2 | 404.7 | 57.8 | 18.9 | 100.7 | 5.2 | 220.2 | 4.5 | 878.6 | 857.3 | 842 | 828.6 | 801.9 | 745.4 | 623.3 | 801.6 | 764.3 | 751.2 | 688.8 | 775.2 | 752.6 | 387.3 | 360 | 374.1 | 355.9 | 352.8 | 356.7 | 348 | 342.6
1362.1 | 1199.1 | 468.7 | 187.48 | 219.1533 | 380.9 | 361.3 | 340.7 | 332.9 | 404.7 | 57.7 | 18.9 | 100.6 | 4.7 | 249.8 | 4.7 | 878.3 | 859.3 | 846.7 | 828 | 804.7 | 745.6 | 625.1 | 803 | 763.8 | 752.7 | 689.6 | 778.2 | 752.1 | 387.4 | 359.9 | 373.9 | 355.8 | 352.9 | 356.9 | 348.1 | 342.6
1363.1 | 1200.1 | 468.3 | 187.32 | 218.9663 | 381.3 | 361.2 | 340.8 | 332 | 406.4 | 57.8 | 18.9 | 100.5 | 5.4 | 216.7 | 5.2 | 878 | 866.1 | 844.5 | 829.7 | 805.4 | 745.6 | 624.9 | 801.9 | 763.5 | 753.6 | 690.2 | 774.9 | 750 | 387.4 | 359.9 | 373.9 | 355.9 | 352.9 | 357 | 348.2 | 342.7
1364.1 | 1201.1 | 468 | 187.2 | 218.826 | 382.2 | 361.6 | 340.8 | 331.4 | 407.2 | 57.8 | 18.9 | 100.5 | 5.2 | 237 | 5.7 | 873.8 | 868 | 836.5 | 830.4 | 802.8 | 745.6 | 624.5 | 808.8 | 763.5 | 755.1 | 690.1 | 766.8 | 748.9 | 387.5 | 359.9 | 373.9 | 356.1 | 353 | 357.3 | 348.3 | 342.7
1365.1 | 1202.1 | 467.7 | 187.08 | 218.6857 | 382 | 361.9 | 341 | 330.8 | 409.9 | 57.9 | 18.9 | 100.5 | 5.2 | 234.1 | 5.5 | 865.4 | 855.7 | 832.7 | 830.9 | 799.4 | 745.5 | 622.7 | 807.2 | 763.2 | 754.1 | 688.5 | 753.9 | 745.8 | 387.5 | 360 | 374 | 356.1 | 353.1 | 357.3 | 348.3 | 342.7
1366.1 | 1203.1 | 468.3 | 187.32 | 218.9663 | 380.3 | 361.9 | 341.5 | 330.5 | 407.4 | 57.9 | 18.9 | 100.5 | 5.3 | 226.3 | 4.8 | 866.8 | 854.2 | 836.1 | 830.8 | 799.7 | 745.6 | 620.7 | 807 | 763.1 | 753.9 | 687.7 | 754.4 | 742.2 | 387.6 | 360.1 | 374.1 | 356.1 | 353.1 | 357.1 | 348.3 | 342.7
1367.1 | 1204.1 | 468.3 | 187.32 | 218.9663 | 379.8 | 362.5 | 341.4 | 330.1 | 411.2 | 57.9 | 18.9 | 100.4 | 4.6 | 220 | 4.3 | 871.8 | 857 | 840.9 | 830.7 | 801.1 | 745.8 | 620.2 | 810.1 | 763.3 | 755.2 | 688.7 | 765.7 | 739.3 | 387.6 | 360.2 | 374.1 | 356.1 | 353.2 | 356.9 | 348.3 | 342.7
1368.1 | 1205.1 | 468.6 | 187.44 | 219.1066 | 380.6 | 363.4 | 341.1 | 330.2 | 414.4 | 58 | 18.9 | 100.5 | 5.1 | 221.1 | 4.2 | 872.5 | 858.3 | 842.3 | 831 | 802.7 | 745.8 | 620.1 | 813.8 | 763.4 | 756 | 688.5 | 767.9 | 735.4 | 387.7 | 360.4 | 374.4 | 356.1 | 353.2 | 356.8 | 348.2 | 342.8
1369.1 | 1206.1 | 467.7 | 187.08 | 218.6857 | 380.9 | 364 | 340.7 | 331 | 416.2 | 58 | 18.9 | 100.5 | 5.3 | 222.5 | 4 | 874.9 | 859.4 | 842.5 | 830.6 | 802.8 | 745.9 | 624 | 816.1 | 763.6 | 757.5 | 688.8 | 768.5 | 732.1 | 387.7 | 360.5 | 374.7 | 356.1 | 353.3 | 356.7 | 348 | 342.7
1370.1 | 1207.1 | 469 | 187.6 | 219.2936 | 382 | 363.9 | 340.7 | 331.4 | 415.6 | 58 | 18.9 | 100.6 | 5.1 | 215.5 | 4.2 | 876.7 | 860 | 846 | 829.8 | 804.8 | 745.9 | 629.9 | 813.6 | 763.7 | 758.5 | 689.5 | 769.4 | 731.3 | 387.8 | 360.5 | 375.1 | 356.1 | 353.4 | 356.8 | 348 | 342.8
1371.1 | 1208.1 | 468.1 | 187.24 | 218.8728 | 382.9 | 363.3 | 341 | 331.6 | 415.3 | 58 | 18.9 | 100.7 | 5.5 | 219.9 | 4.2 | 877.6 | 864 | 840.2 | 830.2 | 804.6 | 746.1 | 630.9 | 805.8 | 764.1 | 758.2 | 689.1 | 772.5 | 730.6 | 387.8 | 360.7 | 375.7 | 356.1 | 353.4 | 357 | 348.2 | 342.9
1372.1 | 1209.1 | 468.2 | 187.28 | 218.9195 | 382.6 | 363 | 341.1 | 331.4 | 420.3 | 58 | 18.9 | 100.8 | 4.8 | 227.2 | 4.1 | 874.4 | 861.4 | 837.2 | 830.9 | 803.4 | 746.3 | 630.4 | 806.5 | 764.8 | 758.5 | 688.8 | 770.9 | 730.1 | 387.9 | 361.2 | 376.2 | 356.4 | 353.5 | 357.2 | 348.3 | 342.9
1373.1 | 1210.1 | 468.6 | 187.44 | 219.1066 | 384.2 | 363.9 | 341.5 | 331.7 | 423.6 | 57.9 | 18.9 | 100.8 | 4.9 | 226.4 | 4.4 | 871.1 | 855.8 | 833.4 | 830.7 | 801.9 | 746.4 | 631.5 | 808.1 | 765.3 | 759.5 | 688.7 | 766.6 | 729.1 | 388 | 361.4 | 376.5 | 356.5 | 353.5 | 357.4 | 348.5 | 342.9
1374.1 | 1211.1 | 468.3 | 187.32 | 218.9663 | 385.4 | 364.8 | 342.2 | 331.8 | 424.3 | 57.9 | 18.9 | 100.9 | 4.8 | 226 | 4.5 | 866.2 | 847.9 | 833.5 | 831 | 802.4 | 746.7 | 630.9 | 804.1 | 765.4 | 759.1 | 688.7 | 757.8 | 727.4 | 388 | 361.6 | 376.7 | 356.6 | 353.6 | 357.7 | 348.7 | 343
1375.1 | 1212.1 | 468.4 | 187.36 | 219.013 | 384.9 | 365.6 | 343.2 | 331.9 | 436.6 | 57.7 | 18.9 | 100.9 | 4.7 | 225.2 | 4.2 | 861.6 | 844.2 | 835.2 | 831.3 | 804.3 | 747 | 630.9 | 801.7 | 766.2 | 759.2 | 688.5 | 754.5 | 724.9 | 388.1 | 361.8 | 376.8 | 356.5 | 353.7 | 357.9 | 348.9 | 343.1
1376.1 | 1213.1 | 468.4 | 187.36 | 219.013 | 383 | 365.6 | 343.4 | 332.3 | 438.8 | 57.6 | 18.9 | 100.8 | 4.3 | 234.5 | 3.8 | 863 | 845.6 | 840.1 | 831.6 | 806 | 747.4 | 629.9 | 804.3 | 766.8 | 760.6 | 689.1 | 764.2 | 722.2 | 388.2 | 361.8 | 376.8 | 356.4 | 353.7 | 358 | 349.1 | 343.1
1377.1 | 1214.1 | 468.1 | 187.24 | 218.8728 | 381.7 | 365.2 | 343.3 | 333 | 439.3 | 57.5 | 18.9 | 100.8 | 4.1 | 252.7 | 4 | 868.6 | 846.8 | 840.1 | 831.8 | 807 | 747.5 | 627.6 | 800.8 | 767.4 | 760 | 689.3 | 768.5 | 724.1 | 388.2 | 361.9 | 376.8 | 356.3 | 353.8 | 358 | 349.1 | 343.2
1378.1 | 1215.1 | 468.4 | 187.36 | 219.013 | 382.9 | 365.2 | 343.2 | 333.2 | 433.1 | 57.5 | 18.9 | 100.8 | 4.7 | 241.5 | 5 | 871.6 | 849.4 | 831.8 | 831.7 | 805.6 | 747.6 | 623.3 | 802.5 | 768.2 | 760 | 688.7 | 766.1 | 730.1 | 388.3 | 361.7 | 376.6 | 356.3 | 353.8 | 357.8 | 349 | 343.2
1379.1 | 1216.1 | 468.5 | 187.4 | 219.0598 | 387.7 | 365.3 | 342.8 | 333.1 | 427.9 | 57.5 | 18.9 | 100.8 | 4.4 | 226.3 | 5.4 | 872.3 | 852.2 | 834.2 | 831.3 | 804.2 | 747.7 | 623.7 | 808.8 | 768.8 | 760.4 | 688 | 758.5 | 735 | 388.4 | 361.7 | 376.6 | 356.3 | 353.9 | 357.6 | 348.8 | 343.1
1380.1 | 1217.1 | 468.6 | 187.44 | 219.1066 | 389.6 | 365.5 | 342.2 | 333.2 | 426.2 | 57.5 | 18.9 | 100.8 | 4.3 | 245.5 | 5.9 | 872.6 | 854.7 | 841.6 | 830.6 | 806.6 | 747.9 | 628.1 | 810.8 | 769.1 | 761.7 | 688.1 | 762 | 736.2 | 388.5 | 361.7 | 376.5 | 356.4 | 354 | 357.6 | 348.6 | 343.1
1381.1 | 1218.1 | 467.5 | 187 | 218.5922 | 390.2 | 364.7 | 341.7 | 333.1 | 425.1 | 57.4 | 18.9 | 100.9 | 4.7 | 235 | 6.2 | 873.5 | 858.1 | 846.6 | 830.5 | 808.7 | 748.2 | 629.4 | 814.2 | 769.6 | 763.2 | 689.2 | 770.5 | 735.2 | 388.5 | 361.6 | 376.4 | 356.2 | 354 | 357.6 | 348.6 | 343.1
1382.1 | 1219.1 | 467.5 | 187 | 218.5922 | 389.9 | 363.7 | 341.6 | 333 | 424.8 | 57.5 | 18.9 | 100.9 | 4.7 | 238.3 | 6.2 | 872.4 | 863.6 | 848.7 | 830.6 | 812.5 | 748.4 | 629.5 | 814.8 | 770.3 | 764.6 | 690.4 | 774.3 | 732.7 | 388.6 | 361.5 | 376.4 | 356.1 | 354.1 | 357.6 | 348.5 | 343.2
1383.1 | 1220.1 | 468.1 | 187.24 | 218.8728 | 388.4 | 363.5 | 341.5 | 332.7 | 433.7 | 57.7 | 18.9 | 101 | 5 | 236.2 | 6.1 | 868.3 | 864.1 | 841.8 | 831.7 | 811.1 | 748.4 | 629.2 | 812.1 | 770.9 | 764.4 | 689.7 | 763.8 | 730 | 388.7 | 361.9 | 377 | 356.3 | 354.2 | 357.8 | 348.4 | 343.1
1384.1 | 1221.1 | 466.4 | 186.56 | 218.0779 | 387.5 | 363 | 342.1 | 332.9 | 441.8 | 57.8 | 18.9 | 101 | 4.6 | 236.2 | 5.9 | 856 | 852.7 | 831.3 | 832.1 | 806.7 | 748.5 | 629.9 | 811.9 | 772.1 | 764.7 | 689.6 | 752.7 | 724.9 | 388.7 | 362.4 | 377.3 | 356.6 | 354.3 | 358.1 | 348.5 | 343.1
1385.1 | 1222.1 | 467.8 | 187.12 | 218.7325 | 389.2 | 361.8 | 342.8 | 333.5 | 443 | 57.8 | 18.9 | 101 | 5.5 | 236.3 | 5.8 | 853.7 | 850 | 832.6 | 831.8 | 807 | 748.7 | 628.8 | 812 | 773.7 | 764.7 | 689 | 747.1 | 719.5 | 388.8 | 362.7 | 377.6 | 356.8 | 354.3 | 358.2 | 348.5 | 343.1
1386.1 | 1223.1 | 467.6 | 187.04 | 218.639 | 388.7 | 361.3 | 343.2 | 334.3 | 441.3 | 57.8 | 18.9 | 101.1 | 5.2 | 235 | 5.5 | 859.9 | 854 | 837.2 | 831.4 | 808.8 | 748.9 | 625.7 | 814 | 774.8 | 765.2 | 689 | 744.7 | 720.6 | 388.9 | 362.6 | 377.6 | 356.7 | 354.4 | 358.4 | 348.5 | 343.2
1387.1 | 1224.1 | 467.8 | 187.12 | 218.7325 | 387.9 | 361 | 344 | 335.3 | 434.9 | 57.7 | 18.9 | 101.1 | 5 | 243.8 | 5.1 | 864.2 | 856.4 | 836 | 831.7 | 808.3 | 749.2 | 625.3 | 810.9 | 775.1 | 764.9 | 688.7 | 751 | 725.9 | 388.9 | 362.8 | 377.6 | 356.8 | 354.5 | 358.5 | 348.7 | 343.3
1388.1 | 1225.1 | 467.9 | 187.16 | 218.7793 | 387 | 360.2 | 343.9 | 336 | 428.1 | 57.5 | 18.9 | 101.1 | 4.9 | 233.9 | 4.9 | 865.8 | 857 | 839 | 832.2 | 807.8 | 749.3 | 626.6 | 810.6 | 775.1 | 764 | 688.9 | 743.5 | 732 | 389 | 362.8 | 377.7 | 356.8 | 354.5 | 358.7 | 348.9 | 343.3
1389.1 | 1226.1 | 468 | 187.2 | 218.826 | 387.2 | 358.9 | 343.6 | 336 | 421.8 | 57.4 | 18.8 | 101.1 | 5.3 | 220.5 | 5.2 | 869.9 | 858.9 | 842.4 | 831.9 | 812.6 | 749.6 | 625.8 | 812.2 | 775 | 764.8 | 690 | 752.9 | 732.8 | 389.1 | 362.6 | 377.7 | 356.7 | 354.6 | 358.8 | 349.1 | 343.4
1390.1 | 1227.1 | 467.6 | 187.04 | 218.639 | 388.6 | 358.1 | 343.3 | 336.2 | 418.3 | 57.5 | 18.8 | 101 | 5.3 | 221.3 | 5.3 | 872.6 | 858.5 | 842.5 | 832.1 | 813.2 | 749.8 | 626.5 | 814.4 | 774.9 | 765.3 | 691.1 | 761.5 | 734.5 | 389.1 | 362.3 | 377.5 | 356.5 | 354.7 | 358.6 | 349.2 | 343.5
1391.1 | 1228.1 | 467.4 | 186.96 | 218.5455 | 389.8 | 359.3 | 343.1 | 336.4 | 415.9 | 57.5 | 18.8 | 101 | 4.9 | 227.7 | 5.7 | 874.3 | 857.9 | 845.5 | 831.9 | 815.1 | 750 | 628.3 | 813.2 | 774.9 | 765.9 | 692.9 | 767.1 | 737.3 | 389.2 | 362.1 | 377.2 | 356.4 | 354.8 | 358.3 | 349.1 | 343.5
1392.1 | 1229.1 | 468 | 187.2 | 218.826 | 389.2 | 361.2 | 342.7 | 336.1 | 417.5 | 57.5 | 18.8 | 100.9 | 4.6 | 232.4 | 5.9 | 876.6 | 860.4 | 849.1 | 832.4 | 816 | 750.2 | 627.6 | 811.2 | 774.9 | 766.2 | 693.8 | 772.6 | 738.3 | 389.3 | 362 | 377.1 | 356.3 | 354.9 | 358.3 | 349 | 343.5
1393.1 | 1230.1 | 467.6 | 187.04 | 218.639 | 392.1 | 362 | 342.7 | 335.5 | 419.7 | 57.6 | 18.8 | 101 | 4.8 | 240.6 | 5.4 | 877.9 | 864.3 | 854.3 | 832.8 | 818.3 | 750.2 | 627 | 815.6 | 774.9 | 767.2 | 694.2 | 775.5 | 736.2 | 389.4 | 361.9 | 377.2 | 356.3 | 354.9 | 358.3 | 348.9 | 343.5
1394.1 | 1231.1 | 467.4 | 186.96 | 218.5455 | 394.1 | 362.2 | 343 | 335.2 | 421.1 | 57.7 | 18.8 | 101.1 | 5.6 | 239.9 | 4.8 | 880.4 | 871.3 | 850.6 | 833.7 | 817.2 | 750.3 | 627.5 | 819.7 | 775 | 767.9 | 694 | 771.1 | 736.4 | 389.4 | 361.8 | 377 | 356.4 | 355 | 358.2 | 348.7 | 343.5
1395.1 | 1232.1 | 467.7 | 187.08 | 218.6857 | 394.4 | 362.7 | 342.8 | 334.9 | 428.1 | 57.6 | 18.8 | 101.1 | 4.6 | 237.6 | 4.6 | 873.2 | 862.2 | 846.6 | 834.1 | 814.7 | 750.3 | 624.7 | 809.4 | 774.7 | 767.8 | 692.8 | 760.6 | 733.2 | 389.5 | 361.9 | 377.2 | 356.7 | 355.1 | 358.1 | 348.8 | 343.5
1396.1 | 1233.1 | 467.4 | 186.96 | 218.5455 | 393.3 | 362.8 | 342.7 | 334.7 | 438.4 | 57.6 | 18.8 | 101.1 | 5.1 | 241.6 | 4.3 | 864.6 | 850.8 | 836.8 | 834.1 | 811 | 750.4 | 620.9 | 795.4 | 775.1 | 765.4 | 691.6 | 748.8 | 729.1 | 389.5 | 362.2 | 377.5 | 356.9 | 355.1 | 358.4 | 349 | 343.5
1397.1 | 1234.1 | 467.9 | 187.16 | 218.7793 | 392 | 363.1 | 343.4 | 335.2 | 436.3 | 57.5 | 18.8 | 101 | 4.9 | 238.8 | 4.5 | 862.1 | 845.6 | 836.2 | 833.9 | 807.9 | 750.7 | 618 | 793 | 776.1 | 764.8 | 690.7 | 740.8 | 728.7 | 389.6 | 362.4 | 377.7 | 357.1 | 355.2 | 358.4 | 349.1 | 343.5
1398.1 | 1235.1 | 467.9 | 187.16 | 218.7793 | 392.6 | 364.4 | 343.9 | 336 | 433.7 | 57.6 | 18.8 | 100.9 | 5.2 | 245.9 | 5.2 | 862.5 | 847.5 | 839.1 | 833.6 | 807.7 | 751 | 614.3 | 793.5 | 776.6 | 765.2 | 690.3 | 743.9 | 727.9 | 389.6 | 362.9 | 378 | 357.3 | 355.3 | 358.5 | 349.2 | 343.5
1399.1 | 1236.1 | 468.2 | 187.28 | 218.9195 | 392 | 364.7 | 344.8 | 336.6 | 436.6 | 57.7 | 18.8 | 100.9 | 4.2 | 243.1 | 5.8 | 865.3 | 852.5 | 845.8 | 833.7 | 810.8 | 751.2 | 611.9 | 797 | 776.9 | 765.8 | 690.7 | 753.1 | 726.8 | 389.7 | 363.1 | 377.9 | 357.3 | 355.3 | 358.5 | 349.3 | 343.6
1400.1 | 1237.1 | 468.4 | 187.36 | 219.013 | 390.9 | 365.4 | 345.1 | 337 | 435.8 | 57.8 | 18.8 | 100.9 | 4.4 | 243.2 | 6 | 868.8 | 858.1 | 849.7 | 833.9 | 813.5 | 751.4 | 613.3 | 804.7 | 777.3 | 767.2 | 692.1 | 765.7 | 726.6 | 389.7 | 363.1 | 377.7 | 357.1 | 355.4 | 358.5 | 349.4 | 343.7
1401.1 | 1238.1 | 468.1 | 187.24 | 218.8728 | 388.5 | 366.7 | 344.9 | 337.1 | 429.9 | 57.9 | 18.8 | 100.9 | 4.3 | 244.2 | 5.9 | 872.1 | 862.4 | 853.6 | 834.3 | 815.4 | 751.5 | 614.3 | 805 | 777 | 767 | 692.4 | 769.7 | 729.1 | 389.8 | 363 | 377.5 | 357.1 | 355.5 | 358.5 | 349.6 | 343.7
1402.1 | 1239.1 | 467.5 | 187 | 218.5922 | 387.5 | 367.4 | 344.3 | 337 | 427.2 | 57.9 | 18.8 | 100.9 | 5.2 | 247 | 5.7 | 872.7 | 864.5 | 856.1 | 834.2 | 817.8 | 751.7 | 616.5 | 806.1 | 776.8 | 767.9 | 693.4 | 773.6 | 730.2 | 389.9 | 363 | 377.2 | 357 | 355.5 | 358.5 | 349.7 | 343.7
1403.1 | 1240.1 | 468.6 | 187.44 | 219.1066 | 387.9 | 367.6 | 343.7 | 336.4 | 425.8 | 57.8 | 18.8 | 100.9 | 4.9 | 247.3 | 5.7 | 874 | 866.2 | 858.8 | 834.6 | 820.8 | 751.7 | 613.6 | 804 | 776.6 | 767.5 | 693.3 | 775.7 | 729 | 389.9 | 362.9 | 377 | 356.9 | 355.6 | 358.2 | 349.5 | 343.7
1404.1 | 1241.1 | 468.1 | 187.24 | 218.8728 | 385.4 | 367.3 | 343.2 | 336 | 425.8 | 57.8 | 18.8 | 100.8 | 4.6 | 243.7 | 5.8 | 878.7 | 869.5 | 860.7 | 835.5 | 820.9 | 751.9 | 613.5 | 806.4 | 776.7 | 768.4 | 693.2 | 775.8 | 727.8 | 390 | 363 | 377.1 | 357 | 355.7 | 358.1 | 349.5 | 343.7
1405.1 | 1242.1 | 469.4 | 187.76 | 219.4806 | 383.1 | 367.3 | 342.9 | 335.7 | 427.4 | 57.7 | 18.8 | 100.8 | 4.5 | 239.1 | 5.9 | 881 | 866.8 | 859.6 | 835.7 | 821.5 | 751.9 | 615.4 | 806.2 | 776.9 | 768.8 | 692.8 | 775.9 | 728.5 | 390.1 | 363 | 377.1 | 357 | 355.7 | 358.1 | 349.5 | 343.8
1406.1 | 1243.1 | 467.6 | 187.04 | 218.639 | 381.2 | 367.1 | 342.5 | 335.7 | 424.6 | 57.7 | 18.8 | 100.9 | 5 | 240.3 | 5.8 | 883.8 | 867.6 | 861 | 836 | 822.7 | 752.2 | 616.4 | 804.7 | 776.9 | 768.6 | 693.1 | 772.5 | 728.7 | 390.1 | 362.9 | 377 | 357 | 355.8 | 358.1 | 349.6 | 343.8
1407.1 | 1244.1 | 468.4 | 187.36 | 219.013 | 380.5 | 366.4 | 341.3 | 335.7 | 424.2 | 57.7 | 18.8 | 101 | 4.7 | 241.3 | 5.9 | 878.8 | 866.4 | 849.6 | 836.6 | 818.3 | 752.2 | 617.4 | 805.4 | 777 | 768.5 | 693.4 | 764.8 | 730 | 390.2 | 363.1 | 377 | 357.1 | 355.9 | 358 | 349.5 | 343.8
1408.1 | 1245.1 | 469 | 187.6 | 219.2936 | 380.8 | 365.5 | 340.6 | 335.5 | 422.2 | 57.8 | 18.8 | 101.2 | 4.7 | 239.3 | 5.8 | 867.6 | 857.4 | 837.6 | 836.8 | 812.8 | 752.2 | 621.2 | 799.3 | 776.9 | 767.1 | 692.4 | 748.5 | 728.6 | 390.2 | 363.3 | 377.3 | 357.3 | 355.9 | 358 | 349.4 | 343.7
1409.1 | 1246.1 | 469.3 | 187.72 | 219.4339 | 381 | 366.3 | 340.3 | 335.6 | 424.5 | 57.9 | 18.8 | 101.4 | 4.7 | 244 | 5.9 | 858.4 | 847.1 | 827.5 | 837.1 | 807.7 | 752.4 | 621.7 | 793.6 | 777 | 765.8 | 691.4 | 736.4 | 726.8 | 390.2 | 363.5 | 377.7 | 357.5 | 356 | 357.9 | 349.3 | 343.7
1410.1 | 1247.1 | 469.3 | 187.72 | 219.4339 | 381.1 | 366.9 | 341.3 | 336 | 430.4 | 58 | 18.8 | 101.6 | 4.5 | 243.8 | 6 | 846.8 | 835.7 | 816.5 | 837.2 | 800.8 | 752.5 | 620.8 | 784.2 | 777 | 763 | 690.5 | 722.1 | 725.5 | 390.3 | 363.6 | 378.2 | 357.6 | 356 | 358.1 | 349.3 | 343.7
1411.1 | 1248.1 | 469.6 | 187.84 | 219.5741 | 381.9 | 368 | 342.3 | 336.4 | 429 | 58 | 18.8 | 101.8 | 4.8 | 243.1 | 6.3 | 843.6 | 830.9 | 810 | 836.8 | 795.3 | 752.8 | 617.9 | 776.2 | 777.1 | 760.8 | 689.4 | 715.3 | 725.5 | 390.3 | 363.9 | 378.8 | 357.7 | 356.1 | 358.4 | 349.5 | 343.7
1412.1 | 1249.1 | 469.3 | 187.72 | 219.4339 | 382.8 | 368.1 | 342.8 | 337.6 | 426.7 | 58.1 | 18.8 | 101.9 | 4.9 | 243.7 | 6.7 | 839.4 | 824.9 | 803.7 | 836.3 | 789.2 | 753.1 | 614.1 | 767.2 | 776.9 | 758.7 | 688.6 | 708.2 | 729 | 390.4 | 364.2 | 379.1 | 357.7 | 356.1 | 358.6 | 349.7 | 343.7
1413.1 | 1250.1 | 468.8 | 187.52 | 219.2001 | 384.8 | 367.6 | 343.2 | 338.6 | 427.6 | 58.1 | 18.8 | 102 | 4.6 | 246.8 | 6.5 | 827.7 | 806.9 | 792.9 | 835.9 | 782.4 | 753.4 | 614.5 | 765.1 | 777 | 756.6 | 688 | 690.1 | 729.4 | 390.4 | 364.8 | 379.9 | 358 | 356.2 | 359 | 350.1 | 343.8
1414.1 | 1251.1 | 469.4 | 187.76 | 219.4806 | 388.2 | 367.7 | 343.8 | 339.6 | 425.9 | 58.1 | 18.8 | 102.1 | 5 | 249.2 | 5.9 | 814.9 | 783 | 776.8 | 835.4 | 774.5 | 753.8 | 615 | 748.8 | 777 | 751.5 | 687.2 | 671.7 | 727.6 | 390.5 | 365.3 | 380.9 | 358.4 | 356.2 | 359.3 | 350.3 | 343.8
1415.1 | 1252.1 | 468.3 | 187.32 | 218.9663 | 389.5 | 367.1 | 345.1 | 340.3 | 424.4 | 58.1 | 18.8 | 102.1 | 4.9 | 249.1 | 5.7 | 809 | 769.1 | 766.4 | 834.4 | 767.5 | 754.1 | 614.9 | 725.6 | 776.9 | 746.8 | 686.6 | 656.9 | 725 | 390.6 | 365.6 | 381.9 | 358.6 | 356.3 | 359.7 | 350.5 | 343.9
1416.1 | 1253.1 | 468.2 | 187.28 | 218.9195 | 391.5 | 367.2 | 346.8 | 341.1 | 423.3 | 58.1 | 18.8 | 102.2 | 5.1 | 248.6 | 5.6 | 809.1 | 772.9 | 768.2 | 833.2 | 764 | 754.6 | 613.3 | 727.4 | 777.3 | 745.3 | 686 | 654 | 724.2 | 390.6 | 365.9 | 382.7 | 358.7 | 356.4 | 360 | 350.7 | 344
1417.1 | 1254.1 | 466.8 | 186.72 | 218.2649 | 393 | 368 | 347.6 | 341.9 | 425.4 | 58.2 | 18.8 | 102.2 | 5.2 | 249.6 | 5.6 | 809.5 | 781.7 | 777.5 | 832 | 764 | 754.9 | 611.1 | 736 | 777.6 | 745 | 685.8 | 659.9 | 723 | 390.7 | 366.4 | 383.9 | 358.8 | 356.4 | 360.5 | 351 | 344
1418.1 | 1255.1 | 467.7 | 187.08 | 218.6857 | 394.2 | 368.3 | 348.1 | 342.1 | 426.3 | 58.2 | 18.8 | 102.2 | 5.1 | 250.3 | 5.4 | 806.1 | 782.7 | 774.5 | 831.2 | 760.9 | 755.2 | 608.9 | 740.3 | 777.7 | 744.8 | 685.8 | 664.8 | 721.3 | 390.8 | 366.8 | 384.8 | 358.9 | 356.5 | 361 | 351.5 | 344.1
1419.1 | 1256.1 | 468.9 | 187.56 | 219.2468 | 395.2 | 368.8 | 349 | 342.9 | 427.9 | 58.2 | 18.8 | 102.2 | 5 | 250.8 | 5.4 | 808.8 | 790.7 | 778.5 | 830.4 | 760 | 755.4 | 606.2 | 742.6 | 777.8 | 744.2 | 685.7 | 670.5 | 722.1 | 390.9 | 367.3 | 385.2 | 358.9 | 356.5 | 361.3 | 351.8 | 344.2
1420.1 | 1257.1 | 469.1 | 187.64 | 219.3403 | 394.5 | 369.2 | 350 | 344 | 428.8 | 58.2 | 18.8 | 102.2 | 4.5 | 250.4 | 5.5 | 810.4 | 798.4 | 783.7 | 829.6 | 758.7 | 755.5 | 608.4 | 753.3 | 777.7 | 743.9 | 685.5 | 669.9 | 720.8 | 391.1 | 367.8 | 385.6 | 358.9 | 356.6 | 361.6 | 352 | 344.3
1421.1 | 1258.1 | 467.2 | 186.88 | 218.452 | 393.7 | 369.4 | 350.7 | 344.8 | 432.2 | 58.2 | 18.8 | 102.2 | 4.7 | 248.7 | 5.8 | 817 | 807.6 | 795 | 828.7 | 761.2 | 755.6 | 613.5 | 763.4 | 777.9 | 745.6 | 685.9 | 681.7 | 717.1 | 391.2 | 368.2 | 385.9 | 359.1 | 356.7 | 361.9 | 352.4 | 344.4
1422.1 | 1259.1 | 467.8 | 187.12 | 218.7325 | 393.1 | 370.4 | 350.9 | 345.3 | 441.8 | 58.3 | 18.8 | 102.2 | 4.8 | 247.1 | 5.9 | 822 | 814.4 | 805.4 | 827.9 | 765.7 | 755.5 | 610.8 | 768.7 | 777.6 | 746.7 | 686.4 | 690.8 | 713 | 391.3 | 368.4 | 386.2 | 359.1 | 356.7 | 362.3 | 352.6 | 344.5
1423.1 | 1260.1 | 467.8 | 187.12 | 218.7325 | 391.4 | 372.2 | 351 | 346.4 | 449.1 | 58.3 | 18.8 | 102.2 | 4.8 | 245.1 | 6.2 | 826.6 | 823.4 | 818.2 | 827.2 | 769.3 | 755.5 | 609.5 | 773.6 | 777.6 | 748.3 | 687.5 | 708 | 710.9 | 391.5 | 368.4 | 385.9 | 359.1 | 356.8 | 362.4 | 352.8 | 344.7
1424.1 | 1261.1 | 468 | 187.2 | 218.826 | 390.6 | 373 | 350.9 | 347.1 | 451.4 | 58.3 | 18.8 | 102.2 | 5.4 | 236.4 | 6 | 828.1 | 823 | 822.4 | 826.7 | 771.8 | 755.3 | 606.7 | 772.8 | 777.4 | 748.7 | 687.6 | 711 | 708.1 | 391.6 | 368.5 | 385.8 | 359.1 | 356.9 | 362.6 | 352.9 | 344.7
1425.1 | 1262.1 | 467.8 | 187.12 | 218.7325 | 389.8 | 373.1 | 350.7 | 347 | 463.5 | 58.3 | 18.8 | 102.2 | 4.8 | 236.6 | 6 | 828.9 | 815.1 | 825.8 | 826.4 | 773.8 | 755.2 | 601.6 | 758.8 | 776.6 | 747.4 | 687 | 702.4 | 704 | 391.7 | 368.7 | 385.9 | 359.1 | 356.9 | 362.7 | 353 | 344.8
1426.1 | 1263.1 | 467.8 | 187.12 | 218.7325 | 390.3 | 372.6 | 350.9 | 347.1 | 462.9 | 58.3 | 18.8 | 102.2 | 4.7 | 252.6 | 5.9 | 834.5 | 813.4 | 828.9 | 825.3 | 776.2 | 755 | 595.1 | 752.7 | 776.3 | 746.2 | 686.6 | 699.1 | 703.9 | 391.8 | 368.6 | 385.7 | 359.2 | 357 | 362.7 | 353 | 344.8
1427.1 | 1264.1 | 467.8 | 187.12 | 218.7325 | 389.7 | 372.2 | 351.2 | 347.5 | 458.5 | 58.3 | 18.8 | 102.2 | 4.3 | 266.3 | 5.1 | 834.5 | 810.9 | 827.6 | 824.9 | 773.5 | 755 | 591.1 | 742.1 | 775.6 | 744 | 685.5 | 696.7 | 705.4 | 392 | 368.6 | 385.6 | 359.3 | 357.1 | 362.6 | 352.9 | 344.8
1428.1 | 1265.1 | 468.6 | 187.44 | 219.1066 | 389.5 | 371.7 | 351 | 347.5 | 454 | 58.2 | 18.8 | 102.1 | 4.6 | 239.8 | 4.8 | 840.9 | 822.8 | 832 | 824.3 | 777.5 | 755.2 | 593.1 | 755.1 | 776.1 | 746.9 | 686.3 | 714.2 | 706.7 | 392.1 | 368.2 | 385.2 | 359.1 | 357.2 | 362.3 | 352.8 | 344.9
1429.1 | 1266.1 | 468.7 | 187.48 | 219.1533 | 389.1 | 371.3 | 350.3 | 347.2 | 455.3 | 58.2 | 18.8 | 102.1 | 4.9 | 230.3 | 5.7 | 841.2 | 827.9 | 834.9 | 824.2 | 782.3 | 755.1 | 594.8 | 764.2 | 776.3 | 748.9 | 687.4 | 726.6 | 704.7 | 392.2 | 367.9 | 384.7 | 359 | 357.2 | 362 | 352.7 | 344.9
1430.1 | 1267.1 | 467.1 | 186.84 | 218.4052 | 386.7 | 371.7 | 349.2 | 346.5 | 458.9 | 58.3 | 18.8 | 102.2 | 5.2 | 230.7 | 6.5 | 843.7 | 829.5 | 840.7 | 824 | 784.4 | 755.1 | 591.2 | 766.2 | 776.2 | 749.6 | 688.1 | 729.7 | 701.7 | 392.3 | 367.8 | 384.2 | 359 | 357.3 | 361.3 | 352.5 | 345
1431.1 | 1268.1 | 468.1 | 187.24 | 218.8728 | 385.7 | 371.1 | 348 | 345.9 | 457.9 | 58.4 | 18.8 | 102.3 | 5 | 216.1 | 6.1 | 849.2 | 832 | 844.1 | 824.5 | 786.9 | 754.9 | 586.9 | 765 | 775.7 | 749.7 | 687.9 | 735.1 | 699.6 | 392.4 | 367.5 | 383.6 | 358.9 | 357.4 | 360.8 | 352.2 | 345
1432.1 | 1269.1 | 468.7 | 187.48 | 219.1533 | 384.8 | 370.8 | 347.1 | 345 | 451.7 | 58.4 | 18.8 | 102.5 | 5.3 | 221.1 | 5.4 | 850.7 | 838.4 | 849 | 824.7 | 791.7 | 754.8 | 589.9 | 777.1 | 775.9 | 751.1 | 687.7 | 745.8 | 698.6 | 392.5 | 367.2 | 383.2 | 358.8 | 357.4 | 360.1 | 351.9 | 345
1433.1 | 1270.1 | 468.3 | 187.32 | 218.9663 | 383.8 | 370.5 | 346.2 | 343.9 | 452.6 | 58.5 | 18.8 | 102.8 | 4.8 | 216 | 5.2 | 856.2 | 844.4 | 854.5 | 824.4 | 795.1 | 754.5 | 593.2 | 783.3 | 775.9 | 752.7 | 688.4 | 753.1 | 698.1 | 392.6 | 366.9 | 382.7 | 358.7 | 357.4 | 359.6 | 351.6 | 345
1434.1 | 1271.1 | 468.2 | 187.28 | 218.9195 | 382.1 | 370.7 | 345.8 | 342.7 | 453.1 | 58.5 | 18.8 | 102.9 | 4.3 | 213.4 | 5 | 860.5 | 847.7 | 857.2 | 824.3 | 798.4 | 754.2 | 594.7 | 788.2 | 775.7 | 753.9 | 689.6 | 761.6 | 699.4 | 392.7 | 366.5 | 382.2 | 358.6 | 357.5 | 359.5 | 351.6 | 344.9
1435.1 | 1272.1 | 468.8 | 187.52 | 219.2001 | 381.1 | 371.3 | 345.3 | 342.2 | 446.6 | 58.6 | 18.8 | 102.9 | 4.6 | 223.1 | 4.7 | 866.6 | 854.8 | 856.1 | 825.4 | 797.9 | 753.9 | 598.2 | 791.3 | 775.1 | 755.2 | 690.6 | 764 | 701.1 | 392.8 | 366.2 | 381.7 | 358.5 | 357.5 | 359.5 | 351.6 | 344.9
1436.1 | 1273.1 | 468.6 | 187.44 | 219.1066 | 379.5 | 370.8 | 344.5 | 342 | 439.8 | 58.6 | 18.8 | 103 | 4.6 | 218.3 | 4.8 | 870.4 | 859.5 | 857.3 | 826.1 | 801.6 | 753.6 | 601.9 | 797.8 | 774.6 | 756.3 | 690.2 | 764.4 | 702.7 | 392.8 | 365.9 | 381.3 | 358.5 | 357.6 | 359.2 | 351.5 | 344.9
1437.1 | 1274.1 | 468.1 | 187.24 | 218.8728 | 379.1 | 369.7 | 343.8 | 341.3 | 440.8 | 58.7 | 18.8 | 103 | 4.2 | 212.9 | 4.5 | 869.9 | 860.9 | 856.5 | 827.3 | 804.2 | 753.2 | 602.6 | 793.8 | 774.1 | 756.1 | 690.4 | 764.9 | 702.3 | 392.9 | 365.7 | 380.9 | 358.5 | 357.6 | 359 | 351.4 | 345
1438.1 | 1275.1 | 468.4 | 187.36 | 219.013 | 378.7 | 369.6 | 344.2 | 340.9 | 437.2 | 58.7 | 18.8 | 103 | 4.4 | 212.7 | 4.2 | 872.6 | 857.1 | 857.8 | 827.3 | 807 | 753.1 | 601.7 | 793.1 | 774.5 | 756.5 | 690.9 | 768.5 | 702.6 | 392.9 | 365.4 | 380.4 | 358.3 | 357.6 | 359 | 351.5 | 345.1
1439.1 | 1276.1 | 467.9 | 187.16 | 218.7793 | 377.6 | 370.2 | 344.2 | 340.8 | 431.1 | 58.7 | 18.8 | 103 | 4 | 227 | 4.5 | 873.8 | 857.8 | 856.9 | 827.4 | 808.4 | 752.9 | 602.8 | 799.1 | 774.6 | 758 | 691.9 | 769.5 | 706.7 | 393 | 365 | 379.9 | 358.3 | 357.7 | 358.8 | 351.3 | 345.1
1440.1 | 1277.1 | 468 | 187.2 | 218.826 | 379.3 | 370.4 | 344 | 341 | 428 | 58.6 | 18.8 | 103 | 4.8 | 242 | 4.6 | 864 | 845.5 | 842 | 828.7 | 801.6 | 752.5 | 603.1 | 788.5 | 773.9 | 755 | 690.4 | 746.9 | 709.1 | 393 | 364.9 | 380 | 358.6 | 357.7 | 358.7 | 351.2 | 345
1441.1 | 1278.1 | 468.1 | 187.24 | 218.8728 | 381.8 | 369 | 343.4 | 340.8 | 423.8 | 58.7 | 18.8 | 103.1 | 4.7 | 242.4 | 4.6 | 850.5 | 830.6 | 823 | 829.2 | 794.8 | 752.4 | 599.7 | 771.2 | 773 | 751 | 687.9 | 726.7 | 717.3 | 393.1 | 364.8 | 379.9 | 358.7 | 357.7 | 358.5 | 351.1 | 345
1442.1 | 1279.1 | 468.4 | 187.36 | 219.013 | 384.4 | 368.5 | 342.8 | 340 | 419.4 | 58.7 | 18.8 | 103.1 | 4.9 | 238.4 | 4.5 | 848.8 | 827.6 | 818.6 | 829.2 | 790.1 | 752.4 | 597 | 765.7 | 772.4 | 748.3 | 686 | 714.7 | 724.4 | 393.1 | 364.7 | 379.8 | 358.7 | 357.8 | 358.4 | 351 | 345
1443.1 | 1280.1 | 468 | 187.2 | 218.826 | 386.5 | 368.6 | 342.4 | 339.9 | 416.9 | 58.7 | 18.8 | 103.2 | 5.3 | 247.3 | 4.3 | 846.8 | 826.4 | 814.9 | 829.3 | 788.2 | 752.5 | 596.2 | 769.5 | 772.5 | 748.1 | 684.8 | 719.9 | 728.4 | 393.1 | 364.7 | 379.9 | 358.8 | 357.8 | 358.3 | 351 | 345
1444.1 | 1281.1 | 468.7 | 187.48 | 219.1533 | 386.7 | 368.6 | 342.5 | 340.2 | 415.8 | 58.7 | 18.8 | 103.3 | 5.6 | 257.7 | 3.9 | 839.6 | 817.8 | 807.4 | 829.8 | 782.2 | 752.5 | 596.8 | 763.5 | 772 | 745.5 | 684.6 | 710.3 | 730.6 | 393.2 | 364.7 | 380 | 358.8 | 357.8 | 358 | 350.8 | 345
1445.1 | 1282.1 | 468 | 187.2 | 218.826 | 385.9 | 368.2 | 342.6 | 340.6 | 414.1 | 58.6 | 18.8 | 103.3 | 5.5 | 258.9 | 3.7 | 841.8 | 824.4 | 811.9 | 829.7 | 780.9 | 752.6 | 598.5 | 772.7 | 771.8 | 746.1 | 684.2 | 711.7 | 731.5 | 393.2 | 364.8 | 380.1 | 358.9 | 357.8 | 357.8 | 350.7 | 344.9
1446.1 | 1283.1 | 467.5 | 187 | 218.5922 | 385 | 367.1 | 343.7 | 340.3 | 412.4 | 58.6 | 18.8 | 103.3 | 5.3 | 250.7 | 3.5 | 845.9 | 826.5 | 822.5 | 829.4 | 782.6 | 752.6 | 595.1 | 772.3 | 771.6 | 745.3 | 684.1 | 714.4 | 736.6 | 393.2 | 364.7 | 380.1 | 358.8 | 357.8 | 357.8 | 350.9 | 345
1447.1 | 1284.1 | 468.3 | 187.32 | 218.9663 | 385.6 | 367 | 344.4 | 340.4 | 410.2 | 58.4 | 18.8 | 103.2 | 5.2 | 241.3 | 3.5 | 854.7 | 829.4 | 831.1 | 828.9 | 785.7 | 752.6 | 597.6 | 774.4 | 771.7 | 745.3 | 685.3 | 727.3 | 738.1 | 393.3 | 364.5 | 380 | 358.5 | 357.9 | 357.7 | 351.2 | 345.1
1448.1 | 1285.1 | 469.8 | 187.92 | 219.6677 | 387.3 | 368.5 | 344.5 | 340.5 | 410 | 58.3 | 18.8 | 103.2 | 4.6 | 238.8 | 3.4 | 862.8 | 836 | 837.9 | 827.9 | 789.6 | 752.5 | 601.1 | 783.6 | 771.5 | 747.4 | 686.7 | 735.4 | 735.9 | 393.3 | 364.5 | 380 | 358.5 | 357.9 | 357.5 | 351.1 | 345.2
1449.1 | 1286.1 | 469.5 | 187.8 | 219.5274 | 388 | 370.2 | 344.5 | 340.2 | 410.7 | 58.2 | 18.8 | 103.3 | 5 | 233 | 3.2 | 866.4 | 841.4 | 844.2 | 827.8 | 793.5 | 752.4 | 602.9 | 788.3 | 771.6 | 748.5 | 687.9 | 745.4 | 733.8 | 393.4 | 364.4 | 380 | 358.4 | 357.9 | 357.4 | 351.2 | 345.3
1450.1 | 1287.1 | 469.3 | 187.72 | 219.4339 | 388.4 | 370.2 | 344.8 | 339.7 | 410.8 | 58.2 | 18.8 | 103.3 | 4.4 | 218.3 | 2.9 | 867.5 | 842.9 | 841.1 | 827.9 | 793.2 | 752.2 | 604.1 | 790.9 | 771.4 | 749 | 688.7 | 741.7 | 734.8 | 393.4 | 364.4 | 380 | 358.5 | 357.9 | 357.4 | 351.3 | 345.3
1451.1 | 1288.1 | 469.3 | 187.72 | 219.4339 | 389.4 | 369.7 | 345 | 339.7 | 408.7 | 58.2 | 18.8 | 103.3 | 4.1 | 218.6 | 3 | 864.3 | 839.8 | 837.4 | 828.3 | 790.4 | 752 | 597.9 | 790.2 | 771 | 747.3 | 688 | 728.7 | 737.4 | 393.4 | 364.3 | 379.9 | 358.5 | 358 | 357.4 | 351.4 | 345.3
1452.1 | 1289.1 | 468.6 | 187.44 | 219.1066 | 390 | 368.6 | 345.3 | 339.4 | 405.2 | 58.2 | 18.8 | 103.2 | 4.1 | 225.1 | 3.3 | 858.8 | 836 | 825.9 | 828.5 | 787.6 | 751.9 | 597.8 | 792.6 | 770.7 | 747.2 | 687.4 | 723.6 | 741.4 | 393.5 | 364.2 | 379.8 | 358.5 | 358 | 357.4 | 351.4 | 345.2
1453.1 | 1290.1 | 468.9 | 187.56 | 219.2468 | 390.8 | 368.5 | 345.5 | 339.1 | 404.2 | 58.2 | 18.8 | 103.2 | 4.9 | 232.1 | 3.2 | 841.2 | 821 | 807.1 | 828.6 | 781.1 | 751.8 | 597 | 779.6 | 769.7 | 744.4 | 686.6 | 705.2 | 746.6 | 393.5 | 364.2 | 379.7 | 358.7 | 358 | 357.5 | 351.5 | 345.2
1454.1 | 1291.1 | 468.5 | 187.4 | 219.0598 | 392.5 | 368.4 | 345.8 | 339.2 | 403.1 | 58.2 | 18.8 | 103.1 | 4.4 | 241.3 | 3.1 | 829.1 | 802.8 | 791.3 | 828.5 | 774.8 | 751.9 | 592.8 | 755.6 | 768.9 | 739.4 | 685.1 | 685.9 | 753.7 | 393.5 | 364.2 | 379.7 | 358.9 | 358 | 357.5 | 351.5 | 345.2
1455.1 | 1292.1 | 468.4 | 187.36 | 219.013 | 396.7 | 368.2 | 345.9 | 339 | 402.7 | 58.3 | 18.8 | 103 | 4.6 | 247 | 3.3 | 830 | 803.5 | 791.7 | 827.8 | 772.4 | 752 | 593.6 | 756.4 | 768.5 | 738.4 | 684.4 | 685 | 755.1 | 393.6 | 364.1 | 379.7 | 359 | 358.1 | 357.5 | 351.4 | 345.2
1456.1 | 1293.1 | 468.2 | 187.28 | 218.9195 | 400.1 | 367.2 | 346.3 | 338.6 | 403.6 | 58.4 | 18.8 | 103 | 5 | 236.5 | 3.5 | 832 | 810 | 788 | 826.9 | 770.1 | 752.1 | 594.8 | 766 | 768.5 | 739.3 | 684.6 | 687.1 | 755.8 | 393.6 | 364.2 | 380.2 | 359 | 358.1 | 357.6 | 351.5 | 345.2
1457.1 | 1294.1 | 468.8 | 187.52 | 219.2001 | 397.9 | 366.5 | 346.6 | 338.3 | 401.4 | 58.4 | 18.8 | 102.9 | 5.5 | 238.3 | 4.1 | 836.4 | 811.4 | 792.8 | 826.1 | 768 | 752.1 | 594.1 | 771.1 | 768.5 | 738.7 | 684.4 | 687.3 | 759.3 | 393.6 | 364.2 | 380.3 | 358.9 | 358.1 | 357.8 | 351.6 | 345.2
1458.1 | 1295.1 | 466.2 | 186.48 | 217.9844 | 395.6 | 368.5 | 347.2 | 338.3 | 400.3 | 58.5 | 18.8 | 102.7 | 5.6 | 246.3 | 4.7 | 839.1 | 815.8 | 803.7 | 825.1 | 769.4 | 752.2 | 592.1 | 774.1 | 768.3 | 737.7 | 684.1 | 684.6 | 759.1 | 393.6 | 364.4 | 380.5 | 359 | 358.1 | 357.9 | 351.6 | 345.3
1459.1 | 1296.1 | 468.4 | 187.36 | 219.013 | 398.4 | 370.4 | 347.6 | 338.6 | 401.9 | 58.6 | 18.8 | 102.7 | 4.8 | 242.8 | 4.9 | 840.5 | 822.1 | 814.7 | 824.9 | 772.9 | 752.2 | 591.8 | 776.5 | 768.2 | 737.6 | 683.9 | 690.5 | 753.8 | 393.7 | 364.6 | 380.7 | 359.2 | 358.2 | 357.9 | 351.6 | 345.3
1460.1 | 1297.1 | 467.8 | 187.12 | 218.7325 | 399.6 | 370.3 | 347.9 | 338.8 | 404.4 | 58.7 | 18.8 | 102.6 | 5 | 244.9 | 5.1 | 837.3 | 821.5 | 817.6 | 825.1 | 773.7 | 752.2 | 592 | 773.3 | 768.3 | 737.5 | 684.2 | 691.7 | 748.4 | 393.7 | 364.8 | 380.9 | 359.3 | 358.2 | 357.8 | 351.6 | 345.4
1461.1 | 1298.1 | 468.2 | 187.28 | 218.9195 | 400.2 | 370.4 | 348.1 | 339 | 409.1 | 58.8 | 18.8 | 102.6 | 4.7 | 255.8 | 5 | 834.7 | 819.8 | 818.7 | 825.5 | 772.1 | 752.2 | 594.1 | 770.5 | 768.6 | 736.8 | 684 | 699.3 | 742.1 | 393.8 | 364.9 | 380.8 | 359.4 | 358.2 | 357.8 | 351.6 | 345.4
1462.1 | 1299.1 | 468.1 | 187.24 | 218.8728 | 399.7 | 369.9 | 348 | 338.8 | 421.8 | 58.8 | 18.8 | 102.6 | 5.2 | 251.5 | 4.8 | 831.8 | 818.9 | 816.1 | 825.8 | 769.3 | 752.3 | 595.2 | 768.7 | 768.7 | 735.6 | 683.8 | 694 | 735.2 | 393.8 | 365.1 | 380.8 | 359.5 | 358.2 | 357.5 | 351.5 | 345.4
1463.1 | 1300.1 | 468.3 | 187.32 | 218.9663 | 399.5 | 369.6 | 347.5 | 338.4 | 428.7 | 58.7 | 18.8 | 102.6 | 4.7 | 248.1 | 4.7 | 835.1 | 825.8 | 814.7 | 825.8 | 769.9 | 752.3 | 594.9 | 774.3 | 769.2 | 736.4 | 683.5 | 697.2 | 732.2 | 393.8 | 365.2 | 380.7 | 359.5 | 358.3 | 357.2 | 351.4 | 345.4
1464.1 | 1301.1 | 468.2 | 187.28 | 218.9195 | 399.3 | 369.5 | 347.2 | 338.3 | 424.1 | 58.7 | 18.8 | 102.6 | 5 | 244.6 | 4.9 | 845.8 | 833.4 | 822 | 825.1 | 773.4 | 752.3 | 595.7 | 775.2 | 769.4 | 736.6 | 683.8 | 713.6 | 736.2 | 393.9 | 365 | 380.5 | 359.6 | 358.3 | 357.2 | 351.5 | 345.4
1465.1 | 1302.1 | 468.5 | 187.4 | 219.0598 | 397.6 | 371.3 | 346.9 | 338.2 | 418.8 | 58.6 | 18.8 | 102.6 | 5.4 | 243.5 | 4.9 | 852.2 | 838.7 | 830.5 | 824.7 | 777.7 | 752.4 | 602.2 | 779.7 | 770.2 | 738.3 | 684.5 | 726.7 | 734.9 | 393.9 | 364.9 | 380.5 | 359.4 | 358.3 | 357.4 | 351.9 | 345.6
1466.1 | 1303.1 | 468.3 | 187.32 | 218.9663 | 398 | 373.1 | 346.6 | 338.4 | 418.9 | 58.6 | 18.8 | 102.7 | 5.3 | 240.3 | 4.9 | 854.3 | 847.6 | 831.5 | 824.4 | 779.9 | 752.5 | 605.1 | 783.6 | 770.9 | 741.4 | 686.7 | 737.9 | 728.1 | 393.9 | 365.1 | 380.5 | 359.4 | 358.3 | 357.4 | 351.9 | 345.7
1467.1 | 1304.1 | 468.4 | 187.36 | 219.013 | 400.7 | 375.4 | 346.4 | 338.5 | 425.2 | 58.5 | 18.8 | 102.8 | 5.2 | 236.9 | 4.9 | 853.6 | 846.6 | 826.7 | 824.1 | 777.7 | 752.3 | 606.7 | 788 | 771.3 | 741.8 | 687.1 | 732.1 | 722.7 | 394 | 365.3 | 380.6 | 359.5 | 358.3 | 357.7 | 352.1 | 345.6
1468.1 | 1305.1 | 468.5 | 187.4 | 219.0598 | 399.5 | 376.1 | 346.7 | 339.1 | 422.5 | 58.5 | 18.8 | 102.8 | 5.2 | 236.7 | 5 | 859.2 | 851 | 829.7 | 823.3 | 781.3 | 752.3 | 608.4 | 793.6 | 771.5 | 743.1 | 687.3 | 740.6 | 720.3 | 394 | 365.2 | 380.6 | 359.4 | 358.4 | 357.9 | 352.5 | 345.7
1469.1 | 1306.1 | 468.5 | 187.4 | 219.0598 | 396.5 | 377 | 346.8 | 340 | 418.6 | 58.4 | 18.8 | 102.9 | 4.9 | 230.6 | 4.7 | 861.5 | 854.4 | 830.5 | 823.2 | 784.6 | 752.2 | 609.4 | 794.9 | 771.2 | 744.5 | 688.1 | 747 | 717.2 | 394 | 365 | 380.4 | 359.3 | 358.4 | 358 | 352.7 | 345.8
1470.1 | 1307.1 | 468.5 | 187.4 | 219.0598 | 397.7 | 376.9 | 347.1 | 340.1 | 430.2 | 58.4 | 18.8 | 103 | 4.9 | 204.1 | 4.4 | 850.4 | 845.3 | 819.4 | 823.4 | 781.2 | 751.9 | 607.1 | 779.8 | 770.4 | 743.5 | 687.7 | 735.1 | 713.1 | 394.1 | 365.3 | 380.5 | 359.6 | 358.4 | 357.9 | 352.7 | 345.8
1471.1 | 1308.1 | 467.7 | 187.08 | 218.6857 | 400 | 376.5 | 347.2 | 339.8 | 431.5 | 58.3 | 18.8 | 103.1 | 5.3 | 189.3 | 4.5 | 832.8 | 823.8 | 801.5 | 823.7 | 774.1 | 751.8 | 601.9 | 755.2 | 768.9 | 738.9 | 685.9 | 712.9 | 712.4 | 394.1 | 365.8 | 381.6 | 360.2 | 358.4 | 358.1 | 352.8 | 345.8
1472.1 | 1309.1 | 468.8 | 187.52 | 219.2001 | 401.6 | 375.7 | 347.4 | 339.7 | 428.2 | 58.3 | 18.8 | 103.2 | 5.1 | 217.7 | 4.4 | 822.8 | 808.1 | 793.2 | 823.5 | 768.4 | 751.8 | 595.5 | 739.7 | 767.8 | 735.1 | 684.2 | 695 | 711.2 | 394.1 | 366.1 | 382.1 | 360.4 | 358.5 | 358.3 | 352.8 | 345.8
1473.1 | 1310.1 | 468.1 | 187.24 | 218.8728 | 403.3 | 376.9 | 348.3 | 340.2 | 427.1 | 58.3 | 18.8 | 103.2 | 4.9 | 246.1 | 3.9 | 812 | 793.9 | 782.7 | 823 | 762.7 | 751.9 | 588.7 | 725.1 | 766.6 | 731.6 | 682.9 | 679.8 | 708 | 394.2 | 366.4 | 382.5 | 360.5 | 358.5 | 358.3 | 352.9 | 345.8
1474.1 | 1311.1 | 468.9 | 187.56 | 219.2468 | 405.1 | 377.5 | 349 | 340.9 | 426.1 | 58.3 | 18.8 | 103.3 | 5.1 | 233.7 | 3.6 | 802.3 | 778.4 | 773.4 | 822.3 | 759.1 | 752 | 582.7 | 713.4 | 765.6 | 728.2 | 681.8 | 666.8 | 707.4 | 394.2 | 366.7 | 383.5 | 360.6 | 358.5 | 358.4 | 352.9 | 345.8
1475.1 | 1312.1 | 468.4 | 187.36 | 219.013 | 406.1 | 376.2 | 350 | 341.1 | 424.5 | 58.3 | 18.8 | 103.3 | 5 | 212.5 | 3.9 | 790.1 | 764.7 | 759.8 | 821.3 | 754.4 | 752.1 | 574.8 | 697.4 | 764.4 | 724.1 | 681 | 651.9 | 706.6 | 394.2 | 367 | 384.2 | 360.7 | 358.5 | 358.4 | 352.8 | 345.8
1476.1 | 1313.1 | 468.9 | 187.56 | 219.2468 | 409.2 | 375.4 | 351.3 | 341.3 | 423.5 | 58.4 | 18.8 | 103.4 | 5.4 | 209.3 | 4.3 | 781.5 | 756.8 | 751.2 | 820.4 | 749.2 | 752.2 | 569 | 685.7 | 763.3 | 720.3 | 680.2 | 640.8 | 704.1 | 394.3 | 367.4 | 384.6 | 360.9 | 358.6 | 358.6 | 352.8 | 345.8
1477.1 | 1314.1 | 468.5 | 187.4 | 219.0598 | 414.9 | 374.5 | 351.8 | 342.2 | 423.5 | 58.5 | 18.8 | 103.5 | 5.3 | 217.4 | 4.6 | 778.1 | 753.5 | 746 | 819.7 | 744.8 | 752.4 | 566.6 | 683.5 | 762.1 | 717.6 | 679.4 | 633 | 702.8 | 394.4 | 367.6 | 385.4 | 361 | 358.6 | 358.9 | 353 | 345.9
1478.1 | 1315.1 | 468.6 | 187.44 | 219.1066 | 417.1 | 373.8 | 352.4 | 343.4 | 421.6 | 58.5 | 18.8 | 103.5 | 4.8 | 226.3 | 5.2 | 780.6 | 759.8 | 743.6 | 818.8 | 741.7 | 752.5 | 568.8 | 686 | 761.6 | 716.4 | 678.9 | 634.7 | 705.8 | 394.4 | 367.7 | 385.7 | 361 | 358.6 | 359.2 | 353.2 | 346
1479.1 | 1316.1 | 468.6 | 187.44 | 219.1066 | 418 | 373.2 | 353.3 | 344.2 | 420.2 | 58.5 | 18.8 | 103.4 | 4.5 | 212.6 | 5.3 | 784.7 | 768.3 | 748.7 | 818.1 | 739.3 | 752.5 | 567.1 | 688.7 | 760.7 | 714.3 | 678.4 | 636.2 | 709.4 | 394.5 | 367.7 | 385.8 | 360.9 | 358.6 | 359.8 | 353.3 | 346.1
1480.1 | 1317.1 | 468.3 | 187.32 | 218.9663 | 421 | 373.6 | 353.7 | 344.8 | 418.4 | 58.6 | 18.8 | 103.4 | 4.8 | 201.5 | 5.5 | 779.7 | 757.9 | 745.8 | 817.4 | 735.2 | 752.5 | 567.2 | 683.6 | 759.8 | 711.6 | 678 | 625.4 | 709 | 394.5 | 368.1 | 386.3 | 361.1 | 358.7 | 360.2 | 353.7 | 346.1
1481.1 | 1318.1 | 468.5 | 187.4 | 219.0598 | 421.4 | 374.4 | 354.1 | 345.4 | 417.4 | 58.6 | 18.8 | 103.6 | 4.7 | 194.5 | 5 | 770.3 | 747.3 | 740.1 | 816.6 | 730.5 | 752.5 | 568.9 | 679.1 | 758.5 | 708.4 | 677.4 | 618.4 | 707.6 | 394.6 | 368.7 | 387.4 | 361.4 | 358.7 | 360.7 | 354 | 346.2
1482.1 | 1319.1 | 468.5 | 187.4 | 219.0598 | 425.1 | 375.3 | 355.1 | 346.3 | 417.1 | 58.6 | 18.8 | 103.7 | 4.9 | 171 | 4.7 | 766.6 | 745.1 | 738.2 | 815.7 | 727.6 | 752.4 | 564.7 | 681.9 | 757.8 | 707.2 | 676.9 | 615.4 | 702.8 | 394.7 | 369.3 | 388.3 | 361.7 | 358.7 | 360.8 | 354.2 | 346.3
1483.1 | 1320.1 | 468.4 | 187.36 | 219.013 | 430.6 | 376.4 | 356.6 | 347.3 | 418.9 | 58.6 | 18.8 | 103.7 | 4.5 | 173.3 | 4.4 | 763.9 | 748.3 | 739.8 | 814.7 | 724.8 | 752.2 | 565.5 | 689.8 | 757.9 | 706.6 | 676.6 | 613.5 | 697.1 | 394.8 | 369.8 | 388.9 | 362 | 358.8 | 361 | 354.5 | 346.4
1484.1 | 1321.1 | 468.2 | 187.28 | 218.9195 | 431.1 | 376.8 | 357.4 | 348.3 | 422.8 | 58.5 | 18.8 | 103.7 | 4.1 | 185.9 | 3.6 | 765 | 747.8 | 740 | 813.7 | 721.4 | 752.1 | 565.9 | 684.9 | 757.3 | 704.4 | 676.4 | 611.1 | 694.2 | 394.8 | 370.4 | 389.4 | 362.2 | 358.8 | 361.2 | 354.6 | 346.5
1485.1 | 1322.1 | 468.4 | 187.36 | 219.013 | 431.3 | 377.2 | 357.9 | 349.1 | 423.9 | 58.4 | 18.8 | 103.8 | 4.5 | 187.1 | 3.2 | 769.2 | 755.7 | 746.7 | 812.7 | 721.7 | 751.9 | 566.5 | 690 | 756.9 | 703.4 | 676 | 616.4 | 693.8 | 394.9 | 370.8 | 390.4 | 362.2 | 358.9 | 361.6 | 354.9 | 346.6
1486.1 | 1323.1 | 468.7 | 187.48 | 219.1533 | 427.7 | 377.5 | 358 | 349.8 | 425.1 | 58.3 | 18.8 | 103.9 | 4.6 | 189.1 | 3.5 | 781.5 | 772.4 | 765.2 | 811.4 | 725.1 | 751.6 | 571.1 | 711.3 | 757.7 | 707.2 | 676.7 | 635.4 | 694.6 | 395 | 370.8 | 390.5 | 362.1 | 358.9 | 361.9 | 355.2 | 346.7
1487.1 | 1324.1 | 469.9 | 187.96 | 219.7144 | 425.4 | 377.7 | 358.5 | 350.7 | 427.4 | 58.3 | 18.8 | 104 | 4.9 | 200.1 | 4.1 | 795.1 | 789.3 | 781.9 | 810.2 | 728.2 | 751.3 | 575.8 | 728.3 | 758.2 | 710.2 | 677.6 | 657.2 | 696.7 | 395.2 | 370.8 | 390.6 | 361.9 | 358.9 | 362.5 | 355.7 | 346.8
1488.1 | 1325.1 | 468.9 | 187.56 | 219.2468 | 422.9 | 378.5 | 358.5 | 350.6 | 425.3 | 58.4 | 18.8 | 104 | 4.8 | 200.9 | 4.1 | 803.2 | 800.1 | 788.7 | 809.7 | 729.7 | 750.8 | 578.5 | 740.1 | 758.9 | 712.2 | 677.6 | 667.8 | 700.2 | 395.3 | 370.9 | 390.7 | 361.9 | 359 | 362.5 | 356.1 | 347
1489.1 | 1326.1 | 468 | 187.2 | 218.826 | 422.4 | 379.7 | 357.9 | 350.4 | 427.2 | 58.4 | 18.8 | 103.9 | 5 | 208.7 | 4.2 | 802.2 | 796.9 | 792.5 | 809.6 | 730.2 | 750.4 | 580 | 735.5 | 758.5 | 711.2 | 677 | 663.1 | 698.8 | 395.4 | 371.2 | 390.6 | 362.1 | 359 | 362.4 | 356.1 | 347
1490.1 | 1327.1 | 468.4 | 187.36 | 219.013 | 421 | 379.9 | 357.5 | 350.1 | 424.6 | 58.5 | 18.8 | 103.8 | 5.2 | 233.8 | 4.5 | 809 | 803.7 | 804.8 | 808.8 | 735.9 | 750.1 | 578.9 | 733.3 | 758.2 | 710.5 | 676.4 | 672.7 | 696.4 | 395.5 | 371.1 | 390.3 | 362.1 | 359.1 | 362.4 | 356.1 | 347.1
1491.1 | 1328.1 | 468.9 | 187.56 | 219.2468 | 420 | 380.2 | 358.1 | 349 | 420 | 58.6 | 18.8 | 103.9 | 4.5 | 241.6 | 3.8 | 816.2 | 806 | 811.3 | 808.6 | 739.8 | 749.6 | 577.8 | 732 | 757.5 | 710.1 | 675.9 | 678 | 694.3 | 395.6 | 370.7 | 389.6 | 361.9 | 359.1 | 362.2 | 355.9 | 347.1
1492.1 | 1329.1 | 468.8 | 187.52 | 219.2001 | 419.1 | 380.8 | 357.9 | 347.8 | 416.7 | 58.6 | 18.8 | 103.9 | 4.8 | 197.6 | 3.3 | 823.7 | 810.7 | 819.4 | 808.2 | 743 | 749.2 | 579.2 | 737.5 | 757.2 | 711 | 675.6 | 685.5 | 694.6 | 395.7 | 370.6 | 389 | 361.9 | 359.2 | 362 | 355.8 | 347.1
1493.1 | 1330.1 | 466.5 | 186.6 | 218.1246 | 420.1 | 380.9 | 357.2 | 347 | 427.2 | 58.5 | 18.8 | 103.8 | 4.6 | 171.7 | 3.8 | 820.8 | 816.8 | 819.9 | 807.9 | 743.6 | 748.9 | 580.6 | 748 | 757.1 | 713.3 | 676 | 693.1 | 695.6 | 395.8 | 370.8 | 388.8 | 362.1 | 359.2 | 361.9 | 355.9 | 347.1
1494.1 | 1331.1 | 467.2 | 186.88 | 218.452 | 425.7 | 380.6 | 356.1 | 346.1 | 433.5 | 58.5 | 18.8 | 103.9 | 5.3 | 197.8 | 4.6 | 813.4 | 806.6 | 810.9 | 808.1 | 742.4 | 748.6 | 580.2 | 743.1 | 756.7 | 712.6 | 676 | 682.3 | 693.4 | 395.9 | 370.9 | 388.8 | 362.3 | 359.3 | 361.9 | 355.8 | 347.2
1495.1 | 1332.1 | 467.7 | 187.08 | 218.6857 | 427.3 | 380.3 | 355.5 | 345.1 | 432.1 | 58.5 | 18.8 | 104.1 | 4.6 | 190.9 | 5.1 | 805.2 | 793.3 | 797.8 | 808 | 737.6 | 748.3 | 576.6 | 722.8 | 755.3 | 708.3 | 674.9 | 670.4 | 693.9 | 396 | 371 | 389.3 | 362.6 | 359.3 | 361.8 | 355.7 | 347.2
1496.1 | 1333.1 | 467 | 186.8 | 218.3584 | 427.6 | 379.7 | 355.6 | 344.8 | 428.3 | 58.6 | 18.8 | 104.2 | 4.5 | 171.6 | 5.5 | 803.2 | 791.7 | 791 | 807.8 | 735 | 748 | 574.7 | 720.2 | 754.1 | 707.6 | 674 | 663.1 | 699.7 | 396.1 | 371.1 | 389.5 | 362.7 | 359.3 | 361.7 | 355.5 | 347.2
1497.1 | 1334.1 | 466.4 | 186.56 | 218.0779 | 427.6 | 378.8 | 356.5 | 344.7 | 425.3 | 58.6 | 18.8 | 104.3 | 4.5 | 169.8 | 5.5 | 807.9 | 793.7 | 793.6 | 807.4 | 735.7 | 747.8 | 573.2 | 714.1 | 753.3 | 705.8 | 673 | 659.3 | 706 | 396.1 | 371.4 | 389.6 | 362.8 | 359.4 | 361.5 | 355.3 | 347.2
1498.1 | 1335.1 | 467.4 | 186.96 | 218.5455 | 427.1 | 378.6 | 356.3 | 344.7 | 421.7 | 58.7 | 18.8 | 104.3 | 4.5 | 188.3 | 5.1 | 816.3 | 800.9 | 797.8 | 806.5 | 736.8 | 747.6 | 572.9 | 716.5 | 752.7 | 704.6 | 672.5 | 665.9 | 709.8 | 396.2 | 371.6 | 390.1 | 362.8 | 359.4 | 361.3 | 355.2 | 347.2
1499.1 | 1336.1 | 467.6 | 187.04 | 218.639 | 427.9 | 378.5 | 356.3 | 344.5 | 419.2 | 58.7 | 18.8 | 104.2 | 4.5 | 201.6 | 4.8 | 829.8 | 812.7 | 809.1 | 805.3 | 742.2 | 747.4 | 575.2 | 729.9 | 752.8 | 706.8 | 672.8 | 679.6 | 715.4 | 396.3 | 371.7 | 390.3 | 362.7 | 359.5 | 361.1 | 355.2 | 347.3
1500.1 | 1337.1 | 466.5 | 186.6 | 218.1246 | 429 | 377.8 | 356.6 | 344.7 | 417.7 | 58.8 | 18.8 | 104.2 | 4.6 | 223 | 4.6 | 836 | 821.7 | 815.6 | 804.6 | 745.7 | 747.1 | 579.2 | 742.6 | 753.1 | 708.1 | 673.4 | 688 | 719.1 | 396.4 | 371.6 | 390 | 362.6 | 359.5 | 360.8 | 355.2 | 347.4
1501.1 | 1338.1 | 468.7 | 187.48 | 219.1533 | 428 | 377.4 | 356.7 | 344.6 | 415.6 | 58.9 | 18.8 | 104.3 | 4.7 | 209.3 | 3.8 | 841.8 | 829.6 | 815.2 | 804.2 | 746.6 | 746.9 | 583.2 | 755.6 | 753.8 | 710.6 | 674.6 | 698.6 | 722 | 396.4 | 371.5 | 389.7 | 362.5 | 359.5 | 360.5 | 355.1 | 347.5
1502.1 | 1339.1 | 468.7 | 187.48 | 219.1533 | 434.6 | 376.9 | 355.9 | 344.4 | 412.9 | 58.9 | 18.8 | 104.3 | 4.3 | 165 | 3.7 | 829.5 | 820.2 | 801.9 | 804.4 | 742.7 | 746.6 | 581.8 | 748.8 | 753.4 | 709.2 | 674.8 | 687.4 | 723.4 | 396.5 | 371.6 | 389.5 | 362.5 | 359.6 | 360.4 | 354.8 | 347.5
1503.1 | 1340.1 | 469.4 | 187.76 | 219.4806 | 439.5 | 377 | 355.4 | 344 | 411.6 | 58.7 | 18.8 | 104.2 | 5.2 | 171.7 | 3.7 | 823.4 | 811.5 | 798.9 | 804.7 | 742.9 | 746.4 | 578.9 | 735.3 | 752.2 | 705.9 | 673.8 | 672.7 | 723.9 | 396.6 | 371.6 | 389.4 | 362.7 | 359.6 | 360.4 | 354.8 | 347.5
1504.1 | 1341.1 | 469.2 | 187.68 | 219.3871 | 440.9 | 377.3 | 356.1 | 343.2 | 411 | 58.7 | 18.8 | 104.2 | 4.8 | 192.4 | 4 | 822 | 810.9 | 802.3 | 804.5 | 744.2 | 746.1 | 571.5 | 729.7 | 750.9 | 705.2 | 672.7 | 669.9 | 721.6 | 396.6 | 371.3 | 389.1 | 362.7 | 359.6 | 360.4 | 354.6 | 347.4
1505.1 | 1342.1 | 467.2 | 186.88 | 218.452 | 439.8 | 376.8 | 356.3 | 342.7 | 411.8 | 58.8 | 18.8 | 104.2 | 4.5 | 191.1 | 4.7 | 831.4 | 819.9 | 807.6 | 804 | 747.1 | 745.8 | 570.2 | 740.2 | 750.6 | 706.6 | 672.4 | 686.4 | 720.2 | 396.7 | 371 | 388.7 | 362.7 | 359.7 | 360.4 | 354.5 | 347.4
1506.1 | 1343.1 | 466.9 | 186.76 | 218.3117 | 437.2 | 376.3 | 356.2 | 342.6 | 412.7 | 58.9 | 18.8 | 104.2 | 4.8 | 179.8 | 5 | 834.4 | 830.1 | 812 | 804 | 748.7 | 745.6 | 574.3 | 752.1 | 751 | 709.5 | 673 | 696.7 | 717 | 396.8 | 371 | 388.4 | 362.6 | 359.7 | 360.5 | 354.4 | 347.5
1507.1 | 1344.1 | 468.6 | 187.44 | 219.1066 | 438.5 | 376.7 | 355.9 | 342.9 | 414 | 59.1 | 18.8 | 104.2 | 5.1 | 182.1 | 5 | 828 | 821.4 | 807.1 | 804.5 | 744.5 | 745.2 | 577.8 | 746 | 750.7 | 709 | 673.2 | 684.3 | 714.6 | 396.8 | 371.2 | 388.5 | 362.9 | 359.7 | 360.7 | 354.4 | 347.5
1508.1 | 1345.1 | 466.5 | 186.6 | 218.1246 | 446.3 | 377.1 | 355.8 | 343.1 | 414.5 | 59.2 | 18.7 | 104.4 | 5.5 | 186.1 | 4.8 | 818.9 | 813 | 790 | 804.8 | 740.9 | 744.9 | 575.7 | 733.1 | 749.9 | 705.2 | 672.3 | 672 | 714.6 | 396.9 | 371.3 | 388.6 | 363.2 | 359.8 | 361.2 | 354.5 | 347.5
1509.1 | 1346.1 | 468.4 | 187.36 | 219.013 | 451 | 377.1 | 356.6 | 343.6 | 414.2 | 59.3 | 18.7 | 104.6 | 5.3 | 192.9 | 4.9 | 804.5 | 801.7 | 774.7 | 804.8 | 736.6 | 744.7 | 573.4 | 725.6 | 749.1 | 702.8 | 671.6 | 660.3 | 712.9 | 396.9 | 371.4 | 388.8 | 363.3 | 359.8 | 361.5 | 354.8 | 347.6
1510.1 | 1347.1 | 468.1 | 187.24 | 218.8728 | 449.8 | 376.8 | 357.2 | 344.4 | 417.9 | 59.4 | 18.7 | 104.7 | 5.7 | 190.1 | 5.4 | 806 | 805 | 777.4 | 804.1 | 736.3 | 744.5 | 571.5 | 721.4 | 748.2 | 702.5 | 670.9 | 664.3 | 714.3 | 397 | 371.5 | 388.9 | 363.3 | 359.8 | 361.2 | 354.7 | 347.6
1511.1 | 1348.1 | 468.3 | 187.32 | 218.9663 | 449.8 | 376.1 | 357.2 | 344.8 | 418.7 | 59.5 | 18.7 | 104.8 | 5.7 | 185.5 | 5.3 | 799.5 | 796.4 | 771.5 | 803.6 | 732.4 | 744.3 | 571 | 710.3 | 747.2 | 699.4 | 670.3 | 656.2 | 719.5 | 397 | 371.6 | 389 | 363.4 | 359.9 | 360.8 | 354.7 | 347.6
1512.1 | 1349.1 | 467.9 | 187.16 | 218.7793 | 451.5 | 375.5 | 357.3 | 345.1 | 417.4 | 59.6 | 18.7 | 104.9 | 5.4 | 183 | 5.2 | 792.3 | 788.4 | 764.6 | 803 | 728.7 | 744.1 | 570.9 | 699.1 | 745.9 | 696.4 | 669.8 | 645.5 | 718.3 | 397.1 | 371.7 | 389 | 363.6 | 359.9 | 360.6 | 354.7 | 347.6
1513.1 | 1350.1 | 467.8 | 187.12 | 218.7325 | 452.1 | 375.1 | 357.4 | 345.5 | 417.1 | 59.7 | 18.7 | 105 | 5.2 | 186.3 | 5.3 | 787.6 | 780.4 | 755.7 | 802.5 | 725.5 | 743.9 | 570.9 | 693.5 | 744.7 | 694.2 | 669.2 | 638.4 | 715.3 | 397.2 | 371.7 | 389.1 | 363.8 | 359.9 | 360.8 | 354.7 | 347.7
1514.1 | 1351.1 | 468.5 | 187.4 | 219.0598 | 454.4 | 374.5 | 357.9 | 346 | 415.7 | 59.8 | 18.7 | 105.1 | 5.2 | 185.6 | 5.4 | 778.4 | 771.4 | 743.3 | 801.4 | 721.8 | 743.7 | 567.1 | 683.8 | 743.2 | 691.7 | 668.8 | 632.2 | 714.3 | 397.2 | 371.7 | 389.2 | 363.8 | 360 | 361.2 | 354.8 | 347.7
1515.1 | 1352.1 | 468.1 | 187.24 | 218.8728 | 452.4 | 373.8 | 358.7 | 346.5 | 415 | 59.9 | 18.7 | 105.2 | 5.4 | 178.6 | 5.5 | 764.4 | 752.4 | 731.1 | 800.4 | 716.3 | 743.4 | 563.7 | 667.8 | 741.6 | 687.7 | 668.3 | 617.1 | 712.1 | 397.3 | 372.1 | 390 | 363.9 | 360 | 361.6 | 354.8 | 347.7
1516.1 | 1353.1 | 468.7 | 187.48 | 219.1533 | 451.5 | 373.7 | 358.8 | 347 | 414.4 | 60 | 18.7 | 105.2 | 4.7 | 181.1 | 5.6 | 752 | 738 | 722.1 | 799.5 | 711.8 | 743.2 | 559.7 | 656.4 | 739.5 | 684.2 | 667.7 | 603.1 | 707.3 | 397.3 | 372.4 | 391 | 364.2 | 360 | 361.9 | 355.2 | 347.8
1517.1 | 1354.1 | 467.8 | 187.12 | 218.7325 | 456 | 373.1 | 359.9 | 347.7 | 413.4 | 60.1 | 18.7 | 105.2 | 4.8 | 189.4 | 5.8 | 749.2 | 731.7 | 717.3 | 798.5 | 707.7 | 742.8 | 555 | 648.2 | 737.8 | 681.1 | 667 | 597.6 | 701.1 | 397.4 | 372.8 | 391.7 | 364.4 | 360.1 | 362.3 | 355.5 | 347.8
1518.1 | 1355.1 | 467 | 186.8 | 218.3584 | 460.5 | 372.5 | 360.8 | 348.5 | 413.1 | 60.1 | 18.7 | 105.2 | 5.1 | 186.3 | 6.3 | 757.8 | 737.5 | 726.9 | 797.2 | 707.7 | 742.5 | 551 | 648.5 | 736.6 | 679.4 | 666.3 | 600.1 | 697 | 397.5 | 373 | 391.9 | 364.6 | 360.1 | 362.6 | 355.7 | 347.9
1519.1 | 1356.1 | 469.1 | 187.64 | 219.3403 | 460.5 | 371.7 | 361.1 | 349.2 | 413.3 | 60.1 | 18.7 | 105.3 | 5 | 168.1 | 6.1 | 769.8 | 753.9 | 739.2 | 796 | 709 | 742.1 | 549.5 | 659.7 | 735.9 | 679.7 | 665.9 | 610.2 | 696.6 | 397.6 | 373.1 | 391.9 | 364.5 | 360.1 | 362.4 | 356 | 348.1
1520.1 | 1357.1 | 468.3 | 187.32 | 218.9663 | 458.8 | 370.3 | 360.7 | 349.7 | 412.6 | 60.1 | 18.7 | 105.2 | 5.5 | 161.2 | 5.3 | 779.4 | 760.8 | 755.2 | 795.4 | 711.5 | 741.7 | 548.1 | 669.3 | 735.6 | 679 | 665.5 | 620.4 | 696.5 | 397.7 | 373.4 | 391.8 | 364.5 | 360.2 | 362.5 | 356.3 | 348.2
1521.1 | 1358.1 | 469.2 | 187.68 | 219.3871 | 459.6 | 369.1 | 360.4 | 349.6 | 414.9 | 60.2 | 18.7 | 105.2 | 5.5 | 165.8 | 4.2 | 779.6 | 759.6 | 758.4 | 795 | 712 | 741.3 | 553.7 | 680.8 | 735.9 | 679.9 | 665.6 | 622.5 | 693 | 397.8 | 373.6 | 392 | 364.7 | 360.2 | 362.9 | 356.5 | 348.3
1522.1 | 1359.1 | 468.4 | 187.36 | 219.013 | 462.7 | 369.3 | 360.5 | 349.6 | 417.1 | 60.2 | 18.7 | 105.3 | 5.5 | 173.3 | 3.6 | 771.1 | 746.9 | 752.8 | 794.6 | 707.8 | 740.9 | 553.1 | 666.7 | 734.4 | 676.1 | 665.5 | 609.6 | 688.6 | 397.8 | 373.8 | 392.2 | 364.9 | 360.3 | 363.5 | 356.7 | 348.3
1523.1 | 1360.1 | 469.1 | 187.64 | 219.3403 | 469.2 | 369.8 | 361 | 350 | 419.5 | 60.3 | 18.7 | 105.4 | 5.5 | 186.8 | 3.2 | 763 | 741.9 | 741.2 | 794.1 | 704.3 | 740.4 | 550.9 | 661.7 | 732.9 | 674.2 | 665.2 | 602.2 | 685.3 | 397.9 | 374.2 | 392.7 | 365.2 | 360.3 | 363.2 | 356.7 | 348.3
1524.1 | 1361.1 | 468.9 | 187.56 | 219.2468 | 467.5 | 370.3 | 362 | 350.7 | 420.2 | 60.3 | 18.7 | 105.6 | 4.7 | 214.5 | 2.8 | 757.7 | 744.5 | 736.9 | 793.2 | 701.5 | 740 | 548.2 | 660.7 | 731.8 | 672.9 | 664.7 | 597.5 | 683.1 | 398 | 374.4 | 392.9 | 365.4 | 360.3 | 362.9 | 356.5 | 348.4
1525.1 | 1362.1 | 468.4 | 187.36 | 219.013 | 467.5 | 370.2 | 362.9 | 351.1 | 419.9 | 60.3 | 18.7 | 105.6 | 4.7 | 207 | 2.8 | 759.5 | 759.2 | 740.4 | 792.4 | 700.5 | 739.5 | 548.7 | 682.8 | 732.7 | 674.6 | 664.4 | 603.5 | 683.2 | 398.1 | 374.6 | 392.9 | 365.4 | 360.4 | 362.8 | 356.5 | 348.4
1526.1 | 1363.1 | 467.9 | 187.16 | 218.7793 | 464.8 | 370 | 363.3 | 351.1 | 419.8 | 60.4 | 18.7 | 105.6 | 4.2 | 187.1 | 3.8 | 760.4 | 766.4 | 739 | 792.1 | 697.9 | 739.1 | 552.9 | 696.1 | 733.7 | 675 | 664.1 | 601.4 | 685.4 | 398.2 | 374.6 | 392.8 | 365.3 | 360.4 | 363 | 356.6 | 348.5
1527.1 | 1364.1 | 468.2 | 187.28 | 218.9195 | 460.6 | 369.8 | 363.4 | 351.2 | 420 | 60.4 | 18.7 | 105.7 | 4.4 | 181.4 | 5.4 | 764.4 | 776.4 | 746.7 | 791.5 | 697.8 | 738.6 | 558.9 | 708 | 734.3 | 675.6 | 664 | 610.1 | 686.6 | 398.3 | 374.5 | 392.8 | 365.3 | 360.5 | 363.4 | 356.9 | 348.5
1528.1 | 1365.1 | 468.2 | 187.28 | 218.9195 | 454.2 | 370.6 | 363.4 | 350.9 | 419.9 | 60.4 | 18.7 | 105.8 | 4.4 | 192.6 | 6.2 | 775.9 | 789.7 | 759.2 | 791 | 699.2 | 738.1 | 565.2 | 727.4 | 735.4 | 679 | 664 | 626 | 688.3 | 398.4 | 374.5 | 392.9 | 365.3 | 360.5 | 363.6 | 357.1 | 348.6
1529.1 | 1366.1 | 468.8 | 187.52 | 219.2001 | 450.8 | 371.5 | 363.6 | 351.3 | 420.7 | 60.4 | 18.7 | 105.9 | 4.2 | 193.9 | 6.1 | 784.7 | 799 | 771.1 | 790.5 | 703.7 | 737.7 | 568.4 | 736.4 | 736.3 | 680.5 | 664.2 | 638.6 | 687.7 | 398.5 | 374.1 | 392.9 | 365.2 | 360.6 | 363.9 | 357.2 | 348.7
1530.1 | 1367.1 | 468.5 | 187.4 | 219.0598 | 448.6 | 371.4 | 363.3 | 351.4 | 423.2 | 60.4 | 18.7 | 106 | 4.2 | 190.9 | 6.2 | 787.1 | 803.6 | 777.8 | 790.1 | 706.9 | 737.3 | 570.3 | 737.8 | 736.3 | 681.5 | 663.9 | 640.2 | 685.3 | 398.6 | 374.3 | 393 | 365.2 | 360.6 | 364 | 357.3 | 348.7
1531.1 | 1368.1 | 468.8 | 187.52 | 219.2001 | 447.2 | 372.4 | 362.4 | 351.1 | 432 | 60.4 | 18.7 | 106 | 4.2 | 188.1 | 6.2 | 798.3 | 815.4 | 788.7 | 790 | 711.8 | 736.9 | 572.9 | 748.2 | 737 | 684.5 | 664.4 | 650 | 683.6 | 398.7 | 374.4 | 393 | 365.2 | 360.7 | 364 | 357.4 | 348.8
1532.1 | 1369.1 | 468.8 | 187.52 | 219.2001 | 443.3 | 373 | 361.7 | 350.7 | 431.2 | 60.4 | 18.7 | 106 | 4.2 | 172.2 | 6.4 | 810.2 | 826.5 | 793.5 | 789.8 | 716.2 | 736.5 | 572.7 | 750.8 | 737.2 | 687.1 | 665.6 | 665.4 | 688.3 | 398.8 | 374.1 | 392.7 | 365.1 | 360.7 | 363.9 | 357.4 | 348.9
1533.1 | 1370.1 | 468.8 | 187.52 | 219.2001 | 439.5 | 373.9 | 361.3 | 350.4 | 424.9 | 60.4 | 18.7 | 105.9 | 4.3 | 192.4 | 7.3 | 813.7 | 831.9 | 800.1 | 789.8 | 721.3 | 736.2 | 576.9 | 759.3 | 738.5 | 689.4 | 666.1 | 677.8 | 692.9 | 398.9 | 373.9 | 392.4 | 365 | 360.7 | 363.7 | 357.3 | 348.9
1534.1 | 1371.1 | 468.1 | 187.24 | 218.8728 | 438.7 | 374.6 | 360.6 | 349.9 | 430.3 | 60.4 | 18.7 | 106 | 5 | 193.3 | 8.1 | 808.9 | 831 | 803.6 | 790.3 | 725.4 | 735.9 | 581.3 | 764.4 | 739.1 | 691.9 | 666 | 681.9 | 688.5 | 399 | 374 | 392.6 | 365.3 | 360.8 | 363.6 | 357.2 | 348.9
1535.1 | 1372.1 | 468.5 | 187.4 | 219.0598 | 440.1 | 377 | 359.7 | 349.3 | 452 | 60.4 | 18.7 | 106 | 5 | 182.6 | 8 | 801.2 | 826.5 | 800 | 791 | 726.4 | 735.6 | 581.3 | 763.6 | 739.3 | 693.2 | 666 | 674.3 | 683 | 399 | 374 | 392.6 | 365.5 | 360.8 | 363.5 | 357 | 348.9
1536.1 | 1373.1 | 468.3 | 187.32 | 218.9663 | 437.7 | 378 | 360.1 | 349.3 | 459.6 | 60.2 | 18.7 | 106 | 5.2 | 186 | 7.9 | 795.4 | 823.6 | 791.3 | 791.2 | 724.6 | 735.2 | 579 | 753.6 | 738.9 | 692.4 | 665.4 | 670.7 | 677.9 | 399.1 | 374.1 | 392.7 | 365.7 | 360.9 | 363.4 | 356.9 | 348.9
1537.1 | 1374.1 | 468.9 | 187.56 | 219.2468 | 434.5 | 378.1 | 360.9 | 349.7 | 463.4 | 60.2 | 18.7 | 106 | 5 | 177.7 | 9.2 | 791.3 | 822.9 | 790 | 791.3 | 724.7 | 735 | 577.9 | 755.4 | 739 | 693.3 | 664.7 | 669.1 | 674 | 399.2 | 374.2 | 392.6 | 365.7 | 360.9 | 363.4 | 356.6 | 348.9
1538.1 | 1375.1 | 468.6 | 187.44 | 219.1066 | 432.5 | 377.3 | 361.6 | 349.8 | 462.4 | 60.1 | 18.7 | 106 | 4.7 | 201.6 | 9.7 | 793.7 | 825.8 | 792.3 | 791.2 | 723.7 | 734.8 | 579.4 | 760.3 | 739.5 | 695.4 | 664.5 | 669.4 | 669.6 | 399.2 | 374.4 | 392.8 | 366 | 361 | 363.6 | 356.5 | 349
1539.1 | 1376.1 | 468.7 | 187.48 | 219.1533 | 431.2 | 376.7 | 361.8 | 350.2 | 458.1 | 60 | 18.7 | 105.9 | 4.9 | 199.4 | 9 | 803.8 | 829.1 | 802.7 | 790.6 | 728.7 | 734.7 | 580.1 | 765.3 | 740.2 | 697.7 | 664.9 | 679.1 | 668.5 | 399.3 | 374.5 | 392.8 | 365.9 | 361 | 363.9 | 356.5 | 349
1540.1 | 1377.1 | 468.9 | 187.56 | 219.2468 | 427.8 | 376.7 | 361.5 | 350.4 | 450.8 | 60 | 18.7 | 105.8 | 4.7 | 200.7 | 8.9 | 811.1 | 836.9 | 810.6 | 790.4 | 733.7 | 734.5 | 582.4 | 770.8 | 740.9 | 700.4 | 665.5 | 691.4 | 670.2 | 399.4 | 374.5 | 392.7 | 365.8 | 361 | 364 | 356.6 | 349.1
1541.1 | 1378.1 | 468.8 | 187.52 | 219.2001 | 424.4 | 377.4 | 361.1 | 350 | 451.8 | 60.1 | 18.7 | 105.8 | 5 | 199.3 | 8.6 | 805.3 | 831.9 | 803.2 | 790.6 | 733.7 | 734.3 | 583.1 | 766.9 | 740.8 | 700.8 | 664.8 | 686.2 | 667.6 | 399.5 | 374.8 | 392.7 | 365.9 | 361.1 | 364 | 356.6 | 349.2
1542.1 | 1379.1 | 469.2 | 187.68 | 219.3871 | 423.9 | 379.2 | 360.3 | 349.1 | 458.3 | 60.1 | 18.7 | 105.7 | 4.9 | 195 | 8.1 | 795 | 819.7 | 792.1 | 790.9 | 729.4 | 734.2 | 582.4 | 755.7 | 740 | 699.2 | 664.3 | 669.5 | 661.7 | 399.5 | 375.3 | 393.2 | 366.3 | 361.1 | 363.9 | 356.4 | 349.1
1543.1 | 1380.1 | 468.8 | 187.52 | 219.2001 | 425.2 | 379.8 | 360.2 | 348.2 | 456.4 | 60.1 | 18.7 | 105.7 | 4.6 | 183.7 | 7.4 | 794.2 | 820.1 | 790.8 | 791 | 731.3 | 734.1 | 581.2 | 752 | 739.6 | 699.2 | 663.7 | 664.1 | 657.4 | 399.6 | 375.5 | 393.5 | 366.4 | 361.1 | 363.8 | 356.2 | 349.1
1544.1 | 1381.1 | 468.9 | 187.56 | 219.2468 | 424.5 | 379.6 | 360.7 | 347.3 | 455.3 | 60.2 | 18.7 | 105.6 | 4.8 | 186.2 | 7.4 | 799.2 | 829.6 | 798.6 | 790.9 | 734.3 | 734 | 580.2 | 762.9 | 739.8 | 701.7 | 663.4 | 672.6 | 656.3 | 399.7 | 375.6 | 393.5 | 366.3 | 361.2 | 363.7 | 356.2 | 349.1
1545.1 | 1382.1 | 468.7 | 187.48 | 219.1533 | 421.9 | 378.9 | 360.8 | 346.9 | 453.1 | 60.3 | 18.7 | 105.5 | 5.1 | 204 | 7.9 | 806.1 | 838.2 | 806.5 | 790.9 | 738.3 | 734 | 583.3 | 772 | 740.7 | 705.6 | 664.5 | 683.8 | 655.4 | 399.8 | 375.6 | 393.4 | 366.3 | 361.2 | 363.9 | 356.4 | 349.2
1546.1 | 1383.1 | 467.2 | 186.88 | 218.452 | 419.7 | 378.1 | 360.4 | 347.1 | 450.3 | 60.3 | 18.7 | 105.5 | 4.9 | 205.8 | 7.8 | 810.4 | 838.5 | 809 | 790.4 | 740.9 | 734.1 | 583.6 | 776.1 | 741.7 | 707.6 | 665.5 | 690.9 | 653.7 | 399.8 | 375.7 | 393.5 | 366.3 | 361.2 | 363.9 | 356.4 | 349.2
1547.1 | 1384.1 | 468.3 | 187.32 | 218.9663 | 419.5 | 379.8 | 359.8 | 347.6 | 450.1 | 60.3 | 18.7 | 105.4 | 4.8 | 203.2 | 7.4 | 810 | 838.7 | 811 | 790.7 | 742.9 | 734 | 582.4 | 773.6 | 742 | 708 | 665.2 | 688.2 | 651.6 | 399.9 | 375.7 | 393.6 | 366.4 | 361.3 | 363.8 | 356.3 | 349.2
1548.1 | 1385.1 | 468 | 187.2 | 218.826 | 419.5 | 380.1 | 359.1 | 347.4 | 448.7 | 60.3 | 18.7 | 105.5 | 4.3 | 201.1 | 7.3 | 811.4 | 842.5 | 808.8 | 790.8 | 746.2 | 734.1 | 579.3 | 777.8 | 742.8 | 710.6 | 665.2 | 695.9 | 650.5 | 400 | 375.5 | 393.5 | 366.3 | 361.3 | 363.6 | 356.2 | 349.3
1549.1 | 1386.1 | 467.7 | 187.08 | 218.6857 | 418.7 | 380.6 | 358.6 | 347.3 | 450.9 | 60.3 | 18.7 | 105.5 | 4.7 | 193 | 7.3 | 812.5 | 844.6 | 810.5 | 791 | 748.1 | 734.1 | 580.9 | 782.2 | 743.5 | 713.1 | 665.4 | 699.2 | 648.3 | 400.1 | 375.5 | 393.2 | 366.5 | 361.3 | 363.4 | 356 | 349.2
1550.1 | 1387.1 | 468.3 | 187.32 | 218.9663 | 418.3 | 381.6 | 358.4 | 347.4 | 458.9 | 60.3 | 18.7 | 105.5 | 5.7 | 198.4 | 6.8 | 817.7 | 847.5 | 816 | 791.1 | 750.1 | 734.2 | 580.6 | 783.6 | 744.2 | 714.8 | 665.6 | 708.4 | 647 | 400.2 | 375.4 | 393.3 | 366.6 | 361.4 | 363.2 | 355.9 | 349.3
1551.1 | 1388.1 | 468.5 | 187.4 | 219.0598 | 416.5 | 381.5 | 357.9 | 347.3 | 457.5 | 60.2 | 18.7 | 105.5 | 5.9 | 193.9 | 6.2 | 823.3 | 851.1 | 813.5 | 791.2 | 751 | 734.3 | 582.8 | 787.6 | 744.8 | 718 | 666.5 | 710.4 | 648.4 | 400.3 | 375.5 | 393.4 | 366.7 | 361.4 | 363.2 | 355.9 | 349.3
1552.1 | 1389.1 | 467.9 | 187.16 | 218.7793 | 414.9 | 381.2 | 357.4 | 347.9 | 453 | 60.1 | 18.7 | 105.5 | 5.2 | 197.3 | 6.2 | 820 | 848.3 | 811.9 | 791.5 | 752 | 734.4 | 582.9 | 787.2 | 745.2 | 719 | 666.4 | 704.8 | 652.1 | 400.3 | 375.4 | 393.4 | 366.7 | 361.4 | 363.4 | 355.9 | 349.3
1553.1 | 1390.1 | 468.3 | 187.32 | 218.9663 | 411.5 | 381.5 | 356.9 | 348.4 | 454.4 | 60.1 | 18.7 | 105.5 | 4.9 | 194.9 | 6.2 | 825.4 | 849.9 | 816.7 | 791.3 | 754.4 | 734.5 | 584.5 | 787.7 | 745.2 | 720.7 | 666.3 | 709 | 654.3 | 400.4 | 375.5 | 393.3 | 366.7 | 361.5 | 363.4 | 355.8 | 349.3
1554.1 | 1391.1 | 468.3 | 187.32 | 218.9663 | 408.6 | 381.4 | 357 | 348.2 | 451.7 | 60 | 18.7 | 105.6 | 5 | 188.8 | 6.8 | 830.3 | 850.3 | 816 | 791.3 | 758.6 | 734.6 | 586 | 789.3 | 745.7 | 721.2 | 665.9 | 713.1 | 655.4 | 400.5 | 375.3 | 393.2 | 366.6 | 361.5 | 363.1 | 355.8 | 349.4
1555.1 | 1392.1 | 468.6 | 187.44 | 219.1066 | 408.5 | 381.4 | 357.2 | 347.8 | 446.8 | 60 | 18.7 | 105.6 | 5.2 | 204.7 | 7.6 | 837.6 | 854.7 | 821.9 | 791.2 | 761 | 734.7 | 588.6 | 790 | 746.3 | 723.3 | 666.9 | 724.5 | 656 | 400.6 | 375 | 392.9 | 366.5 | 361.5 | 362.6 | 355.6 | 349.5
1556.1 | 1393.1 | 468.4 | 187.36 | 219.013 | 411.9 | 381.9 | 357 | 347.4 | 444 | 59.9 | 18.7 | 105.6 | 4.4 | 194.2 | 7.8 | 842.4 | 858.2 | 819.4 | 791.8 | 760.4 | 734.8 | 591 | 791.9 | 746.5 | 724.1 | 667.1 | 726 | 659.2 | 400.6 | 374.9 | 392.5 | 366.6 | 361.5 | 362.2 | 355.4 | 349.4
1557.1 | 1394.1 | 468.2 | 187.28 | 218.9195 | 414.2 | 381.8 | 356.4 | 346.6 | 441.2 | 59.8 | 18.7 | 105.8 | 4.5 | 199.8 | 7.8 | 841.5 | 854.7 | 819.3 | 792.7 | 759.3 | 734.9 | 591.6 | 787.3 | 746.5 | 723.7 | 666.7 | 715.7 | 661.9 | 400.7 | 374.8 | 392.2 | 366.6 | 361.6 | 362 | 355.3 | 349.4
1558.1 | 1395.1 | 468 | 187.2 | 218.826 | 416.6 | 381 | 355.8 | 345.7 | 437 | 59.8 | 18.7 | 105.9 | 4.4 | 203 | 7.7 | 846.1 | 858.2 | 823.8 | 793 | 760.9 | 735 | 594.4 | 790 | 746.5 | 725.1 | 666.8 | 718.6 | 662.3 | 400.7 | 374.6 | 392 | 366.6 | 361.6 | 362 | 355.2 | 349.3
1559.1 | 1396.1 | 468 | 187.2 | 218.826 | 414.8 | 380 | 355.2 | 345.6 | 434.4 | 59.9 | 18.7 | 106 | 4.5 | 203 | 6.7 | 846.3 | 858.9 | 825.1 | 793 | 763 | 735.2 | 594.8 | 788.4 | 746.9 | 725 | 666.8 | 716.3 | 661.6 | 400.8 | 374.5 | 391.8 | 366.7 | 361.6 | 362.1 | 355.2 | 349.3
1560.1 | 1397.1 | 468.2 | 187.28 | 218.9195 | 413.6 | 379.5 | 355 | 345.3 | 431.8 | 59.9 | 18.7 | 106.1 | 4.9 | 180.4 | 6.6 | 834.9 | 849.4 | 817.3 | 793.6 | 760.4 | 735.3 | 590.9 | 778 | 746.1 | 722.5 | 665.9 | 702.6 | 660.2 | 400.8 | 374.5 | 391.7 | 366.8 | 361.6 | 362 | 355.1 | 349.3
1561.1 | 1398.1 | 468.1 | 187.24 | 218.8728 | 412 | 379.8 | 355.2 | 345.6 | 431.7 | 60 | 18.7 | 106.2 | 5.3 | 175.2 | 7.2 | 825.1 | 840.8 | 811.4 | 793.9 | 759.8 | 735.4 | 590.1 | 776.5 | 745.4 | 723.3 | 665.1 | 691.7 | 657.6 | 400.9 | 374.6 | 391.9 | 366.9 | 361.6 | 361.9 | 355 | 349.3
1562.1 | 1399.1 | 468.2 | 187.28 | 218.9195 | 414.6 | 380.3 | 355.5 | 345.9 | 430.5 | 60 | 18.7 | 106.3 | 5.6 | 180 | 7 | 815.5 | 826.3 | 800.3 | 794 | 757.8 | 735.5 | 587 | 766.4 | 744.1 | 721.4 | 664.4 | 681.5 | 654.7 | 400.9 | 374.8 | 392 | 367.1 | 361.7 | 361.8 | 354.8 | 349.2
1563.1 | 1400.1 | 467.2 | 186.88 | 218.452 | 414.9 | 380.8 | 356.1 | 346.3 | 429.3 | 59.9 | 18.7 | 106.3 | 5.3 | 190.4 | 6.4 | 812.6 | 826.4 | 798.3 | 794.2 | 755.4 | 735.6 | 583.6 | 766.1 | 743.8 | 720.1 | 663.7 | 675.6 | 658.8 | 401 | 374.8 | 392.1 | 367.2 | 361.7 | 362 | 354.8 | 349.2
1564.1 | 1401.1 | 468 | 187.2 | 218.826 | 413.6 | 380.3 | 356.6 | 346.3 | 428.5 | 59.9 | 18.7 | 106.4 | 5.3 | 192.6 | 6.7 | 811.6 | 829.8 | 801.5 | 794.3 | 755.2 | 735.7 | 584.2 | 770 | 743.7 | 720.5 | 663.3 | 675.7 | 658.9 | 401 | 374.8 | 392.3 | 367.3 | 361.7 | 362.1 | 355 | 349.3
1565.1 | 1402.1 | 467.4 | 186.96 | 218.5455 | 413.4 | 380.3 | 357.1 | 346.6 | 433 | 59.9 | 18.7 | 106.4 | 5 | 183.8 | 7 | 806.6 | 828.6 | 800.7 | 794.3 | 754.6 | 735.8 | 586.2 | 775.9 | 743.9 | 722.2 | 663.7 | 676.4 | 657.2 | 401 | 374.8 | 392.9 | 367.4 | 361.7 | 362.5 | 355.3 | 349.3
1566.1 | 1403.1 | 468 | 187.2 | 218.826 | 414.6 | 380.9 | 357.5 | 347.2 | 431.3 | 59.9 | 18.7 | 106.4 | 4.7 | 184 | 7.4 | 808.3 | 834.9 | 796.1 | 794.4 | 752.4 | 735.9 | 583.3 | 779.9 | 744.2 | 723.3 | 663.8 | 678.6 | 659.7 | 401.1 | 374.9 | 393.3 | 367.4 | 361.8 | 362.7 | 355.5 | 349.3
1567.1 | 1404.1 | 468 | 187.2 | 218.826 | 416.5 | 382.9 | 358.4 | 348.3 | 431.1 | 59.8 | 18.7 | 106.3 | 5.2 | 204.4 | 7 | 807.1 | 834.8 | 795.5 | 794.5 | 751.7 | 736 | 583.9 | 783.4 | 744.1 | 723.9 | 664 | 676.8 | 660.4 | 401.2 | 375.3 | 393.8 | 367.5 | 361.8 | 363 | 355.7 | 349.4
1568.1 | 1405.1 | 467.9 | 187.16 | 218.7793 | 416.4 | 383.5 | 359.2 | 349 | 435.6 | 59.8 | 18.7 | 106.2 | 5.3 | 207.9 | 6.3 | 812.7 | 838.3 | 800 | 794.3 | 753 | 736.2 | 585.5 | 785.2 | 744.4 | 725.1 | 664.3 | 683.6 | 661.6 | 401.2 | 375.9 | 394.4 | 367.6 | 361.8 | 363.3 | 356 | 349.4
1569.1 | 1406.1 | 467.5 | 187 | 218.5922 | 414.5 | 383.1 | 359.9 | 349.9 | 438.2 | 59.7 | 18.7 | 106.3 | 4.7 | 203 | 6.6 | 816.8 | 842.6 | 808.3 | 794.4 | 756.9 | 736.3 | 584.7 | 776.5 | 744 | 724 | 664 | 690.1 | 664.4 | 401.3 | 376.1 | 394.5 | 367.6 | 361.8 | 364.1 | 356.3 | 349.5
1570.1 | 1407.1 | 468.4 | 187.36 | 219.013 | 414.4 | 384.1 | 360.2 | 350.7 | 438.6 | 59.7 | 18.7 | 106.3 | 4.7 | 199 | 7.1 | 814.8 | 842.8 | 809.7 | 794.4 | 758.9 | 736.4 | 585.7 | 775.4 | 743.8 | 725 | 664.2 | 694.6 | 662.1 | 401.4 | 376.2 | 394.5 | 367.6 | 361.9 | 364.1 | 356.5 | 349.6
1571.1 | 1408.1 | 467.6 | 187.04 | 218.639 | 415.6 | 385.2 | 359.9 | 350.9 | 440.9 | 59.7 | 18.7 | 106.2 | 4.5 | 207.1 | 7.4 | 815.4 | 841.2 | 810.6 | 794 | 760.9 | 736.6 | 584.4 | 778.2 | 743.6 | 726.5 | 664.4 | 697.3 | 658.2 | 401.4 | 376.3 | 394.4 | 367.8 | 361.9 | 364 | 356.6 | 349.7
1572.1 | 1409.1 | 467.5 | 187 | 218.5922 | 419.8 | 385.8 | 359.5 | 350.8 | 449 | 59.8 | 18.7 | 106.2 | 4.3 | 202.6 | 7.6 | 818.8 | 848.9 | 813 | 793.9 | 763.7 | 736.8 | 585.3 | 785 | 744.6 | 728.8 | 665.2 | 702.7 | 656.9 | 401.5 | 376.1 | 394.2 | 367.8 | 361.9 | 363.7 | 356.6 | 349.7
1573.1 | 1410.1 | 467.6 | 187.04 | 218.639 | 425.4 | 385.8 | 359 | 350.6 | 457 | 59.7 | 18.7 | 106.1 | 4.3 | 206.9 | 7.9 | 823 | 853.5 | 820.1 | 793.6 | 768 | 737 | 587.1 | 789 | 745.6 | 731.6 | 666 | 713.7 | 653.5 | 401.6 | 376.1 | 394.2 | 367.8 | 361.9 | 363.3 | 356.7 | 349.8
1574.1 | 1411.1 | 468.3 | 187.32 | 218.9663 | 425.3 | 385.8 | 358.5 | 350.3 | 454.7 | 59.8 | 18.7 | 106 | 5.2 | 197.4 | 7.8 | 830.5 | 863.4 | 827.5 | 793.6 | 771.2 | 737.2 | 584.6 | 791.7 | 746.7 | 733.5 | 666.9 | 725.4 | 653.9 | 401.7 | 375.9 | 393.8 | 367.8 | 362 | 363.1 | 356.6 | 349.8
1575.1 | 1412.1 | 469 | 187.6 | 219.2936 | 426.1 | 385.8 | 358.3 | 349.7 | 453.3 | 59.9 | 18.7 | 106 | 5.3 | 210.1 | 7.4 | 835.2 | 869.6 | 832.6 | 793.7 | 775.1 | 737.4 | 582.4 | 791.7 | 747.4 | 734.6 | 667.2 | 732.1 | 654.4 | 401.7 | 375.6 | 393.3 | 367.7 | 362 | 363 | 356.4 | 349.8
1576.1 | 1413.1 | 468.7 | 187.48 | 219.1533 | 425.2 | 385.9 | 357.9 | 348.9 | 451.9 | 59.9 | 18.7 | 106.1 | 5.1 | 210.4 | 7 | 838.9 | 871.8 | 834.5 | 794 | 774.3 | 737.6 | 584.9 | 792.6 | 748 | 736 | 667.4 | 732.9 | 653 | 401.8 | 375.4 | 393 | 367.7 | 362 | 362.8 | 356.2 | 349.8
1577.1 | 1414.1 | 468.6 | 187.44 | 219.1066 | 424.1 | 386.8 | 357.1 | 348 | 457.9 | 60 | 18.7 | 106.1 | 5 | 212.1 | 6.2 | 828 | 857.2 | 825.7 | 794.3 | 771.4 | 737.7 | 585.3 | 786.4 | 747.4 | 734.3 | 666.8 | 716.3 | 648.9 | 401.8 | 375.6 | 393.2 | 367.9 | 362 | 362.7 | 356.2 | 349.8
1578.1 | 1415.1 | 469.4 | 187.76 | 219.4806 | 423.4 | 387.5 | 357 | 347.1 | 459 | 60 | 18.7 | 106.2 | 4.8 | 199 | 5.5 | 815.6 | 839 | 817 | 794.2 | 771.7 | 737.8 | 580.4 | 771.1 | 745.6 | 732.6 | 666.1 | 701.8 | 645.3 | 401.9 | 375.8 | 393.6 | 368.2 | 362 | 362.7 | 356.1 | 349.7
1579.1 | 1416.1 | 468.7 | 187.48 | 219.1533 | 421.7 | 388.2 | 358 | 347.2 | 458.2 | 60 | 18.7 | 106.3 | 5 | 197.3 | 5.4 | 813.1 | 838.6 | 814.2 | 793.9 | 771 | 738 | 576.9 | 771.3 | 745 | 734.4 | 666.4 | 697.6 | 642.4 | 401.9 | 375.9 | 393.6 | 368.4 | 362.1 | 362.7 | 356 | 349.7
1580.1 | 1417.1 | 469.2 | 187.68 | 219.3871 | 418.6 | 387.7 | 358.4 | 347.7 | 455.4 | 60.1 | 18.7 | 106.3 | 5 | 208.7 | 5.2 | 805.8 | 835.8 | 804.6 | 793.8 | 768.8 | 738.1 | 574.5 | 767.1 | 744.3 | 733.7 | 666 | 689.4 | 639.7 | 402 | 376.2 | 393.7 | 368.5 | 362.1 | 362.9 | 356.1 | 349.7
1581.1 | 1418.1 | 468.7 | 187.48 | 219.1533 | 415.4 | 387 | 359.1 | 348.2 | 457.9 | 59.9 | 18.7 | 106.5 | 4.9 | 209.2 | 4.8 | 800.8 | 828.2 | 800.8 | 793.9 | 766.7 | 738.1 | 573.7 | 764.8 | 743.6 | 733.5 | 665.7 | 683.4 | 638.3 | 402 | 376.6 | 394.2 | 368.7 | 362.1 | 363.3 | 356.3 | 349.8
1582.1 | 1419.1 | 467.9 | 187.16 | 218.7793 | 412.7 | 388.6 | 359.8 | 348.5 | 461.6 | 59.9 | 18.7 | 106.6 | 4.8 | 205.1 | 4.6 | 800.6 | 827.1 | 800.3 | 794 | 765.6 | 738.2 | 571.8 | 756.6 | 742.3 | 732.4 | 665.2 | 679.1 | 636.7 | 402.1 | 376.8 | 394.7 | 368.8 | 362.1 | 363.6 | 356.5 | 349.8
1583.1 | 1420.1 | 468 | 187.2 | 218.826 | 412.1 | 389.4 | 360.7 | 348.7 | 459.2 | 59.9 | 18.7 | 106.7 | 4.9 | 204.5 | 4.6 | 804.8 | 831.5 | 801.5 | 793.9 | 765 | 738.3 | 571.5 | 760.8 | 741.8 | 732.7 | 664.9 | 680.9 | 636.6 | 402.1 | 376.9 | 394.9 | 368.8 | 362.1 | 363.9 | 356.6 | 349.9
1584.1 | 1421.1 | 469 | 187.6 | 219.2936 | 411.2 | 389.7 | 361.1 | 349.2 | 458.9 | 59.9 | 18.7 | 106.8 | 4.7 | 204.4 | 4.8 | 801.6 | 829.6 | 800.5 | 793.7 | 763.7 | 738.4 | 573.4 | 764.3 | 741.8 | 733 | 664.5 | 675.6 | 635.9 | 402.2 | 377.1 | 395 | 369 | 362.1 | 363.9 | 356.7 | 349.9
1585.1 | 1422.1 | 469 | 187.6 | 219.2936 | 410.1 | 390.5 | 361.2 | 349.5 | 458 | 59.9 | 18.7 | 106.8 | 5.1 | 200.5 | 4.7 | 794.6 | 818.7 | 792.6 | 793.6 | 760.3 | 738.5 | 574.3 | 760 | 741 | 731.9 | 664 | 672.2 | 634.6 | 402.3 | 377.3 | 395 | 369.1 | 362.2 | 364.1 | 356.6 | 349.9
1586.1 | 1423.1 | 469 | 187.6 | 219.2936 | 411.1 | 391.2 | 361.4 | 350.1 | 453.4 | 60 | 18.7 | 106.8 | 4.8 | 190.7 | 4.4 | 776.8 | 792.3 | 771.9 | 793.7 | 753.5 | 738.5 | 572.1 | 738.8 | 739.3 | 727 | 663.4 | 656.6 | 634.2 | 402.3 | 377.6 | 395.4 | 369.4 | 362.2 | 364.3 | 356.5 | 349.9
1587.1 | 1424.1 | 469.3 | 187.72 | 219.4339 | 417 | 392.7 | 362 | 350.9 | 449.1 | 60 | 18.7 | 106.9 | 5 | 162.5 | 4 | 758.1 | 766.3 | 755.2 | 793 | 747.8 | 738.5 | 566 | 713 | 737.1 | 722.2 | 662.7 | 636.9 | 632.3 | 402.4 | 378.4 | 396 | 370 | 362.2 | 364.7 | 356.3 | 349.9
1588.1 | 1425.1 | 469 | 187.6 | 219.2936 | 423 | 394.3 | 363.3 | 351.5 | 446 | 60 | 18.7 | 107 | 5 | 158 | 3.9 | 752.7 | 760 | 748.7 | 792.1 | 744.2 | 738.4 | 561.4 | 699.4 | 734.3 | 718.7 | 661.7 | 627.5 | 628.6 | 402.5 | 379.2 | 397 | 370.4 | 362.2 | 364.9 | 356.4 | 349.9
1589.1 | 1426.1 | 468.2 | 187.28 | 218.9195 | 426.5 | 396 | 364.6 | 351.9 | 444.9 | 60 | 18.7 | 107.1 | 5.2 | 166.7 | 3.7 | 753.8 | 763.3 | 750.7 | 791 | 742.1 | 738.3 | 558.1 | 701.6 | 732.7 | 717.4 | 661 | 621.7 | 626.7 | 402.6 | 379.7 | 397.9 | 370.5 | 362.3 | 365.4 | 356.5 | 349.9
1590.1 | 1427.1 | 468.4 | 187.36 | 219.013 | 428.3 | 396.4 | 366.4 | 352.4 | 442.5 | 60 | 18.7 | 107.2 | 4.9 | 185.1 | 3.7 | 752.4 | 764.5 | 752 | 789.9 | 739.4 | 738.1 | 558.3 | 707.2 | 731.9 | 716.1 | 660.5 | 618.9 | 628.2 | 402.7 | 379.9 | 398.2 | 370.3 | 362.3 | 365.9 | 356.7 | 350
1591.1 | 1428.1 | 470.2 | 188.08 | 219.8547 | 428.6 | 395.5 | 367.2 | 352.6 | 439.7 | 60.2 | 18.7 | 107.3 | 4.6 | 202.9 | 3.9 | 742.4 | 756.1 | 742.6 | 789.1 | 734.4 | 737.9 | 557.8 | 699.8 | 730.4 | 712.6 | 660 | 612.8 | 631.5 | 402.8 | 380.3 | 398.9 | 370.3 | 362.3 | 366.1 | 357 | 350
1592.1 | 1429.1 | 469.8 | 187.92 | 219.6677 | 429 | 394.4 | 367.7 | 353 | 438.1 | 60.3 | 18.7 | 107.4 | 4.5 | 200.1 | 3.9 | 739.2 | 752.9 | 734.9 | 788.4 | 729.3 | 737.7 | 556.7 | 697.4 | 729.1 | 709.8 | 659.4 | 606 | 636.6 | 402.9 | 380.7 | 399.8 | 370.4 | 362.4 | 366.3 | 357.1 | 350.2
1593.1 | 1430.1 | 469.6 | 187.84 | 219.5741 | 430.7 | 393.2 | 368.6 | 353.4 | 436.2 | 60.4 | 18.7 | 107.4 | 4.6 | 206.8 | 4.2 | 727.2 | 736.2 | 722.9 | 787.3 | 724 | 737.5 | 555.6 | 686.6 | 727.7 | 706.2 | 659 | 594.6 | 636.3 | 403 | 381.1 | 400.5 | 370.6 | 362.4 | 366.4 | 357.3 | 350.2
1594.1 | 1431.1 | 469.6 | 187.84 | 219.5741 | 434 | 393.1 | 369.6 | 353.9 | 433.6 | 60.4 | 18.7 | 107.4 | 4.8 | 212.6 | 4.6 | 714.1 | 719.3 | 711.4 | 786.2 | 718.8 | 737.2 | 554 | 669.1 | 725.7 | 701.9 | 658.5 | 584.4 | 639.6 | 403.1 | 381.2 | 400.9 | 370.8 | 362.4 | 366.6 | 357.4 | 350.2
1595.1 | 1432.1 | 469.7 | 187.88 | 219.6209 | 440.9 | 392.8 | 370.4 | 354.5 | 431.6 | 60.4 | 18.7 | 107.4 | 4.7 | 200.7 | 4.6 | 716.2 | 715.7 | 712.4 | 784.9 | 716.1 | 736.8 | 552.2 | 659.6 | 723.6 | 698.1 | 657.7 | 577.2 | 639.8 | 403.3 | 381.2 | 401.2 | 370.8 | 362.5 | 367 | 357.6 | 350.2
1596.1 | 1433.1 | 468.2 | 187.28 | 218.9195 | 441.7 | 392.1 | 370.8 | 355.4 | 428.9 | 60.5 | 18.7 | 107.3 | 5 | 218.1 | 4.8 | 725.4 | 726 | 717.7 | 783.6 | 713.8 | 736.5 | 552 | 661.4 | 722.2 | 696.5 | 656.8 | 578.5 | 641.3 | 403.4 | 381.4 | 401.7 | 370.8 | 362.5 | 367.2 | 357.8 | 350.3
1597.1 | 1434.1 | 468 | 187.2 | 218.826 | 443.1 | 392.3 | 371.7 | 355.8 | 430.4 | 60.5 | 18.7 | 107.3 | 5.1 | 220.9 | 4.5 | 727.4 | 730.4 | 718.4 | 782.2 | 711.9 | 736.1 | 553.3 | 668 | 721.2 | 696.2 | 656.4 | 581.7 | 640.4 | 403.5 | 381.4 | 401.9 | 370.8 | 362.5 | 367.4 | 358.2 | 350.4
1598.1 | 1435.1 | 469.6 | 187.84 | 219.5741 | 443.6 | 391.6 | 372 | 355.6 | 430.7 | 60.5 | 18.7 | 107.3 | 5.1 | 233.8 | 3.6 | 728.7 | 731.3 | 721 | 781 | 709.4 | 735.7 | 551.7 | 669.2 | 720.2 | 693.2 | 655.9 | 579.5 | 640.3 | 403.7 | 381.6 | 402.1 | 370.9 | 362.6 | 367.6 | 358.5 | 350.4
1599.1 | 1436.1 | 470.5 | 188.2 | 219.995 | 440.7 | 391.2 | 371.9 | 355.5 | 433 | 60.5 | 18.7 | 107.3 | 4.9 | 236.7 | 2.8 | 731.5 | 736.8 | 730.7 | 779.8 | 708.9 | 735.3 | 552.4 | 673.6 | 719.5 | 692.3 | 655.7 | 583.7 | 637.2 | 403.8 | 381.9 | 402.3 | 371.1 | 362.6 | 367.6 | 358.7 | 350.5
1600.1 | 1437.1 | 470.2 | 188.08 | 219.8547 | 441.4 | 391.5 | 372.2 | 355.7 | 446.8 | 60.5 | 18.7 | 107.3 | 4.7 | 201.9 | 2.4 | 737.7 | 749.1 | 744.5 | 778.7 | 709.9 | 734.8 | 554 | 684.5 | 719.3 | 693.7 | 655.9 | 592.2 | 635.9 | 403.9 | 382.2 | 402.6 | 371.2 | 362.7 | 367.6 | 358.8 | 350.6
1601.1 | 1438.1 | 470.4 | 188.16 | 219.9482 | 442.6 | 392.3 | 372.6 | 356.3 | 449.4 | 60.6 | 18.7 | 107.3 | 4.8 | 174.3 | 2.1 | 736.1 | 755.5 | 742 | 778.1 | 708.7 | 734.4 | 555.5 | 690.2 | 719.4 | 694.3 | 656.2 | 596.4 | 632.4 | 404.1 | 382.6 | 402.9 | 371.4 | 362.7 | 368 | 358.9 | 350.7
1602.1 | 1439.1 | 468.9 | 187.56 | 219.2468 | 442.7 | 393.3 | 372.8 | 356.4 | 452 | 60.5 | 18.7 | 107.3 | 5 | 177.9 | 1.9 | 732.1 | 754.1 | 740.1 | 777.8 | 707.5 | 734 | 555.1 | 686.6 | 718.6 | 692.5 | 655.8 | 594.7 | 629.2 | 404.2 | 382.8 | 403.1 | 371.7 | 362.8 | 368.3 | 359 | 350.8
1603.1 | 1440.1 | 467.3 | 186.92 | 218.4987 | 441.2 | 394.1 | 373.6 | 356.6 | 450.4 | 60.5 | 18.7 | 107.3 | 4.5 | 191.6 | 1.7 | 739 | 771.1 | 741.8 | 777.4 | 704.3 | 733.6 | 556.9 | 698.4 | 718.7 | 693.7 | 655.5 | 597.7 | 627.9 | 404.3 | 382.9 | 403.7 | 371.9 | 362.8 | 368.7 | 359.4 | 350.8
1604.1 | 1441.1 | 467.5 | 187 | 218.5922 | 439.2 | 394 | 374.1 | 356.8 | 445.4 | 60.5 | 18.7 | 107.2 | 4.7 | 209.4 | 1.4 | 751.9 | 787 | 754 | 776.7 | 705.6 | 733.2 | 557.5 | 711.8 | 719.4 | 695.1 | 655.5 | 608.8 | 631.2 | 404.5 | 382.9 | 403.7 | 371.8 | 362.9 | 368.9 | 359.6 | 350.9
1605.1 | 1442.1 | 468.4 | 187.36 | 219.013 | 438.3 | 394 | 373.6 | 356.8 | 447.8 | 60.5 | 18.6 | 107.1 | 4.7 | 227 | 1.5 | 759.6 | 799.1 | 764.1 | 775.9 | 709.6 | 732.9 | 560.4 | 726 | 720.5 | 697.4 | 655.8 | 620.3 | 632.4 | 404.6 | 383 | 403.7 | 371.9 | 362.9 | 368.8 | 359.8 | 351
1606.1 | 1443.1 | 467.8 | 187.12 | 218.7325 | 434.6 | 394.9 | 373.4 | 356.8 | 451 | 60.5 | 18.7 | 107 | 4.4 | 227.3 | 2.1 | 761.8 | 804.3 | 764 | 775.6 | 709.1 | 732.6 | 563.3 | 735 | 721.3 | 698.2 | 656 | 624.2 | 635.1 | 404.7 | 382.9 | 403.9 | 372 | 363 | 369 | 359.9 | 351.1
1607.1 | 1444.1 | 467.9 | 187.16 | 218.7793 | 433 | 395.2 | 373.3 | 356.8 | 451.4 | 60.5 | 18.7 | 106.9 | 4.4 | 207.4 | 4 | 764.1 | 805.9 | 771.6 | 775.4 | 709.5 | 732.3 | 563.5 | 736.8 | 721.7 | 698.2 | 655.6 | 624.2 | 634.8 | 404.9 | 382.6 | 403.8 | 372 | 363 | 369.1 | 360 | 351.1
1608.1 | 1445.1 | 468.3 | 187.32 | 218.9663 | 430.3 | 395.1 | 373.2 | 356.5 | 449.3 | 60.4 | 18.7 | 106.8 | 4.6 | 200.4 | 5 | 777.9 | 819.6 | 785.9 | 775.1 | 715.2 | 732 | 564.2 | 742.6 | 721.9 | 700.9 | 656.1 | 641.6 | 632.9 | 405 | 382.4 | 403.4 | 371.9 | 363.1 | 369.1 | 360 | 351.2
1609.1 | 1446.1 | 468.6 | 187.44 | 219.1066 | 431.8 | 394.5 | 372.8 | 356.5 | 448.9 | 60.4 | 18.7 | 106.7 | 4.9 | 223.5 | 5 | 785.2 | 826.7 | 794.8 | 774.8 | 717.9 | 731.8 | 565.6 | 747.6 | 722.1 | 702.6 | 656.3 | 655.5 | 632.1 | 405.1 | 382.3 | 403.1 | 371.9 | 363.1 | 368.9 | 360 | 351.2
1610.1 | 1447.1 | 468.6 | 187.44 | 219.1066 | 430.2 | 394.6 | 372.3 | 356.4 | 452 | 60.4 | 18.6 | 106.6 | 4.7 | 220.2 | 5.2 | 792.4 | 828.4 | 798.1 | 774.8 | 719.5 | 731.5 | 565.3 | 740.6 | 722.1 | 700.7 | 655.7 | 649.9 | 633 | 405.3 | 382.2 | 402.9 | 371.9 | 363.2 | 368.7 | 360 | 351.3
1611.1 | 1448.1 | 468.7 | 187.48 | 219.1533 | 428.4 | 394.8 | 371.7 | 356.2 | 447.3 | 60.4 | 18.6 | 106.6 | 4.8 | 200.8 | 5.4 | 801.9 | 834.3 | 802.5 | 774.5 | 723.7 | 731.4 | 567 | 751.3 | 722.8 | 703.5 | 656 | 662.7 | 634.7 | 405.4 | 382.1 | 402.4 | 371.8 | 363.2 | 368.5 | 360 | 351.4
1612.1 | 1449.1 | 468.9 | 187.56 | 219.2468 | 427.2 | 395 | 371.4 | 355.6 | 445.6 | 60.4 | 18.6 | 106.7 | 4.8 | 207 | 5.5 | 812.1 | 846.6 | 807.6 | 774.4 | 726.7 | 731.2 | 570 | 758.5 | 723.8 | 705.5 | 656.6 | 675 | 638.1 | 405.5 | 381.9 | 401.9 | 371.9 | 363.3 | 368 | 360 | 351.5
1613.1 | 1450.1 | 468 | 187.2 | 218.826 | 428.5 | 394.7 | 370.9 | 354.6 | 443.3 | 60.5 | 18.6 | 106.6 | 4.5 | 216.4 | 5.8 | 810.2 | 846.9 | 807.8 | 774.5 | 728.3 | 731 | 571 | 758 | 724.4 | 705 | 655.8 | 674 | 640 | 405.6 | 381.9 | 401.6 | 372 | 363.3 | 367.8 | 360 | 351.5
1614.1 | 1451.1 | 468.6 | 187.44 | 219.1066 | 431.2 | 393 | 370.2 | 353.7 | 440.2 | 60.6 | 18.6 | 106.6 | 4.9 | 215.4 | 5.9 | 806.8 | 841.9 | 802.4 | 774.8 | 726.2 | 730.8 | 571.6 | 752.7 | 724.4 | 703.6 | 655.2 | 662.3 | 641.4 | 405.7 | 381.5 | 401.5 | 372.1 | 363.3 | 367.6 | 359.9 | 351.5
1615.1 | 1452.1 | 468.5 | 187.4 | 219.0598 | 435.7 | 392.9 | 369.6 | 353.2 | 437.6 | 60.7 | 18.6 | 106.6 | 4.7 | 213.2 | 5.7 | 805.2 | 836.8 | 797.3 | 774.9 | 725.6 | 730.6 | 573.1 | 752.7 | 724.3 | 703.6 | 654.6 | 657 | 642.4 | 405.8 | 381.4 | 401.5 | 372.1 | 363.4 | 367.3 | 359.6 | 351.5
1616.1 | 1453.1 | 468.8 | 187.52 | 219.2001 | 438.5 | 393.4 | 370 | 352.8 | 436.7 | 60.7 | 18.6 | 106.6 | 5 | 211.2 | 5.8 | 797.9 | 820.6 | 782.8 | 774.9 | 721.6 | 730.5 | 570.8 | 739.4 | 723.7 | 701.5 | 653.9 | 646.2 | 644.9 | 405.9 | 381.3 | 401.3 | 372.2 | 363.4 | 367.2 | 359.4 | 351.5
1617.1 | 1454.1 | 468.8 | 187.52 | 219.2001 | 441.1 | 392.2 | 370.3 | 352.5 | 433.3 | 60.7 | 18.6 | 106.6 | 4.6 | 207.6 | 6.1 | 781.6 | 803.7 | 764.6 | 774.9 | 717.6 | 730.3 | 567.5 | 725.3 | 722.5 | 697.7 | 652.9 | 633.1 | 648.1 | 406 | 381.2 | 401.3 | 372.3 | 363.4 | 367 | 359.1 | 351.5
1618.1 | 1455.1 | 468.5 | 187.4 | 219.0598 | 447.1 | 392.1 | 369.6 | 352.3 | 430.6 | 60.7 | 18.7 | 106.7 | 5 | 209.3 | 5.9 | 766.2 | 786.1 | 755.5 | 774.9 | 712.9 | 730.1 | 564.5 | 709.7 | 720.7 | 694.1 | 652 | 620.2 | 654.9 | 406.1 | 380.9 | 401.2 | 372.4 | 363.5 | 367.1 | 359 | 351.5
1619.1 | 1456.1 | 468.6 | 187.44 | 219.1066 | 452 | 391.3 | 369.3 | 352.3 | 428.6 | 60.7 | 18.7 | 106.7 | 4.5 | 211.9 | 5.7 | 761.5 | 780.3 | 752.5 | 774.4 | 709.6 | 729.9 | 558.9 | 697.7 | 718.5 | 691.5 | 651.2 | 612.7 | 666.1 | 406.1 | 380.7 | 400.9 | 372.2 | 363.5 | 367.5 | 358.9 | 351.5
1620.1 | 1457.1 | 468.5 | 187.4 | 219.0598 | 454.3 | 389.1 | 369.2 | 352.9 | 426.7 | 60.8 | 18.6 | 106.8 | 5.2 | 224.1 | 5.6 | 745.3 | 758.1 | 731.7 | 774 | 703.3 | 729.5 | 552.9 | 680.6 | 716.4 | 687.6 | 650.5 | 602 | 680.5 | 406.2 | 380.6 | 400.6 | 372.2 | 363.5 | 367.4 | 358.7 | 351.6
1621.1 | 1458.1 | 468.5 | 187.4 | 219.0598 | 458.4 | 387.2 | 368.9 | 353.1 | 423 | 60.8 | 18.6 | 106.8 | 5 | 187.4 | 5.2 | 738 | 745.8 | 725.9 | 773.4 | 699.9 | 729.2 | 545.9 | 667.1 | 714.1 | 683.5 | 649.8 | 589.1 | 697.4 | 406.3 | 380.3 | 400.2 | 372.2 | 363.6 | 367.6 | 358.7 | 351.6
1622.1 | 1459.1 | 468.8 | 187.52 | 219.2001 | 460.6 | 386.8 | 368 | 353.1 | 419.2 | 60.8 | 18.6 | 106.9 | 5 | 165.2 | 5.1 | 746.5 | 756.5 | 736.6 | 772.5 | 699.8 | 728.7 | 543.5 | 670.8 | 712.9 | 682.2 | 648.9 | 589.7 | 703.8 | 406.4 | 380.1 | 399.6 | 372.1 | 363.6 | 367.4 | 358.5 | 351.6
1623.1 | 1460.1 | 468.8 | 187.52 | 219.2001 | 464.2 | 388.2 | 367.7 | 352.8 | 417 | 60.8 | 18.6 | 106.9 | 5.4 | 184.7 | 5.2 | 752.1 | 766.8 | 745.8 | 771.6 | 700.2 | 728.3 | 542.3 | 680.1 | 711.9 | 681.6 | 648.2 | 590.3 | 700.3 | 406.4 | 380.1 | 399.6 | 372.2 | 363.6 | 367.3 | 358.5 | 351.6
1624.1 | 1461.1 | 468.7 | 187.48 | 219.1533 | 460.8 | 389.8 | 367.5 | 352.3 | 416.7 | 60.8 | 18.6 | 107 | 4.7 | 181.1 | 5.5 | 760 | 777.6 | 753 | 770.9 | 701.1 | 727.8 | 541.6 | 686.8 | 711.3 | 681.6 | 648 | 597.7 | 696.4 | 406.5 | 379.9 | 399.6 | 372.2 | 363.6 | 367.4 | 358.5 | 351.6
1625.1 | 1462.1 | 469 | 187.6 | 219.2936 | 463.4 | 394.6 | 367.3 | 352.2 | 416.5 | 60.9 | 18.6 | 107.2 | 4.9 | 182.6 | 5.9 | 778.1 | 796.7 | 773.6 | 770 | 707.3 | 727.3 | 545.9 | 707.4 | 711.9 | 684.6 | 648.5 | 623.9 | 692.4 | 406.6 | 379.5 | 399 | 372 | 363.7 | 367.2 | 358.3 | 351.7
1626.1 | 1463.1 | 468.9 | 187.56 | 219.2468 | 464.3 | 396.2 | 367 | 352.3 | 418.5 | 60.9 | 18.6 | 107.3 | 4.8 | 190.9 | 6.4 | 787.3 | 809.2 | 784.5 | 770 | 711 | 727 | 551.5 | 725.2 | 713.4 | 687.8 | 649.6 | 646.6 | 685.8 | 406.6 | 379.1 | 398.4 | 371.9 | 363.7 | 366.9 | 358.2 | 351.7
1627.1 | 1464.1 | 469 | 187.6 | 219.2936 | 461.3 | 398 | 366.4 | 352.2 | 417.6 | 61 | 18.6 | 107.3 | 5.6 | 188.6 | 6.4 | 794.1 | 816.7 | 789.9 | 770.2 | 714.1 | 726.6 | 555.4 | 731.5 | 714.7 | 690.4 | 651.1 | 659.4 | 680.8 | 406.7 | 379 | 397.9 | 372 | 363.7 | 366.6 | 358.1 | 351.7
1628.1 | 1465.1 | 469 | 187.6 | 219.2936 | 460 | 398.4 | 365.6 | 352.3 | 417.5 | 60.9 | 18.6 | 107.4 | 5.4 | 198.8 | 5.8 | 793.9 | 815 | 792.3 | 770.2 | 715.1 | 726.3 | 557.8 | 728.5 | 715.1 | 690.1 | 650.9 | 655 | 674.1 | 406.7 | 379.2 | 398.2 | 372.3 | 363.7 | 366.7 | 358 | 351.7
1629.1 | 1466.1 | 468.3 | 187.32 | 218.9663 | 461.9 | 397.6 | 365.5 | 352.1 | 417.7 | 60.9 | 18.6 | 107.5 | 4.8 | 199.4 | 5.4 | 789.7 | 815.3 | 783.8 | 770.3 | 713.8 | 726 | 561.1 | 735.8 | 715.4 | 690.5 | 650.6 | 652.7 | 667.1 | 406.7 | 379.1 | 398.1 | 372.4 | 363.8 | 366.7 | 358 | 351.7
1630.1 | 1467.1 | 469 | 187.6 | 219.2936 | 457.7 | 396.6 | 365.6 | 351.9 | 419.2 | 60.8 | 18.6 | 107.6 | 5 | 192.2 | 5.2 | 776.1 | 804 | 767.5 | 770.2 | 710.6 | 725.7 | 561.6 | 724.8 | 715.1 | 689.4 | 650.6 | 646.9 | 662.8 | 406.8 | 379 | 398.3 | 372.5 | 363.8 | 366.5 | 357.8 | 351.7
1631.1 | 1468.1 | 469 | 187.6 | 219.2936 | 454.1 | 396.3 | 365.7 | 351.3 | 419.7 | 60.7 | 18.6 | 107.7 | 4.9 | 186.5 | 5.4 | 762.8 | 787.3 | 753.7 | 770 | 706 | 725.4 | 558.3 | 714.1 | 714.4 | 686.8 | 650 | 635.8 | 663.6 | 406.8 | 379.1 | 398.2 | 372.6 | 363.8 | 366.4 | 357.7 | 351.7
1632.1 | 1469.1 | 468.2 | 187.28 | 218.9195 | 458.4 | 396 | 365.8 | 350.8 | 418.6 | 60.8 | 18.6 | 107.7 | 5 | 195.6 | 5.5 | 756.2 | 779.8 | 736.9 | 769.5 | 702.4 | 725.1 | 554.4 | 705.6 | 713 | 684.1 | 649.1 | 626.4 | 669.6 | 406.8 | 379.1 | 398.3 | 372.7 | 363.8 | 366.3 | 357.6 | 351.7
1633.1 | 1470.1 | 468.6 | 187.44 | 219.1066 | 461.4 | 394.7 | 366.3 | 350.6 | 417.4 | 60.8 | 18.6 | 107.6 | 4.6 | 196.6 | 6.1 | 744.3 | 766.1 | 726.7 | 769 | 698.5 | 724.8 | 548.9 | 687.4 | 711.1 | 680.7 | 648.3 | 613.6 | 673.6 | 406.9 | 379.2 | 398.5 | 372.8 | 363.9 | 366.6 | 357.7 | 351.7
1634.1 | 1471.1 | 468.3 | 187.32 | 218.9663 | 459.2 | 394.6 | 366.3 | 351.1 | 415.7 | 60.8 | 18.6 | 107.7 | 4.7 | 211.4 | 5.8 | 728.6 | 746 | 713 | 768.4 | 692.8 | 724.4 | 544.3 | 668.6 | 709.3 | 676.6 | 647.3 | 600.6 | 676.6 | 406.9 | 379.4 | 398.9 | 372.9 | 363.9 | 366.8 | 357.8 | 351.7
1635.1 | 1472.1 | 468.2 | 187.28 | 218.9195 | 460.3 | 394.3 | 366.6 | 351.5 | 413.9 | 60.7 | 18.6 | 107.8 | 4.9 | 196.2 | 5.3 | 718.1 | 733.7 | 706.2 | 767.6 | 688.1 | 723.9 | 539.5 | 654.8 | 707.2 | 673 | 646.4 | 589.3 | 686.1 | 406.9 | 379.7 | 399.2 | 372.9 | 363.9 | 366.8 | 357.9 | 351.8
1636.1 | 1473.1 | 468.3 | 187.32 | 218.9663 | 464.9 | 393.2 | 367 | 352 | 413.1 | 60.6 | 18.6 | 107.9 | 5.1 | 189.1 | 4.8 | 718.7 | 735 | 706.1 | 766.8 | 685.8 | 723.4 | 536.5 | 651.7 | 705.5 | 670.7 | 645.5 | 587.8 | 694.2 | 407 | 379.8 | 399.4 | 372.9 | 363.9 | 366.5 | 358 | 351.9
1637.1 | 1474.1 | 469 | 187.6 | 219.2936 | 471.6 | 392.3 | 367.1 | 352.4 | 411.8 | 60.6 | 18.6 | 108 | 4.7 | 182 | 4.2 | 723.4 | 743.4 | 716.4 | 766 | 686.6 | 722.9 | 533.8 | 658.5 | 704.7 | 670.1 | 644.8 | 587.1 | 694.4 | 407.1 | 379.7 | 399.4 | 372.9 | 363.9 | 366.7 | 358.2 | 351.9
1638.1 | 1475.1 | 468.9 | 187.56 | 219.2468 | 473.8 | 392.7 | 366.7 | 352.6 | 409.8 | 60.7 | 18.6 | 107.9 | 4.2 | 183.1 | 4.2 | 724.7 | 752 | 714.5 | 765.4 | 683.4 | 722.4 | 534.5 | 678.3 | 705.1 | 671.2 | 644.4 | 588.4 | 695.5 | 407.1 | 379.6 | 399.3 | 372.9 | 363.9 | 367.1 | 358.4 | 352
1639.1 | 1476.1 | 469.5 | 187.8 | 219.5274 | 470.6 | 393.9 | 366.3 | 353.2 | 409.2 | 60.7 | 18.6 | 107.8 | 4.4 | 182.3 | 4.4 | 723.9 | 752.7 | 707.1 | 764.8 | 681.5 | 721.9 | 535 | 679.7 | 705.5 | 668.6 | 643.9 | 587.6 | 700.9 | 407.2 | 379.6 | 399.2 | 372.9 | 364 | 366.8 | 358.5 | 352.1
1640.1 | 1477.1 | 468.1 | 187.24 | 218.8728 | 470.6 | 393.8 | 365.9 | 353.1 | 406.5 | 60.6 | 18.6 | 107.8 | 5 | 183.6 | 4.4 | 734.3 | 755.6 | 707.6 | 764.1 | 680.9 | 721.5 | 532.7 | 679.9 | 705.9 | 667.6 | 643.5 | 594 | 707.8 | 407.2 | 379.5 | 398.9 | 372.8 | 364 | 366.7 | 358.6 | 352.1
1641.1 | 1478.1 | 467.5 | 187 | 218.5922 | 471.4 | 393.1 | 365.8 | 353 | 404.6 | 60.5 | 18.6 | 107.8 | 5.1 | 194.9 | 4.3 | 746.7 | 762.6 | 709.4 | 763.5 | 681.1 | 720.9 | 532.2 | 676.6 | 705.7 | 666.4 | 642.9 | 598.6 | 715.1 | 407.3 | 379.2 | 398.5 | 372.7 | 364 | 367.1 | 358.9 | 352.2
1642.1 | 1479.1 | 467 | 186.8 | 218.3584 | 472 | 393.3 | 365.7 | 352.6 | 405.7 | 60.4 | 18.6 | 107.8 | 5.3 | 188.5 | 4.4 | 757.3 | 764.1 | 711.7 | 762.7 | 681.9 | 720.5 | 533 | 668.8 | 705 | 664.4 | 642.3 | 598.4 | 722.7 | 407.3 | 379 | 398.1 | 372.8 | 364 | 367.1 | 358.9 | 352.3
1643.1 | 1480.1 | 468 | 187.2 | 218.826 | 471 | 395.6 | 365.4 | 351.8 | 406.3 | 60.4 | 18.6 | 107.8 | 5.2 | 167.3 | 4.8 | 772.5 | 776 | 722.9 | 762 | 684.2 | 720 | 533.6 | 670.2 | 704.7 | 662.8 | 641.5 | 604.7 | 727.3 | 407.3 | 378.8 | 397.6 | 372.7 | 364.1 | 367.1 | 359 | 352.3
1644.1 | 1481.1 | 468 | 187.2 | 218.826 | 467.5 | 396 | 365.4 | 350.9 | 405.6 | 60.5 | 18.6 | 107.8 | 4.9 | 172 | 5.2 | 787.4 | 789.6 | 743.4 | 761.6 | 690.1 | 719.5 | 539.2 | 684.8 | 705.1 | 663.7 | 641.5 | 622.2 | 724.7 | 407.4 | 378.4 | 396.9 | 372.4 | 364.1 | 367 | 359 | 352.3
1645.1 | 1482.1 | 467.7 | 187.08 | 218.6857 | 465.4 | 396.3 | 364.9 | 350.2 | 404.1 | 60.6 | 18.6 | 107.8 | 4.5 | 177.7 | 5.7 | 793.6 | 800.2 | 762.9 | 761.5 | 695.6 | 719 | 542.8 | 696.1 | 705.7 | 665.1 | 641.9 | 633.2 | 717.2 | 407.4 | 378.1 | 396.3 | 372.3 | 364.1 | 366.6 | 358.7 | 352.3
1646.1 | 1483.1 | 467.8 | 187.12 | 218.7325 | 464.8 | 396.8 | 363.9 | 349.6 | 407.3 | 60.6 | 18.6 | 107.8 | 3.9 | 189.1 | 5.7 | 794.1 | 813.5 | 773.6 | 761.4 | 701.1 | 718.6 | 544.9 | 709.6 | 706.1 | 667.7 | 642.2 | 640.6 | 705.8 | 407.4 | 377.8 | 395.8 | 372.3 | 364.1 | 366.3 | 358.4 | 352.2
1647.1 | 1484.1 | 467.9 | 187.16 | 218.7793 | 463.3 | 398.3 | 362.8 | 348.8 | 416.5 | 60.6 | 18.6 | 107.8 | 4 | 183 | 5.7 | 798.3 | 825.8 | 779.9 | 761.9 | 704.8 | 718.2 | 549.3 | 732.1 | 707.4 | 672.8 | 643.3 | 655.2 | 696.3 | 407.4 | 377.6 | 395.4 | 372.3 | 364.2 | 366.1 | 358.3 | 352.1
1648.1 | 1485.1 | 467.8 | 187.12 | 218.7325 | 462.5 | 399.9 | 362.2 | 348.2 | 420 | 60.6 | 18.6 | 107.9 | 4.8 | 180.2 | 5.5 | 804.3 | 823.7 | 777.9 | 762.4 | 703.8 | 717.9 | 552.4 | 741 | 708.9 | 675.6 | 644.3 | 658.7 | 691.9 | 407.4 | 377.4 | 395.2 | 372.4 | 364.2 | 366 | 358.3 | 352.1
1649.1 | 1486.1 | 467.8 | 187.12 | 218.7325 | 466 | 400.6 | 362.4 | 348.3 | 420.8 | 60.7 | 18.6 | 108 | 5.4 | 185.1 | 5.4 | 790.4 | 811.7 | 769.7 | 762.7 | 701 | 717.5 | 555.1 | 734.5 | 709.5 | 673.8 | 644 | 645.4 | 686.3 | 407.4 | 377.5 | 395.3 | 372.6 | 364.2 | 366 | 358.3 | 352.1
1650.1 | 1487.1 | 468.1 | 187.24 | 218.8728 | 464.9 | 400.3 | 362.9 | 348.7 | 419.1 | 60.6 | 18.6 | 108 | 4.6 | 187.2 | 5.5 | 771.1 | 789.4 | 760 | 762.7 | 697.9 | 717.2 | 554.8 | 721.3 | 708.7 | 671.7 | 643.3 | 633.2 | 677.8 | 407.4 | 377.6 | 395.6 | 372.9 | 364.2 | 365.8 | 358.1 | 352.1
1651.1 | 1488.1 | 467.7 | 187.08 | 218.6857 | 463.8 | 399.6 | 363.8 | 349.5 | 419.3 | 60.6 | 18.6 | 108 | 4.5 | 186.5 | 5.3 | 760.7 | 779.5 | 749.4 | 762.5 | 693.3 | 716.9 | 554.1 | 711.1 | 707.8 | 669.9 | 642.7 | 624.9 | 672.7 | 407.4 | 377.6 | 395.8 | 373 | 364.2 | 365.9 | 358 | 352.1
1652.1 | 1489.1 | 468 | 187.2 | 218.826 | 465.6 | 400.1 | 364.5 | 350.3 | 418.4 | 60.5 | 18.6 | 108.2 | 5.7 | 185 | 5.2 | 765.8 | 794.3 | 751.6 | 762.3 | 694.5 | 716.7 | 553.3 | 721.7 | 707.7 | 671 | 642.1 | 627.6 | 670.5 | 407.4 | 377.9 | 396.6 | 373 | 364.3 | 365.7 | 358 | 352.1
1653.1 | 1490.1 | 468.2 | 187.28 | 218.9195 | 463.7 | 400.5 | 364.9 | 350.9 | 420.5 | 60.6 | 18.6 | 108.4 | 5 | 186.1 | 5.1 | 769.2 | 807.1 | 759.4 | 761.9 | 698.4 | 716.4 | 556 | 734.2 | 708.3 | 674.1 | 642.2 | 636.9 | 667.3 | 407.4 | 378.3 | 396.9 | 373.1 | 364.3 | 365.5 | 357.9 | 352.1
1654.1 | 1491.1 | 467.7 | 187.08 | 218.6857 | 459 | 400.3 | 365.3 | 351.6 | 423.9 | 60.7 | 18.6 | 108.6 | 5.3 | 194.7 | 5 | 777.3 | 822.7 | 770.8 | 761.9 | 704.8 | 716.2 | 559.2 | 746.8 | 709.9 | 677.8 | 642.8 | 654.4 | 662 | 407.4 | 378.5 | 397.2 | 373.2 | 364.3 | 365.8 | 358 | 352.2
1655.1 | 1492.1 | 467.3 | 186.92 | 218.4987 | 455 | 401.2 | 365.2 | 351.5 | 434.1 | 60.7 | 18.6 | 108.8 | 5.1 | 191.1 | 4.8 | 780.2 | 827.5 | 780.6 | 762.1 | 708.6 | 716.1 | 558.2 | 750 | 711.3 | 681.3 | 643.5 | 668.1 | 657.2 | 407.4 | 378.7 | 397.2 | 373.2 | 364.3 | 366 | 358.1 | 352.2
1656.1 | 1493.1 | 468.3 | 187.32 | 218.9663 | 455.9 | 404.1 | 364.9 | 351.9 | 447.9 | 60.8 | 18.6 | 108.9 | 5 | 188.6 | 4.6 | 781.7 | 826.1 | 785.2 | 762.7 | 712.3 | 715.9 | 556.9 | 746.2 | 710.9 | 682.2 | 643.5 | 671 | 652.1 | 407.5 | 378.9 | 397.2 | 373.2 | 364.3 | 366.1 | 358.2 | 352.3
1657.1 | 1494.1 | 466.7 | 186.68 | 218.2182 | 459.1 | 405.7 | 365 | 351.9 | 456.1 | 60.9 | 18.6 | 108.9 | 5.1 | 197.7 | 4.5 | 777.5 | 816.6 | 780.2 | 762.9 | 714.8 | 715.8 | 555 | 738.6 | 710.1 | 683.2 | 644 | 668.9 | 645 | 407.5 | 378.9 | 397.1 | 373.3 | 364.3 | 366.1 | 358.1 | 352.3
1658.1 | 1495.1 | 465.4 | 186.16 | 217.6103 | 460.7 | 406.9 | 365.2 | 352.2 | 459.4 | 60.9 | 18.6 | 108.9 | 4.5 | 196.4 | 4.5 | 777.3 | 814.4 | 778.6 | 762.9 | 714.6 | 715.7 | 555.3 | 738.8 | 709.5 | 684 | 643.9 | 660.2 | 638.6 | 407.5 | 378.9 | 397.1 | 373.4 | 364.4 | 366 | 358 | 352.2
1659.1 | 1496.1 | 467.3 | 186.92 | 218.4987 | 455.5 | 407.8 | 364.8 | 352.6 | 460.6 | 61 | 18.6 | 108.9 | 5 | 185.1 | 4.3 | 785.8 | 821 | 790.4 | 763.1 | 720.9 | 715.6 | 553.8 | 741.9 | 709.1 | 685.5 | 643.9 | 668.7 | 634 | 407.5 | 378.9 | 397 | 373.5 | 364.4 | 366 | 358.1 | 352.3
1660.1 | 1497.1 | 467.3 | 186.92 | 218.4987 | 450.1 | 411.4 | 364 | 352.9 | 454.7 | 61 | 18.6 | 108.9 | 4.8 | 184.4 | 4.1 | 795.8 | 837 | 795.1 | 763.1 | 726.7 | 715.5 | 555.1 | 749.7 | 710 | 688.1 | 644.7 | 687.2 | 633.1 | 407.5 | 378.9 | 396.8 | 373.7 | 364.4 | 366.1 | 358 | 352.3
1661.1 | 1498.1 | 467 | 186.8 | 218.3584 | 449.4 | 414.3 | 363.2 | 352.7 | 451 | 61 | 18.6 | 108.9 | 5.1 | 186.9 | 3.9 | 802 | 842.1 | 798.1 | 763.3 | 728.5 | 715.4 | 558 | 752.9 | 711.1 | 689.9 | 645.2 | 689.6 | 631.1 | 407.6 | 379 | 396.7 | 373.7 | 364.4 | 365.7 | 358.1 | 352.3
1662.1 | 1499.1 | 468.3 | 187.32 | 218.9663 | 448.3 | 415.6 | 363 | 352.5 | 453.6 | 61 | 18.6 | 108.8 | 5 | 184.2 | 3.9 | 806.5 | 842.4 | 806 | 763.8 | 733 | 715.3 | 557.1 | 753.7 | 711.7 | 691.9 | 645.9 | 693.3 | 631.2 | 407.6 | 379 | 396.8 | 373.5 | 364.4 | 365.6 | 358 | 352.3
1663.1 | 1500.1 | 468.7 | 187.48 | 219.1533 | 444.6 | 414.6 | 362.9 | 352.2 | 454.9 | 61.1 | 18.6 | 108.8 | 4.8 | 181.4 | 3.9 | 814.7 | 848.2 | 809.1 | 764.6 | 737.3 | 715.2 | 558.2 | 757.4 | 712.3 | 693.4 | 646.2 | 701.8 | 634 | 407.6 | 378.8 | 396.6 | 373.3 | 364.4 | 365.2 | 358 | 352.4
1664.1 | 1501.1 | 468.4 | 187.36 | 219.013 | 441.7 | 415.9 | 362.7 | 352.3 | 454.7 | 61.1 | 18.6 | 108.8 | 4.9 | 182.5 | 4.1 | 826.5 | 853.5 | 812.4 | 765.4 | 740.6 | 715.2 | 560.4 | 760.9 | 713.2 | 695.1 | 646.2 | 708 | 635.4 | 407.6 | 378.5 | 396.1 | 373.1 | 364.5 | 364.8 | 357.9 | 352.3
1665.1 | 1502.1 | 467.1 | 186.84 | 218.4052 | 439.7 | 416.7 | 362.6 | 352 | 451.9 | 61.2 | 18.6 | 108.9 | 4.6 | 183.1 | 4.5 | 834.2 | 855.5 | 813 | 766.3 | 742.6 | 715.1 | 563 | 761.4 | 713.9 | 696.3 | 646.2 | 715 | 636.5 | 407.6 | 378.1 | 395.6 | 373 | 364.5 | 364.4 | 357.7 | 352.3
1666.1 | 1503.1 | 467.3 | 186.92 | 218.4987 | 437.3 | 419.7 | 362.1 | 351.5 | 446.8 | 61.3 | 18.6 | 108.9 | 4.7 | 183 | 4.9 | 829.3 | 858.6 | 807.2 | 767.1 | 741.2 | 715.1 | 566 | 762.8 | 714.5 | 698 | 646.5 | 712.2 | 636 | 407.6 | 378 | 395.5 | 373 | 364.5 | 364.1 | 357.5 | 352.2
1667.1 | 1504.1 | 468.6 | 187.44 | 219.1066 | 440.4 | 421.9 | 362 | 351 | 443.5 | 61.4 | 18.6 | 108.9 | 4.9 | 182.7 | 5 | 813.8 | 846.2 | 797.6 | 768 | 738 | 715.1 | 565.3 | 758.3 | 714.5 | 698.1 | 646.2 | 698.5 | 635.9 | 407.6 | 378 | 395.5 | 373.2 | 364.5 | 363.9 | 357.3 | 352.2
1668.1 | 1505.1 | 469.2 | 187.68 | 219.3871 | 441.9 | 422.3 | 362.1 | 350.6 | 443.7 | 61.4 | 18.6 | 108.9 | 4.8 | 182.9 | 5 | 798.1 | 828.6 | 787.9 | 768.4 | 736.2 | 715.1 | 561.7 | 738.8 | 713.5 | 694.9 | 645.4 | 675.3 | 630.8 | 407.6 | 378.2 | 395.9 | 373.5 | 364.5 | 363.9 | 357.1 | 352.1
1669.1 | 1506.1 | 469.1 | 187.64 | 219.3403 | 442 | 422 | 362.2 | 350.7 | 445.5 | 61.5 | 18.6 | 108.9 | 5.1 | 182.4 | 4.9 | 789.2 | 816.5 | 781.7 | 768.3 | 733.4 | 715 | 558.2 | 721.7 | 711.8 | 693.4 | 644.4 | 662.5 | 626.4 | 407.6 | 378.6 | 396.3 | 373.8 | 364.5 | 363.9 | 357.1 | 352.1
1670.1 | 1507.1 | 468.9 | 187.56 | 219.2468 | 440.9 | 423 | 362.6 | 351.4 | 444.6 | 61.4 | 18.6 | 109.1 | 5.2 | 182.4 | 4.9 | 805.3 | 821.7 | 784.4 | 767.9 | 736.6 | 714.9 | 555.4 | 716.1 | 710.3 | 692.3 | 643.7 | 662.2 | 626.8 | 407.6 | 378.5 | 396.3 | 373.8 | 364.5 | 364 | 356.9 | 352.1
1671.1 | 1508.1 | 468 | 187.2 | 218.826 | 438.2 | 425.7 | 363 | 351.8 | 439.1 | 61.2 | 18.6 | 109.4 | 5.9 | 182.1 | 4.8 | 818.2 | 831.5 | 791.9 | 768 | 740.9 | 714.8 | 555.6 | 729.3 | 709.9 | 693.3 | 643.3 | 674 | 629 | 407.6 | 378.5 | 396.2 | 373.5 | 364.5 | 364 | 356.9 | 352.1
1672.1 | 1509.1 | 469 | 187.6 | 219.2936 | 433.7 | 430.3 | 362.8 | 352.1 | 438 | 61.1 | 18.6 | 109.6 | 5.5 | 183.3 | 4.4 | 823 | 834.4 | 799.9 | 768.4 | 744.8 | 714.6 | 557.9 | 738 | 710.2 | 694.6 | 643.7 | 682.4 | 630.5 | 407.6 | 378.4 | 395.6 | 373.3 | 364.5 | 364.3 | 357 | 352.1
1673.1 | 1510.1 | 469 | 187.6 | 219.2936 | 429.4 | 434.6 | 362.4 | 351.9 | 436.2 | 61 | 18.6 | 109.7 | 4.7 | 188 | 4 | 828.9 | 834.4 | 799.9 | 768.9 | 746.8 | 714.5 | 557.8 | 738.6 | 710.3 | 695.3 | 644.1 | 694.9 | 635.3 | 407.6 | 378.3 | 395.3 | 373.2 | 364.5 | 364.5 | 357.1 | 352.2
1674.1 | 1511.1 | 468.4 | 187.36 | 219.013 | 427.3 | 435.7 | 361.7 | 351.3 | 430.2 | 61 | 18.6 | 109.8 | 5 | 190.3 | 3.7 | 826.2 | 831.4 | 798.4 | 769.7 | 747.9 | 714.3 | 559.6 | 736.5 | 710.5 | 694.2 | 644.1 | 695.1 | 641.2 | 407.7 | 378 | 395 | 372.9 | 364.5 | 364.5 | 357.1 | 352.2
1675.1 | 1512.1 | 468.3 | 187.32 | 218.9663 | 432.3 | 438.3 | 361.4 | 350.3 | 427.3 | 60.9 | 18.6 | 109.8 | 4.8 | 190.4 | 3.8 | 829.9 | 835.4 | 803.1 | 770.9 | 751.9 | 714.2 | 561.2 | 739.6 | 711.1 | 695.3 | 644.9 | 699.9 | 644.7 | 407.7 | 377.5 | 394.3 | 372.7 | 364.5 | 364.3 | 357.1 | 352.3
1676.1 | 1513.1 | 468.6 | 187.44 | 219.1066 | 435.1 | 441.8 | 360.6 | 349.5 | 424 | 61 | 18.6 | 109.9 | 4.9 | 189.1 | 3.7 | 837.7 | 843.8 | 806.8 | 771.7 | 753.8 | 714 | 564.4 | 746.9 | 712.2 | 696.8 | 646 | 713.2 | 647.1 | 407.7 | 376.9 | 393.6 | 372.6 | 364.5 | 363.9 | 356.9 | 352.2
1677.1 | 1514.1 | 469 | 187.6 | 219.2936 | 434.7 | 444.7 | 359.8 | 349 | 420 | 61.1 | 18.6 | 109.9 | 4.3 | 183.9 | 3.6 | 845.8 | 848.5 | 810.5 | 772.7 | 755.4 | 713.8 | 566.8 | 750.8 | 713.5 | 698.1 | 647.2 | 719.1 | 651.8 | 407.7 | 376.3 | 392.7 | 372.3 | 364.5 | 363.9 | 356.7 | 352.2
1678.1 | 1515.1 | 468.2 | 187.28 | 218.9195 | 434.6 | 445 | 358.8 | 348.6 | 420.2 | 61.1 | 18.6 | 109.9 | 4.6 | 188.2 | 3.5 | 849.6 | 849 | 812.1 | 773.9 | 758.6 | 713.6 | 567.5 | 753.7 | 714.2 | 698.9 | 647.5 | 718.9 | 653 | 407.6 | 375.8 | 391.8 | 372.3 | 364.5 | 363.9 | 356.8 | 352.2
1679.1 | 1516.1 | 468.2 | 187.28 | 218.9195 | 436.4 | 444.1 | 357.7 | 348.5 | 422.8 | 61.1 | 18.6 | 110 | 4.5 | 186 | 3.5 | 849.9 | 848.2 | 816.3 | 775 | 761.7 | 713.5 | 568.4 | 757 | 714.9 | 700.5 | 648.2 | 722.1 | 655.1 | 407.6 | 375.4 | 391.4 | 372.2 | 364.5 | 364 | 357 | 352.2
1680.1 | 1517.1 | 468.4 | 187.36 | 219.013 | 437.9 | 441.6 | 356.5 | 348.4 | 419.8 | 61 | 18.6 | 110.1 | 4.5 | 166.6 | 4 | 858.6 | 854 | 821.5 | 776 | 765 | 713.4 | 570.9 | 763.4 | 716.3 | 702.2 | 649.4 | 730.5 | 655.5 | 407.6 | 374.9 | 391.2 | 372 | 364.5 | 364.1 | 357.2 | 352.3
1681.1 | 1518.1 | 468.8 | 187.52 | 219.2001 | 438.4 | 440.6 | 355.2 | 348.2 | 416.8 | 60.9 | 18.6 | 110.2 | 4.2 | 196.6 | 5 | 859.5 | 856.2 | 823.3 | 776.7 | 767.4 | 713.4 | 572.7 | 768.8 | 717.4 | 702.7 | 649.4 | 724.7 | 653.2 | 407.5 | 374.5 | 390.6 | 371.9 | 364.5 | 363.8 | 357.1 | 352.3
1682.1 | 1519.1 | 469.3 | 187.72 | 219.4339 | 438.7 | 441.5 | 354.7 | 348.2 | 417.5 | 60.8 | 18.6 | 110.2 | 4.8 | 184 | 5.6 | 853.8 | 860.1 | 822.4 | 777.4 | 769.8 | 713.3 | 574.7 | 775.1 | 718.7 | 706 | 649.9 | 731 | 648.2 | 407.5 | 374.2 | 390.1 | 371.9 | 364.5 | 363.5 | 356.8 | 352.2
1683.1 | 1520.1 | 469.5 | 187.8 | 219.5274 | 435.8 | 444.2 | 354.2 | 347.6 | 435.7 | 60.8 | 18.6 | 110.4 | 5 | 185 | 5.8 | 843.2 | 855.9 | 820.5 | 777.9 | 771.2 | 713.4 | 571.2 | 771.5 | 719.4 | 707.7 | 650.5 | 724.3 | 641.6 | 407.4 | 374.2 | 389.9 | 372.1 | 364.5 | 363.3 | 356.6 | 352.1
1684.1 | 1521.1 | 469.3 | 187.72 | 219.4339 | 437.6 | 444.5 | 353.7 | 347.2 | 448.5 | 60.9 | 18.6 | 110.5 | 5.2 | 210.4 | 6 | 841.2 | 860.3 | 822.2 | 778.5 | 771.4 | 713.4 | 570.6 | 774.9 | 719.9 | 709.8 | 650.9 | 719.9 | 637 | 407.4 | 374.2 | 390 | 372.2 | 364.5 | 363.2 | 356.4 | 352
1685.1 | 1522.1 | 469.7 | 187.88 | 219.6209 | 437.9 | 442.4 | 353.8 | 347.3 | 447.4 | 61 | 18.6 | 110.7 | 5.1 | 209.2 | 5 | 841.2 | 862 | 823.7 | 779.2 | 774.8 | 713.5 | 568.8 | 777.4 | 720.3 | 712 | 650.7 | 723.8 | 634 | 407.3 | 374.3 | 389.9 | 372.3 | 364.5 | 363 | 356.1 | 352
1686.1 | 1523.1 | 468.9 | 187.56 | 219.2468 | 437.3 | 443.3 | 354.2 | 347.8 | 447.9 | 61.1 | 18.6 | 110.8 | 4.7 | 164.4 | 4.5 | 845.1 | 864.1 | 823.4 | 779.9 | 776.1 | 713.7 | 567.1 | 781.2 | 721.1 | 713.2 | 650.5 | 722.5 | 634.7 | 407.3 | 374.7 | 390 | 372.6 | 364.4 | 362.7 | 356 | 351.9
1687.1 | 1524.1 | 469.2 | 187.68 | 219.3871 | 438 | 441 | 354.4 | 348.1 | 445.7 | 61.1 | 18.6 | 110.8 | 4.7 | 144.5 | 4.6 | 846.6 | 863.9 | 821 | 781 | 776.5 | 713.8 | 565.3 | 774.8 | 720.8 | 713.9 | 650.7 | 723.6 | 639.9 | 407.2 | 374.8 | 390.3 | 372.6 | 364.4 | 362.6 | 355.8 | 351.9
1688.1 | 1525.1 | 469.1 | 187.64 | 219.3403 | 435.4 | 438.6 | 355.1 | 348.4 | 444 | 61 | 18.6 | 110.8 | 5.1 | 145.4 | 4.3 | 844.2 | 865.7 | 824.4 | 781.8 | 777.1 | 713.9 | 566.7 | 777.4 | 720.9 | 714.6 | 650.7 | 720.6 | 645.5 | 407.1 | 374.9 | 390.3 | 372.6 | 364.4 | 362.6 | 355.8 | 351.9
1689.1 | 1526.1 | 469 | 187.6 | 219.2936 | 429.9 | 436.3 | 355.9 | 348.3 | 440.5 | 61 | 18.6 | 110.7 | 4.7 | 154.9 | 4.4 | 847.2 | 869.3 | 830.2 | 782 | 778.4 | 714.1 | 568.8 | 780.3 | 721.9 | 715.9 | 650.7 | 727.9 | 646.8 | 407.1 | 374.9 | 390.2 | 372.5 | 364.4 | 362.5 | 355.7 | 351.9
1690.1 | 1527.1 | 468.1 | 187.24 | 218.8728 | 426.9 | 435.4 | 356.2 | 348.3 | 440.1 | 61 | 18.6 | 110.7 | 5 | 173.2 | 4.4 | 842.3 | 869.4 | 830.1 | 782.7 | 781.5 | 714.3 | 568.6 | 779.6 | 723.1 | 717.6 | 651.1 | 729.1 | 643.6 | 407.1 | 375.1 | 390.3 | 372.4 | 364.4 | 362.2 | 355.6 | 352
1691.1 | 1528.1 | 468 | 187.2 | 218.826 | 427.8 | 440.7 | 356.2 | 348.2 | 444.8 | 61.1 | 18.6 | 110.6 | 4.7 | 184.2 | 4.9 | 834.7 | 863.5 | 825.5 | 783.3 | 781.5 | 714.6 | 564.1 | 772 | 723.4 | 718.1 | 651.3 | 726.8 | 639.4 | 407 | 375 | 390.2 | 372.4 | 364.4 | 361.8 | 355.4 | 351.9
1692.1 | 1529.1 | 468 | 187.2 | 218.826 | 429.6 | 445.3 | 356.1 | 347.6 | 452.6 | 61.3 | 18.6 | 110.5 | 4.5 | 183 | 5.3 | 832.7 | 862.5 | 822.9 | 783.4 | 782.6 | 714.7 | 561.9 | 776.5 | 723.6 | 718.7 | 651.3 | 722 | 634.5 | 407 | 375 | 390 | 372.4 | 364.4 | 361.6 | 355.3 | 351.9
1693.1 | 1530.1 | 467.8 | 187.12 | 218.7325 | 431.4 | 446 | 355.8 | 346.7 | 466.3 | 61.4 | 18.6 | 110.6 | 5.2 | 179.8 | 5.3 | 826.1 | 855.3 | 816.4 | 783.2 | 780.7 | 714.9 | 560.6 | 774.2 | 723.7 | 719.9 | 651.8 | 716.9 | 630.1 | 407 | 375.1 | 390 | 372.4 | 364.4 | 361.6 | 355.1 | 351.7
1694.1 | 1531.1 | 468.8 | 187.52 | 219.2001 | 434.6 | 446.8 | 355.4 | 346.6 | 469.9 | 61.5 | 18.6 | 110.7 | 5.2 | 177.5 | 5.2 | 812.6 | 834.5 | 794.6 | 783.2 | 774.5 | 714.9 | 558.7 | 762.2 | 722.9 | 718.1 | 651.4 | 697.6 | 626.3 | 406.9 | 375.6 | 390.6 | 372.8 | 364.4 | 361.7 | 355 | 351.7
1695.1 | 1532.1 | 469.5 | 187.8 | 219.5274 | 439.8 | 444.5 | 355.9 | 346.8 | 464 | 61.6 | 18.6 | 110.7 | 5.1 | 174.9 | 5.6 | 787.6 | 802.2 | 769.7 | 782.8 | 766.8 | 714.8 | 555.4 | 731.8 | 720.8 | 712.4 | 650.2 | 672.8 | 623 | 406.9 | 376.1 | 391.1 | 373.2 | 364.4 | 361.9 | 355 | 351.6
1696.1 | 1533.1 | 470.1 | 188.04 | 219.8079 | 442.5 | 446.2 | 357.4 | 347.6 | 463.2 | 61.6 | 18.6 | 110.7 | 5.2 | 175.1 | 5.7 | 772.7 | 784.1 | 754.5 | 782.3 | 761.6 | 714.8 | 552.7 | 713.3 | 718 | 708.8 | 648.8 | 654.8 | 618.6 | 406.9 | 376.6 | 391.6 | 373.5 | 364.3 | 362.3 | 355.3 | 351.5
1697.1 | 1534.1 | 469.3 | 187.72 | 219.4339 | 442.2 | 447 | 359.2 | 348.4 | 459.1 | 61.5 | 18.6 | 110.8 | 5.1 | 173.6 | 5.9 | 760 | 769.4 | 746.5 | 781.2 | 756 | 714.7 | 551.2 | 698.5 | 715.1 | 705.5 | 647.3 | 639.2 | 614.5 | 406.8 | 377.1 | 392.6 | 373.6 | 364.3 | 362.9 | 355.4 | 351.6
1698.1 | 1535.1 | 469.9 | 187.96 | 219.7144 | 443.1 | 444.6 | 360.6 | 349 | 455.8 | 61.5 | 18.6 | 110.8 | 4.9 | 174.1 | 5.9 | 759.2 | 764.4 | 746.4 | 780.4 | 752.8 | 714.5 | 550.1 | 692.8 | 712.9 | 702.7 | 646.1 | 631.7 | 614.2 | 406.8 | 377.4 | 393.2 | 373.7 | 364.3 | 363.2 | 355.6 | 351.6
1699.1 | 1536.1 | 467.4 | 186.96 | 218.5455 | 443 | 446.5 | 361.8 | 349.4 | 452 | 61.7 | 18.6 | 110.7 | 4.8 | 174.9 | 5.7 | 751.4 | 753.9 | 735.4 | 779.3 | 747.1 | 714.3 | 549.6 | 684.6 | 711.2 | 699.6 | 645.1 | 624.6 | 616.5 | 406.8 | 377.8 | 393.8 | 373.7 | 364.3 | 363.5 | 355.7 | 351.6
1700.1 | 1537.1 | 466.7 | 186.68 | 218.2182 | 441.6 | 449.4 | 362.4 | 350.4 | 447.4 | 61.8 | 18.6 | 110.7 | 5.2 | 177.9 | 5.2 | 738.3 | 738.3 | 720.2 | 778.4 | 740.8 | 714 | 547.1 | 670 | 708.8 | 694.9 | 644.1 | 612.1 | 621.9 | 406.8 | 378.2 | 394.7 | 373.8 | 364.3 | 363.9 | 355.9 | 351.6
1701.1 | 1538.1 | 467.2 | 186.88 | 218.452 | 445.1 | 450.3 | 363.2 | 351 | 442.7 | 61.8 | 18.6 | 110.8 | 5 | 177.8 | 4.9 | 729.5 | 726.2 | 713.5 | 777.4 | 735.3 | 713.7 | 543.5 | 660.4 | 706.5 | 691.8 | 643.1 | 600.2 | 624.9 | 406.8 | 378.5 | 395.4 | 374 | 364.3 | 364 | 356 | 351.6
1702.1 | 1539.1 | 468.1 | 187.24 | 218.8728 | 447.6 | 447 | 364.7 | 351.8 | 439.9 | 61.9 | 18.6 | 110.8 | 4.7 | 179.7 | 5 | 715 | 709.3 | 700.9 | 775.9 | 729.3 | 713.4 | 540.1 | 649.1 | 704 | 687.6 | 641.9 | 589.3 | 625.2 | 406.9 | 379.2 | 396.3 | 374.2 | 364.3 | 364.1 | 356 | 351.6
1703.1 | 1540.1 | 467.5 | 187 | 218.5922 | 448.1 | 444.5 | 366 | 352 | 438.3 | 61.9 | 18.6 | 110.8 | 4.7 | 191.3 | 5.3 | 703.8 | 695.5 | 689.4 | 774.5 | 723.3 | 712.9 | 537.8 | 639.6 | 701.6 | 684.3 | 641 | 579.9 | 625.2 | 406.9 | 379.5 | 397.1 | 374.2 | 364.3 | 364.4 | 356.3 | 351.7
1704.1 | 1541.1 | 468 | 187.2 | 218.826 | 447.6 | 443.1 | 366.9 | 352.3 | 435.1 | 62 | 18.6 | 110.9 | 4.5 | 202.9 | 4.9 | 696.5 | 686.6 | 684.1 | 773 | 717.9 | 712.5 | 534 | 627.4 | 699.3 | 680.2 | 640.2 | 572.8 | 628.6 | 407 | 379.8 | 397.6 | 374.3 | 364.3 | 364.8 | 356.6 | 351.7
1705.1 | 1542.1 | 468.2 | 187.28 | 218.9195 | 445.7 | 443.1 | 367.3 | 352.9 | 432.5 | 62 | 18.6 | 110.9 | 4.9 | 195.8 | 4.7 | 704.4 | 701.9 | 697.4 | 771.6 | 715.4 | 712 | 534.7 | 639.9 | 698.3 | 678.7 | 639.4 | 571.3 | 633.3 | 407 | 380 | 398 | 374.2 | 364.3 | 365.2 | 356.9 | 351.7
1706.1 | 1543.1 | 468 | 187.2 | 218.826 | 442.2 | 441.8 | 367.8 | 353.7 | 427.3 | 61.9 | 18.6 | 110.9 | 5.2 | 192.8 | 5.2 | 730.2 | 732 | 723.5 | 770.5 | 717.9 | 711.5 | 537.5 | 670.2 | 699.3 | 681.1 | 639.2 | 589.1 | 644.6 | 407.1 | 380.1 | 398.3 | 374 | 364.3 | 365.4 | 357.3 | 351.8
1707.1 | 1544.1 | 466.3 | 186.52 | 218.0311 | 441.1 | 439.4 | 368.2 | 354.4 | 423.6 | 61.7 | 18.6 | 111 | 5.4 | 194.8 | 5.6 | 752.5 | 755.6 | 748.3 | 769.9 | 723.7 | 711.1 | 541.1 | 694.5 | 701 | 683.3 | 639.8 | 611.9 | 648.2 | 407.2 | 380.1 | 398.3 | 373.8 | 364.4 | 365.7 | 357.8 | 352
1708.1 | 1545.1 | 193.6 | 77.44 | 90.5229 | 439.6 | 441.6 | 368.3 | 354.9 | 423 | 61.5 | 18.6 | 111 | 5 | 196.5 | 5.6 | 769.2 | 774.2 | 769.2 | 769.6 | 730.1 | 710.7 | 546.7 | 712.2 | 702.4 | 685.5 | 640.7 | 634.7 | 645.7 | 407.3 | 379.9 | 398.1 | 373.6 | 364.4 | 365.8 | 358.3 | 352.1
1709.1 | 1546.1 | -6.8 | 0 | 0 | 442.5 | 449.1 | 367.6 | 354.6 | 419.6 | 61.5 | 18.6 | 110.9 | 4.5 | 193.8 | 5.6 | 767.1 | 774.9 | 771.9 | 769.5 | 729.5 | 710.4 | 550.1 | 716.5 | 703.9 | 687 | 641.7 | 645.8 | 641.3 | 407.3 | 379.4 | 397.8 | 373.4 | 364.4 | 365.7 | 358.3 | 352.2
1710.1 | 1547.1 | -6.8 | 0 | 0 | 447.1 | 455.8 | 366.6 | 353.8 | 413.7 | 61.5 | 18.6 | 110.9 | 4.4 | 186.1 | 5.4 | 741.9 | 737.7 | 744.3 | 768.4 | 720.9 | 709.9 | 544.9 | 683.4 | 702 | 680.6 | 641.1 | 625.3 | 632.9 | 407.4 | 378.4 | 397 | 372.8 | 364.4 | 365.3 | 357.9 | 352
1711.1 | 1548.1 | -6.8 | 0 | 0 | 447.6 | 458.8 | 365.1 | 352.7 | 406.8 | 61.4 | 18.6 | 110.9 | 4.3 | 185.8 | 5.2 | 715.5 | 701.3 | 715.3 | 766.8 | 712.5 | 709.6 | 538.1 | 649.5 | 698.5 | 674.8 | 640.2 | 606.3 | 622.3 | 407.5 | 377.3 | 395.9 | 372 | 364.4 | 364.5 | 357.3 | 351.8
1712.1 | 1549.1 | -6.8 | 0 | 0 | 447.9 | 460.4 | 362.9 | 351.1 | 402.4 | 61.2 | 18.6 | 110.8 | 4 | 186.7 | 5.1 | 688.2 | 668.7 | 691.5 | 764.7 | 705.4 | 709.2 | 530.5 | 621.4 | 694.4 | 669.3 | 639.1 | 588.2 | 611.6 | 407.6 | 375.8 | 394.6 | 371.2 | 364.4 | 363.7 | 356.5 | 351.5
1713.1 | 1550.1 | -6.7 | 0 | 0 | 448.6 | 464.4 | 360.7 | 349.1 | 397.4 | 61 | 18.6 | 110.8 | 4.2 | 187.3 | 5 | 669 | 641.3 | 670.9 | 762.5 | 697.3 | 708.7 | 523.7 | 596.8 | 690.1 | 664 | 637.8 | 571.8 | 601.1 | 407.6 | 374.3 | 393.1 | 370.5 | 364.5 | 362.9 | 355.5 | 351.3
1714.1 | 1551.1 | -6.7 | 0 | 0 | 444.7 | 465 | 358.2 | 347 | 394.4 | 60.9 | 18.6 | 110.7 | 4.3 | 188.3 | 5 | 651.9 | 619 | 653.3 | 760 | 689.6 | 708 | 517.2 | 577.2 | 686.1 | 658.7 | 636.5 | 559.4 | 590.8 | 407.6 | 372.7 | 391.5 | 369.8 | 364.4 | 362.2 | 354.4 | 350.9
1715.1 | 1552.1 | -6.7 | 0 | 0 | 441.4 | 461 | 355.5 | 344.8 | 390.8 | 60.9 | 18.6 | 110.5 | 4.1 | 188.6 | 4.9 | 632.8 | 598 | 638.3 | 757.6 | 682.9 | 707.4 | 510.9 | 558.7 | 681.4 | 654 | 634.9 | 548 | 580.9 | 407.6 | 371 | 389.9 | 369.1 | 364.4 | 361.5 | 353.2 | 350.5
1716.1 | 1553.1 | -6.7 | 0 | 0 | 438.5 | 454 | 352.8 | 342.5 | 387.2 | 60.9 | 18.6 | 110.2 | 4.8 | 188.3 | 4.7 | 616.3 | 578.6 | 624.8 | 755.3 | 676.3 | 706.5 | 504.5 | 542.3 | 677.5 | 649.1 | 633.4 | 537.1 | 571.7 | 407.6 | 368.8 | 388.6 | 368.4 | 364.4 | 360.5 | 351.8 | 350.1
1717.1 | 1554.1 | -6.7 | 0 | 0 | 436.8 | 453.6 | 350.4 | 340.2 | 383.9 | 60.9 | 18.6 | 109.9 | 4.7 | 188.7 | 4.5 | 603.2 | 560.2 | 612.1 | 752.9 | 668.8 | 705.6 | 498.3 | 526.3 | 673.5 | 643.9 | 632.3 | 526.6 | 562.5 | 407.6 | 366.6 | 386.9 | 367.6 | 364.4 | 359.6 | 350.6 | 349.7
1718.1 | 1555.1 | -6.8 | 0 | 0 | 431.4 | 455.5 | 348.1 | 338.3 | 380.8 | 60.9 | 18.6 | 109.5 | 4.4 | 192 | 4.2 | 590.6 | 545.3 | 601.1 | 750.6 | 662.7 | 704.6 | 492.5 | 512.9 | 669.4 | 638.9 | 631.4 | 519 | 553.9 | 407.5 | 364.5 | 385.2 | 366.9 | 364.4 | 359 | 349.6 | 349.3
1719.1 | 1556.1 | -6.8 | 0 | 0 | 428.7 | 451.8 | 346 | 336.3 | 377.8 | 60.9 | 18.6 | 109.2 | 4.7 | 200.5 | 4 | 578.1 | 532 | 591.1 | 748.1 | 657.1 | 703.6 | 488.1 | 500.1 | 665.8 | 634.4 | 630.5 | 512 | 546 | 407.5 | 362.5 | 383.5 | 366.3 | 364.3 | 358.2 | 348.4 | 348.9
1720.1 | 1557.1 | -6.7 | 0 | 0 | 425.7 | 447.4 | 344 | 334.1 | 375.7 | 60.7 | 18.6 | 108.8 | 4.5 | 199.7 | 3.8 | 564.1 | 520.6 | 581.9 | 745.6 | 651.3 | 702.7 | 483.1 | 488.8 | 662.2 | 630.2 | 629.3 | 505.5 | 538.4 | 407.4 | 360.6 | 381.8 | 365.7 | 364.3 | 357.4 | 347 | 348.5
1721.1 | 1558.1 | -6.8 | 0 | 0 | 421.8 | 443.2 | 341.9 | 332 | 373.5 | 60.6 | 18.6 | 108.4 | 4.6 | 193.6 | 3.8 | 550.7 | 512.4 | 573.7 | 743.2 | 645.6 | 701.6 | 478.9 | 479.6 | 659.2 | 626 | 628.5 | 499.9 | 531.1 | 407.3 | 358.6 | 380.2 | 365.1 | 364.2 | 356.5 | 345.7 | 348.1
1722.1 | 1559.1 | -6.8 | 0 | 0 | 417.8 | 437.6 | 339.7 | 329.8 | 370.9 | 60.5 | 18.6 | 108 | 4.7 | 192.6 | 4 | 539.2 | 502.5 | 566.7 | 740.8 | 640.4 | 700.4 | 474.9 | 471 | 656.4 | 621.6 | 628 | 493.9 | 523.8 | 407.1 | 356.4 | 378.7 | 364.5 | 364.1 | 355.5 | 344.3 | 347.6
1723.1 | 1560.1 | -6.8 | 0 | 0 | 415.7 | 433.1 | 337.6 | 327.7 | 367.9 | 60.4 | 18.6 | 107.6 | 3.9 | 191.3 | 4 | 528.5 | 495 | 560 | 738.5 | 635.1 | 699.2 | 471.7 | 462.8 | 653.8 | 617.6 | 627.7 | 489 | 516.1 | 407 | 354.4 | 377.1 | 363.8 | 364.1 | 354.5 | 342.9 | 347.2
1724.1 | 1561.1 | -6.7 | 0 | 0 | 413.4 | 428.4 | 335.5 | 325.8 | 365.7 | 60.3 | 18.6 | 107.3 | 4.1 | 198 | 4.5 | 520.5 | 485 | 554.2 | 736.1 | 630 | 697.9 | 468 | 453.9 | 651.4 | 613.5 | 627 | 482.5 | 509 | 406.8 | 352.5 | 375.5 | 363.1 | 364 | 353.5 | 341.3 | 346.7
1725.1 | 1562.1 | -6.7 | 0 | 0 | 411.8 | 423.8 | 333.5 | 324 | 363.7 | 60.4 | 18.6 | 107 | 4.5 | 202 | 4.8 | 517.3 | 474.2 | 548.7 | 733.9 | 625.1 | 696.5 | 464.4 | 446 | 648.9 | 609.6 | 626.3 | 477.7 | 503 | 406.7 | 350.7 | 374.1 | 362.6 | 363.9 | 352.3 | 339.4 | 346.2
1726.1 | 1563.1 | -6.7 | 0 | 0 | 408.7 | 421.1 | 331.7 | 322.2 | 361.6 | 60.5 | 18.6 | 106.6 | 4.1 | 202.5 | 5 | 515.5 | 463.6 | 542.6 | 731.7 | 620.9 | 695.2 | 460.5 | 437.9 | 646.9 | 606 | 625.4 | 473 | 497.3 | 406.5 | 349.1 | 372.7 | 362 | 363.8 | 351 | 337.7 | 345.7
1727.1 | 1564.1 | -6.7 | 0 | 0 | 404.9 | 418.1 | 329.9 | 320.5 | 359.7 | 60.5 | 18.6 | 106.2 | 4.2 | 198.4 | 4.8 | 512 | 453.4 | 536.5 | 729.4 | 616.4 | 693.9 | 458.3 | 431 | 644.1 | 602.2 | 624.3 | 470.2 | 491.8 | 406.3 | 347.4 | 371.3 | 361.5 | 363.7 | 349.9 | 336.2 | 345.2
1728.1 | 1565.1 | -6.7 | 0 | 0 | 403.4 | 415.4 | 328.2 | 318.8 | 357.6 | 60.6 | 18.6 | 105.9 | 4.1 | 194.5 | 4.5 | 506.7 | 442.7 | 531.1 | 727.2 | 612.2 | 692.5 | 455.4 | 424.8 | 641.4 | 598.8 | 623.2 | 467.4 | 485.5 | 406.1 | 345.7 | 370 | 360.9 | 363.6 | 348.9 | 335 | 344.8
1729.1 | 1566.1 | -6.7 | 0 | 0 | 406.9 | 412.6 | 326.5 | 317.2 | 355.7 | 60.6 | 18.6 | 105.6 | 4 | 197.5 | 4.4 | 502 | 433.5 | 525.2 | 725 | 607.7 | 691.2 | 452.6 | 417.8 | 640 | 595.3 | 622.7 | 462.6 | 479 | 405.9 | 344 | 368.7 | 360.4 | 363.4 | 348.1 | 333.8 | 344.3
1730.1 | 1567.1 | -6.7 | 0 | 0 | 411.3 | 409.1 | 325.2 | 315.7 | 353.6 | 60.7 | 18.6 | 105.3 | 3.9 | 213.4 | 4.3 | 496.7 | 424.3 | 519.7 | 722.8 | 603.5 | 689.9 | 449.6 | 412.4 | 639.2 | 591.5 | 622.1 | 458.7 | 472.7 | 405.6 | 342.5 | 367.4 | 359.7 | 363.3 | 347.3 | 332.9 | 343.9
1731.1 | 1568.1 | -6.7 | 0 | 0 | 412.4 | 408 | 323.7 | 314.3 | 351.5 | 60.8 | 18.6 | 105 | 3.6 | 217.8 | 4.1 | 492.4 | 417.7 | 514.4 | 720.4 | 598.8 | 688.5 | 446.7 | 406.8 | 638 | 588.2 | 621.4 | 455.1 | 466.7 | 405.4 | 341 | 366.1 | 359.2 | 363.2 | 346.2 | 331.5 | 343.5
1732.1 | 1569.1 | -6.7 | 0 | 0 | 409.1 | 407 | 322.1 | 313.1 | 349.7 | 60.8 | 18.6 | 104.7 | 4 | 205.9 | 3.9 | 485.4 | 412.6 | 509.5 | 718.2 | 593.9 | 687.1 | 444.4 | 401.2 | 636.3 | 585.3 | 620.5 | 451.8 | 461.9 | 405.2 | 339.5 | 364.5 | 358.7 | 363 | 345.2 | 330 | 342.9
1733.1 | 1570.1 | -6.7 | 0 | 0 | 409.9 | 405.2 | 320.7 | 311.8 | 348.6 | 60.8 | 18.6 | 104.4 | 4 | 202.3 | 3.8 | 479.7 | 407.6 | 505 | 716.1 | 589.8 | 685.6 | 441.3 | 395.9 | 634.6 | 581.9 | 619.1 | 449.5 | 458 | 404.9 | 338.1 | 363.2 | 358.1 | 362.9 | 344 | 328.8 | 342.5
1734.1 | 1571.1 | -6.7 | 0 | 0 | 407.1 | 404.2 | 319.2 | 310.5 | 347.3 | 60.6 | 18.6 | 104.2 | 4.2 | 205.2 | 3.9 | 477.8 | 401.3 | 501.1 | 714 | 585.8 | 684.2 | 438.7 | 391.3 | 632.2 | 578.7 | 618.1 | 448.1 | 454.3 | 404.7 | 336.8 | 361.9 | 357.5 | 362.7 | 343 | 327.7 | 342.1
1735.1 | 1572.1 | -6.7 | 0 | 0 | 409.3 | 404.1 | 318 | 309.1 | 345.6 | 60.5 | 18.6 | 103.9 | 3.9 | 207 | 4 | 474.6 | 395.2 | 497.1 | 712.1 | 582 | 682.8 | 436.9 | 386.3 | 629.8 | 575.6 | 617.6 | 447.4 | 450.8 | 404.4 | 335.6 | 360.9 | 357 | 362.5 | 342.2 | 326.7 | 341.6
1736.1 | 1573.1 | -6.7 | 0 | 0 | 407.7 | 403.3 | 316.9 | 308.1 | 344.3 | 60.4 | 18.6 | 103.7 | 4.1 | 208.9 | 4 | 468.8 | 388.1 | 492.4 | 710.2 | 578.4 | 681.2 | 434.3 | 382 | 627.2 | 572.4 | 616.9 | 445.8 | 446.8 | 404.1 | 334.4 | 359.7 | 356.5 | 362.4 | 341.4 | 325.5 | 341.2
1737.1 | 1574.1 | -6.7 | 0 | 0 | 407.9 | 402.6 | 315.6 | 307 | 343.4 | 60.4 | 18.6 | 103.5 | 3.9 | 207.6 | 3.9 | 465.7 | 382.5 | 488.6 | 708.3 | 574.5 | 679.7 | 432.3 | 379.4 | 621.4 | 569.6 | 616.7 | 445.5 | 442.9 | 403.8 | 333.2 | 358.5 | 356.1 | 362.2 | 340.7 | 324.5 | 340.7
1738.1 | 1575.1 | -6.7 | 0 | 0 | 408.4 | 406.7 | 314.5 | 305.9 | 341.8 | 60.4 | 18.6 | 103.3 | 4.2 | 206.7 | 3.8 | 466.4 | 379.2 | 488.3 | 705.1 | 571.4 | 678.3 | 428.4 | 382.3 | 616 | 567.6 | 616.3 | 444.5 | 438.9 | 403.6 | 332.1 | 357.4 | 355.6 | 362 | 339.7 | 323.3 | 340.3
1739.1 | 1576.1 | -6.7 | 0 | 0 | 411.2 | 410.1 | 313.6 | 304.9 | 339.7 | 60.3 | 18.6 | 103.1 | 4.4 | 205.7 | 3.6 | 460.9 | 374.7 | 484 | 702.7 | 567.3 | 676.9 | 423.9 | 382.8 | 612.5 | 565 | 615.3 | 445.1 | 435.2 | 403.3 | 331.3 | 356.2 | 355.1 | 361.9 | 338.8 | 322.2 | 339.8
1740.1 | 1577.1 | -6.7 | 0 | 0 | 408.3 | 408 | 312.5 | 304.1 | 336.4 | 60.2 | 18.6 | 102.9 | 4.1 | 205.3 | 3.7 | 458.6 | 371.3 | 480.7 | 700.2 | 563.8 | 675.4 | 406.3 | 379 | 590.5 | 563 | 614.5 | 443.7 | 431.9 | 403 | 330.3 | 355.1 | 354.6 | 361.7 | 338.2 | 321.3 | 339.3
1741.1 | 1578.1 | -6.7 | 0 | 0 | 398.9 | 407.4 | 311.4 | 303.1 | 331.4 | 60.1 | 18.6 | 102.7 | 4.1 | 207 | 3.7 | 454.1 | 367.9 | 479.1 | 697.3 | 561.4 | 673.9 | 399.6 | 378.7 | 583 | 560.7 | 613.4 | 442.5 | 428.6 | 402.7 | 328.9 | 354.1 | 354 | 361.5 | 337.6 | 320.5 | 338.8
1742.1 | 1579.1 | -6.7 | 0 | 0 | 400 | 412.2 | 310.3 | 302.1 | 329.5 | 60 | 18.6 | 102.5 | 4.2 | 205.5 | 3.7 | 447.7 | 363.6 | 476 | 695.2 | 558.2 | 672.2 | 387.2 | 376.3 | 566.1 | 558.5 | 612.4 | 442.2 | 425.3 | 402.4 | 327.9 | 353.1 | 353.5 | 361.3 | 337 | 319.8 | 338.4
1743.1 | 1580.1 | -6.7 | 0 | 0 | 393.5 | 415.9 | 309.2 | 301 | 327.3 | 60 | 18.6 | 102.4 | 4.4 | 207.5 | 3.6 | 446.7 | 357.9 | 474.8 | 692.7 | 555.5 | 670.3 | 369.4 | 368.2 | 549.6 | 556.4 | 611.4 | 441 | 421.4 | 402.1 | 326.7 | 352.3 | 353 | 361.1 | 336.3 | 318.7 | 337.9
1744.1 | 1581.1 | -6.7 | 0 | 0 | 394.6 | 419.7 | 307.7 | 299.8 | 323.7 | 59.9 | 18.6 | 102.2 | 4.4 | 209.1 | 3.5 | 437 | 352 | 469.8 | 690.6 | 552.2 | 668 | 350.2 | 341.1 | 544 | 554.5 | 610 | 438.4 | 417.5 | 401.8 | 325.6 | 351.6 | 352.2 | 360.9 | 335.3 | 317.4 | 337.4
1745.1 | 1582.1 | -6.7 | 0 | 0 | 396 | 427.3 | 306.3 | 298.5 | 319.9 | 59.7 | 18.6 | 102.1 | 3.9 | 210 | 3.3 | 426.2 | 346.6 | 463.4 | 688.2 | 548.6 | 665.1 | 335.6 | 328.2 | 537.4 | 552 | 588.6 | 425.6 | 413.7 | 401.4 | 324.3 | 350.6 | 351.4 | 360.7 | 334.4 | 316.4 | 336.9
1746.1 | 1583.1 | -6.7 | 0 | 0 | 396.6 | 430.4 | 305.2 | 297.2 | 316.9 | 59.7 | 18.6 | 101.9 | 3.8 | 204.7 | 2.9 | 418.9 | 337.1 | 456.5 | 685.4 | 545.6 | 661.9 | 334.8 | 319.3 | 514.2 | 548.8 | 578.6 | 416.6 | 409.5 | 401.1 | 322.7 | 349.3 | 350.6 | 360.5 | 333.6 | 315.6 | 336.4
1747.1 | 1584.1 | -6.7 | 0 | 0 | 395.5 | 422.2 | 304.1 | 295.8 | 312.4 | 59.7 | 18.6 | 101.7 | 4.1 | 190.2 | 2.6 | 412.2 | 324.6 | 451 | 678.1 | 542.5 | 658.6 | 330 | 309.3 | 499.2 | 545.9 | 572.8 | 411.2 | 405.2 | 400.8 | 321.3 | 348 | 349.8 | 360.3 | 332.9 | 314.5 | 335.9
1748.1 | 1585.1 | -6.7 | 0 | 0 | 391.5 | 414.6 | 303 | 294.5 | 308.1 | 59.6 | 18.6 | 101.5 | 4.1 | 191.1 | 2.8 | 400.7 | 308.2 | 443.3 | 670.2 | 538.9 | 651.6 | 316.8 | 289.8 | 484.2 | 542.7 | 566.4 | 407.5 | 401.5 | 400.4 | 320.6 | 346.8 | 349.4 | 360.1 | 332.3 | 313.4 | 335.4
1749.1 | 1586.1 | -6.7 | 0 | 0 | 390 | 408.8 | 302 | 293.7 | 303.8 | 59.6 | 18.6 | 101.3 | 4.6 | 205.1 | 3.1 | 391.7 | 295.6 | 436.6 | 663.4 | 535.3 | 643.1 | 305.5 | 254.7 | 470.9 | 538.8 | 558.7 | 399.8 | 398.2 | 400.1 | 319.4 | 345.6 | 348.9 | 359.9 | 331.5 | 312 | 334.8
1750.1 | 1587.1 | -6.7 | 0 | 0 | 388.6 | 403.7 | 301.2 | 293 | 302.3 | 59.6 | 18.6 | 101 | 4.1 | 212.8 | 3.4 | 382.2 | 280.1 | 428.6 | 657.2 | 532.1 | 633.5 | 288.2 | 233.5 | 463.7 | 534.3 | 552.5 | 389.3 | 395.2 | 399.7 | 318.3 | 344.3 | 348.3 | 359.7 | 330.7 | 311.2 | 334.3
1751.1 | 1588.1 | -6.7 | 0 | 0 | 383.2 | 398.2 | 300.2 | 292.3 | 301.1 | 59.6 | 18.6 | 100.8 | 4.9 | 206 | 3.5 | 372.4 | 265.7 | 419.4 | 651.4 | 529.2 | 621.3 | 259.1 | 224.1 | 457.4 | 530.3 | 548.6 | 367.8 | 391.6 | 399.4 | 317.5 | 343.1 | 347.7 | 359.5 | 329.9 | 310.6 | 333.9
1752.1 | 1589.1 | -6.7 | 0 | 0 | 380.5 | 394.3 | 299.2 | 291.6 | 299 | 59.5 | 18.6 | 100.6 | 4.6 | 191.5 | 3.5 | 364.2 | 221.1 | 413.3 | 645.3 | 525.8 | 598.7 | 228.2 | 216.5 | 450.2 | 526.1 | 544.6 | 346 | 387.4 | 399 | 316.5 | 342 | 347.2 | 359.2 | 329.2 | 310.2 | 333.4
1753.1 | 1590.1 | -6.7 | 0 | 0 | 381.5 | 391.7 | 298.3 | 290.7 | 296.5 | 59.4 | 18.6 | 100.4 | 4.5 | 175.7 | 3.6 | 358.8 | 112.9 | 408.2 | 639.7 | 522.3 | 368 | 215.4 | 191.5 | 439.4 | 522.6 | 542 | 302 | 383.4 | 398.6 | 315.7 | 340.8 | 346.8 | 359 | 328.6 | 309.4 | 333
1754.1 | 1591.1 | -6.7 | 0 | 0 | 388 | 391.2 | 297.4 | 289.8 | 293.6 | 59.3 | 18.6 | 100.2 | 4.4 | 189.6 | 4.2 | 353.4 | 94.8 | 402.9 | 634.6 | 519.1 | 110 | 206.9 | 172.4 | 432.6 | 517.8 | 540.1 | 258.8 | 379.5 | 398.2 | 314.7 | 339.8 | 346.2 | 358.8 | 327.9 | 308.5 | 332.5
1755.1 | 1592.1 | -6.7 | 0 | 0 | 390.6 | 388.9 | 296.5 | 288.8 | 289.9 | 59.2 | 18.6 | 100 | 4.2 | 203.1 | 4.6 | 347.1 | 89.2 | 397.3 | 630 | 515.7 | 108.6 | 190.2 | 156.2 | 425.2 | 512.2 | 538.2 | 254.1 | 375.5 | 397.9 | 313.7 | 338.8 | 345.6 | 358.6 | 327.1 | 307.9 | 332
1756.1 | 1593.1 | -6.7 | 0 | 0 | 390.5 | 388.8 | 295.6 | 287.9 | 285.6 | 59.2 | 18.6 | 99.8 | 4.1 | 178.7 | 4.5 | 344.8 | 86.4 | 369 | 625.3 | 512.3 | 108 | 178.6 | 136.2 | 418.5 | 504.2 | 534.9 | 248.3 | 371.4 | 397.5 | 312.7 | 337.9 | 345 | 358.4 | 326.2 | 307.1 | 331.6
1757.1 | 1594.1 | -6.7 | 0 | 0 | 390.1 | 387.1 | 294.7 | 287.1 | 282.1 | 59.1 | 18.6 | 99.5 | 4.4 | 175.3 | 4.6 | 340.1 | 81.3 | 344.8 | 620.1 | 509.8 | 107.7 | 173.2 | 113 | 410.9 | 497.1 | 533.6 | 243.2 | 367.5 | 397.1 | 311.6 | 337 | 344.5 | 358.1 | 325.3 | 306.1 | 331
1758.1 | 1595.1 | -6.7 | 0 | 0 | 389 | 384.8 | 293.8 | 286.2 | 280.2 | 59 | 18.6 | 99.3 | 4.6 | 217 | 4.5 | 336.7 | 72.7 | 339.9 | 613.5 | 507 | 107.2 | 168.7 | 100 | 404 | 490.8 | 533.4 | 241.7 | 363.6 | 396.7 | 310.6 | 335.9 | 343.9 | 357.9 | 324.7 | 305.2 | 330.5
1759.1 | 1596.1 | -6.7 | 0 | 0 | 386.6 | 383.4 | 292.8 | 285.3 | 278.9 | 58.9 | 18.6 | 99.1 | 4.7 | 216 | 4 | 330.7 | 66.9 | 330.2 | 605.2 | 503.4 | 106.3 | 146.4 | 93.1 | 398.2 | 484.6 | 532.8 | 240.6 | 359.7 | 396.2 | 309.4 | 335 | 343.3 | 357.7 | 323.8 | 304.2 | 330
1760.1 | 1597.1 | -6.7 | 0 | 0 | 387.5 | 383.5 | 291.7 | 284.3 | 277.3 | 58.8 | 18.6 | 98.8 | 4.9 | 195.2 | 5.1 | 324.1 | 62.8 | 309.1 | 594.7 | 500.1 | 102 | 130.8 | 87.8 | 389.9 | 477.7 | 532.1 | 237.2 | 354.9 | 395.8 | 308.3 | 334.1 | 342.7 | 357.5 | 323 | 303.4 | 329.5
1761.1 | 1598.1 | -6.7 | 0 | 0 | 389.2 | 385.3 | 290.5 | 283.3 | 276.1 | 58.7 | 18.6 | 98.6 | 4.7 | 212.7 | 5.6 | 315.8 | 63 | 291.1 | 554.4 | 496.4 | 92.5 | 122.3 | 85.8 | 360.7 | 470.5 | 530.9 | 231.9 | 350 | 395.4 | 307.3 | 333.2 | 342.1 | 357.2 | 322.4 | 302.5 | 329.1
1762.1 | 1599.1 | -6.7 | 0 | 0 | 389.8 | 385.6 | 289.3 | 282.5 | 275 | 58.7 | 18.6 | 98.5 | 4.5 | 181.3 | 4.7 | 310.5 | 68.8 | 279.5 | 545 | 492.1 | 89 | 117.5 | 83.7 | 294.1 | 460.6 | 529.8 | 229.3 | 345.8 | 395 | 306.2 | 332.3 | 341.5 | 357 | 321.8 | 301.4 | 328.6
1763.1 | 1600.1 | -6.7 | 0 | 0 | 388.4 | 386.5 | 288 | 281.7 | 274.4 | 58.5 | 18.6 | 98.3 | 4.7 | 152.6 | 3.7 | 304.8 | 66.1 | 264.1 | 540.7 | 488.4 | 86.5 | 112.8 | 83.8 | 141.5 | 447.4 | 528.5 | 228.9 | 340.8 | 394.6 | 305.2 | 331.3 | 340.9 | 356.7 | 321.2 | 300.3 | 328
1764.1 | 1601.1 | -6.7 | 0 | 0 | 389.6 | 386.6 | 286.9 | 280.7 | 273.3 | 58.4 | 18.6 | 98.1 | 4.2 | 180.7 | 3.4 | 299.9 | 67.1 | 240.5 | 532.6 | 483.7 | 83.7 | 109.9 | 84.1 | 118.2 | 406.4 | 528.1 | 232.5 | 335.7 | 394.1 | 304.2 | 330.1 | 340.2 | 356.5 | 320.5 | 299.3 | 327.5
1765.1 | 1602.1 | -6.7 | 0 | 0 | 387.4 | 384.6 | 285.8 | 279.8 | 271.4 | 58.2 | 18.6 | 97.9 | 3.8 | 210.5 | 3.6 | 294.7 | 66.8 | 219.9 | 408.1 | 479.9 | 77 | 106.2 | 80.2 | 118.1 | 261.5 | 527.8 | 234.5 | 329.9 | 393.7 | 303.2 | 329.2 | 339.6 | 356.2 | 319.8 | 298.1 | 327
1766.1 | 1603.1 | -6.7 | 0 | 0 | 383.5 | 382.2 | 284.7 | 278.9 | 270.4 | 58 | 18.6 | 97.7 | 3.7 | 213.8 | 3.7 | 289.7 | 61.7 | 202.6 | 144.3 | 476.6 | 74 | 102.5 | 78 | 117.9 | 122.3 | 526.8 | 238.6 | 324.8 | 393.2 | 302.2 | 328.2 | 339 | 356 | 319.1 | 297.1 | 326.4
1767.1 | 1604.1 | -6.7 | 0 | 0 | 379.3 | 379.5 | 283.7 | 278.1 | 270 | 57.9 | 18.6 | 97.4 | 4.4 | 230.5 | 3.4 | 282.3 | 57.2 | 181 | 137.7 | 473.6 | 72.7 | 100.3 | 79.6 | 117.3 | 85.8 | 524.3 | 236.4 | 320.2 | 392.8 | 301 | 327.4 | 338.5 | 355.7 | 318.5 | 296.5 | 326
1768.1 | 1605.1 | -6.7 | 0 | 0 | 375.9 | 375 | 282.9 | 277.5 | 269.4 | 57.9 | 18.6 | 97.1 | 4.1 | 235.5 | 2.9 | 267 | 56.2 | 160 | 133.8 | 469.8 | 71.5 | 102.5 | 80.6 | 115.9 | 79.9 | 523.4 | 233.4 | 315.9 | 392.3 | 299.9 | 326.4 | 337.9 | 355.5 | 317.9 | 295.6 | 325.5
1769.1 | 1606.1 | -6.7 | 0 | 0 | 373.6 | 371.7 | 282.3 | 276.7 | 268.8 | 57.8 | 18.6 | 96.8 | 4.1 | 210.6 | 2.4 | 254.3 | 56.6 | 146.9 | 132.6 | 464.7 | 68.9 | 100.4 | 79.7 | 116 | 74.3 | 521.5 | 231.4 | 310.3 | 391.9 | 299 | 325.4 | 337.3 | 355.2 | 317 | 294.9 | 324.9
1770.1 | 1607.1 | -6.7 | 0 | 0 | 373 | 367.9 | 281.8 | 275.9 | 267.7 | 57.7 | 18.6 | 96.6 | 4.3 | 188.8 | 2.2 | 243 | 55.8 | 139.7 | 131.1 | 458.6 | 65.9 | 102.8 | 80.7 | 116 | 69.2 | 519.9 | 229.3 | 305.5 | 391.4 | 298.2 | 324.5 | 336.7 | 354.9 | 316.3 | 294.2 | 324.5
1771.1 | 1608.1 | -6.7 | 0 | 0 | 372.7 | 366.2 | 281.1 | 275.3 | 266.6 | 57.6 | 18.6 | 96.5 | 4.4 | 183.2 | 2.2 | 229.4 | 57.8 | 130.1 | 129.4 | 453.3 | 63.1 | 100.6 | 79.8 | 115.8 | 65.9 | 518.6 | 231.7 | 301.5 | 391 | 297.3 | 323.6 | 336.1 | 354.7 | 315.7 | 293.4 | 324
1772.1 | 1609.1 | -6.7 | 0 | 0 | 373.2 | 363.8 | 280.5 | 274.5 | 265.2 | 57.5 | 18.6 | 96.3 | 4.8 | 197.3 | 2 | 202.1 | 55.1 | 107.3 | 129 | 448.8 | 61.1 | 96.8 | 78.6 | 115.6 | 63.3 | 516.8 | 232.7 | 296.1 | 390.5 | 296.4 | 322.8 | 335.4 | 354.4 | 315.1 | 292.3 | 323.5
1773.1 | 1610.1 | -6.7 | 0 | 0 | 374.3 | 364.2 | 279.7 | 273.7 | 263.6 | 57.4 | 18.6 | 96 | 4.3 | 219.3 | 2 | 88.1 | 53.6 | 109.6 | 129.9 | 443.9 | 59.6 | 95.1 | 79.4 | 115.1 | 61 | 515.3 | 233.2 | 288.9 | 390 | 295.4 | 321.9 | 334.8 | 354.1 | 314.4 | 291.3 | 322.9
1774.1 | 1611.1 | -6.7 | 0 | 0 | 373.8 | 363 | 278.8 | 273 | 262.4 | 57.1 | 18.6 | 95.9 | 4.5 | 247.7 | 2.1 | 75.3 | 53.2 | 101.1 | 130 | 438.6 | 57.8 | 96.1 | 73.6 | 114.4 | 58.8 | 513.7 | 234.4 | 282.8 | 389.6 | 294.6 | 321 | 334.3 | 353.9 | 313.8 | 290.7 | 322.4
1775.1 | 1612.1 | -6.7 | 0 | 0 | 375.5 | 362.2 | 278.1 | 272.4 | 261.3 | 56.9 | 18.6 | 95.7 | 4.5 | 263.2 | 2.2 | 72.3 | 52.7 | 93 | 129.5 | 433.1 | 56.2 | 92.3 | 74.6 | 113.5 | 56.2 | 512.7 | 233.5 | 277.3 | 389.1 | 293.7 | 320.1 | 333.7 | 353.6 | 313.2 | 290.1 | 321.9
1776.1 | 1613.1 | -6.7 | 0 | 0 | 376.9 | 362.8 | 277.3 | 271.8 | 260.1 | 56.7 | 18.6 | 95.6 | 4.4 | 266 | 2.3 | 70.6 | 54.7 | 88.1 | 131.2 | 427.2 | 54.6 | 92.4 | 75.6 | 112.4 | 55.6 | 511.5 | 231.2 | 274.4 | 388.6 | 292.7 | 319.3 | 333.1 | 353.3 | 312.8 | 289.4 | 321.4
1777.1 | 1614.1 | -6.7 | 0 | 0 | 377.7 | 360.8 | 276.7 | 271.2 | 258.5 | 56.6 | 18.6 | 95.4 | 4.4 | 261 | 2.2 | 71.5 | 52.7 | 83.4 | 132.1 | 420.4 | 53.2 | 89.7 | 76.3 | 110.8 | 54.8 | 509.8 | 225.3 | 246.9 | 388.2 | 291.7 | 318.5 | 332.5 | 353.1 | 312.3 | 288.6 | 320.9
1778.1 | 1615.1 | -6.7 | 0 | 0 | 377.5 | 358.8 | 276.1 | 270.7 | 257 | 56.4 | 18.6 | 95.3 | 4.5 | 253 | 2.2 | 71.8 | 49.1 | 78.9 | 127.1 | 412.7 | 52.3 | 86.9 | 76.1 | 112.5 | 53.7 | 509.7 | 225.7 | 231.1 | 387.7 | 290.7 | 317.7 | 331.9 | 352.8 | 311.8 | 287.8 | 320.4
1779.1 | 1616.1 | -6.7 | 0 | 0 | 374.5 | 359.3 | 275.7 | 270 | 256.1 | 56.2 | 18.6 | 95.2 | 4.5 | 240.2 | 2.2 | 72.4 | 47.7 | 77.1 | 122.8 | 398.6 | 51.3 | 85.3 | 75.7 | 110.5 | 53.8 | 508.8 | 228.3 | 234.4 | 387.2 | 289.8 | 316.9 | 331.3 | 352.5 | 311.3 | 286.8 | 319.9
1780.1 | 1617.1 | -6.7 | 0 | 0 | 371 | 360.5 | 275.2 | 269.5 | 255.6 | 56.1 | 18.6 | 95 | 4.4 | 235.4 | 2 | 68.7 | 48.7 | 75.9 | 120.7 | 330.5 | 50.1 | 83.7 | 75.3 | 108.6 | 53.2 | 506.5 | 228.7 | 233.4 | 386.8 | 289 | 316 | 330.7 | 352.2 | 310.8 | 286 | 319.4
1781.1 | 1618.1 | -6.7 | 0 | 0 | 367.1 | 357.5 | 274.5 | 269 | 255 | 55.9 | 18.6 | 94.9 | 4.4 | 240.5 | 1.8 | 69.1 | 50.1 | 75.3 | 117.2 | 183 | 48.9 | 82.4 | 74.9 | 107.5 | 52.1 | 504.3 | 229.4 | 229.1 | 386.3 | 288.3 | 315.2 | 330.1 | 351.9 | 310.2 | 285.2 | 318.9
1782.1 | 1619.1 | -6.7 | 0 | 0 | 362.4 | 353.9 | 273.9 | 268.5 | 254.3 | 55.7 | 18.6 | 94.7 | 4.7 | 241.2 | 1.8 | 63.5 | 50.1 | 74.3 | 117.2 | 96.7 | 48.1 | 84 | 74.6 | 106.6 | 50.9 | 502.5 | 230.1 | 217.7 | 385.8 | 287.8 | 314.4 | 329.6 | 351.7 | 309.6 | 284.3 | 318.4
1783.1 | 1620.1 | -6.7 | 0 | 0 | 358 | 349.8 | 273.4 | 267.9 | 253.4 | 55.7 | 18.6 | 94.6 | 4.4 | 238.6 | 1.8 | 59.5 | 47.2 | 73.4 | 113.9 | 90.5 | 46.9 | 83.9 | 73.8 | 106.4 | 49.4 | 499.4 | 227.3 | 190.7 | 385.4 | 287.1 | 313.6 | 329 | 351.4 | 309 | 283.5 | 317.9
1784.1 | 1621.1 | -6.7 | 0 | 0 | 355.5 | 347.6 | 272.9 | 267.3 | 252.3 | 55.6 | 18.6 | 94.4 | 4.1 | 228.6 | 2.1 | 65.1 | 47.1 | 73.2 | 110.9 | 87.2 | 45.9 | 83.7 | 71.1 | 105.4 | 48.2 | 497.7 | 225.1 | 173.1 | 384.9 | 286.4 | 312.9 | 328.5 | 351.1 | 308.4 | 282.9 | 317.4
1785.1 | 1622.1 | -6.7 | 0 | 0 | 353.6 | 345.3 | 272.5 | 266.8 | 251.8 | 55.6 | 18.6 | 94.3 | 3.9 | 225.6 | 2.5 | 66.2 | 48.7 | 73.2 | 106.8 | 84.7 | 44.9 | 80.6 | 69.5 | 104.1 | 45.6 | 496.9 | 225.9 | 169.3 | 384.4 | 285.6 | 312.1 | 327.9 | 350.8 | 307.9 | 282.2 | 316.9
1786.1 | 1623.1 | -6.7 | 0 | 0 | 353.5 | 345.5 | 272 | 266.3 | 251.5 | 55.5 | 18.6 | 94.1 | 4.1 | 228.4 | 2.5 | 69.6 | 49.1 | 72.2 | 103.2 | 82 | 44.8 | 77.6 | 70.2 | 100.5 | 45 | 495.2 | 224.9 | 166.9 | 383.9 | 285 | 311.4 | 327.4 | 350.5 | 307.3 | 281.5 | 316.4
1787.1 | 1624.1 | -6.7 | 0 | 0 | 351.9 | 348.1 | 271.6 | 265.6 | 251 | 55.4 | 18.6 | 93.9 | 4.1 | 235.1 | 2.3 | 75.7 | 50.4 | 72.2 | 99.8 | 80.1 | 44.8 | 75.6 | 71.8 | 99.1 | 43.9 | 493.3 | 224.2 | 163.2 | 383.5 | 284.4 | 310.7 | 326.8 | 350.2 | 306.5 | 280.7 | 315.9
1788.1 | 1625.1 | -6.7 | 0 | 0 | 350.6 | 349 | 271.2 | 265 | 250.6 | 55.3 | 18.6 | 93.8 | 4.2 | 236.5 | 2.3 | 67.2 | 49.1 | 71.4 | 97.3 | 78.3 | 46.4 | 75.1 | 72.6 | 98.4 | 43.3 | 491.2 | 220.8 | 157.5 | 383 | 283.8 | 310.2 | 326.2 | 349.9 | 305.9 | 280.1 | 315.4
1789.1 | 1626.1 | -6.7 | 0 | 0 | 350.5 | 347.3 | 270.7 | 264.6 | 250.2 | 55.1 | 18.6 | 93.7 | 4.1 | 242.5 | 2.4 | 65.5 | 50 | 71.2 | 95 | 76.3 | 45.1 | 75.8 | 72.3 | 95.8 | 42.9 | 489.8 | 220.2 | 150.4 | 382.5 | 283.1 | 309.5 | 325.6 | 349.6 | 305.4 | 279.5 | 315
1790.1 | 1627.1 | -6.7 | 0 | 0 | 348.7 | 347.2 | 270 | 264.2 | 249.6 | 54.9 | 18.6 | 93.5 | 4.2 | 249.4 | 2.6 | 58.7 | 50.3 | 70.7 | 93.2 | 74.8 | 44.1 | 75.2 | 72.1 | 94.2 | 42.2 | 488 | 221.5 | 144.8 | 382 | 282.4 | 308.7 | 325.1 | 349.4 | 305 | 278.7 | 314.5
1791.1 | 1628.1 | -6.7 | 0 | 0 | 347.5 | 348.9 | 269.4 | 263.8 | 249.4 | 54.7 | 18.6 | 93.3 | 4.1 | 252.4 | 2.7 | 52.7 | 47.7 | 69.3 | 91.2 | 73 | 44 | 74.2 | 69.8 | 93 | 40.9 | 485.5 | 220.4 | 140 | 381.6 | 281.8 | 308 | 324.6 | 349.1 | 304.6 | 278.2 | 314
1792.1 | 1629.1 | -6.7 | 0 | 0 | 347 | 348 | 268.8 | 263.5 | 248.9 | 54.6 | 18.6 | 93.1 | 4.4 | 254.4 | 2.7 | 54.4 | 47.8 | 69 | 88.9 | 72.4 | 43.7 | 73.1 | 68.9 | 92.6 | 40.5 | 482.5 | 217.6 | 136.8 | 381.1 | 281.2 | 307.5 | 324.1 | 348.8 | 304.2 | 277.6 | 313.5
1793.1 | 1630.1 | -6.7 | 0 | 0 | 345.6 | 346 | 268.2 | 263.1 | 248 | 54.4 | 18.6 | 92.8 | 4.6 | 251.8 | 2.7 | 54.6 | 49.1 | 68.2 | 87.5 | 72.7 | 43.7 | 72.8 | 68.1 | 90.9 | 39.7 | 480.2 | 216.5 | 135.1 | 380.6 | 280.6 | 306.9 | 323.6 | 348.5 | 303.8 | 277 | 313
1794.1 | 1631.1 | -6.7 | 0 | 0 | 346.7 | 343.2 | 267.9 | 262.7 | 247 | 54.3 | 18.6 | 92.6 | 4.5 | 236.9 | 2.7 | 53.7 | 49.4 | 67.6 | 86.2 | 71.4 | 44.4 | 72.7 | 66.6 | 88.9 | 39.2 | 477.8 | 213.4 | 134.8 | 380.1 | 280 | 306 | 322.9 | 348.2 | 303.4 | 276.6 | 312.5
1795.1 | 1632.1 | -6.7 | 0 | 0 | 345 | 342.2 | 267.6 | 262.2 | 246.3 | 54.2 | 18.6 | 92.4 | 4.5 | 229.8 | 2.9 | 52.6 | 53.2 | 66.4 | 84.2 | 69.7 | 44.6 | 72.8 | 65.8 | 87.7 | 38.9 | 475.6 | 210.5 | 134.1 | 379.6 | 279.3 | 305.3 | 322.4 | 347.9 | 303 | 276.1 | 312.1
1796.1 | 1633.1 | -6.7 | 0 | 0 | 344.3 | 341 | 267.2 | 261.7 | 245.5 | 54.2 | 18.6 | 92.2 | 4.2 | 237 | 3.2 | 52.1 | 46.8 | 65.5 | 81.4 | 67.7 | 43.2 | 72 | 64.8 | 86.5 | 38.7 | 473.4 | 212.5 | 132 | 379.2 | 278.7 | 304.6 | 321.9 | 347.6 | 302.4 | 275.5 | 311.6
1797.1 | 1634.1 | -6.7 | 0 | 0 | 344.6 | 340.7 | 266.7 | 261.2 | 244.8 | 54.1 | 18.6 | 92 | 4.5 | 241.2 | 3.7 | 53.6 | 43 | 64.6 | 79.3 | 66 | 44.2 | 71.2 | 64.4 | 85.4 | 38.2 | 469.3 | 210.3 | 124.7 | 378.7 | 278.2 | 304 | 321.3 | 347.3 | 301.6 | 274.8 | 311.1
1798.1 | 1635.1 | -6.7 | 0 | 0 | 344.1 | 341.3 | 266.1 | 260.9 | 244.5 | 54 | 18.6 | 91.8 | 4.4 | 243.1 | 4.1 | 51.7 | 41.1 | 63.4 | 79.9 | 63.9 | 44.6 | 71.1 | 64.6 | 84.6 | 37.7 | 465.8 | 209.2 | 105.3 | 378.2 | 277.8 | 303.4 | 320.7 | 347 | 300.8 | 274.2 | 310.6
1799.1 | 1636.1 | -6.7 | 0 | 0 | 342.3 | 339.9 | 265.6 | 260.4 | 243.9 | 54 | 18.6 | 91.6 | 4.5 | 229 | 3.9 | 51.3 | 39.6 | 63.4 | 78.7 | 61.3 | 43.7 | 70.8 | 64.5 | 83.3 | 37 | 463.5 | 207.3 | 72.9 | 377.7 | 277.1 | 302.7 | 320.3 | 346.7 | 300.3 | 273.6 | 310.1
1800.1 | 1637.1 | -6.7 | 0 | 0 | 342.8 | 339.9 | 265 | 260 | 243.2 | 54 | 18.6 | 91.4 | 4.5 | 240 | 3.5 | 55 | 41.1 | 62.9 | 77.8 | 59.2 | 43.3 | 70.4 | 63.9 | 82.5 | 36 | 460.3 | 206.9 | 64.4 | 377.3 | 276.3 | 302.1 | 319.7 | 346.4 | 300 | 273.3 | 309.7
1801.1 | 1638.1 | -6.7 | 0 | 0 | 343.7 | 338.4 | 264.4 | 259.5 | 242.6 | 54 | 18.6 | 91.2 | 4.2 | 252.6 | 3.8 | 53.6 | 43.2 | 62.5 | 77.3 | 58.2 | 42.1 | 70 | 63.5 | 81.2 | 35.4 | 457.5 | 206.2 | 61.2 | 376.8 | 275.7 | 301.5 | 319.1 | 346.1 | 299.7 | 272.7 | 309.3
1802.1 | 1639.1 | -6.7 | 0 | 0 | 345.4 | 336.6 | 263.8 | 259.1 | 242.4 | 54 | 18.6 | 91 | 4.5 | 237.3 | 3.8 | 52.3 | 42.7 | 62 | 76.2 | 56.6 | 41 | 69.5 | 63.4 | 80 | 35.2 | 455.6 | 206 | 58.8 | 376.3 | 275 | 300.6 | 318.6 | 345.8 | 299.4 | 272.1 | 308.8
1803.1 | 1640.1 | -6.7 | 0 | 0 | 345.7 | 335.4 | 263.2 | 258.6 | 242.1 | 54.1 | 18.6 | 90.8 | 4.4 | 222.5 | 3.7 | 50.9 | 41.6 | 61.9 | 75.6 | 55 | 39.9 | 69.1 | 63.1 | 79 | 35.4 | 452.7 | 207.5 | 57.5 | 375.8 | 274.4 | 300.1 | 318.1 | 345.5 | 298.9 | 271.5 | 308.3
1804.1 | 1641.1 | -6.7 | 0 | 0 | 345.2 | 332.5 | 262.6 | 258.1 | 242.2 | 54 | 18.6 | 90.7 | 4.2 | 223.7 | 3.2 | 51.3 | 41 | 62 | 75 | 53.8 | 38.9 | 69.3 | 62.7 | 77.8 | 34.6 | 449.8 | 205.5 | 56.5 | 375.3 | 273.9 | 299.6 | 317.5 | 345.2 | 298.3 | 271.1 | 307.8
1805.1 | 1642.1 | -6.7 | 0 | 0 | 344.1 | 330.7 | 262.1 | 257.6 | 241.5 | 53.9 | 18.6 | 90.6 | 3.9 | 229 | 3.3 | 52.7 | 40.7 | 61.5 | 74.6 | 52.7 | 38 | 68.9 | 61.8 | 76.2 | 34.5 | 446.4 | 201 | 55 | 374.8 | 273.2 | 299.1 | 316.9 | 344.9 | 297.9 | 270.6 | 307.4
1806.1 | 1643.1 | -6.7 | 0 | 0 | 342.4 | 329.8 | 261.7 | 257.1 | 240.5 | 53.9 | 18.6 | 90.5 | 4 | 238.9 | 3.5 | 52.5 | 41.5 | 61.4 | 74 | 52.7 | 37.8 | 68.1 | 61.2 | 75 | 34.5 | 443.1 | 199.9 | 53.2 | 374.4 | 272.6 | 298.5 | 316.4 | 344.6 | 297.3 | 270.1 | 306.9
1807.1 | 1644.1 | -6.7 | 0 | 0 | 341 | 329.1 | 261.3 | 256.6 | 239.8 | 53.8 | 18.6 | 90.4 | 3.9 | 252 | 3.4 | 53.4 | 39.5 | 60.8 | 73.5 | 52.3 | 37.6 | 67.8 | 60.5 | 74.1 | 33.9 | 440.4 | 199.2 | 52 | 373.9 | 272 | 297.9 | 315.8 | 344.3 | 296.9 | 269.6 | 306.4
1808.1 | 1645.1 | -6.7 | 0 | 0 | 340.3 | 328.7 | 260.7 | 256 | 238.4 | 53.7 | 18.6 | 90.2 | 3.8 | 249.5 | 3.5 | 51 | 41.5 | 60.5 | 72.2 | 50.8 | 37.1 | 67.4 | 59.6 | 73.6 | 33 | 437.7 | 198.5 | 50.8 | 373.4 | 271.4 | 297.3 | 315.3 | 344 | 296.4 | 269.1 | 306
1809.1 | 1646.1 | -6.7 | 0 | 0 | 338.3 | 329.2 | 260.1 | 255.5 | 237.3 | 53.6 | 18.6 | 90.1 | 4 | 236.9 | 4 | 49.7 | 41.8 | 59 | 71.6 | 49.5 | 36.6 | 67.6 | 59.5 | 72.9 | 33.2 | 435.2 | 196.8 | 49.9 | 372.9 | 270.7 | 296.8 | 314.7 | 343.7 | 295.7 | 268.6 | 305.5
1810.1 | 1647.1 | -6.7 | 0 | 0 | 336.6 | 328.9 | 259.5 | 255.1 | 236.8 | 53.4 | 18.6 | 89.9 | 4 | 243.5 | 4 | 48.8 | 41.9 | 58.7 | 71 | 48.3 | 36.2 | 67.6 | 59.5 | 72.2 | 32.4 | 433.7 | 197.9 | 50.3 | 372.4 | 270.1 | 296.3 | 314.2 | 343.4 | 295.3 | 268.3 | 305.1
1811.1 | 1648.1 | -6.7 | 0 | 0 | 335.9 | 328.9 | 259 | 254.7 | 236.2 | 53.3 | 18.7 | 89.8 | 4 | 238.3 | 4 | 49.5 | 40.2 | 58.8 | 70.3 | 47.1 | 36.1 | 67.6 | 58.1 | 71.4 | 32.8 | 431.4 | 198.9 | 50.3 | 372 | 269.6 | 295.8 | 313.7 | 343.1 | 294.8 | 267.8 | 304.6
1812.1 | 1649.1 | -6.7 | 0 | 0 | 335.2 | 328.2 | 258.4 | 254.3 | 235.2 | 53.1 | 18.7 | 89.7 | 4 | 231.3 | 4.4 | 49.3 | 40.2 | 58 | 68.9 | 46.1 | 36.1 | 67.8 | 57.1 | 70.8 | 32.7 | 430.3 | 199.1 | 50 | 371.5 | 268.9 | 295.2 | 313.1 | 342.8 | 294.4 | 267.3 | 304.2
1813.1 | 1650.1 | -6.7 | 0 | 0 | 332.4 | 326.8 | 257.7 | 253.8 | 233.9 | 52.9 | 18.7 | 89.5 | 4.2 | 238.1 | 4.5 | 48.7 | 39.9 | 57.8 | 67.9 | 45.7 | 36 | 66.3 | 56.8 | 70.3 | 32.7 | 427.5 | 200.6 | 49.8 | 371 | 268.2 | 294.6 | 312.6 | 342.5 | 294 | 266.7 | 303.7
1814.1 | 1651.1 | -6.7 | 0 | 0 | 330.3 | 325 | 256.9 | 253.4 | 233 | 52.8 | 18.7 | 89.4 | 4 | 239.9 | 4.5 | 50.9 | 38.8 | 58.9 | 67.1 | 44.6 | 35.6 | 64.9 | 56.3 | 69.9 | 32.1 | 424.8 | 201.3 | 49.8 | 370.5 | 267.5 | 294 | 312 | 342.2 | 293.6 | 266.2 | 303.3
1815.1 | 1652.1 | -6.7 | 0 | 0 | 328.8 | 323.7 | 256.4 | 253 | 232 | 52.7 | 18.7 | 89.3 | 3.9 | 242.6 | 4.7 | 53.2 | 38.1 | 58.1 | 66.7 | 43.9 | 35.6 | 65.1 | 56.1 | 69.5 | 31.6 | 422.1 | 202.1 | 49.7 | 370 | 266.9 | 293.4 | 311.5 | 341.9 | 293.2 | 265.7 | 302.8
1816.1 | 1653.1 | -6.7 | 0 | 0 | 328.3 | 322.1 | 255.9 | 252.4 | 230.9 | 52.7 | 18.7 | 89.1 | 3.8 | 239.9 | 4.9 | 51.9 | 40.5 | 57.2 | 65.3 | 43.1 | 35.7 | 62.7 | 55.3 | 69.2 | 31.8 | 419.6 | 203.1 | 52 | 369.6 | 266.4 | 292.9 | 310.9 | 341.6 | 292.9 | 265.3 | 302.4
1817.1 | 1654.1 | -6.7 | 0 | 0 | 328.1 | 320.3 | 255.4 | 252.1 | 229.9 | 52.6 | 18.7 | 89 | 4.1 | 252.8 | 4.7 | 49.7 | 40 | 56.5 | 64.5 | 42.7 | 35.8 | 63 | 55 | 68.7 | 32.3 | 417 | 202.1 | 53.7 | 369.1 | 265.9 | 292.4 | 310.4 | 341.3 | 292.5 | 264.8 | 301.9
1818.1 | 1655.1 | -6.7 | 0 | 0 | 329.6 | 318.7 | 254.8 | 251.6 | 229.2 | 52.5 | 18.7 | 88.9 | 3.8 | 256.4 | 4.5 | 49.2 | 39.1 | 56.5 | 64.1 | 42.1 | 35.6 | 63.9 | 54.6 | 68.2 | 32.5 | 415 | 203.2 | 55.2 | 368.6 | 265.3 | 291.9 | 309.9 | 341 | 292.2 | 264.3 | 301.5
1819.1 | 1656.1 | -6.7 | 0 | 0 | 333.8 | 317.5 | 254.1 | 251.2 | 228.6 | 52.5 | 18.7 | 88.7 | 3.6 | 242.8 | 4.8 | 49.9 | 37.8 | 56.2 | 63.1 | 41.4 | 36.2 | 64.4 | 53.5 | 67.5 | 32.4 | 413 | 203.2 | 55.4 | 368.1 | 264.7 | 291.3 | 309.4 | 340.7 | 291.8 | 263.8 | 301
1820.1 | 1657.1 | -6.7 | 0 | 0 | 334.9 | 316.5 | 253.7 | 250.7 | 228.2 | 52.5 | 18.7 | 88.6 | 3.8 | 238.2 | 4.9 | 49 | 37.4 | 55 | 61.9 | 40.9 | 35.9 | 64.4 | 53.7 | 67.1 | 32.1 | 410.8 | 203.3 | 55.7 | 367.7 | 264.1 | 290.6 | 308.8 | 340.4 | 291.3 | 263.3 | 300.6
1821.1 | 1658.1 | -6.7 | 0 | 0 | 334.7 | 316.4 | 253.2 | 250.3 | 228.2 | 52.3 | 18.7 | 88.5 | 3.8 | 239.7 | 5.1 | 48.4 | 37.9 | 55.6 | 61.3 | 40.6 | 37.1 | 64.4 | 53.8 | 66.8 | 31.7 | 408 | 202.3 | 56 | 367.2 | 263.5 | 290 | 308.2 | 340.1 | 291 | 262.9 | 300.1
1822.1 | 1659.1 | -6.7 | 0 | 0 | 335.5 | 315.5 | 252.9 | 249.8 | 228.4 | 52.1 | 18.7 | 88.3 | 3.9 | 242.1 | 5.4 | 48.1 | 38.2 | 54.3 | 60.2 | 40.1 | 38.4 | 64.4 | 53.7 | 65.7 | 31.5 | 405.1 | 203.1 | 56.3 | 366.7 | 263 | 289.4 | 307.7 | 339.8 | 290.7 | 262.4 | 299.7
1823.1 | 1660.1 | -6.7 | 0 | 0 | 337.1 | 314.4 | 252.6 | 249.4 | 228.4 | 52.1 | 18.7 | 88.2 | 3.7 | 249 | 5.1 | 49.4 | 36.3 | 53.3 | 60.1 | 39.8 | 37.1 | 64.8 | 53.8 | 65.6 | 31.3 | 401.3 | 202.8 | 56.2 | 366.2 | 262.4 | 288.9 | 307.1 | 339.5 | 290.2 | 262.1 | 299.3
1824.1 | 1661.1 | -6.7 | 0 | 0 | 337.9 | 314.5 | 252.1 | 249 | 228.1 | 52.1 | 18.7 | 88.1 | 3.7 | 253.4 | 4.8 | 48.4 | 36 | 53.3 | 59.6 | 39.5 | 35.8 | 65 | 53.1 | 65.5 | 31.1 | 397.8 | 201 | 55.5 | 365.8 | 261.8 | 288.3 | 306.6 | 339.2 | 289.7 | 261.8 | 298.8
1825.1 | 1662.1 | -6.7 | 0 | 0 | 337.1 | 314.7 | 251.6 | 248.6 | 228.2 | 52.1 | 18.7 | 87.9 | 3.6 | 248.8 | 4.6 | 49.2 | 36.1 | 52.9 | 59.2 | 39.3 | 34.7 | 64.8 | 53.3 | 65.2 | 30.9 | 394.8 | 201.2 | 55 | 365.3 | 261.4 | 287.7 | 306.1 | 338.8 | 289.4 | 261.4 | 298.5
1826.1 | 1663.1 | -6.7 | 0 | 0 | 335.9 | 314.7 | 251 | 248.2 | 228.3 | 52.1 | 18.7 | 87.7 | 3.6 | 239.5 | 4.6 | 48.5 | 36.9 | 52.4 | 59 | 39.2 | 34.3 | 64.7 | 53.4 | 64.7 | 30.8 | 392.2 | 203 | 54.4 | 364.8 | 260.9 | 287.2 | 305.6 | 338.5 | 289 | 260.8 | 298
1827.1 | 1664.1 | -6.7 | 0 | 0 | 334.1 | 314.8 | 250.6 | 247.8 | 228.1 | 52 | 18.7 | 87.6 | 3.4 | 233.4 | 4.4 | 46.9 | 35.5 | 51 | 58.4 | 39.1 | 34 | 64.4 | 52.8 | 64.2 | 30.9 | 389.6 | 206.4 | 53.7 | 364.3 | 260.4 | 286.7 | 305.2 | 338.2 | 288.4 | 260.3 | 297.5
1828.1 | 1665.1 | -6.7 | 0 | 0 | 331.6 | 315.1 | 250.1 | 247.5 | 227.9 | 52 | 18.7 | 87.4 | 3.6 | 241.6 | 4.4 | 45.4 | 35.2 | 50.9 | 58 | 39 | 33.5 | 63.4 | 50.5 | 63.8 | 30.5 | 386.6 | 206.4 | 53.3 | 363.9 | 260.1 | 286 | 304.7 | 337.9 | 287.9 | 259.8 | 297.1
1829.1 | 1666.1 | -6.7 | 0 | 0 | 331.2 | 314 | 249.6 | 247.1 | 227.9 | 51.9 | 18.7 | 87.3 | 3.5 | 245.5 | 4.2 | 45.5 | 35.5 | 51.1 | 57.2 | 38.7 | 33.8 | 58.1 | 50.7 | 63.6 | 30.2 | 383.6 | 208.3 | 52.8 | 363.4 | 259.6 | 285.6 | 304.2 | 337.6 | 287.6 | 259.3 | 296.7
1830.1 | 1667.1 | -6.7 | 0 | 0 | 332.4 | 312.6 | 249.2 | 246.7 | 227.8 | 51.8 | 18.7 | 87.1 | 3.6 | 244.8 | 4.1 | 44.7 | 36.5 | 51.1 | 56.7 | 38.5 | 35.6 | 59.1 | 51.2 | 63 | 30.2 | 380.2 | 209.6 | 52.2 | 362.9 | 259.1 | 285.1 | 303.7 | 337.3 | 287.2 | 258.8 | 296.2
1831.1 | 1668.1 | -6.7 | 0 | 0 | 332.5 | 312.1 | 248.8 | 246.4 | 227.6 | 51.7 | 18.7 | 86.9 | 3.5 | 244.3 | 3.8 | 44.2 | 35.6 | 50.3 | 55.9 | 38.1 | 36 | 60.1 | 51.6 | 62.4 | 29.9 | 376.6 | 209.7 | 51.4 | 362.4 | 258.5 | 284.7 | 303.2 | 337 | 286.9 | 258.5 | 295.8
1832.1 | 1669.1 | -6.7 | 0 | 0 | 332.3 | 312.1 | 248.3 | 246 | 227.3 | 51.6 | 18.7 | 86.7 | 3.7 | 245 | 4 | 43.5 | 34.8 | 49.1 | 54.8 | 37.4 | 36 | 60.4 | 51 | 61.9 | 29.6 | 374 | 210.4 | 50.7 | 362 | 258 | 284.1 | 302.7 | 336.7 | 286.6 | 258 | 295.3
1833.1 | 1670.1 | -6.7 | 0 | 0 | 330.6 | 311.5 | 247.9 | 245.6 | 227.2 | 51.5 | 18.7 | 86.5 | 3.4 | 251.6 | 4.5 | 42.3 | 35.4 | 47.8 | 54.5 | 37.3 | 36.1 | 61.6 | 51 | 61.4 | 29.4 | 371.6 | 215.3 | 50.4 | 361.5 | 257.6 | 283.7 | 302.2 | 336.4 | 286.2 | 257.6 | 294.9
1834.1 | 1671.1 | -6.7 | 0 | 0 | 328.3 | 311.4 | 247.5 | 245.1 | 227.1 | 51.4 | 18.7 | 86.4 | 3.5 | 247.8 | 4.8 | 41.6 | 36.3 | 47.2 | 54.6 | 37.1 | 36.4 | 62.2 | 51.4 | 60.9 | 29.4 | 369.1 | 217 | 50 | 361 | 257.1 | 283.3 | 301.7 | 336.1 | 285.8 | 257.3 | 294.5
1835.1 | 1672.1 | -6.7 | 0 | 0 | 326.9 | 312 | 247.2 | 244.8 | 226.8 | 51.3 | 18.7 | 86.2 | 3.4 | 238.8 | 5.1 | 41.9 | 34.8 | 46.9 | 54 | 37.7 | 36.5 | 62.3 | 51.1 | 60.6 | 29.6 | 366.2 | 219 | 49.6 | 360.6 | 256.7 | 282.6 | 301.2 | 335.8 | 285.2 | 256.9 | 294.1
1836.1 | 1673.1 | -6.7 | 0 | 0 | 326 | 312.1 | 246.9 | 244.4 | 226.2 | 51.1 | 18.7 | 86.1 | 3.6 | 233.7 | 4.9 | 42.8 | 35.4 | 46.4 | 53.7 | 37.4 | 36.6 | 62.1 | 48.2 | 60.3 | 29.6 | 362.7 | 219.7 | 48.3 | 360.1 | 256.3 | 282.1 | 300.7 | 335.5 | 284.6 | 256.6 | 293.7
1837.1 | 1674.1 | -6.7 | 0 | 0 | 324.1 | 312.6 | 246.4 | 244.1 | 226.1 | 51 | 18.7 | 85.9 | 3.7 | 197 | 4.2 | 42.2 | 34.5 | 46.2 | 53.2 | 37.1 | 36.3 | 62.1 | 46.2 | 59.9 | 29.5 | 359.3 | 219.1 | 47.7 | 359.6 | 255.9 | 281.7 | 300.2 | 335.2 | 284.3 | 256.1 | 293.2
1838.1 | 1675.1 | -6.7 | 0 | 0 | 323 | 313.4 | 245.9 | 243.7 | 226.3 | 50.8 | 18.7 | 85.8 | 3.8 | 182.2 | 3.6 | 42.2 | 34.6 | 45.5 | 52.8 | 36.8 | 35.5 | 62.1 | 46.4 | 59.6 | 29.2 | 356 | 219.3 | 46.8 | 359.1 | 255.5 | 281.3 | 299.8 | 334.9 | 284 | 255.8 | 292.8
1839.1 | 1676.1 | -6.7 | 0 | 0 | 320.8 | 314.4 | 245.6 | 243.3 | 226.3 | 50.6 | 18.7 | 85.7 | 4 | 195.6 | 3.1 | 43.9 | 34.2 | 45.8 | 52.5 | 36.5 | 35.1 | 61.5 | 47.7 | 59.3 | 29 | 353 | 221.6 | 45.9 | 358.7 | 255.1 | 280.9 | 299.3 | 334.6 | 283.5 | 255.4 | 292.4
1840.1 | 1677.1 | -6.7 | 0 | 0 | 320.4 | 315.1 | 245.2 | 243.1 | 226.2 | 50.4 | 18.7 | 85.6 | 3.8 | 222.7 | 2.8 | 43.7 | 34.2 | 45.5 | 52.2 | 36.2 | 35.2 | 61.6 | 48.6 | 59.1 | 28.5 | 350.3 | 222.2 | 45.1 | 358.2 | 254.7 | 280.3 | 298.8 | 334.3 | 282.8 | 255 | 291.9
1841.1 | 1678.1 | -6.7 | 0 | 0 | 321.5 | 314.8 | 244.7 | 242.7 | 226.3 | 50.2 | 18.7 | 85.5 | 3.4 | 228.3 | 2.7 | 43.8 | 33.1 | 44.4 | 52.1 | 36.2 | 35.2 | 61.6 | 48.5 | 58.9 | 28.1 | 348.2 | 222.7 | 44.3 | 357.8 | 254.1 | 279.8 | 298.3 | 334 | 282.4 | 254.7 | 291.5
1842.1 | 1679.1 | -6.7 | 0 | 0 | 320.5 | 314.2 | 244.3 | 242.4 | 226.5 | 50.1 | 18.7 | 85.4 | 3.5 | 186.6 | 3.3 | 43.9 | 32.8 | 43.7 | 51.8 | 36.3 | 35.3 | 61.5 | 47 | 58.5 | 27.6 | 346.2 | 222.5 | 43.7 | 357.3 | 253.7 | 279.4 | 297.9 | 333.7 | 282.1 | 254.5 | 291.1
1843.1 | 1680.1 | -6.7 | 0 | 0 | 319.8 | 313.3 | 243.8 | 242.1 | 226.4 | 50 | 18.7 | 85.2 | 3.5 | 185 | 4.5 | 42.2 | 32.9 | 43.2 | 51.7 | 35.9 | 35.1 | 61.5 | 47.2 | 58.2 | 27.6 | 344.5 | 218.2 | 43.7 | 356.8 | 253.3 | 278.9 | 297.4 | 333.4 | 281.7 | 254.1 | 290.6
1844.1 | 1681.1 | -6.7 | 0 | 0 | 319.8 | 312.7 | 243.4 | 241.8 | 226 | 49.9 | 18.7 | 85.1 | 3.7 | 194.7 | 5.2 | 41.3 | 32.2 | 42.9 | 51.6 | 35.7 | 35.1 | 61.4 | 48.3 | 57.9 | 27.9 | 342.5 | 218.7 | 43.3 | 356.4 | 252.9 | 278.3 | 297 | 333.1 | 281.1 | 253.8 | 290.2
1845.1 | 1682.1 | -6.7 | 0 | 0 | 320.5 | 312.1 | 243 | 241.5 | 225.4 | 50 | 18.7 | 84.9 | 3.7 | 189.1 | 6 | 40.1 | 32.7 | 42.6 | 51.4 | 35.5 | 35.4 | 61.3 | 47.9 | 57.8 | 27.7 | 340.3 | 219 | 43 | 355.9 | 252.5 | 277.8 | 296.5 | 332.8 | 280.6 | 253.5 | 289.8
1846.1 | 1683.1 | -6.7 | 0 | 0 | 318.4 | 311.1 | 242.6 | 241.1 | 224.6 | 49.9 | 18.7 | 84.8 | 3.6 | 211 | 6.8 | 39 | 32.8 | 42.1 | 50.9 | 35.1 | 35.4 | 61.4 | 44.8 | 57.6 | 27.7 | 338.5 | 220.4 | 42.6 | 355.5 | 252 | 277.5 | 296 | 332.5 | 280.1 | 253.2 | 289.4
1847.1 | 1684.1 | -6.7 | 0 | 0 | 316.4 | 312.7 | 242.1 | 240.7 | 224 | 49.8 | 18.7 | 84.7 | 3.6 | 205.7 | 7.1 | 39.5 | 31.7 | 41.8 | 50.5 | 34.6 | 35.2 | 61.2 | 44.1 | 57.4 | 27.7 | 335.4 | 222.7 | 42.1 | 355 | 251.5 | 277.2 | 295.5 | 332.2 | 279.9 | 252.8 | 289
1848.1 | 1685.1 | -6.7 | 0 | 0 | 313.5 | 313.8 | 241.8 | 240.4 | 223.7 | 49.9 | 18.7 | 84.6 | 3.5 | 194.5 | 7.2 | 40.2 | 32.4 | 41.9 | 50.4 | 34.4 | 35.3 | 61.4 | 44.4 | 57.2 | 27.6 | 330.9 | 221.4 | 41.8 | 354.5 | 251 | 276.8 | 295 | 331.9 | 279.5 | 252.4 | 288.6
1849.1 | 1686.1 | -6.7 | 0 | 0 | 311.8 | 314.2 | 241.5 | 240.1 | 223.3 | 50 | 18.7 | 84.5 | 3.7 | 213.9 | 7.6 | 41.1 | 32.2 | 41.8 | 50 | 34.1 | 35.5 | 61.2 | 45.2 | 57.1 | 27.6 | 328.5 | 220.1 | 41.4 | 354.1 | 250.5 | 276.5 | 294.6 | 331.6 | 278.9 | 251.9 | 288.2
1850.1 | 1687.1 | -6.7 | 0 | 0 | 311.6 | 314.9 | 241.3 | 239.7 | 222.8 | 50.1 | 18.7 | 84.4 | 3.3 | 197 | 6.2 | 41.1 | 32.6 | 41.8 | 49.2 | 33.9 | 35.6 | 60.9 | 45.5 | 56.9 | 28.1 | 326.1 | 218.7 | 41.1 | 353.6 | 250 | 276 | 294.1 | 331.3 | 278.5 | 251.3 | 287.8
1851.1 | 1688.1 | -6.7 | 0 | 0 | 310.2 | 315.2 | 240.9 | 239.3 | 222.5 | 50.1 | 18.7 | 84.2 | 3.4 | 246.4 | 4.4 | 40.8 | 33.6 | 41.7 | 48.4 | 33.8 | 35.7 | 60.9 | 45.6 | 56.6 | 27.5 | 323.9 | 219.3 | 40.8 | 353.2 | 249.5 | 275.7 | 293.7 | 331 | 278.1 | 250.9 | 287.3
1852.1 | 1689.1 | -6.7 | 0 | 0 | 308.9 | 314.1 | 240.5 | 238.8 | 222.2 | 50.1 | 18.7 | 84.1 | 3.5 | 288 | 3.4 | 41.5 | 32.4 | 41.8 | 48.3 | 33.6 | 36.2 | 60.7 | 46.4 | 56.4 | 27.2 | 321.5 | 221.6 | 40.8 | 352.7 | 249.1 | 275.2 | 293.2 | 330.7 | 277.8 | 250.6 | 286.9
1853.1 | 1690.1 | -6.7 | 0 | 0 | 308.4 | 312.6 | 240.3 | 238.3 | 222.1 | 50 | 18.7 | 84 | 3.1 | 264.3 | 2.5 | 40.5 | 32.7 | 41.7 | 48.2 | 33.4 | 36.6 | 60.7 | 47.2 | 56.3 | 27.2 | 319.3 | 226.4 | 40.9 | 352.2 | 248.6 | 274.8 | 292.8 | 330.4 | 277.5 | 250.3 | 286.5
1854.1 | 1691.1 | -6.7 | 0 | 0 | 306.6 | 313.9 | 239.9 | 237.9 | 222 | 49.8 | 18.7 | 83.9 | 3.1 | 202.9 | 2.6 | 39.7 | 31.8 | 41.5 | 48 | 33.2 | 36.4 | 60.2 | 44 | 55.9 | 27.4 | 316.9 | 225 | 41 | 351.8 | 248.2 | 274.5 | 292.4 | 330.1 | 277.2 | 250 | 286.1
1855.1 | 1692.1 | -6.7 | 0 | 0 | 303.7 | 316.9 | 239.6 | 237.5 | 221.8 | 49.7 | 18.7 | 83.8 | 3.3 | 197 | 3.1 | 39.1 | 31.5 | 41.4 | 47.8 | 32.9 | 36 | 60.3 | 43.7 | 55.7 | 27.3 | 315 | 226.1 | 40.8 | 351.3 | 247.8 | 274.2 | 291.9 | 329.8 | 276.8 | 249.6 | 285.7
1856.1 | 1693.1 | -6.7 | 0 | 0 | 301.5 | 316.1 | 239.3 | 237.1 | 221.4 | 49.5 | 18.7 | 83.7 | 3.1 | 215.4 | 3.5 | 38.7 | 32.4 | 41.3 | 47.7 | 32.7 | 35.6 | 60.5 | 44.9 | 55.4 | 26.9 | 312.5 | 226 | 40.7 | 350.9 | 247.4 | 273.8 | 291.4 | 329.5 | 276.4 | 249 | 285.2
1857.1 | 1694.1 | -6.7 | 0 | 0 | 298.7 | 317 | 238.9 | 236.7 | 221 | 49.5 | 18.7 | 83.7 | 3.3 | 202.3 | 3.7 | 38.4 | 32.8 | 41 | 47.6 | 32.9 | 35.4 | 60.2 | 45.7 | 55.3 | 26.8 | 309.9 | 228.7 | 40.8 | 350.4 | 247 | 273.4 | 291 | 329.1 | 276 | 248.6 | 284.9
1858.1 | 1695.1 | -6.7 | 0 | 0 | 297 | 316.5 | 238.3 | 236.4 | 220.3 | 49.5 | 18.7 | 83.5 | 3.4 | 181 | 4 | 38.6 | 33.9 | 40.6 | 47.4 | 32.8 | 35.5 | 59.8 | 46 | 55.1 | 26.8 | 305.4 | 227.5 | 40.6 | 350 | 246.6 | 272.9 | 290.6 | 328.8 | 275.8 | 248.2 | 284.5
1859.1 | 1696.1 | -6.7 | 0 | 0 | 296.7 | 316.7 | 237.8 | 236.1 | 219.2 | 49.3 | 18.8 | 83.4 | 3.2 | 182.6 | 4.6 | 38.3 | 33.8 | 40.3 | 47.2 | 32.2 | 35 | 59.8 | 46.3 | 54.8 | 27 | 301 | 225.4 | 41 | 349.5 | 246.2 | 272.6 | 290.1 | 328.5 | 275.5 | 247.8 | 284.1
1860.1 | 1697.1 | -6.7 | 0 | 0 | 296.3 | 316.6 | 237.3 | 235.7 | 218.4 | 49.2 | 18.8 | 83.3 | 3.1 | 212.4 | 5.3 | 37.9 | 33.1 | 40.2 | 46.9 | 31.9 | 34.9 | 59.7 | 46.1 | 54.6 | 27.1 | 297.4 | 223.9 | 41.3 | 349.1 | 245.9 | 272.2 | 289.7 | 328.2 | 275.2 | 247.4 | 283.6
1861.1 | 1698.1 | -6.7 | 0 | 0 | 296.9 | 315.4 | 236.9 | 235.5 | 217.3 | 49.2 | 18.8 | 83.2 | 3 | 214 | 5.8 | 38.2 | 32.9 | 39.8 | 46.7 | 31.8 | 34.9 | 56.1 | 46.2 | 54.3 | 26.8 | 294.8 | 225.9 | 40.8 | 348.6 | 245.5 | 271.8 | 289.2 | 327.9 | 274.8 | 247 | 283.3
1862.1 | 1699.1 | -6.7 | 0 | 0 | 295.2 | 313.7 | 236.6 | 235.2 | 216.7 | 49.2 | 18.8 | 83.1 | 3.3 | 203.2 | 5.5 | 38.7 | 32.7 | 39.5 | 46.3 | 31.7 | 35.1 | 53.8 | 46.8 | 54.2 | 26.8 | 292.7 | 225.5 | 40.6 | 348.2 | 245.1 | 271.5 | 288.7 | 327.6 | 274.3 | 246.6 | 282.9
1863.1 | 1700.1 | -6.7 | 0 | 0 | 294.3 | 312.4 | 236.4 | 234.8 | 216.1 | 49.1 | 18.8 | 83 | 3.4 | 201.9 | 5.3 | 38.8 | 33.1 | 39 | 46 | 31.7 | 34.9 | 53.6 | 47.4 | 53.9 | 26.7 | 290.5 | 225.9 | 40.6 | 347.7 | 244.8 | 271.2 | 288.3 | 327.3 | 273.9 | 246.2 | 282.5
1864.1 | 1701.1 | -6.7 | 0 | 0 | 294.1 | 311.4 | 236.1 | 234.5 | 215.6 | 48.9 | 18.8 | 82.9 | 3.3 | 199.3 | 4.9 | 38.5 | 34 | 38.5 | 45.8 | 31.6 | 35.1 | 54.8 | 47.2 | 53.7 | 26.9 | 288.7 | 224.1 | 40.4 | 347.3 | 244.4 | 270.8 | 287.8 | 327 | 273.5 | 245.8 | 282.2
1865.1 | 1702.1 | -6.7 | 0 | 0 | 294.7 | 309.5 | 235.7 | 234.1 | 215.3 | 48.9 | 18.8 | 82.8 | 3.2 | 200.5 | 4.6 | 38.2 | 33.5 | 38.6 | 45.6 | 31.6 | 35.1 | 55.3 | 47.3 | 53.6 | 26.9 | 286.6 | 222.2 | 40.3 | 346.8 | 244.1 | 270.5 | 287.4 | 326.7 | 273.3 | 245.5 | 281.8
1866.1 | 1703.1 | -6.7 | 0 | 0 | 294.6 | 306.4 | 235.4 | 233.8 | 215 | 48.8 | 18.8 | 82.7 | 3 | 181.9 | 4.5 | 37.8 | 32.8 | 38.4 | 45.3 | 31.6 | 35.1 | 55.5 | 47.2 | 53.3 | 26.9 | 284.7 | 221.4 | 40.2 | 346.4 | 243.7 | 270.2 | 286.9 | 326.4 | 272.8 | 245 | 281.4
1867.1 | 1704.1 | -6.7 | 0 | 0 | 294.4 | 304 | 235.2 | 233.6 | 214.6 | 48.7 | 18.8 | 82.6 | 3 | 175.6 | 4.1 | 37.8 | 32 | 38.3 | 45.1 | 31.6 | 35.1 | 56.2 | 46.8 | 53 | 26.8 | 283.1 | 220.1 | 39.8 | 346 | 243.4 | 269.6 | 286.5 | 326.1 | 272.4 | 244.6 | 281
1868.1 | 1705.1 | -6.7 | 0 | 0 | 292.9 | 303.3 | 235 | 233.3 | 214.4 | 48.7 | 18.8 | 82.5 | 2.8 | 189.3 | 3.6 | 37.9 | 32.6 | 38.2 | 44.8 | 31.6 | 34.7 | 54.2 | 46.9 | 52.8 | 26.8 | 281.6 | 218.9 | 39.3 | 345.5 | 243.1 | 268.9 | 286.1 | 325.8 | 272.1 | 244.2 | 280.6
1869.1 | 1706.1 | -6.7 | 0 | 0 | 292.1 | 302.6 | 234.6 | 232.9 | 214.3 | 48.7 | 18.8 | 82.4 | 3 | 176.6 | 3.2 | 37.2 | 32.9 | 38 | 44.1 | 31.6 | 35.9 | 55.9 | 47.1 | 52.6 | 26.9 | 280.1 | 220.6 | 38.7 | 345.1 | 242.7 | 268.6 | 285.6 | 325.5 | 271.8 | 243.7 | 280.2
1870.1 | 1707.1 | -6.7 | 0 | 0 | 290.6 | 302.9 | 233.9 | 232.6 | 214.5 | 48.6 | 18.8 | 82.3 | 3.1 | 165.2 | 3 | 35.9 | 32.3 | 37.7 | 43 | 31.5 | 36.9 | 56.2 | 47.1 | 52.5 | 27.1 | 279.2 | 219.9 | 38.3 | 344.7 | 242.3 | 268.4 | 285.1 | 325.2 | 271.5 | 243.3 | 279.8
1871.1 | 1708.1 | -6.7 | 0 | 0 | 288.9 | 304 | 233.5 | 232.2 | 214.6 | 48.5 | 18.8 | 82.2 | 3.4 | 168.3 | 3 | 35.2 | 33.4 | 37.8 | 42.4 | 31.4 | 36.2 | 57.1 | 46.9 | 52.4 | 27.5 | 278.2 | 219 | 37.9 | 344.2 | 241.9 | 268 | 284.7 | 324.9 | 271.1 | 243 | 279.4
1872.1 | 1709.1 | -6.7 | 0 | 0 | 288.1 | 305.1 | 233.3 | 231.8 | 214.5 | 48.4 | 18.8 | 82.1 | 3.4 | 176.8 | 3.6 | 35.1 | 34 | 38.1 | 42 | 31.3 | 36 | 57.8 | 46.9 | 52.3 | 27.7 | 276.8 | 214.8 | 37.7 | 343.8 | 241.7 | 267.4 | 284.3 | 324.6 | 270.7 | 242.8 | 279
1873.1 | 1710.1 | -6.7 | 0 | 0 | 288.7 | 305.7 | 233 | 231.3 | 214.5 | 48.4 | 18.8 | 82 | 3.8 | 174.5 | 4 | 34.3 | 35 | 38.4 | 41.6 | 31.2 | 35.7 | 57.7 | 46.9 | 52.3 | 27.8 | 275.2 | 209.2 | 37.6 | 343.4 | 241.3 | 267 | 283.9 | 324.3 | 270.2 | 242.6 | 278.7
1874.1 | 1711.1 | -6.7 | 0 | 0 | 290 | 304.3 | 232.7 | 230.9 | 214.3 | 48.4 | 18.8 | 81.9 | 3.5 | 175.1 | 4.3 | 33.8 | 35.5 | 39 | 41.2 | 31.2 | 35.6 | 57.3 | 47.5 | 52.3 | 27.7 | 274 | 204.8 | 37.5 | 343 | 240.9 | 266.6 | 283.5 | 324 | 269.9 | 242.3 | 278.3
1875.1 | 1712.1 | -6.7 | 0 | 0 | 291.3 | 302.4 | 232.5 | 230.6 | 214.2 | 48.5 | 18.8 | 81.8 | 3.8 | 187.7 | 4.2 | 34.2 | 35.7 | 39.8 | 40.9 | 31.2 | 35.6 | 57.1 | 47.8 | 52.1 | 27.8 | 272.8 | 201.8 | 37.3 | 342.5 | 240.6 | 266.2 | 283.1 | 323.7 | 269.5 | 242 | 278
1876.1 | 1713.1 | -6.7 | 0 | 0 | 291.4 | 300.9 | 232.2 | 230.3 | 214.4 | 48.5 | 18.8 | 81.6 | 3.6 | 212.9 | 4.2 | 33.8 | 36.4 | 40.2 | 40.6 | 31.1 | 35.6 | 57.7 | 48 | 52.1 | 27.9 | 271.6 | 200.5 | 37.2 | 342.1 | 240.3 | 265.9 | 282.8 | 323.4 | 269 | 241.6 | 277.6
1877.1 | 1714.1 | -6.7 | 0 | 0 | 291.7 | 300.5 | 231.8 | 230.1 | 214.2 | 48.5 | 18.8 | 81.5 | 3.5 | 202.7 | 4 | 33.5 | 37.2 | 40.5 | 40.3 | 31.2 | 35.7 | 58 | 48.2 | 52.2 | 28.1 | 270.7 | 198.9 | 37.4 | 341.7 | 240.1 | 265.5 | 282.4 | 323.1 | 268.4 | 241.3 | 277.2
1878.1 | 1715.1 | -6.7 | 0 | 0 | 290.7 | 299.8 | 231.5 | 229.9 | 213.9 | 48.4 | 18.8 | 81.5 | 3.4 | 182 | 3.9 | 33.5 | 38.2 | 40.5 | 40.1 | 31.5 | 35.7 | 57.9 | 48.5 | 52.2 | 28.3 | 269.6 | 196.8 | 37.5 | 341.3 | 239.6 | 265.2 | 281.9 | 322.8 | 268.2 | 240.9 | 276.8
1879.1 | 1716.1 | -6.7 | 0 | 0 | 288.3 | 299.1 | 231.3 | 229.6 | 213.7 | 48.3 | 18.8 | 81.4 | 3.4 | 203 | 3.8 | 33.6 | 38.4 | 40.6 | 39.8 | 31.4 | 35.7 | 57.9 | 48.8 | 52.1 | 28.4 | 268.1 | 195.2 | 37.4 | 340.8 | 239.3 | 264.9 | 281.5 | 322.5 | 267.9 | 240.6 | 276.5
1880.1 | 1717.1 | -6.7 | 0 | 0 | 287.2 | 297.5 | 231 | 229.3 | 213.5 | 48.2 | 18.8 | 81.2 | 3.2 | 210.7 | 4.3 | 34.1 | 38.8 | 40.6 | 39.7 | 31.3 | 35.7 | 57.8 | 48.9 | 51.9 | 28.6 | 266.2 | 192.3 | 37.6 | 340.4 | 239 | 264.6 | 281.2 | 322.1 | 267.7 | 240.3 | 276.1
1881.1 | 1718.1 | -6.7 | 0 | 0 | 286.5 | 297.5 | 230.9 | 229 | 213.5 | 48.1 | 18.8 | 81.1 | 3.6 | 203.6 | 4.4 | 34.2 | 39.4 | 40.6 | 39.6 | 31.3 | 35.7 | 57.7 | 48.7 | 51.9 | 28.8 | 264.3 | 192.1 | 37.2 | 340 | 238.7 | 264.2 | 280.8 | 321.9 | 267.3 | 240 | 275.7
1882.1 | 1719.1 | -6.7 | 0 | 0 | 285 | 297.3 | 230.8 | 228.7 | 213.4 | 48 | 18.8 | 81 | 3.5 | 191.4 | 4.4 | 33.8 | 39.4 | 40.5 | 39.5 | 31.4 | 35.7 | 57.7 | 48.4 | 51.6 | 29 | 262.6 | 191 | 37 | 339.6 | 238.4 | 263.9 | 280.4 | 321.6 | 267.1 | 239.6 | 275.4
1883.1 | 1720.1 | -6.7 | 0 | 0 | 284.1 | 298.5 | 230.6 | 228.5 | 213.4 | 48 | 18.8 | 80.9 | 3.7 | 188 | 3.9 | 33.8 | 39.7 | 40.4 | 39.4 | 31.4 | 35.7 | 57.4 | 48.2 | 51.6 | 29.2 | 261 | 191.3 | 36.9 | 339.1 | 238.1 | 263.7 | 280 | 321.3 | 266.9 | 239.2 | 275
1884.1 | 1721.1 | -6.7 | 0 | 0 | 283.4 | 299.1 | 230.3 | 228.3 | 213.4 | 47.9 | 18.8 | 80.8 | 3.3 | 188.7 | 3.5 | 33.4 | 40.1 | 40.1 | 39.3 | 31.5 | 35.7 | 57.4 | 48.1 | 51.5 | 29.4 | 258.8 | 190 | 36.8 | 338.7 | 237.8 | 263.3 | 279.5 | 321 | 266.7 | 239 | 274.6
1885.1 | 1722.1 | -6.7 | 0 | 0 | 282.2 | 298.5 | 230.1 | 228.1 | 213.4 | 47.8 | 18.8 | 80.7 | 3.5 | 188.4 | 3.1 | 33.4 | 39.8 | 39.9 | 39.2 | 31.5 | 35.7 | 57.5 | 48.1 | 51.4 | 29.6 | 257.3 | 187.9 | 36.7 | 338.3 | 237.6 | 262.8 | 279.1 | 320.7 | 266.3 | 238.8 | 274.2
1886.1 | 1723.1 | -6.7 | 0 | 0 | 281.5 | 297.7 | 229.8 | 227.9 | 213.5 | 47.7 | 18.8 | 80.6 | 3.2 | 185 | 3 | 33.4 | 39.4 | 39.9 | 39.2 | 31.5 | 35.8 | 57.4 | 47.9 | 51.3 | 29.9 | 256.3 | 188.2 | 36.5 | 337.9 | 237.3 | 262.5 | 278.8 | 320.4 | 266.2 | 238.5 | 273.9
1887.1 | 1724.1 | -6.7 | 0 | 0 | 281.1 | 297.2 | 229.6 | 227.6 | 213.5 | 47.7 | 18.8 | 80.5 | 3.5 | 181.8 | 3 | 33.3 | 39.6 | 40 | 39.2 | 31.6 | 35.9 | 56.9 | 47.7 | 51.4 | 30 | 255.3 | 187.6 | 36.2 | 337.4 | 237 | 262.1 | 278.3 | 320.1 | 265.9 | 238.2 | 273.5
1888.1 | 1725.1 | -6.7 | 0 | 0 | 281.9 | 297.8 | 229.4 | 227.4 | 213.4 | 47.6 | 18.8 | 80.4 | 3.4 | 200.6 | 2.9 | 33.6 | 39.8 | 40 | 39.1 | 31.7 | 36 | 58 | 47.7 | 51.4 | 30.2 | 254.3 | 186.1 | 36 | 337 | 236.7 | 261.7 | 277.9 | 319.8 | 265.6 | 238 | 273.2
1889.1 | 1726.1 | -6.7 | 0 | 0 | 281.8 | 297.7 | 229.2 | 227.3 | 213.4 | 47.5 | 18.8 | 80.3 | 3.3 | 238.1 | 3.1 | 33.5 | 40 | 40 | 39.1 | 31.7 | 36 | 58.2 | 47.8 | 51.5 | 30.5 | 253.2 | 186.3 | 35.9 | 336.6 | 236.3 | 261.3 | 277.6 | 319.5 | 265.3 | 237.7 | 272.8
1890.1 | 1727.1 | -6.7 | 0 | 0 | 281.2 | 297.1 | 228.9 | 227.1 | 213.3 | 47.3 | 18.8 | 80.2 | 3.4 | 237.5 | 3.1 | 33.2 | 39.8 | 39.7 | 39.1 | 31.8 | 36 | 58.2 | 48.1 | 51.6 | 30.7 | 252.6 | 186.1 | 35.9 | 336.2 | 236.1 | 261 | 277.2 | 319.2 | 264.9 | 237.4 | 272.4
1891.1 | 1728.1 | -6.7 | 0 | 0 | 280.3 | 295.8 | 228.5 | 226.9 | 213.2 | 47.2 | 18.8 | 80.1 | 3.7 | 195.2 | 3 | 33.1 | 39.2 | 39.3 | 39.1 | 31.8 | 36.1 | 57.3 | 48.3 | 51.7 | 30.9 | 251.4 | 184.6 | 35.7 | 335.7 | 235.8 | 260.8 | 276.8 | 318.9 | 264.4 | 237.2 | 272.1
1892.1 | 1729.1 | -6.7 | 0 | 0 | 278.9 | 295.2 | 228.2 | 226.7 | 213 | 47.2 | 18.8 | 80 | 3.6 | 178.9 | 2.9 | 33.2 | 39.2 | 39.3 | 39.1 | 31.9 | 36.1 | 57.2 | 48.4 | 51.8 | 31.1 | 249.9 | 183.8 | 35.4 | 335.3 | 235.6 | 260.5 | 276.4 | 318.6 | 264.1 | 237 | 271.7
1893.1 | 1730.1 | -6.7 | 0 | 0 | 277.9 | 295 | 228.1 | 226.5 | 212.7 | 47.1 | 18.8 | 79.9 | 3.2 | 193.7 | 2.8 | 33.1 | 39.6 | 39.3 | 39.1 | 31.9 | 36.1 | 57 | 48.4 | 51.8 | 31.2 | 248.2 | 183.4 | 35.2 | 334.9 | 235.4 | 260.2 | 276 | 318.3 | 263.7 | 236.7 | 271.4
1894.1 | 1731.1 | -6.7 | 0 | 0 | 276.7 | 295.7 | 228 | 226.3 | 212.6 | 47.1 | 18.8 | 79.9 | 3.2 | 199.1 | 2.9 | 33 | 39.1 | 39.2 | 39.1 | 31.9 | 36.2 | 56.6 | 48.1 | 51.7 | 31.3 | 246.8 | 183.1 | 35.1 | 334.5 | 235.2 | 259.8 | 275.7 | 318 | 263.4 | 236.5 | 271.1
1895.1 | 1732.1 | -6.7 | 0 | 0 | 275.1 | 295.3 | 227.7 | 226.1 | 212.4 | 47 | 18.8 | 79.8 | 3 | 196.6 | 2.9 | 32.9 | 39.3 | 39.1 | 39.2 | 32 | 36.3 | 56.5 | 48 | 51.6 | 31.5 | 245.8 | 184.8 | 35 | 334 | 234.9 | 259.5 | 275.3 | 317.7 | 263.2 | 236.3 | 270.7
1896.1 | 1733.1 | -6.7 | 0 | 0 | 274.9 | 294.3 | 227.4 | 225.9 | 212.2 | 46.9 | 18.8 | 79.8 | 3.2 | 192.5 | 2.9 | 33.4 | 39.7 | 39 | 39.2 | 32.1 | 36.4 | 56.6 | 48 | 51.6 | 31.8 | 244.6 | 184.2 | 34.9 | 333.6 | 234.6 | 259.2 | 274.9 | 317.4 | 263 | 236 | 270.3
1897.1 | 1734.1 | -6.7 | 0 | 0 | 275.4 | 294 | 227 | 225.5 | 211.9 | 47 | 18.8 | 79.7 | 3.3 | 192.6 | 2.7 | 33.4 | 39.7 | 39 | 39.2 | 32.1 | 36.6 | 56.8 | 47.9 | 51.7 | 31.9 | 243.2 | 182.8 | 34.8 | 333.2 | 234.4 | 258.8 | 274.5 | 317.1 | 262.8 | 235.7 | 270
1898.1 | 1735.1 | -6.7 | 0 | 0 | 274.9 | 293.6 | 226.8 | 225.3 | 211.6 | 47.1 | 18.8 | 79.6 | 3.2 | 205.5 | 2.6 | 33.5 | 39.8 | 39 | 39.3 | 32.2 | 36.7 | 56.6 | 47.8 | 51.7 | 32.1 | 241.9 | 180.8 | 34.7 | 332.8 | 234.2 | 258.2 | 274.1 | 316.8 | 262.4 | 235.5 | 269.7
1899.1 | 1736.1 | -6.7 | 0 | 0 | 274.7 | 293.5 | 226.6 | 225.1 | 211.5 | 47.1 | 18.8 | 79.5 | 3 | 210.1 | 2.5 | 33.6 | 39.4 | 39 | 39.3 | 32.3 | 36.8 | 56.3 | 47.8 | 51.7 | 32.3 | 240.4 | 180.2 | 34.6 | 332.3 | 233.9 | 257.9 | 273.7 | 316.6 | 262.2 | 235.2 | 269.3
1900.1 | 1737.1 | -6.7 | 0 | 0 | 273.8 | 292.6 | 226.4 | 224.8 | 211.4 | 47.1 | 18.8 | 79.5 | 3 | 210.2 | 2.2 | 33.8 | 39.4 | 38.9 | 39.3 | 32.3 | 36.8 | 56 | 47.9 | 51.9 | 32.5 | 238.6 | 181.1 | 34.5 | 331.9 | 233.6 | 257.6 | 273.4 | 316.3 | 262 | 235 | 269
1901.1 | 1738.1 | -6.7 | 0 | 0 | 273.1 | 292.2 | 226.2 | 224.6 | 211.1 | 47.1 | 18.8 | 79.4 | 3.1 | 198.3 | 2 | 33.8 | 39.8 | 39 | 39.4 | 32.4 | 37 | 55.7 | 47.9 | 52 | 32.7 | 236.9 | 180.1 | 34.3 | 331.5 | 233.3 | 257.2 | 273 | 316 | 261.6 | 234.6 | 268.6
1902.1 | 1739.1 | -6.7 | 0 | 0 | 271.9 | 292.8 | 226 | 224.4 | 210.7 | 47 | 18.8 | 79.3 | 3.3 | 180.2 | 2.6 | 34 | 40.3 | 38.9 | 39.4 | 32.5 | 37.1 | 55.6 | 48 | 52.1 | 32.9 | 235.7 | 180.5 | 34.1 | 331.1 | 233.1 | 256.9 | 272.6 | 315.7 | 261.3 | 234.3 | 268.2
1903.1 | 1740.1 | -6.7 | 0 | 0 | 271.5 | 292 | 225.7 | 224.2 | 210.5 | 46.9 | 18.8 | 79.2 | 4 | 180.5 | 4 | 34.2 | 40.9 | 38.8 | 39.4 | 32.6 | 37.3 | 55.9 | 48.1 | 52.1 | 33 | 234.8 | 181.2 | 34.1 | 330.7 | 232.9 | 256.5 | 272.3 | 315.4 | 260.8 | 234.1 | 267.9
1904.1 | 1741.1 | -6.5 | 0 | 0 | 270.8 | 291.4 | 225.3 | 224 | 210.3 | 46.8 | 18.8 | 79.1 | 4.3 | 180.2 | 4.5 | 34.1 | 40.4 | 38.5 | 39.5 | 32.7 | 37.4 | 55.8 | 48.2 | 52.1 | 33.2 | 234.3 | 179.9 | 33.7 | 330.3 | 232.7 | 256.1 | 271.9 | 315.1 | 260.6 | 233.9 | 267.6
1905.1 | 1742.1 | -6.6 | 0 | 0 | 270 | 291.7 | 225.1 | 223.6 | 210.1 | 46.8 | 18.8 | 79 | 3.8 | 208.5 | 5.1 | 33.8 | 40.4 | 38.5 | 39.5 | 32.7 | 37.5 | 55.9 | 48.3 | 52.2 | 33.4 | 233.3 | 179.9 | 33.5 | 329.9 | 232.4 | 255.8 | 271.6 | 314.8 | 260.4 | 233.5 | 267.2
1906.1 | 1743.1 | -6.7 | 0 | 0 | 269.9 | 290.9 | 225 | 223.3 | 209.8 | 46.8 | 18.9 | 78.8 | 4.3 | 237.6 | 4.2 | 33.3 | 40 | 38.3 | 39.6 | 32.8 | 37.6 | 56.1 | 48.4 | 52.3 | 33.6 | 232.3 | 179.3 | 33.4 | 329.5 | 232.2 | 255.4 | 271.2 | 314.5 | 260.2 | 233.3 | 266.9
1907.1 | 1744.1 | -6.4 | 0 | 0 | 269.2 | 290.1 | 224.7 | 223.1 | 209.6 | 46.8 | 18.9 | 78.6 | 3.9 | 218.5 | 4 | 32.7 | 39.4 | 38.1 | 39.6 | 32.8 | 37.8 | 56.1 | 48.6 | 52.4 | 33.8 | 231.6 | 179.1 | 33.2 | 329.1 | 231.9 | 255 | 270.8 | 314.2 | 260 | 233.1 | 266.6
1908.1 | 1745.1 | -5.8 | 0 | 0 | 267.9 | 288.7 | 224.4 | 222.8 | 209.2 | 46.7 | 18.9 | 78.5 | 3.7 | 200 | 5.4 | 32 | 39.1 | 37.8 | 39.7 | 32.9 | 37.9 | 56.1 | 48.4 | 52.3 | 34 | 230.9 | 179.3 | 32.9 | 328.7 | 231.6 | 254.7 | 270.4 | 313.9 | 259.8 | 232.9 | 266.2
1909.1 | 1746.1 | -6.5 | 0 | 0 | 267.5 | 289 | 224.1 | 222.5 | 208.8 | 46.6 | 18.9 | 78.4 | 4 | 211.1 | 6.4 | 31.8 | 39.5 | 37.7 | 39.7 | 32.9 | 38 | 56.8 | 48.4 | 52.3 | 34.1 | 230.4 | 178.3 | 32.8 | 328.3 | 231.3 | 254.4 | 270 | 313.6 | 259.6 | 232.8 | 265.9
1910.1 | 1747.1 | -6.7 | 0 | 0 | 267 | 289 | 223.7 | 222.3 | 208.5 | 46.6 | 18.9 | 78.2 | 3.9 | 206.8 | 6.9 | 31.7 | 39.9 | 37.7 | 39.7 | 32.9 | 38.1 | 57 | 48.4 | 52.3 | 34.3 | 229.8 | 177.3 | 32.7 | 327.9 | 231 | 254 | 269.7 | 313.4 | 259.3 | 232.6 | 265.6
1911.1 | 1748.1 | -6.7 | 0 | 0 | 266 | 288.7 | 223.4 | 222 | 208.4 | 46.5 | 18.9 | 78.1 | 4.1 | 228 | 6 | 31.8 | 40.2 | 37.8 | 39.8 | 33 | 38.2 | 56.9 | 48.4 | 52.3 | 34.4 | 229.7 | 177.1 | 32.5 | 327.5 | 230.7 | 253.7 | 269.3 | 313.1 | 259 | 232.3 | 265.2
1912.1 | 1749.1 | -6.7 | 0 | 0 | 265.2 | 289.4 | 223.2 | 221.8 | 208.2 | 46.4 | 18.9 | 77.9 | 3.9 | 269.3 | 5.3 | 31.8 | 39.6 | 37.5 | 39.8 | 33 | 38.3 | 56.5 | 48.4 | 52.4 | 34.6 | 229.2 | 177.2 | 32.4 | 327.1 | 230.5 | 253.4 | 268.9 | 312.8 | 258.6 | 232 | 264.9
1913.1 | 1750.1 | -6.3 | 0 | 0 | 264.7 | 289.6 | 222.9 | 221.7 | 207.9 | 46.3 | 18.9 | 77.8 | 4.3 | 256.6 | 5.5 | 31.9 | 39.2 | 37.3 | 39.8 | 33 | 38.4 | 56.4 | 48.4 | 52.6 | 34.7 | 227.7 | 177.1 | 32.2 | 326.7 | 230.3 | 253.2 | 268.6 | 312.5 | 258.4 | 231.7 | 264.6
1914.1 | 1751.1 | -6.5 | 0 | 0 | 264.4 | 288.5 | 222.5 | 221.4 | 207.6 | 46.3 | 18.9 | 77.6 | 4.5 | 270.2 | 5.8 | 31.5 | 38.9 | 37.1 | 39.9 | 33.1 | 38.6 | 56.3 | 48.6 | 52.6 | 34.9 | 226.7 | 175.8 | 32.1 | 326.3 | 230.1 | 252.9 | 268.3 | 312.2 | 258.1 | 231.4 | 264.2
1915.1 | 1752.1 | -6.3 | 0 | 0 | 263.9 | 287.4 | 222.2 | 221.1 | 207.3 | 46.2 | 18.9 | 77.5 | 4 | 272.4 | 6.3 | 31.1 | 39 | 37 | 39.9 | 33.1 | 38.7 | 55.7 | 48.5 | 52.7 | 35.1 | 225.9 | 174.1 | 31.9 | 325.9 | 229.9 | 252.7 | 268 | 311.9 | 257.7 | 231.1 | 263.9
1916.1 | 1753.1 | -6 | 0 | 0 | 264 | 286.7 | 222 | 220.9 | 207.2 | 46.1 | 18.9 | 77.4 | 4.4 | 270.3 | 6.7 | 30.9 | 37.9 | 37 | 39.9 | 33 | 38.7 | 55.3 | 48.6 | 52.6 | 35.2 | 225.5 | 173.8 | 31.7 | 325.5 | 229.6 | 252.4 | 267.6 | 311.6 | 257.3 | 230.9 | 263.6
1917.1 | 1754.1 | -6.3 | 0 | 0 | 264 | 285.3 | 221.8 | 220.7 | 207.1 | 46.1 | 18.9 | 77.3 | 4.4 | 262.1 | 6.8 | 30.9 | 37.6 | 37 | 40 | 33.1 | 38.9 | 55.2 | 48.6 | 52.8 | 35.3 | 224.6 | 173.2 | 31.6 | 325.1 | 229.3 | 252 | 267.2 | 311.3 | 257.2 | 230.7 | 263.2
1918.1 | 1755.1 | -6.6 | 0 | 0 | 263 | 284 | 221.6 | 220.6 | 206.9 | 46 | 18.9 | 77.2 | 4.2 | 257.7 | 7.3 | 31.4 | 37.1 | 37 | 40 | 33.1 | 39 | 55.3 | 48.4 | 52.8 | 35.5 | 223.2 | 172.9 | 31.6 | 324.7 | 229 | 251.7 | 266.9 | 311.1 | 256.8 | 230.4 | 262.9
1919.1 | 1756.1 | -6.4 | 0 | 0 | 261.6 | 283.3 | 221.5 | 220.2 | 206.6 | 46 | 18.9 | 77.1 | 3.8 | 249.8 | 8.2 | 31.4 | 37.2 | 37.1 | 40 | 33.1 | 39.1 | 55.3 | 48.3 | 52.8 | 35.6 | 222.8 | 171.8 | 31.5 | 324.4 | 228.8 | 251.4 | 266.5 | 310.8 | 256.4 | 230 | 262.6
1920.1 | 1757.1 | -6 | 0 | 0 | 260.7 | 282.8 | 221.4 | 220 | 206.5 | 46 | 18.9 | 77 | 3.8 | 243 | 8.3 | 30.9 | 37.5 | 37.1 | 40.1 | 33.1 | 39.3 | 55.1 | 47.7 | 52.8 | 35.8 | 223.1 | 170.8 | 31.3 | 324 | 228.6 | 251.1 | 266.2 | 310.5 | 256.1 | 229.7 | 262.2
1921.1 | 1758.1 | -4.8 | 0 | 0 | 259.5 | 281.8 | 221.2 | 219.8 | 206.2 | 46 | 18.9 | 76.9 | 4 | 255.1 | 7.9 | 30.6 | 36.8 | 37 | 40.1 | 33.1 | 39.4 | 54.4 | 47.9 | 52.7 | 36 | 223.3 | 170.7 | 31.2 | 323.6 | 228.4 | 250.8 | 265.8 | 310.2 | 255.9 | 229.5 | 261.9
1922.1 | 1759.1 | -5.5 | 0 | 0 | 258.5 | 280.5 | 220.9 | 219.7 | 205.9 | 45.9 | 18.9 | 76.8 | 4.1 | 236.6 | 8.1 | 30.3 | 36.5 | 36.8 | 40.2 | 33.1 | 39.5 | 54.4 | 47.9 | 52.8 | 36.1 | 223.3 | 169.7 | 31 | 323.2 | 228.2 | 250.4 | 265.5 | 309.9 | 255.7 | 229.2 | 261.7
1923.1 | 1760.1 | -6.5 | 0 | 0 | 258 | 279.2 | 220.6 | 219.5 | 205.7 | 45.7 | 18.9 | 76.7 | 4.3 | 230.8 | 8.6 | 30.5 | 36.5 | 36.5 | 40.2 | 33.1 | 39.6 | 54.8 | 47.3 | 52.8 | 36.3 | 222.9 | 169 | 30.8 | 322.9 | 227.9 | 250.1 | 265.2 | 309.6 | 255.4 | 229 | 261.3
1924.1 | 1761.1 | -5.6 | 0 | 0 | 257.5 | 279.2 | 220.4 | 219.3 | 205.2 | 45.5 | 18.9 | 76.6 | 4.3 | 227.3 | 8.6 | 31.1 | 35.8 | 36.3 | 40.2 | 33.2 | 39.7 | 55 | 47.1 | 52.9 | 36.4 | 222.6 | 169.1 | 30.8 | 322.5 | 227.7 | 249.9 | 264.8 | 309.3 | 255.1 | 228.8 | 261
1925.1 | 1762.1 | -5.4 | 0 | 0 | 256.6 | 279.1 | 220.3 | 219 | 204.9 | 45.5 | 18.9 | 76.5 | 4.4 | 240.3 | 7.8 | 31.6 | 36.3 | 36.1 | 40.3 | 33.2 | 39.9 | 55.1 | 47.5 | 52.8 | 36.5 | 222.3 | 168.6 | 30.8 | 322.1 | 227.4 | 249.5 | 264.4 | 309 | 254.6 | 228.5 | 260.7
1926.1 | 1763.1 | -5 | 0 | 0 | 256.1 | 278.9 | 220.1 | 218.7 | 204.6 | 45.5 | 18.9 | 76.4 | 4 | 236.2 | 7.1 | 31.4 | 36.7 | 36.1 | 40.3 | 33.3 | 40 | 54.8 | 47.3 | 52.7 | 36.7 | 221.9 | 167.9 | 30.8 | 321.7 | 227.1 | 249.3 | 264.1 | 308.8 | 254.3 | 228.3 | 260.4
1927.1 | 1764.1 | -3.2 | 0 | 0 | 255.2 | 279.1 | 219.9 | 218.3 | 204.3 | 45.5 | 18.9 | 76.3 | 3.5 | 231.1 | 7.2 | 31.3 | 36.9 | 36.2 | 40.4 | 33.3 | 40.1 | 54.6 | 47.3 | 52.7 | 36.8 | 221.4 | 167.3 | 30.7 | 321.4 | 226.8 | 249.1 | 263.8 | 308.5 | 254.1 | 228 | 260.1
1928.1 | 1765.1 | -3.2 | 0 | 0 | 254.5 | 278.5 | 219.7 | 218.1 | 204.2 | 45.5 | 18.9 | 76.3 | 3.9 | 242.4 | 7.2 | 31 | 36.5 | 36.2 | 40.4 | 33.3 | 40.2 | 54.5 | 48.2 | 52.8 | 36.9 | 221.7 | 166.8 | 30.5 | 321 | 226.5 | 248.9 | 263.4 | 308.2 | 253.8 | 227.7 | 259.7
1929.1 | 1766.1 | -5.1 | 0 | 0 | 254.1 | 278.3 | 219.4 | 217.8 | 204 | 45.4 | 18.9 | 76.2 | 4 | 236.3 | 7.4 | 30.9 | 36.4 | 36.2 | 40.5 | 33.4 | 40.2 | 54.4 | 48.8 | 52.9 | 37.1 | 221 | 166.3 | 30.4 | 320.6 | 226.3 | 248.5 | 263.1 | 307.9 | 253.3 | 227.5 | 259.5
1930.1 | 1767.1 | -6.4 | 0 | 0 | 253.4 | 277.4 | 219.2 | 217.6 | 203.8 | 45.3 | 18.9 | 76 | 3.8 | 244.7 | 7.8 | 30.8 | 36.7 | 36 | 40.5 | 33.5 | 40.4 | 54.1 | 49.5 | 53 | 37.2 | 219.7 | 166.5 | 30.2 | 320.3 | 226 | 248.2 | 262.8 | 307.6 | 252.9 | 227.2 | 259.1
1931.1 | 1768.1 | -6.5 | 0 | 0 | 253.1 | 276.2 | 219 | 217.3 | 203.7 | 45.2 | 18.9 | 75.9 | 3.9 | 243.6 | 8.3 | 30.5 | 36.8 | 35.8 | 40.5 | 33.6 | 40.4 | 54.2 | 50 | 53 | 37.3 | 218.7 | 167.3 | 30.1 | 319.9 | 225.8 | 247.9 | 262.4 | 307.3 | 252.7 | 226.9 | 258.8
1932.1 | 1769.1 | -6.6 | 0 | 0 | 253.1 | 275.7 | 218.8 | 217.1 | 203.4 | 45.2 | 18.9 | 75.8 | 3.8 | 237.9 | 8.7 | 30.2 | 37.6 | 35.6 | 40.6 | 33.6 | 40.6 | 54.2 | 50 | 53.1 | 37.5 | 218.1 | 167 | 30.1 | 319.5 | 225.5 | 247.7 | 262.1 | 307 | 252.5 | 226.6 | 258.5
1933.1 | 1770.1 | -6.7 | 0 | 0 | 252.8 | 275 | 218.6 | 216.8 | 203.2 | 45.1 | 18.9 | 75.7 | 3.7 | 242.1 | 8.7 | 30.5 | 38.3 | 35.4 | 40.6 | 33.6 | 40.7 | 54.5 | 49.7 | 53.2 | 37.6 | 218.1 | 167.8 | 30 | 319.2 | 225.3 | 247.4 | 261.7 | 306.7 | 252.2 | 226.2 | 258.2
1934.1 | 1771.1 | -6.6 | 0 | 0 | 252.1 | 274.9 | 218.3 | 216.6 | 203.1 | 45.1 | 18.9 | 75.6 | 3.6 | 254.3 | 8.3 | 30.6 | 38.1 | 35.2 | 40.7 | 33.6 | 40.7 | 54.3 | 50.1 | 53.3 | 37.7 | 217.6 | 167.3 | 29.9 | 318.8 | 225 | 247.1 | 261.4 | 306.5 | 251.9 | 225.9 | 257.9
1935.1 | 1772.1 | -6.6 | 0 | 0 | 251.3 | 274.4 | 218.2 | 216.3 | 203.1 | 45 | 18.9 | 75.5 | 4.1 | 265.5 | 8.5 | 30.6 | 38.3 | 35.1 | 40.8 | 33.6 | 40.8 | 54.1 | 49.9 | 53.3 | 37.9 | 217 | 168.1 | 29.8 | 318.4 | 224.8 | 246.8 | 261.1 | 306.2 | 251.5 | 225.6 | 257.6
1936.1 | 1773.1 | -6.4 | 0 | 0 | 250.8 | 273.5 | 218 | 216 | 203 | 44.9 | 18.9 | 75.3 | 4.4 | 256.1 | 8.1 | 30.2 | 38.2 | 35 | 40.8 | 33.7 | 40.9 | 54.2 | 49.9 | 53.4 | 38 | 217 | 168.8 | 29.9 | 318.1 | 224.7 | 246.4 | 260.7 | 305.9 | 251 | 225.4 | 257.3
1937.1 | 1774.1 | -6.5 | 0 | 0 | 250.4 | 273.9 | 217.8 | 215.8 | 202.8 | 44.8 | 18.9 | 75.2 | 4.4 | 248.7 | 7.2 | 30 | 38 | 35 | 40.9 | 33.7 | 41.1 | 54.4 | 50 | 53.4 | 38.1 | 215.9 | 167 | 29.9 | 317.7 | 224.5 | 246.1 | 260.4 | 305.6 | 250.7 | 225.2 | 257
1938.1 | 1775.1 | -6.5 | 0 | 0 | 249.8 | 275 | 217.6 | 215.6 | 202.6 | 44.7 | 18.9 | 75.1 | 4.2 | 270.6 | 8.1 | 29.8 | 38.7 | 35.1 | 40.9 | 33.8 | 41.2 | 54.5 | 49.6 | 53.4 | 38.2 | 215.4 | 166.1 | 29.8 | 317.4 | 224.3 | 245.8 | 260.1 | 305.3 | 250.5 | 224.9 | 256.6
1939.1 | 1776.1 | -6.3 | 0 | 0 | 248.8 | 275 | 217.4 | 215.4 | 202.4 | 44.7 | 18.9 | 75 | 4 | 240.2 | 8.2 | 29.8 | 38.3 | 35.1 | 41 | 33.8 | 41.3 | 54.4 | 49.6 | 53.5 | 38.3 | 214.4 | 166.1 | 29.7 | 317 | 224.1 | 245.5 | 259.8 | 305 | 250.3 | 224.7 | 256.4
1940.1 | 1777.1 | -6.5 | 0 | 0 | 248.1 | 275.4 | 217.1 | 215.2 | 202.2 | 44.7 | 18.9 | 74.9 | 3.7 | 255.6 | 7.9 | 29.7 | 38.7 | 35 | 41 | 33.9 | 41.3 | 54.1 | 49.2 | 53.5 | 38.4 | 213.8 | 167.8 | 29.6 | 316.6 | 223.8 | 245.3 | 259.5 | 304.7 | 250.1 | 224.4 | 256
1941.1 | 1778.1 | -6.6 | 0 | 0 | 247.8 | 274.7 | 216.9 | 214.9 | 201.9 | 44.7 | 18.9 | 74.8 | 3.8 | 243 | 7.9 | 29.3 | 39 | 34.8 | 41.1 | 33.9 | 41.4 | 53.9 | 49.3 | 53.4 | 38.6 | 213 | 168.1 | 29.5 | 316.3 | 223.6 | 245.1 | 259.2 | 304.5 | 250 | 224.2 | 255.7
1942.1 | 1779.1 | -6.7 | 0 | 0 | 247.1 | 274 | 216.7 | 214.5 | 201.4 | 44.7 | 18.9 | 74.8 | 4.1 | 245 | 8.1 | 29.1 | 39 | 34.7 | 41.1 | 33.9 | 41.5 | 54.1 | 49.5 | 53.5 | 38.7 | 212.1 | 168.2 | 29.5 | 315.9 | 223.3 | 244.9 | 258.8 | 304.2 | 249.7 | 224 | 255.4
1943.1 | 1780.1 | -6.3 | 0 | 0 | 246.2 | 273.8 | 216.4 | 214.2 | 201.1 | 44.7 | 18.9 | 74.7 | 4 | 242.7 | 8.3 | 29.1 | 38.6 | 34.7 | 41.2 | 33.9 | 41.6 | 54.4 | 49.9 | 53.5 | 38.8 | 211.5 | 168 | 29.5 | 315.5 | 223 | 244.6 | 258.5 | 303.9 | 249.3 | 223.7 | 255.1
1944.1 | 1781.1 | -5.5 | 0 | 0 | 245.4 | 274.2 | 216.1 | 213.9 | 200.9 | 44.7 | 18.9 | 74.5 | 3.5 | 244.7 | 8.8 | 29.2 | 38.2 | 34.5 | 41.2 | 33.9 | 41.7 | 54.2 | 50.4 | 53.6 | 38.9 | 211.2 | 166.8 | 29.5 | 315.2 | 222.7 | 244.4 | 258.2 | 303.6 | 248.8 | 223.4 | 254.8
1945.1 | 1782.1 | -5.6 | 0 | 0 | 244.7 | 274.7 | 216 | 213.7 | 200.6 | 44.7 | 18.9 | 74.4 | 3.7 | 230.4 | 8.8 | 28.9 | 38 | 34.4 | 41.3 | 33.9 | 41.8 | 53.8 | 51.1 | 53.8 | 39 | 211.4 | 166.1 | 29.3 | 314.8 | 222.4 | 244.2 | 257.8 | 303.4 | 248.6 | 223.2 | 254.5
1946.1 | 1783.1 | -6.2 | 0 | 0 | 244.5 | 274.7 | 215.7 | 213.4 | 200.5 | 44.7 | 18.9 | 74.3 | 3.3 | 248.7 | 8.3 | 28.8 | 38.8 | 34.3 | 41.3 | 33.9 | 41.9 | 53.5 | 51.9 | 53.9 | 39.2 | 210.9 | 166.2 | 29.2 | 314.5 | 222.2 | 243.9 | 257.5 | 303.1 | 248.3 | 222.9 | 254.2
1947.1 | 1784.1 | -6.3 | 0 | 0 | 244.1 | 274 | 215.3 | 213.1 | 200.1 | 44.7 | 18.9 | 74.2 | 3.3 | 240.4 | 6.6 | 28.8 | 39.1 | 34.2 | 41.4 | 33.9 | 42 | 53.6 | 52.3 | 54 | 39.3 | 210.3 | 167.8 | 29 | 314.1 | 221.8 | 243.6 | 257.1 | 302.8 | 248 | 222.6 | 253.9
1948.1 | 1785.1 | -6.6 | 0 | 0 | 243.5 | 272.7 | 215 | 212.9 | 199.8 | 44.6 | 18.9 | 74.1 | 3.5 | 233.2 | 6.6 | 29 | 38.4 | 34.1 | 41.4 | 34 | 42.2 | 53.9 | 52.8 | 54.1 | 39.4 | 209.6 | 166.5 | 28.9 | 313.8 | 221.5 | 243.2 | 256.8 | 302.5 | 247.8 | 222.3 | 253.6
1949.1 | 1786.1 | -6.7 | 0 | 0 | 242.8 | 272 | 214.8 | 212.7 | 199.7 | 44.6 | 18.9 | 74 | 3.5 | 239.5 | 6.8 | 29 | 37.5 | 34 | 41.4 | 34.1 | 42.3 | 53.9 | 53.2 | 54.2 | 39.5 | 209 | 166.7 | 28.9 | 313.5 | 221.2 | 242.9 | 256.5 | 302.3 | 247.4 | 222.1 | 253.3
1950.1 | 1787.1 | -6.6 | 0 | 0 | 242 | 271.5 | 214.6 | 212.5 | 199.5 | 44.7 | 19 | 73.9 | 3.6 | 237 | 6.4 | 28.8 | 37.4 | 33.8 | 41.5 | 34.1 | 42.4 | 53.7 | 53.3 | 54.3 | 39.6 | 208.5 | 166.7 | 28.8 | 313.1 | 220.8 | 242.7 | 256.2 | 302 | 247 | 221.8 | 253
1951.1 | 1788.1 | -6.6 | 0 | 0 | 241.6 | 270.4 | 214.4 | 212.3 | 199.2 | 44.7 | 19 | 73.8 | 3.5 | 240.1 | 6.7 | 29.1 | 37 | 33.7 | 41.5 | 34.1 | 42.5 | 54.3 | 53.3 | 54.4 | 39.8 | 208.7 | 166.5 | 28.7 | 312.8 | 220.5 | 242.4 | 255.8 | 301.7 | 246.7 | 221.5 | 252.7
1952.1 | 1789.1 | -6.6 | 0 | 0 | 240.8 | 269.5 | 214.1 | 212 | 199 | 44.7 | 19 | 73.7 | 4 | 230 | 6.7 | 28.9 | 37 | 33.7 | 41.6 | 34.1 | 42.7 | 54.8 | 53.2 | 54.4 | 39.9 | 208.6 | 167.5 | 28.7 | 312.4 | 220.3 | 242.1 | 255.5 | 301.4 | 246.4 | 221.3 | 252.4
1953.1 | 1790.1 | -6.5 | 0 | 0 | 240.1 | 268.6 | 213.7 | 211.8 | 198.9 | 44.7 | 19 | 73.6 | 3.8 | 246.1 | 6.1 | 28.7 | 36.9 | 33.7 | 41.6 | 34.1 | 42.8 | 55 | 52.8 | 54.5 | 40 | 207.1 | 166.6 | 28.6 | 312.1 | 220 | 241.8 | 255.2 | 301.1 | 246.2 | 221 | 252.1
1954.1 | 1791.1 | -6.4 | 0 | 0 | 239.6 | 267.4 | 213.5 | 211.5 | 198.8 | 44.7 | 19 | 73.6 | 3.3 | 241.4 | 5.6 | 28.6 | 37 | 33.7 | 41.7 | 34.1 | 42.9 | 54.9 | 52.9 | 54.6 | 40.2 | 206.9 | 165.7 | 28.5 | 311.7 | 219.8 | 241.4 | 254.8 | 300.8 | 246 | 220.7 | 251.8
1955.1 | 1792.1 | -6.6 | 0 | 0 | 239.3 | 266.4 | 213.3 | 211.2 | 198.6 | 44.6 | 19 | 73.5 | 3.8 | 232.9 | 4.9 | 28.7 | 37.4 | 33.5 | 41.8 | 34.1 | 43.1 | 54.9 | 53.1 | 54.6 | 40.3 | 207.3 | 164.6 | 28.6 | 311.4 | 219.5 | 241.1 | 254.5 | 300.6 | 245.6 | 220.5 | 251.5
1956.1 | 1793.1 | -6.6 | 0 | 0 | 239 | 265.7 | 213 | 211 | 198.2 | 44.5 | 19 | 73.4 | 4 | 225.2 | 4.3 | 28.4 | 37.8 | 33.5 | 41.8 | 34.1 | 43.2 | 54.6 | 52.5 | 54.6 | 40.4 | 208 | 163.5 | 28.6 | 311.1 | 219.1 | 240.9 | 254.2 | 300.3 | 245.3 | 220.3 | 251.2
1957.1 | 1794.1 | -6.5 | 0 | 0 | 238.6 | 264.5 | 212.8 | 210.8 | 197.8 | 44.5 | 19 | 73.3 | 4 | 228 | 3.7 | 28.4 | 38.2 | 33.5 | 41.8 | 34.1 | 43.3 | 54.1 | 52.4 | 54.6 | 40.5 | 206.6 | 162.3 | 28.4 | 310.7 | 218.8 | 240.6 | 253.9 | 300 | 245 | 220 | 250.9
1958.1 | 1795.1 | -6.4 | 0 | 0 | 238.4 | 263.4 | 212.6 | 210.5 | 197.5 | 44.4 | 19 | 73.2 | 4.3 | 265.5 | 3.8 | 28.7 | 37.4 | 33.6 | 41.9 | 34.1 | 43.4 | 54.4 | 52.5 | 54.6 | 40.6 | 205.8 | 162 | 28.4 | 310.4 | 218.6 | 240.4 | 253.6 | 299.7 | 244.8 | 219.8 | 250.6
1959.1 | 1796.1 | -6.4 | 0 | 0 | 237.9 | 263 | 212.3 | 210.3 | 197 | 44.3 | 19 | 73 | 3.7 | 261.8 | 5 | 29.1 | 37 | 33.6 | 41.9 | 34.1 | 43.5 | 54.8 | 52 | 54.7 | 40.7 | 204.6 | 158.7 | 28.3 | 310 | 218.4 | 240.1 | 253.3 | 299.4 | 244.7 | 219.6 | 250.4
1960.1 | 1797.1 | -6.5 | 0 | 0 | 237.6 | 262.4 | 211.9 | 210.1 | 196.7 | 44.2 | 19 | 73 | 3.4 | 257.3 | 6 | 28.9 | 36.9 | 33.6 | 42 | 34.2 | 43.6 | 54.9 | 51.8 | 54.7 | 40.8 | 203 | 156.6 | 28.4 | 309.7 | 218.2 | 239.8 | 253 | 299.2 | 244.6 | 219.4 | 250.1
1961.1 | 1798.1 | -6.5 | 0 | 0 | 236.9 | 261.5 | 211.6 | 209.9 | 196.5 | 44.2 | 19 | 72.9 | 4.1 | 260.6 | 6.8 | 29 | 37.4 | 33.6 | 42 | 34.2 | 43.7 | 55 | 51.5 | 54.8 | 40.9 | 201.4 | 155.4 | 28.4 | 309.3 | 217.9 | 239.6 | 252.7 | 298.9 | 244.4 | 219.1 | 249.8
1962.1 | 1799.1 | -6.5 | 0 | 0 | 236.4 | 260 | 211.3 | 209.6 | 196.1 | 44.2 | 19 | 72.8 | 4 | 254.9 | 6.9 | 29.3 | 37.6 | 33.9 | 42.1 | 34.2 | 43.8 | 55.2 | 51 | 54.7 | 41 | 200.1 | 154.5 | 28.4 | 309 | 217.6 | 239.3 | 252.4 | 298.6 | 244.2 | 218.9 | 249.5
1963.1 | 1800.1 | -6.5 | 0 | 0 | 236.2 | 259.3 | 210.9 | 209.3 | 195.9 | 44.1 | 19 | 72.8 | 3.9 | 226.8 | 7.2 | 29.5 | 37.1 | 34.1 | 42.1 | 34.3 | 43.9 | 55.1 | 50.6 | 54.8 | 41.1 | 198.5 | 153.3 | 28.4 | 308.7 | 217.4 | 239 | 252.1 | 298.3 | 244 | 218.6 | 249.2
1964.1 | 1801.1 | -6.4 | 0 | 0 | 235.9 | 258.8 | 210.6 | 209 | 195.6 | 44.1 | 19 | 72.7 | 4.3 | 253.3 | 7.6 | 29.3 | 37.1 | 34.4 | 42.2 | 34.3 | 44 | 54.9 | 50.3 | 54.8 | 41.2 | 197.3 | 153.7 | 28.3 | 308.3 | 217.2 | 238.7 | 251.8 | 298.1 | 243.6 | 218.3 | 248.9
1965.1 | 1802.1 | -6.4 | 0 | 0 | 235.4 | 258.7 | 210.4 | 208.8 | 195.4 | 44 | 19 | 72.5 | 4.4 | 246 | 7.9 | 29.2 | 36.4 | 34.5 | 42.2 | 34.3 | 44.1 | 55 | 49.9 | 54.7 | 41.3 | 196.9 | 152.9 | 28.2 | 308 | 216.9 | 238.5 | 251.4 | 297.8 | 243.4 | 218.1 | 248.6
1966.1 | 1803.1 | -6.1 | 0 | 0 | 234.8 | 258.1 | 210.3 | 208.5 | 195 | 43.8 | 19 | 72.4 | 4 | 253.3 | 7.8 | 29 | 36.8 | 34.3 | 42.3 | 34.3 | 44.2 | 55 | 49.3 | 54.7 | 41.4 | 195.6 | 151.1 | 28.1 | 307.6 | 216.7 | 238.3 | 251.1 | 297.5 | 243.2 | 217.8 | 248.4
1967.1 | 1804.1 | -4.5 | 0 | 0 | 234.3 | 258.2 | 210 | 208.3 | 194.4 | 43.8 | 19 | 72.3 | 3.9 | 238.1 | 7.3 | 28.6 | 37 | 34.2 | 42.3 | 34.3 | 44.3 | 54.9 | 49 | 54.7 | 41.4 | 194.5 | 149.6 | 27.9 | 307.3 | 216.4 | 238 | 250.8 | 297.2 | 243 | 217.4 | 248.1
1968.1 | 1805.1 | -3.9 | 0 | 0 | 233.6 | 258.9 | 209.8 | 208.1 | 193.8 | 43.7 | 19 | 72.3 | 3.8 | 242.8 | 7.3 | 28.3 | 36.6 | 33.9 | 42.3 | 34.3 | 44.4 | 54.8 | 48.9 | 54.8 | 41.5 | 194 | 146.6 | 27.7 | 306.9 | 216.2 | 237.7 | 250.5 | 296.9 | 242.8 | 217.1 | 247.8
1969.1 | 1806.1 | -5.6 | 0 | 0 | 233.4 | 259.6 | 209.6 | 207.9 | 193.2 | 43.6 | 19 | 72.2 | 4 | 243.9 | 8.3 | 28.2 | 36 | 33.7 | 42.4 | 34.4 | 44.5 | 54.9 | 49.1 | 54.9 | 41.6 | 193.4 | 144.6 | 27.6 | 306.6 | 215.9 | 237.5 | 250.2 | 296.7 | 242.5 | 216.9 | 247.5
1970.1 | 1807.1 | -6 | 0 | 0 | 233.1 | 258.8 | 209.4 | 207.6 | 192.7 | 43.5 | 19 | 72 | 3.9 | 245.4 | 9 | 28.2 | 36.2 | 33.4 | 42.4 | 34.5 | 44.6 | 54.7 | 49.1 | 54.9 | 41.7 | 192.8 | 143.4 | 27.6 | 306.3 | 215.5 | 237.2 | 249.9 | 296.4 | 242.2 | 216.6 | 247.3
1971.1 | 1808.1 | -6.1 | 0 | 0 | 232.4 | 257.1 | 209.1 | 207.5 | 192.3 | 43.5 | 19 | 71.9 | 4 | 242.9 | 8.7 | 28 | 35.6 | 33.3 | 42.5 | 34.5 | 44.8 | 54.4 | 48.9 | 54.9 | 41.8 | 190.7 | 140.2 | 27.5 | 305.9 | 215.2 | 236.9 | 249.6 | 296.1 | 242 | 216.3 | 247
1972.1 | 1809.1 | -6.5 | 0 | 0 | 231.9 | 255.9 | 208.5 | 207.3 | 191.9 | 43.5 | 19 | 71.8 | 4 | 236.6 | 8.4 | 27.8 | 35.2 | 33.2 | 42.5 | 34.5 | 44.9 | 54.7 | 49 | 54.9 | 41.9 | 189.5 | 139.2 | 27.4 | 305.6 | 214.8 | 236.7 | 249.3 | 295.8 | 241.7 | 216 | 246.7
1973.1 | 1810.1 | -6.7 | 0 | 0 | 231.5 | 254.9 | 208.2 | 207 | 191.6 | 43.5 | 19 | 71.7 | 3.4 | 236.1 | 8.3 | 27.6 | 34.7 | 33.1 | 42.5 | 34.5 | 45 | 54.7 | 49.3 | 55 | 41.9 | 188.9 | 138.9 | 27.3 | 305.3 | 214.4 | 236.4 | 248.9 | 295.6 | 241.4 | 215.8 | 246.4
1974.1 | 1811.1 | -6.7 | 0 | 0 | 231.2 | 254.8 | 208 | 206.8 | 191.1 | 43.5 | 19 | 71.6 | 3.2 | 244.9 | 7.6 | 27.5 | 34.5 | 33 | 42.6 | 34.5 | 45.1 | 55.1 | 49.3 | 55 | 42 | 187.6 | 136.8 | 27.1 | 304.9 | 214.1 | 236.1 | 248.6 | 295.3 | 241.1 | 215.6 | 246.1
1975.1 | 1812.1 | -6.7 | 0 | 0 | 230.9 | 253.8 | 207.8 | 206.4 | 190.7 | 43.5 | 19 | 71.5 | 3.4 | 238.2 | 7.6 | 27.7 | 34.5 | 32.9 | 42.6 | 34.4 | 45.2 | 55.5 | 49.5 | 55.1 | 42.1 | 187.7 | 135.2 | 27 | 304.6 | 213.9 | 235.8 | 248.4 | 295 | 241 | 215.4 | 245.9
1976.1 | 1813.1 | -6.5 | 0 | 0 | 230.6 | 253 | 207.6 | 206.1 | 190.3 | 43.5 | 19 | 71.4 | 3.2 | 240.6 | 7.8 | 27.8 | 34.3 | 32.9 | 42.6 | 34.4 | 45.3 | 55.6 | 49.3 | 55.1 | 42.2 | 188 | 132.1 | 26.9 | 304.3 | 213.6 | 235.5 | 248.1 | 294.7 | 240.8 | 215 | 245.6
1977.1 | 1814.1 | -6.5 | 0 | 0 | 230.3 | 252.6 | 207.4 | 205.7 | 189.8 | 43.4 | 19 | 71.3 | 3.3 | 239.8 | 7.4 | 27.9 | 34.5 | 32.8 | 42.7 | 34.3 | 45.3 | 55.6 | 48.2 | 55.2 | 42.3 | 188.7 | 131.5 | 26.8 | 303.9 | 213.3 | 235.3 | 247.8 | 294.4 | 240.5 | 214.7 | 245.3
1978.1 | 1815.1 | -6.5 | 0 | 0 | 229.9 | 251.7 | 207 | 205.4 | 189.5 | 43.4 | 19.1 | 71.2 | 2.8 | 240.2 | 6.8 | 28 | 33.8 | 32.7 | 42.7 | 34.3 | 45.4 | 55.6 | 49.1 | 55.3 | 42.4 | 187.4 | 129.8 | 26.7 | 303.6 | 213 | 235.1 | 247.5 | 294.2 | 240 | 214.4 | 245
1979.1 | 1816.1 | -6.5 | 0 | 0 | 229.5 | 250.5 | 206.7 | 205 | 189.4 | 43.4 | 19.1 | 71.1 | 2.9 | 235.6 | 6.4 | 28.1 | 33.6 | 32.6 | 42.8 | 34.4 | 45.5 | 55.7 | 50 | 55.4 | 42.5 | 184.8 | 126.4 | 26.6 | 303.3 | 212.8 | 234.8 | 247.2 | 293.9 | 239.5 | 214 | 244.8
1980.1 | 1817.1 | -5.6 | 0 | 0 | 229 | 249.8 | 206.6 | 204.7 | 189.4 | 43.4 | 19.1 | 71 | 2.9 | 241.6 | 5.9 | 27.9 | 33.4 | 32.4 | 42.8 | 34.4 | 45.5 | 56 | 51.4 | 55.5 | 42.6 | 184.7 | 126 | 26.5 | 302.9 | 212.5 | 234.4 | 246.8 | 293.6 | 239 | 213.7 | 244.5
1981.1 | 1818.1 | -5.6 | 0 | 0 | 228.4 | 249.2 | 206.4 | 204.5 | 189.4 | 43.4 | 19.1 | 70.9 | 3 | 260.1 | 5.4 | 27.7 | 33.6 | 32.3 | 42.8 | 34.4 | 45.6 | 56.2 | 51.1 | 55.5 | 42.7 | 184.4 | 125.6 | 26.5 | 302.6 | 212.2 | 234.2 | 246.5 | 293.3 | 238.6 | 213.5 | 244.2
1982.1 | 1819.1 | -5.8 | 0 | 0 | 228 | 249.1 | 206.2 | 204.1 | 189.2 | 43.4 | 19.1 | 70.9 | 3.2 | 257.9 | 4.9 | 27.7 | 34 | 32.2 | 42.9 | 34.5 | 45.7 | 56.3 | 50.2 | 55.5 | 42.8 | 184.1 | 123.7 | 26.8 | 302.3 | 211.9 | 233.9 | 246.2 | 293 | 238.4 | 213.2 | 243.9
1983.1 | 1820.1 | -6.2 | 0 | 0 | 227.9 | 248.7 | 206 | 203.9 | 188.9 | 43.5 | 19.1 | 70.9 | 3.4 | 258.5 | 4.5 | 28.4 | 34 | 32.2 | 42.9 | 34.5 | 45.7 | 56.3 | 49.9 | 55.6 | 42.8 | 184 | 123.4 | 26.8 | 302 | 211.7 | 233.5 | 245.9 | 292.7 | 238.1 | 213 | 243.6
1984.1 | 1821.1 | -6 | 0 | 0 | 227.6 | 248.2 | 205.7 | 203.6 | 188.7 | 43.5 | 19.1 | 70.8 | 3.1 | 263.8 | 4.1 | 29.2 | 34 | 32.3 | 43 | 34.5 | 45.8 | 56.4 | 49.6 | 55.6 | 42.9 | 183.7 | 124.1 | 26.7 | 301.6 | 211.5 | 233.2 | 245.6 | 292.5 | 237.7 | 212.7 | 243.4
1985.1 | 1822.1 | -5.2 | 0 | 0 | 227.2 | 248.3 | 205.3 | 203.3 | 188.5 | 43.6 | 19.1 | 70.8 | 3.1 | 254.3 | 3.8 | 29.5 | 34 | 32.4 | 43 | 34.5 | 45.9 | 56.5 | 49.3 | 55.6 | 42.9 | 183.4 | 122.3 | 26.7 | 301.3 | 211.2 | 232.9 | 245.3 | 292.2 | 237.5 | 212.5 | 243.1
1986.1 | 1823.1 | -5.2 | 0 | 0 | 226.9 | 247.8 | 205 | 202.9 | 188.2 | 43.6 | 19.1 | 70.7 | 3.3 | 242.6 | 3.8 | 29.3 | 34.8 | 32.4 | 43 | 34.5 | 46 | 56.8 | 49.9 | 55.6 | 43 | 184.3 | 121.5 | 26.7 | 301 | 210.9 | 232.6 | 245 | 291.9 | 237.4 | 212.3 | 242.8
1987.1 | 1824.1 | -5.2 | 0 | 0 | 226.5 | 247.8 | 204.7 | 202.5 | 187.8 | 43.7 | 19.1 | 70.7 | 3.1 | 248.4 | 4 | 29.1 | 34.7 | 32.5 | 43.1 | 34.5 | 46.1 | 57.2 | 50 | 55.7 | 43.1 | 184.7 | 121.9 | 26.6 | 300.7 | 210.6 | 232.2 | 244.7 | 291.6 | 237.1 | 211.9 | 242.5
1988.1 | 1825.1 | -5.6 | 0 | 0 | 226 | 247.4 | 204.6 | 202.2 | 187.6 | 43.6 | 19.1 | 70.6 | 3.4 | 261.5 | 4.2 | 28.8 | 34.9 | 32.5 | 43.1 | 34.5 | 46.2 | 57.5 | 49.1 | 55.7 | 43.2 | 184 | 119.8 | 26.6 | 300.3 | 210.3 | 231.9 | 244.5 | 291.4 | 236.7 | 211.6 | 242.3
1989.1 | 1826.1 | -6 | 0 | 0 | 225.1 | 247.7 | 204.4 | 201.9 | 187.4 | 43.6 | 19.1 | 70.6 | 3.3 | 254.9 | 4.1 | 28.5 | 35.2 | 32.5 | 43.1 | 34.6 | 46.2 | 57.5 | 48.7 | 55.7 | 43.2 | 183.6 | 116.5 | 26.5 | 300 | 209.8 | 231.6 | 244.2 | 291.1 | 236.3 | 211.4 | 242
1990.1 | 1827.1 | -5.3 | 0 | 0 | 224.5 | 247.3 | 204.1 | 201.7 | 187.2 | 43.5 | 19.1 | 70.5 | 3.4 | 258 | 3.8 | 28.4 | 34.9 | 32.3 | 43.1 | 34.5 | 46.3 | 57.6 | 48.5 | 55.7 | 43.3 | 184.7 | 113.5 | 26.5 | 299.7 | 209.5 | 231.3 | 243.8 | 290.8 | 235.8 | 211 | 241.7
1991.1 | 1828.1 | -5.8 | 0 | 0 | 224.1 | 246.6 | 203.8 | 201.5 | 186.9 | 43.5 | 19.1 | 70.4 | 3.4 | 274.3 | 3.6 | 28.4 | 35.2 | 32.1 | 43.2 | 34.6 | 46.3 | 57.9 | 47.6 | 55.7 | 43.3 | 185.2 | 112.6 | 26.4 | 299.4 | 209.2 | 231.1 | 243.5 | 290.5 | 235.5 | 210.8 | 241.4
1992.1 | 1829.1 | -6.2 | 0 | 0 | 223.9 | 246 | 203.6 | 201.3 | 186.7 | 43.5 | 19.1 | 70.3 | 3.4 | 261.4 | 4.2 | 28.3 | 35.6 | 32 | 43.2 | 34.6 | 46.4 | 58.2 | 47.1 | 55.8 | 43.4 | 187.9 | 111.8 | 26.4 | 299.1 | 208.8 | 230.9 | 243.2 | 290.2 | 235.3 | 210.4 | 241.1
1993.1 | 1830.1 | -5.7 | 0 | 0 | 223.6 | 245.8 | 203.4 | 201.1 | 186.5 | 43.5 | 19.1 | 70.3 | 3.3 | 253.6 | 4.6 | 28.2 | 35.6 | 32 | 43.2 | 34.6 | 46.5 | 58.2 | 47.5 | 55.8 | 43.4 | 187.4 | 111.3 | 26.5 | 298.8 | 208.4 | 230.7 | 243 | 290 | 235 | 210.2 | 240.9
1994.1 | 1831.1 | -5.3 | 0 | 0 | 223 | 245.1 | 203 | 200.9 | 186.2 | 43.4 | 19.1 | 70.2 | 3.2 | 280.3 | 4.6 | 27.9 | 35 | 32 | 43.3 | 34.6 | 46.5 | 58.5 | 47.2 | 55.8 | 43.5 | 189.3 | 111.6 | 26.3 | 298.5 | 208.1 | 230.4 | 242.7 | 289.7 | 234.8 | 210 | 240.6
1995.1 | 1832.1 | -5.4 | 0 | 0 | 222.4 | 244.1 | 202.7 | 200.6 | 185.9 | 43.5 | 19.1 | 70.2 | 3.5 | 279.8 | 4.7 | 27.8 | 35.2 | 32 | 43.3 | 34.5 | 46.6 | 58.9 | 47.2 | 55.9 | 43.6 | 193.7 | 109.2 | 26.2 | 298.1 | 207.7 | 230 | 242.4 | 289.4 | 234.7 | 209.8 | 240.3
1996.1 | 1833.1 | -5.5 | 0 | 0 | 221.8 | 243.3 | 202.5 | 200.3 | 185.6 | 43.4 | 19.1 | 70.2 | 3.1 | 266.5 | 4.9 | 27.7 | 35 | 32 | 43.3 | 34.5 | 46.7 | 59.1 | 46.8 | 55.9 | 43.7 | 193 | 107.3 | 26.2 | 297.8 | 207.3 | 229.7 | 242.1 | 289.2 | 234.5 | 209.6 | 240.1
1997.1 | 1834.1 | -4.9 | 0 | 0 | 221.2 | 242.8 | 202.3 | 200 | 185.3 | 43.3 | 19.1 | 70.1 | 3.4 | 265.8 | 5.3 | 28.1 | 34.9 | 32 | 43.3 | 34.6 | 46.7 | 59.3 | 46.7 | 55.9 | 43.8 | 194.2 | 107.4 | 26.2 | 297.5 | 207 | 229.3 | 241.8 | 288.9 | 234.1 | 209.3 | 239.8
1998.1 | 1835.1 | -4.8 | 0 | 0 | 220.6 | 242 | 202 | 199.8 | 185.1 | 43.2 | 19.1 | 70 | 3.2 | 270.4 | 5.4 | 28 | 34.4 | 32 | 43.4 | 34.5 | 46.8 | 59.6 | 47.2 | 55.9 | 43.8 | 193.2 | 107.2 | 26.2 | 297.2 | 206.7 | 229 | 241.6 | 288.6 | 233.8 | 208.9 | 239.5
1999.1 | 1836.1 | -5.4 | 0 | 0 | 220.5 | 241.6 | 201.2 | 199.5 | 184.9 | 43.1 | 19.1 | 70 | 3.1 | 272.3 | 5.4 | 27.9 | 34.7 | 32.1 | 43.4 | 34.5 | 46.9 | 59.9 | 46.8 | 56 | 43.9 | 194 | 105.5 | 26.2 | 296.9 | 206.3 | 228.8 | 241.2 | 288.4 | 233.6 | 208.7 | 239.2
2000.1 | 1837.1 | -5.8 | 0 | 0 | 220.2 | 240.6 | 200.3 | 199 | 184.6 | 42.9 | 19.1 | 70 | 3.2 | 275.1 | 5 | 27.7 | 35.2 | 32.1 | 43.4 | 34.4 | 46.9 | 60.1 | 46.8 | 56 | 43.9 | 193.9 | 103.5 | 26.1 | 296.6 | 205.8 | 228.5 | 240.9 | 288.1 | 233.2 | 208.3 | 239
2001.1 | 1838.1 | -5.6 | 0 | 0 | 219.8 | 240.6 | 200 | 198.7 | 184.4 | 42.8 | 19.1 | 69.9 | 3.2 | 272.1 | 4.4 | 27.6 | 35.1 | 32.1 | 43.4 | 34.4 | 47 | 60.3 | 47.8 | 56 | 44 | 194.2 | 102.4 | 26.1 | 296.3 | 205.5 | 228.2 | 240.7 | 287.8 | 232.7 | 208 | 238.7
2002.1 | 1839.1 | -5.4 | 0 | 0 | 219.6 | 240.4 | 200 | 198.4 | 184.1 | 42.7 | 19.1 | 69.8 | 3.4 | 267.8 | 3.9 | 27.6 | 35.1 | 32.1 | 43.5 | 34.4 | 47.1 | 60.6 | 48 | 56 | 44 | 194.8 | 100.1 | 26.2 | 296 | 205.2 | 227.9 | 240.4 | 287.5 | 232.3 | 207.7 | 238.4
2003.1 | 1840.1 | -4.7 | 0 | 0 | 219.2 | 239.3 | 199.9 | 198.1 | 183.6 | 42.7 | 19.1 | 69.8 | 3.3 | 248.9 | 3.6 | 27.6 | 34.9 | 32.1 | 43.5 | 34.4 | 47.1 | 60.9 | 48.5 | 56.1 | 44.1 | 191.7 | 96 | 26.1 | 295.7 | 204.9 | 227.6 | 240.1 | 287.2 | 232 | 207.5 | 238.1
2004.1 | 1841.1 | -5.5 | 0 | 0 | 218.9 | 237.8 | 199.8 | 197.7 | 183.4 | 42.6 | 19.1 | 69.8 | 3.4 | 231.2 | 3.7 | 27.8 | 35.2 | 32.2 | 43.5 | 34.5 | 47.2 | 61.2 | 48.8 | 56.1 | 44.2 | 190.9 | 93.7 | 26 | 295.4 | 204.6 | 227.3 | 239.8 | 287 | 231.6 | 207.2 | 237.9
2005.1 | 1842.1 | -5.8 | 0 | 0 | 218.5 | 237 | 199.7 | 197.4 | 183 | 42.6 | 19.1 | 69.7 | 3.3 | 226.1 | 3.7 | 27.7 | 34.9 | 32.3 | 43.6 | 34.5 | 47.2 | 61.4 | 48.4 | 56.1 | 44.3 | 187.3 | 89.4 | 25.9 | 295.1 | 204.3 | 226.9 | 239.5 | 286.7 | 231.2 | 206.8 | 237.6
2006.1 | 1843.1 | -5.1 | 0 | 0 | 218.1 | 235.6 | 199.5 | 197.2 | 182.8 | 42.5 | 19.1 | 69.7 | 3.1 | 229.1 | 3.5 | 27.5 | 35.2 | 32.4 | 43.6 | 34.5 | 47.3 | 61.5 | 48.1 | 56.2 | 44.3 | 186 | 86.6 | 25.8 | 294.8 | 204 | 226.5 | 239.3 | 286.4 | 230.9 | 206.5 | 237.3
2007.1 | 1844.1 | -4.5 | 0 | 0 | 217.5 | 234.5 | 199.3 | 196.8 | 182.4 | 42.4 | 19.1 | 69.7 | 3.1 | 249.6 | 3.2 | 27.4 | 35.7 | 32.5 | 43.6 | 34.4 | 47.4 | 61.5 | 47.9 | 56.2 | 44.3 | 187.6 | 87.2 | 25.8 | 294.5 | 203.7 | 226.2 | 239 | 286.1 | 230.7 | 206.2 | 237.1
2008.1 | 1845.1 | -4.6 | 0 | 0 | 217.5 | 233.2 | 199 | 196.4 | 182 | 42.4 | 19.1 | 69.6 | 3 | 276.9 | 3.3 | 27.3 | 35.5 | 32.5 | 43.6 | 34.4 | 47.4 | 61.7 | 47 | 56.1 | 44.4 | 189.6 | 87.2 | 25.7 | 294.2 | 203.5 | 225.9 | 238.7 | 285.8 | 230.5 | 205.8 | 236.8
2009.1 | 1846.1 | -5.6 | 0 | 0 | 217.3 | 231.9 | 198.5 | 195.9 | 181.8 | 42.3 | 19.1 | 69.5 | 3 | 276.7 | 3.4 | 27.4 | 34.9 | 32.3 | 43.7 | 34.4 | 47.5 | 62.1 | 46.5 | 56.1 | 44.5 | 191 | 85.7 | 25.7 | 293.9 | 203.3 | 225.6 | 238.4 | 285.5 | 230 | 205.6 | 236.5
2010.1 | 1847.1 | -5.5 | 0 | 0 | 216.9 | 230.7 | 198.2 | 195.6 | 181.6 | 42.3 | 19.1 | 69.4 | 3 | 274.7 | 3.5 | 27.3 | 34.8 | 32.1 | 43.7 | 34.4 | 47.5 | 62.5 | 46.3 | 56.1 | 44.5 | 190 | 83.9 | 25.7 | 293.5 | 202.9 | 225.2 | 238.2 | 285.2 | 229.7 | 205.2 | 236.3
2011.1 | 1848.1 | -4.9 | 0 | 0 | 216.6 | 230.1 | 197.8 | 195.2 | 181.5 | 42.2 | 19.1 | 69.3 | 3.1 | 274.6 | 4 | 27.4 | 34.2 | 31.9 | 43.7 | 34.4 | 47.6 | 62.9 | 46 | 56 | 44.6 | 188.4 | 82.5 | 25.6 | 293.2 | 202.6 | 224.8 | 237.9 | 285 | 229.2 | 204.9 | 236
2012.1 | 1849.1 | -4.4 | 0 | 0 | 216.2 | 229.1 | 197.4 | 194.8 | 181.1 | 42.1 | 19.1 | 69.2 | 3.3 | 293.3 | 4.8 | 28 | 34.5 | 31.7 | 43.7 | 34.4 | 47.7 | 63.4 | 45.9 | 56 | 44.6 | 188.4 | 81.6 | 25.6 | 292.9 | 202.3 | 224.4 | 237.6 | 284.7 | 228.7 | 204.5 | 235.7
2013.1 | 1850.1 | -4.1 | 0 | 0 | 216 | 228.3 | 197 | 194.3 | 180.7 | 42.1 | 19.1 | 69.1 | 3.3 | 286.1 | 5.2 | 28.4 | 34.6 | 31.5 | 43.8 | 34.4 | 47.7 | 63.7 | 45.8 | 56 | 44.7 | 187.1 | 80.8 | 25.6 | 292.6 | 202 | 224.1 | 237.4 | 284.4 | 228.4 | 204.3 | 235.5
2014.1 | 1851.1 | -5 | 0 | 0 | 215.6 | 227.8 | 196.7 | 194 | 180.3 | 42 | 19.1 | 69.1 | 3.2 | 280.7 | 5.1 | 28.3 | 34 | 31.5 | 43.8 | 34.5 | 47.8 | 64.2 | 45.8 | 56.1 | 44.7 | 186.9 | 81.9 | 25.5 | 292.3 | 201.6 | 223.7 | 237.1 | 284.1 | 228.1 | 204 | 235.2
2015.1 | 1852.1 | -5.4 | 0 | 0 | 215.1 | 227.8 | 196.1 | 193.8 | 179.9 | 41.9 | 19.2 | 69 | 3.4 | 285 | 4.9 | 28.1 | 33.8 | 31.4 | 43.8 | 34.5 | 47.9 | 64.7 | 45.9 | 56.1 | 44.8 | 185.8 | 81 | 25.5 | 292 | 201.2 | 223.4 | 236.8 | 283.8 | 227.6 | 203.6 | 235
2016.1 | 1853.1 | -5.2 | 0 | 0 | 214.9 | 228 | 195.8 | 193.5 | 179.9 | 41.8 | 19.2 | 68.9 | 3.1 | 274.4 | 4.9 | 28 | 33.3 | 31.3 | 43.8 | 34.5 | 47.9 | 65.5 | 45.4 | 56.1 | 44.8 | 189.5 | 80.1 | 25.4 | 291.7 | 200.8 | 223.1 | 236.5 | 283.5 | 227.1 | 203.3 | 234.7
2017.1 | 1854.1 | -5.6 | 0 | 0 | 214.5 | 227.2 | 195.6 | 193.1 | 179.8 | 41.8 | 19.2 | 68.9 | 3.3 | 277.3 | 4.6 | 27.8 | 33.6 | 31.3 | 43.9 | 34.6 | 48 | 66.4 | 45.1 | 56.1 | 44.9 | 188.2 | 78.7 | 25.4 | 291.4 | 200.4 | 222.7 | 236.3 | 283.2 | 226.7 | 203 | 234.4
2018.1 | 1855.1 | -5.1 | 0 | 0 | 214.2 | 226.4 | 195.3 | 192.9 | 179.3 | 41.7 | 19.2 | 68.8 | 3.3 | 275.7 | 3.9 | 27.6 | 33.7 | 31.3 | 43.9 | 34.6 | 48 | 67 | 45.1 | 56.1 | 45 | 185.7 | 77.6 | 25.4 | 291.1 | 200.1 | 222.4 | 236 | 283 | 226.4 | 202.8 | 234.2
2019.1 | 1856.1 | -4.5 | 0 | 0 | 214.1 | 225.3 | 194.9 | 192.8 | 178.8 | 41.7 | 19.2 | 68.8 | 3.2 | 247 | 3.3 | 27.4 | 34.2 | 31.2 | 43.9 | 34.6 | 48.1 | 67.6 | 45.4 | 56.1 | 45 | 185.5 | 77.5 | 25.4 | 290.8 | 199.8 | 222.1 | 235.7 | 282.7 | 226 | 202.5 | 233.9
2020.1 | 1857.1 | -5.5 | 0 | 0 | 214 | 224.7 | 194.4 | 192.5 | 178.5 | 41.7 | 19.2 | 68.7 | 3.2 | 217.8 | 2.9 | 27.7 | 34 | 31.1 | 43.9 | 34.6 | 48.1 | 68.5 | 45.6 | 56.2 | 45.1 | 184.7 | 76.1 | 25.4 | 290.5 | 199.5 | 221.8 | 235.4 | 282.4 | 225.7 | 202.1 | 233.6
2021.1 | 1858.1 | -4.1 | 0 | 0 | 214.1 | 223.8 | 193.9 | 192.1 | 178.1 | 41.8 | 19.2 | 68.7 | 3.5 | 211.4 | 2.6 | 27.5 | 34.3 | 31.1 | 44 | 34.6 | 48.2 | 69.4 | 45.4 | 56.2 | 45.1 | 183.3 | 74.9 | 25.4 | 290.2 | 199.1 | 221.6 | 235.1 | 282.1 | 225.2 | 201.7 | 233.4
2022.1 | 1859.1 | -3.6 | 0 | 0 | 213.9 | 223.3 | 193.3 | 191.9 | 177.7 | 41.8 | 19.2 | 68.6 | 3.2 | 221.7 | 2.5 | 27.7 | 34.6 | 31 | 44 | 34.6 | 48.2 | 70.3 | 45.1 | 56.2 | 45.1 | 183.7 | 74.7 | 25.4 | 289.9 | 198.8 | 221.3 | 234.8 | 281.8 | 224.6 | 201.2 | 233.1
2023.1 | 1860.1 | -4.5 | 0 | 0 | 213.8 | 222.8 | 192.8 | 191.6 | 177.5 | 41.7 | 19.2 | 68.6 | 3.2 | 232.6 | 2.8 | 27.8 | 35.1 | 31 | 44 | 34.6 | 48.3 | 71.1 | 45.3 | 56.2 | 45.2 | 182.1 | 73.4 | 25.4 | 289.6 | 198.5 | 221 | 234.5 | 281.5 | 224 | 200.7 | 232.8
2024.1 | 1861.1 | -5.1 | 0 | 0 | 213.6 | 222.4 | 192.5 | 191.4 | 177.2 | 41.7 | 19.2 | 68.5 | 3.4 | 252.4 | 3.4 | 27.8 | 34.7 | 31.1 | 44 | 34.6 | 48.3 | 72 | 45.6 | 56.2 | 45.2 | 182.4 | 72.5 | 25.5 | 289.3 | 198.2 | 220.6 | 234.3 | 281.3 | 223.5 | 200.4 | 232.6
2025.1 | 1862.1 | -5.8 | 0 | 0 | 213.4 | 221.7 | 192.1 | 191 | 176.9 | 41.6 | 19.2 | 68.5 | 3.4 | 273.1 | 4.1 | 28.1 | 34.4 | 31.2 | 44 | 34.6 | 48.4 | 73.2 | 45.5 | 56.3 | 45.3 | 181.7 | 71.6 | 25.5 | 289 | 197.9 | 220.2 | 234 | 281 | 223.2 | 200.2 | 232.3
2026.1 | 1863.1 | -6.1 | 0 | 0 | 213 | 221.1 | 191.7 | 190.4 | 176.6 | 41.6 | 19.2 | 68.4 | 3.7 | 263.1 | 4.3 | 28 | 35.4 | 31.2 | 44.1 | 34.7 | 48.4 | 74.3 | 45.4 | 56.3 | 45.4 | 180.3 | 71.1 | 25.5 | 288.7 | 197.6 | 219.9 | 233.7 | 280.7 | 222.9 | 199.9 | 232
2027.1 | 1864.1 | -6.1 | 0 | 0 | 212.6 | 220.6 | 191.1 | 190 | 176.3 | 41.5 | 19.2 | 68.4 | 3.5 | 244.5 | 4.1 | 27.8 | 35.5 | 31.3 | 44.1 | 34.6 | 48.5 | 75.5 | 45.7 | 56.3 | 45.5 | 179.8 | 70.2 | 25.5 | 288.3 | 197.3 | 219.5 | 233.4 | 280.4 | 222.4 | 199.5 | 231.8
2028.1 | 1865.1 | -5.5 | 0 | 0 | 212 | 220.3 | 190.6 | 189.7 | 176.1 | 41.4 | 19.2 | 68.4 | 3.3 | 237.6 | 3.9 | 27.9 | 35.4 | 31.4 | 44.1 | 34.6 | 48.5 | 76.8 | 45.5 | 56.3 | 45.5 | 177.4 | 68.9 | 25.5 | 288 | 197 | 219.2 | 233.1 | 280.1 | 221.9 | 199.3 | 231.5
2029.1 | 1866.1 | -5.8 | 0 | 0 | 211.5 | 219.8 | 190.1 | 189.5 | 175.9 | 41.4 | 19.2 | 68.3 | 3.2 | 236.9 | 3.6 | 27.8 | 35.5 | 31.3 | 44.1 | 34.6 | 48.3 | 78.1 | 45.5 | 56.4 | 45.5 | 177.4 | 68.3 | 25.4 | 287.7 | 196.7 | 218.9 | 232.9 | 279.8 | 221.4 | 199 | 231.3
2030.1 | 1867.1 | -5.7 | 0 | 0 | 211.6 | 219.3 | 189.8 | 189.2 | 175.5 | 41.4 | 19.2 | 68.3 | 3.4 | 233.7 | 3.2 | 27.7 | 35.4 | 31.3 | 44.1 | 34.6 | 48.3 | 79.4 | 45.5 | 56.4 | 45.5 | 176.2 | 67.6 | 25.3 | 287.4 | 196.4 | 218.7 | 232.6 | 279.5 | 220.9 | 198.6 | 231
2031.1 | 1868.1 | -5.8 | 0 | 0 | 211.4 | 218.2 | 189.4 | 189 | 175.1 | 41.3 | 19.2 | 68.2 | 3.6 | 219.4 | 2.9 | 28 | 34.7 | 31.2 | 44.2 | 34.6 | 48.4 | 80.9 | 45.1 | 56.4 | 45.6 | 176.6 | 66.8 | 25.4 | 287.1 | 196.1 | 218.5 | 232.3 | 279.2 | 220.5 | 198.3 | 230.7
2032.1 | 1869.1 | -6.3 | 0 | 0 | 211.1 | 217.5 | 189 | 188.8 | 174.8 | 41.3 | 19.2 | 68.2 | 3.6 | 202.9 | 3 | 28.1 | 34.5 | 31.2 | 44.2 | 34.6 | 48.5 | 82.3 | 45.1 | 56.4 | 45.6 | 172.4 | 65.6 | 25.4 | 286.8 | 195.8 | 218.3 | 232 | 279 | 220 | 198.1 | 230.5
2033.1 | 1870.1 | -6.5 | 0 | 0 | 210.8 | 217 | 188.5 | 188.5 | 174.5 | 41.3 | 19.2 | 68.1 | 3.8 | 203 | 3.1 | 28 | 34.5 | 31.1 | 44.2 | 34.6 | 48.6 | 83.6 | 45 | 56.4 | 45.7 | 167.9 | 64 | 25.5 | 286.5 | 195.6 | 218 | 231.7 | 278.7 | 219.5 | 197.7 | 230.2
2034.1 | 1871.1 | -6.5 | 0 | 0 | 210.3 | 216.2 | 188.1 | 188 | 174.2 | 41.3 | 19.2 | 68.1 | 3.8 | 222.1 | 2.9 | 27.8 | 34.9 | 31.1 | 44.2 | 34.6 | 48.7 | 84.9 | 44.7 | 56.4 | 45.7 | 166.7 | 63.6 | 25.5 | 286.2 | 195.3 | 217.8 | 231.5 | 278.4 | 219 | 197.4 | 230
2035.1 | 1872.1 | -6.2 | 0 | 0 | 210.2 | 215.5 | 187.7 | 187.5 | 173.9 | 41.3 | 19.2 | 68 | 3.7 | 234.2 | 2.8 | 27.6 | 34.7 | 31.1 | 44.2 | 34.6 | 48.7 | 86.1 | 44.6 | 56.4 | 45.7 | 166.3 | 63.1 | 25.5 | 285.9 | 195.1 | 217.5 | 231.2 | 278.1 | 218.4 | 197.1 | 229.7
2036.1 | 1873.1 | -5.7 | 0 | 0 | 209.6 | 214.5 | 187.3 | 187 | 173.9 | 41.3 | 19.2 | 67.9 | 3.7 | 245.1 | 2.8 | 27.3 | 34.6 | 31.2 | 44.3 | 34.6 | 48.8 | 87.3 | 44.2 | 56.5 | 45.8 | 167.5 | 62.7 | 25.5 | 285.6 | 194.8 | 217.4 | 230.9 | 277.8 | 217.9 | 196.7 | 229.4
2037.1 | 1874.1 | -5.2 | 0 | 0 | 209.2 | 213.4 | 186.9 | 186.8 | 173.6 | 41.3 | 19.2 | 67.8 | 3.8 | 248.2 | 2.7 | 27.2 | 34 | 31.2 | 44.3 | 34.6 | 48.8 | 88.3 | 43.9 | 56.5 | 45.8 | 164.8 | 62 | 25.5 | 285.3 | 194.6 | 217.2 | 230.7 | 277.5 | 217.3 | 196.4 | 229.2
2038.1 | 1875.1 | -5.9 | 0 | 0 | 208.6 | 212.7 | 186.5 | 186.6 | 173.3 | 41.3 | 19.2 | 67.8 | 3.9 | 245.5 | 2.6 | 27.3 | 34.3 | 31.2 | 44.3 | 34.6 | 48.9 | 89.2 | 43.9 | 56.5 | 45.8 | 161.5 | 61.1 | 25.4 | 285 | 194.4 | 217 | 230.4 | 277.3 | 216.9 | 196.1 | 228.9
2039.1 | 1876.1 | -5.8 | 0 | 0 | 208.4 | 212 | 186.1 | 186.4 | 173 | 41.3 | 19.2 | 67.7 | 3.6 | 229.6 | 2.7 | 27.5 | 34.4 | 31.2 | 44.3 | 34.6 | 49 | 90.3 | 43.8 | 56.6 | 45.9 | 160 | 60.8 | 25.4 | 284.7 | 194.1 | 216.8 | 230.1 | 277 | 216.5 | 195.7 | 228.7
2040.1 | 1877.1 | -5.5 | 0 | 0 | 208.2 | 211.1 | 185.8 | 186.2 | 172.7 | 41.3 | 19.2 | 67.6 | 3.8 | 209.2 | 2.8 | 27.7 | 34.3 | 31.2 | 44.3 | 34.6 | 49 | 91.5 | 43.7 | 56.6 | 45.9 | 159.4 | 60 | 25.4 | 284.4 | 193.8 | 216.5 | 229.8 | 276.7 | 216 | 195.4 | 228.4
2041.1 | 1878.1 | -5.2 | 0 | 0 | 207.7 | 210.7 | 185.4 | 186 | 172.3 | 41.3 | 19.2 | 67.6 | 3.8 | 204.2 | 3.1 | 27.4 | 35.1 | 31.2 | 44.3 | 34.6 | 49.1 | 92.5 | 43.9 | 56.6 | 46 | 159.5 | 59.7 | 25.3 | 284.1 | 193.6 | 216.3 | 229.6 | 276.4 | 215.5 | 195.1 | 228.2
2042.1 | 1879.1 | -3.6 | 0 | 0 | 207.2 | 210 | 184.8 | 185.9 | 172 | 41.3 | 19.2 | 67.5 | 3.6 | 216.8 | 3 | 27.1 | 36 | 31.1 | 44.3 | 34.6 | 49.1 | 93.5 | 44.1 | 56.6 | 46.1 | 159 | 58.9 | 25.3 | 283.8 | 193.4 | 216.2 | 229.3 | 276.1 | 215 | 194.8 | 227.9
2043.1 | 1880.1 | -4.2 | 0 | 0 | 206.6 | 209.2 | 184.5 | 185.6 | 171.7 | 41.3 | 19.2 | 67.4 | 3.7 | 236.6 | 2.9 | 26.8 | 36.2 | 31 | 44.4 | 34.5 | 49.1 | 94.5 | 44.3 | 56.6 | 46.1 | 158 | 58.1 | 25.3 | 283.5 | 193.1 | 216 | 229 | 275.8 | 214.6 | 194.6 | 227.7
2044.1 | 1881.1 | -4.4 | 0 | 0 | 206 | 208.9 | 184.3 | 185 | 171.4 | 41.2 | 19.2 | 67.3 | 3.5 | 237.7 | 2.9 | 26.7 | 35.6 | 31 | 44.4 | 34.5 | 49.2 | 95.5 | 44.1 | 56.7 | 46.1 | 155.6 | 56.8 | 25.2 | 283.2 | 192.8 | 215.7 | 228.7 | 275.5 | 214.1 | 194.3 | 227.4
2045.1 | 1882.1 | -5.1 | 0 | 0 | 205.4 | 208.3 | 184 | 184.4 | 171 | 41.2 | 19.2 | 67.2 | 3.4 | 233.1 | 2.9 | 26.6 | 35.2 | 31 | 44.4 | 34.4 | 49.2 | 96.4 | 44.1 | 56.7 | 46.2 | 154.2 | 56 | 25.3 | 282.9 | 192.5 | 215.5 | 228.5 | 275.3 | 213.7 | 194 | 227.2
2046.1 | 1883.1 | -3.9 | 0 | 0 | 204.9 | 207.6 | 183.6 | 184 | 170.8 | 41.1 | 19.2 | 67.2 | 3.6 | 247.8 | 2.9 | 26.8 | 35.5 | 30.9 | 44.4 | 34.4 | 49.3 | 97.3 | 43.9 | 56.7 | 46.2 | 152.5 | 55.5 | 25.3 | 282.6 | 192.3 | 215.3 | 228.2 | 275 | 213.2 | 193.8 | 227
2047.1 | 1884.1 | -4.6 | 0 | 0 | 204.6 | 206.9 | 183.2 | 183.6 | 170.7 | 41 | 19.2 | 67.1 | 3.5 | 270.2 | 3.4 | 26.9 | 35.3 | 30.9 | 44.4 | 34.5 | 49.3 | 98.2 | 44.1 | 56.7 | 46.3 | 149.5 | 54.6 | 25.3 | 282.3 | 192 | 215 | 227.9 | 274.7 | 212.8 | 193.5 | 226.7
2048.1 | 1885.1 | -5.5 | 0 | 0 | 204.1 | 206.3 | 182.9 | 183.3 | 170.5 | 40.9 | 19.3 | 67.1 | 3.4 | 261.3 | 4 | 26.9 | 34.9 | 30.9 | 44.5 | 34.4 | 49.4 | 99.1 | 44 | 56.7 | 46.3 | 149.1 | 54.3 | 25.3 | 282 | 191.7 | 214.9 | 227.7 | 274.4 | 212.3 | 193.2 | 226.4
2049.1 | 1886.1 | -5.8 | 0 | 0 | 203.8 | 205.6 | 182.7 | 183.1 | 170.2 | 40.8 | 19.3 | 67.1 | 2.9 | 244.1 | 4.1 | 27 | 35.1 | 30.9 | 44.5 | 34.4 | 49.4 | 99.9 | 44.1 | 56.7 | 46.4 | 144.4 | 53.8 | 25.2 | 281.7 | 191.5 | 214.6 | 227.4 | 274.1 | 211.9 | 193 | 226.2
2050.1 | 1887.1 | -4.6 | 0 | 0 | 203.6 | 204.9 | 182.4 | 182.8 | 169.9 | 40.6 | 19.3 | 67.1 | 3.1 | 250.2 | 4.3 | 27.1 | 35.8 | 30.9 | 44.5 | 34.5 | 49.5 | 100.6 | 44 | 56.7 | 46.4 | 139.5 | 53.2 | 25.2 | 281.4 | 191.2 | 214.4 | 227.1 | 273.8 | 211.6 | 192.7 | 225.9
2051.1 | 1888.1 | -3.7 | 0 | 0 | 203.3 | 204.6 | 182 | 182.3 | 169.5 | 40.5 | 19.3 | 67 | 3.1 | 252.5 | 4.8 | 27.3 | 35.8 | 30.9 | 44.5 | 34.5 | 49.5 | 101.2 | 43.8 | 56.7 | 46.5 | 137.3 | 52.5 | 25.2 | 281.2 | 190.9 | 214.2 | 226.8 | 273.5 | 211.1 | 192.5 | 225.7
2052.1 | 1889.1 | -3.3 | 0 | 0 | 203 | 204.4 | 181.6 | 181.9 | 169.2 | 40.4 | 19.3 | 67 | 3.2 | 244 | 5 | 27.2 | 36.3 | 31 | 44.5 | 34.5 | 49.6 | 101.8 | 43.5 | 56.7 | 46.6 | 136.2 | 51.8 | 25.3 | 280.9 | 190.6 | 213.9 | 226.6 | 273.3 | 210.7 | 192.2 | 225.4
2053.1 | 1890.1 | -2.9 | 0 | 0 | 202.7 | 204.6 | 181.3 | 181.7 | 169 | 40.4 | 19.3 | 66.9 | 3.3 | 230.3 | 5.8 | 26.9 | 35.9 | 31 | 44.5 | 34.5 | 49.6 | 102.5 | 43.2 | 56.8 | 46.6 | 134.8 | 51.5 | 25.3 | 280.6 | 190.4 | 213.7 | 226.3 | 273 | 210.3 | 192 | 225.2
2054.1 | 1891.1 | -3.9 | 0 | 0 | 202.3 | 204.3 | 181.1 | 181.6 | 168.8 | 40.3 | 19.3 | 66.9 | 2.9 | 239.4 | 6 | 27 | 36.2 | 31 | 44.6 | 34.4 | 49.6 | 103.1 | 43 | 56.8 | 46.6 | 133.4 | 51.3 | 25.3 | 280.3 | 190 | 213.5 | 226.1 | 272.7 | 209.9 | 191.7 | 224.9
2055.1 | 1892.1 | -4.6 | 0 | 0 | 201.8 | 204.2 | 180.8 | 181.4 | 168.7 | 40.3 | 19.3 | 66.9 | 3 | 243.7 | 6 | 27.3 | 36.1 | 31 | 44.6 | 34.4 | 49.7 | 103.7 | 43.1 | 56.8 | 46.6 | 132.9 | 51.2 | 25.3 | 280 | 189.7 | 213.4 | 225.8 | 272.4 | 209.5 | 191.4 | 224.7
2056.1 | 1893.1 | -5.5 | 0 | 0 | 201.4 | 203.9 | 180.5 | 181 | 168.4 | 40.3 | 19.3 | 66.8 | 3 | 247 | 6 | 27.7 | 36 | 30.9 | 44.6 | 34.4 | 49.7 | 104.3 | 43.2 | 56.9 | 46.7 | 131.7 | 51 | 25.2 | 279.7 | 189.4 | 213.2 | 225.5 | 272.1 | 209.1 | 191.2 | 224.4
2057.1 | 1894.1 | -5.7 | 0 | 0 | 201.1 | 203.3 | 180.1 | 180.5 | 168 | 40.2 | 19.3 | 66.8 | 2.7 | 248.2 | 6.4 | 28 | 35.9 | 30.7 | 44.6 | 34.4 | 49.8 | 104.8 | 44.2 | 56.9 | 46.7 | 129.5 | 50.8 | 25.2 | 279.4 | 189.1 | 213 | 225.3 | 271.9 | 208.7 | 190.9 | 224.1
2058.1 | 1895.1 | -5.6 | 0 | 0 | 200.8 | 202.6 | 179.7 | 180.4 | 167.5 | 40.2 | 19.3 | 66.7 | 3.1 | 247.6 | 6.8 | 28.1 | 35.7 | 30.6 | 44.6 | 34.3 | 49.8 | 105.4 | 43.9 | 56.8 | 46.8 | 126 | 50.4 | 25.2 | 279.1 | 188.8 | 212.8 | 225 | 271.6 | 208.4 | 190.6 | 223.9
2059.1 | 1896.1 | -5.6 | 0 | 0 | 200.3 | 202.1 | 179.5 | 180.3 | 167.2 | 40.1 | 19.3 | 66.6 | 3.2 | 246.1 | 6.5 | 28 | 35.8 | 30.6 | 44.6 | 34.4 | 49.9 | 105.9 | 43.7 | 56.9 | 46.8 | 122.7 | 50.2 | 25.2 | 278.8 | 188.5 | 212.6 | 224.7 | 271.3 | 208 | 190.3 | 223.7
2060.1 | 1897.1 | -6.1 | 0 | 0 | 199.9 | 201.7 | 179.3 | 180.2 | 166.9 | 40.1 | 19.3 | 66.5 | 3.5 | 245.8 | 5.6 | 27.6 | 35.7 | 30.6 | 44.6 | 34.4 | 49.9 | 106.3 | 43.3 | 56.9 | 46.8 | 119.6 | 49.9 | 25.1 | 278.5 | 188.3 | 212.3 | 224.4 | 271 | 207.7 | 190.1 | 223.4
2061.1 | 1898.1 | -5.3 | 0 | 0 | 199.4 | 201.4 | 179 | 179.8 | 166.5 | 40.1 | 19.3 | 66.4 | 3.7 | 234.6 | 5.3 | 27.9 | 35.6 | 30.7 | 44.6 | 34.3 | 50 | 106.8 | 44 | 56.9 | 46.9 | 117.8 | 49.6 | 25.1 | 278.2 | 188 | 212.1 | 224.2 | 270.7 | 207.3 | 189.8 | 223.2
2062.1 | 1899.1 | -4.8 | 0 | 0 | 198.8 | 201 | 178.7 | 179.3 | 166.2 | 40.1 | 19.3 | 66.3 | 3.6 | 236.3 | 4.5 | 28.4 | 35.5 | 30.8 | 44.7 | 34.4 | 50 | 107.4 | 45.3 | 56.9 | 47 | 115.7 | 49.4 | 25 | 277.9 | 187.8 | 211.9 | 223.9 | 270.4 | 206.9 | 189.5 | 222.9
2063.1 | 1900.1 | -4 | 0 | 0 | 198.4 | 200.5 | 178.4 | 179 | 165.8 | 40.1 | 19.3 | 66.2 | 3.6 | 243.2 | 3.8 | 28.8 | 35.5 | 30.5 | 44.7 | 34.4 | 50 | 107.9 | 45.5 | 57 | 47.1 | 113.4 | 49.2 | 25 | 277.6 | 187.6 | 211.8 | 223.7 | 270.2 | 206.6 | 189.3 | 222.7
2064.1 | 1901.1 | -2.7 | 0 | 0 | 197.9 | 200.4 | 178 | 178.7 | 165.5 | 40.2 | 19.3 | 66.1 | 3.8 | 245.6 | 4 | 29.4 | 35.6 | 30.3 | 44.7 | 34.4 | 50.1 | 108.2 | 46 | 57 | 47.1 | 111.2 | 49 | 24.9 | 277.3 | 187.3 | 211.6 | 223.4 | 269.9 | 206.3 | 189 | 222.4
2065.1 | 1902.1 | -3.4 | 0 | 0 | 197.9 | 199.9 | 177.5 | 178.3 | 165.2 | 40.2 | 19.3 | 66.1 | 3.8 | 230.6 | 4.5 | 29.1 | 34.9 | 30.2 | 44.7 | 34.4 | 50.1 | 108.6 | 45.7 | 57.1 | 47.1 | 110 | 48.8 | 24.8 | 277 | 187 | 211.4 | 223.1 | 269.6 | 206 | 188.8 | 222.2
2066.1 | 1903.1 | -3.7 | 0 | 0 | 197.5 | 199.5 | 177.1 | 178 | 165 | 40.2 | 19.3 | 66 | 3.9 | 243.1 | 5.2 | 28.7 | 34.7 | 30.2 | 44.7 | 34.3 | 50.1 | 109.1 | 46.3 | 57.1 | 47.2 | 108.7 | 48.5 | 24.7 | 276.7 | 186.7 | 211.2 | 222.8 | 269.3 | 205.7 | 188.5 | 221.9
2067.1 | 1904.1 | -3.9 | 0 | 0 | 196.9 | 198.9 | 176.9 | 177.7 | 164.6 | 40.2 | 19.3 | 66 | 3.8 | 240.4 | 5.4 | 28.4 | 34.2 | 30.1 | 44.7 | 34.3 | 50.2 | 109.6 | 46.8 | 57.2 | 47.3 | 108.6 | 48.3 | 24.7 | 276.4 | 186.5 | 211 | 222.5 | 269 | 205.4 | 188.2 | 221.7
2068.1 | 1905.1 | -5 | 0 | 0 | 196.6 | 198.4 | 176.7 | 177.3 | 164.4 | 40.2 | 19.3 | 65.9 | 3.8 | 213 | 5.2 | 28 | 34.1 | 30.1 | 44.8 | 34.4 | 50.2 | 110.2 | 47.6 | 57.2 | 47.4 | 107.3 | 48 | 24.6 | 276.1 | 186.2 | 210.8 | 222.3 | 268.8 | 205.2 | 188 | 221.4
2069.1 | 1906.1 | -5.8 | 0 | 0 | 196.4 | 197.8 | 176.5 | 176.8 | 164.1 | 40.1 | 19.3 | 65.8 | 3.7 | 219.8 | 4.9 | 27.6 | 33.4 | 30 | 44.8 | 34.4 | 50.3 | 110.7 | 48.2 | 57.2 | 47.5 | 105.8 | 47.7 | 24.6 | 275.8 | 185.9 | 210.6 | 222 | 268.5 | 204.9 | 187.7 | 221.1
2070.1 | 1907.1 | -5.5 | 0 | 0 | 196 | 197.6 | 176.2 | 176.6 | 163.8 | 40 | 19.3 | 65.7 | 3.6 | 229 | 5 | 27.5 | 33.5 | 29.9 | 44.8 | 34.4 | 50.3 | 111.2 | 48.5 | 57.3 | 47.5 | 105 | 47.7 | 24.6 | 275.6 | 185.6 | 210.3 | 221.8 | 268.2 | 204.5 | 187.4 | 220.9
2071.1 | 1908.1 | -5.5 | 0 | 0 | 195.6 | 197.2 | 176.1 | 176.3 | 163.7 | 39.9 | 19.3 | 65.6 | 3.3 | 233.1 | 4.7 | 27.6 | 33.6 | 29.9 | 44.8 | 34.4 | 50.4 | 111.7 | 49.2 | 57.3 | 47.6 | 104.3 | 47.5 | 24.5 | 275.3 | 185.4 | 210 | 221.5 | 268 | 204.1 | 187.1 | 220.7
2072.1 | 1909.1 | -5.3 | 0 | 0 | 195.4 | 196.8 | 175.9 | 176 | 163.5 | 39.8 | 19.3 | 65.6 | 3.2 | 241.1 | 4.6 | 27.6 | 33.6 | 29.6 | 44.8 | 34.4 | 50.4 | 112.3 | 49 | 57.4 | 47.5 | 103.8 | 47.6 | 24.5 | 275 | 185.2 | 209.7 | 221.2 | 267.7 | 203.8 | 186.8 | 220.4
2073.1 | 1910.1 | -5.1 | 0 | 0 | 195.1 | 196.5 | 175.7 | 175.7 | 163.3 | 39.7 | 19.3 | 65.6 | 3.1 | 244.5 | 4.7 | 27.3 | 33.5 | 29.4 | 44.8 | 34.5 | 50.5 | 112.8 | 49.1 | 57.4 | 47.6 | 103 | 47.3 | 24.5 | 274.7 | 184.9 | 209.6 | 221 | 267.4 | 203.5 | 186.5 | 220.2
2074.1 | 1911.1 | -5.6 | 0 | 0 | 194.9 | 196.2 | 175.3 | 175.5 | 163.1 | 39.6 | 19.3 | 65.6 | 3.4 | 243.7 | 4.8 | 27.2 | 33.5 | 29.4 | 44.9 | 34.5 | 50.6 | 113.2 | 48.6 | 57.4 | 47.6 | 101.8 | 47.2 | 24.5 | 274.4 | 184.6 | 209.4 | 220.7 | 267.2 | 203.3 | 186.4 | 219.9
2075.1 | 1912.1 | -5.9 | 0 | 0 | 194.6 | 195.8 | 175 | 175.2 | 162.7 | 39.5 | 19.3 | 65.5 | 3.3 | 243.6 | 5.1 | 27.6 | 33.4 | 29.1 | 44.9 | 34.6 | 50.6 | 113.7 | 47.8 | 57.4 | 47.6 | 101 | 47 | 24.4 | 274.1 | 184.4 | 209.2 | 220.4 | 266.9 | 203 | 186.1 | 219.7
2076.1 | 1913.1 | -5.3 | 0 | 0 | 194.4 | 195.2 | 174.6 | 174.9 | 162.3 | 39.5 | 19.3 | 65.5 | 3.2 | 249.3 | 5.5 | 27.5 | 33.6 | 28.9 | 44.9 | 34.6 | 50.7 | 114.2 | 47.1 | 57.4 | 47.6 | 100.3 | 47 | 24.5 | 273.8 | 184 | 209 | 220.1 | 266.6 | 202.8 | 185.8 | 219.4
2077.1 | 1914.1 | -4.9 | 0 | 0 | 194.3 | 194.8 | 174.3 | 174.5 | 162.1 | 39.5 | 19.3 | 65.5 | 3.3 | 218.8 | 4.8 | 27.4 | 34.1 | 28.8 | 44.9 | 34.7 | 50.7 | 114.6 | 46.7 | 57.4 | 47.7 | 99.6 | 47 | 24.5 | 273.5 | 183.7 | 208.8 | 219.9 | 266.3 | 202.4 | 185.5 | 219.2
2078.1 | 1915.1 | -4.3 | 0 | 0 | 193.8 | 194.4 | 174.1 | 174.1 | 161.9 | 39.5 | 19.3 | 65.4 | 3.6 | 206.9 | 4.1 | 27.8 | 34.4 | 28.7 | 44.9 | 34.8 | 50.7 | 115 | 46.7 | 57.4 | 47.7 | 99 | 46.8 | 24.5 | 273.3 | 183.4 | 208.5 | 219.6 | 266.1 | 202.1 | 185.3 | 219
2079.1 | 1916.1 | -3.8 | 0 | 0 | 193.4 | 194.1 | 173.9 | 173.7 | 161.7 | 39.5 | 19.3 | 65.4 | 3.8 | 224.5 | 4.4 | 28 | 34.5 | 28.6 | 44.9 | 34.8 | 50.8 | 115.3 | 46.7 | 57.4 | 47.7 | 98.4 | 46.6 | 24.4 | 273 | 183 | 208.4 | 219.4 | 265.8 | 201.8 | 185 | 218.7
2080.1 | 1917.1 | -4.3 | 0 | 0 | 193 | 193.5 | 173.5 | 173.5 | 161.4 | 39.5 | 19.3 | 65.3 | 3.4 | 235.5 | 5 | 27.8 | 34.5 | 28.6 | 44.9 | 34.8 | 50.8 | 115.6 | 46.3 | 57.5 | 47.8 | 97.9 | 46.6 | 24.5 | 272.7 | 182.7 | 208.2 | 219.2 | 265.5 | 201.5 | 184.6 | 218.5
2081.1 | 1918.1 | -5.6 | 0 | 0 | 192.4 | 193 | 173.2 | 173.3 | 161.2 | 39.5 | 19.4 | 65.2 | 3.7 | 232.9 | 5.2 | 27.9 | 34.4 | 28.5 | 45 | 34.8 | 50.9 | 116 | 46.7 | 57.5 | 47.8 | 97.4 | 46.5 | 24.5 | 272.4 | 182.4 | 208 | 218.9 | 265.3 | 201.2 | 184.4 | 218.2
2082.1 | 1919.1 | -5.6 | 0 | 0 | 192 | 192.6 | 173 | 173.1 | 161.2 | 39.4 | 19.3 | 65.1 | 3.7 | 226.7 | 5.1 | 28.3 | 34.2 | 28.5 | 45 | 34.8 | 50.9 | 116.5 | 46.6 | 57.5 | 47.9 | 97.1 | 46.6 | 24.5 | 272.1 | 182 | 207.8 | 218.6 | 265 | 200.9 | 184.2 | 218
2083.1 | 1920.1 | -5.2 | 0 | 0 | 192 | 192.4 | 172.8 | 172.8 | 161.1 | 39.3 | 19.3 | 65 | 3.4 | 220.5 | 5.3 | 28.5 | 34.2 | 28.2 | 45 | 34.8 | 51 | 116.9 | 46.9 | 57.5 | 47.9 | 96.8 | 46.7 | 24.4 | 271.8 | 181.8 | 207.6 | 218.4 | 264.7 | 200.6 | 183.9 | 217.8
2084.1 | 1921.1 | -4.9 | 0 | 0 | 191.5 | 192 | 172.6 | 172.5 | 161 | 39.3 | 19.4 | 65 | 3.1 | 211.4 | 5.6 | 28.6 | 34 | 27.9 | 45 | 34.8 | 51 | 117.3 | 46.7 | 57.5 | 47.9 | 96.4 | 46.8 | 24.4 | 271.5 | 181.6 | 207.3 | 218.2 | 264.5 | 200.4 | 183.6 | 217.5
2085.1 | 1922.1 | -4.7 | 0 | 0 | 191.3 | 191.7 | 172.5 | 172.3 | 160.8 | 39.2 | 19.4 | 64.9 | 3 | 222.1 | 5.8 | 28.7 | 34.6 | 27.8 | 45 | 34.9 | 51.1 | 117.7 | 46.7 | 57.5 | 48 | 96.1 | 46.8 | 24.4 | 271.2 | 181.4 | 207 | 217.9 | 264.2 | 200.2 | 183.4 | 217.3
2086.1 | 1923.1 | -4.6 | 0 | 0 | 190.9 | 191.5 | 172.2 | 172.1 | 160.5 | 39.2 | 19.4 | 64.9 | 3.2 | 236.7 | 5.6 | 28.9 | 34.5 | 27.7 | 45 | 34.9 | 51.1 | 118 | 46.4 | 57.5 | 48 | 95.8 | 46.7 | 24.4 | 271 | 181.1 | 206.7 | 217.7 | 263.9 | 200 | 183.1 | 217.1
2087.1 | 1924.1 | -5.6 | 0 | 0 | 190.5 | 191.1 | 171.9 | 171.7 | 160.4 | 39.3 | 19.4 | 64.8 | 2.9 | 227.9 | 5.2 | 28.7 | 34.2 | 27.6 | 45 | 35 | 51.2 | 118.2 | 45.8 | 57.5 | 48 | 95.5 | 46.6 | 24.4 | 270.7 | 180.8 | 206.4 | 217.4 | 263.7 | 199.7 | 182.8 | 216.8
2088.1 | 1925.1 | -5.3 | 0 | 0 | 190 | 190.7 | 171.5 | 171.5 | 160.2 | 39.2 | 19.4 | 64.8 | 3 | 238 | 4.8 | 28.3 | 34.4 | 27.4 | 45 | 35 | 51.2 | 118.5 | 45.2 | 57.5 | 48 | 95.2 | 46.6 | 24.4 | 270.4 | 180.6 | 206.1 | 217.1 | 263.4 | 199.5 | 182.6 | 216.6
2089.1 | 1926.1 | -5 | 0 | 0 | 189.5 | 190.6 | 171.2 | 171.3 | 159.9 | 39.2 | 19.4 | 64.7 | 3.7 | 236.5 | 4.8 | 28.2 | 34 | 27.3 | 45 | 34.9 | 51.3 | 118.9 | 45 | 57.5 | 48.1 | 94.8 | 46.6 | 24.3 | 270.1 | 180.3 | 205.9 | 216.9 | 263.2 | 199.2 | 182.3 | 216.3
2090.1 | 1927.1 | -4.6 | 0 | 0 | 189.1 | 190.6 | 171 | 171 | 159.7 | 39.2 | 19.4 | 64.7 | 3.3 | 237.3 | 5.3 | 28.5 | 34.2 | 27.2 | 45 | 34.8 | 51.4 | 119.3 | 44.9 | 57.6 | 48.2 | 94.6 | 46.6 | 24.3 | 269.8 | 179.9 | 205.8 | 216.6 | 262.9 | 199 | 182 | 216.1
2091.1 | 1928.1 | -3.9 | 0 | 0 | 188.6 | 190.3 | 170.8 | 170.8 | 159.5 | 39.2 | 19.4 | 64.6 | 3.2 | 237.2 | 5.4 | 28.7 | 34.3 | 27.2 | 45.1 | 34.8 | 51.4 | 119.7 | 45.4 | 57.6 | 48.3 | 94.3 | 46.5 | 24.2 | 269.5 | 179.7 | 205.6 | 216.3 | 262.6 | 198.7 | 181.7 | 215.9
2092.1 | 1929.1 | -3.1 | 0 | 0 | 188.2 | 189.7 | 170.7 | 170.6 | 159.3 | 39.3 | 19.4 | 64.6 | 3.7 | 222.3 | 5.5 | 28.7 | 34.2 | 27.2 | 45.1 | 34.8 | 51.5 | 120.1 | 46.3 | 57.6 | 48.5 | 94.1 | 46.4 | 24.2 | 269.3 | 179.4 | 205.4 | 216.1 | 262.4 | 198.4 | 181.4 | 215.6
2093.1 | 1930.1 | -3.9 | 0 | 0 | 188 | 189.1 | 170.5 | 170.2 | 159 | 39.3 | 19.4 | 64.5 | 3.4 | 236.6 | 5.3 | 28.4 | 34 | 27.1 | 45.1 | 34.8 | 51.5 | 120.4 | 46.3 | 57.6 | 48.6 | 94 | 46.4 | 24.1 | 269 | 179.2 | 205.3 | 215.9 | 262.1 | 198.1 | 181.1 | 215.4
2094.1 | 1931.1 | -3.4 | 0 | 0 | 187.7 | 188.8 | 170.4 | 169.7 | 158.7 | 39.3 | 19.4 | 64.4 | 3.3 | 245.9 | 5.1 | 27.9 | 34.1 | 27 | 45.1 | 34.9 | 51.5 | 120.7 | 46.5 | 57.6 | 48.7 | 93.8 | 46.5 | 24.1 | 268.7 | 178.9 | 205.1 | 215.7 | 261.8 | 197.8 | 181 | 215.1
2095.1 | 1932.1 | -3.9 | 0 | 0 | 187.3 | 188.5 | 170.1 | 169.3 | 158.5 | 39.3 | 19.4 | 64.4 | 2.9 | 257.7 | 4.9 | 27.5 | 34.1 | 27 | 45.1 | 34.8 | 51.6 | 120.9 | 47 | 57.6 | 48.7 | 93.6 | 46.6 | 24 | 268.4 | 178.6 | 205 | 215.4 | 261.6 | 197.6 | 180.7 | 214.9
2096.1 | 1933.1 | -4.4 | 0 | 0 | 187 | 188.3 | 169.9 | 169.1 | 158.3 | 39.3 | 19.4 | 64.3 | 3.1 | 261.3 | 4.8 | 28 | 33.9 | 27 | 45.1 | 34.8 | 51.6 | 121.1 | 46.8 | 57.6 | 48.7 | 93.3 | 46.5 | 23.9 | 268.1 | 178.4 | 204.8 | 215.2 | 261.3 | 197.4 | 180.5 | 214.7
2097.1 | 1934.1 | -5.1 | 0 | 0 | 186.5 | 187.9 | 169.7 | 168.8 | 158.1 | 39.2 | 19.4 | 64.3 | 2.8 | 258 | 5.2 | 27.7 | 34.2 | 27 | 45.1 | 34.8 | 51.7 | 121.4 | 46.4 | 57.6 | 48.8 | 93 | 46.3 | 23.9 | 267.9 | 178.2 | 204.6 | 214.9 | 261.1 | 197.1 | 180.2 | 214.4
2098.1 | 1935.1 | -5.5 | 0 | 0 | 185.9 | 187.5 | 169.5 | 168.5 | 158.1 | 39.2 | 19.4 | 64.2 | 2.8 | 258.7 | 5.9 | 27.7 | 34.2 | 27 | 45.1 | 34.8 | 51.7 | 121.6 | 45.8 | 57.6 | 48.7 | 92.8 | 45.8 | 23.9 | 267.6 | 178 | 204.5 | 214.7 | 260.8 | 196.8 | 180 | 214.2
2099.1 | 1936.1 | -5.3 | 0 | 0 | 185.6 | 187.4 | 169.1 | 168.2 | 157.9 | 39.1 | 19.4 | 64.2 | 2.9 | 251.5 | 6.5 | 27.3 | 34.2 | 27 | 45.1 | 34.7 | 51.7 | 121.9 | 45.5 | 57.7 | 48.7 | 92.6 | 45.3 | 23.9 | 267.3 | 177.7 | 204.3 | 214.4 | 260.5 | 196.5 | 179.7 | 214
2100.1 | 1937.1 | -5.3 | 0 | 0 | 185.4 | 187 | 168.7 | 168 | 157.7 | 39 | 19.4 | 64.1 | 3.2 | 249.7 | 6.9 | 26.9 | 34 | 26.9 | 45.2 | 34.7 | 51.8 | 122.3 | 45.3 | 57.7 | 48.7 | 92.3 | 45.1 | 23.9 | 267 | 177.4 | 204.1 | 214.2 | 260.3 | 196.3 | 179.4 | 213.7
2101.1 | 1938.1 | -5 | 0 | 0 | 185.3 | 186.7 | 168.5 | 167.8 | 157.5 | 38.9 | 19.4 | 64.1 | 3.3 | 251.4 | 6.9 | 26.6 | 33.8 | 26.9 | 45.2 | 34.7 | 51.8 | 122.6 | 44.8 | 57.7 | 48.7 | 92.1 | 44.9 | 23.8 | 266.7 | 177.1 | 203.9 | 213.9 | 260 | 196.1 | 179.2 | 213.5
2102.1 | 1939.1 | -5.1 | 0 | 0 | 184.8 | 186.4 | 168.2 | 167.5 | 157.4 | 39 | 19.4 | 64 | 3 | 248.6 | 6.3 | 26.4 | 33.7 | 26.8 | 45.2 | 34.7 | 51.9 | 122.9 | 44.6 | 57.7 | 48.7 | 91.8 | 45 | 23.8 | 266.4 | 176.8 | 203.7 | 213.7 | 259.7 | 195.8 | 178.9 | 213.3
2103.1 | 1940.1 | -4.7 | 0 | 0 | 184.6 | 186.4 | 167.9 | 167.2 | 157.2 | 39 | 19.4 | 64 | 3.3 | 235.1 | 5.7 | 26.2 | 33.7 | 26.8 | 45.2 | 34.7 | 51.9 | 123.3 | 44.1 | 57.6 | 48.7 | 91.6 | 45 | 23.7 | 266.2 | 176.6 | 203.4 | 213.4 | 259.5 | 195.6 | 178.7 | 213
2104.1 | 1941.1 | -3.3 | 0 | 0 | 184.3 | 186.4 | 167.6 | 166.9 | 156.9 | 39.1 | 19.4 | 64 | 3.5 | 257.1 | 5.4 | 26 | 33.7 | 26.8 | 45.2 | 34.7 | 52 | 123.6 | 43.6 | 57.6 | 48.7 | 91.3 | 44.8 | 23.7 | 265.9 | 176.2 | 203.1 | 213.2 | 259.2 | 195.4 | 178.4 | 212.8
2105.1 | 1942.1 | -3.5 | 0 | 0 | 183.7 | 186.3 | 167.4 | 166.7 | 156.5 | 39.1 | 19.4 | 63.9 | 3.1 | 247.7 | 5.2 | 25.8 | 34 | 26.8 | 45.2 | 34.6 | 52.1 | 123.9 | 43.1 | 57.5 | 48.8 | 91.1 | 44.6 | 23.6 | 265.6 | 175.9 | 202.9 | 212.9 | 259 | 195.2 | 178.2 | 212.6
2106.1 | 1943.1 | -4.6 | 0 | 0 | 183.4 | 186.1 | 167.1 | 166.7 | 156.3 | 39.1 | 19.4 | 63.9 | 3.1 | 250.3 | 5.4 | 25.7 | 34.1 | 26.7 | 45.2 | 34.5 | 52.1 | 124.2 | 42.6 | 57.5 | 48.7 | 90.8 | 44.4 | 23.6 | 265.3 | 175.6 | 202.7 | 212.7 | 258.7 | 195 | 177.9 | 212.4
2107.1 | 1944.1 | -5.2 | 0 | 0 | 183.1 | 186.3 | 166.9 | 166.6 | 156.1 | 39.1 | 19.4 | 63.8 | 3.1 | 273.4 | 5.6 | 25.5 | 34.4 | 26.5 | 45.2 | 34.5 | 52.2 | 124.5 | 42.1 | 57.5 | 48.7 | 90.6 | 44.1 | 23.6 | 265.1 | 175.3 | 202.5 | 212.4 | 258.4 | 194.8 | 177.7 | 212.1
2108.1 | 1945.1 | -5.6 | 0 | 0 | 182.8 | 186.4 | 166.7 | 166.4 | 155.9 | 39.1 | 19.4 | 63.8 | 3.4 | 258.5 | 5.3 | 25.5 | 34.4 | 26.5 | 45.2 | 34.5 | 52.2 | 124.8 | 41.7 | 57.5 | 48.7 | 90.3 | 43.8 | 23.8 | 264.8 | 175.1 | 202.3 | 212.2 | 258.2 | 194.7 | 177.5 | 211.9
2109.1 | 1946.1 | -5.5 | 0 | 0 | 182.7 | 186.2 | 166.5 | 166.2 | 155.7 | 39 | 19.4 | 63.7 | 3.2 | 251.7 | 5.2 | 25.4 | 34.6 | 26.5 | 45.2 | 34.5 | 52.3 | 124.9 | 41.4 | 57.5 | 48.7 | 90.1 | 43.7 | 23.7 | 264.5 | 174.9 | 202.1 | 211.9 | 257.9 | 194.5 | 177.2 | 211.7
2110.1 | 1947.1 | -5.3 | 0 | 0 | 182.5 | 185.8 | 166.3 | 165.9 | 155.6 | 38.9 | 19.4 | 63.6 | 3.5 | 265.8 | 5.2 | 25.4 | 34.8 | 26.6 | 45.2 | 34.5 | 52.3 | 125.1 | 41.3 | 57.5 | 48.7 | 89.9 | 43.6 | 23.6 | 264.2 | 174.6 | 201.8 | 211.7 | 257.7 | 194.3 | 177 | 211.5
2111.1 | 1948.1 | -5.1 | 0 | 0 | 182.2 | 185.2 | 166.1 | 165.7 | 155.5 | 38.8 | 19.4 | 63.6 | 2.9 | 261.2 | 5.1 | 25.2 | 35.4 | 26.5 | 45.2 | 34.5 | 52.4 | 125.2 | 41.1 | 57.5 | 48.7 | 89.6 | 43.3 | 23.6 | 264 | 174.3 | 201.6 | 211.4 | 257.4 | 194.2 | 176.8 | 211.2
2112.1 | 1949.1 | -4.3 | 0 | 0 | 181.9 | 184.7 | 165.7 | 165.5 | 155.4 | 38.6 | 19.4 | 63.5 | 2.9 | 271.3 | 5.1 | 25.2 | 35.4 | 26.5 | 45.2 | 34.5 | 52.4 | 125.3 | 40.9 | 57.4 | 48.7 | 89.4 | 43.1 | 23.6 | 263.7 | 174.1 | 201.4 | 211.2 | 257.2 | 194 | 176.5 | 211
2113.1 | 1950.1 | -4.2 | 0 | 0 | 181.4 | 184.4 | 165.4 | 165.3 | 155.2 | 38.5 | 19.4 | 63.5 | 2.7 | 250 | 5 | 25.4 | 35.1 | 26.5 | 45.2 | 34.5 | 52.4 | 125.4 | 40.5 | 57.4 | 48.8 | 89.1 | 42.9 | 23.6 | 263.4 | 173.8 | 201.2 | 211 | 256.9 | 193.8 | 176.2 | 210.8
2114.1 | 1951.1 | -4.5 | 0 | 0 | 181 | 184 | 165 | 165.2 | 154.8 | 38.4 | 19.4 | 63.5 | 2.8 | 244.5 | 4.9 | 25.5 | 35.2 | 26.6 | 45.2 | 34.5 | 52.5 | 125.6 | 40.6 | 57.3 | 48.7 | 88.9 | 42.8 | 23.6 | 263.1 | 173.5 | 200.9 | 210.8 | 256.7 | 193.5 | 176 | 210.5
2115.1 | 1952.1 | -5.4 | 0 | 0 | 180.7 | 183.5 | 164.6 | 164.9 | 154.6 | 38.3 | 19.4 | 63.5 | 2.9 | 257 | 4.7 | 25.6 | 34.8 | 26.6 | 45.2 | 34.5 | 52.6 | 125.8 | 40.8 | 57.2 | 48.7 | 88.7 | 42.5 | 23.5 | 262.8 | 173.2 | 200.7 | 210.5 | 256.4 | 193.2 | 175.8 | 210.3
2116.1 | 1953.1 | -5.9 | 0 | 0 | 180.3 | 182.8 | 164.3 | 164.5 | 154.4 | 38.2 | 19.4 | 63.4 | 3.1 | 244.7 | 4.8 | 25.5 | 35.1 | 26.5 | 45.2 | 34.4 | 52.6 | 125.9 | 40.8 | 57.2 | 48.7 | 88.5 | 42.2 | 23.5 | 262.6 | 173 | 200.5 | 210.3 | 256.2 | 193 | 175.5 | 210.1
2117.1 | 1954.1 | -5.8 | 0 | 0 | 179.8 | 182.2 | 164.2 | 164.1 | 154.2 | 38.2 | 19.4 | 63.3 | 2.8 | 230.8 | 4.7 | 25.7 | 35.1 | 26.5 | 45.2 | 34.4 | 52.7 | 125.9 | 41.2 | 57.2 | 48.8 | 88.2 | 42 | 23.5 | 262.3 | 172.8 | 200.3 | 210 | 255.9 | 192.8 | 175.2 | 209.9
2118.1 | 1955.1 | -5.6 | 0 | 0 | 179.3 | 181.8 | 163.9 | 163.8 | 154 | 38.1 | 19.5 | 63.2 | 2.7 | 255.3 | 4.7 | 25.4 | 34.9 | 26.5 | 45.2 | 34.4 | 52.7 | 125.8 | 41.2 | 57.2 | 48.7 | 88 | 41.8 | 23.6 | 262 | 172.5 | 200.1 | 209.8 | 255.7 | 192.7 | 174.8 | 209.6
2119.1 | 1956.1 | -5.5 | 0 | 0 | 178.9 | 181.2 | 163.5 | 163.4 | 153.7 | 38 | 19.5 | 63.1 | 3 | 263.3 | 5 | 25.1 | 35.2 | 26.5 | 45.2 | 34.4 | 52.7 | 125.7 | 41.3 | 57.2 | 48.8 | 87.8 | 41.6 | 23.6 | 261.8 | 172.3 | 199.9 | 209.6 | 255.4 | 192.6 | 174.6 | 209.4
2120.1 | 1957.1 | -5.3 | 0 | 0 | 178.6 | 180.8 | 163.2 | 163.1 | 153.6 | 37.9 | 19.5 | 63.1 | 3 | 254.4 | 5.5 | 25 | 35.3 | 26.5 | 45.2 | 34.4 | 52.8 | 125.5 | 41.6 | 57.2 | 48.9 | 87.6 | 41.3 | 23.6 | 261.5 | 172.1 | 199.6 | 209.3 | 255.2 | 192.3 | 174.3 | 209.2
2121.1 | 1958.1 | -5 | 0 | 0 | 178.3 | 180.5 | 163 | 162.8 | 153.5 | 37.8 | 19.5 | 63 | 2.9 | 258.7 | 5.6 | 25 | 35.5 | 26.5 | 45.2 | 34.4 | 52.8 | 125.3 | 42 | 57.2 | 49 | 87.5 | 41.1 | 23.7 | 261.2 | 171.8 | 199.3 | 209.1 | 254.9 | 192.1 | 174 | 208.9
2122.1 | 1959.1 | -5.1 | 0 | 0 | 178.1 | 180 | 162.7 | 162.7 | 153.1 | 37.8 | 19.5 | 63 | 2.9 | 261.4 | 5.4 | 25 | 35.4 | 26.5 | 45.3 | 34.3 | 52.9 | 125.3 | 42.5 | 57.2 | 49 | 87.3 | 40.9 | 23.8 | 261 | 171.6 | 199.1 | 208.8 | 254.7 | 192 | 173.7 | 208.7
2123.1 | 1960.1 | -4.5 | 0 | 0 | 177.8 | 179.4 | 162.3 | 162.5 | 152.7 | 37.8 | 19.5 | 63 | 2.6 | 273.6 | 4.8 | 25.1 | 35.7 | 26.6 | 45.3 | 34.3 | 52.9 | 125.3 | 43 | 57.2 | 49.1 | 87.1 | 40.8 | 23.8 | 260.7 | 171.4 | 198.9 | 208.6 | 254.4 | 191.9 | 173.4 | 208.5
2124.1 | 1961.1 | -5.2 | 0 | 0 | 177.5 | 179 | 162 | 162.3 | 152.5 | 37.9 | 19.5 | 62.9 | 2.6 | 277.9 | 4.6 | 25.1 | 35.9 | 26.6 | 45.3 | 34.2 | 52.9 | 125.4 | 43.4 | 57.2 | 49.2 | 87 | 40.3 | 23.8 | 260.4 | 171.2 | 198.6 | 208.3 | 254.2 | 191.7 | 173.2 | 208.2
2125.1 | 1962.1 | -5.9 | 0 | 0 | 177.1 | 179 | 161.9 | 162 | 152.3 | 37.9 | 19.5 | 62.9 | 3.1 | 266.2 | 5.2 | 24.9 | 36 | 26.6 | 45.3 | 34.1 | 52.9 | 125.4 | 43.6 | 57.2 | 49.3 | 86.8 | 40.3 | 23.8 | 260.1 | 170.9 | 198.4 | 208.1 | 253.9 | 191.5 | 172.8 | 208
2126.1 | 1963.1 | -5.4 | 0 | 0 | 177 | 178.9 | 161.8 | 161.7 | 152.1 | 37.9 | 19.5 | 62.9 | 3.2 | 261.4 | 5.8 | 25 | 36.1 | 26.5 | 45.3 | 34.1 | 53 | 125.5 | 43.8 | 57.2 | 49.4 | 86.6 | 40.4 | 23.8 | 259.9 | 170.6 | 198.2 | 207.9 | 253.7 | 191.3 | 172.5 | 207.8
2127.1 | 1964.1 | -5.4 | 0 | 0 | 177 | 178.4 | 161.6 | 161.4 | 151.6 | 38 | 19.5 | 62.9 | 2.6 | 249.9 | 5.5 | 25.1 | 36.2 | 26.6 | 45.3 | 34.1 | 53.1 | 125.4 | 44 | 57.3 | 49.5 | 86.5 | 40.3 | 23.7 | 259.6 | 170.4 | 198 | 207.6 | 253.4 | 191.1 | 172.2 | 207.5
2128.1 | 1965.1 | -5.2 | 0 | 0 | 176.8 | 177.9 | 161.4 | 161.2 | 151.2 | 38 | 19.5 | 62.9 | 2.7 | 257.5 | 5.2 | 25.1 | 36.3 | 26.6 | 45.3 | 34.1 | 53.1 | 125.2 | 44.2 | 57.3 | 49.4 | 86.4 | 40.3 | 23.7 | 259.3 | 170.1 | 197.6 | 207.4 | 253.2 | 191 | 171.9 | 207.3
2129.1 | 1966.1 | -4.9 | 0 | 0 | 176.4 | 177.8 | 161.2 | 161.1 | 151 | 38 | 19.5 | 62.8 | 3 | 279.9 | 5.1 | 25.1 | 36 | 26.6 | 45.3 | 34.1 | 53.1 | 125.2 | 44.5 | 57.3 | 49.4 | 86.3 | 40 | 23.7 | 259 | 169.9 | 197.3 | 207.2 | 253 | 190.8 | 171.7 | 207.1
2130.1 | 1967.1 | -3.9 | 0 | 0 | 176.2 | 177.4 | 161 | 161 | 151 | 38 | 19.5 | 62.8 | 3 | 276 | 4.9 | 25.3 | 35.8 | 26.6 | 45.3 | 34.2 | 53.2 | 125.1 | 44.6 | 57.3 | 49.5 | 86.2 | 39.8 | 23.7 | 258.8 | 169.6 | 197 | 207 | 252.7 | 190.6 | 171.5 | 206.9
2131.1 | 1968.1 | -4.3 | 0 | 0 | 176.2 | 177.3 | 160.8 | 160.8 | 150.8 | 38.1 | 19.5 | 62.8 | 3.1 | 271.8 | 4.6 | 25.7 | 35.9 | 26.5 | 45.3 | 34.2 | 53.2 | 124.8 | 44.6 | 57.3 | 49.6 | 86.1 | 39.6 | 23.7 | 258.5 | 169.3 | 196.7 | 206.8 | 252.5 | 190.4 | 171.2 | 206.6
2132.1 | 1969.1 | -4.8 | 0 | 0 | 175.9 | 177.3 | 160.7 | 160.6 | 150.6 | 38.1 | 19.5 | 62.7 | 3.5 | 271.9 | 4.3 | 26.1 | 36.1 | 26.5 | 45.3 | 34.2 | 53.3 | 124.5 | 44.6 | 57.3 | 49.6 | 86 | 39.4 | 23.8 | 258.2 | 169.1 | 196.4 | 206.5 | 252.2 | 190.3 | 171 | 206.4
2133.1 | 1970.1 | -5.3 | 0 | 0 | 175.5 | 177.3 | 160.6 | 160.3 | 150.3 | 38.1 | 19.5 | 62.7 | 3.3 | 270.5 | 3.9 | 26.3 | 36.1 | 26.4 | 45.3 | 34.3 | 53.3 | 124.3 | 44.7 | 57.3 | 49.7 | 85.9 | 39.4 | 23.8 | 258 | 168.9 | 196 | 206.2 | 252 | 190.1 | 170.7 | 206.2
2134.1 | 1971.1 | -4.4 | 0 | 0 | 175.5 | 176.9 | 160.3 | 160 | 150 | 38.1 | 19.5 | 62.6 | 3.3 | 282.8 | 3.5 | 26.3 | 36 | 26.2 | 45.3 | 34.3 | 53.4 | 124.2 | 44.8 | 57.4 | 49.7 | 85.9 | 39.5 | 23.8 | 257.7 | 168.6 | 195.8 | 206 | 251.7 | 190 | 170.4 | 206
2135.1 | 1972.1 | -4.6 | 0 | 0 | 175.2 | 176.5 | 160.1 | 159.7 | 149.7 | 38.1 | 19.5 | 62.5 | 3.3 | 288.5 | 3.2 | 26.2 | 35.8 | 26 | 45.3 | 34.3 | 53.4 | 124.2 | 44.7 | 57.4 | 49.8 | 85.8 | 39.7 | 23.8 | 257.4 | 168.2 | 195.5 | 205.7 | 251.5 | 189.7 | 170.1 | 205.7
2136.1 | 1973.1 | -4.5 | 0 | 0 | 174.7 | 176 | 159.9 | 159.4 | 149.3 | 38 | 19.5 | 62.4 | 3.3 | 280.2 | 2.9 | 26.2 | 35.9 | 26 | 45.3 | 34.4 | 53.4 | 124.1 | 44.9 | 57.4 | 49.9 | 85.7 | 39.8 | 23.8 | 257.2 | 168 | 195.3 | 205.5 | 251.2 | 189.4 | 169.7 | 205.5
2137.1 | 1974.1 | -4.8 | 0 | 0 | 174.6 | 176.1 | 159.8 | 159.2 | 149.1 | 37.9 | 19.5 | 62.4 | 3.2 | 266.8 | 2.6 | 26.3 | 36.4 | 25.9 | 45.3 | 34.4 | 53.6 | 124.2 | 45.6 | 57.4 | 50 | 85.6 | 39.8 | 23.8 | 256.9 | 167.8 | 195.1 | 205.4 | 251 | 189.2 | 169.4 | 205.3
2138.1 | 1975.1 | -3.8 | 0 | 0 | 174.2 | 176.4 | 159.6 | 159 | 149 | 37.9 | 19.5 | 62.3 | 3.2 | 262.9 | 2.4 | 26.4 | 36 | 25.8 | 45.3 | 34.4 | 53.5 | 124.3 | 45.2 | 57.4 | 50 | 85.5 | 39.9 | 23.8 | 256.6 | 167.6 | 194.8 | 205.1 | 250.7 | 189 | 169.1 | 205.1
2139.1 | 1976.1 | -3.9 | 0 | 0 | 174 | 176.5 | 159.4 | 158.7 | 148.9 | 37.8 | 19.5 | 62.3 | 3.4 | 260.9 | 2.3 | 26.4 | 35.8 | 25.8 | 45.3 | 34.4 | 53.6 | 124.4 | 45.3 | 57.5 | 50.1 | 85.4 | 39.8 | 23.7 | 256.3 | 167.4 | 194.5 | 204.9 | 250.5 | 188.8 | 168.8 | 204.8
2140.1 | 1977.1 | -4.9 | 0 | 0 | 173.6 | 176.3 | 159.2 | 158.4 | 148.9 | 37.8 | 19.5 | 62.2 | 3.6 | 253.3 | 2.1 | 26.4 | 35.9 | 25.8 | 45.3 | 34.4 | 53.7 | 124.5 | 45.4 | 57.5 | 50.2 | 85.4 | 39.7 | 23.9 | 256.1 | 167.1 | 194.2 | 204.6 | 250.2 | 188.6 | 168.6 | 204.6
2141.1 | 1978.1 | -4 | 0 | 0 | 173.3 | 176.1 | 159 | 158.1 | 148.7 | 37.7 | 19.5 | 62.2 | 3.3 | 243.5 | 1.9 | 26.1 | 35.9 | 25.7 | 45.3 | 34.4 | 53.6 | 124.7 | 44.9 | 57.5 | 50.2 | 85.3 | 39.6 | 23.9 | 255.8 | 166.8 | 194.1 | 204.3 | 250 | 188.3 | 168.3 | 204.4
2142.1 | 1979.1 | -3.6 | 0 | 0 | 173.1 | 175.6 | 158.7 | 157.9 | 148.4 | 37.5 | 19.5 | 62.1 | 3.2 | 234.7 | 1.8 | 25.7 | 35.7 | 25.7 | 45.3 | 34.3 | 53.7 | 124.6 | 45.2 | 57.4 | 50.3 | 85.2 | 39.5 | 23.8 | 255.5 | 166.5 | 193.8 | 204.2 | 249.7 | 188.2 | 168 | 204.2
2143.1 | 1980.1 | -3.5 | 0 | 0 | 173 | 175.2 | 158.4 | 157.7 | 148.2 | 37.5 | 19.5 | 62.1 | 2.9 | 232.8 | 1.8 | 25.5 | 35.6 | 25.7 | 45.3 | 34.3 | 53.7 | 124.7 | 45.4 | 57.4 | 50.3 | 85.1 | 39.3 | 23.7 | 255.2 | 166.2 | 193.6 | 204 | 249.5 | 188 | 167.7 | 204
2144.1 | 1981.1 | -3.6 | 0 | 0 | 172.8 | 174.9 | 158.2 | 157.5 | 148 | 37.5 | 19.5 | 62 | 3 | 232.7 | 1.9 | 25.5 | 35.6 | 25.6 | 45.3 | 34.2 | 53.8 | 124.8 | 45.7 | 57.3 | 50.3 | 85 | 39.3 | 23.6 | 255 | 166 | 193.4 | 203.8 | 249.2 | 187.7 | 167.4 | 203.7
2145.1 | 1982.1 | -4.7 | 0 | 0 | 172.4 | 174.6 | 158.1 | 157.2 | 147.9 | 37.4 | 19.5 | 62 | 3 | 237 | 2 | 25.5 | 35.5 | 25.5 | 45.3 | 34.2 | 53.8 | 124.9 | 45.9 | 57.3 | 50.4 | 84.9 | 39.4 | 23.6 | 254.7 | 165.8 | 193.1 | 203.5 | 249 | 187.3 | 167.2 | 203.5
2146.1 | 1983.1 | -5.6 | 0 | 0 | 172.3 | 174.3 | 157.9 | 156.9 | 147.8 | 37.4 | 19.5 | 62 | 3.3 | 247.8 | 2.2 | 26.2 | 35.6 | 25.5 | 45.3 | 34.2 | 53.8 | 125 | 46.2 | 57.3 | 50.4 | 84.7 | 39.5 | 23.6 | 254.4 | 165.6 | 192.8 | 203.2 | 248.7 | 187.2 | 166.9 | 203.3
2147.1 | 1984.1 | -5.7 | 0 | 0 | 172 | 174 | 157.7 | 156.7 | 147.5 | 37.4 | 19.5 | 61.9 | 3.3 | 259.8 | 2.5 | 26.4 | 35.7 | 25.4 | 45.4 | 34.1 | 53.9 | 125 | 45.7 | 57.3 | 50.3 | 84.6 | 39.5 | 23.6 | 254.2 | 165.3 | 192.6 | 203 | 248.5 | 187 | 166.7 | 203.1
2148.1 | 1985.1 | -4.3 | 0 | 0 | 171.7 | 173.5 | 157.5 | 156.6 | 147.2 | 37.3 | 19.5 | 61.9 | 3.1 | 266.7 | 2.8 | 26.4 | 35.8 | 25.4 | 45.4 | 34.1 | 53.9 | 124.9 | 45 | 57.3 | 50.3 | 84.4 | 39.6 | 23.6 | 253.9 | 165 | 192.4 | 202.8 | 248.2 | 186.7 | 166.3 | 202.8
2149.1 | 1986.1 | -3.7 | 0 | 0 | 171.6 | 173.1 | 157.3 | 156.4 | 147.1 | 37.3 | 19.5 | 61.8 | 2.9 | 263 | 3.4 | 26 | 35.8 | 25.4 | 45.4 | 34.2 | 54 | 124.8 | 44.8 | 57.3 | 50.3 | 84.2 | 39.6 | 23.7 | 253.6 | 164.8 | 192.3 | 202.6 | 248 | 186.4 | 166 | 202.6
2150.1 | 1987.1 | -4.2 | 0 | 0 | 171.4 | 173.1 | 156.9 | 156.2 | 146.9 | 37.3 | 19.6 | 61.8 | 2.6 | 244.2 | 4 | 25.8 | 36 | 25.4 | 45.4 | 34.1 | 54 | 124.7 | 44.6 | 57.3 | 50.3 | 84 | 39.6 | 23.6 | 253.4 | 164.6 | 192 | 202.4 | 247.7 | 186.1 | 165.7 | 202.4
2151.1 | 1988.1 | -4.7 | 0 | 0 | 171.3 | 173.3 | 156.7 | 155.9 | 146.6 | 37.3 | 19.6 | 61.8 | 2.8 | 244.3 | 4.1 | 25.7 | 36 | 25.4 | 45.4 | 34.1 | 54 | 124.7 | 44.4 | 57.4 | 50.3 | 83.9 | 39.7 | 23.7 | 253.1 | 164.4 | 191.7 | 202.2 | 247.5 | 185.9 | 165.4 | 202.1
2152.1 | 1989.1 | -5.4 | 0 | 0 | 170.9 | 173.5 | 156.5 | 155.7 | 146.4 | 37.3 | 19.6 | 61.7 | 2.9 | 254 | 3.8 | 25.6 | 36.8 | 25.4 | 45.4 | 34.1 | 54.1 | 124.3 | 44.7 | 57.5 | 50.3 | 83.7 | 39.7 | 23.7 | 252.8 | 164.2 | 191.4 | 201.9 | 247.3 | 185.7 | 165.2 | 201.9
2153.1 | 1990.1 | -5.8 | 0 | 0 | 170.6 | 173 | 156.3 | 155.5 | 146.1 | 37.3 | 19.6 | 61.7 | 2.9 | 257.3 | 3.8 | 25.6 | 45.1 | 25.5 | 45.4 | 34.2 | 54 | 122.5 | 45 | 57.6 | 50.3 | 83.5 | 39.9 | 23.6 | 252.6 | 164 | 191.1 | 201.7 | 247 | 185.4 | 164.9 | 201.7
2154.1 | 1991.1 | -5.8 | 0 | 0 | 170.5 | 172.5 | 156 | 155.2 | 145.8 | 37.3 | 19.6 | 61.6 | 2.8 | 250.2 | 3.8 | 25.9 | 51.1 | 25.6 | 45.4 | 34.3 | 54 | 121.7 | 44.8 | 57.6 | 50.3 | 83.3 | 40 | 23.6 | 252.3 | 163.7 | 191 | 201.5 | 246.8 | 185.1 | 164.6 | 201.4
2155.1 | 1992.1 | -5.3 | 0 | 0 | 170.3 | 172.1 | 155.8 | 155 | 145.5 | 37.3 | 19.6 | 61.6 | 2.8 | 253.8 | 3.8 | 26.5 | 49.7 | 25.8 | 45.4 | 34.3 | 54.1 | 121.4 | 44.3 | 57.5 | 50.2 | 83.2 | 40.3 | 23.6 | 252 | 163.4 | 190.8 | 201.2 | 246.5 | 184.9 | 164.4 | 201.2
2156.1 | 1993.1 | -5.5 | 0 | 0 | 170 | 172 | 155.5 | 154.9 | 145.2 | 37.2 | 19.6 | 61.5 | 3.5 | 264.5 | 3.8 | 26.5 | 49.9 | 25.9 | 45.5 | 34.3 | 54.2 | 95.4 | 44 | 57.7 | 50.1 | 83.1 | 40.2 | 23.6 | 251.8 | 163.2 | 190.6 | 201 | 246.3 | 184.7 | 164.2 | 201
2157.1 | 1994.1 | -5.7 | 0 | 0 | 169.6 | 171.7 | 155.1 | 154.7 | 145 | 37.1 | 19.6 | 61.4 | 3.7 | 271.3 | 3.9 | 26.6 | 50.2 | 25.8 | 45.5 | 34.4 | 54.3 | 83.1 | 43.9 | 57.7 | 50.1 | 82.9 | 41.1 | 23.7 | 251.5 | 162.9 | 190.4 | 200.8 | 246 | 184.4 | 164 | 200.7
2158.1 | 1995.1 | -5.9 | 0 | 0 | 168.9 | 171.4 | 154.9 | 154.4 | 144.9 | 37 | 19.6 | 61.4 | 3.5 | 261.7 | 4.1 | 26.6 | 52.2 | 25.6 | 45.6 | 34.4 | 54.6 | 79.8 | 44.3 | 57.8 | 50.1 | 82.8 | 41.4 | 23.7 | 251.2 | 162.7 | 190.2 | 200.6 | 245.8 | 184.1 | 163.7 | 200.5
2159.1 | 1996.1 | -6.2 | 0 | 0 | 168.6 | 171.2 | 154.7 | 154.2 | 144.7 | 37 | 19.6 | 61.3 | 3.8 | 259.2 | 4.2 | 26.8 | 50.5 | 25.5 | 45.7 | 34.3 | 54.7 | 76.8 | 44 | 57.8 | 50 | 82.7 | 41.6 | 23.7 | 251 | 162.5 | 190 | 200.3 | 245.6 | 184 | 163.6 | 200.3
2160.1 | 1997.1 | -6.1 | 0 | 0 | 168.6 | 171 | 154.6 | 154 | 144.5 | 37 | 19.6 | 61.2 | 3.4 | 264.2 | 4.2 | 27 | 47.4 | 25.5 | 45.7 | 34.4 | 54.8 | 73.8 | 44 | 57.7 | 49.8 | 82.6 | 41.8 | 23.7 | 250.7 | 162.2 | 189.7 | 200.1 | 245.3 | 183.8 | 163.4 | 200.1
2161.1 | 1998.1 | -5.8 | 0 | 0 | 168.3 | 170.8 | 154.4 | 153.9 | 144.1 | 37 | 19.6 | 61.2 | 3.2 | 267 | 4.3 | 27 | 44.2 | 25.4 | 45.8 | 34.5 | 55 | 71.3 | 44 | 57.8 | 49.7 | 82.5 | 41.8 | 23.7 | 250.5 | 161.9 | 189.6 | 199.8 | 245.1 | 183.5 | 163.1 | 199.9
2162.1 | 1999.1 | -5 | 0 | 0 | 168.2 | 170.2 | 154.2 | 153.7 | 143.9 | 37 | 19.6 | 61.2 | 3.2 | 260.8 | 4.8 | 26.9 | 42 | 25.4 | 45.9 | 34.5 | 55.1 | 69.6 | 43.6 | 57.8 | 49.7 | 82.3 | 41.9 | 23.7 | 250.2 | 161.7 | 189.4 | 199.7 | 244.8 | 183.2 | 162.9 | 199.6
2163.1 | 2000.1 | -5.2 | 0 | 0 | 168.1 | 169.9 | 154 | 153.5 | 143.6 | 37 | 19.6 | 61.1 | 2.8 | 248.3 | 4.7 | 26.8 | 40.3 | 25.4 | 45.9 | 34.6 | 55.3 | 68.1 | 44.1 | 57.8 | 49.8 | 82.2 | 41.8 | 23.7 | 249.9 | 161.6 | 189.2 | 199.4 | 244.6 | 182.9 | 162.7 | 199.4
2164.1 | 2001.1 | -5.5 | 0 | 0 | 168 | 169.8 | 153.7 | 153.3 | 143.2 | 36.9 | 19.6 | 61.1 | 3.1 | 267.1 | 4.5 | 26.8 | 39.3 | 25.4 | 46 | 34.5 | 55.6 | 67.6 | 43.9 | 57.9 | 49.8 | 82 | 41.6 | 23.7 | 249.7 | 161.3 | 188.9 | 199.2 | 244.3 | 182.6 | 162.4 | 199.2
2165.1 | 2002.1 | -5.6 | 0 | 0 | 167.8 | 169.6 | 153.5 | 153 | 143 | 36.9 | 19.6 | 61 | 3.2 | 266.1 | 4.5 | 27 | 39 | 25.4 | 46 | 34.4 | 55.8 | 66.9 | 43.9 | 57.9 | 49.9 | 81.9 | 41.3 | 23.6 | 249.4 | 161 | 188.7 | 198.9 | 244.1 | 182.4 | 162.2 | 199
2166.1 | 2003.1 | -5 | 0 | 0 | 167.6 | 169.2 | 153.3 | 152.8 | 142.8 | 36.9 | 19.6 | 61 | 3.4 | 241.6 | 4.2 | 27 | 38.4 | 25.2 | 46.1 | 34.4 | 56.1 | 66.6 | 44.5 | 57.9 | 49.8 | 81.8 | 41.1 | 23.6 | 249.1 | 160.8 | 188.4 | 198.7 | 243.8 | 182.2 | 162 | 198.7
2167.1 | 2004.1 | -4.9 | 0 | 0 | 167.4 | 168.9 | 153.1 | 152.6 | 142.5 | 36.9 | 19.6 | 60.9 | 3.1 | 246.9 | 3.9 | 27.1 | 38.1 | 25.2 | 46.1 | 34.4 | 56.4 | 66.4 | 44.3 | 57.9 | 49.7 | 81.6 | 40.9 | 23.5 | 248.9 | 160.6 | 188.2 | 198.5 | 243.6 | 181.9 | 161.7 | 198.5
2168.1 | 2005.1 | -4.6 | 0 | 0 | 167 | 168.4 | 152.9 | 152.4 | 142.2 | 37 | 19.6 | 60.9 | 3 | 271.3 | 4.1 | 27.1 | 37.8 | 25.1 | 46.2 | 34.4 | 56.7 | 66.1 | 44.1 | 57.9 | 49.6 | 81.5 | 40.6 | 23.6 | 248.6 | 160.4 | 188 | 198.3 | 243.3 | 181.6 | 161.4 | 198.3
2169.1 | 2006.1 | -4 | 0 | 0 | 166.7 | 168 | 152.7 | 152.2 | 142.1 | 37 | 19.6 | 60.8 | 2.9 | 263.7 | 4.1 | 27.3 | 37.3 | 25 | 46.2 | 34.4 | 57 | 66 | 44.6 | 57.9 | 49.6 | 81.3 | 40.4 | 23.6 | 248.4 | 160.2 | 187.8 | 198.1 | 243.1 | 181.4 | 161.2 | 198
2170.1 | 2007.1 | -3.2 | 0 | 0 | 166.6 | 167.7 | 152.5 | 151.9 | 142 | 37 | 19.6 | 60.8 | 2.9 | 218.1 | 4.8 | 27.2 | 36.9 | 25 | 46.2 | 34.5 | 57.2 | 65.9 | 43.8 | 57.9 | 49.7 | 81.2 | 40.2 | 23.5 | 248.1 | 160 | 187.6 | 197.8 | 242.9 | 181.1 | 160.9 | 197.8
2171.1 | 2008.1 | -2.6 | 0 | 0 | 166.5 | 167.3 | 152.2 | 151.6 | 141.9 | 37 | 19.6 | 60.7 | 2.8 | 245.8 | 5.7 | 27.3 | 36.1 | 25 | 46.3 | 34.4 | 57.4 | 65.4 | 43.4 | 57.9 | 49.8 | 81.1 | 40 | 23.5 | 247.8 | 159.8 | 187.3 | 197.6 | 242.6 | 180.9 | 160.6 | 197.6
2172.1 | 2009.1 | -2.7 | 0 | 0 | 165.8 | 167 | 152.1 | 151.5 | 141.7 | 37 | 19.6 | 60.7 | 3.2 | 257.6 | 5.8 | 27 | 35.7 | 25 | 46.3 | 34.4 | 57.8 | 65.3 | 43.8 | 57.9 | 49.8 | 81 | 40 | 23.5 | 247.6 | 159.5 | 187.2 | 197.4 | 242.4 | 180.6 | 160.4 | 197.4
2173.1 | 2010.1 | -3.6 | 0 | 0 | 165.3 | 166.9 | 151.9 | 151.3 | 141.6 | 37 | 19.6 | 60.6 | 3.7 | 224.6 | 5.5 | 26.8 | 34.9 | 24.8 | 46.3 | 34.4 | 57.9 | 65.3 | 42.4 | 57.9 | 49.9 | 80.9 | 40 | 23.5 | 247.3 | 159.2 | 186.9 | 197.2 | 242.1 | 180.4 | 160.1 | 197.2
2174.1 | 2011.1 | -3.6 | 0 | 0 | 165.4 | 166.8 | 151.6 | 151 | 141.4 | 37 | 19.6 | 60.5 | 3.4 | 239.5 | 5.4 | 27 | 34.3 | 24.6 | 46.3 | 34.4 | 58.1 | 65.5 | 42.7 | 57.9 | 49.9 | 80.8 | 39.9 | 23.5 | 247.1 | 159 | 186.8 | 197 | 241.9 | 180.2 | 159.9 | 196.9
2175.1 | 2012.1 | -3.5 | 0 | 0 | 165.4 | 166.4 | 151.4 | 150.8 | 140.8 | 37 | 19.6 | 60.5 | 2.9 | 246.1 | 5.5 | 27.5 | 34.1 | 24.5 | 46.4 | 34.4 | 58.3 | 65.8 | 43.4 | 57.9 | 49.9 | 80.7 | 39.8 | 23.5 | 246.8 | 158.7 | 186.6 | 196.7 | 241.6 | 179.9 | 159.6 | 196.7
2176.1 | 2013.1 | -4.3 | 0 | 0 | 165.5 | 166.1 | 151.2 | 150.7 | 140 | 37.1 | 19.6 | 60.4 | 3 | 210.8 | 4.8 | 27.8 | 33.8 | 24.5 | 46.4 | 34.5 | 58.4 | 66.3 | 42.8 | 57.9 | 49.9 | 80.6 | 39.9 | 23.5 | 246.5 | 158.4 | 186.3 | 196.5 | 241.4 | 179.7 | 159.4 | 196.5
2177.1 | 2014.1 | -4 | 0 | 0 | 165.3 | 166.1 | 151.1 | 150.5 | 139.9 | 37.1 | 19.6 | 60.3 | 3.3 | 209.2 | 4.8 | 27.8 | 33.8 | 24.5 | 46.4 | 34.5 | 58.6 | 66.8 | 43.1 | 57.9 | 49.8 | 80.5 | 39.9 | 23.5 | 246.3 | 158.1 | 186 | 196.3 | 241.2 | 179.5 | 159.2 | 196.3
2178.1 | 2015.1 | -3.9 | 0 | 0 | 164.8 | 165.9 | 150.8 | 150.3 | 139.8 | 37.1 | 19.6 | 60.2 | 3.2 | 206.5 | 4.5 | 28.1 | 33.7 | 24.4 | 46.4 | 34.6 | 58.8 | 67.3 | 43 | 57.9 | 49.7 | 80.5 | 39.8 | 23.5 | 246 | 157.8 | 185.8 | 196.1 | 240.9 | 179.4 | 158.9 | 196.1
2179.1 | 2016.1 | -4 | 0 | 0 | 164.4 | 165.9 | 150.5 | 150.1 | 139.7 | 37.1 | 19.6 | 60.2 | 3.3 | 237.1 | 4.1 | 28.3 | 33.7 | 24.3 | 46.4 | 34.5 | 58.8 | 68 | 42.2 | 57.9 | 49.7 | 80.4 | 39.7 | 23.5 | 245.8 | 157.6 | 185.7 | 196 | 240.7 | 179.2 | 158.6 | 195.9
2180.1 | 2017.1 | -4.1 | 0 | 0 | 164.1 | 165.7 | 150.2 | 149.9 | 139.5 | 37 | 19.6 | 60.1 | 3 | 244.8 | 4.4 | 28.2 | 33.7 | 24.3 | 46.4 | 34.5 | 59 | 68.9 | 42.5 | 57.9 | 49.8 | 80.3 | 39.9 | 23.4 | 245.5 | 157.3 | 185.4 | 195.7 | 240.4 | 178.9 | 158.3 | 195.7
2181.1 | 2018.1 | -5.1 | 0 | 0 | 163.8 | 165.8 | 150 | 149.7 | 139.4 | 37 | 19.6 | 60.1 | 3 | 221.9 | 5.1 | 27.6 | 33.8 | 24.3 | 46.4 | 34.5 | 59.1 | 70 | 42.2 | 57.8 | 49.7 | 80.4 | 39.7 | 23.4 | 245.3 | 157.1 | 185.2 | 195.5 | 240.2 | 178.5 | 158 | 195.5
2182.1 | 2019.1 | -5.7 | 0 | 0 | 163.7 | 165.7 | 149.9 | 149.4 | 139.2 | 37 | 19.6 | 60 | 3.3 | 239.8 | 5.9 | 27.5 | 33.7 | 24.3 | 46.4 | 34.5 | 59.1 | 71.3 | 41.7 | 57.8 | 49.7 | 80.4 | 39.8 | 23.4 | 245 | 156.8 | 185 | 195.3 | 239.9 | 178.3 | 157.7 | 195.2
2183.1 | 2020.1 | -6 | 0 | 0 | 163.6 | 165.5 | 149.8 | 149.3 | 139.1 | 37 | 19.6 | 60 | 3.1 | 231.7 | 6.3 | 27.6 | 33.4 | 24.3 | 46.4 | 34.5 | 59.3 | 72.5 | 42.2 | 57.9 | 49.7 | 80.4 | 39.8 | 23.4 | 244.7 | 156.6 | 184.8 | 195.1 | 239.7 | 178 | 157.5 | 195
2184.1 | 2021.1 | -5.7 | 0 | 0 | 163.5 | 165.3 | 149.5 | 149.2 | 139.1 | 37 | 19.6 | 59.9 | 3 | 226.5 | 6.2 | 27.4 | 33.4 | 24.3 | 46.4 | 34.5 | 59.3 | 73.7 | 41.3 | 57.9 | 49.7 | 80.4 | 39.7 | 23.4 | 244.5 | 156.3 | 184.6 | 194.9 | 239.5 | 177.7 | 157.3 | 194.8
2185.1 | 2022.1 | -5.6 | 0 | 0 | 163 | 164.9 | 149.2 | 149 | 139.2 | 37 | 19.6 | 59.9 | 3.1 | 231.3 | 5.9 | 27.3 | 33 | 24.3 | 46.4 | 34.5 | 59.4 | 75 | 41 | 57.9 | 49.8 | 80.5 | 39.8 | 23.3 | 244.2 | 156.1 | 184.4 | 194.7 | 239.2 | 177.4 | 157 | 194.6
2186.1 | 2023.1 | -5.8 | 0 | 0 | 162.7 | 164.6 | 148.9 | 148.7 | 139.2 | 36.9 | 19.6 | 59.8 | 3.2 | 252 | 6.3 | 27.4 | 32.8 | 24.3 | 46.5 | 34.4 | 59.6 | 76.4 | 42.3 | 57.9 | 49.8 | 80.4 | 39.9 | 23.3 | 244 | 155.9 | 184.1 | 194.4 | 239 | 177.1 | 156.7 | 194.4
2187.1 | 2024.1 | -5.2 | 0 | 0 | 163 | 164.2 | 148.7 | 148.5 | 138.9 | 36.9 | 19.6 | 59.8 | 3.1 | 245.4 | 6.7 | 27.6 | 32.4 | 24.3 | 46.5 | 34.4 | 59.6 | 78 | 41.1 | 57.9 | 49.8 | 80.4 | 40 | 23.3 | 243.7 | 155.7 | 183.7 | 194.2 | 238.7 | 176.9 | 156.5 | 194.2
2188.1 | 2025.1 | -4.5 | 0 | 0 | 163 | 163.9 | 148.6 | 148.3 | 138.6 | 37 | 19.6 | 59.7 | 2.9 | 251.8 | 6.9 | 27.7 | 32.3 | 24.3 | 46.4 | 34.4 | 59.7 | 79.6 | 41.3 | 57.9 | 49.7 | 80.3 | 40.2 | 23.3 | 243.5 | 155.4 | 183.5 | 193.9 | 238.5 | 176.7 | 156.2 | 193.9
2189.1 | 2026.1 | -3.8 | 0 | 0 | 162.7 | 163.6 | 148.5 | 148.1 | 138.3 | 37 | 19.6 | 59.7 | 3.1 | 248.3 | 6.7 | 27.8 | 32.4 | 24.3 | 46.4 | 34.4 | 59.8 | 81.2 | 42.1 | 57.8 | 49.5 | 80.1 | 40.3 | 23.3 | 243.2 | 155.2 | 183.2 | 193.7 | 238.2 | 176.4 | 156 | 193.8
2190.1 | 2027.1 | -4.2 | 0 | 0 | 162.5 | 163.5 | 148.2 | 147.9 | 138.3 | 37 | 19.6 | 59.7 | 3.1 | 243.3 | 6.3 | 27.4 | 31.7 | 24.3 | 46.4 | 34.4 | 59.7 | 82.6 | 40.9 | 57.9 | 49.4 | 80 | 40.2 | 23.3 | 243 | 154.9 | 183 | 193.5 | 238 | 176.1 | 155.7 | 193.5
2191.1 | 2028.1 | -4.4 | 0 | 0 | 162.1 | 163.1 | 147.8 | 147.8 | 138.3 | 36.9 | 19.7 | 59.7 | 2.8 | 249 | 5.9 | 27.1 | 31.2 | 24.3 | 46.4 | 34.3 | 59.8 | 84.2 | 41.4 | 57.9 | 49.4 | 79.8 | 39.8 | 23.3 | 242.7 | 154.7 | 182.9 | 193.3 | 237.8 | 175.9 | 155.5 | 193.3
2192.1 | 2029.1 | -4.3 | 0 | 0 | 161.7 | 162.8 | 147.6 | 147.6 | 138.1 | 36.9 | 19.7 | 59.7 | 2.8 | 248.6 | 5.6 | 27 | 31 | 24.3 | 46.4 | 34.3 | 59.9 | 85.8 | 41.8 | 57.9 | 49.5 | 79.7 | 39.6 | 23.2 | 242.5 | 154.5 | 182.6 | 193.1 | 237.5 | 175.7 | 155.3 | 193.1
2193.1 | 2030.1 | -4.9 | 0 | 0 | 161.4 | 162.7 | 147.3 | 147.3 | 137.9 | 36.9 | 19.7 | 59.6 | 2.9 | 251 | 4.9 | 26.7 | 30.7 | 24.3 | 46.4 | 34.4 | 59.8 | 87.2 | 40.8 | 57.9 | 49.6 | 79.5 | 39.4 | 23.2 | 242.2 | 154.2 | 182.2 | 192.8 | 237.3 | 175.5 | 155.1 | 192.9
2194.1 | 2031.1 | -5.6 | 0 | 0 | 161.1 | 162.5 | 147.1 | 147 | 137.6 | 36.9 | 19.7 | 59.6 | 3.1 | 256.9 | 4 | 26.8 | 30.6 | 24.2 | 46.4 | 34.3 | 59.9 | 88.5 | 40.8 | 57.9 | 49.6 | 79.3 | 39.5 | 23.2 | 242 | 154 | 182 | 192.6 | 237 | 175.4 | 154.9 | 192.7
2195.1 | 2032.1 | -5.7 | 0 | 0 | 160.7 | 162 | 147 | 146.9 | 137.4 | 36.9 | 19.7 | 59.6 | 2.9 | 252.9 | 3.5 | 27.2 | 30.6 | 24.1 | 46.4 | 34.4 | 59.9 | 89.6 | 40.6 | 57.9 | 49.5 | 79.1 | 39.5 | 23.2 | 241.7 | 153.8 | 181.8 | 192.5 | 236.8 | 175.2 | 154.7 | 192.5
2196.1 | 2033.1 | -5.5 | 0 | 0 | 160.2 | 161.4 | 146.9 | 146.7 | 137.3 | 36.9 | 19.7 | 59.5 | 3.2 | 243.1 | 3.5 | 27.6 | 31.1 | 24.1 | 46.4 | 34.4 | 59.9 | 90.5 | 40.3 | 57.9 | 49.5 | 78.9 | 39.6 | 23.2 | 241.5 | 153.6 | 181.6 | 192.3 | 236.5 | 174.9 | 154.4 | 192.3
2197.1 | 2034.1 | -5 | 0 | 0 | 159.9 | 161.3 | 146.7 | 146.4 | 137.3 | 36.8 | 19.7 | 59.5 | 3.1 | 239.5 | 3.6 | 27.7 | 31.1 | 24.1 | 46.4 | 34.4 | 59.9 | 91.7 | 40.2 | 57.9 | 49.6 | 78.8 | 39.7 | 23.1 | 241.2 | 153.4 | 181.3 | 192 | 236.3 | 174.6 | 154.2 | 192.1
2198.1 | 2035.1 | -5 | 0 | 0 | 159.8 | 161.4 | 146.5 | 146.2 | 137.3 | 36.9 | 19.7 | 59.4 | 3 | 244.2 | 3.4 | 27.9 | 31.2 | 24 | 46.4 | 34.4 | 59.9 | 92.7 | 40.1 | 57.9 | 49.5 | 78.8 | 39.6 | 23.1 | 240.9 | 153.2 | 181.1 | 191.7 | 236.1 | 174.3 | 154 | 191.8
2199.1 | 2036.1 | -4.9 | 0 | 0 | 159.5 | 161.6 | 146.4 | 146.1 | 137.1 | 36.9 | 19.7 | 59.4 | 3.1 | 242 | 3.4 | 28 | 31.1 | 24 | 46.4 | 34.4 | 59.9 | 93.7 | 40.2 | 57.9 | 49.6 | 78.7 | 39.3 | 23.1 | 240.7 | 153 | 180.9 | 191.5 | 235.8 | 174.2 | 153.8 | 191.6
2200.1 | 2037.1 | -4.4 | 0 | 0 | 159 | 161.5 | 146.2 | 145.9 | 137 | 36.9 | 19.7 | 59.3 | 3.1 | 214 | 3.2 | 28 | 31.2 | 23.9 | 46.4 | 34.4 | 59.9 | 94.7 | 40.5 | 57.9 | 49.7 | 78.7 | 39.2 | 23 | 240.4 | 152.7 | 180.7 | 191.4 | 235.6 | 174 | 153.6 | 191.4
2201.1 | 2038.1 | -5.1 | 0 | 0 | 158.6 | 161.3 | 146 | 145.7 | 137.1 | 36.8 | 19.7 | 59.3 | 3.4 | 222.5 | 2.9 | 28.1 | 31.2 | 23.9 | 46.4 | 34.4 | 60 | 95.5 | 40.5 | 57.9 | 49.7 | 78.7 | 39.1 | 23 | 240.2 | 152.5 | 180.6 | 191.2 | 235.4 | 173.7 | 153.3 | 191.3
2202.1 | 2039.1 | -5 | 0 | 0 | 158.3 | 161.3 | 145.7 | 145.5 | 137 | 36.7 | 19.7 | 59.3 | 3.1 | 245 | 2.8 | 28 | 31.2 | 23.8 | 46.4 | 34.4 | 60 | 96.4 | 40.6 | 57.9 | 49.6 | 78.6 | 39 | 22.9 | 239.9 | 152.2 | 180.3 | 191 | 235.1 | 173.4 | 153.2 | 191
2203.1 | 2040.1 | -4.7 | 0 | 0 | 158.1 | 161.4 | 145.5 | 145.3 | 136.7 | 36.6 | 19.7 | 59.2 | 3.5 | 253.8 | 2.7 | 27.8 | 31.3 | 23.8 | 46.4 | 34.4 | 60 | 97.2 | 40.7 | 57.9 | 49.6 | 78.5 | 38.8 | 22.9 | 239.7 | 151.9 | 180 | 190.8 | 234.9 | 173.3 | 152.9 | 190.8
2204.1 | 2041.1 | -4.9 | 0 | 0 | 157.9 | 161.4 | 145.2 | 145.1 | 136.5 | 36.6 | 19.7 | 59.2 | 3.5 | 238.2 | 2.5 | 27.9 | 31.5 | 23.8 | 46.4 | 34.4 | 60 | 97.9 | 40.7 | 57.9 | 49.6 | 78.4 | 38.6 | 22.9 | 239.4 | 151.7 | 179.7 | 190.6 | 234.6 | 173.1 | 152.8 | 190.6
2205.1 | 2042.1 | -4.4 | 0 | 0 | 157.6 | 161.2 | 144.9 | 144.9 | 136.3 | 36.6 | 19.7 | 59.2 | 3.1 | 213.4 | 2.6 | 27.7 | 31.7 | 23.8 | 46.4 | 34.3 | 60 | 98.7 | 40.6 | 57.9 | 49.7 | 78.3 | 38.5 | 22.8 | 239.2 | 151.5 | 179.5 | 190.4 | 234.4 | 172.9 | 152.7 | 190.4
2206.1 | 2043.1 | -4.2 | 0 | 0 | 157.2 | 160.8 | 144.8 | 144.7 | 136.1 | 36.5 | 19.7 | 59.2 | 3.1 | 206.3 | 2.5 | 27.6 | 31.3 | 23.8 | 46.4 | 34.3 | 60 | 99.4 | 40.4 | 57.9 | 49.8 | 78.1 | 38.4 | 22.9 | 238.9 | 151.3 | 179.4 | 190.2 | 234.2 | 172.7 | 152.5 | 190.2
2207.1 | 2044.1 | -4.2 | 0 | 0 | 156.9 | 160.2 | 144.6 | 144.5 | 135.9 | 36.4 | 19.7 | 59.1 | 3.2 | 216.6 | 2 | 27.9 | 30.8 | 23.7 | 46.4 | 34.3 | 60 | 100 | 40.4 | 57.9 | 49.8 | 77.9 | 38.3 | 22.9 | 238.7 | 151.1 | 179.2 | 190 | 233.9 | 172.5 | 152.3 | 190
2208.1 | 2045.1 | -3.9 | 0 | 0 | 156.7 | 160 | 144.5 | 144.4 | 135.6 | 36.3 | 19.7 | 59 | 3.3 | 233.9 | 1.9 | 27.8 | 30.7 | 23.7 | 46.3 | 34.3 | 60 | 100.5 | 40.2 | 57.9 | 49.7 | 77.7 | 38.1 | 22.9 | 238.4 | 150.9 | 178.9 | 189.7 | 233.7 | 172.2 | 152 | 189.7
2209.1 | 2046.1 | -4.5 | 0 | 0 | 156.6 | 160.2 | 144.4 | 144.1 | 135.3 | 36.3 | 19.7 | 59 | 3.5 | 252.6 | 1.9 | 27.1 | 30.3 | 23.6 | 46.3 | 34.3 | 59.9 | 101.1 | 39.8 | 57.8 | 49.7 | 77.6 | 37.9 | 22.8 | 238.2 | 150.6 | 178.7 | 189.5 | 233.5 | 172 | 151.9 | 189.6
2210.1 | 2047.1 | -4.1 | 0 | 0 | 156.6 | 160.1 | 144.3 | 143.9 | 135.3 | 36.2 | 19.7 | 58.9 | 3.9 | 266.5 | 2.3 | 26.8 | 30.3 | 23.6 | 46.3 | 34.3 | 59.9 | 101.7 | 39.6 | 57.8 | 49.7 | 77.4 | 38 | 22.8 | 237.9 | 150.3 | 178.5 | 189.3 | 233.2 | 171.9 | 151.7 | 189.4
2211.1 | 2048.1 | -4.4 | 0 | 0 | 156.3 | 159.9 | 144 | 143.8 | 135.2 | 36.1 | 19.7 | 58.9 | 3.9 | 263.6 | 2.8 | 26.8 | 30.3 | 23.6 | 46.3 | 34.2 | 59.9 | 102.2 | 39.6 | 57.8 | 49.7 | 77.2 | 38.1 | 22.8 | 237.7 | 150.1 | 178.3 | 189.1 | 233 | 171.7 | 151.5 | 189.1
2212.1 | 2049.1 | -4.3 | 0 | 0 | 156.1 | 159.6 | 143.7 | 143.6 | 135 | 36.1 | 19.7 | 58.8 | 3.7 | 251.8 | 3.2 | 26.5 | 30.3 | 23.6 | 46.3 | 34.1 | 59.9 | 102.6 | 39.6 | 57.8 | 49.7 | 77.1 | 38.1 | 22.8 | 237.4 | 150 | 178.1 | 188.9 | 232.8 | 171.5 | 151.2 | 188.9
2213.1 | 2050.1 | -4.1 | 0 | 0 | 155.8 | 159.5 | 143.5 | 143.4 | 134.6 | 36 | 19.7 | 58.8 | 3.6 | 223.4 | 3.8 | 26.4 | 30.1 | 23.6 | 46.3 | 34.1 | 59.9 | 102.8 | 39.3 | 57.8 | 49.7 | 76.9 | 38 | 22.7 | 237.2 | 149.8 | 177.9 | 188.7 | 232.5 | 171.3 | 151 | 188.8
2214.1 | 2051.1 | -4.6 | 0 | 0 | 155.7 | 159.2 | 143.4 | 143.3 | 134.2 | 36 | 19.7 | 58.7 | 3 | 239.7 | 5.5 | 26.5 | 30.2 | 23.6 | 46.3 | 34 | 59.9 | 103.2 | 39.3 | 57.8 | 49.7 | 76.7 | 37.8 | 22.7 | 236.9 | 149.6 | 177.6 | 188.4 | 232.3 | 171.1 | 150.8 | 188.5
2215.1 | 2052.1 | -5 | 0 | 0 | 155.5 | 158.7 | 143.3 | 143.1 | 134 | 36 | 19.7 | 58.7 | 3.1 | 249.8 | 7.1 | 26.7 | 30.6 | 23.6 | 46.3 | 34 | 59.9 | 103.6 | 39.2 | 57.7 | 49.6 | 76.5 | 37.6 | 22.9 | 236.7 | 149.3 | 177.3 | 188.2 | 232 | 171 | 150.7 | 188.4
2216.1 | 2053.1 | -5.3 | 0 | 0 | 155.3 | 158.5 | 143.2 | 143 | 133.9 | 36 | 19.7 | 58.6 | 2.9 | 242.7 | 7.8 | 26.7 | 30.8 | 23.6 | 46.3 | 34 | 59.9 | 104.1 | 39.1 | 57.7 | 49.6 | 76.4 | 37.4 | 22.9 | 236.4 | 149.1 | 177.1 | 188.1 | 231.8 | 170.8 | 150.4 | 188.1
2217.1 | 2054.1 | -5.2 | 0 | 0 | 155.1 | 158.3 | 143 | 142.8 | 133.8 | 35.9 | 19.7 | 58.6 | 2.8 | 241.1 | 8.2 | 27 | 31.1 | 23.6 | 46.3 | 34 | 59.9 | 104.4 | 39 | 57.7 | 49.6 | 76.3 | 37.4 | 23 | 236.2 | 148.9 | 176.9 | 187.9 | 231.6 | 170.5 | 150.1 | 187.9
2218.1 | 2055.1 | -4.8 | 0 | 0 | 154.8 | 157.8 | 142.8 | 142.6 | 133.7 | 35.8 | 19.7 | 58.5 | 2.9 | 238.2 | 8.1 | 27.3 | 31.1 | 23.6 | 46.3 | 34 | 59.9 | 104.7 | 38.8 | 57.7 | 49.6 | 76.1 | 37.5 | 23.1 | 235.9 | 148.7 | 176.8 | 187.7 | 231.4 | 170.2 | 149.9 | 187.7
2219.1 | 2056.1 | -4.9 | 0 | 0 | 154.5 | 157.6 | 142.7 | 142.4 | 133.4 | 35.7 | 19.7 | 58.5 | 3.2 | 247.6 | 7.2 | 27.6 | 31 | 23.6 | 46.3 | 34 | 59.8 | 104.9 | 38.7 | 57.6 | 49.6 | 75.9 | 37.4 | 23.1 | 235.7 | 148.4 | 176.6 | 187.5 | 231.1 | 169.8 | 149.6 | 187.5
2220.1 | 2057.1 | -4.9 | 0 | 0 | 154.3 | 157.4 | 142.4 | 142.2 | 133.1 | 35.7 | 19.7 | 58.5 | 3.1 | 230.3 | 6.7 | 27.7 | 30.8 | 23.6 | 46.3 | 34 | 59.8 | 105.2 | 38.5 | 57.6 | 49.6 | 75.8 | 37.4 | 23.1 | 235.4 | 148.1 | 176.4 | 187.3 | 230.9 | 169.7 | 149.4 | 187.3
2221.1 | 2058.1 | -4.3 | 0 | 0 | 154.1 | 157.2 | 142.2 | 142 | 132.9 | 35.6 | 19.7 | 58.5 | 3.1 | 247.5 | 6.9 | 27.2 | 30.5 | 23.7 | 46.3 | 34 | 59.8 | 105.5 | 38.2 | 57.6 | 49.7 | 75.7 | 37.4 | 23 | 235.2 | 148 | 176.2 | 187.1 | 230.7 | 169.5 | 149.1 | 187.1
2222.1 | 2059.1 | -5 | 0 | 0 | 154 | 156.9 | 142 | 141.8 | 132.9 | 35.6 | 19.7 | 58.5 | 3 | 238.9 | 7.2 | 27 | 30.2 | 23.7 | 46.3 | 34.1 | 59.8 | 105.8 | 38.1 | 57.6 | 49.7 | 75.6 | 37.4 | 23 | 234.9 | 147.8 | 176.1 | 186.9 | 230.4 | 169.4 | 149 | 186.9
2223.1 | 2060.1 | -4.6 | 0 | 0 | 153.8 | 156.5 | 141.9 | 141.6 | 133 | 35.6 | 19.7 | 58.4 | 2.9 | 249.6 | 7.4 | 26.8 | 30 | 23.7 | 46.3 | 34.1 | 59.8 | 106.1 | 37.8 | 57.6 | 49.7 | 75.5 | 37.4 | 22.9 | 234.7 | 147.6 | 175.9 | 186.7 | 230.2 | 169.3 | 148.8 | 186.7
2224.1 | 2061.1 | -4.2 | 0 | 0 | 153.6 | 156.6 | 141.8 | 141.5 | 132.9 | 35.5 | 19.7 | 58.3 | 3 | 268.4 | 6.9 | 26.7 | 29.7 | 23.8 | 46.2 | 34 | 59.8 | 106.4 | 37.8 | 57.5 | 49.7 | 75.5 | 37.3 | 22.9 | 234.4 | 147.4 | 175.7 | 186.5 | 230 | 169.1 | 148.6 | 186.6
2225.1 | 2062.1 | -4.6 | 0 | 0 | 153.5 | 156.6 | 141.6 | 141.3 | 132.9 | 35.4 | 19.7 | 58.3 | 2.7 | 286.7 | 6.8 | 26.8 | 30.1 | 24 | 46.2 | 34 | 59.8 | 106.6 | 38 | 57.5 | 49.6 | 75.4 | 37.2 | 22.9 | 234.2 | 147.2 | 175.5 | 186.3 | 229.7 | 168.9 | 148.4 | 186.4
2226.1 | 2063.1 | -4.7 | 0 | 0 | 153.3 | 156.4 | 141.4 | 141.1 | 132.8 | 35.3 | 19.7 | 58.2 | 2.9 | 280.6 | 6.8 | 26.7 | 30.5 | 24 | 46.2 | 34 | 59.8 | 106.8 | 38.1 | 57.5 | 49.6 | 75.4 | 37.3 | 22.9 | 233.9 | 147.1 | 175.3 | 186.1 | 229.5 | 168.7 | 148.3 | 186.2
2227.1 | 2064.1 | -4.9 | 0 | 0 | 153.2 | 156.1 | 141.2 | 140.8 | 132.6 | 35.3 | 19.7 | 58.2 | 2.8 | 281.6 | 6.5 | 26.5 | 30.4 | 24.1 | 46.2 | 34 | 59.8 | 107 | 38.2 | 57.5 | 49.6 | 75.4 | 37.3 | 22.9 | 233.7 | 146.8 | 175.1 | 185.9 | 229.3 | 168.5 | 148.1 | 186
2228.1 | 2065.1 | -4.5 | 0 | 0 | 153 | 155.9 | 141.1 | 140.7 | 132.4 | 35.2 | 19.8 | 58.1 | 2.9 | 272.9 | 6.5 | 26.7 | 30.2 | 24.1 | 46.2 | 33.9 | 59.8 | 107.3 | 38.5 | 57.5 | 49.6 | 75.4 | 37.2 | 22.8 | 233.5 | 146.6 | 175 | 185.7 | 229 | 168.2 | 147.9 | 185.8
2229.1 | 2066.1 | -4.2 | 0 | 0 | 152.9 | 155.8 | 140.9 | 140.6 | 132.2 | 35.2 | 19.8 | 58.1 | 3 | 261.8 | 6.3 | 26.9 | 30.1 | 24.1 | 46.2 | 34 | 59.7 | 107.6 | 38.6 | 57.5 | 49.6 | 75.4 | 37.3 | 22.9 | 233.2 | 146.4 | 174.8 | 185.5 | 228.8 | 168 | 147.7 | 185.6
2230.1 | 2067.1 | -4.2 | 0 | 0 | 152.7 | 155.6 | 140.7 | 140.6 | 132.1 | 35.2 | 19.8 | 58.1 | 2.6 | 262.9 | 5.8 | 27.1 | 30.4 | 24 | 46.2 | 34.1 | 59.7 | 107.9 | 38.4 | 57.5 | 49.7 | 75.4 | 37.3 | 22.9 | 233 | 146.3 | 174.5 | 185.3 | 228.6 | 167.8 | 147.5 | 185.4
2231.1 | 2068.1 | -3.7 | 0 | 0 | 152.4 | 155.6 | 140.5 | 140.4 | 131.9 | 35.3 | 19.8 | 58 | 2.3 | 270.3 | 5 | 27.1 | 30.2 | 24 | 46.2 | 34.1 | 59.7 | 108.1 | 38.4 | 57.5 | 49.7 | 75.4 | 37.3 | 22.9 | 232.7 | 146.1 | 174.2 | 185.1 | 228.4 | 167.5 | 147.3 | 185.2
2232.1 | 2069.1 | -3.7 | 0 | 0 | 152.1 | 155.5 | 140.3 | 140.3 | 131.7 | 35.3 | 19.8 | 58 | 2.7 | 263.9 | 4.6 | 26.7 | 30.2 | 24 | 46.2 | 34.1 | 59.7 | 108.2 | 38.5 | 57.5 | 49.6 | 75.4 | 37.3 | 23 | 232.5 | 145.8 | 174 | 184.9 | 228.1 | 167.4 | 147.1 | 185
2233.1 | 2070.1 | -4.1 | 0 | 0 | 151.9 | 155.3 | 140.1 | 140.1 | 131.7 | 35.3 | 19.8 | 57.9 | 2.6 | 247.5 | 4.5 | 26.7 | 30.5 | 23.9 | 46.2 | 34.1 | 59.7 | 108.3 | 38.5 | 57.5 | 49.6 | 75.4 | 37.3 | 22.9 | 232.2 | 145.5 | 173.7 | 184.7 | 227.9 | 167.2 | 146.9 | 184.8
2234.1 | 2071.1 | -3.5 | 0 | 0 | 151.7 | 155 | 140 | 139.8 | 131.7 | 35.4 | 19.8 | 57.9 | 2.8 | 252 | 4.8 | 26.8 | 30.6 | 23.9 | 46.2 | 34.1 | 59.7 | 108.5 | 38.5 | 57.4 | 49.6 | 75.5 | 37.5 | 22.9 | 232 | 145.3 | 173.5 | 184.6 | 227.7 | 166.9 | 146.7 | 184.6

## First Electrical Failures
SCDU3: No full failure but significant degradation as illustrated by increasing current on source path 1 (C3A1) | Time (s) | Offset Time (s) | C3 A1
| 0 | -163 | -1.2468
| 10 | -153 | 0.082641
| 60 | -103 | 0.076148
| 120 | -43 | 0.076148
| 180 | 17 | 0.071278
| 240 | 77 | 0.072901
| 320 | 157 | 0.084264
| 380 | 217 | 0.082641
| 460 | 297 | 0.081018
| 520 | 357 | 0.072901
| 580 | 417 | 0.072901
| 620 | 457 | 0.071278
| 660 | 497 | 0.074525
| 720 | 557 | 0.081018
| 780 | 617 | 0.082641
| 840 | 677 | 0.077771
| 900 | 737 | 0.077771
| 910 | 747 | 0.074525
| 920 | 757 | 0.074525
| 930 | 767 | 0.072901
| 940 | 777 | 0.072901
| 950 | 787 | 0.072901
| 960 | 797 | 0.072901
| 970 | 807 | 0.074525
| 980 | 817 | 0.074525
| 990 | 827 | 0.074525
| 1000 | 837 | 0.074525
| 1010 | 847 | 0.074525
| 1020 | 857 | 0.074525
| 1030 | 867 | 0.074525
| 1040 | 877 | 0.079395
| 1050 | 887 | 0.082641
| 1060 | 897 | 0.084264
| 1070 | 907 | 0.082641
| 1080 | 917 | 0.087511
| 1090 | 927 | 0.089134
| 1100 | 937 | 0.089134
| 1110 | 947 | 0.089134
| 1120 | 957 | 0.087511
| 1130 | 967 | 0.090758
| 1140 | 977 | 0.087511
| 1150 | 987 | 0.084264
| 1160 | 997 | 0.081018
| 1170 | 1007 | 0.079395
| 1180 | 1017 | 0.079395
| 1200 | 1037 | 0.084264
| 1220 | 1057 | 0.082641
| 1240 | 1077 | 0.082641
| 1260 | 1097 | 0.085888
| 1280 | 1117 | 0.090758
| 1300 | 1137 | 0.092381
| 1320 | 1157 | 0.094004
| 1340 | 1177 | 0.09725
| 1360 | 1197 | 0.10699
| 1380 | 1217 | 0.11348
| 1400 | 1237 | 0.11835
| 1420 | 1257 | 0.12322
| 1440 | 1277 | 0.12972
| 1460 | 1297 | 0.13946
| 1480 | 1317 | 0.1427
| 1500 | 1337 | 0.1427
| 1520 | 1357 | 0.13783
| 1540 | 1377 | 0.14108
| 1560 | 1397 | 0.14595
| 1580 | 1417 | 0.1427
| 1600 | 1437 | 0.13946
| 1620 | 1457 | 0.13459
| 1640 | 1477 | 0.13134
| 1660 | 1497 | 0.12972
| 1680 | 1517 | 0.12322
| 1700 | 1537 | 0.11835
| 1720 | 1557 | 0.11835
| 1740 | 1577 | 0.11998
| 1760 | 1597 | 0.11835
| 1780 | 1617 | 0.11186
| 1800 | 1637 | 0.10699
| 1820 | 1657 | 0.10212
| 1840 | 1677 | 0.10212
| 1860 | 1697 | 0.1005
| 1880 | 1717 | 0.10374
| 1900 | 1737 | 0.1005
| 1920 | 1757 | 0.095627
| 1940 | 1777 | 0.09725
| 1960 | 1797 | 0.09725
| 1980 | 1817 | 0.092381
| 2000 | 1837 | 0.092381
| 2020 | 1857 | 0.081018
| 2040 | 1877 | 0.085888
| 2060 | 1897 | 0.084264
| 2080 | 1917 | 0.085888
| 2100 | 1937 | 0.085888
| 2120 | 1957 | 0.085888
| 2140 | 1977 | 0.089134
| 2160 | 1997 | 0.087511