## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-6 - Circuit Simulator Data Only
Test Date: | 2006-11-06
Circuit Simulator Configurations and connections:
|  | Circuit #1 | Circuit#2 | Circuit #3 | Circuit #4
| CPT Size: | 150 VA | 150 VA | 200 VA | 100 VA
| CPT Grounding: | NOT Grounded | Grounded | Grounded | Grounded
| General Config. | MOV-1 | MOV-1 | MOV-1 | MOV-1
| Cable Type | SR cable (cable item 9) in a bundle of TS cables co-located with Circuit 3 | SR cable (cable item 9) in a bundle of TS cables co-located with Circuit 4 | EPR cable (cable item 2) in a bundle of TS cables co-located with Circuit 3 | XLPO cable (cable item 8) in a bundle of TS cables co-located with Circuit 2
| Wiring Config: | MOV - source centered | MOV - source centered | MOV - source centered | MOV - source centered
| Circuit Path 1: | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source.
| Circuit Path 2: | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source. | Switch Closed: Energized source.
| Circuit Path 3: | no connection | no connection | no connection | no connection
| Circuit Path 4: | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation). | Passive Target: Connected to CPT neutral return through 1.75 k-ohm resistor (un-lit indicator light simulation).
| Circuit Path 5: | Active Target: Connected to Motor Starter and connected to Red conductor. | Active Target: Connected to Motor contactor | Active Target: Connected to Motor contactor | Active Target: Connected to Motor contactor
| Circuit Path 6: | Active Target: Connected to Motor contactor and connected to Wht/Blk conductor. | Active Target: Connected to Motor contactor | Active Target: Connected to Motor contactor | Active Target: Connected to Motor contactor
| Circuit Path 7: | Switch Closed - Connects conductor to CPT nuetral return (ungrounded CPT). | Switch Closed - Connects conductor to CPT nuetral return and to ground (grounded CPT). | Switch Closed - Connects conductor to CPT nuetral return and to ground (grounded CPT). | Switch Closed - Connects conductor to CPT nuetral return and to ground (grounded CPT).
| Circuit Path 8: | Switch open - connected to spare conductor | Switch open - connected to spare conductor | Switch open - connected to spare conductor | Switch open - connected to spare conductor
| Circuit Path 9: | no connection | no connection | no connection | no connection
A Note on Data Conversion and Accuracy:
Each of the voltage and current transducers used produces a 4-20mA signal which is routed through 477ohm precision resistors converting the signal to a nominal 2-10 VDC signal. This DC voltage signal was monitored using a National Instruments PCI-6071E data aquisition (DAQ) card. These data as recorded are presented in the "Raw Test Data" worksheet. The raw data were converted to actual values as shown on the "Converted Test Data" worksheet. The conversion is based on the fact that the 4-20 mA signal corresponds to a full scale reading on the voltage transducers of 0-300 VAC and on the current transducers of 0-5A. Nominal zero point readings for each transducer were taken in a separate test run in order to establish more accurately the zero points for current and voltage measurement. The Zero Point values are provided, and the full run is documented in a separate data file (see 'Zero Points' worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Circuit Fault Summary
Summary of Circuit Faulting Beharior for all Tested Circuits
Circuit 1 | No circuit failures were observed during the burn portion of the test. After burner was extinguished, water spray was activated, and this did lead to circuit failure. No Spurious actuation occurred, rather, shorts to circuit ground led to a fuse blow. Significant degradation of the CPT voltage level is observed prior to ultimate circuit failure. The supply voltage dropped to a value of 94 volts prior to failure.
Circuit 2 | The circuit saw no degradation during the burn period. Water spray was started after the burner was shut off. This led to circuit failure and a fuse blow failure. It appears that mechanism of failure was the source conductor on Path 2 shorting to the grounded conductor on Path 7. Some increase in voltage on the target conductors (4,5,6) is seen, although not sufficient to cause relay chatter or actuation (maximum voltage is about 32V). No significant source voltage degradation prior to fuse blow.
Circuit 3 | The circuit eperienced a fuse blow failure apparently as a result of a short between one energized source conductor and an external ground source. Only very minor degradation of supply voltage prior to fuse blow is noted.
Circuit 4 | This circuit was configured using the MOV-1 wiring scheme. The circuit experienced one spurious operation of one relay, and two spurious operations of the second relay. The total duration of the SA signals was about 16 s. Some degradation of the supply voltage is noted, but at worst, voltage drops by about 20 V.
Note:

## Circuit 1 Faulting
Summary of Observed Faulting Behavior for Circuit #1
DAQ Time | Burner Time | Event | Discussion
162 | 0 | Ignited Gas Burner
xxx | xxx | Burner off | No damage observed during time burner was on.
xxx | xxx | Spray started | Water spray initiated after burner was extinquished
1000 | 838 | shorting between Paths 1,2&7 | The source conductors 1 and 2 both appear to form short circuits to the CPT return side conductor on Path 7.
1000-1170 | 838-1008 | Increasing short quality | The short between the source conductors 1 and 2 increased in quality over a period of about 170 s.
1170 | 1008 | FB | Current increase was sufficient to trip the circuit fuse.
Summary observations |  | No circuit failures were observed during the burn portion of the test. After burner was extinguished, water spray was activated, and this did lead to circuit failure. No Spurious actuation occurred, rather, shorts to circuit ground led to a fuse blow. Significant degradation of the CPT voltage level is observed prior to ultimate circuit failure. The supply voltage dropped to a value of 94 volts prior to failure.

## Converted Data C1
DAQ Time | Burner Time | C1 V1 | C1 A1 | C1 V2 | C1 A2 | C1 V3 | C1 A3 | C1 V4 | C1 A4 | C1 V5 | C1 A5 | C1 V6 | C1 A6 | C1 V7 | C1 A7 | C1 V8 | C1 A8
0 | -162 | 131.3074 | 0.091876 | 130.907 | 0.0048528 |  |  | 0.28746 | 0.0022351 | 0.43642 | 0.0017522 | 0.38586 | 0.00029777 | 0.39567 | 0.079614 | 2.2364 | 0.0035663
30 | -132 | 131.8917 | 0.083759 | 131.4914 | 0.0016062 |  |  | 0.57968 | 0.0038588 | 0.53384 | 0.0033759 | 0.67808 | 0.0019208 | 0.49305 | 0.081237 | 2.5286 | 0.0035663
60 | -102 | 131.5996 | 0.085382 | 131.1992 | 0.0032298 |  |  | 0.38488 | 0.0022351 | 0.53384 | 0.0017522 | 0.58066 | 0.0019208 | 0.39567 | 0.081237 | 2.4312 | 0.0035663
90 | -72 | 131.8917 | 0.083759 | 131.4914 | 0.0048528 |  |  | 0.67706 | 0.0038588 | 0.63122 | 0.0033759 | 0.67808 | 0.0019208 | 0.68785 | 0.079614 | 2.5286 | 0.0051899
120 | -42 | 131.8917 | 0.083759 | 131.4914 | 0.0032298 |  |  | 0.57968 | 0.0038588 | 0.53384 | 0.0017522 | 0.58066 | 0.0035444 | 0.59047 | 0.081237 | 2.4312 | 0.0051899
150 | -12 | 131.8917 | 0.087005 | 131.394 | 0.0032298 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0033759 | 0.67808 | 0.0019208 | 0.59047 | 0.081237 | 2.626 | 0.0051899
180 | 18 | 132.0865 | 0.087005 | 131.6862 | 0.0032298 |  |  | 0.48226 | 0.0038588 | 0.63122 | 0.0033759 | 0.67808 | 0.0019208 | 0.49305 | 0.081237 | 2.5286 | 0.0051899
210 | 48 | 131.5996 | 0.090252 | 131.2966 | 0.0048528 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0017522 | 0.48328 | 0.0019208 | 0.29825 | 0.079614 | 2.3338 | 0.0035663
240 | 78 | 131.9892 | 0.091876 | 131.5888 | 0.0048528 |  |  | 0.38488 | 0.0038588 | 0.33904 | 0.0017522 | 0.48328 | 0.0019208 | 0.39567 | 0.081237 | 2.5286 | 0.0035663
270 | 108 | 132.4761 | 0.085382 | 132.1731 | 0.0032298 |  |  | 0.67706 | 0.0054818 | 0.63122 | 0.0033759 | 0.67808 | 0.0035444 | 0.59047 | 0.08286 | 2.7234 | 0.0051899
300 | 138 | 131.9892 | 0.088629 | 131.5888 | 0.0032298 |  |  | 0.48226 | 0.0038588 | 0.53384 | 0.0033759 | 0.48328 | 0.0019208 | 0.29825 | 0.081237 | 2.626 | 0.0051899
330 | 168 | 132.2813 | 0.096745 | 131.9783 | 0.0064758 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0033759 | 0.48328 | 0.0019208 | 0.39567 | 0.079614 | 2.626 | 0.0051899
360 | 198 | 132.3787 | 0.087005 | 131.881 | 0.0048528 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0033759 | 0.67808 | 0.0035444 | 0.59047 | 0.08286 | 3.3078 | 0.0051899
390 | 228 | 132.1839 | 0.087005 | 131.7836 | 0.0048528 |  |  | 0.48226 | 0.0038588 | 0.53384 | 0.0033759 | 0.58066 | 0.0035444 | 0.39567 | 0.08286 | 3.6973 | 0.0051899
420 | 258 | 132.2813 | 0.087005 | 131.881 | 0.0032298 |  |  | 0.67706 | 0.0054818 | 0.63122 | 0.0049989 | 0.67808 | 0.0035444 | 0.68785 | 0.08286 | 4.1843 | 0.0051899
450 | 288 | 132.9631 | 0.085382 | 132.5627 | 0.0048528 |  |  | 0.67706 | 0.0054818 | 0.72864 | 0.0033759 | 0.67808 | 0.0051674 | 0.68785 | 0.084483 | 4.3791 | 0.0051899
480 | 318 | 132.3787 | 0.091876 | 131.9783 | 0.0064758 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0033759 | 0.48328 | 0.0019208 | 0.39567 | 0.081237 | 4.3791 | 0.0051899
510 | 348 | 132.5735 | 0.088629 | 132.1731 | 0.0048528 |  |  | 0.57968 | 0.0054818 | 0.72864 | 0.0049989 | 0.77546 | 0.0035444 | 0.68785 | 0.084483 | 4.6713 | 0.0068129
540 | 378 | 132.6709 | 0.087005 | 132.2706 | 0.0048528 |  |  | 0.67706 | 0.0054818 | 0.72864 | 0.0049989 | 0.67808 | 0.0035444 | 0.68785 | 0.08286 | 4.6713 | 0.0051899
570 | 408 | 132.3787 | 0.090252 | 131.9783 | 0.0048528 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0049989 | 0.67808 | 0.0035444 | 0.59047 | 0.08286 | 4.6713 | 0.0051899
600 | 438 | 132.1839 | 0.091876 | 131.881 | 0.0048528 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0033759 | 0.48328 | 0.0035444 | 0.39567 | 0.08286 | 4.5739 | 0.0051899
630 | 468 | 131.9892 | 0.096745 | 131.6862 | 0.0097225 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0033759 | 0.48328 | 0.0035444 | 0.39567 | 0.081237 | 4.2817 | 0.0051899
660 | 498 | 132.0865 | 0.093499 | 131.6862 | 0.0064758 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0033759 | 0.48328 | 0.0035444 | 0.39567 | 0.081237 | 4.5739 | 0.0051899
690 | 528 | 132.6709 | 0.088629 | 132.2706 | 0.0048528 |  |  | 0.67706 | 0.0054818 | 0.72864 | 0.0049989 | 0.77546 | 0.0051674 | 0.78523 | 0.084483 | 5.3531 | 0.0068129
720 | 558 | 132.2813 | 0.098368 | 132.0758 | 0.0097225 |  |  | 0.38488 | 0.0054818 | 0.43642 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.081237 | 4.9635 | 0.0051899
750 | 588 | 132.0865 | 0.096745 | 131.7836 | 0.0080995 |  |  | 0.38488 | 0.0054818 | 0.43642 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.08286 | 5.3531 | 0.0051899
780 | 618 | 132.1839 | 0.091876 | 131.881 | 0.0048528 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0049989 | 0.58066 | 0.0035444 | 0.39567 | 0.084483 | 6.3271 | 0.0051899
810 | 648 | 132.2813 | 0.091876 | 132.0758 | 0.0048528 |  |  | 0.57968 | 0.0054818 | 0.53384 | 0.0049989 | 0.58066 | 0.0035444 | 0.59047 | 0.08286 | 6.2297 | 0.0051899
840 | 678 | 132.2813 | 0.096745 | 131.9783 | 0.0080995 |  |  | 0.38488 | 0.0038588 | 0.43642 | 0.0033759 | 0.48328 | 0.0035444 | 0.39567 | 0.08286 | 5.8401 | 0.0051899
870 | 708 | 132.4761 | 0.096745 | 132.2706 | 0.0097225 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0033759 | 0.48328 | 0.0035444 | 0.49305 | 0.081237 | 5.3531 | 0.0051899
900 | 738 | 132.3787 | 0.096745 | 132.1731 | 0.0097225 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.58066 | 0.0051674 | 0.49305 | 0.08286 | 5.3531 | 0.0051899
930 | 768 | 132.9631 | 0.087005 | 132.6601 | 0.0048528 |  |  | 0.67706 | 0.0071055 | 0.72864 | 0.0049989 | 0.67808 | 0.0051674 | 0.68785 | 0.084483 | 5.5479 | 0.0068129
960 | 798 | 132.4761 | 0.098368 | 132.2706 | 0.0097225 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.48328 | 0.0051674 | 0.49305 | 0.08286 | 4.7687 | 0.0051899
990 | 828 | 132.3787 | 0.093499 | 131.9783 | 0.0080995 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.084483 | 2.9182 | 0.0051899
991 | 829 | 132.2813 | 0.095122 | 131.9783 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.48328 | 0.0051674 | 0.49305 | 0.084483 | 2.7234 | 0.0051899
992 | 830 | 132.1839 | 0.093499 | 131.881 | 0.0064758 |  |  | 0.38488 | 0.0054818 | 0.53384 | 0.0049989 | 0.58066 | 0.0051674 | 0.49305 | 0.084483 | 1.4572 | 0.0051899
993 | 831 | 132.3787 | 0.090252 | 131.9783 | 0.0048528 |  |  | 0.48226 | 0.0038588 | 0.53384 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.084483 | 0.77546 | 0.0068129
994 | 832 | 132.1839 | 0.087005 | 131.881 | 0.0048528 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0049989 | 0.67808 | 0.0051674 | 0.59047 | 0.086107 | 1.1651 | 0.0068129
995 | 833 | 132.1839 | 0.083759 | 131.7836 | 0.0097225 |  |  | 1.9432 | 0.0054818 | 3.1635 | 0.0049989 | 2.4312 | 0.0035444 | 0.59047 | 0.094223 | 3.7948 | 0.0068129
996 | 834 | 131.8917 | 0.085382 | 131.4914 | 0.063291 |  |  | 4.5729 | 0.0054818 | 4.9167 | 0.022855 | 3.6973 | 0.010037 | 0.68785 | 0.1137 | 5.4505 | 0.0068129
997 | 835 | 131.5996 | 0.083759 | 131.2966 | 0.11524 |  |  | 4.5729 | 0.0054818 | 5.4037 | 0.029348 | 5.0609 | 0.024647 | 0.59047 | 0.14941 | 4.6713 | 0.0068129
997.2 | 835.2 | 131.5022 | 0.083759 | 131.2966 | 0.11686 |  |  | 4.3781 | 0.0054818 | 5.1115 | 0.027725 | 5.2557 | 0.027894 | 0.59047 | 0.15428 | 4.3791 | 0.0051899
997.4 | 835.4 | 131.5022 | 0.083759 | 131.1992 | 0.12498 |  |  | 4.2807 | 0.0054818 | 5.1115 | 0.027725 | 5.2557 | 0.029517 | 0.68785 | 0.16078 | 4.3791 | 0.0051899
997.6 | 835.6 | 131.4048 | 0.087005 | 131.0044 | 0.14608 |  |  | 4.5729 | 0.0071055 | 5.4037 | 0.030972 | 5.3531 | 0.032763 | 0.59047 | 0.17701 | 4.3791 | 0.0068129
997.8 | 835.8 | 131.21 | 0.083759 | 131.0044 | 0.16393 |  |  | 4.9625 | 0.0054818 | 5.9881 | 0.035841 | 5.7427 | 0.03601 | 0.59047 | 0.19324 | 4.7687 | 0.0068129
998 | 836 | 131.21 | 0.087005 | 130.907 | 0.17043 |  |  | 4.7677 | 0.0054818 | 5.6958 | 0.035841 | 5.7427 | 0.03601 | 0.59047 | 0.19974 | 4.5739 | 0.0068129
998.2 | 836.2 | 131.1126 | 0.083759 | 130.7122 | 0.19478 |  |  | 4.8651 | 0.0054818 | 6.0854 | 0.039088 | 5.8401 | 0.039257 | 0.59047 | 0.21922 | 4.6713 | 0.0068129
998.4 | 836.4 | 130.9178 | 0.087005 | 130.5174 | 0.21913 |  |  | 5.1573 | 0.0054818 | 6.5724 | 0.042334 | 6.1323 | 0.042503 | 0.68785 | 0.23869 | 4.9635 | 0.0068129
998.6 | 836.6 | 130.8204 | 0.087005 | 130.5174 | 0.22886 |  |  | 5.0599 | 0.0054818 | 6.475 | 0.043958 | 6.0349 | 0.042503 | 0.59047 | 0.24843 | 4.8661 | 0.0068129
998.8 | 836.8 | 130.723 | 0.085382 | 130.42 | 0.23373 |  |  | 5.0599 | 0.0071055 | 6.2802 | 0.045581 | 6.1323 | 0.044126 | 0.59047 | 0.25493 | 4.7687 | 0.0068129
999 | 837 | 130.723 | 0.087005 | 130.3226 | 0.24347 |  |  | 4.8651 | 0.0071055 | 6.1828 | 0.043958 | 5.9375 | 0.042503 | 0.59047 | 0.26304 | 4.5739 | 0.0068129
999.2 | 837.2 | 130.723 | 0.085382 | 130.3226 | 0.24672 |  |  | 4.6703 | 0.0071055 | 5.8906 | 0.042334 | 5.7427 | 0.042503 | 0.59047 | 0.26954 | 4.3791 | 0.0051899
999.4 | 837.4 | 130.5282 | 0.083759 | 130.2252 | 0.2662 |  |  | 4.6703 | 0.0054818 | 5.8906 | 0.042334 | 5.8401 | 0.044126 | 0.59047 | 0.28415 | 4.3791 | 0.0068129
999.6 | 837.6 | 130.3334 | 0.085382 | 130.0304 | 0.2873 |  |  | 4.8651 | 0.0054818 | 6.2802 | 0.045581 | 5.9375 | 0.045749 | 0.59047 | 0.30363 | 4.4765 | 0.0068129
999.8 | 837.8 | 130.236 | 0.083759 | 129.933 | 0.30516 |  |  | 4.9625 | 0.0071055 | 6.2802 | 0.045581 | 6.0349 | 0.045749 | 0.59047 | 0.31986 | 4.3791 | 0.0068129
1000 | 838 | 130.1386 | 0.083759 | 129.8357 | 0.31165 |  |  | 4.7677 | 0.0054818 | 6.0854 | 0.047204 | 5.8401 | 0.045749 | 0.59047 | 0.32797 | 4.3791 | 0.0051899
1000.2 | 838.2 | 130.0412 | 0.083759 | 129.7382 | 0.32951 |  |  | 4.7677 | 0.0071055 | 6.0854 | 0.047204 | 5.9375 | 0.045749 | 0.59047 | 0.34258 | 4.2817 | 0.0068129
1000.4 | 838.4 | 129.749 | 0.083759 | 129.4461 | 0.36522 |  |  | 5.1573 | 0.0054818 | 6.6698 | 0.052074 | 6.1323 | 0.048996 | 0.59047 | 0.37505 | 4.5739 | 0.0068129
1000.6 | 838.6 | 129.6516 | 0.082136 | 129.3486 | 0.37821 |  |  | 5.1573 | 0.0054818 | 6.7672 | 0.053697 | 6.2297 | 0.050619 | 0.59047 | 0.38641 | 4.5739 | 0.0068129
1000.8 | 838.8 | 129.5542 | 0.083759 | 129.2513 | 0.39444 |  |  | 5.0599 | 0.0054818 | 6.6698 | 0.053697 | 6.2297 | 0.050619 | 0.59047 | 0.40102 | 4.4765 | 0.0051899
1001 | 839 | 129.3595 | 0.085382 | 128.9591 | 0.4269 |  |  | 5.2547 | 0.0054818 | 7.1568 | 0.055321 | 6.4245 | 0.052243 | 0.49305 | 0.43024 | 4.6713 | 0.0051899
1001.2 | 839.2 | 129.262 | 0.083759 | 128.9591 | 0.43502 |  |  | 5.1573 | 0.0071055 | 7.0594 | 0.055321 | 6.3271 | 0.052243 | 0.59047 | 0.43836 | 4.5739 | 0.0051899
1001.4 | 839.4 | 129.1647 | 0.083759 | 128.9591 | 0.44801 |  |  | 5.1573 | 0.0054818 | 6.962 | 0.055321 | 6.4245 | 0.052243 | 0.59047 | 0.44972 | 4.5739 | 0.0051899
1001.6 | 839.6 | 128.8725 | 0.083759 | 128.5695 | 0.4756 |  |  | 5.3521 | 0.0054818 | 7.1568 | 0.06019 | 6.4245 | 0.053866 | 0.59047 | 0.47732 | 4.6713 | 0.0051899
1001.8 | 839.8 | 128.8725 | 0.083759 | 128.4721 | 0.48372 |  |  | 5.1573 | 0.0054818 | 6.962 | 0.056944 | 6.3271 | 0.052243 | 0.59047 | 0.48381 | 4.4765 | 0.0051899
1002 | 840 | 128.6777 | 0.082136 | 128.3747 | 0.49671 |  |  | 5.1573 | 0.0054818 | 6.962 | 0.056944 | 6.3271 | 0.053866 | 0.59047 | 0.50004 | 4.4765 | 0.0051899
1002.2 | 840.2 | 128.5803 | 0.083759 | 128.1799 | 0.51943 |  |  | 5.2547 | 0.0071055 | 7.0594 | 0.056944 | 6.4245 | 0.053866 | 0.49305 | 0.51952 | 4.4765 | 0.0051899
1002.4 | 840.4 | 128.5803 | 0.083759 | 128.1799 | 0.5243 |  |  | 5.2547 | 0.0054818 | 7.0594 | 0.058567 | 6.4245 | 0.055489 | 0.59047 | 0.52601 | 4.4765 | 0.0051899
1002.6 | 840.6 | 128.3855 | 0.082136 | 128.0825 | 0.5454 |  |  | 5.2547 | 0.0071055 | 7.1568 | 0.058567 | 6.5219 | 0.055489 | 0.49305 | 0.54387 | 4.4765 | 0.0051899
1002.8 | 840.8 | 128.2881 | 0.083759 | 127.9851 | 0.55677 |  |  | 5.2547 | 0.0054818 | 7.0594 | 0.058567 | 6.4245 | 0.055489 | 0.49305 | 0.55523 | 4.3791 | 0.0051899
1003 | 841 | 128.1907 | 0.083759 | 127.8877 | 0.57138 |  |  | 5.2547 | 0.0038588 | 7.0594 | 0.058567 | 6.4245 | 0.053866 | 0.49305 | 0.56984 | 4.3791 | 0.0051899
1003.2 | 841.2 | 127.9959 | 0.083759 | 127.6929 | 0.59086 |  |  | 5.2547 | 0.0054818 | 7.0594 | 0.056944 | 6.4245 | 0.053866 | 0.49305 | 0.59095 | 4.3791 | 0.0051899
1003.4 | 841.4 | 127.8985 | 0.083759 | 127.4981 | 0.62332 |  |  | 5.4495 | 0.0054818 | 7.3516 | 0.06019 | 6.6192 | 0.055489 | 0.49305 | 0.62016 | 4.4765 | 0.0051899
1003.6 | 841.6 | 127.7037 | 0.082136 | 127.4007 | 0.62819 |  |  | 5.2547 | 0.0054818 | 7.0594 | 0.058567 | 6.5219 | 0.055489 | 0.49305 | 0.62666 | 4.3791 | 0.0051899
1003.8 | 841.8 | 127.6063 | 0.082136 | 127.3033 | 0.65254 |  |  | 5.3521 | 0.0054818 | 7.3516 | 0.06019 | 6.6192 | 0.055489 | 0.39567 | 0.64938 | 4.3791 | 0.0051899
1004 | 842 | 127.5089 | 0.083759 | 127.2059 | 0.65579 |  |  | 5.2547 | 0.0054818 | 7.0594 | 0.058567 | 6.6192 | 0.055489 | 0.49305 | 0.65263 | 4.3791 | 0.0035663
1004.2 | 842.2 | 127.3141 | 0.082136 | 127.0111 | 0.68501 |  |  | 5.2547 | 0.0054818 | 7.1568 | 0.06019 | 6.7167 | 0.055489 | 0.59047 | 0.68185 | 4.3791 | 0.0051899
1004.4 | 842.4 | 127.0219 | 0.083759 | 126.8163 | 0.72072 |  |  | 5.3521 | 0.0038588 | 7.449 | 0.06019 | 6.814 | 0.057112 | 0.49305 | 0.71594 | 4.4765 | 0.0051899
1004.6 | 842.6 | 126.6323 | 0.083759 | 126.5242 | 0.74507 |  |  | 5.4495 | 0.0054818 | 7.3516 | 0.06019 | 6.9115 | 0.057112 | 0.49305 | 0.74029 | 4.5739 | 0.0051899
1004.8 | 842.8 | 126.3401 | 0.083759 | 126.4267 | 0.77429 |  |  | 5.4495 | 0.0038588 | 7.449 | 0.061813 | 7.0088 | 0.058735 | 0.49305 | 0.76951 | 4.5739 | 0.0051899
1005 | 843 | 125.6584 | 0.085382 | 126.2319 | 0.80837 |  |  | 5.6443 | 0.0054818 | 7.5464 | 0.061813 | 7.1062 | 0.058735 | 0.49305 | 0.80197 | 4.7687 | 0.0051899
1005.2 | 843.2 | 125.074 | 0.080513 | 126.1346 | 0.8311 |  |  | 5.6443 | 0.0054818 | 7.5464 | 0.061813 | 7.2036 | 0.060359 | 0.39567 | 0.8247 | 4.7687 | 0.0051899
1005.4 | 843.4 | 125.561 | 0.082136 | 125.6476 | 0.88142 |  |  | 5.8391 | 0.0054818 | 7.7412 | 0.061813 | 7.4958 | 0.061982 | 0.49305 | 0.87177 | 4.8661 | 0.0051899
1005.6 | 843.6 | 125.561 | 0.082136 | 125.258 | 0.922 |  |  | 5.8391 | 0.0054818 | 7.8386 | 0.063437 | 7.5932 | 0.063606 | 0.49305 | 0.91073 | 5.0609 | 0.0051899
1005.8 | 843.8 | 125.2688 | 0.082136 | 124.8684 | 0.97395 |  |  | 5.9365 | 0.0054818 | 7.936 | 0.06506 | 7.6906 | 0.065229 | 0.49305 | 0.96268 | 5.2557 | 0.0051899
1006 | 844 | 124.8792 | 0.082136 | 124.4788 | 1.0162 |  |  | 6.0339 | 0.0054818 | 7.936 | 0.06506 | 7.788 | 0.065229 | 0.49305 | 1.0033 | 5.2557 | 0.0051899
1006.2 | 844.2 | 124.6844 | 0.082136 | 124.284 | 1.0454 |  |  | 6.0339 | 0.0054818 | 7.936 | 0.063437 | 7.8854 | 0.065229 | 0.49305 | 1.0341 | 5.2557 | 0.0035663
1006.4 | 844.4 | 124.3922 | 0.082136 | 124.0893 | 1.0795 |  |  | 5.9365 | 0.0054818 | 7.7412 | 0.063437 | 7.8854 | 0.066852 | 0.59047 | 1.0666 | 5.2557 | 0.0051899
1006.6 | 844.6 | 124.1 | 0.080513 | 123.797 | 1.1152 |  |  | 6.0339 | 0.0054818 | 7.936 | 0.063437 | 7.9828 | 0.065229 | 0.49305 | 1.1023 | 5.2557 | 0.0051899
1006.8 | 844.8 | 123.9052 | 0.080513 | 123.5049 | 1.1493 |  |  | 6.0339 | 0.0054818 | 7.8386 | 0.06506 | 7.9828 | 0.066852 | 0.49305 | 1.1364 | 5.3531 | 0.0051899
1007 | 845 | 123.8079 | 0.080513 | 123.4075 | 1.1655 |  |  | 6.0339 | 0.0054818 | 7.7412 | 0.063437 | 7.9828 | 0.066852 | 0.49305 | 1.1558 | 5.2557 | 0.0051899
1007.2 | 845.2 | 123.5156 | 0.082136 | 123.1153 | 1.2028 |  |  | 6.0339 | 0.0054818 | 7.8386 | 0.06506 | 7.9828 | 0.066852 | 0.49305 | 1.1916 | 5.2557 | 0.0051899
1007.4 | 845.4 | 123.4183 | 0.080513 | 123.0179 | 1.2191 |  |  | 5.8391 | 0.0054818 | 7.7412 | 0.061813 | 7.8854 | 0.065229 | 0.59047 | 1.2078 | 5.1583 | 0.0051899
1007.6 | 845.6 | 123.0287 | 0.080513 | 122.6283 | 1.2596 |  |  | 5.9365 | 0.0054818 | 7.6438 | 0.063437 | 7.788 | 0.065229 | 0.49305 | 1.2532 | 5.2557 | 0.0051899
1007.8 | 845.8 | 123.0287 | 0.080513 | 122.6283 | 1.2645 |  |  | 5.7417 | 0.0054818 | 7.449 | 0.06019 | 7.6906 | 0.063606 | 0.59047 | 1.2581 | 5.0609 | 0.0051899
1008 | 846 | 122.7365 | 0.082136 | 122.2387 | 1.2921 |  |  | 5.5469 | 0.0038588 | 7.3516 | 0.06019 | 7.4958 | 0.063606 | 0.49305 | 1.2857 | 5.0609 | 0.0051899
1008.2 | 846.2 | 122.5417 | 0.082136 | 122.1413 | 1.3148 |  |  | 5.5469 | 0.0054818 | 7.2542 | 0.058567 | 7.4958 | 0.061982 | 0.49305 | 1.3101 | 4.8661 | 0.0051899
1008.4 | 846.4 | 122.4443 | 0.080513 | 122.0439 | 1.3376 |  |  | 5.3521 | 0.0054818 | 7.1568 | 0.056944 | 7.301 | 0.061982 | 0.49305 | 1.3328 | 4.7687 | 0.0051899
1008.6 | 846.6 | 122.1521 | 0.080513 | 121.7517 | 1.37 |  |  | 5.2547 | 0.0054818 | 7.0594 | 0.056944 | 7.301 | 0.060359 | 0.49305 | 1.3652 | 4.7687 | 0.0051899
1008.8 | 846.8 | 121.9573 | 0.082136 | 121.5569 | 1.3911 |  |  | 5.2547 | 0.0054818 | 6.962 | 0.055321 | 7.1062 | 0.060359 | 0.39567 | 1.3896 | 4.7687 | 0.0051899
1009 | 847 | 121.7625 | 0.080513 | 121.3621 | 1.4122 |  |  | 5.0599 | 0.0054818 | 6.8646 | 0.055321 | 7.0088 | 0.058735 | 0.59047 | 1.4123 | 4.6713 | 0.0051899
1009.2 | 847.2 | 121.5677 | 0.080513 | 121.2647 | 1.4301 |  |  | 4.8651 | 0.0054818 | 6.5724 | 0.053697 | 6.9115 | 0.058735 | 0.49305 | 1.4302 | 4.5739 | 0.0051899
1009.4 | 847.4 | 121.4703 | 0.080513 | 121.0699 | 1.4609 |  |  | 4.8651 | 0.0054818 | 6.5724 | 0.052074 | 6.7167 | 0.055489 | 0.49305 | 1.4626 | 4.4765 | 0.0035663
1009.6 | 847.6 | 121.1781 | 0.080513 | 120.8751 | 1.4837 |  |  | 4.6703 | 0.0054818 | 6.3776 | 0.05045 | 6.2297 | 0.053866 | 0.49305 | 1.487 | 4.3791 | 0.0051899
1009.8 | 847.8 | 120.9833 | 0.078889 | 120.6803 | 1.5048 |  |  | 4.5729 | 0.010351 | 6.2802 | 0.05045 | 6.4245 | 0.053866 | 0.39567 | 1.5097 | 4.1843 | 0.0035663
1010 | 848 | 120.7885 | 0.080513 | 120.4856 | 1.5161 |  |  | 4.3781 | 0.0054818 | 6.0854 | 0.048827 | 6.2297 | 0.052243 | 0.49305 | 1.5211 | 3.6 | 0.0051899
1010.2 | 848.2 | 120.5937 | 0.078889 | 119.9986 | 1.5518 |  |  | 4.2807 | 0.0054818 | 5.9881 | 0.047204 | 6.0349 | 0.052243 | 0.39567 | 1.56 | 3.9895 | 0.0051899
1010.4 | 848.4 | 120.3989 | 0.077266 | 119.9986 | 1.5681 |  |  | 4.1834 | 0.0054818 | 4.9167 | 0.042334 | 5.8401 | 0.047373 | 0.10349 | 1.5747 | 3.6973 | 0.0084366
1010.6 | 848.6 | 120.3016 | 0.078889 | 119.7064 | 1.5713 |  |  | 3.599 | 0.0054818 | 6.1828 | 0.045581 | 5.6453 | 0.052243 | 0.39567 | 1.5958 | 3.2104 | 0.0035663
1010.8 | 848.8 | 119.8146 | 0.075642 | 119.4142 | 1.6135 |  |  | 3.2094 | 0.0054818 | 5.3063 | 0.042334 | 5.5479 | 0.047373 | 0.29825 | 1.5941 | 3.0156 | 0.011683
1011 | 849 | 119.425 | 0.065903 | 118.5376 | 1.6135 |  |  | 2.2354 | 0.0071055 | 2.7739 | 0.026101 | 3.5025 | 0.055489 | 0.68785 | 1.612 | 1.5546 | 0.0035663
1011.2 | 849.2 | 119.0354 | 0.067526 | 118.7324 | 1.62 |  |  | 1.5536 | -0.010751 | 4.4297 | 0.021232 | 3.8921 | 0.023023 | -0.18874 | 1.638 | 2.2364 | 0.00032025
1011.4 | 849.4 | 119.3276 | 0.077266 | 117.5637 | 1.633 |  |  | 2.0406 | 0.00061214 | 4.0401 | 0.048827 | 3.3078 | 0.052243 | 1.2722 | 1.6412 | 2.4312 | 0.00032025
1011.6 | 849.6 | 118.1588 | 0.070772 | 116.6871 | 1.6557 |  |  | 2.7224 | -0.0010109 | 3.0661 | 0.034218 | 3.9895 | 0.014907 | -0.18874 | 1.6477 | 1.3598 | 0.0084366
1011.8 | 849.8 | 117.6719 | 0.052917 | 116.9793 | 1.6638 |  |  | 2.138 | -0.0058812 | 4.2349 | 0.030972 | 3.8921 | 0.032763 | 0.49305 | 1.6802 | 1.8468 | -0.0013034
1012 | 850 | 117.4771 | 0.059409 | 118.5376 | 1.6379 |  |  | 1.164 | 0.023338 | 2.7739 | 0.021232 | 2.2364 | 0.023023 | 0.78523 | 1.6704 | -0.39331 | -0.022406
1012.2 | 850.2 | 116.6979 | 0.057786 | 115.9079 | 1.6866 |  |  | 1.8458 | 0.0022351 | 3.3583 | 0.022855 | 2.7234 | 0.024647 | -0.091316 | 1.6948 | 1.9442 | -0.0094198
1012.4 | 850.4 | 116.2109 | 0.033437 | 116.6871 | 1.7044 |  |  | 3.3068 | -0.0010109 | 1.8974 | 0.039088 | 2.5286 | 0.029517 | -0.091316 | 1.724 | 0.093675 | -0.014289
1012.6 | 850.6 | 117.2823 | 0.041554 | 116.5897 | 1.7012 |  |  | 1.164 | 0.016845 | 3.0661 | 0.040711 | 2.9182 | 0.034386 | 0.10349 | 1.7305 | 0.87284 | -0.012666
1012.8 | 850.8 | 116.0161 | 0.041554 | 114.447 | 1.7255 |  |  | 0.87186 | 0.042818 | 2.3844 | 0.030972 | 3.113 | 0.02627 | 0.68785 | 1.7321 | 1.4572 | 0.01006
1013 | 851 | 115.4318 | 0.0448 | 114.447 | 1.6931 |  |  | 0.38488 | -0.015621 | 3.1635 | 0.035841 | 1.8468 | 0.03601 | 1.0774 | 1.7467 | -0.10113 | 0.0084366
1013.2 | 851.2 | 115.8213 | 0.0448 | 116.2001 | 1.719 |  |  | -0.0047195 | 0.0071055 | 2.4818 | 0.027725 | 2.7234 | 0.018153 | 0.0060648 | 1.7451 | 2.4312 | 0.0068129
1013.4 | 851.4 | 117.3797 | 0.04967 | 117.2715 | 1.7288 |  |  | 0.38488 | 0.0022351 | 2.287 | 0.024478 | 0.58066 | 0.023023 | 0.39567 | 1.7565 | -0.29589 | 0.00032025
1013.6 | 851.6 | 115.6265 | 0.04967 | 115.6157 | 1.7596 |  |  | 1.2614 | -0.018867 | 3.0661 | 0.027725 | 3.7948 | 0.027894 | 1.7592 | 1.7889 | 0.87284 | -0.0013034
1013.8 | 851.8 | 114.4578 | 0.030191 | 115.3236 | 1.7255 |  |  | 0.48226 | -0.0010109 | 2.0922 | 0.029348 | 2.3338 | 0.02627 | -0.18874 | 1.7532 | 1.8468 | 0.01006
1014 | 852 | 116.6979 | 0.061033 | 113.7652 | 1.7174 |  |  | 1.7484 | 0.0087285 | 0.14424 | 0.019609 | 0.19109 | 0.011661 | 1.467 | 1.7711 | 1.2624 | -0.0045501
1014.2 | 852.2 | 116.5031 | 0.0090883 | 114.8366 | 1.7466 |  |  | 0.87186 | -0.0010109 | 2.8714 | 0.029348 | 2.626 | 0.01653 | -1.5523 | 1.7386 | 0.97026 | 0.013306
1014.4 | 852.4 | 113.0942 | -0.0022747 | 113.7652 | 1.7174 |  |  | 0.87186 | 0.0022351 | 0.53384 | 0.0098686 | -1.5621 | 0.019777 | 1.0774 | 1.8019 | 1.652 | 0.011683
1014.6 | 852.6 | 116.1135 | 0.039931 | 114.8366 | 1.7694 |  |  | -0.0047195 | 0.011975 | 2.1896 | 0.027725 | 1.2624 | 0.060359 | -0.67572 | 1.7922 | -0.19851 | 0.00032025
1014.8 | 852.8 | 116.0161 | 0.038307 | 115.5184 | 1.7661 |  |  | 1.651 | -0.0026345 | 1.4104 | 0.011492 | 3.113 | 0.01653 | -1.0653 | 1.8344 | 1.8468 | -0.071104
1015 | 853 | 114.4578 | 0.020451 | 113.7652 | 1.771 |  |  | 0.38488 | 0.0054818 | 1.2156 | 0.0098686 | 0.87284 | 0.024647 | -0.5783 | 1.8263 | 0.87284 | 0.0068129
1015.2 | 853.2 | 113.0942 | 0.039931 | 114.447 | 1.7466 |  |  | 0.87186 | 0.0054818 | 1.313 | -0.012857 | 0.87284 | 0.0214 | 0.59047 | 1.8035 | -0.19851 | -0.020783
1015.4 | 853.4 | 113.9708 | 0.03506 | 114.934 | 1.7596 |  |  | 0.96924 | -0.022114 | 2.1896 | 0.011492 | 2.5286 | 0.0051674 | -0.18874 | 1.8279 | 1.2624 | 0.011683
1015.6 | 853.6 | 116.3083 | 0.025321 | 115.2262 | 1.7856 |  |  | -0.19952 | 0.0038588 | 2.1896 | 0.011492 | 0.67808 | 0.018153 | 1.2722 | 1.849 | -0.78287 | -0.0029264
1015.8 | 853.8 | 115.237 | 0.0448 | 113.6678 | 1.7921 |  |  | 0.48226 | 0.033078 | 2.3844 | 0.030972 | 0.87284 | 0.039257 | 2.5384 | 1.7597 | 2.4312 | 0.0084366
1016 | 854 | 113.5812 | 0.041554 | 113.7652 | 1.7986 |  |  | -0.78388 | 0.00061214 | -0.73231 | 0.021232 | 2.139 | 0.019777 | 0.20087 | 1.862 | 1.1651 | 0.011683
1016.2 | 854.2 | 114.6526 | 0.051293 | 113.96 | 1.8018 |  |  | -0.39428 | 0.0022351 | 0.82602 | 0.0066219 | 2.4312 | 0.03114 | 0.98003 | 1.8733 | -0.78287 | 0.027915
1016.4 | 854.4 | 115.1395 | 0.048047 | 113.0834 | 1.8408 |  |  | -0.1021 | 0.0054818 | 2.6766 | -0.0031175 | 0.97026 | 0.01653 | 1.5644 | 1.8701 | 0.97026 | 0.021423
1016.6 | 854.6 | 115.5291 | 0.051293 | 114.7392 | 1.8213 |  |  | 0.67706 | 0.016845 | 2.0922 | 0.027725 | 1.1651 | 0.013284 | -1.6497 | 1.8831 | 0.87284 | 0.0084366
1016.8 | 854.8 | 115.0422 | 0.059409 | 114.5444 | 1.8148 |  |  | -0.58908 | 0.026584 | 0.9234 | 0.029348 | 0.38586 | 0.013284 | 0.0060648 | 1.8636 | 0.19109 | 0.011683
1017 | 855 | 113.9708 | 0.028568 | 114.0574 | 1.844 |  |  | -0.2969 | -0.0058812 | 1.1182 | 0.034218 | 1.5546 | 0.024647 | 2.0514 | 1.8944 | -0.49069 | -0.032146
1017.2 | 855.2 | 115.0422 | 0.030191 | 114.5444 | 1.8538 |  |  | 0.28746 | 0.0054818 | 1.2156 | 0.014738 | 1.9442 | 0.0214 | 0.20087 | 1.8944 | 0.58066 | 0.01006
1017.4 | 855.4 | 113.8734 | 0.059409 | 113.473 | 1.8651 |  |  | 0.092701 | 0.013598 | 0.63122 | 0.0066219 | 0.67808 | 0.011661 | 1.0774 | 1.8961 | 0.38586 | 0.027915
1017.6 | 855.6 | 115.7239 | 0.056163 | 114.6418 | 1.8765 |  |  | 0.77444 | -0.0026345 | 2.7739 | 0.027725 | 1.8468 | 0.01653 | 0.78523 | 1.922 | -0.10113 | 0.011683
1017.8 | 855.8 | 114.263 | 0.039931 | 114.1548 | 1.8797 |  |  | -0.0047195 | 0.0054818 | 2.287 | 0.016362 | 3.4052 | 0.010037 | 0.68785 | 1.9431 | -0.10113 | -0.0013034
1018 | 856 | 114.75 | 0.061033 | 115.2262 | 1.8976 |  |  | 1.0667 | 0.015222 | 2.1896 | 0.021232 | 2.0416 | 0.0214 | 0.39567 | 1.9253 | 0.48328 | 0.0084366
1018.2 | 856.2 | 114.3604 | 0.051293 | 114.7392 | 1.8814 |  |  | 0.77444 | 0.0038588 | 2.0922 | 0.024478 | 1.9442 | 0.014907 | 0.20087 | 1.9107 | 0.48328 | 0.00032025
1018.4 | 856.4 | 116.3083 | 0.074019 | 115.2262 | 1.9138 |  |  | 1.0667 | 0.0054818 | 2.8714 | 0.024478 | 2.7234 | 0.023023 | 0.39567 | 1.9383 | 1.1651 | 0.0051899
1018.6 | 856.6 | 115.9187 | 0.080513 | 115.8105 | 1.9187 |  |  | 1.3588 | 0.0071055 | 2.8714 | 0.021232 | 2.7234 | 0.019777 | 0.49305 | 1.9415 | 1.2624 | 0.0051899
1018.8 | 856.8 | 115.7239 | 0.080513 | 116.1027 | 1.9268 |  |  | 1.4562 | 0.0022351 | 3.1635 | 0.022855 | 2.9182 | 0.023023 | 0.68785 | 1.9561 | 0.87284 | 0.0035663
1019 | 857 | 116.6005 | 0.082136 | 115.8105 | 1.9382 |  |  | 1.4562 | 0.0038588 | 3.1635 | 0.026101 | 2.7234 | 0.023023 | 0.49305 | 1.9642 | 1.4572 | 0.0051899
1019.2 | 857.2 | 116.4057 | 0.082136 | 115.8105 | 1.9577 |  |  | 1.5536 | 0.0038588 | 3.3583 | 0.021232 | 2.9182 | 0.0214 | 0.39567 | 1.9853 | 1.4572 | 0.0019433
1019.4 | 857.4 | 116.2109 | 0.083759 | 115.6157 | 1.9463 |  |  | 1.4562 | 0.0054818 | 3.2609 | 0.022855 | 3.0156 | 0.023023 | 0.39567 | 1.9788 | 1.4572 | 0.0051899
1019.6 | 857.6 | 116.4057 | 0.083759 | 116.0053 | 1.9577 |  |  | 1.651 | 0.0022351 | 3.1635 | 0.021232 | 2.8208 | 0.0214 | 0.39567 | 1.9772 | 1.2624 | 0.0035663
1019.8 | 857.8 | 116.3083 | 0.083759 | 115.9079 | 1.9544 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.022855 | 2.9182 | 0.0214 | 0.49305 | 1.9821 | 1.3598 | 0.0068129
1020 | 858 | 116.1135 | 0.085382 | 115.8105 | 1.9658 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.019609 | 2.9182 | 0.0214 | 0.39567 | 1.9918 | 1.3598 | 0.0051899
1020.2 | 858.2 | 116.1135 | 0.085382 | 115.7132 | 1.982 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.022855 | 2.9182 | 0.0214 | 0.39567 | 2.0081 | 1.3598 | 0.0035663
1020.4 | 858.4 | 116.1135 | 0.085382 | 115.6157 | 1.9836 |  |  | 1.5536 | 0.0038588 | 3.2609 | 0.021232 | 2.9182 | 0.0214 | 0.49305 | 2.0113 | 1.3598 | 0.0035663
1020.6 | 858.6 | 116.0161 | 0.087005 | 115.6157 | 1.9869 |  |  | 1.5536 | 0.0038588 | 3.2609 | 0.021232 | 3.0156 | 0.0214 | 0.39567 | 2.0146 | 1.3598 | 0.0051899
1020.8 | 858.8 | 115.9187 | 0.083759 | 115.4209 | 2.0047 |  |  | 1.651 | 0.0038588 | 3.3583 | 0.021232 | 2.9182 | 0.019777 | 0.39567 | 2.0308 | 1.3598 | 0.0051899
1021 | 859 | 115.9187 | 0.087005 | 115.5184 | 2.0047 |  |  | 1.651 | 0.0054818 | 3.2609 | 0.021232 | 2.9182 | 0.0214 | 0.39567 | 2.0324 | 1.2624 | 0.0051899
1021.2 | 859.2 | 115.8213 | 0.087005 | 115.5184 | 1.9999 |  |  | 1.5536 | 0.0038588 | 3.2609 | 0.022855 | 2.9182 | 0.0214 | 0.39567 | 2.0259 | 1.3598 | 0.0035663
1021.4 | 859.4 | 115.9187 | 0.087005 | 115.5184 | 1.9901 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.022855 | 2.8208 | 0.019777 | 0.49305 | 2.0178 | 1.2624 | 0.0051899
1021.6 | 859.6 | 115.7239 | 0.088629 | 115.3236 | 2.0112 |  |  | 1.5536 | 0.0038588 | 3.2609 | 0.021232 | 2.8208 | 0.019777 | 0.39567 | 2.0405 | 1.1651 | 0.0035663
1021.8 | 859.8 | 115.7239 | 0.088629 | 115.2262 | 2.0161 |  |  | 1.651 | 0.0054818 | 3.1635 | 0.022855 | 2.9182 | 0.019777 | 0.39567 | 2.0438 | 1.2624 | 0.0051899
1022 | 860 | 115.5291 | 0.095122 | 115.1288 | 2.0242 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.021232 | 2.9182 | 0.019777 | 0.49305 | 2.0584 | 1.1651 | 0.0051899
1022.2 | 860.2 | 115.4318 | 0.095122 | 115.0314 | 2.0469 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.022855 | 2.8208 | 0.0214 | 0.49305 | 2.0779 | 1.3598 | 0.0051899
1022.4 | 860.4 | 115.4318 | 0.099992 | 114.934 | 2.0453 |  |  | 1.5536 | 0.0054818 | 3.3583 | 0.021232 | 2.9182 | 0.019777 | 0.49305 | 2.0811 | 1.2624 | 0.0051899
1022.6 | 860.6 | 115.237 | 0.10324 | 114.8366 | 2.0534 |  |  | 1.5536 | 0.0038588 | 3.2609 | 0.021232 | 2.9182 | 0.0214 | 0.49305 | 2.0941 | 1.3598 | 0.0051899
1022.8 | 860.8 | 115.237 | 0.10648 | 114.8366 | 2.0486 |  |  | 1.651 | 0.0038588 | 3.2609 | 0.022855 | 2.9182 | 0.019777 | 0.39567 | 2.0909 | 1.2624 | 0.0051899
1023 | 861 | 115.1395 | 0.11622 | 114.7392 | 2.0534 |  |  | 1.651 | 0.0038588 | 3.3583 | 0.022855 | 2.8208 | 0.019777 | 0.49305 | 2.1038 | 1.3598 | 0.0051899
1023.2 | 861.2 | 115.0422 | 0.12109 | 114.5444 | 2.0697 |  |  | 1.5536 | 0.0054818 | 3.2609 | 0.022855 | 2.8208 | 0.0214 | 0.49305 | 2.1266 | 1.3598 | 0.0051899
1023.4 | 861.4 | 114.75 | 0.12921 | 114.3496 | 2.0826 |  |  | 1.651 | 0.0038588 | 3.3583 | 0.022855 | 2.9182 | 0.0214 | 0.39567 | 2.1493 | 1.3598 | 0.0051899
1023.6 | 861.6 | 114.6526 | 0.13408 | 114.2522 | 2.0924 |  |  | 1.5536 | 0.0054818 | 3.4557 | 0.022855 | 3.0156 | 0.0214 | 0.39567 | 2.1607 | 1.3598 | 0.0051899
1023.8 | 861.8 | 114.5552 | 0.1422 | 114.0574 | 2.0891 |  |  | 1.651 | 0.0054818 | 3.4557 | 0.022855 | 3.0156 | 0.0214 | 0.39567 | 2.1655 | 1.3598 | 0.0051899
1024 | 862 | 114.1656 | 0.15031 | 113.7652 | 2.1135 |  |  | 1.651 | 0.0054818 | 3.4557 | 0.026101 | 3.0156 | 0.023023 | 0.39567 | 2.1996 | 1.3598 | 0.0051899
1024.2 | 862.2 | 114.0682 | 0.16817 | 113.6678 | 2.1086 |  |  | 1.7484 | 0.0054818 | 3.5531 | 0.024478 | 3.113 | 0.023023 | 0.49305 | 2.2094 | 1.3598 | 0.0051899
1024.4 | 862.4 | 113.8734 | 0.17953 | 113.473 | 2.1184 |  |  | 1.7484 | 0.0054818 | 3.5531 | 0.024478 | 3.113 | 0.023023 | 0.49305 | 2.2321 | 1.4572 | 0.0051899
1024.6 | 862.6 | 113.6786 | 0.19252 | 113.2782 | 2.1281 |  |  | 1.7484 | 0.0054818 | 3.4557 | 0.026101 | 3.113 | 0.024647 | 0.49305 | 2.2548 | 1.4572 | 0.0051899
1024.8 | 862.8 | 113.5812 | 0.20875 | 112.986 | 2.1232 |  |  | 1.8458 | 0.0054818 | 3.5531 | 0.026101 | 3.113 | 0.023023 | 0.39567 | 2.2645 | 1.4572 | 0.0051899
1025 | 863 | 113.1916 | 0.22336 | 112.7912 | 2.1313 |  |  | 1.8458 | 0.0038588 | 3.6505 | 0.026101 | 3.2104 | 0.024647 | 0.49305 | 2.284 | 1.5546 | 0.0051899
1025.2 | 863.2 | 112.9968 | 0.25583 | 112.499 | 2.12 |  |  | 1.7484 | 0.0054818 | 3.6505 | 0.026101 | 3.113 | 0.024647 | 0.39567 | 2.3084 | 1.4572 | 0.0051899
1025.4 | 863.4 | 112.6072 | 0.2818 | 112.2069 | 2.1265 |  |  | 1.8458 | 0.0038588 | 3.6505 | 0.026101 | 3.2104 | 0.024647 | 0.49305 | 2.336 | 1.5546 | 0.0068129
1025.6 | 863.6 | 112.5098 | 0.29965 | 112.0121 | 2.1313 |  |  | 1.8458 | 0.0054818 | 3.7479 | 0.026101 | 3.2104 | 0.024647 | 0.39567 | 2.3619 | 1.5546 | 0.0068129
1025.8 | 863.8 | 112.3151 | 0.31751 | 111.7199 | 2.1427 |  |  | 1.8458 | 0.0054818 | 3.7479 | 0.027725 | 3.2104 | 0.024647 | 0.39567 | 2.3895 | 1.5546 | 0.0051899
1026 | 864 | 112.1203 | 0.33537 | 111.3303 | 2.1395 |  |  | 1.8458 | 0.0054818 | 3.7479 | 0.026101 | 3.3078 | 0.024647 | 0.49305 | 2.4106 | 1.652 | 0.0051899
1026.2 | 864.2 | 111.9255 | 0.3516 | 111.0381 | 2.1654 |  |  | 1.9432 | 0.0054818 | 3.8453 | 0.027725 | 3.4052 | 0.02627 | 0.49305 | 2.4463 | 1.652 | 0.0051899
1026.4 | 864.4 | 114.8474 | 0.37919 | 112.986 | 2.2109 |  |  | 1.9432 | 0.0054818 | 3.9427 | 0.029348 | 3.4052 | 0.02627 | 0.39567 | 2.5194 | 1.652 | 0.0051899
1026.6 | 864.6 | 115.237 | 0.40192 | 114.2522 | 2.2093 |  |  | 2.0406 | 0.0054818 | 3.9427 | 0.029348 | 3.5025 | 0.027894 | 0.49305 | 2.5405 | 1.652 | 0.0051899
1026.8 | 864.8 | 114.9448 | 0.41004 | 114.3496 | 2.2011 |  |  | 2.0406 | 0.0071055 | 4.0401 | 0.029348 | 3.5025 | 0.027894 | 0.49305 | 2.5405 | 1.652 | 0.0068129
1027 | 865 | 114.8474 | 0.42952 | 114.3496 | 2.193 |  |  | 2.0406 | 0.0054818 | 3.9427 | 0.029348 | 3.5025 | 0.02627 | 0.49305 | 2.5535 | 1.7494 | 0.0068129
1027.2 | 865.2 | 114.75 | 0.44575 | 114.2522 | 2.18 |  |  | 2.138 | 0.0054818 | 3.9427 | 0.029348 | 3.5025 | 0.027894 | 0.39567 | 2.5567 | 1.7494 | 0.0068129
1027.4 | 865.4 | 114.5552 | 0.45549 | 114.1548 | 2.1865 |  |  | 2.138 | 0.0054818 | 4.1375 | 0.029348 | 3.5025 | 0.027894 | 0.59047 | 2.573 | 1.7494 | 0.0051899
1027.6 | 865.6 | 114.4578 | 0.47172 | 114.0574 | 2.1849 |  |  | 2.138 | 0.0038588 | 4.1375 | 0.030972 | 3.6 | 0.02627 | 0.49305 | 2.586 | 1.7494 | 0.0051899
1027.8 | 865.8 | 114.3604 | 0.49282 | 113.96 | 2.1719 |  |  | 2.0406 | 0.0054818 | 4.1375 | 0.030972 | 3.6 | 0.02627 | 0.49305 | 2.5941 | 1.7494 | 0.0068129
1028 | 866 | 114.0682 | 0.5188 | 113.6678 | 2.1817 |  |  | 2.2354 | 0.0054818 | 4.2349 | 0.030972 | 3.6 | 0.027894 | 0.49305 | 2.6314 | 1.7494 | 0.0068129
1028.2 | 866.2 | 113.8734 | 0.53503 | 113.473 | 2.193 |  |  | 2.138 | 0.0054818 | 4.2349 | 0.030972 | 3.6 | 0.027894 | 0.59047 | 2.6574 | 1.8468 | 0.0051899
1028.4 | 866.4 | 113.6786 | 0.55451 | 113.3756 | 2.1947 |  |  | 2.2354 | 0.0038588 | 4.2349 | 0.030972 | 3.6973 | 0.027894 | 0.49305 | 2.6769 | 1.8468 | 0.0051899
1028.6 | 866.6 | 113.5812 | 0.56912 | 113.1808 | 2.2076 |  |  | 2.2354 | 0.0054818 | 4.2349 | 0.030972 | 3.6 | 0.029517 | 0.49305 | 2.7061 | 1.9442 | 0.0068129
1028.8 | 866.8 | 113.4838 | 0.58373 | 112.986 | 2.2011 |  |  | 2.2354 | 0.0054818 | 4.3323 | 0.030972 | 3.6973 | 0.027894 | 0.49305 | 2.7109 | 1.8468 | 0.0051899
1029 | 867 | 113.289 | 0.59022 | 112.8886 | 2.2239 |  |  | 2.2354 | 0.0054818 | 4.4297 | 0.030972 | 3.6973 | 0.029517 | 0.39567 | 2.7418 | 1.9442 | 0.0068129
1029.2 | 867.2 | 113.0942 | 0.6097 | 112.6938 | 2.219 |  |  | 2.2354 | 0.0054818 | 4.2349 | 0.032595 | 3.6973 | 0.029517 | 0.49305 | 2.7564 | 1.9442 | 0.0068129
1029.4 | 867.4 | 112.9968 | 0.62269 | 112.5965 | 2.2158 |  |  | 2.3328 | 0.0054818 | 4.3323 | 0.032595 | 3.7948 | 0.029517 | 0.39567 | 2.7661 | 1.9442 | 0.0068129
1029.6 | 867.6 | 112.8994 | 0.65353 | 112.4017 | 2.2158 |  |  | 2.3328 | 0.0054818 | 4.4297 | 0.032595 | 3.7948 | 0.029517 | 0.49305 | 2.7986 | 1.9442 | 0.0051899
1029.8 | 867.8 | 112.6072 | 0.66327 | 112.2069 | 2.2352 |  |  | 2.3328 | 0.0038588 | 4.5271 | 0.032595 | 3.7948 | 0.029517 | 0.59047 | 2.8246 | 2.0416 | 0.0051899
1030 | 868 | 112.5098 | 0.67463 | 112.1095 | 2.2401 |  |  | 2.2354 | 0.0054818 | 4.4297 | 0.032595 | 3.8921 | 0.027894 | 0.39567 | 2.8424 | 1.9442 | 0.0051899
1030.2 | 868.2 | 112.3151 | 0.69411 | 111.8173 | 2.2547 |  |  | 2.4302 | 0.0054818 | 4.5271 | 0.032595 | 3.8921 | 0.029517 | 0.59047 | 2.8733 | 2.0416 | 0.0068129
1030.4 | 868.4 | 112.1203 | 0.70872 | 111.7199 | 2.2547 |  |  | 2.5276 | 0.0038588 | 4.5271 | 0.032595 | 3.9895 | 0.029517 | 0.39567 | 2.8879 | 2.0416 | 0.0068129
1030.6 | 868.6 | 111.9255 | 0.73794 | 111.5251 | 2.2547 |  |  | 2.4302 | 0.0054818 | 4.5271 | 0.034218 | 3.8921 | 0.03114 | 0.39567 | 2.9171 | 2.0416 | 0.0068129
1030.8 | 868.8 | 111.7307 | 0.7558 | 111.3303 | 2.2563 |  |  | 2.4302 | 0.0054818 | 4.5271 | 0.034218 | 3.9895 | 0.03114 | 0.39567 | 2.9366 | 2.0416 | 0.0068129
1031 | 869 | 111.4385 | 0.78014 | 111.0381 | 2.2596 |  |  | 2.4302 | 0.0054818 | 4.5271 | 0.035841 | 3.9895 | 0.03114 | 0.49305 | 2.9642 | 2.0416 | 0.0068129
1031.2 | 869.2 | 111.4385 | 0.79151 | 110.9407 | 2.2531 |  |  | 2.5276 | 0.0054818 | 4.6245 | 0.034218 | 3.9895 | 0.03114 | 0.49305 | 2.9674 | 2.139 | 0.0051899
1031.4 | 869.4 | 111.3411 | 0.80125 | 110.8433 | 2.2612 |  |  | 2.4302 | 0.0054818 | 4.6245 | 0.034218 | 3.9895 | 0.03114 | 0.39567 | 2.9869 | 2.139 | 0.0051899
1031.6 | 869.6 | 111.3411 | 0.81261 | 110.8433 | 2.2547 |  |  | 2.5276 | 0.0038588 | 4.6245 | 0.035841 | 3.8921 | 0.03114 | 0.49305 | 2.9901 | 2.139 | 0.0051899
1031.8 | 869.8 | 111.0489 | 0.83209 | 110.6485 | 2.2645 |  |  | 2.5276 | 0.0054818 | 4.7219 | 0.034218 | 4.0869 | 0.03114 | 0.39567 | 3.0194 | 2.139 | 0.0051899
1032 | 870 | 110.6593 | 0.84183 | 110.2589 | 2.3002 |  |  | 2.5276 | 0.0054818 | 4.6245 | 0.035841 | 3.9895 | 0.03114 | 0.49305 | 3.0632 | 2.139 | 0.0068129
1032.2 | 870.2 | 110.6593 | 0.85157 | 110.2589 | 2.2969 |  |  | 2.625 | 0.0038588 | 4.7219 | 0.035841 | 4.0869 | 0.03114 | 0.39567 | 3.0697 | 2.2364 | 0.0051899
1032.4 | 870.4 | 110.4645 | 0.87105 | 110.0641 | 2.3002 |  |  | 2.5276 | 0.0054818 | 4.7219 | 0.034218 | 4.0869 | 0.032763 | 0.39567 | 3.0924 | 2.2364 | 0.0051899
1032.6 | 870.6 | 110.2697 | 0.88241 | 109.8693 | 2.3083 |  |  | 2.625 | 0.0054818 | 4.8193 | 0.035841 | 4.0869 | 0.03114 | 0.49305 | 3.1135 | 2.2364 | 0.0051899
1032.8 | 870.8 | 110.2697 | 0.8954 | 109.772 | 2.3067 |  |  | 2.625 | 0.0054818 | 4.8193 | 0.035841 | 4.1843 | 0.032763 | 0.49305 | 3.1249 | 2.2364 | 0.0051899
1033 | 871 | 110.0749 | 0.91325 | 109.6745 | 2.3115 |  |  | 2.5276 | 0.0054818 | 4.8193 | 0.037464 | 4.1843 | 0.032763 | 0.39567 | 3.1444 | 2.3338 | 0.0051899
1033.2 | 871.2 | 109.8801 | 0.93273 | 109.4798 | 2.3196 |  |  | 2.625 | 0.0054818 | 4.9167 | 0.035841 | 4.1843 | 0.032763 | 0.49305 | 3.1752 | 2.2364 | 0.0051899
1033.4 | 871.4 | 109.8801 | 0.94247 | 109.3824 | 2.3213 |  |  | 2.625 | 0.0054818 | 4.8193 | 0.037464 | 4.1843 | 0.034386 | 0.49305 | 3.1849 | 2.2364 | 0.0051899
1033.6 | 871.6 | 109.6854 | 0.9587 | 109.285 | 2.3213 |  |  | 2.7224 | 0.0054818 | 4.9167 | 0.037464 | 4.1843 | 0.032763 | 0.59047 | 3.2028 | 2.3338 | 0.0051899
1033.8 | 871.8 | 109.4906 | 0.97007 | 108.9928 | 2.331 |  |  | 2.7224 | 0.0054818 | 5.0141 | 0.037464 | 4.2817 | 0.032763 | 0.49305 | 3.2271 | 2.4312 | 0.0051899
1034 | 872 | 109.1984 | 0.99117 | 108.798 | 2.3391 |  |  | 2.8198 | 0.0054818 | 5.0141 | 0.037464 | 4.2817 | 0.034386 | 0.20087 | 3.2547 | 2.3338 | 0.0068129
1034.2 | 872.2 | 109.0036 | 0.99442 | 108.6032 | 2.3683 |  |  | 2.8198 | 0.0038588 | 5.0141 | 0.039088 | 4.3791 | 0.034386 | 0.49305 | 3.2807 | 2.4312 | 0.0051899
1034.4 | 872.4 | 108.9062 | 1.009 | 108.5058 | 2.3635 |  |  | 2.8198 | 0.0038588 | 5.1115 | 0.039088 | 4.3791 | 0.03601 | 0.49305 | 3.2969 | 2.4312 | 0.0051899
1034.6 | 872.6 | 108.7114 | 1.0171 | 108.2136 | 2.3862 |  |  | 2.8198 | 0.0054818 | 5.1115 | 0.039088 | 4.4765 | 0.034386 | 0.49305 | 3.3262 | 2.4312 | 0.0051899
1034.8 | 872.8 | 108.614 | 1.0318 | 108.2136 | 2.3781 |  |  | 2.9172 | 0.0054818 | 5.1115 | 0.039088 | 4.3791 | 0.034386 | 0.49305 | 3.331 | 2.5286 | 0.0051899
1035 | 873 | 108.3218 | 1.048 | 107.9214 | 2.4089 |  |  | 2.9172 | 0.0054818 | 5.2089 | 0.039088 | 4.5739 | 0.034386 | 0.49305 | 3.3781 | 2.5286 | 0.0051899
1035.2 | 873.2 | 108.2244 | 1.0626 | 107.824 | 2.3862 |  |  | 2.8198 | 0.0071055 | 5.2089 | 0.037464 | 4.4765 | 0.034386 | 0.49305 | 3.3716 | 2.4312 | 0.0051899
1035.4 | 873.4 | 108.3218 | 1.0642 | 107.9214 | 2.3911 |  |  | 2.9172 | 0.0054818 | 5.3063 | 0.037464 | 4.5739 | 0.03601 | 0.49305 | 3.3797 | 2.4312 | 0.0051899
1035.6 | 873.6 | 108.127 | 1.0707 | 107.824 | 2.3943 |  |  | 2.9172 | 0.0054818 | 5.2089 | 0.040711 | 4.4765 | 0.03601 | 0.49305 | 3.3895 | 2.5286 | 0.0051899
1035.8 | 873.8 | 108.0296 | 1.0837 | 107.6292 | 2.4041 |  |  | 2.9172 | 0.0054818 | 5.3063 | 0.039088 | 4.4765 | 0.034386 | 0.49305 | 3.4122 | 2.5286 | 0.0068129
1036 | 874 | 107.8348 | 1.0983 | 107.4344 | 2.4057 |  |  | 2.9172 | 0.0054818 | 5.3063 | 0.039088 | 4.4765 | 0.03601 | 0.49305 | 3.4301 | 2.626 | 0.0051899
1036.2 | 874.2 | 107.64 | 1.108 | 107.337 | 2.4219 |  |  | 2.9172 | 0.0054818 | 5.3063 | 0.040711 | 4.5739 | 0.03601 | 0.49305 | 3.4528 | 2.626 | 0.0068129
1036.4 | 874.4 | 107.5426 | 1.1032 | 107.1422 | 2.4463 |  |  | 2.9172 | 0.0054818 | 5.3063 | 0.040711 | 4.6713 | 0.037633 | 0.49305 | 3.4706 | 2.626 | 0.0051899
1036.6 | 874.6 | 107.3478 | 1.1162 | 107.0448 | 2.4414 |  |  | 2.9172 | 0.0054818 | 5.3063 | 0.040711 | 4.6713 | 0.034386 | 0.49305 | 3.4788 | 2.626 | 0.0068129
1036.8 | 874.8 | 107.4452 | 1.1145 | 107.1422 | 2.4463 |  |  | 2.9172 | 0.0054818 | 5.4037 | 0.040711 | 4.5739 | 0.03601 | 0.39567 | 3.482 | 2.7234 | 0.0035663
1037 | 875 | 107.3478 | 1.1227 | 106.9474 | 2.4511 |  |  | 2.9172 | 0.0054818 | 5.4037 | 0.040711 | 4.6713 | 0.037633 | 0.49305 | 3.495 | 2.626 | 0.0051899
1037.2 | 875.2 | 107.153 | 1.1308 | 106.7526 | 2.4544 |  |  | 2.9172 | 0.0054818 | 5.4037 | 0.042334 | 4.6713 | 0.03601 | 0.49305 | 3.508 | 2.5286 | 0.0051899
1037.4 | 875.4 | 107.3478 | 1.1291 | 106.8501 | 2.4576 |  |  | 3.0146 | 0.0054818 | 5.4037 | 0.040711 | 4.6713 | 0.037633 | 0.39567 | 3.5096 | 2.626 | 0.0068129
1037.6 | 875.6 | 107.0556 | 1.1324 | 106.6553 | 2.4787 |  |  | 3.0146 | 0.0038588 | 5.4037 | 0.040711 | 4.6713 | 0.037633 | 0.68785 | 3.5323 | 2.7234 | 0.0068129
1037.8 | 875.8 | 106.9582 | 1.1356 | 106.6553 | 2.4836 |  |  | 3.0146 | 0.0054818 | 5.4037 | 0.040711 | 4.6713 | 0.03601 | 0.39567 | 3.5437 | 2.626 | 0.0068129
1038 | 876 | 106.9582 | 1.1421 | 106.5578 | 2.4787 |  |  | 3.112 | 0.0054818 | 5.5011 | 0.042334 | 4.6713 | 0.037633 | 0.39567 | 3.5453 | 2.7234 | 0.0068129
1038.2 | 876.2 | 106.8608 | 1.1438 | 106.5578 | 2.482 |  |  | 3.0146 | 0.0038588 | 5.5011 | 0.042334 | 4.7687 | 0.039257 | 0.49305 | 3.5453 | 2.7234 | 0.0068129
1038.4 | 876.4 | 106.7634 | 1.1486 | 106.4605 | 2.4933 |  |  | 3.0146 | 0.0054818 | 5.4037 | 0.042334 | 4.7687 | 0.037633 | 0.39567 | 3.5648 | 2.7234 | 0.0068129
1038.6 | 876.6 | 106.9582 | 1.1454 | 106.4605 | 2.4885 |  |  | 3.0146 | 0.0054818 | 5.4037 | 0.043958 | 4.7687 | 0.037633 | 0.49305 | 3.555 | 2.7234 | 0.0084366
1038.8 | 876.8 | 106.8608 | 1.1454 | 106.5578 | 2.4901 |  |  | 3.112 | 0.0054818 | 5.4037 | 0.042334 | 4.7687 | 0.037633 | 0.39567 | 3.5599 | 2.7234 | 0.0068129
1039 | 877 | 106.8608 | 1.1535 | 106.4605 | 2.4755 |  |  | 3.0146 | 0.0054818 | 5.4037 | 0.040711 | 4.6713 | 0.037633 | 0.49305 | 3.5518 | 2.7234 | 0.0051899
1039.2 | 877.2 | 106.8608 | 1.1535 | 106.3631 | 2.4852 |  |  | 3.0146 | 0.0054818 | 5.4037 | 0.043958 | 4.7687 | 0.039257 | 0.59047 | 3.5632 | 2.8208 | 0.0051899
1039.4 | 877.4 | 106.666 | 1.1567 | 106.2657 | 2.4966 |  |  | 2.9172 | 0.0054818 | 5.5011 | 0.042334 | 4.8661 | 0.039257 | 0.49305 | 3.5778 | 2.7234 | 0.0068129
1039.6 | 877.6 | 106.5687 | 1.1503 | 106.1683 | 2.5193 |  |  | 3.112 | 0.0054818 | 5.5011 | 0.042334 | 4.8661 | 0.037633 | 0.39567 | 3.5924 | 2.7234 | 0.0051899
1039.8 | 877.8 | 106.666 | 1.1649 | 106.2657 | 2.4966 |  |  | 3.112 | 0.0054818 | 5.5011 | 0.043958 | 4.8661 | 0.039257 | 0.49305 | 3.5875 | 2.7234 | 0.0051899
1040 | 878 | 106.666 | 1.1616 | 106.2657 | 2.495 |  |  | 3.0146 | 0.0071055 | 5.5011 | 0.042334 | 4.7687 | 0.037633 | 0.49305 | 3.5826 | 2.7234 | 0.0068129
1040.2 | 878.2 | 106.666 | 1.1567 | 106.2657 | 2.5063 |  |  | 3.112 | 0.0054818 | 5.5011 | 0.042334 | 4.7687 | 0.039257 | 0.49305 | 3.5859 | 2.8208 | 0.0051899
1040.4 | 878.4 | 106.5687 | 1.1632 | 106.0709 | 2.5144 |  |  | 3.0146 | 0.0054818 | 5.5011 | 0.042334 | 4.8661 | 0.04088 | 0.49305 | 3.6037 | 2.8208 | 0.0068129
1040.6 | 878.6 | 106.666 | 1.1681 | 106.1683 | 2.5096 |  |  | 3.112 | 0.0054818 | 5.5011 | 0.043958 | 4.8661 | 0.037633 | 0.49305 | 3.6021 | 2.7234 | 0.0051899
1040.8 | 878.8 | 106.5687 | 1.1746 | 106.1683 | 2.5063 |  |  | 3.0146 | 0.0054818 | 5.5011 | 0.043958 | 4.7687 | 0.039257 | 0.49305 | 3.6086 | 2.8208 | 0.0051899
1041 | 879 | 106.4712 | 1.1778 | 106.0709 | 2.5079 |  |  | 3.112 | 0.0071055 | 5.5011 | 0.042334 | 4.7687 | 0.04088 | 0.49305 | 3.6119 | 2.7234 | 0.0068129
1041.2 | 879.2 | 106.4712 | 1.1665 | 106.1683 | 2.5177 |  |  | 3.112 | 0.0038588 | 5.5985 | 0.043958 | 4.9635 | 0.039257 | 0.49305 | 3.6135 | 2.8208 | 0.0084366
1041.4 | 879.4 | 106.4712 | 1.1649 | 106.0709 | 2.5209 |  |  | 3.112 | 0.0054818 | 5.5011 | 0.042334 | 4.8661 | 0.037633 | 0.59047 | 3.6119 | 2.8208 | 0.0068129
1041.6 | 879.6 | 106.4712 | 1.1697 | 106.0709 | 2.5161 |  |  | 3.0146 | 0.0054818 | 5.5985 | 0.042334 | 4.9635 | 0.039257 | 0.59047 | 3.6135 | 2.8208 | 0.0084366
1041.8 | 879.8 | 106.4712 | 1.1746 | 106.0709 | 2.5161 |  |  | 3.112 | 0.0071055 | 5.5011 | 0.042334 | 4.8661 | 0.039257 | 0.49305 | 3.6184 | 2.8208 | 0.0051899
1042 | 880 | 106.4712 | 1.1649 | 106.1683 | 2.5079 |  |  | 3.0146 | 0.0054818 | 5.5985 | 0.043958 | 4.8661 | 0.037633 | 0.49305 | 3.6021 | 2.7234 | 0.0051899
1042.2 | 880.2 | 106.4712 | 1.173 | 105.9735 | 2.5177 |  |  | 3.112 | 0.0054818 | 5.5985 | 0.042334 | 5.0609 | 0.039257 | 0.49305 | 3.62 | 2.8208 | 0.0051899
1042.4 | 880.4 | 106.3739 | 1.1697 | 105.8761 | 2.5339 |  |  | 3.2094 | 0.0054818 | 5.5985 | 0.043958 | 4.8661 | 0.039257 | 0.49305 | 3.6297 | 2.8208 | 0.0068129
1042.6 | 880.6 | 106.3739 | 1.186 | 105.9735 | 2.5161 |  |  | 3.112 | 0.0054818 | 5.5985 | 0.043958 | 4.8661 | 0.039257 | 0.49305 | 3.6281 | 2.8208 | 0.0051899
1042.8 | 880.8 | 106.3739 | 1.1795 | 105.9735 | 2.5193 |  |  | 3.112 | 0.0054818 | 5.5985 | 0.043958 | 4.9635 | 0.039257 | 0.49305 | 3.6265 | 2.8208 | 0.0051899
1043 | 881 | 106.4712 | 1.1762 | 106.0709 | 2.5193 |  |  | 3.2094 | 0.0054818 | 5.5985 | 0.042334 | 4.9635 | 0.039257 | 0.59047 | 3.6232 | 2.8208 | 0.0068129
1043.2 | 881.2 | 106.3739 | 1.1811 | 105.9735 | 2.5242 |  |  | 3.112 | 0.0054818 | 5.6958 | 0.042334 | 4.9635 | 0.039257 | 0.39567 | 3.633 | 2.9182 | 0.0068129
1043.4 | 881.4 | 106.2764 | 1.1778 | 105.8761 | 2.5323 |  |  | 3.2094 | 0.0054818 | 5.5985 | 0.043958 | 4.9635 | 0.039257 | 0.49305 | 3.6395 | 2.9182 | 0.0068129
1043.6 | 881.6 | 106.1791 | 1.1778 | 105.8761 | 2.5339 |  |  | 3.112 | 0.0054818 | 5.5985 | 0.043958 | 4.8661 | 0.039257 | 0.39567 | 3.6427 | 2.9182 | 0.0051899
1043.8 | 881.8 | 106.1791 | 1.1697 | 105.7787 | 2.5501 |  |  | 3.2094 | 0.0054818 | 5.6958 | 0.045581 | 4.9635 | 0.04088 | 0.49305 | 3.6492 | 2.9182 | 0.0051899
1044 | 882 | 105.9843 | 1.1811 | 105.6813 | 2.5583 |  |  | 3.2094 | 0.0054818 | 5.6958 | 0.043958 | 5.0609 | 0.04088 | 0.49305 | 3.6671 | 2.9182 | 0.0068129
1044.2 | 882.2 | 106.0817 | 1.1762 | 105.7787 | 2.5583 |  |  | 3.2094 | 0.0054818 | 5.6958 | 0.043958 | 4.9635 | 0.039257 | 0.49305 | 3.6654 | 2.8208 | 0.0068129
1044.4 | 882.4 | 106.0817 | 1.173 | 105.6813 | 2.568 |  |  | 3.2094 | 0.0071055 | 5.6958 | 0.043958 | 5.0609 | 0.04088 | 0.49305 | 3.6703 | 2.8208 | 0.0068129
1044.6 | 882.6 | 106.0817 | 1.1811 | 105.5839 | 2.5713 |  |  | 3.2094 | 0.0054818 | 5.6958 | 0.043958 | 4.9635 | 0.04088 | 0.59047 | 3.6833 | 2.9182 | 0.0068129
1044.8 | 882.8 | 105.9843 | 1.1665 | 105.5839 | 2.5794 |  |  | 3.2094 | 0.0054818 | 5.6958 | 0.043958 | 5.1583 | 0.039257 | 0.49305 | 3.6784 | 3.0156 | 0.0084366
1045 | 883 | 106.0817 | 1.1746 | 105.6813 | 2.5583 |  |  | 3.2094 | 0.0054818 | 5.6958 | 0.043958 | 4.9635 | 0.04088 | 0.49305 | 3.6654 | 2.9182 | 0.0068129
1045.2 | 883.2 | 106.0817 | 1.1843 | 105.6813 | 2.5501 |  |  | 3.2094 | 0.0054818 | 5.7933 | 0.043958 | 5.0609 | 0.039257 | 0.59047 | 3.6654 | 2.9182 | 0.0068129
1045.4 | 883.4 | 106.1791 | 1.1697 | 105.7787 | 2.5615 |  |  | 3.3068 | 0.0054818 | 5.7933 | 0.043958 | 5.0609 | 0.039257 | 0.49305 | 3.6622 | 2.9182 | 0.0068129
1045.6 | 883.6 | 106.1791 | 1.173 | 105.7787 | 2.5631 |  |  | 3.2094 | 0.0054818 | 5.7933 | 0.045581 | 5.0609 | 0.039257 | 0.59047 | 3.6703 | 3.0156 | 0.0051899
1045.8 | 883.8 | 106.0817 | 1.1714 | 105.7787 | 2.5729 |  |  | 3.2094 | 0.0054818 | 5.7933 | 0.043958 | 5.0609 | 0.04088 | 0.49305 | 3.6752 | 3.0156 | 0.0068129
1046 | 884 | 106.1791 | 1.1681 | 105.6813 | 2.5648 |  |  | 3.3068 | 0.0054818 | 5.7933 | 0.045581 | 5.0609 | 0.04088 | 0.49305 | 3.6654 | 2.9182 | 0.0068129
1046.2 | 884.2 | 106.0817 | 1.1892 | 105.6813 | 2.5501 |  |  | 3.2094 | 0.0071055 | 5.7933 | 0.045581 | 5.0609 | 0.04088 | 0.49305 | 3.6719 | 2.9182 | 0.0051899
1046.4 | 884.4 | 105.9843 | 1.1827 | 105.5839 | 2.5631 |  |  | 3.3068 | 0.0054818 | 5.7933 | 0.045581 | 5.0609 | 0.042503 | 0.49305 | 3.6768 | 2.9182 | 0.0068129
1046.6 | 884.6 | 106.0817 | 1.1778 | 105.5839 | 2.5745 |  |  | 3.3068 | 0.0054818 | 5.7933 | 0.045581 | 5.0609 | 0.04088 | 0.49305 | 3.6849 | 3.0156 | 0.0068129
1046.8 | 884.8 | 105.8869 | 1.1957 | 105.4865 | 2.5648 |  |  | 3.3068 | 0.0054818 | 5.7933 | 0.045581 | 5.0609 | 0.042503 | 0.49305 | 3.693 | 2.9182 | 0.0068129
1047 | 885 | 105.7895 | 1.1843 | 105.3891 | 2.5891 |  |  | 3.2094 | 0.0054818 | 5.7933 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7028 | 3.0156 | 0.0068129
1047.2 | 885.2 | 105.8869 | 1.1778 | 105.4865 | 2.5875 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.6963 | 3.0156 | 0.0068129
1047.4 | 885.4 | 105.7895 | 1.1762 | 105.4865 | 2.6021 |  |  | 3.2094 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.042503 | 0.49305 | 3.7076 | 3.0156 | 0.0068129
1047.6 | 885.6 | 105.7895 | 1.1681 | 105.3891 | 2.6183 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7174 | 2.9182 | 0.0051899
1047.8 | 885.8 | 105.7895 | 1.1762 | 105.3891 | 2.6086 |  |  | 3.2094 | 0.0071055 | 5.8906 | 0.045581 | 5.0609 | 0.04088 | 0.49305 | 3.7141 | 3.0156 | 0.0068129
1048 | 886 | 105.7895 | 1.1827 | 105.3891 | 2.5956 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.0609 | 0.04088 | 0.59047 | 3.7109 | 3.0156 | 0.0068129
1048.2 | 886.2 | 105.6921 | 1.1795 | 105.3891 | 2.6135 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7239 | 3.0156 | 0.0068129
1048.4 | 886.4 | 105.7895 | 1.1746 | 105.3891 | 2.6086 |  |  | 3.2094 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.042503 | 0.49305 | 3.7158 | 3.0156 | 0.0051899
1048.6 | 886.6 | 105.7895 | 1.1714 | 105.3891 | 2.6199 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.042503 | 0.49305 | 3.7222 | 3.0156 | 0.0068129
1048.8 | 886.8 | 105.6921 | 1.1778 | 105.3891 | 2.6086 |  |  | 3.4042 | 0.0054818 | 5.8906 | 0.045581 | 5.0609 | 0.04088 | 0.49305 | 3.719 | 3.113 | 0.0068129
1049 | 887 | 105.7895 | 1.1714 | 105.3891 | 2.6135 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.2557 | 0.04088 | 0.49305 | 3.7158 | 3.113 | 0.0051899
1049.2 | 887.2 | 105.7895 | 1.1584 | 105.4865 | 2.6086 |  |  | 3.2094 | 0.0054818 | 5.8906 | 0.045581 | 5.0609 | 0.042503 | 0.49305 | 3.7011 | 3.0156 | 0.0068129
1049.4 | 887.4 | 105.7895 | 1.1697 | 105.4865 | 2.6021 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.042503 | 0.49305 | 3.7044 | 3.0156 | 0.0051899
1049.6 | 887.6 | 105.8869 | 1.1697 | 105.3891 | 2.6102 |  |  | 3.3068 | 0.0038588 | 5.8906 | 0.045581 | 5.2557 | 0.04088 | 0.49305 | 3.7141 | 3.0156 | 0.0051899
1049.8 | 887.8 | 105.7895 | 1.1681 | 105.4865 | 2.6037 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.2557 | 0.04088 | 0.49305 | 3.7076 | 3.0156 | 0.0068129
1050 | 888 | 105.7895 | 1.173 | 105.4865 | 2.6053 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.04088 | 0.49305 | 3.7141 | 3.0156 | 0.0068129
1050.2 | 888.2 | 105.8869 | 1.173 | 105.4865 | 2.5956 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.042503 | 0.49305 | 3.7028 | 3.0156 | 0.0051899
1050.4 | 888.4 | 105.8869 | 1.1778 | 105.4865 | 2.594 |  |  | 3.3068 | 0.0038588 | 5.8906 | 0.045581 | 5.1583 | 0.039257 | 0.59047 | 3.706 | 3.0156 | 0.0051899
1050.6 | 888.6 | 105.9843 | 1.1746 | 105.6813 | 2.5875 |  |  | 3.2094 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.042503 | 0.49305 | 3.6979 | 3.0156 | 0.0068129
1050.8 | 888.8 | 105.8869 | 1.173 | 105.5839 | 2.5826 |  |  | 3.2094 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.042503 | 0.49305 | 3.6914 | 3.0156 | 0.0051899
1051 | 889 | 105.8869 | 1.1697 | 105.5839 | 2.5972 |  |  | 3.2094 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7028 | 3.0156 | 0.0051899
1051.2 | 889.2 | 105.8869 | 1.1681 | 105.4865 | 2.6005 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.04088 | 0.49305 | 3.7011 | 2.9182 | 0.0068129
1051.4 | 889.4 | 105.8869 | 1.1665 | 105.5839 | 2.6053 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7076 | 2.9182 | 0.0068129
1051.6 | 889.6 | 105.9843 | 1.1551 | 105.5839 | 2.6053 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.6946 | 3.0156 | 0.0051899
1051.8 | 889.8 | 105.8869 | 1.1616 | 105.4865 | 2.6151 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.04088 | 0.39567 | 3.7125 | 3.0156 | 0.0068129
1052 | 890 | 105.9843 | 1.1616 | 105.4865 | 2.5972 |  |  | 3.4042 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.693 | 3.0156 | 0.0051899
1052.2 | 890.2 | 105.7895 | 1.1584 | 105.4865 | 2.6053 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.6995 | 3.0156 | 0.0051899
1052.4 | 890.4 | 105.8869 | 1.1535 | 105.4865 | 2.6216 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.2557 | 0.04088 | 0.49305 | 3.7093 | 3.0156 | 0.0051899
1052.6 | 890.6 | 105.7895 | 1.1486 | 105.3891 | 2.6313 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7158 | 3.0156 | 0.0051899
1052.8 | 890.8 | 105.7895 | 1.147 | 105.4865 | 2.6346 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.1583 | 0.04088 | 0.49305 | 3.7141 | 3.0156 | 0.0051899
1053 | 891 | 105.8869 | 1.1649 | 105.4865 | 2.6118 |  |  | 3.2094 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.042503 | 0.49305 | 3.7093 | 3.0156 | 0.0051899
1053.2 | 891.2 | 105.7895 | 1.16 | 105.4865 | 2.6199 |  |  | 3.2094 | 0.0054818 | 5.9881 | 0.047204 | 5.0609 | 0.042503 | 0.49305 | 3.7125 | 3.0156 | 0.0051899
1053.4 | 891.4 | 105.7895 | 1.1584 | 105.4865 | 2.6199 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.04088 | 0.39567 | 3.7125 | 3.0156 | 0.0068129
1053.6 | 891.6 | 105.7895 | 1.1535 | 105.3891 | 2.6264 |  |  | 3.4042 | 0.0038588 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7125 | 3.0156 | 0.0051899
1053.8 | 891.8 | 105.6921 | 1.1616 | 105.3891 | 2.6313 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7239 | 3.0156 | 0.0051899
1054 | 892 | 105.6921 | 1.1567 | 105.2917 | 2.6313 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.1583 | 0.04088 | 0.39567 | 3.7206 | 3.0156 | 0.0051899
1054.2 | 892.2 | 105.6921 | 1.1584 | 105.2917 | 2.6297 |  |  | 3.3068 | 0.0054818 | 5.8906 | 0.047204 | 5.1583 | 0.042503 | 0.39567 | 3.7174 | 3.0156 | 0.0051899
1054.4 | 892.4 | 105.6921 | 1.1551 | 105.3891 | 2.6394 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.39567 | 3.7255 | 3.0156 | 0.0051899
1054.6 | 892.6 | 105.6921 | 1.1584 | 105.2917 | 2.6394 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.732 | 3.0156 | 0.0051899
1054.8 | 892.8 | 105.7895 | 1.1616 | 105.3891 | 2.6232 |  |  | 3.4042 | 0.0054818 | 5.9881 | 0.047204 | 5.1583 | 0.04088 | 0.49305 | 3.7222 | 3.0156 | 0.0051899
1055 | 893 | 105.5947 | 1.1519 | 105.2917 | 2.6427 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.1583 | 0.042503 | 0.49305 | 3.7271 | 3.0156 | 0.0051899
1055.2 | 893.2 | 105.5947 | 1.1454 | 105.3891 | 2.6313 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.1583 | 0.04088 | 0.49305 | 3.7125 | 3.0156 | 0.0051899
1055.4 | 893.4 | 105.5947 | 1.1503 | 105.3891 | 2.6329 |  |  | 3.3068 | 0.0038588 | 5.9881 | 0.047204 | 5.1583 | 0.04088 | 0.49305 | 3.719 | 3.0156 | 0.0051899
1055.6 | 893.6 | 105.3999 | 1.1486 | 105.2917 | 2.6443 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.1583 | 0.04088 | 0.39567 | 3.7255 | 3.113 | 0.0051899
1055.8 | 893.8 | 105.3999 | 1.1519 | 105.3891 | 2.6378 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.045581 | 5.2557 | 0.04088 | 0.49305 | 3.7222 | 3.0156 | 0.0035663
1056 | 894 | 104.9129 | 1.1486 | 105.5839 | 2.6443 |  |  | 3.4042 | 0.0038588 | 5.9881 | 0.045581 | 5.2557 | 0.04088 | 0.39567 | 3.7239 | 3.113 | 0.0035663
1056.2 | 894.2 | 104.7181 | 1.1567 | 105.4865 | 2.6313 |  |  | 3.3068 | 0.0054818 | 6.0854 | 0.045581 | 5.2557 | 0.039257 | 0.49305 | 3.7206 | 3.0156 | 0.0051899
1056.4 | 894.4 | 105.3025 | 1.1616 | 105.3891 | 2.6346 |  |  | 3.4042 | 0.0054818 | 5.9881 | 0.045581 | 5.2557 | 0.04088 | 0.49305 | 3.7271 | 3.0156 | 0.0051899
1056.6 | 894.6 | 105.4973 | 1.1486 | 105.2917 | 2.6524 |  |  | 3.3068 | 0.0054818 | 6.0854 | 0.047204 | 5.1583 | 0.042503 | 0.49305 | 3.7336 | 3.0156 | 0.0051899
1056.8 | 894.8 | 105.5947 | 1.1535 | 105.1943 | 2.6475 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.045581 | 5.2557 | 0.042503 | 0.49305 | 3.732 | 3.113 | 0.0035663
1057 | 895 | 105.6921 | 1.147 | 105.3891 | 2.6475 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.045581 | 5.2557 | 0.042503 | 0.49305 | 3.7255 | 3.0156 | 0.0051899
1057.2 | 895.2 | 105.5947 | 1.1421 | 105.2917 | 2.6589 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.2557 | 0.04088 | 0.49305 | 3.7304 | 3.113 | 0.0051899
1057.4 | 895.4 | 105.5947 | 1.1454 | 105.2917 | 2.6638 |  |  | 3.2094 | 0.0054818 | 6.0854 | 0.047204 | 5.1583 | 0.042503 | 0.39567 | 3.7385 | 3.0156 | 0.0051899
1057.6 | 895.6 | 105.6921 | 1.1438 | 105.2917 | 2.6475 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.1583 | 0.042503 | 0.49305 | 3.7239 | 2.9182 | 0.0051899
1057.8 | 895.8 | 105.5947 | 1.1438 | 105.1943 | 2.6573 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.045581 | 5.2557 | 0.042503 | 0.49305 | 3.732 | 3.0156 | 0.0051899
1058 | 896 | 105.4973 | 1.1486 | 105.1943 | 2.6573 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.045581 | 5.1583 | 0.04088 | 0.39567 | 3.7369 | 3.0156 | 0.0051899
1058.2 | 896.2 | 105.4973 | 1.1356 | 104.9995 | 2.6784 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.047204 | 5.2557 | 0.042503 | 0.49305 | 3.7466 | 3.113 | 0.0035663
1058.4 | 896.4 | 105.4973 | 1.1405 | 105.0969 | 2.6686 |  |  | 3.3068 | 0.0054818 | 5.9881 | 0.047204 | 5.2557 | 0.042503 | 0.49305 | 3.7401 | 3.113 | 0.0051899
1058.6 | 896.6 | 105.3025 | 1.134 | 104.9995 | 2.6946 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.047204 | 5.3531 | 0.042503 | 0.49305 | 3.7596 | 3.113 | 0.0035663
1058.8 | 896.8 | 105.3999 | 1.134 | 105.0969 | 2.6833 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.047204 | 5.1583 | 0.042503 | 0.39567 | 3.7482 | 3.0156 | 0.0051899
1059 | 897 | 105.2051 | 1.1438 | 104.9021 | 2.6914 |  |  | 3.3068 | 0.0054818 | 6.0854 | 0.047204 | 5.2557 | 0.042503 | 0.39567 | 3.7644 | 3.0156 | 0.0051899
1059.2 | 897.2 | 105.3999 | 1.1389 | 104.9021 | 2.6865 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.047204 | 5.2557 | 0.042503 | 0.39567 | 3.7547 | 3.0156 | 0.0051899
1059.4 | 897.4 | 105.3025 | 1.1421 | 104.9021 | 2.6865 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.047204 | 5.3531 | 0.04088 | 0.49305 | 3.7596 | 3.2104 | 0.0051899
1059.6 | 897.6 | 105.2051 | 1.1438 | 104.8047 | 2.6914 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.047204 | 5.2557 | 0.042503 | 0.39567 | 3.7644 | 3.113 | 0.0051899
1059.8 | 897.8 | 105.2051 | 1.1551 | 104.8047 | 2.6865 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.047204 | 5.2557 | 0.042503 | 0.49305 | 3.7726 | 3.113 | 0.0051899
1060 | 898 | 105.2051 | 1.1405 | 104.9021 | 2.693 |  |  | 3.4042 | 0.0038588 | 6.1828 | 0.047204 | 5.3531 | 0.04088 | 0.49305 | 3.7644 | 3.113 | 0.0035663
1060.2 | 898.2 | 105.2051 | 1.1389 | 104.8047 | 2.7027 |  |  | 3.4042 | 0.0038588 | 6.0854 | 0.047204 | 5.3531 | 0.042503 | 0.49305 | 3.7709 | 3.2104 | 0.0035663
1060.4 | 898.4 | 105.1077 | 1.1438 | 104.8047 | 2.6962 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.048827 | 5.2557 | 0.042503 | 0.49305 | 3.7693 | 3.113 | 0.0051899
1060.6 | 898.6 | 105.1077 | 1.1389 | 104.7073 | 2.706 |  |  | 3.5016 | 0.0054818 | 6.1828 | 0.045581 | 5.3531 | 0.042503 | 0.39567 | 3.7758 | 3.113 | 0.0051899
1060.8 | 898.8 | 105.2051 | 1.1535 | 104.8047 | 2.6833 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.047204 | 5.3531 | 0.042503 | 0.49305 | 3.7693 | 3.113 | 0.0051899
1061 | 899 | 105.1077 | 1.1503 | 104.6099 | 2.7076 |  |  | 3.4042 | 0.0054818 | 6.2802 | 0.047204 | 5.4505 | 0.042503 | 0.49305 | 3.7856 | 3.2104 | 0.0035663
1061.2 | 899.2 | 105.0103 | 1.1454 | 104.7073 | 2.7157 |  |  | 3.4042 | 0.0038588 | 6.1828 | 0.048827 | 5.2557 | 0.042503 | 0.49305 | 3.7872 | 3.2104 | 0.0051899
1061.4 | 899.4 | 105.0103 | 1.1486 | 104.6099 | 2.7109 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.048827 | 5.3531 | 0.042503 | 0.49305 | 3.7872 | 3.113 | 0.0051899
1061.6 | 899.6 | 105.1077 | 1.1389 | 104.7073 | 2.7125 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.047204 | 5.3531 | 0.042503 | 0.49305 | 3.7807 | 3.113 | 0.0035663
1061.8 | 899.8 | 105.1077 | 1.1519 | 104.7073 | 2.6962 |  |  | 3.4042 | 0.0038588 | 6.2802 | 0.048827 | 5.3531 | 0.042503 | 0.49305 | 3.7774 | 3.2104 | 0.0035663
1062 | 900 | 105.0103 | 1.1438 | 104.6099 | 2.7044 |  |  | 3.5016 | 0.0038588 | 6.1828 | 0.047204 | 5.3531 | 0.042503 | 0.39567 | 3.7774 | 3.113 | 0.0051899
1062.2 | 900.2 | 105.0103 | 1.1389 | 104.6099 | 2.7109 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.048827 | 5.3531 | 0.044126 | 0.49305 | 3.7791 | 3.113 | 0.0051899
1062.4 | 900.4 | 105.0103 | 1.1519 | 104.6099 | 2.6995 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.047204 | 5.3531 | 0.042503 | 0.39567 | 3.7807 | 3.113 | 0.0051899
1062.6 | 900.6 | 104.9129 | 1.1454 | 104.5125 | 2.7157 |  |  | 3.5016 | 0.0054818 | 6.1828 | 0.048827 | 5.2557 | 0.042503 | 0.49305 | 3.7904 | 3.113 | 0.0051899
1062.8 | 900.8 | 104.9129 | 1.1454 | 104.4151 | 2.7287 |  |  | 3.4042 | 0.0038588 | 6.2802 | 0.047204 | 5.3531 | 0.042503 | 0.49305 | 3.8018 | 3.2104 | 0.0035663
1063 | 901 | 104.8155 | 1.1438 | 104.4151 | 2.7303 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.048827 | 5.2557 | 0.044126 | 0.39567 | 3.8018 | 3.2104 | 0.0051899
1063.2 | 901.2 | 104.9129 | 1.1389 | 104.5125 | 2.7271 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.05045 | 5.3531 | 0.042503 | 0.49305 | 3.7953 | 3.2104 | 0.0051899
1063.4 | 901.4 | 104.6207 | 1.1438 | 104.3177 | 2.7352 |  |  | 3.5016 | 0.0054818 | 6.1828 | 0.048827 | 5.3531 | 0.042503 | 0.49305 | 3.8067 | 3.113 | 0.0051899
1063.6 | 901.6 | 104.6207 | 1.1405 | 104.3177 | 2.7433 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.49305 | 3.8115 | 3.2104 | 0.0051899
1063.8 | 901.8 | 104.7181 | 1.134 | 104.3177 | 2.7482 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.49305 | 3.8115 | 3.2104 | 0.0051899
1064 | 902 | 104.7181 | 1.1356 | 104.3177 | 2.7417 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.047204 | 5.4505 | 0.042503 | 0.49305 | 3.8083 | 3.113 | 0.0051899
1064.2 | 902.2 | 104.7181 | 1.1421 | 104.3177 | 2.7466 |  |  | 3.4042 | 0.0071055 | 6.3776 | 0.048827 | 5.3531 | 0.042503 | 0.49305 | 3.8148 | 3.2104 | 0.0051899
1064.4 | 902.4 | 104.6207 | 1.1389 | 104.2204 | 2.7401 |  |  | 3.4042 | 0.0071055 | 6.2802 | 0.05045 | 5.3531 | 0.042503 | 0.49305 | 3.8083 | 3.2104 | 0.0051899
1064.6 | 902.6 | 104.7181 | 1.1291 | 104.3177 | 2.7498 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.4505 | 0.042503 | 0.49305 | 3.8067 | 3.2104 | 0.0051899
1064.8 | 902.8 | 104.7181 | 1.1373 | 104.4151 | 2.7336 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.4505 | 0.042503 | 0.49305 | 3.8002 | 3.2104 | 0.0051899
1065 | 903 | 104.7181 | 1.134 | 104.4151 | 2.7368 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.05045 | 5.3531 | 0.042503 | 0.49305 | 3.7985 | 3.2104 | 0.0051899
1065.2 | 903.2 | 104.7181 | 1.134 | 104.3177 | 2.7433 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.3531 | 0.042503 | 0.49305 | 3.805 | 3.2104 | 0.0051899
1065.4 | 903.4 | 104.6207 | 1.1356 | 104.3177 | 2.7401 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.4505 | 0.042503 | 0.49305 | 3.805 | 3.2104 | 0.0035663
1065.6 | 903.6 | 104.7181 | 1.1373 | 104.3177 | 2.7384 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.49305 | 3.805 | 3.2104 | 0.0068129
1065.8 | 903.8 | 104.6207 | 1.1227 | 104.3177 | 2.7579 |  |  | 3.5016 | 0.0054818 | 6.3776 | 0.048827 | 5.4505 | 0.042503 | 0.49305 | 3.8067 | 3.2104 | 0.0051899
1066 | 904 | 104.5233 | 1.1291 | 104.2204 | 2.7482 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.3531 | 0.044126 | 0.49305 | 3.8067 | 3.2104 | 0.0051899
1066.2 | 904.2 | 104.5233 | 1.1243 | 104.2204 | 2.7628 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.3531 | 0.044126 | 0.49305 | 3.8131 | 3.2104 | 0.0068129
1066.4 | 904.4 | 104.5233 | 1.1259 | 104.1229 | 2.7758 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.05045 | 5.3531 | 0.044126 | 0.49305 | 3.8278 | 3.2104 | 0.0051899
1066.6 | 904.6 | 104.6207 | 1.1259 | 104.2204 | 2.7644 |  |  | 3.599 | 0.0054818 | 6.2802 | 0.052074 | 5.3531 | 0.044126 | 0.20087 | 3.8196 | 2.9182 | 0.0051899
1066.8 | 904.8 | 104.5233 | 1.1389 | 104.1229 | 2.7596 |  |  | 3.5016 | 0.0071055 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.49305 | 3.8261 | 3.3078 | 0.0051899
1067 | 905 | 104.6207 | 1.1243 | 104.2204 | 2.7628 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.4505 | 0.042503 | 0.39567 | 3.8164 | 3.2104 | 0.0051899
1067.2 | 905.2 | 104.5233 | 1.1227 | 104.2204 | 2.7628 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.05045 | 5.4505 | 0.044126 | 0.49305 | 3.8115 | 3.2104 | 0.0051899
1067.4 | 905.4 | 104.4259 | 1.1178 | 104.0256 | 2.7807 |  |  | 3.4042 | 0.0054818 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.39567 | 3.8245 | 3.2104 | 0.0051899
1067.6 | 905.6 | 104.4259 | 1.1129 | 104.1229 | 2.7807 |  |  | 3.4042 | 0.0054818 | 6.3776 | 0.048827 | 5.4505 | 0.044126 | 0.39567 | 3.8213 | 3.2104 | 0.0051899
1067.8 | 905.8 | 104.2311 | 1.1227 | 103.8308 | 2.7871 |  |  | 3.4042 | 0.0054818 | 6.3776 | 0.048827 | 5.5479 | 0.044126 | 0.49305 | 3.8407 | 3.2104 | 0.0051899
1068 | 906 | 104.4259 | 1.1194 | 104.0256 | 2.7758 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.047204 | 5.5479 | 0.044126 | 0.49305 | 3.8213 | 3.5025 | 0.0051899
1068.2 | 906.2 | 104.4259 | 1.1178 | 104.0256 | 2.7758 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.05045 | 5.4505 | 0.044126 | 0.49305 | 3.8229 | 3.2104 | 0.0051899
1068.4 | 906.4 | 104.3285 | 1.121 | 103.8308 | 2.792 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.39567 | 3.8391 | 3.7948 | 0.0051899
1068.6 | 906.6 | 104.4259 | 1.1113 | 104.0256 | 2.7871 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.3531 | 0.044126 | 0.49305 | 3.8278 | 3.2104 | 0.0051899
1068.8 | 906.8 | 104.2311 | 1.1178 | 103.8308 | 2.7904 |  |  | 3.5016 | 0.0054818 | 6.3776 | 0.048827 | 5.7427 | 0.042503 | 0.68785 | 3.8359 | 3.0156 | 0.0051899
1069 | 907 | 104.2311 | 1.121 | 103.7334 | 2.7969 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.05045 | 5.3531 | 0.042503 | 0.39567 | 3.8407 | 3.3078 | 0.0035663
1069.2 | 907.2 | 104.2311 | 1.1145 | 103.9281 | 2.7953 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.056944 | 5.3531 | 0.044126 | 0.29825 | 3.8342 | 3.113 | 0.0051899
1069.4 | 907.4 | 104.1337 | 1.1259 | 103.7334 | 2.792 |  |  | 3.3068 | 0.0038588 | 6.2802 | 0.048827 | 5.5479 | 0.042503 | 0.68785 | 3.844 | 2.4312 | 0.0068129
1069.6 | 907.6 | 104.1337 | 1.1275 | 103.8308 | 2.7936 |  |  | 3.5016 | 0.0038588 | 6.3776 | 0.048827 | 5.1583 | 0.044126 | 0.39567 | 3.8472 | 3.2104 | 0.0068129
1069.8 | 907.8 | 104.2311 | 1.1194 | 103.8308 | 2.7936 |  |  | 3.5016 | 0.0054818 | 6.2802 | 0.048827 | 5.3531 | 0.042503 | 0.39567 | 3.844 | 3.0156 | 0.0051899
1070 | 908 | 104.1337 | 1.1227 | 104.0256 | 2.7807 |  |  | 3.2094 | 0.0054818 | 6.1828 | 0.048827 | 5.4505 | 0.042503 | 0.39567 | 3.8407 | 3.113 | 0.0051899
1070.2 | 908.2 | 104.0363 | 1.134 | 103.7334 | 2.7807 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.048827 | 5.3531 | 0.044126 | 0.49305 | 3.8359 | 3.2104 | 0.0068129
1070.4 | 908.4 | 103.8415 | 1.1129 | 103.149 | 2.7855 |  |  | 3.112 | 0.0054818 | 6.1828 | 0.048827 | 5.2557 | 0.044126 | 0.49305 | 3.8375 | 3.2104 | 0.0051899
1070.6 | 908.6 | 104.0363 | 1.1194 | 103.5386 | 2.805 |  |  | 3.4042 | 0.0038588 | 6.2802 | 0.048827 | 5.3531 | 0.042503 | 0.39567 | 3.8521 | 3.2104 | 0.0051899
1070.8 | 908.8 | 104.0363 | 1.121 | 103.636 | 2.8001 |  |  | 3.4042 | 0.0038588 | 6.2802 | 0.05045 | 5.8401 | 0.044126 | 0.49305 | 3.8456 | 3.2104 | 0.0051899
1071 | 909 | 104.0363 | 1.1145 | 103.636 | 2.8082 |  |  | 3.4042 | 0.0054818 | 6.0854 | 0.048827 | 5.5479 | 0.044126 | 0.49305 | 3.8489 | 3.113 | 0.0068129
1071.2 | 909.2 | 104.1337 | 1.1113 | 103.5386 | 2.8212 |  |  | 3.3068 | 0.0054818 | 6.2802 | 0.048827 | 5.4505 | 0.044126 | 0.39567 | 3.8537 | 3.2104 | 0.0068129
1071.4 | 909.4 | 103.939 | 1.1113 | 103.3438 | 2.8212 |  |  | 3.3068 | 0.0071055 | 6.2802 | 0.047204 | 5.4505 | 0.042503 | 0.59047 | 3.857 | 2.8208 | 0.0035663
1071.6 | 909.6 | 103.8415 | 1.1097 | 103.4412 | 2.8261 |  |  | 3.3068 | 0.0038588 | 6.2802 | 0.048827 | 5.4505 | 0.042503 | 0.49305 | 3.8602 | 3.0156 | 0.013306
1071.8 | 909.8 | 103.7442 | 1.1194 | 103.4412 | 2.8261 |  |  | 3.4042 | 0.0038588 | 6.3776 | 0.05045 | 5.4505 | 0.044126 | 0.20087 | 3.8716 | 3.2104 | 0.0051899
1072 | 910 | 104.0363 | 1.1194 | 103.4412 | 2.8212 |  |  | 3.5016 | 0.0038588 | 6.2802 | 0.048827 | 5.3531 | 0.052243 | 0.49305 | 3.8635 | 3.2104 | 0.0035663
1072.2 | 910.2 | 103.6467 | 1.1178 | 103.2464 | 2.8277 |  |  | 3.4042 | 0.0054818 | 6.3776 | 0.05045 | 5.2557 | 0.044126 | 0.49305 | 3.87 | 3.113 | 0.0051899
1072.4 | 910.4 | 103.6467 | 1.1162 | 103.3438 | 2.8375 |  |  | 3.5016 | 0.0054818 | 6.3776 | 0.05045 | 5.5479 | 0.042503 | 0.39567 | 3.8797 | 3.6 | 0.0068129
1072.6 | 910.6 | 103.7442 | 1.1162 | 103.3438 | 2.8261 |  |  | 3.5016 | 0.0054818 | 6.3776 | 0.05045 | 5.6453 | 0.044126 | 0.49305 | 3.8667 | 3.3078 | 0.0051899
1072.8 | 910.8 | 103.939 | 1.1194 | 103.3438 | 2.8212 |  |  | 3.4042 | 0.0038588 | 5.9881 | 0.048827 | 5.1583 | 0.044126 | 0.39567 | 3.8618 | 3.2104 | 0.0035663
1073 | 911 | 103.7442 | 1.1145 | 103.3438 | 2.8342 |  |  | 3.4042 | 0.0054818 | 6.2802 | 0.05045 | 5.5479 | 0.044126 | 0.29825 | 3.8765 | 3.113 | 0.0068129
1073.2 | 911.2 | 103.3546 | 1.1097 | 103.3438 | 2.8212 |  |  | 3.3068 | 0.0054818 | 6.5724 | 0.05045 | 5.3531 | 0.044126 | 0.29825 | 3.8618 | 3.4052 | 0.0019433
1073.4 | 911.4 | 103.7442 | 1.1162 | 103.2464 | 2.8407 |  |  | 3.112 | 0.0038588 | 6.1828 | 0.048827 | 5.3531 | 0.044126 | 0.20087 | 3.8732 | 3.2104 | 0.0035663
1073.6 | 911.6 | 103.6467 | 1.1275 | 103.149 | 2.8212 |  |  | 3.3068 | 0.0038588 | 6.0854 | 0.058567 | 5.3531 | 0.044126 | 0.59047 | 3.8716 | 3.113 | 0.0084366
1073.8 | 911.8 | 103.6467 | 1.1145 | 103.2464 | 2.8423 |  |  | 3.3068 | 0.010351 | 5.9881 | 0.05045 | 5.3531 | 0.042503 | 0.49305 | 3.8813 | 3.113 | 0.01006
1074 | 912 | 103.5494 | 1.1048 | 102.662 | 2.8147 |  |  | 2.8198 | 0.0087285 | 5.5985 | 0.042334 | 5.0609 | 0.042503 | 0.78523 | 3.8537 | 2.626 | 0.00032025
1074.2 | 912.2 | 103.5494 | 1.108 | 103.2464 | 2.8358 |  |  | 3.0146 | 0.0038588 | 6.2802 | 0.05045 | 4.9635 | 0.042503 | 0.49305 | 3.87 | 3.5025 | 0.0051899
1074.4 | 912.4 | 103.3546 | 1.108 | 103.2464 | 2.8569 |  |  | 3.112 | 0.0071055 | 6.2802 | 0.045581 | 5.3531 | 0.042503 | 0.68785 | 3.8911 | 3.0156 | 0.0035663
1074.6 | 912.6 | 103.5494 | 1.1194 | 103.0516 | 2.8375 |  |  | 3.3068 | -0.0026345 | 6.1828 | 0.045581 | 5.4505 | 0.045749 | 0.68785 | 3.8813 | 3.0156 | -0.0094198
1074.8 | 912.8 | 103.5494 | 1.1064 | 103.0516 | 2.8423 |  |  | 3.3068 | 0.0054818 | 6.2802 | 0.045581 | 5.9375 | 0.044126 | 0.49305 | 3.8683 | 2.5286 | -0.0013034
1075 | 913 | 102.965 | 1.0853 | 102.4672 | 2.8423 |  |  | 2.0406 | -0.0010109 | 5.5985 | 0.042334 | 5.0609 | 0.04088 | 0.39567 | 3.8781 | 2.8208 | 0.0051899
1075.2 | 913.2 | 103.3546 | 1.1145 | 103.149 | 2.8456 |  |  | 2.138 | 0.0038588 | 6.475 | 0.053697 | 4.5739 | 0.037633 | 0.59047 | 3.8813 | 2.0416 | 0.0084366
1075.4 | 913.4 | 103.3546 | 1.1113 | 103.149 | 2.8488 |  |  | 3.2094 | 0.00061214 | 6.0854 | 0.042334 | 5.5479 | 0.044126 | 0.39567 | 3.8878 | 3.4052 | 0.0035663
1075.6 | 913.6 | 103.452 | 1.1048 | 103.0516 | 2.8456 |  |  | 3.599 | 0.0038588 | 6.8646 | 0.045581 | 5.1583 | 0.042503 | 0.59047 | 3.8797 | 2.139 | 0.00032025
1075.8 | 913.8 | 103.1598 | 1.1162 | 102.7594 | 2.8342 |  |  | 2.9172 | 0.0054818 | 5.8906 | 0.05045 | 5.1583 | 0.044126 | 0.29825 | 3.8829 | 3.113 | 0.0051899
1076 | 914 | 101.8936 | 1.0902 | 101.9802 | 2.8261 |  |  | 2.0406 | -0.0091272 | 5.5985 | 0.045581 | 5.0609 | 0.04088 | 1.3696 | 3.8846 | 2.7234 | 0.023046
1076.2 | 914.2 | 102.965 | 1.1113 | 102.8568 | 2.8245 |  |  | 3.112 | 0.0087285 | 6.2802 | 0.047204 | 5.2557 | 0.044126 | 0.49305 | 3.8716 | 3.113 | 0.011683
1076.4 | 914.4 | 103.3546 | 1.1032 | 102.662 | 2.8375 |  |  | 2.625 | 0.0022351 | 6.0854 | 0.048827 | 4.9635 | 0.044126 | 0.59047 | 3.8748 | 2.626 | 0.0084366
1076.6 | 914.6 | 102.965 | 1.1048 | 103.0516 | 2.8391 |  |  | 3.112 | 0.0038588 | 5.9881 | 0.056944 | 4.8661 | 0.042503 | 0.49305 | 3.8732 | 2.5286 | 0.0051899
1076.8 | 914.8 | 103.452 | 1.1129 | 102.7594 | 2.8618 |  |  | 3.4042 | 0.0038588 | 6.3776 | 0.055321 | 6.0349 | 0.044126 | 1.0774 | 3.8813 | 3.3078 | 0.0084366
1077 | 915 | 103.0624 | 1.108 | 102.5646 | 2.8537 |  |  | 3.3068 | 0.0038588 | 6.2802 | 0.048827 | 5.3531 | 0.044126 | 0.98003 | 3.8927 | 3.2104 | -0.017536
1077.2 | 915.2 | 102.7702 | 1.0999 | 101.9802 | 2.8505 |  |  | 3.0146 | 0.0054818 | 6.0854 | 0.06993 | 4.7687 | 0.039257 | 0.29825 | 3.8911 | 2.626 | 0.0035663
1077.4 | 915.4 | 102.8676 | 1.1129 | 102.5646 | 2.8569 |  |  | 2.9172 | -0.0010109 | 6.1828 | 0.052074 | 5.2557 | 0.045749 | 0.20087 | 3.9073 | 2.5286 | 0.0019433
1077.6 | 915.6 | 102.6728 | 1.1097 | 102.3698 | 2.8569 |  |  | 2.8198 | 0.010351 | 5.6958 | 0.05045 | 5.2557 | 0.037633 | -0.48092 | 3.9041 | 3.4052 | 0.0051899
1077.8 | 915.8 | 102.6728 | 1.1113 | 102.4672 | 2.8667 |  |  | 3.0146 | 0.0071055 | 6.3776 | 0.05045 | 5.3531 | 0.04088 | 0.49305 | 3.9057 | 3.6 | 0.0084366
1078 | 916 | 102.478 | 1.1243 | 102.175 | 2.8521 |  |  | 2.8198 | 0.0054818 | 6.2802 | 0.052074 | 4.9635 | 0.04088 | 0.39567 | 3.9089 | 3.0156 | 0.0051899
1078.2 | 916.2 | 102.965 | 1.1194 | 102.8568 | 2.8781 |  |  | 3.3068 | 0.0054818 | 6.0854 | 0.047204 | 5.3531 | 0.045749 | 0.59047 | 3.9105 | 3.113 | 0.00032025
1078.4 | 916.4 | 102.965 | 1.1178 | 102.8568 | 2.8651 |  |  | 3.5016 | 0.0054818 | 5.8906 | 0.045581 | 5.1583 | 0.042503 | 0.59047 | 3.9041 | 3.113 | 0.0051899
1078.6 | 916.6 | 102.7702 | 1.1259 | 102.5646 | 2.8716 |  |  | 3.4042 | 0.0054818 | 6.1828 | 0.05045 | 5.2557 | 0.042503 | 0.68785 | 3.917 | 3.0156 | 0.014929
1078.8 | 916.8 | 102.965 | 1.1113 | 102.5646 | 2.8683 |  |  | 2.7224 | 0.0022351 | 5.7933 | 0.05045 | 5.2557 | 0.039257 | 0.49305 | 3.9041 | 3.113 | 0.00032025
1079 | 917 | 103.1598 | 1.1113 | 102.7594 | 2.8569 |  |  | 2.8198 | 0.0054818 | 5.8906 | 0.052074 | 5.0609 | 0.044126 | 0.39567 | 3.9105 | 2.2364 | 0.0084366
1079.2 | 917.2 | 102.478 | 1.0999 | 102.7594 | 2.8375 |  |  | 2.625 | 0.010351 | 5.9881 | 0.048827 | 5.1583 | 0.04088 | 0.49305 | 3.9154 | 3.6 | 0.0084366
1079.4 | 917.4 | 102.8676 | 1.108 | 102.7594 | 2.8797 |  |  | 2.7224 | 0.0071055 | 5.7933 | 0.052074 | 4.5739 | 0.042503 | 0.59047 | 3.8959 | 2.626 | 0.01006
1079.6 | 917.6 | 102.8676 | 1.121 | 102.175 | 2.8862 |  |  | 3.4042 | 0.0087285 | 6.475 | 0.048827 | 5.4505 | 0.042503 | 0.49305 | 3.9252 | 2.7234 | 0.0068129
1079.8 | 917.8 | 103.0624 | 1.1129 | 102.5646 | 2.8797 |  |  | 3.5016 | 0.0071055 | 6.475 | 0.043958 | 5.2557 | 0.042503 | 0.49305 | 3.917 | 2.7234 | 0.0084366
1080 | 918 | 102.7702 | 1.1243 | 102.5646 | 2.8781 |  |  | 3.0146 | 0.0038588 | 6.1828 | 0.05045 | 5.3531 | 0.044126 | 0.29825 | 3.9187 | 2.9182 | 0.0068129
1080.2 | 918.2 | 103.5494 | 1.1194 | 102.4672 | 2.8894 |  |  | 3.3068 | 0.0038588 | 6.3776 | 0.048827 | 5.3531 | 0.047373 | 0.88265 | 3.9252 | 3.6 | 0.01006
1080.4 | 918.4 | 102.5754 | 1.1097 | 102.3698 | 2.8878 |  |  | 3.0146 | 0.0054818 | 6.1828 | 0.047204 | 5.2557 | 0.044126 | 0.59047 | 3.9187 | 3.0156 | 0.0051899
1080.6 | 918.6 | 103.1598 | 1.1113 | 102.3698 | 2.8797 |  |  | 3.0146 | 0.0022351 | 5.8906 | 0.048827 | 5.4505 | 0.034386 | 0.10349 | 3.9105 | 2.9182 | 0.0051899
1080.8 | 918.8 | 103.0624 | 1.1178 | 102.662 | 2.8959 |  |  | 3.2094 | 0.0071055 | 6.3776 | 0.048827 | 5.6453 | 0.044126 | 0.39567 | 3.93 | 3.2104 | 0.0051899
1081 | 919 | 102.6728 | 1.1129 | 102.662 | 2.8699 |  |  | 3.5016 | 0.013598 | 5.3063 | 0.048827 | 5.3531 | 0.042503 | 0.68785 | 3.9154 | 2.5286 | 0.0084366
1081.2 | 919.2 | 103.0624 | 1.1162 | 102.662 | 2.8813 |  |  | 3.4042 | 0.0071055 | 6.475 | 0.052074 | 5.3531 | 0.045749 | 0.39567 | 3.9187 | 3.2104 | 0.0019433
1081.4 | 919.4 | 103.1598 | 1.1048 | 102.662 | 2.9008 |  |  | 3.4042 | 0.0054818 | 6.475 | 0.052074 | 5.3531 | 0.044126 | 0.29825 | 3.9268 | 3.113 | 0.0051899
1081.6 | 919.6 | 102.7702 | 1.1113 | 102.5646 | 2.8943 |  |  | 3.2094 | 0.011975 | 6.1828 | 0.05045 | 5.4505 | 0.045749 | 0.39567 | 3.9284 | 3.2104 | 0.0035663
1081.8 | 919.8 | 103.0624 | 1.1097 | 102.662 | 2.8845 |  |  | 3.2094 | 0.0022351 | 6.3776 | 0.047204 | 5.3531 | 0.042503 | 0.49305 | 3.9154 | 3.4052 | 0.0051899
1082 | 920 | 103.1598 | 1.1048 | 103.2464 | 2.8781 |  |  | 3.5016 | 0.0087285 | 6.2802 | 0.048827 | 5.3531 | 0.044126 | 0.49305 | 3.9316 | 3.113 | 0.0068129
1082.2 | 920.2 | 102.6728 | 1.1113 | 102.4672 | 2.8667 |  |  | 3.4042 | 0.0054818 | 6.2802 | 0.048827 | 4.7687 | 0.04088 | 0.59047 | 3.9154 | 2.626 | 0.0051899
1082.4 | 920.4 | 102.965 | 1.1227 | 102.5646 | 2.891 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.05045 | 5.3531 | 0.044126 | 0.49305 | 3.9316 | 3.113 | 0.0051899
1082.6 | 920.6 | 102.965 | 1.1097 | 102.5646 | 2.8943 |  |  | 3.4042 | 0.0054818 | 6.475 | 0.05045 | 5.5479 | 0.044126 | 0.49305 | 3.9268 | 3.2104 | 0.0051899
1082.8 | 920.8 | 102.7702 | 1.1275 | 102.0776 | 2.8781 |  |  | 2.8198 | 0.0038588 | 5.6958 | 0.043958 | 4.8661 | 0.050619 | 0.59047 | 3.917 | 2.139 | 0.0051899
1083 | 921 | 103.2572 | 1.1194 | 102.662 | 2.8829 |  |  | 3.4042 | 0.0054818 | 6.3776 | 0.05045 | 5.4505 | 0.044126 | 0.39567 | 3.9089 | 3.3078 | 0.0051899
1083.2 | 921.2 | 103.1598 | 1.1129 | 102.662 | 2.8845 |  |  | 3.4042 | 0.0038588 | 6.475 | 0.048827 | 5.3531 | 0.042503 | 0.39567 | 3.9154 | 3.113 | 0.0051899
1083.4 | 921.4 | 103.0624 | 1.121 | 103.0516 | 2.8894 |  |  | 3.5016 | 0.0038588 | 6.475 | 0.052074 | 5.4505 | 0.044126 | 0.49305 | 3.9235 | 3.3078 | 0.0051899
1083.6 | 921.6 | 102.965 | 1.1162 | 102.662 | 2.8975 |  |  | 3.4042 | 0.0054818 | 6.475 | 0.052074 | 5.4505 | 0.045749 | 0.49305 | 3.9284 | 3.2104 | 0.0035663
1083.8 | 921.8 | 102.965 | 1.1194 | 102.662 | 2.8845 |  |  | 3.4042 | 0.0054818 | 6.475 | 0.05045 | 5.4505 | 0.044126 | 0.39567 | 3.9219 | 3.2104 | 0.0051899
1084 | 922 | 103.1598 | 1.1178 | 102.5646 | 2.8943 |  |  | 3.5016 | 0.0054818 | 6.475 | 0.05045 | 5.5479 | 0.044126 | 0.39567 | 3.9252 | 3.3078 | 0.0051899
1084.2 | 922.2 | 103.0624 | 1.121 | 102.5646 | 2.8943 |  |  | 3.4042 | 0.0071055 | 6.475 | 0.052074 | 5.4505 | 0.044126 | 0.39567 | 3.9316 | 3.2104 | 0.0051899
1084.4 | 922.4 | 102.965 | 1.1275 | 102.5646 | 2.8943 |  |  | 3.5016 | 0.0038588 | 6.475 | 0.05045 | 5.5479 | 0.045749 | 0.39567 | 3.9365 | 3.3078 | 0.0051899
1084.6 | 922.6 | 102.965 | 1.121 | 102.4672 | 2.9089 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.05045 | 5.5479 | 0.045749 | 0.49305 | 3.9414 | 3.2104 | 0.00032025
1084.8 | 922.8 | 102.6728 | 1.1145 | 102.3698 | 2.8975 |  |  | 3.4042 | 0.0054818 | 6.475 | 0.052074 | 5.5479 | 0.044126 | 0.49305 | 3.93 | 3.3078 | 0.0051899
1085 | 923 | 102.965 | 1.121 | 102.4672 | 2.9138 |  |  | 3.5016 | 0.0038588 | 6.475 | 0.05045 | 5.5479 | 0.045749 | 0.49305 | 3.9495 | 3.2104 | 0.0035663
1085.2 | 923.2 | 102.6728 | 1.1243 | 102.2724 | 2.9365 |  |  | 3.5016 | 0.0038588 | 6.5724 | 0.053697 | 5.6453 | 0.045749 | 0.49305 | 3.9739 | 3.2104 | 0.0051899
1085.4 | 923.4 | 102.6728 | 1.1227 | 102.2724 | 2.9284 |  |  | 3.5016 | 0.0038588 | 6.5724 | 0.052074 | 5.5479 | 0.045749 | 0.39567 | 3.9641 | 3.3078 | 0.0035663
1085.6 | 923.6 | 102.7702 | 1.1275 | 102.4672 | 2.9203 |  |  | 3.5016 | 0.0054818 | 6.6698 | 0.05045 | 5.6453 | 0.044126 | 0.39567 | 3.9625 | 3.3078 | 0.0051899
1085.8 | 923.8 | 102.6728 | 1.134 | 102.2724 | 2.9219 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 3.969 | 3.3078 | 0.0051899
1086 | 924 | 102.6728 | 1.1243 | 102.2724 | 2.9235 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.052074 | 5.5479 | 0.045749 | 0.39567 | 3.9609 | 3.3078 | 0.0051899
1086.2 | 924.2 | 102.7702 | 1.121 | 102.3698 | 2.9251 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 3.9625 | 3.3078 | 0.0051899
1086.4 | 924.4 | 102.7702 | 1.1243 | 102.3698 | 2.9332 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 3.9739 | 3.3078 | 0.0051899
1086.6 | 924.6 | 102.5754 | 1.1194 | 102.175 | 2.9592 |  |  | 3.5016 | 0.0054818 | 6.6698 | 0.052074 | 5.5479 | 0.044126 | 0.39567 | 3.995 | 3.3078 | 0.0051899
1086.8 | 924.8 | 102.5754 | 1.121 | 102.175 | 2.9495 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 3.9885 | 3.3078 | 0.0035663
1087 | 925 | 102.6728 | 1.1243 | 102.2724 | 2.9365 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.044126 | 0.39567 | 3.9755 | 3.2104 | 0.0051899
1087.2 | 925.2 | 102.5754 | 1.1275 | 102.175 | 2.9365 |  |  | 3.5016 | 0.0054818 | 6.5724 | 0.052074 | 5.6453 | 0.044126 | 0.39567 | 3.9803 | 3.3078 | 0.0051899
1087.4 | 925.4 | 102.478 | 1.1243 | 102.0776 | 2.9527 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 3.9901 | 3.3078 | 0.0051899
1087.6 | 925.6 | 102.5754 | 1.1259 | 102.175 | 2.9479 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.053697 | 5.6453 | 0.045749 | 0.49305 | 3.9901 | 3.3078 | 0.0051899
1087.8 | 925.8 | 102.5754 | 1.1243 | 102.175 | 2.9462 |  |  | 3.5016 | 0.0038588 | 6.6698 | 0.052074 | 5.6453 | 0.044126 | 0.49305 | 3.9852 | 3.3078 | 0.0035663
1088 | 926 | 102.5754 | 1.1259 | 102.175 | 2.9479 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.052074 | 5.5479 | 0.045749 | 0.39567 | 3.9885 | 3.3078 | 0.0051899
1088.2 | 926.2 | 102.478 | 1.1259 | 102.175 | 2.9543 |  |  | 3.5016 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.044126 | 0.39567 | 3.9966 | 3.3078 | 0.0035663
1088.4 | 926.4 | 102.478 | 1.1308 | 101.9802 | 2.9543 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 3.9998 | 3.3078 | 0.0051899
1088.6 | 926.6 | 102.5754 | 1.1227 | 102.175 | 2.9576 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 3.9966 | 3.3078 | 0.0051899
1088.8 | 926.8 | 102.3806 | 1.1227 | 101.8828 | 2.9722 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 4.0096 | 3.3078 | 0.0051899
1089 | 927 | 102.2832 | 1.134 | 101.8828 | 2.9754 |  |  | 3.5016 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 4.0225 | 3.4052 | 0.0051899
1089.2 | 927.2 | 102.478 | 1.1259 | 101.9802 | 2.969 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.045749 | 0.39567 | 4.0096 | 3.4052 | 0.0051899
1089.4 | 927.4 | 102.478 | 1.121 | 101.9802 | 2.9706 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.6453 | 0.045749 | 0.49305 | 4.0063 | 3.3078 | 0.0051899
1089.6 | 927.6 | 102.3806 | 1.1243 | 101.9802 | 2.9641 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 4.0031 | 3.4052 | 0.0051899
1089.8 | 927.8 | 102.3806 | 1.1275 | 101.9802 | 2.9543 |  |  | 3.5016 | 0.0071055 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 3.995 | 3.3078 | 0.0051899
1090 | 928 | 102.1858 | 1.1275 | 101.7855 | 2.9787 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.055321 | 5.6453 | 0.047373 | 0.49305 | 4.0193 | 3.3078 | 0.0051899
1090.2 | 928.2 | 102.0884 | 1.134 | 101.7855 | 2.9803 |  |  | 3.599 | 0.0038588 | 6.7672 | 0.053697 | 5.7427 | 0.045749 | 0.39567 | 4.0274 | 3.4052 | 0.0035663
1090.4 | 928.4 | 102.2832 | 1.1308 | 101.8828 | 2.969 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0128 | 3.3078 | 0.0051899
1090.6 | 928.6 | 102.3806 | 1.1243 | 101.9802 | 2.9673 |  |  | 3.5016 | 0.0054818 | 6.6698 | 0.053697 | 5.6453 | 0.045749 | 0.49305 | 4.0063 | 3.3078 | 0.0051899
1090.8 | 928.8 | 102.3806 | 1.1291 | 101.9802 | 2.9625 |  |  | 3.599 | 0.0054818 | 6.5724 | 0.052074 | 5.7427 | 0.045749 | 0.39567 | 4.0047 | 3.4052 | 0.0051899
1091 | 929 | 102.478 | 1.134 | 102.0776 | 2.9527 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 3.9998 | 3.3078 | 0.0035663
1091.2 | 929.2 | 102.2832 | 1.1275 | 101.8828 | 2.9722 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.052074 | 5.7427 | 0.045749 | 0.39567 | 4.0144 | 3.3078 | 0.0035663
1091.4 | 929.4 | 102.3806 | 1.1243 | 101.8828 | 2.9673 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.7427 | 0.045749 | 0.39567 | 4.0031 | 3.3078 | 0.0051899
1091.6 | 929.6 | 102.2832 | 1.1308 | 101.8828 | 2.9657 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0112 | 3.4052 | 0.0035663
1091.8 | 929.8 | 102.2832 | 1.1291 | 101.8828 | 2.969 |  |  | 3.6964 | 0.0038588 | 6.7672 | 0.053697 | 5.6453 | 0.047373 | 0.39567 | 4.0112 | 3.4052 | 0.0051899
1092 | 930 | 102.2832 | 1.121 | 101.8828 | 2.9706 |  |  | 3.5016 | 0.0054818 | 6.7672 | 0.053697 | 5.5479 | 0.045749 | 0.39567 | 4.0031 | 3.3078 | 0.0051899
1092.2 | 930.2 | 102.2832 | 1.1243 | 101.8828 | 2.9706 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0079 | 3.3078 | 0.0051899
1092.4 | 930.4 | 102.2832 | 1.1275 | 101.8828 | 2.9754 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.7427 | 0.045749 | 0.39567 | 4.0128 | 3.3078 | 0.0051899
1092.6 | 930.6 | 102.2832 | 1.1227 | 101.7855 | 2.9754 |  |  | 3.5016 | 0.0038588 | 6.6698 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0112 | 3.3078 | 0.0051899
1092.8 | 930.8 | 102.2832 | 1.1291 | 101.7855 | 2.9657 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0063 | 3.3078 | 0.0035663
1093 | 931 | 102.3806 | 1.1227 | 101.8828 | 2.9673 |  |  | 3.5016 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 4.0014 | 3.4052 | 0.0051899
1093.2 | 931.2 | 102.3806 | 1.1227 | 101.8828 | 2.9592 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 3.995 | 3.4052 | 0.0035663
1093.4 | 931.4 | 102.2832 | 1.1308 | 101.8828 | 2.9625 |  |  | 3.599 | 0.0054818 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 4.0063 | 3.3078 | 0.0051899
1093.6 | 931.6 | 102.2832 | 1.1259 | 101.8828 | 2.9673 |  |  | 3.5016 | 0.0038588 | 6.6698 | 0.053697 | 5.7427 | 0.045749 | 0.39567 | 4.0031 | 3.3078 | 0.0035663
1093.8 | 931.8 | 102.2832 | 1.1291 | 101.8828 | 2.9641 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.045749 | 0.49305 | 4.0063 | 3.3078 | 0.0051899
1094 | 932 | 102.2832 | 1.1259 | 101.7855 | 2.9657 |  |  | 3.599 | 0.0038588 | 6.6698 | 0.052074 | 5.6453 | 0.045749 | 0.49305 | 4.0031 | 3.3078 | 0.0051899
1094.2 | 932.2 | 102.1858 | 1.1324 | 101.7855 | 2.969 |  |  | 3.599 | 0.0038588 | 6.7672 | 0.052074 | 5.7427 | 0.045749 | 0.39567 | 4.0128 | 3.4052 | 0.0051899
1094.4 | 932.4 | 102.0884 | 1.1308 | 101.688 | 2.9884 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.6453 | 0.045749 | 0.49305 | 4.0307 | 3.3078 | 0.0051899
1094.6 | 932.6 | 102.1858 | 1.1308 | 101.688 | 2.9754 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.6453 | 0.047373 | 0.39567 | 4.0161 | 3.4052 | 0.0051899
1094.8 | 932.8 | 102.0884 | 1.1275 | 101.688 | 2.9965 |  |  | 3.5016 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.045749 | 0.39567 | 4.0355 | 3.4052 | 0.0051899
1095 | 933 | 102.0884 | 1.1259 | 101.688 | 2.9933 |  |  | 3.5016 | 0.0038588 | 6.7672 | 0.053697 | 5.6453 | 0.047373 | 0.39567 | 4.0307 | 3.4052 | 0.0051899
1095.2 | 933.2 | 101.991 | 1.134 | 101.5907 | 2.9933 |  |  | 3.6964 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.047373 | 0.39567 | 4.0372 | 3.4052 | 0.0051899
1095.4 | 933.4 | 102.0884 | 1.1243 | 101.5907 | 2.9917 |  |  | 3.599 | 0.0038588 | 6.7672 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0274 | 3.4052 | 0.0051899
1095.6 | 933.6 | 102.0884 | 1.1259 | 101.5907 | 2.9917 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.6453 | 0.047373 | 0.49305 | 4.0274 | 3.3078 | 0.0068129
1095.8 | 933.8 | 101.991 | 1.1275 | 101.4932 | 2.9998 |  |  | 3.599 | 0.0071055 | 6.7672 | 0.052074 | 5.6453 | 0.045749 | 0.39567 | 4.0388 | 3.3078 | 0.0051899
1096 | 934 | 101.991 | 1.1194 | 101.4932 | 3.0063 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.047373 | 0.39567 | 4.0388 | 3.4052 | 0.0051899
1096.2 | 934.2 | 101.8936 | 1.1243 | 101.5907 | 3.0112 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.045749 | 0.49305 | 4.0453 | 3.4052 | 0.0051899
1096.4 | 934.4 | 101.8936 | 1.1259 | 101.4932 | 3.0112 |  |  | 3.6964 | 0.0038588 | 6.7672 | 0.053697 | 5.6453 | 0.045749 | 0.39567 | 4.0501 | 3.4052 | 0.0051899
1096.6 | 934.6 | 101.8936 | 1.1243 | 101.4932 | 3.0095 |  |  | 3.599 | 0.0038588 | 6.8646 | 0.053697 | 5.7427 | 0.047373 | 0.39567 | 4.0453 | 3.4052 | 0.0051899
1096.8 | 934.8 | 101.8936 | 1.1324 | 101.3959 | 3.0063 |  |  | 3.599 | 0.0054818 | 6.8646 | 0.053697 | 5.6453 | 0.047373 | 0.39567 | 4.0469 | 3.4052 | 0.0051899
1097 | 935 | 101.7962 | 1.1291 | 101.3959 | 3.0079 |  |  | 3.6964 | 0.0038588 | 6.8646 | 0.053697 | 5.7427 | 0.045749 | 0.49305 | 4.0469 | 3.4052 | 0.0051899
1097.2 | 935.2 | 101.8936 | 1.1291 | 101.3959 | 3.0128 |  |  | 3.599 | 0.0054818 | 6.8646 | 0.053697 | 5.7427 | 0.045749 | 0.39567 | 4.0518 | 3.4052 | 0.0051899
1097.4 | 935.4 | 101.6988 | 1.1308 | 101.2984 | 3.0209 |  |  | 3.6964 | 0.0054818 | 6.7672 | 0.053697 | 5.6453 | 0.047373 | 0.39567 | 4.0631 | 3.3078 | 0.0068129
1097.6 | 935.6 | 101.6988 | 1.1259 | 101.2984 | 3.0258 |  |  | 3.599 | 0.0054818 | 6.7672 | 0.055321 | 5.7427 | 0.047373 | 0.49305 | 4.0615 | 3.4052 | 0.0051899
1097.8 | 935.8 | 101.6988 | 1.1356 | 101.2011 | 3.0225 |  |  | 3.599 | 0.0054818 | 6.8646 | 0.053697 | 5.8401 | 0.047373 | 0.49305 | 4.068 | 3.4052 | 0.0051899
1098 | 936 | 101.6014 | 1.1291 | 101.2011 | 3.0274 |  |  | 3.6964 | 0.0054818 | 6.8646 | 0.053697 | 5.8401 | 0.045749 | 0.39567 | 4.068 | 3.4052 | 0.0051899
1098.2 | 936.2 | 101.6988 | 1.1227 | 101.2984 | 3.0388 |  |  | 3.6964 | 0.0054818 | 6.7672 | 0.053697 | 5.7427 | 0.047373 | 0.39567 | 4.0696 | 3.3078 | 0.0051899
1098.4 | 936.4 | 101.6014 | 1.1194 | 101.1037 | 3.0452 |  |  | 3.6964 | 0.0054818 | 6.8646 | 0.053697 | 5.7427 | 0.047373 | 0.49305 | 4.0761 | 3.4052 | 0.0035663
1098.6 | 936.6 | 101.6014 | 1.1291 | 101.2984 | 3.0323 |  |  | 3.6964 | 0.0054818 | 6.8646 | 0.055321 | 5.6453 | 0.047373 | 0.39567 | 4.0712 | 3.4052 | 0.0068129
1098.8 | 936.8 | 101.6014 | 1.1291 | 101.2011 | 3.0404 |  |  | 3.6964 | 0.0038588 | 6.8646 | 0.055321 | 5.7427 | 0.047373 | 0.39567 | 4.0794 | 3.4052 | 0.0051899
1099 | 937 | 101.504 | 1.1227 | 101.1037 | 3.0517 |  |  | 3.599 | 0.0054818 | 6.8646 | 0.055321 | 5.7427 | 0.047373 | 0.39567 | 4.0859 | 3.4052 | 0.0051899
1099.2 | 937.2 | 101.504 | 1.1259 | 101.1037 | 3.0517 |  |  | 3.6964 | 0.0038588 | 6.8646 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.0875 | 3.4052 | 0.0051899
1099.4 | 937.4 | 101.4066 | 1.134 | 101.0063 | 3.0517 |  |  | 3.6964 | 0.0054818 | 6.8646 | 0.055321 | 5.8401 | 0.045749 | 0.39567 | 4.0972 | 3.4052 | 0.0051899
1099.6 | 937.6 | 101.3093 | 1.134 | 101.0063 | 3.0631 |  |  | 3.6964 | 0.0038588 | 6.8646 | 0.055321 | 5.8401 | 0.047373 | 0.39567 | 4.1053 | 3.4052 | 0.0051899
1099.8 | 937.8 | 101.3093 | 1.1291 | 100.9089 | 3.0696 |  |  | 3.6964 | 0.0054818 | 6.8646 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1086 | 3.5025 | 0.0051899
1100 | 938 | 101.2118 | 1.1275 | 100.7141 | 3.0842 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1216 | 3.5025 | 0.0051899
1100.2 | 938.2 | 101.1145 | 1.1373 | 100.8115 | 3.0777 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1232 | 3.5025 | 0.0051899
1100.4 | 938.4 | 101.2118 | 1.1324 | 100.8115 | 3.0777 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1199 | 3.5025 | 0.0068129
1100.6 | 938.6 | 101.3093 | 1.1308 | 100.8115 | 3.0793 |  |  | 3.6964 | 0.0038588 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.49305 | 4.1183 | 3.5025 | 0.0051899
1100.8 | 938.8 | 101.2118 | 1.1275 | 100.7141 | 3.0891 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1248 | 3.5025 | 0.0051899
1101 | 939 | 101.1145 | 1.1308 | 100.7141 | 3.0907 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.8401 | 0.047373 | 0.49305 | 4.1297 | 3.4052 | 0.0068129
1101.2 | 939.2 | 101.1145 | 1.1291 | 100.7141 | 3.0956 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.49305 | 4.1362 | 3.5025 | 0.0051899
1101.4 | 939.4 | 101.1145 | 1.1259 | 100.7141 | 3.0956 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.8401 | 0.047373 | 0.39567 | 4.1313 | 3.5025 | 0.0051899
1101.6 | 939.6 | 101.2118 | 1.1259 | 100.7141 | 3.0939 |  |  | 3.6964 | 0.0038588 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1297 | 3.5025 | 0.0051899
1101.8 | 939.8 | 101.017 | 1.1308 | 100.6167 | 3.1053 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.49305 | 4.1443 | 3.5025 | 0.0051899
1102 | 940 | 101.1145 | 1.1356 | 100.7141 | 3.0842 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1297 | 3.4052 | 0.0051899
1102.2 | 940.2 | 101.1145 | 1.1291 | 100.7141 | 3.0907 |  |  | 3.7938 | 0.0038588 | 6.962 | 0.055321 | 5.8401 | 0.045749 | 0.49305 | 4.1297 | 3.5025 | 0.0051899
1102.4 | 940.4 | 101.017 | 1.1291 | 100.6167 | 3.0972 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1362 | 3.5025 | 0.0051899
1102.6 | 940.6 | 101.017 | 1.1308 | 100.6167 | 3.1004 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.141 | 3.5025 | 0.0051899
1102.8 | 940.8 | 101.017 | 1.1259 | 100.7141 | 3.0972 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.056944 | 5.9375 | 0.047373 | 0.39567 | 4.1329 | 3.5025 | 0.0051899
1103 | 941 | 101.017 | 1.1291 | 100.6167 | 3.1037 |  |  | 3.7938 | 0.0038588 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.141 | 3.5025 | 0.0051899
1103.2 | 941.2 | 101.017 | 1.1356 | 100.5193 | 3.0939 |  |  | 3.6964 | 0.0038588 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1394 | 3.5025 | 0.0051899
1103.4 | 941.4 | 101.1145 | 1.134 | 100.6167 | 3.0858 |  |  | 3.7938 | 0.0038588 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1313 | 3.5025 | 0.0051899
1103.6 | 941.6 | 101.017 | 1.1324 | 100.6167 | 3.0939 |  |  | 3.7938 | 0.0038588 | 6.962 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1362 | 3.4052 | 0.0051899
1103.8 | 941.8 | 101.017 | 1.1308 | 100.5193 | 3.0939 |  |  | 3.6964 | 0.0038588 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1346 | 3.5025 | 0.0051899
1104 | 942 | 100.8223 | 1.1291 | 100.4219 | 3.1118 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.056944 | 5.8401 | 0.047373 | 0.39567 | 4.1508 | 3.5025 | 0.0051899
1104.2 | 942.2 | 100.8223 | 1.1356 | 100.4219 | 3.1021 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.8401 | 0.047373 | 0.49305 | 4.1459 | 3.5025 | 0.0051899
1104.4 | 942.4 | 100.9197 | 1.1291 | 100.4219 | 3.1053 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.047373 | 0.39567 | 4.1427 | 3.5025 | 0.0051899
1104.6 | 942.6 | 100.9197 | 1.1308 | 100.4219 | 3.1069 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1459 | 3.5025 | 0.0051899
1104.8 | 942.8 | 100.8223 | 1.1291 | 100.4219 | 3.1183 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.056944 | 5.9375 | 0.047373 | 0.39567 | 4.1573 | 3.5025 | 0.0051899
1105 | 943 | 100.8223 | 1.1259 | 100.4219 | 3.1167 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1524 | 3.5025 | 0.0051899
1105.2 | 943.2 | 100.8223 | 1.1356 | 100.4219 | 3.1021 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1492 | 3.4052 | 0.0051899
1105.4 | 943.4 | 100.8223 | 1.1324 | 100.5193 | 3.0956 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.056944 | 5.8401 | 0.047373 | 0.49305 | 4.1378 | 3.4052 | 0.0051899
1105.6 | 943.6 | 100.8223 | 1.1356 | 100.3245 | 3.1037 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1492 | 3.5025 | 0.0051899
1105.8 | 943.8 | 100.9197 | 1.1308 | 100.4219 | 3.1069 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1475 | 3.5025 | 0.0051899
1106 | 944 | 100.6275 | 1.1421 | 100.2271 | 3.1118 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1638 | 3.5025 | 0.0051899
1106.2 | 944.2 | 100.7249 | 1.1324 | 100.3245 | 3.1118 |  |  | 3.7938 | 0.0038588 | 6.962 | 0.056944 | 5.8401 | 0.047373 | 0.39567 | 4.1557 | 3.5025 | 0.0051899
1106.4 | 944.4 | 100.7249 | 1.134 | 100.3245 | 3.1102 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.154 | 3.5025 | 0.0051899
1106.6 | 944.6 | 100.7249 | 1.1308 | 100.4219 | 3.1086 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1492 | 3.5025 | 0.0035663
1106.8 | 944.8 | 100.7249 | 1.1275 | 100.3245 | 3.1167 |  |  | 3.7938 | 0.0038588 | 6.962 | 0.055321 | 5.9375 | 0.048996 | 0.49305 | 4.1557 | 3.5025 | 0.0035663
1107 | 945 | 100.6275 | 1.1275 | 100.3245 | 3.1215 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 5.9375 | 0.048996 | 0.39567 | 4.1589 | 3.5025 | 0.0035663
1107.2 | 945.2 | 100.6275 | 1.1324 | 100.2271 | 3.1183 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1605 | 3.5025 | 0.0051899
1107.4 | 945.4 | 100.6275 | 1.1308 | 100.2271 | 3.1199 |  |  | 3.7938 | 0.0054818 | 7.1568 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1622 | 3.5025 | 0.0051899
1107.6 | 945.6 | 100.7249 | 1.134 | 100.2271 | 3.1118 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.047373 | 0.49305 | 4.1573 | 3.5025 | 0.0051899
1107.8 | 945.8 | 100.6275 | 1.1324 | 100.2271 | 3.1232 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.167 | 3.5025 | 0.0051899
1108 | 946 | 100.5301 | 1.1243 | 100.1297 | 3.128 |  |  | 3.7938 | 0.0038588 | 7.1568 | 0.055321 | 5.9375 | 0.048996 | 0.39567 | 4.1605 | 3.5025 | 0.0051899
1108.2 | 946.2 | 100.5301 | 1.1275 | 100.1297 | 3.1264 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 5.8401 | 0.047373 | 0.39567 | 4.1638 | 3.5025 | 0.0051899
1108.4 | 946.4 | 100.5301 | 1.1243 | 100.2271 | 3.128 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1654 | 3.5025 | 0.0051899
1108.6 | 946.6 | 100.5301 | 1.121 | 100.2271 | 3.1297 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1622 | 3.5025 | 0.0051899
1108.8 | 946.8 | 100.4327 | 1.1227 | 100.1297 | 3.1475 |  |  | 3.6964 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.047373 | 0.39567 | 4.18 | 3.5025 | 0.0051899
1109 | 947 | 100.4327 | 1.1308 | 100.1297 | 3.1329 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.49305 | 4.1735 | 3.5025 | 0.0051899
1109.2 | 947.2 | 100.6275 | 1.1243 | 100.2271 | 3.1248 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1589 | 3.5025 | 0.0051899
1109.4 | 947.4 | 100.5301 | 1.1194 | 100.2271 | 3.128 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1589 | 3.5025 | 0.0051899
1109.6 | 947.6 | 100.5301 | 1.1227 | 100.2271 | 3.1215 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.39567 | 4.1557 | 3.6 | 0.0035663
1109.8 | 947.8 | 100.5301 | 1.1291 | 100.1297 | 3.128 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.49305 | 4.167 | 3.6 | 0.0051899
1110 | 948 | 100.4327 | 1.121 | 99.9349 | 3.1426 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.39567 | 4.1735 | 3.6 | 0.0068129
1110.2 | 948.2 | 100.4327 | 1.1259 | 100.1297 | 3.1345 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.49305 | 4.1719 | 3.5025 | 0.0035663
1110.4 | 948.4 | 100.4327 | 1.1227 | 100.0323 | 3.1362 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 5.8401 | 0.047373 | 0.39567 | 4.1686 | 3.5025 | 0.0068129
1110.6 | 948.6 | 100.4327 | 1.1243 | 100.0323 | 3.141 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1768 | 3.5025 | 0.0051899
1110.8 | 948.8 | 100.4327 | 1.121 | 100.1297 | 3.1329 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.167 | 3.5025 | 0.0051899
1111 | 949 | 100.4327 | 1.1178 | 100.0323 | 3.1362 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.167 | 3.5025 | 0.0051899
1111.2 | 949.2 | 100.4327 | 1.121 | 100.0323 | 3.1378 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1686 | 3.6 | 0.0051899
1111.4 | 949.4 | 100.5301 | 1.121 | 100.1297 | 3.1248 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.8401 | 0.048996 | 0.39567 | 4.1573 | 3.5025 | 0.0051899
1111.6 | 949.6 | 100.4327 | 1.1324 | 100.1297 | 3.1199 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.8401 | 0.047373 | 0.39567 | 4.1622 | 3.5025 | 0.0051899
1111.8 | 949.8 | 100.4327 | 1.1227 | 100.0323 | 3.128 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1622 | 3.5025 | 0.0051899
1112 | 950 | 100.3353 | 1.121 | 99.9349 | 3.1297 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.49305 | 4.1622 | 3.5025 | 0.0051899
1112.2 | 950.2 | 100.4327 | 1.1227 | 100.1297 | 3.115 |  |  | 3.6964 | 0.0038588 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1492 | 3.5025 | 0.0051899
1112.4 | 950.4 | 100.4327 | 1.121 | 99.9349 | 3.128 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 6.0349 | 0.047373 | 0.49305 | 4.1589 | 3.5025 | 0.0051899
1112.6 | 950.6 | 100.4327 | 1.1178 | 100.0323 | 3.1313 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.49305 | 4.1605 | 3.5025 | 0.0051899
1112.8 | 950.8 | 100.4327 | 1.1162 | 100.0323 | 3.1232 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1508 | 3.5025 | 0.0051899
1113 | 951 | 100.5301 | 1.1227 | 100.2271 | 3.1118 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 5.8401 | 0.048996 | 0.39567 | 4.1459 | 3.4052 | 0.0051899
1113.2 | 951.2 | 100.5301 | 1.1243 | 100.1297 | 3.1134 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1475 | 3.5025 | 0.0051899
1113.4 | 951.4 | 100.4327 | 1.1227 | 100.0323 | 3.1215 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.048996 | 0.39567 | 4.1573 | 3.5025 | 0.0068129
1113.6 | 951.6 | 100.5301 | 1.1178 | 100.1297 | 3.1232 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.056944 | 5.9375 | 0.047373 | 0.49305 | 4.154 | 3.6 | 0.0035663
1113.8 | 951.8 | 100.4327 | 1.1227 | 100.0323 | 3.1215 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.1573 | 3.5025 | 0.0051899
1114 | 952 | 100.4327 | 1.1194 | 100.0323 | 3.1264 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.49305 | 4.1573 | 3.5025 | 0.0051899
1114.2 | 952.2 | 100.2379 | 1.1259 | 99.8375 | 3.141 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.18 | 3.6 | 0.0035663
1114.4 | 952.4 | 100.3353 | 1.1129 | 99.9349 | 3.1443 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.49305 | 4.1686 | 3.6 | 0.0051899
1114.6 | 952.6 | 100.3353 | 1.1145 | 100.0323 | 3.141 |  |  | 3.6964 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.047373 | 0.39567 | 4.167 | 3.5025 | 0.0051899
1114.8 | 952.8 | 100.3353 | 1.1145 | 99.9349 | 3.1426 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 5.9375 | 0.047373 | 0.39567 | 4.167 | 3.5025 | 0.0035663
1115 | 953 | 100.2379 | 1.1275 | 99.8375 | 3.1426 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.18 | 3.5025 | 0.0051899
1115.2 | 953.2 | 100.2379 | 1.1178 | 99.9349 | 3.1362 |  |  | 3.6964 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.047373 | 0.39567 | 4.167 | 3.6 | 0.0051899
1115.4 | 953.4 | 100.3353 | 1.1194 | 99.8375 | 3.1394 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1703 | 3.6 | 0.0051899
1115.6 | 953.6 | 100.3353 | 1.121 | 99.9349 | 3.141 |  |  | 3.6964 | 0.0038588 | 7.1568 | 0.055321 | 6.0349 | 0.048996 | 0.39567 | 4.1719 | 3.5025 | 0.0051899
1115.8 | 953.8 | 100.1405 | 1.1259 | 99.7401 | 3.1459 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.49305 | 4.1833 | 3.6 | 0.0051899
1116 | 954 | 100.2379 | 1.1243 | 99.7401 | 3.1508 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1849 | 3.5025 | 0.0051899
1116.2 | 954.2 | 100.2379 | 1.121 | 99.7401 | 3.1475 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1768 | 3.5025 | 0.0068129
1116.4 | 954.4 | 100.1405 | 1.1275 | 99.7401 | 3.1426 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1816 | 3.5025 | 0.0051899
1116.6 | 954.6 | 100.1405 | 1.1259 | 99.7401 | 3.141 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 6.0349 | 0.048996 | 0.39567 | 4.1784 | 3.6 | 0.0051899
1116.8 | 954.8 | 100.2379 | 1.121 | 99.7401 | 3.1443 |  |  | 3.6964 | 0.0054818 | 7.1568 | 0.056944 | 5.9375 | 0.048996 | 0.49305 | 4.1768 | 3.5025 | 0.0051899
1117 | 955 | 100.1405 | 1.1259 | 99.7401 | 3.1475 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 6.0349 | 0.047373 | 0.49305 | 4.1833 | 3.5025 | 0.0051899
1117.2 | 955.2 | 100.1405 | 1.121 | 99.7401 | 3.1508 |  |  | 3.7938 | 0.0054818 | 7.1568 | 0.056944 | 5.9375 | 0.048996 | 0.39567 | 4.1816 | 3.6 | 0.0035663
1117.4 | 955.4 | 100.1405 | 1.1194 | 99.6427 | 3.1637 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.49305 | 4.193 | 3.6 | 0.0051899
1117.6 | 955.6 | 100.0431 | 1.1194 | 99.6427 | 3.1686 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 6.0349 | 0.047373 | 0.49305 | 4.1962 | 3.5025 | 0.0051899
1117.8 | 955.8 | 99.9457 | 1.121 | 99.4479 | 3.1767 |  |  | 3.6964 | 0.0054818 | 7.1568 | 0.056944 | 6.0349 | 0.050619 | 0.39567 | 4.2076 | 3.5025 | 0.0051899
1118 | 956 | 99.8483 | 1.1227 | 99.4479 | 3.1719 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 5.9375 | 0.048996 | 0.49305 | 4.206 | 3.5025 | 0.0051899
1118.2 | 956.2 | 99.8483 | 1.121 | 99.4479 | 3.1848 |  |  | 3.7938 | 0.0038588 | 7.1568 | 0.056944 | 6.0349 | 0.050619 | 0.39567 | 4.2157 | 3.6 | 0.0051899
1118.4 | 956.4 | 99.8483 | 1.1243 | 99.3505 | 3.1848 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 5.9375 | 0.048996 | 0.39567 | 4.219 | 3.6 | 0.0051899
1118.6 | 956.6 | 99.8483 | 1.1243 | 99.5453 | 3.1767 |  |  | 3.7938 | 0.0038588 | 7.3516 | 0.056944 | 6.0349 | 0.048996 | 0.49305 | 4.2092 | 3.6 | 0.0051899
1118.8 | 956.8 | 99.8483 | 1.121 | 99.3505 | 3.1913 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.056944 | 6.0349 | 0.048996 | 0.39567 | 4.2222 | 3.6 | 0.0035663
1119 | 957 | 99.7509 | 1.1162 | 99.3505 | 3.1978 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.056944 | 6.0349 | 0.048996 | 0.49305 | 4.2238 | 3.6 | 0.0035663
1119.2 | 957.2 | 99.6535 | 1.1194 | 99.2531 | 3.2027 |  |  | 3.8911 | 0.0038588 | 7.1568 | 0.058567 | 6.0349 | 0.047373 | 0.39567 | 4.2287 | 3.6973 | 0.0051899
1119.4 | 957.4 | 99.7509 | 1.1194 | 99.3505 | 3.1962 |  |  | 3.7938 | 0.0038588 | 7.2542 | 0.056944 | 6.0349 | 0.048996 | 0.39567 | 4.2222 | 3.6 | 0.0051899
1119.6 | 957.6 | 99.6535 | 1.1243 | 99.2531 | 3.1962 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.056944 | 6.0349 | 0.048996 | 0.39567 | 4.2287 | 3.6 | 0.0051899
1119.8 | 957.8 | 99.5561 | 1.1243 | 99.1557 | 3.2076 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.056944 | 6.1323 | 0.048996 | 0.49305 | 4.2401 | 3.6 | 0.0051899
1120 | 958 | 99.5561 | 1.1259 | 99.1557 | 3.2043 |  |  | 3.7938 | 0.0038588 | 7.1568 | 0.058567 | 6.1323 | 0.048996 | 0.49305 | 4.2384 | 3.6 | 0.0035663
1120.2 | 958.2 | 99.6535 | 1.121 | 99.1557 | 3.1995 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.056944 | 6.0349 | 0.048996 | 0.29825 | 4.2303 | 3.6 | 0.0068129
1120.4 | 958.4 | 99.5561 | 1.1227 | 99.1557 | 3.2092 |  |  | 3.8911 | 0.0038588 | 7.2542 | 0.056944 | 5.9375 | 0.050619 | 0.49305 | 4.2417 | 3.6973 | 0.0051899
1120.6 | 958.6 | 99.5561 | 1.1275 | 99.1557 | 3.2076 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.056944 | 6.1323 | 0.048996 | 0.49305 | 4.2433 | 3.6 | 0.0035663
1120.8 | 958.8 | 99.5561 | 1.134 | 99.1557 | 3.1978 |  |  | 3.7938 | 0.0054818 | 7.1568 | 0.058567 | 6.1323 | 0.048996 | 0.39567 | 4.2368 | 3.6973 | 0.0051899
1121 | 959 | 99.4587 | 1.1243 | 99.0583 | 3.2141 |  |  | 3.7938 | 0.0054818 | 7.1568 | 0.056944 | 6.0349 | 0.050619 | 0.49305 | 4.2466 | 3.6 | 0.0051899
1121.2 | 959.2 | 99.5561 | 1.1243 | 99.1557 | 3.2011 |  |  | 3.7938 | 0.0054818 | 7.1568 | 0.058567 | 6.0349 | 0.048996 | 0.39567 | 4.2352 | 3.6 | 0.0051899
1121.4 | 959.4 | 99.5561 | 1.1275 | 99.1557 | 3.2076 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.0349 | 0.048996 | 0.39567 | 4.2433 | 3.6 | 0.0051899
1121.6 | 959.6 | 99.5561 | 1.134 | 99.1557 | 3.1881 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.056944 | 6.1323 | 0.048996 | 0.49305 | 4.2303 | 3.6 | 0.0051899
1121.8 | 959.8 | 99.6535 | 1.1291 | 99.1557 | 3.1962 |  |  | 3.8911 | 0.0038588 | 7.1568 | 0.058567 | 6.0349 | 0.048996 | 0.49305 | 4.2336 | 3.6 | 0.0051899
1122 | 960 | 99.5561 | 1.1308 | 99.1557 | 3.1897 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 5.9375 | 0.048996 | 0.39567 | 4.2271 | 3.6 | 0.0051899
1122.2 | 960.2 | 99.6535 | 1.1324 | 99.1557 | 3.1832 |  |  | 3.7938 | 0.0054818 | 7.1568 | 0.056944 | 6.0349 | 0.048996 | 0.49305 | 4.2238 | 3.6 | 0.0068129
1122.4 | 960.4 | 99.4587 | 1.1275 | 99.0583 | 3.2092 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.0349 | 0.048996 | 0.49305 | 4.2449 | 3.6 | 0.0051899
1122.6 | 960.6 | 99.4587 | 1.1291 | 99.1557 | 3.2141 |  |  | 3.8911 | 0.0038588 | 7.2542 | 0.058567 | 6.0349 | 0.050619 | 0.49305 | 4.2514 | 3.6 | 0.0051899
1122.8 | 960.8 | 99.6535 | 1.1275 | 99.2531 | 3.193 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.058567 | 6.0349 | 0.050619 | 0.49305 | 4.2287 | 3.6 | 0.0051899
1123 | 961 | 99.3613 | 1.1291 | 99.1557 | 3.206 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.0349 | 0.050619 | 0.49305 | 4.2449 | 3.6 | 0.0068129
1123.2 | 961.2 | 99.4587 | 1.1243 | 99.0583 | 3.2108 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 6.0349 | 0.050619 | 0.49305 | 4.2417 | 3.6 | 0.0068129
1123.4 | 961.4 | 99.3613 | 1.1243 | 98.9609 | 3.2222 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.0349 | 0.050619 | 0.49305 | 4.2547 | 3.6 | 0.0068129
1123.6 | 961.6 | 99.3613 | 1.1243 | 98.9609 | 3.2157 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2482 | 3.6973 | 0.0068129
1123.8 | 961.8 | 99.3613 | 1.1275 | 98.9609 | 3.2238 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.056944 | 6.1323 | 0.050619 | 0.39567 | 4.2595 | 3.6 | 0.0051899
1124 | 962 | 99.3613 | 1.1243 | 98.8635 | 3.2238 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.0349 | 0.050619 | 0.39567 | 4.2563 | 3.6 | 0.0051899
1124.2 | 962.2 | 99.3613 | 1.1194 | 98.9609 | 3.2335 |  |  | 3.8911 | 0.0071055 | 7.2542 | 0.058567 | 6.1323 | 0.048996 | 0.49305 | 4.2612 | 3.6973 | 0.0051899
1124.4 | 962.4 | 99.2639 | 1.1389 | 98.8635 | 3.2254 |  |  | 3.8911 | 0.0071055 | 7.3516 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2725 | 3.6973 | 0.0051899
1124.6 | 962.6 | 99.2639 | 1.1291 | 98.8635 | 3.2238 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.058567 | 6.2297 | 0.048996 | 0.49305 | 4.2612 | 3.6 | 0.0051899
1124.8 | 962.8 | 99.2639 | 1.134 | 98.7661 | 3.2287 |  |  | 3.8911 | 0.0071055 | 7.3516 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2644 | 3.6 | 0.0068129
1125 | 963 | 99.3613 | 1.1275 | 98.8635 | 3.2222 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.052243 | 0.49305 | 4.2547 | 3.6973 | 0.0068129
1125.2 | 963.2 | 99.4587 | 1.1243 | 99.0583 | 3.2141 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2449 | 3.6 | 0.0068129
1125.4 | 963.4 | 99.4587 | 1.121 | 98.9609 | 3.2303 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2514 | 3.6973 | 0.0051899
1125.6 | 963.6 | 99.4587 | 1.1243 | 98.8635 | 3.2303 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.06019 | 6.0349 | 0.050619 | 0.49305 | 4.2595 | 3.6 | 0.0068129
1125.8 | 963.8 | 99.5561 | 1.1259 | 98.9609 | 3.2238 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.048996 | 0.49305 | 4.2579 | 3.6 | 0.0051899
1126 | 964 | 99.4587 | 1.1308 | 98.7661 | 3.2271 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.06019 | 6.0349 | 0.050619 | 0.49305 | 4.2628 | 3.6 | 0.0068129
1126.2 | 964.2 | 99.7509 | 1.134 | 98.6688 | 3.2352 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.59047 | 4.279 | 3.6973 | 0.0051899
1126.4 | 964.4 | 100.0431 | 1.1308 | 98.474 | 3.2433 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.2297 | 0.050619 | 0.39567 | 4.2823 | 3.6973 | 0.0068129
1126.6 | 964.6 | 99.4587 | 1.1308 | 98.7661 | 3.2303 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2693 | 3.6 | 0.0051899
1126.8 | 964.8 | 99.2639 | 1.1275 | 98.7661 | 3.2368 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2709 | 3.6973 | 0.0051899
1127 | 965 | 99.2639 | 1.1324 | 98.7661 | 3.2271 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2693 | 3.6973 | 0.0051899
1127.2 | 965.2 | 98.9717 | 1.1291 | 98.5713 | 3.2579 |  |  | 3.7938 | 0.0054818 | 7.3516 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.2953 | 3.6973 | 0.0051899
1127.4 | 965.4 | 98.8743 | 1.1243 | 98.5713 | 3.2498 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.2823 | 3.6973 | 0.0051899
1127.6 | 965.6 | 99.0691 | 1.1291 | 98.5713 | 3.2384 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.052243 | 0.39567 | 4.2742 | 3.6 | 0.0068129
1127.8 | 965.8 | 98.9717 | 1.1243 | 98.6688 | 3.2433 |  |  | 3.8911 | 0.0071055 | 7.2542 | 0.058567 | 6.1323 | 0.052243 | 0.49305 | 4.2774 | 3.6973 | 0.0068129
1128 | 966 | 98.9717 | 1.1291 | 98.5713 | 3.2368 |  |  | 3.8911 | 0.0038588 | 7.2542 | 0.06019 | 6.1323 | 0.050619 | 0.49305 | 4.2725 | 3.6973 | 0.0068129
1128.2 | 966.2 | 99.1665 | 1.134 | 98.7661 | 3.2254 |  |  | 3.8911 | 0.0038588 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2677 | 3.7948 | 0.0051899
1128.4 | 966.4 | 99.0691 | 1.134 | 98.6688 | 3.2238 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2644 | 3.6973 | 0.0068129
1128.6 | 966.6 | 99.0691 | 1.1243 | 98.6688 | 3.2384 |  |  | 3.7938 | 0.0054818 | 7.2542 | 0.058567 | 6.1323 | 0.050619 | 0.49305 | 4.2709 | 3.6973 | 0.0068129
1128.8 | 966.8 | 99.0691 | 1.1275 | 98.6688 | 3.2417 |  |  | 3.8911 | 0.0038588 | 7.2542 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.2774 | 3.6973 | 0.0068129
1129 | 967 | 98.9717 | 1.1227 | 98.474 | 3.2498 |  |  | 3.8911 | 0.0038588 | 7.3516 | 0.06019 | 6.1323 | 0.052243 | 0.49305 | 4.279 | 3.6973 | 0.0068129
1129.2 | 967.2 | 98.8743 | 1.1243 | 98.5713 | 3.2482 |  |  | 3.8911 | 0.0038588 | 7.449 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.2807 | 3.6973 | 0.0068129
1129.4 | 967.4 | 98.7769 | 1.1291 | 98.3765 | 3.2547 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.2888 | 3.7948 | 0.0051899
1129.6 | 967.6 | 98.7769 | 1.1243 | 98.3765 | 3.2693 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.06019 | 6.2297 | 0.050619 | 0.49305 | 4.3018 | 3.6973 | 0.0051899
1129.8 | 967.8 | 98.6795 | 1.1259 | 98.3765 | 3.2693 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.06019 | 6.1323 | 0.052243 | 0.49305 | 4.3034 | 3.7948 | 0.0068129
1130 | 968 | 98.6795 | 1.1194 | 98.2792 | 3.2741 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.058567 | 6.2297 | 0.052243 | 0.49305 | 4.3018 | 3.6973 | 0.0068129
1130.2 | 968.2 | 98.6795 | 1.1243 | 98.2792 | 3.2644 |  |  | 3.8911 | 0.0071055 | 7.449 | 0.058567 | 6.3271 | 0.050619 | 0.59047 | 4.2969 | 3.6973 | 0.0051899
1130.4 | 968.4 | 98.5821 | 1.1259 | 98.0844 | 3.2725 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.058567 | 6.1323 | 0.052243 | 0.49305 | 4.3066 | 3.6973 | 0.0051899
1130.6 | 968.6 | 98.5821 | 1.1227 | 98.1817 | 3.2709 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.050619 | 0.49305 | 4.3018 | 3.7948 | 0.0051899
1130.8 | 968.8 | 98.6795 | 1.121 | 98.2792 | 3.2725 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.39567 | 4.3001 | 3.6973 | 0.0068129
1131 | 969 | 98.6795 | 1.1145 | 98.2792 | 3.279 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.058567 | 6.2297 | 0.052243 | 0.49305 | 4.3018 | 3.7948 | 0.0051899
1131.2 | 969.2 | 98.4847 | 1.1178 | 98.0844 | 3.2904 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.058567 | 6.3271 | 0.052243 | 0.39567 | 4.3147 | 3.6973 | 0.0051899
1131.4 | 969.4 | 98.4847 | 1.1178 | 98.0844 | 3.279 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.06019 | 6.1323 | 0.052243 | 0.49305 | 4.305 | 3.6973 | 0.0051899
1131.6 | 969.6 | 98.4847 | 1.1194 | 98.0844 | 3.2822 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.050619 | 0.49305 | 4.3082 | 3.7948 | 0.0051899
1131.8 | 969.8 | 98.4847 | 1.121 | 97.987 | 3.279 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.06019 | 6.2297 | 0.050619 | 0.49305 | 4.3082 | 3.6973 | 0.0051899
1132 | 970 | 98.4847 | 1.121 | 98.0844 | 3.2644 |  |  | 3.8911 | 0.0071055 | 7.3516 | 0.058567 | 6.2297 | 0.052243 | 0.39567 | 4.2936 | 3.6973 | 0.0051899
1132.2 | 970.2 | 98.4847 | 1.1259 | 98.0844 | 3.266 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.06019 | 6.2297 | 0.050619 | 0.59047 | 4.2985 | 3.7948 | 0.0051899
1132.4 | 970.4 | 98.3873 | 1.1243 | 97.987 | 3.2693 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.3001 | 3.7948 | 0.0068129
1132.6 | 970.6 | 98.3873 | 1.121 | 97.987 | 3.2774 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.3082 | 3.6973 | 0.0068129
1132.8 | 970.8 | 98.2899 | 1.1308 | 97.8896 | 3.279 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.318 | 3.7948 | 0.0051899
1133 | 971 | 98.1926 | 1.121 | 97.7922 | 3.3001 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.06019 | 6.3271 | 0.050619 | 0.49305 | 4.3326 | 3.6973 | 0.0068129
1133.2 | 971.2 | 98.0951 | 1.1243 | 97.6948 | 3.2952 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.061813 | 6.2297 | 0.050619 | 0.39567 | 4.3261 | 3.7948 | 0.0068129
1133.4 | 971.4 | 97.9978 | 1.1243 | 97.5 | 3.3115 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.344 | 3.7948 | 0.0051899
1133.6 | 971.6 | 98.1926 | 1.1227 | 97.6948 | 3.2904 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3229 | 3.7948 | 0.0051899
1133.8 | 971.8 | 98.0951 | 1.1259 | 97.6948 | 3.3001 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.058567 | 6.3271 | 0.055489 | 0.49305 | 4.3375 | 3.7948 | 0.0035663
1134 | 972 | 98.0951 | 1.1243 | 97.5974 | 3.3001 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.3342 | 3.7948 | 0.0068129
1134.2 | 972.2 | 97.9978 | 1.121 | 97.5974 | 3.3082 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.050619 | 0.59047 | 4.3407 | 3.7948 | 0.0035663
1134.4 | 972.4 | 97.9978 | 1.121 | 97.5974 | 3.305 |  |  | 3.9886 | 0.0071055 | 7.449 | 0.061813 | 6.3271 | 0.052243 | 0.39567 | 4.3375 | 3.7948 | 0.0084366
1134.6 | 972.6 | 97.9978 | 1.1243 | 97.5974 | 3.305 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.050619 | 0.49305 | 4.3391 | 3.7948 | 0.0068129
1134.8 | 972.8 | 97.9003 | 1.1259 | 97.5 | 3.2969 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3342 | 3.7948 | 0.0068129
1135 | 973 | 97.9978 | 1.1275 | 97.5974 | 3.2904 |  |  | 3.9886 | 0.0054818 | 7.5464 | 0.058567 | 6.3271 | 0.052243 | 0.49305 | 4.3293 | 3.7948 | 0.0051899
1135.2 | 973.2 | 97.9978 | 1.121 | 97.5974 | 3.2904 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.3229 | 3.7948 | 0.0051899
1135.4 | 973.4 | 97.9003 | 1.121 | 97.5 | 3.3098 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.061813 | 6.3271 | 0.052243 | 0.49305 | 4.3423 | 3.6973 | 0.0051899
1135.6 | 973.6 | 98.0951 | 1.1227 | 97.5974 | 3.2871 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3229 | 3.7948 | 0.0051899
1135.8 | 973.8 | 97.803 | 1.1194 | 97.4026 | 3.3163 |  |  | 3.9886 | 0.0071055 | 7.449 | 0.061813 | 6.2297 | 0.052243 | 0.49305 | 4.3472 | 3.7948 | 0.0051899
1136 | 974 | 97.9003 | 1.121 | 97.4026 | 3.2952 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3293 | 3.7948 | 0.0068129
1136.2 | 974.2 | 97.5108 | 1.1145 | 97.013 | 3.352 |  |  | 3.9886 | 0.0071055 | 7.5464 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.378 | 3.6973 | 0.0051899
1136.4 | 974.4 | 97.9003 | 1.1194 | 97.4026 | 3.3017 |  |  | 3.9886 | 0.0071055 | 7.449 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.3326 | 3.7948 | 0.0051899
1136.6 | 974.6 | 97.9978 | 1.121 | 97.5 | 3.292 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.058567 | 6.2297 | 0.050619 | 0.39567 | 4.3245 | 3.7948 | 0.0051899
1136.8 | 974.8 | 97.9978 | 1.1275 | 97.5 | 3.2871 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3293 | 3.7948 | 0.0068129
1137 | 975 | 97.7056 | 1.121 | 97.3052 | 3.3245 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.39567 | 4.3569 | 3.7948 | 0.0051899
1137.2 | 975.2 | 97.803 | 1.1162 | 97.4026 | 3.3131 |  |  | 3.9886 | 0.0038588 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3423 | 3.8921 | 0.0051899
1137.4 | 975.4 | 97.9003 | 1.121 | 97.4026 | 3.2969 |  |  | 3.8911 | 0.0054818 | 7.449 | 0.061813 | 6.2297 | 0.050619 | 0.49305 | 4.3293 | 3.7948 | 0.0068129
1137.6 | 975.6 | 97.9003 | 1.1162 | 97.5 | 3.3001 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.058567 | 6.3271 | 0.052243 | 0.49305 | 4.3261 | 3.7948 | 0.0051899
1137.8 | 975.8 | 97.7056 | 1.1178 | 97.2078 | 3.3261 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3537 | 3.8921 | 0.0051899
1138 | 976 | 97.7056 | 1.1243 | 97.2078 | 3.3147 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3521 | 3.8921 | 0.0051899
1138.2 | 976.2 | 97.9003 | 1.1178 | 97.5 | 3.3001 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.050619 | 0.39567 | 4.3293 | 3.7948 | 0.0051899
1138.4 | 976.4 | 97.9003 | 1.1259 | 97.5974 | 3.2904 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.050619 | 0.49305 | 4.3293 | 3.8921 | 0.0051899
1138.6 | 976.6 | 97.5108 | 1.1178 | 97.013 | 3.3472 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.378 | 3.9895 | 0.0051899
1138.8 | 976.8 | 97.7056 | 1.1275 | 97.3052 | 3.3066 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.2297 | 0.052243 | 0.49305 | 4.3472 | 3.7948 | 0.0051899
1139 | 977 | 97.803 | 1.121 | 97.4026 | 3.305 |  |  | 3.9886 | 0.0054818 | 7.5464 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3358 | 3.8921 | 0.0068129
1139.2 | 977.2 | 97.7056 | 1.1145 | 97.3052 | 3.3245 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.3521 | 3.8921 | 0.0051899
1139.4 | 977.4 | 97.7056 | 1.1162 | 97.3052 | 3.3293 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3602 | 3.7948 | 0.0068129
1139.6 | 977.6 | 97.5108 | 1.1162 | 97.1104 | 3.3488 |  |  | 4.1834 | 0.0054818 | 7.5464 | 0.06019 | 6.5219 | 0.052243 | 0.49305 | 4.3797 | 3.8921 | 0.0068129
1139.8 | 977.8 | 97.5108 | 1.1291 | 97.1104 | 3.3309 |  |  | 4.0859 | 0.0038588 | 7.6438 | 0.06019 | 6.3271 | 0.052243 | 0.49305 | 4.3748 | 3.8921 | 0.0068129
1140 | 978 | 97.4134 | 1.1259 | 97.013 | 3.3342 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.061813 | 6.3271 | 0.052243 | 0.39567 | 4.3748 | 3.8921 | 0.0068129
1140.2 | 978.2 | 97.5108 | 1.1275 | 97.013 | 3.3309 |  |  | 3.9886 | 0.0054818 | 7.5464 | 0.061813 | 6.4245 | 0.052243 | 0.49305 | 4.3732 | 3.7948 | 0.0068129
1140.4 | 978.4 | 97.5108 | 1.1227 | 97.013 | 3.3407 |  |  | 4.0859 | 0.0071055 | 7.5464 | 0.061813 | 6.4245 | 0.052243 | 0.39567 | 4.3813 | 3.8921 | 0.0068129
1140.6 | 978.6 | 97.4134 | 1.1243 | 96.9156 | 3.3504 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.4245 | 0.052243 | 0.49305 | 4.3894 | 3.8921 | 0.0068129
1140.8 | 978.8 | 97.316 | 1.1243 | 96.9156 | 3.3553 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.3959 | 3.8921 | 0.0051899
1141 | 979 | 97.2186 | 1.1405 | 96.8182 | 3.3537 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.4245 | 0.055489 | 0.49305 | 4.4105 | 3.8921 | 0.0068129
1141.2 | 979.2 | 97.4134 | 1.1308 | 97.013 | 3.3358 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.050619 | 0.49305 | 4.3829 | 3.8921 | 0.0068129
1141.4 | 979.4 | 97.4134 | 1.1356 | 97.013 | 3.3374 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.3894 | 3.8921 | 0.0051899
1141.6 | 979.6 | 97.4134 | 1.1259 | 97.013 | 3.3423 |  |  | 4.0859 | 0.0038588 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.3862 | 3.9895 | 0.0051899
1141.8 | 979.8 | 97.4134 | 1.134 | 96.9156 | 3.3407 |  |  | 3.9886 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.391 | 3.9895 | 0.0068129
1142 | 980 | 97.316 | 1.134 | 96.8182 | 3.3456 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.3975 | 3.8921 | 0.0068129
1142.2 | 980.2 | 97.316 | 1.1291 | 96.9156 | 3.3504 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.4245 | 0.052243 | 0.49305 | 4.3975 | 3.8921 | 0.0068129
1142.4 | 980.4 | 97.4134 | 1.134 | 96.9156 | 3.3439 |  |  | 4.0859 | 0.0071055 | 7.6438 | 0.061813 | 6.4245 | 0.052243 | 0.49305 | 4.3959 | 3.8921 | 0.0084366
1142.6 | 980.6 | 97.4134 | 1.1405 | 96.9156 | 3.3374 |  |  | 4.0859 | 0.0071055 | 7.6438 | 0.061813 | 6.4245 | 0.052243 | 0.49305 | 4.3959 | 3.8921 | 0.0068129
1142.8 | 980.8 | 97.316 | 1.1324 | 96.9156 | 3.3488 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.4245 | 0.053866 | 0.49305 | 4.4008 | 3.8921 | 0.0068129
1143 | 981 | 97.0238 | 1.1389 | 96.6234 | 3.365 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.4235 | 3.9895 | 0.0068129
1143.2 | 981.2 | 97.2186 | 1.1373 | 96.7208 | 3.3472 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.404 | 3.9895 | 0.0051899
1143.4 | 981.4 | 97.1212 | 1.1356 | 96.8182 | 3.3585 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.061813 | 6.4245 | 0.053866 | 0.49305 | 4.4154 | 3.9895 | 0.0084366
1143.6 | 981.6 | 97.1212 | 1.1421 | 96.7208 | 3.3488 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.6192 | 0.052243 | 0.49305 | 4.4121 | 3.9895 | 0.0051899
1143.8 | 981.8 | 97.2186 | 1.134 | 96.8182 | 3.3569 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.06019 | 6.6192 | 0.053866 | 0.49305 | 4.4121 | 3.9895 | 0.0068129
1144 | 982 | 97.2186 | 1.1308 | 96.8182 | 3.3537 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.59047 | 4.4073 | 3.9895 | 0.0051899
1144.2 | 982.2 | 96.9264 | 1.1291 | 96.6234 | 3.3878 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.6192 | 0.053866 | 0.49305 | 4.4381 | 3.8921 | 0.0068129
1144.4 | 982.4 | 97.2186 | 1.1356 | 96.7208 | 3.352 |  |  | 4.1834 | 0.0071055 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.59047 | 4.4073 | 3.9895 | 0.0068129
1144.6 | 982.6 | 97.1212 | 1.1405 | 96.6234 | 3.3569 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.063437 | 6.5219 | 0.052243 | 0.49305 | 4.4186 | 3.8921 | 0.0068129
1144.8 | 982.8 | 97.2186 | 1.1438 | 96.8182 | 3.3423 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.063437 | 6.5219 | 0.052243 | 0.59047 | 4.4089 | 3.9895 | 0.0051899
1145 | 983 | 97.1212 | 1.1454 | 96.7208 | 3.3537 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4186 | 3.9895 | 0.0068129
1145.2 | 983.2 | 96.9264 | 1.1356 | 96.526 | 3.3845 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.59047 | 4.4414 | 3.9895 | 0.0051899
1145.4 | 983.4 | 97.1212 | 1.1438 | 96.7208 | 3.3553 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4186 | 3.9895 | 0.0051899
1145.6 | 983.6 | 97.1212 | 1.1373 | 96.6234 | 3.3667 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.06019 | 6.5219 | 0.053866 | 0.49305 | 4.4235 | 4.0869 | 0.0068129
1145.8 | 983.8 | 97.0238 | 1.1373 | 96.6234 | 3.3667 |  |  | 4.0859 | 0.0071055 | 7.6438 | 0.063437 | 6.5219 | 0.053866 | 0.59047 | 4.4267 | 3.8921 | 0.0068129
1146 | 984 | 96.9264 | 1.1421 | 96.4286 | 3.3731 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.4365 | 3.9895 | 0.0068129
1146.2 | 984.2 | 96.9264 | 1.1486 | 96.4286 | 3.3748 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4446 | 3.9895 | 0.0068129
1146.4 | 984.4 | 96.829 | 1.147 | 96.3312 | 3.3845 |  |  | 4.1834 | 0.0071055 | 7.6438 | 0.061813 | 6.6192 | 0.053866 | 0.49305 | 4.4527 | 3.9895 | 0.0051899
1146.6 | 984.6 | 96.9264 | 1.1373 | 96.526 | 3.3764 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.59047 | 4.4365 | 3.9895 | 0.0068129
1146.8 | 984.8 | 97.0238 | 1.1503 | 96.526 | 3.3731 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.59047 | 4.4414 | 3.9895 | 0.0068129
1147 | 985 | 96.9264 | 1.1454 | 96.526 | 3.3634 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4316 | 3.8921 | 0.0068129
1147.2 | 985.2 | 96.829 | 1.1389 | 96.4286 | 3.3796 |  |  | 4.0859 | 0.0071055 | 7.6438 | 0.061813 | 6.4245 | 0.053866 | 0.49305 | 4.4397 | 3.9895 | 0.0068129
1147.4 | 985.4 | 96.7316 | 1.1421 | 96.3312 | 3.3894 |  |  | 4.0859 | 0.0071055 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.59047 | 4.4527 | 4.0869 | 0.0068129
1147.6 | 985.6 | 96.7316 | 1.147 | 96.4286 | 3.378 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4478 | 3.9895 | 0.0051899
1147.8 | 985.8 | 96.9264 | 1.147 | 96.526 | 3.3683 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4381 | 3.8921 | 0.0068129
1148 | 986 | 96.829 | 1.1405 | 96.4286 | 3.3764 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4397 | 3.9895 | 0.0068129
1148.2 | 986.2 | 96.9264 | 1.1389 | 96.526 | 3.3731 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.06019 | 6.5219 | 0.053866 | 0.59047 | 4.4349 | 3.9895 | 0.0068129
1148.4 | 986.4 | 96.7316 | 1.1405 | 96.3312 | 3.391 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4543 | 3.9895 | 0.0068129
1148.6 | 986.6 | 96.7316 | 1.1421 | 96.2338 | 3.3894 |  |  | 4.0859 | 0.0071055 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4543 | 3.9895 | 0.0068129
1148.8 | 986.8 | 96.7316 | 1.1389 | 96.3312 | 3.3878 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.06019 | 6.5219 | 0.053866 | 0.49305 | 4.4511 | 3.9895 | 0.0051899
1149 | 987 | 96.6342 | 1.1567 | 96.2338 | 3.3813 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4608 | 3.9895 | 0.0068129
1149.2 | 987.2 | 96.829 | 1.147 | 96.4286 | 3.3715 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.443 | 3.9895 | 0.0051899
1149.4 | 987.4 | 96.829 | 1.1454 | 96.4286 | 3.3699 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.06019 | 6.6192 | 0.053866 | 0.49305 | 4.4414 | 3.9895 | 0.0051899
1149.6 | 987.6 | 96.7316 | 1.1551 | 96.3312 | 3.3699 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.06019 | 6.5219 | 0.052243 | 0.49305 | 4.4478 | 3.9895 | 0.0051899
1149.8 | 987.8 | 96.829 | 1.1486 | 96.4286 | 3.3618 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.055489 | 0.49305 | 4.4349 | 3.9895 | 0.0051899
1150 | 988 | 96.7316 | 1.1405 | 96.4286 | 3.3634 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4284 | 3.8921 | 0.0051899
1150.2 | 988.2 | 96.7316 | 1.1405 | 96.3312 | 3.3845 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4495 | 3.9895 | 0.0051899
1150.4 | 988.4 | 96.829 | 1.1421 | 96.3312 | 3.3748 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.06019 | 6.6192 | 0.052243 | 0.49305 | 4.4397 | 3.9895 | 0.0051899
1150.6 | 988.6 | 96.6342 | 1.1389 | 96.3312 | 3.391 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.061813 | 6.6192 | 0.053866 | 0.49305 | 4.4527 | 3.9895 | 0.0051899
1150.8 | 988.8 | 96.829 | 1.1421 | 96.4286 | 3.3748 |  |  | 4.1834 | 0.0038588 | 7.6438 | 0.061813 | 6.6192 | 0.052243 | 0.49305 | 4.4397 | 3.8921 | 0.0051899
1151 | 989 | 96.829 | 1.1405 | 96.4286 | 3.3731 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.4381 | 3.8921 | 0.0051899
1151.2 | 989.2 | 96.829 | 1.1535 | 96.4286 | 3.365 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.06019 | 6.5219 | 0.052243 | 0.49305 | 4.443 | 3.8921 | 0.0051899
1151.4 | 989.4 | 96.6342 | 1.147 | 96.2338 | 3.3878 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.39567 | 4.4576 | 3.8921 | 0.0068129
1151.6 | 989.6 | 96.7316 | 1.1389 | 96.3312 | 3.3861 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.06019 | 6.5219 | 0.053866 | 0.49305 | 4.4462 | 3.9895 | 0.0051899
1151.8 | 989.8 | 96.829 | 1.1373 | 96.4286 | 3.3683 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.43 | 3.8921 | 0.0068129
1152 | 990 | 96.5368 | 1.1421 | 96.2338 | 3.3861 |  |  | 4.0859 | 0.0038588 | 7.6438 | 0.06019 | 6.6192 | 0.053866 | 0.49305 | 4.4527 | 3.9895 | 0.0051899
1152.2 | 990.2 | 96.6342 | 1.147 | 96.3312 | 3.3731 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.06019 | 6.5219 | 0.052243 | 0.49305 | 4.443 | 3.9895 | 0.0035663
1152.4 | 990.4 | 96.7316 | 1.1356 | 96.4286 | 3.3748 |  |  | 4.1834 | 0.0054818 | 7.5464 | 0.06019 | 6.5219 | 0.053866 | 0.49305 | 4.4397 | 3.8921 | 0.0051899
1152.6 | 990.6 | 96.7316 | 1.1356 | 96.3312 | 3.3813 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.06019 | 6.5219 | 0.053866 | 0.49305 | 4.4462 | 4.0869 | 0.0051899
1152.8 | 990.8 | 96.6342 | 1.1356 | 96.3312 | 3.3894 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.4478 | 3.9895 | 0.0051899
1153 | 991 | 96.2446 | 1.1632 | 96.0391 | 3.3813 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.39567 | 4.4738 | 3.9895 | 0.0051899
1153.2 | 991.2 | 96.1472 | 1.1438 | 95.9416 | 3.4137 |  |  | 4.1834 | 0.0054818 | 7.6438 | 0.061813 | 6.6192 | 0.053866 | 0.49305 | 4.4852 | 3.9895 | 0.0051899
1153.4 | 991.4 | 96.2446 | 1.134 | 96.1364 | 3.4137 |  |  | 4.1834 | 0.0071055 | 7.6438 | 0.063437 | 6.5219 | 0.053866 | 0.39567 | 4.4706 | 3.9895 | 0.0051899
1153.6 | 991.6 | 96.2446 | 1.1308 | 96.1364 | 3.4089 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4641 | 4.0869 | 0.0051899
1153.8 | 991.8 | 95.9524 | 1.134 | 96.0391 | 3.4202 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.6192 | 0.053866 | 0.49305 | 4.4754 | 3.9895 | 0.0051899
1154 | 992 | 95.4654 | 1.1373 | 96.2338 | 3.4056 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.061813 | 6.6192 | 0.053866 | 0.49305 | 4.4641 | 3.9895 | 0.0051899
1154.2 | 992.2 | 95.9524 | 1.134 | 96.2338 | 3.3975 |  |  | 4.1834 | 0.0038588 | 7.8386 | 0.06019 | 6.6192 | 0.052243 | 0.49305 | 4.4527 | 3.9895 | 0.0051899
1154.4 | 992.4 | 96.342 | 1.1373 | 96.2338 | 3.391 |  |  | 4.1834 | 0.0054818 | 7.7412 | 0.06019 | 6.6192 | 0.053866 | 0.49305 | 4.4478 | 3.9895 | 0.0051899
1154.6 | 992.6 | 96.5368 | 1.134 | 96.2338 | 3.3861 |  |  | 4.0859 | 0.0054818 | 7.7412 | 0.06019 | 6.6192 | 0.052243 | 0.49305 | 4.4414 | 3.9895 | 0.0051899
1154.8 | 992.8 | 96.342 | 1.1389 | 95.9416 | 3.4024 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.053866 | 0.49305 | 4.4625 | 3.9895 | 0.0051899
1155 | 993 | 96.5368 | 1.1373 | 96.1364 | 3.391 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.5219 | 0.053866 | 0.39567 | 4.4495 | 3.9895 | 0.0051899
1155.2 | 993.2 | 96.6342 | 1.1373 | 96.1364 | 3.3845 |  |  | 4.0859 | 0.0054818 | 7.6438 | 0.061813 | 6.5219 | 0.052243 | 0.49305 | 4.4414 | 3.9895 | 0.0051899
1155.4 | 993.4 | 96.5368 | 1.1356 | 96.1364 | 3.3813 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.5219 | 0.053866 | 0.49305 | 4.4381 | 3.8921 | 0.0051899
1155.6 | 993.6 | 96.7316 | 1.134 | 96.2338 | 3.365 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.4235 | 3.8921 | 0.0051899
1155.8 | 993.8 | 96.6342 | 1.1308 | 96.3312 | 3.3667 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.5219 | 0.052243 | 0.49305 | 4.4203 | 3.8921 | 0.0051899
1156 | 994 | 96.6342 | 1.1324 | 96.1364 | 3.378 |  |  | 4.0859 | 0.0038588 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.59047 | 4.4349 | 3.8921 | 0.0051899
1156.2 | 994.2 | 96.7316 | 1.1373 | 96.3312 | 3.3602 |  |  | 4.0859 | 0.0054818 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.39567 | 4.4186 | 3.8921 | 0.0051899
1156.4 | 994.4 | 96.6342 | 1.1373 | 96.2338 | 3.3715 |  |  | 4.0859 | 0.0038588 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.43 | 3.8921 | 0.0051899
1156.6 | 994.6 | 96.7316 | 1.1356 | 96.4286 | 3.3618 |  |  | 4.0859 | 0.0054818 | 7.449 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.4186 | 3.8921 | 0.0051899
1156.8 | 994.8 | 96.7316 | 1.1356 | 96.3312 | 3.3537 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.058567 | 6.5219 | 0.052243 | 0.39567 | 4.4121 | 3.8921 | 0.0035663
1157 | 995 | 96.7316 | 1.1373 | 96.3312 | 3.352 |  |  | 4.0859 | 0.0054818 | 7.449 | 0.06019 | 6.3271 | 0.052243 | 0.39567 | 4.4121 | 3.7948 | 0.0068129
1157.2 | 995.2 | 96.5368 | 1.1356 | 96.1364 | 3.3764 |  |  | 4.0859 | 0.0038588 | 7.5464 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.4365 | 3.8921 | 0.0051899
1157.4 | 995.4 | 96.7316 | 1.1405 | 96.2338 | 3.352 |  |  | 4.0859 | 0.0038588 | 7.449 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.417 | 3.8921 | 0.0051899
1157.6 | 995.6 | 96.7316 | 1.1389 | 96.3312 | 3.3456 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.4089 | 3.8921 | 0.0051899
1157.8 | 995.8 | 96.6342 | 1.1356 | 96.3312 | 3.3504 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.058567 | 6.4245 | 0.050619 | 0.49305 | 4.4105 | 3.7948 | 0.0051899
1158 | 996 | 96.4394 | 1.1405 | 96.1364 | 3.3748 |  |  | 4.0859 | 0.0038588 | 7.449 | 0.06019 | 6.4245 | 0.052243 | 0.49305 | 4.4381 | 3.7948 | 0.0051899
1158.2 | 996.2 | 96.5368 | 1.1389 | 96.1364 | 3.365 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.06019 | 6.4245 | 0.052243 | 0.39567 | 4.4267 | 3.7948 | 0.0051899
1158.4 | 996.4 | 96.6342 | 1.147 | 96.1364 | 3.3504 |  |  | 3.9886 | 0.0038588 | 7.3516 | 0.058567 | 6.3271 | 0.052243 | 0.49305 | 4.4203 | 3.8921 | 0.0051899
1158.6 | 996.6 | 96.5368 | 1.1454 | 96.1364 | 3.3569 |  |  | 3.9886 | 0.0054818 | 7.449 | 0.058567 | 6.4245 | 0.052243 | 0.49305 | 4.4251 | 3.8921 | 0.0051899
1158.8 | 996.8 | 96.6342 | 1.1373 | 96.2338 | 3.3504 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.058567 | 6.3271 | 0.052243 | 0.49305 | 4.4105 | 3.7948 | 0.0051899
1159 | 997 | 96.6342 | 1.134 | 96.2338 | 3.3488 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.056944 | 6.4245 | 0.052243 | 0.59047 | 4.4073 | 3.7948 | 0.0035663
1159.2 | 997.2 | 96.5368 | 1.1438 | 96.1364 | 3.3472 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.058567 | 6.4245 | 0.052243 | 0.49305 | 4.4138 | 3.7948 | 0.0051899
1159.4 | 997.4 | 96.5368 | 1.1373 | 96.2338 | 3.3602 |  |  | 3.9886 | 0.0038588 | 7.3516 | 0.058567 | 6.3271 | 0.052243 | 0.59047 | 4.4219 | 3.7948 | 0.0051899
1159.6 | 997.6 | 96.5368 | 1.1356 | 96.1364 | 3.3569 |  |  | 3.9886 | 0.0038588 | 7.3516 | 0.058567 | 6.3271 | 0.052243 | 0.49305 | 4.417 | 3.8921 | 0.0035663
1159.8 | 997.8 | 96.5368 | 1.1356 | 96.1364 | 3.3472 |  |  | 3.8911 | 0.0054818 | 7.3516 | 0.056944 | 6.3271 | 0.052243 | 0.39567 | 4.4056 | 3.6973 | 0.0051899
1160 | 998 | 96.5368 | 1.1324 | 96.0391 | 3.3569 |  |  | 3.9886 | 0.0054818 | 7.2542 | 0.058567 | 6.3271 | 0.050619 | 0.39567 | 4.4138 | 3.6973 | 0.0051899
1160.2 | 998.2 | 96.4394 | 1.1324 | 96.0391 | 3.3618 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.056944 | 6.3271 | 0.052243 | 0.39567 | 4.4203 | 3.7948 | 0.0051899
1160.4 | 998.4 | 96.5368 | 1.1438 | 96.1364 | 3.3504 |  |  | 3.9886 | 0.0054818 | 7.2542 | 0.056944 | 6.3271 | 0.052243 | 0.49305 | 4.4203 | 3.7948 | 0.0051899
1160.6 | 998.6 | 96.5368 | 1.1438 | 96.0391 | 3.3456 |  |  | 3.8911 | 0.0054818 | 7.2542 | 0.058567 | 6.3271 | 0.050619 | 0.49305 | 4.4138 | 3.7948 | 0.0051899
1160.8 | 998.8 | 96.5368 | 1.1405 | 96.1364 | 3.3439 |  |  | 3.9886 | 0.0038588 | 7.2542 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.4073 | 3.7948 | 0.0051899
1161 | 999 | 96.4394 | 1.1405 | 96.0391 | 3.352 |  |  | 3.9886 | 0.0071055 | 7.2542 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.417 | 3.7948 | 0.0051899
1161.2 | 999.2 | 96.342 | 1.134 | 95.9416 | 3.365 |  |  | 3.8911 | 0.0071055 | 7.2542 | 0.058567 | 6.2297 | 0.052243 | 0.39567 | 4.4219 | 3.7948 | 0.0051899
1161.4 | 999.4 | 96.5368 | 1.1373 | 96.1364 | 3.3488 |  |  | 3.9886 | 0.0054818 | 7.3516 | 0.056944 | 6.2297 | 0.052243 | 0.49305 | 4.4089 | 3.7948 | 0.0068129
1161.6 | 999.6 | 96.5368 | 1.1454 | 96.1364 | 3.3342 |  |  | 3.9886 | 0.0054818 | 7.2542 | 0.056944 | 6.2297 | 0.050619 | 0.49305 | 4.4024 | 3.7948 | 0.0051899
1161.8 | 999.8 | 96.5368 | 1.1486 | 96.1364 | 3.3277 |  |  | 3.9886 | 0.0038588 | 7.1568 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.4008 | 3.7948 | 0.0051899
1162 | 1000 | 96.4394 | 1.1454 | 96.0391 | 3.3342 |  |  | 3.9886 | 0.0054818 | 7.2542 | 0.056944 | 6.2297 | 0.050619 | 0.49305 | 4.404 | 3.7948 | 0.0051899
1162.2 | 1000.2 | 96.6342 | 1.1486 | 96.2338 | 3.3196 |  |  | 3.9886 | 0.0038588 | 7.2542 | 0.058567 | 6.2297 | 0.050619 | 0.49305 | 4.3927 | 3.6973 | 0.0068129
1162.4 | 1000.4 | 96.6342 | 1.147 | 96.1364 | 3.3261 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.056944 | 6.2297 | 0.050619 | 0.49305 | 4.3959 | 3.6973 | 0.0051899
1162.6 | 1000.6 | 96.6342 | 1.1405 | 96.1364 | 3.3277 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.056944 | 6.1323 | 0.052243 | 0.49305 | 4.391 | 3.6973 | 0.0068129
1162.8 | 1000.8 | 96.7316 | 1.1373 | 96.2338 | 3.3293 |  |  | 3.9886 | 0.0054818 | 7.1568 | 0.056944 | 6.2297 | 0.048996 | 0.49305 | 4.3927 | 3.6973 | 0.0051899
1163 | 1001 | 96.6342 | 1.1389 | 96.3312 | 3.3147 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.055321 | 6.2297 | 0.050619 | 0.49305 | 4.3764 | 3.6973 | 0.0051899
1163.2 | 1001.2 | 96.6342 | 1.1405 | 96.2338 | 3.3212 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.055321 | 6.2297 | 0.050619 | 0.39567 | 4.3862 | 3.6973 | 0.0051899
1163.4 | 1001.4 | 96.5368 | 1.1454 | 96.1364 | 3.3309 |  |  | 3.8911 | 0.0054818 | 7.1568 | 0.055321 | 6.2297 | 0.050619 | 0.49305 | 4.4024 | 3.6973 | 0.0051899
1163.6 | 1001.6 | 96.5368 | 1.1405 | 96.2338 | 3.3407 |  |  | 3.8911 | 0.0038588 | 7.1568 | 0.056944 | 6.2297 | 0.050619 | 0.49305 | 4.404 | 3.6973 | 0.0051899
1163.8 | 1001.8 | 96.6342 | 1.1405 | 96.2338 | 3.3326 |  |  | 3.8911 | 0.0038588 | 7.1568 | 0.056944 | 6.2297 | 0.050619 | 0.49305 | 4.3959 | 3.6 | 0.0051899
1164 | 1002 | 96.5368 | 1.1356 | 96.1364 | 3.3277 |  |  | 3.8911 | 0.0038588 | 7.1568 | 0.056944 | 6.2297 | 0.048996 | 0.59047 | 4.3878 | 3.6973 | 0.0051899
1164.2 | 1002.2 | 96.7316 | 1.1405 | 96.3312 | 3.3098 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.056944 | 6.1323 | 0.050619 | 0.49305 | 4.3764 | 3.6973 | 0.0051899
1164.4 | 1002.4 | 96.829 | 1.1389 | 96.3312 | 3.305 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.056944 | 6.1323 | 0.050619 | 0.49305 | 4.3699 | 3.6973 | 0.0051899
1164.6 | 1002.6 | 96.7316 | 1.134 | 96.3312 | 3.3147 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.2297 | 0.050619 | 0.39567 | 4.3748 | 3.6 | 0.0051899
1164.8 | 1002.8 | 96.7316 | 1.1454 | 96.3312 | 3.3163 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.1323 | 0.050619 | 0.39567 | 4.3862 | 3.6973 | 0.0051899
1165 | 1003 | 96.829 | 1.1373 | 96.526 | 3.3001 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3602 | 3.6 | 0.0068129
1165.2 | 1003.2 | 96.829 | 1.1389 | 96.526 | 3.2936 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 6.0349 | 0.050619 | 0.49305 | 4.3586 | 3.6 | 0.0051899
1165.4 | 1003.4 | 96.7316 | 1.147 | 96.3312 | 3.3033 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3748 | 3.6973 | 0.0035663
1165.6 | 1003.6 | 96.7316 | 1.1373 | 96.4286 | 3.3001 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3651 | 3.6 | 0.0051899
1165.8 | 1003.8 | 96.6342 | 1.1324 | 96.2338 | 3.3293 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.2297 | 0.048996 | 0.49305 | 4.3845 | 3.6973 | 0.0051899
1166 | 1004 | 96.5368 | 1.1356 | 96.1364 | 3.3326 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3927 | 3.6973 | 0.0051899
1166.2 | 1004.2 | 96.829 | 1.1373 | 96.4286 | 3.2985 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3618 | 3.6973 | 0.0051899
1166.4 | 1004.4 | 96.5368 | 1.1632 | 96.1364 | 3.3001 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3894 | 3.6 | 0.0051899
1166.6 | 1004.6 | 96.6342 | 1.1438 | 96.2338 | 3.2985 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.59047 | 4.3667 | 3.6973 | 0.0051899
1166.8 | 1004.8 | 96.6342 | 1.1389 | 96.2338 | 3.3001 |  |  | 3.8911 | 0.0054818 | 7.0594 | 0.055321 | 6.0349 | 0.048996 | 0.39567 | 4.3651 | 3.6973 | 0.0051899
1167 | 1005 | 96.5368 | 1.1356 | 96.2338 | 3.305 |  |  | 3.8911 | 0.0038588 | 7.1568 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.3651 | 3.6973 | 0.0035663
1167.2 | 1005.2 | 96.4394 | 1.1567 | 96.0391 | 3.3033 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 6.2297 | 0.048996 | 0.49305 | 4.3878 | 3.6973 | 0.0051899
1167.4 | 1005.4 | 96.6342 | 1.1405 | 96.2338 | 3.305 |  |  | 3.7938 | 0.0038588 | 7.0594 | 0.055321 | 6.1323 | 0.048996 | 0.49305 | 4.3699 | 3.6973 | 0.0051899
1167.6 | 1005.6 | 96.7316 | 1.1291 | 96.3312 | 3.2969 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 6.1323 | 0.048996 | 0.39567 | 4.3521 | 3.6 | 0.0051899
1167.8 | 1005.8 | 96.6342 | 1.1227 | 96.2338 | 3.3131 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.3618 | 3.5025 | 0.0051899
1168 | 1006 | 96.6342 | 1.1291 | 96.2338 | 3.3017 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.053697 | 6.1323 | 0.048996 | 0.49305 | 4.3537 | 3.6 | 0.0051899
1168.2 | 1006.2 | 96.6342 | 1.1324 | 96.3312 | 3.2969 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.053697 | 6.1323 | 0.047373 | 0.49305 | 4.3569 | 3.6 | 0.0051899
1168.4 | 1006.4 | 96.6342 | 1.1324 | 96.2338 | 3.2952 |  |  | 3.7938 | 0.0054818 | 7.0594 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.3553 | 3.6 | 0.0051899
1168.6 | 1006.6 | 96.829 | 1.1324 | 96.4286 | 3.2822 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.3407 | 3.6 | 0.0051899
1168.8 | 1006.8 | 96.829 | 1.1275 | 96.4286 | 3.2774 |  |  | 3.8911 | 0.0038588 | 6.962 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.331 | 3.6 | 0.0051899
1169 | 1007 | 96.829 | 1.1291 | 96.4286 | 3.2774 |  |  | 3.7938 | 0.0054818 | 6.8646 | 0.055321 | 6.0349 | 0.047373 | 0.49305 | 4.331 | 3.6 | 0.0035663
1169.2 | 1007.2 | 96.829 | 1.1275 | 96.3312 | 3.2855 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.3407 | 3.6 | 0.0035663
1169.4 | 1007.4 | 96.5368 | 1.1259 | 96.1364 | 3.3098 |  |  | 3.6964 | 0.0054818 | 6.962 | 0.055321 | 6.0349 | 0.050619 | 0.49305 | 4.3618 | 3.5025 | 0.0068129
1169.6 | 1007.6 | 96.6342 | 1.1259 | 96.2338 | 3.2969 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.055321 | 6.0349 | 0.048996 | 0.49305 | 4.3488 | 3.6 | 0.0068129
1169.8 | 1007.8 | 96.4394 | 1.1275 | 96.0391 | 3.3017 |  |  | 3.7938 | 0.0054818 | 6.962 | 0.053697 | 6.1323 | 0.047373 | 0.49305 | 4.3553 | 3.6 | 0.0051899
1170 | 1008 | 96.1472 | 1.1259 | 95.7468 | 3.3261 |  |  | 3.8911 | 0.0054818 | 6.8646 | 0.055321 | 6.1323 | 0.050619 | 0.49305 | 4.3764 | 3.6 | 0.0051899
1170.2 | 1008.2 | 96.1472 | 1.1243 | 95.6495 | 3.2839 |  |  | 3.7938 | 0.0054818 | 6.8646 | 0.055321 | 5.9375 | 0.050619 | 0.39567 | 4.3358 | 3.5025 | 0.0051899
1170.4 | 1008.4 | 12.1914 | 0.13083 | 11.4015 | 0.29217 |  |  | 1.651 | 0.0054818 | 2.1896 | 0.022855 | 2.0416 | 0.0214 | 0.49305 | 0.3718 | 1.2624 | 0.0051899
1170.6 | 1008.6 | 2.8414 | 0.033437 | 2.5384 | 0.048681 |  |  | 0.96924 | 0.0054818 | 1.1182 | 0.013115 | 1.1651 | 0.011661 | 0.39567 | 0.061758 | 0.67808 | 0.0051899
1170.8 | 1008.8 | 1.3804 | 0.022074 | 1.2722 | 0.024332 |  |  | 0.77444 | 0.0054818 | 0.82602 | 0.0098686 | 0.87284 | 0.010037 | 0.39567 | 0.027669 | 0.38586 | 0.0051899
1171 | 1009 | 0.99081 | 0.015581 | 0.98003 | 0.016216 |  |  | 0.67706 | 0.0054818 | 0.82602 | 0.0082456 | 0.77546 | 0.0067905 | 0.49305 | 0.021175 | 0.38586 | 0.0068129
1171.2 | 1009.2 | 0.89343 | 0.013958 | 0.88265 | 0.012969 |  |  | 0.67706 | 0.0054818 | 0.72864 | 0.0066219 | 0.77546 | 0.0084141 | 0.49305 | 0.017929 | 0.38586 | 0.0051899
1171.4 | 1009.4 | 0.69863 | 0.013958 | 0.68785 | 0.012969 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0066219 | 0.67808 | 0.0067905 | 0.49305 | 0.016306 | 0.28848 | 0.0051899
1171.6 | 1009.6 | 0.69863 | 0.012335 | 0.59043 | 0.011346 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0066219 | 0.58066 | 0.0051674 | 0.39567 | 0.014683 | 0.28848 | 0.0051899
1171.8 | 1009.8 | 0.69863 | 0.010711 | 0.59043 | 0.0097225 |  |  | 0.57968 | 0.0054818 | 0.63122 | 0.0066219 | 0.67808 | 0.0051674 | 0.39567 | 0.013059 | 0.28848 | 0.0051899
1172 | 1010 | 0.69863 | 0.010711 | 0.49305 | 0.0097225 |  |  | 0.57968 | 0.0054818 | 0.53384 | 0.0049989 | 0.58066 | 0.0051674 | 0.39567 | 0.013059 | 0.28848 | 0.0068129
1173 | 1011 | 0.60125 | 0.0090883 | 0.49305 | 0.0080995 |  |  | 0.48226 | 0.0038588 | 0.53384 | 0.0049989 | 0.58066 | 0.0051674 | 0.49305 | 0.011436 | 0.28848 | 0.0051899
1174 | 1012 | 0.60125 | 0.0090883 | 0.49305 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.58066 | 0.0035444 | 0.49305 | 0.009813 | 0.19109 | 0.0035663
1175 | 1013 | 0.50383 | 0.0090883 | 0.49305 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.58066 | 0.0035444 | 0.49305 | 0.0081893 | 0.19109 | 0.0051899
1176 | 1014 | 0.50383 | 0.0090883 | 0.49305 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.009813 | 0.19109 | 0.0051899
1177 | 1015 | 0.60125 | 0.0090883 | 0.39567 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.48328 | 0.0051674 | 0.39567 | 0.009813 | 0.093675 | 0.0051899
1178 | 1016 | 0.50383 | 0.0090883 | 0.39567 | 0.0064758 |  |  | 0.48226 | 0.0038588 | 0.63122 | 0.0049989 | 0.48328 | 0.0051674 | 0.39567 | 0.0081893 | 0.28848 | 0.0051899
1179 | 1017 | 0.50383 | 0.0090883 | 0.49305 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.63122 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.009813 | 0.19109 | 0.0051899
1180 | 1018 | 0.50383 | 0.0090883 | 0.39567 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.43642 | 0.0049989 | 0.48328 | 0.0051674 | 0.49305 | 0.0081893 | 0.19109 | 0.0051899
1210 | 1048 | 0.40645 | 0.0090883 | 0.39567 | 0.0064758 |  |  | 0.48226 | 0.0054818 | 0.43642 | 0.0049989 | 0.58066 | 0.0035444 | 0.49305 | 0.0081893 | 0.19109 | 0.0035663
1240 | 1078 | 0.50383 | 0.0074646 | 0.39567 | 0.0048528 |  |  | 0.48226 | 0.0054818 | 0.53384 | 0.0049989 | 0.48328 | 0.0035444 | 0.49305 | 0.0081893 | 0.19109 | 0.0051899

## Circuit 2 Faulting
Summary of Observed Faulting Behavior for Circuit #2
DAQ Time | Burner Time | Event | Discussion
162 | 0 | Burner on
xxx |  | Burner off | No damage observed during time burner was on.
970-1000 | 808-838 | Spray Started | Water spray initiated after burner was extinquished
1000-1026 | 838-864 | Current leakage from source conductors | Over a period of about 26-28s, there is evidence of degradation in the CPT voltage level which is indicative of power drain on the CPT. The power drain appears to be primarily to ground through the conductor on Path 7 (CPT is grounded) rather than to the other conductors.
1026 | 864 | Fuse Blow
Summary Observations |  | The circuit saw no degradation during the burn period. Water spray was started after the burner was shut off. This led to circuit failure and a fuse blow failure. It appears that mechanism of failure was the source conductor on Path 2 shorting to the grounded conductor on Path 7. Some increase in voltage on the target conductors (4,5,6) is seen, although not sufficient to cause relay chatter or actuation (maximum voltage is about 32V). No significant source voltage degradation prior to fuse blow.

## Converted Data C2
DAQ Time | Burner Time | C2 V1 | C2 A1 | C2 V2 | C2 A2 | C2 V3 | C2 A3 | C2 V4 | C2 A4 | C2 V5 | C2 A5 | C2 V6 | C2 A6 | C2 V7 | C2 A7 | C2 V8 | C2 A8
0 | -162 | 131.0617 | 0.075513 | 130.5026 | 0.0064315 |  |  | 0.27094 | 0.0019606 | 0.11726 | 0.0071332 | 0.213 | 0.0029322 | 0.2568 | 0.069621 | 2.018 | 0.0016967
30 | -132 | 131.3539 | 0.067397 | 130.7947 | 0.0048085 |  |  | 0.27094 | 0.00033696 | 0.11726 | 0.0055102 | 0.213 | 0.0029322 | 0.35418 | 0.069621 | 2.018 | 0.0016967
60 | -102 | 131.1591 | 0.072267 | 130.5026 | 0.0048085 |  |  | 0.27094 | 0.00033696 | 0.11726 | 0.0055102 | 0.31038 | 0.0029322 | 0.2568 | 0.069621 | 2.018 | 0.0016967
90 | -72 | 131.4513 | 0.067397 | 130.8922 | 0.0048085 |  |  | 0.27094 | 0.00033696 | 0.11726 | 0.0055102 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.1154 | 0.0016967
120 | -42 | 131.6461 | 0.06902 | 130.8922 | 0.0048085 |  |  | 0.27094 | 0.00033696 | 0.11726 | 0.0055102 | 0.213 | 0.0078019 | 0.2568 | 0.069621 | 2.018 | 0.0033197
150 | -12 | 131.4513 | 0.070644 | 130.7947 | 0.0048085 |  |  | 0.27094 | 0.00033696 | 0.21468 | 0.0071332 | 0.31038 | 0.0045552 | 0.4516 | 0.071244 | 2.1154 | 0.0033197
180 | 18 | 131.6461 | 0.06902 | 130.9896 | 0.0048085 |  |  | 0.27094 | 0.00033696 | 0.21468 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.1154 | 0.0016967
210 | 48 | 131.3539 | 0.077136 | 130.7947 | 0.0080546 |  |  | 0.27094 | 0.00033696 | 0.11726 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.069621 | 2.1154 | 0.0033197
240 | 78 | 131.6461 | 0.075513 | 131.087 | 0.0064315 |  |  | 0.36836 | 0.0019606 | 0.11726 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.2128 | 0.0033197
270 | 108 | 132.0357 | 0.06902 | 131.4765 | 0.0048085 |  |  | 0.36836 | 0.00033696 | 0.21468 | 0.0071332 | 0.31038 | 0.0029322 | 0.35418 | 0.071244 | 2.2128 | 0.0016967
300 | 138 | 131.6461 | 0.072267 | 131.087 | 0.0048085 |  |  | 0.36836 | 0.00033696 | 0.21468 | 0.0071332 | 0.213 | 0.0045552 | 0.35418 | 0.071244 | 2.6024 | 0.0016967
330 | 168 | 132.2304 | 0.080383 | 131.574 | 0.011301 |  |  | 0.36836 | 0.00033696 | 0.21468 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 3.0894 | 0.0033197
360 | 198 | 131.9382 | 0.070644 | 131.2817 | 0.0048085 |  |  | 0.36836 | 0.00033696 | 0.21468 | 0.0087568 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 3.1868 | 0.0033197
390 | 228 | 131.7434 | 0.07389 | 131.2817 | 0.0048085 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.7972 | 0.0033197
420 | 258 | 131.7434 | 0.070644 | 131.2817 | 0.0064315 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.6998 | 0.0033197
450 | 288 | 132.4252 | 0.06902 | 131.8661 | 0.0048085 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.0071332 | 0.4078 | 0.0045552 | 0.35418 | 0.071244 | 2.3102 | 0.0033197
480 | 318 | 132.133 | 0.077136 | 131.574 | 0.0064315 |  |  | 0.27094 | 0.00033696 | 0.21468 | 0.0087568 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.4076 | 0.0033197
510 | 348 | 132.133 | 0.070644 | 131.6713 | 0.0048085 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.0071332 | 0.31038 | 0.0061789 | 0.35418 | 0.071244 | 2.3102 | 0.0049433
540 | 378 | 132.133 | 0.06902 | 131.6713 | 0.0064315 |  |  | 0.36836 | 0.0019606 | 0.31206 | 0.0071332 | 0.31038 | 0.0045552 | 0.35418 | 0.072868 | 2.2128 | 0.0033197
570 | 408 | 131.9382 | 0.07389 | 131.3792 | 0.0064315 |  |  | 0.36836 | 0.0019606 | 0.31206 | 0.0087568 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 2.1154 | 0.0049433
600 | 438 | 131.9382 | 0.077136 | 131.4765 | 0.0064315 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.0087568 | 0.4078 | 0.0045552 | 0.4516 | 0.071244 | 2.1154 | 0.0033197
630 | 468 | 132.0357 | 0.082007 | 131.4765 | 0.011301 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.0071332 | 0.31038 | 0.0061789 | 0.35418 | 0.071244 | 1.9206 | 0.0049433
660 | 498 | 131.9382 | 0.07876 | 131.4765 | 0.0096782 |  |  | 0.36836 | 0.0019606 | 0.11726 | 0.0087568 | 0.31038 | 0.0045552 | 0.35418 | 0.071244 | 1.6285 | 0.0033197
690 | 528 | 132.133 | 0.070644 | 131.574 | 0.0064315 |  |  | 0.46574 | 0.0019606 | 0.31206 | 0.0087568 | 0.4078 | 0.0045552 | 0.4516 | 0.072868 | 1.4337 | 0.0049433
720 | 558 | 132.2304 | 0.082007 | 131.6713 | 0.012925 |  |  | 0.36836 | 0.0019606 | 0.31206 | 0.0087568 | 0.4078 | 0.0078019 | 0.4516 | 0.072868 | 1.044 | 0.0049433
750 | 588 | 132.0357 | 0.080383 | 131.3792 | 0.011301 |  |  | 0.36836 | 0.0019606 | 0.31206 | 0.0087568 | 0.31038 | 0.0045552 | 0.4516 | 0.072868 | 0.94667 | 0.0049433
780 | 618 | 131.9382 | 0.075513 | 131.3792 | 0.0064315 |  |  | 0.46574 | 0.0019606 | 0.31206 | 0.01038 | 0.31038 | 0.0061789 | 0.4516 | 0.072868 | 0.84925 | 0.0049433
810 | 648 | 131.9382 | 0.07389 | 131.4765 | 0.0064315 |  |  | 0.36836 | 0.0019606 | 0.21468 | 0.01038 | 0.31038 | 0.0045552 | 0.35418 | 0.072868 | 0.75187 | 0.0049433
840 | 678 | 132.2304 | 0.080383 | 131.6713 | 0.0096782 |  |  | 0.36836 | 0.0019606 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.35418 | 0.072868 | 0.84925 | 0.0049433
870 | 708 | 132.3278 | 0.08363 | 131.8661 | 0.012925 |  |  | 0.36836 | 0.0035836 | 0.31206 | 0.0071332 | 0.4078 | 0.0061789 | 0.4516 | 0.072868 | 1.044 | 0.0049433
900 | 738 | 132.2304 | 0.082007 | 131.6713 | 0.012925 |  |  | 0.46574 | 0.0019606 | 0.31206 | 0.0087568 | 0.4078 | 0.0045552 | 0.4516 | 0.072868 | 1.2389 | 0.0049433
930 | 768 | 132.4252 | 0.070644 | 131.9635 | 0.0064315 |  |  | 0.36836 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.35418 | 0.074491 | 1.4337 | 0.0049433
960 | 798 | 132.4252 | 0.08363 | 131.8661 | 0.012925 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 1.6285 | 0.0049433
990 | 828 | 132.0357 | 0.077136 | 131.4765 | 0.0080546 |  |  | 0.46574 | 0.0019606 | 0.31206 | 0.01038 | 0.31038 | 0.0061789 | 0.35418 | 0.074491 | 2.4076 | 0.0049433
991 | 829 | 131.9382 | 0.077136 | 131.4765 | 0.0080546 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.072868 | 2.4076 | 0.0049433
992 | 830 | 131.9382 | 0.077136 | 131.4765 | 0.0064315 |  |  | 0.36836 | 0.0052073 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 2.4076 | 0.0049433
993 | 831 | 132.0357 | 0.075513 | 131.574 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 2.505 | 0.0049433
994 | 832 | 131.9382 | 0.075513 | 131.4765 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.35418 | 0.074491 | 2.505 | 0.0065663
995 | 833 | 132.0357 | 0.07389 | 131.4765 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.40948 | 0.0087568 | 0.4078 | 0.0078019 | 0.4516 | 0.074491 | 2.6024 | 0.0065663
996 | 834 | 132.0357 | 0.070644 | 131.4765 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.40948 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 2.6024 | 0.0065663
997 | 835 | 132.0357 | 0.072267 | 131.4765 | 0.016171 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 2.6998 | 0.0049433
997.2 | 835.2 | 131.9382 | 0.072267 | 131.3792 | 0.021041 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 2.6998 | 0.0049433
997.4 | 835.4 | 131.9382 | 0.072267 | 131.3792 | 0.025911 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 2.6024 | 0.0049433
997.6 | 835.6 | 131.8409 | 0.072267 | 131.3792 | 0.032404 |  |  | 0.46574 | 0.0035836 | 0.50686 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.076114 | 3.1868 | 0.0049433
997.8 | 835.8 | 131.9382 | 0.07389 | 131.3792 | 0.037274 |  |  | 0.46574 | 0.0035836 | 2.3574 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.074491 | 3.6738 | 0.0049433
998 | 836 | 131.8409 | 0.072267 | 131.2817 | 0.04539 |  |  | 0.46574 | 0.0035836 | 3.7209 | 0.01038 | 0.31038 | 0.0061789 | 0.4516 | 0.076114 | 4.3555 | 0.0049433
998.2 | 836.2 | 131.7434 | 0.072267 | 131.2817 | 0.05513 |  |  | 0.36836 | 0.0035836 | 4.5975 | 0.01038 | 0.4078 | 0.0061789 | 0.54898 | 0.076114 | 4.3555 | 0.0049433
998.4 | 836.4 | 131.7434 | 0.072267 | 131.2817 | 0.063246 |  |  | 0.46574 | 0.0035836 | 5.3767 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.076114 | 4.4529 | 0.0049433
998.6 | 836.6 | 131.6461 | 0.07389 | 131.1844 | 0.072986 |  |  | 0.85535 | 0.0035836 | 6.2533 | 0.01038 | 0.4078 | 0.0061789 | 0.4516 | 0.077738 | 4.3555 | 0.0049433
998.8 | 836.8 | 131.5487 | 0.072267 | 131.087 | 0.084349 |  |  | 3.8746 | 0.0035836 | 7.422 | 0.012003 | 0.4078 | 0.0061789 | 0.4516 | 0.076114 | 4.6477 | 0.0049433
999 | 837 | 131.5487 | 0.072267 | 130.9896 | 0.098958 |  |  | 5.6278 | 0.0035836 | 8.9803 | 0.055831 | 0.4078 | 0.0061789 | 0.35418 | 0.077738 | 5.0373 | 0.0049433
999.2 | 837.2 | 131.3539 | 0.070644 | 130.8922 | 0.11032 |  |  | 6.7965 | 0.0035836 | 10.2465 | 0.085051 | 0.4078 | 0.0061789 | 0.4516 | 0.077738 | 5.1347 | 0.0049433
999.4 | 837.4 | 131.3539 | 0.070644 | 130.7947 | 0.12168 |  |  | 7.9653 | 0.0052073 | 11.4153 | 0.096414 | 0.4078 | 0.0061789 | 0.4516 | 0.079361 | 5.4269 | 0.0049433
999.6 | 837.6 | 131.2565 | 0.070644 | 130.6974 | 0.13467 |  |  | 9.3288 | 0.0035836 | 12.7788 | 0.10615 | 0.4078 | 0.0061789 | 0.35418 | 0.079361 | 5.9139 | 0.0049433
999.8 | 837.8 | 131.0617 | 0.070644 | 130.5026 | 0.15577 |  |  | 11.4716 | 0.0035836 | 14.9215 | 0.12239 | 0.4078 | 0.0061789 | 0.4516 | 0.079361 | 7.18 | 0.0065663
1000 | 838 | 130.9643 | 0.070644 | 130.4052 | 0.17201 |  |  | 13.4195 | 0.0035836 | 16.4799 | 0.13375 | 0.4078 | 0.0061789 | 0.4516 | 0.080984 | 9.128 | 0.0049433
1000.2 | 838.2 | 130.7695 | 0.070644 | 130.3078 | 0.19148 |  |  | 15.3674 | 0.0035836 | 18.4278 | 0.14998 | 0.4078 | 0.0061789 | 0.4516 | 0.082607 | 10.6863 | 0.0049433
1000.4 | 838.4 | 130.6721 | 0.06902 | 130.113 | 0.21096 |  |  | 17.3153 | 0.0035836 | 20.181 | 0.16297 | 0.4078 | 0.0061789 | 0.4516 | 0.085854 | 13.0238 | 0.0049433
1000.6 | 838.6 | 130.5747 | 0.06902 | 130.113 | 0.2272 |  |  | 18.9711 | 0.0035836 | 21.5445 | 0.17433 | 0.31038 | 0.0061789 | 0.4516 | 0.087477 | 14.777 | 0.0049433
1000.8 | 838.8 | 130.4773 | 0.06902 | 129.9182 | 0.2483 |  |  | 20.6268 | 0.0035836 | 23.2976 | 0.18569 | 0.4078 | 0.0078019 | 0.4516 | 0.089101 | 15.751 | 0.0049433
1001 | 839 | 130.2825 | 0.06902 | 129.7234 | 0.27265 |  |  | 22.5747 | 0.0035836 | 25.1482 | 0.20193 | 0.4078 | 0.0061789 | 0.4516 | 0.09397 | 18.478 | 0.0049433
1001.2 | 839.2 | 130.0877 | 0.06902 | 129.5286 | 0.29862 |  |  | 24.4253 | 0.0035836 | 26.9987 | 0.21491 | 0.4078 | 0.0061789 | 0.4516 | 0.09884 | 20.1338 | 0.0049433
1001.4 | 839.4 | 129.8929 | 0.06902 | 129.4312 | 0.32459 |  |  | 26.2758 | 0.0035836 | 28.4597 | 0.22465 | 0.4078 | 0.0061789 | 0.4516 | 0.10209 | 20.8156 | 0.0049433
1001.6 | 839.6 | 129.6981 | 0.067397 | 129.139 | 0.34894 |  |  | 28.2238 | 0.0035836 | 30.1154 | 0.23764 | 0.4078 | 0.0061789 | 0.4516 | 0.10696 | 22.1791 | 0.0049433
1001.8 | 839.8 | 129.5033 | 0.06902 | 128.9442 | 0.37005 |  |  | 29.6847 | 0.0035836 | 31.4789 | 0.24738 | 0.50518 | 0.0061789 | 0.4516 | 0.11183 | 23.0557 | 0.0049433
1002 | 840 | 129.3085 | 0.067397 | 128.7494 | 0.39277 |  |  | 31.1457 | 0.0035836 | 32.8425 | 0.25712 | 4.3036 | 0.0061789 | 0.35418 | 0.11832 | 23.64 | 0.0049433
1002.2 | 840.2 | 129.1137 | 0.067397 | 128.5546 | 0.42199 |  |  | 31.5353 | 0.0035836 | 33.2321 | 0.26036 | 6.2516 | 0.0061789 | 0.4516 | 0.12481 | 23.4453 | 0.0049433
1002.4 | 840.4 | 129.0164 | 0.06902 | 128.4573 | 0.43985 |  |  | 31.8274 | 0.0035836 | 33.4269 | 0.26199 | 7.2255 | 0.015918 | 0.4516 | 0.13131 | 23.3479 | 0.0033197
1002.6 | 840.6 | 128.8216 | 0.06902 | 128.3598 | 0.45933 |  |  | 32.217 | 0.0035836 | 33.5243 | 0.26199 | 8.5891 | 0.07111 | 0.35418 | 0.13942 | 23.3479 | 0.0049433
1002.8 | 840.8 | 128.7242 | 0.06902 | 128.165 | 0.4788 |  |  | 32.217 | 0.0035836 | 33.4269 | 0.26361 | 9.9527 | 0.088965 | 0.35418 | 0.14754 | 23.64 | 0.0049433
1003 | 841 | 128.6268 | 0.06902 | 128.0677 | 0.49504 |  |  | 32.0222 | 0.0035836 | 33.3295 | 0.26199 | 11.1214 | 0.098705 | 0.35418 | 0.15565 | 23.5427 | 0.0049433
1003.2 | 841.2 | 128.432 | 0.06902 | 127.9703 | 0.50965 |  |  | 32.0222 | 0.0035836 | 33.2321 | 0.26199 | 12.2902 | 0.10682 | 0.4516 | 0.16377 | 23.64 | 0.0049433
1003.4 | 841.4 | 128.432 | 0.06902 | 127.8729 | 0.52588 |  |  | 31.8274 | 0.0035836 | 33.2321 | 0.26199 | 13.0694 | 0.11331 | 0.4516 | 0.17513 | 23.5427 | 0.0049433
1003.6 | 841.6 | 128.2372 | 0.06902 | 127.7755 | 0.53887 |  |  | 31.4378 | 0.0035836 | 32.9399 | 0.26036 | 13.6537 | 0.11656 | 0.4516 | 0.1865 | 23.2505 | 0.0033197
1003.8 | 841.8 | 128.2372 | 0.06902 | 127.6781 | 0.55023 |  |  | 31.0483 | 0.0035836 | 32.8425 | 0.25874 | 14.4329 | 0.12305 | 0.35418 | 0.19786 | 22.9583 | 0.0049433
1004 | 842 | 128.0424 | 0.067397 | 127.5807 | 0.56321 |  |  | 30.7561 | 0.0035836 | 32.8425 | 0.26036 | 15.1147 | 0.12955 | 0.4516 | 0.21085 | 22.7635 | 0.0049433
1004.2 | 842.2 | 128.0424 | 0.06902 | 127.4833 | 0.58432 |  |  | 30.1717 | 0.0035836 | 32.3555 | 0.25712 | 15.6991 | 0.13117 | 0.4516 | 0.22221 | 21.8869 | 0.0049433
1004.4 | 842.4 | 127.945 | 0.06902 | 127.3859 | 0.60055 |  |  | 29.1977 | 0.0035836 | 31.7711 | 0.25225 | 16.186 | 0.13604 | 0.4516 | 0.23195 | 21.3025 | 0.0049433
1004.6 | 842.6 | 127.8476 | 0.06415 | 127.1911 | 0.61191 |  |  | 28.8081 | 0.0035836 | 31.3816 | 0.24738 | 16.8678 | 0.14091 | 0.4516 | 0.24656 | 20.9129 | 0.0049433
1004.8 | 842.8 | 128.1398 | 0.067397 | 127.0937 | 0.62977 |  |  | 27.8342 | 0.0035836 | 30.6998 | 0.24413 | 17.4522 | 0.14578 | 0.35418 | 0.25954 | 20.1338 | 0.0049433
1005 | 843 | 127.458 | 0.067397 | 126.7041 | 0.6736 |  |  | 26.568 | 0.0035836 | 30.2128 | 0.23926 | 19.4001 | 0.15877 | 0.35418 | 0.26928 | 18.1859 | 0.0049433
1005.2 | 843.2 | 127.0684 | 0.067397 | 126.4119 | 0.70769 |  |  | 25.9837 | 0.0035836 | 29.6284 | 0.23601 | 21.835 | 0.17987 | 0.35418 | 0.28552 | 17.3093 | 0.0049433
1005.4 | 843.4 | 126.7762 | 0.067397 | 126.2171 | 0.73691 |  |  | 24.2305 | 0.0035836 | 28.5571 | 0.22952 | 23.0038 | 0.18961 | 0.35418 | 0.29688 | 15.751 | 0.0049433
1005.6 | 843.6 | 126.5814 | 0.065774 | 126.0223 | 0.76288 |  |  | 23.1591 | 0.0035836 | 27.6805 | 0.22141 | 23.9777 | 0.1961 | 0.35418 | 0.31149 | 14.9717 | 0.0049433
1005.8 | 843.8 | 126.3866 | 0.067397 | 125.8276 | 0.78398 |  |  | 22.1852 | 0.0035836 | 26.9013 | 0.21654 | 24.2699 | 0.19773 | 0.4516 | 0.32285 | 12.5368 | 0.0033197
1006 | 844 | 126.0945 | 0.065774 | 125.6328 | 0.80184 |  |  | 21.5034 | 0.0019606 | 26.5117 | 0.21329 | 24.4647 | 0.19935 | 0.4516 | 0.34396 | 12.0499 | 0.0049433
1006.2 | 844.2 | 125.997 | 0.065774 | 125.5353 | 0.81807 |  |  | 20.7242 | 0.0035836 | 25.7326 | 0.20842 | 24.3673 | 0.19935 | 0.35418 | 0.36506 | 11.9525 | 0.0049433
1006.4 | 844.4 | 125.8997 | 0.067397 | 125.3406 | 0.8408 |  |  | 19.5555 | 0.0019606 | 24.856 | 0.20193 | 23.9777 | 0.1961 | 0.4516 | 0.37967 | 11.3681 | 0.0049433
1006.6 | 844.6 | 125.7049 | 0.067397 | 125.2432 | 0.8619 |  |  | 18.4841 | 0.0035836 | 23.9794 | 0.19543 | 23.7829 | 0.19286 | 0.4516 | 0.40239 | 10.6863 | 0.0049433
1006.8 | 844.8 | 125.6075 | 0.067397 | 125.0484 | 0.88462 |  |  | 16.9258 | 0.0035836 | 22.8107 | 0.18732 | 23.1012 | 0.18961 | 0.35418 | 0.417 | 9.5176 | 0.0049433
1007 | 845 | 125.4127 | 0.065774 | 124.8536 | 0.9106 |  |  | 16.0492 | 0.0019606 | 22.0315 | 0.18245 | 22.9064 | 0.18636 | 0.35418 | 0.45109 | 8.7384 | 0.0033197
1007.2 | 845.2 | 125.2179 | 0.065774 | 124.6588 | 0.9317 |  |  | 15.3674 | 0.0035836 | 21.3497 | 0.17758 | 22.6142 | 0.18474 | 0.4516 | 0.49005 | 8.2514 | 0.0049433
1007.4 | 845.4 | 125.0231 | 0.065774 | 124.464 | 0.9528 |  |  | 14.1986 | 0.0019606 | 20.2783 | 0.16946 | 22.0298 | 0.17987 | 0.4516 | 0.51115 | 7.3748 | 0.0049433
1007.6 | 845.6 | 124.7309 | 0.065774 | 124.1718 | 0.9804 |  |  | 13.3221 | 0.0035836 | 19.4018 | 0.16297 | 21.348 | 0.175 | 0.35418 | 0.52738 | 6.6931 | 0.0049433
1007.8 | 845.8 | 124.5361 | 0.067397 | 124.0744 | 1.008 |  |  | 12.4455 | 0.0035836 | 18.6226 | 0.15647 | 20.4715 | 0.16851 | 0.35418 | 0.55985 | 6.2061 | 0.0033197
1008 | 846 | 124.3413 | 0.067397 | 123.7822 | 1.0372 |  |  | 11.7637 | 0.0019606 | 17.9409 | 0.14998 | 19.7897 | 0.16201 | 0.35418 | 0.59069 | 5.9139 | 0.0033197
1008.2 | 846.2 | 124.0491 | 0.067397 | 123.5874 | 1.0697 |  |  | 11.569 | 0.0035836 | 17.7461 | 0.14998 | 18.7183 | 0.15552 | 0.4516 | 0.63614 | 6.1087 | 0.0049433
1008.4 | 846.4 | 123.8544 | 0.067397 | 123.3926 | 1.1005 |  |  | 11.3742 | 0.0019606 | 17.4539 | 0.14836 | 17.4522 | 0.14578 | 0.4516 | 0.68647 | 6.3035 | 0.0049433
1008.6 | 846.6 | 123.5621 | 0.065774 | 123.1004 | 1.133 |  |  | 10.595 | 0.0035836 | 16.8695 | 0.14511 | 15.7964 | 0.13442 | 0.4516 | 0.71406 | 6.1087 | 0.0049433
1008.8 | 846.8 | 123.3673 | 0.065774 | 122.8082 | 1.1671 |  |  | 10.4002 | 0.0035836 | 16.4799 | 0.14024 | 14.7251 | 0.12468 | 0.35418 | 0.75464 | 6.3035 | 0.0049433
1009 | 847 | 123.1726 | 0.06415 | 122.6134 | 1.1947 |  |  | 9.8158 | 0.0035836 | 15.8955 | 0.137 | 13.5563 | 0.11494 | 0.4516 | 0.79036 | 6.1087 | 0.0049433
1009.2 | 847.2 | 122.9778 | 0.065774 | 122.4186 | 1.2271 |  |  | 9.5236 | 0.0035836 | 15.4085 | 0.13213 | 12.9719 | 0.11169 | 0.35418 | 0.83581 | 6.1087 | 0.0049433
1009.4 | 847.4 | 122.6856 | 0.065774 | 122.3213 | 1.2628 |  |  | 9.0366 | 0.0035836 | 14.9215 | 0.12726 | 12.0954 | 0.1052 | 0.35418 | 0.87314 | 5.9139 | 0.0033197
1009.6 | 847.6 | 122.4908 | 0.065774 | 121.8343 | 1.2888 |  |  | 8.647 | 0.0035836 | 14.532 | 0.12401 | 12.0954 | 0.10358 | 0.4516 | 0.91372 | 6.0113 | 7.2982e-05
1009.8 | 847.8 | 122.296 | 0.062527 | 121.8343 | 1.3034 |  |  | 8.1601 | 0.0019606 | 13.9476 | 0.12076 | 11.511 | 0.10195 | 0.4516 | 0.95106 | 5.9139 | 0.0049433
1010 | 848 | 122.0038 | 0.06415 | 121.5421 | 1.3343 |  |  | 7.8679 | 0.0035836 | 13.071 | 0.11427 | 10.8292 | 0.097082 | 0.15942 | 0.97541 | 5.5243 | 0.0016967
1010.2 | 848.2 | 121.9064 | 0.065774 | 121.2499 | 1.3538 |  |  | 7.6731 | 0.0035836 | 12.4866 | 0.11102 | 10.1474 | 0.093836 | 0.4516 | 1.0095 | 5.4269 | 0.0049433
1010.4 | 848.4 | 121.6142 | 0.065774 | 120.8603 | 1.3878 |  |  | 7.2835 | 0.0035836 | 12.1945 | 0.09479 | 10.05 | 0.088965 | 0.35418 | 1.0468 | 4.9399 | 0.0033197
1010.6 | 848.6 | 121.1272 | 0.062527 | 121.2499 | 1.4609 |  |  | 7.3809 | 0.0035836 | 12.2918 | 0.1094 | 10.4396 | 0.088965 | -0.1328 | 1.115 | 5.7191 | 0.0081893
1010.8 | 848.8 | 120.835 | 0.065774 | 120.0812 | 1.5112 |  |  | 6.7965 | 0.0068303 | 11.7075 | 0.11102 | 9.7579 | 0.090589 | 0.54898 | 1.1523 | 4.5503 | 0.0065663
1011 | 849 | 120.2506 | 0.059281 | 119.4968 | 1.5761 |  |  | 6.6991 | 0.0035836 | 11.7075 | 0.10128 | 9.0761 | 0.085719 | 0.2568 | 1.2027 | 4.3555 | 0.0065663
1011.2 | 849.2 | 119.9585 | 0.06415 | 119.2046 | 1.6281 |  |  | 6.7965 | 0.0019606 | 10.9283 | 0.093167 | 9.8552 | 0.087342 | 0.4516 | 1.2514 | 5.1347 | 0.0033197
1011.4 | 849.4 | 119.0819 | 0.062527 | 119.1072 | 1.6865 |  |  | 6.0173 | 0.0019606 | 10.6361 | 0.09479 | 9.6604 | 0.097082 | -0.23018 | 1.2611 | 4.1607 | -0.011289
1011.6 | 849.6 | 119.8611 | 0.044671 | 119.0098 | 1.6881 |  |  | 6.1148 | 0.0052073 | 10.5387 | 0.086674 | 9.1735 | 0.079226 | 0.93858 | 1.2952 | 4.8425 | 0.0081893
1011.8 | 849.8 | 118.5949 | 0.067397 | 118.7176 | 1.7677 |  |  | 6.1148 | 0.0035836 | 10.2465 | 0.085051 | 9.4657 | 0.058124 | 0.93858 | 1.352 | 4.6477 | 0.017929
1012 | 850 | 118.3027 | 0.060904 | 118.4254 | 1.8002 |  |  | 5.8226 | 0.0019606 | 9.2726 | 0.088297 | 8.8813 | 0.07111 | -0.1328 | 1.3617 | 4.2582 | 0.0033197
1012.2 | 850.2 | 118.0105 | 0.070644 | 117.841 | 1.8505 |  |  | 5.7252 | 0.00033696 | 9.5647 | 0.067194 | 8.4917 | 0.080849 | 0.4516 | 1.3812 | 4.3555 | 0.009813
1012.4 | 850.4 | 118.2053 | 0.056034 | 117.4515 | 1.8651 |  |  | 6.1148 | 0.00033696 | 8.9803 | 0.075311 | 8.2969 | 0.067863 | 0.6464 | 1.3893 | 4.1607 | 0.014683
1012.6 | 850.6 | 118.2053 | 0.067397 | 116.6722 | 1.8975 |  |  | 5.0434 | -0.0045327 | 8.2012 | 0.070441 | 8.1021 | 0.067863 | 0.74378 | 1.4299 | 3.8686 | 7.2982e-05
1012.8 | 850.8 | 117.5236 | 0.070644 | 117.5488 | 1.9365 |  |  | 6.0173 | -0.0061557 | 8.1038 | 0.076934 | 8.2969 | 0.05163 | -0.03538 | 1.438 | 4.5503 | 0.0033197
1013 | 851 | 116.7444 | 0.054411 | 115.8931 | 2.0339 |  |  | 5.2382 | 0.0084533 | 8.1038 | 0.081804 | 8.2969 | 0.059747 | 0.54898 | 1.4965 | 3.479 | 0.0065663
1013.2 | 851.2 | 116.3548 | 0.077136 | 115.6983 | 2.094 |  |  | 4.5564 | -0.001286 | 8.2012 | 0.073688 | 8.3943 | 0.06624 | 1.7177 | 1.55 | 4.5503 | 0.009813
1013.4 | 851.4 | 115.3808 | 0.046295 | 115.9905 | 2.1475 |  |  | 4.6538 | -0.0061557 | 8.7856 | 0.070441 | 9.1735 | 0.06137 | 2.3995 | 1.5987 | 4.3555 | 7.2982e-05
1013.6 | 851.6 | 115.0887 | 0.056034 | 115.6983 | 2.2222 |  |  | 5.1408 | -0.011025 | 6.935 | 0.073688 | 8.8813 | 0.074356 | 0.4516 | 1.6198 | 3.7712 | 0.0016967
1013.8 | 851.8 | 114.7965 | 0.043048 | 114.6269 | 2.2612 |  |  | 5.0434 | -0.0061557 | 8.0064 | 0.057455 | 8.9787 | 0.072733 | 0.54898 | 1.6572 | 4.2582 | 0.009813
1014 | 852 | 114.2121 | 0.036554 | 114.4321 | 2.3407 |  |  | 5.7252 | 0.0019606 | 8.0064 | 0.063948 | 7.9073 | 0.06137 | 0.4516 | 1.6913 | 4.6477 | 0.0016967
1014.2 | 852.2 | 114.3095 | 0.059281 | 114.4321 | 2.3699 |  |  | 5.2382 | 0.0052073 | 8.0064 | 0.063948 | 8.7839 | 0.090589 | 0.062 | 1.7026 | 4.3555 | 0.0081893
1014.4 | 852.4 | 114.1147 | 0.043048 | 113.3608 | 2.4267 |  |  | 5.7252 | 0.02144 | 7.6168 | 0.065571 | 8.2969 | 0.074356 | 0.4516 | 1.7254 | 4.1607 | 0.0049433
1014.6 | 852.6 | 113.8225 | 0.052787 | 112.7764 | 2.4543 |  |  | 4.6538 | 0.0035836 | 7.6168 | 0.057455 | 8.9787 | 0.058124 | 0.54898 | 1.7611 | 3.8686 | 0.0033197
1014.8 | 852.8 | 113.0433 | 0.046295 | 113.8478 | 2.5095 |  |  | 4.8486 | -0.0061557 | 7.909 | 0.041222 | 8.4917 | 0.088965 | -0.52236 | 1.8179 | 4.9399 | 0.0065663
1015 | 853 | 113.4329 | 0.054411 | 112.5816 | 2.568 |  |  | 4.5564 | 0.00033696 | 7.422 | 0.065571 | 8.8813 | 0.085719 | 0.062 | 1.8698 | 4.7451 | 0.0016967
1015.2 | 853.2 | 112.5563 | 0.052787 | 111.9972 | 2.6426 |  |  | 4.1668 | -0.0029091 | 7.7142 | 0.049339 | 8.9787 | 0.074356 | 1.2308 | 1.9137 | 4.8425 | -0.01616
1015.4 | 853.4 | 111.6798 | 0.031685 | 112.192 | 2.7076 |  |  | 5.0434 | 0.0019606 | 6.5454 | 0.060702 | 10.1474 | 0.074356 | 0.4516 | 1.9721 | 3.9659 | 0.009813
1015.6 | 853.6 | 110.7058 | 0.046295 | 111.2181 | 2.7952 |  |  | 4.8486 | 0.0068303 | 7.7142 | 0.062325 | 8.8813 | 0.075979 | -0.03538 | 2.0176 | 4.2582 | 0.021176
1015.8 | 853.8 | 110.9006 | 0.028438 | 110.1467 | 2.8666 |  |  | 5.7252 | 0.0117 | 7.2272 | 0.062325 | 9.3683 | 0.072733 | 0.74378 | 2.0451 | 4.4529 | 0.009813
1016 | 854 | 110.4136 | 0.059281 | 109.5623 | 2.9348 |  |  | 4.946 | -0.0077794 | 8.2012 | 0.054208 | 9.2709 | 0.074356 | 0.2568 | 2.102 | 4.5503 | -0.00155
1016.2 | 854.2 | 109.7319 | 0.036554 | 109.8545 | 2.9705 |  |  | 5.2382 | 0.0019606 | 7.8116 | 0.062325 | 9.7579 | 0.058124 | 0.6464 | 2.1555 | 4.5503 | 0.0033197
1016.4 | 854.4 | 110.2188 | 0.051164 | 109.4649 | 3.0144 |  |  | 5.3356 | 0.0117 | 7.5194 | 0.08018 | 8.8813 | 0.079226 | 1.1334 | 2.1718 | 4.8425 | 0.021176
1016.6 | 854.6 | 109.1475 | 0.047918 | 109.4649 | 3.0631 |  |  | 4.6538 | 0.00033696 | 7.909 | 0.065571 | 9.1735 | 0.074356 | 0.062 | 2.214 | 4.8425 | 0.0033197
1016.8 | 854.8 | 108.6605 | 0.038178 | 108.1988 | 3.1166 |  |  | 4.459 | 0.0068303 | 7.5194 | 0.067194 | 9.0761 | 0.077602 | 0.6464 | 2.2416 | 4.8425 | 0.0065663
1017 | 855 | 109.3423 | 0.057658 | 108.2962 | 3.1507 |  |  | 4.3616 | 0.0052073 | 7.909 | 0.073688 | 9.5631 | 0.07111 | 0.74378 | 2.261 | 4.7451 | 0.0065663
1017.2 | 855.2 | 108.6605 | 0.062527 | 108.2962 | 3.1897 |  |  | 4.8486 | 0.0019606 | 8.1038 | 0.073688 | 9.8552 | 0.079226 | 0.4516 | 2.2529 | 5.2321 | 0.0065663
1017.4 | 855.4 | 108.1735 | 0.056034 | 107.9066 | 3.2335 |  |  | 5.0434 | -0.0061557 | 7.909 | 0.073688 | 9.6604 | 0.072733 | 0.2568 | 2.2903 | 4.7451 | 0.011436
1017.6 | 855.6 | 107.8813 | 0.06902 | 107.3222 | 3.2871 |  |  | 5.2382 | 0.0019606 | 8.2012 | 0.073688 | 9.3683 | 0.080849 | 0.4516 | 2.3179 | 4.5503 | 0.0049433
1017.8 | 855.8 | 107.3943 | 0.057658 | 106.543 | 3.3812 |  |  | 5.1408 | 0.0019606 | 8.2012 | 0.075311 | 9.6604 | 0.084096 | 0.35418 | 2.373 | 5.1347 | 0.0033197
1018 | 856 | 106.8099 | 0.060904 | 106.1535 | 3.4624 |  |  | 5.1408 | 0.0035836 | 8.2986 | 0.073688 | 9.7579 | 0.084096 | 0.35418 | 2.412 | 5.1347 | 0.0049433
1018.2 | 856.2 | 106.5177 | 0.062527 | 105.9587 | 3.5257 |  |  | 5.1408 | 0.0019606 | 8.2986 | 0.075311 | 9.4657 | 0.082473 | 0.2568 | 2.438 | 5.1347 | 0.0049433
1018.4 | 856.4 | 105.7386 | 0.06415 | 105.4717 | 3.5858 |  |  | 5.1408 | 0.0035836 | 8.396 | 0.073688 | 9.7579 | 0.084096 | 0.35418 | 2.4721 | 5.1347 | 0.0049433
1018.6 | 856.6 | 105.5438 | 0.062527 | 104.9847 | 3.6523 |  |  | 5.2382 | 0.0035836 | 8.2986 | 0.075311 | 9.7579 | 0.085719 | 0.35418 | 2.4948 | 5.1347 | 0.0049433
1018.8 | 856.8 | 105.1542 | 0.062527 | 104.6925 | 3.701 |  |  | 5.0434 | 0.0019606 | 8.2986 | 0.076934 | 9.7579 | 0.082473 | 0.35418 | 2.5143 | 5.2321 | 0.0049433
1019 | 857 | 104.862 | 0.060904 | 104.4003 | 3.7351 |  |  | 5.1408 | 0.0019606 | 8.2986 | 0.075311 | 9.7579 | 0.084096 | 0.35418 | 2.5402 | 5.1347 | 0.0049433
1019.2 | 857.2 | 104.6672 | 0.062527 | 104.2055 | 3.7627 |  |  | 5.1408 | 0.0035836 | 8.2012 | 0.072064 | 9.5631 | 0.084096 | 0.4516 | 2.5776 | 5.1347 | 0.0033197
1019.4 | 857.4 | 104.4724 | 0.060904 | 103.9133 | 3.7984 |  |  | 4.946 | 0.0019606 | 8.2012 | 0.073688 | 9.4657 | 0.082473 | 0.4516 | 2.6084 | 5.1347 | 0.0033197
1019.6 | 857.6 | 104.1802 | 0.060904 | 103.5238 | 3.8487 |  |  | 5.0434 | 0.0019606 | 8.1038 | 0.073688 | 9.4657 | 0.080849 | 0.35418 | 2.662 | 5.1347 | 0.0033197
1019.8 | 857.8 | 103.5959 | 0.060904 | 103.0368 | 3.9153 |  |  | 5.0434 | 0.0035836 | 8.2012 | 0.075311 | 9.4657 | 0.080849 | 0.4516 | 2.7123 | 5.1347 | 0.0049433
1020 | 858 | 103.2063 | 0.060904 | 102.7446 | 3.9607 |  |  | 4.946 | 0.0019606 | 8.2012 | 0.073688 | 9.4657 | 0.079226 | 0.35418 | 2.7594 | 5.1347 | 0.0049433
1020.2 | 858.2 | 103.0115 | 0.060904 | 102.5498 | 3.9948 |  |  | 5.0434 | 0.0019606 | 8.2012 | 0.073688 | 9.2709 | 0.080849 | 0.35418 | 2.8097 | 5.1347 | 0.0049433
1020.4 | 858.4 | 102.6219 | 0.060904 | 102.1602 | 4.05 |  |  | 4.946 | 0.0035836 | 8.2012 | 0.072064 | 9.2709 | 0.079226 | 0.4516 | 2.8519 | 5.1347 | 0.0049433
1020.6 | 858.6 | 102.1349 | 0.060904 | 101.5758 | 4.1328 |  |  | 4.946 | 0.0035836 | 8.2012 | 0.073688 | 9.4657 | 0.080849 | 0.4516 | 2.9233 | 5.2321 | 0.0033197
1020.8 | 858.8 | 101.7453 | 0.060904 | 101.1862 | 4.1815 |  |  | 4.946 | 0.0019606 | 8.2986 | 0.073688 | 9.4657 | 0.080849 | 0.35418 | 2.9818 | 5.1347 | 0.0049433
1021 | 859 | 101.3558 | 0.060904 | 100.894 | 4.2302 |  |  | 4.946 | 0.0035836 | 8.2986 | 0.073688 | 9.4657 | 0.082473 | 0.35418 | 3.0289 | 5.2321 | 0.0033197
1021.2 | 859.2 | 100.8688 | 0.060904 | 100.4071 | 4.2984 |  |  | 4.946 | 0.0019606 | 8.2012 | 0.073688 | 9.5631 | 0.082473 | 0.35418 | 3.0759 | 5.3295 | 0.0033197
1021.4 | 859.4 | 100.4792 | 0.062527 | 100.0175 | 4.3519 |  |  | 4.946 | 0.0019606 | 8.2012 | 0.073688 | 9.4657 | 0.082473 | 0.35418 | 3.1198 | 5.2321 | 0.0033197
1021.6 | 859.6 | 100.187 | 0.06902 | 99.6279 | 4.3893 |  |  | 4.8486 | 0.0035836 | 8.1038 | 0.073688 | 9.3683 | 0.080849 | 0.35418 | 3.1474 | 5.1347 | 0.0049433
1021.8 | 859.8 | 99.7974 | 0.07389 | 99.2383 | 4.4331 |  |  | 4.7512 | 0.0019606 | 8.1038 | 0.072064 | 9.2709 | 0.080849 | 0.4516 | 3.1928 | 5.1347 | 0.0049433
1022 | 860 | 99.4078 | 0.075513 | 98.9461 | 4.4737 |  |  | 4.8486 | 0.0019606 | 8.1038 | 0.073688 | 9.2709 | 0.079226 | 0.35418 | 3.2318 | 5.1347 | 0.0049433
1022.2 | 860.2 | 99.213 | 0.082007 | 98.6539 | 4.5062 |  |  | 4.7512 | 0.0019606 | 8.0064 | 0.073688 | 9.1735 | 0.079226 | 0.4516 | 3.2626 | 5.1347 | 0.0049433
1022.4 | 860.4 | 98.8234 | 0.091746 | 98.3617 | 4.5484 |  |  | 4.8486 | 0.0035836 | 8.0064 | 0.072064 | 9.1735 | 0.079226 | 0.4516 | 3.3145 | 5.1347 | 0.0049433
1022.6 | 860.6 | 98.2391 | 0.10636 | 97.6799 | 4.6182 |  |  | 4.7512 | 0.0035836 | 8.1038 | 0.073688 | 9.2709 | 0.079226 | 0.35418 | 3.3908 | 5.2321 | 0.0049433
1022.8 | 860.8 | 97.9468 | 0.12096 | 97.2904 | 4.6506 |  |  | 4.7512 | 0.0019606 | 8.1038 | 0.073688 | 9.2709 | 0.079226 | 0.35418 | 3.4249 | 5.2321 | 0.0033197
1023 | 861 | 97.3625 | 0.14207 | 96.8034 | 4.6993 |  |  | 4.8486 | 0.0019606 | 8.2012 | 0.073688 | 9.3683 | 0.080849 | 0.4516 | 3.4882 | 5.2321 | 0.0049433
1023.2 | 861.2 | 96.9729 | 0.17129 | 96.3164 | 4.7302 |  |  | 4.8486 | 0.0019606 | 8.2012 | 0.073688 | 9.3683 | 0.080849 | 0.54898 | 3.5499 | 5.1347 | 0.0049433
1023.4 | 861.4 | 96.1937 | 0.21836 | 95.732 | 4.7772 |  |  | 4.946 | 0.0019606 | 8.396 | 0.075311 | 9.3683 | 0.080849 | 0.35418 | 3.6668 | 5.3295 | 0.0049433
1023.6 | 861.6 | 95.6094 | 0.2557 | 95.0502 | 4.8308 |  |  | 5.0434 | 0.0035836 | 8.4934 | 0.075311 | 9.5631 | 0.082473 | 0.4516 | 3.7593 | 5.3295 | 0.0049433
1023.8 | 861.8 | 95.025 | 0.28979 | 94.5632 | 4.8568 |  |  | 5.1408 | 0.0035836 | 8.5908 | 0.076934 | 9.5631 | 0.082473 | 0.35418 | 3.8145 | 5.3295 | 0.0049433
1024 | 862 | 94.3432 | 0.33524 | 93.8815 | 4.8909 |  |  | 5.0434 | 0.0035836 | 8.5908 | 0.076934 | 9.4657 | 0.082473 | 0.35418 | 3.8778 | 5.3295 | 0.0049433
1024.2 | 862.2 | 93.6614 | 0.39368 | 93.1997 | 4.9363 |  |  | 5.1408 | 0.0035836 | 8.4934 | 0.076934 | 9.4657 | 0.082473 | 0.4516 | 3.9671 | 5.3295 | 0.0049433
1024.4 | 862.4 | 92.8822 | 0.45536 | 92.4205 | 4.9785 |  |  | 5.1408 | 0.0035836 | 8.5908 | 0.076934 | 9.4657 | 0.082473 | 0.4516 | 4.0596 | 5.3295 | 0.0049433
1024.6 | 862.6 | 92.0057 | 0.5138 | 91.4466 | 5.0321 |  |  | 5.1408 | 0.0035836 | 8.5908 | 0.076934 | 9.4657 | 0.082473 | 0.35418 | 4.1522 | 5.4269 | 0.0049433
1024.8 | 862.8 | 90.6421 | 0.57386 | 90.1804 | 5.1506 |  |  | 5.2382 | 0.0035836 | 8.883 | 0.078557 | 9.8552 | 0.084096 | 0.4516 | 4.3015 | 5.5243 | 0.0049433
1025 | 863 | 89.5708 | 0.64041 | 89.0117 | 5.2464 |  |  | 5.433 | 0.0019606 | 9.0778 | 0.081804 | 9.8552 | 0.085719 | 0.4516 | 4.4232 | 5.6217 | 0.0049433
1025.2 | 863.2 | 88.2072 | 0.71346 | 87.7455 | 5.3292 |  |  | 5.5304 | 0.0019606 | 9.1751 | 0.081804 | 9.9527 | 0.087342 | 0.35418 | 4.5466 | 5.7191 | 0.0049433
1025.4 | 863.4 | 87.3306 | 0.7719 | 86.8689 | 5.3746 |  |  | 5.5304 | 0.0035836 | 9.3699 | 0.081804 | 10.05 | 0.087342 | 0.4516 | 4.6505 | 5.8165 | 0.0049433
1025.6 | 863.6 | 86.4541 | 0.83683 | 85.9923 | 5.399 |  |  | 5.5304 | 0.0035836 | 9.3699 | 0.083427 | 10.1474 | 0.087342 | 0.4516 | 4.7008 | 5.9139 | 0.0049433
1025.8 | 863.8 | 85.5775 | 0.88877 | 85.1158 | 5.399 |  |  | 5.6278 | 0.0035836 | 9.3699 | 0.083427 | 10.1474 | 0.087342 | 0.4516 | 4.7723 | 5.9139 | 0.0049433
1026 | 864 | 84.5061 | 0.94559 | 84.1418 | 5.399 |  |  | 5.6278 | 0.0035836 | 9.4673 | 0.083427 | 10.1474 | 0.087342 | 0.35418 | 4.8664 | 6.0113 | 0.0049433
1026.2 | 864.2 | 83.24 | 1.0024 | 83.0705 | 5.399 |  |  | 5.7252 | 0.0019606 | 9.5647 | 0.086674 | 10.2448 | 0.087342 | 0.35418 | 4.9557 | 6.0113 | 0.0049433
1026.4 | 864.4 | 26.4578 | 0.3466 | 26.9701 | 1.7109 |  |  | 3.1929 | 0.0019606 | 4.5001 | 0.052585 | 4.888 | 0.05163 | 0.4516 | 1.5208 | 3.3816 | 0.0049433
1026.6 | 864.6 | 3.9592 | 0.044671 | 4.1793 | 0.14116 |  |  | 1.2449 | 0.0035836 | 1.3834 | 0.021743 | 1.5766 | 0.019165 | 0.35418 | 0.12644 | 1.3362 | 0.0049433
1026.8 | 864.8 | 1.6217 | 0.018699 | 1.5496 | 0.038897 |  |  | 0.85535 | 0.0019606 | 0.79904 | 0.016873 | 0.89478 | 0.014295 | 0.4516 | 0.035532 | 0.84925 | 0.0065663
1027 | 865 | 1.0373 | 0.012205 | 1.0626 | 0.022664 |  |  | 0.66054 | 0.0035836 | 0.70166 | 0.013627 | 0.69998 | 0.011049 | 0.4516 | 0.020923 | 0.75187 | 0.0049433
1027.2 | 865.2 | 0.93993 | 0.0089587 | 0.86778 | 0.017795 |  |  | 0.66054 | 0.0035836 | 0.50686 | 0.012003 | 0.6026 | 0.011049 | 0.4516 | 0.016053 | 0.65449 | 0.0049433
1027.4 | 865.4 | 0.74513 | 0.0073357 | 0.7704 | 0.014548 |  |  | 0.56316 | 0.0019606 | 0.50686 | 0.01038 | 0.6026 | 0.0094249 | 0.4516 | 0.012807 | 0.55707 | 0.0049433
1027.6 | 865.6 | 0.74513 | 0.0073357 | 0.7704 | 0.012925 |  |  | 0.56316 | 0.0035836 | 0.50686 | 0.01038 | 0.50518 | 0.0078019 | 0.35418 | 0.012807 | 0.55707 | 0.0049433
1027.8 | 865.8 | 0.74513 | 0.0073357 | 0.67302 | 0.011301 |  |  | 0.56316 | 0.0019606 | 0.50686 | 0.01038 | 0.50518 | 0.0078019 | 0.4516 | 0.011183 | 0.55707 | 0.0049433
1028 | 866 | 0.74513 | 0.0057127 | 0.67302 | 0.011301 |  |  | 0.56316 | 0.0035836 | 0.40948 | 0.01038 | 0.50518 | 0.0078019 | 0.35418 | 0.011183 | 0.55707 | 0.0049433
1028.2 | 866.2 | 0.64775 | 0.0057127 | 0.67302 | 0.0096782 |  |  | 0.56316 | 0.0035836 | 0.31206 | 0.0087568 | 0.50518 | 0.0078019 | 0.4516 | 0.0095602 | 0.55707 | 0.0049433
1028.4 | 866.4 | 0.64775 | 0.0057127 | 0.5756 | 0.0080546 |  |  | 0.56316 | 0.0019606 | 0.40948 | 0.01038 | 0.50518 | 0.0078019 | 0.35418 | 0.0095602 | 0.45969 | 0.0049433
1028.6 | 866.6 | 0.64775 | 0.0057127 | 0.67302 | 0.0080546 |  |  | 0.56316 | 0.0035836 | 0.40948 | 0.01038 | 0.4078 | 0.0078019 | 0.4516 | 0.0095602 | 0.45969 | 0.0049433
1028.8 | 866.8 | 0.64775 | 0.0057127 | 0.5756 | 0.0080546 |  |  | 0.56316 | 0.0035836 | 0.31206 | 0.01038 | 0.50518 | 0.0078019 | 0.4516 | 0.0095602 | 0.45969 | 0.0049433
1029 | 867 | 0.64775 | 0.0040891 | 0.5756 | 0.0080546 |  |  | 0.56316 | 0.0035836 | 0.31206 | 0.01038 | 0.4078 | 0.0078019 | 0.35418 | 0.0095602 | 0.36227 | 0.0049433
1029.2 | 867.2 | 0.55033 | 0.0040891 | 0.5756 | 0.0080546 |  |  | 0.46574 | 0.0035836 | 0.40948 | 0.0087568 | 0.50518 | 0.0078019 | 0.4516 | 0.0079366 | 0.45969 | 0.0049433
1029.4 | 867.4 | 0.55033 | 0.0057127 | 0.67302 | 0.0080546 |  |  | 0.56316 | 0.0019606 | 0.40948 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.0095602 | 0.45969 | 0.0049433
1029.6 | 867.6 | 0.64775 | 0.0040891 | 0.5756 | 0.0080546 |  |  | 0.46574 | 0.0035836 | 0.40948 | 0.0087568 | 0.50518 | 0.0061789 | 0.35418 | 0.0079366 | 0.45969 | 0.0065663
1029.8 | 867.8 | 0.55033 | 0.0057127 | 0.5756 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.01038 | 0.4078 | 0.0061789 | 0.4516 | 0.0079366 | 0.45969 | 0.0049433
1030 | 868 | 0.55033 | 0.0040891 | 0.5756 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.0079366 | 0.36227 | 0.0049433
1060 | 898 | 0.45295 | 0.0040891 | 0.47822 | 0.0048085 |  |  | 0.36836 | 0.0035836 | 0.31206 | 0.0087568 | 0.31038 | 0.0045552 | 0.4516 | 0.0063136 | 0.36227 | 0.0049433
1090 | 928 | 0.45295 | 0.0040891 | 0.3808 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.31206 | 0.0071332 | 0.31038 | 0.0045552 | 0.4516 | 0.0046906 | 0.45969 | 0.0033197
1120 | 958 | 0.45295 | 0.0040891 | 0.3808 | 0.0048085 |  |  | 0.36836 | 0.0035836 | 0.31206 | 0.01038 | 0.31038 | 0.0061789 | 0.35418 | 0.0046906 | 0.36227 | 0.0065663
1150 | 988 | 0.45295 | 0.0040891 | 0.3808 | 0.0064315 |  |  | 0.46574 | 0.0019606 | 0.31206 | 0.0087568 | 0.4078 | 0.0045552 | 0.54898 | 0.0063136 | 0.36227 | 0.0049433
1180 | 1018 | 0.45295 | 0.0040891 | 0.47822 | 0.0064315 |  |  | 0.46574 | 0.0019606 | 0.31206 | 0.0087568 | 0.4078 | 0.0061789 | 0.4516 | 0.0063136 | 0.36227 | 0.0049433
1210 | 1048 | 0.45295 | 0.0040891 | 0.47822 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.40948 | 0.0071332 | 0.31038 | 0.0061789 | 0.4516 | 0.0063136 | 0.45969 | 0.0049433
1240 | 1078 | 0.45295 | 0.0057127 | 0.47822 | 0.0064315 |  |  | 0.46574 | 0.0035836 | 0.40948 | 0.0087568 | 0.4078 | 0.0078019 | 0.35418 | 0.0063136 | 0.45969 | 0.0049433

## Circuit 3 Faulting
Summary of Observed Faulting Behavior for Circuit #3
DAQ Time | Burner Time | Event | Discussion
162 | 0 | Burner on
520 | 358 | Initial signs of degradation | There are initial signs of cable degradation based on a voltage return signal on circuit path 6
520-542 | 358-380 | increasing voltage on Target Path 6 | The voltage on circuit path 6 is unsteady, but climbs to a maximum value of approximately 54V. The voltage was not sufficient to cause either relay chatter nor SA.
543 | 381 | Fuse Blow | Source conductor on Path 2 appears to have shorted to external ground causing a fuse blow failure. (No return current detected on the grounded condutor on Path 7).
Summary Observations |  | The circuit eperienced a fuse blow failure apparently as a result of a short between one energized source conductor and an external ground source. Only very minor degradation of supply voltage prior to fuse blow is noted.

## Converted Data C3
DAQ Time | Burner Time | C3 V1 | C3 A1 | C3 V2 | C3 A2 | C3 V3 | C3 A3 | C3 V4 | C3 A4 | C3 V5 | C3 A5 | C3 V6 | C3 A6 | C3 V7 | C3 A7 | C3 V8 | C3 A8
0 | -162 | 132.371 | 0.081018 | 131.7755 | 0.0067236 |  |  | 0.39327 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.31106 | 0.077501 | 2.2128 | 0.006027
30 | -132 | 132.5658 | 0.074525 | 132.165 | 0.0034769 |  |  | 0.39327 | 0.0030389 | 0.37035 | 0.0031344 | 0.086261 | 0.0042351 | 0.31106 | 0.075878 | 2.2128 | 0.006027
60 | -102 | 132.371 | 0.077771 | 131.9703 | 0.0050999 |  |  | 0.29589 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.31106 | 0.077501 | 2.2128 | 0.00765
90 | -72 | 132.6632 | 0.074525 | 132.2625 | 0.0050999 |  |  | 0.39327 | 0.0030389 | 0.46777 | 0.0015107 | 0.18368 | 0.0042351 | 0.31106 | 0.077501 | 2.2128 | 0.00765
120 | -42 | 132.9554 | 0.074525 | 132.3598 | 0.0050999 |  |  | 0.29589 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.31106 | 0.077501 | 2.2128 | 0.006027
150 | -12 | 132.7606 | 0.077771 | 132.2625 | 0.0067236 |  |  | 0.29589 | 0.0046619 | 0.37035 | 0.0047574 | 0.18368 | 0.0058588 | 0.40844 | 0.079125 | 2.3102 | 0.00765
180 | 18 | 132.858 | 0.074525 | 132.4573 | 0.0050999 |  |  | 0.39327 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.31106 | 0.079125 | 2.2128 | 0.006027
210 | 48 | 132.7606 | 0.082641 | 132.165 | 0.0083466 |  |  | 0.39327 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.31106 | 0.079125 | 2.2128 | 0.006027
240 | 78 | 132.9554 | 0.082641 | 132.5546 | 0.0083466 |  |  | 0.39327 | 0.0030389 | 0.46777 | 0.0031344 | 0.28106 | 0.0042351 | 0.31106 | 0.079125 | 2.3102 | 0.00765
270 | 108 | 133.345 | 0.076148 | 132.8468 | 0.0050999 |  |  | 0.39327 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.31106 | 0.079125 | 2.3102 | 0.00765
300 | 138 | 132.858 | 0.081018 | 132.4573 | 0.0067236 |  |  | 0.29589 | 0.0046619 | 0.37035 | 0.0047574 | 0.18368 | 0.0042351 | 0.31106 | 0.079125 | 2.3102 | 0.00765
330 | 168 | 133.345 | 0.085888 | 132.9443 | 0.0099696 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 2.2128 | 0.00765
360 | 198 | 133.2476 | 0.077771 | 132.8468 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0042351 | 0.50586 | 0.080748 | 2.3102 | 0.00765
390 | 228 | 132.9554 | 0.079395 | 132.5546 | 0.0050999 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 2.3102 | 0.00765
420 | 258 | 133.0528 | 0.077771 | 132.5546 | 0.0050999 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0031344 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 2.2128 | 0.00765
450 | 288 | 133.6372 | 0.076148 | 133.2364 | 0.0067236 |  |  | 0.39327 | 0.0030389 | 0.37035 | 0.0031344 | 0.18368 | 0.0042351 | 0.40844 | 0.080748 | 2.018 | 0.0092737
480 | 318 | 133.345 | 0.084264 | 132.9443 | 0.0083466 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.18368 | 0.0042351 | 0.40844 | 0.079125 | 4.5503 | 0.00765
510 | 348 | 133.4424 | 0.079395 | 132.9443 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.1607 | 0.00765
510.2 | 348.2 | 133.4424 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.39327 | 0.0062856 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.50586 | 0.082371 | 4.1607 | 0.0092737
510.4 | 348.4 | 133.4424 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.50586 | 0.082371 | 4.2582 | 0.00765
510.6 | 348.6 | 133.345 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 4.2582 | 0.0092737
510.8 | 348.8 | 133.4424 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.2582 | 0.0092737
511 | 349 | 133.4424 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 4.3555 | 0.00765
511.2 | 349.2 | 133.4424 | 0.079395 | 133.0416 | 0.0083466 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 4.3555 | 0.0092737
511.4 | 349.4 | 133.5397 | 0.077771 | 133.0416 | 0.0067236 |  |  | 0.49069 | 0.0062856 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.4529 | 0.0092737
511.6 | 349.6 | 133.4424 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.4529 | 0.00765
511.8 | 349.8 | 133.5397 | 0.079395 | 133.1391 | 0.0050999 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.4529 | 0.0092737
512 | 350 | 133.4424 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.3555 | 0.0092737
512.2 | 350.2 | 133.5397 | 0.077771 | 133.0416 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 4.3555 | 0.0092737
512.4 | 350.4 | 133.5397 | 0.079395 | 133.1391 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 4.2582 | 0.0092737
512.6 | 350.6 | 133.4424 | 0.079395 | 133.1391 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.50586 | 0.080748 | 4.1607 | 0.00765
512.8 | 350.8 | 133.5397 | 0.079395 | 133.1391 | 0.0067236 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 4.2582 | 0.0092737
513 | 351 | 133.5397 | 0.079395 | 133.0416 | 0.0067236 |  |  | 0.39327 | 0.0062856 | 0.37035 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 4.1607 | 0.0092737
513.2 | 351.2 | 133.4424 | 0.077771 | 133.0416 | 0.0067236 |  |  | 0.49069 | 0.0062856 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.50586 | 0.082371 | 4.1607 | 0.00765
513.4 | 351.4 | 132.371 | 0.079395 | 131.8729 | 0.042436 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.50586 | 0.080748 | 4.4529 | 0.0092737
513.6 | 351.6 | 130.2283 | 0.076148 | 129.8276 | 0.50345 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.079125 | 4.4529 | 0.0092737
513.8 | 351.8 | 131.0074 | 0.072901 | 130.5093 | 0.38495 |  |  | 0.19851 | 0.0079086 | 0.17559 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 4.6477 | 0.00765
514 | 352 | 132.9554 | 0.077771 | 132.4573 | 0.10087 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0074818 | 0.40844 | 0.079125 | 4.7451 | 0.0092737
514.2 | 352.2 | 131.5918 | 0.077771 | 131.0937 | 0.28268 |  |  | 0.49069 | 0.0046619 | 0.56516 | 0.0047574 | 0.47586 | 0.0074818 | 0.31106 | 0.082371 | 4.6477 | 0.006027
514.4 | 352.4 | 129.6439 | 0.074525 | 129.0484 | 0.65928 |  |  | 0.29589 | 0.0079086 | 0.46777 | 0.0047574 | 0.18368 | 0.0042351 | 0.31106 | 0.077501 | 4.7451 | 0.006027
514.6 | 352.6 | 131.2996 | 0.076148 | 130.8989 | 0.36871 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 4.6477 | 0.0092737
514.8 | 352.8 | 132.0788 | 0.077771 | 131.6781 | 0.20476 |  |  | 0.39327 | 0.0062856 | 0.46777 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.082371 | 4.7451 | 0.00765
515 | 353 | 133.2476 | 0.077771 | 132.8468 | 0.063538 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.50586 | 0.082371 | 4.8425 | 0.00765
515.2 | 353.2 | 133.5397 | 0.077771 | 133.1391 | 0.022956 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.0373 | 0.0092737
515.4 | 353.4 | 133.4424 | 0.077771 | 133.0416 | 0.018086 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.0373 | 0.0092737
515.6 | 353.6 | 133.4424 | 0.077771 | 133.0416 | 0.016463 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.0373 | 0.00765
515.8 | 353.8 | 133.4424 | 0.077771 | 133.0416 | 0.016463 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.1347 | 0.00765
516 | 354 | 133.345 | 0.077771 | 132.9443 | 0.01971 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.50586 | 0.080748 | 5.1347 | 0.00765
516.2 | 354.2 | 133.345 | 0.077771 | 132.9443 | 0.01971 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.2321 | 0.00765
516.4 | 354.4 | 133.345 | 0.077771 | 132.9443 | 0.021333 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 5.3295 | 0.0092737
516.6 | 354.6 | 133.4424 | 0.077771 | 132.9443 | 0.026202 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0042351 | 0.50586 | 0.082371 | 5.3295 | 0.00765
516.8 | 354.8 | 133.1502 | 0.082641 | 132.5546 | 0.050552 |  |  | 0.39327 | 0.0062856 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 5.3295 | 0.00765
517 | 355 | 133.2476 | 0.077771 | 132.8468 | 0.065161 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.2321 | 0.0092737
517.2 | 355.2 | 133.4424 | 0.077771 | 133.0416 | 0.031073 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 5.1347 | 0.00765
517.4 | 355.4 | 133.4424 | 0.077771 | 133.0416 | 0.016463 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 5.2321 | 0.0092737
517.6 | 355.6 | 133.345 | 0.077771 | 132.9443 | 0.018086 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 5.5243 | 0.00765
517.8 | 355.8 | 133.345 | 0.077771 | 132.9443 | 0.027826 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.082371 | 5.9139 | 0.00765
518 | 356 | 133.2476 | 0.077771 | 132.9443 | 0.031073 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.080748 | 6.1087 | 0.0092737
518.2 | 356.2 | 133.4424 | 0.077771 | 132.9443 | 0.034319 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 6.2061 | 0.00765
518.4 | 356.4 | 133.2476 | 0.077771 | 132.8468 | 0.040812 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 6.2061 | 0.00765
518.6 | 356.6 | 133.2476 | 0.077771 | 132.8468 | 0.048928 |  |  | 0.49069 | 0.0062856 | 0.37035 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 6.1087 | 0.00765
518.8 | 356.8 | 133.2476 | 0.077771 | 132.8468 | 0.042436 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0031344 | 0.28106 | 0.0058588 | 0.40844 | 0.080748 | 5.8165 | 0.0092737
519 | 357 | 133.2476 | 0.077771 | 132.8468 | 0.042436 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 6.1087 | 0.00765
519.2 | 357.2 | 133.1502 | 0.077771 | 132.7495 | 0.058668 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.082371 | 6.4009 | 0.0092737
519.4 | 357.4 | 132.9554 | 0.077771 | 132.5546 | 0.081394 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.37844 | 0.0058588 | 0.40844 | 0.080748 | 6.5956 | 0.00765
519.6 | 357.6 | 132.4684 | 0.074525 | 132.165 | 0.16093 |  |  | 0.29589 | 0.0062856 | 0.37035 | 0.0047574 | 0.18368 | 0.0058588 | 0.31106 | 0.080748 | 6.5956 | 0.0092737
519.8 | 357.8 | 131.7866 | 0.074525 | 131.2885 | 0.29891 |  |  | 0.39327 | 0.0062856 | 0.37035 | 0.006381 | 0.28106 | 0.0058588 | 0.31106 | 0.079125 | 6.9852 | 0.0092737
520 | 358 | 130.5205 | 0.074525 | 130.1197 | 0.46773 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | -0.0006346 | 0.50586 | 0.079125 | 6.6931 | 0.010897
520.2 | 358.2 | 128.2803 | 0.076148 | 127.7822 | 0.83135 |  |  | 0.68549 | -0.0018308 | 0.37035 | 0.0015107 | 0.57324 | 0.0058588 | 0.21368 | 0.079125 | 7.18 | 0.00765
520.4 | 358.4 | 126.0402 | 0.069655 | 125.5421 | 1.1755 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.006381 | 0.28106 | 0.0058588 | 0.40844 | 0.077501 | 7.3748 | 0.00765
520.6 | 358.6 | 131.1048 | 0.076148 | 130.8015 | 0.40605 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.010728 | 0.40844 | 0.079125 | 8.0566 | 0.00765
520.8 | 358.8 | 132.9554 | 0.076148 | 132.652 | 0.09925 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 8.852 | 0.0074818 | 0.40844 | 0.082371 | 8.641 | 0.00765
521 | 359 | 133.345 | 0.077771 | 132.8468 | 0.050552 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0031344 | 9.1441 | 0.0058588 | 0.40844 | 0.082371 | 8.154 | 0.00765
521.2 | 359.2 | 133.345 | 0.077771 | 133.0416 | 0.032696 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 6.2223 | 0.0074818 | 0.31106 | 0.082371 | 7.4722 | 0.00765
521.4 | 359.4 | 133.345 | 0.076148 | 132.9443 | 0.027826 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 3.2029 | 0.0058588 | 0.40844 | 0.080748 | 7.5696 | 0.00765
521.6 | 359.6 | 133.345 | 0.077771 | 132.9443 | 0.029449 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 3.7874 | 0.0058588 | 0.40844 | 0.080748 | 7.4722 | 0.00765
521.8 | 359.8 | 133.345 | 0.076148 | 132.9443 | 0.027826 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 3.2029 | 0.0042351 | 0.40844 | 0.080748 | 7.3748 | 0.00765
522 | 360 | 133.345 | 0.077771 | 132.9443 | 0.026202 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0031344 | 3.3978 | 0.0042351 | 0.40844 | 0.080748 | 7.5696 | 0.00765
522.2 | 360.2 | 133.345 | 0.077771 | 132.9443 | 0.031073 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 3.7874 | 0.0058588 | 0.40844 | 0.080748 | 7.7644 | 0.00765
522.4 | 360.4 | 133.345 | 0.077771 | 132.9443 | 0.031073 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0031344 | 4.0795 | 0.0058588 | 0.40844 | 0.082371 | 7.9592 | 0.00765
522.6 | 360.6 | 133.345 | 0.076148 | 132.9443 | 0.032696 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 3.8847 | 0.0042351 | 0.40844 | 0.082371 | 8.4462 | 0.00765
522.8 | 360.8 | 133.0528 | 0.077771 | 132.5546 | 0.044059 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 2.3264 | 0.0058588 | 0.40844 | 0.080748 | 8.4462 | 0.00765
523 | 361 | 132.5658 | 0.077771 | 132.165 | 0.14633 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 1.742 | 0.0058588 | 0.40844 | 0.082371 | 8.154 | 0.00765
523.2 | 361.2 | 130.1309 | 0.076148 | 129.7301 | 0.52779 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 2.9108 | 0.0058588 | 0.40844 | 0.079125 | 9.2254 | 0.00765
523.4 | 361.4 | 132.1762 | 0.077771 | 131.8729 | 0.23561 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 1.8394 | 0.0058588 | 0.40844 | 0.080748 | 8.4462 | 0.00765
523.6 | 361.6 | 130.6178 | 0.076148 | 130.2171 | 0.44663 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 1.3524 | 0.0058588 | 0.40844 | 0.080748 | 8.7384 | 0.00765
523.8 | 361.8 | 132.9554 | 0.077771 | 132.652 | 0.096004 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 1.5472 | 0.0058588 | 0.40844 | 0.080748 | 9.0306 | 0.0092737
524 | 362 | 133.345 | 0.077771 | 132.9443 | 0.031073 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 1.1576 | 0.0058588 | 0.40844 | 0.082371 | 9.2254 | 0.00765
524.2 | 362.2 | 133.345 | 0.077771 | 133.0416 | 0.022956 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0031344 | 0.96284 | 0.0042351 | 0.40844 | 0.082371 | 9.2254 | 0.0092737
524.4 | 362.4 | 133.2476 | 0.077771 | 132.8468 | 0.042436 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 1.255 | 0.0058588 | 0.40844 | 0.082371 | 9.7123 | 0.00765
524.6 | 362.6 | 133.2476 | 0.077771 | 132.7495 | 0.065161 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 2.0342 | 0.0058588 | 0.40844 | 0.080748 | 9.9071 | 0.00765
524.8 | 362.8 | 133.345 | 0.077771 | 132.9443 | 0.035942 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 3.3004 | 0.0058588 | 0.31106 | 0.082371 | 9.5176 | 0.00765
525 | 363 | 133.2476 | 0.077771 | 132.8468 | 0.045682 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 6.5144 | 0.0074818 | 0.40844 | 0.080748 | 9.7123 | 0.00765
525.2 | 363.2 | 133.2476 | 0.077771 | 132.9443 | 0.044059 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 5.0535 | 0.013975 | 0.40844 | 0.080748 | 9.615 | 0.00765
525.4 | 363.4 | 133.2476 | 0.077771 | 132.8468 | 0.042436 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 4.0795 | 0.013975 | 0.31106 | 0.082371 | 9.615 | 0.00765
525.6 | 363.6 | 133.2476 | 0.077771 | 132.8468 | 0.042436 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 3.3978 | 0.017221 | 0.50586 | 0.082371 | 9.9071 | 0.00765
525.8 | 363.8 | 133.2476 | 0.077771 | 132.8468 | 0.039189 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 3.7874 | 0.017221 | 0.40844 | 0.080748 | 9.9071 | 0.00765
526 | 364 | 133.2476 | 0.077771 | 132.7495 | 0.037565 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 3.3978 | 0.017221 | 0.40844 | 0.082371 | 9.9071 | 0.0092737
526.2 | 364.2 | 132.858 | 0.077771 | 132.4573 | 0.086264 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 5.2483 | 0.017221 | 0.40844 | 0.082371 | 10.1993 | 0.00765
526.4 | 364.4 | 133.1502 | 0.077771 | 132.7495 | 0.052175 |  |  | 0.49069 | 0.0062856 | 0.37035 | 0.0047574 | 5.0535 | 0.023714 | 0.40844 | 0.082371 | 9.9071 | 0.00765
526.6 | 364.6 | 133.2476 | 0.077771 | 132.7495 | 0.052175 |  |  | 0.58807 | 0.0046619 | 0.37035 | 0.0031344 | 6.0275 | 0.028584 | 0.40844 | 0.082371 | 10.0046 | 0.00765
526.8 | 364.8 | 133.1502 | 0.077771 | 132.7495 | 0.055422 |  |  | 0.58807 | 0.0046619 | 0.37035 | 0.0047574 | 7.1962 | 0.035078 | 0.40844 | 0.082371 | 10.6863 | 0.00765
527 | 365 | 133.1502 | 0.077771 | 132.7495 | 0.053798 |  |  | 0.58807 | 0.0046619 | 0.37035 | 0.0047574 | 7.391 | 0.033454 | 0.40844 | 0.080748 | 11.1733 | 0.00765
527.2 | 365.2 | 132.858 | 0.077771 | 132.5546 | 0.087887 |  |  | 0.68549 | 0.0046619 | 0.46777 | 0.0047574 | 8.852 | 0.049687 | 0.40844 | 0.082371 | 11.9525 | 0.00765
527.4 | 365.4 | 133.2476 | 0.079395 | 132.8468 | 0.060291 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0031344 | 5.3457 | 0.038324 | 0.40844 | 0.082371 | 11.6603 | 0.0092737
527.6 | 365.6 | 133.345 | 0.077771 | 132.9443 | 0.040812 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 3.3978 | 0.023714 | 0.40844 | 0.083995 | 11.5629 | 0.00765
527.8 | 365.8 | 133.4424 | 0.077771 | 132.9443 | 0.037565 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 2.9108 | 0.018845 | 0.40844 | 0.082371 | 11.4655 | 0.00765
528 | 366 | 133.345 | 0.077771 | 132.9443 | 0.032696 |  |  | 0.88025 | 0.0046619 | 0.46777 | 0.0047574 | 1.9368 | 0.013975 | 0.40844 | 0.082371 | 11.6603 | 0.00765
528.2 | 366.2 | 133.345 | 0.077771 | 132.9443 | 0.032696 |  |  | 0.88025 | 0.0046619 | 0.37035 | 0.0031344 | 1.742 | 0.012351 | 0.40844 | 0.082371 | 11.6603 | 0.00765
528.4 | 366.4 | 133.1502 | 0.077771 | 132.7495 | 0.042436 |  |  | 0.78287 | 0.0062856 | 0.37035 | 0.0047574 | 3.7874 | 0.010728 | 0.40844 | 0.082371 | 12.0499 | 0.00765
528.6 | 366.6 | 132.858 | 0.077771 | 132.4573 | 0.091134 |  |  | 0.88025 | 0.0046619 | 0.37035 | 0.0047574 | 12.1635 | 0.046441 | 0.40844 | 0.082371 | 12.7316 | 0.00765
528.8 | 366.8 | 132.9554 | 0.077771 | 132.5546 | 0.09925 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 12.7478 | 0.077282 | 0.31106 | 0.082371 | 12.5368 | 0.00765
529 | 367 | 132.4684 | 0.077771 | 132.0677 | 0.16418 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 19.0786 | 0.11462 | 0.40844 | 0.082371 | 13.9978 | 0.00765
529.2 | 367.2 | 131.884 | 0.077771 | 131.4833 | 0.26969 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 37.8761 | 0.23149 | 0.40844 | 0.082371 | 20.5233 | 0.0092737
529.4 | 367.4 | 132.858 | 0.077771 | 132.5546 | 0.12035 |  |  | 0.88025 | 0.0046619 | 0.37035 | 0.0047574 | 15.1827 | 0.10488 | 0.31106 | 0.082371 | 13.9978 | 0.00765
529.6 | 367.6 | 133.2476 | 0.077771 | 132.9443 | 0.058668 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 5.2483 | 0.041571 | 0.40844 | 0.082371 | 11.6603 | 0.00765
529.8 | 367.8 | 133.345 | 0.077771 | 132.9443 | 0.047305 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0031344 | 3.5926 | 0.025337 | 0.40844 | 0.082371 | 11.6603 | 0.00765
530 | 368 | 133.2476 | 0.077771 | 132.8468 | 0.063538 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 3.9821 | 0.022091 | 0.40844 | 0.082371 | 11.9525 | 0.00765
530.2 | 368.2 | 133.2476 | 0.077771 | 132.7495 | 0.078147 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 5.5405 | 0.026961 | 0.40844 | 0.082371 | 12.0499 | 0.00765
530.4 | 368.4 | 133.0528 | 0.079395 | 132.652 | 0.097627 |  |  | 0.78287 | 0.0062856 | 0.37035 | 0.0031344 | 7.0014 | 0.043194 | 0.40844 | 0.082371 | 12.4395 | 0.00765
530.6 | 368.6 | 133.1502 | 0.077771 | 132.7495 | 0.078147 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 6.0275 | 0.039947 | 0.31106 | 0.082371 | 12.0499 | 0.00765
530.8 | 368.8 | 133.0528 | 0.079395 | 132.652 | 0.086264 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 5.9301 | 0.038324 | 0.40844 | 0.082371 | 12.2447 | 0.00765
531 | 369 | 132.9554 | 0.079395 | 132.5546 | 0.12035 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 8.0728 | 0.048064 | 0.40844 | 0.082371 | 12.5368 | 0.0092737
531.2 | 369.2 | 133.1502 | 0.079395 | 132.7495 | 0.087887 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 8.2676 | 0.05131 | 0.40844 | 0.082371 | 12.342 | 0.00765
531.4 | 369.4 | 132.2736 | 0.079395 | 131.7755 | 0.19502 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 11.0921 | 0.067543 | 0.31106 | 0.082371 | 13.0238 | 0.00765
531.6 | 369.6 | 133.0528 | 0.079395 | 132.652 | 0.097627 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 6.5144 | 0.046441 | 0.40844 | 0.082371 | 12.342 | 0.00765
531.8 | 369.8 | 133.0528 | 0.079395 | 132.652 | 0.087887 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 7.391 | 0.043194 | 0.40844 | 0.082371 | 12.4395 | 0.00765
532 | 370 | 132.858 | 0.079395 | 132.4573 | 0.11224 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 11.6765 | 0.07079 | 0.31106 | 0.082371 | 12.9264 | 0.00765
532.2 | 370.2 | 133.1502 | 0.079395 | 132.7495 | 0.078147 |  |  | 0.78287 | 0.0046619 | 0.37035 | 0.0047574 | 5.6379 | 0.038324 | 0.40844 | 0.082371 | 12.5368 | 0.00765
532.4 | 370.4 | 132.9554 | 0.079395 | 132.5546 | 0.096004 |  |  | 0.78287 | 0.0062856 | 0.46777 | 0.0047574 | 3.3004 | 0.023714 | 0.40844 | 0.082371 | 12.1473 | 0.00765
532.6 | 370.6 | 132.371 | 0.079395 | 131.9703 | 0.22911 |  |  | 0.88025 | 0.0046619 | 0.46777 | 0.0047574 | 2.716 | 0.017221 | 0.40844 | 0.082371 | 12.1473 | 0.00765
532.8 | 370.8 | 132.1762 | 0.079395 | 131.7755 | 0.23398 |  |  | 0.88025 | 0.0046619 | 0.46777 | 0.0047574 | 3.0081 | 0.017221 | 0.40844 | 0.082371 | 12.2447 | 0.00765
533 | 371 | 132.4684 | 0.079395 | 132.0677 | 0.18853 |  |  | 0.88025 | 0.0062856 | 0.46777 | 0.0047574 | 6.2223 | 0.026961 | 0.31106 | 0.082371 | 12.9264 | 0.00765
533.2 | 371.2 | 132.1762 | 0.079395 | 131.7755 | 0.23398 |  |  | 0.97767 | 0.0046619 | 0.37035 | 0.0047574 | 4.6639 | 0.025337 | 0.40844 | 0.082371 | 12.7316 | 0.0092737
533.4 | 371.4 | 132.9554 | 0.079395 | 132.5546 | 0.10899 |  |  | 0.97767 | 0.0046619 | 0.37035 | 0.0047574 | 8.852 | 0.044817 | 0.40844 | 0.082371 | 13.4134 | 0.00765
533.6 | 371.6 | 132.858 | 0.079395 | 132.5546 | 0.12035 |  |  | 0.97767 | 0.0046619 | 0.37035 | 0.0047574 | 12.2608 | 0.039947 | 0.40844 | 0.083995 | 13.803 | 0.00765
533.8 | 371.8 | 132.858 | 0.079395 | 132.4573 | 0.1236 |  |  | 0.97767 | 0.0046619 | 0.37035 | 0.0031344 | 11.7739 | 0.080529 | 0.40844 | 0.083995 | 13.803 | 0.00765
534 | 372 | 132.2736 | 0.079395 | 131.8729 | 0.20314 |  |  | 0.88025 | 0.0046619 | 0.37035 | 0.0047574 | 17.8124 | 0.091892 | 0.40844 | 0.082371 | 15.5562 | 0.0092737
534.2 | 372.2 | 132.5658 | 0.077771 | 132.165 | 0.15444 |  |  | 0.88025 | 0.0062856 | 0.46777 | 0.0047574 | 14.5984 | 0.10001 | 0.40844 | 0.082371 | 14.4848 | 0.00765
534.4 | 372.4 | 132.1762 | 0.077771 | 131.7755 | 0.20963 |  |  | 0.88025 | 0.0046619 | 0.37035 | 0.0047574 | 8.1702 | 0.052933 | 0.50586 | 0.083995 | 13.4134 | 0.00765
534.6 | 372.6 | 125.748 | 0.074525 | 125.3473 | 1.2161 |  |  | 0.88025 | 0.0062856 | 0.27297 | 0.006381 | 28.2339 | 0.15195 | 0.21368 | 0.077501 | 19.6468 | 0.014143
534.8 | 372.8 | 123.8975 | 0.072901 | 123.4968 | 1.5488 |  |  | 1.0751 | 0.0046619 | 0.37035 | 0.0047574 | 12.1635 | 0.093516 | 0.40844 | 0.077501 | 14.4848 | 0.00765
535 | 373 | 127.7933 | 0.074525 | 127.3927 | 0.88167 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 10.2155 | 0.05131 | 0.40844 | 0.079125 | 15.264 | 0.00765
535.2 | 373.2 | 130.423 | 0.076148 | 130.1197 | 0.47098 |  |  | 1.1725 | 0.0062856 | 0.46777 | 0.0047574 | 19.0786 | 0.12436 | 0.31106 | 0.083995 | 20.1338 | 0.0092737
535.4 | 373.4 | 131.4944 | 0.076148 | 130.9963 | 0.33787 |  |  | 1.2699 | 0.0046619 | 0.37035 | 0.0047574 | 20.15 | 0.12598 | 0.40844 | 0.083995 | 20.6208 | 0.00765
535.6 | 373.6 | 131.7866 | 0.077771 | 131.3859 | 0.27781 |  |  | 1.2699 | 0.0046619 | 0.46777 | 0.0047574 | 19.5656 | 0.11137 | 0.40844 | 0.083995 | 20.9129 | 0.00765
535.8 | 373.8 | 131.7866 | 0.077771 | 131.4833 | 0.2632 |  |  | 1.3672 | 0.0046619 | 0.37035 | 0.0047574 | 16.8385 | 0.1065 | 0.40844 | 0.085618 | 21.7895 | 0.00765
536 | 374 | 131.4944 | 0.077771 | 131.0937 | 0.32164 |  |  | 1.4647 | 0.0046619 | 0.46777 | 0.0047574 | 20.15 | 0.10975 | 0.40844 | 0.083995 | 23.64 | 0.0092737
536.2 | 374.2 | 131.7866 | 0.077771 | 131.3859 | 0.30216 |  |  | 1.2699 | 0.0046619 | 0.37035 | 0.0031344 | 15.2801 | 0.10326 | 0.40844 | 0.082371 | 15.5562 | 0.00765
536.4 | 374.4 | 131.7866 | 0.076148 | 131.3859 | 0.2843 |  |  | 1.0751 | 0.0046619 | 0.46777 | 0.0047574 | 8.6572 | 0.054557 | 0.40844 | 0.082371 | 12.829 | 0.00765
536.6 | 374.6 | 130.423 | 0.077771 | 130.0224 | 0.49533 |  |  | 1.1725 | 0.0046619 | 0.46777 | 0.0047574 | 17.3254 | 0.082153 | 0.40844 | 0.082371 | 15.6535 | 0.00765
536.8 | 374.8 | 129.6439 | 0.076148 | 129.1458 | 0.6187 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 17.3254 | 0.10488 | 0.40844 | 0.082371 | 15.4587 | 0.00765
537 | 375 | 131.7866 | 0.077771 | 131.3859 | 0.28593 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 12.6504 | 0.078906 | 0.40844 | 0.082371 | 13.5108 | 0.00765
537.2 | 375.2 | 132.1762 | 0.077771 | 131.7755 | 0.21613 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 14.8905 | 0.093516 | 0.40844 | 0.082371 | 13.803 | 0.00765
537.4 | 375.4 | 132.371 | 0.077771 | 131.9703 | 0.20152 |  |  | 1.0751 | 0.0062856 | 0.46777 | 0.0047574 | 12.7478 | 0.080529 | 0.40844 | 0.083995 | 13.2186 | 0.006027
537.6 | 375.6 | 132.5658 | 0.079395 | 132.165 | 0.16256 |  |  | 1.0751 | 0.0046619 | 0.46777 | 0.0031344 | 16.2541 | 0.10001 | 0.40844 | 0.083995 | 14.0952 | 0.00765
537.8 | 375.8 | 132.4684 | 0.077771 | 132.0677 | 0.17067 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 13.8192 | 0.10001 | 0.50586 | 0.082371 | 13.5108 | 0.00765
538 | 376 | 131.6892 | 0.077771 | 131.1911 | 0.28755 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 14.8905 | 0.10326 | 0.40844 | 0.082371 | 14.29 | 0.00765
538.2 | 376.2 | 131.1048 | 0.077771 | 130.7041 | 0.37196 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 12.4556 | 0.088645 | 0.40844 | 0.083995 | 13.7056 | 0.00765
538.4 | 376.4 | 130.423 | 0.076148 | 130.0224 | 0.48234 |  |  | 1.1725 | 0.0046619 | 0.37035 | 0.0047574 | 13.9166 | 0.088645 | 0.40844 | 0.083995 | 14.29 | 0.0092737
538.6 | 376.6 | 131.0074 | 0.077771 | 130.6067 | 0.39144 |  |  | 1.2699 | 0.0046619 | 0.37035 | 0.0031344 | 15.3775 | 0.096762 | 0.40844 | 0.083995 | 17.6015 | 0.00765
538.8 | 376.8 | 130.5205 | 0.077771 | 130.1197 | 0.48559 |  |  | 1.4647 | 0.0046619 | 0.37035 | 0.0047574 | 21.6109 | 0.13734 | 0.40844 | 0.083995 | 20.3286 | 0.00765
539 | 377 | 129.6439 | 0.076148 | 129.3406 | 0.60409 |  |  | 1.562 | 0.0046619 | 0.37035 | 0.0047574 | 15.3775 | 0.10001 | 0.40844 | 0.083995 | 18.3807 | 0.006027
539.2 | 377.2 | 126.5272 | 0.074525 | 126.0291 | 1.0894 |  |  | 1.6595 | 0.0046619 | 0.46777 | 0.0047574 | 25.8964 | 0.16007 | 0.40844 | 0.083995 | 21.9843 | 0.00765
539.4 | 377.4 | 130.3257 | 0.076148 | 129.9249 | 0.50669 |  |  | 1.6595 | 0.0046619 | 0.37035 | 0.0047574 | 19.663 | 0.13085 | 0.40844 | 0.083995 | 20.2312 | 0.00765
539.6 | 377.6 | 131.6892 | 0.077771 | 131.3859 | 0.28268 |  |  | 1.6595 | 0.0046619 | 0.37035 | 0.0047574 | 21.9031 | 0.1552 | 0.40844 | 0.085618 | 21.4973 | 0.00765
539.8 | 377.8 | 132.1762 | 0.077771 | 131.7755 | 0.22262 |  |  | 1.6595 | 0.0046619 | 0.37035 | 0.0047574 | 21.5135 | 0.15033 | 0.40844 | 0.085618 | 21.4973 | 0.0092737
540 | 378 | 131.9814 | 0.077771 | 131.5807 | 0.24534 |  |  | 1.6595 | 0.0046619 | 0.46777 | 0.0047574 | 19.663 | 0.13734 | 0.40844 | 0.085618 | 22.1791 | 0.0092737
540.2 | 378.2 | 131.884 | 0.077771 | 131.4833 | 0.26807 |  |  | 1.6595 | 0.0046619 | 0.37035 | 0.0047574 | 22.4875 | 0.15845 | 0.40844 | 0.087241 | 24.4192 | 0.0092737
540.4 | 378.4 | 131.397 | 0.076148 | 130.8989 | 0.35248 |  |  | 1.9516 | 0.0046619 | 0.37035 | 0.0047574 | 30.7662 | 0.20065 | 0.40844 | 0.087241 | 28.4125 | 0.00765
540.6 | 378.6 | 131.397 | 0.077771 | 131.0937 | 0.35086 |  |  | 2.049 | 0.0046619 | 0.46777 | 0.0047574 | 33.4933 | 0.225 | 0.40844 | 0.087241 | 29.776 | 0.00765
540.8 | 378.8 | 131.6892 | 0.076148 | 131.2885 | 0.31352 |  |  | 1.9516 | 0.0046619 | 0.37035 | 0.0047574 | 31.5453 | 0.21201 | 0.40844 | 0.087241 | 29.8734 | 0.00765
541 | 379 | 131.6892 | 0.077771 | 131.1911 | 0.30865 |  |  | 2.1464 | 0.0046619 | 0.37035 | 0.006381 | 30.0844 | 0.21201 | 0.40844 | 0.088864 | 31.237 | 0.00765
541.2 | 379.2 | 131.2996 | 0.077771 | 130.8989 | 0.35735 |  |  | 2.1464 | 0.0046619 | 0.46777 | 0.0047574 | 33.9803 | 0.23474 | 0.40844 | 0.088864 | 34.0615 | 0.00765
541.4 | 379.4 | 131.2022 | 0.077771 | 130.8989 | 0.36871 |  |  | 2.1464 | 0.0046619 | 0.37035 | 0.0031344 | 37.1943 | 0.26234 | 0.40844 | 0.090487 | 36.0094 | 0.0092737
541.6 | 379.6 | 130.423 | 0.077771 | 130.0224 | 0.47585 |  |  | 2.4386 | 0.0046619 | 0.37035 | 0.0047574 | 39.6293 | 0.28344 | 0.40844 | 0.090487 | 38.7365 | 0.0092737
541.8 | 379.8 | 128.8647 | 0.076148 | 128.3666 | 0.75343 |  |  | 2.3412 | 0.0046619 | 0.46777 | 0.0031344 | 35.8308 | 0.26721 | 0.40844 | 0.087241 | 30.3604 | 0.00765
542 | 380 | 129.8387 | 0.077771 | 129.438 | 0.57 |  |  | 2.1464 | 0.0046619 | 0.37035 | 0.0047574 | 42.259 | 0.30129 | 0.40844 | 0.085618 | 28.1203 | 0.00765
542.2 | 380.2 | 130.2283 | 0.076148 | 129.8276 | 0.52617 |  |  | 2.049 | 0.0030389 | 0.46777 | 0.0031344 | 47.7132 | 0.33701 | 0.40844 | 0.085618 | 29.4839 | 0.00765
542.4 | 380.4 | 129.9361 | 0.079395 | 129.6328 | 0.55701 |  |  | 2.4386 | 0.0046619 | 0.46777 | 0.006381 | 54.6283 | 0.38408 | 0.50586 | 0.087241 | 36.9834 | 0.006027
542.6 | 380.6 | 129.3517 | 0.076148 | 128.951 | 0.66577 |  |  | 2.7308 | 0.0079086 | 0.37035 | 0.0031344 | 55.3101 | 0.39869 | 0.50586 | 0.087241 | 36.7886 | 0.0092737
542.8 | 380.8 | 130.423 | 0.076148 | 130.0224 | 0.48559 |  |  | 2.536 | 0.0046619 | 0.46777 | 0.0047574 | 49.2715 | 0.34999 | 0.40844 | 0.085618 | 28.9969 | 0.0092737
543 | 381 | 129.1569 | 0.076148 | 128.6588 | 0.64142 |  |  | 2.3412 | 0.0046619 | 0.46777 | 0.0047574 | 39.7267 | 0.27208 | 0.40844 | 0.083995 | 22.9583 | 0.00765
543.2 | 381.2 | 89.9061 | 0.056668 | 88.7262 | 5.4009 |  |  | 2.1464 | 0.0046619 | 0.46777 | 0.0047574 | 13.8192 | 0.11624 | 0.40844 | 0.066138 | 22.0817 | 0.00765
543.4 | 381.4 | 18.417 | 0.030696 | 17.1398 | 1.2161 |  |  | 1.3672 | 0.0046619 | 0.46777 | 0.0047574 | 3.9821 | 0.043194 | 0.40844 | 0.033673 | 5.6217 | 0.00765
543.6 | 381.6 | 3.6128 | 0.016087 | 3.2121 | 0.10412 |  |  | 0.88025 | 0.0046619 | 0.46777 | 0.0047574 | 1.3524 | 0.018845 | 0.40844 | 0.019064 | 1.6285 | 0.0092737
543.8 | 381.8 | 1.5675 | 0.011217 | 1.5563 | 0.029449 |  |  | 0.78287 | 0.0046619 | 0.46777 | 0.0047574 | 0.86542 | 0.012351 | 0.40844 | 0.01257 | 0.94667 | 0.0092737
544 | 382 | 1.1779 | 0.0095933 | 1.0694 | 0.016463 |  |  | 0.68549 | 0.0046619 | 0.46777 | 0.0031344 | 0.67066 | 0.0091048 | 0.40844 | 0.010947 | 0.75187 | 0.00765
545 | 383 | 0.7883 | 0.0079703 | 0.67976 | 0.0083466 |  |  | 0.49069 | 0.0030389 | 0.46777 | 0.0047574 | 0.37844 | 0.0074818 | 0.40844 | 0.0093238 | 0.45969 | 0.00765
546 | 384 | 0.69088 | 0.0063473 | 0.58238 | 0.0067236 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.0077008 | 0.45969 | 0.00765
547 | 385 | 0.5935 | 0.0063473 | 0.58238 | 0.0067236 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.0077008 | 0.45969 | 0.00765
548 | 386 | 0.5935 | 0.0063473 | 0.48496 | 0.0050999 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.0077008 | 0.36227 | 0.00765
549 | 387 | 0.5935 | 0.0047237 | 0.48496 | 0.0050999 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0031344 | 0.28106 | 0.0058588 | 0.40844 | 0.0060771 | 0.45969 | 0.00765
550 | 388 | 0.5935 | 0.0047237 | 0.48496 | 0.0067236 |  |  | 0.49069 | 0.0046619 | 0.46777 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.0060771 | 0.36227 | 0.00765
560 | 398 | 0.49608 | 0.0047237 | 0.38758 | 0.0050999 |  |  | 0.49069 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0042351 | 0.40844 | 0.0077008 | 0.36227 | 0.00765
570 | 408 | 0.49608 | 0.0047237 | 0.48496 | 0.0050999 |  |  | 0.39327 | 0.0046619 | 0.46777 | 0.0031344 | 0.18368 | 0.0042351 | 0.40844 | 0.0077008 | 0.36227 | 0.00765
600 | 438 | 0.49608 | 0.0063473 | 0.38758 | 0.0050999 |  |  | 0.39327 | 0.0046619 | 0.37035 | 0.0047574 | 0.28106 | 0.0058588 | 0.40844 | 0.0060771 | 0.36227 | 0.00765

## Circuit 4 Faulting
Summary of Observed Faulting Behavior for Circuit #4
DAQ Time | Burner Time | Event | Discussion
423 | 261 | Signs of degradation | Initial signs of cable degradation are noted based on an increas in the voltage on circuit path 6.
426 | 264 | Spurious Actuation Path 6 | Circuit Path 6 experiences a hot short and relay lock-in
427 | 265 | Spurious Actuation Path 5 | Circuit Path 5 experiences a hot short and relay lock-in
430 | 268 | Drop-out of Path 6 relay | The spurious operation of Path 6 self-mitigates and relay drops out (after approximately 4 s).
435 | 273 | Drop-out of Path 5 relay | The spurious operation of Path 5 self-mitigates and relay drops out (after approximately 8 s).
440 | 278 | Spurious Actuation Path 5 | The relay on Path 5 re-engages for a second time.
442 | 280 | Fuse blow | A short to ground and fuse blow occurs.
Summary Observations |  | This circuit was configured using the MOV-1 wiring scheme. The circuit experienced one spurious operation of one relay, and two spurious operations of the second relay. The total duration of the SA signals was about 16 s. Some degradation of the supply voltage is noted, but at worst, voltage drops by about 20 V.

## Converted Data C4
DAQ Time | Burner Time | C4 V1 | C4 A1 | C4 V2 | C4 A2 | C4 V3 | C4 A3 | C4 V4 | C4 A4 | C4 V5 | C4 A5 | C4 V6 | C4 A6 | C4 V7 | C4 A7 | C4 V8 | C4 A8
0 | -162 | 128.0869 | 0.087533 | 128.0606 | 0.0074705 |  |  | 0.20121 | 0.0027911 | 0.3569 | 0.0027749 | 0.40375 | -0.00034817 | 0.41993 | 0.076243 | 2.2961 | 0.0045103
30 | -132 | 128.3791 | 0.082664 | 128.3528 | 0.0042238 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.30633 | -0.00034817 | 0.32251 | 0.07462 | 2.2961 | 0.0045103
60 | -102 | 128.1843 | 0.084287 | 128.158 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0027749 | 0.30633 | 0.0012748 | 0.41993 | 0.07462 | 2.2961 | 0.0045103
90 | -72 | 128.4765 | 0.082664 | 128.5476 | 0.0042238 |  |  | 0.20121 | 0.0044148 | 0.3569 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.07462 | 2.2961 | 0.0028873
120 | -42 | 128.4765 | 0.08104 | 128.5476 | 0.0042238 |  |  | 0.20121 | 0.0027911 | 0.45428 | 0.0027749 | 0.30633 | 0.0012748 | 0.32251 | 0.07462 | 2.2961 | 0.0028873
150 | -12 | 128.4765 | 0.084287 | 128.5476 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 2.3935 | 0.0061333
180 | 18 | 128.7686 | 0.082664 | 128.7424 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.30633 | 0.0012748 | 0.41993 | 0.076243 | 2.2961 | 0.0045103
210 | 48 | 128.5738 | 0.092403 | 128.5476 | 0.010717 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0027749 | 0.40375 | -0.00034817 | 0.32251 | 0.076243 | 2.3935 | 0.0028873
240 | 78 | 128.6713 | 0.09078 | 128.7424 | 0.0090935 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.51731 | 0.076243 | 2.3935 | 0.0045103
270 | 108 | 129.2556 | 0.082664 | 129.2293 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 2.2961 | 0.0045103
300 | 138 | 128.6713 | 0.087533 | 128.7424 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 2.3935 | 0.0045103
330 | 168 | 128.5738 | 0.09565 | 128.9372 | 0.013963 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0045215 | 0.41993 | 0.077866 | 2.3935 | 0.0061333
360 | 198 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.50113 | 0.0028978 | 0.51731 | 0.077866 | 2.4908 | 0.0061333
390 | 228 | 128.7686 | 0.089157 | 128.7424 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 5.218 | 0.0045103
390.2 | 228.2 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 5.218 | 0.0045103
390.4 | 228.4 | 128.8661 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.3569 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.3153 | 0.0045103
390.6 | 228.6 | 128.9634 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 5.3153 | 0.0061333
390.8 | 228.8 | 128.8661 | 0.089157 | 128.9372 | 0.0042238 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.4128 | 0.0045103
391 | 229 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.5101 | 0.0061333
391.2 | 229.2 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 5.5101 | 0.0045103
391.4 | 229.4 | 128.7686 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.30633 | 0.0028978 | 0.41993 | 0.076243 | 5.5101 | 0.0045103
391.6 | 229.6 | 128.7686 | 0.089157 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.4128 | 0.0045103
391.8 | 229.8 | 128.8661 | 0.089157 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 5.5101 | 0.0061333
392 | 230 | 128.7686 | 0.089157 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 5.4128 | 0.0045103
392.2 | 230.2 | 128.7686 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 5.4128 | 0.0061333
392.4 | 230.4 | 128.7686 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.5101 | 0.0045103
392.6 | 230.6 | 128.7686 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 5.5101 | 0.0045103
392.8 | 230.8 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 5.5101 | 0.0045103
393 | 231 | 128.7686 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.6075 | 0.0061333
393.2 | 231.2 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 5.8023 | 0.0045103
393.4 | 231.4 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 5.8023 | 0.0045103
393.6 | 231.6 | 128.8661 | 0.089157 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.32251 | 0.076243 | 5.8023 | 0.0045103
393.8 | 231.8 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 5.6075 | 0.0061333
394 | 232 | 128.8661 | 0.087533 | 128.7424 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.7049 | 0.0045103
394.2 | 232.2 | 128.8661 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.7049 | 0.0045103
394.4 | 232.4 | 128.7686 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.6075 | 0.0045103
394.6 | 232.6 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.7049 | 0.0045103
394.8 | 232.8 | 128.8661 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.7049 | 0.0061333
395 | 233 | 128.8661 | 0.089157 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.7049 | 0.0061333
395.2 | 233.2 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.7049 | 0.0045103
395.4 | 233.4 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.50113 | 0.0028978 | 0.51731 | 0.076243 | 5.8023 | 0.0045103
395.6 | 233.6 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.8997 | 0.0045103
395.8 | 233.8 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 5.8997 | 0.0045103
396 | 234 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 5.9971 | 0.0045103
396.2 | 234.2 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.0945 | 0.0045103
396.4 | 234.4 | 128.8661 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 5.9971 | 0.0061333
396.6 | 234.6 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 6.0945 | 0.0061333
396.8 | 234.8 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.0945 | 0.0045103
397 | 235 | 128.9634 | 0.089157 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 6.1919 | 0.0061333
397.2 | 235.2 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0027749 | 0.30633 | 0.0012748 | 0.41993 | 0.076243 | 6.1919 | 0.0045103
397.4 | 235.4 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 6.2893 | 0.0045103
397.6 | 235.6 | 128.8661 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 6.3867 | 0.0045103
397.8 | 235.8 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 6.5815 | 0.0045103
398 | 236 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 6.4841 | 0.0061333
398.2 | 236.2 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.4841 | 0.0061333
398.4 | 236.4 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.5815 | 0.0045103
398.6 | 236.6 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.3867 | 0.0045103
398.8 | 236.8 | 129.0608 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 6.4841 | 0.0045103
399 | 237 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 6.2893 | 0.0045103
399.2 | 237.2 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 6.4841 | 0.0045103
399.4 | 237.4 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.50113 | 0.0028978 | 0.41993 | 0.077866 | 6.5815 | 0.0045103
399.6 | 237.6 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.3569 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.077866 | 6.5815 | 0.0045103
399.8 | 237.8 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.5815 | 0.0045103
400 | 238 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.49339 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 6.7763 | 0.0045103
400.2 | 238.2 | 128.8661 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 6.7763 | 0.0045103
400.4 | 238.4 | 128.9634 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.081113 | 6.7763 | 0.0061333
400.6 | 238.6 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 6.6789 | 0.0045103
400.8 | 238.8 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 6.7763 | 0.0045103
401 | 239 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0076446 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 6.8737 | 0.0045103
401.2 | 239.2 | 128.8661 | 0.08591 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0060216 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 6.9711 | 0.0045103
401.4 | 239.4 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.0685 | 0.0045103
401.6 | 239.6 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 7.0685 | 0.0045103
401.8 | 239.8 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.51731 | 0.077866 | 7.0685 | 0.0045103
402 | 240 | 128.8661 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.3569 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.077866 | 7.0685 | 0.0061333
402.2 | 240.2 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 6.9711 | 0.0045103
402.4 | 240.4 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 6.9711 | 0.0045103
402.6 | 240.6 | 128.8661 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.0685 | 0.0045103
402.8 | 240.8 | 128.8661 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.0685 | 0.0045103
403 | 241 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.1659 | 0.0045103
403.2 | 241.2 | 128.9634 | 0.087533 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 7.0685 | 0.0045103
403.4 | 241.4 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 6.9711 | 0.0061333
403.6 | 241.6 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 7.0685 | 0.0045103
403.8 | 241.8 | 128.9634 | 0.087533 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 7.0685 | 0.0045103
404 | 242 | 128.8661 | 0.087533 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0060216 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 7.1659 | 0.0045103
404.2 | 242.2 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.1659 | 0.0045103
404.4 | 242.4 | 128.9634 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.1659 | 0.0045103
404.6 | 242.6 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 7.3607 | 0.0045103
404.8 | 242.8 | 128.8661 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 7.2633 | 0.0061333
405 | 243 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.2633 | 0.0061333
405.2 | 243.2 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.077866 | 7.3607 | 0.0045103
405.4 | 243.4 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
405.6 | 243.6 | 128.8661 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0028978 | 0.41993 | 0.077866 | 7.1659 | 0.0045103
405.8 | 243.8 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
406 | 244 | 128.8661 | 0.08591 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
406.2 | 244.2 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
406.4 | 244.4 | 128.9634 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
406.6 | 244.6 | 128.9634 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
406.8 | 244.8 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.7763 | 0.0045103
407 | 245 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 6.7763 | 0.0045103
407.2 | 245.2 | 128.8661 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 6.7763 | 0.0045103
407.4 | 245.4 | 128.8661 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.29859 | 0.0060378 | 0.3569 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 6.7763 | 0.0045103
407.6 | 245.6 | 128.9634 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.32251 | 0.077866 | 6.8737 | 0.0061333
407.8 | 245.8 | 128.8661 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 6.8737 | 0.0045103
408 | 246 | 128.8661 | 0.08591 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 6.9711 | 0.0045103
408.2 | 246.2 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 6.9711 | 0.0045103
408.4 | 246.4 | 128.8661 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.0685 | 0.0045103
408.6 | 246.6 | 128.9634 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.0685 | 0.0061333
408.8 | 246.8 | 128.9634 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0027749 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.0685 | 0.0061333
409 | 247 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.0685 | 0.0045103
409.2 | 247.2 | 128.9634 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.3569 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.1659 | 0.0045103
409.4 | 247.4 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 7.3607 | 0.0045103
409.6 | 247.6 | 128.9634 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 7.5555 | 0.0045103
409.8 | 247.8 | 128.9634 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
410 | 248 | 128.8661 | 0.08591 | 128.8398 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.6529 | 0.0045103
410.2 | 248.2 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.3569 | 0.0027749 | 0.40375 | 0.0028978 | 0.51731 | 0.076243 | 7.7503 | 0.0061333
410.4 | 248.4 | 129.0608 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.3569 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.6529 | 0.0045103
410.6 | 248.6 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 7.2633 | 0.0045103
410.8 | 248.8 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.076243 | 7.1659 | 0.0045103
411 | 249 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.2633 | 0.0045103
411.2 | 249.2 | 128.8661 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.3569 | 0.0043979 | 0.50113 | 0.0012748 | 0.41993 | 0.077866 | 7.3607 | 0.0045103
411.4 | 249.4 | 128.9634 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.3607 | 0.0061333
411.6 | 249.6 | 128.9634 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.4581 | 0.0045103
411.8 | 249.8 | 128.8661 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.3607 | 0.0045103
412 | 250 | 128.8661 | 0.08591 | 128.8398 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.30633 | 0.0028978 | 0.51731 | 0.077866 | 7.3607 | 0.0045103
412.2 | 250.2 | 128.9634 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.5555 | 0.0045103
412.4 | 250.4 | 128.9634 | 0.084287 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.4581 | 0.0045103
412.6 | 250.6 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0028978 | 0.41993 | 0.077866 | 7.4581 | 0.0045103
412.8 | 250.8 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 7.3607 | 0.0061333
413 | 251 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.3569 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.3607 | 0.0045103
413.2 | 251.2 | 128.9634 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.49339 | 0.0060378 | 0.3569 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.6529 | 0.0045103
413.4 | 251.4 | 128.9634 | 0.08591 | 129.0345 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 7.6529 | 0.0045103
413.6 | 251.6 | 128.9634 | 0.08591 | 129.0345 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.7503 | 0.0045103
413.8 | 251.8 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.076243 | 7.8477 | 0.0045103
414 | 252 | 128.8661 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 7.7503 | 0.0045103
414.2 | 252.2 | 128.9634 | 0.084287 | 128.9372 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 7.9451 | 0.0061333
414.4 | 252.4 | 128.8661 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.49339 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 8.1399 | 0.0045103
414.6 | 252.6 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 8.0424 | 0.0045103
414.8 | 252.8 | 128.9634 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 8.0424 | 0.0061333
415 | 253 | 128.8661 | 0.08591 | 128.9372 | 0.0074705 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.076243 | 8.1399 | 0.0061333
415.2 | 253.2 | 128.9634 | 0.08591 | 129.0345 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0092676 | 0.40375 | 0.0028978 | 0.41993 | 0.076243 | 9.6008 | 0.0045103
415.4 | 253.4 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0060216 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 9.9904 | 0.0045103
415.6 | 253.6 | 128.8661 | 0.08591 | 128.8398 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 9.6982 | 0.0045103
415.8 | 253.8 | 128.9634 | 0.08591 | 128.9372 | 0.0058469 |  |  | 0.49339 | 0.0044148 | 0.3569 | 0.0043979 | 0.30633 | 0.0012748 | 0.41993 | 0.077866 | 9.7956 | 0.0045103
416 | 254 | 128.7686 | 0.087533 | 128.8398 | 0.0074705 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 9.6008 | 0.0045103
416.2 | 254.2 | 128.8661 | 0.08591 | 128.9372 | 0.0090935 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 9.6982 | 0.0045103
416.4 | 254.4 | 128.8661 | 0.08591 | 128.8398 | 0.0090935 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 9.7956 | 0.0045103
416.6 | 254.6 | 128.8661 | 0.08591 | 128.8398 | 0.010717 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 9.6008 | 0.0045103
416.8 | 254.8 | 128.8661 | 0.08591 | 128.8398 | 0.010717 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 9.6008 | 0.0045103
417 | 255 | 128.8661 | 0.087533 | 128.8398 | 0.01234 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0027749 | 0.40375 | 0.0012748 | 0.51731 | 0.077866 | 9.5034 | 0.0045103
417.2 | 255.2 | 128.7686 | 0.08591 | 128.8398 | 0.01234 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.077866 | 9.5034 | 0.0045103
417.4 | 255.4 | 128.7686 | 0.08591 | 128.8398 | 0.013963 |  |  | 0.59077 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 9.3086 | 0.0045103
417.6 | 255.6 | 128.8661 | 0.087533 | 128.8398 | 0.015587 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.30633 | 0.0012748 | 0.51731 | 0.077866 | 9.2112 | 0.0061333
417.8 | 255.8 | 128.7686 | 0.08591 | 128.7424 | 0.015587 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.077866 | 9.0164 | 0.0045103
418 | 256 | 128.6713 | 0.087533 | 128.645 | 0.01721 |  |  | 0.59077 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.077866 | 9.0164 | 0.0045103
418.2 | 256.2 | 128.7686 | 0.087533 | 128.7424 | 0.018833 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.07949 | 9.1138 | 0.0045103
418.4 | 256.4 | 128.6713 | 0.087533 | 128.645 | 0.018833 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.50113 | 0.0028978 | 0.41993 | 0.077866 | 9.3086 | 0.0061333
418.6 | 256.6 | 128.6713 | 0.087533 | 128.7424 | 0.020457 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.69593 | 0.0028978 | 0.41993 | 0.077866 | 9.406 | 0.0045103
418.8 | 256.8 | 128.6713 | 0.087533 | 128.7424 | 0.02208 |  |  | 0.59077 | 0.0044148 | 0.45428 | 0.0043979 | 0.89073 | 0.0012748 | 0.51731 | 0.07949 | 9.6982 | 0.0061333
419 | 257 | 128.6713 | 0.087533 | 128.645 | 0.023703 |  |  | 0.49339 | 0.0044148 | 0.45428 | 0.0043979 | 1.0855 | 0.0028978 | 0.41993 | 0.07949 | 9.893 | 0.0045103
419.2 | 257.2 | 128.5738 | 0.089157 | 128.645 | 0.026949 |  |  | 0.59077 | 0.0044148 | 0.3569 | 0.0027749 | 1.1829 | 0.0028978 | 0.41993 | 0.07949 | 10.1852 | 0.0045103
419.4 | 257.4 | 128.5738 | 0.089157 | 128.645 | 0.030196 |  |  | 0.68819 | 0.0044148 | 0.5517 | 0.0043979 | 1.5725 | 0.0028978 | 0.41993 | 0.07949 | 11.2565 | 0.0045103
419.6 | 257.6 | 128.5738 | 0.087533 | 128.645 | 0.033443 |  |  | 0.68819 | 0.0060378 | 0.5517 | 0.0043979 | 1.9621 | 0.0012748 | 0.51731 | 0.07949 | 12.3279 | 0.0061333
419.8 | 257.8 | 128.5738 | 0.087533 | 128.645 | 0.038312 |  |  | 0.68819 | 0.0060378 | 0.7465 | 0.0043979 | 2.3517 | 0.0012748 | 0.41993 | 0.07949 | 12.7175 | 0.0045103
420 | 258 | 128.4765 | 0.089157 | 128.4502 | 0.043183 |  |  | 0.78557 | 0.0060378 | 0.84388 | 0.0076446 | 2.5465 | 0.0012748 | 0.41993 | 0.077866 | 13.3019 | 0.0045103
420.2 | 258.2 | 128.5738 | 0.089157 | 128.4502 | 0.044806 |  |  | 0.78557 | 0.0044148 | 1.0387 | 0.0060216 | 2.8387 | 0.0012748 | 0.51731 | 0.07949 | 13.5941 | 0.0045103
420.4 | 258.4 | 128.4765 | 0.087533 | 128.4502 | 0.049675 |  |  | 0.78557 | 0.0044148 | 1.3309 | 0.0043979 | 2.936 | 0.0028978 | 0.41993 | 0.081113 | 16.4185 | 0.0045103
420.6 | 258.6 | 128.4765 | 0.089157 | 128.4502 | 0.054545 |  |  | 0.88295 | 0.0044148 | 1.5257 | 0.0043979 | 3.1308 | 0.0012748 | 0.51731 | 0.07949 | 17.2951 | 0.0061333
420.8 | 258.8 | 128.3791 | 0.089157 | 128.4502 | 0.054545 |  |  | 0.88295 | 0.0044148 | 1.7205 | 0.0027749 | 3.2282 | 0.0012748 | 0.41993 | 0.07949 | 14.9576 | 0.0045103
421 | 259 | 128.3791 | 0.089157 | 128.4502 | 0.057792 |  |  | 0.88295 | 0.0044148 | 1.8178 | 0.0043979 | 3.423 | 0.0028978 | 0.51731 | 0.07949 | 14.8602 | 0.0045103
421.2 | 259.2 | 128.3791 | 0.089157 | 128.3528 | 0.059415 |  |  | 0.88295 | 0.0044148 | 1.8178 | 0.0043979 | 3.6178 | 0.0028978 | 0.41993 | 0.07949 | 15.1524 | 0.0061333
421.4 | 259.4 | 128.3791 | 0.089157 | 128.3528 | 0.062661 |  |  | 0.88295 | 0.0044148 | 1.9152 | 0.0043979 | 3.91 | 0.0045215 | 0.51731 | 0.081113 | 15.6394 | 0.0061333
421.6 | 259.6 | 128.3791 | 0.089157 | 128.4502 | 0.065908 |  |  | 0.98037 | 0.0060378 | 1.9152 | 0.0043979 | 4.0074 | 0.011014 | 0.41993 | 0.081113 | 16.6133 | 0.0045103
421.8 | 259.8 | 128.3791 | 0.089157 | 128.3528 | 0.065908 |  |  | 0.98037 | 0.0060378 | 1.9152 | 0.0043979 | 4.2022 | 0.020754 | 0.41993 | 0.07949 | 15.6394 | 0.0061333
422 | 260 | 128.1843 | 0.089157 | 128.2554 | 0.069155 |  |  | 0.98037 | 0.0060378 | 1.9152 | 0.0043979 | 4.397 | 0.028871 | 0.41993 | 0.081113 | 15.1524 | 0.0061333
422.2 | 260.2 | 128.2817 | 0.089157 | 128.2554 | 0.072401 |  |  | 1.0777 | 0.0060378 | 2.11 | 0.0043979 | 4.4944 | 0.030494 | 0.51731 | 0.07949 | 15.3472 | 0.0045103
422.4 | 260.4 | 128.2817 | 0.09078 | 128.2554 | 0.075648 |  |  | 1.0777 | 0.0044148 | 2.11 | 0.0043979 | 4.7866 | 0.032117 | 0.41993 | 0.07949 | 15.7368 | 0.0061333
422.6 | 260.6 | 128.1843 | 0.089157 | 128.2554 | 0.078894 |  |  | 1.1752 | 0.0044148 | 2.3048 | 0.0043979 | 4.9814 | 0.035364 | 0.51731 | 0.07949 | 16.4185 | 0.0061333
422.8 | 260.8 | 128.1843 | 0.087533 | 128.2554 | 0.082141 |  |  | 1.2725 | 0.0076615 | 2.4996 | 0.0043979 | 5.1761 | 0.036987 | 0.51731 | 0.081113 | 16.7108 | 0.0045103
423 | 261 | 128.2817 | 0.089157 | 128.2554 | 0.085387 |  |  | 1.1752 | 0.0060378 | 2.597 | 0.0043979 | 5.4684 | 0.040234 | 0.41993 | 0.081113 | 16.516 | 0.0045103
423.2 | 261.2 | 128.0869 | 0.089157 | 128.158 | 0.090257 |  |  | 1.2725 | 0.0044148 | 2.9866 | 0.0060216 | 5.6632 | 0.04348 | 0.41993 | 0.081113 | 16.3212 | 0.0045103
423.4 | 261.4 | 127.8921 | 0.089157 | 127.9632 | 0.11136 |  |  | 1.2725 | 0.0060378 | 3.084 | 0.012514 | 8.6824 | 0.062959 | 0.41993 | 0.07949 | 12.0357 | 0.0045103
423.6 | 261.6 | 127.5999 | 0.089157 | 127.671 | 0.15194 |  |  | 1.1752 | 0.0044148 | 2.9866 | 0.017384 | 13.8445 | 0.10679 | 0.41993 | 0.077866 | 12.3279 | 0.0045103
423.8 | 261.8 | 127.9895 | 0.087533 | 127.9632 | 0.1211 |  |  | 1.0777 | 0.0044148 | 2.9866 | 0.020631 | 11.02 | 0.087309 | 0.51731 | 0.07949 | 8.8216 | 0.0045103
424 | 262 | 128.0869 | 0.089157 | 128.158 | 0.091881 |  |  | 0.98037 | 0.0044148 | 2.8892 | 0.022254 | 7.8059 | 0.049973 | 0.51731 | 0.077866 | 6.8737 | 0.007757
424.2 | 262.2 | 127.7947 | 0.087533 | 128.2554 | 0.075648 |  |  | 1.0777 | 0.0044148 | 4.1554 | 0.023877 | 5.1761 | 0.03374 | 0.32251 | 0.08436 | 5.8023 | 0.0061333
424.4 | 262.4 | 127.5999 | 0.094027 | 127.5736 | 0.13084 |  |  | 1.7595 | 0.012531 | 13.0185 | 0.061212 | 7.5137 | 0.058089 | 0.61469 | 0.082736 | 6.4841 | 0.0045103
424.6 | 262.6 | 127.6973 | 0.084287 | 128.4502 | 0.12922 |  |  | 2.3439 | -0.0085712 | 9.22 | 0.072575 | 8.4876 | 0.040234 | 0.12771 | 0.072997 | 7.1659 | 0.01425
424.8 | 262.8 | 127.5999 | 0.089157 | 127.671 | 0.14383 |  |  | 1.5647 | 0.0060378 | 7.6616 | 0.04498 | 11.02 | 0.077569 | 0.41993 | 0.07949 | 8.7242 | 0.0045103
425 | 263 | 127.2103 | 0.089157 | 127.184 | 0.20876 |  |  | 1.7595 | 0.0044148 | 7.1746 | 0.041734 | 17.2533 | 0.13438 | 0.41993 | 0.07949 | 12.9123 | 0.0045103
425.2 | 263.2 | 126.1389 | 0.074547 | 126.0153 | 0.32888 |  |  | 2.0517 | 0.0092845 | 9.9992 | 0.17809 | 32.2524 | 0.24152 | 0.51731 | 0.082736 | 18.5613 | 0.015873
425.4 | 263.4 | 125.9441 | 0.089157 | 125.9178 | 0.36134 |  |  | 2.3439 | 0.015778 | 11.6549 | 0.11153 | 37.6092 | 0.23178 | 0.71211 | 0.076243 | 21.2884 | 0.007757
425.6 | 263.6 | 125.7494 | 0.087533 | 125.7231 | 0.38732 |  |  | 2.2465 | 0.0060378 | 8.246 | 0.066083 | 44.8166 | 0.28372 | 0.41993 | 0.082736 | 25.5738 | 0.0061333
425.8 | 263.8 | 124.5806 | 0.089157 | 124.5543 | 0.52529 |  |  | 2.7335 | 0.0060378 | 15.0638 | 0.12614 | 56.0172 | 0.35677 | 0.71211 | 0.082736 | 28.0088 | 0.007757
426 | 264 | 123.5092 | 0.074547 | 123.6777 | 0.63892 |  |  | 3.9996 | 0.0076615 | 24.9982 | 0.21218 | 66.536 | 0.373 | 0.61469 | 0.08436 | 28.3009 | 0.0045103
426.2 | 264.2 | 125.7494 | 0.08591 | 125.9178 | 0.37433 |  |  | 4.9736 | 0.0060378 | 28.6993 | 0.21867 | 112.4098 | 0.1214 | 0.51731 | 0.08436 | 38.8198 | 0.0061333
426.4 | 264.4 | 125.5546 | 0.063184 | 125.7231 | 0.41329 |  |  | 4.8762 | 0.0092845 | 34.7379 | 0.22192 | 115.0395 | 0.082438 | 0.61469 | 0.085983 | 40.6703 | -0.0036061
426.6 | 264.6 | 124.678 | 0.08591 | 124.6517 | 0.50257 |  |  | 8.7721 | 0.0044148 | 52.8536 | 0.35016 | 115.916 | 0.079192 | 0.51731 | 0.07462 | 45.5401 | -0.0068528
426.8 | 264.8 | 126.4311 | 0.087533 | 126.3074 | 0.32076 |  |  | 19.5831 | 0.0060378 | 110.1228 | 0.12939 | 114.4551 | 0.080815 | 0.41993 | 0.092476 | 47.975 | 0.0061333
427 | 265 | 126.1389 | 0.087533 | 126.1126 | 0.34349 |  |  | 22.6998 | 0.0044148 | 117.5249 | 0.085562 | 110.4618 | 0.075946 | 0.41993 | 0.092476 | 47.3907 | 0.0045103
427.2 | 265.2 | 125.8468 | 0.08591 | 125.9178 | 0.36946 |  |  | 23.8685 | 0.0044148 | 118.1093 | 0.082315 | 109.1956 | 0.074322 | 0.41993 | 0.092476 | 47.975 | 0.0061333
427.4 | 265.4 | 126.6259 | 0.087533 | 126.697 | 0.29966 |  |  | 25.1347 | 0.0060378 | 118.9859 | 0.080692 | 115.0395 | 0.084062 | 0.41993 | 0.095723 | 50.5074 | 0.0045103
427.6 | 265.6 | 125.652 | 0.089157 | 125.7231 | 0.39706 |  |  | 26.2061 | 0.0060378 | 118.3041 | 0.080692 | 107.2477 | 0.072699 | 0.41993 | 0.094099 | 47.2932 | 0.0061333
427.8 | 265.8 | 125.0676 | 0.08591 | 124.9439 | 0.47984 |  |  | 27.4722 | 0.0060378 | 118.3041 | 0.079069 | 102.0857 | 0.067829 | 0.51731 | 0.094099 | 44.4687 | 0.0045103
428 | 266 | 123.9962 | 0.08591 | 123.9699 | 0.58211 |  |  | 29.1279 | 0.0044148 | 117.3301 | 0.082315 | 97.7028 | 0.064583 | 0.51731 | 0.097346 | 51.2865 | 0.0061333
428.2 | 266.2 | 123.1197 | 0.08591 | 123.0934 | 0.69412 |  |  | 30.6863 | 0.0060378 | 116.4536 | 0.080692 | 96.2419 | 0.061336 | 0.51731 | 0.10384 | 59.0782 | 0.0061333
428.4 | 266.4 | 121.8535 | 0.084287 | 121.8272 | 0.83534 |  |  | 31.3681 | 0.0060378 | 115.2848 | 0.079069 | 95.5601 | 0.061336 | 0.41993 | 0.10384 | 59.8574 | 0.0045103
428.6 | 266.6 | 120.49 | 0.082664 | 120.561 | 1.0025 |  |  | 31.2707 | 0.0060378 | 113.8238 | 0.077445 | 97.5081 | 0.059713 | 0.41993 | 0.10709 | 63.3637 | 0.0061333
428.8 | 266.8 | 122.0483 | 0.084287 | 122.022 | 0.83209 |  |  | 32.829 | 0.0060378 | 115.4796 | 0.079069 | 106.9555 | 0.071075 | 0.51731 | 0.11033 | 68.9153 | 0.0061333
429 | 267 | 125.0676 | 0.084287 | 125.0413 | 0.47173 |  |  | 35.1665 | 0.0044148 | 118.4989 | 0.080692 | 117.6692 | 0.082438 | 0.51731 | 0.12007 | 77.681 | 0.0061333
429.2 | 267.2 | 125.9441 | 0.087533 | 125.9178 | 0.36946 |  |  | 35.9457 | 0.0060378 | 119.1807 | 0.082315 | 120.6884 | 0.085685 | 0.51731 | 0.17851 | 77.2914 | 0.0061333
429.4 | 267.4 | 123.8988 | 0.08591 | 123.9699 | 0.58373 |  |  | 36.4327 | 0.0044148 | 116.9405 | 0.080692 | 113.8707 | 0.080815 | 0.41993 | 0.43986 | 72.1294 | 0.0028873
429.6 | 267.6 | 122.0483 | 0.08104 | 122.1194 | 0.8256 |  |  | 36.2379 | 0.0060378 | 114.7978 | 0.082315 | 108.1243 | 0.071075 | 0.41993 | 0.66874 | 72.3242 | 0.0061333
429.8 | 267.8 | 123.5092 | 0.087533 | 123.4829 | 0.65353 |  |  | 37.3093 | 0.0044148 | 115.7718 | 0.077445 | 113.4811 | 0.077569 | 0.41993 | 0.50966 | 80.1159 | 0.0061333
430 | 268 | 119.6134 | 0.084287 | 119.6845 | 1.0886 |  |  | 37.3093 | 0.0044148 | 111.6811 | 0.075822 | 103.4492 | 0.069452 | 0.51731 | 0.97391 | 69.8892 | 0.007757
430.2 | 268.2 | 117.2758 | 0.074547 | 117.6392 | 1.3613 |  |  | 36.4327 | 0.0060378 | 108.8567 | 0.077445 | 98.3846 | 0.058089 | 0.030326 | 1.2612 | 75.733 | -0.0003594
430.4 | 268.4 | 112.6982 | 0.077794 | 112.7693 | 1.9018 |  |  | 35.6535 | 0.0060378 | 104.5712 | 0.070952 | 92.833 | 0.058089 | 0.41993 | 1.8099 | 68.6231 | 0.0061333
430.6 | 268.6 | 111.8217 | 0.077794 | 111.7954 | 2.0333 |  |  | 34.3874 | 0.0044148 | 102.0389 | 0.064459 | 71.4058 | 0.074322 | 0.32251 | 1.9252 | 50.9943 | 0.0061333
430.8 | 268.8 | 112.0164 | 0.071301 | 112.3797 | 1.9522 |  |  | 33.9978 | 0.0076615 | 100.5779 | 0.059589 | 66.2438 | 0.10841 | 0.22513 | 1.844 | 50.2151 | 0.007757
431 | 269 | 111.9191 | 0.07617 | 111.7954 | 2.0073 |  |  | 34.1926 | 0.0044148 | 99.2144 | 0.066083 | 62.7375 | 0.28697 | 0.71211 | 1.8196 | 50.2151 | 0.0045103
431.2 | 269.2 | 109.7763 | 0.074547 | 109.4579 | 2.2865 |  |  | 33.1212 | 0.0027911 | 96.7795 | 0.061212 | 59.426 | 0.32918 | 0.71211 | 2.1005 | 45.6375 | -0.0003594
431.4 | 269.4 | 108.218 | 0.069678 | 108.0943 | 2.3775 |  |  | 33.0238 | 0.0092845 | 95.3185 | 0.061212 | 61.1792 | 0.43469 | 0.030326 | 2.0988 | 47.975 | 0.007757
431.6 | 269.6 | 108.4128 | 0.072924 | 108.4839 | 2.4197 |  |  | 32.9264 | 0.0060378 | 94.4419 | 0.059589 | 61.6661 | 0.43307 | 0.51731 | 2.1086 | 50.0204 | 0.0061333
431.8 | 269.8 | 110.7503 | 0.068054 | 110.8214 | 2.134 |  |  | 33.803 | 0.0060378 | 96.3899 | 0.056343 | 58.7443 | 0.41196 | 0.51731 | 1.8521 | 49.5334 | 0.0045103
432 | 270 | 117.8602 | 0.074547 | 118.0288 | 1.1925 |  |  | 36.3353 | 0.0060378 | 108.2722 | 0.05472 | 37.4144 | 0.22042 | 0.22513 | 1.0096 | 32.489 | 0.007757
432.2 | 270.2 | 120.2952 | 0.08104 | 120.2689 | 0.98793 |  |  | 37.7962 | 0.0060378 | 109.3436 | 0.070952 | 32.7394 | 0.21879 | 0.41993 | 0.82457 | 29.1775 | 0.0045103
432.4 | 270.4 | 126.4311 | 0.084287 | 126.5022 | 0.2883 |  |  | 40.0364 | 0.0060378 | 116.8432 | 0.077445 | 7.9033 | 0.066206 | 0.51731 | 0.24344 | 7.2633 | 0.0061333
432.6 | 270.6 | 122.2431 | 0.082664 | 122.3142 | 0.85969 |  |  | 39.1598 | 0.0044148 | 113.7265 | 0.075822 | 26.2138 | 0.18795 | 0.41993 | 0.75153 | 23.3337 | 0.0061333
432.8 | 270.8 | 126.7233 | 0.08591 | 126.7944 | 0.26719 |  |  | 40.9129 | 0.0060378 | 117.2327 | 0.077445 | 7.9033 | 0.064583 | 0.41993 | 0.21909 | 7.2633 | 0.0061333
433 | 271 | 127.0155 | 0.08591 | 126.9892 | 0.24285 |  |  | 40.9129 | 0.0076615 | 117.4275 | 0.079069 | 9.8512 | 0.072699 | 0.41993 | 0.16877 | 9.6008 | 0.0045103
433.2 | 271.2 | 127.0155 | 0.08591 | 126.9892 | 0.24447 |  |  | 42.1791 | 0.0060378 | 118.1093 | 0.079069 | 8.0981 | 0.061336 | 0.41993 | 0.16552 | 7.5555 | 0.0045103
433.4 | 271.4 | 126.5285 | 0.08591 | 126.5022 | 0.28992 |  |  | 41.7895 | 0.010907 | 115.577 | 0.075822 | 7.7085 | 0.062959 | 0.41993 | 0.20286 | 7.4581 | 0.0045103
433.6 | 271.6 | 126.2364 | 0.08591 | 126.2101 | 0.31752 |  |  | 42.3739 | 0.010907 | 114.9926 | 0.077445 | 4.2022 | 0.032117 | 0.32251 | 0.20611 | 4.0492 | 0.007757
433.8 | 271.8 | 126.5285 | 0.084287 | 126.4048 | 0.28343 |  |  | 34.29 | 0.010907 | 92.981 | 0.079069 | 3.0335 | 0.020754 | 0.51731 | 0.18987 | 2.7831 | 0.0045103
434 | 272 | 125.8468 | 0.08591 | 125.9178 | 0.35323 |  |  | 40.4259 | 0.012531 | 107.2009 | 0.070952 | 2.8387 | 0.017508 | 0.51731 | 0.20773 | 2.4908 | 0.0045103
434.2 | 272.2 | 125.7494 | 0.084287 | 125.7231 | 0.37595 |  |  | 40.8155 | 0.010907 | 106.8113 | 0.066083 | 3.0335 | 0.019131 | 0.41993 | 0.23532 | 2.6856 | 0.0045103
434.4 | 272.4 | 125.4571 | 0.084287 | 125.5283 | 0.42141 |  |  | 43.3479 | 0.012531 | 111.1941 | 0.069329 | 2.3517 | 0.014261 | 0.41993 | 0.21909 | 2.1987 | 0.0061333
434.6 | 272.6 | 125.3598 | 0.084287 | 125.3335 | 0.44088 |  |  | 43.5426 | 0.014154 | 112.5577 | 0.072575 | 2.6439 | 0.017508 | 0.41993 | 0.2337 | 2.1013 | 0.0028873
434.8 | 272.8 | 125.0676 | 0.08591 | 125.0413 | 0.47497 |  |  | 44.4192 | 0.015778 | 112.8499 | 0.070952 | 3.2282 | 0.017508 | 0.41993 | 0.27428 | 2.6856 | 0.0028873
435 | 273 | 125.2624 | 0.08104 | 125.3335 | 0.46361 |  |  | 42.7635 | 0.017401 | 108.8567 | 0.022254 | 4.1048 | 0.017508 | 0.51731 | 0.27591 | 2.4908 | 0.0061333
435.2 | 273.2 | 127.1129 | 0.082664 | 127.184 | 0.21687 |  |  | 25.4269 | 0.012531 | 65.8074 | 0.067706 | 2.0595 | 0.017508 | 0.51731 | 0.20124 | 1.7117 | 0.0028873
435.4 | 273.4 | 126.4311 | 0.08591 | 126.4048 | 0.27206 |  |  | 20.8493 | 0.012531 | 54.412 | 0.16997 | 1.9621 | 0.011014 | 0.41993 | 0.18987 | 1.3221 | 0.0045103
435.6 | 273.6 | 126.2364 | 0.087533 | 126.1126 | 0.34024 |  |  | 17.6352 | 0.0076615 | 44.1853 | 0.25601 | 2.0595 | 0.015885 | 0.41993 | 0.15091 | 1.0299 | 0.0045103
435.8 | 273.8 | 126.9181 | 0.084287 | 126.7944 | 0.24285 |  |  | 12.181 | 0.0092845 | 30.9394 | 0.18621 | 1.1829 | 0.0093912 | 0.51731 | 0.13793 | 0.8351 | 0.0061333
436 | 274 | 127.5025 | 0.087533 | 127.5736 | 0.14707 |  |  | 5.558 | 0.0092845 | 12.8237 | 0.085562 | 1.0855 | 0.0093912 | 0.41993 | 0.13793 | 0.73772 | 0.0045103
436.2 | 274.2 | 127.2103 | 0.087533 | 127.2814 | 0.22661 |  |  | 9.4539 | 0.010907 | 22.4659 | 0.16348 | 1.8647 | 0.011014 | 0.41993 | 0.13955 | 1.4195 | 0.0045103
436.4 | 274.4 | 126.6259 | 0.08591 | 126.697 | 0.2818 |  |  | 13.9341 | 0.012531 | 33.6665 | 0.21867 | 1.7673 | 0.011014 | 0.51731 | 0.14604 | 1.3221 | 0.0045103
436.6 | 274.6 | 127.4051 | 0.08591 | 127.4762 | 0.18928 |  |  | 8.1877 | 0.0076615 | 19.6414 | 0.12127 | 1.5725 | 0.012638 | 0.41993 | 0.13468 | 1.2247 | 0.0028873
436.8 | 274.8 | 127.5999 | 0.087533 | 127.7684 | 0.1633 |  |  | 6.2398 | 0.0092845 | 14.869 | 0.1927 | 1.3777 | 0.0077682 | 0.32251 | 0.12981 | 0.8351 | 0.0061333
437 | 275 | 127.5025 | 0.089157 | 127.3788 | 0.21038 |  |  | 8.6747 | 0.0060378 | 21.1024 | 0.13913 | 1.3777 | 0.0061445 | 0.32251 | 0.13955 | 0.73772 | 0.0045103
437.2 | 275.2 | 127.6973 | 0.084287 | 127.8658 | 0.16493 |  |  | 5.6554 | 0.0076615 | 13.3106 | 0.093679 | 1.3777 | 0.0077682 | 0.41993 | 0.13955 | 0.8351 | 0.0061333
437.4 | 275.4 | 126.6259 | 0.08591 | 126.697 | 0.30128 |  |  | 11.207 | 0.0076615 | 29.4784 | 0.19919 | 1.7673 | 0.0093912 | 0.41993 | 0.1639 | 0.93252 | 0.0028873
437.6 | 275.6 | 126.8207 | 0.087533 | 126.7944 | 0.26882 |  |  | 11.0122 | 0.0076615 | 28.2123 | 0.18458 | 1.8647 | 0.011014 | 0.41993 | 0.15416 | 1.0299 | 0.0028873
437.8 | 275.8 | 125.652 | 0.08591 | 125.6257 | 0.40842 |  |  | 11.0122 | 0.0060378 | 27.8227 | 0.18783 | 4.7866 | 0.022377 | 0.41993 | 0.29376 | 2.5883 | 0.0061333
438 | 276 | 126.6259 | 0.08591 | 126.5996 | 0.29966 |  |  | 11.8888 | 0.0060378 | 30.1602 | 0.20081 | 2.1569 | 0.017508 | 0.51731 | 0.17039 | 1.7117 | 0.0061333
438.2 | 276.2 | 126.7233 | 0.087533 | 126.7944 | 0.26882 |  |  | 11.207 | 0.0060378 | 27.8227 | 0.17971 | 1.4751 | 0.012638 | 0.41993 | 0.16552 | 0.93252 | 0.0045103
438.4 | 276.4 | 127.0155 | 0.08591 | 127.0866 | 0.25421 |  |  | 9.6487 | 0.0076615 | 23.6347 | 0.1651 | 1.4751 | 0.011014 | 0.41993 | 0.15903 | 0.93252 | 0.0045103
438.6 | 276.6 | 126.0416 | 0.08591 | 126.1126 | 0.34511 |  |  | 12.3757 | 0.0060378 | 32.6926 | 0.21867 | 1.8647 | 0.0093912 | 0.41993 | 0.19799 | 0.8351 | 0.0045103
438.8 | 276.8 | 126.7233 | 0.08591 | 126.7944 | 0.28667 |  |  | 10.8174 | 0.0060378 | 27.141 | 0.18133 | 1.8647 | 0.011014 | 0.71211 | 0.17202 | 0.93252 | 0.0061333
439 | 277 | 125.9441 | 0.087533 | 126.2101 | 0.34024 |  |  | 13.3497 | 0.0076615 | 35.8092 | 0.23328 | 2.0595 | 0.012638 | 0.41993 | 0.185 | 0.73772 | 0.0028873
439.2 | 277.2 | 125.3598 | 0.08591 | 125.3335 | 0.43764 |  |  | 13.3497 | 0.0027911 | 33.7639 | 0.23328 | 2.2543 | 0.014261 | 0.32251 | 0.19474 | 0.93252 | 0.0061333
439.4 | 277.4 | 126.3337 | 0.092403 | 126.3074 | 0.34674 |  |  | 12.5705 | 0.0092845 | 31.329 | 0.20893 | 2.2543 | 0.012638 | 0.41993 | 0.19799 | 0.93252 | 0.0028873
439.6 | 277.6 | 126.2364 | 0.089157 | 126.2101 | 0.337 |  |  | 11.694 | 0.0060378 | 29.1863 | 0.19757 | 2.5465 | 0.015885 | 0.41993 | 0.20286 | 1.2247 | 0.0045103
439.8 | 277.8 | 126.0416 | 0.09078 | 126.1126 | 0.36459 |  |  | 13.3497 | 0.0060378 | 33.7639 | 0.2414 | 2.2543 | 0.017508 | 0.41993 | 0.19637 | 1.1273 | 0.0061333
440 | 278 | 126.0416 | 0.09565 | 126.0153 | 0.3581 |  |  | 11.7914 | 0.0076615 | 29.3811 | 0.21055 | 4.7866 | 0.027247 | 0.41993 | 0.20935 | 1.7117 | 0.0045103
440.2 | 278.2 | 124.4832 | 0.09565 | 124.4569 | 0.57724 |  |  | 39.5494 | 0.0044148 | 95.4159 | 0.19757 | 10.3382 | 0.072699 | 0.41993 | 0.37817 | 6.9711 | 0.0061333
440.4 | 278.4 | 122.4379 | 0.097273 | 122.509 | 0.77041 |  |  | 44.127 | 0.0076615 | 109.0514 | 0.079069 | 24.1685 | 0.16847 | 0.41993 | 0.62978 | 20.0222 | 0.0045103
440.6 | 278.6 | 123.4118 | 0.10701 | 123.2881 | 0.67951 |  |  | 44.7114 | 0.0092845 | 113.3369 | 0.075822 | 26.7982 | 0.20581 | 0.22513 | 0.52102 | 24.8921 | 0.00938
440.8 | 278.8 | 124.191 | 0.09565 | 124.1647 | 0.58536 |  |  | 45.0036 | 0.0092845 | 116.2588 | 0.074199 | 29.0383 | 0.22204 | 0.51731 | 0.36843 | 28.8853 | 0.0028873
441 | 279 | 123.3144 | 0.10052 | 123.2881 | 0.68925 |  |  | 45.3932 | 0.014154 | 115.7718 | 0.075822 | 30.2071 | 0.22204 | 0.32251 | 0.48044 | 29.9567 | 0.0061333
441.2 | 279.2 | 120.003 | 0.12325 | 119.9767 | 1.0723 |  |  | 45.0036 | 0.012531 | 113.2395 | 0.072575 | 32.4472 | 0.24639 | 0.61469 | 0.54375 | 32.1968 | 0.0045103
441.4 | 279.4 | 122.3405 | 0.10701 | 122.3142 | 0.7769 |  |  | 45.3932 | 0.014154 | 115.8692 | 0.075822 | 36.1483 | 0.25613 | 0.32251 | 0.52589 | 34.9239 | 0.0045103
441.6 | 279.6 | 122.8274 | 0.11513 | 122.8986 | 0.73145 |  |  | 45.8802 | 0.014154 | 118.4989 | 0.077445 | 30.5967 | 0.2334 | 0.41993 | 0.38467 | 30.9306 | 0.0045103
441.8 | 279.8 | 120.9769 | 0.14435 | 121.048 | 0.90189 |  |  | 45.1984 | 0.017401 | 114.0186 | 0.072575 | 40.7259 | 0.27723 | 0.51731 | 0.68497 | 36.677 | 0.007757
442 | 280 | 95.8486 | 0.09078 | 95.9197 | 3.6809 |  |  | 37.5041 | 0.017401 | 91.8122 | 0.075822 | 26.2138 | 0.19931 | 0.51731 | 0.28402 | 25.4764 | 0.0045103
442.2 | 280.2 | 91.6606 | 0.084287 | 91.7317 | 4.2215 |  |  | 35.6535 | 0.015778 | 86.4554 | 0.13101 | 26.1164 | 0.18957 | 0.61469 | 0.32298 | 24.5025 | 0.011004
442.4 | 280.4 | 14.9121 | 0.038835 | 15.3728 | 1.4635 |  |  | 6.3372 | 0.012531 | 13.9924 | 0.066083 | 5.8579 | 0.056466 | 0.41993 | 0.06975 | 5.6075 | 0.0028873
442.6 | 280.6 | 2.9323 | 0.017733 | 3.1008 | 0.11785 |  |  | 1.6621 | 0.0092845 | 2.7918 | 0.019008 | 1.6699 | 0.017508 | 0.41993 | 0.022675 | 1.6143 | 0.0045103
442.8 | 280.8 | 1.2766 | 0.012862 | 1.3477 | 0.03182 |  |  | 0.88295 | 0.0092845 | 1.4282 | 0.012514 | 0.98811 | 0.0093912 | 0.41993 | 0.014559 | 0.8351 | 0.0045103
443 | 281 | 0.88702 | 0.011239 | 0.95811 | 0.01721 |  |  | 0.78557 | 0.0076615 | 0.94126 | 0.0092676 | 0.79331 | 0.0077682 | 0.51731 | 0.012936 | 0.73772 | 0.0045103
443.2 | 281.2 | 0.7896 | 0.011239 | 0.76331 | 0.01234 |  |  | 0.68819 | 0.0076615 | 0.84388 | 0.0076446 | 0.69593 | 0.0061445 | 0.41993 | 0.0096889 | 0.64033 | 0.0045103
443.4 | 281.4 | 0.69222 | 0.0096164 | 0.66593 | 0.010717 |  |  | 0.59077 | 0.0076615 | 0.7465 | 0.0076446 | 0.69593 | 0.0061445 | 0.41993 | 0.0096889 | 0.44553 | 0.0045103
443.6 | 281.6 | 0.59484 | 0.0096164 | 0.66593 | 0.0090935 |  |  | 0.49339 | 0.0060378 | 0.7465 | 0.0076446 | 0.59851 | 0.0045215 | 0.41993 | 0.0096889 | 0.44553 | 0.0045103
443.8 | 281.8 | 0.59484 | 0.0079928 | 0.66593 | 0.0090935 |  |  | 0.49339 | 0.0060378 | 0.64908 | 0.0060216 | 0.50113 | 0.0045215 | 0.41993 | 0.0096889 | 0.44553 | 0.0045103
444 | 282 | 0.59484 | 0.0079928 | 0.56855 | 0.0090935 |  |  | 0.49339 | 0.0060378 | 0.64908 | 0.0060216 | 0.50113 | 0.0045215 | 0.41993 | 0.0096889 | 0.34811 | 0.0045103
444.2 | 282.2 | 0.59484 | 0.0079928 | 0.56855 | 0.0090935 |  |  | 0.39597 | 0.0060378 | 0.64908 | 0.0060216 | 0.50113 | 0.0045215 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
444.4 | 282.4 | 0.49742 | 0.0079928 | 0.56855 | 0.0074705 |  |  | 0.49339 | 0.0060378 | 0.64908 | 0.0060216 | 0.50113 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
444.6 | 282.6 | 0.49742 | 0.0079928 | 0.47113 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.64908 | 0.0060216 | 0.50113 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
444.8 | 282.8 | 0.49742 | 0.0079928 | 0.56855 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.64908 | 0.0060216 | 0.50113 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
445 | 283 | 0.49742 | 0.0079928 | 0.47113 | 0.0090935 |  |  | 0.39597 | 0.0060378 | 0.64908 | 0.0043979 | 0.50113 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
445.2 | 283.2 | 0.40004 | 0.0079928 | 0.47113 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
445.4 | 283.4 | 0.49742 | 0.0063697 | 0.47113 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0060216 | 0.50113 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
445.6 | 283.6 | 0.40004 | 0.0063697 | 0.47113 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.50113 | 0.0028978 | 0.41993 | 0.0080659 | 0.25073 | 0.0045103
445.8 | 283.8 | 0.49742 | 0.0079928 | 0.47113 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.50113 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
446 | 284 | 0.40004 | 0.0079928 | 0.47113 | 0.0074705 |  |  | 0.49339 | 0.0060378 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
446.2 | 284.2 | 0.40004 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
446.4 | 284.4 | 0.40004 | 0.0063697 | 0.37375 | 0.0074705 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0045215 | 0.51731 | 0.0080659 | 0.34811 | 0.0045103
446.6 | 284.6 | 0.40004 | 0.0063697 | 0.37375 | 0.0026002 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.50113 | 0.0028978 | 0.51731 | 0.0080659 | 0.25073 | 0.0045103
446.8 | 284.8 | 0.30262 | 0.0096164 | 0.27633 | 0.0042238 |  |  | -0.1884 | 0.0076615 | 0.1621 | 0.010891 | 0.40375 | -0.00034817 | 1.1991 | 0.0048192 | 0.73772 | 0.01425
447 | 285 | 0.40004 | 0.0063697 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0060216 | 0.40375 | 0.0028978 | 0.41993 | 0.0080659 | 0.25073 | 0.0045103
447.2 | 285.2 | 0.40004 | 0.0063697 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
447.4 | 285.4 | 0.40004 | 0.0063697 | 0.47113 | 0.0074705 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.50113 | 0.0028978 | 0.32251 | 0.0064422 | 0.25073 | 0.0045103
447.6 | 285.6 | 0.40004 | 0.0063697 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.25073 | 0.0045103
447.8 | 285.8 | 0.40004 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0080659 | 0.25073 | 0.0045103
448 | 286 | 0.40004 | 0.0063697 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
448.2 | 286.2 | 0.40004 | 0.0079928 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.25073 | 0.0045103
448.4 | 286.4 | 0.40004 | 0.0063697 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.30633 | 0.0028978 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
448.6 | 286.6 | 0.40004 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.0064422 | 0.34811 | 0.0045103
448.8 | 286.8 | 0.40004 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.0064422 | 0.34811 | 0.0045103
449 | 287 | 0.40004 | 0.0063697 | 0.37375 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.0080659 | 0.34811 | 0.0045103
449.2 | 287.2 | 0.40004 | 0.0063697 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.25073 | 0.0045103
449.4 | 287.4 | 0.40004 | 0.0063697 | 0.37375 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
449.6 | 287.6 | 0.40004 | 0.0063697 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0061333
449.8 | 287.8 | 0.40004 | 0.0063697 | 0.47113 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
450 | 288 | 0.30262 | 0.0063697 | 0.37375 | 0.0058469 |  |  | 0.29859 | 0.0060378 | 0.5517 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
480 | 318 | 0.30262 | 0.0063697 | 0.37375 | 0.0042238 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0060216 | 0.30633 | 0.0028978 | 0.51731 | 0.0064422 | 0.34811 | 0.0045103
510 | 348 | 0.30262 | 0.0063697 | 0.37375 | 0.0042238 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0060216 | 0.50113 | 0.0028978 | 0.51731 | 0.0080659 | 0.34811 | 0.0061333
540 | 378 | 0.30262 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0027749 | 0.40375 | 0.0028978 | 0.41993 | 0.011313 | 0.25073 | 0.0045103
570 | 408 | 0.30262 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.29859 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.0080659 | 0.25073 | 0.0045103
600 | 438 | 0.30262 | 0.0079928 | 0.27633 | 0.0058469 |  |  | 0.39597 | 0.0044148 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.41993 | 0.0064422 | 0.34811 | 0.0045103
630 | 468 | 0.30262 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0060216 | 0.40375 | 0.0028978 | 0.61469 | 0.0080659 | 0.34811 | 0.0061333
660 | 498 | 0.30262 | 0.0063697 | 0.27633 | 0.0042238 |  |  | 0.29859 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0012748 | 0.41993 | 0.0064422 | 0.25073 | 0.0061333
690 | 528 | 0.30262 | 0.0063697 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.45428 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.0080659 | 0.25073 | 0.0045103
720 | 558 | 0.30262 | 0.0079928 | 0.37375 | 0.0074705 |  |  | 0.49339 | 0.0060378 | 0.45428 | 0.0060216 | 0.50113 | 0.0028978 | 0.51731 | 0.0080659 | 0.34811 | 0.0061333
750 | 588 | 0.30262 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.50113 | 0.0028978 | 0.51731 | 0.0080659 | 0.44553 | 0.0061333
780 | 618 | 0.30262 | 0.0079928 | 0.37375 | 0.0058469 |  |  | 0.39597 | 0.0060378 | 0.5517 | 0.0043979 | 0.40375 | 0.0028978 | 0.51731 | 0.0096889 | 0.34811 | 0.0061333