## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-6
Test Date: | 2006-11-06
Ignition Time Relative to Thermal Data: | 162 | s
Ignition Time Relative to Electrical Data: | 162 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Template Plot

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 6-1 |  |  |  | Location A | Location C - 6-cable bundle 6-2 |  |  |  | Location C | Location A-C 3-cable air drop |  |  | Location E: Conduit with 3-cable bundle |  |  | Location G: Conduit with 3-cable bundle
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable Temp | TC-2 Above Bundle | TC3 Below Bundle | Cable Temp | Air Inside Conduit | Conduit Temp | Cable Temp | Air Inside Conduit | Conduit Temp
0 | -162 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.8 | 23.5 | 15.4 | 1.3 | 246.5 | 4.1 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
1 | -161 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.8 | 23.5 | 15.4 | 1.5 | 254.5 | 3.8 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
2 | -160 | -6.7 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.8 | 23.5 | 15.4 | 1.5 | 268.2 | 4.5 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
3 | -159 | -5.9 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.8 | 23.5 | 15.4 | 1.6 | 258.8 | 5.3 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
4 | -158 | -5.2 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.5 | 15.4 | 1.6 | 260.7 | 5.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
5 | -157 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.8 | 23.5 | 15.4 | 1.8 | 259.6 | 5.6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
6 | -156 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.5 | 15.4 | 1.8 | 252.2 | 5.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
7 | -155 | -6.7 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 251 | 5.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
8 | -154 | -6.4 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 253.1 | 6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.4 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
9 | -153 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.7 | 250 | 5.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
10 | -152 | -6.7 | 0 | 0 | 16 | 16.4 | 16.2 | 16.1 | 16.2 | 14.9 | 23.4 | 15.4 | 1.8 | 239.8 | 5.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
11 | -151 | -6.6 | 0 | 0 | 16 | 16.4 | 16.2 | 16.1 | 16.2 | 14.9 | 23.4 | 15.4 | 1.7 | 254.3 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
12 | -150 | -6.5 | 0 | 0 | 16 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.8 | 256.3 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.4 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
13 | -149 | -6.5 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.8 | 256.6 | 4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
14 | -148 | -6.5 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.8 | 23.4 | 15.4 | 1.6 | 263 | 3.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
15 | -147 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.6 | 264.3 | 4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
16 | -146 | -6.6 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.5 | 264.3 | 4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
17 | -145 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.7 | 265.3 | 4.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
18 | -144 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.6 | 261.8 | 4.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
19 | -143 | -6.6 | 0 | 0 | 16.1 | 16.4 | 16.3 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.5 | 253.8 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
20 | -142 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.3 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.8 | 260.1 | 5.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
21 | -141 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.3 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.7 | 264.2 | 5.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
22 | -140 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.3 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.7 | 253.1 | 6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
23 | -139 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.8 | 240 | 6.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
24 | -138 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.6 | 244.9 | 5.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
25 | -137 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.8 | 23.4 | 15.4 | 1.7 | 249 | 5.6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
26 | -136 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 248.4 | 5.6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
27 | -135 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.8 | 262.6 | 5.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
28 | -134 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 270.1 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
29 | -133 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.3 | 252.2 | 4.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
30 | -132 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 236.6 | 3.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
31 | -131 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.7 | 234.7 | 3.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
32 | -130 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.7 | 261.4 | 3.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
33 | -129 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.8 | 276.7 | 3.5 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
34 | -128 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 263.9 | 4.1 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
35 | -127 | -6.4 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.5 | 258.4 | 4.8 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
36 | -126 | -6.3 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.2 | 14.9 | 23.4 | 15.4 | 1.6 | 250 | 4.9 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
37 | -125 | -6.5 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.1 | 14.9 | 23.4 | 15.4 | 1.6 | 233.9 | 4.8 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
38 | -124 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.1 | 14.9 | 23.4 | 15.4 | 1.6 | 240.3 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
39 | -123 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.1 | 14.9 | 23.4 | 15.4 | 1.8 | 242.2 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
40 | -122 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.1 | 14.9 | 23.4 | 15.4 | 1.7 | 240.2 | 4.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
41 | -121 | -6.5 | 0 | 0 | 16 | 16.4 | 16.1 | 16.3 | 16.1 | 14.9 | 23.4 | 15.4 | 1.7 | 242.9 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
42 | -120 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.3 | 16.1 | 14.9 | 23.4 | 15.4 | 1.9 | 242.7 | 4.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
43 | -119 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.3 | 16.1 | 15 | 23.4 | 15.4 | 1.7 | 241.4 | 4.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
44 | -118 | -6.7 | 0 | 0 | 16 | 16.4 | 16.1 | 16.3 | 16.1 | 14.9 | 23.4 | 15.4 | 1.6 | 241 | 4.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
45 | -117 | -6.6 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16.1 | 14.9 | 23.4 | 15.4 | 1.7 | 240.5 | 4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
46 | -116 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16.1 | 14.9 | 23.4 | 15.4 | 1.6 | 234.5 | 4.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
47 | -115 | -6.6 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16.1 | 14.9 | 23.3 | 15.4 | 1.6 | 213.7 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
48 | -114 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16.1 | 14.9 | 23.4 | 15.4 | 1.6 | 207.5 | 4.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17.1 | 16 | 15.9 | 17.4
49 | -113 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16.1 | 14.9 | 23.3 | 15.4 | 1.6 | 224.8 | 3.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
50 | -112 | -6.6 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16 | 14.9 | 23.4 | 15.4 | 1.7 | 235.2 | 3.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
51 | -111 | -6.8 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16 | 15 | 23.3 | 15.4 | 1.8 | 234.4 | 3.6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
52 | -110 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16 | 15 | 23.3 | 15.4 | 1.7 | 231.5 | 3.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
53 | -109 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.3 | 16.1 | 15 | 23.3 | 15.4 | 1.6 | 228.3 | 3.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
54 | -108 | -6.7 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16 | 15 | 23.3 | 15.4 | 1.9 | 233.3 | 3.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
55 | -107 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.9 | 216.8 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
56 | -106 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 2 | 220 | 4.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
57 | -105 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.9 | 224.2 | 4.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
58 | -104 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.9 | 224.5 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
59 | -103 | -6.7 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.8 | 226.6 | 3.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
60 | -102 | -6.6 | 0 | 0 | 16.1 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.8 | 233.3 | 3.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
61 | -101 | -6.6 | 0 | 0 | 16.1 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.9 | 227.5 | 3.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
62 | -100 | -6.6 | 0 | 0 | 16.1 | 16.3 | 16 | 16.2 | 16.1 | 15 | 23.3 | 15.4 | 1.9 | 212.8 | 3.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
63 | -99 | -6.4 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 15 | 23.3 | 15.4 | 1.8 | 214.3 | 3.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
64 | -98 | -6.5 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 15 | 23.3 | 15.4 | 1.8 | 225 | 2.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
65 | -97 | -6.5 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 15 | 23.3 | 15.4 | 1.7 | 232.5 | 2.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
66 | -96 | -6.7 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 15 | 23.3 | 15.4 | 1.8 | 227.2 | 2.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
67 | -95 | -6.7 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 15 | 23.3 | 15.4 | 1.9 | 212.1 | 2.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
68 | -94 | -6.6 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.3 | 15.3 | 1.8 | 214.4 | 3.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
69 | -93 | -6.7 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.3 | 15.3 | 1.7 | 265.4 | 3.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
70 | -92 | -6.8 | 0 | 0 | 16.1 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.3 | 15.3 | 1.9 | 263.7 | 3.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
71 | -91 | -6.8 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16.1 | 16.1 | 14.9 | 23.3 | 15.4 | 1.7 | 222.6 | 3.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
72 | -90 | -6.8 | 0 | 0 | 16.1 | 16.3 | 16.1 | 16.1 | 16.1 | 14.9 | 23.3 | 15.4 | 1.7 | 193.3 | 3.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
73 | -89 | -6.8 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16.1 | 16.1 | 14.9 | 23.3 | 15.4 | 1.8 | 211.7 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
74 | -88 | -6.7 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16.1 | 16.1 | 14.9 | 23.3 | 15.4 | 1.5 | 238.2 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
75 | -87 | -6.8 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16 | 16.1 | 14.9 | 23.3 | 15.4 | 1.7 | 214.8 | 4.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
76 | -86 | -6.8 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16 | 16.1 | 14.9 | 23.3 | 15.4 | 1.6 | 228.7 | 4.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
77 | -85 | -6.7 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16 | 16.1 | 14.9 | 23.3 | 15.4 | 1.8 | 245.5 | 4.4 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.6 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
78 | -84 | -6.6 | 0 | 0 | 16.2 | 16.3 | 16.1 | 16 | 16.1 | 14.9 | 23.3 | 15.4 | 1.9 | 255.6 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
79 | -83 | -6.4 | 0 | 0 | 16.2 | 16.3 | 16.2 | 16 | 16.1 | 14.9 | 23.3 | 15.4 | 1.8 | 245.7 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
80 | -82 | -6.3 | 0 | 0 | 16.2 | 16.3 | 16.2 | 16 | 16.1 | 14.9 | 23.3 | 15.4 | 1.6 | 239.7 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
81 | -81 | -6.6 | 0 | 0 | 16.2 | 16.3 | 16.2 | 16 | 16.1 | 14.9 | 23.2 | 15.4 | 1.6 | 253.4 | 5.2 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
82 | -80 | -6.8 | 0 | 0 | 16.2 | 16.3 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.5 | 248.5 | 5.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
83 | -79 | -6.9 | 0 | 0 | 16.2 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.6 | 222.5 | 4.6 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
84 | -78 | -6.7 | 0 | 0 | 16.2 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.5 | 232.3 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
85 | -77 | -6.4 | 0 | 0 | 16.2 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.3 | 244.1 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
86 | -76 | -6.4 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.4 | 241.9 | 5.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
87 | -75 | -6.2 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.2 | 245.8 | 5.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
88 | -74 | -6.2 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.4 | 239.4 | 5.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
89 | -73 | -6.4 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16 | 14.9 | 23.2 | 15.4 | 1.6 | 233.2 | 6.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
90 | -72 | -6.6 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16.1 | 14.9 | 23.2 | 15.4 | 1.5 | 228.1 | 5.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
91 | -71 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 234.8 | 5.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
92 | -70 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16 | 16.1 | 14.9 | 23.2 | 15.4 | 2 | 257.6 | 5.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
93 | -69 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.9 | 241.3 | 5.7 | 15.5 | 14.9 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
94 | -68 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 233.8 | 5.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
95 | -67 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 237.2 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
96 | -66 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.7 | 232.8 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
97 | -65 | -6.8 | 0 | 0 | 16.1 | 16.4 | 16.2 | 16.1 | 16.1 | 14.8 | 23.2 | 15.4 | 1.8 | 236.7 | 4.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
98 | -64 | -6.8 | 0 | 0 | 16 | 16.4 | 16.2 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 237.5 | 5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
99 | -63 | -6.7 | 0 | 0 | 16.1 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 234.1 | 5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
100 | -62 | -6.5 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.6 | 245.9 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
101 | -61 | -6.7 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.5 | 246.3 | 4.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
102 | -60 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.7 | 246 | 4.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
103 | -59 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 250.9 | 4.8 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
104 | -58 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 243.6 | 5.4 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
105 | -57 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.9 | 239.6 | 6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
106 | -56 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.7 | 226.2 | 6.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
107 | -55 | -6.8 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.5 | 206.3 | 6.5 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
108 | -54 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.4 | 196.1 | 7.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
109 | -53 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.6 | 214 | 6.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
110 | -52 | -6.6 | 0 | 0 | 16 | 16.4 | 16.1 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.5 | 235.7 | 6.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
111 | -51 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.5 | 253.7 | 6.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
112 | -50 | -6.7 | 0 | 0 | 16 | 16.4 | 16.1 | 16.2 | 16.1 | 14.9 | 23.2 | 15.4 | 1.7 | 245.1 | 6.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
113 | -49 | -6.6 | 0 | 0 | 16 | 16.4 | 16 | 16.1 | 16.1 | 14.9 | 23.2 | 15.4 | 1.7 | 238.3 | 6.1 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
114 | -48 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.2 | 16.1 | 14.9 | 23.2 | 15.4 | 1.7 | 245.4 | 5.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
115 | -47 | -2.2 | 0 | 0 | 16 | 16.4 | 16 | 16.2 | 16.1 | 14.9 | 23.2 | 15.4 | 1.8 | 244.8 | 6 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
116 | -46 | -6.7 | 0 | 0 | 16 | 16.4 | 16 | 16.2 | 16.1 | 14.9 | 23.2 | 15.4 | 1.5 | 242.1 | 6.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
117 | -45 | 0.7 | 0.28 | 0.3273 | 16 | 16.4 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 1.6 | 242.1 | 6.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
118 | -44 | 2.8 | 1.12 | 1.3092 | 16 | 16.4 | 16 | 16.2 | 16 | 14.8 | 23.2 | 15.4 | 1.7 | 242.9 | 6.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
119 | -43 | 3.1 | 1.24 | 1.4495 | 16 | 16.4 | 16 | 16.2 | 16 | 14.8 | 23.2 | 15.4 | 1.7 | 243 | 6.7 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
120 | -42 | 3 | 1.2 | 1.4027 | 16 | 16.4 | 16 | 16.2 | 16 | 14.8 | 23.2 | 15.4 | 1.9 | 242.9 | 6.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
121 | -41 | 1.3 | 0.52 | 0.60785 | 16 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 2 | 240 | 5.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
122 | -40 | -0.5 | 0 | 0 | 16 | 16.4 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 2 | 217.5 | 4.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
123 | -39 | -2.3 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 2.1 | 212.8 | 4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
124 | -38 | -3.1 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 2.3 | 232.1 | 3.8 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
125 | -37 | -3.9 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 1.9 | 253.5 | 4.4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
126 | -36 | -4.2 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.1 | 15.4 | 1.9 | 229.7 | 4.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
127 | -35 | -4.8 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.1 | 15.4 | 1.8 | 229.7 | 4.5 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
128 | -34 | -5.5 | 0 | 0 | 15.9 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.1 | 15.4 | 1.6 | 254.3 | 4.4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
129 | -33 | -5.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.1 | 15.4 | 1.9 | 243.8 | 4.8 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
130 | -32 | -5.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.1 | 15.4 | 2 | 232 | 5.5 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
131 | -31 | -5.9 | 0 | 0 | 15.9 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.2 | 15.4 | 2.1 | 243.1 | 5.5 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
132 | -30 | -6.2 | 0 | 0 | 15.9 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.2 | 255.2 | 5.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
133 | -29 | -6.6 | 0 | 0 | 15.9 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.1 | 248.9 | 5.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
134 | -28 | -6.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 1.8 | 243 | 6.2 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
135 | -27 | -6.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 1.9 | 245.4 | 6.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 14.9 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
136 | -26 | -6.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2 | 245.3 | 6.4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
137 | -25 | -6.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.2 | 15.4 | 1.6 | 244.4 | 5.8 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
138 | -24 | -6.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.2 | 16 | 14.9 | 23.1 | 15.4 | 1.5 | 237.8 | 5.3 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
139 | -23 | -6.8 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.7 | 232.7 | 5.7 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
140 | -22 | -6.8 | 0 | 0 | 15.9 | 16.3 | 16 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.9 | 238 | 6.1 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
141 | -21 | -6.8 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.8 | 232.7 | 5.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
142 | -20 | -6.8 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.7 | 236.8 | 5.2 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
143 | -19 | -6.8 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.6 | 260.4 | 5.2 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
144 | -18 | -6.8 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.5 | 242.8 | 5.4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
145 | -17 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.9 | 257.7 | 5.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
146 | -16 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.8 | 247.3 | 6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
147 | -15 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.7 | 234.5 | 5.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
148 | -14 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 2.1 | 215.2 | 5.6 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
149 | -13 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 2.1 | 238.8 | 5.2 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
150 | -12 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 2.1 | 240.2 | 4.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
151 | -11 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.9 | 216.7 | 4.8 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
152 | -10 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.9 | 207.8 | 5.3 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
153 | -9 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.8 | 204.1 | 5.3 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
154 | -8 | -6.9 | 0 | 0 | 15.9 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.9 | 213.5 | 4.9 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
155 | -7 | -6.6 | 0 | 0 | 16 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.8 | 231.3 | 4.2 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
156 | -6 | -6.6 | 0 | 0 | 16 | 16.3 | 15.9 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 2.1 | 226.8 | 3.9 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
157 | -5 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 1.8 | 213.5 | 4.3 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.7 | 15 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
158 | -4 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.1 | 15.4 | 1.6 | 243.8 | 4.4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.7 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
159 | -3 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.1 | 15.4 | 1.6 | 231.4 | 4.5 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.8 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
160 | -2 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.1 | 15.4 | 1.6 | 235.5 | 4.5 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.8 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
161 | -1 | -6.8 | 0 | 0 | 16 | 16.3 | 16 | 16.1 | 16.1 | 14.9 | 23.1 | 15.4 | 1.9 | 228.9 | 5.4 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.8 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
162 | 0 | 34.9 | 13.96 | 16.3184 | 16 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.2 | 224.7 | 6.1 | 15.5 | 14.8 | 14.8 | 15.8 | 16.2 | 15.3 | 14.8 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
163 | 1 | 334.2 | 133.68 | 156.2642 | 16 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.2 | 236 | 5.7 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.8 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
164 | 2 | 511.7 | 204.68 | 239.2591 | 16 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.2 | 215.9 | 6.2 | 15.5 | 14.8 | 14.9 | 15.8 | 16.2 | 15.3 | 14.9 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
165 | 3 | 539.4 | 215.76 | 252.211 | 16 | 16.3 | 16 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.5 | 213.8 | 6.6 | 15.5 | 14.8 | 15 | 15.8 | 16.3 | 15.3 | 14.9 | 15.1 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
166 | 4 | 517.3 | 206.92 | 241.8776 | 16 | 16.3 | 16.1 | 16.1 | 16 | 14.9 | 23.1 | 15.4 | 2.4 | 212.7 | 7 | 15.5 | 14.9 | 15 | 15.8 | 16.3 | 15.3 | 15.1 | 15.7 | 15.2 | 16.3 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
167 | 5 | 489.9 | 195.96 | 229.0659 | 16.1 | 16.3 | 16.1 | 16.2 | 16.1 | 14.9 | 23.1 | 15.4 | 2.3 | 219.5 | 6.6 | 15.5 | 15.6 | 17.7 | 15.9 | 17.5 | 15.3 | 18.7 | 29.3 | 15.2 | 16.8 | 15.1 | 15.5 | 15.5 | 15.8 | 16 | 17 | 16 | 15.9 | 17.4
168 | 6 | 470.9 | 188.36 | 220.182 | 16.1 | 16.4 | 16.3 | 16.4 | 16.1 | 14.9 | 23.1 | 15.4 | 2.4 | 244.1 | 5.8 | 15.4 | 21.4 | 33 | 16.5 | 21.4 | 15.3 | 34.2 | 73.6 | 15.3 | 20.1 | 15.1 | 15.4 | 15.5 | 15.8 | 16 | 17 | 15.9 | 15.9 | 17.4
169 | 7 | 467.1 | 186.84 | 218.4052 | 16.2 | 16.5 | 16.5 | 16.6 | 16.3 | 15 | 23.1 | 15.4 | 2.4 | 240.5 | 6.7 | 15.4 | 33.8 | 58.3 | 17.6 | 26 | 15.3 | 60.8 | 134.1 | 15.3 | 24.6 | 15.1 | 15.4 | 15.5 | 15.8 | 16 | 17.1 | 15.9 | 15.9 | 17.4
170 | 8 | 461.2 | 184.48 | 215.6465 | 16.4 | 16.6 | 16.8 | 16.8 | 16.7 | 15 | 23.1 | 15.4 | 2.3 | 244.6 | 7.7 | 15.4 | 52.8 | 101.2 | 19.9 | 34.7 | 15.3 | 99.3 | 189.8 | 15.4 | 31.1 | 15.1 | 15.4 | 15.5 | 15.8 | 16 | 17.1 | 15.9 | 15.9 | 17.5
171 | 9 | 449.9 | 179.96 | 210.3629 | 16.6 | 16.9 | 17.1 | 17.3 | 17.3 | 15.1 | 23.1 | 15.4 | 2.3 | 238.9 | 8.4 | 15.4 | 72.7 | 141.9 | 22.1 | 41.5 | 15.3 | 141.4 | 238.6 | 15.5 | 38.3 | 15.2 | 15.3 | 15.5 | 15.8 | 16 | 17.2 | 15.9 | 15.9 | 17.5
172 | 10 | 444.2 | 177.68 | 207.6977 | 16.9 | 17.2 | 17.6 | 18.4 | 18.1 | 15.1 | 23.1 | 15.4 | 2.2 | 235.8 | 8.1 | 15.4 | 93.4 | 177.3 | 24.8 | 47.3 | 15.4 | 185.4 | 290.8 | 15.7 | 46.6 | 15.3 | 15.6 | 15.6 | 15.8 | 16 | 17.2 | 16 | 15.9 | 17.6
173 | 11 | 441.7 | 176.68 | 206.5287 | 17.2 | 17.6 | 18.8 | 20.2 | 19 | 15.2 | 23.1 | 15.4 | 1.9 | 242.4 | 8 | 15.5 | 116.9 | 213.4 | 27.3 | 53.4 | 15.4 | 229.7 | 343 | 16 | 53.2 | 15.4 | 15.9 | 15.7 | 15.8 | 16 | 17.3 | 16 | 15.9 | 17.7
174 | 12 | 439.7 | 175.88 | 205.5936 | 17.9 | 18.5 | 20.4 | 22.3 | 20.8 | 15.2 | 23.1 | 15.4 | 2.2 | 245.5 | 8.1 | 15.5 | 144.8 | 257.3 | 29.9 | 62.5 | 15.5 | 288.3 | 401.7 | 16.6 | 62.4 | 15.7 | 16.3 | 15.8 | 15.8 | 16 | 17.5 | 16 | 15.9 | 17.8
175 | 13 | 440.2 | 176.08 | 205.8274 | 19.1 | 20.1 | 22.2 | 24.4 | 21.8 | 15.3 | 23.1 | 15.4 | 2.4 | 244.6 | 8.1 | 15.6 | 178.9 | 311.9 | 33.7 | 73.8 | 15.5 | 348.4 | 463.7 | 17.7 | 75.9 | 16 | 17 | 15.9 | 15.8 | 16.1 | 17.6 | 16 | 15.9 | 18.1
176 | 14 | 439.6 | 175.84 | 205.5468 | 21.6 | 21.8 | 24.3 | 26.5 | 23.8 | 15.3 | 23.1 | 15.4 | 2.2 | 243.5 | 8.2 | 15.6 | 208.1 | 349.4 | 38 | 88.3 | 15.6 | 393.1 | 500.2 | 19.1 | 88.9 | 16.4 | 17.8 | 16.1 | 15.8 | 16.1 | 17.7 | 15.9 | 15.9 | 18.3
177 | 15 | 439.7 | 175.88 | 205.5936 | 24.1 | 23.4 | 26.8 | 29.5 | 27.3 | 15.4 | 23.1 | 15.4 | 2.6 | 237.6 | 8 | 15.7 | 223.4 | 362.8 | 41.9 | 103.6 | 15.8 | 432.4 | 540.7 | 20.9 | 98.4 | 17 | 18.8 | 16.4 | 15.8 | 16.1 | 18 | 16 | 15.9 | 18.6
178 | 16 | 439.6 | 175.84 | 205.5468 | 26.5 | 25.4 | 29.7 | 32.8 | 31 | 15.4 | 23.1 | 15.4 | 2.4 | 238.1 | 7.6 | 15.8 | 244.9 | 383.7 | 45.6 | 115.9 | 15.9 | 467.6 | 574.6 | 22.3 | 108.3 | 17.6 | 19.9 | 16.7 | 15.8 | 16.1 | 18 | 16 | 15.9 | 18.8
179 | 17 | 440.5 | 176.2 | 205.9676 | 28.6 | 27.7 | 32.8 | 36.1 | 37.2 | 15.5 | 23.1 | 15.4 | 2.5 | 241.6 | 7.2 | 15.9 | 264.4 | 404.9 | 48 | 127.8 | 16.1 | 501 | 607.8 | 23.7 | 116.2 | 18.3 | 21.2 | 17 | 15.8 | 16.2 | 18.2 | 15.9 | 15.9 | 18.9
180 | 18 | 441.6 | 176.64 | 206.482 | 30.6 | 30.6 | 35.9 | 39.8 | 46.6 | 15.5 | 23.1 | 15.4 | 3.1 | 238.1 | 6.8 | 16.1 | 275.5 | 416.2 | 49.3 | 135.1 | 16.3 | 524.1 | 631.4 | 24.6 | 120.3 | 19.2 | 22.7 | 17.4 | 15.8 | 16.2 | 18.3 | 15.9 | 15.9 | 19.1
181 | 19 | 442 | 176.8 | 206.669 | 32.4 | 33.8 | 39 | 43.6 | 50.5 | 15.6 | 23.1 | 15.5 | 2.8 | 241 | 6.2 | 16.3 | 288.6 | 434.1 | 50.2 | 146.4 | 16.6 | 545.6 | 655.3 | 25.2 | 128.6 | 20.2 | 24.3 | 17.8 | 15.8 | 16.2 | 18.6 | 15.9 | 15.9 | 19.2
182 | 20 | 442.1 | 176.84 | 206.7158 | 35.5 | 37.6 | 42.1 | 47 | 54.7 | 15.6 | 23.1 | 15.5 | 3 | 256.2 | 5.4 | 16.5 | 297.7 | 451.1 | 51.3 | 156.2 | 16.8 | 562 | 677 | 26.3 | 134.5 | 21.2 | 26 | 18.2 | 15.8 | 16.3 | 18.6 | 16 | 15.9 | 19.3
183 | 21 | 444.6 | 177.84 | 207.8847 | 38.8 | 42.2 | 45.1 | 50.4 | 59.5 | 15.7 | 23.1 | 15.5 | 2.8 | 262.6 | 5.2 | 16.7 | 303.1 | 451.5 | 51.7 | 163.8 | 17.1 | 574.6 | 694.7 | 27.7 | 138.6 | 22.2 | 27.8 | 18.7 | 15.8 | 16.3 | 18.8 | 16 | 15.9 | 19.6
184 | 22 | 445.2 | 178.08 | 208.1653 | 42 | 46.6 | 48.4 | 53.8 | 67.4 | 15.7 | 23.1 | 15.5 | 3 | 252.1 | 5.9 | 17 | 315.1 | 461.8 | 51.7 | 170 | 17.4 | 596.7 | 711.1 | 29.3 | 145.2 | 23.4 | 29.7 | 19.2 | 15.8 | 16.4 | 19.1 | 16 | 15.9 | 19.7
185 | 23 | 444.7 | 177.88 | 207.9315 | 45.5 | 50.5 | 52.1 | 56.9 | 74.9 | 15.7 | 23 | 15.6 | 3.2 | 258.8 | 6.8 | 17.2 | 328.7 | 485.3 | 52.5 | 178.1 | 17.7 | 623.6 | 732.3 | 31.2 | 153.1 | 24.5 | 31.7 | 19.7 | 15.8 | 16.4 | 19.3 | 15.9 | 15.9 | 19.7
186 | 24 | 445.1 | 178.04 | 208.1185 | 49.6 | 54.2 | 56 | 60.1 | 81.9 | 15.7 | 23 | 15.7 | 2.6 | 250 | 6.5 | 17.6 | 349.7 | 521.5 | 54 | 186.6 | 18.1 | 652.1 | 747.4 | 33.1 | 165.5 | 25.7 | 33.7 | 20.2 | 15.8 | 16.5 | 19.5 | 16 | 16 | 19.8
187 | 25 | 445.3 | 178.12 | 208.212 | 53.7 | 58.4 | 59.9 | 64 | 91 | 15.8 | 23 | 15.9 | 2.5 | 242.1 | 6.1 | 17.9 | 362.9 | 534.3 | 54.8 | 193.6 | 18.4 | 672.9 | 758.8 | 34.7 | 173.8 | 26.9 | 35.7 | 20.7 | 15.8 | 16.5 | 20 | 16 | 16 | 20
188 | 26 | 445.7 | 178.28 | 208.399 | 57.7 | 62.2 | 64.3 | 68.1 | 99.7 | 15.8 | 23 | 16 | 2.7 | 257.8 | 5.7 | 18.2 | 376.8 | 547.2 | 56.1 | 203.7 | 18.9 | 683 | 757.2 | 35.5 | 183.3 | 28.1 | 37.6 | 21.2 | 15.8 | 16.6 | 20.2 | 16 | 16 | 20.2
189 | 27 | 447.4 | 178.96 | 209.1939 | 61.9 | 66.6 | 68.2 | 72.1 | 107.2 | 15.9 | 23 | 16.3 | 2.8 | 247.9 | 5.7 | 18.6 | 386.9 | 556.2 | 56 | 210.1 | 19.3 | 704.5 | 771 | 36.3 | 189.3 | 29.4 | 39.7 | 21.7 | 15.8 | 16.7 | 20.4 | 16 | 16 | 20.5
190 | 28 | 447.6 | 179.04 | 209.2874 | 65.8 | 72.1 | 72 | 76.2 | 112.5 | 15.9 | 23 | 16.6 | 2.8 | 233.5 | 7.2 | 19 | 398.7 | 572.8 | 56.1 | 215 | 19.7 | 720.3 | 773.5 | 37.5 | 198.5 | 30.7 | 41.6 | 22.2 | 15.8 | 16.7 | 20.9 | 15.9 | 16 | 20.7
191 | 29 | 447.6 | 179.04 | 209.2874 | 70.8 | 77.4 | 75.5 | 80.1 | 117.1 | 15.9 | 23 | 17 | 2.8 | 245.8 | 7.9 | 19.5 | 404.4 | 582.5 | 55 | 221.8 | 20.2 | 732.6 | 775.2 | 38.4 | 204.9 | 32.1 | 43.6 | 22.7 | 15.8 | 16.8 | 21.1 | 16 | 16 | 20.9
192 | 30 | 449.3 | 179.72 | 210.0823 | 76 | 82.3 | 79.3 | 84.1 | 120.8 | 15.9 | 23 | 17.6 | 2.9 | 240.3 | 8.1 | 19.9 | 411 | 587.9 | 54.1 | 224.6 | 20.7 | 738.2 | 779.1 | 38.9 | 211.3 | 33.5 | 45.5 | 23.3 | 15.8 | 16.9 | 21.3 | 16 | 16.1 | 21.1
193 | 31 | 448.4 | 179.36 | 209.6615 | 80.6 | 86.8 | 83.1 | 88.3 | 124 | 16 | 23 | 18.1 | 2.7 | 246.2 | 8.1 | 20.4 | 424 | 607.9 | 53 | 230.2 | 21.2 | 751.2 | 791.6 | 39.7 | 219.7 | 34.9 | 47.5 | 23.7 | 15.8 | 17 | 21.5 | 16 | 16.1 | 21.3
194 | 32 | 448.5 | 179.4 | 209.7083 | 84.4 | 90 | 86.6 | 92.6 | 127.7 | 16 | 23 | 18.6 | 2.9 | 242.3 | 8.1 | 20.9 | 434.2 | 611.7 | 51.8 | 239.2 | 21.8 | 764.4 | 792.3 | 40.6 | 231.1 | 36.4 | 49.4 | 24.3 | 15.8 | 17 | 21.5 | 16 | 16.1 | 21.8
195 | 33 | 447.3 | 178.92 | 209.1472 | 88.5 | 93.5 | 90 | 96.7 | 132.4 | 16 | 23 | 19.1 | 3.1 | 241.8 | 7.9 | 21.4 | 435 | 604 | 50.8 | 250.3 | 22.4 | 761.6 | 784 | 41.1 | 236.7 | 37.9 | 51.3 | 24.7 | 15.8 | 17.1 | 21.8 | 16 | 16.1 | 21.9
196 | 34 | 447.1 | 178.84 | 209.0537 | 92.3 | 95.7 | 93.3 | 101.1 | 138.3 | 16.1 | 23 | 19.6 | 2.7 | 242.5 | 7.6 | 22 | 440.1 | 610.4 | 50.5 | 260 | 22.9 | 768.5 | 795.2 | 42.1 | 246.3 | 39.3 | 53.3 | 25.3 | 15.8 | 17.2 | 21.9 | 16 | 16.2 | 22.1
197 | 35 | 448 | 179.2 | 209.4745 | 96 | 98.4 | 96.7 | 104.9 | 144.8 | 16.1 | 23 | 20.1 | 2.5 | 243.5 | 7.4 | 22.6 | 440.1 | 614.5 | 50.4 | 269.3 | 23.5 | 768.7 | 792.7 | 42.4 | 251.6 | 40.8 | 55.2 | 25.8 | 15.8 | 17.3 | 22.2 | 16 | 16.2 | 22.5
198 | 36 | 448.1 | 179.24 | 209.5212 | 98.5 | 102 | 100.3 | 108.5 | 150.4 | 16.1 | 23 | 20.5 | 2.9 | 249.7 | 7.1 | 23.2 | 437.8 | 613.7 | 50.6 | 276.6 | 24.1 | 773.3 | 788.8 | 42.6 | 254 | 42.4 | 57.3 | 26.4 | 15.8 | 17.4 | 22.7 | 16 | 16.2 | 22.9
199 | 37 | 449 | 179.6 | 209.9421 | 101.5 | 105.1 | 103.6 | 111.7 | 154.7 | 16.2 | 23 | 21 | 2.8 | 232.7 | 7.1 | 23.8 | 440.7 | 623.6 | 51.2 | 287 | 24.8 | 780 | 795.1 | 43.8 | 261.6 | 44 | 59.4 | 27 | 15.8 | 17.5 | 23.2 | 16 | 16.2 | 22.9
200 | 38 | 449.5 | 179.8 | 210.1758 | 103.8 | 109 | 106.8 | 114.8 | 158.3 | 16.2 | 23 | 21.5 | 2.6 | 238.2 | 6.6 | 24.5 | 441.4 | 619.4 | 51.9 | 295.2 | 25.4 | 782.5 | 794.3 | 44.8 | 267.7 | 45.5 | 61.6 | 27.6 | 15.8 | 17.6 | 23.6 | 16 | 16.3 | 23
201 | 39 | 451.5 | 180.6 | 211.111 | 106.2 | 113.5 | 109.9 | 117.8 | 165.2 | 16.3 | 23 | 21.9 | 2.4 | 243.1 | 5.7 | 25.2 | 443.7 | 627.6 | 52.5 | 304 | 26.1 | 783.2 | 790.8 | 45.7 | 277.6 | 47.1 | 63.8 | 28.1 | 15.8 | 17.7 | 23.5 | 16 | 16.3 | 23.1
202 | 40 | 452.9 | 181.16 | 211.7656 | 110.1 | 117.2 | 112.9 | 120.4 | 179.2 | 16.3 | 23 | 22.3 | 2.1 | 233.6 | 5.4 | 26 | 443.8 | 630.9 | 53.7 | 310.3 | 26.7 | 785.6 | 788.5 | 45.7 | 283.3 | 48.6 | 66.1 | 28.7 | 15.8 | 17.7 | 23.7 | 15.9 | 16.3 | 23.1
203 | 41 | 454.7 | 181.88 | 212.6072 | 114.3 | 121.4 | 115.8 | 122.9 | 181.5 | 16.3 | 23 | 22.8 | 2.2 | 245.3 | 6.2 | 26.8 | 436.7 | 617.6 | 54.2 | 315.6 | 27.4 | 782.5 | 787.7 | 45.2 | 284.5 | 50.1 | 68.3 | 29.3 | 15.8 | 17.8 | 23.8 | 15.9 | 16.4 | 23.2
204 | 42 | 453.3 | 181.32 | 211.9526 | 117.7 | 124.8 | 118.9 | 125.4 | 183.2 | 16.4 | 23 | 23.2 | 2.5 | 228.5 | 6.2 | 27.6 | 439.8 | 625.1 | 55.8 | 322.9 | 28.1 | 787.3 | 791.6 | 45.3 | 290.3 | 51.6 | 70.6 | 29.8 | 15.8 | 18 | 23.9 | 16 | 16.4 | 23.5
205 | 43 | 454.3 | 181.72 | 212.4202 | 121.4 | 127.5 | 121.6 | 128 | 184.3 | 16.4 | 23 | 23.6 | 2.7 | 212.9 | 6.1 | 28.4 | 444.1 | 634.6 | 57.6 | 330.1 | 28.8 | 795.4 | 798.4 | 45.7 | 297.3 | 53.1 | 72.8 | 30.4 | 15.8 | 18.1 | 24.2 | 16 | 16.4 | 23.8
206 | 44 | 455.4 | 182.16 | 212.9345 | 124.9 | 130 | 124 | 130.4 | 185.5 | 16.4 | 23 | 24.1 | 3 | 231.1 | 6.1 | 29.4 | 451.3 | 643 | 59.5 | 337.5 | 29.5 | 799.6 | 799.4 | 45.8 | 304.8 | 54.6 | 75 | 31.1 | 15.8 | 18.2 | 24.8 | 16 | 16.5 | 24.1
207 | 45 | 455.1 | 182.04 | 212.7943 | 128 | 132.3 | 126 | 132.7 | 187.8 | 16.4 | 23 | 24.6 | 2.6 | 240.3 | 6.2 | 30.3 | 456.7 | 650.3 | 61.2 | 344.8 | 30.1 | 797.6 | 792.8 | 45.8 | 312.7 | 56.1 | 77.1 | 32 | 15.8 | 18.3 | 24.8 | 16 | 16.5 | 24.3
208 | 46 | 456.1 | 182.44 | 213.2618 | 131.3 | 134.6 | 128.6 | 135.3 | 189.5 | 16.4 | 23 | 25 | 2.8 | 233.6 | 6 | 31.3 | 469.9 | 658.5 | 63.2 | 351.8 | 30.9 | 804.1 | 791.2 | 46.5 | 323.2 | 57.5 | 79.2 | 33 | 15.9 | 18.4 | 25.1 | 15.9 | 16.6 | 24.5
209 | 47 | 457.6 | 183.04 | 213.9632 | 134 | 136.6 | 131.2 | 137.1 | 191.3 | 16.4 | 23 | 25.4 | 2.4 | 228.4 | 5.7 | 32.3 | 483.5 | 661.2 | 64.9 | 358.9 | 31.6 | 812.8 | 793.1 | 47.5 | 336.2 | 59 | 81.1 | 35.1 | 15.9 | 18.5 | 25.4 | 16 | 16.6 | 24.8
210 | 48 | 458.6 | 183.44 | 214.4308 | 135.8 | 139 | 133.3 | 139.1 | 192.6 | 16.4 | 23 | 25.8 | 2.3 | 235.5 | 5.4 | 33.3 | 495 | 676.3 | 67.5 | 367.6 | 32.3 | 825.3 | 797.9 | 49.2 | 351.2 | 60.4 | 82.8 | 38.3 | 15.9 | 18.6 | 25.7 | 16 | 16.6 | 25.1
211 | 49 | 458.1 | 183.24 | 214.197 | 138.7 | 141.1 | 135.5 | 141.2 | 195.4 | 16.5 | 23 | 26.1 | 2.3 | 248 | 5.9 | 34.3 | 509.2 | 694 | 70.9 | 375.8 | 33 | 833.2 | 796 | 50.5 | 365 | 61.9 | 84.5 | 42.1 | 15.9 | 18.7 | 26.2 | 16 | 16.7 | 25.7
212 | 50 | 457.1 | 182.84 | 213.7294 | 140.7 | 142.8 | 137.7 | 143.6 | 197.5 | 16.5 | 22.9 | 26.5 | 2.1 | 210.8 | 5.6 | 35.3 | 520.8 | 700.8 | 73.4 | 380 | 33.8 | 838.1 | 798.2 | 51.2 | 374.1 | 63.5 | 86.2 | 45.2 | 15.9 | 18.8 | 26.3 | 16 | 16.7 | 25.9
213 | 51 | 457.1 | 182.84 | 213.7294 | 141.8 | 143.5 | 140.6 | 146.1 | 199.5 | 16.6 | 22.9 | 26.9 | 2.4 | 229 | 5 | 36.4 | 528 | 698.4 | 75.7 | 383.7 | 34.5 | 842.9 | 793.2 | 52.3 | 381.6 | 65.1 | 87.8 | 47.8 | 15.9 | 19 | 26.6 | 16 | 16.8 | 26.1
214 | 52 | 459.1 | 183.64 | 214.6646 | 143.2 | 144.3 | 143.2 | 148.9 | 201.6 | 16.6 | 22.9 | 27.2 | 2.3 | 252.8 | 5 | 37.4 | 530.5 | 695.4 | 78 | 384.7 | 35.3 | 850.2 | 791.1 | 53.9 | 391.1 | 67 | 89.5 | 51.1 | 15.9 | 19.1 | 26.7 | 16 | 16.8 | 26.1
215 | 53 | 459.3 | 183.72 | 214.7581 | 146.1 | 144.7 | 145.2 | 151.1 | 203.6 | 16.6 | 22.9 | 27.5 | 2.3 | 212.2 | 4.5 | 38.6 | 540.8 | 706 | 79.3 | 388.8 | 36.1 | 862.7 | 794.9 | 56.1 | 402.4 | 68.9 | 91.9 | 55.5 | 15.9 | 19.2 | 27.3 | 16 | 16.9 | 26.2
216 | 54 | 460 | 184 | 215.0854 | 149.3 | 146.2 | 147.1 | 153.4 | 204.9 | 16.6 | 22.9 | 27.8 | 2.5 | 187.4 | 3.8 | 39.8 | 547.7 | 716.6 | 79.9 | 394.8 | 36.9 | 869.9 | 800.3 | 58.7 | 414.3 | 70.9 | 95.7 | 59.3 | 15.9 | 19.3 | 27.6 | 16 | 17 | 26.6
217 | 55 | 459.8 | 183.92 | 214.9919 | 151.7 | 147 | 148.5 | 155.6 | 207.5 | 16.6 | 22.9 | 28.1 | 3.1 | 232.5 | 3.5 | 40.9 | 544.4 | 711.6 | 79.9 | 401.8 | 37.7 | 871 | 795.3 | 60.5 | 418.6 | 72.9 | 99.1 | 64.1 | 15.9 | 19.5 | 27.7 | 16 | 17 | 27
218 | 56 | 460.3 | 184.12 | 215.2257 | 152.9 | 147.4 | 150.5 | 158 | 212.9 | 16.7 | 22.9 | 28.4 | 2.7 | 233.8 | 3.8 | 42 | 551.1 | 722.2 | 83 | 409.4 | 38.5 | 880 | 796.8 | 62.8 | 429.5 | 75 | 102.2 | 68.6 | 15.9 | 19.6 | 28.4 | 16 | 17.1 | 27.4
219 | 57 | 461.1 | 184.44 | 215.5997 | 154.5 | 148.7 | 152.6 | 160 | 219 | 16.8 | 22.9 | 28.7 | 2.8 | 201.1 | 5 | 43.2 | 556.9 | 726.2 | 85.3 | 417.6 | 39.3 | 889.6 | 811.9 | 65.2 | 438.6 | 77.1 | 105.2 | 70.6 | 15.9 | 19.7 | 28.8 | 16 | 17.1 | 27.7
220 | 58 | 460.2 | 184.08 | 215.1789 | 157.1 | 149.4 | 154.5 | 161.9 | 226.4 | 16.8 | 22.9 | 29 | 2.8 | 219.8 | 5.7 | 44.5 | 560.2 | 737 | 89.1 | 427.7 | 40.2 | 897.1 | 814.2 | 67.4 | 447.6 | 79.3 | 108 | 74.7 | 15.9 | 19.9 | 28.9 | 16 | 17.2 | 27.7
221 | 59 | 461.5 | 184.6 | 215.7868 | 158.1 | 150.4 | 156.4 | 164 | 235 | 16.8 | 22.9 | 29.3 | 2.6 | 254.3 | 5.4 | 45.6 | 567.1 | 747.6 | 91.6 | 437.6 | 41 | 898.1 | 809.2 | 69.3 | 456.5 | 81.4 | 110.8 | 77 | 15.9 | 20 | 29.1 | 16 | 17.2 | 27.9
222 | 60 | 462.5 | 185 | 216.2543 | 158.1 | 151.7 | 158.3 | 165.9 | 237.2 | 16.9 | 22.9 | 29.6 | 2.5 | 247.7 | 4.8 | 46.8 | 576.4 | 752.4 | 94.3 | 445.1 | 41.9 | 899 | 805.5 | 72.1 | 468.5 | 83.5 | 113.4 | 80.9 | 15.9 | 20.2 | 29.4 | 16 | 17.3 | 28.4
223 | 61 | 461.8 | 184.72 | 215.927 | 157.8 | 153.1 | 160.2 | 168.1 | 236.6 | 17 | 22.9 | 29.9 | 2.8 | 241.9 | 4.4 | 48.1 | 584.6 | 756.4 | 94.3 | 457 | 42.8 | 898.8 | 804.4 | 75.4 | 480.5 | 85.7 | 116 | 87.1 | 15.9 | 20.3 | 29.6 | 16 | 17.4 | 28.9
224 | 62 | 460.9 | 184.36 | 215.5062 | 158.5 | 153.9 | 161.9 | 170.3 | 238.8 | 17.1 | 22.9 | 30.2 | 2.9 | 247.3 | 4.2 | 49.4 | 586.1 | 756.3 | 95.5 | 466.1 | 43.7 | 903.5 | 791.7 | 78.1 | 490.3 | 87.9 | 118.4 | 92 | 15.9 | 20.4 | 29.8 | 16 | 17.4 | 29.1
225 | 63 | 462.2 | 184.88 | 216.1141 | 159.5 | 154.5 | 163.3 | 172.1 | 241 | 17.1 | 22.9 | 30.5 | 2.8 | 245.2 | 4.1 | 50.6 | 581.5 | 742 | 94.9 | 470.8 | 44.5 | 886.4 | 775.8 | 80.3 | 493.6 | 90.2 | 120.7 | 96.3 | 15.9 | 20.6 | 30 | 16 | 17.5 | 29.3
226 | 64 | 463.8 | 185.52 | 216.8622 | 160.8 | 156.8 | 164.8 | 173.9 | 240 | 17.1 | 22.9 | 30.7 | 3 | 216.2 | 3.8 | 51.8 | 577.7 | 729.7 | 95 | 472.4 | 45.4 | 878.4 | 761.5 | 83 | 497.3 | 92.5 | 122.8 | 98.3 | 15.9 | 20.7 | 30.1 | 16 | 17.6 | 29.4
227 | 65 | 464.6 | 185.84 | 217.2363 | 161.9 | 158.7 | 166 | 175.7 | 237.8 | 17.1 | 22.9 | 31 | 2.7 | 204.9 | 3.5 | 53 | 578.9 | 723.1 | 95.4 | 476 | 46.3 | 872.5 | 749.8 | 86.3 | 501.5 | 95 | 125 | 99 | 15.9 | 20.9 | 30.2 | 16 | 17.6 | 29.7
228 | 66 | 465.7 | 186.28 | 217.7506 | 164.3 | 160.6 | 167.3 | 177.2 | 236.1 | 17.1 | 22.8 | 31.2 | 2.4 | 236.6 | 3.5 | 54.3 | 582.3 | 728 | 96.9 | 482.7 | 47.1 | 870.7 | 760.5 | 90.4 | 508.2 | 97.4 | 127.1 | 100 | 15.9 | 21 | 30.3 | 16 | 17.7 | 29.8
229 | 67 | 466 | 186.4 | 217.8909 | 165.8 | 162.3 | 168.5 | 178.5 | 235.5 | 17.2 | 22.8 | 31.4 | 2.3 | 252.2 | 3.6 | 55.5 | 576.5 | 722.6 | 99.6 | 487.2 | 48 | 874.6 | 761.5 | 93.6 | 511.4 | 99.8 | 129.3 | 103.2 | 16 | 21.2 | 30.5 | 16 | 17.8 | 29.9
230 | 68 | 465.6 | 186.24 | 217.7038 | 167.4 | 164.4 | 170.1 | 179.5 | 233.9 | 17.2 | 22.8 | 31.6 | 2.6 | 228.1 | 3.2 | 56.8 | 573.1 | 728.6 | 101.9 | 492.9 | 48.9 | 874.3 | 777.2 | 96.7 | 513.1 | 102.2 | 131.5 | 102.3 | 16 | 21.3 | 31.2 | 16 | 17.9 | 30
231 | 69 | 465 | 186 | 217.4233 | 168.4 | 166.5 | 171.9 | 180.7 | 232.4 | 17.3 | 22.8 | 31.9 | 2.8 | 186.7 | 3 | 58 | 576.6 | 733.9 | 105.7 | 496.2 | 49.8 | 879.5 | 789.8 | 102.4 | 517 | 104.6 | 133.9 | 102.5 | 16 | 21.4 | 31.4 | 16 | 17.9 | 30.6
232 | 70 | 465.5 | 186.2 | 217.6571 | 170.4 | 168.1 | 173.3 | 182.2 | 232.5 | 17.3 | 22.8 | 32.2 | 2.7 | 174.5 | 2.9 | 59.3 | 578.7 | 738 | 109.8 | 501.6 | 50.7 | 884.3 | 799.3 | 108.8 | 524.2 | 106.8 | 136.3 | 105.4 | 16 | 21.6 | 31.3 | 16 | 18 | 31
233 | 71 | 464.9 | 185.96 | 217.3765 | 172.4 | 170.1 | 174.4 | 183.5 | 232.2 | 17.3 | 22.8 | 32.4 | 2.9 | 226.8 | 3.4 | 60.7 | 578.4 | 728.2 | 112 | 505.4 | 51.6 | 883.2 | 796.2 | 114.8 | 528.4 | 109 | 138.7 | 109.3 | 16 | 21.7 | 31.6 | 16 | 18.1 | 31.2
234 | 72 | 464.3 | 185.72 | 217.096 | 172.7 | 170.2 | 175.4 | 184.8 | 231.5 | 17.3 | 22.8 | 32.6 | 3 | 223 | 4.7 | 62 | 573.6 | 717.6 | 114 | 509.7 | 52.5 | 877.4 | 789.5 | 120.9 | 531.4 | 111 | 141 | 111.5 | 16 | 21.9 | 32 | 16 | 18.2 | 31.4
235 | 73 | 464.7 | 185.88 | 217.283 | 173.1 | 170.6 | 176.3 | 185.5 | 229.3 | 17.3 | 22.8 | 32.8 | 2.9 | 201.1 | 5.6 | 63.3 | 572.1 | 719 | 118.7 | 511.8 | 53.3 | 880.6 | 796 | 126.8 | 535.8 | 112.9 | 143.3 | 113.7 | 16 | 22 | 32.3 | 16 | 18.3 | 31.8
236 | 74 | 466.4 | 186.56 | 218.0779 | 174.4 | 172.1 | 176.8 | 186.1 | 227.2 | 17.3 | 22.8 | 33 | 2.8 | 218.7 | 5.4 | 64.6 | 568.3 | 713.1 | 124.2 | 510.2 | 54.1 | 873 | 789.9 | 129.7 | 537.3 | 114.8 | 145.4 | 112.1 | 16 | 22.1 | 32.7 | 16 | 18.4 | 31.8
237 | 75 | 466.5 | 186.6 | 218.1246 | 175.9 | 172.7 | 177.4 | 187.3 | 226.5 | 17.4 | 22.8 | 33.2 | 2.8 | 224.9 | 4.9 | 66 | 570.6 | 718.4 | 129.9 | 510.6 | 55 | 875.9 | 791.6 | 136.7 | 541.9 | 116.6 | 147.3 | 107.8 | 16 | 22.3 | 33 | 16 | 18.5 | 32
238 | 76 | 466.3 | 186.52 | 218.0311 | 176.9 | 173.7 | 177.8 | 188.5 | 226.7 | 17.4 | 22.8 | 33.4 | 3 | 235.3 | 4.2 | 67.5 | 570.9 | 721.5 | 136.1 | 517.9 | 55.9 | 881.8 | 787.2 | 147.6 | 546.7 | 118.4 | 149 | 108.9 | 16 | 22.4 | 33 | 16 | 18.6 | 32.1
239 | 77 | 466.9 | 186.76 | 218.3117 | 176.6 | 174.2 | 178.5 | 189.7 | 226.7 | 17.5 | 22.8 | 33.6 | 2.9 | 248.4 | 3.7 | 69 | 568.9 | 710.6 | 140.1 | 528.9 | 56.9 | 883.7 | 771 | 157 | 552.2 | 120.1 | 150.5 | 111.9 | 16.1 | 22.6 | 33.4 | 16 | 18.7 | 32.4
240 | 78 | 467.6 | 187.04 | 218.639 | 175.7 | 173.7 | 179.3 | 191.2 | 226.3 | 17.5 | 22.8 | 33.8 | 2.6 | 217 | 3.6 | 70.5 | 571.4 | 712.8 | 144.7 | 537.9 | 57.9 | 891.3 | 763.2 | 167.9 | 559.5 | 121.6 | 151.8 | 115.7 | 16.1 | 22.7 | 33.5 | 16 | 18.8 | 32.6
241 | 79 | 467 | 186.8 | 218.3584 | 177.2 | 174.1 | 179.8 | 191.8 | 225.9 | 17.6 | 22.8 | 34 | 2.6 | 215.5 | 5 | 72.1 | 575 | 720.5 | 147.4 | 542.4 | 58.9 | 893.9 | 767.1 | 181.1 | 564.7 | 123.1 | 153 | 119.7 | 16.1 | 22.9 | 33.7 | 16 | 18.9 | 33.1
242 | 80 | 464.8 | 185.92 | 217.3298 | 179 | 176 | 180.5 | 192.3 | 230.6 | 17.7 | 22.8 | 34.2 | 2.3 | 220.8 | 5.3 | 73.6 | 574.6 | 714.1 | 149.4 | 545.6 | 59.9 | 891.1 | 773.2 | 189 | 567.9 | 124.6 | 154 | 122 | 16.1 | 23 | 33.9 | 16 | 19 | 33.4
243 | 81 | 466.1 | 186.44 | 217.9376 | 180.5 | 177.4 | 181.5 | 192.7 | 231.1 | 17.8 | 22.7 | 34.4 | 2.6 | 203.8 | 5.6 | 75.2 | 574.8 | 716.6 | 151.1 | 551.8 | 61 | 895.1 | 785.2 | 199.1 | 574.5 | 126 | 154.8 | 125.8 | 16.1 | 23.2 | 34.3 | 16 | 19.1 | 33.9
244 | 82 | 465.8 | 186.32 | 217.7973 | 181.8 | 178.2 | 182.4 | 193.5 | 230.4 | 17.9 | 22.7 | 34.6 | 2.7 | 235.3 | 5.8 | 76.7 | 574.7 | 724 | 152.4 | 558.3 | 62.1 | 902.8 | 792.8 | 210.2 | 579.3 | 127.6 | 155.5 | 131.7 | 16.1 | 23.3 | 34.6 | 16 | 19.2 | 34
245 | 83 | 465.2 | 186.08 | 217.5168 | 183 | 178.6 | 183 | 194.1 | 232.9 | 17.9 | 22.7 | 34.8 | 2.6 | 251.4 | 5.5 | 78.2 | 576.8 | 737.8 | 154.9 | 566 | 63.2 | 901.9 | 798.1 | 222.7 | 587.1 | 129.2 | 156.3 | 138.5 | 16.1 | 23.5 | 35.4 | 16 | 19.3 | 34.2
246 | 84 | 466.3 | 186.52 | 218.0311 | 183.8 | 179.5 | 183.6 | 194.6 | 234.8 | 18 | 22.7 | 35 | 2.4 | 235.7 | 5.5 | 79.6 | 576.5 | 744.8 | 156.5 | 567.1 | 64.4 | 903.2 | 806.9 | 229.5 | 589 | 130.8 | 157.2 | 143.7 | 16.1 | 23.7 | 35.6 | 16 | 19.4 | 34.4
247 | 85 | 466.6 | 186.64 | 218.1714 | 184.1 | 180.2 | 184.1 | 194.9 | 240.4 | 18.1 | 22.7 | 35.2 | 2.7 | 229.6 | 5.6 | 81 | 573.8 | 743.1 | 157.4 | 568.1 | 65.5 | 902.3 | 802.8 | 231.3 | 590.5 | 132.4 | 158 | 147.5 | 16.1 | 23.8 | 36.1 | 16 | 19.5 | 34.7
248 | 86 | 467.2 | 186.88 | 218.452 | 184.6 | 180.7 | 184.2 | 195.4 | 244.7 | 18.2 | 22.7 | 35.4 | 2.2 | 227 | 5.3 | 82.4 | 567.6 | 738.5 | 157.2 | 570.1 | 66.7 | 897.2 | 795.1 | 234.6 | 592.5 | 134 | 158.7 | 150 | 16.2 | 24 | 36.5 | 16 | 19.6 | 35.1
249 | 87 | 466.4 | 186.56 | 218.0779 | 185.2 | 181.4 | 184.5 | 196.2 | 244.1 | 18.3 | 22.7 | 35.6 | 2.4 | 219.9 | 5.1 | 83.9 | 565 | 731.4 | 157.3 | 573.3 | 67.9 | 896.5 | 779.1 | 238.1 | 595.8 | 135.5 | 159.1 | 153.9 | 16.2 | 24.2 | 36.4 | 16 | 19.7 | 35.5
250 | 88 | 468.1 | 187.24 | 218.8728 | 185.2 | 183 | 185.1 | 196.6 | 245.1 | 18.4 | 22.7 | 35.8 | 3.2 | 219.9 | 4.6 | 85.4 | 564.6 | 729.4 | 156.8 | 579 | 69.2 | 896.2 | 771.7 | 240.7 | 598.4 | 137.1 | 159.5 | 159 | 16.2 | 24.3 | 36.4 | 16 | 19.8 | 35.7
251 | 89 | 468.3 | 187.32 | 218.9663 | 186.2 | 184.4 | 185 | 197 | 244 | 18.5 | 22.7 | 36 | 3 | 240.3 | 4.2 | 87 | 563.8 | 721.1 | 155.6 | 585.1 | 70.5 | 893.8 | 760.9 | 244.4 | 602.2 | 138.3 | 159.8 | 165.5 | 16.2 | 24.5 | 36.4 | 16 | 20 | 36
252 | 90 | 466.2 | 186.48 | 217.9844 | 186.9 | 185 | 184.7 | 197.2 | 243.3 | 18.5 | 22.7 | 36.2 | 3.1 | 238.3 | 4.5 | 88.6 | 563.3 | 721.4 | 154.1 | 593.9 | 71.8 | 895.5 | 763 | 251.7 | 606.1 | 139.4 | 160.3 | 173.7 | 16.2 | 24.6 | 36.7 | 16 | 20.1 | 36.3
253 | 91 | 466.8 | 186.72 | 218.2649 | 187.3 | 186.1 | 185.4 | 197.7 | 243.6 | 18.6 | 22.7 | 36.3 | 2.8 | 206.4 | 4.6 | 90.2 | 562.3 | 733.5 | 152.9 | 601.7 | 73.1 | 901.7 | 773.9 | 255.5 | 610.4 | 140.6 | 160.9 | 184.3 | 16.2 | 24.8 | 37.1 | 16 | 20.2 | 36.6
254 | 92 | 467.7 | 187.08 | 218.6857 | 187.5 | 187.6 | 186.5 | 197.5 | 245.4 | 18.6 | 22.7 | 36.5 | 3 | 194.1 | 4.1 | 91.8 | 561.8 | 737.8 | 152.2 | 608.9 | 74.4 | 904.2 | 769.7 | 261.6 | 614.6 | 141.8 | 161.4 | 196.8 | 16.2 | 25 | 37.3 | 16.1 | 20.3 | 36.6
255 | 93 | 467.7 | 187.08 | 218.6857 | 188.1 | 187.9 | 187.5 | 197 | 245.8 | 18.6 | 22.6 | 36.8 | 3 | 208.2 | 3.4 | 93.4 | 565.3 | 747.6 | 151.9 | 614.3 | 75.8 | 902.1 | 789.8 | 267.8 | 621.2 | 143.2 | 161.9 | 211.3 | 16.3 | 25.1 | 37.6 | 16.1 | 20.4 | 37
256 | 94 | 467.8 | 187.12 | 218.7325 | 188.9 | 188.1 | 188.5 | 196.8 | 247.4 | 18.6 | 22.6 | 36.9 | 3 | 230.1 | 3.2 | 95 | 563.9 | 749.4 | 151.5 | 614.2 | 77.2 | 902.2 | 799.6 | 268.8 | 623.3 | 144.7 | 162.6 | 228.1 | 16.3 | 25.3 | 38.2 | 16.1 | 20.5 | 37.7
257 | 95 | 466.6 | 186.64 | 218.1714 | 189.7 | 189.1 | 189.5 | 197.2 | 248.3 | 18.6 | 22.6 | 37.1 | 3 | 246.2 | 3.4 | 96.6 | 562.8 | 756.2 | 151.5 | 612.9 | 78.9 | 901.2 | 802.1 | 268.9 | 624.9 | 146.1 | 163.5 | 239.5 | 16.3 | 25.5 | 38.4 | 16.1 | 20.6 | 37.6
258 | 96 | 468.5 | 187.4 | 219.0598 | 189.9 | 190.5 | 190.1 | 198.1 | 249.2 | 18.7 | 22.6 | 37.3 | 3 | 247 | 4.2 | 98.2 | 561.4 | 758.2 | 151.4 | 610.9 | 80.6 | 897 | 795.6 | 267.3 | 625.7 | 147.5 | 164.3 | 246.2 | 16.3 | 25.6 | 38.6 | 16.1 | 20.7 | 37.7
259 | 97 | 466.4 | 186.56 | 218.0779 | 190.2 | 191.3 | 190.4 | 199.1 | 250.2 | 18.8 | 22.6 | 37.5 | 2.5 | 249.9 | 4.8 | 99.9 | 558 | 764.1 | 151.7 | 609.1 | 82.3 | 896.1 | 801.3 | 267.5 | 626.6 | 148.9 | 165.4 | 245 | 16.3 | 25.8 | 39 | 16.1 | 20.8 | 38.1
260 | 98 | 465.2 | 186.08 | 217.5168 | 190.8 | 193 | 190.1 | 200.1 | 259.2 | 18.8 | 22.6 | 37.6 | 2.6 | 264.8 | 4.9 | 101.6 | 555.7 | 766.8 | 151.8 | 607.9 | 84.1 | 897.6 | 803.1 | 271.7 | 629.2 | 150.1 | 166.1 | 245.2 | 16.3 | 26 | 39.6 | 16.1 | 21 | 38.4
261 | 99 | 464.1 | 185.64 | 217.0025 | 191.6 | 195.7 | 190.2 | 201.2 | 264.3 | 18.9 | 22.6 | 37.8 | 3 | 263.6 | 5.4 | 103.5 | 554.1 | 759.2 | 152 | 612.2 | 85.6 | 895.6 | 787.1 | 272.5 | 634.4 | 151.3 | 166.9 | 251.1 | 16.4 | 26.2 | 39.7 | 16.1 | 21.1 | 38.8
262 | 100 | 465.5 | 186.2 | 217.6571 | 192.8 | 197 | 190.8 | 202.4 | 269.4 | 18.9 | 22.6 | 38 | 2.7 | 243.4 | 6 | 105.4 | 547.2 | 746.7 | 151 | 610.5 | 87.1 | 888.3 | 788.3 | 272.9 | 631.1 | 152.4 | 167.5 | 254.8 | 16.4 | 26.4 | 40 | 16.1 | 21.2 | 38.9
263 | 101 | 466.7 | 186.68 | 218.2182 | 194.2 | 197.6 | 191.1 | 203.3 | 268 | 19 | 22.6 | 38.1 | 2.9 | 232.5 | 5.3 | 107.3 | 545.2 | 744 | 150.5 | 611.9 | 88.5 | 883.9 | 795.4 | 274 | 632.8 | 153.4 | 168.1 | 258.7 | 16.4 | 26.6 | 40.3 | 16.1 | 21.3 | 39
264 | 102 | 467 | 186.8 | 218.3584 | 194.9 | 198.6 | 191.3 | 204.2 | 265.8 | 19 | 22.6 | 38.3 | 2.9 | 237.1 | 4.6 | 109.3 | 542.2 | 745.4 | 150.1 | 619.1 | 90 | 881.4 | 805.8 | 276.9 | 635.5 | 154.4 | 168.8 | 264.4 | 16.4 | 26.8 | 40.5 | 16.1 | 21.5 | 39.3
265 | 103 | 467.1 | 186.84 | 218.4052 | 194.4 | 198.1 | 192.1 | 204.7 | 264.6 | 19.1 | 22.6 | 38.5 | 2.9 | 251.8 | 4.2 | 111.3 | 540.8 | 750.7 | 149.8 | 622.7 | 91.5 | 883.8 | 815.2 | 280.2 | 638.8 | 155.3 | 169.5 | 273.7 | 16.4 | 27 | 40.8 | 16.1 | 21.6 | 39.8
266 | 104 | 467 | 186.8 | 218.3584 | 195 | 196.5 | 192.6 | 205 | 264.1 | 19.1 | 22.6 | 38.6 | 3.1 | 261.2 | 4.5 | 113.4 | 541.3 | 755.1 | 149.8 | 624.2 | 93 | 884 | 817.9 | 276.2 | 641.3 | 156.1 | 170.4 | 283 | 16.4 | 27.2 | 41.1 | 16.1 | 21.7 | 40.2
267 | 105 | 467 | 186.8 | 218.3584 | 195.7 | 196.3 | 193 | 205 | 263 | 19.1 | 22.6 | 38.8 | 3 | 248.8 | 5.5 | 115.4 | 542.8 | 765.9 | 150.3 | 625.9 | 94.7 | 882.1 | 834.8 | 274.2 | 644.7 | 156.9 | 171.4 | 291.4 | 16.5 | 27.4 | 41.4 | 16.1 | 21.8 | 40.5
268 | 106 | 466.6 | 186.64 | 218.1714 | 196.3 | 197.3 | 193.7 | 205.3 | 263.9 | 19.1 | 22.6 | 38.9 | 3.4 | 245.5 | 6.3 | 117.6 | 544.9 | 774.1 | 150.8 | 629 | 96.3 | 883.7 | 839 | 273.5 | 649.6 | 157.6 | 172.7 | 298.6 | 16.5 | 27.5 | 41.5 | 16.1 | 22 | 40.7
269 | 107 | 468 | 187.2 | 218.826 | 196.2 | 197.4 | 194.2 | 205.7 | 263.5 | 19.1 | 22.6 | 39.1 | 3.3 | 241.2 | 6.3 | 119.7 | 543.9 | 769 | 150.9 | 630 | 98 | 882.9 | 833.1 | 272.7 | 650.1 | 158.3 | 174.1 | 306.7 | 16.5 | 27.7 | 41.7 | 16.1 | 22.1 | 40.7
270 | 108 | 464.9 | 185.96 | 217.3765 | 196.5 | 198.1 | 194.6 | 206.5 | 261.4 | 19.2 | 22.6 | 39.2 | 3.3 | 254 | 6.9 | 121.8 | 544.4 | 762.9 | 150.8 | 629.8 | 99.6 | 882.6 | 814.7 | 271.1 | 651.1 | 159.1 | 175.4 | 314 | 16.5 | 27.9 | 42.1 | 16.1 | 22.3 | 41
271 | 109 | 466.6 | 186.64 | 218.1714 | 197.9 | 198.7 | 195.2 | 206.9 | 259.9 | 19.2 | 22.5 | 39.4 | 2.9 | 250.9 | 7.4 | 123.9 | 545.7 | 754.5 | 150.4 | 629.8 | 101.3 | 882.6 | 802 | 269.8 | 654.1 | 159.8 | 177.3 | 320.5 | 16.5 | 28.1 | 42.4 | 16.1 | 22.4 | 41.4
272 | 110 | 466.2 | 186.48 | 217.9844 | 199.3 | 198.3 | 196 | 207.2 | 261.5 | 19.3 | 22.5 | 39.6 | 2.9 | 249.5 | 7.1 | 126 | 545.5 | 754.6 | 149.6 | 628.7 | 102.9 | 887.2 | 805.6 | 269.4 | 657.4 | 160.6 | 178.9 | 325.3 | 16.6 | 28.3 | 42.4 | 16.1 | 22.5 | 41.9
273 | 111 | 467 | 186.8 | 218.3584 | 200.5 | 197.2 | 197.5 | 207.7 | 261.2 | 19.4 | 22.5 | 39.7 | 2.6 | 257.5 | 6.8 | 128.1 | 547.9 | 757.9 | 149.4 | 626.5 | 104.6 | 890.6 | 800.8 | 271.1 | 660.6 | 161.4 | 180.9 | 329.1 | 16.6 | 28.5 | 42.5 | 16.2 | 22.7 | 42.1
274 | 112 | 466.9 | 186.76 | 218.3117 | 201.5 | 196.2 | 199.1 | 208.4 | 260.7 | 19.4 | 22.5 | 39.8 | 2.7 | 257.4 | 7.6 | 130.3 | 553.8 | 766 | 149.6 | 631.9 | 106.3 | 892 | 791 | 274.7 | 666.3 | 162.2 | 183.6 | 334.8 | 16.6 | 28.6 | 43.2 | 16.2 | 22.8 | 42.3
275 | 113 | 466.5 | 186.6 | 218.1246 | 201.9 | 196.3 | 199.8 | 208.6 | 261.7 | 19.4 | 22.5 | 40 | 3 | 259.9 | 7.6 | 132.6 | 556.6 | 767.4 | 149.5 | 637.2 | 108.1 | 888.9 | 781.5 | 279 | 669.4 | 162.9 | 185.8 | 343.4 | 16.6 | 28.8 | 43.6 | 16.2 | 22.9 | 42.7
276 | 114 | 466.9 | 186.76 | 218.3117 | 201.8 | 196 | 200 | 208.9 | 262.9 | 19.5 | 22.5 | 40 | 3 | 258.9 | 7.6 | 134.9 | 560.1 | 772.7 | 149.8 | 643.8 | 109.8 | 879.8 | 768 | 283.4 | 673.2 | 163.8 | 188.7 | 353 | 16.6 | 29 | 43.9 | 16.2 | 23 | 43.2
277 | 115 | 467.7 | 187.08 | 218.6857 | 201.4 | 196.2 | 200.7 | 209.2 | 262.5 | 19.5 | 22.5 | 40.2 | 3 | 261.6 | 7 | 137.1 | 564.8 | 770.7 | 150.2 | 646.8 | 111.7 | 880.6 | 760.3 | 286.3 | 676 | 164.7 | 192.4 | 361.5 | 16.7 | 29.2 | 44.3 | 16.2 | 23.2 | 43.4
278 | 116 | 467.6 | 187.04 | 218.639 | 201.7 | 196 | 201.7 | 209.5 | 264.7 | 19.5 | 22.5 | 40.3 | 3.3 | 266.2 | 5.9 | 139.4 | 567.7 | 769.4 | 150.1 | 654.5 | 113.5 | 879 | 760.2 | 289 | 677.4 | 165.8 | 195.9 | 371.4 | 16.7 | 29.4 | 44.2 | 16.2 | 23.3 | 43.6
279 | 117 | 468.2 | 187.28 | 218.9195 | 200.6 | 196.1 | 203.2 | 209.9 | 266.2 | 19.5 | 22.5 | 40.4 | 2.9 | 280 | 5.3 | 141.7 | 567.6 | 770.3 | 150.3 | 658 | 115.5 | 879.2 | 756 | 290.6 | 679.4 | 167 | 198.8 | 378.4 | 16.7 | 29.6 | 44.4 | 16.2 | 23.5 | 44
280 | 118 | 467.5 | 187 | 218.5922 | 201.5 | 196.3 | 204.7 | 210.5 | 269.6 | 19.6 | 22.5 | 40.5 | 3.2 | 281.3 | 6.4 | 144.2 | 569 | 767.3 | 150.8 | 661.8 | 117.6 | 883.3 | 765.3 | 292 | 682.8 | 168.2 | 201.6 | 387.2 | 16.7 | 29.8 | 45.1 | 16.2 | 23.6 | 44.4
281 | 119 | 468.8 | 187.52 | 219.2001 | 202.6 | 197 | 205.7 | 210.9 | 269 | 19.6 | 22.5 | 40.7 | 3.4 | 265.2 | 8.1 | 146.5 | 567 | 771.4 | 150.9 | 664.6 | 119.8 | 882.6 | 776.6 | 293.6 | 683.3 | 169.6 | 205.3 | 396.3 | 16.8 | 30 | 45.3 | 16.2 | 23.7 | 44.6
282 | 120 | 468.3 | 187.32 | 218.9663 | 202.9 | 197.3 | 206 | 211.3 | 271.1 | 19.6 | 22.5 | 40.8 | 3.3 | 275.5 | 7.4 | 148.9 | 566.6 | 776 | 150.9 | 669 | 122.2 | 882.4 | 792.3 | 296.8 | 685.6 | 171.1 | 208 | 403 | 16.8 | 30.2 | 45.2 | 16.2 | 23.9 | 44.7
283 | 121 | 468.6 | 187.44 | 219.1066 | 201.7 | 197.2 | 206.7 | 211.6 | 273.9 | 19.7 | 22.5 | 40.9 | 3.2 | 260.6 | 6.6 | 151.4 | 567.7 | 780.2 | 151.5 | 671.9 | 124.8 | 878.4 | 803.1 | 301.7 | 688.9 | 172.5 | 211.3 | 410.3 | 16.8 | 30.4 | 45.5 | 16.2 | 24 | 45.3
284 | 122 | 467.6 | 187.04 | 218.639 | 201.5 | 196.8 | 206.6 | 212.2 | 273.6 | 19.7 | 22.5 | 41.1 | 3.1 | 250.1 | 6.7 | 153.9 | 570.3 | 786.3 | 153.1 | 675.9 | 127.3 | 876.6 | 810.1 | 306.5 | 693 | 174 | 214.8 | 419.8 | 16.8 | 30.6 | 46.1 | 16.2 | 24.2 | 45.7
285 | 123 | 468.7 | 187.48 | 219.1533 | 202 | 197.4 | 206.4 | 212.8 | 275.1 | 19.8 | 22.4 | 41.2 | 3 | 234.7 | 6.6 | 156.5 | 573.4 | 800.6 | 154.6 | 682.2 | 130 | 867.4 | 818.4 | 311.8 | 697.5 | 175.4 | 219 | 428.2 | 16.9 | 30.8 | 46.9 | 16.3 | 24.3 | 46
286 | 124 | 467.9 | 187.16 | 218.7793 | 202.8 | 198.4 | 206.3 | 213.6 | 279.7 | 19.9 | 22.4 | 41.4 | 2.9 | 240.4 | 6.2 | 159.1 | 576.4 | 801.3 | 155.8 | 685.5 | 132.7 | 868 | 811 | 315.7 | 699.4 | 176.8 | 222.5 | 436.3 | 16.9 | 31 | 46.9 | 16.3 | 24.5 | 46
287 | 125 | 468.3 | 187.32 | 218.9663 | 204.3 | 199.6 | 206.9 | 214 | 284.3 | 19.9 | 22.4 | 41.6 | 3.3 | 248.8 | 6.1 | 161.7 | 575.7 | 797.1 | 156.7 | 684.2 | 135.5 | 872 | 809.5 | 317.2 | 700 | 178.2 | 226 | 444.1 | 16.9 | 31.2 | 47.1 | 16.3 | 24.6 | 46.3
288 | 126 | 468 | 187.2 | 218.826 | 204.7 | 201.5 | 207.9 | 214.8 | 283.6 | 19.9 | 22.4 | 41.7 | 3.5 | 250.5 | 6.1 | 164.2 | 576.8 | 788.9 | 157.7 | 681.8 | 138.4 | 873.4 | 809.4 | 318.7 | 698.2 | 179.6 | 229.8 | 448.8 | 16.9 | 31.4 | 47.7 | 16.3 | 24.8 | 46.5
289 | 127 | 469.1 | 187.64 | 219.3403 | 204.5 | 203.5 | 209 | 215.7 | 283.6 | 20 | 22.4 | 41.9 | 3.3 | 274.5 | 5.2 | 166.7 | 577.4 | 787.3 | 158.8 | 686.7 | 141.3 | 872 | 798.1 | 320.4 | 698.9 | 181.1 | 232.6 | 450.1 | 17 | 31.6 | 47.6 | 16.3 | 24.9 | 46.7
290 | 128 | 468.9 | 187.56 | 219.2468 | 205.6 | 204.9 | 209.5 | 216.3 | 282.3 | 20.1 | 22.4 | 42 | 3.2 | 260.6 | 4.8 | 169.4 | 575.4 | 775.8 | 159.2 | 688.8 | 144.3 | 875.7 | 773.2 | 322 | 700.3 | 182.4 | 235.7 | 455.4 | 17 | 31.8 | 47.6 | 16.3 | 25.1 | 47.2
291 | 129 | 468.6 | 187.44 | 219.1066 | 206.3 | 206.2 | 209.4 | 216.6 | 280.5 | 20.2 | 22.4 | 42.2 | 2.9 | 226.1 | 4.8 | 172.1 | 574.5 | 768.8 | 159.9 | 690.8 | 147.2 | 876.2 | 765 | 324.2 | 701.2 | 183.7 | 239.5 | 459.1 | 17 | 32 | 48 | 16.3 | 25.2 | 47.6
292 | 130 | 467.8 | 187.12 | 218.7325 | 207.5 | 206.6 | 209.2 | 216.4 | 279.6 | 20.2 | 22.4 | 42.4 | 3 | 232.5 | 4.6 | 174.8 | 575.7 | 768.6 | 160.9 | 693.5 | 150.1 | 871.8 | 768.7 | 328.9 | 704 | 185.1 | 243.9 | 462.8 | 17 | 32.2 | 48.3 | 16.3 | 25.4 | 48.1
293 | 131 | 467.3 | 186.92 | 218.4987 | 209 | 206.4 | 209.6 | 216.3 | 280.9 | 20.3 | 22.4 | 42.5 | 3.3 | 257.5 | 5.4 | 177.6 | 574.5 | 768.3 | 161.6 | 694.8 | 153 | 880 | 769.5 | 333.4 | 705.7 | 186.3 | 249 | 468.6 | 17.1 | 32.3 | 48.7 | 16.3 | 25.5 | 48.3
294 | 132 | 468.3 | 187.32 | 218.9663 | 209.9 | 207.1 | 210.1 | 216.6 | 281 | 20.4 | 22.4 | 42.6 | 2.9 | 254.5 | 6.3 | 180.3 | 575.6 | 774.3 | 162.4 | 693.2 | 155.9 | 878.2 | 786.1 | 337.6 | 705.3 | 187.6 | 253.1 | 471.8 | 17.1 | 32.5 | 48.9 | 16.4 | 25.7 | 48.8
295 | 133 | 468.6 | 187.44 | 219.1066 | 209.4 | 207.4 | 211 | 217.5 | 280.6 | 20.5 | 22.4 | 42.8 | 3.3 | 249.1 | 6.6 | 183 | 575.6 | 780.2 | 163.7 | 694.5 | 158.7 | 881.1 | 798.1 | 342.1 | 706.8 | 188.8 | 256.5 | 470.7 | 17.1 | 32.7 | 49 | 16.4 | 25.8 | 48.9
296 | 134 | 467.8 | 187.12 | 218.7325 | 209.5 | 207.2 | 211.9 | 217.8 | 280.5 | 20.6 | 22.4 | 43 | 3.5 | 274.5 | 7.4 | 186 | 577.1 | 788.6 | 164.8 | 697.4 | 161.5 | 882.5 | 800 | 346.8 | 710.7 | 189.9 | 259.5 | 474.6 | 17.1 | 32.9 | 49.5 | 16.4 | 26 | 49
297 | 135 | 467.7 | 187.08 | 218.6857 | 209.2 | 206.4 | 212.2 | 218.2 | 278.8 | 20.6 | 22.4 | 43.1 | 3.9 | 253.1 | 7.5 | 189 | 578.6 | 785.7 | 165.8 | 693.3 | 164.3 | 885.4 | 799.5 | 350.8 | 712.2 | 190.9 | 264.6 | 476.6 | 17.2 | 33.1 | 49.8 | 16.4 | 26.1 | 49.5
298 | 136 | 466.5 | 186.6 | 218.1246 | 211.1 | 206.4 | 212.1 | 219 | 277.3 | 20.6 | 22.4 | 43.3 | 3.7 | 247.3 | 7.6 | 192 | 581.3 | 786.2 | 166.9 | 692.6 | 167 | 888.2 | 811.7 | 354.6 | 713.2 | 191.9 | 270.5 | 476.1 | 17.2 | 33.4 | 50.7 | 16.4 | 26.3 | 49.6
299 | 137 | 465.7 | 186.28 | 217.7506 | 212 | 206.5 | 212.2 | 219.5 | 279.3 | 20.7 | 22.3 | 43.5 | 3.4 | 251.1 | 8.3 | 195 | 585 | 794 | 168.3 | 694.7 | 169.7 | 884.6 | 819.7 | 358.3 | 715.2 | 193 | 276.1 | 475.6 | 17.2 | 33.6 | 51 | 16.4 | 26.4 | 49.9
300 | 138 | 466.9 | 186.76 | 218.3117 | 212.9 | 206.1 | 212.6 | 219.9 | 284.4 | 20.8 | 22.3 | 43.7 | 3.3 | 251.7 | 7.7 | 198.1 | 585.9 | 799.3 | 169.7 | 697.3 | 172.4 | 889.5 | 814.6 | 360.8 | 715.8 | 194.1 | 281.9 | 477.8 | 17.3 | 33.8 | 51 | 16.4 | 26.6 | 50.1
301 | 139 | 467 | 186.8 | 218.3584 | 213.8 | 206.9 | 212.6 | 220.8 | 287.2 | 20.9 | 22.3 | 43.9 | 3.8 | 249.2 | 7.4 | 201.3 | 587.1 | 801.5 | 170.9 | 700.7 | 175 | 890.3 | 813.8 | 363 | 716.8 | 195.1 | 287.3 | 483.1 | 17.3 | 34 | 51.4 | 16.4 | 26.8 | 50.5
302 | 140 | 467.5 | 187 | 218.5922 | 214.5 | 207.8 | 212 | 221.5 | 292.4 | 20.8 | 22.3 | 44 | 4.4 | 251.9 | 6.4 | 204.4 | 586.9 | 805.8 | 172.1 | 702.6 | 177.7 | 884.5 | 815.6 | 367.6 | 718.4 | 196.4 | 291.5 | 485.9 | 17.3 | 34.2 | 52 | 16.5 | 26.9 | 50.9
303 | 141 | 467.5 | 187 | 218.5922 | 214.4 | 209.4 | 211.7 | 222.3 | 293.1 | 20.9 | 22.3 | 44.1 | 3.7 | 253.8 | 7.4 | 207.5 | 586.2 | 799.8 | 173.1 | 702.3 | 180.4 | 887.1 | 785.6 | 371.4 | 720.6 | 197.6 | 296.9 | 484.8 | 17.3 | 34.4 | 52.1 | 16.5 | 27.1 | 51.6
304 | 142 | 466.6 | 186.64 | 218.1714 | 214.7 | 210.8 | 211.8 | 223 | 290.4 | 21 | 22.3 | 44.2 | 3.4 | 241.1 | 7.5 | 210.5 | 583.3 | 780.1 | 174.5 | 699.1 | 182.9 | 892.5 | 755.7 | 373.9 | 721.1 | 198.6 | 302.9 | 482.3 | 17.4 | 34.6 | 52.3 | 16.5 | 27.3 | 52.2
305 | 143 | 466.5 | 186.6 | 218.1246 | 215.9 | 211.4 | 211.1 | 223.4 | 287.8 | 20.9 | 22.3 | 44.4 | 3.1 | 245 | 7.2 | 213.4 | 586.5 | 786.4 | 175.4 | 697.6 | 185.6 | 889.6 | 761.5 | 378.3 | 723.4 | 200.1 | 309.7 | 480.2 | 17.4 | 34.8 | 52.7 | 16.5 | 27.4 | 52.3
306 | 144 | 467.1 | 186.84 | 218.4052 | 215.7 | 211.9 | 211.1 | 223.7 | 285.9 | 20.9 | 22.3 | 44.5 | 3.6 | 250.9 | 7.7 | 216.4 | 586.9 | 792.9 | 176.6 | 694.7 | 188.1 | 891.8 | 759.4 | 382 | 724.3 | 201.2 | 318 | 479.9 | 17.4 | 35 | 53.3 | 16.5 | 27.6 | 52.3
307 | 145 | 466.8 | 186.72 | 218.2649 | 215.4 | 212 | 211.8 | 223.1 | 284 | 20.9 | 22.3 | 44.6 | 3.8 | 233.7 | 8.2 | 219.3 | 590.1 | 791.4 | 178.3 | 694 | 190.5 | 888.5 | 747.9 | 385.8 | 726.2 | 202.5 | 324.5 | 478.4 | 17.5 | 35.3 | 53.4 | 16.5 | 27.8 | 52.5
308 | 146 | 467.7 | 187.08 | 218.6857 | 215.9 | 211.8 | 213 | 223.3 | 283.1 | 21 | 22.3 | 44.8 | 3.4 | 241.4 | 8.5 | 222.4 | 592.9 | 788.8 | 180.2 | 694.8 | 192.8 | 885.5 | 755.8 | 389.6 | 728.2 | 203.9 | 335.1 | 479.3 | 17.5 | 35.5 | 53.9 | 16.5 | 27.9 | 53.2
309 | 147 | 467 | 186.8 | 218.3584 | 216.3 | 211 | 214.2 | 223.7 | 284 | 21 | 22.3 | 45 | 3.4 | 232 | 7.6 | 225.3 | 592.5 | 789 | 182.8 | 696.5 | 195 | 881.2 | 764.1 | 394.5 | 729.6 | 205.1 | 342.9 | 481.2 | 17.5 | 35.7 | 54.4 | 16.5 | 28.1 | 53.7
310 | 148 | 467.3 | 186.92 | 218.4987 | 217.3 | 211.3 | 215.1 | 224.2 | 284.4 | 21.1 | 22.3 | 45.1 | 3.4 | 246.1 | 6.5 | 228.3 | 593.2 | 788.8 | 185.2 | 697.9 | 197.1 | 880.6 | 764.1 | 398.9 | 732.6 | 206.4 | 349.5 | 483.3 | 17.6 | 35.9 | 54.5 | 16.6 | 28.2 | 53.9
311 | 149 | 467.9 | 187.16 | 218.7793 | 217.8 | 211.2 | 215.9 | 225.1 | 283.5 | 21.2 | 22.3 | 45.3 | 4.1 | 270 | 5.9 | 231.3 | 593.1 | 785.2 | 187.5 | 699.7 | 199.2 | 876.3 | 772.2 | 403.4 | 733.8 | 207.7 | 357.4 | 486.7 | 17.6 | 36.1 | 54.6 | 16.6 | 28.4 | 54.4
312 | 150 | 467.5 | 187 | 218.5922 | 218.2 | 210.7 | 216.3 | 226.1 | 282.6 | 21.3 | 22.3 | 45.4 | 3.5 | 233.9 | 5.8 | 234.2 | 593.9 | 791.5 | 189.5 | 697.6 | 201.2 | 871.2 | 790.7 | 408.3 | 734.3 | 209 | 368.6 | 488.7 | 17.7 | 36.3 | 55 | 16.6 | 28.6 | 54.4
313 | 151 | 467.6 | 187.04 | 218.639 | 218.9 | 210 | 216.6 | 226.5 | 283.1 | 21.4 | 22.2 | 45.5 | 3.4 | 237.8 | 5.6 | 237 | 595.2 | 801.9 | 191.8 | 697.9 | 203.2 | 871.2 | 801.3 | 412.7 | 734.7 | 210.3 | 380 | 491.6 | 17.7 | 36.6 | 55.3 | 16.6 | 28.7 | 54.5
314 | 152 | 467.8 | 187.12 | 218.7325 | 218.2 | 209.5 | 217 | 226.8 | 285.5 | 21.5 | 22.2 | 45.6 | 3.5 | 253.3 | 5.5 | 239.7 | 594.8 | 803.3 | 193.5 | 698 | 205.4 | 870.4 | 804.6 | 418.4 | 735 | 211.6 | 387.7 | 495.4 | 17.7 | 36.8 | 55.5 | 16.6 | 28.9 | 54.8
315 | 153 | 467.5 | 187 | 218.5922 | 218.9 | 209.6 | 217.7 | 227.2 | 285.6 | 21.6 | 22.2 | 45.7 | 3.1 | 233.4 | 5.4 | 242.2 | 593.7 | 797.2 | 194.6 | 696.4 | 207.7 | 874.9 | 792.1 | 421.9 | 735.6 | 212.8 | 395.5 | 497.1 | 17.8 | 37 | 56.2 | 16.6 | 29.1 | 55.1
316 | 154 | 468 | 187.2 | 218.826 | 219.3 | 211.1 | 217.8 | 228 | 284.2 | 21.7 | 22.2 | 45.7 | 3.4 | 233.9 | 5.6 | 244.2 | 591.4 | 786.2 | 196.6 | 699.1 | 210.1 | 874.8 | 793.3 | 426 | 733.8 | 214 | 407.3 | 499.9 | 17.8 | 37.2 | 56.4 | 16.7 | 29.2 | 55.4
317 | 155 | 467.5 | 187 | 218.5922 | 220.5 | 212.4 | 218.5 | 228.7 | 289.7 | 21.8 | 22.2 | 45.8 | 3.3 | 241.7 | 5.9 | 246.2 | 590.2 | 792.8 | 198.2 | 701.8 | 212.4 | 873.2 | 786.3 | 429.5 | 735.4 | 215.2 | 413.7 | 502.8 | 17.8 | 37.4 | 56.6 | 16.7 | 29.4 | 55.7
318 | 156 | 467.2 | 186.88 | 218.452 | 221.6 | 214.7 | 219.7 | 229.8 | 294.7 | 21.9 | 22.2 | 45.9 | 3.2 | 246.7 | 6.3 | 248.4 | 592.4 | 788 | 198.8 | 703.5 | 214.7 | 876.5 | 765.1 | 433.4 | 738.3 | 216.3 | 422.2 | 507.2 | 17.9 | 37.6 | 57.1 | 16.7 | 29.6 | 56.2
319 | 157 | 467.1 | 186.84 | 218.4052 | 222.1 | 216.9 | 220 | 230.3 | 294.5 | 21.9 | 22.2 | 46.1 | 3.1 | 230.9 | 6.8 | 250.5 | 596.3 | 781.5 | 200.2 | 706.6 | 217 | 884.7 | 743.8 | 437.3 | 738.5 | 217.4 | 432.5 | 513.5 | 17.9 | 37.9 | 57.8 | 16.7 | 29.7 | 56.8
320 | 158 | 467.5 | 187 | 218.5922 | 222.3 | 217.4 | 219.3 | 230.8 | 292.7 | 22 | 22.2 | 46.2 | 3.2 | 238.7 | 7 | 252.5 | 596.7 | 787 | 204.1 | 711 | 219.5 | 882 | 742.1 | 441.7 | 740.3 | 218.5 | 441.8 | 519.8 | 17.9 | 38.1 | 57.9 | 16.7 | 29.9 | 57.1
321 | 159 | 467.8 | 187.12 | 218.7325 | 222.8 | 218.9 | 219.5 | 231.3 | 294.1 | 22.2 | 22.2 | 46.4 | 3.2 | 243 | 6.6 | 254.7 | 597.4 | 789.6 | 207.4 | 711.5 | 222.2 | 880.4 | 754.8 | 446.6 | 740.8 | 219.4 | 454.5 | 525.8 | 18 | 38.3 | 58.1 | 16.7 | 30 | 57.2
322 | 160 | 468.3 | 187.32 | 218.9663 | 223.3 | 219 | 219.8 | 231.4 | 292.9 | 22.3 | 22.2 | 46.6 | 3.7 | 245.1 | 6.5 | 256.7 | 600 | 793.2 | 209.4 | 713.8 | 224.9 | 881.6 | 766.7 | 450.9 | 741.7 | 220.3 | 462.3 | 530.5 | 18 | 38.5 | 58.5 | 16.8 | 30.2 | 57.5
323 | 161 | 468.3 | 187.32 | 218.9663 | 223.3 | 218.8 | 219.8 | 231.2 | 293.4 | 22.3 | 22.2 | 46.7 | 3.5 | 238 | 7 | 258.7 | 601 | 804.2 | 212.5 | 714.6 | 227.6 | 881.1 | 780.1 | 455.1 | 742.8 | 221.2 | 470.4 | 532.9 | 18.1 | 38.8 | 58.9 | 16.8 | 30.4 | 57.8
324 | 162 | 467.9 | 187.16 | 218.7793 | 223.2 | 218.5 | 219.8 | 230.7 | 297.7 | 22.4 | 22.2 | 47 | 3.8 | 238.8 | 6.7 | 260.9 | 600.4 | 802.6 | 215.6 | 718.1 | 230 | 877.5 | 785.4 | 459.6 | 744.3 | 222.3 | 478.7 | 536 | 18.1 | 39 | 59 | 16.8 | 30.6 | 57.8
325 | 163 | 467.3 | 186.92 | 218.4987 | 222.9 | 219.6 | 219.9 | 230.8 | 300.3 | 22.4 | 22.2 | 47.2 | 3.8 | 239.3 | 6.9 | 263.1 | 598.6 | 802.5 | 220 | 720.7 | 232.5 | 883.1 | 764.4 | 463.6 | 744.8 | 223.3 | 488 | 540 | 18.2 | 39.3 | 59.3 | 16.8 | 30.7 | 58
326 | 164 | 467.4 | 186.96 | 218.5455 | 223.6 | 221.7 | 220.2 | 231.3 | 302.3 | 22.5 | 22.2 | 47.4 | 3.3 | 242.8 | 7.3 | 265.2 | 598.1 | 789.2 | 224.4 | 721.9 | 234.9 | 883.7 | 755.5 | 467.6 | 744.1 | 224.1 | 495.4 | 542.9 | 18.2 | 39.5 | 59.6 | 16.8 | 30.9 | 58.4
327 | 165 | 468 | 187.2 | 218.826 | 224.3 | 222.9 | 220.1 | 231.8 | 300.6 | 22.6 | 22.2 | 47.5 | 3.5 | 254.3 | 7 | 267.4 | 600.1 | 796 | 228.8 | 725.6 | 237.3 | 878.2 | 770.7 | 471.2 | 745.5 | 224.6 | 502.5 | 545.5 | 18.2 | 39.7 | 60.1 | 16.8 | 31.1 | 58.8
328 | 166 | 467.1 | 186.84 | 218.4052 | 224.8 | 223.7 | 220.1 | 232.5 | 307.8 | 22.7 | 22.2 | 47.6 | 3.3 | 243.7 | 6.5 | 269.7 | 599.8 | 798.5 | 231.3 | 728.5 | 239.7 | 872.4 | 773.7 | 474.5 | 746.8 | 224.7 | 508.5 | 548 | 18.3 | 39.9 | 60.8 | 16.9 | 31.2 | 59.3
329 | 167 | 467.2 | 186.88 | 218.452 | 224.7 | 225.2 | 220.4 | 233 | 314 | 22.7 | 22.2 | 47.7 | 2.9 | 245.6 | 6.2 | 272 | 600.5 | 799.7 | 232.9 | 729.5 | 242.1 | 870.1 | 787.7 | 478.5 | 746.8 | 224.7 | 516.6 | 551.9 | 18.3 | 40.1 | 61.2 | 16.9 | 31.4 | 59.8
330 | 168 | 467.9 | 187.16 | 218.7793 | 224.2 | 226.8 | 220.5 | 233.3 | 320.2 | 22.8 | 22.2 | 47.8 | 2.9 | 255.9 | 5.6 | 274.2 | 601.2 | 805.5 | 234.7 | 729.4 | 244.5 | 869.3 | 798.3 | 483 | 746.9 | 225 | 520.9 | 553.5 | 18.4 | 40.4 | 61.6 | 16.9 | 31.6 | 59.9
331 | 169 | 467.4 | 186.96 | 218.5455 | 225.2 | 228.3 | 221.5 | 233.1 | 319.8 | 22.8 | 22.2 | 47.9 | 2.8 | 256.3 | 5.3 | 276.2 | 602.4 | 799.3 | 234.9 | 726.8 | 246.9 | 870.6 | 806.4 | 487.4 | 744.4 | 225.1 | 526.3 | 551.4 | 18.4 | 40.6 | 62 | 16.9 | 31.8 | 60.1
332 | 170 | 468.3 | 187.32 | 218.9663 | 226.8 | 228.9 | 222.7 | 233.3 | 320.4 | 23 | 22.2 | 48 | 3.2 | 236.9 | 5.3 | 278.2 | 600.2 | 793.9 | 235.9 | 728.9 | 249.1 | 867.7 | 818.4 | 491.4 | 745.5 | 224.6 | 530.1 | 550 | 18.5 | 40.9 | 62.3 | 16.9 | 32 | 60.5
333 | 171 | 465.8 | 186.32 | 217.7973 | 228.2 | 229.2 | 223 | 233.8 | 323.6 | 23.1 | 22.1 | 48.1 | 3.3 | 251 | 5.2 | 280.3 | 599.7 | 794.9 | 237.8 | 728.5 | 251.5 | 869 | 821.6 | 496.2 | 746.7 | 223.8 | 534.9 | 549 | 18.5 | 41.1 | 62.9 | 17 | 32.2 | 60.7
334 | 172 | 467.9 | 187.16 | 218.7793 | 229.5 | 229.2 | 223.6 | 234.2 | 326.8 | 23.2 | 22.1 | 48.2 | 3.4 | 271.6 | 5.1 | 282.3 | 598.1 | 788.7 | 238.8 | 728 | 253.8 | 869 | 827.2 | 500.6 | 746.3 | 223.7 | 539.3 | 549.1 | 18.6 | 41.3 | 63 | 17 | 32.3 | 61
335 | 173 | 466.6 | 186.64 | 218.1714 | 229.7 | 230.1 | 224.3 | 234.9 | 323.5 | 23.3 | 22.1 | 48.4 | 3.3 | 267.1 | 5.2 | 284.2 | 596.8 | 787.3 | 239.9 | 729.2 | 256.1 | 871 | 820 | 505.5 | 747 | 223.6 | 542.7 | 548.1 | 18.6 | 41.6 | 63.2 | 17 | 32.5 | 61.3
336 | 174 | 467.4 | 186.96 | 218.5455 | 229.2 | 230.1 | 224.5 | 235.4 | 317.7 | 23.4 | 22.1 | 48.6 | 3.5 | 247.9 | 5.8 | 286.1 | 596.2 | 782.8 | 241.9 | 731 | 258.5 | 869.1 | 821.9 | 510.9 | 748.1 | 223.8 | 545.7 | 549.6 | 18.7 | 41.8 | 63.5 | 17 | 32.7 | 61.6
337 | 175 | 465.3 | 186.12 | 217.5636 | 229.4 | 230.6 | 224.7 | 235.2 | 316.4 | 23.6 | 22.1 | 48.8 | 3.4 | 259.9 | 6.1 | 287.9 | 596.3 | 787.5 | 244.4 | 734.5 | 260.8 | 859.4 | 824.6 | 516.7 | 749.7 | 224.5 | 549.8 | 552.4 | 18.7 | 42.1 | 63.9 | 17.1 | 32.9 | 62.1
338 | 176 | 467.6 | 187.04 | 218.639 | 229.8 | 230.9 | 224.6 | 235.3 | 314.6 | 23.6 | 22.1 | 48.9 | 3.3 | 279.7 | 5.7 | 289.9 | 597.1 | 790 | 246.3 | 737.5 | 263.2 | 847.4 | 825.8 | 522.3 | 751.1 | 225.1 | 552.9 | 554.6 | 18.8 | 42.3 | 64.5 | 17.1 | 33.1 | 62.4
339 | 177 | 467.2 | 186.88 | 218.452 | 228.5 | 231 | 223.9 | 235.7 | 312.7 | 23.6 | 22.1 | 49.1 | 3.4 | 283.8 | 6 | 292 | 598.7 | 798.7 | 248.3 | 739.7 | 265.6 | 842.3 | 822.1 | 528.6 | 753.4 | 225.9 | 555.7 | 557.8 | 18.8 | 42.6 | 64.7 | 17.1 | 33.3 | 62.9
340 | 178 | 467.3 | 186.92 | 218.4987 | 228.5 | 230.9 | 223.2 | 235.3 | 311.4 | 23.6 | 22.1 | 49.2 | 3.3 | 256.8 | 6.4 | 294.1 | 603.4 | 803.6 | 250.2 | 741.6 | 268 | 835.9 | 830.6 | 534.9 | 754.9 | 226.9 | 560.4 | 561.4 | 18.9 | 42.8 | 65.2 | 17.1 | 33.4 | 63.2
341 | 179 | 468.5 | 187.4 | 219.0598 | 228.6 | 231.3 | 223 | 235.1 | 310.6 | 23.7 | 22.1 | 49.4 | 4.3 | 253.4 | 7.5 | 296.2 | 605.5 | 804.1 | 251.8 | 739.4 | 270.4 | 832 | 840.2 | 540.6 | 755.1 | 227.4 | 565.2 | 562.9 | 19 | 43 | 65.6 | 17.2 | 33.6 | 63.4
342 | 180 | 468.7 | 187.48 | 219.1533 | 229 | 230.5 | 223.6 | 235.5 | 309.2 | 23.7 | 22.1 | 49.6 | 4.4 | 246.8 | 8.3 | 298.2 | 607.1 | 809 | 253.1 | 741.9 | 272.9 | 830.1 | 846.8 | 546.2 | 755.2 | 228.3 | 569.3 | 564.5 | 19 | 43.3 | 65.8 | 17.2 | 33.8 | 63.7
343 | 181 | 468.2 | 187.28 | 218.9195 | 229.5 | 229.9 | 224.5 | 236.2 | 307.4 | 23.8 | 22.1 | 49.7 | 4 | 258.6 | 8 | 300.1 | 608.1 | 814.5 | 255.1 | 742.7 | 275.6 | 830.4 | 859.8 | 551.7 | 755.8 | 230.2 | 574.6 | 566.7 | 19.1 | 43.6 | 66.3 | 17.2 | 34 | 63.9
344 | 182 | 467.7 | 187.08 | 218.6857 | 230.1 | 230.5 | 225.2 | 236.8 | 309.2 | 23.9 | 22.1 | 49.9 | 3.8 | 247.6 | 7.6 | 302 | 607.4 | 814.4 | 256.1 | 739 | 278 | 833.8 | 846.5 | 556.7 | 754.4 | 233.4 | 577.6 | 564.3 | 19.1 | 43.8 | 66.8 | 17.2 | 34.2 | 64.1
345 | 183 | 467.8 | 187.12 | 218.7325 | 231 | 231.4 | 226.7 | 237.8 | 310.5 | 24 | 22.1 | 50.1 | 3.6 | 250 | 7.1 | 303.8 | 605.6 | 815.7 | 257 | 740 | 280.5 | 834.6 | 839.5 | 562 | 754.3 | 236.9 | 580.5 | 562.2 | 19.2 | 44.1 | 67.5 | 17.3 | 34.4 | 64.5
346 | 184 | 466.7 | 186.68 | 218.2182 | 232.9 | 232.8 | 228.7 | 238.8 | 324.5 | 24 | 22 | 50.3 | 3.4 | 244.2 | 6.7 | 305.6 | 604.8 | 813.6 | 258.2 | 739.8 | 283 | 834.5 | 828.7 | 567.4 | 754.3 | 240.3 | 584 | 561 | 19.2 | 44.4 | 68.2 | 17.3 | 34.6 | 65.1
347 | 185 | 466.9 | 186.76 | 218.3117 | 233.7 | 233.5 | 230.4 | 239.1 | 331.1 | 24.1 | 22 | 50.4 | 3.3 | 246 | 5.9 | 307.4 | 603.7 | 812.1 | 259.2 | 740.1 | 285.5 | 832.9 | 828.9 | 572.8 | 754.7 | 243.6 | 587.4 | 560.7 | 19.3 | 44.6 | 68.2 | 17.3 | 34.8 | 65.3
348 | 186 | 466.1 | 186.44 | 217.9376 | 233.5 | 235.3 | 231.9 | 239.6 | 330.7 | 24.1 | 22 | 50.5 | 3.6 | 256 | 5.4 | 309.2 | 604.2 | 814.6 | 261.1 | 742.4 | 287.9 | 830.2 | 837.4 | 578.1 | 756.1 | 246.1 | 590.9 | 561.2 | 19.4 | 44.9 | 68.5 | 17.3 | 35 | 65.4
349 | 187 | 467.4 | 186.96 | 218.5455 | 233.7 | 235.9 | 232.6 | 240.4 | 327.1 | 24.2 | 22 | 50.6 | 3.5 | 262.7 | 6.4 | 310.9 | 602.9 | 804.5 | 262 | 742.6 | 290.3 | 829.4 | 836.2 | 583 | 755 | 248.2 | 595.7 | 561.9 | 19.4 | 45.2 | 68.7 | 17.4 | 35.2 | 65.6
350 | 188 | 466.9 | 186.76 | 218.3117 | 232.3 | 236 | 232.8 | 241.2 | 328.4 | 24.3 | 22 | 50.6 | 3.7 | 242.6 | 6.1 | 312.4 | 604.3 | 803.9 | 263.4 | 743.6 | 292.6 | 832.2 | 836 | 587.6 | 753.9 | 249.8 | 598.9 | 562.9 | 19.5 | 45.4 | 69.5 | 17.4 | 35.4 | 66
351 | 189 | 466.7 | 186.68 | 218.2182 | 232.5 | 237.4 | 232.8 | 241.5 | 328.2 | 24.3 | 22 | 50.6 | 3.5 | 234.4 | 7 | 314.1 | 604.6 | 812.9 | 265.1 | 744.7 | 294.9 | 833.6 | 847.7 | 591.5 | 753.8 | 251.5 | 602.5 | 561.1 | 19.6 | 45.7 | 70 | 17.4 | 35.6 | 66.4
352 | 190 | 467.6 | 187.04 | 218.639 | 232.8 | 238.9 | 232.9 | 242 | 329.4 | 24.3 | 22 | 50.7 | 4.1 | 253.6 | 6.9 | 315.8 | 606.5 | 818.5 | 267 | 748.3 | 297.2 | 826.4 | 857.2 | 595.9 | 756.7 | 253.3 | 605.9 | 563.1 | 19.6 | 45.9 | 70.8 | 17.4 | 35.8 | 66.9
353 | 191 | 467.4 | 186.96 | 218.5455 | 232.9 | 239.3 | 233.1 | 242.9 | 330.2 | 24.4 | 22 | 50.8 | 4.7 | 246.8 | 7.5 | 317.6 | 605.1 | 818.2 | 268.2 | 746.7 | 299.5 | 828.1 | 845.2 | 600.2 | 757 | 255.1 | 609.9 | 563.2 | 19.7 | 46.2 | 71 | 17.5 | 36 | 67.2
354 | 192 | 467.9 | 187.16 | 218.7793 | 234.4 | 239.1 | 234.5 | 243.7 | 326.1 | 24.4 | 22 | 50.9 | 3.6 | 245.9 | 7.7 | 319.1 | 604.4 | 813.6 | 269.6 | 746.8 | 301.7 | 831.4 | 826.9 | 603.8 | 755.1 | 256.5 | 611.8 | 562.8 | 19.8 | 46.4 | 71.1 | 17.5 | 36.2 | 67.6
355 | 193 | 467.3 | 186.92 | 218.4987 | 234.7 | 238.9 | 235.4 | 244.1 | 321.3 | 24.5 | 22 | 51 | 2.9 | 241.4 | 7 | 320.7 | 603.4 | 807.9 | 271 | 748 | 303.9 | 835.1 | 818 | 608 | 756.8 | 257.7 | 613.1 | 563.6 | 19.8 | 46.7 | 71.6 | 17.5 | 36.4 | 68.3
356 | 194 | 466.3 | 186.52 | 218.0311 | 235.2 | 239.4 | 236.1 | 244.5 | 324.4 | 24.5 | 22 | 51.1 | 3.3 | 245.9 | 6.3 | 322.4 | 603.9 | 804 | 272 | 746.3 | 306 | 836.5 | 815.5 | 612.1 | 756 | 259 | 614.6 | 564.9 | 19.9 | 46.9 | 71.9 | 17.6 | 36.6 | 68.4
357 | 195 | 463.5 | 185.4 | 216.7219 | 235.6 | 239.4 | 236.5 | 244.6 | 324 | 24.4 | 22 | 51.1 | 3.3 | 240.1 | 5.9 | 324.1 | 604 | 806.3 | 273.5 | 746.5 | 308.3 | 837.5 | 819.8 | 615.9 | 756 | 260.2 | 616.1 | 566.7 | 20 | 47.2 | 72.5 | 17.6 | 36.9 | 68.5
358 | 196 | 465.2 | 186.08 | 217.5168 | 234.9 | 238.8 | 237 | 244.9 | 324.6 | 24.4 | 22 | 51.2 | 3.4 | 237.5 | 6.7 | 325.9 | 604.4 | 806.8 | 275.4 | 746 | 310.7 | 836 | 832.5 | 618.6 | 756.4 | 261.8 | 619.6 | 567.8 | 20 | 47.5 | 72.9 | 17.6 | 37.1 | 68.7
359 | 197 | 467.6 | 187.04 | 218.639 | 235 | 238.4 | 237.7 | 245.6 | 324.1 | 24.4 | 21.9 | 51.3 | 3.7 | 239.9 | 6.7 | 327.6 | 604.2 | 809.3 | 277.1 | 745.7 | 312.9 | 833.5 | 839 | 620.6 | 756.2 | 263.2 | 621.2 | 568 | 20.1 | 47.8 | 73.7 | 17.7 | 37.3 | 69
360 | 198 | 466.4 | 186.56 | 218.0779 | 236.4 | 238.8 | 237.9 | 246.7 | 325.5 | 24.4 | 21.9 | 51.4 | 3.3 | 239.7 | 6.4 | 329.3 | 603.7 | 812 | 278.5 | 744.3 | 315.1 | 829 | 845.8 | 620.6 | 756.9 | 264.2 | 624.5 | 568.3 | 20.2 | 48 | 74.3 | 17.7 | 37.5 | 69.3
361 | 199 | 465.6 | 186.24 | 217.7038 | 238 | 240.2 | 238.5 | 247.6 | 327.6 | 24.5 | 21.9 | 51.5 | 3.1 | 240.5 | 7.1 | 331.1 | 602.9 | 812.1 | 280.2 | 743.6 | 317.4 | 824.7 | 854.1 | 620.7 | 757.9 | 264.9 | 625.5 | 569.1 | 20.2 | 48.3 | 74.8 | 17.7 | 37.7 | 69.6
362 | 200 | 465.7 | 186.28 | 217.7506 | 238.5 | 239.8 | 238.7 | 248.3 | 327.5 | 24.5 | 21.9 | 51.5 | 2.7 | 232.3 | 6.9 | 332.9 | 602.2 | 813 | 281.6 | 740.7 | 319.7 | 819.1 | 860.1 | 620.7 | 757.2 | 266 | 626.5 | 570 | 20.3 | 48.6 | 74.9 | 17.8 | 37.9 | 69.9
363 | 201 | 466.1 | 186.44 | 217.9376 | 239.3 | 240.4 | 239 | 249.3 | 327.5 | 24.6 | 21.9 | 51.6 | 3.2 | 233.7 | 6.3 | 334.5 | 602.7 | 820 | 283.3 | 740 | 321.9 | 817.8 | 861.5 | 621.6 | 756.6 | 267.4 | 628.2 | 570.8 | 20.4 | 48.8 | 75.3 | 17.8 | 38.1 | 70.2
364 | 202 | 466.8 | 186.72 | 218.2649 | 240 | 241.3 | 239.4 | 250.7 | 328.8 | 24.6 | 21.9 | 51.8 | 3.5 | 244.9 | 7.2 | 336.3 | 604.5 | 823.9 | 285.1 | 740.4 | 324.3 | 817.1 | 865.2 | 622.2 | 758.5 | 268.9 | 629.8 | 573.6 | 20.5 | 49.1 | 76 | 17.8 | 38.3 | 70.8
365 | 203 | 468 | 187.2 | 218.826 | 238.1 | 242.6 | 240.5 | 251.9 | 329.8 | 24.7 | 21.9 | 51.9 | 3.3 | 250.5 | 7.7 | 338.2 | 606.2 | 827 | 286.9 | 739.1 | 326.6 | 816.9 | 869.5 | 622.8 | 759.1 | 270.5 | 632.5 | 575.8 | 20.5 | 49.4 | 76.7 | 17.8 | 38.5 | 71.3
366 | 204 | 466.5 | 186.6 | 218.1246 | 237.8 | 244 | 240.7 | 252.9 | 332.6 | 24.8 | 21.9 | 52 | 3.1 | 248.4 | 7 | 339.8 | 605.5 | 825.6 | 288.3 | 738.1 | 328.8 | 815.4 | 866.9 | 623.1 | 759.6 | 272.3 | 635 | 578.4 | 20.6 | 49.6 | 77 | 17.9 | 38.7 | 71.6
367 | 205 | 465.3 | 186.12 | 217.5636 | 238.9 | 246.3 | 241.7 | 254 | 336 | 24.8 | 21.9 | 52 | 3.6 | 245.1 | 6.7 | 341.5 | 607 | 826.5 | 289.6 | 739.1 | 331 | 815.1 | 864.5 | 623.2 | 762 | 274.1 | 635.7 | 582.2 | 20.7 | 49.9 | 77.2 | 17.9 | 38.9 | 72
368 | 206 | 466.7 | 186.68 | 218.2182 | 239.5 | 246.8 | 242.8 | 255 | 343.4 | 24.9 | 21.9 | 52.1 | 3.6 | 256 | 6.4 | 343.3 | 608.9 | 829.6 | 291.3 | 740.3 | 333.1 | 812.9 | 861.2 | 622.6 | 763.6 | 275.6 | 637.7 | 586.5 | 20.8 | 50.2 | 77.6 | 18 | 39.1 | 72.2
369 | 207 | 466.7 | 186.68 | 218.2182 | 239.9 | 247.1 | 243.3 | 255.9 | 346.9 | 24.9 | 21.9 | 52.1 | 3.9 | 265.1 | 6.4 | 345.1 | 609.5 | 834.1 | 293.1 | 742.6 | 335.2 | 815 | 849.9 | 622 | 764.3 | 277.1 | 642 | 591.9 | 20.9 | 50.5 | 78.3 | 18 | 39.3 | 72.3
370 | 208 | 466.7 | 186.68 | 218.2182 | 241 | 247.7 | 244.2 | 256.8 | 351.8 | 25 | 21.9 | 52.1 | 3.7 | 253.9 | 6.1 | 346.9 | 611.6 | 839.5 | 294.9 | 742.7 | 337.4 | 820 | 839.2 | 623.1 | 766.1 | 278.5 | 646.8 | 597.4 | 20.9 | 50.8 | 78.9 | 18 | 39.5 | 72.6
371 | 209 | 467.1 | 186.84 | 218.4052 | 241.4 | 249 | 245.1 | 257.6 | 360.8 | 25.1 | 21.9 | 52.2 | 4 | 242.4 | 6.8 | 348.8 | 612.9 | 841.4 | 296.9 | 743.9 | 339.7 | 820.5 | 830.9 | 624.5 | 767 | 280 | 650.4 | 602 | 21 | 51 | 79.2 | 18 | 39.7 | 73
372 | 210 | 469.2 | 187.68 | 219.3871 | 239.5 | 249.3 | 246 | 258.3 | 358.6 | 25.2 | 21.9 | 52.2 | 3.9 | 244.6 | 7.2 | 350.4 | 615.8 | 837.3 | 298.3 | 745.3 | 341.8 | 823.3 | 823.4 | 626.2 | 768.2 | 281.7 | 653 | 607.1 | 21.1 | 51.3 | 79.5 | 18.1 | 40 | 73.6
373 | 211 | 469.5 | 187.8 | 219.5274 | 237.5 | 250.1 | 247 | 258.8 | 358.3 | 25.3 | 21.9 | 52.3 | 3.9 | 244.9 | 7.3 | 352.3 | 619.1 | 833.8 | 299.6 | 747.6 | 343.9 | 826.2 | 816.6 | 627.8 | 769.5 | 283.3 | 654.9 | 611.6 | 21.2 | 51.6 | 79.8 | 18.1 | 40.2 | 73.8
374 | 212 | 467.1 | 186.84 | 218.4052 | 235.9 | 250.8 | 247.8 | 259.2 | 357.6 | 25.4 | 21.9 | 52.4 | 3.9 | 235.5 | 7.1 | 354 | 623.9 | 825.3 | 301.1 | 748.9 | 346 | 830.1 | 817.6 | 629.9 | 769.6 | 285 | 657.8 | 614.8 | 21.2 | 51.9 | 80.4 | 18.2 | 40.4 | 74.2
375 | 213 | 468.2 | 187.28 | 218.9195 | 234.7 | 250.3 | 248.1 | 259.7 | 355.8 | 25.4 | 21.9 | 52.4 | 3.8 | 248.9 | 6.4 | 355.7 | 628.1 | 826.3 | 302.6 | 749.9 | 348.1 | 828.8 | 819.9 | 631.5 | 769.8 | 286.7 | 659.9 | 618.4 | 21.3 | 52.2 | 80.6 | 18.2 | 40.6 | 74.4
376 | 214 | 468.9 | 187.56 | 219.2468 | 234.4 | 250.4 | 248.9 | 259.5 | 352.1 | 25.5 | 21.8 | 52.5 | 3.9 | 221.2 | 5.5 | 357.5 | 631.9 | 820.2 | 304 | 751.8 | 350.3 | 831.7 | 804.6 | 634.1 | 770.9 | 288.3 | 662.9 | 622.2 | 21.4 | 52.5 | 80.8 | 18.2 | 40.9 | 74.7
377 | 215 | 468.1 | 187.24 | 218.8728 | 234.3 | 250.9 | 249.1 | 258.6 | 349.1 | 25.5 | 21.8 | 52.6 | 4 | 222 | 4.5 | 359.5 | 635.9 | 811.4 | 305.1 | 754.3 | 352.5 | 833.5 | 780.3 | 637.5 | 771.6 | 290 | 665.7 | 626.2 | 21.5 | 52.7 | 81.2 | 18.3 | 41.1 | 75.5
378 | 216 | 468.5 | 187.4 | 219.0598 | 234.6 | 251 | 248.2 | 258.2 | 343.5 | 25.6 | 21.8 | 52.7 | 3.5 | 240 | 4.6 | 361.4 | 636.5 | 804.5 | 306.5 | 758.4 | 354.9 | 834.6 | 774.8 | 640.1 | 772.5 | 291.6 | 667.2 | 629.1 | 21.6 | 53 | 81.2 | 18.3 | 41.3 | 76
379 | 217 | 467.6 | 187.04 | 218.639 | 235 | 251.5 | 247.6 | 258 | 341.5 | 25.8 | 21.8 | 52.8 | 3.4 | 241.4 | 4.3 | 363.4 | 638.3 | 811.5 | 308.4 | 759.6 | 357.3 | 837.1 | 762.3 | 644.5 | 772.8 | 293.2 | 668.8 | 632.3 | 21.7 | 53.2 | 81.5 | 18.4 | 41.5 | 76.4
380 | 218 | 468.6 | 187.44 | 219.1066 | 235.8 | 252.5 | 246.9 | 257.2 | 340.2 | 25.9 | 21.8 | 52.9 | 3.8 | 239.2 | 4.4 | 365.4 | 641.8 | 817.2 | 310.1 | 760.4 | 359.8 | 841.3 | 773.8 | 649.3 | 773.4 | 294.8 | 671.9 | 635.4 | 21.7 | 53.4 | 82.3 | 18.4 | 41.7 | 76.5
381 | 219 | 468.5 | 187.4 | 219.0598 | 237 | 252.9 | 246.9 | 256.9 | 344.2 | 26 | 21.8 | 53.1 | 3.6 | 231.1 | 4.7 | 367.2 | 642.9 | 819.7 | 312.3 | 763 | 362.5 | 844.5 | 780 | 653.8 | 774.9 | 296.4 | 675.3 | 638.8 | 21.8 | 53.7 | 82.5 | 18.5 | 41.9 | 76.7
382 | 220 | 468.5 | 187.4 | 219.0598 | 238.5 | 252.9 | 246.8 | 256.9 | 349.2 | 26 | 21.8 | 53.2 | 3.3 | 244.8 | 5.7 | 369.1 | 644.4 | 819.2 | 314.7 | 766.1 | 365.3 | 843.8 | 775.9 | 657.8 | 775.2 | 298 | 678.8 | 641 | 21.9 | 54 | 82.9 | 18.5 | 42.1 | 77
383 | 221 | 468.3 | 187.32 | 218.9663 | 239.1 | 253.6 | 247.1 | 257 | 352.4 | 26.1 | 21.8 | 53.3 | 2.8 | 239.9 | 6.6 | 371 | 646.1 | 826.4 | 317.7 | 769.5 | 368.2 | 840.6 | 782.1 | 661.9 | 776.5 | 299.6 | 683 | 642 | 22 | 54.3 | 83.7 | 18.5 | 42.4 | 77.3
384 | 222 | 467.8 | 187.12 | 218.7325 | 239.2 | 254.7 | 247.5 | 256.5 | 363.9 | 26.1 | 21.8 | 53.5 | 3.1 | 239.2 | 6.2 | 373 | 649.4 | 829.6 | 320.8 | 771 | 371.4 | 839.7 | 794.4 | 666.3 | 778.1 | 301.2 | 687.4 | 642.9 | 22.1 | 54.6 | 84.2 | 18.6 | 42.6 | 77.9
385 | 223 | 469.9 | 187.96 | 219.7144 | 239.4 | 255.7 | 248.1 | 256.6 | 370.6 | 26.2 | 21.8 | 53.7 | 3.2 | 250 | 5.9 | 375.1 | 649.9 | 830 | 324.3 | 772.4 | 374.7 | 828.6 | 789.8 | 670.8 | 779.8 | 302.8 | 689.5 | 644 | 22.2 | 54.8 | 84.4 | 18.6 | 42.8 | 78.5
386 | 224 | 471.4 | 188.56 | 220.4158 | 239.2 | 257 | 248.2 | 256.9 | 372.7 | 26.2 | 21.8 | 53.9 | 3.7 | 235.8 | 5.6 | 377.4 | 654.6 | 831.2 | 328.4 | 773.4 | 378.2 | 674.8 | 794.8 | 677.7 | 780.7 | 304.6 | 693.2 | 645.8 | 22.3 | 55.1 | 84.6 | 18.7 | 43 | 78.9
387 | 225 | 471.5 | 188.6 | 220.4625 | 239.5 | 257.1 | 248.6 | 257.3 | 372.3 | 26.3 | 21.8 | 54 | 3.5 | 243.4 | 5.5 | 379.6 | 654.5 | 836 | 331.9 | 776.2 | 381.9 | 710.2 | 805.2 | 683.9 | 781.8 | 306.2 | 695.2 | 647.1 | 22.3 | 55.4 | 85 | 18.7 | 43.2 | 79.1
388 | 226 | 469.4 | 187.76 | 219.4806 | 240.6 | 256.5 | 249.4 | 257.7 | 369.6 | 26.4 | 21.8 | 54.2 | 3.7 | 258.5 | 6 | 381.8 | 656.9 | 833.8 | 335.7 | 777.9 | 386 | 830.3 | 801.1 | 691.6 | 781.8 | 307.9 | 697.7 | 649.1 | 22.4 | 55.6 | 85.3 | 18.8 | 43.4 | 79.5
389 | 227 | 467.5 | 187 | 218.5922 | 240.7 | 257.2 | 250.1 | 257.9 | 365.8 | 26.5 | 21.8 | 54.3 | 3.8 | 246.8 | 6.1 | 384.1 | 656.1 | 833.4 | 338.9 | 781.6 | 390.1 | 672.6 | 794.7 | 698.2 | 783 | 309.6 | 699.5 | 650.8 | 22.5 | 55.9 | 85.6 | 18.8 | 43.7 | 80.2
390 | 228 | 468.5 | 187.4 | 219.0598 | 241.5 | 258.9 | 250.2 | 257.8 | 368.6 | 26.5 | 21.8 | 54.5 | 4.2 | 253.5 | 6.2 | 386.6 | 657.4 | 835.3 | 342.2 | 783.5 | 394.5 | 803 | 796.5 | 705.5 | 783.3 | 311.3 | 700.5 | 652.5 | 22.6 | 56.1 | 86.1 | 18.8 | 43.9 | 80.7
391 | 229 | 469.2 | 187.68 | 219.3871 | 242.9 | 260.3 | 250.1 | 258.4 | 373.9 | 26.5 | 21.8 | 54.6 | 3.9 | 255.5 | 5.9 | 389 | 659.3 | 836.4 | 346 | 785.1 | 399.2 | 826.1 | 801.6 | 713.3 | 783.9 | 313.1 | 701.7 | 653.3 | 22.7 | 56.4 | 86.5 | 18.9 | 44.1 | 81
392 | 230 | 468.6 | 187.44 | 219.1066 | 243.1 | 261.8 | 250.4 | 259.4 | 375.2 | 26.6 | 21.8 | 54.7 | 4 | 233.5 | 5.2 | 391.3 | 657.1 | 838.1 | 349.3 | 785.7 | 404.3 | 582.1 | 811.9 | 722.5 | 784.3 | 314.9 | 702.4 | 653.4 | 22.8 | 56.7 | 87.1 | 19 | 44.3 | 81.2
393 | 231 | 468.8 | 187.52 | 219.2001 | 243.8 | 263.4 | 250.8 | 260.1 | 371.6 | 26.7 | 21.8 | 54.7 | 3.6 | 219.5 | 5 | 393.6 | 654.4 | 839.7 | 352.7 | 784.2 | 409.5 | 825.2 | 817 | 731.8 | 785.1 | 316.7 | 703.4 | 652.2 | 22.8 | 56.9 | 87.4 | 19 | 44.6 | 81.7
394 | 232 | 469 | 187.6 | 219.2936 | 243 | 264.1 | 251.1 | 261.1 | 368.2 | 26.8 | 21.8 | 54.8 | 3.9 | 232 | 5.1 | 395.9 | 655.7 | 835.5 | 356.5 | 786.1 | 414.6 | 798.3 | 804.1 | 738.9 | 785.4 | 318.2 | 704.4 | 652.4 | 22.9 | 57.2 | 87.4 | 19 | 44.8 | 82.2
395 | 233 | 469.5 | 187.8 | 219.5274 | 243 | 264.8 | 251.3 | 261.8 | 363.5 | 26.9 | 21.7 | 54.8 | 3.6 | 247.7 | 5.6 | 398.2 | 659.1 | 828.7 | 359.7 | 787.1 | 420 | 673.4 | 779.7 | 746.6 | 785.7 | 319.8 | 705.9 | 652.2 | 23 | 57.5 | 87.8 | 19.1 | 45 | 83
396 | 234 | 468.8 | 187.52 | 219.2001 | 243.9 | 265.2 | 250.9 | 262.1 | 359 | 27 | 21.7 | 54.9 | 3.2 | 242.9 | 5.8 | 400.2 | 658.3 | 827.2 | 362.1 | 789 | 425.7 | 829.7 | 778.2 | 754.9 | 786.4 | 321.4 | 706.5 | 650.8 | 23.1 | 57.7 | 88.1 | 19.1 | 45.2 | 83.4
397 | 235 | 468.3 | 187.32 | 218.9663 | 244.8 | 264.7 | 250.9 | 262.6 | 358.5 | 27 | 21.7 | 54.9 | 3.5 | 249.3 | 6.4 | 402.6 | 658.3 | 829.7 | 364.6 | 789.6 | 431.4 | 809 | 765.5 | 762.8 | 787 | 322.9 | 707.6 | 649.6 | 23.2 | 58 | 88.7 | 19.2 | 45.5 | 83.6
398 | 236 | 467.7 | 187.08 | 218.6857 | 245.5 | 264.7 | 251.1 | 262.2 | 356 | 27.1 | 21.7 | 55 | 3.6 | 246 | 6.5 | 404.8 | 657 | 830 | 367.2 | 790.2 | 437.1 | 794.4 | 769.8 | 769.5 | 787.6 | 324.2 | 709.4 | 648.7 | 23.3 | 58.3 | 89.3 | 19.2 | 45.7 | 84.5
399 | 237 | 467.8 | 187.12 | 218.7325 | 246.2 | 265.3 | 250.8 | 261.3 | 353.7 | 27.2 | 21.7 | 55.2 | 3.9 | 254.5 | 6.3 | 407.1 | 659.5 | 829.6 | 369.4 | 790.5 | 442.5 | 827.7 | 773.1 | 775.2 | 787.9 | 325.7 | 711.3 | 648.4 | 23.4 | 58.5 | 89.4 | 19.3 | 45.9 | 84.7
400 | 238 | 468 | 187.2 | 218.826 | 247.4 | 265.2 | 250.8 | 260.3 | 351.6 | 27.2 | 21.7 | 55.3 | 3.3 | 254 | 6 | 409.3 | 658.2 | 827.4 | 371.2 | 787.6 | 447.9 | 780.1 | 781.3 | 782.3 | 788.1 | 327.3 | 714.2 | 645.7 | 23.5 | 58.8 | 89.7 | 19.3 | 46.1 | 85
401 | 239 | 468.5 | 187.4 | 219.0598 | 249.4 | 264.5 | 251.2 | 260.4 | 353.4 | 27.3 | 21.7 | 55.4 | 3 | 240.7 | 5.9 | 411 | 664.5 | 830 | 371.9 | 788.5 | 453.1 | 824.3 | 803.3 | 786.6 | 787.9 | 328.6 | 717.3 | 643.8 | 23.6 | 59.1 | 90.3 | 19.4 | 46.4 | 85.2
402 | 240 | 468.2 | 187.28 | 218.9195 | 251.1 | 263.9 | 251.3 | 261.2 | 359.1 | 27.4 | 21.7 | 55.5 | 3.5 | 249.3 | 6 | 413.2 | 662 | 831.1 | 372.3 | 785 | 458.6 | 827.4 | 810.4 | 790.6 | 788 | 330 | 719.9 | 642 | 23.7 | 59.4 | 90.7 | 19.4 | 46.6 | 85.3
403 | 241 | 466.9 | 186.76 | 218.3117 | 252.4 | 263.8 | 251.6 | 261.9 | 357.3 | 27.4 | 21.7 | 55.7 | 4.1 | 251.5 | 6.2 | 415.1 | 665 | 826.8 | 372.9 | 783 | 463.9 | 641.4 | 811.2 | 794.4 | 787.4 | 331.4 | 721.8 | 640.8 | 23.8 | 59.6 | 91 | 19.5 | 46.8 | 85.7
404 | 242 | 468.1 | 187.24 | 218.8728 | 253.8 | 263.9 | 252 | 262.4 | 359.6 | 27.5 | 21.7 | 55.8 | 3.6 | 247.9 | 6.1 | 417.1 | 668.5 | 831.4 | 373.5 | 784.5 | 468.9 | 786.7 | 823.9 | 796.4 | 787.5 | 332.8 | 724.3 | 639.9 | 23.9 | 59.9 | 91.9 | 19.5 | 47.1 | 86.1
405 | 243 | 466.9 | 186.76 | 218.3117 | 254.4 | 263.5 | 252.8 | 262.7 | 363.1 | 27.5 | 21.7 | 56 | 3.4 | 248.5 | 6.1 | 419.1 | 665.7 | 833.2 | 373.7 | 787.5 | 473.7 | 821.4 | 827.6 | 797.1 | 788.1 | 334.1 | 726.6 | 638.8 | 24 | 60.1 | 92.1 | 19.6 | 47.3 | 86.9
406 | 244 | 468 | 187.2 | 218.826 | 254.7 | 263.1 | 253.2 | 263 | 360.6 | 27.5 | 21.7 | 56.2 | 3.4 | 245.4 | 6.4 | 421.3 | 661.8 | 832.3 | 373.6 | 791.5 | 478.2 | 576.8 | 823.7 | 798 | 788.5 | 335.2 | 728.4 | 638.4 | 24.1 | 60.4 | 92.3 | 19.6 | 47.6 | 87.4
407 | 245 | 467.7 | 187.08 | 218.6857 | 254.4 | 264.1 | 253.5 | 263 | 364.3 | 27.6 | 21.7 | 56.4 | 3.9 | 247.5 | 6.2 | 423.5 | 658.4 | 833.7 | 373.2 | 794.6 | 483 | 815.4 | 811 | 800.2 | 790.1 | 336.4 | 731.5 | 638.2 | 24.2 | 60.7 | 92.8 | 19.7 | 47.8 | 87.6
408 | 246 | 468 | 187.2 | 218.826 | 254.8 | 265.7 | 253.8 | 262.4 | 366.8 | 27.6 | 21.7 | 56.6 | 3.8 | 229.9 | 5.5 | 425.5 | 656.5 | 834.4 | 372.9 | 794.8 | 487.4 | 757 | 820 | 802.9 | 790 | 337.5 | 733.5 | 639 | 24.3 | 60.9 | 92.9 | 19.7 | 48.1 | 87.9
409 | 247 | 467 | 186.8 | 218.3584 | 254.6 | 267.2 | 254.1 | 261.7 | 365.9 | 27.7 | 21.7 | 56.7 | 3.6 | 232.1 | 4.7 | 427.9 | 655.3 | 832.7 | 372.4 | 793.9 | 491.4 | 534.8 | 826.3 | 804.7 | 790.9 | 338.8 | 734.8 | 639 | 24.4 | 61.2 | 93.3 | 19.8 | 48.3 | 88.2
410 | 248 | 467.2 | 186.88 | 218.452 | 255.3 | 267.1 | 254.5 | 261.7 | 362.7 | 27.7 | 21.7 | 56.9 | 3.7 | 235.8 | 4.5 | 430.1 | 653.8 | 830.9 | 372.7 | 790.9 | 495.2 | 814.6 | 829.4 | 808.4 | 791.7 | 340 | 737 | 639.5 | 24.5 | 61.5 | 93.7 | 19.9 | 48.5 | 88.9
411 | 249 | 468.1 | 187.24 | 218.8728 | 256.4 | 265.7 | 255.1 | 262 | 359.8 | 27.8 | 21.6 | 57 | 3.3 | 219.5 | 4.6 | 431.6 | 650.5 | 826.9 | 372.9 | 787.9 | 498.3 | 666.7 | 826.1 | 811.1 | 790.3 | 341.1 | 737.6 | 640.1 | 24.6 | 61.7 | 93.9 | 19.9 | 48.8 | 88.9
412 | 250 | 467.3 | 186.92 | 218.4987 | 258.4 | 264.4 | 255.6 | 262 | 357.8 | 27.9 | 21.6 | 57 | 3.9 | 219 | 4.3 | 433.1 | 648.1 | 823.6 | 373.2 | 784.7 | 501.4 | 582.5 | 821 | 813 | 789.6 | 342.3 | 738.2 | 640.9 | 24.6 | 62 | 94.5 | 20 | 49 | 89
413 | 251 | 468.5 | 187.4 | 219.0598 | 260.1 | 263.6 | 256.7 | 261.6 | 359.1 | 28 | 21.6 | 57.1 | 3.6 | 222.3 | 3.7 | 434.3 | 646.5 | 823.2 | 373.8 | 784.3 | 504.4 | 817 | 818.6 | 815.7 | 789.7 | 343.4 | 739.2 | 642 | 24.8 | 62.3 | 94.7 | 20 | 49.3 | 89.2
414 | 252 | 468.2 | 187.28 | 218.9195 | 261.3 | 262.9 | 257.8 | 261.8 | 358.2 | 28.1 | 21.6 | 57.2 | 3.9 | 226 | 3.4 | 435.7 | 643.2 | 809 | 374.4 | 779.2 | 507.1 | 796.8 | 800.1 | 818.7 | 788 | 344.5 | 739.5 | 641.4 | 24.8 | 62.6 | 94.8 | 20.1 | 49.5 | 89.5
415 | 253 | 467.5 | 187 | 218.5922 | 264.3 | 262.1 | 258.4 | 262.5 | 355.9 | 28.1 | 21.6 | 57.3 | 3.9 | 231.7 | 3.5 | 437.1 | 645.5 | 802.4 | 375.4 | 775.1 | 509.5 | 803.7 | 790.3 | 820.1 | 787.3 | 345.6 | 740.2 | 641.5 | 24.9 | 62.8 | 95.2 | 20.1 | 49.8 | 90.1
416 | 254 | 468.5 | 187.4 | 219.0598 | 266.6 | 260.6 | 259 | 263.5 | 356.2 | 28.2 | 21.6 | 57.4 | 3.5 | 245.7 | 3.8 | 438.4 | 649.6 | 804.9 | 376.8 | 777 | 511.8 | 816.7 | 798.7 | 820.8 | 788.4 | 346.6 | 741.4 | 642.3 | 25 | 63.1 | 95.7 | 20.2 | 50 | 90.7
417 | 255 | 467.2 | 186.88 | 218.452 | 268.9 | 260.1 | 259.7 | 265 | 354.5 | 28.3 | 21.6 | 57.5 | 3.5 | 251.7 | 3.8 | 440.1 | 649.3 | 801.1 | 378.1 | 773.1 | 514.3 | 817.7 | 788.5 | 823.1 | 787.4 | 347.7 | 741.9 | 643.4 | 25.1 | 63.4 | 96.5 | 20.3 | 50.3 | 91.3
418 | 256 | 466.8 | 186.72 | 218.2649 | 270.5 | 259.1 | 261 | 266.4 | 353.4 | 28.3 | 21.6 | 57.6 | 3.5 | 250 | 4.1 | 441.3 | 647.7 | 801.5 | 379.1 | 769 | 516.5 | 817.1 | 782.2 | 824.4 | 786 | 348.7 | 741.5 | 644.9 | 25.2 | 63.7 | 97 | 20.3 | 50.5 | 91.6
419 | 257 | 468.6 | 187.44 | 219.1066 | 271.5 | 257.6 | 262.7 | 268.1 | 353.3 | 28.4 | 21.6 | 57.7 | 4 | 240.6 | 4.3 | 442.7 | 646.4 | 798.8 | 380.1 | 766.9 | 518.9 | 817.3 | 772 | 825.3 | 784.9 | 349.8 | 741.4 | 645.5 | 25.3 | 64 | 97.5 | 20.4 | 50.8 | 92
420 | 258 | 468.4 | 187.36 | 219.013 | 274.3 | 256.4 | 263.8 | 270.1 | 351.3 | 28.5 | 21.6 | 57.9 | 3.7 | 216.8 | 3.8 | 444 | 642.7 | 790.8 | 381.2 | 763.7 | 521.2 | 817.5 | 757.2 | 826.8 | 783.4 | 350.8 | 741.2 | 645.6 | 25.4 | 64.3 | 97.8 | 20.4 | 51 | 92.4
421 | 259 | 468.6 | 187.44 | 219.1066 | 276.5 | 256.1 | 265.1 | 271.7 | 348.9 | 28.6 | 21.6 | 58 | 3.3 | 207 | 3.5 | 445.3 | 640.9 | 787.3 | 382.3 | 760.5 | 523.6 | 816.4 | 757.1 | 827.6 | 782 | 351.8 | 741 | 646.2 | 25.5 | 64.5 | 97.9 | 20.5 | 51.3 | 92.8
422 | 260 | 467.1 | 186.84 | 218.4052 | 278.7 | 255.2 | 267 | 273.2 | 346.9 | 28.7 | 21.6 | 58.2 | 3.5 | 223.8 | 3 | 446.5 | 639.8 | 774.8 | 383.2 | 758.3 | 526.1 | 814.7 | 754.2 | 829.8 | 780.8 | 352.7 | 741.5 | 645.9 | 25.7 | 64.8 | 98.3 | 20.6 | 51.5 | 93.2
423 | 261 | 467.9 | 187.16 | 218.7793 | 280.1 | 253.9 | 268.7 | 274.8 | 344.2 | 28.8 | 21.6 | 58.3 | 3.7 | 254.1 | 3.2 | 447.9 | 638.6 | 766.4 | 384.3 | 756.7 | 528.5 | 755.9 | 742.3 | 831.3 | 779.5 | 353.5 | 742 | 645.7 | 25.7 | 65.1 | 98.6 | 20.6 | 51.8 | 93.8
424 | 262 | 467.6 | 187.04 | 218.639 | 281 | 253 | 269.5 | 276.2 | 342.4 | 28.9 | 21.6 | 58.4 | 3.3 | 269.5 | 3.4 | 449 | 639.3 | 754.6 | 385.7 | 757.2 | 530.9 | 815 | 733.9 | 832 | 779.1 | 354.3 | 742.9 | 645.4 | 25.8 | 65.4 | 99.4 | 20.7 | 52 | 94.3
425 | 263 | 467.8 | 187.12 | 218.7325 | 281.7 | 252.5 | 270.2 | 277.3 | 341.3 | 29 | 21.6 | 58.5 | 3.4 | 245.5 | 3.6 | 450.3 | 637.7 | 755.5 | 387.4 | 757.5 | 533.3 | 800.2 | 725.8 | 832.8 | 780 | 355.1 | 744.3 | 644.6 | 26 | 65.6 | 100.4 | 20.7 | 52.3 | 94.5
426 | 264 | 467.2 | 186.88 | 218.452 | 280.6 | 252 | 270.5 | 277.7 | 342.5 | 29 | 21.6 | 58.6 | 3.4 | 212.7 | 3.8 | 451.7 | 642.8 | 766.4 | 389.8 | 758 | 535.6 | 624.9 | 722.1 | 833.5 | 782.1 | 356 | 746 | 644.5 | 26.1 | 65.9 | 100.5 | 20.8 | 52.5 | 94.9
427 | 265 | 468.4 | 187.36 | 219.013 | 280.8 | 251.4 | 270.9 | 278.4 | 342.7 | 29.2 | 21.6 | 58.7 | 3.6 | 177.3 | 4.4 | 453.4 | 644.3 | 774.6 | 392.9 | 760.5 | 538 | 810.6 | 729.1 | 834.7 | 783.6 | 356.7 | 748.1 | 644.5 | 26.2 | 66.2 | 100.5 | 20.9 | 52.8 | 95.3
428 | 266 | 468 | 187.2 | 218.826 | 280.3 | 252 | 271.4 | 279.4 | 343.6 | 29.3 | 21.5 | 58.8 | 3.3 | 190.2 | 4.5 | 455 | 647.1 | 779.2 | 394.7 | 761.4 | 540.7 | 548 | 728.5 | 836.4 | 784.9 | 357.4 | 750.1 | 645 | 26.3 | 66.5 | 100.7 | 20.9 | 53 | 95.8
429 | 267 | 467.5 | 187 | 218.5922 | 278.9 | 251.2 | 271.1 | 280.2 | 343.3 | 29.4 | 21.5 | 58.9 | 3.9 | 215 | 4.3 | 456.6 | 651 | 776.2 | 396.2 | 761 | 543.6 | 639.6 | 726.7 | 838.6 | 785.2 | 358.2 | 752.1 | 646.5 | 26.4 | 66.8 | 101 | 21 | 53.3 | 96.4
430 | 268 | 468 | 187.2 | 218.826 | 275.7 | 248.8 | 271.8 | 280.4 | 343.7 | 29.5 | 21.5 | 59.1 | 4.5 | 210.8 | 4.7 | 457.9 | 651.8 | 775.9 | 398.3 | 763.2 | 546.7 | 810.3 | 733 | 840.7 | 785.4 | 359 | 753.3 | 649 | 26.5 | 67.1 | 101.3 | 21.1 | 53.6 | 96.9
431 | 269 | 467.9 | 187.16 | 218.7793 | 275.7 | 248.1 | 272.4 | 280.5 | 342.5 | 29.5 | 21.5 | 59.3 | 4.2 | 198.2 | 4.6 | 459.4 | 655.2 | 778.4 | 401 | 763.6 | 549.9 | 452 | 733.5 | 844 | 786.5 | 359.9 | 755.5 | 652 | 26.6 | 67.4 | 101.6 | 21.1 | 53.8 | 97.4
432 | 270 | 467.7 | 187.08 | 218.6857 | 276.4 | 248.2 | 273.7 | 280.1 | 343.9 | 29.6 | 21.5 | 59.4 | 3.5 | 203.3 | 4 | 460.8 | 658.8 | 775.2 | 403.1 | 763.2 | 553.6 | 728.4 | 729.3 | 845.8 | 785.9 | 360.8 | 757.9 | 654.8 | 26.7 | 67.7 | 102.1 | 21.2 | 54.1 | 97.8
433 | 271 | 467.8 | 187.12 | 218.7325 | 275.3 | 248.9 | 274 | 280 | 344.7 | 29.8 | 21.5 | 59.5 | 3.2 | 211.7 | 3.7 | 462.1 | 662 | 771.9 | 404.7 | 764.8 | 557.3 | 811.2 | 729.3 | 845.7 | 785.6 | 361.8 | 759.4 | 657.5 | 26.8 | 68 | 102.4 | 21.2 | 54.3 | 98.2
434 | 272 | 469.7 | 187.88 | 219.6209 | 274.6 | 249.1 | 273.6 | 280.1 | 343.9 | 29.9 | 21.5 | 59.5 | 3.9 | 212.7 | 3.5 | 463.4 | 662.3 | 778.8 | 406 | 768.1 | 561.1 | 360.9 | 745.7 | 844.9 | 787.3 | 362.7 | 760.7 | 659.6 | 26.9 | 68.2 | 102.8 | 21.3 | 54.6 | 98.3
435 | 273 | 469.8 | 187.92 | 219.6677 | 273.1 | 249.4 | 273.6 | 280.2 | 344.3 | 30 | 21.5 | 59.6 | 3.6 | 222.8 | 3.1 | 464.9 | 662.9 | 785.6 | 407.9 | 770 | 565.1 | 798.2 | 767.6 | 842.3 | 788.4 | 363.6 | 761.4 | 661.1 | 27 | 68.5 | 103.7 | 21.4 | 54.9 | 98.6
436 | 274 | 468.8 | 187.52 | 219.2001 | 271.6 | 250.4 | 273.6 | 280.1 | 347.1 | 30 | 21.5 | 59.7 | 3.9 | 212.3 | 3.2 | 466.2 | 661.6 | 794 | 410.3 | 771.3 | 569.1 | 706.2 | 772.7 | 841.4 | 789.1 | 364.6 | 761.9 | 663.9 | 27.1 | 68.8 | 104 | 21.4 | 55.2 | 99.1
437 | 275 | 467.9 | 187.16 | 218.7793 | 270.2 | 251.1 | 273.6 | 279.4 | 350.3 | 30 | 21.5 | 59.8 | 4.2 | 202.7 | 3.2 | 467.9 | 659 | 795.8 | 412.4 | 769 | 573.2 | 380.6 | 770.1 | 842.1 | 789.7 | 365.6 | 762.9 | 666.7 | 27.2 | 69.1 | 104.3 | 21.5 | 55.4 | 99.5
438 | 276 | 467.7 | 187.08 | 218.6857 | 269.4 | 252.3 | 273.6 | 278.3 | 350.2 | 30 | 21.5 | 59.9 | 3.9 | 208.4 | 2.9 | 469.7 | 661.6 | 800.7 | 414.3 | 768.7 | 577.4 | 806.4 | 781.5 | 844.1 | 789.5 | 366.7 | 764.2 | 669.4 | 27.3 | 69.4 | 104.6 | 21.6 | 55.7 | 99.8
439 | 277 | 467.7 | 187.08 | 218.6857 | 270.4 | 254.2 | 273.7 | 277.4 | 349.8 | 30 | 21.5 | 59.9 | 3.8 | 205.7 | 2.8 | 471.6 | 661.7 | 799.1 | 415.7 | 771.5 | 581.7 | 603.6 | 782.9 | 845.2 | 789.5 | 367.9 | 765.8 | 672.5 | 27.4 | 69.7 | 104.7 | 21.7 | 55.9 | 100.3
440 | 278 | 468.1 | 187.24 | 218.8728 | 271.1 | 256.2 | 272.7 | 276.7 | 351.3 | 30 | 21.5 | 60 | 3.5 | 203.8 | 2.6 | 473.1 | 660 | 802.5 | 417.4 | 774 | 585.9 | 495.1 | 792.9 | 846.5 | 788.8 | 369 | 767.2 | 675 | 27.5 | 70 | 105 | 21.7 | 56.2 | 100.8
441 | 279 | 468.4 | 187.36 | 219.013 | 271.4 | 258.1 | 271.4 | 275.4 | 355.1 | 30.2 | 21.5 | 60 | 3.7 | 209.4 | 2.5 | 475.2 | 659.7 | 807.5 | 419.3 | 774.8 | 590.2 | 812.7 | 793.2 | 847.9 | 790.4 | 370.4 | 769.6 | 676.4 | 27.6 | 70.3 | 105.4 | 21.8 | 56.4 | 101.3
442 | 280 | 469.7 | 187.88 | 219.6209 | 272 | 260.3 | 271 | 274.5 | 357 | 30.2 | 21.5 | 60 | 3.4 | 219.6 | 2.4 | 477.4 | 657 | 811.7 | 420.8 | 777 | 594.4 | 812.7 | 805.6 | 848.3 | 790.8 | 371.8 | 771 | 678.3 | 27.8 | 70.6 | 105.5 | 21.9 | 56.7 | 101.7
443 | 281 | 470 | 188 | 219.7612 | 272.5 | 262 | 270.9 | 274 | 355.3 | 30.3 | 21.5 | 60.1 | 3.3 | 238.1 | 2.6 | 479.5 | 657.3 | 817.9 | 422.2 | 779.1 | 598.4 | 811.9 | 810 | 847.2 | 791.3 | 373.1 | 771.8 | 680.2 | 27.9 | 70.9 | 106 | 21.9 | 57 | 102
444 | 282 | 468.6 | 187.44 | 219.1066 | 272.6 | 263.1 | 270.5 | 273.5 | 356 | 30.4 | 21.5 | 60.2 | 3 | 251.5 | 3.3 | 481.9 | 654.7 | 818.7 | 423.3 | 782.1 | 602.5 | 813.7 | 800 | 846.9 | 792.2 | 374.3 | 773.2 | 682.2 | 28 | 71.2 | 106.6 | 22 | 57.2 | 102.4
445 | 283 | 469.1 | 187.64 | 219.3403 | 272.6 | 264.8 | 270.9 | 272.9 | 355.4 | 30.5 | 21.4 | 60.3 | 3.2 | 251.5 | 3.7 | 484.1 | 652.5 | 814.1 | 424.8 | 782.4 | 606.4 | 813.3 | 795 | 847.8 | 792.2 | 375.7 | 773.6 | 684.3 | 28.1 | 71.4 | 107.3 | 22.1 | 57.5 | 102.7
446 | 284 | 469.1 | 187.64 | 219.3403 | 273.6 | 265.5 | 270.9 | 272.7 | 353.9 | 30.5 | 21.4 | 60.5 | 3.1 | 240.3 | 4.6 | 486.2 | 653.9 | 812.2 | 426.2 | 783.5 | 610.5 | 813.4 | 804.7 | 848 | 792.6 | 376.9 | 774.2 | 686.4 | 28.2 | 71.8 | 108 | 22.2 | 57.7 | 103.1
447 | 285 | 468.7 | 187.48 | 219.1533 | 275.2 | 265.8 | 270.1 | 272.6 | 356.1 | 30.6 | 21.4 | 60.7 | 3.6 | 262.9 | 5.7 | 488.4 | 658.4 | 816.4 | 427.4 | 786.1 | 614.5 | 811.3 | 815 | 847.5 | 793.1 | 378.2 | 774.3 | 688.9 | 28.3 | 72.1 | 108.7 | 22.2 | 58 | 103.6
448 | 286 | 469.5 | 187.8 | 219.5274 | 276.2 | 267 | 269 | 272 | 358.8 | 30.6 | 21.4 | 60.9 | 3.8 | 264.5 | 5.9 | 491.1 | 659.3 | 808.3 | 428.7 | 784.8 | 618.5 | 813.3 | 811.6 | 847.9 | 792.9 | 379.5 | 774.7 | 691.1 | 28.4 | 72.4 | 108.9 | 22.3 | 58.2 | 104.1
449 | 287 | 469.1 | 187.64 | 219.3403 | 276.2 | 267.4 | 267.9 | 272 | 361.6 | 30.7 | 21.4 | 61.1 | 3.4 | 235.8 | 5.6 | 493.6 | 659.5 | 811.1 | 430 | 789.4 | 622.6 | 812.1 | 818.8 | 848.2 | 794.7 | 380.7 | 776 | 693.7 | 28.5 | 72.7 | 109 | 22.4 | 58.4 | 104.7
450 | 288 | 468.8 | 187.52 | 219.2001 | 275.2 | 269.1 | 267.4 | 272.4 | 369.6 | 30.8 | 21.4 | 61.2 | 3.1 | 222.1 | 5.1 | 495.9 | 657.5 | 813.6 | 431.2 | 791.7 | 626.7 | 813.3 | 813.8 | 847 | 794.2 | 381.9 | 777.3 | 695.5 | 28.6 | 73 | 109.9 | 22.4 | 58.7 | 105.1
451 | 289 | 468.5 | 187.4 | 219.0598 | 274.8 | 271.2 | 267.9 | 273 | 369.5 | 31 | 21.4 | 61.3 | 3.4 | 236.4 | 4.8 | 498.1 | 658.2 | 808.9 | 432.5 | 793.1 | 630.8 | 815 | 801.5 | 845.4 | 794.8 | 383.2 | 778.7 | 697.3 | 28.8 | 73.3 | 110.1 | 22.5 | 59 | 105.8
452 | 290 | 468.5 | 187.4 | 219.0598 | 274.1 | 273.1 | 268.8 | 273.8 | 366.2 | 31.1 | 21.4 | 61.4 | 3.9 | 233.3 | 4.9 | 500.2 | 657.6 | 803.7 | 433.8 | 794 | 635 | 816 | 794.6 | 844.9 | 794.3 | 384.5 | 779.7 | 698.4 | 28.9 | 73.7 | 110.1 | 22.6 | 59.3 | 106.3
453 | 291 | 469.1 | 187.64 | 219.3403 | 274.1 | 274.1 | 268.6 | 273.6 | 365.4 | 31.2 | 21.4 | 61.5 | 4.1 | 223.3 | 4.5 | 502.3 | 656.6 | 800.3 | 435.3 | 792.8 | 639.3 | 817.5 | 792.7 | 845.7 | 794 | 385.9 | 781.1 | 700.2 | 29 | 74 | 110.2 | 22.7 | 59.6 | 106.5
454 | 292 | 467.7 | 187.08 | 218.6857 | 274.6 | 275 | 268 | 273.6 | 364.5 | 31.3 | 21.4 | 61.5 | 4.8 | 238 | 4.3 | 504.2 | 653.2 | 803.8 | 437 | 794 | 643.7 | 819.3 | 806 | 846.8 | 794.7 | 387.2 | 782.5 | 703.7 | 29.1 | 74.3 | 110.7 | 22.8 | 59.9 | 106.8
455 | 293 | 467.9 | 187.16 | 218.7793 | 274.8 | 275.1 | 268.2 | 273.9 | 363.8 | 31.3 | 21.4 | 61.6 | 4.5 | 247.7 | 4.3 | 506 | 650.4 | 802.2 | 438.7 | 793.1 | 648.3 | 819.4 | 789.5 | 845.5 | 794.1 | 388.6 | 782.7 | 706.7 | 29.2 | 74.6 | 110.9 | 22.8 | 60.1 | 107
456 | 294 | 468.5 | 187.4 | 219.0598 | 275.3 | 274.5 | 267.7 | 274 | 361.9 | 31.4 | 21.4 | 61.7 | 4.5 | 239.2 | 4.2 | 507.5 | 648.1 | 785.3 | 439.9 | 788.5 | 652.8 | 821.8 | 756.6 | 842.2 | 792.5 | 389.9 | 782.6 | 707.3 | 29.4 | 74.9 | 111.3 | 22.9 | 60.4 | 107.3
457 | 295 | 468.8 | 187.52 | 219.2001 | 275 | 275.3 | 269.2 | 274.6 | 359.1 | 31.9 | 21.4 | 61.9 | 4.5 | 213.3 | 4.2 | 508.9 | 645.8 | 778.5 | 443.9 | 789.1 | 655.8 | 821.8 | 753.1 | 843.6 | 792.4 | 389.5 | 783.5 | 710.5 | 29.3 | 75.1 | 111.7 | 22.8 | 61.2 | 108.7
458 | 296 | 468.2 | 187.28 | 218.9195 | 278.3 | 274.4 | 269.2 | 274.6 | 357.1 | 31.7 | 21.4 | 62.1 | 4.6 | 194.2 | 4.3 | 510.8 | 647.7 | 782.3 | 444.1 | 790.2 | 660.9 | 821.6 | 750.2 | 843.9 | 793.9 | 391.9 | 783.7 | 710.3 | 29.6 | 75.5 | 112.2 | 23 | 61.1 | 108.7
459 | 297 | 468.4 | 187.36 | 219.013 | 279.3 | 273.8 | 269.4 | 275.4 | 356.6 | 31.6 | 21.4 | 62.3 | 4.2 | 213.5 | 5.2 | 512.8 | 646.7 | 777.6 | 444.4 | 791.1 | 665.3 | 820 | 753.7 | 843.6 | 794.9 | 393.6 | 784.4 | 711.8 | 29.8 | 75.8 | 112.7 | 23.1 | 61.2 | 109.1
460 | 298 | 468.6 | 187.44 | 219.1066 | 281 | 273.1 | 270.6 | 276.5 | 357.9 | 31.7 | 21.4 | 62.6 | 4.2 | 210.1 | 6.7 | 514.8 | 650.4 | 779.9 | 445.5 | 787.9 | 669.4 | 821.2 | 758.7 | 842.3 | 795.8 | 394.8 | 785.3 | 713.3 | 29.9 | 76.1 | 113.1 | 23.2 | 61.4 | 109.4
461 | 299 | 469.6 | 187.84 | 219.5741 | 282.5 | 272.5 | 271.5 | 276.9 | 359.1 | 31.7 | 21.4 | 62.7 | 4.2 | 219 | 6.5 | 516.8 | 652.3 | 767.9 | 446.5 | 783.5 | 673.4 | 822.5 | 737.2 | 840.5 | 793.5 | 396 | 785.8 | 713.7 | 30 | 76.4 | 113.3 | 23.3 | 61.7 | 109.8
462 | 300 | 470.4 | 188.16 | 219.9482 | 284.3 | 271.4 | 272.1 | 277.1 | 358.9 | 31.7 | 21.3 | 62.8 | 3.7 | 224.8 | 5.8 | 518.4 | 653.9 | 762.2 | 446.8 | 779.8 | 677.8 | 823.5 | 717.7 | 838.2 | 792.6 | 397.4 | 785.7 | 712.5 | 30.1 | 76.7 | 113.8 | 23.4 | 62 | 110.4
463 | 301 | 469.5 | 187.8 | 219.5274 | 285.9 | 271.1 | 273.4 | 277.9 | 359.1 | 31.8 | 21.3 | 62.9 | 3.4 | 229.6 | 5.4 | 519.8 | 654.1 | 752.1 | 447.6 | 775.2 | 681.8 | 826.1 | 703.1 | 834.9 | 791.4 | 398.7 | 785.2 | 711.5 | 30.2 | 77 | 114.1 | 23.4 | 62.3 | 111.2
464 | 302 | 468.7 | 187.48 | 219.1533 | 288.4 | 270.3 | 274.7 | 278.8 | 359.8 | 31.8 | 21.3 | 62.9 | 3 | 236.1 | 4.6 | 521 | 654.5 | 744.6 | 448.9 | 777 | 685.7 | 823.6 | 711.2 | 836.8 | 791.1 | 400.1 | 784.7 | 711.8 | 30.4 | 77.3 | 114.6 | 23.5 | 62.5 | 111.5
465 | 303 | 469.6 | 187.84 | 219.5741 | 287.3 | 269.3 | 276.5 | 279.8 | 361.6 | 31.9 | 21.3 | 63 | 3.4 | 262.5 | 3.7 | 522.8 | 656 | 752.6 | 450.4 | 780.3 | 689.7 | 819.3 | 732.1 | 838.2 | 791.8 | 401.4 | 784.9 | 715 | 30.5 | 77.6 | 115.2 | 23.6 | 62.8 | 111.6
466 | 304 | 469.6 | 187.84 | 219.5741 | 286.6 | 268.1 | 278.2 | 280 | 362.5 | 31.9 | 21.3 | 63.1 | 3.5 | 277.7 | 3.2 | 524.6 | 655.9 | 767.5 | 451.2 | 779.7 | 693.6 | 818.3 | 755.5 | 837.5 | 792.2 | 402.7 | 785 | 716.7 | 30.6 | 77.9 | 115.6 | 23.7 | 63.1 | 112.2
467 | 305 | 469.7 | 187.88 | 219.6209 | 285.9 | 267 | 279.3 | 280.2 | 360.8 | 32 | 21.3 | 63.3 | 3.4 | 244.6 | 3.5 | 526.1 | 655.8 | 775.5 | 452.4 | 780.9 | 697.6 | 816.8 | 766.7 | 835.5 | 793.2 | 404 | 785.6 | 717.3 | 30.7 | 78.3 | 116.1 | 23.8 | 63.4 | 112.6
468 | 306 | 469.1 | 187.64 | 219.3403 | 286.7 | 266.4 | 280.2 | 280.2 | 360.9 | 32 | 21.3 | 63.4 | 3.1 | 218.3 | 4.4 | 528.3 | 658.3 | 783.3 | 454.1 | 781.8 | 701.1 | 817.6 | 768.1 | 832 | 795.2 | 405.3 | 786.7 | 717.9 | 30.8 | 78.6 | 116.7 | 23.9 | 63.7 | 113.1
469 | 307 | 468 | 187.2 | 218.826 | 287.6 | 266.7 | 280.5 | 279.9 | 362.2 | 32.1 | 21.3 | 63.6 | 3.4 | 214.5 | 4.6 | 531.2 | 660 | 787.4 | 455.5 | 781.3 | 704.6 | 818.3 | 774.7 | 831.8 | 796.6 | 406.6 | 788.3 | 719 | 30.9 | 78.9 | 117.2 | 23.9 | 64 | 113.5
470 | 308 | 468.3 | 187.32 | 218.9663 | 289.5 | 268.5 | 280.6 | 280.3 | 365 | 32.3 | 21.3 | 63.7 | 3.1 | 222.6 | 5.1 | 533.9 | 663.2 | 796.2 | 456.7 | 785.2 | 707.9 | 814.8 | 797.3 | 832.8 | 798.5 | 407.8 | 789 | 721.2 | 31.1 | 79.2 | 117.6 | 24 | 64.3 | 113.7
471 | 309 | 469.1 | 187.64 | 219.3403 | 290.8 | 269.5 | 281.4 | 280.8 | 368.1 | 32.5 | 21.3 | 63.9 | 3.7 | 211.4 | 6 | 536.8 | 664.1 | 806.1 | 458 | 787.3 | 710.6 | 812.9 | 812.3 | 832.9 | 798.9 | 409.3 | 788.8 | 723.8 | 31.2 | 79.5 | 118.1 | 24.1 | 64.6 | 114
472 | 310 | 470.3 | 188.12 | 219.9014 | 291.4 | 270.5 | 282.1 | 280.7 | 370.3 | 32.7 | 21.3 | 64.1 | 3.4 | 217 | 6.5 | 540.1 | 665.8 | 808.9 | 459.5 | 789 | 713.5 | 811.5 | 815.6 | 831.4 | 799 | 410.8 | 788.6 | 725.3 | 31.3 | 79.9 | 118.5 | 24.2 | 64.9 | 114.4
473 | 311 | 469.3 | 187.72 | 219.4339 | 292.6 | 272.1 | 282.9 | 280.3 | 371.3 | 32.8 | 21.3 | 64.2 | 3.9 | 253.8 | 6.7 | 543.3 | 667.9 | 811.5 | 460.7 | 788.9 | 716.3 | 812.6 | 822.9 | 830.5 | 800.3 | 412.3 | 788.9 | 726.3 | 31.4 | 80.2 | 119.4 | 24.3 | 65.2 | 114.8
474 | 312 | 470.1 | 188.04 | 219.8079 | 293.9 | 274.1 | 283.5 | 280.6 | 371.7 | 32.9 | 21.3 | 64.3 | 3.6 | 259.4 | 5.8 | 546.6 | 668.4 | 810.4 | 462.5 | 789.2 | 719 | 813.4 | 817.3 | 831.2 | 801.3 | 413.8 | 789.6 | 727.7 | 31.5 | 80.5 | 119.7 | 24.4 | 65.5 | 115.4
475 | 313 | 470.1 | 188.04 | 219.8079 | 294 | 274.9 | 284.1 | 281.5 | 372.1 | 33 | 21.3 | 64.5 | 3.5 | 256.8 | 5.1 | 549.9 | 668.4 | 810.7 | 463.8 | 793.6 | 721.8 | 812.4 | 812.5 | 830.5 | 802.3 | 415.3 | 790.1 | 728.3 | 31.7 | 80.9 | 120.1 | 24.4 | 65.8 | 115.8
476 | 314 | 469.2 | 187.68 | 219.3871 | 294.1 | 275.4 | 284.5 | 282.7 | 374.6 | 33 | 21.3 | 64.5 | 3.1 | 237.4 | 5.2 | 553.4 | 667.5 | 815.6 | 464.9 | 797.8 | 724.4 | 809 | 809.1 | 830.1 | 803.8 | 416.8 | 790.5 | 728.1 | 31.8 | 81.2 | 120.6 | 24.5 | 66.1 | 116.2
477 | 315 | 469.7 | 187.88 | 219.6209 | 293.8 | 277.7 | 284.6 | 283.4 | 377.2 | 33.1 | 21.3 | 64.6 | 3.9 | 235.9 | 5.9 | 557.1 | 666.9 | 817.6 | 466.4 | 800.9 | 726.7 | 808.1 | 802.8 | 828.1 | 804.8 | 418.4 | 790.7 | 728 | 31.9 | 81.6 | 121.2 | 24.6 | 66.4 | 116.7
478 | 316 | 468.6 | 187.44 | 219.1066 | 293.9 | 280.7 | 284.8 | 284 | 378.9 | 33.2 | 21.3 | 64.7 | 4.4 | 208.4 | 5.5 | 560.9 | 668.2 | 810 | 467.8 | 802.2 | 728.9 | 809.8 | 791.2 | 828.3 | 806.3 | 419.9 | 791.7 | 729.3 | 32 | 81.9 | 121.5 | 24.7 | 66.7 | 117.3
479 | 317 | 469.6 | 187.84 | 219.5741 | 293.9 | 282.5 | 285.4 | 285.2 | 377.9 | 33.2 | 21.2 | 64.9 | 4.5 | 201.2 | 4.9 | 564.5 | 669.8 | 792.9 | 469.7 | 798 | 731 | 812.1 | 774.1 | 827.9 | 806.2 | 421.4 | 792.4 | 729.5 | 32.2 | 82.3 | 121.9 | 24.8 | 67 | 118
480 | 318 | 469.2 | 187.68 | 219.3871 | 295.4 | 282.8 | 286.3 | 286 | 376.6 | 33.2 | 21.2 | 65 | 4.2 | 232.2 | 4.3 | 567.8 | 671.3 | 791.9 | 471.6 | 799.3 | 733.4 | 811.5 | 788.7 | 829.3 | 805.8 | 423 | 792.9 | 729.3 | 32.3 | 82.6 | 122.2 | 24.9 | 67.3 | 118.8
481 | 319 | 468.8 | 187.52 | 219.2001 | 297.8 | 282.5 | 288 | 286.5 | 376.6 | 33.2 | 21.2 | 65.1 | 3.5 | 251.5 | 4.1 | 571.1 | 672.3 | 803.1 | 473.6 | 798.1 | 735.8 | 809.9 | 798.6 | 829.3 | 807.2 | 424.7 | 792.5 | 728.5 | 32.4 | 83 | 122.8 | 25 | 67.6 | 119.1
482 | 320 | 469.7 | 187.88 | 219.6209 | 299.6 | 281.8 | 288.6 | 286.4 | 377.7 | 33.3 | 21.2 | 65.2 | 3.9 | 250.6 | 4.7 | 574.2 | 674 | 807.9 | 476.9 | 793.9 | 738.3 | 812 | 795.4 | 827.9 | 806.3 | 426.5 | 791.9 | 724.7 | 32.5 | 83.4 | 123.3 | 25.1 | 67.8 | 119.5
483 | 321 | 469 | 187.6 | 219.2936 | 301.2 | 281 | 288.8 | 287.1 | 377.4 | 33.3 | 21.2 | 65.3 | 4.2 | 236.5 | 5.8 | 577.2 | 673.6 | 801 | 479.7 | 791.2 | 741.2 | 813.5 | 801.4 | 830 | 805.2 | 428.3 | 791 | 719.7 | 32.6 | 83.7 | 124.1 | 25.1 | 68.1 | 119.8
484 | 322 | 469.4 | 187.76 | 219.4806 | 302.9 | 280.4 | 290 | 288.3 | 377.9 | 33.4 | 21.2 | 65.4 | 3.7 | 245 | 6.3 | 580.1 | 675.9 | 796.2 | 481.9 | 787.4 | 744.2 | 814.2 | 800.3 | 830 | 803.8 | 430 | 789.9 | 714.1 | 32.8 | 84.1 | 124.5 | 25.2 | 68.5 | 120.3
485 | 323 | 469.2 | 187.68 | 219.3871 | 305.9 | 280.5 | 292 | 289.7 | 376.6 | 33.5 | 21.2 | 65.4 | 4.1 | 240.6 | 6.8 | 583 | 678.1 | 787.9 | 484.8 | 783.8 | 747.3 | 814.5 | 793.9 | 831.1 | 802.4 | 431.7 | 789 | 709.7 | 32.9 | 84.5 | 124.8 | 25.3 | 68.7 | 120.9
486 | 324 | 468.9 | 187.56 | 219.2468 | 307.9 | 280.6 | 294.5 | 291.4 | 374.6 | 33.5 | 21.2 | 65.5 | 3.7 | 248.1 | 7.4 | 585.7 | 677.8 | 792.4 | 486.9 | 782.7 | 750.1 | 815.5 | 793.4 | 834.3 | 802.6 | 433.5 | 787.8 | 706.4 | 33 | 84.8 | 125.5 | 25.4 | 69.1 | 121.6
487 | 325 | 468.9 | 187.56 | 219.2468 | 309 | 280.1 | 296.3 | 293.3 | 376 | 33.5 | 21.2 | 65.6 | 4 | 253.2 | 7.6 | 588.2 | 678.6 | 797.1 | 488.2 | 779.4 | 753 | 816.5 | 798.2 | 834.1 | 801.9 | 435.3 | 786.2 | 702 | 33.2 | 85.2 | 126.7 | 25.5 | 69.3 | 122.2
488 | 326 | 468.6 | 187.44 | 219.1066 | 310.5 | 281.2 | 297.9 | 294.9 | 377 | 33.6 | 21.2 | 65.7 | 4.1 | 246.2 | 7.2 | 590.7 | 680.3 | 795.6 | 489.8 | 776.7 | 755.7 | 817.9 | 800.3 | 835.1 | 800.5 | 437.1 | 784.5 | 694.9 | 33.3 | 85.6 | 127.2 | 25.6 | 69.6 | 122.9
489 | 327 | 469.2 | 187.68 | 219.3871 | 311.6 | 282.6 | 298.9 | 296.7 | 377.6 | 33.8 | 21.2 | 65.9 | 3.8 | 239.9 | 7.5 | 593.2 | 683.1 | 800.4 | 490.5 | 774.5 | 758.1 | 817.3 | 806.4 | 835.7 | 800.5 | 438.9 | 783.1 | 689.4 | 33.4 | 85.9 | 127.8 | 25.7 | 69.9 | 123.5
490 | 328 | 468 | 187.2 | 218.826 | 313.1 | 282.9 | 300.2 | 298.6 | 378.2 | 33.9 | 21.2 | 66.1 | 4 | 237.8 | 7.5 | 595.6 | 683.6 | 803.3 | 491.2 | 777.1 | 760.4 | 814 | 819.4 | 835.6 | 801.1 | 440.7 | 781.9 | 685.5 | 33.6 | 86.3 | 128.6 | 25.8 | 70.3 | 124.3
491 | 329 | 469 | 187.6 | 219.2936 | 313.5 | 283.5 | 301 | 300.4 | 379.5 | 34 | 21.2 | 66.3 | 4.3 | 239.1 | 6.9 | 597.9 | 682.5 | 808.7 | 492.3 | 778.4 | 762.2 | 811.7 | 831.4 | 833.8 | 801.9 | 442.6 | 781.1 | 679.9 | 33.7 | 86.7 | 128.8 | 25.9 | 70.6 | 124.8
492 | 330 | 469.1 | 187.64 | 219.3403 | 312.5 | 283.8 | 301.4 | 302.2 | 382.1 | 34 | 21.2 | 66.4 | 4.2 | 241 | 6.4 | 600.3 | 683.7 | 811.4 | 492.7 | 778 | 763.9 | 812.6 | 842.9 | 834.1 | 802.7 | 444.5 | 781.1 | 670.9 | 33.8 | 87.1 | 129.4 | 26 | 70.9 | 125.2
493 | 331 | 469 | 187.6 | 219.2936 | 313 | 284.3 | 302.2 | 303.4 | 384 | 34 | 21.2 | 66.5 | 4 | 243.4 | 6.6 | 602.5 | 688 | 809.8 | 493.1 | 778.2 | 765.5 | 812.6 | 842.6 | 832.9 | 803.4 | 446.4 | 781.9 | 664.9 | 34 | 87.5 | 129.8 | 26.1 | 71.2 | 125.6
494 | 332 | 468.5 | 187.4 | 219.0598 | 312 | 285.3 | 303.2 | 305.1 | 385.4 | 34 | 21.2 | 66.5 | 3.6 | 244 | 7.4 | 604.7 | 687.2 | 806.1 | 493.5 | 781.1 | 766.9 | 812.3 | 831.8 | 832.1 | 805 | 448.5 | 783.5 | 664.5 | 34.1 | 87.9 | 130.2 | 26.1 | 71.6 | 126.1
495 | 333 | 468.7 | 187.48 | 219.1533 | 310.1 | 286.2 | 303.6 | 305.9 | 388.2 | 34 | 21.2 | 66.5 | 3.5 | 235.1 | 7.1 | 606.6 | 686.7 | 800.5 | 493.7 | 781.5 | 768.3 | 811.8 | 823.6 | 830.6 | 805.9 | 450.4 | 785.3 | 662.2 | 34.2 | 88.2 | 130.4 | 26.2 | 71.9 | 126.6
496 | 334 | 469.1 | 187.64 | 219.3403 | 307.7 | 286.8 | 303.2 | 306.3 | 387.8 | 34.1 | 21.2 | 66.7 | 3.6 | 232.1 | 6.5 | 608.8 | 685.6 | 801.1 | 494.7 | 783.2 | 769.9 | 811.3 | 829.9 | 831.8 | 806.3 | 452.4 | 786.6 | 659.6 | 34.4 | 88.6 | 131 | 26.3 | 72.2 | 127.1
497 | 335 | 468.9 | 187.56 | 219.2468 | 307.3 | 287.6 | 303 | 306.8 | 388.5 | 34.2 | 21.2 | 66.9 | 3.7 | 241.7 | 6.4 | 610.8 | 685.7 | 802.7 | 495.5 | 785.5 | 771.6 | 811.2 | 836.4 | 832.1 | 806.9 | 454.6 | 787.1 | 657.9 | 34.5 | 89 | 131.9 | 26.4 | 72.5 | 127.6
498 | 336 | 468.5 | 187.4 | 219.0598 | 305.4 | 287.3 | 303.3 | 306.9 | 389.9 | 34.2 | 21.2 | 67.1 | 3.7 | 250.1 | 6.7 | 612.9 | 683.8 | 806 | 496.3 | 789.3 | 773.3 | 809.3 | 848.4 | 831.3 | 807.8 | 456.7 | 787.5 | 655.4 | 34.6 | 89.4 | 132.2 | 26.5 | 72.8 | 128.2
499 | 337 | 468.1 | 187.24 | 218.8728 | 304.1 | 286.3 | 303.5 | 307 | 394.8 | 34.2 | 21.2 | 67.2 | 3.6 | 243.3 | 6.9 | 615.1 | 682.5 | 810.1 | 497.8 | 790 | 774.4 | 808.5 | 843.8 | 830.4 | 808.8 | 459.2 | 787.8 | 653.8 | 34.8 | 89.8 | 132.7 | 26.6 | 73.1 | 128.9
500 | 338 | 468.6 | 187.44 | 219.1066 | 306.2 | 287.3 | 303.6 | 307.5 | 399.6 | 34.2 | 21.2 | 67.3 | 3.8 | 230.9 | 7 | 617.3 | 681.2 | 811.8 | 498.8 | 791.3 | 775.7 | 808.6 | 848.6 | 830.7 | 808.8 | 461.5 | 788.7 | 648.7 | 34.9 | 90.2 | 133.5 | 26.7 | 73.5 | 129.4
501 | 339 | 468.6 | 187.44 | 219.1066 | 308.3 | 287.9 | 304.7 | 308.2 | 400.3 | 34.3 | 21.1 | 67.3 | 4 | 236.9 | 6.8 | 619.3 | 683.4 | 810.1 | 500.3 | 791.3 | 776.8 | 807.5 | 848.8 | 830.9 | 809.2 | 463.6 | 789.3 | 644.8 | 35 | 90.6 | 134.3 | 26.8 | 73.8 | 130
502 | 340 | 469.2 | 187.68 | 219.3871 | 309.6 | 288.8 | 305.3 | 309.1 | 400.7 | 34.4 | 21.1 | 67.3 | 3.6 | 236.3 | 6.4 | 621.3 | 683 | 807.8 | 501.3 | 790.3 | 778.2 | 808.5 | 847.9 | 830.8 | 808.8 | 465.7 | 789.2 | 643.5 | 35.2 | 91 | 134.5 | 26.9 | 74.1 | 130.4
503 | 341 | 469 | 187.6 | 219.2936 | 310.7 | 289.2 | 304.9 | 309.1 | 399.6 | 34.5 | 21.1 | 67.3 | 3.3 | 236.3 | 5.8 | 623 | 684.7 | 802.4 | 503 | 790.4 | 779.7 | 808.9 | 844.5 | 830.8 | 808.1 | 467.7 | 789.7 | 643.8 | 35.3 | 91.4 | 134.7 | 27 | 74.4 | 130.8
504 | 342 | 469 | 187.6 | 219.2936 | 312.1 | 289.5 | 305.2 | 309.4 | 397.4 | 34.4 | 21.1 | 67.3 | 3.5 | 239.9 | 5.2 | 624.7 | 684.3 | 800.7 | 503.6 | 792 | 780.9 | 809.3 | 843.7 | 831.9 | 808.7 | 469.7 | 790.1 | 643.8 | 35.4 | 91.8 | 135.5 | 27.1 | 74.7 | 131.1
505 | 343 | 468.6 | 187.44 | 219.1066 | 313.4 | 289.3 | 305 | 309.3 | 397.2 | 34.5 | 21.1 | 67.3 | 3.6 | 259.6 | 4.8 | 626.4 | 685 | 797.7 | 503.4 | 790.3 | 782.3 | 809.9 | 836 | 831.2 | 808.9 | 471.8 | 790.1 | 642.8 | 35.6 | 92.2 | 135.9 | 27.2 | 75.1 | 131.7
506 | 344 | 469 | 187.6 | 219.2936 | 314.3 | 289.6 | 304.9 | 309.4 | 395.7 | 34.5 | 21.1 | 67.3 | 2.8 | 246.8 | 5.5 | 628.2 | 685.4 | 786.9 | 503.6 | 792.2 | 783.7 | 810.5 | 829.3 | 832 | 808.5 | 473.7 | 790.9 | 643.8 | 35.7 | 92.6 | 136.3 | 27.3 | 75.4 | 132.3
507 | 345 | 468.7 | 187.48 | 219.1533 | 315.1 | 289.3 | 306.3 | 309.3 | 392.4 | 34.6 | 21.1 | 67.3 | 3.5 | 254.9 | 5.6 | 630.1 | 686.3 | 789.8 | 504.2 | 795.6 | 785 | 809.4 | 834.3 | 830.1 | 809.4 | 475.6 | 791.2 | 644.3 | 35.9 | 93 | 137 | 27.4 | 75.7 | 133.2
508 | 346 | 468.4 | 187.36 | 219.013 | 316.7 | 288.9 | 307.4 | 308.7 | 392 | 34.7 | 21.1 | 67.3 | 3.6 | 242.3 | 5.2 | 632.1 | 687.1 | 797.5 | 504 | 796.2 | 786 | 811.5 | 838.7 | 830.3 | 810.4 | 477.5 | 791.7 | 645.5 | 36 | 93.4 | 137.6 | 27.5 | 76 | 133.7
509 | 347 | 468.8 | 187.52 | 219.2001 | 317.5 | 288.9 | 308.1 | 308.7 | 390.5 | 34.9 | 21.1 | 67.5 | 3.7 | 220.4 | 5 | 633.9 | 686.4 | 797 | 503.6 | 797.1 | 787.4 | 811.9 | 837.6 | 831.1 | 810.7 | 479.3 | 791.9 | 645.9 | 36.2 | 93.9 | 138.2 | 27.6 | 76.4 | 134
510 | 348 | 468.9 | 187.56 | 219.2468 | 318.3 | 289.7 | 308.4 | 309.1 | 391.7 | 34.9 | 21.1 | 67.6 | 3.4 | 224.6 | 4.4 | 635.8 | 684.2 | 794.7 | 503.7 | 799.5 | 788.6 | 812.4 | 829.1 | 830.1 | 811.1 | 481.1 | 792.4 | 643.3 | 36.3 | 94.3 | 138.4 | 27.7 | 76.7 | 134.5
511 | 349 | 469.1 | 187.64 | 219.3403 | 319.7 | 290.1 | 308.1 | 309.6 | 391.7 | 34.9 | 21 | 67.6 | 3.8 | 249.1 | 4.2 | 637.6 | 684.3 | 787.3 | 504.2 | 798.5 | 789.8 | 814.7 | 819 | 830.9 | 810.7 | 482.7 | 793.1 | 643.3 | 36.5 | 94.7 | 138.9 | 27.8 | 77 | 135.1
512 | 350 | 468.3 | 187.32 | 218.9663 | 320.9 | 289.8 | 308.1 | 309.7 | 389.4 | 34.9 | 21 | 67.7 | 4.1 | 249.4 | 4.1 | 639.5 | 686.4 | 785.8 | 505 | 798.5 | 791.2 | 816.8 | 821.2 | 830.8 | 810.9 | 484.2 | 793.5 | 644.7 | 36.6 | 95.1 | 139.1 | 27.9 | 77.4 | 135.7
513 | 351 | 468.3 | 187.32 | 218.9663 | 322 | 289.3 | 308.5 | 309.7 | 388.3 | 34.9 | 21 | 67.8 | 4.1 | 246.7 | 3.9 | 641.5 | 686.3 | 792.2 | 505.4 | 799.8 | 792.8 | 816.8 | 829.1 | 830.6 | 811.4 | 485.9 | 793.7 | 645.1 | 36.8 | 95.5 | 139.6 | 28 | 77.7 | 136.3
514 | 352 | 468.9 | 187.56 | 219.2468 | 323.6 | 290.1 | 308.7 | 309.2 | 389.3 | 35 | 21 | 68 | 4.3 | 255 | 3.8 | 643.5 | 687.3 | 798.8 | 505.4 | 800.8 | 793.8 | 818.4 | 832.1 | 831.7 | 811.8 | 488.1 | 793.6 | 643.6 | 36.9 | 96 | 140.5 | 28.1 | 78.1 | 136.8
515 | 353 | 468 | 187.2 | 218.826 | 323.4 | 291.5 | 308.9 | 308.7 | 394.1 | 35.1 | 21 | 68.2 | 4 | 259.2 | 4.1 | 645.3 | 688.8 | 799.8 | 505.3 | 800.2 | 795.1 | 820.3 | 833.7 | 832.9 | 810.6 | 490.3 | 792.5 | 637.8 | 37.1 | 96.4 | 141.2 | 28.2 | 78.4 | 137
516 | 354 | 467.3 | 186.92 | 218.4987 | 324.5 | 292.7 | 309.2 | 309.5 | 397.6 | 35.2 | 21 | 68.2 | 3.9 | 255.8 | 4.3 | 647.1 | 689.5 | 798.2 | 504.7 | 803.6 | 796.3 | 820.5 | 829.6 | 832 | 811.9 | 492.5 | 792 | 636.4 | 37.2 | 96.8 | 141.6 | 28.3 | 78.8 | 137.3
517 | 355 | 467.5 | 187 | 218.5922 | 322.6 | 293.2 | 309.6 | 310.5 | 397.5 | 35.2 | 21 | 68.4 | 3.8 | 253.4 | 4.4 | 648.9 | 687 | 796.7 | 504.3 | 802.8 | 797.3 | 822.2 | 832.2 | 831.3 | 811.6 | 494.6 | 792.2 | 633.5 | 37.4 | 97.3 | 142.3 | 28.4 | 79.1 | 138.1
518 | 356 | 465.4 | 186.16 | 217.6103 | 320.5 | 293.5 | 309.6 | 311.3 | 396.1 | 35.2 | 21 | 68.6 | 3.5 | 252.8 | 4.4 | 650.7 | 689.9 | 792.4 | 504.4 | 802.1 | 798.6 | 825.5 | 825.1 | 831.1 | 811.3 | 496.5 | 793 | 629 | 37.5 | 97.7 | 142.8 | 28.5 | 79.5 | 138.8
519 | 357 | 466.5 | 186.6 | 218.1246 | 318.9 | 293.6 | 309.7 | 312.4 | 394.7 | 35.3 | 21 | 68.9 | 3.6 | 250.5 | 4.5 | 652.7 | 688.9 | 789.1 | 504 | 804 | 800.1 | 825.6 | 823.8 | 829.7 | 811.8 | 498.2 | 793.7 | 629.2 | 37.7 | 98.1 | 143.1 | 28.6 | 79.8 | 139.2
520 | 358 | 467.5 | 187 | 218.5922 | 319.3 | 294.6 | 310.1 | 312.9 | 394.2 | 35.3 | 21 | 69.1 | 4 | 229.8 | 4.5 | 654.7 | 686.4 | 789 | 503.4 | 806.7 | 801.6 | 823.8 | 824.9 | 827.2 | 811.3 | 499.9 | 793.2 | 631 | 37.9 | 98.5 | 143.2 | 28.7 | 80.2 | 139.5
521 | 359 | 467.7 | 187.08 | 218.6857 | 320 | 296.2 | 310.7 | 312.8 | 393.5 | 35.2 | 21 | 69.2 | 3.9 | 219.7 | 4.4 | 656.6 | 686.2 | 788.6 | 502.5 | 806.9 | 803.2 | 825.6 | 827.6 | 824.4 | 811.3 | 501.2 | 793.1 | 629.7 | 38 | 99 | 143.9 | 28.9 | 80.5 | 140
522 | 360 | 467.3 | 186.92 | 218.4987 | 320.8 | 297.2 | 310.9 | 312.4 | 396.2 | 35.2 | 21 | 69.4 | 4 | 227.8 | 4 | 658.6 | 689.3 | 787.6 | 502.2 | 808.6 | 804.4 | 826.5 | 830.2 | 822.4 | 811 | 502.7 | 793.6 | 628.7 | 38.2 | 99.4 | 144.2 | 29 | 80.9 | 140.5
523 | 361 | 466.9 | 186.76 | 218.3117 | 321.5 | 297.7 | 311.3 | 311.8 | 396.6 | 35.2 | 21 | 69.4 | 3.7 | 230.4 | 4 | 660.6 | 690.5 | 790.8 | 501.8 | 809 | 805.4 | 827.6 | 834.5 | 820.8 | 810.6 | 504.4 | 793.5 | 628.2 | 38.3 | 99.8 | 145 | 29.1 | 81.3 | 140.8
524 | 362 | 467.6 | 187.04 | 218.639 | 322 | 298 | 311.7 | 311.9 | 397.5 | 35.2 | 21 | 69.4 | 3.7 | 242.2 | 4 | 662.4 | 690.8 | 791.9 | 501.3 | 807.7 | 806.7 | 829 | 838.7 | 819.4 | 810.9 | 506.1 | 793 | 629.2 | 38.5 | 100.2 | 145.8 | 29.2 | 81.6 | 141.2
525 | 363 | 467.7 | 187.08 | 218.6857 | 321.4 | 298.1 | 311.6 | 311.9 | 397.6 | 35.4 | 21 | 69.5 | 3.7 | 245.3 | 4 | 664.3 | 693.3 | 790.1 | 500.9 | 810.1 | 807.9 | 827.4 | 831.4 | 816.9 | 811.1 | 507.7 | 793.5 | 631.4 | 38.7 | 100.6 | 145.9 | 29.3 | 82 | 141.5
526 | 364 | 467.5 | 187 | 218.5922 | 320.7 | 298 | 311.6 | 311.2 | 396.6 | 35.6 | 21 | 69.6 | 4.1 | 238.8 | 4.1 | 666.2 | 694.8 | 787.8 | 500.5 | 809 | 808.7 | 829.6 | 820.8 | 817.1 | 812 | 509.3 | 794.6 | 632.6 | 38.8 | 101.1 | 146.4 | 29.4 | 82.3 | 142.1
527 | 365 | 467.7 | 187.08 | 218.6857 | 320.5 | 299 | 311 | 311.1 | 395.2 | 35.8 | 21 | 69.7 | 4 | 257.4 | 4.4 | 668.2 | 695.2 | 785.9 | 500.9 | 810.2 | 809.8 | 830.6 | 819 | 817.7 | 812 | 511 | 795.5 | 634.7 | 39 | 101.5 | 146.9 | 29.5 | 82.7 | 143
528 | 366 | 467.9 | 187.16 | 218.7793 | 320.7 | 299.8 | 310.1 | 311.5 | 396.1 | 35.9 | 21 | 69.7 | 4.5 | 264.2 | 4.5 | 670.2 | 696.3 | 785.3 | 501 | 811 | 811.1 | 831.2 | 819.1 | 817.5 | 812.6 | 512.6 | 796.4 | 637.4 | 39.2 | 101.9 | 147.3 | 29.6 | 83.1 | 143.5
529 | 367 | 468.2 | 187.28 | 218.9195 | 321.6 | 300.1 | 309.9 | 311.7 | 397.3 | 36 | 21 | 69.9 | 4.1 | 237.6 | 4.7 | 672.2 | 696.6 | 784.7 | 501.2 | 812.2 | 812.1 | 830.9 | 819.4 | 817.2 | 813.3 | 514.1 | 797.4 | 640.2 | 39.3 | 102.4 | 148 | 29.7 | 83.4 | 144
530 | 368 | 468 | 187.2 | 218.826 | 322.1 | 299.2 | 310.1 | 312.3 | 398.1 | 36.2 | 21 | 70 | 4.1 | 236.4 | 5 | 674.1 | 695.7 | 782.1 | 501.6 | 808.3 | 813.6 | 834.7 | 824.2 | 819.2 | 811.4 | 515.7 | 797.9 | 642.2 | 39.5 | 102.8 | 148.2 | 29.8 | 83.7 | 144.3
531 | 369 | 468.8 | 187.52 | 219.2001 | 322.8 | 298.7 | 310.9 | 312.5 | 399.8 | 36.3 | 21 | 70.1 | 4.7 | 242.9 | 5 | 676.1 | 697.2 | 788.4 | 501.6 | 809.8 | 815.4 | 835 | 828.4 | 819.6 | 810.9 | 517.4 | 797.1 | 642.9 | 39.6 | 103.2 | 149.1 | 30 | 84.1 | 144.8
532 | 370 | 467.6 | 187.04 | 218.639 | 322.5 | 298.4 | 310.8 | 312.9 | 401.4 | 36.4 | 20.9 | 70.2 | 4.6 | 232.1 | 5.2 | 678.1 | 695.9 | 786.9 | 501.7 | 812.6 | 816.8 | 835 | 827.8 | 819.2 | 811.3 | 519.3 | 796.8 | 644.8 | 39.8 | 103.6 | 149.6 | 30.1 | 84.5 | 145.6
533 | 371 | 468.2 | 187.28 | 218.9195 | 323.2 | 298 | 310.4 | 314.1 | 401 | 36.4 | 20.9 | 70.3 | 5.4 | 212.2 | 4.8 | 680.2 | 696.1 | 789.3 | 501.8 | 815 | 818 | 833 | 831.7 | 817.7 | 812.4 | 521.1 | 796.8 | 647.2 | 40 | 104.1 | 149.8 | 30.2 | 84.9 | 145.9
534 | 372 | 467.9 | 187.16 | 218.7793 | 324.1 | 298.9 | 310 | 314.2 | 404.7 | 36.4 | 20.9 | 70.5 | 5.4 | 215.7 | 3.6 | 682.2 | 696.7 | 792.1 | 502.5 | 814 | 818.6 | 834.1 | 832.8 | 817.7 | 812.9 | 523.1 | 796.9 | 648.2 | 40.1 | 104.5 | 150.5 | 30.3 | 85.2 | 146.2
535 | 373 | 467.7 | 187.08 | 218.6857 | 323.3 | 299.6 | 309.9 | 314.2 | 405.1 | 36.4 | 20.9 | 70.6 | 4.3 | 240.3 | 3 | 684.1 | 697.9 | 795.1 | 502.3 | 813.7 | 820 | 835.5 | 836.5 | 818.4 | 813.4 | 525.1 | 797.6 | 648.9 | 40.3 | 105 | 150.9 | 30.4 | 85.6 | 146.5
536 | 374 | 469.6 | 187.84 | 219.5741 | 321.8 | 300.1 | 310.4 | 315 | 410 | 36.4 | 20.9 | 70.7 | 4.8 | 255 | 3 | 686.2 | 696.5 | 796 | 502.5 | 815.1 | 820.9 | 836.8 | 836.6 | 820.2 | 813 | 527.1 | 799 | 649.4 | 40.5 | 105.4 | 151.5 | 30.5 | 86 | 146.9
537 | 375 | 468.5 | 187.4 | 219.0598 | 322.2 | 300.8 | 310.8 | 315.8 | 420.8 | 36.5 | 20.9 | 70.8 | 4.3 | 243.9 | 3.4 | 688.2 | 695.7 | 794.5 | 502.6 | 816.8 | 821.9 | 836.3 | 838.6 | 821.9 | 813.6 | 528.9 | 799.6 | 650 | 40.6 | 105.9 | 152.3 | 30.6 | 86.4 | 147.5
538 | 376 | 469.7 | 187.88 | 219.6209 | 322.8 | 302.2 | 310.8 | 317.3 | 430.7 | 36.7 | 20.9 | 70.9 | 4.8 | 223.5 | 3.5 | 690.1 | 696 | 797.1 | 502.4 | 818.4 | 822.8 | 836.4 | 838.3 | 821.8 | 813 | 531.2 | 800.5 | 650.2 | 40.8 | 106.3 | 152.9 | 30.7 | 86.7 | 148.2
539 | 377 | 469.5 | 187.8 | 219.5274 | 323.2 | 304.7 | 310.3 | 318.3 | 434 | 36.7 | 20.9 | 71 | 4.6 | 222.1 | 3.2 | 692 | 694.2 | 796.4 | 502.5 | 820.5 | 823.8 | 835.6 | 838.6 | 822.8 | 812.9 | 533.7 | 801 | 650.2 | 41 | 106.8 | 153.1 | 30.8 | 87.1 | 148.8
540 | 378 | 468.6 | 187.44 | 219.1066 | 322.8 | 305.5 | 309.9 | 319 | 436.2 | 36.7 | 20.9 | 71.1 | 4.3 | 232.3 | 3.3 | 693.8 | 693.7 | 797.4 | 502.7 | 819.1 | 824.7 | 836.5 | 842.6 | 823.1 | 813.6 | 535.9 | 801.1 | 650.5 | 41.2 | 107.3 | 153.5 | 31 | 87.5 | 149.2
541 | 379 | 468.8 | 187.52 | 219.2001 | 322.3 | 306.2 | 310.5 | 319.7 | 434.8 | 36.8 | 20.9 | 71.2 | 4.2 | 240.7 | 5.5 | 695.7 | 693.4 | 794.8 | 502.8 | 818.5 | 825.8 | 836.5 | 843.9 | 825.3 | 813.7 | 538.4 | 800.7 | 652.6 | 41.3 | 107.7 | 154.1 | 31.1 | 87.9 | 149.8
542 | 380 | 468.5 | 187.4 | 219.0598 | 321.8 | 308.3 | 311 | 320.7 | 429.9 | 36.8 | 20.9 | 71.3 | 4.4 | 222 | 6.7 | 697.3 | 694.9 | 792 | 502.9 | 817.2 | 826.9 | 836.4 | 846.2 | 825.7 | 813.1 | 541.1 | 800 | 654.3 | 41.5 | 108.2 | 154.8 | 31.2 | 88.3 | 150.3
543 | 381 | 468.5 | 187.4 | 219.0598 | 322.3 | 310.1 | 311.1 | 321.7 | 424.1 | 36.8 | 20.9 | 71.5 | 4 | 252.8 | 7.5 | 699.1 | 696.1 | 790.9 | 503.1 | 815.6 | 828 | 837.5 | 842.7 | 824.3 | 812.4 | 543.8 | 799.9 | 655.3 | 41.7 | 108.6 | 155.6 | 31.3 | 88.7 | 150.9
544 | 382 | 467.8 | 187.12 | 218.7325 | 321.9 | 310.2 | 310.8 | 322.7 | 420.9 | 36.9 | 20.9 | 71.7 | 3.5 | 245.5 | 8.1 | 700.8 | 697.8 | 780.4 | 503.6 | 812.8 | 829.3 | 838.7 | 830.6 | 820.2 | 810.8 | 546.5 | 800.1 | 656.9 | 41.9 | 109.1 | 155.7 | 31.4 | 89 | 151.5
545 | 383 | 468.1 | 187.24 | 218.8728 | 321.7 | 310.4 | 310.3 | 323.2 | 418.7 | 37.1 | 20.9 | 71.8 | 4 | 256.2 | 8 | 702.6 | 697.4 | 773.8 | 503.8 | 810.9 | 830.7 | 838.5 | 826.8 | 819 | 808.1 | 549.2 | 799.6 | 658.5 | 42 | 109.5 | 156 | 31.5 | 89.4 | 151.9
546 | 384 | 468.4 | 187.36 | 219.013 | 319.3 | 309.8 | 309.6 | 323.5 | 415.2 | 37.3 | 20.9 | 72 | 4 | 243.9 | 7.5 | 704.4 | 698.5 | 770.3 | 504.1 | 810.7 | 831.9 | 837.4 | 826.6 | 820.4 | 808.3 | 551.8 | 798.9 | 660.9 | 42.2 | 110 | 156 | 31.7 | 89.8 | 152.3
547 | 385 | 469.7 | 187.88 | 219.6209 | 319.4 | 309.8 | 310.1 | 323.4 | 413.3 | 37.5 | 20.9 | 72.1 | 3.9 | 243.7 | 7.7 | 706.1 | 696.3 | 766.3 | 504.4 | 810.4 | 832.9 | 836.9 | 826.4 | 820.7 | 807.5 | 554.5 | 798.3 | 663.2 | 42.4 | 110.4 | 156.4 | 31.8 | 90.1 | 152.7
548 | 386 | 468.8 | 187.52 | 219.2001 | 319.9 | 309.8 | 310.1 | 323.1 | 410.6 | 37.6 | 20.9 | 72.2 | 3.9 | 252.1 | 7.9 | 707.9 | 695.9 | 764.9 | 504.8 | 809.5 | 834.1 | 836.9 | 831.2 | 820.1 | 805.6 | 557 | 797.9 | 664.4 | 42.6 | 110.8 | 156.9 | 31.9 | 90.5 | 153.1
549 | 387 | 468.2 | 187.28 | 218.9195 | 320 | 310.5 | 309.7 | 322.5 | 409.8 | 37.7 | 20.9 | 72.3 | 3.9 | 252.5 | 8 | 709.4 | 696.1 | 759.7 | 505.3 | 807.8 | 835.3 | 836.1 | 835.6 | 818.3 | 802.8 | 559.7 | 796.4 | 664.4 | 42.8 | 111.3 | 157.5 | 32 | 90.9 | 153.4
550 | 388 | 467.8 | 187.12 | 218.7325 | 318.3 | 311.1 | 310.4 | 322.2 | 409.3 | 37.9 | 20.9 | 72.3 | 3.7 | 243.9 | 8.1 | 711.2 | 697.4 | 764.3 | 506 | 805.9 | 836.3 | 835.1 | 836.8 | 816.8 | 802.7 | 562.6 | 794.9 | 663.9 | 42.9 | 111.7 | 158.4 | 32.1 | 91.3 | 153.8
551 | 389 | 467.3 | 186.92 | 218.4987 | 317.1 | 310.9 | 310 | 322.4 | 409.9 | 38 | 20.9 | 72.4 | 4.1 | 244.3 | 7.6 | 712.8 | 700.2 | 764.8 | 507.1 | 804.4 | 837.2 | 836.1 | 832.9 | 817 | 802.3 | 565.8 | 794.7 | 664.1 | 43.1 | 112.1 | 158.7 | 32.3 | 91.6 | 154.3
552 | 390 | 467.7 | 187.08 | 218.6857 | 315.3 | 310 | 309.8 | 323 | 408.8 | 38.1 | 20.9 | 72.4 | 3.8 | 223.6 | 6.5 | 714.7 | 700.6 | 766.5 | 508.1 | 807.4 | 838.2 | 835.7 | 829.7 | 817.6 | 802 | 568.9 | 794.6 | 665.5 | 43.3 | 112.6 | 158.8 | 32.4 | 92 | 155
553 | 391 | 468.1 | 187.24 | 218.8728 | 316 | 309.9 | 309.4 | 323.3 | 410.4 | 38.2 | 20.8 | 72.4 | 4 | 207.8 | 5.8 | 716.6 | 701.3 | 764.3 | 509.2 | 810.1 | 838.6 | 835.3 | 827.9 | 817.4 | 802.9 | 571.9 | 795.2 | 668.1 | 43.5 | 113 | 159.3 | 32.5 | 92.4 | 155.5
554 | 392 | 468.3 | 187.32 | 218.9663 | 317.6 | 310.1 | 309.1 | 323.2 | 410.1 | 38.2 | 20.8 | 72.5 | 4 | 222.5 | 5.4 | 718.4 | 702 | 762.7 | 510 | 811.4 | 839 | 834.5 | 829.8 | 816.5 | 803.1 | 574.7 | 795.4 | 670.1 | 43.7 | 113.4 | 159.9 | 32.6 | 92.8 | 156
555 | 393 | 471.4 | 188.56 | 220.4158 | 318.9 | 310.3 | 309.3 | 322.5 | 408.2 | 38.2 | 20.8 | 72.5 | 4.8 | 233.1 | 5.1 | 720 | 704.2 | 761.7 | 511.3 | 808.7 | 839.4 | 833.4 | 827.6 | 815.7 | 801.5 | 577.6 | 795.5 | 670.7 | 43.8 | 113.9 | 160.4 | 32.7 | 93.2 | 156.2
556 | 394 | 471.9 | 188.76 | 220.6496 | 319.5 | 309.9 | 309.8 | 321.5 | 406.3 | 38.4 | 20.8 | 72.6 | 4.7 | 236.7 | 5.4 | 721.9 | 706.5 | 758.8 | 512.7 | 807.6 | 840.2 | 833 | 823.7 | 816.4 | 801.1 | 580.7 | 796.2 | 672.5 | 44 | 114.4 | 160.7 | 32.9 | 93.6 | 156.6
557 | 395 | 470 | 188 | 219.7612 | 320.2 | 309.2 | 309.8 | 321.4 | 405.2 | 38.6 | 20.8 | 72.7 | 4.6 | 245.8 | 5.9 | 723.6 | 708.7 | 747.8 | 513.8 | 805.1 | 840.9 | 833.5 | 822.7 | 814.8 | 799.2 | 583.5 | 796 | 673.9 | 44.2 | 114.8 | 160.9 | 33 | 93.9 | 157
558 | 396 | 467.3 | 186.92 | 218.4987 | 322.1 | 308.6 | 310.2 | 321.5 | 403.5 | 38.8 | 20.8 | 72.8 | 4.8 | 246.3 | 6.6 | 725.5 | 709.2 | 743.1 | 515 | 804 | 841.8 | 833.7 | 822.1 | 813.4 | 798.2 | 586.4 | 795.7 | 675 | 44.3 | 115.2 | 161.4 | 33.1 | 94.3 | 157.6
559 | 397 | 467.9 | 187.16 | 218.7793 | 324 | 308.8 | 310.7 | 322.1 | 401.9 | 38.9 | 20.8 | 72.9 | 4.9 | 247.4 | 6.9 | 727.4 | 709.1 | 747 | 516.1 | 802.4 | 842.7 | 833.1 | 825 | 811.8 | 797.3 | 589.3 | 795.6 | 676.6 | 44.5 | 115.7 | 162 | 33.2 | 94.7 | 158.3
560 | 398 | 468.1 | 187.24 | 218.8728 | 326 | 308.9 | 311.5 | 322.3 | 402.2 | 39 | 20.8 | 72.9 | 4.6 | 232 | 6 | 729.2 | 708.1 | 750.8 | 517.2 | 799.8 | 843.6 | 833.4 | 827.3 | 810.4 | 797.7 | 592.1 | 795.8 | 678.7 | 44.7 | 116.1 | 162.3 | 33.4 | 95.1 | 159.1
561 | 399 | 468.1 | 187.24 | 218.8728 | 327.4 | 309 | 312.4 | 322.5 | 400.4 | 39.1 | 20.8 | 73 | 4.6 | 251.4 | 5.7 | 731.1 | 708.7 | 751.9 | 518.4 | 798.2 | 844.2 | 834.8 | 828 | 809.6 | 797.6 | 594.7 | 796.7 | 680.4 | 44.9 | 116.5 | 163 | 33.5 | 95.5 | 159.3
562 | 400 | 469.4 | 187.76 | 219.4806 | 326.3 | 309.2 | 313 | 322.2 | 400.3 | 39.2 | 20.8 | 73.1 | 4.9 | 280.4 | 5.5 | 732.8 | 707.6 | 749.7 | 519.5 | 793.6 | 844.8 | 835.1 | 827.2 | 808.9 | 795.4 | 597.4 | 796.4 | 681.8 | 45.1 | 116.9 | 163.3 | 33.6 | 95.9 | 159.5
563 | 401 | 469.4 | 187.76 | 219.4806 | 325.8 | 308.7 | 313.6 | 322.8 | 400.4 | 39.3 | 20.8 | 73.2 | 4.9 | 249 | 5.3 | 734.5 | 711.6 | 746.4 | 521 | 790.4 | 845.3 | 835.4 | 823.8 | 807.6 | 794.6 | 600.4 | 796.7 | 683 | 45.3 | 117.4 | 163.9 | 33.7 | 96.3 | 160
564 | 402 | 468.6 | 187.44 | 219.1066 | 326.4 | 308.5 | 313.7 | 323.1 | 400.9 | 39.4 | 20.8 | 73.4 | 4.8 | 238.1 | 5.7 | 736.1 | 710.8 | 746 | 522.4 | 787.5 | 845.6 | 836.5 | 824.3 | 806.5 | 794.1 | 603.1 | 796.2 | 684.1 | 45.5 | 117.8 | 164.2 | 33.9 | 96.7 | 160.3
565 | 403 | 468.8 | 187.52 | 219.2001 | 328.1 | 307.9 | 314.3 | 323.3 | 401.5 | 39.4 | 20.8 | 73.5 | 4.7 | 272.4 | 6.1 | 737.8 | 709.5 | 749.8 | 523.7 | 787.5 | 846 | 835.5 | 828.8 | 805.3 | 794.1 | 605.6 | 795.3 | 685.1 | 45.7 | 118.2 | 164.7 | 34 | 97 | 160.7
566 | 404 | 468.1 | 187.24 | 218.8728 | 330 | 307.3 | 314.9 | 323.9 | 407.8 | 39.5 | 20.8 | 73.6 | 4.1 | 274.9 | 6.4 | 739.5 | 709.2 | 754.3 | 525.1 | 788.3 | 846.5 | 834.5 | 832.1 | 804.8 | 794.1 | 608.1 | 794.6 | 684.8 | 45.9 | 118.6 | 165.4 | 34.1 | 97.4 | 161.2
567 | 405 | 468.9 | 187.56 | 219.2468 | 332.8 | 307 | 315.8 | 324.4 | 411.5 | 39.5 | 20.8 | 73.7 | 4.1 | 269.5 | 6 | 741.1 | 707.5 | 753.4 | 526.3 | 788.2 | 846.6 | 835.2 | 834.1 | 805.6 | 793.5 | 610.5 | 794.3 | 685.8 | 46.1 | 119.1 | 165.6 | 34.2 | 97.8 | 161.6
568 | 406 | 467.6 | 187.04 | 218.639 | 334.9 | 306.4 | 316.1 | 324.9 | 411.4 | 39.5 | 20.8 | 73.7 | 4 | 254.6 | 6.8 | 742.8 | 708.1 | 761.8 | 527.4 | 786.4 | 846.6 | 835.3 | 835.7 | 805.8 | 794.5 | 612.6 | 793.8 | 686.2 | 46.3 | 119.5 | 166.3 | 34.4 | 98.1 | 162.1
569 | 407 | 469.1 | 187.64 | 219.3403 | 336.9 | 306.8 | 316.5 | 325 | 410.6 | 39.7 | 20.8 | 73.9 | 4.3 | 267.3 | 6.9 | 744.2 | 706.6 | 766.4 | 528.6 | 785.8 | 847 | 836 | 839.5 | 805.8 | 794.5 | 614.9 | 793 | 686.4 | 46.5 | 120 | 167.1 | 34.5 | 98.5 | 162.7
570 | 408 | 468.7 | 187.48 | 219.1533 | 339.3 | 307 | 317.1 | 325.4 | 412.5 | 39.7 | 20.8 | 74.1 | 4.7 | 244.1 | 6.1 | 745.7 | 705.8 | 766.9 | 529.8 | 783.6 | 847.9 | 835.4 | 841.3 | 805.8 | 792.6 | 617.3 | 791.1 | 684.7 | 46.7 | 120.4 | 167.7 | 34.6 | 98.9 | 163.2
571 | 409 | 468 | 187.2 | 218.826 | 339.5 | 307.3 | 317.7 | 326.1 | 415.5 | 39.7 | 20.8 | 74.2 | 4.2 | 222.3 | 4.8 | 747.1 | 708.1 | 769.2 | 531.4 | 784.7 | 849 | 835.9 | 845.3 | 805.9 | 791.2 | 620.2 | 790.1 | 684.4 | 46.9 | 120.9 | 168.3 | 34.8 | 99.2 | 163.8
572 | 410 | 467.6 | 187.04 | 218.639 | 340 | 308.2 | 317.6 | 327.5 | 417.5 | 39.7 | 20.7 | 74.2 | 4.7 | 221.7 | 4.7 | 748.4 | 709.5 | 766 | 533 | 781.9 | 849.9 | 835.8 | 846.6 | 805 | 789.2 | 623.4 | 788.6 | 684.2 | 47.1 | 121.4 | 168.9 | 34.9 | 99.6 | 164.3
573 | 411 | 467.9 | 187.16 | 218.7793 | 340.3 | 308.5 | 318.4 | 328.4 | 418.5 | 39.7 | 20.7 | 74.3 | 4.9 | 231.2 | 4.7 | 749.8 | 710.1 | 761.8 | 534.6 | 782.4 | 851.1 | 836.1 | 849.9 | 804.9 | 789.4 | 626.5 | 787.9 | 684.7 | 47.3 | 121.8 | 169.4 | 35 | 100 | 165
574 | 412 | 468.6 | 187.44 | 219.1066 | 339.1 | 309.6 | 319.8 | 329.4 | 420.3 | 39.8 | 20.7 | 74.5 | 5.1 | 235.8 | 4.6 | 751.2 | 710.6 | 762 | 536.4 | 783.3 | 851.9 | 835.2 | 852.7 | 806.7 | 791.1 | 629.2 | 787.8 | 686.3 | 47.4 | 122.3 | 169.9 | 35.1 | 100.4 | 165.7
575 | 413 | 467.1 | 186.84 | 218.4052 | 338.4 | 311 | 320.1 | 330.7 | 419.6 | 39.9 | 20.7 | 74.6 | 4.4 | 248.8 | 4.7 | 752.6 | 710.9 | 767.1 | 537.8 | 784.4 | 852.7 | 834.1 | 855 | 808.2 | 792.1 | 631.4 | 787.6 | 687.9 | 47.6 | 122.8 | 170.2 | 35.2 | 100.8 | 166.2
576 | 414 | 465.7 | 186.28 | 217.7506 | 339.1 | 311.5 | 320.5 | 331.7 | 419.7 | 40 | 20.7 | 74.6 | 4.4 | 245.1 | 4.9 | 754 | 709.2 | 769.4 | 539.1 | 784.1 | 853.1 | 835.1 | 852.6 | 809.9 | 793.5 | 633.2 | 787.7 | 690.1 | 47.8 | 123.3 | 170.7 | 35.4 | 101.2 | 166.6
577 | 415 | 467.7 | 187.08 | 218.6857 | 340.1 | 311.7 | 321 | 331.5 | 417.7 | 40.2 | 20.7 | 74.6 | 4.4 | 234.1 | 4.7 | 755.2 | 706 | 768.7 | 540.2 | 782.1 | 853.4 | 834.3 | 850.7 | 810.8 | 794.1 | 634.6 | 787.4 | 692.4 | 48 | 123.7 | 171 | 35.5 | 101.6 | 166.8
578 | 416 | 467.3 | 186.92 | 218.4987 | 340.9 | 311.3 | 321 | 331.4 | 416.3 | 40.2 | 20.7 | 74.6 | 4.3 | 236.4 | 4.8 | 756.3 | 704.9 | 767.6 | 541.2 | 781.9 | 853.8 | 833.7 | 848.3 | 810.9 | 794.1 | 635.9 | 786.8 | 694.3 | 48.2 | 124.2 | 171.3 | 35.6 | 102 | 167.4
579 | 417 | 467.3 | 186.92 | 218.4987 | 340.9 | 311.2 | 321.3 | 331.4 | 416.6 | 40.2 | 20.7 | 74.7 | 4.2 | 253 | 4.9 | 757.4 | 707.8 | 770.6 | 542.3 | 783.9 | 854 | 833.6 | 848.4 | 811.6 | 795.3 | 637.5 | 786.9 | 696.6 | 48.4 | 124.7 | 171.6 | 35.7 | 102.4 | 167.8
580 | 418 | 467.3 | 186.92 | 218.4987 | 339.3 | 311.4 | 321.7 | 331.8 | 418.2 | 40.3 | 20.7 | 74.8 | 4.2 | 255.6 | 4.8 | 758.5 | 709.7 | 772.8 | 543.9 | 786.2 | 854.2 | 833.5 | 847.4 | 814.3 | 796.9 | 639.4 | 788.1 | 699.5 | 48.6 | 125.2 | 172.3 | 35.9 | 102.8 | 168.3
581 | 419 | 466.1 | 186.44 | 217.9376 | 335.9 | 312.3 | 321.6 | 332 | 416.4 | 40.3 | 20.7 | 74.8 | 3.6 | 239.8 | 5.2 | 759.5 | 709.5 | 764.4 | 545.3 | 788.5 | 854.6 | 831.9 | 846.1 | 814.1 | 796.4 | 641.2 | 788.7 | 701.3 | 48.8 | 125.7 | 172.7 | 36 | 103.2 | 168.8
582 | 420 | 467.7 | 187.08 | 218.6857 | 333.3 | 312.9 | 321.3 | 331.6 | 415.2 | 40.3 | 20.7 | 74.9 | 3.6 | 219.7 | 5.2 | 760.6 | 709.5 | 764.8 | 546.5 | 792.1 | 854.6 | 832.7 | 846.6 | 815.5 | 797.7 | 642.7 | 789.2 | 701.8 | 49 | 126.1 | 173 | 36.2 | 103.6 | 169.5
583 | 421 | 467.8 | 187.12 | 218.7325 | 333.2 | 313.5 | 321.4 | 331.4 | 419.7 | 40.3 | 20.7 | 75 | 4.3 | 260.5 | 6 | 761.9 | 708.5 | 769.2 | 547.7 | 796.4 | 854.6 | 832.6 | 847.4 | 817.3 | 799.7 | 644 | 789.5 | 702 | 49.2 | 126.6 | 173.4 | 36.3 | 104 | 169.8
584 | 422 | 467.3 | 186.92 | 218.4987 | 332.8 | 315.7 | 321.6 | 331.5 | 424 | 40.4 | 20.7 | 75.2 | 4.3 | 234.2 | 6.7 | 762.7 | 708 | 772.1 | 549 | 799 | 854.2 | 832.8 | 849.4 | 819.3 | 800.5 | 645.5 | 789.4 | 702.4 | 49.3 | 127.1 | 173.9 | 36.5 | 104.4 | 170.1
585 | 423 | 467.7 | 187.08 | 218.6857 | 332.9 | 318 | 321.7 | 331.7 | 427.4 | 40.4 | 20.7 | 75.3 | 5.2 | 224.5 | 7.8 | 763.5 | 708.2 | 774.7 | 550.5 | 803.1 | 854.3 | 834.1 | 850.3 | 822.1 | 801.2 | 647.1 | 789.7 | 703.7 | 49.5 | 127.5 | 174.6 | 36.6 | 104.8 | 170.6
586 | 424 | 468 | 187.2 | 218.826 | 333.1 | 319.3 | 322.1 | 331.6 | 427.7 | 40.5 | 20.7 | 75.5 | 5.2 | 248.2 | 7.4 | 764.4 | 707.3 | 769.5 | 552.1 | 806.4 | 854.7 | 836 | 848 | 824.2 | 798.7 | 649.2 | 789.8 | 703.9 | 49.7 | 128 | 174.8 | 36.8 | 105.2 | 171.2
587 | 425 | 468.1 | 187.24 | 218.8728 | 332.6 | 319.7 | 322.3 | 331.4 | 423.4 | 40.5 | 20.7 | 75.6 | 4.6 | 219.8 | 7.2 | 765.5 | 709.2 | 760 | 553.5 | 807.7 | 855.3 | 837 | 846.8 | 824.6 | 797.2 | 651.3 | 790.1 | 704 | 49.9 | 128.4 | 175.1 | 36.9 | 105.6 | 171.8
588 | 426 | 467.7 | 187.08 | 218.6857 | 333.1 | 320.4 | 322.9 | 331.3 | 426.7 | 40.5 | 20.7 | 75.7 | 4.5 | 239.8 | 7.5 | 766.6 | 709.1 | 767.2 | 555 | 811.3 | 855.8 | 836.9 | 848 | 826 | 799.3 | 652.8 | 790.7 | 703.3 | 50.1 | 128.9 | 176 | 37 | 106 | 172.1
589 | 427 | 467.3 | 186.92 | 218.4987 | 334.6 | 320.7 | 323.7 | 331.2 | 432.3 | 40.6 | 20.7 | 75.6 | 3.9 | 227.7 | 7.4 | 767.5 | 711.5 | 771.8 | 556.7 | 813.6 | 855.8 | 837.9 | 849.5 | 825.8 | 798.3 | 654.5 | 790.4 | 701.9 | 50.3 | 129.3 | 176.8 | 37.2 | 106.4 | 172.5
590 | 428 | 467.2 | 186.88 | 218.452 | 335.3 | 320.4 | 324.4 | 331.4 | 433.6 | 40.7 | 20.7 | 75.7 | 3.7 | 223.5 | 6.8 | 768.3 | 711.2 | 775.9 | 558.5 | 816.3 | 856.2 | 838.1 | 853.3 | 826.6 | 798.1 | 656.9 | 789.6 | 701.7 | 50.5 | 129.7 | 177.2 | 37.3 | 106.7 | 173.1
591 | 429 | 467 | 186.8 | 218.3584 | 334.8 | 322.1 | 324.2 | 331.6 | 432.2 | 40.9 | 20.7 | 75.8 | 4.1 | 233.8 | 5.9 | 769.2 | 711.5 | 779.1 | 560.4 | 814.3 | 856.9 | 839.1 | 855.6 | 826.3 | 798.7 | 659.2 | 788.4 | 701.6 | 50.7 | 130.1 | 177.4 | 37.5 | 107.1 | 173.7
592 | 430 | 467.4 | 186.96 | 218.5455 | 336.1 | 322.9 | 323.6 | 331.5 | 431.3 | 41 | 20.7 | 75.8 | 4.2 | 216.2 | 5.1 | 770.1 | 712.2 | 774.1 | 562.2 | 808.2 | 857.7 | 840.3 | 854.1 | 823.4 | 797.2 | 661.4 | 787.8 | 701.4 | 50.9 | 130.5 | 177.9 | 37.6 | 107.5 | 174.1
593 | 431 | 468 | 187.2 | 218.826 | 336.8 | 322.3 | 323.5 | 332.5 | 431.9 | 41.1 | 20.7 | 75.8 | 3.9 | 196.8 | 5 | 771 | 715.4 | 769 | 564.3 | 803.8 | 858.5 | 838.4 | 853.3 | 821 | 796 | 663.9 | 787.8 | 702.2 | 51.1 | 131 | 178.4 | 37.8 | 107.9 | 174.5
594 | 432 | 467.8 | 187.12 | 218.7325 | 335 | 321.2 | 323.6 | 333.6 | 431.5 | 41.2 | 20.7 | 75.9 | 4.6 | 216.7 | 4.9 | 772 | 718 | 766.3 | 566.3 | 801 | 858.9 | 835.9 | 849.7 | 819.5 | 795.9 | 666.4 | 788.5 | 703.4 | 51.2 | 131.5 | 179 | 37.9 | 108.4 | 175
595 | 433 | 468.5 | 187.4 | 219.0598 | 332.8 | 321.7 | 324.1 | 334.4 | 429.1 | 41.3 | 20.7 | 76 | 4.7 | 206.8 | 5.5 | 772.9 | 718.6 | 758 | 568.1 | 801.5 | 859.4 | 834.5 | 847.5 | 819.8 | 795.3 | 668 | 789.4 | 705.7 | 51.4 | 132 | 179.4 | 38.1 | 108.8 | 175.6
596 | 434 | 468 | 187.2 | 218.826 | 334.1 | 322.2 | 323.3 | 334.6 | 425.2 | 41.3 | 20.7 | 76.2 | 4.6 | 212.4 | 6.1 | 773.7 | 718.2 | 757 | 569.7 | 800.8 | 860.2 | 834.8 | 849.9 | 819.3 | 795.3 | 669.4 | 790.5 | 707.8 | 51.6 | 132.5 | 179.8 | 38.2 | 109.1 | 176.3
597 | 435 | 467.8 | 187.12 | 218.7325 | 335.5 | 322.1 | 323.3 | 334.6 | 424.8 | 41.3 | 20.6 | 76.2 | 3.9 | 228.7 | 5.5 | 774.5 | 717 | 757.4 | 571.2 | 802.9 | 860.9 | 835.7 | 850.9 | 823.9 | 797.2 | 670.3 | 791.2 | 710 | 51.8 | 133 | 180.4 | 38.4 | 109.4 | 176.8
598 | 436 | 467.2 | 186.88 | 218.452 | 336.1 | 321.1 | 324.3 | 334.2 | 427.7 | 41.4 | 20.6 | 76.2 | 4.2 | 233.8 | 4.7 | 775.4 | 715.7 | 759.4 | 572.7 | 805.7 | 861.6 | 837.1 | 852.9 | 827.6 | 797.9 | 671.3 | 791.2 | 711.4 | 52 | 133.4 | 180.8 | 38.5 | 109.8 | 177.1
599 | 437 | 467.5 | 187 | 218.5922 | 334.2 | 320.9 | 325.5 | 333.9 | 426.2 | 41.4 | 20.7 | 76.3 | 4.3 | 214.5 | 3.9 | 776.1 | 714.5 | 761.2 | 573.9 | 808.1 | 861.9 | 836.8 | 855.7 | 827.8 | 798.6 | 672.1 | 791.3 | 712.5 | 52.2 | 133.9 | 181 | 38.6 | 110.1 | 177.6
600 | 438 | 467.4 | 186.96 | 218.5455 | 332.4 | 321.6 | 326.8 | 334.5 | 425.7 | 41.4 | 20.6 | 76.4 | 4.4 | 209.6 | 3.6 | 776.8 | 711.7 | 762.9 | 575.2 | 808.1 | 862 | 836.3 | 857 | 826.8 | 798.5 | 672.9 | 790.9 | 712.9 | 52.4 | 134.3 | 181.5 | 38.8 | 110.5 | 178.2
601 | 439 | 467.8 | 187.12 | 218.7325 | 331.9 | 322.3 | 327.4 | 335.6 | 422.8 | 41.4 | 20.6 | 76.6 | 4.9 | 211.7 | 4.2 | 777.5 | 711.6 | 760.9 | 576.6 | 810.7 | 862.4 | 836 | 857.2 | 827 | 797.8 | 673.7 | 790.6 | 713.9 | 52.6 | 134.7 | 181.9 | 38.9 | 110.8 | 178.7
602 | 440 | 467.7 | 187.08 | 218.6857 | 332 | 323 | 327 | 336.6 | 418.6 | 41.4 | 20.6 | 76.8 | 4.6 | 228.7 | 4.9 | 778.3 | 712.5 | 762 | 578.3 | 810.2 | 863.5 | 836.2 | 856.3 | 825.9 | 797.5 | 674.6 | 789.9 | 714.6 | 52.8 | 135.2 | 182.3 | 39.1 | 111.2 | 179.1
603 | 441 | 468.3 | 187.32 | 218.9663 | 332.8 | 322.7 | 327.4 | 337.4 | 416.9 | 41.4 | 20.6 | 77 | 5.3 | 224.9 | 5.1 | 779.1 | 712.2 | 763.2 | 579.9 | 810.9 | 864.9 | 834.7 | 858.1 | 824.6 | 797.7 | 675.7 | 790.8 | 715.6 | 53 | 135.6 | 182.7 | 39.3 | 111.6 | 179.5
604 | 442 | 468 | 187.2 | 218.826 | 334.8 | 322.5 | 327.4 | 337.7 | 415.6 | 41.4 | 20.6 | 77.2 | 5.2 | 240.7 | 4.8 | 779.9 | 711.5 | 769.9 | 581.5 | 813 | 865.4 | 833.9 | 859.9 | 825.2 | 799.9 | 676.4 | 791.1 | 716.8 | 53.2 | 136 | 183 | 39.4 | 112 | 180
605 | 443 | 467.8 | 187.12 | 218.7325 | 336.4 | 323.2 | 327.5 | 337.5 | 418.2 | 41.3 | 20.6 | 77.3 | 5.1 | 246.5 | 4.4 | 780.4 | 711 | 774.5 | 583.3 | 814.4 | 866.1 | 835.7 | 862 | 826.5 | 800.8 | 677.4 | 790.3 | 716.4 | 53.3 | 136.5 | 183.7 | 39.6 | 112.6 | 180.6
606 | 444 | 467.8 | 187.12 | 218.7325 | 335.3 | 323.4 | 327.8 | 337.7 | 418 | 41.4 | 20.6 | 77.4 | 4.3 | 235.2 | 4.1 | 781.1 | 708.9 | 777.5 | 584.8 | 815.8 | 866.9 | 835.9 | 865.1 | 825.5 | 801.1 | 678.4 | 790.4 | 715.8 | 53.5 | 136.9 | 184.1 | 39.7 | 113.1 | 181.3
607 | 445 | 467.2 | 186.88 | 218.452 | 335 | 324.5 | 327 | 338.1 | 420 | 41.4 | 20.6 | 77.5 | 4.6 | 224.6 | 4 | 781.5 | 708.2 | 779.3 | 586.5 | 815.6 | 867.8 | 836.9 | 867.4 | 826 | 800.6 | 679.7 | 788.9 | 713.5 | 53.7 | 137.3 | 184.9 | 39.9 | 113.5 | 181.9
608 | 446 | 469 | 187.6 | 219.2936 | 335.7 | 326.3 | 327 | 339.4 | 420.7 | 41.4 | 20.6 | 77.5 | 4.4 | 204.8 | 4 | 781.9 | 708.4 | 779.3 | 588.4 | 815.7 | 868.6 | 837.3 | 868.3 | 826 | 800.7 | 681.3 | 788.6 | 712.4 | 53.9 | 137.8 | 185.6 | 40 | 114 | 182.2
609 | 447 | 467.3 | 186.92 | 218.4987 | 335.1 | 327.4 | 327 | 340.7 | 420.8 | 41.4 | 20.6 | 77.5 | 4.6 | 214 | 3.4 | 782.4 | 707.9 | 777.9 | 590.4 | 816.3 | 869.4 | 837.5 | 868.6 | 826 | 799.9 | 682.9 | 788.4 | 712.7 | 54.1 | 138.3 | 185.9 | 40.2 | 114.6 | 182.5
610 | 448 | 468 | 187.2 | 218.826 | 334.3 | 327.9 | 327.7 | 341.4 | 420.5 | 41.4 | 20.6 | 77.6 | 4.8 | 248.4 | 3.8 | 782.9 | 710.2 | 774 | 592.3 | 814.1 | 870.3 | 837.2 | 865.5 | 825.2 | 800.2 | 684.1 | 789.1 | 713.6 | 54.3 | 138.7 | 186.1 | 40.3 | 115.2 | 183
611 | 449 | 467.3 | 186.92 | 218.4987 | 335 | 327.2 | 327.8 | 342 | 420.2 | 41.6 | 20.6 | 77.6 | 5 | 249.8 | 5.7 | 783.6 | 713.1 | 769.3 | 594.4 | 813 | 871.2 | 836.3 | 863 | 825.1 | 800 | 685.1 | 790.6 | 715 | 54.5 | 139.1 | 186.4 | 40.5 | 116 | 183.6
612 | 450 | 467.2 | 186.88 | 218.452 | 336.3 | 326.1 | 327.6 | 342.2 | 420.3 | 41.8 | 20.6 | 77.7 | 5.1 | 227.3 | 6.9 | 784.3 | 713.9 | 767.5 | 596.4 | 816.2 | 871.4 | 835.2 | 866.1 | 825.8 | 801.3 | 685.6 | 791.4 | 716.2 | 54.7 | 139.6 | 186.8 | 40.6 | 116.7 | 183.9
613 | 451 | 469.1 | 187.64 | 219.3403 | 337.2 | 325.3 | 328.5 | 341.7 | 419.1 | 41.9 | 20.6 | 77.9 | 5.4 | 244.4 | 7.1 | 784.8 | 711.2 | 774.7 | 598.2 | 818.9 | 871.4 | 835.8 | 868.5 | 827 | 802.1 | 685.9 | 790.6 | 716.7 | 54.8 | 140 | 187.4 | 40.8 | 117.6 | 184.4
614 | 452 | 469.6 | 187.84 | 219.5741 | 337.3 | 324.4 | 329.1 | 341.8 | 416.6 | 42 | 20.6 | 77.9 | 4.6 | 245 | 6.5 | 785.3 | 710.2 | 780.1 | 600.1 | 818.4 | 872 | 837.2 | 870.9 | 826.1 | 801.6 | 686.8 | 789.9 | 715.7 | 55 | 140.5 | 188 | 41 | 118.3 | 185.1
615 | 453 | 469 | 187.6 | 219.2936 | 338 | 324 | 329 | 342.7 | 416 | 42.1 | 20.6 | 77.9 | 4.4 | 226.4 | 5.9 | 785.7 | 708.8 | 779.3 | 602.1 | 814.6 | 873.1 | 837.6 | 872.3 | 823.3 | 801.7 | 688.5 | 789.4 | 715.4 | 55.2 | 140.9 | 188.6 | 41.1 | 119 | 185.8
616 | 454 | 469 | 187.6 | 219.2936 | 337.4 | 324.6 | 329.1 | 343 | 413.2 | 42.2 | 20.5 | 77.9 | 4.8 | 253.6 | 5.2 | 786.3 | 710.9 | 774.3 | 603.9 | 814.3 | 874.2 | 836.7 | 872.2 | 824 | 801.9 | 690.1 | 790.9 | 716.8 | 55.4 | 141.4 | 188.9 | 41.3 | 119.6 | 186.3
617 | 455 | 468 | 187.2 | 218.826 | 337.3 | 325.4 | 329.2 | 343.5 | 413 | 42.1 | 20.6 | 78 | 4.5 | 257.5 | 5.5 | 786.7 | 713.4 | 770.3 | 605.8 | 816.2 | 874.7 | 835.8 | 869.7 | 825.5 | 802.8 | 690.8 | 791.2 | 718.4 | 55.6 | 141.8 | 189.3 | 41.4 | 120.1 | 186.7
618 | 456 | 468.8 | 187.52 | 219.2001 | 337.7 | 325.9 | 328.4 | 343.8 | 412.4 | 42.1 | 20.5 | 78 | 4.2 | 226 | 6.2 | 787.3 | 715.4 | 767.4 | 607.7 | 818 | 875.3 | 836.7 | 869.4 | 826.4 | 802.5 | 691.7 | 791.5 | 719.4 | 55.8 | 142.2 | 189.7 | 41.6 | 120.5 | 187.2
619 | 457 | 468.3 | 187.32 | 218.9663 | 337.4 | 326.1 | 328.1 | 343.7 | 410.2 | 42.1 | 20.5 | 78.1 | 4 | 221.9 | 6.6 | 787.8 | 716.1 | 763.4 | 609.4 | 821.5 | 875.9 | 835.7 | 867.1 | 827.1 | 802.7 | 692.3 | 792.2 | 720.5 | 56 | 142.7 | 190.3 | 41.7 | 120.9 | 187.6
620 | 458 | 468.3 | 187.32 | 218.9663 | 337.3 | 326.5 | 327.7 | 342.4 | 410.9 | 42.1 | 20.5 | 78.2 | 4.2 | 232 | 6.3 | 788.3 | 716.2 | 763.5 | 610.9 | 821 | 876.5 | 836.1 | 863.8 | 826.2 | 804.1 | 692.8 | 792.5 | 721.6 | 56.2 | 143.1 | 190.7 | 41.9 | 121.4 | 187.9
621 | 459 | 468.4 | 187.36 | 219.013 | 337.9 | 326.5 | 328.3 | 340.6 | 410.5 | 42.1 | 20.5 | 78.3 | 4 | 219 | 6.8 | 788.6 | 718.3 | 759.7 | 612.4 | 818 | 877.2 | 835.3 | 861.8 | 824.9 | 804 | 693.2 | 793.4 | 723.4 | 56.4 | 143.6 | 190.9 | 42 | 121.8 | 188.5
622 | 460 | 468.2 | 187.28 | 218.9195 | 339 | 326.6 | 328.6 | 340.2 | 409.7 | 42.1 | 20.5 | 78.5 | 4 | 224.7 | 6.5 | 789 | 719.6 | 755.1 | 614.1 | 820.4 | 877.4 | 833.9 | 859.4 | 825.2 | 802.7 | 693.8 | 793.2 | 724.6 | 56.6 | 144 | 191.3 | 42.2 | 122.2 | 189
623 | 461 | 468.8 | 187.52 | 219.2001 | 339.9 | 326.7 | 329.5 | 340.8 | 409 | 42.1 | 20.5 | 78.6 | 3.9 | 250.7 | 6.1 | 789.4 | 719.3 | 752.6 | 615.7 | 821 | 878.1 | 833.3 | 859.2 | 824.8 | 802.5 | 694.2 | 794 | 725.3 | 56.8 | 144.4 | 191.7 | 42.3 | 122.5 | 189.7
624 | 462 | 468.6 | 187.44 | 219.1066 | 340.5 | 326.9 | 330.3 | 341.7 | 409 | 42.1 | 20.5 | 78.6 | 4.1 | 234.7 | 6 | 789.8 | 715.7 | 754.7 | 617.2 | 820.4 | 878.8 | 833.2 | 863.7 | 825.1 | 800.1 | 694.7 | 793.8 | 724.8 | 57 | 144.9 | 192.2 | 42.5 | 122.9 | 190
625 | 463 | 467.9 | 187.16 | 218.7793 | 340.8 | 326.9 | 331.4 | 342.5 | 410.7 | 42.1 | 20.5 | 78.6 | 4.3 | 239.5 | 5.8 | 790.3 | 714.3 | 754.5 | 618.8 | 819.2 | 879.3 | 833.3 | 865.2 | 823.5 | 799.9 | 695.4 | 793.9 | 725.2 | 57.2 | 145.3 | 192.6 | 42.6 | 123.2 | 190.2
626 | 464 | 469.4 | 187.76 | 219.4806 | 340.3 | 326.2 | 331.7 | 343.1 | 411.7 | 42.2 | 20.5 | 78.7 | 4.1 | 238.2 | 5.5 | 790.9 | 714.8 | 752.7 | 620.7 | 816.8 | 879.8 | 832.2 | 864.4 | 823.2 | 798.8 | 696.4 | 794 | 726 | 57.4 | 145.7 | 192.9 | 42.8 | 123.5 | 190.6
627 | 465 | 471 | 188.4 | 220.2287 | 341.5 | 326.2 | 331.4 | 343.7 | 413.5 | 42.3 | 20.5 | 78.8 | 3.7 | 229 | 5.3 | 791.5 | 718.5 | 751 | 622.7 | 812.5 | 880.6 | 829.7 | 861.2 | 819 | 798.1 | 697.9 | 795.1 | 726.8 | 57.6 | 146.1 | 193.4 | 42.9 | 123.8 | 191.2
628 | 466 | 471.6 | 188.64 | 220.5093 | 342.6 | 325.7 | 331.4 | 344.1 | 414.5 | 42.4 | 20.5 | 79 | 4 | 239.6 | 5 | 792.1 | 720.4 | 742.5 | 624.7 | 808.4 | 881.4 | 825.6 | 859 | 814.2 | 794.8 | 700.1 | 796.5 | 727.4 | 57.8 | 146.5 | 194.1 | 43.1 | 124 | 192.2
629 | 467 | 469.4 | 187.76 | 219.4806 | 344.6 | 325.9 | 332.9 | 344.2 | 416.5 | 42.5 | 20.5 | 79.1 | 4 | 247.3 | 5 | 792.7 | 718.2 | 737.4 | 626.7 | 803.2 | 882 | 822.9 | 855.3 | 810.4 | 793.6 | 702 | 797.3 | 728.1 | 58 | 147 | 194.7 | 43.2 | 124.3 | 192.8
630 | 468 | 469 | 187.6 | 219.2936 | 346.2 | 325.6 | 334.9 | 343.9 | 417 | 42.6 | 20.5 | 79.3 | 4.4 | 247.3 | 5.1 | 793.3 | 718.4 | 734.9 | 628.8 | 799.7 | 882.7 | 821.1 | 855.8 | 809 | 791.2 | 703.8 | 798.1 | 728.9 | 58.2 | 147.4 | 195.1 | 43.4 | 124.6 | 193.3
631 | 469 | 469 | 187.6 | 219.2936 | 347.1 | 325.8 | 337.1 | 343.5 | 417.3 | 42.6 | 20.5 | 79.4 | 4 | 242.3 | 4.9 | 793.8 | 718.2 | 734 | 630.5 | 802.6 | 882.9 | 821.3 | 856.7 | 812.6 | 791.6 | 705 | 798.3 | 730.4 | 58.4 | 147.8 | 195.4 | 43.5 | 124.8 | 193.9
632 | 470 | 469.2 | 187.68 | 219.3871 | 347.3 | 325.6 | 337.9 | 343.5 | 416.5 | 42.7 | 20.5 | 79.6 | 4.1 | 241.7 | 4.4 | 794.2 | 715.8 | 739.8 | 631.9 | 805.5 | 882.9 | 822.4 | 858.3 | 815 | 791.8 | 705.2 | 798.2 | 731.8 | 58.6 | 148.2 | 195.6 | 43.7 | 125.1 | 194.3
633 | 471 | 468.5 | 187.4 | 219.0598 | 346.7 | 325.1 | 337.6 | 343.4 | 415 | 42.8 | 20.5 | 79.7 | 3.9 | 239.4 | 4.3 | 794.4 | 713.1 | 745.2 | 633 | 807.1 | 883 | 824 | 860.8 | 815.2 | 792.2 | 705 | 797.8 | 731.6 | 58.8 | 148.6 | 195.9 | 43.8 | 125.4 | 194.7
634 | 472 | 469.1 | 187.64 | 219.3403 | 345.4 | 325.6 | 337 | 342.8 | 414.7 | 43 | 20.5 | 79.8 | 3.7 | 225.1 | 4.2 | 794.7 | 710.7 | 754.8 | 634.2 | 807.7 | 883.1 | 825.4 | 863.9 | 817.6 | 792.2 | 704.9 | 797.3 | 730.2 | 59 | 149 | 196.5 | 44 | 125.6 | 195
635 | 473 | 470.2 | 188.08 | 219.8547 | 345.4 | 325.9 | 336.2 | 342.4 | 423.6 | 43.1 | 20.5 | 79.9 | 4.6 | 218.4 | 4 | 795 | 709.7 | 761 | 635.5 | 811.4 | 883 | 827.4 | 864.3 | 821 | 793.7 | 705 | 796.5 | 729 | 59.2 | 149.4 | 197.2 | 44.1 | 125.9 | 195.5
636 | 474 | 469.7 | 187.88 | 219.6209 | 344.9 | 326.6 | 335 | 342.1 | 426.8 | 43.2 | 20.5 | 80.1 | 4.4 | 247.5 | 4.6 | 795.3 | 710 | 767.3 | 637 | 814.3 | 882.6 | 828.2 | 864.9 | 822 | 795 | 705.2 | 794.9 | 728.7 | 59.4 | 149.8 | 197.5 | 44.3 | 126.1 | 195.8
637 | 475 | 469.5 | 187.8 | 219.5274 | 344.2 | 327.9 | 334.6 | 342.2 | 429.5 | 43.2 | 20.5 | 80.1 | 3.9 | 245.2 | 5.1 | 795.6 | 708.2 | 768.2 | 638.5 | 816.6 | 882.7 | 830.2 | 866.3 | 821.3 | 795.5 | 705.4 | 793.6 | 730.5 | 59.6 | 150.2 | 197.9 | 44.5 | 126.3 | 196.2
638 | 476 | 468.8 | 187.52 | 219.2001 | 344.4 | 327.8 | 334.3 | 343.2 | 427.7 | 43.2 | 20.4 | 80.1 | 3.6 | 254.3 | 5.5 | 795.8 | 706.4 | 767.6 | 639.6 | 818.6 | 883.1 | 830.6 | 869 | 821.2 | 795.7 | 705 | 794.1 | 732.5 | 59.8 | 150.7 | 198.2 | 44.6 | 126.5 | 196.3
639 | 477 | 468.8 | 187.52 | 219.2001 | 344.5 | 328 | 333.7 | 344 | 423.1 | 43.3 | 20.4 | 80.2 | 4.1 | 246 | 5.7 | 796.1 | 704.8 | 769.2 | 640.7 | 820.9 | 883.4 | 831.9 | 869.4 | 823.1 | 796.4 | 704.9 | 793.6 | 733.7 | 60 | 151.1 | 198.5 | 44.8 | 126.6 | 196.7
640 | 478 | 469.6 | 187.84 | 219.5741 | 343.7 | 329.3 | 331.9 | 344.6 | 422.7 | 43.4 | 20.4 | 80.3 | 4.3 | 263.4 | 5.5 | 796.5 | 704.7 | 772.2 | 641.8 | 825.3 | 883.5 | 832.1 | 869.2 | 824.6 | 797.5 | 704.8 | 794 | 733.3 | 60.1 | 151.4 | 199.1 | 44.9 | 126.8 | 197.2
641 | 479 | 468.1 | 187.24 | 218.8728 | 342 | 330.5 | 330.9 | 345.1 | 425.1 | 43.4 | 20.4 | 80.4 | 4 | 267.1 | 5.7 | 796.6 | 702.7 | 777 | 642.8 | 827 | 883.7 | 833.1 | 870.2 | 824.3 | 798 | 704.9 | 793 | 731.3 | 60.3 | 151.8 | 199.7 | 45.1 | 127.1 | 197.5
642 | 480 | 469.1 | 187.64 | 219.3403 | 341.2 | 331.5 | 330.7 | 345.7 | 433.5 | 43.5 | 20.4 | 80.6 | 4.2 | 258.9 | 5.8 | 796.8 | 702.6 | 781.7 | 644 | 827.4 | 883.5 | 833.8 | 871.7 | 823.7 | 799.5 | 705 | 792 | 729.5 | 60.5 | 152.3 | 200.2 | 45.2 | 127.3 | 197.7
643 | 481 | 469 | 187.6 | 219.2936 | 341.5 | 332.8 | 329.5 | 346.1 | 440.5 | 43.5 | 20.4 | 80.7 | 4.3 | 265.3 | 5.4 | 796.9 | 700.9 | 783.2 | 645 | 829.1 | 883.5 | 835.3 | 873.5 | 824.6 | 800.2 | 705.7 | 791.6 | 728.2 | 60.7 | 152.6 | 200.4 | 45.4 | 127.6 | 198.2
644 | 482 | 467.8 | 187.12 | 218.7325 | 342.1 | 333.7 | 329.3 | 346.7 | 440.2 | 43.5 | 20.4 | 80.9 | 4.2 | 256.8 | 5.2 | 796.9 | 699.4 | 780.8 | 645.8 | 829.7 | 884.1 | 836.4 | 876.3 | 827.2 | 800.4 | 706.1 | 792.4 | 728.3 | 60.9 | 153.1 | 200.7 | 45.5 | 127.9 | 198.8
645 | 483 | 468.6 | 187.44 | 219.1066 | 341.4 | 334.1 | 328.8 | 347.2 | 435.5 | 43.6 | 20.4 | 81.1 | 4.6 | 240.1 | 4.9 | 796.9 | 701.1 | 778.6 | 646.7 | 831 | 884.5 | 836.4 | 879.2 | 827.8 | 800.6 | 705.8 | 792.3 | 730.5 | 61.1 | 153.5 | 201.1 | 45.7 | 128.1 | 199.2
646 | 484 | 467.5 | 187 | 218.5922 | 340.9 | 334.2 | 327.7 | 347.9 | 432.7 | 43.7 | 20.4 | 81.4 | 4.7 | 232.5 | 4.5 | 796.8 | 698.8 | 778.7 | 647.6 | 829 | 884.9 | 835.4 | 880.1 | 825.8 | 799.1 | 706.2 | 790.5 | 730.1 | 61.3 | 153.9 | 201.8 | 45.8 | 128.4 | 199.4
647 | 485 | 468.3 | 187.32 | 218.9663 | 342.1 | 334.1 | 328.6 | 348.2 | 432.9 | 43.8 | 20.4 | 81.4 | 5.1 | 239.4 | 4.4 | 796.9 | 699.4 | 777.6 | 648.6 | 826.5 | 885.6 | 833.1 | 881.6 | 824.3 | 797.4 | 707 | 790.9 | 729.7 | 61.5 | 154.3 | 202.3 | 46 | 128.7 | 199.7
648 | 486 | 467.7 | 187.08 | 218.6857 | 343.5 | 334.4 | 329.5 | 348.1 | 432.3 | 43.8 | 20.4 | 81.5 | 4.4 | 226.9 | 4.5 | 796.9 | 700 | 775.1 | 649.6 | 825.6 | 886 | 833 | 880 | 824 | 798.4 | 707.4 | 791.5 | 731.1 | 61.7 | 154.7 | 202.6 | 46.1 | 129 | 200
649 | 487 | 467.7 | 187.08 | 218.6857 | 344.1 | 334.6 | 330 | 347.8 | 430.6 | 43.9 | 20.4 | 81.6 | 4.6 | 242.1 | 4.9 | 797 | 698.8 | 776.8 | 650.3 | 823.9 | 886.5 | 833.3 | 878.1 | 823.5 | 798.2 | 707.4 | 790.7 | 732.3 | 61.9 | 155.1 | 202.8 | 46.3 | 129.2 | 200.3
650 | 488 | 468.7 | 187.48 | 219.1533 | 344.6 | 334.3 | 329.5 | 347.1 | 431.5 | 43.9 | 20.4 | 81.5 | 4.5 | 243.7 | 6.1 | 797.1 | 698.7 | 778.4 | 651.2 | 823 | 886.8 | 832.2 | 879.2 | 822.1 | 797 | 707.7 | 790 | 731.1 | 62.1 | 155.4 | 203.8 | 46.5 | 129.5 | 200.9
651 | 489 | 468.1 | 187.24 | 218.8728 | 345.1 | 335 | 329.5 | 346.1 | 430.7 | 44 | 20.4 | 81.5 | 4.1 | 242.6 | 6.3 | 797.1 | 700.7 | 780 | 652.2 | 821.6 | 886.8 | 831.7 | 881 | 823.2 | 797.4 | 708.6 | 790.5 | 731 | 62.3 | 155.8 | 204.3 | 46.6 | 129.8 | 201.5
652 | 490 | 468.3 | 187.32 | 218.9663 | 344.3 | 336 | 330.6 | 345.4 | 431.5 | 44.1 | 20.4 | 81.6 | 4.7 | 236.2 | 5.9 | 797.3 | 701 | 782.9 | 653.1 | 822.2 | 886.7 | 833.1 | 878.7 | 824.9 | 798.1 | 709.6 | 790.9 | 730.7 | 62.5 | 156.2 | 204.9 | 46.8 | 130.1 | 201.8
653 | 491 | 468 | 187.2 | 218.826 | 343.2 | 336.6 | 330.9 | 345.3 | 433.8 | 44.2 | 20.4 | 81.7 | 4.7 | 230.9 | 5.9 | 797.4 | 701 | 785.1 | 653.9 | 824 | 886.4 | 834 | 879.3 | 825.2 | 800.2 | 710.1 | 791.3 | 730.5 | 62.7 | 156.6 | 205.5 | 46.9 | 130.3 | 202.4
654 | 492 | 468.6 | 187.44 | 219.1066 | 343.3 | 336.7 | 330.3 | 345.7 | 436 | 44.4 | 20.4 | 81.7 | 4.2 | 222.4 | 6.1 | 797.4 | 702.8 | 782.9 | 654.8 | 824 | 886.4 | 834.7 | 879 | 825.4 | 801.3 | 710.4 | 791.9 | 731.7 | 62.9 | 156.9 | 205.6 | 47.1 | 130.6 | 203.1
655 | 493 | 465.5 | 186.2 | 217.6571 | 343.8 | 337.1 | 329.3 | 346.2 | 434.1 | 44.4 | 20.4 | 81.8 | 4.1 | 235.1 | 5.1 | 797.4 | 702.2 | 780.4 | 655.6 | 825 | 886.5 | 835.8 | 877.3 | 826.3 | 801.4 | 710.3 | 791.6 | 733.1 | 63.1 | 157.3 | 206 | 47.2 | 130.8 | 203.4
656 | 494 | 466.9 | 186.76 | 218.3117 | 343.9 | 337.5 | 328.8 | 346.6 | 432.6 | 44.5 | 20.4 | 81.8 | 4.4 | 256.7 | 5.1 | 797.5 | 702.1 | 778.6 | 656.2 | 825.4 | 886.5 | 836.1 | 877.4 | 828.1 | 801.6 | 710 | 791.5 | 734.8 | 63.3 | 157.7 | 206.3 | 47.4 | 131 | 203.5
657 | 495 | 466.7 | 186.68 | 218.2182 | 344.1 | 337.7 | 328.6 | 346.8 | 430.4 | 44.6 | 20.4 | 81.9 | 4.1 | 248.4 | 4.7 | 797.8 | 700.9 | 777.6 | 656.9 | 827.1 | 886.6 | 835.7 | 877.1 | 827.5 | 801 | 709.9 | 790.9 | 735.7 | 63.6 | 158.1 | 206.4 | 47.5 | 131.2 | 203.9
658 | 496 | 466.7 | 186.68 | 218.2182 | 345 | 337.4 | 328 | 347.2 | 427.4 | 44.6 | 20.4 | 81.9 | 4.1 | 248.4 | 4.1 | 798.1 | 700.9 | 773.7 | 657.4 | 828.8 | 886.9 | 834.6 | 875.7 | 827.8 | 801 | 709.7 | 791.3 | 736.7 | 63.8 | 158.4 | 206.5 | 47.7 | 131.4 | 204.4
659 | 497 | 468.8 | 187.52 | 219.2001 | 345.2 | 336.6 | 327.3 | 347.4 | 424.2 | 44.7 | 20.4 | 81.9 | 4.2 | 252.6 | 4.9 | 798.2 | 703.4 | 771.5 | 658 | 831.4 | 887.3 | 833.5 | 873.7 | 826.7 | 801.8 | 709.4 | 792.4 | 738 | 64 | 158.8 | 206.8 | 47.9 | 131.5 | 204.8
660 | 498 | 471.9 | 188.76 | 220.6496 | 344.7 | 336.3 | 326.9 | 347.1 | 422.8 | 44.8 | 20.4 | 81.9 | 4.5 | 242.3 | 6.8 | 798.5 | 705.3 | 770.9 | 658.7 | 832.6 | 887.7 | 833.6 | 872.9 | 826.4 | 801.5 | 709.2 | 793.1 | 739.9 | 64.2 | 159.2 | 207.3 | 48 | 131.7 | 205.2
661 | 499 | 471.1 | 188.44 | 220.2755 | 344.8 | 336.3 | 327.7 | 346.6 | 422.5 | 45 | 20.4 | 82 | 4.5 | 243.9 | 7.6 | 798.7 | 702.6 | 770.6 | 659.3 | 834.8 | 888.5 | 833 | 872.8 | 826.7 | 800.4 | 709.4 | 792.2 | 739.9 | 64.4 | 159.5 | 207.8 | 48.2 | 131.9 | 205.4
662 | 500 | 468.5 | 187.4 | 219.0598 | 345.2 | 335.7 | 328.9 | 346.3 | 423.7 | 45.1 | 20.3 | 82.1 | 4.5 | 245.7 | 7.5 | 798.9 | 699 | 772 | 659.8 | 833.7 | 889.3 | 831.5 | 875.1 | 825.4 | 798.9 | 709.4 | 791.2 | 737.6 | 64.6 | 160 | 208.6 | 48.4 | 132.1 | 205.5
663 | 501 | 467.6 | 187.04 | 218.639 | 344.8 | 336.2 | 329.2 | 346 | 429.1 | 45.2 | 20.3 | 82.1 | 4.3 | 248.5 | 7.2 | 799.2 | 697.1 | 772.1 | 660.5 | 834 | 889.8 | 831.4 | 875.6 | 825.2 | 798.4 | 709.7 | 791.2 | 736.5 | 64.8 | 160.4 | 208.8 | 48.5 | 132.4 | 205.9
664 | 502 | 467.7 | 187.08 | 218.6857 | 345.1 | 337.1 | 328.8 | 346.5 | 429.6 | 45.2 | 20.3 | 82.1 | 4.2 | 246.8 | 7 | 799.4 | 698 | 766.7 | 661.4 | 833.8 | 890.4 | 830.8 | 872.2 | 823.7 | 797.1 | 710 | 791.4 | 737.1 | 65.1 | 160.8 | 209 | 48.7 | 132.6 | 206.5
665 | 503 | 468.4 | 187.36 | 219.013 | 344.8 | 337.9 | 327.8 | 346.9 | 427.1 | 45.2 | 20.3 | 82.2 | 4.7 | 250.9 | 6.3 | 799.7 | 699.3 | 764.8 | 662 | 834.6 | 890.9 | 828.4 | 872.2 | 822 | 795.5 | 710.6 | 792.4 | 737.4 | 65.3 | 161.1 | 209.3 | 48.9 | 132.8 | 207.2
666 | 504 | 468.4 | 187.36 | 219.013 | 343.5 | 337.6 | 327.3 | 346.7 | 427.1 | 45.2 | 20.3 | 82.4 | 4.7 | 265.5 | 5.3 | 800.1 | 700 | 765.7 | 662.9 | 834.8 | 891.7 | 828.1 | 873.4 | 822.8 | 795.4 | 711 | 793.3 | 738.7 | 65.5 | 161.5 | 209.8 | 49 | 133 | 207.4
667 | 505 | 469 | 187.6 | 219.2936 | 344 | 337 | 327.6 | 346.6 | 427.1 | 45.2 | 20.3 | 82.5 | 4.8 | 247.6 | 5.2 | 800.6 | 699.6 | 766.1 | 663.7 | 831.6 | 892.4 | 826.6 | 873.5 | 820.8 | 793.9 | 711.5 | 793.8 | 738.5 | 65.7 | 161.9 | 210.3 | 49.2 | 133.2 | 207.7
668 | 506 | 469.2 | 187.68 | 219.3871 | 342.9 | 335.9 | 326.9 | 345.9 | 429.3 | 45.3 | 20.3 | 82.6 | 4.4 | 226.1 | 5.8 | 801 | 697.5 | 766.4 | 664.6 | 830.1 | 893.1 | 826 | 873.5 | 820.9 | 792.8 | 712.3 | 794 | 737.2 | 65.9 | 162.3 | 211 | 49.4 | 133.5 | 207.9
669 | 507 | 468.8 | 187.52 | 219.2001 | 341.7 | 335.1 | 326.5 | 345.4 | 442.2 | 45.3 | 20.3 | 82.7 | 4.1 | 245.8 | 6 | 801.4 | 697.4 | 766.5 | 665.7 | 826.6 | 893.7 | 824.9 | 870.5 | 820.8 | 790.8 | 713.5 | 794.4 | 733.9 | 66.1 | 162.7 | 211.6 | 49.6 | 133.8 | 208.3
670 | 508 | 469.2 | 187.68 | 219.3871 | 342.7 | 336.1 | 326.5 | 345.8 | 449.6 | 45.4 | 20.3 | 82.8 | 4.2 | 254.6 | 6.3 | 801.8 | 696.6 | 768 | 667.1 | 826.7 | 894.1 | 825.1 | 869.3 | 822 | 790.1 | 714.4 | 794.3 | 730.2 | 66.3 | 163.1 | 212.1 | 49.7 | 134.1 | 208.7
671 | 509 | 467.9 | 187.16 | 218.7793 | 343.6 | 337.2 | 325.7 | 346.9 | 457.9 | 45.5 | 20.3 | 82.9 | 4.4 | 255.6 | 7 | 802.1 | 695 | 770 | 668.2 | 829.6 | 894.5 | 826.7 | 868.7 | 824.1 | 789.6 | 715.3 | 797.6 | 728 | 66.6 | 163.6 | 212.5 | 49.9 | 134.4 | 209.1
672 | 510 | 465.3 | 186.12 | 217.5636 | 344 | 337.2 | 325.6 | 348.3 | 468.6 | 45.6 | 20.3 | 83.1 | 4.5 | 266 | 7.3 | 802.4 | 693.2 | 771.6 | 669 | 832 | 894.7 | 828.4 | 868.8 | 826.1 | 790.7 | 715.5 | 797.4 | 727.3 | 66.8 | 164 | 212.7 | 50.1 | 134.6 | 209.6
673 | 511 | 466.6 | 186.64 | 218.1714 | 345.3 | 338.3 | 325.7 | 349.1 | 473.9 | 45.7 | 20.3 | 83.3 | 4.7 | 252.5 | 6.3 | 802.7 | 690.1 | 770.9 | 669.4 | 835.3 | 894.4 | 829.2 | 868.3 | 826.8 | 792 | 715.2 | 797 | 726.1 | 67 | 164.5 | 213 | 50.2 | 134.8 | 210
674 | 512 | 467.6 | 187.04 | 218.639 | 345.8 | 339.8 | 325.3 | 349.4 | 476.3 | 45.8 | 20.3 | 83.5 | 4.8 | 254.5 | 5.9 | 802.8 | 684.7 | 767.7 | 669.8 | 835.2 | 894.8 | 829.4 | 869.3 | 827.1 | 790.4 | 714.9 | 796.9 | 724.8 | 67.2 | 164.9 | 213.3 | 50.4 | 135 | 210.1
675 | 513 | 467.8 | 187.12 | 218.7325 | 344.9 | 340.3 | 325.3 | 348.9 | 471 | 45.9 | 20.3 | 83.6 | 4.5 | 256.5 | 5.9 | 803.2 | 683.8 | 765 | 670.3 | 837.8 | 895.2 | 829.9 | 870 | 828.8 | 788.8 | 714.9 | 797 | 723.8 | 67.4 | 165.3 | 213.6 | 50.6 | 135.3 | 210.4
676 | 514 | 467.9 | 187.16 | 218.7793 | 344.8 | 340.9 | 326.2 | 348.7 | 462.4 | 45.9 | 20.3 | 83.7 | 4.9 | 224.8 | 5.6 | 803.3 | 683.7 | 764.2 | 670.8 | 839.6 | 895.7 | 830.6 | 870.4 | 830.7 | 789.1 | 714.7 | 797 | 723 | 67.6 | 165.7 | 213.9 | 50.7 | 135.6 | 210.8
677 | 515 | 467.1 | 186.84 | 218.4052 | 346.6 | 341.2 | 327.3 | 348.6 | 456.1 | 45.8 | 20.3 | 83.8 | 4.4 | 226.1 | 5.6 | 803.5 | 681.1 | 765.1 | 671.2 | 841.6 | 895.9 | 831.5 | 871.7 | 833.6 | 788 | 714.8 | 797.1 | 722.6 | 67.8 | 166.1 | 214.2 | 50.9 | 135.9 | 211
678 | 516 | 467.5 | 187 | 218.5922 | 347.5 | 341.3 | 327.6 | 348 | 449.6 | 45.8 | 20.3 | 83.9 | 4.2 | 237.6 | 5.4 | 803.6 | 680.8 | 767.7 | 671.6 | 843.2 | 896 | 831.9 | 875.1 | 834.2 | 788.8 | 714.8 | 797.3 | 723.2 | 68 | 166.5 | 214.4 | 51.1 | 136.2 | 211.4
679 | 517 | 467.7 | 187.08 | 218.6857 | 348.2 | 341.3 | 326.5 | 347 | 445.8 | 45.8 | 20.3 | 84 | 4.2 | 244.8 | 5.1 | 803.6 | 680 | 773.4 | 672 | 844.1 | 895.8 | 833 | 877.4 | 834.5 | 790 | 715 | 797.4 | 722.4 | 68.2 | 166.9 | 215 | 51.2 | 136.5 | 211.9
680 | 518 | 467.6 | 187.04 | 218.639 | 348 | 340.9 | 326.2 | 345.9 | 446.9 | 45.9 | 20.3 | 84.1 | 4 | 247.3 | 5.3 | 803.5 | 679.9 | 777.1 | 672.6 | 841.1 | 895.8 | 833.2 | 877.6 | 832.1 | 789.9 | 715.6 | 797.7 | 720.8 | 68.4 | 167.3 | 215.8 | 51.4 | 136.8 | 212.1
681 | 519 | 467 | 186.8 | 218.3584 | 348.2 | 341.4 | 327.6 | 345.4 | 460.6 | 46 | 20.3 | 84.3 | 4.3 | 250.9 | 5.3 | 803.5 | 680.9 | 778.3 | 673.5 | 836.8 | 895.7 | 831.6 | 874.8 | 829.3 | 789 | 716.5 | 798 | 717.7 | 68.6 | 167.7 | 217.1 | 51.5 | 137 | 212.7
682 | 520 | 466.9 | 186.76 | 218.3117 | 348 | 344 | 329.3 | 346.3 | 465.7 | 46.1 | 20.2 | 84.4 | 4.6 | 234.7 | 5.8 | 803.5 | 684.1 | 776.5 | 674.9 | 832.3 | 895.9 | 828.9 | 873.2 | 824.6 | 786 | 718.4 | 798.6 | 714.1 | 68.8 | 168.1 | 218 | 51.7 | 137.3 | 213.3
683 | 521 | 468.3 | 187.32 | 218.9663 | 348.1 | 345.6 | 330.6 | 347.6 | 474.4 | 46.1 | 20.2 | 84.3 | 4.4 | 228.5 | 6.5 | 803.5 | 686.2 | 777.1 | 676.3 | 833.3 | 895.6 | 830.3 | 874.3 | 825.3 | 786.3 | 720.2 | 798.6 | 712 | 69 | 168.5 | 218.1 | 51.9 | 137.6 | 213.7
684 | 522 | 469.3 | 187.72 | 219.4339 | 348.9 | 346 | 331.2 | 348.7 | 481.3 | 46.1 | 20.2 | 84.3 | 4.6 | 249.5 | 7.7 | 803.5 | 687.6 | 780.4 | 677.3 | 834.7 | 894.7 | 832.1 | 876.5 | 827.3 | 788.3 | 721 | 798.3 | 711.2 | 69.2 | 169 | 218.2 | 52 | 137.8 | 214.2
685 | 523 | 467.8 | 187.12 | 218.7325 | 349.5 | 346.1 | 331.3 | 349.6 | 476 | 46.1 | 20.2 | 84.3 | 4.8 | 245.9 | 7.9 | 803.5 | 689.8 | 780.9 | 678 | 838.5 | 894 | 833.8 | 877.4 | 829.9 | 790.5 | 721.2 | 797.9 | 712.7 | 69.4 | 169.4 | 218.5 | 52.2 | 138.1 | 214.7
686 | 524 | 467.3 | 186.92 | 218.4987 | 350.1 | 345.4 | 330.4 | 350.2 | 470.8 | 46.2 | 20.2 | 84.4 | 4.6 | 253.8 | 7.8 | 803.6 | 689.6 | 781.9 | 678.4 | 841 | 893.4 | 836 | 877.6 | 832.5 | 792.3 | 720.8 | 797.4 | 714.5 | 69.6 | 169.8 | 218.5 | 52.3 | 138.4 | 214.9
687 | 525 | 468.6 | 187.44 | 219.1066 | 350.9 | 345.6 | 329.5 | 350.5 | 460.5 | 46.3 | 20.2 | 84.5 | 4.3 | 258.7 | 7.5 | 803.5 | 689.2 | 781.9 | 678.6 | 842.3 | 893.3 | 837.4 | 878.2 | 834.5 | 793.1 | 720.2 | 797.1 | 716.3 | 69.8 | 170.2 | 218.9 | 52.5 | 138.6 | 215.1
688 | 526 | 469 | 187.6 | 219.2936 | 352.3 | 345.2 | 329.5 | 350.2 | 452.6 | 46.3 | 20.2 | 84.5 | 4.3 | 261.8 | 7.9 | 803.5 | 692.4 | 779.6 | 679.1 | 841.8 | 893.3 | 838.4 | 879.2 | 833.2 | 793.6 | 719.7 | 797.1 | 717.6 | 70.1 | 170.6 | 219.7 | 52.7 | 138.9 | 215.5
689 | 527 | 468.5 | 187.4 | 219.0598 | 353.7 | 344.9 | 329.1 | 349.4 | 446.6 | 46.4 | 20.2 | 84.5 | 4.6 | 252.2 | 7.6 | 803.7 | 694.2 | 775.8 | 679.8 | 842 | 893.3 | 838.3 | 876.1 | 832.1 | 793.6 | 719.7 | 797.4 | 719.3 | 70.3 | 171 | 220 | 52.8 | 139.2 | 216.1
690 | 528 | 469.2 | 187.68 | 219.3871 | 354.4 | 344.2 | 328.4 | 348.8 | 442.7 | 46.4 | 20.2 | 84.6 | 4.9 | 245.1 | 7.2 | 803.8 | 693.5 | 770.6 | 680.5 | 844.6 | 893.1 | 836.9 | 874.1 | 831.1 | 793.9 | 719.9 | 797.6 | 720 | 70.5 | 171.4 | 220.4 | 53 | 139.5 | 216.4
691 | 529 | 467.4 | 186.96 | 218.5455 | 355 | 344.4 | 328.2 | 348.6 | 434.7 | 46.5 | 20.2 | 84.6 | 4.6 | 252.6 | 6.5 | 803.9 | 691.5 | 769.7 | 680.8 | 846.8 | 893 | 836.5 | 872.5 | 832 | 793.9 | 719.7 | 797.7 | 719.9 | 70.7 | 171.8 | 220.4 | 53.1 | 139.8 | 216.5
692 | 530 | 468.5 | 187.4 | 219.0598 | 355.2 | 344.4 | 327.7 | 347.7 | 430 | 46.7 | 20.2 | 84.6 | 4.1 | 249.7 | 5.9 | 804 | 688.3 | 771.7 | 680.9 | 849.6 | 892.7 | 835.8 | 876.5 | 831.5 | 793.7 | 719.5 | 798 | 719.4 | 70.9 | 172.2 | 220.5 | 53.3 | 140.1 | 216.6
693 | 531 | 468.3 | 187.32 | 218.9663 | 354.5 | 343.7 | 327.9 | 346.2 | 427.2 | 46.8 | 20.2 | 84.6 | 4.3 | 243.6 | 6.1 | 804.1 | 687.7 | 774.4 | 681.2 | 846.7 | 892.7 | 835.9 | 879.2 | 830.7 | 793.6 | 719.2 | 798.6 | 720 | 71.1 | 172.6 | 221.1 | 53.4 | 140.3 | 217.1
694 | 532 | 468.8 | 187.52 | 219.2001 | 354.2 | 342.8 | 328.8 | 345.1 | 429.2 | 46.8 | 20.2 | 84.6 | 4 | 242.7 | 7.4 | 804.2 | 687.5 | 777 | 681.7 | 842.7 | 892.8 | 833.8 | 879.4 | 827.1 | 792.8 | 719.6 | 799.3 | 717.7 | 71.3 | 172.9 | 221.9 | 53.6 | 140.6 | 217.8
695 | 533 | 468.1 | 187.24 | 218.8728 | 354.5 | 342.3 | 329.6 | 345.6 | 432.8 | 46.7 | 20.2 | 84.7 | 3.9 | 238.5 | 7.9 | 804.3 | 687.1 | 776.3 | 682.7 | 837.2 | 893 | 830.8 | 878.4 | 823.3 | 790.2 | 720.7 | 800 | 713.9 | 71.6 | 173.3 | 222.6 | 53.8 | 140.9 | 218.3
696 | 534 | 468.2 | 187.28 | 218.9195 | 354.1 | 344.1 | 329.7 | 346.5 | 438.2 | 46.7 | 20.2 | 84.7 | 4.3 | 242 | 8.3 | 804.5 | 688.3 | 777.6 | 683.7 | 838.7 | 892.8 | 832.4 | 880 | 826 | 791.5 | 721.4 | 800.2 | 712.8 | 71.8 | 173.7 | 222.9 | 53.9 | 141.2 | 218.6
697 | 535 | 468.3 | 187.32 | 218.9663 | 353.8 | 344.6 | 329.9 | 347.6 | 438.6 | 46.8 | 20.2 | 84.7 | 4.4 | 247.4 | 7.3 | 804.6 | 689.8 | 778.4 | 684.3 | 837.4 | 892.6 | 832.6 | 880.4 | 827.4 | 793.4 | 721.8 | 800.5 | 713.4 | 72 | 174 | 223 | 54.1 | 141.4 | 219.3
698 | 536 | 467.7 | 187.08 | 218.6857 | 353.7 | 344.2 | 330.8 | 347.9 | 438 | 47 | 20.2 | 84.8 | 4.3 | 263.4 | 6.1 | 804.6 | 689.1 | 778.4 | 684.7 | 837.1 | 891.9 | 832.5 | 879.6 | 827 | 793.1 | 722.2 | 800.7 | 713.7 | 72.2 | 174.4 | 223.2 | 54.2 | 141.7 | 219.6
699 | 537 | 468.1 | 187.24 | 218.8728 | 352.9 | 343.4 | 330.9 | 348 | 439.2 | 47.1 | 20.2 | 84.7 | 4.5 | 252.4 | 5.9 | 804.7 | 688 | 774.6 | 685.2 | 841 | 891.4 | 833.5 | 876.1 | 828.3 | 794.1 | 722.1 | 800.6 | 713.2 | 72.4 | 174.7 | 223.5 | 54.4 | 142 | 219.9
700 | 538 | 467.4 | 186.96 | 218.5455 | 350.3 | 343.4 | 330 | 347.9 | 433 | 47.1 | 20.2 | 84.7 | 4.6 | 253.2 | 6.7 | 804.6 | 688 | 768.9 | 685.4 | 843.6 | 891.4 | 834.1 | 874.7 | 828.2 | 794 | 721.7 | 801.5 | 713.8 | 72.7 | 175.1 | 223.7 | 54.5 | 142.2 | 220.3
701 | 539 | 466.6 | 186.64 | 218.1714 | 348.9 | 343.5 | 328.8 | 348.2 | 425.2 | 47.2 | 20.2 | 84.7 | 4.3 | 258 | 7 | 804.8 | 689.7 | 766.4 | 685.8 | 844.6 | 891.4 | 833.9 | 872 | 827.4 | 794.2 | 721.8 | 801.6 | 714.9 | 72.9 | 175.4 | 224.1 | 54.7 | 142.5 | 220.4
702 | 540 | 468.5 | 187.4 | 219.0598 | 348.6 | 342.6 | 328.4 | 347.8 | 420.4 | 47.2 | 20.2 | 84.7 | 3.7 | 251.9 | 7 | 804.9 | 692.1 | 764.9 | 686.6 | 847.2 | 891 | 833.8 | 870.8 | 826.9 | 795.3 | 721.9 | 801.4 | 715.3 | 73.1 | 175.7 | 224.4 | 54.9 | 142.8 | 220.8
703 | 541 | 469 | 187.6 | 219.2936 | 349.6 | 341.5 | 328.7 | 347.2 | 416.3 | 47.2 | 20.2 | 84.6 | 3.6 | 254.2 | 6.8 | 805 | 692.3 | 765.4 | 686.9 | 844.4 | 891.6 | 834.2 | 870.9 | 826.1 | 795.7 | 721.6 | 801.9 | 716.3 | 73.3 | 176.1 | 224.7 | 55 | 143 | 221.2
704 | 542 | 468.3 | 187.32 | 218.9663 | 350.2 | 341.7 | 329.7 | 346.5 | 413.9 | 47.1 | 20.2 | 84.4 | 3.8 | 256 | 6.5 | 805.1 | 692.1 | 767.6 | 687.1 | 841.3 | 891.8 | 833 | 873 | 823.7 | 795.4 | 721.8 | 802.7 | 717.2 | 73.5 | 176.4 | 225.3 | 55.2 | 143.3 | 221.5
705 | 543 | 469 | 187.6 | 219.2936 | 351.3 | 341.1 | 330 | 346.3 | 414.3 | 47.2 | 20.2 | 84.4 | 4.1 | 254.8 | 6.3 | 805.3 | 693.6 | 769 | 687.6 | 841.1 | 892 | 833.1 | 873.1 | 824.3 | 795.9 | 722.2 | 803 | 718.8 | 73.8 | 176.8 | 225.5 | 55.3 | 143.7 | 222.1
706 | 544 | 468.8 | 187.52 | 219.2001 | 351.9 | 340.1 | 330.3 | 346.2 | 413.6 | 47.3 | 20.2 | 84.4 | 4.1 | 254.7 | 6.4 | 805.4 | 695.9 | 769.9 | 688.3 | 842.8 | 892.1 | 833 | 874.1 | 824.7 | 796.9 | 722.2 | 803.4 | 719.6 | 74 | 177.1 | 225.6 | 55.5 | 144 | 222.7
707 | 545 | 466.8 | 186.72 | 218.2649 | 351.5 | 339.1 | 329.8 | 346 | 413.5 | 47.4 | 20.2 | 84.5 | 4.4 | 253.2 | 6.3 | 805.5 | 696.3 | 770.8 | 688.8 | 841.7 | 892.2 | 833.3 | 873.6 | 824.2 | 797.5 | 722.2 | 804 | 719.8 | 74.2 | 177.5 | 226 | 55.6 | 144.3 | 223
708 | 546 | 467.3 | 186.92 | 218.4987 | 352.2 | 337.2 | 329.5 | 345.7 | 412.6 | 47.3 | 20.2 | 84.6 | 4.4 | 249.5 | 6 | 805.5 | 695.1 | 769.9 | 689.1 | 840.1 | 892.5 | 832.8 | 872.8 | 823.3 | 797.4 | 722.5 | 805 | 721.1 | 74.4 | 177.8 | 226.5 | 55.8 | 144.6 | 223.1
709 | 547 | 467 | 186.8 | 218.3584 | 353.7 | 335.1 | 329.3 | 345.3 | 412.7 | 47.2 | 20.1 | 84.8 | 4.6 | 251.8 | 5.7 | 805.6 | 693.4 | 773 | 689.7 | 841.3 | 892.5 | 832 | 873.8 | 823.5 | 798 | 722.9 | 805.9 | 721.2 | 74.6 | 178.1 | 226.7 | 56 | 144.9 | 223.5
710 | 548 | 467.1 | 186.84 | 218.4052 | 355.5 | 333.8 | 329.5 | 344.4 | 411.5 | 47.2 | 20.1 | 84.9 | 4 | 254.7 | 5.7 | 805.7 | 693.7 | 774.6 | 690.3 | 842.8 | 892.4 | 832.1 | 873.5 | 824.7 | 799.5 | 723.2 | 806.3 | 721.6 | 74.9 | 178.4 | 226.9 | 56.1 | 145.2 | 224
711 | 549 | 467.8 | 187.12 | 218.7325 | 356.3 | 332.7 | 329.5 | 343.8 | 410.6 | 47.3 | 20.1 | 85 | 3.7 | 253.6 | 5.7 | 805.7 | 695.2 | 776 | 690.6 | 843.7 | 892.2 | 832.1 | 874.8 | 825.5 | 800.3 | 722.9 | 806.9 | 722.8 | 75.1 | 178.8 | 227.3 | 56.3 | 145.4 | 224.4
712 | 550 | 468.1 | 187.24 | 218.8728 | 357.1 | 332.4 | 329.1 | 343.4 | 410.3 | 47.3 | 20.1 | 85.1 | 4.1 | 260.2 | 5.8 | 805.7 | 695.1 | 773.8 | 691 | 845 | 891.7 | 832.2 | 875.2 | 826.1 | 800 | 723 | 807.6 | 723 | 75.3 | 179.1 | 227.5 | 56.4 | 145.7 | 224.7
713 | 551 | 467.1 | 186.84 | 218.4052 | 358 | 332.3 | 329.1 | 343.4 | 410.5 | 47.4 | 20.1 | 85.2 | 4 | 265.6 | 6.3 | 805.6 | 694.2 | 771.3 | 691.6 | 847.5 | 891.5 | 831.3 | 877.2 | 825.4 | 800 | 723.4 | 807.9 | 722.3 | 75.6 | 179.4 | 228.1 | 56.6 | 146 | 225
714 | 552 | 467.6 | 187.04 | 218.639 | 357.9 | 331.6 | 329.5 | 342.9 | 411.8 | 47.4 | 20.1 | 85.3 | 4 | 243.2 | 7 | 805.5 | 688.9 | 773.2 | 691.8 | 849 | 891.3 | 832.3 | 875.7 | 825 | 800.6 | 723.5 | 808 | 720.6 | 75.8 | 179.8 | 228.6 | 56.8 | 146.2 | 225
715 | 553 | 465.3 | 186.12 | 217.5636 | 357.6 | 330.5 | 330.2 | 342.5 | 409.6 | 47.4 | 20.1 | 85.3 | 4 | 250.1 | 6.9 | 805.4 | 687.8 | 772.4 | 691.9 | 849.3 | 891.4 | 832.9 | 875 | 824.5 | 801.5 | 722.7 | 808.2 | 720.4 | 76 | 180.1 | 228.6 | 56.9 | 146.5 | 225.2
716 | 554 | 467.9 | 187.16 | 218.7793 | 357.7 | 330.9 | 330.5 | 341.9 | 409 | 47.4 | 20.1 | 85.4 | 4 | 251 | 6.6 | 805.4 | 688.1 | 768.4 | 692.3 | 850.2 | 891.6 | 832.9 | 874 | 824.3 | 801 | 722.6 | 808.7 | 720.1 | 76.2 | 180.4 | 228.9 | 57.1 | 146.8 | 225.8
717 | 555 | 467 | 186.8 | 218.3584 | 358.3 | 332.1 | 330.7 | 341.5 | 410.4 | 47.4 | 20.1 | 85.4 | 4 | 250.4 | 6.3 | 805.5 | 688.8 | 764.4 | 692.9 | 849.7 | 892 | 831.8 | 872.3 | 822.7 | 801.1 | 722.6 | 808.8 | 718.9 | 76.5 | 180.8 | 229.1 | 57.2 | 147.1 | 226.2
718 | 556 | 466.6 | 186.64 | 218.1714 | 358.9 | 333.6 | 331.9 | 341.2 | 407.3 | 47.5 | 20.1 | 85.4 | 3.9 | 248.4 | 5.9 | 805.6 | 688.2 | 764.3 | 693.2 | 848.6 | 892.5 | 830.9 | 874.6 | 821.1 | 800.8 | 722.5 | 809.3 | 718.2 | 76.7 | 181.1 | 229.4 | 57.4 | 147.5 | 226.5
719 | 557 | 467.5 | 187 | 218.5922 | 359.9 | 335 | 333 | 341 | 405.4 | 47.6 | 20.1 | 85.3 | 4.2 | 245.6 | 5.5 | 805.6 | 688.4 | 768.2 | 693.7 | 849 | 892.5 | 831.7 | 876.1 | 822.2 | 801.8 | 722.9 | 809.9 | 718.7 | 76.9 | 181.3 | 229.6 | 57.6 | 147.8 | 226.8
720 | 558 | 466.1 | 186.44 | 217.9376 | 361 | 335.7 | 333.6 | 340.9 | 403.2 | 47.6 | 20.1 | 85.4 | 4.1 | 254.9 | 5.3 | 805.6 | 687.5 | 771.9 | 694 | 848.8 | 892.3 | 832.1 | 876.8 | 823.3 | 801.9 | 723.5 | 810.5 | 718.1 | 77.2 | 181.6 | 230 | 57.7 | 148.1 | 226.9
721 | 559 | 467.7 | 187.08 | 218.6857 | 362 | 336.2 | 334 | 340.2 | 404.5 | 47.5 | 20.1 | 85.6 | 4 | 245.7 | 4.9 | 805.5 | 686.2 | 772.6 | 694.3 | 849.6 | 892.4 | 832.2 | 879.1 | 824 | 801.4 | 723.8 | 810.2 | 718 | 77.4 | 181.8 | 230.5 | 57.9 | 148.4 | 227
722 | 560 | 467.9 | 187.16 | 218.7793 | 362.4 | 336.3 | 333.6 | 339.7 | 405.4 | 47.5 | 20.1 | 85.7 | 4.2 | 222.4 | 4.9 | 805.5 | 686.4 | 771.2 | 694.8 | 848.9 | 892.3 | 832.2 | 877.8 | 823.9 | 800.7 | 723.7 | 807 | 718.3 | 77.6 | 182.1 | 230.7 | 58 | 148.6 | 227.5
723 | 561 | 466.5 | 186.6 | 218.1246 | 362.9 | 336.1 | 333.1 | 339.6 | 406.8 | 47.5 | 20.1 | 85.8 | 4.1 | 224.4 | 4.8 | 805.5 | 686.3 | 770.4 | 695.1 | 849.9 | 892.3 | 833.4 | 877.6 | 824.7 | 801.4 | 723.6 | 806.5 | 718.4 | 77.9 | 182.4 | 231 | 58.2 | 148.9 | 228.1
724 | 562 | 464.9 | 185.96 | 217.3765 | 363 | 335.5 | 332.8 | 339.3 | 411.3 | 47.5 | 20.1 | 85.9 | 4.6 | 230.1 | 4.6 | 805.4 | 684.6 | 773.7 | 695.5 | 849 | 892 | 835 | 879.6 | 825.3 | 802.1 | 723.9 | 806.6 | 716.6 | 78.1 | 182.7 | 231.4 | 58.4 | 149.1 | 228.2
725 | 563 | 463.6 | 185.44 | 216.7687 | 363 | 334 | 333.3 | 338.5 | 417.6 | 47.5 | 20.1 | 85.9 | 4.7 | 235.9 | 4.3 | 805.4 | 682.5 | 776.5 | 696.2 | 850.5 | 891.6 | 837.1 | 879.8 | 826.8 | 802.8 | 724.6 | 806.4 | 715.3 | 78.3 | 182.9 | 231.8 | 58.5 | 149.4 | 228.4
726 | 564 | 465.8 | 186.32 | 217.7973 | 362.6 | 332.6 | 333.6 | 337.9 | 420.4 | 47.4 | 20.1 | 86 | 5 | 239.5 | 3.9 | 805.4 | 683.3 | 777.6 | 696.5 | 847.9 | 891.3 | 837.3 | 879.6 | 826.5 | 803.7 | 724.6 | 805.2 | 715.9 | 78.6 | 183.1 | 232.1 | 58.7 | 149.6 | 228.6
727 | 565 | 466.1 | 186.44 | 217.9376 | 363.8 | 331.3 | 333.9 | 338 | 421.3 | 47.5 | 20.1 | 86 | 4.6 | 238.8 | 3.7 | 805.4 | 686.5 | 772.4 | 697 | 842.2 | 891.2 | 834.1 | 876.1 | 820.7 | 803.2 | 724.6 | 805.2 | 716.9 | 78.8 | 183.4 | 232.4 | 58.8 | 149.9 | 229.1
728 | 566 | 466.6 | 186.64 | 218.1714 | 366.7 | 330.5 | 333.8 | 338.5 | 423.7 | 47.5 | 20.1 | 86 | 4.5 | 234.3 | 3.9 | 805.6 | 687.1 | 769.4 | 697.7 | 836.6 | 891 | 831.1 | 874 | 816.3 | 801.7 | 725.1 | 803.7 | 718.3 | 79 | 183.7 | 232.6 | 59 | 150.3 | 229.6
729 | 567 | 467.7 | 187.08 | 218.6857 | 367.1 | 330.5 | 334.5 | 339.3 | 425 | 47.5 | 20.1 | 86.1 | 4.5 | 234.7 | 4 | 805.9 | 688 | 767 | 698.5 | 830.3 | 890.8 | 828.9 | 872.6 | 812.7 | 801.4 | 725.9 | 803.9 | 719.3 | 79.3 | 183.9 | 233 | 59.2 | 150.6 | 230
730 | 568 | 468.2 | 187.28 | 218.9195 | 367 | 329.9 | 335.5 | 340.4 | 426 | 47.5 | 20.1 | 86.1 | 4.3 | 238.9 | 4.1 | 806.2 | 689 | 765.1 | 699.5 | 827.9 | 890.6 | 827.7 | 872.2 | 809.1 | 800.3 | 727 | 803.9 | 719.7 | 79.5 | 184.2 | 233.3 | 59.3 | 151 | 230.3
731 | 569 | 467.6 | 187.04 | 218.639 | 368.5 | 329.7 | 335.6 | 341.5 | 427.1 | 47.6 | 20.1 | 86.1 | 4.4 | 246.8 | 4.5 | 806.4 | 689.3 | 765.7 | 700.5 | 827.4 | 890.3 | 828.2 | 873.8 | 810.2 | 800.6 | 728.2 | 805 | 720.7 | 79.8 | 184.5 | 233.5 | 59.5 | 151.3 | 230.6
732 | 570 | 467.9 | 187.16 | 218.7793 | 369.2 | 329.7 | 335.1 | 341.6 | 424.5 | 47.6 | 20.1 | 86.1 | 4.6 | 235.7 | 4.7 | 806.4 | 689 | 767.4 | 700.8 | 825.1 | 889.6 | 828.7 | 875.8 | 810.7 | 801.6 | 728.6 | 806 | 721.4 | 80 | 184.9 | 233.7 | 59.7 | 151.6 | 230.8
733 | 571 | 467.2 | 186.88 | 218.452 | 369.3 | 328.9 | 335.5 | 340.7 | 423.8 | 47.7 | 20 | 86.1 | 5.5 | 231.5 | 4.9 | 806.5 | 689.6 | 770.7 | 701.1 | 826.9 | 888.9 | 829.9 | 878.4 | 814 | 802.9 | 728.8 | 806.3 | 721.7 | 80.2 | 185.2 | 234.1 | 59.8 | 151.9 | 231.4
734 | 572 | 465.5 | 186.2 | 217.6571 | 369 | 328 | 335.8 | 340.9 | 424.9 | 47.7 | 20 | 86.3 | 5.1 | 237.3 | 5 | 806.5 | 690.6 | 773 | 701.6 | 826.8 | 888.2 | 830.9 | 879.1 | 815.2 | 804.1 | 728.8 | 807.1 | 721.8 | 80.5 | 185.5 | 234.5 | 60 | 152.1 | 231.9
735 | 573 | 466.5 | 186.6 | 218.1246 | 368.7 | 327.9 | 335.8 | 341.8 | 423.1 | 47.7 | 20 | 86.3 | 4.6 | 245.1 | 5 | 806.5 | 691.9 | 774.7 | 701.8 | 828.1 | 887.5 | 831 | 879.7 | 816.2 | 805.4 | 728.6 | 807.5 | 722.1 | 80.7 | 185.8 | 234.8 | 60.2 | 152.4 | 232.4
736 | 574 | 466.6 | 186.64 | 218.1714 | 371.2 | 327.6 | 335.9 | 342.6 | 423.6 | 47.8 | 20 | 86.3 | 4.3 | 232.5 | 4.8 | 806.4 | 690.5 | 775.2 | 702.1 | 828.4 | 887.3 | 831.3 | 879 | 816.4 | 805.1 | 728.8 | 805.5 | 721.8 | 80.9 | 186 | 235.2 | 60.3 | 152.7 | 232.8
737 | 575 | 467 | 186.8 | 218.3584 | 372.7 | 327.5 | 335.9 | 343.5 | 426.5 | 48 | 20 | 86.2 | 4.7 | 217.8 | 4.2 | 806.2 | 686.5 | 774.8 | 702.4 | 825.3 | 887.4 | 828.8 | 877.9 | 813 | 802.4 | 729.6 | 803.8 | 717.4 | 81.2 | 186.3 | 236.2 | 60.5 | 153 | 233.1
738 | 576 | 467.1 | 186.84 | 218.4052 | 374.3 | 327.9 | 336.1 | 344.4 | 431.4 | 48.1 | 20 | 86.2 | 4.6 | 230.9 | 3.9 | 806.3 | 683.2 | 775.4 | 703 | 823.8 | 887.1 | 827.5 | 878.6 | 812.3 | 801.8 | 730.6 | 804.9 | 714.8 | 81.4 | 186.6 | 236.6 | 60.7 | 153.4 | 233.2
739 | 577 | 467.3 | 186.92 | 218.4987 | 374.8 | 328.3 | 336.7 | 345.6 | 436.9 | 48.1 | 20 | 86.1 | 4.6 | 241.3 | 3.9 | 806.3 | 681.3 | 777.7 | 703.5 | 823.8 | 886.4 | 828.9 | 880.4 | 813.3 | 802.8 | 731.1 | 805.9 | 713.4 | 81.7 | 187 | 237 | 60.8 | 153.7 | 233.4
740 | 578 | 467.8 | 187.12 | 218.7325 | 374.8 | 329.4 | 337 | 346.3 | 438.5 | 48.2 | 20 | 86.1 | 4.3 | 250.5 | 4 | 806.2 | 680.3 | 776.8 | 703.7 | 824.8 | 885.7 | 829.5 | 882.2 | 813.2 | 802.3 | 731 | 806 | 713.7 | 81.9 | 187.3 | 237.4 | 61 | 154.1 | 233.9
741 | 579 | 467.4 | 186.96 | 218.5455 | 375.4 | 330.4 | 337.7 | 346.7 | 436.8 | 48.3 | 20 | 86.2 | 4.2 | 246.8 | 4.6 | 806.1 | 679 | 776.6 | 704 | 825.5 | 884.8 | 830.7 | 881.5 | 812.9 | 802.6 | 730.6 | 804.6 | 714 | 82.1 | 187.6 | 237.5 | 61.2 | 154.4 | 234.2
742 | 580 | 467.2 | 186.88 | 218.452 | 375.8 | 330.8 | 338.1 | 346.9 | 435.5 | 48.4 | 20 | 86.2 | 4.4 | 242.5 | 5.2 | 806 | 675.8 | 772.5 | 704.3 | 821.8 | 884.4 | 828 | 877.9 | 808.7 | 800.7 | 730.3 | 803 | 714.8 | 82.4 | 188 | 237.7 | 61.4 | 154.7 | 234.4
743 | 581 | 467.8 | 187.12 | 218.7325 | 377.4 | 331.5 | 338.1 | 347.2 | 433.7 | 48.4 | 20 | 86.3 | 4.4 | 247.8 | 6 | 806 | 675.5 | 767.1 | 704.7 | 816.1 | 884.1 | 823.4 | 874.5 | 801.5 | 797.7 | 730.8 | 802.4 | 715.3 | 82.6 | 188.3 | 238.1 | 61.6 | 155 | 234.8
744 | 582 | 467.9 | 187.16 | 218.7793 | 380.6 | 332.1 | 338.3 | 347.8 | 433.6 | 48.4 | 20 | 86.3 | 4.1 | 260.5 | 6.5 | 805.8 | 674.1 | 762.8 | 705.2 | 811.8 | 883.5 | 819.5 | 871.6 | 797.1 | 796.1 | 731.1 | 803.1 | 716.7 | 82.9 | 188.7 | 238.5 | 61.7 | 155.3 | 235.1
745 | 583 | 467.5 | 187 | 218.5922 | 382.8 | 332.1 | 338.9 | 348.7 | 433.5 | 48.4 | 20 | 86.3 | 4 | 253.2 | 6.5 | 805.7 | 672.1 | 762.6 | 705.3 | 810.4 | 882.9 | 819.2 | 872.7 | 797.2 | 794 | 731.5 | 803.5 | 717.1 | 83.1 | 189.1 | 238.9 | 61.9 | 155.7 | 235.3
746 | 584 | 467.9 | 187.16 | 218.7793 | 383.8 | 331.5 | 339.1 | 348.7 | 432.4 | 48.5 | 20 | 86.5 | 4.5 | 243.6 | 6.5 | 805.6 | 669 | 761.2 | 705.5 | 807.8 | 882.5 | 816.3 | 872.9 | 794 | 791.8 | 732 | 803.3 | 715.1 | 83.4 | 189.4 | 239.1 | 62.1 | 156 | 235.6
747 | 585 | 468.1 | 187.24 | 218.8728 | 383.3 | 331.1 | 339.6 | 348.8 | 433.1 | 48.6 | 20 | 86.7 | 4.8 | 258.9 | 6.7 | 805.5 | 666.1 | 760.2 | 706 | 802.9 | 882.1 | 812.4 | 873 | 789.6 | 788.5 | 733.2 | 803.3 | 713 | 83.6 | 189.8 | 239.8 | 62.3 | 156.3 | 236.2
748 | 586 | 468 | 187.2 | 218.826 | 384.1 | 330.9 | 340.1 | 349.8 | 434.1 | 48.6 | 20 | 86.9 | 4.7 | 251.8 | 6.9 | 805.4 | 665.8 | 763.7 | 706.5 | 802.9 | 881.3 | 813.9 | 874 | 790.7 | 788.4 | 734.1 | 803.6 | 713.1 | 83.8 | 190.2 | 240.1 | 62.4 | 156.6 | 236.5
749 | 587 | 467.8 | 187.12 | 218.7325 | 385.5 | 330.8 | 341 | 350.7 | 434.2 | 48.7 | 20 | 87 | 4.5 | 234.8 | 6.9 | 805.3 | 668.9 | 765.2 | 706.7 | 802 | 880.5 | 816 | 873.6 | 793 | 789.6 | 734 | 803.7 | 714.8 | 84.1 | 190.5 | 240.3 | 62.6 | 156.8 | 236.8
750 | 588 | 468 | 187.2 | 218.826 | 384.8 | 330.9 | 340.9 | 351.1 | 431.8 | 48.7 | 20 | 87.1 | 4.1 | 237 | 6.8 | 805.1 | 672.6 | 768.2 | 707.1 | 803.5 | 879.6 | 818.3 | 874.8 | 796.2 | 791.1 | 733.7 | 803.2 | 715.5 | 84.3 | 190.9 | 240.8 | 62.8 | 157 | 237.5
751 | 589 | 469.1 | 187.64 | 219.3403 | 385.3 | 331 | 340.9 | 351.1 | 435 | 48.7 | 20 | 87.3 | 4.4 | 250.3 | 6.3 | 804.8 | 671.7 | 770.8 | 707.3 | 802.5 | 878.9 | 818.7 | 876.4 | 797.2 | 791.1 | 733.6 | 800.4 | 714.7 | 84.5 | 191.2 | 241.6 | 63 | 157.3 | 237.6
752 | 590 | 466.7 | 186.68 | 218.2182 | 386.7 | 331.2 | 340.8 | 351.1 | 436.4 | 48.8 | 20 | 87.3 | 4.6 | 245 | 5.6 | 804.6 | 668.1 | 768.3 | 707.5 | 800.5 | 878.6 | 815.9 | 877.2 | 793.2 | 787.9 | 734.3 | 798.6 | 713.5 | 84.8 | 191.6 | 242.2 | 63.2 | 157.6 | 237.9
753 | 591 | 466.4 | 186.56 | 218.0779 | 386.6 | 332.3 | 341.5 | 350.8 | 439.1 | 48.9 | 20 | 87.4 | 4.9 | 228 | 5.1 | 804.5 | 666.5 | 769.8 | 707.8 | 800.1 | 878.4 | 818.1 | 878.2 | 795.5 | 788.7 | 734.8 | 797.8 | 712.3 | 85 | 192 | 242.5 | 63.4 | 157.9 | 238.2
754 | 592 | 467.6 | 187.04 | 218.639 | 386.5 | 333.5 | 342.3 | 351.1 | 439.4 | 49 | 20 | 87.4 | 5.3 | 244.4 | 5.2 | 804.3 | 666.3 | 770.7 | 707.8 | 799.2 | 878.3 | 819.4 | 879.5 | 797.9 | 788.5 | 735.1 | 798.3 | 712.2 | 85.3 | 192.4 | 242.5 | 63.6 | 158.2 | 238.6
755 | 593 | 468.3 | 187.32 | 218.9663 | 385.3 | 334.5 | 341.8 | 351.4 | 436.8 | 49 | 20 | 87.5 | 5 | 238.9 | 4.7 | 804.1 | 668 | 772 | 708 | 799.9 | 877.8 | 822.1 | 881.2 | 800.6 | 789.8 | 735.1 | 798.7 | 712.6 | 85.5 | 192.8 | 242.9 | 63.8 | 158.5 | 239
756 | 594 | 468.7 | 187.48 | 219.1533 | 384.1 | 335.7 | 341.7 | 351.7 | 438 | 49.1 | 20 | 87.6 | 4.6 | 214.4 | 4.1 | 803.7 | 667.8 | 773.6 | 707.8 | 800.6 | 877.4 | 823.2 | 882.1 | 801.4 | 790.7 | 734.9 | 796.5 | 712.5 | 85.7 | 193.1 | 243.3 | 63.9 | 158.8 | 239.2
757 | 595 | 467 | 186.8 | 218.3584 | 383.8 | 336.2 | 341.8 | 352.1 | 440 | 49.2 | 20 | 87.7 | 4.7 | 204.6 | 4.5 | 803.4 | 666.9 | 774.3 | 707.7 | 801.4 | 876.6 | 824.2 | 882.3 | 802.8 | 791.1 | 734.7 | 795.9 | 712.5 | 86 | 193.5 | 243.7 | 64.1 | 159.1 | 239.4
758 | 596 | 465.4 | 186.16 | 217.6103 | 383.1 | 335.7 | 342.5 | 352.1 | 439.5 | 49.4 | 20 | 87.8 | 4.5 | 213.9 | 5.2 | 803 | 666.2 | 775.7 | 707.5 | 801.6 | 876 | 825.3 | 882.2 | 803.7 | 791.4 | 734.4 | 796 | 712.9 | 86.2 | 193.8 | 244.1 | 64.3 | 159.4 | 239.5
759 | 597 | 466.5 | 186.6 | 218.1246 | 382.9 | 336.4 | 342.3 | 352.6 | 440.1 | 49.4 | 20 | 87.9 | 4.9 | 217.9 | 5 | 802.6 | 666 | 775.5 | 707.4 | 799.1 | 875.3 | 824.6 | 881.7 | 802.4 | 790.7 | 734.6 | 794.4 | 712.7 | 86.4 | 194.1 | 244.7 | 64.5 | 159.7 | 239.8
760 | 598 | 466.9 | 186.76 | 218.3117 | 383.1 | 337 | 342.1 | 352.7 | 441.4 | 49.4 | 19.9 | 88 | 4.8 | 247.4 | 4.6 | 802.3 | 667.9 | 775.6 | 707.7 | 797.4 | 874.4 | 824.7 | 880.4 | 801.2 | 790.8 | 735.1 | 794 | 713.1 | 86.7 | 194.5 | 245.1 | 64.7 | 160 | 240.3
761 | 599 | 467.4 | 186.96 | 218.5455 | 383.5 | 337.1 | 343 | 353.2 | 440.6 | 49.2 | 19.9 | 88 | 5 | 262 | 4.7 | 802.2 | 668.8 | 771.7 | 708.1 | 795.6 | 873.8 | 823.6 | 878.7 | 798.9 | 788.9 | 735.6 | 794.3 | 715.3 | 86.9 | 194.8 | 245.5 | 64.9 | 160.4 | 240.9
762 | 600 | 466.6 | 186.64 | 218.1714 | 385.2 | 337 | 343.2 | 353.5 | 437.4 | 49.2 | 20 | 88 | 4.3 | 251.1 | 4.5 | 802.2 | 670.6 | 768.7 | 708.6 | 794.3 | 873.6 | 821.6 | 877.8 | 797 | 787.4 | 736.3 | 793.9 | 716 | 87.2 | 195.2 | 245.6 | 65.1 | 160.7 | 241.3
763 | 601 | 467.7 | 187.08 | 218.6857 | 388.5 | 336.7 | 343.2 | 353.5 | 434.4 | 49.2 | 20 | 88 | 4.5 | 231 | 4 | 802.1 | 673.6 | 766.5 | 709 | 794.7 | 873.4 | 821.5 | 876.9 | 795.8 | 788.1 | 736.6 | 794.4 | 716.6 | 87.4 | 195.5 | 246 | 65.3 | 160.9 | 241.7
764 | 602 | 468.7 | 187.48 | 219.1533 | 390.1 | 336.1 | 342.8 | 353.8 | 433.9 | 49.3 | 19.9 | 88 | 4.9 | 240.6 | 3.5 | 802 | 671.8 | 763.1 | 709.2 | 793.4 | 873.2 | 819.8 | 875.1 | 794 | 786.7 | 736.7 | 793.4 | 717.8 | 87.6 | 195.8 | 246.2 | 65.4 | 161.2 | 242
765 | 603 | 467.5 | 187 | 218.5922 | 389.5 | 336.4 | 342.6 | 353.9 | 431.4 | 49.3 | 19.9 | 88 | 4.8 | 240.8 | 3.4 | 801.9 | 673 | 761.4 | 709.3 | 792.9 | 873 | 817.9 | 873.1 | 790.3 | 786.5 | 736.8 | 793.4 | 720.3 | 87.9 | 196.1 | 246.3 | 65.6 | 161.4 | 242.3
766 | 604 | 467 | 186.8 | 218.3584 | 389.8 | 336.4 | 342.7 | 353.9 | 429.6 | 49.3 | 19.9 | 88 | 4.5 | 235.2 | 4.2 | 801.7 | 674.7 | 761.6 | 709.3 | 791.5 | 872.6 | 818.2 | 870.1 | 790.6 | 786.5 | 736.8 | 794.1 | 722.1 | 88.1 | 196.4 | 246.5 | 65.8 | 161.7 | 242.7
767 | 605 | 466.6 | 186.64 | 218.1714 | 390.4 | 336.8 | 342.6 | 353.6 | 429.6 | 49.3 | 19.9 | 88.1 | 4.9 | 234.4 | 3.9 | 801.6 | 676.3 | 763.6 | 709.3 | 789.5 | 872.1 | 816.8 | 868.8 | 789.4 | 787.5 | 736.9 | 794.4 | 723.2 | 88.3 | 196.8 | 247.2 | 66 | 162.1 | 243
768 | 606 | 467.5 | 187 | 218.5922 | 390.3 | 336.9 | 342.8 | 352.9 | 431.1 | 49.2 | 19.9 | 88.1 | 4.9 | 229.9 | 3.9 | 801.6 | 677.5 | 767 | 709.4 | 790 | 871.7 | 819.4 | 871 | 792.9 | 788.1 | 737.3 | 794.7 | 724.5 | 88.6 | 197.1 | 247.6 | 66.2 | 162.4 | 243.4
769 | 607 | 468.6 | 187.44 | 219.1066 | 389.8 | 336.9 | 343.3 | 352.8 | 433.4 | 49.2 | 19.9 | 88.2 | 5 | 237.3 | 4.7 | 801.6 | 679.3 | 770.6 | 709.7 | 793.6 | 871.1 | 822.4 | 872 | 797.9 | 789.4 | 737.7 | 794.8 | 724.8 | 88.8 | 197.4 | 247.9 | 66.4 | 162.8 | 243.6
770 | 608 | 469 | 187.6 | 219.2936 | 389.3 | 336.2 | 343.9 | 353.5 | 434.5 | 49.2 | 19.9 | 88.3 | 5.1 | 206.5 | 5.1 | 801.3 | 678.7 | 772.4 | 709.6 | 797 | 870.3 | 824 | 870.2 | 801.3 | 791 | 737.5 | 795 | 725.1 | 89 | 197.7 | 248 | 66.5 | 163.1 | 243.7
771 | 609 | 468.9 | 187.56 | 219.2468 | 388.4 | 334.8 | 343.8 | 353.7 | 433.6 | 49.3 | 19.9 | 88.4 | 4.9 | 228.6 | 5 | 800.7 | 680.1 | 772.8 | 709.3 | 800.1 | 869.6 | 824.9 | 870.3 | 804.8 | 793.1 | 736.5 | 796.2 | 726.3 | 89.3 | 198 | 248.4 | 66.7 | 163.4 | 243.9
772 | 610 | 468.5 | 187.4 | 219.0598 | 388.1 | 334.3 | 343.3 | 353.4 | 431.7 | 49.4 | 19.9 | 88.4 | 4.3 | 250.4 | 4.2 | 800.4 | 681.7 | 773.4 | 709.1 | 801.9 | 869 | 826.9 | 873 | 807.2 | 793.7 | 736.1 | 795.5 | 727.5 | 89.5 | 198.4 | 248.8 | 66.9 | 163.7 | 244.3
773 | 611 | 468.5 | 187.4 | 219.0598 | 388.8 | 334.3 | 343.1 | 353.3 | 430.5 | 49.4 | 19.9 | 88.6 | 5.2 | 205 | 4 | 800.3 | 683.7 | 772.7 | 709.1 | 802.6 | 868.5 | 828.1 | 873.8 | 807.7 | 794.4 | 736.1 | 795.7 | 728.8 | 89.8 | 198.7 | 249.1 | 67.1 | 164 | 244.7
774 | 612 | 468.7 | 187.48 | 219.1533 | 389.3 | 334.5 | 343.1 | 352.9 | 428.4 | 49.5 | 19.9 | 88.6 | 4.9 | 212.2 | 4.1 | 800.1 | 684.4 | 772.8 | 709.2 | 804.2 | 868 | 828.8 | 873.7 | 806.5 | 795.2 | 735.9 | 796.7 | 729.5 | 90 | 199 | 249.2 | 67.2 | 164.4 | 245
775 | 613 | 468.1 | 187.24 | 218.8728 | 389.6 | 333.3 | 343.1 | 352.3 | 426.5 | 49.5 | 19.9 | 88.7 | 5 | 230.6 | 4 | 800.1 | 686.2 | 772.3 | 709.3 | 804.6 | 868.1 | 830.5 | 873.6 | 805.6 | 795.5 | 736.3 | 797.1 | 730.8 | 90.2 | 199.3 | 249.6 | 67.4 | 164.8 | 245.2
776 | 614 | 466.5 | 186.6 | 218.1246 | 389.5 | 332.4 | 343 | 352 | 425.8 | 49.4 | 19.9 | 88.7 | 5.4 | 246.5 | 4.9 | 800.1 | 686.9 | 769.9 | 709.4 | 804.8 | 868.4 | 830.3 | 873.8 | 804.7 | 795.7 | 736.6 | 797.5 | 731.7 | 90.5 | 199.6 | 249.7 | 67.6 | 165.1 | 245.5
777 | 615 | 466.6 | 186.64 | 218.1714 | 390.2 | 332.4 | 343.5 | 351.3 | 423.7 | 49.6 | 19.9 | 88.6 | 5 | 210.2 | 5.5 | 800.2 | 687.6 | 770.9 | 709.5 | 803.9 | 868.5 | 830.4 | 873.6 | 803.5 | 795.8 | 736.6 | 798 | 733 | 90.7 | 200 | 250 | 67.8 | 165.5 | 245.8
778 | 616 | 465.8 | 186.32 | 217.7973 | 391.3 | 333 | 343.8 | 351 | 422.8 | 49.6 | 19.9 | 88.6 | 4.4 | 206.6 | 6.6 | 800.3 | 687 | 772.4 | 709.7 | 807 | 868.3 | 830.7 | 875.7 | 805.6 | 796.7 | 736.4 | 798.7 | 732.6 | 91 | 200.3 | 250.4 | 67.9 | 165.9 | 246.1
779 | 617 | 468.1 | 187.24 | 218.8728 | 391.7 | 334.1 | 344 | 351.1 | 424.8 | 49.6 | 19.9 | 88.6 | 4.4 | 214.6 | 8.5 | 800.2 | 683.6 | 773.3 | 709.8 | 807 | 868 | 830.9 | 876.4 | 805.9 | 796.4 | 736 | 797.9 | 730.3 | 91.2 | 200.5 | 251.1 | 68.1 | 166.2 | 246.5
780 | 618 | 467.3 | 186.92 | 218.4987 | 391.8 | 334.3 | 344 | 351.4 | 426.1 | 49.5 | 19.9 | 88.7 | 4.4 | 213.3 | 8.6 | 800.2 | 683.5 | 772.5 | 710.1 | 807.8 | 867.5 | 832.8 | 876.2 | 807.7 | 797.4 | 735.8 | 798.8 | 730.1 | 91.4 | 200.8 | 251.5 | 68.3 | 166.5 | 247.1
781 | 619 | 468.2 | 187.28 | 218.9195 | 391.4 | 334.4 | 344.3 | 351.3 | 427.6 | 49.5 | 19.9 | 88.7 | 4.4 | 203.6 | 8.2 | 800.3 | 684.8 | 773.2 | 710.2 | 811.2 | 866.9 | 834 | 877.3 | 810.9 | 798.6 | 735.1 | 800.4 | 731.6 | 91.7 | 201 | 251.8 | 68.4 | 166.8 | 247.5
782 | 620 | 467.6 | 187.04 | 218.639 | 391 | 335 | 344.4 | 351.4 | 428.6 | 49.5 | 19.9 | 88.7 | 4.8 | 212.9 | 7.9 | 800.1 | 684.7 | 772.3 | 710.1 | 810.5 | 866.7 | 834.8 | 876.3 | 809.5 | 797.6 | 735.2 | 798.9 | 731.8 | 91.9 | 201.3 | 252.1 | 68.6 | 167 | 247.7
783 | 621 | 466.4 | 186.56 | 218.0779 | 392 | 336.1 | 344.2 | 352 | 428.8 | 49.5 | 19.9 | 88.8 | 5.2 | 216.8 | 8.2 | 800.2 | 684.6 | 769.9 | 710.2 | 811.4 | 867 | 835.1 | 875.8 | 808.6 | 797.8 | 735.4 | 799.5 | 732.3 | 92.2 | 201.6 | 252.2 | 68.8 | 167.2 | 247.9
784 | 622 | 467.9 | 187.16 | 218.7793 | 394 | 337.6 | 344.2 | 352.8 | 428 | 49.4 | 19.9 | 88.9 | 5.1 | 207.2 | 8.4 | 800.2 | 683.9 | 768.8 | 710.3 | 810.7 | 867.2 | 833.3 | 873.4 | 804.9 | 797.1 | 735.5 | 799.7 | 733.8 | 92.4 | 201.9 | 252.5 | 69 | 167.5 | 248.3
785 | 623 | 466.4 | 186.56 | 218.0779 | 393.5 | 338.4 | 344.4 | 352.9 | 426.4 | 49.4 | 19.9 | 89 | 4.7 | 202.4 | 8.1 | 800.3 | 683.7 | 767.1 | 710.4 | 810.8 | 867.7 | 833.5 | 870.2 | 804.3 | 797.5 | 735.7 | 800.3 | 734.4 | 92.6 | 202.2 | 252.7 | 69.1 | 167.9 | 248.7
786 | 624 | 466.8 | 186.72 | 218.2649 | 393.3 | 337.6 | 344.8 | 352.6 | 423.8 | 49.4 | 19.9 | 89.2 | 4.8 | 203.9 | 7.6 | 800.4 | 684.3 | 766.2 | 710.5 | 812.1 | 867.9 | 833.9 | 869.7 | 803 | 797.5 | 735.7 | 800.8 | 735 | 92.9 | 202.5 | 253 | 69.3 | 168.3 | 249.2
787 | 625 | 466.7 | 186.68 | 218.2182 | 393 | 336.5 | 345.1 | 351.7 | 422.4 | 49.6 | 19.9 | 89.3 | 5 | 220.1 | 8 | 800.5 | 682.9 | 766.8 | 710.4 | 813.8 | 868.3 | 835.2 | 869.7 | 806.2 | 798.1 | 735.4 | 801.3 | 735.8 | 93.1 | 202.7 | 253.3 | 69.5 | 168.6 | 249.4
788 | 626 | 466.7 | 186.68 | 218.2182 | 393.4 | 336.5 | 345.5 | 351.3 | 422.2 | 49.7 | 19.9 | 89.4 | 4.5 | 203.8 | 7.9 | 800.3 | 681.9 | 767.7 | 710 | 816.3 | 868.5 | 835.7 | 870.8 | 809.1 | 798.8 | 734.9 | 802 | 735.7 | 93.3 | 203 | 253.7 | 69.6 | 168.9 | 249.6
789 | 627 | 467 | 186.8 | 218.3584 | 393.5 | 337 | 345.7 | 351 | 422.2 | 49.8 | 19.9 | 89.5 | 5.1 | 210.2 | 8.2 | 800.1 | 679.2 | 766.7 | 709.6 | 819 | 868.6 | 835.2 | 872.1 | 811 | 798 | 734.5 | 801.4 | 734.3 | 93.6 | 203.2 | 253.9 | 69.8 | 169.2 | 249.8
790 | 628 | 468.3 | 187.32 | 218.9663 | 392.2 | 337.1 | 345.5 | 350.2 | 425.6 | 49.7 | 19.8 | 89.6 | 5.1 | 208.1 | 8.5 | 800.1 | 674.4 | 766.5 | 709.8 | 821.5 | 868.8 | 833.8 | 874.1 | 811 | 795 | 734.6 | 801.5 | 731.8 | 93.8 | 203.5 | 254.4 | 70 | 169.6 | 250
791 | 629 | 467.7 | 187.08 | 218.6857 | 390.6 | 336.7 | 345 | 349.9 | 426.7 | 49.6 | 19.8 | 89.7 | 4.4 | 208.3 | 8.2 | 800.3 | 671.2 | 767 | 709.8 | 822.7 | 868.9 | 833.8 | 876.9 | 810.5 | 794.1 | 734.8 | 801.7 | 730.8 | 94 | 203.7 | 254.6 | 70.1 | 169.9 | 250.2
792 | 630 | 468.5 | 187.4 | 219.0598 | 389.5 | 335.6 | 344.4 | 348.9 | 430.8 | 49.6 | 19.8 | 89.6 | 4.1 | 216.6 | 7.9 | 800.5 | 670.3 | 767.8 | 710 | 825.8 | 868.8 | 834.5 | 878.9 | 813 | 794.5 | 735.2 | 801.5 | 729.7 | 94.2 | 203.9 | 255.1 | 70.3 | 170.3 | 250.6
793 | 631 | 467.9 | 187.16 | 218.7793 | 389.9 | 334.4 | 343.8 | 348.8 | 430.3 | 49.6 | 19.8 | 89.7 | 4.5 | 215.1 | 7.6 | 800.3 | 671.8 | 767.7 | 710.3 | 825.7 | 868.9 | 835.4 | 879.2 | 814.9 | 795.4 | 735.2 | 801.7 | 730.1 | 94.4 | 204.1 | 255.3 | 70.5 | 170.6 | 250.9
794 | 632 | 467.5 | 187 | 218.5922 | 390.5 | 333.6 | 343.5 | 349 | 427.8 | 49.5 | 19.8 | 89.7 | 4.5 | 220.9 | 7.1 | 800.2 | 672.9 | 766.9 | 710.1 | 825.7 | 868.6 | 834.9 | 879.6 | 814.9 | 795.7 | 735 | 802.2 | 731.4 | 94.6 | 204.3 | 255.5 | 70.7 | 171 | 251.2
795 | 633 | 468.3 | 187.32 | 218.9663 | 391.5 | 332.4 | 343.1 | 348.7 | 425.8 | 49.4 | 19.8 | 89.8 | 5 | 212.9 | 5.9 | 800.1 | 671.9 | 766.2 | 710 | 824.4 | 868.7 | 834.1 | 878.9 | 810.7 | 794.9 | 734.7 | 802.7 | 731.8 | 94.8 | 204.6 | 255.7 | 70.8 | 171.3 | 251.5
796 | 634 | 468.5 | 187.4 | 219.0598 | 393 | 331.6 | 342.1 | 347.8 | 427 | 49.3 | 19.8 | 89.9 | 5 | 232 | 4.8 | 800.4 | 670.8 | 765.8 | 710.3 | 823.3 | 868.9 | 831.5 | 878.4 | 806.9 | 792.7 | 735.2 | 802.5 | 732.4 | 95.1 | 204.8 | 255.9 | 71 | 171.5 | 251.7
797 | 635 | 467.8 | 187.12 | 218.7325 | 395 | 331 | 342 | 347.4 | 427.2 | 49.3 | 19.8 | 90 | 4.9 | 229.4 | 5.1 | 800.5 | 668.7 | 765.1 | 710.5 | 821.5 | 869.2 | 829.8 | 878.1 | 806.1 | 791.3 | 735.5 | 803.2 | 733.5 | 95.3 | 205.1 | 256.1 | 71.2 | 171.7 | 251.9
798 | 636 | 468.6 | 187.44 | 219.1066 | 395 | 330.5 | 341.9 | 347.3 | 425.5 | 49.4 | 19.8 | 90 | 4.4 | 203.2 | 6.2 | 800.5 | 668.1 | 762.3 | 710.7 | 817.6 | 869.3 | 826.3 | 874.9 | 802.7 | 789.8 | 735.6 | 803.1 | 735 | 95.5 | 205.2 | 256.5 | 71.3 | 172 | 252.3
799 | 637 | 468.6 | 187.44 | 219.1066 | 395.5 | 330.6 | 341.7 | 347 | 425.2 | 49.5 | 19.8 | 90 | 4.2 | 213.9 | 6.8 | 800.6 | 666.6 | 760.4 | 710.9 | 814.9 | 869.3 | 822.4 | 874.8 | 800.5 | 787.3 | 736 | 802.7 | 734.6 | 95.7 | 205.3 | 256.9 | 71.5 | 172.3 | 252.6
800 | 638 | 468.8 | 187.52 | 219.2001 | 395.3 | 330.5 | 341.6 | 346.3 | 426.4 | 49.6 | 19.8 | 90.2 | 4.6 | 221.8 | 6.8 | 800.6 | 664.7 | 762 | 711.3 | 813.4 | 869.1 | 822 | 876.5 | 800.7 | 786.3 | 736.6 | 802.4 | 733.2 | 95.9 | 205.5 | 257.4 | 71.7 | 172.7 | 252.7
801 | 639 | 468.6 | 187.44 | 219.1066 | 394.6 | 330.4 | 341.6 | 346.5 | 427.9 | 49.7 | 19.8 | 90.3 | 4.2 | 223.5 | 6.6 | 800.7 | 664.5 | 764.3 | 711.5 | 814.5 | 868.7 | 823.3 | 879.8 | 803.4 | 786.5 | 736.5 | 803 | 733.2 | 96.1 | 205.7 | 257.9 | 71.9 | 173 | 252.9
802 | 640 | 468.2 | 187.28 | 218.9195 | 394.2 | 331.2 | 340.8 | 347.2 | 430.6 | 49.8 | 19.8 | 90.4 | 4.5 | 254.4 | 6.1 | 800.7 | 665.3 | 765.7 | 711.7 | 813.2 | 868 | 824 | 880.7 | 803.7 | 786.6 | 736.2 | 802.4 | 732.1 | 96.3 | 206 | 258.5 | 72 | 173.4 | 253.4
803 | 641 | 467.9 | 187.16 | 218.7793 | 395.5 | 331.5 | 340.3 | 348.1 | 431.9 | 50 | 19.8 | 90.6 | 4 | 252.1 | 5 | 800.7 | 666.1 | 766.5 | 711.8 | 813.7 | 867.6 | 826.8 | 880.2 | 805.5 | 787.4 | 736.3 | 801.8 | 731.3 | 96.6 | 206.3 | 258.7 | 72.2 | 173.7 | 254
804 | 642 | 469.5 | 187.8 | 219.5274 | 394.9 | 330.9 | 340.8 | 349.2 | 430.6 | 50.1 | 19.8 | 90.8 | 4.2 | 206.3 | 4.5 | 800.5 | 666 | 767.9 | 711.8 | 813.7 | 867.3 | 828.4 | 881 | 806.7 | 788.1 | 736.2 | 801.3 | 730.6 | 96.8 | 206.7 | 258.7 | 72.4 | 173.9 | 254.2
805 | 643 | 468.2 | 187.28 | 218.9195 | 394.7 | 331.1 | 340.4 | 349.5 | 429.5 | 50.2 | 19.8 | 90.9 | 4.4 | 204.7 | 5.7 | 800.3 | 663.8 | 766.5 | 712 | 810.2 | 867 | 826.1 | 877.7 | 802.7 | 787.4 | 735.9 | 801.1 | 730.4 | 97 | 207 | 259 | 72.6 | 174.2 | 254.6
806 | 644 | 467.3 | 186.92 | 218.4987 | 394.2 | 331.5 | 340.3 | 349.6 | 429.2 | 50.3 | 19.8 | 91.1 | 5.2 | 214.1 | 6.5 | 800.2 | 664 | 765.7 | 712.1 | 807.8 | 866.8 | 824.4 | 876.3 | 800.9 | 787 | 735.7 | 800.2 | 731.7 | 97.2 | 207.3 | 259.2 | 72.7 | 174.4 | 255
807 | 645 | 467.8 | 187.12 | 218.7325 | 394.2 | 331.8 | 340.7 | 350.5 | 428.2 | 50.3 | 19.8 | 91.2 | 5 | 204.4 | 6.1 | 800.2 | 663.6 | 763.9 | 712.3 | 807 | 866.5 | 823.1 | 875.9 | 800.1 | 786 | 735.5 | 799.3 | 732 | 97.4 | 207.6 | 259.5 | 72.9 | 174.7 | 255.2
808 | 646 | 467.9 | 187.16 | 218.7793 | 395.6 | 331.9 | 340.9 | 350.9 | 426.8 | 50.3 | 19.8 | 91.3 | 5.2 | 228.7 | 4.7 | 800.3 | 661 | 760.1 | 712.4 | 804.1 | 866.2 | 818.2 | 872.9 | 793.2 | 783.7 | 735.4 | 798.9 | 732 | 97.6 | 207.9 | 259.7 | 73.1 | 174.9 | 255.3
809 | 647 | 469 | 187.6 | 219.2936 | 398.2 | 331.9 | 341 | 351.2 | 426.4 | 50.4 | 19.8 | 91.5 | 5.2 | 249.1 | 4.1 | 800.3 | 658.8 | 758.1 | 712.8 | 800.6 | 866 | 813 | 874.3 | 790.7 | 781.3 | 735.9 | 798.2 | 731.3 | 97.8 | 208.2 | 260.5 | 73.2 | 175.2 | 255.5
810 | 648 | 468.8 | 187.52 | 219.2001 | 398.7 | 332.1 | 341.2 | 351.9 | 428 | 50.5 | 19.8 | 91.7 | 4.7 | 236.4 | 3.5 | 800.2 | 657.4 | 756.7 | 712.9 | 798.1 | 865.4 | 808.9 | 875.2 | 788.8 | 779.2 | 736.6 | 797.6 | 730.1 | 98 | 208.4 | 260.9 | 73.4 | 175.5 | 255.9
811 | 649 | 468.7 | 187.48 | 219.1533 | 398.7 | 332.4 | 341.6 | 352.4 | 429.3 | 50.6 | 19.8 | 91.9 | 5 | 210.2 | 4 | 800.1 | 656 | 756.1 | 713.6 | 793.8 | 865 | 804.6 | 875 | 786.6 | 777.1 | 737.3 | 797.1 | 728.6 | 98.2 | 208.7 | 261.2 | 73.6 | 175.7 | 256.2
812 | 650 | 466 | 186.4 | 217.8909 | 398.8 | 333 | 342.1 | 352.7 | 429.8 | 50.6 | 19.8 | 92.2 | 4.9 | 213.1 | 4.5 | 800 | 655.1 | 754.9 | 714.1 | 789.6 | 864.4 | 797.1 | 872.2 | 782.4 | 774.3 | 737.9 | 796.2 | 726 | 98.5 | 209 | 261.8 | 73.7 | 176 | 256.4
813 | 651 | 464.8 | 185.92 | 217.3298 | 399.6 | 333 | 343.4 | 353.3 | 430.6 | 50.7 | 19.8 | 92.3 | 4.3 | 214.2 | 4 | 800.1 | 653.7 | 753.5 | 714.6 | 784.6 | 863.4 | 791.4 | 870.9 | 780.9 | 771.7 | 738.4 | 795.1 | 722.9 | 98.7 | 209.3 | 262.3 | 73.9 | 176.2 | 256.7
814 | 652 | 465.4 | 186.16 | 217.6103 | 400.8 | 332.5 | 344.7 | 353.6 | 432.5 | 50.8 | 19.8 | 92.4 | 4.5 | 246 | 3.7 | 799.8 | 654.5 | 756.7 | 714.9 | 785.9 | 862.3 | 795.7 | 872.4 | 785.1 | 773.1 | 738.5 | 793.5 | 722.4 | 98.9 | 209.7 | 262.4 | 74.1 | 176.4 | 257
815 | 653 | 468 | 187.2 | 218.826 | 399.7 | 332.8 | 345.5 | 353.9 | 439.1 | 50.9 | 19.8 | 92.4 | 4.4 | 253.5 | 3.5 | 799.5 | 653.7 | 758.4 | 715 | 788 | 861.5 | 803.2 | 872.8 | 789.8 | 774.8 | 737.9 | 792.7 | 722.9 | 99.1 | 210 | 262.7 | 74.2 | 176.7 | 257.3
816 | 654 | 469.3 | 187.72 | 219.4339 | 399.1 | 334.1 | 345.4 | 353.7 | 441.9 | 50.9 | 19.8 | 92.5 | 4.1 | 230.3 | 3.6 | 798.9 | 650.2 | 758.3 | 714.7 | 788.8 | 860.9 | 804.2 | 873.5 | 791.6 | 773.9 | 736.8 | 791.6 | 722.2 | 99.3 | 210.4 | 263.2 | 74.4 | 177 | 257.4
817 | 655 | 469.4 | 187.76 | 219.4806 | 398.8 | 336.7 | 344.4 | 353.3 | 441.4 | 51 | 19.8 | 92.5 | 4.1 | 220.6 | 4.3 | 798.5 | 648.7 | 760.3 | 714.2 | 788.3 | 860.1 | 806.3 | 873.8 | 793.3 | 774.3 | 735.8 | 790.8 | 722.4 | 99.5 | 210.7 | 263.4 | 74.6 | 177.3 | 257.8
818 | 656 | 468.7 | 187.48 | 219.1533 | 401.6 | 338.5 | 343.5 | 353.1 | 443.9 | 51.1 | 19.7 | 92.5 | 4.2 | 231.3 | 5 | 798.4 | 650.4 | 763 | 714 | 789.6 | 859.3 | 810.9 | 875.8 | 795.3 | 775.7 | 734.6 | 790.3 | 723.6 | 99.7 | 211.1 | 263.8 | 74.7 | 177.6 | 258.3
819 | 657 | 466.2 | 186.48 | 217.9844 | 402.9 | 338.9 | 342.9 | 353.8 | 447.5 | 51.1 | 19.7 | 92.5 | 4.4 | 232.2 | 5.7 | 798.1 | 652.3 | 764.2 | 713.6 | 793.1 | 858.7 | 815.8 | 878.1 | 799.6 | 777.2 | 733.6 | 789.5 | 725.5 | 99.9 | 211.4 | 264.2 | 74.9 | 177.9 | 258.5
820 | 658 | 467.5 | 187 | 218.5922 | 402.9 | 339.1 | 343.5 | 354.7 | 450.1 | 51.1 | 19.7 | 92.5 | 4.4 | 227.8 | 5.9 | 797.7 | 652.4 | 763.9 | 713.3 | 792.2 | 858.3 | 817.2 | 877.7 | 800 | 776.5 | 732.5 | 787.9 | 726.6 | 100.1 | 211.8 | 264.5 | 75.1 | 178.2 | 258.7
821 | 659 | 467.3 | 186.92 | 218.4987 | 404.2 | 339.2 | 344.3 | 354.9 | 451.6 | 51.2 | 19.7 | 92.6 | 4.4 | 232.5 | 6.4 | 797.6 | 653.6 | 764.8 | 713.4 | 791.5 | 857.9 | 817.1 | 878.3 | 800.8 | 776.7 | 732.2 | 786.5 | 726.1 | 100.3 | 212.1 | 265.4 | 75.2 | 178.5 | 259.2
822 | 660 | 467.2 | 186.88 | 218.452 | 405.1 | 338.7 | 344.4 | 355.5 | 455.3 | 51.4 | 19.7 | 92.5 | 4.3 | 237.7 | 6.6 | 797.4 | 653.1 | 764.4 | 713.8 | 789.5 | 857.5 | 814.1 | 878.1 | 798.7 | 775.2 | 732.6 | 785.1 | 723.8 | 100.5 | 212.4 | 266 | 75.4 | 178.8 | 259.4
823 | 661 | 466.7 | 186.68 | 218.2182 | 404.8 | 338.4 | 344.4 | 356.2 | 454.6 | 51.6 | 19.7 | 92.6 | 4.2 | 228.7 | 6.5 | 797.3 | 653.9 | 765 | 713.8 | 789.8 | 857.1 | 816.1 | 877.2 | 798.4 | 776.6 | 732.7 | 784.2 | 724.7 | 100.7 | 212.8 | 266.2 | 75.5 | 179.1 | 259.6
824 | 662 | 467.8 | 187.12 | 218.7325 | 404.7 | 339 | 345.3 | 356.4 | 451.1 | 51.6 | 19.7 | 92.5 | 4.2 | 234.1 | 6.3 | 797.1 | 654.5 | 764.8 | 713.6 | 789.5 | 856.7 | 816.6 | 876.7 | 797.4 | 777.7 | 732.1 | 783.5 | 726.5 | 100.9 | 213.2 | 266.3 | 75.7 | 179.4 | 260
825 | 663 | 468.3 | 187.32 | 218.9663 | 404.7 | 339.7 | 345.7 | 356.4 | 448.8 | 51.6 | 19.7 | 92.5 | 4.1 | 241.3 | 6.2 | 797.2 | 654.7 | 764.7 | 713.7 | 788.9 | 856.1 | 817.1 | 876.6 | 798 | 777.2 | 731.9 | 783.1 | 727.1 | 101.2 | 213.5 | 266.7 | 75.9 | 179.8 | 260.4
826 | 664 | 467.4 | 186.96 | 218.5455 | 405.6 | 340.3 | 345.6 | 356.9 | 447.7 | 51.6 | 19.7 | 92.4 | 4.4 | 239.1 | 6.1 | 797.2 | 656.3 | 763.9 | 713.7 | 789 | 855.7 | 818.5 | 875.9 | 798.6 | 777.4 | 731.5 | 782.1 | 728.6 | 101.4 | 213.9 | 266.9 | 76 | 180.1 | 260.7
827 | 665 | 467.1 | 186.84 | 218.4052 | 406.5 | 341.1 | 345.9 | 357.6 | 447.6 | 51.5 | 19.7 | 92.3 | 4.5 | 245.5 | 6.4 | 797.1 | 655.8 | 763.8 | 713.8 | 784.8 | 855.5 | 814.8 | 873.8 | 794.9 | 776.8 | 731.4 | 781.5 | 730 | 101.6 | 214.3 | 267.4 | 76.2 | 180.5 | 260.9
828 | 666 | 467.2 | 186.88 | 218.452 | 406.8 | 341.5 | 345.8 | 357.3 | 445.5 | 51.5 | 19.7 | 92.2 | 4.6 | 226.3 | 5.7 | 797.2 | 654.3 | 762.2 | 714.4 | 780.4 | 854.9 | 808.4 | 871 | 789.3 | 774.5 | 731.7 | 781.1 | 729.6 | 101.8 | 214.7 | 267.8 | 76.4 | 180.8 | 260.9
829 | 667 | 467 | 186.8 | 218.3584 | 407 | 341.2 | 345.6 | 356.9 | 444.1 | 51.4 | 19.7 | 92.2 | 4.6 | 211.9 | 4.9 | 797.3 | 654.6 | 762 | 715.1 | 776 | 854.4 | 802.3 | 869 | 784 | 773.4 | 732.3 | 780.4 | 727.2 | 102 | 215 | 268.3 | 76.5 | 181.1 | 261
830 | 668 | 468.4 | 187.36 | 219.013 | 408.8 | 342 | 346.6 | 357.4 | 443.8 | 51.2 | 19.7 | 92.1 | 4 | 216.2 | 4.9 | 797.3 | 655.7 | 761.8 | 715.6 | 773.6 | 853.9 | 798.6 | 868.6 | 782.1 | 772.3 | 733.2 | 779.6 | 727.1 | 102.2 | 215.4 | 268.7 | 76.7 | 181.5 | 261.4
831 | 669 | 469 | 187.6 | 219.2936 | 410.2 | 342.2 | 347.2 | 357.7 | 443.6 | 51 | 19.7 | 92 | 3.8 | 232.3 | 5 | 797.2 | 656.3 | 762.8 | 715.5 | 772.3 | 853.2 | 799.2 | 867.5 | 781.8 | 773.2 | 733.3 | 779.2 | 727.9 | 102.4 | 215.8 | 268.7 | 76.9 | 181.8 | 261.7
832 | 670 | 469.1 | 187.64 | 219.3403 | 409.9 | 342.1 | 347.7 | 358 | 439.7 | 51 | 19.7 | 92 | 4.2 | 237.7 | 5.3 | 796.9 | 655.3 | 761.4 | 715.1 | 768.6 | 852.6 | 795.2 | 862.7 | 775.6 | 771.4 | 732.5 | 778.6 | 728.7 | 102.6 | 216.2 | 269 | 77 | 182.1 | 261.8
833 | 671 | 469.1 | 187.64 | 219.3403 | 409.5 | 341.6 | 347.9 | 358.3 | 437.4 | 51 | 19.7 | 92.1 | 4.8 | 239.4 | 6 | 796.9 | 652.2 | 756.2 | 715.3 | 764.6 | 852.1 | 790.4 | 858.2 | 769.1 | 768 | 732.4 | 778.3 | 729.2 | 102.9 | 216.5 | 269.4 | 77.2 | 182.4 | 262.2
834 | 672 | 468.9 | 187.56 | 219.2468 | 412 | 340.9 | 347.9 | 358.6 | 437.2 | 51 | 19.7 | 92.1 | 4.8 | 249.1 | 6.7 | 796.8 | 648.6 | 751.9 | 715.2 | 760.3 | 851.4 | 782.8 | 853.6 | 761.4 | 764.8 | 732.1 | 777.9 | 726.7 | 103.1 | 216.9 | 270.5 | 77.4 | 182.7 | 262.7
835 | 673 | 468.7 | 187.48 | 219.1533 | 414.7 | 340.7 | 348.9 | 359 | 438 | 51.1 | 19.7 | 92.2 | 4.5 | 247.9 | 7.6 | 796.6 | 646.6 | 750 | 715.3 | 758.2 | 850.5 | 775.9 | 853.9 | 761 | 762.7 | 732.3 | 777.2 | 724.6 | 103.3 | 217.3 | 271.1 | 77.5 | 183.1 | 263.1
836 | 674 | 468.5 | 187.4 | 219.0598 | 416.7 | 340.4 | 350.3 | 359.6 | 438.5 | 51.2 | 19.7 | 92.2 | 4 | 237.1 | 7.6 | 796.3 | 646.8 | 751.8 | 715.6 | 757.6 | 849.4 | 775.7 | 854 | 763.1 | 764 | 732.4 | 776.4 | 724.7 | 103.5 | 217.8 | 271.1 | 77.7 | 183.4 | 263.3
837 | 675 | 468.8 | 187.52 | 219.2001 | 418.2 | 340.3 | 351 | 360 | 441.3 | 51.2 | 19.7 | 92.2 | 4.3 | 242.6 | 7.2 | 795.9 | 644.4 | 751.3 | 715.4 | 755.7 | 848.4 | 776.2 | 854.1 | 763.2 | 762.4 | 732.2 | 775.3 | 723.7 | 103.7 | 218.2 | 271.6 | 77.9 | 183.7 | 263.5
838 | 676 | 468.7 | 187.48 | 219.1533 | 420.7 | 339.7 | 352 | 360.5 | 442.6 | 51.2 | 19.7 | 92.3 | 4.4 | 248.2 | 7 | 795.8 | 642.8 | 749.4 | 715.3 | 753.7 | 847.5 | 773.6 | 855.5 | 760.9 | 760.5 | 731.9 | 774.5 | 722.9 | 103.9 | 218.6 | 272.2 | 78 | 184.1 | 263.8
839 | 677 | 468.8 | 187.52 | 219.2001 | 422.9 | 339.4 | 353.3 | 361 | 441.7 | 51.2 | 19.7 | 92.3 | 4.5 | 247.7 | 7.9 | 795.4 | 642.6 | 750.2 | 715.3 | 754.1 | 846.8 | 776.7 | 853.3 | 763.1 | 761.8 | 731.4 | 773.4 | 725 | 104.2 | 219 | 272.1 | 78.2 | 184.5 | 264
840 | 678 | 468.9 | 187.56 | 219.2468 | 424.1 | 339.7 | 353.8 | 361.3 | 439.2 | 51.3 | 19.6 | 92.2 | 4.5 | 250.1 | 8.2 | 795 | 644.2 | 750 | 714.8 | 752.8 | 846.4 | 779.1 | 849.2 | 761.9 | 761.3 | 730.5 | 772.4 | 727.6 | 104.4 | 219.4 | 272 | 78.4 | 184.8 | 264.1
841 | 679 | 467.8 | 187.12 | 218.7325 | 423.8 | 340.1 | 353.3 | 361 | 437 | 51.4 | 19.6 | 92.2 | 3.9 | 264 | 7.4 | 795 | 646.6 | 748.2 | 714.3 | 750.9 | 845.9 | 781 | 847.2 | 760.2 | 761 | 729.5 | 772.4 | 729.5 | 104.6 | 219.8 | 272 | 78.5 | 185.1 | 264.7
842 | 680 | 468.6 | 187.44 | 219.1066 | 424.2 | 340.9 | 352.6 | 360.8 | 435.2 | 51.5 | 19.6 | 92.3 | 4.3 | 270 | 6.5 | 794.8 | 650.2 | 749.3 | 714 | 751.4 | 845.5 | 785.1 | 848.7 | 765 | 760.9 | 729 | 772.3 | 731.3 | 104.8 | 220.2 | 272.2 | 78.7 | 185.4 | 265.1
843 | 681 | 469.5 | 187.8 | 219.5274 | 425.4 | 340.9 | 352.2 | 360.4 | 433.9 | 51.6 | 19.6 | 92.2 | 3.8 | 261 | 6 | 794.7 | 650.4 | 749.6 | 713.8 | 751.7 | 844.9 | 787.2 | 850.4 | 769.4 | 760.5 | 729 | 772.5 | 733.6 | 105 | 220.6 | 272.6 | 78.9 | 185.8 | 265.1
844 | 682 | 469.9 | 187.96 | 219.7144 | 425.8 | 340.5 | 352.3 | 359.3 | 433.7 | 51.7 | 19.6 | 92.2 | 3.8 | 250.8 | 5.7 | 794.6 | 650.5 | 751.4 | 713.6 | 751.7 | 844.1 | 792 | 852.5 | 773.1 | 762 | 728.6 | 772.7 | 734.3 | 105.3 | 220.9 | 273 | 79 | 186.2 | 265.2
845 | 683 | 468.7 | 187.48 | 219.1533 | 425.5 | 339.6 | 352.5 | 358.3 | 434.5 | 51.8 | 19.6 | 92.2 | 4.3 | 254.9 | 5.4 | 794.5 | 652.2 | 752.7 | 713.6 | 753.9 | 843.5 | 799.5 | 855 | 782.2 | 763.9 | 727.8 | 772.7 | 735.9 | 105.5 | 221.3 | 273.4 | 79.2 | 186.6 | 265.5
846 | 684 | 468.1 | 187.24 | 218.8728 | 423.8 | 338.6 | 352.1 | 358 | 433 | 51.8 | 19.6 | 92.2 | 4.6 | 274.1 | 5.4 | 794.5 | 656.1 | 752.2 | 713.6 | 754.9 | 842.9 | 803.9 | 855.5 | 784.5 | 764.6 | 727 | 773.2 | 737.4 | 105.7 | 221.7 | 273.5 | 79.4 | 186.9 | 265.9
847 | 685 | 468.1 | 187.24 | 218.8728 | 423.4 | 337.9 | 351.8 | 358.4 | 430.6 | 51.8 | 19.6 | 92.3 | 4.7 | 278 | 5.5 | 794.5 | 659.7 | 752.8 | 713.6 | 754.1 | 842.5 | 806.3 | 856.3 | 784.8 | 765.2 | 726.7 | 774 | 739.4 | 105.9 | 222 | 273.8 | 79.5 | 187.1 | 266.3
848 | 686 | 469.6 | 187.84 | 219.5741 | 426.7 | 337.7 | 351.8 | 358.7 | 428.9 | 52 | 19.6 | 92.3 | 4.5 | 273.5 | 6 | 794.6 | 660.6 | 753.5 | 713.7 | 753.6 | 842.1 | 807.9 | 857.3 | 784.1 | 764.8 | 726.8 | 774.7 | 741.6 | 106.2 | 222.4 | 274.1 | 79.7 | 187.4 | 266.4
849 | 687 | 469.4 | 187.76 | 219.4806 | 428.9 | 338.3 | 352.3 | 358.5 | 428.4 | 52.1 | 19.6 | 92.3 | 4.9 | 272.2 | 6.2 | 794.8 | 660.6 | 753.3 | 713.8 | 753.6 | 841.9 | 807.1 | 859.5 | 783.3 | 765 | 726.9 | 775.7 | 742.5 | 106.4 | 222.7 | 274.4 | 79.9 | 187.7 | 266.7
850 | 688 | 468.8 | 187.52 | 219.2001 | 429.3 | 338.8 | 352.7 | 358.7 | 427.7 | 52 | 19.6 | 92.4 | 4.8 | 258.7 | 7.3 | 794.7 | 660.1 | 756.4 | 713.8 | 753.2 | 841.6 | 805.5 | 860.6 | 784.8 | 765.4 | 727.1 | 776.6 | 742.3 | 106.6 | 223 | 275 | 80 | 188 | 266.9
851 | 689 | 468.4 | 187.36 | 219.013 | 430.2 | 338.4 | 353 | 359.2 | 430.2 | 52 | 19.6 | 92.4 | 4.6 | 253.3 | 7.2 | 794.7 | 659.5 | 758.1 | 714.1 | 752.7 | 841 | 805.7 | 861.2 | 783.8 | 765.3 | 727.3 | 777.1 | 741.6 | 106.8 | 223.4 | 275.5 | 80.2 | 188.4 | 267.1
852 | 690 | 468 | 187.2 | 218.826 | 432.8 | 337.5 | 353.8 | 359.5 | 433.3 | 52 | 19.6 | 92.4 | 4.6 | 252.7 | 6.4 | 794.7 | 657.5 | 757 | 714.4 | 750.3 | 840.7 | 800.3 | 860.3 | 776.4 | 764.2 | 727.6 | 777.2 | 738.7 | 107.1 | 223.7 | 276.2 | 80.4 | 188.8 | 267.5
853 | 691 | 469.5 | 187.8 | 219.5274 | 432.5 | 337.5 | 354.8 | 360 | 439.6 | 51.9 | 19.6 | 92.5 | 4.2 | 265.5 | 5.8 | 794.8 | 652.1 | 754.3 | 714.9 | 749.4 | 840.5 | 795.7 | 859.5 | 773 | 761 | 728.1 | 777.4 | 735.5 | 107.3 | 224 | 276.9 | 80.5 | 189.1 | 267.7
854 | 692 | 467.1 | 186.84 | 218.4052 | 431.6 | 337.6 | 355.1 | 360 | 440.9 | 51.9 | 19.6 | 92.7 | 4.4 | 274 | 5.5 | 794.8 | 649.2 | 753.6 | 715 | 748.2 | 840.2 | 793.3 | 859 | 771.7 | 760.6 | 728.1 | 776.7 | 733.6 | 107.5 | 224.4 | 277.3 | 80.7 | 189.5 | 268
855 | 693 | 468 | 187.2 | 218.826 | 432.8 | 338.9 | 355.8 | 359.4 | 443.1 | 51.9 | 19.6 | 92.9 | 5 | 261.1 | 5 | 794.8 | 646.5 | 752 | 715.3 | 748 | 839.7 | 790.4 | 860.1 | 770.4 | 759.2 | 728.2 | 776.1 | 731.3 | 107.7 | 224.7 | 277.8 | 80.8 | 189.9 | 268.3
856 | 694 | 468.5 | 187.4 | 219.0598 | 434.3 | 340.3 | 356 | 358.9 | 444.6 | 51.9 | 19.6 | 93 | 4.5 | 277.7 | 6.2 | 794.6 | 648.1 | 754.3 | 715.5 | 749.5 | 839.2 | 794.3 | 861.6 | 778.9 | 760.8 | 727.7 | 775.2 | 731.3 | 108 | 225.1 | 278.1 | 81 | 190.3 | 268.6
857 | 695 | 468.6 | 187.44 | 219.1066 | 432.7 | 341.8 | 356.6 | 358.8 | 444.4 | 52 | 19.6 | 93.1 | 5.3 | 273.1 | 6.7 | 794.4 | 649.3 | 757 | 715.4 | 751.3 | 838.5 | 802.2 | 862.7 | 789.7 | 762.9 | 726.7 | 774.4 | 733 | 108.2 | 225.4 | 278.1 | 81.2 | 190.6 | 268.8
858 | 696 | 468.6 | 187.44 | 219.1066 | 430.6 | 343.3 | 356.9 | 359.1 | 442.6 | 52 | 19.6 | 93 | 4.8 | 271.7 | 6.6 | 794 | 650.8 | 758.5 | 715 | 753.6 | 837.8 | 807.2 | 863 | 796.1 | 764.2 | 725.8 | 773.1 | 735 | 108.4 | 225.8 | 278.6 | 81.3 | 190.9 | 269
859 | 697 | 467.2 | 186.88 | 218.452 | 431.2 | 344.2 | 355.9 | 359.3 | 444.4 | 52.1 | 19.6 | 93 | 4.5 | 258 | 6.5 | 793.8 | 650.5 | 757.4 | 714.9 | 752.2 | 837.3 | 803.9 | 860.6 | 789.3 | 762.4 | 725.7 | 772.1 | 734.6 | 108.7 | 226.1 | 279.2 | 81.5 | 191.2 | 269.3
860 | 698 | 467.8 | 187.12 | 218.7325 | 431.4 | 344.5 | 355.6 | 359.5 | 448.3 | 52.2 | 19.6 | 93 | 5.3 | 251.5 | 7.1 | 793.6 | 647.3 | 753.6 | 715.5 | 747.2 | 836.9 | 794.1 | 855.6 | 775 | 758.7 | 726.4 | 771.3 | 731.2 | 108.9 | 226.5 | 279.9 | 81.7 | 191.5 | 269.5
861 | 699 | 467.1 | 186.84 | 218.4052 | 432.3 | 346 | 356.5 | 360.1 | 453.2 | 52.2 | 19.6 | 92.9 | 5.3 | 255.7 | 7.8 | 793.7 | 642 | 749.1 | 715.7 | 741 | 836.4 | 781.8 | 848.9 | 762.3 | 755 | 726.8 | 770.4 | 725.6 | 109.1 | 226.8 | 280.9 | 81.8 | 191.8 | 269.7
862 | 700 | 466.9 | 186.76 | 218.3117 | 433.5 | 347.9 | 358 | 360.3 | 457.2 | 52.2 | 19.6 | 92.9 | 5.4 | 252.1 | 8.8 | 793.5 | 636.6 | 746.5 | 715.5 | 737.7 | 835.6 | 773.4 | 846.4 | 755.8 | 752.7 | 726.7 | 769.3 | 722.6 | 109.4 | 227.2 | 281.2 | 82 | 192.2 | 269.9
863 | 701 | 467.8 | 187.12 | 218.7325 | 434.2 | 348.6 | 358.9 | 360.5 | 457.5 | 52.3 | 19.6 | 92.9 | 4.8 | 256.7 | 8.9 | 793.2 | 632.8 | 745 | 715.5 | 734.6 | 835 | 766.1 | 846.8 | 750.4 | 750.8 | 726.4 | 768 | 719.2 | 109.6 | 227.6 | 281.5 | 82.1 | 192.6 | 270.1
864 | 702 | 469.4 | 187.76 | 219.4806 | 433.2 | 349.2 | 359.6 | 360.7 | 457.7 | 52.4 | 19.6 | 92.9 | 4.4 | 248.2 | 8.2 | 793 | 629.8 | 744 | 715.8 | 732.2 | 834.4 | 760.4 | 845.8 | 746.6 | 748.4 | 726.3 | 766.7 | 716.6 | 109.8 | 228 | 281.9 | 82.3 | 193 | 270.6
865 | 703 | 468.6 | 187.44 | 219.1066 | 432.2 | 349.4 | 360.5 | 361.2 | 455.6 | 52.4 | 19.6 | 92.9 | 5 | 252.3 | 8.2 | 792.9 | 626.2 | 742.8 | 716.1 | 732.8 | 833.9 | 760.3 | 847.8 | 756.1 | 746.4 | 725.7 | 765 | 716.8 | 110 | 228.4 | 281.8 | 82.5 | 193.4 | 271.1
866 | 704 | 468.9 | 187.56 | 219.2468 | 432.4 | 349.1 | 360.6 | 361.8 | 453.3 | 52.4 | 19.6 | 93 | 4.8 | 252.3 | 8.9 | 792.5 | 626.8 | 745.5 | 716.1 | 734.1 | 833.1 | 766.2 | 848.9 | 764.7 | 746.9 | 724.7 | 763.1 | 718.7 | 110.3 | 228.8 | 281.9 | 82.6 | 193.7 | 271.4
867 | 705 | 469 | 187.6 | 219.2936 | 434 | 349.1 | 360.4 | 362.2 | 452.2 | 52.4 | 19.6 | 93 | 4.6 | 251.2 | 9.7 | 792.2 | 626.6 | 747.1 | 716 | 735.8 | 832.7 | 771.2 | 850.4 | 770.2 | 747.3 | 723.9 | 761.4 | 720.1 | 110.5 | 229.1 | 282.3 | 82.8 | 194.1 | 271.6
868 | 706 | 468.4 | 187.36 | 219.013 | 435.2 | 349.6 | 359.6 | 362.4 | 451.3 | 52.4 | 19.6 | 93 | 4.8 | 256.5 | 10.1 | 792 | 621.6 | 743.7 | 716.1 | 731.8 | 832.4 | 765.5 | 845.8 | 759.3 | 744.3 | 723 | 760.2 | 719.7 | 110.7 | 229.4 | 282.7 | 82.9 | 194.5 | 271.9
869 | 707 | 468.8 | 187.52 | 219.2001 | 436.1 | 349.9 | 358.8 | 362.5 | 449.2 | 52.5 | 19.6 | 93 | 5.4 | 259.8 | 9.3 | 791.8 | 616.3 | 741.4 | 716.2 | 732.3 | 831.9 | 760.6 | 845.9 | 759.9 | 741.4 | 722.3 | 758.8 | 719.6 | 111 | 229.8 | 282.8 | 83.1 | 194.8 | 272
870 | 708 | 469.3 | 187.72 | 219.4339 | 437.3 | 349.3 | 359.2 | 362.8 | 447.7 | 52.5 | 19.6 | 93 | 4.7 | 265.8 | 9.3 | 791.3 | 616.6 | 744.4 | 716.3 | 732.7 | 831.6 | 765.2 | 848.5 | 764.5 | 743.1 | 721.2 | 757.5 | 720.1 | 111.2 | 230.1 | 283.2 | 83.3 | 195.1 | 272.2
871 | 709 | 468.3 | 187.32 | 218.9663 | 439.7 | 349.5 | 359.5 | 362.7 | 447.5 | 52.6 | 19.6 | 93 | 4.3 | 257.3 | 9.4 | 791 | 615.7 | 744.6 | 716.5 | 729.3 | 831.2 | 761.9 | 849.8 | 763 | 741.1 | 720.3 | 756.3 | 719 | 111.4 | 230.5 | 283.9 | 83.4 | 195.3 | 272.4
872 | 710 | 468.3 | 187.32 | 218.9663 | 441.3 | 349.8 | 359.3 | 362.6 | 447.4 | 52.7 | 19.6 | 93 | 4 | 257.3 | 10 | 790.9 | 616.9 | 746.3 | 716.8 | 729.8 | 830.9 | 764.8 | 851.5 | 769.7 | 742.1 | 719.9 | 755.3 | 719.7 | 111.7 | 230.9 | 284.2 | 83.6 | 195.5 | 272.7
873 | 711 | 468.2 | 187.28 | 218.9195 | 442.9 | 350.2 | 359 | 362.6 | 445.8 | 52.8 | 19.6 | 93 | 3.8 | 255.7 | 10 | 790.4 | 622.2 | 748.3 | 716.8 | 733.5 | 830.3 | 774.2 | 852.5 | 785.4 | 744.8 | 719 | 753.8 | 722.9 | 111.9 | 231.2 | 284 | 83.8 | 195.8 | 272.8
874 | 712 | 468.7 | 187.48 | 219.1533 | 441.3 | 350.4 | 358.8 | 362.8 | 444.5 | 52.9 | 19.6 | 93.1 | 4.6 | 255.7 | 9.9 | 790 | 628.3 | 750 | 716.5 | 738.7 | 829.6 | 785.7 | 853.8 | 797.8 | 747.6 | 717.8 | 752.6 | 726.8 | 112.2 | 231.6 | 284.1 | 83.9 | 196 | 273.2
875 | 713 | 468.5 | 187.4 | 219.0598 | 440.9 | 349.8 | 358.7 | 362.8 | 442.7 | 53 | 19.6 | 93.1 | 4.7 | 254.4 | 9.8 | 789.5 | 633.5 | 748.7 | 715.9 | 740.2 | 829.3 | 793.9 | 855.1 | 803.5 | 748.8 | 716.4 | 751.8 | 730.2 | 112.4 | 232 | 284.1 | 84.1 | 196.3 | 273.7
876 | 714 | 468.8 | 187.52 | 219.2001 | 439.4 | 349 | 358.1 | 362.5 | 441.7 | 53 | 19.6 | 93.3 | 4.8 | 249.9 | 9.7 | 789 | 635.2 | 749.6 | 715.5 | 744.4 | 829.1 | 799.6 | 857.5 | 813.1 | 749.7 | 715.9 | 751.5 | 731.8 | 112.6 | 232.3 | 284.4 | 84.3 | 196.6 | 273.8
877 | 715 | 468.5 | 187.4 | 219.0598 | 438.1 | 349 | 357.4 | 362.3 | 441.4 | 53.1 | 19.5 | 93.5 | 5.6 | 253.4 | 9.4 | 788.5 | 635.2 | 748.5 | 715.1 | 744.4 | 828.9 | 801.6 | 858 | 813.2 | 749.6 | 715.7 | 751.4 | 733.2 | 112.9 | 232.6 | 284.7 | 84.4 | 196.8 | 273.9
878 | 716 | 468.2 | 187.28 | 218.9195 | 436.9 | 349.2 | 357 | 361.8 | 439.8 | 53.2 | 19.5 | 93.7 | 5.4 | 256.5 | 9 | 788.2 | 635.5 | 748.2 | 715.1 | 746.3 | 829 | 804.5 | 859.3 | 814.6 | 749.3 | 715.7 | 751.5 | 734.9 | 113.1 | 232.9 | 284.8 | 84.6 | 197.2 | 274.1
879 | 717 | 471.7 | 188.68 | 220.556 | 436.7 | 349.3 | 356.5 | 361.1 | 438.7 | 53.3 | 19.5 | 93.7 | 5.4 | 263.5 | 8.6 | 787.8 | 637.2 | 749.4 | 715.2 | 749.9 | 828.9 | 809.3 | 860.3 | 819.7 | 751.3 | 715.4 | 752.1 | 736 | 113.3 | 233.2 | 285 | 84.8 | 197.4 | 274.3
880 | 718 | 473.7 | 189.48 | 221.4912 | 438.7 | 349.1 | 356.4 | 360.3 | 437.6 | 53.3 | 19.5 | 93.8 | 5.5 | 259.6 | 8.1 | 787.3 | 640 | 750.3 | 714.4 | 753.7 | 828.8 | 814 | 862.2 | 831.3 | 752.8 | 714.8 | 752.8 | 738 | 113.6 | 233.5 | 285.2 | 84.9 | 197.7 | 274.5
881 | 719 | 472.4 | 188.96 | 220.8834 | 439.4 | 348.3 | 356.1 | 359.7 | 437.6 | 53.3 | 19.5 | 94 | 4.7 | 265.9 | 7.6 | 786.8 | 640.4 | 750.7 | 713.7 | 755 | 828.8 | 815.6 | 861.6 | 833.3 | 753.1 | 713.7 | 753.2 | 739.1 | 113.8 | 233.8 | 285.3 | 85.1 | 198 | 274.7
882 | 720 | 470 | 188 | 219.7612 | 439 | 346.8 | 355.8 | 358.8 | 436.3 | 53.3 | 19.5 | 94.1 | 5.1 | 262.3 | 7.9 | 786.5 | 636.1 | 748.1 | 713.7 | 751.2 | 828.9 | 807.1 | 858.7 | 820.4 | 750.7 | 713.2 | 754.7 | 738.1 | 114.1 | 234.2 | 285.7 | 85.2 | 198.4 | 274.7
883 | 721 | 470 | 188 | 219.7612 | 440.9 | 345.6 | 356.1 | 357.8 | 434.5 | 53.3 | 19.5 | 94.2 | 4.8 | 268.1 | 8.8 | 786.8 | 629.8 | 743.9 | 714.3 | 746.9 | 828.9 | 795.2 | 855.5 | 803.4 | 746.8 | 713.2 | 755.5 | 734.6 | 114.3 | 234.5 | 285.9 | 85.4 | 198.7 | 274.8
884 | 722 | 469.8 | 187.92 | 219.6677 | 444.6 | 344.3 | 356.3 | 357.1 | 433.8 | 53.2 | 19.5 | 94.3 | 5.3 | 271.8 | 8.6 | 787.1 | 624.2 | 742 | 715.1 | 743.3 | 828.7 | 785 | 853.1 | 790.3 | 744 | 713.2 | 756.2 | 731.1 | 114.6 | 234.8 | 286.6 | 85.5 | 199 | 275.1
885 | 723 | 468.2 | 187.28 | 218.9195 | 446.3 | 343.6 | 356.1 | 356.5 | 435.3 | 53.2 | 19.5 | 94.4 | 5.5 | 267 | 9 | 787 | 622.8 | 742.5 | 715.6 | 740.3 | 828.3 | 778.6 | 851 | 782.5 | 743.2 | 713.4 | 756.4 | 728.1 | 114.8 | 235.2 | 287.4 | 85.7 | 199.3 | 275.6
886 | 724 | 468.7 | 187.48 | 219.1533 | 448.4 | 343.9 | 356.2 | 356.6 | 437.4 | 53.2 | 19.5 | 94.4 | 5.3 | 261.4 | 8.8 | 787 | 619.4 | 739.2 | 716.3 | 736.5 | 828 | 770.2 | 847.8 | 770.4 | 740 | 713.6 | 756.9 | 723.4 | 115 | 235.5 | 288 | 85.8 | 199.6 | 275.8
887 | 725 | 469.3 | 187.72 | 219.4339 | 448.6 | 345.1 | 356.6 | 357.3 | 439.6 | 53.3 | 19.5 | 94.4 | 4.8 | 257.4 | 8.6 | 787.1 | 615.5 | 736.1 | 716.7 | 732.9 | 827.6 | 761.6 | 844.5 | 763.9 | 737.2 | 713.7 | 756.9 | 718.7 | 115.3 | 235.9 | 288.8 | 86 | 199.8 | 275.9
888 | 726 | 469.1 | 187.64 | 219.3403 | 447.7 | 345.4 | 357.3 | 358 | 446.5 | 53.5 | 19.5 | 94.5 | 4.4 | 259.4 | 8.3 | 786.7 | 613 | 736.2 | 717.1 | 733.5 | 827.1 | 759.4 | 844.6 | 767.4 | 735.5 | 713.6 | 756.2 | 716.4 | 115.5 | 236.2 | 288.8 | 86.1 | 200 | 276.2
889 | 727 | 469.3 | 187.72 | 219.4339 | 445.8 | 345.3 | 357.9 | 358.6 | 448.6 | 53.5 | 19.5 | 94.6 | 4.7 | 251.4 | 8.1 | 786.1 | 611.3 | 736.3 | 717.6 | 731.6 | 826.7 | 756.6 | 844.5 | 761.6 | 734.6 | 713.2 | 755.4 | 714.8 | 115.8 | 236.6 | 289.3 | 86.3 | 200.3 | 276.6
890 | 728 | 469.6 | 187.84 | 219.5741 | 444.5 | 346.7 | 357.3 | 358.8 | 462.4 | 53.5 | 19.5 | 94.6 | 4.1 | 250.5 | 7.9 | 785.7 | 608.6 | 736.3 | 717.9 | 735.7 | 826.4 | 762.8 | 846.2 | 771.4 | 733.5 | 712.6 | 754.1 | 713.6 | 116 | 237 | 289.1 | 86.4 | 200.6 | 276.7
891 | 729 | 468.3 | 187.32 | 218.9663 | 444.7 | 347.3 | 357.3 | 359 | 462.1 | 53.4 | 19.5 | 94.7 | 4.9 | 246.1 | 7.5 | 785 | 606.5 | 737 | 717.4 | 733.1 | 826 | 762.5 | 848.4 | 774.8 | 733.6 | 711.6 | 752.4 | 713.5 | 116.2 | 237.4 | 289.4 | 86.6 | 200.8 | 276.8
892 | 730 | 468.8 | 187.52 | 219.2001 | 444.3 | 348.8 | 357.1 | 358.3 | 459.2 | 53.3 | 19.5 | 94.9 | 4.9 | 250.5 | 7.2 | 784.2 | 604.8 | 737.1 | 717.1 | 731.5 | 825.6 | 761.1 | 846.5 | 778.7 | 733.1 | 710.4 | 750.9 | 714.4 | 116.5 | 237.8 | 289.9 | 86.8 | 201.1 | 277.2
893 | 731 | 467.7 | 187.08 | 218.6857 | 443.5 | 349.9 | 356.9 | 357.2 | 454.8 | 53.4 | 19.5 | 94.9 | 5.6 | 247.5 | 7.4 | 783.7 | 603.5 | 738.1 | 717.2 | 733.9 | 825.3 | 762.1 | 849.1 | 785.6 | 732.6 | 709.4 | 748.7 | 715.3 | 116.7 | 238.1 | 289.9 | 86.9 | 201.4 | 277.7
894 | 732 | 465.9 | 186.36 | 217.8441 | 442.2 | 350.7 | 357 | 356.7 | 453.6 | 53.5 | 19.5 | 95 | 6.2 | 251.1 | 8 | 783.1 | 604 | 739.7 | 717.5 | 734.7 | 825.1 | 766.6 | 849.5 | 791.5 | 733.4 | 708.3 | 747.4 | 715.6 | 117 | 238.5 | 290.2 | 87 | 201.8 | 277.9
895 | 733 | 466.2 | 186.48 | 217.9844 | 442.7 | 351.1 | 356.5 | 357.1 | 452.2 | 53.7 | 19.5 | 95 | 5.4 | 248.8 | 8.3 | 782.6 | 603.6 | 740 | 718 | 735.5 | 825 | 769.3 | 851.1 | 790.7 | 733.7 | 707 | 745.2 | 716.2 | 117.2 | 238.9 | 290.6 | 87.2 | 202.2 | 278.1
896 | 734 | 467.3 | 186.92 | 218.4987 | 444.9 | 351.9 | 356.7 | 357.7 | 449.6 | 53.7 | 19.5 | 95.1 | 4.7 | 246.8 | 9 | 781.9 | 604.8 | 742.2 | 718 | 735 | 824.7 | 769.8 | 852.6 | 795.8 | 732.5 | 705.9 | 744.8 | 716.5 | 117.4 | 239.3 | 291 | 87.3 | 202.6 | 278.4
897 | 735 | 467.8 | 187.12 | 218.7325 | 445.2 | 352.9 | 356.5 | 357.6 | 448.6 | 53.7 | 19.5 | 95.2 | 4.3 | 238.8 | 9.7 | 780.9 | 609.3 | 744.8 | 717.8 | 738.4 | 824.3 | 780 | 855.7 | 811.9 | 734.8 | 705.2 | 743.7 | 719.1 | 117.7 | 239.6 | 291 | 87.5 | 203 | 278.6
898 | 736 | 468.4 | 187.36 | 219.013 | 445.4 | 353.1 | 356.9 | 357.4 | 445.2 | 53.7 | 19.5 | 95.4 | 4.7 | 242.1 | 9.7 | 780.2 | 612.5 | 744.5 | 717.4 | 742 | 824.4 | 784 | 855.6 | 816.1 | 735.8 | 704.2 | 742.9 | 721 | 117.9 | 240 | 291.1 | 87.6 | 203.2 | 278.7
899 | 737 | 467.7 | 187.08 | 218.6857 | 446.9 | 353.2 | 356.7 | 357.1 | 444.2 | 53.8 | 19.5 | 95.5 | 4.6 | 245.1 | 9.5 | 779.8 | 609.8 | 742 | 717.6 | 743.3 | 824.6 | 780.3 | 853.5 | 810.9 | 732.2 | 703.9 | 742.4 | 720 | 118.2 | 240.4 | 291.4 | 87.8 | 203.4 | 278.8
900 | 738 | 466.1 | 186.44 | 217.9376 | 447.6 | 352.8 | 355.5 | 357.5 | 449.5 | 53.8 | 19.5 | 95.6 | 4.6 | 241.8 | 8.9 | 779.6 | 610 | 741.4 | 717.7 | 747.3 | 824.9 | 782.6 | 853.2 | 818.5 | 731.9 | 703.9 | 741.9 | 720.5 | 118.4 | 240.7 | 291.5 | 87.9 | 203.6 | 279
901 | 739 | 467.6 | 187.04 | 218.639 | 448.2 | 352.9 | 355.1 | 357.8 | 447.3 | 53.7 | 19.5 | 95.6 | 4.4 | 236 | 9 | 779 | 612.5 | 742.5 | 717.3 | 749.9 | 825.3 | 787.6 | 855.9 | 821.9 | 733.7 | 703.4 | 741.5 | 721.3 | 118.7 | 241 | 291.5 | 88.1 | 203.8 | 279.1
902 | 740 | 467 | 186.8 | 218.3584 | 448.5 | 353.3 | 354.6 | 357.3 | 445.1 | 53.7 | 19.5 | 95.6 | 5.2 | 237.7 | 9.2 | 778.6 | 609.9 | 742.4 | 717.1 | 750.2 | 825.6 | 785.4 | 855.4 | 814.3 | 731.5 | 702.8 | 740.9 | 719.2 | 118.9 | 241.4 | 291.8 | 88.2 | 204.1 | 279.1
903 | 741 | 466.4 | 186.56 | 218.0779 | 446.2 | 353.3 | 353.4 | 356.5 | 448.2 | 53.8 | 19.5 | 95.6 | 5.3 | 239.7 | 9.3 | 778.5 | 607.8 | 742.3 | 717.3 | 748.7 | 826.1 | 780.7 | 856.7 | 804.6 | 730.2 | 702.4 | 740.3 | 717 | 119.1 | 241.7 | 292.5 | 88.3 | 204.4 | 279.3
904 | 742 | 467.4 | 186.96 | 218.5455 | 445 | 353.6 | 352.2 | 355.8 | 450.1 | 53.9 | 19.4 | 95.7 | 5.4 | 243.6 | 9.4 | 778.1 | 610.8 | 743.9 | 717.3 | 749 | 826.2 | 784.4 | 857.7 | 804.2 | 731.3 | 702.1 | 740.6 | 716.5 | 119.4 | 242.1 | 293 | 88.5 | 204.6 | 279.7
905 | 743 | 464.6 | 185.84 | 217.2363 | 444.9 | 353.9 | 351.9 | 356.1 | 452.1 | 53.8 | 19.4 | 95.7 | 5.2 | 251.4 | 9.6 | 777.9 | 610.6 | 743.9 | 718.1 | 747.4 | 826.6 | 781.6 | 856.6 | 799.4 | 728.9 | 702.3 | 740.2 | 714 | 119.6 | 242.4 | 293.8 | 88.6 | 204.8 | 280
906 | 744 | 466.7 | 186.68 | 218.2182 | 444.3 | 354.1 | 351.8 | 356.4 | 457 | 53.7 | 19.4 | 95.6 | 4.9 | 250.7 | 9.2 | 777.8 | 608.5 | 743.8 | 718.6 | 750.7 | 826.9 | 781.4 | 852.4 | 804.2 | 727.8 | 702.5 | 740 | 712.1 | 119.9 | 242.8 | 293.8 | 88.8 | 205.1 | 280.5
907 | 745 | 467.9 | 187.16 | 218.7793 | 446.5 | 354 | 352.1 | 356.7 | 462.2 | 53.7 | 19.4 | 95.7 | 4.9 | 259 | 8.7 | 777.4 | 609.9 | 744.3 | 718.5 | 756 | 827.1 | 788.9 | 851.1 | 822.1 | 730 | 702.1 | 738.9 | 713 | 120.1 | 243.2 | 293.5 | 88.9 | 205.3 | 280.8
908 | 746 | 466.6 | 186.64 | 218.1714 | 444.6 | 354.8 | 352.3 | 357 | 458.3 | 53.8 | 19.4 | 95.8 | 4.8 | 263.1 | 8.3 | 776.9 | 612 | 742.6 | 718.1 | 758.9 | 827.6 | 792 | 849.1 | 825.4 | 731 | 701 | 738.1 | 713.8 | 120.4 | 243.6 | 293.5 | 89.1 | 205.6 | 280.9
909 | 747 | 466.6 | 186.64 | 218.1714 | 442.7 | 355.2 | 351.8 | 357.1 | 451.8 | 53.8 | 19.4 | 95.9 | 4.7 | 264.9 | 8.1 | 776.8 | 616.9 | 740.4 | 718.2 | 759.9 | 828 | 796.7 | 849.9 | 828.6 | 731 | 700.5 | 737.7 | 716.4 | 120.6 | 244 | 293.7 | 89.2 | 205.9 | 281
910 | 748 | 466.7 | 186.68 | 218.2182 | 445 | 355.6 | 351.1 | 356.7 | 446.3 | 53.9 | 19.4 | 96 | 4.8 | 266.3 | 8 | 776.7 | 621.8 | 740.6 | 718.5 | 763.4 | 828.2 | 800.1 | 854.1 | 839.1 | 732.3 | 700.5 | 738 | 719.2 | 120.9 | 244.3 | 293.9 | 89.4 | 206.2 | 281.5
911 | 749 | 467.4 | 186.96 | 218.5455 | 447.9 | 356 | 350.7 | 356.3 | 443.2 | 53.8 | 19.4 | 96 | 4.7 | 270.5 | 7.8 | 776.4 | 624.5 | 741.5 | 718.5 | 766.4 | 828.6 | 804.4 | 856.1 | 847 | 734 | 700.6 | 738.2 | 720.9 | 121.1 | 244.7 | 294 | 89.6 | 206.5 | 281.5
912 | 750 | 467.9 | 187.16 | 218.7793 | 447.6 | 356.1 | 350.4 | 356.3 | 438.6 | 53.7 | 19.4 | 96.1 | 4.4 | 269.4 | 7.1 | 775.9 | 626.9 | 744.8 | 717.8 | 767.9 | 828.8 | 809.3 | 859.4 | 852 | 736.7 | 700.2 | 738.8 | 721.3 | 121.4 | 245.1 | 294.4 | 89.7 | 206.8 | 281.5
913 | 751 | 467.8 | 187.12 | 218.7325 | 445.5 | 356 | 350.1 | 355.9 | 440.2 | 53.7 | 19.4 | 96.2 | 4.6 | 267.8 | 7 | 775.3 | 626.6 | 746.6 | 717 | 767.6 | 829 | 810.9 | 862.4 | 848.6 | 738 | 700.1 | 739.5 | 722.3 | 121.6 | 245.5 | 294.6 | 89.9 | 207.1 | 281.7
914 | 752 | 466.5 | 186.6 | 218.1246 | 444.5 | 355.3 | 349.8 | 355.2 | 437.3 | 53.8 | 19.4 | 96.3 | 4.6 | 255.9 | 7.3 | 774.8 | 627.4 | 747.7 | 716.6 | 765 | 829.2 | 807.5 | 863.2 | 840 | 737.7 | 699.9 | 740.1 | 721.9 | 121.9 | 245.8 | 294.9 | 90 | 207.4 | 282
915 | 753 | 466.8 | 186.72 | 218.2649 | 443.1 | 354.6 | 349.6 | 354.8 | 432.6 | 53.9 | 19.4 | 96.3 | 4.4 | 251.4 | 7.6 | 774.7 | 629.4 | 748.2 | 716.8 | 764.4 | 829.6 | 805.1 | 863.9 | 837.5 | 737.8 | 699.9 | 741 | 722.6 | 122.1 | 246.2 | 295.5 | 90.2 | 207.7 | 282.1
916 | 754 | 467.2 | 186.88 | 218.452 | 446.2 | 353.8 | 350.3 | 354.4 | 430.9 | 53.9 | 19.4 | 96.4 | 4 | 249.2 | 8.1 | 774.9 | 632.7 | 748.1 | 717.6 | 763.4 | 829.7 | 805.2 | 863 | 840.1 | 739.1 | 700.1 | 741.9 | 724.1 | 122.4 | 246.6 | 295.4 | 90.3 | 208 | 282.5
917 | 755 | 466.9 | 186.76 | 218.3117 | 450.6 | 353.5 | 350.8 | 354.5 | 428.4 | 53.9 | 19.4 | 96.4 | 4.8 | 243.8 | 7.8 | 774.7 | 637 | 749.8 | 717.8 | 762.7 | 829.7 | 805.9 | 862.6 | 846.5 | 740.8 | 700.6 | 742.5 | 726.9 | 122.6 | 247 | 295.6 | 90.5 | 208.2 | 282.7
918 | 756 | 466.4 | 186.56 | 218.0779 | 451.9 | 353.9 | 351.2 | 354.7 | 428 | 53.8 | 19.4 | 96.5 | 4.9 | 250.6 | 7.5 | 774.9 | 638.5 | 751.3 | 717.9 | 760.7 | 829.6 | 803.8 | 861.2 | 845.4 | 741.5 | 701.1 | 743 | 728.1 | 122.9 | 247.4 | 296 | 90.7 | 208.4 | 282.8
919 | 757 | 469.7 | 187.88 | 219.6209 | 453.7 | 354.2 | 351.9 | 355.1 | 427.2 | 53.8 | 19.4 | 96.6 | 4.7 | 250.4 | 7.8 | 774.8 | 639.3 | 752.8 | 718.6 | 759.3 | 829.5 | 802.4 | 861.1 | 836.4 | 742.4 | 701.4 | 743.4 | 728.3 | 123.1 | 247.8 | 296.3 | 90.8 | 208.7 | 283
920 | 758 | 470.8 | 188.32 | 220.1352 | 454.6 | 354.5 | 352.3 | 355.7 | 427.9 | 53.9 | 19.4 | 96.6 | 4.9 | 250.6 | 7.8 | 775 | 636.8 | 751.5 | 719.5 | 756.8 | 829.3 | 796.2 | 858.5 | 822.4 | 741.2 | 701.6 | 743.9 | 726.4 | 123.3 | 248.2 | 297 | 91 | 209.1 | 283.3
921 | 759 | 470.2 | 188.08 | 219.8547 | 456.2 | 354.4 | 352.8 | 356.6 | 432.1 | 54 | 19.4 | 96.7 | 4.9 | 247 | 8 | 775.3 | 631.4 | 748 | 720.9 | 753.2 | 828.9 | 785.6 | 855.7 | 808.7 | 737.2 | 701.8 | 744 | 721.4 | 123.6 | 248.7 | 298.2 | 91.1 | 209.5 | 283.5
922 | 760 | 468.9 | 187.56 | 219.2468 | 460.4 | 353.5 | 353.9 | 357.2 | 440.5 | 54.1 | 19.4 | 96.7 | 4.7 | 249.8 | 8.1 | 775.2 | 627.8 | 748.6 | 721.4 | 753.2 | 828.4 | 783.9 | 855.8 | 812.2 | 737.4 | 702.1 | 743.6 | 718.6 | 123.8 | 249.2 | 298.5 | 91.3 | 209.9 | 283.7
923 | 761 | 468.6 | 187.44 | 219.1066 | 462.2 | 352.8 | 355 | 357.5 | 444.5 | 54.1 | 19.4 | 96.7 | 4.6 | 248.1 | 8 | 774.7 | 628.4 | 750.7 | 721.2 | 752.4 | 827.8 | 783.7 | 857.2 | 816.3 | 738.1 | 702.1 | 743.1 | 718.4 | 124.1 | 249.7 | 298.4 | 91.5 | 210.3 | 283.9
924 | 762 | 468.6 | 187.44 | 219.1066 | 463.7 | 353.6 | 355.4 | 357.2 | 450.6 | 54.1 | 19.4 | 96.7 | 4 | 245.1 | 7.9 | 774.3 | 631 | 752.7 | 721.3 | 752 | 827.3 | 783.4 | 857.3 | 810.3 | 739.5 | 702 | 743 | 718.7 | 124.3 | 250.1 | 298.6 | 91.6 | 210.6 | 284.2
925 | 763 | 468.3 | 187.32 | 218.9663 | 463.8 | 354.5 | 355.3 | 357.1 | 451 | 54.1 | 19.4 | 96.6 | 4 | 249.5 | 7.5 | 773.5 | 631 | 754.2 | 721.4 | 749.6 | 826.9 | 781.5 | 857.2 | 810.7 | 740.2 | 701.7 | 742.6 | 719.1 | 124.6 | 250.6 | 298.7 | 91.8 | 211 | 284.5
926 | 764 | 469 | 187.6 | 219.2936 | 463.3 | 354.5 | 355.6 | 357.9 | 447.4 | 54.1 | 19.4 | 96.5 | 4 | 244.6 | 7.1 | 773.4 | 630.7 | 753.1 | 721.9 | 748 | 826.7 | 781.6 | 856.5 | 813.1 | 739.5 | 701.3 | 742 | 720.8 | 124.8 | 251.1 | 299 | 92 | 211.4 | 284.5
927 | 765 | 468.9 | 187.56 | 219.2468 | 465.1 | 354.5 | 356.1 | 358.3 | 445.6 | 54.2 | 19.4 | 96.5 | 4.3 | 244.6 | 7.1 | 774 | 628.1 | 751 | 723.3 | 745.2 | 826.8 | 776 | 855.2 | 802.8 | 736.9 | 701.2 | 741.5 | 720.8 | 125.1 | 251.6 | 299.5 | 92.2 | 211.9 | 284.7
928 | 766 | 468.9 | 187.56 | 219.2468 | 468 | 354.2 | 356.3 | 358.7 | 444.1 | 54.2 | 19.4 | 96.5 | 4.5 | 243.2 | 7.4 | 773.9 | 626.8 | 750.6 | 723.8 | 742.8 | 826.5 | 773 | 853.2 | 800 | 736.2 | 700.8 | 740.7 | 721.5 | 125.3 | 252.1 | 299.7 | 92.3 | 212.3 | 284.9
929 | 767 | 468.1 | 187.24 | 218.8728 | 468.3 | 354.1 | 356.6 | 359.5 | 441.9 | 54.3 | 19.4 | 96.5 | 4.2 | 246.2 | 7 | 773.7 | 625.5 | 751.2 | 724.1 | 741.9 | 826 | 773.7 | 852 | 803.6 | 736.1 | 700.5 | 740.5 | 722 | 125.5 | 252.6 | 299.7 | 92.5 | 212.8 | 285.2
930 | 768 | 467.9 | 187.16 | 218.7793 | 466.3 | 354.1 | 356.7 | 359.9 | 442.6 | 54.4 | 19.4 | 96.5 | 4.4 | 243.4 | 6.5 | 773.6 | 627.3 | 751.2 | 724.1 | 746.3 | 825.7 | 784.4 | 854.1 | 820.3 | 738.3 | 700 | 740.1 | 725.6 | 125.8 | 253.1 | 299.7 | 92.7 | 213.4 | 285.4
931 | 769 | 468.4 | 187.36 | 219.013 | 464 | 353.5 | 356.7 | 359.6 | 440.2 | 54.5 | 19.4 | 96.5 | 4.5 | 237.1 | 6 | 773.5 | 630.5 | 750.4 | 724.1 | 747 | 825.4 | 790.4 | 855 | 829.2 | 738.2 | 699.4 | 739.7 | 728.6 | 126 | 253.6 | 299.8 | 92.9 | 214 | 285.6
932 | 770 | 467.2 | 186.88 | 218.452 | 464.6 | 353.8 | 356.5 | 359.6 | 437.8 | 54.6 | 19.4 | 96.6 | 4.1 | 237.8 | 5.7 | 773.2 | 633.8 | 751.4 | 723.4 | 746.7 | 825.3 | 794.8 | 854.8 | 831.5 | 739.9 | 698.9 | 739.5 | 730.6 | 126.3 | 254.1 | 300 | 93 | 214.7 | 285.8
933 | 771 | 467.3 | 186.92 | 218.4987 | 465.1 | 353.8 | 355.7 | 359.3 | 435.7 | 54.7 | 19.4 | 96.6 | 4.3 | 242.8 | 5.3 | 773 | 635.3 | 752.9 | 722.9 | 745 | 825.1 | 793.5 | 855.3 | 829.4 | 740.3 | 698.6 | 740.6 | 731.1 | 126.5 | 254.6 | 300 | 93.2 | 215.4 | 286
934 | 772 | 466.1 | 186.44 | 217.9376 | 465.6 | 353 | 355.2 | 358.7 | 434.3 | 54.7 | 19.4 | 96.5 | 4.4 | 243.1 | 4.9 | 772.7 | 638.9 | 754.2 | 722.6 | 746.2 | 824.8 | 796.7 | 856.4 | 833.4 | 741.2 | 698.9 | 740.4 | 731.6 | 126.8 | 255.1 | 300.6 | 93.4 | 216.1 | 286.3
935 | 773 | 467.6 | 187.04 | 218.639 | 464.8 | 352.3 | 355.3 | 358.2 | 435 | 54.7 | 19.4 | 96.4 | 4.5 | 243.7 | 4.7 | 773.2 | 637.9 | 755.1 | 723.1 | 746 | 824.7 | 796 | 857.8 | 826.5 | 740.6 | 699.2 | 741.4 | 730 | 127 | 255.6 | 301.2 | 93.6 | 216.9 | 286.6
936 | 774 | 468.4 | 187.36 | 219.013 | 465 | 352.5 | 355.5 | 357.7 | 437.2 | 54.6 | 19.4 | 96.4 | 4.5 | 249.2 | 4.6 | 773.5 | 636.3 | 755.3 | 723.5 | 745 | 824.4 | 792.4 | 858 | 826.2 | 740.2 | 699.5 | 741.2 | 728.6 | 127.2 | 256.1 | 301.6 | 93.8 | 218.1 | 286.8
937 | 775 | 468 | 187.2 | 218.826 | 466.3 | 352.8 | 356.3 | 357.8 | 437.3 | 54.6 | 19.4 | 96.4 | 4.5 | 247 | 4.5 | 773.8 | 632.6 | 752.2 | 724.4 | 742.4 | 824.5 | 783.7 | 854.4 | 807.7 | 736.6 | 699.9 | 741.8 | 725.5 | 127.5 | 256.6 | 302.3 | 94 | 220.6 | 287
938 | 776 | 467.7 | 187.08 | 218.6857 | 469.4 | 353.4 | 357.2 | 358.4 | 438.3 | 54.7 | 19.4 | 96.5 | 4.9 | 250.8 | 4.5 | 774.1 | 627.8 | 748.6 | 725.6 | 739.2 | 824.4 | 775.7 | 850.9 | 794.3 | 733.2 | 700 | 742 | 722.8 | 127.7 | 257.1 | 302.8 | 94.2 | 222.9 | 287.2
939 | 777 | 467.3 | 186.92 | 218.4987 | 470 | 353.6 | 358.1 | 359.1 | 439.1 | 54.7 | 19.3 | 96.5 | 4.6 | 260.6 | 4.3 | 773.7 | 624.3 | 747.4 | 725.6 | 737.7 | 824.1 | 771.3 | 849.9 | 797.5 | 731.9 | 699.6 | 741.4 | 721 | 127.9 | 257.6 | 303 | 94.4 | 224.8 | 287.3
940 | 778 | 468.3 | 187.32 | 218.9663 | 471.8 | 353.8 | 359.1 | 360 | 440 | 54.7 | 19.3 | 96.5 | 4.4 | 251.5 | 4.2 | 773.8 | 620 | 744.8 | 725.6 | 734.7 | 823.6 | 762.6 | 846.8 | 778.6 | 729.2 | 699.2 | 740.9 | 717.5 | 128.2 | 258.1 | 303.4 | 94.6 | 226.3 | 287.6
941 | 779 | 466.1 | 186.44 | 217.9376 | 473.8 | 354.7 | 359.9 | 360.3 | 442.1 | 54.7 | 19.3 | 96.5 | 4.6 | 249.1 | 4.1 | 773.8 | 614.4 | 740.7 | 726 | 729.3 | 823.1 | 752.6 | 840.8 | 759.6 | 725.1 | 698.8 | 741.3 | 713.6 | 128.4 | 258.7 | 304 | 94.8 | 227.5 | 287.8
942 | 780 | 464.9 | 185.96 | 217.3765 | 477.5 | 355.3 | 360.2 | 360.1 | 444 | 54.7 | 19.3 | 96.5 | 4.3 | 251.5 | 4 | 773.4 | 611.6 | 740.3 | 725.9 | 729.3 | 822.4 | 751.9 | 840.8 | 762.3 | 724.4 | 698.3 | 740.5 | 712.6 | 128.6 | 259.2 | 303.9 | 95 | 228.1 | 287.9
943 | 781 | 465.7 | 186.28 | 217.7506 | 479.9 | 355.2 | 360.3 | 360.1 | 445.7 | 54.7 | 19.3 | 96.6 | 5.2 | 255.9 | 4 | 772.7 | 610.1 | 741.9 | 725.7 | 731.5 | 822 | 756.7 | 843.7 | 772 | 724.4 | 697.6 | 739 | 712.4 | 128.8 | 259.7 | 304 | 95.2 | 228.6 | 288.1
944 | 782 | 467.3 | 186.92 | 218.4987 | 478.2 | 355.7 | 360 | 360.5 | 446.9 | 54.7 | 19.3 | 96.7 | 4.4 | 260.5 | 3.7 | 772.2 | 608.5 | 742.4 | 725.5 | 732.8 | 821.7 | 759.2 | 845.2 | 772 | 724 | 696.9 | 737.7 | 712.9 | 129 | 260.3 | 304.2 | 95.4 | 229.4 | 288.5
945 | 783 | 467.8 | 187.12 | 218.7325 | 478.3 | 356.5 | 359.8 | 360.5 | 446.2 | 54.6 | 19.3 | 96.7 | 3.8 | 262.1 | 3.3 | 771.6 | 610 | 744.6 | 724.8 | 734.3 | 821.3 | 764.3 | 848 | 783.4 | 724.8 | 696.1 | 736.3 | 714.7 | 129.2 | 260.8 | 304.3 | 95.6 | 230.5 | 288.7
946 | 784 | 467.2 | 186.88 | 218.452 | 477.8 | 356.8 | 359.4 | 360.8 | 446 | 54.5 | 19.3 | 96.7 | 4.7 | 259.9 | 3.3 | 771.1 | 608.5 | 743.6 | 725.3 | 731.9 | 820.8 | 763.5 | 847.7 | 785.4 | 722.8 | 695.5 | 735.3 | 714.8 | 129.5 | 261.3 | 304.6 | 95.8 | 231.6 | 288.9
947 | 785 | 468 | 187.2 | 218.826 | 477 | 357.1 | 358.9 | 361 | 445.7 | 54.5 | 19.3 | 96.7 | 4.5 | 256.4 | 3.8 | 771.3 | 607.4 | 744.1 | 726.2 | 732.3 | 820.5 | 764.1 | 848.8 | 786.9 | 722.3 | 695 | 734.2 | 715 | 129.7 | 261.8 | 304.8 | 96 | 232.5 | 289.1
948 | 786 | 468.5 | 187.4 | 219.0598 | 476.4 | 357.8 | 358.5 | 361.1 | 444.5 | 54.5 | 19.3 | 96.7 | 4.6 | 257.3 | 4.3 | 770.9 | 611.3 | 746 | 726 | 736.4 | 820.1 | 774 | 851.6 | 801.6 | 724.6 | 694.4 | 733 | 716.8 | 129.9 | 262.4 | 304.8 | 96.2 | 233.2 | 289.4
949 | 787 | 468.5 | 187.4 | 219.0598 | 475.7 | 358 | 357.7 | 361.2 | 442.8 | 54.5 | 19.3 | 96.8 | 5 | 259.9 | 4.4 | 770.5 | 615.5 | 746 | 725.2 | 735.7 | 819.9 | 776.2 | 849.6 | 799.3 | 725.2 | 693.4 | 732.6 | 718.7 | 130.1 | 262.9 | 304.9 | 96.4 | 233.9 | 289.5
950 | 788 | 467.3 | 186.92 | 218.4987 | 475.7 | 357.3 | 356.8 | 361.2 | 440.8 | 54.4 | 19.3 | 97 | 4.7 | 256.1 | 4.5 | 770.5 | 616.7 | 743.1 | 727 | 732.8 | 819.9 | 772.5 | 847.3 | 787.8 | 722.9 | 693.4 | 732.2 | 719.9 | 130.3 | 263.5 | 305.2 | 96.6 | 234.5 | 289.6
951 | 789 | 467.1 | 186.84 | 218.4052 | 475.1 | 356.6 | 356.2 | 361.1 | 438.6 | 54.4 | 19.3 | 97 | 5 | 256.9 | 4.9 | 770.6 | 617.9 | 740.4 | 728.5 | 732.2 | 819.7 | 770.5 | 846.1 | 789.1 | 722.4 | 693.2 | 731.8 | 720.8 | 130.5 | 264 | 305.3 | 96.9 | 235.2 | 289.8
952 | 790 | 467.1 | 186.84 | 218.4052 | 476.2 | 356.5 | 355.9 | 360.5 | 436.7 | 54.3 | 19.3 | 97.1 | 5 | 258.4 | 5.4 | 770.6 | 618.5 | 737.5 | 729.2 | 728.3 | 819.6 | 764.8 | 839 | 773.4 | 720 | 693 | 732.5 | 721 | 130.7 | 264.6 | 305.4 | 97.1 | 235.7 | 290
953 | 791 | 467.1 | 186.84 | 218.4052 | 477.2 | 355.7 | 355.3 | 359.7 | 434.2 | 54.2 | 19.3 | 97 | 5.4 | 262.2 | 6 | 770.6 | 618.5 | 736.2 | 729.8 | 727.6 | 819.2 | 764.2 | 838.4 | 777.4 | 719.7 | 692.8 | 732.4 | 721.4 | 130.9 | 265.2 | 305.6 | 97.3 | 236.3 | 290.3
954 | 792 | 467.9 | 187.16 | 218.7793 | 477.2 | 354.5 | 355.1 | 359.5 | 432.8 | 54.1 | 19.3 | 97 | 5.2 | 271.3 | 5.8 | 770.2 | 622.1 | 738.8 | 730.1 | 729 | 818.8 | 768.8 | 842 | 784.8 | 721.4 | 692.6 | 732.6 | 722.7 | 131.1 | 265.7 | 305.8 | 97.6 | 236.8 | 290.5
955 | 793 | 468 | 187.2 | 218.826 | 478.4 | 353.1 | 354.9 | 359.1 | 432.1 | 54.1 | 19.3 | 97 | 5.2 | 284.5 | 5.5 | 770 | 626.2 | 742 | 729.6 | 730.7 | 818.5 | 774.9 | 845.5 | 797.4 | 722.4 | 692.7 | 733.4 | 724.4 | 131.3 | 266.2 | 305.9 | 97.8 | 237.3 | 290.6
956 | 794 | 467.5 | 187 | 218.5922 | 479.7 | 352.2 | 354.9 | 358.4 | 432 | 54.2 | 19.3 | 96.9 | 5.3 | 292 | 4.8 | 769.8 | 629.8 | 744.9 | 729.8 | 729.7 | 818.5 | 775.6 | 845 | 793.7 | 723.9 | 692.8 | 734.6 | 724.4 | 131.4 | 266.7 | 306.3 | 98 | 237.7 | 290.8
957 | 795 | 455.8 | 182.32 | 213.1216 | 479.1 | 352.1 | 354.8 | 358.1 | 432.5 | 54.3 | 19.3 | 97 | 5.6 | 285.4 | 4.1 | 770 | 630.3 | 744.3 | 731 | 726.4 | 818.2 | 772 | 843.5 | 787.1 | 722.8 | 693 | 735.4 | 724.7 | 131.6 | 267.2 | 306.4 | 98.3 | 238.1 | 291
958 | 796 | 111.1 | 44.44 | 51.9478 | 478.6 | 351.9 | 354.7 | 358.1 | 434.2 | 54.3 | 19.3 | 97 | 5.3 | 270.1 | 4.4 | 769.9 | 635.9 | 746.3 | 730.6 | 725.8 | 817.6 | 773 | 842.6 | 800.4 | 724.5 | 692.7 | 735.9 | 725.5 | 131.8 | 267.7 | 306.5 | 98.5 | 238.4 | 291.2
959 | 797 | -6.9 | 0 | 0 | 479.7 | 351.3 | 354.6 | 358 | 433.6 | 54.4 | 19.3 | 97.1 | 4.7 | 258.4 | 5.2 | 769.5 | 638.3 | 743.4 | 731.3 | 723.3 | 817.3 | 767.3 | 836 | 789 | 722.7 | 692.8 | 737 | 726 | 132 | 268.2 | 306.5 | 98.7 | 238.8 | 291.6
960 | 798 | -6.9 | 0 | 0 | 480.8 | 350.8 | 354.3 | 358 | 430.2 | 54.4 | 19.3 | 97.2 | 4.5 | 268.4 | 5.7 | 769.8 | 630.5 | 734 | 734 | 714.4 | 817.1 | 751 | 821.4 | 750.7 | 716.2 | 692.6 | 738.4 | 719.9 | 132.2 | 268.7 | 306.2 | 99 | 239.2 | 291.4
961 | 799 | -6.9 | 0 | 0 | 482.5 | 350 | 353.8 | 358 | 425.1 | 54.4 | 19.3 | 97.4 | 4.5 | 271.8 | 5.7 | 770 | 620.7 | 725.1 | 734.4 | 706.7 | 816.4 | 734.4 | 807 | 718.7 | 710.6 | 691.7 | 739 | 712.5 | 132.4 | 269.1 | 306 | 99.2 | 239.5 | 291.1
962 | 800 | -6.9 | 0 | 0 | 483.5 | 348.9 | 352.7 | 356.9 | 419.7 | 54.3 | 19.3 | 97.5 | 4.8 | 267 | 5.7 | 769.8 | 612.1 | 717.1 | 733.5 | 699.6 | 815.5 | 719 | 793.9 | 693.8 | 705.3 | 690.3 | 738.9 | 705.7 | 132.5 | 269.4 | 306 | 99.5 | 239.9 | 291
963 | 801 | -6.9 | 0 | 0 | 482.1 | 347.5 | 351.2 | 354.9 | 414.9 | 54.4 | 19.3 | 97.6 | 4.5 | 274.7 | 5.7 | 769.8 | 603.8 | 709.3 | 732.7 | 692.8 | 814 | 705.4 | 782.1 | 675.8 | 700 | 688.5 | 739.5 | 699.2 | 132.7 | 269.8 | 306 | 99.7 | 240.3 | 291
964 | 802 | -6.9 | 0 | 0 | 479.3 | 345.9 | 349.5 | 352.7 | 410.9 | 54.4 | 19.3 | 97.6 | 4.4 | 269.7 | 5.7 | 769.1 | 596.1 | 702.2 | 731.7 | 686.2 | 812.7 | 692.1 | 771.6 | 658.7 | 695.1 | 686.5 | 739.6 | 694.4 | 132.9 | 270.1 | 306 | 100 | 240.7 | 291
965 | 803 | -6.9 | 0 | 0 | 476.9 | 344.4 | 347.6 | 350.2 | 406.7 | 54.3 | 19.3 | 97.4 | 4.4 | 261 | 5.7 | 768 | 589.4 | 696 | 730 | 680.1 | 811 | 680 | 761.7 | 641.6 | 690.2 | 684.4 | 739.2 | 689.6 | 133.1 | 270.4 | 305.9 | 100.2 | 241.1 | 291
966 | 804 | -6.9 | 0 | 0 | 472.7 | 342.7 | 345.8 | 347.5 | 401.9 | 54.3 | 19.2 | 97.2 | 4 | 265.3 | 6.6 | 766.8 | 582.3 | 690.1 | 729 | 674.5 | 809.1 | 668.6 | 753.2 | 633.9 | 685.6 | 682.2 | 738.6 | 685.9 | 133.2 | 270.6 | 305.9 | 100.5 | 241.4 | 291
967 | 805 | -6.9 | 0 | 0 | 469.5 | 340.6 | 344.2 | 345 | 397.8 | 54.4 | 19.2 | 96.8 | 3.5 | 264.3 | 7.1 | 765.1 | 575.1 | 684.2 | 726.9 | 669.2 | 807 | 658.9 | 745.3 | 623.6 | 680.6 | 679.8 | 736.9 | 683 | 133.4 | 270.9 | 305.7 | 100.7 | 241.7 | 291
968 | 806 | -6.9 | 0 | 0 | 467.5 | 338.4 | 342.4 | 342.8 | 393.7 | 54.4 | 19.2 | 96.4 | 3.4 | 260.2 | 6.9 | 763.1 | 568.5 | 678.7 | 725.1 | 664.1 | 804.8 | 649.4 | 737.5 | 618.8 | 676.6 | 677.6 | 735.7 | 679.8 | 133.6 | 271.1 | 305.6 | 101 | 242 | 290.8
969 | 807 | -6.8 | 0 | 0 | 463.2 | 336.2 | 340.5 | 340.9 | 390.2 | 54.3 | 19.2 | 95.9 | 3.5 | 269.3 | 6.9 | 761.2 | 562.7 | 673.6 | 723.5 | 659 | 802.5 | 640.7 | 729.9 | 610.1 | 672.4 | 675.3 | 733.9 | 677 | 133.7 | 271.3 | 305.5 | 101.3 | 242.3 | 290.7
970 | 808 | -6.8 | 0 | 0 | 458.4 | 334 | 338.3 | 338.8 | 387 | 54.3 | 19.2 | 95.4 | 3.1 | 273.6 | 6.8 | 759.1 | 558.1 | 668.6 | 721.4 | 654 | 800.3 | 632.6 | 722 | 601.4 | 668.3 | 673 | 732.2 | 674.5 | 133.9 | 271.5 | 305.4 | 101.5 | 242.6 | 290.7
971 | 809 | -6.8 | 0 | 0 | 453.5 | 332 | 336.6 | 336.7 | 384.5 | 54.4 | 19.2 | 94.9 | 3.2 | 280.8 | 6.9 | 757.4 | 554.1 | 663.8 | 720.4 | 648.8 | 798.2 | 624.1 | 714.9 | 592.6 | 664.4 | 670.6 | 730.7 | 672.1 | 134.1 | 271.6 | 305.4 | 101.8 | 242.9 | 290.7
972 | 810 | -6.8 | 0 | 0 | 449.3 | 330.1 | 335 | 334.6 | 381.8 | 54.4 | 19.2 | 94.3 | 3.4 | 264.7 | 6.4 | 755.9 | 549.1 | 658.8 | 718.4 | 643.7 | 796 | 617.2 | 707.8 | 586.6 | 661 | 668.2 | 728.7 | 669.6 | 134.2 | 271.8 | 305.3 | 102 | 243.1 | 290.7
973 | 811 | -6.8 | 0 | 0 | 444.9 | 328.2 | 333.3 | 332.5 | 379 | 54.4 | 19.2 | 93.8 | 3.7 | 264.7 | 6 | 754.2 | 544.6 | 654.5 | 717.4 | 639 | 793.8 | 610.8 | 700.9 | 581 | 657.7 | 665.9 | 726.6 | 667.4 | 134.4 | 272 | 305.2 | 102.3 | 243.3 | 290.7
974 | 812 | -6.8 | 0 | 0 | 442.1 | 326.5 | 331.7 | 330.7 | 376.8 | 54.5 | 19.2 | 93.3 | 3.7 | 261.8 | 6.6 | 752.7 | 540.5 | 650.6 | 716.3 | 634.5 | 791.5 | 603.8 | 694.4 | 576.9 | 654 | 663.6 | 724.4 | 665.3 | 134.5 | 272.1 | 305.1 | 102.5 | 243.6 | 290.7
975 | 813 | -6.8 | 0 | 0 | 440.8 | 324.9 | 330.3 | 328.8 | 374.2 | 54.5 | 19.2 | 92.8 | 3.8 | 260.1 | 6.9 | 750.9 | 536.3 | 646.8 | 714.7 | 630.4 | 789.2 | 597.9 | 688.8 | 573.8 | 650.3 | 661.4 | 722 | 662.9 | 134.7 | 272.2 | 305.1 | 102.8 | 243.8 | 290.8
976 | 814 | -6.8 | 0 | 0 | 438 | 323.2 | 328.7 | 327.1 | 371.6 | 54.6 | 19.2 | 92.2 | 3.5 | 264.6 | 6.8 | 749.2 | 532.5 | 643.3 | 714.1 | 626.2 | 786.9 | 592.1 | 683.4 | 571 | 647 | 659.2 | 719.2 | 661 | 134.8 | 272.4 | 304.9 | 103.1 | 244 | 290.6
977 | 815 | -6.8 | 0 | 0 | 435 | 321.6 | 327.4 | 325.5 | 369 | 54.6 | 19.2 | 91.7 | 3.7 | 264.6 | 6.6 | 747.8 | 528.6 | 639.5 | 713.1 | 622 | 784.4 | 586.4 | 678.1 | 567 | 643.4 | 657 | 717.4 | 658.6 | 135 | 272.5 | 304.8 | 103.3 | 244.2 | 290.5
978 | 816 | -6.8 | 0 | 0 | 432.7 | 320 | 326.2 | 323.7 | 366.9 | 54.6 | 19.2 | 91.2 | 3.8 | 272.1 | 6.7 | 746.3 | 525 | 636.1 | 712 | 617.3 | 782 | 581.4 | 672.7 | 561.9 | 640.1 | 654.6 | 715.7 | 655.9 | 135.2 | 272.7 | 304.7 | 103.6 | 244.3 | 290.5
979 | 817 | -6.8 | 0 | 0 | 431.6 | 318.6 | 324.8 | 322.2 | 365.2 | 54.5 | 19.2 | 90.7 | 3.8 | 274.7 | 6.6 | 744.2 | 521.5 | 632.6 | 710.4 | 613.2 | 779.7 | 576.3 | 667.6 | 559.3 | 636.4 | 652.3 | 713.3 | 654.3 | 135.3 | 272.8 | 304.6 | 103.8 | 244.5 | 290.4
980 | 818 | -6.8 | 0 | 0 | 430.8 | 317.4 | 323.5 | 320.9 | 363.7 | 54.5 | 19.2 | 90.3 | 4 | 272.8 | 6.2 | 742.1 | 518.4 | 629.4 | 708.5 | 609.6 | 777.4 | 571.5 | 663.1 | 557.4 | 633.6 | 649.9 | 710.8 | 652.9 | 135.5 | 272.9 | 304.6 | 104.1 | 244.6 | 290.3
981 | 819 | -6.8 | 0 | 0 | 429.5 | 316.3 | 322.3 | 319.6 | 361.9 | 54.6 | 19.2 | 89.9 | 4.1 | 261.9 | 6.2 | 740 | 514.4 | 626.2 | 706.9 | 606 | 775 | 567.3 | 658.5 | 554.2 | 631 | 647.6 | 708.5 | 651.4 | 135.6 | 273 | 304.5 | 104.4 | 244.3 | 290.3
982 | 820 | -6.8 | 0 | 0 | 427.6 | 315.1 | 321.4 | 318.3 | 360.2 | 54.6 | 19.2 | 89.5 | 4.1 | 265 | 6.4 | 737.7 | 511.3 | 623.1 | 705 | 601.9 | 772.7 | 563.6 | 653.4 | 548.5 | 627.6 | 645.3 | 706.3 | 649.8 | 135.8 | 273.1 | 304.4 | 104.6 | 244.6 | 290.3
983 | 821 | -6.8 | 0 | 0 | 426.7 | 314.1 | 320.3 | 317 | 358.8 | 54.6 | 19.2 | 89 | 3.8 | 271.7 | 6.6 | 735.3 | 508 | 620.5 | 702.9 | 598.2 | 770.5 | 559.5 | 648.7 | 544.7 | 624.6 | 642.9 | 704.3 | 648.3 | 135.9 | 273.2 | 304.3 | 104.9 | 244.9 | 290.2
984 | 822 | -6.8 | 0 | 0 | 427 | 313.1 | 319 | 315.9 | 357.4 | 54.6 | 19.2 | 88.6 | 3.7 | 269.6 | 6.5 | 733.1 | 504.7 | 617.5 | 701.7 | 594.4 | 768.2 | 555.2 | 644.4 | 541.8 | 621.8 | 640.6 | 702.6 | 646.9 | 136.1 | 273.3 | 304.2 | 105.2 | 245.2 | 290.3
985 | 823 | -6.8 | 0 | 0 | 425.6 | 312 | 318.2 | 314.7 | 356.4 | 54.6 | 19.2 | 88.2 | 4 | 271.9 | 6.3 | 731.5 | 501.8 | 614.6 | 700.9 | 591.1 | 766 | 551.5 | 640 | 538.9 | 619.4 | 638.4 | 700 | 645.4 | 136.2 | 273.4 | 304.1 | 105.5 | 245.4 | 290.4
986 | 824 | -6.8 | 0 | 0 | 425.2 | 311.1 | 317.5 | 313.7 | 354.7 | 54.6 | 19.2 | 87.8 | 3.8 | 268.7 | 6.1 | 729.6 | 499.2 | 612.2 | 699.3 | 587.6 | 763.6 | 548.2 | 635.8 | 536.3 | 616.7 | 636.2 | 697.8 | 643.8 | 136.4 | 273.4 | 304.1 | 105.8 | 245.7 | 290.3
987 | 825 | -6.8 | 0 | 0 | 424.7 | 310.1 | 316.5 | 312.7 | 353 | 54.5 | 19.2 | 87.4 | 4 | 268 | 5.8 | 727.2 | 496 | 609.2 | 697.5 | 584.3 | 761.3 | 545.3 | 631.4 | 533.2 | 613.9 | 633.9 | 695.7 | 642.3 | 136.5 | 273.5 | 304 | 106.1 | 245.9 | 290.2
988 | 826 | -6.8 | 0 | 0 | 424.2 | 309.3 | 315.6 | 311.9 | 352 | 54.4 | 19.2 | 87 | 4 | 272 | 5.4 | 725.3 | 492.3 | 607.4 | 697 | 581 | 759.1 | 542.3 | 627.2 | 532.9 | 611.7 | 631.5 | 693.6 | 640.7 | 136.6 | 273.5 | 303.9 | 106.3 | 246.1 | 290.1
989 | 827 | -6.8 | 0 | 0 | 422 | 308.4 | 314.7 | 311 | 350.5 | 54.4 | 19.2 | 86.7 | 4 | 270.4 | 5 | 724.6 | 488 | 606.7 | 697.4 | 577.8 | 757 | 538.8 | 623 | 529.3 | 609.8 | 629 | 691.4 | 639 | 136.8 | 273.6 | 303.7 | 106.6 | 246.3 | 290
990 | 828 | -6.8 | 0 | 0 | 419.1 | 307.7 | 313.8 | 310.2 | 348.9 | 54.4 | 19.2 | 86.4 | 3.9 | 269.4 | 4.6 | 724.2 | 484 | 604.5 | 697.4 | 574.4 | 755.1 | 535.4 | 618.9 | 523.4 | 607.7 | 626.4 | 689.5 | 637 | 136.9 | 273.6 | 303.6 | 106.9 | 246.5 | 289.9
991 | 829 | -6.8 | 0 | 0 | 417.4 | 307.2 | 313 | 309.4 | 347.8 | 54.4 | 19.2 | 86.1 | 3.7 | 269.8 | 4.4 | 721.5 | 476.8 | 603.9 | 693.8 | 571.8 | 753.1 | 531.5 | 615 | 520.9 | 605.2 | 622.8 | 687.2 | 635.7 | 137 | 273.7 | 303.5 | 107.2 | 246.7 | 289.9
992 | 830 | -6.8 | 0 | 0 | 424 | 307.5 | 312.3 | 308.5 | 344.8 | 54.4 | 19.2 | 85.8 | 4.1 | 270.3 | 4.5 | 721.4 | 468.4 | 603.4 | 690 | 569.1 | 750.8 | 528.2 | 611.8 | 518.8 | 601.2 | 618.4 | 684 | 634.4 | 137.2 | 273.7 | 303.5 | 107.4 | 246.9 | 289.9
993 | 831 | -6.8 | 0 | 0 | 431.7 | 308.4 | 311.5 | 307.5 | 342.2 | 54.3 | 19.2 | 85.4 | 4.1 | 274.8 | 5 | 719.8 | 461 | 602.5 | 686.9 | 565.6 | 748.7 | 525.5 | 608.1 | 511.8 | 598.1 | 614.7 | 682.1 | 633.4 | 137.2 | 273.7 | 303.6 | 107.7 | 247.1 | 290.1
994 | 832 | -6.8 | 0 | 0 | 436.3 | 307.7 | 310.5 | 306.4 | 339.6 | 54.2 | 19.2 | 85.1 | 4 | 277.7 | 5.2 | 717.4 | 448.5 | 600.4 | 676.8 | 562.3 | 746.5 | 520.6 | 604.8 | 511.9 | 593.9 | 609.5 | 678.8 | 631.9 | 137.3 | 273.7 | 303.3 | 108 | 247.3 | 289.9
995 | 833 | -6.8 | 0 | 0 | 447 | 306.9 | 309.3 | 305.2 | 335.8 | 54.1 | 19.2 | 84.8 | 3.9 | 261.2 | 5 | 716.1 | 411.1 | 596.4 | 674.6 | 559.4 | 744.2 | 514.3 | 601.5 | 505 | 589.6 | 603.4 | 673.8 | 630.6 | 137.4 | 273.7 | 303 | 108.3 | 247.4 | 289.6
996 | 834 | -6.8 | 0 | 0 | 449.4 | 305.6 | 307.9 | 304.3 | 331.9 | 54 | 19.2 | 84.5 | 4 | 259 | 4.8 | 709.1 | 373.7 | 585.9 | 656.5 | 556.1 | 742.4 | 503.3 | 597.4 | 495.7 | 585.7 | 582.6 | 666.4 | 629.4 | 137.6 | 273.7 | 302.8 | 108.5 | 247.6 | 289.3
997 | 835 | -6.8 | 0 | 0 | 446.4 | 303.8 | 306.5 | 303.2 | 328.9 | 53.8 | 19.2 | 84.2 | 3.9 | 258.2 | 4.5 | 695 | 363.3 | 531.6 | 630.3 | 552.4 | 740.6 | 483.3 | 592.8 | 480.8 | 572.5 | 548 | 660.7 | 627.3 | 137.7 | 273.7 | 302.7 | 108.8 | 247.8 | 289.1
998 | 836 | -6.8 | 0 | 0 | 438.9 | 302.5 | 304.9 | 302 | 326.6 | 53.5 | 19.2 | 83.9 | 3.7 | 260.1 | 4.4 | 677.9 | 322 | 466.9 | 609.2 | 549 | 737.5 | 455.7 | 588.7 | 465.9 | 560.4 | 527.9 | 652.8 | 625 | 137.8 | 273.7 | 302.4 | 109.1 | 247.9 | 289
999 | 837 | -6.8 | 0 | 0 | 430.1 | 301.3 | 303.2 | 300.9 | 324.7 | 53.3 | 19.2 | 83.6 | 3.8 | 268.1 | 4.8 | 641.9 | 261.7 | 375.2 | 558.9 | 545.7 | 734.3 | 414.7 | 584.6 | 452.6 | 536 | 514.9 | 645.9 | 626.4 | 137.9 | 273.7 | 302.3 | 109.4 | 248.1 | 288.9
1000 | 838 | -6.8 | 0 | 0 | 423.1 | 300.3 | 301.7 | 299.8 | 322.8 | 53 | 19.2 | 83.4 | 3.8 | 262 | 5.8 | 616.5 | 230.6 | 304.4 | 524.7 | 542.8 | 731.3 | 395.3 | 580.4 | 439.4 | 488.3 | 504.3 | 640.9 | 623.7 | 138.1 | 273.7 | 302 | 109.7 | 248.2 | 288.7
1001 | 839 | -6.8 | 0 | 0 | 417.4 | 299.1 | 300.6 | 298.7 | 320.8 | 52.9 | 19.2 | 83.1 | 4.2 | 259.5 | 6.6 | 595 | 204 | 267.1 | 504.7 | 539 | 728.2 | 377.5 | 576.4 | 425.8 | 398 | 493.8 | 635.7 | 620 | 138.2 | 273.6 | 301.8 | 110 | 248.3 | 288.5
1002 | 840 | -6.8 | 0 | 0 | 412.4 | 297.9 | 299.5 | 297.5 | 319 | 52.9 | 19.2 | 82.9 | 4.1 | 259.5 | 6.8 | 580.5 | 183 | 244 | 492.7 | 535.3 | 724.5 | 358.7 | 572.4 | 413 | 241.5 | 483.5 | 629.1 | 617.8 | 138.3 | 273.6 | 301.6 | 110.3 | 248.5 | 288.3
1003 | 841 | -6.8 | 0 | 0 | 409.3 | 296.9 | 298.3 | 295.9 | 317.3 | 52.9 | 19.2 | 82.7 | 4.1 | 260.9 | 6.7 | 568.2 | 168.1 | 234.1 | 483.8 | 532.4 | 719.9 | 336.9 | 567.4 | 405.6 | 131.1 | 472.8 | 622.7 | 616.2 | 138.5 | 273.6 | 301.4 | 110.5 | 248.6 | 288.2
1004 | 842 | -6.8 | 0 | 0 | 406.3 | 295.8 | 297 | 294.2 | 315.6 | 52.9 | 19.2 | 82.4 | 4 | 263.5 | 6.5 | 548 | 161.6 | 225.8 | 476.3 | 529.5 | 714.3 | 308.1 | 561.9 | 395.1 | 95 | 464 | 614.1 | 614.7 | 138.6 | 273.5 | 301.3 | 110.8 | 248.7 | 288
1005 | 843 | -6.8 | 0 | 0 | 401.8 | 294.7 | 295.5 | 292.3 | 314.2 | 52.8 | 19.2 | 82.2 | 3.9 | 262.7 | 6 | 530.7 | 156.8 | 221.8 | 469.8 | 526.6 | 708.1 | 266.5 | 556.4 | 382.8 | 92.5 | 455.3 | 605.4 | 612.6 | 138.8 | 273.5 | 301.1 | 111.1 | 248.8 | 287.9
1006 | 844 | -6.8 | 0 | 0 | 398.6 | 293.8 | 294.4 | 290.7 | 313 | 52.6 | 19.2 | 82 | 4.1 | 262 | 5.8 | 514.2 | 154.3 | 211.8 | 463.7 | 523.5 | 701.3 | 228.8 | 548.2 | 361.6 | 89.8 | 447.2 | 596 | 610.2 | 138.9 | 273.4 | 301 | 111.4 | 248.9 | 287.7
1007 | 845 | -6.8 | 0 | 0 | 395.8 | 293 | 293.4 | 289.3 | 312 | 52.5 | 19.2 | 81.7 | 4 | 262.3 | 5.7 | 464.4 | 150.7 | 202.8 | 457.3 | 520.1 | 676.5 | 210.1 | 511.8 | 340.4 | 82.2 | 440.6 | 586.5 | 608.3 | 139.1 | 273.4 | 300.8 | 111.7 | 249 | 287.5
1008 | 846 | -6.8 | 0 | 0 | 391.4 | 292.3 | 292 | 288 | 310.9 | 52.3 | 19.2 | 81.5 | 4.3 | 263.4 | 5.7 | 240.8 | 145.3 | 200.3 | 449.5 | 516 | 512.9 | 170.2 | 451.7 | 317.4 | 74.8 | 434.7 | 577 | 607.1 | 139.2 | 273.3 | 300.6 | 112 | 249 | 287.4
1009 | 847 | -6.8 | 0 | 0 | 387.2 | 291.7 | 290.7 | 286.7 | 309.6 | 52 | 19.2 | 81.3 | 4.3 | 257.4 | 5.7 | 175.9 | 139.6 | 199.9 | 441.2 | 512.1 | 465.1 | 102 | 432.8 | 295.7 | 69 | 429.3 | 568 | 605.8 | 139.4 | 273.3 | 300.4 | 112.3 | 249.1 | 287.2
1010 | 848 | -6.8 | 0 | 0 | 383.1 | 291 | 289.3 | 285.4 | 308.5 | 51.8 | 19.2 | 81.1 | 4.1 | 249.3 | 6.4 | 172.6 | 124.5 | 196.9 | 432.9 | 507.1 | 441.6 | 97.3 | 425.2 | 263.7 | 63.2 | 423.2 | 558.9 | 604.9 | 139.5 | 273.2 | 300.2 | 112.6 | 249.2 | 287
1011 | 849 | -6.8 | 0 | 0 | 379.1 | 290.2 | 287.9 | 284 | 307.5 | 51.7 | 19.2 | 80.9 | 4 | 255.3 | 6.5 | 168.7 | 123.8 | 197.3 | 423.1 | 502.7 | 413.4 | 96.8 | 411.4 | 183.4 | 58.3 | 417.2 | 547.1 | 602.8 | 139.7 | 273.2 | 300 | 112.9 | 249.3 | 286.9
1012 | 850 | -6.8 | 0 | 0 | 375.6 | 289.4 | 286.4 | 282.7 | 306.3 | 51.7 | 19.2 | 80.7 | 4.2 | 266.9 | 6 | 166.2 | 127.2 | 196 | 414.3 | 497.7 | 379.7 | 94.7 | 381.2 | 113.3 | 56.5 | 409.2 | 534.3 | 601.6 | 139.9 | 273.1 | 299.9 | 113.2 | 249.4 | 286.7
1013 | 851 | -6.8 | 0 | 0 | 373 | 288.5 | 285.1 | 281.5 | 305.4 | 51.7 | 19.2 | 80.5 | 4.2 | 252.1 | 5.4 | 162.8 | 125.2 | 195 | 406.7 | 493.3 | 343.9 | 92 | 312.8 | 109.4 | 51 | 397.9 | 523.1 | 599.9 | 140 | 273.1 | 299.7 | 113.5 | 249.5 | 286.6
1014 | 852 | -6.8 | 0 | 0 | 370.6 | 287.5 | 283.9 | 280.2 | 304.3 | 51.8 | 19.2 | 80.2 | 3.9 | 242.4 | 5.1 | 160.9 | 120.6 | 195.4 | 399 | 489 | 308.8 | 91.2 | 218.2 | 109.7 | 47 | 386.9 | 512.1 | 598.2 | 140.2 | 273 | 299.5 | 113.9 | 249.6 | 286.4
1015 | 853 | -6.8 | 0 | 0 | 367.9 | 286.6 | 282.7 | 279 | 303.3 | 51.7 | 19.2 | 80 | 3.7 | 263.3 | 5.9 | 159 | 114.5 | 194.8 | 391.2 | 481.7 | 276.9 | 86.8 | 169.8 | 108.5 | 43.9 | 376.5 | 501 | 596.7 | 140.4 | 272.9 | 299.3 | 114.2 | 249.6 | 286.3
1016 | 854 | -6.8 | 0 | 0 | 365.8 | 285.6 | 281.7 | 277.7 | 301.8 | 51.6 | 19.2 | 79.8 | 3.6 | 261.3 | 6.4 | 156 | 116.7 | 195.2 | 380.4 | 472.1 | 246.7 | 91.5 | 146.9 | 109.6 | 40.6 | 365.8 | 490 | 595.2 | 140.6 | 272.8 | 299.1 | 114.5 | 249.7 | 286.1
1017 | 855 | -6.8 | 0 | 0 | 363.5 | 284.7 | 280.8 | 276.6 | 300.4 | 51.5 | 19.2 | 79.6 | 3.7 | 261.7 | 6.3 | 155.8 | 115.9 | 196.4 | 366.3 | 465.3 | 221 | 88.6 | 128.8 | 107.1 | 39.4 | 355.9 | 479 | 593.2 | 140.7 | 272.8 | 299 | 114.8 | 249.8 | 285.9
1018 | 856 | -6.8 | 0 | 0 | 360.8 | 283.9 | 279.9 | 275.6 | 299 | 51.4 | 19.2 | 79.4 | 3.8 | 261.8 | 6.4 | 156.4 | 110.9 | 195.2 | 350.1 | 460.7 | 202.3 | 88.1 | 121.4 | 104.4 | 37.3 | 341.5 | 467 | 591.9 | 140.9 | 272.7 | 298.8 | 115.2 | 249.9 | 285.8
1019 | 857 | -6.8 | 0 | 0 | 358.3 | 283 | 279 | 274.7 | 297.4 | 51.4 | 19.2 | 79.2 | 4 | 257.5 | 6.5 | 155.3 | 106 | 194.1 | 313.5 | 456.9 | 186.4 | 84.2 | 105.7 | 103 | 36.5 | 305.5 | 452.7 | 590 | 141.1 | 272.6 | 298.6 | 115.5 | 250 | 285.6
1020 | 858 | -6.8 | 0 | 0 | 355.7 | 282.3 | 278.2 | 273.7 | 295.7 | 51.3 | 19.2 | 79 | 3.8 | 255.7 | 6.4 | 153.3 | 103.7 | 194.4 | 234.6 | 452.5 | 174.9 | 83.6 | 95.5 | 99.8 | 36.4 | 274.4 | 434.7 | 587.9 | 141.3 | 272.6 | 298.4 | 115.9 | 250.1 | 285.5
1021 | 859 | -6.8 | 0 | 0 | 353.4 | 281.5 | 277.6 | 272.6 | 294.2 | 51.3 | 19.2 | 78.8 | 4.2 | 255.5 | 6.1 | 150.6 | 103 | 193.3 | 174.2 | 446.3 | 167 | 80.1 | 86.4 | 98.4 | 35.1 | 247.8 | 410.3 | 585.9 | 141.5 | 272.5 | 298.2 | 116.3 | 250.2 | 285.3
1022 | 860 | -6.8 | 0 | 0 | 351.7 | 280.7 | 276.9 | 271.6 | 292.3 | 51.2 | 19.2 | 78.5 | 3.9 | 252.9 | 5.6 | 148 | 101.7 | 192.7 | 157.6 | 440.9 | 160.2 | 77.4 | 77.8 | 98.5 | 34 | 220.5 | 375.6 | 583.4 | 141.6 | 272.4 | 298 | 116.6 | 250.2 | 285.1
1023 | 861 | -6.8 | 0 | 0 | 350.4 | 279.9 | 276.3 | 270.8 | 290.7 | 51.2 | 19.2 | 78.3 | 3.7 | 240.9 | 5.5 | 145.8 | 100.8 | 195.5 | 155.7 | 436 | 154.4 | 75.6 | 74.5 | 92.9 | 35 | 199.8 | 312.3 | 581.7 | 141.8 | 272.3 | 297.9 | 117 | 250.3 | 285
1024 | 862 | -6.8 | 0 | 0 | 348.8 | 278.9 | 275.6 | 270.1 | 289.5 | 51.2 | 19.2 | 78.1 | 3.8 | 242.9 | 5.4 | 144.1 | 100.2 | 194.9 | 154.2 | 430.8 | 147 | 75.8 | 72.5 | 90.1 | 34.5 | 182.8 | 129.7 | 580.1 | 142 | 272.3 | 297.7 | 117.4 | 250.4 | 284.8
1025 | 863 | -6.8 | 0 | 0 | 346.7 | 278 | 275 | 269.3 | 288.4 | 51.1 | 19.2 | 77.9 | 3.9 | 245.1 | 5.2 | 143.3 | 101 | 194.6 | 153 | 425 | 139.2 | 76.3 | 71.6 | 87.1 | 32.7 | 168.5 | 124.6 | 578.1 | 142.2 | 272.2 | 297.5 | 117.7 | 250.5 | 284.7
1026 | 864 | -6.8 | 0 | 0 | 344.8 | 277 | 274.3 | 268.5 | 286.8 | 51.1 | 19.2 | 77.7 | 3.9 | 248 | 5.2 | 142.4 | 102.6 | 193.9 | 151.4 | 417.4 | 134.2 | 76.4 | 71.3 | 89 | 31.7 | 152.3 | 123 | 576.1 | 142.4 | 272.1 | 297.3 | 118.1 | 250.6 | 284.5
1027 | 865 | -6.8 | 0 | 0 | 343.1 | 276 | 273.6 | 267.8 | 285.1 | 51 | 19.2 | 77.5 | 4.1 | 265 | 4.9 | 140.5 | 101.4 | 192.3 | 149.7 | 409 | 129.5 | 78.2 | 69.8 | 86.4 | 31.9 | 138.8 | 119.6 | 574.7 | 142.6 | 272 | 297.2 | 118.5 | 250.7 | 284.4
1028 | 866 | -6.8 | 0 | 0 | 341.4 | 275.1 | 272.9 | 267.2 | 283.5 | 50.9 | 19.2 | 77.2 | 4.1 | 271.3 | 4.6 | 139.3 | 100.5 | 190.8 | 148.1 | 398.9 | 124.4 | 77 | 67.6 | 88 | 32.2 | 130.9 | 115.1 | 573.1 | 142.9 | 271.9 | 297 | 118.9 | 250.7 | 284.2
1029 | 867 | -6.8 | 0 | 0 | 339.8 | 274 | 272.5 | 266.6 | 282 | 50.8 | 19.2 | 77 | 4.1 | 223.8 | 4.3 | 138.3 | 99.6 | 189.3 | 146.8 | 385.8 | 119.9 | 74.5 | 65.9 | 80.9 | 31.6 | 125.3 | 111.1 | 571.4 | 143 | 271.9 | 296.8 | 119.3 | 250.8 | 284.1
1030 | 868 | -6.8 | 0 | 0 | 338.2 | 272.9 | 271.8 | 266 | 280.7 | 50.8 | 19.2 | 76.8 | 3.7 | 209.5 | 3.8 | 137 | 99.6 | 189.9 | 144.8 | 369.6 | 117.2 | 71.7 | 63.7 | 74.6 | 32 | 117.9 | 107.7 | 569.5 | 143.3 | 271.8 | 296.6 | 119.7 | 250.9 | 283.9
1031 | 869 | -6.8 | 0 | 0 | 336.8 | 271.9 | 271.1 | 265.4 | 279.4 | 50.7 | 19.2 | 76.6 | 4 | 231.5 | 3.7 | 134.8 | 99.4 | 190.6 | 143 | 350.2 | 115 | 70.4 | 62.4 | 74.9 | 32.6 | 118.2 | 104 | 567.6 | 143.5 | 271.7 | 296.4 | 120.1 | 251 | 283.8
1032 | 870 | -6.8 | 0 | 0 | 335.2 | 270.9 | 270.4 | 264.8 | 278.2 | 50.6 | 19.2 | 76.4 | 4.3 | 247.9 | 4.4 | 132.5 | 98.9 | 188.7 | 142.5 | 320.8 | 112.1 | 69.7 | 61.1 | 69.1 | 31.7 | 117.9 | 101.2 | 565.2 | 143.7 | 271.6 | 296.2 | 120.5 | 251.1 | 283.6
1033 | 871 | -6.8 | 0 | 0 | 333.5 | 270 | 269.8 | 264.1 | 277.1 | 50.5 | 19.2 | 76.2 | 4.2 | 257.1 | 5.6 | 131.3 | 98 | 191.8 | 141.7 | 253.5 | 109.3 | 68.4 | 60.4 | 67.2 | 31.9 | 116.9 | 98.4 | 562.5 | 143.9 | 271.5 | 296.1 | 120.9 | 251.1 | 283.5
1034 | 872 | -6.8 | 0 | 0 | 331.5 | 269 | 269.1 | 263.4 | 276.2 | 50.5 | 19.2 | 76 | 4 | 243.2 | 6 | 130.2 | 97.4 | 190.7 | 139.2 | 150.2 | 107 | 67.2 | 60.2 | 68.8 | 32.2 | 115.9 | 95.7 | 559.4 | 144.1 | 271.4 | 295.9 | 121.3 | 251.2 | 283.4
1035 | 873 | -6.8 | 0 | 0 | 329.3 | 268.1 | 268.5 | 262.8 | 275.1 | 50.3 | 19.2 | 75.8 | 3.8 | 237.5 | 6.2 | 129 | 98.5 | 189.9 | 137.7 | 99 | 104.9 | 65.8 | 59.6 | 71.3 | 31.9 | 114.2 | 92.5 | 556.1 | 144.3 | 271.4 | 295.7 | 121.7 | 251.3 | 283.2
1036 | 874 | -6.8 | 0 | 0 | 327.5 | 267.2 | 267.6 | 262.2 | 274 | 50.2 | 19.2 | 75.5 | 4 | 241 | 5.7 | 127.1 | 95.6 | 187.9 | 135.4 | 89.2 | 102.3 | 65.6 | 58.2 | 73.7 | 31.4 | 113.8 | 90.1 | 552.7 | 144.4 | 271.3 | 295.5 | 122 | 251.3 | 283
1037 | 875 | -6.8 | 0 | 0 | 325.9 | 266.2 | 266.7 | 261.4 | 273 | 50.1 | 19.2 | 75.3 | 4.1 | 246.2 | 5.1 | 125.8 | 95.3 | 188.6 | 134.1 | 86 | 99.5 | 65.4 | 56.6 | 73.3 | 31.3 | 113.5 | 88.4 | 548.9 | 144.6 | 271.2 | 295.4 | 122.4 | 251.4 | 282.9
1038 | 876 | -6.8 | 0 | 0 | 324.5 | 265.2 | 266 | 260.9 | 272.1 | 49.9 | 19.2 | 75.1 | 4.2 | 242.8 | 5 | 124.2 | 94.6 | 186.8 | 132.8 | 83.2 | 97 | 67.2 | 54 | 72.5 | 31.9 | 113.8 | 87.2 | 544.6 | 144.8 | 271.1 | 295.2 | 122.8 | 251.5 | 282.7
1039 | 877 | -6.8 | 0 | 0 | 322.9 | 264.3 | 265.4 | 260.4 | 271 | 49.8 | 19.2 | 74.9 | 4 | 242.4 | 5.6 | 122.4 | 94.7 | 183.4 | 132.5 | 80.6 | 94.6 | 66.1 | 53.4 | 66 | 31.4 | 113.5 | 85.6 | 539.3 | 145 | 271 | 295 | 123.2 | 251.5 | 282.6
1040 | 878 | -6.8 | 0 | 0 | 321.3 | 263.7 | 264.7 | 259.9 | 269.8 | 49.7 | 19.2 | 74.7 | 3.6 | 234.4 | 5.6 | 120.9 | 95.3 | 183.2 | 131.5 | 77.7 | 92.7 | 65.6 | 53.1 | 60.8 | 30.4 | 113.1 | 83.8 | 533.8 | 145.2 | 270.9 | 294.8 | 123.5 | 251.6 | 282.4
1041 | 879 | -6.8 | 0 | 0 | 320.1 | 263 | 263.8 | 259.4 | 269 | 49.6 | 19.2 | 74.6 | 4 | 234.9 | 6.2 | 118.9 | 96 | 182.4 | 130.4 | 76.4 | 91 | 65.5 | 52.7 | 61.4 | 29.8 | 112.9 | 81.3 | 527.2 | 145.4 | 270.8 | 294.6 | 123.9 | 251.6 | 282.3
1042 | 880 | -6.8 | 0 | 0 | 318.9 | 262.2 | 263 | 258.8 | 268.2 | 49.5 | 19.2 | 74.4 | 4.3 | 238 | 6.3 | 117.2 | 96.6 | 179.1 | 128.4 | 75.3 | 87.7 | 65.3 | 51.3 | 60.4 | 30 | 112.6 | 79.6 | 519.8 | 145.7 | 270.7 | 294.5 | 124.2 | 251.7 | 282.1
1043 | 881 | -6.8 | 0 | 0 | 317.6 | 261.6 | 262.4 | 258.3 | 267.2 | 49.3 | 19.2 | 74.2 | 4 | 241.7 | 5.7 | 115.4 | 96.7 | 174.4 | 126.3 | 73.9 | 84.1 | 63.7 | 51 | 64.4 | 30.2 | 111.6 | 78.3 | 511.8 | 145.9 | 270.6 | 294.3 | 124.6 | 251.7 | 282
1044 | 882 | -6.8 | 0 | 0 | 316.4 | 261 | 261.4 | 257.7 | 266.2 | 49.1 | 19.2 | 74.1 | 4.1 | 244.6 | 5.6 | 114.1 | 96.6 | 173.3 | 125.5 | 72.5 | 81.9 | 63.7 | 51.2 | 64.9 | 29.9 | 111.3 | 77.1 | 503.2 | 146.1 | 270.5 | 294.1 | 124.9 | 251.7 | 281.8
1045 | 883 | -6.8 | 0 | 0 | 315.4 | 260.4 | 260.4 | 257.3 | 265.2 | 48.9 | 19.2 | 73.9 | 3.9 | 246.8 | 5.6 | 114.2 | 95.3 | 175.2 | 124 | 71.7 | 80 | 62.1 | 50.3 | 58.4 | 29.4 | 111.5 | 75.7 | 494.4 | 146.3 | 270.4 | 293.9 | 125.2 | 251.8 | 281.6
1046 | 884 | -6.8 | 0 | 0 | 314.5 | 259.9 | 259.6 | 256.8 | 264.2 | 48.8 | 19.2 | 73.8 | 3.8 | 250.7 | 5.5 | 111.7 | 94.3 | 174.6 | 121.9 | 70.2 | 78.2 | 62.6 | 50.9 | 57.9 | 28.7 | 110.8 | 74.5 | 480.5 | 146.5 | 270.3 | 293.7 | 125.6 | 251.8 | 281.5
1047 | 885 | -6.8 | 0 | 0 | 313.4 | 259.2 | 258.9 | 256.3 | 263 | 48.7 | 19.2 | 73.6 | 3.7 | 240 | 5 | 108.4 | 93.8 | 171 | 119.8 | 68.9 | 76.6 | 61.3 | 49.5 | 60 | 29.2 | 110.5 | 73.4 | 458.5 | 146.8 | 270.2 | 293.6 | 125.9 | 251.8 | 281.3
1048 | 886 | -6.8 | 0 | 0 | 312.2 | 258.4 | 258.3 | 255.7 | 262.1 | 48.6 | 19.2 | 73.4 | 3.5 | 237.2 | 4.6 | 106.1 | 93.1 | 170.6 | 118.2 | 67.4 | 74.7 | 62 | 47.3 | 63.9 | 29.3 | 110.6 | 72.3 | 435.1 | 147 | 270.1 | 293.4 | 126.2 | 251.9 | 281.2
1049 | 887 | -6.8 | 0 | 0 | 310.8 | 257.6 | 257.7 | 255.2 | 261.1 | 48.5 | 19.2 | 73.3 | 3.8 | 250.8 | 4.2 | 103.8 | 91.7 | 171.9 | 116.1 | 66.8 | 73.6 | 60.8 | 46.4 | 62.8 | 29.1 | 110.6 | 71.3 | 408.6 | 147.2 | 270 | 293.2 | 126.6 | 251.9 | 281
1050 | 888 | -6.8 | 0 | 0 | 309.4 | 257 | 257 | 254.6 | 260 | 48.4 | 19.2 | 73.1 | 3.9 | 241.9 | 3.8 | 100.4 | 90.5 | 168.9 | 113.8 | 66 | 71.8 | 59 | 48.6 | 56.6 | 28.4 | 110 | 70.2 | 377 | 147.4 | 269.9 | 293 | 126.9 | 251.9 | 280.8
1051 | 889 | -6.8 | 0 | 0 | 308.3 | 256.3 | 256.4 | 254 | 259 | 48.3 | 19.2 | 72.9 | 3.8 | 218.3 | 3.6 | 98.2 | 87.7 | 170.1 | 111.8 | 65.3 | 69.8 | 56.1 | 45.3 | 54.5 | 28.5 | 104.3 | 69.5 | 328.9 | 147.7 | 269.8 | 292.8 | 127.2 | 251.9 | 280.7
1052 | 890 | -6.8 | 0 | 0 | 307 | 255.8 | 255.8 | 253.4 | 258.1 | 48.1 | 19.2 | 72.8 | 3.7 | 231.5 | 4 | 95.6 | 85.8 | 167.8 | 109.3 | 64.5 | 68.2 | 54 | 44.8 | 54.8 | 27.5 | 105.2 | 68.7 | 230.7 | 147.9 | 269.7 | 292.6 | 127.6 | 251.9 | 280.5
1053 | 891 | -6.8 | 0 | 0 | 305.7 | 255.2 | 255.1 | 252.8 | 256.9 | 47.9 | 19.2 | 72.6 | 3.8 | 243.6 | 4.2 | 94.1 | 82.7 | 168.7 | 108.1 | 63.6 | 67.2 | 51.2 | 46.2 | 53 | 27.7 | 106.2 | 67.8 | 128.9 | 148.1 | 269.6 | 292.4 | 127.9 | 251.9 | 280.3
1054 | 892 | -6.8 | 0 | 0 | 304.7 | 254.6 | 254.3 | 252.2 | 255.7 | 47.8 | 19.2 | 72.5 | 3.8 | 232.4 | 4.3 | 91.5 | 81.1 | 165 | 106.1 | 62.4 | 66.1 | 50.1 | 44.1 | 52.6 | 27.8 | 106.4 | 67.1 | 111.7 | 148.4 | 269.5 | 292.3 | 128.2 | 251.9 | 280.2
1055 | 893 | -6.8 | 0 | 0 | 304 | 254 | 253.7 | 251.5 | 254.5 | 47.7 | 19.2 | 72.3 | 3.7 | 232.2 | 4.5 | 89.6 | 81.1 | 161.8 | 104.3 | 61.5 | 65.1 | 48.7 | 44.4 | 51.3 | 27.2 | 106.7 | 66.7 | 106.7 | 148.6 | 269.4 | 292.1 | 128.5 | 251.8 | 280
1056 | 894 | -6.8 | 0 | 0 | 303.4 | 253.3 | 252.9 | 250.9 | 253.4 | 47.6 | 19.2 | 72.2 | 3.6 | 251.3 | 5.2 | 87.9 | 80.6 | 158.2 | 103.2 | 60.3 | 62.5 | 48 | 44 | 49.7 | 27.5 | 106.8 | 65.7 | 103.3 | 148.8 | 269.2 | 291.9 | 128.8 | 251.8 | 279.9
1057 | 895 | -6.8 | 0 | 0 | 302.6 | 252.5 | 252.2 | 250.3 | 252.3 | 47.5 | 19.2 | 72 | 3.3 | 247.5 | 6.1 | 86.7 | 79.6 | 159.6 | 101.8 | 58.9 | 56.9 | 46.7 | 41.1 | 49.3 | 27.7 | 106.7 | 64.8 | 101.7 | 149.1 | 269.1 | 291.7 | 129.2 | 251.8 | 279.7
1058 | 896 | -6.8 | 0 | 0 | 301.7 | 251.8 | 251.6 | 249.6 | 251.2 | 47.4 | 19.2 | 71.9 | 3.5 | 248.3 | 6.2 | 85.9 | 78.1 | 159 | 100.2 | 58 | 56.2 | 47.1 | 43.7 | 47.2 | 27.8 | 106.5 | 64 | 100.5 | 149.3 | 269 | 291.5 | 129.5 | 251.8 | 279.5
1059 | 897 | -6.8 | 0 | 0 | 300.7 | 251.2 | 251 | 249 | 250 | 47.4 | 19.2 | 71.8 | 3.6 | 245 | 6.2 | 84.9 | 76.2 | 157.4 | 90.2 | 57.1 | 54.5 | 46 | 41.3 | 46.7 | 28 | 105 | 62.8 | 99.1 | 149.6 | 268.9 | 291.3 | 129.8 | 251.8 | 279.4
1060 | 898 | -6.8 | 0 | 0 | 299.9 | 250.6 | 250.4 | 248.5 | 249 | 47.4 | 19.2 | 71.6 | 3.8 | 254.9 | 6.4 | 73.9 | 76.1 | 152.5 | 80.1 | 56.3 | 53.3 | 43.1 | 39.9 | 44.5 | 28.7 | 105 | 59 | 98.1 | 149.8 | 268.8 | 291.1 | 130.1 | 251.7 | 279.2
1061 | 899 | -6.8 | 0 | 0 | 299.2 | 249.9 | 249.7 | 247.8 | 248 | 47.3 | 19.2 | 71.5 | 3.3 | 247.3 | 6 | 69.1 | 76.1 | 151.5 | 73.1 | 55.6 | 56.3 | 42.4 | 43.9 | 43.3 | 29.2 | 105.1 | 56.6 | 97.9 | 150 | 268.7 | 290.9 | 130.4 | 251.7 | 279
1062 | 900 | -6.8 | 0 | 0 | 298.5 | 249.3 | 249 | 247.2 | 247.2 | 47.2 | 19.2 | 71.3 | 3.3 | 243.9 | 5.4 | 67.9 | 76.3 | 137.5 | 70.9 | 54.8 | 58 | 42.6 | 40 | 43 | 29 | 105.1 | 54.5 | 97.4 | 150.3 | 268.5 | 290.7 | 130.7 | 251.6 | 278.9
1063 | 901 | -6.8 | 0 | 0 | 297.5 | 248.6 | 248.5 | 246.6 | 246.3 | 47.1 | 19.2 | 71.2 | 3.4 | 247 | 4.8 | 67.7 | 75.4 | 134.6 | 72.2 | 54 | 57.4 | 42.6 | 39.7 | 42.3 | 28.7 | 104.6 | 54.2 | 97 | 150.5 | 268.4 | 290.5 | 131 | 251.6 | 278.7
1064 | 902 | -6.8 | 0 | 0 | 296.5 | 247.8 | 247.8 | 246 | 245.5 | 47.1 | 19.2 | 71 | 3.5 | 241.9 | 4.6 | 66.7 | 75 | 132.4 | 73.4 | 53.4 | 56 | 42.1 | 43.4 | 40.7 | 29.6 | 103.8 | 54.1 | 96.9 | 150.8 | 268.3 | 290.4 | 131.3 | 251.6 | 278.5
1065 | 903 | -6.8 | 0 | 0 | 295.6 | 247.1 | 247.2 | 245.3 | 244.6 | 47 | 19.2 | 70.9 | 3.4 | 238.6 | 4.4 | 66 | 75 | 129 | 74 | 52.7 | 57.2 | 42.7 | 37.6 | 40.5 | 29.2 | 102.8 | 54.2 | 96.5 | 151 | 268.2 | 290.2 | 131.7 | 251.5 | 278.4
1066 | 904 | -6.8 | 0 | 0 | 294.8 | 246.4 | 246.6 | 244.6 | 243.5 | 47 | 19.2 | 70.8 | 3.5 | 235.6 | 4.3 | 65.9 | 74.7 | 127 | 74 | 51.9 | 58.1 | 44 | 39.4 | 38.6 | 29 | 103.4 | 53.9 | 96.1 | 151.3 | 268 | 290 | 132 | 251.5 | 278.2
1067 | 905 | -6.8 | 0 | 0 | 293.9 | 245.8 | 246 | 244 | 242.5 | 46.9 | 19.2 | 70.6 | 3.6 | 226.8 | 4.1 | 66.1 | 74.8 | 125.2 | 74.6 | 51.2 | 58.1 | 44.2 | 42.7 | 39.9 | 28.7 | 103.5 | 53.8 | 95.9 | 151.5 | 267.8 | 289.8 | 132.3 | 251.4 | 278.1
1068 | 906 | -6.8 | 0 | 0 | 293.1 | 245.2 | 245.4 | 243.4 | 241.6 | 46.9 | 19.2 | 70.5 | 3.4 | 213.1 | 3.5 | 66.9 | 73.6 | 122.8 | 75.4 | 50.4 | 57.5 | 44.4 | 37.9 | 40.3 | 28.2 | 103.5 | 53.7 | 95.7 | 151.8 | 267.5 | 289.6 | 132.6 | 251.4 | 277.9
1069 | 907 | -6.8 | 0 | 0 | 292.4 | 244.5 | 244.9 | 242.9 | 240.8 | 46.8 | 19.2 | 70.4 | 3.2 | 207.8 | 3.5 | 66.8 | 68.7 | 121.6 | 71.8 | 49.8 | 57.2 | 44.9 | 40.2 | 40.1 | 28.1 | 103.5 | 53.4 | 95.5 | 152 | 267.4 | 289.4 | 132.9 | 251.4 | 277.7
1070 | 908 | -6.8 | 0 | 0 | 291.6 | 243.9 | 244.3 | 242.2 | 240 | 46.7 | 19.2 | 70.2 | 3.5 | 209.2 | 4 | 66.2 | 65 | 122.7 | 70.8 | 49 | 56.7 | 45 | 39.9 | 40.3 | 28.8 | 102.9 | 53 | 95.3 | 152.3 | 267.2 | 289.2 | 133.2 | 251.3 | 277.6
1071 | 909 | -6.8 | 0 | 0 | 290.7 | 243.2 | 243.7 | 241.5 | 239.2 | 46.7 | 19.2 | 70.1 | 3.6 | 228.8 | 4.3 | 66.4 | 67.7 | 119 | 68.7 | 48.1 | 55.1 | 44.2 | 37.2 | 41.2 | 29 | 102.3 | 52.3 | 95.1 | 152.5 | 267.1 | 289 | 133.5 | 251.3 | 277.4
1072 | 910 | -6.8 | 0 | 0 | 289.6 | 242.6 | 243.1 | 241 | 238.4 | 46.6 | 19.2 | 69.9 | 3.3 | 224.1 | 4.5 | 66 | 69.4 | 116.7 | 68 | 47 | 51.1 | 43.6 | 41.9 | 41.2 | 29.2 | 102.4 | 51.7 | 95.2 | 152.8 | 266.9 | 288.8 | 133.8 | 251.2 | 277.3
1073 | 911 | -6.8 | 0 | 0 | 288.8 | 241.9 | 242.5 | 240.4 | 237.7 | 46.5 | 19.2 | 69.8 | 3.3 | 207.5 | 4.7 | 65.4 | 69.3 | 114.8 | 67.6 | 45.9 | 47.7 | 44.5 | 38.8 | 40.7 | 29.2 | 102 | 51.2 | 95 | 153 | 266.8 | 288.7 | 134.1 | 251.2 | 277.1
1074 | 912 | -6.8 | 0 | 0 | 288.2 | 241.4 | 241.9 | 239.9 | 236.9 | 46.4 | 19.2 | 69.7 | 3.3 | 212.4 | 4.6 | 64.8 | 63.8 | 114.7 | 67.4 | 45.1 | 46.2 | 44.8 | 36.8 | 41.1 | 29.3 | 102.1 | 48.6 | 95.1 | 153.3 | 266.7 | 288.5 | 134.4 | 251.1 | 276.9
1075 | 913 | -6.8 | 0 | 0 | 287.4 | 240.8 | 241.3 | 239.4 | 236.1 | 46.2 | 19.2 | 69.6 | 3.2 | 225.2 | 4.1 | 62.6 | 57.3 | 113 | 66.2 | 44.5 | 45 | 45 | 43 | 42 | 28.9 | 102.1 | 47.1 | 94.9 | 153.5 | 266.5 | 288.3 | 134.7 | 251.1 | 276.8
1076 | 914 | -6.8 | 0 | 0 | 286.6 | 240.3 | 240.7 | 238.9 | 235.5 | 46.1 | 19.2 | 69.5 | 3.5 | 239.2 | 3.6 | 63.2 | 60.8 | 109.5 | 66.5 | 43.7 | 44 | 45.2 | 37 | 41.8 | 27.9 | 101.1 | 48.4 | 94.7 | 153.8 | 266.4 | 288.1 | 135 | 251 | 276.6
1077 | 915 | -6.8 | 0 | 0 | 285.8 | 239.8 | 240.1 | 238.3 | 234.9 | 46.1 | 19.2 | 69.3 | 3.5 | 237.2 | 3.1 | 60.3 | 64.6 | 107.5 | 64.5 | 42.7 | 43.4 | 44.9 | 36.7 | 41.6 | 27.9 | 101.3 | 49 | 94.6 | 154 | 266.3 | 287.9 | 135.3 | 251 | 276.4
1078 | 916 | -6.8 | 0 | 0 | 285.2 | 239.2 | 239.6 | 237.9 | 234.3 | 46.2 | 19.3 | 69.2 | 3.6 | 234.4 | 3.2 | 54 | 63.8 | 104.9 | 61.7 | 41.7 | 42 | 44.2 | 42.1 | 41.8 | 28.8 | 101.1 | 48 | 94.5 | 154.3 | 266.1 | 287.7 | 135.6 | 250.9 | 276.3
1079 | 917 | -6.8 | 0 | 0 | 284.6 | 238.6 | 239 | 237.4 | 233.6 | 46.1 | 19.3 | 69.1 | 3.7 | 233.3 | 3.5 | 53.1 | 64.2 | 104 | 60.4 | 41 | 41.1 | 43.3 | 35.6 | 40.8 | 28.7 | 100.9 | 47.2 | 94.5 | 154.5 | 266 | 287.5 | 135.9 | 250.8 | 276.1
1080 | 918 | -6.8 | 0 | 0 | 283.7 | 238.1 | 238.5 | 236.9 | 233.1 | 46.1 | 19.3 | 68.9 | 3.6 | 223.3 | 3.4 | 55.4 | 64.6 | 103.9 | 59.5 | 40.5 | 41.1 | 42.6 | 35.1 | 40.3 | 28.9 | 100.8 | 46.7 | 94.5 | 154.8 | 265.9 | 287.4 | 136.2 | 250.8 | 276
1081 | 919 | -6.8 | 0 | 0 | 283 | 237.6 | 237.9 | 236.3 | 232.6 | 46.1 | 19.3 | 68.8 | 3.2 | 215 | 3.3 | 52.5 | 66.3 | 103.5 | 59.6 | 39.9 | 40.7 | 43 | 35.4 | 39.9 | 28.8 | 100.1 | 46.6 | 94.4 | 155.1 | 265.8 | 287.2 | 136.5 | 250.7 | 275.8
1082 | 920 | -6.8 | 0 | 0 | 282.5 | 237 | 237.3 | 235.8 | 232.1 | 45.9 | 19.3 | 68.7 | 3.3 | 231.4 | 3.2 | 50.2 | 67.9 | 101.2 | 61.3 | 39.5 | 40.7 | 41.5 | 35.3 | 39.9 | 29.1 | 99.7 | 46.2 | 94.3 | 155.3 | 265.7 | 287 | 136.8 | 250.6 | 275.6
1083 | 921 | -6.8 | 0 | 0 | 282 | 236.5 | 236.8 | 235.3 | 231.7 | 45.8 | 19.3 | 68.5 | 3.6 | 232.9 | 3.3 | 48.4 | 68.2 | 98.7 | 62.8 | 39 | 40.5 | 42.5 | 34.9 | 38.9 | 29.8 | 99.7 | 45.4 | 94.3 | 155.6 | 265.5 | 286.8 | 137 | 250.6 | 275.5
1084 | 922 | -6.8 | 0 | 0 | 281.5 | 236 | 236.3 | 234.8 | 231.2 | 45.7 | 19.3 | 68.4 | 3.4 | 205.9 | 3.5 | 50.1 | 67 | 99.9 | 65.9 | 38.6 | 40 | 42.4 | 34.4 | 36.4 | 30.7 | 95.3 | 44.7 | 94.2 | 155.8 | 265.4 | 286.6 | 137.3 | 250.5 | 275.3
1085 | 923 | -6.8 | 0 | 0 | 281.1 | 235.5 | 235.7 | 234.4 | 230.6 | 45.6 | 19.3 | 68.3 | 3.7 | 228.4 | 3.5 | 52.4 | 65.9 | 98.6 | 64.4 | 38 | 39.8 | 42.4 | 34.3 | 36.6 | 31.2 | 97.5 | 44.8 | 94.3 | 156.1 | 265.3 | 286.4 | 137.6 | 250.5 | 275.2
1086 | 924 | -6.8 | 0 | 0 | 280.3 | 234.9 | 235.1 | 233.9 | 229.9 | 45.6 | 19.3 | 68.2 | 3.5 | 255 | 3.9 | 53 | 64.3 | 99.6 | 60.4 | 37.3 | 39.5 | 41.5 | 34.2 | 36.8 | 31.2 | 97.2 | 45.4 | 94.4 | 156.3 | 265.1 | 286.3 | 137.9 | 250.4 | 275
1087 | 925 | -6.8 | 0 | 0 | 279.4 | 234.4 | 234.6 | 233.4 | 229.3 | 45.5 | 19.3 | 68 | 3.7 | 240.1 | 4.1 | 54.9 | 66.4 | 99.8 | 61.3 | 37.4 | 39.5 | 41.6 | 34.1 | 36.7 | 30.7 | 97.4 | 45.5 | 94.4 | 156.6 | 264.9 | 286.1 | 138.2 | 250.3 | 274.9
1088 | 926 | -6.8 | 0 | 0 | 278.7 | 233.9 | 234.2 | 233 | 228.6 | 45.4 | 19.3 | 67.9 | 4 | 233.6 | 4.4 | 56.4 | 67.8 | 102.3 | 62.7 | 37.2 | 39.4 | 41 | 34 | 35.2 | 30.6 | 97.5 | 45.4 | 94.5 | 156.8 | 264.7 | 285.9 | 138.5 | 250.3 | 274.7
1089 | 927 | -6.8 | 0 | 0 | 278.2 | 233.4 | 233.8 | 232.5 | 228 | 45.4 | 19.3 | 67.8 | 3.7 | 232.8 | 4.2 | 56.7 | 68.6 | 103.9 | 63.5 | 36.8 | 39.3 | 40.7 | 33.9 | 35.8 | 29.3 | 96.9 | 44.9 | 94.4 | 157.1 | 264.4 | 285.7 | 138.8 | 250.2 | 274.6
1090 | 928 | -6.8 | 0 | 0 | 277.9 | 233 | 233.4 | 232.1 | 227.4 | 45.3 | 19.3 | 67.6 | 4.2 | 222.6 | 4 | 54.9 | 68.4 | 103.4 | 64.4 | 36.5 | 39.2 | 40.9 | 33.7 | 36.2 | 28.7 | 96.8 | 45.6 | 94.1 | 157.3 | 264.1 | 285.5 | 139.1 | 250.2 | 274.4
1091 | 929 | -6.8 | 0 | 0 | 277.4 | 232.6 | 232.9 | 231.6 | 226.9 | 45.2 | 19.3 | 67.5 | 3.9 | 223.3 | 4.2 | 53 | 66.8 | 100.2 | 64.3 | 36.3 | 38.8 | 41.4 | 33.8 | 36.5 | 28.7 | 96.5 | 46.5 | 94 | 157.6 | 263.9 | 285.4 | 139.3 | 250.1 | 274.3
1092 | 930 | -6.8 | 0 | 0 | 277 | 232.2 | 232.4 | 231.2 | 226.4 | 45.1 | 19.3 | 67.3 | 4.1 | 227.3 | 4 | 52.8 | 60 | 97.3 | 64.2 | 36.1 | 38.2 | 41.7 | 33.6 | 36.6 | 29.3 | 95.5 | 47.3 | 94 | 157.8 | 263.7 | 285.2 | 139.6 | 250.1 | 274.1
1093 | 931 | -6.8 | 0 | 0 | 276.6 | 231.8 | 231.8 | 230.7 | 225.9 | 45 | 19.3 | 67.2 | 3.9 | 241.8 | 4 | 50.8 | 56.4 | 91.3 | 62.3 | 35.8 | 37.9 | 43.8 | 33 | 38.2 | 30.1 | 95.9 | 47.1 | 93.9 | 158.1 | 263.6 | 285 | 139.9 | 250 | 274
1094 | 932 | -6.8 | 0 | 0 | 276.1 | 231.5 | 231.4 | 230.2 | 225.3 | 44.9 | 19.3 | 67.1 | 4 | 237.6 | 3.7 | 47 | 60.1 | 88.9 | 61.2 | 35.5 | 37.7 | 45.2 | 32 | 38 | 30.1 | 96.2 | 46.7 | 93.6 | 158.4 | 263.4 | 284.8 | 140.2 | 250 | 273.8
1095 | 933 | -6.8 | 0 | 0 | 275.5 | 231.1 | 230.9 | 229.7 | 224.7 | 44.9 | 19.3 | 66.9 | 3.8 | 216.3 | 3.6 | 45 | 58 | 89.7 | 57.8 | 35.2 | 37.3 | 45.2 | 31.9 | 35.4 | 30.4 | 96 | 46.2 | 93.5 | 158.6 | 263.2 | 284.6 | 140.5 | 249.9 | 273.7
1096 | 934 | -6.8 | 0 | 0 | 275 | 230.8 | 230.5 | 229.3 | 224.1 | 44.8 | 19.3 | 66.8 | 3.5 | 229.3 | 3.8 | 44.7 | 58.1 | 89.3 | 58.3 | 34.9 | 36.9 | 43.4 | 31.9 | 34.3 | 30.5 | 96.2 | 46.3 | 93.4 | 158.9 | 263.1 | 284.5 | 140.7 | 249.8 | 273.5
1097 | 935 | -6.8 | 0 | 0 | 274.4 | 230.4 | 229.9 | 228.9 | 223.5 | 44.8 | 19.3 | 66.7 | 3.4 | 241.7 | 5.3 | 44.4 | 58.3 | 88.4 | 60.6 | 34.6 | 36.7 | 41.4 | 31.9 | 33.8 | 29.9 | 95.6 | 46.2 | 93.4 | 159.1 | 262.9 | 284.3 | 141 | 249.8 | 273.4
1098 | 936 | -6.8 | 0 | 0 | 273.6 | 230 | 229.5 | 228.6 | 223 | 44.7 | 19.3 | 66.5 | 2.7 | 236.6 | 5.8 | 45.2 | 58.2 | 87.1 | 61.6 | 34.5 | 36.8 | 40.7 | 31.9 | 33 | 29.8 | 94.4 | 46.1 | 93.4 | 159.4 | 262.6 | 284.1 | 141.3 | 249.7 | 273.2
1099 | 937 | -6.8 | 0 | 0 | 273 | 229.5 | 229 | 228.3 | 222.7 | 44.7 | 19.3 | 66.4 | 2.3 | 219.2 | 5.9 | 47.2 | 60.7 | 87.4 | 62.9 | 34.4 | 36.9 | 39.3 | 31.7 | 33.2 | 29.4 | 94.4 | 45.7 | 92.5 | 159.6 | 262.3 | 284 | 141.6 | 249.7 | 273.1
1100 | 938 | -6.8 | 0 | 0 | 272.5 | 229.1 | 228.6 | 227.9 | 222.2 | 44.7 | 19.3 | 66.2 | 2.6 | 253.7 | 6.9 | 47.1 | 59.3 | 86.5 | 64.1 | 34.4 | 36.8 | 39.1 | 31.4 | 33.8 | 29.6 | 94.2 | 46.3 | 92.2 | 159.9 | 262 | 283.8 | 141.9 | 249.6 | 273
1101 | 939 | -6.8 | 0 | 0 | 271.9 | 228.7 | 228.2 | 227.4 | 221.9 | 44.6 | 19.3 | 66.1 | 2.7 | 223.3 | 7.7 | 45.4 | 57.5 | 83.9 | 62.6 | 34.3 | 36.6 | 42.1 | 31.4 | 34 | 29.5 | 93.7 | 46.2 | 91.9 | 160.1 | 261.8 | 283.6 | 142.1 | 249.6 | 272.8
1102 | 940 | -6.8 | 0 | 0 | 271.5 | 228.3 | 227.8 | 226.8 | 221.6 | 44.5 | 19.3 | 66 | 3.5 | 228.9 | 8.4 | 46.4 | 57.6 | 84.3 | 63.2 | 34.2 | 36.5 | 43.4 | 31.2 | 34.4 | 29.6 | 94.1 | 45.7 | 91.6 | 160.4 | 261.5 | 283.4 | 142.4 | 249.5 | 272.7
1103 | 941 | -6.8 | 0 | 0 | 270.9 | 227.8 | 227.3 | 226.4 | 221.1 | 44.4 | 19.3 | 65.9 | 3.7 | 223 | 8.2 | 49.1 | 58 | 81.7 | 62.6 | 34 | 36.4 | 42.8 | 30.9 | 34.9 | 29.3 | 93.6 | 45.4 | 91.9 | 160.6 | 261.3 | 283.2 | 142.7 | 249.5 | 272.5
1104 | 942 | -6.8 | 0 | 0 | 270.2 | 227.3 | 226.8 | 226.1 | 220.6 | 44.3 | 19.3 | 65.8 | 3.7 | 223 | 7.5 | 49.6 | 57.8 | 80.8 | 63.1 | 33.9 | 36.2 | 42.2 | 30.9 | 35.1 | 29.3 | 94.1 | 45.2 | 91.9 | 160.9 | 261 | 283 | 142.9 | 249.4 | 272.4
1105 | 943 | -6.8 | 0 | 0 | 269.4 | 226.8 | 226.4 | 225.6 | 220 | 44.3 | 19.3 | 65.7 | 3.8 | 223.9 | 6.6 | 49.7 | 61 | 80.5 | 63.2 | 33.7 | 35.9 | 41.4 | 30.7 | 34.7 | 29.2 | 94 | 45.6 | 91.7 | 161.1 | 260.8 | 282.8 | 143.2 | 249.4 | 272.2
1106 | 944 | -6.8 | 0 | 0 | 268.8 | 226.4 | 226 | 225.2 | 219.5 | 44.2 | 19.3 | 65.5 | 3.6 | 215.5 | 6.1 | 50.4 | 63.4 | 80.2 | 63.8 | 33.6 | 35.7 | 40.1 | 30.5 | 34.4 | 28.6 | 94 | 45.8 | 91.8 | 161.4 | 260.5 | 282.7 | 143.5 | 249.3 | 272.1
1107 | 945 | -6.8 | 0 | 0 | 268.1 | 226 | 225.7 | 224.8 | 218.9 | 44.1 | 19.3 | 65.4 | 3.5 | 198.6 | 5.3 | 50.7 | 61.9 | 80.8 | 65 | 33.4 | 35.6 | 39.4 | 30.7 | 34.7 | 28.4 | 94.1 | 46 | 91.7 | 161.6 | 260.3 | 282.5 | 143.7 | 249.2 | 271.9
1108 | 946 | -6.8 | 0 | 0 | 267.5 | 225.7 | 225.2 | 224.3 | 218.4 | 44 | 19.3 | 65.3 | 3.3 | 221.7 | 4.4 | 50.6 | 61.9 | 81.6 | 63.8 | 33.3 | 35.7 | 38.6 | 30.6 | 35.1 | 28.5 | 94.7 | 45.8 | 91.4 | 161.9 | 260 | 282.3 | 144 | 249.1 | 271.8
1109 | 947 | -6.8 | 0 | 0 | 267 | 225.5 | 224.7 | 223.8 | 217.9 | 43.9 | 19.3 | 65.2 | 3.1 | 243.9 | 4.3 | 51.7 | 63.8 | 80.5 | 62 | 33.1 | 35.6 | 38.9 | 30.5 | 35.4 | 28.6 | 94.7 | 45.3 | 91.2 | 162.1 | 259.8 | 282.2 | 144.3 | 249.1 | 271.6
1110 | 948 | -6.8 | 0 | 0 | 266.5 | 225.2 | 224.3 | 223.4 | 217.4 | 43.9 | 19.3 | 65.1 | 3.4 | 237 | 4.1 | 52.5 | 65.1 | 79.1 | 61.3 | 33 | 35.7 | 38.5 | 31 | 35.8 | 28.6 | 95 | 45.3 | 91.5 | 162.4 | 259.5 | 282 | 144.5 | 249 | 271.5
1111 | 949 | -6.8 | 0 | 0 | 266.1 | 224.9 | 223.9 | 222.9 | 216.9 | 43.8 | 19.3 | 64.9 | 3.5 | 258.5 | 3.7 | 51.3 | 66.6 | 80.1 | 61.2 | 32.9 | 35.6 | 38.3 | 30.7 | 36.3 | 28.5 | 95.3 | 44.8 | 91.3 | 162.6 | 259.3 | 281.8 | 144.8 | 248.9 | 271.3
1112 | 950 | -6.8 | 0 | 0 | 265.7 | 224.4 | 223.5 | 222.5 | 216.3 | 43.7 | 19.3 | 64.8 | 3.4 | 266.7 | 3.2 | 51.3 | 67.5 | 79.7 | 60.9 | 32.8 | 35.5 | 38.5 | 30.6 | 36 | 28.6 | 95.3 | 44.6 | 91.1 | 162.9 | 259 | 281.6 | 145.1 | 248.9 | 271.2
1113 | 951 | -6.8 | 0 | 0 | 265.3 | 223.9 | 223 | 222.2 | 215.7 | 43.6 | 19.3 | 64.7 | 3.3 | 248.4 | 3.1 | 52.4 | 68.4 | 79.8 | 61 | 32.6 | 35.4 | 38.6 | 30.6 | 35.7 | 27.9 | 95.2 | 45.5 | 91.3 | 163.1 | 258.8 | 281.3 | 145.3 | 248.8 | 271
1114 | 952 | -6.8 | 0 | 0 | 264.9 | 223.5 | 222.6 | 221.8 | 215.1 | 43.5 | 19.3 | 64.6 | 3.3 | 239.2 | 3.4 | 52.5 | 68.6 | 79.8 | 60.5 | 32.5 | 35.2 | 38.1 | 30.1 | 35.6 | 27.5 | 95.3 | 45.8 | 91.7 | 163.3 | 258.5 | 281.2 | 145.6 | 248.7 | 270.8
1115 | 953 | -6.8 | 0 | 0 | 264.5 | 223.1 | 222.3 | 221.3 | 214.6 | 43.5 | 19.3 | 64.4 | 3 | 243.4 | 3.8 | 53.4 | 63.8 | 71.7 | 61.1 | 32.2 | 35.4 | 37.8 | 30.3 | 35.5 | 28.4 | 95.3 | 45.1 | 91.9 | 163.6 | 258.3 | 281 | 145.9 | 248.6 | 270.7
1116 | 954 | -6.8 | 0 | 0 | 264 | 222.8 | 221.8 | 220.9 | 214.2 | 43.4 | 19.3 | 64.3 | 3 | 219.2 | 3.5 | 53.9 | 63 | 69.7 | 61.2 | 32 | 35.4 | 37.8 | 30.4 | 35.1 | 28.2 | 95.3 | 45.4 | 91.7 | 163.8 | 258.1 | 280.8 | 146.1 | 248.6 | 270.6
1117 | 955 | -6.8 | 0 | 0 | 263.4 | 222.4 | 221.4 | 220.6 | 213.8 | 43.3 | 19.3 | 64.2 | 3.5 | 229 | 3.6 | 54.2 | 65 | 69.5 | 57.1 | 31.9 | 35.4 | 37.8 | 29.9 | 34.8 | 28 | 95.6 | 45.7 | 91.4 | 164.1 | 257.8 | 280.7 | 146.4 | 248.5 | 270.4
1118 | 956 | -6.8 | 0 | 0 | 262.8 | 222 | 221 | 220.2 | 213.3 | 43.2 | 19.3 | 64.1 | 3.5 | 248.3 | 4 | 54.2 | 66.2 | 66.1 | 55.7 | 31.7 | 35.2 | 37.9 | 30 | 35 | 28.2 | 96.1 | 43.8 | 91 | 164.3 | 257.6 | 280.5 | 146.6 | 248.4 | 270.3
1119 | 957 | -6.8 | 0 | 0 | 262.2 | 221.6 | 220.6 | 219.7 | 212.8 | 43.1 | 19.3 | 63.9 | 3.2 | 246.2 | 4.4 | 54.2 | 67.2 | 65.1 | 59.8 | 31.5 | 35 | 37.9 | 29.9 | 34.7 | 27.8 | 95.6 | 43.3 | 90.8 | 164.5 | 257.4 | 280.3 | 146.9 | 248.4 | 270.1
1120 | 958 | -6.8 | 0 | 0 | 261.6 | 221.2 | 220.1 | 219.3 | 212.3 | 43 | 19.3 | 63.8 | 3.1 | 230.4 | 6.2 | 53.5 | 67.4 | 65.3 | 61.2 | 31.4 | 35 | 37.3 | 29.9 | 34.5 | 27.6 | 96 | 42.8 | 90.6 | 164.8 | 257.2 | 280.1 | 147.1 | 248.3 | 270
1121 | 959 | -6.8 | 0 | 0 | 261.1 | 220.9 | 219.7 | 218.9 | 211.8 | 42.9 | 19.3 | 63.7 | 3.1 | 238.8 | 7 | 50.3 | 68.5 | 64.3 | 60.6 | 31.3 | 34.9 | 37.3 | 29.8 | 34.9 | 28 | 95.6 | 42.4 | 90.4 | 165 | 257 | 280 | 147.4 | 248.2 | 269.8
1122 | 960 | -6.8 | 0 | 0 | 260.5 | 220.5 | 219.4 | 218.5 | 211.4 | 42.9 | 19.3 | 63.6 | 3.3 | 243.8 | 7.3 | 52.2 | 69.3 | 66.2 | 62 | 31.1 | 34.7 | 37.8 | 29.4 | 34.5 | 27.8 | 94.9 | 42 | 90.4 | 165.2 | 256.8 | 279.8 | 147.7 | 248.1 | 269.7
1123 | 961 | -6.8 | 0 | 0 | 259.7 | 220.1 | 219 | 218.2 | 210.8 | 42.8 | 19.3 | 63.5 | 3.2 | 230.9 | 7.4 | 53.4 | 67.3 | 67.6 | 63.1 | 31 | 34.6 | 37.7 | 29.2 | 34.5 | 27.8 | 94.8 | 41.8 | 90.4 | 165.5 | 256.6 | 279.6 | 147.9 | 248.1 | 269.5
1124 | 962 | -6.8 | 0 | 0 | 258.9 | 219.9 | 218.6 | 217.7 | 210.3 | 42.7 | 19.3 | 63.4 | 3.1 | 236.6 | 7.1 | 52.7 | 65.1 | 68 | 62 | 30.9 | 34.4 | 37.3 | 29.3 | 34.2 | 27.5 | 94.6 | 42.1 | 90.3 | 165.7 | 256.4 | 279.4 | 148.2 | 248 | 269.4
1125 | 963 | -6.8 | 0 | 0 | 258.3 | 219.6 | 218.2 | 217.3 | 210 | 42.6 | 19.3 | 63.3 | 3.2 | 232.5 | 6.5 | 52.1 | 64.1 | 64.4 | 61.7 | 30.8 | 34.1 | 37.5 | 29.3 | 34.3 | 27 | 94.5 | 42.5 | 90.1 | 165.9 | 256.1 | 279.3 | 148.4 | 247.9 | 269.2
1126 | 964 | -6.8 | 0 | 0 | 257.5 | 219.3 | 217.8 | 216.9 | 209.6 | 42.5 | 19.3 | 63.2 | 3.3 | 234.1 | 6.5 | 53.2 | 59.6 | 64.7 | 62.1 | 30.7 | 34 | 37.3 | 29.2 | 34.2 | 26.9 | 94.9 | 42.9 | 90 | 166.2 | 255.9 | 279.1 | 148.7 | 247.8 | 269.1
1127 | 965 | -6.8 | 0 | 0 | 256.8 | 219.1 | 217.4 | 216.5 | 209.2 | 42.4 | 19.3 | 63.1 | 3.2 | 251.6 | 6.6 | 53.3 | 62.6 | 63.6 | 62.3 | 30.6 | 34 | 37 | 29 | 34.9 | 27.4 | 95.1 | 43.1 | 89.8 | 166.4 | 255.7 | 278.9 | 148.9 | 247.7 | 268.9
1128 | 966 | -6.8 | 0 | 0 | 256.3 | 218.8 | 216.9 | 216.2 | 208.8 | 42.3 | 19.3 | 63 | 3.2 | 240.2 | 6.2 | 52.2 | 62.5 | 62 | 62.4 | 30.6 | 34 | 36.9 | 29 | 35 | 27.3 | 94.5 | 43.4 | 89.6 | 166.6 | 255.6 | 278.8 | 149.2 | 247.6 | 268.7
1129 | 967 | -6.8 | 0 | 0 | 255.7 | 218.5 | 216.4 | 215.8 | 208.3 | 42.3 | 19.3 | 62.9 | 3 | 233.5 | 5.6 | 52.3 | 61 | 60.7 | 62.6 | 30.5 | 33.8 | 36.8 | 29 | 34.6 | 27.1 | 93.9 | 43.3 | 89.5 | 166.9 | 255.4 | 278.6 | 149.4 | 247.6 | 268.6
1130 | 968 | -6.8 | 0 | 0 | 255 | 218.2 | 215.9 | 215.4 | 208 | 42.2 | 19.3 | 62.8 | 2.8 | 225.8 | 5 | 52.6 | 64 | 59.1 | 63.4 | 30.4 | 33.6 | 37.3 | 29 | 34.4 | 27 | 94.2 | 42.7 | 89.1 | 167.1 | 255.2 | 278.4 | 149.7 | 247.5 | 268.4
1131 | 969 | -6.8 | 0 | 0 | 254.5 | 217.9 | 215.4 | 215 | 207.6 | 42.2 | 19.3 | 62.7 | 3.1 | 198.5 | 4.2 | 51 | 58.7 | 56.8 | 63.3 | 30.3 | 33.5 | 35.5 | 28.8 | 33.8 | 27 | 94.7 | 42.9 | 88.9 | 167.3 | 255.1 | 278.2 | 149.9 | 247.4 | 268.3
1132 | 970 | -6.8 | 0 | 0 | 254 | 217.6 | 214.9 | 214.6 | 207.2 | 42.1 | 19.3 | 62.6 | 3.2 | 216.6 | 4.2 | 51.1 | 59.1 | 57.1 | 63.3 | 30.2 | 33.7 | 36 | 31.9 | 34.4 | 27.2 | 95 | 42.8 | 88.6 | 167.6 | 254.9 | 278 | 150.1 | 247.3 | 268.1
1133 | 971 | -6.8 | 0 | 0 | 253.5 | 217.3 | 214.5 | 214.2 | 206.7 | 42 | 19.3 | 62.5 | 3.4 | 228.5 | 5.5 | 50.4 | 62.3 | 58.4 | 63.5 | 29.9 | 33.6 | 36.6 | 31.5 | 34.9 | 27.3 | 94.7 | 42.6 | 88.4 | 167.8 | 254.7 | 277.8 | 150.4 | 247.2 | 268
1134 | 972 | -6.7 | 0 | 0 | 252.9 | 216.9 | 214.2 | 213.8 | 206.2 | 41.9 | 19.3 | 62.4 | 3.7 | 211.6 | 6.7 | 50.6 | 64.4 | 60.3 | 61.7 | 29.9 | 33.3 | 36 | 28.6 | 34.7 | 26.9 | 94.8 | 42.6 | 88.2 | 168 | 254.6 | 277.7 | 150.6 | 247.1 | 267.8
1135 | 973 | -6.8 | 0 | 0 | 252.3 | 216.6 | 213.7 | 213.3 | 205.8 | 41.9 | 19.3 | 62.3 | 3.5 | 222.9 | 7.7 | 50.7 | 66.9 | 59.5 | 61.3 | 29.8 | 33.2 | 35.8 | 32.9 | 34.2 | 27.1 | 94.8 | 42.7 | 88.1 | 168.2 | 254.4 | 277.5 | 150.9 | 247 | 267.6
1136 | 974 | -6.8 | 0 | 0 | 251.9 | 216.2 | 213.4 | 212.9 | 205.4 | 41.8 | 19.3 | 62.2 | 3.3 | 213.6 | 7.8 | 48.7 | 69.5 | 59.4 | 55.7 | 29.7 | 33.1 | 35.6 | 29.7 | 34.5 | 27.8 | 94.9 | 41.9 | 88 | 168.5 | 254.3 | 277.3 | 151.1 | 246.9 | 267.5
1137 | 975 | -6.8 | 0 | 0 | 251.5 | 215.9 | 213.1 | 212.5 | 205.1 | 41.6 | 19.3 | 62.1 | 3.3 | 236.9 | 7.2 | 47.8 | 65.6 | 56.7 | 55 | 29.5 | 33.3 | 35.9 | 28.2 | 34.7 | 28 | 94.8 | 39.8 | 87.9 | 168.7 | 254.2 | 277.1 | 151.4 | 246.9 | 267.3
1138 | 976 | -6.8 | 0 | 0 | 251.1 | 215.6 | 212.7 | 212.1 | 204.7 | 41.5 | 19.3 | 62 | 3 | 223.1 | 6.5 | 47.4 | 67.4 | 57.2 | 53.1 | 29.5 | 33.1 | 36.6 | 28.2 | 35.1 | 28.2 | 93.9 | 39.8 | 87.7 | 168.9 | 254 | 277 | 151.6 | 246.8 | 267.2
1139 | 977 | -6.8 | 0 | 0 | 250.7 | 215.3 | 212.3 | 211.6 | 204.4 | 41.4 | 19.3 | 61.9 | 2.8 | 214.8 | 6 | 47.5 | 69.7 | 56.9 | 55.8 | 29.4 | 32.7 | 35 | 28 | 34.3 | 27.7 | 92.7 | 39 | 87.8 | 169.1 | 253.8 | 276.8 | 151.8 | 246.7 | 267
1140 | 978 | -6.8 | 0 | 0 | 250.1 | 215 | 211.8 | 211.2 | 204 | 41.3 | 19.3 | 61.8 | 2.9 | 210.5 | 6.1 | 47.6 | 71 | 55.3 | 57 | 29.3 | 32.4 | 34.7 | 27.7 | 33.6 | 27.6 | 93.7 | 39.2 | 87.9 | 169.4 | 253.7 | 276.6 | 152.1 | 246.6 | 266.9
1141 | 979 | -6.8 | 0 | 0 | 249.6 | 214.6 | 211.3 | 210.7 | 203.6 | 41.2 | 19.3 | 61.8 | 2.9 | 213.2 | 6.3 | 48.5 | 70.4 | 54.2 | 56.7 | 29.1 | 32.3 | 35.6 | 27.7 | 33.8 | 27.5 | 93.9 | 39.6 | 87.9 | 169.6 | 253.6 | 276.4 | 152.3 | 246.5 | 266.7
1142 | 980 | -6.8 | 0 | 0 | 249.1 | 214.3 | 210.9 | 210.3 | 203.1 | 41 | 19.3 | 61.7 | 2.7 | 223.9 | 5.9 | 48.1 | 71.4 | 57.1 | 57.2 | 29 | 32.2 | 35.9 | 27.7 | 34.2 | 27.6 | 93.3 | 40.2 | 87.8 | 169.8 | 253.4 | 276.2 | 152.5 | 246.4 | 266.6
1143 | 981 | -6.8 | 0 | 0 | 248.7 | 214.1 | 210.4 | 209.9 | 202.6 | 40.9 | 19.3 | 61.6 | 2.8 | 206.8 | 5.1 | 47.8 | 66.7 | 56.8 | 57.9 | 28.9 | 32.2 | 36.4 | 27.5 | 33.9 | 27.5 | 92.9 | 40.1 | 87.7 | 170 | 253.3 | 276.1 | 152.8 | 246.3 | 266.5
1144 | 982 | -6.7 | 0 | 0 | 248.3 | 213.8 | 210.1 | 209.4 | 202.2 | 40.8 | 19.3 | 61.5 | 3.1 | 225 | 4.5 | 46.6 | 66.6 | 53.5 | 57.2 | 28.8 | 32.4 | 37.4 | 27.5 | 33.9 | 27.7 | 92.6 | 40.8 | 87.4 | 170.3 | 253.1 | 275.9 | 153 | 246.2 | 266.3
1145 | 983 | -6.6 | 0 | 0 | 247.9 | 213.5 | 209.7 | 209 | 201.7 | 40.8 | 19.3 | 61.4 | 3.2 | 262.3 | 4.4 | 47.5 | 69.3 | 52.5 | 55.8 | 28.8 | 32.7 | 39.1 | 27.4 | 35 | 28 | 93 | 40.9 | 87.3 | 170.5 | 253 | 275.7 | 153.3 | 246.1 | 266.2
1146 | 984 | -6.6 | 0 | 0 | 247.5 | 213.2 | 209.3 | 208.6 | 201.3 | 40.7 | 19.3 | 61.3 | 3 | 247.3 | 4.8 | 47.2 | 67.4 | 53.2 | 55.1 | 28.7 | 32.5 | 39.8 | 27.2 | 35.5 | 28 | 93.1 | 39.8 | 87.1 | 170.7 | 252.9 | 275.5 | 153.5 | 246 | 266
1147 | 985 | -6.8 | 0 | 0 | 246.8 | 213 | 208.9 | 208.1 | 201 | 40.6 | 19.3 | 61.2 | 3.2 | 218.1 | 6.1 | 46.1 | 65 | 53.7 | 55.8 | 28.7 | 32.7 | 39.2 | 26.9 | 34.9 | 27.6 | 92.4 | 38.7 | 87 | 170.9 | 252.7 | 275.3 | 153.7 | 245.9 | 265.9
1148 | 986 | -6.8 | 0 | 0 | 246.1 | 212.7 | 208.4 | 207.7 | 200.5 | 40.5 | 19.3 | 61.1 | 3.3 | 229 | 6.5 | 47 | 67.5 | 53.6 | 55.1 | 28.7 | 32.7 | 37.6 | 26.9 | 33.5 | 27.7 | 91.7 | 37.8 | 86.9 | 171.2 | 252.6 | 275.2 | 154 | 245.8 | 265.7
1149 | 987 | -6.8 | 0 | 0 | 245.6 | 212.3 | 207.9 | 207.2 | 200.1 | 40.5 | 19.3 | 61 | 3.4 | 231.4 | 6.7 | 46.7 | 69.9 | 50.8 | 54.8 | 28.7 | 32.5 | 38.7 | 27 | 34.4 | 27.7 | 92.1 | 37.9 | 86.8 | 171.4 | 252.5 | 275 | 154.2 | 245.8 | 265.6
1150 | 988 | -6.8 | 0 | 0 | 244.9 | 212 | 207.5 | 206.8 | 199.7 | 40.5 | 19.4 | 60.9 | 3.4 | 237.8 | 6.6 | 44 | 72.9 | 52.2 | 55.5 | 28.7 | 32.2 | 38.1 | 26.6 | 34.1 | 27.9 | 92 | 38.1 | 86.6 | 171.6 | 252.3 | 274.8 | 154.4 | 245.7 | 265.5
1151 | 989 | -6.8 | 0 | 0 | 244.3 | 211.6 | 207 | 206.4 | 199.3 | 40.5 | 19.4 | 60.8 | 3.7 | 249.6 | 6.2 | 45.4 | 73.4 | 51.7 | 55.4 | 28.5 | 31.9 | 38.3 | 26.5 | 33.9 | 27.5 | 92.3 | 38.8 | 86.5 | 171.8 | 252.2 | 274.7 | 154.6 | 245.6 | 265.3
1152 | 990 | -6.8 | 0 | 0 | 243.9 | 211.2 | 206.5 | 206 | 198.9 | 40.5 | 19.4 | 60.7 | 3.4 | 250.3 | 5.5 | 42.3 | 65 | 52.2 | 55.3 | 28.5 | 31.7 | 37.8 | 26.7 | 34.2 | 27.2 | 92.7 | 39.2 | 86.3 | 172 | 252.1 | 274.5 | 154.9 | 245.5 | 265.2
1153 | 991 | -6.8 | 0 | 0 | 243.4 | 210.8 | 206.1 | 205.7 | 198.4 | 40.4 | 19.4 | 60.6 | 3.6 | 248.5 | 5.3 | 43.2 | 59.4 | 52.8 | 55.1 | 28.5 | 31.6 | 38.5 | 26.2 | 34.3 | 27.5 | 92.8 | 39.7 | 86.3 | 172.3 | 252 | 274.3 | 155.1 | 245.4 | 265
1154 | 992 | -6.8 | 0 | 0 | 242.8 | 210.5 | 205.8 | 205.2 | 197.9 | 40.4 | 19.4 | 60.6 | 3.7 | 247.5 | 5.3 | 45.2 | 63.1 | 50 | 53.4 | 28.4 | 31.6 | 39.8 | 26.2 | 35.5 | 27.8 | 92.2 | 39.1 | 86.2 | 172.5 | 251.8 | 274.1 | 155.3 | 245.3 | 264.9
1155 | 993 | -6.6 | 0 | 0 | 242.4 | 210.3 | 205.4 | 204.8 | 197.4 | 40.3 | 19.4 | 60.5 | 3.7 | 250.2 | 5.7 | 43.7 | 67.5 | 48.8 | 50.7 | 28.4 | 31.6 | 43.2 | 26 | 37.6 | 28.1 | 91.4 | 38.4 | 86.2 | 172.7 | 251.7 | 273.9 | 155.6 | 245.2 | 264.7
1156 | 994 | -6.7 | 0 | 0 | 241.9 | 210 | 204.9 | 204.3 | 197 | 40.2 | 19.4 | 60.4 | 3.5 | 243 | 6.1 | 43.3 | 71.1 | 47.2 | 47.7 | 28.4 | 31.2 | 44 | 25.8 | 36.5 | 28.4 | 91.1 | 36.8 | 86.2 | 172.9 | 251.6 | 273.7 | 155.8 | 245.1 | 264.5
1157 | 995 | -6.7 | 0 | 0 | 241.4 | 209.8 | 204.6 | 203.8 | 196.7 | 40.2 | 19.4 | 60.3 | 3.6 | 238 | 6.1 | 43.1 | 72.1 | 47.4 | 48.6 | 28.3 | 31 | 44.7 | 25.7 | 35.9 | 28.8 | 92 | 37 | 86.2 | 173.1 | 251.5 | 273.6 | 156 | 245 | 264.4
1158 | 996 | -6.8 | 0 | 0 | 240.9 | 209.4 | 204.2 | 203.4 | 196.3 | 40.1 | 19.4 | 60.1 | 3.5 | 242.9 | 6.1 | 44.4 | 73.2 | 47.7 | 49.6 | 28.2 | 30.8 | 43 | 25.6 | 35.9 | 28.7 | 92.1 | 37.5 | 86.2 | 173.4 | 251.3 | 273.5 | 156.2 | 244.9 | 264.2
1159 | 997 | -6.7 | 0 | 0 | 240.7 | 209.1 | 203.8 | 203.1 | 195.8 | 40.1 | 19.4 | 60 | 3.6 | 246 | 6.2 | 44.2 | 73.4 | 48.8 | 48.5 | 28.2 | 30.6 | 42 | 25.7 | 34 | 28.8 | 92.4 | 37.5 | 86.3 | 173.6 | 251.2 | 273.3 | 156.5 | 244.9 | 264.1
1160 | 998 | -6.8 | 0 | 0 | 240.5 | 208.8 | 203.4 | 202.6 | 195.4 | 40.1 | 19.4 | 59.9 | 3.6 | 247.3 | 6.2 | 44 | 69.1 | 49.2 | 48.8 | 28.2 | 30.5 | 42.5 | 29.5 | 36 | 29.1 | 92.1 | 36.6 | 86.2 | 173.8 | 251.1 | 273.1 | 156.7 | 244.8 | 263.9
1161 | 999 | -6.7 | 0 | 0 | 240.2 | 208.6 | 202.9 | 202.2 | 195 | 40.1 | 19.4 | 59.8 | 3.4 | 250 | 6.2 | 43.4 | 70.8 | 48.9 | 49.4 | 28.3 | 30.1 | 43.2 | 29.2 | 35.9 | 28.3 | 92 | 36.2 | 86.3 | 174 | 250.9 | 272.9 | 156.9 | 244.7 | 263.8
1162 | 1000 | -6.7 | 0 | 0 | 240.1 | 208.3 | 202.6 | 201.8 | 194.6 | 40.1 | 19.4 | 59.7 | 3.2 | 248.2 | 5.8 | 41.2 | 72.5 | 50.3 | 49.3 | 28.4 | 29.8 | 44.1 | 25.7 | 35 | 28.2 | 90.4 | 36.1 | 86.3 | 174.2 | 250.8 | 272.7 | 157.1 | 244.6 | 263.6
1163 | 1001 | -6.6 | 0 | 0 | 239.9 | 208.1 | 202.3 | 201.4 | 194.3 | 40 | 19.4 | 59.6 | 3.1 | 241.8 | 5 | 42.8 | 73.9 | 49.6 | 46.1 | 28.4 | 30 | 45.2 | 31.4 | 35.4 | 28.2 | 91.5 | 36.2 | 86.2 | 174.5 | 250.7 | 272.6 | 157.3 | 244.5 | 263.5
1164 | 1002 | -6.7 | 0 | 0 | 239.5 | 207.9 | 202 | 201.1 | 193.9 | 40 | 19.4 | 59.5 | 3.2 | 239.8 | 4.9 | 42.4 | 73.7 | 46.7 | 46.6 | 28.4 | 29.6 | 44.7 | 27.7 | 36.5 | 28.5 | 91.1 | 36.5 | 86.1 | 174.7 | 250.6 | 272.4 | 157.6 | 244.4 | 263.3
1165 | 1003 | -6.8 | 0 | 0 | 239.2 | 207.7 | 201.7 | 200.7 | 193.6 | 39.9 | 19.4 | 59.4 | 3.3 | 251.4 | 5.1 | 40.5 | 74.4 | 48.5 | 47.9 | 28.5 | 29.1 | 44 | 25.8 | 34.2 | 29 | 90.4 | 36.7 | 86 | 174.9 | 250.5 | 272.2 | 157.8 | 244.3 | 263.2
1166 | 1004 | -6.8 | 0 | 0 | 239 | 207.5 | 201.3 | 200.3 | 193.3 | 39.8 | 19.4 | 59.3 | 3 | 262.5 | 4.9 | 40.2 | 75.4 | 50.3 | 50.3 | 28.5 | 28.9 | 41.5 | 25.9 | 32.2 | 29.6 | 90.3 | 37.3 | 86 | 175.1 | 250.4 | 272 | 158 | 244.2 | 263
1167 | 1005 | -6.8 | 0 | 0 | 238.7 | 207.3 | 201 | 199.8 | 193.1 | 39.8 | 19.4 | 59.2 | 3 | 254.5 | 5.2 | 40.5 | 76.9 | 51.5 | 52.7 | 28.6 | 28.7 | 39.2 | 26 | 31.2 | 30.4 | 89.5 | 37.3 | 85.9 | 175.3 | 250.3 | 271.9 | 158.2 | 244.1 | 262.9
1168 | 1006 | -6.8 | 0 | 0 | 238.4 | 207.1 | 200.7 | 199.4 | 192.9 | 39.7 | 19.4 | 59.1 | 2.8 | 253.2 | 5.2 | 40.7 | 77.9 | 53.1 | 54.2 | 28.6 | 28.6 | 37.9 | 26 | 31 | 30.9 | 89.4 | 37.4 | 85.8 | 175.5 | 250.1 | 271.7 | 158.4 | 244 | 262.7
1169 | 1007 | -6.7 | 0 | 0 | 238 | 206.9 | 200.4 | 199.1 | 192.6 | 39.6 | 19.4 | 59.1 | 2.9 | 249.4 | 5.2 | 41 | 79.1 | 54.7 | 55.4 | 28.6 | 28.6 | 36.8 | 26.1 | 30.6 | 31.5 | 89.8 | 37.5 | 85.7 | 175.7 | 250 | 271.5 | 158.7 | 243.9 | 262.6
1170 | 1008 | -6.4 | 0 | 0 | 237.7 | 206.7 | 200.1 | 198.7 | 192.5 | 39.6 | 19.4 | 59 | 3.1 | 232.8 | 5.9 | 41.5 | 78.7 | 55.2 | 55.4 | 28.7 | 28.6 | 36.1 | 26.2 | 30.4 | 32.1 | 89.9 | 37.6 | 85.5 | 176 | 249.9 | 271.3 | 158.9 | 243.8 | 262.4
1171 | 1009 | -6.2 | 0 | 0 | 237.4 | 206.6 | 199.8 | 198.3 | 192.3 | 39.5 | 19.4 | 58.9 | 3.1 | 241.4 | 6.5 | 42.1 | 78.8 | 55.8 | 56.6 | 28.7 | 28.6 | 35.1 | 26.1 | 30.3 | 32.7 | 89.4 | 37.7 | 85.5 | 176.2 | 249.8 | 271.2 | 159.1 | 243.4 | 262.3
1172 | 1010 | -6.3 | 0 | 0 | 237.3 | 206.3 | 199.5 | 198 | 192.1 | 39.5 | 19.4 | 58.8 | 3.2 | 242.2 | 7 | 42.8 | 78.9 | 56.5 | 57.9 | 28.6 | 28.5 | 33.9 | 26.1 | 30.4 | 33.3 | 89.2 | 37.8 | 85.4 | 176.4 | 249.7 | 271 | 159.3 | 242.8 | 262.1
1173 | 1011 | -6.5 | 0 | 0 | 237 | 206.1 | 199.1 | 197.7 | 191.8 | 39.4 | 19.4 | 58.7 | 3.3 | 227.6 | 7.4 | 43.7 | 78.8 | 56.9 | 59.1 | 28.7 | 28.5 | 33.6 | 26 | 30.4 | 33.9 | 89.4 | 37.9 | 85.3 | 176.6 | 249.6 | 270.8 | 159.5 | 242.5 | 262
1174 | 1012 | -6.7 | 0 | 0 | 236.8 | 205.8 | 198.9 | 197.5 | 191.6 | 39.4 | 19.4 | 58.6 | 3.1 | 239.1 | 6.9 | 44.2 | 79 | 57.5 | 60 | 28.7 | 28.5 | 33.4 | 25.5 | 30.3 | 34.5 | 89.2 | 38 | 85.3 | 176.8 | 249.5 | 270.7 | 159.7 | 242.3 | 261.9
1175 | 1013 | -6.7 | 0 | 0 | 236.4 | 205.6 | 198.6 | 197.3 | 191.4 | 39.3 | 19.4 | 58.5 | 3 | 239.2 | 6.3 | 44.6 | 79.3 | 57.9 | 60.4 | 28.7 | 28.5 | 32.5 | 25.1 | 30.5 | 34.9 | 88.8 | 38 | 85.2 | 177 | 249.3 | 270.5 | 160 | 242.1 | 261.7
1176 | 1014 | -6.5 | 0 | 0 | 236 | 205.4 | 198.3 | 197 | 191.2 | 39.2 | 19.4 | 58.4 | 3.2 | 238.2 | 5.6 | 45.3 | 79.8 | 58.1 | 61.3 | 28.7 | 28.5 | 31.6 | 24.7 | 30.5 | 35.3 | 88.2 | 38.1 | 85.1 | 177.2 | 249.3 | 270.3 | 160.2 | 242 | 261.6
1177 | 1015 | -6.6 | 0 | 0 | 235.7 | 205.1 | 198.1 | 196.7 | 190.9 | 39.1 | 19.4 | 58.3 | 2.8 | 264.2 | 5 | 45.9 | 80.2 | 58.5 | 62.1 | 28.7 | 28.5 | 30.9 | 24.7 | 30.7 | 35.8 | 88.9 | 38.2 | 85 | 177.4 | 249.1 | 270.1 | 160.4 | 241.8 | 261.4
1178 | 1016 | -6.7 | 0 | 0 | 235.3 | 204.9 | 197.7 | 196.4 | 190.7 | 39.1 | 19.4 | 58.2 | 2.9 | 251.7 | 5.7 | 46.5 | 80 | 59.1 | 62.7 | 28.7 | 28.5 | 30.7 | 24.2 | 30.9 | 36.3 | 89.4 | 38.2 | 84.9 | 177.6 | 249 | 270 | 160.6 | 241.7 | 261.3
1179 | 1017 | -6.7 | 0 | 0 | 235.3 | 204.7 | 197.4 | 196.1 | 190.6 | 39.1 | 19.4 | 58.2 | 3 | 237.8 | 6.4 | 47 | 79.7 | 59.5 | 62.3 | 28.7 | 28.5 | 30.5 | 23.9 | 30.6 | 36.9 | 89.4 | 38.2 | 84.8 | 177.8 | 248.9 | 269.8 | 160.8 | 241.6 | 261.1
1180 | 1018 | -6.7 | 0 | 0 | 235.2 | 204.5 | 197.1 | 195.8 | 190.4 | 39.1 | 19.4 | 58.1 | 2.9 | 245.6 | 6.3 | 47.5 | 79.9 | 59.8 | 62.8 | 28.7 | 28.6 | 30.9 | 24.2 | 30 | 37.4 | 89.1 | 38.3 | 84.7 | 178.1 | 248.8 | 269.6 | 161 | 241.5 | 260.9
1181 | 1019 | -6.8 | 0 | 0 | 234.5 | 204.2 | 196.9 | 195.6 | 190.2 | 39.1 | 19.4 | 58 | 2.8 | 258.7 | 5.7 | 47.9 | 80.9 | 60.1 | 63.2 | 28.6 | 28.6 | 31.2 | 23.6 | 30 | 38 | 89.1 | 38.3 | 84.6 | 178.3 | 248.7 | 269.4 | 161.2 | 241.4 | 260.8
1182 | 1020 | -6.8 | 0 | 0 | 233.9 | 204 | 196.7 | 195.3 | 189.9 | 39.1 | 19.4 | 57.9 | 3.4 | 264.2 | 6.6 | 48.5 | 81.8 | 60.3 | 64.6 | 28.6 | 28.6 | 31.1 | 23.5 | 30.5 | 38.5 | 88.8 | 38.3 | 84.5 | 178.5 | 248.6 | 269.3 | 161.4 | 241.3 | 260.7
1183 | 1021 | -6.8 | 0 | 0 | 233.3 | 203.7 | 196.5 | 195 | 189.6 | 39.1 | 19.4 | 57.8 | 3.4 | 259.1 | 6.6 | 48.8 | 82.5 | 60.3 | 65.3 | 28.6 | 28.6 | 31.4 | 23.2 | 30.4 | 38.9 | 88.8 | 38.3 | 84.4 | 178.7 | 248.5 | 269.1 | 161.6 | 241.2 | 260.5
1184 | 1022 | -6.7 | 0 | 0 | 232.8 | 203.5 | 196.3 | 194.6 | 189.3 | 39.1 | 19.4 | 57.7 | 2.9 | 254 | 6.8 | 49.1 | 82.5 | 60.4 | 65.1 | 28.7 | 28.7 | 31.8 | 22.9 | 30.2 | 39.3 | 88.9 | 38.4 | 84.3 | 178.9 | 248.4 | 268.9 | 161.8 | 241.1 | 260.4
1185 | 1023 | -6.5 | 0 | 0 | 232.2 | 203.3 | 196 | 194.4 | 189 | 39 | 19.4 | 57.6 | 2.8 | 262.3 | 7.6 | 49.7 | 82.9 | 60.5 | 65.4 | 28.7 | 28.9 | 32.3 | 25.7 | 30.5 | 39.8 | 88.6 | 38.4 | 84.2 | 179.1 | 248.3 | 268.8 | 162 | 241 | 260.2
1186 | 1024 | -6.5 | 0 | 0 | 231.6 | 203.1 | 195.7 | 194.1 | 188.8 | 39 | 19.4 | 57.6 | 3.3 | 254.3 | 7.9 | 50.1 | 82.6 | 60.8 | 65.6 | 28.7 | 29 | 32.6 | 29 | 31.3 | 40.2 | 88 | 38.4 | 84.1 | 179.3 | 248.2 | 268.6 | 162.2 | 240.9 | 260.1
1187 | 1025 | -6.6 | 0 | 0 | 231 | 202.9 | 195.3 | 193.8 | 188.7 | 38.9 | 19.4 | 57.5 | 3.1 | 263.9 | 8.3 | 50.5 | 81.7 | 61 | 65.7 | 28.8 | 28.9 | 32.6 | 22.5 | 31.8 | 40.7 | 88.1 | 38.4 | 84 | 179.5 | 248.1 | 268.4 | 162.5 | 240.9 | 259.9
1188 | 1026 | -6.6 | 0 | 0 | 230.5 | 202.7 | 194.9 | 193.5 | 188.5 | 38.8 | 19.4 | 57.5 | 3.1 | 262.6 | 8 | 50.8 | 81 | 61.3 | 66 | 28.8 | 29.1 | 32.4 | 27.3 | 31.5 | 41.2 | 88.4 | 38.5 | 84 | 179.7 | 248 | 268.3 | 162.7 | 240.8 | 259.8
1189 | 1027 | -6.4 | 0 | 0 | 230 | 202.5 | 194.6 | 193.2 | 188.2 | 38.7 | 19.5 | 57.4 | 3.3 | 257.7 | 7.5 | 51.2 | 80.4 | 61.3 | 66.3 | 28.8 | 29.1 | 32.1 | 26.7 | 31.6 | 41.6 | 88.5 | 38.5 | 83.9 | 179.9 | 247.9 | 268.1 | 162.9 | 240.7 | 259.6
1190 | 1028 | -6.2 | 0 | 0 | 229.6 | 202.3 | 194.4 | 192.9 | 188 | 38.7 | 19.5 | 57.4 | 3.5 | 264.3 | 7.9 | 51.4 | 80.2 | 61.5 | 66.5 | 28.8 | 29 | 31.6 | 22.3 | 31.2 | 42.1 | 88.3 | 38.6 | 83.8 | 180.1 | 247.8 | 268 | 163.1 | 240.6 | 259.5
1191 | 1029 | -6.4 | 0 | 0 | 229.3 | 202.1 | 194.1 | 192.7 | 187.8 | 38.6 | 19.5 | 57.4 | 3.5 | 263 | 8.1 | 51.6 | 80.2 | 61.4 | 66.9 | 28.8 | 29.1 | 31.4 | 22.4 | 30.5 | 42.5 | 88.1 | 38.6 | 83.8 | 180.3 | 247.7 | 267.8 | 163.3 | 240.5 | 259.3
1192 | 1030 | -6.5 | 0 | 0 | 229 | 201.9 | 193.7 | 192.4 | 187.5 | 38.6 | 19.5 | 57.3 | 3.2 | 258.8 | 8.8 | 52 | 80 | 61.5 | 66.9 | 28.8 | 29.1 | 31.8 | 22.2 | 30.1 | 43 | 88.2 | 38.6 | 83.7 | 180.6 | 247.6 | 267.7 | 163.5 | 240.4 | 259.2
1193 | 1031 | -6.6 | 0 | 0 | 228.9 | 201.6 | 193.5 | 192.2 | 187.3 | 38.6 | 19.5 | 57.3 | 3 | 268.5 | 8.9 | 52.5 | 81 | 61.9 | 66.6 | 28.8 | 29.2 | 31.9 | 22 | 30.1 | 43.4 | 88.2 | 38.7 | 83.6 | 180.8 | 247.5 | 267.5 | 163.7 | 240.3 | 259
1194 | 1032 | -6.6 | 0 | 0 | 228.8 | 201.4 | 193.2 | 191.9 | 187.1 | 38.6 | 19.5 | 57.3 | 2.7 | 259.7 | 8.4 | 52.7 | 80.5 | 62.1 | 66.5 | 28.8 | 29.3 | 31.6 | 21.9 | 31.2 | 43.8 | 88.2 | 38.7 | 83.5 | 181 | 247.4 | 267.3 | 163.9 | 240.3 | 258.9
1195 | 1033 | -6.6 | 0 | 0 | 228.5 | 201.1 | 192.9 | 191.7 | 186.9 | 38.6 | 19.5 | 57.2 | 3 | 264.8 | 8 | 52.7 | 79.9 | 61.9 | 66.5 | 28.8 | 29.4 | 31.9 | 21.7 | 31.9 | 44.2 | 88 | 38.7 | 83.4 | 181.2 | 247.2 | 267.1 | 164.1 | 240.2 | 258.7
1196 | 1034 | -6.5 | 0 | 0 | 228.3 | 200.9 | 192.6 | 191.5 | 186.6 | 38.6 | 19.5 | 57.2 | 3 | 265.6 | 7.7 | 52.9 | 79.6 | 61.7 | 67 | 28.8 | 29.4 | 31.9 | 21.7 | 31.9 | 44.5 | 87.4 | 38.7 | 83.4 | 181.4 | 247.1 | 267 | 164.3 | 240.1 | 258.6
1197 | 1035 | -6.5 | 0 | 0 | 228 | 200.7 | 192.3 | 191.2 | 186.4 | 38.6 | 19.5 | 57.1 | 2.9 | 263.3 | 7.8 | 53.3 | 79.8 | 61.7 | 67.3 | 28.8 | 29.4 | 31.5 | 21.6 | 32.4 | 44.8 | 86.3 | 38.8 | 83.3 | 181.6 | 247.1 | 266.8 | 164.5 | 240 | 258.5
1198 | 1036 | -6.6 | 0 | 0 | 227.8 | 200.5 | 192 | 190.9 | 186.2 | 38.6 | 19.5 | 57 | 3.2 | 258.6 | 7.1 | 53.5 | 79.5 | 61.7 | 67.5 | 28.8 | 29.5 | 31.2 | 21.6 | 32.7 | 45.1 | 85.9 | 38.8 | 83.2 | 181.8 | 247 | 266.6 | 164.7 | 239.9 | 258.3
1199 | 1037 | -6.5 | 0 | 0 | 227.6 | 200.3 | 191.8 | 190.6 | 185.9 | 38.5 | 19.5 | 57 | 3.1 | 263.5 | 6.3 | 53.8 | 79.2 | 61.7 | 67.4 | 28.8 | 29.6 | 31.2 | 21.6 | 33 | 45.4 | 86.2 | 38.8 | 83.1 | 182 | 246.8 | 266.5 | 164.9 | 239.8 | 258.2
1200 | 1038 | -6.6 | 0 | 0 | 227.4 | 200 | 191.6 | 190.3 | 185.7 | 38.4 | 19.5 | 56.9 | 3 | 262.4 | 6.4 | 53.9 | 79.1 | 61.7 | 67.2 | 28.8 | 29.6 | 31.5 | 21.6 | 32.8 | 45.7 | 86.6 | 38.8 | 83.1 | 182.2 | 246.8 | 266.3 | 165 | 239.7 | 258
1201 | 1039 | -6.5 | 0 | 0 | 227.3 | 199.8 | 191.3 | 190 | 185.6 | 38.3 | 19.5 | 56.9 | 3 | 265 | 6.6 | 54.1 | 79.1 | 61.8 | 67.1 | 28.8 | 29.7 | 31.2 | 21.5 | 32.6 | 46 | 86.8 | 38.9 | 83 | 182.4 | 246.7 | 266.1 | 165.3 | 239.6 | 257.9
1202 | 1040 | -6.5 | 0 | 0 | 227.1 | 199.5 | 190.9 | 189.7 | 185.4 | 38.2 | 19.5 | 56.8 | 3 | 282.7 | 6.4 | 54.3 | 78.6 | 61.8 | 67.2 | 28.8 | 29.7 | 30.8 | 21.7 | 32.5 | 46.4 | 86.8 | 38.9 | 82.9 | 182.6 | 246.6 | 266 | 165.4 | 239.5 | 257.7
1203 | 1041 | -6.7 | 0 | 0 | 226.8 | 199.2 | 190.6 | 189.4 | 185.2 | 38 | 19.5 | 56.7 | 3.1 | 261 | 6.1 | 54.5 | 78.2 | 61.8 | 67.6 | 28.8 | 29.8 | 31 | 21.4 | 32.4 | 46.8 | 86.7 | 38.9 | 82.7 | 182.8 | 246.5 | 265.8 | 165.6 | 239.4 | 257.6
1204 | 1042 | -6.8 | 0 | 0 | 226.6 | 199 | 190.4 | 189.2 | 185 | 37.9 | 19.5 | 56.7 | 3.2 | 250.6 | 6 | 54.7 | 78.2 | 61.8 | 68 | 28.7 | 29.9 | 31.4 | 21.2 | 32.4 | 47.1 | 86.8 | 39 | 82.6 | 183 | 246.4 | 265.6 | 165.8 | 239.4 | 257.4
1205 | 1043 | -6.8 | 0 | 0 | 226.4 | 198.7 | 190.1 | 188.9 | 184.8 | 37.9 | 19.5 | 56.6 | 2.8 | 252.5 | 6 | 55.1 | 78.3 | 61.7 | 68.3 | 28.7 | 30 | 31.8 | 21.5 | 32.1 | 47.5 | 87.2 | 39 | 82.5 | 183.3 | 246.3 | 265.5 | 166 | 239.3 | 257.3
1206 | 1044 | -6.5 | 0 | 0 | 226.1 | 198.5 | 189.7 | 188.7 | 184.5 | 37.9 | 19.5 | 56.5 | 2.9 | 260.9 | 5.8 | 55.5 | 78.3 | 61.9 | 68.3 | 28.8 | 30 | 31.8 | 21.2 | 32.4 | 47.9 | 87 | 39 | 82.4 | 183.5 | 246.2 | 265.3 | 166.2 | 239.2 | 257.1
1207 | 1045 | -6.5 | 0 | 0 | 225.8 | 198.3 | 189.5 | 188.5 | 184.3 | 37.9 | 19.5 | 56.5 | 2.9 | 252.6 | 5.5 | 55.7 | 78.3 | 62.4 | 68.1 | 28.8 | 30.1 | 32 | 21 | 32.9 | 48.2 | 86.5 | 39 | 82.4 | 183.7 | 246.1 | 265.1 | 166.4 | 239.1 | 257
1208 | 1046 | -6.5 | 0 | 0 | 225.5 | 198.1 | 189.3 | 188.2 | 184 | 37.9 | 19.5 | 56.4 | 2.9 | 243.4 | 4.6 | 55.9 | 78.1 | 62.7 | 68.4 | 28.8 | 30.3 | 31.6 | 30.3 | 33.3 | 48.5 | 86.4 | 39.1 | 82.3 | 184 | 246 | 265 | 166.6 | 239 | 256.8
1209 | 1047 | -6.3 | 0 | 0 | 225.2 | 197.9 | 189 | 187.9 | 183.6 | 37.8 | 19.5 | 56.4 | 2.9 | 249.9 | 4.9 | 56.2 | 78.2 | 62.7 | 68.1 | 28.8 | 30.2 | 31.3 | 21.4 | 33.4 | 48.7 | 86.3 | 39.1 | 82.3 | 184.2 | 245.9 | 264.8 | 166.8 | 238.9 | 256.7
1210 | 1048 | -6.6 | 0 | 0 | 224.9 | 197.7 | 188.7 | 187.7 | 183.3 | 37.8 | 19.5 | 56.3 | 3.2 | 251.3 | 5.4 | 56.3 | 78.6 | 63.1 | 67.5 | 28.8 | 30.3 | 30.9 | 22 | 33.1 | 49 | 86.2 | 39.1 | 82.2 | 184.4 | 245.8 | 264.6 | 167 | 239 | 256.6
1211 | 1049 | -6.8 | 0 | 0 | 224.7 | 197.5 | 188.5 | 187.4 | 183 | 37.7 | 19.5 | 56.3 | 3 | 251.9 | 5.6 | 56.6 | 79.1 | 63.1 | 67.9 | 28.8 | 30.5 | 31.4 | 29.4 | 32.6 | 49.2 | 85.9 | 39.1 | 82.1 | 184.6 | 245.7 | 264.5 | 167.2 | 239.1 | 256.4
1212 | 1050 | -6.8 | 0 | 0 | 224.4 | 197.2 | 188.3 | 187.2 | 182.8 | 37.7 | 19.5 | 56.2 | 2.9 | 250.8 | 5.6 | 56.9 | 79.7 | 63.3 | 67.8 | 28.8 | 30.3 | 31.6 | 20.9 | 32.9 | 49.4 | 85.7 | 39.2 | 82.1 | 184.9 | 245.6 | 264.3 | 167.4 | 239.1 | 256.2
1213 | 1051 | -6.8 | 0 | 0 | 224.1 | 197.1 | 188 | 186.9 | 182.5 | 37.7 | 19.5 | 56.2 | 2.9 | 247.8 | 5.1 | 57.1 | 78.7 | 63.5 | 67.5 | 28.8 | 30.4 | 31 | 21 | 33.4 | 49.7 | 85.3 | 39.2 | 82 | 185.1 | 245.5 | 264.2 | 167.6 | 239.1 | 256.1
1214 | 1052 | -6.7 | 0 | 0 | 223.7 | 196.8 | 187.7 | 186.7 | 182.2 | 37.6 | 19.5 | 56.2 | 2.8 | 247.8 | 5.1 | 57.2 | 78.5 | 63.4 | 67.3 | 28.8 | 30.5 | 30.4 | 21 | 33.3 | 50.1 | 84.6 | 39.3 | 81.9 | 185.3 | 245.4 | 264 | 167.8 | 239 | 255.9
1215 | 1053 | -6.5 | 0 | 0 | 223.3 | 196.5 | 187.4 | 186.4 | 182 | 37.6 | 19.5 | 56.2 | 2.8 | 224.4 | 5.1 | 57.3 | 78.1 | 63.5 | 67.5 | 28.8 | 30.5 | 30.4 | 20.9 | 33 | 50.5 | 85.1 | 39.3 | 81.8 | 185.6 | 245.3 | 263.9 | 167.9 | 239 | 255.8
1216 | 1054 | -6.1 | 0 | 0 | 222.9 | 196.3 | 187.2 | 186.2 | 181.7 | 37.6 | 19.5 | 56.1 | 3.1 | 225.8 | 5.3 | 57.4 | 78.3 | 63.4 | 67.3 | 28.8 | 30.5 | 30.7 | 20.9 | 32.9 | 50.7 | 85.5 | 39.3 | 81.6 | 185.9 | 245.2 | 263.7 | 168.1 | 239 | 255.7
1217 | 1055 | -5.2 | 0 | 0 | 222.4 | 196 | 187 | 186 | 181.5 | 37.5 | 19.5 | 56.1 | 3.2 | 239.4 | 5.8 | 57.4 | 78.4 | 63.4 | 66.7 | 28.8 | 30.6 | 30.6 | 20.9 | 33 | 50.9 | 85.8 | 39.3 | 81.5 | 186.1 | 245.1 | 263.5 | 168.3 | 238.9 | 255.5
1218 | 1056 | -5.3 | 0 | 0 | 222.2 | 195.8 | 186.8 | 185.8 | 181.3 | 37.5 | 19.5 | 56 | 3.3 | 238.2 | 5.9 | 57.5 | 78.3 | 63.7 | 66.3 | 28.8 | 30.7 | 31.2 | 20.9 | 32.5 | 51.2 | 85.6 | 39.4 | 81.4 | 186.4 | 245 | 263.4 | 168.5 | 238.8 | 255.4
1219 | 1057 | -5.8 | 0 | 0 | 222 | 195.5 | 186.6 | 185.5 | 181.2 | 37.4 | 19.5 | 56 | 3.3 | 228.1 | 5.1 | 57.6 | 78 | 63.6 | 66.5 | 28.8 | 30.8 | 31.2 | 20.9 | 32.5 | 51.5 | 85.2 | 39.4 | 81.4 | 186.7 | 244.9 | 263.2 | 168.7 | 238.8 | 255.2
1220 | 1058 | -6.2 | 0 | 0 | 221.6 | 195.3 | 186.3 | 185.2 | 181.1 | 37.3 | 19.5 | 56 | 3.3 | 248.7 | 4.1 | 57.8 | 77.7 | 63.3 | 67.1 | 28.8 | 30.8 | 31.1 | 20.9 | 32.7 | 51.6 | 85.4 | 39.4 | 81.3 | 186.9 | 244.8 | 263 | 168.9 | 238.7 | 255.1
1221 | 1059 | -6.4 | 0 | 0 | 221.2 | 195.1 | 186.1 | 184.8 | 181 | 37.3 | 19.5 | 55.9 | 3.3 | 258.6 | 3.7 | 57.9 | 78.5 | 63.3 | 67.2 | 28.8 | 30.9 | 31.1 | 20.8 | 32.7 | 51.8 | 85.5 | 39.4 | 81.3 | 187.2 | 244.7 | 262.9 | 169.1 | 238.6 | 254.9
1222 | 1060 | -6.5 | 0 | 0 | 220.8 | 194.9 | 185.8 | 184.5 | 180.9 | 37.2 | 19.5 | 55.9 | 3.2 | 217.1 | 3.8 | 58 | 79.6 | 63 | 67.3 | 28.8 | 30.9 | 30.8 | 20.8 | 32.8 | 52 | 85.6 | 39.5 | 81.3 | 187.5 | 244.6 | 262.7 | 169.2 | 238.5 | 254.8
1223 | 1061 | -6.4 | 0 | 0 | 220.4 | 194.8 | 185.6 | 184.3 | 180.7 | 37.2 | 19.5 | 55.8 | 2.9 | 191.8 | 3.9 | 58.1 | 78.8 | 62.8 | 67.2 | 28.8 | 31 | 31.5 | 20.8 | 33.2 | 52.3 | 85.9 | 39.5 | 81.2 | 187.7 | 244.5 | 262.6 | 169.4 | 238.5 | 254.6
1224 | 1062 | -6.3 | 0 | 0 | 220.1 | 194.6 | 185.4 | 183.9 | 180.6 | 37.2 | 19.5 | 55.8 | 3.2 | 227 | 3.7 | 58.3 | 77.4 | 62.8 | 67.3 | 28.8 | 31.1 | 31.9 | 20.7 | 33.6 | 52.5 | 85.9 | 39.5 | 81.2 | 188 | 244.4 | 262.4 | 169.6 | 238.4 | 254.5
1225 | 1063 | -6.3 | 0 | 0 | 219.8 | 194.4 | 185.1 | 183.7 | 180.4 | 37.1 | 19.5 | 55.7 | 3.2 | 229.1 | 3.6 | 58.4 | 76.7 | 63 | 66.9 | 28.8 | 31.2 | 32 | 21 | 34 | 52.6 | 86 | 39.5 | 81.1 | 188.4 | 244.3 | 262.2 | 169.8 | 238.3 | 254.4
1226 | 1064 | -6.2 | 0 | 0 | 219.5 | 194.2 | 184.9 | 183.5 | 180.2 | 37.1 | 19.5 | 55.7 | 3.3 | 223.4 | 3.4 | 58.5 | 76.9 | 63 | 66.9 | 28.8 | 31.2 | 32.5 | 20.5 | 34.4 | 52.8 | 86.4 | 39.5 | 81 | 188.7 | 244.2 | 262.1 | 170 | 238.2 | 254.2
1227 | 1065 | -6.4 | 0 | 0 | 219.1 | 194 | 184.6 | 183.3 | 179.9 | 37 | 19.5 | 55.6 | 3.1 | 223 | 3.2 | 58.6 | 76.7 | 63.1 | 67.2 | 28.8 | 31.3 | 33 | 20.7 | 34.7 | 53 | 86.5 | 39.6 | 81 | 189 | 244.1 | 261.9 | 170.2 | 238.1 | 254.1
1228 | 1066 | -6.4 | 0 | 0 | 218.8 | 193.8 | 184.4 | 183 | 179.7 | 37 | 19.6 | 55.6 | 3.6 | 213.8 | 3.8 | 58.8 | 76.2 | 63.1 | 66.8 | 28.9 | 31.4 | 32.7 | 20.9 | 34.7 | 53.3 | 85.8 | 39.6 | 80.9 | 189.3 | 244 | 261.8 | 170.3 | 238 | 253.9
1229 | 1067 | -6.4 | 0 | 0 | 218.5 | 193.6 | 184.2 | 182.8 | 179.4 | 36.9 | 19.6 | 55.6 | 3.5 | 213.3 | 3.8 | 58.8 | 75.9 | 62.7 | 66.7 | 28.9 | 31.7 | 32.5 | 30.2 | 34.7 | 53.4 | 85.7 | 39.6 | 80.8 | 189.6 | 243.9 | 261.6 | 170.5 | 237.9 | 253.8
1230 | 1068 | -6.2 | 0 | 0 | 218.1 | 193.3 | 184 | 182.6 | 179.1 | 36.9 | 19.6 | 55.5 | 3.7 | 230.2 | 3.4 | 58.9 | 75.5 | 62.5 | 67 | 28.9 | 31.6 | 32.4 | 26.1 | 34.9 | 53.6 | 86.2 | 39.7 | 80.8 | 189.8 | 243.8 | 261.4 | 170.7 | 237.8 | 253.6
1231 | 1069 | -6.3 | 0 | 0 | 217.8 | 193.1 | 183.8 | 182.3 | 178.9 | 36.9 | 19.6 | 55.4 | 3.4 | 234.6 | 3.4 | 59.1 | 75.1 | 62.8 | 67.3 | 28.9 | 31.6 | 32.2 | 26 | 34.6 | 53.9 | 86.2 | 39.7 | 80.7 | 190.1 | 243.7 | 261.3 | 170.9 | 237.7 | 253.5
1232 | 1070 | -6.3 | 0 | 0 | 217.5 | 192.9 | 183.6 | 182.1 | 178.6 | 36.8 | 19.6 | 55.4 | 3.4 | 237.8 | 3.4 | 59.1 | 74.8 | 62.8 | 67.8 | 28.9 | 31.6 | 32.3 | 28.9 | 33.7 | 54 | 85.9 | 39.8 | 80.7 | 190.4 | 243.6 | 261.1 | 171 | 237.6 | 253.4
1233 | 1071 | -6.3 | 0 | 0 | 217.2 | 192.6 | 183.4 | 181.8 | 178.4 | 36.8 | 19.6 | 55.3 | 3.6 | 238.1 | 3.2 | 59.1 | 75.6 | 63 | 68.1 | 28.9 | 31.5 | 32.2 | 20.9 | 32.7 | 54.2 | 85.5 | 39.8 | 80.6 | 190.6 | 243.5 | 261 | 171.2 | 237.6 | 253.2
1234 | 1072 | -6.2 | 0 | 0 | 216.8 | 192.4 | 183.2 | 181.6 | 178.2 | 36.8 | 19.6 | 55.2 | 3.2 | 231.7 | 3.2 | 59.2 | 76.1 | 63.3 | 68.3 | 28.9 | 31.6 | 32.3 | 23.9 | 32.5 | 54.5 | 84.7 | 39.8 | 80.5 | 190.9 | 243.4 | 260.8 | 171.4 | 237.5 | 253.1
1235 | 1073 | -6.3 | 0 | 0 | 216.5 | 192.2 | 183 | 181.4 | 178 | 36.7 | 19.6 | 55.1 | 2.9 | 210.8 | 3.1 | 59.3 | 76.6 | 63.4 | 68.6 | 28.9 | 31.7 | 32.3 | 27 | 32.7 | 54.7 | 84.3 | 39.9 | 80.3 | 191.1 | 243.3 | 260.7 | 171.6 | 237.4 | 252.9
1236 | 1074 | -6.4 | 0 | 0 | 216.3 | 192 | 182.8 | 181.1 | 177.9 | 36.7 | 19.6 | 55 | 3.1 | 226.7 | 2.8 | 59.3 | 76.2 | 63.8 | 68.8 | 28.9 | 31.6 | 32.3 | 21 | 32.6 | 54.8 | 84.4 | 39.9 | 80.2 | 191.4 | 243.2 | 260.5 | 171.7 | 237.3 | 252.8
1237 | 1075 | -6.4 | 0 | 0 | 216 | 191.8 | 182.6 | 180.9 | 177.7 | 36.6 | 19.6 | 55 | 2.9 | 237.8 | 3.8 | 59.4 | 75.1 | 63.9 | 69 | 28.9 | 31.8 | 32.3 | 25.8 | 33.3 | 55 | 84.6 | 39.9 | 80.1 | 191.6 | 243.1 | 260.3 | 171.9 | 237.2 | 252.7
1238 | 1076 | -6.3 | 0 | 0 | 215.8 | 191.6 | 182.3 | 180.7 | 177.6 | 36.6 | 19.6 | 54.9 | 3.3 | 214.3 | 6 | 59.5 | 74.9 | 63.8 | 68.7 | 28.9 | 31.8 | 32.5 | 25 | 33.8 | 55.2 | 84.6 | 40 | 80.1 | 191.9 | 243 | 260.2 | 172.1 | 237.1 | 252.5
1239 | 1077 | -5.8 | 0 | 0 | 215.5 | 191.4 | 182 | 180.5 | 177.5 | 36.5 | 19.6 | 54.8 | 3.1 | 220 | 7.2 | 59.6 | 74.6 | 63.8 | 68.9 | 28.9 | 31.8 | 32.9 | 20.9 | 34.2 | 55.4 | 84.5 | 40 | 80 | 192.1 | 242.9 | 260 | 172.3 | 237 | 252.4
1240 | 1078 | -5.8 | 0 | 0 | 215.2 | 191.2 | 181.7 | 180.2 | 177.3 | 36.5 | 19.6 | 54.7 | 2.9 | 227.3 | 7.8 | 59.6 | 73.9 | 64 | 69 | 28.9 | 32 | 33.1 | 27.4 | 34.4 | 55.6 | 84.7 | 40 | 79.9 | 192.4 | 242.8 | 259.9 | 172.4 | 236.9 | 252.2
1241 | 1079 | -6.2 | 0 | 0 | 214.8 | 191 | 181.5 | 180 | 177.2 | 36.5 | 19.6 | 54.6 | 3.3 | 239.2 | 6.8 | 59.6 | 73.4 | 64 | 69.3 | 28.9 | 32 | 33.3 | 23 | 34.6 | 55.6 | 85 | 40.1 | 79.8 | 192.6 | 242.7 | 259.7 | 172.6 | 236.8 | 252.1
1242 | 1080 | -6.5 | 0 | 0 | 214.5 | 190.8 | 181.3 | 179.7 | 176.9 | 36.4 | 19.6 | 54.6 | 3.2 | 231.7 | 5.8 | 59.6 | 73 | 64 | 69.2 | 28.9 | 32 | 33.5 | 21 | 34.6 | 55.7 | 84.8 | 40.2 | 79.7 | 192.9 | 242.6 | 259.6 | 172.8 | 236.7 | 251.9
1243 | 1081 | -6.3 | 0 | 0 | 214.2 | 190.6 | 181 | 179.5 | 176.7 | 36.4 | 19.6 | 54.5 | 2.7 | 208.8 | 5.1 | 59.7 | 73 | 63.9 | 68.7 | 29 | 32.2 | 33.6 | 29 | 34 | 55.8 | 84.3 | 40.2 | 79.7 | 193.1 | 242.5 | 259.4 | 173 | 236.6 | 251.8
1244 | 1082 | -5.8 | 0 | 0 | 213.9 | 190.4 | 180.8 | 179.4 | 176.5 | 36.3 | 19.6 | 54.4 | 2.7 | 229.2 | 4.2 | 59.6 | 72.7 | 63.6 | 68.5 | 29 | 32 | 33.4 | 21.6 | 33.3 | 55.9 | 84.2 | 40.3 | 79.6 | 193.3 | 242.4 | 259.3 | 173.1 | 236.5 | 251.7
1245 | 1083 | -5.5 | 0 | 0 | 213.6 | 190.2 | 180.5 | 179.2 | 176.3 | 36.3 | 19.6 | 54.3 | 3.1 | 251.7 | 3.9 | 59.6 | 73 | 63.4 | 68.3 | 29 | 32.1 | 33.2 | 22.1 | 33 | 55.9 | 84.3 | 40.4 | 79.5 | 193.6 | 242.3 | 259.1 | 173.3 | 236.4 | 251.5
1246 | 1084 | -5.8 | 0 | 0 | 213.5 | 190 | 180.2 | 179 | 176.1 | 36.3 | 19.6 | 54.2 | 2.9 | 238.8 | 3.5 | 59.7 | 73 | 63.3 | 68.5 | 29 | 32.3 | 33.4 | 28.4 | 33.3 | 55.9 | 84.4 | 40.4 | 79.5 | 193.8 | 242.2 | 258.9 | 173.4 | 236.3 | 251.4
1247 | 1085 | -6 | 0 | 0 | 213.3 | 189.7 | 179.8 | 178.7 | 176 | 36.3 | 19.6 | 54.2 | 2.9 | 215.8 | 3.3 | 59.7 | 72.8 | 63.3 | 68.6 | 28.9 | 32.2 | 33.7 | 21.4 | 33.9 | 56 | 84.4 | 40.5 | 79.4 | 194 | 242.1 | 258.8 | 173.6 | 236.2 | 251.3
1248 | 1086 | -6.2 | 0 | 0 | 213.1 | 189.5 | 179.5 | 178.4 | 175.8 | 36.2 | 19.6 | 54.1 | 2.5 | 235.1 | 3.8 | 59.7 | 73.2 | 63.1 | 68.5 | 28.9 | 32.4 | 33.6 | 23.7 | 34.5 | 56.1 | 84.6 | 40.6 | 79.4 | 194.2 | 242 | 258.6 | 173.8 | 236.1 | 251.1
1249 | 1087 | -6 | 0 | 0 | 212.8 | 189.2 | 179.3 | 178.2 | 175.5 | 36.2 | 19.6 | 54 | 2.8 | 237.1 | 4.6 | 59.7 | 73.3 | 62.9 | 68.4 | 28.9 | 32.5 | 32.8 | 26.5 | 34.8 | 56.3 | 84.7 | 40.6 | 79.3 | 194.5 | 241.9 | 258.5 | 173.9 | 236 | 251
1250 | 1088 | -5.9 | 0 | 0 | 212.5 | 189.1 | 179.1 | 178 | 175.3 | 36.1 | 19.6 | 54 | 2.9 | 251.7 | 6.1 | 59.8 | 74 | 63 | 68.6 | 28.9 | 32.4 | 32.7 | 21 | 34.3 | 56.5 | 84.7 | 40.7 | 79.2 | 194.7 | 241.8 | 258.3 | 174.1 | 235.9 | 250.8
1251 | 1089 | -6.1 | 0 | 0 | 212.3 | 188.9 | 178.9 | 177.7 | 175.1 | 36 | 19.6 | 53.9 | 2.8 | 228.3 | 6.2 | 59.9 | 73.9 | 62.9 | 69.1 | 28.9 | 32.6 | 32.8 | 25.3 | 33.4 | 56.6 | 84.7 | 40.7 | 79.2 | 194.9 | 241.7 | 258.1 | 174.3 | 235.8 | 250.7
1252 | 1090 | -6.1 | 0 | 0 | 212 | 188.8 | 178.7 | 177.5 | 174.9 | 35.9 | 19.6 | 53.9 | 2.9 | 245.9 | 6 | 60 | 73.4 | 62.8 | 69.9 | 28.9 | 32.6 | 32.8 | 24.8 | 32.6 | 56.7 | 84.8 | 40.8 | 79.1 | 195.1 | 241.6 | 258 | 174.4 | 235.7 | 250.5
1253 | 1091 | -6.1 | 0 | 0 | 211.6 | 188.6 | 178.6 | 177.3 | 174.8 | 35.9 | 19.6 | 53.8 | 2.7 | 232.3 | 6.2 | 60.1 | 73.2 | 62.9 | 70.2 | 28.9 | 32.7 | 32.7 | 21 | 32.2 | 56.9 | 84.9 | 40.8 | 79.1 | 195.3 | 241.5 | 257.9 | 174.6 | 235.6 | 250.4
1254 | 1092 | -6.3 | 0 | 0 | 211.2 | 188.4 | 178.4 | 177.1 | 174.5 | 35.9 | 19.6 | 53.7 | 2.9 | 229.8 | 6.6 | 60.1 | 72.9 | 63 | 69.8 | 28.9 | 32.9 | 32.7 | 26.9 | 31.7 | 56.9 | 84.9 | 40.9 | 79 | 195.5 | 241.4 | 257.7 | 174.8 | 235.5 | 250.3
1255 | 1093 | -6.3 | 0 | 0 | 210.9 | 188.2 | 178.2 | 176.9 | 174.3 | 35.9 | 19.6 | 53.6 | 3 | 236.1 | 6.7 | 60.1 | 72.4 | 62.6 | 69.5 | 28.9 | 32.8 | 32.2 | 23.1 | 31.4 | 57 | 84.8 | 40.9 | 78.9 | 195.7 | 241.3 | 257.5 | 174.9 | 235.5 | 250.1
1256 | 1094 | -6.2 | 0 | 0 | 210.5 | 187.9 | 178 | 176.7 | 174 | 35.8 | 19.6 | 53.6 | 3.4 | 236.6 | 6.7 | 60.1 | 72.3 | 62.5 | 69.5 | 28.9 | 32.8 | 32.2 | 21 | 31.2 | 57.1 | 84.6 | 41 | 78.9 | 195.9 | 241.2 | 257.4 | 175.1 | 235.4 | 250
1257 | 1095 | -6 | 0 | 0 | 210.1 | 187.7 | 177.8 | 176.5 | 173.8 | 35.7 | 19.6 | 53.5 | 3.1 | 232.4 | 6.6 | 60.1 | 72.5 | 62.8 | 69.2 | 28.9 | 33 | 32.6 | 28.2 | 31.6 | 57.2 | 84.4 | 41 | 78.8 | 196 | 241.1 | 257.2 | 175.3 | 235.3 | 249.8
1258 | 1096 | -6.2 | 0 | 0 | 209.9 | 187.5 | 177.5 | 176.3 | 173.6 | 35.7 | 19.6 | 53.4 | 2.9 | 246.8 | 6.8 | 60.1 | 72.1 | 63 | 69.2 | 28.9 | 32.9 | 32.5 | 21.3 | 31.4 | 57.2 | 84.5 | 41.1 | 78.8 | 196.2 | 241 | 257.1 | 175.4 | 235.2 | 249.7
1259 | 1097 | -6.2 | 0 | 0 | 209.6 | 187.3 | 177.1 | 176 | 173.4 | 35.6 | 19.6 | 53.4 | 2.8 | 261.5 | 6.8 | 60 | 71.5 | 62.9 | 69.2 | 28.9 | 32.9 | 32.8 | 21.5 | 31.2 | 57.3 | 84.7 | 41.1 | 78.7 | 196.4 | 241 | 256.9 | 175.6 | 235.1 | 249.6
1260 | 1098 | -6.3 | 0 | 0 | 209.3 | 187.1 | 176.8 | 175.8 | 173.2 | 35.4 | 19.6 | 53.4 | 2.8 | 253.7 | 6.5 | 60 | 71.5 | 62.8 | 68.8 | 28.9 | 33.1 | 32.7 | 27.8 | 31 | 57.4 | 84.7 | 41.1 | 78.6 | 196.6 | 240.8 | 256.8 | 175.7 | 235 | 249.4
1261 | 1099 | -6.3 | 0 | 0 | 209.1 | 186.8 | 176.6 | 175.6 | 172.9 | 35.4 | 19.6 | 53.3 | 3 | 269.8 | 6.7 | 60 | 71.5 | 62.6 | 69 | 28.9 | 32.9 | 32.5 | 21.2 | 30.7 | 57.5 | 84.4 | 41.1 | 78.6 | 196.7 | 240.7 | 256.6 | 175.9 | 234.9 | 249.3
1262 | 1100 | -6.3 | 0 | 0 | 208.8 | 186.6 | 176.4 | 175.3 | 172.6 | 35.3 | 19.6 | 53.3 | 3 | 256.9 | 7.1 | 60.1 | 71.5 | 62.2 | 69 | 28.9 | 33 | 32.4 | 23.2 | 30.4 | 57.6 | 84.2 | 41.1 | 78.5 | 196.9 | 240.6 | 256.5 | 176.1 | 234.8 | 249.2
1263 | 1101 | -6.3 | 0 | 0 | 208.5 | 186.4 | 176.2 | 175.1 | 172.4 | 35.2 | 19.6 | 53.3 | 2.8 | 254.7 | 7 | 60.1 | 71.7 | 62.1 | 69.1 | 28.9 | 33.1 | 32.2 | 25.8 | 30.2 | 57.7 | 83.9 | 41.1 | 78.5 | 197.1 | 240.5 | 256.3 | 176.2 | 234.7 | 249
1264 | 1102 | -6.2 | 0 | 0 | 208.2 | 186.2 | 176.1 | 174.8 | 172.1 | 35.2 | 19.6 | 53.2 | 2.9 | 225.7 | 6.2 | 60.1 | 71.5 | 61.9 | 69 | 28.9 | 33 | 32.1 | 21.3 | 30 | 57.8 | 84 | 41.1 | 78.4 | 197.2 | 240.4 | 256.2 | 176.4 | 234.6 | 248.9
1265 | 1103 | -6.2 | 0 | 0 | 207.9 | 186 | 175.9 | 174.7 | 171.9 | 35.1 | 19.6 | 53.2 | 2.9 | 256.3 | 5.8 | 60 | 71 | 62.2 | 69.2 | 28.9 | 33 | 32.1 | 20.8 | 29.7 | 57.8 | 83.9 | 41.1 | 78.4 | 197.4 | 240.3 | 256 | 176.5 | 234.5 | 248.7
1266 | 1104 | -6.2 | 0 | 0 | 207.8 | 185.8 | 175.7 | 174.5 | 171.6 | 35 | 19.6 | 53.1 | 3.3 | 238.3 | 6.4 | 60 | 70.4 | 62.4 | 69 | 28.9 | 33 | 32 | 20.8 | 29.4 | 57.9 | 83.7 | 41.1 | 78.3 | 197.5 | 240.2 | 255.9 | 176.7 | 234.4 | 248.6
1267 | 1105 | -6.1 | 0 | 0 | 207.5 | 185.6 | 175.4 | 174.3 | 171.4 | 34.9 | 19.6 | 53 | 3.1 | 261.1 | 6.5 | 60 | 70 | 62.5 | 69.1 | 28.9 | 33.1 | 31.9 | 20.8 | 29.3 | 58.1 | 83.9 | 41.1 | 78.3 | 197.7 | 240.1 | 255.7 | 176.8 | 234.3 | 248.5
1268 | 1106 | -6 | 0 | 0 | 207.2 | 185.4 | 175.1 | 174 | 171.1 | 34.9 | 19.6 | 53 | 3 | 263.3 | 6.4 | 60 | 69.6 | 62.6 | 68.9 | 28.9 | 33.1 | 31.8 | 20.8 | 29.3 | 58.2 | 84 | 41.1 | 78.2 | 197.8 | 240 | 255.5 | 177 | 234.2 | 248.3
1269 | 1107 | -6.3 | 0 | 0 | 206.8 | 185.2 | 174.8 | 173.8 | 170.8 | 34.9 | 19.6 | 52.9 | 2.9 | 269.5 | 6.6 | 60 | 69.3 | 62.7 | 68.8 | 28.9 | 33.1 | 31.8 | 20.8 | 29.5 | 58.3 | 84.2 | 41.1 | 78.2 | 198 | 239.9 | 255.4 | 177.1 | 234.1 | 248.2
1270 | 1108 | -6 | 0 | 0 | 206.6 | 185 | 174.6 | 173.7 | 170.4 | 34.9 | 19.7 | 52.8 | 2.7 | 268.3 | 6.5 | 60 | 68.8 | 62.9 | 68.9 | 28.9 | 33.2 | 31 | 20.8 | 29.7 | 58.5 | 84.2 | 41.1 | 78.1 | 198.1 | 239.8 | 255.2 | 177.3 | 234 | 248
1271 | 1109 | -5.6 | 0 | 0 | 206.4 | 184.8 | 174.4 | 173.5 | 170.1 | 34.9 | 19.6 | 52.8 | 2.7 | 265.6 | 6.1 | 60 | 68.7 | 62.7 | 68.8 | 28.9 | 33.2 | 30.3 | 20.8 | 29.9 | 58.5 | 83.9 | 41.1 | 78 | 198.3 | 239.7 | 255.1 | 177.5 | 233.9 | 247.9
1272 | 1110 | -5.8 | 0 | 0 | 206.3 | 184.7 | 174.2 | 173.2 | 169.9 | 34.9 | 19.6 | 52.7 | 2.9 | 267 | 5.7 | 59.9 | 68.6 | 62.2 | 68.5 | 28.9 | 33.2 | 30.4 | 20.8 | 30.5 | 58.6 | 83.8 | 41.1 | 78 | 198.4 | 239.6 | 254.9 | 177.6 | 233.8 | 247.8
1273 | 1111 | -6.1 | 0 | 0 | 206 | 184.5 | 174 | 172.9 | 169.8 | 34.9 | 19.7 | 52.7 | 2.7 | 264.7 | 5.3 | 59.9 | 68.2 | 62 | 68.1 | 28.9 | 33.3 | 30.5 | 20.8 | 30.9 | 58.7 | 83.9 | 41.1 | 77.9 | 198.5 | 239.5 | 254.8 | 177.8 | 233.7 | 247.6
1274 | 1112 | -6.3 | 0 | 0 | 205.8 | 184.2 | 173.8 | 172.7 | 169.5 | 34.8 | 19.7 | 52.6 | 3.2 | 262.1 | 5 | 59.9 | 67.4 | 61.9 | 67.5 | 28.9 | 33.3 | 31.1 | 20.8 | 31.3 | 58.8 | 84.1 | 41.1 | 77.8 | 198.7 | 239.4 | 254.7 | 177.9 | 233.6 | 247.5
1275 | 1113 | -6.3 | 0 | 0 | 205.8 | 183.9 | 173.7 | 172.4 | 169.3 | 34.9 | 19.7 | 52.6 | 3 | 253.7 | 4.8 | 59.8 | 67.2 | 61.8 | 67.7 | 28.9 | 33.3 | 31.2 | 20.9 | 31.9 | 59 | 84.3 | 41.1 | 77.8 | 198.8 | 239.3 | 254.5 | 178.1 | 233.5 | 247.4
1276 | 1114 | -6.3 | 0 | 0 | 205.6 | 183.7 | 173.5 | 172.2 | 169 | 34.8 | 19.7 | 52.5 | 3.3 | 235.8 | 4.5 | 59.8 | 67.1 | 62.2 | 68.1 | 28.9 | 33.3 | 31.1 | 20.6 | 32.2 | 59.1 | 84.3 | 41 | 77.7 | 198.9 | 239.2 | 254.3 | 178.2 | 233.4 | 247.2
1277 | 1115 | -6.4 | 0 | 0 | 205.4 | 183.4 | 173.3 | 172 | 168.6 | 34.8 | 19.7 | 52.4 | 3.1 | 235.6 | 4.4 | 59.8 | 66.9 | 62.5 | 67.9 | 28.8 | 33.4 | 31 | 20.4 | 32.2 | 59.2 | 84.4 | 41 | 77.6 | 199.1 | 239.1 | 254.2 | 178.4 | 233.3 | 247.1
1278 | 1116 | -6.4 | 0 | 0 | 205.1 | 183.2 | 173.1 | 171.7 | 168.3 | 34.8 | 19.7 | 52.4 | 3 | 248.1 | 4.5 | 59.8 | 66.8 | 62.4 | 67.9 | 28.8 | 33.4 | 31.2 | 20.7 | 32.3 | 59.3 | 84.5 | 41 | 77.6 | 199.2 | 239 | 254 | 178.5 | 233.2 | 247
1279 | 1117 | -6.2 | 0 | 0 | 204.8 | 183.1 | 172.9 | 171.5 | 168.1 | 34.8 | 19.7 | 52.3 | 3.2 | 235.1 | 4.6 | 59.8 | 66.6 | 62.3 | 68.1 | 28.8 | 33.4 | 31.5 | 20.3 | 32 | 59.4 | 84.4 | 41 | 77.6 | 199.3 | 238.9 | 253.9 | 178.7 | 233.1 | 246.8
1280 | 1118 | -6.3 | 0 | 0 | 204.6 | 182.9 | 172.7 | 171.3 | 167.9 | 34.8 | 19.7 | 52.2 | 3.1 | 232.9 | 4.6 | 59.9 | 66.5 | 62.4 | 67.9 | 28.8 | 33.4 | 31.6 | 20.4 | 31.5 | 59.4 | 84.4 | 41 | 77.5 | 199.4 | 238.8 | 253.8 | 178.8 | 233.1 | 246.7