## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-7
Test Date: | 2006-11-08
Ignition Time Relative to Thermal Data: | 152 | s
Ignition Time Relative to Electrical Data: | 152 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Cable bundle in conduit at location E

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 7-1 |  |  |  | Location A | Location C - 6-cable bundle 7-3 |  |  |  | Location C | Location E - 3+1 bundle 7-4 in Conduit |  |  | Location G - 6-cable bundle 7-3 |  |  |  | Location G
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Cable 1 TC | Air Inside Conduit | Conduit Temp | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung
0 | -152 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 16.9 | 15.8 | 22.6 | 16.3 | 1.3 | 139.3 | 3.6 | 16 | 15.7 | 15.8 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
1 | -151 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 16.9 | 15.8 | 22.6 | 16.3 | 1.3 | 145.7 | 3.5 | 16 | 15.7 | 15.8 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
2 | -150 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 16.9 | 15.8 | 22.6 | 16.3 | 1.4 | 155.1 | 3.5 | 16 | 15.7 | 15.8 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.6 | 17.8
3 | -149 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 16.9 | 15.8 | 22.6 | 16.3 | 1.4 | 157.5 | 3.4 | 16 | 15.7 | 15.8 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
4 | -148 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.8 | 22.6 | 16.3 | 1.3 | 158.2 | 3.2 | 16 | 15.7 | 15.8 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
5 | -147 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 16.9 | 15.8 | 22.6 | 16.3 | 1.3 | 160 | 3.3 | 16 | 15.7 | 15.8 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
6 | -146 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.8 | 22.6 | 16.3 | 1.4 | 162.7 | 3.4 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.6 | 17.8
7 | -145 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.8 | 22.6 | 16.3 | 1.3 | 170.4 | 3.2 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
8 | -144 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 181.2 | 3.1 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
9 | -143 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 189.5 | 2.9 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.6 | 17.8
10 | -142 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 194.3 | 2.6 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.6 | 17.8
11 | -141 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.2 | 201.9 | 2.7 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
12 | -140 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.4 | 206.2 | 3.3 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
13 | -139 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.5 | 196.3 | 4.1 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
14 | -138 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.4 | 176.7 | 5 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
15 | -137 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 175.8 | 5.3 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.1 | 16.2 | 16.5 | 17.8
16 | -136 | -6.5 | 0 | 0 | 16.8 | 17.1 | 16.9 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 180.9 | 5.3 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.6 | 17.8
17 | -135 | -6.5 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 187.5 | 5.4 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
18 | -134 | -6.4 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.4 | 191.1 | 5.3 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
19 | -133 | -6.5 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.5 | 184.7 | 5.4 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.1 | 16.2 | 16.5 | 17.8
20 | -132 | -6.6 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.4 | 179.5 | 5.3 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.1 | 16.2 | 16.5 | 17.8
21 | -131 | -6.6 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.2 | 178.4 | 5.1 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.6 | 17.8
22 | -130 | -6.7 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.1 | 162.4 | 5.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
23 | -129 | -6.7 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.2 | 174.8 | 5.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.6 | 17.8
24 | -128 | -6.8 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.1 | 192.3 | 5.6 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.6 | 17.8
25 | -127 | -6.8 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.2 | 186.8 | 5.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
26 | -126 | -6.8 | 0 | 0 | 16.8 | 17.1 | 16.9 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.2 | 187.1 | 6.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
27 | -125 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 191.9 | 5.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
28 | -124 | -6.4 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.3 | 193.9 | 5.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
29 | -123 | -6.4 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.3 | 209 | 5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
30 | -122 | -6.4 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17 | 15.9 | 22.6 | 16.3 | 1.4 | 189 | 4.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
31 | -121 | -6.4 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.4 | 178.2 | 4.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
32 | -120 | -6.5 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.5 | 193 | 4.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
33 | -119 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.3 | 202.6 | 4.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
34 | -118 | -6.7 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.3 | 193.2 | 4 | 16 | 15.7 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
35 | -117 | -5.9 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.2 | 197.7 | 3.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
36 | -116 | 0.4 | 0.16 | 0.18703 | 16.8 | 17.1 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.2 | 209.5 | 3.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.3 | 16.6 | 17.8
37 | -115 | -4 | 0 | 0 | 16.8 | 17.1 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.2 | 213.9 | 4.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.3 | 16.6 | 17.8
38 | -114 | -6.9 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 210.6 | 4.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.8
39 | -113 | -6.8 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.2 | 182.2 | 4.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.3 | 16.5 | 17.8
40 | -112 | -6.8 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 0.9 | 183.6 | 4.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.3 | 16.5 | 17.8
41 | -111 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1 | 197.1 | 4.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.8
42 | -110 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1 | 195.2 | 4.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.8
43 | -109 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 203.1 | 4.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.6 | 17.8
44 | -108 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.2 | 211.1 | 4.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.3 | 16.5 | 17.8
45 | -107 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 208 | 4.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.8
46 | -106 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.4 | 1 | 196.6 | 5.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.6 | 17.8
47 | -105 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 193.7 | 5.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.8
48 | -104 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 201.7 | 5.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
49 | -103 | -6.3 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 16 | 22.6 | 16.3 | 1.2 | 208.9 | 5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
50 | -102 | -6.1 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 16 | 22.6 | 16.3 | 1.4 | 204.3 | 5.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
51 | -101 | -6.2 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.3 | 197.6 | 5.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
52 | -100 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.4 | 228 | 5.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
53 | -99 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.6 | 207.3 | 5.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
54 | -98 | -6.3 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.5 | 202.6 | 6.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
55 | -97 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.4 | 205.7 | 6.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
56 | -96 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.4 | 200.1 | 6.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.8 | 16.2 | 16.2 | 16.5 | 17.8
57 | -95 | -6.4 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.3 | 199.1 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
58 | -94 | -6.5 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 196.2 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
59 | -93 | -6.5 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1 | 191.5 | 6.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
60 | -92 | -6.4 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 185.7 | 6.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
61 | -91 | -6.5 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.6 | 16.3 | 1.1 | 186.5 | 6.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
62 | -90 | -6.7 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 186.9 | 5.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
63 | -89 | -6.7 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 184.2 | 5.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
64 | -88 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 223.2 | 5.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
65 | -87 | -6.7 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 223 | 4.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
66 | -86 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 207 | 4.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
67 | -85 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 220.7 | 3.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
68 | -84 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 236.9 | 3.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
69 | -83 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 230.5 | 3.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
70 | -82 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 0.9 | 206.1 | 3.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
71 | -81 | -6.4 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 0.9 | 187.3 | 3.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
72 | -80 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1 | 191.4 | 4.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
73 | -79 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 201.8 | 4.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
74 | -78 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.4 | 197.9 | 4.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
75 | -77 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.3 | 188 | 4.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
76 | -76 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.3 | 177.7 | 4.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
77 | -75 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.3 | 180.6 | 4.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
78 | -74 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 192.3 | 4.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
79 | -73 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.3 | 189.4 | 4.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
80 | -72 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 177.7 | 5.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
81 | -71 | -6.7 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 172.5 | 6.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
82 | -70 | -6.8 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.3 | 171.6 | 6.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
83 | -69 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 167.7 | 6.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
84 | -68 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 168.3 | 6.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
85 | -67 | -6.8 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 179.5 | 6.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
86 | -66 | -6.8 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 186.6 | 5.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
87 | -65 | -6.8 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 191.1 | 4.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
88 | -64 | -6.6 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 191 | 5.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
89 | -63 | -6.4 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 203 | 5.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
90 | -62 | -6.4 | 0 | 0 | 16.8 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.1 | 210.7 | 5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
91 | -61 | -6.6 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 180.3 | 5.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
92 | -60 | -6.3 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 157.3 | 6.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
93 | -59 | -6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 181 | 5.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
94 | -58 | -6.1 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 194.1 | 5.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
95 | -57 | -6.4 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.1 | 185.1 | 6.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
96 | -56 | -6.1 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.2 | 165 | 6.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
97 | -55 | -5.8 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.1 | 176.3 | 5.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
98 | -54 | -5.8 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.1 | 173.1 | 6.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
99 | -53 | -6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 180.4 | 6.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
100 | -52 | -6.3 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1 | 181.7 | 7.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
101 | -51 | -6.5 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.3 | 181.6 | 8.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
102 | -50 | -6.5 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.2 | 180.5 | 8.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
103 | -49 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.8 | 22.5 | 16.3 | 1.3 | 179.8 | 7.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
104 | -48 | -6.6 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 181.8 | 8.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
105 | -47 | -6.7 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 185.3 | 9.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
106 | -46 | -6.8 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 183.2 | 10.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
107 | -45 | -6.8 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.3 | 180.4 | 9.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
108 | -44 | -6.7 | 0 | 0 | 16.9 | 17 | 16.7 | 16.8 | 17.1 | 15.9 | 22.5 | 16.3 | 1 | 178.3 | 9.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
109 | -43 | -6.6 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1 | 181.6 | 8.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
110 | -42 | -6.7 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 0.9 | 179 | 8.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
111 | -41 | -6.7 | 0 | 0 | 16.9 | 17 | 16.7 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1 | 172.3 | 8.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
112 | -40 | -5.9 | 0 | 0 | 16.9 | 17 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1 | 179.3 | 7.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
113 | -39 | -5.1 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 184.4 | 7.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
114 | -38 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.5 | 16.3 | 1.1 | 179.6 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
115 | -37 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.7 | 16.8 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 180.1 | 6.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
116 | -36 | -6.6 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.8 | 17.1 | 15.9 | 22.5 | 16.3 | 1.2 | 177.4 | 6.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
117 | -35 | -5.4 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 16 | 22.5 | 16.3 | 1.3 | 177.4 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
118 | -34 | -4.3 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 16 | 22.5 | 16.3 | 1.2 | 178 | 7.8 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
119 | -33 | -4.6 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 16 | 22.5 | 16.3 | 1.1 | 173.7 | 8.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
120 | -32 | -5.7 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 16 | 22.4 | 16.3 | 1.3 | 173 | 8.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
121 | -31 | -5.7 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 16 | 22.4 | 16.3 | 1.2 | 176.7 | 8.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
122 | -30 | -6.2 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 16 | 22.4 | 16.3 | 1.2 | 185.1 | 7.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
123 | -29 | -6.2 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 190 | 6.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
124 | -28 | -6.3 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 184.5 | 6.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
125 | -27 | -6 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 175.1 | 7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
126 | -26 | -6.4 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 175 | 7.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
127 | -25 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 178.6 | 7.2 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
128 | -24 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 179.1 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
129 | -23 | -6.8 | 0 | 0 | 16.8 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 0.9 | 185.8 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
130 | -22 | -6.8 | 0 | 0 | 16.8 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 180.3 | 6.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
131 | -21 | -6.8 | 0 | 0 | 16.8 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 178.6 | 7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
132 | -20 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 186.7 | 6.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.8 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
133 | -19 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 186.2 | 6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.6 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
134 | -18 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 0.9 | 183.2 | 5.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
135 | -17 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 183.6 | 4.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
136 | -16 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 175 | 4.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
137 | -15 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 169.5 | 4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
138 | -14 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 173.8 | 3.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
139 | -13 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 175.9 | 3.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
140 | -12 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 177 | 4.3 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
141 | -11 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.3 | 177.2 | 4.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
142 | -10 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 182.2 | 4.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
143 | -9 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 195.9 | 4.7 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
144 | -8 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 195.5 | 4.9 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
145 | -7 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.3 | 180.3 | 5.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
146 | -6 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 183 | 5.6 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
147 | -5 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 182.1 | 5.5 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.1 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
148 | -4 | -6.8 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.1 | 183.5 | 5.4 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
149 | -3 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 175.2 | 5.1 | 16 | 15.6 | 15.7 | 16.3 | 16.9 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
150 | -2 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.3 | 175.5 | 5.1 | 16 | 15.6 | 15.7 | 16.3 | 17 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
151 | -1 | -6.9 | 0 | 0 | 16.9 | 16.9 | 16.8 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 177.2 | 5.6 | 16 | 15.6 | 15.7 | 16.3 | 17 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.8 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
152 | 0 | 101.4 | 40.56 | 47.4123 | 16.9 | 17 | 16.9 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 179 | 6 | 16 | 15.6 | 15.7 | 16.3 | 17 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
153 | 1 | 364.9 | 145.96 | 170.6188 | 16.9 | 17 | 16.9 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 177.9 | 6.6 | 16 | 15.6 | 15.7 | 16.3 | 17 | 16.2 | 15.7 | 16.4 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
154 | 2 | 444.4 | 177.76 | 207.7912 | 16.9 | 16.9 | 16.9 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 184 | 6.6 | 16 | 15.6 | 15.7 | 16.3 | 17 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.6 | 17.8
155 | 3 | 436.2 | 174.48 | 203.9571 | 16.9 | 17 | 16.9 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1.2 | 194.1 | 6.8 | 16 | 15.6 | 15.7 | 16.3 | 17 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
156 | 4 | 405.5 | 162.2 | 189.6025 | 16.8 | 17 | 16.9 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 185.5 | 6.8 | 16 | 15.7 | 16.1 | 16.3 | 17 | 16.2 | 15.7 | 16.5 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
157 | 5 | 384.8 | 153.92 | 179.9236 | 16.9 | 17 | 16.9 | 16.9 | 17.1 | 15.9 | 22.4 | 16.3 | 1 | 161.6 | 6.3 | 16 | 16.7 | 17.8 | 16.3 | 17.2 | 16.2 | 15.7 | 17 | 16.1 | 17 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.2 | 16.5 | 17.8
158 | 6 | 377.5 | 151 | 176.5103 | 16.9 | 17 | 17 | 17 | 17.1 | 15.9 | 22.4 | 16.3 | 1.3 | 167.5 | 5.6 | 16 | 20.8 | 26.8 | 16.3 | 18.1 | 16.2 | 17 | 21.7 | 16.1 | 17.7 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.9
159 | 7 | 373.3 | 149.32 | 174.5465 | 16.9 | 17 | 17.1 | 17.1 | 21.7 | 15.9 | 22.4 | 16.3 | 1.3 | 194.6 | 5.8 | 16 | 28.2 | 45.8 | 16.3 | 20 | 16.2 | 21.3 | 31.9 | 16.2 | 19 | 16.6 | 16.9 | 17.7 | 16.7 | 16.2 | 16.3 | 16.5 | 17.9
160 | 8 | 360.1 | 144.04 | 168.3745 | 17 | 17 | 17.3 | 17.3 | 35.3 | 15.9 | 22.4 | 16.3 | 1.4 | 185.4 | 6 | 16 | 39.7 | 72.4 | 16.4 | 22.4 | 16.2 | 29.7 | 47 | 16.5 | 21.4 | 16.6 | 16.9 | 17.8 | 16.7 | 16.2 | 16.4 | 16.5 | 18
161 | 9 | 354.6 | 141.84 | 165.8028 | 17.1 | 17.1 | 17.5 | 17.4 | 51.9 | 16 | 22.4 | 16.3 | 1.2 | 165.1 | 5.7 | 16 | 53.7 | 106.8 | 16.4 | 25.2 | 16.2 | 38.4 | 62 | 17 | 23.9 | 16.6 | 16.9 | 17.8 | 16.7 | 16.3 | 16.5 | 16.5 | 18.1
162 | 10 | 352.5 | 141 | 164.8209 | 17.3 | 17.2 | 17.7 | 17.7 | 70.2 | 16 | 22.4 | 16.3 | 1.4 | 180.2 | 5.1 | 16 | 71.5 | 131.5 | 16.4 | 27.7 | 16.2 | 48.8 | 84.5 | 17.7 | 27.3 | 16.6 | 16.9 | 17.9 | 16.7 | 16.4 | 16.6 | 16.5 | 18.2
163 | 11 | 351 | 140.4 | 164.1195 | 17.5 | 17.3 | 18.5 | 18.5 | 85.3 | 16 | 22.4 | 16.3 | 1.6 | 188.1 | 4.8 | 16 | 86.1 | 157.7 | 16.5 | 30.5 | 16.2 | 56.2 | 96 | 18.1 | 28.8 | 16.6 | 16.9 | 18 | 16.7 | 16.6 | 16.7 | 16.5 | 18.2
164 | 12 | 350.9 | 140.36 | 164.0728 | 17.7 | 17.4 | 19.5 | 19.4 | 96.9 | 16.1 | 22.4 | 16.3 | 1.7 | 178 | 4.6 | 16 | 109.7 | 204.6 | 16.6 | 34.8 | 16.2 | 64.1 | 108.9 | 18.7 | 31.4 | 16.6 | 16.9 | 18 | 16.7 | 17.6 | 16.9 | 16.5 | 18.4
165 | 13 | 353.3 | 141.32 | 165.1949 | 17.9 | 17.6 | 20.7 | 20.7 | 108 | 16.1 | 22.4 | 16.3 | 1.7 | 176.2 | 4.6 | 16.1 | 145.8 | 251.2 | 16.6 | 40.4 | 16.3 | 76.4 | 143.2 | 19.4 | 37.1 | 16.6 | 17 | 18.2 | 16.7 | 18.3 | 17.1 | 16.5 | 18.5
166 | 14 | 353.8 | 141.52 | 165.4287 | 18.3 | 18 | 22 | 22.2 | 125 | 16.1 | 22.4 | 16.3 | 1.7 | 189.4 | 4.1 | 16.1 | 172.8 | 275.4 | 16.7 | 43.5 | 16.3 | 88.9 | 165.4 | 20.2 | 41 | 16.6 | 17 | 18.3 | 16.7 | 20.7 | 17.8 | 16.5 | 18.7
167 | 15 | 354.9 | 141.96 | 165.9431 | 19.9 | 19.5 | 23.4 | 23.8 | 148.1 | 16.2 | 22.4 | 16.3 | 1.6 | 197.8 | 4.2 | 16.2 | 203.7 | 325 | 16.7 | 49.9 | 16.4 | 104.7 | 192.4 | 20.9 | 47 | 16.6 | 17.1 | 18.5 | 16.7 | 24.8 | 19.3 | 16.5 | 19
168 | 16 | 356.5 | 142.6 | 166.6912 | 22.2 | 22 | 25.1 | 25.6 | 169.8 | 16.2 | 22.4 | 16.3 | 1.6 | 195.9 | 3.9 | 16.2 | 227.4 | 345 | 16.8 | 55.4 | 16.5 | 115.4 | 206.5 | 21.7 | 51.5 | 16.6 | 17.1 | 18.7 | 16.8 | 28.8 | 21.6 | 16.5 | 19.4
169 | 17 | 356.9 | 142.76 | 166.8782 | 24.4 | 25.1 | 26.8 | 27.5 | 180.6 | 16.2 | 22.4 | 16.3 | 1.7 | 195.7 | 3.6 | 16.3 | 262.2 | 383.6 | 16.9 | 61.3 | 16.5 | 130.3 | 244.7 | 22.5 | 56.6 | 16.6 | 17.2 | 18.8 | 16.8 | 32.4 | 22.9 | 16.5 | 19.7
170 | 18 | 358 | 143.2 | 167.3925 | 26.6 | 27.3 | 28.8 | 29.6 | 213.9 | 16.3 | 22.4 | 16.3 | 1.6 | 196.5 | 3.4 | 16.3 | 306.1 | 422.9 | 17 | 67 | 16.7 | 152.2 | 291.2 | 23.7 | 63.8 | 16.6 | 17.2 | 19 | 16.8 | 36.5 | 24.2 | 16.5 | 20
171 | 19 | 358.4 | 143.36 | 167.5796 | 28.7 | 29.3 | 31 | 31.8 | 244.1 | 16.3 | 22.4 | 16.3 | 1.3 | 187.7 | 4.3 | 16.4 | 348.8 | 461.8 | 17.1 | 73.9 | 16.8 | 171.8 | 327.5 | 25.1 | 71.3 | 16.6 | 17.3 | 19.2 | 16.8 | 42.9 | 26 | 16.5 | 20.3
172 | 20 | 358 | 143.2 | 167.3925 | 31.4 | 32.1 | 33.6 | 34.1 | 265.5 | 16.3 | 22.4 | 16.3 | 1.4 | 173 | 5.9 | 16.5 | 388.3 | 488.1 | 17.3 | 79 | 16.9 | 196.9 | 364 | 26.5 | 80.4 | 16.6 | 17.4 | 19.3 | 16.8 | 49.9 | 28.9 | 16.5 | 20.6
173 | 21 | 358.9 | 143.56 | 167.8134 | 34.1 | 35.5 | 36.3 | 36.6 | 286.5 | 16.4 | 22.4 | 16.4 | 1.5 | 148 | 6.6 | 16.7 | 432.8 | 512.6 | 17.5 | 83 | 17.1 | 219.5 | 409.2 | 28.2 | 88.8 | 16.6 | 17.4 | 19.6 | 16.8 | 54 | 32.1 | 16.5 | 21.1
174 | 22 | 360.5 | 144.2 | 168.5615 | 38.5 | 38.9 | 39.2 | 39.4 | 309.1 | 16.4 | 22.4 | 16.4 | 1.7 | 170.6 | 6.9 | 16.9 | 475.2 | 535.9 | 17.7 | 87.5 | 17.3 | 243.5 | 445.2 | 30.3 | 98.1 | 16.6 | 17.5 | 19.8 | 16.8 | 58 | 34.5 | 16.5 | 21.5
175 | 23 | 361.5 | 144.6 | 169.0291 | 41.8 | 42 | 42.5 | 42.6 | 316.3 | 16.4 | 22.4 | 16.4 | 1.7 | 181.2 | 7.8 | 17.1 | 502.9 | 566.5 | 17.9 | 91.3 | 17.5 | 258.8 | 456.6 | 31.5 | 103.8 | 16.6 | 17.6 | 20.1 | 16.8 | 61.6 | 36.5 | 16.5 | 21.9
176 | 24 | 361.8 | 144.72 | 169.1693 | 45.7 | 45.9 | 45.8 | 46.2 | 317.6 | 16.5 | 22.4 | 16.4 | 1.7 | 161 | 7.9 | 17.4 | 535.5 | 583 | 18.2 | 95.2 | 17.7 | 273.7 | 480.4 | 31.6 | 111.8 | 16.6 | 17.7 | 20.2 | 16.8 | 64.4 | 39.6 | 16.5 | 22.1
177 | 25 | 362.1 | 144.84 | 169.3096 | 49.6 | 49.6 | 49.5 | 49.7 | 316.1 | 16.5 | 22.4 | 16.5 | 1.6 | 165.9 | 8.9 | 17.8 | 547.7 | 579.9 | 18.5 | 99 | 18.1 | 288 | 484.4 | 32 | 119.4 | 16.6 | 17.8 | 20.3 | 16.9 | 69.9 | 42.3 | 16.6 | 22.8
178 | 26 | 363.5 | 145.4 | 169.9642 | 53.1 | 53.7 | 53.2 | 52.9 | 321.1 | 16.5 | 22.4 | 16.5 | 1.6 | 176.4 | 9.4 | 18.3 | 580.5 | 610 | 18.8 | 105.7 | 18.4 | 304.8 | 510.9 | 33 | 127.3 | 16.6 | 17.9 | 20.4 | 16.9 | 75.8 | 46.1 | 16.6 | 23.4
179 | 27 | 364.2 | 145.68 | 170.2915 | 56.8 | 57.8 | 57 | 56.2 | 324.9 | 16.6 | 22.4 | 16.6 | 1.6 | 170.8 | 9.8 | 18.7 | 594.3 | 637.2 | 19.2 | 110.4 | 18.8 | 314 | 517 | 33.2 | 133.9 | 16.6 | 18 | 20.5 | 16.9 | 80.3 | 49.8 | 16.6 | 24.1
180 | 28 | 364.2 | 145.68 | 170.2915 | 60.3 | 61.6 | 60.8 | 59.4 | 319.5 | 16.6 | 22.3 | 16.6 | 1.7 | 175.5 | 9.7 | 19.3 | 601.3 | 647.6 | 19.6 | 116.6 | 19.3 | 318.8 | 511.5 | 33.7 | 138 | 16.6 | 18.1 | 20.8 | 16.9 | 84.2 | 53.2 | 16.6 | 24.9
181 | 29 | 362.7 | 145.08 | 169.5902 | 62.8 | 65.9 | 64.6 | 62.2 | 312 | 16.6 | 22.3 | 16.7 | 1.8 | 176.3 | 8.7 | 19.9 | 620.4 | 665.7 | 20.2 | 127.4 | 19.7 | 330.4 | 528.9 | 34.1 | 147 | 16.6 | 18.1 | 21.1 | 16.9 | 85.2 | 56.7 | 16.6 | 25.7
182 | 30 | 364.9 | 145.96 | 170.6188 | 66 | 70.1 | 68.2 | 65 | 313.2 | 16.7 | 22.3 | 16.8 | 1.9 | 186.6 | 7.7 | 20.5 | 625.8 | 674.2 | 20.8 | 133 | 20.2 | 335.5 | 531.5 | 34.6 | 152 | 16.6 | 18.2 | 21.2 | 17 | 86.2 | 59.8 | 16.6 | 26.5
183 | 31 | 364.8 | 145.92 | 170.5721 | 68.5 | 74.9 | 71.7 | 67.9 | 320.8 | 16.7 | 22.3 | 17.1 | 1.7 | 215.2 | 6.3 | 21.1 | 644.2 | 682.2 | 21.5 | 139.9 | 20.7 | 345 | 554.1 | 35.2 | 159 | 16.6 | 18.3 | 21.5 | 17 | 88.2 | 62.2 | 16.6 | 26.9
184 | 32 | 365.7 | 146.28 | 170.9929 | 72.2 | 79.3 | 75 | 70.6 | 327.5 | 16.7 | 22.3 | 17.3 | 1.6 | 231 | 5.3 | 21.7 | 655.5 | 678.9 | 22.3 | 143.8 | 21.2 | 348 | 557.1 | 36.6 | 165.5 | 16.6 | 18.4 | 21.9 | 17 | 90.2 | 64.3 | 16.7 | 27.2
185 | 33 | 366.5 | 146.6 | 171.367 | 76 | 82.2 | 78.3 | 73.4 | 334 | 16.7 | 22.3 | 17.6 | 1.9 | 215.7 | 3.8 | 22.4 | 647.9 | 671 | 23.2 | 147.3 | 21.8 | 349.9 | 547.2 | 37.7 | 168 | 16.6 | 18.5 | 22.2 | 17 | 92.3 | 67.1 | 16.7 | 27.7
186 | 34 | 367.5 | 147 | 171.8345 | 78.4 | 86.2 | 81.8 | 76.5 | 326.4 | 16.7 | 22.3 | 17.9 | 1.7 | 188.7 | 3 | 23.1 | 647.3 | 656.3 | 24.4 | 149.6 | 22.3 | 350.7 | 542 | 38.9 | 171.1 | 16.6 | 18.6 | 22.3 | 17.1 | 94.3 | 69.9 | 16.7 | 28.3
187 | 35 | 367.3 | 146.92 | 171.741 | 81.6 | 89.6 | 84.7 | 79.9 | 327 | 16.8 | 22.3 | 18.1 | 1.7 | 169.5 | 2.8 | 23.8 | 643.8 | 642.6 | 25.8 | 150.7 | 22.9 | 354.9 | 533.8 | 39.9 | 174.8 | 16.6 | 18.8 | 22.5 | 17.1 | 96.2 | 72.7 | 16.7 | 28.5
188 | 36 | 367.6 | 147.04 | 171.8813 | 85.7 | 92.8 | 87.7 | 83.1 | 324.3 | 16.8 | 22.3 | 18.4 | 2 | 167.8 | 2.6 | 24.5 | 657.1 | 651.1 | 29.5 | 154.6 | 23.5 | 357.5 | 548.7 | 40.6 | 179 | 16.6 | 18.9 | 22.6 | 17.1 | 98.1 | 74.9 | 16.8 | 28.9
189 | 37 | 369.2 | 147.68 | 172.6294 | 89.3 | 96.7 | 90.7 | 86.2 | 322.6 | 16.8 | 22.3 | 18.8 | 1.7 | 171 | 2.3 | 25.2 | 655.5 | 638.4 | 38.8 | 156.9 | 24.1 | 359.4 | 538.6 | 42.3 | 181.7 | 16.6 | 19 | 22.5 | 17.1 | 100.9 | 76.7 | 16.8 | 29.4
190 | 38 | 368.3 | 147.32 | 172.2086 | 92.3 | 99.5 | 93.4 | 89.6 | 321.3 | 16.8 | 22.3 | 19.1 | 1.8 | 171.2 | 2.3 | 26 | 649.7 | 622.6 | 46.1 | 158.6 | 24.8 | 356.2 | 529.3 | 42.8 | 183.7 | 16.6 | 19.1 | 22.8 | 17.2 | 103.7 | 78.7 | 16.8 | 29.9
191 | 39 | 370.2 | 148.08 | 173.097 | 94.4 | 102.9 | 96.5 | 92.8 | 322.2 | 16.8 | 22.3 | 19.5 | 1.6 | 176.8 | 3.3 | 26.8 | 642.2 | 596.8 | 51.3 | 159.1 | 25.5 | 353.3 | 516.8 | 44 | 185.4 | 16.6 | 19.2 | 23.2 | 17.2 | 106.4 | 81.6 | 16.9 | 30.5
192 | 40 | 370.3 | 148.12 | 173.1437 | 98.1 | 106.2 | 99.9 | 95.6 | 319.6 | 16.9 | 22.3 | 19.9 | 1.8 | 195.4 | 4.6 | 27.6 | 641.6 | 583.7 | 56.1 | 160.9 | 26.2 | 353.5 | 513.6 | 45.6 | 189.7 | 16.6 | 19.3 | 23.3 | 17.2 | 109.6 | 84.1 | 16.9 | 31.1
193 | 41 | 370.1 | 148.04 | 173.0502 | 102.1 | 109.5 | 103 | 98.7 | 318.5 | 16.9 | 22.3 | 20.2 | 1.9 | 194.8 | 5.5 | 28.5 | 625.7 | 589.4 | 59.2 | 164.7 | 27 | 352.4 | 503.7 | 46.5 | 191.4 | 16.6 | 19.5 | 23.6 | 17.3 | 112.3 | 86.5 | 17 | 31.6
194 | 42 | 371.3 | 148.52 | 173.6113 | 105.6 | 112 | 106 | 102.1 | 314.9 | 16.9 | 22.3 | 20.6 | 1.8 | 198.4 | 6.1 | 29.4 | 627.8 | 591.2 | 64.9 | 168.9 | 27.7 | 350.6 | 505 | 47.3 | 194.4 | 16.6 | 19.6 | 23.8 | 17.3 | 114.4 | 89.8 | 17 | 32.2
195 | 43 | 371.9 | 148.76 | 173.8919 | 107.9 | 114.9 | 109.4 | 105.2 | 309.7 | 17 | 22.3 | 21 | 1.9 | 189.1 | 7.2 | 30.3 | 620 | 589.3 | 69.9 | 173.2 | 28.5 | 347.2 | 493.1 | 48.7 | 196.7 | 16.6 | 19.7 | 23.9 | 17.4 | 117.7 | 92.6 | 17 | 33
196 | 44 | 370.2 | 148.08 | 173.097 | 111.3 | 116.9 | 112.5 | 107.9 | 300.2 | 17 | 22.3 | 21.4 | 1.9 | 183.1 | 7.7 | 31.3 | 603.8 | 583.1 | 73.4 | 175.2 | 29.2 | 341.1 | 477 | 49.2 | 196.1 | 16.6 | 19.9 | 24.1 | 17.4 | 121.3 | 95.2 | 17.1 | 33.7
197 | 45 | 371.1 | 148.44 | 173.5178 | 115.8 | 119.3 | 115.5 | 110.4 | 294.3 | 17 | 22.3 | 21.7 | 2.1 | 187.7 | 7.6 | 32.3 | 597.8 | 592.7 | 78.5 | 179.2 | 30 | 338.3 | 474.2 | 49.8 | 197.5 | 16.6 | 20 | 24.3 | 17.4 | 123.1 | 97.5 | 17.1 | 34.4
198 | 46 | 372.3 | 148.92 | 174.0789 | 118.4 | 122.2 | 118.3 | 112.4 | 289.1 | 17.1 | 22.3 | 22.1 | 2 | 186.8 | 7.8 | 33.3 | 598.4 | 611 | 84.7 | 183.5 | 30.8 | 336.5 | 475 | 51 | 199.4 | 16.6 | 20.1 | 24.4 | 17.5 | 124.4 | 99.5 | 17.2 | 34.8
199 | 47 | 373 | 149.2 | 174.4062 | 121.2 | 124.3 | 120.7 | 114.5 | 290.6 | 17.1 | 22.3 | 22.4 | 1.8 | 180.3 | 8.4 | 34.3 | 614.1 | 624.9 | 92.2 | 188.9 | 31.7 | 341.4 | 494.3 | 51.8 | 205.4 | 16.6 | 20.2 | 24.8 | 17.5 | 126.3 | 101.7 | 17.2 | 35.2
200 | 48 | 372.7 | 149.08 | 174.2659 | 123 | 127.1 | 123.1 | 116.6 | 293.7 | 17.1 | 22.3 | 22.7 | 1.8 | 179.3 | 8.5 | 35.3 | 623.4 | 638.9 | 97.9 | 196.3 | 32.5 | 348.3 | 505 | 53 | 210.8 | 16.6 | 20.4 | 25.1 | 17.6 | 127.7 | 104.2 | 17.3 | 35.8
201 | 49 | 372.9 | 149.16 | 174.3594 | 124.7 | 130.5 | 125.4 | 118.7 | 299.3 | 17.2 | 22.3 | 23.1 | 1.8 | 185.1 | 8.4 | 36.4 | 627.6 | 660.3 | 105.3 | 202.3 | 33.3 | 350 | 505.5 | 53.9 | 214.8 | 16.6 | 20.5 | 25.4 | 17.6 | 129.5 | 106.5 | 17.3 | 36.4
202 | 50 | 373.4 | 149.36 | 174.5932 | 126.2 | 133.9 | 127.7 | 121 | 309.2 | 17.2 | 22.3 | 23.4 | 2 | 184.9 | 8.4 | 37.5 | 622.5 | 652.2 | 109.2 | 207.6 | 34.2 | 352.9 | 513.9 | 55 | 219.1 | 16.6 | 20.7 | 25.6 | 17.6 | 130.6 | 109 | 17.4 | 36.9
203 | 51 | 373.4 | 149.36 | 174.5932 | 127.9 | 136 | 129.9 | 123.5 | 311.2 | 17.3 | 22.3 | 23.7 | 2.1 | 193.6 | 8.2 | 38.7 | 612.7 | 646.5 | 114.1 | 212.8 | 35.1 | 351.8 | 506.7 | 56.1 | 220.4 | 16.6 | 20.8 | 25.7 | 17.7 | 132.2 | 111.2 | 17.4 | 37.5
204 | 52 | 374 | 149.6 | 174.8738 | 128.8 | 137.8 | 131.8 | 125.8 | 304 | 17.3 | 22.3 | 24 | 2.1 | 195.1 | 7.8 | 40 | 605 | 646.5 | 120.1 | 215.5 | 36 | 345.8 | 488.2 | 57.2 | 220.6 | 16.6 | 21 | 25.7 | 17.7 | 133.7 | 113.3 | 17.5 | 38.3
205 | 53 | 375.6 | 150.24 | 175.6219 | 130.4 | 139.8 | 133.9 | 127.9 | 299.7 | 17.3 | 22.3 | 24.3 | 1.9 | 185.6 | 7.7 | 41.3 | 612.7 | 656.9 | 127.5 | 219.1 | 36.9 | 347 | 497.6 | 58.9 | 223.5 | 16.6 | 21.1 | 25.9 | 17.8 | 135.4 | 114.8 | 17.6 | 38.8
206 | 54 | 375.8 | 150.32 | 175.7154 | 132.7 | 141 | 135.7 | 129.4 | 310.7 | 17.3 | 22.3 | 24.6 | 2.1 | 187.7 | 7.6 | 42.5 | 634.6 | 667.8 | 134.6 | 222.2 | 37.9 | 355.7 | 521.6 | 60.3 | 229.8 | 16.6 | 21.2 | 26.3 | 17.8 | 137.2 | 116.2 | 17.6 | 39.4
207 | 55 | 376 | 150.4 | 175.8089 | 134.4 | 141.6 | 137.3 | 130.8 | 322.2 | 17.3 | 22.3 | 24.9 | 2.2 | 189.3 | 7.5 | 43.8 | 634.8 | 665.9 | 137.7 | 226.5 | 38.9 | 357.9 | 511.5 | 61.1 | 232.3 | 16.6 | 21.4 | 26.5 | 17.9 | 138.6 | 118.8 | 17.7 | 40
208 | 56 | 375.6 | 150.24 | 175.6219 | 135.9 | 142.8 | 138.9 | 131.9 | 318 | 17.3 | 22.3 | 25.2 | 2 | 184.6 | 7 | 45.1 | 617.5 | 653.1 | 137.3 | 229 | 39.9 | 352.5 | 490.2 | 61.7 | 231.4 | 16.6 | 21.5 | 26.6 | 17.9 | 139.6 | 120.6 | 17.8 | 40.6
209 | 57 | 376.4 | 150.56 | 175.996 | 137.8 | 145 | 140.4 | 132.9 | 313.3 | 17.3 | 22.3 | 25.5 | 2 | 179 | 6.3 | 46.5 | 615.4 | 645.3 | 138.8 | 231 | 40.9 | 347.4 | 480.7 | 62.5 | 231.5 | 16.6 | 21.7 | 26.8 | 18 | 141.2 | 122 | 17.9 | 41
210 | 58 | 376.8 | 150.72 | 176.183 | 140.5 | 146.5 | 142.1 | 134 | 303.7 | 17.4 | 22.3 | 25.7 | 2.1 | 184.8 | 6.2 | 47.9 | 603.2 | 636.7 | 140.4 | 233.2 | 41.9 | 343.7 | 474.7 | 63.7 | 232.3 | 16.6 | 21.8 | 26.9 | 18 | 143.5 | 123.1 | 18 | 41.6
211 | 59 | 376.8 | 150.72 | 176.183 | 142.5 | 146.7 | 143.7 | 135.4 | 302.8 | 17.4 | 22.3 | 26 | 1.9 | 190 | 6.5 | 49.3 | 591.3 | 626.4 | 141.6 | 234.8 | 43 | 341.4 | 474.1 | 65 | 233.5 | 16.6 | 22 | 27 | 18.1 | 144.4 | 124.5 | 18 | 42.1
212 | 60 | 377.5 | 151 | 176.5103 | 144.7 | 146.4 | 144.9 | 136.9 | 301.7 | 17.4 | 22.3 | 26.3 | 1.8 | 180.6 | 6.3 | 50.6 | 589.7 | 618.6 | 143.8 | 235.3 | 44 | 338 | 474.1 | 65.3 | 234.8 | 16.6 | 22.1 | 27.3 | 18.2 | 145.2 | 126.2 | 18.1 | 42.7
213 | 61 | 378.8 | 151.52 | 177.1181 | 146.4 | 147.2 | 146 | 138.6 | 310.9 | 17.5 | 22.3 | 26.6 | 2.1 | 181.5 | 6.2 | 51.9 | 602.5 | 621.8 | 148.5 | 238.9 | 45 | 346.7 | 502.6 | 66.5 | 239.5 | 16.6 | 22.3 | 27.6 | 18.2 | 146.2 | 127.2 | 18.2 | 43.2
214 | 62 | 378.8 | 151.52 | 177.1181 | 147.4 | 148.3 | 147.1 | 140.2 | 319.3 | 17.5 | 22.2 | 26.9 | 2.3 | 185.8 | 6.2 | 53.3 | 611.5 | 621.2 | 153.4 | 241.5 | 46.1 | 350.3 | 506.2 | 67.5 | 243.5 | 16.7 | 22.4 | 28 | 18.3 | 148.3 | 128.4 | 18.3 | 43.6
215 | 63 | 378.8 | 151.52 | 177.1181 | 149 | 149.2 | 148.3 | 141.6 | 320.3 | 17.6 | 22.2 | 27.2 | 2.2 | 196.3 | 6.3 | 54.7 | 627.9 | 621.6 | 158 | 243.4 | 47.1 | 352.4 | 512 | 68.1 | 245.5 | 16.7 | 22.6 | 28.1 | 18.3 | 149.7 | 130.3 | 18.4 | 44
216 | 64 | 377.8 | 151.12 | 176.6506 | 149.9 | 150.9 | 149.6 | 143.1 | 329 | 17.6 | 22.2 | 27.5 | 2.1 | 191.4 | 6.2 | 56.1 | 652.8 | 622.9 | 163.2 | 245.6 | 48.1 | 359.3 | 536.9 | 69 | 251.6 | 16.7 | 22.7 | 28.5 | 18.4 | 151.1 | 131.8 | 18.4 | 44.6
217 | 65 | 378.4 | 151.36 | 176.9311 | 151.2 | 152.6 | 151.1 | 144.7 | 329.8 | 17.7 | 22.2 | 27.8 | 2 | 178.6 | 6.1 | 57.7 | 658.4 | 622.2 | 165.8 | 249.2 | 49.1 | 358 | 525 | 70.6 | 253.5 | 16.7 | 22.9 | 28.8 | 18.4 | 152.4 | 132.9 | 18.5 | 45.3
218 | 66 | 378.4 | 151.36 | 176.9311 | 154 | 153.8 | 152.7 | 146.4 | 328.5 | 17.8 | 22.2 | 28.1 | 1.9 | 176.2 | 6.3 | 59.4 | 652.5 | 611 | 166.1 | 251.6 | 50.1 | 356.9 | 518.8 | 73.3 | 255.1 | 16.7 | 23.1 | 28.9 | 18.5 | 153.6 | 134.1 | 18.6 | 45.8
219 | 67 | 378.8 | 151.52 | 177.1181 | 156 | 155.1 | 154.3 | 148.2 | 328.1 | 17.8 | 22.2 | 28.4 | 1.8 | 176.4 | 5.7 | 61.2 | 665.9 | 613.5 | 171.4 | 252.4 | 51.2 | 359 | 531.9 | 74.3 | 257.5 | 16.7 | 23.2 | 29 | 18.5 | 155.2 | 135.5 | 18.7 | 46.4
220 | 68 | 380.5 | 152.2 | 177.913 | 158.3 | 156.2 | 155.9 | 149.5 | 339.6 | 17.7 | 22.2 | 28.7 | 1.9 | 184.7 | 5 | 63 | 675 | 605.3 | 173.8 | 254.1 | 52.2 | 367.1 | 548.1 | 75.1 | 263.4 | 16.7 | 23.4 | 29.4 | 18.6 | 156.8 | 137.2 | 18.8 | 46.8
221 | 69 | 373.9 | 149.56 | 174.827 | 159.4 | 157.7 | 157.5 | 150.6 | 346.7 | 17.8 | 22.2 | 29 | 1.9 | 184.8 | 4.7 | 64.9 | 686.8 | 608.4 | 177.2 | 255.3 | 53.3 | 372.4 | 557.1 | 77.1 | 266.7 | 16.7 | 23.6 | 29.9 | 18.7 | 160.7 | 139.3 | 18.9 | 47.5
222 | 70 | 378.2 | 151.28 | 176.8376 | 160.4 | 158.8 | 159.1 | 151.7 | 350.9 | 17.9 | 22.2 | 29.2 | 1.7 | 179.9 | 5.1 | 67 | 702.2 | 617.6 | 182.8 | 258.5 | 54.3 | 380.3 | 575.3 | 78.9 | 270.6 | 16.7 | 23.7 | 30.1 | 18.7 | 163.7 | 141.5 | 19 | 48.2
223 | 71 | 377 | 150.8 | 176.2765 | 160.6 | 160.3 | 160.2 | 153.2 | 354.6 | 18 | 22.2 | 29.5 | 1.9 | 172.9 | 5.8 | 69.2 | 717.5 | 630.3 | 186 | 262.5 | 55.4 | 387.1 | 574.9 | 80.9 | 275.8 | 16.7 | 23.9 | 30.2 | 18.8 | 164.8 | 143.3 | 19.1 | 49
224 | 72 | 378.9 | 151.56 | 177.1649 | 160 | 161.2 | 161.6 | 154.7 | 349.8 | 18.1 | 22.2 | 29.8 | 2.3 | 164.7 | 6 | 71.5 | 733.1 | 643.6 | 190 | 266 | 56.5 | 388.8 | 584.8 | 83.5 | 279.8 | 16.7 | 24.1 | 30.3 | 18.9 | 165.4 | 145.1 | 19.2 | 49.6
225 | 73 | 377.9 | 151.16 | 176.6973 | 160.7 | 161.4 | 162.9 | 156 | 348.9 | 18.1 | 22.2 | 30 | 1.9 | 166.8 | 5.9 | 74 | 734.7 | 645.8 | 190.7 | 270.7 | 57.5 | 388.2 | 575.6 | 85.7 | 283 | 16.7 | 24.2 | 30.5 | 18.9 | 166.3 | 146.6 | 19.3 | 50.2
226 | 74 | 379.5 | 151.8 | 177.4455 | 162.2 | 162 | 163.9 | 157.1 | 342.8 | 18.2 | 22.2 | 30.2 | 1.9 | 175.1 | 5.8 | 76.7 | 742.3 | 667.6 | 197 | 276.3 | 58.6 | 391 | 582.9 | 87.6 | 287.2 | 16.7 | 24.4 | 30.7 | 19 | 166.4 | 147.7 | 19.4 | 50.7
227 | 75 | 381 | 152.4 | 178.1468 | 161.9 | 164 | 164.8 | 158.2 | 346.4 | 18.2 | 22.2 | 30.4 | 1.9 | 173.1 | 6 | 79.4 | 747.5 | 682.4 | 198.8 | 281.8 | 59.7 | 389.2 | 587.3 | 89.7 | 289.1 | 16.7 | 24.6 | 30.9 | 19.1 | 168.3 | 148.8 | 19.5 | 51.3
228 | 76 | 380.7 | 152.28 | 178.0065 | 161.5 | 164.9 | 165.5 | 158.7 | 356.7 | 18.3 | 22.2 | 30.6 | 1.9 | 159.5 | 5.8 | 82.2 | 758.4 | 689.6 | 201.9 | 288.3 | 60.9 | 396.3 | 605.2 | 91.6 | 295.6 | 16.7 | 24.7 | 31.2 | 19.1 | 168.9 | 149.8 | 19.6 | 51.7
229 | 77 | 378.3 | 151.32 | 176.8844 | 161 | 165.3 | 165.8 | 159.3 | 359.5 | 18.3 | 22.2 | 30.9 | 1.9 | 173.2 | 5.4 | 84.9 | 764.2 | 681.6 | 202.6 | 291.5 | 62 | 394.1 | 603.1 | 93.6 | 298.5 | 16.7 | 24.9 | 31.4 | 19.2 | 169.4 | 149.9 | 19.7 | 52.2
230 | 78 | 378.2 | 151.28 | 176.8376 | 161.1 | 166.6 | 165.9 | 160.5 | 354 | 18.4 | 22.2 | 31.1 | 1.9 | 176.7 | 5.2 | 87.8 | 760.6 | 670.5 | 202.6 | 292.7 | 63.1 | 391.1 | 593.7 | 96.4 | 300.5 | 16.7 | 25.1 | 31.6 | 19.3 | 170 | 150.5 | 19.8 | 52.7
231 | 79 | 379.4 | 151.76 | 177.3987 | 161.2 | 168 | 166.2 | 161.6 | 344.3 | 18.4 | 22.2 | 31.3 | 2.1 | 163.3 | 5.6 | 90.7 | 752.1 | 664.8 | 203.1 | 295.9 | 64.3 | 388.4 | 581.2 | 98.1 | 301.7 | 16.7 | 25.2 | 31.8 | 19.3 | 170.3 | 152 | 19.9 | 53.2
232 | 80 | 379.5 | 151.8 | 177.4455 | 161 | 169 | 166.6 | 162.6 | 342.8 | 18.4 | 22.2 | 31.5 | 2.2 | 164.1 | 5.7 | 93.9 | 745 | 667.8 | 204.7 | 298.7 | 65.5 | 386.4 | 584.1 | 99.9 | 303.2 | 16.8 | 25.4 | 32.1 | 19.4 | 170.6 | 153.1 | 20.1 | 53.7
233 | 81 | 378.8 | 151.52 | 177.1181 | 161.2 | 169.5 | 167.3 | 163.4 | 344.7 | 18.4 | 22.2 | 31.7 | 2.1 | 167.1 | 5.8 | 97 | 739.8 | 666.7 | 204.7 | 301.2 | 66.7 | 387.7 | 584.7 | 101.5 | 305.5 | 16.8 | 25.5 | 32.3 | 19.5 | 171.4 | 153.4 | 20.2 | 54.2
234 | 82 | 377.9 | 151.16 | 176.6973 | 161.5 | 170.1 | 167.8 | 163.8 | 347.9 | 18.4 | 22.2 | 31.8 | 2.4 | 177.3 | 5.7 | 100.2 | 744.4 | 685.2 | 208.9 | 303.8 | 67.8 | 391.7 | 595.8 | 104.5 | 309.2 | 16.8 | 25.7 | 32.5 | 19.6 | 172.6 | 153.8 | 20.3 | 54.6
235 | 83 | 376.7 | 150.68 | 176.1362 | 162.5 | 171.4 | 168 | 164 | 360.5 | 18.4 | 22.2 | 32 | 2.3 | 181.1 | 5.5 | 103.4 | 751.4 | 679.7 | 213.4 | 306.1 | 69 | 396.4 | 598.8 | 107.1 | 313 | 16.8 | 25.8 | 32.8 | 19.6 | 174.1 | 154.3 | 20.4 | 55.1
236 | 84 | 377.8 | 151.12 | 176.6506 | 163.3 | 172 | 168.6 | 164 | 357.5 | 18.4 | 22.2 | 32.2 | 2.2 | 178.4 | 5.2 | 106.7 | 749.7 | 676.1 | 216.3 | 310.1 | 70 | 396.8 | 601.5 | 108.8 | 315.4 | 16.8 | 26 | 33.1 | 19.7 | 174.5 | 154.9 | 20.5 | 55.5
237 | 85 | 377 | 150.8 | 176.2765 | 163.8 | 172.7 | 169.3 | 164.2 | 362 | 18.4 | 22.1 | 32.4 | 2.2 | 178.9 | 5 | 110.2 | 759.3 | 677.8 | 219.4 | 313.5 | 71.1 | 403.9 | 615.9 | 111.2 | 321.2 | 16.8 | 26.2 | 33.5 | 19.8 | 175 | 155.1 | 20.6 | 55.9
238 | 86 | 374.8 | 149.92 | 175.2478 | 163.6 | 173.4 | 169.9 | 164.6 | 363.6 | 18.4 | 22.1 | 32.6 | 2.2 | 182.5 | 5.2 | 114 | 768.7 | 684 | 221.7 | 318.1 | 72.2 | 410.3 | 630.8 | 114.2 | 327.6 | 16.8 | 26.3 | 33.7 | 19.9 | 175.5 | 155.6 | 20.8 | 56.3
239 | 87 | 374.4 | 149.76 | 175.0608 | 164.4 | 174.2 | 170.6 | 165.6 | 360.2 | 18.5 | 22.1 | 32.8 | 2.3 | 180.7 | 5.2 | 118 | 776.3 | 693.3 | 223.5 | 324.1 | 73.2 | 410.1 | 631.8 | 117 | 330.6 | 16.8 | 26.5 | 34 | 19.9 | 176 | 156.1 | 20.9 | 56.8
240 | 88 | 373.9 | 149.56 | 174.827 | 166 | 174.4 | 171.6 | 166.9 | 359.5 | 18.5 | 22.1 | 33 | 2.5 | 180.5 | 5.5 | 122.3 | 786.2 | 703 | 225.1 | 328.5 | 74.2 | 413.4 | 640 | 120.3 | 335.5 | 16.8 | 26.7 | 34.4 | 20 | 176.9 | 156 | 21 | 57.2
241 | 89 | 374.7 | 149.88 | 175.2011 | 167.1 | 174.4 | 172.4 | 167.7 | 361.8 | 18.6 | 22.1 | 33.2 | 2.3 | 178.3 | 5.7 | 126.8 | 799.8 | 721.7 | 228.4 | 333.5 | 75.2 | 417.8 | 655.3 | 124.1 | 341.3 | 16.8 | 26.9 | 34.6 | 20.1 | 177.6 | 156.3 | 21.1 | 57.6
242 | 90 | 374.7 | 149.88 | 175.2011 | 166.8 | 174.7 | 173.2 | 168.7 | 357.5 | 18.6 | 22.1 | 33.3 | 2.2 | 176.3 | 5.8 | 131.6 | 801.1 | 716.7 | 228.3 | 338 | 76.3 | 418.8 | 648.5 | 129.1 | 343.7 | 16.8 | 27 | 34.7 | 20.2 | 178.4 | 157 | 21.2 | 58
243 | 91 | 374.1 | 149.64 | 174.9205 | 167.2 | 174.3 | 173.8 | 169.4 | 359.2 | 18.7 | 22.1 | 33.5 | 2.2 | 175.7 | 6.1 | 136.7 | 806.5 | 728.2 | 229.3 | 343.6 | 77.4 | 420.5 | 653.5 | 132.9 | 347.5 | 16.9 | 27.2 | 35 | 20.3 | 179 | 157.9 | 21.4 | 58.4
244 | 92 | 374.1 | 149.64 | 174.9205 | 167.3 | 174.4 | 174.2 | 169.7 | 370.8 | 18.7 | 22.1 | 33.7 | 1.9 | 174.5 | 6.3 | 141.9 | 806.2 | 736.9 | 229.3 | 348.2 | 78.5 | 421.5 | 652.3 | 135.8 | 352 | 16.9 | 27.4 | 35.4 | 20.3 | 179.5 | 158.2 | 21.5 | 58.7
245 | 93 | 376.5 | 150.6 | 176.0427 | 167.5 | 174.2 | 174.5 | 170.3 | 378.7 | 18.7 | 22.1 | 33.9 | 1.8 | 170.3 | 6.3 | 147.4 | 817.3 | 744.3 | 230.4 | 351 | 79.6 | 430.4 | 677.1 | 140.4 | 359.3 | 16.9 | 27.6 | 35.7 | 20.4 | 180.6 | 159.1 | 21.6 | 59.2
246 | 94 | 374.5 | 149.8 | 175.1076 | 167.5 | 174.2 | 174.8 | 170.6 | 391.6 | 18.8 | 22.1 | 34.1 | 2.4 | 174.6 | 6.1 | 153.4 | 831.7 | 752.4 | 232.1 | 355.9 | 80.7 | 438 | 704.2 | 146.3 | 367.4 | 16.9 | 27.8 | 35.7 | 20.5 | 181.3 | 160 | 21.7 | 59.8
247 | 95 | 374.6 | 149.84 | 175.1543 | 168.8 | 174.8 | 174.7 | 171.8 | 408.3 | 18.9 | 22.1 | 34.3 | 2.2 | 177 | 5.9 | 160.2 | 841.1 | 756 | 232.3 | 361.5 | 81.8 | 446.2 | 720.3 | 152.1 | 374.9 | 16.9 | 28 | 35.9 | 20.6 | 181.9 | 160.2 | 21.9 | 60.4
248 | 96 | 376.7 | 150.68 | 176.1362 | 169.6 | 175.9 | 174.7 | 173.1 | 415.7 | 18.9 | 22.1 | 34.5 | 2.1 | 180.3 | 5.7 | 167.3 | 849.7 | 763 | 232.3 | 367 | 82.8 | 449.7 | 730.2 | 157.2 | 379.3 | 16.9 | 28.1 | 36.1 | 20.7 | 182.4 | 160.7 | 22 | 60.9
249 | 97 | 376.6 | 150.64 | 176.0895 | 170.2 | 177.1 | 175.1 | 173.7 | 414.4 | 19 | 22.1 | 34.7 | 2.1 | 187.6 | 5.3 | 174.7 | 853.1 | 779.8 | 233.2 | 376.9 | 83.9 | 458.9 | 740.9 | 161.3 | 387.8 | 16.9 | 28.3 | 36.3 | 20.8 | 182.7 | 161.3 | 22.1 | 61.4
250 | 98 | 376.2 | 150.48 | 175.9024 | 170.8 | 177.6 | 176.1 | 174.2 | 416.5 | 19 | 22.1 | 34.9 | 1.8 | 191 | 5 | 181.8 | 857 | 781.5 | 235 | 383.6 | 85 | 466.6 | 749 | 166.7 | 395.9 | 16.9 | 28.5 | 36.6 | 20.8 | 183.2 | 161.4 | 22.3 | 61.9
251 | 99 | 375.9 | 150.36 | 175.7622 | 171.6 | 179.1 | 177 | 174.6 | 410.6 | 19.1 | 22.1 | 35.1 | 1.8 | 180.8 | 4.8 | 188.1 | 855.7 | 784.9 | 236.1 | 391.8 | 86.3 | 471.8 | 749.3 | 173.3 | 403.1 | 16.9 | 28.7 | 36.8 | 20.9 | 184 | 161.7 | 22.4 | 62.3
252 | 100 | 376.8 | 150.72 | 176.183 | 172.3 | 179.7 | 177.7 | 174.9 | 406 | 19.2 | 22 | 35.2 | 2 | 171.9 | 4.6 | 194.6 | 858.6 | 802.1 | 237.9 | 400.3 | 87.6 | 482 | 759.7 | 176.4 | 414.7 | 17 | 28.9 | 37.1 | 21 | 185.2 | 162.5 | 22.6 | 62.6
253 | 101 | 376.2 | 150.48 | 175.9024 | 173.2 | 179.8 | 178.5 | 175.2 | 407.7 | 19.3 | 22 | 35.3 | 2.1 | 179.5 | 4.5 | 201.3 | 860.1 | 809.1 | 239 | 406.2 | 88.9 | 490.1 | 761.6 | 178.5 | 421.3 | 17 | 29.1 | 37.5 | 21.1 | 185.4 | 164.1 | 22.7 | 63.1
254 | 102 | 376.4 | 150.56 | 175.996 | 173.7 | 180 | 179.3 | 175.6 | 411 | 19.4 | 22 | 35.5 | 2.4 | 187.3 | 4.5 | 208.1 | 862.9 | 796.7 | 239.7 | 411.9 | 90.3 | 490.7 | 745.9 | 180.7 | 424.4 | 17 | 29.3 | 37.8 | 21.2 | 185.4 | 165.2 | 22.9 | 63.7
255 | 103 | 377 | 150.8 | 176.2765 | 174.1 | 180.4 | 180.1 | 176.3 | 404.7 | 19.5 | 22 | 35.6 | 2.1 | 187.4 | 4.3 | 214.8 | 861.6 | 782.5 | 240.3 | 415.1 | 91.7 | 485.3 | 738.6 | 181.5 | 425 | 17 | 29.5 | 38.2 | 21.3 | 185.9 | 165.8 | 23 | 64.1
256 | 104 | 375.4 | 150.16 | 175.5284 | 174.2 | 181.2 | 180.6 | 177 | 400.9 | 19.6 | 22 | 35.7 | 2.1 | 181.6 | 3.9 | 220.4 | 860.7 | 784.7 | 241 | 419.7 | 93.2 | 480.2 | 743.5 | 182.8 | 425.5 | 17 | 29.7 | 38.5 | 21.3 | 186.4 | 166.2 | 23.1 | 64.6
257 | 105 | 374.7 | 149.88 | 175.2011 | 174.8 | 183 | 181.2 | 177.4 | 404.6 | 19.6 | 22 | 35.8 | 2 | 177.7 | 3.8 | 225 | 861.7 | 786.2 | 242.2 | 424.8 | 94.8 | 479.7 | 746.1 | 186.4 | 429.4 | 17 | 29.9 | 38.4 | 21.4 | 186.7 | 167.1 | 23.3 | 65
258 | 106 | 374.9 | 149.96 | 175.2946 | 174.9 | 184.8 | 181.9 | 177.9 | 408.6 | 19.7 | 22 | 35.9 | 2 | 176.4 | 3.8 | 229.3 | 862.4 | 783.4 | 243.6 | 427.7 | 96.4 | 477.2 | 742.6 | 188.1 | 431.3 | 17 | 30.1 | 38.6 | 21.5 | 187.3 | 167.5 | 23.4 | 65.4
259 | 107 | 377.1 | 150.84 | 176.3233 | 175.8 | 185.8 | 182.2 | 178.4 | 412.8 | 19.7 | 22 | 36 | 2.3 | 172.9 | 3.5 | 233.6 | 864.2 | 788.6 | 245 | 430.2 | 98 | 474.2 | 742.3 | 191.2 | 433.4 | 17 | 30.3 | 39.2 | 21.6 | 187.5 | 167.8 | 23.6 | 65.9
260 | 108 | 376.6 | 150.64 | 176.0895 | 176.3 | 187.6 | 182.6 | 179 | 417.8 | 19.8 | 22 | 36.1 | 2.4 | 190.2 | 3.6 | 237.7 | 865.7 | 782.8 | 246.1 | 435.1 | 99.7 | 472.4 | 744.9 | 195.2 | 436.3 | 17.1 | 30.5 | 39.8 | 21.7 | 188.6 | 168.4 | 23.7 | 66.5
261 | 109 | 376.8 | 150.72 | 176.183 | 176.3 | 188.8 | 182.6 | 179.8 | 424.7 | 19.8 | 22 | 36.2 | 2.5 | 198.7 | 3.8 | 241.4 | 871.1 | 785.2 | 247.6 | 439.1 | 101.5 | 473.9 | 755.9 | 199.6 | 440.3 | 17.1 | 30.7 | 39.8 | 21.8 | 189.4 | 168.8 | 23.9 | 66.9
262 | 110 | 375.7 | 150.28 | 175.6687 | 176.5 | 188.6 | 182.4 | 180.6 | 428.5 | 19.9 | 22 | 36.3 | 2.2 | 182.3 | 4 | 244.8 | 875.3 | 781.7 | 249.8 | 441.1 | 103.2 | 476.5 | 761.1 | 203 | 444.6 | 17.1 | 31 | 40.1 | 21.9 | 191.1 | 169 | 24 | 67.3
263 | 111 | 375.8 | 150.32 | 175.7154 | 177.1 | 188.8 | 182.5 | 181.4 | 423.7 | 20 | 22 | 36.4 | 2.3 | 194.4 | 4.3 | 247.6 | 867.7 | 778.9 | 251.9 | 442.1 | 105 | 471.4 | 750.3 | 205.8 | 445.2 | 17.1 | 31.2 | 40.5 | 22 | 192 | 169.4 | 24.1 | 67.7
264 | 112 | 375.9 | 150.36 | 175.7622 | 178.5 | 189.8 | 183.2 | 182.2 | 419.5 | 20.1 | 22 | 36.5 | 2.2 | 209 | 3.8 | 249.9 | 864.4 | 780.6 | 254.4 | 444.9 | 106.9 | 469.3 | 748 | 210.4 | 447 | 17.1 | 31.4 | 40.8 | 22.1 | 192.6 | 169.8 | 24.3 | 68.2
265 | 113 | 377 | 150.8 | 176.2765 | 179.2 | 190.7 | 183.9 | 182.9 | 417.7 | 20.1 | 22 | 36.7 | 2 | 204.4 | 3 | 252.1 | 864.6 | 789.7 | 257.2 | 448 | 108.8 | 470.1 | 753.5 | 215.3 | 452.1 | 17.1 | 31.6 | 40.8 | 22.2 | 193 | 170.3 | 24.5 | 68.8
266 | 114 | 378.1 | 151.24 | 176.7908 | 178.5 | 190.6 | 184.2 | 183.3 | 419.2 | 20.2 | 22 | 36.8 | 2.1 | 200 | 3.8 | 254.4 | 869.9 | 788.4 | 260.3 | 449 | 110.6 | 468.9 | 755.7 | 220 | 454.8 | 17.1 | 31.8 | 41 | 22.3 | 193.5 | 171.1 | 24.6 | 69.4
267 | 115 | 377.8 | 151.12 | 176.6506 | 178.5 | 190.2 | 184.4 | 183.2 | 419.7 | 20.3 | 22 | 37 | 2.2 | 180.7 | 4.5 | 256.6 | 873.4 | 784.8 | 263.5 | 451.3 | 112.5 | 470.2 | 751.6 | 225.2 | 457 | 17.2 | 32 | 41.3 | 22.3 | 194.1 | 171.9 | 24.7 | 70
268 | 116 | 374.1 | 149.64 | 174.9205 | 178.8 | 189.7 | 184.8 | 183.4 | 416.1 | 20.3 | 22 | 37.1 | 2 | 154.4 | 4.5 | 258.5 | 877.4 | 780.8 | 266.3 | 454.1 | 114.4 | 466.1 | 740.7 | 227.2 | 457.9 | 17.2 | 32.2 | 41.6 | 22.4 | 194.9 | 172.1 | 24.9 | 70.4
269 | 117 | 375.7 | 150.28 | 175.6687 | 179.9 | 190.5 | 185.4 | 184 | 423 | 20.3 | 21.9 | 37.2 | 2.3 | 150.6 | 3.9 | 260.3 | 874.8 | 766.8 | 268.8 | 454.5 | 116.3 | 466.4 | 743.2 | 229.7 | 460.2 | 17.2 | 32.4 | 42 | 22.5 | 195.5 | 172.2 | 25.1 | 70.7
270 | 118 | 376.1 | 150.44 | 175.8557 | 180.7 | 192.5 | 186.1 | 184.7 | 428.3 | 20.4 | 21.9 | 37.3 | 2.2 | 184.9 | 4 | 262.1 | 873.5 | 763 | 270.8 | 457.4 | 118.3 | 467.4 | 741.8 | 230.9 | 462.2 | 17.2 | 32.7 | 42.5 | 22.6 | 196 | 173 | 25.2 | 71.3
271 | 119 | 376.6 | 150.64 | 176.0895 | 181.4 | 194.6 | 186.9 | 185.3 | 423.9 | 20.5 | 21.9 | 37.4 | 2.3 | 203.6 | 4.5 | 263.7 | 872.7 | 758.7 | 272.8 | 457.6 | 120.3 | 466.2 | 735.6 | 231.7 | 465.1 | 17.2 | 32.9 | 42.8 | 22.7 | 196.2 | 173.2 | 25.4 | 71.7
272 | 120 | 378.6 | 151.44 | 177.0246 | 182 | 196.5 | 187.3 | 186.1 | 421.4 | 20.5 | 21.9 | 37.5 | 2.2 | 208.4 | 4 | 265.3 | 871.2 | 763.5 | 274.3 | 459.9 | 122.3 | 464.9 | 728.5 | 233.6 | 467.4 | 17.2 | 33.1 | 43 | 22.8 | 197.2 | 173.8 | 25.5 | 72.1
273 | 121 | 379.2 | 151.68 | 177.3052 | 182.6 | 196.9 | 187.5 | 187 | 414.6 | 20.6 | 21.9 | 37.7 | 2.2 | 206.7 | 3.7 | 266.4 | 866.6 | 760.3 | 276.9 | 463 | 124.3 | 461.8 | 719.2 | 234.7 | 467.8 | 17.3 | 33.4 | 43.3 | 22.9 | 198.2 | 174.6 | 25.7 | 72.7
274 | 122 | 377.5 | 151 | 176.5103 | 183.6 | 197.2 | 188.1 | 188 | 410.4 | 20.7 | 21.9 | 37.8 | 2.4 | 199.1 | 4.1 | 267.3 | 865.7 | 777.5 | 280 | 468.9 | 126.3 | 463.2 | 722.2 | 237.6 | 471.5 | 17.3 | 33.6 | 43.5 | 23 | 198.9 | 174.7 | 25.9 | 73.2
275 | 123 | 376.9 | 150.76 | 176.2298 | 184.2 | 197.1 | 188.5 | 188.9 | 417.1 | 20.7 | 21.9 | 37.9 | 2.2 | 178.1 | 4 | 268.5 | 866.1 | 780.3 | 283.6 | 472 | 128.3 | 466.2 | 734.2 | 241.4 | 475.5 | 17.3 | 33.8 | 43.8 | 23.1 | 199.5 | 175.3 | 26 | 73.5
276 | 124 | 376.6 | 150.64 | 176.0895 | 183.6 | 196.9 | 189 | 189.4 | 427.2 | 20.7 | 21.9 | 38 | 2.2 | 172 | 3.9 | 270.2 | 873.1 | 768.3 | 287.2 | 474.7 | 130.1 | 466.9 | 736.6 | 245.2 | 480 | 17.3 | 34 | 44.1 | 23.2 | 200.3 | 175.8 | 26.2 | 73.9
277 | 125 | 376.9 | 150.76 | 176.2298 | 183.3 | 197 | 189.3 | 190 | 427.2 | 20.8 | 21.9 | 38.2 | 2 | 182.9 | 4 | 272.1 | 876.1 | 776.3 | 290.8 | 480.2 | 131.9 | 469.8 | 740.1 | 247.9 | 483.2 | 17.3 | 34.2 | 44.4 | 23.3 | 201.8 | 176.1 | 26.4 | 74.4
278 | 126 | 376.8 | 150.72 | 176.183 | 182.8 | 197.1 | 189.2 | 190.4 | 425.7 | 20.9 | 21.9 | 38.3 | 2.2 | 186.1 | 4 | 273.8 | 874.6 | 784 | 295.2 | 484.4 | 133.7 | 476.7 | 745.8 | 251.9 | 489.7 | 17.4 | 34.5 | 44.7 | 23.4 | 201.7 | 176.4 | 26.5 | 75.1
279 | 127 | 377 | 150.8 | 176.2765 | 184.1 | 197.4 | 188.8 | 191.1 | 426.2 | 20.9 | 21.9 | 38.5 | 2 | 174.3 | 3.7 | 275 | 880.4 | 772.1 | 299.5 | 486 | 135.4 | 475.3 | 743.6 | 252.6 | 490.3 | 17.4 | 34.7 | 45.1 | 23.5 | 201.7 | 176.8 | 26.7 | 75.6
280 | 128 | 376 | 150.4 | 175.8089 | 184.7 | 197.6 | 189.2 | 191.8 | 423.4 | 21 | 21.9 | 38.6 | 2.5 | 168.9 | 3.5 | 275.5 | 879.3 | 746.6 | 302.3 | 486.8 | 137 | 469 | 727.6 | 249.9 | 488.9 | 17.4 | 34.9 | 45.5 | 23.6 | 202.6 | 177.3 | 26.9 | 76
281 | 129 | 372.9 | 149.16 | 174.3594 | 185.1 | 197.3 | 190 | 192.1 | 426.5 | 21.1 | 21.9 | 38.8 | 2.6 | 174.3 | 3.2 | 275.8 | 873.5 | 725.7 | 303.9 | 485.3 | 138.7 | 461.9 | 710.5 | 247.6 | 487.8 | 17.4 | 35.1 | 45.9 | 23.7 | 202.9 | 177.8 | 27 | 76.5
282 | 130 | 373.3 | 149.32 | 174.5465 | 186.1 | 197.3 | 190.9 | 192.5 | 418.3 | 21.2 | 21.9 | 38.9 | 2.4 | 176.2 | 2.7 | 276.3 | 872.3 | 735 | 305.6 | 485.8 | 140.2 | 457.4 | 707.8 | 246.4 | 487.2 | 17.4 | 35.4 | 46.1 | 23.8 | 202.5 | 177.8 | 27.2 | 77
283 | 131 | 373.6 | 149.44 | 174.6867 | 185.9 | 197.6 | 191.6 | 193.1 | 422.3 | 21.2 | 21.9 | 39 | 2.5 | 167.7 | 2.3 | 277 | 872.9 | 736.6 | 307.9 | 488.7 | 141.8 | 455.5 | 714.8 | 246.5 | 489.8 | 17.4 | 35.6 | 46.2 | 23.9 | 202.5 | 178.4 | 27.4 | 77.5
284 | 132 | 371.9 | 148.76 | 173.8919 | 185.1 | 197.9 | 191.8 | 193.7 | 423 | 21.3 | 21.9 | 39.1 | 2.5 | 153.6 | 2 | 278.1 | 866 | 729.4 | 309.8 | 490.4 | 143.4 | 451.9 | 706.3 | 245.4 | 488.6 | 17.5 | 35.8 | 46.4 | 24 | 202.7 | 178.5 | 27.5 | 77.9
285 | 133 | 371.9 | 148.76 | 173.8919 | 184.7 | 198.7 | 192.2 | 194.1 | 419.4 | 21.3 | 21.9 | 39.2 | 2.2 | 139.5 | 2.4 | 279.4 | 864.8 | 725.1 | 311.9 | 491.5 | 145 | 449.4 | 705.7 | 245.3 | 489.5 | 17.5 | 36.1 | 46.8 | 24.1 | 202.7 | 178.8 | 27.7 | 78.3
286 | 134 | 371.7 | 148.68 | 173.7984 | 185.1 | 199 | 192.7 | 194.6 | 415.1 | 21.3 | 21.8 | 39.3 | 2.4 | 142.2 | 3.4 | 280.8 | 870.8 | 717 | 314.2 | 491.3 | 146.5 | 451.6 | 700.5 | 246 | 490.1 | 17.5 | 36.3 | 47.1 | 24.2 | 203.4 | 178.9 | 27.9 | 78.8
287 | 135 | 372.2 | 148.88 | 174.0321 | 185 | 199 | 193.1 | 194.9 | 412.2 | 21.3 | 21.8 | 39.4 | 2.4 | 156.1 | 3.8 | 282.3 | 871.4 | 716.1 | 317.1 | 491.5 | 147.9 | 452 | 697.4 | 247.8 | 491.9 | 17.5 | 36.5 | 47.3 | 24.3 | 204.3 | 179.1 | 28.1 | 79.2
288 | 136 | 373.8 | 149.52 | 174.7803 | 185.2 | 199.5 | 193.1 | 195.2 | 411.8 | 21.3 | 21.8 | 39.6 | 2.4 | 177 | 4.4 | 284 | 875.6 | 714.1 | 319.3 | 491.6 | 149.4 | 455 | 696.3 | 249 | 493.5 | 17.5 | 36.7 | 47.7 | 24.4 | 204.4 | 179.4 | 28.3 | 79.6
289 | 137 | 372.5 | 149 | 174.1724 | 186.1 | 199.5 | 192.8 | 195.5 | 406.9 | 21.3 | 21.8 | 39.7 | 2.3 | 173.2 | 4.7 | 285.7 | 881.3 | 712.1 | 321.6 | 492.8 | 150.8 | 459.1 | 694.7 | 251.6 | 497.1 | 17.6 | 37 | 47.9 | 24.5 | 204.5 | 179.6 | 28.4 | 80.1
290 | 138 | 372.4 | 148.96 | 174.1257 | 186.7 | 199 | 193 | 196 | 399.5 | 21.3 | 21.8 | 39.9 | 2.6 | 156.9 | 5.3 | 286.9 | 878.6 | 706.3 | 323.7 | 493.6 | 152.2 | 458.1 | 693 | 253 | 496.4 | 17.6 | 37.2 | 48 | 24.6 | 204.6 | 180 | 28.6 | 80.5
291 | 139 | 372.7 | 149.08 | 174.2659 | 187.3 | 199.5 | 193.5 | 196.4 | 391.3 | 21.3 | 21.8 | 40 | 2.5 | 156.4 | 5.3 | 288 | 874.6 | 708.6 | 325.3 | 496 | 153.6 | 453.8 | 681.2 | 253.2 | 495.7 | 17.6 | 37.4 | 48.2 | 24.7 | 205 | 180.3 | 28.8 | 81
292 | 140 | 372.5 | 149 | 174.1724 | 188 | 200.2 | 194 | 196.9 | 385.7 | 21.3 | 21.8 | 40.1 | 2.4 | 154.4 | 4.9 | 289.1 | 876.8 | 716.2 | 327.1 | 498.7 | 155.1 | 455.6 | 688.1 | 254.3 | 498.2 | 17.6 | 37.6 | 48.1 | 24.8 | 205 | 180.6 | 28.9 | 81.4
293 | 141 | 372.3 | 148.92 | 174.0789 | 187.9 | 199.6 | 194.4 | 197.3 | 394.1 | 21.4 | 21.8 | 40.2 | 2.4 | 162.1 | 4.9 | 290.4 | 880.2 | 724.3 | 329.4 | 502 | 156.5 | 456.8 | 694.6 | 254.5 | 499.6 | 17.6 | 37.8 | 48.4 | 24.9 | 205 | 180.9 | 29.1 | 81.7
294 | 142 | 372.9 | 149.16 | 174.3594 | 188.1 | 198.7 | 194.6 | 197.6 | 394.3 | 21.4 | 21.8 | 40.3 | 2.4 | 167.8 | 5.2 | 291.9 | 880.2 | 729.7 | 332.6 | 503 | 157.9 | 457.5 | 693.3 | 255.2 | 501.4 | 17.7 | 38 | 48.8 | 25 | 205.3 | 181.5 | 29.3 | 82.3
295 | 143 | 371.9 | 148.76 | 173.8919 | 188.4 | 198.2 | 195 | 198 | 387.9 | 21.4 | 21.8 | 40.4 | 2.4 | 169 | 5.4 | 293.4 | 878.7 | 745.5 | 335.6 | 506.8 | 159.2 | 457.1 | 686.4 | 255.9 | 503.2 | 17.7 | 38.2 | 48.9 | 25.1 | 205.8 | 181.7 | 29.5 | 83
296 | 144 | 371.6 | 148.64 | 173.7516 | 188.8 | 198 | 195.2 | 198.3 | 383.1 | 21.4 | 21.8 | 40.5 | 2.6 | 154.4 | 5.1 | 295 | 872.5 | 731.4 | 338.4 | 506.5 | 160.5 | 459.4 | 688.8 | 256.4 | 505.2 | 17.7 | 38.4 | 49 | 25.2 | 205.8 | 182.3 | 29.7 | 83.6
297 | 145 | 372.3 | 148.92 | 174.0789 | 189.5 | 197.7 | 195.1 | 198.6 | 386.6 | 21.5 | 21.8 | 40.6 | 2.7 | 143.4 | 5.2 | 297.1 | 872.7 | 750.4 | 341 | 512.2 | 161.8 | 458.7 | 698.6 | 256.6 | 506.2 | 17.7 | 38.7 | 49.4 | 25.3 | 206.3 | 182.4 | 29.8 | 84.1
298 | 146 | 372.5 | 149 | 174.1724 | 189.7 | 197.9 | 195.1 | 198.3 | 389.6 | 21.5 | 21.8 | 40.8 | 2.6 | 153.7 | 5 | 299.2 | 868.4 | 761.2 | 344.8 | 515.6 | 163.2 | 460.8 | 696.1 | 258.5 | 509.7 | 17.8 | 38.9 | 49.8 | 25.4 | 206.2 | 182.9 | 30 | 84.6
299 | 147 | 372.7 | 149.08 | 174.2659 | 189.2 | 198 | 195.7 | 198 | 385.6 | 21.6 | 21.8 | 40.9 | 2.3 | 150.4 | 4.6 | 301.1 | 871.1 | 773.7 | 348.2 | 518.1 | 164.5 | 461.7 | 688.8 | 260.2 | 510.9 | 17.8 | 39.1 | 50 | 25.5 | 206.4 | 183.8 | 30.2 | 85
300 | 148 | 372 | 148.8 | 173.9386 | 188.3 | 197.8 | 196 | 198.1 | 382.6 | 21.6 | 21.8 | 41 | 2.3 | 156.2 | 4.3 | 303.1 | 868.8 | 784 | 351.9 | 522.6 | 165.8 | 465.8 | 698.5 | 262.1 | 514.9 | 17.8 | 39.2 | 50.2 | 25.6 | 206.6 | 184.9 | 30.4 | 85.4
301 | 149 | 371.6 | 148.64 | 173.7516 | 188.5 | 197.5 | 196.1 | 198.5 | 384.1 | 21.7 | 21.8 | 41.1 | 2.5 | 164.3 | 4.1 | 304.9 | 861.5 | 791.3 | 356.1 | 529 | 167.2 | 478.2 | 696.7 | 265.2 | 521.2 | 17.8 | 39.4 | 50.3 | 25.7 | 206.4 | 185.8 | 30.6 | 86.2
302 | 150 | 372.5 | 149 | 174.1724 | 188.7 | 196.2 | 196.4 | 198.6 | 381.2 | 21.7 | 21.8 | 41.3 | 2.2 | 174 | 3.7 | 306.8 | 871.3 | 793.2 | 360.1 | 531 | 168.5 | 483.9 | 695.6 | 268.5 | 523.1 | 17.9 | 39.6 | 50.5 | 25.8 | 206.7 | 185.9 | 30.8 | 86.7
303 | 151 | 369.8 | 147.92 | 172.91 | 188.7 | 195.5 | 196.8 | 198.7 | 381.7 | 21.8 | 21.8 | 41.4 | 2.3 | 191 | 3.3 | 308.5 | 876.6 | 780.8 | 362.9 | 531.2 | 169.9 | 487.5 | 681.2 | 270.6 | 525.7 | 17.9 | 39.8 | 50.7 | 25.9 | 206.7 | 186.2 | 31 | 87.3
304 | 152 | 369.9 | 147.96 | 172.9567 | 188.9 | 196.5 | 197.1 | 198.7 | 377.9 | 21.8 | 21.8 | 41.6 | 2.4 | 192.5 | 3.2 | 310.2 | 876.8 | 771.1 | 364.5 | 533.2 | 171.2 | 488.8 | 675.2 | 272.2 | 525.9 | 17.9 | 40 | 50.9 | 26 | 206.6 | 186.7 | 31.1 | 87.9
305 | 153 | 368.5 | 147.4 | 172.3021 | 188.6 | 197.5 | 197.1 | 198.7 | 376.5 | 21.8 | 21.8 | 41.7 | 2.4 | 171.6 | 3.8 | 312.3 | 874.7 | 785.2 | 366.9 | 538.8 | 172.6 | 494.3 | 690.6 | 274.8 | 529.7 | 17.9 | 40.2 | 51.1 | 26.1 | 206.6 | 186.9 | 31.3 | 88.2
306 | 154 | 369.6 | 147.84 | 172.8164 | 188.9 | 196.9 | 197.6 | 198.7 | 377.1 | 21.9 | 21.8 | 41.8 | 2.1 | 166.5 | 4 | 314.7 | 881.1 | 785.4 | 370.6 | 540.4 | 173.9 | 497.2 | 701.5 | 278.1 | 532.4 | 18 | 40.4 | 51.5 | 26.2 | 206.8 | 187.1 | 31.5 | 88.6
307 | 155 | 370.3 | 148.12 | 173.1437 | 189.7 | 195.6 | 198.5 | 198.6 | 382.4 | 21.9 | 21.8 | 41.9 | 2.1 | 168.5 | 4 | 317.6 | 886.8 | 801.7 | 374.6 | 542.6 | 175.3 | 496 | 710 | 280.3 | 533.9 | 18 | 40.6 | 51.8 | 26.3 | 206.9 | 187.4 | 31.7 | 89
308 | 156 | 371.5 | 148.6 | 173.7048 | 189.2 | 194.5 | 199.1 | 198.3 | 387.4 | 21.9 | 21.8 | 42 | 2.1 | 180.9 | 3.6 | 320.4 | 878.6 | 804 | 378.5 | 548.3 | 176.7 | 498.7 | 724.2 | 282.8 | 537.6 | 18 | 40.8 | 52.1 | 26.4 | 207.2 | 187.9 | 31.9 | 89.2
309 | 157 | 371.1 | 148.44 | 173.5178 | 188.8 | 193.6 | 199.7 | 198.5 | 394.7 | 21.9 | 21.8 | 42.1 | 2.3 | 206.6 | 3.8 | 323.2 | 877.1 | 812 | 382.1 | 552.8 | 178.1 | 500.2 | 725 | 285.1 | 540 | 18 | 41 | 52.4 | 26.5 | 207.3 | 188.2 | 32.1 | 89.7
310 | 158 | 370.7 | 148.28 | 173.3308 | 189.1 | 192.8 | 200.1 | 198.7 | 393.3 | 22 | 21.8 | 42.2 | 2.4 | 182.2 | 3.9 | 326.2 | 877.9 | 805.2 | 386 | 556.3 | 179.4 | 501.5 | 725.7 | 287.2 | 541.6 | 18.1 | 41.2 | 52.6 | 26.7 | 207.5 | 188.3 | 32.3 | 90.2
311 | 159 | 369.7 | 147.88 | 172.8632 | 189.4 | 193.1 | 200.6 | 198.8 | 396.3 | 22 | 21.7 | 42.3 | 2.4 | 167.2 | 4.2 | 328.9 | 877.1 | 793.1 | 389 | 556.5 | 180.6 | 499 | 722.1 | 288.6 | 540.8 | 18.1 | 41.4 | 52.7 | 26.8 | 207.5 | 188.5 | 32.5 | 90.7
312 | 160 | 369.1 | 147.64 | 172.5827 | 189.7 | 194.4 | 201.2 | 198.6 | 394.3 | 22.1 | 21.7 | 42.4 | 2.1 | 182.5 | 4.4 | 331.5 | 880.3 | 788.9 | 391.2 | 557.4 | 181.8 | 495.1 | 717.1 | 288.9 | 540 | 18.1 | 41.6 | 53 | 26.9 | 207.6 | 188.7 | 32.6 | 91.1
313 | 161 | 369.6 | 147.84 | 172.8164 | 190.6 | 196 | 201.4 | 198.6 | 390 | 22.1 | 21.7 | 42.5 | 2.4 | 178.8 | 4.3 | 334.3 | 881.1 | 776.3 | 393.7 | 558.4 | 183 | 491.2 | 710.7 | 289.3 | 540.7 | 18.2 | 41.8 | 53.3 | 27 | 207.6 | 189.1 | 32.8 | 91.5
314 | 162 | 370.4 | 148.16 | 173.1905 | 191.4 | 197 | 201.5 | 198.8 | 387.3 | 22.1 | 21.7 | 42.5 | 2.3 | 178.4 | 4 | 336.7 | 883.8 | 775.2 | 395.8 | 556.9 | 184.1 | 488.9 | 709.3 | 290.6 | 539.8 | 18.2 | 42 | 53.6 | 27.1 | 207.9 | 189.3 | 33 | 92.1
315 | 163 | 370.4 | 148.16 | 173.1905 | 192.1 | 197.7 | 201.8 | 199 | 388.1 | 22.1 | 21.7 | 42.6 | 2.4 | 207.8 | 4.1 | 339.6 | 885.6 | 774.3 | 398.7 | 560 | 185.3 | 487.7 | 714.7 | 292.1 | 542 | 18.2 | 42.2 | 53.8 | 27.2 | 208.7 | 189.5 | 33.2 | 92.5
316 | 164 | 370.2 | 148.08 | 173.097 | 193 | 197.8 | 201.9 | 199.5 | 393.3 | 22.2 | 21.7 | 42.7 | 2.5 | 202.9 | 4.5 | 342.6 | 885.6 | 771 | 401.8 | 560.3 | 186.4 | 482.4 | 701.3 | 292.7 | 540.4 | 18.2 | 42.4 | 54.2 | 27.3 | 209.2 | 189.6 | 33.4 | 93
317 | 165 | 370.8 | 148.32 | 173.3775 | 194.1 | 197.8 | 202.3 | 200 | 392.5 | 22.3 | 21.7 | 42.8 | 2.3 | 191 | 5.1 | 344.7 | 876.3 | 781.5 | 404.7 | 563.6 | 187.4 | 481.9 | 700.2 | 294.7 | 540.7 | 18.3 | 42.6 | 54.3 | 27.4 | 210 | 190.3 | 33.6 | 93.7
318 | 166 | 371.6 | 148.64 | 173.7516 | 194.7 | 196.8 | 202.7 | 199.9 | 395.8 | 22.4 | 21.7 | 42.9 | 2.1 | 194.2 | 5.7 | 346.5 | 873.2 | 778.8 | 407.8 | 565.6 | 188.5 | 491.1 | 710.5 | 299.4 | 545.7 | 18.3 | 42.8 | 54.2 | 27.5 | 210 | 190.4 | 33.8 | 94.1
319 | 167 | 370.6 | 148.24 | 173.284 | 194.4 | 195.9 | 202.9 | 200.1 | 397.8 | 22.4 | 21.7 | 43 | 2.4 | 188.5 | 6.2 | 349 | 876.7 | 789.1 | 410.8 | 568.7 | 189.3 | 498.6 | 717.4 | 303.7 | 549.4 | 18.3 | 43 | 54.5 | 27.7 | 210.1 | 190.7 | 34 | 94.5
320 | 168 | 371.1 | 148.44 | 173.5178 | 193.5 | 195 | 203 | 200.3 | 394.2 | 22.4 | 21.7 | 43.1 | 2.3 | 185.4 | 6.2 | 351.1 | 874.6 | 791.1 | 413.4 | 569.3 | 190.3 | 499.2 | 708.4 | 306.1 | 549.1 | 18.4 | 43.2 | 54.6 | 27.8 | 210.2 | 191.1 | 34.2 | 95
321 | 169 | 371.9 | 148.76 | 173.8919 | 193.8 | 194.2 | 203.4 | 200.7 | 389.1 | 22.4 | 21.7 | 43.1 | 2.1 | 191.9 | 6.3 | 353.7 | 877.5 | 793.2 | 416.2 | 571 | 191.5 | 500.1 | 702.9 | 308.8 | 549.1 | 18.4 | 43.4 | 55 | 27.9 | 212.4 | 191.7 | 34.3 | 95.5
322 | 170 | 372.7 | 149.08 | 174.2659 | 193.7 | 194 | 203.9 | 201.2 | 385.9 | 22.5 | 21.7 | 43.2 | 2.3 | 195.8 | 6.5 | 356.4 | 868.1 | 801.4 | 420.1 | 573.9 | 192.8 | 502.4 | 715.4 | 312.2 | 551.6 | 18.4 | 43.6 | 55.5 | 28 | 212.6 | 192.7 | 34.5 | 96.2
323 | 171 | 372.4 | 148.96 | 174.1257 | 194.6 | 193.2 | 204.9 | 202.1 | 394 | 22.5 | 21.7 | 43.3 | 2.4 | 186.7 | 6.4 | 359.6 | 862.7 | 799.2 | 423.7 | 576.6 | 194.3 | 508.5 | 724.3 | 315.9 | 557 | 18.4 | 43.8 | 55.9 | 28.1 | 212.6 | 193.4 | 34.7 | 96.6
324 | 172 | 371 | 148.4 | 173.471 | 195.5 | 192.2 | 205.6 | 202.8 | 396.7 | 22.6 | 21.7 | 43.4 | 2.3 | 185.5 | 6.2 | 362.8 | 868.7 | 785.7 | 426.9 | 577 | 195.9 | 509.8 | 716.6 | 318.3 | 558.1 | 18.5 | 44 | 56.1 | 28.3 | 212.9 | 193.8 | 34.9 | 97.1
325 | 173 | 370.9 | 148.36 | 173.4243 | 195.8 | 191.9 | 205.9 | 203.2 | 391.7 | 22.6 | 21.7 | 43.5 | 2.5 | 195.6 | 6 | 365.7 | 874.6 | 783.5 | 429.9 | 578.5 | 197.4 | 506.5 | 722.8 | 320.7 | 558 | 18.5 | 44.2 | 56.4 | 28.4 | 213.6 | 194.3 | 35.1 | 97.6
326 | 174 | 370.8 | 148.32 | 173.3775 | 196.1 | 192.9 | 206.4 | 203.5 | 396.6 | 22.7 | 21.7 | 43.5 | 2.5 | 192.1 | 6.3 | 368.4 | 872.2 | 780.1 | 432.7 | 579.6 | 198.9 | 503.6 | 717.6 | 323.2 | 558.1 | 18.5 | 44.4 | 56.7 | 28.5 | 214.5 | 194.4 | 35.3 | 98
327 | 175 | 370.9 | 148.36 | 173.4243 | 196 | 194.2 | 206.7 | 204.2 | 393.7 | 22.7 | 21.7 | 43.6 | 2.6 | 189.5 | 6.3 | 370.7 | 870.9 | 789.5 | 434.6 | 581.7 | 200.1 | 501.2 | 713.5 | 325.8 | 557.4 | 18.6 | 44.6 | 56.8 | 28.6 | 214.3 | 194.2 | 35.5 | 98.5
328 | 176 | 372.3 | 148.92 | 174.0789 | 196.5 | 194.8 | 206.7 | 204.7 | 390.9 | 22.8 | 21.7 | 43.7 | 2.3 | 189.1 | 6.3 | 373.7 | 868.3 | 799.2 | 436.9 | 585 | 201.2 | 504 | 720.9 | 329.5 | 560.4 | 18.6 | 44.8 | 56.9 | 28.7 | 214.2 | 194.2 | 35.7 | 99
329 | 177 | 372.4 | 148.96 | 174.1257 | 197.1 | 194.9 | 206.8 | 205 | 399 | 22.8 | 21.7 | 43.8 | 2.5 | 186.9 | 6 | 376.8 | 861.7 | 807.4 | 439.2 | 589 | 202.3 | 507.5 | 740.3 | 334.1 | 566 | 18.6 | 45 | 57.1 | 28.8 | 214.5 | 194.4 | 35.9 | 99.4
330 | 178 | 371.8 | 148.72 | 173.8451 | 196.6 | 194.8 | 206.8 | 205.1 | 408.4 | 22.9 | 21.6 | 43.9 | 2.4 | 189.8 | 5.7 | 380.3 | 869.9 | 797.6 | 442.1 | 590 | 203.2 | 506.8 | 744.2 | 337.1 | 567.8 | 18.6 | 45.2 | 57.5 | 28.9 | 214.6 | 194.4 | 36.1 | 99.9
331 | 179 | 369.9 | 147.96 | 172.9567 | 197.1 | 195.2 | 206.8 | 205.2 | 419.7 | 22.9 | 21.6 | 44 | 2.4 | 201.1 | 5.9 | 384.3 | 869.8 | 800.5 | 444.3 | 592.1 | 204.2 | 509.7 | 752.7 | 340.2 | 571.3 | 18.7 | 45.5 | 58 | 29.1 | 215.1 | 194.5 | 36.3 | 100.2
332 | 180 | 372.2 | 148.88 | 174.0321 | 196.2 | 196.5 | 207 | 205.9 | 420.3 | 23 | 21.6 | 44.1 | 2.5 | 184.6 | 6 | 388.1 | 864.4 | 807.7 | 445.8 | 595.5 | 205.3 | 510.7 | 746.6 | 342.8 | 573.5 | 18.7 | 45.7 | 58.3 | 29.2 | 215.3 | 194.9 | 36.5 | 100.7
333 | 181 | 371.3 | 148.52 | 173.6113 | 196.2 | 197.5 | 207.6 | 206.8 | 418.7 | 23.1 | 21.6 | 44.2 | 2.5 | 181.2 | 6 | 392 | 864.6 | 804.9 | 447.6 | 597 | 206.3 | 511.9 | 753.7 | 346.2 | 575 | 18.7 | 45.9 | 58.6 | 29.3 | 215.3 | 195.5 | 36.7 | 101.2
334 | 182 | 371 | 148.4 | 173.471 | 196.7 | 198.4 | 207.5 | 207.6 | 418 | 23.1 | 21.6 | 44.3 | 2.5 | 184.5 | 5.9 | 395.5 | 862.3 | 809.6 | 448.7 | 600.3 | 207.3 | 509.8 | 754.3 | 349.1 | 576.4 | 18.8 | 46.1 | 58.7 | 29.4 | 215.6 | 196.3 | 36.9 | 101.7
335 | 183 | 371.9 | 148.76 | 173.8919 | 196.1 | 200.1 | 207.1 | 208.2 | 417.7 | 23.2 | 21.6 | 44.4 | 2.7 | 188.6 | 5.6 | 398.8 | 864 | 808.5 | 450.7 | 602.4 | 208.4 | 513.1 | 765 | 353.8 | 579.8 | 18.8 | 46.3 | 58.8 | 29.6 | 216 | 196.8 | 37.1 | 102.3
336 | 184 | 371.4 | 148.56 | 173.6581 | 195.8 | 201.3 | 206.9 | 208.5 | 414.4 | 23.2 | 21.6 | 44.5 | 2.4 | 184.4 | 5.7 | 401.6 | 871.6 | 791.2 | 452.8 | 603.2 | 209.4 | 511.8 | 752.3 | 355.2 | 580.2 | 18.8 | 46.6 | 59.2 | 29.7 | 217.1 | 197.8 | 37.3 | 102.8
337 | 185 | 371.7 | 148.68 | 173.7984 | 196.4 | 201.9 | 206.4 | 208.8 | 411 | 23.2 | 21.6 | 44.6 | 2.2 | 179.3 | 5.7 | 403.7 | 866.8 | 783.8 | 453.9 | 603.4 | 210.3 | 507.1 | 750.1 | 358.4 | 580.2 | 18.9 | 46.8 | 59.6 | 29.8 | 217.3 | 198.2 | 37.5 | 103.2
338 | 186 | 370.9 | 148.36 | 173.4243 | 197.9 | 202.5 | 205.9 | 209.3 | 411.2 | 23.3 | 21.6 | 44.7 | 2.5 | 190.8 | 5.4 | 406.3 | 861.8 | 778.2 | 454.6 | 602.3 | 211.3 | 502.8 | 748.1 | 361.2 | 580.7 | 18.9 | 47 | 60 | 29.9 | 217.5 | 198.3 | 37.7 | 103.6
339 | 187 | 371.4 | 148.56 | 173.6581 | 199 | 203.3 | 205.7 | 210 | 412.2 | 23.3 | 21.6 | 44.8 | 2.1 | 200.3 | 5.3 | 409 | 854.6 | 788.6 | 455.5 | 603.4 | 212.3 | 499.6 | 748.6 | 364.3 | 580.4 | 18.9 | 47.2 | 60.2 | 30.1 | 217.7 | 198.6 | 37.9 | 104.1
340 | 188 | 371.3 | 148.52 | 173.6113 | 200.7 | 203.8 | 205.7 | 210.4 | 414 | 23.4 | 21.6 | 44.9 | 2.1 | 189.5 | 5 | 411.7 | 852.3 | 788.7 | 456.6 | 605.2 | 213.5 | 500.8 | 746.6 | 368 | 580.1 | 19 | 47.4 | 60.3 | 30.2 | 217.8 | 198.7 | 38.1 | 104.6
341 | 189 | 371.1 | 148.44 | 173.5178 | 201.3 | 203.9 | 205.3 | 210.7 | 416.7 | 23.4 | 21.6 | 45 | 2.6 | 188.4 | 5 | 414.6 | 853.2 | 780.7 | 457.6 | 604.9 | 214.7 | 497.9 | 743.7 | 370.2 | 580.1 | 19 | 47.6 | 60.6 | 30.3 | 217.8 | 198.8 | 38.3 | 105
342 | 190 | 371.3 | 148.52 | 173.6113 | 201.8 | 203.7 | 204.9 | 210.7 | 415 | 23.5 | 21.6 | 45.1 | 2.1 | 187.9 | 5.1 | 416.9 | 852 | 779.2 | 458.3 | 604.5 | 216 | 497.6 | 738 | 374.4 | 579.5 | 19.1 | 47.9 | 60.8 | 30.4 | 217.7 | 199.9 | 38.5 | 105.4
343 | 191 | 372 | 148.8 | 173.9386 | 202.2 | 202.5 | 204.9 | 210.6 | 419.7 | 23.5 | 21.6 | 45.2 | 1.8 | 191.5 | 5.1 | 419.8 | 851.8 | 787.5 | 459.1 | 605.6 | 217.3 | 496.2 | 740.7 | 377.1 | 579 | 19.1 | 48.1 | 61 | 30.6 | 217.9 | 200.3 | 38.7 | 105.9
344 | 192 | 372.1 | 148.84 | 173.9854 | 202.8 | 202.3 | 205.2 | 210.8 | 427.2 | 23.4 | 21.6 | 45.3 | 2.3 | 192.9 | 4.8 | 423.2 | 856.1 | 760.4 | 460.3 | 603.6 | 218.6 | 494.2 | 750.7 | 379 | 579.1 | 19.1 | 48.3 | 61.4 | 30.7 | 218.7 | 200.4 | 38.9 | 106.4
345 | 193 | 371.5 | 148.6 | 173.7048 | 204.2 | 203.7 | 205.7 | 210.8 | 441.7 | 23.5 | 21.6 | 45.4 | 2.3 | 193 | 4.5 | 427 | 854.9 | 741.3 | 461 | 601.2 | 219.9 | 492 | 746.5 | 379.9 | 579.4 | 19.2 | 48.5 | 61.9 | 30.8 | 219.3 | 200.4 | 39 | 106.9
346 | 194 | 372.1 | 148.84 | 173.9854 | 205.5 | 205.5 | 206.4 | 211.4 | 448.9 | 23.5 | 21.6 | 45.5 | 2.6 | 193.1 | 4.3 | 430.6 | 852.2 | 723.8 | 461.1 | 599.2 | 221.2 | 491 | 751.5 | 382.8 | 579.9 | 19.2 | 48.7 | 62.3 | 30.9 | 219.9 | 200.5 | 39.3 | 107.4
347 | 195 | 371.4 | 148.56 | 173.6581 | 206.6 | 207.7 | 206.9 | 212 | 449.4 | 23.6 | 21.6 | 45.6 | 2.5 | 195 | 4.1 | 432.4 | 843.5 | 717.9 | 460.9 | 598.1 | 222.5 | 487.7 | 743.5 | 384.2 | 579.8 | 19.2 | 49 | 62.4 | 31 | 219.9 | 200.3 | 39.5 | 107.8
348 | 196 | 372.4 | 148.96 | 174.1257 | 207 | 208.3 | 207.4 | 212.1 | 450.4 | 23.6 | 21.6 | 45.8 | 3 | 197.9 | 3.9 | 434.9 | 841.2 | 725 | 461 | 596.5 | 223.7 | 487.9 | 740.9 | 387.6 | 579.6 | 19.3 | 49.2 | 62.6 | 31.2 | 220.8 | 200.2 | 39.7 | 108.3
349 | 197 | 372.1 | 148.84 | 173.9854 | 207.7 | 209.1 | 207.9 | 212.5 | 455.3 | 23.7 | 21.5 | 45.9 | 2.5 | 198.4 | 3.9 | 437.6 | 836.2 | 719 | 461.6 | 595.3 | 224.9 | 487 | 741.5 | 389.3 | 578.8 | 19.3 | 49.4 | 62.8 | 31.3 | 221.4 | 200.6 | 39.9 | 108.7
350 | 198 | 369.5 | 147.8 | 172.7697 | 208 | 209.4 | 208.3 | 212.9 | 462.1 | 23.7 | 21.5 | 46 | 2.6 | 194.4 | 4.3 | 440.3 | 833.8 | 710.7 | 461.5 | 592.6 | 226.1 | 481.9 | 732.7 | 388.4 | 577.3 | 19.3 | 49.6 | 63.3 | 31.4 | 221.7 | 200.7 | 40.1 | 109.1
351 | 199 | 371.5 | 148.6 | 173.7048 | 207.8 | 209.6 | 208.8 | 213.1 | 461.9 | 23.8 | 21.6 | 46.1 | 2.9 | 184.2 | 4.4 | 442.6 | 836.2 | 715.2 | 462.2 | 591.6 | 227.3 | 479.4 | 730 | 388.8 | 576.5 | 19.4 | 49.8 | 63.7 | 31.6 | 222.2 | 200.6 | 40.3 | 109.6
352 | 200 | 371.6 | 148.64 | 173.7516 | 206.8 | 210.4 | 209.1 | 213.5 | 459.8 | 23.8 | 21.5 | 46.3 | 2.7 | 170.3 | 4.7 | 445.3 | 835.5 | 722.7 | 463.5 | 590.9 | 228.6 | 479.3 | 734.2 | 390.8 | 576.5 | 19.4 | 50.1 | 64 | 31.7 | 222.3 | 200.7 | 40.5 | 110
353 | 201 | 368.8 | 147.52 | 172.4424 | 206.5 | 210.8 | 209.4 | 213.8 | 465.3 | 23.9 | 21.5 | 46.4 | 2.6 | 171.2 | 4.9 | 448.9 | 836.4 | 742 | 464.7 | 591.5 | 229.8 | 482.7 | 739.5 | 393.4 | 578.7 | 19.5 | 50.3 | 64.3 | 31.8 | 222.7 | 201.5 | 40.7 | 110.4
354 | 202 | 368.7 | 147.48 | 172.3956 | 207.4 | 210.3 | 209.7 | 213.9 | 466.4 | 24 | 21.5 | 46.5 | 2.5 | 178.5 | 4.8 | 452.2 | 841.4 | 753.1 | 466.1 | 593.1 | 231.1 | 483.6 | 739.6 | 395.8 | 579.5 | 19.5 | 50.5 | 64.6 | 31.9 | 222.8 | 202 | 40.9 | 111.1
355 | 203 | 369.2 | 147.68 | 172.6294 | 207.3 | 210.4 | 210.1 | 214.3 | 462.1 | 24 | 21.5 | 46.5 | 2.6 | 187.7 | 5.2 | 454.5 | 842.4 | 759.6 | 466.7 | 595.1 | 232.4 | 482.4 | 733.1 | 397.1 | 578.6 | 19.5 | 50.7 | 64.9 | 32.1 | 223.4 | 202.1 | 41.1 | 111.6
356 | 204 | 370.5 | 148.2 | 173.2373 | 207 | 210.9 | 210.3 | 214.9 | 457 | 24.1 | 21.5 | 46.6 | 2.8 | 190.8 | 5 | 456.9 | 844.3 | 762.6 | 467.9 | 594.8 | 233.6 | 479.6 | 740.7 | 399.5 | 580.2 | 19.6 | 50.9 | 65.1 | 32.2 | 223.7 | 202.3 | 41.3 | 112
357 | 205 | 371.3 | 148.52 | 173.6113 | 207.4 | 211.2 | 210.7 | 215.3 | 454.3 | 24.2 | 21.5 | 46.7 | 2.9 | 174.7 | 4.4 | 458.8 | 851.4 | 755.7 | 469.7 | 594.9 | 234.8 | 481.8 | 745.4 | 403.3 | 580.9 | 19.6 | 51.2 | 65.5 | 32.3 | 223.8 | 202.5 | 41.5 | 112.5
358 | 206 | 370.7 | 148.28 | 173.3308 | 207.3 | 211.9 | 210.9 | 215.4 | 451.9 | 24.2 | 21.5 | 46.8 | 2.6 | 155.7 | 4 | 460.4 | 853.9 | 754.6 | 470.8 | 594.8 | 236 | 478.9 | 741.1 | 404.5 | 579.7 | 19.6 | 51.4 | 65.6 | 32.4 | 224.1 | 203 | 41.7 | 113.1
359 | 207 | 373 | 149.2 | 174.4062 | 206.5 | 213 | 211.1 | 215.3 | 447 | 24.3 | 21.5 | 46.9 | 2.1 | 192.7 | 3.6 | 462.3 | 854.6 | 760.2 | 471.6 | 594 | 237.2 | 475.5 | 723.9 | 404.3 | 579.1 | 19.7 | 51.6 | 65.9 | 32.6 | 223.8 | 203.6 | 41.9 | 113.8
360 | 208 | 368.4 | 147.36 | 172.2553 | 205.9 | 214.2 | 211.2 | 214.9 | 436.8 | 24.4 | 21.5 | 47 | 2.2 | 210.1 | 3.5 | 464.5 | 855.7 | 775.9 | 472.5 | 597 | 238.2 | 476 | 727.1 | 407.4 | 579.4 | 19.7 | 51.8 | 66 | 32.7 | 223.6 | 203.5 | 42.1 | 114.3
361 | 209 | 370 | 148 | 173.0035 | 205.4 | 214.6 | 211.3 | 214.7 | 437.6 | 24.4 | 21.5 | 47.1 | 2.2 | 184.1 | 3.8 | 467.3 | 852.2 | 795.1 | 473.2 | 600.6 | 239.3 | 480.2 | 744.7 | 411.4 | 582.6 | 19.8 | 52 | 66.4 | 32.8 | 224.1 | 203.4 | 42.3 | 114.8
362 | 210 | 370.4 | 148.16 | 173.1905 | 205.5 | 214.3 | 211.5 | 214.2 | 447.1 | 24.5 | 21.5 | 47.2 | 2.9 | 171.7 | 4.6 | 470.3 | 845.4 | 806 | 474.3 | 605.8 | 240.4 | 487.6 | 754.3 | 416.5 | 586.3 | 19.8 | 52.2 | 66.8 | 33 | 224 | 203.4 | 42.6 | 115.3
363 | 211 | 371 | 148.4 | 173.471 | 205.1 | 214 | 211.6 | 214.2 | 450.1 | 24.5 | 21.5 | 47.3 | 2.5 | 175.7 | 5.4 | 473.2 | 844.5 | 806.3 | 475.1 | 607 | 241.4 | 489.5 | 756.5 | 417.9 | 587.5 | 19.8 | 52.5 | 67.2 | 33.1 | 224.1 | 203.2 | 42.7 | 115.6
364 | 212 | 370.7 | 148.28 | 173.3308 | 205 | 214.2 | 211.7 | 214.4 | 452.7 | 24.5 | 21.5 | 47.4 | 2.3 | 183.4 | 5.3 | 477.1 | 855 | 789 | 475.9 | 608.7 | 242.3 | 488.6 | 751.1 | 418 | 589.1 | 19.9 | 52.7 | 67.4 | 33.2 | 224.1 | 203.5 | 43 | 115.9
365 | 213 | 372.7 | 149.08 | 174.2659 | 205 | 215.5 | 212 | 214.5 | 454.7 | 24.6 | 21.5 | 47.5 | 2.8 | 202.1 | 5 | 480.8 | 860.5 | 793.9 | 476.2 | 608.9 | 243.2 | 488.3 | 760.2 | 420.5 | 591.1 | 19.9 | 52.9 | 67.6 | 33.4 | 224.3 | 203.7 | 43.2 | 116.3
366 | 214 | 373 | 149.2 | 174.4062 | 205 | 216 | 212.4 | 214.8 | 465 | 24.6 | 21.5 | 47.6 | 3 | 201.8 | 4.7 | 483.9 | 859.3 | 796.4 | 476.7 | 611.2 | 244.2 | 490.7 | 757.6 | 421.7 | 591.5 | 20 | 53.1 | 68.1 | 33.5 | 224.8 | 203.6 | 43.4 | 116.8
367 | 215 | 372 | 148.8 | 173.9386 | 204.6 | 216.2 | 213 | 215.4 | 465.9 | 24.7 | 21.5 | 47.7 | 2.7 | 193.4 | 4.7 | 486.2 | 861 | 800.7 | 476.9 | 614.3 | 245.1 | 490.7 | 754.1 | 422.9 | 592.7 | 20 | 53.4 | 68.5 | 33.6 | 225 | 204.3 | 43.6 | 117.3
368 | 216 | 371.1 | 148.44 | 173.5178 | 203.3 | 216.7 | 212.9 | 216.3 | 463.9 | 24.6 | 21.5 | 47.7 | 2.7 | 191.7 | 4.8 | 488.2 | 846.9 | 817.8 | 477.2 | 622.2 | 246.1 | 494.8 | 762.1 | 427.7 | 596.5 | 20.1 | 53.6 | 68.7 | 33.7 | 225.1 | 205.1 | 43.8 | 117.9
369 | 217 | 371.1 | 148.44 | 173.5178 | 201.8 | 217.2 | 212.6 | 216.9 | 464.1 | 24.6 | 21.5 | 47.8 | 2.6 | 200.7 | 4.8 | 489.8 | 840.9 | 819.3 | 477.2 | 627.4 | 247 | 494 | 765.1 | 427.6 | 596.1 | 20.1 | 53.8 | 68.9 | 33.9 | 225.8 | 205.3 | 44 | 118.3
370 | 218 | 371.2 | 148.48 | 173.5646 | 202.3 | 217.6 | 212.5 | 217.1 | 472.7 | 24.7 | 21.5 | 47.8 | 2.7 | 211.2 | 4.9 | 492.3 | 843.3 | 821.5 | 477 | 628.5 | 247.8 | 492.8 | 765.5 | 428.1 | 596.6 | 20.1 | 54 | 69.4 | 34 | 227.2 | 205.6 | 44.2 | 118.8
371 | 219 | 371.4 | 148.56 | 173.6581 | 203.1 | 217.6 | 212.8 | 217.6 | 477.8 | 24.7 | 21.5 | 47.9 | 2.6 | 195.1 | 5.2 | 494.6 | 851.6 | 796.2 | 476.9 | 628.2 | 248.6 | 493.1 | 764.4 | 429.2 | 598.3 | 20.2 | 54.3 | 69.9 | 34.2 | 227.9 | 206.2 | 44.4 | 119.2
372 | 220 | 371.4 | 148.56 | 173.6581 | 203.3 | 219 | 213.1 | 218.5 | 480.1 | 24.8 | 21.5 | 47.9 | 2.3 | 210.3 | 5.4 | 496.5 | 851.4 | 798.5 | 476.8 | 630.6 | 249.4 | 493.1 | 764.6 | 430.4 | 599.3 | 20.2 | 54.5 | 70.3 | 34.3 | 228.3 | 206.5 | 44.7 | 119.7
373 | 221 | 372 | 148.8 | 173.9386 | 204.1 | 220.2 | 213.5 | 219.3 | 478.5 | 24.9 | 21.5 | 48 | 2.6 | 212 | 5.5 | 498.1 | 846.3 | 801.7 | 477 | 634.1 | 250.2 | 494.5 | 771.6 | 431.9 | 601.4 | 20.3 | 54.7 | 70.3 | 34.4 | 228.6 | 206.8 | 44.9 | 120.1
374 | 222 | 371.7 | 148.68 | 173.7984 | 205.8 | 220.7 | 213.5 | 220.2 | 474.3 | 25 | 21.5 | 48.1 | 2.4 | 208.7 | 5.6 | 499.7 | 843.6 | 802.8 | 478 | 637.2 | 251.1 | 497.6 | 766.3 | 431.6 | 602.9 | 20.3 | 55 | 70.5 | 34.5 | 229 | 207.2 | 45.1 | 120.6
375 | 223 | 371.3 | 148.52 | 173.6113 | 207.1 | 220.3 | 213.2 | 220.7 | 464.6 | 25.1 | 21.5 | 48.1 | 2.4 | 205.3 | 6 | 501.1 | 847.4 | 779.5 | 478.5 | 636.9 | 252 | 497.8 | 760.4 | 429.8 | 604 | 20.4 | 55.2 | 71.1 | 34.7 | 229.3 | 207.2 | 45.3 | 121
376 | 224 | 370.7 | 148.28 | 173.3308 | 208.1 | 218.7 | 213.3 | 220.7 | 458.7 | 25.1 | 21.5 | 48.2 | 2.7 | 209.7 | 6 | 503.5 | 853 | 775.8 | 478.8 | 637.4 | 253 | 497.1 | 761.3 | 428.8 | 605.5 | 20.4 | 55.4 | 71.3 | 34.8 | 229.3 | 207.7 | 45.5 | 121.5
377 | 225 | 371.7 | 148.68 | 173.7984 | 209.1 | 217.4 | 213.6 | 220.5 | 451.2 | 25.1 | 21.5 | 48.2 | 2.3 | 211.7 | 6 | 505.5 | 855 | 768.8 | 479.1 | 637.3 | 254 | 497.3 | 761.3 | 427.9 | 605 | 20.4 | 55.6 | 71.5 | 34.9 | 229.2 | 208.2 | 45.7 | 122
378 | 226 | 371.6 | 148.64 | 173.7516 | 209.9 | 216.2 | 213.7 | 220.2 | 447.9 | 25.1 | 21.5 | 48.3 | 2.7 | 209.2 | 5.8 | 507.5 | 859.4 | 764.3 | 479 | 637.8 | 255.1 | 499.4 | 760.9 | 427.9 | 605.6 | 20.5 | 55.9 | 71.6 | 35.1 | 229.4 | 208.4 | 45.9 | 122.3
379 | 227 | 371.3 | 148.52 | 173.6113 | 210.2 | 216.5 | 213.8 | 219.8 | 440 | 25.1 | 21.4 | 48.4 | 2.8 | 202.5 | 5.5 | 509.2 | 855.8 | 767.3 | 479 | 640.7 | 256.2 | 497.2 | 759.4 | 428 | 608.1 | 20.5 | 56.1 | 71.7 | 35.2 | 229.4 | 208.8 | 46.1 | 122.9
380 | 228 | 371.6 | 148.64 | 173.7516 | 210.5 | 217.5 | 214.2 | 219.4 | 432.8 | 25.2 | 21.4 | 48.4 | 2.8 | 194.4 | 5.1 | 511.6 | 850.3 | 776 | 479.1 | 641.4 | 257.2 | 498.4 | 755.1 | 427.6 | 609.4 | 20.6 | 56.3 | 72 | 35.4 | 229.3 | 208.7 | 46.4 | 123.3
381 | 229 | 371.7 | 148.68 | 173.7984 | 209.9 | 218.2 | 214.1 | 218.8 | 432.6 | 25.2 | 21.4 | 48.5 | 2.6 | 193.5 | 4.6 | 513.7 | 840.1 | 793.7 | 479.8 | 647 | 258.3 | 501.5 | 758.2 | 428.8 | 610.5 | 20.6 | 56.5 | 72.3 | 35.5 | 229 | 208.9 | 46.6 | 123.7
382 | 230 | 371.4 | 148.56 | 173.6581 | 209.6 | 219 | 214 | 218.2 | 434.3 | 25.2 | 21.4 | 48.6 | 2.5 | 193.4 | 4.2 | 515.6 | 831 | 801.8 | 480.9 | 650.4 | 259.3 | 503.9 | 761.5 | 428.2 | 612.3 | 20.7 | 56.7 | 72.7 | 35.6 | 228.9 | 209 | 46.8 | 124
383 | 231 | 372 | 148.8 | 173.9386 | 210.5 | 219.2 | 214.1 | 217.7 | 438.9 | 25.3 | 21.4 | 48.7 | 2.8 | 200.7 | 4 | 517.5 | 825.2 | 804 | 481.7 | 651.1 | 260.4 | 507.5 | 767.7 | 428.8 | 613.4 | 20.7 | 56.9 | 72.8 | 35.8 | 228.6 | 209.3 | 46.9 | 124.4
384 | 232 | 371.3 | 148.52 | 173.6113 | 210.7 | 219 | 214.1 | 217.3 | 445.9 | 25.4 | 21.4 | 48.8 | 2.9 | 194.1 | 4.1 | 519.9 | 826.5 | 801.3 | 482.2 | 651.1 | 261.5 | 508.6 | 771.5 | 429.1 | 614.6 | 20.8 | 57.2 | 73.1 | 35.9 | 228.6 | 209.5 | 47.2 | 124.7
385 | 233 | 371.1 | 148.44 | 173.5178 | 210 | 220.3 | 214.3 | 217.4 | 440.7 | 25.5 | 21.4 | 48.9 | 2.9 | 178 | 4.3 | 522.6 | 825.4 | 801.8 | 482.3 | 653.1 | 262.7 | 509.1 | 766.7 | 428.8 | 614.1 | 20.8 | 57.4 | 73.3 | 36 | 228.7 | 209.5 | 47.5 | 125.2
386 | 234 | 370.8 | 148.32 | 173.3775 | 209.8 | 220.4 | 214.7 | 218 | 441 | 25.6 | 21.4 | 49 | 2.9 | 179 | 4.4 | 526 | 823.1 | 802.2 | 482.3 | 655 | 263.9 | 511 | 772.5 | 429.8 | 616.1 | 20.9 | 57.6 | 73.5 | 36.2 | 228.5 | 209.4 | 47.6 | 125.6
387 | 235 | 371.7 | 148.68 | 173.7984 | 210.9 | 219.9 | 214.9 | 218.5 | 449.3 | 25.7 | 21.4 | 49.1 | 3 | 191.2 | 4.4 | 528.7 | 818 | 797.1 | 482.5 | 654.9 | 265.2 | 514.8 | 777.1 | 431.6 | 618.9 | 20.9 | 57.7 | 73.9 | 36.3 | 228.3 | 210.3 | 47.9 | 126.2
388 | 236 | 371.7 | 148.68 | 173.7984 | 211.9 | 219.8 | 215 | 218.7 | 456.7 | 25.8 | 21.4 | 49.3 | 2.8 | 193.6 | 4.3 | 532.1 | 817.2 | 792.4 | 482 | 654.5 | 266.5 | 515.5 | 776.2 | 432.3 | 619 | 21 | 58 | 74.3 | 36.4 | 228.2 | 210.6 | 48 | 126.7
389 | 237 | 371.5 | 148.6 | 173.7048 | 213 | 220.3 | 215.2 | 218.8 | 463 | 25.9 | 21.4 | 49.4 | 2.7 | 189.9 | 4.2 | 535.6 | 818.9 | 798.6 | 481.4 | 655 | 267.8 | 514.8 | 772.2 | 432.6 | 618.5 | 21 | 58.2 | 74.6 | 36.6 | 228.4 | 210.8 | 48.3 | 127
390 | 238 | 371 | 148.4 | 173.471 | 213.7 | 221.1 | 215.3 | 219.3 | 462.5 | 26 | 21.4 | 49.5 | 2.8 | 188.9 | 3.9 | 538.7 | 815.8 | 815.8 | 480.8 | 658.7 | 269 | 517.5 | 773.8 | 433.7 | 620.3 | 21.1 | 58.5 | 74.8 | 36.7 | 228.4 | 211.4 | 48.5 | 127.4
391 | 239 | 371.1 | 148.44 | 173.5178 | 213.8 | 221.2 | 215.5 | 219.8 | 462.1 | 26.1 | 21.4 | 49.6 | 2.9 | 191.7 | 3.8 | 540.4 | 814.8 | 815.6 | 480.5 | 661.9 | 270.1 | 521.3 | 778.9 | 436 | 623.2 | 21.1 | 58.7 | 75.1 | 36.9 | 228.7 | 211.5 | 48.7 | 127.8
392 | 240 | 370.8 | 148.32 | 173.3775 | 213.8 | 221 | 215.7 | 220.3 | 457.9 | 26.2 | 21.4 | 49.7 | 2.4 | 193 | 3.8 | 542 | 811.7 | 812.1 | 480.3 | 663.7 | 271.2 | 524.5 | 777.1 | 437.8 | 624 | 21.2 | 59 | 75.3 | 37 | 228.7 | 211.7 | 48.9 | 128.3
393 | 241 | 371 | 148.4 | 173.471 | 213.4 | 220.9 | 215.8 | 220.9 | 453 | 26.2 | 21.4 | 49.8 | 2.7 | 195.9 | 4 | 544.1 | 809 | 814.5 | 480.1 | 664.9 | 272.3 | 528.3 | 774.6 | 440.1 | 625.9 | 21.2 | 59.2 | 75.5 | 37.1 | 228.9 | 212.1 | 49.2 | 128.7
394 | 242 | 371 | 148.4 | 173.471 | 213 | 221 | 216.3 | 221.2 | 454.9 | 26.3 | 21.4 | 50 | 2.9 | 194.5 | 3.9 | 546.6 | 807.9 | 814 | 480 | 666.5 | 273.4 | 532.3 | 782.4 | 442.4 | 628.4 | 21.3 | 59.4 | 75.9 | 37.3 | 229 | 212.3 | 49.4 | 129.1
395 | 243 | 370.5 | 148.2 | 173.2373 | 212.7 | 221.4 | 216.7 | 221 | 454.4 | 26.3 | 21.4 | 50.1 | 2.6 | 194.4 | 3.7 | 549.6 | 810.2 | 807.1 | 480.2 | 667.2 | 274.5 | 533.8 | 783.2 | 444.3 | 630.6 | 21.3 | 59.7 | 76.4 | 37.4 | 229.1 | 212.8 | 49.6 | 129.5
396 | 244 | 370.9 | 148.36 | 173.4243 | 212.8 | 221.7 | 217.2 | 220.8 | 457 | 26.3 | 21.4 | 50.2 | 3 | 194 | 3.7 | 552.9 | 812.2 | 805.4 | 480.7 | 667.7 | 275.6 | 532.1 | 782 | 446.3 | 630.7 | 21.4 | 60 | 76.7 | 37.5 | 229.1 | 212.9 | 49.8 | 129.8
397 | 245 | 371.6 | 148.64 | 173.7516 | 212.7 | 222.1 | 217.4 | 220.7 | 454.4 | 26.3 | 21.4 | 50.3 | 2.7 | 194.5 | 3.7 | 555.7 | 813.2 | 799.9 | 481.2 | 667.6 | 276.7 | 529.7 | 775.3 | 447.5 | 630.2 | 21.4 | 60.2 | 76.9 | 37.7 | 229 | 213.2 | 50 | 130.3
398 | 246 | 370.7 | 148.28 | 173.3308 | 212.7 | 222.2 | 217.7 | 220.7 | 452.8 | 26.3 | 21.4 | 50.5 | 2.9 | 194.4 | 3.8 | 558.4 | 812.2 | 799.9 | 481.6 | 670 | 277.9 | 528.2 | 781.6 | 449.4 | 631.8 | 21.5 | 60.5 | 77.1 | 37.8 | 229 | 214 | 50.2 | 130.7
399 | 247 | 371.7 | 148.68 | 173.7984 | 211.5 | 222.9 | 217.6 | 220.2 | 451.5 | 26.4 | 21.4 | 50.6 | 2.6 | 189 | 4.1 | 561.1 | 813.5 | 798.8 | 482.2 | 669.2 | 279.2 | 524.4 | 779.6 | 451.1 | 632.4 | 21.5 | 60.7 | 77.3 | 38 | 229.2 | 214.7 | 50.4 | 131.3
400 | 248 | 371.1 | 148.44 | 173.5178 | 211.1 | 222.8 | 217.7 | 219.7 | 453.4 | 26.5 | 21.3 | 50.7 | 2.6 | 185.4 | 4.3 | 563.2 | 810.1 | 805.3 | 482.9 | 672.1 | 280.3 | 524.2 | 784.6 | 453.8 | 635.5 | 21.6 | 60.9 | 77.3 | 38.1 | 229 | 214.8 | 50.6 | 131.9
401 | 249 | 370.9 | 148.36 | 173.4243 | 210.9 | 222.6 | 218.1 | 219.6 | 456.4 | 26.5 | 21.3 | 50.8 | 2.7 | 185.6 | 4.5 | 566 | 812.5 | 814.7 | 484 | 674.6 | 281.3 | 528.9 | 784.5 | 456.6 | 637.8 | 21.6 | 61.1 | 77.7 | 38.3 | 229 | 214.7 | 50.8 | 132.1
402 | 250 | 371 | 148.4 | 173.471 | 210.5 | 222.1 | 218.2 | 219.7 | 451.8 | 26.6 | 21.3 | 50.9 | 2.9 | 186.2 | 4.7 | 568.2 | 808.7 | 816.5 | 485.2 | 676.9 | 282.3 | 531.4 | 786.6 | 459 | 639.1 | 21.7 | 61.4 | 78 | 38.4 | 229.1 | 214.7 | 51.1 | 132.5
403 | 251 | 371.1 | 148.44 | 173.5178 | 211 | 222.2 | 218.2 | 220 | 451.4 | 26.6 | 21.3 | 50.9 | 2.6 | 186.8 | 4.8 | 569.6 | 806.4 | 814.9 | 487 | 676.3 | 283.3 | 541.4 | 778.5 | 462.3 | 641.6 | 21.7 | 61.6 | 78.4 | 38.5 | 229.2 | 215.4 | 51.3 | 133
404 | 252 | 372.1 | 148.84 | 173.9854 | 211.6 | 222.5 | 218.6 | 220.2 | 445.4 | 26.7 | 21.3 | 50.9 | 3 | 187.5 | 4.6 | 570.6 | 805.1 | 813.9 | 488.5 | 679 | 284.3 | 553.5 | 770.4 | 465.1 | 645.1 | 21.8 | 61.8 | 78.6 | 38.7 | 229 | 216 | 51.5 | 133.4
405 | 253 | 371.3 | 148.52 | 173.6113 | 212 | 221.9 | 219.3 | 220.5 | 441.9 | 26.7 | 21.3 | 51 | 2.8 | 188.7 | 4.3 | 571.9 | 804 | 809.8 | 489.9 | 680.5 | 285.4 | 555.8 | 770.9 | 467 | 646 | 21.8 | 62 | 79 | 38.8 | 228.6 | 216.2 | 51.7 | 133.8
406 | 254 | 370.6 | 148.24 | 173.284 | 211.8 | 221.2 | 219.8 | 220.4 | 434 | 26.7 | 21.3 | 51 | 2.8 | 195.1 | 3.9 | 573.8 | 802.4 | 807.3 | 491 | 683 | 286.7 | 550.9 | 759.3 | 467.9 | 645.7 | 21.9 | 62.2 | 79.2 | 39 | 228.6 | 216 | 51.9 | 134.2
407 | 255 | 371.1 | 148.44 | 173.5178 | 210.9 | 221.4 | 220.7 | 219.8 | 433.8 | 26.7 | 21.3 | 51 | 2.7 | 200.7 | 3.6 | 574.7 | 800.8 | 811.7 | 492.1 | 685.4 | 288 | 547.2 | 756.9 | 469 | 646.5 | 21.9 | 62.4 | 79.3 | 39.1 | 229.1 | 215.9 | 52.1 | 134.6
408 | 256 | 370.7 | 148.28 | 173.3308 | 210.7 | 221.7 | 221.4 | 219.6 | 436.5 | 26.7 | 21.3 | 51.1 | 2.7 | 192.8 | 3.4 | 576.3 | 801 | 814.5 | 493.4 | 686.6 | 289.4 | 546.3 | 765 | 471.3 | 648.1 | 22 | 62.7 | 79.7 | 39.3 | 229.5 | 215.8 | 52.4 | 134.9
409 | 257 | 370.8 | 148.32 | 173.3775 | 211.9 | 222.1 | 222.1 | 219.7 | 446.8 | 26.7 | 21.3 | 51.1 | 2.5 | 181.5 | 3.3 | 577.2 | 800.4 | 807.3 | 494.8 | 687.4 | 290.9 | 541.5 | 766.1 | 472.5 | 647.8 | 22 | 62.8 | 80.1 | 39.4 | 229.5 | 215.8 | 52.6 | 135.3
410 | 258 | 370.7 | 148.28 | 173.3308 | 212.4 | 223.1 | 222.5 | 220.4 | 455.4 | 26.8 | 21.3 | 51.2 | 2.8 | 177.2 | 3.4 | 578 | 805 | 805.5 | 496.3 | 687.3 | 292.3 | 537.4 | 770.9 | 473.9 | 647.9 | 22.1 | 63 | 80.5 | 39.6 | 229.8 | 215.8 | 52.7 | 135.7
411 | 259 | 371.1 | 148.44 | 173.5178 | 213.2 | 223.7 | 222.3 | 221.4 | 460.1 | 26.9 | 21.3 | 51.3 | 2.7 | 175 | 3.3 | 577.7 | 805.9 | 801.4 | 498.1 | 687.4 | 293.7 | 533.6 | 771.1 | 475.4 | 647.2 | 22.1 | 63.2 | 81 | 39.7 | 230.2 | 216.5 | 52.8 | 136.1
412 | 260 | 371.5 | 148.6 | 173.7048 | 214.7 | 225.8 | 222.3 | 222.3 | 467.8 | 26.8 | 21.3 | 51.4 | 3.1 | 184.8 | 3.1 | 577.3 | 805.1 | 795.9 | 499.6 | 686.3 | 295.4 | 530 | 773.4 | 475.8 | 646.8 | 22.2 | 63.3 | 81.3 | 39.9 | 230.7 | 216.7 | 53.2 | 136.6
413 | 261 | 371.1 | 148.44 | 173.5178 | 216.2 | 228.1 | 222.8 | 223.2 | 470.7 | 26.8 | 21.3 | 51.5 | 2.8 | 191.9 | 3 | 578 | 796 | 787.7 | 495.8 | 686.7 | 296.9 | 527.1 | 769.6 | 476.5 | 646.4 | 22.3 | 63.4 | 81.6 | 40 | 231.3 | 216.7 | 53.5 | 137
414 | 262 | 370.7 | 148.28 | 173.3308 | 217.2 | 229.1 | 223 | 224.4 | 475.9 | 26.9 | 21.3 | 51.6 | 2.3 | 191.8 | 2.6 | 579.5 | 800.9 | 783.8 | 502.4 | 687.2 | 298.4 | 522.9 | 766.9 | 476.7 | 645.9 | 22.3 | 63.6 | 81.8 | 40.2 | 231.6 | 217.4 | 53.7 | 137.6
415 | 263 | 371.5 | 148.6 | 173.7048 | 217.4 | 229.7 | 222.7 | 225.2 | 490.3 | 27 | 21.3 | 51.6 | 2.4 | 191.4 | 2.4 | 580.9 | 796.7 | 780.5 | 502.8 | 686.5 | 299.7 | 517.4 | 772.2 | 476.9 | 644.7 | 22.4 | 63.8 | 82.1 | 40.3 | 232.3 | 217.1 | 53.9 | 137.9
416 | 264 | 371.6 | 148.64 | 173.7516 | 218.4 | 229.9 | 222.3 | 225.5 | 490.8 | 27.1 | 21.3 | 51.7 | 2.3 | 187.1 | 2.6 | 583 | 794.2 | 782.1 | 504.7 | 687.2 | 301.1 | 516.9 | 780.6 | 478.5 | 646.3 | 22.4 | 64 | 82.4 | 40.4 | 232.6 | 217.4 | 54.1 | 138.4
417 | 265 | 371.1 | 148.44 | 173.5178 | 219 | 230.5 | 221.9 | 225.8 | 489.3 | 27.2 | 21.3 | 51.8 | 2.6 | 178.2 | 3.1 | 585.3 | 729.3 | 781.3 | 473.7 | 686.4 | 302.5 | 516.3 | 781.9 | 479.7 | 645.8 | 22.5 | 64.2 | 82.8 | 40.6 | 233.4 | 217.2 | 54.3 | 138.8
418 | 266 | 369.7 | 147.88 | 172.8632 | 218.8 | 230.5 | 221.8 | 226 | 489.4 | 27.2 | 21.3 | 51.9 | 2.7 | 165.5 | 3.3 | 587 | 692.9 | 760.9 | 451.2 | 684 | 303.8 | 513.6 | 771 | 479.5 | 644.7 | 22.5 | 64.4 | 83.2 | 40.8 | 233.7 | 217.2 | 54.5 | 139.2
419 | 267 | 368.1 | 147.24 | 172.1151 | 219 | 232.3 | 222.1 | 226.6 | 494.3 | 27.3 | 21.3 | 52 | 2.6 | 165.4 | 3.3 | 588.8 | 779.1 | 743.5 | 494.3 | 681.6 | 305.1 | 511.2 | 759.7 | 478.6 | 643.5 | 22.6 | 64.6 | 83.8 | 40.9 | 234 | 217.4 | 54.7 | 139.5
420 | 268 | 371.7 | 148.68 | 173.7984 | 219.3 | 233.8 | 222.2 | 227.1 | 499.9 | 27.3 | 21.2 | 52.1 | 2.4 | 168.5 | 3.5 | 589 | 821.9 | 733.9 | 516.4 | 679.1 | 306.5 | 510 | 766.3 | 478.9 | 643.9 | 22.6 | 64.8 | 84.1 | 41 | 234.5 | 217.9 | 55 | 139.9
421 | 269 | 369.6 | 147.84 | 172.8164 | 220 | 234.7 | 222 | 227.2 | 493.6 | 27.3 | 21.3 | 52.1 | 2.5 | 173.9 | 3.4 | 588.5 | 822 | 738.8 | 519 | 679.4 | 307.9 | 509.9 | 760.5 | 479.3 | 644 | 22.7 | 65 | 84.3 | 41.2 | 234.9 | 218.3 | 55.2 | 140.4
422 | 270 | 369.7 | 147.88 | 172.8632 | 221 | 235.1 | 222.5 | 227.8 | 484 | 27.4 | 21.3 | 52.2 | 2.6 | 179.1 | 3.3 | 588 | 819.5 | 760 | 521.7 | 682.2 | 309.4 | 512.3 | 759.4 | 480.4 | 647.2 | 22.8 | 65.2 | 84.7 | 41.3 | 236.7 | 218 | 55.4 | 140.8
423 | 271 | 370.5 | 148.2 | 173.2373 | 221.6 | 235 | 223 | 228.3 | 477.1 | 27.4 | 21.2 | 52.3 | 2.8 | 189.3 | 3.7 | 586.3 | 814.1 | 774.7 | 524.2 | 686.2 | 311 | 514.8 | 772.5 | 482.5 | 649.2 | 22.8 | 65.4 | 84.6 | 41.5 | 236.8 | 218.7 | 55.6 | 141.1
424 | 272 | 370.8 | 148.32 | 173.3775 | 220.4 | 235 | 223.8 | 228.7 | 474.1 | 27.5 | 21.2 | 52.3 | 2.8 | 196.5 | 3.7 | 586 | 814.3 | 778.6 | 527 | 689.7 | 312.7 | 514.8 | 783 | 484.3 | 650.8 | 22.9 | 65.6 | 84.7 | 41.6 | 236.6 | 219.1 | 55.8 | 141.5
425 | 273 | 370.4 | 148.16 | 173.1905 | 220.9 | 234.3 | 224.6 | 228.5 | 472.3 | 27.6 | 21.2 | 52.4 | 3 | 195.8 | 3.5 | 586.2 | 817.1 | 774 | 530 | 688.9 | 314.3 | 512.3 | 783.5 | 485.4 | 651 | 22.9 | 65.8 | 85.2 | 41.8 | 236.5 | 219.2 | 56.1 | 142
426 | 274 | 371.9 | 148.76 | 173.8919 | 220.8 | 233.6 | 225.3 | 228.3 | 462.6 | 27.8 | 21.2 | 52.4 | 2.8 | 194.8 | 3.4 | 585.3 | 818.1 | 776.6 | 532.6 | 688 | 315.9 | 511.8 | 780.9 | 486.5 | 650.3 | 23 | 66 | 85.6 | 41.9 | 236.6 | 219.4 | 56.3 | 142.4
427 | 275 | 372.6 | 149.04 | 174.2192 | 220.8 | 232.5 | 226.2 | 228 | 456.1 | 27.9 | 21.2 | 52.5 | 2.7 | 195.6 | 3.3 | 585.1 | 818.3 | 776.9 | 535.9 | 688 | 317.6 | 512.3 | 781.8 | 488 | 650.4 | 23 | 66.2 | 85.7 | 42.1 | 236.8 | 219.7 | 56.5 | 142.8
428 | 276 | 372.4 | 148.96 | 174.1257 | 220.9 | 232.1 | 226.4 | 227.7 | 456.4 | 28 | 21.2 | 52.5 | 2.8 | 194.5 | 3.2 | 585.7 | 818.7 | 780 | 539 | 688.1 | 319.3 | 514 | 784.7 | 489.6 | 651.2 | 23.1 | 66.5 | 86 | 42.3 | 237 | 220.3 | 56.7 | 143.2
429 | 277 | 369.5 | 147.8 | 172.7697 | 220.6 | 232.2 | 226.7 | 227.2 | 460.3 | 28.1 | 21.2 | 52.6 | 2.9 | 190.2 | 3.3 | 585.3 | 814.7 | 780.1 | 541.9 | 689.7 | 321.1 | 515.6 | 773.7 | 490 | 652.1 | 23.2 | 66.7 | 86.2 | 42.4 | 237 | 220.2 | 56.9 | 143.6
430 | 278 | 368 | 147.2 | 172.0683 | 220.6 | 231.3 | 226.7 | 227 | 451.6 | 28.1 | 21.2 | 52.6 | 2.8 | 188.7 | 3.2 | 585.2 | 811.6 | 783.1 | 545.1 | 689.8 | 322.9 | 517.6 | 770.7 | 491.2 | 653.1 | 23.2 | 66.9 | 86.3 | 42.5 | 237.3 | 219.9 | 57.1 | 144
431 | 279 | 369.8 | 147.92 | 172.91 | 220.9 | 229.6 | 226.3 | 227.1 | 452 | 28.2 | 21.2 | 52.7 | 2.9 | 188 | 2.9 | 587 | 813.6 | 779.2 | 547.7 | 688.9 | 324.7 | 519.1 | 779.4 | 493.2 | 653.7 | 23.3 | 67.2 | 86.6 | 42.7 | 237.4 | 220 | 57.3 | 144.3
432 | 280 | 369.4 | 147.76 | 172.7229 | 221.7 | 229 | 226.4 | 226.9 | 456.8 | 28.2 | 21.2 | 52.8 | 3 | 187.5 | 2.5 | 590 | 818.9 | 766 | 550.9 | 685.5 | 326.6 | 515 | 776.1 | 494.4 | 653.1 | 23.3 | 67.4 | 87 | 42.8 | 237.4 | 220.4 | 57.5 | 144.7
433 | 281 | 370.7 | 148.28 | 173.3308 | 222.5 | 229.3 | 226.2 | 226.8 | 468.5 | 28.2 | 21.2 | 52.9 | 2.8 | 187.1 | 2.2 | 593 | 826 | 762.7 | 554.3 | 683.2 | 328.5 | 512.9 | 769 | 495.6 | 652.1 | 23.4 | 67.6 | 87.3 | 43 | 237 | 220.8 | 57.7 | 145.1
434 | 282 | 372.6 | 149.04 | 174.2192 | 223.9 | 230.1 | 226.8 | 227.3 | 479.7 | 28.2 | 21.2 | 53 | 2.8 | 189.9 | 2 | 595.2 | 825.7 | 775.1 | 557.5 | 684.8 | 330.5 | 511.1 | 761.8 | 497.5 | 652.2 | 23.5 | 67.9 | 87.7 | 43.1 | 237 | 221.1 | 58 | 145.3
435 | 283 | 371.7 | 148.68 | 173.7984 | 223.4 | 230.5 | 227.5 | 228.1 | 474.5 | 28.4 | 21.2 | 53.1 | 3 | 199.3 | 2 | 597 | 824.1 | 786.9 | 561 | 686.5 | 332.6 | 512.3 | 769.6 | 500 | 653.3 | 23.5 | 68.1 | 88.1 | 43.3 | 237.1 | 220.8 | 58.2 | 145.6
436 | 284 | 370.7 | 148.28 | 173.3308 | 223.1 | 229.6 | 228.1 | 228.9 | 485.5 | 28.5 | 21.2 | 53.1 | 2.5 | 202.2 | 2 | 598.3 | 822.5 | 788.1 | 563.9 | 687.9 | 334.8 | 514.7 | 783.9 | 503.3 | 655.7 | 23.6 | 68.4 | 88.4 | 43.5 | 237.6 | 220.9 | 58.4 | 145.9
437 | 285 | 370.2 | 148.08 | 173.097 | 222.6 | 228.6 | 228.3 | 229.4 | 494 | 28.6 | 21.2 | 53.2 | 2.7 | 192.4 | 2.1 | 599.4 | 824.7 | 779.8 | 566.4 | 685.8 | 337 | 516.2 | 779.4 | 505.3 | 655.5 | 23.6 | 68.7 | 88.9 | 43.6 | 238.1 | 221.2 | 58.6 | 146.4
438 | 286 | 371 | 148.4 | 173.471 | 222.6 | 228.4 | 227.9 | 230.3 | 495.3 | 28.7 | 21.2 | 53.3 | 2.4 | 187.1 | 2.1 | 600.8 | 823.6 | 781.2 | 569.3 | 686.8 | 339.3 | 512 | 776.7 | 505.6 | 654.9 | 23.7 | 68.9 | 89 | 43.8 | 238.4 | 221.2 | 58.8 | 146.8
439 | 287 | 370.8 | 148.32 | 173.3775 | 223 | 229.3 | 227.6 | 230.6 | 502.9 | 28.7 | 21.2 | 53.3 | 2.3 | 187.3 | 2.3 | 602.5 | 822.5 | 777 | 571.4 | 686 | 341.5 | 509.4 | 781.3 | 506.8 | 654.6 | 23.8 | 69.2 | 89.3 | 43.9 | 238.7 | 222.1 | 59.1 | 147.2
440 | 288 | 371.3 | 148.52 | 173.6113 | 223.9 | 228.7 | 228.1 | 231.2 | 505.9 | 28.7 | 21.2 | 53.4 | 2.5 | 187 | 2.3 | 604 | 822.8 | 755.4 | 573.8 | 682.2 | 343.8 | 509 | 777 | 507.2 | 652.6 | 23.8 | 69.5 | 89.8 | 44.1 | 239.2 | 222.9 | 59.3 | 147.6
441 | 289 | 371 | 148.4 | 173.471 | 225 | 229.2 | 229.6 | 231.9 | 507.4 | 28.8 | 21.2 | 53.4 | 2.7 | 190.9 | 2.5 | 606 | 825.1 | 740 | 576.4 | 679.8 | 346 | 506.7 | 772.3 | 508 | 651.1 | 23.9 | 69.7 | 90.3 | 44.2 | 239.9 | 222.8 | 59.5 | 148.1
442 | 290 | 371 | 148.4 | 173.471 | 225.7 | 231.8 | 230.8 | 232.8 | 510.8 | 28.9 | 21.2 | 53.5 | 2.7 | 202.9 | 2.8 | 608.2 | 827.2 | 726.2 | 579 | 676.1 | 348.2 | 502 | 764.1 | 508.5 | 649.5 | 23.9 | 70 | 90.9 | 44.4 | 241.2 | 222.7 | 59.7 | 148.6
443 | 291 | 370.8 | 148.32 | 173.3775 | 226.1 | 233.2 | 231.4 | 233.7 | 513.5 | 28.9 | 21.2 | 53.5 | 2.8 | 213 | 3 | 609.5 | 826.3 | 719.9 | 581.8 | 674.4 | 350.4 | 501.4 | 756.2 | 508.7 | 648.5 | 24 | 70.3 | 91.2 | 44.5 | 242 | 223.4 | 59.9 | 148.9
444 | 292 | 371.2 | 148.48 | 173.5646 | 226.9 | 233.6 | 232.2 | 234.7 | 504.9 | 29 | 21.2 | 53.6 | 2.6 | 215.9 | 3.3 | 610.8 | 821.2 | 735 | 584.3 | 674.2 | 352.7 | 500.7 | 759.5 | 509.3 | 648.2 | 24.1 | 70.6 | 91.4 | 44.7 | 242.9 | 224 | 60.2 | 149.4
445 | 293 | 368.6 | 147.44 | 172.3489 | 226.7 | 234.1 | 232.4 | 235.7 | 504.9 | 29 | 21.2 | 53.6 | 2.9 | 208.9 | 3.6 | 612.8 | 817.8 | 737.6 | 586.4 | 674.3 | 354.9 | 501.9 | 771.8 | 510.9 | 649.7 | 24.1 | 70.8 | 91.7 | 44.8 | 244.4 | 224.6 | 60.4 | 149.8
446 | 294 | 368 | 147.2 | 172.0683 | 227.4 | 234.9 | 232.3 | 236.5 | 504.1 | 29 | 21.1 | 53.7 | 2.8 | 202.4 | 4 | 613.4 | 817.8 | 734.6 | 589.1 | 672.4 | 357.2 | 501.7 | 767.3 | 512.1 | 648.4 | 24.2 | 71.1 | 91.9 | 45 | 245 | 224.8 | 60.6 | 150.2
447 | 295 | 369.5 | 147.8 | 172.7697 | 228.9 | 234.6 | 232.2 | 237 | 499.2 | 29.1 | 21.1 | 53.8 | 3.1 | 202.5 | 4.1 | 614 | 815.2 | 744.6 | 592.1 | 673.7 | 359.5 | 500.6 | 766.2 | 513.2 | 647.9 | 24.2 | 71.4 | 92.3 | 45.1 | 245.5 | 225.1 | 60.8 | 150.7
448 | 296 | 369.9 | 147.96 | 172.9567 | 229.7 | 234.6 | 232.5 | 237.3 | 497 | 29.2 | 21.2 | 53.9 | 2.6 | 200 | 3.9 | 615.8 | 811.8 | 752.9 | 595 | 673.7 | 361.8 | 499 | 773 | 514.4 | 647.9 | 24.3 | 71.6 | 92.3 | 45.3 | 245.9 | 225.3 | 61.1 | 151.1
449 | 297 | 370 | 148 | 173.0035 | 230.1 | 235.9 | 232.5 | 237.6 | 502.6 | 29.2 | 21.2 | 54 | 2.6 | 199 | 3.7 | 618.8 | 812.2 | 761.3 | 597.8 | 673.2 | 364.2 | 498.3 | 775.4 | 515.7 | 647.7 | 24.4 | 71.9 | 92.8 | 45.4 | 246 | 225.4 | 61.3 | 151.5
450 | 298 | 371.5 | 148.6 | 173.7048 | 230.5 | 236.3 | 232.6 | 237.8 | 507.4 | 29.3 | 21.2 | 54.1 | 2.7 | 200.1 | 3.5 | 622.1 | 812.1 | 767.2 | 599.5 | 672.9 | 366.6 | 497.5 | 776.1 | 516.7 | 648.3 | 24.4 | 72.2 | 93.3 | 45.6 | 246.2 | 225.5 | 61.5 | 151.9
451 | 299 | 372.1 | 148.84 | 173.9854 | 231.1 | 237.1 | 233 | 238.5 | 510.1 | 29.4 | 21.2 | 54.2 | 2.7 | 198.5 | 3.6 | 625.1 | 815.3 | 749.8 | 601.7 | 670.2 | 368.9 | 498.6 | 767 | 517.6 | 647.3 | 24.5 | 72.4 | 93.6 | 45.8 | 246.6 | 225.7 | 61.7 | 152.3
452 | 300 | 371.8 | 148.72 | 173.8451 | 231.3 | 237.2 | 233.4 | 239 | 520.6 | 29.5 | 21.2 | 54.4 | 2.8 | 198.2 | 3.6 | 627 | 817.2 | 732.9 | 604.8 | 667.4 | 371.1 | 497.4 | 760.6 | 517.7 | 646 | 24.6 | 72.7 | 93.7 | 45.9 | 247.1 | 226.3 | 61.9 | 152.7
453 | 301 | 369 | 147.6 | 172.5359 | 231.9 | 237.5 | 233.7 | 239.3 | 531.3 | 29.6 | 21.2 | 54.5 | 2.8 | 196.4 | 3.6 | 629.5 | 814 | 739.1 | 606.7 | 667.8 | 373.3 | 500.5 | 762.7 | 519 | 646.6 | 24.6 | 72.9 | 94.1 | 46.1 | 247.5 | 226.9 | 62.1 | 153.4
454 | 302 | 369.4 | 147.76 | 172.7229 | 232 | 237 | 234.4 | 239.8 | 526.2 | 29.8 | 21.2 | 54.6 | 2.8 | 193 | 3.4 | 631 | 812.8 | 743.6 | 609.2 | 668.8 | 375.6 | 502.3 | 765 | 519.9 | 646.7 | 24.7 | 73.1 | 94.4 | 46.2 | 247.9 | 227.5 | 62.4 | 153.8
455 | 303 | 370 | 148 | 173.0035 | 231.3 | 235.9 | 234.5 | 240.4 | 523.5 | 30 | 21.2 | 54.7 | 2.8 | 187.8 | 3 | 633.1 | 812 | 759 | 612.1 | 671.3 | 377.8 | 504.2 | 770.8 | 521.2 | 647.3 | 24.8 | 73.4 | 94.7 | 46.4 | 248.3 | 227.9 | 62.6 | 154.2
456 | 304 | 370.2 | 148.08 | 173.097 | 230.8 | 235.3 | 234.5 | 241 | 512.3 | 30 | 21.2 | 54.7 | 2.6 | 184.8 | 2.9 | 635.8 | 808.6 | 778.3 | 614.6 | 674.9 | 380 | 507.4 | 772.2 | 522.5 | 650.1 | 24.8 | 73.6 | 94.7 | 46.5 | 248.6 | 228.1 | 62.8 | 154.6
457 | 305 | 370 | 148 | 173.0035 | 230.7 | 235.3 | 234.7 | 241.2 | 503.7 | 29.9 | 21.1 | 54.8 | 2.7 | 195.1 | 3.1 | 637 | 807 | 773.9 | 616.6 | 676.4 | 382.3 | 508.4 | 758.5 | 523.2 | 650.2 | 24.9 | 73.9 | 94.9 | 46.7 | 249.1 | 228.7 | 63 | 155.1
458 | 306 | 370.9 | 148.36 | 173.4243 | 230.7 | 235.4 | 235.2 | 241.1 | 487.4 | 29.8 | 21.1 | 54.8 | 2.8 | 198.8 | 3.3 | 638.8 | 809.4 | 778.3 | 618.9 | 677.2 | 384.4 | 510 | 746.6 | 523.6 | 648.3 | 25 | 74.2 | 95.1 | 46.8 | 249.2 | 229.1 | 63.2 | 155.6
459 | 307 | 370.3 | 148.12 | 173.1437 | 230.2 | 235.2 | 235.6 | 241.3 | 483.3 | 29.8 | 21.1 | 54.9 | 2.8 | 206.9 | 3.3 | 641.8 | 807.3 | 784.4 | 621.7 | 679.6 | 386.5 | 514.8 | 750.9 | 524.7 | 650.5 | 25 | 74.5 | 95.4 | 47 | 249.3 | 229.4 | 63.5 | 156.1
460 | 308 | 370.1 | 148.04 | 173.0502 | 230.4 | 235.6 | 235.5 | 241.1 | 478.3 | 29.7 | 21.1 | 55 | 2.9 | 203.2 | 3.5 | 644.1 | 805.5 | 789.6 | 624.2 | 681.5 | 388.4 | 524.1 | 745.3 | 525.3 | 652.5 | 25.1 | 74.8 | 95.7 | 47.2 | 249.3 | 229.6 | 63.7 | 156.6
461 | 309 | 370.2 | 148.08 | 173.097 | 230.3 | 236.8 | 235.1 | 240.6 | 469.3 | 29.8 | 21.1 | 55.1 | 3.1 | 199.7 | 3.5 | 646 | 804.2 | 792.4 | 626.8 | 684.4 | 390.3 | 527.8 | 730.9 | 526.5 | 653.3 | 25.2 | 75.1 | 95.9 | 47.3 | 248.9 | 229.5 | 63.9 | 156.9
462 | 310 | 370.9 | 148.36 | 173.4243 | 229.9 | 237.3 | 234.3 | 239.7 | 465.9 | 29.8 | 21.1 | 55.2 | 3 | 195.4 | 3.2 | 647.7 | 802.1 | 790.8 | 629 | 687.6 | 392.2 | 534.3 | 738.5 | 528.3 | 656.2 | 25.2 | 75.4 | 96.2 | 47.5 | 248.7 | 229.3 | 64.1 | 157.2
463 | 311 | 371.1 | 148.44 | 173.5178 | 229.9 | 237.4 | 233.6 | 238.9 | 460.7 | 29.9 | 21.1 | 55.4 | 2.7 | 180.2 | 3.1 | 650.2 | 802.4 | 794.7 | 631.1 | 689.3 | 394.3 | 535.4 | 742.5 | 529.6 | 656.6 | 25.3 | 75.7 | 96.5 | 47.6 | 249.1 | 229.5 | 64.4 | 157.7
464 | 312 | 371.7 | 148.68 | 173.7984 | 228.9 | 237.3 | 233.6 | 238.6 | 454.3 | 30 | 21.1 | 55.5 | 2.9 | 179 | 3.4 | 652.8 | 800.4 | 801.6 | 633.6 | 692.9 | 396.6 | 534.8 | 747.5 | 530.9 | 658.7 | 25.4 | 76 | 96.7 | 47.8 | 249 | 229.2 | 64.6 | 158
465 | 313 | 371.2 | 148.48 | 173.5646 | 229.3 | 237.9 | 233.8 | 238.3 | 454 | 30 | 21.1 | 55.6 | 2.6 | 188.2 | 3.9 | 655.8 | 800.8 | 807.8 | 636.6 | 693.5 | 399 | 541.1 | 744.1 | 532.6 | 659.6 | 25.4 | 76.3 | 96.9 | 47.9 | 248.7 | 229.8 | 64.8 | 158.5
466 | 314 | 371.8 | 148.72 | 173.8451 | 228.7 | 236.8 | 234 | 238.1 | 453.5 | 30 | 21.1 | 55.8 | 2.9 | 185.1 | 4.4 | 658.8 | 800.7 | 813.3 | 639.1 | 697.3 | 401.4 | 543.8 | 749.9 | 534.8 | 661.2 | 25.5 | 76.6 | 97.1 | 48.1 | 248.1 | 229.7 | 65 | 158.8
467 | 315 | 371.7 | 148.68 | 173.7984 | 228.8 | 235.6 | 233.9 | 237.8 | 454.6 | 30.1 | 21.1 | 55.9 | 2.9 | 194.7 | 5.5 | 662 | 799.8 | 819.4 | 641.8 | 699.2 | 403.8 | 545.2 | 762.7 | 536.8 | 663.3 | 25.6 | 76.8 | 97.4 | 48.3 | 247.6 | 230 | 65.2 | 159.1
468 | 316 | 371.7 | 148.68 | 173.7984 | 228.7 | 234.9 | 233.5 | 237.4 | 456.3 | 30.1 | 21.1 | 56 | 2.7 | 191.8 | 6.1 | 663.8 | 799 | 813.9 | 643.7 | 700.6 | 406.2 | 549.1 | 761.4 | 538.3 | 665.7 | 25.6 | 77.1 | 97.7 | 48.4 | 247.1 | 230.1 | 65.4 | 159.5
469 | 317 | 371.6 | 148.64 | 173.7516 | 225.4 | 235.1 | 235.9 | 237.9 | 453.7 | 31 | 21.1 | 56.1 | 2.9 | 188.6 | 6.2 | 665.6 | 799.4 | 808.5 | 649.9 | 699.1 | 406.7 | 548 | 759.9 | 539.6 | 665 | 25.4 | 77.2 | 97.9 | 48.4 | 247.2 | 231.7 | 63.6 | 160.4
470 | 318 | 371.6 | 148.64 | 173.7516 | 228.9 | 233.7 | 234.1 | 236.5 | 458.3 | 30.4 | 21.1 | 56.1 | 2.8 | 197.9 | 5.9 | 668.5 | 800.5 | 811.7 | 648.7 | 700.9 | 411.2 | 546.1 | 763.3 | 541.6 | 666.8 | 25.8 | 77.7 | 98.2 | 48.7 | 246.2 | 230.1 | 65.9 | 160.1
471 | 319 | 372.3 | 148.92 | 174.0789 | 229.7 | 233.7 | 234.1 | 236 | 459.8 | 30.5 | 21.1 | 56.2 | 2.6 | 201.1 | 5.9 | 671.3 | 802.3 | 797.7 | 651.3 | 700.3 | 414.6 | 548.6 | 765.4 | 543.3 | 668 | 25.8 | 78 | 98.6 | 48.9 | 245.9 | 230.7 | 66.1 | 160.5
472 | 320 | 371.6 | 148.64 | 173.7516 | 230.2 | 232.7 | 233.8 | 235.4 | 465.2 | 30.5 | 21.1 | 56.3 | 3.3 | 192.5 | 5.9 | 675.4 | 807.3 | 791.2 | 654.9 | 699.3 | 419.1 | 552.7 | 763.1 | 545.2 | 668.7 | 25.9 | 78.3 | 99 | 49.1 | 245.2 | 231.2 | 66.3 | 160.9
473 | 321 | 371 | 148.4 | 173.471 | 230.4 | 231.9 | 233.3 | 234.9 | 466.4 | 30.6 | 21.1 | 56.4 | 3.3 | 185 | 5.5 | 678.2 | 806.2 | 799.7 | 658.1 | 701.6 | 424.4 | 556.9 | 756.4 | 547.2 | 669.8 | 26 | 78.5 | 99.2 | 49.2 | 245 | 231.6 | 66.5 | 161.2
474 | 322 | 371.1 | 148.44 | 173.5178 | 230.5 | 231.3 | 233.1 | 234.4 | 460.7 | 30.7 | 21.1 | 56.4 | 3.2 | 163.8 | 4.5 | 679.2 | 803.5 | 805.9 | 660.7 | 704.7 | 429.8 | 560 | 763.4 | 549 | 672.6 | 26 | 78.8 | 99.2 | 49.4 | 245 | 231.3 | 66.7 | 161.4
475 | 323 | 370.3 | 148.12 | 173.1437 | 231.4 | 231.1 | 233.2 | 234.1 | 464.9 | 30.8 | 21.1 | 56.5 | 2.7 | 170.6 | 3.9 | 682.6 | 805.1 | 809.7 | 663.9 | 706 | 435 | 558 | 773.2 | 550.5 | 673.2 | 26.1 | 79.1 | 99.4 | 49.5 | 245 | 231.1 | 67 | 161.7
476 | 324 | 372.5 | 149 | 174.1724 | 231.5 | 231.2 | 233.8 | 233.8 | 470.9 | 30.8 | 21.1 | 56.5 | 2.7 | 196.4 | 4 | 685.7 | 804.1 | 805.2 | 666.7 | 706.6 | 439.9 | 557.9 | 772.7 | 552 | 671.6 | 26.2 | 79.3 | 99.7 | 49.7 | 245.1 | 230.9 | 67.2 | 162
477 | 325 | 370.5 | 148.2 | 173.2373 | 232.9 | 232.1 | 234.3 | 233.5 | 472.6 | 30.8 | 21.1 | 56.6 | 2.5 | 185.6 | 4.9 | 687.3 | 804.6 | 787.8 | 669.5 | 703.7 | 444.8 | 556 | 764.5 | 553 | 670.6 | 26.3 | 79.6 | 100.1 | 49.9 | 245.3 | 231.3 | 67.4 | 162.4
478 | 326 | 372.2 | 148.88 | 174.0321 | 233.8 | 232.7 | 234.6 | 233.4 | 472.5 | 30.9 | 21.1 | 56.6 | 2.9 | 171.9 | 5.4 | 689.4 | 806.4 | 785 | 673.3 | 701.9 | 449.4 | 552.5 | 761.2 | 554 | 669.9 | 26.3 | 79.8 | 100.3 | 50 | 245.5 | 231.4 | 67.6 | 162.7
479 | 327 | 372.2 | 148.88 | 174.0321 | 234.5 | 233.5 | 234.4 | 233.3 | 475 | 31 | 21.1 | 56.7 | 2.9 | 199.8 | 5.2 | 690.7 | 806.1 | 780.9 | 676.5 | 701.4 | 453.9 | 552.1 | 760.6 | 555 | 671.5 | 26.4 | 80.1 | 100.4 | 50.2 | 245.7 | 231.6 | 67.9 | 163.1
480 | 328 | 370.4 | 148.16 | 173.1905 | 235 | 234.7 | 234.2 | 233.5 | 469.4 | 31 | 21 | 56.8 | 3.1 | 191.2 | 5.2 | 690.2 | 806.7 | 771.2 | 679.1 | 701.1 | 458.1 | 561.8 | 731.3 | 556.3 | 671.8 | 26.5 | 80.3 | 100.7 | 50.3 | 245.8 | 231.6 | 68.1 | 163.6
481 | 329 | 371.1 | 148.44 | 173.5178 | 235.3 | 235 | 234.5 | 233.8 | 461.9 | 31.1 | 21 | 56.9 | 2.7 | 182.2 | 5.4 | 690.9 | 804 | 772 | 681.2 | 701 | 462.1 | 566.6 | 722.8 | 558.3 | 669.9 | 26.6 | 80.6 | 100.9 | 50.5 | 245.8 | 231.8 | 68.3 | 163.9
482 | 330 | 369.7 | 147.88 | 172.8632 | 236 | 234.9 | 235 | 233.9 | 464.8 | 31.1 | 21 | 56.9 | 3.1 | 184 | 5.9 | 691.9 | 806.1 | 762.9 | 683.7 | 699.1 | 466.1 | 569 | 711.2 | 560.1 | 669.9 | 26.6 | 80.8 | 101.2 | 50.7 | 245.6 | 232.3 | 68.5 | 164.3
483 | 331 | 371.7 | 148.68 | 173.7984 | 236.6 | 235.1 | 235.6 | 233.7 | 463.2 | 31.2 | 21 | 57 | 3 | 179.5 | 6.5 | 692.9 | 807.8 | 757.1 | 686.3 | 698.1 | 470.1 | 571.9 | 709.4 | 562.3 | 669.9 | 26.7 | 81 | 101.6 | 50.8 | 245.6 | 232.1 | 68.7 | 164.6
484 | 332 | 371.2 | 148.48 | 173.5646 | 237.4 | 234.8 | 236.3 | 233.4 | 461 | 31.3 | 21 | 57.1 | 3.1 | 172.2 | 6.8 | 693.8 | 809.9 | 743.4 | 689.6 | 695.3 | 474.1 | 573.5 | 690.9 | 564 | 668.9 | 26.8 | 81.2 | 101.9 | 51 | 245.6 | 232.1 | 69 | 164.8
485 | 333 | 371.2 | 148.48 | 173.5646 | 238.6 | 233.4 | 237.4 | 233.4 | 450.9 | 31.3 | 21 | 57.2 | 3 | 174.3 | 6.4 | 694.5 | 811.5 | 726 | 693.1 | 691.9 | 478.3 | 568 | 681.3 | 565.3 | 666 | 26.8 | 81.4 | 101.9 | 51.1 | 245.9 | 232.5 | 69.2 | 165.2
486 | 334 | 371.5 | 148.6 | 173.7048 | 240.1 | 232.5 | 238.6 | 233.5 | 443.9 | 31.3 | 21 | 57.3 | 3.1 | 181.8 | 5.7 | 696.1 | 809.2 | 715.3 | 696.5 | 690.8 | 482.5 | 561.7 | 678.4 | 566.3 | 664.4 | 26.9 | 81.6 | 102.2 | 51.3 | 246 | 232.4 | 69.4 | 165.7
487 | 335 | 370 | 148 | 173.0035 | 240.7 | 230.8 | 239.5 | 233.6 | 439.6 | 31.4 | 21 | 57.4 | 3.2 | 210.1 | 5 | 698.1 | 808 | 707.6 | 699.3 | 687.4 | 486.5 | 556.6 | 689.5 | 566.7 | 664.5 | 27 | 81.8 | 102.4 | 51.5 | 246.1 | 232.4 | 69.6 | 165.9
488 | 336 | 371.3 | 148.52 | 173.6113 | 240 | 230 | 240.6 | 234.2 | 436.8 | 31.8 | 21 | 57.5 | 3 | 201.7 | 3.8 | 699.9 | 808.6 | 692.5 | 702.5 | 685 | 489.8 | 561.4 | 673.9 | 567.2 | 663.1 | 27 | 81.9 | 102.6 | 51.6 | 246.8 | 233 | 69.2 | 166.3
489 | 337 | 371.9 | 148.76 | 173.8919 | 240.5 | 229.3 | 240.8 | 234.2 | 436.6 | 31.7 | 21 | 57.6 | 2.9 | 161.9 | 3.2 | 701.4 | 805.9 | 690.2 | 703.1 | 683.7 | 493.8 | 566.1 | 678.8 | 567.9 | 662.9 | 27.1 | 82.2 | 103 | 51.7 | 247.1 | 232.7 | 69.8 | 166.6
490 | 338 | 370.2 | 148.08 | 173.097 | 240.8 | 228.7 | 241.1 | 233.8 | 440.2 | 31.6 | 21 | 57.7 | 2.8 | 159.8 | 2.7 | 704 | 805.6 | 692.5 | 705 | 682.3 | 497.7 | 570.1 | 702 | 568.7 | 663.8 | 27.2 | 82.5 | 103.4 | 52 | 247.4 | 232.7 | 70.3 | 166.9
491 | 339 | 371.6 | 148.64 | 173.7516 | 240.9 | 228.4 | 241 | 233.5 | 454.9 | 31.6 | 21 | 57.8 | 2.6 | 198.8 | 2.7 | 707 | 808 | 692.2 | 708.4 | 679.7 | 501.2 | 569.5 | 715.7 | 569.3 | 663.9 | 27.3 | 82.7 | 103.9 | 52.1 | 247.8 | 232.6 | 70.5 | 167.3
492 | 340 | 371.2 | 148.48 | 173.5646 | 241.6 | 228.6 | 240.9 | 233.7 | 463.5 | 31.7 | 21 | 57.9 | 2.5 | 221.5 | 2.8 | 709.6 | 809.3 | 695.1 | 712.1 | 677.4 | 504.7 | 569.8 | 722.3 | 569.8 | 662.6 | 27.3 | 82.9 | 104.4 | 52.3 | 248.2 | 232.7 | 70.7 | 167.6
493 | 341 | 371.1 | 148.44 | 173.5178 | 242.3 | 229.7 | 241.1 | 234.3 | 472.5 | 31.8 | 21 | 57.9 | 2.4 | 209.9 | 3 | 711.4 | 808.9 | 697.9 | 714.4 | 676.7 | 508.1 | 568.6 | 735.1 | 570.3 | 663.3 | 27.4 | 83.2 | 104.8 | 52.4 | 248.4 | 232.7 | 71 | 167.9
494 | 342 | 371.4 | 148.56 | 173.6581 | 243 | 231.1 | 241.8 | 234.9 | 472.6 | 31.9 | 21 | 57.9 | 2.7 | 201.5 | 3.5 | 712.1 | 808 | 690.8 | 716 | 674.2 | 511.7 | 567.1 | 720.7 | 571 | 661.9 | 27.5 | 83.4 | 104.8 | 52.6 | 248.7 | 232.9 | 71.2 | 168.2
495 | 343 | 371.4 | 148.56 | 173.6581 | 243.8 | 231.4 | 242.1 | 235.4 | 464.1 | 32 | 20.9 | 57.9 | 2.8 | 192.2 | 3.7 | 713.6 | 805.8 | 700.6 | 717.2 | 674.2 | 515.5 | 566.4 | 720.6 | 571.9 | 662.9 | 27.6 | 83.6 | 104.8 | 52.8 | 249.1 | 233.2 | 71.4 | 168.5
496 | 344 | 369.5 | 147.8 | 172.7697 | 244 | 231.7 | 242.3 | 235.9 | 462.3 | 32 | 21 | 57.9 | 2.7 | 185.7 | 3.6 | 715.1 | 805.1 | 709.7 | 718.1 | 674.4 | 519.6 | 565.8 | 733.8 | 573.2 | 663.7 | 27.6 | 83.9 | 104.9 | 52.9 | 249.4 | 233.2 | 71.6 | 168.9
497 | 345 | 369.1 | 147.64 | 172.5827 | 244.3 | 231 | 242.3 | 236.6 | 462 | 32.1 | 21 | 57.9 | 2.6 | 183.8 | 3.4 | 716.3 | 803.3 | 706.7 | 719.3 | 672.8 | 524 | 567.5 | 729.1 | 574.4 | 664 | 27.7 | 84.1 | 105.3 | 53.1 | 249.8 | 232.9 | 71.8 | 169.2
498 | 346 | 370.9 | 148.36 | 173.4243 | 243.5 | 229.9 | 242.6 | 237 | 454.3 | 32.2 | 21 | 58 | 2.7 | 191.5 | 3.1 | 717.8 | 802.6 | 708.4 | 721.8 | 670.4 | 528.3 | 567 | 716.2 | 574.3 | 663 | 27.8 | 84.3 | 105.6 | 53.2 | 250.2 | 233.1 | 72.1 | 169.5
499 | 347 | 370.7 | 148.28 | 173.3308 | 243.1 | 228.7 | 242.8 | 237.2 | 450.4 | 32.2 | 21 | 58 | 2.7 | 201.5 | 3.1 | 719.6 | 801.7 | 712.6 | 724.2 | 671.4 | 533 | 564.7 | 700.9 | 574.5 | 662.6 | 27.9 | 84.6 | 105.8 | 53.4 | 250.5 | 233.9 | 72.3 | 169.9
500 | 348 | 370.5 | 148.2 | 173.2373 | 243.2 | 227.3 | 242.7 | 237.3 | 444.3 | 32.2 | 20.9 | 58 | 2.9 | 209.2 | 3.2 | 720.5 | 803.4 | 694.4 | 726.1 | 667.6 | 537.9 | 561.5 | 684.7 | 574.5 | 660.6 | 27.9 | 84.8 | 106.1 | 53.6 | 250.6 | 234.2 | 72.5 | 170.1
501 | 349 | 371.3 | 148.52 | 173.6113 | 243.6 | 226.5 | 243.2 | 237.3 | 433.3 | 32.1 | 20.9 | 58.1 | 3.1 | 216.5 | 3.1 | 721.7 | 805 | 682.7 | 728.4 | 664.3 | 543.2 | 554.2 | 669 | 574.9 | 657.2 | 28 | 85 | 106.3 | 53.7 | 250.5 | 234.2 | 72.7 | 170.6
502 | 350 | 371.7 | 148.68 | 173.7984 | 244.9 | 225.5 | 243.9 | 237 | 431 | 32.1 | 20.9 | 58.1 | 2.8 | 209.1 | 2.9 | 723.5 | 805.2 | 679.1 | 730.3 | 662.8 | 548.6 | 548.5 | 671.2 | 575 | 655.6 | 28.1 | 85.2 | 106.6 | 53.9 | 250.7 | 234.4 | 73 | 170.9
503 | 351 | 371.8 | 148.72 | 173.8451 | 245.3 | 224.3 | 244.6 | 236.8 | 428 | 32.1 | 20.9 | 58.1 | 2.8 | 181.7 | 3.2 | 725.6 | 803 | 680.8 | 731.9 | 660.9 | 553.9 | 545 | 668.2 | 575.2 | 654.3 | 28.2 | 85.4 | 106.9 | 54 | 250.9 | 234.5 | 73.2 | 171.2
504 | 352 | 371.1 | 148.44 | 173.5178 | 246 | 223.4 | 244.9 | 236.7 | 425.6 | 32 | 20.9 | 58.1 | 2.9 | 178 | 3.3 | 727.1 | 802.4 | 702.2 | 734.1 | 660.6 | 559.1 | 543 | 662.8 | 575.5 | 653.3 | 28.2 | 85.7 | 106.9 | 54.2 | 251 | 234.3 | 73.4 | 171.5
505 | 353 | 370.8 | 148.32 | 173.3775 | 246.6 | 222.2 | 244.9 | 236.6 | 420.3 | 32 | 20.9 | 58.2 | 3.2 | 184.3 | 3.5 | 728.4 | 797.3 | 724.6 | 736.6 | 662.6 | 564.5 | 546.8 | 669.3 | 576.2 | 654.7 | 28.3 | 85.9 | 107.1 | 54.4 | 251.8 | 234.4 | 73.6 | 171.9
506 | 354 | 370.5 | 148.2 | 173.2373 | 246.8 | 221.7 | 244.7 | 236.8 | 416.2 | 32.2 | 20.9 | 58.3 | 2.9 | 191.8 | 3.9 | 730.3 | 793.4 | 739.1 | 738.9 | 664.9 | 569.7 | 549.1 | 684.1 | 577.2 | 658.5 | 28.4 | 86.1 | 107.5 | 54.5 | 252.6 | 235.2 | 73.8 | 172.3
507 | 355 | 371.3 | 148.52 | 173.6113 | 246.1 | 221.5 | 244.5 | 236.9 | 423.1 | 32.2 | 20.9 | 58.4 | 2.8 | 193.9 | 4.2 | 732.7 | 793.9 | 740.5 | 741.5 | 664.5 | 575 | 550 | 702.7 | 578.2 | 658.6 | 28.5 | 86.3 | 107.9 | 54.7 | 252.3 | 236.3 | 74 | 172.9
508 | 356 | 370.3 | 148.12 | 173.1437 | 245.4 | 222.1 | 244.7 | 236.8 | 427.4 | 32.2 | 20.9 | 58.4 | 3 | 195.8 | 4.2 | 735 | 794.1 | 746.6 | 744.8 | 667.4 | 580.3 | 548.7 | 714.9 | 578.7 | 658.2 | 28.5 | 86.5 | 108.1 | 54.8 | 252.1 | 236.9 | 74.2 | 173.3
509 | 357 | 371.8 | 148.72 | 173.8451 | 245.3 | 223.4 | 244.7 | 237.1 | 424.3 | 32.2 | 20.9 | 58.5 | 3.3 | 197.4 | 4.2 | 735.8 | 793.3 | 735.6 | 747.8 | 665.5 | 585.4 | 553.1 | 701.7 | 578.5 | 659.4 | 28.6 | 86.7 | 108.3 | 55 | 252.4 | 237.4 | 74.4 | 173.6
510 | 358 | 371.2 | 148.48 | 173.5646 | 245.2 | 223.7 | 244.7 | 237.4 | 423.2 | 32.2 | 20.9 | 58.5 | 3.1 | 197.7 | 4.1 | 736.9 | 793.6 | 735.2 | 750.1 | 665.6 | 590.1 | 551.2 | 692.9 | 578.6 | 658.1 | 28.7 | 87 | 108.4 | 55.2 | 251.9 | 238 | 74.7 | 174.1
511 | 359 | 371.1 | 148.44 | 173.5178 | 245.8 | 224.2 | 245.2 | 237.8 | 425.4 | 32.3 | 20.9 | 58.6 | 3 | 201.6 | 4.2 | 738.3 | 792.9 | 736.3 | 751.4 | 666.3 | 595.3 | 549.3 | 686.9 | 578.7 | 658.1 | 28.8 | 87.2 | 108.7 | 55.3 | 252.5 | 238.2 | 74.9 | 174.4
512 | 360 | 370.1 | 148.04 | 173.0502 | 245.8 | 224.1 | 245.8 | 237.8 | 423 | 32.4 | 20.9 | 58.8 | 3 | 202.9 | 4 | 740.9 | 795 | 733.5 | 752.6 | 666.4 | 601 | 550.7 | 692.2 | 579.3 | 658.6 | 28.9 | 87.4 | 108.9 | 55.5 | 252.6 | 238.1 | 75.1 | 174.8
513 | 361 | 368.6 | 147.44 | 172.3489 | 246.1 | 223.6 | 245.8 | 237.2 | 423.4 | 32.4 | 20.9 | 58.9 | 2.9 | 205.3 | 3.9 | 741.6 | 794.1 | 719.6 | 754 | 664.3 | 606.4 | 553.2 | 677.7 | 579.5 | 658.2 | 28.9 | 87.7 | 109.2 | 55.6 | 253.4 | 238.4 | 75.3 | 175.1
514 | 362 | 370.5 | 148.2 | 173.2373 | 246.3 | 223.2 | 245.7 | 236.7 | 419.8 | 32.4 | 20.9 | 58.9 | 2.8 | 193.5 | 4.2 | 742.1 | 794.9 | 703 | 755.9 | 661.2 | 611.5 | 552.8 | 663.9 | 579.9 | 656.4 | 29 | 87.9 | 109.4 | 55.8 | 253.2 | 238.3 | 75.5 | 175.4
515 | 363 | 368.8 | 147.52 | 172.4424 | 246.4 | 223.5 | 245.5 | 236.8 | 412.4 | 32.5 | 20.9 | 59.1 | 2.6 | 182.9 | 5.4 | 743.3 | 794.3 | 691 | 756.5 | 660.7 | 617.2 | 552.5 | 659.3 | 580.8 | 654.8 | 29.1 | 88.1 | 109.7 | 56 | 253 | 238.1 | 75.7 | 175.7
516 | 364 | 367.1 | 146.84 | 171.6475 | 247 | 223.2 | 245.5 | 237.1 | 415 | 32.5 | 20.9 | 59.2 | 2.9 | 186.1 | 6.3 | 745.5 | 794.4 | 692.2 | 758.7 | 661 | 623.6 | 560.9 | 665.8 | 582.3 | 655.4 | 29.2 | 88.3 | 109.8 | 56.1 | 252.7 | 238 | 76 | 175.8
517 | 365 | 368 | 147.2 | 172.0683 | 247.4 | 223 | 245.9 | 236.8 | 415.7 | 32.5 | 20.9 | 59.3 | 2.6 | 171.7 | 6.4 | 748.1 | 794.4 | 693.4 | 760.4 | 659.5 | 629.6 | 557.4 | 665 | 583.6 | 655.3 | 29.3 | 88.5 | 110.3 | 56.3 | 252.8 | 237.8 | 76.2 | 176
518 | 366 | 368.6 | 147.44 | 172.3489 | 247.6 | 223.2 | 245.7 | 236.5 | 414.6 | 32.5 | 20.9 | 59.3 | 2.7 | 197.5 | 6.3 | 749.8 | 792.9 | 692.2 | 761 | 658.5 | 635.2 | 563.2 | 656.9 | 584.7 | 656.2 | 29.3 | 88.7 | 110.6 | 56.5 | 253.2 | 237.6 | 76.4 | 176.3
519 | 367 | 368.7 | 147.48 | 172.3956 | 247.6 | 223.4 | 245.8 | 236.7 | 412.2 | 32.5 | 20.9 | 59.4 | 2.7 | 208.9 | 6.4 | 750.2 | 793 | 672.7 | 762.9 | 654.2 | 640.2 | 558 | 641 | 585.7 | 653.3 | 29.4 | 88.8 | 110.8 | 56.6 | 253.5 | 237.8 | 76.5 | 176.7
520 | 368 | 371.8 | 148.72 | 173.8451 | 249 | 223.4 | 246.4 | 236.7 | 408.1 | 32.4 | 20.9 | 59.4 | 2.6 | 200.7 | 6.1 | 751 | 793.4 | 658.1 | 764 | 651.5 | 646 | 554.1 | 626.2 | 587.2 | 649.8 | 29.5 | 89 | 111.1 | 56.8 | 253.4 | 237.8 | 76.8 | 177.1
521 | 369 | 372.6 | 149.04 | 174.2192 | 250.2 | 223 | 247 | 236.3 | 403.2 | 32.4 | 20.9 | 59.5 | 2.7 | 217.1 | 6.2 | 752.4 | 792.2 | 645.3 | 764.2 | 650.3 | 652.2 | 550 | 615.4 | 588.5 | 648.2 | 29.6 | 89.1 | 111.3 | 57 | 254.6 | 237.8 | 77 | 177.4
522 | 370 | 372.6 | 149.04 | 174.2192 | 251.3 | 222.2 | 247.6 | 236.1 | 402.1 | 32.5 | 20.9 | 59.5 | 2.6 | 212 | 6.2 | 754.3 | 792.6 | 642.6 | 765.8 | 649.3 | 657.8 | 548.2 | 610.4 | 589.4 | 647.6 | 29.6 | 89.3 | 111.4 | 57.1 | 254.9 | 238 | 77.3 | 177.8
523 | 371 | 372.5 | 149 | 174.1724 | 251.9 | 221.5 | 248.2 | 236.1 | 403.4 | 32.5 | 20.9 | 59.5 | 2.8 | 203.9 | 6.1 | 756.4 | 789.7 | 652.3 | 766.1 | 651.4 | 663 | 546.4 | 620.9 | 590.5 | 647 | 29.7 | 89.5 | 111.6 | 57.3 | 254.6 | 238.5 | 77.5 | 178.2
524 | 372 | 372.6 | 149.04 | 174.2192 | 252.3 | 220.9 | 248.7 | 236.2 | 407.7 | 32.6 | 20.9 | 59.5 | 3.2 | 205.5 | 5.9 | 757.3 | 789.1 | 651.4 | 768.4 | 649.9 | 667.1 | 546.7 | 626.4 | 590.9 | 647.6 | 29.8 | 89.7 | 111.8 | 57.4 | 254.7 | 239 | 77.7 | 178.5
525 | 373 | 369.3 | 147.72 | 172.6762 | 252 | 221 | 249.8 | 236.3 | 408.2 | 32.9 | 20.9 | 59.5 | 2.9 | 218.2 | 5.4 | 759.3 | 789.1 | 670.9 | 772.4 | 650.2 | 671.4 | 550.9 | 639 | 591.9 | 648.2 | 29.8 | 89.8 | 111.9 | 57.5 | 255.3 | 239.8 | 77.2 | 178.9
526 | 374 | 370 | 148 | 173.0035 | 252.6 | 221 | 249.8 | 236.2 | 417.8 | 32.8 | 20.9 | 59.5 | 3 | 184 | 5.2 | 763.6 | 786.5 | 697.8 | 771.7 | 656.5 | 676.6 | 552 | 674.2 | 592.6 | 651.3 | 30 | 90.1 | 112.4 | 57.8 | 254.9 | 239.5 | 78.1 | 179.2
527 | 375 | 369.4 | 147.76 | 172.7229 | 252.7 | 221.5 | 250.6 | 236 | 424 | 32.9 | 20.9 | 59.5 | 2.7 | 181.5 | 5.6 | 766.4 | 783.6 | 713 | 773.4 | 656.9 | 679.4 | 553.4 | 697.3 | 592.9 | 654 | 30 | 90.4 | 112.7 | 57.9 | 255.8 | 239.8 | 78.3 | 179.5
528 | 376 | 369.9 | 147.96 | 172.9567 | 252.2 | 223.1 | 250.7 | 235.9 | 431.5 | 33 | 20.8 | 59.5 | 3.1 | 188.9 | 5.9 | 768.8 | 781 | 727.4 | 776.2 | 659.6 | 680.5 | 560.6 | 721.6 | 593.1 | 657.7 | 30.1 | 90.6 | 113 | 58.1 | 256 | 239.8 | 78.6 | 179.8
529 | 377 | 370.4 | 148.16 | 173.1905 | 250.1 | 224.8 | 251 | 236.2 | 435.9 | 33 | 20.8 | 59.6 | 3 | 189.6 | 6.1 | 770.6 | 779.6 | 740.2 | 779.4 | 663.5 | 681.1 | 563.5 | 738.9 | 594 | 661.7 | 30.2 | 90.9 | 113.3 | 58.3 | 256 | 240.3 | 78.8 | 180.2
530 | 378 | 369.7 | 147.88 | 172.8632 | 249.5 | 225.7 | 250.9 | 236.5 | 436.9 | 33 | 20.8 | 59.6 | 3.1 | 190.7 | 6.6 | 771.8 | 779.1 | 745.8 | 781.8 | 665.4 | 682 | 565.5 | 743.3 | 595 | 663.1 | 30.3 | 91.1 | 113.6 | 58.4 | 255.9 | 240.3 | 79 | 180.5
531 | 379 | 369.6 | 147.84 | 172.8164 | 249.7 | 226.3 | 250.7 | 236.7 | 434.1 | 33 | 20.8 | 59.6 | 2.7 | 190.7 | 6.6 | 771.9 | 776.4 | 742.4 | 783.4 | 666.5 | 684.2 | 570.4 | 726.4 | 596.5 | 663.8 | 30.4 | 91.4 | 113.6 | 58.6 | 256 | 240.2 | 79.2 | 180.8
532 | 380 | 370.1 | 148.04 | 173.0502 | 250.1 | 227.1 | 250.1 | 236.9 | 428.3 | 33.1 | 20.8 | 59.7 | 2.4 | 189.3 | 6.9 | 771.9 | 775.4 | 737.3 | 784.5 | 668.7 | 687.8 | 572.7 | 719.4 | 597.5 | 664.8 | 30.5 | 91.6 | 113.9 | 58.8 | 255.9 | 240.6 | 79.4 | 181.1
533 | 381 | 371.6 | 148.64 | 173.7516 | 250.4 | 228 | 250.1 | 237.4 | 429 | 33.1 | 20.8 | 59.7 | 2.6 | 187.8 | 7.5 | 772.1 | 775.3 | 734.7 | 786.1 | 668.8 | 690.6 | 576.1 | 709 | 598.4 | 666.2 | 30.5 | 91.8 | 114.2 | 58.9 | 255.9 | 241.1 | 79.6 | 181.5
534 | 382 | 371.4 | 148.56 | 173.6581 | 248.6 | 228.4 | 250.4 | 237.4 | 426.7 | 33.1 | 20.8 | 59.8 | 3.1 | 184.4 | 7.8 | 771.9 | 775.2 | 733.6 | 787.3 | 668.2 | 694.1 | 577.1 | 696.7 | 600.2 | 664.5 | 30.6 | 92.1 | 114.3 | 59.1 | 256 | 241.2 | 79.8 | 181.9
535 | 383 | 370.6 | 148.24 | 173.284 | 247.5 | 228.8 | 250.7 | 237.6 | 428.7 | 33.1 | 20.8 | 59.8 | 2.7 | 189.1 | 7.1 | 772.6 | 773.8 | 735.2 | 788.2 | 669.9 | 697.6 | 577.6 | 701.8 | 601.7 | 665.5 | 30.7 | 92.3 | 114.7 | 59.2 | 255.9 | 241 | 80.1 | 182.2
536 | 384 | 369.8 | 147.92 | 172.91 | 246.8 | 229 | 250.7 | 237.7 | 428.9 | 33.1 | 20.8 | 59.9 | 2.8 | 192.8 | 6.4 | 774.5 | 773.9 | 738.9 | 790.1 | 671.8 | 700.1 | 576.6 | 703.1 | 602.6 | 666.4 | 30.8 | 92.5 | 114.9 | 59.4 | 255.9 | 241.3 | 80.3 | 182.4
537 | 385 | 370.4 | 148.16 | 173.1905 | 245.7 | 228.8 | 250.6 | 238 | 431.2 | 33.1 | 20.8 | 59.9 | 2.7 | 190.4 | 6.7 | 776.5 | 776.2 | 739 | 793 | 671.3 | 702.2 | 573.8 | 716.7 | 604 | 666.7 | 30.9 | 92.8 | 115.2 | 59.6 | 256 | 241.4 | 80.5 | 182.7
538 | 386 | 370 | 148 | 173.0035 | 245.1 | 228.6 | 250.3 | 238.2 | 441.3 | 33.1 | 20.8 | 59.9 | 3 | 188.6 | 9 | 780.1 | 778.6 | 744 | 796.4 | 673.2 | 704.1 | 579 | 747.6 | 605.2 | 668.2 | 30.9 | 93 | 115.6 | 59.8 | 256.2 | 241.6 | 80.7 | 182.9
539 | 387 | 371 | 148.4 | 173.471 | 243.8 | 227.6 | 250 | 238.5 | 457.7 | 33.1 | 20.8 | 59.9 | 3 | 185.2 | 10.1 | 782.9 | 778 | 751.7 | 798.2 | 676.8 | 705.3 | 580.4 | 771.9 | 606.4 | 670.7 | 31 | 93.3 | 116.2 | 59.9 | 256.7 | 241.8 | 80.9 | 183.2
540 | 388 | 370.4 | 148.16 | 173.1905 | 243.3 | 227.6 | 249.9 | 239.1 | 467.7 | 33.2 | 20.8 | 59.9 | 3.2 | 188.8 | 10.4 | 784.2 | 778 | 760.7 | 799.7 | 679.2 | 706 | 586.6 | 784.5 | 607 | 674.1 | 31.1 | 93.6 | 116.6 | 60.1 | 257.1 | 241.9 | 81.1 | 183.6
541 | 389 | 370.8 | 148.32 | 173.3775 | 243 | 228.7 | 249.7 | 240.1 | 470.6 | 33.3 | 20.8 | 60.1 | 3.2 | 190.6 | 10.5 | 785.3 | 778.4 | 775.1 | 801.6 | 680.9 | 705.8 | 587.1 | 785.9 | 608.3 | 676.4 | 31.2 | 93.8 | 116.7 | 60.3 | 257.1 | 241.7 | 81.4 | 183.8
542 | 390 | 370.6 | 148.24 | 173.284 | 242.7 | 230.4 | 249.6 | 240.8 | 467 | 33.4 | 20.8 | 60.2 | 2.8 | 170.5 | 10.1 | 786.7 | 777 | 784.1 | 803.4 | 683.2 | 706.4 | 584.3 | 789.6 | 609.9 | 677.5 | 31.3 | 94.1 | 117.1 | 60.4 | 257.1 | 241.9 | 81.6 | 184.2
543 | 391 | 371 | 148.4 | 173.471 | 242.2 | 231.2 | 249.6 | 241 | 466.3 | 33.5 | 20.8 | 60.3 | 2.9 | 173.5 | 9.5 | 787.2 | 777 | 787 | 805.5 | 684.6 | 706.9 | 586.2 | 793.7 | 611.3 | 680.5 | 31.4 | 94.3 | 117.3 | 60.6 | 257.1 | 242.3 | 81.8 | 184.5
544 | 392 | 371.3 | 148.52 | 173.6113 | 241.2 | 232.3 | 249.8 | 241 | 462 | 33.5 | 20.8 | 60.4 | 2.6 | 175.2 | 9 | 788.2 | 776.7 | 798.5 | 807.1 | 689.2 | 707 | 584.8 | 797.2 | 613.2 | 682.1 | 31.4 | 94.6 | 117.4 | 60.8 | 257.3 | 242.4 | 82 | 184.8
545 | 393 | 371.1 | 148.44 | 173.5178 | 241.4 | 233.5 | 249.9 | 241 | 466.9 | 33.6 | 20.8 | 60.4 | 2.4 | 189.3 | 8.8 | 788.8 | 775.4 | 798.2 | 808.5 | 693 | 707.1 | 585.1 | 804.5 | 614.9 | 683.7 | 31.5 | 94.9 | 117.8 | 60.9 | 257.4 | 242.9 | 82.2 | 185
546 | 394 | 370.7 | 148.28 | 173.3308 | 242.1 | 234.7 | 249.8 | 240.8 | 470.8 | 33.7 | 20.8 | 60.5 | 2.6 | 194.6 | 8.4 | 789.6 | 777.3 | 779.8 | 811 | 691.1 | 707 | 581.2 | 804.4 | 616.8 | 683.8 | 31.6 | 95.1 | 118 | 61.1 | 257.7 | 243.5 | 82.5 | 185.3
547 | 395 | 371.9 | 148.76 | 173.8919 | 242.6 | 235.2 | 249.8 | 241.1 | 472.9 | 33.6 | 20.8 | 60.5 | 2.7 | 203.2 | 8.4 | 791.2 | 781.2 | 759.2 | 813.6 | 687.5 | 707.4 | 577.5 | 797.5 | 618.9 | 683 | 31.7 | 95.4 | 118.3 | 61.3 | 257.8 | 243.7 | 82.7 | 185.5
548 | 396 | 370.9 | 148.36 | 173.4243 | 243.9 | 235.8 | 249.8 | 241.6 | 468.8 | 33.6 | 20.8 | 60.6 | 2.6 | 212 | 8.3 | 792.2 | 784.2 | 741 | 815.7 | 683.6 | 708 | 574.3 | 778.2 | 621.1 | 681.2 | 31.8 | 95.6 | 118.7 | 61.4 | 257.7 | 243.7 | 82.9 | 185.8
549 | 397 | 371.4 | 148.56 | 173.6581 | 245.7 | 236.4 | 250.4 | 242.2 | 457 | 33.6 | 20.8 | 60.7 | 3 | 182.7 | 8.5 | 792.5 | 786.1 | 722.5 | 816.2 | 679.9 | 708.9 | 569.8 | 753.6 | 623.6 | 678.3 | 31.9 | 95.9 | 119 | 61.6 | 257.6 | 243.4 | 83.1 | 186.1
550 | 398 | 372.4 | 148.96 | 174.1257 | 247.2 | 235.8 | 251 | 242.7 | 446.9 | 33.7 | 20.8 | 60.8 | 3 | 179.8 | 8.1 | 792.6 | 784.4 | 706.4 | 815.4 | 676.9 | 710.3 | 566.6 | 738.1 | 625.7 | 676.2 | 32 | 96.1 | 119.1 | 61.8 | 257.9 | 243.3 | 83.4 | 186.3
551 | 399 | 370.8 | 148.32 | 173.3775 | 248.8 | 234.8 | 251 | 242.9 | 434.4 | 33.8 | 20.8 | 60.9 | 3.1 | 172.3 | 8.2 | 792.5 | 781 | 691.4 | 813.6 | 674.2 | 711.8 | 562.9 | 718.7 | 627.5 | 674.2 | 32 | 96.4 | 119.4 | 61.9 | 258.1 | 243.4 | 83.5 | 186.6
552 | 400 | 371.2 | 148.48 | 173.5646 | 250.1 | 233.8 | 251 | 243.3 | 427.4 | 34 | 20.8 | 61 | 2.6 | 181.8 | 7.7 | 792.2 | 778.3 | 686.1 | 811.9 | 672.5 | 713.5 | 559.9 | 705.3 | 629.5 | 672.2 | 32.1 | 96.6 | 119.8 | 62.1 | 259.2 | 243.5 | 83.8 | 186.9
553 | 401 | 371.4 | 148.56 | 173.6581 | 251.6 | 232.6 | 250.8 | 243.7 | 422.6 | 34 | 20.7 | 61.1 | 2.8 | 196.6 | 7.2 | 792.7 | 776.8 | 682.2 | 811.6 | 671.4 | 715.6 | 558 | 694.3 | 632.1 | 670.8 | 32.2 | 96.9 | 120.1 | 62.3 | 260.2 | 244.2 | 84 | 187.3
554 | 402 | 371.6 | 148.64 | 173.7516 | 252.3 | 231.2 | 250.6 | 244.2 | 423.3 | 34 | 20.7 | 61.2 | 3.2 | 198.8 | 7 | 793.8 | 775.1 | 685.1 | 811.9 | 670.9 | 717.6 | 555.6 | 687.9 | 634.3 | 669.5 | 32.3 | 97.1 | 120.3 | 62.5 | 259.9 | 244.6 | 84.2 | 187.6
555 | 403 | 371.9 | 148.76 | 173.8919 | 252.1 | 230.3 | 251.1 | 244.4 | 421.4 | 33.9 | 20.7 | 61.3 | 3.2 | 211.6 | 6.7 | 794.2 | 771.7 | 693.4 | 811.4 | 671.3 | 719.6 | 554 | 684.1 | 636.6 | 669.1 | 32.4 | 97.4 | 120.4 | 62.6 | 259.7 | 245.5 | 84.4 | 188.1
556 | 404 | 372.1 | 148.84 | 173.9854 | 251.9 | 229.8 | 251.4 | 244.3 | 418.9 | 33.9 | 20.7 | 61.5 | 3.7 | 206.2 | 6.7 | 793.3 | 770.7 | 696.4 | 812.1 | 671.4 | 721.4 | 556.7 | 668.4 | 639.2 | 668.7 | 32.5 | 97.6 | 120.5 | 62.8 | 259.9 | 246.1 | 84.6 | 188.5
557 | 405 | 372.1 | 148.84 | 173.9854 | 250.8 | 229.4 | 251.3 | 244.3 | 416.9 | 34 | 20.7 | 61.6 | 3.9 | 193.6 | 6.6 | 793.2 | 770.6 | 711.1 | 813.3 | 671.5 | 723.8 | 556.7 | 675.2 | 641.7 | 669.9 | 32.5 | 97.9 | 120.9 | 62.9 | 261 | 246.3 | 84.8 | 188.9
558 | 406 | 372.5 | 149 | 174.1724 | 250.5 | 228.5 | 251.8 | 244.5 | 414.9 | 34 | 20.7 | 61.8 | 4 | 191.9 | 6.2 | 793.3 | 770.8 | 712.1 | 815.5 | 670.8 | 725.8 | 555.7 | 685 | 643.6 | 671.3 | 32.6 | 98.1 | 121.1 | 63.1 | 262.4 | 246.1 | 85.1 | 189.3
559 | 407 | 371.8 | 148.72 | 173.8451 | 250.9 | 228 | 252.3 | 245.2 | 414.2 | 34.1 | 20.7 | 61.9 | 3.7 | 192.8 | 5.8 | 793.7 | 770.3 | 722.8 | 816.8 | 671.2 | 727 | 557.5 | 690.3 | 645.5 | 672.4 | 32.7 | 98.3 | 121.1 | 63.3 | 261.9 | 246.2 | 85.3 | 189.6
560 | 408 | 371.4 | 148.56 | 173.6581 | 250.7 | 228.1 | 252.5 | 245.7 | 413.5 | 34.2 | 20.7 | 62.1 | 3.1 | 197 | 5.5 | 793.4 | 769.7 | 731.4 | 818.3 | 675.7 | 728 | 564.5 | 684.4 | 647.1 | 674.8 | 32.8 | 98.6 | 121.4 | 63.5 | 262 | 246.2 | 85.5 | 189.9
561 | 409 | 371.2 | 148.48 | 173.5646 | 250.6 | 228.4 | 252.8 | 245.6 | 416.3 | 34.3 | 20.7 | 62.2 | 2.9 | 193.2 | 5 | 793.7 | 769.1 | 738.6 | 820.4 | 678.3 | 728.5 | 568.9 | 693.3 | 648.8 | 678.1 | 32.9 | 98.8 | 121.9 | 63.6 | 261.7 | 246.6 | 85.7 | 190
562 | 410 | 370.7 | 148.28 | 173.3308 | 251.2 | 228.7 | 253.5 | 245.4 | 421 | 34.3 | 20.7 | 62.3 | 2.9 | 179 | 5.4 | 793.8 | 771 | 733.1 | 822.6 | 676.4 | 729.4 | 570.6 | 681.5 | 651.5 | 677 | 33 | 99 | 122.3 | 63.8 | 261.6 | 247.2 | 86 | 190.4
563 | 411 | 371 | 148.4 | 173.471 | 251.6 | 228.3 | 254 | 245.4 | 417.4 | 34.3 | 20.7 | 62.4 | 3.1 | 178.3 | 6.4 | 794.7 | 771.3 | 721.3 | 824.7 | 675.4 | 731.2 | 570.8 | 671.5 | 654.6 | 675.9 | 33.1 | 99.3 | 122.5 | 64 | 261.2 | 247.4 | 86.2 | 190.7
564 | 412 | 371.3 | 148.52 | 173.6113 | 251.7 | 228.4 | 255.2 | 245.7 | 415.7 | 34.3 | 20.7 | 62.4 | 2.9 | 177.2 | 6.8 | 796.3 | 770.2 | 720.3 | 825.9 | 676.3 | 733.5 | 566.9 | 676.5 | 657.4 | 675.6 | 33.2 | 99.5 | 122.7 | 64.2 | 261.2 | 247.2 | 86.4 | 191
565 | 413 | 371.2 | 148.48 | 173.5646 | 251.2 | 229.9 | 255.6 | 245.9 | 419.6 | 34.4 | 20.7 | 62.5 | 2.8 | 195.6 | 6.9 | 797.6 | 770.3 | 719.3 | 827.5 | 676.2 | 735.2 | 564 | 680.2 | 659 | 675.1 | 33.2 | 99.8 | 123 | 64.3 | 261.1 | 247.3 | 86.6 | 191.2
566 | 414 | 371 | 148.4 | 173.471 | 251.5 | 230.4 | 255.6 | 245.6 | 420.2 | 34.5 | 20.7 | 62.6 | 2.6 | 188.9 | 7.6 | 797.6 | 772.3 | 712.6 | 828.5 | 673.7 | 736.5 | 563.3 | 672.7 | 660.9 | 673.2 | 33.3 | 100 | 123.2 | 64.5 | 261 | 247.2 | 86.8 | 191.5
567 | 415 | 371.7 | 148.68 | 173.7984 | 251 | 230.5 | 255.5 | 245.2 | 420.2 | 34.5 | 20.7 | 62.6 | 2.4 | 189.8 | 8 | 797.4 | 771.6 | 711.7 | 829.1 | 674.4 | 737.3 | 563.4 | 670.5 | 662.2 | 673 | 33.4 | 100.3 | 123.4 | 64.7 | 260.9 | 247.5 | 87.1 | 191.8
568 | 416 | 370.9 | 148.36 | 173.4243 | 249.5 | 229.7 | 255.3 | 245.1 | 418.6 | 34.5 | 20.7 | 62.6 | 2.7 | 187.2 | 6.9 | 797.7 | 773.2 | 712.2 | 830.8 | 673.1 | 738.3 | 563 | 674.5 | 664.3 | 672.1 | 33.5 | 100.5 | 123.7 | 64.9 | 261 | 247.4 | 87.2 | 192.1
569 | 417 | 371.9 | 148.76 | 173.8919 | 249.8 | 229.2 | 255.2 | 244.9 | 421.1 | 34.5 | 20.7 | 62.7 | 2.9 | 185 | 7.1 | 799.1 | 773.8 | 714.4 | 832.3 | 673.8 | 739.5 | 562.1 | 678.8 | 666.4 | 672.2 | 33.6 | 100.8 | 124.1 | 65 | 261 | 247.5 | 87.5 | 192.3
570 | 418 | 372.5 | 149 | 174.1724 | 250.1 | 228.8 | 254.9 | 244.2 | 422.1 | 34.6 | 20.7 | 62.7 | 3.2 | 176 | 7.1 | 799.1 | 774.6 | 711.7 | 833.6 | 672.5 | 740.4 | 561.5 | 674.6 | 668.6 | 671.5 | 33.7 | 101 | 124.3 | 65.2 | 261.2 | 247.3 | 87.7 | 192.7
571 | 419 | 371.3 | 148.52 | 173.6113 | 248.7 | 228.5 | 254.9 | 244 | 418.6 | 34.6 | 20.7 | 62.7 | 3.5 | 173.5 | 6.7 | 798.9 | 775.7 | 705.9 | 834.7 | 670.8 | 742.3 | 562.5 | 658 | 671.6 | 670.4 | 33.8 | 101.2 | 124.6 | 65.4 | 261.2 | 247.4 | 87.9 | 193
572 | 420 | 371.3 | 148.52 | 173.6113 | 248 | 228.8 | 255.1 | 243.8 | 414.6 | 34.7 | 20.7 | 62.7 | 3.2 | 190.2 | 7.2 | 799 | 773.8 | 720.6 | 834.4 | 672.6 | 744.4 | 568.7 | 654.3 | 673 | 672.6 | 33.9 | 101.5 | 124.7 | 65.5 | 261.4 | 247.8 | 88.1 | 193.4
573 | 421 | 371.4 | 148.56 | 173.6581 | 247.6 | 229.9 | 255.7 | 244.2 | 417.5 | 34.8 | 20.7 | 62.7 | 3 | 186.7 | 6.9 | 800.9 | 774.4 | 728.7 | 836.1 | 676.2 | 745 | 574.3 | 671.1 | 673.8 | 675.5 | 34 | 101.7 | 124.9 | 65.7 | 261.9 | 247.9 | 88.3 | 193.8
574 | 422 | 371 | 148.4 | 173.471 | 247.6 | 229.7 | 256.3 | 244.8 | 419 | 34.9 | 20.7 | 62.7 | 2.9 | 192.4 | 6 | 802.2 | 774.7 | 726.5 | 838.2 | 675.9 | 745.2 | 572.2 | 669.1 | 675.6 | 674.8 | 34 | 101.9 | 125.2 | 65.9 | 261.9 | 248.1 | 88.5 | 194
575 | 423 | 372.5 | 149 | 174.1724 | 247.8 | 229.7 | 256.9 | 245.1 | 417.3 | 35.1 | 20.7 | 62.7 | 3 | 198.8 | 6.4 | 803.5 | 775.8 | 735.2 | 840.1 | 676.2 | 746.3 | 571 | 676.4 | 677.6 | 675.4 | 34.1 | 102.2 | 125.6 | 66.1 | 262 | 247.9 | 88.7 | 194.3
576 | 424 | 372.1 | 148.84 | 173.9854 | 247.6 | 229.6 | 257.1 | 245.1 | 420.1 | 35.2 | 20.7 | 62.7 | 3.2 | 192.8 | 6.9 | 805.5 | 776.3 | 740.2 | 842.2 | 679.9 | 747.8 | 569.7 | 692.9 | 680.1 | 676.2 | 34.2 | 102.4 | 125.8 | 66.2 | 262.2 | 248 | 89 | 194.6
577 | 425 | 372.3 | 148.92 | 174.0789 | 246.8 | 229.9 | 256.8 | 245 | 422.6 | 35.4 | 20.7 | 62.8 | 3.3 | 171.9 | 7.2 | 806.8 | 776.5 | 734.7 | 844.5 | 678 | 748.9 | 566.5 | 701.2 | 682.9 | 676.7 | 34.3 | 102.6 | 126 | 66.4 | 262.4 | 247.9 | 89.2 | 194.9
578 | 426 | 372.1 | 148.84 | 173.9854 | 247.1 | 231 | 256.7 | 245 | 424.6 | 35.5 | 20.7 | 62.8 | 3.3 | 172.2 | 7.5 | 807.6 | 774.4 | 745.9 | 844.7 | 678.3 | 750.1 | 564.3 | 711.8 | 685.7 | 677.6 | 34.4 | 102.9 | 126.2 | 66.6 | 262.6 | 248 | 89.4 | 195.2
579 | 427 | 372.2 | 148.88 | 174.0321 | 247.3 | 231.3 | 256.4 | 245.1 | 426.1 | 35.6 | 20.7 | 62.9 | 3.3 | 166.3 | 7.9 | 808.7 | 776.2 | 761.7 | 846.5 | 682.3 | 750.8 | 565.7 | 734.6 | 688 | 681 | 34.5 | 103.1 | 126.6 | 66.8 | 262.8 | 248.1 | 89.6 | 195.6
580 | 428 | 371.6 | 148.64 | 173.7516 | 247.4 | 231 | 255.7 | 245.2 | 432.4 | 35.7 | 20.7 | 63 | 3.3 | 172.2 | 7.8 | 809.6 | 774.7 | 769.3 | 847.8 | 685.6 | 751.8 | 566 | 746.4 | 690 | 683 | 34.6 | 103.4 | 126.9 | 66.9 | 262.7 | 248 | 89.8 | 195.8
581 | 429 | 370.8 | 148.32 | 173.3775 | 247.4 | 231.5 | 255.4 | 245.4 | 441.5 | 35.7 | 20.7 | 63 | 2.8 | 171.7 | 6.7 | 810.9 | 775.8 | 775.5 | 849.2 | 687.1 | 753 | 565 | 765.9 | 692.6 | 685.2 | 34.7 | 103.6 | 127.4 | 67.1 | 262.7 | 247.8 | 90 | 196.1
582 | 430 | 371 | 148.4 | 173.471 | 246.8 | 233 | 255.7 | 245.6 | 442.4 | 35.8 | 20.7 | 63.1 | 2.9 | 169.9 | 6.6 | 810.8 | 773.8 | 782.7 | 851.3 | 689.6 | 754.2 | 564.4 | 766.6 | 694 | 686.3 | 34.8 | 103.8 | 127.4 | 67.3 | 262.7 | 248 | 90.2 | 196.3
583 | 431 | 371.8 | 148.72 | 173.8451 | 245.7 | 234.2 | 255.5 | 246 | 443.8 | 35.8 | 20.7 | 63.1 | 3.1 | 159.5 | 6.6 | 811.2 | 774.3 | 785.2 | 853.3 | 691.8 | 754.4 | 564.8 | 769.8 | 694.9 | 688.1 | 34.9 | 104.1 | 127.6 | 67.5 | 262.1 | 248.3 | 90.5 | 196.7
584 | 432 | 371.4 | 148.56 | 173.6581 | 245.2 | 234.7 | 255.3 | 246.4 | 443.5 | 35.9 | 20.7 | 63.2 | 3.5 | 185.5 | 5.8 | 811.5 | 772.9 | 792.4 | 853.4 | 694 | 754.3 | 571.9 | 778.3 | 695.4 | 690.8 | 35 | 104.3 | 127.8 | 67.6 | 261.9 | 248.4 | 90.7 | 196.9
585 | 433 | 372.1 | 148.84 | 173.9854 | 244.9 | 235.5 | 254.8 | 246.5 | 446.7 | 35.9 | 20.7 | 63.2 | 3.3 | 209.2 | 5.2 | 811.6 | 772.1 | 791.1 | 854.7 | 694.4 | 753.3 | 574 | 786.6 | 696.1 | 692.2 | 35 | 104.6 | 128.1 | 67.8 | 261.5 | 248.3 | 90.9 | 197.1
586 | 434 | 371.3 | 148.52 | 173.6113 | 244.9 | 236.9 | 254.6 | 246.8 | 448.5 | 35.9 | 20.6 | 63.2 | 2.8 | 195.6 | 4.2 | 811.9 | 772.8 | 792.6 | 855.8 | 696.3 | 752.5 | 576.1 | 792.2 | 696.8 | 694.6 | 35.1 | 104.8 | 128.5 | 68 | 261.4 | 248.6 | 91.1 | 197.3
587 | 435 | 371.5 | 148.6 | 173.7048 | 245.2 | 238.7 | 254.8 | 246.6 | 447.3 | 35.9 | 20.6 | 63.2 | 3.2 | 198.1 | 4.1 | 812.2 | 775.5 | 781.8 | 858.2 | 694.8 | 752.4 | 576.6 | 787.2 | 699.2 | 695.4 | 35.2 | 105.1 | 128.6 | 68.2 | 261.3 | 248.7 | 91.4 | 197.6
588 | 436 | 371.6 | 148.64 | 173.7516 | 245.3 | 240 | 254.8 | 246.5 | 441.6 | 36 | 20.6 | 63.2 | 3.6 | 206.9 | 5.1 | 813.2 | 777.3 | 784.6 | 859.7 | 695.1 | 753.7 | 578.2 | 778.6 | 703.1 | 696 | 35.3 | 105.3 | 128.9 | 68.4 | 261 | 248.3 | 91.6 | 197.8
589 | 437 | 371.6 | 148.64 | 173.7516 | 244.8 | 241.1 | 255 | 246.8 | 442.3 | 36 | 20.6 | 63.2 | 3.1 | 221.1 | 6.7 | 814.1 | 776.8 | 793.2 | 861.2 | 697.7 | 755.7 | 576.5 | 776.8 | 706.6 | 696.3 | 35.4 | 105.6 | 129.2 | 68.5 | 261.1 | 248.2 | 91.8 | 198
590 | 438 | 371.3 | 148.52 | 173.6113 | 244.9 | 241.1 | 255 | 246.8 | 447.9 | 36 | 20.6 | 63.2 | 3.2 | 232.4 | 6.9 | 814.9 | 777.2 | 798.8 | 862.7 | 704.3 | 758.3 | 576.3 | 775.9 | 710.2 | 696.1 | 35.5 | 105.8 | 129.4 | 68.7 | 261.3 | 247.9 | 92 | 198.2
591 | 439 | 370.8 | 148.32 | 173.3775 | 246.1 | 241.6 | 255.1 | 246.9 | 451.5 | 36 | 20.6 | 63.1 | 3.1 | 224.8 | 7.2 | 816.3 | 777.4 | 796.1 | 864.2 | 706.1 | 761 | 575.5 | 783.6 | 713.8 | 697.2 | 35.6 | 106.1 | 129.5 | 68.9 | 261.5 | 247.7 | 92.3 | 198.5
592 | 440 | 370.8 | 148.32 | 173.3775 | 247 | 242.6 | 254.9 | 247.3 | 454.7 | 36 | 20.6 | 63.1 | 2.9 | 227.3 | 7 | 817 | 776.5 | 797.5 | 865.1 | 708.1 | 762.3 | 580.8 | 779.3 | 714.2 | 700.1 | 35.7 | 106.3 | 129.8 | 69.1 | 262 | 248 | 92.4 | 198.7
593 | 441 | 371.5 | 148.6 | 173.7048 | 246.7 | 243 | 255 | 247.9 | 454.3 | 36 | 20.6 | 63.2 | 2.8 | 199.3 | 6.4 | 817.3 | 777.4 | 795.1 | 865.5 | 709.3 | 762.7 | 589 | 776.2 | 715.6 | 701.1 | 35.8 | 106.6 | 130.2 | 69.2 | 262.4 | 248.3 | 92.7 | 199
594 | 442 | 371 | 148.4 | 173.471 | 246.3 | 243.1 | 255 | 248.9 | 450 | 36.1 | 20.6 | 63.3 | 3.1 | 204.8 | 6 | 817.5 | 778.8 | 795.5 | 865.5 | 714.4 | 764 | 593.9 | 764.8 | 718.2 | 701.9 | 35.9 | 106.8 | 130.5 | 69.4 | 262.3 | 249.1 | 92.9 | 199.4
595 | 443 | 370.7 | 148.28 | 173.3308 | 245.9 | 243.8 | 255.3 | 249.2 | 447.4 | 36.2 | 20.6 | 63.3 | 3.5 | 190 | 5.4 | 817.2 | 778.8 | 792.5 | 865.3 | 715.2 | 765 | 600.6 | 751.2 | 719.5 | 703.6 | 36 | 107 | 130.7 | 69.6 | 262.1 | 250.1 | 93.1 | 199.8
596 | 444 | 371.4 | 148.56 | 173.6581 | 245.7 | 244.6 | 255.2 | 249.2 | 446.5 | 36.2 | 20.6 | 63.4 | 3.2 | 160.9 | 4.8 | 817.2 | 779.2 | 797.8 | 865.3 | 718.5 | 765.2 | 604.9 | 745 | 720.3 | 705.5 | 36.1 | 107.3 | 131 | 69.8 | 262.1 | 250.9 | 93.4 | 200.1
597 | 445 | 371 | 148.4 | 173.471 | 245.8 | 246.5 | 255.5 | 249.2 | 446.1 | 36.3 | 20.6 | 63.4 | 3.6 | 161.7 | 3.9 | 817.3 | 776.3 | 800.8 | 865.5 | 722.6 | 765.4 | 611 | 747.9 | 721.2 | 706.7 | 36.2 | 107.5 | 131.2 | 69.9 | 262.4 | 251.5 | 93.6 | 200.4
598 | 446 | 372.5 | 149 | 174.1724 | 246 | 248 | 256.1 | 249 | 446.7 | 36.3 | 20.6 | 63.5 | 3.2 | 173.5 | 3.2 | 817.9 | 775.5 | 797.6 | 866.1 | 722.9 | 765.4 | 612 | 745.3 | 722.2 | 707.2 | 36.3 | 107.7 | 131.3 | 70.1 | 262.3 | 251.6 | 93.8 | 200.7
599 | 447 | 372.1 | 148.84 | 173.9854 | 245.9 | 248.5 | 256.6 | 248.9 | 451.2 | 36.3 | 20.6 | 63.5 | 3.1 | 193.7 | 2.4 | 819.8 | 776.7 | 797.4 | 867.5 | 722.2 | 765.6 | 610.4 | 762 | 722.5 | 708.9 | 36.4 | 108 | 131.6 | 70.3 | 262.4 | 251.7 | 94 | 200.8
600 | 448 | 372.3 | 148.92 | 174.0789 | 245.1 | 249.2 | 256.8 | 249.1 | 457 | 36.4 | 20.6 | 63.6 | 3 | 219.9 | 2.2 | 821.3 | 775.8 | 794.9 | 868.7 | 722.1 | 765.7 | 605.3 | 770.9 | 723.4 | 709.5 | 36.4 | 108.2 | 131.9 | 70.5 | 262.5 | 251.8 | 94.2 | 201
601 | 449 | 371.4 | 148.56 | 173.6581 | 244.7 | 249.6 | 256.6 | 249.6 | 455.3 | 36.4 | 20.6 | 63.6 | 3.1 | 229.2 | 2 | 821.5 | 776 | 791.8 | 869.8 | 722.4 | 766.3 | 602.3 | 764.1 | 723.9 | 710.7 | 36.5 | 108.4 | 132.2 | 70.7 | 262.6 | 251.7 | 94.4 | 201.3
602 | 450 | 371.9 | 148.76 | 173.8919 | 244.7 | 249.2 | 256.8 | 249.9 | 456.6 | 36.4 | 20.6 | 63.7 | 2.9 | 205.3 | 2.1 | 822.1 | 775.7 | 794.2 | 870.5 | 722.2 | 766.2 | 601.1 | 779.4 | 724.2 | 712.4 | 36.6 | 108.7 | 132.4 | 70.9 | 262.7 | 251.5 | 94.7 | 201.6
603 | 451 | 369.3 | 147.72 | 172.6762 | 244.9 | 248.2 | 256.7 | 250.2 | 459.9 | 36.3 | 20.6 | 63.8 | 2.8 | 174.9 | 3.7 | 822.4 | 775.6 | 795.3 | 872.1 | 721.7 | 765.9 | 597.3 | 783.8 | 724.5 | 712.8 | 36.7 | 108.9 | 132.7 | 71 | 262.5 | 252.1 | 94.9 | 201.8
604 | 452 | 368.6 | 147.44 | 172.3489 | 245.2 | 247.5 | 256.4 | 250.4 | 459.4 | 36.2 | 20.6 | 63.8 | 3 | 190.3 | 5.6 | 823 | 776.5 | 799.6 | 872.9 | 723.4 | 766.2 | 594.2 | 784.7 | 726.1 | 713.1 | 36.8 | 109.1 | 133.1 | 71.2 | 262.6 | 252.3 | 95.1 | 202.1
605 | 453 | 370 | 148 | 173.0035 | 245.3 | 246.5 | 256.1 | 250.2 | 461.9 | 36.1 | 20.6 | 63.8 | 3.2 | 195 | 6.6 | 823.2 | 773.6 | 800 | 873.7 | 724.9 | 766.1 | 595.7 | 796.5 | 726.7 | 715.6 | 36.9 | 109.4 | 133.6 | 71.4 | 262.6 | 252.3 | 95.3 | 202.3
606 | 454 | 370.2 | 148.08 | 173.097 | 245 | 247 | 256.1 | 250.1 | 468.5 | 36 | 20.6 | 63.9 | 3.1 | 185 | 6.8 | 823.6 | 773 | 805.2 | 874.7 | 726.2 | 765.5 | 595.1 | 806.2 | 726.8 | 716.9 | 37 | 109.6 | 133.8 | 71.6 | 262.6 | 252.6 | 95.6 | 202.6
607 | 455 | 370.4 | 148.16 | 173.1905 | 245.3 | 248 | 256.1 | 250.3 | 475.9 | 35.9 | 20.6 | 64 | 3.1 | 196.6 | 6.7 | 823.2 | 771.3 | 809.4 | 874.7 | 726.6 | 764.8 | 597.3 | 811 | 726.2 | 718.2 | 37.1 | 109.9 | 133.9 | 71.7 | 262.7 | 252.9 | 95.8 | 202.9
608 | 456 | 370.9 | 148.36 | 173.4243 | 245.8 | 249.1 | 255.3 | 250.7 | 476.7 | 36 | 20.6 | 64 | 3.5 | 199 | 6.6 | 823.8 | 772.5 | 812.2 | 875.8 | 728.8 | 763.5 | 598.9 | 813.6 | 726.1 | 720 | 37.2 | 110.1 | 134.2 | 71.9 | 262.9 | 253.3 | 96 | 203.1
609 | 457 | 372.4 | 148.96 | 174.1257 | 245.5 | 249.9 | 254.9 | 251.1 | 476.2 | 36.2 | 20.6 | 64 | 3.1 | 202.4 | 6.5 | 824.5 | 772.7 | 812.9 | 877.1 | 730 | 763.4 | 594.8 | 806.8 | 727.5 | 719 | 37.3 | 110.4 | 134.4 | 72.1 | 263.1 | 253.5 | 96.2 | 203.4
610 | 458 | 373.1 | 149.24 | 174.453 | 245.2 | 250.2 | 255.1 | 251.6 | 481.7 | 36.2 | 20.6 | 64 | 3.4 | 180.8 | 6.6 | 825.6 | 774.4 | 809.3 | 879 | 729.7 | 764.1 | 592.7 | 807.2 | 728.8 | 719.3 | 37.4 | 110.6 | 134.7 | 72.3 | 263.3 | 253.7 | 96.5 | 203.6
611 | 459 | 373.1 | 149.24 | 174.453 | 245.2 | 249.7 | 255.2 | 252.3 | 499.3 | 36.3 | 20.6 | 64 | 3.4 | 195.9 | 6.6 | 826.5 | 775 | 807.5 | 879.9 | 728.9 | 765.1 | 588.2 | 799.4 | 730.3 | 717.8 | 37.5 | 110.9 | 135 | 72.5 | 263.4 | 253.7 | 96.7 | 203.9
612 | 460 | 368.8 | 147.52 | 172.4424 | 245.2 | 250.1 | 255.4 | 252.8 | 502.7 | 36.3 | 20.6 | 64 | 2.8 | 198.3 | 6.7 | 827.4 | 775.6 | 810.5 | 880.5 | 731 | 766.6 | 585.8 | 799.4 | 731.8 | 717.2 | 37.6 | 111.1 | 135.3 | 72.6 | 263.4 | 253.6 | 96.9 | 204
613 | 461 | 370.1 | 148.04 | 173.0502 | 245.8 | 250.8 | 255.7 | 253.4 | 500.6 | 36.2 | 20.6 | 64 | 2.7 | 204.2 | 6.8 | 827.1 | 775.9 | 810.9 | 879.6 | 732.3 | 767.1 | 588.5 | 789.9 | 732.8 | 717.8 | 37.7 | 111.4 | 135.5 | 72.8 | 263.7 | 253.2 | 97.1 | 204.3
614 | 462 | 370.7 | 148.28 | 173.3308 | 246 | 250.8 | 255.2 | 253.8 | 489.9 | 36.1 | 20.6 | 64.1 | 3.1 | 218.3 | 7.2 | 826.7 | 777 | 814 | 879.1 | 732.4 | 767 | 590.2 | 774 | 733.4 | 717.2 | 37.8 | 111.6 | 135.7 | 73 | 264 | 253.2 | 97.3 | 204.5
615 | 463 | 369.5 | 147.8 | 172.7697 | 246.9 | 250.7 | 255.5 | 253.7 | 479.6 | 36 | 20.6 | 64.1 | 3 | 208.4 | 7.3 | 827.2 | 777.3 | 811.2 | 879.5 | 734.6 | 767.5 | 587.4 | 770.3 | 734.3 | 717.2 | 37.9 | 111.8 | 135.9 | 73.2 | 264.2 | 253.2 | 97.6 | 204.8
616 | 464 | 370.8 | 148.32 | 173.3775 | 246 | 250.5 | 255.7 | 253.5 | 475.3 | 36 | 20.6 | 64.2 | 3.2 | 207.7 | 7 | 827.7 | 776.6 | 809.5 | 878.8 | 734.3 | 768 | 590 | 762.8 | 735.6 | 717.5 | 38 | 112.1 | 136.2 | 73.4 | 265.1 | 253.6 | 97.8 | 205.1
617 | 465 | 371.1 | 148.44 | 173.5178 | 245.8 | 250.8 | 255.9 | 253.3 | 470.3 | 36.1 | 20.5 | 64.2 | 3.2 | 208.3 | 6.9 | 828.4 | 777.8 | 810.5 | 878.3 | 735.3 | 768.9 | 587.6 | 764.9 | 736.9 | 717.2 | 38.1 | 112.3 | 136.3 | 73.5 | 265 | 254.4 | 98 | 205.5
618 | 466 | 371.2 | 148.48 | 173.5646 | 247 | 251 | 256.1 | 253.3 | 469.8 | 36.1 | 20.5 | 64.2 | 3.3 | 202.3 | 7.1 | 829.7 | 779.3 | 805.1 | 877.7 | 733.6 | 770.3 | 583.4 | 764.1 | 738.5 | 716.4 | 38.2 | 112.5 | 136.6 | 73.7 | 264.9 | 254.6 | 98.2 | 205.7
619 | 467 | 370.6 | 148.24 | 173.284 | 247.5 | 251.5 | 256.4 | 252.8 | 460.8 | 36.1 | 20.5 | 64.3 | 3.2 | 199.2 | 7.4 | 830.3 | 780.4 | 806.1 | 877 | 734.7 | 771.7 | 582.5 | 748 | 740.2 | 715.4 | 38.3 | 112.8 | 137 | 73.9 | 264.9 | 254.2 | 98.5 | 205.9
620 | 468 | 370.8 | 148.32 | 173.3775 | 248.1 | 252.2 | 256.5 | 252.7 | 452 | 36.2 | 20.5 | 64.4 | 3.1 | 199.5 | 7.8 | 828.9 | 777.9 | 799.7 | 876 | 734.7 | 773.1 | 583.6 | 723 | 741.7 | 714.4 | 38.4 | 113 | 137.3 | 74.1 | 264.9 | 253.8 | 98.7 | 206.1
621 | 469 | 372 | 148.8 | 173.9386 | 248.8 | 252 | 256.6 | 252.8 | 444.6 | 36.4 | 20.5 | 64.4 | 3 | 200 | 7.9 | 828.1 | 776.1 | 794.8 | 874.6 | 732.7 | 775 | 581.4 | 707.1 | 743.6 | 712.3 | 38.5 | 113.2 | 137.3 | 74.3 | 264.8 | 253.7 | 98.9 | 206.2
622 | 470 | 372.5 | 149 | 174.1724 | 248.9 | 251.7 | 256.7 | 253.1 | 438.8 | 36.5 | 20.5 | 64.5 | 2.8 | 199.2 | 7.7 | 828.8 | 777.3 | 795.8 | 874.5 | 733.5 | 777.8 | 581.4 | 711 | 745.9 | 712.8 | 38.6 | 113.5 | 137.5 | 74.4 | 264.7 | 253.5 | 99.1 | 206.4
623 | 471 | 371.8 | 148.72 | 173.8451 | 248.4 | 251.5 | 257.2 | 253 | 441.3 | 36.5 | 20.5 | 64.6 | 3 | 196.9 | 7.3 | 830.7 | 778.8 | 791.9 | 873.4 | 731.9 | 779 | 580.3 | 732.6 | 746.5 | 714.2 | 38.7 | 113.6 | 137.8 | 74.6 | 264.8 | 253.3 | 99.3 | 206.6
624 | 472 | 369.2 | 147.68 | 172.6294 | 247.7 | 251 | 257.7 | 253 | 470.1 | 36.6 | 20.5 | 64.7 | 3.3 | 178.9 | 6.6 | 833 | 780.3 | 787.1 | 870.5 | 728.5 | 781.2 | 582.8 | 740.8 | 747.8 | 714.1 | 38.8 | 113.9 | 138.4 | 74.8 | 265.1 | 253.3 | 99.6 | 206.8
625 | 473 | 367 | 146.8 | 171.6007 | 248 | 250.9 | 257.9 | 253.3 | 492.9 | 36.6 | 20.5 | 64.8 | 3.1 | 191.3 | 6.1 | 835.5 | 780.3 | 786.6 | 867.3 | 727.5 | 783.3 | 582.4 | 758.8 | 749 | 714.2 | 38.9 | 114.1 | 138.7 | 75 | 265.6 | 253.5 | 99.8 | 207
626 | 474 | 369.4 | 147.76 | 172.7229 | 248.2 | 251.2 | 258.4 | 253.9 | 504 | 36.7 | 20.5 | 64.8 | 3.2 | 200.1 | 6.4 | 837.6 | 780.3 | 794 | 867.1 | 728.9 | 784 | 582.3 | 766.5 | 749.3 | 715.6 | 39 | 114.3 | 138.9 | 75.1 | 266.3 | 253.8 | 100 | 207.3
627 | 475 | 370.1 | 148.04 | 173.0502 | 248.8 | 251.1 | 258.5 | 254.6 | 500.6 | 36.9 | 20.5 | 64.8 | 3.3 | 195.5 | 6.5 | 838 | 781.1 | 800.7 | 867.5 | 732.8 | 785 | 583.6 | 762.7 | 750 | 716.8 | 39.1 | 114.6 | 139 | 75.3 | 266.5 | 254.5 | 100.2 | 207.6
628 | 476 | 371.9 | 148.76 | 173.8919 | 248.9 | 251.3 | 258.7 | 255.6 | 495.1 | 36.9 | 20.5 | 64.9 | 3.3 | 205 | 6.1 | 838.5 | 781.8 | 801.5 | 868.1 | 732.8 | 786.1 | 586.4 | 764.5 | 751.1 | 718.3 | 39.2 | 114.8 | 139.1 | 75.5 | 266.8 | 254.8 | 100.5 | 207.9
629 | 477 | 372.1 | 148.84 | 173.9854 | 249.2 | 250.6 | 258.9 | 255.9 | 488.8 | 36.9 | 20.5 | 64.9 | 3.3 | 204.9 | 6.2 | 838.2 | 781.8 | 800.7 | 867.6 | 733.1 | 787.8 | 586.5 | 746 | 751.6 | 717.1 | 39.3 | 115.1 | 139.3 | 75.7 | 267.2 | 255.3 | 100.7 | 208.1
630 | 478 | 371.7 | 148.68 | 173.7984 | 249.4 | 251.2 | 259 | 255.5 | 479.5 | 37 | 20.5 | 65 | 3 | 196.2 | 6.5 | 838.5 | 780.6 | 803.9 | 867.4 | 734.6 | 789.5 | 587.4 | 755.1 | 752.9 | 718.1 | 39.4 | 115.3 | 139.6 | 75.9 | 267.1 | 255.9 | 100.9 | 208.4
631 | 479 | 372.3 | 148.92 | 174.0789 | 250.1 | 252 | 259.2 | 254.4 | 477.3 | 37 | 20.5 | 65.1 | 3.1 | 212.7 | 6.5 | 838.5 | 780 | 805.1 | 867.8 | 736 | 790.1 | 584.3 | 761.2 | 753.1 | 718.8 | 39.5 | 115.5 | 139.9 | 76 | 266.7 | 256 | 101.1 | 208.6
632 | 480 | 371.9 | 148.76 | 173.8919 | 249.2 | 251.4 | 259.4 | 253.8 | 471.9 | 37 | 20.5 | 65.2 | 3.2 | 209.2 | 6.6 | 838.2 | 779.1 | 804.7 | 867.5 | 735.4 | 790.7 | 585.9 | 754.2 | 754 | 718.9 | 39.6 | 115.8 | 140.3 | 76.2 | 266.9 | 255.7 | 101.3 | 208.8
633 | 481 | 372 | 148.8 | 173.9386 | 248.1 | 252.2 | 259.5 | 253.8 | 463.4 | 37.1 | 20.5 | 65.2 | 3.3 | 208.3 | 6.7 | 837.9 | 779 | 805.4 | 867.6 | 734.5 | 790.9 | 588.4 | 746.1 | 754.9 | 719.7 | 39.7 | 116 | 140.5 | 76.4 | 267.3 | 255.6 | 101.5 | 209
634 | 482 | 370.2 | 148.08 | 173.097 | 248.3 | 253.7 | 259.4 | 253.8 | 459 | 37.2 | 20.5 | 65.2 | 3.1 | 220.1 | 6.9 | 837.3 | 778.8 | 805.8 | 866.8 | 733.6 | 791.5 | 592.5 | 727.3 | 755 | 718.5 | 39.8 | 116.3 | 140.8 | 76.6 | 267.3 | 255.4 | 101.8 | 209.2
635 | 483 | 369.3 | 147.72 | 172.6762 | 247.2 | 254.2 | 259.3 | 253.8 | 452.1 | 37.4 | 20.5 | 65.3 | 3 | 225.5 | 6.6 | 837.2 | 779.2 | 808.5 | 867.6 | 737.1 | 792.5 | 591.7 | 724.2 | 756 | 718.1 | 39.9 | 116.5 | 141 | 76.8 | 267.4 | 255.2 | 102 | 209.4
636 | 484 | 371 | 148.4 | 173.471 | 246.6 | 254.1 | 259.9 | 253.6 | 450.9 | 37.4 | 20.5 | 65.3 | 2.8 | 208.1 | 6.6 | 837.3 | 780.3 | 808.3 | 869 | 742.6 | 793 | 592.7 | 730.7 | 757.1 | 720.4 | 40 | 116.8 | 141.2 | 76.9 | 267.3 | 254.9 | 102.2 | 209.6
637 | 485 | 371 | 148.4 | 173.471 | 246.7 | 254.3 | 260.3 | 253.5 | 449.9 | 37.3 | 20.5 | 65.3 | 2.7 | 201.8 | 7 | 836.7 | 778.9 | 805.8 | 869.2 | 740.6 | 792.9 | 595.3 | 724.2 | 758 | 721.4 | 40.1 | 117 | 141.4 | 77.1 | 267.3 | 255.2 | 102.4 | 210
638 | 486 | 370.3 | 148.12 | 173.1437 | 247.3 | 255 | 260.6 | 253.1 | 445.8 | 37.2 | 20.5 | 65.3 | 2.7 | 212.6 | 7.1 | 835.8 | 777.6 | 805 | 867.9 | 741.7 | 792 | 594.9 | 715.8 | 758.1 | 720.8 | 40.2 | 117.2 | 141.6 | 77.3 | 267.1 | 255.4 | 102.6 | 210.2
639 | 487 | 370 | 148 | 173.0035 | 249.5 | 254.9 | 261 | 252.9 | 442.4 | 37.2 | 20.5 | 65.4 | 3.1 | 214 | 7.5 | 835.1 | 776.9 | 805.7 | 867.9 | 741.3 | 791.5 | 596.6 | 715.4 | 758.6 | 720.1 | 40.3 | 117.5 | 141.9 | 77.5 | 266.8 | 255.4 | 102.8 | 210.4
640 | 488 | 370.6 | 148.24 | 173.284 | 249.3 | 254.8 | 260.9 | 252.7 | 437.5 | 37.3 | 20.5 | 65.4 | 2.7 | 212.1 | 7.4 | 834.7 | 777.7 | 806.7 | 867.9 | 743.9 | 791.7 | 594.9 | 719.3 | 758.6 | 720 | 40.4 | 117.7 | 142.2 | 77.7 | 266.5 | 255.4 | 103 | 210.6
641 | 489 | 371.1 | 148.44 | 173.5178 | 249.2 | 254.6 | 260.9 | 252.4 | 435.1 | 37.3 | 20.5 | 65.4 | 2.3 | 210.1 | 7.4 | 835.4 | 778.6 | 807.8 | 868.4 | 745.3 | 792.2 | 595.3 | 726.6 | 759.8 | 720.8 | 40.5 | 117.9 | 142.4 | 77.9 | 266.6 | 255.4 | 103.2 | 210.9
642 | 490 | 371.9 | 148.76 | 173.8919 | 249.1 | 253.4 | 261.2 | 252.5 | 437.5 | 37.5 | 20.5 | 65.5 | 2.9 | 203.1 | 7.4 | 837 | 780.7 | 809.6 | 868.8 | 746 | 793.5 | 590 | 742.7 | 760.5 | 720.9 | 40.6 | 118.1 | 142.7 | 78 | 266.9 | 255.5 | 103.4 | 211.1
643 | 491 | 371.8 | 148.72 | 173.8451 | 249.3 | 253.2 | 261.1 | 253.1 | 444.6 | 37.5 | 20.5 | 65.6 | 3 | 205.8 | 7.4 | 838 | 779.3 | 810.7 | 868.7 | 746.6 | 794.6 | 588.3 | 755.1 | 761.6 | 721.2 | 40.7 | 118.2 | 142.9 | 78.2 | 267.4 | 255.5 | 103.7 | 211.2
644 | 492 | 371.2 | 148.48 | 173.5646 | 250 | 254.4 | 261.1 | 253.6 | 454.1 | 37.5 | 20.5 | 65.7 | 3.1 | 206.6 | 7.3 | 838.5 | 778.2 | 810.6 | 868.4 | 746.5 | 793.9 | 588.5 | 765.2 | 762.5 | 723.1 | 40.8 | 118.5 | 143.2 | 78.4 | 267.7 | 255.7 | 103.9 | 211.5
645 | 493 | 371.3 | 148.52 | 173.6113 | 248.9 | 255.1 | 261.3 | 253.9 | 457.9 | 37.5 | 20.5 | 65.7 | 2.9 | 204.9 | 7.2 | 838.4 | 778.8 | 812.2 | 868 | 748.5 | 792.8 | 593.3 | 767 | 763.7 | 725.4 | 41 | 118.7 | 143.3 | 78.6 | 267.8 | 256.2 | 104.1 | 211.8
646 | 494 | 371.2 | 148.48 | 173.5646 | 247.5 | 255.2 | 261.5 | 253.8 | 456.5 | 37.5 | 20.4 | 65.8 | 2.7 | 202.9 | 7.2 | 837.3 | 777.7 | 809.3 | 867.2 | 748.4 | 791.3 | 596.6 | 761.9 | 763.9 | 726.7 | 41.1 | 118.9 | 143.4 | 78.7 | 268 | 256.8 | 104.3 | 212.1
647 | 495 | 370.5 | 148.2 | 173.2373 | 246.8 | 255.9 | 261.6 | 253.8 | 454.3 | 37.5 | 20.4 | 65.8 | 3.4 | 206.2 | 7.5 | 837 | 779.6 | 809.3 | 867.1 | 748.5 | 790.2 | 599 | 757.9 | 763.6 | 727.7 | 41.2 | 119.2 | 143.6 | 78.9 | 267.9 | 257.3 | 104.5 | 212.3
648 | 496 | 371.3 | 148.52 | 173.6113 | 246 | 256.3 | 261.7 | 253.4 | 452.7 | 37.5 | 20.4 | 65.9 | 3.5 | 208.3 | 7.2 | 837.1 | 781.1 | 809.1 | 866.9 | 748.8 | 790.2 | 603.7 | 752.5 | 764.1 | 728.3 | 41.3 | 119.5 | 144 | 79.1 | 267.9 | 257.9 | 104.7 | 212.5
649 | 497 | 371.5 | 148.6 | 173.7048 | 245.4 | 256.7 | 262 | 253.5 | 451.7 | 37.5 | 20.4 | 65.9 | 3.5 | 208.2 | 6.5 | 837.2 | 781.6 | 806.6 | 867.5 | 748.4 | 789.9 | 606.1 | 745.8 | 764.4 | 728.7 | 41.4 | 119.7 | 144.3 | 79.3 | 267.9 | 258.5 | 104.9 | 212.8
650 | 498 | 371.5 | 148.6 | 173.7048 | 245.2 | 257.1 | 262.4 | 253.6 | 444.4 | 37.7 | 20.4 | 65.9 | 3.7 | 226.8 | 6.4 | 837.8 | 784.2 | 805.9 | 867.9 | 748.3 | 790.7 | 603.7 | 744.5 | 764.4 | 727.6 | 41.5 | 120 | 144.5 | 79.5 | 267.9 | 258.7 | 105.1 | 213
651 | 499 | 371.2 | 148.48 | 173.5646 | 245.2 | 256.5 | 262.8 | 253.5 | 446.3 | 37.7 | 20.4 | 65.9 | 3.6 | 241.7 | 5.8 | 838.2 | 784.8 | 808.7 | 868.4 | 750.9 | 792.5 | 603.6 | 742.7 | 765.3 | 728.2 | 41.6 | 120.3 | 144.7 | 79.6 | 268 | 259.1 | 105.3 | 213.3
652 | 500 | 371.9 | 148.76 | 173.8919 | 245.7 | 255.7 | 263.1 | 253.3 | 445.5 | 37.7 | 20.4 | 65.8 | 3.1 | 209.3 | 5.2 | 837.4 | 783.2 | 807.5 | 868.1 | 754.1 | 793.8 | 604.6 | 743 | 766.8 | 729.3 | 41.7 | 120.6 | 144.8 | 79.8 | 268.5 | 259.5 | 105.5 | 213.5
653 | 501 | 371.5 | 148.6 | 173.7048 | 246.7 | 255 | 263 | 253.4 | 444.9 | 37.7 | 20.4 | 65.8 | 3.1 | 194.2 | 5.4 | 837.3 | 782.7 | 808.3 | 867.8 | 756.5 | 792.6 | 604.8 | 746.9 | 767.2 | 729.8 | 41.8 | 120.8 | 145.1 | 80 | 268.6 | 259.7 | 105.8 | 213.7
654 | 502 | 372 | 148.8 | 173.9386 | 246.7 | 254.3 | 263.2 | 253.9 | 444.5 | 37.7 | 20.4 | 65.8 | 3 | 200.5 | 5.4 | 837.4 | 781.1 | 807.4 | 867.3 | 755.7 | 791 | 604.1 | 757 | 766.8 | 729.5 | 41.9 | 121.1 | 145.5 | 80.2 | 268.6 | 259.4 | 106 | 213.9
655 | 503 | 371.3 | 148.52 | 173.6113 | 247.1 | 254.6 | 263.1 | 254 | 450.2 | 37.7 | 20.4 | 65.8 | 3.4 | 206.3 | 5.8 | 837.8 | 781.3 | 808.9 | 867.2 | 755.5 | 790.7 | 601.4 | 764.9 | 766.3 | 729.3 | 42 | 121.3 | 145.7 | 80.4 | 268.7 | 259.4 | 106.2 | 214
656 | 504 | 371.3 | 148.52 | 173.6113 | 247.2 | 255 | 263.3 | 253.7 | 454.8 | 37.7 | 20.4 | 65.9 | 3.7 | 199.1 | 6 | 838 | 781.6 | 810.4 | 867.2 | 757.7 | 791.4 | 599.9 | 760.9 | 767 | 730.2 | 42.2 | 121.6 | 146 | 80.6 | 269.5 | 259.2 | 106.4 | 214.2
657 | 505 | 371.7 | 148.68 | 173.7984 | 246.7 | 256.2 | 263.4 | 254.2 | 454.2 | 37.8 | 20.4 | 65.9 | 3.9 | 190.6 | 6.7 | 837.8 | 781.6 | 810 | 867.5 | 759.7 | 790.7 | 603.5 | 760.1 | 767.8 | 731.8 | 42.3 | 121.8 | 146.1 | 80.7 | 269.6 | 259.6 | 106.6 | 214.5
658 | 506 | 371.6 | 148.64 | 173.7516 | 246.3 | 257.1 | 263.5 | 255.2 | 456.9 | 37.7 | 20.4 | 66 | 3.7 | 200.2 | 6.6 | 837.6 | 782.4 | 809 | 867.1 | 761.5 | 789.7 | 609.9 | 760 | 768.9 | 733.7 | 42.4 | 122.1 | 146.3 | 80.9 | 269.9 | 259.5 | 106.8 | 214.8
659 | 507 | 371.8 | 148.72 | 173.8451 | 245.8 | 257.7 | 263.6 | 255.4 | 461.6 | 37.9 | 20.4 | 66 | 3.5 | 196.2 | 6.7 | 837.5 | 782.3 | 808.1 | 865.9 | 759.5 | 789.4 | 612.3 | 755.4 | 769.7 | 732.5 | 42.5 | 122.3 | 146.6 | 81.1 | 270.1 | 259.5 | 107 | 215
660 | 508 | 372.5 | 149 | 174.1724 | 245.9 | 258.3 | 263.9 | 255.7 | 456 | 38 | 20.4 | 66.1 | 3.5 | 202.6 | 7.2 | 838 | 783.4 | 808.3 | 865.6 | 758.7 | 789.7 | 611.6 | 753.8 | 770.4 | 732.1 | 42.6 | 122.5 | 146.8 | 81.3 | 270.1 | 259.7 | 107.2 | 215.2
661 | 509 | 370.9 | 148.36 | 173.4243 | 247 | 258.6 | 264.4 | 256.1 | 456.9 | 38.2 | 20.4 | 66.1 | 3.3 | 199.4 | 7 | 838.5 | 783.4 | 808.6 | 866 | 759.3 | 789.3 | 610 | 753.3 | 770.8 | 732.2 | 42.7 | 122.7 | 147 | 81.5 | 270.5 | 260.1 | 107.4 | 215.4
662 | 510 | 371.6 | 148.64 | 173.7516 | 248.1 | 257.6 | 264.5 | 256.2 | 457.6 | 38.2 | 20.4 | 66.2 | 3.5 | 202.2 | 6.7 | 838.7 | 784.1 | 808.8 | 866.6 | 760.1 | 788.7 | 610.4 | 752.8 | 771 | 732.9 | 42.8 | 123 | 147.2 | 81.6 | 270.8 | 260.4 | 107.6 | 215.7
663 | 511 | 371.8 | 148.72 | 173.8451 | 249 | 257.3 | 265 | 256.3 | 457.1 | 38.2 | 20.4 | 66.2 | 3.2 | 200.7 | 6.6 | 838.3 | 784.9 | 808.8 | 866.9 | 759.9 | 788.2 | 612 | 746.7 | 771.2 | 733.1 | 42.9 | 123.2 | 147.5 | 81.8 | 270.6 | 261.1 | 107.8 | 216
664 | 512 | 371.3 | 148.52 | 173.6113 | 248.3 | 258.2 | 265 | 255.8 | 450.5 | 38.2 | 20.4 | 66.2 | 3.4 | 212 | 6.1 | 837.8 | 786.8 | 806.5 | 866.3 | 757.5 | 788.5 | 612.2 | 731.4 | 770.9 | 732.2 | 43 | 123.4 | 147.8 | 82 | 270.7 | 261.7 | 108 | 216.2
665 | 513 | 371.9 | 148.76 | 173.8919 | 248.1 | 258.9 | 265.3 | 255.3 | 448.6 | 38.2 | 20.4 | 66.3 | 3.5 | 222.3 | 5.8 | 837.1 | 788.7 | 805.7 | 864.9 | 756.6 | 789.3 | 612.6 | 721.2 | 771.1 | 730.4 | 43.1 | 123.7 | 148.2 | 82.2 | 270.9 | 262.3 | 108.2 | 216.5
666 | 514 | 371.1 | 148.44 | 173.5178 | 248.8 | 260.1 | 265.9 | 255.7 | 445.4 | 38.1 | 20.4 | 66.3 | 3.4 | 220 | 5.5 | 837.2 | 786.7 | 806.1 | 865.5 | 758.1 | 789.8 | 610.9 | 722.8 | 771.7 | 731.6 | 43.2 | 123.9 | 148.3 | 82.4 | 270.8 | 262.6 | 108.4 | 216.7
667 | 515 | 371.6 | 148.64 | 173.7516 | 249.4 | 259.8 | 266.5 | 256.1 | 443.9 | 38.1 | 20.4 | 66.3 | 3.2 | 214.9 | 6.4 | 837.6 | 785.3 | 805.6 | 865.8 | 756 | 790.6 | 609.2 | 722.3 | 771.9 | 731.1 | 43.4 | 124.1 | 148.4 | 82.5 | 270.5 | 262.7 | 108.7 | 216.9
668 | 516 | 371.5 | 148.6 | 173.7048 | 249.4 | 259.7 | 266.7 | 256.3 | 445.8 | 38.3 | 20.4 | 66.3 | 2.8 | 206.6 | 8.3 | 838 | 785.9 | 805.2 | 865.4 | 754.1 | 790.2 | 607.7 | 735.5 | 772.1 | 731.2 | 43.5 | 124.3 | 148.7 | 82.7 | 270.6 | 262.1 | 108.8 | 217
669 | 517 | 372 | 148.8 | 173.9386 | 249.8 | 258.8 | 266.6 | 256.2 | 452.8 | 38.4 | 20.4 | 66.3 | 2.9 | 202.3 | 10.2 | 838.3 | 786.4 | 805.6 | 864.9 | 754.2 | 790.9 | 605.8 | 742.8 | 773.1 | 731 | 43.6 | 124.6 | 149.2 | 82.9 | 270.7 | 261.6 | 109 | 217.1
670 | 518 | 371.9 | 148.76 | 173.8919 | 250 | 258.1 | 266.7 | 256.4 | 457.5 | 38.4 | 20.4 | 66.3 | 3.1 | 197 | 10.7 | 839.5 | 787 | 806.3 | 864.8 | 754.1 | 792.3 | 602.8 | 750.6 | 774.3 | 730.9 | 43.7 | 124.8 | 149.4 | 83.1 | 271.3 | 261.4 | 109.2 | 217.2
671 | 519 | 371.1 | 148.44 | 173.5178 | 249.6 | 258.3 | 266.4 | 256.8 | 457.9 | 38.3 | 20.4 | 66.4 | 3.7 | 197.8 | 10.1 | 840.6 | 786 | 806.4 | 865.8 | 753.1 | 794 | 599.2 | 747.4 | 774.2 | 728.7 | 43.8 | 125 | 149.5 | 83.3 | 271.6 | 261.4 | 109.4 | 217.3
672 | 520 | 370.3 | 148.12 | 173.1437 | 250.2 | 258.8 | 266.2 | 257.4 | 459.6 | 38.3 | 20.4 | 66.5 | 3.7 | 202.1 | 9.5 | 841.8 | 784.7 | 807.8 | 866.5 | 753.6 | 795.9 | 597.8 | 749.8 | 775.2 | 729 | 43.9 | 125.2 | 149.8 | 83.4 | 271.5 | 261.7 | 109.6 | 217.6
673 | 521 | 370.8 | 148.32 | 173.3775 | 249.9 | 259.5 | 266.1 | 257.3 | 456.6 | 38.3 | 20.4 | 66.5 | 3.4 | 189.4 | 9.1 | 841.5 | 783.8 | 804.3 | 866.7 | 751.3 | 796.5 | 601.3 | 735.1 | 775.6 | 727.8 | 44 | 125.4 | 149.9 | 83.6 | 271.8 | 262.2 | 109.8 | 217.9
674 | 522 | 370.8 | 148.32 | 173.3775 | 249.7 | 260.1 | 265.9 | 257.4 | 450 | 38.4 | 20.4 | 66.6 | 3.4 | 189.6 | 8.5 | 841.8 | 783 | 802.4 | 866.8 | 748.4 | 797.5 | 602.3 | 723.9 | 776 | 726.3 | 44.1 | 125.5 | 150.1 | 83.8 | 271.4 | 262.7 | 110 | 218.1
675 | 523 | 369.5 | 147.8 | 172.7697 | 249.7 | 260.3 | 265.8 | 257.7 | 447.1 | 38.4 | 20.4 | 66.6 | 3.2 | 182.9 | 8 | 842.3 | 782.1 | 802.9 | 867.3 | 749 | 797 | 602.8 | 728 | 777.4 | 726.8 | 44.2 | 125.7 | 150.3 | 84 | 271.4 | 262.9 | 110.2 | 218.3
676 | 524 | 370.4 | 148.16 | 173.1905 | 249.1 | 259.8 | 266.3 | 257.8 | 450.5 | 38.5 | 20.4 | 66.7 | 3.5 | 188.4 | 7.4 | 842.7 | 781.2 | 802.7 | 866.9 | 747.1 | 795.8 | 601.6 | 746.4 | 777.7 | 727.2 | 44.3 | 125.9 | 150.6 | 84.2 | 271.3 | 262.6 | 110.4 | 218.5
677 | 525 | 371.4 | 148.56 | 173.6581 | 250 | 259.2 | 266.5 | 257.6 | 458.5 | 38.6 | 20.4 | 66.8 | 3.3 | 192 | 7 | 843.7 | 783.4 | 802.3 | 867.1 | 745.5 | 795.1 | 605.2 | 749.7 | 777.7 | 727.3 | 44.4 | 126.1 | 150.8 | 84.3 | 271.3 | 262.5 | 110.6 | 218.7
678 | 526 | 371.1 | 148.44 | 173.5178 | 250.7 | 259.7 | 266.4 | 257.3 | 455.9 | 38.6 | 20.4 | 66.8 | 3.6 | 185.5 | 6.2 | 844.3 | 784.3 | 803.1 | 867.2 | 745.5 | 794.7 | 605.9 | 745.7 | 777.9 | 728.1 | 44.6 | 126.3 | 151 | 84.5 | 271.5 | 262.3 | 110.8 | 218.9
679 | 527 | 371 | 148.4 | 173.471 | 250.7 | 259.8 | 266.6 | 257.1 | 448.9 | 38.7 | 20.4 | 66.8 | 3.3 | 196.1 | 6.2 | 844.4 | 785.1 | 803.3 | 867.4 | 749.6 | 793.9 | 606.7 | 750.8 | 778.4 | 728.8 | 44.7 | 126.5 | 151.2 | 84.7 | 271.7 | 262.1 | 111 | 219.2
680 | 528 | 371.2 | 148.48 | 173.5646 | 250.7 | 259.2 | 266.4 | 257.2 | 454.1 | 38.8 | 20.4 | 66.7 | 3.5 | 200.8 | 7 | 844.7 | 785.9 | 804 | 866.9 | 752.7 | 792.6 | 607.7 | 762.4 | 779.2 | 730.2 | 44.8 | 126.7 | 151.4 | 84.9 | 271.9 | 262.1 | 111.2 | 219.3
681 | 529 | 371.1 | 148.44 | 173.5178 | 250.7 | 259.3 | 266.2 | 257.1 | 455.5 | 38.8 | 20.4 | 66.7 | 3.8 | 183.9 | 7 | 844 | 785.5 | 801.8 | 866.3 | 752.4 | 792.1 | 608.2 | 748.6 | 779.2 | 730.1 | 44.9 | 126.9 | 151.6 | 85 | 272.6 | 262.2 | 111.4 | 219.5
682 | 530 | 371.7 | 148.68 | 173.7984 | 250.7 | 260 | 266.1 | 257 | 452 | 38.9 | 20.4 | 66.7 | 3.4 | 209.2 | 7.1 | 843.4 | 784.4 | 799.8 | 865.4 | 749.3 | 792.6 | 608.4 | 736.3 | 778.1 | 727.7 | 45 | 127.1 | 151.8 | 85.2 | 272.7 | 262.7 | 111.6 | 219.8
683 | 531 | 370.7 | 148.28 | 173.3308 | 250.2 | 260.2 | 266 | 257 | 444.5 | 39 | 20.4 | 66.7 | 3.5 | 193.4 | 7 | 843.4 | 784.8 | 798.4 | 865.7 | 749.9 | 793.8 | 610.8 | 730.2 | 778.1 | 728 | 45.1 | 127.3 | 152.2 | 85.4 | 272.4 | 263.3 | 111.8 | 220.1
684 | 532 | 371.1 | 148.44 | 173.5178 | 248.9 | 260.4 | 266.1 | 257 | 440.6 | 39 | 20.4 | 66.7 | 3.5 | 197.4 | 6.7 | 843.7 | 783.3 | 798 | 864.4 | 747 | 795.1 | 609.2 | 724.9 | 777.8 | 725.3 | 45.2 | 127.5 | 152.6 | 85.6 | 272.5 | 263.3 | 112 | 220.3
685 | 533 | 371.7 | 148.68 | 173.7984 | 248.6 | 261.5 | 266.3 | 256.8 | 437.4 | 39.1 | 20.4 | 66.7 | 3.2 | 225 | 6.5 | 844.2 | 781.3 | 798.5 | 863.8 | 748.2 | 796.6 | 606.7 | 727.6 | 778.1 | 724 | 45.3 | 127.7 | 152.7 | 85.8 | 272.7 | 263.4 | 112.2 | 220.5
686 | 534 | 371.7 | 148.68 | 173.7984 | 249.2 | 262 | 266.8 | 256.9 | 437.3 | 39.1 | 20.3 | 66.9 | 3.5 | 208.3 | 6.5 | 845.1 | 780 | 798.6 | 863.1 | 747.1 | 797.4 | 608.2 | 733.8 | 779.5 | 724.7 | 45.4 | 127.9 | 152.8 | 85.9 | 273.1 | 263.4 | 112.4 | 220.7
687 | 535 | 371.4 | 148.56 | 173.6581 | 250 | 261.6 | 266.9 | 256.9 | 443 | 39.2 | 20.3 | 67 | 3.3 | 185.7 | 6.5 | 845.8 | 780.5 | 799.4 | 864 | 752.6 | 797.1 | 609.6 | 744.4 | 780.6 | 725.7 | 45.6 | 128.1 | 153.2 | 86.1 | 273.6 | 263.3 | 112.6 | 220.9
688 | 536 | 372.2 | 148.88 | 174.0321 | 250.5 | 260.9 | 267 | 257 | 447.6 | 39.2 | 20.3 | 67.2 | 3.1 | 204 | 7 | 845.8 | 780.1 | 800.8 | 863.3 | 756.3 | 797.2 | 610.5 | 754.5 | 781.4 | 727.2 | 45.7 | 128.3 | 153.6 | 86.3 | 274 | 263.1 | 112.8 | 221
689 | 537 | 371.2 | 148.48 | 173.5646 | 251.5 | 259.7 | 267 | 257.1 | 451.4 | 39.3 | 20.3 | 67.3 | 3.4 | 182.1 | 7.3 | 845.8 | 778.3 | 800.9 | 862.7 | 758.3 | 796.9 | 611 | 768.2 | 782.5 | 727.7 | 45.8 | 128.6 | 153.8 | 86.5 | 274.6 | 263 | 113 | 221.2
690 | 538 | 371.7 | 148.68 | 173.7984 | 252 | 259.4 | 267 | 257.3 | 458 | 39.4 | 20.3 | 67.4 | 3.5 | 193.6 | 7.7 | 845.8 | 777.5 | 800.8 | 861.8 | 757.7 | 795.3 | 610.7 | 775.3 | 782.9 | 729.7 | 45.9 | 128.8 | 154.1 | 86.7 | 275 | 262.9 | 113.1 | 221.3
691 | 539 | 371 | 148.4 | 173.471 | 251.7 | 259.9 | 267.1 | 257.7 | 457.5 | 39.3 | 20.3 | 67.5 | 3.4 | 180.1 | 8.3 | 846.7 | 778.2 | 801.1 | 861.2 | 756 | 794.9 | 608.7 | 772.9 | 782.1 | 729.4 | 46 | 129 | 154.3 | 86.8 | 275.5 | 263.1 | 113.3 | 221.6
692 | 540 | 370.9 | 148.36 | 173.4243 | 251 | 259.7 | 267.5 | 258.4 | 456.7 | 39.3 | 20.3 | 67.6 | 3 | 174 | 8.3 | 847.7 | 777.5 | 803 | 860.8 | 757.3 | 795.3 | 609.3 | 772.5 | 782.6 | 728.1 | 46.2 | 129.2 | 154.5 | 87 | 275.7 | 263 | 113.5 | 221.8
693 | 541 | 371.9 | 148.76 | 173.8919 | 250.8 | 259.8 | 268 | 258.6 | 458 | 39.2 | 20.3 | 67.6 | 3.2 | 190.7 | 8.5 | 848.3 | 777.6 | 802.1 | 860.3 | 756.7 | 795.3 | 610.1 | 765.8 | 782.9 | 728.3 | 46.3 | 129.4 | 154.7 | 87.2 | 275.9 | 263.1 | 113.7 | 222
694 | 542 | 371.3 | 148.52 | 173.6113 | 250.5 | 260.1 | 268 | 258.8 | 453.9 | 39.2 | 20.3 | 67.7 | 2.9 | 191.8 | 7.9 | 848.7 | 777.6 | 801.6 | 859.3 | 758.2 | 795.9 | 610.1 | 759.5 | 782.2 | 727.8 | 46.4 | 129.6 | 154.9 | 87.4 | 276 | 263.4 | 113.9 | 222.2
695 | 543 | 370.6 | 148.24 | 173.284 | 249 | 261 | 268 | 258.8 | 449.5 | 39.2 | 20.3 | 67.8 | 3 | 187.7 | 7.4 | 848.9 | 775 | 799.5 | 857.4 | 754.7 | 797 | 606.9 | 756.7 | 781.4 | 725.2 | 46.5 | 129.9 | 155.1 | 87.6 | 276.1 | 263.6 | 114.1 | 222.6
696 | 544 | 371.8 | 148.72 | 173.8451 | 248.4 | 262.3 | 267.8 | 258.8 | 453.9 | 39.2 | 20.3 | 67.8 | 3.4 | 178.3 | 7.2 | 849.5 | 770.5 | 796.7 | 855.4 | 748.7 | 798.9 | 603.2 | 752.5 | 779.9 | 720.9 | 46.6 | 130.1 | 155.6 | 87.7 | 276.7 | 263.6 | 114.3 | 222.7
697 | 545 | 373 | 149.2 | 174.4062 | 248.6 | 262.9 | 267.8 | 258.9 | 457.9 | 39.2 | 20.3 | 67.8 | 3.4 | 195.2 | 7.2 | 850.6 | 769.2 | 798.5 | 855.7 | 748.6 | 799.9 | 603.9 | 753.1 | 780.2 | 720.9 | 46.7 | 130.3 | 155.9 | 87.9 | 276.7 | 263.4 | 114.5 | 222.9
698 | 546 | 373.4 | 149.36 | 174.5932 | 248.6 | 262.7 | 267.6 | 259.1 | 454.2 | 39.3 | 20.3 | 67.9 | 3.5 | 198.8 | 7.7 | 851.3 | 769.1 | 800.6 | 857 | 750.8 | 799.8 | 604.7 | 752.1 | 781.2 | 721.2 | 46.8 | 130.5 | 156 | 88.1 | 276.6 | 263.3 | 114.6 | 223
699 | 547 | 372.5 | 149 | 174.1724 | 249.8 | 262.4 | 267.7 | 259.2 | 454.4 | 39.4 | 20.3 | 68 | 2.8 | 192.3 | 7.8 | 850.7 | 768.6 | 800 | 857.7 | 750.6 | 798.5 | 607.2 | 747.1 | 782.2 | 720.8 | 46.9 | 130.8 | 156.2 | 88.3 | 276.4 | 263.6 | 114.8 | 223.2
700 | 548 | 372.3 | 148.92 | 174.0789 | 250.5 | 262.6 | 267.3 | 258.9 | 453.2 | 39.6 | 20.3 | 68.1 | 3 | 198 | 8 | 850.6 | 769.6 | 800.6 | 858 | 753.4 | 796.9 | 608.9 | 757.4 | 782.8 | 721.8 | 47.1 | 131 | 156.4 | 88.4 | 276.4 | 264 | 115 | 223.5
701 | 549 | 372.3 | 148.92 | 174.0789 | 250.7 | 263 | 267 | 258.5 | 457.8 | 39.7 | 20.3 | 68.2 | 2.9 | 195.8 | 7.8 | 850.3 | 770.5 | 801.3 | 858.3 | 754.4 | 796.2 | 610.4 | 759.3 | 783.2 | 723.4 | 47.2 | 131.2 | 156.8 | 88.6 | 276.5 | 263.8 | 115.2 | 223.7
702 | 550 | 372.6 | 149.04 | 174.2192 | 250.5 | 263.2 | 266.8 | 258.4 | 454.2 | 39.6 | 20.3 | 68.2 | 3 | 199.9 | 7.6 | 849.7 | 770.5 | 801.8 | 858.5 | 755 | 796.3 | 612.1 | 758.4 | 783.9 | 724.8 | 47.3 | 131.4 | 157 | 88.8 | 276.4 | 264.1 | 115.4 | 223.9
703 | 551 | 372.3 | 148.92 | 174.0789 | 250 | 263.5 | 266.9 | 258.6 | 450 | 39.6 | 20.3 | 68.3 | 3 | 198.6 | 7.4 | 848.6 | 770.6 | 799.4 | 858.1 | 751.3 | 795.8 | 615.3 | 744.2 | 783.8 | 723.5 | 47.4 | 131.6 | 157.3 | 88.9 | 276.4 | 264.2 | 115.6 | 224.1
704 | 552 | 372.3 | 148.92 | 174.0789 | 249.9 | 263.8 | 267.3 | 258.6 | 446 | 39.6 | 20.3 | 68.3 | 3.4 | 197.8 | 7.4 | 848 | 770.4 | 798.7 | 857.8 | 749.9 | 796.3 | 618.8 | 739 | 783.9 | 721.9 | 47.5 | 131.8 | 157.5 | 89.1 | 276.5 | 264.6 | 115.8 | 224.3
705 | 553 | 371.3 | 148.52 | 173.6113 | 250.2 | 264 | 267.8 | 258.2 | 446.3 | 39.7 | 20.3 | 68.3 | 2.9 | 196.3 | 7.3 | 848.3 | 770.9 | 798.9 | 859 | 750.8 | 795.2 | 619.9 | 747.7 | 784 | 721.6 | 47.6 | 132 | 157.7 | 89.3 | 276.9 | 265.2 | 116 | 224.5
706 | 554 | 372.2 | 148.88 | 174.0321 | 250.6 | 263.8 | 268 | 258.1 | 450.7 | 39.7 | 20.3 | 68.3 | 3.1 | 196.1 | 7.2 | 848.2 | 771.3 | 798.2 | 859.2 | 750.3 | 793.8 | 621.2 | 747.2 | 784.2 | 721.8 | 47.7 | 132.2 | 157.8 | 89.5 | 276.6 | 265.4 | 116.1 | 224.7
707 | 555 | 371.9 | 148.76 | 173.8919 | 250.7 | 264.5 | 267.8 | 257.9 | 447.3 | 39.7 | 20.3 | 68.4 | 2.8 | 197.9 | 7.2 | 848.1 | 770.9 | 797.5 | 859.2 | 749.3 | 793 | 620.3 | 749 | 784.1 | 721.8 | 47.9 | 132.3 | 157.9 | 89.7 | 276.5 | 265.1 | 116.4 | 224.8
708 | 556 | 372 | 148.8 | 173.9386 | 250 | 264.2 | 267.9 | 257.6 | 450 | 39.7 | 20.3 | 68.4 | 3.2 | 211.8 | 6.9 | 848.8 | 770.7 | 796.9 | 859.2 | 748.2 | 793.8 | 617.9 | 759.6 | 783.1 | 720.4 | 48 | 132.5 | 158.2 | 89.8 | 276.5 | 264.9 | 116.5 | 224.9
709 | 557 | 371.7 | 148.68 | 173.7984 | 250.3 | 263.6 | 267.8 | 257.5 | 464.5 | 39.8 | 20.3 | 68.4 | 3.2 | 214 | 6.6 | 849.8 | 769.3 | 794.3 | 858.3 | 743.6 | 795 | 613.7 | 762.3 | 781.9 | 717.4 | 48.1 | 132.7 | 158.5 | 90 | 276.8 | 264.9 | 116.7 | 225
710 | 558 | 372.3 | 148.92 | 174.0789 | 251.1 | 263.2 | 268.1 | 257.8 | 478.8 | 39.9 | 20.3 | 68.4 | 3.1 | 214.5 | 5.9 | 851.3 | 767.8 | 795.8 | 857 | 741.5 | 796.3 | 616 | 769 | 781.1 | 715 | 48.2 | 132.8 | 158.8 | 90.2 | 277 | 264.7 | 116.9 | 225.2
711 | 559 | 371.1 | 148.44 | 173.5178 | 251.2 | 263.6 | 268.5 | 258.2 | 491.6 | 40 | 20.3 | 68.5 | 3.1 | 222.4 | 5.8 | 852 | 767.4 | 797.2 | 857.4 | 743.9 | 796.7 | 621.9 | 765.9 | 782 | 715.2 | 48.3 | 133 | 159.1 | 90.4 | 277.1 | 264.6 | 117.1 | 225.4
712 | 560 | 371 | 148.4 | 173.471 | 251.2 | 262.9 | 268.3 | 258.7 | 489.3 | 40.2 | 20.3 | 68.5 | 3.4 | 224.9 | 5.6 | 853 | 768 | 797 | 858.3 | 741.5 | 796.5 | 620.5 | 772.4 | 782.7 | 715.4 | 48.4 | 133.2 | 159.4 | 90.5 | 277 | 264.6 | 117.3 | 225.6
713 | 561 | 371.1 | 148.44 | 173.5178 | 251.4 | 261.5 | 267.8 | 259.1 | 499 | 40.3 | 20.3 | 68.6 | 3.5 | 218.5 | 5.6 | 854.1 | 766.8 | 798.8 | 857.9 | 739.5 | 797.3 | 618.6 | 777.5 | 781.6 | 713.2 | 48.5 | 133.4 | 159.6 | 90.7 | 277 | 265 | 117.5 | 225.7
714 | 562 | 371.6 | 148.64 | 173.7516 | 250.7 | 260.3 | 267.4 | 259.1 | 504.8 | 40.3 | 20.3 | 68.6 | 3.6 | 203.4 | 6.2 | 854.9 | 766.7 | 801.5 | 857.4 | 744 | 797.3 | 619.2 | 785 | 782.2 | 714.5 | 48.7 | 133.6 | 159.9 | 90.9 | 277.3 | 265.1 | 117.7 | 225.9
715 | 563 | 371.1 | 148.44 | 173.5178 | 249.6 | 260.8 | 267.1 | 259.5 | 511.9 | 40.3 | 20.2 | 68.7 | 3.8 | 191.1 | 6.8 | 855.6 | 765.9 | 802.8 | 856.4 | 745 | 797.3 | 617.8 | 789.5 | 781.4 | 714.2 | 48.8 | 133.8 | 160.2 | 91 | 277.8 | 264.9 | 117.8 | 226
716 | 564 | 372.7 | 149.08 | 174.2659 | 250.4 | 261.6 | 266.6 | 260.2 | 511.9 | 40.3 | 20.3 | 68.8 | 3.3 | 193.3 | 7.2 | 856.9 | 765.4 | 802.3 | 856 | 745.7 | 798.5 | 616.7 | 790.6 | 781 | 714 | 48.9 | 134 | 160.4 | 91.2 | 277.7 | 265 | 118.1 | 226.2
717 | 565 | 372.9 | 149.16 | 174.3594 | 250.8 | 262.2 | 266.3 | 260.9 | 507.3 | 40.3 | 20.2 | 68.8 | 3.5 | 196.2 | 7.2 | 857.6 | 766.3 | 801.6 | 856.4 | 744.7 | 798.2 | 619.6 | 789.1 | 783.2 | 716 | 49 | 134.2 | 160.5 | 91.4 | 277.8 | 265.2 | 118.2 | 226.4
718 | 566 | 370.8 | 148.32 | 173.3775 | 251.2 | 262.6 | 266.1 | 261.6 | 505.1 | 40.3 | 20.2 | 68.8 | 3.4 | 190.7 | 7.1 | 858.2 | 766.3 | 801.3 | 855.2 | 743.4 | 797.5 | 618.5 | 790.2 | 783.3 | 715.5 | 49.1 | 134.4 | 160.8 | 91.6 | 277.8 | 265.7 | 118.4 | 226.6
719 | 567 | 372.5 | 149 | 174.1724 | 251.4 | 262.9 | 265.5 | 261.8 | 520.5 | 40.4 | 20.2 | 68.8 | 3.3 | 197 | 6.5 | 858.8 | 763.2 | 799.8 | 853 | 739.1 | 798.6 | 617.2 | 788.2 | 781.7 | 713.5 | 49.2 | 134.6 | 161.4 | 91.7 | 278.1 | 266.1 | 118.6 | 226.8
720 | 568 | 371.6 | 148.64 | 173.7516 | 251 | 263.1 | 265.7 | 261.6 | 523.5 | 40.3 | 20.2 | 68.9 | 3 | 208.2 | 5.8 | 859.5 | 760.7 | 798.6 | 850.9 | 734.7 | 800 | 618.8 | 779.8 | 781 | 710.8 | 49.4 | 134.8 | 161.8 | 91.9 | 278.4 | 266.4 | 118.8 | 226.9
721 | 569 | 372.6 | 149.04 | 174.2192 | 250.4 | 263.2 | 266.1 | 261.9 | 522.7 | 40.3 | 20.2 | 69 | 3.3 | 200.8 | 5.5 | 860.1 | 761.1 | 798.6 | 851 | 735.6 | 801.2 | 624.1 | 780.1 | 781.7 | 710.3 | 49.5 | 135 | 161.9 | 92.1 | 278.6 | 266.6 | 119 | 227.1
722 | 570 | 370.5 | 148.2 | 173.2373 | 249.7 | 263 | 266.3 | 262.8 | 524.5 | 40.4 | 20.2 | 69 | 3.1 | 192.6 | 5.3 | 860 | 761.5 | 796.9 | 851.7 | 735.2 | 801.5 | 622.8 | 780.4 | 782.3 | 711.1 | 49.6 | 135.3 | 162.1 | 92.3 | 278.8 | 266.7 | 119.2 | 227.3
723 | 571 | 369.6 | 147.84 | 172.8164 | 249.8 | 262.6 | 266.2 | 263.5 | 516.1 | 40.6 | 20.2 | 69 | 3.4 | 197.9 | 5.5 | 859.7 | 760.1 | 794.8 | 851.2 | 732 | 802.5 | 621.8 | 771.5 | 782 | 709 | 49.7 | 135.5 | 162.4 | 92.4 | 279.2 | 266.9 | 119.4 | 227.5
724 | 572 | 370.4 | 148.16 | 173.1905 | 249.9 | 262 | 265.7 | 263.8 | 508.5 | 40.7 | 20.2 | 69.1 | 3.9 | 203.3 | 5.8 | 859.6 | 757.8 | 792.8 | 849.2 | 728.7 | 803.6 | 619.4 | 766.6 | 780.6 | 706.9 | 49.8 | 135.7 | 162.6 | 92.6 | 279.5 | 267 | 119.6 | 227.7
725 | 573 | 369.8 | 147.92 | 172.91 | 251.8 | 262.8 | 265.8 | 264 | 506.2 | 40.6 | 20.2 | 69.2 | 3.4 | 196.7 | 5.7 | 859.3 | 753 | 791.1 | 847.3 | 724.6 | 805.7 | 624.5 | 758.8 | 779.1 | 702.9 | 49.9 | 135.9 | 163 | 92.8 | 280.5 | 266.9 | 119.7 | 227.8
726 | 574 | 371.4 | 148.56 | 173.6581 | 253 | 263.7 | 266.1 | 264.4 | 501.9 | 40.6 | 20.2 | 69.2 | 3.6 | 194 | 6.1 | 859.2 | 749.6 | 789.4 | 845.6 | 723.4 | 807.4 | 624 | 756.2 | 779.1 | 701 | 50.1 | 136.2 | 163.4 | 92.9 | 280.8 | 266.7 | 119.9 | 228
727 | 575 | 372.6 | 149.04 | 174.2192 | 253.4 | 263.1 | 266.6 | 265 | 493.7 | 40.7 | 20.2 | 69.2 | 3.4 | 198.7 | 6.2 | 858.8 | 746 | 786.6 | 843.3 | 717.8 | 808.7 | 621.6 | 746.3 | 778.6 | 698.4 | 50.2 | 136.4 | 163.6 | 93.1 | 280.8 | 266.8 | 120.1 | 228.2
728 | 576 | 370.4 | 148.16 | 173.1905 | 254.5 | 262.1 | 266.9 | 265.9 | 491 | 40.8 | 20.2 | 69.2 | 3.6 | 192.8 | 6.4 | 858.9 | 742.5 | 786.3 | 841.8 | 714.4 | 810.1 | 628.2 | 747.9 | 778.1 | 696.5 | 50.3 | 136.7 | 163.9 | 93.3 | 281 | 266.7 | 120.3 | 228.3
729 | 577 | 369 | 147.6 | 172.5359 | 256.4 | 262.4 | 267 | 266.4 | 496.8 | 41 | 20.2 | 69.3 | 3.5 | 194.4 | 6.4 | 858.9 | 742 | 786.3 | 842.2 | 712.2 | 811.5 | 634.1 | 749.3 | 778.9 | 694.6 | 50.4 | 137 | 164.4 | 93.4 | 281.3 | 267.2 | 120.5 | 228.5
730 | 578 | 370.7 | 148.28 | 173.3308 | 257.4 | 262.9 | 267.2 | 267 | 493.7 | 41.1 | 20.2 | 69.3 | 3.7 | 194.8 | 6.2 | 858.7 | 742.6 | 787.7 | 842.6 | 711.9 | 811.6 | 635 | 748.7 | 780 | 693.8 | 50.5 | 137.3 | 164.4 | 93.6 | 281.7 | 267.2 | 120.7 | 228.7
731 | 579 | 369.6 | 147.84 | 172.8164 | 258.7 | 262.6 | 267.4 | 267.5 | 485.9 | 41.3 | 20.2 | 69.4 | 3.5 | 194.5 | 6 | 858.4 | 743.2 | 789.9 | 844.4 | 715.2 | 811.4 | 632.1 | 750.3 | 780.3 | 693.3 | 50.7 | 137.7 | 164.5 | 93.8 | 282.2 | 267.4 | 120.9 | 228.9
732 | 580 | 371.3 | 148.52 | 173.6113 | 260 | 263 | 267.5 | 267.3 | 484.1 | 41.4 | 20.2 | 69.4 | 3.2 | 192.4 | 5.6 | 858.3 | 745.6 | 790.8 | 845.7 | 717.6 | 809.8 | 629.1 | 757.4 | 781.7 | 694.5 | 50.8 | 138 | 164.8 | 94 | 282.2 | 267.7 | 121.1 | 229.1
733 | 581 | 371.5 | 148.6 | 173.7048 | 260.3 | 263.5 | 267.1 | 267.2 | 490.5 | 41.6 | 20.2 | 69.5 | 3.2 | 191.9 | 5.1 | 858.4 | 748.6 | 792.3 | 846.4 | 717.8 | 809.1 | 629.2 | 767.6 | 782 | 695.5 | 50.9 | 138.3 | 165 | 94.2 | 282.7 | 268.1 | 121.3 | 229.4
734 | 582 | 370.9 | 148.36 | 173.4243 | 260.6 | 263.4 | 266.8 | 266.8 | 498.7 | 41.6 | 20.2 | 69.5 | 3.2 | 197 | 4.6 | 858.6 | 752.1 | 793.3 | 847.4 | 717.1 | 808.9 | 626 | 773.3 | 782.6 | 696.6 | 51 | 138.6 | 165.2 | 94.3 | 282.6 | 268.1 | 121.5 | 229.6
735 | 583 | 371.4 | 148.56 | 173.6581 | 260.8 | 263 | 267.1 | 266.6 | 490.1 | 41.5 | 20.2 | 69.5 | 3.2 | 193.3 | 3.7 | 858.1 | 752.8 | 790.9 | 847.3 | 714.1 | 808.2 | 625.5 | 767.1 | 783 | 696.7 | 51.1 | 138.9 | 165.3 | 94.5 | 282.8 | 267.9 | 121.6 | 229.6
736 | 584 | 371.4 | 148.56 | 173.6581 | 261.6 | 262.2 | 267.2 | 266.7 | 488.6 | 41.5 | 20.2 | 69.6 | 3.3 | 190.1 | 3.6 | 858.4 | 754.3 | 792.6 | 847.6 | 713.9 | 807.4 | 623.3 | 776.8 | 783.6 | 697.3 | 51.2 | 139.2 | 165.5 | 94.7 | 282.6 | 267.6 | 121.8 | 229.7
737 | 585 | 371.9 | 148.76 | 173.8919 | 262.5 | 261.7 | 267 | 266.5 | 495 | 41.5 | 20.2 | 69.7 | 3.2 | 187 | 4.8 | 858.8 | 758.1 | 794.7 | 848 | 716.1 | 806.6 | 625 | 775.2 | 784.3 | 698.5 | 51.4 | 139.5 | 165.7 | 94.8 | 282.6 | 267.8 | 122 | 229.9
738 | 586 | 372.2 | 148.88 | 174.0321 | 263.4 | 261.7 | 266.9 | 266.3 | 492.4 | 41.5 | 20.2 | 69.8 | 3.3 | 184 | 5.8 | 858.2 | 761.1 | 796.9 | 849.2 | 718.6 | 805.1 | 629.3 | 776 | 786.3 | 700.3 | 51.5 | 139.7 | 165.8 | 95 | 282.3 | 268.3 | 122.2 | 230.2
739 | 587 | 371.5 | 148.6 | 173.7048 | 264.3 | 261.7 | 266.6 | 265.7 | 491.2 | 41.5 | 20.2 | 69.9 | 3 | 182.3 | 5.9 | 857.1 | 763.4 | 797.8 | 850.2 | 721.9 | 803 | 634.6 | 781.2 | 787.8 | 703.8 | 51.6 | 140 | 166.1 | 95.2 | 282 | 268.1 | 122.3 | 230.3
740 | 588 | 372.5 | 149 | 174.1724 | 264.7 | 261.5 | 266 | 264.8 | 489.3 | 41.5 | 20.2 | 69.9 | 2.9 | 186.3 | 6 | 856.6 | 764.1 | 796.6 | 849.6 | 720.5 | 802.5 | 634.5 | 785.8 | 787.4 | 704.1 | 51.7 | 140.2 | 166.4 | 95.4 | 281.8 | 268.1 | 122.5 | 230.4
741 | 589 | 371.4 | 148.56 | 173.6581 | 264.1 | 261.7 | 266.1 | 264.1 | 499.6 | 41.5 | 20.2 | 70 | 2.9 | 179.4 | 6 | 856.3 | 764 | 797.7 | 849.4 | 721.3 | 802.6 | 632.9 | 785.3 | 787.3 | 704.2 | 51.8 | 140.4 | 166.7 | 95.5 | 281.7 | 268.2 | 122.7 | 230.5
742 | 590 | 371.7 | 148.68 | 173.7984 | 264.5 | 262.5 | 266.4 | 264.1 | 486.6 | 41.5 | 20.2 | 70 | 2.9 | 184.3 | 5.8 | 855.8 | 765.5 | 798.9 | 849.3 | 724.1 | 802.1 | 632.8 | 782.8 | 788.1 | 706.3 | 52 | 140.7 | 166.9 | 95.7 | 282.1 | 268.5 | 122.9 | 230.7
743 | 591 | 372 | 148.8 | 173.9386 | 264.7 | 262.1 | 266.4 | 264.2 | 474.1 | 41.6 | 20.2 | 70 | 3.4 | 177.7 | 6.6 | 854.9 | 767.6 | 798.1 | 849.2 | 727.1 | 800.1 | 639.3 | 778.5 | 789.3 | 708.5 | 52.1 | 140.9 | 167.1 | 95.9 | 282.5 | 268.5 | 123.1 | 230.9
744 | 592 | 371.9 | 148.76 | 173.8919 | 265.9 | 261.6 | 266.7 | 264.1 | 466.6 | 41.7 | 20.2 | 70 | 3.6 | 172.8 | 7.2 | 854.3 | 769.6 | 797.9 | 848.8 | 729.3 | 798.4 | 638.2 | 779.4 | 789.3 | 709.5 | 52.2 | 141 | 167.4 | 96 | 282.5 | 268.7 | 123.3 | 231.1
745 | 593 | 372.3 | 148.92 | 174.0789 | 266.4 | 261.8 | 267.4 | 264.3 | 473.7 | 41.9 | 20.2 | 70.1 | 3.4 | 172.6 | 6.9 | 853.8 | 771.5 | 799.8 | 849 | 733.6 | 797.5 | 638.7 | 788.3 | 789.8 | 711.4 | 52.3 | 141.2 | 167.7 | 96.2 | 282.6 | 268.6 | 123.5 | 231.3
746 | 594 | 371.9 | 148.76 | 173.8919 | 266.7 | 262.2 | 267.9 | 264.3 | 474.5 | 41.9 | 20.2 | 70.2 | 3.6 | 176.5 | 6.7 | 853.2 | 773.3 | 800.5 | 848.8 | 735.7 | 797.1 | 639.8 | 785.2 | 790.1 | 713.7 | 52.5 | 141.4 | 167.9 | 96.4 | 282.9 | 268.7 | 123.6 | 231.5
747 | 595 | 371.7 | 148.68 | 173.7984 | 267.1 | 263 | 267.9 | 263.9 | 472.7 | 42 | 20.2 | 70.2 | 3.5 | 162.4 | 7.1 | 852.6 | 773.8 | 800.3 | 848.5 | 737.7 | 796.4 | 641.9 | 777.3 | 790.7 | 714.3 | 52.6 | 141.5 | 168.2 | 96.6 | 283.1 | 268.7 | 123.8 | 231.6
748 | 596 | 374.4 | 149.76 | 175.0608 | 267.5 | 263.5 | 268.2 | 263.6 | 469.7 | 42.1 | 20.2 | 70.2 | 3.6 | 176.1 | 7 | 851.9 | 774.4 | 799.7 | 848.4 | 740.9 | 795.2 | 644.3 | 775.6 | 791.4 | 716 | 52.7 | 141.7 | 168.4 | 96.8 | 283.2 | 268.9 | 124 | 231.8
749 | 597 | 375.5 | 150.2 | 175.5751 | 268 | 263.9 | 268.7 | 263.1 | 466.3 | 42.1 | 20.2 | 70.3 | 3.3 | 167.7 | 7.4 | 851.9 | 776.1 | 800.1 | 847.8 | 741 | 793.8 | 645.3 | 779.8 | 791.4 | 716.3 | 52.8 | 141.8 | 168.6 | 96.9 | 283.2 | 269.7 | 124.2 | 232.1
750 | 598 | 374.1 | 149.64 | 174.9205 | 268.4 | 264.2 | 269.2 | 262.9 | 469.4 | 42.2 | 20.2 | 70.4 | 3.4 | 176.4 | 7.7 | 852.4 | 777.5 | 800 | 847.2 | 740.6 | 792.9 | 645.7 | 779.2 | 791.1 | 716.8 | 53 | 142 | 168.9 | 97.1 | 283.3 | 270.3 | 124.4 | 232.3
751 | 599 | 373.1 | 149.24 | 174.453 | 268.8 | 264.5 | 270 | 262.5 | 479.4 | 42.3 | 20.2 | 70.5 | 3 | 177.7 | 7.6 | 852.4 | 778.2 | 802 | 847.8 | 745.6 | 792.6 | 644.3 | 783.3 | 791.1 | 717.8 | 53.1 | 142.2 | 169.2 | 97.3 | 283.5 | 270.3 | 124.6 | 232.5
752 | 600 | 373 | 149.2 | 174.4062 | 269.5 | 265.1 | 270.4 | 261.8 | 484.9 | 42.3 | 20.2 | 70.6 | 3.1 | 171.2 | 7.9 | 851.9 | 778.2 | 803.1 | 847.6 | 748.8 | 791.7 | 648.2 | 784.4 | 792.2 | 720.9 | 53.2 | 142.4 | 169.5 | 97.5 | 283.6 | 270.4 | 124.8 | 232.7
753 | 601 | 372.9 | 149.16 | 174.3594 | 269.1 | 265.6 | 270.5 | 261.2 | 479.3 | 42.3 | 20.2 | 70.6 | 3.1 | 167.1 | 8.1 | 851.1 | 778.2 | 803.1 | 846.8 | 750.7 | 790.9 | 650.1 | 783.4 | 792.8 | 723 | 53.3 | 142.6 | 169.7 | 97.7 | 283.7 | 270.5 | 125 | 232.9
754 | 602 | 371.2 | 148.48 | 173.5646 | 268.8 | 266.5 | 270.6 | 260.9 | 480.2 | 42.3 | 20.2 | 70.7 | 2.7 | 167.8 | 8 | 850.8 | 779.3 | 803.7 | 846.7 | 752.8 | 790.6 | 650.2 | 785.6 | 793 | 725 | 53.5 | 142.8 | 169.9 | 97.9 | 283.9 | 270.8 | 125.1 | 233
755 | 603 | 371.6 | 148.64 | 173.7516 | 269.4 | 267.2 | 270.9 | 260.7 | 479.9 | 42.2 | 20.2 | 70.8 | 3.1 | 169.6 | 7.8 | 851.1 | 779.2 | 805 | 846.7 | 754 | 790.9 | 650.1 | 786.8 | 792.4 | 724.2 | 53.6 | 143 | 170.2 | 98.1 | 284.2 | 271.2 | 125.3 | 233.2
756 | 604 | 373.6 | 149.44 | 174.6867 | 269.9 | 267 | 271.3 | 260.7 | 485.9 | 42.3 | 20.2 | 70.8 | 2.8 | 166.5 | 8.3 | 851.8 | 778.9 | 805.3 | 846.7 | 755.8 | 790.7 | 645.7 | 789.3 | 792.2 | 724 | 53.7 | 143.2 | 170.5 | 98.2 | 284.5 | 272 | 125.5 | 233.4
757 | 605 | 372 | 148.8 | 173.9386 | 270.2 | 266.6 | 271.9 | 260.6 | 487.3 | 42.3 | 20.2 | 70.8 | 2.4 | 164.9 | 8.5 | 852.3 | 778.2 | 806.2 | 846.4 | 758.2 | 791.5 | 643.2 | 780.7 | 791.7 | 725.2 | 53.8 | 143.5 | 170.6 | 98.4 | 284.5 | 272.5 | 125.7 | 233.6
758 | 606 | 372.2 | 148.88 | 174.0321 | 270.3 | 267.3 | 272.4 | 261 | 479 | 42.3 | 20.2 | 70.8 | 2.5 | 170.9 | 8.1 | 852.3 | 777 | 806 | 845.8 | 759 | 792.8 | 642.5 | 772 | 791.4 | 724.5 | 54 | 143.7 | 170.8 | 98.6 | 284.5 | 272.4 | 125.9 | 233.8
759 | 607 | 373 | 149.2 | 174.4062 | 270.7 | 268.5 | 272.4 | 261.1 | 472.3 | 42.4 | 20.2 | 70.8 | 2.9 | 163.3 | 8.1 | 853.2 | 777 | 807.1 | 846.2 | 755.5 | 793.4 | 641.5 | 772.9 | 791.8 | 723.8 | 54.1 | 143.9 | 171.1 | 98.8 | 284.6 | 272.4 | 126.1 | 233.9
760 | 608 | 373 | 149.2 | 174.4062 | 271.3 | 268.7 | 272.2 | 260.6 | 483.6 | 42.4 | 20.2 | 70.9 | 3.4 | 168.4 | 8.1 | 854.3 | 776.9 | 807.2 | 846.6 | 755.4 | 793.7 | 637.6 | 785.6 | 791.8 | 723.2 | 54.2 | 144.3 | 171.5 | 99 | 284.4 | 272 | 126.2 | 234.1
761 | 609 | 371.8 | 148.72 | 173.8451 | 272.1 | 268.8 | 272.7 | 260.1 | 507.6 | 42.4 | 20.2 | 70.9 | 3.3 | 178.9 | 8.2 | 855.7 | 774.2 | 803.4 | 844.5 | 748.9 | 796.3 | 630.9 | 784 | 790 | 720.5 | 54.4 | 144.7 | 172.1 | 99.2 | 284.6 | 271.8 | 126.4 | 234.1
762 | 610 | 372.7 | 149.08 | 174.2659 | 273 | 268.7 | 273.2 | 259.9 | 507.2 | 42.4 | 20.2 | 71 | 3 | 179.5 | 7.8 | 857.1 | 773.5 | 803.3 | 843.9 | 746.2 | 797.6 | 627.5 | 783.9 | 790.6 | 719.6 | 54.5 | 145.1 | 172.5 | 99.4 | 285.2 | 271.6 | 126.6 | 234.3
763 | 611 | 372.6 | 149.04 | 174.2192 | 274.3 | 268.6 | 273.6 | 260.3 | 511.1 | 42.4 | 20.2 | 71 | 3.2 | 169 | 7.2 | 858.5 | 772.5 | 805 | 843.6 | 747 | 798.5 | 624.7 | 791.1 | 790.3 | 718.7 | 54.6 | 145.4 | 172.7 | 99.6 | 285.9 | 271.6 | 126.8 | 234.5
764 | 612 | 371.4 | 148.56 | 173.6581 | 275.4 | 269.2 | 274.3 | 261.8 | 519.9 | 42.3 | 20.2 | 71.1 | 3 | 165.1 | 6.6 | 859.6 | 770.9 | 804 | 843.2 | 745.4 | 799.7 | 619.3 | 789.6 | 789.5 | 716.8 | 54.7 | 145.8 | 173 | 99.8 | 286.5 | 272.4 | 127 | 234.7
765 | 613 | 371.8 | 148.72 | 173.8451 | 275.7 | 270.6 | 274.4 | 263.7 | 522.5 | 42.3 | 20.2 | 71.1 | 3.4 | 166 | 6 | 860.7 | 768.6 | 802.8 | 842.1 | 741.3 | 801.3 | 614.7 | 791.5 | 788.5 | 716.2 | 54.9 | 146.2 | 173.4 | 100 | 286.9 | 272.5 | 127.2 | 235
766 | 614 | 370.7 | 148.28 | 173.3308 | 275.7 | 271.2 | 274.5 | 265.2 | 521.2 | 42.3 | 20.2 | 71.2 | 3.1 | 173 | 5.6 | 861.5 | 766.5 | 803.3 | 841.4 | 739.6 | 803.1 | 606.8 | 789.9 | 787.7 | 715 | 55 | 146.5 | 173.6 | 100.2 | 287.3 | 273.1 | 127.3 | 235.2
767 | 615 | 370.3 | 148.12 | 173.1437 | 275.9 | 272.1 | 274.8 | 266.6 | 517.9 | 42.3 | 20.2 | 71.2 | 2.9 | 177.9 | 5.4 | 862.3 | 765.4 | 803.1 | 841.5 | 739.8 | 804.7 | 605.9 | 788.1 | 787.8 | 714.4 | 55.1 | 146.8 | 173.8 | 100.4 | 287.6 | 273.4 | 127.5 | 235.4
768 | 616 | 372.1 | 148.84 | 173.9854 | 275.4 | 273.1 | 274.8 | 267.8 | 512.1 | 42.2 | 20.2 | 71.3 | 3.2 | 172.7 | 4.9 | 862.5 | 762.7 | 801.1 | 840.6 | 736 | 806.4 | 602.8 | 778.3 | 786.4 | 711.7 | 55.3 | 147.2 | 174 | 100.6 | 287.7 | 273.8 | 127.7 | 235.7
769 | 617 | 370.3 | 148.12 | 173.1437 | 274.8 | 272.8 | 274.9 | 269 | 500.5 | 42.3 | 20.2 | 71.3 | 3.1 | 178.2 | 4.6 | 863 | 760.7 | 801.6 | 839.9 | 734.1 | 807.3 | 601.6 | 779.8 | 786.6 | 710.6 | 55.4 | 147.5 | 174.3 | 100.8 | 287.8 | 274.5 | 127.9 | 235.9
770 | 618 | 371.6 | 148.64 | 173.7516 | 275.1 | 272.2 | 274.9 | 269.2 | 505.7 | 42.4 | 20.2 | 71.4 | 3.1 | 188.2 | 4.6 | 863.9 | 760.2 | 803.5 | 839.5 | 734.3 | 807.1 | 601.3 | 780.6 | 787 | 710.7 | 55.5 | 147.8 | 174.8 | 101 | 288.2 | 274.8 | 128.1 | 236.1
771 | 619 | 371.5 | 148.6 | 173.7048 | 275.2 | 272.8 | 274.4 | 269.1 | 514.2 | 42.5 | 20.2 | 71.5 | 2.8 | 168.4 | 5.4 | 864.8 | 760.8 | 805 | 839.4 | 734.2 | 807.8 | 599.1 | 786.3 | 787.1 | 710.3 | 55.7 | 148.1 | 175.1 | 101.2 | 288.7 | 275 | 128.3 | 236.2
772 | 620 | 370.7 | 148.28 | 173.3308 | 276 | 274.2 | 274.3 | 269.2 | 514.2 | 42.5 | 20.2 | 71.5 | 3.2 | 180.8 | 5.8 | 865.7 | 764.6 | 805.8 | 840.2 | 735.3 | 808 | 601.6 | 786.7 | 787.9 | 712 | 55.8 | 148.4 | 175.3 | 101.4 | 289.3 | 275.1 | 128.5 | 236.3
773 | 621 | 370.6 | 148.24 | 173.284 | 276.6 | 275.2 | 274.5 | 269.7 | 506.6 | 42.5 | 20.1 | 71.6 | 3 | 178.1 | 5.8 | 866.3 | 767.6 | 805.6 | 840.1 | 732.3 | 808.7 | 602.7 | 787 | 788 | 711.4 | 55.9 | 148.7 | 175.6 | 101.6 | 290.1 | 275.4 | 128.6 | 236.5
774 | 622 | 372.4 | 148.96 | 174.1257 | 277.1 | 275.1 | 275.2 | 270.7 | 503.1 | 42.5 | 20.1 | 71.8 | 2.5 | 164.2 | 6.3 | 866.5 | 770.1 | 807.4 | 840.9 | 733.1 | 808.7 | 606.1 | 790.9 | 789.2 | 713.5 | 56 | 149 | 175.9 | 101.8 | 290.8 | 275.6 | 128.8 | 236.7
775 | 623 | 374.1 | 149.64 | 174.9205 | 277.5 | 275.9 | 276.1 | 271.4 | 508.9 | 42.5 | 20.1 | 71.9 | 2.9 | 177.7 | 6.5 | 866.5 | 772.7 | 809 | 841.4 | 735.1 | 807.2 | 606.8 | 794.9 | 790.7 | 715 | 56.2 | 149.3 | 176.1 | 102 | 291.3 | 275.7 | 129 | 236.9
776 | 624 | 374.9 | 149.96 | 175.2946 | 277.2 | 276.6 | 276.7 | 271.8 | 500.9 | 42.5 | 20.1 | 71.9 | 3.1 | 177.4 | 6.4 | 865.8 | 773.8 | 807.8 | 840.8 | 735.4 | 806.3 | 607 | 787.1 | 790.8 | 715.5 | 56.3 | 149.6 | 176.1 | 102.2 | 291.7 | 276.2 | 129.2 | 237.1
777 | 625 | 373.8 | 149.52 | 174.7803 | 276.6 | 276.5 | 276.6 | 271.7 | 489.4 | 42.5 | 20.1 | 72 | 3.2 | 168.4 | 6.6 | 865.4 | 774 | 805 | 840.2 | 732.5 | 806.3 | 605.9 | 777.2 | 789.5 | 712.9 | 56.4 | 149.9 | 176.1 | 102.4 | 292.6 | 276.7 | 129.4 | 237.3
778 | 626 | 373.2 | 149.28 | 174.4997 | 276.4 | 275.8 | 276.3 | 271.4 | 487.4 | 42.6 | 20.1 | 72 | 3.3 | 171.1 | 6.8 | 864.9 | 775.4 | 802.2 | 839.6 | 730.6 | 805.9 | 604.6 | 775.3 | 788.8 | 711.4 | 56.6 | 150.1 | 176.4 | 102.6 | 292.5 | 276.6 | 129.6 | 237.5
779 | 627 | 372.7 | 149.08 | 174.2659 | 275.5 | 274.9 | 276.5 | 271.2 | 488 | 42.7 | 20.1 | 72 | 3.2 | 179 | 6.6 | 864.7 | 775.5 | 800.1 | 839.4 | 728.5 | 805.4 | 602.6 | 773.8 | 788.1 | 710 | 56.7 | 150.4 | 176.7 | 102.8 | 292.1 | 276.3 | 129.8 | 237.6
780 | 628 | 371.2 | 148.48 | 173.5646 | 274.6 | 274.5 | 276.6 | 271.1 | 484.5 | 42.8 | 20.1 | 72 | 3 | 168.4 | 6.4 | 864.3 | 773.9 | 799.1 | 839.2 | 726.1 | 805.5 | 602.5 | 764.7 | 786.9 | 707.9 | 56.8 | 150.7 | 176.9 | 103 | 291.9 | 276.3 | 129.9 | 237.8
781 | 629 | 372 | 148.8 | 173.9386 | 274.5 | 274.8 | 276.1 | 271 | 475.7 | 42.8 | 20.1 | 72 | 3.1 | 169.3 | 6.8 | 864 | 771.1 | 797.7 | 838.8 | 723.8 | 805.5 | 598.4 | 760.9 | 785.5 | 705 | 57 | 150.9 | 177.2 | 103.2 | 291.6 | 276.2 | 130.1 | 237.9
782 | 630 | 371.5 | 148.6 | 173.7048 | 274.5 | 275.5 | 275.3 | 270.8 | 472.4 | 42.8 | 20.1 | 72 | 3.5 | 175.3 | 7.5 | 864.4 | 771.5 | 798.5 | 838.6 | 724.8 | 805.5 | 597 | 769 | 785.1 | 705.5 | 57.1 | 151.2 | 177.4 | 103.4 | 291.5 | 275.7 | 130.3 | 238
783 | 631 | 372.9 | 149.16 | 174.3594 | 274.5 | 275 | 275 | 270.7 | 479.9 | 42.8 | 20.1 | 72.1 | 3.7 | 178.4 | 7.7 | 864.5 | 773.3 | 799.3 | 839.1 | 725.3 | 804.9 | 597.1 | 773.4 | 785.5 | 705.6 | 57.2 | 151.4 | 177.6 | 103.7 | 291.4 | 275.5 | 130.4 | 238.2
784 | 632 | 371.7 | 148.68 | 173.7984 | 273.7 | 274.7 | 275 | 271.1 | 487 | 42.8 | 20.1 | 72.2 | 3.2 | 173 | 7.5 | 864.3 | 775.8 | 801.3 | 839.8 | 727.8 | 803 | 600.5 | 783.1 | 786.5 | 707.5 | 57.4 | 151.7 | 177.8 | 103.9 | 291.2 | 275.1 | 130.6 | 238.2
785 | 633 | 372.8 | 149.12 | 174.3127 | 273.6 | 274.9 | 274.6 | 271.7 | 496.3 | 42.8 | 20.1 | 72.3 | 2.8 | 162.4 | 6.8 | 864.3 | 777.4 | 804 | 840.3 | 732.2 | 801.9 | 600.4 | 792 | 786.6 | 709.4 | 57.5 | 151.9 | 178.1 | 104.1 | 291 | 275.2 | 130.8 | 238.3
786 | 634 | 372.2 | 148.88 | 174.0321 | 274.2 | 275.2 | 273.9 | 271.9 | 505.9 | 42.8 | 20.1 | 72.4 | 3.1 | 168.4 | 6.3 | 864.3 | 778.7 | 806.4 | 840 | 735.8 | 801.1 | 598.8 | 795.7 | 787.2 | 711.5 | 57.6 | 152.2 | 178.3 | 104.3 | 291 | 275.2 | 131 | 238.5
787 | 635 | 371.9 | 148.76 | 173.8919 | 274.3 | 275.5 | 273.4 | 272.2 | 508.2 | 42.9 | 20.1 | 72.6 | 3 | 172.8 | 6.1 | 864 | 779.8 | 807.7 | 839.4 | 737.7 | 800 | 599 | 799.9 | 787.8 | 712.2 | 57.8 | 152.4 | 178.6 | 104.5 | 291.3 | 275.5 | 131.2 | 238.6
788 | 636 | 371.8 | 148.72 | 173.8451 | 274.1 | 275.8 | 272.8 | 272.3 | 508.7 | 43 | 20.1 | 72.7 | 2.9 | 172.6 | 6.1 | 864 | 780.2 | 808.5 | 838.6 | 740.8 | 799.1 | 597.6 | 804.4 | 788.1 | 714.3 | 57.9 | 152.7 | 178.9 | 104.7 | 291.5 | 275.3 | 131.4 | 238.7
789 | 637 | 371.7 | 148.68 | 173.7984 | 273.8 | 275.8 | 272.8 | 272.4 | 513.8 | 43.1 | 20.1 | 72.7 | 2.9 | 173 | 6.3 | 864.1 | 780.3 | 810.6 | 837.7 | 743.1 | 798 | 595.8 | 805 | 788.7 | 715.6 | 58 | 152.9 | 179.4 | 104.9 | 291.8 | 275.4 | 131.5 | 238.9
790 | 638 | 370.2 | 148.08 | 173.097 | 273.8 | 275.8 | 272 | 272.7 | 507.4 | 43.1 | 20.1 | 72.8 | 3.3 | 173 | 6.4 | 863.6 | 780.6 | 811.2 | 837.9 | 746.6 | 797.7 | 598.3 | 793.1 | 788.4 | 715.5 | 58.2 | 153.2 | 179.7 | 105.1 | 292.1 | 275.4 | 131.8 | 239.1
791 | 639 | 371.1 | 148.44 | 173.5178 | 273.2 | 276.2 | 272.2 | 273.5 | 494.1 | 43.1 | 20.1 | 72.8 | 3.4 | 178.6 | 6.2 | 863.1 | 780.1 | 809.4 | 836.8 | 745.7 | 797 | 599.5 | 781.4 | 787.2 | 713 | 58.3 | 153.4 | 179.7 | 105.4 | 292.2 | 275.3 | 131.9 | 239.3
792 | 640 | 369.1 | 147.64 | 172.5827 | 272.4 | 276.6 | 273 | 273.7 | 484.4 | 43.1 | 20.1 | 72.9 | 3.6 | 178.9 | 6.1 | 863.1 | 780.9 | 805.3 | 835 | 741.5 | 797.1 | 599.2 | 772.9 | 785.8 | 710.5 | 58.5 | 153.6 | 179.7 | 105.6 | 292 | 275.4 | 132.1 | 239.4
793 | 641 | 372.1 | 148.84 | 173.9854 | 271.9 | 277 | 273.7 | 273.3 | 483.2 | 43.1 | 20.1 | 72.9 | 3.7 | 178.5 | 6.1 | 863.8 | 778.6 | 802.5 | 833.3 | 736.2 | 797.8 | 593.5 | 771.4 | 784.1 | 709.2 | 58.6 | 153.9 | 180.2 | 105.8 | 291.8 | 275.4 | 132.3 | 239.6
794 | 642 | 371.1 | 148.44 | 173.5178 | 271.7 | 277.8 | 273.9 | 272.7 | 481.6 | 43.1 | 20.1 | 73 | 3.7 | 177.2 | 5.9 | 864.3 | 776.4 | 802.1 | 833 | 736.3 | 798.2 | 592.5 | 775 | 783.7 | 707.8 | 58.7 | 154.1 | 180.7 | 106 | 291.6 | 275.2 | 132.5 | 239.6
795 | 643 | 370.2 | 148.08 | 173.097 | 271.8 | 278.3 | 273.8 | 272.5 | 490.7 | 43.1 | 20.1 | 73.1 | 3.6 | 170.6 | 5.7 | 865 | 774 | 800.7 | 832.4 | 735 | 798.4 | 590 | 770.3 | 782.9 | 706 | 58.9 | 154.4 | 180.8 | 106.3 | 291.5 | 275.2 | 132.7 | 239.8
796 | 644 | 371.8 | 148.72 | 173.8451 | 271.8 | 278.4 | 273.3 | 272.7 | 485 | 43.1 | 20.1 | 73.2 | 3.3 | 172.6 | 5.6 | 865.2 | 770.9 | 797.2 | 831.2 | 729.8 | 799.2 | 586.5 | 759.6 | 781.4 | 703.2 | 59 | 154.7 | 180.8 | 106.5 | 291.4 | 275.2 | 132.8 | 239.9
797 | 645 | 371.1 | 148.44 | 173.5178 | 271.4 | 278.1 | 272.5 | 273.2 | 489.2 | 43 | 20.1 | 73.3 | 2.7 | 174.1 | 5.1 | 866.1 | 770.3 | 798 | 830.4 | 730.1 | 799.3 | 584.9 | 766.8 | 781.1 | 703.5 | 59.2 | 154.9 | 181.1 | 106.7 | 291.3 | 275.1 | 133 | 239.9
798 | 646 | 370.8 | 148.32 | 173.3775 | 271.5 | 278.5 | 272.2 | 273.1 | 496.1 | 43 | 20.1 | 73.4 | 2.8 | 161.1 | 4.9 | 867 | 768.5 | 798.5 | 829.3 | 729.6 | 800 | 583.5 | 769.8 | 780.2 | 703.5 | 59.3 | 155.2 | 181.5 | 106.9 | 291.3 | 275.4 | 133.2 | 240.1
799 | 647 | 372.2 | 148.88 | 174.0321 | 272 | 279 | 272 | 273.5 | 503.2 | 42.9 | 20.1 | 73.5 | 2.7 | 165.2 | 5.6 | 868.4 | 767.3 | 799.5 | 828.4 | 728.3 | 800.2 | 582.4 | 774.5 | 780 | 703 | 59.4 | 155.4 | 182 | 107.1 | 291.8 | 275.5 | 133.4 | 240.3
800 | 648 | 371.1 | 148.44 | 173.5178 | 272.5 | 279.1 | 271.7 | 274.4 | 508.2 | 42.9 | 20.1 | 73.6 | 2.9 | 182.5 | 5.9 | 868.9 | 766.9 | 801.1 | 828.2 | 729.6 | 799.6 | 583.5 | 778.7 | 780.5 | 704.3 | 59.6 | 155.7 | 182.2 | 107.4 | 291.9 | 275.7 | 133.6 | 240.4
801 | 649 | 371.3 | 148.52 | 173.6113 | 272.7 | 279.1 | 271.8 | 275.1 | 505.6 | 42.9 | 20.1 | 73.6 | 3.2 | 167.7 | 6.7 | 868.1 | 768.4 | 803.3 | 829.5 | 735.3 | 798.5 | 588 | 779.4 | 781.6 | 707.5 | 59.7 | 155.9 | 182.3 | 107.6 | 292 | 276.5 | 133.8 | 240.6
802 | 650 | 369.6 | 147.84 | 172.8164 | 272.9 | 279.1 | 271.3 | 275.5 | 493.2 | 43 | 20.1 | 73.7 | 3.7 | 184.3 | 7.6 | 866.9 | 770.8 | 802.8 | 830.5 | 734.7 | 797 | 594.7 | 774.9 | 782.3 | 708.7 | 59.8 | 156.1 | 182.5 | 107.8 | 291.9 | 277.3 | 134 | 240.8
803 | 651 | 371.9 | 148.76 | 173.8919 | 272.8 | 279.1 | 271 | 275.8 | 483 | 43 | 20.1 | 73.8 | 3.1 | 180.4 | 8.4 | 865.6 | 774.8 | 801 | 831.4 | 734.2 | 794.8 | 600.7 | 770.7 | 782.5 | 709.2 | 60 | 156.3 | 182.7 | 108 | 291.4 | 277.8 | 134.2 | 241
804 | 652 | 372 | 148.8 | 173.9386 | 271.9 | 278.8 | 271.7 | 275.7 | 476.3 | 43.1 | 20.1 | 73.9 | 3.2 | 177.6 | 9 | 864.9 | 777.3 | 802.8 | 832.1 | 735.5 | 793.1 | 605.1 | 771.1 | 782.8 | 709.5 | 60.1 | 156.6 | 182.9 | 108.3 | 291.2 | 278.1 | 134.3 | 241.2
805 | 653 | 372.1 | 148.84 | 173.9854 | 270.8 | 277.8 | 272.5 | 275.3 | 476.1 | 43.1 | 20.1 | 73.9 | 3.1 | 181.4 | 8.9 | 864.1 | 779.2 | 805.6 | 832.8 | 742.1 | 791.3 | 604.2 | 776.8 | 783.6 | 712.8 | 60.3 | 156.8 | 183.1 | 108.5 | 290.8 | 278.4 | 134.5 | 241.3
806 | 654 | 370.2 | 148.08 | 173.097 | 270.4 | 277.2 | 273 | 274.5 | 475.6 | 43.2 | 20.1 | 73.9 | 3.7 | 178 | 9.1 | 863.5 | 780.2 | 806.5 | 832.8 | 745.2 | 789.9 | 605.1 | 782.7 | 784.1 | 714.8 | 60.4 | 157 | 183.3 | 108.7 | 290.9 | 278.2 | 134.7 | 241.4
807 | 655 | 371.9 | 148.76 | 173.8919 | 270 | 277 | 273.3 | 274 | 475.4 | 43.3 | 20.1 | 74 | 4 | 179 | 8.8 | 863.5 | 781.3 | 805.8 | 832.9 | 743.9 | 789 | 606.6 | 782.5 | 783.8 | 714.3 | 60.5 | 157.2 | 183.4 | 108.9 | 290.9 | 278 | 134.9 | 241.4
808 | 656 | 374.1 | 149.64 | 174.9205 | 269.8 | 277.3 | 273.8 | 273.5 | 480.4 | 43.4 | 20.1 | 74 | 3.4 | 187.3 | 7.9 | 863.7 | 782.5 | 804.2 | 833.1 | 743.2 | 788.2 | 606.7 | 782.5 | 783.5 | 714.7 | 60.7 | 157.4 | 183.6 | 109.1 | 290.6 | 278 | 135.1 | 241.5
809 | 657 | 373.9 | 149.56 | 174.827 | 269.5 | 277.4 | 274.2 | 273 | 484 | 43.4 | 20 | 74 | 3.7 | 178.8 | 7.5 | 864.3 | 781.2 | 802 | 832.1 | 739.6 | 788.4 | 603.2 | 776.8 | 781.8 | 712.8 | 60.8 | 157.6 | 183.9 | 109.4 | 290.6 | 277.8 | 135.3 | 241.6
810 | 658 | 372.5 | 149 | 174.1724 | 269.4 | 277.2 | 274.2 | 272.7 | 489.3 | 43.4 | 20 | 74 | 3.6 | 181.2 | 7.6 | 864.9 | 776.1 | 798.1 | 829.1 | 735.2 | 789.2 | 596.6 | 769.2 | 780 | 710.1 | 61 | 157.8 | 184.5 | 109.6 | 290.7 | 277.8 | 135.5 | 241.7
811 | 659 | 371.8 | 148.72 | 173.8451 | 270 | 278.1 | 273.8 | 272.7 | 493.1 | 43.4 | 20 | 74 | 3.5 | 184.5 | 7.4 | 865.1 | 771.9 | 797.3 | 827 | 733.7 | 790.3 | 592.1 | 765 | 778.3 | 707.4 | 61.1 | 158 | 184.8 | 109.8 | 290.7 | 277.8 | 135.7 | 241.8
812 | 660 | 372.2 | 148.88 | 174.0321 | 270.9 | 279.7 | 273.5 | 273.1 | 489.3 | 43.4 | 20 | 74 | 3.5 | 178.7 | 7.4 | 865.3 | 769.3 | 797 | 825.4 | 733.6 | 791.6 | 587.3 | 763.6 | 776.7 | 705.3 | 61.2 | 158.3 | 185.2 | 110 | 292.3 | 277.8 | 135.9 | 241.9
813 | 661 | 371.8 | 148.72 | 173.8451 | 271.5 | 281.6 | 273.4 | 274 | 483.7 | 43.3 | 20 | 74 | 3.5 | 181.2 | 7.7 | 865.2 | 765 | 796.8 | 824.6 | 730.9 | 792.4 | 583.5 | 753.9 | 775.3 | 702.5 | 61.4 | 158.5 | 185.2 | 110.3 | 292.1 | 278 | 136.1 | 242.1
814 | 662 | 371.8 | 148.72 | 173.8451 | 271.5 | 280.9 | 273.6 | 275.4 | 476.2 | 43.3 | 20 | 74 | 3.5 | 177.3 | 7.7 | 865 | 761.9 | 798.3 | 824.5 | 731.2 | 792.8 | 579.7 | 750.1 | 774.2 | 700.1 | 61.5 | 158.7 | 185.3 | 110.5 | 291.7 | 278.4 | 136.3 | 242.2
815 | 663 | 371.8 | 148.72 | 173.8451 | 271.2 | 279.4 | 273.5 | 275.9 | 472.4 | 43.2 | 20 | 74.1 | 3.5 | 174.3 | 7.4 | 864.9 | 760.6 | 798.9 | 824.8 | 731.4 | 792.7 | 579.4 | 746.3 | 773.6 | 699 | 61.7 | 158.9 | 185.4 | 110.7 | 291.5 | 278.5 | 136.5 | 242.4
816 | 664 | 372 | 148.8 | 173.9386 | 271.7 | 278 | 273.6 | 276.5 | 470.9 | 43.3 | 20 | 74.2 | 3.4 | 177.2 | 6.9 | 864.8 | 758.9 | 797.1 | 823.5 | 728.3 | 792.5 | 577.4 | 742.9 | 772.4 | 696.2 | 61.8 | 159.1 | 185.4 | 110.9 | 291.3 | 278.3 | 136.7 | 242.5
817 | 665 | 370.8 | 148.32 | 173.3775 | 272 | 277.1 | 273.7 | 276.6 | 471.5 | 43.3 | 20 | 74.2 | 3.2 | 176.9 | 6.8 | 864.9 | 757.9 | 797.6 | 824.4 | 729.4 | 792.2 | 575.2 | 752.4 | 771.9 | 695.6 | 61.9 | 159.3 | 185.8 | 111.2 | 291.2 | 278.4 | 136.8 | 242.6
818 | 666 | 368.5 | 147.4 | 172.3021 | 271.8 | 277.5 | 273.6 | 276 | 476.2 | 43.3 | 20 | 74.3 | 3.4 | 176.7 | 7 | 865 | 755.3 | 797.7 | 823.1 | 729.1 | 792 | 571.8 | 753.8 | 770.8 | 694.3 | 62.1 | 159.5 | 186.2 | 111.4 | 291.1 | 278.3 | 137.1 | 242.6
819 | 667 | 369.6 | 147.84 | 172.8164 | 271.8 | 278.2 | 273.6 | 275.5 | 472.4 | 43.3 | 20 | 74.3 | 3.4 | 176.5 | 7.2 | 865.4 | 755 | 799.4 | 822.8 | 730.4 | 791.7 | 571 | 752.8 | 770.3 | 694.2 | 62.2 | 159.7 | 186.4 | 111.6 | 291.4 | 277.9 | 137.2 | 242.7
820 | 668 | 371.7 | 148.68 | 173.7984 | 272.2 | 278.4 | 273.7 | 275.9 | 473.2 | 43.2 | 20 | 74.4 | 3.4 | 177.2 | 7 | 865.9 | 756.9 | 799.3 | 823.1 | 729.4 | 791.1 | 571.2 | 757.1 | 770.1 | 694.6 | 62.3 | 159.9 | 186.7 | 111.8 | 291.6 | 277.6 | 137.4 | 242.8
821 | 669 | 370.7 | 148.28 | 173.3308 | 272.9 | 278.3 | 273 | 276.2 | 480.9 | 43.1 | 20 | 74.4 | 3.3 | 180 | 6.9 | 866 | 757.5 | 799.2 | 823.5 | 728.6 | 790.6 | 569.3 | 752.6 | 769.4 | 693.8 | 62.5 | 160.1 | 186.8 | 112.1 | 291.3 | 277.9 | 137.7 | 242.9
822 | 670 | 370.6 | 148.24 | 173.284 | 272.9 | 278.8 | 272.4 | 276.4 | 478.9 | 43.2 | 20 | 74.4 | 3.6 | 181.8 | 6.7 | 865.9 | 760.5 | 798.8 | 824.9 | 729 | 789.7 | 571.1 | 755.4 | 769.9 | 695.5 | 62.6 | 160.3 | 187 | 112.3 | 291.1 | 278.3 | 137.9 | 243
823 | 671 | 371 | 148.4 | 173.471 | 272.4 | 279.1 | 271.7 | 276.5 | 481 | 43.3 | 20 | 74.5 | 3.2 | 174 | 6.8 | 865.5 | 763.1 | 801.2 | 825.6 | 730.2 | 788.4 | 573.9 | 758.9 | 770.5 | 695.9 | 62.8 | 160.5 | 187.2 | 112.5 | 291.1 | 278.6 | 138 | 243.1
824 | 672 | 370.5 | 148.2 | 173.2373 | 272 | 278.8 | 270.9 | 276.5 | 476.4 | 43.4 | 20 | 74.5 | 3.5 | 174.4 | 6.9 | 865 | 764.3 | 800.4 | 825.7 | 730.8 | 787.1 | 578.4 | 752.1 | 770 | 695.6 | 62.9 | 160.6 | 187.3 | 112.7 | 290.9 | 278.9 | 138.2 | 243.3
825 | 673 | 371.5 | 148.6 | 173.7048 | 272.3 | 277.9 | 270.8 | 276.1 | 470.2 | 43.5 | 20 | 74.5 | 3.6 | 176.3 | 6.7 | 864.3 | 767.1 | 798 | 826 | 728.9 | 785.8 | 580.9 | 746.1 | 769.7 | 695.7 | 63.1 | 160.8 | 187.5 | 113 | 290.7 | 279 | 138.4 | 243.5
826 | 674 | 370.9 | 148.36 | 173.4243 | 271.9 | 277.6 | 270.7 | 275.6 | 465.8 | 43.5 | 20 | 74.6 | 3.4 | 176.5 | 6.6 | 863.3 | 770.2 | 799 | 827.3 | 731.8 | 784.1 | 588.5 | 752.9 | 770.4 | 699.1 | 63.2 | 161 | 187.7 | 113.2 | 290.2 | 279.2 | 138.6 | 243.6
827 | 675 | 371.5 | 148.6 | 173.7048 | 272.2 | 277.4 | 271 | 275.1 | 465.6 | 43.5 | 20 | 74.7 | 3.4 | 186.2 | 6.3 | 862 | 773.3 | 798.4 | 827.3 | 732.1 | 782.2 | 594.9 | 751 | 770.7 | 701.1 | 63.3 | 161.2 | 188 | 113.4 | 289.9 | 279.4 | 138.8 | 243.7
828 | 676 | 372.9 | 149.16 | 174.3594 | 272.2 | 277.3 | 271.6 | 274.6 | 459.3 | 43.5 | 20 | 74.7 | 3.2 | 180.8 | 6.1 | 861.1 | 775.6 | 798.3 | 827.6 | 731.9 | 780.5 | 601 | 747.5 | 770.8 | 701.9 | 63.5 | 161.4 | 188.2 | 113.7 | 289.9 | 279.6 | 139 | 243.9
829 | 677 | 371.9 | 148.76 | 173.8919 | 272.1 | 277.1 | 272.6 | 274.3 | 454.2 | 43.6 | 20 | 74.8 | 3.5 | 179.8 | 6.1 | 860.8 | 776.9 | 798.6 | 828.2 | 732.1 | 779.2 | 602 | 746.5 | 770.5 | 702.7 | 63.6 | 161.6 | 188.4 | 113.9 | 289.7 | 279.5 | 139.2 | 244
830 | 678 | 371.6 | 148.64 | 173.7516 | 271.7 | 277 | 273.2 | 274.1 | 451.5 | 43.6 | 20 | 74.9 | 3.1 | 184.4 | 6.2 | 861.1 | 777.7 | 798.5 | 828.8 | 731.7 | 778.5 | 601.2 | 741.8 | 770 | 702.8 | 63.8 | 161.8 | 188.5 | 114.1 | 289.5 | 279.3 | 139.4 | 244
831 | 679 | 371.3 | 148.52 | 173.6113 | 271.3 | 276.6 | 273.7 | 273.9 | 448.9 | 43.7 | 20 | 74.9 | 3.2 | 179.7 | 6 | 861.3 | 777.2 | 799.2 | 829.6 | 731.9 | 778 | 599.6 | 747.2 | 769.7 | 702.3 | 63.9 | 162 | 188.6 | 114.3 | 289.8 | 279.3 | 139.6 | 244.1
832 | 680 | 371.2 | 148.48 | 173.5646 | 271.1 | 276.2 | 274.1 | 273.7 | 457.4 | 43.7 | 20 | 74.8 | 3.1 | 176.7 | 5.7 | 861.7 | 776.9 | 802.1 | 830.5 | 737.3 | 777.4 | 596.7 | 762.1 | 769.6 | 703.2 | 64.1 | 162.2 | 188.8 | 114.6 | 290.4 | 279.4 | 139.8 | 244.3
833 | 681 | 371.4 | 148.56 | 173.6581 | 270.9 | 276 | 274 | 273.7 | 463.6 | 43.6 | 20 | 74.8 | 3.2 | 176.5 | 5.5 | 861.3 | 776.9 | 803.5 | 831 | 740.4 | 777.1 | 594.1 | 769.2 | 769.8 | 705.4 | 64.2 | 162.3 | 189 | 114.8 | 290.6 | 279.6 | 140 | 244.4
834 | 682 | 372.5 | 149 | 174.1724 | 270.8 | 276.5 | 273.4 | 273.7 | 467.9 | 43.6 | 20 | 74.8 | 3.2 | 175.9 | 5.4 | 860.8 | 779 | 803.9 | 831.8 | 740.7 | 776.3 | 595.1 | 775.3 | 770.8 | 709.5 | 64.3 | 162.5 | 189.2 | 115 | 290.7 | 279.9 | 140.3 | 244.5
835 | 683 | 371.5 | 148.6 | 173.7048 | 270.5 | 276.5 | 272.5 | 273.9 | 466.1 | 43.6 | 20 | 74.8 | 3.3 | 175.1 | 5.4 | 860.7 | 780.9 | 803.8 | 831.8 | 740.1 | 775.4 | 596.7 | 772.8 | 770.9 | 709.2 | 64.5 | 162.7 | 189.4 | 115.3 | 290.3 | 280 | 140.4 | 244.7
836 | 684 | 372.3 | 148.92 | 174.0789 | 270.7 | 276.2 | 272.2 | 273.8 | 467.6 | 43.6 | 20 | 74.8 | 3.7 | 171.6 | 5.2 | 860.3 | 782.4 | 805.7 | 833.1 | 744 | 774.1 | 602.5 | 779.2 | 771.8 | 712 | 64.6 | 162.9 | 189.5 | 115.5 | 289.6 | 279.9 | 140.6 | 244.8
837 | 685 | 371.5 | 148.6 | 173.7048 | 270.7 | 276.3 | 272.2 | 273.4 | 468.2 | 43.6 | 20 | 74.8 | 3.6 | 176.2 | 5.2 | 860 | 783.2 | 806 | 833.4 | 745.9 | 772.6 | 604.9 | 786.1 | 772.5 | 715.1 | 64.8 | 163.1 | 189.7 | 115.7 | 289.2 | 279.9 | 140.8 | 244.9
838 | 686 | 379.5 | 151.8 | 177.4455 | 271.3 | 275.6 | 272 | 272.7 | 475.9 | 43.5 | 20 | 74.7 | 3.6 | 181.3 | 5.3 | 860.9 | 784.9 | 805.8 | 833.7 | 744.1 | 772.2 | 601.8 | 791 | 772.1 | 715.8 | 64.9 | 163.3 | 190.1 | 116 | 289.1 | 279.8 | 141 | 245.1
839 | 687 | 378.5 | 151.4 | 176.9779 | 271.7 | 275.5 | 272 | 271.9 | 489.2 | 43.5 | 20 | 74.7 | 3.6 | 178.6 | 4.8 | 861.7 | 783.5 | 803.3 | 833.3 | 741.2 | 772.1 | 598.8 | 790.6 | 771.7 | 714.8 | 65.1 | 163.5 | 190.3 | 116.2 | 289 | 279.9 | 141.2 | 245.2
840 | 688 | 383.9 | 153.56 | 179.5028 | 272.1 | 276.2 | 272.4 | 271.9 | 498.1 | 43.5 | 20 | 74.6 | 3.6 | 163.8 | 4.7 | 862.8 | 783.7 | 804.1 | 832.3 | 741 | 772.3 | 597.3 | 797.4 | 771.9 | 714.7 | 65.2 | 163.7 | 190.7 | 116.4 | 289.3 | 279.7 | 141.4 | 245.3
841 | 689 | 405.2 | 162.08 | 189.4622 | 272.4 | 276.6 | 272.2 | 272.4 | 509.1 | 43.4 | 20 | 74.7 | 3.3 | 157.6 | 4.7 | 864.3 | 784 | 805.5 | 830.7 | 740.8 | 772.2 | 596.8 | 802.1 | 772.3 | 716.1 | 65.3 | 163.9 | 190.9 | 116.6 | 289.6 | 279.3 | 141.6 | 245.3
842 | 690 | 430.7 | 172.28 | 201.3854 | 272.3 | 276 | 272.3 | 273.2 | 509.4 | 43.4 | 20 | 74.7 | 3 | 168 | 4.6 | 865.8 | 784.9 | 806.9 | 830.1 | 740.6 | 772.3 | 597.3 | 801.7 | 772.3 | 718.4 | 65.5 | 164.1 | 191 | 116.9 | 289.7 | 279 | 141.8 | 245.4
843 | 691 | 445.1 | 178.04 | 208.1185 | 272.8 | 275.7 | 272.4 | 273.8 | 510.8 | 43.5 | 20 | 74.7 | 3.4 | 180.1 | 4.5 | 867.1 | 786.8 | 807.3 | 830.6 | 739.9 | 772.6 | 597.2 | 800.4 | 772.6 | 719 | 65.6 | 164.3 | 191.2 | 117.1 | 289.8 | 279 | 142 | 245.5
844 | 692 | 450.7 | 180.28 | 210.7369 | 272.5 | 275.8 | 272.2 | 274.3 | 511 | 43.6 | 20 | 74.7 | 3.5 | 178.1 | 4.7 | 868.2 | 786.6 | 808.6 | 830.8 | 742.3 | 773.1 | 593.7 | 805 | 772.4 | 719.5 | 65.8 | 164.5 | 191.6 | 117.3 | 290 | 278.9 | 142.3 | 245.6
845 | 693 | 451 | 180.4 | 210.8772 | 273.2 | 277 | 271.7 | 274.5 | 506 | 43.8 | 20 | 74.8 | 3.5 | 176.7 | 5 | 868.4 | 787 | 812.7 | 832 | 746.2 | 773.2 | 592.5 | 811.7 | 773.2 | 721.8 | 65.9 | 164.7 | 191.8 | 117.6 | 290 | 279.3 | 142.5 | 245.7
846 | 694 | 450.7 | 180.28 | 210.7369 | 273.8 | 278 | 271.9 | 274.9 | 511.9 | 43.9 | 20 | 74.8 | 3.1 | 175.3 | 5.1 | 868.5 | 785.9 | 814.4 | 831.6 | 750.7 | 772.9 | 589.2 | 814.2 | 773.5 | 724.6 | 66.1 | 164.9 | 192 | 117.8 | 290.4 | 279.4 | 142.7 | 245.8
847 | 695 | 450.7 | 180.28 | 210.7369 | 274.5 | 278.5 | 272.4 | 275.2 | 513.7 | 43.9 | 20 | 74.9 | 3.6 | 166.2 | 4.6 | 868.6 | 787 | 816.8 | 831.1 | 754.4 | 772.8 | 590.5 | 813.6 | 774 | 727.3 | 66.2 | 165.1 | 192.3 | 118 | 290.8 | 279.9 | 142.8 | 246
848 | 696 | 452.6 | 181.04 | 211.6253 | 275 | 279.6 | 273.1 | 275.7 | 509.8 | 43.9 | 20 | 74.9 | 3.8 | 154.6 | 4.4 | 868.9 | 789 | 818.8 | 831.9 | 757.5 | 772.3 | 591.9 | 816.2 | 774.7 | 728.1 | 66.3 | 165.3 | 192.5 | 118.3 | 290.9 | 280.1 | 143.1 | 246.1
849 | 697 | 452.4 | 180.96 | 211.5318 | 274.9 | 280.7 | 273.2 | 275.8 | 508 | 44 | 20 | 75 | 3.6 | 151.1 | 4.2 | 869.1 | 790.2 | 818.7 | 833 | 756.8 | 772 | 593.1 | 816.5 | 775 | 729.4 | 66.5 | 165.5 | 192.8 | 118.5 | 291 | 280.2 | 143.3 | 246.3
850 | 698 | 453.3 | 181.32 | 211.9526 | 275.1 | 281.1 | 273.1 | 275.6 | 513.7 | 44 | 20 | 75 | 3.5 | 159.5 | 4 | 869.1 | 791.3 | 817.3 | 833.3 | 755 | 771.4 | 598.9 | 813.7 | 775.5 | 731 | 66.6 | 165.8 | 193.1 | 118.7 | 291.1 | 280.7 | 143.5 | 246.5
851 | 699 | 454.1 | 181.64 | 212.3267 | 275.5 | 281.1 | 273.4 | 275.1 | 512.3 | 44 | 20 | 75 | 3.8 | 168.7 | 3.6 | 868.1 | 793.1 | 819.4 | 833.6 | 757.8 | 770.8 | 604.5 | 814.6 | 776.2 | 732.8 | 66.8 | 166 | 193.5 | 119 | 291.1 | 281.1 | 143.7 | 246.6
852 | 700 | 455.2 | 182.08 | 212.841 | 275.3 | 281.5 | 273.7 | 274.9 | 509.5 | 44 | 20 | 75 | 3.6 | 143.8 | 3.3 | 867.3 | 793.7 | 819.6 | 833.4 | 760.1 | 770.2 | 608.2 | 814.2 | 777.4 | 735.7 | 66.9 | 166.2 | 193.5 | 119.2 | 291.2 | 281.3 | 143.9 | 246.7
853 | 701 | 455.9 | 182.36 | 213.1683 | 275.5 | 282.5 | 274.4 | 275.4 | 515.3 | 44.1 | 20 | 75 | 3.4 | 130.4 | 3.2 | 866.9 | 795.3 | 821.1 | 834.2 | 759.8 | 769.6 | 612.2 | 815.8 | 777.9 | 737 | 67.1 | 166.4 | 193.7 | 119.4 | 291.4 | 281.3 | 144.1 | 246.8
854 | 702 | 457.6 | 183.04 | 213.9632 | 275.7 | 282.8 | 275 | 276.1 | 518.5 | 44.1 | 20 | 75 | 3.9 | 153.9 | 3.2 | 866.7 | 796.5 | 823.1 | 834.1 | 759.6 | 769 | 617.2 | 816.5 | 778.3 | 739.7 | 67.2 | 166.6 | 193.9 | 119.7 | 291.7 | 281.3 | 144.3 | 246.9
855 | 703 | 457.7 | 183.08 | 214.01 | 276.2 | 282.5 | 275.4 | 276.5 | 520.8 | 44.1 | 20 | 75.1 | 3.5 | 177 | 3.8 | 866.8 | 798.5 | 826 | 835.6 | 762.8 | 768.3 | 618.9 | 815.4 | 778.8 | 741.9 | 67.4 | 166.9 | 194.2 | 119.9 | 292 | 281.3 | 144.5 | 247.1
856 | 704 | 458.7 | 183.48 | 214.4775 | 275.6 | 282 | 275.4 | 276.5 | 514.2 | 44.2 | 20 | 75.1 | 3.2 | 173.4 | 4.8 | 866.9 | 800.4 | 827.2 | 836.3 | 764 | 767.7 | 621.3 | 815.5 | 779.2 | 743.9 | 67.5 | 167.1 | 194.3 | 120.1 | 292.1 | 281.4 | 144.7 | 247.3
857 | 705 | 460.1 | 184.04 | 215.1322 | 275.6 | 282.1 | 275.2 | 276.3 | 508.6 | 44.2 | 20 | 75.1 | 3.2 | 164.4 | 5.6 | 866.8 | 800.7 | 827.4 | 837.1 | 764.7 | 767.4 | 627.4 | 810.3 | 779.1 | 745.7 | 67.7 | 167.3 | 194.5 | 120.4 | 292.6 | 281.9 | 144.9 | 247.5
858 | 706 | 458.8 | 183.52 | 214.5243 | 275.3 | 282.9 | 275.7 | 276.2 | 508.5 | 44.3 | 20 | 75.2 | 3.4 | 169.2 | 6.1 | 867.1 | 802.3 | 826.4 | 837.6 | 766 | 766.9 | 629.5 | 812.6 | 779.9 | 746.1 | 67.8 | 167.5 | 194.7 | 120.6 | 293.1 | 282.6 | 145.1 | 247.7
859 | 707 | 459.7 | 183.88 | 214.9451 | 275.2 | 284.2 | 276.1 | 276.3 | 520.2 | 44.3 | 20 | 75.2 | 3.5 | 186.7 | 6.1 | 868.2 | 802.8 | 826.2 | 838 | 767.3 | 766.7 | 629.7 | 816.4 | 780.4 | 747.6 | 67.9 | 167.7 | 195.1 | 120.8 | 293.2 | 283.2 | 145.3 | 247.8
860 | 708 | 460.6 | 184.24 | 215.3659 | 275.5 | 285.4 | 276.9 | 276.7 | 539.1 | 44.3 | 20 | 75.3 | 3.6 | 180.7 | 5.8 | 869.8 | 804.3 | 825.3 | 837.7 | 767.4 | 767 | 626.4 | 816.3 | 780.4 | 747.7 | 68.1 | 168 | 195.5 | 121.1 | 293.4 | 283.2 | 145.5 | 247.9
861 | 709 | 460.5 | 184.2 | 215.3192 | 275.8 | 285.7 | 277 | 277.1 | 553.2 | 44.4 | 20 | 75.3 | 3.7 | 159.9 | 5.4 | 872.1 | 801.9 | 825.5 | 835.8 | 764.5 | 768.1 | 618.4 | 813.2 | 779 | 744.9 | 68.2 | 168.2 | 196 | 121.3 | 293.9 | 283.1 | 145.8 | 248.1
862 | 710 | 461 | 184.4 | 215.553 | 275.7 | 286.3 | 277 | 277.6 | 556.7 | 44.4 | 20 | 75.4 | 3.2 | 171.9 | 5.3 | 873.5 | 801 | 828.8 | 836.7 | 767.7 | 769.9 | 613.4 | 817.5 | 778.9 | 746.1 | 68.4 | 168.5 | 196.4 | 121.5 | 294.8 | 283.9 | 145.9 | 248.3
863 | 711 | 462.4 | 184.96 | 216.2076 | 275.6 | 287.1 | 277.2 | 278.9 | 549.7 | 44.5 | 20 | 75.5 | 3.6 | 173.9 | 5.5 | 874.2 | 800.9 | 831.5 | 838 | 770.5 | 771 | 611.2 | 821.9 | 779.4 | 747.5 | 68.5 | 168.7 | 196.8 | 121.7 | 295.5 | 284.6 | 146.1 | 248.5
864 | 712 | 462.3 | 184.92 | 216.1608 | 275.6 | 288.3 | 277.5 | 280.3 | 551.9 | 44.5 | 20 | 75.6 | 3.6 | 160.2 | 5.6 | 874.8 | 800.3 | 833.4 | 838.6 | 771.3 | 772.1 | 609.6 | 823.9 | 779.5 | 747.2 | 68.7 | 169 | 197.1 | 122 | 295.5 | 285.5 | 146.4 | 248.6
865 | 713 | 462.6 | 185.04 | 216.3011 | 275.6 | 290.2 | 277.7 | 281.3 | 554 | 44.5 | 19.9 | 75.7 | 3.9 | 168.3 | 5.2 | 875.7 | 801.1 | 833.8 | 839.1 | 773.5 | 772.6 | 613.2 | 827.1 | 780.9 | 751.1 | 68.8 | 169.3 | 197.2 | 122.2 | 295.6 | 286.4 | 146.6 | 248.9
866 | 714 | 464.8 | 185.92 | 217.3298 | 276.5 | 290 | 278.1 | 281.7 | 548.7 | 44.6 | 19.9 | 75.7 | 3.7 | 166 | 4.7 | 875.8 | 802.1 | 834.3 | 839.9 | 774.2 | 772.8 | 617.6 | 826.4 | 781.5 | 751.8 | 69 | 169.5 | 197.5 | 122.5 | 295.9 | 287 | 146.8 | 249.1
867 | 715 | 466.2 | 186.48 | 217.9844 | 277.5 | 290.1 | 278.4 | 281.8 | 538.1 | 44.6 | 19.9 | 75.7 | 3.7 | 162 | 4.4 | 874.1 | 802.7 | 835.1 | 840.7 | 776.9 | 772.6 | 626 | 819.9 | 782.4 | 754 | 69.1 | 169.8 | 197.6 | 122.7 | 296 | 287.7 | 147 | 249.4
868 | 716 | 466.5 | 186.6 | 218.1246 | 277.7 | 289.6 | 278.7 | 281.8 | 525.4 | 44.7 | 19.9 | 75.7 | 3.5 | 176.3 | 4.1 | 873.4 | 803 | 832.6 | 841.3 | 776.3 | 772.3 | 633.7 | 813.1 | 782.8 | 755 | 69.3 | 170 | 197.9 | 122.9 | 296.1 | 288.4 | 147.2 | 249.7
869 | 717 | 465.8 | 186.32 | 217.7973 | 278.5 | 289.1 | 279.5 | 282.2 | 512 | 44.7 | 19.9 | 75.7 | 3.6 | 174.2 | 4.2 | 873 | 803.7 | 831.1 | 841.5 | 775.5 | 772.2 | 636.3 | 810.3 | 783.2 | 755.7 | 69.4 | 170.2 | 198.2 | 123.2 | 296 | 288.9 | 147.4 | 250
870 | 718 | 465.9 | 186.36 | 217.8441 | 278.1 | 288.7 | 281 | 282.5 | 514.1 | 44.8 | 19.9 | 75.8 | 3.8 | 175.7 | 4.5 | 873.9 | 805.5 | 833.3 | 841.9 | 778.4 | 772.5 | 634.4 | 812.2 | 783.3 | 755.9 | 69.6 | 170.5 | 198.5 | 123.4 | 297.4 | 289.4 | 147.6 | 250
871 | 719 | 465.6 | 186.24 | 217.7038 | 278.1 | 289.5 | 282.1 | 282.9 | 517.1 | 44.8 | 19.9 | 75.8 | 3.5 | 179.6 | 5 | 875 | 805.3 | 834.5 | 842.2 | 781.2 | 773.8 | 627.9 | 811.5 | 782.8 | 755.6 | 69.7 | 170.7 | 198.8 | 123.6 | 297.7 | 289.9 | 147.8 | 250.2
872 | 720 | 466.4 | 186.56 | 218.0779 | 278.9 | 290.7 | 282.8 | 283.8 | 518.2 | 44.9 | 19.9 | 75.9 | 3.5 | 174 | 5.7 | 875.5 | 805 | 834.9 | 842.3 | 782.5 | 774.8 | 628.1 | 811.5 | 783.1 | 756.9 | 69.8 | 171 | 199.1 | 123.9 | 297.8 | 289.9 | 148 | 250.4
873 | 721 | 467.1 | 186.84 | 218.4052 | 279 | 291.8 | 282.8 | 284.4 | 525.9 | 44.9 | 19.9 | 76 | 3.4 | 154.1 | 5.7 | 875.7 | 805.2 | 835.1 | 842.9 | 784.5 | 775.1 | 627.8 | 816.6 | 783.7 | 758.3 | 70 | 171.2 | 199.2 | 124.1 | 298 | 290.5 | 148.2 | 250.6
874 | 722 | 468.2 | 187.28 | 218.9195 | 279.5 | 292.9 | 282.4 | 284.5 | 536.2 | 44.9 | 19.9 | 76.1 | 3.8 | 160.5 | 5.1 | 877.2 | 805.3 | 835 | 842 | 786.1 | 775.5 | 625.3 | 820.5 | 784 | 759.4 | 70.1 | 171.5 | 199.5 | 124.3 | 298.3 | 291 | 148.4 | 250.8
875 | 723 | 468.4 | 187.36 | 219.013 | 280.1 | 293.9 | 282.2 | 284.5 | 538.4 | 44.9 | 19.9 | 76.2 | 4 | 190.6 | 5.1 | 879.6 | 804.1 | 835.6 | 841.3 | 784.6 | 777 | 619.9 | 823 | 783.8 | 759.1 | 70.3 | 171.7 | 200.1 | 124.6 | 298.7 | 291.3 | 148.6 | 250.9
876 | 724 | 468.5 | 187.4 | 219.0598 | 279.9 | 296.1 | 282 | 284.8 | 566.9 | 44.9 | 19.9 | 76.3 | 3.9 | 189.4 | 4.5 | 881 | 801.8 | 834.5 | 840.8 | 780.7 | 778.5 | 614.3 | 821 | 783.3 | 757.7 | 70.4 | 172 | 200.6 | 124.8 | 298.8 | 291.4 | 148.8 | 251
877 | 725 | 469.1 | 187.64 | 219.3403 | 279.9 | 297.5 | 282.4 | 285.7 | 589.8 | 44.9 | 19.9 | 76.3 | 3.7 | 167.3 | 4 | 881.9 | 799 | 833.5 | 841.4 | 779.3 | 780 | 610.5 | 824.4 | 783.1 | 757.9 | 70.6 | 172.2 | 201.1 | 125.1 | 299.4 | 291.5 | 149.1 | 251.1
878 | 726 | 470.5 | 188.2 | 219.995 | 280.4 | 298.9 | 283 | 287 | 591.4 | 45 | 19.9 | 76.4 | 3.7 | 176.5 | 4.1 | 883 | 796.9 | 834 | 841.4 | 778.7 | 781.1 | 608.7 | 826.9 | 782.8 | 756.9 | 70.7 | 172.5 | 201.2 | 125.3 | 300 | 292.2 | 149.2 | 251.4
879 | 727 | 470.5 | 188.2 | 219.995 | 281.3 | 299.7 | 283.4 | 288.4 | 581.8 | 45.2 | 19.9 | 76.4 | 3.4 | 192.1 | 4.6 | 883.5 | 795 | 834.7 | 841.7 | 779 | 782.6 | 607 | 815 | 781.8 | 755.2 | 70.9 | 172.8 | 201.6 | 125.5 | 300.4 | 292.6 | 149.5 | 251.6
880 | 728 | 469.8 | 187.92 | 219.6677 | 283 | 300.8 | 284.2 | 289.4 | 567.4 | 45.2 | 19.9 | 76.5 | 3.4 | 198.6 | 5 | 884 | 792.2 | 834.2 | 842.1 | 778 | 783.8 | 605.8 | 808 | 781.2 | 753.3 | 71 | 173.1 | 201.7 | 125.8 | 300.7 | 292.9 | 149.7 | 251.8
881 | 729 | 471.5 | 188.6 | 220.4625 | 284.4 | 301.6 | 285 | 290 | 552.7 | 45.2 | 19.9 | 76.5 | 3.2 | 212.2 | 6.3 | 884.5 | 791.1 | 832.1 | 843.4 | 776.1 | 784.6 | 606.3 | 806.6 | 780.8 | 753 | 71.2 | 173.3 | 201.8 | 126 | 300.8 | 293.4 | 149.9 | 252
882 | 730 | 472.4 | 188.96 | 220.8834 | 284.9 | 301 | 285.3 | 290.1 | 546.4 | 45.1 | 19.9 | 76.6 | 3 | 198.6 | 7.3 | 884.6 | 791.6 | 831.1 | 844.2 | 776.6 | 785.1 | 609.4 | 800.9 | 780.5 | 752.4 | 71.3 | 173.6 | 202.1 | 126.2 | 300.8 | 293.9 | 150.1 | 252.2
883 | 731 | 472.5 | 189 | 220.9301 | 285 | 300.1 | 285.8 | 289.9 | 544.4 | 45 | 19.9 | 76.7 | 3.2 | 200.8 | 7.1 | 884.4 | 793 | 831.6 | 845.3 | 778 | 785.5 | 611.3 | 804.6 | 780.4 | 751.8 | 71.5 | 173.8 | 202.2 | 126.5 | 300.9 | 294.5 | 150.3 | 252.5
884 | 732 | 470.5 | 188.2 | 219.995 | 285 | 299.7 | 286.4 | 289.6 | 551.7 | 45 | 19.9 | 76.8 | 3.4 | 208.8 | 7.1 | 884.4 | 793.5 | 831 | 846.2 | 776.9 | 785.6 | 609.8 | 809.8 | 780.2 | 752.6 | 71.6 | 174.1 | 202.5 | 126.7 | 300.8 | 294.7 | 150.5 | 252.7
885 | 733 | 469.4 | 187.76 | 219.4806 | 285.9 | 299.7 | 286.5 | 289.1 | 556.2 | 45.1 | 19.9 | 76.8 | 3.2 | 209.7 | 7.2 | 884.9 | 790.6 | 827.9 | 844.8 | 773.3 | 786.3 | 605.9 | 802.2 | 778.6 | 748.9 | 71.8 | 174.3 | 203.1 | 127 | 301.3 | 294.4 | 150.7 | 252.7
886 | 734 | 470.4 | 188.16 | 219.9482 | 286.5 | 300.1 | 286.4 | 288.9 | 563.1 | 45.2 | 19.9 | 76.9 | 3.4 | 211.2 | 7 | 885.7 | 787.3 | 825.5 | 843.8 | 769.1 | 787.3 | 602 | 804.6 | 777.6 | 748.6 | 71.9 | 174.6 | 203.7 | 127.2 | 302 | 294.4 | 150.9 | 252.7
887 | 735 | 470 | 188 | 219.7612 | 287.3 | 299.7 | 286.2 | 289.5 | 560.1 | 45.2 | 19.9 | 76.9 | 3.5 | 192.7 | 6.6 | 886.7 | 786.6 | 826.9 | 844.1 | 770.8 | 788.1 | 600.2 | 807.8 | 777.9 | 749.5 | 72.1 | 174.8 | 204 | 127.4 | 302.8 | 294.6 | 151.2 | 252.9
888 | 736 | 471.1 | 188.44 | 220.2755 | 287.5 | 299.3 | 286.6 | 290.8 | 569 | 45.3 | 19.9 | 77 | 3.5 | 192.3 | 6.2 | 886.9 | 788.4 | 831 | 844.5 | 772.1 | 787.9 | 601.3 | 817 | 779.1 | 752.3 | 72.2 | 175.1 | 204.1 | 127.6 | 303.4 | 294.3 | 151.3 | 253
889 | 737 | 469.6 | 187.84 | 219.5741 | 288 | 300.6 | 287.1 | 291.8 | 576.2 | 45.3 | 19.9 | 77.1 | 3.2 | 183.4 | 6.2 | 886.5 | 787.9 | 834.2 | 844.3 | 775.5 | 788 | 599 | 821.7 | 779.4 | 752.3 | 72.4 | 175.4 | 204.4 | 127.9 | 303.7 | 294.6 | 151.5 | 253.2
890 | 738 | 471.3 | 188.52 | 220.369 | 288.3 | 301.6 | 287.4 | 292.7 | 575.8 | 45.4 | 19.9 | 77.3 | 3.3 | 154.8 | 5.7 | 886.2 | 788.5 | 836.3 | 844.6 | 777.7 | 788.4 | 599.1 | 828 | 779.5 | 753.9 | 72.5 | 175.6 | 204.8 | 128.1 | 304.1 | 294.8 | 151.8 | 253.5
891 | 739 | 471.4 | 188.56 | 220.4158 | 288 | 302.4 | 288.1 | 293.8 | 586.6 | 45.4 | 19.9 | 77.3 | 3.6 | 140.2 | 4.9 | 886.3 | 789.1 | 837.5 | 845.2 | 779.6 | 788.6 | 598.9 | 831.6 | 779.5 | 755.1 | 72.7 | 175.9 | 205.3 | 128.4 | 304.6 | 295 | 152 | 253.7
892 | 740 | 471.6 | 188.64 | 220.5093 | 287.6 | 303.7 | 288.8 | 294.2 | 583.4 | 45.4 | 19.9 | 77.4 | 3.8 | 144.5 | 4.1 | 886.4 | 790.5 | 836.2 | 845.6 | 778.9 | 788.2 | 600 | 830.5 | 779.4 | 755.4 | 72.8 | 176.2 | 205.5 | 128.6 | 305 | 295 | 152.2 | 253.9
893 | 741 | 470.5 | 188.2 | 219.995 | 287.7 | 303.5 | 289.4 | 294 | 572.1 | 45.4 | 19.9 | 77.4 | 3.8 | 164.7 | 3.4 | 886.6 | 788.3 | 832.4 | 844.4 | 774.3 | 788.2 | 597.4 | 816.1 | 778 | 752.1 | 73 | 176.4 | 205.8 | 128.8 | 305.2 | 295.2 | 152.5 | 254.1
894 | 742 | 469.9 | 187.96 | 219.7144 | 288 | 304.2 | 290.3 | 293.9 | 555.4 | 45.4 | 19.9 | 77.4 | 3.6 | 186.7 | 4.1 | 886.3 | 783.4 | 829.8 | 842.5 | 770.2 | 789.1 | 594.6 | 800.4 | 776 | 747.8 | 73.1 | 176.7 | 206.3 | 129.1 | 305.6 | 295.9 | 152.7 | 254.3
895 | 743 | 468.3 | 187.32 | 218.9663 | 288.1 | 305.5 | 290.4 | 293.8 | 543.7 | 45.3 | 19.9 | 77.5 | 3.5 | 186.1 | 5.1 | 886.6 | 781.2 | 828.1 | 841.3 | 769.2 | 789.9 | 591 | 793.1 | 774.4 | 745.5 | 73.3 | 176.9 | 206.5 | 129.3 | 305.5 | 295.7 | 152.9 | 254.5
896 | 744 | 469.3 | 187.72 | 219.4339 | 288.5 | 305.1 | 290.2 | 293.7 | 542.2 | 45.2 | 19.9 | 77.5 | 3.7 | 186.2 | 5.7 | 887.5 | 777.7 | 825.7 | 840.2 | 765.1 | 790.7 | 589.8 | 798.3 | 773.1 | 743.6 | 73.4 | 177.2 | 206.8 | 129.5 | 306 | 295.6 | 153.1 | 254.6
897 | 745 | 471.3 | 188.52 | 220.369 | 289.4 | 304.1 | 290.2 | 293.7 | 557.5 | 45.1 | 19.9 | 77.5 | 4 | 193.1 | 6.2 | 888.3 | 775.3 | 826.2 | 839.5 | 762.5 | 791.4 | 586.9 | 807.3 | 772.5 | 742.6 | 73.6 | 177.5 | 207.3 | 129.8 | 306.9 | 295.8 | 153.3 | 254.8
898 | 746 | 470.1 | 188.04 | 219.8079 | 290.6 | 303.9 | 290.6 | 294.3 | 568.2 | 45.1 | 19.9 | 77.6 | 3.7 | 183.1 | 6.5 | 888.5 | 775.6 | 824.9 | 838.6 | 761.4 | 792.2 | 584.8 | 810.2 | 771.9 | 743.5 | 73.7 | 177.8 | 207.8 | 130 | 307.7 | 295.9 | 153.5 | 254.9
899 | 747 | 469.7 | 187.88 | 219.6209 | 292.4 | 305.3 | 291 | 295.3 | 578 | 45.2 | 19.9 | 77.7 | 3.4 | 177.1 | 6.8 | 889.3 | 774.1 | 823.1 | 836.9 | 758.2 | 792.9 | 582.8 | 808.6 | 771.2 | 742.8 | 73.9 | 178.1 | 208.4 | 130.2 | 308.5 | 296 | 153.8 | 255.1
900 | 748 | 471.8 | 188.72 | 220.6028 | 293.5 | 307.8 | 291.3 | 296.3 | 588.5 | 45.3 | 19.9 | 77.8 | 3.6 | 169.6 | 6.9 | 889.9 | 772.1 | 822.3 | 834.9 | 755.4 | 793.7 | 581.5 | 810.5 | 770.3 | 740.8 | 74 | 178.4 | 208.7 | 130.5 | 310.2 | 296.3 | 154 | 255.4
901 | 749 | 470.8 | 188.32 | 220.1352 | 294.3 | 309.8 | 292.5 | 297.6 | 604.1 | 45.5 | 19.9 | 77.9 | 3.3 | 169.2 | 7.1 | 890.5 | 770.8 | 822.1 | 834.4 | 752.9 | 794.2 | 581.8 | 814.4 | 770.2 | 740.7 | 74.2 | 178.6 | 209 | 130.7 | 310.7 | 297.4 | 154.2 | 255.7
902 | 750 | 471.8 | 188.72 | 220.6028 | 294.6 | 310.4 | 294.1 | 299.5 | 606.4 | 45.6 | 19.9 | 78 | 3.5 | 166.1 | 7 | 889.9 | 772.7 | 826.1 | 835.6 | 753.9 | 794.1 | 586.5 | 818.3 | 770.8 | 742 | 74.4 | 178.9 | 209.2 | 130.9 | 311.4 | 297.8 | 154.4 | 255.9
903 | 751 | 470.8 | 188.32 | 220.1352 | 294.8 | 310.8 | 295.2 | 300.6 | 589.6 | 45.6 | 19.8 | 78.1 | 3.6 | 166.7 | 6.6 | 887.9 | 776.8 | 827.7 | 837.6 | 755.2 | 793.2 | 597.9 | 819.6 | 772.4 | 745.9 | 74.5 | 179.2 | 209.4 | 131.2 | 312.6 | 298.5 | 154.7 | 256.3
904 | 752 | 470.9 | 188.36 | 220.182 | 295 | 311.7 | 295.9 | 301.1 | 581 | 45.6 | 19.8 | 78.1 | 4.2 | 173.5 | 6.5 | 886.1 | 780.5 | 827.1 | 838.5 | 755.8 | 791.7 | 605 | 821.7 | 773.7 | 747 | 74.7 | 179.5 | 209.5 | 131.4 | 312.8 | 299.3 | 154.9 | 256.5
905 | 753 | 470.5 | 188.2 | 219.995 | 295.3 | 311.8 | 296.2 | 301.7 | 579.3 | 45.5 | 19.8 | 78.2 | 4.3 | 178.4 | 6.7 | 884.1 | 783.7 | 825.5 | 839.5 | 755.2 | 789.9 | 614.5 | 812.1 | 774.8 | 748.9 | 74.8 | 179.7 | 209.7 | 131.6 | 312.8 | 300.1 | 155.1 | 256.8
906 | 754 | 471.1 | 188.44 | 220.2755 | 295.4 | 311.6 | 296.7 | 301.6 | 567.6 | 45.4 | 19.8 | 78.3 | 4.4 | 172.9 | 6.7 | 882.3 | 785 | 821.7 | 839.2 | 752.9 | 788.3 | 623.8 | 797.8 | 775.5 | 749.5 | 75 | 180 | 210 | 131.9 | 313.2 | 301 | 155.3 | 257.2
907 | 755 | 471.2 | 188.48 | 220.3223 | 295.8 | 311.6 | 297.4 | 301.2 | 549.4 | 45.3 | 19.8 | 78.3 | 4.1 | 164.5 | 5.9 | 881.1 | 785.6 | 818.3 | 839.7 | 751 | 787.1 | 629.9 | 790.3 | 775.9 | 749.6 | 75.1 | 180.2 | 210.2 | 132.1 | 313.4 | 302.1 | 155.6 | 257.4
908 | 756 | 472.7 | 189.08 | 221.0236 | 296.5 | 311.3 | 298.6 | 301.2 | 538.4 | 45.3 | 19.8 | 78.4 | 4 | 152.9 | 5.1 | 880.1 | 786.2 | 816.9 | 840.3 | 750.3 | 786.3 | 632.4 | 793 | 776.3 | 749.9 | 75.3 | 180.5 | 210.5 | 132.3 | 313.8 | 302.5 | 155.8 | 257.7
909 | 757 | 471.8 | 188.72 | 220.6028 | 296.4 | 311 | 299.4 | 301.5 | 543.2 | 45.3 | 19.8 | 78.5 | 4.1 | 160.7 | 4.5 | 880.5 | 787.8 | 816.9 | 840.7 | 750 | 785.3 | 631.6 | 800.4 | 776.6 | 751.5 | 75.4 | 180.7 | 210.8 | 132.6 | 314.2 | 302.8 | 156 | 257.8
910 | 758 | 471.3 | 188.52 | 220.369 | 296.2 | 310.7 | 299.9 | 301.2 | 550.2 | 45.4 | 19.8 | 78.5 | 3.7 | 164.9 | 4.3 | 881.4 | 788.4 | 818.4 | 840.8 | 749.9 | 784.9 | 628 | 804.8 | 776.5 | 752 | 75.6 | 181 | 211.2 | 132.8 | 314.8 | 303.2 | 156.2 | 258
911 | 759 | 471.5 | 188.6 | 220.4625 | 296.7 | 310.5 | 300.3 | 301 | 547 | 45.6 | 19.8 | 78.5 | 3.9 | 168.5 | 4.8 | 881.8 | 787.6 | 818.9 | 840.9 | 748.4 | 784.9 | 624.2 | 797.7 | 775.8 | 749.9 | 75.7 | 181.2 | 211.6 | 133 | 315.6 | 303.8 | 156.5 | 258.3
912 | 760 | 470.9 | 188.36 | 220.182 | 297.2 | 309.6 | 300.1 | 301.2 | 538.4 | 45.7 | 19.8 | 78.6 | 3.8 | 168.1 | 5.1 | 881.9 | 784 | 817.3 | 839.6 | 745.6 | 785.4 | 619 | 793.2 | 774 | 746.3 | 75.9 | 181.5 | 211.8 | 133.3 | 315.6 | 304.2 | 156.7 | 258.6
913 | 761 | 470.4 | 188.16 | 219.9482 | 297.3 | 308.5 | 300.2 | 301.2 | 528.5 | 45.8 | 19.8 | 78.6 | 3.7 | 168.8 | 5 | 881.9 | 783.3 | 819.1 | 840.5 | 749.1 | 785.8 | 616.1 | 792 | 773.4 | 745.7 | 76 | 181.7 | 211.7 | 133.5 | 315.4 | 304.2 | 156.9 | 258.8
914 | 762 | 471.5 | 188.6 | 220.4625 | 297.5 | 307.6 | 299.6 | 301 | 525.9 | 45.9 | 19.8 | 78.6 | 3.6 | 177.5 | 5.2 | 881.7 | 783 | 821.3 | 840.6 | 749 | 785.9 | 612.7 | 788.8 | 772.3 | 744.2 | 76.2 | 182 | 211.8 | 133.8 | 314.9 | 304.3 | 157.1 | 258.9
915 | 763 | 471.7 | 188.68 | 220.556 | 297.1 | 307.6 | 299.1 | 300.2 | 520 | 45.9 | 19.8 | 78.7 | 4.1 | 183.4 | 5.2 | 881.6 | 780.7 | 820 | 839.8 | 746.8 | 786.3 | 608.8 | 780.2 | 770.6 | 741 | 76.3 | 182.2 | 212.2 | 134 | 314.4 | 304.6 | 157.3 | 259.1
916 | 764 | 471.3 | 188.52 | 220.369 | 297.1 | 306.5 | 299.1 | 299.3 | 520.5 | 45.9 | 19.8 | 78.8 | 3.8 | 185.8 | 5.1 | 882 | 776.5 | 816.2 | 837 | 742.6 | 786.7 | 603.7 | 776.7 | 768.9 | 738.5 | 76.5 | 182.5 | 213 | 134.2 | 315.2 | 304.5 | 157.6 | 259.2
917 | 765 | 471.3 | 188.52 | 220.369 | 297.5 | 306.5 | 299.7 | 298.8 | 526.4 | 45.8 | 19.8 | 79 | 3.7 | 181 | 4.9 | 882.4 | 774 | 816.8 | 835.4 | 742.1 | 787.2 | 598.5 | 771.8 | 767.1 | 736.2 | 76.7 | 182.8 | 213.4 | 134.5 | 315.3 | 303.7 | 157.8 | 259.2
918 | 766 | 471.1 | 188.44 | 220.2755 | 297.1 | 307.3 | 300.2 | 298.8 | 514.7 | 45.8 | 19.8 | 79.2 | 3.6 | 167.1 | 4.9 | 881.7 | 769.8 | 815.2 | 834.3 | 739.3 | 787.6 | 594.5 | 761.9 | 765.3 | 732.8 | 76.8 | 183.1 | 213.5 | 134.7 | 315 | 303.6 | 158 | 259.3
919 | 767 | 470.8 | 188.32 | 220.1352 | 296.7 | 307.4 | 300.5 | 299 | 512.8 | 45.8 | 19.8 | 79.4 | 3.8 | 158.1 | 4.7 | 880.7 | 767.5 | 815.2 | 834.2 | 738.9 | 787.5 | 591.2 | 761 | 764.2 | 731.3 | 77 | 183.3 | 213.7 | 134.9 | 315.5 | 303.4 | 158.2 | 259.5
920 | 768 | 470.9 | 188.36 | 220.182 | 296.4 | 307.6 | 300.5 | 299 | 502.8 | 45.8 | 19.8 | 79.5 | 3.9 | 172.5 | 4 | 879.8 | 766.6 | 814.1 | 833.6 | 736.9 | 787.1 | 588 | 759.3 | 763.2 | 729.2 | 77.1 | 183.6 | 213.9 | 135.2 | 315.7 | 303.2 | 158.5 | 259.7
921 | 769 | 472 | 188.8 | 220.6963 | 296.2 | 307.5 | 300.2 | 298.4 | 502.7 | 46 | 19.8 | 79.6 | 4.1 | 210.9 | 3.4 | 879.3 | 766.8 | 813.1 | 834.2 | 736.3 | 786.7 | 585.5 | 755.9 | 762.2 | 727.3 | 77.3 | 183.9 | 214.2 | 135.4 | 315.1 | 302.8 | 158.7 | 259.8
922 | 770 | 471.9 | 188.76 | 220.6496 | 295.5 | 307.2 | 300.2 | 297.8 | 501.4 | 46.1 | 19.8 | 79.7 | 3.4 | 203.6 | 3 | 878 | 768.2 | 811.8 | 834.5 | 736.1 | 785.7 | 586.9 | 757.9 | 762.1 | 727.7 | 77.4 | 184.2 | 214.3 | 135.7 | 314.6 | 302.6 | 158.9 | 259.9
923 | 771 | 471.8 | 188.72 | 220.6028 | 295.3 | 307.5 | 300.4 | 297 | 500.2 | 46.2 | 19.8 | 79.8 | 3.7 | 186.3 | 2.9 | 877 | 765.7 | 809 | 831.4 | 732.1 | 784.9 | 583.9 | 755 | 761 | 725.4 | 77.6 | 184.4 | 214.7 | 135.9 | 314.2 | 301.9 | 159.1 | 259.9
924 | 772 | 471.9 | 188.76 | 220.6496 | 295.1 | 307.1 | 300.3 | 296 | 491.4 | 46.3 | 19.8 | 79.9 | 3.8 | 187.8 | 3.1 | 875.5 | 763.1 | 804.7 | 830.6 | 729.1 | 784.2 | 581.3 | 742.5 | 759.6 | 722.2 | 77.8 | 184.7 | 214.9 | 136.2 | 314.5 | 301.4 | 159.3 | 260
925 | 773 | 471.4 | 188.56 | 220.4158 | 294.2 | 305.8 | 300.1 | 295.2 | 484.1 | 46.4 | 19.8 | 80 | 3.8 | 185.4 | 3.4 | 874.5 | 762.3 | 802.3 | 829.3 | 726.6 | 783.3 | 580.6 | 741.2 | 758.7 | 721 | 77.9 | 185 | 215.2 | 136.4 | 315 | 301 | 159.6 | 260.1
926 | 774 | 471.1 | 188.44 | 220.2755 | 293.7 | 305.4 | 299.8 | 295.6 | 484.3 | 46.5 | 19.8 | 80.2 | 3.8 | 177.7 | 3.8 | 873.7 | 763.7 | 806.5 | 829.7 | 727.7 | 782.6 | 580.7 | 749.8 | 758.5 | 721.7 | 78.1 | 185.2 | 215.4 | 136.7 | 315 | 300.9 | 159.8 | 260.3
927 | 775 | 471.2 | 188.48 | 220.3223 | 293.8 | 305.6 | 299.1 | 296.3 | 493.7 | 46.4 | 19.8 | 80.3 | 3.7 | 168.4 | 4.2 | 873.1 | 767.9 | 812.1 | 830.4 | 732.2 | 781.4 | 583 | 766.3 | 759.5 | 724.5 | 78.2 | 185.5 | 215.6 | 136.9 | 314.4 | 301 | 160 | 260.3
928 | 776 | 471.5 | 188.6 | 220.4625 | 293.9 | 305.3 | 298.8 | 296.4 | 512 | 46.4 | 19.8 | 80.5 | 4 | 167.6 | 4.2 | 873.1 | 771.5 | 815 | 831.7 | 734 | 780.1 | 587 | 784.2 | 760.9 | 727.6 | 78.4 | 185.7 | 215.9 | 137.1 | 314.4 | 300.9 | 160.2 | 260.5
929 | 777 | 471.4 | 188.56 | 220.4158 | 293.7 | 305.4 | 297.7 | 295.9 | 525.9 | 46.4 | 19.8 | 80.7 | 3.3 | 170.6 | 4 | 873.6 | 775 | 816.7 | 833.3 | 734.8 | 778.7 | 592 | 795.4 | 762.6 | 730.5 | 78.5 | 186 | 216 | 137.4 | 314.9 | 300.5 | 160.4 | 260.6
930 | 778 | 471.7 | 188.68 | 220.556 | 293.8 | 305.4 | 296.6 | 295.5 | 537.7 | 46.4 | 19.8 | 80.9 | 3.6 | 176.7 | 3.9 | 874 | 778.6 | 820.1 | 834 | 735.8 | 777.5 | 594.4 | 806.9 | 764 | 733.4 | 78.7 | 186.2 | 216.3 | 137.6 | 314.8 | 300 | 160.7 | 260.7
931 | 779 | 472 | 188.8 | 220.6963 | 293.4 | 305.2 | 296.1 | 295.5 | 540.5 | 46.5 | 19.8 | 81 | 4.2 | 179.4 | 4.1 | 873.5 | 782.2 | 825.9 | 835.5 | 740.8 | 776.1 | 597.5 | 813.3 | 765.7 | 737.1 | 78.9 | 186.4 | 216.6 | 137.8 | 314.4 | 299.9 | 160.9 | 261
932 | 780 | 471.5 | 188.6 | 220.4625 | 293.3 | 304.9 | 296.6 | 295.7 | 531.8 | 46.5 | 19.8 | 81.1 | 3.8 | 173.7 | 4.2 | 872.8 | 785 | 828.4 | 836.4 | 745.1 | 774.6 | 604.5 | 809.7 | 767.1 | 739.8 | 79 | 186.6 | 216.8 | 138.1 | 313.8 | 299.9 | 161.1 | 261.1
933 | 781 | 471.7 | 188.68 | 220.556 | 293.6 | 305.2 | 296.9 | 295.6 | 526.6 | 46.6 | 19.8 | 81.2 | 3.8 | 174.7 | 4 | 872.1 | 787.7 | 828.6 | 836.4 | 747 | 773.1 | 616.4 | 809.5 | 768.9 | 742.7 | 79.2 | 186.9 | 216.9 | 138.3 | 313.4 | 300 | 161.3 | 261.4
934 | 782 | 472.2 | 188.88 | 220.7898 | 293.5 | 305.4 | 296.8 | 295.1 | 529.6 | 46.6 | 19.8 | 81.3 | 3.7 | 175.4 | 3.9 | 872 | 791.8 | 831.3 | 836 | 750 | 772.1 | 624.4 | 803.1 | 770.2 | 746 | 79.4 | 187.1 | 217.2 | 138.6 | 313.5 | 299.9 | 161.6 | 261.5
935 | 783 | 471.5 | 188.6 | 220.4625 | 293.3 | 305.6 | 296.1 | 295 | 532.1 | 46.7 | 19.8 | 81.3 | 3.6 | 174.7 | 3.8 | 872.2 | 794.5 | 832.9 | 837.5 | 751.3 | 771.3 | 627.9 | 811 | 771.5 | 747.9 | 79.5 | 187.3 | 217.5 | 138.8 | 313.6 | 300 | 161.7 | 261.6
936 | 784 | 470.4 | 188.16 | 219.9482 | 292.9 | 305.5 | 295.8 | 295.2 | 544.5 | 46.8 | 19.8 | 81.3 | 3.5 | 175.8 | 4 | 874 | 795.7 | 832.2 | 838.5 | 751.2 | 770.7 | 625.2 | 816.3 | 772.3 | 748.4 | 79.7 | 187.5 | 217.8 | 139 | 313.6 | 300.4 | 162 | 261.8
937 | 785 | 469.4 | 187.76 | 219.4806 | 292.8 | 305.5 | 296.4 | 295.2 | 553.2 | 46.8 | 19.8 | 81.3 | 3.3 | 180.6 | 4.2 | 874.5 | 795.7 | 830.8 | 839.6 | 750.1 | 770.4 | 625.6 | 818.6 | 773.5 | 750.3 | 79.9 | 187.7 | 217.9 | 139.3 | 313.8 | 300.6 | 162.2 | 261.9
938 | 786 | 469.8 | 187.92 | 219.6677 | 292.5 | 304.8 | 297 | 295.2 | 545.9 | 46.8 | 19.8 | 81.3 | 3.2 | 171.6 | 4.4 | 874.2 | 797.4 | 831.5 | 840.2 | 752.5 | 770.4 | 629.6 | 818.9 | 774.8 | 752.3 | 80 | 187.9 | 218.2 | 139.5 | 313.6 | 300.8 | 162.4 | 262.1
939 | 787 | 471.2 | 188.48 | 220.3223 | 292.4 | 304.5 | 296.9 | 294.9 | 539.9 | 46.7 | 19.8 | 81.4 | 3.6 | 165.2 | 4.7 | 873.6 | 797.4 | 828.9 | 840.5 | 753.6 | 770.3 | 635 | 818.3 | 776 | 754.9 | 80.2 | 188.1 | 218.3 | 139.7 | 313.1 | 301 | 162.6 | 262.3
940 | 788 | 470.1 | 188.04 | 219.8079 | 292.5 | 304.4 | 296.3 | 294.7 | 538.1 | 46.6 | 19.8 | 81.4 | 3.7 | 167.4 | 4.8 | 874.5 | 798.7 | 826 | 839.6 | 752.8 | 770.1 | 639.6 | 811.9 | 776.8 | 756.3 | 80.4 | 188.4 | 218.6 | 140 | 313 | 301.3 | 162.8 | 262.4
941 | 789 | 470.5 | 188.2 | 219.995 | 293.1 | 304.1 | 295.8 | 294.6 | 534 | 46.5 | 19.8 | 81.3 | 3.4 | 167.3 | 4.7 | 876 | 799.4 | 825.5 | 840.3 | 753.4 | 770.2 | 640.2 | 812.1 | 777.6 | 757 | 80.5 | 188.6 | 218.8 | 140.2 | 313 | 301.3 | 163.1 | 262.6
942 | 790 | 470.5 | 188.2 | 219.995 | 293.7 | 303.8 | 296.6 | 294.8 | 540.8 | 46.4 | 19.8 | 81.3 | 3.2 | 167.1 | 4.6 | 877.1 | 799.9 | 826.1 | 841.7 | 752.8 | 770.6 | 637.8 | 815.2 | 778.4 | 757.7 | 80.7 | 188.8 | 219 | 140.5 | 313.2 | 301.3 | 163.3 | 262.8
943 | 791 | 471.4 | 188.56 | 220.4158 | 294.2 | 302.7 | 297.2 | 294.9 | 549.6 | 46.4 | 19.7 | 81.3 | 3.1 | 170 | 4.5 | 878.2 | 797.7 | 823.8 | 841.5 | 750.3 | 771.6 | 633 | 814.5 | 778.2 | 756.4 | 80.9 | 189 | 219.3 | 140.7 | 313.5 | 301.4 | 163.5 | 262.8
944 | 792 | 471.8 | 188.72 | 220.6028 | 295.7 | 301.9 | 297.6 | 295.1 | 552 | 46.4 | 19.7 | 81.3 | 3.1 | 169 | 4.4 | 879.4 | 797.4 | 824.8 | 842.5 | 749.8 | 772.6 | 630 | 816.1 | 778.7 | 757.3 | 81 | 189.3 | 219.7 | 141 | 313.6 | 301.9 | 163.7 | 263
945 | 793 | 471.7 | 188.68 | 220.556 | 297.3 | 301.9 | 297.9 | 295.3 | 557.4 | 46.5 | 19.7 | 81.3 | 3.3 | 172.6 | 4.2 | 880.1 | 796.4 | 822.6 | 842.6 | 748.4 | 773.5 | 629.3 | 818.5 | 779.4 | 759.6 | 81.2 | 189.5 | 220 | 141.2 | 313.5 | 302.5 | 163.9 | 263.2
946 | 794 | 471.6 | 188.64 | 220.5093 | 298 | 303.2 | 298 | 295.4 | 549.9 | 46.6 | 19.7 | 81.3 | 3.4 | 173.4 | 4.2 | 880.6 | 792.4 | 819.5 | 842.2 | 744.6 | 774.7 | 624.1 | 807.7 | 778.5 | 755.4 | 81.4 | 189.7 | 220.1 | 141.4 | 313.1 | 302.6 | 164.2 | 263.3
947 | 795 | 471.2 | 188.48 | 220.3223 | 299.2 | 304.7 | 298 | 295.4 | 543.9 | 46.6 | 19.7 | 81.3 | 3.4 | 170.9 | 4.2 | 881.9 | 790.4 | 823 | 841.8 | 746.9 | 775.8 | 619.7 | 810.7 | 778.3 | 754.8 | 81.5 | 190 | 220.4 | 141.7 | 313 | 302.5 | 164.4 | 263.5
948 | 796 | 471.5 | 188.6 | 220.4625 | 300.4 | 304.8 | 297.6 | 295.3 | 546 | 46.7 | 19.7 | 81.3 | 3.6 | 170.3 | 4.3 | 882.5 | 787.8 | 822.4 | 841.4 | 744.2 | 777.1 | 615.4 | 801.1 | 777.2 | 752.2 | 81.7 | 190.2 | 220.8 | 141.9 | 313 | 302.2 | 164.6 | 263.5
949 | 797 | 472 | 188.8 | 220.6963 | 301.5 | 304.7 | 297.5 | 295.7 | 546.9 | 46.7 | 19.7 | 81.4 | 3.6 | 168.2 | 4.1 | 881.9 | 783.1 | 817.7 | 838.8 | 741.1 | 778.3 | 609.7 | 789.1 | 775.8 | 749.5 | 81.9 | 190.4 | 221.2 | 142.2 | 313.2 | 302.4 | 164.8 | 263.6
950 | 798 | 472.5 | 189 | 220.9301 | 302.1 | 305.5 | 297.9 | 296.5 | 535.3 | 46.8 | 19.7 | 81.4 | 3.7 | 164.1 | 3.9 | 880.1 | 776.4 | 810.2 | 836.1 | 736.2 | 779.6 | 605 | 765.9 | 773.7 | 744.2 | 82 | 190.7 | 221.6 | 142.4 | 314 | 302.4 | 165 | 263.8
951 | 799 | 471.9 | 188.76 | 220.6496 | 302.9 | 306.7 | 298.7 | 297 | 523 | 46.8 | 19.7 | 81.4 | 3.7 | 162.6 | 4 | 878.1 | 770.2 | 805 | 833.2 | 731.5 | 780.8 | 600.2 | 752.7 | 771.7 | 740.2 | 82.2 | 190.9 | 221.8 | 142.7 | 314.5 | 302.4 | 165.3 | 263.9
952 | 800 | 472.1 | 188.84 | 220.7431 | 304.6 | 306.9 | 298.9 | 297.5 | 508.2 | 46.8 | 19.7 | 81.5 | 3.6 | 163.3 | 4.6 | 876.1 | 764.2 | 800 | 830.1 | 727.5 | 781.8 | 592.7 | 742.9 | 769.6 | 736.5 | 82.4 | 191.2 | 222 | 142.9 | 315 | 302.6 | 165.5 | 264
953 | 801 | 472.6 | 189.04 | 220.9769 | 305.7 | 307.2 | 299.9 | 297.7 | 498.3 | 46.8 | 19.7 | 81.5 | 3.7 | 164.1 | 5.1 | 873.1 | 756.1 | 790.5 | 825.3 | 721.3 | 782.8 | 586.1 | 721.9 | 767.4 | 731.3 | 82.5 | 191.5 | 222.4 | 143.1 | 316.4 | 302.7 | 165.7 | 264.2
954 | 802 | 472.1 | 188.84 | 220.7431 | 306.5 | 307.9 | 300.8 | 298.1 | 497.2 | 46.8 | 19.7 | 81.6 | 4 | 166.1 | 5.3 | 870.3 | 750.6 | 784.5 | 822.5 | 717 | 783.6 | 578.8 | 713.7 | 765.2 | 727.2 | 82.7 | 191.7 | 223 | 143.4 | 316.9 | 302.8 | 165.9 | 264.4
955 | 803 | 472.4 | 188.96 | 220.8834 | 307.9 | 308.3 | 302.3 | 298.4 | 503 | 46.9 | 19.7 | 81.8 | 3.9 | 176.5 | 5.4 | 867.7 | 745.3 | 781 | 820.9 | 713.2 | 784.1 | 575.6 | 715.3 | 763.3 | 724.4 | 82.9 | 192 | 223.7 | 143.6 | 318.2 | 302.6 | 166.1 | 264.6
956 | 804 | 473.2 | 189.28 | 221.2574 | 308.8 | 308.6 | 303.7 | 299.8 | 505.1 | 47 | 19.7 | 81.9 | 3.8 | 163.6 | 5.4 | 866.5 | 743.3 | 786.6 | 820.2 | 712.5 | 784.3 | 572.3 | 725.3 | 762.2 | 722.6 | 83.1 | 192.3 | 224.1 | 143.9 | 319 | 302.8 | 166.3 | 264.8
957 | 805 | 473.1 | 189.24 | 221.2107 | 309.8 | 308.6 | 304.1 | 301.6 | 509.5 | 47.1 | 19.7 | 82.1 | 3.9 | 158.7 | 5.5 | 864.9 | 741.1 | 791.5 | 820.2 | 712.2 | 784.4 | 570.2 | 727.6 | 760.8 | 719.9 | 83.2 | 192.6 | 224.5 | 144.1 | 319.9 | 303 | 166.6 | 264.9
958 | 806 | 471.8 | 188.72 | 220.6028 | 310.4 | 308.6 | 304.4 | 303.7 | 504.7 | 47.1 | 19.7 | 82.3 | 3.8 | 162.3 | 5.5 | 862.9 | 738 | 792.5 | 819.2 | 710.5 | 784.4 | 567.9 | 722.2 | 759.2 | 717.2 | 83.4 | 192.9 | 225 | 144.3 | 320.8 | 303.6 | 166.8 | 265.1
959 | 807 | 473 | 189.2 | 221.1639 | 309.7 | 309.1 | 304.8 | 305.4 | 497.1 | 47 | 19.7 | 82.4 | 3.6 | 166.9 | 5.2 | 860.8 | 735 | 790 | 818.2 | 708 | 784.3 | 564.4 | 711.7 | 757.3 | 713.6 | 83.6 | 193.2 | 225 | 144.6 | 321.4 | 304.4 | 167 | 265.3
960 | 808 | 470.9 | 188.36 | 220.182 | 310.4 | 310 | 304.6 | 306.1 | 494.2 | 46.9 | 19.7 | 82.5 | 3.7 | 165.9 | 5.1 | 859.3 | 734.7 | 787 | 818.9 | 705.9 | 783.7 | 564.9 | 707.2 | 756 | 711 | 83.7 | 193.5 | 225 | 144.8 | 321.6 | 305.3 | 167.2 | 265.6
961 | 809 | 470.6 | 188.24 | 220.0417 | 311.4 | 310.5 | 304.6 | 306 | 495 | 46.9 | 19.7 | 82.6 | 3.9 | 167 | 5 | 858 | 736.6 | 789 | 818.9 | 705.4 | 782.8 | 569.3 | 712.3 | 755.5 | 710.3 | 83.9 | 193.7 | 225.2 | 145 | 321.9 | 305.9 | 167.4 | 265.9
962 | 810 | 470.4 | 188.16 | 219.9482 | 312.2 | 310.2 | 304.1 | 305.6 | 490.8 | 47 | 19.7 | 82.6 | 3.6 | 166.8 | 5.2 | 857.3 | 738.1 | 791.7 | 820.4 | 705.5 | 781.5 | 572.9 | 714.5 | 755.4 | 709.6 | 84.1 | 194 | 225.3 | 145.3 | 322.1 | 306.3 | 167.7 | 266.2
963 | 811 | 473.1 | 189.24 | 221.2107 | 312.7 | 309.5 | 304.1 | 305.3 | 506.7 | 47.1 | 19.7 | 82.7 | 3.8 | 168.7 | 5.6 | 858.3 | 741.7 | 798.5 | 821.2 | 708.8 | 780.2 | 576.5 | 736.5 | 756.5 | 712.6 | 84.2 | 194.3 | 225.7 | 145.5 | 322.2 | 306.2 | 167.9 | 266.3
964 | 812 | 472.1 | 188.84 | 220.7431 | 314 | 308.2 | 304.4 | 305.3 | 522 | 47.2 | 19.7 | 82.9 | 3.8 | 168.3 | 5.9 | 859 | 743.8 | 799.7 | 821.2 | 708.1 | 778.9 | 575.3 | 745.7 | 756.1 | 712.4 | 84.4 | 194.5 | 226.1 | 145.8 | 322.5 | 306 | 168.1 | 266.4
965 | 813 | 471.4 | 188.56 | 220.4158 | 315.5 | 307.1 | 304 | 305.3 | 522.1 | 47.2 | 19.7 | 83 | 3.5 | 168.4 | 6.3 | 859.4 | 743.8 | 801.2 | 822.4 | 708.2 | 777.8 | 574.9 | 749.6 | 755.7 | 712 | 84.6 | 194.8 | 226.5 | 146 | 323.1 | 306.1 | 168.3 | 266.5
966 | 814 | 471.7 | 188.68 | 220.556 | 315.8 | 306.6 | 303.3 | 305.5 | 517.1 | 47.3 | 19.7 | 83.2 | 3.5 | 170.1 | 6.4 | 859.3 | 743.4 | 802.3 | 823.4 | 707.1 | 777.1 | 572 | 751.5 | 754.1 | 709.7 | 84.8 | 195.1 | 226.9 | 146.2 | 323 | 305.9 | 168.5 | 266.6
967 | 815 | 471.9 | 188.76 | 220.6496 | 315.1 | 305.8 | 303.9 | 306 | 521.9 | 47.4 | 19.7 | 83.3 | 3.8 | 171.4 | 6.3 | 859.5 | 745.1 | 805.8 | 823.5 | 706.8 | 776.1 | 575.3 | 766.6 | 754.6 | 712.3 | 84.9 | 195.4 | 227 | 146.4 | 323.7 | 305.5 | 168.8 | 266.7
968 | 816 | 470.8 | 188.32 | 220.1352 | 315.3 | 305.2 | 304.4 | 306.8 | 528 | 47.5 | 19.7 | 83.5 | 3.9 | 172 | 6.1 | 859.1 | 744.9 | 806.9 | 823.2 | 706.9 | 775.3 | 574.5 | 764.3 | 753.9 | 711.4 | 85.1 | 195.6 | 227.3 | 146.7 | 323.9 | 306.1 | 169 | 267
969 | 817 | 471.8 | 188.72 | 220.6028 | 314.6 | 305.3 | 304.3 | 307.4 | 515.4 | 47.6 | 19.7 | 83.7 | 3.8 | 167.9 | 6 | 858.5 | 743.8 | 806.2 | 822.6 | 704.3 | 774.5 | 572.1 | 758.1 | 753 | 710 | 85.3 | 195.9 | 227.7 | 146.9 | 323.6 | 306.4 | 169.2 | 267.1
970 | 818 | 471.6 | 188.64 | 220.5093 | 313.3 | 305.2 | 305.5 | 308 | 523.1 | 47.7 | 19.7 | 83.9 | 3.8 | 166.4 | 5.7 | 858.8 | 745.9 | 807.7 | 824 | 705.1 | 773.4 | 572.9 | 763.1 | 753.1 | 712.3 | 85.4 | 196.2 | 228.1 | 147.1 | 323.2 | 306.2 | 169.4 | 267.2
971 | 819 | 471.1 | 188.44 | 220.2755 | 312.4 | 306.2 | 306.5 | 308.4 | 521.4 | 47.7 | 19.6 | 84 | 3.7 | 171.5 | 5.2 | 859.4 | 747.3 | 806.9 | 824.7 | 704.4 | 772.5 | 571.1 | 765.5 | 753.2 | 712.4 | 85.6 | 196.4 | 228.4 | 147.4 | 323.3 | 305.9 | 169.6 | 267.3
972 | 820 | 471 | 188.4 | 220.2287 | 311.6 | 307.1 | 307.1 | 308.3 | 521.9 | 47.8 | 19.6 | 84.1 | 3.5 | 167.9 | 4.8 | 860.2 | 750.5 | 809.5 | 826 | 706.4 | 771.2 | 573.6 | 778.9 | 754.6 | 716.4 | 85.8 | 196.7 | 228.6 | 147.6 | 323.6 | 305.9 | 169.9 | 267.5
973 | 821 | 472.4 | 188.96 | 220.8834 | 312.5 | 308.1 | 307.7 | 308.4 | 524.3 | 47.8 | 19.6 | 84.2 | 4 | 170.1 | 4.8 | 861.1 | 754.7 | 815.7 | 827.5 | 710.7 | 770.1 | 575.8 | 774.6 | 755.1 | 717.7 | 86 | 197 | 228.8 | 147.9 | 324.2 | 306 | 170.1 | 267.7
974 | 822 | 472.6 | 189.04 | 220.9769 | 312.8 | 309.6 | 307.6 | 309.1 | 525.6 | 47.9 | 19.7 | 84.3 | 3.7 | 173.9 | 5 | 861.8 | 758 | 818.8 | 826 | 714.6 | 768.9 | 579 | 780 | 755.4 | 717.8 | 86.1 | 197.3 | 228.8 | 148.1 | 324.1 | 306 | 170.3 | 267.9
975 | 823 | 471.9 | 188.76 | 220.6496 | 312.8 | 310.9 | 307.2 | 309.7 | 529.7 | 47.9 | 19.7 | 84.4 | 3.6 | 173.6 | 5.2 | 862.4 | 760.3 | 817.3 | 828.9 | 713.5 | 767.7 | 579.6 | 780.3 | 755.6 | 717.6 | 86.3 | 197.5 | 229.1 | 148.3 | 324 | 306.1 | 170.5 | 268.1
976 | 824 | 470.9 | 188.36 | 220.182 | 313.4 | 311.4 | 306.8 | 309.7 | 537.3 | 48 | 19.6 | 84.3 | 3.7 | 174.1 | 5.7 | 863.1 | 761.9 | 813.5 | 829.6 | 712.6 | 766.6 | 581 | 783.2 | 756 | 719.3 | 86.5 | 197.8 | 229.6 | 148.6 | 324.1 | 306 | 170.8 | 268.3
977 | 825 | 471.7 | 188.68 | 220.556 | 313.7 | 311.5 | 306.4 | 309.3 | 534.1 | 48.1 | 19.6 | 84.4 | 4 | 177 | 6 | 862.7 | 765 | 815.4 | 828.9 | 715.8 | 765.4 | 589.1 | 789.2 | 757.7 | 723 | 86.7 | 198 | 229.7 | 148.8 | 324.8 | 306.4 | 171 | 268.5
978 | 826 | 468.5 | 187.4 | 219.0598 | 314.9 | 311.6 | 306.9 | 308.9 | 533.3 | 48.1 | 19.6 | 84.4 | 4 | 176.8 | 5.8 | 863.2 | 769.6 | 814.7 | 831.4 | 717.4 | 764.1 | 597.4 | 793.1 | 759.9 | 726.7 | 86.8 | 198.3 | 229.9 | 149 | 325.2 | 306.9 | 171.2 | 268.7
979 | 827 | 469.1 | 187.64 | 219.3403 | 315.3 | 311.1 | 307.6 | 308.4 | 534.7 | 48.1 | 19.6 | 84.4 | 3.8 | 176.7 | 5.7 | 863.5 | 773.6 | 814.7 | 831.9 | 717.7 | 762.8 | 607.1 | 795.6 | 761.6 | 729.3 | 87 | 198.5 | 230.1 | 149.3 | 325.5 | 307.3 | 171.4 | 269
980 | 828 | 469.5 | 187.8 | 219.5274 | 315.2 | 310.7 | 307.8 | 308.3 | 536.1 | 48.1 | 19.6 | 84.4 | 4.1 | 175.9 | 5.5 | 862.7 | 774.7 | 818.8 | 834 | 721.3 | 761.6 | 614.9 | 793.5 | 763.5 | 732.3 | 87.2 | 198.7 | 230.3 | 149.5 | 325.3 | 308.1 | 171.6 | 269.3
981 | 829 | 471.9 | 188.76 | 220.6496 | 314.6 | 309.9 | 308 | 308.1 | 532.3 | 48.1 | 19.6 | 84.3 | 3.9 | 176.5 | 5.3 | 862.4 | 776.9 | 819.8 | 832 | 724.8 | 760.5 | 623.4 | 789.3 | 765.3 | 735.3 | 87.4 | 199 | 230.5 | 149.7 | 325 | 308.7 | 171.8 | 269.6
982 | 830 | 471.8 | 188.72 | 220.6028 | 313.9 | 309.4 | 308.5 | 307.7 | 532 | 48.1 | 19.6 | 84.3 | 3.6 | 176.4 | 5.1 | 862.3 | 779.9 | 822.5 | 834.6 | 727.7 | 759.6 | 629.9 | 790.7 | 767.4 | 737.7 | 87.5 | 199.2 | 230.6 | 150 | 324.7 | 308.5 | 172.1 | 269.7
983 | 831 | 472.4 | 188.96 | 220.8834 | 314.2 | 308.5 | 309.4 | 307.3 | 528.2 | 48.1 | 19.6 | 84.4 | 3.7 | 173 | 5 | 862.3 | 781.4 | 823 | 838.3 | 729.6 | 758.8 | 635.6 | 785.8 | 768.9 | 739.7 | 87.7 | 199.4 | 230.9 | 150.2 | 324.9 | 308.6 | 172.3 | 269.9
984 | 832 | 472.8 | 189.12 | 221.0704 | 314.3 | 307.4 | 310.2 | 307 | 523.1 | 48.1 | 19.6 | 84.4 | 3.3 | 175.4 | 5.2 | 862.9 | 783.7 | 824.4 | 836.9 | 733.5 | 758.1 | 638.1 | 794.2 | 770 | 741.2 | 87.9 | 199.6 | 231 | 150.4 | 325.5 | 309.2 | 172.5 | 270.2
985 | 833 | 472.5 | 189 | 220.9301 | 314.4 | 306.7 | 310.4 | 307.1 | 528.2 | 48.1 | 19.6 | 84.4 | 3.2 | 177.1 | 5.3 | 864.4 | 787 | 827.2 | 837.3 | 736.4 | 757.8 | 636.4 | 799.3 | 771.2 | 743.7 | 88.1 | 199.9 | 231.3 | 150.7 | 326.4 | 309.3 | 172.7 | 270.4
986 | 834 | 470.7 | 188.28 | 220.0885 | 314 | 306.2 | 310.7 | 306.5 | 543.4 | 48.2 | 19.6 | 84.5 | 3.4 | 176 | 5.3 | 866.3 | 787.4 | 826.2 | 836.9 | 735.4 | 757.9 | 630.2 | 808.7 | 770.2 | 743.4 | 88.2 | 200.1 | 231.7 | 150.9 | 326.6 | 309.1 | 173 | 270.5
987 | 835 | 471.5 | 188.6 | 220.4625 | 313.5 | 304.9 | 310.9 | 305.7 | 551.1 | 48.3 | 19.6 | 84.5 | 3.8 | 178.7 | 4.9 | 867.9 | 786.7 | 821.5 | 838.3 | 732.8 | 758.2 | 627.1 | 811.3 | 770 | 744.3 | 88.4 | 200.3 | 231.9 | 151.2 | 327.1 | 309 | 173.1 | 270.5
988 | 836 | 471.5 | 188.6 | 220.4625 | 313.4 | 304.4 | 310.8 | 305.6 | 576.5 | 48.4 | 19.6 | 84.5 | 3.8 | 187.1 | 4.5 | 867.8 | 779.8 | 815.4 | 835.4 | 728.3 | 759 | 620.6 | 801 | 767.4 | 740.9 | 88.6 | 200.5 | 232.5 | 151.4 | 327.8 | 309.3 | 173.4 | 270.6
989 | 837 | 470.6 | 188.24 | 220.0417 | 313.9 | 304.3 | 310.9 | 306.4 | 576.3 | 48.4 | 19.6 | 84.4 | 3.8 | 186.5 | 4 | 866.7 | 770 | 810.5 | 831.2 | 724.1 | 760.3 | 610.9 | 787.6 | 762.9 | 736.5 | 88.8 | 200.8 | 233.5 | 151.6 | 328 | 309.5 | 173.6 | 270.7
990 | 838 | 471.7 | 188.68 | 220.556 | 314.9 | 303.3 | 311 | 307.3 | 575.2 | 48.5 | 19.6 | 84.3 | 3.9 | 175 | 3.7 | 866.5 | 764.2 | 810.2 | 831.8 | 722.6 | 761.4 | 604.5 | 794.7 | 761 | 736 | 89 | 201.1 | 233.9 | 151.9 | 328.9 | 309.6 | 173.8 | 270.9
991 | 839 | 471.9 | 188.76 | 220.6496 | 315.8 | 302.8 | 311.3 | 308.2 | 576 | 48.5 | 19.6 | 84.3 | 3.7 | 173.3 | 3.8 | 866.8 | 764.3 | 816 | 831.9 | 726.6 | 762.3 | 601.5 | 806.1 | 761.4 | 738.1 | 89.1 | 201.3 | 234 | 152.1 | 328.8 | 309.6 | 174.1 | 271.1
992 | 840 | 471.7 | 188.68 | 220.556 | 316.3 | 303.5 | 312.1 | 309.7 | 580.5 | 48.6 | 19.6 | 84.3 | 3.6 | 175.4 | 3.8 | 867.5 | 767.1 | 817.9 | 833.8 | 727.9 | 762.8 | 602.6 | 809.4 | 763.6 | 741.4 | 89.3 | 201.6 | 234.1 | 152.3 | 329 | 309.8 | 174.3 | 271.2
993 | 841 | 472.5 | 189 | 220.9301 | 317.4 | 304.2 | 312.2 | 310.9 | 583.4 | 48.7 | 19.6 | 84.3 | 3.6 | 178.3 | 3.7 | 868.2 | 771.5 | 818.7 | 835.3 | 728.1 | 762.9 | 610 | 814.6 | 767.1 | 744.8 | 89.5 | 201.8 | 234.3 | 152.6 | 329.3 | 310.1 | 174.5 | 271.4
994 | 842 | 473 | 189.2 | 221.1639 | 318.2 | 304.8 | 311.9 | 311.8 | 593.9 | 48.7 | 19.6 | 84.3 | 3.3 | 182.5 | 3.3 | 868.5 | 775.4 | 821 | 836.8 | 729.7 | 762.8 | 614.4 | 818.5 | 769.8 | 747.3 | 89.7 | 202.1 | 234.7 | 152.8 | 329.4 | 310.6 | 174.8 | 271.6
995 | 843 | 473.2 | 189.28 | 221.2574 | 318.6 | 306.4 | 311.5 | 312.3 | 598.2 | 48.8 | 19.6 | 84.2 | 3.5 | 183.4 | 3.3 | 869.2 | 778.5 | 823.2 | 838.6 | 731.8 | 762.9 | 616.2 | 821.4 | 771.9 | 748.7 | 89.8 | 202.3 | 234.9 | 153.1 | 329.7 | 311.3 | 175 | 271.9
996 | 844 | 471.6 | 188.64 | 220.5093 | 318.6 | 308.7 | 311 | 312 | 605.9 | 48.8 | 19.6 | 84.2 | 3.7 | 184.1 | 3.5 | 869.9 | 781.6 | 824.3 | 840.2 | 732.1 | 763.3 | 622.4 | 825.7 | 773.8 | 750.9 | 90 | 202.6 | 235.1 | 153.3 | 329.8 | 311.6 | 175.2 | 272
997 | 845 | 472.9 | 189.16 | 221.1171 | 319.8 | 310.5 | 310.6 | 311.5 | 621.1 | 48.9 | 19.6 | 84.2 | 3.6 | 183.3 | 3.8 | 871.3 | 785.1 | 827.8 | 838.9 | 734.6 | 764 | 620.5 | 831 | 774.7 | 752.3 | 90.2 | 202.8 | 235.6 | 153.5 | 330.3 | 312 | 175.4 | 272.2
998 | 846 | 472.1 | 188.84 | 220.7431 | 320.5 | 311.9 | 310.8 | 311.3 | 612.1 | 48.9 | 19.6 | 84.2 | 3.8 | 181.2 | 3.7 | 871.8 | 784.2 | 831.9 | 837.9 | 735.7 | 765.4 | 614.9 | 831.8 | 772.6 | 752.7 | 90.4 | 203.1 | 235.7 | 153.8 | 330.7 | 312.3 | 175.6 | 272.4
999 | 847 | 472.8 | 189.12 | 221.0704 | 320.8 | 314 | 311.2 | 311.6 | 608 | 48.8 | 19.6 | 84.2 | 3.8 | 175.7 | 3.8 | 871.4 | 784 | 832.2 | 838.3 | 736 | 766.5 | 616.2 | 831.7 | 774.1 | 755.1 | 90.6 | 203.4 | 235.8 | 154 | 331 | 312.8 | 175.9 | 272.6
1000 | 848 | 472.8 | 189.12 | 221.0704 | 321.6 | 314.5 | 310.9 | 312 | 620.1 | 48.8 | 19.6 | 84.2 | 3.6 | 169.8 | 3.9 | 871.8 | 784.5 | 831.8 | 841.5 | 737.6 | 767.2 | 618.2 | 830.5 | 775.5 | 756.1 | 90.7 | 203.6 | 236.2 | 154.2 | 330.8 | 312.8 | 176.1 | 272.8
1001 | 849 | 472.1 | 188.84 | 220.7431 | 321.4 | 314.3 | 310.4 | 312.1 | 619.4 | 48.8 | 19.6 | 84.2 | 3.5 | 174.7 | 4.4 | 873 | 782.2 | 826.6 | 835.6 | 734.8 | 768.1 | 613.1 | 824.4 | 772.4 | 753.6 | 90.9 | 203.9 | 236.8 | 154.5 | 330.7 | 312.7 | 176.3 | 272.9
1002 | 850 | 473.6 | 189.44 | 221.4444 | 320.6 | 315.7 | 310.1 | 312.2 | 605 | 48.8 | 19.6 | 84.2 | 3.5 | 172.8 | 4.8 | 873 | 774.6 | 820.9 | 836.1 | 731.9 | 769.4 | 604.7 | 808 | 768.3 | 749.8 | 91.1 | 204.1 | 237.3 | 154.7 | 330.7 | 313.1 | 176.5 | 273.1
1003 | 851 | 473.4 | 189.36 | 221.3509 | 319.7 | 317.6 | 310.1 | 312.6 | 591.5 | 48.9 | 19.6 | 84.3 | 3.6 | 169.3 | 5 | 872.7 | 770.2 | 822.4 | 833.1 | 730 | 770.9 | 598.1 | 810 | 765 | 747.6 | 91.3 | 204.4 | 237.8 | 154.9 | 331 | 313.4 | 176.8 | 273.4
1004 | 852 | 472.2 | 188.88 | 220.7898 | 319.4 | 319.3 | 310.4 | 313.4 | 583.3 | 48.9 | 19.6 | 84.4 | 3.5 | 159.3 | 4.9 | 873.5 | 772.4 | 825.9 | 836.5 | 732.8 | 771.8 | 601.5 | 814.5 | 766.8 | 751 | 91.5 | 204.7 | 237.7 | 155.1 | 331.2 | 314 | 176.9 | 273.6
1005 | 853 | 472.6 | 189.04 | 220.9769 | 319.7 | 320.1 | 310.4 | 314.2 | 582.8 | 49 | 19.6 | 84.5 | 3.9 | 173 | 5.1 | 874.6 | 775 | 829.9 | 838.2 | 735.1 | 771.9 | 605.4 | 814.8 | 769.6 | 751.8 | 91.7 | 204.9 | 237.8 | 155.3 | 330.7 | 314.4 | 177.2 | 273.9
1006 | 854 | 473.3 | 189.32 | 221.3042 | 319.9 | 320.1 | 310.3 | 314.6 | 582 | 48.9 | 19.6 | 84.6 | 3.8 | 176.1 | 5.3 | 875.5 | 776.5 | 833.1 | 836.9 | 738.7 | 771.9 | 605.6 | 823.2 | 771.7 | 753.9 | 91.8 | 205.2 | 238.1 | 155.6 | 330.2 | 314.6 | 177.4 | 274
1007 | 855 | 472.8 | 189.12 | 221.0704 | 320.5 | 320.3 | 310.6 | 314.5 | 582.2 | 48.9 | 19.6 | 84.7 | 3.6 | 173.8 | 5.3 | 876.5 | 776.7 | 834 | 838 | 738.7 | 772.3 | 603.7 | 827.9 | 772.2 | 754.1 | 92 | 205.4 | 238.4 | 155.8 | 330.2 | 315 | 177.6 | 274.2
1008 | 856 | 472.7 | 189.08 | 221.0236 | 321 | 320.8 | 310.6 | 313.9 | 585.6 | 49 | 19.6 | 84.8 | 3.8 | 172.4 | 5 | 877.1 | 777.3 | 834.1 | 837.4 | 739.7 | 772.5 | 608.1 | 831.4 | 774.2 | 756 | 92.2 | 205.7 | 238.6 | 156 | 330.1 | 315.5 | 177.8 | 274.4
1009 | 857 | 472.7 | 189.08 | 221.0236 | 321.6 | 320.1 | 310.7 | 313.5 | 604 | 49 | 19.6 | 84.8 | 3.8 | 175.7 | 4.5 | 877.8 | 779.2 | 833 | 840.8 | 739.6 | 772.6 | 613.1 | 831.4 | 776.5 | 759 | 92.4 | 205.9 | 238.8 | 156.2 | 330 | 315.9 | 178.1 | 274.5
1010 | 858 | 472.3 | 188.92 | 220.8366 | 322.4 | 319.8 | 310.8 | 313.4 | 613 | 48.9 | 19.6 | 84.8 | 3.9 | 170.1 | 4.3 | 879.2 | 780.3 | 826.6 | 837.8 | 735.5 | 772.6 | 612.9 | 833.5 | 777.5 | 757.9 | 92.6 | 206.2 | 239.2 | 156.5 | 329.8 | 315.8 | 178.3 | 274.6
1011 | 859 | 472.6 | 189.04 | 220.9769 | 323.3 | 320.1 | 310.7 | 313.3 | 599.5 | 48.9 | 19.6 | 84.8 | 3.9 | 164.6 | 5.1 | 878.6 | 774.8 | 819.4 | 833 | 730.6 | 772.9 | 606.9 | 817.4 | 774.1 | 752.4 | 92.8 | 206.4 | 239.5 | 156.7 | 329.7 | 315.5 | 178.5 | 274.8
1012 | 860 | 472.2 | 188.88 | 220.7898 | 324.8 | 319.9 | 311.1 | 313.2 | 597.5 | 49 | 19.6 | 84.8 | 3.8 | 169.9 | 5.9 | 877.8 | 769 | 813.4 | 830.9 | 726.4 | 773.7 | 602.4 | 816.7 | 771.3 | 750.7 | 92.9 | 206.7 | 239.9 | 156.9 | 329.8 | 315.5 | 178.7 | 275
1013 | 861 | 472.5 | 189 | 220.9301 | 326.2 | 320.3 | 312 | 313.1 | 601.1 | 49 | 19.6 | 84.8 | 4 | 170.5 | 6.2 | 877 | 764.1 | 809.8 | 831.2 | 723.8 | 774.6 | 599.2 | 809.7 | 768.3 | 747.8 | 93.1 | 207 | 240.4 | 157.1 | 330.3 | 315.3 | 178.9 | 275.1
1014 | 862 | 473.6 | 189.44 | 221.4444 | 327.1 | 320.7 | 312.8 | 313.7 | 587.3 | 49 | 19.6 | 84.8 | 3.6 | 183.5 | 6.4 | 875.3 | 757.6 | 804.5 | 827.3 | 719.6 | 775.3 | 594.2 | 791.2 | 764.8 | 743.6 | 93.3 | 207.2 | 240.4 | 157.3 | 330.7 | 315.3 | 179.1 | 275.3
1015 | 863 | 473.5 | 189.4 | 221.3977 | 328.8 | 320.9 | 313.8 | 314.5 | 574.1 | 49 | 19.6 | 84.8 | 4 | 192.8 | 6.3 | 874.1 | 752.8 | 803.5 | 825.8 | 716.7 | 776.1 | 588.6 | 788.4 | 761.4 | 740.2 | 93.5 | 207.5 | 240.7 | 157.5 | 330.9 | 315.2 | 179.4 | 275.4
1016 | 864 | 473.4 | 189.36 | 221.3509 | 331.4 | 321 | 314.5 | 315.2 | 573.7 | 49.1 | 19.6 | 84.8 | 4 | 196.8 | 5.6 | 874 | 752.6 | 809.6 | 825.9 | 718.7 | 776.3 | 588 | 797.6 | 760.9 | 740.9 | 93.7 | 207.7 | 241 | 157.7 | 331.2 | 315.4 | 179.6 | 275.6
1017 | 865 | 473 | 189.2 | 221.1639 | 333.3 | 321.1 | 315.1 | 315.6 | 569 | 49.2 | 19.6 | 84.8 | 4 | 183.2 | 5.1 | 873.6 | 751.5 | 811.8 | 824.7 | 718.1 | 776.8 | 587.1 | 799.1 | 760.1 | 739.3 | 93.8 | 208 | 241.3 | 157.9 | 331.4 | 315.7 | 179.8 | 275.7
1018 | 866 | 471.7 | 188.68 | 220.556 | 334 | 321.9 | 315.6 | 315.7 | 567.1 | 49.2 | 19.6 | 84.7 | 3.9 | 177.6 | 5.5 | 871.6 | 748.9 | 807.9 | 821.5 | 715.2 | 777.2 | 583 | 785.5 | 757.6 | 736.5 | 94 | 208.3 | 241.7 | 158.2 | 331.7 | 315.9 | 180 | 275.8
1019 | 867 | 472.6 | 189.04 | 220.9769 | 335.1 | 321.8 | 316.3 | 315.8 | 551.1 | 49.1 | 19.6 | 84.7 | 3.7 | 178.2 | 6.4 | 870 | 747.8 | 806 | 820.7 | 713.5 | 777.2 | 581.3 | 778.5 | 755.7 | 733.8 | 94.2 | 208.5 | 241.8 | 158.4 | 332.2 | 316.2 | 180.2 | 275.9
1020 | 868 | 471.4 | 188.56 | 220.4158 | 336.5 | 320.9 | 316.6 | 316.3 | 537.1 | 49 | 19.6 | 84.6 | 3.5 | 179.5 | 6.9 | 867.4 | 745.2 | 801.6 | 818.3 | 710.8 | 777 | 579 | 766.3 | 754 | 730.4 | 94.4 | 208.8 | 242 | 158.6 | 332.3 | 316.4 | 180.5 | 276.1
1021 | 869 | 471.7 | 188.68 | 220.556 | 338.7 | 319.3 | 316.8 | 316.8 | 523.2 | 48.9 | 19.6 | 84.6 | 4.1 | 187.7 | 7.1 | 864.6 | 742.6 | 798.5 | 819.2 | 708.2 | 776.6 | 575.4 | 752.8 | 751.4 | 727 | 94.6 | 209 | 242.1 | 158.8 | 332.6 | 316.4 | 180.6 | 276.2
1022 | 870 | 471.8 | 188.72 | 220.6028 | 341.3 | 318.1 | 316.5 | 316.9 | 512.6 | 48.8 | 19.5 | 84.6 | 3.9 | 188.1 | 6.9 | 864 | 741.7 | 798.1 | 820.9 | 707.8 | 776.1 | 574.3 | 749.1 | 750.8 | 725.5 | 94.8 | 209.3 | 242.3 | 159 | 332.7 | 316.3 | 180.8 | 276.3
1023 | 871 | 471.9 | 188.76 | 220.6496 | 343.8 | 317.1 | 316.6 | 316.9 | 515.5 | 48.9 | 19.5 | 84.6 | 3.8 | 184.1 | 6.1 | 864.8 | 743.3 | 798.4 | 820 | 706.5 | 775.3 | 573.6 | 756.9 | 751.7 | 725.9 | 94.9 | 209.5 | 242.6 | 159.2 | 332.3 | 316.8 | 181 | 276.6
1024 | 872 | 472.5 | 189 | 220.9301 | 345.3 | 316.4 | 316.5 | 316.5 | 512.5 | 49.1 | 19.5 | 84.6 | 3.4 | 184.8 | 5.6 | 864.2 | 745.4 | 802.2 | 822.1 | 708.7 | 774.7 | 575.5 | 747.2 | 751.6 | 724.8 | 95.1 | 209.8 | 242.9 | 159.4 | 332.4 | 317.1 | 181.3 | 276.8
1025 | 873 | 471.4 | 188.56 | 220.4158 | 346.1 | 315.1 | 316.8 | 315.6 | 504.4 | 49.2 | 19.5 | 84.7 | 4 | 181.2 | 5.5 | 864.7 | 747.6 | 802.8 | 818.7 | 708.2 | 774.2 | 577.1 | 762.4 | 752.4 | 725.8 | 95.3 | 210 | 243 | 159.6 | 333.5 | 317 | 181.5 | 277.1
1026 | 874 | 472.6 | 189.04 | 220.9769 | 344.6 | 314.5 | 317.4 | 314.6 | 516.1 | 49.2 | 19.5 | 84.7 | 4 | 170.9 | 5.3 | 862.7 | 743.1 | 795.2 | 814.4 | 703.3 | 773.3 | 575.7 | 752.7 | 750.6 | 722.5 | 95.5 | 210.3 | 243.3 | 159.8 | 333 | 317.2 | 181.7 | 277.3
1027 | 875 | 472.1 | 188.84 | 220.7431 | 343.6 | 314.5 | 317.9 | 313.7 | 518.7 | 49.3 | 19.5 | 84.7 | 3.7 | 171.9 | 5.4 | 859.6 | 736.4 | 787.7 | 812.5 | 699.6 | 773 | 571.8 | 742.3 | 746.6 | 718.7 | 95.7 | 210.5 | 243.8 | 160 | 332.6 | 316.9 | 181.9 | 277.4
1028 | 876 | 472.2 | 188.88 | 220.7898 | 344.3 | 315.5 | 318.4 | 313.2 | 530 | 49.4 | 19.5 | 84.7 | 3 | 174.3 | 5.2 | 857.3 | 732.4 | 784 | 809.6 | 696.5 | 772.9 | 568.5 | 743 | 743.9 | 716 | 95.8 | 210.8 | 244.4 | 160.2 | 332.3 | 316.3 | 182.1 | 277.4
1029 | 877 | 472.4 | 188.96 | 220.8834 | 346.4 | 316.1 | 318.6 | 313.7 | 525 | 49.5 | 19.5 | 84.9 | 3.3 | 178.8 | 5.7 | 855.2 | 728.4 | 777.2 | 806.6 | 692.7 | 772.7 | 564.6 | 735.3 | 741.7 | 713.5 | 96 | 211 | 244.5 | 160.4 | 332 | 316.4 | 182.3 | 277.4
1030 | 878 | 471.8 | 188.72 | 220.6028 | 346.2 | 315.3 | 319.3 | 314.8 | 520.9 | 49.6 | 19.5 | 85 | 3.2 | 177.2 | 6.4 | 851.8 | 723.4 | 769.9 | 805.4 | 688.6 | 772.6 | 559 | 726.1 | 738.4 | 709.6 | 96.2 | 211.3 | 244.9 | 160.6 | 332.4 | 316.5 | 182.5 | 277.5
1031 | 879 | 472.2 | 188.88 | 220.7898 | 347.2 | 315 | 320.2 | 315.7 | 511.1 | 49.8 | 19.5 | 85.2 | 3.1 | 178.5 | 7 | 850.9 | 723.6 | 768.6 | 804.1 | 687.9 | 772 | 555.5 | 725.8 | 735.8 | 707.5 | 96.4 | 211.6 | 245 | 160.8 | 333.8 | 316.1 | 182.7 | 277.6
1032 | 880 | 472.2 | 188.88 | 220.7898 | 347.6 | 314.7 | 321 | 316.8 | 509.2 | 49.8 | 19.5 | 85.3 | 3.5 | 180.5 | 6.9 | 850.2 | 724.1 | 762.8 | 802.9 | 685.1 | 771.5 | 555.1 | 725.3 | 735 | 705.6 | 96.6 | 211.8 | 245.1 | 160.9 | 335.4 | 316.7 | 183 | 277.9
1033 | 881 | 471.6 | 188.64 | 220.5093 | 347.1 | 314.4 | 321.2 | 317.8 | 507.9 | 49.9 | 19.5 | 85.2 | 3.6 | 176.4 | 6.3 | 850.1 | 727.3 | 762.6 | 804.4 | 684.1 | 770.6 | 556.5 | 731.5 | 734.7 | 705.4 | 96.8 | 212.1 | 245.1 | 161.1 | 335.9 | 317 | 183.1 | 278
1034 | 882 | 471 | 188.4 | 220.2287 | 346 | 314.4 | 320.7 | 318.5 | 505.4 | 50 | 19.5 | 85.3 | 3.3 | 183.1 | 6.1 | 849.7 | 729 | 764.6 | 802 | 682.9 | 769.8 | 557.2 | 736.7 | 733.9 | 703.9 | 97 | 212.3 | 245.3 | 161.3 | 336.2 | 317.2 | 183.4 | 278.2
1035 | 883 | 471.1 | 188.44 | 220.2755 | 344.6 | 313.7 | 320 | 318.9 | 508.3 | 50.1 | 19.5 | 85.3 | 3.6 | 178.9 | 5.9 | 850.4 | 732 | 771.4 | 801.4 | 683.2 | 768.6 | 558.7 | 741.7 | 733.9 | 704.5 | 97.1 | 212.6 | 245.6 | 161.5 | 336.3 | 317.6 | 183.6 | 278.4
1036 | 884 | 470.8 | 188.32 | 220.1352 | 343.4 | 313 | 318.8 | 318.9 | 511.1 | 50.2 | 19.5 | 85.3 | 3.7 | 172.8 | 5.4 | 851.6 | 737.8 | 779.8 | 804 | 687.3 | 767.4 | 561.7 | 753.6 | 734.4 | 706.9 | 97.3 | 212.8 | 245.8 | 161.7 | 336.4 | 318 | 183.8 | 278.6
1037 | 885 | 471.9 | 188.76 | 220.6496 | 342.5 | 312.6 | 317.8 | 318.9 | 517 | 50.2 | 19.5 | 85.4 | 3.8 | 195.6 | 5.4 | 852.3 | 741.3 | 790.2 | 803.8 | 691.7 | 766.2 | 562.4 | 761.7 | 734.9 | 707.3 | 97.5 | 213.1 | 246 | 161.9 | 336.2 | 318.2 | 184 | 278.7
1038 | 886 | 472.3 | 188.92 | 220.8366 | 340.9 | 312.9 | 317.8 | 319 | 524.2 | 50.2 | 19.5 | 85.4 | 3.7 | 191.7 | 5.7 | 852.9 | 743.9 | 795.6 | 803.7 | 693.9 | 765.2 | 562.2 | 772 | 734.3 | 707.5 | 97.7 | 213.3 | 246.2 | 162 | 335.8 | 318.2 | 184.2 | 278.8
1039 | 887 | 472.2 | 188.88 | 220.7898 | 339.4 | 312.6 | 317.5 | 318.6 | 526.3 | 50.2 | 19.5 | 85.5 | 3.8 | 184.8 | 6 | 853.6 | 745.7 | 793.9 | 803.7 | 694 | 764.1 | 562.2 | 774 | 734.3 | 708.5 | 97.9 | 213.6 | 246.5 | 162.2 | 335.5 | 318.2 | 184.4 | 278.9
1040 | 888 | 471.7 | 188.68 | 220.556 | 338.1 | 311.8 | 317 | 317.8 | 526.7 | 50.2 | 19.5 | 85.6 | 3.7 | 187.1 | 6.7 | 853.6 | 741.7 | 793.4 | 801.9 | 694.5 | 763.5 | 559 | 772.7 | 731.6 | 706.3 | 98.1 | 213.8 | 247 | 162.4 | 335.4 | 318 | 184.6 | 279
1041 | 889 | 471.7 | 188.68 | 220.556 | 337.2 | 312.1 | 316.3 | 317.4 | 527.8 | 50.1 | 19.5 | 85.7 | 3.3 | 178.7 | 7.5 | 854.6 | 739.6 | 795.9 | 802.2 | 694.7 | 763 | 558.5 | 772 | 729.7 | 706.1 | 98.3 | 214.1 | 247.5 | 162.6 | 335.1 | 317.4 | 184.9 | 279
1042 | 890 | 470.9 | 188.36 | 220.182 | 336.1 | 312.5 | 315.9 | 316.9 | 534.4 | 50 | 19.5 | 85.8 | 3.3 | 178.4 | 7.4 | 853.8 | 735.7 | 795.8 | 799.8 | 694.4 | 762.5 | 556 | 778 | 728.2 | 705.8 | 98.5 | 214.3 | 247.9 | 162.8 | 335.2 | 316.9 | 185.1 | 279.1
1043 | 891 | 471.6 | 188.64 | 220.5093 | 335.3 | 312.7 | 316.1 | 316.8 | 550.9 | 50 | 19.5 | 85.9 | 3.5 | 176.1 | 7 | 853.5 | 734.3 | 794.4 | 797.2 | 693.5 | 762.4 | 554.3 | 780.2 | 727.6 | 706.3 | 98.7 | 214.6 | 248.5 | 163 | 335.4 | 316.4 | 185.3 | 279.2
1044 | 892 | 471.1 | 188.44 | 220.2755 | 335.4 | 313.9 | 317 | 317.8 | 555 | 50.1 | 19.5 | 86.1 | 3.6 | 171.8 | 6.8 | 852.3 | 730.6 | 787.8 | 794.4 | 690.4 | 762 | 553.4 | 773.9 | 726.9 | 705 | 98.8 | 214.9 | 248.9 | 163.1 | 335.5 | 316.1 | 185.5 | 279.3
1045 | 893 | 472 | 188.8 | 220.6963 | 335.5 | 314.4 | 317.8 | 318.8 | 554.8 | 50.2 | 19.5 | 86.3 | 4 | 177.7 | 6.9 | 851.3 | 726.7 | 787.7 | 792 | 689.1 | 761.9 | 552.1 | 770.2 | 725.6 | 703.8 | 99 | 215.2 | 249.3 | 163.3 | 336.2 | 315.9 | 185.7 | 279.4
1046 | 894 | 471.8 | 188.72 | 220.6028 | 336.4 | 314.7 | 318.9 | 319.7 | 558.1 | 50.3 | 19.5 | 86.4 | 3.9 | 180.8 | 6.9 | 851.3 | 725.1 | 790.4 | 791.1 | 689.7 | 761.6 | 550.3 | 777.5 | 724.5 | 703.8 | 99.2 | 215.4 | 249.5 | 163.5 | 337 | 315.9 | 185.9 | 279.5
1047 | 895 | 473.3 | 189.32 | 221.3042 | 336.8 | 315.3 | 319.1 | 320.5 | 557.5 | 50.4 | 19.5 | 86.5 | 3.7 | 182 | 7 | 851 | 724.9 | 790.2 | 791.6 | 689.6 | 761 | 551.4 | 781 | 725.1 | 703.4 | 99.4 | 215.7 | 249.7 | 163.7 | 338.1 | 316.5 | 186.2 | 279.7
1048 | 896 | 473.4 | 189.36 | 221.3509 | 338.4 | 316 | 318.9 | 321.2 | 565.1 | 50.6 | 19.5 | 86.6 | 3.7 | 183.6 | 7.2 | 849 | 720.9 | 783.9 | 790.9 | 686.3 | 760.6 | 550.6 | 768.7 | 723.9 | 701.7 | 99.6 | 216 | 249.9 | 163.8 | 338.3 | 316.9 | 186.4 | 279.9
1049 | 897 | 471.9 | 188.76 | 220.6496 | 339.5 | 316.6 | 319.2 | 321.6 | 553.6 | 50.7 | 19.5 | 86.7 | 3.3 | 184.8 | 7.2 | 847.4 | 718.9 | 780.1 | 789.4 | 682.6 | 760.1 | 549.3 | 754.3 | 721.7 | 698.3 | 99.8 | 216.2 | 250 | 164 | 338.5 | 317.3 | 186.6 | 280.1
1050 | 898 | 472.2 | 188.88 | 220.7898 | 340.4 | 316.8 | 319 | 321.6 | 544.6 | 50.8 | 19.5 | 86.8 | 3.8 | 183.8 | 6.8 | 846.7 | 717.3 | 782.8 | 789.7 | 681.8 | 759.6 | 548.4 | 745.9 | 720.3 | 697.6 | 100 | 216.5 | 250.4 | 164.2 | 338.3 | 317.8 | 186.9 | 280.2
1051 | 899 | 472 | 188.8 | 220.6963 | 343.5 | 316.2 | 319.8 | 321 | 530.7 | 50.9 | 19.5 | 86.8 | 3.9 | 181.9 | 6.4 | 845.2 | 714 | 778.6 | 787.5 | 678.8 | 759 | 547.3 | 746 | 719.5 | 695.5 | 100.2 | 216.8 | 250.5 | 164.4 | 338.3 | 318.4 | 187.1 | 280.4
1052 | 900 | 471.2 | 188.48 | 220.3223 | 344.8 | 315.3 | 320.5 | 320.8 | 534.9 | 51 | 19.5 | 86.9 | 3.8 | 178.8 | 6.2 | 844.3 | 712.4 | 778.4 | 787.4 | 676.6 | 758.2 | 546.5 | 749.9 | 719.5 | 695.1 | 100.3 | 217 | 250.7 | 164.5 | 339.2 | 318.8 | 187.3 | 280.5
1053 | 901 | 470.8 | 188.32 | 220.1352 | 346.2 | 314.7 | 320.6 | 320.9 | 532.3 | 51.1 | 19.5 | 86.8 | 3.5 | 177.7 | 6.2 | 844.8 | 720.2 | 781.4 | 790.9 | 678.7 | 757.4 | 551.8 | 753.6 | 720.9 | 696.5 | 100.5 | 217.3 | 250.7 | 164.7 | 340.3 | 318.7 | 187.5 | 280.7
1054 | 902 | 470.3 | 188.12 | 219.9014 | 348.4 | 313.7 | 320.7 | 321.4 | 524.9 | 51 | 19.5 | 86.9 | 3.7 | 173.4 | 6.2 | 845.3 | 727.3 | 779.2 | 791.4 | 677.2 | 756.2 | 560.6 | 758.5 | 724.2 | 698.5 | 100.7 | 217.5 | 250.7 | 164.9 | 340.1 | 318.4 | 187.7 | 280.8
1055 | 903 | 471.4 | 188.56 | 220.4158 | 348.2 | 312.5 | 320.7 | 321.8 | 525.3 | 51.1 | 19.5 | 86.9 | 3.8 | 179 | 6.3 | 846.6 | 736 | 783.4 | 793.4 | 681.1 | 755.2 | 570.5 | 763.9 | 727.5 | 701.9 | 100.9 | 217.7 | 250.9 | 165 | 339.8 | 318.5 | 188 | 281
1056 | 904 | 472.6 | 189.04 | 220.9769 | 347.2 | 312.1 | 320.8 | 321.5 | 521.5 | 51.1 | 19.5 | 86.9 | 3.6 | 186.1 | 5.8 | 848.4 | 739.7 | 780.9 | 795.7 | 682 | 754.3 | 573.2 | 768.3 | 729.4 | 703.2 | 101.1 | 218 | 251.2 | 165.2 | 339.7 | 319 | 188.2 | 281.2
1057 | 905 | 473 | 189.2 | 221.1639 | 346.3 | 311.8 | 321.6 | 320.4 | 517.1 | 51 | 19.5 | 86.9 | 3.6 | 183.3 | 5.1 | 848 | 736.2 | 779.9 | 794 | 681.3 | 753.6 | 569.5 | 757.2 | 727.3 | 699.9 | 101.3 | 218.2 | 251.5 | 165.4 | 339.5 | 319.6 | 188.5 | 281.4
1058 | 906 | 470.6 | 188.24 | 220.0417 | 345.6 | 311.7 | 322 | 319.2 | 513.3 | 51 | 19.5 | 87 | 3.2 | 173.5 | 4.6 | 844.6 | 726.8 | 770.6 | 789 | 677.2 | 753 | 560.5 | 737.8 | 724.2 | 695.9 | 101.5 | 218.4 | 252 | 165.5 | 339.6 | 319.7 | 188.6 | 281.7
1059 | 907 | 471.2 | 188.48 | 220.3223 | 345.1 | 312.5 | 322.5 | 318.5 | 500 | 51 | 19.5 | 87.1 | 3.2 | 183.9 | 4.7 | 838.8 | 715.3 | 761.1 | 782.5 | 672.2 | 752.4 | 552.5 | 710.5 | 720 | 691.2 | 101.7 | 218.7 | 252.2 | 165.7 | 339.4 | 319.9 | 188.9 | 281.8
1060 | 908 | 471.4 | 188.56 | 220.4158 | 347.9 | 312.7 | 322.7 | 318.3 | 490.5 | 51 | 19.5 | 87.1 | 3.2 | 175.3 | 4.8 | 835.9 | 717.2 | 756.4 | 783.1 | 670.3 | 751.8 | 551.3 | 705.6 | 717.7 | 689.8 | 101.9 | 218.9 | 252.3 | 165.9 | 338.8 | 319.7 | 189.1 | 281.9
1061 | 909 | 471.4 | 188.56 | 220.4158 | 350.8 | 313.3 | 322.4 | 318.7 | 487.1 | 50.9 | 19.5 | 87.2 | 3.3 | 173.5 | 4.5 | 835.9 | 724.1 | 758.2 | 784.3 | 669.7 | 751 | 554.2 | 717.7 | 718.4 | 690.2 | 102.1 | 219.2 | 252.3 | 166 | 338.3 | 319.2 | 189.3 | 282
1062 | 910 | 471.8 | 188.72 | 220.6028 | 352.2 | 312.9 | 322.2 | 318.8 | 490.8 | 50.9 | 19.5 | 87.3 | 3.6 | 175.9 | 4.3 | 835.8 | 723.3 | 762.7 | 784.1 | 670.4 | 750.4 | 552.9 | 714.8 | 717.6 | 688.2 | 102.2 | 219.4 | 252.4 | 166.2 | 337.9 | 319.3 | 189.5 | 282
1063 | 911 | 471.4 | 188.56 | 220.4158 | 352.7 | 312.4 | 322 | 318.7 | 492.3 | 50.9 | 19.5 | 87.3 | 3.4 | 193.2 | 4.6 | 837.1 | 726.9 | 763.1 | 785.6 | 670.9 | 749.6 | 553.9 | 726.4 | 717.6 | 689.7 | 102.4 | 219.6 | 252.5 | 166.4 | 337.6 | 319 | 189.7 | 282.2
1064 | 912 | 472.3 | 188.92 | 220.8366 | 351.8 | 311.8 | 322 | 318.3 | 488.6 | 50.9 | 19.4 | 87.5 | 3.4 | 197.2 | 4.4 | 838.1 | 732.2 | 766 | 787.5 | 671.4 | 748.8 | 556.3 | 726.4 | 719 | 690.1 | 102.6 | 219.8 | 252.7 | 166.5 | 337.2 | 318.7 | 189.9 | 282.3
1065 | 913 | 471.7 | 188.68 | 220.556 | 351.3 | 311.8 | 322.2 | 317.8 | 501.6 | 50.9 | 19.4 | 87.6 | 3.6 | 184.2 | 4.6 | 840.5 | 738 | 766.5 | 789.6 | 670.8 | 747.8 | 561.6 | 744.9 | 721.9 | 693.5 | 102.8 | 220 | 252.9 | 166.7 | 337 | 318.3 | 190.2 | 282.4
1066 | 914 | 472.1 | 188.84 | 220.7431 | 351.4 | 310.5 | 322.6 | 317.1 | 503.7 | 51 | 19.4 | 87.6 | 3.6 | 198 | 5.1 | 840.1 | 738.9 | 757 | 788.6 | 666.3 | 747.1 | 562.6 | 738.6 | 722.4 | 692.1 | 103 | 220.3 | 253.1 | 166.9 | 337.1 | 318.5 | 190.4 | 282.5
1067 | 915 | 471.9 | 188.76 | 220.6496 | 352 | 308.8 | 323.3 | 316.4 | 497.7 | 51 | 19.4 | 87.8 | 3.7 | 181.6 | 5 | 839.1 | 736.1 | 758 | 787.3 | 665.5 | 746.3 | 562.7 | 733.2 | 722.4 | 691.7 | 103.2 | 220.5 | 253.3 | 167 | 336.7 | 318.4 | 190.6 | 282.6
1068 | 916 | 471.7 | 188.68 | 220.556 | 352.1 | 307.6 | 323.8 | 316.6 | 495.3 | 50.9 | 19.4 | 87.9 | 3.9 | 185.6 | 4.6 | 839.1 | 731.3 | 754.8 | 783.6 | 663.6 | 745.8 | 562.3 | 733.1 | 721.8 | 691.2 | 103.4 | 220.7 | 253.6 | 167.2 | 336.4 | 318.2 | 190.8 | 282.6
1069 | 917 | 472.3 | 188.92 | 220.8366 | 351.5 | 307.2 | 323.9 | 316.8 | 501.5 | 50.9 | 19.4 | 88 | 3.8 | 212.7 | 4.2 | 836.8 | 723 | 745.8 | 781.8 | 659.7 | 745.6 | 558.9 | 718.8 | 719.5 | 687.3 | 103.5 | 220.9 | 254.1 | 167.4 | 336.3 | 318.2 | 191 | 282.8
1070 | 918 | 470.8 | 188.32 | 220.1352 | 351.6 | 307.5 | 323.4 | 317.2 | 505.9 | 51 | 19.4 | 88 | 3.6 | 218.4 | 3.9 | 834 | 718 | 743.5 | 780.9 | 657.4 | 745.4 | 557 | 704.2 | 717.6 | 684.5 | 103.7 | 221.1 | 254.2 | 167.5 | 336.3 | 318.3 | 191.3 | 282.8
1071 | 919 | 471.5 | 188.6 | 220.4625 | 352 | 307.5 | 323.1 | 317.6 | 504.4 | 51.1 | 19.4 | 88.1 | 4.3 | 198.5 | 3.7 | 833.2 | 714.6 | 744.7 | 779.8 | 655.8 | 745.3 | 557.1 | 702.9 | 716 | 682.9 | 103.9 | 221.3 | 254.3 | 167.7 | 336 | 318.3 | 191.4 | 282.9
1072 | 920 | 470 | 188 | 219.7612 | 353 | 307.3 | 323.3 | 317.8 | 512.3 | 51.2 | 19.4 | 88.1 | 3.8 | 186.4 | 3.9 | 833.9 | 716.2 | 752.1 | 779.8 | 657.9 | 745.5 | 556.5 | 719.4 | 714.7 | 682.6 | 104.1 | 221.5 | 254.5 | 167.9 | 335.8 | 318.9 | 191.7 | 283.1
1073 | 921 | 471.1 | 188.44 | 220.2755 | 352.7 | 307 | 323.7 | 317.4 | 518.3 | 51.3 | 19.4 | 88.1 | 3.8 | 191.8 | 4 | 836.2 | 726.4 | 761.9 | 783.3 | 660.8 | 745 | 563.6 | 733.1 | 717.7 | 686.8 | 104.3 | 221.8 | 254.6 | 168 | 335.4 | 319.3 | 191.9 | 283.3
1074 | 922 | 468.4 | 187.36 | 219.013 | 351.5 | 306.8 | 323.5 | 316.7 | 517.8 | 51.3 | 19.4 | 88.1 | 3.5 | 186.4 | 3.7 | 838.3 | 735.8 | 764.6 | 785.8 | 662.3 | 744.7 | 568.5 | 731.7 | 721.1 | 689.4 | 104.5 | 222 | 254.7 | 168.1 | 335 | 319.4 | 192.1 | 283.5
1075 | 923 | 472.2 | 188.88 | 220.7898 | 351.3 | 306.7 | 323.1 | 316.3 | 522.7 | 51.4 | 19.4 | 88 | 3.5 | 182.3 | 3.8 | 840.8 | 742.4 | 764.7 | 787.3 | 661.9 | 744.3 | 569.4 | 752.5 | 723.7 | 692.2 | 104.7 | 222.2 | 254.9 | 168.3 | 334.9 | 319.1 | 192.3 | 283.5
1076 | 924 | 472.1 | 188.84 | 220.7431 | 351.4 | 307.1 | 323.2 | 315.5 | 539.6 | 51.4 | 19.4 | 88 | 3.8 | 187.3 | 4 | 840.1 | 738.5 | 762.1 | 785.2 | 660.8 | 744.3 | 568.2 | 754.2 | 723.3 | 690.2 | 104.9 | 222.4 | 255.3 | 168.5 | 335.1 | 318.9 | 192.5 | 283.5
1077 | 925 | 471.7 | 188.68 | 220.556 | 351.8 | 308.3 | 323.7 | 314.9 | 539.7 | 51.4 | 19.4 | 88 | 3.8 | 192.8 | 4.1 | 836.9 | 727.4 | 750.3 | 781.2 | 656.8 | 744.5 | 565.8 | 733.8 | 720.8 | 686.6 | 105.1 | 222.6 | 255.6 | 168.6 | 335 | 318.7 | 192.7 | 283.5
1078 | 926 | 471.7 | 188.68 | 220.556 | 353.1 | 308.2 | 323.8 | 315.1 | 525.7 | 51.4 | 19.4 | 88 | 3.4 | 191.3 | 3.9 | 833.4 | 718 | 743.2 | 777.8 | 652.6 | 744.8 | 557.9 | 712.9 | 716.8 | 683.1 | 105.3 | 222.8 | 255.8 | 168.8 | 335 | 318.4 | 193 | 283.6
1079 | 927 | 471.2 | 188.48 | 220.3223 | 353.3 | 308.4 | 323.6 | 315.2 | 524.5 | 51.4 | 19.4 | 88 | 3.8 | 187.3 | 3.6 | 833.5 | 717.9 | 749.6 | 776.3 | 653.4 | 744.9 | 556.2 | 727.4 | 714.9 | 684.1 | 105.5 | 223 | 256.1 | 168.9 | 335.1 | 318.5 | 193.2 | 283.6
1080 | 928 | 471.7 | 188.68 | 220.556 | 352.8 | 309 | 323.8 | 315.6 | 538.5 | 51.4 | 19.4 | 88 | 3.5 | 189.6 | 3.2 | 834.6 | 718.6 | 756.1 | 776.3 | 655.5 | 745.1 | 554.9 | 737.6 | 714.1 | 684.5 | 105.7 | 223.3 | 256.6 | 169.1 | 335.2 | 318.6 | 193.4 | 283.8
1081 | 929 | 471 | 188.4 | 220.2287 | 352.6 | 309.9 | 324.4 | 316.5 | 544.7 | 51.4 | 19.4 | 88.1 | 3.4 | 189.3 | 3 | 835.2 | 717.3 | 754.5 | 776.3 | 654.6 | 745.4 | 553.4 | 744.4 | 712.8 | 683.5 | 105.9 | 223.5 | 256.9 | 169.3 | 335.6 | 318.7 | 193.6 | 283.8
1082 | 930 | 471.4 | 188.56 | 220.4158 | 352.8 | 309.8 | 325.1 | 317.9 | 547.8 | 51.4 | 19.4 | 88.1 | 3.6 | 192.4 | 3.1 | 834.8 | 714.2 | 755.3 | 775 | 653.7 | 745.6 | 550.7 | 743.5 | 711.4 | 681.8 | 106.1 | 223.8 | 257.2 | 169.4 | 336.2 | 319.1 | 193.8 | 283.9
1083 | 931 | 472.2 | 188.88 | 220.7898 | 353.2 | 309.5 | 325.7 | 319.2 | 549.1 | 51.4 | 19.4 | 88.2 | 3.9 | 209.4 | 3.4 | 834.3 | 709.6 | 760.2 | 774.1 | 654.4 | 746 | 547.8 | 740.9 | 709.1 | 680.2 | 106.3 | 224 | 257.8 | 169.6 | 337.1 | 319.6 | 194.1 | 284.1
1084 | 932 | 473.1 | 189.24 | 221.2107 | 353 | 309.8 | 325.9 | 320.4 | 543.5 | 51.4 | 19.4 | 88.1 | 3.4 | 206.2 | 3.6 | 833.6 | 707.4 | 761 | 772.7 | 652.8 | 746.1 | 543.8 | 741.8 | 707.2 | 678.4 | 106.5 | 224.3 | 258.1 | 169.7 | 337.7 | 320.5 | 194.3 | 284.3
1085 | 933 | 473.3 | 189.32 | 221.3042 | 353.6 | 310.1 | 325.8 | 321.5 | 547.9 | 51.4 | 19.4 | 88.1 | 3.5 | 194 | 3.3 | 833.3 | 705 | 754.6 | 771 | 651 | 745.9 | 542.5 | 751.4 | 706.5 | 677.8 | 106.6 | 224.5 | 258.2 | 169.9 | 338.2 | 321 | 194.5 | 284.5
1086 | 934 | 473 | 189.2 | 221.1639 | 354.7 | 311 | 326.5 | 322.4 | 558.6 | 51.5 | 19.4 | 88.2 | 3.4 | 191.9 | 3.2 | 834.6 | 716.5 | 753.6 | 772.6 | 651.4 | 745.6 | 546.9 | 760.9 | 708.2 | 680.5 | 106.8 | 224.8 | 258.6 | 170 | 338.6 | 321.3 | 194.7 | 284.7
1087 | 935 | 472.8 | 189.12 | 221.0704 | 356.1 | 311.8 | 327.1 | 323.2 | 559.9 | 51.5 | 19.4 | 88.2 | 3.7 | 189.4 | 3.3 | 833.5 | 717.7 | 750.1 | 772.3 | 649.3 | 745.5 | 548.5 | 740.3 | 707.1 | 679.3 | 107 | 225 | 258.8 | 170.2 | 339 | 321.3 | 195 | 284.8
1088 | 936 | 473 | 189.2 | 221.1639 | 355.7 | 312.2 | 327.3 | 323.1 | 551.4 | 51.5 | 19.4 | 88.3 | 3.7 | 193 | 3.5 | 830.7 | 712.3 | 743.7 | 770.1 | 646.1 | 744.9 | 544.7 | 729.7 | 705.3 | 676.5 | 107.2 | 225.3 | 259.2 | 170.3 | 339.4 | 321.2 | 195.2 | 284.9
1089 | 937 | 472.7 | 189.08 | 221.0236 | 357.3 | 312.9 | 327 | 323.1 | 537.5 | 51.6 | 19.4 | 88.3 | 3.5 | 194.8 | 3.2 | 829.8 | 721.3 | 748.4 | 772.1 | 648.9 | 743.9 | 545.9 | 720.6 | 704.8 | 675.5 | 107.4 | 225.5 | 259.1 | 170.5 | 339.6 | 321.4 | 195.4 | 285.1
1090 | 938 | 472.4 | 188.96 | 220.8834 | 359.2 | 313.5 | 326.9 | 323.4 | 535.2 | 51.7 | 19.4 | 88.3 | 4.1 | 192.9 | 3.3 | 830.6 | 726.7 | 754.3 | 773.7 | 651.8 | 742.9 | 548.9 | 729.9 | 706.3 | 677.4 | 107.6 | 225.8 | 259.3 | 170.6 | 340.1 | 321.4 | 195.6 | 285.1
1091 | 939 | 472.6 | 189.04 | 220.9769 | 359.3 | 314.1 | 326.8 | 323.3 | 544.1 | 51.7 | 19.4 | 88.3 | 4.2 | 186.3 | 3.3 | 829 | 715.7 | 746.4 | 769.5 | 649 | 742 | 545.3 | 729.9 | 705.1 | 675.7 | 107.8 | 226.1 | 259.9 | 170.8 | 340.2 | 321.5 | 195.8 | 285.3
1092 | 940 | 472.5 | 189 | 220.9301 | 358.8 | 315.2 | 327.4 | 322.9 | 539.8 | 51.7 | 19.4 | 88.3 | 3.8 | 179.2 | 3.3 | 824.6 | 703.6 | 738.1 | 765.5 | 646.1 | 741.3 | 541.3 | 714 | 702 | 672.4 | 108 | 226.3 | 260.5 | 170.9 | 340.7 | 321.3 | 196.1 | 285.3
1093 | 941 | 472.6 | 189.04 | 220.9769 | 358.8 | 315.9 | 327.9 | 323.1 | 530 | 51.8 | 19.4 | 88.3 | 3.5 | 168.5 | 3.4 | 822.9 | 704.1 | 731.2 | 765.1 | 644.5 | 740.6 | 538.7 | 706.7 | 699.8 | 670.5 | 108.2 | 226.6 | 260.7 | 171 | 341.1 | 321.2 | 196.3 | 285.4
1094 | 942 | 472.5 | 189 | 220.9301 | 360.4 | 315.6 | 326.9 | 323.7 | 522.9 | 51.9 | 19.4 | 88.3 | 3.7 | 163.8 | 2.9 | 824.7 | 715.6 | 735.7 | 765.3 | 646 | 739.9 | 539.3 | 723.2 | 699.9 | 672.4 | 108.4 | 226.9 | 260.7 | 171.2 | 341.2 | 320.8 | 196.5 | 285.4
1095 | 943 | 472.8 | 189.12 | 221.0704 | 361.2 | 316.1 | 326.6 | 324.8 | 527.2 | 52 | 19.4 | 88.3 | 3.6 | 172.1 | 2.3 | 827.3 | 723.6 | 736.8 | 766.3 | 646.1 | 739.1 | 541 | 737.5 | 701.4 | 673.7 | 108.6 | 227.1 | 260.8 | 171.4 | 341.2 | 320.9 | 196.7 | 285.5
1096 | 944 | 472.6 | 189.04 | 220.9769 | 360.4 | 316.9 | 326.8 | 325 | 539.1 | 52.1 | 19.4 | 88.3 | 4 | 196.3 | 2.1 | 829.9 | 729.3 | 745 | 767.9 | 648 | 738.4 | 541.8 | 745.7 | 702.2 | 674.9 | 108.8 | 227.4 | 261.1 | 171.5 | 341.3 | 321.1 | 196.9 | 285.6
1097 | 945 | 472.4 | 188.96 | 220.8834 | 359.2 | 316 | 326.6 | 325 | 535.8 | 52.1 | 19.4 | 88.3 | 4.2 | 210.5 | 2 | 832.4 | 739 | 757.9 | 770.4 | 651.7 | 737.6 | 542.8 | 762.2 | 703.3 | 677.3 | 109 | 227.6 | 261.3 | 171.7 | 341.5 | 321.2 | 197.1 | 285.7
1098 | 946 | 473.2 | 189.28 | 221.2574 | 358.2 | 315.7 | 327 | 325.3 | 542.7 | 52.2 | 19.4 | 88.4 | 4.1 | 203.1 | 2 | 833.5 | 752.4 | 767.8 | 774 | 655.6 | 736.9 | 552.6 | 772.7 | 707.2 | 682.9 | 109.2 | 227.9 | 261.3 | 171.8 | 341.9 | 321.4 | 197.4 | 285.9
1099 | 947 | 473.3 | 189.32 | 221.3042 | 358.7 | 316.4 | 326.6 | 325.3 | 546.1 | 52.3 | 19.4 | 88.4 | 3.9 | 184.8 | 2.4 | 834.4 | 761.5 | 768.6 | 775.8 | 657 | 736.1 | 558.7 | 766.7 | 709.7 | 683.7 | 109.4 | 228.1 | 261.3 | 171.9 | 341.9 | 322 | 197.6 | 286.1
1100 | 948 | 472.4 | 188.96 | 220.8834 | 359.1 | 317.6 | 325.8 | 325.5 | 531.9 | 52.4 | 19.4 | 88.4 | 4.1 | 173 | 2.9 | 832.6 | 752.4 | 758.9 | 775.2 | 654.2 | 735.1 | 557.6 | 743.7 | 708.4 | 679.9 | 109.6 | 228.3 | 261.3 | 172.1 | 341.9 | 322.1 | 197.8 | 286.2
1101 | 949 | 473.3 | 189.32 | 221.3042 | 360 | 317.3 | 325 | 325.7 | 515.1 | 52.4 | 19.4 | 88.5 | 3.7 | 176.9 | 3.3 | 826.8 | 740.2 | 745.3 | 770 | 650.9 | 734.2 | 554.7 | 711.7 | 705.5 | 675.9 | 109.7 | 228.6 | 261.4 | 172.2 | 341.8 | 322.2 | 198 | 286.4
1102 | 950 | 473.3 | 189.32 | 221.3042 | 361.2 | 316.5 | 324.5 | 325.3 | 499.8 | 52.3 | 19.4 | 88.6 | 3.3 | 184.6 | 3.5 | 823.7 | 736.5 | 739.4 | 769 | 649.7 | 733.3 | 553.5 | 705 | 703.4 | 674.2 | 109.9 | 228.8 | 261.5 | 172.4 | 341.6 | 322.4 | 198.2 | 286.6
1103 | 951 | 473.7 | 189.48 | 221.4912 | 363.9 | 315.7 | 323.9 | 324 | 494.7 | 52.2 | 19.4 | 88.7 | 4.1 | 183.9 | 3.5 | 824.3 | 745.1 | 740 | 770 | 650 | 732.5 | 558.6 | 705.9 | 703.8 | 674.2 | 110.1 | 229 | 261.6 | 172.6 | 341.1 | 322.8 | 198.4 | 286.8
1104 | 952 | 473.5 | 189.4 | 221.3977 | 363.9 | 314.5 | 323 | 322.6 | 499.8 | 52.2 | 19.4 | 88.8 | 4.1 | 180.3 | 3.5 | 827 | 752.3 | 737.4 | 773 | 648.7 | 731.8 | 559.8 | 709.5 | 704.1 | 674.1 | 110.3 | 229.2 | 261.8 | 172.7 | 340.9 | 322.9 | 198.7 | 287
1105 | 953 | 473.5 | 189.4 | 221.3977 | 363.3 | 312.7 | 323 | 321.2 | 504 | 52.2 | 19.4 | 88.9 | 3.5 | 180.5 | 3.5 | 827.5 | 758.2 | 733.9 | 772.8 | 648 | 731.3 | 559 | 703.5 | 704.4 | 673.1 | 110.5 | 229.4 | 262.1 | 172.9 | 340.5 | 322.5 | 198.9 | 287.1
1106 | 954 | 472.9 | 189.16 | 221.1171 | 362.5 | 311.3 | 323.3 | 319.8 | 498.3 | 52.3 | 19.4 | 89 | 3.5 | 180.5 | 3.4 | 827.7 | 761.4 | 735.2 | 772.9 | 649 | 730.6 | 559.1 | 702.2 | 704.4 | 672.5 | 110.7 | 229.5 | 262.2 | 173 | 340.1 | 322.3 | 199.1 | 287.1
1107 | 955 | 472.4 | 188.96 | 220.8834 | 361.8 | 310.3 | 323.7 | 318.4 | 495 | 52.4 | 19.4 | 89.1 | 3.8 | 185.6 | 3.4 | 824.4 | 744.1 | 727.8 | 769.3 | 645.5 | 730 | 555.8 | 687.6 | 701.8 | 668.6 | 110.9 | 229.7 | 262.6 | 173.2 | 339.6 | 321.8 | 199.3 | 287.1
1108 | 956 | 472.8 | 189.12 | 221.0704 | 360.8 | 310 | 324.2 | 318 | 489.7 | 52.5 | 19.4 | 89.1 | 3.8 | 193.8 | 3.5 | 819.5 | 730.9 | 720.8 | 765.8 | 643.3 | 729.4 | 550.9 | 665.4 | 698.5 | 665.3 | 111.1 | 229.9 | 262.8 | 173.3 | 339.3 | 321.2 | 199.5 | 287
1109 | 957 | 472.8 | 189.12 | 221.0704 | 360 | 310 | 324.9 | 317.6 | 481.6 | 52.5 | 19.4 | 89.3 | 4.2 | 187.5 | 3.7 | 814.7 | 722.8 | 716.6 | 763.2 | 640.2 | 728.7 | 547.9 | 650.3 | 696 | 662 | 111.3 | 230.1 | 263.1 | 173.5 | 339.1 | 321 | 199.7 | 287.1
1110 | 958 | 472.9 | 189.16 | 221.1171 | 361 | 310.1 | 325.4 | 317.7 | 479.5 | 52.7 | 19.4 | 89.3 | 4.3 | 185.5 | 3.8 | 813.9 | 722.2 | 718.7 | 762.6 | 639.6 | 728 | 545.6 | 656.4 | 694.6 | 660.6 | 111.5 | 230.3 | 263.2 | 173.6 | 338.8 | 320.9 | 199.9 | 287.1
1111 | 959 | 472.7 | 189.08 | 221.0236 | 361.7 | 310.2 | 325.7 | 318.3 | 485.8 | 52.8 | 19.4 | 89.5 | 4.3 | 181.8 | 3.7 | 814.2 | 716.3 | 722.2 | 762.1 | 638.9 | 727.3 | 543.1 | 656.3 | 693.3 | 659.2 | 111.7 | 230.5 | 263.6 | 173.8 | 338.6 | 320.9 | 200.1 | 287.2
1112 | 960 | 472.7 | 189.08 | 221.0236 | 364.9 | 309 | 325.9 | 319.1 | 489 | 52.8 | 19.4 | 89.6 | 3.5 | 174.8 | 3.4 | 814.3 | 706.2 | 721.2 | 760.3 | 637.2 | 726.6 | 538.4 | 662.5 | 691.2 | 657.8 | 111.9 | 230.8 | 264.1 | 173.9 | 338.5 | 320.8 | 200.4 | 287.3
1113 | 961 | 472.7 | 189.08 | 221.0236 | 365 | 308.1 | 326.9 | 320.3 | 505.1 | 52.7 | 19.3 | 89.8 | 3.8 | 184.2 | 3.2 | 815 | 703.4 | 731.4 | 759.8 | 638 | 726.1 | 535.6 | 684.9 | 689.6 | 657.6 | 112.1 | 231 | 264.6 | 174.1 | 338.7 | 320.6 | 200.6 | 287.3
1114 | 962 | 473 | 189.2 | 221.1639 | 363.9 | 308.6 | 327.3 | 321.3 | 532.7 | 52.7 | 19.3 | 89.9 | 3.7 | 210.4 | 3.2 | 818.1 | 712.4 | 735.4 | 760.7 | 639.8 | 725.7 | 536.5 | 709.7 | 690.2 | 659.8 | 112.3 | 231.3 | 265 | 174.3 | 339 | 320.9 | 200.8 | 287.3
1115 | 963 | 472 | 188.8 | 220.6963 | 363.7 | 309.6 | 327.2 | 322.4 | 535.5 | 52.7 | 19.3 | 89.9 | 3.7 | 217.9 | 3.2 | 819.2 | 711.5 | 740.1 | 760.2 | 638.8 | 725.3 | 537.2 | 705.7 | 689.9 | 658.8 | 112.5 | 231.5 | 265.1 | 174.4 | 339.4 | 321 | 201 | 287.4
1116 | 964 | 472.3 | 188.92 | 220.8366 | 364.7 | 310.3 | 327.5 | 323.5 | 529.3 | 52.7 | 19.4 | 89.9 | 3.3 | 183 | 3.2 | 819.7 | 711.8 | 749.5 | 761 | 640 | 724.8 | 535.1 | 710.5 | 689.2 | 658.7 | 112.7 | 231.7 | 265.4 | 174.6 | 340.3 | 320.8 | 201.2 | 287.5
1117 | 965 | 473.5 | 189.4 | 221.3977 | 363.6 | 310.4 | 328.2 | 324.6 | 525 | 52.7 | 19.3 | 90 | 3.8 | 184.7 | 3.8 | 822 | 731.8 | 755.5 | 764.5 | 643.2 | 724.3 | 540.2 | 719.8 | 691 | 662.1 | 112.9 | 232 | 265.4 | 174.8 | 340.6 | 320.7 | 201.5 | 287.6
1118 | 966 | 473.1 | 189.24 | 221.2107 | 363 | 311.5 | 328.6 | 325.5 | 520.3 | 52.7 | 19.3 | 90 | 3.6 | 205.3 | 4.7 | 824.8 | 747.9 | 761.2 | 767.5 | 646.9 | 723.8 | 543.8 | 728.3 | 692.6 | 664.2 | 113.1 | 232.2 | 265.4 | 174.9 | 340.7 | 320.7 | 201.7 | 287.7
1119 | 967 | 472.8 | 189.12 | 221.0704 | 363.2 | 312.3 | 328.3 | 325.7 | 527.7 | 52.7 | 19.3 | 90 | 3.8 | 184.7 | 5.4 | 826.9 | 754 | 764.7 | 769.8 | 648 | 723.2 | 543.8 | 738.5 | 693 | 664.5 | 113.3 | 232.4 | 265.8 | 175.1 | 340.9 | 320.6 | 201.9 | 287.9
1120 | 968 | 472.4 | 188.96 | 220.8834 | 364.6 | 312.7 | 328.3 | 325.2 | 527.7 | 52.8 | 19.3 | 90 | 3.7 | 181.6 | 5.7 | 825.5 | 745 | 755 | 770.2 | 645.1 | 722.7 | 543.4 | 725.8 | 692.8 | 662.5 | 113.5 | 232.6 | 265.9 | 175.2 | 341 | 320.8 | 202.1 | 287.9
1121 | 969 | 472.9 | 189.16 | 221.1171 | 366.1 | 312.9 | 328.8 | 324.6 | 520.1 | 52.8 | 19.3 | 89.9 | 3.6 | 181.8 | 5.8 | 824 | 741 | 750.2 | 769.7 | 643.3 | 722.1 | 543.4 | 717.6 | 692.4 | 661.9 | 113.8 | 232.9 | 266.1 | 175.4 | 340.9 | 321.3 | 202.3 | 288
1122 | 970 | 472.7 | 189.08 | 221.0236 | 367.5 | 314 | 328.5 | 324.5 | 511.9 | 52.9 | 19.3 | 89.9 | 3.6 | 182.1 | 5.9 | 823.3 | 744.5 | 752.8 | 769.5 | 645.2 | 721.4 | 543 | 711.6 | 692.3 | 661.7 | 114 | 233.1 | 266.1 | 175.6 | 340.9 | 321.8 | 202.5 | 288.2
1123 | 971 | 472.7 | 189.08 | 221.0236 | 369.1 | 314.8 | 328 | 324.2 | 503.9 | 53 | 19.3 | 89.9 | 3.9 | 182.5 | 5.9 | 822.9 | 748.7 | 744.4 | 769.9 | 643.6 | 720.8 | 539.3 | 706.9 | 691.1 | 660.2 | 114.2 | 233.3 | 266.2 | 175.7 | 341.1 | 322.2 | 202.8 | 288.4
1124 | 972 | 472 | 188.8 | 220.6963 | 369.3 | 315.5 | 328 | 323.9 | 504.6 | 53.1 | 19.3 | 89.9 | 4.2 | 183.4 | 5.7 | 822.1 | 754.6 | 738 | 771.1 | 642.2 | 720.1 | 539.9 | 701.1 | 690.5 | 659.1 | 114.4 | 233.5 | 266.4 | 175.9 | 340.9 | 322.4 | 202.9 | 288.5
1125 | 973 | 472.5 | 189 | 220.9301 | 368.3 | 315.3 | 328.1 | 323.5 | 504.5 | 53.1 | 19.3 | 90.1 | 3.9 | 187.2 | 5.7 | 823 | 765.1 | 734.9 | 771.8 | 643.5 | 719.5 | 543.3 | 703.3 | 691.2 | 659 | 114.6 | 233.7 | 266.4 | 176 | 340.7 | 322.3 | 203.2 | 288.6
1126 | 974 | 472.6 | 189.04 | 220.9769 | 367.6 | 315.4 | 328 | 323.2 | 507.5 | 53 | 19.3 | 90.3 | 3.9 | 185.3 | 5.6 | 824.6 | 769 | 742.5 | 771 | 645.1 | 719 | 542.6 | 722.1 | 693 | 660.9 | 114.8 | 233.9 | 266.8 | 176.2 | 340.5 | 322.1 | 203.4 | 288.6
1127 | 975 | 471.8 | 188.72 | 220.6028 | 366.7 | 315.8 | 327.8 | 322.8 | 511.2 | 53 | 19.3 | 90.5 | 3.7 | 184.2 | 5.3 | 828.5 | 776.2 | 748.9 | 773.6 | 648 | 718.5 | 544.6 | 727.7 | 693.5 | 662.7 | 115 | 234.1 | 267.2 | 176.4 | 340.4 | 322.2 | 203.6 | 288.7
1128 | 976 | 473.2 | 189.28 | 221.2574 | 365.6 | 316.1 | 327.8 | 322.2 | 512.8 | 53.1 | 19.3 | 90.6 | 4 | 184.9 | 5.1 | 830.5 | 779.3 | 753.1 | 775.7 | 649.3 | 718.3 | 548.6 | 733.2 | 695.5 | 665.1 | 115.1 | 234.3 | 267.2 | 176.5 | 340.1 | 322.3 | 203.8 | 288.8
1129 | 977 | 471.9 | 188.76 | 220.6496 | 364.5 | 316.6 | 327.3 | 321.2 | 511.3 | 53.2 | 19.3 | 90.6 | 3.6 | 184.9 | 4.8 | 829.6 | 776.6 | 751.1 | 776 | 649.1 | 717.8 | 549 | 723.7 | 695.3 | 663.7 | 115.3 | 234.5 | 267.1 | 176.7 | 340 | 321.7 | 204 | 288.8
1130 | 978 | 473 | 189.2 | 221.1639 | 364.6 | 315.9 | 327 | 320.8 | 505.8 | 53.3 | 19.3 | 90.7 | 3.6 | 187.1 | 4.5 | 830.5 | 782.9 | 748.8 | 778.1 | 650.1 | 717.5 | 551 | 717.1 | 696.1 | 663.5 | 115.5 | 234.7 | 267.2 | 176.9 | 339.9 | 321.3 | 204.2 | 288.9
1131 | 979 | 472.4 | 188.96 | 220.8834 | 364.9 | 314.6 | 326.6 | 320.4 | 498.8 | 53.4 | 19.3 | 90.7 | 4.3 | 194.2 | 4.4 | 830 | 785.2 | 749 | 778.8 | 650.9 | 717 | 550.6 | 714 | 696.5 | 662.4 | 115.8 | 234.8 | 267.2 | 177 | 339.6 | 321.1 | 204.4 | 288.9
1132 | 980 | 472.8 | 189.12 | 221.0704 | 367.1 | 313.9 | 326.2 | 319.5 | 490.5 | 53.4 | 19.3 | 90.8 | 4.3 | 195.2 | 4.3 | 829 | 789.2 | 739.7 | 780.1 | 649.5 | 716.4 | 554.8 | 703.5 | 698 | 662.9 | 116 | 235 | 267.3 | 177.2 | 339.6 | 321.1 | 204.7 | 289
1133 | 981 | 472.2 | 188.88 | 220.7898 | 367.8 | 313.8 | 326.4 | 318.2 | 486.3 | 53.5 | 19.3 | 90.9 | 3.8 | 189.6 | 4.4 | 829.1 | 795.4 | 741.9 | 781.7 | 650.3 | 715.9 | 558.6 | 704 | 700.1 | 663.9 | 116.2 | 235.2 | 267.4 | 177.4 | 339.5 | 321.2 | 204.8 | 289
1134 | 982 | 472.4 | 188.96 | 220.8834 | 367.3 | 313.5 | 326.6 | 317.5 | 482.2 | 53.5 | 19.3 | 91 | 3.3 | 184.3 | 4.3 | 829.5 | 794.6 | 745.1 | 782.2 | 652.2 | 715.5 | 560 | 697.7 | 700.9 | 664.5 | 116.4 | 235.3 | 267.5 | 177.5 | 339.3 | 320.9 | 205.1 | 289.1
1135 | 983 | 472.7 | 189.08 | 221.0236 | 366 | 312.2 | 326.2 | 317.4 | 480.7 | 53.6 | 19.3 | 91.1 | 3.9 | 186.8 | 4.2 | 830.3 | 795.3 | 752.6 | 783.6 | 654.3 | 715 | 560.4 | 705.6 | 700.7 | 664 | 116.6 | 235.5 | 267.6 | 177.7 | 339.1 | 320.8 | 205.2 | 289.1
1136 | 984 | 472.5 | 189 | 220.9301 | 364.7 | 311.3 | 326.2 | 317 | 483.5 | 53.7 | 19.3 | 91.2 | 3.6 | 197.6 | 4.3 | 832.2 | 796 | 749.6 | 784.7 | 654.4 | 714.8 | 561.3 | 718.5 | 701 | 665.4 | 116.8 | 235.7 | 267.7 | 177.9 | 338.8 | 320.7 | 205.5 | 289.2
1137 | 985 | 472.8 | 189.12 | 221.0704 | 364.4 | 310.4 | 326 | 316.4 | 488 | 53.9 | 19.3 | 91.3 | 4 | 199.8 | 4.3 | 832.8 | 788.8 | 740.6 | 784.7 | 652.7 | 714.6 | 559.7 | 713 | 699.8 | 663.8 | 117 | 235.8 | 268 | 178 | 338.8 | 320.5 | 205.7 | 289.2
1138 | 986 | 472.9 | 189.16 | 221.1171 | 364.6 | 310.6 | 326 | 315.7 | 484 | 53.9 | 19.3 | 91.3 | 4 | 197.9 | 4.1 | 829.9 | 776.1 | 734.1 | 782 | 650.1 | 714.2 | 555.5 | 696.1 | 697.7 | 660.6 | 117.3 | 236 | 268.2 | 178.2 | 338.6 | 320.6 | 205.9 | 289.1
1139 | 987 | 472 | 188.8 | 220.6963 | 364.7 | 310 | 326.3 | 315.6 | 482.9 | 54 | 19.3 | 91.3 | 3.8 | 187.3 | 4.1 | 828.1 | 770 | 729 | 780.9 | 648.2 | 714 | 550.4 | 704.3 | 695.8 | 660.2 | 117.5 | 236.2 | 268.5 | 178.4 | 338.5 | 320.3 | 206.1 | 289.1
1140 | 988 | 472.5 | 189 | 220.9301 | 364.9 | 310.6 | 326.7 | 315.8 | 487.9 | 54 | 19.3 | 91.3 | 4 | 169.1 | 4.1 | 825.3 | 762.6 | 725.2 | 778.2 | 646 | 713.7 | 548.3 | 690.7 | 694 | 657.9 | 117.7 | 236.4 | 268.7 | 178.6 | 338.4 | 320.2 | 206.3 | 289.2
1141 | 989 | 472.5 | 189 | 220.9301 | 367.3 | 310.5 | 326.8 | 316.3 | 482.9 | 54 | 19.3 | 91.3 | 4 | 174.1 | 4.2 | 821 | 746.2 | 716.4 | 774.9 | 642.6 | 713.4 | 543.6 | 670.5 | 691.1 | 654.2 | 117.9 | 236.6 | 269 | 178.7 | 338.2 | 320 | 206.5 | 289.2
1142 | 990 | 471.9 | 188.76 | 220.6496 | 368.4 | 309.6 | 327.3 | 316.6 | 473.6 | 54.1 | 19.3 | 91.4 | 4.2 | 182.2 | 4.5 | 818.9 | 735.4 | 718.6 | 773.8 | 641.6 | 713 | 538.9 | 661.2 | 688.5 | 651.9 | 118.1 | 236.8 | 269 | 178.9 | 338 | 319.8 | 206.7 | 289.2
1143 | 991 | 472 | 188.8 | 220.6963 | 368.3 | 309.6 | 327.3 | 316.5 | 473.7 | 54.1 | 19.3 | 91.4 | 3.9 | 183.9 | 4.6 | 821.1 | 745.8 | 725.1 | 774.2 | 643.4 | 712.6 | 539.4 | 674.5 | 688.4 | 653.1 | 118.3 | 237 | 269.1 | 179.1 | 337.6 | 319.9 | 206.9 | 289.3
1144 | 992 | 472.6 | 189.04 | 220.9769 | 367.5 | 308.8 | 327 | 316.1 | 478.2 | 54.2 | 19.3 | 91.3 | 4 | 186 | 4.7 | 822 | 754.7 | 724.5 | 774.5 | 642.4 | 712.3 | 541.9 | 678.9 | 689.2 | 652.1 | 118.5 | 237.1 | 269.2 | 179.3 | 337.2 | 320 | 207.1 | 289.4
1145 | 993 | 473.2 | 189.28 | 221.2574 | 366.4 | 308.1 | 327.2 | 315.6 | 488.4 | 54.3 | 19.3 | 91.3 | 3.8 | 185.7 | 4.7 | 822.8 | 754.4 | 719.4 | 774 | 641.6 | 712 | 544.1 | 691.7 | 690.2 | 652.5 | 118.7 | 237.3 | 269.5 | 179.4 | 337.3 | 320.2 | 207.3 | 289.4
1146 | 994 | 473.4 | 189.36 | 221.3509 | 366.2 | 308.2 | 327.7 | 314.7 | 492.2 | 54.4 | 19.3 | 91.3 | 3.4 | 187 | 4.7 | 817.7 | 735.3 | 701.1 | 769.3 | 637.3 | 711.6 | 539.7 | 668.5 | 687.8 | 648.6 | 118.9 | 237.5 | 270 | 179.6 | 337.8 | 320.3 | 207.6 | 289.4
1147 | 995 | 475.4 | 190.16 | 222.2861 | 367.7 | 308.7 | 328.4 | 314.1 | 489.3 | 54.5 | 19.3 | 91.4 | 3.2 | 189.4 | 4.5 | 811.1 | 722.5 | 683.9 | 765.2 | 633.2 | 711.1 | 537.7 | 648 | 685.7 | 645.2 | 119.1 | 237.7 | 270.1 | 179.8 | 337.8 | 320.1 | 207.7 | 289.4
1148 | 996 | 475.9 | 190.36 | 222.5199 | 368.1 | 309.1 | 328.8 | 314.6 | 479.4 | 54.5 | 19.3 | 91.5 | 3.8 | 190.5 | 4.5 | 804.6 | 706.7 | 674.1 | 759.8 | 630.1 | 710.5 | 534.3 | 628.8 | 683.4 | 642.2 | 119.3 | 237.9 | 270.1 | 180 | 337.5 | 319.7 | 207.9 | 289.4
1149 | 997 | 476.2 | 190.48 | 222.6601 | 368.7 | 309.9 | 328.5 | 315.5 | 473.1 | 54.6 | 19.3 | 91.5 | 3.8 | 191.3 | 4.9 | 802 | 704 | 673.4 | 758.2 | 629.1 | 709.7 | 530.5 | 634.3 | 681.8 | 640.3 | 119.5 | 238 | 270.1 | 180.1 | 337.1 | 319.1 | 208.1 | 289.4
1150 | 998 | 475.2 | 190.08 | 222.1926 | 368.5 | 310.2 | 328.4 | 315.6 | 475.4 | 54.6 | 19.3 | 91.6 | 4 | 186.9 | 5 | 803.4 | 713.3 | 676.6 | 758.1 | 629.1 | 709.1 | 532.1 | 658.1 | 682 | 641.3 | 119.8 | 238.2 | 270.1 | 180.3 | 336.6 | 318.8 | 208.3 | 289.4
1151 | 999 | 475.1 | 190.04 | 222.1458 | 367.4 | 309.5 | 328.1 | 315 | 480.8 | 54.7 | 19.3 | 91.6 | 4.3 | 174.1 | 4.5 | 801.9 | 714.9 | 665.1 | 757.4 | 626.9 | 708.5 | 534.3 | 649 | 682.1 | 640 | 120 | 238.4 | 270.3 | 180.5 | 336.3 | 318.9 | 208.6 | 289.5
1152 | 1000 | 473.6 | 189.44 | 221.4444 | 366.9 | 308.1 | 327.7 | 314.1 | 477.1 | 54.7 | 19.3 | 91.7 | 4.3 | 161.9 | 3.6 | 796.7 | 705.7 | 656.7 | 755.7 | 623.9 | 707.7 | 533.2 | 626.5 | 680 | 637.2 | 120.2 | 238.6 | 270.3 | 180.6 | 335.9 | 319 | 208.7 | 289.6
1153 | 1001 | 474.2 | 189.68 | 221.725 | 367.7 | 306.8 | 327.5 | 313.3 | 467.2 | 54.7 | 19.3 | 91.8 | 4.4 | 153.8 | 3.1 | 792.9 | 715 | 658.6 | 756.4 | 624.3 | 706.9 | 536.4 | 623.1 | 678.9 | 637.4 | 120.4 | 238.7 | 270.3 | 180.8 | 335.8 | 318.9 | 208.9 | 289.6
1154 | 1002 | 473.7 | 189.48 | 221.4912 | 368.7 | 306.6 | 327.6 | 313.1 | 464.3 | 54.6 | 19.3 | 91.8 | 4.5 | 154.6 | 3 | 790.7 | 725.9 | 659.5 | 757.5 | 623.8 | 706.1 | 543.7 | 615.8 | 680.2 | 637.9 | 120.6 | 238.9 | 270.4 | 181 | 335.9 | 318.9 | 209.1 | 289.7
1155 | 1003 | 473.8 | 189.52 | 221.538 | 368.7 | 306.5 | 327.6 | 313.5 | 460.1 | 54.6 | 19.3 | 91.9 | 4.5 | 181 | 3.4 | 789.6 | 728.8 | 661 | 757.8 | 623.6 | 705.3 | 547.8 | 612.5 | 680.7 | 637.2 | 120.8 | 239 | 270.4 | 181.1 | 336.2 | 318.9 | 209.3 | 289.8
1156 | 1004 | 473.6 | 189.44 | 221.4444 | 367.4 | 305 | 328 | 313.5 | 454.7 | 54.4 | 19.3 | 92 | 4.1 | 187.8 | 3.5 | 787.2 | 722.5 | 657.7 | 757.9 | 622.4 | 704.4 | 546.8 | 602.7 | 680.1 | 635.1 | 121 | 239.1 | 270.5 | 181.3 | 336.4 | 318.8 | 209.6 | 289.9
1157 | 1005 | 474.2 | 189.68 | 221.725 | 367.2 | 303.5 | 328.6 | 313.7 | 449.8 | 54.2 | 19.3 | 92.1 | 4.2 | 184.6 | 3.5 | 786.4 | 720.7 | 667.6 | 757.8 | 622 | 703.5 | 541 | 597.1 | 677.5 | 632.3 | 121.2 | 239.3 | 270.6 | 181.5 | 336.6 | 318.7 | 209.8 | 289.9
1158 | 1006 | 474.2 | 189.68 | 221.725 | 366.6 | 303 | 328.9 | 314.1 | 452.1 | 54 | 19.3 | 92.3 | 4.2 | 183.7 | 3.4 | 791.6 | 741.3 | 694.8 | 759.6 | 626 | 702.7 | 543 | 629.2 | 677.7 | 635.7 | 121.4 | 239.4 | 270.8 | 181.7 | 336.4 | 319 | 210 | 290
1159 | 1007 | 474.1 | 189.64 | 221.6782 | 365.5 | 303.1 | 328.7 | 314 | 462.1 | 53.9 | 19.3 | 92.4 | 4.3 | 183.7 | 3.1 | 798.1 | 759.1 | 722.5 | 762.3 | 631.5 | 702.2 | 547.2 | 663.5 | 680.9 | 641.7 | 121.6 | 239.6 | 270.9 | 181.8 | 336.4 | 319.2 | 210.1 | 290.1
1160 | 1008 | 473.5 | 189.4 | 221.3977 | 365 | 303.4 | 328.7 | 313.5 | 488.4 | 54 | 19.3 | 92.5 | 3.9 | 182.8 | 2.9 | 804.3 | 773 | 732.4 | 765.4 | 634 | 701.9 | 552 | 692.5 | 685.6 | 647.4 | 121.8 | 239.7 | 271.3 | 182 | 336.4 | 319.3 | 210.4 | 290.1
1161 | 1009 | 473.8 | 189.52 | 221.538 | 363.7 | 304.1 | 328.6 | 312.6 | 509.9 | 54.2 | 19.3 | 92.5 | 4.1 | 180.6 | 2.8 | 807.9 | 783.2 | 735.1 | 767.8 | 635 | 701.8 | 554.8 | 693.2 | 687.8 | 648 | 122 | 239.9 | 271.6 | 182.2 | 336.5 | 319.4 | 210.6 | 290.1
1162 | 1010 | 471.9 | 188.76 | 220.6496 | 362.2 | 305 | 328.4 | 312.3 | 500.3 | 54.3 | 19.3 | 92.6 | 4 | 169.8 | 2.7 | 810 | 792.6 | 735.4 | 769.1 | 636 | 701.4 | 559.6 | 677.4 | 688.5 | 648.4 | 122.2 | 240 | 271.6 | 182.4 | 336.5 | 319.2 | 210.8 | 290.1
1163 | 1011 | 470.5 | 188.2 | 219.995 | 361.3 | 304.8 | 328.4 | 312.5 | 494.2 | 54.4 | 19.3 | 92.7 | 3.9 | 154 | 2.5 | 811.2 | 799.3 | 746.8 | 771.8 | 640.5 | 701.3 | 570.9 | 673.3 | 690.8 | 653.3 | 122.4 | 240.2 | 271.7 | 182.6 | 336.7 | 319.3 | 211 | 290.3
1164 | 1012 | 471.3 | 188.52 | 220.369 | 360.8 | 304.8 | 327.8 | 312.8 | 494.1 | 54.5 | 19.3 | 92.8 | 3.7 | 154 | 2.3 | 812.7 | 800.4 | 757.2 | 774.7 | 644.4 | 701.6 | 582.2 | 695.6 | 695.5 | 658.4 | 122.6 | 240.3 | 271.7 | 182.7 | 337 | 319.4 | 211.2 | 290.5
1165 | 1013 | 472.6 | 189.04 | 220.9769 | 359.7 | 304.5 | 327.2 | 313.4 | 498.7 | 54.6 | 19.3 | 92.8 | 3.7 | 161.9 | 2.2 | 815.4 | 803.7 | 763.4 | 778 | 648.2 | 701.9 | 590.8 | 723.4 | 699.4 | 663 | 122.8 | 240.5 | 271.8 | 182.9 | 337.1 | 319.4 | 211.4 | 290.5
1166 | 1014 | 474.2 | 189.68 | 221.725 | 358.2 | 304.7 | 327 | 313.3 | 507.5 | 54.7 | 19.3 | 92.9 | 3.8 | 155.2 | 2.1 | 818.1 | 805.7 | 776.2 | 779.8 | 653.7 | 702.4 | 599.1 | 744.4 | 704.2 | 668.5 | 122.9 | 240.6 | 272 | 183.1 | 337.4 | 320 | 211.6 | 290.6
1167 | 1015 | 473.8 | 189.52 | 221.538 | 356.9 | 305.5 | 327.5 | 312.9 | 514.1 | 54.8 | 19.3 | 92.9 | 3.6 | 157.5 | 1.9 | 821.7 | 813.8 | 784.9 | 782.4 | 657.3 | 702.9 | 599.3 | 762.7 | 707.3 | 672.4 | 123.1 | 240.8 | 272.3 | 183.3 | 337.7 | 320.6 | 211.8 | 290.7
1168 | 1016 | 472.3 | 188.92 | 220.8366 | 356.3 | 305.8 | 327.8 | 313.1 | 531.7 | 54.8 | 19.3 | 92.9 | 3.4 | 184 | 1.8 | 824.5 | 810.1 | 774.9 | 782.9 | 656.9 | 703.3 | 593 | 772.6 | 706.9 | 671.5 | 123.3 | 240.9 | 272.7 | 183.4 | 338 | 321.2 | 212 | 290.8
1169 | 1017 | 471.9 | 188.76 | 220.6496 | 356 | 306.2 | 327.7 | 313.2 | 535 | 54.6 | 19.3 | 92.8 | 3.5 | 204.9 | 1.9 | 825.5 | 802.2 | 774.9 | 783.7 | 657.1 | 703.8 | 585.8 | 760.8 | 705.5 | 669.8 | 123.5 | 241.1 | 272.8 | 183.6 | 338.3 | 321.4 | 212.3 | 290.9
1170 | 1018 | 471.6 | 188.64 | 220.5093 | 358.8 | 306.6 | 327.9 | 313.1 | 530.6 | 54.5 | 19.3 | 92.8 | 3.6 | 205.2 | 1.8 | 828.2 | 810.4 | 772.8 | 786.1 | 660 | 704.4 | 584.8 | 758.3 | 706.3 | 671.4 | 123.7 | 241.3 | 272.8 | 183.8 | 338.5 | 322 | 212.4 | 291.1
1171 | 1019 | 471.6 | 188.64 | 220.5093 | 360.1 | 306.2 | 328 | 314 | 524.8 | 54.4 | 19.3 | 92.7 | 3.9 | 191.7 | 1.8 | 830.3 | 816.2 | 764 | 787.5 | 661.3 | 704.9 | 590.8 | 751.4 | 708.3 | 673.9 | 123.9 | 241.4 | 272.7 | 184 | 338.7 | 322.3 | 212.6 | 291.2
1172 | 1020 | 472.2 | 188.88 | 220.7898 | 359.3 | 305.9 | 327.4 | 314.1 | 517.3 | 54.4 | 19.2 | 92.7 | 4 | 191.4 | 1.8 | 831.4 | 815.7 | 753 | 787.1 | 660.2 | 705.4 | 589.2 | 749.5 | 708.8 | 672.5 | 124.1 | 241.6 | 272.9 | 184.1 | 338.8 | 322.2 | 212.8 | 291.2
1173 | 1021 | 472.3 | 188.92 | 220.8366 | 358.1 | 305.6 | 327 | 313.5 | 514.4 | 54.4 | 19.2 | 92.7 | 3.6 | 189.6 | 2.3 | 834.1 | 818.8 | 748.6 | 788.1 | 661 | 705.8 | 589.9 | 747.4 | 708.7 | 674.4 | 124.3 | 241.7 | 273 | 184.3 | 338.8 | 322.2 | 213.1 | 291.4
1174 | 1022 | 472.5 | 189 | 220.9301 | 357.2 | 305.4 | 326.9 | 312.8 | 518.8 | 54.4 | 19.2 | 92.7 | 4 | 180.2 | 2.8 | 833.7 | 805 | 738.1 | 786.1 | 657.8 | 706.4 | 584.2 | 736.2 | 707.1 | 671.6 | 124.5 | 241.9 | 273.3 | 184.5 | 339 | 321.9 | 213.2 | 291.4
1175 | 1023 | 472.2 | 188.88 | 220.7898 | 357.3 | 305.8 | 326.8 | 312.6 | 515 | 54.3 | 19.2 | 92.7 | 3.9 | 159.1 | 3.2 | 830.1 | 785.2 | 726.3 | 782.7 | 654.8 | 706.7 | 574 | 706.5 | 703 | 666.9 | 124.7 | 242 | 273.9 | 184.7 | 339 | 321.5 | 213.4 | 291.3
1176 | 1024 | 472.3 | 188.92 | 220.8366 | 357.7 | 306.2 | 326.8 | 312.3 | 504.3 | 54.3 | 19.2 | 92.7 | 4.1 | 155.3 | 3.3 | 826.8 | 773.2 | 726.1 | 781.2 | 653.1 | 707 | 567.5 | 710.6 | 700.4 | 664.9 | 124.9 | 242.2 | 274 | 184.8 | 339.1 | 321.6 | 213.6 | 291.3
1177 | 1025 | 473 | 189.2 | 221.1639 | 358.8 | 306.5 | 327.1 | 311.6 | 506 | 54.4 | 19.2 | 92.8 | 3.5 | 171.2 | 3.6 | 826.4 | 771.1 | 741 | 780.9 | 655 | 707.2 | 566.6 | 719.1 | 700 | 664.4 | 125.1 | 242.4 | 274.1 | 185 | 339.1 | 321.9 | 213.8 | 291.3
1178 | 1026 | 472.2 | 188.88 | 220.7898 | 359.3 | 306.7 | 326.6 | 311 | 520.2 | 54.4 | 19.2 | 92.9 | 3.6 | 183.2 | 3.5 | 826.2 | 762.3 | 746.9 | 779 | 655.1 | 707.6 | 564.6 | 711.9 | 698.4 | 662.5 | 125.3 | 242.6 | 274.5 | 185.2 | 339.3 | 321.4 | 214.1 | 291.3
1179 | 1027 | 472.6 | 189.04 | 220.9769 | 359.2 | 306.9 | 325.9 | 310.6 | 525.2 | 54.4 | 19.2 | 93 | 3.9 | 173.9 | 4.1 | 824.7 | 752.6 | 748.3 | 776.9 | 653 | 707.8 | 560.6 | 700.2 | 695.7 | 659.2 | 125.4 | 242.8 | 274.8 | 185.4 | 339.5 | 321.3 | 214.3 | 291.2
1180 | 1028 | 470.6 | 188.24 | 220.0417 | 359.4 | 307 | 326.5 | 311.4 | 525.8 | 54.5 | 19.2 | 93.1 | 4.2 | 173.7 | 4.7 | 824.8 | 748.3 | 752.6 | 776.4 | 653.4 | 708 | 557.7 | 718.3 | 694.4 | 659.1 | 125.6 | 243 | 275.1 | 185.6 | 339.6 | 321.4 | 214.5 | 291.2
1181 | 1029 | 470.9 | 188.36 | 220.182 | 359 | 307.6 | 327.6 | 312.7 | 531.2 | 54.5 | 19.2 | 93.2 | 3.8 | 181.8 | 4.9 | 826 | 754.8 | 743 | 776.2 | 651.6 | 708.4 | 556.4 | 731.1 | 694.7 | 659.2 | 125.8 | 243.2 | 275.1 | 185.7 | 339.6 | 321.6 | 214.7 | 291.3
1182 | 1030 | 472.6 | 189.04 | 220.9769 | 358.1 | 307.6 | 327.8 | 313.8 | 541.3 | 54.5 | 19.2 | 93.3 | 3.7 | 184.1 | 5 | 828.4 | 760.5 | 751 | 777 | 652.4 | 708.7 | 557.3 | 752.6 | 696.4 | 660.6 | 126 | 243.3 | 275.2 | 185.9 | 339.8 | 321.8 | 214.9 | 291.3
1183 | 1031 | 473.4 | 189.36 | 221.3509 | 358.2 | 307.7 | 327.7 | 314.4 | 544.2 | 54.6 | 19.2 | 93.4 | 3.8 | 192.1 | 4.5 | 832.6 | 775 | 770.9 | 779.6 | 655.9 | 709.1 | 559.3 | 764.5 | 697.7 | 664.2 | 126.2 | 243.5 | 275.3 | 186.1 | 339.8 | 322 | 215.1 | 291.4
1184 | 1032 | 474.1 | 189.64 | 221.6782 | 357 | 308.7 | 327.3 | 315.1 | 538.6 | 54.7 | 19.2 | 93.5 | 3.6 | 200.6 | 4 | 835.6 | 783.8 | 781.9 | 782.6 | 660.9 | 709.4 | 563.3 | 766.3 | 699.9 | 666.7 | 126.4 | 243.7 | 275.3 | 186.3 | 339.7 | 322.4 | 215.3 | 291.5
1185 | 1033 | 472.7 | 189.08 | 221.0236 | 355.4 | 309.2 | 327 | 315.8 | 533.6 | 54.9 | 19.2 | 93.5 | 3.8 | 192 | 3.4 | 837.9 | 794.5 | 776.5 | 785.3 | 661.6 | 709.6 | 567.4 | 758.1 | 702.6 | 666.5 | 126.6 | 243.9 | 275.4 | 186.5 | 339.6 | 322.8 | 215.5 | 291.6
1186 | 1034 | 471.9 | 188.76 | 220.6496 | 354.8 | 309.4 | 326.7 | 315.8 | 527 | 55 | 19.2 | 93.5 | 3.9 | 193.5 | 2.7 | 838.5 | 801.6 | 758.8 | 785.8 | 660.1 | 709.8 | 567.2 | 758.3 | 703.6 | 666 | 126.8 | 244 | 275.5 | 186.6 | 339.5 | 323 | 215.7 | 291.6
1187 | 1035 | 471.8 | 188.72 | 220.6028 | 355.9 | 310.1 | 326.7 | 315.4 | 527.1 | 55.1 | 19.2 | 93.5 | 3.9 | 210.9 | 2.3 | 838.6 | 795 | 749.7 | 784.8 | 657.4 | 710.1 | 566.7 | 764.2 | 704.2 | 665.8 | 127 | 244.2 | 275.7 | 186.8 | 339.4 | 322.8 | 215.9 | 291.6
1188 | 1036 | 471.3 | 188.52 | 220.369 | 356.9 | 310.9 | 326.9 | 315 | 528 | 55.1 | 19.2 | 93.5 | 3.7 | 213.3 | 2.1 | 840.2 | 796.2 | 759.6 | 785.3 | 659.9 | 710.4 | 566.8 | 779.9 | 705.7 | 667.7 | 127.2 | 244.4 | 276 | 187 | 339.6 | 322.4 | 216.1 | 291.6
1189 | 1037 | 470.1 | 188.04 | 219.8079 | 357.5 | 311.2 | 327 | 314.1 | 539.9 | 55.2 | 19.2 | 93.5 | 3.7 | 190.5 | 2.3 | 840.5 | 790.2 | 752.6 | 785.4 | 658.5 | 710.9 | 566.1 | 773.1 | 705.3 | 667.5 | 127.3 | 244.6 | 276.1 | 187.2 | 339.7 | 322.2 | 216.3 | 291.7
1190 | 1038 | 470.9 | 188.36 | 220.182 | 357.9 | 312.6 | 326.8 | 314.4 | 536.4 | 55.1 | 19.2 | 93.5 | 3.7 | 159.6 | 2.5 | 837.5 | 776 | 745.4 | 782.7 | 655.9 | 711.1 | 560.9 | 753.4 | 702.2 | 664.9 | 127.5 | 244.8 | 276.5 | 187.3 | 339.7 | 321.8 | 216.5 | 291.6
1191 | 1039 | 472 | 188.8 | 220.6963 | 358.7 | 313.8 | 326.7 | 314.8 | 525.3 | 55 | 19.2 | 93.5 | 3.8 | 152.6 | 2.8 | 835.4 | 776 | 742.3 | 782.2 | 654.9 | 711.3 | 557.8 | 741.1 | 699.8 | 662.8 | 127.7 | 244.9 | 276.8 | 187.5 | 339.7 | 321.5 | 216.7 | 291.6
1192 | 1040 | 472.9 | 189.16 | 221.1171 | 359.2 | 314.6 | 326.6 | 314.8 | 516.3 | 54.9 | 19.2 | 93.5 | 3.7 | 176.8 | 3.2 | 833.9 | 773.9 | 743.4 | 781.5 | 654.4 | 711.3 | 555.9 | 727.5 | 697.8 | 661.1 | 127.9 | 245.1 | 277 | 187.7 | 339.6 | 321.2 | 216.9 | 291.6
1193 | 1041 | 472 | 188.8 | 220.6963 | 359.8 | 315.6 | 326.6 | 315.1 | 513 | 54.9 | 19.2 | 93.6 | 4 | 188.1 | 3.4 | 831.4 | 767.8 | 752.7 | 779.9 | 655.2 | 711.2 | 551.4 | 726.6 | 695.5 | 659.6 | 128.1 | 245.3 | 277.2 | 187.9 | 339.4 | 321.2 | 217.1 | 291.6
1194 | 1042 | 472.9 | 189.16 | 221.1171 | 360.6 | 316.3 | 326.2 | 315 | 511.2 | 55 | 19.2 | 93.6 | 3.6 | 190.7 | 3.7 | 834.4 | 785.8 | 761.4 | 781.9 | 658.8 | 711.3 | 556.2 | 748.6 | 698.4 | 665.4 | 128.3 | 245.5 | 277.3 | 188.1 | 339.5 | 321.3 | 217.3 | 291.6
1195 | 1043 | 470.1 | 188.04 | 219.8079 | 359.9 | 315.8 | 326.1 | 314.8 | 522.6 | 55.1 | 19.2 | 93.6 | 3.3 | 188.7 | 4.4 | 836.4 | 793.6 | 747 | 783.5 | 658.2 | 711.5 | 554 | 751.7 | 699 | 665.7 | 128.5 | 245.7 | 277.5 | 188.3 | 339.6 | 321.2 | 217.5 | 291.6
1196 | 1044 | 470.9 | 188.36 | 220.182 | 359 | 315.3 | 326.3 | 314.8 | 529.6 | 55.2 | 19.2 | 93.6 | 3.6 | 175.9 | 4.7 | 839.2 | 801.4 | 751.3 | 784.4 | 659.3 | 711.6 | 553.5 | 762.4 | 699.7 | 666.3 | 128.6 | 245.9 | 277.9 | 188.4 | 339.6 | 321.2 | 217.7 | 291.6
1197 | 1045 | 469.8 | 187.92 | 219.6677 | 358.6 | 315 | 326.5 | 315.4 | 537.8 | 55.2 | 19.2 | 93.6 | 3.9 | 181.6 | 4.8 | 841.7 | 806 | 758.3 | 785.8 | 661 | 711.8 | 553.8 | 767.5 | 700.2 | 667.3 | 128.8 | 246.1 | 278.1 | 188.6 | 339.6 | 321.2 | 217.9 | 291.6
1198 | 1046 | 472.2 | 188.88 | 220.7898 | 359.1 | 314.5 | 326.1 | 315.9 | 544.1 | 55.3 | 19.2 | 93.5 | 3.5 | 182.5 | 4.9 | 842.8 | 809.1 | 758.5 | 786.8 | 659.2 | 711.9 | 554.6 | 774.7 | 701.1 | 667.8 | 129 | 246.3 | 278.1 | 188.8 | 339.7 | 320.9 | 218.1 | 291.7
1199 | 1047 | 471.2 | 188.48 | 220.3223 | 359.6 | 315.4 | 325.2 | 315.7 | 545.6 | 55.3 | 19.2 | 93.5 | 3.4 | 180.8 | 5.2 | 844 | 812 | 769.5 | 788.7 | 661 | 712.3 | 560.5 | 788.9 | 705 | 671.3 | 129.2 | 246.5 | 278.2 | 189 | 339.5 | 321.3 | 218.3 | 291.7
1200 | 1048 | 472.3 | 188.92 | 220.8366 | 359 | 316.2 | 324.4 | 315.5 | 569.2 | 55.4 | 19.2 | 93.4 | 3.6 | 186 | 5 | 844.7 | 815 | 782.5 | 790.6 | 667 | 713.3 | 571.9 | 802.8 | 710.9 | 677.6 | 129.4 | 246.6 | 278.4 | 189.1 | 339.6 | 321.5 | 218.5 | 291.9
1201 | 1049 | 471.6 | 188.64 | 220.5093 | 357.9 | 316.9 | 324 | 315.2 | 582.5 | 55.4 | 19.2 | 93.4 | 3.7 | 192.2 | 4.9 | 845.5 | 815.9 | 794.9 | 792.9 | 673.5 | 714.1 | 582.4 | 808.5 | 716.9 | 683.1 | 129.6 | 246.8 | 278.6 | 189.3 | 339.9 | 321.7 | 218.7 | 291.8
1202 | 1050 | 472.8 | 189.12 | 221.0704 | 356.2 | 317.9 | 324.5 | 314.9 | 575.7 | 55.5 | 19.2 | 93.4 | 4 | 193.4 | 4.3 | 846.2 | 826.6 | 787.7 | 795.1 | 675.2 | 714.8 | 587.3 | 807.7 | 720.8 | 686.5 | 129.8 | 247 | 278.7 | 189.5 | 340.1 | 322 | 218.9 | 291.9
1203 | 1051 | 472.2 | 188.88 | 220.7898 | 355.3 | 319.1 | 325.1 | 314.9 | 565.4 | 55.5 | 19.2 | 93.3 | 3.8 | 180.8 | 4.2 | 841.9 | 807.8 | 756.7 | 791 | 670.2 | 715.2 | 582.7 | 771.6 | 718.1 | 681.3 | 130 | 247.1 | 279 | 189.7 | 340.3 | 321.9 | 219.1 | 292
1204 | 1052 | 472.7 | 189.08 | 221.0236 | 355.8 | 320 | 325.5 | 314.8 | 543.1 | 55.4 | 19.2 | 93.3 | 4 | 190.6 | 4.3 | 837.6 | 794.5 | 750.2 | 789.2 | 668.9 | 715.2 | 573.8 | 747.7 | 713.1 | 677 | 130.2 | 247.3 | 279.1 | 189.9 | 340.1 | 322 | 219.3 | 292.1
1205 | 1053 | 472.6 | 189.04 | 220.9769 | 356.8 | 320.1 | 325.5 | 314.3 | 529.6 | 55.5 | 19.2 | 93.3 | 4.1 | 209.4 | 4.2 | 837.3 | 790.1 | 744.7 | 788.5 | 667.9 | 715.5 | 571 | 743.7 | 710.9 | 675.9 | 130.3 | 247.5 | 279.2 | 190 | 339.9 | 322.1 | 219.5 | 292.1
1206 | 1054 | 472.3 | 188.92 | 220.8366 | 357.5 | 320.2 | 324.8 | 314.1 | 531.8 | 55.7 | 19.2 | 93.2 | 3.6 | 191.5 | 3.8 | 837.6 | 786.8 | 731.7 | 786.9 | 664.8 | 715.9 | 568.1 | 734.4 | 708.3 | 673.5 | 130.5 | 247.7 | 279.5 | 190.2 | 339.9 | 322.1 | 219.7 | 292.2
1207 | 1055 | 472.6 | 189.04 | 220.9769 | 358.4 | 320 | 324.7 | 314.1 | 529.4 | 55.8 | 19.2 | 93.2 | 3.9 | 163.9 | 3.8 | 836.2 | 790.7 | 728.5 | 787.4 | 663.3 | 716 | 564 | 723.1 | 706 | 671.3 | 130.7 | 247.8 | 279.6 | 190.4 | 340 | 322.2 | 219.9 | 292.3
1208 | 1056 | 472 | 188.8 | 220.6963 | 360.8 | 319.8 | 325.3 | 315 | 515.4 | 55.9 | 19.2 | 93.2 | 4.2 | 166.3 | 3.2 | 836 | 797.9 | 734.3 | 788.6 | 665.2 | 716.1 | 563.6 | 718.9 | 705.1 | 671.4 | 130.9 | 248 | 279.5 | 190.6 | 339.9 | 322.2 | 220.1 | 292.3
1209 | 1057 | 472.2 | 188.88 | 220.7898 | 361.9 | 319.4 | 325.6 | 315.9 | 507.7 | 55.9 | 19.2 | 93.2 | 4.3 | 180.8 | 3 | 838 | 804 | 755.9 | 790.3 | 668.7 | 716 | 567.9 | 730.9 | 706.9 | 673.2 | 131.1 | 248.2 | 279.4 | 190.7 | 339.8 | 322.8 | 220.3 | 292.4
1210 | 1058 | 472.6 | 189.04 | 220.9769 | 360.5 | 319.4 | 326.2 | 316.3 | 515.4 | 56 | 19.2 | 93.3 | 4.4 | 200.2 | 4.4 | 839.1 | 794.6 | 738 | 788.5 | 665.8 | 716.2 | 568.4 | 748.1 | 708.5 | 674.3 | 131.3 | 248.3 | 279.7 | 190.9 | 339.8 | 323.2 | 220.5 | 292.6
1211 | 1059 | 472.2 | 188.88 | 220.7898 | 359.3 | 320.1 | 326.7 | 316.4 | 527.2 | 56 | 19.2 | 93.4 | 4.7 | 209.3 | 6.1 | 836.8 | 775.5 | 723.2 | 784.9 | 661.6 | 716.4 | 562.7 | 743.8 | 706.1 | 671.7 | 131.5 | 248.5 | 280.3 | 191.1 | 339.8 | 323.4 | 220.7 | 292.6
1212 | 1060 | 472.8 | 189.12 | 221.0704 | 359.6 | 320.6 | 327.2 | 315.9 | 526 | 56.2 | 19.2 | 93.4 | 4.6 | 207 | 7.2 | 830.8 | 755 | 703.5 | 779.7 | 657.7 | 716.5 | 556.4 | 711.9 | 702.1 | 667.6 | 131.7 | 248.7 | 280.8 | 191.3 | 339.9 | 323.5 | 220.9 | 292.7
1213 | 1061 | 472.8 | 189.12 | 221.0704 | 362.4 | 320.6 | 328.1 | 315.8 | 515.2 | 56.3 | 19.2 | 93.5 | 4 | 207.2 | 7.7 | 826.7 | 746 | 692.8 | 778.1 | 654.9 | 716.3 | 551 | 693.2 | 697.3 | 664.7 | 131.8 | 248.9 | 280.9 | 191.4 | 340.1 | 323.4 | 221.1 | 292.7
1214 | 1062 | 472.5 | 189 | 220.9301 | 365.1 | 320.3 | 328.5 | 316.7 | 507.3 | 56.3 | 19.2 | 93.5 | 4.5 | 211.3 | 7.7 | 825.4 | 746.7 | 692.2 | 777.9 | 653.7 | 716.1 | 547.2 | 692.3 | 694.2 | 662.6 | 132 | 249.1 | 280.9 | 191.6 | 340.3 | 323.2 | 221.3 | 292.8
1215 | 1063 | 472.6 | 189.04 | 220.9769 | 365.2 | 319.6 | 328.6 | 318 | 511.5 | 56.4 | 19.2 | 93.5 | 3.8 | 217.9 | 7.6 | 828.5 | 763.7 | 716.5 | 778.6 | 657.1 | 716 | 549.2 | 718.4 | 695.7 | 665.7 | 132.2 | 249.3 | 281 | 191.8 | 340.4 | 323.5 | 221.5 | 292.8
1216 | 1064 | 472.3 | 188.92 | 220.8366 | 362.9 | 318.7 | 328.8 | 319 | 518.9 | 56.4 | 19.2 | 93.6 | 4.3 | 229.9 | 7.1 | 832 | 775.8 | 738 | 780.1 | 659.3 | 715.9 | 550 | 731.6 | 697.1 | 667.1 | 132.4 | 249.5 | 281.1 | 192 | 340.4 | 323.7 | 221.7 | 292.8
1217 | 1065 | 472.7 | 189.08 | 221.0236 | 362 | 318 | 328.9 | 319.6 | 525.8 | 56.4 | 19.2 | 93.6 | 4.2 | 213.4 | 6.8 | 835.5 | 788.5 | 750.7 | 782.6 | 662.8 | 715.7 | 552.9 | 744.7 | 698.8 | 668.8 | 132.6 | 249.6 | 281.3 | 192.1 | 340.5 | 324.1 | 222 | 292.9
1218 | 1066 | 472.4 | 188.96 | 220.8834 | 361.2 | 317.4 | 328.8 | 319.8 | 530.6 | 56.4 | 19.2 | 93.6 | 4.2 | 214.3 | 6.4 | 839.2 | 798.2 | 746.7 | 785 | 663.7 | 715.7 | 556.1 | 752.6 | 700.4 | 670 | 132.7 | 249.8 | 281.4 | 192.3 | 340.6 | 324.6 | 222.1 | 293.1
1219 | 1067 | 473.4 | 189.36 | 221.3509 | 359.6 | 316.8 | 328.5 | 320.1 | 535.7 | 56.4 | 19.2 | 93.6 | 4 | 225.7 | 6.1 | 842.5 | 805.4 | 767.7 | 787.1 | 666.8 | 715.6 | 560.3 | 767.6 | 703.1 | 673.2 | 132.9 | 250 | 281.5 | 192.5 | 340.6 | 324.8 | 222.3 | 293.2
1220 | 1068 | 472.5 | 189 | 220.9301 | 358.4 | 316.7 | 328.1 | 320.2 | 542.6 | 56.3 | 19.1 | 93.5 | 4.3 | 222.2 | 6.1 | 845.9 | 806.2 | 775.2 | 788.2 | 669.3 | 715.7 | 560.6 | 784.7 | 704.4 | 675.9 | 133.1 | 250.2 | 281.8 | 192.7 | 340.7 | 324.6 | 222.5 | 293.2
1221 | 1069 | 471.9 | 188.76 | 220.6496 | 358 | 316.5 | 327.4 | 319.9 | 549 | 56.2 | 19.1 | 93.5 | 4.1 | 196.4 | 6.7 | 848.4 | 810.4 | 774.6 | 789.8 | 669.3 | 715.8 | 562.8 | 790.7 | 705.2 | 677 | 133.3 | 250.3 | 282 | 192.9 | 340.8 | 324.5 | 222.7 | 293.2
1222 | 1070 | 474.4 | 189.76 | 221.8185 | 358.4 | 316.4 | 327 | 319.8 | 555 | 56.2 | 19.1 | 93.5 | 3.9 | 201.2 | 7.3 | 847.2 | 802 | 765.9 | 788.5 | 667.5 | 715.9 | 561.7 | 780.4 | 704 | 675.9 | 133.5 | 250.5 | 282.3 | 193 | 340.7 | 324.2 | 222.9 | 293.3
1223 | 1071 | 472.8 | 189.12 | 221.0704 | 358.9 | 316.3 | 326.8 | 319.7 | 545.8 | 56.1 | 19.1 | 93.6 | 4 | 210.5 | 7.1 | 844.8 | 796.6 | 754.7 | 788.2 | 666.3 | 716 | 559.9 | 761.1 | 702.3 | 673.4 | 133.6 | 250.7 | 282.4 | 193.2 | 340.6 | 324 | 223.1 | 293.3
1224 | 1072 | 472.1 | 188.84 | 220.7431 | 360.4 | 316.2 | 326.6 | 319.5 | 537.7 | 56.1 | 19.1 | 93.7 | 3.7 | 202.9 | 6.5 | 845 | 805.8 | 757 | 790.2 | 667.3 | 716 | 561.3 | 764.9 | 703.5 | 674.3 | 133.8 | 250.9 | 282.4 | 193.4 | 340.4 | 323.5 | 223.3 | 293.3
1225 | 1073 | 473.6 | 189.44 | 221.4444 | 360.1 | 315.7 | 326.6 | 319.1 | 538.8 | 56.1 | 19.1 | 93.7 | 3.5 | 217.5 | 6.5 | 846.7 | 816.2 | 755.1 | 791.6 | 667.6 | 716.1 | 562.8 | 772.8 | 706.3 | 676 | 134 | 251.1 | 282.5 | 193.6 | 340.2 | 323 | 223.5 | 293.4
1226 | 1074 | 474.4 | 189.76 | 221.8185 | 359 | 315.3 | 325.8 | 318.4 | 546.2 | 56.2 | 19.1 | 93.8 | 4.2 | 220 | 6.7 | 849.2 | 823.4 | 768.6 | 792.6 | 670.5 | 716.6 | 566.8 | 783.9 | 709.6 | 680.1 | 134.2 | 251.2 | 282.7 | 193.8 | 340.1 | 322.5 | 223.7 | 293.4
1227 | 1075 | 474 | 189.6 | 221.6315 | 357.9 | 314.9 | 324.9 | 317.5 | 550.8 | 56.3 | 19.1 | 93.9 | 4.6 | 206.7 | 7.5 | 848.8 | 809.5 | 754.7 | 790.2 | 667.4 | 716.9 | 567.6 | 777.3 | 710 | 679.4 | 134.4 | 251.4 | 283 | 193.9 | 340.2 | 322.3 | 223.9 | 293.4
1228 | 1076 | 472.7 | 189.08 | 221.0236 | 357.9 | 315.6 | 324.4 | 316.8 | 540.3 | 56.3 | 19.1 | 93.9 | 4.2 | 216.2 | 7.8 | 846.2 | 794.9 | 743.4 | 788.5 | 664.7 | 717 | 561.2 | 755.1 | 706.6 | 675.5 | 134.5 | 251.6 | 283.3 | 194.1 | 340.5 | 322.3 | 224.1 | 293.4
1229 | 1077 | 472 | 188.8 | 220.6963 | 357.7 | 316.6 | 325.2 | 316.4 | 526.4 | 56.4 | 19.1 | 93.9 | 4.2 | 206.7 | 7.8 | 844.2 | 783.6 | 742 | 786.3 | 663.2 | 717.1 | 557.4 | 756.8 | 704.6 | 675 | 134.7 | 251.8 | 283.4 | 194.3 | 340.7 | 322.3 | 224.3 | 293.5
1230 | 1078 | 472.1 | 188.84 | 220.7431 | 357.9 | 317.4 | 325.4 | 316.4 | 525.1 | 56.4 | 19.1 | 94 | 4.2 | 213 | 8.2 | 841.2 | 771.3 | 744.6 | 784.8 | 663.4 | 717.1 | 553.9 | 748.3 | 701.7 | 672.8 | 134.9 | 252 | 283.7 | 194.4 | 340.8 | 322.5 | 224.5 | 293.6
1231 | 1079 | 471.6 | 188.64 | 220.5093 | 358.6 | 318.3 | 325.9 | 317 | 538.3 | 56.5 | 19.1 | 94 | 4.4 | 211 | 8.1 | 843 | 782.1 | 747.5 | 785.1 | 665 | 717.2 | 555.6 | 765.9 | 701.5 | 674.7 | 135.1 | 252.1 | 283.9 | 194.6 | 341 | 322.5 | 224.7 | 293.6
1232 | 1080 | 471.6 | 188.64 | 220.5093 | 358.8 | 319.3 | 326.8 | 317.6 | 550.6 | 56.5 | 19.1 | 94 | 4.1 | 210.5 | 8 | 845 | 787.8 | 742.7 | 785.6 | 662.8 | 717.3 | 554.7 | 765.8 | 701 | 673.8 | 135.3 | 252.3 | 284.1 | 194.8 | 341.1 | 322.4 | 224.9 | 293.7
1233 | 1081 | 472 | 188.8 | 220.6963 | 358.7 | 320.6 | 327 | 317.9 | 542.6 | 56.5 | 19.1 | 94.1 | 4.5 | 207.6 | 7.5 | 843.4 | 785 | 737.5 | 783.6 | 660.3 | 717.4 | 554.5 | 759.7 | 700.5 | 672.8 | 135.5 | 252.5 | 284.2 | 195 | 341.3 | 322.5 | 225.1 | 293.7
1234 | 1082 | 471.3 | 188.52 | 220.369 | 358.8 | 320.7 | 326.9 | 318.2 | 535.6 | 56.5 | 19.1 | 94 | 4.2 | 206.6 | 7.2 | 838.6 | 768.2 | 730.9 | 780.5 | 658.7 | 717.1 | 549.3 | 740 | 698.1 | 669.3 | 135.7 | 252.7 | 284.5 | 195.2 | 341.5 | 322.6 | 225.3 | 293.7
1235 | 1083 | 472 | 188.8 | 220.6963 | 359.4 | 320.1 | 327.1 | 318 | 523.7 | 56.5 | 19.1 | 94 | 4.2 | 209.1 | 7.6 | 836 | 765 | 733.4 | 780.2 | 659.4 | 716.8 | 547 | 726.8 | 695.8 | 667.2 | 135.9 | 252.9 | 284.6 | 195.3 | 341.5 | 322.7 | 225.5 | 293.8
1236 | 1084 | 472.2 | 188.88 | 220.7898 | 360.8 | 319.7 | 327 | 317.9 | 523.9 | 56.5 | 19.1 | 94 | 4.6 | 205.6 | 8.1 | 838.5 | 780.1 | 747.8 | 783.8 | 662.6 | 716.6 | 550.5 | 747.1 | 697.5 | 670 | 136.1 | 253 | 284.5 | 195.5 | 341.3 | 322.6 | 225.7 | 293.9
1237 | 1085 | 471 | 188.4 | 220.2287 | 363.3 | 319.4 | 327.1 | 317.9 | 522.2 | 56.4 | 19.1 | 94.1 | 4.2 | 200.3 | 8.7 | 841.3 | 792.8 | 766.5 | 787.4 | 665.5 | 716.5 | 558.1 | 756.1 | 701.4 | 673.9 | 136.2 | 253.2 | 284.5 | 195.7 | 341.3 | 322.4 | 225.8 | 293.9
1238 | 1086 | 472 | 188.8 | 220.6963 | 362.9 | 319.5 | 327.6 | 317.6 | 527.9 | 56.3 | 19.1 | 94.2 | 3.7 | 201.5 | 7.9 | 842.9 | 788.9 | 770.1 | 788.4 | 664.1 | 716.4 | 559.3 | 775.8 | 702.3 | 674.6 | 136.4 | 253.4 | 284.7 | 195.8 | 341.3 | 322.6 | 226 | 293.9
1239 | 1087 | 471.8 | 188.72 | 220.6028 | 362.5 | 318.9 | 327.8 | 317 | 548.4 | 56.3 | 19.1 | 94.2 | 4.4 | 207 | 7.1 | 843.8 | 778.7 | 769.8 | 786 | 663.2 | 716.5 | 558 | 786.7 | 701.1 | 674.4 | 136.6 | 253.5 | 285.1 | 196 | 341.3 | 322.8 | 226.2 | 293.9
1240 | 1088 | 472.3 | 188.92 | 220.8366 | 361.5 | 318.3 | 328 | 316.4 | 557.9 | 56.2 | 19.1 | 94.3 | 4.3 | 193.3 | 6.5 | 845.7 | 782.6 | 765.7 | 784.7 | 663.4 | 716.9 | 559.5 | 791.1 | 701.5 | 676.3 | 136.8 | 253.7 | 285.4 | 196.2 | 341.5 | 323 | 226.4 | 294
1241 | 1089 | 472 | 188.8 | 220.6963 | 361.4 | 317.9 | 328.4 | 316.2 | 561.1 | 56.2 | 19.1 | 94.3 | 4.3 | 205.3 | 6.2 | 844.4 | 773.3 | 737.3 | 781.2 | 658.2 | 717.1 | 557.3 | 784 | 700.9 | 675 | 137 | 253.9 | 285.7 | 196.4 | 341.9 | 323 | 226.6 | 294.1
1242 | 1090 | 472.3 | 188.92 | 220.8366 | 361.7 | 318.1 | 328.2 | 316.1 | 565.8 | 56.1 | 19.1 | 94.4 | 4.4 | 207.9 | 6.3 | 843 | 766.1 | 728.8 | 780 | 655.8 | 717.3 | 555 | 789.1 | 700.1 | 673.8 | 137.2 | 254.1 | 286 | 196.5 | 342.4 | 322.8 | 226.8 | 294.1
1243 | 1091 | 471.7 | 188.68 | 220.556 | 363.2 | 318.3 | 328.3 | 317 | 569.6 | 56.1 | 19.1 | 94.4 | 4.5 | 193.4 | 6.5 | 845.2 | 778.7 | 745.5 | 780.8 | 659.7 | 717.8 | 555.7 | 801.9 | 702 | 677.3 | 137.4 | 254.3 | 286 | 196.7 | 342.8 | 323.1 | 227 | 294.2
1244 | 1092 | 471.2 | 188.48 | 220.3223 | 363.6 | 318.5 | 328.8 | 318.2 | 577.2 | 56.1 | 19.1 | 94.3 | 4.7 | 193.2 | 6.4 | 847 | 793.2 | 753 | 783.4 | 661.7 | 718.5 | 564.9 | 807.9 | 706.4 | 682.2 | 137.6 | 254.5 | 286.2 | 196.9 | 343.4 | 323.5 | 227.2 | 294.3
1245 | 1093 | 471.9 | 188.76 | 220.6496 | 362.4 | 319.1 | 329 | 319.1 | 590 | 56.2 | 19.1 | 94.4 | 4.3 | 191.6 | 6.2 | 847.9 | 804 | 756 | 784.6 | 662.1 | 719.4 | 573.3 | 818.5 | 710.7 | 686.4 | 137.8 | 254.6 | 286.3 | 197.1 | 343.6 | 323.4 | 227.4 | 294.4
1246 | 1094 | 471.8 | 188.72 | 220.6028 | 361.9 | 319.2 | 329.2 | 319.9 | 598.5 | 56.2 | 19.1 | 94.4 | 4.3 | 203.7 | 6.9 | 849.5 | 809 | 756.3 | 785.7 | 662.6 | 720.2 | 575.2 | 825.2 | 712 | 687.7 | 138 | 254.8 | 286.5 | 197.2 | 344.1 | 323.1 | 227.6 | 294.5
1247 | 1095 | 472.5 | 189 | 220.9301 | 361.8 | 319.5 | 329.4 | 320 | 599.9 | 56.2 | 19.1 | 94.4 | 4.2 | 212.4 | 7.7 | 848.1 | 793.4 | 742.6 | 783.3 | 660.3 | 720.8 | 573.1 | 815.5 | 711.5 | 686.2 | 138.2 | 255 | 287 | 197.4 | 344.5 | 323.5 | 227.8 | 294.5
1248 | 1096 | 473.5 | 189.4 | 221.3977 | 361.8 | 319.8 | 329.3 | 319.6 | 595.3 | 56.3 | 19.1 | 94.4 | 4.2 | 207.1 | 8 | 846.5 | 783.7 | 735.2 | 780.8 | 657.9 | 721.3 | 566.9 | 807.4 | 709 | 683.9 | 138.3 | 255.2 | 287.4 | 197.6 | 344.9 | 324 | 228 | 294.6
1249 | 1097 | 473.7 | 189.48 | 221.4912 | 362.8 | 319.7 | 329.7 | 319.9 | 602.4 | 56.3 | 19.1 | 94.3 | 4.3 | 209.4 | 8.6 | 846.5 | 782.3 | 747.2 | 780.5 | 659 | 722.1 | 564.7 | 817.9 | 708.3 | 684.2 | 138.5 | 255.4 | 287.6 | 197.8 | 345.3 | 324.4 | 228.2 | 294.8
1250 | 1098 | 473.6 | 189.44 | 221.4444 | 362.8 | 319.7 | 330.6 | 319.9 | 600.6 | 56.3 | 19.1 | 94.2 | 4.6 | 197.9 | 8.5 | 846.9 | 777.8 | 749.2 | 779.8 | 659.9 | 722.9 | 562.7 | 812.6 | 707.8 | 685.9 | 138.7 | 255.6 | 288.1 | 198 | 345.7 | 324.9 | 228.4 | 294.9
1251 | 1099 | 472.8 | 189.12 | 221.0704 | 363.1 | 319.5 | 331.3 | 320.4 | 595.4 | 56.4 | 19.1 | 94.2 | 4.2 | 194.9 | 8 | 840.8 | 755.1 | 722.2 | 774.9 | 654.7 | 723.4 | 556.7 | 787.6 | 704.5 | 681.3 | 138.9 | 255.8 | 288.5 | 198.1 | 346.2 | 325 | 228.6 | 294.9
1252 | 1100 | 473.1 | 189.24 | 221.2107 | 363.1 | 320.6 | 331.9 | 322 | 583.6 | 56.4 | 19.1 | 94.2 | 4.1 | 208.3 | 7.4 | 836.6 | 741.8 | 713.4 | 771.4 | 651.9 | 723.7 | 551.3 | 764.9 | 700.9 | 678.8 | 139.1 | 256 | 288.8 | 198.3 | 346.7 | 325.4 | 228.8 | 294.9
1253 | 1101 | 472.9 | 189.16 | 221.1171 | 363.2 | 321.7 | 332.1 | 323.9 | 575.9 | 56.4 | 19.1 | 94.1 | 4.4 | 196 | 6.9 | 837.6 | 748.7 | 736.4 | 771.1 | 654.5 | 724 | 549.6 | 772.3 | 699 | 679.3 | 139.3 | 256.2 | 289.1 | 198.5 | 347.3 | 325.6 | 229 | 295
1254 | 1102 | 473.4 | 189.36 | 221.3509 | 364.3 | 321.8 | 331.9 | 324.9 | 584.8 | 56.4 | 19.1 | 94.1 | 4.1 | 202.9 | 6.9 | 841.1 | 769.3 | 765.2 | 775.3 | 662.1 | 724.4 | 552.8 | 796.2 | 700.9 | 684 | 139.5 | 256.5 | 288.9 | 198.7 | 347.8 | 326.1 | 229.2 | 295.2
1255 | 1103 | 473.5 | 189.4 | 221.3977 | 365.4 | 323.9 | 331.1 | 325.6 | 575.7 | 56.3 | 19.1 | 94.2 | 4.1 | 214 | 7 | 842.4 | 789.1 | 772.9 | 780.3 | 664 | 724.5 | 559.8 | 796.8 | 703.4 | 686.2 | 139.7 | 256.7 | 288.8 | 198.8 | 348.2 | 326.4 | 229.4 | 295.4
1256 | 1104 | 472.7 | 189.08 | 221.0236 | 364.8 | 325.6 | 330.6 | 326 | 581.7 | 56.3 | 19.1 | 94.2 | 4.2 | 210.3 | 7 | 846 | 803.8 | 783.4 | 784.1 | 664.8 | 724.8 | 564.8 | 810.1 | 706.3 | 689.4 | 139.9 | 256.9 | 289.1 | 199 | 348.4 | 326.5 | 229.6 | 295.5
1257 | 1105 | 473.2 | 189.28 | 221.2574 | 363.8 | 327.7 | 330.7 | 325.8 | 603.3 | 56.2 | 19.1 | 94.2 | 4.2 | 216.8 | 6.9 | 849 | 801.3 | 790.8 | 784.1 | 666.2 | 725.2 | 563.4 | 810.8 | 707.5 | 689.8 | 140.1 | 257 | 289.5 | 199.2 | 348.7 | 326.8 | 229.8 | 295.6
1258 | 1106 | 473.3 | 189.32 | 221.3042 | 362.8 | 330 | 330.5 | 325.8 | 607.4 | 56.1 | 19.1 | 94.1 | 4.4 | 195.8 | 6.9 | 850.7 | 798.4 | 799.4 | 785.6 | 666.1 | 725.6 | 561.6 | 815.8 | 707.4 | 690.2 | 140.3 | 257.3 | 289.8 | 199.4 | 349 | 326.8 | 230 | 295.7
1259 | 1107 | 473.1 | 189.24 | 221.2107 | 362.5 | 331.8 | 330.6 | 326.4 | 617.8 | 56.1 | 19.1 | 94.1 | 4.5 | 200.1 | 6.8 | 851 | 784.7 | 793.7 | 783.3 | 666.4 | 726 | 560.2 | 817.3 | 707.1 | 689.8 | 140.5 | 257.5 | 290.1 | 199.6 | 349.4 | 327 | 230.2 | 295.7
1260 | 1108 | 473.2 | 189.28 | 221.2574 | 362.3 | 332.8 | 331.3 | 327.1 | 625.5 | 56.1 | 19.1 | 94.1 | 4.6 | 205.6 | 7 | 851.6 | 790.3 | 789.3 | 782.4 | 665.5 | 726.6 | 560.9 | 822.6 | 706.7 | 690.6 | 140.7 | 257.7 | 290.4 | 199.7 | 349.8 | 326.7 | 230.4 | 295.8
1261 | 1109 | 472.8 | 189.12 | 221.0704 | 362.8 | 333.7 | 331.7 | 328.3 | 624.9 | 56 | 19.1 | 94 | 4.5 | 199.2 | 7.1 | 848.3 | 771.8 | 757.6 | 779.2 | 660.8 | 727 | 560.5 | 797 | 705.3 | 688.8 | 140.8 | 257.9 | 290.8 | 199.9 | 350.5 | 326.7 | 230.7 | 296
1262 | 1110 | 472.9 | 189.16 | 221.1171 | 364.6 | 334 | 331.8 | 329.7 | 601.5 | 56 | 19.1 | 94 | 4.4 | 205.5 | 7.4 | 841.4 | 753.4 | 736 | 775.2 | 657.2 | 727.1 | 554.1 | 767.4 | 701.5 | 683.6 | 141 | 258.1 | 291.1 | 200.1 | 351.1 | 326.7 | 230.9 | 296
1263 | 1111 | 472.6 | 189.04 | 220.9769 | 366.7 | 333.9 | 332.2 | 330.8 | 577 | 55.8 | 19.1 | 94 | 4.5 | 217.3 | 7 | 835.8 | 739.7 | 710.7 | 771.5 | 653 | 726.7 | 549 | 743.9 | 698 | 680.7 | 141.2 | 258.3 | 291.2 | 200.3 | 351.3 | 326.7 | 231 | 296.1
1264 | 1112 | 479.5 | 191.8 | 224.2031 | 367.7 | 334.3 | 332.7 | 331.3 | 556.8 | 55.7 | 19.1 | 94 | 4.2 | 203.3 | 6.8 | 830.8 | 725.3 | 717.4 | 768.5 | 652.3 | 726 | 542 | 720.8 | 693.9 | 676.9 | 141.4 | 258.5 | 291.7 | 200.5 | 351.7 | 326.8 | 231.3 | 296.1
1265 | 1113 | 483.7 | 193.48 | 226.167 | 368 | 334.3 | 333.9 | 331.7 | 548.2 | 55.7 | 19.1 | 93.9 | 4.4 | 207.8 | 6.5 | 828.1 | 723.3 | 719.8 | 766.9 | 650.8 | 725.3 | 538.3 | 716 | 690.8 | 674.3 | 141.6 | 258.8 | 292.6 | 200.6 | 352.2 | 326.9 | 231.5 | 296.2
1266 | 1114 | 485.1 | 194.04 | 226.8216 | 368.2 | 334.7 | 335.2 | 331.8 | 539.5 | 55.7 | 19.1 | 93.9 | 4.4 | 213.6 | 6.3 | 824.4 | 712.9 | 710.8 | 764.4 | 649 | 724.6 | 537.1 | 716.1 | 688.8 | 672.8 | 141.8 | 259.1 | 292.5 | 200.8 | 352.6 | 327.1 | 231.6 | 296.3
1267 | 1115 | 483.4 | 193.36 | 226.0267 | 368.5 | 335.5 | 335.8 | 331.6 | 544.5 | 55.7 | 19.1 | 94 | 4.3 | 201.2 | 6.3 | 823.9 | 710.4 | 703.7 | 762.6 | 647.6 | 723.9 | 535.6 | 718.9 | 686.3 | 671.2 | 142 | 259.3 | 292.8 | 201 | 353.2 | 327 | 231.9 | 296.4
1268 | 1116 | 481.3 | 192.52 | 225.0448 | 367.9 | 338.2 | 336.6 | 331.7 | 548.5 | 55.7 | 19.1 | 94 | 4 | 207.3 | 6.1 | 824.1 | 712.8 | 692.9 | 762.2 | 646 | 723.1 | 534.7 | 725.8 | 684.3 | 670.2 | 142.1 | 259.5 | 292.9 | 201.2 | 353.3 | 327.1 | 232.1 | 296.6
1269 | 1117 | 479.9 | 191.96 | 224.3902 | 367.2 | 339.5 | 337.8 | 332 | 546.6 | 55.8 | 19.1 | 94.1 | 4.1 | 206.8 | 5.6 | 824.7 | 715.2 | 721.8 | 761.6 | 647 | 722.2 | 533.9 | 738.5 | 682.8 | 669.1 | 142.3 | 259.8 | 292.9 | 201.3 | 353.4 | 327 | 232.3 | 296.6
1270 | 1118 | 478.5 | 191.4 | 223.7356 | 367.1 | 340.7 | 338.3 | 331.9 | 554.3 | 56 | 19.1 | 94.2 | 4.1 | 215.2 | 5.5 | 827 | 722.9 | 739 | 760.8 | 650.3 | 721.6 | 535.2 | 769 | 683.9 | 671.3 | 142.5 | 260 | 293.2 | 201.5 | 353.5 | 326.9 | 232.5 | 296.7
1271 | 1119 | 474.8 | 189.92 | 222.0055 | 366.4 | 342.3 | 338.4 | 331.9 | 573.7 | 56.1 | 19.1 | 94.2 | 4.3 | 200.6 | 5.5 | 829.3 | 725.1 | 755.1 | 760.5 | 656 | 721.2 | 535.1 | 782.4 | 684.6 | 673.4 | 142.7 | 260.2 | 293.6 | 201.7 | 353.8 | 327.1 | 232.7 | 296.8
1272 | 1120 | 474.5 | 189.8 | 221.8653 | 365.6 | 344.7 | 338.4 | 332.5 | 581.5 | 56.2 | 19.1 | 94.3 | 4.7 | 209.2 | 5.2 | 830 | 720 | 768.2 | 759.9 | 659.3 | 720.7 | 534.4 | 787 | 684.6 | 675.2 | 142.9 | 260.4 | 293.9 | 201.9 | 354.3 | 327.4 | 232.9 | 296.9
1273 | 1121 | 473.7 | 189.48 | 221.4912 | 364.2 | 346.5 | 338 | 333.6 | 587 | 56.3 | 19.1 | 94.3 | 4.2 | 224.6 | 4.4 | 832.5 | 734.4 | 774.7 | 761.5 | 660.2 | 720.3 | 534.2 | 799 | 684.6 | 676.7 | 143.1 | 260.7 | 294.2 | 202.1 | 354.7 | 327.8 | 233.1 | 297
1274 | 1122 | 472.8 | 189.12 | 221.0704 | 362.9 | 347.4 | 337 | 334.5 | 608.4 | 56.2 | 19.1 | 94.3 | 4 | 208.4 | 3.6 | 835.3 | 753.9 | 762.7 | 763.4 | 659.5 | 720.3 | 540 | 813.2 | 687.6 | 680.4 | 143.3 | 260.9 | 294.3 | 202.2 | 355.1 | 327.9 | 233.3 | 297.1
1275 | 1123 | 473.2 | 189.28 | 221.2574 | 362.1 | 347.7 | 336.5 | 334.9 | 626.9 | 56.1 | 19.1 | 94.3 | 4.2 | 192.6 | 3 | 836.4 | 754.9 | 758.9 | 763 | 659.2 | 720.2 | 540.8 | 818.4 | 688.3 | 681.9 | 143.5 | 261.1 | 294.8 | 202.4 | 355.5 | 327.8 | 233.5 | 297.2
1276 | 1124 | 474.4 | 189.76 | 221.8185 | 361.8 | 347.6 | 336 | 335.7 | 623.6 | 56 | 19.1 | 94.3 | 4.3 | 196.9 | 3.2 | 837.6 | 771.2 | 778.9 | 765.9 | 665.7 | 720.4 | 546.7 | 828.8 | 691.9 | 686.4 | 143.7 | 261.4 | 294.9 | 202.6 | 356 | 327.9 | 233.7 | 297.3
1277 | 1125 | 474.4 | 189.76 | 221.8185 | 361.4 | 347.9 | 335.7 | 336.6 | 618 | 56 | 19.1 | 94.3 | 4.7 | 216 | 4.1 | 840 | 784.5 | 799.7 | 769.5 | 671.3 | 720.4 | 550 | 834.1 | 695.3 | 689.2 | 143.9 | 261.6 | 294.9 | 202.8 | 356.4 | 328.7 | 233.9 | 297.5
1278 | 1126 | 474.1 | 189.64 | 221.6782 | 360.7 | 348.1 | 335.6 | 337 | 619.6 | 56 | 19.1 | 94.4 | 5.2 | 194.6 | 5.3 | 843.8 | 794 | 809.6 | 772.6 | 675.7 | 720.6 | 552.5 | 840.2 | 697.7 | 692.1 | 144.1 | 261.8 | 295.3 | 203 | 356.7 | 329.7 | 234.1 | 297.7
1279 | 1127 | 473.5 | 189.4 | 221.3977 | 359.9 | 349.5 | 335.2 | 337.5 | 628.3 | 56.1 | 19.1 | 94.4 | 4.7 | 169.6 | 5.2 | 846.6 | 791.5 | 803.4 | 773 | 677.5 | 720.8 | 553.4 | 843.9 | 698.7 | 694.3 | 144.2 | 262 | 295.6 | 203.1 | 356.9 | 330.3 | 234.3 | 297.8
1280 | 1128 | 473.7 | 189.48 | 221.4912 | 359.2 | 351.7 | 335.1 | 338 | 633.5 | 56.2 | 19.1 | 94.4 | 4.2 | 175.7 | 5.5 | 848 | 792 | 778.1 | 772 | 675.7 | 721 | 553.7 | 842.1 | 698.3 | 695 | 144.5 | 262.2 | 295.8 | 203.3 | 357.3 | 330.6 | 234.5 | 298
1281 | 1129 | 474.1 | 189.64 | 221.6782 | 359.1 | 353.1 | 335.6 | 338.2 | 642.1 | 56.2 | 19.1 | 94.5 | 4 | 169.4 | 6.4 | 849.2 | 792.2 | 771.1 | 770.9 | 676.9 | 721.6 | 556.3 | 838.5 | 698.9 | 696.7 | 144.6 | 262.4 | 296.1 | 203.5 | 357.8 | 331.2 | 234.7 | 298.1
1282 | 1130 | 474.1 | 189.64 | 221.6782 | 359.1 | 353.2 | 336.1 | 338.6 | 641.9 | 56.3 | 19.1 | 94.5 | 4 | 168.9 | 7.4 | 850.8 | 803.8 | 792.2 | 773.7 | 681.5 | 722.1 | 561.6 | 841.1 | 701.2 | 699.1 | 144.8 | 262.6 | 296.2 | 203.7 | 358.3 | 331.6 | 235 | 298.3
1283 | 1131 | 473.7 | 189.48 | 221.4912 | 358.9 | 353.1 | 336.6 | 339 | 654.4 | 56.4 | 19.1 | 94.5 | 4.4 | 183.8 | 8.1 | 851.3 | 809.6 | 788 | 776.7 | 682.4 | 722.9 | 570.7 | 843.8 | 706 | 703.1 | 145 | 262.8 | 296.2 | 203.9 | 358.7 | 332 | 235.2 | 298.5
1284 | 1132 | 473.2 | 189.28 | 221.2574 | 359.7 | 352.7 | 336.6 | 339.3 | 655.9 | 56.4 | 19.1 | 94.5 | 4.3 | 186 | 8.5 | 850.8 | 817.1 | 785.9 | 779.7 | 681.9 | 723.6 | 580.4 | 847.3 | 711.6 | 706.4 | 145.2 | 263 | 296.3 | 204 | 359 | 332.3 | 235.3 | 298.6
1285 | 1133 | 473.9 | 189.56 | 221.5847 | 360.4 | 352.2 | 336.4 | 339.5 | 654.8 | 56.5 | 19.1 | 94.6 | 4.1 | 190.5 | 8.6 | 853.1 | 824.6 | 808.8 | 782.7 | 687.1 | 724.2 | 584.5 | 847.8 | 715 | 708.7 | 145.4 | 263.2 | 296.4 | 204.2 | 359 | 332.5 | 235.5 | 298.7
1286 | 1134 | 474 | 189.6 | 221.6315 | 360.4 | 352 | 336.3 | 339.6 | 639.9 | 56.5 | 19.1 | 94.5 | 4.2 | 190.8 | 8.4 | 854.2 | 824.4 | 823.2 | 786 | 691.3 | 724.9 | 593.8 | 847.2 | 718.7 | 712.9 | 145.6 | 263.3 | 296.4 | 204.4 | 359 | 333.1 | 235.7 | 298.9
1287 | 1135 | 473.8 | 189.52 | 221.538 | 360.4 | 353.6 | 336.4 | 339.4 | 626.4 | 56.6 | 19.1 | 94.4 | 4.2 | 186.3 | 7.7 | 855.7 | 828.1 | 817.1 | 789.3 | 693.3 | 725.7 | 600.7 | 846.5 | 723 | 715.4 | 145.8 | 263.5 | 296.5 | 204.6 | 358.7 | 333.6 | 235.9 | 299.1
1288 | 1136 | 473.8 | 189.52 | 221.538 | 360.4 | 353.9 | 336.2 | 338.9 | 615 | 56.6 | 19.1 | 94.4 | 4.3 | 176.6 | 7.3 | 857.8 | 835.6 | 817.1 | 792.6 | 695.4 | 726.5 | 600 | 843.3 | 725.2 | 716.6 | 146 | 263.6 | 296.7 | 204.8 | 358.3 | 333.8 | 236.1 | 299.2
1289 | 1137 | 473.8 | 189.52 | 221.538 | 360 | 353.5 | 335.9 | 337.9 | 606.4 | 56.6 | 19 | 94.3 | 3.9 | 168.8 | 6.7 | 859.2 | 849.1 | 803.9 | 794.2 | 695.2 | 727.3 | 598.3 | 843.1 | 725.4 | 716.5 | 146.3 | 263.8 | 296.8 | 204.9 | 358.2 | 333.7 | 236.3 | 299.2
1290 | 1138 | 473.4 | 189.36 | 221.3509 | 360 | 352.9 | 336.2 | 336.9 | 625.8 | 56.7 | 19 | 94.3 | 4 | 176.9 | 6.2 | 859.3 | 838.9 | 784.1 | 793.7 | 691.6 | 728.2 | 595.3 | 841.5 | 724.6 | 715.8 | 146.5 | 264 | 297.2 | 205.1 | 358 | 333.4 | 236.5 | 299.3
1291 | 1139 | 472.3 | 188.92 | 220.8366 | 360.1 | 352.5 | 336.4 | 336.4 | 619.8 | 56.7 | 19 | 94.3 | 4.1 | 187.4 | 6.5 | 857 | 821 | 763.1 | 790.1 | 687.9 | 729 | 589.4 | 820.4 | 721.8 | 712.4 | 146.7 | 264.2 | 297.6 | 205.3 | 357.9 | 333.1 | 236.7 | 299.3
1292 | 1140 | 474.1 | 189.64 | 221.6782 | 360.3 | 351.7 | 335.8 | 336.4 | 606.5 | 56.7 | 19 | 94.3 | 4.1 | 196.3 | 6.4 | 854.6 | 803.4 | 755.8 | 786.7 | 686.5 | 729.6 | 585.6 | 811.7 | 720 | 709 | 146.9 | 264.3 | 297.5 | 205.5 | 357.8 | 332.5 | 236.9 | 299.5
1293 | 1141 | 471 | 188.4 | 220.2287 | 361.2 | 351.4 | 334.9 | 336.5 | 592.8 | 56.7 | 19 | 94.3 | 4.5 | 220.2 | 5.9 | 851.2 | 782.3 | 740.9 | 783.6 | 683.5 | 730 | 579.4 | 787.2 | 717 | 706.2 | 147.1 | 264.5 | 297.7 | 205.6 | 357.7 | 331.9 | 237.1 | 299.6
1294 | 1142 | 471.3 | 188.52 | 220.369 | 362 | 350.7 | 334.1 | 335.9 | 572.4 | 56.6 | 19 | 94.3 | 4 | 203.3 | 5.3 | 848.3 | 777.4 | 738.1 | 782.2 | 681.2 | 730.1 | 574.7 | 763.4 | 714.3 | 702.6 | 147.3 | 264.7 | 297.7 | 205.8 | 357.2 | 331.5 | 237.3 | 299.7
1295 | 1143 | 471.7 | 188.68 | 220.556 | 362.7 | 349.8 | 333.9 | 335.3 | 553.2 | 56.5 | 19 | 94.3 | 4.1 | 181.3 | 5.2 | 849.5 | 795.1 | 764.8 | 784.3 | 683.8 | 730.2 | 577.1 | 770.5 | 714.9 | 703.3 | 147.5 | 264.8 | 297.5 | 206 | 356.7 | 331.6 | 237.4 | 299.8
1296 | 1144 | 472.2 | 188.88 | 220.7898 | 362.4 | 349.4 | 333.9 | 334.5 | 552.9 | 56.5 | 19 | 94.2 | 4.6 | 199.2 | 5.7 | 852.6 | 806 | 764.4 | 788.1 | 685.9 | 730.6 | 581 | 788.4 | 718 | 706.9 | 147.7 | 265 | 297.7 | 206.2 | 356.3 | 331.5 | 237.6 | 299.9
1297 | 1145 | 473.5 | 189.4 | 221.3977 | 362.2 | 348.9 | 333.7 | 333.3 | 567.3 | 56.5 | 19 | 94.1 | 4.3 | 209.6 | 5.8 | 852.5 | 800.4 | 738.1 | 788.8 | 680.2 | 731 | 580.1 | 786.9 | 718.9 | 704.5 | 147.9 | 265.1 | 297.9 | 206.4 | 356.1 | 331.3 | 237.8 | 299.9
1298 | 1146 | 471.2 | 188.48 | 220.3223 | 361.9 | 348.8 | 333.2 | 331.7 | 571.9 | 56.5 | 19 | 94.2 | 4.1 | 208.8 | 5.1 | 853.6 | 800.9 | 762 | 788.6 | 682.2 | 731.2 | 577.5 | 792.4 | 717.9 | 704 | 148.1 | 265.3 | 298.1 | 206.5 | 355.9 | 330.9 | 238 | 300
1299 | 1147 | 472.2 | 188.88 | 220.7898 | 361 | 349.5 | 333 | 330.7 | 570.9 | 56.5 | 19 | 94.2 | 4.1 | 205.4 | 4.6 | 855.2 | 811.6 | 785.8 | 791.7 | 687.9 | 731.7 | 583 | 805.8 | 720.5 | 708.5 | 148.3 | 265.4 | 298 | 206.7 | 355.8 | 331.3 | 238.2 | 300
1300 | 1148 | 471.9 | 188.76 | 220.6496 | 359.9 | 351 | 333 | 330.6 | 579.9 | 56.5 | 19 | 94.4 | 4.4 | 192.7 | 4.5 | 856 | 820 | 786.7 | 794.5 | 688.8 | 732.6 | 591.6 | 814.1 | 725.8 | 713.1 | 148.5 | 265.6 | 298 | 206.9 | 355.6 | 331.4 | 238.4 | 300.2
1301 | 1149 | 472 | 188.8 | 220.6963 | 359.3 | 350.7 | 332 | 330.8 | 585.9 | 56.5 | 19 | 94.6 | 4.1 | 178.3 | 4.4 | 855.4 | 823 | 770 | 795.8 | 685.4 | 733.2 | 592.6 | 809.5 | 727.3 | 712 | 148.8 | 265.7 | 298.2 | 207.1 | 355.4 | 331.4 | 238.5 | 300.3
1302 | 1150 | 472.5 | 189 | 220.9301 | 359.9 | 349 | 331 | 330.7 | 581.6 | 56.6 | 19 | 94.7 | 3.8 | 177.4 | 4.6 | 855.9 | 827.5 | 768.5 | 797.7 | 684.1 | 733.6 | 592 | 811.4 | 727.9 | 711.3 | 149 | 265.8 | 298.4 | 207.3 | 355.3 | 331.2 | 238.7 | 300.4
1303 | 1151 | 472.6 | 189.04 | 220.9769 | 362.2 | 347.2 | 330.8 | 330.4 | 579.7 | 56.6 | 19 | 94.8 | 3.7 | 203.2 | 5.1 | 857.1 | 830.8 | 779 | 799.1 | 684.4 | 734.5 | 592.8 | 817.8 | 730 | 712.9 | 149.2 | 265.9 | 298.6 | 207.5 | 355.2 | 331.3 | 238.9 | 300.4
1304 | 1152 | 472.6 | 189.04 | 220.9769 | 364.3 | 346.2 | 331.5 | 329.7 | 585.6 | 56.6 | 19 | 94.8 | 4.1 | 195.8 | 5.5 | 858.6 | 827.1 | 781 | 798.4 | 684.7 | 735.5 | 589.8 | 828 | 730.3 | 713.8 | 149.4 | 266.1 | 298.8 | 207.6 | 355 | 331.3 | 239.1 | 300.6
1305 | 1153 | 472.8 | 189.12 | 221.0704 | 364.5 | 345.9 | 331.8 | 329.4 | 596.1 | 56.6 | 19 | 94.9 | 4.1 | 201.1 | 6.1 | 856.8 | 813.9 | 762.5 | 796.4 | 682 | 736.2 | 585.7 | 813.7 | 727.8 | 710.6 | 149.6 | 266.3 | 299.1 | 207.8 | 355.2 | 330.9 | 239.3 | 300.6
1306 | 1154 | 472.7 | 189.08 | 221.0236 | 364.5 | 346.2 | 332.2 | 329.7 | 596.9 | 56.6 | 19 | 94.9 | 4.1 | 197.9 | 6 | 856.6 | 814.8 | 762.5 | 795.8 | 681.1 | 736.9 | 581.3 | 806.4 | 725.3 | 709.5 | 149.9 | 266.4 | 299.4 | 208 | 355.2 | 330.7 | 239.5 | 300.7
1307 | 1155 | 472.6 | 189.04 | 220.9769 | 364.3 | 345.6 | 332.9 | 330 | 593.2 | 56.6 | 19 | 95 | 4.1 | 179.3 | 5.8 | 854.9 | 801.5 | 741.9 | 792.5 | 678.2 | 737.4 | 578.3 | 805.1 | 722.8 | 708.6 | 150.1 | 266.6 | 299.7 | 208.2 | 355.3 | 330.8 | 239.7 | 300.7
1308 | 1156 | 470.9 | 188.36 | 220.182 | 364.8 | 344.9 | 333.5 | 329.9 | 604 | 56.5 | 19 | 95 | 4.4 | 190.3 | 6.8 | 853.6 | 792.3 | 751 | 789.7 | 678.3 | 738 | 575.2 | 803.2 | 720.1 | 707.9 | 150.3 | 266.7 | 300.1 | 208.4 | 355.6 | 331 | 239.8 | 300.7
1309 | 1157 | 472.6 | 189.04 | 220.9769 | 365.5 | 344.6 | 334 | 330.2 | 596.9 | 56.6 | 19 | 95 | 4.4 | 184.8 | 7.9 | 850.9 | 779.1 | 738.6 | 786.6 | 675.7 | 738.3 | 571.5 | 786.4 | 717.1 | 705 | 150.5 | 266.9 | 300.3 | 208.5 | 356.1 | 331.2 | 240.1 | 300.8
1310 | 1158 | 471.5 | 188.6 | 220.4625 | 365.6 | 344.9 | 334.4 | 331 | 588.6 | 56.6 | 19 | 95 | 4.2 | 190.2 | 8.3 | 844.5 | 759.5 | 710.4 | 781.8 | 669.8 | 738.2 | 566.6 | 762.8 | 713.4 | 700.8 | 150.7 | 267.1 | 300.5 | 208.7 | 356.5 | 331.1 | 240.3 | 300.9
1311 | 1159 | 472.3 | 188.92 | 220.8366 | 367.3 | 344.6 | 335.1 | 331.7 | 571.2 | 56.7 | 19 | 95 | 4.5 | 192.9 | 8.2 | 838.8 | 744.6 | 689.5 | 778.8 | 665.2 | 737.8 | 561.3 | 740.5 | 709.5 | 696.7 | 150.9 | 267.3 | 300.6 | 208.9 | 357 | 331.2 | 240.5 | 300.9
1312 | 1160 | 471.6 | 188.64 | 220.5093 | 369 | 344.3 | 335.5 | 332 | 558.5 | 56.7 | 19 | 95 | 4.7 | 192.6 | 8.1 | 837.4 | 746.9 | 686.2 | 779.5 | 663.4 | 737.3 | 558 | 741 | 707.4 | 694.4 | 151.2 | 267.5 | 300.5 | 209.1 | 357.4 | 331.4 | 240.7 | 301
1313 | 1161 | 471.7 | 188.68 | 220.556 | 370.6 | 344 | 335.4 | 332.2 | 551.8 | 56.7 | 19 | 95 | 4.6 | 192.3 | 8.2 | 840.6 | 765.6 | 700.4 | 781.6 | 663.2 | 737 | 561.1 | 763.7 | 709.5 | 696.1 | 151.4 | 267.7 | 300.4 | 209.3 | 357.5 | 331.5 | 240.9 | 301.2
1314 | 1162 | 471.5 | 188.6 | 220.4625 | 370.7 | 344.9 | 335.6 | 332.3 | 557.9 | 56.5 | 19 | 95 | 4.2 | 188 | 8 | 844.7 | 780 | 730 | 784 | 668.3 | 737.2 | 568.2 | 786.7 | 713.6 | 700.8 | 151.6 | 267.8 | 300.6 | 209.4 | 357.4 | 332.2 | 241.1 | 301.3
1315 | 1163 | 471.8 | 188.72 | 220.6028 | 369.9 | 345.4 | 335.8 | 332 | 588.2 | 56.2 | 19 | 94.9 | 4.1 | 187.9 | 7.7 | 846.7 | 782 | 737.1 | 785 | 666.9 | 737.4 | 568.4 | 796.1 | 715.2 | 700.2 | 151.8 | 268 | 300.9 | 209.6 | 357.4 | 332.4 | 241.2 | 301.3
1316 | 1164 | 472.1 | 188.84 | 220.7431 | 369 | 346.1 | 336 | 331.5 | 587.9 | 56.1 | 19 | 94.9 | 3.7 | 192.3 | 7.8 | 849.4 | 797.7 | 754.6 | 787.4 | 668.6 | 737.8 | 577.3 | 806.7 | 718.8 | 704.2 | 152.1 | 268.1 | 300.9 | 209.8 | 357.4 | 332.3 | 241.4 | 301.5
1317 | 1165 | 473.7 | 189.48 | 221.4912 | 368.7 | 346.7 | 336.5 | 331 | 592.9 | 55.9 | 19 | 94.8 | 4.4 | 189.1 | 8.3 | 851 | 799.8 | 768.7 | 788.8 | 669.7 | 737.9 | 578.4 | 815.1 | 720.3 | 705.9 | 152.3 | 268.3 | 301.1 | 210 | 357.3 | 332.5 | 241.6 | 301.6
1318 | 1166 | 474.9 | 189.96 | 222.0523 | 368.7 | 347.5 | 336.4 | 330.2 | 597 | 55.9 | 19 | 94.8 | 3.8 | 188.6 | 8.7 | 850.3 | 788.5 | 770.4 | 787.7 | 669.3 | 737.8 | 574.4 | 808.5 | 718.4 | 703.9 | 152.5 | 268.4 | 301.5 | 210.1 | 357.2 | 332.5 | 241.8 | 301.7
1319 | 1167 | 480.5 | 192.2 | 224.6707 | 367.6 | 348.2 | 336.5 | 329.9 | 587 | 56 | 19 | 94.7 | 3.9 | 181.7 | 8.7 | 849.9 | 788.6 | 783.8 | 788.3 | 673 | 737.5 | 572.2 | 797.2 | 716 | 703.6 | 152.7 | 268.6 | 301.5 | 210.3 | 357.1 | 332.2 | 242 | 301.7
1320 | 1168 | 492.3 | 196.92 | 230.1881 | 366.8 | 348.9 | 336.6 | 330.2 | 577.2 | 56.1 | 19 | 94.7 | 4 | 179.8 | 8.4 | 851.4 | 797.6 | 779.1 | 791.5 | 674.5 | 737.4 | 573.9 | 809 | 716.7 | 704.9 | 153 | 268.8 | 301.5 | 210.5 | 356.8 | 332.4 | 242.1 | 301.7
1321 | 1169 | 505.3 | 202.12 | 236.2666 | 367.4 | 348.7 | 336.2 | 330.2 | 567.9 | 56.2 | 19 | 94.6 | 3.9 | 184.7 | 8.1 | 851.6 | 798.8 | 763.9 | 790.8 | 672.7 | 737.2 | 575.3 | 802.5 | 717.4 | 703.8 | 153.2 | 268.9 | 301.5 | 210.7 | 356.6 | 332.7 | 242.4 | 301.9
1322 | 1170 | 517.3 | 206.92 | 241.8776 | 368.1 | 349.3 | 335.4 | 329.5 | 555.1 | 56.3 | 19 | 94.6 | 4 | 188.6 | 7.8 | 849.5 | 786.6 | 751.8 | 789 | 672.1 | 736.7 | 574.4 | 787.5 | 716.7 | 701.8 | 153.4 | 269.1 | 301.7 | 210.9 | 356.4 | 333.1 | 242.5 | 301.9
1323 | 1171 | 524.7 | 209.88 | 245.3376 | 368 | 349.9 | 334.8 | 328.8 | 551.1 | 56.4 | 19 | 94.6 | 4.2 | 175.6 | 7.9 | 846.7 | 774.2 | 739.5 | 785.5 | 670 | 736.2 | 570.3 | 773 | 713.4 | 700.1 | 153.6 | 269.2 | 302.1 | 211 | 356.1 | 333.4 | 242.7 | 302
1324 | 1172 | 527.9 | 211.16 | 246.8339 | 367.4 | 349.1 | 335.4 | 328 | 552.9 | 56.5 | 19 | 94.5 | 3.9 | 193.5 | 8.1 | 843.5 | 765.1 | 718.9 | 781.8 | 666.5 | 735.6 | 564.7 | 758.9 | 709.4 | 695.8 | 153.9 | 269.4 | 302.5 | 211.2 | 356.1 | 333.2 | 242.8 | 302
1325 | 1173 | 531.1 | 212.44 | 248.3301 | 368 | 348.7 | 336.1 | 327.5 | 555 | 56.6 | 19 | 94.5 | 3.8 | 181 | 7.6 | 842.4 | 756 | 723.9 | 779 | 666.2 | 735 | 561.8 | 749.9 | 706.9 | 694.3 | 154.1 | 269.6 | 303.1 | 211.4 | 356.1 | 332.9 | 243 | 302.1
1326 | 1174 | 533.2 | 213.28 | 249.312 | 369.5 | 348.8 | 336.8 | 327.9 | 554.2 | 56.5 | 19 | 94.5 | 3.8 | 187 | 7.6 | 845.9 | 770.7 | 746 | 781.4 | 668.9 | 734.8 | 563.7 | 771.6 | 707.5 | 696.1 | 154.3 | 269.8 | 303.3 | 211.6 | 356.1 | 332.9 | 243.2 | 302.2
1327 | 1175 | 535.1 | 214.04 | 250.2004 | 370.4 | 349.6 | 337.7 | 328.9 | 581.6 | 56.4 | 19 | 94.6 | 4.2 | 174.6 | 7.8 | 848 | 781 | 748 | 782.9 | 667.6 | 735.2 | 567.7 | 788.7 | 710.2 | 698.4 | 154.6 | 270 | 303.2 | 211.7 | 356.3 | 333.1 | 243.4 | 302.3
1328 | 1176 | 535.1 | 214.04 | 250.2004 | 370.7 | 350.2 | 338.3 | 330.1 | 593.5 | 56.3 | 19 | 94.6 | 3.9 | 177.2 | 8 | 849 | 785 | 733.3 | 783.6 | 664.9 | 735.2 | 570.6 | 797.1 | 712.7 | 699 | 154.8 | 270.1 | 303.3 | 211.9 | 356.7 | 333.6 | 243.6 | 302.4
1329 | 1177 | 534.8 | 213.92 | 250.0602 | 370.4 | 350.8 | 338.7 | 330.8 | 594.7 | 56.3 | 19 | 94.7 | 3.7 | 182 | 7.5 | 846.8 | 779 | 710 | 782.3 | 661.6 | 735.1 | 569.4 | 793 | 713.4 | 697.9 | 155 | 270.3 | 303.4 | 212.1 | 357.1 | 334.1 | 243.8 | 302.7
1330 | 1178 | 534.8 | 213.92 | 250.0602 | 372 | 350.9 | 339 | 330.7 | 583.5 | 56.4 | 18.9 | 94.8 | 4.1 | 177 | 7.1 | 844.4 | 767.2 | 704.8 | 780.6 | 659 | 734.9 | 563.7 | 783.9 | 712.3 | 695.6 | 155.2 | 270.5 | 303.6 | 212.2 | 357.4 | 334.4 | 244 | 302.8
1331 | 1179 | 536.2 | 214.48 | 250.7148 | 373.2 | 350.3 | 339 | 330.5 | 582.6 | 56.4 | 18.9 | 94.9 | 4 | 189.5 | 6.5 | 844.2 | 763.9 | 705.7 | 779.4 | 658.5 | 735 | 564.2 | 785 | 712.8 | 697.5 | 155.5 | 270.7 | 303.9 | 212.4 | 357.9 | 334.6 | 244.2 | 302.9
1332 | 1180 | 536.9 | 214.76 | 251.0421 | 373.2 | 350.1 | 339.4 | 330.2 | 593.2 | 56.5 | 19 | 95 | 4.1 | 190.7 | 6.8 | 844.9 | 762.2 | 700.1 | 778.1 | 657.4 | 735.3 | 562.5 | 790.8 | 712.7 | 698 | 155.7 | 270.9 | 304.3 | 212.6 | 358.2 | 334.8 | 244.4 | 303
1333 | 1181 | 536.9 | 214.76 | 251.0421 | 374.1 | 350.5 | 340.1 | 330.1 | 600.7 | 56.5 | 19 | 95.1 | 4.1 | 178.4 | 6.8 | 842 | 749.4 | 690.5 | 774 | 653.6 | 735.2 | 560.6 | 780.2 | 711.1 | 694.9 | 155.9 | 271 | 304.6 | 212.8 | 358.3 | 334.8 | 244.5 | 303.1
1334 | 1182 | 537.2 | 214.88 | 251.1823 | 375.8 | 350.4 | 341.1 | 330.5 | 585.2 | 56.6 | 19 | 95.2 | 4.2 | 174.7 | 7.2 | 841.4 | 750.1 | 699.8 | 773.2 | 654.6 | 735 | 559.1 | 772.3 | 708.6 | 692.3 | 156.2 | 271.2 | 305 | 212.9 | 358.5 | 334.8 | 244.7 | 303.2
1335 | 1183 | 538.9 | 215.56 | 251.9772 | 377.7 | 349.9 | 341.7 | 331.6 | 573.2 | 56.6 | 18.9 | 95.2 | 4.2 | 174.7 | 7.6 | 841.6 | 755.6 | 710.9 | 772.7 | 654.7 | 734.7 | 558.2 | 768.8 | 706.4 | 691.9 | 156.4 | 271.4 | 305.4 | 213.1 | 358.7 | 334.8 | 244.9 | 303.3
1336 | 1184 | 538.9 | 215.56 | 251.9772 | 381.1 | 350 | 342.2 | 332.7 | 571.9 | 56.7 | 18.9 | 95.3 | 4.1 | 178.7 | 8.3 | 840.9 | 759.5 | 727.9 | 774 | 653.9 | 734.3 | 557.9 | 754.3 | 705.2 | 689.8 | 156.6 | 271.6 | 305.7 | 213.3 | 359.1 | 335 | 245.1 | 303.4
1337 | 1185 | 538.8 | 215.52 | 251.9305 | 384.2 | 350.6 | 342.8 | 333.2 | 562.9 | 56.7 | 18.9 | 95.4 | 3.9 | 179 | 9 | 842 | 778.6 | 750.7 | 776.7 | 656.9 | 733.7 | 558.6 | 761.1 | 704.9 | 691 | 156.9 | 271.8 | 305.6 | 213.5 | 359.6 | 335.4 | 245.3 | 303.6
1338 | 1186 | 538.9 | 215.56 | 251.9772 | 384.9 | 351.4 | 343.7 | 334.1 | 559.9 | 56.8 | 18.9 | 95.4 | 3.9 | 178 | 9.7 | 844.5 | 788.2 | 735.4 | 778.2 | 655.1 | 733.1 | 559.2 | 769.2 | 705.2 | 691.2 | 157.1 | 272 | 305.6 | 213.7 | 359.8 | 335.8 | 245.5 | 303.7
1339 | 1187 | 538.7 | 215.48 | 251.8837 | 386 | 351.7 | 344.1 | 334.8 | 555.9 | 56.9 | 18.9 | 95.5 | 3.8 | 188.5 | 9.6 | 845.6 | 786.5 | 717.9 | 779.1 | 653.6 | 732.7 | 558.6 | 765.4 | 705.3 | 689.9 | 157.4 | 272.2 | 305.7 | 213.8 | 360 | 336.1 | 245.7 | 303.9
1340 | 1188 | 539.6 | 215.84 | 252.3045 | 387.3 | 351 | 344.4 | 335.5 | 546.8 | 57 | 18.9 | 95.5 | 3.6 | 189.5 | 9.3 | 842 | 774.3 | 705.9 | 777 | 651.9 | 732.2 | 558.2 | 746.4 | 704.7 | 688.6 | 157.6 | 272.4 | 305.9 | 214 | 360.3 | 336.5 | 245.8 | 304.1
1341 | 1189 | 540.4 | 216.16 | 252.6786 | 387.5 | 350.7 | 344.8 | 336 | 540.4 | 57.2 | 18.9 | 95.6 | 3.6 | 197.2 | 8.9 | 836.5 | 764.9 | 688 | 775 | 649.4 | 731.4 | 556.4 | 718.9 | 702.3 | 684.7 | 157.8 | 272.6 | 305.9 | 214.2 | 360.6 | 337 | 246 | 304.2
1342 | 1190 | 541.7 | 216.68 | 253.2864 | 388.4 | 350.7 | 345.1 | 336 | 529.1 | 57.3 | 18.9 | 95.7 | 3.8 | 205.2 | 7.6 | 835.1 | 766 | 680.5 | 774.7 | 647.8 | 730.6 | 556 | 719.1 | 700.1 | 683.8 | 158.1 | 272.8 | 306.1 | 214.3 | 360.5 | 337.4 | 246.2 | 304.4
1343 | 1191 | 542 | 216.8 | 253.4267 | 388.5 | 350.7 | 345.5 | 335.3 | 535 | 57.4 | 18.9 | 95.7 | 4.2 | 201.9 | 6.2 | 834.8 | 767 | 673.1 | 774.2 | 646.8 | 730.2 | 555.6 | 721.1 | 699 | 683 | 158.3 | 272.9 | 306.4 | 214.5 | 360.4 | 337.3 | 246.4 | 304.5
1344 | 1192 | 542 | 216.8 | 253.4267 | 387.8 | 350.1 | 345.8 | 334.1 | 535.2 | 57.5 | 18.9 | 95.7 | 4.7 | 156.6 | 5.6 | 833.6 | 765.1 | 677.1 | 773.2 | 646 | 728.7 | 554 | 711.7 | 697.2 | 680.2 | 158.6 | 273.1 | 306.4 | 214.7 | 360.5 | 337.2 | 246.5 | 304.6
1345 | 1193 | 542.1 | 216.84 | 253.4735 | 386.3 | 348.8 | 346.3 | 333.8 | 532.1 | 57.6 | 18.9 | 95.8 | 4.4 | 181 | 5.2 | 834.4 | 769.4 | 683.1 | 773 | 645.1 | 727.9 | 555 | 728.8 | 697.9 | 681.2 | 158.8 | 273.3 | 306.4 | 214.9 | 360.2 | 337.3 | 246.7 | 304.8
1346 | 1194 | 541.6 | 216.64 | 253.2397 | 384.3 | 347.7 | 346.2 | 334.2 | 547.3 | 57.8 | 18.9 | 96 | 4.1 | 188.6 | 5.2 | 838.7 | 791.8 | 704.5 | 774.6 | 647.5 | 727.7 | 561.4 | 761.3 | 701.7 | 686.5 | 159 | 273.4 | 306.5 | 215 | 359.9 | 337.3 | 246.9 | 304.9
1347 | 1195 | 540.5 | 216.2 | 252.7253 | 382.7 | 347.9 | 346 | 334.4 | 577.2 | 57.9 | 18.9 | 96.1 | 3.9 | 160.1 | 5.6 | 841.2 | 803.7 | 706.3 | 776.4 | 649.6 | 727.9 | 566.5 | 774.5 | 704.9 | 689.8 | 159.3 | 273.6 | 306.8 | 215.2 | 359.7 | 337.3 | 247 | 305
1348 | 1196 | 541.4 | 216.56 | 253.1462 | 382 | 348.4 | 346.1 | 333.9 | 576.8 | 58 | 18.9 | 96.3 | 4 | 166.2 | 5.9 | 838 | 792.5 | 701 | 775.6 | 646.5 | 727.5 | 566.9 | 744 | 704.3 | 686.4 | 159.5 | 273.8 | 307 | 215.4 | 359.6 | 337.2 | 247.2 | 305.1
1349 | 1197 | 542.3 | 216.92 | 253.567 | 382.8 | 349.1 | 346.6 | 332.9 | 557.3 | 58 | 18.9 | 96.5 | 3.8 | 176.8 | 5.6 | 835.7 | 780.4 | 699 | 775.6 | 646 | 726.8 | 563.5 | 730.5 | 701.3 | 683.3 | 159.8 | 273.9 | 307.1 | 215.5 | 359.6 | 337.1 | 247.3 | 305.2
1350 | 1198 | 543 | 217.2 | 253.8943 | 383.3 | 350.1 | 346.7 | 332.5 | 553.5 | 58 | 18.9 | 96.6 | 3.8 | 187.8 | 5.8 | 837.9 | 798.7 | 697.9 | 779.8 | 646.5 | 726.5 | 569.2 | 747.1 | 703.5 | 686 | 160 | 274.1 | 307.2 | 215.7 | 359.9 | 337.2 | 247.6 | 305.4
1351 | 1199 | 543.2 | 217.28 | 253.9878 | 383.3 | 351.2 | 346.3 | 332.5 | 562.9 | 58 | 18.9 | 96.7 | 4.3 | 174.3 | 5.9 | 841.2 | 810.5 | 717.8 | 782.6 | 649.4 | 727 | 578.4 | 777.7 | 708.2 | 690.1 | 160.3 | 274.3 | 307.2 | 215.9 | 359.9 | 338.5 | 247.8 | 305.6
1352 | 1200 | 544.5 | 217.8 | 254.5957 | 382.1 | 352.1 | 345.7 | 332.5 | 570.5 | 58 | 18.9 | 96.8 | 4.6 | 190.4 | 5.8 | 840.5 | 805.1 | 715.1 | 782.3 | 649.2 | 727.3 | 578.1 | 763.7 | 709.8 | 688.9 | 160.5 | 274.4 | 307.5 | 216 | 359.9 | 339.5 | 247.9 | 305.7
1353 | 1201 | 545.2 | 218.08 | 254.923 | 381.9 | 353.2 | 345.8 | 331.8 | 559.5 | 58 | 18.9 | 96.8 | 4.5 | 204 | 5.5 | 836.8 | 793.3 | 710.3 | 779.6 | 646.8 | 726.8 | 572.9 | 740.8 | 707.4 | 685.6 | 160.8 | 274.6 | 307.8 | 216.2 | 359.9 | 339.5 | 248.1 | 305.8
1354 | 1202 | 545.9 | 218.36 | 255.2503 | 382.7 | 353 | 346.1 | 330.9 | 546.9 | 58 | 18.9 | 96.8 | 4.5 | 199 | 5.2 | 834.3 | 782.3 | 698.3 | 778.2 | 645.6 | 726.1 | 568.7 | 725.5 | 704.3 | 683.5 | 161 | 274.8 | 308 | 216.4 | 359.7 | 339.5 | 248.2 | 306
1355 | 1203 | 544.9 | 217.96 | 254.7827 | 383.8 | 351.4 | 346.6 | 330.2 | 538.7 | 58 | 18.9 | 96.8 | 4.1 | 203.8 | 4.9 | 831.7 | 770.8 | 689 | 776.2 | 644.1 | 725.3 | 562 | 712.1 | 700.3 | 680.6 | 161.3 | 274.9 | 308.4 | 216.5 | 359.8 | 339.5 | 248.4 | 306.1
1356 | 1204 | 544.2 | 217.68 | 254.4554 | 385.2 | 350.5 | 346.8 | 330.1 | 538.5 | 57.9 | 18.9 | 96.8 | 4 | 218.7 | 4.3 | 832.6 | 778.6 | 700.8 | 776.1 | 644.1 | 724.5 | 560.1 | 721.9 | 699 | 680 | 161.5 | 275.1 | 308.5 | 216.7 | 360.2 | 339.9 | 248.6 | 306.3
1357 | 1205 | 544.2 | 217.68 | 254.4554 | 386.4 | 350.4 | 347.2 | 330.8 | 546.9 | 57.9 | 18.9 | 96.9 | 3.7 | 214.2 | 3.8 | 837.4 | 803.4 | 714.5 | 779.9 | 648.1 | 724.9 | 573.7 | 754.8 | 704.3 | 687.2 | 161.8 | 275.3 | 308.4 | 216.9 | 360.5 | 340.5 | 248.7 | 306.6
1358 | 1206 | 545.9 | 218.36 | 255.2503 | 387.7 | 350.2 | 347.5 | 331.8 | 559.1 | 57.8 | 18.9 | 97 | 4 | 195.3 | 3.3 | 837.9 | 826.7 | 718.9 | 783.2 | 650.4 | 725.4 | 587.4 | 751 | 709.9 | 691 | 162 | 275.5 | 308.4 | 217.1 | 360.9 | 341.6 | 248.9 | 306.9
1359 | 1207 | 546.3 | 218.52 | 255.4373 | 388.5 | 350.7 | 348.1 | 332.2 | 552 | 57.6 | 18.9 | 97.1 | 3.3 | 181.1 | 3.5 | 839.9 | 839.3 | 741.8 | 786.5 | 654.5 | 725.5 | 597.8 | 767.4 | 714 | 693.6 | 162.3 | 275.6 | 308.4 | 217.2 | 361.2 | 342.2 | 249.1 | 307.2
1360 | 1208 | 546.6 | 218.64 | 255.5776 | 386.9 | 350.8 | 348.2 | 332.2 | 559.5 | 57.5 | 18.9 | 97.1 | 3.2 | 187.5 | 3.8 | 843.7 | 843 | 758.1 | 790.3 | 658.8 | 726.1 | 603.3 | 788.2 | 718.4 | 698 | 162.6 | 275.8 | 308.5 | 217.4 | 361.3 | 342.7 | 249.3 | 307.3
1361 | 1209 | 546.6 | 218.64 | 255.5776 | 385.5 | 350.2 | 347.7 | 331.7 | 577.6 | 57.5 | 18.9 | 97.2 | 3.6 | 186.2 | 3.6 | 847.4 | 850.6 | 770.6 | 794.2 | 660.5 | 726.8 | 603.9 | 804.4 | 720.9 | 699.8 | 162.9 | 275.9 | 308.8 | 217.6 | 361.6 | 343 | 249.4 | 307.5
1362 | 1210 | 546.5 | 218.6 | 255.5308 | 384 | 349.5 | 347.9 | 331.2 | 584.3 | 57.6 | 18.9 | 97.3 | 4.2 | 176.3 | 3.3 | 850.4 | 858.2 | 766.7 | 798.1 | 662.1 | 727.4 | 606.3 | 809.1 | 723.7 | 702.7 | 163.1 | 276.1 | 308.9 | 217.7 | 361.6 | 343.1 | 249.6 | 307.7
1363 | 1211 | 545.8 | 218.32 | 255.2035 | 382.7 | 349.8 | 348.4 | 331.2 | 578.9 | 57.7 | 18.9 | 97.4 | 3.6 | 189.5 | 3.8 | 850.6 | 859.4 | 768.9 | 800.3 | 665 | 728.1 | 612.5 | 805.7 | 726.9 | 705.8 | 163.4 | 276.2 | 308.9 | 217.9 | 361.7 | 343.5 | 249.8 | 307.9
1364 | 1212 | 545.3 | 218.12 | 254.9697 | 382.5 | 349.3 | 348.4 | 331 | 571.2 | 57.7 | 18.9 | 97.5 | 3.8 | 206.7 | 5.4 | 853.4 | 868 | 785.9 | 803.3 | 668 | 728.6 | 614.8 | 811.2 | 729.7 | 708.1 | 163.7 | 276.4 | 309 | 218.1 | 361.6 | 344 | 250 | 308
1365 | 1213 | 546.7 | 218.68 | 255.6243 | 383 | 349.5 | 348 | 330.6 | 569.9 | 57.6 | 18.9 | 97.5 | 3.8 | 194.7 | 6.7 | 854.4 | 865.1 | 800 | 805.2 | 671 | 729.4 | 623.8 | 818.8 | 733.1 | 711.6 | 163.9 | 276.5 | 309.1 | 218.2 | 361.7 | 344.6 | 250.1 | 308.3
1366 | 1214 | 546.8 | 218.72 | 255.6711 | 383.8 | 350.4 | 347.9 | 330.8 | 582.3 | 57.6 | 18.9 | 97.5 | 4 | 197.8 | 8.1 | 854.2 | 862.3 | 806.7 | 805.5 | 673.1 | 731 | 632.6 | 815.8 | 736.7 | 715.1 | 164.2 | 276.7 | 309.2 | 218.4 | 361.9 | 344.7 | 250.3 | 308.4
1367 | 1215 | 547.9 | 219.16 | 256.1854 | 383.4 | 351.1 | 347.5 | 330.8 | 598.9 | 57.7 | 18.9 | 97.6 | 4.3 | 207.2 | 8.5 | 854.9 | 874.5 | 785.3 | 806.9 | 671.5 | 732.2 | 625.4 | 820.2 | 737.6 | 713.4 | 164.5 | 276.8 | 309.6 | 218.6 | 362.5 | 344.7 | 250.5 | 308.5
1368 | 1216 | 547.9 | 219.16 | 256.1854 | 382.9 | 350.6 | 347.8 | 330.9 | 598.6 | 57.7 | 18.9 | 97.7 | 4.4 | 205.7 | 7.7 | 855.4 | 861 | 773.3 | 806.2 | 669 | 733.4 | 619.5 | 823 | 736.2 | 712.7 | 164.7 | 276.9 | 310.1 | 218.8 | 363.3 | 345.2 | 250.6 | 308.7
1369 | 1217 | 547.7 | 219.08 | 256.0919 | 383.6 | 350.5 | 348.5 | 331.5 | 599.1 | 57.9 | 18.9 | 97.8 | 3.9 | 186.6 | 6.9 | 852.9 | 839.7 | 742.5 | 802.3 | 665.1 | 735 | 611.9 | 811.2 | 734 | 709.4 | 165 | 277.1 | 310.7 | 218.9 | 363.9 | 345.6 | 250.9 | 308.9
1370 | 1218 | 547.7 | 219.08 | 256.0919 | 384.5 | 350.6 | 349.4 | 332.1 | 592.2 | 58 | 18.9 | 97.8 | 4.3 | 142.7 | 6.1 | 850.2 | 817.9 | 731.8 | 797.4 | 662.8 | 734.9 | 605.1 | 790.7 | 730.1 | 706.7 | 165.3 | 277.3 | 310.9 | 219.1 | 364.6 | 346.1 | 251 | 309.1
1371 | 1219 | 548.6 | 219.44 | 256.5127 | 386.7 | 351.1 | 349.7 | 332.4 | 588.4 | 58.1 | 18.9 | 97.9 | 4.1 | 149.3 | 5.2 | 853.1 | 825.4 | 761.5 | 799.1 | 667.1 | 735.7 | 603.8 | 802.4 | 729.4 | 709.1 | 165.5 | 277.5 | 311.1 | 219.3 | 364.9 | 346.3 | 251.2 | 309.3
1372 | 1220 | 549.8 | 219.92 | 257.0738 | 388.2 | 352.4 | 349.6 | 333.2 | 601.2 | 58.2 | 18.9 | 98 | 4 | 182.8 | 5.2 | 856.8 | 837.2 | 791.2 | 803.2 | 673.7 | 737.2 | 613.7 | 817.4 | 733.4 | 714.1 | 165.8 | 277.6 | 311 | 219.4 | 365.3 | 346.4 | 251.4 | 309.5
1373 | 1221 | 550 | 220 | 257.1673 | 388.7 | 354.2 | 349.1 | 334.4 | 595.7 | 58.2 | 18.9 | 98 | 3.8 | 187.6 | 5.4 | 858.7 | 840.9 | 810.6 | 806.1 | 679.9 | 738.3 | 622.8 | 825 | 736.8 | 717 | 166 | 277.8 | 310.9 | 219.6 | 365.4 | 346.5 | 251.6 | 309.7
1374 | 1222 | 549.1 | 219.64 | 256.7465 | 387.7 | 356.1 | 349 | 335 | 603.8 | 58.3 | 18.9 | 98 | 3.9 | 188.2 | 5.4 | 860.2 | 849.2 | 798.7 | 807.7 | 682.2 | 739.2 | 624.6 | 828.6 | 738.1 | 719.2 | 166.3 | 278 | 311.3 | 219.8 | 365.7 | 346.4 | 251.7 | 309.9
1375 | 1223 | 548.8 | 219.52 | 256.6062 | 386.3 | 357.8 | 348.6 | 335.2 | 615.5 | 58.3 | 18.9 | 98 | 4 | 185.9 | 5.1 | 862.8 | 861.8 | 803.6 | 810.3 | 682.8 | 745.7 | 618.7 | 837.2 | 730.1 | 721.1 | 166.6 | 278.1 | 311.6 | 219.9 | 365.9 | 346.7 | 251.9 | 310
1376 | 1224 | 549.4 | 219.76 | 256.8868 | 384.9 | 358.6 | 348.5 | 335.4 | 642.3 | 58.4 | 18.9 | 98.1 | 3.7 | 175.4 | 4.5 | 864 | 865.8 | 807.6 | 810.1 | 685.7 | 741.7 | 623.7 | 842.4 | 741.8 | 723.2 | 166.8 | 278.3 | 312 | 220.1 | 366.3 | 346.9 | 252.1 | 310.2
1377 | 1225 | 549.7 | 219.88 | 257.0271 | 384.2 | 359.3 | 348.5 | 335.9 | 643 | 58.4 | 18.9 | 98.1 | 3.4 | 176.7 | 4.1 | 864.2 | 851 | 797.6 | 808.1 | 685.3 | 742.5 | 616.6 | 831.4 | 739 | 721.5 | 167.1 | 278.5 | 312.8 | 220.2 | 367.4 | 347.3 | 252.3 | 310.3
1378 | 1226 | 550.5 | 220.2 | 257.4011 | 384.9 | 359.5 | 348.3 | 336.2 | 633.8 | 58.5 | 18.9 | 98.1 | 3.5 | 200.6 | 5.2 | 865.4 | 851.2 | 781.4 | 808.7 | 683.4 | 743.3 | 613.7 | 833.6 | 737.9 | 720.6 | 167.4 | 278.7 | 313.1 | 220.4 | 368 | 348.2 | 252.4 | 310.4
1379 | 1227 | 551 | 220.4 | 257.6349 | 385.5 | 360.2 | 348.7 | 336.6 | 636.8 | 58.5 | 18.9 | 98 | 3.9 | 183.8 | 6.5 | 867.1 | 855 | 776.1 | 809.7 | 682.8 | 744.1 | 612.3 | 841.4 | 738.3 | 721.7 | 167.6 | 278.9 | 313.2 | 220.6 | 369.1 | 348.6 | 252.6 | 310.6
1380 | 1228 | 550.5 | 220.2 | 257.4011 | 386.5 | 360.1 | 349.3 | 337.7 | 637.1 | 58.6 | 18.9 | 98 | 4.4 | 187.9 | 7.4 | 869.1 | 850.3 | 776.7 | 810.7 | 682.7 | 745 | 611.5 | 836.4 | 739.7 | 722.3 | 167.9 | 279.1 | 313.5 | 220.7 | 369.8 | 348.8 | 252.8 | 310.8
1381 | 1229 | 551.1 | 220.44 | 257.6817 | 389.2 | 360.4 | 349.4 | 338.6 | 629.4 | 58.6 | 18.9 | 98 | 4.3 | 186.3 | 7.7 | 869 | 838.5 | 784.2 | 809.7 | 684.9 | 746 | 606.8 | 832.6 | 739 | 722.6 | 168.2 | 279.3 | 314 | 220.9 | 370.6 | 349.2 | 253 | 311
1382 | 1230 | 550.2 | 220.08 | 257.2608 | 389.6 | 361.7 | 349.6 | 339.6 | 635.7 | 58.7 | 18.9 | 98 | 3.8 | 181.7 | 7.7 | 869.5 | 837.8 | 813.6 | 810.4 | 690.6 | 746.8 | 606.2 | 841.1 | 738.7 | 723.7 | 168.4 | 279.5 | 314.2 | 221.1 | 371.2 | 349.5 | 253.2 | 311.1
1383 | 1231 | 551.4 | 220.56 | 257.8219 | 390.1 | 365.4 | 350.6 | 341 | 653.4 | 58.8 | 18.9 | 98.1 | 4.2 | 189.7 | 6.9 | 872 | 841.7 | 831.1 | 813.5 | 696.1 | 747.6 | 605.8 | 851.3 | 739.7 | 726.8 | 168.7 | 279.7 | 314.3 | 221.2 | 371.6 | 350.4 | 253.4 | 311.3
1384 | 1232 | 552 | 220.8 | 258.1025 | 389.5 | 368.8 | 351 | 341.9 | 669.8 | 58.7 | 18.9 | 98.1 | 4.1 | 181.6 | 6.1 | 872.9 | 835.1 | 820 | 813.6 | 695.9 | 748.6 | 602.9 | 849.6 | 739.9 | 727.5 | 169 | 279.9 | 314.7 | 221.4 | 372.2 | 351.1 | 253.6 | 311.5
1385 | 1233 | 552.2 | 220.88 | 258.196 | 388.8 | 369.8 | 350.8 | 342.5 | 677.4 | 58.7 | 18.9 | 98.1 | 4.3 | 165.2 | 5.7 | 873.4 | 827 | 831.3 | 812.2 | 699.1 | 749.5 | 600.1 | 853 | 738.8 | 727.8 | 169.2 | 280.2 | 315.3 | 221.6 | 372.8 | 351.5 | 253.8 | 311.7
1386 | 1234 | 551.9 | 220.76 | 258.0557 | 387.8 | 369.2 | 350.9 | 343.9 | 672.3 | 58.8 | 18.9 | 98.2 | 4.6 | 184 | 5.6 | 872.1 | 817.3 | 835.5 | 812 | 702 | 754.1 | 565.8 | 837.5 | 696.4 | 727.1 | 169.5 | 280.4 | 315.8 | 221.7 | 373.3 | 351.9 | 254 | 311.8
1387 | 1235 | 552.4 | 220.96 | 258.2895 | 387.6 | 369.2 | 351.9 | 345.1 | 649.5 | 58.8 | 18.9 | 98.2 | 4.8 | 188.9 | 5.3 | 872.6 | 818 | 828.8 | 812.7 | 701.1 | 749.9 | 592.5 | 833.3 | 733.9 | 726.8 | 169.7 | 280.6 | 316.2 | 221.9 | 373.8 | 352.7 | 254.2 | 312
1388 | 1236 | 552.5 | 221 | 258.3363 | 387.6 | 370.8 | 352.9 | 346.5 | 641.4 | 58.8 | 18.9 | 98.3 | 4.9 | 186.1 | 4.9 | 874.2 | 828.3 | 823.2 | 814.2 | 700.2 | 750.3 | 591.4 | 833.3 | 732.8 | 726.4 | 170 | 280.9 | 316.2 | 222 | 374.2 | 353 | 254.3 | 312.3
1389 | 1237 | 552.2 | 220.88 | 258.196 | 388.5 | 371.9 | 353.8 | 347.2 | 650.4 | 58.8 | 18.9 | 98.4 | 4.3 | 179.8 | 4.7 | 872.6 | 818.8 | 804.5 | 813.2 | 700.8 | 750.2 | 590.8 | 827.2 | 732.7 | 725.1 | 170.3 | 281.1 | 316.2 | 222.2 | 374.6 | 352.7 | 254.5 | 312.5
1390 | 1238 | 553 | 221.2 | 258.5701 | 389.1 | 373.1 | 354.3 | 347.8 | 640.3 | 58.7 | 18.9 | 98.4 | 3.9 | 178 | 4 | 873.7 | 825.2 | 804.3 | 813.3 | 702.3 | 750.2 | 589.9 | 830.1 | 731.8 | 725.5 | 170.5 | 281.3 | 316.4 | 222.4 | 375 | 352.9 | 254.7 | 312.7
1391 | 1239 | 551.8 | 220.72 | 258.009 | 389.2 | 373.2 | 354.2 | 347.9 | 636.3 | 58.7 | 18.9 | 98.5 | 3.7 | 172.9 | 3.6 | 873.8 | 833.1 | 796 | 814.4 | 701.1 | 750.6 | 593.9 | 836.7 | 734 | 726.6 | 170.8 | 281.6 | 316.3 | 222.5 | 375.1 | 353 | 254.9 | 312.9
1392 | 1240 | 552.4 | 220.96 | 258.2895 | 388.9 | 373.5 | 354.3 | 348 | 636.3 | 58.6 | 18.9 | 98.5 | 3.9 | 170 | 3.8 | 873.9 | 835.4 | 810.7 | 815.7 | 705 | 751.2 | 605.3 | 841.8 | 738.4 | 729.8 | 171.1 | 281.8 | 316.4 | 222.7 | 375.1 | 353 | 255.1 | 313.1
1393 | 1241 | 553 | 221.2 | 258.5701 | 387.7 | 374 | 354.5 | 347.9 | 648.7 | 58.6 | 18.9 | 98.7 | 3.6 | 184.5 | 4.7 | 872 | 834.8 | 824.6 | 816.2 | 709.4 | 752.1 | 616.8 | 845.9 | 742 | 732.5 | 171.3 | 282 | 316.5 | 222.8 | 375.2 | 352.9 | 255.3 | 313.3
1394 | 1242 | 552.7 | 221.08 | 258.4298 | 387.8 | 375.1 | 354.2 | 347.6 | 666.3 | 58.7 | 18.9 | 98.7 | 3.8 | 178.9 | 5.3 | 870.8 | 833.5 | 834 | 816.3 | 712.6 | 753 | 627.6 | 848.1 | 745.4 | 735.4 | 171.6 | 282.2 | 316.8 | 223 | 375.4 | 352.9 | 255.4 | 313.5
1395 | 1243 | 553 | 221.2 | 258.5701 | 387.8 | 374.6 | 354.2 | 347.2 | 667.8 | 58.6 | 18.9 | 98.8 | 3.6 | 168.9 | 5.5 | 872.9 | 849 | 829.4 | 816.7 | 712.2 | 753.9 | 631.4 | 854.9 | 748.8 | 737.2 | 171.9 | 282.4 | 317 | 223.2 | 375.4 | 353.3 | 255.6 | 313.7
1396 | 1244 | 553.5 | 221.4 | 258.8038 | 387.6 | 373.9 | 354.7 | 346.9 | 663 | 58.6 | 18.9 | 98.8 | 4 | 181.6 | 5.7 | 868.4 | 854.3 | 785.8 | 816.9 | 707.4 | 754.7 | 626.4 | 834.4 | 747.9 | 733.6 | 172.1 | 282.6 | 317.3 | 223.3 | 375.3 | 353.5 | 255.8 | 313.8
1397 | 1245 | 553.6 | 221.44 | 258.8506 | 388.4 | 373.5 | 355.3 | 346.7 | 647.9 | 58.6 | 18.9 | 98.9 | 3.7 | 197.3 | 5.5 | 862.2 | 826.1 | 749.2 | 811.8 | 702.6 | 755.8 | 612.1 | 798.3 | 737.8 | 728.2 | 172.4 | 282.8 | 317.9 | 223.5 | 375.5 | 353.7 | 255.9 | 314
1398 | 1246 | 554.3 | 221.72 | 259.1779 | 389.9 | 372.8 | 356.1 | 346.8 | 620.9 | 58.5 | 18.9 | 98.8 | 3.6 | 195.3 | 5.2 | 858.7 | 811.8 | 742 | 806.8 | 699.7 | 754.2 | 607.7 | 773.2 | 737.8 | 724.2 | 172.6 | 283 | 318.1 | 223.6 | 375.3 | 354 | 256.1 | 314.2
1399 | 1247 | 554.6 | 221.84 | 259.3182 | 391 | 373.2 | 356.4 | 346.8 | 602.8 | 58.5 | 18.8 | 98.8 | 3.7 | 166.3 | 5.4 | 862.6 | 825.6 | 749.7 | 808.3 | 699.7 | 753.9 | 606.4 | 785.5 | 736.7 | 725.1 | 172.9 | 283.3 | 318 | 223.8 | 375.3 | 354.2 | 256.3 | 314.4
1400 | 1248 | 554.5 | 221.8 | 259.2714 | 391.5 | 375.4 | 356.3 | 346.9 | 596.1 | 58.6 | 18.8 | 98.9 | 3.6 | 169.2 | 5.9 | 865.5 | 838.9 | 762.7 | 810.7 | 700.8 | 754 | 611.7 | 803.1 | 739.3 | 728.6 | 173.2 | 283.5 | 318 | 224 | 375.2 | 354.1 | 256.5 | 314.6
1401 | 1249 | 553 | 221.2 | 258.5701 | 390.6 | 376.7 | 356.1 | 347.1 | 587.1 | 58.7 | 18.8 | 99.1 | 3.9 | 179.8 | 7 | 863.8 | 837.9 | 751.6 | 810 | 697.2 | 754.6 | 613.4 | 790.2 | 740.5 | 726.4 | 173.4 | 283.7 | 318.1 | 224.1 | 375.1 | 354.4 | 256.7 | 314.9
1402 | 1250 | 553.5 | 221.4 | 258.8038 | 390.9 | 376 | 356.1 | 346.5 | 575.2 | 58.8 | 18.8 | 99.2 | 3.5 | 179.6 | 7.4 | 867.6 | 842.9 | 770.6 | 812.9 | 698.4 | 754.7 | 615.8 | 799.3 | 742.1 | 728.1 | 173.7 | 283.9 | 318.2 | 224.3 | 375.2 | 355.1 | 256.9 | 315.1
1403 | 1251 | 554.6 | 221.84 | 259.3182 | 390.7 | 376 | 355.8 | 345.3 | 588.1 | 58.9 | 18.8 | 99.3 | 3.8 | 180.6 | 7.9 | 870.7 | 852.3 | 784.1 | 814.3 | 699.7 | 755.7 | 620.1 | 820.7 | 746.1 | 731.8 | 173.9 | 284.1 | 318.3 | 224.5 | 375.2 | 355.3 | 257.1 | 315.3
1404 | 1252 | 555.2 | 222.08 | 259.5987 | 389.6 | 374.4 | 355.8 | 344.5 | 606.6 | 59 | 18.8 | 99.4 | 4.3 | 181.2 | 8.2 | 873.2 | 866.1 | 781.1 | 815.6 | 698 | 756.9 | 618 | 834.5 | 747.8 | 732.1 | 174.2 | 284.3 | 318.4 | 224.6 | 375.3 | 355.7 | 257.2 | 315.5
1405 | 1253 | 555.5 | 222.2 | 259.739 | 389.5 | 373.4 | 356.1 | 343.9 | 634.9 | 59 | 18.8 | 99.5 | 4.2 | 177 | 8 | 870.6 | 852.6 | 752.4 | 813.2 | 693.9 | 758 | 611.5 | 825.8 | 743.7 | 730.6 | 174.5 | 284.5 | 319.1 | 224.8 | 375.6 | 356.3 | 257.4 | 315.7
1406 | 1254 | 556 | 222.4 | 259.9728 | 390.5 | 373.2 | 356.7 | 343.7 | 625.5 | 59 | 18.8 | 99.6 | 4.6 | 174.8 | 7.6 | 862.6 | 816.2 | 732 | 806.8 | 689.2 | 768.2 | 496.6 | 787.3 | 601.9 | 724.8 | 174.7 | 284.6 | 319.7 | 224.9 | 375.9 | 356.3 | 257.6 | 315.8
1407 | 1255 | 554.3 | 221.72 | 259.1779 | 392.4 | 373.6 | 356.9 | 343.5 | 611 | 59.1 | 18.8 | 99.7 | 3.9 | 176 | 7.3 | 857.9 | 788.7 | 739.1 | 801.9 | 688.1 | 757.7 | 597.1 | 772.1 | 736.7 | 721.6 | 175 | 284.9 | 320.1 | 225.1 | 376.5 | 356.4 | 257.8 | 315.9
1408 | 1256 | 555.8 | 222.32 | 259.8793 | 393.5 | 374.8 | 357 | 343.4 | 615.2 | 59.2 | 18.8 | 99.7 | 4.3 | 176.1 | 7.1 | 857.3 | 779.8 | 752.8 | 798.4 | 687.2 | 757.1 | 593 | 761.7 | 732.3 | 720.5 | 175.2 | 285.1 | 320.7 | 225.3 | 377.3 | 356.3 | 258 | 316.1
1409 | 1257 | 556.5 | 222.6 | 260.2066 | 393.6 | 375.5 | 357.7 | 344.1 | 606.7 | 59.3 | 18.8 | 99.8 | 4.4 | 177.1 | 7 | 860.9 | 785.4 | 764.7 | 798.8 | 687.9 | 757.1 | 592.6 | 777.3 | 730.9 | 721.1 | 175.5 | 285.3 | 320.5 | 225.5 | 377.9 | 356.2 | 258.2 | 316.3
1410 | 1258 | 555.8 | 222.32 | 259.8793 | 394.7 | 376.2 | 357.9 | 345.3 | 625.2 | 59.5 | 18.8 | 99.9 | 4.3 | 176.6 | 6.8 | 862.1 | 783.4 | 763.4 | 798.2 | 685.8 | 757.1 | 591.2 | 787.7 | 729.7 | 720.3 | 175.8 | 285.6 | 321 | 225.6 | 378.3 | 356.7 | 258.4 | 316.4
1411 | 1259 | 556.7 | 222.68 | 260.3001 | 394.9 | 377.9 | 358.4 | 346.1 | 624 | 59.6 | 18.8 | 99.9 | 4.7 | 175.7 | 6.8 | 857.6 | 761.8 | 734.5 | 793.8 | 681.8 | 755.9 | 589.6 | 783.3 | 727.3 | 718 | 176 | 285.8 | 321.7 | 225.8 | 378.8 | 357.1 | 258.6 | 316.6
1412 | 1260 | 556.8 | 222.72 | 260.3468 | 394.4 | 381.5 | 359.1 | 346.6 | 620.6 | 59.6 | 18.8 | 99.9 | 4.4 | 175.8 | 6.8 | 853.7 | 747.7 | 738.5 | 790.4 | 681 | 756.4 | 586.8 | 770.1 | 725.4 | 716.5 | 176.3 | 286.1 | 322.1 | 225.9 | 379.6 | 357.9 | 258.8 | 316.8
1413 | 1261 | 556.2 | 222.48 | 260.0663 | 394.9 | 383.8 | 360.4 | 347.6 | 606.2 | 59.6 | 18.8 | 100 | 4 | 179.1 | 6.4 | 848.7 | 743.1 | 711.8 | 786.8 | 677.5 | 755.5 | 581.9 | 740.1 | 721.1 | 711.7 | 176.5 | 286.3 | 322.5 | 226.1 | 380.1 | 357.9 | 259 | 316.9
1414 | 1262 | 556.4 | 222.56 | 260.1598 | 395.3 | 383.1 | 362 | 349.2 | 593.1 | 59.5 | 18.8 | 100.1 | 4.3 | 180.7 | 6.4 | 846.9 | 745.1 | 707 | 784.6 | 675.8 | 754.2 | 578.6 | 738.8 | 717.8 | 709.2 | 176.8 | 286.6 | 322.8 | 226.3 | 380.6 | 357.6 | 259.2 | 317.1
1415 | 1263 | 556.4 | 222.56 | 260.1598 | 395.7 | 382.6 | 363.9 | 350.5 | 589.9 | 59.4 | 18.8 | 100.1 | 4 | 186.6 | 5.8 | 843 | 734.9 | 705.3 | 780.7 | 673.4 | 753.1 | 573.5 | 731.9 | 714.6 | 706 | 177.1 | 286.9 | 323.2 | 226.4 | 381.2 | 357.7 | 259.4 | 317.2
1416 | 1264 | 556.9 | 222.76 | 260.3936 | 396.5 | 384 | 364.6 | 351.4 | 600.6 | 59.4 | 18.8 | 100.2 | 3.7 | 199.1 | 5.3 | 844.1 | 740.9 | 718.3 | 779.4 | 672.6 | 752.3 | 574.7 | 746.1 | 714.2 | 706.2 | 177.3 | 287.1 | 323.4 | 226.6 | 381.7 | 357.7 | 259.6 | 317.4
1417 | 1265 | 556.9 | 222.76 | 260.3936 | 397.8 | 385.3 | 365.1 | 352.4 | 602.9 | 59.4 | 18.8 | 100.2 | 3.7 | 186.3 | 5.2 | 844.4 | 744.9 | 714.6 | 778.3 | 670.7 | 751.5 | 575.9 | 746.8 | 714.5 | 705.7 | 177.6 | 287.4 | 323.4 | 226.8 | 382.1 | 358 | 259.9 | 317.6
1418 | 1266 | 557.4 | 222.96 | 260.6274 | 398.6 | 385.6 | 365.1 | 353.1 | 595.7 | 59.4 | 18.8 | 100.3 | 3.6 | 170.4 | 5.2 | 838.6 | 736.7 | 687.9 | 773.8 | 665.8 | 750.6 | 575.1 | 734.9 | 713.1 | 703.5 | 177.8 | 287.6 | 323.7 | 226.9 | 382.6 | 357.9 | 260 | 317.7
1419 | 1267 | 557 | 222.8 | 260.4404 | 399.3 | 386.4 | 365.9 | 354 | 588.3 | 59.3 | 18.8 | 100.4 | 3.9 | 182.8 | 5.5 | 833.5 | 724.7 | 661.3 | 770.1 | 662.6 | 749.2 | 571.5 | 712.7 | 710.2 | 699.6 | 178.1 | 287.9 | 324.2 | 227.1 | 383.1 | 358.1 | 260.3 | 317.9
1420 | 1268 | 557.5 | 223 | 260.6742 | 400.3 | 388.2 | 366.8 | 354.6 | 575.9 | 59.3 | 18.8 | 100.4 | 4.3 | 184.9 | 5.7 | 834.3 | 735.2 | 659.1 | 769.3 | 660.4 | 747.7 | 569.7 | 721.3 | 708.3 | 698 | 178.3 | 288.1 | 324.2 | 227.2 | 383.7 | 358.3 | 260.5 | 318.1
1421 | 1269 | 559 | 223.6 | 261.3755 | 400 | 390.6 | 367.2 | 355 | 588.3 | 59.2 | 18.8 | 100.4 | 3.7 | 185.1 | 5.5 | 839.3 | 763.8 | 670.6 | 772 | 663 | 746.8 | 571.8 | 750.9 | 709.8 | 700.8 | 178.6 | 288.3 | 324.2 | 227.4 | 383.9 | 358.3 | 260.7 | 318.3
1422 | 1270 | 559.6 | 223.84 | 261.6561 | 398.3 | 390.6 | 367.2 | 355.4 | 609.7 | 59.3 | 18.8 | 100.4 | 3.8 | 185.8 | 5.4 | 842.1 | 784.2 | 657.9 | 773.6 | 661.9 | 746.3 | 576.9 | 761.6 | 712.4 | 702.6 | 178.8 | 288.6 | 324.2 | 227.5 | 383.9 | 358.6 | 260.9 | 318.5
1423 | 1271 | 560.4 | 224.16 | 262.0301 | 398.1 | 388.3 | 366.8 | 355.8 | 609.1 | 59.4 | 18.8 | 100.4 | 4.2 | 186.3 | 5.5 | 840.1 | 788.9 | 651.8 | 774.1 | 660.5 | 746 | 582.1 | 743.8 | 713.2 | 700.6 | 179.1 | 288.8 | 324.1 | 227.7 | 384.1 | 358.7 | 261.1 | 318.8
1424 | 1272 | 561.1 | 224.44 | 262.3574 | 398.4 | 387.7 | 366.6 | 356 | 589.1 | 59.4 | 18.8 | 100.4 | 3.9 | 181.1 | 5.6 | 841.5 | 803.8 | 662.9 | 775.7 | 662.4 | 744.6 | 587.3 | 752.4 | 714.4 | 701.8 | 179.3 | 289 | 324 | 227.9 | 384.2 | 359 | 261.3 | 319
1425 | 1273 | 561.1 | 224.44 | 262.3574 | 398.1 | 387.8 | 366.3 | 355.8 | 592 | 59.5 | 18.8 | 100.4 | 4.4 | 179 | 5.9 | 846.5 | 816.6 | 666.3 | 779.6 | 663.1 | 744.1 | 590.8 | 782.1 | 717.1 | 705.7 | 179.6 | 289.2 | 324.2 | 228 | 384 | 359.4 | 261.5 | 319.2
1426 | 1274 | 560 | 224 | 261.8431 | 398.4 | 387.1 | 366 | 355.4 | 609.9 | 59.5 | 18.8 | 100.4 | 4.7 | 178.2 | 6 | 840.5 | 794.1 | 647.1 | 776.2 | 658.2 | 743.3 | 587.8 | 759.3 | 715.4 | 701.5 | 179.8 | 289.4 | 325 | 228.2 | 384 | 359.5 | 261.7 | 319.3
1427 | 1275 | 558.6 | 223.44 | 261.1885 | 399.7 | 387 | 365.8 | 354.6 | 588.4 | 59.6 | 18.8 | 100.3 | 4.1 | 168.6 | 6 | 830.4 | 764.4 | 626.2 | 768.8 | 653.9 | 741.5 | 579.1 | 718.6 | 710.1 | 695.8 | 180.1 | 289.6 | 325.4 | 228.3 | 384.2 | 359.8 | 261.9 | 319.5
1428 | 1276 | 557.9 | 223.16 | 260.8612 | 401.5 | 386.5 | 365.1 | 353.5 | 564.7 | 59.7 | 18.8 | 100.4 | 4.3 | 164.2 | 6.4 | 825.8 | 754.1 | 619.2 | 766.3 | 651.5 | 739.5 | 573.5 | 694.4 | 705.8 | 692 | 180.3 | 289.7 | 325.4 | 228.5 | 384.1 | 360.2 | 262.1 | 319.8
1429 | 1277 | 557.6 | 223.04 | 260.7209 | 401.7 | 385.1 | 364.5 | 352.7 | 550.9 | 59.7 | 18.8 | 100.4 | 4.2 | 166.5 | 6.4 | 826.9 | 773 | 623.7 | 768.3 | 651.9 | 737.9 | 576 | 696.7 | 705.4 | 692.2 | 180.6 | 289.9 | 325.1 | 228.7 | 383.7 | 360.4 | 262.3 | 320
1430 | 1278 | 556.1 | 222.44 | 260.0195 | 400.9 | 384.2 | 364.5 | 352 | 551.8 | 59.8 | 18.8 | 100.6 | 3.8 | 172.9 | 6.6 | 830.9 | 795.8 | 641.7 | 771.9 | 653 | 736.8 | 586.6 | 717.8 | 707.4 | 694.9 | 180.8 | 290.2 | 325.1 | 228.8 | 383.3 | 360.8 | 262.5 | 320.3
1431 | 1279 | 556.7 | 222.68 | 260.3001 | 399.5 | 383.1 | 364.2 | 351.6 | 552.8 | 59.8 | 18.8 | 100.7 | 4.5 | 176.9 | 6.8 | 835.8 | 813.6 | 654.4 | 775.4 | 655.6 | 735.9 | 593.6 | 719.8 | 709.7 | 697.1 | 181.1 | 290.3 | 325.1 | 229 | 383.1 | 361.1 | 262.6 | 320.6
1432 | 1280 | 556.7 | 222.68 | 260.3001 | 398.3 | 383.8 | 363.8 | 351.5 | 549.7 | 59.8 | 18.8 | 100.8 | 4.1 | 185.5 | 7 | 841.2 | 828.2 | 667.8 | 779.6 | 657.8 | 735.2 | 597.5 | 735.1 | 711.5 | 698.4 | 181.3 | 290.5 | 325.1 | 229.1 | 382.9 | 361.3 | 262.9 | 320.8
1433 | 1281 | 557.1 | 222.84 | 260.4871 | 397.2 | 385 | 363.1 | 351.3 | 555.8 | 59.8 | 18.8 | 100.9 | 4 | 179.1 | 6.9 | 846.8 | 835.3 | 690.5 | 783.1 | 657.7 | 734.6 | 599.3 | 758.1 | 713.1 | 700.2 | 181.6 | 290.7 | 325.4 | 229.3 | 382.9 | 361.5 | 263 | 321
1434 | 1282 | 558 | 223.2 | 260.9079 | 395.8 | 384.9 | 362.5 | 350.3 | 556 | 59.8 | 18.8 | 101 | 4.1 | 177.4 | 6.7 | 849.3 | 843 | 716.1 | 787 | 661 | 733.8 | 602.1 | 775.9 | 715 | 702.9 | 181.8 | 290.9 | 325.4 | 229.4 | 382.9 | 361.5 | 263.2 | 321.2
1435 | 1283 | 558.3 | 223.32 | 261.0482 | 395.4 | 384.7 | 361.8 | 349.3 | 560.4 | 59.8 | 18.8 | 101.1 | 4.4 | 185.2 | 6.1 | 850.2 | 847.9 | 729 | 789.4 | 663.5 | 733.4 | 607.5 | 776.1 | 716.6 | 704 | 182.1 | 291.1 | 325.5 | 229.6 | 382.9 | 361.6 | 263.4 | 321.4
1436 | 1284 | 558 | 223.2 | 260.9079 | 395.2 | 384.4 | 361.4 | 349.1 | 553.6 | 59.9 | 18.8 | 101.2 | 4.4 | 195.9 | 5.8 | 851.4 | 853.4 | 730.4 | 791.6 | 662.6 | 732.7 | 603.9 | 773.5 | 716.7 | 703 | 182.3 | 291.2 | 325.7 | 229.8 | 382.7 | 362.2 | 263.6 | 321.6
1437 | 1285 | 557.1 | 222.84 | 260.4871 | 395.8 | 382.9 | 360.3 | 349.2 | 556.3 | 60 | 18.8 | 101.3 | 4.3 | 185.2 | 5.5 | 854.1 | 853.1 | 741.1 | 793.4 | 662.8 | 732.4 | 602.5 | 790.7 | 717.2 | 704.2 | 182.6 | 291.4 | 325.9 | 229.9 | 382.6 | 362.5 | 263.8 | 321.8
1438 | 1286 | 558.6 | 223.44 | 261.1885 | 396 | 381.4 | 359.6 | 348.9 | 564.3 | 60.1 | 18.8 | 101.4 | 4.2 | 179 | 6.6 | 852.1 | 835.8 | 726.5 | 790.6 | 660 | 732.1 | 598.6 | 778.8 | 715.6 | 702.1 | 182.8 | 291.6 | 326.2 | 230.1 | 382.5 | 362.6 | 264 | 322.1
1439 | 1287 | 559.4 | 223.76 | 261.5625 | 396 | 380.2 | 359.6 | 348.1 | 558.4 | 60.1 | 18.8 | 101.6 | 4.7 | 185 | 7.1 | 849 | 824.7 | 717.3 | 788.9 | 658.9 | 731.5 | 594.3 | 759 | 713.5 | 699.3 | 183.1 | 291.8 | 326.7 | 230.2 | 382.2 | 363.1 | 264.2 | 322.3
1440 | 1288 | 558.6 | 223.44 | 261.1885 | 395.2 | 379.7 | 359.5 | 347.2 | 558 | 60.2 | 18.8 | 101.7 | 4.4 | 184.4 | 7.1 | 848.1 | 815.5 | 710.9 | 787 | 658.1 | 731 | 592.1 | 762.9 | 711.9 | 698.5 | 183.3 | 292 | 326.8 | 230.4 | 382 | 363.3 | 264.4 | 322.6
1441 | 1289 | 558.7 | 223.48 | 261.2352 | 395.5 | 379.6 | 359.4 | 347 | 570.5 | 60.2 | 18.8 | 101.9 | 4.3 | 180.5 | 7.2 | 850 | 820.5 | 707.5 | 788.9 | 658.3 | 730.7 | 589.9 | 777.5 | 711.5 | 698.6 | 183.6 | 292.2 | 327.1 | 230.6 | 381.7 | 363.4 | 264.6 | 322.8
1442 | 1290 | 559.6 | 223.84 | 261.6561 | 396 | 379.8 | 359.6 | 346.5 | 582.4 | 60.3 | 18.8 | 101.9 | 4.1 | 181.3 | 7 | 854 | 831.3 | 711.4 | 789.6 | 659 | 731 | 592.6 | 797.8 | 713 | 701.8 | 183.8 | 292.4 | 327.2 | 230.7 | 381.6 | 363.2 | 264.8 | 323
1443 | 1291 | 558.7 | 223.48 | 261.2352 | 395.4 | 379.8 | 360.4 | 346 | 602.4 | 60.3 | 18.8 | 102 | 4.1 | 187.5 | 6.5 | 856.3 | 834.7 | 734.1 | 790.4 | 660.4 | 731.7 | 595 | 810.9 | 714.7 | 704.5 | 184.1 | 292.6 | 327.3 | 230.9 | 382 | 363 | 265 | 323.1
1444 | 1292 | 558.3 | 223.32 | 261.0482 | 394.5 | 379.9 | 361 | 345.7 | 620.7 | 60.2 | 18.8 | 102.1 | 4.3 | 186 | 6 | 859.2 | 844.1 | 758 | 794.2 | 665.8 | 733 | 605.9 | 818.4 | 719.2 | 710.5 | 184.3 | 292.8 | 327.4 | 231 | 382.3 | 363 | 265.2 | 323.3
1445 | 1293 | 559.6 | 223.84 | 261.6561 | 393.6 | 380.5 | 361.4 | 345.8 | 640.3 | 60.1 | 18.8 | 102.1 | 4.3 | 186.8 | 6.1 | 861.3 | 851.7 | 760.9 | 796.4 | 665.8 | 734.4 | 611.8 | 833.2 | 723.9 | 714.8 | 184.6 | 293 | 327.7 | 231.2 | 382.4 | 363.1 | 265.4 | 323.4
1446 | 1294 | 558.6 | 223.44 | 261.1885 | 393 | 381.1 | 361.7 | 346.2 | 686.7 | 60 | 18.8 | 102.2 | 4.3 | 174.3 | 6.2 | 862 | 851.1 | 766.2 | 796.1 | 667.6 | 735.9 | 612.1 | 841.5 | 725.9 | 717.8 | 184.8 | 293.1 | 328.3 | 231.3 | 383 | 363 | 265.6 | 323.6
1447 | 1295 | 558.5 | 223.4 | 261.1417 | 392.7 | 383.4 | 362.2 | 346.2 | 694.2 | 60 | 18.8 | 102.3 | 4.7 | 170.7 | 5.8 | 859.4 | 834.9 | 750.4 | 795.1 | 665.2 | 736.5 | 606.8 | 832.4 | 723.5 | 714.9 | 185 | 293.3 | 328.9 | 231.5 | 383.7 | 363.5 | 265.8 | 323.7
1448 | 1296 | 561.3 | 224.52 | 262.4509 | 392.9 | 385.7 | 362.7 | 346.7 | 692.1 | 60 | 18.8 | 102.3 | 4.6 | 166.9 | 5.4 | 857.3 | 819.2 | 747.7 | 792.8 | 665.2 | 737 | 603.5 | 824.9 | 720.7 | 712.9 | 185.3 | 293.6 | 329.3 | 231.7 | 384.2 | 363.5 | 266 | 323.8
1449 | 1297 | 561.9 | 224.76 | 262.7315 | 392.9 | 387.4 | 363.4 | 347.9 | 674.8 | 60.1 | 18.8 | 102.4 | 4.7 | 168.9 | 5.5 | 851 | 795.5 | 726 | 787.4 | 661.8 | 736.9 | 598.1 | 796.6 | 717.5 | 709.7 | 185.5 | 293.8 | 329.6 | 231.8 | 384.5 | 363.3 | 266.2 | 323.9
1450 | 1298 | 560.2 | 224.08 | 261.9366 | 394.5 | 388.8 | 363.8 | 348.8 | 640.8 | 60.1 | 18.8 | 102.4 | 4.3 | 178.2 | 5.2 | 845.3 | 781.1 | 721.9 | 784.4 | 659.4 | 736.2 | 591.6 | 768.8 | 713.8 | 705.4 | 185.8 | 294 | 329.7 | 231.9 | 384.7 | 363.4 | 266.4 | 324.1
1451 | 1299 | 559.3 | 223.72 | 261.5158 | 395.5 | 390.1 | 364.1 | 349.4 | 623.1 | 60.1 | 18.8 | 102.4 | 4.1 | 190.7 | 5.6 | 847.9 | 792.1 | 745.9 | 785.9 | 663.2 | 736 | 590.6 | 788.9 | 712.9 | 706.7 | 186 | 294.3 | 329.6 | 232.1 | 384.7 | 363.5 | 266.6 | 324.3
1452 | 1300 | 560.3 | 224.12 | 261.9834 | 396.1 | 390.1 | 364.1 | 349.1 | 618.4 | 60 | 18.8 | 102.5 | 3.9 | 174.8 | 6.5 | 849.8 | 796.9 | 727.2 | 787.5 | 662.2 | 736.1 | 591.2 | 784.6 | 713.3 | 705.9 | 186.2 | 294.5 | 329.8 | 232.3 | 384.4 | 364.1 | 266.8 | 324.4
1453 | 1301 | 559.3 | 223.72 | 261.5158 | 395.6 | 388 | 364.2 | 348.5 | 605.5 | 59.9 | 18.8 | 102.5 | 4.4 | 171 | 6.6 | 845.3 | 786.1 | 705.8 | 785.4 | 659.2 | 735.7 | 587.2 | 756.8 | 710 | 701.1 | 186.5 | 294.7 | 330.2 | 232.4 | 384.3 | 364.1 | 267 | 324.6
1454 | 1302 | 558.3 | 223.32 | 261.0482 | 395.4 | 388.9 | 365 | 347.9 | 582 | 60 | 18.8 | 102.5 | 4.5 | 165.7 | 6.5 | 837.8 | 763.7 | 685 | 780.4 | 655.3 | 734.5 | 582 | 722.7 | 705.4 | 696.2 | 186.7 | 294.9 | 330.3 | 232.5 | 384.4 | 364.3 | 267.1 | 324.6
1455 | 1303 | 558.7 | 223.48 | 261.2352 | 396 | 389.3 | 365.5 | 347.3 | 563.6 | 60.1 | 18.8 | 102.6 | 4.2 | 177.8 | 6.2 | 834.9 | 763.1 | 673.5 | 778.9 | 654 | 733.2 | 576.9 | 703 | 702.1 | 692.5 | 187 | 295.1 | 330.5 | 232.7 | 384.5 | 364.3 | 267.3 | 324.7
1456 | 1304 | 559.5 | 223.8 | 261.6093 | 396.1 | 387.9 | 365.7 | 347.3 | 560.8 | 60.2 | 18.8 | 102.7 | 3.8 | 184.6 | 5.9 | 837.5 | 781.3 | 667.6 | 780.3 | 653 | 732.2 | 576.6 | 720.8 | 701.7 | 692.3 | 187.2 | 295.3 | 330.6 | 232.9 | 384.5 | 363.9 | 267.5 | 324.8
1457 | 1305 | 560.4 | 224.16 | 262.0301 | 396 | 387.1 | 365.5 | 347.9 | 577.6 | 60.3 | 18.7 | 102.8 | 4.2 | 171.7 | 6.3 | 843.3 | 801 | 679.2 | 783.5 | 654 | 731.9 | 578.3 | 750.4 | 703.3 | 695.6 | 187.4 | 295.6 | 330.6 | 233 | 384.4 | 363.3 | 267.7 | 325
1458 | 1306 | 559.4 | 223.76 | 261.5625 | 397.4 | 387 | 365.3 | 348.5 | 585.5 | 60.3 | 18.7 | 102.8 | 3.9 | 172.9 | 7.1 | 843 | 793.4 | 673.2 | 782.3 | 652.8 | 731.3 | 575.8 | 751.6 | 702.2 | 693.2 | 187.7 | 295.8 | 330.8 | 233.1 | 384.5 | 363.2 | 267.9 | 325.1
1459 | 1307 | 559.2 | 223.68 | 261.469 | 398.7 | 387 | 365 | 349.1 | 581.7 | 60.3 | 18.7 | 102.9 | 4 | 187.9 | 7.3 | 839.2 | 781.2 | 657.7 | 778.9 | 649.3 | 730.5 | 571 | 730.7 | 699.7 | 689.8 | 187.9 | 296 | 330.9 | 233.3 | 384.5 | 363.1 | 268.1 | 325.3
1460 | 1308 | 560.6 | 224.24 | 262.1236 | 398.3 | 388.1 | 364.4 | 350 | 561.5 | 60.4 | 18.8 | 103 | 4.1 | 187.3 | 7.5 | 838.7 | 794 | 667.5 | 780.1 | 650.3 | 729.4 | 572.2 | 723.5 | 698.8 | 689.4 | 188.1 | 296.2 | 331 | 233.4 | 384.4 | 362.9 | 268.3 | 325.5
1461 | 1309 | 562 | 224.8 | 262.7782 | 398.2 | 388.5 | 364.1 | 350.9 | 559.5 | 60.4 | 18.7 | 103.1 | 4.2 | 177.6 | 7.6 | 841.6 | 810.7 | 681.8 | 783.7 | 653.1 | 728.8 | 579.6 | 747.4 | 701.9 | 692.2 | 188.4 | 296.3 | 330.9 | 233.6 | 384 | 363.2 | 268.4 | 325.7
1462 | 1310 | 560.9 | 224.36 | 262.2639 | 397.7 | 387.6 | 363.9 | 351.4 | 565.5 | 60.6 | 18.7 | 103.1 | 4.6 | 176.2 | 7.7 | 843.4 | 818.4 | 696.4 | 785.8 | 655 | 728.8 | 586.2 | 759.2 | 705.1 | 695 | 188.6 | 296.5 | 331.1 | 233.7 | 383.7 | 363.2 | 268.6 | 325.8
1463 | 1311 | 560 | 224 | 261.8431 | 397.3 | 387.1 | 363.7 | 351.1 | 566.7 | 60.6 | 18.7 | 103 | 4.4 | 174.7 | 7.2 | 843.6 | 817 | 691.6 | 785.1 | 652.6 | 728.4 | 582 | 751.3 | 703.9 | 691.7 | 188.8 | 296.7 | 331.4 | 233.9 | 383.5 | 363 | 268.8 | 325.9
1464 | 1312 | 560.7 | 224.28 | 262.1704 | 397.2 | 386.2 | 363.7 | 350.2 | 559.3 | 60.7 | 18.7 | 103 | 4.2 | 160.9 | 6.8 | 844.4 | 817.2 | 689.5 | 785.7 | 652.7 | 727.7 | 581 | 752 | 701.8 | 690.2 | 189.1 | 296.8 | 331.3 | 234 | 383.3 | 363.3 | 269 | 326.2
1465 | 1313 | 561.3 | 224.52 | 262.4509 | 398 | 386.3 | 364 | 349.8 | 557.1 | 60.8 | 18.7 | 103.1 | 4 | 166 | 6 | 841.6 | 799.5 | 684.7 | 783.8 | 650.5 | 726.9 | 581.9 | 750 | 701.2 | 689.6 | 189.3 | 297 | 331.3 | 234.2 | 383.1 | 363.7 | 269.1 | 326.4
1466 | 1314 | 560.9 | 224.36 | 262.2639 | 397.7 | 384.7 | 364 | 349.2 | 547.3 | 60.9 | 18.7 | 103.1 | 4.7 | 172.6 | 5.7 | 841.4 | 802.7 | 694.2 | 784 | 650.5 | 725.8 | 579.6 | 744.6 | 699.8 | 687.6 | 189.5 | 297.2 | 331.2 | 234.3 | 382.9 | 363.7 | 269.3 | 326.5
1467 | 1315 | 562 | 224.8 | 262.7782 | 397 | 383.3 | 363.4 | 348.3 | 547.4 | 61 | 18.7 | 103.1 | 4.7 | 180.3 | 5.3 | 845.6 | 819.5 | 713.3 | 787.7 | 653.7 | 725.6 | 587.2 | 764.4 | 703 | 692 | 189.8 | 297.3 | 331.3 | 234.5 | 382.6 | 364 | 269.4 | 326.7
1468 | 1316 | 561.6 | 224.64 | 262.5912 | 396.5 | 383.3 | 362.9 | 347.3 | 550.9 | 61.1 | 18.7 | 103.2 | 4.1 | 182.5 | 4.6 | 849 | 835.7 | 733.6 | 791.6 | 655.3 | 725.5 | 590.1 | 768.7 | 705.7 | 694.3 | 190 | 297.5 | 331.4 | 234.6 | 382.2 | 364.7 | 269.6 | 326.9
1469 | 1317 | 560.7 | 224.28 | 262.1704 | 397.1 | 384.2 | 363 | 346.4 | 552.9 | 61.2 | 18.7 | 103.3 | 4.1 | 168.8 | 4.6 | 853.8 | 845.4 | 760.7 | 794.7 | 661.1 | 725.8 | 592.7 | 785.8 | 709.1 | 697.1 | 190.2 | 297.6 | 331.5 | 234.8 | 381.9 | 364.9 | 269.7 | 327.1
1470 | 1318 | 559.4 | 223.76 | 261.5625 | 397.1 | 386.6 | 363.2 | 345.4 | 562 | 61.3 | 18.7 | 103.4 | 4.7 | 167.9 | 4.6 | 856.3 | 845.6 | 762.2 | 795.3 | 660.7 | 726.1 | 592.1 | 794.5 | 710.5 | 697.9 | 190.4 | 297.8 | 331.8 | 234.9 | 382.2 | 364.6 | 269.9 | 327.2
1471 | 1319 | 559.9 | 223.96 | 261.7963 | 396.5 | 386.8 | 362.6 | 345.1 | 558.4 | 61.4 | 18.7 | 103.5 | 5 | 179.2 | 4.3 | 857 | 851.4 | 755.9 | 797 | 659.7 | 726.1 | 591.6 | 794.6 | 710.8 | 698.2 | 190.7 | 297.9 | 331.9 | 235.1 | 382.1 | 364.7 | 270.1 | 327.3
1472 | 1320 | 560.7 | 224.28 | 262.1704 | 396.7 | 386 | 362.3 | 345.2 | 555.4 | 61.6 | 18.7 | 103.5 | 5.1 | 151.1 | 4 | 857.4 | 855.2 | 748.9 | 798.3 | 659.9 | 726.2 | 596.7 | 790.6 | 712.4 | 699.6 | 190.9 | 298 | 332 | 235.2 | 382.1 | 364.7 | 270.2 | 327.5
1473 | 1321 | 561.2 | 224.48 | 262.4042 | 396.2 | 385 | 361.9 | 345.2 | 565 | 61.7 | 18.7 | 103.7 | 4.7 | 170.5 | 4.2 | 860.1 | 855.8 | 764.5 | 797.9 | 662.9 | 726.6 | 595.4 | 800.9 | 712.4 | 700.6 | 191.1 | 298.1 | 332.4 | 235.4 | 382.3 | 364.9 | 270.4 | 327.8
1474 | 1322 | 560.4 | 224.16 | 262.0301 | 395.1 | 383.7 | 361 | 345.2 | 596.1 | 61.8 | 18.7 | 103.9 | 4.2 | 192.1 | 4.2 | 863.9 | 856.6 | 768.7 | 798.6 | 663.7 | 727.2 | 594 | 816.7 | 712.8 | 701.8 | 191.3 | 298.3 | 332.7 | 235.5 | 382.5 | 365 | 270.5 | 327.9
1475 | 1323 | 560.6 | 224.24 | 262.1236 | 394.4 | 382.9 | 360.7 | 345.2 | 614.3 | 62 | 18.7 | 104 | 4.4 | 172.3 | 4.3 | 866 | 854.5 | 787.7 | 800.2 | 665.7 | 727.8 | 593.3 | 823 | 712.5 | 702.7 | 191.6 | 298.4 | 332.9 | 235.7 | 382.7 | 364.7 | 270.7 | 328
1476 | 1324 | 562 | 224.8 | 262.7782 | 393.5 | 383.4 | 360.9 | 345.2 | 613 | 62.1 | 18.7 | 104.1 | 4.4 | 174.8 | 5 | 866.9 | 856.3 | 786.2 | 802.7 | 668.5 | 728.4 | 596.1 | 820.3 | 713.6 | 704.8 | 191.8 | 298.6 | 333 | 235.8 | 382.5 | 364.4 | 270.8 | 328.1
1477 | 1325 | 561.5 | 224.6 | 262.5445 | 393.3 | 384.4 | 361.2 | 344.9 | 601.2 | 62.1 | 18.7 | 104.2 | 4.3 | 198.6 | 5.3 | 863.6 | 840.4 | 760.1 | 801.9 | 666.3 | 728.3 | 591.9 | 793.9 | 711.3 | 701.6 | 192 | 298.8 | 333.1 | 236 | 382.2 | 364.4 | 270.9 | 328.2
1478 | 1326 | 560.7 | 224.28 | 262.1704 | 393.6 | 385.2 | 361 | 344.8 | 582 | 62.2 | 18.7 | 104.2 | 4.2 | 184.9 | 5.3 | 861 | 837.6 | 744.5 | 800.7 | 665.6 | 728 | 592.8 | 779.3 | 710.8 | 700.7 | 192.2 | 298.9 | 333.1 | 236.1 | 381.7 | 364.2 | 271 | 328.3
1479 | 1327 | 560.7 | 224.28 | 262.1704 | 394.2 | 386.1 | 361.1 | 344.5 | 564.6 | 62.3 | 18.7 | 104.3 | 4.6 | 174.1 | 5.1 | 857.1 | 843.3 | 741.6 | 801.9 | 664.9 | 727.7 | 598.3 | 763.8 | 711.7 | 701.7 | 192.4 | 299.1 | 332.9 | 236.3 | 381.3 | 364.8 | 271.2 | 328.5
1480 | 1328 | 561.1 | 224.44 | 262.3574 | 395.1 | 386 | 360.8 | 344.1 | 548.7 | 62.3 | 18.7 | 104.2 | 4.5 | 177.6 | 5 | 854 | 850.2 | 723.6 | 801.2 | 664.7 | 727.1 | 604.6 | 750.3 | 712 | 701.3 | 192.7 | 299.2 | 332.9 | 236.4 | 381.5 | 365.1 | 271.2 | 328.8
1481 | 1329 | 560.7 | 224.28 | 262.1704 | 395 | 386.2 | 360.1 | 343.7 | 536.2 | 62.4 | 18.7 | 104.2 | 4.4 | 179 | 5.2 | 853.5 | 850.3 | 722.3 | 803.8 | 667.3 | 726.8 | 613.5 | 740.3 | 712.7 | 702.4 | 192.9 | 299.3 | 332.8 | 236.6 | 382.1 | 365.7 | 271.3 | 329.1
1482 | 1330 | 560.1 | 224.04 | 261.8899 | 395.2 | 390 | 359.6 | 344.3 | 539.6 | 62.4 | 18.7 | 104.2 | 4.6 | 183.7 | 5 | 855.7 | 851.4 | 734.3 | 806.5 | 670.8 | 727 | 623.8 | 750 | 715.8 | 706.6 | 193.1 | 299.5 | 332.9 | 236.7 | 382.8 | 366.2 | 271.4 | 329.5
1483 | 1331 | 560.8 | 224.32 | 262.2172 | 394.1 | 391.5 | 359.8 | 345.1 | 544.7 | 62.4 | 18.7 | 104.3 | 4.3 | 189.9 | 4.6 | 858 | 858.1 | 770.4 | 808.4 | 676.9 | 727.3 | 631.8 | 759.8 | 719.2 | 710.6 | 193.3 | 299.6 | 333.1 | 236.9 | 383.4 | 367.2 | 271.5 | 329.8
1484 | 1332 | 562.5 | 225 | 263.012 | 392.8 | 391.5 | 360.1 | 345.4 | 560 | 62.4 | 18.7 | 104.4 | 4.3 | 194.2 | 4.2 | 861.8 | 856 | 793.4 | 809.2 | 682.6 | 728.2 | 636 | 783.5 | 721.8 | 713.8 | 193.5 | 299.8 | 333.3 | 237 | 383.7 | 367.6 | 271.6 | 329.9
1485 | 1333 | 562.8 | 225.12 | 263.1523 | 390.8 | 390.3 | 360.4 | 346 | 600.8 | 62.3 | 18.7 | 104.6 | 4.3 | 189.6 | 4.2 | 864.9 | 863.9 | 781.3 | 810.9 | 682.5 | 729.5 | 634.8 | 794.8 | 723.8 | 715.4 | 193.7 | 299.9 | 333.7 | 237.2 | 383.9 | 367.7 | 271.7 | 330.1
1486 | 1334 | 562.6 | 225.04 | 263.0588 | 388.9 | 388.7 | 360.2 | 346.7 | 601.4 | 62.2 | 18.7 | 104.7 | 4.7 | 192.4 | 4.3 | 868.4 | 874 | 792 | 814.3 | 684.8 | 730.1 | 633 | 809.2 | 725.4 | 717.3 | 194 | 300.1 | 333.8 | 237.3 | 384 | 367.5 | 271.8 | 330.3
1487 | 1335 | 562.1 | 224.84 | 262.825 | 389.3 | 388.2 | 359.9 | 347.7 | 607 | 62.2 | 18.7 | 104.8 | 4.5 | 189.3 | 5 | 871 | 872.3 | 799.9 | 816.2 | 688.7 | 731.4 | 636.4 | 823.9 | 728.6 | 721.7 | 194.2 | 300.2 | 333.9 | 237.4 | 384 | 367.4 | 271.9 | 330.5
1488 | 1336 | 562.4 | 224.96 | 262.9653 | 391.6 | 388.5 | 359.6 | 348.2 | 614 | 62.3 | 18.7 | 104.9 | 4.3 | 186.3 | 5.3 | 872.9 | 871.1 | 818.7 | 817.2 | 693.6 | 732.7 | 641.1 | 828.2 | 731.6 | 725.7 | 194.4 | 300.4 | 334 | 237.6 | 384 | 367.7 | 272 | 330.7
1489 | 1337 | 561.9 | 224.76 | 262.7315 | 391.6 | 388.3 | 360 | 348.4 | 612.7 | 62.3 | 18.7 | 105 | 4.1 | 185.3 | 5.4 | 872.4 | 867.9 | 821.2 | 818.8 | 697.7 | 734 | 645.2 | 828.8 | 734.6 | 728.2 | 194.6 | 300.5 | 334 | 237.7 | 384.2 | 368.1 | 272.1 | 330.9
1490 | 1338 | 562.7 | 225.08 | 263.1056 | 390.9 | 388.7 | 360.4 | 348.8 | 624.3 | 62.3 | 18.7 | 105.1 | 4.1 | 187.2 | 5.7 | 873.2 | 867.5 | 833.4 | 820.2 | 700.8 | 735.4 | 648 | 836.2 | 737.1 | 730.9 | 194.8 | 300.7 | 334.1 | 237.9 | 384.2 | 368.2 | 272.2 | 331
1491 | 1339 | 562.5 | 225 | 263.012 | 390.5 | 389.3 | 360.3 | 349.2 | 627.4 | 62.3 | 18.7 | 105.1 | 4.3 | 192 | 5.9 | 874.7 | 865.4 | 830 | 821.9 | 702.3 | 736.8 | 651.2 | 839.3 | 739.4 | 733.7 | 195 | 300.8 | 334.4 | 238 | 384.1 | 368.3 | 272.3 | 331.1
1492 | 1340 | 562.5 | 225 | 263.012 | 390.7 | 389.9 | 360 | 349.3 | 643.1 | 62.3 | 18.7 | 105.2 | 4 | 183.2 | 5.9 | 876.2 | 865.1 | 828.1 | 823 | 703.9 | 738.4 | 651.6 | 848.7 | 741.9 | 736.9 | 195.2 | 301 | 334.6 | 238.2 | 384 | 368.4 | 272.4 | 331.3
1493 | 1341 | 562.7 | 225.08 | 263.1056 | 390.3 | 390.4 | 359.6 | 349.4 | 655.3 | 62.3 | 18.7 | 105.2 | 3.7 | 181.9 | 5.9 | 877.2 | 878.9 | 815.4 | 824.5 | 702.9 | 740.1 | 652.6 | 849.7 | 744.3 | 738.7 | 195.4 | 301.1 | 334.9 | 238.3 | 384 | 368.2 | 272.5 | 331.4
1494 | 1342 | 563.3 | 225.32 | 263.3861 | 390.6 | 390.7 | 359.5 | 349.5 | 653.6 | 62.3 | 18.7 | 105.2 | 3.7 | 182.4 | 5.8 | 877.1 | 888.2 | 796.9 | 826.8 | 702.1 | 741.6 | 647 | 851.5 | 743.4 | 737.2 | 195.7 | 301.3 | 335.1 | 238.5 | 384 | 368.2 | 272.5 | 331.6
1495.1 | 1343.1 | 562.4 | 224.96 | 262.9653 | 391.1 | 390.7 | 359.9 | 349.7 | 651.7 | 62.3 | 18.7 | 105.3 | 4 | 191.6 | 5.7 | 879.2 | 884.2 | 801.6 | 827.3 | 703.1 | 743.2 | 643.8 | 852 | 742.5 | 739.3 | 195.9 | 301.4 | 335.4 | 238.6 | 384 | 368.3 | 272.7 | 331.8
1496.1 | 1344.1 | 561.9 | 224.76 | 262.7315 | 391.6 | 389.7 | 360.5 | 349.7 | 655 | 62.2 | 18.7 | 105.3 | 4.3 | 204.5 | 6 | 876.6 | 882.4 | 789.8 | 828.9 | 700.5 | 744.3 | 639.7 | 835.5 | 741.1 | 736.8 | 196.1 | 301.6 | 335.8 | 238.8 | 384 | 368 | 272.7 | 331.9
1497.1 | 1345.1 | 563.5 | 225.4 | 263.4796 | 391.6 | 388.5 | 360.7 | 349.3 | 631.4 | 62.1 | 18.7 | 105.3 | 4.4 | 191.9 | 5.8 | 877.4 | 876.6 | 795 | 828.7 | 701.6 | 745.1 | 639.5 | 828.6 | 741.6 | 737.8 | 196.3 | 301.7 | 335.6 | 238.9 | 384.1 | 368.1 | 272.8 | 332.1
1498.1 | 1346.1 | 562.7 | 225.08 | 263.1056 | 390.9 | 388.2 | 360.3 | 349.6 | 620.7 | 62 | 18.7 | 105.3 | 4.1 | 186.6 | 5.5 | 878.7 | 869.5 | 810.6 | 829.7 | 705.6 | 746.4 | 648.8 | 828.8 | 743.6 | 741.3 | 196.5 | 301.9 | 335.7 | 239 | 384.3 | 369.3 | 273 | 332.5
1499.1 | 1347.1 | 562.2 | 224.88 | 262.8718 | 391 | 388.6 | 360.4 | 349.8 | 609.4 | 62 | 18.7 | 105.3 | 4.1 | 189.6 | 5.4 | 879.4 | 875.7 | 804.4 | 832.3 | 705.4 | 758.7 | 638.8 | 831.4 | 731.1 | 741.8 | 196.7 | 302.1 | 335.6 | 239.2 | 384.4 | 369.3 | 273 | 332.7
1500.1 | 1348.1 | 562.4 | 224.96 | 262.9653 | 391 | 388.6 | 360.5 | 350.1 | 611.5 | 62.1 | 18.7 | 105.3 | 4.3 | 185.3 | 4.9 | 878 | 884.2 | 779.7 | 832.5 | 701.7 | 748.6 | 642.1 | 829.9 | 744.2 | 740.3 | 196.9 | 302.2 | 335.8 | 239.3 | 384.5 | 368.7 | 273.2 | 332.8
1501.1 | 1349.1 | 563.2 | 225.28 | 263.3393 | 390.9 | 388.9 | 360.1 | 350.1 | 609.2 | 62.2 | 18.7 | 105.3 | 4.1 | 179.9 | 4.4 | 876.4 | 875.3 | 774 | 831 | 699.5 | 749.3 | 635.6 | 825.9 | 741.6 | 737.4 | 197.1 | 302.4 | 336.4 | 239.5 | 385.1 | 368.4 | 273.2 | 332.9
1502.1 | 1350.1 | 563.5 | 225.4 | 263.4796 | 390.8 | 389.8 | 359.5 | 350.1 | 608.6 | 62.3 | 18.7 | 105.3 | 4.2 | 178.6 | 3.7 | 877 | 861.5 | 784.7 | 830.3 | 700.3 | 749.8 | 630.9 | 806.3 | 739.1 | 735.1 | 197.3 | 302.6 | 336.8 | 239.6 | 385.2 | 368.7 | 273.3 | 333
1503.1 | 1351.1 | 562.6 | 225.04 | 263.0588 | 391.8 | 390.3 | 359.4 | 350.5 | 606.6 | 62.5 | 18.6 | 105.4 | 3.9 | 175.1 | 3.2 | 876.2 | 851.6 | 786.1 | 828.7 | 700.2 | 750.2 | 626.9 | 790.7 | 736.3 | 732.2 | 197.5 | 302.8 | 337 | 239.8 | 385.3 | 369.2 | 273.3 | 333.1
1504.1 | 1352.1 | 561.4 | 224.56 | 262.4977 | 392.7 | 391.7 | 359.7 | 350.3 | 607.3 | 62.7 | 18.6 | 105.5 | 4 | 164.9 | 3.3 | 876.8 | 840.6 | 800.9 | 827.7 | 701.1 | 750.4 | 622.3 | 792.3 | 733.8 | 731.2 | 197.7 | 303 | 337.2 | 239.9 | 385.5 | 369.3 | 273.5 | 333.2
1505.1 | 1353.1 | 563.8 | 225.52 | 263.6199 | 393.3 | 392.7 | 360.4 | 350.2 | 623.1 | 62.8 | 18.6 | 105.5 | 4.1 | 171.6 | 3.8 | 879.4 | 837.7 | 801.3 | 828.2 | 700.4 | 751.3 | 620.8 | 808.3 | 733.2 | 733.2 | 197.9 | 303.2 | 337.6 | 240.1 | 385.8 | 369.4 | 273.6 | 333.3
1506.1 | 1354.1 | 563.9 | 225.56 | 263.6666 | 393.7 | 393.5 | 361.1 | 350.6 | 635.7 | 62.8 | 18.6 | 105.5 | 4.3 | 188.5 | 4.2 | 880.7 | 834.5 | 809.4 | 826.7 | 701.6 | 752 | 617.9 | 815.2 | 732.4 | 732.7 | 198.1 | 303.4 | 338 | 240.2 | 386.2 | 369.3 | 273.7 | 333.5
1507.1 | 1355.1 | 563.3 | 225.32 | 263.3861 | 393.5 | 394.6 | 361.9 | 351.1 | 645.2 | 62.8 | 18.7 | 105.5 | 4.7 | 185.6 | 4.4 | 883.8 | 840.7 | 825 | 826.3 | 704.9 | 753.1 | 619.2 | 827.3 | 733.9 | 735.2 | 198.3 | 303.6 | 338.3 | 240.4 | 386.6 | 369.1 | 273.8 | 333.6
1508.1 | 1356.1 | 561.9 | 224.76 | 262.7315 | 392.9 | 395.5 | 362.7 | 351.5 | 647.2 | 62.8 | 18.6 | 105.5 | 4.9 | 171.5 | 4.8 | 885.7 | 846.6 | 834.9 | 828.1 | 708 | 754.2 | 622.1 | 832.4 | 735.8 | 736.7 | 198.5 | 303.8 | 338.3 | 240.5 | 387.1 | 369.2 | 273.9 | 333.7
1509.1 | 1357.1 | 564.2 | 225.68 | 263.8069 | 392.7 | 395.5 | 362.8 | 351.9 | 654.5 | 62.8 | 18.6 | 105.5 | 4.6 | 181 | 4.6 | 886 | 847.1 | 826.7 | 827.4 | 709.1 | 755.2 | 622.7 | 839.5 | 736.8 | 737.7 | 198.7 | 304 | 338.5 | 240.7 | 387.2 | 369.5 | 274.1 | 333.9
1510.1 | 1358.1 | 564.7 | 225.88 | 264.0407 | 393 | 396 | 363.6 | 352.3 | 663.2 | 62.9 | 18.6 | 105.5 | 4.4 | 185.3 | 4.2 | 886.4 | 842.8 | 823.7 | 826.9 | 708.9 | 755.9 | 621 | 839 | 736.2 | 737.3 | 198.9 | 304.3 | 339 | 240.8 | 387.6 | 369.4 | 274.3 | 334
1511.1 | 1359.1 | 564 | 225.6 | 263.7134 | 393.5 | 396.5 | 363.8 | 352.6 | 672.6 | 63 | 18.6 | 105.5 | 4.3 | 177.7 | 3.6 | 884.8 | 833.6 | 801.9 | 823.3 | 704.5 | 756.2 | 617.8 | 821.2 | 734 | 734.1 | 199.1 | 304.5 | 339.5 | 241 | 388.2 | 369.1 | 274.5 | 334
1512.1 | 1360.1 | 563.8 | 225.52 | 263.6199 | 393.9 | 396.4 | 363.9 | 353.3 | 661.3 | 63.1 | 18.6 | 105.4 | 4 | 178.6 | 3.3 | 884.8 | 828.5 | 798.4 | 819.7 | 703.8 | 756.5 | 615 | 817.9 | 731.9 | 734.2 | 199.3 | 304.7 | 339.8 | 241.1 | 388.8 | 369.2 | 274.7 | 334.1
1513.1 | 1361.1 | 563.6 | 225.44 | 263.5264 | 394.2 | 397.4 | 364.6 | 354.1 | 667.5 | 63.1 | 18.6 | 105.4 | 4 | 192.7 | 3.8 | 886.8 | 838.6 | 798.6 | 819.7 | 705.6 | 757.3 | 617.1 | 828.5 | 732.6 | 736.8 | 199.5 | 304.9 | 340.1 | 241.3 | 389.2 | 369.8 | 274.9 | 334.2
1514.1 | 1362.1 | 564.3 | 225.72 | 263.8537 | 395.7 | 399.1 | 365.2 | 354.7 | 679.1 | 62.8 | 18.6 | 105.5 | 4 | 191.8 | 5.2 | 887.9 | 834.4 | 792 | 817.7 | 703.5 | 758.1 | 616.2 | 832.9 | 732.8 | 737.7 | 199.7 | 305.1 | 340.5 | 241.4 | 389.6 | 369.8 | 275.2 | 334.3
1515.1 | 1363.1 | 564.3 | 225.72 | 263.8537 | 396.9 | 399.9 | 365.9 | 355.5 | 684.1 | 62.7 | 18.6 | 105.6 | 4 | 178.5 | 6 | 885.1 | 823.8 | 777.7 | 815.8 | 700.3 | 758.4 | 612.8 | 821.2 | 730.5 | 735.5 | 199.9 | 305.4 | 341.1 | 241.6 | 390 | 369.6 | 275.4 | 334.5
1516.1 | 1364.1 | 563.3 | 225.32 | 263.3861 | 397.4 | 400.9 | 366.6 | 356.8 | 676.1 | 62.8 | 18.6 | 105.6 | 3.9 | 189.2 | 6.5 | 875.7 | 797.5 | 733.7 | 809.6 | 694.2 | 758.3 | 607.8 | 799.5 | 727.2 | 730.9 | 200.1 | 305.7 | 341.4 | 241.7 | 390.5 | 369.7 | 275.7 | 334.6
1517.1 | 1365.1 | 562.4 | 224.96 | 262.9653 | 398.9 | 402.2 | 366.7 | 358.1 | 641.4 | 62.8 | 18.6 | 105.6 | 4.2 | 180.7 | 6.8 | 868.7 | 777.7 | 717.7 | 804 | 690.7 | 757.2 | 601.8 | 773.2 | 723.4 | 726.6 | 200.3 | 305.9 | 341.2 | 241.9 | 391 | 369.7 | 276 | 334.7
1518.1 | 1366.1 | 562.8 | 225.12 | 263.1523 | 401.2 | 402.9 | 367.2 | 359.4 | 612.5 | 62.9 | 18.6 | 105.5 | 3.9 | 189.5 | 7 | 863.7 | 765.8 | 698.3 | 799.1 | 687.1 | 756 | 594.7 | 757.5 | 719.8 | 723.2 | 200.5 | 306.1 | 341.2 | 242 | 391.4 | 369.7 | 276.2 | 334.9
1519.1 | 1367.1 | 564.6 | 225.84 | 263.9939 | 403.6 | 403.8 | 367.5 | 360.5 | 589.4 | 62.9 | 18.6 | 105.5 | 3.9 | 188.5 | 6.9 | 860.6 | 762.2 | 685.7 | 794.9 | 683.7 | 754.8 | 587.7 | 741.2 | 717.1 | 719.4 | 200.7 | 306.3 | 341.1 | 242.1 | 392 | 369.4 | 276.4 | 335.1
1520.1 | 1368.1 | 564.6 | 225.84 | 263.9939 | 405.5 | 402.8 | 367.2 | 361.1 | 582.2 | 62.9 | 18.6 | 105.4 | 4.3 | 178.6 | 6.4 | 863.4 | 783.8 | 689.4 | 796.7 | 682.7 | 754.1 | 589.6 | 760.3 | 718.1 | 720.7 | 200.9 | 306.6 | 341.1 | 242.3 | 392.4 | 369.4 | 276.7 | 335.3
1521.1 | 1369.1 | 562.9 | 225.16 | 263.1991 | 405.8 | 401.6 | 367.4 | 360.8 | 593.2 | 62.9 | 18.6 | 105.4 | 4.3 | 184.7 | 6.4 | 868.6 | 807.8 | 709.1 | 799.8 | 683.5 | 754 | 591.6 | 785 | 719.9 | 722.8 | 201.1 | 306.8 | 341.3 | 242.4 | 392.7 | 369.7 | 276.9 | 335.4
1522.1 | 1370.1 | 563 | 225.2 | 263.2458 | 405.5 | 402 | 367.8 | 360.3 | 604.3 | 62.7 | 18.6 | 105.5 | 4.5 | 184.9 | 6.2 | 872.6 | 821 | 726.5 | 802 | 683.7 | 754.4 | 594.5 | 797.6 | 721.3 | 724.4 | 201.3 | 307 | 341.4 | 242.6 | 392.5 | 369.5 | 277.1 | 335.6
1523.1 | 1371.1 | 563.6 | 225.44 | 263.5264 | 405.1 | 403.6 | 368.2 | 360 | 618.8 | 62.6 | 18.6 | 105.5 | 4.7 | 181.6 | 7 | 872.7 | 811.7 | 712.5 | 800.1 | 682.6 | 754.6 | 593.1 | 801.2 | 720.3 | 722.5 | 201.5 | 307.1 | 341.7 | 242.8 | 392.3 | 369.3 | 277.3 | 335.6
1524.1 | 1372.1 | 563.8 | 225.52 | 263.6199 | 404.4 | 403.8 | 368.7 | 359.4 | 621.7 | 62.7 | 18.6 | 105.5 | 4.6 | 189.7 | 7.5 | 864.7 | 788.3 | 680 | 793.9 | 676.8 | 754.1 | 587.6 | 771.8 | 717 | 717.7 | 201.7 | 307.3 | 342.3 | 242.9 | 392.5 | 369 | 277.6 | 335.7
1525.1 | 1373.1 | 563.5 | 225.4 | 263.4796 | 405.5 | 403.1 | 369.5 | 359.2 | 594.7 | 62.7 | 18.6 | 105.6 | 4.5 | 184.4 | 7.4 | 859.6 | 785.4 | 680.2 | 790.9 | 675.5 | 752.3 | 584.3 | 740.1 | 713.1 | 713.7 | 201.9 | 307.5 | 342 | 243.1 | 392.4 | 368.9 | 277.8 | 335.9
1526.1 | 1374.1 | 563.9 | 225.56 | 263.6666 | 406.9 | 403.8 | 370.1 | 359.6 | 581.9 | 62.8 | 18.6 | 105.7 | 4.7 | 185.8 | 6.8 | 862.8 | 813 | 696.9 | 795.2 | 678.5 | 751.4 | 589.8 | 757 | 714 | 715.9 | 202.1 | 307.7 | 341.9 | 243.2 | 392.8 | 369.2 | 278.1 | 336.1
1527.1 | 1375.1 | 564 | 225.6 | 263.7134 | 405.8 | 404.3 | 370 | 359.8 | 589.3 | 62.9 | 18.6 | 105.8 | 4.5 | 191.8 | 6.1 | 864.7 | 813.9 | 709.1 | 796.2 | 678.5 | 748.5 | 591.4 | 781.4 | 711.8 | 717.6 | 202.3 | 307.9 | 342 | 243.4 | 393.2 | 369.7 | 278.3 | 336.3
1528.1 | 1376.1 | 563.5 | 225.4 | 263.4796 | 405.1 | 404.4 | 370.1 | 360.1 | 599.8 | 62.9 | 18.6 | 105.9 | 4.3 | 180.9 | 5.6 | 866.8 | 820 | 727.6 | 797.7 | 678.9 | 748.7 | 596.1 | 791.4 | 714.7 | 717.1 | 202.5 | 308.1 | 342.3 | 243.5 | 392.9 | 370.1 | 278.5 | 336.5
1529.1 | 1377.1 | 564.2 | 225.68 | 263.8069 | 405.6 | 404.2 | 370.1 | 359.8 | 602.2 | 63 | 18.6 | 106 | 4.5 | 169 | 6.4 | 862.4 | 804.8 | 714.6 | 793.7 | 675.4 | 749.9 | 593.2 | 764.2 | 712.4 | 712.8 | 202.7 | 308.3 | 342.6 | 243.7 | 392.6 | 370 | 278.8 | 336.5
1530.1 | 1378.1 | 564.2 | 225.68 | 263.8069 | 406.2 | 402.7 | 369.7 | 358.8 | 586.7 | 63 | 18.6 | 106.1 | 4.6 | 174.7 | 6.9 | 858.7 | 794.1 | 693.4 | 790.8 | 671.6 | 748.6 | 588.3 | 739.1 | 708.6 | 708.6 | 202.9 | 308.5 | 342.9 | 243.8 | 392.4 | 370.2 | 279 | 336.6
1531.1 | 1379.1 | 565.2 | 226.08 | 264.2745 | 408.2 | 400.6 | 370.1 | 357.7 | 590.9 | 63.1 | 18.6 | 106.2 | 4.7 | 162.9 | 7.6 | 858.9 | 805.2 | 684 | 790.6 | 671 | 747.6 | 587.3 | 748.5 | 707.4 | 708.4 | 203.1 | 308.7 | 343 | 244 | 392.3 | 370.3 | 279.2 | 336.8
1532.1 | 1380.1 | 563.6 | 225.44 | 263.5264 | 407.9 | 398.6 | 370.4 | 357.1 | 597.5 | 63 | 18.6 | 106.3 | 4.5 | 181.3 | 8.1 | 858.8 | 807.3 | 688.2 | 792.3 | 670.8 | 747 | 592 | 738.7 | 707.8 | 708 | 203.3 | 308.8 | 343.1 | 244.1 | 392.2 | 370.6 | 279.4 | 337.1
1533.1 | 1381.1 | 563.5 | 225.4 | 263.4796 | 408.5 | 396.5 | 370.6 | 356.9 | 586.5 | 62.8 | 18.6 | 106.3 | 4.4 | 173.4 | 8.7 | 862.2 | 810.8 | 699.2 | 794 | 673 | 747.4 | 591.9 | 744.9 | 707.6 | 709.4 | 203.5 | 309 | 343 | 244.2 | 391.8 | 370.8 | 279.7 | 337.3
1534.1 | 1382.1 | 564.1 | 225.64 | 263.7602 | 409.2 | 395.6 | 370.5 | 356.6 | 587.6 | 62.7 | 18.6 | 106.3 | 4.7 | 173.3 | 8.7 | 862.2 | 801.6 | 689.5 | 792.5 | 670.9 | 747.3 | 590.1 | 741.5 | 705.4 | 706.3 | 203.7 | 309.2 | 343.4 | 244.4 | 391.5 | 370.8 | 279.9 | 337.4
1535.1 | 1383.1 | 564.9 | 225.96 | 264.1342 | 409.7 | 395 | 370.5 | 355.7 | 590.2 | 62.7 | 18.6 | 106.4 | 3.5 | 169.1 | 8.5 | 864.2 | 805.8 | 697.5 | 792.2 | 670.8 | 747.1 | 589.1 | 754.2 | 704.4 | 706.4 | 203.9 | 309.4 | 343.7 | 244.5 | 391.3 | 370.6 | 280.1 | 337.5
1536.1 | 1384.1 | 564.5 | 225.8 | 263.9472 | 409 | 394.7 | 370.5 | 354.8 | 594.7 | 62.7 | 18.6 | 106.4 | 4 | 164.5 | 8.3 | 862.4 | 795.1 | 698.3 | 790 | 669.3 | 746.2 | 589.4 | 752.8 | 703.4 | 704.7 | 204.1 | 309.6 | 343.8 | 244.6 | 390.9 | 370.4 | 280.3 | 337.6
1537.1 | 1385.1 | 565.4 | 226.16 | 264.368 | 409.8 | 395 | 370.6 | 354.3 | 594.6 | 62.7 | 18.6 | 106.6 | 4.1 | 164.4 | 8.2 | 862.4 | 793.6 | 736.2 | 789.5 | 671.2 | 745.5 | 587.7 | 744.2 | 701.4 | 702.6 | 204.3 | 309.7 | 344.1 | 244.8 | 390.8 | 370.2 | 280.4 | 337.6
1538.1 | 1386.1 | 564 | 225.6 | 263.7134 | 410.3 | 395.7 | 370.9 | 353.8 | 585.6 | 62.8 | 18.6 | 106.6 | 4.1 | 153.8 | 7.7 | 862.5 | 801.1 | 739.6 | 791.9 | 672.8 | 744.2 | 587.7 | 734.2 | 699.2 | 701.3 | 204.5 | 309.9 | 344.4 | 244.9 | 390.7 | 369.9 | 280.6 | 337.7
1539.1 | 1387.1 | 564.7 | 225.88 | 264.0407 | 410.3 | 396 | 371.6 | 353.6 | 579.7 | 62.8 | 18.6 | 106.8 | 4 | 155.1 | 7.4 | 861.4 | 804.1 | 730.2 | 791.4 | 669.8 | 743.4 | 588.3 | 740.4 | 698.8 | 701 | 204.7 | 310.1 | 344.6 | 245.1 | 390.5 | 369.9 | 280.7 | 337.8
1540.1 | 1388.1 | 565.6 | 226.24 | 264.4615 | 410.4 | 395.4 | 371.7 | 353.8 | 579.1 | 62.8 | 18.6 | 106.9 | 3.9 | 186.5 | 7.4 | 862 | 810.2 | 728.3 | 792 | 670.9 | 741.8 | 587.8 | 731.8 | 698.2 | 699.9 | 204.9 | 310.4 | 344.8 | 245.2 | 390.6 | 370 | 280.9 | 337.9
1541.1 | 1389.1 | 564.9 | 225.96 | 264.1342 | 411.2 | 395.5 | 371.7 | 354.5 | 565.2 | 62.9 | 18.6 | 107 | 4.2 | 162.3 | 6.7 | 857.7 | 801 | 715.1 | 790 | 668.6 | 739.5 | 586.2 | 710 | 696.1 | 697.4 | 205 | 310.6 | 344.9 | 245.3 | 390.5 | 370.3 | 281.1 | 338.1
1542.1 | 1390.1 | 565 | 226 | 264.181 | 410.9 | 395.3 | 371.5 | 354.9 | 552.8 | 62.9 | 18.6 | 107.1 | 4.2 | 165.5 | 7.1 | 852.9 | 795.1 | 722.1 | 788.7 | 668.8 | 736.4 | 585.7 | 702.1 | 694.4 | 695.2 | 205.2 | 310.8 | 344.9 | 245.5 | 390.2 | 370.5 | 281.2 | 338.2
1543.1 | 1391.1 | 564.4 | 225.76 | 263.9004 | 409.7 | 395.7 | 371.6 | 354.4 | 552.4 | 62.9 | 18.6 | 107.1 | 4.2 | 160 | 7.5 | 855.4 | 809.4 | 738.7 | 790.4 | 671.3 | 735 | 586.6 | 724.5 | 694.4 | 696.8 | 205.4 | 311 | 344.9 | 245.6 | 389.3 | 370.9 | 281.5 | 338.3
1544.1 | 1392.1 | 563.5 | 225.4 | 263.4796 | 409.4 | 396 | 371.6 | 353.5 | 547.5 | 62.8 | 18.6 | 107.2 | 4.5 | 166.5 | 7.8 | 858.4 | 831.2 | 755.7 | 792.9 | 675.1 | 733.7 | 596 | 729.1 | 697.3 | 701.1 | 205.6 | 311.1 | 344.9 | 245.7 | 388.8 | 371.2 | 281.6 | 338.5
1545.1 | 1393.1 | 564.5 | 225.8 | 263.9472 | 407.9 | 397.4 | 371.6 | 352.4 | 554.9 | 62.7 | 18.6 | 107.3 | 4.4 | 177.7 | 8.1 | 864.8 | 844.1 | 777.1 | 795.8 | 679.3 | 732.9 | 602.1 | 750.9 | 700.3 | 705.7 | 205.8 | 311.3 | 344.9 | 245.9 | 389.1 | 371.3 | 281.8 | 338.7
1546.1 | 1394.1 | 564 | 225.6 | 263.7134 | 406.6 | 399.3 | 371.9 | 351.6 | 565.7 | 62.7 | 18.6 | 107.4 | 4 | 150.7 | 8.3 | 867.2 | 843.9 | 788.1 | 798.3 | 680.1 | 732.7 | 602.2 | 761.4 | 701.3 | 706.1 | 206 | 311.5 | 345.3 | 246 | 389.4 | 371.8 | 282 | 338.8
1547.1 | 1395.1 | 563.1 | 225.24 | 263.2926 | 407.6 | 400.2 | 372.1 | 351.5 | 582.9 | 62.7 | 18.6 | 107.5 | 4.5 | 157.9 | 8.4 | 868.9 | 838.2 | 781.6 | 799.9 | 680.9 | 732.9 | 601 | 776.3 | 701.6 | 707.3 | 206.2 | 311.6 | 345.5 | 246.1 | 389.8 | 372.2 | 282.3 | 339
1548.1 | 1396.1 | 563.7 | 225.48 | 263.5731 | 407 | 400.3 | 372.2 | 352 | 586.1 | 62.8 | 18.6 | 107.6 | 4.2 | 167.1 | 7.9 | 867.3 | 830.7 | 769.3 | 798.3 | 680.2 | 732.7 | 598.9 | 767.6 | 700.1 | 704.5 | 206.4 | 311.8 | 345.7 | 246.3 | 390.1 | 372.4 | 282.5 | 339.3
1549.1 | 1397.1 | 563.7 | 225.48 | 263.5731 | 406.3 | 399.8 | 372.4 | 352.3 | 577.7 | 62.9 | 18.6 | 107.7 | 4.4 | 154.1 | 7.8 | 864.3 | 817.8 | 754.1 | 798 | 679.1 | 732.1 | 596.2 | 751.7 | 697.7 | 702.5 | 206.6 | 312 | 346.1 | 246.4 | 390.4 | 372.5 | 282.7 | 339.4
1550.1 | 1398.1 | 563.8 | 225.52 | 263.6199 | 406.1 | 399.1 | 372.4 | 352.8 | 574.3 | 62.9 | 18.6 | 107.8 | 4.2 | 174.9 | 8 | 866.7 | 833 | 757.1 | 799.2 | 680.2 | 731.8 | 601.4 | 763.2 | 698.5 | 705 | 206.8 | 312.1 | 346 | 246.5 | 390.2 | 372.7 | 282.9 | 339.6
1551.1 | 1399.1 | 360.1 | 144.04 | 168.3745 | 405.7 | 398.6 | 372.4 | 353.3 | 583.6 | 63 | 18.6 | 107.9 | 4.6 | 176.8 | 7.6 | 867.2 | 825.7 | 757 | 799.5 | 680.3 | 731.4 | 598.6 | 764.7 | 698.2 | 703.8 | 207 | 312.3 | 346.3 | 246.7 | 390.1 | 373 | 283.1 | 339.7
1552.1 | 1400.1 | -5.5 | 0 | 0 | 405 | 399.5 | 371.6 | 353.3 | 584.2 | 63.2 | 18.6 | 107.9 | 4 | 173.1 | 7.1 | 864.3 | 819.7 | 751.6 | 799.1 | 680.2 | 730.7 | 597.2 | 757.6 | 696.9 | 703 | 207.2 | 312.4 | 346.6 | 246.8 | 390.1 | 373.2 | 283.3 | 339.8
1553.1 | 1401.1 | -6.9 | 0 | 0 | 403.5 | 399.6 | 370.9 | 353 | 566.4 | 63.3 | 18.6 | 108 | 3.8 | 166.6 | 7.3 | 848.7 | 779.4 | 718.5 | 790 | 675 | 729.1 | 590.8 | 715.1 | 692 | 696.6 | 207.3 | 312.6 | 346.1 | 247 | 389.9 | 373 | 283.5 | 340
1554.1 | 1402.1 | -6.9 | 0 | 0 | 401.5 | 400 | 369.3 | 353.1 | 536.6 | 63.4 | 18.6 | 108.1 | 3.7 | 170.5 | 7.8 | 829.5 | 739.8 | 662.1 | 778.6 | 666.9 | 726.6 | 581.6 | 674.4 | 687.3 | 690.1 | 207.5 | 312.7 | 345.4 | 247.1 | 389.2 | 372.2 | 283.7 | 339.9
1555.1 | 1403.1 | -6.9 | 0 | 0 | 399.3 | 399.2 | 367.2 | 352.6 | 506.6 | 63.4 | 18.6 | 108.1 | 3.9 | 165.4 | 7.7 | 812.4 | 706.8 | 618 | 765.5 | 659.9 | 723.6 | 573.8 | 637.8 | 682.5 | 684.2 | 207.7 | 312.8 | 344.9 | 247.2 | 388.2 | 371.1 | 283.9 | 339.7
1556.1 | 1404.1 | -6.9 | 0 | 0 | 395.7 | 396.4 | 364.7 | 351.4 | 484.9 | 63.4 | 18.6 | 108.2 | 3.6 | 153.6 | 6.8 | 796.7 | 673 | 581.8 | 754 | 654.3 | 720.7 | 566.2 | 607.2 | 678.8 | 678 | 207.9 | 312.9 | 344.6 | 247.4 | 387 | 369.6 | 284.1 | 339.6
1557.1 | 1405.1 | -6.9 | 0 | 0 | 391.6 | 392.5 | 362.1 | 349.7 | 469 | 63.5 | 18.6 | 108.2 | 3.5 | 148.2 | 6.1 | 783.8 | 649 | 552.4 | 746 | 648.9 | 728.1 | 522.5 | 584.3 | 627.2 | 672.2 | 208.1 | 312.9 | 344.4 | 247.5 | 385.8 | 368.3 | 284.2 | 339.3
1558.1 | 1406.1 | -6.9 | 0 | 0 | 388.4 | 388.5 | 359.4 | 347.6 | 456.2 | 63.6 | 18.6 | 108.2 | 3.8 | 152.1 | 5.3 | 772.2 | 628.6 | 521.8 | 736.1 | 643.4 | 714.1 | 551.5 | 555.4 | 670.1 | 666.4 | 208.3 | 313 | 344.2 | 247.6 | 384.5 | 367.1 | 284.4 | 339.1
1559.1 | 1407.1 | -6.9 | 0 | 0 | 385 | 385.2 | 356.3 | 345.2 | 444.5 | 63.5 | 18.6 | 108 | 3.8 | 151.5 | 4.9 | 759.8 | 608.8 | 496.3 | 725.7 | 637.9 | 710.2 | 544.4 | 532.6 | 665.5 | 660.9 | 208.4 | 313 | 344 | 247.8 | 383.1 | 365.2 | 284.5 | 338.7
1560.1 | 1408.1 | -6.9 | 0 | 0 | 381.9 | 382.7 | 353.1 | 342.7 | 433.6 | 63.6 | 18.6 | 107.8 | 3.8 | 149.2 | 4.8 | 747.6 | 592.4 | 470 | 715.9 | 632.5 | 706.2 | 538.4 | 514.2 | 661.2 | 655.7 | 208.6 | 313 | 343.8 | 247.9 | 381.6 | 363.2 | 284.7 | 338.4
1561.1 | 1409.1 | -6.8 | 0 | 0 | 378.5 | 379.6 | 349.9 | 340.1 | 422.7 | 63.5 | 18.6 | 107.5 | 3.6 | 156 | 6.2 | 738.5 | 575.9 | 447.9 | 708.7 | 626.5 | 702.8 | 533.2 | 496 | 656.9 | 650.3 | 208.8 | 313.1 | 343.5 | 248.1 | 380.1 | 360.8 | 284.8 | 338
1562.1 | 1410.1 | -6.8 | 0 | 0 | 374.9 | 375.9 | 347 | 337.9 | 412.7 | 63.2 | 18.6 | 107.2 | 3.8 | 159.2 | 6.8 | 731.2 | 563.3 | 426.6 | 701.5 | 621.2 | 696.7 | 526.1 | 479.8 | 649.7 | 645.1 | 209 | 313 | 343.2 | 248.2 | 378.9 | 357.9 | 285 | 337.6
1563.1 | 1411.1 | -6.8 | 0 | 0 | 371.6 | 372.3 | 344.5 | 335.8 | 403.8 | 63.1 | 18.6 | 106.7 | 3.6 | 163.8 | 7.1 | 723.5 | 550.1 | 407.5 | 695 | 615.8 | 696.8 | 522.9 | 467.4 | 648.6 | 640.3 | 209.2 | 313 | 342.9 | 248.3 | 377.7 | 355 | 285.1 | 337.1
1564.1 | 1412.1 | -6.8 | 0 | 0 | 368.3 | 368.7 | 342 | 333.8 | 395.4 | 63 | 18.6 | 106.3 | 3.7 | 163.5 | 7.3 | 716.5 | 539.2 | 391.9 | 687.3 | 611.4 | 693.5 | 518.2 | 454.8 | 645.2 | 635.5 | 209.4 | 313 | 342.7 | 248.4 | 376.3 | 352.8 | 285.2 | 336.7
1565.1 | 1413.1 | -6.8 | 0 | 0 | 365.5 | 366.2 | 339.4 | 331.8 | 388.2 | 63 | 18.6 | 105.8 | 3.8 | 168.1 | 7.2 | 709.9 | 529.3 | 375.7 | 681.3 | 606.3 | 689.5 | 514.4 | 442.4 | 642.1 | 630.7 | 209.6 | 313 | 342.5 | 248.6 | 375 | 350.9 | 285.3 | 336.3
1566.1 | 1414.1 | -6.8 | 0 | 0 | 362.4 | 363.3 | 337 | 329.7 | 381.7 | 63 | 18.6 | 105.4 | 3.8 | 163.8 | 6.8 | 702.5 | 518 | 362.5 | 673.2 | 601.7 | 686.3 | 509.8 | 430.4 | 638.6 | 626 | 209.7 | 312.9 | 342.2 | 248.7 | 373.7 | 348.6 | 285.5 | 335.9
1567.1 | 1415.1 | -6.8 | 0 | 0 | 359.6 | 359.9 | 334.5 | 327.5 | 375.4 | 62.9 | 18.6 | 104.9 | 3.8 | 153 | 6.3 | 696.8 | 507.7 | 349.8 | 666.8 | 597.4 | 682.5 | 505.5 | 421.9 | 634.8 | 622 | 209.9 | 312.8 | 342 | 248.8 | 372.3 | 346.1 | 285.6 | 335.5
1568.1 | 1416.1 | -6.8 | 0 | 0 | 356.8 | 356.9 | 331.9 | 325.2 | 369.5 | 62.9 | 18.6 | 104.5 | 3.4 | 149.3 | 5.5 | 691.1 | 499.2 | 337.1 | 660.3 | 593 | 678.6 | 500.9 | 414.4 | 630.7 | 617.6 | 210.1 | 312.8 | 341.8 | 249 | 370.7 | 343.7 | 285.7 | 335
1569.1 | 1417.1 | -6.8 | 0 | 0 | 354.6 | 354.7 | 329.4 | 322.9 | 364.6 | 62.9 | 18.6 | 104 | 3.6 | 152.7 | 4.9 | 684.8 | 490.5 | 325.8 | 653.9 | 588.4 | 675.1 | 497.3 | 405.2 | 627.2 | 613.1 | 210.3 | 312.7 | 341.5 | 249.1 | 369.3 | 341.4 | 285.8 | 334.6
1570.1 | 1418.1 | -6.8 | 0 | 0 | 352.2 | 352.5 | 327 | 320.9 | 360.6 | 63 | 18.5 | 103.6 | 3.3 | 157.3 | 4.5 | 678.9 | 483.4 | 317.3 | 645.9 | 584.5 | 671.4 | 494 | 396.1 | 623.6 | 609.2 | 210.5 | 312.7 | 341.3 | 249.2 | 368 | 339.5 | 285.9 | 334.2
1571.1 | 1419.1 | -6.8 | 0 | 0 | 349.9 | 350.1 | 324.8 | 319.1 | 356.4 | 63.1 | 18.6 | 103.2 | 3.2 | 163.6 | 4.3 | 672.7 | 476.8 | 308.9 | 638.4 | 580.9 | 667.8 | 491.4 | 387.7 | 619.8 | 605.2 | 210.7 | 312.6 | 341 | 249.3 | 366.7 | 337.6 | 286 | 333.8
1572.1 | 1420.1 | -6.8 | 0 | 0 | 348 | 347.8 | 322.7 | 317.2 | 353.1 | 63.1 | 18.6 | 102.8 | 3 | 166.3 | 4.5 | 667.4 | 470.6 | 300.6 | 634 | 577.6 | 664.2 | 487.7 | 381.6 | 616.8 | 601.1 | 210.9 | 312.5 | 340.8 | 249.4 | 365.5 | 335.4 | 286.2 | 333.4
1573.1 | 1421.1 | -6.8 | 0 | 0 | 346.2 | 345.9 | 320.6 | 315.4 | 350.3 | 63.1 | 18.5 | 102.3 | 3.1 | 172.3 | 4.6 | 662.2 | 465 | 293.1 | 628.5 | 573.9 | 661 | 484.4 | 373.8 | 613.2 | 597.1 | 211.1 | 312.4 | 340.6 | 249.5 | 363.8 | 333.4 | 286.2 | 332.9
1574.1 | 1422.1 | -6.8 | 0 | 0 | 344.3 | 343.9 | 318.6 | 313.7 | 348.2 | 63.1 | 18.6 | 101.9 | 3.1 | 174 | 5.1 | 657.3 | 460 | 286.8 | 622.7 | 570.6 | 657.7 | 480.4 | 368.9 | 608.4 | 593.5 | 211.3 | 312.4 | 340.3 | 249.6 | 362.1 | 331.7 | 286.3 | 332.5
1575.1 | 1423.1 | -6.8 | 0 | 0 | 342.5 | 341.9 | 316.7 | 312 | 345.6 | 63 | 18.6 | 101.5 | 2.9 | 163.2 | 5.3 | 652.2 | 454.1 | 280.4 | 617.6 | 567.2 | 655.2 | 478.1 | 362.3 | 606.3 | 589.8 | 211.5 | 312.3 | 340.1 | 249.8 | 361.1 | 329.7 | 286.4 | 332
1576.1 | 1424.1 | -6.8 | 0 | 0 | 340.8 | 339.8 | 314.9 | 310.4 | 343.3 | 62.8 | 18.5 | 101.2 | 2.8 | 147.3 | 4.9 | 647.6 | 448.7 | 273.9 | 612 | 564.1 | 651.9 | 474.7 | 355.6 | 603.5 | 586.1 | 211.7 | 312.2 | 339.8 | 249.9 | 360.4 | 327.9 | 286.5 | 331.6
1577.1 | 1425.1 | -6.8 | 0 | 0 | 338.9 | 338 | 313.1 | 308.8 | 341.1 | 62.7 | 18.6 | 100.9 | 3.1 | 151.6 | 4.9 | 642.8 | 443.7 | 267.3 | 606.2 | 560.9 | 648.5 | 471.9 | 352 | 600 | 582.9 | 211.9 | 312.1 | 339.6 | 250 | 359.3 | 326.2 | 286.6 | 331.2
1578.1 | 1426.1 | -6.8 | 0 | 0 | 337.2 | 336.4 | 311.3 | 307.4 | 339.3 | 62.5 | 18.5 | 100.6 | 3 | 141.5 | 4.7 | 637.6 | 438.1 | 259.9 | 601.8 | 557.5 | 645.2 | 469.6 | 346.5 | 596.7 | 579.6 | 212.1 | 312 | 339.4 | 250.1 | 358.7 | 324.2 | 286.7 | 330.7
1579.1 | 1427.1 | -6.8 | 0 | 0 | 335.9 | 335 | 309.8 | 306 | 337.3 | 62.5 | 18.5 | 100.3 | 3.2 | 156 | 5.6 | 632.6 | 433.4 | 254.7 | 597.2 | 554 | 641.9 | 466.5 | 343.2 | 593.5 | 576 | 212.3 | 311.9 | 339.1 | 250.2 | 357.8 | 322.4 | 286.8 | 330.3
1580.1 | 1428.1 | -6.8 | 0 | 0 | 335 | 333.4 | 308.2 | 304.6 | 335.6 | 62.5 | 18.5 | 100 | 3.7 | 161.1 | 6.8 | 628.1 | 429.4 | 249.9 | 592.6 | 551.3 | 638.7 | 464.5 | 340.1 | 590.1 | 572.9 | 212.5 | 311.8 | 338.9 | 250.3 | 357.2 | 320.7 | 286.9 | 329.8
1581.1 | 1429.1 | -6.8 | 0 | 0 | 333.7 | 331.9 | 306.8 | 303.2 | 333.5 | 62.4 | 18.5 | 99.7 | 3.3 | 152.2 | 6.9 | 624 | 423.1 | 243 | 589.6 | 547.7 | 635.8 | 461.9 | 333.7 | 587.1 | 569.3 | 212.7 | 311.7 | 338.6 | 250.4 | 356.3 | 319.1 | 287 | 329.3
1582.1 | 1430.1 | -6.8 | 0 | 0 | 332.3 | 330.3 | 305.4 | 301.9 | 331.7 | 62.2 | 18.5 | 99.4 | 3.2 | 164.6 | 6.5 | 619.5 | 418.6 | 237.1 | 584.1 | 544.5 | 632.9 | 459.8 | 330.2 | 584.2 | 566 | 213 | 311.6 | 338.4 | 250.4 | 355 | 317.4 | 287 | 328.9
1583.1 | 1431.1 | -6.8 | 0 | 0 | 330.9 | 328.7 | 304.1 | 300.6 | 330.3 | 62.1 | 18.5 | 99.1 | 3.3 | 179.5 | 6.3 | 614.9 | 413.8 | 232.1 | 578.7 | 542.1 | 629.7 | 457.4 | 326.3 | 581.8 | 562.6 | 213.2 | 311.5 | 338.1 | 250.5 | 354.5 | 316 | 287.2 | 328.4
1584.1 | 1432.1 | -6.8 | 0 | 0 | 329.5 | 327.2 | 302.7 | 299.3 | 328.2 | 61.9 | 18.6 | 98.8 | 3.5 | 166.9 | 5.8 | 610.8 | 409.9 | 227 | 575.5 | 538.8 | 626.6 | 454.4 | 321.1 | 579 | 559.3 | 213.4 | 311.4 | 337.9 | 250.6 | 353.6 | 314.7 | 287.2 | 328.1
1585.1 | 1433.1 | -6.8 | 0 | 0 | 328.3 | 325.6 | 301.3 | 298.1 | 326.1 | 61.7 | 18.6 | 98.6 | 3.5 | 169.9 | 6.2 | 607.3 | 407.1 | 222.4 | 571.7 | 535.7 | 623.6 | 451 | 318.7 | 576.2 | 556.4 | 213.6 | 311.3 | 337.6 | 250.7 | 352.4 | 313.4 | 287.3 | 327.7
1586.1 | 1434.1 | -6.8 | 0 | 0 | 327.3 | 324.4 | 299.9 | 297 | 324.5 | 61.6 | 18.5 | 98.3 | 3.6 | 172.5 | 7.1 | 603.3 | 404.5 | 218.2 | 567.3 | 532.5 | 620.5 | 448.8 | 314.2 | 573.1 | 553.5 | 213.8 | 311.2 | 337.4 | 250.8 | 351.3 | 312.2 | 287.4 | 327.3
1587.1 | 1435.1 | -6.8 | 0 | 0 | 326.1 | 323.2 | 298.7 | 295.9 | 323.2 | 61.7 | 18.5 | 98 | 3.5 | 160.1 | 7.1 | 599.8 | 401.2 | 213.4 | 563.5 | 529.6 | 617.5 | 446.6 | 310.8 | 570.4 | 550.8 | 214 | 311.1 | 337.2 | 250.9 | 350.5 | 310.9 | 287.4 | 326.9
1588.1 | 1436.1 | -6.8 | 0 | 0 | 324.9 | 321.9 | 297.4 | 294.8 | 321.3 | 61.7 | 18.5 | 97.7 | 3.8 | 156.3 | 7 | 596.1 | 397.8 | 209.6 | 559.6 | 526.1 | 614.6 | 443.3 | 307.1 | 568 | 547.7 | 214.2 | 310.9 | 336.9 | 251 | 349.6 | 309.7 | 287.5 | 326.4
1589.1 | 1437.1 | -6.8 | 0 | 0 | 323.9 | 320.6 | 296.2 | 293.6 | 319.8 | 61.7 | 18.5 | 97.4 | 3.8 | 156 | 6.5 | 592.6 | 395 | 207.3 | 556.1 | 523.8 | 611.6 | 439.9 | 305.9 | 565.3 | 545 | 214.4 | 310.8 | 336.7 | 251.1 | 348.2 | 308.5 | 287.6 | 326
1590.1 | 1438.1 | -6.8 | 0 | 0 | 322.9 | 319.3 | 295.1 | 292.5 | 318.3 | 61.6 | 18.5 | 97.2 | 3.8 | 157.4 | 6.4 | 589.3 | 391.4 | 204 | 552.6 | 521.7 | 608.5 | 437.5 | 301.4 | 563.1 | 542.4 | 214.6 | 310.7 | 336.5 | 251.1 | 347.4 | 307.4 | 287.7 | 325.6
1591.1 | 1439.1 | -6.8 | 0 | 0 | 321.9 | 318.1 | 293.9 | 291.5 | 316.8 | 61.4 | 18.5 | 96.9 | 3.5 | 176 | 7 | 586 | 387.6 | 200.4 | 550 | 518.3 | 605.6 | 435 | 297.4 | 561.2 | 539.5 | 214.8 | 310.6 | 336.2 | 251.2 | 346.8 | 306.3 | 287.8 | 325.2
1592.1 | 1440.1 | -6.8 | 0 | 0 | 320.8 | 317.2 | 292.7 | 290.5 | 316.2 | 61.3 | 18.5 | 96.6 | 3.4 | 158.8 | 7.4 | 582.4 | 383.9 | 196.6 | 545.7 | 515.1 | 602.8 | 432.8 | 293.7 | 558.9 | 536.7 | 215 | 310.5 | 336 | 251.3 | 345.8 | 305.1 | 287.8 | 324.8
1593.1 | 1441.1 | -6.8 | 0 | 0 | 319.8 | 316 | 291.4 | 289.5 | 315.6 | 61.2 | 18.5 | 96.3 | 3.4 | 164 | 7.2 | 578.5 | 380.6 | 193.2 | 540.9 | 512.5 | 600 | 431.1 | 290.9 | 556.8 | 534.5 | 215.2 | 310.4 | 335.7 | 251.4 | 345.1 | 303.9 | 287.9 | 324.4
1594.1 | 1442.1 | -6.8 | 0 | 0 | 318.8 | 314.8 | 290.3 | 288.5 | 314.1 | 61.1 | 18.5 | 96 | 3.4 | 176.7 | 7 | 574.7 | 377.9 | 190.3 | 536.8 | 509.8 | 597.2 | 429.3 | 287.6 | 554.1 | 532.2 | 215.4 | 310.2 | 335.5 | 251.5 | 344.3 | 302.9 | 288 | 323.9
1595.1 | 1443.1 | -6.8 | 0 | 0 | 318 | 313.6 | 289.3 | 287.6 | 312.5 | 61 | 18.5 | 95.7 | 3.3 | 184.2 | 7 | 570.5 | 373.8 | 187.8 | 532.4 | 507.3 | 594.4 | 426.9 | 284.5 | 551.7 | 529.4 | 215.6 | 310.1 | 335.2 | 251.5 | 343.5 | 301.9 | 288 | 323.5
1596.1 | 1444.1 | -6.8 | 0 | 0 | 317.3 | 312.4 | 288.3 | 286.6 | 311.7 | 60.9 | 18.6 | 95.4 | 3.2 | 179.6 | 7.3 | 567.3 | 369.5 | 184.8 | 529.8 | 504.9 | 591.6 | 425.3 | 282.1 | 550.4 | 527 | 215.7 | 310 | 335 | 251.6 | 342.4 | 300.9 | 288.1 | 323.1
1597.1 | 1445.1 | -6.8 | 0 | 0 | 316.1 | 311.4 | 287.2 | 285.7 | 310.9 | 60.9 | 18.6 | 95.2 | 3.4 | 172.7 | 7.6 | 564.2 | 366.6 | 182.2 | 527.2 | 502.7 | 588.9 | 423.1 | 279.4 | 548.9 | 524.9 | 215.9 | 309.8 | 334.7 | 251.7 | 341.4 | 300 | 288.2 | 322.7
1598.1 | 1446.1 | -6.8 | 0 | 0 | 315.2 | 310.3 | 286.3 | 284.9 | 310.4 | 60.8 | 18.6 | 94.9 | 3.5 | 173.4 | 7.8 | 560.9 | 361.6 | 179.8 | 524 | 500.3 | 586.2 | 420.1 | 276.6 | 546.8 | 522.5 | 216.1 | 309.7 | 334.5 | 251.7 | 340.7 | 299 | 288.2 | 322.3
1599.1 | 1447.1 | -6.8 | 0 | 0 | 314.2 | 309.4 | 285.4 | 284 | 309.9 | 60.8 | 18.6 | 94.7 | 3.3 | 181.3 | 7.9 | 557.5 | 358.7 | 177.7 | 520.5 | 498.1 | 583.6 | 416 | 273.3 | 544.3 | 519.9 | 216.3 | 309.6 | 334.3 | 251.8 | 340 | 298.1 | 288.3 | 321.9
1600.1 | 1448.1 | -6.8 | 0 | 0 | 313.5 | 308.6 | 284.5 | 283.2 | 309.3 | 60.6 | 18.6 | 94.4 | 3.1 | 171.6 | 7.8 | 554.4 | 355.4 | 175.5 | 517.6 | 495.9 | 581 | 413.1 | 270.8 | 541.6 | 517.4 | 216.4 | 309.4 | 334 | 251.9 | 339 | 297.1 | 288.3 | 321.5
1601.1 | 1449.1 | -6.8 | 0 | 0 | 312.9 | 307.8 | 283.6 | 282.4 | 308.5 | 60.5 | 18.6 | 94.2 | 3.1 | 171.7 | 7.6 | 551.2 | 351.8 | 173.4 | 514.2 | 493.7 | 578.3 | 411.3 | 269 | 538.9 | 514.6 | 216.6 | 309.3 | 333.8 | 251.9 | 338.1 | 296.2 | 288.4 | 321
1602.1 | 1450.1 | -6.8 | 0 | 0 | 312 | 306.9 | 282.7 | 281.5 | 307.5 | 60.4 | 18.6 | 94 | 3.2 | 169.8 | 7.3 | 548.1 | 349 | 171 | 510.6 | 491.8 | 575.8 | 409.1 | 267.5 | 536.3 | 512.2 | 216.8 | 309.1 | 333.5 | 252 | 337.3 | 295.2 | 288.4 | 320.6
1603.1 | 1451.1 | -6.8 | 0 | 0 | 311.1 | 306 | 281.8 | 280.7 | 306.7 | 60.2 | 18.6 | 93.7 | 3.2 | 170.5 | 7.3 | 544.7 | 347.1 | 168.5 | 507.6 | 489.6 | 573.2 | 407.7 | 265.7 | 533.4 | 509.8 | 216.9 | 309 | 333.3 | 252.1 | 336.6 | 294.3 | 288.5 | 320.2
1604.1 | 1452.1 | -6.8 | 0 | 0 | 310.1 | 305.3 | 281 | 279.8 | 305.8 | 59.9 | 18.6 | 93.5 | 3.1 | 170.5 | 7.7 | 541.4 | 345.4 | 166.5 | 504.4 | 487.9 | 570.6 | 406.8 | 264.8 | 530.5 | 507.8 | 217.1 | 308.9 | 333.1 | 252.1 | 335.4 | 293.4 | 288.5 | 319.7
1605.1 | 1453.1 | -6.8 | 0 | 0 | 309.4 | 304.4 | 280.2 | 279 | 304.9 | 59.8 | 18.6 | 93.2 | 3.5 | 171.3 | 7.9 | 538.5 | 343.6 | 165.4 | 502 | 485.8 | 568 | 404 | 263 | 528.3 | 505.3 | 217.3 | 308.7 | 332.8 | 252.2 | 334.2 | 292.6 | 288.6 | 319.3
1606.1 | 1454.1 | -6.8 | 0 | 0 | 308.4 | 303.5 | 279.5 | 278.1 | 303.9 | 59.7 | 18.6 | 93 | 3.7 | 169 | 7.9 | 535.6 | 341.5 | 164.6 | 498.1 | 483.7 | 565.4 | 401.8 | 260.3 | 526.5 | 503.5 | 217.4 | 308.6 | 332.6 | 252.3 | 333.1 | 291.7 | 288.6 | 318.9
1607.1 | 1455.1 | -6.8 | 0 | 0 | 307.7 | 302.6 | 278.8 | 277.2 | 303.2 | 59.7 | 18.6 | 92.8 | 3.3 | 171.8 | 7.7 | 532.4 | 339.8 | 162.8 | 495.3 | 481.6 | 563 | 399.1 | 258.1 | 524.7 | 501.3 | 217.6 | 308.4 | 332.3 | 252.3 | 332.3 | 290.8 | 288.7 | 318.5
1608.1 | 1456.1 | -6.8 | 0 | 0 | 306.9 | 301.7 | 278.1 | 276.5 | 302.5 | 59.7 | 18.6 | 92.6 | 3.7 | 172.3 | 7.5 | 529.6 | 337.3 | 161.2 | 492.3 | 479.8 | 560.7 | 395.7 | 255.6 | 523.3 | 499.2 | 217.7 | 308.3 | 332.1 | 252.4 | 331.4 | 290 | 288.7 | 318.1
1609.1 | 1457.1 | -6.8 | 0 | 0 | 306.2 | 300.9 | 277.3 | 275.8 | 301.8 | 59.7 | 18.6 | 92.4 | 3.4 | 161.8 | 7.6 | 526.5 | 334.3 | 159.2 | 489 | 477.7 | 558.4 | 392.1 | 253.7 | 521.5 | 497.4 | 217.9 | 308.2 | 331.9 | 252.4 | 330.5 | 289.2 | 288.7 | 317.7
1610.1 | 1458.1 | -6.8 | 0 | 0 | 305.5 | 300.1 | 276.4 | 275 | 301.4 | 59.5 | 18.6 | 92.2 | 3.4 | 160.8 | 7.4 | 523.6 | 332.2 | 157 | 485.6 | 475.6 | 556.1 | 389.7 | 252.2 | 520 | 495.2 | 218 | 308 | 331.6 | 252.5 | 329.7 | 288.5 | 288.8 | 317.3
1611.1 | 1459.1 | -6.8 | 0 | 0 | 305.1 | 299.2 | 275.6 | 274.3 | 301 | 59.4 | 18.6 | 92 | 3.6 | 164.6 | 7 | 520.7 | 328.5 | 155.6 | 483.4 | 473.3 | 553.8 | 388 | 250.4 | 518.1 | 493.2 | 218.2 | 307.9 | 331.4 | 252.6 | 328.9 | 287.7 | 288.8 | 316.9
1612.1 | 1460.1 | -6.8 | 0 | 0 | 304.6 | 298.3 | 274.7 | 273.5 | 300.5 | 59.2 | 18.6 | 91.8 | 3.6 | 159.4 | 6.6 | 517.8 | 325.8 | 154.6 | 478.8 | 471.2 | 551.5 | 385.9 | 248.2 | 516.6 | 491.4 | 218.3 | 307.7 | 331.1 | 252.6 | 327.9 | 287 | 288.9 | 316.4
1613.1 | 1461.1 | -6.8 | 0 | 0 | 303.8 | 297.5 | 274 | 272.8 | 299.9 | 59 | 18.6 | 91.5 | 3.8 | 166.7 | 6 | 514.7 | 324.6 | 152.5 | 475.4 | 469.2 | 549.2 | 383.9 | 246.1 | 515.5 | 489.9 | 218.5 | 307.6 | 330.9 | 252.7 | 326.9 | 286.3 | 288.9 | 316
1614.1 | 1462.1 | -6.8 | 0 | 0 | 303 | 297 | 273.3 | 272.2 | 299.4 | 58.8 | 18.6 | 91.3 | 3.6 | 167 | 5.6 | 511.6 | 321.9 | 150.5 | 473.1 | 466.3 | 547 | 381.4 | 243.8 | 513.4 | 487.8 | 218.6 | 307.4 | 330.6 | 252.7 | 325.9 | 285.6 | 288.9 | 315.6
1615.1 | 1463.1 | -6.8 | 0 | 0 | 302.4 | 296.4 | 272.6 | 271.4 | 298.8 | 58.7 | 18.6 | 91.1 | 3.4 | 169.1 | 5.9 | 508.7 | 318 | 149.2 | 470.5 | 464.1 | 544.8 | 379 | 241.4 | 512.1 | 485.4 | 218.7 | 307.3 | 330.4 | 252.8 | 325.1 | 284.8 | 289 | 315.2
1616.1 | 1464.1 | -6.8 | 0 | 0 | 301.9 | 295.6 | 272 | 270.8 | 298.3 | 58.6 | 18.6 | 90.9 | 3.4 | 165.1 | 6.2 | 505.7 | 315 | 147.7 | 467.7 | 461.7 | 542.5 | 376.8 | 240.8 | 511.2 | 484.3 | 218.9 | 307.1 | 330.2 | 252.8 | 324.3 | 284.1 | 289 | 314.9
1617.1 | 1465.1 | -6.8 | 0 | 0 | 301.2 | 294.9 | 271.3 | 270.1 | 297.7 | 58.6 | 18.6 | 90.7 | 3.4 | 154.7 | 6.1 | 502.6 | 312 | 145.9 | 464.2 | 459.4 | 540.3 | 375.1 | 239.9 | 509.9 | 482.6 | 219 | 307 | 329.9 | 252.9 | 323.4 | 283.4 | 289 | 314.4
1618.1 | 1466.1 | -6.8 | 0 | 0 | 300.2 | 294.1 | 270.6 | 269.4 | 296.9 | 58.5 | 18.6 | 90.5 | 3.4 | 150.7 | 5.7 | 500 | 307.9 | 144.5 | 461.6 | 457.4 | 538.3 | 373.7 | 238.4 | 508.3 | 480.5 | 219.1 | 306.8 | 329.7 | 252.9 | 322.8 | 282.6 | 289.1 | 314.1
1619.1 | 1467.1 | -6.8 | 0 | 0 | 299.7 | 293.5 | 270 | 268.7 | 296.1 | 58.5 | 18.6 | 90.3 | 3.3 | 154 | 5.4 | 497.3 | 303.1 | 143.8 | 458.9 | 456 | 536.3 | 370.4 | 236.8 | 506.7 | 478.7 | 219.3 | 306.7 | 329.5 | 253 | 322.3 | 282 | 289.1 | 313.6
1620.1 | 1468.1 | -6.8 | 0 | 0 | 299.2 | 292.7 | 269.3 | 268.1 | 295.5 | 58.5 | 18.6 | 90.1 | 3.3 | 167.6 | 5.1 | 494.8 | 298.7 | 143.5 | 456.3 | 453.6 | 534.1 | 369.2 | 234.8 | 505.5 | 476.9 | 219.4 | 306.5 | 329.2 | 253 | 321.6 | 281.3 | 289.1 | 313.3
1621.1 | 1469.1 | -6.8 | 0 | 0 | 298.3 | 292 | 268.6 | 267.5 | 295 | 58.4 | 18.6 | 89.9 | 3 | 172.6 | 5.7 | 492.2 | 296.7 | 142.8 | 454.2 | 451.8 | 531.9 | 367.6 | 232.8 | 504.2 | 475.3 | 219.5 | 306.4 | 329 | 253.1 | 320.8 | 280.6 | 289.1 | 312.9
1622.1 | 1470.1 | -6.8 | 0 | 0 | 297.6 | 291.3 | 267.9 | 266.9 | 294.2 | 58.4 | 18.6 | 89.7 | 3.2 | 172.2 | 6.2 | 489.6 | 295 | 141 | 451.4 | 450.3 | 529.9 | 364.4 | 231.4 | 502.2 | 473.4 | 219.7 | 306.2 | 328.8 | 253.1 | 320.1 | 280.1 | 289.2 | 312.5
1623.1 | 1471.1 | -6.8 | 0 | 0 | 296.9 | 290.6 | 267.3 | 266.3 | 293.4 | 58.3 | 18.6 | 89.5 | 3.1 | 172.2 | 6.4 | 487.5 | 293.5 | 139.5 | 448.6 | 448.3 | 527.9 | 362.3 | 229.9 | 500 | 470.8 | 219.8 | 306.1 | 328.5 | 253.2 | 319.3 | 279.5 | 289.2 | 312.1
1624.1 | 1472.1 | -6.8 | 0 | 0 | 296.3 | 289.9 | 266.7 | 265.8 | 292.8 | 58.2 | 18.6 | 89.3 | 2.8 | 171.1 | 6.5 | 484.7 | 292.7 | 138.8 | 444.9 | 446.7 | 525.8 | 359.4 | 228.3 | 497.7 | 468.3 | 219.9 | 305.9 | 328.3 | 253.3 | 318.4 | 278.8 | 289.2 | 311.6
1625.1 | 1473.1 | -6.8 | 0 | 0 | 295.6 | 289.2 | 266.1 | 265.3 | 292.2 | 58.1 | 18.6 | 89.2 | 2.6 | 166.5 | 6.7 | 481.9 | 291.8 | 137.7 | 442.4 | 444.9 | 523.7 | 356.9 | 226.5 | 495.3 | 466.6 | 220.1 | 305.8 | 328 | 253.3 | 317.6 | 278 | 289.2 | 311.2
1626.1 | 1474.1 | -6.8 | 0 | 0 | 294.9 | 288.4 | 265.5 | 264.8 | 291.4 | 58.1 | 18.6 | 89 | 2.8 | 171 | 6.4 | 480 | 290 | 136.2 | 440.4 | 443.5 | 521.7 | 355.9 | 225.8 | 492.7 | 464.7 | 220.2 | 305.6 | 327.8 | 253.3 | 317.1 | 277.4 | 289.2 | 310.8
1627.1 | 1475.1 | -6.8 | 0 | 0 | 294.5 | 287.6 | 265 | 264.3 | 290.4 | 58.1 | 18.6 | 88.8 | 2.9 | 191.4 | 6.2 | 477.9 | 289.5 | 135.1 | 438.1 | 441.8 | 519.6 | 355.8 | 224.9 | 490.7 | 462.6 | 220.3 | 305.4 | 327.6 | 253.4 | 316.5 | 276.8 | 289.2 | 310.4
1628.1 | 1476.1 | -6.8 | 0 | 0 | 293.9 | 286.9 | 264.6 | 263.7 | 289.7 | 58 | 18.6 | 88.7 | 3.1 | 179.9 | 6.3 | 475.6 | 288.6 | 133.6 | 434.8 | 439.8 | 517.5 | 353.6 | 224.8 | 489.1 | 460.5 | 220.4 | 305.3 | 327.4 | 253.4 | 315.8 | 276.2 | 289.2 | 310
1629.1 | 1477.1 | -6.8 | 0 | 0 | 293.6 | 286.3 | 264.1 | 263 | 289.3 | 57.8 | 18.6 | 88.5 | 3 | 167.1 | 6.6 | 473 | 288 | 132.7 | 431.4 | 438.1 | 515.7 | 351.2 | 224.3 | 487.1 | 459.1 | 220.6 | 305.1 | 327.1 | 253.5 | 314.6 | 275.6 | 289.2 | 309.6
1630.1 | 1478.1 | -6.8 | 0 | 0 | 293.7 | 285.6 | 263.6 | 262.5 | 288.8 | 57.7 | 18.6 | 88.3 | 3 | 169.3 | 6.7 | 470.7 | 287.3 | 131.6 | 429.2 | 436.5 | 513.7 | 350.6 | 223.5 | 485.5 | 457.3 | 220.7 | 304.9 | 326.9 | 253.5 | 313.9 | 275 | 289.2 | 309.2
1631.1 | 1479.1 | -6.8 | 0 | 0 | 293.8 | 285.2 | 263 | 262.1 | 288.1 | 57.5 | 18.6 | 88.2 | 2.9 | 166.2 | 6.7 | 468 | 286.5 | 130.6 | 427 | 434.6 | 511.7 | 348.8 | 222.3 | 484 | 455.9 | 220.8 | 304.8 | 326.7 | 253.6 | 313.3 | 274.4 | 289.2 | 308.9
1632.1 | 1480.1 | -6.8 | 0 | 0 | 293.4 | 284.6 | 262.4 | 261.5 | 287.3 | 57.4 | 18.6 | 88 | 3.1 | 170.5 | 6.9 | 465.8 | 284.9 | 129.2 | 425.2 | 433 | 509.6 | 347.1 | 222 | 482.7 | 454.4 | 220.9 | 304.6 | 326.4 | 253.6 | 312.8 | 273.8 | 289.3 | 308.4
1633.1 | 1481.1 | -6.8 | 0 | 0 | 292.7 | 284.1 | 261.9 | 261 | 286.8 | 57.4 | 18.6 | 87.8 | 3.3 | 169.7 | 7.5 | 463.3 | 283.6 | 128.4 | 423.4 | 431.7 | 507.6 | 344.8 | 220.4 | 481.5 | 453 | 221.1 | 304.5 | 326.2 | 253.6 | 312 | 273.1 | 289.3 | 308.1
1634.1 | 1482.1 | -6.8 | 0 | 0 | 292 | 283.5 | 261.4 | 260.4 | 286.2 | 57.2 | 18.6 | 87.7 | 3.1 | 168.4 | 7.3 | 461 | 282.1 | 127.5 | 420.6 | 430.1 | 505.7 | 343.2 | 218.8 | 480.1 | 451.3 | 221.2 | 304.3 | 326 | 253.7 | 311.4 | 272.5 | 289.3 | 307.6
1635.1 | 1483.1 | -6.8 | 0 | 0 | 291.2 | 282.9 | 260.8 | 259.9 | 285.6 | 57 | 18.6 | 87.5 | 3.1 | 166.8 | 6.9 | 458.6 | 281 | 126.5 | 416.8 | 428.4 | 503.8 | 342 | 217.7 | 478.3 | 449.7 | 221.3 | 304.2 | 325.8 | 253.7 | 311 | 271.9 | 289.2 | 307.3
1636.1 | 1484.1 | -6.8 | 0 | 0 | 290.7 | 282.3 | 260.1 | 259.4 | 285 | 56.9 | 18.6 | 87.3 | 3.3 | 171.3 | 6 | 456.3 | 280.5 | 125.6 | 414.4 | 426.5 | 501.9 | 341.5 | 217.4 | 476.7 | 447.8 | 221.4 | 304 | 325.5 | 253.8 | 310.6 | 271.3 | 289.2 | 306.9
1637.1 | 1485.1 | -6.8 | 0 | 0 | 290.1 | 281.8 | 259.5 | 258.9 | 284.4 | 56.8 | 18.6 | 87.1 | 3.3 | 158.3 | 5.5 | 454 | 278.9 | 124.7 | 412.5 | 425 | 500.1 | 339.9 | 216.8 | 474.8 | 446.3 | 221.6 | 303.8 | 325.3 | 253.8 | 309.9 | 270.8 | 289.2 | 306.5
1638.1 | 1486.1 | -6.8 | 0 | 0 | 289.4 | 281.4 | 259 | 258.4 | 283.8 | 56.6 | 18.6 | 86.8 | 3.3 | 166.1 | 5.4 | 451.8 | 277.5 | 123.8 | 411.1 | 423.2 | 498.5 | 337 | 215.4 | 472.6 | 444.6 | 221.7 | 303.7 | 325.1 | 253.9 | 309.2 | 270.2 | 289.3 | 306.1
1639.1 | 1487.1 | -6.8 | 0 | 0 | 288.8 | 280.8 | 258.6 | 258 | 283.4 | 56.6 | 18.6 | 86.6 | 3.4 | 172.4 | 5.5 | 449.8 | 276 | 122.9 | 409.7 | 421.9 | 496.7 | 335.7 | 214.1 | 470.6 | 442.8 | 221.8 | 303.5 | 324.8 | 253.9 | 308.6 | 269.7 | 289.2 | 305.7
1640.1 | 1488.1 | -6.8 | 0 | 0 | 288.2 | 280.1 | 258 | 257.5 | 283 | 56.5 | 18.6 | 86.5 | 3.5 | 164.6 | 5.3 | 448.1 | 273.6 | 122.3 | 407.6 | 420.4 | 495 | 334.8 | 212.7 | 468.7 | 440.9 | 221.9 | 303.3 | 324.6 | 253.9 | 308 | 269.2 | 289.2 | 305.3
1641.1 | 1489.1 | -6.8 | 0 | 0 | 287.6 | 279.6 | 257.5 | 257 | 282.6 | 56.5 | 18.6 | 86.3 | 3.3 | 162 | 5.7 | 446 | 271.8 | 121.7 | 404.8 | 418.7 | 493 | 333.8 | 211.1 | 467.5 | 439.4 | 222 | 303.2 | 324.4 | 254 | 307.4 | 268.7 | 289.2 | 304.9
1642.1 | 1490.1 | -6.8 | 0 | 0 | 287.1 | 279 | 257 | 256.5 | 281.9 | 56.3 | 18.6 | 86.1 | 2.8 | 174.8 | 7.2 | 443.7 | 271 | 121.1 | 403 | 417.1 | 491.2 | 331.1 | 210 | 465.9 | 437.6 | 222.2 | 303 | 324.2 | 254 | 306.7 | 268.1 | 289.2 | 304.5
1643.1 | 1491.1 | -6.8 | 0 | 0 | 286.5 | 278.4 | 256.5 | 255.9 | 281.2 | 56.2 | 18.6 | 86 | 3.1 | 182.9 | 8.3 | 442 | 267.6 | 120.7 | 401.6 | 415.8 | 489.4 | 330.5 | 208.6 | 464.4 | 436 | 222.3 | 302.9 | 324 | 254.1 | 306 | 267.6 | 289.2 | 304.1
1644.1 | 1492.1 | -6.8 | 0 | 0 | 286 | 277.9 | 256.1 | 255.3 | 280.5 | 56.1 | 18.6 | 85.8 | 3.4 | 172.3 | 8.7 | 440.1 | 264.7 | 120.2 | 399.4 | 414.4 | 487.7 | 328.6 | 208.3 | 463.6 | 434.9 | 222.4 | 302.7 | 323.7 | 254.1 | 305.4 | 267.1 | 289.2 | 303.7
1645.1 | 1493.1 | -6.8 | 0 | 0 | 285.5 | 277.5 | 255.6 | 254.8 | 279.8 | 56.1 | 18.6 | 85.6 | 3.2 | 175.3 | 8.6 | 437.8 | 263.3 | 119.5 | 397.1 | 413.2 | 486.2 | 327.3 | 207.5 | 462.3 | 433.5 | 222.5 | 302.5 | 323.5 | 254.2 | 305 | 266.5 | 289.2 | 303.4
1646.1 | 1494.1 | -6.8 | 0 | 0 | 284.9 | 277 | 255.2 | 254.2 | 279.1 | 56 | 18.6 | 85.5 | 3.2 | 175.3 | 8.5 | 435.6 | 262.2 | 118.6 | 395.4 | 412 | 484.7 | 325.4 | 206.7 | 460.8 | 431.9 | 222.7 | 302.4 | 323.3 | 254.2 | 304.3 | 266 | 289.2 | 303
1647.1 | 1495.1 | -6.8 | 0 | 0 | 284.4 | 276.4 | 254.7 | 253.8 | 278.6 | 55.9 | 18.6 | 85.3 | 3.3 | 165.4 | 8.2 | 434.1 | 259.7 | 117.8 | 393.9 | 410.6 | 483 | 323.3 | 205.8 | 459.5 | 430.2 | 222.8 | 302.2 | 323.1 | 254.2 | 303.8 | 265.4 | 289.1 | 302.6
1648.1 | 1496.1 | -6.8 | 0 | 0 | 284 | 275.8 | 254.2 | 253.2 | 278 | 55.9 | 18.6 | 85.1 | 3.1 | 163.8 | 7.6 | 432.5 | 258.8 | 116.9 | 392.3 | 409 | 481.4 | 320.4 | 203.3 | 458.2 | 429 | 222.9 | 302.1 | 322.8 | 254.3 | 303.4 | 264.8 | 289.1 | 302.2
1649.1 | 1497.1 | -6.8 | 0 | 0 | 283.5 | 275.3 | 253.8 | 252.8 | 277.3 | 55.8 | 18.6 | 85 | 3.1 | 167.6 | 7.2 | 430.6 | 258.7 | 116.1 | 390 | 407.2 | 479.9 | 319 | 201.7 | 457.2 | 427.9 | 223 | 301.9 | 322.6 | 254.3 | 302.8 | 264.2 | 289.1 | 301.8
1650.1 | 1498.1 | -6.8 | 0 | 0 | 282.9 | 275 | 253.4 | 252.3 | 276.8 | 55.7 | 18.6 | 84.8 | 3.3 | 180.8 | 7.4 | 428.7 | 258.2 | 115.3 | 388.9 | 405.6 | 478.3 | 317.7 | 200.8 | 455.4 | 426.2 | 223.1 | 301.7 | 322.4 | 254.4 | 302.2 | 263.7 | 289.1 | 301.5
1651.1 | 1499.1 | -6.8 | 0 | 0 | 282.2 | 274.6 | 253 | 251.8 | 276.3 | 55.6 | 18.6 | 84.6 | 3.5 | 167.7 | 7.3 | 427 | 257.1 | 114.5 | 386.9 | 404.3 | 476.8 | 318.5 | 200.2 | 453.5 | 424.5 | 223.2 | 301.6 | 322.2 | 254.4 | 301.5 | 263.2 | 289.1 | 301.1
1652.1 | 1500.1 | -6.8 | 0 | 0 | 281.5 | 274.1 | 252.6 | 251.3 | 275.8 | 55.6 | 18.6 | 84.5 | 3.4 | 160.5 | 7 | 425.4 | 255.7 | 113.8 | 386 | 402.7 | 475.3 | 317.8 | 199.2 | 451.4 | 422.8 | 223.3 | 301.4 | 321.9 | 254.4 | 300.8 | 262.9 | 289 | 300.7
1653.1 | 1501.1 | -6.8 | 0 | 0 | 281.2 | 273.6 | 252.2 | 250.9 | 275.3 | 55.5 | 18.6 | 84.4 | 3.2 | 166.8 | 6.4 | 423.5 | 255.4 | 113.2 | 383.5 | 401.3 | 473.8 | 316.6 | 197.9 | 449.2 | 421.2 | 223.5 | 301.2 | 321.7 | 254.5 | 300.1 | 262.5 | 289 | 300.3
1654.1 | 1502.1 | -6.8 | 0 | 0 | 281.1 | 273.1 | 251.7 | 250.5 | 274.9 | 55.4 | 18.6 | 84.3 | 3 | 150.7 | 5.6 | 421.6 | 254.7 | 112.4 | 381.2 | 400.1 | 472.2 | 314.6 | 196.1 | 447.3 | 419.6 | 223.6 | 301.1 | 321.5 | 254.5 | 299.3 | 262 | 289 | 300
1655.1 | 1503.1 | -6.8 | 0 | 0 | 280.9 | 272.7 | 251.3 | 250 | 274.6 | 55.3 | 18.6 | 84.1 | 3.1 | 162.5 | 5.2 | 419.5 | 254.4 | 111.8 | 378.5 | 398.5 | 470.7 | 313.1 | 194.9 | 445.2 | 417.8 | 223.7 | 300.9 | 321.2 | 254.6 | 298.8 | 261.6 | 289 | 299.6
1656.1 | 1504.1 | -6.8 | 0 | 0 | 280.3 | 272.2 | 250.9 | 249.6 | 274.2 | 55.1 | 18.6 | 84 | 3.2 | 173.7 | 5.4 | 417.4 | 253.6 | 111.5 | 376.5 | 397 | 469.3 | 311.4 | 194.4 | 443.7 | 416.5 | 223.8 | 300.7 | 321 | 254.6 | 298.4 | 261.2 | 288.9 | 299.2
1657.1 | 1505.1 | -6.8 | 0 | 0 | 279.8 | 271.7 | 250.4 | 249.1 | 273.7 | 54.8 | 18.6 | 83.9 | 3.3 | 147.2 | 6.1 | 415.4 | 251.8 | 110.7 | 374.1 | 395.5 | 467.8 | 309.9 | 193.9 | 442.2 | 414.9 | 223.9 | 300.6 | 320.8 | 254.6 | 298.1 | 260.7 | 288.9 | 298.8
1658.1 | 1506.1 | -6.8 | 0 | 0 | 279.3 | 271.3 | 250 | 248.6 | 273.2 | 54.6 | 18.7 | 83.8 | 3.1 | 160.6 | 6.3 | 413.4 | 251 | 110.2 | 372.1 | 393.9 | 466.3 | 310.6 | 193.1 | 441 | 413.6 | 224 | 300.4 | 320.6 | 254.7 | 297.7 | 260.2 | 288.9 | 298.5
1659.1 | 1507.1 | -6.8 | 0 | 0 | 278.8 | 270.9 | 249.6 | 248 | 272.8 | 54.4 | 18.6 | 83.7 | 3.1 | 152 | 6 | 411.7 | 248.6 | 109.9 | 370.5 | 392.6 | 464.7 | 309.6 | 192.7 | 440 | 412.6 | 224.1 | 300.2 | 320.4 | 254.7 | 297.3 | 259.7 | 288.9 | 298.1
1660.1 | 1508.1 | -6.8 | 0 | 0 | 278.3 | 270.5 | 249.2 | 247.5 | 272.3 | 54.4 | 18.6 | 83.6 | 3 | 167.9 | 5.4 | 410.2 | 246.4 | 109.5 | 369.3 | 391.3 | 463.2 | 308.4 | 192.9 | 439 | 411.2 | 224.2 | 300.1 | 320.2 | 254.8 | 296.6 | 259.2 | 288.8 | 297.7
1661.1 | 1509.1 | -6.8 | 0 | 0 | 277.7 | 270.1 | 248.8 | 247 | 271.8 | 54.5 | 18.6 | 83.4 | 3.1 | 186.2 | 5.1 | 408.7 | 245.8 | 108.8 | 368.6 | 390 | 461.6 | 307 | 192.1 | 438 | 409.5 | 224.4 | 299.9 | 320 | 254.8 | 296.2 | 258.8 | 288.8 | 297.3
1662.1 | 1510.1 | -6.8 | 0 | 0 | 277.2 | 269.6 | 248.3 | 246.6 | 271.4 | 54.5 | 18.7 | 83.3 | 3.3 | 141.9 | 4.9 | 407 | 244.1 | 108.1 | 366.9 | 388.8 | 460.1 | 305.4 | 190.8 | 436.2 | 408.2 | 224.5 | 299.7 | 319.8 | 254.8 | 295.7 | 258.3 | 288.7 | 296.9
1663.1 | 1511.1 | -6.8 | 0 | 0 | 276.6 | 269.1 | 247.8 | 246.1 | 271.1 | 54.4 | 18.7 | 83.1 | 3.5 | 135.8 | 4.5 | 405.7 | 241.5 | 107.6 | 365.6 | 387.3 | 458.7 | 304.9 | 190.6 | 435.3 | 407.1 | 224.6 | 299.6 | 319.6 | 254.9 | 295.2 | 257.9 | 288.7 | 296.6
1664.1 | 1512.1 | -6.8 | 0 | 0 | 275.8 | 268.8 | 247.5 | 245.6 | 270.7 | 54.2 | 18.7 | 83 | 3.6 | 140.6 | 4.5 | 404.4 | 239 | 107.2 | 364.6 | 385.9 | 457.3 | 304.2 | 191.9 | 434.6 | 406.1 | 224.7 | 299.4 | 319.3 | 254.9 | 294.7 | 257.4 | 288.7 | 296.2
1665.1 | 1513.1 | -6.8 | 0 | 0 | 275.3 | 268.4 | 247 | 245.2 | 270.2 | 54.1 | 18.7 | 82.8 | 3.5 | 144.5 | 5 | 402.7 | 238.7 | 106.5 | 363 | 384.7 | 455.8 | 302.9 | 191.8 | 433.9 | 404.9 | 224.8 | 299.2 | 319.1 | 254.9 | 294.3 | 257 | 288.6 | 295.8
1666.1 | 1514.1 | -6.8 | 0 | 0 | 274.9 | 268 | 246.6 | 244.7 | 269.8 | 53.9 | 18.7 | 82.7 | 3.5 | 145.3 | 5.4 | 400.6 | 238.3 | 105.6 | 360.1 | 382.7 | 454.4 | 301.1 | 190.4 | 432.8 | 403.3 | 224.9 | 299.1 | 318.9 | 255 | 294 | 256.5 | 288.6 | 295.4
1667.1 | 1515.1 | -6.8 | 0 | 0 | 274.4 | 267.5 | 246.2 | 244.3 | 269.4 | 53.9 | 18.7 | 82.5 | 3.4 | 159.7 | 4.5 | 398.5 | 237.1 | 104.6 | 357.6 | 380.9 | 453.2 | 299.6 | 189 | 431.2 | 401.9 | 225 | 298.9 | 318.6 | 255 | 293.6 | 256.1 | 288.6 | 295
1668.1 | 1516.1 | -6.8 | 0 | 0 | 274 | 267.2 | 245.7 | 243.8 | 269.2 | 53.8 | 18.7 | 82.4 | 3.3 | 166.6 | 4.4 | 396.6 | 235.5 | 103.6 | 355.4 | 379.1 | 451.9 | 299.7 | 187.8 | 429.6 | 400.4 | 225.1 | 298.7 | 318.4 | 255.1 | 293.1 | 255.6 | 288.5 | 294.7
1669.1 | 1517.1 | -6.8 | 0 | 0 | 273.6 | 266.9 | 245.3 | 243.3 | 268.9 | 53.8 | 18.7 | 82.2 | 3.2 | 154.2 | 4.9 | 394.8 | 234.3 | 103.2 | 353.7 | 377.3 | 450.6 | 299.6 | 186.5 | 428.2 | 398.9 | 225.2 | 298.6 | 318.2 | 255.1 | 292.3 | 255.1 | 288.5 | 294.3
1670.1 | 1518.1 | -6.8 | 0 | 0 | 273.2 | 266.5 | 244.8 | 242.9 | 268.5 | 53.7 | 18.7 | 82.1 | 3.2 | 135.2 | 5.9 | 392.6 | 233.1 | 102.7 | 351.9 | 375.6 | 449.1 | 298.9 | 185.8 | 426.5 | 397.5 | 225.2 | 298.4 | 318 | 255.1 | 291.6 | 254.7 | 288.4 | 293.9
1671.1 | 1519.1 | -6.8 | 0 | 0 | 272.7 | 266 | 244.4 | 242.5 | 268.1 | 53.7 | 18.7 | 82 | 3.1 | 130 | 6 | 391.1 | 231.8 | 102.5 | 350.3 | 374.5 | 447.7 | 298.6 | 185.1 | 425.2 | 395.9 | 225.3 | 298.2 | 317.8 | 255.2 | 291 | 254.2 | 288.4 | 293.6
1672.1 | 1520.1 | -6.8 | 0 | 0 | 272.4 | 265.7 | 243.9 | 242.1 | 267.8 | 53.6 | 18.7 | 81.9 | 3.2 | 166.7 | 6.3 | 389.8 | 231.7 | 102.3 | 348.5 | 373.1 | 446.1 | 298.5 | 184.1 | 423.9 | 394.9 | 225.4 | 298 | 317.6 | 255.2 | 290.5 | 253.7 | 288.3 | 293.2
1673.1 | 1521.1 | -6.8 | 0 | 0 | 272 | 265.2 | 243.5 | 241.8 | 267.3 | 53.6 | 18.7 | 81.7 | 3.3 | 158 | 6.9 | 388.6 | 231.2 | 101.8 | 347.3 | 371.6 | 444.7 | 296.9 | 184.1 | 422.7 | 393.7 | 225.5 | 297.9 | 317.3 | 255.2 | 290 | 253.3 | 288.3 | 292.9
1674.1 | 1522.1 | -6.8 | 0 | 0 | 271.5 | 264.7 | 243.1 | 241.4 | 266.8 | 53.5 | 18.7 | 81.6 | 3.3 | 135.4 | 6.7 | 387.3 | 229.7 | 101.4 | 346.4 | 370.2 | 443.4 | 296.1 | 184.6 | 422 | 392.7 | 225.6 | 297.7 | 317.1 | 255.3 | 289.5 | 252.8 | 288.3 | 292.5
1675.1 | 1523.1 | -6.8 | 0 | 0 | 271 | 264.2 | 242.7 | 241 | 266.3 | 53.4 | 18.7 | 81.5 | 3.5 | 135.5 | 5.9 | 385.7 | 228.4 | 100.9 | 344.8 | 368.7 | 442.1 | 294.8 | 184.6 | 421.1 | 391.3 | 225.7 | 297.5 | 316.8 | 255.3 | 289 | 252.4 | 288.2 | 292.1
1676.1 | 1524.1 | -6.8 | 0 | 0 | 270.5 | 263.7 | 242.3 | 240.5 | 265.6 | 53.3 | 18.7 | 81.4 | 3.3 | 161.2 | 5.6 | 384.2 | 227.5 | 100.3 | 343 | 366.9 | 440.7 | 294.1 | 183.4 | 419.8 | 389.9 | 225.8 | 297.4 | 316.7 | 255.4 | 288.4 | 252 | 288.1 | 291.7
1677.1 | 1525.1 | -6.8 | 0 | 0 | 270 | 263.4 | 241.9 | 240.1 | 265 | 53.2 | 18.7 | 81.2 | 3.1 | 163.6 | 5.7 | 382.8 | 226.4 | 99.8 | 341.5 | 365.2 | 439.4 | 293.8 | 182.1 | 418.3 | 388.7 | 225.8 | 297.2 | 316.5 | 255.4 | 287.8 | 251.6 | 288.1 | 291.3
1678.1 | 1526.1 | -6.8 | 0 | 0 | 269.5 | 263.2 | 241.6 | 239.7 | 264.3 | 53.1 | 18.7 | 81.1 | 3.2 | 186.9 | 5.3 | 381.3 | 226 | 99.5 | 339.4 | 363.6 | 438.1 | 291.9 | 181.2 | 417 | 387.4 | 225.9 | 297 | 316.3 | 255.4 | 287.2 | 251.2 | 288.1 | 291
1679.1 | 1527.1 | -6.8 | 0 | 0 | 269.1 | 262.9 | 241.2 | 239.3 | 263.9 | 53 | 18.7 | 81 | 3.4 | 154.3 | 5.1 | 379.9 | 225.4 | 99.2 | 337.9 | 362.2 | 436.8 | 290.8 | 180.3 | 414.9 | 386 | 226 | 296.9 | 316.1 | 255.5 | 286.5 | 250.8 | 288 | 290.6
1680.1 | 1528.1 | -6.8 | 0 | 0 | 268.6 | 262.6 | 240.8 | 238.9 | 263.6 | 52.9 | 18.7 | 80.9 | 3.3 | 139.7 | 5.4 | 378.5 | 224.4 | 98.8 | 336.1 | 360.8 | 435.5 | 290.7 | 179.9 | 413.1 | 384.7 | 226.1 | 296.7 | 315.8 | 255.5 | 285.7 | 250.4 | 288 | 290.3
1681.1 | 1529.1 | -6.8 | 0 | 0 | 268.2 | 262.1 | 240.4 | 238.6 | 263.3 | 52.8 | 18.7 | 80.8 | 3.1 | 156.4 | 5.2 | 376.8 | 223.9 | 98.6 | 332.7 | 359.7 | 434.2 | 290.5 | 179.7 | 411.6 | 383.4 | 226.1 | 296.4 | 315.6 | 255.5 | 285.1 | 250 | 287.9 | 289.9
1682.1 | 1530.1 | -6.8 | 0 | 0 | 267.9 | 261.6 | 240 | 238.2 | 263 | 52.6 | 18.7 | 80.7 | 3.2 | 167.1 | 4.5 | 375.1 | 223.7 | 98.1 | 330 | 358.3 | 432.9 | 290.7 | 179.3 | 409.8 | 381.9 | 226.2 | 296.2 | 315.4 | 255.6 | 284.4 | 249.6 | 287.9 | 289.6
1683.1 | 1531.1 | -6.8 | 0 | 0 | 267.6 | 261.2 | 239.7 | 237.9 | 262.6 | 52.5 | 18.7 | 80.6 | 2.9 | 138 | 4.4 | 373.7 | 223.3 | 97.7 | 328.1 | 356.6 | 431.5 | 290 | 178.9 | 407.9 | 380.5 | 226.3 | 296 | 315.2 | 255.6 | 283.7 | 249.2 | 287.8 | 289.2
1684.1 | 1532.1 | -6.8 | 0 | 0 | 267.3 | 260.9 | 239.3 | 237.5 | 262.2 | 52.4 | 18.7 | 80.5 | 3.4 | 150.9 | 4.3 | 372.4 | 222.1 | 97.2 | 326.4 | 354.9 | 430.3 | 289 | 177.5 | 406.1 | 378.8 | 226.3 | 295.8 | 315 | 255.7 | 283.2 | 248.8 | 287.8 | 288.9
1685.1 | 1533.1 | -6.8 | 0 | 0 | 267 | 260.6 | 238.9 | 237.2 | 261.8 | 52.3 | 18.7 | 80.3 | 3.3 | 167.4 | 4.6 | 370.9 | 221.4 | 96.7 | 324.2 | 353.5 | 428.9 | 288.7 | 176.7 | 404.3 | 377.3 | 226.4 | 295.6 | 314.8 | 255.7 | 282.7 | 248.4 | 287.7 | 288.6
1686.1 | 1534.1 | -6.8 | 0 | 0 | 266.7 | 260.2 | 238.5 | 236.9 | 261.4 | 52.2 | 18.7 | 80.1 | 3.3 | 153.9 | 5.3 | 369.3 | 220.7 | 96.2 | 321 | 352 | 427.7 | 288.9 | 176.2 | 402.8 | 375.8 | 226.5 | 295.4 | 314.6 | 255.7 | 282.1 | 248 | 287.7 | 288.2
1687.1 | 1535.1 | -6.8 | 0 | 0 | 266.3 | 259.9 | 238.1 | 236.5 | 261 | 52.2 | 18.7 | 80 | 3.5 | 156.5 | 5.9 | 367.7 | 219.9 | 95.7 | 319.8 | 350.6 | 426.4 | 288.5 | 176.3 | 401.5 | 374.5 | 226.5 | 295.2 | 314.3 | 255.8 | 281.6 | 247.6 | 287.6 | 287.9
1688.1 | 1536.1 | -6.8 | 0 | 0 | 265.9 | 259.6 | 237.7 | 236.1 | 260.4 | 52.2 | 18.7 | 79.9 | 3.7 | 159.3 | 6.1 | 365.9 | 218.8 | 95.2 | 317.3 | 349.3 | 425.4 | 287.8 | 177.3 | 399.9 | 373.4 | 226.6 | 295 | 314.1 | 255.8 | 281.2 | 247.2 | 287.6 | 287.5
1689.1 | 1537.1 | -6.8 | 0 | 0 | 265.5 | 259.2 | 237.4 | 235.8 | 259.9 | 52 | 18.7 | 79.8 | 3 | 160.5 | 5.9 | 364.4 | 218.2 | 94.7 | 315.3 | 347.8 | 424.1 | 287.8 | 177.6 | 398.4 | 372.1 | 226.7 | 294.8 | 313.9 | 255.8 | 280.8 | 246.8 | 287.5 | 287.2
1690.1 | 1538.1 | -6.8 | 0 | 0 | 265.1 | 258.6 | 237.1 | 235.4 | 259.4 | 51.7 | 18.7 | 79.7 | 3.4 | 157.1 | 5.6 | 362.8 | 217.5 | 94.4 | 314.2 | 346.2 | 422.8 | 287.1 | 177.6 | 396.9 | 371 | 226.7 | 294.6 | 313.7 | 255.9 | 280.2 | 246.4 | 287.4 | 286.8
1691.1 | 1539.1 | -6.8 | 0 | 0 | 264.7 | 258.1 | 236.8 | 235 | 259.1 | 51.6 | 18.7 | 79.6 | 3.4 | 177 | 5.2 | 361.8 | 216.9 | 94 | 313.6 | 345.1 | 421.6 | 287.4 | 176.8 | 395.4 | 369.8 | 226.8 | 294.5 | 313.5 | 255.9 | 279.5 | 246.1 | 287.4 | 286.5
1692.1 | 1540.1 | -6.8 | 0 | 0 | 264.4 | 257.7 | 236.4 | 234.6 | 258.9 | 51.6 | 18.7 | 79.5 | 3.2 | 170.8 | 4.7 | 360.8 | 214.9 | 93.6 | 312.8 | 344 | 420.3 | 285.5 | 175.7 | 393.9 | 368.5 | 226.8 | 294.3 | 313.3 | 256 | 278.9 | 245.8 | 287.3 | 286.2
1693.1 | 1541.1 | -6.8 | 0 | 0 | 263.9 | 257.3 | 236 | 234.3 | 258.6 | 51.6 | 18.8 | 79.4 | 3.4 | 163.7 | 4.5 | 359.9 | 213.4 | 93.4 | 311.8 | 342.9 | 419 | 285.5 | 175.1 | 393.3 | 367.7 | 226.9 | 294.1 | 313.1 | 256 | 278.3 | 245.5 | 287.3 | 285.8
1694.1 | 1542.1 | -6.8 | 0 | 0 | 263.5 | 257 | 235.5 | 233.9 | 258.2 | 51.5 | 18.8 | 79.3 | 3.6 | 167.1 | 4.5 | 358.6 | 212.5 | 93.2 | 309.9 | 341.9 | 417.8 | 285.3 | 173.7 | 392.5 | 366.7 | 227 | 293.9 | 312.8 | 256.1 | 277.9 | 245.1 | 287.2 | 285.5
1695.1 | 1543.1 | -6.8 | 0 | 0 | 263.3 | 256.7 | 235.1 | 233.6 | 257.8 | 51.5 | 18.8 | 79.2 | 3.8 | 158.5 | 4.3 | 357.5 | 211.1 | 92.9 | 309.1 | 340.9 | 416.4 | 285.2 | 172 | 391.7 | 365.3 | 227 | 293.8 | 312.6 | 256.1 | 277.5 | 244.8 | 287.2 | 285.2
1696.1 | 1544.1 | -6.8 | 0 | 0 | 263 | 256.3 | 234.7 | 233.2 | 257.5 | 51.5 | 18.8 | 79 | 3.4 | 158.1 | 4.2 | 356.4 | 208.2 | 92.6 | 308.5 | 339.9 | 415.1 | 284.3 | 170.7 | 390.3 | 364 | 227.1 | 293.6 | 312.4 | 256.1 | 277.1 | 244.4 | 287.1 | 284.8
1697.1 | 1545.1 | -6.8 | 0 | 0 | 262.6 | 256 | 234.3 | 232.8 | 257.2 | 51.6 | 18.8 | 78.9 | 3.5 | 187.4 | 4.1 | 355 | 207.5 | 92.4 | 306.6 | 339.1 | 413.9 | 281.7 | 169.6 | 389.2 | 362.7 | 227.1 | 293.5 | 312.2 | 256.2 | 276.7 | 244 | 287.1 | 284.5
1698.1 | 1546.1 | -6.8 | 0 | 0 | 262 | 255.7 | 234 | 232.4 | 256.9 | 51.7 | 18.8 | 78.8 | 3.6 | 177.2 | 4 | 353.7 | 206.4 | 92.1 | 305.7 | 338.4 | 412.6 | 280.6 | 168.6 | 388.7 | 361.8 | 227.2 | 293.3 | 312 | 256.2 | 276.4 | 243.6 | 287 | 284.1
1699.1 | 1547.1 | -6.8 | 0 | 0 | 261.6 | 255.3 | 233.7 | 232 | 256.5 | 51.7 | 18.8 | 78.7 | 3.4 | 168.5 | 4.2 | 352.5 | 205.8 | 91.8 | 304.8 | 337.6 | 411.3 | 279.8 | 167.7 | 388.4 | 361 | 227.3 | 293.2 | 311.8 | 256.3 | 276 | 243.2 | 286.9 | 283.7
1700.1 | 1548.1 | -6.8 | 0 | 0 | 261.1 | 255 | 233.4 | 231.7 | 256.1 | 51.8 | 18.8 | 78.6 | 3.5 | 174.7 | 4.5 | 351.3 | 204.2 | 91.5 | 304.8 | 336.3 | 409.9 | 278.7 | 167.3 | 388 | 360.3 | 227.3 | 293 | 311.5 | 256.3 | 275.7 | 242.8 | 286.9 | 283.4
1701.1 | 1549.1 | -6.8 | 0 | 0 | 260.5 | 254.6 | 233.1 | 231.3 | 255.9 | 51.8 | 18.8 | 78.5 | 3.4 | 167.1 | 4.5 | 350.1 | 202.5 | 91 | 303.9 | 335.2 | 408.6 | 277.2 | 166.7 | 387.1 | 359.7 | 227.4 | 292.8 | 311.3 | 256.3 | 275.3 | 242.4 | 286.8 | 283
1702.1 | 1550.1 | -6.8 | 0 | 0 | 260 | 254.2 | 232.8 | 230.8 | 255.6 | 51.9 | 18.8 | 78.4 | 3.1 | 155.1 | 4.5 | 349.2 | 202.1 | 90.7 | 303.5 | 334.3 | 407.4 | 277.5 | 165.6 | 386.5 | 358.4 | 227.4 | 292.7 | 311.1 | 256.4 | 274.8 | 241.9 | 286.8 | 282.7
1703.1 | 1551.1 | -6.8 | 0 | 0 | 259.6 | 253.6 | 232.5 | 230.5 | 255.3 | 51.8 | 18.8 | 78.4 | 3.4 | 168.5 | 3.9 | 347.7 | 201.2 | 90.7 | 301.2 | 332.8 | 406.2 | 277 | 164.8 | 385.8 | 357.4 | 227.5 | 292.5 | 310.9 | 256.4 | 274.3 | 241.5 | 286.7 | 282.4
1704.1 | 1552.1 | -6.8 | 0 | 0 | 259.7 | 253.2 | 232.3 | 230.1 | 254.9 | 51.7 | 18.8 | 78.3 | 3.3 | 197.5 | 4 | 345.9 | 200.4 | 90.5 | 299.6 | 331.6 | 405.1 | 276.3 | 164.6 | 384.6 | 356.1 | 227.5 | 292.4 | 310.7 | 256.5 | 273.9 | 241.1 | 286.7 | 282
1705.1 | 1553.1 | -6.8 | 0 | 0 | 259.2 | 252.8 | 231.9 | 229.7 | 254.5 | 51.7 | 18.8 | 78.1 | 3.2 | 184.3 | 4.4 | 344.7 | 199.4 | 90.5 | 298.2 | 330.4 | 404 | 275.8 | 164 | 383.3 | 354.8 | 227.6 | 292.2 | 310.5 | 256.5 | 273.7 | 240.8 | 286.6 | 281.7
1706.1 | 1554.1 | -6.8 | 0 | 0 | 258.8 | 252.5 | 231.6 | 229.4 | 254.1 | 51.6 | 18.8 | 78 | 3.3 | 171.8 | 4.7 | 343.4 | 198.3 | 90.1 | 296.1 | 329.2 | 402.9 | 274.1 | 163.7 | 381.7 | 353.7 | 227.7 | 292.1 | 310.3 | 256.6 | 273.5 | 240.3 | 286.6 | 281.3
1707.1 | 1555.1 | -6.8 | 0 | 0 | 258.4 | 252.2 | 231.3 | 229.2 | 253.8 | 51.3 | 18.8 | 78 | 3 | 190.6 | 4.7 | 341.5 | 197.6 | 89.9 | 294.1 | 328.3 | 401.8 | 273.3 | 163.4 | 380.6 | 352.7 | 227.7 | 291.9 | 310.1 | 256.6 | 273.1 | 240 | 286.5 | 281
1708.1 | 1556.1 | -6.8 | 0 | 0 | 258.4 | 251.9 | 231 | 228.8 | 253.5 | 51.2 | 18.8 | 77.9 | 3.2 | 187.7 | 5.1 | 339.8 | 196.9 | 89.4 | 292.7 | 326.8 | 400.7 | 271.8 | 162.5 | 379.5 | 351.4 | 227.8 | 291.8 | 309.8 | 256.7 | 272.8 | 239.6 | 286.4 | 280.7
1709.1 | 1557.1 | -6.8 | 0 | 0 | 258.3 | 251.6 | 230.7 | 228.4 | 253.2 | 51.1 | 18.8 | 77.8 | 3.6 | 181.3 | 5.4 | 338.7 | 196.4 | 89.1 | 291.9 | 325.3 | 399.6 | 270.5 | 162.4 | 378.2 | 350 | 227.9 | 291.6 | 309.6 | 256.7 | 272.5 | 239.2 | 286.4 | 280.4
1710.1 | 1558.1 | -6.8 | 0 | 0 | 258 | 251.3 | 230.5 | 228.1 | 253 | 51 | 18.8 | 77.7 | 3.6 | 182.9 | 5.4 | 337.5 | 195.6 | 88.9 | 290.5 | 324 | 398.6 | 269.5 | 161.4 | 376.7 | 349.1 | 227.9 | 291.5 | 309.4 | 256.7 | 272.2 | 238.8 | 286.3 | 280
1711.1 | 1559.1 | -6.8 | 0 | 0 | 257.5 | 250.9 | 230.1 | 227.8 | 252.7 | 50.8 | 18.8 | 77.6 | 3.6 | 182.1 | 5.9 | 336.2 | 195.8 | 88.6 | 288.4 | 322.6 | 397.5 | 269.2 | 160.2 | 375.4 | 348.1 | 228 | 291.3 | 309.2 | 256.8 | 271.9 | 238.5 | 286.3 | 279.7
1712.1 | 1560.1 | -6.8 | 0 | 0 | 256.8 | 250.6 | 229.8 | 227.4 | 252.5 | 50.6 | 18.8 | 77.5 | 3.5 | 186.2 | 6.3 | 334.5 | 195.4 | 88.2 | 287.1 | 321.3 | 396.3 | 268.5 | 159.3 | 374.2 | 346.8 | 228.1 | 291.2 | 309 | 256.8 | 271.7 | 238.1 | 286.2 | 279.4
1713.1 | 1561.1 | -6.8 | 0 | 0 | 256.3 | 250.3 | 229.5 | 227.1 | 252.2 | 50.5 | 18.8 | 77.3 | 3.4 | 191.7 | 6.6 | 333.8 | 194.4 | 87.9 | 286.8 | 320.3 | 395 | 266.8 | 158.5 | 372.8 | 345.6 | 228.1 | 291 | 308.8 | 256.9 | 271.4 | 237.9 | 286.1 | 279
1714.1 | 1562.1 | -6.8 | 0 | 0 | 255.9 | 250 | 229.2 | 226.8 | 251.9 | 50.4 | 18.8 | 77.2 | 3.2 | 201.3 | 7.3 | 332.9 | 193.9 | 87.7 | 285.5 | 319.1 | 393.9 | 266.4 | 157.4 | 371.5 | 344.4 | 228.2 | 290.9 | 308.6 | 256.9 | 271 | 237.6 | 286.1 | 278.7
1715.1 | 1563.1 | -6.8 | 0 | 0 | 255.5 | 249.7 | 228.9 | 226.5 | 251.5 | 50.3 | 18.8 | 77.1 | 3.2 | 190.8 | 7.2 | 331.8 | 193.3 | 87.5 | 284.6 | 317.8 | 392.8 | 266.2 | 156.8 | 370.7 | 343.2 | 228.2 | 290.7 | 308.4 | 257 | 270.7 | 237.3 | 286 | 278.3
1716.1 | 1564.1 | -6.8 | 0 | 0 | 255.3 | 249.3 | 228.7 | 226.2 | 251.1 | 50.2 | 18.8 | 77 | 3.3 | 194.8 | 6.9 | 331.1 | 192.3 | 87.2 | 284.5 | 316.7 | 391.7 | 265.6 | 156.8 | 369.9 | 342 | 228.3 | 290.5 | 308.1 | 257 | 270.4 | 237 | 285.9 | 278
1717.1 | 1565.1 | -6.8 | 0 | 0 | 255.2 | 249.1 | 228.4 | 225.8 | 250.7 | 50.2 | 18.8 | 76.8 | 3.1 | 200.6 | 6.1 | 330.5 | 191.5 | 86.7 | 284.8 | 315.7 | 390.6 | 265.4 | 156 | 368.9 | 341 | 228.4 | 290.4 | 307.9 | 257.1 | 270.1 | 236.6 | 285.9 | 277.7
1718.1 | 1566.1 | -6.8 | 0 | 0 | 254.8 | 248.7 | 228.1 | 225.4 | 250.4 | 50.2 | 18.8 | 76.7 | 2.9 | 174.7 | 5.2 | 330.1 | 190.6 | 86.2 | 283.5 | 314.8 | 389.5 | 265 | 155.2 | 368 | 339.8 | 228.4 | 290.2 | 307.7 | 257.1 | 269.8 | 236.2 | 285.8 | 277.4
1719.1 | 1567.1 | -6.7 | 0 | 0 | 254.6 | 248.4 | 227.8 | 225 | 250 | 50.1 | 18.8 | 76.6 | 3 | 199.9 | 6.1 | 329.4 | 189.5 | 85.7 | 281.9 | 313.6 | 388.3 | 263.6 | 154.9 | 367.2 | 338.8 | 228.5 | 290.1 | 307.5 | 257.2 | 269.5 | 235.9 | 285.7 | 277.1
1720.1 | 1568.1 | -6.7 | 0 | 0 | 254.2 | 248 | 227.5 | 224.7 | 249.6 | 49.9 | 18.8 | 76.5 | 3.1 | 192 | 7.1 | 328.5 | 189.7 | 85.3 | 280.9 | 312.6 | 387.2 | 262.2 | 154.5 | 366 | 337.7 | 228.6 | 289.9 | 307.3 | 257.2 | 269.2 | 235.5 | 285.6 | 276.8
1721.1 | 1569.1 | -6.7 | 0 | 0 | 253.8 | 247.6 | 227.1 | 224.3 | 249.3 | 49.8 | 18.8 | 76.4 | 3.3 | 185.9 | 6.8 | 327.7 | 189.5 | 85 | 280 | 311.7 | 386.1 | 262.1 | 154.3 | 364.9 | 336.6 | 228.6 | 289.8 | 307.1 | 257.2 | 268.9 | 235.2 | 285.6 | 276.5
1722.1 | 1570.1 | -6.8 | 0 | 0 | 253.4 | 247.2 | 226.7 | 224 | 249 | 49.7 | 18.8 | 76.3 | 3.5 | 181.3 | 6.6 | 327 | 189.5 | 84.9 | 279.6 | 310.8 | 385.1 | 262.4 | 154 | 364.2 | 335.8 | 228.7 | 289.6 | 306.9 | 257.3 | 268.6 | 234.9 | 285.5 | 276.1
1723.1 | 1571.1 | -6.8 | 0 | 0 | 252.7 | 246.9 | 226.5 | 223.7 | 248.6 | 49.6 | 18.8 | 76.2 | 3.2 | 182.8 | 7.2 | 326.2 | 188.8 | 84.8 | 279.4 | 309.8 | 384 | 262.3 | 154.1 | 363.6 | 334.8 | 228.8 | 289.5 | 306.7 | 257.3 | 268.3 | 234.6 | 285.4 | 275.8
1724.1 | 1572.1 | -6.8 | 0 | 0 | 252.4 | 246.5 | 226.2 | 223.4 | 248.2 | 49.4 | 18.8 | 76.1 | 3 | 177.4 | 7.4 | 325.3 | 187.1 | 84.6 | 278.2 | 308.8 | 382.9 | 261.6 | 153.6 | 362.4 | 333.6 | 228.9 | 289.3 | 306.5 | 257.4 | 268.1 | 234.2 | 285.4 | 275.5
1725.1 | 1573.1 | -6.8 | 0 | 0 | 252.2 | 246.2 | 225.9 | 223.1 | 247.9 | 49.3 | 18.8 | 76 | 3.1 | 176.4 | 7.4 | 324.1 | 187 | 84.4 | 275.8 | 308 | 382.1 | 260.6 | 153.2 | 361.3 | 332.5 | 228.9 | 289.2 | 306.3 | 257.4 | 267.8 | 233.9 | 285.3 | 275.2
1726.1 | 1574.1 | -6.8 | 0 | 0 | 252.1 | 245.9 | 225.6 | 222.8 | 247.6 | 49.2 | 18.8 | 75.9 | 3.1 | 177.7 | 7.3 | 322.3 | 187.4 | 84.2 | 274 | 307.2 | 381 | 261 | 152.8 | 360.5 | 331.3 | 229 | 289 | 306.1 | 257.4 | 267.4 | 233.5 | 285.2 | 274.9
1727.1 | 1575.1 | -6.7 | 0 | 0 | 252.1 | 245.5 | 225.3 | 222.5 | 247.3 | 49.2 | 18.8 | 75.8 | 2.9 | 204.7 | 7.7 | 320.7 | 187.1 | 83.9 | 273.3 | 306.2 | 380 | 260.3 | 152.3 | 359.4 | 330.3 | 229.1 | 288.9 | 305.9 | 257.5 | 267.1 | 233.2 | 285.1 | 274.5
1728.1 | 1576.1 | -6.7 | 0 | 0 | 252.1 | 245.1 | 225.1 | 222.2 | 247 | 49.2 | 18.8 | 75.7 | 2.9 | 201.3 | 7.3 | 319.4 | 186.4 | 83.5 | 272.8 | 305.2 | 379 | 260.6 | 151.5 | 358.6 | 329.2 | 229.1 | 288.8 | 305.7 | 257.5 | 266.7 | 232.8 | 285.1 | 274.2
1729.1 | 1577.1 | -6.7 | 0 | 0 | 251.8 | 244.6 | 224.8 | 221.8 | 246.7 | 49.1 | 18.8 | 75.7 | 2.9 | 206.8 | 7 | 318.3 | 185.3 | 83.3 | 272.2 | 304.3 | 378 | 260.9 | 150.7 | 357.8 | 328.1 | 229.2 | 288.6 | 305.5 | 257.6 | 266.3 | 232.5 | 285 | 273.9
1730.1 | 1578.1 | -6.7 | 0 | 0 | 251.6 | 244.2 | 224.5 | 221.5 | 246.3 | 49.1 | 18.9 | 75.6 | 3.1 | 189.9 | 6.6 | 317 | 184.3 | 83.1 | 270.9 | 303.1 | 377 | 260.6 | 150.6 | 356.6 | 327.1 | 229.3 | 288.5 | 305.2 | 257.6 | 265.8 | 232.2 | 284.9 | 273.6
1731.1 | 1579.1 | -6.7 | 0 | 0 | 251.2 | 243.9 | 224 | 221.2 | 245.9 | 49.1 | 18.9 | 75.5 | 3.7 | 202.2 | 6.2 | 316 | 184 | 82.6 | 269.7 | 302 | 376 | 259.2 | 150.3 | 355.5 | 326.4 | 229.3 | 288.3 | 305 | 257.7 | 265.2 | 231.8 | 284.8 | 273.3
1732.1 | 1580.1 | -6.8 | 0 | 0 | 250.8 | 243.6 | 223.6 | 220.9 | 245.5 | 49.1 | 18.8 | 75.4 | 3.3 | 207.2 | 6 | 315.3 | 183.2 | 82.1 | 269.5 | 301 | 374.9 | 258.5 | 150.2 | 354.8 | 325.8 | 229.4 | 288.1 | 304.8 | 257.7 | 264.7 | 231.5 | 284.7 | 272.9
1733.1 | 1581.1 | -6.8 | 0 | 0 | 250.3 | 243.3 | 223.2 | 220.6 | 245.2 | 49.1 | 18.9 | 75.3 | 3.3 | 186.8 | 5.8 | 314.5 | 182.4 | 82 | 268.8 | 299.7 | 373.9 | 258.6 | 149.7 | 354.2 | 325 | 229.5 | 288 | 304.7 | 257.7 | 264.1 | 231.1 | 284.7 | 272.6
1734.1 | 1582.1 | -6.8 | 0 | 0 | 249.7 | 243 | 222.9 | 220.4 | 245 | 49.1 | 18.9 | 75.2 | 3.2 | 194.2 | 5.7 | 313.3 | 181.8 | 81.7 | 268.2 | 298.8 | 372.8 | 257.3 | 149.9 | 353.4 | 323.8 | 229.6 | 287.8 | 304.5 | 257.8 | 263.5 | 230.8 | 284.6 | 272.3
1735.1 | 1583.1 | -6.7 | 0 | 0 | 249.3 | 242.6 | 222.6 | 220.1 | 244.7 | 49.1 | 18.9 | 75.1 | 3.3 | 198.4 | 5.9 | 312.2 | 182.1 | 81.2 | 266.9 | 297.8 | 371.8 | 256.3 | 149.2 | 352.5 | 322.8 | 229.6 | 287.7 | 304.2 | 257.8 | 263.1 | 230.4 | 284.5 | 272
1736.1 | 1584.1 | -6.7 | 0 | 0 | 249.2 | 242.3 | 222.3 | 219.7 | 244.3 | 49.1 | 18.9 | 75 | 2.9 | 180 | 5.8 | 311.6 | 181.6 | 80.9 | 265.9 | 296.8 | 370.7 | 256.9 | 149.6 | 351.9 | 322 | 229.7 | 287.6 | 304 | 257.8 | 262.7 | 230 | 284.5 | 271.7
1737.1 | 1585.1 | -6.6 | 0 | 0 | 248.9 | 241.9 | 222 | 219.4 | 244 | 49 | 18.9 | 75 | 3.1 | 174.7 | 5.1 | 311 | 181.2 | 80.5 | 265.1 | 295.8 | 369.7 | 256.3 | 149.1 | 351 | 321.6 | 229.8 | 287.4 | 303.8 | 257.9 | 262.3 | 229.7 | 284.3 | 271.4
1738.1 | 1586.1 | -6.7 | 0 | 0 | 248.5 | 241.6 | 221.7 | 219 | 243.7 | 48.8 | 18.9 | 74.9 | 3.2 | 183 | 4.4 | 310.3 | 180.3 | 80.3 | 264.5 | 295 | 368.8 | 254.1 | 148.3 | 349.6 | 320.6 | 229.9 | 287.3 | 303.6 | 257.9 | 262 | 229.3 | 284.2 | 271.1
1739.1 | 1587.1 | -6.8 | 0 | 0 | 248.3 | 241.4 | 221.5 | 218.7 | 243.5 | 48.7 | 18.9 | 74.8 | 3.1 | 193.6 | 4.1 | 309.5 | 179.2 | 80.2 | 263.3 | 293.8 | 367.8 | 254.5 | 148.2 | 348.6 | 319.3 | 229.9 | 287.2 | 303.4 | 258 | 261.7 | 229 | 284.2 | 270.8
1740.1 | 1588.1 | -6.8 | 0 | 0 | 247.9 | 241.1 | 221.2 | 218.4 | 243.2 | 48.7 | 18.9 | 74.8 | 2.9 | 194.3 | 4 | 308.9 | 178.4 | 79.9 | 262.7 | 292.5 | 366.8 | 254.6 | 147.7 | 347.6 | 318.2 | 230 | 287.1 | 303.2 | 258 | 261.4 | 228.7 | 284.1 | 270.5
1741.1 | 1589.1 | -6.8 | 0 | 0 | 247.5 | 240.8 | 221 | 218.1 | 243 | 48.7 | 18.9 | 74.7 | 2.6 | 191.2 | 3.7 | 308.7 | 177.1 | 79.7 | 262 | 291.3 | 365.8 | 254 | 147.1 | 346.5 | 317.4 | 230.1 | 286.9 | 303 | 258.1 | 261 | 228.4 | 284 | 270.2
1742.1 | 1590.1 | -6.8 | 0 | 0 | 247.2 | 240.5 | 220.8 | 217.8 | 242.7 | 48.7 | 18.9 | 74.6 | 3 | 182.1 | 3.2 | 307.9 | 176.5 | 79.7 | 260.2 | 290.3 | 364.8 | 251.7 | 146.1 | 345.1 | 316.2 | 230.2 | 286.8 | 302.8 | 258.1 | 260.7 | 228.1 | 283.9 | 269.9
1743.1 | 1591.1 | -6.8 | 0 | 0 | 247 | 240.1 | 220.5 | 217.5 | 242.5 | 48.7 | 18.9 | 74.5 | 2.9 | 166.5 | 2.9 | 307 | 176.1 | 79.4 | 259.1 | 289.4 | 363.8 | 250.6 | 145.6 | 343.9 | 315.5 | 230.2 | 286.7 | 302.6 | 258.1 | 260.3 | 227.7 | 283.8 | 269.5
1744.1 | 1592.1 | -6.8 | 0 | 0 | 246.7 | 239.7 | 220.2 | 217.3 | 242.2 | 48.6 | 18.9 | 74.5 | 3.1 | 165 | 3.7 | 306.3 | 176 | 79 | 258.5 | 288.3 | 362.8 | 250.8 | 145.2 | 343.1 | 314.6 | 230.3 | 286.5 | 302.4 | 258.2 | 259.9 | 227.4 | 283.8 | 269.3
1745.1 | 1593.1 | -6.7 | 0 | 0 | 246.8 | 239.3 | 220 | 217.1 | 241.9 | 48.6 | 18.9 | 74.4 | 3.3 | 175.2 | 5 | 305.7 | 175.8 | 78.7 | 258.4 | 287.6 | 361.9 | 250.8 | 144.9 | 342.3 | 313.8 | 230.4 | 286.4 | 302.2 | 258.2 | 259.5 | 227.1 | 283.7 | 268.9
1746.1 | 1594.1 | -6.7 | 0 | 0 | 246.3 | 239.1 | 219.7 | 216.8 | 241.6 | 48.5 | 18.9 | 74.3 | 3.1 | 173 | 6.8 | 304.8 | 175.7 | 78.4 | 257.4 | 286.8 | 361 | 248.5 | 144.6 | 341 | 312.9 | 230.5 | 286.3 | 302 | 258.3 | 259 | 226.7 | 283.6 | 268.6
1747.1 | 1595.1 | -6.7 | 0 | 0 | 246 | 238.8 | 219.4 | 216.5 | 241.3 | 48.6 | 18.9 | 74.2 | 3.3 | 177.6 | 7.6 | 304.3 | 174.8 | 78.2 | 256 | 285.8 | 360.1 | 248.1 | 144.4 | 340.2 | 312.2 | 230.5 | 286.2 | 301.8 | 258.3 | 258.5 | 226.3 | 283.5 | 268.3
1748.1 | 1596.1 | -6.7 | 0 | 0 | 245.5 | 238.5 | 219.1 | 216.2 | 241 | 48.6 | 18.9 | 74.2 | 3.3 | 170.5 | 7.6 | 303.5 | 174.1 | 77.9 | 254.5 | 284.8 | 359.2 | 246.7 | 144 | 339.1 | 311.3 | 230.6 | 286 | 301.6 | 258.3 | 258.3 | 225.9 | 283.4 | 268
1749.1 | 1597.1 | -6.7 | 0 | 0 | 244.8 | 237.9 | 218.7 | 215.9 | 240.8 | 48.6 | 18.9 | 74.1 | 3.5 | 167.5 | 7.4 | 302.7 | 173.9 | 77.5 | 253.2 | 283.8 | 358.2 | 246.6 | 143.3 | 338.3 | 310.2 | 230.7 | 285.9 | 301.4 | 258.3 | 258 | 225.6 | 283.3 | 267.7
1750.1 | 1598.1 | -6.8 | 0 | 0 | 244.4 | 237.4 | 218.4 | 215.7 | 240.5 | 48.5 | 18.9 | 74 | 3.1 | 166.1 | 7.5 | 301.9 | 173.3 | 77.4 | 252.7 | 283 | 357.3 | 245.7 | 143.1 | 337.3 | 309.4 | 230.8 | 285.7 | 301.2 | 258.3 | 257.5 | 225.4 | 283.2 | 267.4
1751.1 | 1599.1 | -6.7 | 0 | 0 | 244.2 | 237 | 218.1 | 215.4 | 240.1 | 48.4 | 18.9 | 73.8 | 3.3 | 163.7 | 8 | 300.8 | 171.8 | 77.3 | 251.6 | 282 | 356.3 | 245.2 | 142.6 | 336.6 | 308.7 | 230.9 | 285.6 | 301 | 258.4 | 257 | 225.1 | 283.1 | 267.1
1752.1 | 1600.1 | -6.6 | 0 | 0 | 244 | 236.6 | 217.8 | 215 | 239.8 | 48.3 | 18.9 | 73.7 | 3.2 | 166.9 | 8 | 299.9 | 170.1 | 77.1 | 251.2 | 281.3 | 355.4 | 244.6 | 142.6 | 336 | 308.1 | 230.9 | 285.4 | 300.8 | 258.4 | 256.7 | 224.8 | 283.1 | 266.8
1753.1 | 1601.1 | -6.6 | 0 | 0 | 244.1 | 236.3 | 217.5 | 214.7 | 239.5 | 48.3 | 18.9 | 73.6 | 2.9 | 174.8 | 7.7 | 299.1 | 168.6 | 76.9 | 250.9 | 280.3 | 354.4 | 244.2 | 142 | 335.2 | 307.3 | 231 | 285.3 | 300.6 | 258.5 | 256.4 | 224.5 | 283 | 266.5
1754.1 | 1602.1 | -6.4 | 0 | 0 | 243.7 | 235.9 | 217.2 | 214.4 | 239.1 | 48.4 | 18.9 | 73.5 | 3.2 | 179.2 | 7.4 | 298.3 | 167.4 | 76.7 | 250.6 | 279.5 | 353.5 | 243.6 | 142.2 | 334.5 | 306.5 | 231.1 | 285.2 | 300.4 | 258.5 | 256.2 | 224.2 | 282.8 | 266.2
1755.1 | 1603.1 | -6.2 | 0 | 0 | 243.3 | 235.5 | 216.8 | 214.1 | 238.8 | 48.4 | 18.9 | 73.4 | 2.8 | 181.7 | 6.7 | 297.6 | 166.5 | 76.6 | 249.8 | 278.6 | 352.6 | 242.9 | 141.7 | 333.9 | 305.9 | 231.2 | 285 | 300.2 | 258.5 | 255.9 | 223.8 | 282.8 | 265.9
1756.1 | 1604.1 | -6.4 | 0 | 0 | 242.7 | 235.2 | 216.5 | 213.9 | 238.5 | 48.4 | 18.9 | 73.4 | 2.9 | 207.3 | 5.6 | 297 | 166.2 | 76.4 | 249 | 277.8 | 351.6 | 243.1 | 141.1 | 333.2 | 305.3 | 231.3 | 284.9 | 300 | 258.6 | 255.5 | 223.5 | 282.7 | 265.6
1757.1 | 1605.1 | -6.4 | 0 | 0 | 242.3 | 234.9 | 216.1 | 213.6 | 238.1 | 48.4 | 18.9 | 73.3 | 3.3 | 229.8 | 5.1 | 296.4 | 165.5 | 76.1 | 248.4 | 277.1 | 350.6 | 241.2 | 141.4 | 332.6 | 304.8 | 231.3 | 284.8 | 299.8 | 258.6 | 254.9 | 223.2 | 282.6 | 265.3
1758.1 | 1606.1 | -6.2 | 0 | 0 | 242.1 | 234.6 | 215.8 | 213.4 | 237.7 | 48.3 | 18.9 | 73.2 | 3.2 | 206.5 | 4.8 | 295.7 | 164.5 | 75.8 | 247.6 | 276.4 | 349.7 | 240.3 | 141.3 | 332 | 304.2 | 231.4 | 284.6 | 299.6 | 258.6 | 254.7 | 222.9 | 282.5 | 265
1759.1 | 1607.1 | -6.4 | 0 | 0 | 241.9 | 234.2 | 215.5 | 213.1 | 237.3 | 48.2 | 18.9 | 73.1 | 3.4 | 203.7 | 4.7 | 294.4 | 164 | 75.9 | 245.9 | 275.6 | 348.9 | 238.7 | 141 | 331.4 | 303.8 | 231.5 | 284.5 | 299.4 | 258.7 | 254.4 | 222.5 | 282.4 | 264.6
1760.1 | 1608.1 | -6.7 | 0 | 0 | 241.6 | 233.8 | 215.2 | 212.6 | 237 | 48.2 | 18.9 | 73.1 | 3.1 | 204.5 | 4.6 | 292.2 | 164.2 | 75.7 | 243.7 | 274.5 | 348 | 237.7 | 140.7 | 330.8 | 302.8 | 231.6 | 284.4 | 299.2 | 258.7 | 254.1 | 222.2 | 282.4 | 264.4
1761.1 | 1609.1 | -6.4 | 0 | 0 | 241.2 | 233.4 | 215 | 212.2 | 236.7 | 48.1 | 18.9 | 73 | 3.3 | 204.9 | 4.3 | 290.7 | 164.1 | 75.6 | 242.2 | 273.5 | 347.1 | 236.3 | 140 | 329.8 | 301.8 | 231.7 | 284.2 | 299 | 258.7 | 253.7 | 221.9 | 282.3 | 264
1762.1 | 1610.1 | -6.1 | 0 | 0 | 240.9 | 233 | 214.7 | 211.8 | 236.4 | 48.1 | 18.9 | 72.9 | 3.3 | 205.5 | 4.2 | 289.5 | 163.9 | 75.4 | 240.9 | 272.5 | 346.3 | 236.4 | 140.3 | 328.8 | 301 | 231.7 | 284.1 | 298.9 | 258.8 | 253.3 | 221.6 | 282.2 | 263.7
1763.1 | 1611.1 | -6 | 0 | 0 | 240.6 | 232.7 | 214.4 | 211.5 | 236.2 | 48.1 | 18.9 | 72.9 | 3.1 | 203.6 | 4.2 | 288.5 | 164.1 | 75.4 | 239.6 | 271.8 | 345.5 | 235.3 | 140.3 | 327.8 | 300.2 | 231.8 | 283.9 | 298.7 | 258.8 | 252.9 | 221.3 | 282.1 | 263.4
1764.1 | 1612.1 | -6.4 | 0 | 0 | 240.3 | 232.3 | 214.1 | 211.2 | 235.9 | 48 | 18.9 | 72.7 | 3.1 | 187.8 | 4.2 | 287.8 | 162.8 | 75.4 | 238.7 | 271 | 344.5 | 234.7 | 139.9 | 326.9 | 299.3 | 231.9 | 283.8 | 298.5 | 258.8 | 252.5 | 221.1 | 282 | 263.1
1765.1 | 1613.1 | -6.8 | 0 | 0 | 240.2 | 232 | 213.9 | 211 | 235.7 | 48 | 18.9 | 72.6 | 3.4 | 174.5 | 4 | 287.1 | 161.4 | 75.3 | 237.8 | 270.3 | 343.6 | 233.6 | 139.6 | 326.3 | 298.5 | 232 | 283.7 | 298.3 | 258.9 | 252.1 | 220.7 | 281.9 | 262.9
1766.1 | 1614.1 | -6.8 | 0 | 0 | 240.1 | 231.7 | 213.6 | 210.7 | 235.3 | 48 | 18.9 | 72.5 | 3.3 | 172.5 | 3.5 | 286.5 | 159.8 | 75.1 | 237.5 | 269.7 | 342.6 | 232.5 | 139.2 | 325.7 | 297.5 | 232.1 | 283.5 | 298.1 | 258.9 | 251.7 | 220.4 | 281.8 | 262.6
1767.1 | 1615.1 | -6.7 | 0 | 0 | 239.9 | 231.2 | 213.3 | 210.3 | 234.9 | 47.9 | 18.9 | 72.4 | 3.3 | 173.1 | 3.2 | 286.1 | 159.2 | 74.9 | 237.2 | 268.9 | 341.7 | 232.2 | 138.8 | 325.1 | 297.1 | 232.1 | 283.4 | 297.9 | 258.9 | 251.2 | 220 | 281.7 | 262.3
1768.1 | 1616.1 | -6.7 | 0 | 0 | 239.6 | 230.8 | 213 | 209.9 | 234.5 | 47.9 | 18.9 | 72.3 | 3.5 | 181.5 | 4.1 | 286 | 157.9 | 74.5 | 236.9 | 268 | 340.8 | 230.9 | 138.8 | 324.2 | 296.1 | 232.2 | 283.2 | 297.7 | 258.9 | 250.9 | 219.7 | 281.6 | 262
1769.1 | 1617.1 | -6.7 | 0 | 0 | 239.3 | 230.5 | 212.7 | 209.6 | 234.2 | 47.8 | 18.9 | 72.2 | 3.7 | 187.6 | 5.1 | 285.6 | 156.8 | 74.2 | 236.3 | 267.3 | 339.9 | 229.3 | 139 | 323.5 | 295.4 | 232.3 | 283.1 | 297.5 | 258.9 | 250.7 | 219.5 | 281.5 | 261.7
1770.1 | 1618.1 | -6.7 | 0 | 0 | 238.9 | 230.3 | 212.6 | 209.4 | 234 | 47.8 | 18.9 | 72.1 | 3.4 | 189 | 5.2 | 284.9 | 156.7 | 73.9 | 235.6 | 266.6 | 339.1 | 228.1 | 138.5 | 322.9 | 294.5 | 232.4 | 283 | 297.3 | 259 | 250.4 | 219.2 | 281.4 | 261.4
1771.1 | 1619.1 | -6.6 | 0 | 0 | 238.6 | 229.9 | 212.2 | 209 | 233.7 | 47.7 | 19 | 72.1 | 3.5 | 189.5 | 5.1 | 284.4 | 156.4 | 73.6 | 235.2 | 265.8 | 338.3 | 227.1 | 137.3 | 322.1 | 293.8 | 232.5 | 282.8 | 297.2 | 259 | 250.2 | 219 | 281.3 | 261.1
1772.1 | 1620.1 | -6.6 | 0 | 0 | 238.5 | 229.6 | 212 | 208.8 | 233.3 | 47.7 | 19 | 72 | 3.6 | 186.7 | 5.4 | 284.1 | 155.3 | 73.2 | 234.9 | 265.1 | 337.4 | 226.1 | 136.5 | 321.4 | 293 | 232.5 | 282.7 | 297 | 259 | 249.9 | 218.7 | 281.2 | 260.8
1773.1 | 1621.1 | -6.6 | 0 | 0 | 238 | 229.2 | 211.7 | 208.5 | 233 | 47.6 | 19 | 71.9 | 3.8 | 185 | 6.4 | 283.7 | 154.3 | 73 | 234.2 | 264.2 | 336.5 | 224.6 | 136.8 | 320.9 | 292.8 | 232.6 | 282.5 | 296.8 | 259.1 | 249.6 | 218.5 | 281.1 | 260.5
1774.1 | 1622.1 | -6.6 | 0 | 0 | 237.3 | 228.8 | 211.3 | 208.3 | 232.8 | 47.5 | 19 | 71.9 | 3.9 | 183.9 | 7.1 | 282.8 | 154.3 | 72.7 | 233.3 | 263.3 | 335.6 | 223 | 136.8 | 320.2 | 291.9 | 232.7 | 282.3 | 296.6 | 259.1 | 249.4 | 218.3 | 281.1 | 260.3
1775.1 | 1623.1 | -6.6 | 0 | 0 | 236.7 | 228.5 | 210.9 | 208.1 | 232.5 | 47.4 | 19 | 71.8 | 3.8 | 185.7 | 7.4 | 281.8 | 153.9 | 72.6 | 232.1 | 262.5 | 334.7 | 221.3 | 136.2 | 319.2 | 291 | 232.8 | 282.2 | 296.4 | 259.1 | 249 | 218.1 | 281 | 260
1776.1 | 1624.1 | -6.6 | 0 | 0 | 236 | 228.1 | 210.7 | 207.9 | 232.2 | 47.3 | 19 | 71.7 | 3.5 | 184.5 | 7.5 | 281 | 152.6 | 72.4 | 230.8 | 261.6 | 333.9 | 220.6 | 135.4 | 318.2 | 290.2 | 232.8 | 282 | 296.2 | 259.1 | 248.7 | 217.9 | 280.8 | 259.7
1777.1 | 1625.1 | -6.6 | 0 | 0 | 235.8 | 227.7 | 210.3 | 207.7 | 231.8 | 47.2 | 19 | 71.6 | 3.2 | 183.3 | 7.5 | 280.1 | 153 | 72.2 | 229.7 | 260.9 | 333 | 220.2 | 135.3 | 317.3 | 289.6 | 232.9 | 281.9 | 296 | 259.1 | 248.3 | 217.7 | 280.7 | 259.4
1778.1 | 1626.1 | -6.5 | 0 | 0 | 235.7 | 227.4 | 210 | 207.5 | 231.5 | 47.1 | 19 | 71.6 | 3 | 175.5 | 7.4 | 279.6 | 152.8 | 71.9 | 229.2 | 260.1 | 332.3 | 219.9 | 135.6 | 316.2 | 288.6 | 233 | 281.7 | 295.8 | 259.2 | 248.1 | 217.4 | 280.6 | 259.1
1779.1 | 1627.1 | -6.5 | 0 | 0 | 235.4 | 227.2 | 209.6 | 207.3 | 231.2 | 47 | 19 | 71.6 | 3.3 | 179.2 | 6.9 | 279.2 | 152 | 71.7 | 228.8 | 259.3 | 331.5 | 218.7 | 135.2 | 314.9 | 287.7 | 233.1 | 281.6 | 295.7 | 259.2 | 247.9 | 217.1 | 280.5 | 258.9
1780.1 | 1628.1 | -6.5 | 0 | 0 | 235.2 | 226.9 | 209.3 | 207 | 231 | 46.9 | 19 | 71.5 | 3.6 | 179.3 | 6.6 | 278.6 | 150.9 | 71.7 | 227.7 | 258.7 | 330.7 | 218.4 | 134.4 | 313.9 | 286.9 | 233.2 | 281.5 | 295.5 | 259.2 | 247.6 | 216.9 | 280.5 | 258.6
1781.1 | 1629.1 | -6.6 | 0 | 0 | 234.8 | 226.7 | 209 | 206.8 | 230.8 | 46.8 | 19 | 71.5 | 3.8 | 180 | 6.3 | 277.7 | 151 | 71.5 | 226.5 | 257.7 | 329.9 | 218.8 | 134.1 | 313 | 286.3 | 233.3 | 281.3 | 295.3 | 259.3 | 247.2 | 216.6 | 280.4 | 258.3
1782.1 | 1630.1 | -6.5 | 0 | 0 | 235.1 | 226.3 | 208.7 | 206.6 | 230.6 | 46.8 | 19 | 71.4 | 3.8 | 181.1 | 5.8 | 277.1 | 151.4 | 71.3 | 225.8 | 256.7 | 329.1 | 218.6 | 133.5 | 312 | 285.3 | 233.3 | 281.2 | 295.1 | 259.3 | 246.8 | 216.4 | 280.3 | 258.1
1783.1 | 1631.1 | -6.6 | 0 | 0 | 235.2 | 226 | 208.4 | 206.4 | 230.4 | 46.8 | 19 | 71.3 | 3.7 | 178 | 5.9 | 276 | 151.9 | 71.2 | 224.2 | 256.2 | 328.3 | 218.2 | 132.8 | 310.9 | 284.5 | 233.4 | 281.1 | 294.9 | 259.3 | 246.4 | 216.1 | 280.2 | 257.8
1784.1 | 1632.1 | -6.7 | 0 | 0 | 234.8 | 225.7 | 208.2 | 206.2 | 230 | 46.8 | 19 | 71.3 | 3.5 | 179.5 | 5.8 | 275 | 151.6 | 71 | 223.3 | 255.5 | 327.3 | 217.6 | 132.4 | 309.7 | 283.5 | 233.5 | 280.9 | 294.7 | 259.3 | 246 | 215.9 | 280.1 | 257.5
1785.1 | 1633.1 | -6.7 | 0 | 0 | 234.3 | 225.3 | 208 | 205.9 | 229.8 | 46.8 | 19 | 71.2 | 3.3 | 182.6 | 5.4 | 273.9 | 151.5 | 71.1 | 222.1 | 254.7 | 326.5 | 216.8 | 132.3 | 308.7 | 282.7 | 233.6 | 280.8 | 294.5 | 259.4 | 245.7 | 215.6 | 280 | 257.2
1786.1 | 1634.1 | -6.7 | 0 | 0 | 233.7 | 224.9 | 207.6 | 205.7 | 229.4 | 46.7 | 19 | 71.2 | 3.4 | 187.3 | 5.5 | 272.4 | 151.1 | 71 | 220.5 | 253.8 | 325.6 | 215.8 | 131.7 | 307.9 | 282 | 233.6 | 280.7 | 294.4 | 259.4 | 245.4 | 215.3 | 279.9 | 256.9
1787.1 | 1635.1 | -6.5 | 0 | 0 | 233.3 | 224.5 | 207.2 | 205.4 | 229.1 | 46.7 | 19 | 71.2 | 3.5 | 181.6 | 5.5 | 271.9 | 150.9 | 70.7 | 220.2 | 253 | 324.9 | 215.2 | 131.5 | 306.8 | 281.2 | 233.7 | 280.5 | 294.2 | 259.4 | 245.1 | 215 | 279.8 | 256.6
1788.1 | 1636.1 | -6.5 | 0 | 0 | 232.6 | 224.3 | 207 | 205.1 | 228.8 | 46.6 | 19 | 71.1 | 3.4 | 181.5 | 5.7 | 271.4 | 150.9 | 70.5 | 219.6 | 252.2 | 324.2 | 214.3 | 130.8 | 305.9 | 280.5 | 233.8 | 280.4 | 294 | 259.4 | 244.8 | 214.8 | 279.7 | 256.3
1789.1 | 1637.1 | -6.5 | 0 | 0 | 232.3 | 224.1 | 206.8 | 204.8 | 228.5 | 46.6 | 19 | 71 | 3.6 | 179.1 | 6.1 | 270.8 | 150.6 | 70.3 | 219 | 251.2 | 323.2 | 214.4 | 130.2 | 305.3 | 280.3 | 233.9 | 280.3 | 293.8 | 259.5 | 244.5 | 214.6 | 279.6 | 256
1790.1 | 1638.1 | -6.5 | 0 | 0 | 231.9 | 223.7 | 206.6 | 204.5 | 228.2 | 46.5 | 19 | 70.9 | 3.2 | 176.5 | 5.7 | 270.1 | 150.6 | 70.2 | 218.6 | 250.4 | 322.3 | 214.3 | 129.7 | 304.6 | 279.4 | 233.9 | 280.1 | 293.6 | 259.5 | 244.3 | 214.4 | 279.5 | 255.8
1791.1 | 1639.1 | -6.5 | 0 | 0 | 231.2 | 223.3 | 206.4 | 204.1 | 227.9 | 46.4 | 19 | 70.8 | 3.2 | 195.3 | 5.1 | 269.4 | 150.2 | 70.1 | 217.3 | 249.6 | 321.5 | 214.4 | 129.3 | 303.9 | 278.6 | 234 | 280 | 293.4 | 259.5 | 244.1 | 214.1 | 279.4 | 255.5
1792.1 | 1640.1 | -6.5 | 0 | 0 | 230.6 | 222.9 | 206.1 | 203.7 | 227.5 | 46.3 | 19 | 70.7 | 3.2 | 190.5 | 4.9 | 268.3 | 149.6 | 70 | 215.7 | 248.8 | 320.5 | 214.1 | 129.1 | 303.1 | 278.2 | 234.1 | 279.9 | 293.3 | 259.5 | 243.8 | 213.8 | 279.2 | 255.3
1793.1 | 1641.1 | -6.5 | 0 | 0 | 230.5 | 222.6 | 205.7 | 203.5 | 227.2 | 46.3 | 19 | 70.7 | 3.4 | 182.3 | 4.2 | 267.6 | 149.1 | 70 | 214.8 | 248.1 | 319.7 | 214 | 128.6 | 302.3 | 277.3 | 234.2 | 279.7 | 293.1 | 259.5 | 243.4 | 213.5 | 279.1 | 255
1794.1 | 1642.1 | -6.6 | 0 | 0 | 230.3 | 222.4 | 205.3 | 203.3 | 226.9 | 46.2 | 19 | 70.6 | 3.4 | 192.8 | 3.9 | 266.7 | 148.6 | 69.9 | 213.9 | 247.3 | 319 | 213.4 | 128.7 | 301.6 | 276.7 | 234.2 | 279.6 | 292.9 | 259.5 | 243.2 | 213.2 | 279 | 254.7
1795.1 | 1643.1 | -6.6 | 0 | 0 | 229.9 | 222.1 | 205 | 203.1 | 226.6 | 46.1 | 19 | 70.5 | 3.1 | 209 | 4 | 266 | 148.7 | 69.8 | 213.3 | 246.5 | 318.1 | 211.9 | 128.4 | 300.6 | 275.9 | 234.3 | 279.5 | 292.7 | 259.5 | 243 | 213 | 278.9 | 254.4
1796.1 | 1644.1 | -6.7 | 0 | 0 | 229.4 | 221.8 | 204.7 | 202.8 | 226.3 | 46.1 | 19 | 70.5 | 3.4 | 203.4 | 4.3 | 265.3 | 148.6 | 69.4 | 212 | 245.6 | 317.3 | 211.4 | 127.9 | 299.6 | 275.3 | 234.4 | 279.3 | 292.5 | 259.6 | 242.7 | 212.8 | 278.8 | 254.1
1797.1 | 1645.1 | -6.7 | 0 | 0 | 228.9 | 221.5 | 204.5 | 202.5 | 226.1 | 46.2 | 19 | 70.4 | 3.4 | 215.3 | 4.6 | 264.3 | 148.7 | 69.4 | 210.5 | 244.8 | 316.5 | 210 | 127.8 | 298.6 | 274.5 | 234.5 | 279.2 | 292.3 | 259.6 | 242.4 | 212.5 | 278.7 | 253.9
1798.1 | 1646.1 | -6.6 | 0 | 0 | 228.3 | 221.1 | 204.4 | 202.2 | 226 | 46.2 | 19 | 70.3 | 3.4 | 209 | 4.9 | 263.5 | 148.7 | 69.2 | 209.8 | 243.9 | 315.8 | 209.4 | 127.8 | 297.9 | 273.9 | 234.5 | 279.1 | 292.1 | 259.6 | 241.9 | 212.3 | 278.6 | 253.6
1799.1 | 1647.1 | -6 | 0 | 0 | 228.2 | 220.7 | 204.2 | 201.9 | 225.8 | 46.2 | 19.1 | 70.3 | 3.3 | 201.2 | 5.2 | 262.9 | 148.7 | 69.2 | 209.4 | 243.4 | 315.1 | 209.6 | 127.3 | 297.1 | 273.3 | 234.6 | 278.9 | 292 | 259.6 | 241.5 | 212 | 278.5 | 253.3
1800.1 | 1648.1 | -6 | 0 | 0 | 228.5 | 220.4 | 203.9 | 201.6 | 225.6 | 46.1 | 19.1 | 70.2 | 3.2 | 219.6 | 4.9 | 262.3 | 148.9 | 69.1 | 208.7 | 242.8 | 314.2 | 210.2 | 126.7 | 296.1 | 272.5 | 234.7 | 278.8 | 291.8 | 259.6 | 241.2 | 211.7 | 278.4 | 253.1
1801.1 | 1649.1 | -6.4 | 0 | 0 | 228.4 | 220 | 203.7 | 201.3 | 225.3 | 46.1 | 19.1 | 70.1 | 3.1 | 258.5 | 4.1 | 261.9 | 148.9 | 68.9 | 208.2 | 242 | 313.6 | 209.9 | 126 | 295.3 | 271.6 | 234.8 | 278.7 | 291.6 | 259.7 | 241 | 211.4 | 278.3 | 252.8
1802.1 | 1650.1 | -6.6 | 0 | 0 | 228.2 | 219.5 | 203.4 | 201 | 225.1 | 46.1 | 19.1 | 70.1 | 3.2 | 243.8 | 3.3 | 261.1 | 148.2 | 68.8 | 207.5 | 241 | 312.8 | 209.6 | 125.8 | 294.7 | 271 | 234.9 | 278.6 | 291.4 | 259.7 | 240.7 | 211.2 | 278.2 | 252.5
1803.1 | 1651.1 | -6.7 | 0 | 0 | 227.6 | 219.1 | 203.2 | 200.7 | 224.8 | 46.1 | 19.1 | 70 | 3.1 | 217.3 | 3 | 260.3 | 148.3 | 68.7 | 206.8 | 240.3 | 312 | 209.6 | 126.2 | 294.3 | 270.6 | 234.9 | 278.5 | 291.2 | 259.7 | 240.3 | 210.9 | 278.1 | 252.3
1804.1 | 1652.1 | -6.7 | 0 | 0 | 226.9 | 218.6 | 202.9 | 200.5 | 224.5 | 46 | 19.1 | 69.9 | 3.2 | 217.2 | 2.9 | 259.8 | 148.2 | 68.6 | 206.6 | 239.6 | 311.3 | 210 | 126.1 | 293.9 | 270 | 235 | 278.3 | 291 | 259.7 | 240 | 210.7 | 278 | 252
1805.1 | 1653.1 | -6.7 | 0 | 0 | 226.6 | 218.1 | 202.7 | 200.3 | 224.3 | 45.9 | 19.1 | 69.8 | 2.9 | 231.1 | 3.1 | 259.6 | 148.6 | 68.5 | 206.7 | 238.9 | 310.5 | 210 | 125.6 | 293.1 | 269.2 | 235.1 | 278.2 | 290.8 | 259.7 | 239.6 | 210.4 | 277.9 | 251.7
1806.1 | 1654.1 | -6.6 | 0 | 0 | 226.6 | 217.7 | 202.4 | 200 | 224.1 | 45.7 | 19.1 | 69.7 | 3 | 233.3 | 3.1 | 259.4 | 148.6 | 68.3 | 206.8 | 238.1 | 309.8 | 210.1 | 124.8 | 292.3 | 268.3 | 235.2 | 278 | 290.7 | 259.7 | 239.2 | 210.2 | 277.8 | 251.4
1807.1 | 1655.1 | -6.5 | 0 | 0 | 226.6 | 217.3 | 202.1 | 199.6 | 223.9 | 45.6 | 19.1 | 69.6 | 3.1 | 237.8 | 2.8 | 259.1 | 148.2 | 68.2 | 206.4 | 237.2 | 309.2 | 210.1 | 124.5 | 291.7 | 267.8 | 235.2 | 277.9 | 290.5 | 259.7 | 238.8 | 210 | 277.6 | 251.2
1808.1 | 1656.1 | -6.5 | 0 | 0 | 226.5 | 216.8 | 201.8 | 199.1 | 223.7 | 45.6 | 19.1 | 69.5 | 2.7 | 229.4 | 2.8 | 258.1 | 147.9 | 68 | 205 | 236.5 | 308.5 | 209.1 | 124.3 | 290.9 | 266.9 | 235.3 | 277.8 | 290.3 | 259.8 | 238.5 | 209.7 | 277.6 | 250.9
1809.1 | 1657.1 | -6.5 | 0 | 0 | 226.1 | 216.5 | 201.5 | 198.8 | 223.5 | 45.6 | 19.1 | 69.5 | 3.1 | 225.8 | 2.8 | 256.9 | 146.6 | 67.7 | 203.5 | 235.6 | 307.7 | 208 | 123.8 | 290.1 | 266.2 | 235.4 | 277.7 | 290.1 | 259.8 | 238.1 | 209.4 | 277.4 | 250.7
1810.1 | 1658.1 | -6.5 | 0 | 0 | 225.9 | 216.2 | 201.1 | 198.4 | 223.3 | 45.6 | 19.1 | 69.4 | 3.1 | 243.4 | 2.7 | 256.2 | 144.8 | 67.6 | 202.4 | 234.7 | 307.1 | 207.9 | 123.7 | 289.5 | 265.8 | 235.5 | 277.5 | 289.9 | 259.8 | 237.8 | 209.1 | 277.3 | 250.4
1811.1 | 1659.1 | -6.7 | 0 | 0 | 226 | 215.9 | 200.7 | 198 | 223.1 | 45.4 | 19.1 | 69.3 | 3.1 | 250.7 | 2.7 | 255.6 | 144.5 | 67.4 | 202 | 233.8 | 306.4 | 207.2 | 123.1 | 289 | 265 | 235.5 | 277.4 | 289.7 | 259.8 | 237.5 | 208.9 | 277.2 | 250.1
1812.1 | 1660.1 | -6.7 | 0 | 0 | 225.7 | 215.6 | 200.6 | 197.6 | 222.8 | 45.3 | 19.1 | 69.2 | 3.3 | 242.6 | 3.1 | 254.7 | 144.3 | 67.1 | 201.5 | 233.2 | 305.6 | 206.9 | 122.8 | 288.5 | 264.3 | 235.6 | 277.3 | 289.5 | 259.9 | 237.2 | 208.6 | 277.1 | 249.9
1813.1 | 1661.1 | -6.7 | 0 | 0 | 225.7 | 215.2 | 200.4 | 197.4 | 222.6 | 45.2 | 19.1 | 69.1 | 3.5 | 233.7 | 3.4 | 254.2 | 144.2 | 66.9 | 200.9 | 232.4 | 305 | 205.3 | 122.6 | 288 | 263.6 | 235.7 | 277.1 | 289.4 | 259.9 | 236.9 | 208.3 | 277 | 249.7
1814.1 | 1662.1 | -6.6 | 0 | 0 | 225.4 | 214.8 | 200.2 | 197.1 | 222.3 | 45.1 | 19.1 | 69 | 3.3 | 234.3 | 3.4 | 253.8 | 143.7 | 66.7 | 200.7 | 231.5 | 304.4 | 204.8 | 122.9 | 287.5 | 263.2 | 235.7 | 277 | 289.2 | 259.9 | 236.6 | 208 | 276.8 | 249.4
1815.1 | 1663.1 | -6.6 | 0 | 0 | 224.9 | 214.5 | 199.9 | 196.9 | 222.1 | 44.9 | 19.1 | 69 | 3.3 | 248.2 | 3.3 | 253.6 | 143.3 | 66.6 | 200.2 | 230.7 | 303.8 | 204.1 | 122.3 | 286.7 | 262.5 | 235.8 | 276.9 | 289 | 259.9 | 236.3 | 207.7 | 276.7 | 249.1
1816.1 | 1664.1 | -6.5 | 0 | 0 | 224.2 | 214.3 | 199.7 | 196.6 | 221.8 | 44.8 | 19.1 | 69 | 3.3 | 264.3 | 3.1 | 253.1 | 142.7 | 66.5 | 199.4 | 229.9 | 303.1 | 203.4 | 121.9 | 286.2 | 262.1 | 235.9 | 276.8 | 288.8 | 259.9 | 236.1 | 207.4 | 276.7 | 248.9
1817.1 | 1665.1 | -6.4 | 0 | 0 | 223.6 | 214.1 | 199.6 | 196.4 | 221.6 | 44.8 | 19.1 | 68.9 | 3.4 | 262.8 | 2.9 | 252 | 141.9 | 66.4 | 198.5 | 229.3 | 302.5 | 202.7 | 121.7 | 285.6 | 261.5 | 236 | 276.6 | 288.6 | 259.9 | 235.9 | 207.1 | 276.5 | 248.6
1818.1 | 1666.1 | -6.5 | 0 | 0 | 223.4 | 214.1 | 199.4 | 196.1 | 221.4 | 44.7 | 19.1 | 68.9 | 3.1 | 245.6 | 2.5 | 251.5 | 141.7 | 66.4 | 197.9 | 228.7 | 301.8 | 202.3 | 121.1 | 284.7 | 260.6 | 236 | 276.5 | 288.5 | 259.9 | 235.6 | 206.8 | 276.4 | 248.3
1819.1 | 1667.1 | -6.6 | 0 | 0 | 223 | 213.9 | 199.2 | 195.9 | 221.1 | 44.6 | 19.1 | 68.9 | 3.3 | 220.1 | 2.2 | 251.2 | 141.7 | 66.2 | 197.7 | 228 | 301.1 | 201.7 | 120.3 | 284.1 | 260.1 | 236.1 | 276.4 | 288.3 | 259.9 | 235.2 | 206.5 | 276.3 | 248.1
1820.1 | 1668.1 | -6.5 | 0 | 0 | 222.4 | 213.7 | 198.9 | 195.6 | 220.8 | 44.5 | 19.1 | 68.8 | 3.2 | 212.4 | 2 | 251 | 140.9 | 66.1 | 197.5 | 227.3 | 300.5 | 200.9 | 119.8 | 283.5 | 259.4 | 236.2 | 276.2 | 288.1 | 259.9 | 235 | 206.2 | 276.2 | 247.8
1821.1 | 1669.1 | -6.6 | 0 | 0 | 221.9 | 213.4 | 198.7 | 195.4 | 220.6 | 44.4 | 19.1 | 68.7 | 3.2 | 222.1 | 1.9 | 250.7 | 139.8 | 65.9 | 197.2 | 226.7 | 299.8 | 199.8 | 120.1 | 283.1 | 259.1 | 236.2 | 276.1 | 287.9 | 259.9 | 234.7 | 206 | 276.1 | 247.6
1822.1 | 1670.1 | -6.7 | 0 | 0 | 221.4 | 213.1 | 198.2 | 195.1 | 220.2 | 44.3 | 19.1 | 68.7 | 3.4 | 229.1 | 2.2 | 250.3 | 138.9 | 65.9 | 196.7 | 226.1 | 299.2 | 199.4 | 119.4 | 282.6 | 258.7 | 236.3 | 276 | 287.8 | 259.9 | 234.4 | 205.7 | 276 | 247.3
1823.1 | 1671.1 | -6.6 | 0 | 0 | 221 | 212.8 | 197.8 | 194.9 | 219.8 | 44.2 | 19.1 | 68.6 | 3.3 | 228.1 | 2.4 | 249.3 | 137.7 | 65.8 | 195.8 | 225.6 | 298.5 | 199.5 | 118.9 | 282.3 | 258.1 | 236.4 | 275.8 | 287.6 | 260 | 234.1 | 205.5 | 275.9 | 247
1824.1 | 1672.1 | -6.5 | 0 | 0 | 220.6 | 212.5 | 197.4 | 194.8 | 219.5 | 44.2 | 19.1 | 68.6 | 3.3 | 225.5 | 2.3 | 248.3 | 137.1 | 65.8 | 195.7 | 225.1 | 297.8 | 199.3 | 118.6 | 282 | 257.8 | 236.5 | 275.7 | 287.4 | 260 | 233.7 | 205.2 | 275.8 | 246.8
1825.1 | 1673.1 | -6.3 | 0 | 0 | 220.4 | 212.1 | 197 | 194.6 | 219.2 | 44.1 | 19.1 | 68.5 | 2.9 | 221.5 | 2.2 | 247.7 | 135.5 | 65.8 | 195.9 | 224.6 | 297.1 | 198.9 | 119.2 | 281.7 | 257.6 | 236.5 | 275.6 | 287.2 | 260 | 233.4 | 205 | 275.7 | 246.6

## First Electrical Failures
SCDU-4 At Location G | Time (s) | Offset Time (s) | C4 V1 | C4 V5
| 0 | -152 | 129.0608 | 0.064722
| 60 | -92 | 128.6713 | 0.1621
| 120 | -32 | 128.2817 | 0.1621
| 180 | 28 | 128.5738 | 0.25952
| 240 | 88 | 128.3791 | 0.1621
| 300 | 148 | 128.8661 | 0.25952
| 360 | 208 | 128.7686 | 0.3569
| 420 | 268 | 125.4571 | 0.25952
| 480 | 328 | 128.3791 | 0.3569
| 540 | 388 | 128.3791 | 0.3569
| 600 | 448 | 128.5738 | 0.3569
| 660 | 508 | 128.6713 | 0.3569
| 720 | 568 | 128.5738 | 0.45428
| 780 | 628 | 128.7686 | 0.3569
| 840 | 688 | 128.4765 | 0.45428
| 900 | 748 | 128.7686 | 0.45428
| 960 | 808 | 128.5738 | 0.45428
| 1020 | 868 | 128.4765 | 0.3569
| 1080 | 928 | 128.7686 | 0.45428
| 1140 | 988 | 128.7686 | 0.45428
| 1200 | 1048 | 128.7686 | 0.45428
| 1260 | 1108 | 128.6713 | 0.45428
| 1320 | 1168 | 128.9634 | 0.45428
| 1380 | 1228 | 128.6713 | 0.45428
| 1430 | 1278 | 129.1582 | 0.5517
| 1430.2 | 1278.2 | 129.1582 | 0.5517
| 1430.4 | 1278.4 | 129.1582 | 0.45428
| 1430.6 | 1278.6 | 129.0608 | 0.45428
| 1430.8 | 1278.8 | 129.0608 | 0.45428
| 1431 | 1279 | 129.0608 | 0.45428
| 1431.2 | 1279.2 | 129.0608 | 0.45428
| 1431.4 | 1279.4 | 128.9634 | 0.45428
| 1431.6 | 1279.6 | 129.0608 | 0.5517
| 1431.8 | 1279.8 | 129.1582 | 0.5517
| 1432 | 1280 | 129.0608 | 0.5517
| 1432.2 | 1280.2 | 129.1582 | 0.5517
| 1432.4 | 1280.4 | 129.1582 | 0.45428
| 1432.6 | 1280.6 | 129.1582 | 0.5517
| 1432.8 | 1280.8 | 129.0608 | 0.45428
| 1433 | 1281 | 129.1582 | 0.45428
| 1433.2 | 1281.2 | 129.1582 | 0.5517
| 1433.4 | 1281.4 | 129.1582 | 0.45428
| 1433.6 | 1281.6 | 129.1582 | 0.5517
| 1433.8 | 1281.8 | 129.1582 | 0.5517
| 1434 | 1282 | 129.0608 | 0.5517
| 1434.2 | 1282.2 | 129.1582 | 0.5517
| 1434.4 | 1282.4 | 129.1582 | 0.5517
| 1434.6 | 1282.6 | 129.1582 | 0.45428
| 1434.8 | 1282.8 | 129.1582 | 0.5517
| 1435 | 1283 | 129.0608 | 0.5517
| 1435.2 | 1283.2 | 129.1582 | 0.5517
| 1435.4 | 1283.4 | 129.0608 | 0.5517
| 1435.6 | 1283.6 | 129.1582 | 0.5517
| 1435.8 | 1283.8 | 129.1582 | 0.45428
| 1436 | 1284 | 126.5285 | 0.45428
| 1436.2 | 1284.2 | 128.8661 | 0.45428
| 1436.4 | 1284.4 | 129.0608 | 0.5517
| 1436.6 | 1284.6 | 129.1582 | 0.45428
| 1436.8 | 1284.8 | 129.0608 | 0.45428
| 1437 | 1285 | 129.0608 | 0.5517
| 1437.2 | 1285.2 | 129.0608 | 0.5517
| 1437.4 | 1285.4 | 129.0608 | 0.45428
| 1437.6 | 1285.6 | 129.0608 | 0.45428
| 1437.8 | 1285.8 | 128.9634 | 0.45428
| 1438 | 1286 | 128.9634 | 0.45428
| 1438.2 | 1286.2 | 128.8661 | 0.45428
| 1438.4 | 1286.4 | 128.4765 | 0.5517
| 1438.6 | 1286.6 | 128.4765 | 0.5517
| 1438.8 | 1286.8 | 128.7686 | 0.5517
| 1439 | 1287 | 128.9634 | 0.5517
| 1439.2 | 1287.2 | 128.9634 | 0.5517
| 1439.4 | 1287.4 | 128.9634 | 0.5517
| 1439.6 | 1287.6 | 129.0608 | 0.5517
| 1439.8 | 1287.8 | 129.0608 | 0.5517
| 1440 | 1288 | 129.0608 | 0.45428
| 1450 | 1298 | 128.8661 | 0.45428
| 1460 | 1308 | 128.6713 | 0.5517
| 1470 | 1318 | 128.7686 | 0.5517
| 1480 | 1328 | 128.6713 | 0.45428
| 1480.2 | 1328.2 | 128.6713 | 0.45428
| 1480.4 | 1328.4 | 128.6713 | 0.5517
| 1480.6 | 1328.6 | 128.7686 | 0.5517
| 1480.8 | 1328.8 | 128.7686 | 0.5517
| 1481 | 1329 | 128.8661 | 0.45428
| 1481.2 | 1329.2 | 128.7686 | 0.5517
| 1481.4 | 1329.4 | 128.8661 | 0.45428
| 1481.6 | 1329.6 | 128.7686 | 0.5517
| 1481.8 | 1329.8 | 128.7686 | 0.5517
| 1482 | 1330 | 128.7686 | 0.5517
| 1482.2 | 1330.2 | 128.7686 | 0.5517
| 1482.4 | 1330.4 | 128.8661 | 0.5517
| 1482.6 | 1330.6 | 128.7686 | 0.45428
| 1482.8 | 1330.8 | 128.7686 | 0.45428
| 1483 | 1331 | 128.7686 | 0.5517
| 1483.2 | 1331.2 | 128.7686 | 0.5517
| 1483.4 | 1331.4 | 128.8661 | 0.5517
| 1483.6 | 1331.6 | 128.7686 | 0.45428
| 1483.8 | 1331.8 | 128.7686 | 0.5517
| 1484 | 1332 | 128.6713 | 0.5517
| 1484.2 | 1332.2 | 128.6713 | 0.45428
| 1484.4 | 1332.4 | 128.6713 | 0.5517
| 1484.6 | 1332.6 | 128.5738 | 1.2335
| 1484.8 | 1332.8 | 128.4765 | 9.4148
| 1485 | 1333 | 128.2817 | 11.6549
| 1485.2 | 1333.2 | 127.9895 | 12.6289
| 1485.4 | 1333.4 | 127.6973 | 11.6549
| 1485.6 | 1333.6 | 127.5999 | -18.6354
| 1485.8 | 1333.8 | 126.9181 | 9.8043
| 1486 | 1334 | 127.2103 | 8.733
| 1486.2 | 1334.2 | 127.4051 | 89.1825
| 1486.4 | 1334.4 | 127.5999 | 124.1479
| 1486.6 | 1334.6 | 127.5025 | 126.7776
| 1486.8 | 1334.8 | 127.5025 | 127.1672
| 1487 | 1335 | 123.704 | 123.3687
| 1487.2 | 1335.2 | 127.3077 | 126.9724
| 1487.4 | 1335.4 | 127.5025 | 127.2646
| 1487.6 | 1335.6 | 127.5999 | 127.2646
| 1487.8 | 1335.8 | 127.5999 | 127.2646
| 1488 | 1336 | 127.4051 | 127.2646
| 1488.2 | 1336.2 | 126.8207 | 126.6802
| 1488.4 | 1336.4 | 125.0676 | 124.7323
| 1488.6 | 1336.6 | 127.4051 | 127.1672
| 1488.8 | 1336.8 | 101.595 | 100.9675
| 1489 | 1337 | 125.9441 | 125.7062
| 1489.2 | 1337.2 | 128.1843 | 127.9463
| 1489.4 | 1337.4 | 128.3791 | 128.1411
| 1489.6 | 1337.6 | 128.3791 | 128.1411
| 1489.8 | 1337.8 | 128.3791 | 128.1411
| 1490 | 1338 | 128.3791 | 128.1411
| 1490.2 | 1338.2 | 128.3791 | 128.2385
| 1490.4 | 1338.4 | 128.3791 | 128.2385
| 1490.6 | 1338.6 | 128.3791 | 128.2385
| 1490.8 | 1338.8 | 128.4765 | 128.2385
| 1491 | 1339 | 128.4765 | 128.3359
| 1491.2 | 1339.2 | 128.3791 | 128.2385
| 1491.4 | 1339.4 | 128.4765 | 128.2385
| 1491.6 | 1339.6 | 128.4765 | 128.2385
| 1491.8 | 1339.8 | 128.4765 | 128.3359
| 1492 | 1340 | 128.4765 | 128.2385
| 1492.2 | 1340.2 | 128.3791 | 128.3359
| 1492.4 | 1340.4 | 128.4765 | 128.2385
| 1492.6 | 1340.6 | 128.3791 | 128.2385
| 1492.8 | 1340.8 | 128.3791 | 128.2385
| 1493 | 1341 | 128.3791 | 128.2385
| 1493.2 | 1341.2 | 128.4765 | 128.2385
| 1493.4 | 1341.4 | 128.3791 | 128.3359
| 1493.6 | 1341.6 | 128.3791 | 128.3359
| 1493.8 | 1341.8 | 128.2817 | 128.3359
| 1494 | 1342 | 128.0869 | 128.2385
| 1494.2 | 1342.2 | 127.6973 | 128.1411
| 1494.4 | 1342.4 | 128.1843 | 128.1411
| 1494.6 | 1342.6 | 128.2817 | 127.9463
| 1494.8 | 1342.8 | 128.2817 | 127.9463
| 1495 | 1343 | 128.2817 | 128.1411
| 1495.2 | 1343.2 | 128.3791 | 128.2385
| 1495.4 | 1343.4 | 128.3791 | 128.2385
| 1495.6 | 1343.6 | 128.3791 | 128.2385
| 1495.8 | 1343.8 | 128.4765 | 128.2385
| 1496 | 1344 | 128.4765 | 128.2385
| 1496.2 | 1344.2 | 128.5738 | 128.3359
| 1496.4 | 1344.4 | 128.5738 | 128.3359
| 1496.6 | 1344.6 | 128.4765 | 128.3359
| 1496.8 | 1344.8 | 128.4765 | 128.4333
| 1497 | 1345 | 128.3791 | 128.2385
| 1497.2 | 1345.2 | 128.4765 | 128.3359
| 1497.4 | 1345.4 | 128.4765 | 128.3359
| 1497.6 | 1345.6 | 128.4765 | 128.3359
| 1497.8 | 1345.8 | 128.4765 | 128.3359
| 1498 | 1346 | 127.2103 | 127.0698
| 1498.2 | 1346.2 | 128.3791 | 128.2385
| 1498.4 | 1346.4 | 128.4765 | 128.3359
| 1498.6 | 1346.6 | 128.4765 | 128.3359
| 1498.8 | 1346.8 | 128.4765 | 128.3359
| 1499 | 1347 | 128.4765 | 128.3359
| 1499.2 | 1347.2 | 128.4765 | 128.3359
| 1499.4 | 1347.4 | 128.3791 | 128.3359
| 1499.6 | 1347.6 | 128.4765 | 128.3359
| 1499.8 | 1347.8 | 128.3791 | 128.2385
| 1500 | 1348 | 128.3791 | 128.2385
| 1500.2 | 1348.2 | 128.3791 | 128.3359
| 1500.4 | 1348.4 | 128.3791 | 128.3359
| 1500.6 | 1348.6 | 128.4765 | 128.3359
| 1500.8 | 1348.8 | 128.3791 | 128.2385
| 1501 | 1349 | 128.3791 | 128.3359
| 1501.2 | 1349.2 | 128.3791 | 128.2385
| 1501.4 | 1349.4 | 128.4765 | 128.3359
| 1501.6 | 1349.6 | 128.4765 | 128.3359
| 1501.8 | 1349.8 | 128.3791 | 128.3359
| 1502 | 1350 | 120.8795 | 120.6416
| 1502.2 | 1350.2 | 127.7947 | 127.7515
| 1502.4 | 1350.4 | 128.3791 | 128.1411
| 1502.6 | 1350.6 | 128.3791 | 128.2385
| 1502.8 | 1350.8 | 128.3791 | 128.2385
| 1503 | 1351 | 128.3791 | 128.3359
| 1503.2 | 1351.2 | 128.3791 | 128.2385
| 1503.4 | 1351.4 | 128.4765 | 128.3359
| 1503.6 | 1351.6 | 128.3791 | 128.3359
| 1503.8 | 1351.8 | 128.3791 | 128.2385
| 1504 | 1352 | 128.3791 | 128.2385
| 1504.2 | 1352.2 | 128.3791 | 128.2385
| 1504.4 | 1352.4 | 128.4765 | 128.3359
| 1504.6 | 1352.6 | 128.3791 | 128.2385
| 1504.8 | 1352.8 | 128.3791 | 128.3359
| 1505 | 1353 | 128.2817 | 128.2385
| 1505.2 | 1353.2 | 128.2817 | 128.2385
| 1505.4 | 1353.4 | 128.2817 | 128.2385
| 1505.6 | 1353.6 | 128.2817 | 128.2385
| 1505.8 | 1353.8 | 128.3791 | 128.2385
| 1506 | 1354 | 128.2817 | 128.1411
| 1506.2 | 1354.2 | 128.3791 | 128.2385
| 1506.4 | 1354.4 | 128.3791 | 128.2385
| 1506.6 | 1354.6 | 128.2817 | 128.2385
| 1506.8 | 1354.8 | 128.2817 | 128.1411
| 1507 | 1355 | 128.2817 | 128.1411
| 1507.2 | 1355.2 | 128.2817 | 128.1411
| 1507.4 | 1355.4 | 128.2817 | 128.1411
| 1507.6 | 1355.6 | 128.2817 | 128.1411
| 1507.8 | 1355.8 | 128.1843 | 128.2385
| 1508 | 1356 | 128.1843 | 128.0438
| 1508.2 | 1356.2 | 128.2817 | 128.1411
| 1508.4 | 1356.4 | 128.1843 | 128.1411
| 1508.6 | 1356.6 | 128.2817 | 128.2385
| 1508.8 | 1356.8 | 128.2817 | 128.1411
| 1509 | 1357 | 128.2817 | 128.1411
| 1509.2 | 1357.2 | 128.2817 | 128.2385
| 1509.4 | 1357.4 | 128.1843 | 128.1411
| 1509.6 | 1357.6 | 127.5999 | 127.5568
| 1509.8 | 1357.8 | 127.9895 | 127.9463
| 1510 | 1358 | 31.1773 | 30.7446
| 1510.2 | 1358.2 | 4.5881 | 4.6424
| 1510.4 | 1358.4 | 1.5688 | 1.7205
| 1510.6 | 1358.6 | 1.0818 | 1.1361
| 1510.8 | 1358.8 | 0.88702 | 0.84388
| 1511 | 1359 | 0.69222 | 0.84388
| 1511.2 | 1359.2 | 0.69222 | 0.84388
| 1511.4 | 1359.4 | 0.59484 | 0.64908
| 1511.6 | 1359.6 | 0.59484 | 0.7465
| 1511.8 | 1359.8 | 0.49742 | 0.64908
| 1512 | 1360 | 0.49742 | 0.64908
| 1515 | 1363 | 0.40004 | 0.5517
| 1530 | 1378 | 0.40004 | 0.45428
| 1560 | 1408 | 0.30262 | 0.45428
| 1620 | 1468 | 0.30262 | 0.5517
| 1680 | 1528 | 0.30262 | 0.45428
| 1740 | 1588 | 0.30262 | 0.45428