## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 7, Location A, IRMS #1
Test conditions: Cable: Bundle of 6, 7-conductor, 12 AWG, XLPE, PVC, PE, EPR, TS/TP, & XLPO control cables (Items 10, 1, 15, 2, 3, & 8). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position A in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 200 kW heat release rate and increased to ~300 kW during the test. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 152 seconds of baseline data monitoring.
DAQ Time | Burner Time | Event | Interpretation
152 | 0 | Ignited Gas Burner
304-309 | 152-157 | Conductors D7 & D8 both short to ground at less than 1000 ohms (176 & 126) | Cable D shorts to ground
334-345 | 182-193 | Conductors D7 & D8 both short to conductor E10 at less than 1000 ohms (175 & 125) | Possible cable to cable short
343-345 | 191-193 | Conductors F11 & F12 both short to ground at less than 100 ohms (26 & 2) | Cable F shorts to ground
367 | 215 | Conductors F11 & F12 short together at less than 100 ohms (25) | Cable F shorted internally
429 | 277 | Conductors B3 & B4 short together at less than 100 ohms (25) | Cable B shorted internally
456-464 | 304-312 | Conductors C5 & C6 both short to ground at less than 100 ohms (36 & 32) | Cable C shorts to ground
476 | 324 | Conductors C5 & C6 short together at less than 1000 ohms (609) | Cable C shorted internally
489-494 | 337-342 | The existing ground faults on conductors D7 & D8 decrease to less than 100 ohms (5 & 5)
506-510 | 354-358 | Conductors E9 & E10 both short to ground at less than 100 ohms (6 & 9) | Cable E shorts to ground
513 | 361 | Conductors D7 & D8 short together at less than 100 ohms (12) | Cable D shorted internally
538 | 386 | Conductors E9 & E10 short together at less than 100 ohms (4) | Cable E shorted internally
555 | 403 | Conductors A1 & A2 short together at less than 100 ohms (21) | Cable A shorted internally
583 | 431 | Conductor A2 shorts to ground at less than 1000 ohms (305)
610-626 | 458-474 | Conductors B3 & B4 both short to ground at less than 100 ohms (3 & 1) | Cable B shorts to ground
661 | 509 | The existing internal short between conductors C5 & C6 decreases to less than 100 ohms (21)
745-767 | 593-615 | Conductor A1 shorts to ground at less than 100 ohms (1) and the existing ground fault on conductor A2 decreases to less than 100 ohms (1) | Cable A shorts to ground
1551 | 1399 | Gas burner is shut off
Additional Observations
Observation 1 | One possible cable to cable interaction took place during this test (between cables D & E).

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | PVC | (Item #1)
|  |  |  | Cable C = | PE | (Item #15)
|  |  |  | Cable D = | EPR | (Item #2)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | XLPO | (Item #8)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| A1 | = | Center of bundle, under jacket
| A2 | = | Air above bundle
| A3 | = | Air below bundle
| A4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE | (Item #10)
|  |  |  | Cable B = | PVC | (Item #1)
|  |  |  | Cable C = | PE | (Item #15)
|  |  |  | Cable D = | EPR | (Item #2)
|  |  |  | Cable E = | TS/TP | (Item #3)
|  |  |  | Cable F = | XLPO | (Item #8)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 7 |  |  | 2006-11-08 | 8:39
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-151.5 | 258837.9994 | -149 | 260237.9994 | -146 | 259037.9994 | -143.5 | 255137.9994 | -140.5 | 261537.9994 | -121 | 260937.9994 | -118 | 255837.9994 | -115.5 | 262237.9994 | -112.5 | 258937.9994 | -93 | 260237.9994 | -90 | 261837.9994 | -87.5 | 258637.9994 | -84.5 | 258037.9994 | -81.5 | 263937.9994 | -79 | 258837.9994 | -76 | 518775.9997 | -67.5 | 258537.9994 | -64.5 | 506175.9997 | -62 | 264237.9994 | -59.5 | 508175.9997 | -56.5 | 263937.9994 | -53.5 | 256537.9994 | -45.5 | 260137.9994 | -37 | 263437.9994 | -34 | 264737.9994 | -31.5 | 529575.9997 | -28.5 | 263237.9994 | -20 | 527375.9997 | -17.5 | 513775.9997 | -14.5 | 264437.9994 | -11.5 | 256437.9994 | -9 | 262837.9994 | -6 | 263237.9994 | -3.5 | 262237.9994 | 5 | 261337.9994 | 8 | 265137.9994 | 16.5 | 263137.9994 | 19 | 265037.9994 | 22 | 264637.9994 | 24.5 | 264937.9994 | 27.5 | 259537.9994 | 30.5 | 263537.9994
32 | 258837.9994 | 36 | 260237.9994 | 38.5 | 259037.9994 | 41.5 | 255137.9994 | 44.5 | 261537.9994 | 64 | 260937.9994 | 66.5 | 255837.9994 | 69.5 | 262237.9994 | 72.5 | 258937.9994 | 92 | 260237.9994 | 94.5 | 261837.9994 | 97.5 | 258637.9994 | 100.5 | 258037.9994 | 103 | 263937.9994 | 106 | 517775.9997 | 108.5 | 518775.9997 | 117 | 258537.9994 | 120 | 253037.9994 | 122.5 | 264237.9994 | 125.5 | 254037.9994 | 128.5 | 263937.9994 | 131 | 256537.9994 | 139.5 | 260137.9994 | 148 | 263437.9994 | 150.5 | 264737.9994 | 153.5 | 529575.9997 | 156.5 | 263237.9994 | 164.5 | 263637.9994 | 167.5 | 256837.9994 | 170.5 | 264437.9994 | 173 | 256437.9994 | 176 | 1853.8281 | 178.5 | 332.7505 | 181.5 | 175.2743 | 190 | 762.6467 | 192.5 | 125.0171 | 201 | 263137.9994 | 204 | 265037.9994 | 206.5 | 264637.9994 | 209.5 | 264937.9994 | 212.5 | 259537.9994 | 215 | 24.9887
218 | 258837.9994 | 220.5 | 260237.9994 | 223.5 | 259037.9994 | 226.5 | 255137.9994 | 229 | 261537.9994 | 248.5 | 260937.9994 | 251.5 | 255837.9994 | 254.5 | 262237.9994 | 257 | 258937.9994 | 276.5 | 40.1466 | 279.5 | 130868.9988 | 282.5 | 86145.9982 | 285 | 128968.9988 | 288 | 65909.4976 | 290.5 | 129368.9988 | 293.5 | 129618.9988 | 302 | 258537.9994 | 304.5 | 253037.9994 | 307.5 | 264237.9994 | 310.5 | 84612.6648 | 313 | 43906.3297 | 316 | 4742.1941 | 324 | 608.9234 | 332.5 | 98.3896 | 335.5 | 44.6464 | 338.5 | 34.5537 | 341 | 908.7985 | 349.5 | 52.0172 | 352.5 | 45.7533 | 355 | 40.6282 | 357.5 | 30.3675 | 360.5 | 12.1668 | 363.5 | 6.7055 | 366.5 | 29.2893 | 374.5 | 12.0648 | 377.5 | 14.9922 | 386 | 4.241 | 388.5 | 11.9273 | 391.5 | 4.5411 | 394.5 | 7.1777 | 397 | 29.2565 | 400 | 17.2384
402.5 | 20.7292 | 405.5 | 260237.9994 | 408.5 | 259037.9994 | 411 | 255137.9994 | 414 | 261537.9994 | 433.5 | 700.531 | 436.5 | 557.7008 | 439 | 327.5833 | 442 | 304.3562 | 461.5 | 643.1696 | 464 | 18081.5844 | 467 | 17.5217 | 469.5 | 33.3454 | 472.5 | 15.9766 | 475.5 | 30.8467 | 478.5 | 1.0824 | 486.5 | 14.7778 | 489.5 | 0.63976 | 492.5 | 16.0571 | 495 | 4.0245 | 498 | 21.9012 | 500.5 | 0.065901 | 509 | 20.9351 | 517.5 | 24.3331 | 520.5 | 8.0515 | 523 | 1.5623 | 526 | 16.088 | 534.5 | 27.9101 | 537 | 11.2002 | 540 | 23.5473 | 542.5 | 17.5045 | 545.5 | 20.071 | 548 | 25.0895 | 551 | 23.6408 | 559.5 | 14.249 | 562 | 27.2467 | 570.5 | 5.8151 | 573.5 | 7.3997 | 576.5 | 9.3569 | 579 | 13.2746 | 582 | 27.044 | 584.5 | 13.7786
587.5 | 0.33492 | 590 | 14.3842 | 593 | 28.5445 | 596 | 10.3065 | 598.5 | 20.7813 | 618 | 30.2266 | 621 | 13.8796 | 623.5 | 16.1191 | 626.5 | 0.93506 | 646.5 | 15.8073 | 649 | 5.595 | 651.5 | 28.2133 | 654.5 | 11.726 | 657.5 | 26.5403 | 660.5 | 0.093264 | 663 | 21.2574 | 671.5 | 24.418 | 674.5 | 7.5996 | 677 | 26.6855 | 679.5 | 18.6393 | 682.5 | 0.32402 | 685.5 | 12.1769 | 694 | 7.8442 | 702.5 | 16.603 | 705 | 18.872 | 707.5 | 30.2031 | 710.5 | 6.5255 | 719 | 14.9539 | 722 | 2.7296 | 724.5 | 1.5678 | 727.5 | 5.6972 | 730 | 10.2613 | 733 | 8.2127 | 735.5 | 15.4838 | 744 | 8.115 | 747 | 26.8706 | 755.5 | 27.729 | 758 | 23.6517 | 761 | 2.5937 | 764 | 0.5099 | 766.5 | 25.0279 | 769.5 | 24.8057
772.5 | 15.5498 | 775 | 20.232 | 778 | 8.0345 | 780.5 | 1.7849 | 783.5 | 7.1379 | 803 | 21.6025 | 805.5 | 15.5837 | 808.5 | 13.1094 | 811.5 | 21.6553 | 831 | 0.9462 | 833.5 | 9.8365 | 836.5 | 16.8082 | 839.5 | 17.7438 | 842 | 6.6777 | 845 | 0.47498 | 847.5 | 13.7768 | 856.5 | 24.7272 | 859 | 3.8755 | 862 | 6.219 | 864.5 | 5.6469 | 867.5 | 6.9931 | 870.5 | 5.6483 | 878.5 | 5.8342 | 887 | 3.5903 | 889.5 | 16.8637 | 892.5 | 31.4658 | 895.5 | 5.6345 | 903.5 | 1.9935 | 906.5 | 19.3278 | 909.5 | 5.7245 | 912 | 19.7719 | 915 | 15.0166 | 918 | 15.9821 | 920.5 | 12.4054 | 929 | 4.2506 | 931.5 | 23.818 | 940.5 | 0.65631 | 943 | 0.46858 | 945.5 | 22.9308 | 948.5 | 8.8276 | 951.5 | 20.7112 | 954 | 12.4194
957 | 9.133 | 960 | 8.3065 | 962.5 | 0.93592 | 965.5 | 27.3062 | 968 | 24.9467 | 987.5 | 10.9529 | 990.5 | 24.9013 | 993.5 | 12.5555 | 996 | 14.379 | 1015.5 | 10.0683 | 1018.5 | 0.95986 | 1021.5 | 11.2891 | 1024 | 15.9924 | 1027 | 20.0689 | 1029.5 | 27.8571 | 1032.5 | 9.5384 | 1041 | 4.5096 | 1043.5 | 23.6456 | 1046.5 | 11.4875 | 1049.5 | 0.8928 | 1052 | 6.0079 | 1055 | 4.0408 | 1063.5 | 23.3001 | 1071.5 | 1.3816 | 1074.5 | 2.9668 | 1077.5 | 0.71296 | 1080 | 20.3124 | 1088.5 | 3.9262 | 1091.5 | 16.9696 | 1094 | 8.0192 | 1097 | 0.46777 | 1099.5 | 14.4459 | 1102.5 | 1.7542 | 1105.5 | 28.378 | 1113.5 | 27.9978 | 1116.5 | 24.3569 | 1125 | 0.97092 | 1127.5 | 27.6397 | 1130.5 | 11.5118 | 1133.5 | 1.1124 | 1136 | 14.49 | 1139 | 0.61018
1142 | 8.7517 | 1144.5 | 9.9234 | 1147.5 | 5.6044 | 1150 | 4.1699 | 1153 | 12.1516 | 1172.5 | 22.0132 | 1175.5 | 7.1007 | 1178 | 25.2227 | 1181 | 28.037 | 1200.5 | 2.6089 | 1203.5 | 16.6886 | 1206 | 13.2601 | 1209 | 22.5343 | 1211.5 | 11.5059 | 1214.5 | 28.707 | 1217.5 | 0.93849 | 1225.5 | 23.3174 | 1228.5 | 0.88412 | 1231.5 | 9.9929 | 1234 | 5.3732 | 1237 | 6.7227 | 1239.5 | 23.8145 | 1248 | 16.1367 | 1256.5 | 25.3082 | 1259.5 | 3.853 | 1262 | 20.4934 | 1265 | 11.7949 | 1273.5 | 1.3374 | 1276 | 18.4751 | 1279 | 21.6705 | 1281.5 | 4.3084 | 1284.5 | 0.96837 | 1287.5 | 12.6389 | 1290 | 12.0068 | 1298.5 | 7.2378 | 1301.5 | 0.18877 | 1309.5 | 20.8366 | 1312.5 | 0.98704 | 1315.5 | 0.98365 | 1318 | 7.2228 | 1321 | 7.4068 | 1323.5 | 14.3415
1326.5 | 396.5544 | 1329.5 | 10351.7537 | 1332 | 3324.6275 | 1335 | 23.1935 | 1337.5 | 22.4738 | 1357.5 | 24.4123 | 1360 | 4.727 | 1363 | 31.1502 | 1365.5 | 7.4793 | 1385.5 | 1739.8792 | 1388 | 13.0866 | 1391 | 30.4061 | 1393.5 | 13.7167 | 1396.5 | 37.0737 | 1399.5 | 10.3901 | 1402 | 12.6498 | 1410.5 | 30.6258 | 1413 | 27.9555 | 1416 | 52.815 | 1419 | 35.4978 | 1421.5 | 29.7405 | 1424.5 | 46.0901 | 1433 | 367.5729 | 1441.5 | 27.1771 | 1444 | 18.268 | 1447 | 18.1589 | 1449.5 | 11.0604 | 1458 | 24.7926 | 1461 | 4.0761 | 1463.5 | 25.175 | 1466.5 | 0.91356 | 1469.5 | 24.1679 | 1472 | 12.2899 | 1475 | 0.62918 | 1483.5 | 10.2487 | 1486 | 22.112 | 1494.5 | 7.0259 | 1497.5 | 0.047483 | 1500 | 19.8837 | 1503 | 26.2761 | 1505.5 | 0.94021 | 1508.5 | 14.2388
1511.5 | 13.1083 | 1514 | 26.1761 | 1517 | 80.8134 | 1519.5 | 210.7652 | 1522.5 | 270.1611 | 1542 | 21.3688 | 1545 | 51.3281 | 1547.5 | 261.9033 | 1550.5 | 261.3478 | 1570 | 77.2707 | 1573 | 736.6715 | 1575.5 | 636.931 | 1578.5 | 672.6644 | 1581.5 | 45313.0274 | 1584 | 677.3883 | 1587 | 4932.2215 | 1595.5 | 6893.7101 | 1598 | 245881.1385 | 1601 | 1583.5857 | 1603.5 | 727.6237 | 1606.5 | 1028.2247 | 1609.5 | 1157.9049 | 1617.5 | 19.9695 | 1626 | 87745.9982 | 1629 | 66109.4976 | 1631.5 | 88179.3315 | 1634.5 | 87679.3315 | 1643 | 131768.9988 | 1645.5 | 85545.9982 | 1648.5 | 88079.3315 | 1651.5 | 36548.2814 | 1654 | 28.3512 | 1657 | 60.5619 | 1659.5 | 21.7463 | 1668 | 64.0822 | 1671 | 54.2488 | 1679.5 | 59.6695 | 1682 | 132468.9988 | 1685 | 66084.4976 | 1687.5 | 264937.9994 | 1690.5 | 259537.9994 | 1693.5 | 16.9966
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 7 |  |  | 2006-11-08 | 8:39
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-146.1 | 255138 |  | -123.7 | 255838 | -95.7222 | 258038 | -80.0556 | 255838 | -65.8889 | 255138 | -57.1111 | 253038 | -33 | 258038 | -27.4 | 254038 | -15.1111 | 258838 | -12 | 256538 | 5.6 | 263538 | 8 | 256438
38.5 | 255138 |  | 60.9 | 255838 | 89.1111 | 258038 | 104.6111 | 253038 | 118.9444 | 255138 | 127.7222 | 253038 | 151.8 | 175.8549 | 157.4 | 125.7345 | 169.6667 | 258838 | 172.7222 | 256538 | 190.5 | 26.2634 | 192.7 | 1.6196
223.5 | 255138 |  | 245.9 | 255838 | 273.8333 | 4101.6301 | 289.4444 | 4742.2264 | 303.7778 | 35.7447 | 312.3889 | 31.5579 | 336.6 | 4.6788 | 342.2 | 4.7145 | 354.3889 | 5.7605 | 357.6667 | 8.6667 | 375.3 | 13.5182 | 377.4 | 0.62519
408.3 | 2816.2811 |  | 430.7 | 304.7469 | 458.6111 | 2.6258 | 474.2778 | 0.89199 | 488.5 | 3.1301 | 497.2778 | 12.5933 | 521.3 | 6.6686 | 526.9 | 0.62424 | 539.2778 | 0.62543 | 542.3333 | 3.6502 | 560 | 0.62187 | 562.3 | 2.9434
593 | 1.2267 |  | 615.3 | 0.63636 | 643.3889 | 1.4647 | 659 | 1.9058 | 673.2778 | 5.2382 | 682 | 0.63 | 706 | 4.2753 | 711.6 | 8.9786 | 724 | 1.3326 | 727.1111 | 0.62831 | 744.7 | 22.6923 | 747 | 6.2704
777.9 | 3.2934 |  | 800.2 | 11.8523 | 828.1111 | 0.63317 | 843.8333 | 0.87116 | 858 | 0.63735 | 866.7222 | 0.63341 | 891 | 0.6386 | 896.4 | 1.1252 | 908.7778 | 0.62591 | 911.8333 | 0.64235 | 929.5 | 0.9687 | 931.7 | 0.62591
962.6 | 0.63612 |  | 984.9 | 0.63661 | 1012.8889 | 0.62927 | 1028.4444 | 0.64412 | 1042.8333 | 0.6459 | 1051.5 | 1.1357 | 1075.6 | 0.62352 | 1081.2 | 2.1118 | 1093.3889 | 0.62424 | 1096.6667 | 2.1325 | 1114.3 | 2.1853 | 1116.5 | 0.62519
1147.4 | 5.6449 |  | 1169.8 | 8.5403 | 1197.7222 | 0.63317 | 1213.2778 | 0.65129 | 1227.5556 | 2.92 | 1236.2778 | 0.67548 | 1260.5 | 0.62687 | 1266 | 1.7797 | 1278.3333 | 0.62163 | 1281.3889 | 0.6214 | 1299 | 0.62234 | 1301.3 | 18.489
1332.1 | 13.713 |  | 1354.5 | 3.2373 | 1382.5556 | 11.804 | 1398 | 4.2517 | 1412.3889 | 0.62831 | 1421 | 0.63711 | 1445.2 | 2.1963 | 1450.9 | 11.6779 | 1463.1111 | 0.62591 | 1466.1667 | 0.62234 | 1483.9 | 1.6281 | 1486 | 2.3467
1516.9 | 140.1147 |  | 1539.3 | 128.2761 | 1567.2778 | 491.2289 | 1582.8889 | 727.8111 | 1597.1111 | 9.5059 | 1605.8333 | 3.1696 | 1630 | 23.0478 | 1635.6 | 35.9027 | 1647.8889 | 30.3161 | 1651 | 45.9156 | 1668.6 | 16.1061 | 1671 | 6.1419
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## F11-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.9512 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39029.3579 | 1 | 0 | 39029.358 | 1 | 0 |  | 30.5 | 182.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263538 | 263538 | 263537.9994
39029.3601 | 2088 | 0 | 39029.3601 | 2080 | 0 |  | 215 | 367 | 127.4725 | 0 | 126.9841 | 0 | 1.2747 | 0 | 1.2698 | 0 | 1.2747 | 1.2698 | 26.2634 | 26.749 | 24.9887
39029.3622 | 2223 | 0 | 39029.3622 | 2620 | 0 |  | 400 | 552 | 135.7143 | 0 | 159.9512 | 0 | 1.3571 | 0 | 1.5995 | 0 | 1.3571 | 1.5995 | 18.5956 | 0.62519 | 17.2384
39029.3644 | 2289 | 0 | 39029.3644 | 2561 | 0 |  | 584.5 | 736.5 | 139.7436 | 0 | 156.3492 | 0 | 1.3974 | 0 | 1.5635 | 0 | 1.3974 | 1.5635 | 15.1761 | 2.9434 | 13.7786
39029.3665 | 2091 | 0 | 39029.3665 | 2215 | 0 |  | 769.5 | 921.5 | 127.6557 | 0 | 135.2259 | 0 | 1.2766 | 0 | 1.3523 | 0 | 1.2766 | 1.3523 | 26.0823 | 19.0239 | 24.8057
39029.3686 | 2316 | 0 | 39029.3686 | 2075 | 0 |  | 954 | 1106 | 141.3919 | 0 | 126.6789 | 0 | 1.4139 | 0 | 1.2668 | 0 | 1.4139 | 1.2668 | 13.8333 | 27.0545 | 12.4194
39029.3708 | 2580 | 0 | 39029.3708 | 2620 | 0 |  | 1139 | 1291 | 157.5092 | 0 | 159.9512 | 0 | 1.5751 | 0 | 1.5995 | 0 | 1.5751 | 1.5995 | 2.1853 | 0.62519 | 0.61018
39029.3729 | 2278 | 0 | 39029.3729 | 2225 | 0 |  | 1323.5 | 1475.5 | 139.072 | 0 | 135.8364 | 0 | 1.3907 | 0 | 1.3584 | 0 | 1.3907 | 1.3584 | 15.7322 | 18.489 | 14.3415
39029.375 | 2280 | 0 | 39029.3751 | 2148 | 0 |  | 1508.5 | 1660.5 | 139.1941 | 0 | 131.1355 | 0 | 1.3919 | 0 | 1.3114 | 0 | 1.3919 | 1.3114 | 15.6307 | 22.7365 | 14.2388
39029.3772 | 1269 | 1161 | 39029.3772 | 1257 | 1108 |  | 1693.5 | 1845.5 | 77.4725 | 70.8791 | 76.7399 | 67.6435 | 0.77473 | 0.70879 | 0.7674 | 0.67643 | 0.065934 | 0.090965 | 2497.2919 | 2180.4665 | 16.9966

## E10-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.5092 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39029.3579 | 1 | 0 | 39029.3579 | 1 | 0 |  | 27.5 | 179.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259538 | 259538 | 259537.9994
39029.36 | 1 | 0 | 39029.3601 | 2555 | 0 |  | 212.5 | 364.5 | 0.06105 | 0 | 155.9829 | 0 | 0.0006105 | 0 | 1.5598 | 0 | 0.0006105 | 1.5598 | 259538 | 1.6196 | 259537.9994
39029.3622 | 1990 | 0 | 39029.3622 | 2167 | 0 |  | 397 | 549 | 121.4896 | 0 | 132.2955 | 0 | 1.2149 | 0 | 1.323 | 0 | 1.2149 | 1.323 | 30.4714 | 19.8145 | 29.2565
39029.3643 | 2024 | 0 | 39029.3643 | 2215 | 0 |  | 582 | 734 | 123.5653 | 0 | 135.2259 | 0 | 1.2357 | 0 | 1.3523 | 0 | 1.2357 | 1.3523 | 28.2796 | 17.2181 | 27.044
39029.3665 | 2056 | 0 | 39029.3665 | 2046 | 0 |  | 766.5 | 918.5 | 125.5189 | 0 | 124.9084 | 0 | 1.2552 | 0 | 1.2491 | 0 | 1.2552 | 1.2491 | 26.2831 | 26.9003 | 25.0279
39029.3686 | 2128 | 0 | 39029.3686 | 2099 | 0 |  | 951.5 | 1103.5 | 129.9145 | 0 | 128.1441 | 0 | 1.2991 | 0 | 1.2814 | 0 | 1.2991 | 1.2814 | 22.0103 | 23.696 | 20.7112
39029.3707 | 2241 | 0 | 39029.3708 | 2449 | 0 |  | 1136 | 1288 | 136.8132 | 0 | 149.5116 | 0 | 1.3681 | 0 | 1.4951 | 0 | 1.3681 | 1.4951 | 15.8581 | 6.018 | 14.49
39029.3729 | 2385 | 0 | 39029.3729 | 2133 | 0 |  | 1321 | 1473 | 145.6044 | 0 | 130.2198 | 0 | 1.456 | 0 | 1.3022 | 0 | 1.456 | 1.3022 | 8.8629 | 21.7243 | 7.4068
39029.375 | 2580 | 0 | 39029.375 | 2340 | 0 |  | 1505.5 | 1657.5 | 157.5092 | 0 | 142.8571 | 0 | 1.5751 | 0 | 1.4286 | 0 | 1.5751 | 1.4286 | 0.63488 | 10.9564 | 0.94021
39029.3772 | 1 | 0 | 39029.3772 | 2118 | 0 |  | 1690.5 | 1842.5 | 0.06105 | 0 | 129.304 | 0 | 0.0006105 | 0 | 1.293 | 0 | 0.0006105 | 1.293 | 259538 | 22.5864 | 259537.9994

## E10-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.8059 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39029.3579 | 1 | 0 | 39029.3579 | 1 | 0 |  | 24.5 | 176.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264938 | 264938 | 264937.9994
39029.36 | 1 | 0 | 39029.36 | 885 | 0 |  | 209.5 | 361.5 | 0.06105 | 0 | 54.0293 | 0 | 0.0006105 | 0 | 0.54029 | 0 | 0.0006105 | 0.54029 | 264938 | 199.478 | 264937.9994
39029.3622 | 2439 | 0 | 39029.3622 | 2147 | 0 |  | 394.5 | 546.5 | 148.9011 | 0 | 131.0745 | 0 | 1.489 | 0 | 1.3107 | 0 | 1.489 | 1.3107 | 8.6667 | 23.4457 | 7.1777
39029.3643 | 2311 | 0 | 39029.3643 | 2634 | 0 |  | 579 | 731 | 141.0867 | 0 | 160.8059 | 0 | 1.4109 | 0 | 1.6081 | 0 | 1.4109 | 1.6081 | 14.6854 | 0.62187 | 13.2746
39029.3664 | 2596 | 0 | 39029.3664 | 2049 | 0 |  | 764 | 916 | 158.486 | 0 | 125.0916 | 0 | 1.5849 | 0 | 1.2509 | 0 | 1.5849 | 1.2509 | 2.0948 | 29.3499 | 0.5099
39029.3686 | 2403 | 0 | 39029.3686 | 2618 | 0 |  | 948.5 | 1100.5 | 146.7033 | 0 | 159.8291 | 0 | 1.467 | 0 | 1.5983 | 0 | 1.467 | 1.5983 | 10.2946 | 1.2368 | 8.8276
39029.3707 | 2581 | 0 | 39029.3707 | 2038 | 0 |  | 1133.5 | 1285.5 | 157.5702 | 0 | 124.42 | 0 | 1.5757 | 0 | 1.2442 | 0 | 1.5757 | 1.2442 | 2.6881 | 30.0481 | 1.1124
39029.3728 | 2438 | 0 | 39029.3729 | 2461 | 0 |  | 1318 | 1470 | 148.84 | 0 | 150.2442 | 0 | 1.4884 | 0 | 1.5024 | 0 | 1.4884 | 1.5024 | 8.7112 | 7.6952 | 7.2228
39029.375 | 2078 | 0 | 39029.375 | 2313 | 0 |  | 1503 | 1655 | 126.862 | 0 | 141.2088 | 0 | 1.2686 | 0 | 1.4121 | 0 | 1.2686 | 1.4121 | 27.5448 | 14.5863 | 26.2761
39029.3771 | 1 | 0 | 39029.3771 | 2126 | 0 |  | 1687.5 | 1839.5 | 0.06105 | 0 | 129.7924 | 0 | 0.0006105 | 0 | 1.2979 | 0 | 0.0006105 | 1.2979 | 264938 | 24.6651 | 264937.9994

## E9-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.6227 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39029.3578 | 1 | 0 | 39029.3579 | 1 | 0 |  | 22 | 174 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264638 | 264638 | 264637.9994
39029.36 | 1 | 0 | 39029.36 | 2552 | 0 |  | 206.5 | 358.5 | 0.06105 | 0 | 155.7998 | 0 | 0.0006105 | 0 | 1.558 | 0 | 0.0006105 | 1.558 | 264638 | 3.7375 | 264637.9994
39029.3621 | 2496 | 0 | 39029.3621 | 2018 | 0 |  | 391.5 | 543.5 | 152.381 | 0 | 123.199 | 0 | 1.5238 | 0 | 1.232 | 0 | 1.5238 | 1.232 | 6.0649 | 31.1883 | 4.5411
39029.3643 | 2389 | 0 | 39029.3643 | 2062 | 0 |  | 576.5 | 728.5 | 145.8486 | 0 | 125.8852 | 0 | 1.4585 | 0 | 1.2589 | 0 | 1.4585 | 1.2589 | 10.8154 | 28.3889 | 9.3569
39029.3664 | 2542 | 0 | 39029.3664 | 2405 | 0 |  | 761 | 913 | 155.1893 | 0 | 146.8254 | 0 | 1.5519 | 0 | 1.4683 | 0 | 1.5519 | 1.4683 | 4.1456 | 10.0782 | 2.5937
39029.3685 | 2131 | 0 | 39029.3685 | 2043 | 0 |  | 945.5 | 1097.5 | 130.0977 | 0 | 124.7253 | 0 | 1.301 | 0 | 1.2473 | 0 | 1.301 | 1.2473 | 24.2318 | 29.583 | 22.9308
39029.3707 | 2344 | 0 | 39029.3707 | 2223 | 0 |  | 1130.5 | 1282.5 | 143.1013 | 0 | 135.7143 | 0 | 1.431 | 0 | 1.3571 | 0 | 1.431 | 1.3571 | 12.9428 | 19.0904 | 11.5118
39029.3728 | 2631 | 0 | 39029.3728 | 2089 | 0 |  | 1315.5 | 1467.5 | 160.6227 | 0 | 127.5336 | 0 | 1.6062 | 0 | 1.2753 | 0 | 1.6062 | 1.2753 | 0.62258 | 26.7295 | 0.98365
39029.3749 | 2184 | 0 | 39029.375 | 2407 | 0 |  | 1500 | 1652 | 133.3333 | 0 | 146.9475 | 0 | 1.3333 | 0 | 1.4695 | 0 | 1.3333 | 1.4695 | 21.217 | 9.9867 | 19.8837
39029.3771 | 4 | 0 | 39029.3771 | 1943 | 0 |  | 1685 | 1837 | 0.2442 | 0 | 118.6203 | 0 | 0.002442 | 0 | 1.1862 | 0 | 0.002442 | 1.1862 | 66084.5 | 36.2522 | 66084.4976

## E9-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.8669 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39029.3578 | 1 | 0 | 39029.3578 | 1 | 0 |  | 19 | 171 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265038 | 265038 | 265037.9994
39029.3599 | 1 | 0 | 39029.36 | 532 | 0 |  | 204 | 356 | 0.06105 | 0 | 32.4786 | 0 | 0.0006105 | 0 | 0.32479 | 0 | 0.0006105 | 0.32479 | 265038 | 398.3797 | 265037.9994
39029.3621 | 2339 | 0 | 39029.3621 | 2243 | 0 |  | 388.5 | 540.5 | 142.7961 | 0 | 136.9353 | 0 | 1.428 | 0 | 1.3694 | 0 | 1.428 | 1.3694 | 13.3553 | 18.2069 | 11.9273
39029.3642 | 2435 | 0 | 39029.3642 | 2028 | 0 |  | 573.5 | 725.5 | 148.6569 | 0 | 123.8095 | 0 | 1.4866 | 0 | 1.2381 | 0 | 1.4866 | 1.2381 | 8.8862 | 30.7387 | 7.3997
39029.3664 | 2122 | 0 | 39029.3664 | 2161 | 0 |  | 758 | 910 | 129.5482 | 0 | 131.9292 | 0 | 1.2955 | 0 | 1.3193 | 0 | 1.2955 | 1.3193 | 24.9472 | 22.6923 | 23.6517
39029.3685 | 2598 | 0 | 39029.3685 | 2411 | 0 |  | 943 | 1095 | 158.6081 | 0 | 147.1917 | 0 | 1.5861 | 0 | 1.4719 | 0 | 1.5861 | 1.4719 | 2.0547 | 9.9701 | 0.46858
39029.3706 | 2057 | 0 | 39029.3706 | 2564 | 0 |  | 1127.5 | 1279.5 | 125.58 | 0 | 156.5324 | 0 | 1.2558 | 0 | 1.5653 | 0 | 1.2558 | 1.5653 | 28.8955 | 3.408 | 27.6397
39029.3728 | 2635 | 0 | 39029.3728 | 2429 | 0 |  | 1312.5 | 1464.5 | 160.8669 | 0 | 148.2906 | 0 | 1.6087 | 0 | 1.4829 | 0 | 1.6087 | 1.4829 | 0.62163 | 9.1552 | 0.98704
39029.3749 | 2611 | 0 | 39029.3749 | 2596 | 0 |  | 1497.5 | 1649.5 | 159.4017 | 0 | 158.486 | 0 | 1.594 | 0 | 1.5849 | 0 | 1.594 | 1.5849 | 1.5465 | 2.1333 | 0.047483
39029.377 | 2 | 0 | 39029.3771 | 1379 | 0 |  | 1682 | 1834 | 0.1221 | 0 | 84.188 | 0 | 0.001221 | 0 | 0.84188 | 0 | 0.001221 | 0.84188 | 132469 | 92.2683 | 132468.9988

## E9-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.707 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39029.3578 | 1 | 0 | 39029.3578 | 1 | 0 |  | 16.5 | 168.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39029.3599 | 1 | 0 | 39029.3599 | 1 | 0 |  | 201 | 353 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263138 | 263138 | 263137.9994
39029.362 | 2489 | 0 | 39029.3621 | 2116 | 0 |  | 386 | 538 | 151.9536 | 0 | 129.1819 | 0 | 1.5195 | 0 | 1.2918 | 0 | 1.5195 | 1.2918 | 5.7605 | 24.4036 | 4.241
39029.3642 | 2453 | 0 | 39029.3642 | 2261 | 0 |  | 570.5 | 722.5 | 149.7558 | 0 | 138.0342 | 0 | 1.4976 | 0 | 1.3803 | 0 | 1.4976 | 1.3803 | 7.3127 | 16.4255 | 5.8151
39029.3663 | 2041 | 0 | 39029.3663 | 2513 | 0 |  | 755.5 | 907.5 | 124.6032 | 0 | 153.4188 | 0 | 1.246 | 0 | 1.5342 | 0 | 1.246 | 1.5342 | 28.975 | 4.7505 | 27.729
39029.3685 | 2575 | 0 | 39029.3685 | 2295 | 0 |  | 940.5 | 1092.5 | 157.2039 | 0 | 140.1099 | 0 | 1.572 | 0 | 1.4011 | 0 | 1.572 | 1.4011 | 2.2283 | 14.7007 | 0.65631
39029.3706 | 2616 | 0 | 39029.3706 | 2042 | 0 |  | 1125 | 1277 | 159.707 | 0 | 124.6642 | 0 | 1.5971 | 0 | 1.2466 | 0 | 1.5971 | 1.2466 | 0.62615 | 28.9119 | 0.97092
39029.3727 | 2155 | 0 | 39029.3728 | 2041 | 0 |  | 1309.5 | 1461.5 | 131.5629 | 0 | 124.6032 | 0 | 1.3156 | 0 | 1.246 | 0 | 1.3156 | 1.246 | 22.1522 | 28.975 | 20.8366
39029.3749 | 2426 | 0 | 39029.3749 | 2198 | 0 |  | 1494.5 | 1646.5 | 148.1074 | 0 | 134.188 | 0 | 1.4811 | 0 | 1.3419 | 0 | 1.4811 | 1.3419 | 8.507 | 19.7625 | 7.0259
39029.377 | 950 | 1043 | 39029.377 | 1003 | 977 |  | 1679.5 | 1831.5 | 57.9976 | 63.6752 | 61.2332 | 59.6459 | 0.57998 | 0.63675 | 0.61233 | 0.59646 | 0.056777 | 0.015873 | 1384.2659 | 3655.0456 | 59.6695

## D8-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.928 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39029.3577 | 1 | 0 | 39029.3577 | 1 | 0 |  | 8 | 160 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 265138 | 265138 | 265137.9994
39029.3598 | 1175 | 0 | 39029.3598 | 1 | 0 |  | 192.5 | 344.5 | 71.7338 | 0 | 0.06105 | 0 | 0.71734 | 0 | 0.0006105 | 0 | 0.71734 | 0.0006105 | 125.7345 | 265138 | 125.0171
39029.362 | 2279 | 0 | 39029.362 | 2232 | 0 |  | 377.5 | 529.5 | 139.1331 | 0 | 136.2637 | 0 | 1.3913 | 0 | 1.3626 | 0 | 1.3913 | 1.3626 | 16.3835 | 18.8342 | 14.9922
39029.3641 | 2064 | 0 | 39029.3641 | 2336 | 0 |  | 562 | 714 | 126.0073 | 0 | 142.6129 | 0 | 1.2601 | 0 | 1.4261 | 0 | 1.2601 | 1.4261 | 28.5068 | 13.5437 | 27.2467
39029.3662 | 2070 | 0 | 39029.3662 | 2586 | 0 |  | 747 | 899 | 126.3736 | 0 | 157.8755 | 0 | 1.2637 | 0 | 1.5788 | 0 | 1.2637 | 1.5788 | 28.1343 | 2.5669 | 26.8706
39029.3684 | 2120 | 0 | 39029.3684 | 2032 | 0 |  | 931.5 | 1083.5 | 129.4261 | 0 | 124.0537 | 0 | 1.2943 | 0 | 1.2405 | 0 | 1.2943 | 1.2405 | 25.1123 | 30.5305 | 23.818
39029.3705 | 2111 | 0 | 39029.3705 | 2597 | 0 |  | 1116.5 | 1268.5 | 128.8767 | 0 | 158.547 | 0 | 1.2888 | 0 | 1.5855 | 0 | 1.2888 | 1.5855 | 25.6457 | 2.1325 | 24.3569
39029.3727 | 2606 | 0 | 39029.3727 | 2636 | 0 |  | 1301.5 | 1453.5 | 159.0965 | 0 | 160.928 | 0 | 1.591 | 0 | 1.6093 | 0 | 1.591 | 1.6093 | 1.7797 | 0.6214 | 0.18877
39029.3748 | 2149 | 0 | 39029.3748 | 2117 | 0 |  | 1486 | 1638 | 131.1966 | 0 | 129.243 | 0 | 1.312 | 0 | 1.2924 | 0 | 1.312 | 1.2924 | 23.4239 | 25.2896 | 22.112
39029.3769 | 1708 | 0 | 39029.3769 | 1 | 0 |  | 1671 | 1823 | 104.2735 | 0 | 0.06105 | 0 | 1.0427 | 0 | 0.0006105 | 0 | 1.0427 | 0.0006105 | 55.2916 | 265138 | 54.2488

## D8-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.6081 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39029.3576 | 1 | 0 | 39029.3577 | 1 | 0 |  | 5 | 157 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261338 | 261338 | 261337.9994
39029.3598 | 303 | 0 | 39029.3598 | 1 | 0 |  | 190 | 342 | 18.4982 | 0 | 0.06105 | 0 | 0.18498 | 0 | 0.0006105 | 0 | 0.18498 | 0.0006105 | 762.8317 | 261338 | 762.6467
39029.3619 | 2304 | 0 | 39029.3619 | 2422 | 0 |  | 374.5 | 526.5 | 140.6593 | 0 | 147.8632 | 0 | 1.4066 | 0 | 1.4786 | 0 | 1.4066 | 1.4786 | 13.4714 | 7.943 | 12.0648
39029.3641 | 2261 | 0 | 39029.3641 | 2202 | 0 |  | 559.5 | 711.5 | 138.0342 | 0 | 134.4322 | 0 | 1.3803 | 0 | 1.3443 | 0 | 1.3803 | 1.3443 | 15.6294 | 18.7275 | 14.249
39029.3662 | 2386 | 0 | 39029.3662 | 2580 | 0 |  | 744 | 896 | 145.6654 | 0 | 157.5092 | 0 | 1.4567 | 0 | 1.5751 | 0 | 1.4567 | 1.5751 | 9.5717 | 1.3326 | 8.115
39029.3683 | 2472 | 0 | 39029.3684 | 2326 | 0 |  | 929 | 1081 | 150.9158 | 0 | 142.0024 | 0 | 1.5092 | 0 | 1.42 | 0 | 1.5092 | 1.42 | 5.7597 | 12.3981 | 4.2506
39029.3705 | 2023 | 0 | 39029.3705 | 2598 | 0 |  | 1113.5 | 1265.5 | 123.5043 | 0 | 158.6081 | 0 | 1.235 | 0 | 1.5861 | 0 | 1.235 | 1.5861 | 29.2328 | 0.63048 | 27.9978
39029.3726 | 2405 | 0 | 39029.3726 | 2179 | 0 |  | 1298.5 | 1450.5 | 146.8254 | 0 | 133.0281 | 0 | 1.4683 | 0 | 1.3303 | 0 | 1.4683 | 1.3303 | 8.706 | 19.9807 | 7.2378
39029.3748 | 2341 | 0 | 39029.3748 | 2237 | 0 |  | 1483.5 | 1635.5 | 142.9182 | 0 | 136.569 | 0 | 1.4292 | 0 | 1.3657 | 0 | 1.4292 | 1.3657 | 11.6779 | 16.8699 | 10.2487
39029.3769 | 1584 | 0 | 39029.3769 | 1 | 0 |  | 1668 | 1820 | 96.7033 | 0 | 0.06105 | 0 | 0.96703 | 0 | 0.0006105 | 0 | 0.96703 | 0.0006105 | 65.0492 | 261338 | 64.0822

## D7-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.1575 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39029.3575 | 1 | 0 | 39029.3576 | 1 | 0 |  | -3.5 | 148.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39029.3597 | 951 | 0 | 39029.3597 | 1 | 0 |  | 181.5 | 333.5 | 58.0586 | 0 | 0.06105 | 0 | 0.58059 | 0 | 0.0006105 | 0 | 0.58059 | 0.0006105 | 175.8549 | 262238 | 175.2743
39029.3618 | 2010 | 0 | 39029.3618 | 2234 | 0 |  | 366.5 | 518.5 | 122.7106 | 0 | 136.3858 | 0 | 1.2271 | 0 | 1.3639 | 0 | 1.2271 | 1.3639 | 30.5164 | 17.4297 | 29.2893
39029.364 | 2100 | 0 | 39029.364 | 2394 | 0 |  | 551 | 703 | 128.2051 | 0 | 146.1538 | 0 | 1.2821 | 0 | 1.4615 | 0 | 1.2821 | 1.4615 | 24.9229 | 9.5815 | 23.6408
39029.3661 | 2245 | 0 | 39029.3661 | 2607 | 0 |  | 735.5 | 887.5 | 137.0574 | 0 | 159.1575 | 0 | 1.3706 | 0 | 1.5916 | 0 | 1.3706 | 1.5916 | 16.8543 | 0.62831 | 15.4838
39029.3682 | 2305 | 0 | 39029.3683 | 2369 | 0 |  | 920.5 | 1072.5 | 140.7204 | 0 | 144.6276 | 0 | 1.4072 | 0 | 1.4463 | 0 | 1.4072 | 1.4463 | 13.8126 | 10.7379 | 12.4054
39029.3704 | 2024 | 0 | 39029.3704 | 2204 | 0 |  | 1105.5 | 1257.5 | 123.5653 | 0 | 134.5543 | 0 | 1.2357 | 0 | 1.3455 | 0 | 1.2357 | 1.3455 | 29.6136 | 19.0281 | 28.378
39029.3725 | 2313 | 0 | 39029.3725 | 2603 | 0 |  | 1290 | 1442 | 141.2088 | 0 | 158.9133 | 0 | 1.4121 | 0 | 1.5891 | 0 | 1.4121 | 1.5891 | 13.4189 | 0.78294 | 12.0068
39029.3747 | 2567 | 0 | 39029.3747 | 2027 | 0 |  | 1475 | 1627 | 156.7155 | 0 | 123.7485 | 0 | 1.5672 | 0 | 1.2375 | 0 | 1.5672 | 1.2375 | 2.1963 | 29.4218 | 0.62918
39029.3768 | 2132 | 0 | 39029.3768 | 986 | 0 |  | 1659.5 | 1811.5 | 130.1587 | 0 | 60.1954 | 0 | 1.3016 | 0 | 0.60195 | 0 | 1.3016 | 0.60195 | 23.0478 | 166.0629 | 21.7463

## D7-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.768 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39029.3575 | 1 | 0 | 39029.3575 | 1 | 0 |  | -6 | 146 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263238 | 263238 | 263237.9994
39029.3597 | 608 | 0 | 39029.3597 | 1 | 0 |  | 178.5 | 330.5 | 37.1184 | 0 | 0.06105 | 0 | 0.37118 | 0 | 0.0006105 | 0 | 0.37118 | 0.0006105 | 333.1217 | 263238 | 332.7505
39029.3618 | 2434 | 0 | 39029.3618 | 2220 | 0 |  | 363.5 | 515.5 | 148.5958 | 0 | 135.5311 | 0 | 1.486 | 0 | 1.3553 | 0 | 1.486 | 1.3553 | 8.1915 | 18.6207 | 6.7055
39029.3639 | 2084 | 0 | 39029.3639 | 2360 | 0 |  | 548 | 700 | 127.2283 | 0 | 144.0781 | 0 | 1.2723 | 0 | 1.4408 | 0 | 1.2723 | 1.4408 | 26.3618 | 11.5839 | 25.0895
39029.3661 | 2401 | 0 | 39029.3661 | 2203 | 0 |  | 733 | 885 | 146.5812 | 0 | 134.4933 | 0 | 1.4658 | 0 | 1.3449 | 0 | 1.4658 | 1.3449 | 9.6785 | 19.5361 | 8.2127
39029.3682 | 2244 | 0 | 39029.3682 | 2617 | 0 |  | 918 | 1070 | 136.9963 | 0 | 159.768 | 0 | 1.37 | 0 | 1.5977 | 0 | 1.37 | 1.5977 | 17.352 | 0.62591 | 15.9821
39029.3703 | 2549 | 0 | 39029.3704 | 2066 | 0 |  | 1102.5 | 1254.5 | 155.6166 | 0 | 126.1294 | 0 | 1.5562 | 0 | 1.2613 | 0 | 1.5562 | 1.2613 | 3.3103 | 27.4627 | 1.7542
39029.3725 | 2309 | 0 | 39029.3725 | 2189 | 0 |  | 1287.5 | 1439.5 | 140.9646 | 0 | 133.6386 | 0 | 1.4096 | 0 | 1.3364 | 0 | 1.4096 | 1.3364 | 14.0485 | 20.3006 | 12.6389
39029.3746 | 2316 | 0 | 39029.3746 | 2617 | 0 |  | 1472 | 1624 | 141.3919 | 0 | 159.768 | 0 | 1.4139 | 0 | 1.5977 | 0 | 1.4139 | 1.5977 | 13.7038 | 0.62591 | 12.2899
39029.3768 | 1630 | 0 | 39029.3768 | 2 | 0 |  | 1657 | 1809 | 99.5116 | 0 | 0.1221 | 0 | 0.99512 | 0 | 0.001221 | 0 | 0.99512 | 0.001221 | 61.5571 | 131569 | 60.5619

## D7-D8
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.5238 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39029.3575 | 1 | 0 | 39029.3575 | 1 | 0 |  | -9 | 143 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262838 | 262838 | 262837.9994
39029.3596 | 426 | 103 | 39029.3596 | 1001 | 734 |  | 176 | 328 | 26.0073 | 6.2882 | 61.1111 | 44.8107 | 0.26007 | 0.062882 | 0.61111 | 0.44811 | 0.19719 | 0.163 | 704.6298 | 1000.038 | 1853.8281
39029.3618 | 2315 | 0 | 39029.3618 | 2511 | 0 |  | 360.5 | 512.5 | 141.3309 | 0 | 153.2967 | 0 | 1.4133 | 0 | 1.533 | 0 | 1.4133 | 1.533 | 13.5801 | 4.7145 | 12.1668
39029.3639 | 2166 | 0 | 39029.3639 | 2029 | 0 |  | 545.5 | 697.5 | 132.2344 | 0 | 123.8706 | 0 | 1.3223 | 0 | 1.2387 | 0 | 1.3223 | 1.2387 | 21.3934 | 29.5899 | 20.071
39029.366 | 2354 | 0 | 39029.3661 | 2116 | 0 |  | 730 | 882 | 143.7118 | 0 | 129.1819 | 0 | 1.4371 | 0 | 1.2918 | 0 | 1.4371 | 1.2918 | 11.6984 | 24.2618 | 10.2613
39029.3682 | 2259 | 0 | 39029.3682 | 2087 | 0 |  | 915 | 1067 | 137.9121 | 0 | 127.4115 | 0 | 1.3791 | 0 | 1.2741 | 0 | 1.3791 | 1.2741 | 16.3958 | 25.9885 | 15.0166
39029.3703 | 2270 | 0 | 39029.3703 | 2575 | 0 |  | 1099.5 | 1251.5 | 138.5836 | 0 | 157.2039 | 0 | 1.3858 | 0 | 1.572 | 0 | 1.3858 | 1.572 | 15.8317 | 2.1118 | 14.4459
39029.3725 | 2613 | 0 | 39029.3725 | 2398 | 0 |  | 1284.5 | 1436.5 | 159.5238 | 0 | 146.398 | 0 | 1.5952 | 0 | 1.464 | 0 | 1.5952 | 1.464 | 0.62687 | 9.6489 | 0.96837
39029.3746 | 2096 | 0 | 39029.3746 | 2301 | 0 |  | 1469.5 | 1621.5 | 127.9609 | 0 | 140.4762 | 0 | 1.2796 | 0 | 1.4048 | 0 | 1.2796 | 1.4048 | 25.4475 | 14.2712 | 24.1679
39029.3767 | 2029 | 0 | 39029.3767 | 1514 | 4 |  | 1654 | 1806 | 123.8706 | 0 | 92.4298 | 0.2442 | 1.2387 | 0 | 0.9243 | 0.002442 | 1.2387 | 0.92186 | 29.5899 | 74.1311 | 28.3512

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 7 |  |  | 2006-11-08 | 8:39
39029.3558 | 1 | 0 | 1 | Mix | 7-C | Tray A | IRMS | 1
39029.358 | 1 | 0 | 1 |  | 200 kW |  | Bundle
39029.3601 | 1 | 0 | 1
39029.3622 | 1147 | 1194 | 1
39029.3644 | 2558 | 0 | 1
39029.3665 | 2215 | 0 | 1
39029.3687 | 2342 | 0 | 1
39029.3708 | 2350 | 0 | 1
39029.3729 | 2207 | 3 | 1
39029.3751 | 1530 | 859 | 1
1
39029.3558 | 1 | 0 | 2
39029.3601 | 1 | 0 | 2
39029.3623 | 1083 | 1051 | 2
39029.3644 | 2075 | 0 | 2
39029.3665 | 2315 | 0 | 2
39029.3687 | 2573 | 0 | 2
39029.3708 | 2147 | 0 | 2
39029.373 | 2509 | 4 | 2
39029.3751 | 1576 | 785 | 2
2
39029.3559 | 1 | 0 | 3
39029.358 | 1 | 0 | 3
39029.3601 | 1 | 0 | 3
39029.3623 | 1 | 0 | 3
39029.3644 | 2249 | 0 | 3
39029.3666 | 2142 | 0 | 3
39029.3687 | 2372 | 0 | 3
39029.3708 | 2338 | 0 | 3
39029.373 | 2028 | 1 | 3
39029.3751 | 1546 | 830 | 3
3
39029.3559 | 1 | 0 | 4
39029.358 | 1 | 0 | 4
39029.3602 | 1 | 0 | 4
39029.3623 | 1901 | 0 | 4
39029.3644 | 2505 | 0 | 4
39029.3666 | 2171 | 0 | 4
39029.3687 | 2290 | 0 | 4
39029.3708 | 2587 | 0 | 4
39029.373 | 2135 | 1 | 4
39029.3751 | 1424 | 863 | 4
4
39029.3559 | 1 | 0 | 5
39029.358 | 1 | 0 | 5
39029.3602 | 1 | 0 | 5
39029.3623 | 1 | 0 | 5
39029.3644 | 1997 | 0 | 5
39029.3666 | 2367 | 0 | 5
39029.3687 | 2575 | 0 | 5
39029.3709 | 2420 | 0 | 5
39029.373 | 2280 | 2 | 5
39029.3751 | 1197 | 764 | 5
5
39029.3559 | 1 | 0 | 6
39029.358 | 1 | 0 | 6
39029.3602 | 1 | 0 | 6
39029.3623 | 1729 | 0 | 6
39029.3645 | 2131 | 0 | 6
39029.3666 | 2569 | 0 | 6
39029.3687 | 2539 | 0 | 6
39029.3709 | 2058 | 0 | 6
39029.373 | 2038 | 2 | 6
39029.3752 | 1257 | 972 | 6
6
39029.3559 | 1 | 0 | 7
39029.3581 | 1 | 0 | 7
39029.3602 | 1 | 0 | 7
39029.3623 | 1 | 0 | 7
39029.3645 | 2285 | 0 | 7
39029.3666 | 2471 | 0 | 7
39029.3688 | 1986 | 0 | 7
39029.3709 | 2416 | 0 | 7
39029.373 | 2051 | 0 | 7
39029.3752 | 820 | 0 | 7
7
39029.3559 | 1 | 0 | 8
39029.3581 | 1 | 0 | 8
39029.3602 | 1 | 0 | 8
39029.3624 | 1478 | 0 | 8
39029.3645 | 2087 | 0 | 8
39029.3666 | 2278 | 0 | 8
39029.3688 | 2536 | 0 | 8
39029.3709 | 2047 | 0 | 8
39029.3731 | 2029 | 0 | 8
39029.3752 | 2017 | 0 | 8
8
39029.356 | 1 | 0 | 9
39029.3581 | 1 | 0 | 9
39029.3602 | 1 | 0 | 9
39029.3624 | 1 | 0 | 9
39029.3645 | 2143 | 0 | 9
39029.3667 | 2409 | 0 | 9
39029.3688 | 2073 | 0 | 9
39029.3709 | 2304 | 0 | 9
39029.3731 | 2114 | 0 | 9
39029.3752 | 706 | 0 | 9
9
39029.356 | 1 | 0 | 10
39029.3581 | 1 | 0 | 10
39029.3603 | 1 | 0 | 10
39029.3624 | 2031 | 0 | 10
39029.3645 | 2600 | 0 | 10
39029.3667 | 2526 | 0 | 10
39029.3688 | 2587 | 0 | 10
39029.3709 | 2320 | 0 | 10
39029.3731 | 2509 | 0 | 10
39029.3752 | 2536 | 0 | 10
10
39029.356 | 1 | 0 | 11
39029.3581 | 1 | 0 | 11
39029.3603 | 1 | 0 | 11
39029.3624 | 2 | 0 | 11
39029.3645 | 2099 | 0 | 11
39029.3667 | 2571 | 0 | 11
39029.3688 | 2522 | 0 | 11
39029.371 | 2284 | 0 | 11
39029.3731 | 2289 | 0 | 11
39029.3752 | 650 | 0 | 11
11
39029.356 | 1 | 0 | 12
39029.3581 | 1 | 0 | 12
39029.3603 | 1792 | 0 | 12
39029.3624 | 2381 | 0 | 12
39029.3646 | 2195 | 0 | 12
39029.3667 | 2383 | 0 | 12
39029.3688 | 2349 | 0 | 12
39029.371 | 2095 | 0 | 12
39029.3731 | 2361 | 0 | 12
39029.3753 | 2048 | 0 | 12
12
39029.356 | 1 | 0 | 13
39029.3582 | 1 | 0 | 13
39029.3603 | 1 | 0 | 13
39029.3624 | 6 | 0 | 13
39029.3646 | 2122 | 0 | 13
39029.3667 | 2499 | 0 | 13
39029.3689 | 2074 | 0 | 13
39029.371 | 1998 | 0 | 13
39029.3731 | 2329 | 0 | 13
39029.3753 | 629 | 0 | 13
13
39029.356 | 1 | 0 | 14
39029.3582 | 1 | 0 | 14
39029.3603 | 2344 | 0 | 14
39029.3625 | 2025 | 0 | 14
39029.3646 | 2020 | 0 | 14
39029.3667 | 2410 | 0 | 14
39029.3689 | 2505 | 0 | 14
39029.371 | 2455 | 0 | 14
39029.3731 | 2500 | 0 | 14
39029.3753 | 1645 | 0 | 14
14
39029.3561 | 1 | 0 | 15
39029.3582 | 1 | 0 | 15
39029.3603 | 1 | 0 | 15
39029.3625 | 33 | 0 | 15
39029.3646 | 2578 | 0 | 15
39029.3667 | 2546 | 0 | 15
39029.3689 | 2501 | 0 | 15
39029.371 | 2547 | 0 | 15
39029.3732 | 2231 | 0 | 15
39029.3753 | 558 | 0 | 15
15
39029.3561 | 1 | 0 | 16
39029.3582 | 1 | 0 | 16
39029.3603 | 1817 | 0 | 16
39029.3625 | 2418 | 0 | 16
39029.3646 | 2106 | 0 | 16
39029.3668 | 2178 | 0 | 16
39029.3689 | 2171 | 0 | 16
39029.371 | 2132 | 0 | 16
39029.3732 | 2552 | 0 | 16
39029.3753 | 2117 | 0 | 16
16
39029.3561 | 1 | 0 | 17
39029.3582 | 1 | 0 | 17
39029.3604 | 1 | 0 | 17
39029.3625 | 95 | 0 | 17
39029.3646 | 2350 | 0 | 17
39029.3668 | 2581 | 0 | 17
39029.3689 | 2417 | 0 | 17
39029.3711 | 2044 | 0 | 17
39029.3732 | 2226 | 0 | 17
39029.3753 | 607 | 0 | 17
17
39029.3561 | 1 | 0 | 18
39029.3582 | 1 | 0 | 18
39029.3604 | 1 | 0 | 18
39029.3625 | 2014 | 0 | 18
39029.3647 | 2578 | 0 | 18
39029.3668 | 2518 | 0 | 18
39029.3689 | 2527 | 0 | 18
39029.3711 | 2629 | 0 | 18
39029.3732 | 2131 | 0 | 18
39029.3753 | 2112 | 0 | 18
18
39029.3561 | 1 | 0 | 19
39029.3583 | 1 | 0 | 19
39029.3604 | 1 | 0 | 19
39029.3625 | 147 | 0 | 19
39029.3647 | 2118 | 0 | 19
39029.3668 | 2349 | 0 | 19
39029.3689 | 2384 | 0 | 19
39029.3711 | 2477 | 0 | 19
39029.3732 | 1955 | 0 | 19
39029.3754 | 656 | 0 | 19
19
39029.3561 | 1 | 0 | 20
39029.3583 | 1 | 0 | 20
39029.3604 | 2581 | 0 | 20
39029.3625 | 2058 | 0 | 20
39029.3647 | 2493 | 0 | 20
39029.3668 | 2541 | 0 | 20
39029.369 | 2107 | 0 | 20
39029.3711 | 2179 | 0 | 20
39029.3732 | 2624 | 0 | 20
39029.3754 | 2009 | 0 | 20
20
39029.3562 | 1 | 0 | 21
39029.3583 | 1 | 0 | 21
39029.3604 | 1 | 0 | 21
39029.3626 | 199 | 0 | 21
39029.3647 | 2136 | 0 | 21
39029.3669 | 2073 | 0 | 21
39029.369 | 2279 | 0 | 21
39029.3711 | 2127 | 0 | 21
39029.3733 | 2421 | 0 | 21
39029.3754 | 583 | 0 | 21
21
39029.3562 | 1 | 0 | 22
39029.3583 | 0 | 0 | 22
39029.3605 | 2417 | 0 | 22
39029.3626 | 2572 | 0 | 22
39029.3647 | 2236 | 0 | 22
39029.3669 | 2360 | 0 | 22
39029.369 | 2233 | 0 | 22
39029.3711 | 2459 | 0 | 22
39029.3733 | 2584 | 0 | 22
39029.3754 | 2156 | 0 | 22
22
39029.3562 | 1 | 0 | 23
39029.3583 | 1 | 0 | 23
39029.3605 | 1 | 0 | 23
39029.3626 | 326 | 0 | 23
39029.3647 | 1986 | 0 | 23
39029.3669 | 2124 | 0 | 23
39029.369 | 2323 | 0 | 23
39029.3712 | 2117 | 0 | 23
39029.3733 | 2077 | 0 | 23
39029.3754 | 1326 | 1050 | 23
23
39029.3562 | 1 | 0 | 24
39029.3583 | 1 | 0 | 24
39029.3605 | 1 | 0 | 24
39029.3626 | 2104 | 0 | 24
39029.3648 | 2385 | 0 | 24
39029.3669 | 2065 | 0 | 24
39029.369 | 2594 | 0 | 24
39029.3712 | 2491 | 0 | 24
39029.3733 | 2196 | 0 | 24
39029.3755 | 1310 | 833 | 24
24
39029.3562 | 1 | 0 | 25
39029.3584 | 1 | 0 | 25
39029.3605 | 1 | 0 | 25
39029.3626 | 389 | 0 | 25
39029.3648 | 2221 | 0 | 25
39029.3669 | 2189 | 0 | 25
39029.3691 | 2029 | 0 | 25
39029.3712 | 2358 | 0 | 25
39029.3733 | 2410 | 0 | 25
39029.3755 | 1226 | 876 | 25
25
39029.3562 | 1 | 0 | 26
39029.3584 | 1 | 0 | 26
39029.3605 | 1 | 0 | 26
39029.3627 | 383 | 0 | 26
39029.3648 | 2297 | 0 | 26
39029.3669 | 2450 | 0 | 26
39029.3691 | 2543 | 0 | 26
39029.3712 | 2257 | 0 | 26
39029.3733 | 2455 | 0 | 26
39029.3755 | 1063 | 829 | 26
26
39029.3562 | 1 | 0 | 27
39029.3584 | 1 | 0 | 27
39029.3605 | 1 | 0 | 27
39029.3627 | 613 | 0 | 27
39029.3648 | 2233 | 0 | 27
39029.3669 | 2291 | 0 | 27
39029.3691 | 2302 | 0 | 27
39029.3712 | 2074 | 0 | 27
39029.3734 | 1982 | 0 | 27
39029.3755 | 724 | 0 | 27
27
39029.3563 | 1 | 0 | 28
39029.3584 | 1 | 0 | 28
39029.3605 | 1 | 0 | 28
39029.3627 | 1798 | 0 | 28
39029.3648 | 2329 | 0 | 28
39029.367 | 2079 | 0 | 28
39029.3691 | 2344 | 0 | 28
39029.3712 | 2214 | 0 | 28
39029.3734 | 2607 | 0 | 28
39029.3755 | 2275 | 0 | 28
28
39029.3563 | 1 | 0 | 29
39029.3584 | 1 | 0 | 29
39029.3606 | 1 | 0 | 29
39029.3627 | 640 | 0 | 29
39029.3648 | 2574 | 0 | 29
39029.367 | 2107 | 0 | 29
39029.3691 | 2238 | 0 | 29
39029.3712 | 2004 | 0 | 29
39029.3734 | 2378 | 0 | 29
39029.3755 | 716 | 0 | 29
29
39029.3563 | 1 | 0 | 30
39029.3584 | 1 | 0 | 30
39029.3606 | 1 | 0 | 30
39029.3627 | 1816 | 0 | 30
39029.3648 | 2024 | 0 | 30
39029.367 | 2543 | 0 | 30
39029.3691 | 2267 | 0 | 30
39029.3713 | 2573 | 0 | 30
39029.3734 | 2253 | 0 | 30
39029.3755 | 2495 | 0 | 30
30
39029.3563 | 1 | 0 | 31
39029.3584 | 1 | 0 | 31
39029.3606 | 1 | 0 | 31
39029.3627 | 650 | 0 | 31
39029.3649 | 2200 | 0 | 31
39029.367 | 2367 | 0 | 31
39029.3691 | 2520 | 0 | 31
39029.3713 | 2562 | 0 | 31
39029.3734 | 2047 | 0 | 31
39029.3756 | 649 | 0 | 31
31
39029.3563 | 1 | 0 | 32
39029.3585 | 1 | 0 | 32
39029.3606 | 2188 | 0 | 32
39029.3627 | 2059 | 0 | 32
39029.3649 | 2407 | 0 | 32
39029.367 | 2581 | 0 | 32
39029.3692 | 2130 | 0 | 32
39029.3713 | 2309 | 0 | 32
39029.3734 | 2030 | 0 | 32
39029.3756 | 1512 | 0 | 32
32
39029.3563 | 1 | 0 | 33
39029.3585 | 1 | 0 | 33
39029.3606 | 1 | 0 | 33
39029.3628 | 894 | 0 | 33
39029.3649 | 1986 | 0 | 33
39029.367 | 2580 | 0 | 33
39029.3692 | 2124 | 0 | 33
39029.3713 | 2097 | 0 | 33
39029.3735 | 2491 | 0 | 33
39029.3756 | 384 | 0 | 33
33
39029.3564 | 1 | 0 | 34
39029.3585 | 1 | 0 | 34
39029.3606 | 2534 | 0 | 34
39029.3628 | 2318 | 0 | 34
39029.3649 | 2142 | 0 | 34
39029.3671 | 2172 | 0 | 34
39029.3692 | 2445 | 0 | 34
39029.3713 | 2511 | 0 | 34
39029.3735 | 2116 | 0 | 34
39029.3756 | 1737 | 0 | 34
34
39029.3564 | 1 | 0 | 35
39029.3585 | 1 | 0 | 35
39029.3607 | 2 | 0 | 35
39029.3628 | 1182 | 0 | 35
39029.3649 | 2109 | 0 | 35
39029.3671 | 2434 | 0 | 35
39029.3692 | 2290 | 0 | 35
39029.3714 | 2198 | 0 | 35
39029.3735 | 2517 | 0 | 35
39029.3756 | 341 | 0 | 35
35
39029.3564 | 1 | 0 | 36
39029.3585 | 1 | 0 | 36
39029.3607 | 2115 | 0 | 36
39029.3628 | 2087 | 0 | 36
39029.365 | 2489 | 0 | 36
39029.3671 | 2182 | 0 | 36
39029.3692 | 2030 | 0 | 36
39029.3714 | 2599 | 0 | 36
39029.3735 | 2480 | 0 | 36
39029.3756 | 2333 | 0 | 36
36
39029.3564 | 1 | 0 | 37
39029.3586 | 1 | 0 | 37
39029.3607 | 1 | 0 | 37
39029.3628 | 893 | 0 | 37
39029.365 | 2310 | 0 | 37
39029.3671 | 2541 | 0 | 37
39029.3692 | 2487 | 0 | 37
39029.3714 | 2000 | 0 | 37
39029.3735 | 2322 | 0 | 37
39029.3757 | 646 | 0 | 37
37
39029.3564 | 1 | 0 | 38
39029.3586 | 0 | 0 | 38
39029.3607 | 1801 | 0 | 38
39029.3628 | 2078 | 0 | 38
39029.365 | 2297 | 0 | 38
39029.3671 | 2612 | 0 | 38
39029.3693 | 2397 | 0 | 38
39029.3714 | 2588 | 0 | 38
39029.3735 | 2601 | 0 | 38
39029.3757 | 2527 | 0 | 38
38
39029.3564 | 1 | 0 | 39
39029.3586 | 1 | 0 | 39
39029.3607 | 1 | 0 | 39
39029.3629 | 924 | 0 | 39
39029.365 | 2573 | 0 | 39
39029.3671 | 2557 | 0 | 39
39029.3693 | 2091 | 0 | 39
39029.3714 | 2085 | 0 | 39
39029.3736 | 1923 | 0 | 39
39029.3757 | 558 | 0 | 39
39
39029.3565 | 1 | 0 | 40
39029.3586 | 1 | 0 | 40
39029.3607 | 2357 | 0 | 40
39029.3629 | 2226 | 0 | 40
39029.365 | 2066 | 0 | 40
39029.3672 | 2502 | 0 | 40
39029.3693 | 2208 | 0 | 40
39029.3714 | 2330 | 0 | 40
39029.3736 | 2353 | 0 | 40
39029.3757 | 2588 | 0 | 40
40
39029.3565 | 1 | 0 | 41
39029.3586 | 0 | 0 | 41
39029.3608 | 1 | 0 | 41
39029.3629 | 1111 | 0 | 41
39029.365 | 2133 | 0 | 41
39029.3672 | 2120 | 0 | 41
39029.3693 | 2326 | 0 | 41
39029.3714 | 2051 | 0 | 41
39029.3736 | 2325 | 0 | 41
39029.3757 | 442 | 0 | 41
41
39029.3565 | 1 | 0 | 42
39029.3586 | 1 | 0 | 42
39029.3608 | 2302 | 0 | 42
39029.3629 | 2570 | 0 | 42
39029.365 | 2507 | 0 | 42
39029.3672 | 2176 | 0 | 42
39029.3693 | 2246 | 0 | 42
39029.3715 | 2222 | 0 | 42
39029.3736 | 2628 | 0 | 42
39029.3757 | 2249 | 0 | 42
42
39029.3565 | 1 | 0 | 43
39029.3586 | 1 | 0 | 43
39029.3608 | 1105 | 1069 | 43
39029.3629 | 2434 | 5 | 43
39029.3651 | 2222 | 0 | 43
39029.3672 | 2587 | 0 | 43
39029.3693 | 2335 | 0 | 43
39029.3715 | 2500 | 0 | 43
39029.3736 | 2274 | 2 | 43
39029.3758 | 1087 | 832 | 43
43
39029.3565 | 1 | 0 | 44
39029.3587 | 1 | 0 | 44
39029.3608 | 954 | 977 | 44
39029.3629 | 2103 | 3 | 44
39029.3651 | 2395 | 0 | 44
39029.3672 | 2089 | 0 | 44
39029.3694 | 2287 | 0 | 44
39029.3715 | 2221 | 0 | 44
39029.3736 | 2330 | 4 | 44
39029.3758 | 1098 | 993 | 44
44
39029.3565 | 1 | 0 | 45
39029.3587 | 1 | 0 | 45
39029.3608 | 2 | 0 | 45
39029.363 | 1960 | 1 | 45
39029.3651 | 2446 | 0 | 45
39029.3672 | 2354 | 0 | 45
39029.3694 | 2603 | 0 | 45
39029.3715 | 2219 | 0 | 45
39029.3736 | 2288 | 0 | 45
39029.3758 | 313 | 0 | 45
45
39029.3566 | 1 | 0 | 46
39029.3587 | 1 | 0 | 46
39029.3608 | 1 | 0 | 46
39029.363 | 1900 | 0 | 46
39029.3651 | 2489 | 0 | 46
39029.3672 | 2137 | 0 | 46
39029.3694 | 2011 | 0 | 46
39029.3715 | 2047 | 0 | 46
39029.3737 | 2545 | 0 | 46
39029.3758 | 2392 | 0 | 46
46
39029.3566 | 1 | 0 | 47
39029.3587 | 1 | 0 | 47
39029.3609 | 3 | 0 | 47
39029.363 | 2177 | 0 | 47
39029.3651 | 1999 | 0 | 47
39029.3673 | 2190 | 0 | 47
39029.3694 | 2296 | 0 | 47
39029.3715 | 2257 | 0 | 47
39029.3737 | 1966 | 0 | 47
39029.3758 | 351 | 0 | 47
47
39029.3566 | 1 | 0 | 48
39029.3587 | 1 | 0 | 48
39029.3609 | 1 | 0 | 48
39029.363 | 1944 | 0 | 48
39029.3651 | 2454 | 0 | 48
39029.3673 | 2127 | 0 | 48
39029.3694 | 1995 | 0 | 48
39029.3716 | 2285 | 0 | 48
39029.3737 | 2571 | 0 | 48
39029.3758 | 2309 | 0 | 48
48
39029.3566 | 1 | 0 | 49
39029.3587 | 1 | 0 | 49
39029.3609 | 2 | 0 | 49
39029.363 | 1919 | 0 | 49
39029.3652 | 2282 | 0 | 49
39029.3673 | 2168 | 0 | 49
39029.3694 | 2200 | 0 | 49
39029.3716 | 2085 | 0 | 49
39029.3737 | 2243 | 0 | 49
39029.3759 | 334 | 0 | 49
49
39029.3566 | 1 | 0 | 50
39029.3588 | 1 | 0 | 50
39029.3609 | 2466 | 0 | 50
39029.363 | 2420 | 0 | 50
39029.3652 | 2275 | 0 | 50
39029.3673 | 2565 | 0 | 50
39029.3695 | 2436 | 0 | 50
39029.3716 | 2355 | 0 | 50
39029.3737 | 2095 | 0 | 50
39029.3759 | 1712 | 0 | 50
50
39029.3566 | 1 | 0 | 51
39029.3588 | 1 | 0 | 51
39029.3609 | 4 | 0 | 51
39029.3631 | 2250 | 0 | 51
39029.3652 | 2066 | 0 | 51
39029.3673 | 2441 | 0 | 51
39029.3695 | 2175 | 0 | 51
39029.3716 | 2338 | 0 | 51
39029.3737 | 1910 | 0 | 51
39029.3759 | 291 | 2 | 51
51
39029.3567 | 1 | 0 | 52
39029.3588 | 1 | 0 | 52
39029.3609 | 2024 | 0 | 52
39029.3631 | 2624 | 0 | 52
39029.3652 | 2342 | 0 | 52
39029.3673 | 2611 | 0 | 52
39029.3695 | 2542 | 0 | 52
39029.3716 | 2131 | 0 | 52
39029.3738 | 2078 | 0 | 52
39029.3759 | 1621 | 0 | 52
52
39029.3567 | 1 | 0 | 53
39029.3588 | 0 | 0 | 53
39029.3609 | 2 | 0 | 53
39029.3631 | 1961 | 0 | 53
39029.3652 | 2552 | 0 | 53
39029.3674 | 2538 | 0 | 53
39029.3695 | 2006 | 0 | 53
39029.3716 | 1993 | 0 | 53
39029.3738 | 2316 | 0 | 53
39029.3759 | 333 | 0 | 53
53
39029.3567 | 1 | 0 | 54
39029.3588 | 1 | 0 | 54
39029.361 | 1939 | 0 | 54
39029.3631 | 2324 | 0 | 54
39029.3652 | 2053 | 0 | 54
39029.3674 | 2281 | 0 | 54
39029.3695 | 2141 | 0 | 54
39029.3717 | 2573 | 0 | 54
39029.3738 | 2157 | 0 | 54
39029.3759 | 1987 | 0 | 54
54
39029.3567 | 0 | 0 | 55
39029.3588 | 0 | 0 | 55
39029.361 | 2 | 0 | 55
39029.3631 | 2528 | 0 | 55
39029.3653 | 2117 | 0 | 55
39029.3674 | 2253 | 0 | 55
39029.3695 | 2338 | 0 | 55
39029.3717 | 2578 | 0 | 55
39029.3738 | 2275 | 0 | 55
39029.3759 | 386 | 14 | 55
55
39029.3567 | 1 | 0 | 56
39029.3589 | 1 | 0 | 56
39029.361 | 2230 | 0 | 56
39029.3631 | 2458 | 0 | 56
39029.3653 | 2145 | 0 | 56
39029.3674 | 2035 | 0 | 56
39029.3695 | 2059 | 0 | 56
39029.3717 | 2207 | 0 | 56
39029.3738 | 2106 | 0 | 56
39029.376 | 1778 | 0 | 56
56
39029.3567 | 1 | 0 | 57
39029.3589 | 1 | 0 | 57
39029.361 | 1 | 0 | 57
39029.3631 | 2540 | 0 | 57
39029.3653 | 2503 | 0 | 57
39029.3674 | 2009 | 0 | 57
39029.3696 | 2001 | 0 | 57
39029.3717 | 2033 | 0 | 57
39029.3738 | 2045 | 0 | 57
39029.376 | 120 | 0 | 57
57
39029.3567 | 1 | 0 | 58
39029.3589 | 1 | 0 | 58
39029.361 | 2473 | 0 | 58
39029.3632 | 2299 | 0 | 58
39029.3653 | 2430 | 0 | 58
39029.3674 | 2601 | 0 | 58
39029.3696 | 2610 | 0 | 58
39029.3717 | 2559 | 0 | 58
39029.3739 | 2417 | 0 | 58
39029.376 | 2268 | 0 | 58
58
39029.3568 | 1 | 0 | 59
39029.3589 | 1 | 0 | 59
39029.361 | 1 | 0 | 59
39029.3632 | 2187 | 0 | 59
39029.3653 | 2009 | 0 | 59
39029.3675 | 2295 | 0 | 59
39029.3696 | 2265 | 0 | 59
39029.3717 | 2087 | 0 | 59
39029.3739 | 1870 | 0 | 59
39029.376 | 201 | 0 | 59
59
39029.3568 | 1 | 0 | 60
39029.3589 | 1 | 0 | 60
39029.3611 | 2037 | 0 | 60
39029.3632 | 2561 | 0 | 60
39029.3653 | 2305 | 0 | 60
39029.3675 | 2195 | 0 | 60
39029.3696 | 2192 | 0 | 60
39029.3718 | 2360 | 0 | 60
39029.3739 | 2487 | 0 | 60
39029.376 | 2382 | 0 | 60
60
39029.3568 | 1 | 0 | 61
39029.3589 | 1 | 0 | 61
39029.3611 | 1 | 0 | 61
39029.3632 | 2227 | 0 | 61
39029.3654 | 2058 | 0 | 61
39029.3675 | 2053 | 0 | 61
39029.3696 | 2440 | 0 | 61
39029.3718 | 2076 | 0 | 61
39029.3739 | 1962 | 0 | 61
39029.3761 | 109 | 34 | 61
61
39029.3568 | 1 | 0 | 62
39029.359 | 1 | 0 | 62
39029.3611 | 20 | 0 | 62
39029.3632 | 2027 | 0 | 62
39029.3654 | 2136 | 0 | 62
39029.3675 | 2570 | 0 | 62
39029.3697 | 2179 | 0 | 62
39029.3718 | 2513 | 0 | 62
39029.3739 | 2206 | 0 | 62
39029.3761 | 133 | 28 | 62
62
39029.3568 | 0 | 0 | 63
39029.359 | 1 | 0 | 63
39029.3611 | 1 | 0 | 63
39029.3633 | 2509 | 0 | 63
39029.3654 | 2322 | 0 | 63
39029.3675 | 2403 | 0 | 63
39029.3697 | 2027 | 0 | 63
39029.3718 | 2515 | 0 | 63
39029.3739 | 1960 | 0 | 63
39029.3761 | 51 | 1 | 63
63
39029.3569 | 1 | 0 | 64
39029.359 | 1 | 0 | 64
39029.3611 | 34 | 0 | 64
39029.3633 | 2039 | 0 | 64
39029.3654 | 2443 | 0 | 64
39029.3675 | 2122 | 0 | 64
39029.3697 | 2498 | 0 | 64
39029.3718 | 2403 | 0 | 64
39029.3761 | 21 | 0 | 64
64
39029.3569 | 1 | 0 | 65
39029.359 | 1 | 0 | 65
39029.3611 | 1 | 0 | 65
39029.3633 | 2251 | 0 | 65
39029.3654 | 2066 | 0 | 65
39029.3676 | 2454 | 0 | 65
39029.3697 | 2341 | 0 | 65
39029.3718 | 2372 | 0 | 65
39029.374 | 1718 | 0 | 65
39029.3761 | 157 | 0 | 65
65
39029.3569 | 1 | 0 | 66
39029.359 | 1 | 0 | 66
39029.3612 | 2308 | 0 | 66
39029.3633 | 2079 | 0 | 66
39029.3654 | 2535 | 0 | 66
39029.3676 | 2585 | 0 | 66
39029.3697 | 2627 | 0 | 66
39029.3719 | 2024 | 0 | 66
39029.374 | 2272 | 0 | 66
39029.3761 | 1505 | 0 | 66
66
39029.3569 | 0 | 0 | 67
39029.359 | 1 | 0 | 67
39029.3612 | 3 | 0 | 67
39029.3633 | 2409 | 0 | 67
39029.3655 | 2119 | 0 | 67
39029.3676 | 2373 | 0 | 67
39029.3697 | 2525 | 0 | 67
39029.3719 | 2379 | 0 | 67
39029.374 | 1860 | 0 | 67
39029.3761 | 307 | 0 | 67
67
39029.3569 | 1 | 0 | 68
39029.3591 | 1 | 0 | 68
39029.3612 | 2048 | 0 | 68
39029.3633 | 2080 | 0 | 68
39029.3655 | 2332 | 0 | 68
39029.3676 | 2297 | 0 | 68
39029.3697 | 2224 | 0 | 68
39029.3719 | 2190 | 0 | 68
39029.374 | 2267 | 0 | 68
39029.3762 | 1870 | 0 | 68
68
39029.3569 | 1 | 0 | 69
39029.3591 | 1 | 0 | 69
39029.3612 | 6 | 0 | 69
39029.3633 | 2143 | 0 | 69
39029.3655 | 2591 | 0 | 69
39029.3676 | 2434 | 0 | 69
39029.3698 | 2456 | 0 | 69
39029.3719 | 2440 | 0 | 69
39029.374 | 2016 | 0 | 69
39029.3762 | 234 | 0 | 69
69
39029.3569 | 0 | 0 | 70
39029.3591 | 1 | 0 | 70
39029.3612 | 1964 | 0 | 70
39029.3634 | 2574 | 0 | 70
39029.3655 | 2410 | 0 | 70
39029.3676 | 2291 | 0 | 70
39029.3698 | 2624 | 0 | 70
39029.3719 | 2102 | 0 | 70
39029.3741 | 2075 | 0 | 70
39029.3762 | 1594 | 0 | 70
70
39029.357 | 1 | 0 | 71
39029.3591 | 1 | 0 | 71
39029.3612 | 53 | 0 | 71
39029.3634 | 2529 | 0 | 71
39029.3655 | 2260 | 0 | 71
39029.3677 | 2396 | 0 | 71
39029.3698 | 2432 | 0 | 71
39029.3719 | 2052 | 0 | 71
39029.3741 | 1744 | 0 | 71
39029.3762 | 204 | 0 | 71
71
39029.357 | 1 | 0 | 72
39029.3591 | 1 | 0 | 72
39029.3613 | 2095 | 0 | 72
39029.3634 | 2476 | 0 | 72
39029.3655 | 2081 | 0 | 72
39029.3677 | 2550 | 0 | 72
39029.3698 | 2164 | 0 | 72
39029.3719 | 2439 | 0 | 72
39029.3741 | 2434 | 0 | 72
39029.3762 | 1558 | 0 | 72
72
39029.357 | 1 | 0 | 73
39029.3591 | 1 | 0 | 73
39029.3613 | 114 | 0 | 73
39029.3634 | 2085 | 0 | 73
39029.3656 | 2233 | 0 | 73
39029.3677 | 2056 | 0 | 73
39029.3698 | 2046 | 0 | 73
39029.372 | 2252 | 0 | 73
39029.3741 | 1747 | 0 | 73
39029.3762 | 155 | 0 | 73
73
39029.357 | 1 | 0 | 74
39029.3592 | 1 | 0 | 74
39029.3613 | 2568 | 0 | 74
39029.3634 | 2366 | 0 | 74
39029.3656 | 2513 | 0 | 74
39029.3677 | 2032 | 0 | 74
39029.3698 | 2563 | 0 | 74
39029.372 | 2041 | 0 | 74
39029.3741 | 2032 | 0 | 74
39029.3763 | 2282 | 0 | 74
74
39029.357 | 1 | 0 | 75
39029.3592 | 1 | 0 | 75
39029.3613 | 133 | 0 | 75
39029.3634 | 2221 | 0 | 75
39029.3656 | 2007 | 0 | 75
39029.3677 | 2353 | 0 | 75
39029.3699 | 2032 | 0 | 75
39029.372 | 2456 | 0 | 75
39029.3741 | 1713 | 0 | 75
39029.3763 | 61 | 0 | 75
75
39029.357 | 1 | 0 | 76
39029.3592 | 1 | 0 | 76
39029.3613 | 2109 | 0 | 76
39029.3635 | 2073 | 0 | 76
39029.3656 | 2226 | 0 | 76
39029.3677 | 2156 | 0 | 76
39029.3699 | 2318 | 0 | 76
39029.372 | 2612 | 0 | 76
39029.3742 | 2482 | 0 | 76
39029.3763 | 2512 | 0 | 76
76
39029.3571 | 1 | 0 | 77
39029.3592 | 1 | 0 | 77
39029.3613 | 1063 | 217 | 77
39029.3635 | 2129 | 0 | 77
39029.3656 | 2381 | 0 | 77
39029.3678 | 2425 | 0 | 77
39029.3699 | 2089 | 0 | 77
39029.372 | 2215 | 0 | 77
39029.3742 | 1916 | 49 | 77
39029.3763 | 1218 | 1144 | 77
77
39029.3571 | 1 | 0 | 78
39029.3592 | 0 | 0 | 78
39029.3614 | 2 | 0 | 78
39029.3635 | 1974 | 0 | 78
39029.3656 | 2044 | 0 | 78
39029.3678 | 2586 | 0 | 78
39029.3699 | 2215 | 0 | 78
39029.372 | 2179 | 0 | 78
39029.3742 | 1922 | 55 | 78
39029.3763 | 1145 | 1058 | 78
78
39029.3571 | 1 | 0 | 79
39029.3592 | 1 | 0 | 79
39029.3614 | 1059 | 0 | 79
39029.3635 | 2073 | 0 | 79
39029.3656 | 2601 | 0 | 79
39029.3678 | 2320 | 0 | 79
39029.3699 | 2414 | 0 | 79
39029.3721 | 2234 | 0 | 79
39029.3742 | 2577 | 0 | 79
39029.3763 | 41 | 0 | 79
79
39029.3571 | 1 | 0 | 80
39029.3592 | 1 | 0 | 80
39029.3614 | 2555 | 0 | 80
39029.3635 | 2532 | 0 | 80
39029.3657 | 2061 | 0 | 80
39029.3678 | 2286 | 0 | 80
39029.3699 | 2210 | 0 | 80
39029.3721 | 2573 | 0 | 80
39029.3742 | 2550 | 0 | 80
39029.3764 | 1853 | 0 | 80
80
39029.3571 | 1 | 0 | 81
39029.3593 | 1 | 0 | 81
39029.3614 | 1231 | 0 | 81
39029.3657 | 2215 | 0 | 81
39029.3678 | 2350 | 0 | 81
39029.37 | 2169 | 0 | 81
39029.3721 | 2414 | 0 | 81
39029.3742 | 2143 | 0 | 81
39029.3764 | 9 | 0 | 81
81
39029.3571 | 1 | 0 | 82
39029.3593 | 1 | 0 | 82
39029.3614 | 2288 | 0 | 82
39029.3636 | 2300 | 0 | 82
39029.3657 | 2031 | 0 | 82
39029.3678 | 2379 | 0 | 82
39029.37 | 2037 | 0 | 82
39029.3721 | 2176 | 0 | 82
39029.3742 | 1999 | 0 | 82
39029.3764 | 1643 | 0 | 82
82
39029.3572 | 1 | 0 | 83
39029.3593 | 1 | 0 | 83
39029.3614 | 1323 | 0 | 83
39029.3636 | 2098 | 0 | 83
39029.3657 | 2234 | 0 | 83
39029.3678 | 2507 | 0 | 83
39029.37 | 2560 | 0 | 83
39029.3721 | 2082 | 0 | 83
39029.3743 | 2052 | 0 | 83
39029.3764 | 3 | 0 | 83
83
39029.3572 | 1 | 0 | 84
39029.3593 | 1 | 0 | 84
39029.3614 | 1349 | 0 | 84
39029.3636 | 2619 | 0 | 84
39029.3657 | 2447 | 0 | 84
39029.3679 | 2542 | 0 | 84
39029.37 | 2487 | 0 | 84
39029.3721 | 2226 | 0 | 84
39029.3743 | 2104 | 0 | 84
39029.3764 | 1876 | 0 | 84
84
39029.3572 | 1 | 0 | 85
39029.3593 | 1 | 0 | 85
39029.3615 | 1817 | 0 | 85
39029.3636 | 2418 | 0 | 85
39029.3657 | 2203 | 0 | 85
39029.3679 | 2240 | 0 | 85
39029.37 | 2534 | 0 | 85
39029.3722 | 2513 | 0 | 85
39029.3743 | 2214 | 0 | 85
39029.3764 | 4 | 0 | 85
85
39029.3572 | 1 | 0 | 86
39029.3593 | 1 | 0 | 86
39029.3615 | 2430 | 0 | 86
39029.3636 | 2339 | 0 | 86
39029.3658 | 2543 | 0 | 86
39029.3679 | 2080 | 0 | 86
39029.37 | 2447 | 0 | 86
39029.3722 | 2098 | 0 | 86
39029.3743 | 2632 | 0 | 86
39029.3765 | 1596 | 0 | 86
86
39029.3572 | 0 | 0 | 87
39029.3594 | 0 | 0 | 87
39029.3615 | 1951 | 0 | 87
39029.3636 | 2568 | 0 | 87
39029.3658 | 2015 | 0 | 87
39029.3679 | 1996 | 0 | 87
39029.3701 | 2589 | 0 | 87
39029.3722 | 2174 | 0 | 87
39029.3743 | 2216 | 0 | 87
39029.3765 | 3 | 0 | 87
87
39029.3572 | 1 | 0 | 88
39029.3594 | 1 | 0 | 88
39029.3615 | 2333 | 0 | 88
39029.3637 | 2595 | 0 | 88
39029.3658 | 2153 | 0 | 88
39029.3679 | 2429 | 0 | 88
39029.3701 | 2503 | 0 | 88
39029.3722 | 2632 | 0 | 88
39029.3744 | 2235 | 0 | 88
39029.3765 | 2281 | 0 | 88
88
39029.3573 | 1 | 0 | 89
39029.3594 | 1 | 0 | 89
39029.3615 | 261 | 0 | 89
39029.3637 | 2242 | 0 | 89
39029.3658 | 2438 | 0 | 89
39029.368 | 2458 | 0 | 89
39029.3701 | 2165 | 0 | 89
39029.3722 | 2326 | 0 | 89
39029.3744 | 2341 | 0 | 89
39029.3765 | 3 | 0 | 89
89
39029.3573 | 1 | 0 | 90
39029.3594 | 1 | 0 | 90
39029.3616 | 2146 | 0 | 90
39029.3637 | 2183 | 0 | 90
39029.3658 | 2478 | 0 | 90
39029.368 | 2617 | 0 | 90
39029.3701 | 2227 | 0 | 90
39029.3722 | 2044 | 0 | 90
39029.3744 | 2573 | 0 | 90
39029.3765 | 2481 | 0 | 90
90
39029.3573 | 1 | 0 | 91
39029.3594 | 1 | 0 | 91
39029.3616 | 1102 | 0 | 91
39029.3637 | 2029 | 0 | 91
39029.3658 | 2110 | 0 | 91
39029.368 | 2133 | 0 | 91
39029.3701 | 2398 | 0 | 91
39029.3723 | 2032 | 0 | 91
39029.3744 | 2104 | 0 | 91
39029.3765 | 3 | 0 | 91
91
39029.3573 | 1 | 0 | 92
39029.3594 | 2 | 0 | 92
39029.3616 | 2409 | 0 | 92
39029.3637 | 2112 | 0 | 92
39029.3659 | 2326 | 0 | 92
39029.368 | 2558 | 0 | 92
39029.3701 | 2614 | 0 | 92
39029.3723 | 2278 | 0 | 92
39029.3744 | 2556 | 0 | 92
39029.3766 | 1998 | 0 | 92
92
39029.3573 | 1 | 0 | 93
39029.3595 | 1 | 0 | 93
39029.3616 | 1862 | 0 | 93
39029.3637 | 2350 | 0 | 93
39029.3659 | 2536 | 0 | 93
39029.368 | 2448 | 0 | 93
39029.3702 | 2179 | 0 | 93
39029.3723 | 2045 | 0 | 93
39029.3744 | 2109 | 0 | 93
39029.3766 | 3 | 0 | 93
93
39029.3573 | 1 | 0 | 94
39029.3595 | 1 | 0 | 94
39029.3616 | 2085 | 0 | 94
39029.3637 | 2601 | 0 | 94
39029.3659 | 2403 | 0 | 94
39029.368 | 2529 | 0 | 94
39029.3702 | 2281 | 0 | 94
39029.3723 | 2398 | 0 | 94
39029.3744 | 2218 | 0 | 94
39029.3766 | 1520 | 0 | 94
94
39029.3573 | 0 | 0 | 95
39029.3595 | 1 | 0 | 95
39029.3616 | 1723 | 0 | 95
39029.3638 | 2042 | 0 | 95
39029.3659 | 2267 | 0 | 95
39029.368 | 2547 | 0 | 95
39029.3702 | 2501 | 0 | 95
39029.3723 | 2563 | 0 | 95
39029.3745 | 2092 | 0 | 95
39029.3766 | 2 | 0 | 95
95
39029.3574 | 1 | 0 | 96
39029.3595 | 1 | 0 | 96
39029.3616 | 2349 | 0 | 96
39029.3638 | 2114 | 0 | 96
39029.3659 | 2163 | 0 | 96
39029.3681 | 2157 | 0 | 96
39029.3702 | 2621 | 0 | 96
39029.3723 | 2337 | 0 | 96
39029.3745 | 2537 | 0 | 96
39029.3766 | 1951 | 0 | 96
96
39029.3574 | 0 | 0 | 97
39029.3595 | 1 | 0 | 97
39029.3617 | 1750 | 0 | 97
39029.3638 | 2282 | 0 | 97
39029.3659 | 2465 | 0 | 97
39029.3681 | 2130 | 0 | 97
39029.3702 | 2172 | 0 | 97
39029.3723 | 2145 | 0 | 97
39029.3745 | 2434 | 0 | 97
39029.3766 | 3 | 0 | 97
97
39029.3574 | 1 | 0 | 98
39029.3595 | 1 | 0 | 98
39029.3617 | 2030 | 0 | 98
39029.3638 | 2170 | 0 | 98
39029.366 | 2553 | 0 | 98
39029.3681 | 2317 | 0 | 98
39029.3702 | 2450 | 0 | 98
39029.3724 | 2075 | 0 | 98
39029.3745 | 2307 | 0 | 98
39029.3766 | 1656 | 0 | 98
98
39029.3574 | 1 | 0 | 99
39029.3596 | 1 | 0 | 99
39029.3617 | 1866 | 0 | 99
39029.3638 | 2119 | 0 | 99
39029.366 | 2565 | 0 | 99
39029.3681 | 2467 | 0 | 99
39029.3702 | 2416 | 0 | 99
39029.3724 | 2151 | 0 | 99
39029.3745 | 2092 | 0 | 99
39029.3767 | 3 | 0 | 99
99
39029.3574 | 1 | 0 | 100
39029.3596 | 1 | 0 | 100
39029.3617 | 2006 | 0 | 100
39029.3639 | 2629 | 0 | 100
39029.366 | 2136 | 0 | 100
39029.3681 | 2620 | 0 | 100
39029.3703 | 2273 | 0 | 100
39029.3724 | 2419 | 0 | 100
39029.3745 | 2603 | 0 | 100
39029.3767 | 2184 | 0 | 100
100
39029.3575 | 1 | 0 | 101
39029.3596 | 1 | 0 | 101
39029.3617 | 1950 | 0 | 101
39029.3639 | 2159 | 0 | 101
39029.366 | 2394 | 0 | 101
39029.3681 | 2119 | 0 | 101
39029.3703 | 2515 | 0 | 101
39029.3724 | 2425 | 0 | 101
39029.3746 | 2549 | 0 | 101
39029.3767 | 7 | 0 | 101
101
39029.3575 | 1 | 0 | 102
39029.3596 | 1 | 0 | 102
39029.3617 | 2490 | 0 | 102
39029.3639 | 2253 | 0 | 102
39029.366 | 2391 | 0 | 102
39029.3682 | 2114 | 0 | 102
39029.3703 | 2069 | 0 | 102
39029.3724 | 2030 | 0 | 102
39029.3746 | 2504 | 0 | 102
39029.3767 | 2213 | 0 | 102
102
39029.3575 | 1 | 0 | 103
39029.3596 | 426 | 103 | 103
39029.3618 | 2315 | 0 | 103
39029.3639 | 2166 | 0 | 103
39029.366 | 2354 | 0 | 103
39029.3682 | 2259 | 0 | 103
39029.3703 | 2270 | 0 | 103
39029.3725 | 2613 | 0 | 103
39029.3746 | 2096 | 0 | 103
39029.3767 | 2029 | 0 | 103
103
39029.3575 | 1 | 0 | 104
39029.3596 | 1001 | 734 | 104
39029.3618 | 2511 | 0 | 104
39029.3639 | 2029 | 0 | 104
39029.3661 | 2116 | 0 | 104
39029.3682 | 2087 | 0 | 104
39029.3703 | 2575 | 0 | 104
39029.3725 | 2398 | 0 | 104
39029.3746 | 2301 | 0 | 104
39029.3767 | 1514 | 4 | 104
104
39029.3575 | 1 | 0 | 105
39029.3597 | 608 | 0 | 105
39029.3618 | 2434 | 0 | 105
39029.3639 | 2084 | 0 | 105
39029.3661 | 2401 | 0 | 105
39029.3682 | 2244 | 0 | 105
39029.3703 | 2549 | 0 | 105
39029.3725 | 2309 | 0 | 105
39029.3746 | 2316 | 0 | 105
39029.3768 | 1630 | 0 | 105
105
39029.3575 | 1 | 0 | 106
39029.3597 | 1 | 0 | 106
39029.3618 | 2220 | 0 | 106
39029.3639 | 2360 | 0 | 106
39029.3661 | 2203 | 0 | 106
39029.3682 | 2617 | 0 | 106
39029.3704 | 2066 | 0 | 106
39029.3725 | 2189 | 0 | 106
39029.3746 | 2617 | 0 | 106
39029.3768 | 2 | 0 | 106
106
39029.3575 | 1 | 0 | 107
39029.3597 | 951 | 0 | 107
39029.3618 | 2010 | 0 | 107
39029.364 | 2100 | 0 | 107
39029.3661 | 2245 | 0 | 107
39029.3682 | 2305 | 0 | 107
39029.3704 | 2024 | 0 | 107
39029.3725 | 2313 | 0 | 107
39029.3747 | 2567 | 0 | 107
39029.3768 | 2132 | 0 | 107
107
39029.3576 | 1 | 0 | 108
39029.3597 | 1 | 0 | 108
39029.3618 | 2234 | 0 | 108
39029.364 | 2394 | 0 | 108
39029.3661 | 2607 | 0 | 108
39029.3683 | 2369 | 0 | 108
39029.3704 | 2204 | 0 | 108
39029.3725 | 2603 | 0 | 108
39029.3747 | 2027 | 0 | 108
39029.3768 | 986 | 0 | 108
108
39029.3576 | 1 | 0 | 109
39029.3597 | 1160 | 0 | 109
39029.3619 | 2543 | 0 | 109
39029.364 | 2040 | 0 | 109
39029.3661 | 2294 | 0 | 109
39029.3683 | 2042 | 0 | 109
39029.3704 | 2440 | 0 | 109
39029.3725 | 2463 | 0 | 109
39029.3747 | 2577 | 0 | 109
39029.3768 | 2586 | 0 | 109
109
39029.3576 | 1 | 0 | 110
39029.3597 | 1 | 0 | 110
39029.3619 | 2551 | 0 | 110
39029.364 | 2064 | 0 | 110
39029.3661 | 2311 | 0 | 110
39029.3683 | 2282 | 0 | 110
39029.3704 | 2603 | 0 | 110
39029.3726 | 2114 | 0 | 110
39029.3747 | 2124 | 0 | 110
39029.3768 | 1955 | 0 | 110
110
39029.3576 | 1 | 0 | 111
39029.3597 | 1246 | 0 | 111
39029.3619 | 2203 | 0 | 111
39029.364 | 2242 | 0 | 111
39029.3662 | 2261 | 0 | 111
39029.3683 | 2196 | 0 | 111
39029.3704 | 2451 | 0 | 111
39029.3726 | 2393 | 0 | 111
39029.3747 | 2567 | 0 | 111
39029.3769 | 2642 | 0 | 111
111
39029.3576 | 1 | 0 | 112
39029.3598 | 1 | 0 | 112
39029.3619 | 2042 | 0 | 112
39029.364 | 2225 | 0 | 112
39029.3662 | 2616 | 0 | 112
39029.3683 | 2282 | 0 | 112
39029.3705 | 2519 | 0 | 112
39029.3726 | 2631 | 0 | 112
39029.3747 | 2221 | 0 | 112
39029.3769 | 2230 | 0 | 112
112
39029.3576 | 1 | 0 | 113
39029.3598 | 303 | 0 | 113
39029.3619 | 2304 | 0 | 113
39029.3641 | 2261 | 0 | 113
39029.3662 | 2386 | 0 | 113
39029.3683 | 2472 | 0 | 113
39029.3705 | 2023 | 0 | 113
39029.3726 | 2405 | 0 | 113
39029.3748 | 2341 | 0 | 113
39029.3769 | 1584 | 0 | 113
113
39029.3577 | 1 | 0 | 114
39029.3598 | 1 | 0 | 114
39029.3619 | 2422 | 0 | 114
39029.3641 | 2202 | 0 | 114
39029.3662 | 2580 | 0 | 114
39029.3684 | 2326 | 0 | 114
39029.3705 | 2598 | 0 | 114
39029.3726 | 2179 | 0 | 114
39029.3748 | 2237 | 0 | 114
39029.3769 | 1 | 0 | 114
114
39029.3577 | 1 | 0 | 115
39029.3598 | 1175 | 0 | 115
39029.362 | 2279 | 0 | 115
39029.3641 | 2064 | 0 | 115
39029.3662 | 2070 | 0 | 115
39029.3684 | 2120 | 0 | 115
39029.3705 | 2111 | 0 | 115
39029.3727 | 2606 | 0 | 115
39029.3748 | 2149 | 0 | 115
39029.3769 | 1708 | 0 | 115
115
39029.3577 | 1 | 0 | 116
39029.3598 | 1 | 0 | 116
39029.362 | 2232 | 0 | 116
39029.3641 | 2336 | 0 | 116
39029.3662 | 2586 | 0 | 116
39029.3684 | 2032 | 0 | 116
39029.3705 | 2597 | 0 | 116
39029.3727 | 2636 | 0 | 116
39029.3748 | 2117 | 0 | 116
39029.3769 | 1 | 0 | 116
116
39029.3577 | 1 | 0 | 117
39029.3598 | 1162 | 0 | 117
39029.362 | 2287 | 0 | 117
39029.3641 | 2468 | 0 | 117
39029.3663 | 2130 | 0 | 117
39029.3684 | 2562 | 0 | 117
39029.3705 | 2490 | 0 | 117
39029.3727 | 2236 | 0 | 117
39029.3748 | 1514 | 0 | 117
39029.377 | 1980 | 0 | 117
117
39029.3577 | 1 | 0 | 118
39029.3599 | 176 | 0 | 118
39029.362 | 2190 | 0 | 118
39029.3641 | 2268 | 0 | 118
39029.3663 | 2485 | 0 | 118
39029.3684 | 2613 | 0 | 118
39029.3706 | 2381 | 0 | 118
39029.3727 | 2536 | 0 | 118
39029.3748 | 2618 | 0 | 118
39029.377 | 1772 | 0 | 118
118
39029.3577 | 1 | 0 | 119
39029.3599 | 1189 | 0 | 119
39029.362 | 2265 | 0 | 119
39029.3642 | 2565 | 0 | 119
39029.3663 | 2561 | 0 | 119
39029.3684 | 2027 | 0 | 119
39029.3706 | 2082 | 0 | 119
39029.3727 | 2209 | 0 | 119
39029.3748 | 1766 | 0 | 119
39029.377 | 1748 | 0 | 119
119
39029.3578 | 1 | 0 | 120
39029.3599 | 1732 | 0 | 120
39029.362 | 2551 | 0 | 120
39029.3642 | 2625 | 0 | 120
39029.3663 | 2473 | 0 | 120
39029.3684 | 2280 | 0 | 120
39029.3706 | 2068 | 0 | 120
39029.3727 | 2492 | 0 | 120
39029.3749 | 2364 | 0 | 120
39029.377 | 1505 | 0 | 120
120
39029.3578 | 1 | 0 | 121
39029.3599 | 1 | 0 | 121
39029.362 | 2489 | 0 | 121
39029.3642 | 2453 | 0 | 121
39029.3663 | 2041 | 0 | 121
39029.3685 | 2575 | 0 | 121
39029.3706 | 2616 | 0 | 121
39029.3727 | 2155 | 0 | 121
39029.3749 | 2426 | 0 | 121
39029.377 | 950 | 1043 | 121
121
39029.3578 | 1 | 0 | 122
39029.3599 | 1 | 0 | 122
39029.3621 | 2116 | 0 | 122
39029.3642 | 2261 | 0 | 122
39029.3663 | 2513 | 0 | 122
39029.3685 | 2295 | 0 | 122
39029.3706 | 2042 | 0 | 122
39029.3728 | 2041 | 0 | 122
39029.3749 | 2198 | 0 | 122
39029.377 | 1003 | 977 | 122
122
39029.3578 | 1 | 0 | 123
39029.3599 | 1 | 0 | 123
39029.3621 | 2339 | 0 | 123
39029.3642 | 2435 | 0 | 123
39029.3664 | 2122 | 0 | 123
39029.3685 | 2598 | 0 | 123
39029.3706 | 2057 | 0 | 123
39029.3728 | 2635 | 0 | 123
39029.3749 | 2611 | 0 | 123
39029.377 | 2 | 0 | 123
123
39029.3578 | 1 | 0 | 124
39029.36 | 532 | 0 | 124
39029.3621 | 2243 | 0 | 124
39029.3642 | 2028 | 0 | 124
39029.3664 | 2161 | 0 | 124
39029.3685 | 2411 | 0 | 124
39029.3706 | 2564 | 0 | 124
39029.3728 | 2429 | 0 | 124
39029.3749 | 2596 | 0 | 124
39029.3771 | 1379 | 0 | 124
124
39029.3578 | 1 | 0 | 125
39029.36 | 1 | 0 | 125
39029.3621 | 2496 | 0 | 125
39029.3643 | 2389 | 0 | 125
39029.3664 | 2542 | 0 | 125
39029.3685 | 2131 | 0 | 125
39029.3707 | 2344 | 0 | 125
39029.3728 | 2631 | 0 | 125
39029.3749 | 2184 | 0 | 125
39029.3771 | 4 | 0 | 125
125
39029.3579 | 1 | 0 | 126
39029.36 | 2552 | 0 | 126
39029.3621 | 2018 | 0 | 126
39029.3643 | 2062 | 0 | 126
39029.3664 | 2405 | 0 | 126
39029.3685 | 2043 | 0 | 126
39029.3707 | 2223 | 0 | 126
39029.3728 | 2089 | 0 | 126
39029.375 | 2407 | 0 | 126
39029.3771 | 1943 | 0 | 126
126
39029.3579 | 1 | 0 | 127
39029.36 | 1 | 0 | 127
39029.3622 | 2439 | 0 | 127
39029.3643 | 2311 | 0 | 127
39029.3664 | 2596 | 0 | 127
39029.3686 | 2403 | 0 | 127
39029.3707 | 2581 | 0 | 127
39029.3728 | 2438 | 0 | 127
39029.375 | 2078 | 0 | 127
39029.3771 | 1 | 0 | 127
127
39029.3579 | 1 | 0 | 128
39029.36 | 885 | 0 | 128
39029.3622 | 2147 | 0 | 128
39029.3643 | 2634 | 0 | 128
39029.3664 | 2049 | 0 | 128
39029.3686 | 2618 | 0 | 128
39029.3707 | 2038 | 0 | 128
39029.3729 | 2461 | 0 | 128
39029.375 | 2313 | 0 | 128
39029.3771 | 2126 | 0 | 128
128
39029.3579 | 1 | 0 | 129
39029.36 | 1 | 0 | 129
39029.3622 | 1990 | 0 | 129
39029.3643 | 2024 | 0 | 129
39029.3665 | 2056 | 0 | 129
39029.3686 | 2128 | 0 | 129
39029.3707 | 2241 | 0 | 129
39029.3729 | 2385 | 0 | 129
39029.375 | 2580 | 0 | 129
39029.3772 | 1 | 0 | 129
129
39029.3579 | 1 | 0 | 130
39029.3601 | 2555 | 0 | 130
39029.3622 | 2167 | 0 | 130
39029.3643 | 2215 | 0 | 130
39029.3665 | 2046 | 0 | 130
39029.3686 | 2099 | 0 | 130
39029.3708 | 2449 | 0 | 130
39029.3729 | 2133 | 0 | 130
39029.375 | 2340 | 0 | 130
39029.3772 | 2118 | 0 | 130
130
39029.3579 | 1 | 0 | 131
39029.3601 | 2088 | 0 | 131
39029.3622 | 2223 | 0 | 131
39029.3644 | 2289 | 0 | 131
39029.3665 | 2091 | 0 | 131
39029.3686 | 2316 | 0 | 131
39029.3708 | 2580 | 0 | 131
39029.3729 | 2278 | 0 | 131
39029.375 | 2280 | 0 | 131
39029.3772 | 1269 | 1161 | 131
131
39029.358 | 1 | 0 | 132
39029.3601 | 2080 | 0 | 132
39029.3622 | 2620 | 0 | 132
39029.3644 | 2561 | 0 | 132
39029.3665 | 2215 | 0 | 132
39029.3686 | 2075 | 0 | 132
39029.3708 | 2620 | 0 | 132
39029.3729 | 2225 | 0 | 132
39029.3751 | 2148 | 0 | 132
39029.3772 | 1257 | 1108 | 132
132

## C6-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 156.6166 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39029.3575 | 1 | 0 | 39029.3575 | 1 | 0 |  | -11.5 | 140.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
39029.3596 | 1 | 0 | 39029.3596 | 1 | 0 |  | 173 | 325 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256438 | 256438 | 256437.9994
39029.3617 | 1950 | 0 | 39029.3617 | 2490 | 0 |  | 357.5 | 509.5 | 119.0476 | 0 | 152.0147 | 0 | 1.1905 | 0 | 1.5201 | 0 | 1.1905 | 1.5201 | 31.5579 | 3.0273 | 30.3675
39029.3639 | 2159 | 0 | 39029.3639 | 2253 | 0 |  | 542.5 | 694.5 | 131.8071 | 0 | 137.5458 | 0 | 1.3181 | 0 | 1.3755 | 0 | 1.3181 | 1.3755 | 18.8226 | 13.8651 | 17.5045
39029.366 | 2394 | 0 | 39029.366 | 2391 | 0 |  | 727.5 | 879.5 | 146.1538 | 0 | 145.9707 | 0 | 1.4615 | 0 | 1.4597 | 0 | 1.4615 | 1.4597 | 7.1587 | 7.2932 | 5.6972
39029.3681 | 2119 | 0 | 39029.3682 | 2114 | 0 |  | 912 | 1064 | 129.3651 | 0 | 129.0598 | 0 | 1.2937 | 0 | 1.2906 | 0 | 1.2937 | 1.2906 | 21.0656 | 21.3519 | 19.7719
39029.3703 | 2515 | 0 | 39029.3703 | 2069 | 0 |  | 1097 | 1249 | 153.5409 | 0 | 126.3126 | 0 | 1.5354 | 0 | 1.2631 | 0 | 1.5354 | 1.2631 | 2.0032 | 23.9913 | 0.46777
39029.3724 | 2425 | 0 | 39029.3724 | 2030 | 0 |  | 1281.5 | 1433.5 | 148.0464 | 0 | 123.9316 | 0 | 1.4805 | 0 | 1.2393 | 0 | 1.4805 | 1.2393 | 5.7889 | 26.3734 | 4.3084
39029.3746 | 2549 | 0 | 39029.3746 | 2504 | 0 |  | 1466.5 | 1618.5 | 155.6166 | 0 | 152.8694 | 0 | 1.5562 | 0 | 1.5287 | 0 | 1.5562 | 1.5287 | 0.6426 | 2.4513 | 0.91356
39029.3767 | 7 | 0 | 39029.3767 | 2213 | 0 |  | 1651.5 | 1803.5 | 0.42735 | 0 | 135.1038 | 0 | 0.0042735 | 0 | 1.351 | 0 | 0.0042735 | 1.351 | 36548.2857 | 15.9232 | 36548.2814

## C6-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.5006 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39029.3574 | 1 | 0 | 39029.3574 | 1 | 0 |  | -14.5 | 137.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39029.3596 | 1 | 0 | 39029.3596 | 1 | 0 |  | 170.5 | 322.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264438 | 264438 | 264437.9994
39029.3617 | 1866 | 0 | 39029.3617 | 2006 | 0 |  | 355 | 507 | 113.9194 | 0 | 122.4664 | 0 | 1.1392 | 0 | 1.2247 | 0 | 1.1392 | 1.2247 | 41.7674 | 31.8734 | 40.6282
39029.3638 | 2119 | 0 | 39029.3639 | 2629 | 0 |  | 540 | 692 | 129.3651 | 0 | 160.5006 | 0 | 1.2937 | 0 | 1.605 | 0 | 1.2937 | 1.605 | 24.841 | 0.62305 | 23.5473
39029.366 | 2565 | 0 | 39029.366 | 2136 | 0 |  | 724.5 | 876.5 | 156.5934 | 0 | 130.4029 | 0 | 1.5659 | 0 | 1.304 | 0 | 1.5659 | 1.304 | 3.1337 | 23.8474 | 1.5678
39029.3681 | 2467 | 0 | 39029.3681 | 2620 | 0 |  | 909.5 | 1061.5 | 150.6105 | 0 | 159.9512 | 0 | 1.5061 | 0 | 1.5995 | 0 | 1.5061 | 1.5995 | 7.2306 | 0.9687 | 5.7245
39029.3702 | 2416 | 0 | 39029.3703 | 2273 | 0 |  | 1094 | 1246 | 147.4969 | 0 | 138.7668 | 0 | 1.475 | 0 | 1.3877 | 0 | 1.475 | 1.3877 | 9.4942 | 16.3828 | 8.0192
39029.3724 | 2151 | 0 | 39029.3724 | 2419 | 0 |  | 1279 | 1431 | 131.3187 | 0 | 147.6801 | 0 | 1.3132 | 0 | 1.4768 | 0 | 1.3132 | 1.4768 | 22.9837 | 9.3584 | 21.6705
39029.3745 | 2092 | 0 | 39029.3745 | 2603 | 0 |  | 1463.5 | 1615.5 | 127.7167 | 0 | 158.9133 | 0 | 1.2772 | 0 | 1.5891 | 0 | 1.2772 | 1.5891 | 26.4522 | 1.6281 | 25.175
39029.3767 | 3 | 0 | 39029.3767 | 2184 | 0 |  | 1648.5 | 1800.5 | 0.18315 | 0 | 133.3333 | 0 | 0.0018315 | 0 | 1.3333 | 0 | 0.0018315 | 1.3333 | 88079.3333 | 21.1255 | 88079.3315

## C6-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 156.8608 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39029.3574 | 0 | 0 | 39029.3574 | 1 | 0 |  | -17.5 | 134.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 513776 | 256838 | 513775.9997
39029.3595 | 1 | 0 | 39029.3595 | 1 | 0 |  | 167.5 | 319.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256838 | 256838 | 256837.9994
39029.3617 | 1750 | 0 | 39029.3617 | 2030 | 0 |  | 352.5 | 504.5 | 106.8376 | 0 | 123.9316 | 0 | 1.0684 | 0 | 1.2393 | 0 | 1.0684 | 1.2393 | 46.8217 | 26.5704 | 45.7533
39029.3638 | 2282 | 0 | 39029.3638 | 2170 | 0 |  | 537 | 689 | 139.3162 | 0 | 132.4786 | 0 | 1.3932 | 0 | 1.3248 | 0 | 1.3932 | 1.3248 | 12.5933 | 18.4046 | 11.2002
39029.3659 | 2465 | 0 | 39029.366 | 2553 | 0 |  | 722 | 874 | 150.4884 | 0 | 155.8608 | 0 | 1.5049 | 0 | 1.5586 | 0 | 1.5049 | 1.5586 | 4.2345 | 0.6416 | 2.7296
39029.3681 | 2130 | 0 | 39029.3681 | 2317 | 0 |  | 906.5 | 1058.5 | 130.0366 | 0 | 141.453 | 0 | 1.3004 | 0 | 1.4145 | 0 | 1.3004 | 1.4145 | 20.6282 | 10.8925 | 19.3278
39029.3702 | 2172 | 0 | 39029.3702 | 2450 | 0 |  | 1091.5 | 1243.5 | 132.6007 | 0 | 149.5726 | 0 | 1.326 | 0 | 1.4957 | 0 | 1.326 | 1.4957 | 18.2956 | 4.8727 | 16.9696
39029.3723 | 2145 | 0 | 39029.3724 | 2075 | 0 |  | 1276 | 1428 | 130.9524 | 0 | 126.6789 | 0 | 1.3095 | 0 | 1.2668 | 0 | 1.3095 | 1.2668 | 19.7846 | 23.8255 | 18.4751
39029.3745 | 2434 | 0 | 39029.3745 | 2307 | 0 |  | 1461 | 1613 | 148.5958 | 0 | 140.8425 | 0 | 1.486 | 0 | 1.4084 | 0 | 1.486 | 1.4084 | 5.562 | 11.3732 | 4.0761
39029.3766 | 3 | 0 | 39029.3766 | 1656 | 0 |  | 1645.5 | 1797.5 | 0.18315 | 0 | 101.0989 | 0 | 0.0018315 | 0 | 1.011 | 0 | 0.0018315 | 1.011 | 85546 | 55.1558 | 85545.9982

## C6-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.0122 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39029.3573 | 0 | 0 | 39029.3574 | 1 | 0 |  | -20 | 132 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 527376 | 263638 | 527375.9997
39029.3595 | 1 | 0 | 39029.3595 | 1 | 0 |  | 164.5 | 316.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263638 | 263638 | 263637.9994
39029.3616 | 1723 | 0 | 39029.3616 | 2349 | 0 |  | 349.5 | 501.5 | 105.1893 | 0 | 143.4066 | 0 | 1.0519 | 0 | 1.4341 | 0 | 1.0519 | 1.4341 | 53.0691 | 12.2767 | 52.0172
39029.3638 | 2042 | 0 | 39029.3638 | 2114 | 0 |  | 534.5 | 686.5 | 124.6642 | 0 | 129.0598 | 0 | 1.2466 | 0 | 1.2906 | 0 | 1.2466 | 1.2906 | 29.1567 | 24.7578 | 27.9101
39029.3659 | 2267 | 0 | 39029.3659 | 2163 | 0 |  | 719 | 871 | 138.4005 | 0 | 132.0513 | 0 | 1.384 | 0 | 1.3205 | 0 | 1.384 | 1.3205 | 16.3379 | 21.9316 | 14.9539
39029.368 | 2547 | 0 | 39029.3681 | 2157 | 0 |  | 903.5 | 1055.5 | 155.4945 | 0 | 131.685 | 0 | 1.5549 | 0 | 1.3168 | 0 | 1.5549 | 1.3168 | 3.5485 | 22.2707 | 1.9935
39029.3702 | 2501 | 0 | 39029.3702 | 2621 | 0 |  | 1088.5 | 1240.5 | 152.6862 | 0 | 160.0122 | 0 | 1.5269 | 0 | 1.6001 | 0 | 1.5269 | 1.6001 | 5.453 | 0.62495 | 3.9262
39029.3723 | 2563 | 0 | 39029.3723 | 2337 | 0 |  | 1273.5 | 1425.5 | 156.4713 | 0 | 142.674 | 0 | 1.5647 | 0 | 1.4267 | 0 | 1.5647 | 1.4267 | 2.9021 | 12.8532 | 1.3374
39029.3745 | 2092 | 0 | 39029.3745 | 2537 | 0 |  | 1458 | 1610 | 127.7167 | 0 | 154.884 | 0 | 1.2772 | 0 | 1.5488 | 0 | 1.2772 | 1.5488 | 26.0698 | 3.9566 | 24.7926
39029.3766 | 2 | 0 | 39029.3766 | 1951 | 0 |  | 1643 | 1795 | 0.1221 | 0 | 119.1087 | 0 | 0.001221 | 0 | 1.1911 | 0 | 0.001221 | 1.1911 | 131769 | 35.1809 | 131768.9988

## C5-F12
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.768 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39029.3573 | 1 | 0 | 39029.3573 | 1 | 0 |  | -28.5 | 123.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263238 | 263238 | 263237.9994
39029.3594 | 1 | 0 | 39029.3594 | 1 | 0 |  | 156.5 | 308.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263238 | 263238 | 263237.9994
39029.3615 | 261 | 0 | 39029.3616 | 2146 | 0 |  | 341 | 493 | 15.9341 | 0 | 131.0134 | 0 | 0.15934 | 0 | 1.3101 | 0 | 0.15934 | 1.3101 | 908.9579 | 22.7111 | 908.7985
39029.3637 | 2242 | 0 | 39029.3637 | 2183 | 0 |  | 526 | 678 | 136.8742 | 0 | 133.2723 | 0 | 1.3687 | 0 | 1.3327 | 0 | 1.3687 | 1.3327 | 17.4567 | 20.6312 | 16.088
39029.3658 | 2438 | 0 | 39029.3658 | 2478 | 0 |  | 710.5 | 862.5 | 148.84 | 0 | 151.2821 | 0 | 1.4884 | 0 | 1.5128 | 0 | 1.4884 | 1.5128 | 8.0139 | 6.2704 | 6.5255
39029.368 | 2458 | 0 | 39029.368 | 2617 | 0 |  | 895.5 | 1047.5 | 150.0611 | 0 | 159.768 | 0 | 1.5006 | 0 | 1.5977 | 0 | 1.5006 | 1.5977 | 7.1351 | 0.62591 | 5.6345
39029.3701 | 2165 | 0 | 39029.3701 | 2227 | 0 |  | 1080 | 1232 | 132.1734 | 0 | 135.9585 | 0 | 1.3217 | 0 | 1.3596 | 0 | 1.3217 | 1.3596 | 21.6342 | 18.2479 | 20.3124
39029.3722 | 2326 | 0 | 39029.3722 | 2044 | 0 |  | 1265 | 1417 | 142.0024 | 0 | 124.7863 | 0 | 1.42 | 0 | 1.2479 | 0 | 1.42 | 1.2479 | 13.215 | 28.8346 | 11.7949
39029.3744 | 2341 | 0 | 39029.3744 | 2573 | 0 |  | 1449.5 | 1601.5 | 142.9182 | 0 | 157.0818 | 0 | 1.4292 | 0 | 1.5708 | 0 | 1.4292 | 1.5708 | 12.4895 | 2.3467 | 11.0604
39029.3765 | 3 | 0 | 39029.3765 | 2481 | 0 |  | 1634.5 | 1786.5 | 0.18315 | 0 | 151.4652 | 0 | 0.0018315 | 0 | 1.5147 | 0 | 0.0018315 | 1.5147 | 87679.3333 | 6.1419 | 87679.3315

## C5-F11
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.6838 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39029.3572 | 0 | 0 | 39029.3572 | 1 | 0 |  | -31.5 | 120.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 529576 | 264738 | 529575.9997
39029.3594 | 0 | 0 | 39029.3594 | 1 | 0 |  | 153.5 | 305.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 529576 | 264738 | 529575.9997
39029.3615 | 1951 | 0 | 39029.3615 | 2333 | 0 |  | 338.5 | 490.5 | 119.1087 | 0 | 142.4298 | 0 | 1.1911 | 0 | 1.4243 | 0 | 1.1911 | 1.4243 | 35.7447 | 13.5182 | 34.5537
39029.3636 | 2568 | 0 | 39029.3637 | 2595 | 0 |  | 523 | 675 | 156.7766 | 0 | 158.4249 | 0 | 1.5678 | 0 | 1.5842 | 0 | 1.5678 | 1.5842 | 3.1301 | 2.057 | 1.5623
39029.3658 | 2015 | 0 | 39029.3658 | 2153 | 0 |  | 707.5 | 859.5 | 123.0159 | 0 | 131.4408 | 0 | 1.2302 | 0 | 1.3144 | 0 | 1.2302 | 1.3144 | 31.4333 | 23.0088 | 30.2031
39029.3679 | 1996 | 0 | 39029.3679 | 2429 | 0 |  | 892.5 | 1044.5 | 121.8559 | 0 | 148.2906 | 0 | 1.2186 | 0 | 1.4829 | 0 | 1.2186 | 1.4829 | 32.6844 | 9.0317 | 31.4658
39029.3701 | 2589 | 0 | 39029.3701 | 2503 | 0 |  | 1077.5 | 1229.5 | 158.0586 | 0 | 152.8083 | 0 | 1.5806 | 0 | 1.5281 | 0 | 1.5806 | 1.5281 | 2.2935 | 5.8082 | 0.71296
39029.3722 | 2174 | 0 | 39029.3722 | 2632 | 0 |  | 1262 | 1414 | 132.7228 | 0 | 160.6838 | 0 | 1.3272 | 0 | 1.6068 | 0 | 1.3272 | 1.6068 | 21.8206 | 0.62234 | 20.4934
39029.3743 | 2216 | 0 | 39029.3744 | 2235 | 0 |  | 1447 | 1599 | 135.2869 | 0 | 136.4469 | 0 | 1.3529 | 0 | 1.3645 | 0 | 1.3529 | 1.3645 | 19.5117 | 18.4957 | 18.1589
39029.3765 | 3 | 0 | 39029.3765 | 2281 | 0 |  | 1631.5 | 1783.5 | 0.18315 | 0 | 139.2552 | 0 | 0.0018315 | 0 | 1.3926 | 0 | 0.0018315 | 1.3926 | 88179.3333 | 16.1061 | 88179.3315

## C5-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.6838 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39029.3572 | 1 | 0 | 39029.3572 | 1 | 0 |  | -34 | 118 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39029.3593 | 1 | 0 | 39029.3593 | 1 | 0 |  | 150.5 | 302.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264738 | 264738 | 264737.9994
39029.3615 | 1817 | 0 | 39029.3615 | 2430 | 0 |  | 335.5 | 487.5 | 110.928 | 0 | 148.3516 | 0 | 1.1093 | 0 | 1.4835 | 0 | 1.1093 | 1.4835 | 45.7556 | 8.9868 | 44.6464
39029.3636 | 2418 | 0 | 39029.3636 | 2339 | 0 |  | 520.5 | 672.5 | 147.619 | 0 | 142.7961 | 0 | 1.4762 | 0 | 1.428 | 0 | 1.4762 | 1.428 | 9.5277 | 13.227 | 8.0515
39029.3657 | 2203 | 0 | 39029.3658 | 2543 | 0 |  | 705 | 857 | 134.4933 | 0 | 155.2503 | 0 | 1.3449 | 0 | 1.5525 | 0 | 1.3449 | 1.5525 | 20.217 | 4.1439 | 18.872
39029.3679 | 2240 | 0 | 39029.3679 | 2080 | 0 |  | 889.5 | 1041.5 | 136.7521 | 0 | 126.9841 | 0 | 1.3675 | 0 | 1.2698 | 0 | 1.3675 | 1.2698 | 18.2312 | 27.326 | 16.8637
39029.37 | 2534 | 0 | 39029.37 | 2447 | 0 |  | 1074.5 | 1226.5 | 154.7009 | 0 | 149.3895 | 0 | 1.547 | 0 | 1.4939 | 0 | 1.547 | 1.4939 | 4.5138 | 8.2297 | 2.9668
39029.3722 | 2513 | 0 | 39029.3722 | 2098 | 0 |  | 1259.5 | 1411.5 | 153.4188 | 0 | 128.083 | 0 | 1.5342 | 0 | 1.2808 | 0 | 1.5342 | 1.2808 | 5.3872 | 26.2336 | 3.853
39029.3743 | 2214 | 0 | 39029.3743 | 2632 | 0 |  | 1444 | 1596 | 135.1648 | 0 | 160.6838 | 0 | 1.3516 | 0 | 1.6068 | 0 | 1.3516 | 1.6068 | 19.6197 | 0.62234 | 18.268
39029.3764 | 4 | 0 | 39029.3765 | 1596 | 0 |  | 1629 | 1781 | 0.2442 | 0 | 97.4359 | 0 | 0.002442 | 0 | 0.97436 | 0 | 0.002442 | 0.97436 | 66109.5 | 65.9386 | 66109.4976

## C5-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.8901 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39029.3572 | 1 | 0 | 39029.3572 | 1 | 0 |  | -37 | 115 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263438 | 263438 | 263437.9994
39029.3593 | 1 | 0 | 39029.3593 | 1 | 0 |  | 148 | 300 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263438 | 263438 | 263437.9994
39029.3614 | 1323 | 0 | 39029.3614 | 1349 | 0 |  | 332.5 | 484.5 | 80.7692 | 0 | 82.3565 | 0 | 0.80769 | 0 | 0.82357 | 0 | 0.80769 | 0.82357 | 99.1973 | 95.358 | 98.3896
39029.3636 | 2098 | 0 | 39029.3636 | 2619 | 0 |  | 517.5 | 669.5 | 128.083 | 0 | 159.8901 | 0 | 1.2808 | 0 | 1.5989 | 0 | 1.2808 | 1.5989 | 25.6139 | 0.62543 | 24.3331
39029.3657 | 2234 | 0 | 39029.3657 | 2447 | 0 |  | 702.5 | 854.5 | 136.3858 | 0 | 149.3895 | 0 | 1.3639 | 0 | 1.4939 | 0 | 1.3639 | 1.4939 | 17.9669 | 7.6984 | 16.603
39029.3678 | 2507 | 0 | 39029.3679 | 2542 | 0 |  | 887 | 1039 | 153.0525 | 0 | 155.1893 | 0 | 1.5305 | 0 | 1.5519 | 0 | 1.5305 | 1.5519 | 5.1209 | 3.6735 | 3.5903
39029.37 | 2560 | 0 | 39029.37 | 2487 | 0 |  | 1071.5 | 1223.5 | 156.2882 | 0 | 151.8315 | 0 | 1.5629 | 0 | 1.5183 | 0 | 1.5629 | 1.5183 | 2.9445 | 5.9662 | 1.3816
39029.3721 | 2082 | 0 | 39029.3721 | 2226 | 0 |  | 1256.5 | 1408.5 | 127.1062 | 0 | 135.8974 | 0 | 1.2711 | 0 | 1.359 | 0 | 1.2711 | 1.359 | 26.5793 | 18.3908 | 25.3082
39029.3743 | 2052 | 0 | 39029.3743 | 2104 | 0 |  | 1441.5 | 1593.5 | 125.2747 | 0 | 128.4493 | 0 | 1.2527 | 0 | 1.2845 | 0 | 1.2527 | 1.2845 | 28.4298 | 25.2557 | 27.1771
39029.3764 | 3 | 0 | 39029.3764 | 1876 | 0 |  | 1626 | 1778 | 0.18315 | 0 | 114.5299 | 0 | 0.0018315 | 0 | 1.1453 | 0 | 0.0018315 | 1.1453 | 87746 | 40.4787 | 87745.9982

## C5-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.8755 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39029.3571 | 1 | 0 | 39029.3571 | 1 | 0 |  | -45.5 | 106.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260138 | 260138 | 260137.9994
39029.3592 | 1 | 0 | 39029.3592 | 0 | 0 |  | 139.5 | 291.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 260138 | 520376 | 260137.9994
39029.3613 | 1063 | 217 | 39029.3614 | 2 | 0 |  | 324 | 476 | 64.8962 | 13.2479 | 0.1221 | 0 | 0.64896 | 0.13248 | 0.001221 | 0 | 0.51648 | 0.001221 | 181.9957 | 130019 | 608.9234
39029.3635 | 2129 | 0 | 39029.3635 | 1974 | 0 |  | 509 | 661 | 129.9756 | 0 | 120.5128 | 0 | 1.2998 | 0 | 1.2051 | 0 | 1.2998 | 1.2051 | 22.2349 | 31.8328 | 20.9351
39029.3656 | 2381 | 0 | 39029.3656 | 2044 | 0 |  | 694 | 846 | 145.3602 | 0 | 124.7863 | 0 | 1.4536 | 0 | 1.2479 | 0 | 1.4536 | 1.2479 | 9.2978 | 27.318 | 7.8442
39029.3678 | 2425 | 0 | 39029.3678 | 2586 | 0 |  | 878.5 | 1030.5 | 148.0464 | 0 | 157.8755 | 0 | 1.4805 | 0 | 1.5788 | 0 | 1.4805 | 1.5788 | 7.3146 | 0.63341 | 5.8342
39029.3699 | 2089 | 0 | 39029.3699 | 2215 | 0 |  | 1063.5 | 1215.5 | 127.5336 | 0 | 135.2259 | 0 | 1.2753 | 0 | 1.3523 | 0 | 1.2753 | 1.3523 | 24.5754 | 17.4889 | 23.3001
39029.372 | 2215 | 0 | 39029.372 | 2179 | 0 |  | 1248 | 1400 | 135.2259 | 0 | 133.0281 | 0 | 1.3523 | 0 | 1.3303 | 0 | 1.3523 | 1.3303 | 17.4889 | 19.43 | 16.1367
39029.3742 | 1916 | 49 | 39029.3742 | 1922 | 55 |  | 1433 | 1585 | 116.9719 | 2.9915 | 117.3382 | 3.3578 | 1.1697 | 0.029915 | 1.1734 | 0.033578 | 1.1398 | 1.1398 | 39.3883 | 39.3883 | 367.5729
39029.3763 | 1218 | 1144 | 39029.3763 | 1145 | 1058 |  | 1617.5 | 1769.5 | 74.359 | 69.8413 | 69.9023 | 64.591 | 0.74359 | 0.69841 | 0.69902 | 0.64591 | 0.045177 | 0.053114 | 9704.3049 | 1915.1453 | 19.9695

## B4-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 156.6777 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39029.357 | 1 | 0 | 39029.357 | 1 | 0 |  | -53.5 | 98.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
39029.3591 | 1 | 0 | 39029.3591 | 1 | 0 |  | 131 | 283 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 256538 | 256538 | 256537.9994
39029.3612 | 53 | 0 | 39029.3613 | 2095 | 0 |  | 316 | 468 | 3.2357 | 0 | 127.8999 | 0 | 0.032357 | 0 | 1.279 | 0 | 0.032357 | 1.279 | 4742.2264 | 22.5002 | 4742.1941
39029.3634 | 2529 | 0 | 39029.3634 | 2476 | 0 |  | 500.5 | 652.5 | 154.3956 | 0 | 151.16 | 0 | 1.544 | 0 | 1.5116 | 0 | 1.544 | 1.5116 | 1.4781 | 3.6502 | 0.065901
39029.3655 | 2260 | 0 | 39029.3655 | 2081 | 0 |  | 685.5 | 837.5 | 137.9731 | 0 | 127.0452 | 0 | 1.3797 | 0 | 1.2705 | 0 | 1.3797 | 1.2705 | 13.5566 | 23.3244 | 12.1769
39029.3677 | 2396 | 0 | 39029.3677 | 2550 | 0 |  | 870.5 | 1022.5 | 146.2759 | 0 | 155.6777 | 0 | 1.4628 | 0 | 1.5568 | 0 | 1.4628 | 1.5568 | 7.111 | 0.64235 | 5.6483
39029.3698 | 2432 | 0 | 39029.3698 | 2164 | 0 |  | 1055 | 1207 | 148.4737 | 0 | 132.1123 | 0 | 1.4847 | 0 | 1.3211 | 0 | 1.4847 | 1.3211 | 5.5255 | 18.5943 | 4.0408
39029.3719 | 2052 | 0 | 39029.3719 | 2439 | 0 |  | 1239.5 | 1391.5 | 125.2747 | 0 | 148.9011 | 0 | 1.2527 | 0 | 1.489 | 0 | 1.2527 | 1.489 | 25.0673 | 5.2226 | 23.8145
39029.3741 | 1744 | 0 | 39029.3741 | 2434 | 0 |  | 1424.5 | 1576.5 | 106.4713 | 0 | 148.5958 | 0 | 1.0647 | 0 | 1.486 | 0 | 1.0647 | 1.486 | 47.1548 | 5.4388 | 46.0901
39029.3762 | 204 | 0 | 39029.3762 | 1558 | 0 |  | 1609.5 | 1761.5 | 12.4542 | 0 | 95.116 | 0 | 0.12454 | 0 | 0.95116 | 0 | 0.12454 | 0.95116 | 1158.0294 | 64.7227 | 1157.9049

## B4-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.1954 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39029.3569 | 1 | 0 | 39029.3569 | 0 | 0 |  | -56.5 | 95.5 | 0.06105 | 0 | 0.030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0 | 0.0006105 | 0.00030525 | 263938 | 527976 | 263937.9994
39029.3591 | 1 | 0 | 39029.3591 | 1 | 0 |  | 128.5 | 280.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263938 | 263938 | 263937.9994
39029.3612 | 6 | 0 | 39029.3612 | 1964 | 0 |  | 313 | 465 | 0.3663 | 0 | 119.9023 | 0 | 0.003663 | 0 | 1.199 | 0 | 0.003663 | 1.199 | 43906.3333 | 34.4389 | 43906.3297
39029.3633 | 2143 | 0 | 39029.3634 | 2574 | 0 |  | 498 | 650 | 130.8303 | 0 | 157.1429 | 0 | 1.3083 | 0 | 1.5714 | 0 | 1.3083 | 1.5714 | 23.2095 | 2.5789 | 21.9012
39029.3655 | 2591 | 0 | 39029.3655 | 2410 | 0 |  | 682.5 | 834.5 | 158.1807 | 0 | 147.1306 | 0 | 1.5818 | 0 | 1.4713 | 0 | 1.5818 | 1.4713 | 1.9058 | 9.5593 | 0.32402
39029.3676 | 2434 | 0 | 39029.3676 | 2291 | 0 |  | 867.5 | 1019.5 | 148.5958 | 0 | 139.8657 | 0 | 1.486 | 0 | 1.3987 | 0 | 1.486 | 1.3987 | 8.479 | 15.2501 | 6.9931
39029.3698 | 2456 | 0 | 39029.3698 | 2624 | 0 |  | 1052 | 1204 | 149.9389 | 0 | 160.1954 | 0 | 1.4994 | 0 | 1.602 | 0 | 1.4994 | 1.602 | 7.5073 | 0.62424 | 6.0079
39029.3719 | 2440 | 0 | 39029.3719 | 2102 | 0 |  | 1237 | 1389 | 148.9621 | 0 | 128.3272 | 0 | 1.4896 | 0 | 1.2833 | 0 | 1.4896 | 1.2833 | 8.2123 | 25.6127 | 6.7227
39029.374 | 2016 | 0 | 39029.3741 | 2075 | 0 |  | 1421.5 | 1573.5 | 123.0769 | 0 | 126.6789 | 0 | 1.2308 | 0 | 1.2668 | 0 | 1.2308 | 1.2668 | 30.9712 | 27.2472 | 29.7405
39029.3762 | 234 | 0 | 39029.3762 | 1594 | 0 |  | 1606.5 | 1758.5 | 14.2857 | 0 | 97.3138 | 0 | 0.14286 | 0 | 0.97314 | 0 | 0.14286 | 0.97314 | 1028.3675 | 65.6449 | 1028.2247

## B4-D8
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 155.1514 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39029.3569 | 0 | 0 | 39029.3569 | 1 | 0 |  | -59.5 | 92.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 508176 | 254038 | 508175.9997
39029.359 | 1 | 0 | 39029.3591 | 1 | 0 |  | 125.5 | 277.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 254038 | 254038 | 254037.9994
39029.3612 | 3 | 0 | 39029.3612 | 2048 | 0 |  | 310.5 | 462.5 | 0.18315 | 0 | 125.0305 | 0 | 0.0018315 | 0 | 1.2503 | 0 | 0.0018315 | 1.2503 | 84612.6667 | 24.0908 | 84612.6648
39029.3633 | 2409 | 0 | 39029.3633 | 2080 | 0 |  | 495 | 647 | 147.0696 | 0 | 126.9841 | 0 | 1.4707 | 0 | 1.2698 | 0 | 1.4707 | 1.2698 | 5.4952 | 22.1817 | 4.0245
39029.3655 | 2119 | 0 | 39029.3655 | 2332 | 0 |  | 679.5 | 831.5 | 129.3651 | 0 | 142.3687 | 0 | 1.2937 | 0 | 1.4237 | 0 | 1.2937 | 1.4237 | 19.933 | 8.9786 | 18.6393
39029.3676 | 2373 | 0 | 39029.3676 | 2297 | 0 |  | 864.5 | 1016.5 | 144.8718 | 0 | 140.232 | 0 | 1.4487 | 0 | 1.4023 | 0 | 1.4487 | 1.4023 | 7.0957 | 10.6391 | 5.6469
39029.3697 | 2525 | 0 | 39029.3697 | 2224 | 0 |  | 1049.5 | 1201.5 | 154.1514 | 0 | 135.7753 | 0 | 1.5415 | 0 | 1.3578 | 0 | 1.5415 | 1.3578 | 0.64871 | 14.2707 | 0.8928
39029.3719 | 2379 | 0 | 39029.3719 | 2190 | 0 |  | 1234 | 1386 | 145.2381 | 0 | 133.6996 | 0 | 1.4524 | 0 | 1.337 | 0 | 1.4524 | 1.337 | 6.8256 | 16.0447 | 5.3732
39029.374 | 1860 | 0 | 39029.374 | 2267 | 0 |  | 1419 | 1571 | 113.5531 | 0 | 138.4005 | 0 | 1.1355 | 0 | 1.384 | 0 | 1.1355 | 1.384 | 36.6333 | 12.1032 | 35.4978
39029.3761 | 307 | 0 | 39029.3762 | 1870 | 0 |  | 1603.5 | 1755.5 | 18.7424 | 0 | 114.1636 | 0 | 0.18742 | 0 | 1.1416 | 0 | 0.18742 | 1.1416 | 727.8111 | 35.9027 | 727.6237

## B4-D7
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.3785 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39029.3569 | 1 | 0 | 39029.3569 | 1 | 0 |  | -62 | 90 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39029.359 | 1 | 0 | 39029.359 | 1 | 0 |  | 122.5 | 274.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 264238 | 264238 | 264237.9994
39029.3611 | 1 | 0 | 39029.3612 | 2308 | 0 |  | 307.5 | 459.5 | 0.06105 | 0 | 140.9035 | 0 | 0.0006105 | 0 | 1.409 | 0 | 0.0006105 | 1.409 | 264238 | 14.5312 | 264237.9994
39029.3633 | 2251 | 0 | 39029.3633 | 2079 | 0 |  | 492.5 | 644.5 | 137.4237 | 0 | 126.9231 | 0 | 1.3742 | 0 | 1.2692 | 0 | 1.3742 | 1.2692 | 17.4314 | 27.1467 | 16.0571
39029.3654 | 2066 | 0 | 39029.3654 | 2535 | 0 |  | 677 | 829 | 126.1294 | 0 | 154.7619 | 0 | 1.2613 | 0 | 1.5476 | 0 | 1.2613 | 1.5476 | 27.9468 | 4.2753 | 26.6855
39029.3676 | 2454 | 0 | 39029.3676 | 2585 | 0 |  | 862 | 1014 | 149.8168 | 0 | 157.8144 | 0 | 1.4982 | 0 | 1.5781 | 0 | 1.4982 | 1.5781 | 7.7172 | 2.2584 | 6.219
39029.3697 | 2341 | 0 | 39029.3697 | 2627 | 0 |  | 1046.5 | 1198.5 | 142.9182 | 0 | 160.3785 | 0 | 1.4292 | 0 | 1.6038 | 0 | 1.4292 | 1.6038 | 12.9167 | 0.62352 | 11.4875
39029.3718 | 2372 | 0 | 39029.3719 | 2024 | 0 |  | 1231.5 | 1383.5 | 144.8107 | 0 | 123.5653 | 0 | 1.4481 | 0 | 1.2357 | 0 | 1.4481 | 1.2357 | 11.441 | 30.6018 | 9.9929
39029.374 | 1718 | 0 | 39029.374 | 2272 | 0 |  | 1416 | 1568 | 104.884 | 0 | 138.7057 | 0 | 1.0488 | 0 | 1.3871 | 0 | 1.0488 | 1.3871 | 53.8638 | 16.346 | 52.815
39029.3761 | 157 | 0 | 39029.3761 | 1505 | 0 |  | 1601 | 1753 | 9.5849 | 0 | 91.8803 | 0 | 0.095849 | 0 | 0.9188 | 0 | 0.095849 | 0.9188 | 1583.6815 | 75.6399 | 1583.5857

## B4-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 154.5409 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39029.3568 | 0 | 0 | 39029.3569 | 1 | 0 |  | -64.5 | 87.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 506176 | 253038 | 506175.9997
39029.359 | 1 | 0 | 39029.359 | 1 | 0 |  | 120 | 272 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 253038 | 253038 | 253037.9994
39029.3611 | 1 | 0 | 39029.3611 | 34 | 0 |  | 304.5 | 456.5 | 0.06105 | 0 | 2.0757 | 0 | 0.0006105 | 0 | 0.020757 | 0 | 0.0006105 | 0.020757 | 253038 | 7345.2353 | 253037.9994
39029.3633 | 2509 | 0 | 39029.3633 | 2039 | 0 |  | 489.5 | 641.5 | 153.1746 | 0 | 124.4811 | 0 | 1.5317 | 0 | 1.2448 | 0 | 1.5317 | 1.2448 | 0.89199 | 24.1481 | 0.63976
39029.3654 | 2322 | 0 | 39029.3654 | 2443 | 0 |  | 674.5 | 826.5 | 141.7582 | 0 | 149.1453 | 0 | 1.4176 | 0 | 1.4915 | 0 | 1.4176 | 1.4915 | 9.0172 | 3.6177 | 7.5996
39029.3675 | 2403 | 0 | 39029.3675 | 2122 | 0 |  | 859 | 1011 | 146.7033 | 0 | 129.5482 | 0 | 1.467 | 0 | 1.2955 | 0 | 1.467 | 1.2955 | 5.3425 | 19.2922 | 3.8755
39029.3697 | 2027 | 0 | 39029.3697 | 2498 | 0 |  | 1043.5 | 1195.5 | 123.7485 | 0 | 152.5031 | 0 | 1.2375 | 0 | 1.525 | 0 | 1.2375 | 1.525 | 24.8831 | 1.3363 | 23.6456
39029.3718 | 2515 | 0 | 39029.3718 | 2403 | 0 |  | 1228.5 | 1380.5 | 153.5409 | 0 | 146.7033 | 0 | 1.5354 | 0 | 1.467 | 0 | 1.5354 | 1.467 | 0.65129 | 5.3425 | 0.88412
39029.3739 | 1960 | 0 |  | 1852 | 0 |  | 1413 | 1565 | 119.6581 | 0 | 113.0647 | 0 | 1.1966 | 0 | 1.1306 | 0 | 1.1966 | 1.1306 | 29.152 | 36.6836 | 27.9555
39029.3761 | 51 | 1 | 39029.3761 | 21 | 0 |  | 1598 | 1750 | 3.1136 | 0.06105 | 1.2821 | 0 | 0.031136 | 0.0006105 | 0.012821 | 0 | 0.030525 | 0.012821 | 4961.5901 | 11954.1905 | 245881.1385

## B4-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 157.8987 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39029.3568 | 1 | 0 | 39029.3568 | 1 | 0 |  | -67.5 | 84.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39029.3589 | 1 | 0 | 39029.359 | 1 | 0 |  | 117 | 269 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258538 | 258538 | 258537.9994
39029.3611 | 1 | 0 | 39029.3611 | 20 | 0 |  | 302 | 454 | 0.06105 | 0 | 1.221 | 0 | 0.0006105 | 0 | 0.01221 | 0 | 0.0006105 | 0.01221 | 258538 | 12831.9 | 258537.9994
39029.3632 | 2227 | 0 | 39029.3632 | 2027 | 0 |  | 486.5 | 638.5 | 135.9585 | 0 | 123.7485 | 0 | 1.3596 | 0 | 1.2375 | 0 | 1.3596 | 1.2375 | 16.1374 | 27.5964 | 14.7778
39029.3654 | 2058 | 0 | 39029.3654 | 2136 | 0 |  | 671.5 | 823.5 | 125.641 | 0 | 130.4029 | 0 | 1.2564 | 0 | 1.304 | 0 | 1.2564 | 1.304 | 25.6744 | 21.0852 | 24.418
39029.3675 | 2053 | 0 | 39029.3675 | 2570 | 0 |  | 856.5 | 1008.5 | 125.3358 | 0 | 156.8987 | 0 | 1.2534 | 0 | 1.569 | 0 | 1.2534 | 1.569 | 25.9805 | 0.63735 | 24.7272
39029.3696 | 2440 | 0 | 39029.3697 | 2179 | 0 |  | 1041 | 1193 | 148.9621 | 0 | 133.0281 | 0 | 1.4896 | 0 | 1.3303 | 0 | 1.4896 | 1.3303 | 5.9992 | 18.6957 | 4.5096
39029.3718 | 2076 | 0 | 39029.3718 | 2513 | 0 |  | 1225.5 | 1377.5 | 126.7399 | 0 | 153.4188 | 0 | 1.2674 | 0 | 1.5342 | 0 | 1.2674 | 1.5342 | 24.5848 | 2.92 | 23.3174
39029.3739 | 1962 | 0 | 39029.3739 | 2206 | 0 |  | 1410.5 | 1562.5 | 119.7802 | 0 | 134.6764 | 0 | 1.1978 | 0 | 1.3468 | 0 | 1.1978 | 1.3468 | 31.8236 | 17.243 | 30.6258
39029.3761 | 109 | 34 | 39029.3761 | 133 | 28 |  | 1595.5 | 1747.5 | 6.6545 | 2.0757 | 8.1197 | 1.7094 | 0.066545 | 0.020757 | 0.081197 | 0.017094 | 0.045788 | 0.064103 | 3368.0013 | 2355.2 | 6893.7101

## B3-E10
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.3871 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39029.3567 | 0 | 0 | 39029.3567 | 1 | 0 |  | -76 | 76 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 518776 | 259338 | 518775.9997
39029.3588 | 0 | 0 | 39029.3589 | 1 | 0 |  | 108.5 | 260.5 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 518776 | 259338 | 518775.9997
39029.361 | 2 | 0 | 39029.361 | 2230 | 0 |  | 293.5 | 445.5 | 0.1221 | 0 | 136.1416 | 0 | 0.001221 | 0 | 1.3614 | 0 | 0.001221 | 1.3614 | 129619 | 16.3399 | 129618.9988
39029.3631 | 2528 | 0 | 39029.3631 | 2458 | 0 |  | 478.5 | 630.5 | 154.3346 | 0 | 150.0611 | 0 | 1.5433 | 0 | 1.5006 | 0 | 1.5433 | 1.5006 | 2.6258 | 5.5484 | 1.0824
39029.3653 | 2117 | 0 | 39029.3653 | 2145 | 0 |  | 663 | 815 | 129.243 | 0 | 130.9524 | 0 | 1.2924 | 0 | 1.3095 | 0 | 1.2924 | 1.3095 | 22.5498 | 20.9501 | 21.2574
39029.3674 | 2253 | 0 | 39029.3674 | 2035 | 0 |  | 847.5 | 999.5 | 137.5458 | 0 | 124.2369 | 0 | 1.3755 | 0 | 1.2424 | 0 | 1.3755 | 1.2424 | 15.1522 | 27.488 | 13.7768
39029.3695 | 2338 | 0 | 39029.3695 | 2059 | 0 |  | 1032.5 | 1184.5 | 142.735 | 0 | 125.7021 | 0 | 1.4274 | 0 | 1.257 | 0 | 1.4274 | 1.257 | 10.9658 | 26.0019 | 9.5384
39029.3717 | 2578 | 0 | 39029.3717 | 2207 | 0 |  | 1217.5 | 1369.5 | 157.3871 | 0 | 134.7375 | 0 | 1.5739 | 0 | 1.3474 | 0 | 1.5739 | 1.3474 | 0.63538 | 17.5523 | 0.93849
39029.3738 | 2275 | 0 | 39029.3738 | 2106 | 0 |  | 1402 | 1554 | 138.8889 | 0 | 128.5714 | 0 | 1.3889 | 0 | 1.2857 | 0 | 1.3889 | 1.2857 | 14.0387 | 23.1899 | 12.6498
39029.3759 | 386 | 14 | 39029.376 | 1778 | 0 |  | 1587 | 1739 | 23.5653 | 0.8547 | 108.547 | 0 | 0.23565 | 0.008547 | 1.0855 | 0 | 0.22711 | 1.0855 | 646.653 | 45.9156 | 4932.2215

## B3-E9
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39029.3567 | 1 | 0 | 39029.3567 | 1 | 0 |  | -79 | 73 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39029.3588 | 0 | 0 | 39029.3588 | 1 | 0 |  | 106 | 258 | 0.030525 | 0 | 0.06105 | 0 | 0.00030525 | 0 | 0.0006105 | 0 | 0.00030525 | 0.0006105 | 517776 | 258838 | 517775.9997
39029.3609 | 2 | 0 | 39029.361 | 1939 | 0 |  | 290.5 | 442.5 | 0.1221 | 0 | 118.3761 | 0 | 0.001221 | 0 | 1.1838 | 0 | 0.001221 | 1.1838 | 129369 | 33.542 | 129368.9988
39029.3631 | 1961 | 0 | 39029.3631 | 2324 | 0 |  | 475.5 | 627.5 | 119.7192 | 0 | 141.8803 | 0 | 1.1972 | 0 | 1.4188 | 0 | 1.1972 | 1.4188 | 32.0439 | 11.4191 | 30.8467
39029.3652 | 2552 | 0 | 39029.3652 | 2053 | 0 |  | 660.5 | 812.5 | 155.7998 | 0 | 125.3358 | 0 | 1.558 | 0 | 1.2534 | 0 | 1.558 | 1.2534 | 1.4647 | 26.1266 | 0.093264
39029.3674 | 2538 | 0 | 39029.3674 | 2281 | 0 |  | 845 | 997 | 154.9451 | 0 | 139.2552 | 0 | 1.5495 | 0 | 1.3926 | 0 | 1.5495 | 1.3926 | 2.0244 | 13.5195 | 0.47498
39029.3695 | 2006 | 0 | 39029.3695 | 2141 | 0 |  | 1029.5 | 1181.5 | 122.4664 | 0 | 130.7082 | 0 | 1.2247 | 0 | 1.3071 | 0 | 1.2247 | 1.3071 | 29.0818 | 20.9426 | 27.8571
39029.3716 | 1993 | 0 | 39029.3717 | 2573 | 0 |  | 1214.5 | 1366.5 | 121.6728 | 0 | 157.0818 | 0 | 1.2167 | 0 | 1.5708 | 0 | 1.2167 | 1.5708 | 29.9237 | 0.63661 | 28.707
39029.3738 | 2316 | 0 | 39029.3738 | 2157 | 0 |  | 1399.5 | 1551.5 | 141.3919 | 0 | 131.685 | 0 | 1.4139 | 0 | 1.3168 | 0 | 1.4139 | 1.3168 | 11.804 | 20.0454 | 10.3901
39029.3759 | 333 | 0 | 39029.3759 | 1987 | 0 |  | 1584 | 1736 | 20.3297 | 0 | 121.3065 | 0 | 0.2033 | 0 | 1.2131 | 0 | 0.2033 | 1.2131 | 677.5916 | 30.3161 | 677.3883

## B3-D8
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 161.1954 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39029.3566 | 1 | 0 | 39029.3567 | 1 | 0 |  | -81.5 | 70.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263938 | 263938 | 263937.9994
39029.3588 | 1 | 0 | 39029.3588 | 1 | 0 |  | 103 | 255 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 263938 | 263938 | 263937.9994
39029.3609 | 4 | 0 | 39029.3609 | 2024 | 0 |  | 288 | 440 | 0.2442 | 0 | 123.5653 | 0 | 0.002442 | 0 | 1.2357 | 0 | 0.002442 | 1.2357 | 65909.5 | 30.4536 | 65909.4976
39029.3631 | 2250 | 0 | 39029.3631 | 2624 | 0 |  | 472.5 | 624.5 | 137.3626 | 0 | 160.1954 | 0 | 1.3736 | 0 | 1.602 | 0 | 1.3736 | 1.602 | 17.3502 | 0.62424 | 15.9766
39029.3652 | 2066 | 0 | 39029.3652 | 2342 | 0 |  | 657.5 | 809.5 | 126.1294 | 0 | 142.9792 | 0 | 1.2613 | 0 | 1.4298 | 0 | 1.2613 | 1.4298 | 27.8015 | 12.7404 | 26.5403
39029.3673 | 2441 | 0 | 39029.3673 | 2611 | 0 |  | 842 | 994 | 149.0232 | 0 | 159.4017 | 0 | 1.4902 | 0 | 1.594 | 0 | 1.4902 | 1.594 | 8.168 | 1.1252 | 6.6777
39029.3695 | 2175 | 0 | 39029.3695 | 2542 | 0 |  | 1027 | 1179 | 132.7839 | 0 | 155.1893 | 0 | 1.3278 | 0 | 1.5519 | 0 | 1.3278 | 1.5519 | 21.3968 | 3.8702 | 20.0689
39029.3716 | 2338 | 0 | 39029.3716 | 2131 | 0 |  | 1211.5 | 1363.5 | 142.735 | 0 | 130.0977 | 0 | 1.4274 | 0 | 1.301 | 0 | 1.4274 | 1.301 | 12.9333 | 23.9033 | 11.5059
39029.3737 | 1910 | 0 | 39029.3738 | 2078 | 0 |  | 1396.5 | 1548.5 | 116.6056 | 0 | 126.862 | 0 | 1.1661 | 0 | 1.2686 | 0 | 1.1661 | 1.2686 | 38.2398 | 27.0635 | 37.0737
39029.3759 | 291 | 2 | 39029.3759 | 1621 | 0 |  | 1581.5 | 1733.5 | 17.7656 | 0.1221 | 98.9621 | 0 | 0.17766 | 0.001221 | 0.98962 | 0 | 0.17643 | 0.98962 | 821.9799 | 62.8859 | 45313.0274

## B3-D7
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 157.5934 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39029.3566 | 1 | 0 | 39029.3566 | 1 | 0 |  | -84.5 | 67.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39029.3587 | 1 | 0 | 39029.3588 | 1 | 0 |  | 100.5 | 252.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258038 | 258038 | 258037.9994
39029.3609 | 2 | 0 | 39029.3609 | 2466 | 0 |  | 285 | 437 | 0.1221 | 0 | 150.5495 | 0 | 0.001221 | 0 | 1.5055 | 0 | 0.001221 | 1.5055 | 128969 | 4.6788 | 128968.9988
39029.363 | 1919 | 0 | 39029.363 | 2420 | 0 |  | 469.5 | 621.5 | 117.1551 | 0 | 147.7411 | 0 | 1.1716 | 0 | 1.4774 | 0 | 1.1716 | 1.4774 | 34.5169 | 6.6686 | 33.3454
39029.3652 | 2282 | 0 | 39029.3652 | 2275 | 0 |  | 654.5 | 806.5 | 139.3162 | 0 | 138.8889 | 0 | 1.3932 | 0 | 1.3889 | 0 | 1.3932 | 1.3889 | 13.1192 | 13.4673 | 11.726
39029.3673 | 2168 | 0 | 39029.3673 | 2565 | 0 |  | 839.5 | 991.5 | 132.3565 | 0 | 156.5934 | 0 | 1.3236 | 0 | 1.5659 | 0 | 1.3236 | 1.5659 | 19.0673 | 0.6386 | 17.7438
39029.3694 | 2200 | 0 | 39029.3695 | 2436 | 0 |  | 1024 | 1176 | 134.3101 | 0 | 148.7179 | 0 | 1.3431 | 0 | 1.4872 | 0 | 1.3431 | 1.4872 | 17.3355 | 5.968 | 15.9924
39029.3716 | 2085 | 0 | 39029.3716 | 2355 | 0 |  | 1209 | 1361 | 127.2894 | 0 | 143.7729 | 0 | 1.2729 | 0 | 1.4377 | 0 | 1.2729 | 1.4377 | 23.8072 | 9.6127 | 22.5343
39029.3737 | 2243 | 0 | 39029.3737 | 2095 | 0 |  | 1393.5 | 1545.5 | 136.9353 | 0 | 127.8999 | 0 | 1.3694 | 0 | 1.279 | 0 | 1.3694 | 1.279 | 15.086 | 23.2162 | 13.7167
39029.3759 | 334 | 0 | 39029.3759 | 1712 | 0 |  | 1578.5 | 1730.5 | 20.3907 | 0 | 104.5177 | 0 | 0.20391 | 0 | 1.0452 | 0 | 0.20391 | 1.0452 | 672.8683 | 50.7815 | 672.6644

## B3-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 157.9597 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39029.3566 | 1 | 0 | 39029.3566 | 1 | 0 |  | -87.5 | 64.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39029.3587 | 1 | 0 | 39029.3587 | 1 | 0 |  | 97.5 | 249.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258638 | 258638 | 258637.9994
39029.3609 | 3 | 0 | 39029.3609 | 1 | 0 |  | 282.5 | 434.5 | 0.18315 | 0 | 0.06105 | 0 | 0.0018315 | 0 | 0.0006105 | 0 | 0.0018315 | 0.0006105 | 86146 | 258638 | 86145.9982
39029.363 | 2177 | 0 | 39029.363 | 1944 | 0 |  | 467 | 619 | 132.906 | 0 | 118.6813 | 0 | 1.3291 | 0 | 1.1868 | 0 | 1.3291 | 1.1868 | 18.8507 | 33.0957 | 17.5217
39029.3651 | 1999 | 0 | 39029.3651 | 2454 | 0 |  | 651.5 | 803.5 | 122.0391 | 0 | 149.8168 | 0 | 1.2204 | 0 | 1.4982 | 0 | 1.2204 | 1.4982 | 29.4337 | 5.4352 | 28.2133
39029.3673 | 2190 | 0 | 39029.3673 | 2127 | 0 |  | 836.5 | 988.5 | 133.6996 | 0 | 129.8535 | 0 | 1.337 | 0 | 1.2985 | 0 | 1.337 | 1.2985 | 18.1452 | 21.6446 | 16.8082
39029.3694 | 2296 | 0 | 39029.3694 | 1995 | 0 |  | 1021.5 | 1173.5 | 140.1709 | 0 | 121.7949 | 0 | 1.4017 | 0 | 1.2179 | 0 | 1.4017 | 1.2179 | 12.6908 | 29.6932 | 11.2891
39029.3715 | 2257 | 0 | 39029.3716 | 2285 | 0 |  | 1206 | 1358 | 137.79 | 0 | 139.4994 | 0 | 1.3779 | 0 | 1.395 | 0 | 1.3779 | 1.395 | 14.638 | 13.2333 | 13.2601
39029.3737 | 1966 | 0 | 39029.3737 | 2571 | 0 |  | 1391 | 1543 | 120.0244 | 0 | 156.9597 | 0 | 1.2002 | 0 | 1.5696 | 0 | 1.2002 | 1.5696 | 31.6063 | 0.63711 | 30.4061
39029.3758 | 351 | 0 | 39029.3758 | 2309 | 0 |  | 1575.5 | 1727.5 | 21.4286 | 0 | 140.9646 | 0 | 0.21429 | 0 | 1.4096 | 0 | 0.21429 | 1.4096 | 637.1453 | 12.0563 | 636.931

## B3-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.9133 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39029.3565 | 1 | 0 | 39029.3566 | 1 | 0 |  | -90 | 62 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39029.3587 | 1 | 0 | 39029.3587 | 1 | 0 |  | 94.5 | 246.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261838 | 261838 | 261837.9994
39029.3608 | 2 | 0 | 39029.3608 | 1 | 0 |  | 279.5 | 431.5 | 0.1221 | 0 | 0.06105 | 0 | 0.001221 | 0 | 0.0006105 | 0 | 0.001221 | 0.0006105 | 130869 | 261838 | 130868.9988
39029.363 | 1960 | 1 | 39029.363 | 1900 | 0 |  | 464 | 616 | 119.6581 | 0.06105 | 115.9951 | 0 | 1.1966 | 0.0006105 | 1.16 | 0 | 1.196 | 1.16 | 33.7045 | 37.8621 | 18081.5844
39029.3651 | 2446 | 0 | 39029.3651 | 2489 | 0 |  | 649 | 801 | 149.3284 | 0 | 151.9536 | 0 | 1.4933 | 0 | 1.5195 | 0 | 1.4933 | 1.5195 | 7.0883 | 5.2382 | 5.595
39029.3672 | 2354 | 0 | 39029.3672 | 2137 | 0 |  | 833.5 | 985.5 | 143.7118 | 0 | 130.464 | 0 | 1.4371 | 0 | 1.3046 | 0 | 1.4371 | 1.3046 | 11.2736 | 22.5728 | 9.8365
39029.3694 | 2603 | 0 | 39029.3694 | 2011 | 0 |  | 1018.5 | 1170.5 | 158.9133 | 0 | 122.7717 | 0 | 1.5891 | 0 | 1.2277 | 0 | 1.5891 | 1.2277 | 0.62927 | 30.2526 | 0.95986
39029.3715 | 2219 | 0 | 39029.3715 | 2047 | 0 |  | 1203.5 | 1355.5 | 135.4701 | 0 | 124.9695 | 0 | 1.3547 | 0 | 1.2497 | 0 | 1.3547 | 1.2497 | 18.0433 | 27.9619 | 16.6886
39029.3736 | 2288 | 0 | 39029.3737 | 2545 | 0 |  | 1388 | 1540 | 139.6825 | 0 | 155.3724 | 0 | 1.3968 | 0 | 1.5537 | 0 | 1.3968 | 1.5537 | 14.4834 | 2.9226 | 13.0866
39029.3758 | 313 | 0 | 39029.3758 | 2392 | 0 |  | 1573 | 1725 | 19.1087 | 0 | 146.0317 | 0 | 0.19109 | 0 | 1.4603 | 0 | 0.19109 | 1.4603 | 736.8626 | 9.5059 | 736.6715

## B3-B4
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.9365 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39029.3565 | 1 | 0 | 39029.3565 | 1 | 0 |  | -93 | 59 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39029.3586 | 1 | 0 | 39029.3587 | 1 | 0 |  | 92 | 244 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39029.3608 | 1105 | 1069 | 39029.3608 | 954 | 977 |  | 276.5 | 428.5 | 67.4603 | 65.2625 | 58.2418 | 59.6459 | 0.6746 | 0.65263 | 0.58242 | 0.59646 | 0.021978 | 0.014042 | 4101.6301 | 201193.4981 | 40.1466
39029.3629 | 2434 | 5 | 39029.3629 | 2103 | 3 |  | 461.5 | 613.5 | 148.5958 | 0.30525 | 128.3883 | 0.18315 | 1.486 | 0.0030525 | 1.2839 | 0.0018315 | 1.4829 | 1.2821 | 7.0328 | 24.3217 | 643.1696
39029.3651 | 2222 | 0 | 39029.3651 | 2395 | 0 |  | 646.5 | 798.5 | 135.6532 | 0 | 146.2149 | 0 | 1.3565 | 0 | 1.4621 | 0 | 1.3565 | 1.4621 | 17.1638 | 8.7006 | 15.8073
39029.3672 | 2587 | 0 | 39029.3672 | 2089 | 0 |  | 831 | 983 | 157.9365 | 0 | 127.5336 | 0 | 1.5794 | 0 | 1.2753 | 0 | 1.5794 | 1.2753 | 0.63317 | 24.6233 | 0.9462
39029.3693 | 2335 | 0 | 39029.3694 | 2287 | 0 |  | 1015.5 | 1167.5 | 142.5519 | 0 | 139.6215 | 0 | 1.4255 | 0 | 1.3962 | 0 | 1.4255 | 1.3962 | 11.4938 | 13.8338 | 10.0683
39029.3715 | 2500 | 0 | 39029.3715 | 2221 | 0 |  | 1200.5 | 1352.5 | 152.6252 | 0 | 135.5922 | 0 | 1.5263 | 0 | 1.3559 | 0 | 1.5263 | 1.3559 | 4.1352 | 17.2166 | 2.6089
39029.3736 | 2274 | 2 | 39029.3736 | 2330 | 4 |  | 1385.5 | 1537.5 | 138.8278 | 0.1221 | 142.2466 | 0.2442 | 1.3883 | 0.001221 | 1.4225 | 0.002442 | 1.3871 | 1.42 | 14.6055 | 11.8933 | 1739.8792
39029.3758 | 1087 | 832 | 39029.3758 | 1098 | 993 |  | 1570 | 1722 | 66.3614 | 50.7937 | 67.033 | 60.6227 | 0.66361 | 0.50794 | 0.67033 | 0.60623 | 0.15568 | 0.064103 | 491.2289 | 1549.6043 | 77.2707

## A2-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.1429 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39029.3563 | 1 | 0 | 39029.3563 | 1 | 0 |  | -112.5 | 39.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
39029.3584 | 1 | 0 | 39029.3584 | 1 | 0 |  | 72.5 | 224.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
39029.3606 | 1 | 0 | 39029.3606 | 1 | 0 |  | 257 | 409 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258938 | 258938 | 258937.9994
39029.3627 | 640 | 0 | 39029.3627 | 1816 | 0 |  | 442 | 594 | 39.072 | 0 | 110.8669 | 0 | 0.39072 | 0 | 1.1087 | 0 | 0.39072 | 1.1087 | 304.7469 | 42.6421 | 304.3562
39029.3648 | 2574 | 0 | 39029.3648 | 2024 | 0 |  | 626.5 | 778.5 | 157.1429 | 0 | 123.5653 | 0 | 1.5714 | 0 | 1.2357 | 0 | 1.5714 | 1.2357 | 0.63636 | 27.9832 | 0.93506
39029.367 | 2107 | 0 | 39029.367 | 2543 | 0 |  | 811.5 | 963.5 | 128.6325 | 0 | 155.2503 | 0 | 1.2863 | 0 | 1.5525 | 0 | 1.2863 | 1.5525 | 22.9416 | 1.8632 | 21.6553
39029.3691 | 2238 | 0 | 39029.3691 | 2267 | 0 |  | 996 | 1148 | 136.63 | 0 | 138.4005 | 0 | 1.3663 | 0 | 1.384 | 0 | 1.3663 | 1.384 | 15.7453 | 14.2647 | 14.379
39029.3712 | 2004 | 0 | 39029.3713 | 2573 | 0 |  | 1181 | 1333 | 122.3443 | 0 | 157.0818 | 0 | 1.2234 | 0 | 1.5708 | 0 | 1.2234 | 1.5708 | 29.2605 | 0.67548 | 28.037
39029.3734 | 2378 | 0 | 39029.3734 | 2253 | 0 |  | 1365.5 | 1517.5 | 145.177 | 0 | 137.5458 | 0 | 1.4518 | 0 | 1.3755 | 0 | 1.4518 | 1.3755 | 8.931 | 14.9747 | 7.4793
39029.3755 | 716 | 0 | 39029.3755 | 2495 | 0 |  | 1550.5 | 1702.5 | 43.7118 | 0 | 152.3199 | 0 | 0.43712 | 0 | 1.5232 | 0 | 0.43712 | 1.5232 | 261.7849 | 3.8228 | 261.3478

## A2-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 160.1575 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39029.3562 | 1 | 0 | 39029.3563 | 1 | 0 |  | -115.5 | 36.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39029.3584 | 1 | 0 | 39029.3584 | 1 | 0 |  | 69.5 | 221.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39029.3605 | 1 | 0 | 39029.3605 | 1 | 0 |  | 254.5 | 406.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 262238 | 262238 | 262237.9994
39029.3627 | 613 | 0 | 39029.3627 | 1798 | 0 |  | 439 | 591 | 37.4237 | 0 | 109.768 | 0 | 0.37424 | 0 | 1.0977 | 0 | 0.37424 | 1.0977 | 327.9576 | 45.9055 | 327.5833
39029.3648 | 2233 | 0 | 39029.3648 | 2329 | 0 |  | 623.5 | 775.5 | 136.3248 | 0 | 142.1856 | 0 | 1.3632 | 0 | 1.4219 | 0 | 1.3632 | 1.4219 | 17.4823 | 12.6398 | 16.1191
39029.3669 | 2291 | 0 | 39029.367 | 2079 | 0 |  | 808.5 | 960.5 | 139.8657 | 0 | 126.9231 | 0 | 1.3987 | 0 | 1.2692 | 0 | 1.3987 | 1.2692 | 14.5081 | 26.1847 | 13.1094
39029.3691 | 2302 | 0 | 39029.3691 | 2344 | 0 |  | 993.5 | 1145.5 | 140.5372 | 0 | 143.1013 | 0 | 1.4054 | 0 | 1.431 | 0 | 1.4054 | 1.431 | 13.9609 | 11.9189 | 12.5555
39029.3712 | 2074 | 0 | 39029.3712 | 2214 | 0 |  | 1178 | 1330 | 126.6178 | 0 | 135.1648 | 0 | 1.2662 | 0 | 1.3516 | 0 | 1.2662 | 1.3516 | 26.4889 | 18.4905 | 25.2227
39029.3734 | 1982 | 0 | 39029.3734 | 2607 | 0 |  | 1363 | 1515 | 121.0012 | 0 | 159.1575 | 0 | 1.21 | 0 | 1.5916 | 0 | 1.21 | 1.5916 | 32.3602 | 0.62831 | 31.1502
39029.3755 | 724 | 0 | 39029.3755 | 2275 | 0 |  | 1547.5 | 1699.5 | 44.2002 | 0 | 138.8889 | 0 | 0.442 | 0 | 1.3889 | 0 | 0.442 | 1.3889 | 262.3453 | 15.3134 | 261.9033

## A2-B4
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 156.2503 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39029.3562 | 1 | 0 | 39029.3562 | 1 | 0 |  | -118 | 34 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39029.3584 | 1 | 0 | 39029.3584 | 1 | 0 |  | 66.5 | 218.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39029.3605 | 1 | 0 | 39029.3605 | 1 | 0 |  | 251.5 | 403.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255838 | 255838 | 255837.9994
39029.3626 | 389 | 0 | 39029.3627 | 383 | 0 |  | 436.5 | 588.5 | 23.7485 | 0 | 23.3822 | 0 | 0.23748 | 0 | 0.23382 | 0 | 0.23748 | 0.23382 | 557.9383 | 568.2454 | 557.7008
39029.3648 | 2221 | 0 | 39029.3648 | 2297 | 0 |  | 621 | 773 | 135.5922 | 0 | 140.232 | 0 | 1.3559 | 0 | 1.4023 | 0 | 1.3559 | 1.4023 | 15.2355 | 11.4227 | 13.8796
39029.3669 | 2189 | 0 | 39029.3669 | 2450 | 0 |  | 805.5 | 957.5 | 133.6386 | 0 | 149.5726 | 0 | 1.3364 | 0 | 1.4957 | 0 | 1.3364 | 1.4957 | 16.9201 | 4.4645 | 15.5837
39029.3691 | 2029 | 0 | 39029.3691 | 2543 | 0 |  | 990.5 | 1142.5 | 123.8706 | 0 | 155.2503 | 0 | 1.2387 | 0 | 1.5525 | 0 | 1.2387 | 1.5525 | 26.14 | 0.64412 | 24.9013
39029.3712 | 2358 | 0 | 39029.3712 | 2257 | 0 |  | 1175.5 | 1327.5 | 143.956 | 0 | 137.79 | 0 | 1.4396 | 0 | 1.3779 | 0 | 1.4396 | 1.3779 | 8.5403 | 13.3974 | 7.1007
39029.3733 | 2410 | 0 | 39029.3733 | 2455 | 0 |  | 1360 | 1512 | 147.1306 | 0 | 149.8779 | 0 | 1.4713 | 0 | 1.4988 | 0 | 1.4713 | 1.4988 | 6.1983 | 4.2517 | 4.727
39029.3755 | 1226 | 876 | 39029.3755 | 1063 | 829 |  | 1545 | 1697 | 74.8474 | 53.4799 | 64.8962 | 50.6105 | 0.74847 | 0.5348 | 0.64896 | 0.50611 | 0.21368 | 0.14286 | 398.1312 | 5805.0584 | 51.3281

## A2-B3
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.3639 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39029.3562 | 1 | 0 | 39029.3562 | 1 | 0 |  | -121 | 31 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
39029.3583 | 1 | 0 | 39029.3583 | 1 | 0 |  | 64 | 216 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
39029.3605 | 1 | 0 | 39029.3605 | 1 | 0 |  | 248.5 | 400.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260938 | 260938 | 260937.9994
39029.3626 | 326 | 0 | 39029.3626 | 2104 | 0 |  | 433.5 | 585.5 | 19.9023 | 0 | 128.4493 | 0 | 0.19902 | 0 | 1.2845 | 0 | 0.19902 | 1.2845 | 700.7301 | 24.0675 | 700.531
39029.3647 | 1986 | 0 | 39029.3648 | 2385 | 0 |  | 618 | 770 | 121.2454 | 0 | 145.6044 | 0 | 1.2125 | 0 | 1.456 | 0 | 1.2125 | 1.456 | 31.4391 | 9.4499 | 30.2266
39029.3669 | 2124 | 0 | 39029.3669 | 2065 | 0 |  | 803 | 955 | 129.6703 | 0 | 126.0684 | 0 | 1.2967 | 0 | 1.2607 | 0 | 1.2967 | 1.2607 | 22.8992 | 26.4107 | 21.6025
39029.369 | 2323 | 0 | 39029.369 | 2594 | 0 |  | 987.5 | 1139.5 | 141.8193 | 0 | 158.3639 | 0 | 1.4182 | 0 | 1.5836 | 0 | 1.4182 | 1.5836 | 12.3711 | 0.63146 | 10.9529
39029.3712 | 2117 | 0 | 39029.3712 | 2491 | 0 |  | 1172.5 | 1324.5 | 129.243 | 0 | 152.0757 | 0 | 1.2924 | 0 | 1.5208 | 0 | 1.2924 | 1.5208 | 23.3056 | 4.7925 | 22.0132
39029.3733 | 2077 | 0 | 39029.3733 | 2196 | 0 |  | 1357.5 | 1509.5 | 126.801 | 0 | 134.0659 | 0 | 1.268 | 0 | 1.3407 | 0 | 1.268 | 1.3407 | 25.6803 | 18.8698 | 24.4123
39029.3754 | 1326 | 1050 | 39029.3755 | 1310 | 833 |  | 1542 | 1694 | 80.9524 | 64.1026 | 79.9756 | 50.8547 | 0.80952 | 0.64103 | 0.79976 | 0.50855 | 0.1685 | 0.29121 | 560.4505 | 2242.1158 | 21.3688

## A1-C6
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 159.7302 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39029.356 | 1 | 0 | 39029.356 | 1 | 0 |  | -140.5 | 11.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39029.3581 | 1 | 0 | 39029.3581 | 1 | 0 |  | 44.5 | 196.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39029.3602 | 1 | 0 | 39029.3603 | 1 | 0 |  | 229 | 381 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 261538 | 261538 | 261537.9994
39029.3624 | 1 | 0 | 39029.3624 | 2031 | 0 |  | 414 | 566 | 0.06105 | 0 | 123.9927 | 0 | 0.0006105 | 0 | 1.2399 | 0 | 0.0006105 | 1.2399 | 261538 | 28.8223 | 261537.9994
39029.3645 | 2143 | 0 | 39029.3645 | 2600 | 0 |  | 598.5 | 750.5 | 130.8303 | 0 | 158.7302 | 0 | 1.3083 | 0 | 1.5873 | 0 | 1.3083 | 1.5873 | 22.0896 | 0.63 | 20.7813
39029.3667 | 2409 | 0 | 39029.3667 | 2526 | 0 |  | 783.5 | 935.5 | 147.0696 | 0 | 154.2125 | 0 | 1.4707 | 0 | 1.5421 | 0 | 1.4707 | 1.5421 | 8.6086 | 3.578 | 7.1379
39029.3688 | 2073 | 0 | 39029.3688 | 2587 | 0 |  | 968 | 1120 | 126.5568 | 0 | 157.9365 | 0 | 1.2656 | 0 | 1.5794 | 0 | 1.2656 | 1.5794 | 26.2123 | 1.1357 | 24.9467
39029.3709 | 2304 | 0 | 39029.3709 | 2320 | 0 |  | 1153 | 1305 | 140.6593 | 0 | 141.6361 | 0 | 1.4066 | 0 | 1.4164 | 0 | 1.4066 | 1.4164 | 13.5582 | 12.775 | 12.1516
39029.3731 | 2114 | 0 | 39029.3731 | 2509 | 0 |  | 1337.5 | 1489.5 | 129.0598 | 0 | 153.1746 | 0 | 1.2906 | 0 | 1.5317 | 0 | 1.2906 | 1.5317 | 23.7644 | 4.2798 | 22.4738
39029.3752 | 706 | 0 | 39029.3752 | 2536 | 0 |  | 1522.5 | 1674.5 | 43.1013 | 0 | 154.823 | 0 | 0.43101 | 0 | 1.5482 | 0 | 0.43101 | 1.5482 | 270.5921 | 3.1696 | 270.1611

## A1-C5
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 155.823 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39029.3559 | 1 | 0 | 39029.3559 | 1 | 0 |  | -143.5 | 8.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39029.3581 | 1 | 0 | 39029.3581 | 1 | 0 |  | 41.5 | 193.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39029.3602 | 1 | 0 | 39029.3602 | 1 | 0 |  | 226.5 | 378.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 255138 | 255138 | 255137.9994
39029.3623 | 1 | 0 | 39029.3624 | 1478 | 0 |  | 411 | 563 | 0.06105 | 0 | 90.232 | 0 | 0.0006105 | 0 | 0.90232 | 0 | 0.0006105 | 0.90232 | 255138 | 72.6915 | 255137.9994
39029.3645 | 2285 | 0 | 39029.3645 | 2087 | 0 |  | 596 | 748 | 139.4994 | 0 | 127.4115 | 0 | 1.395 | 0 | 1.2741 | 0 | 1.395 | 1.2741 | 11.7015 | 22.299 | 10.3065
39029.3666 | 2471 | 0 | 39029.3666 | 2278 | 0 |  | 780.5 | 932.5 | 150.8547 | 0 | 139.072 | 0 | 1.5085 | 0 | 1.3907 | 0 | 1.5085 | 1.3907 | 3.2934 | 12.0448 | 1.7849
39029.3688 | 1986 | 0 | 39029.3688 | 2536 | 0 |  | 965.5 | 1117.5 | 121.2454 | 0 | 154.823 | 0 | 1.2125 | 0 | 1.5482 | 0 | 1.2125 | 1.5482 | 28.5186 | 0.6459 | 27.3062
39029.3709 | 2416 | 0 | 39029.3709 | 2047 | 0 |  | 1150 | 1302 | 147.4969 | 0 | 124.9695 | 0 | 1.475 | 0 | 1.2497 | 0 | 1.475 | 1.2497 | 5.6449 | 24.6888 | 4.1699
39029.373 | 2051 | 0 | 39029.3731 | 2029 | 0 |  | 1335 | 1487 | 125.2137 | 0 | 123.8706 | 0 | 1.2521 | 0 | 1.2387 | 0 | 1.2521 | 1.2387 | 24.4456 | 25.795 | 23.1935
39029.3752 | 820 | 0 | 39029.3752 | 2017 | 0 |  | 1519.5 | 1671.5 | 50.0611 | 0 | 123.138 | 0 | 0.50061 | 0 | 1.2314 | 0 | 0.50061 | 1.2314 | 211.2659 | 26.5434 | 210.7652

## A1-B4
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.2039 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39029.3559 | 1 | 0 | 39029.3559 | 1 | 0 |  | -146 | 6 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39029.358 | 1 | 0 | 39029.358 | 1 | 0 |  | 38.5 | 190.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39029.3602 | 1 | 0 | 39029.3602 | 1 | 0 |  | 223.5 | 375.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 259038 | 259038 | 259037.9994
39029.3623 | 1 | 0 | 39029.3623 | 1729 | 0 |  | 408.5 | 560.5 | 0.06105 | 0 | 105.5556 | 0 | 0.0006105 | 0 | 1.0556 | 0 | 0.0006105 | 1.0556 | 259038 | 49.8774 | 259037.9994
39029.3644 | 1997 | 0 | 39029.3645 | 2131 | 0 |  | 593 | 745 | 121.917 | 0 | 130.0977 | 0 | 1.2192 | 0 | 1.301 | 0 | 1.2192 | 1.301 | 29.7636 | 21.6039 | 28.5445
39029.3666 | 2367 | 0 | 39029.3666 | 2569 | 0 |  | 778 | 930 | 144.5055 | 0 | 156.8376 | 0 | 1.4451 | 0 | 1.5684 | 0 | 1.4451 | 1.5684 | 9.4795 | 0.87116 | 8.0345
39029.3687 | 2575 | 0 | 39029.3687 | 2539 | 0 |  | 962.5 | 1114.5 | 157.2039 | 0 | 155.0061 | 0 | 1.572 | 0 | 1.5501 | 0 | 1.572 | 1.5501 | 0.63612 | 2.063 | 0.93592
39029.3709 | 2420 | 0 | 39029.3709 | 2058 | 0 |  | 1147.5 | 1299.5 | 147.7411 | 0 | 125.641 | 0 | 1.4774 | 0 | 1.2564 | 0 | 1.4774 | 1.2564 | 7.0818 | 25.9174 | 5.6044
39029.373 | 2280 | 2 | 39029.373 | 2038 | 2 |  | 1332 | 1484 | 139.1941 | 0.1221 | 124.42 | 0.1221 | 1.3919 | 0.001221 | 1.2442 | 0.001221 | 1.3907 | 1.243 | 13.713 | 27.3759 | 3324.6275
39029.3751 | 1197 | 764 | 39029.3752 | 1257 | 972 |  | 1517 | 1669 | 73.0769 | 46.6422 | 76.7399 | 59.3407 | 0.73077 | 0.46642 | 0.7674 | 0.59341 | 0.26435 | 0.17399 | 310.5223 | 4762.0712 | 80.8134

## A1-B3
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.9365 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39029.3559 | 1 | 0 | 39029.3559 | 1 | 0 |  | -149 | 3 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39029.358 | 1 | 0 | 39029.358 | 1 | 0 |  | 36 | 188 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39029.3601 | 1 | 0 | 39029.3602 | 1 | 0 |  | 220.5 | 372.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 260238 | 260238 | 260237.9994
39029.3623 | 1 | 0 | 39029.3623 | 1901 | 0 |  | 405.5 | 557.5 | 0.06105 | 0 | 116.0562 | 0 | 0.0006105 | 0 | 1.1606 | 0 | 0.0006105 | 1.1606 | 260238 | 36.9479 | 260237.9994
39029.3644 | 2249 | 0 | 39029.3644 | 2505 | 0 |  | 590 | 742 | 137.3016 | 0 | 152.9304 | 0 | 1.373 | 0 | 1.5293 | 0 | 1.373 | 1.5293 | 15.7572 | 3.9273 | 14.3842
39029.3666 | 2142 | 0 | 39029.3666 | 2171 | 0 |  | 775 | 927 | 130.7692 | 0 | 132.5397 | 0 | 1.3077 | 0 | 1.3254 | 0 | 1.3077 | 1.3254 | 21.5397 | 19.9162 | 20.232
39029.3687 | 2372 | 0 | 39029.3687 | 2290 | 0 |  | 960 | 1112 | 144.8107 | 0 | 139.8046 | 0 | 1.4481 | 0 | 1.398 | 0 | 1.4481 | 1.398 | 9.7546 | 13.6847 | 8.3065
39029.3708 | 2338 | 0 | 39029.3708 | 2587 | 0 |  | 1144.5 | 1296.5 | 142.735 | 0 | 157.9365 | 0 | 1.4274 | 0 | 1.5794 | 0 | 1.4274 | 1.5794 | 11.3507 | 0.63317 | 9.9234
39029.373 | 2028 | 1 | 39029.373 | 2135 | 1 |  | 1329.5 | 1481.5 | 123.8095 | 0.06105 | 130.3419 | 0.06105 | 1.2381 | 0.0006105 | 1.3034 | 0.0006105 | 1.2375 | 1.3028 | 28.4496 | 21.9847 | 10351.7537
39029.3751 | 1546 | 830 | 39029.3751 | 1424 | 863 |  | 1514 | 1666 | 94.3834 | 50.6716 | 86.9353 | 52.6862 | 0.94383 | 0.50672 | 0.86935 | 0.52686 | 0.43712 | 0.34249 | 140.1147 | 2147.2882 | 26.1761

## A1-A2
Open Burn Test 7 |  |  | 2006-11-08 | 8:39 |  |  | Vs = |  | 158.0818 |  | R = | 100
Mix | 7-C | Tray A | IRMS | 1
0 | 200 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39029.3558 | 1 | 0 | 39029.3558 | 1 | 0 |  | -151.5 | 0.5 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39029.358 | 1 | 0 |  | 1 | 0 |  | 32 | 184 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39029.3601 | 1 | 0 | 39029.3601 | 1 | 0 |  | 218 | 370 | 0.06105 | 0 | 0.06105 | 0 | 0.0006105 | 0 | 0.0006105 | 0 | 0.0006105 | 0.0006105 | 258838 | 258838 | 258837.9994
39029.3622 | 1147 | 1194 | 39029.3623 | 1083 | 1051 |  | 402.5 | 554.5 | 70.0244 | 72.8938 | 66.1172 | 64.1636 | 0.70024 | 0.72894 | 0.66117 | 0.64164 | 0.028694 | 0.019536 | 2816.2811 | 28322.237 | 20.7292
39029.3644 | 2558 | 0 | 39029.3644 | 2075 | 0 |  | 587.5 | 739.5 | 156.1661 | 0 | 126.6789 | 0 | 1.5617 | 0 | 1.2668 | 0 | 1.5617 | 1.2668 | 1.2267 | 24.7894 | 0.33492
39029.3665 | 2215 | 0 | 39029.3665 | 2315 | 0 |  | 772.5 | 924.5 | 135.2259 | 0 | 141.3309 | 0 | 1.3523 | 0 | 1.4133 | 0 | 1.3523 | 1.4133 | 16.902 | 11.8523 | 15.5498
39029.3687 | 2342 | 0 | 39029.3687 | 2573 | 0 |  | 957 | 1109 | 142.9792 | 0 | 157.0818 | 0 | 1.4298 | 0 | 1.5708 | 0 | 1.4298 | 1.5708 | 10.5628 | 0.63661 | 9.133
39029.3708 | 2350 | 0 | 39029.3708 | 2147 | 0 |  | 1142 | 1294 | 143.4676 | 0 | 131.0745 | 0 | 1.4347 | 0 | 1.3107 | 0 | 1.4347 | 1.3107 | 10.1864 | 20.6046 | 8.7517
39029.3729 | 2207 | 3 | 39029.373 | 2509 | 4 |  | 1326.5 | 1478.5 | 134.7375 | 0.18315 | 153.1746 | 0.2442 | 1.3474 | 0.0018315 | 1.5317 | 0.002442 | 1.3455 | 1.5293 | 18.1109 | 3.2373 | 396.5544
39029.3751 | 1530 | 859 | 39029.3751 | 1576 | 785 |  | 1511.5 | 1663.5 | 93.4066 | 52.442 | 96.2149 | 47.9243 | 0.93407 | 0.52442 | 0.96215 | 0.47924 | 0.40965 | 0.48291 | 78439.134 | 128.2761 | 13.1083

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY A
0 | -152 | 16 | 15.7 | 15.8 | 16.3 | 16.9
1 | -151 | 16 | 15.7 | 15.8 | 16.3 | 16.9
2 | -150 | 16 | 15.7 | 15.8 | 16.3 | 16.9
3 | -149 | 16 | 15.7 | 15.8 | 16.3 | 16.9
4 | -148 | 16 | 15.7 | 15.8 | 16.3 | 16.9
5 | -147 | 16 | 15.7 | 15.8 | 16.3 | 16.9
6 | -146 | 16 | 15.7 | 15.7 | 16.3 | 16.9
7 | -145 | 16 | 15.7 | 15.7 | 16.3 | 16.9
8 | -144 | 16 | 15.7 | 15.7 | 16.3 | 16.9
9 | -143 | 16 | 15.7 | 15.7 | 16.3 | 16.9
10 | -142 | 16 | 15.7 | 15.7 | 16.3 | 16.9
11 | -141 | 16 | 15.7 | 15.7 | 16.3 | 16.9
12 | -140 | 16 | 15.7 | 15.7 | 16.3 | 16.9
13 | -139 | 16 | 15.7 | 15.7 | 16.3 | 16.9
14 | -138 | 16 | 15.7 | 15.7 | 16.3 | 16.9
15 | -137 | 16 | 15.7 | 15.7 | 16.3 | 16.9
16 | -136 | 16 | 15.7 | 15.7 | 16.3 | 16.9
17 | -135 | 16 | 15.7 | 15.7 | 16.3 | 16.9
18 | -134 | 16 | 15.7 | 15.7 | 16.3 | 16.9
19 | -133 | 16 | 15.7 | 15.7 | 16.3 | 16.9
20 | -132 | 16 | 15.7 | 15.7 | 16.3 | 16.9
21 | -131 | 16 | 15.7 | 15.7 | 16.3 | 16.9
22 | -130 | 16 | 15.6 | 15.7 | 16.3 | 16.9
23 | -129 | 16 | 15.6 | 15.7 | 16.3 | 16.9
24 | -128 | 16 | 15.7 | 15.7 | 16.3 | 16.9
25 | -127 | 16 | 15.6 | 15.7 | 16.3 | 16.9
26 | -126 | 16 | 15.6 | 15.7 | 16.3 | 16.9
27 | -125 | 16 | 15.6 | 15.7 | 16.3 | 16.9
28 | -124 | 16 | 15.6 | 15.7 | 16.3 | 16.9
29 | -123 | 16 | 15.6 | 15.7 | 16.3 | 16.9
30 | -122 | 16 | 15.6 | 15.7 | 16.3 | 16.9
31 | -121 | 16 | 15.6 | 15.7 | 16.3 | 16.9
32 | -120 | 16 | 15.6 | 15.7 | 16.3 | 16.9
33 | -119 | 16 | 15.6 | 15.7 | 16.3 | 16.9
34 | -118 | 16 | 15.7 | 15.7 | 16.3 | 16.9
35 | -117 | 16 | 15.6 | 15.7 | 16.3 | 16.9
36 | -116 | 16 | 15.6 | 15.7 | 16.3 | 16.9
37 | -115 | 16 | 15.6 | 15.7 | 16.3 | 16.9
38 | -114 | 16 | 15.6 | 15.7 | 16.3 | 16.9
39 | -113 | 16 | 15.6 | 15.7 | 16.3 | 16.9
40 | -112 | 16 | 15.6 | 15.7 | 16.3 | 16.9
41 | -111 | 16 | 15.6 | 15.7 | 16.3 | 16.9
42 | -110 | 16 | 15.6 | 15.7 | 16.3 | 16.9
43 | -109 | 16 | 15.6 | 15.7 | 16.3 | 16.9
44 | -108 | 16 | 15.6 | 15.7 | 16.3 | 16.9
45 | -107 | 16 | 15.6 | 15.7 | 16.3 | 16.9
46 | -106 | 16 | 15.6 | 15.7 | 16.3 | 16.9
47 | -105 | 16 | 15.6 | 15.7 | 16.3 | 16.9
48 | -104 | 16 | 15.6 | 15.7 | 16.3 | 16.9
49 | -103 | 16 | 15.6 | 15.7 | 16.3 | 16.9
50 | -102 | 16 | 15.6 | 15.7 | 16.3 | 16.9
51 | -101 | 16 | 15.6 | 15.7 | 16.3 | 16.9
52 | -100 | 16 | 15.6 | 15.7 | 16.3 | 16.9
53 | -99 | 16 | 15.6 | 15.7 | 16.3 | 16.9
54 | -98 | 16 | 15.6 | 15.7 | 16.3 | 16.9
55 | -97 | 16 | 15.6 | 15.7 | 16.3 | 16.9
56 | -96 | 16 | 15.6 | 15.7 | 16.3 | 16.9
57 | -95 | 16 | 15.6 | 15.7 | 16.3 | 16.9
58 | -94 | 16 | 15.6 | 15.7 | 16.3 | 16.9
59 | -93 | 16 | 15.6 | 15.7 | 16.3 | 16.9
60 | -92 | 16 | 15.6 | 15.7 | 16.3 | 16.9
61 | -91 | 16 | 15.6 | 15.7 | 16.3 | 16.9
62 | -90 | 16 | 15.6 | 15.7 | 16.3 | 16.9
63 | -89 | 16 | 15.6 | 15.7 | 16.3 | 16.9
64 | -88 | 16 | 15.6 | 15.7 | 16.3 | 16.9
65 | -87 | 16 | 15.6 | 15.7 | 16.3 | 16.9
66 | -86 | 16 | 15.6 | 15.7 | 16.3 | 16.9
67 | -85 | 16 | 15.6 | 15.7 | 16.3 | 16.9
68 | -84 | 16 | 15.6 | 15.7 | 16.3 | 16.9
69 | -83 | 16 | 15.6 | 15.7 | 16.3 | 16.9
70 | -82 | 16 | 15.6 | 15.7 | 16.3 | 16.9
71 | -81 | 16 | 15.6 | 15.7 | 16.3 | 16.9
72 | -80 | 16 | 15.6 | 15.7 | 16.3 | 16.9
73 | -79 | 16 | 15.6 | 15.7 | 16.3 | 16.9
74 | -78 | 16 | 15.6 | 15.7 | 16.3 | 16.9
75 | -77 | 16 | 15.6 | 15.7 | 16.3 | 16.9
76 | -76 | 16 | 15.6 | 15.7 | 16.3 | 16.9
77 | -75 | 16 | 15.6 | 15.7 | 16.3 | 16.9
78 | -74 | 16 | 15.6 | 15.7 | 16.3 | 16.9
79 | -73 | 16 | 15.6 | 15.7 | 16.3 | 16.9
80 | -72 | 16 | 15.6 | 15.7 | 16.3 | 16.9
81 | -71 | 16 | 15.6 | 15.7 | 16.3 | 16.9
82 | -70 | 16 | 15.6 | 15.7 | 16.3 | 16.9
83 | -69 | 16 | 15.6 | 15.7 | 16.3 | 16.9
84 | -68 | 16 | 15.6 | 15.7 | 16.3 | 16.9
85 | -67 | 16 | 15.6 | 15.7 | 16.3 | 16.9
86 | -66 | 16 | 15.6 | 15.7 | 16.3 | 16.9
87 | -65 | 16 | 15.6 | 15.7 | 16.3 | 16.9
88 | -64 | 16 | 15.6 | 15.7 | 16.3 | 16.9
89 | -63 | 16 | 15.6 | 15.7 | 16.3 | 16.9
90 | -62 | 16 | 15.6 | 15.7 | 16.3 | 16.9
91 | -61 | 16 | 15.6 | 15.7 | 16.3 | 16.9
92 | -60 | 16 | 15.6 | 15.7 | 16.3 | 16.9
93 | -59 | 16 | 15.6 | 15.7 | 16.3 | 16.9
94 | -58 | 16 | 15.6 | 15.7 | 16.3 | 16.9
95 | -57 | 16 | 15.6 | 15.7 | 16.3 | 16.9
96 | -56 | 16 | 15.6 | 15.7 | 16.3 | 16.9
97 | -55 | 16 | 15.6 | 15.7 | 16.3 | 16.9
98 | -54 | 16 | 15.6 | 15.7 | 16.3 | 16.9
99 | -53 | 16 | 15.6 | 15.7 | 16.3 | 16.9
100 | -52 | 16 | 15.6 | 15.7 | 16.3 | 16.9
101 | -51 | 16 | 15.6 | 15.7 | 16.3 | 16.9
102 | -50 | 16 | 15.6 | 15.7 | 16.3 | 16.9
103 | -49 | 16 | 15.6 | 15.7 | 16.3 | 16.9
104 | -48 | 16 | 15.6 | 15.7 | 16.3 | 16.9
105 | -47 | 16 | 15.6 | 15.7 | 16.3 | 16.9
106 | -46 | 16 | 15.6 | 15.7 | 16.3 | 16.9
107 | -45 | 16 | 15.6 | 15.7 | 16.3 | 16.9
108 | -44 | 16 | 15.6 | 15.7 | 16.3 | 16.9
109 | -43 | 16 | 15.6 | 15.7 | 16.3 | 16.9
110 | -42 | 16 | 15.6 | 15.7 | 16.3 | 16.9
111 | -41 | 16 | 15.6 | 15.7 | 16.3 | 16.9
112 | -40 | 16 | 15.6 | 15.7 | 16.3 | 16.9
113 | -39 | 16 | 15.6 | 15.7 | 16.3 | 16.9
114 | -38 | 16 | 15.6 | 15.7 | 16.3 | 16.9
115 | -37 | 16 | 15.6 | 15.7 | 16.3 | 16.9
116 | -36 | 16 | 15.6 | 15.7 | 16.3 | 16.9
117 | -35 | 16 | 15.6 | 15.7 | 16.3 | 16.9
118 | -34 | 16 | 15.6 | 15.7 | 16.3 | 16.9
119 | -33 | 16 | 15.6 | 15.7 | 16.3 | 16.9
120 | -32 | 16 | 15.6 | 15.7 | 16.3 | 16.9
121 | -31 | 16 | 15.6 | 15.7 | 16.3 | 16.9
122 | -30 | 16 | 15.6 | 15.7 | 16.3 | 16.9
123 | -29 | 16 | 15.6 | 15.7 | 16.3 | 16.9
124 | -28 | 16 | 15.6 | 15.7 | 16.3 | 16.9
125 | -27 | 16 | 15.6 | 15.7 | 16.3 | 16.9
126 | -26 | 16 | 15.6 | 15.7 | 16.3 | 16.9
127 | -25 | 16 | 15.6 | 15.7 | 16.3 | 16.9
128 | -24 | 16 | 15.6 | 15.7 | 16.3 | 16.9
129 | -23 | 16 | 15.6 | 15.7 | 16.3 | 16.9
130 | -22 | 16 | 15.6 | 15.7 | 16.3 | 16.9
131 | -21 | 16 | 15.6 | 15.7 | 16.3 | 16.9
132 | -20 | 16 | 15.6 | 15.7 | 16.3 | 16.9
133 | -19 | 16 | 15.6 | 15.7 | 16.3 | 16.9
134 | -18 | 16 | 15.6 | 15.7 | 16.3 | 16.9
135 | -17 | 16 | 15.6 | 15.7 | 16.3 | 16.9
136 | -16 | 16 | 15.6 | 15.7 | 16.3 | 16.9
137 | -15 | 16 | 15.6 | 15.7 | 16.3 | 16.9
138 | -14 | 16 | 15.6 | 15.7 | 16.3 | 16.9
139 | -13 | 16 | 15.6 | 15.7 | 16.3 | 16.9
140 | -12 | 16 | 15.6 | 15.7 | 16.3 | 16.9
141 | -11 | 16 | 15.6 | 15.7 | 16.3 | 16.9
142 | -10 | 16 | 15.6 | 15.7 | 16.3 | 16.9
143 | -9 | 16 | 15.6 | 15.7 | 16.3 | 16.9
144 | -8 | 16 | 15.6 | 15.7 | 16.3 | 16.9
145 | -7 | 16 | 15.6 | 15.7 | 16.3 | 16.9
146 | -6 | 16 | 15.6 | 15.7 | 16.3 | 16.9
147 | -5 | 16 | 15.6 | 15.7 | 16.3 | 16.9
148 | -4 | 16 | 15.6 | 15.7 | 16.3 | 16.9
149 | -3 | 16 | 15.6 | 15.7 | 16.3 | 16.9
150 | -2 | 16 | 15.6 | 15.7 | 16.3 | 17
151 | -1 | 16 | 15.6 | 15.7 | 16.3 | 17
152 | 0 | 16 | 15.6 | 15.7 | 16.3 | 17
153 | 1 | 16 | 15.6 | 15.7 | 16.3 | 17
154 | 2 | 16 | 15.6 | 15.7 | 16.3 | 17
155 | 3 | 16 | 15.6 | 15.7 | 16.3 | 17
156 | 4 | 16 | 15.7 | 16.1 | 16.3 | 17
157 | 5 | 16 | 16.7 | 17.8 | 16.3 | 17.2
158 | 6 | 16 | 20.8 | 26.8 | 16.3 | 18.1
159 | 7 | 16 | 28.2 | 45.8 | 16.3 | 20
160 | 8 | 16 | 39.7 | 72.4 | 16.4 | 22.4
161 | 9 | 16 | 53.7 | 106.8 | 16.4 | 25.2
162 | 10 | 16 | 71.5 | 131.5 | 16.4 | 27.7
163 | 11 | 16 | 86.1 | 157.7 | 16.5 | 30.5
164 | 12 | 16 | 109.7 | 204.6 | 16.6 | 34.8
165 | 13 | 16.1 | 145.8 | 251.2 | 16.6 | 40.4
166 | 14 | 16.1 | 172.8 | 275.4 | 16.7 | 43.5
167 | 15 | 16.2 | 203.7 | 325 | 16.7 | 49.9
168 | 16 | 16.2 | 227.4 | 345 | 16.8 | 55.4
169 | 17 | 16.3 | 262.2 | 383.6 | 16.9 | 61.3
170 | 18 | 16.3 | 306.1 | 422.9 | 17 | 67
171 | 19 | 16.4 | 348.8 | 461.8 | 17.1 | 73.9
172 | 20 | 16.5 | 388.3 | 488.1 | 17.3 | 79
173 | 21 | 16.7 | 432.8 | 512.6 | 17.5 | 83
174 | 22 | 16.9 | 475.2 | 535.9 | 17.7 | 87.5
175 | 23 | 17.1 | 502.9 | 566.5 | 17.9 | 91.3
176 | 24 | 17.4 | 535.5 | 583 | 18.2 | 95.2
177 | 25 | 17.8 | 547.7 | 579.9 | 18.5 | 99
178 | 26 | 18.3 | 580.5 | 610 | 18.8 | 105.7
179 | 27 | 18.7 | 594.3 | 637.2 | 19.2 | 110.4
180 | 28 | 19.3 | 601.3 | 647.6 | 19.6 | 116.6
181 | 29 | 19.9 | 620.4 | 665.7 | 20.2 | 127.4
182 | 30 | 20.5 | 625.8 | 674.2 | 20.8 | 133
183 | 31 | 21.1 | 644.2 | 682.2 | 21.5 | 139.9
184 | 32 | 21.7 | 655.5 | 678.9 | 22.3 | 143.8
185 | 33 | 22.4 | 647.9 | 671 | 23.2 | 147.3
186 | 34 | 23.1 | 647.3 | 656.3 | 24.4 | 149.6
187 | 35 | 23.8 | 643.8 | 642.6 | 25.8 | 150.7
188 | 36 | 24.5 | 657.1 | 651.1 | 29.5 | 154.6
189 | 37 | 25.2 | 655.5 | 638.4 | 38.8 | 156.9
190 | 38 | 26 | 649.7 | 622.6 | 46.1 | 158.6
191 | 39 | 26.8 | 642.2 | 596.8 | 51.3 | 159.1
192 | 40 | 27.6 | 641.6 | 583.7 | 56.1 | 160.9
193 | 41 | 28.5 | 625.7 | 589.4 | 59.2 | 164.7
194 | 42 | 29.4 | 627.8 | 591.2 | 64.9 | 168.9
195 | 43 | 30.3 | 620 | 589.3 | 69.9 | 173.2
196 | 44 | 31.3 | 603.8 | 583.1 | 73.4 | 175.2
197 | 45 | 32.3 | 597.8 | 592.7 | 78.5 | 179.2
198 | 46 | 33.3 | 598.4 | 611 | 84.7 | 183.5
199 | 47 | 34.3 | 614.1 | 624.9 | 92.2 | 188.9
200 | 48 | 35.3 | 623.4 | 638.9 | 97.9 | 196.3
201 | 49 | 36.4 | 627.6 | 660.3 | 105.3 | 202.3
202 | 50 | 37.5 | 622.5 | 652.2 | 109.2 | 207.6
203 | 51 | 38.7 | 612.7 | 646.5 | 114.1 | 212.8
204 | 52 | 40 | 605 | 646.5 | 120.1 | 215.5
205 | 53 | 41.3 | 612.7 | 656.9 | 127.5 | 219.1
206 | 54 | 42.5 | 634.6 | 667.8 | 134.6 | 222.2
207 | 55 | 43.8 | 634.8 | 665.9 | 137.7 | 226.5
208 | 56 | 45.1 | 617.5 | 653.1 | 137.3 | 229
209 | 57 | 46.5 | 615.4 | 645.3 | 138.8 | 231
210 | 58 | 47.9 | 603.2 | 636.7 | 140.4 | 233.2
211 | 59 | 49.3 | 591.3 | 626.4 | 141.6 | 234.8
212 | 60 | 50.6 | 589.7 | 618.6 | 143.8 | 235.3
213 | 61 | 51.9 | 602.5 | 621.8 | 148.5 | 238.9
214 | 62 | 53.3 | 611.5 | 621.2 | 153.4 | 241.5
215 | 63 | 54.7 | 627.9 | 621.6 | 158 | 243.4
216 | 64 | 56.1 | 652.8 | 622.9 | 163.2 | 245.6
217 | 65 | 57.7 | 658.4 | 622.2 | 165.8 | 249.2
218 | 66 | 59.4 | 652.5 | 611 | 166.1 | 251.6
219 | 67 | 61.2 | 665.9 | 613.5 | 171.4 | 252.4
220 | 68 | 63 | 675 | 605.3 | 173.8 | 254.1
221 | 69 | 64.9 | 686.8 | 608.4 | 177.2 | 255.3
222 | 70 | 67 | 702.2 | 617.6 | 182.8 | 258.5
223 | 71 | 69.2 | 717.5 | 630.3 | 186 | 262.5
224 | 72 | 71.5 | 733.1 | 643.6 | 190 | 266
225 | 73 | 74 | 734.7 | 645.8 | 190.7 | 270.7
226 | 74 | 76.7 | 742.3 | 667.6 | 197 | 276.3
227 | 75 | 79.4 | 747.5 | 682.4 | 198.8 | 281.8
228 | 76 | 82.2 | 758.4 | 689.6 | 201.9 | 288.3
229 | 77 | 84.9 | 764.2 | 681.6 | 202.6 | 291.5
230 | 78 | 87.8 | 760.6 | 670.5 | 202.6 | 292.7
231 | 79 | 90.7 | 752.1 | 664.8 | 203.1 | 295.9
232 | 80 | 93.9 | 745 | 667.8 | 204.7 | 298.7
233 | 81 | 97 | 739.8 | 666.7 | 204.7 | 301.2
234 | 82 | 100.2 | 744.4 | 685.2 | 208.9 | 303.8
235 | 83 | 103.4 | 751.4 | 679.7 | 213.4 | 306.1
236 | 84 | 106.7 | 749.7 | 676.1 | 216.3 | 310.1
237 | 85 | 110.2 | 759.3 | 677.8 | 219.4 | 313.5
238 | 86 | 114 | 768.7 | 684 | 221.7 | 318.1
239 | 87 | 118 | 776.3 | 693.3 | 223.5 | 324.1
240 | 88 | 122.3 | 786.2 | 703 | 225.1 | 328.5
241 | 89 | 126.8 | 799.8 | 721.7 | 228.4 | 333.5
242 | 90 | 131.6 | 801.1 | 716.7 | 228.3 | 338
243 | 91 | 136.7 | 806.5 | 728.2 | 229.3 | 343.6
244 | 92 | 141.9 | 806.2 | 736.9 | 229.3 | 348.2
245 | 93 | 147.4 | 817.3 | 744.3 | 230.4 | 351
246 | 94 | 153.4 | 831.7 | 752.4 | 232.1 | 355.9
247 | 95 | 160.2 | 841.1 | 756 | 232.3 | 361.5
248 | 96 | 167.3 | 849.7 | 763 | 232.3 | 367
249 | 97 | 174.7 | 853.1 | 779.8 | 233.2 | 376.9
250 | 98 | 181.8 | 857 | 781.5 | 235 | 383.6
251 | 99 | 188.1 | 855.7 | 784.9 | 236.1 | 391.8
252 | 100 | 194.6 | 858.6 | 802.1 | 237.9 | 400.3
253 | 101 | 201.3 | 860.1 | 809.1 | 239 | 406.2
254 | 102 | 208.1 | 862.9 | 796.7 | 239.7 | 411.9
255 | 103 | 214.8 | 861.6 | 782.5 | 240.3 | 415.1
256 | 104 | 220.4 | 860.7 | 784.7 | 241 | 419.7
257 | 105 | 225 | 861.7 | 786.2 | 242.2 | 424.8
258 | 106 | 229.3 | 862.4 | 783.4 | 243.6 | 427.7
259 | 107 | 233.6 | 864.2 | 788.6 | 245 | 430.2
260 | 108 | 237.7 | 865.7 | 782.8 | 246.1 | 435.1
261 | 109 | 241.4 | 871.1 | 785.2 | 247.6 | 439.1
262 | 110 | 244.8 | 875.3 | 781.7 | 249.8 | 441.1
263 | 111 | 247.6 | 867.7 | 778.9 | 251.9 | 442.1
264 | 112 | 249.9 | 864.4 | 780.6 | 254.4 | 444.9
265 | 113 | 252.1 | 864.6 | 789.7 | 257.2 | 448
266 | 114 | 254.4 | 869.9 | 788.4 | 260.3 | 449
267 | 115 | 256.6 | 873.4 | 784.8 | 263.5 | 451.3
268 | 116 | 258.5 | 877.4 | 780.8 | 266.3 | 454.1
269 | 117 | 260.3 | 874.8 | 766.8 | 268.8 | 454.5
270 | 118 | 262.1 | 873.5 | 763 | 270.8 | 457.4
271 | 119 | 263.7 | 872.7 | 758.7 | 272.8 | 457.6
272 | 120 | 265.3 | 871.2 | 763.5 | 274.3 | 459.9
273 | 121 | 266.4 | 866.6 | 760.3 | 276.9 | 463
274 | 122 | 267.3 | 865.7 | 777.5 | 280 | 468.9
275 | 123 | 268.5 | 866.1 | 780.3 | 283.6 | 472
276 | 124 | 270.2 | 873.1 | 768.3 | 287.2 | 474.7
277 | 125 | 272.1 | 876.1 | 776.3 | 290.8 | 480.2
278 | 126 | 273.8 | 874.6 | 784 | 295.2 | 484.4
279 | 127 | 275 | 880.4 | 772.1 | 299.5 | 486
280 | 128 | 275.5 | 879.3 | 746.6 | 302.3 | 486.8
281 | 129 | 275.8 | 873.5 | 725.7 | 303.9 | 485.3
282 | 130 | 276.3 | 872.3 | 735 | 305.6 | 485.8
283 | 131 | 277 | 872.9 | 736.6 | 307.9 | 488.7
284 | 132 | 278.1 | 866 | 729.4 | 309.8 | 490.4
285 | 133 | 279.4 | 864.8 | 725.1 | 311.9 | 491.5
286 | 134 | 280.8 | 870.8 | 717 | 314.2 | 491.3
287 | 135 | 282.3 | 871.4 | 716.1 | 317.1 | 491.5
288 | 136 | 284 | 875.6 | 714.1 | 319.3 | 491.6
289 | 137 | 285.7 | 881.3 | 712.1 | 321.6 | 492.8
290 | 138 | 286.9 | 878.6 | 706.3 | 323.7 | 493.6
291 | 139 | 288 | 874.6 | 708.6 | 325.3 | 496
292 | 140 | 289.1 | 876.8 | 716.2 | 327.1 | 498.7
293 | 141 | 290.4 | 880.2 | 724.3 | 329.4 | 502
294 | 142 | 291.9 | 880.2 | 729.7 | 332.6 | 503
295 | 143 | 293.4 | 878.7 | 745.5 | 335.6 | 506.8
296 | 144 | 295 | 872.5 | 731.4 | 338.4 | 506.5
297 | 145 | 297.1 | 872.7 | 750.4 | 341 | 512.2
298 | 146 | 299.2 | 868.4 | 761.2 | 344.8 | 515.6
299 | 147 | 301.1 | 871.1 | 773.7 | 348.2 | 518.1
300 | 148 | 303.1 | 868.8 | 784 | 351.9 | 522.6
301 | 149 | 304.9 | 861.5 | 791.3 | 356.1 | 529
302 | 150 | 306.8 | 871.3 | 793.2 | 360.1 | 531
303 | 151 | 308.5 | 876.6 | 780.8 | 362.9 | 531.2
304 | 152 | 310.2 | 876.8 | 771.1 | 364.5 | 533.2
305 | 153 | 312.3 | 874.7 | 785.2 | 366.9 | 538.8
306 | 154 | 314.7 | 881.1 | 785.4 | 370.6 | 540.4
307 | 155 | 317.6 | 886.8 | 801.7 | 374.6 | 542.6
308 | 156 | 320.4 | 878.6 | 804 | 378.5 | 548.3
309 | 157 | 323.2 | 877.1 | 812 | 382.1 | 552.8
310 | 158 | 326.2 | 877.9 | 805.2 | 386 | 556.3
311 | 159 | 328.9 | 877.1 | 793.1 | 389 | 556.5
312 | 160 | 331.5 | 880.3 | 788.9 | 391.2 | 557.4
313 | 161 | 334.3 | 881.1 | 776.3 | 393.7 | 558.4
314 | 162 | 336.7 | 883.8 | 775.2 | 395.8 | 556.9
315 | 163 | 339.6 | 885.6 | 774.3 | 398.7 | 560
316 | 164 | 342.6 | 885.6 | 771 | 401.8 | 560.3
317 | 165 | 344.7 | 876.3 | 781.5 | 404.7 | 563.6
318 | 166 | 346.5 | 873.2 | 778.8 | 407.8 | 565.6
319 | 167 | 349 | 876.7 | 789.1 | 410.8 | 568.7
320 | 168 | 351.1 | 874.6 | 791.1 | 413.4 | 569.3
321 | 169 | 353.7 | 877.5 | 793.2 | 416.2 | 571
322 | 170 | 356.4 | 868.1 | 801.4 | 420.1 | 573.9
323 | 171 | 359.6 | 862.7 | 799.2 | 423.7 | 576.6
324 | 172 | 362.8 | 868.7 | 785.7 | 426.9 | 577
325 | 173 | 365.7 | 874.6 | 783.5 | 429.9 | 578.5
326 | 174 | 368.4 | 872.2 | 780.1 | 432.7 | 579.6
327 | 175 | 370.7 | 870.9 | 789.5 | 434.6 | 581.7
328 | 176 | 373.7 | 868.3 | 799.2 | 436.9 | 585
329 | 177 | 376.8 | 861.7 | 807.4 | 439.2 | 589
330 | 178 | 380.3 | 869.9 | 797.6 | 442.1 | 590
331 | 179 | 384.3 | 869.8 | 800.5 | 444.3 | 592.1
332 | 180 | 388.1 | 864.4 | 807.7 | 445.8 | 595.5
333 | 181 | 392 | 864.6 | 804.9 | 447.6 | 597
334 | 182 | 395.5 | 862.3 | 809.6 | 448.7 | 600.3
335 | 183 | 398.8 | 864 | 808.5 | 450.7 | 602.4
336 | 184 | 401.6 | 871.6 | 791.2 | 452.8 | 603.2
337 | 185 | 403.7 | 866.8 | 783.8 | 453.9 | 603.4
338 | 186 | 406.3 | 861.8 | 778.2 | 454.6 | 602.3
339 | 187 | 409 | 854.6 | 788.6 | 455.5 | 603.4
340 | 188 | 411.7 | 852.3 | 788.7 | 456.6 | 605.2
341 | 189 | 414.6 | 853.2 | 780.7 | 457.6 | 604.9
342 | 190 | 416.9 | 852 | 779.2 | 458.3 | 604.5
343 | 191 | 419.8 | 851.8 | 787.5 | 459.1 | 605.6
344 | 192 | 423.2 | 856.1 | 760.4 | 460.3 | 603.6
345 | 193 | 427 | 854.9 | 741.3 | 461 | 601.2
346 | 194 | 430.6 | 852.2 | 723.8 | 461.1 | 599.2
347 | 195 | 432.4 | 843.5 | 717.9 | 460.9 | 598.1
348 | 196 | 434.9 | 841.2 | 725 | 461 | 596.5
349 | 197 | 437.6 | 836.2 | 719 | 461.6 | 595.3
350 | 198 | 440.3 | 833.8 | 710.7 | 461.5 | 592.6
351 | 199 | 442.6 | 836.2 | 715.2 | 462.2 | 591.6
352 | 200 | 445.3 | 835.5 | 722.7 | 463.5 | 590.9
353 | 201 | 448.9 | 836.4 | 742 | 464.7 | 591.5
354 | 202 | 452.2 | 841.4 | 753.1 | 466.1 | 593.1
355 | 203 | 454.5 | 842.4 | 759.6 | 466.7 | 595.1
356 | 204 | 456.9 | 844.3 | 762.6 | 467.9 | 594.8
357 | 205 | 458.8 | 851.4 | 755.7 | 469.7 | 594.9
358 | 206 | 460.4 | 853.9 | 754.6 | 470.8 | 594.8
359 | 207 | 462.3 | 854.6 | 760.2 | 471.6 | 594
360 | 208 | 464.5 | 855.7 | 775.9 | 472.5 | 597
361 | 209 | 467.3 | 852.2 | 795.1 | 473.2 | 600.6
362 | 210 | 470.3 | 845.4 | 806 | 474.3 | 605.8
363 | 211 | 473.2 | 844.5 | 806.3 | 475.1 | 607
364 | 212 | 477.1 | 855 | 789 | 475.9 | 608.7
365 | 213 | 480.8 | 860.5 | 793.9 | 476.2 | 608.9
366 | 214 | 483.9 | 859.3 | 796.4 | 476.7 | 611.2
367 | 215 | 486.2 | 861 | 800.7 | 476.9 | 614.3
368 | 216 | 488.2 | 846.9 | 817.8 | 477.2 | 622.2
369 | 217 | 489.8 | 840.9 | 819.3 | 477.2 | 627.4
370 | 218 | 492.3 | 843.3 | 821.5 | 477 | 628.5
371 | 219 | 494.6 | 851.6 | 796.2 | 476.9 | 628.2
372 | 220 | 496.5 | 851.4 | 798.5 | 476.8 | 630.6
373 | 221 | 498.1 | 846.3 | 801.7 | 477 | 634.1
374 | 222 | 499.7 | 843.6 | 802.8 | 478 | 637.2
375 | 223 | 501.1 | 847.4 | 779.5 | 478.5 | 636.9
376 | 224 | 503.5 | 853 | 775.8 | 478.8 | 637.4
377 | 225 | 505.5 | 855 | 768.8 | 479.1 | 637.3
378 | 226 | 507.5 | 859.4 | 764.3 | 479 | 637.8
379 | 227 | 509.2 | 855.8 | 767.3 | 479 | 640.7
380 | 228 | 511.6 | 850.3 | 776 | 479.1 | 641.4
381 | 229 | 513.7 | 840.1 | 793.7 | 479.8 | 647
382 | 230 | 515.6 | 831 | 801.8 | 480.9 | 650.4
383 | 231 | 517.5 | 825.2 | 804 | 481.7 | 651.1
384 | 232 | 519.9 | 826.5 | 801.3 | 482.2 | 651.1
385 | 233 | 522.6 | 825.4 | 801.8 | 482.3 | 653.1
386 | 234 | 526 | 823.1 | 802.2 | 482.3 | 655
387 | 235 | 528.7 | 818 | 797.1 | 482.5 | 654.9
388 | 236 | 532.1 | 817.2 | 792.4 | 482 | 654.5
389 | 237 | 535.6 | 818.9 | 798.6 | 481.4 | 655
390 | 238 | 538.7 | 815.8 | 815.8 | 480.8 | 658.7
391 | 239 | 540.4 | 814.8 | 815.6 | 480.5 | 661.9
392 | 240 | 542 | 811.7 | 812.1 | 480.3 | 663.7
393 | 241 | 544.1 | 809 | 814.5 | 480.1 | 664.9
394 | 242 | 546.6 | 807.9 | 814 | 480 | 666.5
395 | 243 | 549.6 | 810.2 | 807.1 | 480.2 | 667.2
396 | 244 | 552.9 | 812.2 | 805.4 | 480.7 | 667.7
397 | 245 | 555.7 | 813.2 | 799.9 | 481.2 | 667.6
398 | 246 | 558.4 | 812.2 | 799.9 | 481.6 | 670
399 | 247 | 561.1 | 813.5 | 798.8 | 482.2 | 669.2
400 | 248 | 563.2 | 810.1 | 805.3 | 482.9 | 672.1
401 | 249 | 566 | 812.5 | 814.7 | 484 | 674.6
402 | 250 | 568.2 | 808.7 | 816.5 | 485.2 | 676.9
403 | 251 | 569.6 | 806.4 | 814.9 | 487 | 676.3
404 | 252 | 570.6 | 805.1 | 813.9 | 488.5 | 679
405 | 253 | 571.9 | 804 | 809.8 | 489.9 | 680.5
406 | 254 | 573.8 | 802.4 | 807.3 | 491 | 683
407 | 255 | 574.7 | 800.8 | 811.7 | 492.1 | 685.4
408 | 256 | 576.3 | 801 | 814.5 | 493.4 | 686.6
409 | 257 | 577.2 | 800.4 | 807.3 | 494.8 | 687.4
410 | 258 | 578 | 805 | 805.5 | 496.3 | 687.3
411 | 259 | 577.7 | 805.9 | 801.4 | 498.1 | 687.4
412 | 260 | 577.3 | 805.1 | 795.9 | 499.6 | 686.3
413 | 261 | 578 | 796 | 787.7 | 495.8 | 686.7
414 | 262 | 579.5 | 800.9 | 783.8 | 502.4 | 687.2
415 | 263 | 580.9 | 796.7 | 780.5 | 502.8 | 686.5
416 | 264 | 583 | 794.2 | 782.1 | 504.7 | 687.2
417 | 265 | 585.3 | 729.3 | 781.3 | 473.7 | 686.4
418 | 266 | 587 | 692.9 | 760.9 | 451.2 | 684
419 | 267 | 588.8 | 779.1 | 743.5 | 494.3 | 681.6
420 | 268 | 589 | 821.9 | 733.9 | 516.4 | 679.1
421 | 269 | 588.5 | 822 | 738.8 | 519 | 679.4
422 | 270 | 588 | 819.5 | 760 | 521.7 | 682.2
423 | 271 | 586.3 | 814.1 | 774.7 | 524.2 | 686.2
424 | 272 | 586 | 814.3 | 778.6 | 527 | 689.7
425 | 273 | 586.2 | 817.1 | 774 | 530 | 688.9
426 | 274 | 585.3 | 818.1 | 776.6 | 532.6 | 688
427 | 275 | 585.1 | 818.3 | 776.9 | 535.9 | 688
428 | 276 | 585.7 | 818.7 | 780 | 539 | 688.1
429 | 277 | 585.3 | 814.7 | 780.1 | 541.9 | 689.7
430 | 278 | 585.2 | 811.6 | 783.1 | 545.1 | 689.8
431 | 279 | 587 | 813.6 | 779.2 | 547.7 | 688.9
432 | 280 | 590 | 818.9 | 766 | 550.9 | 685.5
433 | 281 | 593 | 826 | 762.7 | 554.3 | 683.2
434 | 282 | 595.2 | 825.7 | 775.1 | 557.5 | 684.8
435 | 283 | 597 | 824.1 | 786.9 | 561 | 686.5
436 | 284 | 598.3 | 822.5 | 788.1 | 563.9 | 687.9
437 | 285 | 599.4 | 824.7 | 779.8 | 566.4 | 685.8
438 | 286 | 600.8 | 823.6 | 781.2 | 569.3 | 686.8
439 | 287 | 602.5 | 822.5 | 777 | 571.4 | 686
440 | 288 | 604 | 822.8 | 755.4 | 573.8 | 682.2
441 | 289 | 606 | 825.1 | 740 | 576.4 | 679.8
442 | 290 | 608.2 | 827.2 | 726.2 | 579 | 676.1
443 | 291 | 609.5 | 826.3 | 719.9 | 581.8 | 674.4
444 | 292 | 610.8 | 821.2 | 735 | 584.3 | 674.2
445 | 293 | 612.8 | 817.8 | 737.6 | 586.4 | 674.3
446 | 294 | 613.4 | 817.8 | 734.6 | 589.1 | 672.4
447 | 295 | 614 | 815.2 | 744.6 | 592.1 | 673.7
448 | 296 | 615.8 | 811.8 | 752.9 | 595 | 673.7
449 | 297 | 618.8 | 812.2 | 761.3 | 597.8 | 673.2
450 | 298 | 622.1 | 812.1 | 767.2 | 599.5 | 672.9
451 | 299 | 625.1 | 815.3 | 749.8 | 601.7 | 670.2
452 | 300 | 627 | 817.2 | 732.9 | 604.8 | 667.4
453 | 301 | 629.5 | 814 | 739.1 | 606.7 | 667.8
454 | 302 | 631 | 812.8 | 743.6 | 609.2 | 668.8
455 | 303 | 633.1 | 812 | 759 | 612.1 | 671.3
456 | 304 | 635.8 | 808.6 | 778.3 | 614.6 | 674.9
457 | 305 | 637 | 807 | 773.9 | 616.6 | 676.4
458 | 306 | 638.8 | 809.4 | 778.3 | 618.9 | 677.2
459 | 307 | 641.8 | 807.3 | 784.4 | 621.7 | 679.6
460 | 308 | 644.1 | 805.5 | 789.6 | 624.2 | 681.5
461 | 309 | 646 | 804.2 | 792.4 | 626.8 | 684.4
462 | 310 | 647.7 | 802.1 | 790.8 | 629 | 687.6
463 | 311 | 650.2 | 802.4 | 794.7 | 631.1 | 689.3
464 | 312 | 652.8 | 800.4 | 801.6 | 633.6 | 692.9
465 | 313 | 655.8 | 800.8 | 807.8 | 636.6 | 693.5
466 | 314 | 658.8 | 800.7 | 813.3 | 639.1 | 697.3
467 | 315 | 662 | 799.8 | 819.4 | 641.8 | 699.2
468 | 316 | 663.8 | 799 | 813.9 | 643.7 | 700.6
469 | 317 | 665.6 | 799.4 | 808.5 | 649.9 | 699.1
470 | 318 | 668.5 | 800.5 | 811.7 | 648.7 | 700.9
471 | 319 | 671.3 | 802.3 | 797.7 | 651.3 | 700.3
472 | 320 | 675.4 | 807.3 | 791.2 | 654.9 | 699.3
473 | 321 | 678.2 | 806.2 | 799.7 | 658.1 | 701.6
474 | 322 | 679.2 | 803.5 | 805.9 | 660.7 | 704.7
475 | 323 | 682.6 | 805.1 | 809.7 | 663.9 | 706
476 | 324 | 685.7 | 804.1 | 805.2 | 666.7 | 706.6
477 | 325 | 687.3 | 804.6 | 787.8 | 669.5 | 703.7
478 | 326 | 689.4 | 806.4 | 785 | 673.3 | 701.9
479 | 327 | 690.7 | 806.1 | 780.9 | 676.5 | 701.4
480 | 328 | 690.2 | 806.7 | 771.2 | 679.1 | 701.1
481 | 329 | 690.9 | 804 | 772 | 681.2 | 701
482 | 330 | 691.9 | 806.1 | 762.9 | 683.7 | 699.1
483 | 331 | 692.9 | 807.8 | 757.1 | 686.3 | 698.1
484 | 332 | 693.8 | 809.9 | 743.4 | 689.6 | 695.3
485 | 333 | 694.5 | 811.5 | 726 | 693.1 | 691.9
486 | 334 | 696.1 | 809.2 | 715.3 | 696.5 | 690.8
487 | 335 | 698.1 | 808 | 707.6 | 699.3 | 687.4
488 | 336 | 699.9 | 808.6 | 692.5 | 702.5 | 685
489 | 337 | 701.4 | 805.9 | 690.2 | 703.1 | 683.7
490 | 338 | 704 | 805.6 | 692.5 | 705 | 682.3
491 | 339 | 707 | 808 | 692.2 | 708.4 | 679.7
492 | 340 | 709.6 | 809.3 | 695.1 | 712.1 | 677.4
493 | 341 | 711.4 | 808.9 | 697.9 | 714.4 | 676.7
494 | 342 | 712.1 | 808 | 690.8 | 716 | 674.2
495 | 343 | 713.6 | 805.8 | 700.6 | 717.2 | 674.2
496 | 344 | 715.1 | 805.1 | 709.7 | 718.1 | 674.4
497 | 345 | 716.3 | 803.3 | 706.7 | 719.3 | 672.8
498 | 346 | 717.8 | 802.6 | 708.4 | 721.8 | 670.4
499 | 347 | 719.6 | 801.7 | 712.6 | 724.2 | 671.4
500 | 348 | 720.5 | 803.4 | 694.4 | 726.1 | 667.6
501 | 349 | 721.7 | 805 | 682.7 | 728.4 | 664.3
502 | 350 | 723.5 | 805.2 | 679.1 | 730.3 | 662.8
503 | 351 | 725.6 | 803 | 680.8 | 731.9 | 660.9
504 | 352 | 727.1 | 802.4 | 702.2 | 734.1 | 660.6
505 | 353 | 728.4 | 797.3 | 724.6 | 736.6 | 662.6
506 | 354 | 730.3 | 793.4 | 739.1 | 738.9 | 664.9
507 | 355 | 732.7 | 793.9 | 740.5 | 741.5 | 664.5
508 | 356 | 735 | 794.1 | 746.6 | 744.8 | 667.4
509 | 357 | 735.8 | 793.3 | 735.6 | 747.8 | 665.5
510 | 358 | 736.9 | 793.6 | 735.2 | 750.1 | 665.6
511 | 359 | 738.3 | 792.9 | 736.3 | 751.4 | 666.3
512 | 360 | 740.9 | 795 | 733.5 | 752.6 | 666.4
513 | 361 | 741.6 | 794.1 | 719.6 | 754 | 664.3
514 | 362 | 742.1 | 794.9 | 703 | 755.9 | 661.2
515 | 363 | 743.3 | 794.3 | 691 | 756.5 | 660.7
516 | 364 | 745.5 | 794.4 | 692.2 | 758.7 | 661
517 | 365 | 748.1 | 794.4 | 693.4 | 760.4 | 659.5
518 | 366 | 749.8 | 792.9 | 692.2 | 761 | 658.5
519 | 367 | 750.2 | 793 | 672.7 | 762.9 | 654.2
520 | 368 | 751 | 793.4 | 658.1 | 764 | 651.5
521 | 369 | 752.4 | 792.2 | 645.3 | 764.2 | 650.3
522 | 370 | 754.3 | 792.6 | 642.6 | 765.8 | 649.3
523 | 371 | 756.4 | 789.7 | 652.3 | 766.1 | 651.4
524 | 372 | 757.3 | 789.1 | 651.4 | 768.4 | 649.9
525 | 373 | 759.3 | 789.1 | 670.9 | 772.4 | 650.2
526 | 374 | 763.6 | 786.5 | 697.8 | 771.7 | 656.5
527 | 375 | 766.4 | 783.6 | 713 | 773.4 | 656.9
528 | 376 | 768.8 | 781 | 727.4 | 776.2 | 659.6
529 | 377 | 770.6 | 779.6 | 740.2 | 779.4 | 663.5
530 | 378 | 771.8 | 779.1 | 745.8 | 781.8 | 665.4
531 | 379 | 771.9 | 776.4 | 742.4 | 783.4 | 666.5
532 | 380 | 771.9 | 775.4 | 737.3 | 784.5 | 668.7
533 | 381 | 772.1 | 775.3 | 734.7 | 786.1 | 668.8
534 | 382 | 771.9 | 775.2 | 733.6 | 787.3 | 668.2
535 | 383 | 772.6 | 773.8 | 735.2 | 788.2 | 669.9
536 | 384 | 774.5 | 773.9 | 738.9 | 790.1 | 671.8
537 | 385 | 776.5 | 776.2 | 739 | 793 | 671.3
538 | 386 | 780.1 | 778.6 | 744 | 796.4 | 673.2
539 | 387 | 782.9 | 778 | 751.7 | 798.2 | 676.8
540 | 388 | 784.2 | 778 | 760.7 | 799.7 | 679.2
541 | 389 | 785.3 | 778.4 | 775.1 | 801.6 | 680.9
542 | 390 | 786.7 | 777 | 784.1 | 803.4 | 683.2
543 | 391 | 787.2 | 777 | 787 | 805.5 | 684.6
544 | 392 | 788.2 | 776.7 | 798.5 | 807.1 | 689.2
545 | 393 | 788.8 | 775.4 | 798.2 | 808.5 | 693
546 | 394 | 789.6 | 777.3 | 779.8 | 811 | 691.1
547 | 395 | 791.2 | 781.2 | 759.2 | 813.6 | 687.5
548 | 396 | 792.2 | 784.2 | 741 | 815.7 | 683.6
549 | 397 | 792.5 | 786.1 | 722.5 | 816.2 | 679.9
550 | 398 | 792.6 | 784.4 | 706.4 | 815.4 | 676.9
551 | 399 | 792.5 | 781 | 691.4 | 813.6 | 674.2
552 | 400 | 792.2 | 778.3 | 686.1 | 811.9 | 672.5
553 | 401 | 792.7 | 776.8 | 682.2 | 811.6 | 671.4
554 | 402 | 793.8 | 775.1 | 685.1 | 811.9 | 670.9
555 | 403 | 794.2 | 771.7 | 693.4 | 811.4 | 671.3
556 | 404 | 793.3 | 770.7 | 696.4 | 812.1 | 671.4
557 | 405 | 793.2 | 770.6 | 711.1 | 813.3 | 671.5
558 | 406 | 793.3 | 770.8 | 712.1 | 815.5 | 670.8
559 | 407 | 793.7 | 770.3 | 722.8 | 816.8 | 671.2
560 | 408 | 793.4 | 769.7 | 731.4 | 818.3 | 675.7
561 | 409 | 793.7 | 769.1 | 738.6 | 820.4 | 678.3
562 | 410 | 793.8 | 771 | 733.1 | 822.6 | 676.4
563 | 411 | 794.7 | 771.3 | 721.3 | 824.7 | 675.4
564 | 412 | 796.3 | 770.2 | 720.3 | 825.9 | 676.3
565 | 413 | 797.6 | 770.3 | 719.3 | 827.5 | 676.2
566 | 414 | 797.6 | 772.3 | 712.6 | 828.5 | 673.7
567 | 415 | 797.4 | 771.6 | 711.7 | 829.1 | 674.4
568 | 416 | 797.7 | 773.2 | 712.2 | 830.8 | 673.1
569 | 417 | 799.1 | 773.8 | 714.4 | 832.3 | 673.8
570 | 418 | 799.1 | 774.6 | 711.7 | 833.6 | 672.5
571 | 419 | 798.9 | 775.7 | 705.9 | 834.7 | 670.8
572 | 420 | 799 | 773.8 | 720.6 | 834.4 | 672.6
573 | 421 | 800.9 | 774.4 | 728.7 | 836.1 | 676.2
574 | 422 | 802.2 | 774.7 | 726.5 | 838.2 | 675.9
575 | 423 | 803.5 | 775.8 | 735.2 | 840.1 | 676.2
576 | 424 | 805.5 | 776.3 | 740.2 | 842.2 | 679.9
577 | 425 | 806.8 | 776.5 | 734.7 | 844.5 | 678
578 | 426 | 807.6 | 774.4 | 745.9 | 844.7 | 678.3
579 | 427 | 808.7 | 776.2 | 761.7 | 846.5 | 682.3
580 | 428 | 809.6 | 774.7 | 769.3 | 847.8 | 685.6
581 | 429 | 810.9 | 775.8 | 775.5 | 849.2 | 687.1
582 | 430 | 810.8 | 773.8 | 782.7 | 851.3 | 689.6
583 | 431 | 811.2 | 774.3 | 785.2 | 853.3 | 691.8
584 | 432 | 811.5 | 772.9 | 792.4 | 853.4 | 694
585 | 433 | 811.6 | 772.1 | 791.1 | 854.7 | 694.4
586 | 434 | 811.9 | 772.8 | 792.6 | 855.8 | 696.3
587 | 435 | 812.2 | 775.5 | 781.8 | 858.2 | 694.8
588 | 436 | 813.2 | 777.3 | 784.6 | 859.7 | 695.1
589 | 437 | 814.1 | 776.8 | 793.2 | 861.2 | 697.7
590 | 438 | 814.9 | 777.2 | 798.8 | 862.7 | 704.3
591 | 439 | 816.3 | 777.4 | 796.1 | 864.2 | 706.1
592 | 440 | 817 | 776.5 | 797.5 | 865.1 | 708.1
593 | 441 | 817.3 | 777.4 | 795.1 | 865.5 | 709.3
594 | 442 | 817.5 | 778.8 | 795.5 | 865.5 | 714.4
595 | 443 | 817.2 | 778.8 | 792.5 | 865.3 | 715.2
596 | 444 | 817.2 | 779.2 | 797.8 | 865.3 | 718.5
597 | 445 | 817.3 | 776.3 | 800.8 | 865.5 | 722.6
598 | 446 | 817.9 | 775.5 | 797.6 | 866.1 | 722.9
599 | 447 | 819.8 | 776.7 | 797.4 | 867.5 | 722.2
600 | 448 | 821.3 | 775.8 | 794.9 | 868.7 | 722.1
601 | 449 | 821.5 | 776 | 791.8 | 869.8 | 722.4
602 | 450 | 822.1 | 775.7 | 794.2 | 870.5 | 722.2
603 | 451 | 822.4 | 775.6 | 795.3 | 872.1 | 721.7
604 | 452 | 823 | 776.5 | 799.6 | 872.9 | 723.4
605 | 453 | 823.2 | 773.6 | 800 | 873.7 | 724.9
606 | 454 | 823.6 | 773 | 805.2 | 874.7 | 726.2
607 | 455 | 823.2 | 771.3 | 809.4 | 874.7 | 726.6
608 | 456 | 823.8 | 772.5 | 812.2 | 875.8 | 728.8
609 | 457 | 824.5 | 772.7 | 812.9 | 877.1 | 730
610 | 458 | 825.6 | 774.4 | 809.3 | 879 | 729.7
611 | 459 | 826.5 | 775 | 807.5 | 879.9 | 728.9
612 | 460 | 827.4 | 775.6 | 810.5 | 880.5 | 731
613 | 461 | 827.1 | 775.9 | 810.9 | 879.6 | 732.3
614 | 462 | 826.7 | 777 | 814 | 879.1 | 732.4
615 | 463 | 827.2 | 777.3 | 811.2 | 879.5 | 734.6
616 | 464 | 827.7 | 776.6 | 809.5 | 878.8 | 734.3
617 | 465 | 828.4 | 777.8 | 810.5 | 878.3 | 735.3
618 | 466 | 829.7 | 779.3 | 805.1 | 877.7 | 733.6
619 | 467 | 830.3 | 780.4 | 806.1 | 877 | 734.7
620 | 468 | 828.9 | 777.9 | 799.7 | 876 | 734.7
621 | 469 | 828.1 | 776.1 | 794.8 | 874.6 | 732.7
622 | 470 | 828.8 | 777.3 | 795.8 | 874.5 | 733.5
623 | 471 | 830.7 | 778.8 | 791.9 | 873.4 | 731.9
624 | 472 | 833 | 780.3 | 787.1 | 870.5 | 728.5
625 | 473 | 835.5 | 780.3 | 786.6 | 867.3 | 727.5
626 | 474 | 837.6 | 780.3 | 794 | 867.1 | 728.9
627 | 475 | 838 | 781.1 | 800.7 | 867.5 | 732.8
628 | 476 | 838.5 | 781.8 | 801.5 | 868.1 | 732.8
629 | 477 | 838.2 | 781.8 | 800.7 | 867.6 | 733.1
630 | 478 | 838.5 | 780.6 | 803.9 | 867.4 | 734.6
631 | 479 | 838.5 | 780 | 805.1 | 867.8 | 736
632 | 480 | 838.2 | 779.1 | 804.7 | 867.5 | 735.4
633 | 481 | 837.9 | 779 | 805.4 | 867.6 | 734.5
634 | 482 | 837.3 | 778.8 | 805.8 | 866.8 | 733.6
635 | 483 | 837.2 | 779.2 | 808.5 | 867.6 | 737.1
636 | 484 | 837.3 | 780.3 | 808.3 | 869 | 742.6
637 | 485 | 836.7 | 778.9 | 805.8 | 869.2 | 740.6
638 | 486 | 835.8 | 777.6 | 805 | 867.9 | 741.7
639 | 487 | 835.1 | 776.9 | 805.7 | 867.9 | 741.3
640 | 488 | 834.7 | 777.7 | 806.7 | 867.9 | 743.9
641 | 489 | 835.4 | 778.6 | 807.8 | 868.4 | 745.3
642 | 490 | 837 | 780.7 | 809.6 | 868.8 | 746
643 | 491 | 838 | 779.3 | 810.7 | 868.7 | 746.6
644 | 492 | 838.5 | 778.2 | 810.6 | 868.4 | 746.5
645 | 493 | 838.4 | 778.8 | 812.2 | 868 | 748.5
646 | 494 | 837.3 | 777.7 | 809.3 | 867.2 | 748.4
647 | 495 | 837 | 779.6 | 809.3 | 867.1 | 748.5
648 | 496 | 837.1 | 781.1 | 809.1 | 866.9 | 748.8
649 | 497 | 837.2 | 781.6 | 806.6 | 867.5 | 748.4
650 | 498 | 837.8 | 784.2 | 805.9 | 867.9 | 748.3
651 | 499 | 838.2 | 784.8 | 808.7 | 868.4 | 750.9
652 | 500 | 837.4 | 783.2 | 807.5 | 868.1 | 754.1
653 | 501 | 837.3 | 782.7 | 808.3 | 867.8 | 756.5
654 | 502 | 837.4 | 781.1 | 807.4 | 867.3 | 755.7
655 | 503 | 837.8 | 781.3 | 808.9 | 867.2 | 755.5
656 | 504 | 838 | 781.6 | 810.4 | 867.2 | 757.7
657 | 505 | 837.8 | 781.6 | 810 | 867.5 | 759.7
658 | 506 | 837.6 | 782.4 | 809 | 867.1 | 761.5
659 | 507 | 837.5 | 782.3 | 808.1 | 865.9 | 759.5
660 | 508 | 838 | 783.4 | 808.3 | 865.6 | 758.7
661 | 509 | 838.5 | 783.4 | 808.6 | 866 | 759.3
662 | 510 | 838.7 | 784.1 | 808.8 | 866.6 | 760.1
663 | 511 | 838.3 | 784.9 | 808.8 | 866.9 | 759.9
664 | 512 | 837.8 | 786.8 | 806.5 | 866.3 | 757.5
665 | 513 | 837.1 | 788.7 | 805.7 | 864.9 | 756.6
666 | 514 | 837.2 | 786.7 | 806.1 | 865.5 | 758.1
667 | 515 | 837.6 | 785.3 | 805.6 | 865.8 | 756
668 | 516 | 838 | 785.9 | 805.2 | 865.4 | 754.1
669 | 517 | 838.3 | 786.4 | 805.6 | 864.9 | 754.2
670 | 518 | 839.5 | 787 | 806.3 | 864.8 | 754.1
671 | 519 | 840.6 | 786 | 806.4 | 865.8 | 753.1
672 | 520 | 841.8 | 784.7 | 807.8 | 866.5 | 753.6
673 | 521 | 841.5 | 783.8 | 804.3 | 866.7 | 751.3
674 | 522 | 841.8 | 783 | 802.4 | 866.8 | 748.4
675 | 523 | 842.3 | 782.1 | 802.9 | 867.3 | 749
676 | 524 | 842.7 | 781.2 | 802.7 | 866.9 | 747.1
677 | 525 | 843.7 | 783.4 | 802.3 | 867.1 | 745.5
678 | 526 | 844.3 | 784.3 | 803.1 | 867.2 | 745.5
679 | 527 | 844.4 | 785.1 | 803.3 | 867.4 | 749.6
680 | 528 | 844.7 | 785.9 | 804 | 866.9 | 752.7
681 | 529 | 844 | 785.5 | 801.8 | 866.3 | 752.4
682 | 530 | 843.4 | 784.4 | 799.8 | 865.4 | 749.3
683 | 531 | 843.4 | 784.8 | 798.4 | 865.7 | 749.9
684 | 532 | 843.7 | 783.3 | 798 | 864.4 | 747
685 | 533 | 844.2 | 781.3 | 798.5 | 863.8 | 748.2
686 | 534 | 845.1 | 780 | 798.6 | 863.1 | 747.1
687 | 535 | 845.8 | 780.5 | 799.4 | 864 | 752.6
688 | 536 | 845.8 | 780.1 | 800.8 | 863.3 | 756.3
689 | 537 | 845.8 | 778.3 | 800.9 | 862.7 | 758.3
690 | 538 | 845.8 | 777.5 | 800.8 | 861.8 | 757.7
691 | 539 | 846.7 | 778.2 | 801.1 | 861.2 | 756
692 | 540 | 847.7 | 777.5 | 803 | 860.8 | 757.3
693 | 541 | 848.3 | 777.6 | 802.1 | 860.3 | 756.7
694 | 542 | 848.7 | 777.6 | 801.6 | 859.3 | 758.2
695 | 543 | 848.9 | 775 | 799.5 | 857.4 | 754.7
696 | 544 | 849.5 | 770.5 | 796.7 | 855.4 | 748.7
697 | 545 | 850.6 | 769.2 | 798.5 | 855.7 | 748.6
698 | 546 | 851.3 | 769.1 | 800.6 | 857 | 750.8
699 | 547 | 850.7 | 768.6 | 800 | 857.7 | 750.6
700 | 548 | 850.6 | 769.6 | 800.6 | 858 | 753.4
701 | 549 | 850.3 | 770.5 | 801.3 | 858.3 | 754.4
702 | 550 | 849.7 | 770.5 | 801.8 | 858.5 | 755
703 | 551 | 848.6 | 770.6 | 799.4 | 858.1 | 751.3
704 | 552 | 848 | 770.4 | 798.7 | 857.8 | 749.9
705 | 553 | 848.3 | 770.9 | 798.9 | 859 | 750.8
706 | 554 | 848.2 | 771.3 | 798.2 | 859.2 | 750.3
707 | 555 | 848.1 | 770.9 | 797.5 | 859.2 | 749.3
708 | 556 | 848.8 | 770.7 | 796.9 | 859.2 | 748.2
709 | 557 | 849.8 | 769.3 | 794.3 | 858.3 | 743.6
710 | 558 | 851.3 | 767.8 | 795.8 | 857 | 741.5
711 | 559 | 852 | 767.4 | 797.2 | 857.4 | 743.9
712 | 560 | 853 | 768 | 797 | 858.3 | 741.5
713 | 561 | 854.1 | 766.8 | 798.8 | 857.9 | 739.5
714 | 562 | 854.9 | 766.7 | 801.5 | 857.4 | 744
715 | 563 | 855.6 | 765.9 | 802.8 | 856.4 | 745
716 | 564 | 856.9 | 765.4 | 802.3 | 856 | 745.7
717 | 565 | 857.6 | 766.3 | 801.6 | 856.4 | 744.7
718 | 566 | 858.2 | 766.3 | 801.3 | 855.2 | 743.4
719 | 567 | 858.8 | 763.2 | 799.8 | 853 | 739.1
720 | 568 | 859.5 | 760.7 | 798.6 | 850.9 | 734.7
721 | 569 | 860.1 | 761.1 | 798.6 | 851 | 735.6
722 | 570 | 860 | 761.5 | 796.9 | 851.7 | 735.2
723 | 571 | 859.7 | 760.1 | 794.8 | 851.2 | 732
724 | 572 | 859.6 | 757.8 | 792.8 | 849.2 | 728.7
725 | 573 | 859.3 | 753 | 791.1 | 847.3 | 724.6
726 | 574 | 859.2 | 749.6 | 789.4 | 845.6 | 723.4
727 | 575 | 858.8 | 746 | 786.6 | 843.3 | 717.8
728 | 576 | 858.9 | 742.5 | 786.3 | 841.8 | 714.4
729 | 577 | 858.9 | 742 | 786.3 | 842.2 | 712.2
730 | 578 | 858.7 | 742.6 | 787.7 | 842.6 | 711.9
731 | 579 | 858.4 | 743.2 | 789.9 | 844.4 | 715.2
732 | 580 | 858.3 | 745.6 | 790.8 | 845.7 | 717.6
733 | 581 | 858.4 | 748.6 | 792.3 | 846.4 | 717.8
734 | 582 | 858.6 | 752.1 | 793.3 | 847.4 | 717.1
735 | 583 | 858.1 | 752.8 | 790.9 | 847.3 | 714.1
736 | 584 | 858.4 | 754.3 | 792.6 | 847.6 | 713.9
737 | 585 | 858.8 | 758.1 | 794.7 | 848 | 716.1
738 | 586 | 858.2 | 761.1 | 796.9 | 849.2 | 718.6
739 | 587 | 857.1 | 763.4 | 797.8 | 850.2 | 721.9
740 | 588 | 856.6 | 764.1 | 796.6 | 849.6 | 720.5
741 | 589 | 856.3 | 764 | 797.7 | 849.4 | 721.3
742 | 590 | 855.8 | 765.5 | 798.9 | 849.3 | 724.1
743 | 591 | 854.9 | 767.6 | 798.1 | 849.2 | 727.1
744 | 592 | 854.3 | 769.6 | 797.9 | 848.8 | 729.3
745 | 593 | 853.8 | 771.5 | 799.8 | 849 | 733.6
746 | 594 | 853.2 | 773.3 | 800.5 | 848.8 | 735.7
747 | 595 | 852.6 | 773.8 | 800.3 | 848.5 | 737.7
748 | 596 | 851.9 | 774.4 | 799.7 | 848.4 | 740.9
749 | 597 | 851.9 | 776.1 | 800.1 | 847.8 | 741
750 | 598 | 852.4 | 777.5 | 800 | 847.2 | 740.6
751 | 599 | 852.4 | 778.2 | 802 | 847.8 | 745.6
752 | 600 | 851.9 | 778.2 | 803.1 | 847.6 | 748.8
753 | 601 | 851.1 | 778.2 | 803.1 | 846.8 | 750.7
754 | 602 | 850.8 | 779.3 | 803.7 | 846.7 | 752.8
755 | 603 | 851.1 | 779.2 | 805 | 846.7 | 754
756 | 604 | 851.8 | 778.9 | 805.3 | 846.7 | 755.8
757 | 605 | 852.3 | 778.2 | 806.2 | 846.4 | 758.2
758 | 606 | 852.3 | 777 | 806 | 845.8 | 759
759 | 607 | 853.2 | 777 | 807.1 | 846.2 | 755.5
760 | 608 | 854.3 | 776.9 | 807.2 | 846.6 | 755.4
761 | 609 | 855.7 | 774.2 | 803.4 | 844.5 | 748.9
762 | 610 | 857.1 | 773.5 | 803.3 | 843.9 | 746.2
763 | 611 | 858.5 | 772.5 | 805 | 843.6 | 747
764 | 612 | 859.6 | 770.9 | 804 | 843.2 | 745.4
765 | 613 | 860.7 | 768.6 | 802.8 | 842.1 | 741.3
766 | 614 | 861.5 | 766.5 | 803.3 | 841.4 | 739.6
767 | 615 | 862.3 | 765.4 | 803.1 | 841.5 | 739.8
768 | 616 | 862.5 | 762.7 | 801.1 | 840.6 | 736
769 | 617 | 863 | 760.7 | 801.6 | 839.9 | 734.1
770 | 618 | 863.9 | 760.2 | 803.5 | 839.5 | 734.3
771 | 619 | 864.8 | 760.8 | 805 | 839.4 | 734.2
772 | 620 | 865.7 | 764.6 | 805.8 | 840.2 | 735.3
773 | 621 | 866.3 | 767.6 | 805.6 | 840.1 | 732.3
774 | 622 | 866.5 | 770.1 | 807.4 | 840.9 | 733.1
775 | 623 | 866.5 | 772.7 | 809 | 841.4 | 735.1
776 | 624 | 865.8 | 773.8 | 807.8 | 840.8 | 735.4
777 | 625 | 865.4 | 774 | 805 | 840.2 | 732.5
778 | 626 | 864.9 | 775.4 | 802.2 | 839.6 | 730.6
779 | 627 | 864.7 | 775.5 | 800.1 | 839.4 | 728.5
780 | 628 | 864.3 | 773.9 | 799.1 | 839.2 | 726.1
781 | 629 | 864 | 771.1 | 797.7 | 838.8 | 723.8
782 | 630 | 864.4 | 771.5 | 798.5 | 838.6 | 724.8
783 | 631 | 864.5 | 773.3 | 799.3 | 839.1 | 725.3
784 | 632 | 864.3 | 775.8 | 801.3 | 839.8 | 727.8
785 | 633 | 864.3 | 777.4 | 804 | 840.3 | 732.2
786 | 634 | 864.3 | 778.7 | 806.4 | 840 | 735.8
787 | 635 | 864 | 779.8 | 807.7 | 839.4 | 737.7
788 | 636 | 864 | 780.2 | 808.5 | 838.6 | 740.8
789 | 637 | 864.1 | 780.3 | 810.6 | 837.7 | 743.1
790 | 638 | 863.6 | 780.6 | 811.2 | 837.9 | 746.6
791 | 639 | 863.1 | 780.1 | 809.4 | 836.8 | 745.7
792 | 640 | 863.1 | 780.9 | 805.3 | 835 | 741.5
793 | 641 | 863.8 | 778.6 | 802.5 | 833.3 | 736.2
794 | 642 | 864.3 | 776.4 | 802.1 | 833 | 736.3
795 | 643 | 865 | 774 | 800.7 | 832.4 | 735
796 | 644 | 865.2 | 770.9 | 797.2 | 831.2 | 729.8
797 | 645 | 866.1 | 770.3 | 798 | 830.4 | 730.1
798 | 646 | 867 | 768.5 | 798.5 | 829.3 | 729.6
799 | 647 | 868.4 | 767.3 | 799.5 | 828.4 | 728.3
800 | 648 | 868.9 | 766.9 | 801.1 | 828.2 | 729.6
801 | 649 | 868.1 | 768.4 | 803.3 | 829.5 | 735.3
802 | 650 | 866.9 | 770.8 | 802.8 | 830.5 | 734.7
803 | 651 | 865.6 | 774.8 | 801 | 831.4 | 734.2
804 | 652 | 864.9 | 777.3 | 802.8 | 832.1 | 735.5
805 | 653 | 864.1 | 779.2 | 805.6 | 832.8 | 742.1
806 | 654 | 863.5 | 780.2 | 806.5 | 832.8 | 745.2
807 | 655 | 863.5 | 781.3 | 805.8 | 832.9 | 743.9
808 | 656 | 863.7 | 782.5 | 804.2 | 833.1 | 743.2
809 | 657 | 864.3 | 781.2 | 802 | 832.1 | 739.6
810 | 658 | 864.9 | 776.1 | 798.1 | 829.1 | 735.2
811 | 659 | 865.1 | 771.9 | 797.3 | 827 | 733.7
812 | 660 | 865.3 | 769.3 | 797 | 825.4 | 733.6
813 | 661 | 865.2 | 765 | 796.8 | 824.6 | 730.9
814 | 662 | 865 | 761.9 | 798.3 | 824.5 | 731.2
815 | 663 | 864.9 | 760.6 | 798.9 | 824.8 | 731.4
816 | 664 | 864.8 | 758.9 | 797.1 | 823.5 | 728.3
817 | 665 | 864.9 | 757.9 | 797.6 | 824.4 | 729.4
818 | 666 | 865 | 755.3 | 797.7 | 823.1 | 729.1
819 | 667 | 865.4 | 755 | 799.4 | 822.8 | 730.4
820 | 668 | 865.9 | 756.9 | 799.3 | 823.1 | 729.4
821 | 669 | 866 | 757.5 | 799.2 | 823.5 | 728.6
822 | 670 | 865.9 | 760.5 | 798.8 | 824.9 | 729
823 | 671 | 865.5 | 763.1 | 801.2 | 825.6 | 730.2
824 | 672 | 865 | 764.3 | 800.4 | 825.7 | 730.8
825 | 673 | 864.3 | 767.1 | 798 | 826 | 728.9
826 | 674 | 863.3 | 770.2 | 799 | 827.3 | 731.8
827 | 675 | 862 | 773.3 | 798.4 | 827.3 | 732.1
828 | 676 | 861.1 | 775.6 | 798.3 | 827.6 | 731.9
829 | 677 | 860.8 | 776.9 | 798.6 | 828.2 | 732.1
830 | 678 | 861.1 | 777.7 | 798.5 | 828.8 | 731.7
831 | 679 | 861.3 | 777.2 | 799.2 | 829.6 | 731.9
832 | 680 | 861.7 | 776.9 | 802.1 | 830.5 | 737.3
833 | 681 | 861.3 | 776.9 | 803.5 | 831 | 740.4
834 | 682 | 860.8 | 779 | 803.9 | 831.8 | 740.7
835 | 683 | 860.7 | 780.9 | 803.8 | 831.8 | 740.1
836 | 684 | 860.3 | 782.4 | 805.7 | 833.1 | 744
837 | 685 | 860 | 783.2 | 806 | 833.4 | 745.9
838 | 686 | 860.9 | 784.9 | 805.8 | 833.7 | 744.1
839 | 687 | 861.7 | 783.5 | 803.3 | 833.3 | 741.2
840 | 688 | 862.8 | 783.7 | 804.1 | 832.3 | 741
841 | 689 | 864.3 | 784 | 805.5 | 830.7 | 740.8
842 | 690 | 865.8 | 784.9 | 806.9 | 830.1 | 740.6
843 | 691 | 867.1 | 786.8 | 807.3 | 830.6 | 739.9
844 | 692 | 868.2 | 786.6 | 808.6 | 830.8 | 742.3
845 | 693 | 868.4 | 787 | 812.7 | 832 | 746.2
846 | 694 | 868.5 | 785.9 | 814.4 | 831.6 | 750.7
847 | 695 | 868.6 | 787 | 816.8 | 831.1 | 754.4
848 | 696 | 868.9 | 789 | 818.8 | 831.9 | 757.5
849 | 697 | 869.1 | 790.2 | 818.7 | 833 | 756.8
850 | 698 | 869.1 | 791.3 | 817.3 | 833.3 | 755
851 | 699 | 868.1 | 793.1 | 819.4 | 833.6 | 757.8
852 | 700 | 867.3 | 793.7 | 819.6 | 833.4 | 760.1
853 | 701 | 866.9 | 795.3 | 821.1 | 834.2 | 759.8
854 | 702 | 866.7 | 796.5 | 823.1 | 834.1 | 759.6
855 | 703 | 866.8 | 798.5 | 826 | 835.6 | 762.8
856 | 704 | 866.9 | 800.4 | 827.2 | 836.3 | 764
857 | 705 | 866.8 | 800.7 | 827.4 | 837.1 | 764.7
858 | 706 | 867.1 | 802.3 | 826.4 | 837.6 | 766
859 | 707 | 868.2 | 802.8 | 826.2 | 838 | 767.3
860 | 708 | 869.8 | 804.3 | 825.3 | 837.7 | 767.4
861 | 709 | 872.1 | 801.9 | 825.5 | 835.8 | 764.5
862 | 710 | 873.5 | 801 | 828.8 | 836.7 | 767.7
863 | 711 | 874.2 | 800.9 | 831.5 | 838 | 770.5
864 | 712 | 874.8 | 800.3 | 833.4 | 838.6 | 771.3
865 | 713 | 875.7 | 801.1 | 833.8 | 839.1 | 773.5
866 | 714 | 875.8 | 802.1 | 834.3 | 839.9 | 774.2
867 | 715 | 874.1 | 802.7 | 835.1 | 840.7 | 776.9
868 | 716 | 873.4 | 803 | 832.6 | 841.3 | 776.3
869 | 717 | 873 | 803.7 | 831.1 | 841.5 | 775.5
870 | 718 | 873.9 | 805.5 | 833.3 | 841.9 | 778.4
871 | 719 | 875 | 805.3 | 834.5 | 842.2 | 781.2
872 | 720 | 875.5 | 805 | 834.9 | 842.3 | 782.5
873 | 721 | 875.7 | 805.2 | 835.1 | 842.9 | 784.5
874 | 722 | 877.2 | 805.3 | 835 | 842 | 786.1
875 | 723 | 879.6 | 804.1 | 835.6 | 841.3 | 784.6
876 | 724 | 881 | 801.8 | 834.5 | 840.8 | 780.7
877 | 725 | 881.9 | 799 | 833.5 | 841.4 | 779.3
878 | 726 | 883 | 796.9 | 834 | 841.4 | 778.7
879 | 727 | 883.5 | 795 | 834.7 | 841.7 | 779
880 | 728 | 884 | 792.2 | 834.2 | 842.1 | 778
881 | 729 | 884.5 | 791.1 | 832.1 | 843.4 | 776.1
882 | 730 | 884.6 | 791.6 | 831.1 | 844.2 | 776.6
883 | 731 | 884.4 | 793 | 831.6 | 845.3 | 778
884 | 732 | 884.4 | 793.5 | 831 | 846.2 | 776.9
885 | 733 | 884.9 | 790.6 | 827.9 | 844.8 | 773.3
886 | 734 | 885.7 | 787.3 | 825.5 | 843.8 | 769.1
887 | 735 | 886.7 | 786.6 | 826.9 | 844.1 | 770.8
888 | 736 | 886.9 | 788.4 | 831 | 844.5 | 772.1
889 | 737 | 886.5 | 787.9 | 834.2 | 844.3 | 775.5
890 | 738 | 886.2 | 788.5 | 836.3 | 844.6 | 777.7
891 | 739 | 886.3 | 789.1 | 837.5 | 845.2 | 779.6
892 | 740 | 886.4 | 790.5 | 836.2 | 845.6 | 778.9
893 | 741 | 886.6 | 788.3 | 832.4 | 844.4 | 774.3
894 | 742 | 886.3 | 783.4 | 829.8 | 842.5 | 770.2
895 | 743 | 886.6 | 781.2 | 828.1 | 841.3 | 769.2
896 | 744 | 887.5 | 777.7 | 825.7 | 840.2 | 765.1
897 | 745 | 888.3 | 775.3 | 826.2 | 839.5 | 762.5
898 | 746 | 888.5 | 775.6 | 824.9 | 838.6 | 761.4
899 | 747 | 889.3 | 774.1 | 823.1 | 836.9 | 758.2
900 | 748 | 889.9 | 772.1 | 822.3 | 834.9 | 755.4
901 | 749 | 890.5 | 770.8 | 822.1 | 834.4 | 752.9
902 | 750 | 889.9 | 772.7 | 826.1 | 835.6 | 753.9
903 | 751 | 887.9 | 776.8 | 827.7 | 837.6 | 755.2
904 | 752 | 886.1 | 780.5 | 827.1 | 838.5 | 755.8
905 | 753 | 884.1 | 783.7 | 825.5 | 839.5 | 755.2
906 | 754 | 882.3 | 785 | 821.7 | 839.2 | 752.9
907 | 755 | 881.1 | 785.6 | 818.3 | 839.7 | 751
908 | 756 | 880.1 | 786.2 | 816.9 | 840.3 | 750.3
909 | 757 | 880.5 | 787.8 | 816.9 | 840.7 | 750
910 | 758 | 881.4 | 788.4 | 818.4 | 840.8 | 749.9
911 | 759 | 881.8 | 787.6 | 818.9 | 840.9 | 748.4
912 | 760 | 881.9 | 784 | 817.3 | 839.6 | 745.6
913 | 761 | 881.9 | 783.3 | 819.1 | 840.5 | 749.1
914 | 762 | 881.7 | 783 | 821.3 | 840.6 | 749
915 | 763 | 881.6 | 780.7 | 820 | 839.8 | 746.8
916 | 764 | 882 | 776.5 | 816.2 | 837 | 742.6
917 | 765 | 882.4 | 774 | 816.8 | 835.4 | 742.1
918 | 766 | 881.7 | 769.8 | 815.2 | 834.3 | 739.3
919 | 767 | 880.7 | 767.5 | 815.2 | 834.2 | 738.9
920 | 768 | 879.8 | 766.6 | 814.1 | 833.6 | 736.9
921 | 769 | 879.3 | 766.8 | 813.1 | 834.2 | 736.3
922 | 770 | 878 | 768.2 | 811.8 | 834.5 | 736.1
923 | 771 | 877 | 765.7 | 809 | 831.4 | 732.1
924 | 772 | 875.5 | 763.1 | 804.7 | 830.6 | 729.1
925 | 773 | 874.5 | 762.3 | 802.3 | 829.3 | 726.6
926 | 774 | 873.7 | 763.7 | 806.5 | 829.7 | 727.7
927 | 775 | 873.1 | 767.9 | 812.1 | 830.4 | 732.2
928 | 776 | 873.1 | 771.5 | 815 | 831.7 | 734
929 | 777 | 873.6 | 775 | 816.7 | 833.3 | 734.8
930 | 778 | 874 | 778.6 | 820.1 | 834 | 735.8
931 | 779 | 873.5 | 782.2 | 825.9 | 835.5 | 740.8
932 | 780 | 872.8 | 785 | 828.4 | 836.4 | 745.1
933 | 781 | 872.1 | 787.7 | 828.6 | 836.4 | 747
934 | 782 | 872 | 791.8 | 831.3 | 836 | 750
935 | 783 | 872.2 | 794.5 | 832.9 | 837.5 | 751.3
936 | 784 | 874 | 795.7 | 832.2 | 838.5 | 751.2
937 | 785 | 874.5 | 795.7 | 830.8 | 839.6 | 750.1
938 | 786 | 874.2 | 797.4 | 831.5 | 840.2 | 752.5
939 | 787 | 873.6 | 797.4 | 828.9 | 840.5 | 753.6
940 | 788 | 874.5 | 798.7 | 826 | 839.6 | 752.8
941 | 789 | 876 | 799.4 | 825.5 | 840.3 | 753.4
942 | 790 | 877.1 | 799.9 | 826.1 | 841.7 | 752.8
943 | 791 | 878.2 | 797.7 | 823.8 | 841.5 | 750.3
944 | 792 | 879.4 | 797.4 | 824.8 | 842.5 | 749.8
945 | 793 | 880.1 | 796.4 | 822.6 | 842.6 | 748.4
946 | 794 | 880.6 | 792.4 | 819.5 | 842.2 | 744.6
947 | 795 | 881.9 | 790.4 | 823 | 841.8 | 746.9
948 | 796 | 882.5 | 787.8 | 822.4 | 841.4 | 744.2
949 | 797 | 881.9 | 783.1 | 817.7 | 838.8 | 741.1
950 | 798 | 880.1 | 776.4 | 810.2 | 836.1 | 736.2
951 | 799 | 878.1 | 770.2 | 805 | 833.2 | 731.5
952 | 800 | 876.1 | 764.2 | 800 | 830.1 | 727.5
953 | 801 | 873.1 | 756.1 | 790.5 | 825.3 | 721.3
954 | 802 | 870.3 | 750.6 | 784.5 | 822.5 | 717
955 | 803 | 867.7 | 745.3 | 781 | 820.9 | 713.2
956 | 804 | 866.5 | 743.3 | 786.6 | 820.2 | 712.5
957 | 805 | 864.9 | 741.1 | 791.5 | 820.2 | 712.2
958 | 806 | 862.9 | 738 | 792.5 | 819.2 | 710.5
959 | 807 | 860.8 | 735 | 790 | 818.2 | 708
960 | 808 | 859.3 | 734.7 | 787 | 818.9 | 705.9
961 | 809 | 858 | 736.6 | 789 | 818.9 | 705.4
962 | 810 | 857.3 | 738.1 | 791.7 | 820.4 | 705.5
963 | 811 | 858.3 | 741.7 | 798.5 | 821.2 | 708.8
964 | 812 | 859 | 743.8 | 799.7 | 821.2 | 708.1
965 | 813 | 859.4 | 743.8 | 801.2 | 822.4 | 708.2
966 | 814 | 859.3 | 743.4 | 802.3 | 823.4 | 707.1
967 | 815 | 859.5 | 745.1 | 805.8 | 823.5 | 706.8
968 | 816 | 859.1 | 744.9 | 806.9 | 823.2 | 706.9
969 | 817 | 858.5 | 743.8 | 806.2 | 822.6 | 704.3
970 | 818 | 858.8 | 745.9 | 807.7 | 824 | 705.1
971 | 819 | 859.4 | 747.3 | 806.9 | 824.7 | 704.4
972 | 820 | 860.2 | 750.5 | 809.5 | 826 | 706.4
973 | 821 | 861.1 | 754.7 | 815.7 | 827.5 | 710.7
974 | 822 | 861.8 | 758 | 818.8 | 826 | 714.6
975 | 823 | 862.4 | 760.3 | 817.3 | 828.9 | 713.5
976 | 824 | 863.1 | 761.9 | 813.5 | 829.6 | 712.6
977 | 825 | 862.7 | 765 | 815.4 | 828.9 | 715.8
978 | 826 | 863.2 | 769.6 | 814.7 | 831.4 | 717.4
979 | 827 | 863.5 | 773.6 | 814.7 | 831.9 | 717.7
980 | 828 | 862.7 | 774.7 | 818.8 | 834 | 721.3
981 | 829 | 862.4 | 776.9 | 819.8 | 832 | 724.8
982 | 830 | 862.3 | 779.9 | 822.5 | 834.6 | 727.7
983 | 831 | 862.3 | 781.4 | 823 | 838.3 | 729.6
984 | 832 | 862.9 | 783.7 | 824.4 | 836.9 | 733.5
985 | 833 | 864.4 | 787 | 827.2 | 837.3 | 736.4
986 | 834 | 866.3 | 787.4 | 826.2 | 836.9 | 735.4
987 | 835 | 867.9 | 786.7 | 821.5 | 838.3 | 732.8
988 | 836 | 867.8 | 779.8 | 815.4 | 835.4 | 728.3
989 | 837 | 866.7 | 770 | 810.5 | 831.2 | 724.1
990 | 838 | 866.5 | 764.2 | 810.2 | 831.8 | 722.6
991 | 839 | 866.8 | 764.3 | 816 | 831.9 | 726.6
992 | 840 | 867.5 | 767.1 | 817.9 | 833.8 | 727.9
993 | 841 | 868.2 | 771.5 | 818.7 | 835.3 | 728.1
994 | 842 | 868.5 | 775.4 | 821 | 836.8 | 729.7
995 | 843 | 869.2 | 778.5 | 823.2 | 838.6 | 731.8
996 | 844 | 869.9 | 781.6 | 824.3 | 840.2 | 732.1
997 | 845 | 871.3 | 785.1 | 827.8 | 838.9 | 734.6
998 | 846 | 871.8 | 784.2 | 831.9 | 837.9 | 735.7
999 | 847 | 871.4 | 784 | 832.2 | 838.3 | 736
1000 | 848 | 871.8 | 784.5 | 831.8 | 841.5 | 737.6
1001 | 849 | 873 | 782.2 | 826.6 | 835.6 | 734.8
1002 | 850 | 873 | 774.6 | 820.9 | 836.1 | 731.9
1003 | 851 | 872.7 | 770.2 | 822.4 | 833.1 | 730
1004 | 852 | 873.5 | 772.4 | 825.9 | 836.5 | 732.8
1005 | 853 | 874.6 | 775 | 829.9 | 838.2 | 735.1
1006 | 854 | 875.5 | 776.5 | 833.1 | 836.9 | 738.7
1007 | 855 | 876.5 | 776.7 | 834 | 838 | 738.7
1008 | 856 | 877.1 | 777.3 | 834.1 | 837.4 | 739.7
1009 | 857 | 877.8 | 779.2 | 833 | 840.8 | 739.6
1010 | 858 | 879.2 | 780.3 | 826.6 | 837.8 | 735.5
1011 | 859 | 878.6 | 774.8 | 819.4 | 833 | 730.6
1012 | 860 | 877.8 | 769 | 813.4 | 830.9 | 726.4
1013 | 861 | 877 | 764.1 | 809.8 | 831.2 | 723.8
1014 | 862 | 875.3 | 757.6 | 804.5 | 827.3 | 719.6
1015 | 863 | 874.1 | 752.8 | 803.5 | 825.8 | 716.7
1016 | 864 | 874 | 752.6 | 809.6 | 825.9 | 718.7
1017 | 865 | 873.6 | 751.5 | 811.8 | 824.7 | 718.1
1018 | 866 | 871.6 | 748.9 | 807.9 | 821.5 | 715.2
1019 | 867 | 870 | 747.8 | 806 | 820.7 | 713.5
1020 | 868 | 867.4 | 745.2 | 801.6 | 818.3 | 710.8
1021 | 869 | 864.6 | 742.6 | 798.5 | 819.2 | 708.2
1022 | 870 | 864 | 741.7 | 798.1 | 820.9 | 707.8
1023 | 871 | 864.8 | 743.3 | 798.4 | 820 | 706.5
1024 | 872 | 864.2 | 745.4 | 802.2 | 822.1 | 708.7
1025 | 873 | 864.7 | 747.6 | 802.8 | 818.7 | 708.2
1026 | 874 | 862.7 | 743.1 | 795.2 | 814.4 | 703.3
1027 | 875 | 859.6 | 736.4 | 787.7 | 812.5 | 699.6
1028 | 876 | 857.3 | 732.4 | 784 | 809.6 | 696.5
1029 | 877 | 855.2 | 728.4 | 777.2 | 806.6 | 692.7
1030 | 878 | 851.8 | 723.4 | 769.9 | 805.4 | 688.6
1031 | 879 | 850.9 | 723.6 | 768.6 | 804.1 | 687.9
1032 | 880 | 850.2 | 724.1 | 762.8 | 802.9 | 685.1
1033 | 881 | 850.1 | 727.3 | 762.6 | 804.4 | 684.1
1034 | 882 | 849.7 | 729 | 764.6 | 802 | 682.9
1035 | 883 | 850.4 | 732 | 771.4 | 801.4 | 683.2
1036 | 884 | 851.6 | 737.8 | 779.8 | 804 | 687.3
1037 | 885 | 852.3 | 741.3 | 790.2 | 803.8 | 691.7
1038 | 886 | 852.9 | 743.9 | 795.6 | 803.7 | 693.9
1039 | 887 | 853.6 | 745.7 | 793.9 | 803.7 | 694
1040 | 888 | 853.6 | 741.7 | 793.4 | 801.9 | 694.5
1041 | 889 | 854.6 | 739.6 | 795.9 | 802.2 | 694.7
1042 | 890 | 853.8 | 735.7 | 795.8 | 799.8 | 694.4
1043 | 891 | 853.5 | 734.3 | 794.4 | 797.2 | 693.5
1044 | 892 | 852.3 | 730.6 | 787.8 | 794.4 | 690.4
1045 | 893 | 851.3 | 726.7 | 787.7 | 792 | 689.1
1046 | 894 | 851.3 | 725.1 | 790.4 | 791.1 | 689.7
1047 | 895 | 851 | 724.9 | 790.2 | 791.6 | 689.6
1048 | 896 | 849 | 720.9 | 783.9 | 790.9 | 686.3
1049 | 897 | 847.4 | 718.9 | 780.1 | 789.4 | 682.6
1050 | 898 | 846.7 | 717.3 | 782.8 | 789.7 | 681.8
1051 | 899 | 845.2 | 714 | 778.6 | 787.5 | 678.8
1052 | 900 | 844.3 | 712.4 | 778.4 | 787.4 | 676.6
1053 | 901 | 844.8 | 720.2 | 781.4 | 790.9 | 678.7
1054 | 902 | 845.3 | 727.3 | 779.2 | 791.4 | 677.2
1055 | 903 | 846.6 | 736 | 783.4 | 793.4 | 681.1
1056 | 904 | 848.4 | 739.7 | 780.9 | 795.7 | 682
1057 | 905 | 848 | 736.2 | 779.9 | 794 | 681.3
1058 | 906 | 844.6 | 726.8 | 770.6 | 789 | 677.2
1059 | 907 | 838.8 | 715.3 | 761.1 | 782.5 | 672.2
1060 | 908 | 835.9 | 717.2 | 756.4 | 783.1 | 670.3
1061 | 909 | 835.9 | 724.1 | 758.2 | 784.3 | 669.7
1062 | 910 | 835.8 | 723.3 | 762.7 | 784.1 | 670.4
1063 | 911 | 837.1 | 726.9 | 763.1 | 785.6 | 670.9
1064 | 912 | 838.1 | 732.2 | 766 | 787.5 | 671.4
1065 | 913 | 840.5 | 738 | 766.5 | 789.6 | 670.8
1066 | 914 | 840.1 | 738.9 | 757 | 788.6 | 666.3
1067 | 915 | 839.1 | 736.1 | 758 | 787.3 | 665.5
1068 | 916 | 839.1 | 731.3 | 754.8 | 783.6 | 663.6
1069 | 917 | 836.8 | 723 | 745.8 | 781.8 | 659.7
1070 | 918 | 834 | 718 | 743.5 | 780.9 | 657.4
1071 | 919 | 833.2 | 714.6 | 744.7 | 779.8 | 655.8
1072 | 920 | 833.9 | 716.2 | 752.1 | 779.8 | 657.9
1073 | 921 | 836.2 | 726.4 | 761.9 | 783.3 | 660.8
1074 | 922 | 838.3 | 735.8 | 764.6 | 785.8 | 662.3
1075 | 923 | 840.8 | 742.4 | 764.7 | 787.3 | 661.9
1076 | 924 | 840.1 | 738.5 | 762.1 | 785.2 | 660.8
1077 | 925 | 836.9 | 727.4 | 750.3 | 781.2 | 656.8
1078 | 926 | 833.4 | 718 | 743.2 | 777.8 | 652.6
1079 | 927 | 833.5 | 717.9 | 749.6 | 776.3 | 653.4
1080 | 928 | 834.6 | 718.6 | 756.1 | 776.3 | 655.5
1081 | 929 | 835.2 | 717.3 | 754.5 | 776.3 | 654.6
1082 | 930 | 834.8 | 714.2 | 755.3 | 775 | 653.7
1083 | 931 | 834.3 | 709.6 | 760.2 | 774.1 | 654.4
1084 | 932 | 833.6 | 707.4 | 761 | 772.7 | 652.8
1085 | 933 | 833.3 | 705 | 754.6 | 771 | 651
1086 | 934 | 834.6 | 716.5 | 753.6 | 772.6 | 651.4
1087 | 935 | 833.5 | 717.7 | 750.1 | 772.3 | 649.3
1088 | 936 | 830.7 | 712.3 | 743.7 | 770.1 | 646.1
1089 | 937 | 829.8 | 721.3 | 748.4 | 772.1 | 648.9
1090 | 938 | 830.6 | 726.7 | 754.3 | 773.7 | 651.8
1091 | 939 | 829 | 715.7 | 746.4 | 769.5 | 649
1092 | 940 | 824.6 | 703.6 | 738.1 | 765.5 | 646.1
1093 | 941 | 822.9 | 704.1 | 731.2 | 765.1 | 644.5
1094 | 942 | 824.7 | 715.6 | 735.7 | 765.3 | 646
1095 | 943 | 827.3 | 723.6 | 736.8 | 766.3 | 646.1
1096 | 944 | 829.9 | 729.3 | 745 | 767.9 | 648
1097 | 945 | 832.4 | 739 | 757.9 | 770.4 | 651.7
1098 | 946 | 833.5 | 752.4 | 767.8 | 774 | 655.6
1099 | 947 | 834.4 | 761.5 | 768.6 | 775.8 | 657
1100 | 948 | 832.6 | 752.4 | 758.9 | 775.2 | 654.2
1101 | 949 | 826.8 | 740.2 | 745.3 | 770 | 650.9
1102 | 950 | 823.7 | 736.5 | 739.4 | 769 | 649.7
1103 | 951 | 824.3 | 745.1 | 740 | 770 | 650
1104 | 952 | 827 | 752.3 | 737.4 | 773 | 648.7
1105 | 953 | 827.5 | 758.2 | 733.9 | 772.8 | 648
1106 | 954 | 827.7 | 761.4 | 735.2 | 772.9 | 649
1107 | 955 | 824.4 | 744.1 | 727.8 | 769.3 | 645.5
1108 | 956 | 819.5 | 730.9 | 720.8 | 765.8 | 643.3
1109 | 957 | 814.7 | 722.8 | 716.6 | 763.2 | 640.2
1110 | 958 | 813.9 | 722.2 | 718.7 | 762.6 | 639.6
1111 | 959 | 814.2 | 716.3 | 722.2 | 762.1 | 638.9
1112 | 960 | 814.3 | 706.2 | 721.2 | 760.3 | 637.2
1113 | 961 | 815 | 703.4 | 731.4 | 759.8 | 638
1114 | 962 | 818.1 | 712.4 | 735.4 | 760.7 | 639.8
1115 | 963 | 819.2 | 711.5 | 740.1 | 760.2 | 638.8
1116 | 964 | 819.7 | 711.8 | 749.5 | 761 | 640
1117 | 965 | 822 | 731.8 | 755.5 | 764.5 | 643.2
1118 | 966 | 824.8 | 747.9 | 761.2 | 767.5 | 646.9
1119 | 967 | 826.9 | 754 | 764.7 | 769.8 | 648
1120 | 968 | 825.5 | 745 | 755 | 770.2 | 645.1
1121 | 969 | 824 | 741 | 750.2 | 769.7 | 643.3
1122 | 970 | 823.3 | 744.5 | 752.8 | 769.5 | 645.2
1123 | 971 | 822.9 | 748.7 | 744.4 | 769.9 | 643.6
1124 | 972 | 822.1 | 754.6 | 738 | 771.1 | 642.2
1125 | 973 | 823 | 765.1 | 734.9 | 771.8 | 643.5
1126 | 974 | 824.6 | 769 | 742.5 | 771 | 645.1
1127 | 975 | 828.5 | 776.2 | 748.9 | 773.6 | 648
1128 | 976 | 830.5 | 779.3 | 753.1 | 775.7 | 649.3
1129 | 977 | 829.6 | 776.6 | 751.1 | 776 | 649.1
1130 | 978 | 830.5 | 782.9 | 748.8 | 778.1 | 650.1
1131 | 979 | 830 | 785.2 | 749 | 778.8 | 650.9
1132 | 980 | 829 | 789.2 | 739.7 | 780.1 | 649.5
1133 | 981 | 829.1 | 795.4 | 741.9 | 781.7 | 650.3
1134 | 982 | 829.5 | 794.6 | 745.1 | 782.2 | 652.2
1135 | 983 | 830.3 | 795.3 | 752.6 | 783.6 | 654.3
1136 | 984 | 832.2 | 796 | 749.6 | 784.7 | 654.4
1137 | 985 | 832.8 | 788.8 | 740.6 | 784.7 | 652.7
1138 | 986 | 829.9 | 776.1 | 734.1 | 782 | 650.1
1139 | 987 | 828.1 | 770 | 729 | 780.9 | 648.2
1140 | 988 | 825.3 | 762.6 | 725.2 | 778.2 | 646
1141 | 989 | 821 | 746.2 | 716.4 | 774.9 | 642.6
1142 | 990 | 818.9 | 735.4 | 718.6 | 773.8 | 641.6
1143 | 991 | 821.1 | 745.8 | 725.1 | 774.2 | 643.4
1144 | 992 | 822 | 754.7 | 724.5 | 774.5 | 642.4
1145 | 993 | 822.8 | 754.4 | 719.4 | 774 | 641.6
1146 | 994 | 817.7 | 735.3 | 701.1 | 769.3 | 637.3
1147 | 995 | 811.1 | 722.5 | 683.9 | 765.2 | 633.2
1148 | 996 | 804.6 | 706.7 | 674.1 | 759.8 | 630.1
1149 | 997 | 802 | 704 | 673.4 | 758.2 | 629.1
1150 | 998 | 803.4 | 713.3 | 676.6 | 758.1 | 629.1
1151 | 999 | 801.9 | 714.9 | 665.1 | 757.4 | 626.9
1152 | 1000 | 796.7 | 705.7 | 656.7 | 755.7 | 623.9
1153 | 1001 | 792.9 | 715 | 658.6 | 756.4 | 624.3
1154 | 1002 | 790.7 | 725.9 | 659.5 | 757.5 | 623.8
1155 | 1003 | 789.6 | 728.8 | 661 | 757.8 | 623.6
1156 | 1004 | 787.2 | 722.5 | 657.7 | 757.9 | 622.4
1157 | 1005 | 786.4 | 720.7 | 667.6 | 757.8 | 622
1158 | 1006 | 791.6 | 741.3 | 694.8 | 759.6 | 626
1159 | 1007 | 798.1 | 759.1 | 722.5 | 762.3 | 631.5
1160 | 1008 | 804.3 | 773 | 732.4 | 765.4 | 634
1161 | 1009 | 807.9 | 783.2 | 735.1 | 767.8 | 635
1162 | 1010 | 810 | 792.6 | 735.4 | 769.1 | 636
1163 | 1011 | 811.2 | 799.3 | 746.8 | 771.8 | 640.5
1164 | 1012 | 812.7 | 800.4 | 757.2 | 774.7 | 644.4
1165 | 1013 | 815.4 | 803.7 | 763.4 | 778 | 648.2
1166 | 1014 | 818.1 | 805.7 | 776.2 | 779.8 | 653.7
1167 | 1015 | 821.7 | 813.8 | 784.9 | 782.4 | 657.3
1168 | 1016 | 824.5 | 810.1 | 774.9 | 782.9 | 656.9
1169 | 1017 | 825.5 | 802.2 | 774.9 | 783.7 | 657.1
1170 | 1018 | 828.2 | 810.4 | 772.8 | 786.1 | 660
1171 | 1019 | 830.3 | 816.2 | 764 | 787.5 | 661.3
1172 | 1020 | 831.4 | 815.7 | 753 | 787.1 | 660.2
1173 | 1021 | 834.1 | 818.8 | 748.6 | 788.1 | 661
1174 | 1022 | 833.7 | 805 | 738.1 | 786.1 | 657.8
1175 | 1023 | 830.1 | 785.2 | 726.3 | 782.7 | 654.8
1176 | 1024 | 826.8 | 773.2 | 726.1 | 781.2 | 653.1
1177 | 1025 | 826.4 | 771.1 | 741 | 780.9 | 655
1178 | 1026 | 826.2 | 762.3 | 746.9 | 779 | 655.1
1179 | 1027 | 824.7 | 752.6 | 748.3 | 776.9 | 653
1180 | 1028 | 824.8 | 748.3 | 752.6 | 776.4 | 653.4
1181 | 1029 | 826 | 754.8 | 743 | 776.2 | 651.6
1182 | 1030 | 828.4 | 760.5 | 751 | 777 | 652.4
1183 | 1031 | 832.6 | 775 | 770.9 | 779.6 | 655.9
1184 | 1032 | 835.6 | 783.8 | 781.9 | 782.6 | 660.9
1185 | 1033 | 837.9 | 794.5 | 776.5 | 785.3 | 661.6
1186 | 1034 | 838.5 | 801.6 | 758.8 | 785.8 | 660.1
1187 | 1035 | 838.6 | 795 | 749.7 | 784.8 | 657.4
1188 | 1036 | 840.2 | 796.2 | 759.6 | 785.3 | 659.9
1189 | 1037 | 840.5 | 790.2 | 752.6 | 785.4 | 658.5
1190 | 1038 | 837.5 | 776 | 745.4 | 782.7 | 655.9
1191 | 1039 | 835.4 | 776 | 742.3 | 782.2 | 654.9
1192 | 1040 | 833.9 | 773.9 | 743.4 | 781.5 | 654.4
1193 | 1041 | 831.4 | 767.8 | 752.7 | 779.9 | 655.2
1194 | 1042 | 834.4 | 785.8 | 761.4 | 781.9 | 658.8
1195 | 1043 | 836.4 | 793.6 | 747 | 783.5 | 658.2
1196 | 1044 | 839.2 | 801.4 | 751.3 | 784.4 | 659.3
1197 | 1045 | 841.7 | 806 | 758.3 | 785.8 | 661
1198 | 1046 | 842.8 | 809.1 | 758.5 | 786.8 | 659.2
1199 | 1047 | 844 | 812 | 769.5 | 788.7 | 661
1200 | 1048 | 844.7 | 815 | 782.5 | 790.6 | 667
1201 | 1049 | 845.5 | 815.9 | 794.9 | 792.9 | 673.5
1202 | 1050 | 846.2 | 826.6 | 787.7 | 795.1 | 675.2
1203 | 1051 | 841.9 | 807.8 | 756.7 | 791 | 670.2
1204 | 1052 | 837.6 | 794.5 | 750.2 | 789.2 | 668.9
1205 | 1053 | 837.3 | 790.1 | 744.7 | 788.5 | 667.9
1206 | 1054 | 837.6 | 786.8 | 731.7 | 786.9 | 664.8
1207 | 1055 | 836.2 | 790.7 | 728.5 | 787.4 | 663.3
1208 | 1056 | 836 | 797.9 | 734.3 | 788.6 | 665.2
1209 | 1057 | 838 | 804 | 755.9 | 790.3 | 668.7
1210 | 1058 | 839.1 | 794.6 | 738 | 788.5 | 665.8
1211 | 1059 | 836.8 | 775.5 | 723.2 | 784.9 | 661.6
1212 | 1060 | 830.8 | 755 | 703.5 | 779.7 | 657.7
1213 | 1061 | 826.7 | 746 | 692.8 | 778.1 | 654.9
1214 | 1062 | 825.4 | 746.7 | 692.2 | 777.9 | 653.7
1215 | 1063 | 828.5 | 763.7 | 716.5 | 778.6 | 657.1
1216 | 1064 | 832 | 775.8 | 738 | 780.1 | 659.3
1217 | 1065 | 835.5 | 788.5 | 750.7 | 782.6 | 662.8
1218 | 1066 | 839.2 | 798.2 | 746.7 | 785 | 663.7
1219 | 1067 | 842.5 | 805.4 | 767.7 | 787.1 | 666.8
1220 | 1068 | 845.9 | 806.2 | 775.2 | 788.2 | 669.3
1221 | 1069 | 848.4 | 810.4 | 774.6 | 789.8 | 669.3
1222 | 1070 | 847.2 | 802 | 765.9 | 788.5 | 667.5
1223 | 1071 | 844.8 | 796.6 | 754.7 | 788.2 | 666.3
1224 | 1072 | 845 | 805.8 | 757 | 790.2 | 667.3
1225 | 1073 | 846.7 | 816.2 | 755.1 | 791.6 | 667.6
1226 | 1074 | 849.2 | 823.4 | 768.6 | 792.6 | 670.5
1227 | 1075 | 848.8 | 809.5 | 754.7 | 790.2 | 667.4
1228 | 1076 | 846.2 | 794.9 | 743.4 | 788.5 | 664.7
1229 | 1077 | 844.2 | 783.6 | 742 | 786.3 | 663.2
1230 | 1078 | 841.2 | 771.3 | 744.6 | 784.8 | 663.4
1231 | 1079 | 843 | 782.1 | 747.5 | 785.1 | 665
1232 | 1080 | 845 | 787.8 | 742.7 | 785.6 | 662.8
1233 | 1081 | 843.4 | 785 | 737.5 | 783.6 | 660.3
1234 | 1082 | 838.6 | 768.2 | 730.9 | 780.5 | 658.7
1235 | 1083 | 836 | 765 | 733.4 | 780.2 | 659.4
1236 | 1084 | 838.5 | 780.1 | 747.8 | 783.8 | 662.6
1237 | 1085 | 841.3 | 792.8 | 766.5 | 787.4 | 665.5
1238 | 1086 | 842.9 | 788.9 | 770.1 | 788.4 | 664.1
1239 | 1087 | 843.8 | 778.7 | 769.8 | 786 | 663.2
1240 | 1088 | 845.7 | 782.6 | 765.7 | 784.7 | 663.4
1241 | 1089 | 844.4 | 773.3 | 737.3 | 781.2 | 658.2
1242 | 1090 | 843 | 766.1 | 728.8 | 780 | 655.8
1243 | 1091 | 845.2 | 778.7 | 745.5 | 780.8 | 659.7
1244 | 1092 | 847 | 793.2 | 753 | 783.4 | 661.7
1245 | 1093 | 847.9 | 804 | 756 | 784.6 | 662.1
1246 | 1094 | 849.5 | 809 | 756.3 | 785.7 | 662.6
1247 | 1095 | 848.1 | 793.4 | 742.6 | 783.3 | 660.3
1248 | 1096 | 846.5 | 783.7 | 735.2 | 780.8 | 657.9
1249 | 1097 | 846.5 | 782.3 | 747.2 | 780.5 | 659
1250 | 1098 | 846.9 | 777.8 | 749.2 | 779.8 | 659.9
1251 | 1099 | 840.8 | 755.1 | 722.2 | 774.9 | 654.7
1252 | 1100 | 836.6 | 741.8 | 713.4 | 771.4 | 651.9
1253 | 1101 | 837.6 | 748.7 | 736.4 | 771.1 | 654.5
1254 | 1102 | 841.1 | 769.3 | 765.2 | 775.3 | 662.1
1255 | 1103 | 842.4 | 789.1 | 772.9 | 780.3 | 664
1256 | 1104 | 846 | 803.8 | 783.4 | 784.1 | 664.8
1257 | 1105 | 849 | 801.3 | 790.8 | 784.1 | 666.2
1258 | 1106 | 850.7 | 798.4 | 799.4 | 785.6 | 666.1
1259 | 1107 | 851 | 784.7 | 793.7 | 783.3 | 666.4
1260 | 1108 | 851.6 | 790.3 | 789.3 | 782.4 | 665.5
1261 | 1109 | 848.3 | 771.8 | 757.6 | 779.2 | 660.8
1262 | 1110 | 841.4 | 753.4 | 736 | 775.2 | 657.2
1263 | 1111 | 835.8 | 739.7 | 710.7 | 771.5 | 653
1264 | 1112 | 830.8 | 725.3 | 717.4 | 768.5 | 652.3
1265 | 1113 | 828.1 | 723.3 | 719.8 | 766.9 | 650.8
1266 | 1114 | 824.4 | 712.9 | 710.8 | 764.4 | 649
1267 | 1115 | 823.9 | 710.4 | 703.7 | 762.6 | 647.6
1268 | 1116 | 824.1 | 712.8 | 692.9 | 762.2 | 646
1269 | 1117 | 824.7 | 715.2 | 721.8 | 761.6 | 647
1270 | 1118 | 827 | 722.9 | 739 | 760.8 | 650.3
1271 | 1119 | 829.3 | 725.1 | 755.1 | 760.5 | 656
1272 | 1120 | 830 | 720 | 768.2 | 759.9 | 659.3
1273 | 1121 | 832.5 | 734.4 | 774.7 | 761.5 | 660.2
1274 | 1122 | 835.3 | 753.9 | 762.7 | 763.4 | 659.5
1275 | 1123 | 836.4 | 754.9 | 758.9 | 763 | 659.2
1276 | 1124 | 837.6 | 771.2 | 778.9 | 765.9 | 665.7
1277 | 1125 | 840 | 784.5 | 799.7 | 769.5 | 671.3
1278 | 1126 | 843.8 | 794 | 809.6 | 772.6 | 675.7
1279 | 1127 | 846.6 | 791.5 | 803.4 | 773 | 677.5
1280 | 1128 | 848 | 792 | 778.1 | 772 | 675.7
1281 | 1129 | 849.2 | 792.2 | 771.1 | 770.9 | 676.9
1282 | 1130 | 850.8 | 803.8 | 792.2 | 773.7 | 681.5
1283 | 1131 | 851.3 | 809.6 | 788 | 776.7 | 682.4
1284 | 1132 | 850.8 | 817.1 | 785.9 | 779.7 | 681.9
1285 | 1133 | 853.1 | 824.6 | 808.8 | 782.7 | 687.1
1286 | 1134 | 854.2 | 824.4 | 823.2 | 786 | 691.3
1287 | 1135 | 855.7 | 828.1 | 817.1 | 789.3 | 693.3
1288 | 1136 | 857.8 | 835.6 | 817.1 | 792.6 | 695.4
1289 | 1137 | 859.2 | 849.1 | 803.9 | 794.2 | 695.2
1290 | 1138 | 859.3 | 838.9 | 784.1 | 793.7 | 691.6
1291 | 1139 | 857 | 821 | 763.1 | 790.1 | 687.9
1292 | 1140 | 854.6 | 803.4 | 755.8 | 786.7 | 686.5
1293 | 1141 | 851.2 | 782.3 | 740.9 | 783.6 | 683.5
1294 | 1142 | 848.3 | 777.4 | 738.1 | 782.2 | 681.2
1295 | 1143 | 849.5 | 795.1 | 764.8 | 784.3 | 683.8
1296 | 1144 | 852.6 | 806 | 764.4 | 788.1 | 685.9
1297 | 1145 | 852.5 | 800.4 | 738.1 | 788.8 | 680.2
1298 | 1146 | 853.6 | 800.9 | 762 | 788.6 | 682.2
1299 | 1147 | 855.2 | 811.6 | 785.8 | 791.7 | 687.9
1300 | 1148 | 856 | 820 | 786.7 | 794.5 | 688.8
1301 | 1149 | 855.4 | 823 | 770 | 795.8 | 685.4
1302 | 1150 | 855.9 | 827.5 | 768.5 | 797.7 | 684.1
1303 | 1151 | 857.1 | 830.8 | 779 | 799.1 | 684.4
1304 | 1152 | 858.6 | 827.1 | 781 | 798.4 | 684.7
1305 | 1153 | 856.8 | 813.9 | 762.5 | 796.4 | 682
1306 | 1154 | 856.6 | 814.8 | 762.5 | 795.8 | 681.1
1307 | 1155 | 854.9 | 801.5 | 741.9 | 792.5 | 678.2
1308 | 1156 | 853.6 | 792.3 | 751 | 789.7 | 678.3
1309 | 1157 | 850.9 | 779.1 | 738.6 | 786.6 | 675.7
1310 | 1158 | 844.5 | 759.5 | 710.4 | 781.8 | 669.8
1311 | 1159 | 838.8 | 744.6 | 689.5 | 778.8 | 665.2
1312 | 1160 | 837.4 | 746.9 | 686.2 | 779.5 | 663.4
1313 | 1161 | 840.6 | 765.6 | 700.4 | 781.6 | 663.2
1314 | 1162 | 844.7 | 780 | 730 | 784 | 668.3
1315 | 1163 | 846.7 | 782 | 737.1 | 785 | 666.9
1316 | 1164 | 849.4 | 797.7 | 754.6 | 787.4 | 668.6
1317 | 1165 | 851 | 799.8 | 768.7 | 788.8 | 669.7
1318 | 1166 | 850.3 | 788.5 | 770.4 | 787.7 | 669.3
1319 | 1167 | 849.9 | 788.6 | 783.8 | 788.3 | 673
1320 | 1168 | 851.4 | 797.6 | 779.1 | 791.5 | 674.5
1321 | 1169 | 851.6 | 798.8 | 763.9 | 790.8 | 672.7
1322 | 1170 | 849.5 | 786.6 | 751.8 | 789 | 672.1
1323 | 1171 | 846.7 | 774.2 | 739.5 | 785.5 | 670
1324 | 1172 | 843.5 | 765.1 | 718.9 | 781.8 | 666.5
1325 | 1173 | 842.4 | 756 | 723.9 | 779 | 666.2
1326 | 1174 | 845.9 | 770.7 | 746 | 781.4 | 668.9
1327 | 1175 | 848 | 781 | 748 | 782.9 | 667.6
1328 | 1176 | 849 | 785 | 733.3 | 783.6 | 664.9
1329 | 1177 | 846.8 | 779 | 710 | 782.3 | 661.6
1330 | 1178 | 844.4 | 767.2 | 704.8 | 780.6 | 659
1331 | 1179 | 844.2 | 763.9 | 705.7 | 779.4 | 658.5
1332 | 1180 | 844.9 | 762.2 | 700.1 | 778.1 | 657.4
1333 | 1181 | 842 | 749.4 | 690.5 | 774 | 653.6
1334 | 1182 | 841.4 | 750.1 | 699.8 | 773.2 | 654.6
1335 | 1183 | 841.6 | 755.6 | 710.9 | 772.7 | 654.7
1336 | 1184 | 840.9 | 759.5 | 727.9 | 774 | 653.9
1337 | 1185 | 842 | 778.6 | 750.7 | 776.7 | 656.9
1338 | 1186 | 844.5 | 788.2 | 735.4 | 778.2 | 655.1
1339 | 1187 | 845.6 | 786.5 | 717.9 | 779.1 | 653.6
1340 | 1188 | 842 | 774.3 | 705.9 | 777 | 651.9
1341 | 1189 | 836.5 | 764.9 | 688 | 775 | 649.4
1342 | 1190 | 835.1 | 766 | 680.5 | 774.7 | 647.8
1343 | 1191 | 834.8 | 767 | 673.1 | 774.2 | 646.8
1344 | 1192 | 833.6 | 765.1 | 677.1 | 773.2 | 646
1345 | 1193 | 834.4 | 769.4 | 683.1 | 773 | 645.1
1346 | 1194 | 838.7 | 791.8 | 704.5 | 774.6 | 647.5
1347 | 1195 | 841.2 | 803.7 | 706.3 | 776.4 | 649.6
1348 | 1196 | 838 | 792.5 | 701 | 775.6 | 646.5
1349 | 1197 | 835.7 | 780.4 | 699 | 775.6 | 646
1350 | 1198 | 837.9 | 798.7 | 697.9 | 779.8 | 646.5
1351 | 1199 | 841.2 | 810.5 | 717.8 | 782.6 | 649.4
1352 | 1200 | 840.5 | 805.1 | 715.1 | 782.3 | 649.2
1353 | 1201 | 836.8 | 793.3 | 710.3 | 779.6 | 646.8
1354 | 1202 | 834.3 | 782.3 | 698.3 | 778.2 | 645.6
1355 | 1203 | 831.7 | 770.8 | 689 | 776.2 | 644.1
1356 | 1204 | 832.6 | 778.6 | 700.8 | 776.1 | 644.1
1357 | 1205 | 837.4 | 803.4 | 714.5 | 779.9 | 648.1
1358 | 1206 | 837.9 | 826.7 | 718.9 | 783.2 | 650.4
1359 | 1207 | 839.9 | 839.3 | 741.8 | 786.5 | 654.5
1360 | 1208 | 843.7 | 843 | 758.1 | 790.3 | 658.8
1361 | 1209 | 847.4 | 850.6 | 770.6 | 794.2 | 660.5
1362 | 1210 | 850.4 | 858.2 | 766.7 | 798.1 | 662.1
1363 | 1211 | 850.6 | 859.4 | 768.9 | 800.3 | 665
1364 | 1212 | 853.4 | 868 | 785.9 | 803.3 | 668
1365 | 1213 | 854.4 | 865.1 | 800 | 805.2 | 671
1366 | 1214 | 854.2 | 862.3 | 806.7 | 805.5 | 673.1
1367 | 1215 | 854.9 | 874.5 | 785.3 | 806.9 | 671.5
1368 | 1216 | 855.4 | 861 | 773.3 | 806.2 | 669
1369 | 1217 | 852.9 | 839.7 | 742.5 | 802.3 | 665.1
1370 | 1218 | 850.2 | 817.9 | 731.8 | 797.4 | 662.8
1371 | 1219 | 853.1 | 825.4 | 761.5 | 799.1 | 667.1
1372 | 1220 | 856.8 | 837.2 | 791.2 | 803.2 | 673.7
1373 | 1221 | 858.7 | 840.9 | 810.6 | 806.1 | 679.9
1374 | 1222 | 860.2 | 849.2 | 798.7 | 807.7 | 682.2
1375 | 1223 | 862.8 | 861.8 | 803.6 | 810.3 | 682.8
1376 | 1224 | 864 | 865.8 | 807.6 | 810.1 | 685.7
1377 | 1225 | 864.2 | 851 | 797.6 | 808.1 | 685.3
1378 | 1226 | 865.4 | 851.2 | 781.4 | 808.7 | 683.4
1379 | 1227 | 867.1 | 855 | 776.1 | 809.7 | 682.8
1380 | 1228 | 869.1 | 850.3 | 776.7 | 810.7 | 682.7
1381 | 1229 | 869 | 838.5 | 784.2 | 809.7 | 684.9
1382 | 1230 | 869.5 | 837.8 | 813.6 | 810.4 | 690.6
1383 | 1231 | 872 | 841.7 | 831.1 | 813.5 | 696.1
1384 | 1232 | 872.9 | 835.1 | 820 | 813.6 | 695.9
1385 | 1233 | 873.4 | 827 | 831.3 | 812.2 | 699.1
1386 | 1234 | 872.1 | 817.3 | 835.5 | 812 | 702
1387 | 1235 | 872.6 | 818 | 828.8 | 812.7 | 701.1
1388 | 1236 | 874.2 | 828.3 | 823.2 | 814.2 | 700.2
1389 | 1237 | 872.6 | 818.8 | 804.5 | 813.2 | 700.8
1390 | 1238 | 873.7 | 825.2 | 804.3 | 813.3 | 702.3
1391 | 1239 | 873.8 | 833.1 | 796 | 814.4 | 701.1
1392 | 1240 | 873.9 | 835.4 | 810.7 | 815.7 | 705
1393 | 1241 | 872 | 834.8 | 824.6 | 816.2 | 709.4
1394 | 1242 | 870.8 | 833.5 | 834 | 816.3 | 712.6
1395 | 1243 | 872.9 | 849 | 829.4 | 816.7 | 712.2
1396 | 1244 | 868.4 | 854.3 | 785.8 | 816.9 | 707.4
1397 | 1245 | 862.2 | 826.1 | 749.2 | 811.8 | 702.6
1398 | 1246 | 858.7 | 811.8 | 742 | 806.8 | 699.7
1399 | 1247 | 862.6 | 825.6 | 749.7 | 808.3 | 699.7
1400 | 1248 | 865.5 | 838.9 | 762.7 | 810.7 | 700.8
1401 | 1249 | 863.8 | 837.9 | 751.6 | 810 | 697.2
1402 | 1250 | 867.6 | 842.9 | 770.6 | 812.9 | 698.4
1403 | 1251 | 870.7 | 852.3 | 784.1 | 814.3 | 699.7
1404 | 1252 | 873.2 | 866.1 | 781.1 | 815.6 | 698
1405 | 1253 | 870.6 | 852.6 | 752.4 | 813.2 | 693.9
1406 | 1254 | 862.6 | 816.2 | 732 | 806.8 | 689.2
1407 | 1255 | 857.9 | 788.7 | 739.1 | 801.9 | 688.1
1408 | 1256 | 857.3 | 779.8 | 752.8 | 798.4 | 687.2
1409 | 1257 | 860.9 | 785.4 | 764.7 | 798.8 | 687.9
1410 | 1258 | 862.1 | 783.4 | 763.4 | 798.2 | 685.8
1411 | 1259 | 857.6 | 761.8 | 734.5 | 793.8 | 681.8
1412 | 1260 | 853.7 | 747.7 | 738.5 | 790.4 | 681
1413 | 1261 | 848.7 | 743.1 | 711.8 | 786.8 | 677.5
1414 | 1262 | 846.9 | 745.1 | 707 | 784.6 | 675.8
1415 | 1263 | 843 | 734.9 | 705.3 | 780.7 | 673.4
1416 | 1264 | 844.1 | 740.9 | 718.3 | 779.4 | 672.6
1417 | 1265 | 844.4 | 744.9 | 714.6 | 778.3 | 670.7
1418 | 1266 | 838.6 | 736.7 | 687.9 | 773.8 | 665.8
1419 | 1267 | 833.5 | 724.7 | 661.3 | 770.1 | 662.6
1420 | 1268 | 834.3 | 735.2 | 659.1 | 769.3 | 660.4
1421 | 1269 | 839.3 | 763.8 | 670.6 | 772 | 663
1422 | 1270 | 842.1 | 784.2 | 657.9 | 773.6 | 661.9
1423 | 1271 | 840.1 | 788.9 | 651.8 | 774.1 | 660.5
1424 | 1272 | 841.5 | 803.8 | 662.9 | 775.7 | 662.4
1425 | 1273 | 846.5 | 816.6 | 666.3 | 779.6 | 663.1
1426 | 1274 | 840.5 | 794.1 | 647.1 | 776.2 | 658.2
1427 | 1275 | 830.4 | 764.4 | 626.2 | 768.8 | 653.9
1428 | 1276 | 825.8 | 754.1 | 619.2 | 766.3 | 651.5
1429 | 1277 | 826.9 | 773 | 623.7 | 768.3 | 651.9
1430 | 1278 | 830.9 | 795.8 | 641.7 | 771.9 | 653
1431 | 1279 | 835.8 | 813.6 | 654.4 | 775.4 | 655.6
1432 | 1280 | 841.2 | 828.2 | 667.8 | 779.6 | 657.8
1433 | 1281 | 846.8 | 835.3 | 690.5 | 783.1 | 657.7
1434 | 1282 | 849.3 | 843 | 716.1 | 787 | 661
1435 | 1283 | 850.2 | 847.9 | 729 | 789.4 | 663.5
1436 | 1284 | 851.4 | 853.4 | 730.4 | 791.6 | 662.6
1437 | 1285 | 854.1 | 853.1 | 741.1 | 793.4 | 662.8
1438 | 1286 | 852.1 | 835.8 | 726.5 | 790.6 | 660
1439 | 1287 | 849 | 824.7 | 717.3 | 788.9 | 658.9
1440 | 1288 | 848.1 | 815.5 | 710.9 | 787 | 658.1
1441 | 1289 | 850 | 820.5 | 707.5 | 788.9 | 658.3
1442 | 1290 | 854 | 831.3 | 711.4 | 789.6 | 659
1443 | 1291 | 856.3 | 834.7 | 734.1 | 790.4 | 660.4
1444 | 1292 | 859.2 | 844.1 | 758 | 794.2 | 665.8
1445 | 1293 | 861.3 | 851.7 | 760.9 | 796.4 | 665.8
1446 | 1294 | 862 | 851.1 | 766.2 | 796.1 | 667.6
1447 | 1295 | 859.4 | 834.9 | 750.4 | 795.1 | 665.2
1448 | 1296 | 857.3 | 819.2 | 747.7 | 792.8 | 665.2
1449 | 1297 | 851 | 795.5 | 726 | 787.4 | 661.8
1450 | 1298 | 845.3 | 781.1 | 721.9 | 784.4 | 659.4
1451 | 1299 | 847.9 | 792.1 | 745.9 | 785.9 | 663.2
1452 | 1300 | 849.8 | 796.9 | 727.2 | 787.5 | 662.2
1453 | 1301 | 845.3 | 786.1 | 705.8 | 785.4 | 659.2
1454 | 1302 | 837.8 | 763.7 | 685 | 780.4 | 655.3
1455 | 1303 | 834.9 | 763.1 | 673.5 | 778.9 | 654
1456 | 1304 | 837.5 | 781.3 | 667.6 | 780.3 | 653
1457 | 1305 | 843.3 | 801 | 679.2 | 783.5 | 654
1458 | 1306 | 843 | 793.4 | 673.2 | 782.3 | 652.8
1459 | 1307 | 839.2 | 781.2 | 657.7 | 778.9 | 649.3
1460 | 1308 | 838.7 | 794 | 667.5 | 780.1 | 650.3
1461 | 1309 | 841.6 | 810.7 | 681.8 | 783.7 | 653.1
1462 | 1310 | 843.4 | 818.4 | 696.4 | 785.8 | 655
1463 | 1311 | 843.6 | 817 | 691.6 | 785.1 | 652.6
1464 | 1312 | 844.4 | 817.2 | 689.5 | 785.7 | 652.7
1465 | 1313 | 841.6 | 799.5 | 684.7 | 783.8 | 650.5
1466 | 1314 | 841.4 | 802.7 | 694.2 | 784 | 650.5
1467 | 1315 | 845.6 | 819.5 | 713.3 | 787.7 | 653.7
1468 | 1316 | 849 | 835.7 | 733.6 | 791.6 | 655.3
1469 | 1317 | 853.8 | 845.4 | 760.7 | 794.7 | 661.1
1470 | 1318 | 856.3 | 845.6 | 762.2 | 795.3 | 660.7
1471 | 1319 | 857 | 851.4 | 755.9 | 797 | 659.7
1472 | 1320 | 857.4 | 855.2 | 748.9 | 798.3 | 659.9
1473 | 1321 | 860.1 | 855.8 | 764.5 | 797.9 | 662.9
1474 | 1322 | 863.9 | 856.6 | 768.7 | 798.6 | 663.7
1475 | 1323 | 866 | 854.5 | 787.7 | 800.2 | 665.7
1476 | 1324 | 866.9 | 856.3 | 786.2 | 802.7 | 668.5
1477 | 1325 | 863.6 | 840.4 | 760.1 | 801.9 | 666.3
1478 | 1326 | 861 | 837.6 | 744.5 | 800.7 | 665.6
1479 | 1327 | 857.1 | 843.3 | 741.6 | 801.9 | 664.9
1480 | 1328 | 854 | 850.2 | 723.6 | 801.2 | 664.7
1481 | 1329 | 853.5 | 850.3 | 722.3 | 803.8 | 667.3
1482 | 1330 | 855.7 | 851.4 | 734.3 | 806.5 | 670.8
1483 | 1331 | 858 | 858.1 | 770.4 | 808.4 | 676.9
1484 | 1332 | 861.8 | 856 | 793.4 | 809.2 | 682.6
1485 | 1333 | 864.9 | 863.9 | 781.3 | 810.9 | 682.5
1486 | 1334 | 868.4 | 874 | 792 | 814.3 | 684.8
1487 | 1335 | 871 | 872.3 | 799.9 | 816.2 | 688.7
1488 | 1336 | 872.9 | 871.1 | 818.7 | 817.2 | 693.6
1489 | 1337 | 872.4 | 867.9 | 821.2 | 818.8 | 697.7
1490 | 1338 | 873.2 | 867.5 | 833.4 | 820.2 | 700.8
1491 | 1339 | 874.7 | 865.4 | 830 | 821.9 | 702.3
1492 | 1340 | 876.2 | 865.1 | 828.1 | 823 | 703.9
1493 | 1341 | 877.2 | 878.9 | 815.4 | 824.5 | 702.9
1494 | 1342 | 877.1 | 888.2 | 796.9 | 826.8 | 702.1
1495.1 | 1343.1 | 879.2 | 884.2 | 801.6 | 827.3 | 703.1
1496.1 | 1344.1 | 876.6 | 882.4 | 789.8 | 828.9 | 700.5
1497.1 | 1345.1 | 877.4 | 876.6 | 795 | 828.7 | 701.6
1498.1 | 1346.1 | 878.7 | 869.5 | 810.6 | 829.7 | 705.6
1499.1 | 1347.1 | 879.4 | 875.7 | 804.4 | 832.3 | 705.4
1500.1 | 1348.1 | 878 | 884.2 | 779.7 | 832.5 | 701.7
1501.1 | 1349.1 | 876.4 | 875.3 | 774 | 831 | 699.5
1502.1 | 1350.1 | 877 | 861.5 | 784.7 | 830.3 | 700.3
1503.1 | 1351.1 | 876.2 | 851.6 | 786.1 | 828.7 | 700.2
1504.1 | 1352.1 | 876.8 | 840.6 | 800.9 | 827.7 | 701.1
1505.1 | 1353.1 | 879.4 | 837.7 | 801.3 | 828.2 | 700.4
1506.1 | 1354.1 | 880.7 | 834.5 | 809.4 | 826.7 | 701.6
1507.1 | 1355.1 | 883.8 | 840.7 | 825 | 826.3 | 704.9
1508.1 | 1356.1 | 885.7 | 846.6 | 834.9 | 828.1 | 708
1509.1 | 1357.1 | 886 | 847.1 | 826.7 | 827.4 | 709.1
1510.1 | 1358.1 | 886.4 | 842.8 | 823.7 | 826.9 | 708.9
1511.1 | 1359.1 | 884.8 | 833.6 | 801.9 | 823.3 | 704.5
1512.1 | 1360.1 | 884.8 | 828.5 | 798.4 | 819.7 | 703.8
1513.1 | 1361.1 | 886.8 | 838.6 | 798.6 | 819.7 | 705.6
1514.1 | 1362.1 | 887.9 | 834.4 | 792 | 817.7 | 703.5
1515.1 | 1363.1 | 885.1 | 823.8 | 777.7 | 815.8 | 700.3
1516.1 | 1364.1 | 875.7 | 797.5 | 733.7 | 809.6 | 694.2
1517.1 | 1365.1 | 868.7 | 777.7 | 717.7 | 804 | 690.7
1518.1 | 1366.1 | 863.7 | 765.8 | 698.3 | 799.1 | 687.1
1519.1 | 1367.1 | 860.6 | 762.2 | 685.7 | 794.9 | 683.7
1520.1 | 1368.1 | 863.4 | 783.8 | 689.4 | 796.7 | 682.7
1521.1 | 1369.1 | 868.6 | 807.8 | 709.1 | 799.8 | 683.5
1522.1 | 1370.1 | 872.6 | 821 | 726.5 | 802 | 683.7
1523.1 | 1371.1 | 872.7 | 811.7 | 712.5 | 800.1 | 682.6
1524.1 | 1372.1 | 864.7 | 788.3 | 680 | 793.9 | 676.8
1525.1 | 1373.1 | 859.6 | 785.4 | 680.2 | 790.9 | 675.5
1526.1 | 1374.1 | 862.8 | 813 | 696.9 | 795.2 | 678.5
1527.1 | 1375.1 | 864.7 | 813.9 | 709.1 | 796.2 | 678.5
1528.1 | 1376.1 | 866.8 | 820 | 727.6 | 797.7 | 678.9
1529.1 | 1377.1 | 862.4 | 804.8 | 714.6 | 793.7 | 675.4
1530.1 | 1378.1 | 858.7 | 794.1 | 693.4 | 790.8 | 671.6
1531.1 | 1379.1 | 858.9 | 805.2 | 684 | 790.6 | 671
1532.1 | 1380.1 | 858.8 | 807.3 | 688.2 | 792.3 | 670.8
1533.1 | 1381.1 | 862.2 | 810.8 | 699.2 | 794 | 673
1534.1 | 1382.1 | 862.2 | 801.6 | 689.5 | 792.5 | 670.9
1535.1 | 1383.1 | 864.2 | 805.8 | 697.5 | 792.2 | 670.8
1536.1 | 1384.1 | 862.4 | 795.1 | 698.3 | 790 | 669.3
1537.1 | 1385.1 | 862.4 | 793.6 | 736.2 | 789.5 | 671.2
1538.1 | 1386.1 | 862.5 | 801.1 | 739.6 | 791.9 | 672.8
1539.1 | 1387.1 | 861.4 | 804.1 | 730.2 | 791.4 | 669.8
1540.1 | 1388.1 | 862 | 810.2 | 728.3 | 792 | 670.9
1541.1 | 1389.1 | 857.7 | 801 | 715.1 | 790 | 668.6
1542.1 | 1390.1 | 852.9 | 795.1 | 722.1 | 788.7 | 668.8
1543.1 | 1391.1 | 855.4 | 809.4 | 738.7 | 790.4 | 671.3
1544.1 | 1392.1 | 858.4 | 831.2 | 755.7 | 792.9 | 675.1
1545.1 | 1393.1 | 864.8 | 844.1 | 777.1 | 795.8 | 679.3
1546.1 | 1394.1 | 867.2 | 843.9 | 788.1 | 798.3 | 680.1
1547.1 | 1395.1 | 868.9 | 838.2 | 781.6 | 799.9 | 680.9
1548.1 | 1396.1 | 867.3 | 830.7 | 769.3 | 798.3 | 680.2
1549.1 | 1397.1 | 864.3 | 817.8 | 754.1 | 798 | 679.1
1550.1 | 1398.1 | 866.7 | 833 | 757.1 | 799.2 | 680.2
1551.1 | 1399.1 | 867.2 | 825.7 | 757 | 799.5 | 680.3
1552.1 | 1400.1 | 864.3 | 819.7 | 751.6 | 799.1 | 680.2
1553.1 | 1401.1 | 848.7 | 779.4 | 718.5 | 790 | 675
1554.1 | 1402.1 | 829.5 | 739.8 | 662.1 | 778.6 | 666.9
1555.1 | 1403.1 | 812.4 | 706.8 | 618 | 765.5 | 659.9
1556.1 | 1404.1 | 796.7 | 673 | 581.8 | 754 | 654.3
1557.1 | 1405.1 | 783.8 | 649 | 552.4 | 746 | 648.9
1558.1 | 1406.1 | 772.2 | 628.6 | 521.8 | 736.1 | 643.4
1559.1 | 1407.1 | 759.8 | 608.8 | 496.3 | 725.7 | 637.9
1560.1 | 1408.1 | 747.6 | 592.4 | 470 | 715.9 | 632.5
1561.1 | 1409.1 | 738.5 | 575.9 | 447.9 | 708.7 | 626.5
1562.1 | 1410.1 | 731.2 | 563.3 | 426.6 | 701.5 | 621.2
1563.1 | 1411.1 | 723.5 | 550.1 | 407.5 | 695 | 615.8
1564.1 | 1412.1 | 716.5 | 539.2 | 391.9 | 687.3 | 611.4
1565.1 | 1413.1 | 709.9 | 529.3 | 375.7 | 681.3 | 606.3
1566.1 | 1414.1 | 702.5 | 518 | 362.5 | 673.2 | 601.7
1567.1 | 1415.1 | 696.8 | 507.7 | 349.8 | 666.8 | 597.4
1568.1 | 1416.1 | 691.1 | 499.2 | 337.1 | 660.3 | 593
1569.1 | 1417.1 | 684.8 | 490.5 | 325.8 | 653.9 | 588.4
1570.1 | 1418.1 | 678.9 | 483.4 | 317.3 | 645.9 | 584.5
1571.1 | 1419.1 | 672.7 | 476.8 | 308.9 | 638.4 | 580.9
1572.1 | 1420.1 | 667.4 | 470.6 | 300.6 | 634 | 577.6
1573.1 | 1421.1 | 662.2 | 465 | 293.1 | 628.5 | 573.9
1574.1 | 1422.1 | 657.3 | 460 | 286.8 | 622.7 | 570.6
1575.1 | 1423.1 | 652.2 | 454.1 | 280.4 | 617.6 | 567.2
1576.1 | 1424.1 | 647.6 | 448.7 | 273.9 | 612 | 564.1
1577.1 | 1425.1 | 642.8 | 443.7 | 267.3 | 606.2 | 560.9
1578.1 | 1426.1 | 637.6 | 438.1 | 259.9 | 601.8 | 557.5
1579.1 | 1427.1 | 632.6 | 433.4 | 254.7 | 597.2 | 554
1580.1 | 1428.1 | 628.1 | 429.4 | 249.9 | 592.6 | 551.3
1581.1 | 1429.1 | 624 | 423.1 | 243 | 589.6 | 547.7
1582.1 | 1430.1 | 619.5 | 418.6 | 237.1 | 584.1 | 544.5
1583.1 | 1431.1 | 614.9 | 413.8 | 232.1 | 578.7 | 542.1
1584.1 | 1432.1 | 610.8 | 409.9 | 227 | 575.5 | 538.8
1585.1 | 1433.1 | 607.3 | 407.1 | 222.4 | 571.7 | 535.7
1586.1 | 1434.1 | 603.3 | 404.5 | 218.2 | 567.3 | 532.5
1587.1 | 1435.1 | 599.8 | 401.2 | 213.4 | 563.5 | 529.6
1588.1 | 1436.1 | 596.1 | 397.8 | 209.6 | 559.6 | 526.1
1589.1 | 1437.1 | 592.6 | 395 | 207.3 | 556.1 | 523.8
1590.1 | 1438.1 | 589.3 | 391.4 | 204 | 552.6 | 521.7
1591.1 | 1439.1 | 586 | 387.6 | 200.4 | 550 | 518.3
1592.1 | 1440.1 | 582.4 | 383.9 | 196.6 | 545.7 | 515.1
1593.1 | 1441.1 | 578.5 | 380.6 | 193.2 | 540.9 | 512.5
1594.1 | 1442.1 | 574.7 | 377.9 | 190.3 | 536.8 | 509.8
1595.1 | 1443.1 | 570.5 | 373.8 | 187.8 | 532.4 | 507.3
1596.1 | 1444.1 | 567.3 | 369.5 | 184.8 | 529.8 | 504.9
1597.1 | 1445.1 | 564.2 | 366.6 | 182.2 | 527.2 | 502.7
1598.1 | 1446.1 | 560.9 | 361.6 | 179.8 | 524 | 500.3
1599.1 | 1447.1 | 557.5 | 358.7 | 177.7 | 520.5 | 498.1
1600.1 | 1448.1 | 554.4 | 355.4 | 175.5 | 517.6 | 495.9
1601.1 | 1449.1 | 551.2 | 351.8 | 173.4 | 514.2 | 493.7
1602.1 | 1450.1 | 548.1 | 349 | 171 | 510.6 | 491.8
1603.1 | 1451.1 | 544.7 | 347.1 | 168.5 | 507.6 | 489.6
1604.1 | 1452.1 | 541.4 | 345.4 | 166.5 | 504.4 | 487.9
1605.1 | 1453.1 | 538.5 | 343.6 | 165.4 | 502 | 485.8
1606.1 | 1454.1 | 535.6 | 341.5 | 164.6 | 498.1 | 483.7
1607.1 | 1455.1 | 532.4 | 339.8 | 162.8 | 495.3 | 481.6
1608.1 | 1456.1 | 529.6 | 337.3 | 161.2 | 492.3 | 479.8
1609.1 | 1457.1 | 526.5 | 334.3 | 159.2 | 489 | 477.7
1610.1 | 1458.1 | 523.6 | 332.2 | 157 | 485.6 | 475.6
1611.1 | 1459.1 | 520.7 | 328.5 | 155.6 | 483.4 | 473.3
1612.1 | 1460.1 | 517.8 | 325.8 | 154.6 | 478.8 | 471.2
1613.1 | 1461.1 | 514.7 | 324.6 | 152.5 | 475.4 | 469.2
1614.1 | 1462.1 | 511.6 | 321.9 | 150.5 | 473.1 | 466.3
1615.1 | 1463.1 | 508.7 | 318 | 149.2 | 470.5 | 464.1
1616.1 | 1464.1 | 505.7 | 315 | 147.7 | 467.7 | 461.7
1617.1 | 1465.1 | 502.6 | 312 | 145.9 | 464.2 | 459.4
1618.1 | 1466.1 | 500 | 307.9 | 144.5 | 461.6 | 457.4
1619.1 | 1467.1 | 497.3 | 303.1 | 143.8 | 458.9 | 456
1620.1 | 1468.1 | 494.8 | 298.7 | 143.5 | 456.3 | 453.6
1621.1 | 1469.1 | 492.2 | 296.7 | 142.8 | 454.2 | 451.8
1622.1 | 1470.1 | 489.6 | 295 | 141 | 451.4 | 450.3
1623.1 | 1471.1 | 487.5 | 293.5 | 139.5 | 448.6 | 448.3
1624.1 | 1472.1 | 484.7 | 292.7 | 138.8 | 444.9 | 446.7
1625.1 | 1473.1 | 481.9 | 291.8 | 137.7 | 442.4 | 444.9
1626.1 | 1474.1 | 480 | 290 | 136.2 | 440.4 | 443.5
1627.1 | 1475.1 | 477.9 | 289.5 | 135.1 | 438.1 | 441.8
1628.1 | 1476.1 | 475.6 | 288.6 | 133.6 | 434.8 | 439.8
1629.1 | 1477.1 | 473 | 288 | 132.7 | 431.4 | 438.1
1630.1 | 1478.1 | 470.7 | 287.3 | 131.6 | 429.2 | 436.5
1631.1 | 1479.1 | 468 | 286.5 | 130.6 | 427 | 434.6
1632.1 | 1480.1 | 465.8 | 284.9 | 129.2 | 425.2 | 433
1633.1 | 1481.1 | 463.3 | 283.6 | 128.4 | 423.4 | 431.7
1634.1 | 1482.1 | 461 | 282.1 | 127.5 | 420.6 | 430.1
1635.1 | 1483.1 | 458.6 | 281 | 126.5 | 416.8 | 428.4
1636.1 | 1484.1 | 456.3 | 280.5 | 125.6 | 414.4 | 426.5
1637.1 | 1485.1 | 454 | 278.9 | 124.7 | 412.5 | 425
1638.1 | 1486.1 | 451.8 | 277.5 | 123.8 | 411.1 | 423.2
1639.1 | 1487.1 | 449.8 | 276 | 122.9 | 409.7 | 421.9
1640.1 | 1488.1 | 448.1 | 273.6 | 122.3 | 407.6 | 420.4
1641.1 | 1489.1 | 446 | 271.8 | 121.7 | 404.8 | 418.7
1642.1 | 1490.1 | 443.7 | 271 | 121.1 | 403 | 417.1
1643.1 | 1491.1 | 442 | 267.6 | 120.7 | 401.6 | 415.8
1644.1 | 1492.1 | 440.1 | 264.7 | 120.2 | 399.4 | 414.4
1645.1 | 1493.1 | 437.8 | 263.3 | 119.5 | 397.1 | 413.2
1646.1 | 1494.1 | 435.6 | 262.2 | 118.6 | 395.4 | 412
1647.1 | 1495.1 | 434.1 | 259.7 | 117.8 | 393.9 | 410.6
1648.1 | 1496.1 | 432.5 | 258.8 | 116.9 | 392.3 | 409
1649.1 | 1497.1 | 430.6 | 258.7 | 116.1 | 390 | 407.2
1650.1 | 1498.1 | 428.7 | 258.2 | 115.3 | 388.9 | 405.6
1651.1 | 1499.1 | 427 | 257.1 | 114.5 | 386.9 | 404.3
1652.1 | 1500.1 | 425.4 | 255.7 | 113.8 | 386 | 402.7
1653.1 | 1501.1 | 423.5 | 255.4 | 113.2 | 383.5 | 401.3
1654.1 | 1502.1 | 421.6 | 254.7 | 112.4 | 381.2 | 400.1
1655.1 | 1503.1 | 419.5 | 254.4 | 111.8 | 378.5 | 398.5
1656.1 | 1504.1 | 417.4 | 253.6 | 111.5 | 376.5 | 397
1657.1 | 1505.1 | 415.4 | 251.8 | 110.7 | 374.1 | 395.5
1658.1 | 1506.1 | 413.4 | 251 | 110.2 | 372.1 | 393.9
1659.1 | 1507.1 | 411.7 | 248.6 | 109.9 | 370.5 | 392.6
1660.1 | 1508.1 | 410.2 | 246.4 | 109.5 | 369.3 | 391.3
1661.1 | 1509.1 | 408.7 | 245.8 | 108.8 | 368.6 | 390
1662.1 | 1510.1 | 407 | 244.1 | 108.1 | 366.9 | 388.8
1663.1 | 1511.1 | 405.7 | 241.5 | 107.6 | 365.6 | 387.3
1664.1 | 1512.1 | 404.4 | 239 | 107.2 | 364.6 | 385.9
1665.1 | 1513.1 | 402.7 | 238.7 | 106.5 | 363 | 384.7
1666.1 | 1514.1 | 400.6 | 238.3 | 105.6 | 360.1 | 382.7
1667.1 | 1515.1 | 398.5 | 237.1 | 104.6 | 357.6 | 380.9
1668.1 | 1516.1 | 396.6 | 235.5 | 103.6 | 355.4 | 379.1
1669.1 | 1517.1 | 394.8 | 234.3 | 103.2 | 353.7 | 377.3
1670.1 | 1518.1 | 392.6 | 233.1 | 102.7 | 351.9 | 375.6
1671.1 | 1519.1 | 391.1 | 231.8 | 102.5 | 350.3 | 374.5
1672.1 | 1520.1 | 389.8 | 231.7 | 102.3 | 348.5 | 373.1
1673.1 | 1521.1 | 388.6 | 231.2 | 101.8 | 347.3 | 371.6
1674.1 | 1522.1 | 387.3 | 229.7 | 101.4 | 346.4 | 370.2
1675.1 | 1523.1 | 385.7 | 228.4 | 100.9 | 344.8 | 368.7
1676.1 | 1524.1 | 384.2 | 227.5 | 100.3 | 343 | 366.9
1677.1 | 1525.1 | 382.8 | 226.4 | 99.8 | 341.5 | 365.2
1678.1 | 1526.1 | 381.3 | 226 | 99.5 | 339.4 | 363.6
1679.1 | 1527.1 | 379.9 | 225.4 | 99.2 | 337.9 | 362.2
1680.1 | 1528.1 | 378.5 | 224.4 | 98.8 | 336.1 | 360.8
1681.1 | 1529.1 | 376.8 | 223.9 | 98.6 | 332.7 | 359.7
1682.1 | 1530.1 | 375.1 | 223.7 | 98.1 | 330 | 358.3
1683.1 | 1531.1 | 373.7 | 223.3 | 97.7 | 328.1 | 356.6
1684.1 | 1532.1 | 372.4 | 222.1 | 97.2 | 326.4 | 354.9
1685.1 | 1533.1 | 370.9 | 221.4 | 96.7 | 324.2 | 353.5
1686.1 | 1534.1 | 369.3 | 220.7 | 96.2 | 321 | 352
1687.1 | 1535.1 | 367.7 | 219.9 | 95.7 | 319.8 | 350.6
1688.1 | 1536.1 | 365.9 | 218.8 | 95.2 | 317.3 | 349.3
1689.1 | 1537.1 | 364.4 | 218.2 | 94.7 | 315.3 | 347.8
1690.1 | 1538.1 | 362.8 | 217.5 | 94.4 | 314.2 | 346.2
1691.1 | 1539.1 | 361.8 | 216.9 | 94 | 313.6 | 345.1
1692.1 | 1540.1 | 360.8 | 214.9 | 93.6 | 312.8 | 344
1693.1 | 1541.1 | 359.9 | 213.4 | 93.4 | 311.8 | 342.9
1694.1 | 1542.1 | 358.6 | 212.5 | 93.2 | 309.9 | 341.9
1695.1 | 1543.1 | 357.5 | 211.1 | 92.9 | 309.1 | 340.9
1696.1 | 1544.1 | 356.4 | 208.2 | 92.6 | 308.5 | 339.9
1697.1 | 1545.1 | 355 | 207.5 | 92.4 | 306.6 | 339.1
1698.1 | 1546.1 | 353.7 | 206.4 | 92.1 | 305.7 | 338.4
1699.1 | 1547.1 | 352.5 | 205.8 | 91.8 | 304.8 | 337.6
1700.1 | 1548.1 | 351.3 | 204.2 | 91.5 | 304.8 | 336.3
1701.1 | 1549.1 | 350.1 | 202.5 | 91 | 303.9 | 335.2
1702.1 | 1550.1 | 349.2 | 202.1 | 90.7 | 303.5 | 334.3
1703.1 | 1551.1 | 347.7 | 201.2 | 90.7 | 301.2 | 332.8
1704.1 | 1552.1 | 345.9 | 200.4 | 90.5 | 299.6 | 331.6
1705.1 | 1553.1 | 344.7 | 199.4 | 90.5 | 298.2 | 330.4
1706.1 | 1554.1 | 343.4 | 198.3 | 90.1 | 296.1 | 329.2
1707.1 | 1555.1 | 341.5 | 197.6 | 89.9 | 294.1 | 328.3
1708.1 | 1556.1 | 339.8 | 196.9 | 89.4 | 292.7 | 326.8
1709.1 | 1557.1 | 338.7 | 196.4 | 89.1 | 291.9 | 325.3
1710.1 | 1558.1 | 337.5 | 195.6 | 88.9 | 290.5 | 324
1711.1 | 1559.1 | 336.2 | 195.8 | 88.6 | 288.4 | 322.6
1712.1 | 1560.1 | 334.5 | 195.4 | 88.2 | 287.1 | 321.3
1713.1 | 1561.1 | 333.8 | 194.4 | 87.9 | 286.8 | 320.3
1714.1 | 1562.1 | 332.9 | 193.9 | 87.7 | 285.5 | 319.1
1715.1 | 1563.1 | 331.8 | 193.3 | 87.5 | 284.6 | 317.8
1716.1 | 1564.1 | 331.1 | 192.3 | 87.2 | 284.5 | 316.7
1717.1 | 1565.1 | 330.5 | 191.5 | 86.7 | 284.8 | 315.7
1718.1 | 1566.1 | 330.1 | 190.6 | 86.2 | 283.5 | 314.8
1719.1 | 1567.1 | 329.4 | 189.5 | 85.7 | 281.9 | 313.6
1720.1 | 1568.1 | 328.5 | 189.7 | 85.3 | 280.9 | 312.6
1721.1 | 1569.1 | 327.7 | 189.5 | 85 | 280 | 311.7
1722.1 | 1570.1 | 327 | 189.5 | 84.9 | 279.6 | 310.8
1723.1 | 1571.1 | 326.2 | 188.8 | 84.8 | 279.4 | 309.8
1724.1 | 1572.1 | 325.3 | 187.1 | 84.6 | 278.2 | 308.8
1725.1 | 1573.1 | 324.1 | 187 | 84.4 | 275.8 | 308
1726.1 | 1574.1 | 322.3 | 187.4 | 84.2 | 274 | 307.2
1727.1 | 1575.1 | 320.7 | 187.1 | 83.9 | 273.3 | 306.2
1728.1 | 1576.1 | 319.4 | 186.4 | 83.5 | 272.8 | 305.2
1729.1 | 1577.1 | 318.3 | 185.3 | 83.3 | 272.2 | 304.3
1730.1 | 1578.1 | 317 | 184.3 | 83.1 | 270.9 | 303.1
1731.1 | 1579.1 | 316 | 184 | 82.6 | 269.7 | 302
1732.1 | 1580.1 | 315.3 | 183.2 | 82.1 | 269.5 | 301
1733.1 | 1581.1 | 314.5 | 182.4 | 82 | 268.8 | 299.7
1734.1 | 1582.1 | 313.3 | 181.8 | 81.7 | 268.2 | 298.8
1735.1 | 1583.1 | 312.2 | 182.1 | 81.2 | 266.9 | 297.8
1736.1 | 1584.1 | 311.6 | 181.6 | 80.9 | 265.9 | 296.8
1737.1 | 1585.1 | 311 | 181.2 | 80.5 | 265.1 | 295.8
1738.1 | 1586.1 | 310.3 | 180.3 | 80.3 | 264.5 | 295
1739.1 | 1587.1 | 309.5 | 179.2 | 80.2 | 263.3 | 293.8
1740.1 | 1588.1 | 308.9 | 178.4 | 79.9 | 262.7 | 292.5
1741.1 | 1589.1 | 308.7 | 177.1 | 79.7 | 262 | 291.3
1742.1 | 1590.1 | 307.9 | 176.5 | 79.7 | 260.2 | 290.3
1743.1 | 1591.1 | 307 | 176.1 | 79.4 | 259.1 | 289.4
1744.1 | 1592.1 | 306.3 | 176 | 79 | 258.5 | 288.3
1745.1 | 1593.1 | 305.7 | 175.8 | 78.7 | 258.4 | 287.6
1746.1 | 1594.1 | 304.8 | 175.7 | 78.4 | 257.4 | 286.8
1747.1 | 1595.1 | 304.3 | 174.8 | 78.2 | 256 | 285.8
1748.1 | 1596.1 | 303.5 | 174.1 | 77.9 | 254.5 | 284.8
1749.1 | 1597.1 | 302.7 | 173.9 | 77.5 | 253.2 | 283.8
1750.1 | 1598.1 | 301.9 | 173.3 | 77.4 | 252.7 | 283
1751.1 | 1599.1 | 300.8 | 171.8 | 77.3 | 251.6 | 282
1752.1 | 1600.1 | 299.9 | 170.1 | 77.1 | 251.2 | 281.3
1753.1 | 1601.1 | 299.1 | 168.6 | 76.9 | 250.9 | 280.3
1754.1 | 1602.1 | 298.3 | 167.4 | 76.7 | 250.6 | 279.5
1755.1 | 1603.1 | 297.6 | 166.5 | 76.6 | 249.8 | 278.6
1756.1 | 1604.1 | 297 | 166.2 | 76.4 | 249 | 277.8
1757.1 | 1605.1 | 296.4 | 165.5 | 76.1 | 248.4 | 277.1
1758.1 | 1606.1 | 295.7 | 164.5 | 75.8 | 247.6 | 276.4
1759.1 | 1607.1 | 294.4 | 164 | 75.9 | 245.9 | 275.6
1760.1 | 1608.1 | 292.2 | 164.2 | 75.7 | 243.7 | 274.5
1761.1 | 1609.1 | 290.7 | 164.1 | 75.6 | 242.2 | 273.5
1762.1 | 1610.1 | 289.5 | 163.9 | 75.4 | 240.9 | 272.5
1763.1 | 1611.1 | 288.5 | 164.1 | 75.4 | 239.6 | 271.8
1764.1 | 1612.1 | 287.8 | 162.8 | 75.4 | 238.7 | 271
1765.1 | 1613.1 | 287.1 | 161.4 | 75.3 | 237.8 | 270.3
1766.1 | 1614.1 | 286.5 | 159.8 | 75.1 | 237.5 | 269.7
1767.1 | 1615.1 | 286.1 | 159.2 | 74.9 | 237.2 | 268.9
1768.1 | 1616.1 | 286 | 157.9 | 74.5 | 236.9 | 268
1769.1 | 1617.1 | 285.6 | 156.8 | 74.2 | 236.3 | 267.3
1770.1 | 1618.1 | 284.9 | 156.7 | 73.9 | 235.6 | 266.6
1771.1 | 1619.1 | 284.4 | 156.4 | 73.6 | 235.2 | 265.8
1772.1 | 1620.1 | 284.1 | 155.3 | 73.2 | 234.9 | 265.1
1773.1 | 1621.1 | 283.7 | 154.3 | 73 | 234.2 | 264.2
1774.1 | 1622.1 | 282.8 | 154.3 | 72.7 | 233.3 | 263.3
1775.1 | 1623.1 | 281.8 | 153.9 | 72.6 | 232.1 | 262.5
1776.1 | 1624.1 | 281 | 152.6 | 72.4 | 230.8 | 261.6
1777.1 | 1625.1 | 280.1 | 153 | 72.2 | 229.7 | 260.9
1778.1 | 1626.1 | 279.6 | 152.8 | 71.9 | 229.2 | 260.1
1779.1 | 1627.1 | 279.2 | 152 | 71.7 | 228.8 | 259.3
1780.1 | 1628.1 | 278.6 | 150.9 | 71.7 | 227.7 | 258.7
1781.1 | 1629.1 | 277.7 | 151 | 71.5 | 226.5 | 257.7
1782.1 | 1630.1 | 277.1 | 151.4 | 71.3 | 225.8 | 256.7
1783.1 | 1631.1 | 276 | 151.9 | 71.2 | 224.2 | 256.2
1784.1 | 1632.1 | 275 | 151.6 | 71 | 223.3 | 255.5
1785.1 | 1633.1 | 273.9 | 151.5 | 71.1 | 222.1 | 254.7
1786.1 | 1634.1 | 272.4 | 151.1 | 71 | 220.5 | 253.8
1787.1 | 1635.1 | 271.9 | 150.9 | 70.7 | 220.2 | 253
1788.1 | 1636.1 | 271.4 | 150.9 | 70.5 | 219.6 | 252.2
1789.1 | 1637.1 | 270.8 | 150.6 | 70.3 | 219 | 251.2
1790.1 | 1638.1 | 270.1 | 150.6 | 70.2 | 218.6 | 250.4
1791.1 | 1639.1 | 269.4 | 150.2 | 70.1 | 217.3 | 249.6
1792.1 | 1640.1 | 268.3 | 149.6 | 70 | 215.7 | 248.8
1793.1 | 1641.1 | 267.6 | 149.1 | 70 | 214.8 | 248.1
1794.1 | 1642.1 | 266.7 | 148.6 | 69.9 | 213.9 | 247.3
1795.1 | 1643.1 | 266 | 148.7 | 69.8 | 213.3 | 246.5
1796.1 | 1644.1 | 265.3 | 148.6 | 69.4 | 212 | 245.6
1797.1 | 1645.1 | 264.3 | 148.7 | 69.4 | 210.5 | 244.8
1798.1 | 1646.1 | 263.5 | 148.7 | 69.2 | 209.8 | 243.9
1799.1 | 1647.1 | 262.9 | 148.7 | 69.2 | 209.4 | 243.4
1800.1 | 1648.1 | 262.3 | 148.9 | 69.1 | 208.7 | 242.8
1801.1 | 1649.1 | 261.9 | 148.9 | 68.9 | 208.2 | 242
1802.1 | 1650.1 | 261.1 | 148.2 | 68.8 | 207.5 | 241
1803.1 | 1651.1 | 260.3 | 148.3 | 68.7 | 206.8 | 240.3
1804.1 | 1652.1 | 259.8 | 148.2 | 68.6 | 206.6 | 239.6
1805.1 | 1653.1 | 259.6 | 148.6 | 68.5 | 206.7 | 238.9
1806.1 | 1654.1 | 259.4 | 148.6 | 68.3 | 206.8 | 238.1
1807.1 | 1655.1 | 259.1 | 148.2 | 68.2 | 206.4 | 237.2
1808.1 | 1656.1 | 258.1 | 147.9 | 68 | 205 | 236.5
1809.1 | 1657.1 | 256.9 | 146.6 | 67.7 | 203.5 | 235.6
1810.1 | 1658.1 | 256.2 | 144.8 | 67.6 | 202.4 | 234.7
1811.1 | 1659.1 | 255.6 | 144.5 | 67.4 | 202 | 233.8
1812.1 | 1660.1 | 254.7 | 144.3 | 67.1 | 201.5 | 233.2
1813.1 | 1661.1 | 254.2 | 144.2 | 66.9 | 200.9 | 232.4
1814.1 | 1662.1 | 253.8 | 143.7 | 66.7 | 200.7 | 231.5
1815.1 | 1663.1 | 253.6 | 143.3 | 66.6 | 200.2 | 230.7
1816.1 | 1664.1 | 253.1 | 142.7 | 66.5 | 199.4 | 229.9
1817.1 | 1665.1 | 252 | 141.9 | 66.4 | 198.5 | 229.3
1818.1 | 1666.1 | 251.5 | 141.7 | 66.4 | 197.9 | 228.7
1819.1 | 1667.1 | 251.2 | 141.7 | 66.2 | 197.7 | 228
1820.1 | 1668.1 | 251 | 140.9 | 66.1 | 197.5 | 227.3
1821.1 | 1669.1 | 250.7 | 139.8 | 65.9 | 197.2 | 226.7
1822.1 | 1670.1 | 250.3 | 138.9 | 65.9 | 196.7 | 226.1
1823.1 | 1671.1 | 249.3 | 137.7 | 65.8 | 195.8 | 225.6
1824.1 | 1672.1 | 248.3 | 137.1 | 65.8 | 195.7 | 225.1
1825.1 | 1673.1 | 247.7 | 135.5 | 65.8 | 195.9 | 224.6

## Test Facts
Last row in IRMS data sheets: | 15
Time when Penlight power was initiated: | 152