## Test Conditions
CAROLFIRE Intermediate Scale Test Number IT-10
Test Date: | 2006-11-16
Ignition Time Relative to Thermal Data: | 174 | s
Ignition Time Relative to Electrical Data: | 174 | s
A Note regarding Propene Gas Flow Reading and calculation of Heat Release Rate:
The indicated flow rate is recorded in Standard Liters per Minute (SLM) of Gas. There is a correction factor of 0.40 applied to reflect the behavior of Propene versus the Flow Controller calibration gas which is Nitrogen. Hence, the actual flow of Propene in SLM is the indicated flow (shown in the data set as "Propene Gas Flow Reading") times 0.40. The heat release rate (HRR) can then be estimated using the gas density at standard conditions, heat of combustion, and the combustion efficiency. The result of this calculation is also shown on the data sheet based on the assumed properties listed below in the rows immediately below. Note that altering the values listed here will result in revised calculations of the HRR.
| Gas Burner Heat Release Rate Calculation Parameters: | Value | Units
| Gas Density At Standard conditions | 1.802 | kg/m3
| Heat of Combustion | 45.79 | MJ/kg
| One liter equals | 0.001 | m3
| Combustion efficiency | 0.85 | %

## Data Plots
Plots for Location G bundles - both SCDU circuits shown

## Thermal Data
Time |  | Burner |  |  | Hood & Ambient Facility Temperatures | [5 empty] | Stack |  |  | External Wind |  | Location A - 6-cable bundle 10-1 |  |  |  | Location A | Location C - 6-cable bundle 10-2 |  |  |  | Location C | Location E - 3+1 bundle 10-3 in Conduit |  |  | Location G - 6-cable bundle 10-4 |  |  |  | Location G | Slug Calorimeters
Time (s) | Offset Time (s) | Raw Gas Flow | Corrected Gas Flow (SLM) | Nominal HRR (kW) | Hood East | Hood West | Hood North | Hood South | Hood Top | Facility Ambient | O2 analyzer | stack temp | diff press stack *10 | wind direction | wind speed (mph) | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | TC-1 Cable E | TC-2 Above Bundle | TC3 Below Bundle | TC4 Bundle Center | Tray Rung | Cable 1 TC | Air Inside Conduit | Conduit Temp | TC-1 Cable E | TC-2 Above Bundle | TC-3 Below Bundle | TC-4 Bundle Center | Tray Rung | Slug Calorimeter Above Location F | Slug Calorimeter Above Location G
0 | -174 | -6.5 | 0 | 0 | 12.9 | 13.4 | 13.2 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2 | 190.9 | 4.1 | 12.4 | 11.4 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12.1 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
1 | -173 | -6.4 | 0 | 0 | 13 | 13.4 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.1 | 184.3 | 3.9 | 12.4 | 11.4 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12.1 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
2 | -172 | -6.3 | 0 | 0 | 13 | 13.4 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.1 | 180.9 | 3.8 | 12.4 | 11.4 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12.1 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
3 | -171 | -6.3 | 0 | 0 | 13 | 13.4 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.2 | 183.9 | 3.6 | 12.4 | 11.4 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
4 | -170 | -6.4 | 0 | 0 | 13 | 13.4 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.3 | 191.8 | 3.4 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
5 | -169 | -6.4 | 0 | 0 | 13 | 13.4 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.2 | 193.4 | 3.2 | 12.4 | 11.4 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
6 | -168 | -6.4 | 0 | 0 | 13 | 13.3 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.2 | 200.5 | 3.2 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
7 | -167 | -6.4 | 0 | 0 | 13 | 13.3 | 13.3 | 13.3 | 14.2 | 11.3 | 22.4 | 11 | 2.1 | 202.8 | 3.4 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
8 | -166 | -6.6 | 0 | 0 | 13 | 13.3 | 13.3 | 13.2 | 14.2 | 11.3 | 22.4 | 11 | 2.1 | 200.2 | 3.6 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
9 | -165 | -6.5 | 0 | 0 | 13 | 13.3 | 13.3 | 13.2 | 14.2 | 11.3 | 22.4 | 11 | 2.5 | 203.3 | 3.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
10 | -164 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.2 | 14.2 | 11.4 | 22.4 | 11 | 2.2 | 206.8 | 3.5 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
11 | -163 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.2 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 207.3 | 3.5 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
12 | -162 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.2 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 212.9 | 3.3 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
13 | -161 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.2 | 14.2 | 11.4 | 22.4 | 11 | 2.2 | 217 | 3.2 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
14 | -160 | -6.4 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.2 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 213.8 | 3.2 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
15 | -159 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.2 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 210.2 | 3.1 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
16 | -158 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 2.3 | 210.6 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
17 | -157 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 211.1 | 3.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
18 | -156 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 198 | 3.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
19 | -155 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 194.6 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
20 | -154 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 2.3 | 216.6 | 3.4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
21 | -153 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 218.9 | 3.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
22 | -152 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.4 | 22.4 | 11 | 2.1 | 197.2 | 4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
23 | -151 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 2.3 | 205.8 | 4.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
24 | -150 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 2.1 | 221.8 | 4.1 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
25 | -149 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 2 | 223.4 | 4.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
26 | -148 | -6.4 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 2 | 217.6 | 4.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
27 | -147 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 2.1 | 215.2 | 3.8 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
28 | -146 | -6.4 | 0 | 0 | 13 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 1.9 | 215.7 | 3.6 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
29 | -145 | -6.3 | 0 | 0 | 13 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 1.9 | 216.3 | 3.6 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
30 | -144 | -6.4 | 0 | 0 | 13 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 11 | 2 | 221 | 3.3 | 12.4 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
31 | -143 | -6.4 | 0 | 0 | 12.9 | 13.3 | 13.3 | 13 | 14.2 | 11.5 | 22.4 | 10.9 | 2 | 221.8 | 3.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
32 | -142 | -6.6 | 0 | 0 | 12.9 | 13.3 | 13.3 | 13 | 14.2 | 11.4 | 22.4 | 11 | 2 | 198.7 | 3.6 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
33 | -141 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.3 | 13.1 | 14.2 | 11.4 | 22.4 | 10.9 | 1.9 | 189.6 | 3.9 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
34 | -140 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 2 | 207.7 | 4.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
35 | -139 | -6.6 | 0 | 0 | 12.8 | 13.3 | 13.2 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 1.9 | 199.2 | 5.6 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
36 | -138 | -6.6 | 0 | 0 | 12.8 | 13.3 | 13.2 | 13.1 | 14.2 | 11.4 | 22.4 | 11 | 1.9 | 200.6 | 6.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
37 | -137 | -6.6 | 0 | 0 | 12.8 | 13.4 | 13.2 | 13 | 14.2 | 11.3 | 22.4 | 11 | 2.1 | 208.8 | 6.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
38 | -136 | -6.6 | 0 | 0 | 12.8 | 13.4 | 13.2 | 13 | 14.2 | 11.3 | 22.4 | 11 | 2.5 | 209.1 | 6 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
39 | -135 | -6.6 | 0 | 0 | 12.8 | 13.4 | 13.2 | 13 | 14.2 | 11.3 | 22.4 | 11 | 2 | 209.9 | 5.9 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
40 | -134 | -6.5 | 0 | 0 | 12.8 | 13.3 | 13.2 | 13 | 14.2 | 11.3 | 22.4 | 11 | 2.3 | 210.7 | 5.6 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
41 | -133 | -6.5 | 0 | 0 | 12.8 | 13.3 | 13.2 | 13 | 14.2 | 11.3 | 22.4 | 11 | 2.3 | 212.7 | 5.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
42 | -132 | -6.6 | 0 | 0 | 12.8 | 13.3 | 13.2 | 13 | 14.2 | 11.3 | 22.4 | 11 | 2.3 | 211.2 | 4.9 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
43 | -131 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 207.1 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
44 | -130 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 199.8 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
45 | -129 | -6.4 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 207.3 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.8 | 14.1 | 15.8 | 15.7 | 15.3
46 | -128 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.2 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 1.9 | 210.2 | 4.4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
47 | -127 | -6.6 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13 | 14.2 | 11.2 | 22.4 | 11 | 1.9 | 206.9 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
48 | -126 | -6.7 | 0 | 0 | 13 | 13.3 | 13.2 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 212.4 | 4.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
49 | -125 | -6.7 | 0 | 0 | 12.9 | 13.3 | 13.2 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.1 | 210.2 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
50 | -124 | -6.7 | 0 | 0 | 12.9 | 13.3 | 13.2 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.2 | 218.6 | 4.8 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
51 | -123 | -6.7 | 0 | 0 | 12.9 | 13.3 | 13.2 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.2 | 216.3 | 5.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
52 | -122 | -6.6 | 0 | 0 | 12.9 | 13.3 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 212.8 | 5.4 | 12.3 | 11.3 | 11.1 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
53 | -121 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 211.4 | 5.4 | 12.3 | 11.3 | 11.1 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
54 | -120 | -6.3 | 0 | 0 | 12.9 | 13.3 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.4 | 210.7 | 5.1 | 12.3 | 11.3 | 11.1 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
55 | -119 | -6.1 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.4 | 214 | 4.7 | 12.3 | 11.3 | 11.1 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
56 | -118 | -6 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 214.1 | 4.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
57 | -117 | -6.1 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.5 | 209.6 | 4.4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
58 | -116 | -6.4 | 0 | 0 | 12.8 | 13.4 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.2 | 209.1 | 4.4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
59 | -115 | -6.4 | 0 | 0 | 12.8 | 13.4 | 13.1 | 12.9 | 14.2 | 11.2 | 22.4 | 11 | 2.3 | 208.4 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
60 | -114 | -6.4 | 0 | 0 | 12.8 | 13.4 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2.1 | 208.4 | 4.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.8 | 14.1 | 15.7 | 15.7 | 15.3
61 | -113 | -6.4 | 0 | 0 | 12.8 | 13.4 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2.1 | 210.2 | 3.9 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.8 | 14.1 | 15.7 | 15.7 | 15.3
62 | -112 | -6.3 | 0 | 0 | 12.8 | 13.4 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2 | 217.7 | 3.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
63 | -111 | -6.5 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2.1 | 221.4 | 3.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
64 | -110 | -6.6 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2.2 | 224.3 | 3.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.8 | 14.1 | 15.7 | 15.7 | 15.3
65 | -109 | -6.5 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2.4 | 225.4 | 4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
66 | -108 | -6.5 | 0 | 0 | 12.8 | 13.3 | 13.1 | 12.8 | 14.2 | 11.2 | 22.4 | 11 | 2.4 | 214.6 | 4.9 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
67 | -107 | -6.3 | 0 | 0 | 12.9 | 13.3 | 13.2 | 12.8 | 14.2 | 11.2 | 22.3 | 11 | 2.3 | 215.9 | 5.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
68 | -106 | -6.3 | 0 | 0 | 12.9 | 13.3 | 13.2 | 12.8 | 14.2 | 11.3 | 22.3 | 11 | 2 | 250.6 | 5.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
69 | -105 | -6.4 | 0 | 0 | 12.9 | 13.2 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 11 | 2.1 | 243.9 | 4.8 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
70 | -104 | -6.4 | 0 | 0 | 13 | 13.2 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 212.1 | 4.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
71 | -103 | -6.5 | 0 | 0 | 13 | 13.2 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 11 | 2 | 196.7 | 4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.3 | 11.8 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
72 | -102 | -6.6 | 0 | 0 | 13 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 11 | 1.9 | 231.8 | 3.5 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
73 | -101 | -6.4 | 0 | 0 | 13 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.4 | 10.9 | 2.1 | 274.6 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
74 | -100 | -6.4 | 0 | 0 | 13 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 262.2 | 2.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
75 | -99 | -6.5 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 216.3 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.3 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
76 | -98 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 215.8 | 3.4 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
77 | -97 | -6.5 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 228.3 | 3.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
78 | -96 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 214.6 | 3.7 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
79 | -95 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.8 | 14.2 | 11.3 | 22.3 | 10.9 | 2 | 200.2 | 4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
80 | -94 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.8 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 213.4 | 4.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
81 | -93 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.8 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 220.2 | 4.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
82 | -92 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.3 | 12.8 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 213.5 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 12 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
83 | -91 | -6.6 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 211.7 | 4.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 12 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
84 | -90 | -6.5 | 0 | 0 | 13.1 | 13.1 | 13.3 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 210 | 4.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
85 | -89 | -6.5 | 0 | 0 | 13 | 13.1 | 13.3 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.5 | 204.8 | 4.2 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 12 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
86 | -88 | -6.4 | 0 | 0 | 13 | 13.2 | 13.3 | 12.9 | 14.2 | 11.3 | 22.3 | 10.9 | 2.5 | 204.3 | 4.2 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
87 | -87 | -6.4 | 0 | 0 | 13 | 13.2 | 13.3 | 13 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 203.3 | 4.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
88 | -86 | -6.3 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13 | 14.2 | 11.3 | 22.3 | 10.8 | 2.2 | 212.1 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
89 | -85 | -6.3 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 211 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.8 | 15.7 | 15.3
90 | -84 | -6.2 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13 | 14.2 | 11.3 | 22.3 | 10.9 | 2 | 178.5 | 3.9 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
91 | -83 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.3 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 192.4 | 3.5 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
92 | -82 | -6.6 | 0 | 0 | 12.9 | 13.3 | 13.3 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 214.5 | 3.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.6 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
93 | -81 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.3 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 197.8 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
94 | -80 | -6.5 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 217.4 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
95 | -79 | -6.7 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 210.1 | 5.6 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
96 | -78 | -6.7 | 0 | 0 | 12.9 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 207.8 | 5.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
97 | -77 | -6.7 | 0 | 0 | 13 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 228 | 5.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
98 | -76 | -6.7 | 0 | 0 | 13 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.5 | 205.8 | 4.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
99 | -75 | -6.6 | 0 | 0 | 13 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 225 | 4.9 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
100 | -74 | -6.5 | 0 | 0 | 13 | 13.3 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 231.4 | 5.1 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
101 | -73 | -6.4 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.4 | 218 | 5.1 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
102 | -72 | -6.3 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.4 | 214 | 4.9 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
103 | -71 | -6.4 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 240.9 | 4.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
104 | -70 | -6.5 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.1 | 242.7 | 4.3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
105 | -69 | -6.6 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 221.9 | 4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.7 | 15.3
106 | -68 | -6.6 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.4 | 212.9 | 3.7 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
107 | -67 | -6.6 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.3 | 214.7 | 3.3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
108 | -66 | -6.7 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2.2 | 241.8 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
109 | -65 | -6.7 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2 | 257.1 | 3.1 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
110 | -64 | -6.7 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.3 | 22.3 | 10.9 | 2 | 242.5 | 3.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
111 | -63 | -6.7 | 0 | 0 | 13 | 13.2 | 13.2 | 13.1 | 14.2 | 11.2 | 22.3 | 10.9 | 2.2 | 222.4 | 3.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
112 | -62 | -6.6 | 0 | 0 | 13.1 | 13.2 | 13.2 | 13.1 | 14.2 | 11.2 | 22.3 | 10.9 | 2.1 | 206.5 | 3.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
113 | -61 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.2 | 13.1 | 14.2 | 11.2 | 22.3 | 10.9 | 2.3 | 195.7 | 3.2 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
114 | -60 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2.1 | 201.8 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
115 | -59 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2.3 | 208.2 | 3.1 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
116 | -58 | -6.6 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2.3 | 216.4 | 2.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
117 | -57 | -6.5 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2.2 | 223.7 | 2.5 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
118 | -56 | -6.4 | 0 | 0 | 13.1 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2 | 234 | 2.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
119 | -55 | -6.4 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.3 | 246.8 | 2.4 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
120 | -54 | -6.5 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.4 | 239.9 | 2.3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
121 | -53 | -6.5 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.2 | 225.9 | 2.3 | 12.3 | 11.3 | 11.1 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14 | 15.7 | 15.7 | 15.3
122 | -52 | -6.6 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2.1 | 224 | 2.3 | 12.3 | 11.3 | 11.1 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
123 | -51 | -6.6 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.3 | 11.2 | 22.3 | 10.8 | 2 | 226.9 | 2.2 | 12.3 | 11.3 | 11.1 | 13 | 12.6 | 13.2 | 11.8 | 12 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
124 | -50 | -6.7 | 0 | 0 | 13.2 | 13.3 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.1 | 230.5 | 2.3 | 12.3 | 11.3 | 11.1 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
125 | -49 | -6.6 | 0 | 0 | 13.2 | 13.2 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.3 | 234.7 | 2.6 | 12.3 | 11.3 | 11.1 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14 | 15.7 | 15.7 | 15.2
126 | -48 | -6.6 | 0 | 0 | 13.2 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 2 | 236 | 2.5 | 12.3 | 11.3 | 11.1 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
127 | -47 | -6.6 | 0 | 0 | 13.2 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 1.9 | 236.6 | 2.5 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
128 | -46 | -6.6 | 0 | 0 | 13.2 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 2 | 238.4 | 2.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.5 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
129 | -45 | -6.6 | 0 | 0 | 13.2 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 1.9 | 245.1 | 2.9 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
130 | -44 | -6.6 | 0 | 0 | 13.1 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 1.9 | 229.6 | 2.6 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
131 | -43 | -6.6 | 0 | 0 | 13.1 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 2 | 212.6 | 2.6 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
132 | -42 | -5.4 | 0 | 0 | 13.1 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 2.3 | 211 | 3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
133 | -41 | -4.2 | 0 | 0 | 13.1 | 13.2 | 13.4 | 13 | 14.2 | 11.3 | 22.3 | 10.8 | 2.6 | 211.4 | 3.4 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
134 | -40 | -6.8 | 0 | 0 | 13.1 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.8 | 2.5 | 211.6 | 3.7 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14 | 15.7 | 15.7 | 15.3
135 | -39 | -6.7 | 0 | 0 | 13.1 | 13.2 | 13.4 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.8 | 212.9 | 3.6 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
136 | -38 | -6.7 | 0 | 0 | 13.1 | 13.2 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 2.7 | 213.4 | 3.6 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
137 | -37 | -6.7 | 0 | 0 | 13 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 2.7 | 205.1 | 3.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
138 | -36 | -6.7 | 0 | 0 | 13 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 2.5 | 197.9 | 3.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
139 | -35 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 2.3 | 206.8 | 3.8 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
140 | -34 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 2.1 | 220.4 | 3.9 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
141 | -33 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 1.9 | 224.1 | 3.9 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14 | 15.7 | 15.6 | 15.3
142 | -32 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 2 | 213.4 | 4 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14 | 15.7 | 15.7 | 15.3
143 | -31 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13.1 | 14.2 | 11.2 | 22.3 | 10.8 | 1.9 | 190.2 | 4.1 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
144 | -30 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.8 | 1.8 | 217 | 4.1 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
145 | -29 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.9 | 1.8 | 227.9 | 4.3 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
146 | -28 | -6.7 | 0 | 0 | 13 | 13.2 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.9 | 1.8 | 199.3 | 4.6 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
147 | -27 | -6.7 | 0 | 0 | 13 | 13.2 | 13.3 | 13 | 14.2 | 11.2 | 22.3 | 10.9 | 1.7 | 213.2 | 4.8 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
148 | -26 | -6.7 | 0 | 0 | 13 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.9 | 1.6 | 211.5 | 4.9 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.6 | 15.3
149 | -25 | -6.7 | 0 | 0 | 13.1 | 13.2 | 13.3 | 12.9 | 14.2 | 11.2 | 22.3 | 10.9 | 1.7 | 208.7 | 4.8 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14 | 15.7 | 15.7 | 15.3
150 | -24 | -6.7 | 0 | 0 | 13.1 | 13.2 | 13.3 | 12.9 | 14.2 | 11.1 | 22.2 | 10.9 | 1.7 | 206.6 | 4.5 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.7 | 15.3
151 | -23 | -6.7 | 0 | 0 | 13.1 | 13.2 | 13.2 | 12.9 | 14.2 | 11.1 | 22.3 | 10.9 | 1.9 | 213.8 | 3.8 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
152 | -22 | -6.7 | 0 | 0 | 13.1 | 13.2 | 13.2 | 12.9 | 14.2 | 11.1 | 22.3 | 10.9 | 1.8 | 250.5 | 3.2 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
153 | -21 | -6.7 | 0 | 0 | 13.2 | 13.1 | 13.2 | 12.9 | 14.2 | 11.2 | 22.3 | 10.9 | 1.7 | 276 | 2.9 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
154 | -20 | -6.7 | 0 | 0 | 13.2 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.3 | 10.9 | 1.6 | 277 | 2.4 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
155 | -19 | -6.7 | 0 | 0 | 13.2 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.3 | 10.9 | 1.7 | 270.9 | 2.1 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.7 | 15.2
156 | -18 | -6.7 | 0 | 0 | 13.2 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.3 | 10.9 | 1.7 | 256.4 | 2 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.8 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
157 | -17 | -6.7 | 0 | 0 | 13.2 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.3 | 10.9 | 1.7 | 228.4 | 2.2 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.7 | 15.2
158 | -16 | -6.7 | 0 | 0 | 13.2 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.3 | 10.9 | 1.8 | 206.4 | 3.1 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.6 | 15.2
159 | -15 | -6.7 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 1.9 | 214.8 | 3.4 | 12.3 | 11.2 | 11.1 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.7 | 15.2
160 | -14 | -6.7 | 0 | 0 | 13.1 | 13.1 | 13.2 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 1.9 | 222.3 | 3.9 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
161 | -13 | -6.7 | 0 | 0 | 13.1 | 13.1 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 2.1 | 222.6 | 4 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.7 | 15.3
162 | -12 | -6.7 | 0 | 0 | 13 | 13.1 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 2.2 | 219 | 4.1 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14.1 | 15.7 | 15.6 | 15.3
163 | -11 | -6.7 | 0 | 0 | 13 | 13.1 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 2.1 | 216.4 | 4.6 | 12.3 | 11.2 | 11.2 | 13 | 12.6 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.6 | 15.2
164 | -10 | -6.7 | 0 | 0 | 13 | 13.1 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.2 | 215.8 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.7 | 14 | 15.7 | 15.7 | 15.2
165 | -9 | -6.7 | 0 | 0 | 13 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.4 | 217.2 | 4.9 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.5 | 14.1 | 13.7 | 14 | 15.7 | 15.6 | 15.2
166 | -8 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.3 | 206.7 | 4.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.6 | 15.2
167 | -7 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.2 | 206.3 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.5 | 14.1 | 13.6 | 14.1 | 15.7 | 15.6 | 15.3
168 | -6 | -6.7 | 0 | 0 | 12.8 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.5 | 208.2 | 4.6 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
169 | -5 | -6.7 | 0 | 0 | 12.8 | 13.2 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 2.3 | 206.3 | 4.7 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14 | 15.7 | 15.7 | 15.3
170 | -4 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 2.1 | 206 | 4.8 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.3
171 | -3 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.3 | 211.2 | 5.3 | 12.3 | 11.3 | 11.2 | 13 | 12.6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
172 | -2 | -6.7 | 0 | 0 | 12.9 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.3 | 205.6 | 5.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.5 | 14.1 | 13.6 | 14 | 15.7 | 15.6 | 15.2
173 | -1 | -4.8 | 0 | 0 | 12.9 | 13.2 | 13.3 | 12.7 | 14.2 | 11.2 | 22.2 | 10.9 | 2.1 | 208.7 | 5.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 12 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.5 | 14.1 | 13.6 | 14 | 15.7 | 15.6 | 15.2
174 | 0 | 213.2 | 85.28 | 99.6874 | 12.9 | 13.2 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 2.1 | 210.3 | 5.2 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 12 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.5 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
175 | 1 | 511.1 | 204.44 | 238.9786 | 12.9 | 13.2 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 1.9 | 210.9 | 5.3 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 12 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.7 | 15.2
176 | 2 | 567.8 | 227.12 | 265.4902 | 12.9 | 13.2 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.9 | 1.9 | 205.3 | 6 | 12.3 | 11.3 | 11.2 | 13 | 12.7 | 13.2 | 11.8 | 12 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14 | 15.7 | 15.6 | 15.2
177 | 3 | 528.5 | 211.4 | 247.1144 | 12.9 | 13.2 | 13.3 | 12.8 | 14.2 | 11.2 | 22.2 | 10.8 | 2.1 | 204.3 | 6.6 | 12.3 | 11.4 | 11.4 | 13 | 12.8 | 13.2 | 11.8 | 12 | 13.5 | 13.4 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14.1 | 15.7 | 15.6 | 15.3
178 | 4 | 491.4 | 196.56 | 229.7673 | 13 | 13.2 | 13.3 | 12.9 | 14.2 | 11.3 | 22.2 | 10.8 | 2.1 | 210.7 | 7 | 12.3 | 13 | 16.8 | 13.3 | 13.7 | 13.2 | 12.1 | 13.2 | 13.5 | 13.6 | 15 | 14.8 | 15.6 | 14.6 | 14.1 | 13.6 | 14 | 15.7 | 15.6 | 15.3
179 | 5 | 475 | 190 | 222.0991 | 13 | 13.2 | 13.4 | 13 | 15.5 | 11.3 | 22.2 | 10.8 | 2.3 | 209.5 | 6.8 | 12.3 | 23.2 | 43.6 | 16.4 | 18.3 | 13.2 | 16.7 | 23.7 | 13.5 | 15.7 | 15 | 14.8 | 15.7 | 14.6 | 14.1 | 13.7 | 14.1 | 15.8 | 15.7 | 15.3
180 | 6 | 456.9 | 182.76 | 213.6359 | 13.1 | 13.3 | 13.5 | 13.3 | 27.6 | 11.3 | 22.2 | 10.8 | 2.2 | 212.7 | 6.7 | 12.3 | 42.1 | 85.3 | 19.6 | 32.1 | 13.2 | 25.4 | 37.4 | 13.5 | 19.6 | 15 | 14.8 | 15.7 | 14.5 | 14.1 | 13.7 | 14.1 | 15.9 | 15.7 | 15.3
181 | 7 | 442 | 176.8 | 206.669 | 13.3 | 13.4 | 13.7 | 13.5 | 43.8 | 11.3 | 22.2 | 10.8 | 2.7 | 224.6 | 6 | 12.3 | 63.1 | 125.1 | 23.5 | 50.3 | 13.3 | 34.5 | 51.9 | 13.6 | 26.5 | 15 | 14.8 | 15.7 | 14.5 | 14.2 | 13.9 | 14 | 16 | 15.7 | 15.2
182 | 8 | 433.5 | 173.4 | 202.6946 | 13.7 | 13.6 | 13.9 | 13.9 | 60 | 11.3 | 22.2 | 10.8 | 2.7 | 225.3 | 5.5 | 12.3 | 98.8 | 189.2 | 28.5 | 67 | 13.4 | 51.2 | 87.8 | 13.6 | 33.9 | 15 | 14.8 | 15.8 | 14.5 | 14.2 | 14 | 14.1 | 16.1 | 15.8 | 15.2
183 | 9 | 432.2 | 172.88 | 202.0868 | 14.1 | 13.9 | 14.4 | 14.9 | 80.4 | 11.4 | 22.2 | 10.8 | 2.9 | 218.7 | 5.1 | 12.3 | 131.9 | 216.5 | 31.7 | 80.6 | 13.6 | 69.6 | 118.8 | 13.7 | 41.8 | 15 | 14.8 | 15.8 | 14.5 | 14.4 | 14.2 | 14.1 | 16.3 | 15.9 | 15.3
184 | 10 | 435.9 | 174.36 | 203.8168 | 14.6 | 14.4 | 16.3 | 16.3 | 94.4 | 11.4 | 22.2 | 10.8 | 3 | 228.6 | 4.8 | 12.4 | 180.8 | 268.9 | 36.3 | 96 | 14 | 95.3 | 162.5 | 13.7 | 52.8 | 15 | 14.8 | 15.9 | 14.5 | 15.3 | 14.4 | 14.1 | 16.4 | 16 | 15.3
185 | 11 | 440.8 | 176.32 | 206.1079 | 15.3 | 15.1 | 18.6 | 17.6 | 116.3 | 11.5 | 22.2 | 10.8 | 3.3 | 243.2 | 4.5 | 12.4 | 229.5 | 315.4 | 40.5 | 112.9 | 14.4 | 117.9 | 195.3 | 13.8 | 65.5 | 15 | 14.8 | 16.1 | 14.5 | 18.3 | 14.8 | 14.1 | 16.7 | 16.2 | 15.3
186 | 12 | 443.6 | 177.44 | 207.4171 | 16.5 | 15.8 | 21.8 | 19.1 | 127.1 | 11.6 | 22.2 | 10.8 | 3.6 | 242.7 | 4.1 | 12.5 | 269.3 | 354.3 | 44.6 | 122.7 | 14.9 | 142.6 | 234.4 | 13.8 | 74.3 | 15 | 14.8 | 16.2 | 14.5 | 20.8 | 15.6 | 14.1 | 17 | 16.4 | 15.4
187 | 13 | 444.9 | 177.96 | 208.025 | 18 | 17.2 | 24.8 | 21.6 | 138.7 | 11.6 | 22.2 | 10.8 | 3.7 | 236.6 | 3.9 | 12.5 | 291.8 | 382.1 | 47.7 | 130.7 | 15.7 | 159.2 | 255.3 | 13.9 | 79.8 | 15 | 14.9 | 16.4 | 14.5 | 25.9 | 17.7 | 14.1 | 17.4 | 16.6 | 15.4
188 | 14 | 448 | 179.2 | 209.4745 | 20.4 | 19.1 | 27.7 | 24.4 | 157.4 | 11.7 | 22.2 | 10.8 | 3.6 | 235.8 | 4 | 12.6 | 319.6 | 406.3 | 50.3 | 139 | 16.4 | 172.8 | 272.1 | 14 | 83.9 | 15 | 14.9 | 16.6 | 14.6 | 28.5 | 20 | 14.1 | 17.7 | 16.9 | 15.6
189 | 15 | 448.7 | 179.48 | 209.8018 | 22.6 | 20.9 | 31.4 | 27.3 | 179.6 | 11.8 | 22.2 | 10.8 | 4 | 226.4 | 4.1 | 12.7 | 343.8 | 426.8 | 50.6 | 148.3 | 17.1 | 187.9 | 287.7 | 14.1 | 91.5 | 15 | 14.9 | 16.9 | 14.6 | 29.9 | 22.1 | 14.2 | 18.2 | 17.1 | 15.7
190 | 16 | 449.2 | 179.68 | 210.0356 | 25.1 | 23.5 | 35 | 30.1 | 189.3 | 11.8 | 22.2 | 10.9 | 4 | 217.9 | 4 | 12.8 | 368.2 | 468.5 | 51.9 | 161.1 | 17.9 | 200.4 | 301.4 | 14.2 | 98.7 | 15 | 14.9 | 16.9 | 14.6 | 32 | 24.3 | 14.1 | 18.6 | 17.3 | 15.7
191 | 17 | 450.9 | 180.36 | 210.8304 | 28 | 26.2 | 38.5 | 33.4 | 201.7 | 11.9 | 22.2 | 10.9 | 3.9 | 223 | 3.9 | 13 | 401 | 501.2 | 53.3 | 170.2 | 18.6 | 218.3 | 323.3 | 14.3 | 105.5 | 15 | 14.9 | 17 | 14.6 | 34.3 | 26.1 | 14.2 | 19 | 17.6 | 15.8
192 | 18 | 451.2 | 180.48 | 210.9707 | 30.7 | 29.6 | 42.4 | 36.4 | 217.6 | 11.9 | 22.2 | 10.9 | 3.9 | 227.5 | 3.5 | 13.3 | 407.9 | 506.8 | 54.3 | 176.4 | 19.4 | 225.5 | 323.4 | 14.4 | 110.1 | 15 | 15 | 17.2 | 14.6 | 36.8 | 28 | 14.2 | 19.3 | 17.9 | 15.9
193 | 19 | 452.6 | 181.04 | 211.6253 | 34 | 33.1 | 47.2 | 39.5 | 233.6 | 12 | 22.2 | 11 | 3.8 | 247.7 | 3.1 | 13.6 | 410.4 | 510.2 | 55.6 | 184.2 | 20.1 | 230.7 | 324.6 | 14.6 | 114.7 | 15 | 15 | 17.5 | 14.6 | 39.2 | 29.9 | 14.2 | 19.6 | 18.2 | 16
194 | 20 | 452.6 | 181.04 | 211.6253 | 37.7 | 36.4 | 52.4 | 42.9 | 232.5 | 12 | 22.2 | 11 | 3.5 | 250.6 | 2.7 | 13.9 | 419.7 | 528.2 | 57.6 | 195.2 | 20.9 | 234 | 331.3 | 14.7 | 118.4 | 15 | 15 | 17.6 | 14.6 | 42.5 | 31.7 | 14.3 | 20 | 18.4 | 16
195 | 21 | 453.6 | 181.44 | 212.0929 | 41.1 | 39.7 | 58 | 46.4 | 232.1 | 12.1 | 22.2 | 11.1 | 3.4 | 230.7 | 2.6 | 14.3 | 438.8 | 560.7 | 59.3 | 202 | 21.6 | 238.6 | 345.7 | 14.9 | 123.3 | 15 | 15.1 | 17.8 | 14.7 | 46.4 | 33.7 | 14.3 | 20.4 | 18.6 | 16.1
196 | 22 | 453.7 | 181.48 | 212.1397 | 45.5 | 42.8 | 63.6 | 50.1 | 236.6 | 12.2 | 22.2 | 11.1 | 3.4 | 211.6 | 3.1 | 14.8 | 460.7 | 588 | 61.4 | 208.4 | 22.3 | 246.6 | 363.5 | 15.6 | 127.2 | 15 | 15.1 | 18.1 | 14.7 | 49.6 | 35.9 | 14.3 | 20.9 | 18.8 | 16.2
197 | 23 | 455.3 | 182.12 | 212.8878 | 49.9 | 46 | 68.6 | 54.3 | 250.7 | 12.2 | 22.2 | 11.3 | 3.9 | 215.8 | 3.6 | 15.3 | 481.1 | 595.5 | 63.5 | 223.7 | 23 | 259.6 | 382.4 | 16.3 | 135.1 | 15 | 15.1 | 18.2 | 14.7 | 52.6 | 39.1 | 14.4 | 21.5 | 19.1 | 16.3
198 | 24 | 457.3 | 182.92 | 213.8229 | 54.3 | 50.5 | 73.7 | 58.6 | 258.5 | 12.3 | 22.2 | 11.4 | 3.6 | 223 | 4.2 | 16 | 493.9 | 609.3 | 65.1 | 239.6 | 23.8 | 267.6 | 397.6 | 16.9 | 146.7 | 15 | 15.2 | 18.4 | 14.7 | 55.6 | 42.6 | 14.4 | 22 | 19.5 | 16.4
199 | 25 | 457 | 182.8 | 213.6827 | 58.7 | 53.3 | 78.6 | 63 | 267.2 | 12.4 | 22.2 | 12 | 2.8 | 235.8 | 4 | 16.7 | 510 | 619.3 | 67.3 | 251.4 | 24.7 | 285.5 | 418.3 | 17.8 | 156.8 | 15 | 15.2 | 18.9 | 14.7 | 59.2 | 45.6 | 14.5 | 22.5 | 19.7 | 16.5
200 | 26 | 457.6 | 183.04 | 213.9632 | 63.5 | 56.4 | 82.8 | 67.3 | 282.2 | 12.4 | 22.2 | 12.8 | 2.8 | 243.2 | 3.7 | 17.6 | 538.5 | 640.1 | 71.5 | 264.3 | 25.5 | 301.2 | 443.2 | 19.8 | 165.9 | 15 | 15.3 | 19 | 14.8 | 62.8 | 48.8 | 14.5 | 23.1 | 20 | 16.7
201 | 27 | 457.9 | 183.16 | 214.1035 | 67.6 | 60.2 | 86.3 | 71.2 | 295.7 | 12.5 | 22.2 | 13.7 | 3.3 | 233.1 | 3.4 | 18.5 | 574.1 | 653.9 | 76.8 | 280.9 | 26.5 | 326.1 | 475.8 | 22 | 181.8 | 15 | 15.3 | 19.1 | 14.8 | 66.7 | 51.6 | 14.6 | 23.7 | 20.4 | 16.8
202 | 28 | 459.2 | 183.68 | 214.7113 | 71.5 | 63.6 | 90.4 | 74.9 | 302 | 12.5 | 22.2 | 14.7 | 3.2 | 219.4 | 3.4 | 19.7 | 593.8 | 663.1 | 81.4 | 296 | 27.6 | 339.3 | 488.6 | 23.1 | 191.7 | 15 | 15.4 | 19.3 | 14.8 | 70.7 | 55.1 | 14.6 | 24.4 | 20.8 | 17
203 | 29 | 459.6 | 183.84 | 214.8984 | 74.5 | 67.7 | 95.1 | 78.6 | 305.8 | 12.6 | 22.2 | 15.6 | 3.1 | 231.6 | 3.8 | 21 | 624.2 | 687 | 86.3 | 306.9 | 28.7 | 353.9 | 504.8 | 25.1 | 198.7 | 15 | 15.4 | 19.4 | 14.8 | 73.9 | 58.2 | 14.7 | 25 | 21.2 | 17.1
204 | 30 | 459.9 | 183.96 | 215.0386 | 77.7 | 72 | 100 | 82 | 315.1 | 12.6 | 22.2 | 16.5 | 2.6 | 245 | 4.3 | 22.6 | 647.7 | 705.1 | 92.9 | 318.3 | 29.9 | 371.4 | 525.4 | 27.9 | 208.7 | 15 | 15.5 | 19.5 | 14.8 | 77.4 | 60.8 | 14.7 | 25.7 | 21.6 | 17.2
205 | 31 | 461.6 | 184.64 | 215.8335 | 80.8 | 75.9 | 104.5 | 85.1 | 318.7 | 12.7 | 22.2 | 17.2 | 3.1 | 210.6 | 4.1 | 24.3 | 666.6 | 725.4 | 98.9 | 326.9 | 31 | 389.7 | 551.9 | 30.5 | 217.9 | 15 | 15.5 | 19.8 | 14.8 | 81.2 | 63.4 | 14.8 | 26.5 | 21.9 | 17.4
206 | 32 | 463.3 | 185.32 | 216.6284 | 83.9 | 80.1 | 108.7 | 88.1 | 319.7 | 12.8 | 22.2 | 17.8 | 2.9 | 237.1 | 4 | 26.4 | 690.7 | 735.2 | 102.7 | 337.6 | 32.3 | 403.4 | 574.7 | 33.4 | 225.9 | 15 | 15.6 | 20 | 14.9 | 84.5 | 65.8 | 14.9 | 27.3 | 22.4 | 17.6
207 | 33 | 463.7 | 185.48 | 216.8154 | 87.6 | 83.5 | 112.6 | 91.1 | 327.4 | 12.8 | 22.2 | 18.3 | 2.7 | 258.8 | 4.2 | 28.7 | 691.9 | 729.8 | 106.7 | 350.7 | 33.7 | 408.9 | 572.1 | 34.7 | 234.2 | 15 | 15.7 | 20.3 | 14.9 | 88.1 | 68.3 | 15 | 27.6 | 22.9 | 17.7
208 | 34 | 463.9 | 185.56 | 216.9089 | 91.5 | 86.8 | 115.8 | 94.6 | 340.9 | 12.9 | 22.2 | 18.8 | 3.1 | 218.4 | 3.9 | 31.2 | 687.9 | 720.1 | 110.8 | 363.6 | 35 | 412.7 | 559.4 | 35.6 | 238.4 | 15 | 15.7 | 20.5 | 14.9 | 91.9 | 71.5 | 15 | 28.2 | 23.4 | 17.8
209 | 35 | 464.4 | 185.76 | 217.1427 | 95.2 | 89.2 | 119.4 | 97.6 | 340.7 | 12.9 | 22.2 | 19.4 | 2.9 | 215.5 | 3.9 | 33.9 | 684.9 | 716.4 | 114.1 | 379.9 | 36.3 | 411.9 | 558.5 | 36.3 | 242.6 | 15 | 15.8 | 20.5 | 14.9 | 95.5 | 73.8 | 15.1 | 28.7 | 23.8 | 18
210 | 36 | 463 | 185.2 | 216.4881 | 100.3 | 91.3 | 122.8 | 100.8 | 340.1 | 13 | 22.2 | 20 | 3.3 | 248 | 4.2 | 36.7 | 704.6 | 722.2 | 118.9 | 396.3 | 37.7 | 423.2 | 576.7 | 38 | 255.7 | 15 | 15.9 | 20.6 | 14.9 | 99.4 | 76.9 | 15.2 | 29.1 | 24.1 | 18.2
211 | 37 | 464 | 185.6 | 216.9557 | 103.9 | 93.8 | 126.3 | 104.6 | 341.1 | 13 | 22.2 | 20.5 | 3.4 | 240.5 | 4.4 | 39.6 | 722.8 | 729.1 | 123.1 | 406.7 | 39 | 435 | 590.5 | 39.9 | 266.1 | 15 | 16 | 21 | 14.9 | 102.6 | 81.2 | 15.3 | 29.6 | 24.4 | 18.3
212 | 38 | 464.4 | 185.76 | 217.1427 | 106.7 | 96.9 | 129.9 | 108.2 | 350.1 | 13 | 22.2 | 21 | 3.4 | 235.5 | 4.7 | 42.8 | 727.5 | 726.4 | 127 | 418 | 40.5 | 442 | 593.5 | 42.3 | 274.5 | 15 | 16 | 21.3 | 15 | 105.6 | 85.2 | 15.4 | 30.4 | 24.8 | 18.5
213 | 39 | 464.2 | 185.68 | 217.0492 | 110.3 | 99 | 133.3 | 111.6 | 349.8 | 13.1 | 22.2 | 21.4 | 3.3 | 230.3 | 4.5 | 46 | 725.5 | 725.3 | 130 | 428.2 | 42 | 448.4 | 597 | 44.1 | 280.3 | 15 | 16.1 | 21.5 | 15 | 108.5 | 88 | 15.5 | 31 | 25.3 | 18.7
214 | 40 | 466.3 | 186.52 | 218.0311 | 113.8 | 102.6 | 136.2 | 114.7 | 363.3 | 13 | 22.2 | 21.8 | 3.2 | 247.7 | 4.1 | 49.4 | 730.2 | 729.5 | 135.3 | 436 | 43.5 | 456.4 | 596.2 | 46.2 | 286.4 | 15 | 16.2 | 21.9 | 15 | 112.6 | 90.7 | 15.6 | 31.7 | 25.8 | 18.9
215 | 41 | 467.1 | 186.84 | 218.4052 | 117.7 | 105.3 | 139.6 | 118.1 | 390.1 | 13 | 22.2 | 22.2 | 2.9 | 258.6 | 3.7 | 52.9 | 726.7 | 731.2 | 140.1 | 441.7 | 45.1 | 461.5 | 596.6 | 48 | 292.6 | 15 | 16.3 | 22.4 | 15 | 115.9 | 93.5 | 15.8 | 32.4 | 26.3 | 19.1
216 | 42 | 466.9 | 186.76 | 218.3117 | 118.6 | 107 | 142.9 | 120.7 | 385.1 | 13 | 22.2 | 22.6 | 2.6 | 237.1 | 4 | 56.4 | 708.9 | 721.4 | 143.3 | 442.7 | 46.7 | 459.5 | 585.2 | 48.3 | 295.1 | 15 | 16.4 | 22.5 | 15.1 | 119.4 | 95.8 | 15.9 | 33 | 26.7 | 19.4
217 | 43 | 467.7 | 187.08 | 218.6857 | 119.8 | 110.4 | 145.3 | 123.5 | 407.7 | 12.9 | 22.2 | 23 | 3.2 | 227.4 | 4.4 | 59.9 | 700.3 | 711.1 | 146.4 | 448 | 48.3 | 462.1 | 580.1 | 49.5 | 299.7 | 15 | 16.5 | 22.8 | 15.1 | 123.2 | 98.9 | 16 | 33.8 | 27.1 | 19.5
218 | 44 | 469.1 | 187.64 | 219.3403 | 122.3 | 113 | 147.7 | 126.3 | 420.9 | 12.9 | 22.2 | 23.3 | 3.8 | 263.4 | 4.7 | 63.2 | 706 | 713.8 | 150.6 | 449.7 | 50 | 467.9 | 582.5 | 51.9 | 304.1 | 15 | 16.6 | 23.1 | 15.1 | 127.3 | 101.9 | 16.1 | 34.6 | 27.6 | 19.8
219 | 45 | 469.8 | 187.92 | 219.6677 | 124.9 | 116.7 | 151.1 | 129.3 | 414 | 13 | 22.2 | 23.6 | 3.3 | 257.1 | 4.4 | 66.4 | 693.5 | 713.3 | 152.8 | 452 | 51.6 | 463.1 | 571.5 | 53.1 | 306.3 | 15 | 16.7 | 23.3 | 15.1 | 130.7 | 105.8 | 16.3 | 35.4 | 28.1 | 20
220 | 46 | 469.1 | 187.64 | 219.3403 | 126.5 | 119.9 | 153.6 | 131.8 | 399.4 | 13 | 22.2 | 23.9 | 3.3 | 226.6 | 4.1 | 69.3 | 691.6 | 714.6 | 155.3 | 460.6 | 53.3 | 460.8 | 573.7 | 54 | 309.7 | 15.1 | 16.8 | 23.8 | 15.2 | 135 | 108.4 | 16.5 | 36.1 | 28.6 | 20.3
221 | 47 | 468.9 | 187.56 | 219.2468 | 128.5 | 122.5 | 156.4 | 134 | 390.6 | 12.9 | 22.2 | 24.1 | 3.1 | 233.8 | 4.2 | 72.1 | 693 | 710.5 | 158 | 470.5 | 54.9 | 461.3 | 580.5 | 55.2 | 318.7 | 15.1 | 16.9 | 24.1 | 15.2 | 137.6 | 111.7 | 16.6 | 36.8 | 29.1 | 20.5
222 | 48 | 470.7 | 188.28 | 220.0885 | 130 | 125.1 | 158.9 | 136 | 376.7 | 12.9 | 22.2 | 24.2 | 3 | 239.6 | 4.5 | 74.7 | 699.9 | 709.8 | 161.1 | 476.9 | 56.6 | 457.2 | 579.5 | 56.4 | 321.7 | 15.1 | 17 | 24.2 | 15.2 | 138.9 | 114 | 16.7 | 37.8 | 29.5 | 20.7
223 | 49 | 471.3 | 188.52 | 220.369 | 132.1 | 127 | 160.8 | 137.5 | 361.8 | 12.9 | 22.2 | 24.4 | 3.3 | 242.5 | 5.4 | 77 | 708.3 | 706.8 | 164.8 | 486 | 58.3 | 457 | 581.6 | 57.2 | 325 | 15.1 | 17.1 | 24.4 | 15.2 | 140.6 | 116.3 | 16.8 | 38.2 | 29.9 | 20.9
224 | 50 | 471.7 | 188.68 | 220.556 | 133.8 | 127.7 | 162.6 | 139.1 | 357.1 | 12.9 | 22.2 | 24.7 | 4 | 241 | 5.8 | 79.2 | 715.9 | 697.4 | 168.9 | 496.6 | 59.9 | 459.7 | 590.3 | 58.8 | 335.1 | 15.1 | 17.2 | 24.6 | 15.3 | 142.4 | 119.5 | 17 | 39 | 30.3 | 21.1
225 | 51 | 472.3 | 188.92 | 220.8366 | 135.6 | 130.3 | 165.1 | 139.9 | 355.2 | 12.9 | 22.2 | 25.1 | 3.4 | 238.5 | 5.8 | 81.2 | 718.1 | 699.3 | 172.3 | 506.2 | 61.6 | 465.6 | 599.2 | 60 | 344.6 | 15.1 | 17.3 | 24.9 | 15.3 | 144 | 121.7 | 17.1 | 39.7 | 30.8 | 21.3
226 | 52 | 475.1 | 190.04 | 222.1458 | 137.9 | 132.9 | 167.3 | 140.6 | 353.5 | 12.9 | 22.2 | 25.4 | 2.9 | 245.2 | 5.8 | 83.1 | 736.1 | 712.3 | 175.7 | 514.2 | 63.3 | 475.7 | 613 | 61.9 | 353 | 15.1 | 17.4 | 25.3 | 15.3 | 145.5 | 123.7 | 17.2 | 40.2 | 31.3 | 21.5
227 | 53 | 474 | 189.6 | 221.6315 | 141.3 | 135.4 | 168.8 | 140.8 | 361.8 | 12.9 | 22.2 | 25.7 | 3.3 | 246.1 | 5.7 | 84.8 | 740.8 | 714.5 | 179.3 | 524.9 | 65 | 477 | 616.8 | 63.4 | 361.9 | 15.1 | 17.5 | 25.4 | 15.4 | 146.6 | 125.9 | 17.4 | 41.1 | 31.9 | 21.6
228 | 54 | 473.7 | 189.48 | 221.4912 | 143.8 | 136.6 | 170.1 | 142 | 373 | 12.9 | 22.1 | 26 | 3.1 | 234.1 | 5.7 | 86.2 | 733.8 | 720.5 | 181.7 | 533.6 | 66.7 | 483.5 | 623.2 | 64.9 | 372.3 | 15.1 | 17.6 | 25.5 | 15.4 | 148.3 | 126.9 | 17.5 | 41.8 | 32.4 | 21.8
229 | 55 | 473.2 | 189.28 | 221.2574 | 145.2 | 138.1 | 171.2 | 143.3 | 371.3 | 13 | 22.1 | 26.4 | 2.7 | 238.9 | 5.3 | 87.3 | 735.8 | 719.3 | 184.4 | 539.3 | 68.4 | 481.4 | 617.2 | 65.9 | 375.8 | 15.1 | 17.7 | 25.8 | 15.5 | 150.5 | 128.1 | 17.6 | 42.4 | 32.9 | 22
230 | 56 | 473.6 | 189.44 | 221.4444 | 146.9 | 139.7 | 172.2 | 144 | 385.4 | 13 | 22.1 | 26.7 | 2.9 | 248.5 | 4.7 | 88.6 | 757.7 | 730.7 | 189.3 | 541.9 | 70.4 | 488.6 | 617 | 67.9 | 382.9 | 15.1 | 17.8 | 26.3 | 15.5 | 152.1 | 129.5 | 17.8 | 43.1 | 33.4 | 22.2
231 | 57 | 472.1 | 188.84 | 220.7431 | 149.3 | 141.4 | 172.8 | 145.4 | 398 | 13 | 22.1 | 27 | 3.5 | 254 | 4.5 | 89.9 | 772.4 | 738.4 | 194.1 | 549.8 | 72.4 | 489.2 | 618.3 | 70 | 390 | 15.1 | 17.9 | 26.5 | 15.5 | 153.3 | 131.2 | 17.9 | 43.8 | 33.9 | 22.5
232 | 58 | 473.4 | 189.36 | 221.3509 | 149.4 | 143.2 | 172.8 | 147.4 | 400.1 | 13 | 22.1 | 27.3 | 3.8 | 251.1 | 4.9 | 91.5 | 784.1 | 753 | 197.9 | 558.3 | 74.6 | 496.4 | 628.4 | 72 | 400.2 | 15.1 | 18 | 26.6 | 15.6 | 154.6 | 132.9 | 18 | 44.4 | 34.3 | 22.7
233 | 59 | 473 | 189.2 | 221.1639 | 148.7 | 144.5 | 172 | 148.8 | 398.6 | 13 | 22.1 | 27.7 | 3.7 | 261.1 | 5.1 | 93.2 | 793.7 | 743.9 | 201 | 561.3 | 76.9 | 497.3 | 626.7 | 73.7 | 403.7 | 15.1 | 18.1 | 27 | 15.6 | 156.6 | 134.5 | 18.2 | 45.1 | 34.9 | 22.9
234 | 60 | 472.4 | 188.96 | 220.8834 | 150.2 | 145.8 | 171.7 | 150 | 395.1 | 13.1 | 22.1 | 27.9 | 3.6 | 251.7 | 5.4 | 95 | 790.8 | 729.7 | 203.1 | 561.2 | 79.3 | 493.2 | 616.5 | 75.1 | 405.4 | 15.2 | 18.3 | 27.3 | 15.6 | 158.2 | 135.6 | 18.3 | 45.6 | 35.4 | 23.1
235 | 61 | 472.4 | 188.96 | 220.8834 | 151.9 | 147.5 | 173.2 | 151.3 | 397.4 | 13.1 | 22.1 | 28.3 | 3.5 | 229.8 | 5.4 | 97.1 | 795.9 | 729.3 | 205.7 | 564.8 | 81.6 | 491.2 | 614.8 | 76.1 | 406.9 | 15.2 | 18.4 | 27.6 | 15.7 | 160.1 | 137.7 | 18.6 | 46.1 | 35.9 | 23.3
236 | 62 | 474.7 | 189.88 | 221.9588 | 152.8 | 149.9 | 175.5 | 152 | 395.7 | 13.1 | 22.1 | 28.6 | 3.2 | 232.7 | 5.1 | 99.7 | 789.5 | 713.3 | 206.7 | 567.5 | 83.8 | 486.7 | 614.8 | 77 | 410 | 15.2 | 18.5 | 28 | 15.7 | 162.1 | 140.2 | 18.7 | 46.7 | 36.4 | 23.6
237 | 63 | 477.7 | 191.08 | 223.3615 | 153.5 | 152.6 | 176.8 | 153.1 | 383.6 | 13.2 | 22.1 | 28.8 | 3.6 | 251 | 4.6 | 102.9 | 770.7 | 695.1 | 207.2 | 569.8 | 86.1 | 478.2 | 600.6 | 77.5 | 411.2 | 15.2 | 18.6 | 28.2 | 15.8 | 164.1 | 141.8 | 18.9 | 47.4 | 37 | 23.8
238 | 64 | 478.2 | 191.28 | 223.5953 | 155 | 153.5 | 178 | 154 | 379.1 | 13.2 | 22.1 | 28.9 | 3.7 | 257.3 | 4.4 | 108.1 | 770.5 | 696.7 | 209.8 | 576.4 | 88.3 | 471.7 | 592.8 | 78.7 | 414.6 | 15.2 | 18.7 | 28.4 | 15.8 | 165.8 | 143.5 | 19 | 48.1 | 37.4 | 24
239 | 65 | 478.7 | 191.48 | 223.8291 | 156.8 | 154.4 | 178.5 | 155.1 | 386.8 | 13.2 | 22.1 | 29.1 | 3.7 | 261.2 | 4.1 | 113.6 | 779.8 | 706.9 | 212.5 | 578.4 | 90.5 | 476.3 | 600.6 | 80.5 | 421.4 | 15.2 | 18.9 | 28.5 | 15.9 | 167.3 | 145.7 | 19.2 | 48.9 | 37.8 | 24.2
240 | 66 | 477.9 | 191.16 | 223.455 | 158.9 | 155.7 | 179.3 | 156.4 | 388 | 13.2 | 22.1 | 29.3 | 3.2 | 239.7 | 3.5 | 118.9 | 794.2 | 717.9 | 214.1 | 575.9 | 92.7 | 483.7 | 618.6 | 82.9 | 425.5 | 15.2 | 19 | 28.7 | 15.9 | 168.1 | 148 | 19.3 | 49.9 | 38.2 | 24.5
241 | 67 | 474.6 | 189.84 | 221.912 | 160.2 | 157.3 | 180.4 | 157 | 384.6 | 13.2 | 22.1 | 29.6 | 3.2 | 208 | 3.2 | 124.6 | 808.1 | 739.3 | 216.9 | 582 | 94.9 | 496.1 | 639.5 | 85.8 | 432.6 | 15.2 | 19.1 | 29 | 15.9 | 169 | 149.1 | 19.5 | 50.6 | 38.7 | 24.7
242 | 68 | 476.7 | 190.68 | 222.8939 | 161.5 | 158.9 | 181.9 | 158.2 | 381.7 | 13.3 | 22.1 | 29.8 | 3.4 | 206.1 | 3.1 | 131 | 819.4 | 749.4 | 219.3 | 587.4 | 97.3 | 509.4 | 658.3 | 89.2 | 440 | 15.2 | 19.3 | 29.3 | 16 | 171.1 | 150.3 | 19.7 | 51.1 | 39.4 | 24.9
243 | 69 | 476.6 | 190.64 | 222.8472 | 162 | 160.3 | 182.8 | 159.2 | 384.4 | 13.3 | 22.1 | 30.1 | 3.3 | 215.5 | 3.6 | 138 | 832.7 | 762 | 222.8 | 594.6 | 99.9 | 521.2 | 671.6 | 92 | 451 | 15.2 | 19.4 | 29.7 | 16 | 173.3 | 151.9 | 19.8 | 51.7 | 40.1 | 25.1
244 | 70 | 477.2 | 190.88 | 223.1277 | 162.2 | 161.8 | 183 | 160.6 | 393.1 | 13.4 | 22.1 | 30.3 | 3.2 | 207.5 | 3.8 | 145.4 | 844.8 | 772.9 | 226.4 | 600.4 | 102.5 | 528.6 | 681.8 | 95.5 | 459.8 | 15.3 | 19.5 | 29.9 | 16.1 | 174.1 | 153.7 | 20 | 52.4 | 40.9 | 25.4
245 | 71 | 477.2 | 190.88 | 223.1277 | 162.7 | 162.5 | 182.8 | 161.6 | 395 | 13.4 | 22.1 | 30.5 | 3.5 | 236.4 | 3.5 | 153 | 848.3 | 770.8 | 230.1 | 604.3 | 105.3 | 527.9 | 675 | 98.2 | 462.9 | 15.3 | 19.6 | 30.3 | 16.1 | 175.2 | 155 | 20.2 | 53.1 | 41.6 | 25.7
246 | 72 | 477.8 | 191.12 | 223.4083 | 162.6 | 163.2 | 183.3 | 162.5 | 401.3 | 13.5 | 22.1 | 30.8 | 3.4 | 273.7 | 3.7 | 160.4 | 848.1 | 753.2 | 231.9 | 614 | 108 | 524.6 | 668.7 | 101 | 466.9 | 15.3 | 19.8 | 30.5 | 16.2 | 176.7 | 156.3 | 20.3 | 53.7 | 42.4 | 25.9
247 | 73 | 477.8 | 191.12 | 223.4083 | 162 | 165.1 | 183.6 | 164.1 | 403.6 | 13.5 | 22.1 | 31 | 3.7 | 267.2 | 3.9 | 168.1 | 853.3 | 757.4 | 233.8 | 618.6 | 110.7 | 531.9 | 678.2 | 104.3 | 474 | 15.3 | 19.9 | 30.7 | 16.2 | 178.2 | 157.1 | 20.4 | 54.1 | 42.9 | 26.1
248 | 74 | 476.9 | 190.76 | 222.9874 | 162.2 | 166.1 | 184 | 165.2 | 415.5 | 13.6 | 22 | 31.1 | 3.9 | 260.7 | 4.7 | 176.9 | 859.8 | 769 | 236.2 | 620.7 | 113.5 | 535.5 | 686.8 | 107.2 | 479.7 | 15.3 | 20 | 31.4 | 16.3 | 179.4 | 158.9 | 20.6 | 54.7 | 43.5 | 26.4
249 | 75 | 477.6 | 191.04 | 223.3148 | 164.1 | 166.9 | 185 | 166.2 | 420.9 | 13.7 | 22 | 31.3 | 3.7 | 241.7 | 4.6 | 186 | 859.9 | 771 | 238.6 | 621.8 | 116.3 | 534.8 | 682.9 | 109.4 | 483 | 15.3 | 20.1 | 31.7 | 16.4 | 180.3 | 160 | 20.8 | 55.3 | 44.2 | 26.7
250 | 76 | 477.4 | 190.96 | 223.2212 | 167 | 167.4 | 186.1 | 167.7 | 412.7 | 13.7 | 22 | 31.4 | 3.9 | 210 | 4.5 | 195 | 861.7 | 764 | 240.9 | 626.1 | 119 | 536.1 | 675.7 | 110.8 | 488.6 | 15.3 | 20.3 | 31.8 | 16.4 | 181.7 | 161.2 | 21 | 55.8 | 44.8 | 26.9
251 | 77 | 477.6 | 191.04 | 223.3148 | 168.6 | 167.7 | 186.6 | 168.9 | 410.6 | 13.7 | 22 | 31.5 | 3.5 | 217.4 | 3.8 | 203.6 | 866.9 | 755.7 | 243.3 | 630.7 | 121.6 | 538.1 | 682.9 | 111.8 | 493.1 | 15.3 | 20.4 | 32.1 | 16.5 | 182.5 | 162.1 | 21.2 | 56.7 | 45.3 | 27.2
252 | 78 | 478.2 | 191.28 | 223.5953 | 170.2 | 168.2 | 186.5 | 170.2 | 415.6 | 13.8 | 22 | 31.5 | 4.6 | 242.9 | 3.3 | 211.7 | 873.8 | 753.7 | 246.7 | 635.1 | 124.1 | 539.7 | 682.4 | 113.7 | 499.4 | 15.3 | 20.5 | 32.3 | 16.5 | 183.9 | 162.6 | 21.4 | 57.3 | 45.9 | 27.4
253 | 79 | 475.9 | 190.36 | 222.5199 | 171.4 | 168.8 | 188 | 170.5 | 416.1 | 13.8 | 22 | 31.6 | 4.1 | 249.3 | 3.1 | 219.1 | 876.2 | 760.6 | 251.1 | 641.7 | 126.6 | 546 | 688.4 | 116 | 505.6 | 15.4 | 20.7 | 32.6 | 16.6 | 185.1 | 163.7 | 21.5 | 57.8 | 46.4 | 27.7
254 | 80 | 478.1 | 191.24 | 223.5485 | 172.3 | 169.4 | 188.8 | 170.8 | 422.5 | 13.8 | 22 | 31.7 | 3.5 | 250.7 | 2.8 | 225.6 | 880.1 | 752.4 | 253.1 | 648.3 | 129.2 | 550.6 | 690.2 | 118.3 | 513.3 | 15.4 | 20.8 | 32.8 | 16.7 | 187.4 | 164.9 | 21.7 | 58.4 | 47 | 27.9
255 | 81 | 476.2 | 190.48 | 222.6601 | 173.1 | 169.9 | 189.5 | 172.1 | 420.8 | 13.8 | 22 | 31.7 | 3.4 | 235.3 | 3.1 | 231.3 | 881.9 | 760.7 | 255.5 | 654.5 | 131.7 | 553.6 | 697.1 | 120.5 | 519.2 | 15.4 | 21 | 33.1 | 16.7 | 188.3 | 166 | 21.9 | 59.2 | 47.7 | 28.2
256 | 82 | 477.1 | 190.84 | 223.081 | 173.3 | 171.3 | 189.7 | 173.2 | 408.5 | 13.9 | 22 | 31.8 | 4 | 222 | 4 | 236.5 | 890.2 | 750.3 | 256.7 | 660.4 | 134.2 | 552.9 | 694.9 | 121.6 | 523.7 | 15.4 | 21.1 | 33.4 | 16.8 | 189.6 | 167.6 | 22.1 | 59.9 | 48.4 | 28.5
257 | 83 | 478.4 | 191.36 | 223.6888 | 173.8 | 171.5 | 189.7 | 173.7 | 402.8 | 13.9 | 22 | 31.9 | 3.3 | 202.3 | 4.4 | 241.6 | 900.7 | 752.2 | 259.8 | 665.9 | 136.7 | 553.8 | 698.8 | 123.2 | 531.7 | 15.4 | 21.2 | 33.5 | 16.8 | 190.8 | 169.4 | 22.3 | 60.6 | 49 | 28.8
258 | 84 | 476.9 | 190.76 | 222.9874 | 173.4 | 171.6 | 190.3 | 174.6 | 402 | 14 | 22 | 31.9 | 3.5 | 237.3 | 6.4 | 246.7 | 899.8 | 771.6 | 264 | 670.7 | 139 | 560.3 | 717.3 | 125.4 | 540.6 | 15.4 | 21.4 | 33.7 | 16.9 | 191.5 | 170.1 | 22.5 | 61.2 | 49.5 | 29
259 | 85 | 477.2 | 190.88 | 223.1277 | 174.6 | 172.3 | 190.3 | 175.5 | 401.1 | 14 | 22 | 32 | 4 | 215.2 | 7.5 | 251.8 | 894.3 | 778.8 | 267 | 673 | 141.4 | 570.2 | 732.5 | 127.7 | 545.9 | 15.4 | 21.5 | 34 | 17 | 192.1 | 171.2 | 22.7 | 61.8 | 50.1 | 29.3
260 | 86 | 476.6 | 190.64 | 222.8472 | 175.6 | 172 | 190.8 | 175.3 | 396 | 14.1 | 22 | 32.1 | 3.2 | 237.1 | 7.2 | 256.3 | 892.1 | 772.8 | 268.3 | 679.5 | 143.8 | 564.6 | 719.4 | 128.5 | 547.1 | 15.5 | 21.7 | 34.3 | 17 | 192.7 | 171.8 | 22.9 | 62.4 | 50.7 | 29.5
261 | 87 | 476.5 | 190.6 | 222.8004 | 177 | 172.1 | 191.9 | 175.8 | 400.6 | 14.1 | 22 | 32.2 | 3.4 | 244.8 | 6.8 | 260.3 | 895.8 | 757.3 | 268.4 | 683.4 | 146.1 | 555.5 | 713.5 | 129.1 | 548.1 | 15.5 | 21.8 | 34.7 | 17.1 | 194.5 | 172.7 | 23.1 | 62.9 | 51.3 | 29.8
262 | 88 | 476.2 | 190.48 | 222.6601 | 177.7 | 172.6 | 193.3 | 176.6 | 396.9 | 14.2 | 22 | 32.4 | 3.8 | 247.9 | 6.9 | 263.9 | 893 | 759.8 | 270.7 | 687.3 | 148.5 | 558.4 | 719.4 | 130.7 | 552.7 | 15.5 | 22 | 34.8 | 17.2 | 194.8 | 173.6 | 23.3 | 63.5 | 51.8 | 30
263 | 89 | 477 | 190.8 | 223.0342 | 179.5 | 173 | 193.8 | 177.3 | 401.8 | 14.2 | 22 | 32.6 | 3.3 | 235.5 | 7.6 | 267.3 | 891.4 | 760.9 | 272.9 | 690.6 | 150.8 | 562.1 | 720.1 | 133.5 | 557.7 | 15.5 | 22.1 | 35 | 17.3 | 194.8 | 174.2 | 23.5 | 64.1 | 52.4 | 30.3
264 | 90 | 477 | 190.8 | 223.0342 | 180.3 | 173.5 | 193 | 177.2 | 402.7 | 14.2 | 21.9 | 32.7 | 3.5 | 238.6 | 7.7 | 270.4 | 890.2 | 763.4 | 276.2 | 695.1 | 153.2 | 555.8 | 709.3 | 135.2 | 557.7 | 15.5 | 22.3 | 35.2 | 17.3 | 195 | 174.9 | 23.6 | 64.6 | 53.1 | 30.5
265 | 91 | 475.1 | 190.04 | 222.1458 | 181.4 | 174.2 | 192.3 | 176.1 | 410.4 | 14.2 | 21.9 | 32.9 | 3.5 | 244.6 | 7.6 | 273.5 | 893.6 | 768.2 | 279 | 698.4 | 155.6 | 552.4 | 707.2 | 138.1 | 559.7 | 15.5 | 22.4 | 35.4 | 17.4 | 195.3 | 175.7 | 23.8 | 65.2 | 53.7 | 30.7
266 | 92 | 477.1 | 190.84 | 223.081 | 182 | 174.6 | 192.1 | 176.1 | 411.4 | 14.3 | 21.9 | 33 | 3.5 | 245.9 | 7.8 | 276.7 | 892.4 | 774.2 | 283.1 | 704.1 | 158 | 557.9 | 716.5 | 141.3 | 565.4 | 15.5 | 22.6 | 35.7 | 17.5 | 195.7 | 176.5 | 24 | 65.7 | 54.3 | 30.9
267 | 93 | 475.5 | 190.2 | 222.3328 | 182.4 | 175.3 | 193.1 | 176.8 | 417.4 | 14.3 | 21.9 | 33.2 | 3.6 | 239 | 7.9 | 279.9 | 892.7 | 778.5 | 284.7 | 706.3 | 160.6 | 561.2 | 724.8 | 144.7 | 571.3 | 15.6 | 22.7 | 36.1 | 17.6 | 195.9 | 176.8 | 24.2 | 66.1 | 54.9 | 31.1
268 | 94 | 477.2 | 190.88 | 223.1277 | 183 | 176.1 | 193.1 | 177.8 | 416.6 | 14.3 | 21.9 | 33.4 | 3.4 | 244.6 | 8 | 283.2 | 890.2 | 772.7 | 285.6 | 710.2 | 163.2 | 564.8 | 736.1 | 148 | 576.7 | 15.6 | 22.9 | 36.3 | 17.7 | 196.3 | 177.1 | 24.4 | 66.7 | 55.6 | 31.4
269 | 95 | 476.1 | 190.44 | 222.6134 | 183.7 | 176.9 | 193.6 | 178.5 | 405.8 | 14.4 | 21.9 | 33.5 | 3.6 | 245.1 | 7.9 | 286.4 | 894 | 768.8 | 285.5 | 712.6 | 165.9 | 562.8 | 732.5 | 150.3 | 579.9 | 15.6 | 23 | 36.6 | 17.7 | 196.8 | 178.1 | 24.6 | 67.3 | 56.2 | 31.6
270 | 96 | 475.9 | 190.36 | 222.5199 | 183.6 | 176.8 | 195.1 | 178.4 | 397.1 | 14.4 | 21.9 | 33.6 | 3.2 | 234.6 | 7.6 | 289.5 | 890.3 | 778.9 | 284.9 | 712.8 | 168.6 | 562.5 | 734.8 | 152.2 | 583.5 | 15.6 | 23.2 | 36.9 | 17.8 | 197.5 | 179.4 | 24.7 | 68 | 56.8 | 31.9
271 | 97 | 476.4 | 190.56 | 222.7537 | 183.4 | 176.9 | 195.9 | 178.7 | 388.8 | 14.4 | 21.9 | 33.7 | 3.2 | 229 | 7.5 | 292.6 | 882.8 | 795.8 | 284.1 | 714.7 | 171.3 | 569.6 | 749.8 | 155.3 | 588.1 | 15.6 | 23.3 | 37.3 | 17.9 | 198 | 180.2 | 24.9 | 68.7 | 57.4 | 32.1
272 | 98 | 475.2 | 190.08 | 222.1926 | 184.1 | 177.1 | 195.8 | 179.2 | 386.3 | 14.5 | 21.9 | 33.8 | 3.5 | 232.5 | 7.2 | 295.7 | 877.8 | 800.1 | 283.5 | 715.1 | 174.1 | 577.4 | 759.4 | 159.3 | 593 | 15.6 | 23.5 | 37.6 | 18 | 198.5 | 181.2 | 25.1 | 69.3 | 58.1 | 32.4
273 | 99 | 477.1 | 190.84 | 223.081 | 184.9 | 177.3 | 196.1 | 178.9 | 389.4 | 14.5 | 21.9 | 33.8 | 3.3 | 233.1 | 6.8 | 298.7 | 872.9 | 803.7 | 283.3 | 717 | 177.1 | 578.5 | 759.3 | 162.5 | 595.4 | 15.7 | 23.6 | 37.8 | 18.1 | 198.4 | 182 | 25.2 | 70 | 58.8 | 32.6
274 | 100 | 479.3 | 191.72 | 224.1096 | 184.9 | 176.8 | 196.6 | 179.6 | 394.6 | 14.5 | 21.9 | 34 | 3.5 | 239.4 | 6.5 | 301.6 | 869.1 | 805.2 | 283.6 | 721 | 180.1 | 587 | 765.8 | 166.8 | 601.7 | 15.7 | 23.8 | 38.3 | 18.2 | 198.5 | 182.1 | 25.5 | 70.7 | 59.5 | 32.9
275 | 101 | 479 | 191.6 | 223.9694 | 185.8 | 176.8 | 196.6 | 180.6 | 396.9 | 14.6 | 21.9 | 34.1 | 3.5 | 251.3 | 6 | 304.4 | 873.7 | 795.2 | 284.1 | 724.5 | 183.3 | 590.1 | 762.6 | 170.2 | 606.6 | 15.7 | 23.9 | 38.4 | 18.3 | 199.3 | 182.9 | 25.7 | 71.1 | 60.2 | 33.1
276 | 102 | 478.8 | 191.52 | 223.8758 | 187 | 177.6 | 197.3 | 180.6 | 393.7 | 14.7 | 21.9 | 34.3 | 3.5 | 249.8 | 5.6 | 307.2 | 883 | 780.8 | 284.8 | 729.5 | 186.5 | 591.8 | 764.6 | 173.4 | 609.9 | 15.7 | 24.1 | 38.6 | 18.4 | 200.7 | 183.9 | 25.9 | 71.5 | 60.8 | 33.4
277 | 103 | 475.5 | 190.2 | 222.3328 | 187.7 | 178.3 | 198.7 | 180.2 | 394.3 | 14.8 | 21.9 | 34.4 | 3.5 | 256.9 | 5.4 | 309.8 | 885.2 | 772 | 285.8 | 731.7 | 189.8 | 594.1 | 761.9 | 176.9 | 613.1 | 15.7 | 24.3 | 39 | 18.4 | 201.6 | 184.6 | 26.1 | 72.1 | 61.4 | 33.6
278 | 104 | 475.2 | 190.08 | 222.1926 | 188.2 | 178.8 | 198.8 | 179.8 | 394.5 | 14.9 | 21.9 | 34.5 | 3.8 | 264.8 | 5.2 | 312.4 | 885.8 | 786.7 | 287.5 | 734.1 | 193 | 598.6 | 766.4 | 179.8 | 618.5 | 15.8 | 24.4 | 39.3 | 18.5 | 202.4 | 185.1 | 26.3 | 72.7 | 62 | 33.9
279 | 105 | 475.7 | 190.28 | 222.4264 | 189.4 | 179.4 | 198.9 | 180.2 | 391.1 | 14.9 | 21.9 | 34.5 | 3.7 | 253.9 | 5 | 314.9 | 889.8 | 779.7 | 290 | 737.4 | 196.3 | 596.9 | 755.9 | 181.7 | 621.5 | 15.8 | 24.6 | 39.6 | 18.6 | 204.4 | 186 | 26.5 | 73.1 | 62.7 | 34.2
280 | 106 | 476.1 | 190.44 | 222.6134 | 189.8 | 180.3 | 198.9 | 180.9 | 386.8 | 15 | 21.9 | 34.5 | 3.4 | 255.7 | 4.9 | 317.2 | 889.7 | 780.2 | 292.4 | 741 | 199.5 | 605 | 768.9 | 184.3 | 628.4 | 15.8 | 24.7 | 39.9 | 18.7 | 205.3 | 187.1 | 26.6 | 73.7 | 63.3 | 34.5
281 | 107 | 475.8 | 190.32 | 222.4731 | 190.3 | 181.1 | 198.1 | 181.5 | 387.4 | 15.1 | 21.9 | 34.6 | 3.3 | 262.8 | 4.8 | 319.5 | 881.3 | 789.5 | 295 | 740.5 | 202.8 | 610 | 770.4 | 187.2 | 632.7 | 15.8 | 24.9 | 40.2 | 18.8 | 206 | 188 | 26.8 | 74.1 | 63.9 | 34.7
282 | 108 | 476.2 | 190.48 | 222.6601 | 190.8 | 181.4 | 199 | 182.1 | 384.9 | 15.2 | 21.9 | 34.7 | 3.5 | 246.8 | 4.4 | 321.7 | 883.1 | 790.5 | 298 | 740.8 | 206 | 606.2 | 763.9 | 188.4 | 631.5 | 15.8 | 25.1 | 40.4 | 18.9 | 206 | 188.6 | 27.1 | 74.8 | 64.6 | 35
283 | 109 | 476.8 | 190.72 | 222.9407 | 189.9 | 181.9 | 199.9 | 182.2 | 384.9 | 15.3 | 21.9 | 34.8 | 3.7 | 252.1 | 4 | 323.9 | 878.4 | 799.2 | 301.2 | 742.2 | 209.2 | 613.6 | 764.6 | 191.1 | 635.3 | 15.8 | 25.2 | 40.6 | 19 | 206.3 | 188.9 | 27.2 | 75.3 | 65.2 | 35.3
284 | 110 | 477.2 | 190.88 | 223.1277 | 188.8 | 182.4 | 200.3 | 182.6 | 390.6 | 15.4 | 21.8 | 35 | 3.6 | 283.7 | 4 | 326.2 | 880.1 | 801.9 | 304.6 | 744.5 | 212.3 | 612.8 | 756.1 | 193 | 638.6 | 15.9 | 25.4 | 40.8 | 19.1 | 206.5 | 189.4 | 27.4 | 75.8 | 65.8 | 35.5
285 | 111 | 475.8 | 190.32 | 222.4731 | 189.3 | 182.6 | 201 | 182.5 | 404 | 15.4 | 21.8 | 35.2 | 3.5 | 275.9 | 3.5 | 328.3 | 882.3 | 791.4 | 308.4 | 746.1 | 215.5 | 617.8 | 757.1 | 195.5 | 642.1 | 15.9 | 25.6 | 41.2 | 19.2 | 207 | 189.8 | 27.6 | 76.3 | 66.5 | 35.7
286 | 112 | 477.1 | 190.84 | 223.081 | 190 | 181.6 | 201.7 | 182.5 | 425.5 | 15.5 | 21.8 | 35.4 | 3.7 | 241 | 3.3 | 330.3 | 882.4 | 784.9 | 312.3 | 746.2 | 218.8 | 623.9 | 758.6 | 198.7 | 646.2 | 15.9 | 25.8 | 41.7 | 19.3 | 207.4 | 190.4 | 27.8 | 76.9 | 67.3 | 36
287 | 113 | 476.7 | 190.68 | 222.8939 | 190.2 | 180.5 | 201.9 | 182.6 | 428.2 | 15.5 | 21.8 | 35.5 | 3.8 | 224.3 | 3.6 | 332.1 | 874.3 | 791.5 | 316.3 | 748.4 | 222 | 626 | 755.9 | 202.4 | 648.4 | 15.9 | 25.9 | 42 | 19.4 | 208 | 191 | 27.9 | 77.4 | 68.1 | 36.2
288 | 114 | 477.3 | 190.92 | 223.1745 | 191.1 | 180.2 | 202.4 | 183.3 | 427.3 | 15.6 | 21.8 | 35.7 | 3.7 | 225.1 | 3.7 | 333.7 | 873.9 | 790 | 320.3 | 749.6 | 225.3 | 625.5 | 758.1 | 205.6 | 650.1 | 15.9 | 26.1 | 42.2 | 19.5 | 208.4 | 191.6 | 28.1 | 77.9 | 68.9 | 36.4
289 | 115 | 477.9 | 191.16 | 223.455 | 192.7 | 179.6 | 203.7 | 184.1 | 422.1 | 15.6 | 21.8 | 35.8 | 3.9 | 237.9 | 3.8 | 335.2 | 877.5 | 779 | 323.8 | 751.7 | 228.5 | 621.4 | 752.1 | 208.5 | 651.4 | 16 | 26.3 | 42.5 | 19.6 | 208.8 | 191.9 | 28.4 | 78.5 | 69.7 | 36.7
290 | 116 | 477.8 | 191.12 | 223.4083 | 193.4 | 179.1 | 204.3 | 184.7 | 421 | 15.6 | 21.8 | 35.9 | 4.1 | 266.8 | 4 | 336.7 | 877.7 | 776.6 | 327.7 | 751 | 231.7 | 616.2 | 742.2 | 211.3 | 651.1 | 16 | 26.5 | 42.7 | 19.7 | 208.9 | 192.3 | 28.6 | 78.8 | 70.4 | 37
291 | 117 | 477.8 | 191.12 | 223.4083 | 192.3 | 177.8 | 203.2 | 185 | 457 | 15.7 | 21.8 | 36.1 | 3.9 | 261.8 | 4.1 | 338.2 | 879.6 | 771.1 | 331.8 | 751.2 | 234.8 | 608.8 | 724.6 | 213.8 | 650.4 | 16 | 26.6 | 43.3 | 19.8 | 210.4 | 193 | 28.8 | 79.3 | 71.1 | 37.2
292 | 118 | 477.8 | 191.12 | 223.4083 | 191.8 | 176.9 | 201.8 | 185.4 | 467 | 15.7 | 21.8 | 36.3 | 3.4 | 226.3 | 3.9 | 339.8 | 879.1 | 746.3 | 335.8 | 752.7 | 237.9 | 597.1 | 710.3 | 215.2 | 650.4 | 16 | 26.8 | 43.5 | 20 | 211.3 | 193.4 | 29 | 79.9 | 71.7 | 37.5
293 | 119 | 478.3 | 191.32 | 223.6421 | 192.2 | 177.8 | 202 | 186.4 | 473 | 15.8 | 21.8 | 36.3 | 3.5 | 213.5 | 3.6 | 341.1 | 880.2 | 730.1 | 340.5 | 754.6 | 241 | 592 | 703.8 | 217.6 | 650.8 | 16 | 27 | 44.1 | 20.1 | 212.5 | 193.8 | 29.3 | 80.4 | 72.3 | 37.8
294 | 120 | 478.7 | 191.48 | 223.8291 | 192.1 | 179.9 | 203.6 | 186.7 | 479.7 | 15.8 | 21.8 | 36.4 | 3.7 | 215.3 | 3.4 | 342.3 | 880.2 | 724.8 | 345.2 | 754.6 | 244 | 587.9 | 696.1 | 219.6 | 649.8 | 16.1 | 27.2 | 44.5 | 20.2 | 213 | 194.8 | 29.5 | 81.2 | 72.9 | 38.1
295 | 121 | 478.7 | 191.48 | 223.8291 | 192.9 | 181 | 204.8 | 186.7 | 478.1 | 15.9 | 21.8 | 36.6 | 3.5 | 242.9 | 2.9 | 343.5 | 879.1 | 733.5 | 350 | 752.3 | 246.8 | 579 | 684.9 | 220.7 | 648.1 | 16.1 | 27.3 | 44.7 | 20.3 | 213.7 | 195.1 | 29.7 | 81.6 | 73.4 | 38.4
296 | 122 | 478.1 | 191.24 | 223.5485 | 193.3 | 181.1 | 205.5 | 187.9 | 467.3 | 16 | 21.8 | 36.7 | 3.4 | 270.3 | 2.6 | 344.6 | 875.9 | 738.9 | 354.7 | 752.6 | 249.3 | 568.2 | 678.1 | 221.8 | 647.4 | 16.1 | 27.5 | 44.9 | 20.4 | 215.3 | 196 | 29.9 | 82.1 | 74 | 38.7
297 | 123 | 478.4 | 191.36 | 223.6888 | 194 | 180.9 | 206.8 | 188.1 | 464.8 | 16.1 | 21.8 | 36.9 | 3.3 | 278.4 | 2.5 | 345.7 | 877 | 740.2 | 359.4 | 752.6 | 251.6 | 558.1 | 670.4 | 222.4 | 646.2 | 16.1 | 27.7 | 45.3 | 20.5 | 215.7 | 196.4 | 30.2 | 82.8 | 74.5 | 39
298 | 124 | 478.2 | 191.28 | 223.5953 | 195.4 | 182.2 | 208.3 | 188.6 | 465.6 | 16.1 | 21.8 | 37 | 3.8 | 261 | 2.6 | 346.8 | 881 | 734.8 | 364.6 | 754.4 | 253.6 | 555 | 663.5 | 223.2 | 646 | 16.1 | 27.9 | 45.6 | 20.6 | 216.6 | 197.1 | 30.4 | 83.4 | 75 | 39.3
299 | 125 | 478.4 | 191.36 | 223.6888 | 195.6 | 184.7 | 209.2 | 189.4 | 473.7 | 16.1 | 21.8 | 37.1 | 3.7 | 247.3 | 2.7 | 347.7 | 877.3 | 724.5 | 369.8 | 755.1 | 255.6 | 549.5 | 656.6 | 224.4 | 646.5 | 16.2 | 28.1 | 45.9 | 20.7 | 216.6 | 197.8 | 30.7 | 84 | 75.6 | 39.6
300 | 126 | 477.9 | 191.16 | 223.455 | 196.2 | 185.4 | 209.5 | 190.5 | 468.9 | 16.1 | 21.8 | 37.2 | 3.5 | 235.4 | 3 | 348.7 | 871.4 | 701.6 | 374.8 | 756.2 | 257.5 | 541.7 | 643 | 224.5 | 644.7 | 16.2 | 28.2 | 46.2 | 20.9 | 216.8 | 198 | 30.8 | 84.4 | 76.1 | 39.9
301 | 127 | 478.3 | 191.32 | 223.6421 | 199.2 | 186.5 | 209.6 | 191.4 | 466.5 | 16.2 | 21.8 | 37.4 | 3.1 | 230.6 | 3.2 | 349.6 | 866.3 | 697.6 | 380 | 757.5 | 259.3 | 536.2 | 640.1 | 224.9 | 644.5 | 16.2 | 28.4 | 46.4 | 21 | 218.2 | 198.3 | 31.1 | 84.9 | 76.7 | 40.2
302 | 128 | 478.2 | 191.28 | 223.5953 | 200.2 | 187.3 | 210.3 | 191.5 | 463.7 | 16.2 | 21.7 | 37.7 | 3.3 | 241.3 | 3.6 | 350.4 | 869 | 704.8 | 385.1 | 758.7 | 261 | 531.7 | 641.7 | 226.6 | 645.4 | 16.2 | 28.6 | 46.8 | 21.1 | 219.8 | 198.8 | 31.3 | 85.4 | 77.2 | 40.4
303 | 129 | 478 | 191.2 | 223.5018 | 200.4 | 186.6 | 211.1 | 192.5 | 450.9 | 16.2 | 21.7 | 38 | 3.7 | 242.4 | 3.7 | 351.2 | 862.3 | 701.1 | 390.3 | 760.5 | 262.6 | 529.4 | 640.8 | 228.1 | 646.4 | 16.3 | 28.8 | 47 | 21.2 | 220.2 | 199.4 | 31.5 | 86.2 | 77.7 | 40.8
304 | 130 | 478.8 | 191.52 | 223.8758 | 200.9 | 186 | 211.2 | 193.1 | 454.6 | 16.2 | 21.7 | 38.4 | 3.7 | 237.7 | 3.5 | 352 | 868 | 715.9 | 395.7 | 762.1 | 264.3 | 529.5 | 641 | 230.7 | 649.2 | 16.3 | 29 | 47.3 | 21.3 | 221.2 | 199.4 | 31.7 | 86.7 | 78.3 | 41.1
305 | 131 | 478.4 | 191.36 | 223.6888 | 199.8 | 186.3 | 211.3 | 192.1 | 450.4 | 16.2 | 21.7 | 38.7 | 3.5 | 228.4 | 3.1 | 352.8 | 867.3 | 701.5 | 401.3 | 764.8 | 266 | 529.1 | 637 | 232.3 | 649.5 | 16.3 | 29.1 | 47.7 | 21.5 | 222.5 | 200.1 | 32 | 87.1 | 78.8 | 41.4
306 | 132 | 478.9 | 191.56 | 223.9226 | 199.9 | 186.4 | 211.5 | 191.4 | 442.8 | 16.3 | 21.7 | 38.9 | 3.5 | 204.1 | 2.7 | 353.5 | 869.3 | 703 | 407.5 | 765.2 | 267.7 | 525.9 | 641.2 | 233.5 | 649.7 | 16.3 | 29.3 | 47.9 | 21.6 | 222.3 | 201 | 32.2 | 87.7 | 79.4 | 41.6
307 | 133 | 479 | 191.6 | 223.9694 | 199.1 | 187.2 | 212.8 | 191.5 | 440.4 | 16.3 | 21.7 | 39 | 3.5 | 195.9 | 2.4 | 354.3 | 873.3 | 709.8 | 413.5 | 768 | 269.3 | 530.4 | 651.7 | 235.8 | 651.3 | 16.4 | 29.5 | 48.2 | 21.7 | 222.3 | 201.5 | 32.4 | 88 | 79.8 | 41.8
308 | 134 | 478.2 | 191.28 | 223.5953 | 198.5 | 187.8 | 213.7 | 191.8 | 437.1 | 16.3 | 21.7 | 39.1 | 3.4 | 203.3 | 2.2 | 355.6 | 877.3 | 727.4 | 419.2 | 767.1 | 270.9 | 535.9 | 663.9 | 238.1 | 654 | 16.4 | 29.7 | 48.4 | 21.8 | 223 | 202 | 32.6 | 88.4 | 80.4 | 42.1
309 | 135 | 479.1 | 191.64 | 224.0161 | 199.8 | 187.7 | 213.5 | 191.9 | 439.5 | 16.3 | 21.7 | 39.2 | 3.1 | 217 | 2 | 357.2 | 878.3 | 736.3 | 424.5 | 768.9 | 272.7 | 546.1 | 677.3 | 240.6 | 658.1 | 16.4 | 29.9 | 48.7 | 21.9 | 223.5 | 202.6 | 32.9 | 88.9 | 81.1 | 42.5
310 | 136 | 478.6 | 191.44 | 223.7823 | 200.8 | 188.3 | 213.6 | 192.3 | 432.9 | 16.4 | 21.7 | 39.3 | 3.3 | 235.1 | 2 | 358.9 | 879.2 | 754.4 | 429.9 | 770 | 274.4 | 555.3 | 692.4 | 243.2 | 660.9 | 16.4 | 30 | 49.2 | 22.1 | 223.7 | 203.7 | 33.1 | 89.4 | 81.8 | 42.8
311 | 137 | 479.8 | 191.92 | 224.3434 | 200.9 | 188.8 | 213.8 | 192.5 | 432.8 | 16.5 | 21.7 | 39.4 | 3.9 | 232.3 | 2.3 | 360.8 | 875.6 | 765.1 | 435.5 | 770.6 | 276.2 | 558.1 | 693.2 | 244.5 | 662.4 | 16.5 | 30.2 | 49.5 | 22.2 | 224.1 | 204.2 | 33.4 | 89.9 | 82.4 | 43.1
312 | 138 | 479.2 | 191.68 | 224.0629 | 201.4 | 188.1 | 214.4 | 192.7 | 433.3 | 16.5 | 21.7 | 39.4 | 4 | 205.9 | 3 | 362.5 | 877.2 | 764.2 | 441.8 | 775.9 | 278 | 561.4 | 691.4 | 245.8 | 664.7 | 16.5 | 30.4 | 49.8 | 22.3 | 224.8 | 204.4 | 33.5 | 90.3 | 83.1 | 43.4
313 | 139 | 478 | 191.2 | 223.5018 | 202.8 | 186.8 | 214.6 | 192.4 | 435 | 16.6 | 21.7 | 39.5 | 4.1 | 221.8 | 3.9 | 364.2 | 878.8 | 766.2 | 448.3 | 780 | 279.7 | 564.6 | 697 | 247 | 667.3 | 16.5 | 30.6 | 50.1 | 22.5 | 225 | 205.6 | 33.7 | 90.9 | 83.8 | 43.7
314 | 140 | 479.4 | 191.76 | 224.1564 | 203.5 | 184.8 | 215.2 | 193 | 441.5 | 16.7 | 21.7 | 39.6 | 3.8 | 216.7 | 4.7 | 366.1 | 879.8 | 751.8 | 455 | 782.1 | 281.5 | 564 | 696.6 | 247.8 | 669.5 | 16.5 | 30.8 | 50.6 | 22.6 | 224.8 | 206.2 | 33.9 | 91.6 | 84.4 | 44
315 | 141 | 477.5 | 191 | 223.268 | 204.2 | 184.5 | 216.2 | 193.8 | 442.6 | 16.7 | 21.7 | 39.7 | 3.6 | 193.5 | 5.6 | 368.1 | 874.4 | 743.3 | 461.8 | 781.6 | 283.2 | 563.9 | 686.8 | 247.9 | 668.7 | 16.6 | 30.9 | 50.9 | 22.7 | 224.8 | 206.3 | 34.1 | 92.1 | 85 | 44.3
316 | 142 | 477.6 | 191.04 | 223.3148 | 205.2 | 185 | 216.6 | 194.3 | 443.8 | 16.7 | 21.6 | 39.8 | 4.1 | 209.4 | 5.9 | 370 | 869.7 | 741 | 469.2 | 780.2 | 284.8 | 560.5 | 679.1 | 247.7 | 668.1 | 16.6 | 31.1 | 51.2 | 22.8 | 224.7 | 206 | 34.4 | 92.4 | 85.6 | 44.5
317 | 143 | 478.7 | 191.48 | 223.8291 | 205.7 | 185.7 | 216.8 | 195.2 | 445.4 | 16.7 | 21.7 | 39.8 | 3.6 | 199.7 | 6 | 371.7 | 861.9 | 733.8 | 476.1 | 778.5 | 286.3 | 555.9 | 667.1 | 247.7 | 665.9 | 16.6 | 31.3 | 51.4 | 23 | 225 | 206.3 | 34.6 | 92.9 | 86.1 | 44.8
318 | 144 | 478.5 | 191.4 | 223.7356 | 207.1 | 186.3 | 217.5 | 196 | 449.9 | 16.7 | 21.6 | 39.8 | 3.7 | 192.1 | 6.1 | 373.3 | 854.2 | 724.9 | 482.8 | 779.2 | 287.8 | 550.7 | 655.3 | 247.7 | 666 | 16.7 | 31.5 | 51.7 | 23.1 | 225.8 | 206.2 | 34.7 | 93.4 | 86.6 | 45.1
319 | 145 | 478.1 | 191.24 | 223.5485 | 208 | 186.2 | 217.3 | 196.6 | 476 | 16.8 | 21.6 | 39.8 | 4 | 200.3 | 6.4 | 374.7 | 853 | 729.9 | 490.2 | 782 | 289.2 | 557.3 | 661.1 | 249 | 669.1 | 16.7 | 31.7 | 52.2 | 23.2 | 226 | 206.3 | 34.9 | 93.9 | 87.2 | 45.4
320 | 146 | 478.8 | 191.52 | 223.8758 | 208.7 | 186.7 | 217.8 | 197.4 | 481.5 | 16.9 | 21.6 | 39.9 | 4 | 195.6 | 7.3 | 376 | 853 | 720.3 | 498.4 | 782.1 | 290.7 | 558.5 | 662.9 | 249.7 | 671.4 | 16.7 | 31.9 | 52.8 | 23.4 | 226.2 | 206.8 | 35.2 | 94.4 | 87.8 | 45.7
321 | 147 | 478.8 | 191.52 | 223.8758 | 209.7 | 188.1 | 218.8 | 197.8 | 477.3 | 16.9 | 21.6 | 39.9 | 3.9 | 199.7 | 7.7 | 377.2 | 852.7 | 715.7 | 505.8 | 783.6 | 292.1 | 557 | 658.4 | 249.8 | 671.3 | 16.7 | 32.1 | 53 | 23.5 | 226.6 | 207.3 | 35.4 | 94.8 | 88.4 | 46
322 | 148 | 478 | 191.2 | 223.5018 | 210.6 | 188.6 | 219 | 198.1 | 478.8 | 17 | 21.6 | 40 | 3.5 | 207.2 | 7.7 | 378.3 | 852.3 | 723.7 | 513.7 | 784.3 | 293.6 | 554.8 | 657.2 | 249.6 | 669.8 | 16.8 | 32.2 | 53.3 | 23.7 | 227 | 207.4 | 35.6 | 95.4 | 89 | 46.2
323 | 149 | 480.6 | 192.24 | 224.7175 | 211.5 | 189.2 | 220 | 198.9 | 488.2 | 17.1 | 21.6 | 40.1 | 3.6 | 203.2 | 7.2 | 379.4 | 855 | 720.8 | 521.6 | 784.8 | 295 | 555.1 | 661.8 | 249.7 | 670 | 16.8 | 32.4 | 53.7 | 23.8 | 227.1 | 207.8 | 35.8 | 96 | 89.6 | 46.5
324 | 150 | 480.4 | 192.16 | 224.624 | 212.7 | 190.2 | 221.6 | 199.4 | 489.4 | 17.1 | 21.6 | 40.2 | 3.6 | 202.9 | 6.9 | 380.6 | 856.1 | 707.6 | 531.9 | 787.8 | 296.5 | 551.2 | 653.1 | 249.4 | 671.2 | 16.8 | 32.6 | 54.1 | 23.9 | 227.5 | 208.3 | 36.1 | 96.5 | 90.1 | 46.8
325 | 151 | 480.3 | 192.12 | 224.5772 | 212.4 | 189.8 | 221.6 | 199.9 | 479.8 | 17.2 | 21.6 | 40.3 | 3.8 | 207.2 | 6.6 | 382 | 855.3 | 695.1 | 542.1 | 789 | 298 | 552.7 | 651.8 | 248.9 | 671.3 | 16.8 | 32.8 | 54.4 | 24.1 | 228.1 | 208.6 | 36.3 | 97 | 90.7 | 47.1
326 | 152 | 480.2 | 192.08 | 224.5305 | 213.3 | 189.4 | 221.8 | 200.4 | 472.3 | 17.2 | 21.6 | 40.5 | 3.8 | 209.3 | 6 | 383.5 | 853.3 | 684.6 | 551.9 | 787.9 | 299.4 | 546.9 | 640.2 | 248.8 | 670.2 | 16.9 | 33 | 55.1 | 24.2 | 228.8 | 209.2 | 36.5 | 97.5 | 91.2 | 47.4
327 | 153 | 480.1 | 192.04 | 224.4837 | 213.5 | 190.3 | 222.9 | 201.3 | 496.9 | 17.2 | 21.6 | 40.6 | 3.6 | 209.2 | 5.8 | 385 | 850 | 676.6 | 561 | 788.5 | 300.9 | 549.3 | 635.8 | 248.9 | 670.4 | 16.9 | 33.2 | 55.5 | 24.4 | 229.5 | 209.6 | 36.7 | 97.9 | 91.7 | 47.7
328 | 154 | 478.3 | 191.32 | 223.6421 | 215.2 | 191.2 | 224.3 | 202 | 534 | 17.3 | 21.6 | 40.7 | 3.4 | 217.6 | 5.5 | 386.5 | 847.3 | 692.7 | 571.4 | 787.4 | 302.4 | 558.4 | 640.5 | 249.5 | 672.7 | 16.9 | 33.4 | 55.8 | 24.5 | 230.3 | 209.9 | 36.9 | 98.4 | 92.3 | 48
329 | 155 | 479.4 | 191.76 | 224.1564 | 216.5 | 191.6 | 225.1 | 203 | 545.4 | 17.4 | 21.6 | 40.8 | 3.7 | 215.4 | 4.9 | 388.1 | 846.9 | 695.6 | 582.6 | 789.2 | 303.8 | 564.1 | 637 | 250.4 | 673.2 | 17 | 33.6 | 56.2 | 24.7 | 231.4 | 210.8 | 37.2 | 98.9 | 92.9 | 48.1
330 | 156 | 478.9 | 191.56 | 223.9226 | 218.4 | 192.6 | 225.4 | 203.4 | 546.8 | 17.4 | 21.6 | 41 | 3.8 | 203.7 | 4.5 | 389.9 | 844.3 | 698.9 | 593.1 | 786.4 | 305.3 | 566.5 | 636.1 | 251.2 | 673.4 | 17 | 33.8 | 56.6 | 24.8 | 232.3 | 211.4 | 37.4 | 99.3 | 93.5 | 48.5
331 | 157 | 479.2 | 191.68 | 224.0629 | 219.1 | 194.6 | 227 | 204.6 | 561.2 | 17.5 | 21.6 | 41.1 | 4.2 | 215.2 | 5.1 | 391.7 | 837.4 | 713.7 | 601.2 | 781.2 | 306.8 | 563.9 | 634 | 251.7 | 672.4 | 17 | 34 | 57.1 | 24.9 | 232.9 | 212.1 | 37.6 | 99.9 | 94.2 | 48.9
332 | 158 | 479.9 | 191.96 | 224.3902 | 219.5 | 196.2 | 227.3 | 204.5 | 548.5 | 17.5 | 21.6 | 41.1 | 3.7 | 207.9 | 5.8 | 393.4 | 832.2 | 742.2 | 607.2 | 778.6 | 308.3 | 564.9 | 653.1 | 252 | 672.7 | 17.1 | 34.2 | 57 | 25.1 | 233 | 212.4 | 37.8 | 100.6 | 94.9 | 49.2
333 | 159 | 479.3 | 191.72 | 224.1096 | 219.7 | 197 | 226.3 | 204.8 | 517.6 | 17.6 | 21.6 | 41.1 | 3.4 | 190.8 | 6.3 | 395.3 | 827.2 | 755.7 | 613.4 | 780.5 | 309.7 | 570.1 | 670.2 | 252.1 | 674.8 | 17.1 | 34.4 | 57.1 | 25.2 | 233.3 | 213.2 | 38.1 | 101.1 | 95.5 | 49.5
334 | 160 | 479.8 | 191.92 | 224.3434 | 219.7 | 197.9 | 225.8 | 204.7 | 499 | 17.6 | 21.6 | 41.1 | 3.6 | 200.3 | 6.2 | 397.2 | 824.4 | 769.2 | 620.6 | 784.9 | 311.2 | 575.7 | 677.1 | 252.5 | 676.9 | 17.1 | 34.6 | 57.6 | 25.4 | 234 | 214.5 | 38.3 | 101.7 | 96.2 | 49.8
335 | 161 | 479.4 | 191.76 | 224.1564 | 219.4 | 198.4 | 224.7 | 204.4 | 487.6 | 17.7 | 21.6 | 41 | 3.9 | 202.5 | 6.3 | 399.2 | 826.8 | 771.8 | 629.9 | 787.2 | 312.7 | 575.7 | 680 | 252.6 | 677.4 | 17.2 | 34.8 | 57.9 | 25.5 | 234.1 | 215.6 | 38.5 | 102.4 | 96.9 | 50.1
336 | 162 | 479.5 | 191.8 | 224.2031 | 218.6 | 199.2 | 224.1 | 204.9 | 485.8 | 17.8 | 21.6 | 41 | 3.5 | 205 | 6.2 | 401.4 | 827.7 | 774 | 637.3 | 790.6 | 314.3 | 582.8 | 692.5 | 253 | 680.3 | 17.2 | 35 | 58.5 | 25.7 | 234.1 | 216 | 38.7 | 102.9 | 97.5 | 50.3
337 | 163 | 478.9 | 191.56 | 223.9226 | 217.9 | 200 | 224.6 | 205.3 | 498.3 | 17.8 | 21.6 | 41 | 3.7 | 210.3 | 6 | 403.8 | 828.8 | 767.1 | 644.7 | 791.3 | 315.9 | 585.3 | 691.8 | 253.3 | 682 | 17.2 | 35.2 | 58.9 | 25.8 | 234.2 | 216.1 | 39 | 103.3 | 98.2 | 50.6
338 | 164 | 479.3 | 191.72 | 224.1096 | 216.9 | 201.3 | 225.1 | 205.7 | 500.9 | 17.9 | 21.6 | 41.2 | 3.8 | 205.7 | 5.8 | 406.5 | 825.4 | 765.8 | 648.1 | 788.8 | 317.5 | 585.6 | 687.2 | 253.4 | 680.7 | 17.3 | 35.4 | 59.1 | 26 | 234.2 | 216.4 | 39.2 | 103.7 | 98.9 | 50.8
339 | 165 | 479.2 | 191.68 | 224.0629 | 217 | 202.1 | 225.6 | 205.8 | 510.2 | 17.9 | 21.5 | 41.5 | 3.7 | 207.5 | 5.7 | 409.4 | 826.9 | 763.8 | 654.2 | 785.9 | 319.1 | 588.7 | 680.2 | 253.4 | 678.6 | 17.3 | 35.6 | 59.8 | 26.1 | 234.5 | 216.8 | 39.4 | 104.1 | 99.6 | 51.2
340 | 166 | 479.3 | 191.72 | 224.1096 | 216.9 | 202.7 | 226.1 | 206.3 | 532.8 | 18 | 21.5 | 41.6 | 3.6 | 203.5 | 5.5 | 412.4 | 825.8 | 758.1 | 657.9 | 783.1 | 320.8 | 582.8 | 670.1 | 253.2 | 677.1 | 17.3 | 35.8 | 60 | 26.3 | 234.9 | 217.6 | 39.6 | 104.5 | 100.4 | 51.4
341 | 167 | 478.7 | 191.48 | 223.8291 | 216.3 | 204.5 | 226.3 | 207.1 | 529.3 | 18 | 21.5 | 41.8 | 3.6 | 197 | 5.6 | 380.7 | 272.8 | 247.8 | 246.1 | 779.6 | 322.4 | 584.2 | 675.9 | 253.2 | 676.5 | 17.3 | 36 | 60.2 | 26.4 | 235.1 | 217.8 | 39.8 | 105.1 | 101.1 | 51.7
342 | 168 | 479.7 | 191.88 | 224.2967 | 215.9 | 206.4 | 226.8 | 207.4 | 523.7 | 18.1 | 21.5 | 41.8 | 3.5 | 203.9 | 5.5 | 416.9 | 794.2 | 727.7 | 644.1 | 780.5 | 324 | 581 | 682.9 | 253.3 | 676.3 | 17.4 | 36.2 | 60.4 | 26.6 | 235.6 | 218.3 | 40 | 105.5 | 101.8 | 52
343 | 169 | 481.1 | 192.44 | 224.9513 | 215.8 | 206.8 | 227 | 207.2 | 503.5 | 18.2 | 21.5 | 41.9 | 3.6 | 200.3 | 5.3 | 422.8 | 823.2 | 748.9 | 668.1 | 784.4 | 325.6 | 580.9 | 693.3 | 253.3 | 679.1 | 17.4 | 36.4 | 60.8 | 26.8 | 236 | 218.8 | 40.2 | 106 | 102.4 | 52.3
344 | 170 | 480.9 | 192.36 | 224.8578 | 215.1 | 205.6 | 228 | 207 | 502.1 | 18.2 | 21.5 | 42 | 3.7 | 190.5 | 5.1 | 426.4 | 824.8 | 764.9 | 670.5 | 784.6 | 327.1 | 588.4 | 702.8 | 253.9 | 682.1 | 17.5 | 36.6 | 61.4 | 26.9 | 236.3 | 218.9 | 40.5 | 106.5 | 103 | 52.6
345 | 171 | 482.6 | 193.04 | 225.6526 | 215.2 | 205.7 | 227.8 | 206.4 | 506.2 | 18.3 | 21.5 | 42 | 3.4 | 190.6 | 5 | 430.1 | 825.4 | 788.6 | 671.6 | 785.8 | 328.6 | 601.2 | 718.7 | 254.5 | 685.4 | 17.5 | 36.8 | 61.6 | 27.1 | 236 | 219.5 | 40.7 | 107.1 | 103.5 | 52.9
346 | 172 | 484.3 | 193.72 | 226.4475 | 213.8 | 207 | 228.1 | 207 | 517.5 | 18.4 | 21.5 | 42.1 | 3.5 | 194.5 | 4.7 | 433.8 | 821.4 | 785 | 673.4 | 785 | 330.2 | 610.3 | 714.8 | 254.7 | 685.5 | 17.5 | 37 | 61.9 | 27.2 | 235.7 | 219.4 | 40.9 | 107.7 | 104.2 | 53.1
347 | 173 | 484.5 | 193.8 | 226.541 | 214 | 207 | 227.8 | 207.3 | 525.7 | 18.4 | 21.5 | 42.3 | 3.6 | 209.3 | 4.7 | 437.6 | 825.2 | 769.1 | 679.2 | 785 | 331.8 | 606.5 | 704.7 | 254.3 | 685.2 | 17.6 | 37.2 | 62.4 | 27.4 | 235.9 | 219.3 | 41.1 | 108.1 | 105.1 | 53.5
348 | 174 | 482.4 | 192.96 | 225.5591 | 213.5 | 207.7 | 226.9 | 207.6 | 525.7 | 18.4 | 21.5 | 42.4 | 3.7 | 200.1 | 5.9 | 441.5 | 825.5 | 770.5 | 682.1 | 788.8 | 333.4 | 607.8 | 708.3 | 253.8 | 688.4 | 17.6 | 37.4 | 62.6 | 27.6 | 235.7 | 219.3 | 41.4 | 108.5 | 105.8 | 53.8
349 | 175 | 481.9 | 192.76 | 225.3253 | 213.5 | 207.8 | 227.1 | 208.5 | 525.8 | 18.5 | 21.5 | 42.5 | 4.1 | 196.1 | 6.5 | 445.6 | 826.3 | 776.6 | 686.2 | 787.2 | 335 | 605.4 | 696.3 | 253.6 | 688.2 | 17.6 | 37.6 | 63 | 27.7 | 237.4 | 219.4 | 41.6 | 109.1 | 106.4 | 54.1
350 | 176 | 480.9 | 192.36 | 224.8578 | 214.4 | 207.7 | 228.6 | 209.2 | 526.3 | 18.5 | 21.5 | 42.6 | 3.1 | 199 | 6.4 | 449.9 | 825.3 | 802.4 | 688.1 | 789.2 | 336.5 | 607.3 | 699.7 | 253.4 | 688.1 | 17.7 | 37.8 | 63.2 | 27.9 | 238.4 | 219.6 | 41.9 | 109.7 | 107 | 54.4
351 | 177 | 479.6 | 191.84 | 224.2499 | 214.9 | 208.4 | 228.8 | 209.9 | 506.2 | 18.6 | 21.5 | 42.6 | 3 | 191 | 6.2 | 454.2 | 824 | 812.2 | 688.7 | 791 | 338 | 610.8 | 715.9 | 253 | 689.5 | 17.7 | 38 | 63.4 | 28 | 238.6 | 219.9 | 42.1 | 110.2 | 107.7 | 54.7
352 | 178 | 480 | 192 | 224.4369 | 214.8 | 207.6 | 227.7 | 209.7 | 490 | 18.6 | 21.5 | 42.7 | 3.2 | 198.6 | 6.5 | 458.6 | 824 | 801.3 | 690.9 | 795 | 339.5 | 622 | 726.3 | 252.8 | 692.9 | 17.7 | 38.2 | 63.9 | 28.2 | 238.7 | 220.4 | 42.3 | 110.9 | 108.4 | 55
353 | 179 | 480 | 192 | 224.4369 | 215.5 | 207 | 226.7 | 208.9 | 477.3 | 18.7 | 21.5 | 42.7 | 3.5 | 200.9 | 6.6 | 463.2 | 824.6 | 813.6 | 692.4 | 797.7 | 341 | 635.1 | 737.5 | 253.1 | 698.1 | 17.8 | 38.4 | 64.4 | 28.4 | 238.5 | 220.7 | 42.6 | 111.4 | 109.1 | 55.3
354 | 180 | 479.9 | 191.96 | 224.3902 | 216 | 207.2 | 226.2 | 208.3 | 474.6 | 18.7 | 21.5 | 42.9 | 3.3 | 191.1 | 6.6 | 468 | 823.6 | 820.6 | 694.3 | 798.8 | 342.5 | 639.6 | 745.1 | 253.1 | 699.7 | 17.8 | 38.6 | 64.5 | 28.5 | 238.4 | 221 | 42.8 | 112 | 109.8 | 55.6
355 | 181 | 480.4 | 192.16 | 224.624 | 216.9 | 207.1 | 226.2 | 207.7 | 464.8 | 18.7 | 21.5 | 43 | 3.7 | 187.9 | 6.9 | 472.9 | 826.3 | 802.2 | 697.9 | 799.4 | 344.1 | 641.7 | 736.2 | 252.7 | 699.8 | 17.8 | 38.8 | 64.7 | 28.7 | 238.4 | 221.3 | 42.9 | 112.5 | 110.5 | 55.9
356 | 182 | 479.9 | 191.96 | 224.3902 | 219.4 | 207.3 | 226.2 | 207.8 | 468.6 | 18.7 | 21.5 | 43.3 | 3.4 | 187.3 | 7.3 | 478 | 827.3 | 805.1 | 700.6 | 797.8 | 345.7 | 641.4 | 737.7 | 252.3 | 699.7 | 17.9 | 39 | 65 | 28.8 | 239.6 | 222 | 43.1 | 113.2 | 111.2 | 56.2
357 | 183 | 479.5 | 191.8 | 224.2031 | 221.2 | 207.9 | 226.7 | 207.8 | 467.7 | 18.7 | 21.5 | 43.5 | 3.9 | 171.5 | 7.2 | 483.1 | 829.1 | 800.6 | 703.4 | 796.8 | 347.3 | 638.5 | 739.1 | 251.8 | 699.4 | 17.9 | 39.2 | 65.3 | 29 | 240.1 | 222.6 | 43.4 | 113.6 | 111.9 | 56.5
358 | 184 | 479.6 | 191.84 | 224.2499 | 220.7 | 208 | 227 | 208 | 467.7 | 18.8 | 21.5 | 43.7 | 3.8 | 156.1 | 6.7 | 488.4 | 753.5 | 575.4 | 629.1 | 798.4 | 348.9 | 632.9 | 730.6 | 251.3 | 698.9 | 18 | 39.5 | 65.6 | 29.2 | 240 | 223 | 43.6 | 114.1 | 112.6 | 56.8
359 | 185 | 479.2 | 191.68 | 224.0629 | 220.1 | 207.8 | 226.3 | 207.9 | 480.6 | 18.8 | 21.5 | 43.9 | 3.3 | 161 | 5.7 | 493.5 | 828.8 | 800.2 | 706 | 800.7 | 350.5 | 637.9 | 731.7 | 251.2 | 701.1 | 18 | 39.7 | 65.9 | 29.3 | 239.6 | 223.6 | 43.8 | 114.6 | 113.2 | 57.1
360 | 186 | 479.3 | 191.72 | 224.1096 | 220.4 | 207.9 | 226.3 | 208.2 | 491.7 | 18.8 | 21.5 | 44 | 3.2 | 192 | 5.8 | 498.4 | 828.4 | 797 | 708.7 | 803.3 | 352 | 645.5 | 736.9 | 251 | 702.9 | 18 | 39.9 | 66.3 | 29.5 | 239.5 | 224.2 | 44 | 115.2 | 113.8 | 57.4
361 | 187 | 479.2 | 191.68 | 224.0629 | 221.8 | 208.1 | 227.3 | 208.5 | 485.8 | 18.8 | 21.5 | 44.2 | 3.4 | 195 | 6.5 | 503.3 | 831.7 | 791.9 | 712.2 | 805 | 353.6 | 648.9 | 744.4 | 250.8 | 706.5 | 18.1 | 40.1 | 66.7 | 29.7 | 239.7 | 224.3 | 44.2 | 115.6 | 114.6 | 57.7
362 | 188 | 478.6 | 191.44 | 223.7823 | 221 | 208.4 | 227.8 | 208.3 | 483.2 | 18.9 | 21.4 | 44.3 | 3.5 | 194.1 | 6.6 | 508.4 | 832.5 | 798.1 | 714.5 | 805.7 | 355.2 | 653.3 | 751.2 | 250.6 | 708.2 | 18.1 | 40.3 | 67.1 | 29.9 | 240.6 | 224.5 | 44.4 | 116 | 115.3 | 58
363 | 189 | 476.8 | 190.72 | 222.9407 | 222.1 | 208.3 | 228.2 | 208.6 | 476.8 | 18.9 | 21.5 | 44.4 | 3.4 | 190.2 | 6.9 | 513.5 | 833.2 | 788.2 | 715.4 | 806.7 | 356.7 | 656 | 755.1 | 250.3 | 709.1 | 18.2 | 40.5 | 67.3 | 30 | 240.7 | 225 | 44.7 | 116.6 | 115.9 | 58.4
364 | 190 | 479.4 | 191.76 | 224.1564 | 221.8 | 208.2 | 229.4 | 209.1 | 471.3 | 19 | 21.4 | 44.6 | 3.9 | 195.3 | 7.2 | 518.6 | 832.3 | 787.5 | 715.5 | 811.2 | 358.4 | 665.1 | 765.9 | 249.9 | 713.7 | 18.2 | 40.7 | 67.6 | 30.2 | 240.7 | 225.4 | 44.9 | 117 | 116.6 | 58.7
365 | 191 | 479.6 | 191.84 | 224.2499 | 220.4 | 208.1 | 230.2 | 208.9 | 473.9 | 19 | 21.4 | 44.8 | 3.7 | 195 | 6.9 | 523.8 | 832.2 | 785.6 | 717 | 813.4 | 360 | 670 | 767.8 | 249.4 | 715.9 | 18.2 | 40.9 | 67.9 | 30.4 | 240.5 | 226 | 45.1 | 117.6 | 117.3 | 59
366 | 192 | 478.9 | 191.56 | 223.9226 | 220.8 | 207.7 | 230.4 | 209.3 | 471.2 | 19.1 | 21.4 | 45 | 4.2 | 187.7 | 6.8 | 529.1 | 833.4 | 782.7 | 720 | 811.9 | 361.6 | 671 | 763.9 | 249 | 716.4 | 18.3 | 41.2 | 68.3 | 30.5 | 241 | 226 | 45.3 | 118 | 118 | 59.4
367 | 193 | 476.9 | 190.76 | 222.9874 | 220.6 | 207.5 | 229.8 | 209.9 | 475.9 | 19.2 | 21.4 | 45.2 | 4.2 | 187.8 | 6.4 | 534.4 | 834.8 | 792.8 | 722.3 | 811.5 | 363.3 | 670.5 | 766.5 | 248.4 | 718.3 | 18.3 | 41.4 | 68.7 | 30.7 | 241.4 | 226.3 | 45.6 | 118.6 | 118.7 | 59.7
368 | 194 | 475.6 | 190.24 | 222.3796 | 220.1 | 207.9 | 229 | 210.3 | 475.5 | 19.2 | 21.4 | 45.4 | 3.6 | 198.2 | 5.9 | 539.6 | 833.3 | 797.5 | 722.3 | 811.9 | 364.9 | 672.3 | 771.7 | 247.8 | 720.9 | 18.3 | 41.6 | 69 | 30.9 | 241.7 | 226.2 | 45.8 | 119 | 119.4 | 60
369 | 195 | 478.5 | 191.4 | 223.7356 | 219.2 | 208.9 | 228.6 | 211 | 470.1 | 19.3 | 21.4 | 45.4 | 4 | 197 | 5.6 | 544.9 | 832.5 | 810.4 | 723.7 | 812.4 | 366.5 | 674.3 | 773.7 | 247.4 | 722.7 | 18.4 | 41.8 | 69.4 | 31.1 | 241.9 | 226.4 | 46 | 119.5 | 120.2 | 60.3
370 | 196 | 478.1 | 191.24 | 223.5485 | 220.1 | 208.5 | 227.5 | 211 | 472 | 19.3 | 21.4 | 45.5 | 4.2 | 179.3 | 5.5 | 550.1 | 831.4 | 816.8 | 723.6 | 812.8 | 368.1 | 672.7 | 776.7 | 247.2 | 722.1 | 18.4 | 42 | 69.7 | 31.3 | 242.1 | 227 | 46.2 | 120.2 | 121 | 60.7
371 | 197 | 478.3 | 191.32 | 223.6421 | 220.9 | 208.3 | 226.9 | 211.1 | 471.8 | 19.4 | 21.4 | 45.6 | 3.7 | 193.8 | 5.4 | 555.4 | 830.3 | 814.7 | 723.8 | 815.8 | 369.7 | 675 | 779.1 | 246.9 | 723.8 | 18.5 | 42.3 | 70 | 31.4 | 242.8 | 227.1 | 46.4 | 120.6 | 121.8 | 61
372 | 198 | 477.4 | 190.96 | 223.2212 | 220.7 | 207.7 | 227.2 | 211.5 | 496.4 | 19.5 | 21.4 | 45.7 | 4.1 | 205.4 | 5.5 | 560.8 | 830.3 | 808.2 | 725.6 | 815.8 | 371.3 | 678.1 | 775.2 | 246.8 | 725.9 | 18.5 | 42.5 | 70.7 | 31.6 | 242.9 | 228.1 | 46.6 | 121.1 | 122.5 | 61.3
373 | 199 | 477.3 | 190.92 | 223.1745 | 222 | 206.4 | 227.4 | 211.5 | 512.5 | 19.5 | 21.4 | 45.9 | 4.1 | 202.4 | 5.6 | 566.2 | 830.3 | 800.4 | 726.1 | 812.9 | 373 | 674.2 | 762.5 | 247.2 | 722.9 | 18.6 | 42.7 | 71.2 | 31.8 | 242.9 | 228.7 | 46.9 | 121.5 | 123.2 | 61.6
374 | 200 | 478.4 | 191.36 | 223.6888 | 224.2 | 206.3 | 228.4 | 211.8 | 510.7 | 19.6 | 21.4 | 45.9 | 4 | 199.1 | 5.2 | 571.3 | 828.5 | 818.2 | 724.7 | 814.1 | 374.6 | 678 | 772.9 | 247.7 | 724.4 | 18.6 | 42.9 | 71.4 | 32 | 243.1 | 228.8 | 47.1 | 122 | 123.8 | 61.9
375 | 201 | 479.4 | 191.76 | 224.1564 | 225.2 | 208.1 | 229.3 | 212.8 | 508 | 19.6 | 21.4 | 46.1 | 3.7 | 196.2 | 5.3 | 575.7 | 830.9 | 805.4 | 725.4 | 812.3 | 376.2 | 673.3 | 768.9 | 248.1 | 725.7 | 18.6 | 43.2 | 71.8 | 32.1 | 243.4 | 229.1 | 47.3 | 122.4 | 124.6 | 62.2
376 | 202 | 479.1 | 191.64 | 224.0161 | 224.6 | 208.1 | 229.5 | 213 | 524.4 | 19.6 | 21.4 | 46.2 | 4.1 | 200.9 | 5.5 | 579.5 | 830.5 | 797.2 | 725.9 | 812.8 | 377.8 | 671.5 | 765.9 | 248.7 | 726 | 18.7 | 43.4 | 72.1 | 32.3 | 243.7 | 229.6 | 47.5 | 122.9 | 125.4 | 62.4
377 | 203 | 479 | 191.6 | 223.9694 | 223.8 | 207.1 | 230 | 213 | 538.4 | 19.6 | 21.4 | 46.3 | 3.8 | 199 | 5.2 | 582.3 | 832.8 | 787.8 | 725.8 | 813.4 | 379.5 | 672.9 | 765.1 | 249.3 | 727.3 | 18.7 | 43.6 | 72.4 | 32.5 | 243.8 | 230.3 | 47.7 | 123.6 | 126.2 | 62.8
378 | 204 | 477.9 | 191.16 | 223.455 | 223.1 | 209.4 | 231 | 213.6 | 547.3 | 19.6 | 21.4 | 46.5 | 3.9 | 183.9 | 4.5 | 584.3 | 831.5 | 793.4 | 724.8 | 812.7 | 381.1 | 672.8 | 765.3 | 250 | 727.7 | 18.8 | 43.8 | 72.9 | 32.7 | 243.9 | 230.6 | 48 | 124 | 126.9 | 63.1
379 | 205 | 478.1 | 191.24 | 223.5485 | 224.1 | 211 | 231.8 | 213.9 | 535.8 | 19.7 | 21.4 | 46.6 | 4 | 188.8 | 4.2 | 585.6 | 829.5 | 783.4 | 723.4 | 813 | 382.7 | 675 | 765.3 | 250.8 | 727.9 | 18.8 | 44 | 73.3 | 32.9 | 244.6 | 230.6 | 48.2 | 124.4 | 127.5 | 63.4
380 | 206 | 477.6 | 191.04 | 223.3148 | 224.1 | 211 | 233.1 | 213.8 | 533.1 | 19.7 | 21.4 | 46.6 | 4.2 | 206 | 4.1 | 585.9 | 832.8 | 783.9 | 723.5 | 813.1 | 384.3 | 677.2 | 765.4 | 251.6 | 728.2 | 18.9 | 44.3 | 73.6 | 33 | 245.7 | 230.2 | 48.4 | 124.8 | 128.3 | 63.8
381 | 207 | 475.4 | 190.16 | 222.2861 | 223.5 | 211.7 | 234.4 | 213.7 | 548.4 | 19.7 | 21.4 | 46.7 | 3.6 | 210.7 | 4.3 | 585.6 | 828.1 | 795.2 | 721.6 | 815.6 | 385.9 | 683.9 | 772 | 252.5 | 730.2 | 18.9 | 44.5 | 74.1 | 33.2 | 246 | 230 | 48.7 | 125.2 | 129 | 64.2
382 | 208 | 477.1 | 190.84 | 223.081 | 223.7 | 213.1 | 234.8 | 213.9 | 555.2 | 19.8 | 21.4 | 46.8 | 3.4 | 194.3 | 4 | 584.8 | 828.4 | 792.6 | 721.7 | 818.6 | 387.5 | 690.3 | 780.2 | 253.3 | 734.3 | 18.9 | 44.7 | 74.5 | 33.4 | 246.8 | 230.6 | 48.9 | 125.6 | 129.8 | 64.5
383 | 209 | 477.3 | 190.92 | 223.1745 | 224.1 | 213.8 | 235.2 | 214 | 548.8 | 19.8 | 21.4 | 46.8 | 4.4 | 193.8 | 4.2 | 583.9 | 830.2 | 786.7 | 722.6 | 818.8 | 389 | 691.5 | 773.2 | 254.1 | 735.7 | 19 | 44.9 | 74.8 | 33.6 | 247.5 | 231 | 49.1 | 126.1 | 130.5 | 64.8
384 | 210 | 476.4 | 190.56 | 222.7537 | 225.2 | 213.8 | 236.1 | 214.6 | 552.1 | 19.8 | 21.4 | 46.9 | 4.2 | 195.8 | 4.7 | 582.8 | 828.7 | 770.2 | 722.8 | 817.5 | 390.7 | 690.9 | 766.1 | 254.9 | 733.8 | 19 | 45.2 | 75.4 | 33.8 | 248.2 | 231.4 | 49.4 | 126.5 | 131.2 | 65.2
385 | 211 | 477.8 | 191.12 | 223.4083 | 225.6 | 215.3 | 235.7 | 214.9 | 557.7 | 19.9 | 21.4 | 47 | 4 | 194.5 | 4.5 | 581.5 | 830.9 | 758.5 | 723.6 | 815.7 | 392.4 | 685.6 | 757.2 | 255.8 | 732.4 | 19.1 | 45.4 | 75.7 | 34 | 249.1 | 231.7 | 49.7 | 127.1 | 131.9 | 65.5
386 | 212 | 478.1 | 191.24 | 223.5485 | 226.1 | 216.5 | 236.2 | 215.9 | 552.7 | 20 | 21.4 | 47.1 | 4.6 | 193 | 4.1 | 580 | 830.6 | 764.1 | 723.7 | 818.6 | 394 | 685.5 | 758.9 | 256.7 | 733.2 | 19.1 | 45.6 | 75.8 | 34.2 | 249.5 | 232.2 | 49.9 | 127.6 | 132.5 | 65.8
387 | 213 | 478.3 | 191.32 | 223.6421 | 227.6 | 216.3 | 237.3 | 216.7 | 541.9 | 20 | 21.3 | 47.1 | 4.6 | 189.4 | 4.3 | 578.8 | 829.1 | 785.1 | 723.2 | 818.9 | 395.6 | 685.5 | 766.1 | 257.7 | 733.9 | 19.2 | 45.9 | 76 | 34.3 | 249.9 | 232.9 | 50.1 | 128.2 | 133.1 | 66.2
388 | 214 | 478.4 | 191.36 | 223.6888 | 227.3 | 216.6 | 236.9 | 216.4 | 533.9 | 20.1 | 21.3 | 47.1 | 4.7 | 171.6 | 4.7 | 577.8 | 828.4 | 803.1 | 723.4 | 820.6 | 397.2 | 693.1 | 779.1 | 258.7 | 736.5 | 19.2 | 46.1 | 76.4 | 34.5 | 250.4 | 234.1 | 50.3 | 128.9 | 133.7 | 66.5
389 | 215 | 477.5 | 191 | 223.268 | 227.4 | 217.2 | 236.2 | 215.7 | 533.6 | 20.2 | 21.3 | 47.2 | 4.4 | 176.2 | 4.9 | 577.1 | 830.4 | 801.6 | 724.4 | 820.7 | 398.8 | 693.1 | 782.4 | 259.8 | 737.3 | 19.3 | 46.3 | 77 | 34.7 | 251.3 | 234.7 | 50.5 | 129.6 | 134.5 | 66.8
390 | 216 | 477.8 | 191.12 | 223.4083 | 228.1 | 218.2 | 236.2 | 214.9 | 527.2 | 20.3 | 21.3 | 47.3 | 3.8 | 190 | 4.8 | 576.3 | 833.6 | 785.1 | 726.2 | 821.3 | 400.4 | 691.5 | 782.9 | 260.9 | 738.8 | 19.3 | 46.6 | 77.2 | 34.9 | 251.4 | 235.1 | 50.8 | 130 | 135.2 | 67.2
391 | 217 | 478.1 | 191.24 | 223.5485 | 231 | 218.3 | 236.1 | 214.2 | 518.7 | 20.3 | 21.3 | 47.4 | 4 | 191.8 | 4.9 | 575.7 | 833.9 | 797.7 | 727.2 | 821.2 | 402.1 | 686.6 | 779.2 | 261.9 | 738.7 | 19.4 | 46.8 | 77.4 | 35.1 | 252 | 235.1 | 51 | 130.5 | 135.9 | 67.5
392 | 218 | 477.9 | 191.16 | 223.455 | 232.2 | 217.9 | 236.9 | 215.2 | 518.8 | 20.4 | 21.3 | 47.5 | 4.1 | 197.8 | 4.6 | 575.3 | 834 | 818.4 | 728.1 | 819.3 | 403.8 | 688.2 | 787.3 | 262.9 | 739.5 | 19.4 | 47.1 | 77.8 | 35.3 | 251.9 | 235.3 | 51.2 | 131.2 | 136.6 | 67.9
393 | 219 | 480 | 192 | 224.4369 | 230.7 | 217.1 | 237.6 | 216 | 521.3 | 20.5 | 21.3 | 47.7 | 4.3 | 200.1 | 4.3 | 575.2 | 831.9 | 827.1 | 728.3 | 818.5 | 405.4 | 688.4 | 785.8 | 263.9 | 740.6 | 19.5 | 47.3 | 78.3 | 35.5 | 252.2 | 235.5 | 51.4 | 131.7 | 137.3 | 68.2
394 | 220 | 479.2 | 191.68 | 224.0629 | 231.1 | 217.1 | 237.8 | 215.4 | 523.1 | 20.5 | 21.3 | 47.8 | 4.2 | 197.5 | 5 | 575.5 | 830.2 | 813 | 727.2 | 817.2 | 407.1 | 686.5 | 783.6 | 264.8 | 740.2 | 19.5 | 47.5 | 78.7 | 35.7 | 252.9 | 236.2 | 51.7 | 132.3 | 138.2 | 68.5
395 | 221 | 478.8 | 191.52 | 223.8758 | 232.6 | 217.7 | 237.8 | 215.3 | 511.7 | 20.6 | 21.3 | 47.8 | 3.8 | 193.7 | 5.3 | 575.9 | 831.5 | 797.9 | 726.8 | 818.2 | 408.7 | 683.7 | 774.3 | 265.5 | 740.1 | 19.6 | 47.8 | 78.9 | 35.9 | 253 | 236.3 | 51.9 | 132.7 | 138.9 | 68.9
396 | 222 | 479.5 | 191.8 | 224.2031 | 234.8 | 217.5 | 237.8 | 216 | 505.6 | 20.6 | 21.3 | 47.9 | 3.5 | 188.9 | 5.1 | 576.4 | 827.5 | 806.2 | 725.9 | 817.4 | 410.3 | 684.9 | 781.1 | 266.3 | 741 | 19.6 | 48 | 79.1 | 36 | 253 | 236.7 | 52.1 | 133.2 | 139.6 | 69.2
397 | 223 | 479.4 | 191.76 | 224.1564 | 234.8 | 216.5 | 237.6 | 216.5 | 504.9 | 20.7 | 21.3 | 48 | 3.8 | 179.8 | 4.3 | 577 | 825.4 | 806.2 | 725.9 | 817.4 | 411.9 | 684.6 | 782.5 | 267.4 | 741.3 | 19.6 | 48.3 | 79.5 | 36.2 | 252.7 | 236.9 | 52.3 | 133.4 | 140.3 | 69.5
398 | 224 | 477.7 | 191.08 | 223.3615 | 235.4 | 216.8 | 237.6 | 216.7 | 505.7 | 20.7 | 21.3 | 48.2 | 4 | 175.6 | 3.5 | 577.6 | 826.3 | 800.5 | 726.2 | 816.9 | 413.5 | 677.6 | 776.7 | 268.5 | 741.2 | 19.7 | 48.5 | 79.8 | 36.4 | 252.9 | 237.2 | 52.5 | 134 | 141 | 69.8
399 | 225 | 477.3 | 190.92 | 223.1745 | 235.2 | 218.1 | 238.1 | 217.5 | 517.7 | 20.8 | 21.3 | 48.3 | 4.2 | 181.6 | 3.3 | 578.3 | 825.2 | 792.3 | 725.8 | 816.6 | 415 | 670.7 | 765 | 269.5 | 741.6 | 19.7 | 48.8 | 80.4 | 36.6 | 253.1 | 237.8 | 52.7 | 134.7 | 141.7 | 70.2
400 | 226 | 479.6 | 191.84 | 224.2499 | 235 | 219.4 | 238.2 | 217.7 | 520.7 | 20.8 | 21.3 | 48.4 | 3.9 | 190.3 | 4 | 578.9 | 823 | 783.3 | 725.7 | 815.6 | 416.6 | 666.9 | 760.1 | 270.6 | 741.9 | 19.8 | 49 | 80.9 | 36.8 | 252.9 | 238 | 53 | 135 | 142.3 | 70.5
401 | 227 | 478 | 191.2 | 223.5018 | 236.7 | 220.3 | 236.8 | 217.8 | 524.2 | 20.9 | 21.3 | 48.6 | 3.9 | 207.4 | 4.7 | 579.2 | 823.7 | 782.7 | 725.7 | 817.4 | 418.1 | 664.3 | 762.6 | 271.7 | 742.4 | 19.8 | 49.3 | 81.3 | 37 | 252.7 | 238.2 | 53.2 | 135.5 | 142.9 | 70.8
402 | 228 | 477.1 | 190.84 | 223.081 | 236.7 | 220.6 | 237.8 | 217.8 | 523.1 | 21 | 21.3 | 49 | 3.9 | 213.8 | 5.3 | 579.5 | 825.1 | 768.7 | 724.7 | 817.6 | 419.6 | 663.3 | 761.6 | 272.9 | 742.3 | 19.9 | 49.5 | 81.5 | 37.2 | 252.8 | 239 | 53.4 | 136 | 143.6 | 71.2
403 | 229 | 477.6 | 191.04 | 223.3148 | 237 | 219.9 | 238.7 | 217.2 | 522.1 | 21 | 21.3 | 49.3 | 3.6 | 189.9 | 5.7 | 579.8 | 825.6 | 762.2 | 725.1 | 819.4 | 421.1 | 668.8 | 765.1 | 274 | 743.1 | 19.9 | 49.8 | 81.7 | 37.4 | 252.9 | 239.4 | 53.6 | 136.4 | 144.2 | 71.5
404 | 230 | 478.4 | 191.36 | 223.6888 | 237.2 | 219.4 | 238.2 | 216.9 | 516.7 | 21.1 | 21.3 | 49.6 | 3.4 | 193.3 | 6.3 | 580.1 | 825.1 | 773.4 | 725.7 | 820.4 | 422.5 | 670.6 | 766.4 | 275.1 | 744.2 | 20 | 50 | 82.2 | 37.6 | 253.8 | 239.4 | 53.9 | 137 | 144.7 | 71.8
405 | 231 | 477.9 | 191.16 | 223.455 | 237.3 | 218.9 | 238 | 218.3 | 524 | 21.1 | 21.3 | 49.8 | 3.9 | 191.3 | 6.1 | 580.4 | 824.4 | 777.6 | 725.3 | 820.9 | 423.9 | 672.2 | 766.2 | 276 | 744.6 | 20 | 50.3 | 82.8 | 37.8 | 253.2 | 239.8 | 54.1 | 137.5 | 145.4 | 72.2
406 | 232 | 477.6 | 191.04 | 223.3148 | 236.9 | 218.9 | 238.2 | 219.6 | 527 | 21.2 | 21.3 | 49.9 | 3.6 | 196.2 | 5.7 | 580.6 | 825.7 | 762.6 | 725.5 | 822 | 425.4 | 669.2 | 763.1 | 277 | 744.3 | 20.1 | 50.5 | 83 | 38 | 253.7 | 240 | 54.3 | 137.9 | 146.1 | 72.5
407 | 233 | 476.9 | 190.76 | 222.9874 | 237.7 | 219.6 | 238.4 | 220.5 | 515.1 | 21.2 | 21.3 | 50 | 3.5 | 201.4 | 5.4 | 580.8 | 824.8 | 751.3 | 725.2 | 822.1 | 426.9 | 662.7 | 754.6 | 278.1 | 744.1 | 20.1 | 50.8 | 83.2 | 38.2 | 253.8 | 240 | 54.5 | 138.4 | 146.7 | 72.8
408 | 234 | 477.4 | 190.96 | 223.2212 | 237.8 | 219.3 | 239.1 | 220.8 | 524.4 | 21.3 | 21.3 | 50.1 | 3.9 | 200.9 | 5 | 581.1 | 822.5 | 752.3 | 725.1 | 824.1 | 428.5 | 663.9 | 756.2 | 279.4 | 745.4 | 20.2 | 51 | 83.6 | 38.4 | 254.7 | 240.2 | 54.8 | 138.8 | 147.3 | 73.2
409 | 235 | 478.2 | 191.28 | 223.5953 | 238.1 | 218.2 | 239.8 | 221.4 | 531.2 | 21.3 | 21.3 | 50.1 | 3.9 | 200.8 | 4.6 | 581.4 | 818.7 | 756 | 724.6 | 826.1 | 430 | 667.1 | 767 | 280.9 | 746.9 | 20.2 | 51.3 | 83.9 | 38.6 | 254.9 | 240.9 | 55 | 139.3 | 147.9 | 73.5
410 | 236 | 478.4 | 191.36 | 223.6888 | 237.6 | 217.4 | 240 | 221.9 | 525.2 | 21.4 | 21.2 | 50.1 | 4.1 | 209.7 | 4.3 | 581.7 | 814.8 | 756.3 | 723.9 | 827.8 | 431.6 | 674.3 | 778.2 | 282.3 | 749.6 | 20.3 | 51.5 | 84.2 | 38.8 | 254.7 | 241.9 | 55.2 | 139.9 | 148.5 | 73.9
411 | 237 | 478 | 191.2 | 223.5018 | 237.2 | 217.1 | 240.1 | 221.9 | 519.9 | 21.4 | 21.2 | 50.1 | 3.9 | 213.9 | 4 | 582.1 | 814.9 | 762.1 | 724.3 | 830.4 | 433.4 | 679.2 | 786 | 283.8 | 750.4 | 20.4 | 51.8 | 84.6 | 39 | 255 | 242.2 | 55.4 | 140.3 | 149.2 | 74.2
412 | 238 | 475.8 | 190.32 | 222.4731 | 237.8 | 216.5 | 240.5 | 221.8 | 519.6 | 21.4 | 21.2 | 50.1 | 3.7 | 204.9 | 3.9 | 582.5 | 812.9 | 755.3 | 724.2 | 833.3 | 435.2 | 678.7 | 786.3 | 285.3 | 751.5 | 20.4 | 52 | 85 | 39.2 | 256 | 242.4 | 55.7 | 140.6 | 149.9 | 74.5
413 | 239 | 477.6 | 191.04 | 223.3148 | 238 | 216 | 240.8 | 222.2 | 513.3 | 21.5 | 21.2 | 50.1 | 4 | 206.9 | 3.9 | 582.9 | 813 | 758.1 | 724.8 | 836.4 | 437.2 | 678 | 785.3 | 286.6 | 752 | 20.5 | 52.3 | 85.2 | 39.4 | 256.2 | 242.5 | 55.9 | 141.3 | 150.6 | 74.8
414 | 240 | 477.4 | 190.96 | 223.2212 | 236.9 | 215.5 | 241.2 | 222.9 | 511 | 21.6 | 21.2 | 50.1 | 4 | 213.8 | 4.3 | 583.5 | 811 | 772 | 724.1 | 838.7 | 439.3 | 679.1 | 783.2 | 288.1 | 753.3 | 20.5 | 52.5 | 85.5 | 39.6 | 256 | 242.6 | 56.1 | 141.7 | 151.2 | 75.1
415 | 241 | 478.2 | 191.28 | 223.5953 | 235.8 | 215.8 | 241.6 | 223 | 510 | 21.7 | 21.2 | 50.1 | 4.1 | 208.7 | 5 | 584.2 | 809.1 | 773.5 | 724.5 | 838.7 | 441.4 | 678.5 | 781.1 | 289.6 | 753.8 | 20.6 | 52.8 | 85.9 | 39.8 | 256 | 242.4 | 56.3 | 142.2 | 151.8 | 75.4
416 | 242 | 477.8 | 191.12 | 223.4083 | 235.1 | 216.1 | 241.7 | 223.2 | 503.4 | 21.7 | 21.2 | 50.1 | 4.2 | 208.1 | 5.7 | 585.1 | 808.3 | 764.3 | 724 | 839.5 | 443.5 | 677.5 | 776.3 | 291 | 752.4 | 20.6 | 53 | 86.2 | 40 | 255.7 | 242.5 | 56.5 | 142.6 | 152.5 | 75.7
417 | 243 | 477.8 | 191.12 | 223.4083 | 235 | 215.8 | 241.1 | 222.3 | 495.6 | 21.7 | 21.2 | 50.1 | 4.2 | 204.4 | 6 | 586.3 | 809.3 | 750.2 | 725 | 842 | 445.7 | 680.4 | 770.1 | 292.6 | 751.2 | 20.7 | 53.3 | 86.4 | 40.2 | 255.7 | 242.7 | 56.8 | 143.2 | 153.1 | 76
418 | 244 | 478.6 | 191.44 | 223.7823 | 236.6 | 215.7 | 241.2 | 221.7 | 490.8 | 21.8 | 21.2 | 50.2 | 4.2 | 196.4 | 5.8 | 587.7 | 811.1 | 746.2 | 726.1 | 843.2 | 448 | 680.5 | 767 | 294.2 | 751.5 | 20.7 | 53.5 | 86.6 | 40.4 | 255.7 | 242.8 | 57 | 143.8 | 153.8 | 76.3
419 | 245 | 477.8 | 191.12 | 223.4083 | 237.5 | 215.4 | 241.1 | 221.2 | 487.8 | 21.9 | 21.2 | 50.2 | 4.6 | 198 | 5.6 | 589.5 | 815.5 | 751.8 | 728.5 | 843.7 | 450.1 | 675 | 760.1 | 295.7 | 751.5 | 20.8 | 53.8 | 87 | 40.6 | 255.7 | 242.9 | 57.2 | 144.2 | 154.4 | 76.6
420 | 246 | 478.3 | 191.32 | 223.6421 | 238.2 | 215 | 241.5 | 221.4 | 485.9 | 22 | 21.2 | 50.3 | 4.7 | 197.4 | 5.6 | 591.5 | 812.2 | 752.1 | 729.1 | 844.8 | 452.2 | 672 | 755.8 | 297.2 | 751.5 | 20.9 | 54 | 87.4 | 40.8 | 255.9 | 242.7 | 57.4 | 144.5 | 155 | 77
421 | 247 | 477.3 | 190.92 | 223.1745 | 237.5 | 215.1 | 241.8 | 220.8 | 488.9 | 22.1 | 21.2 | 50.4 | 3.9 | 201.4 | 5.6 | 593.5 | 812.5 | 761.1 | 730.3 | 846.5 | 454.2 | 669.3 | 760.3 | 298.6 | 752.3 | 20.9 | 54.3 | 87.7 | 41 | 256.3 | 242.4 | 57.6 | 144.9 | 155.6 | 77.2
422 | 248 | 478.5 | 191.4 | 223.7356 | 236.9 | 214.6 | 242.8 | 221 | 484.3 | 22.2 | 21.2 | 50.6 | 3.8 | 206.1 | 5.3 | 595.5 | 813.2 | 752.2 | 731.4 | 845.1 | 456 | 667.1 | 756.7 | 300 | 753 | 21 | 54.5 | 88.3 | 41.2 | 256.8 | 242.3 | 57.8 | 145.3 | 156.2 | 77.6
423 | 249 | 478.3 | 191.32 | 223.6421 | 237.4 | 213.9 | 243.5 | 221.2 | 502.2 | 22.2 | 21.2 | 50.6 | 4.2 | 187.6 | 4.7 | 597.5 | 817.2 | 743.2 | 732.8 | 842.2 | 457.9 | 663.4 | 742.5 | 301.3 | 751.4 | 21 | 54.8 | 88.9 | 41.4 | 256.8 | 242.1 | 58 | 145.7 | 156.8 | 77.9
424 | 250 | 477.9 | 191.16 | 223.455 | 238.3 | 214.9 | 243.9 | 220.9 | 516.2 | 22.3 | 21.2 | 50.7 | 4.1 | 166.1 | 4.1 | 599.5 | 815.3 | 739 | 733.4 | 841.9 | 459.9 | 658.8 | 738.1 | 302.7 | 750.5 | 21.1 | 55 | 89.3 | 41.6 | 256.7 | 242.1 | 58.2 | 146.1 | 157.4 | 78.2
425 | 251 | 477.8 | 191.12 | 223.4083 | 239 | 216.5 | 243.9 | 221.3 | 527.9 | 22.3 | 21.2 | 50.8 | 4.3 | 198.9 | 3.5 | 601.5 | 814.7 | 742.9 | 733.8 | 840.8 | 461.7 | 655.1 | 739.6 | 304.1 | 750.9 | 21.1 | 55.3 | 89.8 | 41.8 | 256.5 | 241.8 | 58.5 | 146.6 | 158 | 78.5
426 | 252 | 478.6 | 191.44 | 223.7823 | 238.4 | 216.9 | 243.9 | 221.7 | 534.7 | 22.4 | 21.2 | 51 | 4.4 | 230.7 | 3.3 | 603.6 | 817 | 735 | 734.6 | 840.8 | 463.5 | 652.5 | 735.3 | 305.5 | 750.9 | 21.2 | 55.5 | 90.1 | 42 | 257 | 241.8 | 58.7 | 147.1 | 158.6 | 78.9
427 | 253 | 478.1 | 191.24 | 223.5485 | 237.5 | 216.7 | 244.6 | 222.1 | 551.9 | 22.5 | 21.2 | 51.1 | 4.3 | 208.3 | 3.1 | 605.8 | 813.9 | 723.8 | 734.1 | 839 | 465.3 | 649.1 | 729.6 | 306.9 | 750 | 21.3 | 55.8 | 90.4 | 42.2 | 256.9 | 242.2 | 59 | 147.6 | 159.2 | 79.3
428 | 254 | 477.6 | 191.04 | 223.3148 | 237.7 | 216.5 | 244.3 | 222.5 | 562.7 | 22.6 | 21.2 | 51.1 | 4.2 | 182.9 | 3.1 | 607.9 | 813.2 | 701.1 | 734.4 | 835.3 | 467.1 | 647.5 | 720.8 | 308.2 | 749.5 | 21.3 | 56 | 90.9 | 42.4 | 256.8 | 242.5 | 59.2 | 148 | 159.8 | 79.6
429 | 255 | 478.6 | 191.44 | 223.7823 | 238.3 | 217.4 | 243.9 | 223.3 | 565.1 | 22.7 | 21.2 | 51.2 | 4.1 | 187.6 | 3.1 | 609.9 | 814.4 | 685.2 | 735 | 832.1 | 469 | 649.1 | 718.2 | 309.5 | 749.6 | 21.4 | 56.3 | 91.5 | 42.6 | 257.2 | 242.5 | 59.4 | 148.5 | 160.4 | 79.9
430 | 256 | 480.6 | 192.24 | 224.7175 | 239.4 | 218.7 | 244.5 | 223.9 | 573.3 | 22.7 | 21.2 | 51.4 | 4.4 | 208.1 | 3.5 | 612 | 815.5 | 677.2 | 736 | 829.8 | 470.9 | 649 | 715.9 | 310.8 | 750.5 | 21.4 | 56.5 | 91.8 | 42.8 | 257.7 | 242.7 | 59.7 | 148.8 | 161 | 80.3
431 | 257 | 480.7 | 192.28 | 224.7642 | 239.9 | 219.7 | 245.9 | 224.3 | 572.5 | 22.8 | 21.2 | 51.5 | 4.5 | 207.7 | 4.5 | 614.4 | 814.7 | 675.3 | 736.2 | 827.9 | 472.8 | 648.4 | 714.9 | 312.1 | 750.3 | 21.5 | 56.8 | 92.1 | 43.1 | 258.7 | 243.1 | 59.9 | 149.4 | 161.6 | 80.6
432 | 258 | 479.5 | 191.8 | 224.2031 | 242.3 | 220.7 | 246.2 | 224.9 | 574.5 | 22.9 | 21.2 | 51.6 | 4.1 | 201.1 | 5.3 | 617 | 813.6 | 687.5 | 736.7 | 826.3 | 474.8 | 647.7 | 711 | 313.3 | 749.2 | 21.6 | 57.1 | 92.5 | 43.3 | 260.1 | 243.4 | 60.2 | 149.9 | 162.1 | 81
433 | 259 | 478.2 | 191.28 | 223.5953 | 244.5 | 221.7 | 246.7 | 225.3 | 573.6 | 22.9 | 21.2 | 51.6 | 3.6 | 206.7 | 6 | 619.8 | 813.2 | 702.6 | 737 | 825.3 | 476.8 | 645.2 | 710.6 | 314.5 | 749 | 21.6 | 57.3 | 92.8 | 43.5 | 261 | 243.6 | 60.4 | 150.4 | 162.7 | 81.4
434 | 260 | 479.4 | 191.76 | 224.1564 | 245.5 | 222.3 | 247 | 226.3 | 565 | 23 | 21.2 | 51.7 | 3.7 | 210.1 | 6.4 | 622.9 | 814.9 | 689.7 | 738.2 | 825.2 | 478.8 | 643.2 | 705.3 | 315.7 | 749.1 | 21.7 | 57.6 | 93.1 | 43.7 | 262.6 | 244.3 | 60.7 | 150.9 | 163.3 | 81.7
435 | 261 | 480.4 | 192.16 | 224.624 | 246.2 | 222.8 | 246.9 | 227.7 | 559.2 | 23 | 21.2 | 51.7 | 3.8 | 208.5 | 6.3 | 625.8 | 816.1 | 665.8 | 739.1 | 821.6 | 480.9 | 642.3 | 701.7 | 316.8 | 749.1 | 21.7 | 57.8 | 93.6 | 43.9 | 262.9 | 244.7 | 60.9 | 151.5 | 163.8 | 82.1
436 | 262 | 479.8 | 191.92 | 224.3434 | 245.6 | 223 | 246.4 | 228.8 | 560.5 | 23.1 | 21.2 | 51.7 | 4.1 | 207.1 | 6.1 | 628.6 | 816 | 644.2 | 740 | 817.8 | 482.9 | 641.3 | 695.1 | 317.9 | 748.2 | 21.8 | 58 | 94 | 44.1 | 263.4 | 244.8 | 61.1 | 152 | 164.3 | 82.4
437 | 263 | 480.5 | 192.2 | 224.6707 | 244.8 | 222.8 | 247.6 | 229.6 | 570 | 23.2 | 21.2 | 51.7 | 3.8 | 206.5 | 6.1 | 631.5 | 814.7 | 639.5 | 741.3 | 815.8 | 485 | 641.9 | 694.5 | 319 | 748.4 | 21.9 | 58.3 | 94.6 | 44.3 | 264 | 245 | 61.4 | 152.5 | 164.9 | 82.8
438 | 264 | 478.9 | 191.56 | 223.9226 | 245.7 | 223.2 | 248.5 | 229.9 | 581 | 23.2 | 21.1 | 51.9 | 4.4 | 210.4 | 6 | 634.5 | 814 | 642.4 | 742.5 | 816.1 | 487 | 639.7 | 692.7 | 320.1 | 749.5 | 21.9 | 58.5 | 94.9 | 44.5 | 264.5 | 245.6 | 61.7 | 153.2 | 165.4 | 83.1
439 | 265 | 479.5 | 191.8 | 224.2031 | 245 | 224.4 | 248.7 | 229.9 | 590.3 | 23.3 | 21.2 | 52.1 | 4.7 | 210.3 | 5.7 | 637.4 | 814.8 | 634.9 | 743.7 | 813.4 | 488.9 | 639.3 | 693.7 | 321.2 | 749.8 | 22 | 58.8 | 95.4 | 44.7 | 265 | 245.9 | 61.9 | 153.8 | 166.1 | 83.5
440 | 266 | 480.1 | 192.04 | 224.4837 | 245 | 224.3 | 249 | 230.3 | 595.7 | 23.3 | 21.1 | 52.3 | 4.2 | 195.8 | 5.6 | 640.5 | 812.9 | 628.9 | 744.4 | 811.8 | 490.8 | 636.6 | 690.4 | 322.3 | 749.4 | 22.1 | 59 | 95.9 | 44.9 | 265.5 | 246.4 | 62.2 | 154.3 | 166.7 | 83.9
441 | 267 | 478.9 | 191.56 | 223.9226 | 245.9 | 223.9 | 249.7 | 230.9 | 594.5 | 23.3 | 21.1 | 52.4 | 4.4 | 193 | 5.6 | 643.7 | 812.7 | 628.6 | 746.4 | 813.5 | 492.7 | 637 | 694.8 | 323.4 | 750.3 | 22.1 | 59.3 | 96.4 | 45.1 | 266.4 | 246.7 | 62.5 | 154.8 | 167.3 | 84.3
442 | 268 | 479 | 191.6 | 223.9694 | 246.5 | 224.4 | 250.4 | 231.7 | 587.3 | 23.4 | 21.1 | 52.5 | 4.4 | 198.1 | 5.4 | 646.9 | 811.7 | 637.9 | 748.8 | 812.3 | 494.7 | 632.7 | 693.4 | 324.6 | 749.9 | 22.2 | 59.5 | 96.7 | 45.4 | 267.4 | 247.2 | 62.7 | 155.3 | 167.9 | 84.6
443 | 269 | 477.7 | 191.08 | 223.3615 | 246.9 | 224 | 251.3 | 232.3 | 597.8 | 23.4 | 21.1 | 52.6 | 4.7 | 197 | 5.2 | 650.4 | 809.9 | 654 | 751.1 | 810 | 496.6 | 634.2 | 696.5 | 325.7 | 750.5 | 22.2 | 59.8 | 97.6 | 45.6 | 267.9 | 247.9 | 63 | 155.9 | 168.5 | 85
444 | 270 | 476.2 | 190.48 | 222.6601 | 247.1 | 223.4 | 254.5 | 233.6 | 608.6 | 23.4 | 21.1 | 52.7 | 4 | 197.2 | 5.1 | 654 | 807.7 | 686.8 | 752.5 | 811.9 | 498.4 | 636.5 | 701.1 | 326.8 | 750.9 | 22.3 | 60 | 97.9 | 45.8 | 268.6 | 248.4 | 63.2 | 156.5 | 169.2 | 85.3
445 | 271 | 477.2 | 190.88 | 223.1277 | 246.8 | 224.2 | 255.9 | 234.9 | 608.9 | 23.5 | 21.1 | 52.8 | 3.8 | 204.7 | 4.9 | 657.3 | 805.9 | 707.1 | 753.2 | 814.6 | 500.1 | 638.8 | 709.4 | 327.9 | 750.9 | 22.4 | 60.3 | 98.1 | 46 | 268.7 | 248.9 | 63.5 | 157 | 169.9 | 85.7
446 | 272 | 476.7 | 190.68 | 222.8939 | 247.1 | 225.9 | 256.1 | 235.3 | 604.1 | 23.5 | 21.1 | 53.1 | 3.8 | 198.3 | 4.9 | 660.3 | 806.7 | 730.5 | 754.7 | 816.9 | 501.9 | 642.2 | 718.6 | 329 | 752.6 | 22.4 | 60.5 | 98.2 | 46.2 | 269 | 248.9 | 63.7 | 157.4 | 170.6 | 86
447 | 273 | 480.2 | 192.08 | 224.5305 | 247.3 | 226 | 255.8 | 234.8 | 587.1 | 23.6 | 21.1 | 53.3 | 4.1 | 187.5 | 5.1 | 663.1 | 807.9 | 740.6 | 756.7 | 819.8 | 503.7 | 640.5 | 717.9 | 330.1 | 752.3 | 22.5 | 60.8 | 98.5 | 46.4 | 269.2 | 249.4 | 64 | 158 | 171.3 | 86.4
448 | 274 | 478.1 | 191.24 | 223.5485 | 248.4 | 226.2 | 256 | 234.3 | 573.3 | 23.7 | 21.1 | 53.4 | 4 | 180.4 | 5.1 | 666 | 807.3 | 737.5 | 757.9 | 823.5 | 505.6 | 639.7 | 725.1 | 331.2 | 752.1 | 22.6 | 61.1 | 98.7 | 46.6 | 269.3 | 249.9 | 64.2 | 158.6 | 172 | 86.7
449 | 275 | 477.8 | 191.12 | 223.4083 | 249.1 | 226.6 | 256 | 234 | 561.6 | 23.8 | 21.1 | 53.4 | 4.4 | 179.5 | 5 | 669 | 806.6 | 742 | 759.4 | 825.7 | 507.4 | 640 | 730.6 | 332.2 | 753.2 | 22.6 | 61.3 | 99.2 | 46.9 | 269.6 | 250.4 | 64.5 | 159.2 | 172.6 | 87
450 | 276 | 477 | 190.8 | 223.0342 | 250.3 | 226.5 | 255.9 | 233.4 | 551.7 | 23.9 | 21.1 | 53.5 | 4.3 | 185.1 | 5.6 | 672.2 | 802.8 | 762.3 | 759.8 | 829 | 509.3 | 651.3 | 743.4 | 333.2 | 754.3 | 22.7 | 61.6 | 99.5 | 47.1 | 269.8 | 250.9 | 64.7 | 159.6 | 173.2 | 87.4
451 | 277 | 476.7 | 190.68 | 222.8939 | 251 | 226.6 | 255.4 | 232 | 537.1 | 23.9 | 21.1 | 53.3 | 4.1 | 192 | 5.5 | 675.2 | 801.9 | 757.8 | 761.2 | 830.8 | 511.3 | 659.5 | 753.9 | 334.3 | 756.1 | 22.8 | 61.8 | 99.6 | 47.3 | 270 | 251.3 | 64.9 | 160.2 | 173.8 | 87.7
452 | 278 | 476.7 | 190.68 | 222.8939 | 250.7 | 227 | 255.7 | 230.8 | 527.9 | 24 | 21.1 | 53.3 | 3.9 | 200.7 | 5.1 | 678 | 803.8 | 748.5 | 762.7 | 833.4 | 513.1 | 661.6 | 755.1 | 335.3 | 756.8 | 22.8 | 62.1 | 99.8 | 47.5 | 270.4 | 251 | 65.1 | 160.7 | 174.5 | 88.1
453 | 279 | 478.3 | 191.32 | 223.6421 | 250.4 | 225.1 | 255.9 | 230.6 | 514.5 | 24 | 21.1 | 53.3 | 3.6 | 206.8 | 5 | 680.7 | 808.2 | 746.8 | 766.2 | 834.1 | 515 | 663.9 | 760.7 | 336.3 | 757.3 | 22.9 | 62.3 | 100.1 | 47.7 | 270.1 | 251.1 | 65.4 | 161.1 | 175.2 | 88.4
454 | 280 | 478.3 | 191.32 | 223.6421 | 249.7 | 224.1 | 255.9 | 230.6 | 512.8 | 24.1 | 21.1 | 53.4 | 4.6 | 205.5 | 5.1 | 683.5 | 812.2 | 770.6 | 769.3 | 833.7 | 516.9 | 670.8 | 768.6 | 337.4 | 758 | 23 | 62.6 | 100.5 | 47.9 | 269.9 | 251.6 | 65.6 | 161.7 | 175.8 | 88.8
455 | 281 | 479.1 | 191.64 | 224.0161 | 250.5 | 223.4 | 255.9 | 230 | 515.2 | 24.2 | 21.1 | 53.4 | 4 | 200.7 | 5.1 | 686.4 | 810.1 | 794.5 | 770.6 | 835.2 | 518.9 | 674.8 | 771.2 | 338.5 | 757.9 | 23 | 62.9 | 100.7 | 48.2 | 270 | 252 | 65.9 | 162.3 | 176.4 | 89.1
456 | 282 | 479.2 | 191.68 | 224.0629 | 250.7 | 223.2 | 255.6 | 230.4 | 513.5 | 24.3 | 21.1 | 53.5 | 4.6 | 196.2 | 5.5 | 689 | 812.7 | 797.9 | 772.5 | 835.5 | 521 | 673.4 | 771.3 | 339.6 | 758.5 | 23.1 | 63.1 | 101.3 | 48.4 | 269.6 | 252.3 | 66.1 | 162.8 | 177.1 | 89.4
457 | 283 | 478.2 | 191.28 | 223.5953 | 250 | 223.2 | 254.8 | 231 | 504.5 | 24.4 | 21.1 | 53.5 | 4.4 | 181.6 | 5.6 | 691.7 | 812.2 | 790.6 | 773.4 | 838 | 523.1 | 674.6 | 773.3 | 340.7 | 758.4 | 23.2 | 63.4 | 101.5 | 48.6 | 269.1 | 252.3 | 66.3 | 163.1 | 177.8 | 89.8
458 | 284 | 478 | 191.2 | 223.5018 | 251.2 | 223.1 | 254.5 | 231 | 503.3 | 24.5 | 21.1 | 53.4 | 4.2 | 188.9 | 5.4 | 694.4 | 813.3 | 795.9 | 775.4 | 838.3 | 525.3 | 677.9 | 776.6 | 341.8 | 759.1 | 23.2 | 63.7 | 101.9 | 48.8 | 268.8 | 252.4 | 66.6 | 163.5 | 178.5 | 90.1
459 | 285 | 478.3 | 191.32 | 223.6421 | 252.4 | 223.4 | 254.9 | 231.1 | 503.4 | 24.5 | 21.1 | 53.5 | 4.7 | 197 | 5.3 | 697.4 | 815.4 | 786.3 | 779.2 | 837.6 | 527.5 | 672.2 | 767.4 | 342.9 | 757.8 | 23.3 | 63.9 | 102.3 | 49 | 268.8 | 252.7 | 66.8 | 164 | 179.2 | 90.4
460 | 286 | 474.9 | 189.96 | 222.0523 | 253.8 | 224.3 | 255.5 | 231.1 | 502.4 | 24.6 | 21.1 | 53.7 | 4.4 | 196 | 5.2 | 700.6 | 814.8 | 799 | 780.3 | 838.9 | 529.7 | 672.6 | 771.4 | 344 | 758.2 | 23.4 | 64.2 | 102.6 | 49.2 | 268.7 | 252.5 | 67 | 164.5 | 179.8 | 90.7
461 | 287 | 477.5 | 191 | 223.268 | 254.3 | 225.1 | 256.2 | 231.9 | 507.6 | 24.6 | 21.1 | 53.8 | 4.7 | 196.7 | 4.7 | 703.6 | 814.4 | 800.1 | 780.6 | 840.7 | 531.8 | 672.5 | 773.5 | 345.3 | 758.2 | 23.5 | 64.4 | 103.1 | 49.4 | 268.9 | 252.6 | 67.2 | 164.9 | 180.4 | 91
462 | 288 | 477.4 | 190.96 | 223.2212 | 255.3 | 225.9 | 256.7 | 232.6 | 517.9 | 24.6 | 21.1 | 53.9 | 4.8 | 197.5 | 4.3 | 706.5 | 815.7 | 798.4 | 782.5 | 840.4 | 533.7 | 668.4 | 769.6 | 346.6 | 758.2 | 23.5 | 64.7 | 103.6 | 49.7 | 269.1 | 252.8 | 67.5 | 165.4 | 181.1 | 91.4
463 | 289 | 476.5 | 190.6 | 222.8004 | 254.7 | 226.6 | 256.6 | 232.5 | 532.7 | 24.7 | 21 | 54 | 4.7 | 196.5 | 4 | 709.2 | 815.7 | 791.9 | 785 | 839.6 | 535.6 | 663.9 | 764.5 | 347.8 | 757.1 | 23.6 | 65 | 104.2 | 49.9 | 269.5 | 253 | 67.7 | 165.8 | 181.8 | 91.8
464 | 290 | 477.4 | 190.96 | 223.2212 | 253.7 | 226.7 | 257.2 | 232.9 | 544.5 | 24.7 | 21 | 54.1 | 5.2 | 198.9 | 3.9 | 712 | 817.1 | 780.8 | 787.8 | 835.9 | 537.4 | 662.2 | 760.3 | 349.1 | 757.4 | 23.7 | 65.3 | 104.6 | 50.1 | 270.2 | 253.2 | 68 | 166.1 | 182.5 | 92.1
465 | 291 | 477.9 | 191.16 | 223.455 | 253.9 | 227.3 | 257.7 | 233.2 | 555 | 24.8 | 21 | 54.2 | 4.7 | 197.4 | 3.9 | 714.8 | 816.9 | 790.6 | 789.9 | 833.8 | 539.3 | 655.4 | 751.8 | 350.4 | 757.2 | 23.7 | 65.6 | 104.8 | 50.3 | 271 | 253.2 | 68.2 | 166.6 | 183.1 | 92.5
466 | 292 | 478.9 | 191.56 | 223.9226 | 253.4 | 227.2 | 258.7 | 233.3 | 570 | 25 | 21 | 54.4 | 4.8 | 183.5 | 4.3 | 717.5 | 817.2 | 780.6 | 793.6 | 828.7 | 541.1 | 646.5 | 747.3 | 351.8 | 757.1 | 23.8 | 65.8 | 105.2 | 50.5 | 271.4 | 253.5 | 68.5 | 167.1 | 183.8 | 92.8
467 | 293 | 479.8 | 191.92 | 224.3434 | 253.6 | 228.2 | 259.2 | 234.5 | 586.4 | 25 | 21 | 54.5 | 4.9 | 193.5 | 4.5 | 720.5 | 818.5 | 786.6 | 796.4 | 827 | 543 | 641.7 | 740.3 | 353.1 | 756 | 23.9 | 66.1 | 105.8 | 50.8 | 271.8 | 253.8 | 68.7 | 167.6 | 184.5 | 93.2
468 | 294 | 480.4 | 192.16 | 224.624 | 253.4 | 229.9 | 259.9 | 235.2 | 594.9 | 25.1 | 21 | 54.7 | 4.2 | 215.4 | 4.4 | 723.4 | 818.9 | 781.9 | 797.8 | 824.6 | 544.9 | 638.7 | 736.6 | 354.6 | 755.9 | 23.9 | 66.4 | 106.2 | 51 | 272.3 | 254 | 69 | 168.1 | 185.2 | 93.5
469 | 295 | 479.5 | 191.8 | 224.2031 | 252.6 | 230.1 | 260.4 | 236.3 | 603 | 25.2 | 21 | 54.8 | 4.2 | 215.5 | 3.9 | 726.2 | 817.4 | 782.5 | 799.3 | 821.4 | 546.7 | 634.5 | 731 | 356 | 755.2 | 24 | 66.7 | 106.7 | 51.2 | 272.8 | 254.3 | 69.2 | 168.6 | 186 | 93.9
470 | 296 | 479.1 | 191.64 | 224.0161 | 253.2 | 231.6 | 260.7 | 236.8 | 599.5 | 25.3 | 21 | 54.8 | 3.5 | 185.3 | 3.8 | 728.9 | 817.1 | 794.7 | 800 | 821.6 | 548.5 | 631.7 | 734.7 | 357.5 | 754.7 | 24.1 | 67 | 106.9 | 51.4 | 273.1 | 254.8 | 69.5 | 169.2 | 186.8 | 94.3
471 | 297 | 478.6 | 191.44 | 223.7823 | 252.3 | 232.9 | 261.3 | 238.1 | 606 | 25.4 | 21 | 55 | 4 | 178.3 | 4 | 731.5 | 816.6 | 797.3 | 799.6 | 823.9 | 550.2 | 629.8 | 735.9 | 359 | 755.9 | 24.2 | 67.3 | 107.5 | 51.6 | 273.4 | 255.4 | 69.8 | 169.8 | 187.5 | 94.6
472 | 298 | 479.1 | 191.64 | 224.0161 | 251.7 | 233.2 | 260.5 | 238.3 | 613.1 | 25.4 | 21 | 55.2 | 4.7 | 191.8 | 4.5 | 733.9 | 816.2 | 799.1 | 800.3 | 824.1 | 551.9 | 632.3 | 733.7 | 360.5 | 756.5 | 24.2 | 67.6 | 107.9 | 51.9 | 274.2 | 256.1 | 70.1 | 170.2 | 188.2 | 95.1
473 | 299 | 479.7 | 191.88 | 224.2967 | 251.4 | 233.8 | 260.6 | 237.9 | 612 | 25.5 | 21 | 55.4 | 3.9 | 195.5 | 4.9 | 736.3 | 815.1 | 793.4 | 801.2 | 825.1 | 553.6 | 630.1 | 735.3 | 362.1 | 756.3 | 24.3 | 67.9 | 108.2 | 52.1 | 274.3 | 256.5 | 70.3 | 170.7 | 188.9 | 95.4
474 | 300 | 480.1 | 192.04 | 224.4837 | 251.6 | 234.4 | 260.5 | 238.4 | 606.2 | 25.6 | 21 | 55.6 | 4 | 187.3 | 5.1 | 738.7 | 816.2 | 790.9 | 802.5 | 826.4 | 555.2 | 634.4 | 743.9 | 363.6 | 756.9 | 24.4 | 68.1 | 108.5 | 52.3 | 274.2 | 256.9 | 70.5 | 171.1 | 189.6 | 95.7
475 | 301 | 479.2 | 191.68 | 224.0629 | 253 | 234.9 | 261 | 239.2 | 595.8 | 25.6 | 21 | 55.6 | 4.3 | 178 | 5.2 | 741.2 | 817 | 798.3 | 802.6 | 827.9 | 556.8 | 634.9 | 747.4 | 365.3 | 755.8 | 24.5 | 68.4 | 108.7 | 52.5 | 275.2 | 257 | 70.8 | 171.5 | 190.3 | 96.1
476 | 302 | 478 | 191.2 | 223.5018 | 254.4 | 236.1 | 261.5 | 239.4 | 592 | 25.7 | 21 | 55.7 | 4.5 | 181.7 | 5.3 | 743.7 | 815.6 | 801.4 | 802.3 | 828.3 | 558.3 | 631.2 | 745.6 | 367 | 755 | 24.5 | 68.7 | 109.1 | 52.8 | 276.7 | 257.5 | 71 | 171.9 | 190.9 | 96.4
477 | 303 | 476.8 | 190.72 | 222.9407 | 256.1 | 236.6 | 261.1 | 239.2 | 583.4 | 25.7 | 21 | 55.7 | 4.2 | 185 | 5.3 | 746 | 814.5 | 807 | 802 | 830.8 | 559.9 | 628.5 | 744.7 | 368.6 | 754.9 | 24.6 | 69 | 109.4 | 53 | 276.6 | 258 | 71.3 | 172.6 | 191.6 | 96.8
478 | 304 | 479.4 | 191.76 | 224.1564 | 256.2 | 236.8 | 260.5 | 240.2 | 587.5 | 25.7 | 21 | 55.9 | 4 | 184.8 | 5.2 | 748.3 | 815.5 | 807 | 802.7 | 832.9 | 561.5 | 624.7 | 741 | 370.5 | 754.1 | 24.7 | 69.3 | 109.8 | 53.2 | 276.5 | 258.1 | 71.5 | 173.1 | 192.3 | 97.2
479 | 305 | 478.5 | 191.4 | 223.7356 | 256.4 | 237.1 | 259.9 | 240.4 | 601.4 | 25.7 | 21 | 56.1 | 4.4 | 183.2 | 4.9 | 750.7 | 816.1 | 789.9 | 805.3 | 831.2 | 563.2 | 623.8 | 733.7 | 372.3 | 753.4 | 24.8 | 69.6 | 110.3 | 53.4 | 276.4 | 258.6 | 71.8 | 173.6 | 193 | 97.5
480 | 306 | 477.1 | 190.84 | 223.081 | 256.3 | 238.4 | 260 | 241.2 | 606.3 | 25.8 | 21 | 56.1 | 4.5 | 179 | 4.8 | 753.2 | 815.5 | 772.6 | 807.2 | 828.2 | 565 | 621.2 | 723.9 | 374.1 | 752.8 | 24.9 | 69.8 | 111.1 | 53.7 | 276.1 | 258.8 | 72 | 174.1 | 193.8 | 97.9
481 | 307 | 479.3 | 191.72 | 224.1096 | 256.3 | 239.4 | 260.6 | 241.3 | 625.2 | 25.8 | 21 | 56.2 | 3.7 | 179.3 | 4.8 | 755.8 | 813.3 | 761.2 | 808.6 | 821.8 | 566.7 | 618.6 | 711.9 | 376 | 751.3 | 24.9 | 70.1 | 111.9 | 53.9 | 276 | 258.7 | 72.2 | 174.6 | 194.5 | 98.2
482 | 308 | 480 | 192 | 224.4369 | 257.3 | 239.4 | 261.7 | 242.4 | 638.9 | 25.9 | 21 | 56.2 | 4 | 178.2 | 4.8 | 758.6 | 811.9 | 765.9 | 809.9 | 815.3 | 568.4 | 620.4 | 709.5 | 377.9 | 749.4 | 25 | 70.4 | 112.3 | 54.1 | 276.5 | 258.6 | 72.5 | 175 | 195.2 | 98.6
483 | 309 | 479.1 | 191.64 | 224.0161 | 258.2 | 239.2 | 262.9 | 243.4 | 645.7 | 26 | 21 | 56.4 | 4.1 | 186.2 | 4.6 | 761.6 | 811.4 | 775.6 | 811.1 | 811.6 | 570.1 | 619.4 | 705.4 | 380 | 748.6 | 25.1 | 70.7 | 113 | 54.3 | 277.1 | 258.9 | 72.8 | 175.4 | 196 | 98.9
484 | 310 | 477.5 | 191 | 223.268 | 257.9 | 239.7 | 263.6 | 244.5 | 652.1 | 26.1 | 21 | 56.5 | 3.7 | 201.8 | 5.2 | 764.5 | 810.2 | 777.9 | 811.9 | 808.6 | 572 | 616.8 | 700.4 | 382 | 747.4 | 25.2 | 71 | 113.3 | 54.6 | 277.7 | 259.7 | 73 | 176 | 196.8 | 99.3
485 | 311 | 477.3 | 190.92 | 223.1745 | 258.5 | 240.3 | 264.7 | 245.3 | 645.8 | 26.2 | 21 | 56.7 | 4 | 200.5 | 5.6 | 767.3 | 812.4 | 798.5 | 812.2 | 809.3 | 573.9 | 614.7 | 700.1 | 384.1 | 746 | 25.2 | 71.3 | 113.6 | 54.8 | 278.7 | 260.5 | 73.3 | 176.5 | 197.6 | 99.7
486 | 312 | 477.3 | 190.92 | 223.1745 | 257.4 | 240.2 | 264.9 | 246.4 | 623.3 | 26.3 | 21 | 56.8 | 4.4 | 187.1 | 5.9 | 770 | 812.1 | 812.3 | 810.7 | 811.6 | 575.7 | 620.7 | 711.6 | 386.1 | 746.7 | 25.3 | 71.6 | 113.8 | 55 | 279.1 | 260.8 | 73.6 | 177.1 | 198.4 | 100.1
487 | 313 | 477.3 | 190.92 | 223.1745 | 257.5 | 240.2 | 265.5 | 247.4 | 596.3 | 26.4 | 21 | 56.9 | 4.5 | 189.3 | 6.3 | 772.5 | 812.4 | 808.3 | 809.2 | 815.2 | 577.4 | 627.6 | 720.2 | 388.3 | 747.9 | 25.4 | 71.9 | 114.1 | 55.3 | 279.9 | 260.8 | 73.8 | 177.6 | 199.2 | 100.5
488 | 314 | 477.9 | 191.16 | 223.455 | 257.5 | 240.6 | 264.5 | 247 | 584.1 | 26.4 | 20.9 | 57 | 4.3 | 193.9 | 6.8 | 774.8 | 814.4 | 805.7 | 809.2 | 817.7 | 578.9 | 631.5 | 724.2 | 390.5 | 747.8 | 25.5 | 72.2 | 114.4 | 55.5 | 280.3 | 261.3 | 74.1 | 178.1 | 200 | 100.9
489 | 315 | 479 | 191.6 | 223.9694 | 259 | 241.2 | 262.5 | 246.5 | 573.3 | 26.5 | 20.9 | 57.2 | 3.9 | 198.7 | 6.8 | 777.1 | 815.8 | 809.6 | 809.9 | 819.3 | 580.4 | 632.7 | 726.6 | 392.5 | 747.2 | 25.6 | 72.5 | 114.7 | 55.7 | 281.5 | 262 | 74.3 | 178.5 | 200.7 | 101.3
490 | 316 | 479.1 | 191.64 | 224.0161 | 261.2 | 241.6 | 262.3 | 246.4 | 565.4 | 26.5 | 20.9 | 57.2 | 3.9 | 195.4 | 6.9 | 779.5 | 815.6 | 811.9 | 810.5 | 821.8 | 582.2 | 631.5 | 726.5 | 394.6 | 746.9 | 25.6 | 72.8 | 114.9 | 55.9 | 280.9 | 262.3 | 74.6 | 179 | 201.4 | 101.6
491 | 317 | 479 | 191.6 | 223.9694 | 261.3 | 242 | 262.1 | 245.7 | 572.9 | 26.5 | 20.9 | 57.3 | 4.3 | 208 | 6.7 | 781.8 | 817.3 | 816.6 | 811.7 | 824.5 | 583.9 | 634.6 | 737.1 | 396.7 | 748.1 | 25.7 | 73.1 | 115.3 | 56.2 | 280.8 | 262.4 | 74.8 | 179.5 | 202.1 | 101.9
492 | 318 | 475 | 190 | 222.0991 | 261 | 242.2 | 262.2 | 244.8 | 578.2 | 26.5 | 20.9 | 57.4 | 4.3 | 213.2 | 6.2 | 784.2 | 818.7 | 807.6 | 812.4 | 827.2 | 585.4 | 637.1 | 742 | 398.8 | 748 | 25.8 | 73.4 | 115.6 | 56.4 | 280.8 | 262.6 | 75 | 180 | 202.8 | 102.3
493 | 319 | 477.5 | 191 | 223.268 | 259.8 | 242.7 | 261.2 | 243.8 | 569.3 | 26.6 | 20.9 | 57.5 | 4 | 213.6 | 5.5 | 786.4 | 817.4 | 810.1 | 811.5 | 829.1 | 586.8 | 639.6 | 746.8 | 400.9 | 749.2 | 25.9 | 73.7 | 115.9 | 56.6 | 280.6 | 263.2 | 75.2 | 180.5 | 203.6 | 102.6
494 | 320 | 477.3 | 190.92 | 223.1745 | 260.1 | 243.3 | 260.6 | 242.1 | 557.7 | 26.6 | 20.9 | 57.5 | 4.7 | 205.5 | 4.8 | 788.5 | 816.8 | 814.3 | 811.2 | 831.1 | 588.2 | 640.3 | 752.3 | 402.9 | 749.3 | 26 | 74 | 116.2 | 56.9 | 280.2 | 263.6 | 75.5 | 180.9 | 204.3 | 102.9
495 | 321 | 478.4 | 191.36 | 223.6888 | 260.7 | 243.5 | 261.1 | 241.6 | 557.5 | 26.7 | 20.9 | 57.4 | 4.5 | 192.3 | 4.6 | 790.6 | 816.6 | 821.8 | 810.5 | 832.5 | 589.7 | 644 | 758.2 | 405 | 749.3 | 26.1 | 74.2 | 116.5 | 57.1 | 279.6 | 263.5 | 75.7 | 181.2 | 205 | 103.3
496 | 322 | 478.4 | 191.36 | 223.6888 | 260.3 | 243.6 | 262.1 | 241.9 | 559.4 | 26.7 | 20.9 | 57.5 | 4.7 | 179.1 | 4.7 | 792.6 | 815 | 823.9 | 810.3 | 833 | 591.3 | 649.3 | 764.4 | 407.1 | 750.1 | 26.2 | 74.5 | 116.9 | 57.3 | 280 | 263.4 | 76 | 181.5 | 205.7 | 103.6
497 | 323 | 479 | 191.6 | 223.9694 | 260 | 244.3 | 262.5 | 242 | 575.2 | 26.7 | 20.9 | 57.6 | 4.3 | 185.6 | 4.7 | 794.5 | 816.5 | 822.9 | 811 | 831.8 | 592.9 | 648.2 | 756.8 | 409.2 | 748.7 | 26.2 | 74.8 | 117.5 | 57.5 | 280.2 | 263 | 76.2 | 181.9 | 206.4 | 104
498 | 324 | 478.4 | 191.36 | 223.6888 | 261.3 | 245.2 | 262.1 | 241.8 | 593.3 | 26.7 | 20.9 | 57.7 | 4.5 | 187.9 | 5.8 | 796.4 | 817.4 | 827.4 | 811 | 828.7 | 594.7 | 642.9 | 747.3 | 411.3 | 746.8 | 26.3 | 75.1 | 118 | 57.8 | 280.2 | 263.3 | 76.4 | 182.3 | 207.3 | 104.3
499 | 325 | 477.6 | 191.04 | 223.3148 | 262.4 | 246.5 | 262.9 | 242.4 | 592.2 | 26.9 | 20.9 | 57.8 | 4.6 | 184.1 | 6.8 | 798.3 | 817.9 | 823.8 | 812.2 | 829.7 | 596.4 | 643.5 | 750.3 | 413.3 | 747.9 | 26.4 | 75.4 | 118.4 | 58 | 280.1 | 263.7 | 76.7 | 182.8 | 208 | 104.7
500 | 326 | 478.3 | 191.32 | 223.6421 | 263.9 | 246.7 | 262.7 | 242.9 | 599.5 | 27 | 20.9 | 57.8 | 4.9 | 190.7 | 7.2 | 800.2 | 816.5 | 833.9 | 813 | 830.3 | 597.9 | 646.5 | 756.3 | 415.3 | 749.5 | 26.5 | 75.7 | 118.7 | 58.2 | 280 | 263.5 | 76.9 | 183.2 | 208.8 | 105
501 | 327 | 478.9 | 191.56 | 223.9226 | 263.8 | 247.7 | 262.4 | 244.1 | 592.5 | 27 | 20.9 | 57.9 | 4.4 | 195.4 | 7.1 | 802.1 | 817.5 | 830.9 | 813.3 | 827.7 | 599.4 | 649.5 | 756 | 417.4 | 748.9 | 26.6 | 75.9 | 118.9 | 58.5 | 280.1 | 263.6 | 77.2 | 183.6 | 209.6 | 105.4
502 | 328 | 479.5 | 191.8 | 224.2031 | 263.2 | 248.9 | 262.9 | 244.8 | 592.2 | 27.1 | 20.9 | 58.1 | 4.4 | 194.4 | 7 | 804.1 | 818.2 | 824.7 | 813.7 | 825.6 | 601.1 | 650.9 | 755.3 | 419.5 | 748.6 | 26.7 | 76.2 | 119.2 | 58.7 | 280.3 | 263.8 | 77.4 | 184.1 | 210.5 | 105.7
503 | 329 | 479.1 | 191.64 | 224.0161 | 261.4 | 249.3 | 263.9 | 244.1 | 596.1 | 27.2 | 20.9 | 58.2 | 4.7 | 192 | 6.6 | 806.2 | 819.4 | 814.5 | 814.3 | 826 | 602.8 | 645.8 | 745.7 | 421.6 | 747.4 | 26.8 | 76.5 | 119.4 | 58.9 | 280.1 | 264.7 | 77.6 | 184.6 | 211.3 | 106.1
504 | 330 | 479 | 191.6 | 223.9694 | 259.7 | 250.5 | 264.2 | 243 | 583.4 | 27.3 | 20.9 | 58.4 | 4.6 | 189.1 | 6.1 | 808.5 | 819.8 | 805.7 | 814.5 | 828.1 | 604.8 | 643.6 | 741 | 423.6 | 747.5 | 26.9 | 76.8 | 119.6 | 59.2 | 280.1 | 265.1 | 77.9 | 185 | 212 | 106.4
505 | 331 | 479.6 | 191.84 | 224.2499 | 259.2 | 251.2 | 263.7 | 242 | 580 | 27.4 | 20.9 | 58.7 | 4.6 | 194.2 | 5.9 | 810.7 | 818.1 | 791.1 | 814.4 | 832.3 | 607 | 639.9 | 737.2 | 425.6 | 747.3 | 26.9 | 77.1 | 120 | 59.4 | 280.8 | 265.6 | 78.1 | 185.4 | 212.6 | 106.7
506 | 332 | 479.6 | 191.84 | 224.2499 | 260.8 | 251.2 | 262.8 | 241.8 | 571.5 | 27.4 | 20.9 | 58.9 | 3.9 | 190.8 | 5.9 | 812.8 | 819.7 | 787 | 814.1 | 833.8 | 609.3 | 635.3 | 731.4 | 427.7 | 747.6 | 27 | 77.3 | 120.4 | 59.6 | 280.8 | 265.7 | 78.3 | 185.8 | 213.3 | 107.1
507 | 333 | 479.5 | 191.8 | 224.2031 | 261.9 | 250.6 | 263.1 | 241.7 | 581.2 | 27.5 | 20.9 | 59.1 | 4.1 | 178.9 | 5.9 | 814.8 | 817.9 | 790.1 | 813.9 | 833.7 | 611.7 | 633.1 | 731.3 | 429.8 | 748.5 | 27.1 | 77.6 | 120.7 | 59.9 | 280.4 | 265.2 | 78.6 | 186.2 | 214 | 107.4
508 | 334 | 478.9 | 191.56 | 223.9226 | 262.3 | 250.4 | 263.8 | 241.5 | 600.6 | 27.5 | 20.9 | 59.2 | 4.6 | 176.4 | 5.5 | 816.7 | 815.7 | 806.7 | 813.8 | 833.5 | 613.8 | 633 | 734.9 | 431.8 | 748.8 | 27.2 | 77.9 | 121.2 | 60.1 | 280.2 | 264.8 | 78.8 | 186.4 | 214.7 | 107.7
509 | 335 | 478.5 | 191.4 | 223.7356 | 261.6 | 250.7 | 263.5 | 241.1 | 605.8 | 27.6 | 20.9 | 59.4 | 4 | 190.2 | 5 | 818.5 | 814 | 803 | 813 | 836.8 | 615.9 | 632.7 | 736.1 | 434 | 747.8 | 27.3 | 78.2 | 121.3 | 60.4 | 280.4 | 264.5 | 79 | 186.9 | 215.6 | 108.1
510 | 336 | 478.6 | 191.44 | 223.7823 | 262.1 | 250.4 | 263.4 | 241 | 597 | 27.6 | 20.9 | 59.6 | 4.7 | 186 | 4.5 | 820.2 | 816.6 | 809.8 | 813.2 | 838.8 | 618.1 | 634.4 | 737.1 | 436.1 | 747.8 | 27.4 | 78.5 | 121.5 | 60.6 | 280.9 | 264.6 | 79.3 | 187.3 | 216.3 | 108.4
511 | 337 | 478.2 | 191.28 | 223.5953 | 262.2 | 250.1 | 263.3 | 240.9 | 579.7 | 27.7 | 20.9 | 59.7 | 4.6 | 170.8 | 4.5 | 821.9 | 817.3 | 821.9 | 813.3 | 840.5 | 620.2 | 636.3 | 735.5 | 438.3 | 746.9 | 27.5 | 78.7 | 121.8 | 60.8 | 280.9 | 264.6 | 79.5 | 187.8 | 217.1 | 108.8
512 | 338 | 478.9 | 191.56 | 223.9226 | 261.6 | 250.4 | 264.2 | 240.4 | 579.1 | 27.7 | 20.9 | 59.7 | 4.9 | 187.8 | 4.9 | 823.6 | 817.3 | 827.7 | 813.4 | 841.9 | 622.4 | 635.8 | 738.4 | 440.4 | 746.7 | 27.6 | 79 | 122 | 61.1 | 280.5 | 264.5 | 79.7 | 188.2 | 217.7 | 109.1
513 | 339 | 477.6 | 191.04 | 223.3148 | 259.5 | 250.6 | 264.9 | 240.1 | 578.6 | 27.8 | 20.9 | 59.8 | 4.9 | 201.8 | 5.4 | 825.1 | 818.2 | 823.1 | 813.9 | 844.2 | 624.4 | 638.5 | 742.9 | 442.7 | 747.2 | 27.7 | 79.3 | 122.3 | 61.3 | 280.3 | 264.6 | 79.9 | 188.4 | 218.3 | 109.4
514 | 340 | 477.8 | 191.12 | 223.4083 | 258.3 | 249.9 | 265.1 | 239.8 | 564.4 | 27.8 | 20.9 | 60 | 4.4 | 187.2 | 5.9 | 826.7 | 819.1 | 821.9 | 814.4 | 846.6 | 626.4 | 641.4 | 744.9 | 444.9 | 746.7 | 27.8 | 79.5 | 122.6 | 61.5 | 280.2 | 264.8 | 80.2 | 188.7 | 218.9 | 109.8
515 | 341 | 478.9 | 191.56 | 223.9226 | 259.2 | 249.7 | 264.6 | 240.4 | 553.8 | 27.8 | 20.9 | 60.1 | 4.1 | 196 | 6.4 | 828.2 | 817.2 | 817.3 | 814 | 847.5 | 628.4 | 645.4 | 746.4 | 447.1 | 747.6 | 27.9 | 79.8 | 123 | 61.8 | 280.8 | 264.9 | 80.4 | 189.1 | 219.6 | 110.1
516 | 342 | 478.4 | 191.36 | 223.6888 | 260.2 | 249 | 263.8 | 241.5 | 540.1 | 27.9 | 20.9 | 60.2 | 4.4 | 197.3 | 6.4 | 829.6 | 817.8 | 809.5 | 813.9 | 850.7 | 630.3 | 639.9 | 738.3 | 449.4 | 747.4 | 28 | 80.1 | 123.2 | 62 | 280.9 | 264.8 | 80.6 | 189.4 | 220.2 | 110.4
517 | 343 | 478.4 | 191.36 | 223.6888 | 261.4 | 248.7 | 263.8 | 242.3 | 532 | 28 | 20.9 | 60.3 | 4.8 | 189.8 | 5.8 | 830.9 | 819.6 | 806.6 | 813.4 | 852.7 | 632.3 | 640.8 | 739.9 | 451.7 | 748.2 | 28.1 | 80.4 | 123.5 | 62.3 | 280.9 | 264.7 | 80.9 | 189.8 | 220.7 | 110.7
518 | 344 | 479.1 | 191.64 | 224.0161 | 263.5 | 248.9 | 263.9 | 242.4 | 525.4 | 28 | 20.8 | 60.4 | 4.5 | 173.3 | 5.1 | 832.2 | 822.7 | 791 | 813.9 | 852.8 | 634.3 | 644 | 743 | 454.1 | 747.7 | 28.2 | 80.7 | 123.9 | 62.5 | 280.8 | 265.1 | 81.1 | 190.2 | 221.3 | 111
519 | 345 | 477.3 | 190.92 | 223.1745 | 265.1 | 249.1 | 264.1 | 242.6 | 528.4 | 28.1 | 20.9 | 60.3 | 4.9 | 162.8 | 4.5 | 833.3 | 825.1 | 773.9 | 813.8 | 855 | 636.4 | 639.6 | 729.9 | 456.5 | 748 | 28.2 | 80.9 | 124.3 | 62.7 | 281 | 265.7 | 81.3 | 190.6 | 221.9 | 111.4
520 | 346 | 479.3 | 191.72 | 224.1096 | 266.9 | 248.6 | 265.3 | 242.4 | 523.5 | 28.2 | 20.8 | 60.4 | 5.1 | 181.1 | 4.2 | 834.5 | 826.2 | 767.9 | 813.1 | 854.9 | 639 | 633.6 | 720.8 | 459 | 746.4 | 28.3 | 81.2 | 124.3 | 63 | 281.7 | 265.9 | 81.5 | 191 | 222.5 | 111.7
521 | 347 | 478.6 | 191.44 | 223.7823 | 268.3 | 248.2 | 266.8 | 242.3 | 506.8 | 28.2 | 20.8 | 60.5 | 4.4 | 203.8 | 3.8 | 835.7 | 823.5 | 768 | 811.9 | 856.1 | 641.8 | 625.2 | 711 | 461.5 | 745.1 | 28.4 | 81.5 | 124.5 | 63.2 | 282 | 266 | 81.8 | 191.4 | 223.1 | 112.1
522 | 348 | 480 | 192 | 224.4369 | 270.7 | 247.7 | 267.1 | 242.5 | 501.7 | 28.3 | 20.8 | 60.6 | 4 | 215.9 | 3.5 | 836.9 | 822.3 | 773.1 | 811.7 | 857.1 | 644.4 | 620.7 | 705.7 | 464.1 | 744.8 | 28.5 | 81.8 | 124.9 | 63.5 | 282.1 | 266.6 | 82 | 192 | 223.6 | 112.4
523 | 349 | 479.4 | 191.76 | 224.1564 | 270.5 | 246.6 | 267.8 | 242.8 | 503.9 | 28.4 | 20.8 | 60.7 | 4.3 | 211.6 | 2.9 | 838 | 821.7 | 772.9 | 812.3 | 858.8 | 646.8 | 621.2 | 706.9 | 466.6 | 745.7 | 28.6 | 82.1 | 125.3 | 63.7 | 282.1 | 266.7 | 82.2 | 192.5 | 224.2 | 112.7
524 | 350 | 478.9 | 191.56 | 223.9226 | 269.8 | 245.3 | 268.2 | 244.2 | 499.9 | 28.6 | 20.8 | 61 | 4.6 | 191.8 | 2.7 | 839.2 | 821.9 | 770.7 | 813.6 | 860.6 | 648.9 | 624 | 705.2 | 469.2 | 745.9 | 28.7 | 82.4 | 125.6 | 63.9 | 282.3 | 266.8 | 82.4 | 192.9 | 224.8 | 113.1
525 | 351 | 479.3 | 191.72 | 224.1096 | 268.9 | 245 | 269 | 245 | 495 | 28.7 | 20.8 | 61.2 | 4.2 | 179.5 | 2.6 | 840.5 | 822.7 | 775 | 814.2 | 862.5 | 651 | 623.3 | 705.8 | 471.9 | 746.6 | 28.8 | 82.6 | 125.8 | 64.2 | 282.3 | 267 | 82.7 | 193.3 | 225.2 | 113.4
526 | 352 | 479.1 | 191.64 | 224.0161 | 269.1 | 245.6 | 270.8 | 244.5 | 492.2 | 28.8 | 20.8 | 61.3 | 4.1 | 193.6 | 2.5 | 841.9 | 822.9 | 780 | 814.8 | 862.3 | 652.9 | 625.2 | 710.1 | 474.5 | 747.5 | 28.9 | 82.9 | 126.1 | 64.4 | 282.4 | 267.3 | 82.9 | 193.7 | 225.8 | 113.7
527 | 353 | 479.6 | 191.84 | 224.2499 | 269.7 | 245.2 | 271.9 | 244.2 | 500.7 | 28.8 | 20.8 | 61.3 | 4.5 | 212.4 | 2.7 | 843.1 | 821.8 | 779.3 | 814.7 | 864 | 654.8 | 621.7 | 707.4 | 477.3 | 747.9 | 29 | 83.2 | 126.4 | 64.7 | 282.7 | 267.7 | 83.1 | 194.1 | 226.4 | 114
528 | 354 | 479.4 | 191.76 | 224.1564 | 270.3 | 244.5 | 272 | 243.9 | 506.6 | 28.8 | 20.8 | 61.2 | 4 | 216.6 | 3.4 | 844.1 | 822.3 | 777.4 | 815.3 | 864 | 656.6 | 618.2 | 703.5 | 480.1 | 748.2 | 29.1 | 83.5 | 126.7 | 64.9 | 283.1 | 267.7 | 83.3 | 194.5 | 227 | 114.3
529 | 355 | 479.4 | 191.76 | 224.1564 | 270.1 | 244.7 | 271.1 | 244.8 | 508.5 | 28.8 | 20.8 | 61.3 | 4.2 | 212.3 | 4.1 | 845.3 | 825.1 | 776.9 | 817.1 | 864 | 658.4 | 615.1 | 702.4 | 482.9 | 748.4 | 29.2 | 83.7 | 126.9 | 65.2 | 283.5 | 267.5 | 83.6 | 194.8 | 227.5 | 114.6
530 | 356 | 477.8 | 191.12 | 223.4083 | 270.1 | 244.8 | 270.4 | 245.8 | 505.9 | 28.9 | 20.8 | 61.3 | 3.9 | 214.3 | 4.3 | 846.4 | 826 | 765.2 | 818.5 | 864.4 | 659.9 | 610.5 | 698 | 485.8 | 748.7 | 29.3 | 84 | 127.3 | 65.4 | 284.8 | 267.5 | 83.8 | 195.3 | 228 | 115
531 | 357 | 479.1 | 191.64 | 224.0161 | 271.3 | 245 | 270.5 | 247 | 515.3 | 29 | 20.8 | 61.2 | 4.2 | 221.8 | 4.5 | 847.6 | 826.7 | 767.8 | 820.1 | 864.7 | 661.6 | 609.5 | 699.7 | 488.7 | 748.5 | 29.4 | 84.3 | 127.7 | 65.6 | 285.3 | 268 | 84.1 | 195.6 | 228.5 | 115.4
532 | 358 | 478.7 | 191.48 | 223.8291 | 272.5 | 245.1 | 270.5 | 247.5 | 519.5 | 29 | 20.8 | 61.3 | 3.8 | 213.1 | 4.8 | 848.6 | 826 | 772.5 | 821 | 864.7 | 663 | 613.3 | 706.4 | 491.6 | 750.5 | 29.5 | 84.6 | 128 | 65.9 | 286.2 | 268.8 | 84.3 | 196.2 | 229.1 | 115.7
533 | 359 | 478.6 | 191.44 | 223.7823 | 272.8 | 245.2 | 270.8 | 247.6 | 517.9 | 29.1 | 20.8 | 61.5 | 4.5 | 208.1 | 4.9 | 849.4 | 825.4 | 776.4 | 821.5 | 867.1 | 664.2 | 618.6 | 713.5 | 494.5 | 751.5 | 29.6 | 84.9 | 128.4 | 66.1 | 285.8 | 269.4 | 84.5 | 196.6 | 229.6 | 116.1
534 | 360 | 478.8 | 191.52 | 223.8758 | 273.2 | 245.1 | 271.8 | 246.9 | 508.5 | 29 | 20.8 | 61.6 | 4.1 | 208.9 | 4.8 | 850.2 | 824.6 | 774.2 | 821.5 | 868.8 | 665.3 | 621.9 | 719.3 | 497.4 | 752.2 | 29.7 | 85.1 | 128.7 | 66.4 | 285.2 | 269.8 | 84.7 | 197.2 | 230 | 116.4
535 | 361 | 477.9 | 191.16 | 223.455 | 272.9 | 244.6 | 272.8 | 247 | 499.3 | 29.1 | 20.8 | 61.6 | 3.7 | 201.9 | 4.8 | 850.9 | 827.6 | 762.6 | 822.9 | 869.8 | 666.2 | 617.4 | 713.9 | 500.2 | 752.1 | 29.8 | 85.4 | 128.9 | 66.6 | 284.9 | 270 | 84.9 | 197.5 | 230.5 | 116.8
536 | 362 | 478.4 | 191.36 | 223.6888 | 271.4 | 244.1 | 273.5 | 247 | 493.9 | 29.2 | 20.8 | 61.6 | 3.6 | 197.9 | 4.9 | 851.6 | 829.5 | 766.2 | 824 | 870.3 | 667.3 | 622.8 | 721.2 | 503.1 | 753.3 | 30 | 85.7 | 129.1 | 66.8 | 284.5 | 270.2 | 85.2 | 197.9 | 230.9 | 117.1
537 | 363 | 478.3 | 191.32 | 223.6421 | 272.1 | 243.8 | 273.4 | 246.9 | 485.4 | 29.3 | 20.8 | 61.5 | 4 | 197 | 4.8 | 852.4 | 829.2 | 759.3 | 823.3 | 869 | 668.6 | 630.9 | 724 | 506 | 753.6 | 30.1 | 86 | 129.4 | 67.1 | 284.2 | 270.5 | 85.4 | 198.3 | 231.3 | 117.4
538 | 364 | 478.4 | 191.36 | 223.6888 | 273.7 | 243.8 | 273.6 | 247.2 | 478.4 | 29.3 | 20.8 | 61.5 | 3.9 | 194.8 | 4.6 | 853.2 | 827.7 | 754.2 | 820.9 | 868.4 | 670.1 | 629.3 | 716.8 | 508.9 | 751.6 | 30.2 | 86.2 | 129.6 | 67.3 | 284.2 | 271.2 | 85.6 | 198.7 | 231.8 | 117.7
539 | 365 | 477.7 | 191.08 | 223.3615 | 275.2 | 243.8 | 274.3 | 247.1 | 472.8 | 29.3 | 20.8 | 61.5 | 4.3 | 191.5 | 4.3 | 854.1 | 826.4 | 757.5 | 819.9 | 866 | 671.8 | 626.1 | 712 | 511.8 | 750.2 | 30.3 | 86.5 | 129.9 | 67.5 | 284.2 | 271.4 | 85.8 | 199 | 232.2 | 118
540 | 366 | 477.9 | 191.16 | 223.455 | 275.4 | 243.7 | 275.7 | 246.6 | 473.3 | 29.5 | 20.8 | 61.4 | 3.8 | 201.6 | 4.6 | 854.9 | 825.8 | 767.5 | 819.9 | 867.3 | 673.3 | 629.1 | 720.3 | 514.8 | 752.2 | 30.4 | 86.8 | 130.2 | 67.8 | 283.5 | 271.8 | 86 | 199.6 | 232.7 | 118.4
541 | 367 | 477.7 | 191.08 | 223.3615 | 275.5 | 243.4 | 276.6 | 247 | 478.7 | 29.7 | 20.8 | 61.4 | 3.7 | 211.3 | 4.6 | 855.7 | 824.1 | 782.2 | 820.1 | 868.2 | 674.5 | 637.4 | 732.5 | 517.8 | 753.5 | 30.5 | 87.1 | 130.5 | 68 | 283.5 | 271.8 | 86.2 | 199.8 | 233.2 | 118.7
542 | 368 | 478.1 | 191.24 | 223.5485 | 275.9 | 243.1 | 277.2 | 247.1 | 481.9 | 29.7 | 20.8 | 61.4 | 3.9 | 210.3 | 4.6 | 856.3 | 823.9 | 781.8 | 820.2 | 868.3 | 675.5 | 646.4 | 735.8 | 520.7 | 753.9 | 30.6 | 87.4 | 130.9 | 68.3 | 283.5 | 272 | 86.4 | 200.2 | 233.6 | 119
543 | 369 | 478.1 | 191.24 | 223.5485 | 275.2 | 243.1 | 277.1 | 246.6 | 473.2 | 29.8 | 20.8 | 61.4 | 4.1 | 213.1 | 4.7 | 856.7 | 826.5 | 778 | 821.2 | 867.5 | 676.6 | 642.5 | 730.5 | 523.6 | 753.5 | 30.7 | 87.6 | 131.2 | 68.5 | 283.3 | 271.5 | 86.7 | 200.6 | 234.1 | 119.3
544 | 370 | 478.7 | 191.48 | 223.8291 | 275.1 | 243 | 276.9 | 245.7 | 472.9 | 29.9 | 20.8 | 61.5 | 5 | 221.1 | 4.5 | 857.1 | 827.2 | 782.2 | 821.3 | 866.5 | 678 | 641.4 | 728.8 | 526.4 | 754.1 | 30.8 | 87.9 | 131.5 | 68.7 | 283.2 | 271.4 | 86.9 | 200.9 | 234.5 | 119.6
545 | 371 | 477.9 | 191.16 | 223.455 | 275.3 | 243.1 | 277.1 | 245.7 | 469.3 | 29.9 | 20.7 | 61.8 | 5.3 | 219.8 | 4.5 | 857.5 | 826.6 | 789 | 820 | 866.9 | 679.4 | 641.5 | 725.8 | 529.1 | 752.1 | 30.9 | 88.2 | 131.7 | 69 | 283.2 | 271.3 | 87.1 | 201.4 | 235 | 119.9
546 | 372 | 477.2 | 190.88 | 223.1277 | 274.6 | 244 | 277.7 | 245.8 | 464.2 | 29.9 | 20.7 | 61.9 | 5.3 | 210.9 | 4.6 | 857.9 | 825.1 | 793.2 | 818.9 | 866.7 | 681.1 | 647.8 | 733.9 | 531.8 | 752.3 | 31 | 88.4 | 132.1 | 69.2 | 283.2 | 271.3 | 87.3 | 201.7 | 235.5 | 120.2
547 | 373 | 477.3 | 190.92 | 223.1745 | 274 | 244.8 | 277.3 | 245.8 | 461 | 30 | 20.8 | 62 | 4.6 | 201.2 | 4.7 | 858.3 | 823.4 | 800 | 818.2 | 868.8 | 682.4 | 652.1 | 740.2 | 534.5 | 753.5 | 31.1 | 88.7 | 132.4 | 69.5 | 283.2 | 271.6 | 87.5 | 202.1 | 236 | 120.5
548 | 374 | 478 | 191.2 | 223.5018 | 273.9 | 245.2 | 277.1 | 245.9 | 463 | 30 | 20.7 | 62 | 4.3 | 193.5 | 4.7 | 858.5 | 822.8 | 798 | 818.7 | 870.6 | 683.4 | 658.1 | 746.9 | 537 | 755.8 | 31.2 | 89 | 132.6 | 69.7 | 283.8 | 271.7 | 87.8 | 202.5 | 236.4 | 120.8
549 | 375 | 478.5 | 191.4 | 223.7356 | 272.1 | 245.3 | 276.5 | 245.9 | 467 | 30 | 20.7 | 62.1 | 4.3 | 191.6 | 4.8 | 858.8 | 823.5 | 787.8 | 820 | 871.7 | 684.2 | 661.5 | 752.8 | 539.4 | 757.5 | 31.4 | 89.2 | 132.9 | 70 | 284 | 271.9 | 88 | 202.8 | 236.8 | 121.2
550 | 376 | 478 | 191.2 | 223.5018 | 272.1 | 244.7 | 275.5 | 245.5 | 463.4 | 30 | 20.7 | 62.2 | 4.3 | 191.8 | 4.9 | 859.1 | 825.3 | 781.1 | 820 | 871.1 | 685 | 659.1 | 746.7 | 541.6 | 757.1 | 31.5 | 89.5 | 133 | 70.2 | 284 | 271.8 | 88.2 | 203.1 | 237.3 | 121.5
551 | 377 | 478.7 | 191.48 | 223.8291 | 273.1 | 244.3 | 274.8 | 245.7 | 462.5 | 30.1 | 20.7 | 62.1 | 4.3 | 193.5 | 4.6 | 859.3 | 827.2 | 787.2 | 820.5 | 871.5 | 686 | 661.9 | 748.2 | 543.7 | 758.3 | 31.6 | 89.8 | 133.3 | 70.4 | 284.1 | 271.9 | 88.4 | 203.4 | 237.8 | 121.8
552 | 378 | 478.6 | 191.44 | 223.7823 | 273.6 | 243.7 | 274.5 | 246.4 | 469.1 | 30.1 | 20.7 | 62 | 4.5 | 199.6 | 4.8 | 859.5 | 828.6 | 782.8 | 820.7 | 870.6 | 686.9 | 654.1 | 742.6 | 545.8 | 756.7 | 31.7 | 90 | 133.6 | 70.7 | 284.1 | 271.8 | 88.6 | 203.9 | 238.3 | 122.1
553 | 379 | 478.3 | 191.32 | 223.6421 | 272.2 | 243.5 | 274.4 | 247.1 | 470.9 | 30.2 | 20.7 | 61.9 | 4.7 | 202.7 | 4.9 | 859.9 | 829.6 | 780 | 821.7 | 872 | 688 | 646 | 739 | 547.8 | 756.7 | 31.8 | 90.3 | 133.9 | 70.9 | 284.3 | 271.9 | 88.8 | 204.1 | 238.7 | 122.4
554 | 380 | 478.3 | 191.32 | 223.6421 | 271.7 | 243.8 | 274.3 | 247.6 | 469.4 | 30.2 | 20.7 | 62 | 4.4 | 201.1 | 4.9 | 860.1 | 828.5 | 788.6 | 821.6 | 872.4 | 689.2 | 638 | 736.7 | 549.8 | 757.6 | 31.9 | 90.5 | 134.2 | 71.2 | 284.1 | 272.1 | 89.1 | 204.6 | 239.1 | 122.7
555 | 381 | 478.6 | 191.44 | 223.7823 | 272.2 | 244 | 274.7 | 248.6 | 471.6 | 30.3 | 20.7 | 62 | 4.7 | 206.7 | 5.1 | 860.5 | 827.1 | 798.3 | 821.6 | 871.2 | 690.4 | 637 | 738.3 | 551.7 | 757.5 | 32 | 90.8 | 134.6 | 71.4 | 283.5 | 272.1 | 89.3 | 204.9 | 239.4 | 123
556 | 382 | 478.5 | 191.4 | 223.7356 | 272.5 | 244.2 | 274.8 | 248.5 | 471.7 | 30.3 | 20.7 | 62 | 5.2 | 211.9 | 5.9 | 860.7 | 825.9 | 794 | 821.5 | 872.1 | 691.6 | 638.9 | 740.9 | 553.7 | 757.8 | 32.1 | 91.1 | 134.8 | 71.7 | 283.5 | 272.3 | 89.5 | 205.3 | 239.9 | 123.3
557 | 383 | 479.2 | 191.68 | 224.0629 | 273.3 | 244.5 | 275.6 | 248.9 | 472 | 30.4 | 20.7 | 62 | 4.8 | 211.7 | 6.2 | 860.9 | 826.5 | 788.7 | 821.8 | 872.6 | 692.9 | 646.2 | 744.5 | 555.6 | 758 | 32.3 | 91.3 | 135.1 | 71.9 | 283.2 | 272.7 | 89.7 | 205.8 | 240.4 | 123.6
558 | 384 | 479.4 | 191.76 | 224.1564 | 273.7 | 245.1 | 276.3 | 249.4 | 471.4 | 30.4 | 20.7 | 61.9 | 5 | 207 | 6.1 | 861.2 | 829.1 | 791.1 | 823.1 | 871.7 | 694.2 | 649.2 | 746.4 | 557.5 | 757.6 | 32.4 | 91.6 | 135.4 | 72.2 | 283.1 | 272.9 | 89.9 | 206 | 240.8 | 123.9
559 | 385 | 480.3 | 192.12 | 224.5772 | 274.3 | 244.7 | 276.6 | 249.7 | 477.6 | 30.4 | 20.7 | 61.9 | 4.2 | 205.7 | 5.9 | 861.6 | 828.8 | 803.6 | 823.3 | 871.5 | 695.4 | 645.2 | 740.2 | 559.4 | 756.6 | 32.5 | 91.9 | 135.9 | 72.4 | 282.9 | 273.2 | 90.1 | 206.4 | 241.3 | 124.2
560 | 386 | 479.8 | 191.92 | 224.3434 | 274.3 | 244.4 | 277.3 | 249.8 | 481.3 | 30.5 | 20.7 | 61.9 | 4.8 | 197.3 | 4.9 | 862 | 827.2 | 809.3 | 823.6 | 870.2 | 696.4 | 648.2 | 744 | 561.1 | 755.8 | 32.6 | 92.1 | 136.2 | 72.6 | 283 | 273.1 | 90.3 | 206.8 | 241.9 | 124.5
561 | 387 | 479.2 | 191.68 | 224.0629 | 272.3 | 244.6 | 278 | 249.6 | 481.9 | 30.6 | 20.7 | 61.9 | 5 | 185 | 4.3 | 862.3 | 827.5 | 806.3 | 824.5 | 871.7 | 697.3 | 651 | 747.3 | 563 | 756.2 | 32.7 | 92.4 | 136.4 | 72.9 | 283.4 | 273.2 | 90.5 | 207.1 | 242.4 | 124.8
562 | 388 | 476 | 190.4 | 222.5666 | 270.2 | 245.3 | 278.2 | 249.5 | 483.4 | 30.7 | 20.7 | 62 | 4.4 | 180.6 | 4.4 | 862.8 | 828 | 804.3 | 825.6 | 872.9 | 698.1 | 649.4 | 747.2 | 564.9 | 756.9 | 32.8 | 92.6 | 136.7 | 73.1 | 283.3 | 273.1 | 90.7 | 207.5 | 242.9 | 125.1
563 | 389 | 478.7 | 191.48 | 223.8291 | 268.8 | 246.1 | 278.4 | 248.3 | 481.7 | 30.7 | 20.7 | 62 | 4.5 | 189.9 | 4.3 | 863.2 | 828.9 | 805.3 | 826 | 873.3 | 698.9 | 649 | 749.7 | 566.6 | 757.2 | 32.9 | 92.9 | 136.9 | 73.4 | 283.5 | 273 | 91 | 207.9 | 243.4 | 125.5
564 | 390 | 478.8 | 191.52 | 223.8758 | 269.4 | 246.2 | 278 | 247.7 | 479.8 | 30.8 | 20.7 | 62 | 4.6 | 213.1 | 4.5 | 863.5 | 830.3 | 805.5 | 826.6 | 873.4 | 699.6 | 660.2 | 754.1 | 568.3 | 758.2 | 33.1 | 93.1 | 137.2 | 73.6 | 283.7 | 273.2 | 91.2 | 208.2 | 243.9 | 125.7
565 | 391 | 479 | 191.6 | 223.9694 | 270 | 246.8 | 277.6 | 247.5 | 475.1 | 30.9 | 20.7 | 62.1 | 5.1 | 203.7 | 4.4 | 863.9 | 829.4 | 802.2 | 825.7 | 873.4 | 700.5 | 662.1 | 756 | 569.9 | 757.6 | 33.2 | 93.4 | 137.5 | 73.9 | 283.9 | 273.7 | 91.4 | 208.6 | 244.4 | 126
566 | 392 | 478.3 | 191.32 | 223.6421 | 269.8 | 247.5 | 277 | 246.9 | 471.1 | 30.9 | 20.7 | 62.2 | 5 | 200 | 4.7 | 864.1 | 830.9 | 801.5 | 825.5 | 873.9 | 701.2 | 663.7 | 753.7 | 571.6 | 758.4 | 33.3 | 93.6 | 137.9 | 74.1 | 283.8 | 273.9 | 91.6 | 208.9 | 244.9 | 126.4
567 | 393 | 478.3 | 191.32 | 223.6421 | 270.5 | 248.2 | 276.5 | 246.4 | 464 | 30.9 | 20.7 | 62.2 | 4.7 | 216.4 | 4.9 | 864.5 | 831.9 | 800.1 | 825.8 | 873.8 | 702 | 663.8 | 755.4 | 573.2 | 759 | 33.4 | 93.9 | 138 | 74.4 | 283.9 | 273.8 | 91.8 | 209.2 | 245.4 | 126.7
568 | 394 | 478.9 | 191.56 | 223.9226 | 271.3 | 248.8 | 276.5 | 246.4 | 460 | 30.9 | 20.7 | 62.2 | 4.9 | 199.2 | 5.1 | 864.6 | 832 | 790.6 | 826 | 875.1 | 702.7 | 663 | 754.1 | 574.8 | 760 | 33.5 | 94.1 | 138.3 | 74.6 | 284.1 | 274 | 92 | 209.5 | 245.9 | 126.9
569 | 395 | 478.3 | 191.32 | 223.6421 | 272.3 | 248.8 | 275.9 | 246.5 | 453.9 | 31 | 20.7 | 62.2 | 4.6 | 198 | 5 | 864.9 | 831.8 | 787.2 | 824.9 | 875.7 | 703.3 | 664.7 | 750.6 | 576.3 | 758.9 | 33.6 | 94.4 | 138.5 | 74.9 | 284.4 | 274.1 | 92.3 | 209.8 | 246.3 | 127.2
570 | 396 | 478.7 | 191.48 | 223.8291 | 272.7 | 248.7 | 275.9 | 246.8 | 446.6 | 31.1 | 20.7 | 62.2 | 4.5 | 203.2 | 5.1 | 865.3 | 830 | 782.2 | 824.3 | 875.8 | 704.1 | 658.9 | 746.1 | 577.8 | 758.7 | 33.7 | 94.6 | 138.8 | 75.2 | 284.4 | 274.1 | 92.5 | 210.2 | 246.8 | 127.6
571 | 397 | 478.5 | 191.4 | 223.7356 | 273.2 | 248 | 276.2 | 247.3 | 445.9 | 31.1 | 20.7 | 62.4 | 4.7 | 202.9 | 5.1 | 865.7 | 829.2 | 770.5 | 823.7 | 876.3 | 704.9 | 655.6 | 740.3 | 579.4 | 758.5 | 33.8 | 94.9 | 139.1 | 75.4 | 285 | 273.9 | 92.7 | 210.6 | 247.2 | 127.9
572 | 398 | 478.8 | 191.52 | 223.8758 | 275.3 | 247.7 | 275.8 | 247.5 | 443.6 | 31.2 | 20.7 | 62.7 | 4.5 | 203.1 | 5 | 865.8 | 828.5 | 755.5 | 822.6 | 874.9 | 705.7 | 650.2 | 733.3 | 580.8 | 757.8 | 34 | 95.1 | 139.3 | 75.7 | 285.2 | 273.9 | 92.9 | 210.9 | 247.5 | 128.2
573 | 399 | 479.1 | 191.64 | 224.0161 | 276.9 | 247.7 | 275.9 | 248 | 435.4 | 31.3 | 20.7 | 62.9 | 4.8 | 202.2 | 5.1 | 865.9 | 827.8 | 755.8 | 822.5 | 876 | 706.5 | 643.8 | 727.5 | 582.4 | 757.1 | 34.1 | 95.4 | 139.6 | 75.9 | 285.2 | 274 | 93.1 | 211.1 | 248 | 128.5
574 | 400 | 481.8 | 192.72 | 225.2786 | 277.5 | 247.7 | 275.7 | 248.5 | 430.5 | 31.3 | 20.7 | 63.1 | 4.7 | 202.3 | 5.2 | 866.1 | 828.8 | 752.1 | 823.1 | 874.4 | 707.3 | 639.8 | 728.1 | 583.8 | 756.7 | 34.2 | 95.6 | 139.8 | 76.2 | 285 | 274.2 | 93.3 | 211.4 | 248.5 | 128.9
575 | 401 | 482.7 | 193.08 | 225.6994 | 277.5 | 247.6 | 275.5 | 248 | 430.1 | 31.3 | 20.7 | 63.4 | 4.8 | 205.7 | 5.3 | 866.2 | 827.8 | 762.1 | 823.1 | 874.3 | 707.8 | 639.4 | 731.4 | 585.3 | 757 | 34.3 | 95.9 | 140 | 76.4 | 284.7 | 274.7 | 93.6 | 211.8 | 248.9 | 129.1
576 | 402 | 482.8 | 193.12 | 225.7462 | 277.4 | 247.6 | 275.3 | 247.6 | 433.7 | 31.3 | 20.7 | 63.5 | 4.6 | 210.4 | 5.4 | 866 | 826.3 | 760.1 | 822.4 | 875.1 | 708.4 | 644.3 | 736.5 | 586.8 | 758 | 34.4 | 96.1 | 140.4 | 76.7 | 284.5 | 275.1 | 93.8 | 212.2 | 249.3 | 129.4
577 | 403 | 483.5 | 193.4 | 226.0735 | 279 | 247.8 | 275.8 | 248.1 | 439.6 | 31.4 | 20.7 | 63.5 | 4.9 | 220.3 | 5.4 | 865.9 | 825.5 | 771.4 | 823 | 874.8 | 709 | 653.5 | 742.4 | 588.3 | 758.8 | 34.6 | 96.4 | 141 | 77 | 284.6 | 275.7 | 94 | 212.5 | 249.8 | 129.7
578 | 404 | 481.3 | 192.52 | 225.0448 | 279.2 | 248.3 | 276.7 | 248.4 | 444.9 | 31.4 | 20.7 | 63.5 | 4.5 | 217.7 | 4.9 | 865.7 | 825.8 | 785 | 823.4 | 874.3 | 709.7 | 650.9 | 741.7 | 590 | 758.3 | 34.7 | 96.6 | 141.1 | 77.2 | 284.8 | 275.8 | 94.2 | 212.8 | 250.4 | 130
579 | 405 | 482.7 | 193.08 | 225.6994 | 278.4 | 248.2 | 277 | 249.3 | 448.7 | 31.4 | 20.7 | 63.5 | 4.6 | 215 | 4.2 | 865.4 | 825.6 | 789.3 | 823.5 | 873.8 | 710.4 | 650.6 | 743.7 | 591.5 | 759.2 | 34.8 | 96.9 | 141.3 | 77.5 | 285.3 | 276 | 94.4 | 213.2 | 251 | 130.4
580 | 406 | 482.7 | 193.08 | 225.6994 | 277.4 | 248.3 | 276.6 | 250.4 | 446.5 | 31.5 | 20.7 | 63.7 | 4.1 | 213 | 3.5 | 865.3 | 824 | 800.1 | 822.3 | 872.2 | 711 | 650.4 | 745.2 | 593 | 759.1 | 34.9 | 97.1 | 141.6 | 77.7 | 285.6 | 276.2 | 94.6 | 213.4 | 251.5 | 130.7
581 | 407 | 482.2 | 192.88 | 225.4656 | 277.5 | 248.5 | 275.4 | 251 | 442.8 | 31.5 | 20.7 | 63.8 | 4.4 | 205.9 | 3.1 | 865.1 | 822.4 | 800.7 | 821.5 | 874.3 | 711.5 | 651.2 | 747.4 | 594.5 | 759 | 35 | 97.4 | 142 | 78 | 286 | 276.3 | 94.8 | 213.8 | 252 | 131
582 | 408 | 482.2 | 192.88 | 225.4656 | 277.6 | 248.4 | 275.2 | 250.8 | 450.3 | 31.6 | 20.7 | 63.9 | 4.3 | 201.4 | 3 | 864.8 | 823.1 | 790.9 | 821.5 | 874.8 | 712.1 | 641.1 | 736 | 596 | 758.5 | 35.1 | 97.6 | 142.3 | 78.3 | 285.9 | 276.2 | 95 | 214 | 252.4 | 131.3
583 | 409 | 480.1 | 192.04 | 224.4837 | 278.3 | 248.7 | 275.4 | 251.2 | 456.9 | 31.8 | 20.7 | 63.9 | 4.3 | 198.8 | 3.2 | 864.5 | 822.3 | 775.5 | 821.1 | 876 | 712.8 | 630.9 | 726.3 | 597.5 | 758.3 | 35.3 | 97.9 | 142.6 | 78.5 | 285.9 | 276.2 | 95.2 | 214.4 | 252.8 | 131.6
584 | 410 | 479 | 191.6 | 223.9694 | 279.9 | 248.5 | 275.4 | 250.1 | 452.1 | 31.8 | 20.7 | 64 | 4.3 | 216.7 | 3.7 | 864.1 | 820.1 | 768.9 | 820 | 876 | 713.5 | 628.8 | 719.7 | 598.9 | 757.3 | 35.4 | 98.2 | 142.7 | 78.8 | 286.4 | 276.3 | 95.5 | 214.8 | 253.2 | 131.9
585 | 411 | 479.4 | 191.76 | 224.1564 | 280.7 | 248.7 | 275.5 | 249.3 | 444.7 | 31.8 | 20.6 | 64 | 4.2 | 207.3 | 4.1 | 863.7 | 819.5 | 767.5 | 819.9 | 875.5 | 713.8 | 631.3 | 717.6 | 600.3 | 756.1 | 35.5 | 98.4 | 143 | 79.1 | 286.7 | 276.2 | 95.7 | 215.1 | 253.7 | 132.2
586 | 412 | 479.2 | 191.68 | 224.0629 | 281.8 | 249.1 | 277.5 | 249.4 | 442.3 | 31.8 | 20.6 | 64 | 4.4 | 204.9 | 4.5 | 863.4 | 819.1 | 771.4 | 820.4 | 876.9 | 714.2 | 624.7 | 713.8 | 601.7 | 755.4 | 35.6 | 98.7 | 143.2 | 79.3 | 287.2 | 276.2 | 95.9 | 215.3 | 254.2 | 132.5
587 | 413 | 479.9 | 191.96 | 224.3902 | 280.4 | 248.9 | 279 | 250 | 454.6 | 31.8 | 20.6 | 64.1 | 4 | 205.7 | 4.4 | 863.4 | 818.9 | 778.5 | 821.5 | 877.6 | 714.4 | 621.2 | 717.6 | 603.1 | 754.7 | 35.7 | 98.9 | 143.5 | 79.6 | 287.5 | 276.3 | 96.1 | 215.6 | 254.7 | 132.9
588 | 414 | 480.1 | 192.04 | 224.4837 | 280 | 248.7 | 280.2 | 250.2 | 455.8 | 31.8 | 20.6 | 64.1 | 3.8 | 196.5 | 4.2 | 863.4 | 819.2 | 780.2 | 822.2 | 877.8 | 714.3 | 623.4 | 721.7 | 604.4 | 755.8 | 35.9 | 99.2 | 143.8 | 79.9 | 287.8 | 276.7 | 96.3 | 216 | 255.1 | 133.2
589 | 415 | 479.2 | 191.68 | 224.0629 | 279.7 | 249 | 280 | 250.6 | 457 | 31.8 | 20.6 | 64.2 | 4.4 | 193.4 | 4.2 | 863.5 | 820.1 | 783.5 | 823.5 | 877.8 | 714.3 | 627.9 | 728.6 | 605.7 | 756.8 | 36 | 99.4 | 144.1 | 80.2 | 288 | 277 | 96.6 | 216.4 | 255.5 | 133.5
590 | 416 | 479.6 | 191.84 | 224.2499 | 279.8 | 249 | 279.5 | 249.8 | 450.7 | 31.7 | 20.6 | 64.3 | 4.3 | 187.7 | 4.4 | 863.6 | 820.2 | 776.5 | 823.6 | 877.6 | 714.5 | 622.8 | 721.2 | 606.9 | 755.2 | 36.1 | 99.7 | 144.4 | 80.4 | 288.3 | 277.3 | 96.8 | 216.7 | 255.9 | 133.8
591 | 417 | 480.8 | 192.32 | 224.811 | 278.9 | 248.6 | 279.5 | 249.7 | 446.4 | 31.7 | 20.6 | 64.4 | 4.5 | 172.6 | 4.8 | 863.5 | 819 | 772.2 | 823.1 | 877.9 | 714.8 | 614.4 | 714.5 | 608.1 | 753.9 | 36.2 | 99.9 | 144.8 | 80.7 | 288.3 | 277.3 | 97 | 216.9 | 256.4 | 134.1
592 | 418 | 479.5 | 191.8 | 224.2031 | 278.3 | 248.2 | 279.7 | 250.1 | 448.5 | 31.7 | 20.6 | 64.4 | 4 | 174.2 | 5.2 | 863.4 | 820 | 781.1 | 824 | 876.9 | 715 | 618.9 | 719.8 | 609.5 | 754.8 | 36.3 | 100.2 | 145 | 81 | 288.2 | 277.3 | 97.2 | 217.2 | 256.9 | 134.4
593 | 419 | 481 | 192.4 | 224.9045 | 278.5 | 248.8 | 279.9 | 251.1 | 454.9 | 31.7 | 20.6 | 64.4 | 4.1 | 180.8 | 5.2 | 863.4 | 821.1 | 790 | 824.9 | 877.2 | 715.1 | 627.8 | 731.5 | 610.8 | 755.7 | 36.5 | 100.4 | 145.5 | 81.2 | 288.3 | 277.7 | 97.4 | 217.6 | 257.4 | 134.7
594 | 420 | 481 | 192.4 | 224.9045 | 278.6 | 249.3 | 279.4 | 252.3 | 454.9 | 31.8 | 20.6 | 64.6 | 4.2 | 188.5 | 5.3 | 863.4 | 821 | 796.9 | 825.1 | 876.7 | 715.3 | 641.8 | 740.2 | 612.2 | 755.6 | 36.6 | 100.7 | 145.6 | 81.5 | 288.5 | 277.6 | 97.6 | 217.9 | 257.9 | 135
595 | 421 | 479.7 | 191.88 | 224.2967 | 278.8 | 249.2 | 278.8 | 252.8 | 450.9 | 31.8 | 20.6 | 64.8 | 4.3 | 186.8 | 5.2 | 863.4 | 820.6 | 803.4 | 824.9 | 877 | 715.5 | 648.5 | 744.9 | 613.6 | 756.7 | 36.7 | 100.9 | 145.9 | 81.8 | 288.7 | 277.5 | 97.8 | 218.1 | 258.4 | 135.3
596 | 422 | 480.3 | 192.12 | 224.5772 | 277.2 | 249.7 | 278.5 | 253.4 | 452.4 | 31.9 | 20.6 | 64.9 | 3.9 | 189.5 | 5 | 863.4 | 820.2 | 804.4 | 824.9 | 877 | 715.6 | 657.5 | 750.5 | 614.8 | 756.7 | 36.8 | 101.1 | 146.1 | 82.1 | 289 | 277.5 | 98 | 218.4 | 258.8 | 135.6
597 | 423 | 479.4 | 191.76 | 224.1564 | 275.8 | 250.7 | 278.9 | 253.8 | 457.1 | 31.9 | 20.6 | 65.1 | 4.3 | 196.4 | 5.2 | 863.4 | 822.4 | 804.6 | 826 | 877 | 715.6 | 656.2 | 748.5 | 616.1 | 756.4 | 36.9 | 101.4 | 146.4 | 82.3 | 289.1 | 277.8 | 98.2 | 218.7 | 259.3 | 135.9
598 | 424 | 479.9 | 191.96 | 224.3902 | 276.5 | 251.5 | 278.9 | 254 | 460.1 | 32 | 20.6 | 65.2 | 4.6 | 180.8 | 5.5 | 863.8 | 822.8 | 811.2 | 825.5 | 874.4 | 716 | 655.2 | 746.8 | 617.3 | 754.1 | 37.1 | 101.6 | 146.8 | 82.6 | 289.7 | 278 | 98.5 | 219.1 | 259.8 | 136.2
599 | 425 | 479.4 | 191.76 | 224.1564 | 275.2 | 252.5 | 279.1 | 254.4 | 456.4 | 32 | 20.6 | 65.3 | 4.3 | 184.8 | 5.5 | 864 | 822.7 | 815.2 | 825.3 | 871.8 | 716.6 | 650 | 739.8 | 618.6 | 752.8 | 37.2 | 101.9 | 147 | 82.9 | 289.7 | 278.1 | 98.7 | 219.5 | 260.4 | 136.4
600 | 426 | 479.5 | 191.8 | 224.2031 | 274.4 | 253.4 | 278.8 | 255.1 | 454.4 | 32.2 | 20.6 | 65.4 | 4.6 | 190.3 | 5.6 | 864 | 821.9 | 816.2 | 824.8 | 872.2 | 717.2 | 647.2 | 737 | 619.9 | 751.2 | 37.3 | 102.1 | 147.2 | 83.2 | 289.7 | 278.1 | 98.9 | 219.8 | 260.9 | 136.7
601 | 427 | 479.8 | 191.92 | 224.3434 | 274.1 | 254.2 | 278.1 | 255.2 | 454.2 | 32.3 | 20.6 | 65.5 | 4.3 | 191.4 | 5.8 | 864.1 | 821 | 821.4 | 824.9 | 871.4 | 717.6 | 645.8 | 737.1 | 621.2 | 751.4 | 37.4 | 102.3 | 147.5 | 83.4 | 290.3 | 278.1 | 99.1 | 220.1 | 261.4 | 137
602 | 428 | 480 | 192 | 224.4369 | 274.1 | 254.8 | 277.2 | 255.4 | 462.4 | 32.4 | 20.6 | 65.4 | 4.6 | 189.8 | 5.9 | 864 | 820.3 | 826.3 | 825.2 | 869.2 | 717.8 | 642.2 | 738.5 | 622.6 | 750.1 | 37.6 | 102.6 | 148 | 83.7 | 290.9 | 278.1 | 99.3 | 220.5 | 261.9 | 137.4
603 | 429 | 480 | 192 | 224.4369 | 273.2 | 256.5 | 276.4 | 256.2 | 470.1 | 32.5 | 20.6 | 65.4 | 4.3 | 178.8 | 5.8 | 863.9 | 820.3 | 824.2 | 825.4 | 868.4 | 717.9 | 648.9 | 744.2 | 623.8 | 749.7 | 37.7 | 102.8 | 148.2 | 84 | 290.9 | 278.1 | 99.5 | 220.8 | 262.4 | 137.7
604 | 430 | 479.9 | 191.96 | 224.3902 | 272.6 | 257.4 | 276.2 | 256.4 | 468.9 | 32.6 | 20.6 | 65.5 | 4.3 | 186 | 5.4 | 863.7 | 820.9 | 819.7 | 826.2 | 871.1 | 718 | 653.4 | 744 | 625.1 | 751.2 | 37.8 | 103 | 148.4 | 84.3 | 290.6 | 278 | 99.7 | 221.1 | 262.9 | 138
605 | 431 | 480.1 | 192.04 | 224.4837 | 272.6 | 257.9 | 275.8 | 256.7 | 467.9 | 32.6 | 20.6 | 65.6 | 3.9 | 204.3 | 5.1 | 863.6 | 820.4 | 825.2 | 826.6 | 872.5 | 718.2 | 660.6 | 752.6 | 626.5 | 752.4 | 37.9 | 103.3 | 148.7 | 84.6 | 290.4 | 277.8 | 99.9 | 221.3 | 263.4 | 138.3
606 | 432 | 494.3 | 197.72 | 231.1233 | 273.5 | 258.5 | 275.5 | 256.3 | 483.3 | 32.6 | 20.6 | 65.7 | 4.2 | 200.3 | 5.1 | 863.5 | 820 | 828.2 | 827 | 872.9 | 718.4 | 659.5 | 756.9 | 628 | 751.6 | 38.1 | 103.5 | 149.2 | 84.9 | 290.4 | 277.8 | 100.2 | 221.6 | 263.9 | 138.6
607 | 433 | 492.5 | 197 | 230.2816 | 273.2 | 259.6 | 276.1 | 255.9 | 509.4 | 32.6 | 20.6 | 65.7 | 4.2 | 196.7 | 5.2 | 863.4 | 821.7 | 828.1 | 828.2 | 871.3 | 718.7 | 658.6 | 760.9 | 629.5 | 751.2 | 38.2 | 103.7 | 149.6 | 85.1 | 290.6 | 277.8 | 100.3 | 221.8 | 264.5 | 138.9
608 | 434 | 499.8 | 199.92 | 233.695 | 273.8 | 260.5 | 276.9 | 255.4 | 529.8 | 32.6 | 20.6 | 65.7 | 4.5 | 176.8 | 5.2 | 863.4 | 822.1 | 827.6 | 827.7 | 866.7 | 719 | 649.1 | 751.7 | 630.9 | 749.7 | 38.3 | 104 | 150.1 | 85.4 | 291.2 | 277.7 | 100.6 | 222.1 | 265.1 | 139.2
609 | 435 | 517 | 206.8 | 241.7373 | 274.4 | 260.9 | 277.2 | 255 | 538.1 | 32.6 | 20.6 | 65.7 | 4.7 | 192.1 | 5.6 | 863.6 | 818.4 | 822.6 | 826.6 | 861.7 | 719.4 | 638.1 | 739.9 | 632.3 | 746.4 | 38.4 | 104.1 | 150.6 | 85.7 | 291.7 | 277.7 | 100.8 | 222.4 | 265.7 | 139.6
610 | 436 | 530.2 | 212.08 | 247.9093 | 275 | 261.8 | 275.9 | 255.7 | 546.1 | 32.6 | 20.6 | 65.7 | 4.4 | 205.2 | 5.8 | 864 | 816.9 | 827.1 | 827 | 861.9 | 719.9 | 641.5 | 745.1 | 633.8 | 746.9 | 38.6 | 104.4 | 150.9 | 86 | 292.1 | 278 | 101 | 222.7 | 266.3 | 139.9
611 | 437 | 537.3 | 214.92 | 251.2291 | 276.1 | 262.8 | 275.3 | 257.3 | 560.4 | 32.7 | 20.6 | 65.7 | 4.5 | 205.2 | 5.7 | 864.1 | 817.3 | 827.1 | 828.1 | 862.1 | 720.1 | 642.3 | 747.9 | 635.4 | 748.6 | 38.7 | 104.6 | 151.1 | 86.3 | 293.3 | 278.5 | 101.2 | 223 | 266.9 | 140.2
612 | 438 | 539.7 | 215.88 | 252.3513 | 275 | 263.3 | 275.5 | 259 | 587.8 | 32.7 | 20.6 | 65.8 | 4.3 | 186.3 | 5.2 | 864.3 | 817.7 | 826.3 | 828.8 | 862.1 | 720.5 | 640.9 | 743.8 | 637.1 | 748.9 | 38.8 | 104.8 | 151.7 | 86.5 | 294.2 | 278.9 | 101.5 | 223.4 | 267.6 | 140.5
613 | 439 | 540.8 | 216.32 | 252.8656 | 274.4 | 264.6 | 277 | 260.3 | 613.4 | 32.7 | 20.6 | 65.8 | 4.6 | 188.7 | 5.1 | 864.4 | 818.3 | 826.7 | 830.2 | 863.5 | 721.1 | 643.1 | 744.6 | 638.6 | 749.9 | 38.9 | 105.1 | 152.1 | 86.8 | 295.1 | 279.3 | 101.7 | 223.7 | 268.2 | 140.9
614 | 440 | 541.2 | 216.48 | 253.0526 | 275.2 | 265.9 | 277.8 | 261.7 | 615.6 | 32.7 | 20.6 | 65.9 | 4.7 | 211.1 | 5.1 | 864.7 | 819.1 | 826.8 | 831.3 | 865 | 721.5 | 649 | 753 | 640.1 | 751.3 | 39.1 | 105.3 | 152.3 | 87.1 | 296 | 279.8 | 101.9 | 224.2 | 268.9 | 141.2
615 | 441 | 542 | 216.8 | 253.4267 | 276.1 | 266.1 | 278.6 | 262.7 | 612.6 | 32.9 | 20.6 | 66 | 4.7 | 210.6 | 5.8 | 864.7 | 819.2 | 830.6 | 831.6 | 866.1 | 721.8 | 658.4 | 759.1 | 641.6 | 753.2 | 39.2 | 105.6 | 152.8 | 87.4 | 296.8 | 280.4 | 102.1 | 224.5 | 269.5 | 141.6
616 | 442 | 541.9 | 216.76 | 253.38 | 277.7 | 266.8 | 279.4 | 263 | 618.5 | 33 | 20.6 | 66.3 | 5.1 | 216.7 | 6.1 | 864.7 | 818.9 | 832.2 | 831.8 | 867 | 722.4 | 671.8 | 767.4 | 643.1 | 755.1 | 39.3 | 105.8 | 153.3 | 87.7 | 297.4 | 281.5 | 102.3 | 225 | 270 | 141.9
617 | 443 | 543.8 | 217.52 | 254.2683 | 279.6 | 267.7 | 281 | 263 | 602.4 | 33.1 | 20.6 | 66.4 | 4.9 | 235.6 | 6 | 864.6 | 817.9 | 833.1 | 831.5 | 869.2 | 723.1 | 684.1 | 773.4 | 644.6 | 756.4 | 39.4 | 106 | 153.6 | 88 | 298.1 | 282.3 | 102.6 | 225.4 | 270.7 | 142.2
618 | 444 | 546.3 | 218.52 | 255.4373 | 281.3 | 268.3 | 281.9 | 262.4 | 584.4 | 33.1 | 20.6 | 66.6 | 4.7 | 222.6 | 5.9 | 864.6 | 818 | 831.3 | 831.4 | 870.6 | 723.9 | 687.8 | 778 | 646 | 757.3 | 39.6 | 106.3 | 153.9 | 88.2 | 298.5 | 283.2 | 102.8 | 225.9 | 271.4 | 142.5
619 | 445 | 547.7 | 219.08 | 256.0919 | 283 | 268.9 | 282.9 | 262.5 | 576.4 | 33.2 | 20.5 | 66.7 | 4.5 | 218.2 | 5.4 | 864.5 | 819.2 | 826.8 | 832.2 | 872.3 | 724.8 | 694.7 | 780.1 | 647.3 | 758.9 | 39.7 | 106.5 | 154.2 | 88.5 | 298.9 | 284.1 | 103 | 226.3 | 272 | 142.8
620 | 446 | 548.7 | 219.48 | 256.5595 | 283.7 | 269.6 | 284.4 | 263.7 | 566.5 | 33.3 | 20.5 | 66.7 | 4.5 | 257.7 | 5.1 | 864.5 | 819.8 | 828.8 | 833.1 | 872.6 | 725.3 | 688.7 | 779.1 | 648.6 | 760.6 | 39.8 | 106.8 | 154.5 | 88.8 | 299.6 | 284.7 | 103.2 | 226.7 | 272.6 | 143.2
621 | 447 | 548.3 | 219.32 | 256.3724 | 283.1 | 269.9 | 284.4 | 264 | 572.5 | 33.4 | 20.5 | 66.8 | 5 | 218.2 | 4.8 | 864.4 | 821.2 | 825.6 | 833.7 | 873.6 | 725.9 | 679 | 772.6 | 649.9 | 759.9 | 40 | 107 | 154.8 | 89.1 | 299.9 | 285 | 103.4 | 227 | 273.2 | 143.5
622 | 448 | 550.3 | 220.12 | 257.3076 | 282.6 | 269.7 | 284.9 | 263.4 | 559.8 | 33.4 | 20.6 | 66.9 | 4.9 | 199.6 | 4.9 | 864.4 | 822.8 | 828.5 | 834.6 | 874.4 | 726.6 | 684.3 | 773.7 | 651.1 | 761.2 | 40.1 | 107.3 | 155.1 | 89.4 | 300.4 | 285.1 | 103.7 | 227.4 | 273.7 | 143.8
623 | 449 | 551 | 220.4 | 257.6349 | 283.4 | 270.2 | 285.4 | 262.6 | 553.6 | 33.4 | 20.5 | 67 | 4.8 | 218.9 | 5.1 | 864.4 | 825.6 | 826.2 | 836.1 | 873.9 | 727.4 | 685 | 772.4 | 652.4 | 761.5 | 40.2 | 107.5 | 155.6 | 89.7 | 300.6 | 285.1 | 103.9 | 227.8 | 274.2 | 144.1
624 | 450 | 550 | 220 | 257.1673 | 284.1 | 270.7 | 286.9 | 262.6 | 545.9 | 33.4 | 20.5 | 67.2 | 4.2 | 197.6 | 5.2 | 864.5 | 826.1 | 829.6 | 837.4 | 875 | 728.1 | 692.5 | 776.7 | 653.6 | 762.8 | 40.3 | 107.7 | 155.8 | 90 | 301 | 285.5 | 104.1 | 228.1 | 274.7 | 144.5
625 | 451 | 548.8 | 219.52 | 256.6062 | 283.9 | 271.1 | 287.4 | 262.4 | 541.4 | 33.4 | 20.5 | 67.3 | 4.3 | 202.9 | 4.9 | 864.4 | 826 | 825.6 | 837.9 | 876.7 | 728.7 | 692.9 | 774.3 | 654.8 | 763.6 | 40.5 | 108 | 156.2 | 90.3 | 301.5 | 286 | 104.3 | 228.5 | 275.3 | 144.8
626 | 452 | 549.4 | 219.76 | 256.8868 | 284.6 | 271.4 | 288.2 | 262.3 | 548.6 | 33.5 | 20.5 | 67.3 | 4.5 | 226.2 | 4.6 | 864.3 | 827.3 | 820.9 | 838.1 | 876.9 | 729.2 | 681.1 | 766.7 | 656 | 764.7 | 40.6 | 108.2 | 156.8 | 90.5 | 302.3 | 286.4 | 104.5 | 228.8 | 275.9 | 145.1
627 | 453 | 550.8 | 220.32 | 257.5414 | 284.1 | 270.7 | 288.3 | 262.7 | 564.6 | 33.6 | 20.5 | 67.3 | 4.9 | 218.7 | 4.4 | 864.1 | 828.8 | 813.2 | 838.9 | 875.8 | 729.9 | 669.8 | 755.8 | 657.2 | 763.6 | 40.7 | 108.5 | 157.5 | 90.8 | 303.5 | 286.8 | 104.7 | 229.2 | 276.4 | 145.4
628 | 454 | 552 | 220.8 | 258.1025 | 283.7 | 269.9 | 287.4 | 263.9 | 569.5 | 33.7 | 20.5 | 67.4 | 5 | 208.6 | 4.5 | 864.2 | 829.8 | 809.4 | 839.9 | 875.2 | 730.8 | 661.1 | 746.7 | 658.5 | 762.8 | 40.9 | 108.7 | 157.9 | 91.1 | 304 | 286.9 | 105 | 229.5 | 276.9 | 145.8
629 | 455 | 551.6 | 220.64 | 257.9154 | 283.7 | 270 | 287.9 | 265.7 | 576.7 | 33.7 | 20.5 | 67.5 | 5.1 | 234.9 | 4.3 | 864.2 | 828.6 | 809 | 840.9 | 876.5 | 731.6 | 657.8 | 743.5 | 659.7 | 762.1 | 41 | 109 | 158.3 | 91.4 | 304.3 | 287.4 | 105.2 | 229.9 | 277.4 | 146.2
630 | 456 | 553 | 221.2 | 258.5701 | 283.8 | 271.2 | 289.3 | 266.6 | 569 | 33.8 | 20.5 | 67.6 | 4.3 | 227.6 | 3.9 | 864.2 | 827.7 | 808.4 | 841 | 877.1 | 732.1 | 659.8 | 749.4 | 661 | 763.2 | 41.1 | 109.2 | 158.5 | 91.7 | 304.8 | 288.1 | 105.4 | 230.2 | 278 | 146.5
631 | 457 | 553.6 | 221.44 | 258.8506 | 284.6 | 272.3 | 290.6 | 266.9 | 564.2 | 33.8 | 20.5 | 67.7 | 4.9 | 217.8 | 3.7 | 864.2 | 828.5 | 808 | 842.5 | 878.8 | 732.5 | 657.9 | 749 | 662.1 | 763.7 | 41.2 | 109.5 | 158.8 | 92 | 305.3 | 288.5 | 105.6 | 230.6 | 278.5 | 146.8
632 | 458 | 555.5 | 222.2 | 259.739 | 284.3 | 272.3 | 290.7 | 268 | 557.5 | 33.9 | 20.5 | 67.7 | 4.8 | 225.8 | 3.5 | 864.3 | 828.4 | 811.5 | 843 | 880.8 | 732.8 | 656.6 | 749.3 | 663.1 | 764.4 | 41.4 | 109.7 | 159.3 | 92.3 | 306 | 289 | 105.9 | 231.1 | 279 | 147.1
633 | 459 | 556.9 | 222.76 | 260.3936 | 285.2 | 271.9 | 289.6 | 268.8 | 559.1 | 34 | 20.5 | 67.8 | 4.8 | 234.2 | 3.2 | 864.4 | 831.1 | 813.6 | 845 | 881.1 | 733.3 | 651.8 | 744.4 | 664.3 | 764.2 | 41.5 | 110 | 159.9 | 92.6 | 306.9 | 289.5 | 106.1 | 231.4 | 279.6 | 147.5
634 | 460 | 555.3 | 222.12 | 259.6455 | 286.5 | 272.7 | 289.8 | 269 | 573.7 | 34.2 | 20.5 | 68 | 5 | 221.2 | 3.3 | 864.6 | 831.5 | 813.9 | 845.5 | 879.8 | 733.9 | 646.5 | 741.1 | 665.5 | 762.6 | 41.7 | 110.2 | 160.6 | 92.9 | 307.5 | 290.1 | 106.3 | 231.7 | 280.1 | 147.8
635 | 461 | 555.8 | 222.32 | 259.8793 | 288.5 | 272.4 | 291.8 | 269.9 | 605.8 | 34.3 | 20.5 | 68.1 | 4.5 | 206.8 | 3.7 | 864.8 | 831.7 | 814 | 846.5 | 880.4 | 734.3 | 640.3 | 736 | 666.7 | 762 | 41.8 | 110.5 | 160.8 | 93.2 | 308.3 | 290.6 | 106.6 | 232.1 | 280.7 | 148.1
636 | 462 | 555.6 | 222.24 | 259.7858 | 290.9 | 271.8 | 293.5 | 270 | 627.4 | 34.5 | 20.5 | 68.1 | 4 | 213.8 | 3.9 | 865.1 | 830 | 822.5 | 846 | 880.5 | 734.9 | 639.4 | 738.6 | 667.9 | 762.5 | 41.9 | 110.8 | 161.3 | 93.5 | 309 | 291.1 | 106.8 | 232.5 | 281.4 | 148.5
637 | 463 | 556.5 | 222.6 | 260.2066 | 292.2 | 271.1 | 294.5 | 271.7 | 647.1 | 34.6 | 20.5 | 68.2 | 4.5 | 230.5 | 3.9 | 865.4 | 827.6 | 825.3 | 845.4 | 881.4 | 735.3 | 645.5 | 744.8 | 669.2 | 763.9 | 42.1 | 111 | 161.9 | 93.8 | 309.7 | 291.6 | 107 | 232.9 | 282 | 148.9
638 | 464 | 557.5 | 223 | 260.6742 | 294 | 270.6 | 296.4 | 273.2 | 651.9 | 34.7 | 20.5 | 68.2 | 4.3 | 239.2 | 3.6 | 865.6 | 826.8 | 829.2 | 845.2 | 881.3 | 735.9 | 653.4 | 750.7 | 670.5 | 765.1 | 42.2 | 111.3 | 162.3 | 94.1 | 310.2 | 292.1 | 107.3 | 233.3 | 282.7 | 149.2
639 | 465 | 556.6 | 222.64 | 260.2533 | 296 | 271.3 | 297.1 | 274 | 652.3 | 34.7 | 20.5 | 68.2 | 4.4 | 233.6 | 3.4 | 865.7 | 826.4 | 831.3 | 845.4 | 882 | 736.3 | 657.3 | 753.6 | 671.8 | 766.5 | 42.3 | 111.5 | 162.6 | 94.3 | 310.9 | 292.7 | 107.5 | 233.7 | 283.4 | 149.6
640 | 466 | 556.8 | 222.72 | 260.3468 | 296.6 | 272.5 | 297.3 | 275.1 | 638.2 | 34.7 | 20.5 | 68.4 | 4.6 | 213.2 | 3.4 | 865.9 | 825.5 | 834.4 | 845.2 | 881.2 | 736.6 | 662.2 | 755.8 | 672.9 | 767.7 | 42.5 | 111.8 | 162.8 | 94.6 | 311.6 | 293.3 | 107.7 | 234.1 | 284.1 | 149.9
641 | 467 | 559.4 | 223.76 | 261.5625 | 297.3 | 274.1 | 298.6 | 275.3 | 629.9 | 34.8 | 20.5 | 68.4 | 3.9 | 207.9 | 3.4 | 866 | 823.6 | 835.3 | 844.9 | 880.5 | 737 | 667 | 759.5 | 673.9 | 768.6 | 42.6 | 112 | 163.2 | 94.9 | 312.4 | 293.8 | 108 | 234.6 | 284.7 | 150.2
642 | 468 | 560.8 | 224.32 | 262.2172 | 298.5 | 275.9 | 299.4 | 275.3 | 635.7 | 35 | 20.5 | 68.4 | 4 | 231.9 | 3.3 | 865.9 | 822.5 | 834.7 | 844.8 | 880 | 737.4 | 669.2 | 763.5 | 675 | 771.2 | 42.7 | 112.3 | 163.7 | 95.2 | 312.9 | 294.6 | 108.2 | 235.1 | 285.3 | 150.5
643 | 469 | 559.4 | 223.76 | 261.5625 | 298.5 | 277.1 | 300.3 | 276.5 | 641 | 35.1 | 20.5 | 68.5 | 4.4 | 229.4 | 3.2 | 865.8 | 821.9 | 834.4 | 845.9 | 879.4 | 737.9 | 670.8 | 765.1 | 676.1 | 771.9 | 42.9 | 112.5 | 164.3 | 95.5 | 313.4 | 294.9 | 108.4 | 235.5 | 286 | 150.9
644 | 470 | 561 | 224.4 | 262.3107 | 299.5 | 278.2 | 301.3 | 277.2 | 652 | 35.2 | 20.5 | 68.5 | 4.8 | 208.8 | 3.2 | 865.9 | 820.2 | 838 | 846.1 | 879.1 | 738.4 | 673.7 | 769 | 677.2 | 771.6 | 43 | 112.8 | 165 | 95.8 | 314.7 | 295 | 108.7 | 235.8 | 286.7 | 151.3
645 | 471 | 560.6 | 224.24 | 262.1236 | 300.2 | 279 | 301.8 | 278.4 | 651.6 | 35.4 | 20.5 | 68.7 | 4.6 | 197.6 | 3.2 | 866 | 819.2 | 837.4 | 846.1 | 879.1 | 738.9 | 677.4 | 772.8 | 678.1 | 772.6 | 43.1 | 113 | 165.2 | 96.1 | 315.4 | 295.2 | 108.9 | 236.2 | 287.4 | 151.7
646 | 472 | 560.8 | 224.32 | 262.2172 | 301.7 | 278.6 | 301.4 | 279.9 | 654.3 | 35.5 | 20.5 | 68.8 | 5.1 | 207.2 | 3.2 | 866 | 818.8 | 834.3 | 846.3 | 879.5 | 739.5 | 676.8 | 773.5 | 679.2 | 774.2 | 43.3 | 113.3 | 165.6 | 96.4 | 315.6 | 295.8 | 109.2 | 236.6 | 288.1 | 152.1
647 | 473 | 560.7 | 224.28 | 262.1704 | 302.1 | 278.8 | 301.6 | 280.7 | 652.3 | 35.5 | 20.5 | 69 | 4.2 | 219.3 | 3.1 | 865.7 | 819.2 | 830.4 | 846 | 880.6 | 740.3 | 675.4 | 775.7 | 680.3 | 776 | 43.4 | 113.5 | 166 | 96.7 | 316 | 296.2 | 109.4 | 237 | 288.7 | 152.4
648 | 474 | 561.7 | 224.68 | 262.638 | 301.6 | 279.2 | 301.2 | 281 | 631.6 | 35.6 | 20.5 | 69.2 | 4.6 | 218.5 | 2.9 | 865.6 | 820.6 | 826.8 | 846.4 | 880.1 | 740.9 | 674.4 | 773.9 | 681.3 | 776.5 | 43.6 | 113.8 | 166.5 | 97 | 316.4 | 296.8 | 109.6 | 237.3 | 289.3 | 152.8
649 | 475 | 562.5 | 225 | 263.012 | 302.6 | 279.2 | 302 | 281 | 630.1 | 35.7 | 20.5 | 69.3 | 5.1 | 206.8 | 2.7 | 865.5 | 822.2 | 825.3 | 847.4 | 878.3 | 741.5 | 672.7 | 768 | 682.2 | 776.6 | 43.7 | 113.9 | 166.9 | 97.3 | 316.7 | 297.2 | 109.9 | 237.7 | 289.9 | 153.1
650 | 476 | 562.3 | 224.92 | 262.9185 | 304.4 | 278.9 | 302.9 | 280.7 | 619.9 | 35.8 | 20.5 | 69.3 | 4.6 | 188.3 | 2.9 | 865.4 | 823.1 | 823.4 | 848.6 | 878.5 | 742.3 | 666.3 | 763.8 | 683.2 | 775.8 | 43.8 | 114 | 167.1 | 97.6 | 317.2 | 297.6 | 110.2 | 238.1 | 290.5 | 153.4
651 | 477 | 561.1 | 224.44 | 262.3574 | 305.4 | 278.9 | 302.9 | 280.7 | 606.6 | 35.9 | 20.5 | 69.4 | 4.7 | 191.4 | 2.7 | 865.4 | 824.1 | 824.9 | 848.9 | 880.2 | 742.7 | 662.2 | 762.4 | 684.1 | 775.1 | 44 | 114.2 | 167.5 | 97.9 | 318.1 | 297.8 | 110.4 | 238.5 | 291.1 | 153.8
652 | 478 | 563.8 | 225.52 | 263.6199 | 305.8 | 280.9 | 303.1 | 281 | 610.1 | 35.9 | 20.5 | 69.3 | 4.7 | 217.5 | 2.5 | 865.4 | 825.2 | 824 | 849.3 | 879.5 | 743.2 | 660 | 761 | 684.9 | 775.2 | 44.1 | 114.4 | 167.9 | 98.2 | 318.7 | 298.1 | 110.6 | 238.9 | 291.7 | 154.1
653 | 479 | 563.7 | 225.48 | 263.5731 | 306.7 | 281.1 | 303.7 | 281.8 | 621.2 | 36 | 20.5 | 69.4 | 4.8 | 230.4 | 2.6 | 865.4 | 823.9 | 824.1 | 849.1 | 878.8 | 743.7 | 652.9 | 754.2 | 685.7 | 773.6 | 44.2 | 114.7 | 168.5 | 98.5 | 318.8 | 298.2 | 110.9 | 239.2 | 292.3 | 154.5
654 | 480 | 564.4 | 225.76 | 263.9004 | 307.4 | 281.8 | 303.7 | 281.2 | 629.4 | 36.1 | 20.5 | 69.6 | 5.6 | 227 | 2.5 | 865.4 | 824.8 | 824 | 850 | 878.8 | 744.1 | 653.7 | 755.6 | 686.5 | 773 | 44.4 | 114.9 | 169 | 98.9 | 319.5 | 298.7 | 111.1 | 239.6 | 293 | 154.9
655 | 481 | 563.5 | 225.4 | 263.4796 | 307.2 | 281.8 | 304.9 | 281.3 | 624.5 | 36.2 | 20.5 | 69.7 | 5.1 | 231.5 | 2.4 | 865.4 | 826.2 | 826.5 | 850.7 | 880.8 | 744.4 | 657.4 | 759.2 | 687.1 | 773.4 | 44.5 | 115.2 | 169.2 | 99.1 | 319.7 | 299.4 | 111.4 | 240 | 293.6 | 155.2
656 | 482 | 562.8 | 225.12 | 263.1523 | 307.3 | 281.5 | 304.6 | 282 | 622.9 | 36.3 | 20.5 | 69.8 | 5 | 238.5 | 2.4 | 865.4 | 826.5 | 825.8 | 850.9 | 882.7 | 744.6 | 661 | 758.8 | 687.8 | 773.8 | 44.6 | 115.4 | 169.6 | 99.5 | 320 | 299.7 | 111.6 | 240.4 | 294.3 | 155.5
657 | 483 | 562.5 | 225 | 263.012 | 309.1 | 281.2 | 303 | 281.7 | 626.5 | 36.4 | 20.4 | 69.9 | 5.1 | 242.1 | 2.7 | 865.7 | 827.2 | 826.6 | 852.2 | 883.3 | 745 | 662.2 | 758.4 | 688.5 | 773.6 | 44.8 | 115.7 | 170.2 | 99.8 | 321 | 300.2 | 111.9 | 240.8 | 294.9 | 155.9
658 | 484 | 564 | 225.6 | 263.7134 | 309.8 | 281.8 | 302.3 | 280.4 | 626.5 | 36.5 | 20.4 | 70 | 5.1 | 234 | 2.9 | 866.2 | 826.6 | 830.7 | 852.7 | 882 | 745.5 | 663 | 758.7 | 689.3 | 773.3 | 44.9 | 116 | 170.8 | 100.1 | 321.2 | 300.7 | 112.1 | 241.1 | 295.6 | 156.2
659 | 485 | 564.2 | 225.68 | 263.8069 | 310.3 | 282.5 | 304.2 | 280.7 | 633.1 | 36.6 | 20.4 | 70.1 | 4.6 | 232.5 | 3.1 | 866.6 | 825.3 | 834.2 | 852.6 | 882.2 | 745.9 | 663.9 | 759.6 | 690 | 773.9 | 45.1 | 116.2 | 171.1 | 100.4 | 321.3 | 300.7 | 112.4 | 241.5 | 296.3 | 156.6
660 | 486 | 563.8 | 225.52 | 263.6199 | 310.8 | 282.4 | 305.1 | 281.2 | 625.4 | 36.6 | 20.4 | 70.2 | 4.3 | 234.2 | 3.2 | 866.9 | 825.1 | 833.3 | 853.5 | 883.5 | 746.1 | 666.2 | 762 | 690.7 | 775.6 | 45.2 | 116.5 | 171.4 | 100.7 | 321.3 | 300.7 | 112.6 | 241.9 | 296.9 | 156.9
661 | 487 | 565.6 | 226.24 | 264.4615 | 313.1 | 282.7 | 305 | 281.9 | 614.3 | 36.7 | 20.4 | 70.1 | 4.4 | 234.1 | 2.9 | 867.6 | 825.9 | 835.9 | 854.6 | 885.3 | 746.3 | 671 | 764 | 691.4 | 775.5 | 45.4 | 116.8 | 171.8 | 101 | 321.6 | 300.5 | 112.9 | 242.3 | 297.4 | 157.3
662 | 488 | 567 | 226.8 | 265.1161 | 313.1 | 283.3 | 305.1 | 282.5 | 608.2 | 36.7 | 20.4 | 70.1 | 4.5 | 234.9 | 2.8 | 867.9 | 825.4 | 833.5 | 855.8 | 884.5 | 746.4 | 674 | 765.7 | 692 | 776.5 | 45.5 | 117 | 172.3 | 101.3 | 321.2 | 300.8 | 113.1 | 242.6 | 298.1 | 157.6
663 | 489 | 565.5 | 226.2 | 264.4148 | 312.2 | 283.3 | 304.9 | 282.3 | 622.2 | 36.7 | 20.4 | 70.2 | 4.9 | 243.7 | 2.8 | 868.1 | 825.1 | 830.9 | 855.3 | 884 | 746.6 | 670.3 | 763.3 | 692.6 | 777.6 | 45.7 | 117.3 | 172.9 | 101.7 | 321.7 | 300.9 | 113.4 | 242.9 | 298.6 | 158
664 | 490 | 563.3 | 225.32 | 263.3861 | 312.8 | 283.4 | 305 | 281.9 | 630.5 | 36.7 | 20.4 | 70.1 | 4.9 | 247.7 | 2.9 | 868.2 | 825.3 | 831.9 | 855.3 | 883.7 | 747.1 | 667.3 | 766 | 693.4 | 777.7 | 45.8 | 117.6 | 173.2 | 102 | 322.6 | 301.2 | 113.6 | 243.3 | 299.2 | 158.3
665 | 491 | 564.7 | 225.88 | 264.0407 | 313.3 | 283.6 | 304.8 | 282 | 621.7 | 36.6 | 20.4 | 70.2 | 4.8 | 244.4 | 3.1 | 868.1 | 823.3 | 834.6 | 854.1 | 883.4 | 747.5 | 682.5 | 773.4 | 694.2 | 778.9 | 46 | 117.8 | 173.4 | 102.3 | 322.7 | 301.5 | 113.9 | 243.8 | 299.8 | 158.7
666 | 492 | 566.6 | 226.64 | 264.9291 | 315 | 284.4 | 304.6 | 283 | 622.8 | 36.5 | 20.4 | 70.2 | 4.9 | 246.4 | 3.2 | 868.1 | 823.9 | 834 | 855.2 | 881.5 | 747.9 | 691 | 780.3 | 695 | 780.5 | 46.1 | 118.1 | 173.9 | 102.6 | 322.7 | 302 | 114.2 | 244.1 | 300.5 | 159
667 | 493 | 565.2 | 226.08 | 264.2745 | 316.6 | 284.6 | 305 | 282.2 | 630.4 | 36.4 | 20.4 | 70.3 | 5.1 | 244.7 | 3.4 | 868.6 | 825.5 | 835.4 | 857.1 | 879.4 | 748.3 | 696 | 787.1 | 695.8 | 781.8 | 46.3 | 118.4 | 174.5 | 102.9 | 323.1 | 302.3 | 114.4 | 244.5 | 301.1 | 159.4
668 | 494 | 565.8 | 226.32 | 264.555 | 318.2 | 284 | 305.6 | 281.4 | 617.1 | 36.3 | 20.4 | 70.3 | 4.8 | 241.1 | 3.6 | 868.9 | 824.5 | 837 | 857.1 | 879.5 | 748.7 | 706.5 | 792.6 | 696.5 | 782 | 46.4 | 118.6 | 174.7 | 103.3 | 323.8 | 303 | 114.7 | 244.9 | 301.7 | 159.7
669 | 495 | 564.9 | 225.96 | 264.1342 | 319.4 | 284.3 | 306.3 | 281.9 | 591.7 | 36.3 | 20.4 | 70.4 | 5.3 | 247.5 | 4 | 869.1 | 824.6 | 836.2 | 857.6 | 880.1 | 749.1 | 711.3 | 795 | 697 | 783 | 46.6 | 118.9 | 174.8 | 103.6 | 324.2 | 303.1 | 114.9 | 245.2 | 302.4 | 160.1
670 | 496 | 564.3 | 225.72 | 263.8537 | 320.5 | 284.2 | 306.5 | 282.7 | 584.3 | 36.2 | 20.4 | 70.4 | 5.2 | 242.7 | 3.8 | 869.4 | 823.4 | 840.3 | 858.1 | 879.8 | 749.4 | 718.3 | 797.8 | 697.6 | 783.3 | 46.7 | 119.2 | 175.2 | 103.9 | 324.6 | 303.3 | 115.2 | 245.6 | 302.9 | 160.4
671 | 497 | 566 | 226.4 | 264.6486 | 318.9 | 284.4 | 306.4 | 283.3 | 581.1 | 36.2 | 20.4 | 70.3 | 4.7 | 231.6 | 3.6 | 869.8 | 823.2 | 842.6 | 858.8 | 880.3 | 749.6 | 723.8 | 799.7 | 698 | 782.5 | 46.9 | 119.2 | 175.5 | 104.3 | 325.2 | 303.5 | 115.4 | 246 | 303.5 | 160.8
672 | 498 | 565.7 | 226.28 | 264.5083 | 318.3 | 285.3 | 306.9 | 284 | 577.1 | 36.3 | 20.4 | 70.4 | 4.9 | 229.9 | 3.5 | 869.9 | 821.3 | 843.9 | 858.3 | 879.5 | 749.9 | 734.2 | 803.8 | 698.5 | 783.4 | 47 | 119.3 | 175.9 | 104.6 | 325.9 | 303.9 | 115.7 | 246.5 | 304.1 | 161.1
673 | 499 | 564.4 | 225.76 | 263.9004 | 319.1 | 285.6 | 307.1 | 283.7 | 568.9 | 36.5 | 20.4 | 70.5 | 4.7 | 223.8 | 3.2 | 869.9 | 819.3 | 844.9 | 857.6 | 879 | 750.5 | 737.4 | 803.9 | 698.9 | 783.3 | 47.2 | 119.5 | 176.1 | 104.9 | 326.3 | 304.3 | 115.9 | 246.9 | 304.7 | 161.5
674 | 500 | 564.3 | 225.72 | 263.8537 | 319.1 | 286.2 | 307.5 | 284.3 | 567.9 | 36.6 | 20.4 | 70.8 | 4.5 | 206.8 | 2.9 | 869.9 | 819.3 | 845 | 857.7 | 879.1 | 751.1 | 741.9 | 805.2 | 699.5 | 785.2 | 47.3 | 119.7 | 176.4 | 105.3 | 326.1 | 305.3 | 116.2 | 247.3 | 305.3 | 161.8
675 | 501 | 564.4 | 225.76 | 263.9004 | 318.9 | 287.5 | 307 | 284.8 | 564.7 | 36.6 | 20.4 | 70.9 | 5.1 | 195.4 | 3.6 | 869.6 | 820.4 | 844.8 | 858.2 | 879.6 | 751.6 | 746.7 | 805.8 | 700.1 | 786.7 | 47.5 | 119.9 | 176.9 | 105.6 | 326.1 | 305.7 | 116.5 | 247.7 | 305.9 | 162.2
676 | 502 | 565.8 | 226.32 | 264.555 | 319.6 | 288.3 | 307.4 | 284.9 | 565.2 | 36.7 | 20.4 | 71 | 5 | 205.9 | 4.8 | 869.8 | 820.6 | 845.3 | 859.5 | 879 | 752 | 747.9 | 808.9 | 700.6 | 787.1 | 47.6 | 120.2 | 177.3 | 105.9 | 325.8 | 305.9 | 116.7 | 248 | 306.5 | 162.5
677 | 503 | 566.6 | 226.64 | 264.9291 | 319.9 | 287.1 | 308.4 | 285.1 | 568.7 | 36.8 | 20.4 | 71.1 | 5.1 | 202.8 | 5.8 | 870.1 | 820.5 | 845.5 | 860.8 | 878 | 752.3 | 748.3 | 811.1 | 701.1 | 787.2 | 47.8 | 120.5 | 177.7 | 106.3 | 325.9 | 307.3 | 116.9 | 248.3 | 307.1 | 162.9
678 | 504 | 566.1 | 226.44 | 264.6953 | 319.3 | 286.7 | 308.6 | 285.2 | 572.3 | 36.9 | 20.4 | 71.1 | 4.5 | 213.9 | 5.8 | 870.7 | 820.9 | 846.1 | 862.1 | 877.9 | 752.5 | 742.5 | 808.8 | 701.7 | 788.5 | 48 | 120.8 | 178 | 106.6 | 326.3 | 308.1 | 117.2 | 248.8 | 307.7 | 163.2
679 | 505 | 566.4 | 226.56 | 264.8356 | 319.4 | 286.8 | 308.8 | 285 | 583.8 | 37.1 | 20.4 | 71.2 | 4.5 | 216.5 | 5.5 | 871 | 820.7 | 845.2 | 862.7 | 877.5 | 753 | 741.3 | 810.5 | 702.2 | 790 | 48.1 | 121.1 | 178.3 | 107 | 328.1 | 308.5 | 117.5 | 249.1 | 308.3 | 163.6
680 | 506 | 566.3 | 226.52 | 264.7888 | 318.2 | 286.6 | 308.6 | 285.2 | 584.9 | 37.2 | 20.4 | 71.1 | 4.8 | 213.3 | 5.8 | 871.1 | 820.6 | 844.4 | 862.8 | 877.6 | 753.6 | 747.6 | 811.9 | 702.9 | 791.4 | 48.3 | 121.4 | 178.9 | 107.3 | 327.7 | 308.4 | 117.7 | 249.5 | 308.9 | 164
681 | 507 | 566.9 | 226.76 | 265.0694 | 318.3 | 286.4 | 308.3 | 285.8 | 591.9 | 37.3 | 20.4 | 71.1 | 4.7 | 207.8 | 6.2 | 870.9 | 818.9 | 845 | 861.7 | 877.4 | 754.2 | 755.9 | 813.5 | 703.5 | 791.9 | 48.4 | 121.6 | 179.2 | 107.7 | 327.7 | 308.6 | 118 | 249.8 | 309.6 | 164.4
682 | 508 | 567.2 | 226.88 | 265.2096 | 318.3 | 286.3 | 307.3 | 285.8 | 589.4 | 37.4 | 20.4 | 71.1 | 4.5 | 211.2 | 6.5 | 870.7 | 817.9 | 844.2 | 861.3 | 877.3 | 754.7 | 758.2 | 817.4 | 704.3 | 792.2 | 48.6 | 121.9 | 179.4 | 108 | 328.6 | 309 | 118.3 | 250.1 | 310.3 | 164.8
683 | 509 | 566.4 | 226.56 | 264.8356 | 318.6 | 286.3 | 307 | 286.5 | 582.9 | 37.5 | 20.4 | 71 | 4.8 | 210.8 | 6.7 | 870.9 | 818.8 | 843.6 | 862.3 | 876.3 | 755.3 | 763.5 | 819 | 704.8 | 791.3 | 48.8 | 122.2 | 179.7 | 108.4 | 329 | 309.5 | 118.6 | 250.5 | 311 | 165.2
684 | 510 | 564.9 | 225.96 | 264.1342 | 318.1 | 286.4 | 307.3 | 286.4 | 564.1 | 37.5 | 20.3 | 70.9 | 5.1 | 210.8 | 6.7 | 871.5 | 818.9 | 843.1 | 863.7 | 875.9 | 755.9 | 769.7 | 819.9 | 705.4 | 790.7 | 48.9 | 122.5 | 180.1 | 108.7 | 329.3 | 310.3 | 118.8 | 250.9 | 311.7 | 165.6
685 | 511 | 564.5 | 225.8 | 263.9472 | 316.4 | 287.4 | 307.6 | 287 | 550.3 | 37.4 | 20.3 | 70.8 | 5.5 | 209 | 6.8 | 872.1 | 818.5 | 843.2 | 864.8 | 874.3 | 756.5 | 769.7 | 818.8 | 705.9 | 790.2 | 49.1 | 122.7 | 180.4 | 109.1 | 329.7 | 310.9 | 119.1 | 251.4 | 312.5 | 165.9
686 | 512 | 565.3 | 226.12 | 264.3213 | 316.2 | 288.5 | 307.3 | 287.2 | 536.8 | 37.4 | 20.3 | 70.8 | 4.9 | 209.4 | 7.1 | 872.4 | 817.9 | 843.2 | 865.4 | 874.2 | 757 | 767.2 | 817.9 | 706.3 | 787.8 | 49.2 | 122.9 | 180.7 | 109.5 | 330 | 311.3 | 119.4 | 251.7 | 313.1 | 166.3
687 | 513 | 565.4 | 226.16 | 264.368 | 316 | 289.5 | 307 | 286.3 | 534.5 | 37.5 | 20.3 | 70.8 | 4.6 | 208.2 | 6.9 | 873 | 818.2 | 844 | 866.5 | 874.7 | 757.3 | 771.2 | 818.5 | 706.7 | 789.9 | 49.4 | 123.1 | 181 | 109.8 | 329.9 | 311.6 | 119.7 | 252.1 | 313.8 | 166.7
688 | 514 | 565.6 | 226.24 | 264.4615 | 316.6 | 290.3 | 306.4 | 285.7 | 538.8 | 37.6 | 20.3 | 71 | 4.4 | 207.8 | 6.7 | 873.6 | 817.3 | 845.5 | 867.1 | 874.9 | 757.7 | 773 | 819.4 | 707.2 | 790.2 | 49.6 | 123.3 | 181.4 | 110.2 | 330 | 311.6 | 120 | 252.4 | 314.5 | 167
689 | 515 | 565.8 | 226.32 | 264.555 | 318.1 | 291.1 | 305.8 | 284.4 | 553.2 | 37.7 | 20.3 | 71.1 | 4.3 | 204.2 | 6.8 | 873.8 | 817.2 | 846.4 | 867.9 | 874.6 | 757.9 | 771.2 | 820.2 | 707.8 | 790.4 | 49.7 | 123.5 | 181.8 | 110.5 | 330.1 | 311.8 | 120.2 | 252.6 | 315.1 | 167.4
690 | 516 | 565.4 | 226.16 | 264.368 | 318.9 | 291.5 | 304.9 | 283.6 | 551.5 | 37.7 | 20.3 | 71.2 | 5.2 | 202.3 | 7.1 | 874.2 | 817.2 | 846.4 | 868.8 | 875.6 | 758.2 | 776 | 820.7 | 708.2 | 791.9 | 49.9 | 123.7 | 182 | 110.9 | 330.4 | 312.6 | 120.5 | 253 | 315.8 | 167.7
691 | 517 | 565.1 | 226.04 | 264.2277 | 319.5 | 291.8 | 305 | 283.8 | 534.8 | 37.8 | 20.3 | 71.5 | 4.9 | 203.7 | 7.5 | 874.8 | 817.6 | 845.5 | 870 | 877.2 | 758.4 | 771.2 | 823.3 | 708.6 | 792.3 | 50.1 | 124 | 182.3 | 111.3 | 329.9 | 312.7 | 120.8 | 253.3 | 316.5 | 168
692 | 518 | 565.2 | 226.08 | 264.2745 | 319.6 | 292.5 | 305.2 | 284.5 | 527.9 | 37.9 | 20.3 | 71.7 | 4.6 | 209.8 | 7.5 | 875.7 | 818.4 | 845 | 871.7 | 878.4 | 758.7 | 772.1 | 822.8 | 708.8 | 792 | 50.2 | 124.2 | 182.7 | 111.6 | 329.6 | 312.8 | 121 | 253.7 | 317.2 | 168.4
693 | 519 | 565.5 | 226.2 | 264.4148 | 318.3 | 292.7 | 306 | 284.2 | 521.5 | 38 | 20.3 | 71.9 | 4.5 | 211.4 | 7.3 | 876.5 | 819.9 | 844.4 | 873 | 879.1 | 759 | 777.2 | 822.4 | 709.2 | 792.7 | 50.4 | 124.5 | 183 | 112 | 330 | 313 | 121.3 | 254 | 317.7 | 168.7
694 | 520 | 566 | 226.4 | 264.6486 | 317.7 | 293.1 | 306.7 | 284.6 | 518.3 | 38.1 | 20.3 | 72.1 | 4.2 | 227.9 | 6.6 | 877.4 | 820.4 | 845.8 | 873.8 | 879.4 | 759.4 | 780.9 | 822.5 | 709.5 | 793 | 50.6 | 124.8 | 183.4 | 112.4 | 330.2 | 313 | 121.6 | 254.3 | 318.4 | 169.1
695 | 521 | 566.4 | 226.56 | 264.8356 | 318.3 | 293.7 | 306.6 | 285.5 | 512.9 | 38.2 | 20.3 | 72.4 | 4.4 | 220.5 | 6 | 878.1 | 821.5 | 846 | 873.8 | 876.8 | 759.7 | 785.9 | 821.9 | 709.8 | 792.4 | 50.7 | 125 | 183.6 | 112.7 | 330.7 | 313.5 | 121.9 | 254.7 | 319.2 | 169.4
696 | 522 | 566.1 | 226.44 | 264.6953 | 317.6 | 294 | 306.7 | 284.7 | 508.1 | 38.2 | 20.3 | 72.7 | 4.6 | 210.8 | 5.5 | 879 | 822.6 | 846.1 | 874.7 | 876.7 | 759.9 | 789.5 | 822.4 | 710.3 | 793.2 | 50.9 | 125.3 | 183.9 | 113.1 | 331 | 314.4 | 122.1 | 255.2 | 320 | 169.8
697 | 523 | 565.4 | 226.16 | 264.368 | 318.5 | 293.6 | 306.8 | 284.6 | 504.7 | 38.2 | 20.3 | 73 | 4.5 | 228.4 | 4.4 | 879.4 | 822.7 | 845.2 | 875.1 | 877.8 | 759.9 | 787 | 821.3 | 710.5 | 794.1 | 51.1 | 125.5 | 184.2 | 113.5 | 330.6 | 314.8 | 122.4 | 255.5 | 320.6 | 170.1
698 | 524 | 565.9 | 226.36 | 264.6018 | 318.9 | 294.1 | 306.8 | 284.3 | 505.1 | 38.3 | 20.3 | 73.2 | 4.7 | 233.8 | 3.9 | 879.8 | 821.6 | 843 | 875.2 | 878.4 | 759.9 | 784.8 | 821.1 | 711 | 795.1 | 51.3 | 125.7 | 184.7 | 113.8 | 330.6 | 314.6 | 122.7 | 255.8 | 321.1 | 170.5
699 | 525 | 565 | 226 | 264.181 | 319.8 | 293.9 | 306.4 | 283.6 | 508.6 | 38.3 | 20.3 | 73.2 | 4.3 | 214.9 | 3.9 | 880.5 | 822.5 | 841 | 876 | 878.8 | 760 | 779.2 | 817.9 | 711.4 | 795.7 | 51.4 | 126 | 185.1 | 114.2 | 330.5 | 314.8 | 123 | 256.1 | 321.8 | 170.8
700 | 526 | 567.9 | 227.16 | 265.537 | 319.3 | 294.2 | 305.8 | 283 | 509.5 | 38.4 | 20.3 | 73.2 | 4.5 | 225 | 4.1 | 881.4 | 823.4 | 840.4 | 877.1 | 880.1 | 760.3 | 777.6 | 818.7 | 711.8 | 796.4 | 51.6 | 126.2 | 185.4 | 114.6 | 330.8 | 314.7 | 123.3 | 256.4 | 322.4 | 171.2
701 | 527 | 567.1 | 226.84 | 265.1629 | 319.1 | 294.6 | 305.8 | 282.4 | 505.3 | 38.5 | 20.3 | 73.2 | 5 | 210.7 | 5.1 | 882.1 | 823.5 | 838.8 | 877.8 | 880.4 | 760.6 | 771.3 | 817 | 712.1 | 796.8 | 51.8 | 126.4 | 185.7 | 115 | 331.1 | 314.9 | 123.6 | 256.8 | 323 | 171.5
702 | 528 | 567.2 | 226.88 | 265.2096 | 319.7 | 294.6 | 304 | 282.6 | 507.9 | 38.6 | 20.3 | 73.3 | 4.8 | 212.4 | 6.3 | 882.2 | 822.1 | 838.9 | 877 | 880.3 | 760.9 | 770.8 | 814.9 | 712.5 | 796.4 | 51.9 | 126.6 | 185.9 | 115.3 | 331.8 | 315.6 | 123.9 | 257.3 | 323.6 | 171.8
703 | 529 | 567.7 | 227.08 | 265.4434 | 321.9 | 294.5 | 304.5 | 283.7 | 505.3 | 38.6 | 20.3 | 73.4 | 4.9 | 209.9 | 6.9 | 882.1 | 820.6 | 840 | 876.1 | 881.9 | 760.9 | 770.8 | 814.5 | 712.9 | 795.6 | 52.1 | 126.8 | 186.2 | 115.7 | 332.8 | 315.6 | 124.2 | 257.7 | 324.2 | 172.2
704 | 530 | 567.9 | 227.16 | 265.537 | 322.3 | 294.9 | 305.5 | 284.9 | 512.1 | 38.7 | 20.3 | 73.5 | 4.7 | 208.6 | 7.4 | 882.1 | 819.9 | 841.5 | 875.6 | 882.5 | 760.8 | 764.4 | 810.5 | 713.2 | 794.9 | 52.3 | 127 | 186.4 | 116.1 | 333.3 | 315.6 | 124.4 | 258 | 324.7 | 172.6
705 | 531 | 568.3 | 227.32 | 265.724 | 321 | 295.6 | 306.5 | 285.6 | 519.3 | 38.8 | 20.3 | 73.7 | 5.1 | 225.9 | 7.4 | 882.2 | 817.8 | 843.7 | 875.3 | 882.8 | 760.8 | 762.8 | 810.6 | 713.6 | 794.7 | 52.4 | 127.2 | 186.8 | 116.5 | 333.2 | 315.6 | 124.7 | 258.3 | 325.2 | 172.9
706 | 532 | 566.1 | 226.44 | 264.6953 | 320.5 | 295.7 | 306.9 | 284.7 | 522 | 38.8 | 20.3 | 73.9 | 5.2 | 202.1 | 7.9 | 882.2 | 816.8 | 845.7 | 875.4 | 882.6 | 760.6 | 765.3 | 813 | 714.2 | 795.7 | 52.6 | 127.4 | 187.2 | 116.9 | 333.2 | 315.6 | 125 | 258.6 | 325.8 | 173.3
707 | 533 | 565.6 | 226.24 | 264.4615 | 320.7 | 295.1 | 306.7 | 284.3 | 522.9 | 38.8 | 20.3 | 74 | 6.1 | 217.2 | 8.2 | 882.1 | 815.9 | 845.1 | 875.1 | 883.1 | 760.5 | 766.9 | 812.3 | 714.8 | 796.3 | 52.8 | 127.7 | 187.5 | 117.3 | 333.4 | 315.7 | 125.3 | 258.9 | 326.4 | 173.6
708 | 534 | 565.7 | 226.28 | 264.5083 | 320 | 294.9 | 306.6 | 284 | 529.3 | 38.8 | 20.3 | 74.1 | 5.1 | 222.8 | 7.8 | 881.7 | 816.5 | 843.9 | 874.7 | 882.5 | 760.5 | 761.5 | 809.5 | 715.2 | 796.6 | 53 | 127.9 | 187.8 | 117.6 | 333.5 | 315.8 | 125.6 | 259.3 | 326.9 | 174
709 | 535 | 565 | 226 | 264.181 | 320.8 | 295 | 307.1 | 283.9 | 529.5 | 38.8 | 20.3 | 74.2 | 4.5 | 224.7 | 7.1 | 881.8 | 815.7 | 844.6 | 874.5 | 883.5 | 760.5 | 762 | 808.1 | 715.6 | 797.4 | 53.2 | 128.2 | 188.1 | 118 | 333.1 | 316.2 | 125.9 | 259.7 | 327.3 | 174.4
710 | 536 | 565.7 | 226.28 | 264.5083 | 322.6 | 295.3 | 307.6 | 284.7 | 520.3 | 38.8 | 20.3 | 74.2 | 4.2 | 218.2 | 6.8 | 881.8 | 814.7 | 845.8 | 874.1 | 883.2 | 760.6 | 766.4 | 809.1 | 715.9 | 797.6 | 53.3 | 128.4 | 188.4 | 118.4 | 333.4 | 316.4 | 126.2 | 259.9 | 327.8 | 174.7
711 | 537 | 566.5 | 226.6 | 264.8823 | 322.7 | 296.4 | 307.6 | 284.9 | 513.8 | 38.7 | 20.3 | 74.2 | 4.4 | 207.3 | 7.3 | 881.8 | 815.2 | 844.8 | 873.6 | 882.8 | 760.8 | 772.9 | 812.6 | 716.4 | 798.2 | 53.5 | 128.7 | 188.9 | 118.8 | 334.3 | 317 | 126.4 | 260.2 | 328.1 | 175.1
712 | 538 | 566.2 | 226.48 | 264.7421 | 323.9 | 296.1 | 308.2 | 285.3 | 504.9 | 38.7 | 20.2 | 74.2 | 5.1 | 208.1 | 7.7 | 882.5 | 815.8 | 844.7 | 874.3 | 880.1 | 761.1 | 777.4 | 814.8 | 717 | 798.7 | 53.7 | 128.9 | 189.1 | 119.2 | 335.1 | 318 | 126.7 | 260.6 | 328.4 | 175.4
713 | 539 | 565.6 | 226.24 | 264.4615 | 325.7 | 295.4 | 309.4 | 285.9 | 497 | 38.7 | 20.2 | 74.4 | 5.3 | 212 | 8 | 883.1 | 815.6 | 846.9 | 874.7 | 878.8 | 761.2 | 778.9 | 814.1 | 717.5 | 797.8 | 53.9 | 129.1 | 189.5 | 119.6 | 336 | 318.2 | 127 | 261 | 328.9 | 175.8
714 | 540 | 567 | 226.8 | 265.1161 | 325.8 | 295.5 | 310.2 | 285.9 | 494.4 | 38.8 | 20.2 | 74.5 | 4.9 | 212.5 | 8 | 882.6 | 815 | 848.1 | 874 | 876.6 | 761.2 | 780.8 | 814.1 | 717.9 | 796.5 | 54 | 129.4 | 189.6 | 120 | 336.4 | 318.8 | 127.3 | 261.4 | 329.5 | 176.2
715 | 541 | 566 | 226.4 | 264.6486 | 324.2 | 294.2 | 310.6 | 285.8 | 494.7 | 38.8 | 20.2 | 74.6 | 4.8 | 215.3 | 7.9 | 882.1 | 815.3 | 848.3 | 873.4 | 875 | 761.3 | 775.7 | 810.8 | 718.3 | 794.4 | 54.2 | 129.7 | 189.9 | 120.4 | 336.4 | 319.2 | 127.6 | 261.7 | 330 | 176.6
716 | 542 | 566.7 | 226.68 | 264.9759 | 322.9 | 294 | 310.8 | 285.2 | 507.5 | 38.9 | 20.2 | 74.7 | 4.9 | 200.4 | 7.1 | 881.7 | 814.9 | 849.2 | 873.5 | 877.3 | 761.3 | 768.4 | 811.2 | 718.8 | 794.8 | 54.4 | 129.9 | 190.3 | 120.7 | 337.1 | 319.5 | 127.9 | 262 | 330.6 | 177
717 | 543 | 567.7 | 227.08 | 265.4434 | 324.3 | 294.3 | 310.5 | 284.9 | 511.8 | 38.9 | 20.2 | 74.9 | 4.5 | 208.4 | 7 | 881.7 | 814.3 | 851.4 | 873.5 | 875.3 | 761.4 | 767.1 | 809.9 | 719.4 | 794.5 | 54.6 | 130.2 | 190.6 | 121.1 | 336.7 | 319.5 | 128.2 | 262.2 | 331.1 | 177.3
718 | 544 | 566.9 | 226.76 | 265.0694 | 323.9 | 294 | 309.4 | 285.1 | 513.1 | 39 | 20.2 | 75 | 5.1 | 204 | 7.1 | 881.8 | 814.5 | 851.8 | 873.8 | 875.6 | 761.4 | 764.9 | 810.8 | 720 | 794.8 | 54.8 | 130.4 | 190.8 | 121.5 | 335.9 | 319.2 | 128.5 | 262.5 | 331.7 | 177.7
719 | 545 | 566.8 | 226.72 | 265.0226 | 323.5 | 294.4 | 308.1 | 285.5 | 520.5 | 39 | 20.2 | 75 | 5.3 | 200.5 | 7.6 | 881.7 | 814.1 | 852.9 | 873.6 | 876 | 761.7 | 764.1 | 812.8 | 720.8 | 795 | 55 | 130.7 | 191.2 | 121.9 | 335.2 | 319 | 128.7 | 262.7 | 332.3 | 178
720 | 546 | 567.5 | 227 | 265.3499 | 322.8 | 294.5 | 308.1 | 285.3 | 516.7 | 39.1 | 20.2 | 75.1 | 5.3 | 201.9 | 7.8 | 882.1 | 814.1 | 854 | 874 | 873.9 | 761.9 | 770.3 | 815.3 | 721.7 | 794.9 | 55.1 | 130.9 | 191.5 | 122.3 | 335.4 | 319.5 | 129 | 262.9 | 332.9 | 178.4
721 | 547 | 566.4 | 226.56 | 264.8356 | 321.3 | 295.3 | 307.5 | 284.1 | 505.3 | 39.2 | 20.2 | 75.2 | 5.7 | 200.8 | 8 | 882.5 | 814.6 | 856.1 | 875 | 872.4 | 762.2 | 774.1 | 817.6 | 722.5 | 793 | 55.3 | 131.2 | 191.8 | 122.7 | 335.5 | 319.3 | 129.3 | 263.2 | 333.5 | 178.7
722 | 548 | 566.5 | 226.6 | 264.8823 | 320.1 | 296.6 | 307.1 | 284.2 | 510.4 | 39.3 | 20.2 | 75.2 | 5.7 | 202.4 | 7.9 | 882.7 | 814.4 | 856 | 875.4 | 872.2 | 762.4 | 776.9 | 817.2 | 723.3 | 793.4 | 55.5 | 131.5 | 192.1 | 123.1 | 335.2 | 319.1 | 129.6 | 263.4 | 334.1 | 179.1
723 | 549 | 565.6 | 226.24 | 264.4615 | 320.6 | 297.7 | 306.4 | 284.6 | 518 | 39.4 | 20.2 | 75.1 | 5.5 | 203.1 | 7.9 | 883.4 | 814.8 | 856.6 | 876.1 | 872.6 | 762.5 | 771.8 | 814.1 | 724 | 793.4 | 55.7 | 131.7 | 192.3 | 123.5 | 335.1 | 318.6 | 129.9 | 263.6 | 334.7 | 179.4
724 | 550 | 566.4 | 226.56 | 264.8356 | 320.7 | 298.1 | 306.3 | 284.3 | 531.6 | 39.4 | 20.2 | 75.2 | 5.5 | 206.9 | 7.9 | 883.2 | 813.2 | 856.3 | 875.7 | 872.7 | 762.6 | 766.2 | 810.5 | 724.7 | 793.2 | 55.9 | 132 | 192.7 | 123.9 | 335.7 | 318.1 | 130.2 | 263.8 | 335.2 | 179.8
725 | 551 | 569.1 | 227.64 | 266.098 | 320.7 | 298.3 | 306 | 283.8 | 536.6 | 39.6 | 20.2 | 75.3 | 4.8 | 211.4 | 7.9 | 883.1 | 812.7 | 856.1 | 875.5 | 873.1 | 762.6 | 769.6 | 812.8 | 725.5 | 793 | 56 | 132.3 | 193 | 124.3 | 336.1 | 317.9 | 130.5 | 264.1 | 335.7 | 180.1
726 | 552 | 567.5 | 227 | 265.3499 | 320.5 | 297.9 | 305.1 | 283.2 | 525 | 39.6 | 20.2 | 75.5 | 5.8 | 209.9 | 7.9 | 882.9 | 811.7 | 855.9 | 875.1 | 871.7 | 762.7 | 776.4 | 814.7 | 726.2 | 792.2 | 56.2 | 132.5 | 193.2 | 124.7 | 336.5 | 318.1 | 130.8 | 264.3 | 336.3 | 180.5
727 | 553 | 568.2 | 227.28 | 265.6772 | 319.1 | 298.2 | 305 | 283.9 | 524.4 | 39.7 | 20.2 | 75.5 | 6.2 | 204.3 | 7.7 | 883.2 | 811.5 | 855.8 | 874.9 | 872.8 | 762.8 | 776.8 | 814.9 | 727 | 793.1 | 56.4 | 132.8 | 193.6 | 125.1 | 336 | 317.7 | 131.1 | 264.6 | 336.9 | 180.9
728 | 554 | 568.2 | 227.28 | 265.6772 | 320 | 298.9 | 303.9 | 284.3 | 530 | 39.6 | 20.2 | 75.3 | 5.7 | 206.9 | 6.9 | 883.3 | 811.7 | 855.5 | 874.7 | 874.1 | 763 | 773.4 | 815.6 | 727.7 | 794.4 | 56.6 | 133.1 | 193.9 | 125.5 | 335.9 | 317.5 | 131.4 | 264.8 | 337.6 | 181.2
729 | 555 | 566.6 | 226.64 | 264.9291 | 320.8 | 299.4 | 303.7 | 284.7 | 532.8 | 39.5 | 20.2 | 75.4 | 5.5 | 206.8 | 6.5 | 883.4 | 812.8 | 856.1 | 875.3 | 873.3 | 763.3 | 771.8 | 816 | 728.5 | 795 | 56.8 | 133.3 | 194.2 | 125.9 | 335.7 | 317.4 | 131.7 | 265 | 338.1 | 181.5
730 | 556 | 566.3 | 226.52 | 264.7888 | 321.1 | 299.8 | 304.3 | 285.1 | 532.3 | 39.4 | 20.2 | 75.5 | 5.6 | 210 | 6.3 | 883.4 | 812.4 | 855.2 | 875.5 | 874 | 763.6 | 771.4 | 815.1 | 729.2 | 794 | 57 | 133.6 | 194.4 | 126.3 | 335.3 | 317.3 | 132 | 265.4 | 338.5 | 181.8
731 | 557 | 565.7 | 226.28 | 264.5083 | 320.3 | 299.8 | 304.3 | 285.7 | 528.1 | 39.4 | 20.2 | 75.4 | 5.1 | 207.3 | 6 | 883.4 | 812.6 | 854.8 | 874.9 | 875.9 | 763.8 | 773 | 816.6 | 730 | 794 | 57.1 | 133.9 | 194.8 | 126.7 | 334.7 | 317.3 | 132.3 | 265.7 | 339 | 182.2
732 | 558 | 566.2 | 226.48 | 264.7421 | 319.9 | 299.6 | 304.6 | 285.3 | 522 | 39.5 | 20.2 | 75.4 | 4.9 | 210.1 | 5.6 | 883.7 | 813.7 | 853.9 | 874.7 | 876.2 | 764.1 | 773.1 | 817.8 | 730.7 | 794.7 | 57.3 | 134.1 | 195.1 | 127.1 | 334.8 | 317.3 | 132.6 | 265.9 | 339.6 | 182.5
733 | 559 | 566.5 | 226.6 | 264.8823 | 319.9 | 299.7 | 305.3 | 284.6 | 514.3 | 39.5 | 20.2 | 75.5 | 4.9 | 213 | 5.6 | 884.4 | 814.7 | 852.7 | 874.9 | 876.8 | 764.4 | 773.3 | 817.1 | 731.2 | 794.4 | 57.5 | 134.4 | 195.3 | 127.5 | 334.9 | 317.2 | 132.9 | 266.2 | 340.1 | 182.8
734 | 560 | 566.4 | 226.56 | 264.8356 | 321.1 | 300.1 | 306.3 | 284.1 | 510.4 | 39.4 | 20.2 | 75.5 | 4.9 | 202.9 | 6.1 | 885.1 | 814.8 | 854.8 | 875.3 | 878.1 | 764.7 | 773.9 | 815.1 | 731.9 | 794.9 | 57.7 | 134.7 | 195.6 | 128 | 334.8 | 316.9 | 133.2 | 266.4 | 340.5 | 183.1
735 | 561 | 566.2 | 226.48 | 264.7421 | 322.3 | 300.5 | 307 | 284.4 | 508.4 | 39.4 | 20.2 | 75.4 | 5 | 227.2 | 5.9 | 885.2 | 812.9 | 856.6 | 875 | 877.1 | 764.9 | 775.9 | 814.9 | 732.5 | 795.1 | 57.9 | 134.9 | 195.8 | 128.4 | 335.1 | 317.5 | 133.5 | 266.7 | 341 | 183.5
736 | 562 | 566.7 | 226.68 | 264.9759 | 323.3 | 301 | 307 | 285.5 | 500.3 | 39.4 | 20.2 | 75.4 | 5.3 | 228.2 | 5.3 | 885.1 | 811 | 856.7 | 874.6 | 877.8 | 764.9 | 778 | 814.5 | 733.2 | 794.9 | 58.1 | 135.2 | 196 | 128.8 | 335.8 | 317.3 | 133.8 | 266.9 | 341.4 | 183.8
737 | 563 | 567 | 226.8 | 265.1161 | 323 | 301 | 307.3 | 286.2 | 501.3 | 39.4 | 20.2 | 75.6 | 5.2 | 202.7 | 4.9 | 885.4 | 810.6 | 857.3 | 874.8 | 879.3 | 765.4 | 779.6 | 813.6 | 734.1 | 795.5 | 58.3 | 135.4 | 196.4 | 129.2 | 335.9 | 317.6 | 134.2 | 267.2 | 342 | 184.2
738 | 564 | 566.2 | 226.48 | 264.7421 | 322.3 | 301.6 | 307.9 | 286.3 | 499 | 39.5 | 20.2 | 75.6 | 5.2 | 209.4 | 4.4 | 885.6 | 810.6 | 855.5 | 874.9 | 879.4 | 766 | 776.5 | 812.2 | 735.1 | 795.9 | 58.5 | 135.7 | 196.6 | 129.6 | 336 | 317.6 | 134.5 | 267.4 | 342.6 | 184.6
739 | 565 | 566.3 | 226.52 | 264.7888 | 322.1 | 302.2 | 308.2 | 286.9 | 495.5 | 39.6 | 20.2 | 75.6 | 5.2 | 238 | 3.7 | 886 | 811.5 | 853.9 | 875.4 | 880.8 | 766.3 | 769.1 | 809.8 | 736 | 796 | 58.6 | 136 | 196.8 | 130.1 | 335.8 | 317.4 | 134.8 | 267.6 | 343 | 184.9
740 | 566 | 566.2 | 226.48 | 264.7421 | 323.6 | 302.5 | 308 | 287.7 | 502.7 | 39.7 | 20.2 | 75.5 | 5.8 | 263 | 3.2 | 886.1 | 812.5 | 853.6 | 875.1 | 881.4 | 766.5 | 763.5 | 806.8 | 737 | 796.8 | 58.8 | 136.2 | 197.2 | 130.5 | 336.3 | 317.5 | 135.1 | 267.8 | 343.4 | 185.3
741 | 567 | 566.5 | 226.6 | 264.8823 | 324.7 | 303.1 | 308.4 | 286.5 | 500.1 | 39.8 | 20.2 | 75.5 | 5.6 | 263.2 | 2.8 | 886.2 | 813.6 | 851.2 | 874.7 | 881.3 | 766.8 | 753.4 | 800 | 737.9 | 797.4 | 59 | 136.5 | 197.4 | 130.9 | 336.8 | 317.3 | 135.4 | 268 | 343.9 | 185.6
742 | 568 | 567.1 | 226.84 | 265.1629 | 324.7 | 302.8 | 309.2 | 285.7 | 501.1 | 39.8 | 20.2 | 75.6 | 5.8 | 251.8 | 2.6 | 886.1 | 811.5 | 847.2 | 874 | 883.3 | 766.8 | 743.6 | 794.9 | 738.7 | 796.8 | 59.2 | 136.7 | 197.6 | 131.3 | 336.6 | 317.2 | 135.7 | 268.2 | 344.3 | 186
743 | 569 | 566.6 | 226.64 | 264.9291 | 325.4 | 301.5 | 309.1 | 284.9 | 504.2 | 39.8 | 20.2 | 75.6 | 5.1 | 231.2 | 2.4 | 886.1 | 810.8 | 845.5 | 873.5 | 883.7 | 766.7 | 737.7 | 791 | 739.3 | 797.1 | 59.4 | 137 | 198 | 131.7 | 336.6 | 317.2 | 136.1 | 268.4 | 344.8 | 186.3
744 | 570 | 565.5 | 226.2 | 264.4148 | 326.8 | 300 | 308.5 | 285.1 | 497.7 | 39.8 | 20.2 | 75.8 | 5.6 | 208.7 | 2.2 | 886.2 | 810.4 | 843.9 | 873.2 | 882.9 | 766.7 | 734.7 | 789.8 | 739.9 | 796.5 | 59.6 | 137.3 | 198.3 | 132.2 | 336.5 | 317.3 | 136.4 | 268.6 | 345.2 | 186.7
745 | 571 | 566.1 | 226.44 | 264.6953 | 327.5 | 299.1 | 308.3 | 285.3 | 501.8 | 39.8 | 20.1 | 76 | 5.4 | 188.7 | 2.1 | 885.8 | 808.7 | 843.4 | 872.1 | 883.6 | 766.6 | 730 | 788.6 | 740.5 | 796.1 | 59.7 | 137.5 | 198.7 | 132.6 | 336 | 316.8 | 136.7 | 268.8 | 345.6 | 187
746 | 572 | 566.4 | 226.56 | 264.8356 | 328.9 | 298.4 | 308.5 | 285.9 | 511.2 | 39.9 | 20.1 | 76 | 5.7 | 186.2 | 1.7 | 885.4 | 807.9 | 842.2 | 870.8 | 882.2 | 766.3 | 722.7 | 782.4 | 740.9 | 796.3 | 59.9 | 137.8 | 199.2 | 133 | 335.9 | 316.4 | 137.1 | 268.9 | 346.1 | 187.3
747 | 573 | 565.2 | 226.08 | 264.2745 | 329.9 | 297.5 | 309.5 | 286.6 | 516.6 | 39.9 | 20.1 | 76 | 5.2 | 214.7 | 1.7 | 884.7 | 805.9 | 841.9 | 869.4 | 882.3 | 766.4 | 707.8 | 770.5 | 741.1 | 793.8 | 60.1 | 138 | 199.6 | 133.4 | 335.5 | 316.3 | 137.4 | 269 | 346.5 | 187.6
748 | 574 | 565.2 | 226.08 | 264.2745 | 330.9 | 297 | 310.1 | 287 | 535.3 | 40 | 20.1 | 76 | 5.2 | 239.3 | 2 | 884.5 | 805.2 | 843 | 868.5 | 880.7 | 766.4 | 695.4 | 769.4 | 741.4 | 792.5 | 60.3 | 138.3 | 199.9 | 133.8 | 335.2 | 316.2 | 137.7 | 269.1 | 346.9 | 188
749 | 575 | 567.8 | 227.12 | 265.4902 | 332 | 296.4 | 310.7 | 288.2 | 548.1 | 40 | 20.1 | 75.9 | 5.5 | 238.7 | 2.5 | 884.1 | 804.8 | 844.2 | 868.4 | 881.8 | 766.4 | 683.4 | 762.2 | 741.7 | 791.4 | 60.5 | 138.6 | 200.3 | 134.2 | 335 | 316 | 138.1 | 269.3 | 347.4 | 188.3
750 | 576 | 566.6 | 226.64 | 264.9291 | 332 | 295.9 | 310.8 | 290.1 | 547.5 | 40 | 20.1 | 75.8 | 4.9 | 213.9 | 3.3 | 883.6 | 803.7 | 847.3 | 868.1 | 882.7 | 766.4 | 688 | 765.3 | 741.9 | 791.5 | 60.7 | 138.8 | 200.5 | 134.6 | 334.6 | 315.9 | 138.4 | 269.6 | 347.8 | 188.6
751 | 577 | 566.9 | 226.76 | 265.0694 | 332.7 | 295 | 310.8 | 291 | 545.9 | 40 | 20.1 | 75.6 | 4.8 | 232.6 | 3.5 | 883.1 | 803.2 | 846.5 | 867.5 | 883.5 | 766.3 | 690.4 | 771.2 | 742.3 | 791.8 | 60.9 | 139.1 | 200.7 | 135.1 | 334.3 | 315.8 | 138.7 | 269.7 | 348.2 | 188.9
752 | 578 | 565.8 | 226.32 | 264.555 | 333.6 | 295.2 | 310.9 | 291.4 | 546.2 | 40 | 20.1 | 75.5 | 5.3 | 233.4 | 3.2 | 883 | 804.7 | 846.3 | 867.3 | 883.2 | 766.2 | 692 | 775.1 | 742.7 | 793.9 | 61.1 | 139.4 | 201.2 | 135.5 | 334.3 | 315.6 | 139.1 | 269.9 | 348.7 | 189.2
753 | 579 | 566.5 | 226.6 | 264.8823 | 333.6 | 295.3 | 311.3 | 291 | 550.8 | 40 | 20.1 | 75.6 | 5.3 | 208.8 | 3 | 882.7 | 806.4 | 845.1 | 867 | 881.2 | 766.2 | 687.7 | 770.1 | 743.2 | 792.8 | 61.2 | 139.6 | 201.6 | 135.9 | 333.8 | 315.7 | 139.4 | 270.2 | 349.2 | 189.5
754 | 580 | 565.5 | 226.2 | 264.4148 | 334.6 | 294.7 | 311.8 | 291.4 | 566.1 | 40.2 | 20.1 | 75.7 | 5.2 | 214.5 | 3.1 | 882.7 | 805.9 | 844.9 | 866.4 | 878 | 766.4 | 678.4 | 761.9 | 743.8 | 790.3 | 61.4 | 139.9 | 202.3 | 136.3 | 333.9 | 315.8 | 139.8 | 270.4 | 349.7 | 189.8
755 | 581 | 565.4 | 226.16 | 264.368 | 335.6 | 295.4 | 312.3 | 292.3 | 582.2 | 40.3 | 20.1 | 75.8 | 5.2 | 235.9 | 2.8 | 882.4 | 804.2 | 846.7 | 865.5 | 876 | 766.6 | 672 | 761 | 744.3 | 790.2 | 61.6 | 140.1 | 202.6 | 136.8 | 333.8 | 315.5 | 140.1 | 270.6 | 350.2 | 190.2
756 | 582 | 565.2 | 226.08 | 264.2745 | 335.8 | 296.4 | 312.4 | 292.6 | 597 | 40.4 | 20.1 | 75.9 | 5.1 | 242.5 | 2.5 | 882.1 | 801.6 | 849.3 | 865.5 | 873.9 | 766.6 | 672.4 | 764.3 | 744.9 | 789.8 | 61.8 | 140.4 | 203 | 137.2 | 334.2 | 315.2 | 140.4 | 270.8 | 350.8 | 190.5
757 | 583 | 567.1 | 226.84 | 265.1629 | 335.2 | 296.4 | 312.4 | 294.5 | 604.6 | 40.5 | 20.1 | 76.1 | 5.2 | 228 | 2.2 | 881.6 | 800.7 | 851.5 | 865.3 | 873.4 | 766.6 | 674.1 | 767.1 | 745.4 | 787.9 | 62 | 140.7 | 203.3 | 137.6 | 334.4 | 315.1 | 140.8 | 271 | 351.3 | 190.9
758 | 584 | 565.6 | 226.24 | 264.4615 | 334.5 | 296.9 | 312.8 | 295.6 | 609.4 | 40.6 | 20.1 | 76.2 | 5.4 | 205.1 | 2.2 | 881.4 | 800.2 | 853.5 | 865.4 | 872.1 | 766.7 | 672.5 | 766.9 | 746 | 786.7 | 62.2 | 140.9 | 203.7 | 138 | 334.3 | 315.1 | 141.2 | 271.1 | 351.8 | 191.2
759 | 585 | 566.7 | 226.68 | 264.9759 | 334.8 | 297.9 | 312.7 | 296.5 | 604.2 | 40.6 | 20.1 | 76.3 | 5.1 | 201.5 | 2.9 | 882 | 803.3 | 854.4 | 866.5 | 873 | 766.8 | 675.1 | 769.2 | 746.4 | 787.5 | 62.4 | 141.1 | 204.1 | 138.4 | 334 | 315.4 | 141.5 | 271.4 | 352.3 | 191.5
760 | 586 | 565.5 | 226.2 | 264.4148 | 335.4 | 297.9 | 311.4 | 295.9 | 588.4 | 40.6 | 20.1 | 76.4 | 5 | 210.9 | 3.5 | 883 | 804.4 | 856.4 | 867.5 | 874.3 | 766.7 | 688.8 | 776.5 | 746.9 | 788.5 | 62.6 | 141.3 | 204.1 | 138.8 | 333.7 | 315.6 | 141.8 | 271.6 | 352.7 | 191.8
761 | 587 | 565.3 | 226.12 | 264.3213 | 334.6 | 297.4 | 309.5 | 294.8 | 570.1 | 40.5 | 20.1 | 76.5 | 5 | 227.6 | 3.7 | 883.1 | 803.4 | 857.1 | 867.4 | 876.7 | 766.7 | 703.4 | 780.4 | 747.5 | 789.1 | 62.7 | 141.5 | 204.4 | 139.3 | 333.6 | 316 | 142.2 | 271.9 | 353.1 | 192.1
762 | 588 | 564.9 | 225.96 | 264.1342 | 334.8 | 297.5 | 308.7 | 293.6 | 566.4 | 40.4 | 20.1 | 76.6 | 4.8 | 235.7 | 3.9 | 882.6 | 803.1 | 856 | 866.6 | 876.6 | 766.6 | 714.4 | 782.4 | 748.1 | 789.9 | 62.9 | 141.8 | 204.6 | 139.7 | 333.7 | 316.1 | 142.5 | 272.3 | 353.6 | 192.4
763 | 589 | 565.9 | 226.36 | 264.6018 | 335.2 | 298 | 309.2 | 293.4 | 569.7 | 40.4 | 20.1 | 76.7 | 5.4 | 227.9 | 4 | 882.8 | 802.9 | 855.7 | 866.3 | 876.9 | 766.6 | 723.1 | 783.7 | 748.6 | 790.8 | 63.1 | 142 | 205.1 | 140.2 | 334.1 | 316.2 | 142.8 | 272.4 | 354 | 192.7
764 | 590 | 567.1 | 226.84 | 265.1629 | 335.7 | 298.2 | 310.2 | 293.8 | 564.2 | 40.5 | 20.1 | 76.9 | 5.7 | 215.8 | 3.9 | 883 | 803.7 | 853.4 | 866.2 | 877.3 | 766.8 | 728.4 | 787.4 | 749 | 791.8 | 63.3 | 142.3 | 205.3 | 140.6 | 334.6 | 316.7 | 143.2 | 272.7 | 354.5 | 193.1
765 | 591 | 566.3 | 226.52 | 264.7888 | 336.2 | 298 | 310.4 | 293.6 | 547.6 | 40.5 | 20.1 | 77 | 5.7 | 213.1 | 3.9 | 882.9 | 805 | 849.3 | 865.4 | 877.5 | 767 | 732 | 786.1 | 749.3 | 792.4 | 63.5 | 142.5 | 205.6 | 141 | 334.6 | 317.2 | 143.5 | 272.9 | 354.9 | 193.4
766 | 592 | 565.6 | 226.24 | 264.4615 | 336.7 | 297.9 | 310.8 | 293 | 545.6 | 40.6 | 20.1 | 77.1 | 5.4 | 208.1 | 3.9 | 882.5 | 804.2 | 850.2 | 864.9 | 877.9 | 767 | 732.5 | 786.8 | 749.7 | 792 | 63.7 | 142.8 | 206 | 141.4 | 334.8 | 317.5 | 143.9 | 273.1 | 355.2 | 193.7
767 | 593 | 567.4 | 226.96 | 265.3032 | 336.7 | 298.1 | 311.9 | 293 | 545.6 | 40.7 | 20.1 | 77.2 | 6 | 210.6 | 4 | 881.9 | 804.5 | 851.1 | 864.6 | 880.2 | 767 | 739.6 | 789.7 | 750.3 | 792.9 | 63.9 | 143 | 206.2 | 141.9 | 335 | 317.9 | 144.2 | 273.5 | 355.6 | 194
768 | 594 | 567.7 | 227.08 | 265.4434 | 334.6 | 298.6 | 312.5 | 292.9 | 538.2 | 40.7 | 20.1 | 77.3 | 5.4 | 228.4 | 4.2 | 881.3 | 805.4 | 850.8 | 863.7 | 881.9 | 767.3 | 736.4 | 784.9 | 750.7 | 791.6 | 64 | 143.2 | 206.3 | 142.3 | 335.5 | 318.3 | 144.6 | 273.7 | 356.1 | 194.3
769 | 595 | 567.2 | 226.88 | 265.2096 | 334.8 | 299.3 | 311.9 | 293.2 | 528.7 | 40.8 | 20.1 | 77.3 | 5.9 | 244.2 | 3.9 | 880.7 | 805.2 | 851.8 | 863.2 | 881.7 | 767.3 | 739.3 | 787.8 | 751 | 791.4 | 64.2 | 143.5 | 206.4 | 142.7 | 335.8 | 318.4 | 144.9 | 273.9 | 356.5 | 194.7
770 | 596 | 566.3 | 226.52 | 264.7888 | 336 | 299.3 | 311.3 | 292.7 | 525.1 | 40.8 | 20.1 | 77.4 | 6 | 248.8 | 3.7 | 880.2 | 805.4 | 852.8 | 862.8 | 881.7 | 767.2 | 743.9 | 788.5 | 751.3 | 791 | 64.4 | 143.7 | 206.8 | 143.2 | 335.9 | 318.5 | 145.3 | 274.2 | 356.9 | 195
771 | 597 | 563.9 | 225.56 | 263.6666 | 335.2 | 299.1 | 310.9 | 292 | 542.2 | 40.8 | 20.1 | 77.6 | 5.2 | 247.2 | 3.6 | 880 | 804.9 | 852.4 | 862.5 | 879.9 | 767.5 | 733.2 | 783.6 | 751.8 | 788.8 | 64.6 | 144 | 207.4 | 143.6 | 336.4 | 318.6 | 145.6 | 274.3 | 357.4 | 195.3
772 | 598 | 565.9 | 226.36 | 264.6018 | 334.7 | 299 | 310.6 | 292.5 | 568.1 | 40.9 | 20.1 | 77.7 | 4.8 | 238.4 | 3.6 | 879.9 | 805.6 | 849.5 | 861.8 | 877.4 | 767.7 | 719.1 | 777.9 | 752.3 | 787.7 | 64.8 | 144.2 | 208.1 | 144 | 336.7 | 319 | 145.9 | 274.5 | 357.9 | 195.6
773 | 599 | 565.3 | 226.12 | 264.3213 | 335.6 | 298.3 | 311.5 | 293.1 | 584 | 41 | 20.1 | 77.8 | 5.6 | 224.2 | 3.6 | 879.7 | 805.5 | 846.6 | 860.8 | 875.2 | 767.9 | 704.9 | 768.1 | 752.8 | 786.4 | 64.9 | 144.5 | 208.6 | 144.5 | 337 | 319 | 146.3 | 274.6 | 358.4 | 196
774 | 600 | 568.1 | 227.24 | 265.6305 | 336.6 | 298.6 | 312.1 | 294.5 | 588.8 | 41.1 | 20.1 | 77.9 | 5.2 | 230.5 | 3.9 | 879.3 | 803.5 | 844.7 | 859.7 | 873.8 | 768.2 | 692.3 | 757.3 | 753.2 | 784 | 65.1 | 144.7 | 209 | 144.9 | 336.8 | 319 | 146.7 | 274.8 | 358.9 | 196.3
775 | 601 | 567.4 | 226.96 | 265.3032 | 339.5 | 297.9 | 313.3 | 295.3 | 597.4 | 41.1 | 20.1 | 77.9 | 4.8 | 251.3 | 4.2 | 879.2 | 801.8 | 844.8 | 858.9 | 872.4 | 768.4 | 686.1 | 755.6 | 753.7 | 782.6 | 65.3 | 145 | 209.4 | 145.4 | 337 | 319.1 | 147 | 275 | 359.4 | 196.6
776 | 602 | 565.5 | 226.2 | 264.4148 | 341.2 | 297.3 | 314.2 | 296.4 | 608.8 | 41.1 | 20.1 | 78 | 5.5 | 254.5 | 4.1 | 879 | 801.8 | 847.4 | 859.1 | 871.4 | 768.3 | 685.3 | 760.9 | 754.3 | 782.5 | 65.5 | 145.2 | 209.9 | 145.8 | 336.8 | 318.8 | 147.4 | 275.1 | 359.9 | 197
777 | 603 | 565.6 | 226.24 | 264.4615 | 342.3 | 296.7 | 315.3 | 297.5 | 619.2 | 41.1 | 20.1 | 78.1 | 6.1 | 255.6 | 3.9 | 878.8 | 802.2 | 845 | 859.1 | 869.1 | 768.2 | 688.1 | 759.5 | 754.8 | 782 | 65.7 | 145.4 | 210.9 | 146.3 | 336.7 | 318.9 | 147.8 | 275.3 | 360.4 | 197.3
778 | 604 | 566.4 | 226.56 | 264.8356 | 342.9 | 296.3 | 316.8 | 298.7 | 641.5 | 41.1 | 20.1 | 78.2 | 6.1 | 255.4 | 3.5 | 878.4 | 799 | 842.6 | 858.8 | 864.2 | 768.5 | 680.5 | 750.9 | 755.4 | 778.9 | 65.8 | 145.6 | 211.5 | 146.8 | 337.1 | 319.2 | 148.1 | 275.5 | 361 | 197.6
779 | 605 | 566.9 | 226.76 | 265.0694 | 343.5 | 296.6 | 317.4 | 299.7 | 649.8 | 41 | 20.1 | 78.3 | 5.9 | 245.9 | 3.4 | 878.5 | 793.3 | 837.2 | 858.6 | 857.8 | 768.8 | 672.9 | 740.1 | 756 | 776.4 | 66 | 145.9 | 212 | 147.2 | 337.6 | 319.4 | 148.5 | 275.7 | 361.6 | 197.9
780 | 606 | 566.3 | 226.52 | 264.7888 | 343.4 | 297.6 | 316 | 300.4 | 649.2 | 41 | 20.1 | 78.3 | 5.3 | 245.3 | 3.6 | 878.8 | 788.7 | 834.4 | 858.4 | 852.4 | 769.3 | 665.9 | 730.4 | 756.4 | 773 | 66.2 | 146.1 | 212.5 | 147.7 | 338.1 | 319.7 | 148.9 | 276 | 362.1 | 198.3
781 | 607 | 566.1 | 226.44 | 264.6953 | 344.2 | 299.6 | 317 | 301.8 | 655.7 | 41.1 | 20.1 | 78.3 | 4.9 | 243.8 | 3.5 | 879.1 | 786 | 832.5 | 858.1 | 848.5 | 769.4 | 656.6 | 727.8 | 757 | 771.5 | 66.4 | 146.3 | 212.9 | 148.2 | 338.8 | 320.3 | 149.3 | 276.3 | 362.7 | 198.6
782 | 608 | 565.9 | 226.36 | 264.6018 | 344.4 | 300.9 | 317.7 | 303.3 | 665.8 | 41.2 | 20.1 | 78.4 | 6 | 236.2 | 3.5 | 879.1 | 784.1 | 831.6 | 858.2 | 845.4 | 769.6 | 649.8 | 723.7 | 757.5 | 768.7 | 66.6 | 146.6 | 213.5 | 148.7 | 340 | 320.6 | 149.7 | 276.6 | 363.2 | 199
783 | 609 | 567.8 | 227.12 | 265.4902 | 344.6 | 300.9 | 317.4 | 304.3 | 670.6 | 41.2 | 20.1 | 78.4 | 6.2 | 222.8 | 3.5 | 879.2 | 780.4 | 830.7 | 858.6 | 843.4 | 770 | 641 | 718.2 | 758 | 767.6 | 66.8 | 146.8 | 214.1 | 149.2 | 341.5 | 321.1 | 150.1 | 276.8 | 363.8 | 199.4
784 | 610 | 568 | 227.2 | 265.5837 | 345.6 | 300.9 | 317.9 | 305.4 | 664.1 | 41.3 | 20 | 78.3 | 5.3 | 223.8 | 3.7 | 878.9 | 779.2 | 833.2 | 857.6 | 842.1 | 770.1 | 634.7 | 721.2 | 758.5 | 767.1 | 66.9 | 147.1 | 214.6 | 149.7 | 342.5 | 321.9 | 150.6 | 277.2 | 364.3 | 199.7
785 | 611 | 567.8 | 227.12 | 265.4902 | 346 | 301.2 | 320.2 | 307 | 658.2 | 41.3 | 20 | 78.2 | 5.1 | 211.7 | 3.9 | 878.3 | 780.6 | 835.5 | 857.1 | 842.3 | 769.9 | 634.1 | 728.7 | 759 | 767.4 | 67.1 | 147.3 | 214.7 | 150.2 | 343.1 | 322.5 | 151 | 277.5 | 364.8 | 200.1
786 | 612 | 566.7 | 226.68 | 264.9759 | 345.7 | 300.9 | 321.4 | 307.7 | 656 | 41.3 | 20 | 78.1 | 5.3 | 221 | 4 | 877.3 | 782.7 | 839.5 | 856.4 | 844.2 | 769.5 | 640.1 | 740 | 759.5 | 768 | 67.3 | 147.6 | 215 | 150.7 | 343.7 | 322.7 | 151.4 | 277.8 | 365.2 | 200.5
787 | 613 | 567.3 | 226.92 | 265.2564 | 346.3 | 299.9 | 322.1 | 307.9 | 655.1 | 41.3 | 20 | 78 | 5.3 | 224.7 | 3.7 | 876.2 | 785.2 | 839.1 | 855.8 | 846.8 | 769 | 646.6 | 746.8 | 759.8 | 769.8 | 67.5 | 147.8 | 215.3 | 151.2 | 344.1 | 323 | 152.5 | 278.1 | 365.7 | 200.9
788 | 614 | 567.5 | 227 | 265.3499 | 347.8 | 300.1 | 322.3 | 307.5 | 660.7 | 41.3 | 20 | 78 | 5.1 | 224.3 | 3.4 | 875.3 | 787.1 | 839.6 | 855.2 | 847.5 | 768.8 | 652.4 | 752.9 | 760.2 | 771 | 67.7 | 148.1 | 216 | 151.8 | 344.3 | 323.4 | 154.2 | 278.4 | 366.1 | 201.2
789 | 615 | 567.1 | 226.84 | 265.1629 | 348.7 | 300 | 321.6 | 305.9 | 666.3 | 41.3 | 20 | 78 | 5.2 | 218.8 | 3.7 | 874.3 | 787.8 | 836.5 | 854.2 | 849 | 768.6 | 658.6 | 755.6 | 760.6 | 770.7 | 67.9 | 148.3 | 216.4 | 152.3 | 344.8 | 323.8 | 156.5 | 278.7 | 366.6 | 201.5
790 | 616 | 567.2 | 226.88 | 265.2096 | 349.6 | 300.9 | 321.1 | 303.9 | 657.7 | 41.2 | 20 | 78 | 5.2 | 230.8 | 4 | 873.8 | 791.5 | 837.9 | 854 | 850.7 | 768.5 | 671 | 763.2 | 761.1 | 773 | 68 | 148.5 | 216.4 | 152.9 | 344.2 | 324.2 | 158.8 | 278.9 | 367.1 | 201.9
791 | 617 | 567.3 | 226.92 | 265.2564 | 349.4 | 302.2 | 320.8 | 303.8 | 648.2 | 41.2 | 20 | 77.9 | 4.9 | 259.8 | 3.7 | 874.1 | 795.5 | 841.4 | 854.9 | 852 | 768.3 | 685.1 | 773.4 | 761.4 | 774 | 68.2 | 148.8 | 216.8 | 153.5 | 343.6 | 324.3 | 161.1 | 279.2 | 367.6 | 202.2
792 | 618 | 567.5 | 227 | 265.3499 | 348.6 | 303.9 | 319.9 | 304.3 | 642 | 41.3 | 20 | 78 | 5.5 | 253.4 | 3.7 | 874.2 | 798.9 | 844.4 | 856 | 854.2 | 768.2 | 699.1 | 782.4 | 761.8 | 774.4 | 68.4 | 149 | 217.1 | 154.1 | 343.1 | 324.1 | 163.4 | 279.4 | 368.1 | 202.5
793 | 619 | 566.7 | 226.68 | 264.9759 | 348.2 | 305.8 | 318.5 | 304.2 | 644 | 41.4 | 20 | 77.9 | 5.9 | 238.7 | 3.8 | 874.3 | 799.3 | 844.3 | 856 | 851.9 | 768.2 | 696.2 | 775.2 | 762 | 771.9 | 68.6 | 149.3 | 217.9 | 154.7 | 342.6 | 323.8 | 165.5 | 279.6 | 368.6 | 202.8
794 | 620 | 566 | 226.4 | 264.6486 | 346 | 307.8 | 317.9 | 304 | 638 | 41.4 | 20 | 78 | 5.4 | 236.4 | 3.8 | 874.4 | 796.5 | 843.3 | 855.8 | 851.5 | 768.5 | 685.9 | 767 | 762.2 | 770.6 | 68.8 | 149.5 | 218.1 | 155.4 | 342.4 | 323.7 | 167.6 | 279.8 | 369.2 | 203.2
795 | 621 | 567.7 | 227.08 | 265.4434 | 344.4 | 309.6 | 318.1 | 302.8 | 620 | 41.4 | 20 | 78 | 5.6 | 231.6 | 3.8 | 874.1 | 796.7 | 842.7 | 855.2 | 854 | 768.6 | 680.9 | 766.2 | 762.4 | 771.7 | 68.9 | 149.8 | 218.2 | 156 | 342.2 | 323.5 | 169.3 | 280 | 369.6 | 203.4
796 | 622 | 567.2 | 226.88 | 265.2096 | 345.1 | 309.4 | 317.9 | 302.4 | 612.4 | 41.4 | 20 | 78.1 | 5.5 | 213.7 | 3.6 | 873.5 | 799 | 843.5 | 855.3 | 856.2 | 768.4 | 689.8 | 773.6 | 762.7 | 774.1 | 69.1 | 150 | 218.6 | 156.7 | 342 | 323.5 | 171 | 280.2 | 370 | 203.7
797 | 623 | 567.2 | 226.88 | 265.2096 | 346.9 | 308 | 316.8 | 302.8 | 615.3 | 41.4 | 20 | 78.2 | 5.5 | 225.9 | 3.2 | 873.2 | 799.7 | 843.4 | 855.1 | 859 | 768.2 | 690.8 | 774 | 763.1 | 775.3 | 69.3 | 150.3 | 219.1 | 157.4 | 341.7 | 323.3 | 172.5 | 280.4 | 370.4 | 204
798 | 624 | 566.8 | 226.72 | 265.0226 | 348.2 | 307.1 | 316.3 | 303.3 | 603.3 | 41.4 | 20 | 78.3 | 5.8 | 247.6 | 3.3 | 872.8 | 800.7 | 843.7 | 854.5 | 861.5 | 768 | 703.5 | 777.5 | 763.3 | 776.7 | 69.5 | 150.5 | 219.2 | 158.2 | 341.5 | 323.4 | 174.1 | 280.6 | 370.9 | 204.4
799 | 625 | 567.2 | 226.88 | 265.2096 | 348.5 | 305.8 | 317 | 302.9 | 582.2 | 41.5 | 20 | 78.4 | 5.6 | 240.2 | 3.4 | 872.1 | 801.9 | 843.2 | 853.7 | 864.1 | 767.7 | 714.3 | 781 | 763.4 | 777.7 | 69.7 | 150.8 | 219.4 | 158.9 | 341.2 | 323.7 | 175.3 | 280.8 | 371.2 | 204.6
800 | 626 | 567.9 | 227.16 | 265.537 | 350 | 305.2 | 317.2 | 302.6 | 580 | 41.6 | 20 | 78.5 | 5.3 | 228.3 | 3.7 | 871.6 | 802.3 | 842.4 | 853.6 | 865.7 | 767.5 | 717.9 | 787.6 | 763.6 | 779.6 | 69.9 | 151 | 219.9 | 159.6 | 341.1 | 323.8 | 176.4 | 281 | 371.7 | 205
801 | 627 | 567.9 | 227.16 | 265.537 | 351.2 | 303.7 | 316.7 | 301.7 | 585.6 | 41.7 | 20 | 78.6 | 5 | 192.5 | 4.1 | 870.5 | 800.8 | 840.8 | 852.5 | 865.5 | 767.3 | 722.3 | 791.7 | 763.8 | 781.5 | 70 | 151.3 | 220.1 | 160.4 | 340.7 | 323.7 | 177.7 | 281.2 | 372.1 | 205.3
802 | 628 | 566 | 226.4 | 264.6486 | 351.2 | 303.4 | 316 | 301.1 | 601 | 41.7 | 20 | 78.6 | 4.9 | 193.8 | 3.8 | 869.6 | 801.4 | 835.9 | 851.7 | 864.1 | 767.4 | 716.3 | 787.3 | 764.2 | 781.7 | 70.2 | 151.6 | 220.9 | 161.1 | 340.9 | 323.6 | 179.1 | 281.4 | 372.5 | 205.6
803 | 629 | 565.9 | 226.36 | 264.6018 | 349.5 | 304.5 | 315.5 | 300.2 | 623.3 | 41.8 | 20 | 78.7 | 5.6 | 209.4 | 3.4 | 869.4 | 794.5 | 831.2 | 850.9 | 859.5 | 767.9 | 699.8 | 770.2 | 764.4 | 777.6 | 70.4 | 151.8 | 221.6 | 161.9 | 341.3 | 323.5 | 180.5 | 281.5 | 373 | 205.9
804 | 630 | 566.3 | 226.52 | 264.7888 | 349.7 | 304.3 | 316.7 | 299.3 | 629.3 | 41.9 | 20 | 78.7 | 5.5 | 220.3 | 3.3 | 869.4 | 789.1 | 828.4 | 850.4 | 858.4 | 768.5 | 685.1 | 757.6 | 764.7 | 775.5 | 70.5 | 152.1 | 221.9 | 162.6 | 341.4 | 323.3 | 181.7 | 281.6 | 373.5 | 206.2
805 | 631 | 566 | 226.4 | 264.6486 | 350.4 | 304.1 | 317.8 | 300.4 | 620.6 | 41.8 | 20 | 78.5 | 5.5 | 228.8 | 3.3 | 868.6 | 791 | 828.2 | 849.9 | 861.2 | 768.7 | 686.8 | 764.3 | 764.9 | 775.5 | 70.7 | 152.3 | 222.1 | 163.4 | 341.4 | 323.3 | 182.9 | 281.8 | 373.9 | 206.6
806 | 632 | 566 | 226.4 | 264.6486 | 350.2 | 304.4 | 317.5 | 301.9 | 605.8 | 41.8 | 20 | 78.3 | 5.6 | 230.1 | 3.5 | 867.9 | 792.9 | 829 | 849.3 | 862.4 | 768.6 | 691.7 | 767.9 | 765.1 | 776.6 | 70.9 | 152.6 | 222.3 | 164.1 | 341.3 | 323.3 | 184.1 | 282.1 | 374.3 | 206.9
807 | 633 | 567.5 | 227 | 265.3499 | 350.6 | 304.3 | 317.5 | 302.4 | 590.8 | 41.9 | 20 | 78.2 | 5.5 | 230.4 | 4.1 | 867 | 794.5 | 827.1 | 849 | 864.5 | 768.6 | 692.1 | 769.1 | 765.3 | 776.4 | 71.1 | 152.9 | 222.4 | 164.9 | 341 | 323.4 | 185.2 | 282.3 | 374.7 | 207.1
808 | 634 | 567.9 | 227.16 | 265.537 | 351.7 | 304.2 | 317.4 | 301.8 | 581.4 | 41.9 | 20 | 78.3 | 5.4 | 236.6 | 4.1 | 866.4 | 796.1 | 827.2 | 848.9 | 866.5 | 768.4 | 692.1 | 769.4 | 765.5 | 777.2 | 71.2 | 153.1 | 222.8 | 165.6 | 340.7 | 323.6 | 186.2 | 282.4 | 375.1 | 207.5
809 | 635 | 566.3 | 226.52 | 264.7888 | 353 | 304.7 | 316.4 | 301.2 | 588.9 | 41.9 | 20 | 78.4 | 5.8 | 243.2 | 4 | 866.1 | 798.1 | 829.5 | 849 | 868.1 | 768.2 | 696.1 | 773.5 | 765.8 | 778.3 | 71.4 | 153.4 | 223.2 | 166.4 | 340.5 | 323.6 | 187 | 282.6 | 375.5 | 207.7
810 | 636 | 565.5 | 226.2 | 264.4148 | 353.1 | 304.9 | 316.6 | 301.3 | 592.7 | 42 | 20 | 78.6 | 5.3 | 250.9 | 3.8 | 865.7 | 799.4 | 832.4 | 848.8 | 869.6 | 767.8 | 705.2 | 778.1 | 765.9 | 779.1 | 71.5 | 153.6 | 223.4 | 167.1 | 340.5 | 323.8 | 187.8 | 282.8 | 375.9 | 208
811 | 637 | 566.4 | 226.56 | 264.8356 | 352.9 | 304.4 | 317.3 | 301.7 | 591.3 | 42 | 20 | 78.9 | 5.4 | 245.6 | 3.8 | 865.6 | 802.7 | 834.6 | 849.4 | 870.1 | 767.5 | 709.8 | 783.2 | 765.9 | 779.8 | 71.7 | 153.9 | 223.8 | 167.9 | 341.1 | 323.6 | 188.8 | 283 | 376.4 | 208.4
812 | 638 | 566.7 | 226.68 | 264.9759 | 354.2 | 303 | 317.2 | 301.7 | 594.4 | 42 | 20 | 79.3 | 5.4 | 229.7 | 4 | 865.5 | 803.2 | 834.6 | 849.4 | 870.7 | 767.2 | 711.9 | 783.9 | 765.9 | 779.7 | 71.9 | 154.1 | 224.3 | 168.6 | 341.2 | 323.4 | 189.7 | 283.1 | 376.9 | 208.7
813 | 639 | 566.3 | 226.52 | 264.7888 | 354 | 301.9 | 316.7 | 301.1 | 595.4 | 42 | 20 | 79.7 | 5.2 | 229 | 4.1 | 865.3 | 803.4 | 835.7 | 849.4 | 870.5 | 767.1 | 708.8 | 784.4 | 765.9 | 780.3 | 72 | 154.4 | 224.6 | 169.3 | 341.5 | 323.3 | 190.9 | 283.2 | 377.3 | 209
814 | 640 | 566.2 | 226.48 | 264.7421 | 353.6 | 301.3 | 317.1 | 301.1 | 594 | 41.9 | 20 | 79.9 | 5.2 | 223.4 | 4.1 | 865.2 | 801.5 | 833.6 | 849.2 | 868.4 | 767.1 | 697.9 | 776.1 | 766 | 778.7 | 72.2 | 154.6 | 224.8 | 170.1 | 341.7 | 323.2 | 191.7 | 283.3 | 377.6 | 209.3
815 | 641 | 565.7 | 226.28 | 264.5083 | 353.8 | 301.3 | 317.8 | 301.4 | 593.6 | 42 | 20 | 80.1 | 5.8 | 220.1 | 4.1 | 865 | 801.2 | 833 | 849.3 | 867.4 | 767.3 | 694.6 | 774.2 | 766.2 | 777.8 | 72.3 | 154.9 | 225.2 | 170.8 | 341.6 | 323.2 | 192.4 | 283.5 | 378 | 209.6
816 | 642 | 565.5 | 226.2 | 264.4148 | 354.2 | 300.8 | 316.6 | 301.8 | 606.4 | 42.2 | 20 | 80.2 | 5.7 | 240.4 | 3.9 | 864.5 | 800.1 | 835.2 | 848.6 | 867.2 | 767.4 | 692.8 | 777 | 766.2 | 776.7 | 72.5 | 155.1 | 225.6 | 171.5 | 341.5 | 323.2 | 193.3 | 283.7 | 378.4 | 209.9
817 | 643 | 566.3 | 226.52 | 264.7888 | 355.4 | 301.3 | 315.5 | 301.2 | 622.5 | 42.4 | 20 | 80.3 | 5.5 | 252.6 | 3.8 | 864.3 | 799.9 | 837.6 | 848.4 | 869.1 | 767.2 | 700.1 | 783.6 | 766.3 | 777 | 72.6 | 155.4 | 226 | 172.2 | 341.7 | 323.1 | 194.2 | 283.8 | 378.8 | 210.2
818 | 644 | 566.3 | 226.52 | 264.7888 | 356 | 302.1 | 315.5 | 301.1 | 632.2 | 42.5 | 20 | 80.4 | 5.1 | 241.3 | 4.4 | 864.1 | 800.1 | 837.6 | 848.2 | 869.7 | 767 | 699.8 | 783.3 | 766.4 | 775.6 | 72.8 | 155.6 | 226.5 | 172.9 | 341.4 | 322.9 | 194.9 | 284 | 379.3 | 210.5
819 | 645 | 566.4 | 226.56 | 264.8356 | 356.2 | 302.8 | 315.1 | 301.8 | 637.1 | 42.6 | 20 | 80.5 | 5.7 | 239.1 | 5.2 | 864.2 | 801 | 835 | 848.2 | 866.8 | 767.2 | 688.2 | 775.9 | 766.5 | 772.5 | 73 | 155.9 | 227.1 | 173.6 | 341.6 | 322.6 | 195.6 | 284.1 | 379.8 | 210.8
820 | 646 | 567.9 | 227.16 | 265.537 | 355.2 | 303.8 | 315.2 | 302.5 | 639.8 | 42.8 | 20 | 80.7 | 5.6 | 254.8 | 5.3 | 864.2 | 797.6 | 832.6 | 847.9 | 863.7 | 767.3 | 677.8 | 766.8 | 766.7 | 770.2 | 73.2 | 156.1 | 227.4 | 174.3 | 341.4 | 322.7 | 196.2 | 284.2 | 380.3 | 211.1
821 | 647 | 566.9 | 226.76 | 265.0694 | 356.3 | 304 | 315.9 | 303.1 | 634.5 | 42.8 | 20 | 80.8 | 5.5 | 256.2 | 5.2 | 864.1 | 794 | 828.1 | 847 | 861.4 | 767.5 | 666.8 | 760.2 | 766.8 | 769.7 | 73.3 | 156.4 | 227.8 | 174.9 | 341.6 | 322.7 | 196.8 | 284.3 | 380.6 | 211.4
822 | 648 | 567.9 | 227.16 | 265.537 | 358.7 | 303.6 | 318.2 | 303 | 630.4 | 42.9 | 20 | 80.9 | 5.3 | 233.6 | 5.2 | 863.5 | 791.8 | 826.5 | 846.3 | 859.9 | 767.4 | 664.3 | 762.5 | 767.1 | 769.7 | 73.5 | 156.6 | 228.3 | 175.6 | 341.9 | 323 | 197.4 | 284.5 | 381 | 211.7
823 | 649 | 567 | 226.8 | 265.1161 | 359.2 | 303.9 | 319.5 | 304.5 | 628.6 | 43 | 19.9 | 81 | 5.4 | 233.6 | 5.1 | 862.8 | 792.4 | 829 | 845.6 | 861 | 767.1 | 671.9 | 771.1 | 767.2 | 769.9 | 73.6 | 156.9 | 228.3 | 176.3 | 342 | 323.2 | 198.1 | 284.7 | 381.4 | 212.1
824 | 650 | 567.7 | 227.08 | 265.4434 | 359.3 | 304 | 320.2 | 306.1 | 621.7 | 43.1 | 19.9 | 81.1 | 5.9 | 237.8 | 5.3 | 862.4 | 795.2 | 827.4 | 845.3 | 862.4 | 766.9 | 675.7 | 772.8 | 767.4 | 769.8 | 73.8 | 157.1 | 228.6 | 176.9 | 341.9 | 323.2 | 199 | 284.9 | 381.9 | 212.4
825 | 651 | 567.8 | 227.12 | 265.4902 | 359.4 | 304.2 | 320.1 | 306.5 | 617 | 43.1 | 19.9 | 81.2 | 5.8 | 238.2 | 5.3 | 861.9 | 795 | 826.5 | 844.8 | 863.5 | 766.7 | 674.8 | 768.3 | 767.6 | 768.3 | 74 | 157.4 | 229 | 177.6 | 342.1 | 323.6 | 199.7 | 285 | 382.2 | 212.7
826 | 652 | 567.8 | 227.12 | 265.4902 | 359.7 | 304.5 | 319.2 | 306.5 | 614.4 | 43.2 | 19.9 | 81.2 | 4.8 | 248.1 | 5.3 | 861.7 | 794 | 827.8 | 844.5 | 862.4 | 766.8 | 670.6 | 760.6 | 768 | 767.6 | 74.1 | 157.6 | 229.6 | 178.2 | 342.6 | 323.9 | 200.4 | 285.2 | 382.6 | 213
827 | 653 | 566.9 | 226.76 | 265.0694 | 360.9 | 305 | 319.5 | 306.9 | 626.7 | 43.2 | 19.9 | 81.1 | 6 | 236.4 | 5.5 | 861.9 | 794.3 | 829.5 | 844.9 | 861.1 | 767 | 667 | 760.6 | 768.3 | 766.7 | 74.3 | 157.9 | 230.1 | 178.9 | 343.3 | 324.2 | 201.2 | 285.4 | 383 | 213.3
828 | 654 | 567.1 | 226.84 | 265.1629 | 361.2 | 305 | 320 | 307.5 | 631.2 | 43.2 | 19.9 | 81 | 5.5 | 226.6 | 5.7 | 862.2 | 795.8 | 832.1 | 845.3 | 862.7 | 767 | 672.5 | 760.8 | 768.6 | 766.4 | 74.4 | 158.1 | 230.3 | 179.6 | 343.6 | 324.4 | 201.9 | 285.6 | 383.4 | 213.6
829 | 655 | 566.7 | 226.68 | 264.9759 | 362.1 | 305.2 | 319.8 | 307.7 | 626.2 | 43.1 | 19.9 | 81.1 | 5.3 | 213.9 | 5.3 | 862.3 | 793.6 | 831.1 | 845 | 859.4 | 767.1 | 671.8 | 756.3 | 768.9 | 765.5 | 74.6 | 158.4 | 230.7 | 180.3 | 343.8 | 324.6 | 202.4 | 285.8 | 383.7 | 213.9
830 | 656 | 566.8 | 226.72 | 265.0226 | 361.9 | 305.2 | 319 | 307.3 | 636.3 | 43 | 19.9 | 81.3 | 5.2 | 194.2 | 4.6 | 862.2 | 792.7 | 830.1 | 844.7 | 858.4 | 767.2 | 665.8 | 753.3 | 769.1 | 764.5 | 74.7 | 158.6 | 231.2 | 180.9 | 344 | 324.9 | 203.1 | 285.9 | 384 | 214.2
831 | 657 | 566.2 | 226.48 | 264.7421 | 362.3 | 305.3 | 316.9 | 306.7 | 649 | 43 | 19.9 | 81.4 | 5.1 | 196.1 | 3.5 | 862.3 | 794 | 829 | 845 | 857.2 | 767 | 665 | 756 | 769.3 | 764.9 | 74.9 | 158.9 | 231.4 | 181.6 | 344.4 | 325.3 | 203.7 | 286.1 | 384.4 | 214.5
832 | 658 | 566 | 226.4 | 264.6486 | 362.2 | 305.6 | 315.7 | 306.8 | 658.8 | 43 | 19.9 | 81.4 | 5.1 | 221.1 | 2.9 | 862.4 | 794.1 | 828.4 | 845.2 | 857.3 | 766.9 | 659.8 | 759.8 | 769.6 | 764.5 | 75 | 159.1 | 231.9 | 182.2 | 344.7 | 325.6 | 204.3 | 286.2 | 384.8 | 214.8
833 | 659 | 565.8 | 226.32 | 264.555 | 361.9 | 305.3 | 315.9 | 307.2 | 662.2 | 43 | 19.9 | 81.3 | 5.7 | 246.8 | 3.1 | 862.1 | 796.6 | 828.7 | 845.2 | 858.5 | 767 | 659.5 | 762.2 | 769.9 | 765.7 | 75.2 | 159.4 | 232.3 | 182.9 | 345 | 325.7 | 204.8 | 286.4 | 385.2 | 215.2
834 | 660 | 565.9 | 226.36 | 264.6018 | 362.1 | 305.9 | 317.6 | 307.6 | 659.8 | 43.1 | 19.9 | 81.3 | 5.2 | 246.4 | 3.2 | 861.9 | 797.1 | 829.1 | 845 | 857.4 | 767.3 | 660.8 | 765.5 | 770.2 | 765.9 | 75.3 | 159.6 | 232.5 | 183.5 | 345 | 325.9 | 205.3 | 286.5 | 385.6 | 215.5
835 | 661 | 566.7 | 226.68 | 264.9759 | 362.3 | 306.9 | 318.9 | 307 | 639.3 | 43.1 | 19.9 | 81.3 | 5.4 | 240.7 | 3.4 | 861.6 | 799.4 | 830.8 | 845.1 | 858.1 | 767.4 | 673.6 | 770.2 | 770.3 | 767 | 75.5 | 159.9 | 232.4 | 184.2 | 344.7 | 325.9 | 206 | 286.7 | 386 | 215.8
836 | 662 | 566.9 | 226.76 | 265.0694 | 361.7 | 307.1 | 318.6 | 306.8 | 618.8 | 43.2 | 19.9 | 81.3 | 5.3 | 234.9 | 3.5 | 861 | 802.1 | 831.2 | 844.1 | 859.2 | 767.5 | 697.6 | 777.5 | 770.5 | 767.7 | 75.6 | 160.1 | 232.7 | 184.8 | 345 | 326.4 | 206.7 | 287 | 386.3 | 216.1
837 | 663 | 566.3 | 226.52 | 264.7888 | 360.9 | 307.5 | 318.8 | 306.3 | 606.2 | 43.2 | 19.9 | 81.4 | 6.1 | 233.7 | 3.7 | 860.8 | 801.9 | 834.1 | 843.6 | 859.4 | 767.5 | 716.4 | 787.8 | 770.7 | 768.7 | 75.8 | 160.4 | 233 | 185.4 | 344.8 | 326.8 | 207 | 287.3 | 386.7 | 216.4
838 | 664 | 566.6 | 226.64 | 264.9291 | 360.1 | 308.6 | 318.9 | 306.2 | 593 | 43.2 | 19.9 | 81.4 | 5.6 | 233.4 | 3.7 | 860.5 | 800.5 | 836.4 | 843.2 | 860.4 | 767.6 | 727.1 | 793 | 770.8 | 769.4 | 75.9 | 160.7 | 233.2 | 186 | 344.5 | 327.2 | 207.2 | 287.4 | 387.1 | 216.7
839 | 665 | 565.8 | 226.32 | 264.555 | 359.1 | 309.8 | 318.6 | 305.8 | 583.3 | 43.2 | 19.9 | 81.3 | 5.7 | 210.7 | 3.6 | 859.9 | 800.3 | 837.9 | 842.8 | 861.9 | 767.8 | 733.5 | 796.1 | 770.8 | 770.2 | 76.1 | 160.9 | 233.5 | 186.6 | 344.3 | 327.2 | 207.8 | 287.5 | 387.6 | 217
840 | 666 | 567.6 | 227.04 | 265.3967 | 357.8 | 310.4 | 318.7 | 305.7 | 576.9 | 43.3 | 19.9 | 81.2 | 4.9 | 206.6 | 4.1 | 859.8 | 802.1 | 838.2 | 843 | 862.4 | 767.9 | 732.2 | 797.3 | 770.8 | 771.1 | 76.2 | 161.2 | 233.8 | 187.2 | 344 | 327.1 | 208.2 | 287.6 | 388.1 | 217.3
841 | 667 | 565.3 | 226.12 | 264.3213 | 356.9 | 310.7 | 318.4 | 305.1 | 589.8 | 43.3 | 19.9 | 81.2 | 5.3 | 209.3 | 3.9 | 860.3 | 804.5 | 839.1 | 844.3 | 859.4 | 768.1 | 719.7 | 792.1 | 770.9 | 769.5 | 76.4 | 161.5 | 234.2 | 187.8 | 343.9 | 327.1 | 208.8 | 287.7 | 388.5 | 217.6
842 | 668 | 564.9 | 225.96 | 264.1342 | 357 | 310.8 | 317.8 | 303.8 | 602.4 | 43.3 | 19.9 | 81.2 | 5.1 | 215.8 | 4.2 | 860.7 | 809.6 | 839.1 | 844.9 | 857.4 | 768.2 | 710.4 | 789.6 | 771 | 768.7 | 76.5 | 161.7 | 234.5 | 188.4 | 343.9 | 326.8 | 209.2 | 287.8 | 388.8 | 217.9
843 | 669 | 565.2 | 226.08 | 264.2745 | 356.7 | 311.4 | 317.8 | 303.4 | 603.4 | 43.4 | 19.9 | 81.2 | 4.9 | 218.7 | 4.3 | 861 | 810.5 | 839.6 | 845.5 | 859.2 | 768 | 708.1 | 792.8 | 771 | 770.5 | 76.7 | 162 | 234.7 | 189 | 343.5 | 326.4 | 209.6 | 287.8 | 389.1 | 218.1
844 | 670 | 566.4 | 226.56 | 264.8356 | 355.6 | 311.6 | 317.6 | 302.8 | 599.4 | 43.4 | 19.9 | 81.2 | 4.8 | 222.3 | 4.1 | 861.5 | 811.4 | 840 | 846 | 858.9 | 767.7 | 718 | 797.8 | 771.1 | 772.1 | 76.8 | 162.3 | 235 | 189.6 | 343.2 | 326.2 | 210 | 288 | 389.4 | 218.4
845 | 671 | 566.9 | 226.76 | 265.0694 | 354.7 | 312 | 317.2 | 302.7 | 605.5 | 43.4 | 19.9 | 81.2 | 5.2 | 218.3 | 3.6 | 861.7 | 812.3 | 837.9 | 846.5 | 860.3 | 767.7 | 717.1 | 798.2 | 771.2 | 771.4 | 77 | 162.5 | 235.3 | 190.1 | 343 | 326 | 210.4 | 288 | 389.7 | 218.7
846 | 672 | 565.7 | 226.28 | 264.5083 | 354.2 | 312 | 317.8 | 302.6 | 604.4 | 43.4 | 19.9 | 81.4 | 5.4 | 242.7 | 3.4 | 861.9 | 816.5 | 837.9 | 847.9 | 861.1 | 767.6 | 722.1 | 802.9 | 771.4 | 773.2 | 77.1 | 162.8 | 235.7 | 190.7 | 343 | 325.9 | 210.9 | 288.2 | 390.1 | 219
847 | 673 | 566.9 | 226.76 | 265.0694 | 353.8 | 312.4 | 318.7 | 303.2 | 599.8 | 43.4 | 19.9 | 81.5 | 5.4 | 233 | 3.3 | 862 | 818.6 | 838.4 | 848.4 | 861.3 | 767.7 | 732.5 | 807.7 | 771.7 | 773.7 | 77.3 | 163.1 | 235.8 | 191.3 | 342.8 | 326.1 | 211.5 | 288.4 | 390.4 | 219.3
848 | 674 | 568.2 | 227.28 | 265.6772 | 354.8 | 313.2 | 319.3 | 302.8 | 580.8 | 43.4 | 19.9 | 81.5 | 5.4 | 209.1 | 3.3 | 862.1 | 818.7 | 837.6 | 848.4 | 862.3 | 767.7 | 737.7 | 810.9 | 771.8 | 773.9 | 77.4 | 163.4 | 235.9 | 191.9 | 342.7 | 326 | 211.9 | 288.5 | 390.8 | 219.5
849 | 675 | 565 | 226 | 264.181 | 354.3 | 313.7 | 319 | 302.5 | 563.5 | 43.5 | 19.9 | 81.5 | 6.2 | 231.1 | 3.3 | 861.7 | 817.9 | 835.2 | 847.7 | 863.2 | 767.7 | 739.7 | 810.7 | 771.9 | 774.3 | 77.6 | 163.6 | 236 | 192.4 | 342.5 | 326.1 | 212.1 | 288.6 | 391.1 | 219.8
850 | 676 | 565 | 226 | 264.181 | 353.5 | 314.1 | 318.1 | 302.3 | 551.3 | 43.5 | 19.9 | 81.6 | 6.6 | 229.5 | 3.4 | 861.3 | 815.6 | 835.6 | 846.9 | 863.1 | 767.8 | 751.8 | 813.3 | 772 | 775.1 | 77.8 | 163.9 | 236.3 | 193 | 342.2 | 326.3 | 212.4 | 288.8 | 391.4 | 220.1
851 | 677 | 566.1 | 226.44 | 264.6953 | 354.3 | 313.9 | 318.4 | 302 | 541.1 | 43.6 | 19.9 | 81.7 | 5.9 | 222.4 | 3.7 | 861 | 812 | 835.6 | 845.5 | 863.6 | 768 | 762.7 | 814.1 | 772.3 | 775 | 77.9 | 164.2 | 236.6 | 193.5 | 342.5 | 326.6 | 212.8 | 289 | 391.7 | 220.4
852 | 678 | 565.6 | 226.24 | 264.4615 | 354.8 | 315.4 | 318.9 | 302.3 | 527.9 | 43.6 | 19.9 | 81.7 | 5.8 | 223.4 | 4.3 | 860.6 | 812.9 | 833.4 | 845 | 865 | 768.2 | 765.8 | 817.9 | 772.4 | 775.7 | 78.1 | 164.5 | 236.9 | 194.1 | 342.9 | 326.9 | 213.1 | 289.2 | 392.2 | 220.7
853 | 679 | 566.1 | 226.44 | 264.6953 | 354.3 | 315.2 | 320 | 302.9 | 524.9 | 43.6 | 19.8 | 81.8 | 5.8 | 224.9 | 4.3 | 860.5 | 813.9 | 832.8 | 844.7 | 865 | 768.6 | 773.2 | 817.3 | 772.6 | 777.5 | 78.2 | 164.7 | 237.1 | 194.7 | 343.2 | 327.2 | 213.5 | 289.4 | 392.6 | 221
854 | 680 | 567.9 | 227.16 | 265.537 | 354.6 | 314.9 | 321.7 | 303.3 | 522.3 | 43.7 | 19.8 | 81.9 | 5.9 | 218.7 | 4.4 | 860.3 | 811.6 | 835.1 | 844 | 865.6 | 769.1 | 779.2 | 818 | 772.9 | 778 | 78.4 | 165 | 237.2 | 195.2 | 343.8 | 327.7 | 214 | 289.5 | 392.9 | 221.3
855 | 681 | 566.8 | 226.72 | 265.0226 | 354.1 | 315.5 | 321.5 | 303.7 | 515.8 | 43.7 | 19.8 | 81.9 | 6 | 210.5 | 4.6 | 859.8 | 812.8 | 833.8 | 843.4 | 865.9 | 769.4 | 779.1 | 818.4 | 773.1 | 778.2 | 78.6 | 165.3 | 237.4 | 195.7 | 344.5 | 328.5 | 214.4 | 289.8 | 393.2 | 221.5
856 | 682 | 565.3 | 226.12 | 264.3213 | 354.4 | 315.6 | 321.1 | 303.3 | 507.8 | 43.8 | 19.8 | 81.9 | 5.3 | 200.2 | 3.9 | 859.4 | 813.8 | 827.6 | 842.7 | 865.6 | 769.7 | 770.5 | 811.6 | 773.1 | 776.5 | 78.7 | 165.5 | 237.6 | 196.3 | 345.7 | 329.4 | 215 | 290.1 | 393.5 | 221.9
857 | 683 | 565.5 | 226.2 | 264.4148 | 355 | 315.7 | 321.2 | 303 | 500 | 43.8 | 19.8 | 82 | 5.8 | 212.1 | 3.5 | 859.3 | 811 | 828.1 | 842.5 | 867.1 | 769.8 | 772.7 | 814.2 | 773.1 | 776.9 | 78.9 | 165.8 | 237.8 | 196.8 | 346 | 330.2 | 215.5 | 290.4 | 393.8 | 222.2
858 | 684 | 566 | 226.4 | 264.6486 | 356.1 | 316.4 | 321.7 | 303.2 | 514.6 | 43.8 | 19.8 | 82.2 | 5.7 | 221.6 | 3.7 | 859.2 | 808.6 | 832.8 | 843 | 864 | 769.8 | 771.3 | 815 | 773.4 | 776.7 | 79 | 166 | 238.2 | 197.3 | 346.1 | 330.1 | 216 | 290.7 | 394.1 | 222.5
859 | 685 | 566.4 | 226.56 | 264.8356 | 356 | 316.1 | 322.2 | 302.9 | 525.2 | 43.9 | 19.8 | 82.4 | 6.1 | 228.1 | 3.8 | 858.7 | 807.4 | 834.7 | 843.8 | 862.9 | 769.9 | 775.7 | 816.5 | 773.4 | 774.5 | 79.2 | 166.3 | 238.4 | 197.9 | 346.2 | 330.2 | 216.5 | 290.8 | 394.5 | 222.7
860 | 686 | 566.2 | 226.48 | 264.7421 | 354.9 | 316.4 | 322.4 | 302.2 | 517.6 | 44 | 19.8 | 82.6 | 6 | 244.5 | 4.1 | 858.4 | 805.6 | 835.9 | 842.6 | 864.4 | 769.8 | 781.3 | 816.2 | 773.3 | 775.2 | 79.4 | 166.6 | 238.4 | 198.4 | 346.1 | 330.9 | 216.8 | 291 | 394.9 | 223
861 | 687 | 565.8 | 226.32 | 264.555 | 354.2 | 315.4 | 321.5 | 302.2 | 514 | 44 | 19.8 | 82.7 | 6 | 256 | 4.4 | 858.3 | 806.3 | 834.9 | 842 | 864.8 | 769.7 | 785.3 | 817.3 | 773.2 | 775.6 | 79.5 | 166.8 | 238.7 | 199 | 345.8 | 331.7 | 217.1 | 291.3 | 395.3 | 223.3
862 | 688 | 566.2 | 226.48 | 264.7421 | 354.8 | 314.9 | 321.1 | 301.9 | 511.2 | 44.1 | 19.8 | 82.8 | 5.4 | 254.5 | 4.4 | 858.3 | 809.5 | 834.8 | 842.3 | 865.2 | 769.9 | 788.8 | 819 | 773.3 | 776.4 | 79.7 | 167.1 | 238.9 | 199.5 | 346 | 332 | 217.5 | 291.6 | 395.7 | 223.6
863 | 689 | 567.7 | 227.08 | 265.4434 | 353.8 | 315.4 | 321.8 | 301.4 | 510.4 | 44.1 | 19.8 | 82.9 | 5.1 | 248.3 | 4.4 | 858 | 810.4 | 835 | 842.2 | 866.9 | 769.9 | 792.2 | 818.5 | 773.6 | 777.9 | 79.9 | 167.4 | 239.1 | 200 | 346.3 | 332.1 | 217.9 | 291.7 | 396.1 | 223.9
864 | 690 | 567.3 | 226.92 | 265.2564 | 352.7 | 314.4 | 321.4 | 301 | 505 | 44.2 | 19.8 | 82.9 | 5.5 | 245 | 4.3 | 857.8 | 812 | 835.5 | 842.6 | 865 | 770.1 | 797.3 | 822.3 | 774 | 777.8 | 80.1 | 167.6 | 239.2 | 200.5 | 346.6 | 332.7 | 218.2 | 292 | 396.5 | 224.2
865 | 691 | 567.6 | 227.04 | 265.3967 | 352.6 | 313.2 | 320.9 | 300.1 | 512 | 44.2 | 19.8 | 82.8 | 5.7 | 236.8 | 4.6 | 858.3 | 812.1 | 836.8 | 844 | 863.2 | 770.1 | 794.5 | 822 | 774.3 | 777.4 | 80.2 | 167.9 | 239.6 | 201.1 | 346.8 | 333.2 | 218.5 | 292.1 | 396.8 | 224.4
866 | 692 | 567.3 | 226.92 | 265.2564 | 352.4 | 312.1 | 320.9 | 299.6 | 524.3 | 44.1 | 19.8 | 82.8 | 5.9 | 240.4 | 5.4 | 858.5 | 811.2 | 838.5 | 844.6 | 862.8 | 770.3 | 786 | 821.6 | 774.6 | 777.2 | 80.4 | 168.2 | 240 | 201.6 | 346.7 | 333.7 | 218.7 | 292.3 | 397.2 | 224.7
867 | 693 | 567.7 | 227.08 | 265.4434 | 353.2 | 311.6 | 319.9 | 299.9 | 534.1 | 44 | 19.8 | 82.8 | 6.7 | 231.3 | 5.8 | 858.6 | 814.2 | 838.6 | 845 | 863.5 | 770.3 | 775.8 | 820.6 | 775 | 777.5 | 80.6 | 168.5 | 240.2 | 202.1 | 346.5 | 333.8 | 219.1 | 292.4 | 397.5 | 225
868 | 694 | 566.5 | 226.6 | 264.8823 | 354 | 311.4 | 318.9 | 300.1 | 540.8 | 44 | 19.8 | 82.8 | 6 | 212.5 | 6 | 858.7 | 812.9 | 839.3 | 845.9 | 863.5 | 770.3 | 774.7 | 822.4 | 775.3 | 778 | 80.7 | 168.7 | 240.3 | 202.6 | 346.2 | 333.7 | 219.4 | 292.5 | 397.7 | 225.3
869 | 695 | 568 | 227.2 | 265.5837 | 354.6 | 310.6 | 318.1 | 300.4 | 549.2 | 43.9 | 19.8 | 82.9 | 6.7 | 222.1 | 5.9 | 858.6 | 811.8 | 841.1 | 845.5 | 864 | 770.3 | 781 | 822.4 | 775.8 | 778.7 | 80.9 | 169 | 240.6 | 203.1 | 345.9 | 334.1 | 219.6 | 292.6 | 398 | 225.6
870 | 696 | 567.1 | 226.84 | 265.1629 | 355.2 | 309.9 | 317.5 | 301.1 | 556.1 | 43.9 | 19.8 | 82.9 | 6.3 | 234.6 | 5.6 | 858.5 | 814.2 | 842.6 | 845.4 | 862.7 | 770.7 | 775 | 819.5 | 776.2 | 779.4 | 81.1 | 169.3 | 240.9 | 203.6 | 345.4 | 333.9 | 219.9 | 292.8 | 398.4 | 225.8
871 | 697 | 567.8 | 227.12 | 265.4902 | 355.5 | 308.7 | 316.8 | 301.7 | 566.3 | 43.9 | 19.8 | 82.9 | 5.6 | 228.9 | 5 | 858.4 | 816.8 | 840.8 | 845.2 | 863.9 | 771 | 766.6 | 816.4 | 776.7 | 779.7 | 81.3 | 169.6 | 241.3 | 204.1 | 345.6 | 333.4 | 220.3 | 292.8 | 398.7 | 226.1
872 | 698 | 567.6 | 227.04 | 265.3967 | 354.6 | 307.9 | 315.5 | 301.2 | 571.9 | 44 | 19.8 | 82.9 | 5.4 | 222.3 | 4.5 | 858.5 | 818.8 | 839.6 | 845.3 | 866.1 | 771.3 | 759.3 | 813.9 | 777.1 | 778.7 | 81.5 | 169.8 | 241.5 | 204.6 | 345.2 | 332.9 | 220.6 | 292.8 | 398.9 | 226.4
873 | 699 | 567.8 | 227.12 | 265.4902 | 353.5 | 307.3 | 316.2 | 300.8 | 572.3 | 44 | 19.8 | 82.8 | 5.5 | 228.5 | 4.6 | 858.6 | 818.4 | 839.4 | 845.6 | 867.1 | 771.6 | 756.2 | 813.2 | 777.5 | 780.4 | 81.7 | 170.1 | 241.7 | 205 | 345 | 333 | 220.9 | 292.9 | 399.2 | 226.6
874 | 700 | 568 | 227.2 | 265.5837 | 353.8 | 306.5 | 316.4 | 300.8 | 588.9 | 44 | 19.8 | 82.9 | 6 | 246.6 | 5.2 | 858.2 | 820 | 837 | 844.8 | 867 | 771.7 | 745.9 | 809.3 | 778 | 779.9 | 81.8 | 170.4 | 242.2 | 205.5 | 345.3 | 333 | 221.3 | 293.1 | 399.4 | 226.9
875 | 701 | 567.4 | 226.96 | 265.3032 | 355.8 | 305.7 | 316 | 301.3 | 598.4 | 44 | 19.8 | 83 | 6.4 | 238.5 | 5.4 | 857.6 | 822.7 | 832.6 | 844.8 | 865.2 | 771.9 | 735.8 | 804.3 | 778.5 | 780.2 | 82 | 170.7 | 242.6 | 206 | 345.7 | 333 | 221.5 | 293.3 | 399.7 | 227.2
876 | 702 | 567.4 | 226.96 | 265.3032 | 356.6 | 304.4 | 317.4 | 301.8 | 592.2 | 44 | 19.8 | 82.9 | 5.6 | 259.7 | 5.5 | 857.1 | 823.3 | 831.1 | 844.4 | 864.6 | 771.9 | 730.2 | 799.2 | 778.8 | 779.8 | 82.2 | 170.9 | 242.8 | 206.4 | 345.5 | 332.6 | 221.7 | 293.4 | 400 | 227.5
877 | 703 | 567.4 | 226.96 | 265.3032 | 357 | 303.9 | 317.9 | 302.5 | 601.8 | 44.1 | 19.8 | 82.9 | 5.5 | 243.6 | 4.8 | 856.9 | 821.4 | 829.5 | 844.2 | 863 | 772 | 719.7 | 792.8 | 779.2 | 778.4 | 82.4 | 171.2 | 243.3 | 206.9 | 345.4 | 332.3 | 222.1 | 293.4 | 400.2 | 227.7
878 | 704 | 567.9 | 227.16 | 265.537 | 357.9 | 303.8 | 318.4 | 302.9 | 625.1 | 44.1 | 19.8 | 82.9 | 5 | 217.9 | 4.3 | 856.7 | 816.2 | 826.3 | 843.8 | 861.5 | 772.1 | 712.3 | 787.4 | 779.5 | 776.4 | 82.6 | 171.5 | 244.1 | 207.4 | 345.8 | 332.1 | 222.5 | 293.4 | 400.5 | 228
879 | 705 | 567.5 | 227 | 265.3499 | 358 | 304.1 | 318.6 | 304.1 | 645.6 | 44.1 | 19.8 | 83 | 5.1 | 229.6 | 4.3 | 856.4 | 815.1 | 826.8 | 843.8 | 860.9 | 772.1 | 712.5 | 792 | 779.8 | 775.6 | 82.8 | 171.8 | 244.4 | 207.8 | 346.4 | 332.1 | 222.9 | 293.5 | 400.9 | 228.3
880 | 706 | 567.5 | 227 | 265.3499 | 359.9 | 305 | 319.4 | 305.3 | 657.9 | 44.2 | 19.8 | 83 | 5.8 | 233 | 4.3 | 856.4 | 813.6 | 825.6 | 844 | 859.3 | 772.1 | 708.9 | 791 | 780.2 | 775.5 | 83 | 172 | 245.1 | 208.3 | 347.4 | 332.2 | 223.5 | 293.6 | 401.3 | 228.6
881 | 707 | 567.2 | 226.88 | 265.2096 | 362 | 306 | 320.2 | 306.1 | 660.2 | 44.3 | 19.8 | 82.9 | 5.5 | 238.6 | 4.9 | 856.5 | 813.5 | 826.4 | 843.8 | 857.1 | 772.1 | 700.8 | 788.2 | 780.3 | 774.1 | 83.2 | 172.3 | 245.4 | 208.7 | 348.2 | 332.4 | 224.2 | 293.8 | 401.6 | 228.9
882 | 708 | 567.5 | 227 | 265.3499 | 363.6 | 306.9 | 322.2 | 307.1 | 664.9 | 44.4 | 19.8 | 82.9 | 5.4 | 240.3 | 5.4 | 856.5 | 813.7 | 826.5 | 843.7 | 857.9 | 772.1 | 695.8 | 785.6 | 780.4 | 773.2 | 83.4 | 172.6 | 245.5 | 209.1 | 348.6 | 332.6 | 224.7 | 293.9 | 402 | 229.2
883 | 709 | 567.1 | 226.84 | 265.1629 | 364.1 | 308.5 | 323 | 307.9 | 663.1 | 44.5 | 19.8 | 82.9 | 5.5 | 235.8 | 5.5 | 856.2 | 813.1 | 827.2 | 843.8 | 856.1 | 772.3 | 686.4 | 781 | 780.6 | 771 | 83.5 | 172.9 | 246.1 | 209.6 | 349.1 | 332.9 | 225.2 | 294 | 402.3 | 229.5
884 | 710 | 567.1 | 226.84 | 265.1629 | 365.1 | 309.3 | 322.9 | 308.4 | 657.1 | 44.6 | 19.8 | 82.9 | 5.3 | 223.5 | 5.4 | 855.7 | 812.2 | 823.6 | 842.7 | 856 | 772.1 | 682.3 | 781.7 | 780.7 | 769.7 | 83.7 | 173.2 | 246.4 | 210 | 349.5 | 333.2 | 225.5 | 294.1 | 402.6 | 229.8
885 | 711 | 567.2 | 226.88 | 265.2096 | 367 | 309.6 | 323.5 | 308 | 637.2 | 44.7 | 19.8 | 82.9 | 5.7 | 248.2 | 6.2 | 855 | 808.7 | 819.9 | 841.9 | 853.8 | 772 | 679.9 | 778.1 | 780.8 | 770.2 | 83.9 | 173.4 | 246.7 | 210.5 | 350 | 333.5 | 225.9 | 294.3 | 402.9 | 230.1
886 | 712 | 567.4 | 226.96 | 265.3032 | 367.1 | 309.7 | 324.6 | 308.3 | 629.9 | 44.7 | 19.8 | 82.8 | 5 | 240.3 | 6.9 | 854.7 | 811.4 | 822.9 | 842.2 | 853.4 | 771.7 | 685.7 | 783.9 | 780.9 | 771.1 | 84.1 | 173.7 | 246.9 | 211 | 350.4 | 333.7 | 226.3 | 294.4 | 403.1 | 230.3
887 | 713 | 567 | 226.8 | 265.1161 | 367.7 | 310.1 | 324.5 | 309.5 | 641.3 | 44.8 | 19.8 | 82.7 | 5.3 | 236.7 | 7.1 | 854.5 | 813.3 | 823.1 | 841.9 | 853.2 | 771.4 | 686.5 | 784.2 | 780.9 | 770.3 | 84.3 | 174 | 247.5 | 211.5 | 350.9 | 333.6 | 226.7 | 294.6 | 403.4 | 230.6
888 | 714 | 567.6 | 227.04 | 265.3967 | 368.2 | 310.6 | 323.7 | 310.1 | 649.3 | 44.8 | 19.8 | 82.7 | 5.6 | 238.8 | 6.6 | 854.2 | 812.1 | 822.1 | 841.9 | 851.4 | 771.4 | 684.4 | 781.7 | 780.9 | 769.4 | 84.5 | 174.3 | 247.8 | 211.9 | 351.3 | 333.5 | 227.1 | 294.6 | 403.8 | 231
889 | 715 | 566.5 | 226.6 | 264.8823 | 368.2 | 311.5 | 324.1 | 310.4 | 657.3 | 44.7 | 19.8 | 82.8 | 4.9 | 247.5 | 6.3 | 854.1 | 812 | 822.1 | 842.3 | 850.5 | 771.3 | 681 | 780.4 | 781 | 767.4 | 84.7 | 174.6 | 248.3 | 212.4 | 351.7 | 333.5 | 227.6 | 294.8 | 404.1 | 231.3
890 | 716 | 566.6 | 226.64 | 264.9291 | 368.3 | 312.1 | 324.4 | 311.1 | 657.8 | 44.7 | 19.8 | 82.8 | 4.9 | 234.1 | 6.2 | 853.7 | 813.1 | 823.7 | 842.4 | 850 | 771.1 | 681.3 | 783.5 | 781 | 766.4 | 84.9 | 174.9 | 248.6 | 212.9 | 352.1 | 333.8 | 228.1 | 294.9 | 404.5 | 231.5
891 | 717 | 567.4 | 226.96 | 265.3032 | 368.3 | 312.6 | 324.2 | 311.4 | 663.8 | 44.6 | 19.8 | 82.8 | 5 | 244.4 | 6.3 | 853.5 | 812.2 | 827.6 | 842.4 | 850.7 | 770.8 | 689.6 | 785.7 | 780.8 | 765.5 | 85.1 | 175.2 | 248.8 | 213.4 | 352.4 | 333.9 | 228.4 | 295.1 | 404.8 | 231.8
892 | 718 | 567 | 226.8 | 265.1161 | 368.2 | 314.3 | 324.4 | 311.7 | 663.8 | 44.6 | 19.8 | 82.9 | 4.6 | 251.8 | 6 | 853.6 | 811 | 827.3 | 842.3 | 850 | 770.9 | 687.6 | 784 | 780.6 | 764.7 | 85.3 | 175.5 | 249 | 213.9 | 352.4 | 334.1 | 228.8 | 295.3 | 405.2 | 232.1
893 | 719 | 567.2 | 226.88 | 265.2096 | 367.8 | 315.9 | 325 | 312.1 | 652.9 | 44.7 | 19.8 | 82.9 | 5 | 241.4 | 5.7 | 853.3 | 813.3 | 827.1 | 842.6 | 852.3 | 771.1 | 691 | 784.9 | 780.6 | 764.4 | 85.5 | 175.7 | 249.3 | 214.3 | 352.2 | 334.1 | 229.2 | 295.5 | 405.5 | 232.4
894 | 720 | 566.6 | 226.64 | 264.9291 | 366.5 | 315.6 | 326 | 312.6 | 644.8 | 44.8 | 19.8 | 82.9 | 4.9 | 206.2 | 4.9 | 852.7 | 817.5 | 824.2 | 843.1 | 854.8 | 770.9 | 692.5 | 783.5 | 780.5 | 765.1 | 85.7 | 176 | 249.6 | 214.8 | 352.6 | 334.1 | 229.6 | 295.6 | 405.8 | 232.7
895 | 721 | 567.7 | 227.08 | 265.4434 | 366.2 | 315.3 | 325.7 | 312.5 | 633.1 | 44.8 | 19.8 | 83 | 5 | 228.6 | 4.5 | 852.1 | 821.9 | 822.7 | 843.6 | 855.8 | 770.8 | 701.5 | 787.1 | 780.4 | 767 | 85.9 | 176.3 | 249.8 | 215.3 | 353.2 | 334.3 | 230 | 295.8 | 406.1 | 232.9
896 | 722 | 568.6 | 227.44 | 265.8643 | 367.7 | 314.7 | 324.5 | 312.4 | 624.7 | 44.9 | 19.8 | 83 | 4.8 | 252.9 | 4.8 | 851.4 | 821.6 | 821.5 | 842.7 | 856.4 | 771 | 700.2 | 786 | 780.6 | 767.4 | 86.2 | 176.6 | 250.1 | 215.8 | 353.2 | 334.5 | 230.2 | 295.9 | 406.3 | 233.2
897 | 723 | 568.6 | 227.44 | 265.8643 | 368.2 | 315.2 | 323.6 | 312.5 | 623.1 | 45 | 19.8 | 82.9 | 5.4 | 217.4 | 4.4 | 850.9 | 821.5 | 824.6 | 841.9 | 853.6 | 771 | 699.3 | 790.7 | 780.7 | 766.2 | 86.4 | 176.9 | 250.4 | 216.3 | 353.2 | 334.3 | 230.6 | 296 | 406.6 | 233.5
898 | 724 | 566.6 | 226.64 | 264.9291 | 367.7 | 315.3 | 322 | 312.6 | 633 | 45.1 | 19.8 | 82.9 | 5.4 | 185.5 | 4.5 | 850.6 | 822.2 | 827.8 | 842 | 853.5 | 770.9 | 698.6 | 790.5 | 780.8 | 765.3 | 86.6 | 177.1 | 250.8 | 216.8 | 353.7 | 334.2 | 230.9 | 296.1 | 406.9 | 233.8
899 | 725 | 566.9 | 226.76 | 265.0694 | 366.6 | 315.3 | 321 | 311.8 | 632.7 | 45.1 | 19.8 | 83 | 5.3 | 219.8 | 4.1 | 850.4 | 824.8 | 827.6 | 842.2 | 853.3 | 770.9 | 698.9 | 792.9 | 780.9 | 765.1 | 86.8 | 177.4 | 250.9 | 217.3 | 353.9 | 333.9 | 231.2 | 296.3 | 407.3 | 234.1
900 | 726 | 566.7 | 226.68 | 264.9759 | 365.1 | 314.7 | 319.7 | 311.9 | 635.8 | 45 | 19.8 | 83 | 4.6 | 237.1 | 4 | 850.3 | 827.4 | 830.1 | 843.1 | 854.6 | 770.8 | 706.4 | 800.5 | 780.9 | 765 | 87 | 177.7 | 251.2 | 217.7 | 353.8 | 333.9 | 231.4 | 296.4 | 407.6 | 234.4
901 | 727 | 566.2 | 226.48 | 264.7421 | 365.2 | 314.1 | 318.7 | 311.6 | 636.8 | 45 | 19.7 | 83 | 5.5 | 211.2 | 3.9 | 850.1 | 829.6 | 832.4 | 843.4 | 858 | 770.5 | 710.9 | 803.3 | 780.9 | 765.9 | 87.2 | 178 | 251.3 | 218.1 | 353.3 | 333.8 | 231.5 | 296.6 | 407.9 | 234.6
902 | 728 | 566.7 | 226.68 | 264.9759 | 365.5 | 313.5 | 318 | 311.1 | 620.2 | 45 | 19.7 | 83 | 4.9 | 208.4 | 3.8 | 850.2 | 830.4 | 832.1 | 844 | 859 | 770.2 | 719.2 | 804.4 | 780.9 | 767.5 | 87.5 | 178.3 | 251.4 | 218.5 | 352.8 | 333.8 | 231.7 | 296.8 | 408.2 | 234.9
903 | 729 | 567.2 | 226.88 | 265.2096 | 364.9 | 313.7 | 317.7 | 311 | 613.6 | 45 | 19.7 | 83.1 | 5.2 | 219.9 | 3.6 | 849.9 | 827.2 | 833.1 | 843.4 | 860.6 | 769.9 | 735.2 | 807 | 780.9 | 768.9 | 87.7 | 178.6 | 251.8 | 218.9 | 352.4 | 333.9 | 231.8 | 296.9 | 408.4 | 235.1
904 | 730 | 568.2 | 227.28 | 265.6772 | 364.5 | 314.3 | 317.8 | 310.2 | 621.1 | 45.1 | 19.7 | 83.2 | 5.8 | 225 | 3.3 | 849.4 | 826.8 | 832.7 | 842.6 | 861.5 | 769.8 | 745.3 | 809.2 | 781 | 769.8 | 87.9 | 178.8 | 252.2 | 219.2 | 352.2 | 333.9 | 231.9 | 297.1 | 408.7 | 235.4
905 | 731 | 567.9 | 227.16 | 265.537 | 363.8 | 315 | 318.5 | 309.9 | 622.3 | 45.2 | 19.7 | 83.4 | 5.2 | 228 | 3.3 | 848.8 | 828.5 | 829.5 | 842.3 | 862.3 | 769.8 | 752.2 | 810.2 | 781 | 771.4 | 88.1 | 179.2 | 252.4 | 219.5 | 352.3 | 333.7 | 232.1 | 297.2 | 409.1 | 235.7
906 | 732 | 567.8 | 227.12 | 265.4902 | 363.3 | 315.7 | 319.6 | 308.9 | 630.9 | 45.2 | 19.7 | 83.5 | 5.6 | 220.5 | 3.5 | 848.2 | 831.2 | 825.4 | 841.9 | 862.7 | 769.8 | 755.5 | 813.3 | 781.1 | 773.5 | 88.3 | 179.4 | 252.6 | 219.8 | 352.3 | 333.6 | 232.4 | 297.2 | 409.4 | 235.9
907 | 733 | 567.3 | 226.92 | 265.2564 | 363.2 | 316.2 | 320.1 | 308.5 | 624.1 | 45.3 | 19.7 | 83.6 | 5.6 | 210.6 | 3.4 | 847.7 | 833.5 | 825.5 | 841.5 | 863 | 769.9 | 760.3 | 814.6 | 781.2 | 775.3 | 88.5 | 179.7 | 252.8 | 220.1 | 352.1 | 333.7 | 232.7 | 297.4 | 409.6 | 236.2
908 | 734 | 568.3 | 227.32 | 265.724 | 362.9 | 316.5 | 321 | 307.9 | 622 | 45.3 | 19.7 | 83.6 | 5.2 | 207.8 | 3.6 | 847 | 830.1 | 825.6 | 840.3 | 863.3 | 770.3 | 762.6 | 817.5 | 781.3 | 777.3 | 88.8 | 180 | 253 | 220.4 | 352 | 333.9 | 232.9 | 297.6 | 409.8 | 236.5
909 | 735 | 568.1 | 227.24 | 265.6305 | 362.7 | 317.1 | 322.5 | 307.3 | 627.4 | 45.3 | 19.7 | 83.5 | 5.6 | 223.6 | 3.4 | 846.8 | 834.3 | 825.2 | 840.3 | 863.7 | 770.6 | 756 | 816.2 | 781.4 | 778.4 | 89 | 180.3 | 253.4 | 220.7 | 352 | 334.2 | 233.1 | 297.8 | 410.1 | 236.8
910 | 736 | 568.7 | 227.48 | 265.911 | 362.4 | 318 | 323.3 | 307.6 | 626.6 | 45.4 | 19.7 | 83.5 | 5.2 | 216.6 | 3.2 | 846.7 | 834.6 | 827.6 | 840.4 | 864.8 | 770.9 | 750.3 | 814.6 | 781.6 | 778 | 89.2 | 180.6 | 253.5 | 221 | 351.9 | 334.2 | 233.4 | 298 | 410.3 | 237
911 | 737 | 568.7 | 227.48 | 265.911 | 361.9 | 318.4 | 324.2 | 307.3 | 622.9 | 45.5 | 19.7 | 83.4 | 4.8 | 209.7 | 3.1 | 846.3 | 831.6 | 829.3 | 839.9 | 865.4 | 770.8 | 756 | 816.5 | 781.6 | 778.7 | 89.4 | 180.9 | 253.7 | 221.3 | 351.8 | 334.5 | 233.6 | 298.1 | 410.5 | 237.3
912 | 738 | 566.1 | 226.44 | 264.6953 | 361.8 | 318.6 | 324.4 | 306.6 | 610.2 | 45.5 | 19.7 | 83.4 | 4.7 | 210.7 | 3.2 | 846 | 830.8 | 829 | 839.8 | 865 | 771.2 | 766.2 | 817.7 | 781.9 | 779.9 | 89.6 | 181.2 | 253.9 | 221.7 | 352.1 | 334.7 | 233.8 | 298.2 | 410.8 | 237.5
913 | 739 | 566.6 | 226.64 | 264.9291 | 362.1 | 319.2 | 324.7 | 307.2 | 600.1 | 45.4 | 19.7 | 83.3 | 4.7 | 211.3 | 2.9 | 845.8 | 829.7 | 831 | 839.7 | 865 | 771.6 | 771.9 | 819.9 | 782.3 | 780.4 | 89.8 | 181.5 | 254.2 | 222 | 352 | 335 | 233.9 | 298.4 | 411.1 | 237.8
914 | 740 | 566.3 | 226.52 | 264.7888 | 362.8 | 320.4 | 325.1 | 308.5 | 586.8 | 45.3 | 19.7 | 83.3 | 5 | 211.7 | 2.6 | 845.7 | 831.4 | 833 | 841 | 864.1 | 772 | 773 | 819.9 | 782.6 | 779.1 | 90 | 181.8 | 254.4 | 222.3 | 352.1 | 335.2 | 234.1 | 298.6 | 411.5 | 238.1
915 | 741 | 566.7 | 226.68 | 264.9759 | 362.4 | 321.6 | 325 | 308.9 | 574.4 | 45.3 | 19.7 | 83.4 | 5 | 218.9 | 2.4 | 845.7 | 829.5 | 834.9 | 841.8 | 863.7 | 772.5 | 770.9 | 818.7 | 782.8 | 777.4 | 90.3 | 182.1 | 254.6 | 222.6 | 352.3 | 335.3 | 234.2 | 298.7 | 411.9 | 238.3
916 | 742 | 568.1 | 227.24 | 265.6305 | 361.8 | 322 | 324.3 | 308 | 562.7 | 45.3 | 19.7 | 83.6 | 5.5 | 237.1 | 2.3 | 845.7 | 829.2 | 833.5 | 841.3 | 865.5 | 772.6 | 779.1 | 821 | 782.9 | 778.7 | 90.5 | 182.4 | 254.7 | 222.9 | 352.3 | 335.5 | 234.5 | 298.9 | 412.3 | 238.6
917 | 743 | 566.5 | 226.6 | 264.8823 | 361.6 | 322.3 | 323.9 | 307.4 | 553.8 | 45.4 | 19.7 | 83.7 | 5.2 | 244.6 | 2.7 | 845.8 | 832.8 | 832.4 | 842.1 | 865.7 | 772.9 | 783.9 | 821.2 | 783.2 | 778.7 | 90.7 | 182.7 | 254.9 | 223.2 | 352.6 | 335.5 | 234.7 | 299.1 | 412.6 | 238.9
918 | 744 | 566.4 | 226.56 | 264.8356 | 361.9 | 323.1 | 323.8 | 307.9 | 550.9 | 45.4 | 19.7 | 83.8 | 5.1 | 241.9 | 3 | 845.7 | 830.5 | 831.7 | 841.7 | 865.2 | 772.9 | 789 | 820.2 | 783.4 | 779.1 | 90.9 | 183 | 255.1 | 223.5 | 352.4 | 335.4 | 235 | 299.2 | 412.9 | 239.1
919 | 745 | 566.9 | 226.76 | 265.0694 | 363.1 | 323.7 | 323.9 | 307.7 | 558.4 | 45.3 | 19.7 | 84 | 5 | 241.3 | 3.1 | 845.8 | 834.3 | 831.4 | 842.3 | 864.3 | 772.9 | 793 | 820.9 | 783.6 | 781.2 | 91.1 | 183.2 | 255.4 | 223.9 | 352.2 | 335.5 | 235.2 | 299.3 | 413.2 | 239.4
920 | 746 | 568.2 | 227.28 | 265.6772 | 363.2 | 323.8 | 323.9 | 307 | 552 | 45.2 | 19.7 | 84.1 | 4.9 | 240.4 | 3.2 | 846 | 832.8 | 831.8 | 842.4 | 865 | 773.1 | 798.5 | 820.8 | 783.7 | 782 | 91.3 | 183.5 | 255.5 | 224.2 | 352 | 335.6 | 235.4 | 299.5 | 413.4 | 239.7
921 | 747 | 568.1 | 227.24 | 265.6305 | 362.9 | 324.2 | 323.9 | 307.5 | 555.1 | 45.2 | 19.7 | 84.2 | 4.9 | 239.4 | 3.3 | 846 | 832 | 831 | 842.1 | 865.1 | 773.2 | 802.5 | 821.6 | 783.8 | 782.1 | 91.6 | 183.8 | 255.8 | 224.5 | 352.2 | 335.8 | 235.7 | 299.6 | 413.6 | 239.9
922 | 748 | 567.7 | 227.08 | 265.4434 | 363.3 | 323.9 | 324.3 | 307.7 | 549.2 | 45.1 | 19.7 | 84.3 | 5.5 | 238.6 | 3.6 | 846.1 | 834.5 | 830.6 | 842.3 | 866.3 | 773.5 | 805.3 | 823.3 | 783.8 | 782.6 | 91.8 | 184.1 | 256 | 224.8 | 352.5 | 336.7 | 236 | 299.7 | 413.9 | 240.2
923 | 749 | 567.3 | 226.92 | 265.2564 | 364.3 | 323.7 | 324.3 | 306.8 | 547.2 | 45.1 | 19.7 | 84.3 | 5.3 | 237.3 | 3.8 | 845.8 | 835.4 | 827 | 842.3 | 866.6 | 773.5 | 804.7 | 826 | 784 | 784.7 | 92 | 184.4 | 256.2 | 225.1 | 352.6 | 337.7 | 236.4 | 300.1 | 414.2 | 240.4
924 | 750 | 566 | 226.4 | 264.6486 | 365.1 | 323.6 | 324.3 | 306.8 | 543.4 | 45.1 | 19.7 | 84.3 | 5.8 | 233.8 | 3.8 | 845.3 | 838.5 | 822.8 | 842.3 | 866.8 | 773.5 | 807 | 824.3 | 784.2 | 785.6 | 92.2 | 184.7 | 256.4 | 225.4 | 353.2 | 338.1 | 236.7 | 300.2 | 414.4 | 240.7
925 | 751 | 567 | 226.8 | 265.1161 | 365.2 | 322.4 | 325.1 | 307.2 | 539.7 | 45.1 | 19.7 | 84.3 | 5.8 | 233.8 | 4 | 845 | 840.3 | 820.5 | 842.2 | 866.8 | 773.7 | 805.3 | 823.3 | 784.3 | 786 | 92.4 | 184.9 | 256.6 | 225.7 | 353.6 | 338.4 | 237 | 300.4 | 414.6 | 241
926 | 752 | 564.9 | 225.96 | 264.1342 | 365.8 | 321.7 | 326.1 | 307.3 | 530.5 | 45.1 | 19.7 | 84.4 | 5.9 | 241.7 | 4 | 844.6 | 841.1 | 819.2 | 841.2 | 866.2 | 773.6 | 806.1 | 824.8 | 784.4 | 786.9 | 92.6 | 185.2 | 256.8 | 226 | 353.6 | 338.7 | 237.2 | 300.7 | 414.7 | 241.2
927 | 753 | 564 | 225.6 | 263.7134 | 365.5 | 321.1 | 326.6 | 307.4 | 543.8 | 45.2 | 19.7 | 84.6 | 5.6 | 246.2 | 4.1 | 844.3 | 839.8 | 820.5 | 840.7 | 866.3 | 773.5 | 796.8 | 823.6 | 784.6 | 788 | 92.8 | 185.5 | 257.1 | 226.4 | 353.6 | 338.9 | 237.4 | 300.8 | 414.9 | 241.5
928 | 754 | 563.6 | 225.44 | 263.5264 | 366 | 319.6 | 327.3 | 307.9 | 562.9 | 45.3 | 19.7 | 84.7 | 5.4 | 245.6 | 4.1 | 843.9 | 836.7 | 821.4 | 840.1 | 867.5 | 773.6 | 800 | 825.1 | 785 | 788.4 | 93.1 | 185.8 | 257.5 | 226.7 | 353.8 | 338.9 | 237.7 | 300.9 | 415 | 241.8
929 | 755 | 564.3 | 225.72 | 263.8537 | 365.3 | 319.5 | 327.6 | 307.1 | 575 | 45.4 | 19.7 | 85 | 5.1 | 243.2 | 4 | 843.7 | 834.3 | 823.7 | 839.7 | 867.2 | 773.7 | 801.2 | 825.5 | 785.3 | 788.9 | 93.3 | 186.1 | 257.7 | 227 | 354.2 | 339 | 238 | 301 | 415.3 | 242
930 | 756 | 564.4 | 225.76 | 263.9004 | 364.8 | 319.5 | 327.1 | 306.7 | 588.3 | 45.5 | 19.7 | 85.1 | 5 | 235.4 | 3.8 | 843.6 | 832 | 825.9 | 839.3 | 868.5 | 773.9 | 800.5 | 826 | 785.5 | 788.6 | 93.5 | 186.3 | 257.9 | 227.3 | 354.2 | 339.5 | 238.2 | 301.1 | 415.6 | 242.3
931 | 757 | 563.1 | 225.24 | 263.2926 | 364.9 | 319.2 | 326.9 | 306.1 | 588.8 | 45.5 | 19.7 | 85.2 | 4.7 | 224.1 | 3.5 | 843.5 | 830 | 827.2 | 839 | 869.6 | 774.2 | 804.4 | 826.1 | 785.8 | 789.1 | 93.7 | 186.6 | 258.2 | 227.6 | 354.2 | 340.3 | 238.5 | 301.4 | 415.9 | 242.6
932 | 758 | 564.3 | 225.72 | 263.8537 | 364.8 | 319.1 | 327.8 | 305.7 | 580.2 | 45.6 | 19.7 | 85.3 | 5.3 | 207.7 | 3.2 | 843.2 | 834.5 | 824.7 | 839.6 | 871.2 | 774.8 | 801.5 | 823.4 | 786 | 789.1 | 93.9 | 186.9 | 258.3 | 227.9 | 354.3 | 340.9 | 238.7 | 301.6 | 416.2 | 242.9
933 | 759 | 565.5 | 226.2 | 264.4148 | 364.9 | 318.8 | 327.3 | 305.8 | 566.3 | 45.7 | 19.7 | 85.4 | 5.6 | 199.8 | 2.9 | 843 | 840.8 | 823.1 | 839.9 | 871.9 | 775.7 | 795 | 819.5 | 786.4 | 788.6 | 94.1 | 187.2 | 258.4 | 228.3 | 354.3 | 341.2 | 238.9 | 301.9 | 416.5 | 243.1
934 | 760 | 566.2 | 226.48 | 264.7421 | 365.8 | 318.2 | 326.9 | 306.4 | 553.6 | 45.8 | 19.7 | 85.4 | 5.8 | 212.1 | 2.7 | 842.6 | 842.3 | 824.4 | 839.3 | 871.8 | 776.1 | 793.2 | 821.7 | 786.7 | 787.6 | 94.3 | 187.5 | 258.5 | 228.6 | 354.5 | 341.5 | 239.2 | 302.1 | 416.6 | 243.4
935 | 761 | 567 | 226.8 | 265.1161 | 367.4 | 317.7 | 327.6 | 307.7 | 539.8 | 45.9 | 19.7 | 85.4 | 5.4 | 233.7 | 2.6 | 842.2 | 838 | 826.4 | 838.6 | 872.2 | 776 | 793.9 | 820.4 | 786.8 | 787 | 94.5 | 187.8 | 258.7 | 228.9 | 354.4 | 341.8 | 239.4 | 302.3 | 416.7 | 243.7
936 | 762 | 566.3 | 226.52 | 264.7888 | 368.1 | 317.4 | 328.1 | 307.9 | 539.3 | 46 | 19.7 | 85.4 | 5.7 | 239.3 | 2.7 | 841.9 | 836.7 | 827.2 | 838 | 872.7 | 775.8 | 794.6 | 820.1 | 786.9 | 787.2 | 94.8 | 188 | 258.9 | 229.2 | 354.5 | 342.2 | 239.5 | 302.5 | 416.9 | 243.9
937 | 763 | 566.2 | 226.48 | 264.7421 | 368.8 | 317.2 | 328.5 | 307.4 | 551.7 | 46.1 | 19.7 | 85.4 | 6.3 | 234 | 2.9 | 841.6 | 840.8 | 823.4 | 838 | 871.4 | 775.7 | 783.8 | 815.6 | 787 | 786.6 | 95 | 188.3 | 259.4 | 229.5 | 354.7 | 342.6 | 239.9 | 302.7 | 417.2 | 244.2
938 | 764 | 564.7 | 225.88 | 264.0407 | 368.8 | 316.9 | 327.5 | 307 | 573.2 | 46.1 | 19.6 | 85.5 | 5.9 | 212.9 | 3.1 | 841.4 | 848 | 821.8 | 839.1 | 871.2 | 775.9 | 769 | 808.6 | 787.2 | 785.5 | 95.2 | 188.6 | 259.8 | 229.8 | 354.7 | 342.5 | 240.2 | 302.8 | 417.4 | 244.4
939 | 765 | 565.7 | 226.28 | 264.5083 | 369 | 316.8 | 326.5 | 307.5 | 579.1 | 46.2 | 19.6 | 85.6 | 5.7 | 213.7 | 4 | 841.2 | 848.6 | 822 | 839.3 | 868.3 | 776.1 | 757.9 | 800.9 | 787.4 | 785.3 | 95.4 | 188.9 | 259.9 | 230.1 | 354.5 | 342.3 | 240.4 | 302.9 | 417.6 | 244.7
940 | 766 | 565.6 | 226.24 | 264.4615 | 369.9 | 316.7 | 326.1 | 308 | 579.2 | 46.2 | 19.6 | 85.7 | 5.4 | 214.6 | 4.4 | 840.9 | 844.1 | 823 | 838.7 | 868.3 | 776.3 | 744.7 | 790.7 | 787.6 | 782.5 | 95.6 | 189.1 | 260.2 | 230.4 | 354.6 | 342.4 | 240.5 | 303 | 417.7 | 245
941 | 767 | 564.4 | 225.76 | 263.9004 | 370.8 | 317 | 325.4 | 308 | 579.3 | 46.2 | 19.6 | 85.7 | 4.7 | 224.7 | 4.3 | 840.5 | 838.2 | 820.7 | 837.9 | 866.3 | 776.4 | 734.9 | 784.3 | 787.9 | 781.7 | 95.8 | 189.4 | 260.4 | 230.7 | 354.4 | 342.2 | 240.6 | 303.1 | 417.9 | 245.2
942 | 768 | 565.8 | 226.32 | 264.555 | 370.9 | 317.1 | 325.8 | 308.3 | 581.7 | 46.3 | 19.6 | 85.8 | 5.1 | 245.6 | 4.5 | 840.2 | 835 | 819.2 | 837.5 | 863.8 | 776.1 | 728.1 | 784 | 788.2 | 780.7 | 96 | 189.7 | 260.8 | 231 | 354.2 | 341.8 | 240.7 | 303.2 | 418 | 245.5
943 | 769 | 566 | 226.4 | 264.6486 | 371.8 | 317.6 | 325.8 | 308.2 | 608 | 46.4 | 19.6 | 85.8 | 5 | 236 | 4.2 | 840.1 | 831.3 | 818.2 | 837.3 | 863.3 | 775.8 | 719 | 783.4 | 788.5 | 779.5 | 96.3 | 190 | 261.3 | 231.3 | 354.3 | 341.4 | 241 | 303.2 | 418.2 | 245.7
944 | 770 | 566.5 | 226.6 | 264.8823 | 371.7 | 318.5 | 325.7 | 308.8 | 627 | 46.4 | 19.6 | 85.8 | 5.4 | 221.9 | 3.6 | 839.7 | 828.2 | 816.6 | 836.6 | 860.4 | 775.7 | 712.5 | 781.9 | 788.7 | 778.8 | 96.5 | 190.2 | 261.6 | 231.6 | 354.5 | 341 | 241.3 | 303.2 | 418.4 | 246
945 | 771 | 566.7 | 226.68 | 264.9759 | 372.6 | 319.4 | 324.9 | 309.9 | 635.4 | 46.5 | 19.6 | 86 | 5.6 | 230.3 | 3.4 | 839.5 | 817.7 | 810.4 | 836 | 856.4 | 776.2 | 695.4 | 767.9 | 789 | 776.3 | 96.7 | 190.5 | 262.2 | 231.9 | 355.2 | 340.7 | 241.6 | 303.3 | 418.7 | 246.2
946 | 772 | 566.9 | 226.76 | 265.0694 | 371.9 | 319.3 | 325.4 | 310.8 | 644.9 | 46.6 | 19.6 | 86.1 | 5.1 | 240.7 | 3.9 | 839.4 | 816.5 | 809.8 | 836.4 | 855.5 | 776.3 | 690.7 | 771.4 | 789.2 | 775.9 | 96.9 | 190.8 | 262.3 | 232.1 | 355.4 | 340.5 | 241.7 | 303.4 | 418.9 | 246.5
947 | 773 | 567.1 | 226.84 | 265.1629 | 372.2 | 319.4 | 326.3 | 311.3 | 645.7 | 46.7 | 19.6 | 86 | 5.4 | 237.4 | 4.4 | 838.9 | 815.1 | 807.5 | 835.7 | 854.6 | 776.2 | 684.9 | 768.1 | 789.3 | 775.8 | 97.1 | 191.1 | 262.6 | 232.4 | 355.9 | 340.5 | 242.1 | 303.6 | 419 | 246.8
948 | 774 | 566.8 | 226.72 | 265.0226 | 371.8 | 320.4 | 325.7 | 312.2 | 651.9 | 46.8 | 19.6 | 86 | 4.9 | 244.7 | 4.8 | 838.3 | 820.3 | 809 | 835.7 | 856.2 | 776.3 | 688.5 | 775.5 | 789.7 | 776.7 | 97.3 | 191.3 | 262.9 | 232.7 | 356.2 | 340.8 | 242.4 | 303.8 | 419.2 | 247.1
949 | 775 | 567.3 | 226.92 | 265.2564 | 370.9 | 321 | 326.8 | 313 | 651 | 46.9 | 19.6 | 86 | 5.1 | 249.4 | 5.4 | 837.9 | 823.9 | 814.1 | 835.5 | 857.2 | 776 | 695.2 | 784.9 | 790 | 778.1 | 97.6 | 191.6 | 263.2 | 233 | 356.4 | 341 | 242.7 | 303.9 | 419.4 | 247.4
950 | 776 | 567.4 | 226.96 | 265.3032 | 370.8 | 321.2 | 327.7 | 314.2 | 658.9 | 47 | 19.6 | 85.8 | 5.4 | 253.7 | 5.1 | 837.8 | 825.9 | 818 | 835.4 | 857.3 | 775.7 | 704.5 | 792 | 790.1 | 779.5 | 97.8 | 191.9 | 263.4 | 233.4 | 356.7 | 341.1 | 243 | 304.1 | 419.6 | 247.6
951 | 777 | 567 | 226.8 | 265.1161 | 370.7 | 321.7 | 327.7 | 314.7 | 660.8 | 47 | 19.6 | 85.7 | 5.3 | 241.2 | 4.9 | 837.7 | 826.7 | 821.1 | 835.3 | 858.6 | 775.3 | 714.4 | 797 | 790.1 | 780.4 | 98 | 192.1 | 263.8 | 233.7 | 356.7 | 341.6 | 243.2 | 304.3 | 419.9 | 247.9
952 | 778 | 566.8 | 226.72 | 265.0226 | 371.2 | 321.8 | 327.1 | 314.5 | 650 | 47.1 | 19.6 | 85.6 | 5 | 213 | 4.8 | 837.6 | 828.5 | 824 | 835.5 | 857.3 | 774.7 | 729.6 | 801.5 | 790.4 | 780.6 | 98.2 | 192.4 | 263.8 | 234 | 356.2 | 342.3 | 243.4 | 304.5 | 420.2 | 248.2
953 | 779 | 567 | 226.8 | 265.1161 | 370.9 | 322.3 | 327.6 | 314.6 | 631.8 | 47.1 | 19.6 | 85.7 | 5 | 203 | 4.4 | 837.6 | 832.4 | 824.9 | 836.4 | 858.5 | 774.1 | 739.4 | 802.8 | 790.7 | 779.9 | 98.4 | 192.7 | 263.8 | 234.3 | 356 | 342.6 | 243.6 | 304.8 | 420.4 | 248.4
954 | 780 | 566.8 | 226.72 | 265.0226 | 370.7 | 321.3 | 326.8 | 314.5 | 618.4 | 47.1 | 19.6 | 85.9 | 5.4 | 225 | 4.3 | 837.5 | 838.2 | 823.2 | 836.4 | 859.5 | 773.4 | 739.3 | 798.8 | 791.1 | 779.8 | 98.7 | 192.9 | 263.9 | 234.7 | 355.7 | 342.5 | 243.8 | 304.9 | 420.6 | 248.7
955 | 781 | 566.6 | 226.64 | 264.9291 | 369.5 | 320.3 | 326.1 | 313.3 | 600.1 | 47 | 19.6 | 86 | 5.4 | 217 | 4.3 | 837.5 | 838.3 | 823.6 | 835.8 | 860.2 | 772.4 | 750.4 | 805.3 | 791.5 | 781 | 98.9 | 193.2 | 264.1 | 235 | 355.4 | 342.2 | 243.9 | 305 | 420.7 | 248.9
956 | 782 | 566.9 | 226.76 | 265.0694 | 368.8 | 320.2 | 325.3 | 312.3 | 597.7 | 46.9 | 19.6 | 85.9 | 4.6 | 206.5 | 4.2 | 837.6 | 836.7 | 824.3 | 835.9 | 861.6 | 771.8 | 758.7 | 808.5 | 791.8 | 782 | 99.1 | 193.5 | 264.4 | 235.3 | 355.3 | 341.8 | 244.2 | 305 | 420.9 | 249.2
957 | 783 | 566.4 | 226.56 | 264.8356 | 367.8 | 321.2 | 324.5 | 311.6 | 600.9 | 46.8 | 19.6 | 85.8 | 4.7 | 220.2 | 4.2 | 837.8 | 836.3 | 824.5 | 835.9 | 862.1 | 771.4 | 764.7 | 809.4 | 792.1 | 782.7 | 99.3 | 193.7 | 264.7 | 235.6 | 355.3 | 341.4 | 244.6 | 305.1 | 421.1 | 249.4
958 | 784 | 566.3 | 226.52 | 264.7888 | 366.4 | 322.3 | 324.4 | 310.5 | 608.6 | 46.7 | 19.6 | 85.8 | 4.9 | 227.4 | 4.1 | 837.9 | 838.5 | 825.6 | 836 | 863 | 771.2 | 765.5 | 810.5 | 792.3 | 783.6 | 99.5 | 194 | 264.9 | 235.9 | 355.3 | 341.3 | 244.8 | 305.2 | 421.4 | 249.7
959 | 785 | 566.7 | 226.68 | 264.9759 | 365 | 323.2 | 324.5 | 310 | 612.9 | 46.7 | 19.6 | 85.8 | 4.5 | 218.8 | 3.6 | 838 | 838.6 | 825.3 | 836.4 | 863.8 | 771.2 | 769.7 | 811.6 | 792.6 | 786 | 99.7 | 194.3 | 265.1 | 236.2 | 355.4 | 341.1 | 245 | 305.3 | 421.7 | 249.9
960 | 786 | 566.6 | 226.64 | 264.9291 | 364.3 | 323.9 | 324.2 | 310.3 | 623.6 | 46.7 | 19.6 | 85.7 | 4.9 | 215.1 | 3.1 | 838.1 | 835.4 | 825.9 | 836.4 | 864.5 | 771.2 | 769.5 | 813.1 | 792.9 | 786.5 | 100 | 194.5 | 265.4 | 236.5 | 355.3 | 340.9 | 245.1 | 305.4 | 422 | 250.2
961 | 787 | 566.9 | 226.76 | 265.0694 | 363.4 | 324 | 323.8 | 310.3 | 630.6 | 46.7 | 19.6 | 85.7 | 4.8 | 210.8 | 3 | 838.1 | 831.5 | 826 | 835.9 | 864.3 | 771.3 | 777.1 | 813.1 | 793.2 | 785.5 | 100.2 | 194.8 | 265.6 | 236.8 | 355.1 | 340.7 | 245.4 | 305.5 | 422.3 | 250.4
962 | 788 | 567.5 | 227 | 265.3499 | 363.2 | 325.2 | 324.2 | 309.3 | 633 | 46.7 | 19.6 | 85.7 | 5.3 | 210.5 | 3.6 | 838.1 | 832.5 | 826.7 | 836 | 863 | 771.6 | 774.9 | 812.5 | 793.3 | 784.4 | 100.4 | 195.1 | 266.2 | 237.1 | 355.2 | 340.5 | 245.6 | 305.6 | 422.6 | 250.7
963 | 789 | 566.6 | 226.64 | 264.9291 | 362.2 | 326.4 | 324.6 | 308.6 | 651.3 | 46.8 | 19.6 | 85.7 | 5.6 | 204.3 | 4.9 | 838.1 | 833.2 | 826.8 | 836.5 | 860.6 | 772.1 | 764.9 | 806.3 | 793.6 | 782.4 | 100.6 | 195.3 | 266.8 | 237.3 | 355.3 | 340.3 | 245.8 | 305.7 | 423 | 250.9
964 | 790 | 567.3 | 226.92 | 265.2564 | 361 | 327.7 | 325.1 | 309 | 658.1 | 46.8 | 19.6 | 85.7 | 5.4 | 198.9 | 5.5 | 838.1 | 835.5 | 826.9 | 836.5 | 860 | 772.2 | 752.2 | 803.1 | 794 | 781.4 | 100.8 | 195.6 | 267.1 | 237.6 | 355.3 | 340.2 | 246.1 | 305.8 | 423.3 | 251.2
965 | 791 | 567.4 | 226.96 | 265.3032 | 360.1 | 329.3 | 325.8 | 309.2 | 657.7 | 46.8 | 19.6 | 85.6 | 5.8 | 210.6 | 5.6 | 837.9 | 836.1 | 826.2 | 836.4 | 859.2 | 771.7 | 749 | 803.1 | 794.5 | 780 | 101.1 | 195.9 | 267.2 | 237.9 | 355.3 | 340 | 246.4 | 305.9 | 423.5 | 251.4
966 | 792 | 567.6 | 227.04 | 265.3967 | 359.8 | 330.4 | 325.2 | 308.5 | 654.8 | 46.8 | 19.6 | 85.4 | 5.9 | 219.2 | 5.5 | 837.7 | 833.7 | 827.6 | 836.4 | 859.9 | 771.3 | 758.3 | 807.8 | 794.8 | 780 | 101.3 | 196.1 | 267.4 | 238.2 | 355.7 | 340.1 | 246.7 | 306 | 423.8 | 251.7
967 | 793 | 567.2 | 226.88 | 265.2096 | 359.6 | 331.2 | 324.4 | 308 | 638.3 | 46.8 | 19.6 | 85.3 | 5.9 | 202.7 | 5.3 | 837.5 | 833 | 829 | 836.2 | 859.1 | 771.3 | 762.9 | 808.3 | 794.9 | 779.7 | 101.5 | 196.4 | 267.5 | 238.5 | 355.9 | 340.2 | 246.9 | 306.1 | 424.2 | 251.9
968 | 794 | 567.7 | 227.08 | 265.4434 | 359.8 | 331.6 | 323.5 | 307.5 | 621.3 | 46.9 | 19.6 | 85.2 | 5.6 | 191.1 | 5 | 837.5 | 836.3 | 829.4 | 836.8 | 858.8 | 771 | 762.1 | 810.1 | 795 | 778.6 | 101.7 | 196.7 | 267.6 | 238.8 | 355.7 | 340.2 | 247.2 | 306.3 | 424.5 | 252.2
969 | 795 | 565.4 | 226.16 | 264.368 | 360.7 | 331.7 | 322 | 306.8 | 607.7 | 46.9 | 19.6 | 85.2 | 5.5 | 201.9 | 4.6 | 837.3 | 835.8 | 830.2 | 836.8 | 860.3 | 770.3 | 764.6 | 812.4 | 795.1 | 778.3 | 101.9 | 196.9 | 267.7 | 239.1 | 355.3 | 340.1 | 247.4 | 306.4 | 424.7 | 252.4
970 | 796 | 566.1 | 226.44 | 264.6953 | 361.4 | 331.9 | 321.5 | 306.1 | 610.2 | 46.9 | 19.6 | 85.4 | 4.9 | 205.4 | 4.5 | 837.2 | 838.3 | 828.5 | 836.7 | 861.3 | 769.7 | 757.8 | 810 | 795.1 | 779.1 | 102.1 | 197.2 | 268.1 | 239.4 | 355 | 339.9 | 247.6 | 306.5 | 424.9 | 252.7
971 | 797 | 566.1 | 226.44 | 264.6953 | 361.6 | 332.3 | 321.6 | 305.5 | 619.9 | 46.9 | 19.6 | 85.5 | 4.7 | 206.4 | 4.8 | 837.1 | 840.6 | 825.8 | 837.6 | 861.9 | 769.4 | 760.3 | 814 | 795.2 | 780.6 | 102.3 | 197.5 | 268.3 | 239.7 | 355 | 339.8 | 247.8 | 306.6 | 425 | 252.9
972 | 798 | 565.7 | 226.28 | 264.5083 | 361.2 | 332.4 | 320.1 | 305.1 | 617.2 | 46.9 | 19.6 | 85.8 | 5.8 | 204.8 | 5 | 837.1 | 841.6 | 826.5 | 837.6 | 862.4 | 769.4 | 769.4 | 818.8 | 795.4 | 781.2 | 102.6 | 197.7 | 268.4 | 239.9 | 355.1 | 339.9 | 248 | 306.7 | 425.2 | 253.1
973 | 799 | 566 | 226.4 | 264.6486 | 361 | 333.2 | 319.1 | 305.4 | 620.1 | 46.7 | 19.6 | 86.2 | 5.7 | 186.5 | 4.9 | 837.1 | 841.2 | 825.6 | 837.8 | 864.3 | 769.7 | 767.5 | 818.5 | 795.5 | 782.7 | 102.8 | 198 | 268.7 | 240.2 | 355.2 | 340 | 248.2 | 306.8 | 425.4 | 253.4
974 | 800 | 568.7 | 227.48 | 265.911 | 360.4 | 333.2 | 318.1 | 305.8 | 630.1 | 46.6 | 19.6 | 86.4 | 5.8 | 203.1 | 5.4 | 837 | 840.6 | 823.2 | 836.9 | 864.1 | 769.7 | 769.6 | 814 | 795.6 | 783.4 | 103 | 198.2 | 269 | 240.4 | 355.6 | 339.7 | 248.4 | 306.8 | 425.7 | 253.6
975 | 801 | 570.4 | 228.16 | 266.7059 | 360.1 | 332.6 | 318.4 | 305.3 | 635.2 | 46.5 | 19.6 | 86.6 | 5.5 | 214.8 | 5.7 | 836.8 | 840.5 | 823 | 836.3 | 864.7 | 770.1 | 767.6 | 809.7 | 796 | 783.3 | 103.2 | 198.5 | 269.2 | 240.7 | 355.7 | 339.8 | 248.7 | 306.9 | 425.9 | 253.9
976 | 802 | 570.3 | 228.12 | 266.6591 | 360.4 | 332.6 | 318.8 | 304.9 | 632.9 | 46.5 | 19.6 | 86.7 | 5.6 | 200.8 | 6 | 836.7 | 837.4 | 823.1 | 836 | 864.3 | 770.1 | 778.9 | 813 | 796.2 | 785.2 | 103.4 | 198.7 | 269.4 | 240.9 | 356.1 | 339.9 | 249 | 307.1 | 426.1 | 254.1
977 | 803 | 568.3 | 227.32 | 265.724 | 361 | 332.7 | 319.2 | 304.7 | 625.8 | 46.5 | 19.6 | 86.7 | 5.3 | 198.9 | 6.2 | 836.6 | 834.8 | 823.9 | 835.6 | 864.8 | 770.3 | 782 | 816.9 | 796.3 | 785.8 | 103.7 | 199 | 269.8 | 241.1 | 356.5 | 340 | 249.3 | 307.2 | 426.5 | 254.4
978 | 804 | 568.5 | 227.4 | 265.8175 | 361.4 | 333.1 | 318.8 | 305.5 | 630.2 | 46.6 | 19.6 | 86.7 | 4.8 | 223.2 | 5.7 | 836.4 | 831.9 | 824.6 | 834.8 | 864.4 | 770.6 | 787.5 | 819 | 796.4 | 787.3 | 103.9 | 199.3 | 270.1 | 241.3 | 356.7 | 340.3 | 249.7 | 307.3 | 426.9 | 254.6
979 | 805 | 567.8 | 227.12 | 265.4902 | 361.6 | 333 | 320.1 | 306 | 625.7 | 46.6 | 19.5 | 86.7 | 4.7 | 251.8 | 5.6 | 836.1 | 829.4 | 824.5 | 834.3 | 862.9 | 770.9 | 796.3 | 822.3 | 796.5 | 788.6 | 104.1 | 199.5 | 270.3 | 241.6 | 357.2 | 340.7 | 250 | 307.5 | 427.1 | 254.9
980 | 806 | 567.5 | 227 | 265.3499 | 361.3 | 333.2 | 320.8 | 306.2 | 609.1 | 46.6 | 19.5 | 86.6 | 5.7 | 228.3 | 5.3 | 835.8 | 829.3 | 826.3 | 836 | 860.2 | 771.6 | 800.7 | 826.4 | 796.8 | 787.7 | 104.3 | 199.8 | 270.5 | 241.8 | 357.5 | 341.2 | 250.2 | 307.7 | 427.4 | 255.2
981 | 807 | 567.4 | 226.96 | 265.3032 | 361.2 | 333.7 | 322.5 | 307.2 | 601.6 | 46.6 | 19.5 | 86.6 | 5.5 | 220.6 | 5.6 | 835.8 | 828.8 | 827 | 836.4 | 859.1 | 771.6 | 804.4 | 827.7 | 796.9 | 788.3 | 104.5 | 200 | 270.7 | 242.1 | 357.6 | 341.4 | 250.4 | 307.9 | 427.9 | 255.4
982 | 808 | 566.2 | 226.48 | 264.7421 | 361.3 | 334.4 | 323.9 | 307.2 | 594.5 | 46.6 | 19.5 | 86.5 | 5.3 | 237.4 | 5.2 | 835.6 | 826.2 | 827.3 | 835 | 858.6 | 771.7 | 812.8 | 827.1 | 797 | 789.5 | 104.8 | 200.3 | 270.9 | 242.4 | 358 | 341.7 | 250.7 | 308.1 | 428.3 | 255.7
983 | 809 | 567.1 | 226.84 | 265.1629 | 360.5 | 334.1 | 324.2 | 306.9 | 581.4 | 46.6 | 19.5 | 86.4 | 5.5 | 234.5 | 4.6 | 835.4 | 825.6 | 827.3 | 834.1 | 858.2 | 772 | 815.8 | 826.3 | 797.2 | 789.5 | 105 | 200.5 | 271.1 | 242.7 | 358.3 | 342 | 251 | 308.4 | 428.6 | 256
984 | 810 | 567.9 | 227.16 | 265.537 | 359.5 | 333.4 | 325 | 307.8 | 571.2 | 46.7 | 19.5 | 86.4 | 5.7 | 197.9 | 4.5 | 835.1 | 824.4 | 827.3 | 833.2 | 858.3 | 772.1 | 819 | 825.1 | 797.3 | 789.7 | 105.2 | 200.8 | 271.3 | 243 | 358.7 | 342.3 | 251.2 | 308.6 | 428.9 | 256.2
985 | 811 | 567.8 | 227.12 | 265.4902 | 359.1 | 333.4 | 325 | 308.8 | 564.8 | 46.8 | 19.5 | 86.2 | 5.2 | 190.7 | 3.4 | 834.9 | 823.4 | 826.6 | 832.5 | 859 | 772.3 | 819.3 | 825.9 | 797.4 | 789.8 | 105.4 | 201.1 | 271.5 | 243.4 | 359.1 | 342.5 | 251.5 | 308.8 | 429.3 | 256.5
986 | 812 | 568 | 227.2 | 265.5837 | 359.1 | 333.4 | 325.7 | 309.9 | 572.8 | 46.8 | 19.5 | 86.1 | 5.5 | 213.2 | 2.8 | 834.9 | 825.3 | 825.7 | 832.6 | 859.2 | 772.5 | 819 | 826.1 | 797.5 | 790.9 | 105.6 | 201.3 | 271.8 | 243.8 | 359.4 | 342.6 | 251.7 | 309 | 429.7 | 256.8
987 | 813 | 567.9 | 227.16 | 265.537 | 360.2 | 334 | 326.7 | 310 | 579.3 | 46.9 | 19.5 | 86.2 | 4.9 | 226.6 | 2.5 | 835.1 | 825.7 | 826.2 | 833 | 858.4 | 772.6 | 821.1 | 824.7 | 797.7 | 791.3 | 105.8 | 201.6 | 271.9 | 244.2 | 359.7 | 343.1 | 252 | 309.1 | 430 | 257.1
988 | 814 | 567.6 | 227.04 | 265.3967 | 361 | 334.2 | 327.4 | 309.3 | 585.3 | 47 | 19.5 | 86.1 | 5.2 | 220.4 | 2.5 | 835.1 | 829.5 | 824.8 | 833.3 | 858.7 | 772.5 | 817.7 | 826.5 | 797.8 | 790.5 | 106.1 | 201.8 | 272.1 | 244.5 | 359.8 | 343.3 | 252.2 | 309.3 | 430.3 | 257.3
989 | 815 | 567.4 | 226.96 | 265.3032 | 362.2 | 334 | 326.6 | 309.4 | 583.9 | 47.1 | 19.5 | 85.8 | 4.7 | 212.4 | 2.4 | 835.1 | 832.6 | 824.6 | 833.6 | 858.9 | 772.7 | 813.9 | 826.4 | 798 | 792.2 | 106.3 | 202.1 | 272.3 | 244.8 | 360.4 | 343.4 | 252.5 | 309.4 | 430.6 | 257.6
990 | 816 | 567.3 | 226.92 | 265.2564 | 362 | 334.1 | 326.5 | 309.3 | 604.5 | 47.1 | 19.5 | 85.7 | 5.3 | 212.9 | 2.4 | 835.3 | 834.4 | 825.9 | 834.3 | 858.3 | 773.2 | 800.3 | 825.6 | 798.3 | 791.5 | 106.5 | 202.4 | 272.8 | 245.1 | 360.8 | 343.5 | 252.7 | 309.5 | 430.9 | 257.8
991 | 817 | 567.3 | 226.92 | 265.2564 | 361.9 | 335.2 | 326.2 | 308.6 | 619.1 | 47.2 | 19.5 | 85.8 | 5.2 | 215.1 | 2.7 | 835.6 | 835.4 | 827.8 | 835.6 | 857.9 | 773.2 | 792.1 | 824.5 | 798.7 | 790 | 106.7 | 202.6 | 273.1 | 245.4 | 361.2 | 343.8 | 253 | 309.6 | 431.3 | 258.1
992 | 818 | 569.7 | 227.88 | 266.3786 | 362.4 | 336.4 | 325.5 | 308.6 | 629.1 | 47.2 | 19.5 | 85.9 | 5.1 | 214.9 | 2.8 | 835.8 | 837.3 | 827.5 | 836.8 | 856.7 | 773.5 | 773.6 | 814.8 | 799.2 | 789.2 | 106.9 | 202.9 | 273.3 | 245.7 | 361.7 | 343.7 | 253.3 | 309.7 | 431.7 | 258.4
993 | 819 | 569.4 | 227.76 | 266.2383 | 362.4 | 336.6 | 325.3 | 309.1 | 631.7 | 47.3 | 19.5 | 85.9 | 5.5 | 206.4 | 3.4 | 836.1 | 840.5 | 825.9 | 838 | 856.7 | 774 | 758.9 | 809.4 | 799.8 | 787.1 | 107.1 | 203.2 | 273.5 | 246 | 361.9 | 343.7 | 253.5 | 309.8 | 431.9 | 258.6
994 | 820 | 568.1 | 227.24 | 265.6305 | 362.9 | 336.5 | 324.8 | 308.7 | 634.7 | 47.3 | 19.5 | 86 | 5.4 | 223.8 | 3.5 | 836 | 844.2 | 822.2 | 838.3 | 856.3 | 773.7 | 748.7 | 808 | 800.4 | 788.3 | 107.4 | 203.4 | 273.9 | 246.3 | 362 | 343.7 | 253.8 | 310 | 432.1 | 258.9
995 | 821 | 568.4 | 227.36 | 265.7707 | 363.8 | 335.7 | 323.5 | 309.2 | 636.6 | 47.4 | 19.5 | 86.2 | 5.3 | 231.4 | 3.5 | 835.8 | 841.3 | 822.2 | 837.6 | 857 | 773.8 | 746 | 809.8 | 801 | 788.6 | 107.6 | 203.7 | 274.1 | 246.6 | 362 | 343.7 | 254 | 310.1 | 432.2 | 259.1
996 | 822 | 567.2 | 226.88 | 265.2096 | 364.7 | 335.5 | 322.8 | 310.2 | 640.4 | 47.5 | 19.5 | 86.2 | 5 | 220.1 | 3.8 | 835.7 | 835.2 | 820.5 | 836.4 | 857.7 | 773.6 | 760.5 | 812.7 | 801.4 | 789.3 | 107.8 | 204 | 274.4 | 246.9 | 362.1 | 343.8 | 254.2 | 310.3 | 432.4 | 259.4
997 | 823 | 568.2 | 227.28 | 265.6772 | 365 | 335.9 | 322.4 | 310.5 | 646.2 | 47.5 | 19.5 | 86.2 | 5.6 | 213.8 | 4.1 | 835.5 | 833.4 | 820.8 | 836 | 858.4 | 773.4 | 766.3 | 814.6 | 801.5 | 789.9 | 108 | 204.2 | 274.7 | 247.2 | 362.6 | 343.8 | 254.4 | 310.4 | 432.8 | 259.7
998 | 824 | 567.1 | 226.84 | 265.1629 | 364.7 | 336.1 | 322.7 | 310.9 | 650.6 | 47.6 | 19.5 | 86 | 6.1 | 213.6 | 4.1 | 835.5 | 834.7 | 822.7 | 836.9 | 857.3 | 773.5 | 767.1 | 818.7 | 801.7 | 789.2 | 108.2 | 204.5 | 274.9 | 247.4 | 362.8 | 343.7 | 254.6 | 310.5 | 433.1 | 259.9
999 | 825 | 567.8 | 227.12 | 265.4902 | 364.1 | 336.1 | 323.1 | 311.4 | 629.4 | 47.6 | 19.5 | 85.9 | 6.5 | 213.5 | 4 | 835.5 | 832.9 | 823.2 | 836.1 | 858 | 773.3 | 776.1 | 821 | 801.8 | 790 | 108.4 | 204.8 | 274.9 | 247.7 | 363 | 344.1 | 254.8 | 310.8 | 433.4 | 260.2
1000 | 826 | 568 | 227.2 | 265.5837 | 363.8 | 336.4 | 323.1 | 311.4 | 620.1 | 47.6 | 19.5 | 85.8 | 5.9 | 213.2 | 4.1 | 835.4 | 832.4 | 823.7 | 835.6 | 858.5 | 773.1 | 782.9 | 822.9 | 801.9 | 791 | 108.7 | 205 | 275.1 | 248 | 363.2 | 344.4 | 254.9 | 311 | 433.7 | 260.5
1001 | 827 | 568.1 | 227.24 | 265.6305 | 363.5 | 336.2 | 324.6 | 310.9 | 616.8 | 47.6 | 19.5 | 85.7 | 5.6 | 212.3 | 4.5 | 835.4 | 831 | 824 | 835.7 | 858.4 | 773.2 | 790.7 | 824.8 | 801.9 | 791.5 | 108.9 | 205.3 | 275.3 | 248.3 | 363.1 | 344.7 | 255 | 311.2 | 433.9 | 260.7
1002 | 828 | 567.1 | 226.84 | 265.1629 | 362.9 | 336 | 325.7 | 310.1 | 610.6 | 47.7 | 19.5 | 85.7 | 5.6 | 214.8 | 4.5 | 835.2 | 827.9 | 824.7 | 834.9 | 858 | 773.2 | 799.9 | 825 | 801.8 | 792 | 109.1 | 205.5 | 275.6 | 248.6 | 362.9 | 345 | 255.2 | 311.5 | 434.1 | 261
1003 | 829 | 568 | 227.2 | 265.5837 | 362.1 | 335.9 | 326.4 | 309.8 | 603.4 | 47.8 | 19.5 | 85.8 | 5.2 | 220.3 | 4.2 | 835.1 | 825.9 | 825.3 | 834.8 | 856.9 | 773.3 | 802.1 | 826.1 | 801.6 | 792.5 | 109.3 | 205.8 | 275.8 | 248.8 | 362.8 | 345 | 255.3 | 311.7 | 434.5 | 261.2
1004 | 830 | 567.4 | 226.96 | 265.3032 | 363.1 | 336.2 | 326.9 | 310.2 | 608.5 | 48 | 19.5 | 85.8 | 6.1 | 230.1 | 3.6 | 835 | 825.3 | 825.2 | 834.7 | 856.7 | 773.3 | 804.6 | 825.6 | 801.4 | 793.5 | 109.6 | 206.1 | 276 | 249.1 | 362.6 | 345.1 | 255.5 | 311.8 | 434.8 | 261.5
1005 | 831 | 567.8 | 227.12 | 265.4902 | 363 | 336.5 | 327.3 | 309.9 | 607.1 | 48.1 | 19.5 | 85.9 | 5 | 220.8 | 3.2 | 835 | 826.6 | 825.6 | 834.9 | 856.1 | 773.5 | 804 | 826.3 | 801.3 | 794.8 | 109.8 | 206.3 | 276.2 | 249.2 | 362.6 | 345.1 | 255.7 | 311.9 | 435.1 | 261.7
1006 | 832 | 566.8 | 226.72 | 265.0226 | 361.6 | 336.5 | 327.8 | 309.6 | 612.9 | 48.2 | 19.5 | 86 | 5.2 | 214.7 | 3.1 | 834.9 | 831.1 | 826.1 | 835.1 | 856.7 | 773.8 | 799.5 | 826.5 | 801.4 | 793.2 | 110 | 206.6 | 276.4 | 249.3 | 362.4 | 345.1 | 255.9 | 311.9 | 435.3 | 261.9
1007 | 833 | 567.5 | 227 | 265.3499 | 361.5 | 336.9 | 326.5 | 309.1 | 616 | 48.3 | 19.5 | 85.9 | 5.5 | 233 | 3.4 | 834.9 | 830.5 | 826.2 | 834.9 | 857.7 | 773.7 | 801.9 | 825.4 | 801.4 | 792.8 | 110.2 | 206.8 | 276.6 | 249.5 | 362.5 | 345.1 | 256.1 | 312 | 435.6 | 262.2
1008 | 834 | 567.2 | 226.88 | 265.2096 | 362.1 | 337 | 324.8 | 308.4 | 623.7 | 48.4 | 19.5 | 86 | 5.4 | 250.4 | 3.6 | 834.9 | 828.8 | 826 | 834.5 | 857.9 | 773.5 | 800.7 | 823.5 | 801.4 | 791.7 | 110.5 | 207.1 | 276.8 | 249.7 | 362.3 | 345.1 | 256.3 | 312.2 | 435.8 | 262.4
1009 | 835 | 566.8 | 226.72 | 265.0226 | 362.4 | 337.6 | 323.9 | 308.1 | 627.3 | 48.5 | 19.5 | 86 | 5.2 | 251.5 | 3.8 | 834.9 | 829.1 | 826.6 | 834.8 | 858.8 | 773.4 | 805.7 | 827.1 | 801.5 | 791.8 | 110.7 | 207.3 | 277 | 249.9 | 362.4 | 345.4 | 256.5 | 312.4 | 436.1 | 262.6
1010 | 836 | 568 | 227.2 | 265.5837 | 362.4 | 338.1 | 323.1 | 307.9 | 615.6 | 48.5 | 19.5 | 86.1 | 4.8 | 238.8 | 3.7 | 835 | 830.5 | 827.5 | 834.5 | 857 | 773.5 | 800.6 | 827.2 | 801.5 | 791.5 | 110.9 | 207.6 | 277.1 | 250.2 | 362.3 | 345.4 | 256.7 | 312.6 | 436.4 | 262.8
1011 | 837 | 566.8 | 226.72 | 265.0226 | 363.2 | 338.3 | 323.3 | 307.4 | 620.8 | 48.6 | 19.5 | 86.1 | 4.7 | 243.9 | 3.6 | 835 | 832.7 | 827.1 | 835.2 | 854.2 | 773.7 | 782.8 | 822.9 | 801.8 | 789.9 | 111.1 | 207.8 | 277.6 | 250.4 | 362.1 | 345.4 | 256.9 | 312.7 | 436.7 | 263.1
1012 | 838 | 566.5 | 226.6 | 264.8823 | 363.2 | 338.8 | 322.9 | 307 | 629.4 | 48.7 | 19.5 | 86.2 | 4.5 | 257.8 | 3.5 | 835.3 | 833.5 | 826.2 | 836.2 | 853.6 | 773.8 | 776.9 | 819.9 | 802.3 | 789.2 | 111.4 | 208.1 | 277.8 | 250.5 | 362 | 345.2 | 257.1 | 312.7 | 436.9 | 263.3
1013 | 839 | 568.1 | 227.24 | 265.6305 | 363.4 | 339 | 323.1 | 307 | 627.6 | 48.8 | 19.5 | 86.2 | 5.1 | 233.4 | 3.1 | 835.5 | 832.5 | 826.2 | 836.1 | 853.2 | 774.1 | 772.1 | 817.4 | 802.8 | 789.3 | 111.6 | 208.4 | 277.9 | 250.8 | 361.9 | 345.1 | 257.3 | 312.8 | 437.2 | 263.6
1014 | 840 | 567.6 | 227.04 | 265.3967 | 365.1 | 339.2 | 323.2 | 307 | 636.8 | 48.8 | 19.5 | 86.2 | 4.7 | 197.3 | 2.9 | 835.6 | 837.6 | 826.2 | 836.4 | 853.5 | 773.9 | 769.1 | 817.1 | 803.3 | 789.9 | 111.8 | 208.6 | 278.2 | 251 | 361.7 | 345.2 | 257.5 | 312.9 | 437.4 | 263.8
1015 | 841 | 567.9 | 227.16 | 265.537 | 367.5 | 339.2 | 323.3 | 306.7 | 650.8 | 48.7 | 19.5 | 86.2 | 4.9 | 201.7 | 2.9 | 835.6 | 842.9 | 822.3 | 836.5 | 855.3 | 774.2 | 755.5 | 808.1 | 803.6 | 789 | 112 | 208.9 | 278.5 | 251.3 | 361.6 | 345.2 | 257.7 | 313 | 437.6 | 264
1016 | 842 | 568.1 | 227.24 | 265.6305 | 369.5 | 339 | 323 | 306.5 | 633.4 | 48.7 | 19.5 | 86.2 | 5.1 | 234.4 | 3.8 | 835.2 | 843.9 | 821.1 | 836.2 | 856.1 | 774.4 | 748.7 | 805.4 | 804 | 787.5 | 112.2 | 209.1 | 278.6 | 251.6 | 361.3 | 345 | 257.9 | 313.1 | 437.7 | 264.3
1017 | 843 | 568 | 227.2 | 265.5837 | 369.3 | 339.1 | 322.5 | 306.7 | 628 | 48.7 | 19.5 | 86.2 | 4.8 | 218.7 | 5.7 | 835 | 845 | 817.7 | 835.6 | 856.4 | 774.3 | 744.8 | 802.8 | 804.5 | 787.3 | 112.5 | 209.4 | 279.1 | 251.7 | 361.4 | 344.9 | 258.2 | 313.2 | 437.8 | 264.5
1018 | 844 | 566.7 | 226.68 | 264.9759 | 370 | 339.4 | 322.8 | 307.2 | 644.7 | 48.7 | 19.5 | 86.2 | 5.2 | 205.9 | 7.4 | 834.8 | 847.3 | 812.9 | 835.5 | 854.7 | 774.1 | 734.7 | 801.2 | 804.6 | 786.6 | 112.7 | 209.7 | 279.7 | 251.9 | 361.9 | 345.2 | 258.4 | 313.3 | 438 | 264.8
1019 | 845 | 568 | 227.2 | 265.5837 | 370.8 | 339.7 | 323.8 | 308.1 | 644.5 | 48.8 | 19.5 | 86.2 | 5 | 214.7 | 7.5 | 834.4 | 849.7 | 812.7 | 836.3 | 855.2 | 773.7 | 730 | 802.6 | 804.8 | 787 | 112.9 | 209.9 | 279.6 | 252 | 362.2 | 345.6 | 258.7 | 313.5 | 438.3 | 265
1020 | 846 | 567.4 | 226.96 | 265.3032 | 371.3 | 339 | 325.3 | 309.2 | 648.3 | 48.8 | 19.5 | 86.3 | 5 | 201.2 | 8.3 | 834.2 | 847.5 | 814.5 | 835.8 | 856 | 773.5 | 742.2 | 808.6 | 805.1 | 788.4 | 113.1 | 210.2 | 279.8 | 252.2 | 362.5 | 346 | 258.9 | 313.7 | 438.4 | 265.3
1021 | 847 | 566.5 | 226.6 | 264.8823 | 372.4 | 339 | 325.4 | 309.9 | 647.5 | 48.7 | 19.5 | 86.4 | 5.5 | 202.5 | 8.8 | 834.3 | 843.3 | 816.8 | 835.5 | 856.9 | 773.2 | 751.8 | 812.5 | 805.1 | 789 | 113.4 | 210.5 | 280 | 252.4 | 363.1 | 346.4 | 259.2 | 313.8 | 438.6 | 265.6
1022 | 848 | 566.4 | 226.56 | 264.8356 | 372.4 | 339.4 | 325.5 | 309.6 | 646.4 | 48.7 | 19.5 | 86.6 | 5.2 | 198 | 9.1 | 834.2 | 844.3 | 815.4 | 835.2 | 857.6 | 773 | 753.7 | 812.8 | 804.9 | 788.8 | 113.6 | 210.8 | 280.2 | 252.7 | 363.1 | 346.9 | 259.4 | 314 | 438.9 | 265.9
1023 | 849 | 566.9 | 226.76 | 265.0694 | 370.9 | 339 | 326.1 | 310.2 | 628.3 | 48.7 | 19.5 | 86.8 | 5.6 | 196.5 | 8.8 | 834 | 845.8 | 814.5 | 835 | 859 | 772.6 | 753.7 | 812.4 | 804.7 | 790.3 | 113.8 | 211.1 | 280.3 | 253 | 362.7 | 347 | 259.5 | 314.2 | 439 | 266.1
1024 | 850 | 566.5 | 226.6 | 264.8823 | 370.5 | 338.7 | 326.6 | 310.1 | 620.4 | 48.7 | 19.5 | 86.9 | 5.5 | 194.3 | 8.2 | 833.7 | 847.6 | 814.8 | 834.7 | 859.3 | 772.4 | 763 | 817.4 | 804.7 | 792 | 114 | 211.4 | 280.6 | 253.3 | 362.4 | 346.9 | 259.6 | 314.3 | 439.1 | 266.3
1025 | 851 | 566 | 226.4 | 264.6486 | 371.7 | 338.8 | 325.9 | 309.6 | 615.6 | 48.8 | 19.5 | 87 | 5.7 | 202.6 | 7.3 | 833.6 | 848.9 | 816.2 | 835.3 | 860.2 | 772.3 | 763.7 | 818.3 | 804.6 | 792.3 | 114.3 | 211.7 | 280.8 | 253.6 | 362 | 346.8 | 259.7 | 314.4 | 439.2 | 266.6
1026 | 852 | 566.6 | 226.64 | 264.9291 | 372.7 | 338.7 | 326.2 | 309.8 | 611.8 | 48.8 | 19.5 | 87 | 5.5 | 214 | 6.7 | 833.4 | 846.7 | 816.3 | 834.2 | 860.3 | 772 | 767.5 | 817.4 | 804.4 | 791 | 114.5 | 212 | 280.9 | 253.8 | 362 | 346.5 | 259.8 | 314.5 | 439.4 | 266.8
1027 | 853 | 566.3 | 226.52 | 264.7888 | 373.5 | 338.7 | 326.7 | 310.1 | 598.6 | 48.8 | 19.5 | 87 | 5.2 | 204.5 | 6.4 | 833.2 | 843.6 | 817.4 | 833.7 | 860.1 | 771.6 | 776.1 | 820.3 | 804.3 | 791.4 | 114.7 | 212.3 | 281 | 254 | 361.8 | 346.3 | 260 | 314.6 | 439.6 | 267
1028 | 854 | 565.6 | 226.24 | 264.4615 | 374.1 | 339 | 326.4 | 310.3 | 590 | 48.8 | 19.5 | 87.2 | 5.1 | 199.9 | 6.7 | 832.9 | 841.9 | 816.8 | 833.2 | 860.6 | 771.5 | 785.3 | 823.2 | 804.1 | 789.8 | 114.9 | 212.5 | 281.3 | 254.2 | 361.5 | 346.4 | 260.1 | 314.7 | 439.9 | 267.2
1029 | 855 | 566 | 226.4 | 264.6486 | 374.7 | 339.1 | 326.4 | 310.1 | 599.8 | 48.8 | 19.5 | 87.4 | 5.2 | 209.4 | 6.7 | 832.6 | 845 | 815.9 | 832.5 | 860.3 | 771.5 | 779.4 | 821.6 | 803.8 | 791 | 115.2 | 212.8 | 281.6 | 254.4 | 361.6 | 346.4 | 260.3 | 314.8 | 440.3 | 267.4
1030 | 856 | 566.6 | 226.64 | 264.9291 | 375.5 | 339 | 326.5 | 309.1 | 611.4 | 48.8 | 19.4 | 87.5 | 4.7 | 204.1 | 6.5 | 832.4 | 844.2 | 815.6 | 832.1 | 860.2 | 771.6 | 780.7 | 821.8 | 803.6 | 792.1 | 115.4 | 213.1 | 281.8 | 254.7 | 362 | 346.4 | 260.4 | 315 | 440.5 | 267.6
1031 | 857 | 566.9 | 226.76 | 265.0694 | 374.4 | 339.2 | 326 | 308.8 | 604.2 | 48.8 | 19.4 | 87.5 | 5.5 | 199.4 | 6.9 | 832.2 | 838.7 | 816.6 | 831.4 | 859.8 | 771.5 | 793 | 823.7 | 803.6 | 790.7 | 115.6 | 213.4 | 281.9 | 254.9 | 362.5 | 346.7 | 260.7 | 315.2 | 440.7 | 267.9
1032 | 858 | 567.1 | 226.84 | 265.1629 | 374.8 | 339.9 | 326.4 | 309.2 | 584.4 | 48.8 | 19.4 | 87.5 | 6.1 | 215.4 | 6.6 | 832 | 837 | 817.2 | 832.4 | 857.8 | 771.8 | 800.6 | 825.3 | 803.3 | 789.1 | 115.8 | 213.7 | 282.2 | 255.1 | 363.1 | 347.1 | 260.9 | 315.4 | 441.1 | 268.1
1033 | 859 | 566.8 | 226.72 | 265.0226 | 376 | 341.1 | 327.7 | 309.8 | 567.4 | 48.8 | 19.4 | 87.6 | 5.9 | 214.7 | 6.2 | 832 | 836 | 817.2 | 832.9 | 857.1 | 772 | 807.4 | 825.5 | 803.2 | 787.8 | 116.1 | 214 | 282.3 | 255.4 | 363.6 | 347.4 | 261.1 | 315.6 | 441.6 | 268.4
1034 | 860 | 566.8 | 226.72 | 265.0226 | 375.6 | 341.9 | 327.9 | 310.2 | 553.8 | 48.9 | 19.4 | 87.7 | 5.7 | 222.1 | 5.6 | 831.9 | 835.1 | 816.9 | 833 | 854.9 | 772.1 | 807 | 826.4 | 803.2 | 786.3 | 116.3 | 214.3 | 282.3 | 255.6 | 363.9 | 347.8 | 261.3 | 315.8 | 442 | 268.6
1035 | 861 | 567.3 | 226.92 | 265.2564 | 375.2 | 342.4 | 327.2 | 310.2 | 540.4 | 48.9 | 19.4 | 87.7 | 5.8 | 233.5 | 5 | 831.8 | 835 | 816.8 | 834.8 | 851.5 | 772 | 800.4 | 821.7 | 803.4 | 782.2 | 116.5 | 214.6 | 282.4 | 255.8 | 363.9 | 348.1 | 261.5 | 316.1 | 442.3 | 268.9
1036 | 862 | 566.5 | 226.6 | 264.8823 | 374.1 | 342.6 | 326.8 | 309.6 | 531.6 | 48.9 | 19.4 | 87.7 | 5.2 | 237 | 4.4 | 832 | 834.8 | 819.3 | 835.3 | 850.1 | 771.6 | 806.8 | 823.6 | 803.4 | 781.1 | 116.8 | 214.9 | 282.6 | 256.1 | 364.3 | 348.9 | 261.7 | 316.3 | 442.7 | 269.1
1037 | 863 | 565.7 | 226.28 | 264.5083 | 373.1 | 342.8 | 326.9 | 309.8 | 536 | 48.9 | 19.4 | 87.9 | 5.4 | 236 | 3.7 | 832.1 | 836.2 | 819.6 | 833.8 | 851.5 | 771.4 | 808.5 | 826.8 | 803.5 | 782.2 | 117 | 215.2 | 282.9 | 256.4 | 364.6 | 349.1 | 261.9 | 316.5 | 443 | 269.3
1038 | 864 | 566 | 226.4 | 264.6486 | 372 | 342.9 | 327.7 | 309.9 | 536.7 | 48.9 | 19.4 | 88.1 | 5.7 | 224.3 | 3.3 | 832.2 | 838.4 | 818 | 833.4 | 853.6 | 771.4 | 810 | 828.8 | 803.5 | 784 | 117.2 | 215.5 | 283 | 256.7 | 364.6 | 349.4 | 262 | 316.7 | 443.3 | 269.6
1039 | 865 | 566.5 | 226.6 | 264.8823 | 371.1 | 342.7 | 327.1 | 310.3 | 540.3 | 48.8 | 19.4 | 88.2 | 4.7 | 220.6 | 3.5 | 832.5 | 837.8 | 818.8 | 833.1 | 855 | 771.4 | 811.1 | 828.7 | 803.8 | 785.2 | 117.4 | 215.8 | 283.2 | 256.9 | 364.7 | 349.4 | 262.2 | 316.8 | 443.5 | 269.8
1040 | 866 | 565.4 | 226.16 | 264.368 | 370.4 | 342.9 | 327.1 | 310.7 | 557.3 | 48.9 | 19.4 | 88.3 | 5.4 | 222 | 3.7 | 832.8 | 839 | 820.6 | 834 | 855.5 | 771.7 | 814.2 | 827.6 | 804.1 | 785.6 | 117.7 | 216.1 | 283.4 | 257.2 | 364.7 | 349.2 | 262.3 | 316.8 | 443.6 | 270
1041 | 867 | 568.5 | 227.4 | 265.8175 | 370.4 | 343.1 | 327.5 | 310.7 | 553.5 | 48.9 | 19.4 | 88.4 | 5.7 | 235.2 | 3.7 | 833 | 836 | 820.8 | 834.1 | 855.8 | 771.8 | 818.6 | 826.1 | 804.2 | 785.1 | 117.9 | 216.4 | 283.5 | 257.5 | 364.7 | 348.9 | 262.5 | 317 | 443.8 | 270.3
1042 | 868 | 565.7 | 226.28 | 264.5083 | 372.2 | 343.2 | 326.8 | 310.6 | 550.4 | 48.9 | 19.4 | 88.5 | 5.4 | 238.1 | 3.7 | 833.2 | 834.8 | 821 | 834.3 | 854.2 | 771.9 | 819.2 | 828.8 | 804.3 | 786.1 | 118.1 | 216.6 | 283.8 | 257.8 | 364.8 | 349.1 | 262.7 | 317.1 | 444 | 270.5
1043 | 869 | 566 | 226.4 | 264.6486 | 372.4 | 343.4 | 325.8 | 309.9 | 558.9 | 48.9 | 19.4 | 88.6 | 4.9 | 233.3 | 3.5 | 833.3 | 833.4 | 821.4 | 833.9 | 854.7 | 771.9 | 819.8 | 830.7 | 804.4 | 784.8 | 118.4 | 216.9 | 284 | 258.1 | 364.9 | 349.1 | 262.9 | 317.2 | 444.3 | 270.7
1044 | 870 | 566.3 | 226.52 | 264.7888 | 372.8 | 343.3 | 325.2 | 309.4 | 565.4 | 49 | 19.4 | 88.5 | 5.5 | 237.1 | 3.8 | 833.5 | 832.4 | 822 | 834.2 | 853.3 | 772.2 | 817.7 | 830.6 | 804.5 | 785.6 | 118.6 | 217.2 | 284.2 | 258.3 | 365 | 349.1 | 263.1 | 317.4 | 444.6 | 271
1045 | 871 | 566.5 | 226.6 | 264.8823 | 373.6 | 343.2 | 324.6 | 309.5 | 578.9 | 49 | 19.4 | 88.3 | 5.7 | 258.3 | 4.4 | 833.7 | 833.1 | 821.1 | 834 | 853.4 | 772.3 | 814.6 | 831.5 | 804.8 | 785.9 | 118.8 | 217.5 | 284.5 | 258.5 | 365.3 | 349 | 263.3 | 317.6 | 444.8 | 271.2
1046 | 872 | 565.5 | 226.2 | 264.4148 | 373.7 | 343.3 | 324 | 308.8 | 595.9 | 49 | 19.4 | 88.2 | 6.4 | 251.3 | 4.6 | 833.9 | 835.5 | 822.5 | 834.2 | 853.2 | 772.6 | 807.6 | 830.8 | 805 | 786.5 | 119 | 217.7 | 284.9 | 258.8 | 365.3 | 349.1 | 263.5 | 317.7 | 445.1 | 271.5
1047 | 873 | 565.2 | 226.08 | 264.2745 | 373.3 | 343.3 | 323.7 | 308.5 | 599.5 | 49 | 19.4 | 88.3 | 5.9 | 246.8 | 4.9 | 834.2 | 837 | 823.9 | 834.7 | 851.6 | 772.6 | 798.8 | 829.2 | 805.5 | 784.9 | 119.3 | 218 | 285 | 259.1 | 365.3 | 348.9 | 263.7 | 317.8 | 445.4 | 271.7
1048 | 874 | 565.1 | 226.04 | 264.2277 | 373.2 | 343.9 | 323.5 | 309.4 | 608.3 | 49 | 19.4 | 88.2 | 5.4 | 258.9 | 5.5 | 834.3 | 836.7 | 824.2 | 835.1 | 851.5 | 772.5 | 785.9 | 821.7 | 805.8 | 783.8 | 119.5 | 218.2 | 285.4 | 259.4 | 365.2 | 348.8 | 263.8 | 317.9 | 445.7 | 271.9
1049 | 875 | 565.9 | 226.36 | 264.6018 | 373.6 | 344.8 | 323.4 | 310.3 | 625.9 | 49 | 19.4 | 88.1 | 6.1 | 238.4 | 5.4 | 834.4 | 835.6 | 824.2 | 835.8 | 849.6 | 772.4 | 778.3 | 819.7 | 806.2 | 782.4 | 119.8 | 218.5 | 285.6 | 259.7 | 365.1 | 348.7 | 264 | 317.9 | 446 | 272.1
1050 | 876 | 566.3 | 226.52 | 264.7888 | 374.2 | 345.2 | 324.2 | 310.9 | 623 | 48.9 | 19.4 | 87.9 | 5.6 | 248.9 | 6.6 | 834.6 | 834.1 | 825.8 | 837.3 | 847 | 772 | 776.2 | 820.7 | 806.6 | 780.6 | 120 | 218.8 | 285.6 | 260 | 365 | 348.6 | 264.3 | 318 | 446.2 | 272.4
1051 | 877 | 565.9 | 226.36 | 264.6018 | 374.8 | 345.5 | 323.6 | 311.6 | 620.2 | 48.9 | 19.4 | 87.8 | 5.6 | 246.9 | 7.8 | 834.8 | 833.2 | 826 | 837.3 | 844.6 | 771.7 | 764.4 | 815.1 | 806.8 | 777.8 | 120.2 | 219 | 285.9 | 260.3 | 365 | 348.4 | 264.5 | 318.1 | 446.5 | 272.6
1052 | 878 | 566.8 | 226.72 | 265.0226 | 375.1 | 346.2 | 323.2 | 312.5 | 644.3 | 48.8 | 19.4 | 87.7 | 6.2 | 242.7 | 8.3 | 835 | 832.3 | 824.7 | 836.5 | 843 | 771.9 | 745 | 803.1 | 806.8 | 774.5 | 120.5 | 219.3 | 286.7 | 260.6 | 365.1 | 348.2 | 264.8 | 318.2 | 446.9 | 272.8
1053 | 879 | 567 | 226.8 | 265.1161 | 375.3 | 347.1 | 323 | 312.6 | 670.1 | 48.8 | 19.4 | 87.7 | 6.2 | 246.6 | 8.2 | 835.1 | 832.3 | 822.2 | 835.1 | 842.7 | 771.9 | 739.1 | 801.2 | 806.9 | 774.2 | 120.7 | 219.5 | 286.9 | 260.9 | 365.3 | 348 | 265 | 318.2 | 447.3 | 273.1
1054 | 880 | 566.9 | 226.76 | 265.0694 | 375.4 | 347.4 | 322.4 | 313.1 | 682.6 | 48.8 | 19.4 | 87.8 | 6.1 | 246 | 7.8 | 834.9 | 835.1 | 816.2 | 833.9 | 842.8 | 771.7 | 746.5 | 803.7 | 807 | 775.2 | 120.9 | 219.8 | 287.1 | 261.2 | 365.6 | 348.1 | 265.2 | 318.3 | 447.5 | 273.3
1055 | 881 | 566 | 226.4 | 264.6486 | 375.2 | 347.3 | 322.3 | 313.1 | 664.8 | 48.8 | 19.4 | 87.8 | 6.5 | 263.4 | 7.5 | 834.3 | 838.5 | 810.4 | 832.9 | 843.4 | 772 | 744.7 | 802 | 806.9 | 776.7 | 121.2 | 220 | 287.3 | 261.5 | 365.9 | 348.2 | 265.5 | 318.4 | 447.7 | 273.5
1056 | 882 | 566.8 | 226.72 | 265.0226 | 375.5 | 346.6 | 322.5 | 313.3 | 647.6 | 48.8 | 19.4 | 87.7 | 6.7 | 264.8 | 8.1 | 833.8 | 841.4 | 808 | 831.8 | 843 | 772.4 | 738.7 | 799.9 | 807.1 | 776.8 | 121.4 | 220.3 | 287.5 | 261.8 | 366.4 | 348.3 | 265.8 | 318.5 | 447.8 | 273.8
1057 | 883 | 565.8 | 226.32 | 264.555 | 376 | 345.6 | 323.1 | 313.8 | 647.8 | 48.9 | 19.4 | 87.6 | 6.3 | 262.7 | 8.1 | 833.2 | 843.5 | 807.3 | 830.9 | 843.2 | 772.5 | 729.3 | 794.7 | 807.3 | 775.8 | 121.7 | 220.5 | 288 | 262.2 | 366.8 | 348.4 | 266.1 | 318.6 | 447.9 | 274.1
1058 | 884 | 566.6 | 226.64 | 264.9291 | 377.5 | 343.9 | 324.6 | 315.3 | 645.9 | 48.9 | 19.4 | 87.5 | 5.4 | 253.1 | 8.3 | 832.7 | 848.6 | 805.2 | 830.3 | 844 | 772.7 | 714.4 | 786.7 | 807.6 | 775 | 121.9 | 220.8 | 288.3 | 262.5 | 367.3 | 348.6 | 266.5 | 318.8 | 448 | 274.3
1059 | 885 | 566.1 | 226.44 | 264.6953 | 378.6 | 342.4 | 325.8 | 316.5 | 629.4 | 48.9 | 19.4 | 87.3 | 5.9 | 255.5 | 8.4 | 832.1 | 848.3 | 802.9 | 829.2 | 845 | 773.2 | 707.4 | 777.8 | 808.1 | 773.5 | 122.1 | 221 | 288.2 | 262.8 | 367.4 | 348.7 | 266.8 | 318.9 | 448.1 | 274.6
1060 | 886 | 565.5 | 226.2 | 264.4148 | 379.7 | 341.1 | 327.5 | 316.9 | 611.6 | 48.8 | 19.4 | 87.1 | 6.2 | 256.2 | 8.5 | 831.5 | 850.1 | 801.4 | 828.8 | 846 | 773.2 | 707.4 | 782.9 | 808.7 | 774.5 | 122.4 | 221.3 | 288.4 | 263.1 | 367.4 | 349.1 | 267 | 319.1 | 448.1 | 274.8
1061 | 887 | 566.4 | 226.56 | 264.8356 | 380.3 | 339.9 | 326.7 | 317.3 | 592.7 | 48.8 | 19.4 | 87.2 | 6.2 | 253.3 | 8.6 | 830.9 | 848.4 | 802.3 | 828.2 | 849.6 | 772.5 | 717.4 | 788.2 | 809 | 775.4 | 122.6 | 221.5 | 288.4 | 263.4 | 367.5 | 349.3 | 267.2 | 319.3 | 448.1 | 275.1
1062 | 888 | 567 | 226.8 | 265.1161 | 380.3 | 338.8 | 326.1 | 317.8 | 573.7 | 48.8 | 19.4 | 87.2 | 5.2 | 254.4 | 8.6 | 830.6 | 847.6 | 803.2 | 827.5 | 851.3 | 771.6 | 728.5 | 790.4 | 808.9 | 775.6 | 122.9 | 221.7 | 288.4 | 263.7 | 367.3 | 349.3 | 267.3 | 319.4 | 448.2 | 275.3
1063 | 889 | 566.1 | 226.44 | 264.6953 | 380 | 339.5 | 326.2 | 317.9 | 565.5 | 48.8 | 19.4 | 87.4 | 5.1 | 251.8 | 8.5 | 830.4 | 847.4 | 805.9 | 826.8 | 853.3 | 771.1 | 739.3 | 797.1 | 808.7 | 776.9 | 123.1 | 222 | 288.7 | 264 | 367 | 349.3 | 267.4 | 319.6 | 448.3 | 275.5
1064 | 890 | 566.4 | 226.56 | 264.8356 | 379 | 340 | 326.4 | 317.7 | 559.1 | 48.7 | 19.4 | 87.4 | 5.2 | 253.6 | 8.3 | 830.1 | 847.8 | 808.2 | 826.4 | 856.3 | 770.8 | 749.7 | 799 | 808.5 | 777.5 | 123.4 | 222.2 | 288.9 | 264.4 | 366.8 | 349.6 | 267.5 | 319.8 | 448.3 | 275.7
1065 | 891 | 565.8 | 226.32 | 264.555 | 379.4 | 340.4 | 326.7 | 317.2 | 551.5 | 48.8 | 19.3 | 87.5 | 5.1 | 238.7 | 8.2 | 830 | 844.8 | 810.1 | 826.4 | 856.4 | 770.5 | 751.3 | 796.9 | 808.1 | 777.2 | 123.6 | 222.5 | 289 | 264.7 | 366.8 | 350.2 | 267.7 | 320 | 448.4 | 275.9
1066 | 892 | 566.5 | 226.6 | 264.8823 | 381.6 | 340.8 | 326.2 | 315.9 | 552.7 | 48.8 | 19.3 | 87.7 | 5.5 | 238.6 | 8 | 830.1 | 843.1 | 811.3 | 826.8 | 856.5 | 770.1 | 736.6 | 790 | 807.8 | 775.4 | 123.8 | 222.7 | 289 | 265 | 366.6 | 350.2 | 267.8 | 320.1 | 448.6 | 276.2
1067 | 893 | 566.9 | 226.76 | 265.0694 | 382.6 | 341.5 | 326 | 315 | 564.2 | 48.9 | 19.4 | 87.8 | 5.7 | 237.8 | 7.8 | 830.1 | 845.3 | 811.3 | 826.6 | 855.9 | 769.8 | 729.4 | 785.8 | 807.8 | 773.9 | 124.1 | 223 | 289.5 | 265.3 | 366.4 | 349.9 | 268 | 320.1 | 448.7 | 276.4
1068 | 894 | 566.9 | 226.76 | 265.0694 | 384.5 | 341.4 | 325.5 | 314.3 | 568.5 | 48.9 | 19.4 | 88 | 5.8 | 237.6 | 6.9 | 830 | 850.5 | 807.5 | 826 | 853.3 | 769.8 | 714.2 | 772.7 | 807.7 | 772.3 | 124.3 | 223.2 | 290 | 265.6 | 366.1 | 349.8 | 268.2 | 320.2 | 448.8 | 276.6
1069 | 895 | 566.8 | 226.72 | 265.0226 | 387 | 341.3 | 325.1 | 313.7 | 582.5 | 49 | 19.4 | 88.1 | 5.5 | 238.4 | 6.5 | 829.7 | 850 | 805.3 | 825.6 | 851.2 | 769.9 | 704.2 | 765.8 | 807.5 | 771 | 124.6 | 223.4 | 290.1 | 265.8 | 365.7 | 349.4 | 268.3 | 320.1 | 448.8 | 276.8
1070 | 896 | 566.6 | 226.64 | 264.9291 | 388.2 | 341.2 | 325.5 | 313.3 | 603.1 | 49.1 | 19.4 | 88.2 | 5.8 | 249.9 | 6.7 | 829.3 | 847.2 | 802.4 | 824.8 | 849.4 | 769.7 | 691.5 | 759.1 | 807.7 | 769.4 | 124.8 | 223.7 | 290.5 | 266.1 | 365.8 | 349 | 268.6 | 320.1 | 448.8 | 277
1071 | 897 | 567.3 | 226.92 | 265.2564 | 389.7 | 341.3 | 325.6 | 313.4 | 613 | 49.1 | 19.3 | 88.3 | 5.6 | 251.7 | 6.4 | 828.8 | 835.7 | 799.3 | 823.8 | 849.7 | 770 | 679.4 | 751.5 | 807.8 | 768.4 | 125.1 | 223.9 | 290.7 | 266.4 | 366.1 | 348.6 | 268.8 | 320.2 | 448.9 | 277.2
1072 | 898 | 566.4 | 226.56 | 264.8356 | 389.4 | 341.4 | 326.6 | 314 | 607.6 | 49.1 | 19.3 | 88.5 | 5.2 | 262.5 | 5.7 | 828 | 818.9 | 791.8 | 822 | 846.5 | 770.4 | 669.4 | 740.6 | 807.9 | 766.5 | 125.3 | 224.2 | 291 | 266.6 | 366.5 | 348.2 | 269 | 320.3 | 448.8 | 277.4
1073 | 899 | 567.2 | 226.88 | 265.2096 | 389.8 | 341.3 | 327.1 | 315.2 | 608.8 | 49 | 19.3 | 88.5 | 5.1 | 269 | 5.8 | 827.2 | 806.5 | 785.4 | 820.3 | 844.1 | 770.2 | 667.3 | 740 | 807.9 | 766.6 | 125.5 | 224.4 | 291.2 | 266.9 | 366.8 | 348 | 269.3 | 320.3 | 448.8 | 277.7
1074 | 900 | 568 | 227.2 | 265.5837 | 389.9 | 341.3 | 327.3 | 315.8 | 622.2 | 49 | 19.3 | 88.6 | 4.9 | 262.6 | 6.6 | 826.4 | 797.1 | 783.4 | 819.1 | 840.8 | 770.6 | 660.4 | 733.4 | 808 | 765.7 | 125.8 | 224.7 | 291.6 | 267.2 | 367.6 | 348 | 269.7 | 320.4 | 448.8 | 277.9
1075 | 901 | 567 | 226.8 | 265.1161 | 390.5 | 340.8 | 328 | 316.7 | 633 | 49 | 19.3 | 88.7 | 5.6 | 263.8 | 6.8 | 825.7 | 801 | 784.2 | 818.6 | 840.4 | 770.9 | 660 | 740.5 | 807.8 | 766.2 | 126 | 224.9 | 291.8 | 267.4 | 368.2 | 348 | 270.1 | 320.5 | 448.7 | 278.2
1076 | 902 | 566 | 226.4 | 264.6486 | 391 | 340.8 | 330.3 | 318.1 | 642.3 | 49 | 19.3 | 88.8 | 5.2 | 283.7 | 6.1 | 825 | 803.9 | 784.4 | 817.9 | 841.1 | 770.9 | 660.8 | 746.4 | 807.7 | 765.9 | 126.3 | 225.2 | 292.1 | 267.7 | 368.9 | 348.2 | 270.4 | 320.6 | 448.8 | 278.5
1077 | 903 | 567.2 | 226.88 | 265.2096 | 390.6 | 340.9 | 331.8 | 318.7 | 653.7 | 49.1 | 19.3 | 88.9 | 5.3 | 263 | 5.3 | 824.4 | 807.9 | 783.1 | 817 | 840.7 | 770.8 | 665.2 | 754.4 | 807.5 | 766.8 | 126.5 | 225.4 | 292.4 | 267.9 | 369.5 | 348.4 | 270.7 | 320.8 | 448.8 | 278.7
1078 | 904 | 568.5 | 227.4 | 265.8175 | 391.7 | 340.9 | 332.4 | 319.2 | 644.7 | 49.2 | 19.3 | 89.1 | 5.7 | 251.2 | 5.7 | 823.7 | 804.8 | 779.8 | 815.7 | 841.7 | 770.9 | 662.1 | 745.9 | 807.4 | 767.2 | 126.8 | 225.7 | 292.4 | 268.2 | 369.8 | 348.7 | 271 | 321 | 448.8 | 279
1079 | 905 | 565.3 | 226.12 | 264.3213 | 391.6 | 340.4 | 333.1 | 319.8 | 625.4 | 49.2 | 19.3 | 89.1 | 6.1 | 262.2 | 6.8 | 822.9 | 807.9 | 781.3 | 815 | 842.9 | 770.3 | 676 | 757 | 806.8 | 769.5 | 127 | 225.9 | 292.5 | 268.5 | 370 | 349 | 271.3 | 321.2 | 448.8 | 279.2
1080 | 906 | 566.3 | 226.52 | 264.7888 | 391.6 | 340.3 | 334.3 | 320.1 | 614 | 49.2 | 19.3 | 89.1 | 5.9 | 254.2 | 7.6 | 822.3 | 803.2 | 778.3 | 813.9 | 843.5 | 769.8 | 674.5 | 755.1 | 806.8 | 769.5 | 127.3 | 226.2 | 292.8 | 268.8 | 370.2 | 349.4 | 271.4 | 321.3 | 448.8 | 279.5
1081 | 907 | 566.1 | 226.44 | 264.6953 | 391.9 | 340 | 335.2 | 320.3 | 611.4 | 49.2 | 19.3 | 89.1 | 5.4 | 260 | 8.1 | 821.6 | 807.7 | 780.9 | 813.3 | 845.9 | 769.5 | 677.5 | 762 | 806.2 | 771.3 | 127.5 | 226.4 | 292.9 | 269.1 | 370.3 | 349.7 | 271.6 | 321.4 | 448.8 | 279.7
1082 | 908 | 565.2 | 226.08 | 264.2745 | 391.3 | 340.1 | 336.6 | 320.4 | 619.6 | 49.3 | 19.3 | 89 | 5.4 | 263.5 | 7.7 | 821 | 813 | 784.9 | 812.9 | 846.9 | 769.3 | 692.9 | 769.4 | 805.5 | 772.8 | 127.8 | 226.7 | 293.1 | 269.5 | 370.7 | 349.8 | 271.8 | 321.6 | 448.7 | 280
1083 | 909 | 566.1 | 226.44 | 264.6953 | 390.5 | 340.1 | 337.1 | 320.6 | 625.3 | 49.3 | 19.3 | 89 | 5.2 | 264.2 | 7.3 | 820.7 | 819.1 | 787.7 | 813.6 | 848.4 | 768.9 | 697.2 | 774.2 | 804.9 | 773.3 | 128 | 226.9 | 293.6 | 269.8 | 370.8 | 349.9 | 272.1 | 321.7 | 448.7 | 280.2
1084 | 910 | 566.1 | 226.44 | 264.6953 | 389.3 | 340.6 | 338.4 | 320.8 | 640.8 | 49.4 | 19.3 | 89 | 5 | 238.8 | 7.3 | 820.6 | 820.2 | 790.5 | 813.7 | 848.9 | 768.6 | 696.3 | 775.7 | 804.4 | 773 | 128.3 | 227.2 | 293.9 | 270.1 | 370.9 | 349.8 | 272.3 | 321.8 | 448.9 | 280.4
1085 | 911 | 566.4 | 226.56 | 264.8356 | 388.4 | 341.2 | 338.6 | 320.5 | 639.9 | 49.4 | 19.3 | 88.9 | 5 | 251.4 | 7.1 | 820.3 | 821.7 | 792.5 | 813.4 | 847.3 | 768.7 | 702.4 | 779.2 | 803.6 | 773.5 | 128.5 | 227.4 | 293.9 | 270.4 | 370.9 | 349.9 | 272.5 | 321.9 | 449.2 | 280.7
1086 | 912 | 566.2 | 226.48 | 264.7421 | 387.6 | 342.2 | 339.2 | 320.7 | 651.3 | 49.5 | 19.3 | 88.8 | 5.4 | 244.7 | 7.2 | 820.1 | 825.9 | 793.7 | 813.5 | 847.1 | 768.4 | 719.4 | 788.9 | 803.2 | 774.9 | 128.8 | 227.7 | 294.2 | 270.7 | 370.6 | 350.1 | 272.7 | 322 | 449.4 | 280.9
1087 | 913 | 566.9 | 226.76 | 265.0694 | 389.1 | 342.9 | 340.3 | 321.4 | 649.2 | 49.5 | 19.3 | 88.7 | 5.5 | 248.9 | 7.3 | 820 | 833.9 | 794.9 | 814.6 | 847 | 768.5 | 719.9 | 790.1 | 803 | 775.3 | 129 | 227.9 | 294.4 | 271.1 | 370.5 | 350.1 | 272.9 | 322.1 | 449.7 | 281.1
1088 | 914 | 567 | 226.8 | 265.1161 | 390.3 | 342.9 | 339.7 | 320.8 | 635.6 | 49.6 | 19.3 | 88.6 | 5.4 | 244.9 | 7.2 | 819.8 | 838.7 | 796.2 | 815.1 | 845.9 | 768.4 | 720.7 | 792 | 802.4 | 777 | 129.3 | 228.2 | 294.6 | 271.4 | 370.6 | 350.2 | 273.1 | 322.3 | 449.8 | 281.4
1089 | 915 | 566 | 226.4 | 264.6486 | 389.5 | 342.8 | 338.5 | 320.8 | 633.8 | 49.7 | 19.3 | 88.6 | 5.4 | 242.7 | 7.1 | 819.7 | 843.5 | 798.6 | 816.2 | 844.5 | 768.2 | 721 | 795.6 | 802.3 | 776.1 | 129.5 | 228.4 | 294.8 | 271.7 | 370.6 | 350.4 | 273.3 | 322.4 | 449.8 | 281.6
1090 | 916 | 566 | 226.4 | 264.6486 | 390.1 | 343.1 | 338.1 | 321.2 | 633.3 | 49.7 | 19.3 | 88.5 | 5.4 | 243.4 | 6.9 | 819.9 | 845.4 | 801.4 | 816.8 | 844.1 | 767.8 | 728.5 | 801.2 | 802.1 | 775.8 | 129.7 | 228.6 | 294.9 | 272 | 370.3 | 350.5 | 273.5 | 322.6 | 450 | 281.9
1091 | 917 | 566 | 226.4 | 264.6486 | 391.6 | 343.6 | 338.5 | 320.4 | 647.5 | 49.7 | 19.3 | 88.4 | 5.4 | 242.7 | 6.6 | 819.7 | 847.2 | 802.4 | 816.9 | 844.2 | 767.3 | 731.8 | 804.9 | 801.5 | 775.9 | 130 | 228.9 | 295.3 | 272.3 | 369.9 | 350.6 | 273.6 | 322.7 | 450.1 | 282.1
1092 | 918 | 565.8 | 226.32 | 264.555 | 391.6 | 344.2 | 338.8 | 319.7 | 662.8 | 49.7 | 19.3 | 88.3 | 5.3 | 243 | 6.2 | 819.4 | 851.9 | 801.5 | 816.2 | 844.3 | 767.5 | 732.8 | 805 | 800.8 | 777.9 | 130.2 | 229.1 | 295.7 | 272.6 | 369.8 | 350.4 | 273.8 | 322.8 | 450.3 | 282.3
1093 | 919 | 567 | 226.8 | 265.1161 | 390.1 | 345 | 338.5 | 319.1 | 671.8 | 49.8 | 19.3 | 88.1 | 5.5 | 242.2 | 5.9 | 819 | 850.4 | 797.7 | 815.9 | 844.6 | 768 | 725.8 | 799 | 800.7 | 778.6 | 130.5 | 229.4 | 296 | 272.8 | 369.9 | 350.5 | 274 | 322.8 | 450.5 | 282.5
1094 | 920 | 567.5 | 227 | 265.3499 | 389.3 | 345.6 | 338.1 | 319 | 674.9 | 49.8 | 19.3 | 88.1 | 5.5 | 242.1 | 5.8 | 818.4 | 840.6 | 792.6 | 814.4 | 844.5 | 768.6 | 710.7 | 788.3 | 800.6 | 777.3 | 130.8 | 229.6 | 296.4 | 273.1 | 370.1 | 350.5 | 274.3 | 322.9 | 450.7 | 282.7
1095 | 921 | 566.6 | 226.64 | 264.9291 | 389.1 | 345.9 | 338.8 | 320 | 671.8 | 49.7 | 19.3 | 88.1 | 5.9 | 240.8 | 5.9 | 817.7 | 839.2 | 790.9 | 813.4 | 845.2 | 769 | 710.4 | 790.7 | 800.7 | 777.6 | 131 | 229.9 | 296.5 | 273.4 | 370.2 | 350.5 | 274.5 | 323 | 450.7 | 283
1096 | 922 | 567 | 226.8 | 265.1161 | 389.5 | 346.3 | 338.8 | 320.3 | 663.2 | 49.6 | 19.3 | 88.1 | 5.9 | 233.5 | 5.9 | 817.2 | 842.7 | 793.5 | 812.9 | 846.9 | 769.3 | 714 | 790 | 800.8 | 778.2 | 131.3 | 230.1 | 296.7 | 273.7 | 370.2 | 350.4 | 274.8 | 323.1 | 450.7 | 283.2
1097 | 923 | 564.4 | 225.76 | 263.9004 | 389.8 | 346.6 | 338.5 | 320.3 | 659.1 | 49.6 | 19.3 | 88.1 | 5.5 | 234.8 | 5.5 | 816.9 | 842.6 | 793.4 | 812.6 | 847.4 | 769.8 | 712.2 | 789.9 | 801.2 | 777.5 | 131.5 | 230.3 | 296.9 | 273.9 | 370.3 | 350.6 | 275 | 323.3 | 450.8 | 283.4
1098 | 924 | 564.6 | 225.84 | 263.9939 | 390.3 | 346.7 | 339.5 | 320.7 | 652.8 | 49.6 | 19.3 | 88.2 | 5.1 | 244.1 | 5.3 | 816.7 | 842.3 | 796.6 | 812.4 | 848.8 | 769.7 | 721.8 | 794.8 | 801.3 | 778.6 | 131.8 | 230.6 | 297 | 274.1 | 370.4 | 350.9 | 275.3 | 323.5 | 450.9 | 283.7
1099 | 925 | 564.7 | 225.88 | 264.0407 | 390.6 | 346.7 | 339.7 | 320.6 | 636.2 | 49.7 | 19.3 | 88.3 | 5.5 | 243.9 | 5.3 | 816.5 | 844.5 | 798.2 | 813.2 | 846.6 | 769.5 | 731 | 799.2 | 801.4 | 779.2 | 132 | 230.8 | 297.1 | 274.4 | 370.6 | 351.3 | 275.5 | 323.8 | 451 | 283.9
1100 | 926 | 565 | 226 | 264.181 | 391.5 | 346.9 | 339.1 | 320.3 | 621.6 | 49.7 | 19.3 | 88.3 | 4.9 | 248.2 | 5.9 | 816.3 | 843.6 | 798.5 | 813.8 | 843.3 | 769 | 725.9 | 798.1 | 801.3 | 777.5 | 132.3 | 231.1 | 297.2 | 274.6 | 370.8 | 351.5 | 275.7 | 323.9 | 451.1 | 284.1
1101 | 927 | 564.7 | 225.88 | 264.0407 | 392.7 | 347.8 | 338 | 320.3 | 641.6 | 49.8 | 19.3 | 88.5 | 5 | 254.3 | 6.6 | 816.1 | 845 | 797.8 | 813.5 | 842 | 768.6 | 722.5 | 795.8 | 800.8 | 776.9 | 132.5 | 231.3 | 297.7 | 274.9 | 370.7 | 351.7 | 275.9 | 324 | 451.2 | 284.4
1102 | 928 | 566.6 | 226.64 | 264.9291 | 393.6 | 348.4 | 336.6 | 319.5 | 656.7 | 49.8 | 19.3 | 88.7 | 5.7 | 258.6 | 7.3 | 815.8 | 848.9 | 797.5 | 813.2 | 843.3 | 768.3 | 724.9 | 798.6 | 800.3 | 778.1 | 132.8 | 231.5 | 297.9 | 275.2 | 370.8 | 352.1 | 276.2 | 324.2 | 451.4 | 284.6
1103 | 929 | 568.1 | 227.24 | 265.6305 | 393.7 | 348.3 | 335.4 | 318.9 | 640.8 | 49.9 | 19.3 | 88.6 | 5.3 | 258.4 | 7.2 | 815.4 | 848.4 | 798.8 | 812.7 | 843.5 | 768.5 | 741.8 | 802.3 | 800.1 | 780.4 | 133 | 231.8 | 298 | 275.4 | 371.2 | 352.9 | 276.3 | 324.4 | 451.6 | 284.8
1104 | 930 | 566.9 | 226.76 | 265.0694 | 393.7 | 348.3 | 334.9 | 318.4 | 634.7 | 49.9 | 19.3 | 88.7 | 5.4 | 247.5 | 6.8 | 815.3 | 851 | 798.6 | 812.7 | 844.3 | 768.4 | 752 | 806 | 799.6 | 780.7 | 133.3 | 232 | 298.2 | 275.6 | 371.5 | 353 | 276.6 | 324.6 | 451.6 | 285
1105 | 931 | 566 | 226.4 | 264.6486 | 393.7 | 348.7 | 335.8 | 318.6 | 647.5 | 50.1 | 19.3 | 88.8 | 6 | 252.1 | 6.3 | 815.1 | 854.5 | 796.3 | 813 | 844.3 | 768.5 | 758.2 | 808.5 | 798.8 | 781.8 | 133.5 | 232.2 | 298.6 | 275.9 | 372 | 353.3 | 276.9 | 324.7 | 451.7 | 285.1
1106 | 932 | 565.8 | 226.32 | 264.555 | 389.9 | 350 | 338.2 | 319.3 | 659.7 | 50.3 | 19.3 | 88.9 | 5.9 | 263.8 | 6.1 | 814.9 | 858.9 | 795.8 | 813.2 | 844.3 | 769 | 755 | 809 | 798.5 | 782.2 | 133.8 | 232.5 | 299 | 276.1 | 372.8 | 353.7 | 277.1 | 324.9 | 451.7 | 284.9
1107 | 933 | 566 | 226.4 | 264.6486 | 389.6 | 349.6 | 338.7 | 318.3 | 677 | 50.1 | 19.3 | 88.9 | 6 | 253.4 | 5.6 | 814.5 | 853.9 | 794.2 | 812.8 | 843.3 | 769.5 | 738.9 | 802.7 | 798.3 | 781 | 134.1 | 232.7 | 299.4 | 276.4 | 373.2 | 353.8 | 277.4 | 325 | 452.1 | 285.5
1108 | 934 | 565.8 | 226.32 | 264.555 | 389.4 | 350 | 337.7 | 318.2 | 684.6 | 50 | 19.3 | 88.8 | 5.9 | 237.1 | 5 | 814.2 | 847 | 793.8 | 812.4 | 843.1 | 770.3 | 726.1 | 792.2 | 798.1 | 780.3 | 134.3 | 232.9 | 299.5 | 276.6 | 373.7 | 354 | 277.7 | 325.1 | 452.5 | 286
1109 | 935 | 565.9 | 226.36 | 264.6018 | 388.5 | 350.2 | 337.5 | 318.9 | 665.7 | 49.9 | 19.3 | 88.7 | 5.6 | 238.6 | 4.5 | 813.8 | 847.2 | 792.9 | 812.6 | 844.7 | 770 | 724.9 | 794.4 | 798 | 782.3 | 134.6 | 233.1 | 299.5 | 276.9 | 374 | 354.1 | 277.9 | 325.3 | 452.6 | 286.3
1110 | 936 | 566.1 | 226.44 | 264.6953 | 388.6 | 350.4 | 336.8 | 319.8 | 666.5 | 49.9 | 19.3 | 88.6 | 6 | 230.5 | 4.8 | 813.6 | 847.2 | 793.6 | 812.8 | 845.3 | 769.8 | 726.7 | 797.1 | 797.8 | 783.2 | 134.9 | 233.4 | 299.9 | 277.2 | 374.2 | 354.6 | 278.1 | 325.5 | 452.6 | 286.5
1111 | 937 | 566.3 | 226.52 | 264.7888 | 389.2 | 350.7 | 336.2 | 320.2 | 669.5 | 49.9 | 19.3 | 88.5 | 5.7 | 234.1 | 5.2 | 813.6 | 849.7 | 796.2 | 813.7 | 844 | 769.6 | 729.5 | 798 | 798.2 | 780.6 | 135.1 | 233.6 | 300.3 | 277.5 | 374.3 | 354.8 | 278.4 | 325.6 | 452.6 | 286.7
1112 | 938 | 566 | 226.4 | 264.6486 | 389.8 | 351.1 | 335.8 | 320.6 | 680.3 | 49.9 | 19.3 | 88.3 | 5.6 | 238.6 | 5.6 | 813.4 | 851.2 | 798 | 813.5 | 844.1 | 769.7 | 727.4 | 795.3 | 798.1 | 779.8 | 135.4 | 233.8 | 300.6 | 277.7 | 374.2 | 354.7 | 278.6 | 325.8 | 452.9 | 287
1113 | 939 | 566.7 | 226.68 | 264.9759 | 390.6 | 351.9 | 336.4 | 320.7 | 677.9 | 49.9 | 19.3 | 88.2 | 5.3 | 236.7 | 5.1 | 813.7 | 851.9 | 798.4 | 814.1 | 843.5 | 769.6 | 718.6 | 790.6 | 798 | 778.8 | 135.6 | 234 | 300.9 | 278 | 374.4 | 354.7 | 278.8 | 325.8 | 453.1 | 287.2
1114 | 940 | 567.2 | 226.88 | 265.2096 | 389.8 | 352.8 | 337 | 320.9 | 678 | 50 | 19.3 | 88.2 | 5.8 | 249.2 | 4.8 | 813.8 | 843.2 | 796.5 | 813.9 | 839.5 | 770.1 | 701 | 775.7 | 798.4 | 776.4 | 135.9 | 234.2 | 301.3 | 278.3 | 374.5 | 354.6 | 279 | 325.9 | 453.3 | 287.4
1115 | 941 | 567 | 226.8 | 265.1161 | 390.5 | 353.6 | 336.8 | 320.3 | 680.4 | 50 | 19.3 | 88.2 | 5.9 | 243.4 | 4.8 | 813.8 | 841.2 | 796.8 | 813.9 | 838.9 | 770.2 | 694.4 | 774.8 | 798.8 | 773.3 | 136.2 | 234.4 | 301.5 | 278.6 | 374.8 | 354.8 | 279.2 | 326.1 | 453.5 | 287.7
1116 | 942 | 566.4 | 226.56 | 264.8356 | 390.8 | 353.2 | 338 | 319.9 | 673.8 | 50.1 | 19.3 | 88.3 | 6.3 | 232.9 | 4.8 | 813.5 | 845.6 | 797.1 | 813.8 | 839.7 | 769.4 | 707.1 | 781.2 | 799.1 | 774 | 136.4 | 234.7 | 301.3 | 278.9 | 374.9 | 354.8 | 279.4 | 326.1 | 453.7 | 287.9
1117 | 943 | 565.8 | 226.32 | 264.555 | 392 | 353 | 338.5 | 320 | 664.5 | 50.1 | 19.3 | 88.3 | 6.3 | 228.2 | 4.4 | 813.3 | 851.1 | 797.5 | 814.3 | 840.8 | 769 | 719.2 | 789.6 | 799.1 | 774.8 | 136.7 | 234.9 | 301.5 | 279.1 | 374.6 | 354.9 | 279.6 | 326.3 | 453.8 | 288.2
1118 | 944 | 566.5 | 226.6 | 264.8823 | 392.6 | 353.4 | 337.3 | 319.6 | 659.5 | 50.1 | 19.3 | 88.3 | 6.4 | 240.3 | 3.9 | 813.1 | 852.3 | 799 | 814 | 841.8 | 768.8 | 734.4 | 795.4 | 799 | 777 | 137 | 235.1 | 301.7 | 279.4 | 374.3 | 355 | 279.7 | 326.4 | 454 | 288.4
1119 | 945 | 567.4 | 226.96 | 265.3032 | 392.8 | 353.7 | 337.1 | 318.8 | 649.8 | 50.1 | 19.3 | 88.3 | 6.6 | 267.1 | 3.6 | 813.2 | 856.5 | 799.8 | 815.1 | 842.4 | 768.7 | 749.6 | 801.6 | 798.8 | 778.2 | 137.2 | 235.3 | 302 | 279.7 | 374.1 | 355.1 | 279.8 | 326.5 | 454.1 | 288.6
1120 | 946 | 566.8 | 226.72 | 265.0226 | 393.4 | 354.4 | 336.8 | 318.5 | 649.6 | 50.1 | 19.3 | 88.4 | 5.5 | 282.9 | 3.4 | 813.4 | 854.4 | 801.5 | 816.7 | 842.7 | 768.8 | 748.8 | 805 | 799 | 777.8 | 137.5 | 235.5 | 302.4 | 279.9 | 374 | 355.1 | 279.9 | 326.7 | 454.3 | 288.8
1121 | 947 | 566.9 | 226.76 | 265.0694 | 393.2 | 355.9 | 337 | 318.7 | 650.3 | 50.1 | 19.3 | 88.5 | 5.8 | 256 | 2.9 | 813.5 | 857.1 | 803 | 818.1 | 842.8 | 768.5 | 747.6 | 808.1 | 798.8 | 775.4 | 137.8 | 235.7 | 302.6 | 280.1 | 374.2 | 355.3 | 280.1 | 326.8 | 454.7 | 289
1122 | 948 | 567.6 | 227.04 | 265.3967 | 392.3 | 357.2 | 336.6 | 319.5 | 631.5 | 50.1 | 19.3 | 88.7 | 5.3 | 227.3 | 2.9 | 814.1 | 859.7 | 803.3 | 819.6 | 840 | 768.4 | 749.3 | 806.3 | 798.9 | 773.6 | 138 | 235.9 | 302.8 | 280.4 | 374.2 | 355.7 | 280.3 | 327 | 455 | 289.2
1123 | 949 | 567.3 | 226.92 | 265.2564 | 391.4 | 358.2 | 335.8 | 319.7 | 626 | 50 | 19.3 | 89 | 5.6 | 224.7 | 2.8 | 814.2 | 862 | 803.4 | 818.9 | 839.2 | 768.4 | 739.5 | 803.2 | 798.9 | 772 | 138.3 | 236.1 | 303.1 | 280.6 | 374 | 356.1 | 280.4 | 327.1 | 455.3 | 289.4
1124 | 950 | 567.2 | 226.88 | 265.2096 | 391.2 | 358.4 | 335.8 | 319.6 | 639.6 | 50 | 19.3 | 89.2 | 4.9 | 235.9 | 2.8 | 814 | 862.8 | 803.3 | 818 | 839.7 | 768 | 733.9 | 802.9 | 798.6 | 772.5 | 138.5 | 236.3 | 303.4 | 280.8 | 373.8 | 356 | 280.5 | 327.2 | 455.7 | 289.6
1125 | 951 | 567.1 | 226.84 | 265.1629 | 390.9 | 357.9 | 336.4 | 319.3 | 648.3 | 50 | 19.3 | 89.3 | 5.3 | 255.7 | 2.9 | 814 | 860.6 | 801.4 | 816.9 | 837.6 | 767.7 | 721.5 | 793.6 | 798.5 | 770.5 | 138.8 | 236.6 | 303.7 | 281 | 373.7 | 355.9 | 280.6 | 327.3 | 455.8 | 289.8
1126 | 952 | 567.4 | 226.96 | 265.3032 | 390.4 | 357.7 | 337.1 | 319.8 | 653.5 | 50 | 19.3 | 89.3 | 5.7 | 263.3 | 3.1 | 813.7 | 849.9 | 797 | 814.9 | 837.3 | 768 | 706.1 | 778 | 798.4 | 768.4 | 139 | 236.8 | 304.2 | 281.2 | 373.6 | 355.6 | 280.7 | 327.3 | 455.9 | 290
1127 | 953 | 566.9 | 226.76 | 265.0694 | 391.7 | 358 | 338.3 | 320.5 | 636 | 50 | 19.3 | 89.4 | 6.2 | 261.2 | 3.8 | 812.9 | 840.1 | 793.1 | 812.7 | 836.7 | 768.2 | 696.3 | 765.8 | 798.4 | 767.4 | 139.3 | 237 | 304.3 | 281.4 | 373.6 | 355.3 | 280.9 | 327.4 | 455.9 | 290.2
1128 | 954 | 566.8 | 226.72 | 265.0226 | 392.2 | 357.9 | 339.3 | 321.5 | 625.5 | 49.9 | 19.2 | 89.5 | 6.4 | 262.7 | 4.9 | 812.2 | 837.2 | 791.8 | 811.3 | 837.6 | 768.2 | 690.3 | 763.4 | 799 | 766.8 | 139.5 | 237.2 | 304.6 | 281.6 | 374 | 355.5 | 281.2 | 327.5 | 455.9 | 290.5
1129 | 955 | 566.6 | 226.64 | 264.9291 | 391.5 | 358.1 | 340 | 322.5 | 611.3 | 49.8 | 19.2 | 89.7 | 6.2 | 254.3 | 5.9 | 811.7 | 839.2 | 793.4 | 811 | 837.9 | 767.8 | 690.4 | 767.6 | 799.8 | 767.7 | 139.8 | 237.4 | 304.6 | 281.8 | 374.5 | 355.7 | 281.4 | 327.6 | 455.9 | 290.7
1130 | 956 | 566.9 | 226.76 | 265.0694 | 391.4 | 357.9 | 341.3 | 323 | 625.4 | 49.7 | 19.2 | 89.7 | 5.6 | 215.6 | 5.7 | 811.3 | 841 | 795 | 810.6 | 839.8 | 767.4 | 694.1 | 773.9 | 799.6 | 768 | 140 | 237.7 | 305 | 282 | 374.9 | 355.9 | 281.6 | 327.7 | 456 | 290.9
1131 | 957 | 564.6 | 225.84 | 263.9939 | 393.2 | 356.7 | 341.8 | 323.3 | 636.4 | 49.8 | 19.2 | 89.7 | 5.8 | 232.1 | 5.2 | 811 | 845.2 | 796.2 | 810.2 | 841.4 | 766.7 | 710.1 | 780.7 | 799 | 769.1 | 140.3 | 237.9 | 305.2 | 282.2 | 375.3 | 355.9 | 281.9 | 327.9 | 456.2 | 291.1
1132 | 958 | 564.8 | 225.92 | 264.0875 | 392.7 | 356.3 | 342 | 323.6 | 639 | 49.9 | 19.2 | 89.8 | 5.6 | 240.3 | 4.6 | 810.8 | 848.2 | 797.4 | 810.6 | 842 | 766.4 | 713.9 | 784.2 | 798.4 | 769.1 | 140.5 | 238.1 | 305.3 | 282.4 | 375.2 | 356 | 282 | 328 | 456.3 | 291.4
1133 | 959 | 563.4 | 225.36 | 263.4329 | 393 | 356.6 | 341.7 | 324 | 638 | 50 | 19.2 | 89.9 | 5.9 | 225.9 | 4.3 | 810.5 | 848.6 | 797.7 | 810.3 | 843.3 | 766.4 | 705.9 | 779.1 | 798 | 767.7 | 140.8 | 238.3 | 305.6 | 282.7 | 375.1 | 355.9 | 282.2 | 328.2 | 456.5 | 291.6
1134 | 960 | 564.1 | 225.64 | 263.7602 | 392.6 | 356.5 | 342.4 | 323.5 | 618.3 | 50 | 19.2 | 90 | 5.9 | 218.3 | 4.3 | 810.1 | 852.6 | 796.9 | 810.6 | 843.9 | 765.7 | 713.1 | 783.2 | 797.8 | 768.9 | 141 | 238.6 | 305.7 | 282.9 | 375 | 356 | 282.4 | 328.3 | 456.6 | 291.8
1135 | 961 | 564.3 | 225.72 | 263.8537 | 392.3 | 356.4 | 342.8 | 322.6 | 606.3 | 50.1 | 19.2 | 90 | 6.1 | 212.7 | 4 | 810 | 853.8 | 798.5 | 810.4 | 845.5 | 765.2 | 721 | 785.9 | 797.8 | 768.2 | 141.3 | 238.8 | 305.8 | 283.1 | 374.9 | 356.2 | 282.5 | 328.4 | 456.5 | 292
1136 | 962 | 566.2 | 226.48 | 264.7421 | 392.1 | 357 | 342.7 | 322.4 | 608 | 50.1 | 19.2 | 90 | 5.9 | 215.5 | 3.8 | 809.8 | 856.4 | 798.5 | 810.3 | 847.2 | 764.7 | 722.6 | 789.3 | 797.7 | 769.1 | 141.5 | 239 | 306 | 283.3 | 374.8 | 356.4 | 282.6 | 328.5 | 456.6 | 292.2
1137 | 963 | 567 | 226.8 | 265.1161 | 391.7 | 357.6 | 342.7 | 322.4 | 604.8 | 50.1 | 19.2 | 90.1 | 5.7 | 221.2 | 3.5 | 809.8 | 858.3 | 796.6 | 810.3 | 849.1 | 764 | 721.4 | 788.4 | 797.5 | 769.2 | 141.8 | 239.2 | 306.1 | 283.5 | 374.7 | 356.3 | 282.8 | 328.6 | 456.7 | 292.4
1138 | 964 | 566.1 | 226.44 | 264.6953 | 392.1 | 357.6 | 343 | 322.7 | 607 | 50 | 19.2 | 90.1 | 5.5 | 234.4 | 3.4 | 809.6 | 857.5 | 796.6 | 810.2 | 849.7 | 763.9 | 715.8 | 783 | 797.5 | 768.2 | 142 | 239.4 | 306.4 | 283.7 | 374.5 | 356 | 282.9 | 328.6 | 456.7 | 292.6
1139 | 965 | 565.9 | 226.36 | 264.6018 | 392.1 | 357 | 342.6 | 322.4 | 616.3 | 49.9 | 19.2 | 90.1 | 5.3 | 222.9 | 3.5 | 809.5 | 854.7 | 797 | 809.8 | 849.2 | 763.6 | 712.3 | 780.2 | 797.2 | 766.6 | 142.2 | 239.6 | 306.7 | 283.9 | 374.3 | 355.9 | 283 | 328.7 | 456.8 | 292.8
1140 | 966 | 565.7 | 226.28 | 264.5083 | 392.4 | 356.9 | 341.2 | 321.7 | 624.8 | 49.8 | 19.2 | 90.3 | 4.9 | 201.9 | 4.8 | 809.5 | 853.8 | 797.7 | 810 | 850 | 763.1 | 709.8 | 779.1 | 797 | 765.5 | 142.5 | 239.9 | 306.9 | 284.1 | 374 | 356 | 283.2 | 328.8 | 456.9 | 293
1141 | 967 | 566.2 | 226.48 | 264.7421 | 392.4 | 357.5 | 341 | 321.6 | 633.2 | 49.9 | 19.2 | 90.4 | 5.7 | 216.5 | 6.5 | 809.7 | 849.6 | 799.6 | 810.1 | 850.2 | 762.7 | 714.3 | 783.7 | 796.7 | 765.5 | 142.7 | 240.1 | 307.2 | 284.3 | 373.8 | 356.1 | 283.3 | 329 | 457 | 293.3
1142 | 968 | 565 | 226 | 264.181 | 391 | 358.4 | 341.8 | 321.3 | 638.7 | 50 | 19.2 | 90.6 | 5.6 | 198.6 | 7.1 | 810.1 | 848.6 | 800.9 | 811.3 | 847.3 | 762.4 | 711.2 | 782.7 | 797 | 763.6 | 142.9 | 240.3 | 307.3 | 284.5 | 373.7 | 356 | 283.4 | 329.1 | 457.1 | 293.4
1143 | 969 | 565.3 | 226.12 | 264.3213 | 389 | 360 | 342.1 | 321.7 | 647.5 | 50.1 | 19.2 | 90.7 | 5.5 | 217.3 | 7.4 | 810.3 | 850.3 | 802.2 | 812.4 | 845.8 | 762.5 | 711.7 | 787.1 | 797 | 762.5 | 143.1 | 240.5 | 307.6 | 284.7 | 373.7 | 355.7 | 283.6 | 329.1 | 457.4 | 293.6
1144 | 970 | 565.8 | 226.32 | 264.555 | 386.5 | 360.7 | 341.8 | 322.2 | 661.6 | 50.2 | 19.2 | 90.8 | 5.8 | 203 | 7.6 | 810.6 | 853.2 | 801.9 | 813.1 | 844.7 | 762.4 | 719.5 | 792.6 | 796.6 | 763.8 | 143.3 | 240.7 | 307.9 | 284.8 | 373.7 | 355.4 | 283.7 | 329.2 | 457.7 | 293.8
1145 | 971 | 566 | 226.4 | 264.6486 | 384.7 | 361.1 | 341.9 | 322.5 | 668.4 | 50.2 | 19.2 | 90.8 | 5.1 | 205.4 | 7.8 | 810.6 | 855 | 801.7 | 812.7 | 845.6 | 762.6 | 721.3 | 792.2 | 796.1 | 764.6 | 143.5 | 240.9 | 308.2 | 285 | 373.7 | 355.2 | 283.9 | 329.2 | 457.9 | 294
1146 | 972 | 565.2 | 226.08 | 264.2745 | 384.1 | 361.3 | 342.4 | 322.8 | 681.1 | 50.2 | 19.2 | 90.8 | 5.6 | 207.8 | 7.9 | 810.5 | 849 | 801.3 | 811.7 | 845.2 | 763 | 734.1 | 795.1 | 795.2 | 767.2 | 143.8 | 241.1 | 308.4 | 285.2 | 374 | 355.5 | 284.1 | 329.4 | 458.1 | 294.2
1147 | 973 | 565.5 | 226.2 | 264.4148 | 383.8 | 360.8 | 342.4 | 322.8 | 681.9 | 50.3 | 19.2 | 90.9 | 5 | 206.7 | 8.1 | 810.4 | 850.5 | 800.4 | 811.5 | 844.8 | 763.1 | 736.9 | 796.7 | 795 | 767.7 | 144 | 241.3 | 308.6 | 285.4 | 374.5 | 355.7 | 284.4 | 329.5 | 458.2 | 294.4
1148 | 974 | 565.8 | 226.32 | 264.555 | 383.4 | 360.2 | 342.4 | 322.7 | 695.5 | 50.4 | 19.2 | 90.9 | 5.1 | 209.1 | 8.3 | 810.3 | 850 | 799.7 | 810.6 | 842.2 | 763.8 | 736.7 | 797.1 | 794.6 | 767.1 | 144.2 | 241.5 | 309.1 | 285.6 | 375 | 356 | 284.7 | 329.5 | 458.4 | 294.7
1149 | 975 | 566.4 | 226.56 | 264.8356 | 383 | 360.5 | 342.7 | 322.9 | 710.5 | 50.4 | 19.2 | 91 | 5.1 | 210.3 | 8.5 | 810 | 846.8 | 795.1 | 810.1 | 838.4 | 764.8 | 718.8 | 786.1 | 794.4 | 765.6 | 144.4 | 241.7 | 309.5 | 285.9 | 375.4 | 355.9 | 285 | 329.6 | 458.7 | 294.9
1150 | 976 | 567.4 | 226.96 | 265.3032 | 383.9 | 360.6 | 342.1 | 323.2 | 712.1 | 50.5 | 19.2 | 91.2 | 5.8 | 210.4 | 8.1 | 809.6 | 834 | 792.1 | 808.9 | 834.3 | 765.8 | 702.5 | 773.5 | 794.8 | 763.7 | 144.6 | 241.9 | 310.3 | 286.1 | 376.1 | 356.1 | 285.3 | 329.6 | 458.8 | 295.1
1151 | 977 | 568.3 | 227.32 | 265.724 | 384.1 | 361.3 | 343.3 | 323.6 | 718.6 | 50.5 | 19.2 | 91.3 | 5.6 | 210.5 | 7.7 | 809.4 | 829.9 | 793.6 | 808.4 | 832.5 | 766.4 | 692.1 | 771.8 | 795.7 | 760.9 | 144.8 | 242.1 | 310.4 | 286.3 | 376.9 | 356.4 | 285.7 | 329.8 | 459 | 295.4
1152 | 978 | 568 | 227.2 | 265.5837 | 384.4 | 362 | 344.5 | 324.8 | 705.6 | 50.6 | 19.2 | 91.3 | 5.5 | 208 | 7.6 | 809.2 | 830.2 | 792.6 | 808 | 832.9 | 766.2 | 686 | 773.6 | 795.9 | 760.3 | 145 | 242.3 | 310.4 | 286.5 | 377.1 | 356.6 | 286 | 329.9 | 459.2 | 295.6
1153 | 979 | 572.6 | 229.04 | 267.7346 | 385.3 | 363 | 345.8 | 325 | 694.1 | 50.6 | 19.2 | 91.2 | 5.7 | 206.3 | 7.6 | 808.9 | 829.6 | 791.3 | 807.7 | 834.7 | 765.9 | 682.5 | 774.3 | 796 | 761.8 | 145.2 | 242.6 | 310.4 | 286.7 | 377.2 | 356.7 | 286.2 | 330.1 | 459.3 | 295.8
1154 | 980 | 594 | 237.6 | 277.7407 | 385.1 | 363.6 | 346.4 | 325.4 | 685.8 | 50.6 | 19.2 | 91 | 5.9 | 205.7 | 7.9 | 808.5 | 830.4 | 790.7 | 807.5 | 836.6 | 765.9 | 685.2 | 778 | 796.3 | 762.6 | 145.4 | 242.8 | 310.7 | 287 | 377.6 | 356.9 | 286.5 | 330.3 | 459.4 | 296
1155 | 981 | 625.6 | 250.24 | 292.5161 | 385.3 | 363.9 | 345.9 | 326.4 | 682.6 | 50.6 | 19.2 | 91 | 6.1 | 204.6 | 7.7 | 808 | 832.4 | 791.1 | 807.4 | 838.9 | 765.6 | 700.6 | 784.2 | 796.4 | 764.3 | 145.6 | 243 | 310.9 | 287.2 | 377.9 | 356.9 | 286.8 | 330.5 | 459.5 | 296.3
1156 | 982 | 641.9 | 256.76 | 300.1376 | 385.2 | 363.2 | 346.7 | 327.1 | 660.9 | 50.7 | 19.2 | 90.9 | 5.6 | 209.4 | 7.5 | 807.5 | 835.4 | 786.4 | 806.8 | 841.1 | 765.2 | 705.8 | 783.5 | 796.2 | 766.2 | 145.7 | 243.2 | 310.9 | 287.5 | 378.1 | 357.3 | 286.9 | 330.6 | 459.6 | 296.5
1157 | 983 | 649.8 | 259.92 | 303.8315 | 385.3 | 362.5 | 347.3 | 327.4 | 636.3 | 50.7 | 19.2 | 90.7 | 5.4 | 216.2 | 7.4 | 806.9 | 840.4 | 788.3 | 807 | 844.2 | 765 | 714.6 | 786.7 | 795.6 | 767.6 | 145.9 | 243.4 | 311.3 | 287.7 | 378.1 | 357.8 | 287.2 | 330.8 | 459.5 | 296.7
1158 | 984 | 650.1 | 260.04 | 303.9718 | 384.6 | 362.4 | 347.6 | 327.7 | 626 | 50.8 | 19.2 | 90.5 | 5.6 | 227.5 | 6.4 | 806.5 | 843.3 | 789.3 | 806.6 | 845.6 | 764.5 | 708.7 | 784.8 | 795.8 | 766.7 | 146.1 | 243.6 | 311.4 | 288 | 377.9 | 358.1 | 287.3 | 330.9 | 459.6 | 296.9
1159 | 985 | 649.5 | 259.8 | 303.6912 | 384.3 | 362.3 | 347.6 | 327 | 627.5 | 50.8 | 19.2 | 90.3 | 4.9 | 230.3 | 5 | 805.9 | 846 | 786.7 | 805.9 | 848.2 | 764.1 | 704.3 | 782.1 | 795.4 | 767.2 | 146.3 | 243.8 | 311.7 | 288.2 | 377.6 | 358.1 | 287.4 | 331.1 | 459.7 | 297.1
1160 | 986 | 646.4 | 258.56 | 302.2417 | 384.8 | 362.2 | 347.2 | 326.1 | 631.5 | 50.9 | 19.2 | 90.2 | 5.8 | 253.4 | 3.8 | 805.3 | 848.7 | 788.4 | 806.2 | 850 | 763.9 | 707.8 | 784.6 | 795 | 768.3 | 146.4 | 244 | 312.1 | 288.5 | 377.7 | 358.2 | 287.5 | 331.2 | 459.8 | 297.3
1161 | 987 | 644.4 | 257.76 | 301.3066 | 386.1 | 362.9 | 348.2 | 325.6 | 654.4 | 50.8 | 19.2 | 90.2 | 6.1 | 255.1 | 3.1 | 804.8 | 848.8 | 789.2 | 805.8 | 850.2 | 763.9 | 707.8 | 784.8 | 795 | 767.6 | 146.6 | 244.2 | 312.6 | 288.7 | 378.1 | 358.3 | 287.8 | 331.3 | 459.8 | 297.5
1162 | 988 | 641.7 | 256.68 | 300.0441 | 386.5 | 363.7 | 348 | 325.6 | 645.8 | 50.7 | 19.2 | 90.3 | 6.2 | 230 | 2.7 | 804.4 | 854.5 | 789.1 | 805.9 | 851 | 764 | 720.3 | 792 | 794.7 | 769.5 | 146.8 | 244.4 | 312.5 | 288.9 | 378.5 | 358.6 | 288.1 | 331.5 | 460 | 297.8
1163 | 989 | 640 | 256 | 299.2493 | 386 | 364.4 | 348.5 | 325.2 | 634.1 | 50.6 | 19.2 | 90.4 | 6.1 | 219.8 | 3.1 | 804 | 857.9 | 790.7 | 805.9 | 852.8 | 763.9 | 737.7 | 798.3 | 794.2 | 771.1 | 147 | 244.6 | 312.6 | 289.1 | 379 | 359.4 | 288.3 | 331.7 | 460.3 | 298
1164 | 990 | 639.2 | 255.68 | 298.8752 | 386.3 | 365 | 346.9 | 325.4 | 628.3 | 50.6 | 19.2 | 90.5 | 5.7 | 233.5 | 3.3 | 803.9 | 858.3 | 790.7 | 806 | 854.3 | 764.1 | 744.3 | 803.8 | 793.7 | 773.1 | 147.1 | 244.8 | 312.8 | 289.3 | 379.3 | 359.7 | 288.5 | 331.9 | 460.5 | 298.2
1165 | 991 | 641.1 | 256.44 | 299.7636 | 386.8 | 365 | 345.7 | 325.9 | 631.2 | 50.7 | 19.2 | 90.5 | 5.5 | 244.5 | 3.5 | 803.5 | 856.6 | 791.1 | 805.8 | 854.9 | 764.2 | 750.6 | 807.6 | 792.8 | 774.4 | 147.3 | 244.9 | 313.1 | 289.5 | 379.7 | 360.2 | 288.8 | 332.1 | 460.8 | 298.4
1166 | 992 | 641.7 | 256.68 | 300.0441 | 388.1 | 365 | 346.1 | 326.8 | 648.3 | 50.7 | 19.2 | 90.6 | 5.9 | 224.5 | 3.7 | 803.5 | 859.5 | 790.6 | 805.6 | 857.8 | 764.4 | 754.3 | 807.8 | 792.6 | 775.1 | 147.5 | 245.2 | 313.6 | 289.7 | 380.1 | 360.7 | 289 | 332.3 | 461 | 298.7
1167 | 993 | 644.3 | 257.72 | 301.2598 | 389.3 | 364.6 | 346.6 | 327.1 | 652.4 | 50.9 | 19.2 | 90.6 | 5.6 | 186.7 | 3.9 | 803.3 | 864.2 | 790.6 | 806 | 858.3 | 764.7 | 752.1 | 805.5 | 792.3 | 776 | 147.7 | 245.3 | 313.8 | 290 | 380.1 | 360.9 | 289.2 | 332.5 | 461.3 | 298.9
1168 | 994 | 643.5 | 257.4 | 300.8858 | 389.2 | 364.6 | 347.4 | 326.7 | 638.5 | 51 | 19.2 | 90.6 | 5.5 | 192.9 | 4.3 | 803.3 | 859.5 | 792.6 | 805.5 | 859.1 | 764.7 | 761.2 | 807.6 | 792.5 | 777.1 | 147.8 | 245.5 | 313.8 | 290.2 | 380.5 | 361.3 | 289.5 | 332.7 | 461.5 | 299.1
1169 | 995 | 644.5 | 257.8 | 301.3533 | 388.7 | 364.9 | 348.1 | 326 | 629.8 | 51.1 | 19.2 | 90.7 | 5.7 | 202.5 | 4.4 | 803.1 | 857.9 | 793.4 | 805.5 | 859.4 | 765 | 771 | 811.1 | 791.6 | 779.3 | 148 | 245.7 | 313.9 | 290.4 | 380.7 | 361.9 | 289.8 | 332.9 | 461.8 | 299.3
1170 | 996 | 647.5 | 259 | 302.7561 | 388.5 | 364.9 | 348.4 | 325.8 | 629 | 51.2 | 19.2 | 90.7 | 6.6 | 209.1 | 3.9 | 803.1 | 857.9 | 794.7 | 805.5 | 859.4 | 765.2 | 779.1 | 815.1 | 791.7 | 780.7 | 148.2 | 245.9 | 314.2 | 290.6 | 381 | 362.1 | 290.1 | 333.1 | 462 | 299.6
1171 | 997 | 647.5 | 259 | 302.7561 | 388.6 | 364.7 | 347.8 | 326 | 638.3 | 51.2 | 19.2 | 90.8 | 5.8 | 227.2 | 4.2 | 803.2 | 861.5 | 794.6 | 806 | 860.1 | 765.6 | 775.3 | 815.9 | 791.4 | 781.6 | 148.4 | 246.1 | 314.5 | 290.8 | 381.2 | 362.2 | 290.4 | 333.3 | 462.3 | 299.8
1172 | 998 | 648.9 | 259.56 | 303.4107 | 388.9 | 364.7 | 347.1 | 326 | 639.2 | 51.3 | 19.1 | 90.9 | 6.1 | 221.8 | 4.7 | 803.2 | 861 | 794.1 | 807 | 859.7 | 766.2 | 760.9 | 814 | 790.8 | 781.7 | 148.6 | 246.2 | 314.8 | 291 | 381.2 | 362.3 | 290.7 | 333.4 | 462.7 | 300
1173 | 999 | 648.3 | 259.32 | 303.1301 | 389.4 | 365.4 | 348.4 | 325.6 | 643.9 | 51.4 | 19.1 | 91.1 | 6 | 220.7 | 5 | 803.3 | 862.1 | 795.3 | 807.7 | 859.1 | 766.4 | 758.1 | 812.9 | 791.2 | 781.1 | 148.8 | 246.4 | 315.3 | 291.2 | 381.3 | 362.6 | 291 | 333.6 | 462.9 | 300.3
1174 | 1000 | 647.6 | 259.04 | 302.8028 | 389.1 | 366.2 | 350.6 | 325.4 | 656.1 | 51.4 | 19.2 | 91.2 | 5.3 | 221 | 4.7 | 803.4 | 857.7 | 796.1 | 807.9 | 860.3 | 766.3 | 760 | 814.3 | 791.6 | 781.3 | 149 | 246.6 | 315.5 | 291.3 | 381.4 | 362.8 | 291.2 | 333.8 | 463.1 | 300.5
1175 | 1001 | 646.8 | 258.72 | 302.4288 | 389.9 | 366.8 | 351.8 | 325.6 | 658 | 51.4 | 19.1 | 91.2 | 5.4 | 219.3 | 4.1 | 803.2 | 857.2 | 795 | 808 | 859.9 | 766.6 | 766.4 | 818.8 | 791.3 | 783.6 | 149.2 | 246.8 | 315.6 | 291.6 | 381.5 | 363.2 | 291.5 | 334 | 463.2 | 300.7
1176 | 1002 | 648.8 | 259.52 | 303.3639 | 391.4 | 367.2 | 350.9 | 324.8 | 661.9 | 51.4 | 19.1 | 91.3 | 5.5 | 210.5 | 3.7 | 803.2 | 862.1 | 794.2 | 808.7 | 859.8 | 767.3 | 767.9 | 821.2 | 791.4 | 784.6 | 149.4 | 247 | 316 | 291.8 | 381.7 | 363.4 | 291.7 | 334.3 | 463.3 | 300.9
1177 | 1003 | 649.2 | 259.68 | 303.551 | 392.3 | 367.6 | 350.4 | 324.6 | 675.9 | 51.5 | 19.1 | 91.4 | 5.8 | 190.3 | 4 | 803.4 | 865 | 794.3 | 809 | 859.1 | 768 | 776.1 | 823 | 791.5 | 786.3 | 149.6 | 247.1 | 316.3 | 292 | 382.4 | 363.9 | 292.1 | 334.5 | 463.5 | 301.2
1178 | 1004 | 649.1 | 259.64 | 303.5042 | 392.3 | 367.9 | 350.2 | 324.6 | 672.3 | 51.5 | 19.1 | 91.4 | 5.3 | 184.4 | 3.8 | 803.6 | 863 | 796 | 808.8 | 859 | 768.5 | 784.1 | 824.8 | 791.9 | 787 | 149.8 | 247.3 | 316.4 | 292.2 | 382.7 | 364.3 | 292.4 | 334.8 | 463.7 | 301.4
1179 | 1005 | 650.6 | 260.24 | 304.2056 | 392 | 368.4 | 349.6 | 324.5 | 682.8 | 51.6 | 19.2 | 91.5 | 5.4 | 209.7 | 4.3 | 803.4 | 872.9 | 794 | 808.9 | 857.9 | 769.4 | 767.6 | 818.8 | 792.4 | 786.9 | 150 | 247.5 | 316.9 | 292.4 | 383.1 | 364.7 | 292.7 | 334.9 | 464 | 301.6
1180 | 1006 | 650.1 | 260.04 | 303.9718 | 392.4 | 369 | 349.9 | 324.4 | 701.5 | 51.7 | 19.1 | 91.5 | 6.2 | 219.2 | 4.7 | 803.2 | 881.2 | 788.8 | 809.3 | 855.5 | 770.3 | 747.8 | 800.9 | 792.7 | 784.1 | 150.2 | 247.7 | 317.8 | 292.6 | 383.8 | 365 | 293.1 | 335 | 464.4 | 301.8
1181 | 1007 | 650 | 260 | 303.925 | 393 | 369.8 | 349.9 | 324.6 | 710.6 | 51.8 | 19.1 | 91.6 | 6.2 | 222.6 | 4.8 | 803.1 | 878.5 | 786.1 | 808.9 | 853.2 | 771.2 | 731.1 | 787 | 793.3 | 780.8 | 150.4 | 247.8 | 318.1 | 292.8 | 384.3 | 365.2 | 293.6 | 335.2 | 464.6 | 302.1
1182 | 1008 | 651.9 | 260.76 | 304.8134 | 393.4 | 370.4 | 350.8 | 325.7 | 711.8 | 51.9 | 19.1 | 91.7 | 6.2 | 220.6 | 4.9 | 802.6 | 874.7 | 783.1 | 808.2 | 852.4 | 771.2 | 726.9 | 791.3 | 793.6 | 782.3 | 150.7 | 248 | 318.3 | 293 | 385.1 | 365.6 | 294 | 335.4 | 464.9 | 302.3
1183 | 1009 | 650.3 | 260.12 | 304.0653 | 394.6 | 371.7 | 351.9 | 326.6 | 717.3 | 51.9 | 19.1 | 91.9 | 6.4 | 211.1 | 4.8 | 802.2 | 868.4 | 779.7 | 807.1 | 850.8 | 771.6 | 716 | 792 | 793.7 | 781.7 | 150.9 | 248.2 | 318.9 | 293.2 | 386.4 | 366.1 | 294.5 | 335.6 | 465.1 | 302.6
1184 | 1010 | 650.2 | 260.08 | 304.0185 | 396.4 | 372.3 | 352.2 | 327.1 | 728.3 | 52 | 19.1 | 92.1 | 6.6 | 199.4 | 4.8 | 801.6 | 859.7 | 777.9 | 806.3 | 849 | 772.1 | 714.8 | 788.1 | 794.3 | 780.5 | 151.1 | 248.3 | 319.3 | 293.4 | 387.8 | 366.5 | 295.1 | 335.8 | 465.3 | 302.8
1185 | 1011 | 650 | 260 | 303.925 | 397.3 | 373.1 | 353.3 | 328.3 | 735.7 | 52.1 | 19.1 | 92 | 6 | 196.7 | 5.1 | 801.2 | 845 | 776.1 | 805.2 | 845.8 | 772.6 | 707.4 | 779.7 | 795.2 | 778.3 | 151.3 | 248.5 | 319.9 | 293.7 | 389.1 | 366.9 | 295.7 | 336 | 465.5 | 303.1
1186 | 1012 | 652 | 260.8 | 304.8602 | 398.3 | 374.4 | 355.2 | 329.7 | 744.3 | 52.2 | 19.1 | 92.1 | 5.4 | 204.8 | 5.8 | 801.1 | 835.6 | 776.2 | 804.5 | 843.6 | 773.2 | 696.1 | 772.8 | 795.4 | 774.9 | 151.5 | 248.6 | 320.7 | 293.9 | 390.4 | 367.8 | 296.3 | 336.2 | 465.7 | 303.4
1187 | 1013 | 650.8 | 260.32 | 304.2991 | 399.5 | 375.7 | 356.4 | 331.1 | 747.9 | 52.2 | 19.1 | 92.1 | 5.4 | 203.5 | 6.6 | 801.3 | 839.8 | 778.8 | 805.3 | 843.3 | 772.9 | 695.9 | 777.7 | 796.2 | 773 | 151.7 | 248.8 | 320.5 | 294.2 | 391.2 | 368.4 | 296.7 | 336.5 | 466 | 303.7
1188 | 1014 | 648.8 | 259.52 | 303.3639 | 399.3 | 376.5 | 357 | 332.7 | 744.5 | 52.2 | 19.1 | 92.2 | 5.3 | 204.6 | 7.3 | 801.4 | 842.4 | 782 | 805.4 | 842.4 | 772.4 | 702.3 | 783.4 | 796 | 772.1 | 152 | 248.9 | 320.9 | 294.4 | 391.6 | 368.7 | 297.2 | 336.8 | 466.3 | 303.9
1189 | 1015 | 649.8 | 259.92 | 303.8315 | 399 | 377.6 | 356.9 | 333.9 | 732.4 | 52.3 | 19.1 | 92.3 | 5.6 | 198 | 7.5 | 801.3 | 843.8 | 785.6 | 805.6 | 842.6 | 771.8 | 720.5 | 792.7 | 796 | 774.1 | 152.2 | 249.1 | 321 | 294.7 | 392 | 369.3 | 297.6 | 337.1 | 466.8 | 304.2
1190 | 1016 | 649.5 | 259.8 | 303.6912 | 397.8 | 378.9 | 357 | 333.5 | 706.7 | 52.3 | 19.1 | 92.3 | 6 | 217.8 | 6.2 | 801.5 | 847.1 | 789.1 | 805.9 | 842.6 | 771.6 | 740.7 | 801.6 | 795.6 | 775.8 | 152.4 | 249.2 | 321.1 | 295 | 392.5 | 369.9 | 298 | 337.4 | 467.1 | 304.5
1191 | 1017 | 651.5 | 260.6 | 304.6264 | 397.1 | 379.5 | 356.7 | 333.4 | 680.3 | 52.4 | 19.1 | 92.3 | 5.3 | 264.7 | 5.1 | 801.4 | 849.1 | 791.5 | 808 | 841.3 | 771.8 | 742.3 | 802.8 | 795.7 | 774 | 152.6 | 249.4 | 321.4 | 295.3 | 392.9 | 370.1 | 298.4 | 337.7 | 467.5 | 304.7
1192 | 1018 | 652.1 | 260.84 | 304.9069 | 397.7 | 380.2 | 357.2 | 333.5 | 689.4 | 52.4 | 19.1 | 92.4 | 5 | 262.4 | 5 | 800.9 | 853.1 | 793.1 | 806.6 | 842.6 | 771.8 | 750.8 | 805.7 | 795.2 | 775.2 | 152.8 | 249.5 | 321.7 | 295.6 | 393.3 | 370 | 298.8 | 337.9 | 468.1 | 305
1193 | 1019 | 649.7 | 259.88 | 303.7847 | 398.7 | 380.2 | 357.1 | 333.5 | 686.3 | 52.4 | 19.1 | 92.5 | 5 | 247.4 | 5 | 800.7 | 855.6 | 794 | 806.2 | 844.2 | 771.9 | 752.8 | 810.5 | 794.7 | 778 | 153.1 | 249.6 | 321.8 | 295.9 | 393.8 | 370.1 | 299.1 | 338.1 | 468.4 | 305.3
1194 | 1020 | 652.3 | 260.92 | 305.0004 | 397.8 | 380 | 356.7 | 334.3 | 679.9 | 52.4 | 19.1 | 92.5 | 5.4 | 239.7 | 4.6 | 800.7 | 856.5 | 794.8 | 805.8 | 844.3 | 772 | 764.1 | 815.8 | 794.7 | 779.5 | 153.3 | 249.8 | 322 | 296.1 | 394.3 | 370.5 | 299.6 | 338.3 | 468.7 | 305.5
1195 | 1021 | 651.5 | 260.6 | 304.6264 | 397.8 | 380.1 | 356.4 | 334.9 | 669.5 | 52.3 | 19.1 | 92.5 | 5.7 | 236.9 | 4.6 | 800.9 | 854.3 | 796.6 | 806 | 844.9 | 772 | 775.7 | 820.4 | 794.4 | 779 | 153.5 | 249.9 | 322.2 | 296.4 | 394.5 | 370.9 | 300 | 338.7 | 469.1 | 305.8
1196 | 1022 | 651.4 | 260.56 | 304.5796 | 397.3 | 380.4 | 356 | 335.7 | 654.2 | 52.2 | 19.1 | 92.4 | 5.7 | 224.8 | 4.6 | 800.7 | 854.9 | 796.6 | 805.6 | 844.8 | 772.2 | 784.8 | 822.4 | 793.7 | 781.5 | 153.7 | 250.1 | 322.3 | 296.6 | 394.5 | 371 | 300.3 | 338.9 | 469.7 | 306.1
1197 | 1023 | 654 | 261.6 | 305.7953 | 396.4 | 381.1 | 356 | 336.4 | 653.5 | 52.1 | 19.1 | 92.5 | 5.5 | 211.4 | 4.3 | 800.6 | 852 | 796.5 | 805.1 | 846.2 | 772.7 | 791 | 823.6 | 793.1 | 783.5 | 153.9 | 250.2 | 322.6 | 296.9 | 394.7 | 371.3 | 300.6 | 339.1 | 470.1 | 306.3
1198 | 1024 | 652.7 | 261.08 | 305.1875 | 395.9 | 381.6 | 356.7 | 336.8 | 652.2 | 52 | 19.1 | 92.6 | 5.7 | 225.4 | 4.2 | 800.5 | 857.4 | 798.2 | 804.8 | 848.1 | 773 | 795.2 | 824.1 | 792.8 | 783.5 | 154.1 | 250.4 | 322.9 | 297.2 | 394.9 | 371.5 | 301.1 | 339.3 | 470.5 | 306.6
1199 | 1025 | 652.5 | 261 | 305.094 | 395.9 | 381.2 | 357.6 | 337.1 | 670 | 52 | 19.1 | 92.8 | 6.4 | 217.9 | 4.4 | 800.6 | 859.1 | 801.3 | 805.5 | 848 | 773.5 | 789 | 825.5 | 792.8 | 783.5 | 154.4 | 250.5 | 323.4 | 297.4 | 395.2 | 371.7 | 301.5 | 339.5 | 470.9 | 306.8
1200 | 1026 | 653.4 | 261.36 | 305.5148 | 395.5 | 380.7 | 357.5 | 337.9 | 683.9 | 52 | 19.1 | 92.8 | 6.3 | 208.6 | 4.9 | 800.5 | 857.9 | 801.2 | 805 | 849.8 | 773.6 | 787.5 | 823.1 | 792.8 | 784.4 | 154.6 | 250.7 | 323.6 | 297.7 | 395.6 | 371.8 | 301.8 | 339.7 | 471.4 | 307.1
1201 | 1027 | 652.2 | 260.88 | 304.9537 | 395.2 | 380.5 | 357.3 | 338.3 | 693.9 | 52.1 | 19.1 | 92.8 | 5.7 | 224.9 | 4.2 | 800.4 | 862 | 800.6 | 805.7 | 850.2 | 773.6 | 788 | 825.5 | 792.8 | 784.3 | 154.8 | 250.9 | 323.9 | 297.9 | 396 | 372.2 | 302.4 | 340 | 471.8 | 307.3
1202 | 1028 | 652.9 | 261.16 | 305.281 | 394 | 380.4 | 357.2 | 338.5 | 696.6 | 52.1 | 19.1 | 92.8 | 5.7 | 241.1 | 3.8 | 800.6 | 860.7 | 800.4 | 805.4 | 850.5 | 773.5 | 793 | 827.5 | 792.2 | 786.7 | 155 | 251 | 324.2 | 298.1 | 396.2 | 372.7 | 302.8 | 340.2 | 472.2 | 307.6
1203 | 1029 | 653.9 | 261.56 | 305.7486 | 393.7 | 380.6 | 356.6 | 338.6 | 685.7 | 52.1 | 19.1 | 92.9 | 5.9 | 210.3 | 4.5 | 800.7 | 860.1 | 801.1 | 805.7 | 850.2 | 773.7 | 800 | 828.3 | 791.8 | 787.9 | 155.2 | 251.2 | 324.2 | 298.4 | 396.4 | 373.2 | 303.1 | 340.6 | 472.5 | 307.8
1204 | 1030 | 654.2 | 261.68 | 305.8888 | 395.1 | 381.6 | 356.3 | 338.8 | 668.1 | 52.2 | 19.1 | 93 | 5.7 | 232.9 | 5.4 | 801.1 | 864.4 | 800.7 | 807.3 | 849.5 | 774.1 | 796.2 | 833.5 | 792.6 | 787.4 | 155.5 | 251.4 | 324.3 | 298.6 | 396.2 | 373.4 | 303.5 | 340.8 | 472.8 | 308.1
1205 | 1031 | 653 | 261.2 | 305.3278 | 397 | 382.4 | 357.1 | 338.3 | 672 | 52.2 | 19.1 | 93.1 | 5.6 | 233 | 5.7 | 801.4 | 863.5 | 801.3 | 807.3 | 850 | 774 | 797.6 | 836.8 | 792.7 | 788.8 | 155.7 | 251.5 | 324.7 | 298.8 | 396.4 | 373.5 | 303.9 | 341 | 473.1 | 308.3
1206 | 1032 | 653.4 | 261.36 | 305.5148 | 397.8 | 383.2 | 358.2 | 338.4 | 682.6 | 52.3 | 19.1 | 93.1 | 5.4 | 229.2 | 5.4 | 801.9 | 865 | 802.6 | 809.2 | 848.9 | 774 | 788.3 | 835.9 | 792.9 | 786.3 | 155.9 | 251.7 | 325.2 | 299.1 | 396.2 | 373.6 | 304.2 | 341.2 | 473.3 | 308.5
1207 | 1033 | 653.6 | 261.44 | 305.6083 | 398.6 | 383.9 | 358.3 | 338.9 | 702.8 | 52.3 | 19.1 | 93.1 | 5.3 | 238 | 4.7 | 802.1 | 868.1 | 802.5 | 811.5 | 846.4 | 773.9 | 774.5 | 828 | 792.8 | 784.1 | 156.1 | 251.9 | 325.8 | 299.3 | 396.4 | 373.7 | 304.5 | 341.4 | 473.8 | 308.8
1208 | 1034 | 652.9 | 261.16 | 305.281 | 399.3 | 384.6 | 359.2 | 338.9 | 711.8 | 52.3 | 19.1 | 93 | 6.3 | 239.4 | 4.3 | 802.2 | 870.8 | 801.5 | 812.2 | 846.1 | 774.5 | 767.1 | 820.4 | 792.7 | 783.6 | 156.3 | 252 | 326.3 | 299.5 | 396.8 | 373.8 | 304.9 | 341.5 | 474.3 | 309
1209 | 1035 | 655.1 | 262.04 | 306.3097 | 398.2 | 385.3 | 360.3 | 339.6 | 718.3 | 52.3 | 19.1 | 93 | 6.1 | 233.8 | 4.4 | 802.3 | 871.7 | 800.1 | 811.4 | 847 | 774.2 | 760.1 | 816 | 792.7 | 782.1 | 156.5 | 252.2 | 326.7 | 299.7 | 396.6 | 373.9 | 305.3 | 341.7 | 474.6 | 309.3
1210 | 1036 | 653.4 | 261.36 | 305.5148 | 397.4 | 385.8 | 360.4 | 339.8 | 719.1 | 52.3 | 19.1 | 92.9 | 6.4 | 253.8 | 5.5 | 802.1 | 874.5 | 798.5 | 810.9 | 849.3 | 774.2 | 760.8 | 816.1 | 793.5 | 783.1 | 156.8 | 252.4 | 326.7 | 299.8 | 396.3 | 374.2 | 305.6 | 341.9 | 474.8 | 309.5
1211 | 1037 | 653.5 | 261.4 | 305.5615 | 399.1 | 386 | 360.7 | 339.4 | 725.9 | 52.3 | 19.1 | 93 | 5.8 | 255.9 | 6.9 | 802 | 874.5 | 799 | 810.7 | 850 | 774.2 | 761.6 | 816.3 | 793.6 | 784.8 | 157 | 252.6 | 327.4 | 300 | 396.1 | 374.3 | 305.9 | 342.1 | 475 | 309.8
1212 | 1038 | 655.1 | 262.04 | 306.3097 | 398.8 | 386.4 | 361.3 | 338.7 | 737.7 | 52.3 | 19.1 | 93 | 5.9 | 247.7 | 7.6 | 802 | 875.4 | 799.1 | 810.6 | 850.5 | 774.5 | 754.9 | 814.4 | 793.6 | 784.5 | 157.2 | 252.8 | 327.9 | 300.2 | 396.2 | 374.2 | 306.2 | 342.2 | 475.3 | 310
1213 | 1039 | 654.8 | 261.92 | 306.1694 | 398.5 | 387.3 | 362.5 | 338.7 | 744.1 | 52.2 | 19.1 | 93.1 | 5.5 | 248.6 | 8 | 802 | 875 | 800.4 | 811.7 | 850.1 | 774.9 | 745.2 | 810.6 | 794 | 783.9 | 157.4 | 253 | 328.2 | 300.4 | 396.7 | 374 | 306.7 | 342.3 | 475.6 | 310.2
1214 | 1040 | 654.2 | 261.68 | 305.8888 | 398.5 | 387.8 | 362.8 | 340.1 | 748.8 | 52.2 | 19.1 | 93.4 | 5.7 | 243.5 | 7.6 | 802.3 | 879 | 800 | 811.5 | 850.9 | 774.7 | 743.9 | 810.5 | 794.7 | 782.3 | 157.6 | 253.1 | 328.3 | 300.6 | 397.4 | 374.5 | 307.1 | 342.5 | 475.9 | 310.5
1215 | 1041 | 655.1 | 262.04 | 306.3097 | 398.9 | 387.9 | 363.1 | 340.7 | 747.5 | 52.2 | 19.1 | 93.5 | 5.8 | 241.8 | 7.3 | 802.6 | 884.2 | 799.7 | 812.1 | 848.6 | 775.1 | 741.5 | 804.8 | 795.7 | 782.3 | 157.8 | 253.3 | 328.6 | 300.8 | 397.9 | 374.9 | 307.6 | 342.8 | 476.2 | 310.7
1216 | 1042 | 655.7 | 262.28 | 306.5902 | 399.9 | 388.2 | 362.6 | 341.1 | 742.5 | 52.3 | 19.1 | 93.6 | 5.5 | 243.7 | 7.1 | 803 | 879.6 | 800.2 | 812 | 848.9 | 775 | 746 | 809.2 | 796.1 | 781.8 | 158 | 253.5 | 329 | 301 | 398.2 | 375.4 | 308.1 | 343.1 | 476.7 | 311
1217 | 1043 | 656 | 262.4 | 306.7305 | 400.3 | 388 | 363.2 | 341.6 | 731.8 | 52.3 | 19.1 | 93.7 | 5.8 | 236.1 | 6.6 | 803.5 | 876.9 | 801.3 | 813.1 | 849.4 | 774.9 | 749.2 | 809.9 | 796.4 | 782.4 | 158.3 | 253.7 | 329.3 | 301.2 | 398.3 | 375.8 | 308.4 | 343.3 | 477 | 311.3
1218 | 1044 | 655.7 | 262.28 | 306.5902 | 400.6 | 388.5 | 364.5 | 342 | 727.3 | 52.3 | 19.1 | 93.8 | 6.1 | 235.5 | 5.7 | 803.5 | 881.5 | 798.2 | 812.9 | 849.5 | 774.8 | 744.5 | 807.8 | 796.1 | 781 | 158.5 | 253.9 | 329.7 | 301.4 | 398.3 | 375.7 | 308.7 | 343.5 | 477.3 | 311.5
1219 | 1045 | 655.5 | 262.2 | 306.4967 | 401.3 | 388.2 | 365.5 | 341.9 | 714.4 | 52.4 | 19.1 | 93.7 | 5.7 | 232.8 | 5.4 | 803.1 | 886.6 | 796.4 | 812.8 | 850 | 774.8 | 744.1 | 806.2 | 795.8 | 783.1 | 158.7 | 254.1 | 330 | 301.6 | 398.5 | 375.8 | 309.1 | 343.7 | 477.4 | 311.7
1220 | 1046 | 657.3 | 262.92 | 307.3383 | 402 | 388.4 | 365.4 | 341.4 | 709.4 | 52.4 | 19.1 | 93.7 | 5.9 | 232.6 | 6 | 803 | 884.1 | 796 | 812.3 | 849.9 | 775 | 737.9 | 800 | 795.8 | 782.5 | 158.9 | 254.3 | 330.3 | 301.8 | 398.7 | 375.7 | 309.5 | 343.9 | 477.5 | 312
1221 | 1047 | 656.9 | 262.76 | 307.1513 | 403.5 | 388.2 | 365.8 | 340.3 | 712.4 | 52.4 | 19.1 | 93.7 | 6.1 | 231.7 | 6.1 | 803.4 | 881.7 | 796.7 | 813.1 | 849.4 | 774.9 | 736.1 | 802.5 | 796.5 | 781.5 | 159.1 | 254.5 | 330.8 | 302 | 399 | 375.7 | 309.9 | 344.1 | 477.7 | 312.3
1222 | 1048 | 656.5 | 262.6 | 306.9643 | 404.5 | 388.7 | 365.7 | 340.1 | 712.9 | 52.5 | 19.1 | 93.8 | 5.9 | 228.8 | 6.1 | 803.8 | 874.4 | 797.5 | 812.7 | 850.9 | 774.9 | 748.8 | 807.1 | 796.3 | 783.4 | 159.4 | 254.7 | 330.8 | 302.1 | 399.4 | 375.8 | 310.3 | 344.3 | 478.1 | 312.5
1223 | 1049 | 657.5 | 263 | 307.4318 | 404.4 | 388.9 | 366.3 | 339.8 | 719.6 | 52.5 | 19.1 | 93.8 | 5.7 | 240.5 | 6.4 | 803.8 | 874.3 | 797.9 | 812.5 | 852 | 774.8 | 750.7 | 809.4 | 796.3 | 784.2 | 159.6 | 254.8 | 331.1 | 302.3 | 399.5 | 376 | 310.7 | 344.5 | 478.5 | 312.8
1224 | 1050 | 657.6 | 263.04 | 307.4786 | 403.5 | 387.5 | 366.8 | 340 | 729.9 | 52.6 | 19.1 | 93.8 | 5.1 | 246.9 | 6.8 | 803.8 | 875.2 | 796.1 | 812.9 | 852.5 | 774.8 | 750.1 | 813.2 | 795.7 | 784.1 | 159.8 | 255.1 | 331.5 | 302.6 | 399.5 | 376.2 | 311.1 | 344.7 | 478.8 | 313
1225 | 1051 | 656.8 | 262.72 | 307.1045 | 402.9 | 387.6 | 366 | 340.9 | 729.1 | 52.6 | 19.1 | 93.8 | 5.4 | 231.7 | 6.6 | 803.8 | 870.5 | 798.1 | 813.1 | 853.7 | 774.9 | 756.9 | 817.9 | 795.8 | 785.5 | 160 | 255.3 | 331.9 | 302.7 | 399.8 | 376.7 | 311.5 | 345 | 479 | 313.3
1226 | 1052 | 657 | 262.8 | 307.1981 | 403.4 | 388.3 | 366.2 | 340.9 | 726.8 | 52.5 | 19.1 | 93.8 | 5.7 | 237.7 | 6.4 | 803.9 | 873.6 | 796.9 | 812.8 | 852.6 | 775.4 | 751.1 | 816.4 | 796.3 | 785.7 | 160.2 | 255.4 | 332.3 | 302.9 | 399.8 | 376.9 | 311.7 | 345.2 | 479.3 | 313.5
1227 | 1053 | 657.6 | 263.04 | 307.4786 | 404.4 | 388.9 | 366.9 | 340.8 | 742.6 | 52.5 | 19.1 | 93.7 | 5 | 240.9 | 6 | 803.8 | 877.2 | 791.2 | 812 | 851.1 | 776.2 | 738.3 | 807.1 | 796.3 | 785 | 160.4 | 255.6 | 332.9 | 303.1 | 400.1 | 376.8 | 312.2 | 345.3 | 479.7 | 313.7
1228 | 1054 | 656.2 | 262.48 | 306.824 | 406 | 389.4 | 367.5 | 340 | 752.4 | 52.5 | 19.1 | 93.7 | 5.4 | 234.8 | 5.8 | 803.4 | 876.4 | 786 | 809.5 | 847.5 | 777.6 | 722 | 784 | 796.3 | 783.2 | 160.7 | 255.8 | 333.6 | 303.3 | 401 | 376.7 | 312.7 | 345.5 | 480 | 314
1229 | 1055 | 655.6 | 262.24 | 306.5435 | 407.3 | 390.3 | 367.3 | 340.4 | 751.8 | 52.4 | 19 | 93.7 | 5.2 | 240.5 | 5.9 | 803.2 | 867 | 786.2 | 809.3 | 845.9 | 778 | 715.6 | 783.4 | 797 | 782.9 | 160.9 | 256 | 333.7 | 303.5 | 401.9 | 376.7 | 313.2 | 345.7 | 480.2 | 314.3
1230 | 1056 | 656.9 | 262.76 | 307.1513 | 407.9 | 391 | 367.9 | 341.2 | 756.5 | 52.4 | 19 | 93.8 | 5.2 | 240.3 | 6 | 803.4 | 857.1 | 787.1 | 808.8 | 844.5 | 778.7 | 706.7 | 780.2 | 797.4 | 781.7 | 161.1 | 256.2 | 334.1 | 303.6 | 402.9 | 376.9 | 313.8 | 345.9 | 480.4 | 314.6
1231 | 1057 | 657.6 | 263.04 | 307.4786 | 408.3 | 392 | 366.9 | 342.4 | 761.3 | 52.3 | 19 | 93.8 | 5 | 243.4 | 5.6 | 803.3 | 856.2 | 787.5 | 808.3 | 844.1 | 778.5 | 710 | 788.4 | 797.8 | 781.3 | 161.3 | 256.4 | 334.5 | 303.8 | 403.8 | 377.2 | 314.3 | 346.2 | 480.7 | 314.9
1232 | 1058 | 657 | 262.8 | 307.1981 | 409.3 | 393.6 | 367.5 | 343.1 | 762.3 | 52.3 | 19 | 93.9 | 5.9 | 243.1 | 5.3 | 803.1 | 859.3 | 787.8 | 808.9 | 842.3 | 778.2 | 712.5 | 792.5 | 797.8 | 782.6 | 161.6 | 256.7 | 334.7 | 304 | 404.6 | 377.6 | 314.8 | 346.4 | 481.1 | 315.2
1233 | 1059 | 656.7 | 262.68 | 307.0578 | 408.6 | 395.3 | 368.1 | 342.9 | 763.8 | 52.3 | 19 | 93.8 | 5.9 | 226.6 | 5 | 803.5 | 860.8 | 790.8 | 809.9 | 842.8 | 778.1 | 723.3 | 798.4 | 798.5 | 783.4 | 161.8 | 256.9 | 334.9 | 304.2 | 405 | 378.1 | 315.3 | 346.7 | 481.4 | 315.5
1234 | 1060 | 657.1 | 262.84 | 307.2448 | 408.2 | 395.6 | 367.2 | 342.7 | 757.9 | 52.4 | 19 | 93.8 | 5.8 | 244.6 | 4.2 | 803.8 | 860.9 | 792 | 809.4 | 843.7 | 778.4 | 723.9 | 800.1 | 798.3 | 784.2 | 162 | 257.1 | 335.3 | 304.4 | 405.5 | 378.6 | 315.7 | 347 | 481.8 | 315.7
1235 | 1061 | 657.3 | 262.92 | 307.3383 | 408.1 | 394.9 | 366.6 | 343.9 | 745.7 | 52.4 | 19 | 93.8 | 5.9 | 278.8 | 4.3 | 803.8 | 868.9 | 791.4 | 810.1 | 845.5 | 778.2 | 729.5 | 804.9 | 797.6 | 786 | 162.2 | 257.3 | 335.5 | 304.6 | 405.7 | 379 | 316.1 | 347.2 | 482.2 | 316
1236 | 1062 | 658 | 263.2 | 307.6656 | 408.1 | 393.9 | 367.6 | 344.8 | 718.5 | 52.5 | 19 | 93.8 | 5.8 | 277.3 | 4.5 | 803.7 | 869 | 791 | 810 | 846.3 | 778.2 | 726.7 | 801.4 | 797.7 | 786.5 | 162.4 | 257.5 | 335.7 | 304.8 | 405.5 | 379.2 | 316.5 | 347.4 | 482.3 | 316.3
1237 | 1063 | 659.1 | 263.64 | 308.18 | 408.6 | 392.7 | 368.1 | 345.1 | 703.4 | 52.6 | 19 | 93.7 | 5.9 | 252.4 | 5 | 803.5 | 867.6 | 790.6 | 809.8 | 848.7 | 777.7 | 732 | 802.7 | 797.7 | 787.2 | 162.6 | 257.7 | 336.1 | 304.9 | 405.2 | 379.2 | 316.8 | 347.6 | 482.4 | 316.5
1238 | 1064 | 661.5 | 264.6 | 309.3022 | 408.9 | 391.5 | 368.1 | 344.8 | 690.4 | 52.6 | 19 | 93.6 | 6 | 253.7 | 5.1 | 803.3 | 869.5 | 791.7 | 809.9 | 851.3 | 777.2 | 737.1 | 804.1 | 797.6 | 788.2 | 162.9 | 257.9 | 336 | 305.1 | 404.6 | 379.4 | 317 | 347.9 | 482.5 | 316.8
1239 | 1065 | 660.6 | 264.24 | 308.8813 | 409.6 | 390.6 | 367.6 | 343.8 | 673.6 | 52.6 | 19 | 93.8 | 6.1 | 251.9 | 4.7 | 803.1 | 871.6 | 790.5 | 810.2 | 853 | 776.5 | 745.1 | 806.6 | 797.6 | 789.6 | 163.1 | 258.1 | 336 | 305.2 | 404.2 | 379.5 | 317.1 | 348.1 | 482.5 | 317
1240 | 1066 | 659 | 263.6 | 308.1332 | 409.9 | 388.6 | 367 | 343 | 662.4 | 52.7 | 19 | 94 | 6.1 | 261.8 | 4.2 | 803.1 | 875.4 | 789.7 | 810.4 | 854.2 | 775.9 | 746.7 | 806.9 | 797.8 | 790.3 | 163.3 | 258.3 | 336.4 | 305.4 | 403.7 | 379.7 | 317.3 | 348.3 | 482.6 | 317.2
1241 | 1067 | 656.9 | 262.76 | 307.1513 | 411.3 | 388 | 365.6 | 341.9 | 670.7 | 52.7 | 19 | 94.3 | 6.1 | 266.4 | 3.5 | 803 | 872.8 | 788.5 | 810.2 | 855.2 | 775.8 | 741.7 | 806.9 | 797.5 | 791 | 163.5 | 258.6 | 336.7 | 305.5 | 403.2 | 379.5 | 317.5 | 348.4 | 482.7 | 317.4
1242 | 1068 | 658.4 | 263.36 | 307.8527 | 412.3 | 387.5 | 364.8 | 340.5 | 668.9 | 52.8 | 19 | 94.7 | 6.4 | 239.8 | 3.7 | 802.9 | 870.2 | 788.6 | 810 | 856.3 | 775.3 | 753.6 | 809.5 | 797.4 | 791.9 | 163.8 | 258.8 | 336.9 | 305.7 | 403.3 | 379.8 | 317.8 | 348.5 | 482.9 | 317.6
1243 | 1069 | 660 | 264 | 308.6008 | 412.6 | 387.7 | 363.9 | 339.8 | 662.4 | 52.8 | 19 | 95 | 6 | 227.6 | 4.3 | 802.6 | 872.9 | 787.9 | 809.4 | 857.7 | 775.2 | 755.4 | 810.9 | 797.2 | 792.7 | 164 | 259 | 337.1 | 305.8 | 403.1 | 380.2 | 318 | 348.7 | 483 | 317.8
1244 | 1070 | 661.9 | 264.76 | 309.4892 | 412.6 | 387.3 | 363.9 | 339.8 | 655.1 | 52.8 | 19 | 95.2 | 5.9 | 238.2 | 3.9 | 802.3 | 873.8 | 788.2 | 808.9 | 858.6 | 775.5 | 758.3 | 809.6 | 796.5 | 793.7 | 164.2 | 259.2 | 337.1 | 305.9 | 403 | 380.8 | 318.3 | 349 | 483.2 | 318.1
1245 | 1071 | 662.8 | 265.12 | 309.91 | 413 | 386.3 | 363.8 | 339.2 | 640.6 | 52.8 | 19 | 95.4 | 5.6 | 246.5 | 3.4 | 802.4 | 875.1 | 789.9 | 808.6 | 859.5 | 775.3 | 767.9 | 813.3 | 796.3 | 794.3 | 164.5 | 259.4 | 337.2 | 306 | 402.8 | 381.5 | 318.6 | 349.3 | 483.3 | 318.3
1246 | 1072 | 660.3 | 264.12 | 308.7411 | 412.5 | 385.9 | 364.1 | 338.5 | 649.5 | 52.8 | 19 | 95.5 | 6.2 | 249.1 | 3.1 | 802.5 | 870.7 | 791.9 | 808.2 | 860.6 | 775 | 775.6 | 817.4 | 796.5 | 795.1 | 164.7 | 259.6 | 337.8 | 306.1 | 402.7 | 381.8 | 318.8 | 349.6 | 483.4 | 318.6
1247 | 1073 | 659.1 | 263.64 | 308.18 | 412 | 386.2 | 363.8 | 337.6 | 668.1 | 52.9 | 19 | 95.5 | 5.2 | 247.5 | 3 | 802.7 | 867.6 | 793 | 808.9 | 859.8 | 774.8 | 774.6 | 818.6 | 796.1 | 795.4 | 164.9 | 259.9 | 338.1 | 306.2 | 402.8 | 381.9 | 319 | 349.7 | 483.6 | 318.8
1248 | 1074 | 659.1 | 263.64 | 308.18 | 411 | 388 | 363.6 | 337.7 | 684.2 | 53 | 19 | 95.5 | 5.2 | 249.6 | 3.3 | 803.1 | 866.3 | 794.5 | 809.1 | 859.4 | 774.9 | 772.9 | 821.2 | 795.8 | 795.8 | 165.1 | 260.1 | 338.4 | 306.3 | 402.9 | 382 | 319.3 | 349.9 | 483.8 | 319
1249 | 1075 | 658.9 | 263.56 | 308.0865 | 409.6 | 389.6 | 363.5 | 337.5 | 705.3 | 53.1 | 19 | 95.5 | 5.5 | 248.4 | 3.5 | 803.2 | 874 | 792.3 | 809.3 | 859.4 | 775.3 | 764.8 | 814.9 | 794.8 | 795.2 | 165.4 | 260.3 | 338.9 | 306.4 | 403.6 | 382.1 | 319.7 | 350 | 484.1 | 319.3
1250 | 1076 | 658.7 | 263.48 | 307.9929 | 408.2 | 390.6 | 364.1 | 337.6 | 723.8 | 53.2 | 19 | 95.6 | 5.5 | 234 | 3.5 | 803.3 | 869.5 | 791.9 | 809.3 | 856.7 | 775.9 | 753.3 | 809.9 | 794.4 | 794.9 | 165.6 | 260.5 | 339.7 | 306.5 | 404.2 | 382.7 | 320.2 | 350.2 | 484.4 | 319.5
1251 | 1077 | 658.8 | 263.52 | 308.0397 | 406.9 | 390.8 | 363.7 | 338.1 | 730.1 | 53.2 | 19 | 95.8 | 5.3 | 230 | 3.7 | 803.6 | 867.6 | 793.3 | 810 | 854.2 | 776.1 | 748.3 | 808.2 | 795.3 | 792.8 | 165.8 | 260.7 | 339.7 | 306.6 | 404.5 | 383.1 | 320.7 | 350.5 | 484.8 | 319.8
1252 | 1078 | 660.8 | 264.32 | 308.9749 | 406.2 | 390.4 | 364.9 | 339 | 725.6 | 53.2 | 19 | 95.9 | 5.1 | 243.3 | 4.1 | 804.2 | 866.1 | 796 | 811.1 | 853.4 | 776.1 | 754.5 | 813 | 796.3 | 793.7 | 166.1 | 260.9 | 339.6 | 306.7 | 404.7 | 383.6 | 321.1 | 350.8 | 485.1 | 320.1
1253 | 1079 | 659.9 | 263.96 | 308.554 | 406 | 390.9 | 365.2 | 339.6 | 714.3 | 53.2 | 19 | 95.9 | 5.5 | 259.8 | 4.2 | 804.2 | 867.5 | 794.9 | 810.7 | 852.7 | 776.1 | 762.2 | 818.3 | 796.3 | 795.6 | 166.3 | 261.1 | 339.8 | 306.8 | 405 | 384 | 321.6 | 351.1 | 485.6 | 320.3
1254 | 1080 | 661.1 | 264.44 | 309.1151 | 406.8 | 390.7 | 365.3 | 340.3 | 720.3 | 53.3 | 19 | 95.8 | 5.5 | 260.9 | 4.2 | 804.1 | 874.2 | 790.6 | 810.5 | 852.6 | 776.1 | 751.7 | 814.4 | 795.4 | 796.3 | 166.5 | 261.3 | 340.3 | 307 | 405.2 | 384.1 | 321.9 | 351.2 | 486 | 320.5
1255 | 1081 | 659.4 | 263.76 | 308.3202 | 409 | 391.2 | 365.6 | 341.6 | 722.2 | 53.4 | 19 | 95.8 | 6.2 | 255 | 4.5 | 803.8 | 870.5 | 789.7 | 809.5 | 852.8 | 776.5 | 742.5 | 807.3 | 795.6 | 795.5 | 166.8 | 261.6 | 340.9 | 307.1 | 405.7 | 384.2 | 322.3 | 351.4 | 486.2 | 320.8
1256 | 1082 | 658.9 | 263.56 | 308.0865 | 410 | 390.4 | 367 | 343.2 | 722.9 | 53.4 | 19 | 95.8 | 5.6 | 254.1 | 4.8 | 803.5 | 863.6 | 790.9 | 809.2 | 853.1 | 776.2 | 757.3 | 811.7 | 795.6 | 796.8 | 167 | 261.8 | 340.8 | 307.3 | 405.9 | 384.3 | 322.6 | 351.6 | 486.3 | 321
1257 | 1083 | 660.7 | 264.28 | 308.9281 | 411.4 | 389.6 | 366.8 | 343.8 | 726.8 | 53.5 | 19 | 95.8 | 5.8 | 237.5 | 4.8 | 803.3 | 862.9 | 792.4 | 808.1 | 852.6 | 776.5 | 775.2 | 815.9 | 795.6 | 798 | 167.2 | 262 | 341.1 | 307.4 | 406.4 | 384.4 | 323.1 | 351.8 | 486.4 | 321.3
1258 | 1084 | 658.4 | 263.36 | 307.8527 | 411.3 | 390.1 | 365.7 | 343.9 | 727.7 | 53.5 | 19 | 95.9 | 6.2 | 230.1 | 5.3 | 803.3 | 862.1 | 792.9 | 807.6 | 852.4 | 776.4 | 786.3 | 818.6 | 795 | 798.8 | 167.5 | 262.2 | 341.2 | 307.6 | 406.9 | 384.8 | 323.5 | 352.1 | 486.8 | 321.5
1259 | 1085 | 659 | 263.6 | 308.1332 | 410.8 | 391.2 | 365.9 | 344.8 | 721.3 | 53.5 | 19 | 96 | 6.2 | 265.9 | 5.5 | 803.6 | 856.3 | 795.8 | 808.4 | 851 | 776.3 | 782.7 | 822.2 | 794.9 | 797.3 | 167.7 | 262.4 | 341.6 | 307.8 | 406.9 | 384.8 | 323.9 | 352.3 | 487.1 | 321.8
1260 | 1086 | 660.5 | 264.2 | 308.8346 | 410.8 | 392.3 | 365.7 | 344.6 | 727.6 | 53.6 | 19 | 96 | 5.9 | 246.7 | 5.5 | 803.8 | 859.8 | 797.2 | 810.7 | 851.2 | 776.7 | 770.5 | 818.7 | 794.6 | 795.4 | 167.9 | 262.6 | 342.3 | 308 | 407.3 | 384.9 | 324.2 | 352.5 | 487.6 | 322
1261 | 1087 | 661.7 | 264.68 | 309.3957 | 410.5 | 393.2 | 366.7 | 344.7 | 731.3 | 53.7 | 19 | 95.9 | 6.2 | 224.3 | 5.4 | 804.1 | 861.3 | 796.3 | 809.9 | 851.9 | 776.4 | 767.7 | 820.5 | 794 | 797 | 168.2 | 262.8 | 342.3 | 308.2 | 407.9 | 384.8 | 324.6 | 352.7 | 488 | 322.3
1262 | 1088 | 661.6 | 264.64 | 309.3489 | 412.6 | 393.6 | 367.1 | 344.7 | 722.5 | 53.8 | 19 | 95.9 | 6.2 | 238 | 5.2 | 804.1 | 864.9 | 796.4 | 810.3 | 853.5 | 776.5 | 779.4 | 828.6 | 793.8 | 799.1 | 168.4 | 263 | 342.4 | 308.3 | 408.1 | 384.9 | 325 | 352.9 | 488.2 | 322.5
1263 | 1089 | 662 | 264.8 | 309.5359 | 413.7 | 394.7 | 367.2 | 345.4 | 710.1 | 53.8 | 19 | 96 | 6.6 | 250.5 | 4.8 | 804.1 | 864 | 797.1 | 809.6 | 852.1 | 776.4 | 775 | 826.9 | 793.7 | 800.6 | 168.6 | 263.2 | 342.9 | 308.5 | 408.3 | 384.9 | 325.4 | 353.1 | 488.3 | 322.8
1264 | 1090 | 662.8 | 265.12 | 309.91 | 414.2 | 395.7 | 367.2 | 345.6 | 717.8 | 53.9 | 19 | 96 | 6.2 | 253.8 | 4.4 | 804 | 860.6 | 797 | 809.2 | 852.6 | 776.5 | 781.4 | 826.8 | 793.4 | 802 | 168.9 | 263.5 | 343.2 | 308.7 | 408.9 | 385.2 | 325.9 | 353.3 | 488.6 | 323
1265 | 1091 | 664.2 | 265.68 | 310.5646 | 415.2 | 396.8 | 368.6 | 345.1 | 715.3 | 53.9 | 19 | 96.1 | 6.4 | 256.4 | 4 | 804.1 | 855.2 | 796.8 | 809.3 | 853.8 | 776.5 | 791.1 | 829.9 | 793.8 | 802.6 | 169.1 | 263.7 | 343.2 | 308.9 | 409.2 | 385.5 | 326.2 | 353.6 | 488.8 | 323.3
1266 | 1092 | 663.6 | 265.44 | 310.2841 | 415.3 | 396.3 | 368.8 | 345.1 | 714.1 | 54 | 19 | 96.1 | 5.9 | 239.4 | 3.4 | 804.3 | 852.6 | 796.6 | 808.3 | 853.8 | 776.8 | 795.3 | 830 | 793.5 | 803.6 | 169.4 | 263.9 | 343.6 | 309.1 | 409.1 | 385.6 | 326.6 | 353.9 | 489.1 | 323.6
1267 | 1093 | 660.9 | 264.36 | 309.0216 | 414.9 | 396.1 | 367.8 | 344.8 | 727.4 | 54 | 19 | 96 | 6.1 | 209 | 3.3 | 804 | 855.5 | 792.7 | 808.4 | 852.8 | 776.8 | 795.4 | 831.3 | 792.5 | 804.6 | 169.6 | 264.1 | 344 | 309.3 | 409.7 | 385.8 | 327.1 | 354.1 | 489.7 | 323.8
1268 | 1094 | 660.5 | 264.2 | 308.8346 | 413.5 | 396.2 | 367.6 | 345.3 | 736.1 | 54 | 19 | 96.1 | 6.2 | 196.7 | 3.3 | 803.5 | 855.1 | 791.6 | 808.3 | 852.2 | 777 | 791.7 | 834.8 | 792 | 805.9 | 169.8 | 264.3 | 344.3 | 309.5 | 410.2 | 385.9 | 327.6 | 354.3 | 490 | 324.1
1269 | 1095 | 661 | 264.4 | 309.0684 | 415 | 396.7 | 366.7 | 345.2 | 743.9 | 54 | 19 | 96.1 | 5.8 | 214.2 | 3.6 | 803.5 | 857.2 | 791.8 | 808.4 | 850.8 | 777.5 | 793 | 831.6 | 792.4 | 805.4 | 170.1 | 264.5 | 344.7 | 309.8 | 410.9 | 386.2 | 328 | 354.5 | 490.1 | 324.3
1270 | 1096 | 659.8 | 263.92 | 308.5073 | 416 | 398 | 366 | 344.9 | 749.4 | 54 | 19 | 96.1 | 5.9 | 223.2 | 3.4 | 803.5 | 861.4 | 789.3 | 809.2 | 850.5 | 778.6 | 780.2 | 824.5 | 793 | 803 | 170.3 | 264.7 | 345.2 | 310 | 411.8 | 386.3 | 328.6 | 354.7 | 490.5 | 324.6
1271 | 1097 | 661.7 | 264.68 | 309.3957 | 417 | 398.6 | 365.9 | 345.5 | 740.9 | 54 | 19 | 96.1 | 6 | 230.4 | 3.5 | 803.1 | 868 | 783.4 | 809.6 | 851.5 | 778.7 | 765 | 812.9 | 793.2 | 803.8 | 170.5 | 265 | 345.4 | 310.2 | 412.3 | 386.5 | 328.9 | 355 | 490.8 | 324.9
1272 | 1098 | 663 | 265.2 | 310.0035 | 418.2 | 399.2 | 365.5 | 346 | 728.8 | 54 | 19 | 96.2 | 6.9 | 237.1 | 3.5 | 802.4 | 864.1 | 782.6 | 808.5 | 849.7 | 779 | 747.6 | 799.8 | 793.8 | 801.1 | 170.8 | 265.2 | 345.9 | 310.4 | 412.9 | 386.7 | 329.4 | 355.3 | 490.9 | 325.2
1273 | 1099 | 663.1 | 265.24 | 310.0503 | 420.1 | 401 | 364.4 | 346.8 | 727 | 54 | 19 | 96.3 | 5.8 | 242.2 | 3.9 | 802.3 | 856.4 | 786.4 | 807.5 | 848.4 | 778.7 | 748.9 | 805.2 | 794.9 | 799.6 | 171 | 265.4 | 345.8 | 310.7 | 413.2 | 386.9 | 329.8 | 355.5 | 491 | 325.4
1274 | 1100 | 661.6 | 264.64 | 309.3489 | 420.5 | 402.6 | 363.7 | 348 | 723.9 | 54.1 | 19 | 96.5 | 5.4 | 244.5 | 4.3 | 802.6 | 852 | 791.4 | 807.8 | 848.3 | 778.7 | 763.1 | 812.2 | 795.8 | 799.9 | 171.3 | 265.6 | 346 | 310.9 | 413.8 | 387.1 | 330.2 | 355.9 | 491.2 | 325.7
1275 | 1101 | 661 | 264.4 | 309.0684 | 420.6 | 403.7 | 363.5 | 348.4 | 730.6 | 54.1 | 19 | 96.6 | 5.2 | 253.8 | 4.1 | 802.4 | 858.3 | 792.4 | 807.2 | 849.7 | 778.8 | 760.4 | 812.3 | 795.9 | 799.3 | 171.5 | 265.9 | 346.6 | 311.2 | 413.9 | 387 | 330.5 | 356.1 | 491.7 | 325.9
1276 | 1102 | 661.9 | 264.76 | 309.4892 | 420.7 | 404 | 363.7 | 348.3 | 730.3 | 54.2 | 19 | 96.6 | 5.8 | 254 | 4.2 | 801.9 | 860.5 | 790.3 | 807.2 | 850.8 | 778.6 | 759.2 | 812.4 | 795.2 | 800.4 | 171.7 | 266.1 | 346.8 | 311.5 | 413.8 | 387.1 | 330.9 | 356.3 | 492.1 | 326.1
1277 | 1103 | 664 | 265.6 | 310.4711 | 420.9 | 403.4 | 365.1 | 348.5 | 732.5 | 54.2 | 19 | 96.6 | 6.3 | 253.6 | 4.3 | 801.6 | 861.8 | 790.3 | 807.7 | 851.1 | 778.3 | 762.1 | 814.9 | 795.2 | 801.1 | 172 | 266.3 | 347.1 | 311.7 | 413.6 | 387.1 | 331.1 | 356.5 | 492.2 | 326.3
1278 | 1104 | 662.8 | 265.12 | 309.91 | 419.3 | 403.6 | 365.9 | 349 | 740.3 | 54.2 | 19 | 96.7 | 6.2 | 249.2 | 4.6 | 801.5 | 858.9 | 791.5 | 807.4 | 851.2 | 778 | 768.1 | 815.3 | 795.5 | 801.8 | 172.2 | 266.5 | 347.5 | 312 | 413.4 | 387.1 | 331.4 | 356.6 | 492.4 | 326.4
1279 | 1105 | 662.9 | 265.16 | 309.9568 | 419.1 | 404.5 | 366.3 | 349.2 | 736.3 | 54.2 | 19 | 96.8 | 5.5 | 217.9 | 4.8 | 801.8 | 853.7 | 792.5 | 806.5 | 852.8 | 777.7 | 780.2 | 818 | 795.3 | 802.1 | 172.4 | 266.8 | 347.4 | 312.2 | 413.2 | 387 | 331.7 | 356.8 | 492.7 | 326.5
1280 | 1106 | 661.2 | 264.48 | 309.1619 | 419 | 406 | 366.7 | 348.5 | 736.9 | 54.2 | 18.9 | 97 | 5.4 | 204.3 | 5 | 801.9 | 850.6 | 793.1 | 806 | 852.7 | 777.8 | 788.1 | 818.2 | 794.8 | 803.3 | 172.7 | 267 | 347.8 | 312.5 | 413.4 | 387.1 | 332.1 | 357 | 493.1 | 326.7
1281 | 1107 | 662.8 | 265.12 | 309.91 | 416.8 | 407.4 | 367.1 | 348.6 | 749.7 | 54.2 | 18.9 | 97.1 | 5.5 | 246.3 | 4.8 | 802.1 | 850.6 | 793.9 | 807.1 | 851.6 | 778 | 781.1 | 821.5 | 794.4 | 801.4 | 172.9 | 267.2 | 348.6 | 312.7 | 413.8 | 387 | 332.5 | 357.1 | 493.6 | 326.8
1282 | 1108 | 663.3 | 265.32 | 310.1438 | 415.6 | 408.5 | 367.3 | 349.6 | 757.1 | 54.3 | 18.9 | 97.1 | 5.9 | 219.5 | 4.7 | 802.2 | 847 | 794 | 807.5 | 852.7 | 777.7 | 784.1 | 822.9 | 794.2 | 800.1 | 173.2 | 267.4 | 348.7 | 312.9 | 414.4 | 387.1 | 332.9 | 357.3 | 494.1 | 327
1283 | 1109 | 664.3 | 265.72 | 310.6114 | 417.1 | 409.6 | 368.1 | 350.4 | 754.3 | 54.2 | 18.9 | 97 | 6.4 | 236.8 | 3.9 | 802.5 | 840.4 | 795.1 | 807.9 | 852.9 | 777.8 | 792.8 | 826.6 | 794 | 800.7 | 173.4 | 267.7 | 348.7 | 313.1 | 414.9 | 387.6 | 333.3 | 357.6 | 494.4 | 327.2
1284 | 1110 | 664.2 | 265.68 | 310.5646 | 416.7 | 410.2 | 369.2 | 351.1 | 738.4 | 54.2 | 18.9 | 96.9 | 6.1 | 247.7 | 4 | 802.8 | 840.4 | 796.5 | 809.2 | 852.1 | 777.9 | 800.3 | 830.9 | 794.1 | 800.2 | 173.6 | 267.9 | 348.9 | 313.3 | 414.9 | 387.9 | 333.6 | 357.9 | 494.9 | 327.4
1285 | 1111 | 662.7 | 265.08 | 309.8632 | 417.1 | 410.6 | 370.5 | 351.5 | 728.6 | 54.2 | 18.9 | 97 | 5.3 | 217.1 | 3.9 | 802.6 | 841.9 | 796.3 | 807.8 | 852.8 | 778 | 806.5 | 829.5 | 793.3 | 801.5 | 173.8 | 268.1 | 349 | 313.5 | 414.6 | 388.2 | 333.7 | 358.1 | 495.6 | 327.7
1286 | 1112 | 662.3 | 264.92 | 309.6762 | 418.4 | 410.8 | 370.9 | 351.7 | 729.9 | 54.2 | 18.9 | 97 | 5.9 | 211.4 | 3.6 | 802.8 | 841.8 | 796.4 | 807 | 852.5 | 778 | 811.1 | 830.4 | 791.9 | 802.5 | 174.1 | 268.4 | 349.4 | 313.8 | 414.6 | 388.4 | 334 | 358.4 | 496.1 | 327.9
1287 | 1113 | 662.9 | 265.16 | 309.9568 | 418 | 411.3 | 370.8 | 352.1 | 738 | 54.2 | 18.9 | 97.1 | 6.2 | 239.2 | 3.9 | 803 | 837.9 | 796.8 | 806.9 | 851.8 | 778.2 | 812.4 | 828.9 | 791.4 | 802.8 | 174.3 | 268.6 | 349.7 | 314 | 414.8 | 388.4 | 334.4 | 358.6 | 496.4 | 328.1
1288 | 1114 | 662.8 | 265.12 | 309.91 | 417.1 | 411.1 | 371.4 | 352.5 | 733.2 | 54.1 | 18.9 | 97.1 | 5.7 | 249.6 | 4.1 | 803.1 | 836.1 | 797.1 | 807.5 | 852 | 778.4 | 814.8 | 833.1 | 791.8 | 802.8 | 174.6 | 268.8 | 349.9 | 314.2 | 415.1 | 388.7 | 334.8 | 358.8 | 496.8 | 328.4
1289 | 1115 | 663.8 | 265.52 | 310.3776 | 416.3 | 411.2 | 372.1 | 353.6 | 730.5 | 54.1 | 18.9 | 97 | 6.1 | 242.9 | 4.2 | 802.9 | 834.9 | 797.2 | 806.2 | 852.4 | 778.7 | 818.5 | 831.6 | 791.5 | 804.9 | 174.8 | 269 | 350 | 314.5 | 416 | 389.1 | 335.2 | 359.1 | 497.3 | 328.7
1290 | 1116 | 665.3 | 266.12 | 311.0789 | 415.7 | 412.1 | 372.3 | 354.3 | 713.7 | 54.1 | 18.9 | 97 | 7 | 237.3 | 4.3 | 803 | 832.2 | 796.1 | 805.3 | 852.5 | 778.9 | 820.6 | 828.4 | 791 | 805.4 | 175 | 269.3 | 350.2 | 314.7 | 417 | 389.6 | 335.6 | 359.4 | 497.7 | 328.9
1291 | 1117 | 665.5 | 266.2 | 311.1725 | 413.8 | 413.4 | 372.3 | 354.3 | 708.7 | 54 | 18.9 | 96.9 | 6.9 | 226 | 4.6 | 803.1 | 832.9 | 797.2 | 804.9 | 851.9 | 779.2 | 822.3 | 829.2 | 790.7 | 806.4 | 175.3 | 269.5 | 350.6 | 314.9 | 417.3 | 390.1 | 335.9 | 359.6 | 498.1 | 329.2
1292 | 1118 | 664.5 | 265.8 | 310.7049 | 414.7 | 413.9 | 373.6 | 354.8 | 723.2 | 54 | 18.9 | 96.8 | 6.5 | 218 | 4.4 | 803.2 | 831.9 | 800.3 | 805.1 | 851.8 | 779.2 | 819.2 | 828.3 | 790.5 | 806.9 | 175.5 | 269.7 | 351.2 | 315.2 | 417.5 | 390.4 | 336.2 | 359.9 | 498.7 | 329.4
1293 | 1119 | 664.5 | 265.8 | 310.7049 | 414.9 | 414.2 | 374.8 | 355.1 | 731.2 | 54 | 18.9 | 96.7 | 6.1 | 226.4 | 4.3 | 803.2 | 833.2 | 800.7 | 806 | 851.9 | 779.1 | 806 | 827.8 | 790.6 | 806 | 175.7 | 269.9 | 351.5 | 315.5 | 417.4 | 390.3 | 336.5 | 360.1 | 499.1 | 329.7
1294 | 1120 | 662.4 | 264.96 | 309.723 | 415.4 | 415.2 | 375.7 | 354.8 | 742 | 54 | 18.9 | 96.5 | 6.4 | 258.7 | 4.7 | 803.3 | 838.1 | 798.4 | 806.4 | 851.4 | 779.1 | 789.2 | 829.6 | 789.8 | 803.5 | 176 | 270.2 | 352.1 | 315.7 | 417.6 | 390.4 | 336.9 | 360.3 | 499.6 | 330
1295 | 1121 | 661.7 | 264.68 | 309.3957 | 417.1 | 416.4 | 375.9 | 355.3 | 748.9 | 53.9 | 18.9 | 96.5 | 6.1 | 242.1 | 5.6 | 803.5 | 844.8 | 795 | 806.3 | 851 | 779.2 | 775.5 | 830.6 | 790.4 | 803.4 | 176.2 | 270.4 | 352.3 | 316 | 417.9 | 390.5 | 337.3 | 360.4 | 499.8 | 330.2
1296 | 1122 | 663.4 | 265.36 | 310.1906 | 418 | 417 | 376.9 | 356 | 743 | 53.9 | 18.9 | 96.5 | 6 | 227.5 | 7.5 | 803.7 | 843.1 | 793.2 | 807.1 | 849.6 | 778.7 | 782.6 | 830 | 790.7 | 804.7 | 176.5 | 270.6 | 352.3 | 316.2 | 418.4 | 390.7 | 337.7 | 360.7 | 500 | 330.5
1297 | 1123 | 663.8 | 265.52 | 310.3776 | 418.9 | 418 | 378.1 | 356.1 | 741.1 | 54 | 18.9 | 96.6 | 5.9 | 251.6 | 6.8 | 803.7 | 840.6 | 794 | 806.8 | 850.3 | 778.7 | 792.1 | 831.3 | 791.1 | 806.1 | 176.7 | 270.9 | 352.7 | 316.5 | 418.8 | 391 | 338.2 | 360.9 | 500 | 330.8
1298 | 1124 | 665.2 | 266.08 | 311.0322 | 419.6 | 418.4 | 378.1 | 355.7 | 746.6 | 54 | 18.9 | 96.6 | 5.8 | 234.3 | 5.9 | 804.1 | 840.2 | 795.6 | 806.5 | 850.1 | 778.7 | 792.4 | 832.5 | 791.6 | 806.4 | 177 | 271.1 | 353 | 316.7 | 419.1 | 391.1 | 338.5 | 361.1 | 500.2 | 331
1299 | 1125 | 664.5 | 265.8 | 310.7049 | 419.5 | 418.6 | 377.6 | 355.9 | 750.7 | 54.1 | 18.9 | 96.7 | 5.7 | 230.6 | 6.5 | 804.4 | 840.1 | 796 | 806 | 850.5 | 778.7 | 794.4 | 829.1 | 792 | 807 | 177.2 | 271.3 | 353.2 | 317 | 419.1 | 391.2 | 338.9 | 361.4 | 500.6 | 331.3
1300 | 1126 | 664.1 | 265.64 | 310.5179 | 418.5 | 418.7 | 377.5 | 356.4 | 749.7 | 54.1 | 18.9 | 96.7 | 5.2 | 231.1 | 7.1 | 804.4 | 839.1 | 795.7 | 806 | 850.9 | 778.5 | 798.6 | 829.9 | 791.6 | 808.3 | 177.5 | 271.6 | 353.3 | 317.2 | 419.2 | 391.1 | 339.3 | 361.6 | 501 | 331.6
1301 | 1127 | 663.6 | 265.44 | 310.2841 | 418.6 | 418.5 | 377.6 | 356.8 | 751.9 | 54.2 | 18.9 | 96.8 | 5.7 | 231.3 | 7.5 | 804.3 | 839.3 | 794.4 | 805.7 | 851 | 778.5 | 801 | 833.7 | 791.6 | 809.4 | 177.8 | 271.8 | 353.7 | 317.5 | 419.4 | 391 | 339.5 | 361.8 | 501.3 | 331.8
1302 | 1128 | 665.1 | 266.04 | 310.9854 | 417.9 | 418.1 | 377.4 | 357 | 757.1 | 54.2 | 18.9 | 96.9 | 6 | 226.8 | 7.6 | 804.4 | 835 | 795.1 | 805.6 | 851.2 | 778.5 | 803.5 | 833.2 | 791.2 | 809.5 | 178.1 | 272 | 354.1 | 317.7 | 419.8 | 391 | 339.9 | 362 | 501.5 | 332.1
1303 | 1129 | 665.2 | 266.08 | 311.0322 | 417.6 | 417.2 | 377.7 | 357.5 | 747.6 | 54.1 | 18.9 | 97 | 5.4 | 216.7 | 7.5 | 804.6 | 835.7 | 795.2 | 806.5 | 850 | 778.5 | 804.9 | 831.6 | 791 | 809.9 | 178.3 | 272.3 | 354.2 | 318 | 420 | 391.1 | 340.3 | 362.2 | 501.8 | 332.4
1304 | 1130 | 664.7 | 265.88 | 310.7984 | 418.3 | 417.3 | 378.1 | 358 | 750.9 | 54.1 | 18.9 | 97 | 6.1 | 224.3 | 7.3 | 805.1 | 839.5 | 796.4 | 808 | 850.3 | 778.5 | 797.1 | 832.3 | 791.4 | 808.8 | 178.6 | 272.5 | 354.6 | 318.3 | 420.5 | 391.2 | 340.7 | 362.3 | 502.1 | 332.6
1305 | 1131 | 665.9 | 266.36 | 311.3595 | 418.2 | 417.8 | 377.7 | 358.2 | 751.5 | 54.1 | 18.9 | 97.1 | 5.1 | 220 | 6.7 | 805.4 | 839.5 | 796.3 | 808.8 | 850.2 | 778.3 | 801.4 | 833.5 | 791.1 | 809.8 | 178.9 | 272.7 | 354.8 | 318.5 | 420.5 | 391.3 | 341.1 | 362.6 | 502.4 | 332.9
1306 | 1132 | 665.5 | 266.2 | 311.1725 | 418 | 417.2 | 378.2 | 358.4 | 748.2 | 54.1 | 18.9 | 97.1 | 5.3 | 223.3 | 6 | 805.5 | 840.3 | 794.4 | 809.2 | 849 | 778.1 | 811.6 | 829.6 | 791.2 | 811.1 | 179.1 | 272.9 | 355 | 318.8 | 420.7 | 391.7 | 341.5 | 362.8 | 502.6 | 333.2
1307 | 1133 | 663.6 | 265.44 | 310.2841 | 418.6 | 416.6 | 377.7 | 358.3 | 731.7 | 54.1 | 18.9 | 97.1 | 6 | 215.9 | 5.5 | 805.5 | 840.4 | 794.5 | 809.3 | 850.1 | 778.1 | 815.6 | 829 | 791.1 | 812.3 | 179.4 | 273.2 | 355.1 | 319 | 421.2 | 392.1 | 341.9 | 363.2 | 502.9 | 333.4
1308 | 1134 | 663.5 | 265.4 | 310.2373 | 419.1 | 416.5 | 377.5 | 358.3 | 720.9 | 54.1 | 18.9 | 97 | 6.1 | 207.7 | 4.6 | 805.6 | 842 | 795 | 809.2 | 850.8 | 778 | 808.3 | 829.9 | 791.4 | 812 | 179.7 | 273.4 | 355.4 | 319.3 | 421.2 | 392.2 | 342.2 | 363.4 | 503.1 | 333.7
1309 | 1135 | 662.7 | 265.08 | 309.8632 | 420.5 | 417.1 | 378 | 358.5 | 725.5 | 54.2 | 18.9 | 96.8 | 5.9 | 214.6 | 4.5 | 805.5 | 843.2 | 792.9 | 808.4 | 850.2 | 778 | 804.8 | 831.7 | 791 | 813.1 | 180 | 273.7 | 355.7 | 319.6 | 421.1 | 392.2 | 342.5 | 363.6 | 503.5 | 334
1310 | 1136 | 663.3 | 265.32 | 310.1438 | 422 | 418.1 | 377.7 | 357.9 | 714.8 | 54.2 | 18.9 | 96.8 | 6.3 | 229.5 | 4.3 | 805.4 | 842.7 | 792.1 | 808.6 | 850.6 | 778.2 | 809.8 | 833.7 | 790.7 | 814.4 | 180.2 | 273.9 | 355.9 | 319.8 | 421.1 | 392.6 | 342.8 | 363.8 | 503.7 | 334.2
1311 | 1137 | 663.4 | 265.36 | 310.1906 | 422 | 419.6 | 376.1 | 356.6 | 714.5 | 54.2 | 18.8 | 96.8 | 5.7 | 240.6 | 3.8 | 805.4 | 841.5 | 792.1 | 808.4 | 850.6 | 778.2 | 813.1 | 832.2 | 790.3 | 815 | 180.5 | 274.1 | 356 | 320.1 | 421.1 | 392.8 | 343.1 | 364.1 | 503.9 | 334.5
1312 | 1138 | 663.8 | 265.52 | 310.3776 | 421.8 | 419.6 | 375.4 | 356.3 | 719.3 | 54.2 | 18.8 | 96.9 | 5.7 | 243.7 | 3.6 | 805.5 | 841.4 | 793.2 | 808.3 | 851.4 | 778.2 | 815.2 | 835.3 | 790.9 | 815.7 | 180.7 | 274.4 | 356.3 | 320.3 | 421.3 | 393.3 | 343.5 | 364.4 | 504.2 | 334.8
1313 | 1139 | 664 | 265.6 | 310.4711 | 421.3 | 419.6 | 375.1 | 356.1 | 730.2 | 54.2 | 18.9 | 96.9 | 6.3 | 237.3 | 3.2 | 805.9 | 843 | 794.7 | 809 | 851.1 | 778 | 803.4 | 836.7 | 791.1 | 814.4 | 181 | 274.6 | 356.8 | 320.6 | 422 | 393.4 | 343.9 | 364.5 | 504.6 | 335
1314 | 1140 | 665.3 | 266.12 | 311.0789 | 421.4 | 420.2 | 375.6 | 356 | 735.6 | 54.2 | 18.9 | 96.9 | 5.5 | 214.2 | 2.9 | 806.2 | 840.6 | 795.9 | 809.4 | 850.9 | 777.7 | 796.9 | 838.2 | 791.4 | 812.7 | 181.2 | 274.8 | 357 | 320.9 | 422.2 | 393.5 | 344.2 | 364.7 | 504.8 | 335.3
1315 | 1141 | 664.5 | 265.8 | 310.7049 | 421 | 420.6 | 375.4 | 356.7 | 742.3 | 54.2 | 18.8 | 96.9 | 5.8 | 205.9 | 2.7 | 806.4 | 839 | 796.4 | 810.2 | 852.5 | 777.5 | 796 | 835.2 | 792.2 | 811.9 | 181.4 | 275.1 | 357.4 | 321.1 | 422 | 393.7 | 344.6 | 364.9 | 505.2 | 335.6
1316 | 1142 | 666 | 266.4 | 311.4063 | 420.6 | 420.4 | 375.7 | 357.2 | 748 | 54.2 | 18.8 | 97 | 5.2 | 220.6 | 3 | 806.4 | 844.4 | 795.2 | 809.5 | 852.9 | 777.5 | 783.9 | 829.5 | 792 | 811.8 | 181.7 | 275.3 | 357.9 | 321.4 | 421.9 | 393.7 | 345 | 365.1 | 505.6 | 335.8
1317 | 1143 | 666.3 | 266.52 | 311.5465 | 421.9 | 420.3 | 376.2 | 358 | 747.7 | 54.1 | 18.8 | 97 | 5.7 | 231.4 | 3.3 | 806.4 | 847.2 | 793.3 | 810.4 | 852.7 | 777.5 | 776 | 827.7 | 792.1 | 810.7 | 181.9 | 275.6 | 358.2 | 321.7 | 421.9 | 393.6 | 345.4 | 365.2 | 505.9 | 336.1
1318 | 1144 | 666.9 | 266.76 | 311.8271 | 423 | 419.9 | 377.2 | 359 | 731 | 54.1 | 18.8 | 97.1 | 6.5 | 233.9 | 3.5 | 806.5 | 843.1 | 792.5 | 810.3 | 852.1 | 776.8 | 783.8 | 827.7 | 792.2 | 812 | 182.2 | 275.8 | 358.1 | 321.9 | 421.7 | 393.5 | 345.8 | 365.4 | 506.1 | 336.3
1319 | 1145 | 666.4 | 266.56 | 311.5933 | 424.3 | 419.3 | 377.4 | 358.6 | 740.5 | 54.1 | 18.8 | 97.1 | 6.4 | 245.1 | 4 | 806.5 | 844.5 | 793.5 | 809.9 | 851.6 | 776.8 | 785.8 | 830.4 | 792.4 | 813 | 182.4 | 276 | 358.6 | 322.2 | 421.8 | 393.5 | 346.1 | 365.6 | 506.3 | 336.6
1320 | 1146 | 665.5 | 266.2 | 311.1725 | 424.6 | 419.9 | 377.3 | 359.1 | 744.4 | 54.2 | 18.8 | 97.2 | 6.1 | 245 | 4.5 | 806.8 | 842.5 | 794 | 810.2 | 848.1 | 776.6 | 778.9 | 830.3 | 792.3 | 812.6 | 182.7 | 276.3 | 359 | 322.4 | 422 | 393.5 | 346.4 | 365.8 | 506.6 | 336.9
1321 | 1147 | 664.7 | 265.88 | 310.7984 | 423.5 | 422.1 | 379 | 359.8 | 743.9 | 54.2 | 18.8 | 97.3 | 6 | 242.8 | 4.9 | 806.9 | 839.4 | 794.7 | 810.3 | 848.7 | 776.5 | 777.3 | 831.5 | 792.6 | 811 | 183 | 276.5 | 359.3 | 322.7 | 422.5 | 393.3 | 346.8 | 366 | 507 | 337.1
1322 | 1148 | 665.9 | 266.36 | 311.3595 | 422.4 | 422.8 | 379.2 | 360.5 | 744.3 | 54.3 | 18.8 | 97.3 | 6.5 | 247.2 | 4.8 | 807 | 835.3 | 795 | 809.6 | 848.4 | 776.5 | 786 | 829.4 | 792.4 | 812 | 183.3 | 276.8 | 359.4 | 322.9 | 423 | 393.5 | 347.2 | 366.2 | 507.4 | 337.4
1323 | 1149 | 666.3 | 266.52 | 311.5465 | 420.3 | 423.4 | 378.2 | 361.1 | 740.4 | 54.3 | 18.8 | 97.3 | 6.6 | 242.8 | 4.8 | 807 | 836.1 | 795.9 | 809.5 | 847.8 | 776.6 | 785.6 | 829.8 | 792.8 | 811.8 | 183.6 | 277 | 359.9 | 323.2 | 423.2 | 393.8 | 347.6 | 366.4 | 507.8 | 337.7
1324 | 1150 | 667.1 | 266.84 | 311.9206 | 418.7 | 423.3 | 377.3 | 361 | 750.3 | 54.3 | 18.8 | 97.4 | 6.8 | 236.2 | 4.7 | 807 | 839.9 | 795 | 809.1 | 848.9 | 777.2 | 771.5 | 825.2 | 792.9 | 809.4 | 183.9 | 277.3 | 360.7 | 323.5 | 423.6 | 393.9 | 348 | 366.5 | 508.3 | 338
1325 | 1151 | 668.4 | 267.36 | 312.5284 | 417.4 | 422.9 | 378.8 | 361.6 | 749.4 | 54.4 | 18.8 | 97.3 | 6.1 | 238.2 | 4.1 | 806.7 | 841.6 | 792.2 | 810.1 | 849.2 | 777 | 768.3 | 822.4 | 792.3 | 810.4 | 184.2 | 277.5 | 360.6 | 323.8 | 423.5 | 394 | 348.3 | 366.7 | 508.6 | 338.3
1326 | 1152 | 667.2 | 266.88 | 311.9673 | 417.3 | 421.8 | 379.4 | 362.6 | 717.1 | 54.4 | 18.8 | 97.3 | 5.7 | 253.6 | 3.9 | 806.3 | 836.5 | 791.5 | 810.3 | 847 | 776.1 | 784.4 | 824.6 | 792.3 | 812.3 | 184.6 | 277.8 | 360.3 | 324.1 | 423.4 | 394.1 | 348.6 | 367 | 508.6 | 338.5
1327 | 1153 | 665.3 | 266.12 | 311.0789 | 417 | 420.5 | 379.2 | 362.6 | 692.5 | 54.5 | 18.8 | 97.3 | 6.3 | 265 | 3.9 | 806.2 | 830.5 | 791.4 | 809 | 847.4 | 775.8 | 795.9 | 823.5 | 792.7 | 812.8 | 184.9 | 278 | 360.6 | 324.3 | 423.4 | 394.5 | 348.9 | 367.2 | 508.7 | 338.8
1328 | 1154 | 664.8 | 265.92 | 310.8452 | 417.8 | 420.6 | 379.4 | 362.4 | 698.1 | 54.5 | 18.8 | 97.4 | 5.9 | 254.8 | 3.7 | 806 | 831.9 | 793.2 | 808.2 | 848.9 | 775.9 | 798 | 824.7 | 793.2 | 813.6 | 185.3 | 278.2 | 361.2 | 324.6 | 423.8 | 394.8 | 349.1 | 367.4 | 509.1 | 339
1329 | 1155 | 665 | 266 | 310.9387 | 418.9 | 421.8 | 380.4 | 362.2 | 703.8 | 54.6 | 18.8 | 97.5 | 6.4 | 232.4 | 3.6 | 805.6 | 837.2 | 793.8 | 807.9 | 850.8 | 776.2 | 797.1 | 827.2 | 792.4 | 814 | 185.7 | 278.5 | 361.3 | 324.9 | 424.5 | 395.2 | 349.5 | 367.6 | 509.7 | 339.3
1330 | 1156 | 666.1 | 266.44 | 311.453 | 419.5 | 422.4 | 381 | 362 | 702.8 | 54.6 | 18.8 | 97.4 | 6.2 | 236.1 | 3.8 | 805.4 | 841.5 | 793.7 | 808.5 | 853.7 | 776.1 | 791.1 | 827.2 | 792.3 | 814.9 | 186 | 278.7 | 361.4 | 325.2 | 424.5 | 395.5 | 349.8 | 367.8 | 509.9 | 339.6
1331 | 1157 | 666 | 266.4 | 311.4063 | 420 | 422.9 | 381 | 362 | 701.5 | 54.7 | 18.8 | 97.4 | 6 | 249.7 | 4.1 | 805.4 | 842.9 | 793.4 | 809.2 | 854.3 | 775.7 | 781.5 | 825.6 | 792.5 | 814.5 | 186.4 | 279 | 361.5 | 325.5 | 424.1 | 395.6 | 350 | 368 | 510.1 | 339.9
1332 | 1158 | 664.7 | 265.88 | 310.7984 | 422.1 | 423.1 | 381.5 | 362 | 716.5 | 54.8 | 18.8 | 97.4 | 5.7 | 247.6 | 4 | 805.5 | 840.9 | 794 | 808.9 | 854.3 | 775.4 | 784.2 | 825.6 | 792.4 | 814.7 | 186.8 | 279.2 | 362 | 325.7 | 424.2 | 395.9 | 350.3 | 368.1 | 510.2 | 340.1
1333 | 1159 | 663.3 | 265.32 | 310.1438 | 422.9 | 423.3 | 381.4 | 361.8 | 726.7 | 54.9 | 18.8 | 97.6 | 5.6 | 248.3 | 4.1 | 805.7 | 838.5 | 794.8 | 810.9 | 853.9 | 775.4 | 782.6 | 827.9 | 792.7 | 813 | 187.1 | 279.4 | 362.4 | 326 | 424 | 396.2 | 350.6 | 368.4 | 510.4 | 340.4
1334 | 1160 | 664.5 | 265.8 | 310.7049 | 423.3 | 424.7 | 381.3 | 361.9 | 727.8 | 55 | 18.8 | 97.9 | 5.8 | 251.1 | 4.9 | 806.1 | 838.9 | 794.9 | 812.7 | 854.1 | 775.6 | 768.1 | 821.3 | 792.9 | 809.5 | 187.4 | 279.7 | 363.1 | 326.2 | 423.8 | 396.4 | 350.8 | 368.5 | 510.8 | 340.7
1335 | 1161 | 666.8 | 266.72 | 311.7803 | 425.4 | 426.3 | 381.6 | 362.1 | 732.1 | 55.1 | 18.8 | 98 | 5.9 | 251.7 | 6 | 806.2 | 843.1 | 793.3 | 812.1 | 854.8 | 774.8 | 764.5 | 819.3 | 792.2 | 810.5 | 187.7 | 279.9 | 363 | 326.5 | 423.4 | 396.3 | 351 | 368.6 | 511.2 | 341
1336 | 1162 | 666.3 | 266.52 | 311.5465 | 425.6 | 426.2 | 382.2 | 361.7 | 733.5 | 55.1 | 18.8 | 98.1 | 6 | 243.6 | 6.3 | 806.3 | 841 | 793.7 | 812 | 855.2 | 774.3 | 762.2 | 820.6 | 792.5 | 810.3 | 187.9 | 280.1 | 363.5 | 326.7 | 423.2 | 396.4 | 351.2 | 368.8 | 511.3 | 341.2
1337 | 1163 | 668.1 | 267.24 | 312.3882 | 424.5 | 425.5 | 381.8 | 361.6 | 734.8 | 55.1 | 18.8 | 98.2 | 5.9 | 233.1 | 5.9 | 806.5 | 838.7 | 793.4 | 811.8 | 856.4 | 773.8 | 768.4 | 821.5 | 792.6 | 809.8 | 188.2 | 280.3 | 363.7 | 326.9 | 422.9 | 396.1 | 351.4 | 368.9 | 511.4 | 341.5
1338 | 1164 | 666.6 | 266.64 | 311.6868 | 423.9 | 424.8 | 382.9 | 361.7 | 738.9 | 55.3 | 18.8 | 98.4 | 5.7 | 247.6 | 5.4 | 806.8 | 832.5 | 794.5 | 811.8 | 857.5 | 773.7 | 777.4 | 822.7 | 792.9 | 809.9 | 188.5 | 280.5 | 363.8 | 327.1 | 422.9 | 396.1 | 351.6 | 369.1 | 511.7 | 341.8
1339 | 1165 | 665.7 | 266.28 | 311.266 | 423.6 | 423.9 | 382.9 | 361.6 | 744.1 | 55.4 | 18.8 | 98.5 | 5.8 | 226.7 | 5 | 807 | 838.1 | 791.8 | 812 | 857.4 | 773.7 | 771.1 | 822.3 | 793.2 | 809.4 | 188.7 | 280.8 | 364.1 | 327.4 | 423 | 395.9 | 351.9 | 369.3 | 512.1 | 342.1
1340 | 1166 | 666.1 | 266.44 | 311.453 | 423.4 | 424 | 382.8 | 361.9 | 723.2 | 55.4 | 18.8 | 98.6 | 5.8 | 210.5 | 4.6 | 806.8 | 840.6 | 789.7 | 813.6 | 857 | 773.7 | 773.8 | 825.9 | 792.9 | 811.5 | 189 | 281 | 364 | 327.6 | 422.7 | 396.1 | 352.2 | 369.5 | 512.5 | 342.4
1341 | 1167 | 668.2 | 267.28 | 312.4349 | 424.3 | 423.8 | 382.7 | 363 | 705.5 | 55.5 | 18.8 | 98.7 | 5.3 | 210.9 | 4.3 | 806.9 | 844.7 | 791.2 | 814.5 | 857.6 | 773.6 | 779.6 | 828.2 | 793.1 | 812.8 | 189.2 | 281.2 | 364.2 | 327.8 | 422.6 | 396.2 | 352.4 | 369.7 | 512.5 | 342.6
1342 | 1168 | 667.7 | 267.08 | 312.2011 | 424.7 | 423.1 | 382.2 | 363.1 | 717.1 | 55.5 | 18.8 | 98.8 | 5.9 | 220.7 | 4.1 | 807.2 | 846.8 | 791.8 | 814.3 | 856.3 | 773.2 | 782.7 | 828.3 | 792.3 | 813.9 | 189.4 | 281.5 | 364.6 | 328 | 422.4 | 396.2 | 352.6 | 369.8 | 512.5 | 342.9
1343 | 1169 | 667.9 | 267.16 | 312.2946 | 426 | 422.7 | 381.9 | 363 | 733.3 | 55.6 | 18.8 | 98.9 | 6 | 232.9 | 3.8 | 807.6 | 844.3 | 793.9 | 814.3 | 855.3 | 773.1 | 778.8 | 830.1 | 792.2 | 812.7 | 189.6 | 281.7 | 365.1 | 328.3 | 422.7 | 396.3 | 352.9 | 370 | 512.7 | 343.2
1344 | 1170 | 667.4 | 266.96 | 312.0609 | 426.1 | 423.7 | 381.9 | 362.3 | 744.6 | 55.6 | 18.8 | 98.9 | 6 | 245.7 | 3.8 | 807.9 | 845.2 | 794.7 | 814.1 | 854.7 | 773 | 775.9 | 829.6 | 792.6 | 812.5 | 189.8 | 281.9 | 365.4 | 328.5 | 422.7 | 396.5 | 353.2 | 370.2 | 513 | 343.5
1345 | 1171 | 667.7 | 267.08 | 312.2011 | 424.4 | 424.1 | 382.6 | 361.8 | 742.8 | 55.7 | 18.8 | 98.9 | 5.5 | 254.9 | 3.6 | 808.1 | 844.8 | 795.5 | 814.2 | 854.3 | 773.2 | 771 | 828.7 | 792.6 | 812.6 | 190 | 282.2 | 365.5 | 328.7 | 422.7 | 396.7 | 353.5 | 370.3 | 513.2 | 343.7
1346 | 1172 | 666.5 | 266.6 | 311.64 | 422.6 | 423.9 | 382.9 | 361.7 | 737.1 | 55.8 | 18.8 | 99 | 5.7 | 236 | 3.6 | 808.5 | 841 | 795.6 | 814.3 | 854.7 | 773.1 | 772.4 | 828.1 | 792.9 | 811.1 | 190.2 | 282.4 | 365.7 | 329 | 422.7 | 396.9 | 353.8 | 370.5 | 513.4 | 344
1347 | 1173 | 667.3 | 266.92 | 312.0141 | 422.1 | 423.9 | 382.8 | 362.1 | 732.3 | 55.8 | 18.8 | 99 | 5.6 | 229.3 | 3.7 | 808.7 | 841.3 | 796.5 | 814.3 | 856.4 | 773.2 | 770.8 | 828.5 | 792.5 | 812.9 | 190.4 | 282.6 | 366 | 329.2 | 422.9 | 397 | 354 | 370.7 | 513.8 | 344.3
1348 | 1174 | 666.4 | 266.56 | 311.5933 | 422.3 | 424.7 | 382.9 | 362.8 | 740.2 | 55.9 | 18.8 | 99.1 | 5.9 | 237.3 | 4.1 | 809 | 842.7 | 797.2 | 814.3 | 856.9 | 773.1 | 770.8 | 827 | 791.8 | 813.4 | 190.7 | 282.9 | 366.2 | 329.5 | 422.8 | 397.2 | 354.2 | 370.9 | 514.1 | 344.6
1349 | 1175 | 665.7 | 266.28 | 311.266 | 422.4 | 425.2 | 382.8 | 363.3 | 724.4 | 55.9 | 18.8 | 99.1 | 5.6 | 240.4 | 4 | 809.3 | 840.4 | 798.3 | 814.7 | 857.8 | 773.2 | 778.8 | 830.9 | 792.3 | 815 | 190.9 | 283.1 | 366.2 | 329.8 | 422.7 | 397.3 | 354.5 | 371.1 | 514.2 | 344.9
1350 | 1176 | 666.9 | 266.76 | 311.8271 | 423.8 | 425 | 382.5 | 363.9 | 714.2 | 56 | 18.8 | 99.1 | 6.5 | 245.4 | 3.6 | 809.5 | 842.8 | 797.3 | 814.8 | 859 | 773.3 | 783.1 | 831.2 | 792.3 | 815.9 | 191.1 | 283.4 | 366.5 | 330 | 422.9 | 397.4 | 354.8 | 371.3 | 514.5 | 345.2
1351 | 1177 | 667.3 | 266.92 | 312.0141 | 424.7 | 424.6 | 382.7 | 363.8 | 697.7 | 56.1 | 18.8 | 99.1 | 6.1 | 246.2 | 3.4 | 809.7 | 843.3 | 797.7 | 815 | 859.7 | 773.2 | 787.3 | 835.1 | 792 | 816.5 | 191.4 | 283.6 | 366.5 | 330.3 | 423.1 | 397.6 | 355.1 | 371.5 | 514.7 | 345.4
1352 | 1178 | 666.9 | 266.76 | 311.8271 | 424.6 | 424.7 | 383.3 | 363.6 | 674.3 | 56.1 | 18.8 | 99.1 | 5.8 | 251.2 | 3.6 | 809.7 | 843.8 | 798.3 | 815.3 | 861.3 | 773.1 | 792.2 | 834.7 | 791.6 | 816.4 | 191.6 | 283.8 | 366.7 | 330.5 | 423.3 | 398 | 355.3 | 371.8 | 515 | 345.7
1353 | 1179 | 668.2 | 267.28 | 312.4349 | 424.3 | 425.3 | 383.2 | 363.8 | 656.3 | 56.1 | 18.8 | 99.2 | 6.1 | 255.4 | 4 | 809.7 | 845.9 | 797.7 | 815.7 | 863.2 | 772.6 | 795.7 | 835.4 | 791.2 | 816.8 | 191.9 | 284.1 | 366.7 | 330.8 | 423.3 | 398.4 | 355.5 | 372 | 515.2 | 346
1354 | 1180 | 669.6 | 267.84 | 313.0895 | 424.6 | 425.8 | 383.9 | 363.3 | 642.1 | 56 | 18.8 | 99.3 | 5.8 | 251.5 | 4 | 809.8 | 843.3 | 799.3 | 816 | 864.2 | 772.2 | 796 | 837.1 | 790.5 | 815.8 | 192.1 | 284.3 | 366.8 | 331 | 423.5 | 398.7 | 355.7 | 372.2 | 515.4 | 346.2
1355 | 1181 | 668.3 | 267.32 | 312.4817 | 424.7 | 427.2 | 382.9 | 363 | 636.8 | 55.9 | 18.7 | 99.4 | 6.3 | 248.8 | 3.8 | 810.2 | 840.5 | 799.8 | 816 | 864.5 | 772 | 799.6 | 839.2 | 790 | 814.8 | 192.4 | 284.5 | 367 | 331.2 | 424 | 399.3 | 356 | 372.6 | 515.7 | 346.5
1356 | 1182 | 667.1 | 266.84 | 311.9206 | 425.3 | 428.9 | 382.4 | 363.3 | 632.3 | 55.9 | 18.7 | 99.5 | 5.7 | 247.8 | 3.7 | 810.4 | 839 | 798.4 | 815.2 | 862.9 | 771.8 | 800.1 | 837.7 | 789.6 | 814.5 | 192.6 | 284.8 | 367.1 | 331.5 | 424.4 | 399.9 | 356.4 | 372.8 | 516.1 | 346.8
1357 | 1183 | 669.1 | 267.64 | 312.8557 | 424.8 | 430.2 | 381.9 | 363.9 | 654.4 | 56 | 18.7 | 99.6 | 6 | 247.8 | 3.7 | 810.6 | 839.6 | 799.2 | 815.2 | 861.8 | 771.9 | 793.7 | 838.9 | 789.2 | 813.4 | 192.9 | 285 | 367.7 | 331.8 | 424.9 | 400.4 | 356.6 | 373.1 | 516.6 | 347.1
1358 | 1184 | 668.5 | 267.4 | 312.5752 | 424 | 431 | 381.4 | 363.9 | 669.8 | 56.1 | 18.7 | 99.7 | 6.2 | 247.4 | 3.5 | 810.7 | 839.3 | 798.4 | 815.1 | 862.4 | 771.8 | 796.2 | 838.4 | 788.6 | 812.5 | 193.2 | 285.3 | 367.7 | 332 | 425.1 | 400.7 | 356.9 | 373.3 | 516.9 | 347.4
1359 | 1185 | 668.9 | 267.56 | 312.7622 | 422.2 | 432 | 381 | 364.4 | 668.3 | 56.2 | 18.7 | 99.8 | 6.5 | 243.5 | 3.3 | 810.9 | 834.6 | 799.5 | 815.3 | 862.6 | 771.9 | 797.4 | 835.9 | 787.7 | 813.6 | 193.5 | 285.5 | 367.8 | 332.3 | 425.6 | 401.2 | 357.2 | 373.5 | 517.1 | 347.7
1360 | 1186 | 667.3 | 266.92 | 312.0141 | 420.7 | 432.3 | 379.9 | 364.1 | 658 | 56.3 | 18.7 | 100 | 6 | 229.1 | 3.1 | 811.3 | 834.7 | 801.3 | 816.8 | 859.9 | 771.9 | 795 | 836.7 | 787.7 | 811.9 | 193.8 | 285.7 | 367.9 | 332.5 | 425.8 | 401.6 | 357.4 | 373.8 | 517.3 | 348
1361 | 1187 | 665.7 | 266.28 | 311.266 | 418.5 | 432.6 | 379.1 | 363.9 | 668.6 | 56.3 | 18.7 | 100.1 | 5.5 | 220.2 | 2.9 | 811.5 | 836.5 | 801.8 | 816.3 | 861.2 | 771.9 | 801.3 | 835 | 787.6 | 811.8 | 194 | 286 | 368.4 | 332.8 | 425.8 | 401.9 | 357.6 | 373.9 | 517.6 | 348.3
1362 | 1188 | 665.3 | 266.12 | 311.0789 | 416.3 | 432.2 | 379.3 | 363.4 | 673 | 56.3 | 18.7 | 100.2 | 5.9 | 223.5 | 3 | 811.5 | 834.2 | 802.1 | 816.4 | 861.4 | 771.8 | 805 | 837.8 | 787.2 | 811.7 | 194.3 | 286.2 | 368.7 | 333.1 | 425.9 | 401.9 | 357.9 | 374.1 | 517.9 | 348.5
1363 | 1189 | 667.4 | 266.96 | 312.0609 | 414.2 | 431.8 | 379.6 | 363.7 | 669.8 | 56.3 | 18.7 | 100.1 | 6.2 | 220.5 | 3.2 | 811.6 | 833.8 | 801.4 | 816.2 | 861.7 | 772 | 801 | 837.8 | 787.2 | 811 | 194.6 | 286.5 | 368.8 | 333.3 | 426.1 | 401.5 | 358.2 | 374.2 | 518.2 | 348.8
1364 | 1190 | 667.3 | 266.92 | 312.0141 | 412.2 | 432.4 | 380.8 | 363.8 | 683.6 | 56.4 | 18.7 | 100 | 6.2 | 216.3 | 5 | 811.5 | 838.6 | 800.8 | 816.1 | 860.8 | 772 | 792.7 | 835.8 | 786.5 | 811.4 | 194.8 | 286.7 | 369.3 | 333.6 | 426 | 401.3 | 358.5 | 374.3 | 518.5 | 349.1
1365 | 1191 | 667.9 | 267.16 | 312.2946 | 411.3 | 433.4 | 382.3 | 363.8 | 705.1 | 56.4 | 18.7 | 100 | 6.4 | 208.2 | 6.6 | 811.6 | 840.5 | 800.4 | 817.5 | 860.4 | 771.9 | 789.1 | 837.7 | 785.9 | 811.6 | 195.1 | 286.9 | 369.6 | 333.8 | 426.1 | 401.2 | 358.7 | 374.4 | 518.8 | 349.4
1366 | 1192 | 668 | 267.2 | 312.3414 | 410.2 | 434 | 382.3 | 364.2 | 724.7 | 56.4 | 18.7 | 100.1 | 6 | 208.2 | 7.7 | 811.9 | 839.3 | 801.2 | 817.9 | 860 | 772.1 | 785.2 | 835.6 | 786.6 | 809.8 | 195.4 | 287.2 | 370.1 | 334.1 | 426.2 | 401 | 359 | 374.5 | 519 | 349.6
1367 | 1193 | 667.5 | 267 | 312.1076 | 409.7 | 433.7 | 382.3 | 364.3 | 735.8 | 56.5 | 18.7 | 100.2 | 5.5 | 205.7 | 8.4 | 811.7 | 842 | 799 | 818.1 | 860 | 772 | 768.5 | 827.3 | 787.2 | 808.2 | 195.6 | 287.4 | 370.7 | 334.4 | 426.4 | 400.8 | 359.3 | 374.6 | 519.4 | 349.9
1368 | 1194 | 665.5 | 266.2 | 311.1725 | 410.7 | 433.6 | 383.1 | 364.4 | 736 | 56.5 | 18.7 | 100.4 | 5.9 | 206.6 | 8 | 811.7 | 842.4 | 798.3 | 818.5 | 859.1 | 772 | 762.1 | 821.7 | 786.9 | 808.3 | 195.9 | 287.6 | 371.1 | 334.6 | 426.4 | 400.8 | 359.6 | 374.7 | 519.5 | 350.2
1369 | 1195 | 667.7 | 267.08 | 312.2011 | 412.5 | 434.6 | 383.2 | 364.8 | 740.7 | 56.6 | 18.7 | 100.5 | 6 | 206 | 7.9 | 811.6 | 844.3 | 795.9 | 818.3 | 857.2 | 772.4 | 752.7 | 814.2 | 787.2 | 806 | 196.2 | 287.9 | 371.7 | 334.9 | 426.6 | 401.1 | 359.8 | 374.9 | 519.6 | 350.4
1370 | 1196 | 668.7 | 267.48 | 312.6687 | 414.3 | 434.3 | 383.6 | 365.4 | 732.4 | 56.5 | 18.7 | 100.5 | 6.1 | 204.7 | 7.9 | 811.4 | 849.1 | 794.8 | 818.6 | 857 | 772.1 | 750.1 | 812.6 | 787.5 | 805 | 196.4 | 288.1 | 371.5 | 335.1 | 426.7 | 401 | 360.1 | 375.1 | 519.7 | 350.7
1371 | 1197 | 669.1 | 267.64 | 312.8557 | 415.8 | 434.3 | 385.4 | 365.6 | 726 | 56.3 | 18.7 | 100.7 | 5.8 | 212.4 | 7.4 | 811.1 | 850.8 | 790 | 819 | 856.7 | 772.3 | 739.3 | 801.6 | 788.5 | 803.5 | 196.7 | 288.4 | 371.7 | 335.4 | 426.8 | 400.8 | 360.4 | 375.2 | 519.8 | 351
1372 | 1198 | 668.6 | 267.44 | 312.622 | 419.9 | 434.3 | 386.2 | 364.9 | 713.9 | 56.2 | 18.7 | 100.6 | 6.1 | 211.8 | 6.5 | 810.6 | 849.2 | 788.1 | 818.8 | 857 | 772 | 732.7 | 798.3 | 789.2 | 802.1 | 197 | 288.6 | 372.1 | 335.7 | 427.1 | 400.7 | 360.8 | 375.3 | 519.8 | 351.3
1373 | 1199 | 666.6 | 266.64 | 311.6868 | 422.6 | 434 | 386.2 | 364.7 | 714.7 | 56.2 | 18.7 | 100.6 | 6.9 | 212 | 5.6 | 810.2 | 845.4 | 790.8 | 818.8 | 858 | 771.5 | 738.7 | 801.6 | 789.7 | 803.4 | 197.2 | 288.9 | 372.1 | 336 | 427.5 | 400.7 | 361 | 375.5 | 519.8 | 351.6
1374 | 1200 | 668.3 | 267.32 | 312.4817 | 424.8 | 433.5 | 386.2 | 364.7 | 725.5 | 56.3 | 18.7 | 100.4 | 6.2 | 217.1 | 5 | 810.3 | 843.6 | 792 | 818.4 | 858.2 | 771.4 | 745.1 | 803 | 790.2 | 803.1 | 197.5 | 289.1 | 372.5 | 336.2 | 427.5 | 400.4 | 361.3 | 375.7 | 519.8 | 351.8
1375 | 1201 | 667.7 | 267.08 | 312.2011 | 427.4 | 433.3 | 385.8 | 364.7 | 742.2 | 56.4 | 18.7 | 100.3 | 6.5 | 236.5 | 4.8 | 810.2 | 843.9 | 792.3 | 816.7 | 858 | 771.7 | 741.9 | 800.5 | 790.3 | 802.5 | 197.7 | 289.4 | 372.9 | 336.5 | 427.8 | 400.5 | 361.6 | 375.8 | 520.1 | 352.1
1376 | 1202 | 667.7 | 267.08 | 312.2011 | 427.5 | 433.5 | 386.1 | 365.1 | 746.9 | 56.4 | 18.7 | 100.4 | 6.1 | 225.9 | 4.3 | 810.2 | 839 | 793.4 | 817.2 | 857.8 | 771.7 | 747.1 | 804.8 | 789.9 | 801.8 | 197.9 | 289.6 | 373.2 | 336.8 | 428 | 400.6 | 362 | 376 | 520.5 | 352.4
1377 | 1203 | 666.7 | 266.68 | 311.7336 | 427.5 | 434.4 | 386 | 365.3 | 745.1 | 56.5 | 18.7 | 100.5 | 6.4 | 224.2 | 4.2 | 810.2 | 839.8 | 792.3 | 817.5 | 856.1 | 771.8 | 744.6 | 807.4 | 790.2 | 803.2 | 198.2 | 289.9 | 373.6 | 337.1 | 428.3 | 400.7 | 362.3 | 376.1 | 521.1 | 352.7
1378 | 1204 | 666.6 | 266.64 | 311.6868 | 426.5 | 434.7 | 386.1 | 365.6 | 727.3 | 56.6 | 18.7 | 100.6 | 6.4 | 223.8 | 4.6 | 810.8 | 835.4 | 794.3 | 819.9 | 854.1 | 771.9 | 744.9 | 807.2 | 790.7 | 801.3 | 198.4 | 290.1 | 373.3 | 337.4 | 427.8 | 400.6 | 362.5 | 376.3 | 521.4 | 353
1379 | 1205 | 668 | 267.2 | 312.3414 | 425.2 | 435.1 | 386.6 | 365.4 | 702.8 | 56.6 | 18.7 | 100.6 | 6.7 | 220 | 4.8 | 811.1 | 829.7 | 794.9 | 821.2 | 853 | 771.7 | 753.5 | 814.8 | 791.6 | 799.7 | 198.6 | 290.4 | 373.3 | 337.7 | 427.6 | 400.8 | 362.6 | 376.5 | 521.7 | 353.2
1380 | 1206 | 668.4 | 267.36 | 312.5284 | 424.8 | 435.7 | 385.7 | 365.2 | 681.8 | 56.6 | 18.7 | 100.7 | 6.4 | 220.3 | 4.7 | 811.3 | 826.1 | 794.8 | 820.2 | 852.3 | 771.7 | 761.2 | 820.5 | 791.8 | 799.9 | 198.9 | 290.6 | 373.7 | 338 | 427.2 | 400.9 | 362.8 | 376.7 | 522.4 | 353.5
1381 | 1207 | 668.8 | 267.52 | 312.7155 | 423.7 | 436.1 | 385 | 365.1 | 696.2 | 56.7 | 18.7 | 100.7 | 5.4 | 226.7 | 4.6 | 811.2 | 829.7 | 796.6 | 819.2 | 852.1 | 772.3 | 758.2 | 821.6 | 792 | 799.3 | 199.1 | 290.9 | 374.4 | 338.3 | 427 | 400.8 | 363 | 376.8 | 523 | 353.7
1382 | 1208 | 668.3 | 267.32 | 312.4817 | 423.1 | 436.2 | 385.4 | 365.2 | 722.9 | 56.7 | 18.7 | 100.8 | 5.3 | 232.5 | 4.3 | 811.2 | 832 | 796.4 | 819.3 | 851.2 | 772.8 | 742.3 | 812 | 791.5 | 798 | 199.3 | 291.1 | 375.1 | 338.6 | 427.5 | 400.7 | 363.4 | 377 | 523.6 | 354
1383 | 1209 | 667.4 | 266.96 | 312.0609 | 422.6 | 436.6 | 386 | 365.6 | 733.8 | 56.7 | 18.7 | 100.8 | 5 | 239.7 | 4.2 | 811.5 | 834.1 | 796.5 | 821.6 | 848.8 | 773.2 | 728.5 | 799.9 | 791.7 | 793.9 | 199.6 | 291.4 | 375.4 | 338.8 | 428 | 400.6 | 363.7 | 377.1 | 524 | 354.3
1384 | 1210 | 666.9 | 266.76 | 311.8271 | 421.1 | 437.4 | 386.6 | 365.9 | 730.1 | 56.8 | 18.7 | 100.8 | 5.2 | 240.1 | 4.1 | 811.6 | 834.2 | 795.9 | 821.1 | 847.4 | 773.1 | 720.2 | 796.7 | 792.3 | 791.5 | 199.8 | 291.6 | 375.8 | 339.1 | 428.5 | 400.4 | 364 | 377.2 | 524.3 | 354.5
1385 | 1211 | 668.5 | 267.4 | 312.5752 | 420.2 | 437.3 | 387 | 366.3 | 743.4 | 56.8 | 18.7 | 100.8 | 4.7 | 241.3 | 3.9 | 811.6 | 835.3 | 795.1 | 819.2 | 846.2 | 772.9 | 721.2 | 797.1 | 792.3 | 791.5 | 200.1 | 291.9 | 376.1 | 339.4 | 428.8 | 400.5 | 364.4 | 377.3 | 524.4 | 354.8
1386 | 1212 | 667.7 | 267.08 | 312.2011 | 420.9 | 438.2 | 387.6 | 365.9 | 753.9 | 56.9 | 18.7 | 100.9 | 5.3 | 239 | 3.5 | 811.7 | 829.9 | 795.7 | 819.9 | 844.9 | 772.1 | 726.4 | 804.4 | 791.9 | 792.4 | 200.4 | 292.1 | 376.2 | 339.7 | 429.1 | 400.6 | 364.6 | 377.5 | 524.6 | 355.1
1387 | 1213 | 668.4 | 267.36 | 312.5284 | 421.5 | 439.4 | 388.1 | 365.6 | 761.5 | 56.9 | 18.7 | 100.8 | 5.5 | 235.6 | 3 | 812 | 829.7 | 795.4 | 819.8 | 846.1 | 772.1 | 737.1 | 809.5 | 792.4 | 792.7 | 200.6 | 292.4 | 376.6 | 340 | 429.4 | 400.8 | 365 | 377.6 | 524.8 | 355.4
1388 | 1214 | 669.1 | 267.64 | 312.8557 | 422.6 | 439.9 | 388.5 | 366.2 | 763.1 | 56.9 | 18.7 | 100.9 | 5.7 | 236.6 | 2.9 | 812.1 | 830.9 | 796.4 | 819.5 | 846.1 | 771.9 | 743.4 | 813.9 | 791.9 | 794.7 | 200.9 | 292.7 | 377 | 340.3 | 430 | 400.9 | 365.3 | 377.8 | 525.4 | 355.7
1389 | 1215 | 668.7 | 267.48 | 312.6687 | 423.9 | 440.3 | 389.5 | 366.3 | 754.7 | 56.9 | 18.7 | 100.8 | 5.7 | 240.6 | 3.2 | 812.5 | 829.6 | 797.4 | 819.5 | 845.9 | 771.9 | 746.1 | 815.1 | 791.5 | 796 | 201.2 | 292.9 | 377 | 340.6 | 430 | 400.7 | 365.7 | 378 | 525.8 | 356
1390 | 1216 | 667.8 | 267.12 | 312.2479 | 424.4 | 441.1 | 390 | 366.6 | 745.9 | 56.9 | 18.7 | 100.7 | 5.5 | 235.3 | 3.9 | 812.6 | 828.4 | 797.7 | 819 | 846.2 | 771.6 | 757.1 | 816.6 | 791 | 797.1 | 201.5 | 293.2 | 377 | 340.9 | 429.8 | 400.6 | 365.9 | 378.1 | 526 | 356.3
1391 | 1217 | 667.9 | 267.16 | 312.2946 | 424.3 | 440.7 | 390.4 | 366.8 | 736.3 | 56.9 | 18.7 | 100.7 | 5.8 | 230.2 | 4.7 | 812.9 | 829.2 | 798.7 | 819.2 | 846.7 | 771.4 | 764.4 | 820.9 | 790.7 | 798.1 | 201.8 | 293.4 | 377.2 | 341.2 | 429.8 | 400.6 | 366.2 | 378.4 | 526.3 | 356.5
1392 | 1218 | 667.4 | 266.96 | 312.0609 | 424.4 | 441 | 390.7 | 367.3 | 727.5 | 56.9 | 18.7 | 100.7 | 4.9 | 234.5 | 5.2 | 813.2 | 831.5 | 800.6 | 819.5 | 847.9 | 771.4 | 769.6 | 821 | 790.1 | 799 | 202.1 | 293.7 | 377.5 | 341.5 | 429.7 | 400.7 | 366.4 | 378.6 | 526.6 | 356.8
1393 | 1219 | 668 | 267.2 | 312.3414 | 424 | 441.6 | 390.8 | 367.6 | 732.2 | 56.9 | 18.7 | 100.6 | 4.8 | 231.2 | 5.3 | 813.5 | 833.2 | 800.2 | 820 | 848.4 | 771.9 | 756.2 | 820.9 | 790 | 797.2 | 202.3 | 293.9 | 378 | 341.8 | 429.8 | 400.7 | 366.7 | 378.7 | 526.9 | 357.1
1394 | 1220 | 668.1 | 267.24 | 312.3882 | 424.2 | 442.6 | 390.7 | 367.4 | 724.6 | 56.8 | 18.7 | 100.6 | 5.2 | 218.9 | 5.2 | 814.2 | 828.6 | 801.2 | 821.9 | 846.9 | 771.9 | 756 | 821.5 | 790 | 796.7 | 202.6 | 294.2 | 378 | 342.1 | 429.5 | 400.7 | 366.8 | 378.8 | 527.2 | 357.3
1395 | 1221 | 668.2 | 267.28 | 312.4349 | 424.5 | 444.3 | 391 | 367.4 | 714.3 | 56.8 | 18.7 | 100.6 | 5.6 | 218.5 | 4.8 | 814.5 | 832.7 | 800.3 | 821.9 | 846.4 | 771.7 | 757.6 | 824.7 | 790.5 | 796 | 202.8 | 294.4 | 378.3 | 342.4 | 429.6 | 400.6 | 367 | 379 | 527.6 | 357.6
1396 | 1222 | 668.4 | 267.36 | 312.5284 | 424.6 | 444.6 | 390.9 | 367.7 | 724.8 | 56.8 | 18.7 | 100.7 | 5.9 | 219 | 4.4 | 814.5 | 832.6 | 800.4 | 821.3 | 846.6 | 771.7 | 766.5 | 825.7 | 789.8 | 798.8 | 203.1 | 294.7 | 378.5 | 342.6 | 429.8 | 400.6 | 367.3 | 379.1 | 528.1 | 357.8
1397 | 1223 | 668.5 | 267.4 | 312.5752 | 424.7 | 443.6 | 391.3 | 368.1 | 730.6 | 56.8 | 18.7 | 100.9 | 6.1 | 218.1 | 4.7 | 814.6 | 827.1 | 799.6 | 820.8 | 846.8 | 771.7 | 776.9 | 824.4 | 789.5 | 799.5 | 203.3 | 294.9 | 378.6 | 342.9 | 429.7 | 400.7 | 367.5 | 379.3 | 528.4 | 358.1
1398 | 1224 | 668.4 | 267.36 | 312.5284 | 423.4 | 443 | 390.9 | 367.7 | 715.6 | 56.8 | 18.7 | 100.9 | 6.2 | 211.1 | 5.4 | 814.8 | 826.2 | 801.2 | 821.2 | 847.4 | 772.2 | 783.8 | 826 | 790 | 800.2 | 203.5 | 295.2 | 378.9 | 343.2 | 429.8 | 401.1 | 367.7 | 379.5 | 528.7 | 358.3
1399 | 1225 | 669 | 267.6 | 312.809 | 422.8 | 442.7 | 390.9 | 367.5 | 701.2 | 56.8 | 18.7 | 100.9 | 6.1 | 213.6 | 6 | 814.9 | 826.8 | 803.7 | 821.5 | 848.3 | 772.5 | 789 | 826.4 | 789.8 | 801.8 | 203.8 | 295.4 | 379 | 343.4 | 429.9 | 401.8 | 368 | 379.8 | 529.3 | 358.6
1400 | 1226 | 668.4 | 267.36 | 312.5284 | 423.5 | 443.2 | 391.4 | 368.2 | 677.9 | 56.9 | 18.7 | 100.9 | 6 | 222.8 | 6.5 | 815.1 | 829.8 | 802.8 | 822.8 | 846.8 | 772.5 | 791.3 | 833.5 | 789.8 | 800.2 | 204 | 295.7 | 378.9 | 343.7 | 430.5 | 402.7 | 368.3 | 380.1 | 529.7 | 358.8
1401 | 1227 | 668.4 | 267.36 | 312.5284 | 423.3 | 444.3 | 391.5 | 368.7 | 651.8 | 56.9 | 18.7 | 101 | 6.1 | 232.4 | 6.8 | 815.1 | 829.1 | 803.7 | 825.3 | 846.3 | 771.7 | 796.2 | 835.3 | 789.9 | 798.1 | 204.3 | 295.9 | 379.1 | 344 | 431.4 | 403.9 | 368.7 | 380.5 | 530.2 | 359.1
1402 | 1228 | 668.9 | 267.56 | 312.7622 | 423.1 | 446.5 | 391.5 | 370.2 | 638.3 | 57 | 18.7 | 101 | 5.4 | 216.2 | 6.7 | 815.4 | 832.3 | 802.9 | 825.8 | 848.7 | 771.4 | 783.6 | 830.4 | 790.3 | 797.6 | 204.5 | 296.2 | 379.3 | 344.3 | 431.4 | 404.4 | 368.9 | 380.8 | 530.7 | 359.4
1403 | 1229 | 668.7 | 267.48 | 312.6687 | 424.9 | 447 | 391.7 | 370.6 | 649.7 | 57 | 18.7 | 101 | 5.9 | 212.1 | 6.6 | 815.1 | 833.9 | 800.9 | 825.4 | 850.9 | 771.1 | 771.6 | 820.2 | 789.3 | 798.2 | 204.8 | 296.4 | 379.8 | 344.6 | 431.2 | 404.7 | 369.1 | 380.9 | 530.9 | 359.7
1404 | 1230 | 668.6 | 267.44 | 312.622 | 426.6 | 445.9 | 392 | 369.6 | 671 | 57.1 | 18.7 | 101.1 | 5.7 | 219.2 | 6.4 | 814.9 | 833.7 | 800.6 | 824.7 | 852.2 | 770.5 | 771 | 814.4 | 789.4 | 797.6 | 205.1 | 296.7 | 379.8 | 344.8 | 431.5 | 404.9 | 369.3 | 381 | 530.9 | 359.9
1405 | 1231 | 668.7 | 267.48 | 312.6687 | 427 | 444.9 | 392.2 | 369.2 | 667.5 | 57.1 | 18.7 | 101.1 | 5.9 | 224.3 | 5.9 | 815 | 832.4 | 800.4 | 823.9 | 853.3 | 769.8 | 777.3 | 818.1 | 790 | 798.9 | 205.4 | 296.9 | 379.8 | 345.1 | 431.4 | 405.5 | 369.5 | 381.3 | 530.9 | 360.1
1406 | 1232 | 667.7 | 267.08 | 312.2011 | 426.9 | 443.5 | 391 | 368.9 | 666.4 | 57.1 | 18.7 | 101.3 | 6.1 | 233.2 | 5.2 | 814.9 | 833.9 | 799.8 | 823.9 | 854.4 | 769.4 | 779.5 | 821.6 | 790.1 | 800.5 | 205.6 | 297.1 | 380.1 | 345.3 | 431.3 | 405.7 | 369.7 | 381.4 | 531 | 360.4
1407 | 1233 | 668.8 | 267.52 | 312.7155 | 427 | 441.4 | 389.8 | 369.1 | 667.3 | 57.2 | 18.7 | 101.6 | 6.3 | 224.4 | 4.9 | 814.7 | 839 | 798.5 | 824.4 | 856.1 | 769.2 | 773.2 | 819.4 | 789.9 | 801.2 | 205.9 | 297.4 | 380.4 | 345.6 | 431.1 | 405.3 | 369.8 | 381.5 | 531.1 | 360.6
1408 | 1234 | 669.1 | 267.64 | 312.8557 | 426.9 | 439.8 | 389.8 | 369 | 676 | 57.3 | 18.7 | 101.7 | 5.5 | 222.7 | 5 | 814.5 | 838.7 | 797.9 | 824.5 | 856.9 | 769.2 | 767.8 | 816.1 | 789.7 | 801.2 | 206.2 | 297.6 | 380.6 | 345.8 | 430.9 | 405.1 | 370 | 381.6 | 531.1 | 360.8
1409 | 1235 | 667.6 | 267.04 | 312.1544 | 426.9 | 439.2 | 389.2 | 368.6 | 696.1 | 57.3 | 18.7 | 101.9 | 5.8 | 234.3 | 5 | 814.4 | 844.3 | 796.2 | 825.1 | 858.3 | 769 | 765.8 | 813.4 | 790.1 | 801.5 | 206.4 | 297.8 | 381 | 346 | 430.5 | 404.8 | 370.1 | 381.6 | 531 | 361.1
1410 | 1236 | 668.3 | 267.32 | 312.4817 | 428.2 | 439.1 | 389.1 | 367.8 | 703.5 | 57.4 | 18.7 | 101.9 | 6.1 | 235.9 | 5 | 814.2 | 845.8 | 793.7 | 824.7 | 858.3 | 769.5 | 762.4 | 807 | 790.7 | 801.2 | 206.6 | 298.1 | 381.1 | 346.2 | 430.1 | 404.6 | 370.2 | 381.8 | 531 | 361.3
1411 | 1237 | 668 | 267.2 | 312.3414 | 430.1 | 438.5 | 389.2 | 366.7 | 691.1 | 57.4 | 18.7 | 102.1 | 6.3 | 231.8 | 4.9 | 813.8 | 845.7 | 792 | 824.4 | 859 | 769.1 | 758.6 | 803 | 791.5 | 800.8 | 206.9 | 298.3 | 381.2 | 346.4 | 429.7 | 404.3 | 370.4 | 381.8 | 531 | 361.5
1412 | 1238 | 668.4 | 267.36 | 312.5284 | 431.8 | 437.7 | 388.4 | 365.6 | 674.6 | 57.5 | 18.7 | 102.2 | 7.2 | 218.4 | 4.9 | 813.4 | 841.2 | 792.2 | 824.6 | 860 | 768.4 | 760 | 803.3 | 791.6 | 801.9 | 207.1 | 298.5 | 381.2 | 346.6 | 429.3 | 404.2 | 370.5 | 381.9 | 530.9 | 361.7
1413 | 1239 | 668.3 | 267.32 | 312.4817 | 433.2 | 436.9 | 387.9 | 365.1 | 672.5 | 57.4 | 18.7 | 102.3 | 6.3 | 204.7 | 5.3 | 813.1 | 841.8 | 792.7 | 823.2 | 860.4 | 767.6 | 768.1 | 806.8 | 791.4 | 803.8 | 207.3 | 298.7 | 381.4 | 346.8 | 429.2 | 404.1 | 370.7 | 382.1 | 530.9 | 362
1414 | 1240 | 668.6 | 267.44 | 312.622 | 433.9 | 435.8 | 387.4 | 364.4 | 684.6 | 57.3 | 18.7 | 102.3 | 6.2 | 208.7 | 6.1 | 812.9 | 845.4 | 792.1 | 822.8 | 861.2 | 766.9 | 772.9 | 809.3 | 791.1 | 805.3 | 207.6 | 298.9 | 381.6 | 347 | 429.1 | 404.3 | 370.8 | 382.2 | 531.1 | 362.2
1415 | 1241 | 668.5 | 267.4 | 312.5752 | 436.1 | 435.1 | 386.7 | 363 | 697.3 | 57.2 | 18.7 | 102.3 | 6.7 | 206.1 | 7.1 | 812.7 | 844.4 | 792.2 | 823 | 860.5 | 766.6 | 769.7 | 814.1 | 790.5 | 807.3 | 207.8 | 299.2 | 382 | 347.2 | 429.3 | 404.4 | 370.9 | 382.2 | 531.2 | 362.4
1416 | 1242 | 668.6 | 267.44 | 312.622 | 438 | 434.6 | 387.1 | 362.1 | 711.5 | 57.1 | 18.7 | 102.4 | 6.4 | 193.2 | 7.4 | 812.8 | 844 | 793 | 822.8 | 859.7 | 766.6 | 765.3 | 814 | 790 | 807.2 | 208 | 299.4 | 382.4 | 347.4 | 429.9 | 404.4 | 371.1 | 382.3 | 531.3 | 362.7
1417 | 1243 | 668.2 | 267.28 | 312.4349 | 438.6 | 434.3 | 386.8 | 361.7 | 727.7 | 57 | 18.6 | 102.5 | 6 | 196.4 | 7.4 | 812.7 | 844.2 | 792.8 | 822.9 | 858.9 | 767.3 | 752.5 | 809.2 | 790.5 | 805.1 | 208.2 | 299.6 | 383.1 | 347.6 | 430.4 | 404.5 | 371.5 | 382.5 | 531.5 | 362.9
1418 | 1244 | 668.5 | 267.4 | 312.5752 | 440 | 434.4 | 386.9 | 362.2 | 737 | 57 | 18.6 | 102.5 | 6.5 | 194.3 | 6.9 | 812.6 | 840 | 793.1 | 822.6 | 858.6 | 766.9 | 756.2 | 811.9 | 790.5 | 805.4 | 208.5 | 299.9 | 383 | 347.8 | 430.8 | 404.4 | 371.8 | 382.6 | 531.7 | 363.2
1419 | 1245 | 668.5 | 267.4 | 312.5752 | 439.5 | 435.7 | 386.8 | 362.2 | 744.9 | 57.1 | 18.6 | 102.4 | 5.9 | 206.3 | 5.8 | 812.7 | 839.2 | 794.6 | 823.5 | 859 | 766.7 | 761.8 | 814.6 | 790.1 | 806.2 | 208.7 | 300.1 | 383.2 | 348 | 431.3 | 404.5 | 372.1 | 382.7 | 531.7 | 363.4
1420 | 1246 | 668.5 | 267.4 | 312.5752 | 439.3 | 436.2 | 386.4 | 362.7 | 734.9 | 57.2 | 18.6 | 102.4 | 5.7 | 216.4 | 5.2 | 812.6 | 838.2 | 796.6 | 823.9 | 861.1 | 766.4 | 764.3 | 816.4 | 790.3 | 807.7 | 208.9 | 300.4 | 383.2 | 348.2 | 431.3 | 404.7 | 372.3 | 382.9 | 531.7 | 363.7
1421 | 1247 | 668.7 | 267.48 | 312.6687 | 439.9 | 435.7 | 386.2 | 363.6 | 722.4 | 57.2 | 18.6 | 102.4 | 6.1 | 198.8 | 4.7 | 812.5 | 841.5 | 796.1 | 824.8 | 862.5 | 766.1 | 767.7 | 817 | 790.1 | 808.4 | 209.2 | 300.6 | 383.4 | 348.4 | 431 | 405.2 | 372.4 | 383 | 531.7 | 363.9
1422 | 1248 | 670.1 | 268.04 | 313.3233 | 439.8 | 435.5 | 385.9 | 363.2 | 720.2 | 57.3 | 18.6 | 102.5 | 5.9 | 207.6 | 4.4 | 812.5 | 841.4 | 796.1 | 824.7 | 863.5 | 765.5 | 771.5 | 817.2 | 789.8 | 808.4 | 209.4 | 300.8 | 383.6 | 348.7 | 430.6 | 405.4 | 372.6 | 383.2 | 531.7 | 364.2
1423 | 1249 | 670.1 | 268.04 | 313.3233 | 442.1 | 435.1 | 385.8 | 362.1 | 711.6 | 57.3 | 18.6 | 102.6 | 5.5 | 227 | 4.2 | 812.8 | 840.6 | 796.6 | 825.1 | 863.9 | 765.1 | 775.3 | 818.5 | 790.1 | 808.3 | 209.6 | 301.1 | 383.6 | 348.9 | 430.1 | 405.9 | 372.7 | 383.4 | 531.7 | 364.4
1424 | 1250 | 668.1 | 267.24 | 312.3882 | 443.6 | 434.7 | 386.2 | 361.6 | 700.6 | 57.3 | 18.6 | 102.7 | 5.4 | 229.6 | 4.6 | 813.2 | 834.7 | 798.3 | 824.9 | 864.5 | 764.9 | 784.4 | 821.7 | 790 | 809.2 | 209.8 | 301.3 | 383.7 | 349.1 | 429.5 | 406.2 | 372.8 | 383.6 | 531.9 | 364.6
1425 | 1251 | 668.9 | 267.56 | 312.7622 | 442.7 | 434.8 | 385.9 | 361.7 | 695.8 | 57.4 | 18.6 | 102.7 | 6.2 | 216.9 | 5.2 | 813.3 | 834.3 | 800.1 | 824.8 | 865.3 | 764.8 | 788.2 | 823 | 789.9 | 810.1 | 210.1 | 301.6 | 383.9 | 349.3 | 429.3 | 406.3 | 372.9 | 383.8 | 532 | 364.8
1426 | 1252 | 669.1 | 267.64 | 312.8557 | 442 | 434.9 | 386 | 362.3 | 701.4 | 57.4 | 18.6 | 102.9 | 6.2 | 204.1 | 5.5 | 813.6 | 835.9 | 801.3 | 824.7 | 866.7 | 764.6 | 787.9 | 819.4 | 789.4 | 809.9 | 210.3 | 301.8 | 384.1 | 349.5 | 429.2 | 406.4 | 373.1 | 383.9 | 532.2 | 365
1427 | 1253 | 668.3 | 267.32 | 312.4817 | 440.8 | 435.1 | 386 | 363.1 | 690.9 | 57.5 | 18.6 | 103.1 | 5.5 | 212 | 5.9 | 813.7 | 839.1 | 801.2 | 825.5 | 867.4 | 764.1 | 789.4 | 819.3 | 788.5 | 810.9 | 210.6 | 302 | 384.2 | 349.7 | 429.2 | 406.8 | 373.3 | 384.1 | 532.3 | 365.2
1428 | 1254 | 668.6 | 267.44 | 312.622 | 440.4 | 435 | 385.7 | 363.7 | 680.9 | 57.5 | 18.6 | 103.1 | 6.2 | 230.9 | 5.2 | 813.6 | 842 | 799 | 825.9 | 868.2 | 764 | 788 | 821.3 | 788 | 812.2 | 210.8 | 302.3 | 384.3 | 349.9 | 429.1 | 407.1 | 373.5 | 384.4 | 532.3 | 365.5
1429 | 1255 | 669.7 | 267.88 | 313.1363 | 441.9 | 434.4 | 385.4 | 363.4 | 688.2 | 57.6 | 18.6 | 103.2 | 6.8 | 235.2 | 4.5 | 813.5 | 841.5 | 799.1 | 826.8 | 868.5 | 763.8 | 782.8 | 819 | 788.2 | 812.9 | 211 | 302.5 | 384.6 | 350.1 | 428.8 | 406.9 | 373.6 | 384.6 | 532.2 | 365.7
1430 | 1256 | 670.2 | 268.08 | 313.3701 | 442.4 | 434.1 | 385.3 | 363 | 697.9 | 57.6 | 18.6 | 103.2 | 6.3 | 224.6 | 4.3 | 813.8 | 837.2 | 799.9 | 826.5 | 869.2 | 763.6 | 782.3 | 818.3 | 788.6 | 812.6 | 211.2 | 302.8 | 384.8 | 350.2 | 428.7 | 406.8 | 373.7 | 384.7 | 532.2 | 365.9
1431 | 1257 | 668.5 | 267.4 | 312.5752 | 441.4 | 434.3 | 384.7 | 362.3 | 707.5 | 57.7 | 18.6 | 103.3 | 5.7 | 187.6 | 4.9 | 813.9 | 834.1 | 800.5 | 825.6 | 867.8 | 763.5 | 778.3 | 816.7 | 789 | 812.8 | 211.5 | 303 | 385 | 350.4 | 428.6 | 406.7 | 373.9 | 384.8 | 532.2 | 366.1
1432 | 1258 | 667.8 | 267.12 | 312.2479 | 441.9 | 435.2 | 385.4 | 361.4 | 717 | 57.7 | 18.6 | 103.5 | 6.3 | 190.5 | 5.7 | 814 | 833.7 | 801.5 | 825.3 | 868 | 763.7 | 771.8 | 814.8 | 789.4 | 811.8 | 211.7 | 303.3 | 385.3 | 350.6 | 428.6 | 406.9 | 374 | 384.9 | 532.4 | 366.3
1433 | 1259 | 668.3 | 267.32 | 312.4817 | 442 | 436 | 386.1 | 360.6 | 715.4 | 57.7 | 18.6 | 103.5 | 6.3 | 206.7 | 5.8 | 814.1 | 832.6 | 800.7 | 825.1 | 868.2 | 763.6 | 780.9 | 817.1 | 789.1 | 813.6 | 211.9 | 303.6 | 385.3 | 350.8 | 428.8 | 407.2 | 374.2 | 385.1 | 532.4 | 366.5
1434 | 1260 | 667.5 | 267 | 312.1076 | 440.4 | 436 | 386.8 | 360.4 | 699.4 | 57.8 | 18.6 | 103.5 | 6.6 | 216.7 | 5.8 | 814.2 | 830.7 | 801.9 | 825.3 | 868.2 | 763.6 | 787.4 | 814.9 | 788.8 | 813.1 | 212.2 | 303.8 | 385.3 | 350.9 | 428.8 | 407.6 | 374.3 | 385.4 | 532.5 | 366.7
1435 | 1261 | 669.3 | 267.72 | 312.9493 | 438.3 | 436.2 | 386.8 | 361.5 | 671.9 | 57.8 | 18.6 | 103.6 | 6.2 | 218.4 | 5.7 | 814 | 827.7 | 802.2 | 825.3 | 867.3 | 763.3 | 793.8 | 817.2 | 788.8 | 812.1 | 212.4 | 304.1 | 385.3 | 351.1 | 428.8 | 408.2 | 374.5 | 385.7 | 532.7 | 366.9
1436 | 1262 | 668.2 | 267.28 | 312.4349 | 435.7 | 436.8 | 387.3 | 362.2 | 658.9 | 57.9 | 18.6 | 103.6 | 6.6 | 199.4 | 6.2 | 814.4 | 826.5 | 803.7 | 826.1 | 864.2 | 763.6 | 786.6 | 822.3 | 789.3 | 810.9 | 212.7 | 304.4 | 385.6 | 351.3 | 429 | 408.3 | 374.7 | 385.8 | 533 | 367.2
1437 | 1263 | 667.7 | 267.08 | 312.2011 | 434.6 | 438.2 | 387.8 | 362.4 | 675.7 | 58 | 18.6 | 103.6 | 5.8 | 204.3 | 6.7 | 814.4 | 829.6 | 803 | 826 | 863.6 | 764 | 770.3 | 814.2 | 789.6 | 807.4 | 212.9 | 304.7 | 386.3 | 351.4 | 429.6 | 407.8 | 374.9 | 385.8 | 533.3 | 367.4
1438 | 1264 | 667.7 | 267.08 | 312.2011 | 435.4 | 439.7 | 388.1 | 362.9 | 692.5 | 58 | 18.6 | 103.6 | 6.7 | 198 | 6.9 | 814.1 | 833.3 | 800.3 | 825.5 | 864.4 | 764.2 | 760.2 | 803.9 | 789.2 | 806.5 | 213.1 | 305 | 386.4 | 351.6 | 430 | 407.7 | 375.2 | 385.9 | 533.6 | 367.6
1439 | 1265 | 667.6 | 267.04 | 312.1544 | 436.1 | 439.4 | 388.4 | 363.7 | 683.2 | 58.1 | 18.6 | 103.6 | 7.1 | 186.8 | 6.6 | 813.8 | 834.6 | 800.2 | 825.5 | 864.4 | 763.5 | 767.5 | 806.1 | 788.6 | 808.1 | 213.4 | 305.3 | 386.3 | 351.8 | 429.9 | 408.1 | 375.3 | 386.2 | 533.6 | 367.8
1440 | 1266 | 667 | 266.8 | 311.8738 | 436 | 438 | 388.4 | 364.4 | 673.8 | 58.2 | 18.6 | 103.5 | 6.7 | 221.7 | 6.6 | 813.6 | 831.9 | 799.5 | 825.5 | 864.5 | 762.7 | 776.4 | 807.8 | 788.2 | 808.7 | 213.6 | 305.6 | 386.2 | 352 | 429.8 | 408.3 | 375.5 | 386.4 | 533.5 | 368
1441 | 1267 | 667.6 | 267.04 | 312.1544 | 436.6 | 436.7 | 388.1 | 364.9 | 658.2 | 58.2 | 18.6 | 103.5 | 6.8 | 233.2 | 6 | 813.3 | 832.1 | 798.1 | 824.5 | 865 | 762.2 | 777.3 | 808.8 | 787.8 | 809.5 | 213.8 | 305.9 | 386.3 | 352.2 | 429.8 | 408.3 | 375.5 | 386.5 | 533.5 | 368.2
1442 | 1268 | 668.7 | 267.48 | 312.6687 | 438.3 | 436 | 387.4 | 364.9 | 650.4 | 58.3 | 18.6 | 103.5 | 7.2 | 205 | 5.9 | 813.1 | 831.9 | 798 | 824.5 | 865.3 | 761.9 | 780.8 | 813 | 787.6 | 810.7 | 214 | 306.2 | 386.5 | 352.4 | 429.7 | 407.9 | 375.6 | 386.6 | 533.4 | 368.4
1443 | 1269 | 668.5 | 267.4 | 312.5752 | 437.6 | 436.1 | 387.1 | 364.2 | 652 | 58.4 | 18.6 | 103.4 | 7.4 | 211 | 6.2 | 813.3 | 830.2 | 798.9 | 824.2 | 865.9 | 762.1 | 787.8 | 815.5 | 788 | 811.7 | 214.2 | 306.5 | 386.7 | 352.6 | 429.7 | 407.7 | 375.8 | 386.6 | 533.4 | 368.6
1444 | 1270 | 668.6 | 267.44 | 312.622 | 435.9 | 436.6 | 387.4 | 363.7 | 662.6 | 58.4 | 18.6 | 103.3 | 6.6 | 223.8 | 5.9 | 813.1 | 831.9 | 798.8 | 824.2 | 867.3 | 762.3 | 784 | 817.5 | 787.7 | 813.2 | 214.4 | 306.7 | 386.9 | 352.8 | 429.6 | 407.7 | 375.9 | 386.7 | 533.6 | 368.8
1445 | 1271 | 668.5 | 267.4 | 312.5752 | 434.7 | 437.4 | 388.7 | 363.5 | 666.8 | 58.4 | 18.6 | 103.4 | 7.3 | 233.5 | 5.3 | 813 | 831.1 | 798.7 | 823.9 | 866.9 | 762.4 | 787.8 | 817.7 | 787.3 | 814.3 | 214.6 | 307 | 386.9 | 353 | 429.4 | 408.1 | 376 | 386.8 | 533.8 | 369
1446 | 1272 | 669.1 | 267.64 | 312.8557 | 433.6 | 437.7 | 388.6 | 362.9 | 660.6 | 58.4 | 18.6 | 103.5 | 7.3 | 219.3 | 4.7 | 812.8 | 828.9 | 798.9 | 824.3 | 864.2 | 762.6 | 793 | 818.3 | 787.4 | 815.3 | 214.8 | 307.3 | 387 | 353.1 | 429.5 | 408.8 | 376.1 | 387.1 | 533.9 | 369.3
1447 | 1273 | 668.5 | 267.4 | 312.5752 | 433.2 | 437.5 | 387.5 | 363.1 | 649.9 | 58.4 | 18.6 | 103.6 | 6.3 | 214.4 | 3.8 | 813 | 826.4 | 799.3 | 823.9 | 863 | 762.4 | 799.4 | 818.2 | 787.2 | 815.8 | 215 | 307.5 | 387.1 | 353.3 | 429.8 | 409.2 | 376.4 | 387.3 | 534 | 369.5
1448 | 1274 | 669.5 | 267.8 | 313.0428 | 432.3 | 437.6 | 386.7 | 363.6 | 644.6 | 58.4 | 18.6 | 103.6 | 6.3 | 247.8 | 3.3 | 813.2 | 825.2 | 800.7 | 824.4 | 866.2 | 762.9 | 805.5 | 823.4 | 787.7 | 815.5 | 215.1 | 307.8 | 387.3 | 353.5 | 430.3 | 409.9 | 376.7 | 387.6 | 534.2 | 369.7
1449 | 1275 | 668.3 | 267.32 | 312.4817 | 432.2 | 437.8 | 386.5 | 363.9 | 642.9 | 58.4 | 18.6 | 103.4 | 6.9 | 253.8 | 3.2 | 813.2 | 827.3 | 801.1 | 824 | 866.4 | 763.1 | 808.8 | 824.8 | 787.7 | 814.8 | 215.3 | 308 | 387.4 | 353.7 | 430.4 | 410.5 | 376.9 | 387.8 | 534.6 | 369.9
1450 | 1276 | 668.2 | 267.28 | 312.4349 | 430.6 | 437.9 | 386.2 | 364.3 | 648.7 | 58.5 | 18.6 | 103.4 | 6.7 | 247.7 | 3.4 | 813.1 | 829.8 | 802.5 | 824.1 | 863.7 | 763.1 | 808.4 | 823.3 | 787.1 | 815.5 | 215.5 | 308.3 | 387.5 | 353.9 | 430.6 | 410.9 | 377.1 | 388 | 535 | 370.1
1451 | 1277 | 669.8 | 267.92 | 313.183 | 429.3 | 437.6 | 385.3 | 364 | 637.1 | 58.5 | 18.6 | 103.5 | 6.3 | 250.1 | 4.4 | 812.9 | 829.9 | 803.2 | 823.7 | 862.1 | 762.5 | 806.9 | 819.7 | 786.2 | 815.6 | 215.7 | 308.5 | 387.5 | 354.1 | 430.4 | 411.1 | 377.3 | 388.3 | 535.1 | 370.3
1452 | 1278 | 669.8 | 267.92 | 313.183 | 428.6 | 436.7 | 385.1 | 364 | 635.4 | 58.6 | 18.6 | 103.5 | 6.4 | 244.1 | 5 | 812.8 | 828 | 802.9 | 823.2 | 863.1 | 761.8 | 807.3 | 818.3 | 785.6 | 816.3 | 215.9 | 308.7 | 387.6 | 354.3 | 430.2 | 411.3 | 377.5 | 388.4 | 535 | 370.5
1453 | 1279 | 670.6 | 268.24 | 313.5571 | 427.9 | 436.3 | 384.9 | 364 | 656.7 | 58.5 | 18.5 | 103.6 | 5.9 | 231.5 | 5.4 | 812.6 | 828.2 | 801.8 | 822.8 | 865.6 | 761.5 | 806 | 817.3 | 785.1 | 817 | 216 | 308.9 | 388 | 354.5 | 430.4 | 411 | 377.6 | 388.5 | 535 | 370.7
1454 | 1280 | 669.3 | 267.72 | 312.9493 | 429.5 | 436.2 | 384.6 | 363.8 | 672.9 | 58.5 | 18.6 | 103.6 | 6.2 | 246.8 | 5.7 | 812.3 | 831 | 800.3 | 823.1 | 865.5 | 761.4 | 805.8 | 818 | 784.4 | 818.4 | 216.1 | 309.1 | 388.3 | 354.7 | 430.7 | 411.3 | 377.9 | 388.7 | 535.1 | 370.9
1455 | 1281 | 668.8 | 267.52 | 312.7155 | 430.3 | 436.3 | 384.8 | 364.5 | 675 | 58.6 | 18.5 | 103.6 | 6.3 | 246.3 | 5.8 | 812.4 | 832.4 | 800.4 | 823.7 | 866.5 | 761.6 | 803.2 | 819.2 | 784.9 | 820.4 | 216.3 | 309.4 | 388.4 | 354.9 | 430.8 | 411.3 | 378.1 | 388.8 | 535.1 | 371.1
1456 | 1282 | 668 | 267.2 | 312.3414 | 430.1 | 436.7 | 384.4 | 364.8 | 673.7 | 58.6 | 18.5 | 103.7 | 6 | 225 | 5.3 | 812.6 | 827.8 | 800.4 | 823.1 | 869.1 | 761.6 | 807.5 | 814.1 | 785.2 | 820.6 | 216.5 | 309.6 | 388.4 | 355.1 | 430.8 | 411.1 | 378.3 | 388.9 | 535.1 | 371.3
1457 | 1283 | 667.7 | 267.08 | 312.2011 | 431 | 437.7 | 384.5 | 365.1 | 688.8 | 58.7 | 18.5 | 103.8 | 6 | 228.6 | 5 | 812.6 | 824.4 | 800.1 | 822.3 | 867.6 | 762 | 807.6 | 816.4 | 785.7 | 820.8 | 216.6 | 309.7 | 388.7 | 355.4 | 430.9 | 410.5 | 378.5 | 388.9 | 535.3 | 371.5
1458 | 1284 | 666.7 | 266.68 | 311.7336 | 430.6 | 437.9 | 384.5 | 364.9 | 694.9 | 58.6 | 18.5 | 104 | 6.4 | 251.1 | 4.9 | 812.8 | 824.4 | 801.1 | 821.9 | 865.8 | 762.5 | 803.6 | 816.4 | 786.2 | 819.5 | 216.8 | 309.9 | 388.9 | 355.6 | 431 | 409.9 | 378.8 | 389 | 535.6 | 371.7
1459 | 1285 | 669.6 | 267.84 | 313.0895 | 429.2 | 438.7 | 384.6 | 365.3 | 711.2 | 58.6 | 18.5 | 104.1 | 6.6 | 234.5 | 4.9 | 813.2 | 827.2 | 803.2 | 822.9 | 864.4 | 762.9 | 797.8 | 817.6 | 786.6 | 817.6 | 217 | 310.1 | 389.2 | 355.8 | 431.3 | 409.5 | 379.1 | 389.1 | 535.9 | 372
1460 | 1286 | 668.7 | 267.48 | 312.6687 | 429.2 | 440.5 | 383.8 | 366.5 | 702.3 | 58.5 | 18.5 | 104.1 | 5.9 | 208 | 4.7 | 813.6 | 831.1 | 804.9 | 823.1 | 863.9 | 762.7 | 795.5 | 821.8 | 787.2 | 815.6 | 217.2 | 310.3 | 389.2 | 356 | 431.4 | 409.5 | 379.4 | 389.3 | 536.3 | 372.2
1461 | 1287 | 668.3 | 267.32 | 312.4817 | 429.9 | 441.8 | 384.1 | 367.1 | 701.5 | 58.5 | 18.5 | 104.2 | 5.2 | 203 | 4.6 | 813.4 | 833.3 | 803.7 | 823 | 862.8 | 762.3 | 788.4 | 823.8 | 787.2 | 816.5 | 217.4 | 310.5 | 389.4 | 356.3 | 431.4 | 409.3 | 379.6 | 389.4 | 536.4 | 372.4
1462 | 1288 | 668.7 | 267.48 | 312.6687 | 432.5 | 441.6 | 384.9 | 367.5 | 714 | 58.5 | 18.5 | 104.2 | 6.2 | 217.2 | 4 | 813.3 | 837.8 | 799.7 | 824 | 858.5 | 762.2 | 774.2 | 818.1 | 787 | 816.7 | 217.6 | 310.6 | 389.9 | 356.5 | 431.5 | 409 | 379.8 | 389.4 | 536.5 | 372.6
1463 | 1289 | 669.4 | 267.76 | 312.996 | 434.8 | 441.3 | 385.5 | 367.4 | 712.6 | 58.6 | 18.5 | 104.2 | 5.4 | 226.2 | 3.8 | 813.1 | 843.5 | 792.8 | 824.6 | 852.2 | 762.4 | 760.6 | 801.2 | 787.8 | 815.7 | 217.8 | 310.8 | 390.2 | 356.8 | 431.6 | 408.6 | 380 | 389.4 | 536.4 | 372.8
1464 | 1290 | 667.6 | 267.04 | 312.1544 | 436.5 | 441.1 | 387 | 368 | 712.1 | 58.6 | 18.5 | 104.2 | 6 | 236.5 | 3.9 | 812.8 | 844.7 | 787.5 | 825 | 846 | 762.8 | 743.3 | 784.8 | 788.5 | 814.7 | 218 | 311 | 390.4 | 357 | 431.9 | 408.5 | 380.3 | 389.5 | 536.3 | 373
1465 | 1291 | 666.8 | 266.72 | 311.7803 | 436.7 | 441.4 | 387.8 | 368.7 | 717.6 | 58.5 | 18.5 | 104.1 | 5.8 | 238.5 | 3.7 | 812.7 | 842.6 | 790.3 | 824.1 | 846.3 | 762.5 | 740.3 | 787.3 | 789.2 | 815.2 | 218.1 | 311.2 | 390.7 | 357.3 | 432.6 | 408.3 | 380.6 | 389.6 | 536.2 | 373.2
1466 | 1292 | 669.2 | 267.68 | 312.9025 | 438.1 | 441.9 | 388.3 | 370 | 726.3 | 58.5 | 18.5 | 104.2 | 5.6 | 249.3 | 3.9 | 812.6 | 839.7 | 792 | 822.8 | 846.8 | 762.1 | 741.5 | 790.4 | 789.7 | 815 | 218.3 | 311.3 | 391 | 357.5 | 433.3 | 408.2 | 381 | 389.7 | 536.2 | 373.5
1467 | 1293 | 668.1 | 267.24 | 312.3882 | 440.1 | 442.5 | 388.9 | 370.6 | 734.9 | 58.5 | 18.5 | 104.3 | 5.3 | 244.3 | 4.2 | 812.5 | 841.7 | 790.9 | 823 | 845.1 | 761.7 | 733.2 | 786.8 | 790 | 813.7 | 218.6 | 311.5 | 391.1 | 357.8 | 433.8 | 408 | 381.4 | 389.8 | 536.2 | 373.7
1468 | 1294 | 666.4 | 266.56 | 311.5933 | 441.2 | 442.8 | 389.8 | 370.6 | 738 | 58.6 | 18.5 | 104.3 | 5.2 | 220.9 | 4.4 | 812.1 | 842.1 | 790.1 | 823.2 | 841.9 | 761.7 | 728.2 | 780.5 | 790.5 | 811.6 | 218.8 | 311.6 | 391.3 | 358 | 433.8 | 408 | 381.6 | 389.9 | 536.1 | 373.9
1469 | 1295 | 668 | 267.2 | 312.3414 | 441.7 | 443 | 389.2 | 370.4 | 727.6 | 58.7 | 18.5 | 104.3 | 6.1 | 226.2 | 4.5 | 812 | 835.4 | 791.8 | 822.5 | 846.4 | 761.3 | 745.9 | 789.1 | 790.2 | 812.9 | 219 | 311.8 | 391.2 | 358.3 | 433.8 | 407.9 | 381.9 | 390 | 536.1 | 374.1
1470 | 1296 | 667.9 | 267.16 | 312.2946 | 442 | 442.5 | 388.2 | 370.3 | 713.2 | 58.8 | 18.5 | 104.2 | 6.1 | 249.5 | 5 | 812.1 | 833 | 796.1 | 822.6 | 848.8 | 761.3 | 757.9 | 798 | 790.6 | 813.4 | 219.2 | 312 | 391.4 | 358.6 | 433.9 | 407.9 | 382 | 390.2 | 536.2 | 374.3
1471 | 1297 | 669.6 | 267.84 | 313.0895 | 443.8 | 442 | 387.8 | 369.9 | 715.9 | 58.9 | 18.5 | 104.1 | 5.2 | 243 | 4.8 | 812.4 | 833.9 | 798.1 | 823.2 | 851.3 | 760.8 | 760 | 800.6 | 790.6 | 812.5 | 219.4 | 312.1 | 391.7 | 358.9 | 433.7 | 407.6 | 382.1 | 390.2 | 536.4 | 374.5
1472 | 1298 | 667.8 | 267.12 | 312.2479 | 445.4 | 441.7 | 387 | 369.3 | 721.4 | 58.8 | 18.5 | 104.1 | 5.3 | 234.1 | 4.5 | 812.3 | 839.9 | 799.4 | 823.5 | 853.8 | 760.6 | 766 | 803.9 | 790.2 | 813 | 219.6 | 312.3 | 391.7 | 359.2 | 433.5 | 407.6 | 382.2 | 390.4 | 536.5 | 374.7
1473 | 1299 | 667.9 | 267.16 | 312.2946 | 445 | 441.1 | 387.6 | 369 | 702.3 | 58.8 | 18.5 | 104.3 | 5.7 | 256.8 | 4.2 | 812.2 | 844.2 | 798.7 | 825.1 | 856.7 | 760 | 775.4 | 805.2 | 789.8 | 814.6 | 219.8 | 312.4 | 391.6 | 359.5 | 433.2 | 407.9 | 382.3 | 390.5 | 536.5 | 374.9
1474 | 1300 | 667.9 | 267.16 | 312.2946 | 445.2 | 440.8 | 387.5 | 369.1 | 682.8 | 58.9 | 18.5 | 104.5 | 5.8 | 242.2 | 4.2 | 812.4 | 846.4 | 798.6 | 824.6 | 858.8 | 759.6 | 776.5 | 803.9 | 789.3 | 816 | 220 | 312.5 | 391.7 | 359.7 | 432.8 | 408.2 | 382.5 | 390.7 | 536.5 | 375.1
1475 | 1301 | 667.8 | 267.12 | 312.2479 | 446.2 | 441.5 | 387.3 | 368.9 | 665.6 | 58.8 | 18.5 | 104.6 | 5.4 | 231.4 | 4.7 | 812.2 | 847.3 | 798.4 | 823.6 | 858.4 | 759.2 | 778.2 | 803.8 | 788.7 | 816.6 | 220.2 | 312.7 | 391.8 | 360 | 432.4 | 408.1 | 382.5 | 390.8 | 536.5 | 375.3
1476 | 1302 | 668.6 | 267.44 | 312.622 | 446.1 | 442.3 | 387.3 | 368.3 | 674.9 | 58.7 | 18.5 | 104.7 | 5.6 | 243.8 | 5.3 | 812 | 844.6 | 796.8 | 822.9 | 859.8 | 758.7 | 782.4 | 804.9 | 788.5 | 817.4 | 220.5 | 312.8 | 392 | 360.2 | 432.1 | 407.9 | 382.6 | 390.9 | 536.5 | 375.5
1477 | 1303 | 667.9 | 267.16 | 312.2946 | 445.3 | 442.5 | 387.4 | 367.7 | 674.8 | 58.7 | 18.5 | 104.9 | 5.4 | 257.6 | 5.2 | 812.2 | 838.9 | 795.6 | 822.9 | 860.2 | 758.8 | 787.6 | 808.4 | 788.9 | 817 | 220.7 | 312.9 | 392.1 | 360.4 | 431.9 | 408.2 | 382.8 | 391.1 | 536.6 | 375.7
1478 | 1304 | 668.4 | 267.36 | 312.5284 | 445.1 | 443.7 | 387.7 | 367.7 | 659.5 | 58.6 | 18.5 | 105 | 5.9 | 261.5 | 4.7 | 812.7 | 839.4 | 798.9 | 824.3 | 859 | 759.2 | 790.2 | 811.5 | 789.4 | 815.8 | 220.9 | 313.1 | 392.3 | 360.7 | 432.1 | 408.9 | 383 | 391.3 | 537 | 375.9
1479 | 1305 | 667.5 | 267 | 312.1076 | 444.4 | 444.4 | 387.1 | 368.6 | 652.9 | 58.6 | 18.5 | 105.1 | 5.9 | 250.2 | 4.2 | 812.5 | 839 | 799.5 | 823.1 | 859.1 | 759.2 | 793.6 | 813.2 | 789.2 | 816.9 | 221.1 | 313.2 | 392.4 | 360.9 | 432.2 | 409.5 | 383.2 | 391.5 | 537.6 | 376.1
1480 | 1306 | 668.1 | 267.24 | 312.3882 | 443.7 | 445.2 | 388.2 | 369.2 | 655.9 | 58.7 | 18.5 | 105.2 | 5.8 | 218.6 | 4.3 | 812.3 | 843.6 | 800.2 | 822.9 | 859 | 759.5 | 798.6 | 814.1 | 788.6 | 818.1 | 221.4 | 313.4 | 392.6 | 361.1 | 432.6 | 410 | 383.5 | 391.8 | 537.9 | 376.3
1481 | 1307 | 668.4 | 267.36 | 312.5284 | 442.5 | 444.8 | 389.5 | 369.7 | 660.1 | 58.7 | 18.5 | 105.2 | 5.7 | 233.5 | 4.7 | 812.3 | 842.3 | 800.1 | 822.5 | 860.2 | 759.1 | 797.1 | 811.2 | 788.1 | 819.1 | 221.6 | 313.5 | 392.6 | 361.3 | 432.8 | 410.2 | 383.6 | 392 | 538.1 | 376.5
1482 | 1308 | 668.5 | 267.4 | 312.5752 | 441.8 | 443.8 | 389.7 | 369.8 | 653.7 | 58.7 | 18.5 | 105.2 | 6.2 | 237.8 | 4.6 | 812.2 | 839.1 | 800.1 | 822.1 | 861.6 | 758.6 | 798.5 | 809 | 787.6 | 818.6 | 221.8 | 313.6 | 392.6 | 361.5 | 433.1 | 410.8 | 383.8 | 392.2 | 538.1 | 376.7
1483 | 1309 | 668.2 | 267.28 | 312.4349 | 441.4 | 444 | 389.4 | 369.7 | 638.9 | 58.8 | 18.5 | 105.2 | 6.1 | 221.3 | 4.1 | 812.3 | 842.1 | 801.7 | 822.6 | 862.9 | 758.4 | 799.8 | 813.1 | 787.6 | 816.6 | 222 | 313.8 | 392.7 | 361.7 | 433.7 | 411.9 | 384 | 392.4 | 538.2 | 376.9
1484 | 1310 | 668.6 | 267.44 | 312.622 | 440.8 | 444.5 | 389.1 | 369.7 | 639.5 | 58.9 | 18.5 | 105.2 | 6.1 | 205.3 | 3.6 | 812.5 | 843.1 | 802 | 822.8 | 865.7 | 758 | 800.1 | 815.9 | 787.7 | 817.2 | 222.1 | 313.9 | 392.8 | 362 | 434.1 | 412.2 | 384.3 | 392.7 | 538.4 | 377.1
1485 | 1311 | 668.5 | 267.4 | 312.5752 | 441.5 | 444.6 | 388.3 | 369.8 | 649.4 | 59 | 18.5 | 105.1 | 5.9 | 192.9 | 3.2 | 812.6 | 848.5 | 802.3 | 823.2 | 867.6 | 757.4 | 802 | 813.3 | 786.9 | 817.8 | 222.3 | 314 | 392.9 | 362.2 | 434.3 | 412.1 | 384.4 | 392.8 | 538.5 | 377.3
1486 | 1312 | 667.8 | 267.12 | 312.2479 | 441.6 | 444.3 | 388.5 | 370.2 | 658.5 | 59.1 | 18.5 | 105.2 | 6.7 | 188.6 | 3.4 | 812.8 | 847 | 802.4 | 823.5 | 869.8 | 757.1 | 802.4 | 810.2 | 786.6 | 818.1 | 222.5 | 314.2 | 393 | 362.4 | 434.3 | 412 | 384.5 | 392.9 | 538.5 | 377.5
1487 | 1313 | 669 | 267.6 | 312.809 | 442 | 443.8 | 388.2 | 370 | 655.5 | 59.1 | 18.5 | 105.2 | 6.3 | 198.4 | 3.7 | 812.8 | 847.9 | 801.8 | 823.9 | 870.8 | 756.9 | 806.1 | 808.6 | 786.1 | 818.5 | 222.7 | 314.3 | 393.1 | 362.7 | 434.1 | 412.1 | 384.7 | 393 | 538.5 | 377.7
1488 | 1314 | 668.9 | 267.56 | 312.7622 | 443.3 | 443.6 | 387.3 | 369 | 640.4 | 59.3 | 18.5 | 105.4 | 6.3 | 208.9 | 3.8 | 813 | 842.7 | 802.9 | 823.7 | 871.8 | 756.7 | 808.8 | 807 | 786.2 | 818.6 | 222.8 | 314.4 | 393.1 | 362.9 | 434.3 | 412.2 | 384.9 | 393.1 | 538.7 | 377.9
1489 | 1315 | 668.2 | 267.28 | 312.4349 | 444.1 | 444 | 387.4 | 368.8 | 642.8 | 59.4 | 18.5 | 105.7 | 6.2 | 210.5 | 3.8 | 813.3 | 844.7 | 804.8 | 823.6 | 873.9 | 756.7 | 807.2 | 806.8 | 786.4 | 819.4 | 223 | 314.5 | 393.3 | 363.1 | 434.6 | 412.5 | 385.1 | 393.3 | 538.9 | 378.1
1490 | 1316 | 667.7 | 267.08 | 312.2011 | 444.7 | 443.9 | 387.6 | 369.3 | 651.9 | 59.4 | 18.5 | 105.8 | 6.1 | 219.8 | 3.5 | 813.3 | 847 | 805.3 | 823.6 | 873.4 | 756.3 | 801 | 807.7 | 786 | 818.2 | 223.2 | 314.6 | 393.3 | 363.4 | 434.9 | 412.3 | 385.3 | 393.5 | 539.1 | 378.3
1491 | 1317 | 668.4 | 267.36 | 312.5284 | 444.4 | 443.7 | 387.6 | 368.9 | 669.9 | 59.5 | 18.5 | 106 | 5.7 | 206.2 | 3.6 | 813.3 | 848.3 | 804 | 823.4 | 870.6 | 755.9 | 788.2 | 808.6 | 786.2 | 815.2 | 223.4 | 314.8 | 393.7 | 363.6 | 435 | 412.1 | 385.5 | 393.5 | 539.1 | 378.5
1492 | 1318 | 668.6 | 267.44 | 312.622 | 445.4 | 443.8 | 387.4 | 368.6 | 683.8 | 59.6 | 18.5 | 106.1 | 5.9 | 187.5 | 4 | 813.3 | 847.8 | 803.3 | 823.2 | 870 | 755.5 | 778.2 | 806.3 | 786.4 | 812.7 | 223.6 | 314.9 | 394.2 | 363.9 | 435.3 | 412.1 | 385.6 | 393.5 | 539.1 | 378.6
1493 | 1319 | 668.5 | 267.4 | 312.5752 | 445.6 | 443.7 | 387.9 | 368.5 | 685.7 | 59.7 | 18.5 | 106.3 | 6.3 | 202.5 | 4.6 | 813.1 | 849.8 | 803 | 823.2 | 870.1 | 754.9 | 776.2 | 801.3 | 786.6 | 813.3 | 223.8 | 315 | 394.1 | 364.1 | 435.1 | 412 | 385.7 | 393.6 | 539 | 378.8
1494 | 1320 | 668.4 | 267.36 | 312.5284 | 446.2 | 443.1 | 387.7 | 368 | 693.8 | 59.7 | 18.5 | 106.3 | 6.4 | 205.7 | 4.7 | 813.5 | 846.4 | 803.8 | 823.7 | 869.1 | 754.8 | 770.3 | 795.1 | 787.2 | 812.9 | 224 | 315.1 | 394.2 | 364.3 | 434.7 | 411.9 | 385.8 | 393.7 | 538.9 | 379
1495 | 1321 | 668.7 | 267.48 | 312.6687 | 446.6 | 442.4 | 387.6 | 367.4 | 695.7 | 59.7 | 18.5 | 106.3 | 6.7 | 197.2 | 4.4 | 814 | 845 | 805.1 | 823.6 | 868.3 | 754.4 | 773.9 | 794.9 | 787.7 | 813.1 | 224.2 | 315.2 | 394.5 | 364.5 | 434.5 | 412.1 | 385.9 | 393.8 | 538.9 | 379.2
1496 | 1322 | 668.6 | 267.44 | 312.622 | 446.2 | 442.2 | 388.3 | 367.3 | 697.6 | 59.7 | 18.5 | 106.5 | 6.7 | 213 | 4.3 | 814.1 | 850.3 | 804.6 | 823.8 | 867.6 | 754.7 | 774.4 | 795.3 | 788.5 | 813.9 | 224.4 | 315.3 | 394.6 | 364.8 | 434.5 | 412.3 | 386.1 | 393.9 | 539 | 379.4
1497 | 1323 | 669 | 267.6 | 312.809 | 445.2 | 442 | 388.4 | 368.5 | 688.3 | 59.8 | 18.5 | 106.6 | 6.4 | 221.9 | 4.3 | 814.2 | 849.7 | 804.5 | 824 | 868.4 | 754.3 | 778.3 | 796.8 | 788.4 | 814.9 | 224.7 | 315.4 | 394.6 | 365 | 434.3 | 412.5 | 386.2 | 394 | 539.1 | 379.5
1498 | 1324 | 669.3 | 267.72 | 312.9493 | 443 | 441.2 | 388.8 | 369.2 | 691.6 | 59.8 | 18.5 | 106.7 | 6 | 207.1 | 4.1 | 814.4 | 850.3 | 806 | 824.6 | 869.5 | 754.2 | 783 | 797.5 | 788.6 | 815 | 224.9 | 315.5 | 394.7 | 365.2 | 434.1 | 412.8 | 386.4 | 394.1 | 539 | 379.7
1499 | 1325 | 668.9 | 267.56 | 312.7622 | 441.9 | 441.3 | 388.4 | 369.1 | 685.1 | 59.8 | 18.5 | 106.8 | 5.7 | 201.8 | 3.8 | 814.8 | 844.7 | 805.2 | 824 | 870 | 753.9 | 788.1 | 793.5 | 788.4 | 815.2 | 225.1 | 315.6 | 394.7 | 365.4 | 433.9 | 412.5 | 386.5 | 394.3 | 539.1 | 379.9
1500 | 1326 | 669 | 267.6 | 312.809 | 441.7 | 441.9 | 387.6 | 368.5 | 687.9 | 59.9 | 18.5 | 106.9 | 5.3 | 206.6 | 3.6 | 815 | 843.8 | 805.8 | 823.5 | 869.2 | 753.8 | 789 | 794.3 | 788.1 | 815.6 | 225.3 | 315.7 | 394.9 | 365.6 | 433.8 | 412.4 | 386.7 | 394.4 | 539.3 | 380.1
1501 | 1327 | 669.5 | 267.8 | 313.0428 | 444.4 | 442.6 | 386.6 | 368.8 | 704.8 | 59.9 | 18.5 | 106.8 | 5.9 | 209.3 | 3.3 | 815.1 | 846.3 | 804.8 | 823.5 | 865.7 | 754.1 | 772.2 | 791.7 | 788.6 | 813.9 | 225.5 | 315.8 | 395.7 | 365.8 | 434.3 | 412.6 | 386.9 | 394.6 | 539.4 | 380.3
1502 | 1328 | 669.1 | 267.64 | 312.8557 | 446.8 | 442.8 | 387.2 | 368.8 | 718.4 | 59.9 | 18.5 | 106.7 | 5.8 | 209.5 | 3 | 815.1 | 849.2 | 800.8 | 823.5 | 862.5 | 754.3 | 760.1 | 786.1 | 788.7 | 812.8 | 225.8 | 315.9 | 395.6 | 366.1 | 435 | 412.6 | 387.2 | 394.6 | 539.6 | 380.5
1503 | 1329 | 670.3 | 268.12 | 313.4168 | 447.2 | 443.2 | 387.6 | 368.6 | 714.7 | 59.9 | 18.5 | 106.7 | 5.7 | 210.5 | 2.9 | 815.5 | 842.1 | 802.1 | 823.3 | 861.7 | 754.1 | 772.4 | 789.2 | 788.6 | 813.5 | 226 | 316 | 395.6 | 366.3 | 435.3 | 413 | 387.5 | 394.8 | 539.5 | 380.7
1504 | 1330 | 670.7 | 268.28 | 313.6039 | 447.5 | 443.2 | 388.4 | 369 | 709 | 59.8 | 18.5 | 106.7 | 5.6 | 210.5 | 2.8 | 815.7 | 836.6 | 803.6 | 822.9 | 859.9 | 754.4 | 776.3 | 791.8 | 789.2 | 813.4 | 226.2 | 316.1 | 395.8 | 366.6 | 435.5 | 413.6 | 387.7 | 395 | 539.7 | 380.9
1505 | 1331 | 669.3 | 267.72 | 312.9493 | 447.1 | 443.2 | 389 | 369.3 | 721.2 | 59.8 | 18.5 | 106.8 | 6.1 | 212.1 | 2.7 | 815.7 | 835 | 803.7 | 822.3 | 858.5 | 754.7 | 774.9 | 793.7 | 789.3 | 813.3 | 226.5 | 316.2 | 396.1 | 366.8 | 435.6 | 413.4 | 387.9 | 395.1 | 539.9 | 381.1
1506 | 1332 | 668.8 | 267.52 | 312.7155 | 446.2 | 444 | 389.9 | 370 | 719.4 | 59.8 | 18.5 | 106.9 | 6.2 | 208.9 | 2.7 | 815.6 | 835.4 | 804 | 822 | 859.9 | 754.7 | 782.9 | 794.6 | 789.2 | 814.1 | 226.7 | 316.3 | 396.1 | 367.1 | 435.8 | 413.8 | 388.1 | 395.3 | 540 | 381.3
1507 | 1333 | 668.8 | 267.52 | 312.7155 | 445.5 | 445 | 390.1 | 370.7 | 722.4 | 59.8 | 18.5 | 106.8 | 5.8 | 204.3 | 2.9 | 815.3 | 838.1 | 802.2 | 822 | 858.7 | 754.7 | 780.4 | 792.9 | 789.3 | 814.8 | 226.9 | 316.4 | 396.4 | 367.4 | 436 | 413.7 | 388.3 | 395.4 | 540.2 | 381.5
1508 | 1334 | 668.4 | 267.36 | 312.5284 | 445.4 | 444.3 | 389.6 | 371.2 | 706.8 | 59.9 | 18.5 | 106.8 | 6.4 | 211 | 2.9 | 814.9 | 840.2 | 801 | 822.7 | 856.9 | 754.6 | 782.6 | 792 | 789.4 | 816.2 | 227.1 | 316.4 | 396.3 | 367.7 | 436 | 413.6 | 388.5 | 395.5 | 540.3 | 381.7
1509 | 1335 | 669 | 267.6 | 312.809 | 445.6 | 443.5 | 389.8 | 371.7 | 685.8 | 59.9 | 18.5 | 106.8 | 5.7 | 231.4 | 2.7 | 814.7 | 838.1 | 801.2 | 822.8 | 857.4 | 754.1 | 792.4 | 789 | 789.5 | 816.5 | 227.4 | 316.5 | 396.4 | 368 | 436.2 | 413.9 | 388.7 | 395.6 | 540.2 | 381.9
1510 | 1336 | 668.7 | 267.48 | 312.6687 | 445.7 | 443.3 | 388.8 | 371.7 | 697.1 | 59.9 | 18.5 | 107 | 5.6 | 240.2 | 2.5 | 815 | 835.5 | 802.9 | 822.7 | 858.5 | 754.1 | 791.8 | 789.2 | 789.8 | 816.6 | 227.6 | 316.6 | 396.8 | 368.3 | 436.3 | 414.1 | 388.9 | 395.7 | 540.1 | 382
1511 | 1337 | 669.9 | 267.96 | 313.2298 | 446.4 | 443.4 | 387.6 | 371.3 | 717.1 | 59.9 | 18.5 | 106.9 | 6 | 240.4 | 2.2 | 815.2 | 836.1 | 803.9 | 822.9 | 856.7 | 754.4 | 778.9 | 790.1 | 790.3 | 815.2 | 227.8 | 316.7 | 397.3 | 368.6 | 436.8 | 414.2 | 389.2 | 395.8 | 540.3 | 382.2
1512 | 1338 | 669.7 | 267.88 | 313.1363 | 447.5 | 444.7 | 387.2 | 370.9 | 732.5 | 59.9 | 18.5 | 106.9 | 5.4 | 236.8 | 2.1 | 815.4 | 837.6 | 803 | 822.7 | 852.3 | 754.3 | 769.2 | 787.3 | 790.8 | 814.6 | 228 | 316.7 | 397.5 | 368.9 | 436.9 | 414.2 | 389.3 | 395.9 | 540.5 | 382.4
1513 | 1339 | 670.1 | 268.04 | 313.3233 | 446.7 | 445.2 | 388.3 | 370.7 | 743.1 | 59.9 | 18.5 | 107.1 | 5.3 | 236.4 | 2.2 | 815.4 | 842 | 800.2 | 822.8 | 848 | 754.2 | 761.3 | 783.7 | 791.3 | 813.4 | 228.2 | 316.8 | 397.8 | 369.2 | 437.3 | 414.3 | 389.6 | 396 | 540.7 | 382.6
1514 | 1340 | 668.5 | 267.4 | 312.5752 | 446.3 | 445.8 | 389.2 | 371 | 750.5 | 59.9 | 18.4 | 107.2 | 5.6 | 237.1 | 2.2 | 815.4 | 841.4 | 798.6 | 824 | 846.9 | 753.9 | 759.3 | 782.9 | 791.5 | 813.6 | 228.4 | 316.9 | 398.1 | 369.5 | 437.6 | 414.5 | 389.9 | 396.2 | 540.8 | 382.8
1515 | 1341 | 668.3 | 267.32 | 312.4817 | 446.4 | 446.1 | 388.8 | 371 | 744.7 | 60 | 18.5 | 107.2 | 5.9 | 236.7 | 2.2 | 815.5 | 839.9 | 799.3 | 824.2 | 847.5 | 753.6 | 766.5 | 785 | 791.4 | 814.3 | 228.7 | 317 | 398 | 369.8 | 437.7 | 414.6 | 390.2 | 396.3 | 540.8 | 383
1516 | 1342 | 668.6 | 267.44 | 312.622 | 446.1 | 447.8 | 388 | 370.6 | 751.2 | 60 | 18.4 | 107.2 | 6.2 | 236.7 | 2.1 | 815.8 | 845.3 | 799.6 | 824 | 846.8 | 753.7 | 760.4 | 782.7 | 792.1 | 813.6 | 228.9 | 317.1 | 398.6 | 370.2 | 438 | 414.1 | 390.5 | 396.3 | 540.8 | 383.2
1517 | 1343 | 668.7 | 267.48 | 312.6687 | 446.5 | 448.3 | 387.4 | 371.1 | 755.3 | 60.1 | 18.4 | 107.1 | 6.4 | 236.7 | 1.9 | 816.1 | 846.7 | 799 | 824.3 | 845.9 | 753.7 | 754.7 | 780.8 | 792.2 | 813.4 | 229.1 | 317.2 | 398.6 | 370.5 | 438.4 | 413.6 | 390.7 | 396.4 | 541 | 383.4
1518 | 1344 | 668.2 | 267.28 | 312.4349 | 447.7 | 448.9 | 387.5 | 371.2 | 757.9 | 60.1 | 18.4 | 107 | 6.5 | 233.3 | 1.8 | 816.6 | 848.3 | 799.4 | 824.9 | 844.5 | 754 | 757 | 781.5 | 792.8 | 813.8 | 229.2 | 317.2 | 398.7 | 370.9 | 438.7 | 413.1 | 390.9 | 396.4 | 541 | 383.6
1519 | 1345 | 668.2 | 267.28 | 312.4349 | 448.3 | 448.8 | 387.7 | 371.6 | 746.5 | 60.1 | 18.4 | 106.9 | 5.9 | 225.5 | 1.8 | 816.6 | 854.6 | 795.6 | 825 | 841.3 | 753.9 | 752.8 | 778.1 | 793.2 | 813.5 | 229.4 | 317.3 | 398.8 | 371.2 | 438.9 | 413.1 | 391.2 | 396.5 | 541.1 | 383.8
1520 | 1346 | 667.5 | 267 | 312.1076 | 450.4 | 447.8 | 387.8 | 372.5 | 733.9 | 60.1 | 18.4 | 106.8 | 6.6 | 221.8 | 1.8 | 816.3 | 849.8 | 794.4 | 825.5 | 837.2 | 753.8 | 743.3 | 772.2 | 793.2 | 813.2 | 229.6 | 317.4 | 399.1 | 371.6 | 439.4 | 412.9 | 391.5 | 396.6 | 541.1 | 384
1521 | 1347 | 668.1 | 267.24 | 312.3882 | 451.5 | 446.8 | 387.4 | 372.7 | 726.5 | 60.1 | 18.4 | 106.8 | 6.7 | 225.2 | 1.8 | 816.3 | 843.2 | 796.5 | 824.6 | 838.5 | 753.3 | 749.7 | 773.8 | 793.2 | 814.7 | 229.7 | 317.5 | 399.2 | 372 | 439.4 | 412.7 | 391.8 | 396.7 | 540.9 | 384.2
1522 | 1348 | 667.8 | 267.12 | 312.2479 | 452.2 | 446.8 | 387.2 | 372.4 | 725.3 | 60.1 | 18.4 | 106.8 | 6 | 233.7 | 1.9 | 816.1 | 841.4 | 795.7 | 824.1 | 838.1 | 752.9 | 758.7 | 775.4 | 793.1 | 815.5 | 229.9 | 317.6 | 399.5 | 372.4 | 439.6 | 412.6 | 392.1 | 396.7 | 541 | 384.4
1523 | 1349 | 670.4 | 268.16 | 313.4636 | 456.7 | 446.9 | 387.3 | 372.8 | 726 | 60.2 | 18.4 | 106.8 | 6 | 243.7 | 2.1 | 815.8 | 839.9 | 794.4 | 823.9 | 838.4 | 752.7 | 767 | 779.8 | 792.5 | 817.2 | 230 | 317.7 | 399.5 | 372.8 | 439.8 | 412.3 | 392.3 | 396.8 | 541.1 | 384.6
1524 | 1350 | 669.5 | 267.8 | 313.0428 | 458 | 447 | 387.6 | 372.5 | 722 | 60.2 | 18.4 | 106.7 | 6 | 244.9 | 2.2 | 815.7 | 839.6 | 795.4 | 823.9 | 839.6 | 752.3 | 765.7 | 782.9 | 792.1 | 818.6 | 230.1 | 317.8 | 399.9 | 373.2 | 440 | 411.9 | 392.5 | 396.9 | 541.1 | 384.8
1525 | 1351 | 670.1 | 268.04 | 313.3233 | 458.2 | 447.4 | 387.9 | 372.6 | 733 | 60.2 | 18.4 | 106.7 | 6 | 244.4 | 2.4 | 816.1 | 838.3 | 795.6 | 823.8 | 839.2 | 752.1 | 763.3 | 784.3 | 792.2 | 818.3 | 230.3 | 317.9 | 400.7 | 373.6 | 440.3 | 411.8 | 392.8 | 396.9 | 541.2 | 385
1526 | 1352 | 669.2 | 267.68 | 312.9025 | 458.7 | 448.1 | 388.6 | 373.2 | 735.4 | 60.2 | 18.4 | 106.7 | 6.2 | 243.6 | 2.4 | 816.2 | 837.5 | 796.8 | 824.4 | 842.8 | 752.3 | 771.8 | 786.4 | 792.1 | 819.4 | 230.4 | 318 | 400.5 | 374 | 440.4 | 412.2 | 393.1 | 397.1 | 541.4 | 385.2
1527 | 1353 | 669.4 | 267.76 | 312.996 | 457.5 | 448.7 | 388.9 | 373 | 740.2 | 60.2 | 18.4 | 106.7 | 6 | 242 | 2.7 | 816 | 840.5 | 797.8 | 825.4 | 844 | 752.5 | 771.1 | 787.3 | 792.3 | 819.4 | 230.6 | 318.1 | 400.7 | 374.4 | 440.5 | 412.7 | 393.3 | 397.3 | 541.7 | 385.4
1528 | 1354 | 669.8 | 267.92 | 313.183 | 456.6 | 449 | 389.9 | 373.6 | 749.4 | 60.2 | 18.4 | 106.7 | 6.1 | 240.3 | 2.8 | 815.9 | 842 | 799.2 | 825.3 | 846.4 | 752.2 | 773.9 | 786.1 | 792.5 | 819.2 | 230.7 | 318.2 | 400.9 | 374.7 | 440.5 | 412.8 | 393.6 | 397.4 | 541.7 | 385.6
1529 | 1355 | 670 | 268 | 313.2766 | 456.5 | 448.7 | 390.2 | 374.1 | 741.9 | 60.3 | 18.4 | 106.8 | 5.9 | 241.6 | 2.8 | 816.1 | 844 | 800.8 | 825.3 | 846.9 | 751.8 | 772.1 | 786.2 | 792.6 | 819.5 | 230.9 | 318.3 | 400.9 | 375.1 | 440.5 | 413.1 | 393.7 | 397.5 | 541.8 | 385.8
1530 | 1356 | 669.8 | 267.92 | 313.183 | 457.9 | 448.4 | 390.2 | 374 | 741.7 | 60.3 | 18.4 | 106.9 | 5.7 | 245 | 2.7 | 816.1 | 842.7 | 801 | 825.7 | 849.1 | 751.5 | 769.9 | 785.2 | 792.3 | 819.9 | 231 | 318.4 | 401.1 | 375.5 | 440.6 | 412.9 | 393.9 | 397.6 | 541.8 | 386
1531 | 1357 | 669.9 | 267.96 | 313.2298 | 458.7 | 448.8 | 390.4 | 373.9 | 737.2 | 60.4 | 18.4 | 106.9 | 6.2 | 244.6 | 2.6 | 816.2 | 842.2 | 800.5 | 825.8 | 849.5 | 751.4 | 759.1 | 782.5 | 792.7 | 818.3 | 231.2 | 318.6 | 401.2 | 375.9 | 440.5 | 412.5 | 394 | 397.6 | 541.7 | 386.1
1532 | 1358 | 669.7 | 267.88 | 313.1363 | 458 | 448.2 | 390.5 | 372.8 | 733.1 | 60.4 | 18.4 | 106.9 | 6.2 | 244.9 | 2.5 | 816.1 | 843.7 | 798.8 | 826.6 | 847.8 | 750.7 | 745.6 | 776.8 | 793.2 | 817.6 | 231.3 | 318.7 | 401.7 | 376.3 | 440.1 | 412 | 394.1 | 397.7 | 541.7 | 386.3
1533 | 1359 | 668.7 | 267.48 | 312.6687 | 458 | 447.5 | 390.4 | 371.8 | 737.6 | 60.5 | 18.4 | 107 | 5.8 | 244.9 | 2.4 | 816.3 | 847.1 | 798.4 | 827 | 846.5 | 749.6 | 744.4 | 775.6 | 793.3 | 816.6 | 231.5 | 318.8 | 401.9 | 376.7 | 440 | 411.9 | 394.3 | 397.8 | 541.6 | 386.5
1534 | 1360 | 669.4 | 267.76 | 312.996 | 457.6 | 447.5 | 391 | 371.8 | 738.5 | 60.5 | 18.4 | 107.2 | 6.2 | 244.8 | 2.3 | 816.5 | 846.1 | 797.3 | 826.5 | 845.9 | 749 | 744.3 | 774.5 | 793.4 | 816.1 | 231.7 | 318.9 | 402.2 | 377.1 | 439.9 | 412.1 | 394.4 | 397.9 | 541.5 | 386.6
1535 | 1361 | 670.2 | 268.08 | 313.3701 | 457.7 | 448.3 | 390.9 | 371.5 | 737.6 | 60.5 | 18.4 | 107.3 | 6.6 | 242.1 | 2.4 | 816.1 | 847.5 | 790.5 | 826.6 | 843 | 749.1 | 737.3 | 765.5 | 793.8 | 815.4 | 231.8 | 319 | 402.3 | 377.4 | 439.9 | 412.1 | 394.6 | 398 | 541.4 | 386.8
1536 | 1362 | 669.7 | 267.88 | 313.1363 | 458.3 | 448.3 | 391.1 | 371.4 | 712.4 | 60.4 | 18.4 | 107.4 | 6.1 | 235.5 | 2.7 | 815.5 | 849.7 | 785.3 | 826.6 | 837.6 | 749.1 | 725.7 | 752.8 | 794.2 | 812.8 | 232 | 319.1 | 402.2 | 377.8 | 439.7 | 412.4 | 394.7 | 398.1 | 541.3 | 387
1537 | 1363 | 668.5 | 267.4 | 312.5752 | 457.8 | 448.2 | 390.8 | 371.5 | 691.8 | 60.3 | 18.4 | 107.4 | 6.5 | 229 | 3.1 | 814.9 | 846 | 785.1 | 826.7 | 840 | 748.3 | 723.1 | 756.3 | 794.4 | 812.3 | 232.2 | 319.2 | 402.2 | 378.1 | 439.4 | 412.7 | 394.8 | 398.2 | 541 | 387.2
1538 | 1364 | 667.4 | 266.96 | 312.0609 | 456.3 | 447.1 | 390 | 371 | 683.7 | 60.2 | 18.4 | 107.5 | 6.6 | 239.4 | 3.2 | 814.5 | 844.6 | 786.8 | 827 | 846.3 | 747.1 | 734.5 | 763.2 | 793.8 | 813.2 | 232.4 | 319.3 | 402.2 | 378.4 | 438.9 | 412.7 | 394.8 | 398.4 | 540.8 | 387.3
1539 | 1365 | 667.8 | 267.12 | 312.2479 | 453.7 | 445.8 | 389.3 | 370.4 | 674 | 60.1 | 18.4 | 107.5 | 5.9 | 246 | 3.3 | 814.1 | 843.7 | 790 | 826 | 851.7 | 745.9 | 747.1 | 767.3 | 793 | 813 | 232.5 | 319.4 | 402.1 | 378.8 | 438.5 | 412.9 | 394.8 | 398.5 | 540.7 | 387.5
1540 | 1366 | 669.2 | 267.68 | 312.9025 | 453 | 445 | 388.8 | 369.9 | 655.7 | 60.1 | 18.4 | 107.6 | 5.7 | 248.5 | 3.6 | 813.7 | 838 | 793.2 | 824.6 | 856.5 | 745 | 758.9 | 770.5 | 792.1 | 814 | 232.7 | 319.6 | 402.1 | 379.1 | 438.2 | 412.9 | 394.9 | 398.6 | 540.6 | 387.6
1541 | 1367 | 668.3 | 267.32 | 312.4817 | 453.5 | 446 | 388.2 | 369.5 | 644.5 | 60.2 | 18.4 | 107.7 | 5.6 | 256 | 3.9 | 813.4 | 836.5 | 795.8 | 823.8 | 858 | 744.7 | 766.4 | 773.6 | 791.6 | 813.7 | 232.9 | 319.7 | 402.2 | 379.4 | 438.2 | 413 | 395 | 398.7 | 540.6 | 387.8
1542 | 1368 | 668.7 | 267.48 | 312.6687 | 452.1 | 446.5 | 387.8 | 369.1 | 636.2 | 60.3 | 18.4 | 108 | 5.7 | 257.5 | 4.1 | 813.2 | 833 | 797.9 | 822.7 | 857.9 | 744.2 | 768.6 | 774.3 | 791.2 | 811.8 | 233.1 | 319.8 | 402.3 | 379.7 | 438 | 412.9 | 395.1 | 398.8 | 540.7 | 388
1543 | 1369 | 667.8 | 267.12 | 312.2479 | 451.5 | 446.7 | 387.9 | 368.4 | 654.8 | 60.4 | 18.4 | 108.1 | 6 | 241.7 | 4.1 | 813.1 | 829.9 | 799.3 | 822.4 | 857.5 | 744 | 769.9 | 777.5 | 790.9 | 811 | 233.3 | 319.9 | 402.6 | 379.9 | 437.7 | 412.7 | 395.2 | 398.9 | 540.8 | 388.1
1544 | 1370 | 668.5 | 267.4 | 312.5752 | 451.7 | 447.4 | 388.5 | 368.6 | 669.1 | 60.4 | 18.4 | 108.2 | 6.2 | 228.9 | 4 | 813.1 | 834.7 | 800.5 | 823.1 | 857.7 | 744 | 776.1 | 783 | 790.4 | 811.1 | 233.5 | 320 | 402.8 | 380.2 | 437.6 | 412.8 | 395.3 | 399 | 540.9 | 388.3
1545 | 1371 | 668.3 | 267.32 | 312.4817 | 450.9 | 448 | 389 | 368.6 | 668.3 | 60.5 | 18.4 | 108.3 | 6.1 | 233.3 | 3.9 | 813.3 | 839.1 | 800.6 | 823.6 | 859.7 | 743.6 | 775.2 | 785.7 | 789.9 | 811.5 | 233.6 | 320.2 | 402.7 | 380.5 | 437.1 | 412.9 | 395.4 | 399.1 | 541.1 | 388.4
1546 | 1372 | 668 | 267.2 | 312.3414 | 451.7 | 447.1 | 388.9 | 369.2 | 672.4 | 60.6 | 18.4 | 108.3 | 6.1 | 236.1 | 3.7 | 813.3 | 839.1 | 799.8 | 824.1 | 859.4 | 743.2 | 779.5 | 788.3 | 789.5 | 812.1 | 233.8 | 320.3 | 402.7 | 380.8 | 437 | 413.2 | 395.6 | 399.3 | 541.1 | 388.6
1547 | 1373 | 668.3 | 267.32 | 312.4817 | 452.4 | 446.4 | 388.6 | 369.4 | 678 | 60.6 | 18.4 | 108.5 | 5.7 | 236 | 3.4 | 813.2 | 839.6 | 800.8 | 824.2 | 855.9 | 742.8 | 779.5 | 788 | 789 | 812.2 | 234 | 320.4 | 403.1 | 381.1 | 437.1 | 413.8 | 395.8 | 399.4 | 541.1 | 388.8
1548 | 1374 | 668.6 | 267.44 | 312.622 | 452 | 446.5 | 388.1 | 369.3 | 697.7 | 60.7 | 18.4 | 108.7 | 6.3 | 235.7 | 3.3 | 812.9 | 839.7 | 798.5 | 823.3 | 853.2 | 742.5 | 766 | 785 | 788.9 | 810.2 | 234.2 | 320.5 | 403.6 | 381.4 | 437.2 | 414 | 395.9 | 399.5 | 541.1 | 388.9
1549 | 1375 | 669.3 | 267.72 | 312.9493 | 452.8 | 446.7 | 388.6 | 370.1 | 712.9 | 60.7 | 18.4 | 108.8 | 6.5 | 234.4 | 3.2 | 812.8 | 835.3 | 797.7 | 822.8 | 851.8 | 742.4 | 764.7 | 784.1 | 788.8 | 810.8 | 234.4 | 320.6 | 403.7 | 381.7 | 437.4 | 414.3 | 396.1 | 399.5 | 541.1 | 389.1
1550 | 1376 | 668.6 | 267.44 | 312.622 | 453.4 | 446.9 | 389.1 | 369.7 | 704.6 | 60.8 | 18.4 | 108.9 | 6.2 | 235.3 | 3.1 | 813 | 829.8 | 797.6 | 823.1 | 853.9 | 742.5 | 771.2 | 787.9 | 789.1 | 809 | 234.5 | 320.7 | 403.6 | 382 | 437.7 | 414.7 | 396.3 | 399.7 | 541.1 | 389.3
1551 | 1377 | 669.3 | 267.72 | 312.9493 | 452.3 | 448.1 | 389.5 | 370.2 | 705.2 | 60.8 | 18.4 | 109 | 6.1 | 236.7 | 2.9 | 812.8 | 833.4 | 797 | 821.6 | 850.9 | 743.3 | 769.7 | 787.9 | 789.2 | 810.1 | 234.7 | 320.8 | 404.1 | 382.3 | 438 | 415 | 396.6 | 399.9 | 541.5 | 389.4
1552 | 1378 | 668.3 | 267.32 | 312.4817 | 452.3 | 448.2 | 389.9 | 371.2 | 723.8 | 60.8 | 18.4 | 109 | 5.6 | 238.7 | 3 | 812.4 | 835.5 | 793.3 | 821.9 | 842.6 | 743.9 | 747.2 | 777.8 | 789.6 | 808 | 234.9 | 320.9 | 404.9 | 382.7 | 438.5 | 414.6 | 396.7 | 399.9 | 542.1 | 389.6
1553 | 1379 | 667.6 | 267.04 | 312.1544 | 453.4 | 448 | 392.2 | 371.7 | 724.8 | 60.8 | 18.4 | 109 | 5.9 | 240.2 | 3.1 | 812.1 | 836.4 | 790.5 | 822.7 | 840.3 | 743.5 | 734.7 | 771 | 790.4 | 806.3 | 235.1 | 320.9 | 404.9 | 383 | 438.7 | 414.2 | 396.9 | 399.9 | 542.2 | 389.8
1554 | 1380 | 668.8 | 267.52 | 312.7155 | 454.4 | 450.1 | 393.6 | 371.8 | 725.7 | 60.9 | 18.4 | 109.1 | 6 | 240.4 | 3.3 | 811.8 | 833.6 | 790.7 | 821.8 | 840 | 743.2 | 729.6 | 767.7 | 790.9 | 805.1 | 235.3 | 321 | 405.3 | 383.4 | 438.9 | 414.4 | 397.2 | 400 | 542 | 390
1555 | 1381 | 668.1 | 267.24 | 312.3882 | 453.9 | 452 | 394.2 | 372.5 | 729.6 | 61 | 18.4 | 109.1 | 6.2 | 241.2 | 3.6 | 811.5 | 832.2 | 789.2 | 821.3 | 840.2 | 742.9 | 725.5 | 765.2 | 791.3 | 803.3 | 235.5 | 321.1 | 405.5 | 383.8 | 439.1 | 414.7 | 397.4 | 400.1 | 541.9 | 390.2
1556 | 1382 | 668.3 | 267.32 | 312.4817 | 452.1 | 451.7 | 393.9 | 372.9 | 730.7 | 61 | 18.4 | 109.1 | 6.8 | 242.5 | 3.7 | 811.4 | 829.6 | 792.2 | 820.7 | 844.5 | 742.4 | 743 | 772.9 | 790.6 | 805.6 | 235.6 | 321.2 | 405.3 | 384.2 | 439.2 | 414.9 | 397.6 | 400.2 | 541.8 | 390.4
1557 | 1383 | 668 | 267.2 | 312.3414 | 451.8 | 451.1 | 393.6 | 372.7 | 717.4 | 61.1 | 18.4 | 109 | 6.7 | 242.8 | 3.7 | 811.2 | 826.3 | 793.7 | 819.8 | 847.9 | 741.9 | 752 | 776.3 | 789.9 | 806.4 | 235.8 | 321.2 | 405.2 | 384.5 | 439.1 | 414.8 | 397.7 | 400.4 | 541.8 | 390.5
1558 | 1384 | 668.5 | 267.4 | 312.5752 | 454.5 | 450.8 | 393.6 | 372.1 | 730 | 61.1 | 18.4 | 109.2 | 5.6 | 242.8 | 3.5 | 811.2 | 828.4 | 793.3 | 819.4 | 846.5 | 741.3 | 748.4 | 779.5 | 789.3 | 806.8 | 236 | 321.3 | 405.8 | 384.9 | 439.3 | 414.5 | 397.9 | 400.4 | 541.9 | 390.7
1559 | 1385 | 668.2 | 267.28 | 312.4349 | 455 | 450 | 393.4 | 372.5 | 745.1 | 61.2 | 18.4 | 109.2 | 5.4 | 242 | 3.6 | 811.1 | 826.6 | 793.8 | 819.4 | 844.8 | 740.8 | 747.3 | 780.1 | 788.5 | 806.8 | 236.2 | 321.3 | 406.1 | 385.3 | 439.7 | 414.1 | 398.1 | 400.4 | 542.1 | 390.8
1560 | 1386 | 668.1 | 267.24 | 312.3882 | 455.6 | 448.9 | 393 | 373 | 748.9 | 61.2 | 18.4 | 109.1 | 5.4 | 240.5 | 3.6 | 811.1 | 827.2 | 795.7 | 819.9 | 844 | 741.1 | 749.9 | 784.8 | 788.4 | 806.1 | 236.4 | 321.4 | 406.4 | 385.7 | 440.3 | 414 | 398.4 | 400.4 | 542.1 | 391
1561 | 1387 | 668.4 | 267.36 | 312.5284 | 455.1 | 449.4 | 393.6 | 373.7 | 734.7 | 61.3 | 18.4 | 109 | 5.6 | 235.7 | 3.5 | 811.3 | 824.4 | 798 | 819.7 | 843.3 | 741 | 749.1 | 785.4 | 788.3 | 805.7 | 236.6 | 321.5 | 406.5 | 386.1 | 440.8 | 414.2 | 398.8 | 400.6 | 542.3 | 391.2
1562 | 1388 | 668.7 | 267.48 | 312.6687 | 454 | 449.9 | 394.1 | 374.1 | 736.5 | 61.3 | 18.4 | 108.8 | 6.3 | 231.5 | 3.4 | 811.3 | 823.5 | 800.8 | 820.9 | 845.5 | 740.6 | 759.5 | 787.6 | 787.9 | 806.9 | 236.8 | 321.5 | 406.6 | 386.5 | 441 | 414.4 | 399 | 400.7 | 542.5 | 391.4
1563 | 1389 | 667.9 | 267.16 | 312.2946 | 452.8 | 450.3 | 394.7 | 373.9 | 729.9 | 61.3 | 18.4 | 108.5 | 5.7 | 222.4 | 3.4 | 811.4 | 821.5 | 801.4 | 820.2 | 846.2 | 740.4 | 767.7 | 785.7 | 787.4 | 807.3 | 237 | 321.6 | 406.5 | 386.9 | 440.9 | 414.7 | 399.2 | 400.8 | 542.7 | 391.6
1564 | 1390 | 668.7 | 267.48 | 312.6687 | 452 | 449.9 | 394.6 | 373.8 | 732.9 | 61.4 | 18.4 | 108.4 | 5.7 | 207.5 | 3.6 | 811.4 | 824 | 800.8 | 820.6 | 847.1 | 740.1 | 769.8 | 788.7 | 786.8 | 807 | 237.2 | 321.7 | 406.8 | 387.3 | 441.1 | 414.8 | 399.4 | 400.8 | 542.9 | 391.8
1565 | 1391 | 668.7 | 267.48 | 312.6687 | 450.9 | 449.5 | 394.5 | 373.1 | 740.8 | 61.4 | 18.4 | 108.4 | 5.8 | 195.9 | 3.9 | 811.3 | 830 | 798.8 | 821.3 | 847.8 | 739.7 | 769.6 | 790.7 | 786.2 | 808.3 | 237.4 | 321.7 | 407.2 | 387.7 | 441 | 414.7 | 399.6 | 400.9 | 543.1 | 391.9
1566 | 1392 | 668.5 | 267.4 | 312.5752 | 450.4 | 449.2 | 395.4 | 372.6 | 737.8 | 61.4 | 18.4 | 108.4 | 6.2 | 199.2 | 4.4 | 810.9 | 830.8 | 795.8 | 822.1 | 842.8 | 739.7 | 758.5 | 787.5 | 786.2 | 807.9 | 237.6 | 321.8 | 407.6 | 388.1 | 441 | 414.8 | 399.9 | 400.9 | 543.1 | 392.1
1567 | 1393 | 668.1 | 267.24 | 312.3882 | 450.6 | 448.8 | 395.6 | 372.7 | 723.9 | 61.4 | 18.4 | 108.4 | 6 | 198.4 | 4.6 | 810.7 | 831 | 795 | 822.5 | 844.3 | 739.4 | 753.2 | 783.6 | 786.5 | 807 | 237.7 | 321.9 | 407.8 | 388.5 | 441.1 | 414.5 | 400.1 | 400.9 | 543.1 | 392.3
1568 | 1394 | 668.8 | 267.52 | 312.7155 | 452 | 448.1 | 394.8 | 372.6 | 715.9 | 61.5 | 18.4 | 108.4 | 6.4 | 201.8 | 4.6 | 810.9 | 831.1 | 797.3 | 822.3 | 846.3 | 738.9 | 757.3 | 784.6 | 786.5 | 808.2 | 237.9 | 321.9 | 407.5 | 388.9 | 440.7 | 414.7 | 400.3 | 401.1 | 543 | 392.4
1569 | 1395 | 668.2 | 267.28 | 312.4349 | 451.1 | 448.1 | 394.5 | 372 | 720.3 | 61.5 | 18.4 | 108.4 | 6.5 | 201.7 | 4.3 | 811.3 | 831.3 | 798.2 | 822.2 | 846.7 | 738.4 | 759.8 | 786.1 | 786.4 | 807.6 | 238.1 | 322 | 407.9 | 389.2 | 440.4 | 414.7 | 400.4 | 401.2 | 542.9 | 392.6
1570 | 1396 | 667.8 | 267.12 | 312.2479 | 451.7 | 448.2 | 393.7 | 371 | 732.8 | 61.5 | 18.4 | 108.4 | 6 | 202.3 | 4.2 | 811.4 | 834.5 | 797.7 | 823 | 844 | 738.7 | 751.9 | 783.8 | 786.7 | 807.6 | 238.3 | 322.1 | 408.4 | 389.6 | 440.4 | 414.6 | 400.6 | 401.2 | 543.1 | 392.7
1571 | 1397 | 668.5 | 267.4 | 312.5752 | 452.6 | 447.3 | 394.4 | 370 | 717.9 | 61.5 | 18.3 | 108.5 | 5.7 | 207.3 | 4.1 | 811.4 | 839.1 | 797.9 | 823.7 | 844 | 738.5 | 746.9 | 782.8 | 787.3 | 807.9 | 238.5 | 322.2 | 408.2 | 389.9 | 440.2 | 414.4 | 400.8 | 401.2 | 543.1 | 392.9
1572 | 1398 | 667.8 | 267.12 | 312.2479 | 452.1 | 446.7 | 395 | 369.7 | 704.6 | 61.6 | 18.3 | 108.6 | 6.2 | 213.4 | 3.9 | 811.8 | 837.3 | 798.4 | 823.3 | 845 | 738.1 | 746.6 | 784.1 | 787.3 | 808.2 | 238.6 | 322.2 | 408.2 | 390.2 | 440.1 | 414.3 | 401 | 401.2 | 543 | 393
1573 | 1399 | 668.7 | 267.48 | 312.6687 | 452.1 | 446.2 | 395.1 | 370.1 | 694.4 | 61.6 | 18.3 | 108.5 | 6.8 | 216.4 | 4 | 811.8 | 834.9 | 797.4 | 823.3 | 846.2 | 737.5 | 757.2 | 785.2 | 786.9 | 809 | 238.8 | 322.3 | 408.1 | 390.6 | 439.7 | 414.1 | 401.1 | 401.3 | 542.9 | 393.2
1574 | 1400 | 669.9 | 267.96 | 313.2298 | 452.2 | 445.3 | 394.7 | 370.5 | 693.3 | 61.5 | 18.3 | 108.4 | 6.6 | 227.2 | 3.8 | 811.6 | 836.2 | 794.2 | 824.1 | 847.4 | 736.9 | 758 | 785.4 | 786.5 | 810.3 | 239 | 322.4 | 408.2 | 390.9 | 439.4 | 414.1 | 401.3 | 401.3 | 542.8 | 393.3
1575 | 1401 | 670.1 | 268.04 | 313.3233 | 454 | 444.9 | 394.4 | 370.6 | 693.8 | 61.5 | 18.3 | 108.4 | 6.4 | 230.1 | 3.2 | 811.4 | 839.9 | 789.5 | 825.4 | 846.8 | 736.7 | 752.2 | 781.1 | 786.4 | 810.2 | 239.2 | 322.4 | 408.5 | 391.2 | 439.3 | 414.1 | 401.6 | 401.4 | 542.7 | 393.5
1576 | 1402 | 669.7 | 267.88 | 313.1363 | 456.2 | 444 | 393.2 | 370.9 | 675.6 | 61.5 | 18.3 | 108.4 | 6.4 | 230.7 | 2.9 | 811.1 | 839.2 | 788.2 | 825 | 849.2 | 736.1 | 755.1 | 780.2 | 786.4 | 811.5 | 239.3 | 322.5 | 408.3 | 391.5 | 439.2 | 413.6 | 401.9 | 401.4 | 542.5 | 393.6
1577 | 1403 | 670.7 | 268.28 | 313.6039 | 455.6 | 441.8 | 393.3 | 371.8 | 666.8 | 61.5 | 18.3 | 108.3 | 6 | 231.5 | 3.6 | 810.8 | 838.5 | 788.6 | 823.9 | 851 | 735.1 | 752.2 | 777.4 | 785.9 | 811.6 | 239.5 | 322.6 | 408.5 | 391.8 | 439.5 | 413.2 | 402.1 | 401.4 | 542.3 | 393.8
1578 | 1404 | 669.2 | 267.68 | 312.9025 | 456.6 | 440.4 | 393.3 | 372 | 657.4 | 61.4 | 18.3 | 108.2 | 5.7 | 209.1 | 4.8 | 810.7 | 839.2 | 788.7 | 823.4 | 852.5 | 734 | 757 | 780.3 | 785.2 | 812.7 | 239.7 | 322.6 | 408.6 | 392 | 439.8 | 413.1 | 402.5 | 401.6 | 542.1 | 394
1579 | 1405 | 667.6 | 267.04 | 312.1544 | 456.8 | 440.7 | 393.2 | 371.6 | 671.7 | 61.3 | 18.3 | 108.2 | 6.1 | 208.6 | 5.4 | 811 | 837.3 | 791.2 | 823 | 849.9 | 733.3 | 758.3 | 781.5 | 784.7 | 812.2 | 239.8 | 322.7 | 409 | 392.3 | 440.1 | 412.9 | 402.8 | 401.6 | 542 | 394.2
1580 | 1406 | 667.7 | 267.08 | 312.2011 | 455.7 | 441.2 | 392.7 | 370.7 | 686.2 | 61.2 | 18.3 | 108.4 | 6.4 | 215.3 | 5.5 | 811.2 | 833.8 | 793.6 | 822 | 849.4 | 733.4 | 757.1 | 782.3 | 784.2 | 811.7 | 240 | 322.7 | 409.1 | 392.6 | 440 | 412.9 | 403.1 | 401.6 | 542.2 | 394.3
1581 | 1407 | 669.5 | 267.8 | 313.0428 | 454.7 | 441.6 | 392 | 369.8 | 695.4 | 61 | 18.3 | 108.6 | 7.5 | 204.7 | 5.5 | 811.4 | 828.1 | 796.4 | 821.7 | 850.1 | 733.3 | 761 | 783.5 | 783.9 | 812.3 | 240.1 | 322.8 | 409.3 | 392.9 | 440 | 413.4 | 403.4 | 401.7 | 542.5 | 394.4
1582 | 1408 | 668.4 | 267.36 | 312.5284 | 453.8 | 441.9 | 391.4 | 368.9 | 699.6 | 61 | 18.3 | 108.7 | 7 | 194.6 | 5.2 | 811.8 | 828.3 | 796.9 | 821.5 | 848.8 | 733.5 | 760.4 | 786 | 784 | 812.6 | 240.3 | 322.8 | 409.3 | 393.2 | 440.1 | 413.7 | 403.8 | 401.8 | 542.6 | 394.6
1583 | 1409 | 668.2 | 267.28 | 312.4349 | 452.5 | 442.7 | 391.5 | 369.2 | 712.1 | 61 | 18.3 | 108.9 | 6.5 | 183.8 | 4.5 | 811.7 | 833.6 | 791.8 | 822.2 | 844.8 | 733.9 | 755.9 | 785.9 | 784 | 812.4 | 240.5 | 322.9 | 409.9 | 393.5 | 440.6 | 413.9 | 404.1 | 401.9 | 542.9 | 394.7
1584 | 1410 | 669 | 267.6 | 312.809 | 452.9 | 443.8 | 392.9 | 370.1 | 723.8 | 61 | 18.3 | 109 | 6.7 | 169.5 | 4.2 | 811.7 | 834.6 | 790.5 | 823.7 | 845.3 | 733.8 | 754.4 | 787.7 | 784.1 | 813.1 | 240.7 | 323 | 410.2 | 393.7 | 441.1 | 414.1 | 404.6 | 401.9 | 543.1 | 394.9
1585 | 1411 | 668.7 | 267.48 | 312.6687 | 453.1 | 444.3 | 394.6 | 370.9 | 726.1 | 61.1 | 18.3 | 109 | 6.5 | 182.6 | 4 | 811.8 | 835.8 | 790.7 | 823.9 | 846.6 | 733.4 | 749.1 | 785.7 | 784.2 | 812.3 | 240.9 | 323.1 | 410.3 | 394 | 441.5 | 414.4 | 405.1 | 402 | 543.1 | 395.1
1586 | 1412 | 669.4 | 267.76 | 312.996 | 454.3 | 444.4 | 395.1 | 370.6 | 722.1 | 61.2 | 18.3 | 108.9 | 6.7 | 178.1 | 3.7 | 811.7 | 837.7 | 789.4 | 823.7 | 843.9 | 732.8 | 737.5 | 779.1 | 784.4 | 810.6 | 241.1 | 323.2 | 410.6 | 394.3 | 441.6 | 414.3 | 405.4 | 402 | 543 | 395.3
1587 | 1413 | 669.1 | 267.64 | 312.8557 | 456.9 | 445.1 | 394.4 | 370.8 | 720.3 | 61.3 | 18.3 | 108.8 | 6.4 | 171.2 | 3.3 | 811.9 | 838.4 | 791.2 | 824.2 | 846.7 | 732.3 | 739.4 | 780 | 784.4 | 809.9 | 241.3 | 323.2 | 410.5 | 394.7 | 441.7 | 414.2 | 405.8 | 402.1 | 542.8 | 395.4
1588 | 1414 | 668.3 | 267.32 | 312.4817 | 459.5 | 445.3 | 393.6 | 370.8 | 720.3 | 61.4 | 18.3 | 108.7 | 7 | 169.6 | 3.5 | 811.8 | 837.3 | 790.5 | 822.8 | 844.3 | 732.5 | 727.2 | 774.7 | 785 | 808.6 | 241.4 | 323.3 | 410.9 | 395 | 441.7 | 414.4 | 406.3 | 402.2 | 542.7 | 395.6
1589 | 1415 | 668.1 | 267.24 | 312.3882 | 461.1 | 446 | 394.4 | 370.9 | 719.5 | 61.5 | 18.3 | 108.7 | 7 | 203.8 | 4.7 | 811.9 | 836.6 | 790.7 | 822.5 | 844 | 732.1 | 725.1 | 773.6 | 785.3 | 807.2 | 241.6 | 323.4 | 411 | 395.3 | 441.6 | 414.7 | 407.1 | 402.4 | 542.7 | 395.8
1590 | 1416 | 667.2 | 266.88 | 311.9673 | 460.2 | 445.7 | 395.4 | 370.8 | 724.2 | 61.6 | 18.3 | 108.7 | 7.3 | 199.9 | 6.3 | 812 | 835.7 | 791.3 | 822.4 | 845.4 | 731.3 | 731.6 | 777.3 | 785.1 | 808.1 | 241.8 | 323.6 | 411.1 | 395.6 | 441.2 | 414.7 | 407.6 | 402.4 | 542.6 | 395.9
1591 | 1417 | 668.4 | 267.36 | 312.5284 | 460.7 | 445.5 | 395.6 | 370.4 | 734 | 61.6 | 18.3 | 108.6 | 6.7 | 205.3 | 5.2 | 812.4 | 834.3 | 791.7 | 822.7 | 840.4 | 731 | 730 | 777.5 | 785.1 | 807.5 | 242 | 323.7 | 411.6 | 395.9 | 441.2 | 414.9 | 408.3 | 402.5 | 542.7 | 396
1592 | 1418 | 668.6 | 267.44 | 312.622 | 460.5 | 446.4 | 395.8 | 369.3 | 741.4 | 61.6 | 18.3 | 108.7 | 6.8 | 210.4 | 5.1 | 812.9 | 832.3 | 790 | 823.2 | 836.2 | 730.7 | 721.8 | 772.7 | 785.2 | 805.2 | 242.1 | 323.8 | 412.1 | 396.2 | 441.4 | 415 | 409 | 402.5 | 542.9 | 396.2
1593 | 1419 | 669 | 267.6 | 312.809 | 460 | 446.3 | 396.6 | 369.4 | 748.2 | 61.4 | 18.3 | 108.7 | 6.8 | 212.5 | 6.1 | 812.9 | 832.2 | 788.3 | 824.3 | 836.9 | 730.5 | 718.8 | 771.9 | 785 | 804.5 | 242.3 | 323.9 | 412.1 | 396.5 | 441.4 | 415.3 | 409.6 | 402.6 | 542.9 | 396.4
1594 | 1420 | 668.5 | 267.4 | 312.5752 | 459 | 446.2 | 397.2 | 370.1 | 752.2 | 61.2 | 18.3 | 108.7 | 6.7 | 221.9 | 5.8 | 812.7 | 835.1 | 787 | 826 | 838.6 | 730.3 | 716.6 | 773.9 | 785.3 | 805.9 | 242.5 | 324.1 | 412.4 | 396.8 | 441.8 | 415.7 | 410.4 | 402.8 | 542.9 | 396.5
1595 | 1421 | 668.7 | 267.48 | 312.6687 | 459.4 | 445.6 | 396.9 | 371.6 | 746.2 | 61.1 | 18.3 | 108.7 | 7.4 | 202.4 | 6.2 | 812.6 | 835.4 | 788.8 | 825.1 | 838.2 | 730.4 | 717.7 | 774.6 | 785.2 | 806.4 | 242.6 | 324.2 | 412.5 | 397.1 | 441.9 | 416 | 410.9 | 402.9 | 542.8 | 396.7
1596 | 1422 | 668.5 | 267.4 | 312.5752 | 459 | 445.5 | 397.5 | 372.2 | 742.6 | 61.2 | 18.3 | 108.7 | 7.5 | 229.6 | 6.6 | 812.5 | 833 | 790.4 | 824.9 | 834 | 729.8 | 711.3 | 771.1 | 785.3 | 804.9 | 242.8 | 324.4 | 413 | 397.3 | 442 | 416 | 411.3 | 402.9 | 542.7 | 396.9
1597 | 1423 | 668.3 | 267.32 | 312.4817 | 457.8 | 445.3 | 398.2 | 371.9 | 751 | 61.2 | 18.3 | 108.8 | 7.9 | 210.1 | 7.1 | 812.4 | 831.2 | 791.6 | 823.4 | 836.4 | 729 | 721.7 | 774.3 | 784.6 | 804.8 | 242.9 | 324.5 | 413 | 397.6 | 442.1 | 415.9 | 411.8 | 403 | 542.7 | 397
1598 | 1424 | 668.3 | 267.32 | 312.4817 | 457.8 | 444.8 | 396.9 | 371 | 751.6 | 61.2 | 18.3 | 108.8 | 7.6 | 202.4 | 7 | 812.4 | 832.6 | 793.2 | 823.8 | 838.5 | 728.7 | 722.9 | 776.3 | 784 | 805.4 | 243.1 | 324.6 | 413.2 | 397.9 | 442 | 416.1 | 412.3 | 403.1 | 542.9 | 397.2
1599 | 1425 | 669.5 | 267.8 | 313.0428 | 458.3 | 444.9 | 395.7 | 370.6 | 752.5 | 61.3 | 18.3 | 108.8 | 7.4 | 197.8 | 5.5 | 812.3 | 831.3 | 792.8 | 824.3 | 840.8 | 728.5 | 722.5 | 777.3 | 784 | 805.6 | 243.2 | 324.7 | 413.2 | 398.1 | 441.9 | 416.1 | 412.7 | 403.2 | 543 | 397.3
1600 | 1426 | 668.7 | 267.48 | 312.6687 | 459.4 | 444.7 | 396.1 | 370.1 | 757.1 | 61.5 | 18.3 | 108.7 | 7.7 | 240.6 | 4.3 | 812.5 | 829.2 | 794.5 | 824 | 840.8 | 728 | 723.8 | 776.1 | 783.5 | 804.7 | 243.4 | 324.9 | 413.6 | 398.4 | 441.9 | 416 | 413.1 | 403.2 | 543.1 | 397.5
1601 | 1427 | 668.8 | 267.52 | 312.7155 | 460.3 | 444.7 | 397.3 | 370 | 768.1 | 61.6 | 18.3 | 108.7 | 7 | 248.9 | 4.5 | 812.4 | 827.3 | 793.6 | 823.1 | 837.5 | 728.2 | 720.8 | 773.7 | 783.2 | 804.2 | 243.5 | 325 | 414 | 398.6 | 442.1 | 415.8 | 413.7 | 403.3 | 543.2 | 397.6
1602 | 1428 | 669.3 | 267.72 | 312.9493 | 459.5 | 446.2 | 398.5 | 370.4 | 772.8 | 61.6 | 18.3 | 108.7 | 6.4 | 246.9 | 5.1 | 812.2 | 826.4 | 792.4 | 823.5 | 835.4 | 728.6 | 717.1 | 769.3 | 783.9 | 802.5 | 243.7 | 325.1 | 414.6 | 398.9 | 442.5 | 415.8 | 414.3 | 403.3 | 543.5 | 397.8
1603 | 1429 | 668.9 | 267.56 | 312.7622 | 458.4 | 447.6 | 399.9 | 370.9 | 765.6 | 61.7 | 18.3 | 108.7 | 7 | 248.9 | 4.7 | 812.1 | 825.8 | 791.2 | 824.7 | 837.7 | 728.5 | 716.6 | 768.6 | 784.6 | 802.9 | 243.8 | 325.2 | 414.6 | 399.1 | 442.6 | 416.2 | 414.9 | 403.5 | 543.6 | 398
1604 | 1430 | 668.6 | 267.44 | 312.622 | 458.2 | 447.4 | 400.3 | 371.5 | 740.8 | 61.7 | 18.3 | 108.7 | 6.2 | 242.2 | 4.3 | 812.3 | 822.1 | 794 | 825.5 | 843.7 | 727.9 | 726.4 | 772.9 | 784.4 | 804.1 | 244 | 325.4 | 414.3 | 399.4 | 442.4 | 416.3 | 415.3 | 403.6 | 543.5 | 398.2
1605 | 1431 | 667.6 | 267.04 | 312.1544 | 458.2 | 448 | 401.1 | 372 | 726.1 | 61.8 | 18.3 | 108.8 | 6.5 | 225.1 | 4.1 | 812.5 | 822.4 | 795.9 | 825.1 | 848.2 | 727.6 | 738.9 | 779.3 | 784 | 805.4 | 244.1 | 325.5 | 414.2 | 399.6 | 442.4 | 416.8 | 415.7 | 403.8 | 543.4 | 398.3
1606 | 1432 | 668.6 | 267.44 | 312.622 | 459.4 | 448.6 | 401.2 | 371.8 | 725.9 | 61.8 | 18.3 | 108.9 | 6.3 | 210.3 | 3.9 | 812.6 | 827.7 | 796.9 | 825.3 | 849.5 | 727 | 744.3 | 781.7 | 783.4 | 805.9 | 244.2 | 325.6 | 414.4 | 399.9 | 442.6 | 417.1 | 416 | 403.9 | 543.5 | 398.5
1607 | 1433 | 669 | 267.6 | 312.809 | 461 | 447.9 | 401.7 | 371.8 | 731.3 | 61.8 | 18.3 | 109 | 5.6 | 224.9 | 4.6 | 812.7 | 824.8 | 797.1 | 825.5 | 849.1 | 726.7 | 746.7 | 782.6 | 782.7 | 807.8 | 244.4 | 325.8 | 414.5 | 400.1 | 442.8 | 417 | 416.3 | 403.8 | 543.5 | 398.6
1608 | 1434 | 668.6 | 267.44 | 312.622 | 461.5 | 446.8 | 401.9 | 371.6 | 725.2 | 61.8 | 18.3 | 109.1 | 6.5 | 206.4 | 6.2 | 812.5 | 822.3 | 797.3 | 825.1 | 851.5 | 727 | 746.9 | 784.4 | 782.4 | 808.6 | 244.5 | 325.9 | 414.5 | 400.3 | 442.6 | 417.4 | 416.6 | 403.9 | 543.4 | 398.8
1609 | 1435 | 668.9 | 267.56 | 312.7622 | 462.2 | 448 | 401.5 | 370.7 | 724.1 | 61.9 | 18.3 | 109.4 | 6.3 | 220.4 | 7.8 | 812.2 | 821.2 | 796.1 | 824 | 850 | 726.9 | 753.7 | 784.9 | 782.3 | 810.1 | 244.7 | 326 | 414.5 | 400.5 | 442.2 | 417.7 | 416.9 | 404 | 543.3 | 398.9
1610 | 1436 | 668.7 | 267.48 | 312.6687 | 460.8 | 447.2 | 400.2 | 370 | 712.6 | 61.9 | 18.2 | 109.6 | 6.8 | 210.4 | 7.9 | 811.7 | 822.1 | 794.1 | 824.8 | 851.9 | 726.8 | 752.5 | 787.9 | 782 | 811.8 | 244.9 | 326.1 | 414.4 | 400.7 | 442 | 418 | 417.2 | 404.2 | 543.3 | 399
1611 | 1437 | 668.9 | 267.56 | 312.7622 | 458.5 | 446 | 398.9 | 370 | 702.2 | 62 | 18.3 | 109.7 | 7.1 | 252.3 | 6.6 | 811.4 | 827.3 | 794.5 | 825.6 | 856.4 | 726.4 | 756.3 | 788.9 | 781.7 | 812.3 | 245.1 | 326.3 | 414.3 | 400.9 | 441.9 | 418.1 | 417.4 | 404.3 | 543.3 | 399.2
1612 | 1438 | 668.4 | 267.36 | 312.5284 | 456.4 | 445.3 | 397.4 | 370.3 | 683.1 | 62.1 | 18.3 | 109.7 | 6.8 | 229.8 | 6.3 | 811.2 | 829.3 | 795.3 | 825.2 | 860.7 | 726 | 762 | 788.9 | 781.2 | 811.2 | 245.3 | 326.4 | 414.3 | 401 | 441.7 | 417.8 | 417.6 | 404.4 | 543.2 | 399.3
1613 | 1439 | 668.8 | 267.52 | 312.7155 | 456.5 | 444.9 | 395.7 | 370.2 | 677.7 | 62.2 | 18.3 | 109.9 | 6.4 | 221.1 | 6 | 811.5 | 830.3 | 797.2 | 824.7 | 863.1 | 725.5 | 757.8 | 789.7 | 781.5 | 811.4 | 245.5 | 326.6 | 414.5 | 401.2 | 441.5 | 417.3 | 417.7 | 404.4 | 543.2 | 399.4
1614 | 1440 | 587.1 | 234.84 | 274.5144 | 457.3 | 445.9 | 395.3 | 370.5 | 691.7 | 62.3 | 18.2 | 110.1 | 6.1 | 228.5 | 5.8 | 811.5 | 835.9 | 795.2 | 825.7 | 864.3 | 725.2 | 751.1 | 786.9 | 781.6 | 810.6 | 245.6 | 326.7 | 414.8 | 401.4 | 441.5 | 416.8 | 418 | 404.4 | 543.3 | 399.5
1615 | 1441 | 67.4 | 26.96 | 31.5147 | 457.7 | 446.3 | 395.9 | 370.9 | 689.9 | 62.4 | 18.2 | 110.2 | 6.5 | 212.1 | 5.7 | 811.6 | 835.9 | 792 | 826.7 | 863.7 | 725.3 | 737.5 | 779.3 | 782.2 | 810 | 245.7 | 326.9 | 415 | 401.5 | 441.3 | 416.4 | 418.2 | 404.5 | 543.2 | 399.7
1616 | 1442 | -6.8 | 0 | 0 | 457.5 | 445.8 | 395.6 | 370.8 | 671.7 | 62.4 | 18.2 | 110.3 | 5.9 | 218.8 | 6.1 | 811.4 | 828.2 | 784.6 | 825.3 | 857 | 725.3 | 719.7 | 764.9 | 782.9 | 807.4 | 245.8 | 327 | 414.5 | 401.6 | 440.9 | 415.9 | 418.3 | 404.5 | 543 | 399.8
1617 | 1443 | -6.8 | 0 | 0 | 455.7 | 443.5 | 394.2 | 369.9 | 635.3 | 62.5 | 18.2 | 110.3 | 5.4 | 231.2 | 6.1 | 810.9 | 807.1 | 772.1 | 821.6 | 838.2 | 725.2 | 696.2 | 733.5 | 783.8 | 797.7 | 246 | 327.2 | 413.9 | 401.7 | 440.1 | 414.8 | 418.4 | 404.3 | 542.7 | 399.9
1618 | 1444 | -6.8 | 0 | 0 | 452.2 | 440.3 | 392.6 | 368.4 | 597.5 | 62.5 | 18.2 | 110.2 | 5.3 | 215.7 | 6 | 810.2 | 780.7 | 760.9 | 817 | 818.2 | 724.6 | 672.7 | 707.7 | 784.2 | 788.6 | 246.1 | 327.3 | 413.5 | 401.9 | 439 | 413.3 | 418.1 | 404 | 542.2 | 400
1619 | 1445 | -6.8 | 0 | 0 | 447.5 | 436.8 | 389.8 | 366.9 | 567.9 | 62.5 | 18.2 | 110.2 | 5.4 | 213 | 6.4 | 809.1 | 754.5 | 751 | 812.1 | 799.9 | 723.6 | 651.8 | 684.2 | 784.1 | 779.8 | 246.3 | 327.5 | 413.2 | 401.9 | 437.5 | 411.3 | 417.9 | 403.6 | 541.7 | 400.1
1620 | 1446 | -6.7 | 0 | 0 | 443.1 | 432.9 | 386.3 | 365.1 | 544.4 | 62.4 | 18.2 | 110.1 | 5.1 | 229.2 | 6.3 | 808 | 731.5 | 742.4 | 807.2 | 785.4 | 722.3 | 633.4 | 663 | 783.7 | 772 | 246.5 | 327.6 | 412.9 | 402 | 436 | 409.1 | 417.6 | 403.2 | 541.2 | 400.2
1621 | 1447 | -6.7 | 0 | 0 | 442.1 | 429.7 | 382.6 | 362.6 | 524.5 | 62.4 | 18.2 | 109.7 | 5.6 | 239.6 | 6.6 | 806.8 | 711.9 | 734.1 | 802.5 | 772.3 | 721 | 616.9 | 644.9 | 782.9 | 765 | 246.6 | 327.7 | 412.7 | 402 | 434.3 | 407 | 417.2 | 402.8 | 540.7 | 400.2
1622 | 1448 | -6.7 | 0 | 0 | 440.8 | 426.6 | 378.7 | 359.9 | 507.9 | 62.3 | 18.2 | 109.4 | 5.6 | 232.9 | 6.6 | 805.9 | 695.9 | 726.5 | 797.9 | 758.9 | 719.7 | 602 | 627.3 | 781.3 | 759 | 246.8 | 327.8 | 412.4 | 402 | 432.9 | 404.6 | 416.6 | 402.2 | 540.2 | 400.2
1623 | 1449 | -6.7 | 0 | 0 | 437.2 | 426.1 | 374.9 | 357.1 | 493.3 | 62.3 | 18.2 | 108.8 | 4.6 | 230.6 | 6.5 | 805 | 680.7 | 719.9 | 793.6 | 749.2 | 718.5 | 588.8 | 612.3 | 779.7 | 753.4 | 247 | 327.9 | 412.1 | 401.9 | 431.5 | 401.3 | 416 | 401.6 | 539.7 | 400.3
1624 | 1450 | -6.7 | 0 | 0 | 434.8 | 424.9 | 371.5 | 354.5 | 480.2 | 62.3 | 18.2 | 108.1 | 4.6 | 247.3 | 7.3 | 803.8 | 666.6 | 713.5 | 789.2 | 740.9 | 717.5 | 576.5 | 598.5 | 778.2 | 747.8 | 247.2 | 327.9 | 411.8 | 401.9 | 430 | 398 | 415.3 | 401 | 539.2 | 400.3
1625 | 1451 | -6.7 | 0 | 0 | 433.4 | 422.5 | 368.7 | 351.8 | 468.4 | 62.2 | 18.2 | 107.3 | 4.4 | 246.1 | 7.6 | 802.5 | 654.4 | 707.7 | 784.9 | 732.4 | 716.2 | 564.3 | 587 | 776.7 | 742.5 | 247.4 | 328 | 411.5 | 401.8 | 428.3 | 394.4 | 414.7 | 400.3 | 538.7 | 400.4
1626 | 1452 | -6.7 | 0 | 0 | 430.7 | 418.4 | 366.4 | 349.3 | 457.9 | 62.2 | 18.2 | 106.4 | 4.7 | 242 | 7.4 | 801.1 | 643.3 | 702.2 | 781 | 725.2 | 714.9 | 553.5 | 575.7 | 775 | 737.3 | 247.6 | 328.1 | 411.2 | 401.6 | 426.7 | 391.4 | 414.1 | 399.8 | 538.1 | 400.4
1627 | 1453 | -6.7 | 0 | 0 | 428 | 414.5 | 363.9 | 346.8 | 448.5 | 62.1 | 18.2 | 105.6 | 4.3 | 251.7 | 7.1 | 799.7 | 633.7 | 697 | 777 | 717.7 | 713.7 | 542.4 | 565.8 | 773.6 | 731.6 | 247.8 | 328.1 | 410.9 | 401.5 | 425.1 | 388.6 | 413.5 | 399.2 | 537.6 | 400.4
1628 | 1454 | -6.7 | 0 | 0 | 424.9 | 411.1 | 361.7 | 344.3 | 440.2 | 62 | 18.2 | 104.9 | 4.7 | 251.7 | 6.8 | 798.2 | 623.7 | 692.1 | 772.9 | 711.2 | 712.7 | 532.8 | 557 | 771.8 | 726 | 247.9 | 328.2 | 410.5 | 401.3 | 423.7 | 385.9 | 412.8 | 398.6 | 537.1 | 400.4
1629 | 1455 | -6.7 | 0 | 0 | 422.2 | 409.7 | 359.2 | 342.2 | 433.1 | 61.9 | 18.2 | 104.3 | 4.4 | 245 | 6.9 | 796.7 | 614.5 | 687.2 | 769.3 | 704.3 | 711.2 | 525 | 547.1 | 769.7 | 720.8 | 248.1 | 328.2 | 410.2 | 401.1 | 422.1 | 383.3 | 412.1 | 398 | 536.5 | 400.4
1630 | 1456 | -6.7 | 0 | 0 | 421.3 | 407.9 | 356.8 | 340.1 | 425.8 | 61.8 | 18.2 | 103.6 | 4.4 | 252.2 | 6.3 | 795.5 | 607 | 682.8 | 765.8 | 697.6 | 710 | 517 | 538.8 | 767.7 | 715.4 | 248.3 | 328.3 | 409.9 | 400.8 | 420.5 | 380.8 | 411.5 | 397.5 | 536 | 400.4
1631 | 1457 | -6.7 | 0 | 0 | 419.2 | 405.4 | 354.7 | 338.1 | 419.8 | 61.7 | 18.2 | 103 | 4.3 | 261.6 | 5.7 | 794.2 | 600.4 | 678.6 | 761.7 | 688.5 | 708.6 | 509.6 | 530.7 | 766 | 710.2 | 248.5 | 328.4 | 409.6 | 400.6 | 419.7 | 378.4 | 410.8 | 396.9 | 535.4 | 400.4
1632 | 1458 | -6.7 | 0 | 0 | 418.4 | 402.9 | 352.5 | 336.1 | 415.5 | 61.7 | 18.2 | 102.3 | 4.2 | 251.3 | 5.5 | 792.7 | 594.3 | 674.7 | 758.8 | 682.3 | 707.1 | 502.4 | 522.5 | 764.1 | 705.1 | 248.6 | 328.4 | 409.3 | 400.3 | 418.7 | 376.1 | 410.1 | 396.2 | 534.9 | 400.4
1633 | 1459 | -6.7 | 0 | 0 | 417.8 | 400.8 | 350 | 334.1 | 411.3 | 61.7 | 18.2 | 101.7 | 4.5 | 246.5 | 4.8 | 791.1 | 588.2 | 670.7 | 756.1 | 678.4 | 705.9 | 496.2 | 515.7 | 762.5 | 699.8 | 248.8 | 328.4 | 409 | 400.1 | 417.3 | 373.8 | 409.3 | 395.6 | 534.4 | 400.4
1634 | 1460 | -6.7 | 0 | 0 | 416.8 | 400 | 347.6 | 332.3 | 407.3 | 61.6 | 18.2 | 101.1 | 4.6 | 248.1 | 4.8 | 789.5 | 581.1 | 667.3 | 753.3 | 674.2 | 705 | 489.9 | 508.8 | 760.9 | 694.7 | 249 | 328.5 | 408.7 | 399.8 | 415.8 | 371.4 | 408.6 | 395.1 | 533.8 | 400.4
1635 | 1461 | -6.7 | 0 | 0 | 415.1 | 398.4 | 345.7 | 330.6 | 404.2 | 61.5 | 18.2 | 100.5 | 4.9 | 247.4 | 5 | 787.7 | 575 | 664.4 | 750.4 | 670.5 | 703.9 | 484.4 | 501.8 | 759 | 689.7 | 249.1 | 328.5 | 408.3 | 399.5 | 414.2 | 369.3 | 407.9 | 394.5 | 533.2 | 400.4
1636 | 1462 | -6.7 | 0 | 0 | 412.9 | 395.7 | 344.1 | 329.3 | 400.2 | 61.4 | 18.2 | 99.9 | 4.6 | 242.8 | 5.2 | 785.9 | 568.5 | 661.4 | 747.5 | 666.1 | 702.7 | 478.8 | 495.7 | 757.1 | 685 | 249.3 | 328.5 | 408 | 399.1 | 412.6 | 367.3 | 407.3 | 393.8 | 532.7 | 400.4
1637 | 1463 | -6.7 | 0 | 0 | 409.3 | 394 | 342.4 | 327.8 | 395.2 | 61.4 | 18.2 | 99.3 | 4.6 | 245.6 | 4.7 | 784.1 | 563.2 | 658.2 | 744.9 | 660 | 701.5 | 473.7 | 489.3 | 755.3 | 680.8 | 249.4 | 328.6 | 407.7 | 398.8 | 410.9 | 365.6 | 406.6 | 393.3 | 532.2 | 400.4
1638 | 1464 | -6.7 | 0 | 0 | 407.2 | 393.4 | 340.5 | 326.2 | 391.4 | 61.2 | 18.2 | 98.8 | 4.9 | 256.2 | 4.3 | 782.3 | 559.1 | 655.2 | 742.6 | 654.1 | 700.1 | 469.2 | 483.3 | 753.1 | 675.9 | 249.6 | 328.6 | 407.4 | 398.4 | 409.4 | 363.5 | 406 | 392.6 | 531.6 | 400.3
1639 | 1465 | -6.7 | 0 | 0 | 406.4 | 391.3 | 338.9 | 324.8 | 388.1 | 61.1 | 18.2 | 98.4 | 4.8 | 276 | 4.6 | 780.7 | 553 | 652.4 | 740.4 | 649.8 | 698.7 | 465.2 | 477.9 | 750.7 | 671.4 | 249.7 | 328.6 | 407.1 | 398.1 | 408 | 361.6 | 405.4 | 392.1 | 531.1 | 400.3
1640 | 1466 | -6.7 | 0 | 0 | 403.9 | 389.1 | 337.4 | 323.4 | 385 | 61 | 18.2 | 97.9 | 4.4 | 264.3 | 5.1 | 778.9 | 546.9 | 649.9 | 737.6 | 646.2 | 696.8 | 463.9 | 471.4 | 748.1 | 668 | 249.9 | 328.7 | 406.8 | 397.7 | 406.4 | 360.1 | 404.7 | 391.5 | 530.5 | 400.3
1641 | 1467 | -6.7 | 0 | 0 | 402.4 | 387.2 | 335.8 | 322 | 383 | 60.9 | 18.2 | 97.4 | 4.8 | 252.6 | 5.5 | 777.2 | 542.2 | 647.2 | 734.2 | 641.9 | 694.9 | 463.8 | 467.2 | 744.4 | 664.8 | 250.1 | 328.7 | 406.5 | 397.3 | 405 | 358.5 | 404 | 390.9 | 530 | 400.2
1642 | 1468 | -6.7 | 0 | 0 | 402.2 | 384.9 | 334.2 | 320.6 | 381.3 | 60.9 | 18.2 | 97 | 4.6 | 262.8 | 5.5 | 775.5 | 537.8 | 644.5 | 731.7 | 638.6 | 693.2 | 464 | 463.1 | 740.3 | 661 | 250.2 | 328.7 | 406.1 | 397 | 404 | 357 | 403.4 | 390.4 | 529.4 | 400.2
1643 | 1469 | -6.7 | 0 | 0 | 400.8 | 383.4 | 332.9 | 319.2 | 379.7 | 60.7 | 18.2 | 96.6 | 4.5 | 262.1 | 5.3 | 773.8 | 532.7 | 641.8 | 728.9 | 636.1 | 691.6 | 463.7 | 458.4 | 736.8 | 657.4 | 250.4 | 328.7 | 405.8 | 396.6 | 402.9 | 356 | 402.9 | 389.8 | 528.9 | 400.1
1644 | 1470 | -6.7 | 0 | 0 | 397.8 | 381.6 | 331.6 | 318 | 378.1 | 60.6 | 18.2 | 96.2 | 4.7 | 263.8 | 5.1 | 771.9 | 528.2 | 639.1 | 726.6 | 633.2 | 690 | 463 | 454.2 | 733.3 | 653.9 | 250.5 | 328.8 | 405.5 | 396.2 | 401.8 | 354.6 | 402.3 | 389.2 | 528.3 | 400.1
1645 | 1471 | -6.7 | 0 | 0 | 395.4 | 381 | 330.3 | 317 | 376.5 | 60.5 | 18.2 | 95.8 | 5 | 270 | 5.2 | 770.2 | 524.2 | 636.6 | 724.3 | 629.4 | 688.3 | 462.2 | 450.1 | 729.8 | 650.9 | 250.7 | 328.8 | 405.2 | 395.8 | 400.4 | 353 | 401.6 | 388.6 | 527.8 | 400
1646 | 1472 | -6.7 | 0 | 0 | 393.9 | 379.3 | 329.2 | 316.1 | 375 | 60.4 | 18.2 | 95.4 | 5.2 | 272.1 | 5.3 | 768.5 | 519.3 | 633.8 | 722 | 624.9 | 686.6 | 461.4 | 446.6 | 726.2 | 647.2 | 250.8 | 328.8 | 404.8 | 395.5 | 399 | 351.6 | 401.1 | 388.1 | 527.2 | 399.9
1647 | 1473 | -6.7 | 0 | 0 | 392.7 | 378.8 | 328.5 | 315.1 | 373.6 | 60.3 | 18.2 | 95.1 | 5 | 268 | 5.2 | 766.7 | 516 | 631.3 | 720.1 | 620.6 | 684.9 | 459.8 | 441.9 | 723.3 | 644 | 251 | 328.8 | 404.5 | 395.1 | 397.6 | 350.3 | 400.3 | 387.4 | 526.6 | 399.9
1648 | 1474 | -6.7 | 0 | 0 | 392.4 | 378.4 | 327.6 | 314.3 | 372.1 | 60.2 | 18.2 | 94.8 | 4.4 | 263.9 | 5 | 764.9 | 513.7 | 628.9 | 717.9 | 618 | 683.3 | 457.5 | 436.5 | 720.7 | 640 | 251.2 | 328.9 | 404.2 | 394.7 | 396.4 | 349.3 | 399.7 | 386.9 | 526.1 | 399.8
1649 | 1475 | -6.7 | 0 | 0 | 392.9 | 377.4 | 326.8 | 313.5 | 370.7 | 60 | 18.2 | 94.4 | 4.5 | 261.7 | 4.8 | 763.3 | 511.4 | 626.4 | 715.8 | 614.6 | 682.3 | 453.4 | 430.9 | 718.7 | 636.5 | 251.3 | 328.9 | 403.9 | 394.3 | 395.3 | 348.3 | 399.1 | 386.4 | 525.5 | 399.8
1650 | 1476 | -6.7 | 0 | 0 | 394.4 | 376.3 | 325.9 | 312.9 | 369.2 | 59.8 | 18.2 | 94.1 | 4.5 | 259.1 | 4.8 | 761.7 | 507.4 | 623.9 | 713.4 | 610.9 | 681 | 451.5 | 426.2 | 716.6 | 633.2 | 251.5 | 328.9 | 403.5 | 394 | 394.6 | 347.1 | 398.4 | 385.8 | 524.9 | 399.7
1651 | 1477 | -6.7 | 0 | 0 | 393.9 | 375.1 | 324.8 | 312.3 | 367.9 | 59.7 | 18.2 | 93.8 | 4.1 | 259 | 4.9 | 760.1 | 505.8 | 621.4 | 711.4 | 606.8 | 679.2 | 450.8 | 421.7 | 713.6 | 629.4 | 251.6 | 328.9 | 403.2 | 393.6 | 393.5 | 345.8 | 397.9 | 385.3 | 524.4 | 399.6
1652 | 1478 | -6.7 | 0 | 0 | 392.8 | 373.3 | 323.8 | 311.7 | 366.6 | 59.5 | 18.2 | 93.4 | 4.5 | 253.3 | 4.8 | 758.5 | 503.6 | 618.9 | 709.1 | 601.6 | 677.9 | 449.4 | 416.7 | 711.5 | 626.1 | 251.8 | 328.9 | 402.9 | 393.2 | 392 | 344.7 | 397.4 | 384.7 | 523.8 | 399.6
1653 | 1479 | -6.7 | 0 | 0 | 393.6 | 371.6 | 323.2 | 311 | 365.3 | 59.4 | 18.2 | 92.9 | 4.9 | 251.5 | 4.5 | 756.8 | 499.3 | 616.3 | 707 | 597.8 | 676.5 | 446.9 | 411.7 | 709.6 | 623.2 | 251.9 | 328.9 | 402.6 | 392.8 | 391.2 | 343.5 | 396.9 | 384.1 | 523.3 | 399.5
1654 | 1480 | -6.7 | 0 | 0 | 392.1 | 369.9 | 322.7 | 310.3 | 364.1 | 59.3 | 18.2 | 92.6 | 4.9 | 251.8 | 4.2 | 755 | 495.8 | 614.1 | 704.7 | 593.8 | 675.6 | 443.4 | 407.3 | 707.9 | 619.5 | 252 | 328.9 | 402.3 | 392.4 | 390 | 342.5 | 396.3 | 383.6 | 522.7 | 399.5
1655 | 1481 | -6.7 | 0 | 0 | 391.8 | 368.6 | 322.3 | 309.6 | 362.9 | 59 | 18.2 | 92.3 | 5.1 | 252.4 | 4 | 753.3 | 492.4 | 612 | 702.6 | 589.3 | 674.6 | 440.4 | 403.3 | 706.1 | 616.2 | 252.2 | 328.9 | 401.9 | 392.1 | 389.2 | 341.5 | 395.7 | 383.1 | 522.2 | 399.4
1656 | 1482 | -6.7 | 0 | 0 | 391.4 | 367.4 | 321.6 | 308.7 | 361.8 | 58.8 | 18.2 | 92 | 5.4 | 254.5 | 3.9 | 751.7 | 489.9 | 609.5 | 700.7 | 584.7 | 673.8 | 435 | 398.9 | 704.8 | 612.3 | 252.4 | 328.9 | 401.6 | 391.7 | 388 | 340.3 | 395.2 | 382.5 | 521.6 | 399.3
1657 | 1483 | -6.7 | 0 | 0 | 388.9 | 366.1 | 321 | 308 | 360.9 | 58.6 | 18.2 | 91.6 | 5.2 | 254.7 | 4 | 750.1 | 487.6 | 607.1 | 698.2 | 579.9 | 673 | 430.4 | 394.8 | 703.7 | 609 | 252.5 | 328.9 | 401.3 | 391.3 | 386.8 | 339.3 | 394.7 | 381.9 | 521 | 399.3
1658 | 1484 | -6.7 | 0 | 0 | 387.7 | 364.9 | 320.4 | 307.3 | 360.3 | 58.4 | 18.2 | 91.2 | 4.8 | 250 | 4.2 | 748.5 | 485.4 | 604.7 | 696.2 | 575.4 | 671.8 | 427.4 | 390.5 | 702.1 | 606.5 | 252.6 | 328.9 | 401 | 391 | 385.7 | 338.4 | 394 | 381.4 | 520.5 | 399.2
1659 | 1485 | -6.7 | 0 | 0 | 387.4 | 363.5 | 319.9 | 306.4 | 360.5 | 58.2 | 18.3 | 90.8 | 4.8 | 242 | 4.3 | 746.9 | 484.3 | 602.3 | 693.7 | 572 | 670.7 | 424.1 | 387.1 | 700.4 | 603.5 | 252.8 | 328.9 | 400.6 | 390.6 | 384.3 | 337.5 | 393.2 | 380.8 | 520 | 399.1
1660 | 1486 | -6.7 | 0 | 0 | 386.5 | 362.4 | 319.2 | 305.5 | 359.8 | 58 | 18.3 | 90.6 | 4.8 | 258.2 | 4.1 | 745.7 | 481.6 | 600.6 | 689.8 | 569.5 | 669.4 | 422.9 | 385.7 | 698.4 | 600 | 252.9 | 328.9 | 400.3 | 390.3 | 382.9 | 336.5 | 392.5 | 380.2 | 519.4 | 399
1661 | 1487 | -6.7 | 0 | 0 | 384.4 | 361.3 | 318.2 | 304.7 | 358.9 | 57.9 | 18.3 | 90.3 | 5.1 | 266.7 | 4 | 744.5 | 480 | 599 | 687.6 | 567.3 | 668 | 421.7 | 384.9 | 696.3 | 597.1 | 253 | 328.9 | 400 | 390 | 381.6 | 335.6 | 392 | 379.6 | 518.8 | 398.9
1662 | 1488 | -6.7 | 0 | 0 | 383 | 360.5 | 317.2 | 304.2 | 358.2 | 57.8 | 18.3 | 90 | 5.6 | 250.7 | 3.7 | 743.1 | 478.6 | 596.9 | 683.9 | 564.4 | 666.9 | 417.9 | 383.9 | 694.7 | 594.4 | 253.2 | 328.9 | 399.7 | 389.6 | 380.7 | 334.7 | 391.4 | 379.1 | 518.3 | 398.8
1663 | 1489 | -6.7 | 0 | 0 | 382 | 360 | 316.3 | 303.7 | 356 | 57.7 | 18.3 | 89.8 | 4.9 | 231.4 | 3.4 | 741.7 | 474.9 | 595.2 | 678.8 | 563 | 665.9 | 416.1 | 382.6 | 692.8 | 591.1 | 253.3 | 328.9 | 399.3 | 389.4 | 379.8 | 333.8 | 390.7 | 378.5 | 517.7 | 398.7
1664 | 1490 | -6.6 | 0 | 0 | 378.5 | 359.4 | 315.3 | 303.2 | 351.1 | 57.6 | 18.3 | 89.5 | 4.5 | 236.9 | 3.4 | 740.3 | 472.7 | 593.6 | 674.6 | 561.3 | 665.1 | 413.1 | 380.3 | 691.2 | 587.7 | 253.3 | 328.9 | 399 | 389.2 | 378.5 | 332.9 | 390.2 | 377.9 | 517.2 | 398.6
1665 | 1491 | -6.7 | 0 | 0 | 374.5 | 358.6 | 314.7 | 302.6 | 339.3 | 57.4 | 18.3 | 89.3 | 4.7 | 249.8 | 3.8 | 739.5 | 467.9 | 593.8 | 667.9 | 559.8 | 663.3 | 407.4 | 376.4 | 689.3 | 582.2 | 253.4 | 328.9 | 398.6 | 388.9 | 377.7 | 331.7 | 389.5 | 377.3 | 516.6 | 398.5
1666 | 1492 | -6.7 | 0 | 0 | 371.3 | 356.8 | 314.1 | 301.5 | 328.2 | 57.1 | 18.3 | 89.1 | 4.6 | 255.7 | 4.1 | 738.4 | 465.5 | 593.1 | 663.3 | 558.4 | 661.6 | 402.7 | 372.9 | 687.5 | 577.9 | 253.5 | 328.8 | 398.3 | 388.6 | 376.7 | 330.6 | 388.9 | 376.7 | 516.1 | 398.5
1667 | 1493 | -6.6 | 0 | 0 | 367.9 | 357.2 | 313.3 | 300.1 | 293.5 | 56.9 | 18.3 | 88.9 | 4.7 | 256.5 | 4.3 | 736.9 | 462.4 | 591.3 | 658.9 | 555.8 | 655.6 | 395.6 | 368.5 | 684.3 | 573.3 | 253.6 | 328.8 | 397.9 | 388.4 | 375.4 | 329.4 | 388.2 | 376.1 | 515.5 | 398.4
1668 | 1494 | -6.7 | 0 | 0 | 363.1 | 356.6 | 312.1 | 298.7 | 224.1 | 56.7 | 18.3 | 88.6 | 4.9 | 250.5 | 4.3 | 735.2 | 457.1 | 588.4 | 656.5 | 552.5 | 648.1 | 360 | 363 | 678.6 | 566.7 | 253.7 | 328.7 | 397.5 | 388.1 | 374.2 | 327.8 | 387.4 | 375.4 | 515 | 398.3
1669 | 1495 | -6.6 | 0 | 0 | 361.1 | 354.1 | 310.4 | 296.7 | 192 | 56.5 | 18.3 | 88.4 | 5.4 | 239.2 | 4.5 | 732.5 | 446.6 | 582.9 | 651.9 | 549 | 600.2 | 332.3 | 351.4 | 640.2 | 553.4 | 253.8 | 328.7 | 397.1 | 387.9 | 373.5 | 326.1 | 387 | 374.7 | 514.4 | 398.2
1670 | 1496 | -6.7 | 0 | 0 | 356.9 | 352.3 | 309.3 | 294.8 | 91.2 | 56.4 | 18.3 | 88.2 | 5.4 | 221.9 | 4.7 | 727.4 | 427.5 | 572.3 | 642.5 | 544.8 | 474.2 | 322.1 | 302.3 | 575.8 | 546.4 | 254 | 328.6 | 396.7 | 387.6 | 373.1 | 324.5 | 386.5 | 374.1 | 513.8 | 398.1
1671 | 1497 | -6.7 | 0 | 0 | 354.2 | 350.5 | 308.7 | 293.8 | 72.4 | 56.3 | 18.3 | 88 | 5.2 | 206 | 5.3 | 720.6 | 400.5 | 561.8 | 631.8 | 540.4 | 421.8 | 283.5 | 255.7 | 532.5 | 539.2 | 254.1 | 328.5 | 396.4 | 387.4 | 372.5 | 323.3 | 385.8 | 373.4 | 513.2 | 398
1672 | 1498 | -6.7 | 0 | 0 | 352.5 | 348.5 | 308 | 293.1 | 70.3 | 56.3 | 18.3 | 87.8 | 5.5 | 210.6 | 5.6 | 712.4 | 366 | 547.4 | 619.8 | 537.2 | 314.6 | 216.7 | 232.6 | 496 | 534.7 | 254.3 | 328.5 | 396 | 387.1 | 371.2 | 322.1 | 385.1 | 372.8 | 512.5 | 397.9
1673 | 1499 | -6.7 | 0 | 0 | 350.7 | 346.8 | 307.4 | 292.4 | 72.3 | 56.3 | 18.3 | 87.6 | 5 | 215.8 | 5.9 | 703.3 | 332.8 | 530.2 | 603.2 | 534 | 220.1 | 167.2 | 221.2 | 394.7 | 529.5 | 254.4 | 328.4 | 395.6 | 386.9 | 369.8 | 321.2 | 384.3 | 372.2 | 511.9 | 397.8
1674 | 1500 | -6.7 | 0 | 0 | 349.2 | 345.1 | 306.6 | 291.7 | 74.4 | 56.4 | 18.3 | 87.4 | 4.4 | 224.8 | 5.9 | 695.8 | 309.5 | 511.2 | 582.5 | 530 | 207.4 | 143.3 | 214.6 | 299.7 | 519.5 | 254.5 | 328.3 | 395.2 | 386.7 | 368.5 | 320.5 | 383.7 | 371.6 | 511.2 | 397.6
1675 | 1501 | -6.7 | 0 | 0 | 347.6 | 343.9 | 305.8 | 291.2 | 74 | 56.5 | 18.3 | 87.2 | 4.3 | 228.9 | 5.6 | 687.4 | 284.1 | 479.9 | 553.3 | 526.6 | 204 | 110.4 | 195.2 | 285.8 | 510.5 | 254.7 | 328.3 | 394.9 | 386.5 | 367.3 | 319.8 | 383.1 | 371 | 510.5 | 397.5
1676 | 1502 | -6.7 | 0 | 0 | 346.2 | 342.9 | 305 | 291 | 77.7 | 56.5 | 18.3 | 87 | 4.3 | 244.6 | 5.1 | 680.4 | 259.1 | 447.1 | 528.3 | 523.3 | 200.5 | 106.9 | 141.1 | 270.4 | 503.5 | 254.9 | 328.2 | 394.6 | 386.3 | 366.2 | 319.1 | 382.4 | 370.4 | 509.9 | 397.4
1677 | 1503 | -6.7 | 0 | 0 | 345 | 342.5 | 304.5 | 290.8 | 80.1 | 56.5 | 18.3 | 86.8 | 4.1 | 246.3 | 4.3 | 675.8 | 234.1 | 420.8 | 502.6 | 518.9 | 197.6 | 108.8 | 98.5 | 251.6 | 497.5 | 255 | 328.2 | 394.2 | 386.1 | 365.6 | 318.4 | 381.6 | 369.8 | 509.2 | 397.2
1678 | 1504 | -6.7 | 0 | 0 | 344 | 342.4 | 304 | 290.4 | 78.8 | 56.5 | 18.3 | 86.6 | 4.3 | 200 | 4.1 | 668.7 | 213.4 | 394.5 | 472.5 | 517.8 | 194.7 | 109.3 | 85.7 | 235.5 | 492.1 | 255.1 | 328.2 | 393.8 | 385.9 | 365.1 | 317.8 | 380.9 | 369.3 | 508.5 | 397.1
1679 | 1505 | -6.7 | 0 | 0 | 342.8 | 342.5 | 303.3 | 289.7 | 78.1 | 56.3 | 18.3 | 86.3 | 4.3 | 190.9 | 3.9 | 661.6 | 200.9 | 368 | 444.8 | 515.9 | 190.8 | 108.6 | 87.3 | 220.2 | 482.5 | 255.2 | 328.1 | 393.5 | 385.7 | 364.5 | 317.3 | 380.3 | 368.7 | 507.9 | 397
1680 | 1506 | -6.7 | 0 | 0 | 341.8 | 342.2 | 302.6 | 289.2 | 77.1 | 56.1 | 18.3 | 86 | 4.5 | 238.7 | 3.6 | 654.6 | 203.9 | 347.9 | 417.5 | 513.2 | 186.4 | 105.3 | 85.2 | 211.4 | 477.6 | 255.3 | 328.1 | 393.1 | 385.5 | 364 | 316.7 | 379.8 | 368.1 | 507.3 | 396.9
1681 | 1507 | -6.7 | 0 | 0 | 341.1 | 341.7 | 302 | 288.8 | 72.4 | 56 | 18.3 | 85.8 | 4.4 | 258.4 | 3.5 | 646.3 | 200.5 | 329.7 | 393.8 | 509.9 | 182.5 | 102.7 | 83.7 | 204.4 | 471.9 | 255.5 | 328.1 | 392.8 | 385.4 | 363.4 | 316 | 379.4 | 367.5 | 506.7 | 396.7
1682 | 1508 | -6.7 | 0 | 0 | 340.5 | 341.8 | 301.5 | 288.3 | 73 | 55.9 | 18.3 | 85.5 | 4.4 | 228.6 | 3.4 | 636.4 | 198.9 | 302.3 | 367.4 | 505.6 | 176.5 | 104.6 | 81.2 | 196.9 | 472 | 255.6 | 328.1 | 392.4 | 385.3 | 363 | 315.2 | 378.8 | 366.9 | 506.1 | 396.6
1683 | 1509 | -6.7 | 0 | 0 | 339.9 | 341.5 | 301.1 | 287.4 | 72.1 | 55.7 | 18.3 | 85.3 | 4.4 | 192.2 | 3.2 | 623.1 | 198.1 | 254.8 | 332.9 | 502.3 | 174.4 | 101.3 | 82.6 | 189.9 | 464.3 | 255.8 | 328 | 392.1 | 385.3 | 362.3 | 314.3 | 378.2 | 366.3 | 505.4 | 396.4
1684 | 1510 | -6.7 | 0 | 0 | 339.2 | 341.4 | 300.5 | 286.6 | 72.1 | 55.5 | 18.3 | 85 | 4.5 | 183.8 | 2.8 | 607.8 | 197.4 | 219.1 | 290.4 | 498 | 168.1 | 101.1 | 82 | 177.1 | 456.5 | 255.9 | 328 | 391.7 | 385.3 | 361.3 | 313.6 | 377.5 | 365.8 | 504.8 | 396.3
1685 | 1511 | -6.7 | 0 | 0 | 338.5 | 341.2 | 299.9 | 285.9 | 74 | 55.4 | 18.3 | 84.8 | 4.5 | 199.8 | 2.5 | 593.7 | 194.5 | 197.1 | 274.6 | 492.7 | 165.4 | 95.8 | 84.6 | 157.1 | 448 | 256 | 327.9 | 391.4 | 385.3 | 360.4 | 313 | 376.9 | 365.2 | 504.3 | 396.1
1686 | 1512 | -6.7 | 0 | 0 | 338 | 340.7 | 299.1 | 285.3 | 75.2 | 55.3 | 18.3 | 84.6 | 4.5 | 211.3 | 2.4 | 580.1 | 191.3 | 187.6 | 264.2 | 491.2 | 164.9 | 100.1 | 86.5 | 151.2 | 435.9 | 256.2 | 327.9 | 391 | 385.4 | 359.7 | 312.5 | 376.4 | 364.7 | 503.7 | 396
1687 | 1513 | -6.7 | 0 | 0 | 337.5 | 340 | 298.5 | 284.4 | 75.5 | 55.1 | 18.3 | 84.3 | 4.8 | 217 | 2.4 | 568 | 189.5 | 177.4 | 254.2 | 487.5 | 162.7 | 103.6 | 85.7 | 148 | 411.7 | 256.3 | 327.8 | 390.7 | 385.5 | 358.7 | 312 | 376.2 | 364.2 | 503.1 | 395.9
1688 | 1514 | -6.7 | 0 | 0 | 336.8 | 339.6 | 298 | 283.3 | 74.9 | 54.9 | 18.3 | 84.1 | 4.9 | 235 | 2.5 | 554.3 | 188.2 | 161.7 | 246.6 | 482.3 | 163.1 | 99.3 | 85.5 | 146.5 | 420.2 | 256.5 | 327.8 | 390.3 | 385.6 | 357.9 | 311.5 | 376 | 363.6 | 502.5 | 395.7
1689 | 1515 | -6.7 | 0 | 0 | 336.3 | 340 | 297.2 | 282.2 | 74.4 | 54.6 | 18.3 | 83.8 | 4.9 | 256.5 | 2.5 | 539.1 | 190.7 | 149.8 | 242.1 | 475.4 | 161.7 | 96.7 | 87.5 | 141.8 | 406.9 | 256.6 | 327.8 | 390 | 385.6 | 357 | 310.8 | 375.5 | 363.1 | 502 | 395.6
1690 | 1516 | -6.7 | 0 | 0 | 335.5 | 339.6 | 296.2 | 281.1 | 73.1 | 54.5 | 18.3 | 83.6 | 5.2 | 257.7 | 2.4 | 523.9 | 191.2 | 140.2 | 235.8 | 471.2 | 160.1 | 100.2 | 87.4 | 133.9 | 376.6 | 256.7 | 327.7 | 389.7 | 385.7 | 356.3 | 310.1 | 374.8 | 362.5 | 501.4 | 395.5
1691 | 1517 | -6.7 | 0 | 0 | 334.9 | 339.1 | 295 | 280.4 | 72.3 | 54.3 | 18.3 | 83.2 | 5.2 | 243.2 | 2.2 | 509.3 | 190.8 | 132.4 | 227.7 | 468.4 | 154.5 | 104 | 84.3 | 124.4 | 318.7 | 256.9 | 327.7 | 389.3 | 385.8 | 355.4 | 309.5 | 374.2 | 362 | 500.9 | 395.3
1692 | 1518 | -6.7 | 0 | 0 | 334.6 | 338.9 | 294 | 279.6 | 71.5 | 54.1 | 18.3 | 82.9 | 5 | 222.7 | 2 | 495.3 | 188.5 | 126 | 220.6 | 466.3 | 148.5 | 95.4 | 70.1 | 119.4 | 198.4 | 257 | 327.6 | 389 | 385.9 | 354.7 | 308.8 | 373.7 | 361.3 | 500.3 | 395.2
1693 | 1519 | -6.7 | 0 | 0 | 334.1 | 339.4 | 293.1 | 279.1 | 71.8 | 54 | 18.3 | 82.6 | 4.7 | 205 | 1.9 | 479.5 | 184.7 | 120.9 | 215 | 463.1 | 151.1 | 92.4 | 67.1 | 115.3 | 99 | 257.1 | 327.6 | 388.7 | 385.9 | 353.9 | 308.1 | 373.2 | 360.8 | 499.9 | 395.1
1694 | 1520 | -6.7 | 0 | 0 | 333.5 | 339.1 | 292.1 | 278.5 | 72.2 | 53.8 | 18.3 | 82.3 | 5 | 193 | 1.9 | 461.7 | 184.6 | 116.3 | 208.8 | 456.7 | 144 | 89.1 | 70.8 | 110.3 | 91.7 | 257.3 | 327.5 | 388.3 | 386 | 353.1 | 307.4 | 372.6 | 360.3 | 499.3 | 394.9
1695 | 1521 | -6.6 | 0 | 0 | 332.7 | 338.3 | 291.1 | 278.1 | 72.3 | 53.7 | 18.3 | 82.1 | 4.6 | 189.9 | 2 | 442.7 | 181.4 | 112.9 | 204.2 | 311 | 138.6 | 88.2 | 71.9 | 105.6 | 88.4 | 257.4 | 327.4 | 388 | 386.1 | 352.4 | 306.7 | 371.9 | 359.8 | 498.7 | 394.8
1696 | 1522 | -6.6 | 0 | 0 | 331.9 | 337.6 | 289.5 | 277.9 | 72.9 | 53.5 | 18.3 | 81.9 | 4.6 | 194.8 | 2.7 | 421.6 | 180.2 | 110.2 | 197.6 | 186.1 | 136.5 | 86.9 | 73.4 | 103.4 | 86.4 | 257.5 | 327.4 | 387.7 | 386.1 | 352 | 306.1 | 371.3 | 359.2 | 498.1 | 394.6
1697 | 1523 | -6.6 | 0 | 0 | 331.2 | 337.2 | 288.2 | 277.5 | 71.3 | 53.2 | 18.3 | 81.6 | 4.7 | 205 | 3.4 | 396.5 | 177.4 | 109 | 193.7 | 159.8 | 139.1 | 88.4 | 77.8 | 102.4 | 84.6 | 257.6 | 327.3 | 387.3 | 386.2 | 351.3 | 305.5 | 370.8 | 358.7 | 497.5 | 394.5
1698 | 1524 | -6.7 | 0 | 0 | 330.6 | 336.5 | 287.5 | 277.2 | 71.2 | 53 | 18.3 | 81.4 | 4.6 | 210.9 | 3.5 | 365.5 | 173.7 | 107.7 | 188.4 | 157.8 | 137.5 | 90.1 | 79.5 | 99.4 | 83.8 | 257.7 | 327.2 | 387 | 386.2 | 350.2 | 305.1 | 370.3 | 358.2 | 496.9 | 394.4
1699 | 1525 | -6.7 | 0 | 0 | 330.1 | 335.3 | 286.4 | 276.9 | 69.4 | 52.9 | 18.4 | 81.2 | 4.9 | 207.5 | 3.4 | 326.8 | 169.9 | 105.5 | 183.7 | 164.6 | 134.4 | 93.7 | 77.5 | 96.9 | 82.6 | 257.8 | 327.2 | 386.6 | 386.2 | 349.5 | 304.5 | 369.8 | 357.7 | 496.3 | 394.2
1700 | 1526 | -6.7 | 0 | 0 | 329.5 | 333.9 | 285.3 | 277 | 70.5 | 52.8 | 18.3 | 81.1 | 4.5 | 212.9 | 3.2 | 280.1 | 170.6 | 103.3 | 180.8 | 171.6 | 138 | 95.6 | 70.6 | 95.7 | 82 | 257.9 | 327.1 | 386.3 | 386.2 | 348.7 | 303.9 | 369.2 | 357.1 | 495.8 | 394
1701 | 1527 | -6.6 | 0 | 0 | 328.9 | 333.6 | 284.7 | 277.1 | 72.2 | 52.7 | 18.3 | 80.9 | 4.4 | 223.6 | 3.1 | 227.5 | 168.6 | 101.9 | 178.1 | 168.3 | 134.6 | 97.5 | 60.5 | 95.5 | 81.3 | 258 | 327.1 | 385.9 | 386.2 | 347.7 | 303.4 | 368.6 | 356.6 | 495.2 | 393.9
1702 | 1528 | -6.6 | 0 | 0 | 328 | 333.3 | 284 | 276.9 | 74.3 | 52.6 | 18.3 | 80.6 | 4.4 | 227.4 | 2.9 | 189.4 | 163.1 | 99.9 | 174.5 | 164.3 | 120.5 | 92.2 | 61.5 | 94.5 | 79.7 | 258.1 | 327 | 385.6 | 386.2 | 347.1 | 303 | 367.9 | 356.1 | 494.7 | 393.7
1703 | 1529 | -6.7 | 0 | 0 | 327.3 | 332.9 | 283.5 | 276.9 | 75.4 | 52.4 | 18.4 | 80.4 | 4.6 | 232.6 | 3.1 | 176.4 | 163 | 97 | 169.5 | 159.4 | 106.6 | 92.8 | 60.9 | 92.9 | 76.9 | 258.3 | 326.9 | 385.3 | 386.3 | 346.5 | 302.4 | 367.3 | 355.6 | 494.1 | 393.6
1704 | 1530 | -6.7 | 0 | 0 | 326.7 | 332.1 | 283 | 276.6 | 76.1 | 52.3 | 18.4 | 80.2 | 4.8 | 250.1 | 3.7 | 170.6 | 162.2 | 94.5 | 169.2 | 155.5 | 106.5 | 90.9 | 61.3 | 92.8 | 74.4 | 258.4 | 326.8 | 384.9 | 386.3 | 346.1 | 301.9 | 366.9 | 355.1 | 493.6 | 393.4
1705 | 1531 | -6.6 | 0 | 0 | 326.3 | 331.6 | 282.6 | 276.4 | 75.5 | 52.3 | 18.4 | 80.1 | 4.3 | 253.9 | 4 | 166.1 | 164 | 92.6 | 165.4 | 151.2 | 110.7 | 88.2 | 62.2 | 91.4 | 72.6 | 258.5 | 326.7 | 384.6 | 386.2 | 345.6 | 301.4 | 366.4 | 354.5 | 493 | 393.3
1706 | 1532 | -6.7 | 0 | 0 | 325.6 | 330.9 | 282 | 276.4 | 75.6 | 52.4 | 18.4 | 79.9 | 4.7 | 232.9 | 4.3 | 162 | 162.9 | 91.1 | 163.6 | 151.1 | 106.2 | 85.2 | 60.1 | 89.5 | 71.1 | 258.7 | 326.7 | 384.3 | 386.2 | 345.1 | 301 | 365.9 | 353.9 | 492.4 | 393.1
1707 | 1533 | -6.6 | 0 | 0 | 324.5 | 330 | 281.5 | 276 | 77.7 | 52.3 | 18.4 | 79.8 | 5 | 232.4 | 4.8 | 158.7 | 160.9 | 90.1 | 161.3 | 149.7 | 105.3 | 83 | 58.1 | 88.7 | 69.4 | 258.8 | 326.6 | 383.9 | 386.1 | 344.4 | 300.4 | 365.4 | 353.5 | 491.8 | 393
1708 | 1534 | -6.6 | 0 | 0 | 323.7 | 329.3 | 281.3 | 275.6 | 77.2 | 52.3 | 18.4 | 79.6 | 4.7 | 238.5 | 4.9 | 156 | 156.8 | 89 | 159.2 | 145.4 | 106.4 | 84.7 | 58.8 | 87.7 | 67.6 | 259 | 326.5 | 383.6 | 386.1 | 344 | 299.8 | 365 | 352.9 | 491.2 | 392.8
1709 | 1535 | -6.7 | 0 | 0 | 322.8 | 329.1 | 281.1 | 275.3 | 72.5 | 52.2 | 18.4 | 79.4 | 4.8 | 235 | 4.8 | 153.3 | 156.5 | 87.2 | 155.7 | 139.9 | 105.3 | 84.4 | 59.9 | 87.5 | 64.3 | 259.1 | 326.5 | 383.3 | 386 | 343.6 | 299.2 | 364.5 | 352.4 | 490.6 | 392.7
1710 | 1536 | -6.6 | 0 | 0 | 321.8 | 328.9 | 280.7 | 274.8 | 76.2 | 52.1 | 18.4 | 79.3 | 4.6 | 237.5 | 4.4 | 151 | 155.9 | 85.4 | 153 | 118.3 | 97.9 | 83.5 | 57.9 | 86.7 | 62.8 | 259.2 | 326.4 | 382.9 | 385.9 | 343.2 | 298.7 | 363.8 | 351.9 | 490.1 | 392.5
1711 | 1537 | -6.6 | 0 | 0 | 321.3 | 328.6 | 280.6 | 274.3 | 76.6 | 51.9 | 18.4 | 79.1 | 4.6 | 241.9 | 3.8 | 148.7 | 152.2 | 83.9 | 150.1 | 100.8 | 93.2 | 81.5 | 60.1 | 87.1 | 61.3 | 259.3 | 326.3 | 382.6 | 385.8 | 342.6 | 298.3 | 363.3 | 351.4 | 489.5 | 392.3
1712 | 1538 | -6.7 | 0 | 0 | 321 | 328.3 | 280.3 | 273.8 | 76.7 | 51.8 | 18.4 | 79.1 | 4.4 | 222.5 | 3.2 | 146 | 151.3 | 82.4 | 148.8 | 104.7 | 89.2 | 85 | 61.9 | 86.8 | 58.8 | 259.4 | 326.3 | 382.3 | 385.6 | 342.1 | 297.9 | 362.8 | 350.8 | 488.9 | 392.2
1713 | 1539 | -6.7 | 0 | 0 | 320.7 | 327.6 | 280 | 273.5 | 77.3 | 51.7 | 18.4 | 78.9 | 4.7 | 210.2 | 2.8 | 143.4 | 148.7 | 80.8 | 143.2 | 104.4 | 89 | 85.6 | 51.5 | 85.8 | 55.6 | 259.5 | 326.2 | 382 | 385.5 | 341.5 | 297.4 | 362.4 | 350.4 | 488.3 | 392
1714 | 1540 | -6.7 | 0 | 0 | 320.6 | 326.9 | 279.9 | 273.5 | 73.7 | 51.5 | 18.4 | 78.7 | 4.8 | 201.3 | 2.8 | 141.1 | 146.4 | 79.2 | 138.9 | 93.5 | 89 | 88.4 | 50.3 | 84.7 | 51 | 259.7 | 326.1 | 381.6 | 385.3 | 341 | 296.9 | 361.9 | 349.8 | 487.8 | 391.9
1715 | 1541 | -6.7 | 0 | 0 | 320.3 | 325.7 | 279.9 | 273.4 | 76.3 | 51.4 | 18.4 | 78.6 | 4.3 | 213.9 | 2.9 | 138.8 | 144.3 | 77.6 | 134.8 | 76.9 | 90.4 | 89.2 | 52.5 | 83.9 | 48.9 | 259.8 | 326.1 | 381.3 | 385.2 | 340.6 | 296.5 | 361.4 | 349.3 | 487.2 | 391.7
1716 | 1542 | -6.7 | 0 | 0 | 319.7 | 325.1 | 279.5 | 273 | 78.2 | 51.3 | 18.4 | 78.5 | 4.5 | 230.3 | 3 | 136.7 | 145.3 | 75.9 | 131.6 | 73.4 | 92.3 | 88.9 | 54.9 | 82.7 | 48.9 | 259.9 | 326 | 381 | 385 | 340.2 | 296.1 | 361 | 348.7 | 486.6 | 391.5
1717 | 1543 | -6.7 | 0 | 0 | 318.9 | 324.4 | 278.9 | 272.6 | 78.6 | 51.2 | 18.4 | 78.3 | 4.4 | 223.8 | 3 | 134.7 | 145.5 | 74.4 | 129.7 | 71.1 | 90.8 | 86.6 | 56.3 | 82.4 | 48.5 | 260 | 325.9 | 380.6 | 384.8 | 339.8 | 295.7 | 360.6 | 348.2 | 486.1 | 391.4
1718 | 1544 | -6.7 | 0 | 0 | 317.9 | 323.5 | 278.4 | 272.1 | 78 | 51.1 | 18.4 | 78.1 | 4.4 | 214.5 | 3.8 | 132.6 | 144.4 | 72.6 | 128.1 | 69.8 | 87.3 | 84.6 | 56.6 | 82.5 | 47.7 | 260.1 | 325.9 | 380.3 | 384.6 | 339.4 | 295.3 | 360.2 | 347.7 | 485.5 | 391.2
1719 | 1545 | -6.6 | 0 | 0 | 317.3 | 322.8 | 278.5 | 271.7 | 78.9 | 51 | 18.4 | 77.9 | 4.5 | 213.5 | 5.1 | 128 | 143.6 | 71.5 | 126.5 | 73.6 | 90.4 | 83.8 | 58.2 | 83 | 46.9 | 260.2 | 325.8 | 380 | 384.4 | 338.8 | 294.9 | 359.7 | 347.2 | 485 | 391.1
1720 | 1546 | -6.7 | 0 | 0 | 316.6 | 322.4 | 278.3 | 271.3 | 76.5 | 50.8 | 13.6 | 77.7 | 4.6 | 225.7 | 5.3 | 123.5 | 140.2 | 71.2 | 124.5 | 73.7 | 90 | 83.1 | 60.3 | 80.6 | 46.2 | 260.3 | 325.8 | 379.7 | 384.1 | 338.3 | 294.4 | 359.2 | 346.7 | 484.5 | 390.9
1721 | 1547 | -6.7 | 0 | 0 | 315.9 | 322.3 | 277.9 | 271.1 | 75.3 | 50.7 | -12.5 | 77.5 | 4.5 | 237.1 | 5 | 119.9 | 138.4 | 70.1 | 120.9 | 69.9 | 91.2 | 83.2 | 60.6 | 80.5 | 45.4 | 260.4 | 325.7 | 379.4 | 383.9 | 337.6 | 293.9 | 358.7 | 346.1 | 484 | 390.8
1722 | 1548 | -6.7 | 0 | 0 | 315.1 | 322.1 | 277.5 | 270.8 | 74.2 | 50.5 | -12.5 | 77.4 | 4.3 | 234.3 | 4.7 | 116.6 | 137.1 | 69.7 | 118.2 | 70.1 | 87.5 | 85.9 | 57.4 | 78.3 | 45.3 | 260.5 | 325.6 | 379 | 383.7 | 337.1 | 293.4 | 358.2 | 345.6 | 483.5 | 390.6
1723 | 1549 | -6.7 | 0 | 0 | 314.3 | 321.8 | 277.2 | 270.4 | 75.3 | 50.5 | -12.5 | 77.2 | 3.9 | 210.7 | 4.1 | 114.2 | 135.4 | 68.6 | 116.8 | 68.8 | 84.3 | 81.8 | 57.9 | 79.3 | 45 | 260.7 | 325.6 | 378.7 | 383.4 | 336.4 | 293 | 357.6 | 345.1 | 482.9 | 390.4
1724 | 1550 | -6.7 | 0 | 0 | 313.7 | 321.6 | 276.8 | 269.7 | 84.4 | 50.5 | -12.5 | 77.1 | 3.9 | 134.2 | 0.7 | 111.5 | 133.2 | 67.6 | 114.6 | 65.7 | 82.6 | 81.4 | 57.5 | 78 | 45.1 | 260.8 | 325.5 | 378.4 | 383.2 | 335.7 | 292.4 | 357.1 | 344.6 | 482.4 | 390.3
1725 | 1551 | -6.7 | 0 | 0 | 313.2 | 321.4 | 276.4 | 269.2 | 100.3 | 50.4 | -12.5 | 76.9 | 4.2 | 501.2 | 133.1 | 108.9 | 133.3 | 66.8 | 112.5 | 63.9 | 81.8 | 81.5 | 58.3 | 77.7 | 45.4 | 260.9 | 325.4 | 378 | 382.9 | 335.2 | 291.8 | 356.5 | 344.1 | 481.9 | 390.1
1726 | 1552 | -6.7 | 0 | 0 | 313 | 321 | 275.9 | 268.9 | 117.5 | 50.3 | -12.5 | 76.8 | 4.5 | 504 | 140.7 | 107.1 | 128.1 | 66.5 | 112.6 | 61.3 | 76.6 | 81.6 | 58.7 | 76.2 | 45.1 | 261 | 325.4 | 377.7 | 382.6 | 334.9 | 291.3 | 356 | 343.6 | 481.4 | 389.9
1727 | 1553 | -6.7 | 0 | 0 | 312.6 | 320.6 | 275.8 | 268.8 | 133.4 | 50.1 | -12.5 | 76.6 | 4.8 | 355.3 | 99.4 | 105.3 | 125.5 | 65.9 | 113.1 | 60.1 | 76.5 | 82.2 | 51.8 | 75.1 | 44.1 | 261.1 | 325.3 | 377.4 | 382.4 | 334.2 | 290.9 | 355.6 | 343.1 | 480.8 | 389.8
1728 | 1554 | -6.7 | 0 | 0 | 311.9 | 320.2 | 275.5 | 268.9 | 142.9 | 49.9 | -12.5 | 76.4 | 4.3 | 259.9 | 72.9 | 103.7 | 122.8 | 64.7 | 110 | 60 | 75.1 | 80.9 | 52.2 | 74.8 | 44.5 | 261.3 | 325.2 | 377.1 | 382.1 | 333.6 | 290.4 | 355.1 | 342.6 | 480.3 | 389.6
1729 | 1555 | -6.7 | 0 | 0 | 311.3 | 319.3 | 275 | 268.7 | 158.8 | 49.9 | -12.5 | 76.3 | 4.2 | 220.5 | 61.9 | 101.8 | 119.5 | 63.8 | 107.3 | 60.2 | 76.8 | 80.3 | 47.2 | 75.7 | 44.6 | 261.4 | 325.2 | 376.8 | 381.8 | 333 | 290.2 | 354.7 | 342.1 | 479.7 | 389.4
1730 | 1556 | -6.7 | 0 | 0 | 311 | 318.5 | 274.7 | 268.4 | 173.5 | 49.8 | -12.5 | 76.2 | 4.9 | 191.3 | 53.8 | 99.8 | 118.9 | 63.3 | 105.2 | 59.3 | 79.9 | 81.5 | 50.3 | 76.5 | 45 | 261.5 | 325.1 | 376.5 | 381.5 | 332.6 | 289.9 | 354.3 | 341.7 | 479.2 | 389.2
1731 | 1557 | -6.7 | 0 | 0 | 311 | 318 | 274.4 | 268 | 186.1 | 49.6 | -12.5 | 76 | 4.6 | 166.7 | 47 | 97.7 | 118 | 62.9 | 103.6 | 58.1 | 78.9 | 77.3 | 53.3 | 75.4 | 45.4 | 261.6 | 325.1 | 376.2 | 381.2 | 332.2 | 289.5 | 353.9 | 341.1 | 478.7 | 389
1732 | 1558 | -6.7 | 0 | 0 | 310.7 | 317.7 | 274.2 | 267.6 | 197.4 | 49.4 | -12.5 | 75.9 | 4.7 | 146.2 | 41.3 | 95.6 | 117 | 62.2 | 102.8 | 57.3 | 78.7 | 78.3 | 54 | 74.7 | 45.3 | 261.8 | 325 | 375.8 | 380.9 | 331.7 | 289.2 | 353.6 | 340.7 | 478.1 | 388.9
1733 | 1559 | -6.7 | 0 | 0 | 310.2 | 317.4 | 274 | 267.2 | 207.8 | 49.3 | -12.5 | 75.8 | 4.7 | 129.3 | 36.6 | 92.9 | 115.4 | 60.8 | 100.2 | 56.8 | 77.5 | 79 | 51.6 | 75 | 44.2 | 261.9 | 325 | 375.5 | 380.6 | 331.4 | 288.7 | 353.3 | 340.2 | 477.6 | 388.7
1734 | 1560 | -6.7 | 0 | 0 | 309.6 | 316.7 | 273.6 | 266.8 | 214.1 | 49.3 | -12.5 | 75.6 | 4.6 | 115.5 | 32.7 | 90 | 112.7 | 60.3 | 99.1 | 56.3 | 80 | 78.8 | 47.3 | 74.7 | 43.6 | 262 | 324.9 | 375.2 | 380.3 | 331 | 288.3 | 353 | 339.7 | 477.1 | 388.5
1735 | 1561 | -6.7 | 0 | 0 | 309 | 316.6 | 273.4 | 266.5 | 156.2 | 49.2 | -12.5 | 75.4 | 4.9 | 104.2 | 29.6 | 87.6 | 111.2 | 59.8 | 98 | 55.8 | 80.9 | 78 | 50.8 | 74 | 43 | 262.2 | 324.9 | 374.9 | 380 | 330.6 | 287.8 | 352.7 | 339.2 | 476.6 | 388.4
1736 | 1562 | -6.7 | 0 | 0 | 308.6 | 316.4 | 273.5 | 266.1 | 174.4 | 49.2 | -12.5 | 75.3 | 4.8 | 94.7 | 26.9 | 85.6 | 108.4 | 59.7 | 94.5 | 55.1 | 82.1 | 75.4 | 53.1 | 72.5 | 42.2 | 262.4 | 324.8 | 374.6 | 379.7 | 330.2 | 287.3 | 352.4 | 338.7 | 476 | 388.2
1737 | 1563 | -6.7 | 0 | 0 | 308.2 | 315.4 | 273.7 | 265.7 | 192.1 | 49.2 | -12.5 | 75.1 | 4.6 | 86.8 | 24.7 | 83.2 | 107.3 | 59.8 | 92.5 | 54.7 | 80.8 | 76.1 | 55.3 | 72.4 | 41.8 | 262.5 | 324.7 | 374.3 | 379.3 | 329.9 | 286.9 | 352 | 338.2 | 475.5 | 388
1738 | 1564 | -6.7 | 0 | 0 | 307.8 | 314.2 | 273.6 | 265.4 | 205 | 49.3 | -12.5 | 74.9 | 5 | 80 | 22.8 | 80.9 | 106.4 | 58.7 | 91.8 | 54.4 | 75.2 | 74.5 | 57.2 | 73.1 | 41.3 | 262.6 | 324.7 | 373.9 | 379 | 329.5 | 286.5 | 351.5 | 337.8 | 475 | 387.9
1739 | 1565 | -6.7 | 0 | 0 | 307.1 | 313.8 | 273.2 | 265.1 | 209.6 | 49.3 | -12.5 | 74.7 | 4.6 | 74.2 | 21.2 | 78.8 | 103.6 | 57.4 | 90.5 | 54.1 | 73.6 | 76.1 | 58.5 | 73.4 | 40.5 | 262.8 | 324.6 | 373.6 | 378.7 | 328.8 | 286.1 | 351.1 | 337.3 | 474.5 | 387.7
1740 | 1566 | -6.7 | 0 | 0 | 306.5 | 313.5 | 272.9 | 264.8 | 219.3 | 49.4 | -12.5 | 74.5 | 4.4 | 69.3 | 19.9 | 77.1 | 101.3 | 56.5 | 88.2 | 53.8 | 76.6 | 77.3 | 55.4 | 72.5 | 39.2 | 262.9 | 324.6 | 373.3 | 378.4 | 328.4 | 285.7 | 350.6 | 336.8 | 474.1 | 387.5
1741 | 1567 | -6.7 | 0 | 0 | 306.2 | 313.1 | 272.4 | 264.5 | 228.1 | 49.4 | -12.5 | 74.3 | 4.8 | 65 | 18.7 | 75.6 | 99.5 | 56.3 | 86.2 | 53.6 | 79.5 | 77.2 | 56.8 | 70.2 | 38.8 | 263.1 | 324.5 | 373.1 | 378.1 | 328 | 285.2 | 350.1 | 336.3 | 473.6 | 387.3
1742 | 1568 | -6.7 | 0 | 0 | 306 | 312.5 | 271.9 | 264.1 | 235.6 | 49.4 | -12.5 | 74.1 | 5.1 | 61.3 | 17.6 | 74.2 | 99.3 | 55.8 | 85.1 | 53.7 | 80.3 | 75.8 | 55.1 | 69.7 | 39.2 | 263.2 | 324.4 | 372.8 | 377.8 | 327.6 | 284.7 | 349.8 | 335.9 | 473.1 | 387.2
1743 | 1569 | -6.7 | 0 | 0 | 305.6 | 312.2 | 271.7 | 263.7 | 241.9 | 49.3 | -12.5 | 73.9 | 5.4 | 58 | 16.7 | 73 | 98.2 | 54.8 | 84.7 | 53.8 | 77.5 | 75.3 | 50.7 | 69.5 | 39.5 | 263.4 | 324.4 | 372.4 | 377.4 | 327 | 284.1 | 349.5 | 335.4 | 472.6 | 387
1744 | 1570 | -6.7 | 0 | 0 | 305.2 | 311.7 | 271.7 | 263.2 | 247.2 | 49.2 | -12.5 | 73.8 | 5.2 | 55.2 | 15.9 | 71.9 | 96.1 | 54.4 | 84 | 53.8 | 76.7 | 73.8 | 50.1 | 69.1 | 39.5 | 263.5 | 324.3 | 372.2 | 377.1 | 326.5 | 283.7 | 349.2 | 334.9 | 472 | 386.8
1745 | 1571 | -6.7 | 0 | 0 | 304.8 | 311 | 271.4 | 262.6 | 251.5 | 49 | -12.5 | 73.7 | 4.7 | 52.6 | 15.2 | 70.5 | 93.4 | 53.7 | 81.9 | 53.7 | 74.4 | 75 | 43.7 | 67.9 | 39.1 | 263.7 | 324.2 | 371.8 | 376.8 | 325.9 | 283.3 | 348.8 | 334.5 | 471.6 | 386.6
1746 | 1572 | -6.7 | 0 | 0 | 304.3 | 310.5 | 270.8 | 262.1 | 255.1 | 48.8 | -12.5 | 73.6 | 4.5 | 50.3 | 14.6 | 68.9 | 92.2 | 52.7 | 80.2 | 53.4 | 72.3 | 76.8 | 45.6 | 67.4 | 39.4 | 263.8 | 324.1 | 371.5 | 376.5 | 325.4 | 282.8 | 348.5 | 334 | 471.1 | 386.4
1747 | 1573 | -6.7 | 0 | 0 | 303.7 | 309.9 | 270.5 | 261.7 | 258 | 48.6 | -12.5 | 73.5 | 4.4 | 48.2 | 14 | 67.2 | 91.6 | 51.6 | 78.4 | 53.4 | 72 | 79.9 | 46.7 | 67.2 | 39.7 | 264 | 324.1 | 371.2 | 376.1 | 325 | 282.3 | 348.1 | 333.5 | 470.6 | 386.3
1748 | 1574 | -6.7 | 0 | 0 | 303.2 | 309.2 | 270.3 | 261.4 | 260.8 | 48.4 | -12.5 | 73.3 | 4.2 | 46.4 | 13.5 | 65.5 | 90.7 | 50.1 | 77.7 | 53.3 | 72.4 | 78.4 | 39 | 66.9 | 39.7 | 264.1 | 324 | 370.9 | 375.8 | 324.5 | 281.8 | 347.7 | 333 | 470.1 | 386.1
1749 | 1575 | -6.7 | 0 | 0 | 302.7 | 308.5 | 270 | 261 | 263.4 | 48.2 | -12.5 | 73.1 | 4 | 44.7 | 13 | 64.2 | 90.6 | 48.8 | 77.7 | 53.4 | 71.3 | 75.2 | 42.7 | 66 | 39.4 | 264.3 | 323.9 | 370.6 | 375.5 | 324 | 281.2 | 347.2 | 332.5 | 469.6 | 385.9
1750 | 1576 | -6.7 | 0 | 0 | 302.1 | 307.8 | 269.9 | 260.5 | 265.7 | 48.1 | -12.5 | 73 | 3.5 | 43.1 | 12.6 | 63.2 | 89.5 | 48.2 | 77.9 | 53.5 | 72.6 | 74.8 | 45.1 | 65.8 | 39.5 | 264.4 | 323.8 | 370.3 | 375.1 | 323.5 | 280.7 | 346.8 | 332.1 | 469.1 | 385.7
1751 | 1577 | -6.7 | 0 | 0 | 301.6 | 307.2 | 269.5 | 260.1 | 267.8 | 48.1 | -12.5 | 72.9 | 4.1 | 41.7 | 12.2 | 62.1 | 88.2 | 48.2 | 77.1 | 53 | 72.4 | 74.2 | 49 | 65.8 | 39.2 | 264.5 | 323.8 | 370 | 374.8 | 323.1 | 280.2 | 346.5 | 331.6 | 468.6 | 385.5
1752 | 1578 | -6.7 | 0 | 0 | 301 | 306.5 | 269.1 | 259.7 | 269.9 | 48 | -12.5 | 72.7 | 3.8 | 40.4 | 11.8 | 61 | 86.9 | 51.9 | 77.2 | 52.9 | 73 | 78 | 44.1 | 66.3 | 39.1 | 264.6 | 323.7 | 369.7 | 374.5 | 322.5 | 279.7 | 346 | 331.2 | 468.1 | 385.4
1753 | 1579 | -6.7 | 0 | 0 | 300.5 | 306 | 268.5 | 259.4 | 271.7 | 47.8 | -12.5 | 72.6 | 3.8 | 39.2 | 11.5 | 60.3 | 86.2 | 52.1 | 76.9 | 53 | 74.3 | 78.1 | 45.2 | 65.4 | 39.1 | 264.8 | 323.6 | 369.4 | 374.1 | 322.1 | 279.3 | 345.6 | 330.7 | 467.6 | 385.2
1754 | 1580 | -6.7 | 0 | 0 | 300.1 | 305.6 | 268 | 259 | 273.4 | 47.7 | -12.5 | 72.5 | 4.2 | 38 | 11.1 | 59.4 | 86.1 | 51 | 76.1 | 52.6 | 74.2 | 74.9 | 46.5 | 66.2 | 38.8 | 264.9 | 323.6 | 369.1 | 373.8 | 321.6 | 278.9 | 345.3 | 330.2 | 467.1 | 385
1755 | 1581 | -6.7 | 0 | 0 | 299.8 | 305 | 267.6 | 258.6 | 273.7 | 47.6 | -12.5 | 72.3 | 4.2 | 37 | 10.8 | 59.2 | 85.8 | 50.3 | 75.3 | 52.1 | 73.7 | 75.3 | 44.6 | 66.5 | 39.1 | 265 | 323.5 | 368.8 | 373.5 | 321.1 | 278.4 | 344.8 | 329.7 | 466.7 | 384.8
1756 | 1582 | -6.7 | 0 | 0 | 299.4 | 304.5 | 267.2 | 258.2 | 275.1 | 47.5 | -12.5 | 72.2 | 4.6 | 36 | 10.6 | 58.3 | 84.8 | 49.9 | 74 | 51.9 | 71.3 | 77.1 | 46.9 | 64.3 | 39.4 | 265.2 | 323.5 | 368.5 | 373.1 | 320.4 | 277.9 | 344.4 | 329.3 | 466.2 | 384.6
1757 | 1583 | -6.7 | 0 | 0 | 299.1 | 303.9 | 266.9 | 257.9 | 276.4 | 47.4 | -12.5 | 72 | 4.7 | 35.1 | 10.3 | 57.7 | 83.7 | 49.4 | 72.7 | 51.7 | 70.5 | 75 | 47.1 | 63.3 | 39.8 | 265.3 | 323.4 | 368.2 | 372.8 | 319.7 | 277.5 | 344.1 | 328.8 | 465.7 | 384.4
1758 | 1584 | -6.7 | 0 | 0 | 298.8 | 303.1 | 266.7 | 257.6 | 277.2 | 47.3 | -12.5 | 71.9 | 4.7 | 34.3 | 10.1 | 57.1 | 83.8 | 48.8 | 71.1 | 51.5 | 72.4 | 77.1 | 48.5 | 64 | 39.6 | 265.4 | 323.3 | 367.9 | 372.5 | 319.1 | 277 | 343.7 | 328.4 | 465.2 | 384.3
1759 | 1585 | -6.7 | 0 | 0 | 298.3 | 302.4 | 266.4 | 257.2 | 277.7 | 47.2 | -12.5 | 71.8 | 4.4 | 33.5 | 9.9 | 56.1 | 83.5 | 48.1 | 70.2 | 51.6 | 73.7 | 75.1 | 51.8 | 64.5 | 39.1 | 265.6 | 323.3 | 367.6 | 372.1 | 318.6 | 276.5 | 343.2 | 327.9 | 464.8 | 384.1
1760 | 1586 | -6.7 | 0 | 0 | 297.9 | 301.9 | 266 | 256.7 | 278.6 | 47 | -12.5 | 71.7 | 4.8 | 32.7 | 9.6 | 55.1 | 81.2 | 47.7 | 68.5 | 51.3 | 71.7 | 76.8 | 53.4 | 61.9 | 38.4 | 265.7 | 323.2 | 367.3 | 371.7 | 318.2 | 276 | 342.8 | 327.4 | 464.3 | 383.9
1761 | 1587 | -6.7 | 0 | 0 | 297.4 | 301.5 | 265.7 | 256.4 | 279.5 | 47 | -12.5 | 71.6 | 5 | 32 | 9.4 | 53.9 | 80.6 | 47.2 | 67.3 | 51 | 69.7 | 75.3 | 50.3 | 61.1 | 38.4 | 265.8 | 323.1 | 367 | 371.4 | 317.8 | 275.5 | 342.4 | 327 | 463.8 | 383.7
1762 | 1588 | -6.7 | 0 | 0 | 296.9 | 300.9 | 265.4 | 256.1 | 280.2 | 46.9 | -12.5 | 71.5 | 4.7 | 31.3 | 9.3 | 53.1 | 81 | 46.5 | 67 | 50.8 | 67.9 | 74.3 | 41.2 | 60.5 | 38.5 | 266 | 323 | 366.7 | 371.1 | 317.2 | 275.1 | 342.1 | 326.5 | 463.3 | 383.5
1763 | 1589 | -6.7 | 0 | 0 | 296.6 | 300.2 | 265.2 | 255.7 | 280.1 | 46.8 | -12.5 | 71.4 | 4.6 | 30.7 | 9.1 | 52.3 | 81.2 | 46.1 | 65.9 | 50.8 | 70.2 | 75.5 | 41.1 | 59 | 38 | 266.1 | 323 | 366.4 | 370.7 | 316.6 | 274.7 | 341.7 | 326 | 462.9 | 383.3
1764 | 1590 | -6.7 | 0 | 0 | 296.1 | 299.8 | 264.9 | 255.3 | 278.7 | 46.8 | -12.5 | 71.2 | 4.7 | 30.1 | 8.9 | 51.5 | 80.6 | 45.7 | 65.1 | 50.8 | 69.3 | 75.1 | 43.3 | 58.6 | 37.7 | 266.3 | 322.9 | 366.1 | 370.4 | 316.1 | 274.2 | 341.2 | 325.6 | 462.4 | 383.1
1765 | 1591 | -6.7 | 0 | 0 | 295.5 | 299.4 | 264.6 | 255 | 277.7 | 46.7 | -12.5 | 71.1 | 4.2 | 29.5 | 8.7 | 50.9 | 81 | 45.5 | 63.9 | 50.7 | 74 | 73 | 45.1 | 59 | 37.7 | 266.4 | 322.8 | 365.8 | 370 | 315.5 | 273.8 | 340.9 | 325.1 | 461.9 | 382.9
1766 | 1592 | -6.7 | 0 | 0 | 294.9 | 299 | 264.3 | 254.6 | 277.4 | 46.6 | -12.5 | 71 | 4.2 | 28.9 | 8.6 | 50.3 | 80 | 45.3 | 62.6 | 50.6 | 75.5 | 69.9 | 47.5 | 59 | 38 | 266.5 | 322.7 | 365.5 | 369.7 | 315 | 273.4 | 340.5 | 324.7 | 461.4 | 382.7
1767 | 1593 | -6.7 | 0 | 0 | 294.7 | 298 | 264 | 254.4 | 277.6 | 46.5 | -12.5 | 70.8 | 4.1 | 28.4 | 8.4 | 49.4 | 77.6 | 45.2 | 61.6 | 50.7 | 76.8 | 69 | 49.3 | 59.1 | 38.2 | 266.6 | 322.7 | 365.2 | 369.3 | 314.6 | 273 | 340.2 | 324.2 | 461 | 382.5
1768 | 1594 | -6.7 | 0 | 0 | 294.5 | 296.9 | 263.8 | 254.1 | 278.1 | 46.5 | -12.5 | 70.7 | 3.9 | 27.9 | 8.3 | 48.7 | 77.2 | 45.1 | 61.2 | 50.6 | 79.9 | 69.3 | 50.8 | 60.1 | 39 | 266.7 | 322.6 | 364.9 | 369 | 314.2 | 272.5 | 339.8 | 323.8 | 460.5 | 382.3
1769 | 1595 | -6.7 | 0 | 0 | 294.3 | 296.6 | 263.5 | 253.8 | 278.6 | 46.4 | -12.5 | 70.6 | 3.8 | 27.4 | 8.2 | 48.2 | 76.7 | 44.9 | 60.3 | 50.3 | 81.8 | 70.1 | 52.5 | 61 | 39.9 | 266.9 | 322.6 | 364.7 | 368.6 | 313.5 | 272.1 | 339.5 | 323.4 | 460.1 | 382.2
1770 | 1596 | -6.7 | 0 | 0 | 294 | 296.2 | 263.2 | 253.6 | 279.2 | 46.3 | -12.5 | 70.4 | 3.8 | 27 | 8 | 47.8 | 76.8 | 44.9 | 59.7 | 50.1 | 83.7 | 70.5 | 54 | 62.3 | 40.7 | 267 | 322.5 | 364.4 | 368.3 | 313 | 271.8 | 339.1 | 323 | 459.6 | 382
1771 | 1597 | -6.7 | 0 | 0 | 293.7 | 295.6 | 262.8 | 253.2 | 279.8 | 46.2 | -12.5 | 70.3 | 3.8 | 26.5 | 7.9 | 47.5 | 76.9 | 44.7 | 59.6 | 49.9 | 85.5 | 70.3 | 55.1 | 63.1 | 41.4 | 267.1 | 322.4 | 364.1 | 368 | 312.6 | 271.4 | 338.8 | 322.5 | 459.1 | 381.8
1772 | 1598 | -6.7 | 0 | 0 | 293.2 | 295.3 | 262.5 | 252.8 | 280.5 | 46.1 | -12.5 | 70.1 | 4.1 | 26.1 | 7.8 | 47.3 | 77.1 | 44.6 | 59.5 | 49.8 | 86.5 | 69.9 | 56.1 | 63.9 | 42 | 267.3 | 322.3 | 363.8 | 367.6 | 311.8 | 271.1 | 338.4 | 322.1 | 458.7 | 381.6
1773 | 1599 | -6.7 | 0 | 0 | 292.9 | 294.7 | 262.3 | 252.6 | 281.2 | 46.1 | -12.5 | 70 | 4 | 25.7 | 7.7 | 47.1 | 77.4 | 44.1 | 58.9 | 49.7 | 87.5 | 70 | 56.9 | 64.9 | 42.5 | 267.4 | 322.3 | 363.5 | 367.3 | 311.1 | 270.7 | 338 | 321.6 | 458.2 | 381.3
1774 | 1600 | -6.7 | 0 | 0 | 292.8 | 294.5 | 262.1 | 252.3 | 281.7 | 46.1 | -12.5 | 70 | 4.3 | 25.3 | 7.6 | 47.1 | 77.5 | 43.2 | 58.4 | 49.6 | 88.4 | 70.6 | 57.5 | 66.1 | 43.1 | 267.5 | 322.2 | 363.2 | 366.9 | 310.6 | 270.4 | 337.6 | 321.2 | 457.7 | 381.2
1775 | 1601 | -6.7 | 0 | 0 | 292.8 | 294.1 | 261.9 | 252.1 | 282.2 | 46.2 | -12.5 | 69.8 | 4.1 | 24.9 | 7.5 | 46.9 | 77.2 | 43 | 58.3 | 49.3 | 89.4 | 71.3 | 57.8 | 66.9 | 43.7 | 267.6 | 322.2 | 362.9 | 366.6 | 310.2 | 270 | 337.3 | 320.8 | 457.3 | 381
1776 | 1602 | -6.7 | 0 | 0 | 292.7 | 293.6 | 261.7 | 251.8 | 282.7 | 46.2 | -12.5 | 69.7 | 4.3 | 24.5 | 7.3 | 46.8 | 77 | 42.8 | 58.2 | 49.1 | 90 | 71.1 | 58.4 | 67.9 | 44.3 | 267.8 | 322.1 | 362.7 | 366.2 | 309.6 | 269.6 | 336.8 | 320.3 | 456.8 | 380.8
1777 | 1603 | -6.7 | 0 | 0 | 292.5 | 292.8 | 261.4 | 251.5 | 283.2 | 46.1 | -12.5 | 69.6 | 3.9 | 24.2 | 7.2 | 46.7 | 76.9 | 42.6 | 57.5 | 48.9 | 90.4 | 70.1 | 58.4 | 68.8 | 44.9 | 267.9 | 322 | 362.4 | 365.9 | 309.1 | 269.2 | 336.5 | 319.9 | 456.4 | 380.6
1778 | 1604 | -6.7 | 0 | 0 | 292.5 | 292.2 | 261 | 251.3 | 283.7 | 46.2 | -12.5 | 69.4 | 4.3 | 23.8 | 7.2 | 46.6 | 75.5 | 42.4 | 57.5 | 48.7 | 90.9 | 70 | 58.6 | 69.5 | 45.3 | 268 | 322 | 362.1 | 365.5 | 308.4 | 268.8 | 336.1 | 319.5 | 455.9 | 380.4
1779 | 1605 | -6.7 | 0 | 0 | 292.3 | 292.1 | 260.8 | 251.1 | 284.1 | 46.2 | -12.5 | 69.3 | 4.2 | 23.5 | 7.1 | 46.6 | 74.9 | 42.4 | 57.6 | 48.6 | 90.9 | 69.3 | 58.5 | 70.2 | 45.8 | 268.1 | 321.9 | 361.8 | 365.2 | 307.9 | 268.4 | 335.7 | 319.1 | 455.5 | 380.2
1780 | 1606 | -6.7 | 0 | 0 | 291.9 | 292.3 | 260.6 | 251 | 284.5 | 46.2 | -12.5 | 69.2 | 4 | 23.2 | 7 | 46.5 | 74.8 | 42.3 | 57.4 | 48.4 | 90.8 | 69.1 | 58.3 | 70.6 | 46.3 | 268.2 | 321.8 | 361.5 | 364.8 | 307.4 | 268 | 335.4 | 318.6 | 455 | 380
1781 | 1607 | -6.7 | 0 | 0 | 291.7 | 292 | 260.3 | 250.8 | 284.8 | 46.2 | -12.5 | 69.2 | 3.8 | 22.9 | 6.9 | 46.4 | 74.7 | 42.3 | 57.3 | 48.3 | 90.9 | 69.6 | 57.9 | 70.9 | 46.7 | 268.4 | 321.7 | 361.2 | 364.5 | 306.9 | 267.6 | 335.1 | 318.2 | 454.6 | 379.8
1782 | 1608 | -6.7 | 0 | 0 | 291.7 | 291.5 | 260 | 250.5 | 285.1 | 46 | -12.5 | 69.1 | 4 | 22.6 | 6.8 | 46.4 | 74 | 42.4 | 57.1 | 48.1 | 90.7 | 71.2 | 58.1 | 71.2 | 47.1 | 268.5 | 321.7 | 360.9 | 364.1 | 306.4 | 267.2 | 334.8 | 317.8 | 454.1 | 379.6
1783 | 1609 | -6.7 | 0 | 0 | 291.5 | 291.7 | 259.8 | 250.3 | 285.3 | 45.8 | -12.5 | 69 | 3.8 | 22.3 | 6.7 | 46.4 | 73.9 | 42.4 | 56.8 | 47.8 | 91.2 | 71.1 | 58.3 | 71.5 | 47.5 | 268.5 | 321.6 | 360.6 | 363.7 | 305.8 | 266.9 | 334.4 | 317.4 | 453.6 | 379.4
1784 | 1610 | -6.7 | 0 | 0 | 291.3 | 291.8 | 259.5 | 249.9 | 285.4 | 45.7 | -12.5 | 68.9 | 3.8 | 22 | 6.6 | 46.4 | 73.9 | 42.5 | 56.9 | 47.7 | 91.7 | 70.9 | 58.3 | 72 | 47.9 | 268.6 | 321.5 | 360.3 | 363.4 | 305.2 | 266.5 | 334 | 316.9 | 453.2 | 379.2
1785 | 1611 | -6.6 | 0 | 0 | 291.2 | 291.3 | 259.2 | 249.6 | 285.4 | 45.7 | -12.5 | 68.8 | 4.1 | 21.8 | 6.6 | 46.4 | 74.1 | 42.5 | 57.3 | 47.5 | 91.6 | 69.6 | 58.5 | 72.2 | 48.3 | 268.7 | 321.5 | 360 | 363.1 | 304.6 | 266 | 333.7 | 316.5 | 452.7 | 379
1786 | 1612 | -6.6 | 0 | 0 | 291 | 290.8 | 259 | 249.4 | 285.6 | 45.7 | -12.5 | 68.7 | 3.9 | 21.5 | 6.5 | 46.3 | 74.6 | 42.4 | 57.5 | 47.2 | 90.8 | 69.1 | 58.5 | 72.1 | 48.7 | 268.8 | 321.4 | 359.7 | 362.7 | 304.2 | 265.6 | 333.3 | 316.1 | 452.3 | 378.8
1787 | 1613 | -6.7 | 0 | 0 | 290.9 | 290.5 | 258.8 | 249.2 | 285.6 | 45.8 | -12.5 | 68.6 | 3.7 | 21.2 | 6.4 | 46.3 | 75 | 42.4 | 57.3 | 47 | 91.2 | 68.7 | 58.8 | 72.2 | 49.3 | 268.9 | 321.3 | 359.5 | 362.4 | 303.8 | 265.2 | 332.9 | 315.7 | 451.9 | 378.6
1788 | 1614 | -6.7 | 0 | 0 | 290.7 | 290.4 | 258.5 | 249 | 285.7 | 45.8 | -12.5 | 68.5 | 3.7 | 21 | 6.3 | 46.3 | 74.7 | 42.4 | 56.9 | 46.9 | 91.3 | 68.4 | 58.7 | 72.2 | 49.7 | 269 | 321.2 | 359.2 | 362 | 303.3 | 264.9 | 332.6 | 315.3 | 451.4 | 378.4
1789 | 1615 | -6.6 | 0 | 0 | 290.5 | 290.2 | 258.3 | 248.7 | 285.8 | 45.9 | -12.5 | 68.4 | 4 | 20.7 | 6.3 | 46.2 | 73.7 | 42.4 | 56.3 | 46.8 | 90.4 | 68.3 | 58.5 | 72.1 | 50.1 | 269.1 | 321.2 | 358.9 | 361.7 | 303 | 264.5 | 332.2 | 314.9 | 451 | 378.2
1790 | 1616 | -6.6 | 0 | 0 | 290.3 | 289.9 | 258.2 | 248.5 | 285.8 | 45.9 | -12.5 | 68.3 | 4.1 | 20.5 | 6.2 | 46.2 | 73.2 | 42.3 | 56.1 | 46.7 | 90.2 | 68.4 | 58.5 | 72.4 | 50.3 | 269.2 | 321.1 | 358.6 | 361.4 | 302.5 | 264.2 | 331.8 | 314.4 | 450.5 | 377.9
1791 | 1617 | -6.6 | 0 | 0 | 290 | 289.6 | 258 | 248.3 | 285.8 | 45.8 | -12.5 | 68.2 | 4.1 | 20.3 | 6.1 | 46.2 | 73.3 | 42.1 | 56.8 | 46.6 | 90.2 | 68.5 | 58.5 | 72.5 | 50.6 | 269.3 | 321 | 358.3 | 361 | 302.2 | 263.8 | 331.5 | 314 | 450.1 | 377.7
1792 | 1618 | -6.6 | 0 | 0 | 289.7 | 289.2 | 257.7 | 248 | 285.7 | 45.7 | -12.5 | 68.1 | 3.9 | 20.1 | 6.1 | 46.1 | 73.9 | 42.2 | 56.9 | 46.4 | 90.1 | 69.1 | 58.6 | 72.6 | 51.1 | 269.4 | 320.9 | 358 | 360.7 | 301.7 | 263.5 | 331.2 | 313.6 | 449.6 | 377.5
1793 | 1619 | -6.6 | 0 | 0 | 289.4 | 289 | 257.5 | 247.8 | 285.6 | 45.6 | -12.5 | 68 | 3.6 | 19.8 | 6 | 46.1 | 73.8 | 42.1 | 57.1 | 46.3 | 90.2 | 67.9 | 58.5 | 72.6 | 51.4 | 269.5 | 320.9 | 357.7 | 360.4 | 301.2 | 263.2 | 330.9 | 313.2 | 449.2 | 377.3
1794 | 1620 | -6.6 | 0 | 0 | 289.2 | 288.8 | 257.2 | 247.6 | 285.3 | 45.4 | -12.5 | 67.9 | 3.8 | 19.6 | 6 | 46.2 | 73.7 | 42 | 57.3 | 46.1 | 90.1 | 67.1 | 58.5 | 72.6 | 51.8 | 269.6 | 320.8 | 357.4 | 360 | 300.7 | 262.8 | 330.6 | 312.8 | 448.7 | 377.1
1795 | 1621 | -6.6 | 0 | 0 | 289.1 | 288.3 | 256.9 | 247.3 | 285.1 | 45.3 | -12.5 | 67.8 | 4.4 | 19.4 | 5.9 | 46.2 | 73.6 | 42.1 | 57.6 | 46 | 89.6 | 66.6 | 58.6 | 72.7 | 52.1 | 269.7 | 320.7 | 357.2 | 359.7 | 300.3 | 262.4 | 330.2 | 312.5 | 448.3 | 376.9
1796 | 1622 | -6.6 | 0 | 0 | 289 | 287.8 | 256.6 | 247.1 | 284.8 | 45.2 | -12.5 | 67.7 | 4.1 | 19.2 | 5.8 | 46.2 | 73 | 41.9 | 57.5 | 45.8 | 88.9 | 66.2 | 59.2 | 72.9 | 52.4 | 269.8 | 320.6 | 356.9 | 359.4 | 300.1 | 262 | 329.8 | 312 | 447.9 | 376.7
1797 | 1623 | -6.6 | 0 | 0 | 288.9 | 287.4 | 256.4 | 246.8 | 284.6 | 45.1 | -12.5 | 67.6 | 4.1 | 19 | 5.8 | 46.1 | 73.3 | 41.7 | 57.7 | 45.6 | 88.6 | 66.1 | 59.2 | 73 | 52.7 | 270 | 320.6 | 356.6 | 359 | 300.1 | 261.6 | 329.5 | 311.6 | 447.4 | 376.5
1798 | 1624 | -6.7 | 0 | 0 | 288.8 | 287.1 | 256.1 | 246.5 | 284.3 | 45 | -12.5 | 67.4 | 4.1 | 18.8 | 5.7 | 46.1 | 73.6 | 41.6 | 58 | 45.5 | 88.1 | 67.5 | 59.4 | 73 | 53 | 270.1 | 320.5 | 356.3 | 358.7 | 299.8 | 261.2 | 329.2 | 311.2 | 447 | 376.3
1799 | 1625 | -6.7 | 0 | 0 | 288.5 | 286.7 | 255.8 | 246.2 | 284 | 44.9 | -12.5 | 67.2 | 4.5 | 18.6 | 5.7 | 46.2 | 73.7 | 41.4 | 58.1 | 45.5 | 88 | 68.3 | 59.8 | 73 | 53.4 | 270.2 | 320.4 | 356.1 | 358.4 | 299.4 | 260.8 | 328.9 | 310.8 | 446.6 | 376.1
1800 | 1626 | -6.7 | 0 | 0 | 288 | 286.5 | 255.6 | 246 | 283.7 | 44.8 | -12.5 | 67.1 | 4.1 | 18.4 | 5.6 | 46.2 | 73.4 | 41.1 | 58.1 | 45.4 | 87.8 | 68.9 | 60 | 72.7 | 53.8 | 270.3 | 320.4 | 355.8 | 358.1 | 299 | 260.4 | 328.5 | 310.4 | 446.1 | 375.9
1801 | 1627 | -6.7 | 0 | 0 | 287.6 | 286.3 | 255.3 | 245.7 | 283.2 | 44.7 | -12.5 | 66.9 | 3.8 | 18.3 | 5.6 | 46.2 | 73.3 | 41.3 | 58.1 | 45.3 | 87.5 | 67.6 | 59.8 | 72.6 | 54.1 | 270.4 | 320.3 | 355.5 | 357.7 | 298.7 | 260 | 328.1 | 310 | 445.7 | 375.7
1802 | 1628 | -6.7 | 0 | 0 | 287.2 | 286.1 | 255.1 | 245.5 | 282.8 | 44.5 | -12.5 | 66.9 | 4.3 | 18.1 | 5.5 | 46.2 | 73 | 41.4 | 57.9 | 45.2 | 87.4 | 66.7 | 59.7 | 72.5 | 54.4 | 270.5 | 320.2 | 355.2 | 357.4 | 298.5 | 259.6 | 327.8 | 309.6 | 445.2 | 375.5
1803 | 1629 | -6.7 | 0 | 0 | 286.8 | 285.7 | 254.9 | 245.2 | 282.5 | 44.3 | -12.5 | 66.9 | 3.7 | 17.9 | 5.5 | 46.2 | 73.6 | 41.6 | 57.6 | 45 | 87.1 | 66.4 | 59.5 | 72.4 | 54.7 | 270.6 | 320.1 | 354.9 | 357.1 | 298.3 | 259.3 | 327.6 | 309.3 | 444.8 | 375.3
1804 | 1630 | -6.7 | 0 | 0 | 286.3 | 285.3 | 254.6 | 245 | 282.3 | 44.2 | -12.5 | 66.8 | 3.9 | 17.7 | 5.4 | 46.2 | 74 | 41.6 | 57.7 | 44.9 | 86.8 | 66.1 | 58.3 | 72.4 | 55 | 270.7 | 320.1 | 354.7 | 356.8 | 298 | 259 | 327.2 | 308.8 | 444.4 | 375
1805 | 1631 | -6.6 | 0 | 0 | 286.1 | 284.9 | 254.4 | 244.6 | 282.3 | 44.2 | -12.5 | 66.6 | 3.7 | 17.6 | 5.4 | 46.3 | 74.1 | 41.8 | 57.6 | 44.7 | 86.4 | 65.2 | 57.1 | 72.4 | 55.3 | 270.8 | 320 | 354.4 | 356.5 | 297.7 | 258.7 | 326.9 | 308.5 | 443.9 | 374.8
1806 | 1632 | -6.6 | 0 | 0 | 286 | 284.4 | 254.1 | 244.3 | 282.2 | 44.2 | -12.5 | 66.6 | 3.8 | 17.4 | 5.3 | 46.3 | 72.9 | 42 | 57.7 | 44.6 | 86.2 | 64.7 | 56.6 | 72.6 | 55.7 | 271 | 319.9 | 354.1 | 356.2 | 297.4 | 258.4 | 326.6 | 308.1 | 443.5 | 374.6
1807 | 1633 | -6.6 | 0 | 0 | 285.8 | 283.8 | 253.9 | 244.1 | 281.8 | 44.1 | -12.5 | 66.5 | 3.9 | 17.2 | 5.3 | 46.4 | 72 | 42.1 | 57.1 | 44.4 | 86.4 | 65.3 | 56.2 | 72.7 | 55.9 | 271.1 | 319.9 | 353.8 | 355.8 | 297.2 | 258 | 326.3 | 307.7 | 443.1 | 374.4
1808 | 1634 | -6.6 | 0 | 0 | 285.7 | 283.3 | 253.7 | 243.8 | 281.6 | 44 | -12.5 | 66.3 | 4.1 | 17.1 | 5.2 | 46.4 | 71.3 | 42.3 | 56.4 | 44.3 | 86.5 | 65.6 | 55.2 | 72.7 | 56.1 | 271.2 | 319.8 | 353.6 | 355.5 | 296.9 | 257.7 | 325.9 | 307.3 | 442.6 | 374.2
1809 | 1635 | -6.6 | 0 | 0 | 285.4 | 283.3 | 253.5 | 243.6 | 281.5 | 43.8 | -12.5 | 66.2 | 4.1 | 17 | 5.2 | 46.5 | 71 | 42.4 | 56.4 | 44.2 | 86.3 | 66.9 | 54.3 | 72.6 | 56.3 | 271.3 | 319.7 | 353.3 | 355.2 | 296.5 | 257.4 | 325.6 | 306.9 | 442.2 | 374
1810 | 1636 | -6.7 | 0 | 0 | 284.9 | 283 | 253.2 | 243.2 | 281.2 | 43.6 | -12.5 | 66.1 | 3.8 | 16.8 | 5.1 | 46.5 | 71.8 | 42.4 | 56.3 | 44.1 | 86.3 | 67 | 53.9 | 72.9 | 56.5 | 271.4 | 319.6 | 353 | 354.9 | 296 | 257.2 | 325.4 | 306.5 | 441.8 | 373.8
1811 | 1637 | -6.7 | 0 | 0 | 284.8 | 282.7 | 252.9 | 243 | 281 | 43.5 | -12.5 | 66.1 | 4.3 | 16.6 | 5.1 | 46.6 | 71.4 | 42.6 | 56.5 | 44 | 86.1 | 66.3 | 53.6 | 72.8 | 56.7 | 271.5 | 319.6 | 352.7 | 354.6 | 295.4 | 256.9 | 325 | 306.1 | 441.4 | 373.6
1812 | 1638 | -6.6 | 0 | 0 | 284.6 | 282.6 | 252.7 | 242.7 | 280.8 | 43.4 | -12.5 | 66 | 3.6 | 16.5 | 5.1 | 46.6 | 71.7 | 42.7 | 56.6 | 43.9 | 85.8 | 66.5 | 53.9 | 72.6 | 56.9 | 271.6 | 319.5 | 352.5 | 354.3 | 295.1 | 256.5 | 324.6 | 305.7 | 441 | 373.4
1813 | 1639 | -6.6 | 0 | 0 | 284.4 | 282.4 | 252.4 | 242.5 | 280.5 | 43.3 | -12.5 | 65.9 | 4.3 | 16.4 | 5 | 46.7 | 71.8 | 42.9 | 56.8 | 43.9 | 85.8 | 67 | 53.6 | 72.5 | 57.1 | 271.8 | 319.4 | 352.2 | 353.9 | 294.7 | 256.1 | 324.3 | 305.3 | 440.5 | 373.1
1814 | 1640 | -6.6 | 0 | 0 | 284.1 | 282.1 | 252.2 | 242.3 | 280.2 | 43.2 | -12.5 | 65.9 | 4.6 | 16.2 | 5 | 46.7 | 71.4 | 42.9 | 57.1 | 43.9 | 85.8 | 66.3 | 53.3 | 72.5 | 57.3 | 271.9 | 319.4 | 351.9 | 353.6 | 294.4 | 255.8 | 323.9 | 304.9 | 440.1 | 372.9
1815 | 1641 | -6.6 | 0 | 0 | 283.9 | 281.8 | 251.9 | 242 | 279.9 | 43.1 | -12.5 | 65.8 | 4.4 | 16.1 | 5 | 46.8 | 71 | 43 | 56.8 | 43.8 | 86 | 66 | 52.7 | 72.5 | 57.5 | 272 | 319.3 | 351.7 | 353.3 | 294.2 | 255.4 | 323.6 | 304.5 | 439.7 | 372.7
1816 | 1642 | -6.6 | 0 | 0 | 283.6 | 281.4 | 251.6 | 241.7 | 279.6 | 43 | -12.5 | 65.7 | 4.2 | 15.9 | 4.9 | 46.8 | 71 | 43 | 57.2 | 43.6 | 85.3 | 65.9 | 52.4 | 72.1 | 57.6 | 272.1 | 319.2 | 351.4 | 353 | 293.9 | 255 | 323.3 | 304.2 | 439.3 | 372.5
1817 | 1643 | -6.6 | 0 | 0 | 283.3 | 281.1 | 251.3 | 241.5 | 279.4 | 43 | -12.5 | 65.7 | 4.2 | 15.8 | 4.9 | 46.9 | 70.9 | 42.9 | 57 | 43.6 | 84.8 | 65.7 | 52.8 | 72 | 57.9 | 272.2 | 319.2 | 351.1 | 352.7 | 293.7 | 254.7 | 323 | 303.8 | 438.9 | 372.3
1818 | 1644 | -6.7 | 0 | 0 | 283 | 281 | 251 | 241.2 | 279.3 | 42.9 | -12.5 | 65.6 | 4 | 15.7 | 4.8 | 46.9 | 70.7 | 42.9 | 57.5 | 43.6 | 84.7 | 65.7 | 52.8 | 71.9 | 58.1 | 272.3 | 319.1 | 350.8 | 352.4 | 293.3 | 254.3 | 322.7 | 303.4 | 438.5 | 372.1
1819 | 1645 | -6.6 | 0 | 0 | 282.6 | 280.7 | 250.8 | 240.9 | 279.1 | 42.9 | -12.5 | 65.5 | 3.8 | 15.6 | 4.8 | 46.9 | 70.7 | 43 | 57.4 | 43.5 | 84.6 | 66.2 | 53.2 | 72 | 58.3 | 272.4 | 319 | 350.6 | 352.1 | 292.9 | 254 | 322.4 | 303.1 | 438 | 371.9
1820 | 1646 | -6.6 | 0 | 0 | 282.3 | 280.4 | 250.6 | 240.5 | 278.8 | 42.9 | -12.5 | 65.4 | 4 | 15.4 | 4.8 | 46.9 | 70.1 | 43.2 | 57.3 | 43.5 | 84.5 | 65.7 | 53.6 | 72 | 58.6 | 272.5 | 319 | 350.3 | 351.8 | 292.6 | 253.6 | 322.1 | 302.6 | 437.6 | 371.7
1821 | 1647 | -6.5 | 0 | 0 | 282 | 280.2 | 250.4 | 240.2 | 278.4 | 42.9 | -12.5 | 65.3 | 3.9 | 15.3 | 4.7 | 46.9 | 70 | 43.2 | 57.1 | 43.5 | 84.1 | 64.8 | 54 | 72 | 58.9 | 272.6 | 318.9 | 350 | 351.5 | 292.3 | 253.1 | 321.8 | 302.3 | 437.2 | 371.4
1822 | 1648 | -6.4 | 0 | 0 | 281.5 | 280 | 250.1 | 240 | 277.9 | 42.8 | -12.5 | 65.1 | 3.7 | 15.2 | 4.7 | 47 | 70.2 | 43.1 | 56.8 | 43.4 | 83.6 | 64.4 | 53.9 | 71.9 | 59 | 272.7 | 318.8 | 349.8 | 351.2 | 292.2 | 252.8 | 321.4 | 301.9 | 436.8 | 371.2
1823 | 1649 | -6.5 | 0 | 0 | 281.1 | 279.8 | 249.9 | 239.7 | 277.3 | 42.6 | -12.5 | 65 | 4.1 | 15.1 | 4.7 | 47 | 70 | 43.2 | 57 | 43.2 | 83.6 | 64.9 | 53.6 | 71.8 | 59.2 | 272.8 | 318.7 | 349.5 | 350.9 | 291.9 | 252.5 | 321.1 | 301.6 | 436.4 | 371
1824 | 1650 | -6.5 | 0 | 0 | 280.8 | 279.5 | 249.6 | 239.5 | 276.8 | 42.6 | -12.5 | 64.9 | 4.1 | 15 | 4.6 | 47.1 | 70 | 43.2 | 57.2 | 43.1 | 83.9 | 65 | 53.2 | 72.1 | 59.3 | 272.9 | 318.7 | 349.2 | 350.6 | 291.6 | 252.2 | 320.8 | 301.2 | 436 | 370.8
1825 | 1651 | -6.5 | 0 | 0 | 280.3 | 279.1 | 249.3 | 239.3 | 276.5 | 42.5 | -12.5 | 64.8 | 4.2 | 14.8 | 4.6 | 47.1 | 69.8 | 43.1 | 57.1 | 43 | 84 | 64.7 | 52.9 | 72.3 | 59.5 | 273 | 318.6 | 349 | 350.3 | 291.1 | 251.9 | 320.5 | 300.8 | 435.6 | 370.6
1826 | 1652 | -6.4 | 0 | 0 | 280 | 278.7 | 249 | 239 | 276.3 | 42.4 | -12.5 | 64.7 | 4.2 | 14.7 | 4.6 | 47.1 | 69.8 | 43.2 | 56.6 | 42.9 | 83.9 | 64.1 | 52.5 | 72.4 | 59.7 | 273.1 | 318.5 | 348.7 | 350 | 290.8 | 251.6 | 320.3 | 300.4 | 435.1 | 370.4
1827 | 1653 | -6.5 | 0 | 0 | 279.6 | 278.1 | 248.7 | 238.7 | 276.1 | 42.3 | -12.5 | 64.7 | 4 | 14.6 | 4.5 | 47.2 | 70 | 43.4 | 56.6 | 42.8 | 83.8 | 63.6 | 52.4 | 72.4 | 59.9 | 273.2 | 318.4 | 348.4 | 349.7 | 290.5 | 251.3 | 319.9 | 300 | 434.7 | 370.1
1828 | 1654 | -6.4 | 0 | 0 | 279.3 | 277.7 | 248.5 | 238.4 | 275.8 | 42.2 | -12.5 | 64.6 | 3.8 | 14.5 | 4.5 | 47.2 | 70.2 | 43.5 | 56.7 | 42.8 | 84 | 64.6 | 52 | 72.4 | 60 | 273.3 | 318.3 | 348.2 | 349.4 | 290.2 | 251 | 319.6 | 299.7 | 434.3 | 369.9
1829 | 1655 | -6.4 | 0 | 0 | 278.9 | 277.2 | 248.1 | 238.1 | 275.5 | 42.1 | -12.5 | 64.5 | 4.1 | 14.4 | 4.5 | 47.3 | 69.8 | 43.7 | 56.2 | 42.6 | 84 | 65.9 | 51.8 | 72.5 | 60.1 | 273.4 | 318.3 | 347.9 | 349 | 289.9 | 250.7 | 319.3 | 299.3 | 433.9 | 369.7
1830 | 1656 | -6.4 | 0 | 0 | 278.7 | 276.5 | 247.8 | 237.8 | 275.3 | 42.1 | -12.5 | 64.4 | 3.8 | 14.3 | 4.4 | 47.3 | 69.2 | 43.7 | 57.1 | 42.5 | 83.8 | 65.9 | 52 | 72.5 | 60.2 | 273.5 | 318.2 | 347.6 | 348.7 | 289.7 | 250.4 | 319.1 | 298.9 | 433.5 | 369.5
1831 | 1657 | -6.4 | 0 | 0 | 278.6 | 275.9 | 247.6 | 237.5 | 275.2 | 42 | -12.5 | 64.3 | 3.6 | 14.2 | 4.4 | 47.4 | 69.3 | 43.8 | 57.1 | 42.4 | 83.5 | 65.5 | 51.6 | 72.3 | 60.4 | 273.5 | 318.1 | 347.4 | 348.4 | 289.6 | 250.1 | 318.9 | 298.5 | 433.1 | 369.3
1832 | 1658 | -6.4 | 0 | 0 | 278.2 | 275.8 | 247.3 | 237.2 | 275 | 41.9 | -12.5 | 64.2 | 4 | 14.1 | 4.4 | 47.4 | 69.3 | 43.8 | 57.1 | 42.3 | 83.4 | 65.9 | 51.7 | 72.1 | 60.6 | 273.6 | 318.1 | 347.1 | 348.1 | 289.4 | 249.7 | 318.7 | 298.2 | 432.7 | 369
1833 | 1659 | -6.4 | 0 | 0 | 277.8 | 275.6 | 246.9 | 237 | 274.9 | 41.8 | -12.5 | 64.1 | 4.1 | 14 | 4.3 | 47.4 | 68.8 | 43.9 | 56.1 | 42.3 | 83.6 | 66.4 | 52.3 | 72.2 | 60.8 | 273.7 | 318 | 346.9 | 347.8 | 289.3 | 249.3 | 318.4 | 297.8 | 432.3 | 368.8
1834 | 1660 | -6.4 | 0 | 0 | 277.6 | 275.5 | 246.6 | 236.7 | 274.7 | 41.8 | -12.5 | 64 | 4.2 | 13.9 | 4.3 | 47.5 | 69 | 43.9 | 56.8 | 42.3 | 84 | 66.4 | 53 | 72.3 | 61 | 273.8 | 317.9 | 346.6 | 347.6 | 289.2 | 249 | 318.1 | 297.4 | 431.9 | 368.6
1835 | 1661 | -6.5 | 0 | 0 | 277.2 | 275.3 | 246.4 | 236.5 | 274.5 | 41.7 | -12.5 | 63.9 | 4.2 | 13.8 | 4.3 | 47.6 | 71.2 | 44 | 56.9 | 42.3 | 84.2 | 66.7 | 54.1 | 72.4 | 61.1 | 273.8 | 317.8 | 346.3 | 347.3 | 289 | 248.7 | 317.9 | 297.1 | 431.5 | 368.4
1836 | 1662 | -6.5 | 0 | 0 | 276.6 | 275.1 | 246.2 | 236.2 | 274.3 | 41.7 | -12.5 | 63.9 | 4.4 | 13.7 | 4.3 | 47.7 | 69.5 | 44 | 56.9 | 42.2 | 84.1 | 66 | 53.5 | 72.6 | 61.3 | 273.9 | 317.7 | 346.1 | 347 | 288.7 | 248.5 | 317.6 | 296.7 | 431.1 | 368.2
1837 | 1663 | -6.5 | 0 | 0 | 276.3 | 275.1 | 246 | 236 | 274.1 | 41.6 | -12.5 | 63.8 | 4.3 | 13.6 | 4.2 | 47.8 | 69 | 44.1 | 57.2 | 42.2 | 83.9 | 66.2 | 52.5 | 72.5 | 61.5 | 274 | 317.7 | 345.8 | 346.7 | 288.5 | 248.1 | 317.3 | 296.4 | 430.7 | 367.9
1838 | 1664 | -6.5 | 0 | 0 | 276.1 | 275.1 | 245.7 | 235.7 | 273.9 | 41.6 | -12.5 | 63.7 | 4 | 13.5 | 4.2 | 47.9 | 69.2 | 44.1 | 57.3 | 42.1 | 83.8 | 66.1 | 52.1 | 72.5 | 61.6 | 274 | 317.6 | 345.6 | 346.4 | 288.3 | 247.8 | 317.1 | 296 | 430.3 | 367.7
1839 | 1665 | -6.4 | 0 | 0 | 275.6 | 274.7 | 245.3 | 235.5 | 273.7 | 41.6 | -12.5 | 63.7 | 3.9 | 13.4 | 4.2 | 47.9 | 68.9 | 44 | 57 | 42.1 | 83.7 | 66 | 51.5 | 72.6 | 61.6 | 274.1 | 317.5 | 345.3 | 346.1 | 288.1 | 247.5 | 316.8 | 295.6 | 429.9 | 367.5
1840 | 1666 | -6.5 | 0 | 0 | 275.3 | 274.4 | 245.1 | 235.2 | 273.4 | 41.6 | -12.5 | 63.6 | 3.8 | 13.3 | 4.2 | 48 | 68.7 | 44 | 57.4 | 42.1 | 83.7 | 65 | 50.2 | 72.6 | 61.7 | 274.1 | 317.4 | 345 | 345.8 | 287.9 | 247.2 | 316.4 | 295.3 | 429.5 | 367.3
1841 | 1667 | -6.4 | 0 | 0 | 275 | 274.4 | 244.8 | 234.9 | 273 | 41.6 | -12.5 | 63.5 | 3.7 | 13.2 | 4.1 | 48 | 69 | 44.1 | 57.1 | 42 | 83.6 | 63.7 | 49.5 | 72.6 | 61.6 | 274.2 | 317.3 | 344.8 | 345.6 | 287.7 | 246.9 | 316.1 | 294.9 | 429.1 | 367.1
1842 | 1668 | -6.4 | 0 | 0 | 274.4 | 274.4 | 244.6 | 234.8 | 272.7 | 41.5 | -12.5 | 63.5 | 4.4 | 13.1 | 4.1 | 48.1 | 69.2 | 44.1 | 57.2 | 41.9 | 83.4 | 64.4 | 48.8 | 72.6 | 61.6 | 274.2 | 317.2 | 344.6 | 345.3 | 287.5 | 246.6 | 315.9 | 294.5 | 428.7 | 366.9
1843 | 1669 | -6.4 | 0 | 0 | 273.8 | 274.3 | 244.3 | 234.5 | 272.4 | 41.5 | -12.5 | 63.4 | 4 | 13.1 | 4.1 | 48.2 | 68.6 | 44.1 | 57.6 | 41.9 | 83.3 | 64.6 | 47.8 | 72.6 | 61.7 | 274.3 | 317.2 | 344.3 | 345 | 287.3 | 246.3 | 315.6 | 294.2 | 428.3 | 366.6
1844 | 1670 | -6.4 | 0 | 0 | 273.2 | 274.1 | 244 | 234.3 | 272.1 | 41.4 | -12.5 | 63.3 | 3.9 | 13 | 4.1 | 48.2 | 68.1 | 44.2 | 58 | 41.8 | 83.3 | 64.7 | 48.2 | 72.6 | 61.8 | 274.4 | 317.1 | 344 | 344.7 | 287 | 246 | 315.4 | 293.8 | 427.9 | 366.4
1845 | 1671 | -6.2 | 0 | 0 | 272.8 | 273.8 | 243.7 | 234.1 | 271.8 | 41.4 | -12.5 | 63.3 | 3.8 | 12.9 | 4 | 48.3 | 68.8 | 44.2 | 57.5 | 41.8 | 82.6 | 64.6 | 47.9 | 72.5 | 61.9 | 274.4 | 317 | 343.8 | 344.5 | 286.7 | 245.8 | 315.2 | 293.5 | 427.5 | 366.2
1846 | 1672 | -6.4 | 0 | 0 | 272.5 | 273.2 | 243.4 | 233.9 | 271.4 | 41.4 | -12.5 | 63.2 | 4 | 12.8 | 4 | 48.4 | 68.6 | 44.2 | 57.6 | 41.9 | 82.3 | 64 | 48.6 | 72.3 | 62.1 | 274.5 | 316.9 | 343.5 | 344.2 | 286.5 | 245.5 | 314.9 | 293.1 | 427.1 | 366
1847 | 1673 | -6.4 | 0 | 0 | 272.3 | 272.7 | 243.2 | 233.7 | 271.1 | 41.4 | -12.5 | 63.1 | 3.9 | 12.7 | 4 | 48.5 | 69.4 | 44.3 | 57.7 | 41.9 | 82.2 | 63.8 | 50.3 | 72.3 | 62.2 | 274.6 | 316.8 | 343.3 | 343.9 | 286.3 | 245.3 | 314.6 | 292.8 | 426.7 | 365.8
1848 | 1674 | -6.4 | 0 | 0 | 272.2 | 272.4 | 242.9 | 233.5 | 270.7 | 41.4 | -12.5 | 63 | 3.5 | 12.6 | 4 | 48.6 | 68.8 | 44.4 | 57.3 | 41.9 | 82.2 | 64.1 | 49.8 | 72.3 | 62.4 | 274.7 | 316.8 | 343 | 343.7 | 286.2 | 245.1 | 314.3 | 292.4 | 426.3 | 365.5
1849 | 1675 | -6.5 | 0 | 0 | 271.9 | 271.7 | 242.6 | 233.2 | 270.4 | 41.5 | -12.5 | 62.9 | 3.5 | 12.6 | 3.9 | 48.7 | 68.3 | 44.6 | 57.2 | 41.8 | 82 | 64.2 | 49.4 | 72.3 | 62.5 | 274.8 | 316.7 | 342.8 | 343.4 | 286 | 244.9 | 313.9 | 292.1 | 425.9 | 365.3
1850 | 1676 | -6.6 | 0 | 0 | 271.7 | 271 | 242.3 | 233 | 270.2 | 41.4 | -12.5 | 62.8 | 3.5 | 12.5 | 3.9 | 48.8 | 67.9 | 44.7 | 56.6 | 41.8 | 81.4 | 64 | 49.1 | 72 | 62.6 | 274.8 | 316.6 | 342.5 | 343.1 | 285.9 | 244.7 | 313.7 | 291.7 | 425.6 | 365.1
1851 | 1677 | -6.6 | 0 | 0 | 271.5 | 270.7 | 242 | 232.7 | 270.1 | 41.4 | -12.5 | 62.7 | 3.6 | 12.4 | 3.9 | 48.9 | 67.9 | 44.7 | 57.3 | 41.7 | 81.3 | 63.9 | 49.7 | 71.9 | 62.7 | 274.9 | 316.5 | 342.3 | 342.8 | 285.7 | 244.5 | 313.5 | 291.4 | 425.2 | 364.9
1852 | 1678 | -6.5 | 0 | 0 | 271.2 | 270.5 | 241.8 | 232.5 | 270 | 41.5 | -12.5 | 62.5 | 3.7 | 12.3 | 3.9 | 48.9 | 67.6 | 44.9 | 57.4 | 41.6 | 81.1 | 64 | 51.7 | 71.8 | 62.9 | 275 | 316.4 | 342 | 342.5 | 285.5 | 244.4 | 313.3 | 291.1 | 424.8 | 364.6
1853 | 1679 | -6.5 | 0 | 0 | 270.9 | 270.2 | 241.5 | 232.3 | 269.8 | 41.5 | -12.5 | 62.4 | 3.7 | 12.2 | 3.9 | 49 | 67.2 | 45.1 | 56.6 | 41.5 | 80.7 | 64.5 | 53.3 | 71.8 | 63 | 275.1 | 316.3 | 341.8 | 342.3 | 285.3 | 244.3 | 313.1 | 290.8 | 424.4 | 364.4
1854 | 1680 | -6.5 | 0 | 0 | 270.4 | 270.2 | 241.2 | 232.1 | 269.4 | 41.6 | -12.5 | 62.3 | 3.8 | 12.2 | 3.8 | 49.1 | 66.7 | 45.3 | 56.1 | 41.4 | 80.5 | 64.3 | 54 | 71.8 | 63 | 275.1 | 316.2 | 341.5 | 342 | 285.1 | 244.1 | 312.9 | 290.4 | 424 | 364.2
1855 | 1681 | -6.4 | 0 | 0 | 269.9 | 270.1 | 240.9 | 231.8 | 269 | 41.6 | -12.5 | 62.3 | 3.6 | 12.1 | 3.8 | 49.1 | 66.5 | 45.3 | 55.5 | 41.4 | 80.3 | 63.4 | 54.5 | 71.7 | 63.1 | 275.2 | 316.1 | 341.3 | 341.7 | 284.8 | 244 | 312.7 | 290.1 | 423.6 | 364
1856 | 1682 | -6.4 | 0 | 0 | 269.9 | 269.7 | 240.6 | 231.6 | 268.6 | 41.7 | -12.5 | 62.3 | 3.7 | 12 | 3.8 | 49.2 | 66.5 | 45.5 | 55.4 | 41.3 | 80 | 63.6 | 54.9 | 71.7 | 63.3 | 275.3 | 316.1 | 341 | 341.5 | 284.7 | 243.9 | 312.6 | 289.8 | 423.2 | 363.8
1857 | 1683 | -6.4 | 0 | 0 | 269.8 | 269.4 | 240.4 | 231.3 | 268.3 | 41.7 | -12.5 | 62.2 | 3.9 | 12 | 3.8 | 49.3 | 66.4 | 45.7 | 55.8 | 41.2 | 80 | 63.6 | 55.1 | 71.6 | 63.4 | 275.3 | 316 | 340.8 | 341.2 | 284.5 | 243.7 | 312.3 | 289.5 | 422.8 | 363.5
1858 | 1684 | -6.4 | 0 | 0 | 269.1 | 269.1 | 240.1 | 231.1 | 268.1 | 41.7 | -12.5 | 62.1 | 3.8 | 11.9 | 3.7 | 49.3 | 66.6 | 45.8 | 56.3 | 41.2 | 79.9 | 64.3 | 54.9 | 71.5 | 63.4 | 275.4 | 315.9 | 340.5 | 341 | 284.3 | 243.5 | 312.2 | 289.2 | 422.4 | 363.3
1859 | 1685 | -6.3 | 0 | 0 | 268.8 | 268.7 | 239.9 | 230.9 | 268 | 41.6 | -12.5 | 62 | 4 | 11.8 | 3.7 | 49.4 | 66.1 | 45.7 | 56.2 | 41.1 | 79.9 | 64 | 54.4 | 71.4 | 63.6 | 275.5 | 315.8 | 340.3 | 340.7 | 284.1 | 243.2 | 312.1 | 288.9 | 422 | 363.1
1860 | 1686 | -6.2 | 0 | 0 | 268.7 | 268.4 | 239.6 | 230.7 | 267.8 | 41.5 | -12.5 | 61.9 | 3.9 | 11.7 | 3.7 | 49.4 | 65.9 | 45.7 | 56.4 | 41.1 | 79.8 | 63.9 | 54.6 | 71.4 | 63.7 | 275.6 | 315.7 | 340 | 340.4 | 283.8 | 243 | 311.9 | 288.6 | 421.7 | 362.9
1861 | 1687 | -6.2 | 0 | 0 | 267.9 | 268.1 | 239.3 | 230.4 | 267.4 | 41.4 | -12.5 | 61.9 | 3.8 | 11.7 | 3.7 | 49.5 | 67.1 | 45.6 | 56.6 | 41.1 | 79.8 | 64.5 | 55 | 71.5 | 63.9 | 275.6 | 315.6 | 339.8 | 340.2 | 283.6 | 242.8 | 311.7 | 288.2 | 421.3 | 362.7
1862 | 1688 | -6.2 | 0 | 0 | 267.6 | 267.7 | 239.1 | 230.1 | 267 | 41.3 | -12.5 | 61.8 | 3.5 | 11.6 | 3.7 | 49.5 | 67.1 | 45.6 | 56.8 | 41 | 79.6 | 64.3 | 54.9 | 71.5 | 63.9 | 275.7 | 315.5 | 339.5 | 339.9 | 283.4 | 242.6 | 311.5 | 287.9 | 420.9 | 362.4
1863 | 1689 | -6.3 | 0 | 0 | 267.5 | 267.5 | 238.9 | 229.9 | 266.5 | 41.2 | -12.5 | 61.8 | 4 | 11.5 | 3.6 | 49.6 | 66.7 | 45.5 | 56.2 | 41 | 79.7 | 64 | 55.7 | 71.6 | 64 | 275.8 | 315.5 | 339.3 | 339.6 | 283.2 | 242.4 | 311.3 | 287.6 | 420.5 | 362.2
1864 | 1690 | -6.4 | 0 | 0 | 267.2 | 267.2 | 238.6 | 229.7 | 266.3 | 41.2 | -12.5 | 61.8 | 4 | 11.5 | 3.6 | 49.7 | 66.9 | 45.3 | 55.9 | 40.8 | 79.9 | 64 | 55.8 | 71.6 | 64 | 275.9 | 315.4 | 339.1 | 339.4 | 282.9 | 242.2 | 311.1 | 287.2 | 420.1 | 362
1865 | 1691 | -6.3 | 0 | 0 | 267 | 266.7 | 238.2 | 229.4 | 266.3 | 41.1 | -12.5 | 61.8 | 3.8 | 11.4 | 3.6 | 49.7 | 66.9 | 45.4 | 55.2 | 40.8 | 80 | 63.7 | 55.9 | 71.7 | 64 | 275.9 | 315.3 | 338.8 | 339.1 | 282.6 | 241.9 | 310.9 | 287 | 419.7 | 361.8
1866 | 1692 | -6.2 | 0 | 0 | 266.9 | 266.3 | 238 | 229.2 | 266.4 | 41.1 | -12.5 | 61.8 | 3.6 | 11.3 | 3.6 | 49.8 | 66.7 | 45.3 | 55.2 | 40.7 | 79.9 | 63.3 | 55.5 | 71.7 | 64 | 276 | 315.2 | 338.6 | 338.8 | 282.4 | 241.7 | 310.6 | 286.6 | 419.4 | 361.5
1867 | 1693 | -6.2 | 0 | 0 | 266.6 | 266 | 237.8 | 229 | 266.4 | 41 | -12.5 | 61.7 | 3.5 | 11.3 | 3.6 | 49.9 | 66.4 | 45.1 | 55.6 | 40.6 | 79.7 | 63.5 | 54.9 | 71.6 | 64 | 276 | 315.1 | 338.3 | 338.6 | 282.2 | 241.4 | 310.4 | 286.3 | 419 | 361.3
1868 | 1694 | -6.2 | 0 | 0 | 266.4 | 265.8 | 237.6 | 228.8 | 266.4 | 41 | -12.5 | 61.7 | 3.1 | 11.2 | 3.5 | 50 | 66.6 | 45 | 56.3 | 40.5 | 79.8 | 64.3 | 55.6 | 71.6 | 64 | 276 | 315 | 338.1 | 338.3 | 282 | 241.2 | 310.2 | 286 | 418.6 | 361.1
1869 | 1695 | -6.4 | 0 | 0 | 266.1 | 265.5 | 237.3 | 228.7 | 266.3 | 40.9 | -12.5 | 61.7 | 3.3 | 11.1 | 3.5 | 50 | 65.9 | 45 | 56.1 | 40.3 | 80.1 | 64.4 | 56.3 | 71.7 | 64 | 276.1 | 314.9 | 337.9 | 338.1 | 281.7 | 240.9 | 310 | 285.7 | 418.2 | 360.9
1870 | 1696 | -6.5 | 0 | 0 | 265.9 | 265.1 | 237 | 228.5 | 266.2 | 40.9 | -12.5 | 61.6 | 3.6 | 11.1 | 3.5 | 50 | 65.4 | 44.9 | 56.1 | 40.2 | 80.1 | 63.8 | 55.8 | 71.8 | 64 | 276.2 | 314.8 | 337.6 | 337.8 | 281.5 | 240.7 | 309.8 | 285.4 | 417.8 | 360.6
1871 | 1697 | -6.5 | 0 | 0 | 265.6 | 264.6 | 236.8 | 228.2 | 266 | 40.9 | -12.5 | 61.6 | 3.8 | 11 | 3.5 | 50 | 65 | 44.9 | 56.4 | 40.2 | 79.7 | 63.8 | 56 | 71.8 | 64 | 276.3 | 314.8 | 337.4 | 337.6 | 281.3 | 240.5 | 309.6 | 285.1 | 417.5 | 360.4
1872 | 1698 | -6.3 | 0 | 0 | 265.2 | 264.2 | 236.6 | 227.9 | 265.6 | 40.9 | -12.5 | 61.5 | 3.6 | 11 | 3.5 | 50.1 | 64.4 | 44.8 | 55.8 | 40.2 | 79.3 | 63.1 | 55.7 | 71.6 | 64.2 | 276.4 | 314.7 | 337.1 | 337.3 | 280.9 | 240.2 | 309.4 | 284.8 | 417.1 | 360.2
1873 | 1699 | -6.2 | 0 | 0 | 265 | 264.1 | 236.4 | 227.7 | 265.3 | 40.9 | -12.5 | 61.4 | 3.4 | 10.9 | 3.5 | 50.2 | 65.3 | 44.8 | 55.6 | 40.2 | 79.2 | 63 | 55.1 | 71.4 | 64.4 | 276.4 | 314.6 | 336.9 | 337 | 280.6 | 240 | 309.2 | 284.5 | 416.7 | 360
1874 | 1700 | -6.2 | 0 | 0 | 264.8 | 264 | 236.3 | 227.4 | 265 | 40.9 | -12.5 | 61.3 | 3.3 | 10.8 | 3.4 | 50.2 | 64.7 | 44.8 | 56.6 | 40.2 | 79.2 | 62.3 | 54.5 | 71.4 | 64.6 | 276.4 | 314.5 | 336.7 | 336.8 | 280.4 | 239.7 | 308.9 | 284.2 | 416.3 | 359.8
1875 | 1701 | -6.1 | 0 | 0 | 264.5 | 263.3 | 236 | 227.2 | 264.7 | 40.9 | -12.5 | 61.2 | 3.6 | 10.8 | 3.4 | 50.3 | 64.5 | 45.1 | 57.4 | 40.2 | 79 | 62 | 55.3 | 71.2 | 64.7 | 276.6 | 314.4 | 336.4 | 336.5 | 280.2 | 239.4 | 308.7 | 283.9 | 415.9 | 359.5
1876 | 1702 | -6 | 0 | 0 | 264.2 | 262.9 | 235.8 | 227 | 264.5 | 40.9 | -12.5 | 61.2 | 3.4 | 10.7 | 3.4 | 50.3 | 65 | 45.2 | 56.7 | 40.1 | 79 | 62.2 | 55.7 | 71.2 | 64.8 | 276.6 | 314.3 | 336.2 | 336.3 | 280 | 239.2 | 308.5 | 283.5 | 415.6 | 359.3
1877 | 1703 | -5.8 | 0 | 0 | 264 | 262.9 | 235.6 | 226.8 | 264.3 | 40.8 | -12.5 | 61.1 | 3.7 | 10.7 | 3.4 | 50.3 | 65.1 | 45.2 | 56.1 | 40.1 | 78.8 | 62.7 | 54.8 | 71.1 | 64.8 | 276.6 | 314.2 | 335.9 | 336 | 279.8 | 238.9 | 308.3 | 283.2 | 415.2 | 359.1
1878 | 1704 | -6 | 0 | 0 | 263.8 | 262.6 | 235.4 | 226.7 | 264.2 | 40.7 | -12.5 | 61.1 | 3.6 | 10.6 | 3.4 | 50.3 | 65.1 | 45.2 | 55 | 40 | 78.9 | 63.6 | 54.5 | 71.1 | 64.8 | 276.7 | 314.1 | 335.7 | 335.7 | 279.6 | 238.6 | 308 | 282.9 | 414.8 | 358.9
1879 | 1705 | -6.1 | 0 | 0 | 263.5 | 262.2 | 235.1 | 226.5 | 264.2 | 40.6 | -12.5 | 61 | 3.8 | 10.6 | 3.4 | 50.4 | 65.7 | 45.2 | 55.4 | 39.9 | 79 | 63.7 | 54.3 | 71.2 | 64.9 | 276.8 | 314 | 335.5 | 335.5 | 279.4 | 238.4 | 307.8 | 282.6 | 414.4 | 358.7
1880 | 1706 | -6.3 | 0 | 0 | 263.3 | 261.8 | 234.8 | 226.4 | 264 | 40.5 | -12.5 | 61 | 4.1 | 10.5 | 3.3 | 50.3 | 66.4 | 45.3 | 55.7 | 39.9 | 79.1 | 63.5 | 53.8 | 71.2 | 64.9 | 276.9 | 313.9 | 335.2 | 335.2 | 279.2 | 238.2 | 307.6 | 282.4 | 414.1 | 358.5
1881 | 1707 | -6.3 | 0 | 0 | 263.1 | 261.5 | 234.7 | 226.1 | 263.7 | 40.3 | -12.5 | 61 | 3.9 | 10.5 | 3.3 | 50.3 | 66.4 | 45.4 | 56.3 | 39.8 | 79.2 | 64.1 | 54.1 | 71.3 | 64.8 | 276.9 | 313.9 | 335 | 334.9 | 278.9 | 237.9 | 307.4 | 282.1 | 413.7 | 358.3
1882 | 1708 | -6.2 | 0 | 0 | 262.9 | 261.2 | 234.5 | 225.8 | 263.2 | 40.3 | -12.5 | 61 | 4 | 10.4 | 3.3 | 50.3 | 67.1 | 45.5 | 56 | 39.7 | 79.1 | 63.3 | 54.7 | 71.3 | 64.9 | 277 | 313.8 | 334.8 | 334.7 | 278.7 | 237.7 | 307.2 | 281.8 | 413.3 | 358
1883 | 1709 | -6 | 0 | 0 | 262.5 | 261 | 234.2 | 225.6 | 263 | 40.3 | -12.5 | 60.9 | 4 | 10.3 | 3.3 | 50.3 | 65.9 | 45.5 | 56.1 | 39.7 | 79 | 63.1 | 55.2 | 71.2 | 64.9 | 277 | 313.7 | 334.5 | 334.4 | 278.5 | 237.4 | 307 | 281.5 | 413 | 357.8
1884 | 1710 | -6.1 | 0 | 0 | 262.3 | 260.8 | 234 | 225.4 | 262.9 | 40.3 | -12.5 | 60.8 | 4 | 10.3 | 3.3 | 50.4 | 65.4 | 45.5 | 56.8 | 39.7 | 78.4 | 63 | 55.2 | 71 | 65 | 277.1 | 313.6 | 334.3 | 334.2 | 278.3 | 237.1 | 306.8 | 281.2 | 412.6 | 357.6
1885 | 1711 | -6.2 | 0 | 0 | 261.9 | 260.6 | 233.8 | 225.2 | 262.8 | 40.3 | -12.5 | 60.7 | 3.9 | 10.2 | 3.3 | 50.3 | 65.8 | 45.4 | 57.3 | 39.6 | 78 | 63.3 | 55.8 | 70.8 | 65 | 277.3 | 313.5 | 334.1 | 333.9 | 278.1 | 236.8 | 306.6 | 280.9 | 412.2 | 357.4
1886 | 1712 | -6.2 | 0 | 0 | 261.5 | 260.3 | 233.6 | 225 | 262.8 | 40.3 | -12.5 | 60.6 | 4.3 | 10.2 | 3.2 | 50.3 | 65.2 | 45.4 | 56.4 | 39.6 | 78.1 | 62.6 | 56.7 | 70.8 | 65.1 | 277.3 | 313.4 | 333.8 | 333.7 | 277.9 | 236.6 | 306.4 | 280.6 | 411.8 | 357.2
1887 | 1713 | -6.2 | 0 | 0 | 261.2 | 260 | 233.3 | 224.7 | 262.6 | 40.3 | -12.5 | 60.5 | 4.3 | 10.1 | 3.2 | 50.3 | 65.3 | 45.3 | 55.7 | 39.5 | 78 | 62.2 | 57.1 | 70.9 | 65.3 | 277.2 | 313.3 | 333.6 | 333.4 | 277.6 | 236.3 | 306.1 | 280.3 | 411.5 | 357
1888 | 1714 | -6.2 | 0 | 0 | 260.9 | 259.9 | 233.1 | 224.5 | 262.4 | 40.2 | -12.5 | 60.5 | 4.2 | 10.1 | 3.2 | 50.3 | 65.4 | 45.2 | 55.7 | 39.4 | 78 | 62.2 | 56.6 | 71 | 65.4 | 277.4 | 313.2 | 333.4 | 333.1 | 277.3 | 236.1 | 306 | 280 | 411.1 | 356.7
1889 | 1715 | -6.2 | 0 | 0 | 260.9 | 259.9 | 232.9 | 224.2 | 262.1 | 40.2 | -12.5 | 60.4 | 3.7 | 10 | 3.2 | 50.3 | 66 | 45.2 | 54.8 | 39.3 | 77.9 | 62.6 | 55.8 | 71 | 65.1 | 277.4 | 313.2 | 333.1 | 332.9 | 277.1 | 235.8 | 305.8 | 279.7 | 410.8 | 356.5
1890 | 1716 | -6.2 | 0 | 0 | 260.9 | 259.7 | 232.6 | 224 | 261.5 | 40.1 | -12.5 | 60.4 | 3.7 | 10 | 3.2 | 50.3 | 65 | 45.1 | 54.3 | 39.3 | 78.1 | 63 | 54.3 | 71.1 | 65.1 | 277.7 | 313.1 | 332.9 | 332.6 | 276.9 | 235.6 | 305.6 | 279.4 | 410.4 | 356.3
1891 | 1717 | -6.3 | 0 | 0 | 260.8 | 259.5 | 232.3 | 223.8 | 260 | 40.1 | -12.5 | 60.3 | 3.8 | 9.9 | 3.2 | 50.3 | 63.9 | 45.1 | 54.2 | 39.2 | 78.3 | 62.8 | 52.9 | 71.1 | 64.9 | 277.7 | 313 | 332.7 | 332.4 | 276.7 | 235.4 | 305.4 | 279.1 | 410 | 356.1
1892 | 1718 | -6.4 | 0 | 0 | 260.5 | 259.5 | 231.9 | 223.6 | 258.5 | 40 | -12.5 | 60.3 | 3.9 | 9.9 | 3.2 | 50.3 | 63.3 | 45 | 54.6 | 39.1 | 78.3 | 63.1 | 51.9 | 71.1 | 64.9 | 277.9 | 312.9 | 332.5 | 332.1 | 276.3 | 235.2 | 305.1 | 278.9 | 409.7 | 355.9
1893 | 1719 | -6.3 | 0 | 0 | 260.1 | 259.2 | 231.7 | 223.4 | 257.3 | 39.9 | -12.5 | 60.2 | 3.8 | 9.8 | 3.1 | 50.3 | 63.3 | 45 | 55 | 39 | 78.5 | 63.4 | 51.2 | 71.1 | 65 | 277.8 | 312.8 | 332.2 | 331.9 | 275.9 | 235 | 304.9 | 278.6 | 409.3 | 355.7
1894 | 1720 | -6.2 | 0 | 0 | 259.4 | 259.1 | 231.6 | 223.2 | 256.2 | 39.9 | -12.5 | 60.2 | 3.8 | 9.8 | 3.1 | 50.2 | 63.4 | 45 | 55.8 | 39 | 78.6 | 63.2 | 51.8 | 71.2 | 65.1 | 277.7 | 312.7 | 332 | 331.6 | 275.6 | 234.8 | 304.7 | 278.3 | 409 | 355.5
1895 | 1721 | -6 | 0 | 0 | 259.1 | 259.1 | 231.5 | 223.1 | 255 | 39.8 | -12.5 | 60.2 | 3.6 | 9.7 | 3.1 | 50.2 | 64.3 | 45 | 55.7 | 38.9 | 78.5 | 62.9 | 51.8 | 71.2 | 65 | 277.7 | 312.6 | 331.8 | 331.4 | 275.4 | 234.6 | 304.5 | 278 | 408.6 | 355.3
1896 | 1722 | -6.1 | 0 | 0 | 258.9 | 258.8 | 231.3 | 222.9 | 254.3 | 39.8 | -12.5 | 60.1 | 3.9 | 9.7 | 3.1 | 50.2 | 63.9 | 45.1 | 55 | 38.7 | 78.2 | 62.6 | 52.7 | 71.1 | 65 | 277.8 | 312.5 | 331.6 | 331.1 | 275.2 | 234.4 | 304.3 | 277.7 | 408.3 | 355
1897 | 1723 | -6.2 | 0 | 0 | 258.8 | 258.5 | 231 | 222.8 | 253.8 | 39.7 | -12.5 | 60.1 | 3.6 | 9.6 | 3.1 | 50.1 | 63.9 | 45.1 | 55.7 | 38.7 | 78 | 62.5 | 54.1 | 70.9 | 65.2 | 278 | 312.4 | 331.3 | 330.9 | 274.9 | 234.2 | 304.1 | 277.4 | 407.9 | 354.8
1898 | 1724 | -6.2 | 0 | 0 | 258.5 | 258 | 230.8 | 222.6 | 253.9 | 39.6 | -12.5 | 60.1 | 3.4 | 9.6 | 3.1 | 50.1 | 64.1 | 45.1 | 56.5 | 38.7 | 77.6 | 62.4 | 55 | 70.8 | 65.3 | 278.1 | 312.3 | 331.1 | 330.6 | 274.6 | 234 | 303.9 | 277.2 | 407.5 | 354.6
1899 | 1725 | -6.1 | 0 | 0 | 258.3 | 257.5 | 230.7 | 222.4 | 254 | 39.5 | -12.5 | 60.1 | 3.5 | 9.6 | 3.1 | 50.1 | 64.9 | 44.9 | 56.4 | 38.6 | 77.5 | 62.6 | 55.4 | 70.8 | 65.2 | 278.2 | 312.2 | 330.9 | 330.4 | 274.4 | 233.8 | 303.7 | 276.9 | 407.2 | 354.4
1900 | 1726 | -6.1 | 0 | 0 | 258 | 257.3 | 230.5 | 222.1 | 254.3 | 39.4 | -12.5 | 60 | 3.4 | 9.5 | 3 | 50.1 | 65.3 | 44.8 | 56.2 | 38.6 | 77.5 | 62.7 | 55.8 | 70.7 | 65.3 | 278.3 | 312.1 | 330.7 | 330.1 | 274.2 | 233.6 | 303.5 | 276.6 | 406.8 | 354.2
1901 | 1727 | -6.2 | 0 | 0 | 257.5 | 257.2 | 230.2 | 221.9 | 254.3 | 39.4 | -12.5 | 60 | 3.5 | 9.5 | 3 | 50.1 | 65.3 | 44.9 | 56.7 | 38.6 | 77.1 | 62.7 | 55.9 | 70.6 | 65.3 | 278.4 | 312 | 330.4 | 329.9 | 274.1 | 233.3 | 303.4 | 276.3 | 406.5 | 354
1902 | 1728 | -6.1 | 0 | 0 | 257.1 | 257.3 | 230 | 221.7 | 254.1 | 39.3 | -12.5 | 59.9 | 3.2 | 9.4 | 3 | 50 | 63.7 | 44.7 | 56.3 | 38.6 | 76.5 | 62.7 | 55.9 | 70.3 | 65.4 | 278.5 | 311.9 | 330.2 | 329.7 | 273.9 | 233.1 | 303.1 | 276 | 406.1 | 353.8
1903 | 1729 | -6.1 | 0 | 0 | 256.9 | 257.3 | 229.8 | 221.5 | 253.5 | 39.2 | -12.5 | 59.9 | 3.4 | 9.4 | 3 | 50 | 63.8 | 44.5 | 56.4 | 38.5 | 76.1 | 62.7 | 56.5 | 70.1 | 65.3 | 278.4 | 311.8 | 330 | 329.4 | 273.7 | 232.9 | 303 | 275.8 | 405.8 | 353.5
1904 | 1730 | -6.4 | 0 | 0 | 256.7 | 257.3 | 229.7 | 221.4 | 252.9 | 39.2 | -12.5 | 59.8 | 3.5 | 9.3 | 3 | 50 | 63.6 | 44.2 | 56.9 | 38.2 | 76.2 | 62.8 | 57.2 | 70.1 | 65.2 | 278.5 | 311.7 | 329.8 | 329.2 | 273.6 | 232.7 | 302.8 | 275.5 | 405.4 | 353.3
1905 | 1731 | -6.4 | 0 | 0 | 256.5 | 257.3 | 229.5 | 221.2 | 252.6 | 39.1 | -12.5 | 59.8 | 3.6 | 9.3 | 3 | 50 | 63.5 | 44.1 | 57.4 | 37.9 | 76.1 | 62.4 | 57.4 | 70.1 | 65.3 | 278.7 | 311.6 | 329.6 | 328.9 | 273.4 | 232.4 | 302.6 | 275.2 | 405.1 | 353.1
1906 | 1732 | -6.2 | 0 | 0 | 256.1 | 257 | 229.3 | 221 | 252.3 | 39.1 | -12.5 | 59.7 | 3.5 | 9.2 | 3 | 50 | 63.7 | 43.9 | 57.7 | 37.8 | 76 | 61.8 | 58 | 70.1 | 65.4 | 278.6 | 311.5 | 329.3 | 328.7 | 273.2 | 232.2 | 302.5 | 274.9 | 404.7 | 352.9
1907 | 1733 | -6.2 | 0 | 0 | 255.8 | 256.7 | 229 | 220.8 | 252 | 39.1 | -12.5 | 59.6 | 3.9 | 9.2 | 3 | 49.9 | 63.6 | 44 | 57.2 | 37.9 | 75.9 | 61.9 | 58.4 | 70 | 65.4 | 278.7 | 311.4 | 329.1 | 328.4 | 273 | 232.1 | 302.3 | 274.7 | 404.4 | 352.7
1908 | 1734 | -6.1 | 0 | 0 | 255.8 | 256.7 | 228.9 | 220.5 | 252.1 | 39.1 | -12.5 | 59.6 | 4 | 9.2 | 2.9 | 49.9 | 63.3 | 44 | 57.6 | 38 | 75.9 | 62.5 | 58.8 | 70 | 65.5 | 278.8 | 311.3 | 328.9 | 328.2 | 272.9 | 231.8 | 302.1 | 274.4 | 404 | 352.5
1909 | 1735 | -5.9 | 0 | 0 | 255.7 | 256.5 | 228.7 | 220.4 | 252.2 | 39.1 | -12.5 | 59.6 | 3.6 | 9.1 | 2.9 | 49.8 | 62.1 | 43.9 | 57 | 38 | 75.8 | 63 | 58.8 | 69.9 | 65.5 | 278.7 | 311.2 | 328.7 | 328 | 272.7 | 231.6 | 301.9 | 274.1 | 403.7 | 352.3
1910 | 1736 | -6.1 | 0 | 0 | 255.6 | 255.9 | 228.5 | 220.2 | 252.2 | 39.1 | -12.5 | 59.5 | 3.8 | 9.1 | 2.9 | 49.8 | 62.8 | 43.7 | 57.3 | 38.1 | 76.2 | 62.6 | 58.6 | 70 | 65.5 | 278.8 | 311.1 | 328.4 | 327.7 | 272.5 | 231.4 | 301.7 | 273.9 | 403.3 | 352.1
1911 | 1737 | -5.8 | 0 | 0 | 255.4 | 255.5 | 228.1 | 220.1 | 252.5 | 39.1 | -12.5 | 59.5 | 3.7 | 9 | 2.9 | 49.8 | 63.1 | 43.4 | 57.4 | 38.2 | 76.4 | 62.8 | 59 | 70 | 65.6 | 278.7 | 311.1 | 328.2 | 327.5 | 272.3 | 231.3 | 301.5 | 273.6 | 403 | 351.8
1912 | 1738 | -5.9 | 0 | 0 | 255.2 | 255.1 | 227.9 | 219.9 | 252.9 | 39.1 | -12.5 | 59.5 | 3.9 | 9 | 2.9 | 49.8 | 62.5 | 43.3 | 56.9 | 38.2 | 76.4 | 62.9 | 59.6 | 70 | 65.6 | 278.8 | 310.9 | 328 | 327.2 | 272 | 231.1 | 301.3 | 273.3 | 402.6 | 351.6
1913 | 1739 | -6.1 | 0 | 0 | 255.1 | 254.9 | 227.8 | 219.8 | 253.2 | 39 | -12.5 | 59.6 | 4.2 | 8.9 | 2.9 | 49.7 | 62.8 | 43.2 | 56.4 | 38.1 | 76.5 | 62.7 | 59.9 | 70.1 | 65.8 | 279 | 310.9 | 327.8 | 327 | 271.7 | 230.9 | 301.1 | 273.1 | 402.3 | 351.4
1914 | 1740 | -6 | 0 | 0 | 255 | 254.8 | 227.6 | 219.6 | 253.2 | 39 | -12.5 | 59.5 | 3.7 | 8.9 | 2.9 | 49.7 | 62.8 | 43.2 | 56.3 | 38.1 | 75.7 | 63.2 | 60 | 69.8 | 65.9 | 279 | 310.8 | 327.6 | 326.7 | 271.5 | 230.7 | 301 | 272.8 | 401.9 | 351.2
1915 | 1741 | -6 | 0 | 0 | 254.7 | 254.7 | 227.4 | 219.5 | 253.2 | 38.9 | -12.5 | 59.5 | 3.9 | 8.9 | 2.9 | 49.6 | 62.9 | 43.1 | 56.5 | 38 | 75.7 | 64.2 | 60.1 | 69.7 | 65.9 | 278.9 | 310.7 | 327.4 | 326.5 | 271.3 | 230.5 | 300.8 | 272.5 | 401.6 | 351
1916 | 1742 | -6.1 | 0 | 0 | 254.4 | 254.5 | 227.2 | 219.3 | 253.2 | 38.8 | -12.5 | 59.5 | 4.2 | 8.8 | 2.8 | 49.6 | 61.9 | 43 | 56.5 | 38 | 75.5 | 63.9 | 59.7 | 69.6 | 65.8 | 279.1 | 310.6 | 327.1 | 326.3 | 271.2 | 230.3 | 300.6 | 272.3 | 401.3 | 350.8
1917 | 1743 | -6 | 0 | 0 | 254.2 | 254.1 | 226.9 | 219.1 | 252.4 | 38.7 | -12.5 | 59.4 | 3.9 | 8.8 | 2.8 | 49.6 | 62.2 | 43 | 57 | 37.9 | 75.4 | 63 | 59.8 | 69.6 | 65.9 | 279 | 310.5 | 326.9 | 326 | 271 | 230.1 | 300.4 | 272 | 400.9 | 350.6
1918 | 1744 | -6 | 0 | 0 | 254.1 | 253.8 | 226.8 | 219 | 251.8 | 38.6 | -12.5 | 59.4 | 4 | 8.8 | 2.8 | 49.5 | 61.9 | 42.9 | 57 | 37.9 | 75.2 | 63.1 | 59.9 | 69.5 | 65.9 | 279.2 | 310.4 | 326.7 | 325.8 | 270.8 | 230 | 300.3 | 271.7 | 400.6 | 350.4
1919 | 1745 | -6.1 | 0 | 0 | 253.9 | 253.7 | 226.7 | 218.8 | 252 | 38.5 | -12.5 | 59.3 | 4 | 8.7 | 2.8 | 49.5 | 61.4 | 42.8 | 57 | 37.9 | 75.1 | 62.9 | 59.8 | 69.4 | 66 | 279.2 | 310.3 | 326.5 | 325.5 | 270.6 | 229.8 | 300 | 271.5 | 400.2 | 350.1
1920 | 1746 | -6 | 0 | 0 | 253.6 | 253.3 | 226.5 | 218.7 | 252.1 | 38.4 | -12.5 | 59.3 | 4.4 | 8.7 | 2.8 | 49.5 | 61.5 | 42.7 | 57.7 | 37.9 | 74.9 | 63.1 | 59.7 | 69.3 | 66.1 | 279.2 | 310.2 | 326.3 | 325.3 | 270.4 | 229.6 | 299.8 | 271.2 | 399.9 | 349.9
1921 | 1747 | -6.2 | 0 | 0 | 253.3 | 252.9 | 226.4 | 218.5 | 252.1 | 38.3 | -12.5 | 59.3 | 4.5 | 8.6 | 2.8 | 49.5 | 61.5 | 42.5 | 58 | 37.8 | 75.2 | 62.2 | 59.7 | 69.3 | 66.2 | 279.4 | 310.1 | 326.1 | 325.1 | 270.2 | 229.4 | 299.6 | 270.9 | 399.6 | 349.7
1922 | 1748 | -6.3 | 0 | 0 | 253 | 252.5 | 226.2 | 218.3 | 251.9 | 38.2 | -12.5 | 59.2 | 4.8 | 8.6 | 2.8 | 49.5 | 60.5 | 42.4 | 56.7 | 37.8 | 75.2 | 62 | 59.8 | 69.3 | 66.1 | 279.2 | 310 | 325.9 | 324.8 | 269.9 | 229.2 | 299.4 | 270.7 | 399.2 | 349.5
1923 | 1749 | -6.2 | 0 | 0 | 252.4 | 252.2 | 225.9 | 218 | 251.1 | 38.1 | -12.5 | 59.1 | 5 | 8.6 | 2.8 | 49.5 | 60.9 | 42.4 | 55.7 | 37.7 | 75.4 | 62.5 | 59.6 | 69.4 | 66.1 | 279.2 | 309.9 | 325.6 | 324.6 | 269.7 | 228.9 | 299.2 | 270.4 | 398.9 | 349.3
1924 | 1750 | -6.1 | 0 | 0 | 252 | 252.2 | 225.7 | 217.8 | 249.9 | 38 | -12.5 | 59 | 4.6 | 8.5 | 2.8 | 49.5 | 60.6 | 42.3 | 54.5 | 37.8 | 75.3 | 63.5 | 59.9 | 69.5 | 66.2 | 279.1 | 309.8 | 325.4 | 324.4 | 269.6 | 228.7 | 299.1 | 270.1 | 398.6 | 349.1
1925 | 1751 | -6.1 | 0 | 0 | 251.8 | 252.1 | 225.4 | 217.6 | 248.1 | 38 | -12.5 | 58.9 | 4.2 | 8.5 | 2.7 | 49.5 | 60.2 | 42.2 | 54.4 | 37.8 | 75.1 | 64.1 | 60.4 | 69.5 | 66.4 | 279.2 | 309.7 | 325.2 | 324.1 | 269.4 | 228.5 | 298.8 | 269.9 | 398.2 | 348.9
1926 | 1752 | -6.1 | 0 | 0 | 251.6 | 252 | 225.2 | 217.4 | 246.2 | 37.9 | -12.5 | 58.8 | 4.1 | 8.4 | 2.7 | 49.4 | 59.6 | 42.1 | 54.3 | 37.8 | 74.8 | 63.9 | 60.7 | 69.4 | 66.5 | 279.5 | 309.6 | 325 | 323.9 | 269.2 | 228.3 | 298.7 | 269.6 | 397.9 | 348.7
1927 | 1753 | -6 | 0 | 0 | 251.5 | 251.8 | 225.1 | 217.1 | 244.8 | 37.8 | -12.5 | 58.8 | 3.9 | 8.4 | 2.7 | 49.4 | 60.3 | 42 | 55.4 | 37.7 | 75 | 64.3 | 60.6 | 69.4 | 66.7 | 279.6 | 309.5 | 324.8 | 323.6 | 269 | 228.2 | 298.5 | 269.3 | 397.5 | 348.5
1928 | 1754 | -6.1 | 0 | 0 | 251.3 | 251.6 | 225 | 216.9 | 243.3 | 37.7 | -12.5 | 58.8 | 3.9 | 8.4 | 2.7 | 49.4 | 60.2 | 41.8 | 56.3 | 37.6 | 75 | 64.4 | 60.1 | 69.4 | 66.7 | 279.6 | 309.4 | 324.6 | 323.4 | 268.9 | 228 | 298.2 | 269.1 | 397.2 | 348.2
1929 | 1755 | -6 | 0 | 0 | 251.1 | 251.3 | 224.8 | 216.7 | 242.1 | 37.6 | -12.5 | 58.7 | 3.6 | 8.3 | 2.7 | 49.4 | 60.4 | 41.6 | 56.7 | 37.6 | 75.2 | 63.7 | 59.4 | 69.4 | 66.7 | 279.6 | 309.3 | 324.4 | 323.2 | 268.7 | 227.8 | 298 | 268.9 | 396.9 | 348
1930 | 1756 | -6 | 0 | 0 | 251 | 250.7 | 224.7 | 216.4 | 241.6 | 37.6 | -12.5 | 58.6 | 3.5 | 8.3 | 2.7 | 49.4 | 60.2 | 41.3 | 56.5 | 37.5 | 75.3 | 63.7 | 59.5 | 69.5 | 66.7 | 279.6 | 309.2 | 324.1 | 322.9 | 268.5 | 227.6 | 297.9 | 268.6 | 396.6 | 347.8
1931 | 1757 | -6.1 | 0 | 0 | 250.9 | 250.1 | 224.5 | 216.3 | 240.8 | 37.5 | -12.5 | 58.5 | 4 | 8.3 | 2.7 | 49.3 | 60.4 | 41.2 | 56.8 | 37.5 | 75.4 | 63.7 | 59.7 | 69.6 | 66.8 | 279.5 | 309.1 | 323.9 | 322.7 | 268.3 | 227.4 | 297.6 | 268.4 | 396.2 | 347.6
1932 | 1758 | -6.1 | 0 | 0 | 250.7 | 249.7 | 224.2 | 216.2 | 240.5 | 37.5 | -12.5 | 58.4 | 4.4 | 8.2 | 2.7 | 49.3 | 60.1 | 41.2 | 55.6 | 37.4 | 75.2 | 63.5 | 60.1 | 69.6 | 66.9 | 279.5 | 309 | 323.7 | 322.5 | 268.1 | 227.2 | 297.4 | 268.1 | 395.9 | 347.4
1933 | 1759 | -6.1 | 0 | 0 | 250.6 | 249.7 | 224.1 | 216 | 240.6 | 37.5 | -12.5 | 58.4 | 4.2 | 8.2 | 2.7 | 49.2 | 59.5 | 41.2 | 55.5 | 37.4 | 75.2 | 63.5 | 60.5 | 69.6 | 67 | 279.5 | 308.9 | 323.5 | 322.2 | 267.8 | 227.1 | 297.2 | 267.9 | 395.6 | 347.2
1934 | 1760 | -6.1 | 0 | 0 | 250.5 | 249.7 | 224 | 215.7 | 240.6 | 37.4 | -12.5 | 58.3 | 4 | 8.2 | 2.6 | 49.2 | 59.6 | 41.1 | 55.8 | 37.3 | 75.2 | 63.4 | 60.3 | 69.6 | 67 | 279.6 | 308.8 | 323.3 | 322 | 267.5 | 226.9 | 297 | 267.6 | 395.2 | 347
1935 | 1761 | -6.1 | 0 | 0 | 250 | 249.6 | 223.8 | 215.5 | 239.9 | 37.4 | -12.5 | 58.3 | 3.8 | 8.1 | 2.6 | 49.1 | 59.7 | 41 | 56 | 37.3 | 75.3 | 63.5 | 60.6 | 69.6 | 67 | 279.8 | 308.7 | 323.1 | 321.7 | 267.3 | 226.8 | 296.8 | 267.4 | 394.9 | 346.8
1936 | 1762 | -6.1 | 0 | 0 | 249.7 | 249.1 | 223.7 | 215.2 | 238.9 | 37.3 | -12.5 | 58.3 | 4.2 | 8.1 | 2.6 | 49.1 | 59.3 | 40.8 | 56.5 | 37.3 | 75.1 | 64.3 | 60.8 | 69.6 | 67.1 | 279.9 | 308.6 | 322.9 | 321.5 | 267.1 | 226.5 | 296.6 | 267.1 | 394.6 | 346.6
1937 | 1763 | -6.1 | 0 | 0 | 249.5 | 248.6 | 223.6 | 215.1 | 238.4 | 37.3 | -12.5 | 58.2 | 4.3 | 8 | 2.6 | 49 | 59.4 | 40.7 | 57 | 37.3 | 74.7 | 64.3 | 61.1 | 69.5 | 67 | 279.9 | 308.5 | 322.7 | 321.3 | 267 | 226.3 | 296.4 | 266.9 | 394.2 | 346.4
1938 | 1764 | -6.1 | 0 | 0 | 249.3 | 248.2 | 223.5 | 215.1 | 237.5 | 37.2 | -12.5 | 58.2 | 4.1 | 8 | 2.6 | 48.9 | 59.9 | 40.5 | 56.6 | 37.3 | 74.7 | 64.5 | 61.5 | 69.4 | 67.1 | 279.9 | 308.4 | 322.5 | 321.1 | 266.8 | 226.1 | 296.2 | 266.6 | 393.9 | 346.2
1939 | 1765 | -6.2 | 0 | 0 | 249.2 | 248.1 | 223.3 | 214.9 | 236.1 | 37.2 | -12.5 | 58.1 | 3.7 | 8 | 2.6 | 48.9 | 59.6 | 40.4 | 57 | 37.2 | 74.8 | 64.1 | 61.3 | 69.5 | 67.1 | 280.1 | 308.3 | 322.3 | 320.8 | 266.7 | 225.9 | 296.1 | 266.4 | 393.6 | 346
1940 | 1766 | -6.1 | 0 | 0 | 249.1 | 248.1 | 223.1 | 214.8 | 235.6 | 37.3 | -12.5 | 58.1 | 3.8 | 7.9 | 2.6 | 48.8 | 59.6 | 40.2 | 56.5 | 37.2 | 74.7 | 63.7 | 60.9 | 69.5 | 67 | 280.1 | 308.2 | 322.1 | 320.6 | 266.5 | 225.7 | 295.9 | 266.2 | 393.3 | 345.7
1941 | 1767 | -6 | 0 | 0 | 248.9 | 248 | 222.8 | 214.6 | 235 | 37.3 | -12.5 | 58 | 3.9 | 7.9 | 2.6 | 48.8 | 58 | 40 | 56.4 | 37.2 | 74.7 | 63.2 | 60.3 | 69.5 | 66.6 | 280 | 308.1 | 321.9 | 320.3 | 266.4 | 225.5 | 295.7 | 265.9 | 392.9 | 345.5
1942 | 1768 | -5.7 | 0 | 0 | 248.7 | 247.5 | 222.6 | 214.5 | 234.7 | 37.3 | -12.5 | 57.9 | 3.8 | 7.9 | 2.6 | 48.8 | 57.5 | 39.9 | 56 | 37.1 | 74.5 | 62.9 | 59.7 | 69.5 | 66.6 | 280 | 308 | 321.7 | 320.1 | 266.2 | 225.3 | 295.5 | 265.7 | 392.6 | 345.3
1943 | 1769 | -5.9 | 0 | 0 | 248.5 | 246.9 | 222.5 | 214.4 | 234.6 | 37.3 | -12.5 | 57.9 | 4 | 7.8 | 2.6 | 48.7 | 57.6 | 39.7 | 55 | 37.1 | 74.2 | 63 | 59.5 | 69.4 | 66.6 | 280.3 | 307.9 | 321.5 | 319.9 | 266 | 225.1 | 295.3 | 265.4 | 392.3 | 345.1
1944 | 1770 | -6.1 | 0 | 0 | 248.4 | 246.8 | 222.4 | 214.3 | 235.5 | 37.3 | -12.5 | 57.8 | 4 | 7.8 | 2.5 | 48.7 | 58.4 | 39.6 | 55 | 37.1 | 74.4 | 62.6 | 59.5 | 69.4 | 66.7 | 280.2 | 307.8 | 321.2 | 319.7 | 265.7 | 224.9 | 295.1 | 265.2 | 392 | 344.9
1945 | 1771 | -6.2 | 0 | 0 | 248.2 | 246.6 | 222.3 | 214.1 | 236.5 | 37.3 | -12.5 | 57.8 | 4.1 | 7.8 | 2.5 | 48.6 | 58.4 | 39.6 | 54.4 | 37.1 | 74.6 | 62.6 | 59.2 | 69.5 | 66.7 | 280.2 | 307.7 | 321 | 319.4 | 265.5 | 224.7 | 294.9 | 265 | 391.6 | 344.7
1946 | 1772 | -6.1 | 0 | 0 | 247.9 | 246.3 | 222.1 | 213.9 | 237 | 37.3 | -12.5 | 57.7 | 3.8 | 7.8 | 2.5 | 48.6 | 57.5 | 39.6 | 54.6 | 37.1 | 74.9 | 63.1 | 59.1 | 69.6 | 66.7 | 280.2 | 307.6 | 320.9 | 319.2 | 265.3 | 224.5 | 294.7 | 264.7 | 391.3 | 344.5
1947 | 1773 | -6.1 | 0 | 0 | 247.7 | 246 | 222 | 213.7 | 236.9 | 37.3 | -12.5 | 57.6 | 3.8 | 7.7 | 2.5 | 48.5 | 56.6 | 39.6 | 54.6 | 37 | 75 | 63.3 | 59.4 | 69.6 | 66.8 | 280 | 307.5 | 320.6 | 319 | 265.1 | 224.3 | 294.5 | 264.5 | 391 | 344.3
1948 | 1774 | -6 | 0 | 0 | 247.6 | 245.8 | 221.8 | 213.7 | 236.7 | 37.3 | -12.5 | 57.6 | 4.1 | 7.7 | 2.5 | 48.5 | 56.4 | 39.5 | 54.4 | 36.9 | 74.9 | 63.3 | 59.8 | 69.7 | 66.8 | 280.1 | 307.4 | 320.4 | 318.7 | 265 | 224.1 | 294.3 | 264.2 | 390.7 | 344.1
1949 | 1775 | -6 | 0 | 0 | 247.3 | 245.6 | 221.5 | 213.6 | 236 | 37.3 | -12.5 | 57.5 | 3.8 | 7.6 | 2.5 | 48.4 | 56.3 | 39.5 | 54.6 | 36.8 | 75 | 63.1 | 59.5 | 69.7 | 66.9 | 280.3 | 307.3 | 320.2 | 318.5 | 264.8 | 223.9 | 294.1 | 264 | 390.4 | 343.9
1950 | 1776 | -6 | 0 | 0 | 247 | 245.7 | 221.3 | 213.6 | 235.9 | 37.4 | -12.5 | 57.5 | 3.9 | 7.6 | 2.5 | 48.4 | 56.1 | 39.6 | 54.4 | 36.8 | 75.2 | 62.7 | 59.5 | 69.8 | 67 | 280.4 | 307.2 | 320 | 318.3 | 264.7 | 223.7 | 294 | 263.8 | 390 | 343.7
1951 | 1777 | -6 | 0 | 0 | 246.9 | 245.6 | 221.1 | 213.4 | 235.7 | 37.3 | -12.5 | 57.4 | 3.9 | 7.6 | 2.5 | 48.4 | 55.7 | 39.6 | 54.3 | 36.9 | 75.1 | 62.9 | 60 | 69.7 | 67.1 | 280.3 | 307.1 | 319.8 | 318 | 264.5 | 223.4 | 293.8 | 263.5 | 389.7 | 343.5
1952 | 1778 | -6 | 0 | 0 | 246.8 | 245.2 | 220.9 | 213.2 | 235.7 | 37.3 | -12.5 | 57.3 | 3.7 | 7.6 | 2.5 | 48.3 | 55.9 | 39.4 | 54.5 | 36.9 | 74.7 | 62.2 | 59.8 | 69.6 | 67.1 | 280.3 | 307 | 319.6 | 317.8 | 264.4 | 223.3 | 293.6 | 263.3 | 389.4 | 343.3
1953 | 1779 | -6.2 | 0 | 0 | 246.6 | 244.7 | 220.7 | 213.1 | 235.8 | 37.3 | -12.5 | 57.3 | 3.6 | 7.5 | 2.5 | 48.3 | 55.6 | 39.2 | 54.9 | 36.9 | 74.3 | 61.6 | 59.7 | 69.4 | 67.1 | 280.2 | 306.9 | 319.4 | 317.6 | 264.2 | 223.1 | 293.4 | 263.1 | 389.1 | 343.1
1954 | 1780 | -6.2 | 0 | 0 | 246.5 | 244.6 | 220.6 | 212.8 | 235.5 | 37.2 | -12.5 | 57.2 | 4 | 7.5 | 2.5 | 48.2 | 55.2 | 39 | 55.6 | 36.9 | 74.2 | 61.8 | 59.8 | 69.2 | 67.1 | 280.3 | 306.8 | 319.2 | 317.4 | 263.9 | 222.9 | 293.2 | 262.8 | 388.8 | 342.8
1955 | 1781 | -6.2 | 0 | 0 | 246.4 | 244.4 | 220.5 | 212.7 | 235.4 | 37.2 | -12.4 | 57.2 | 4.1 | 174.5 | 1.2 | 48.2 | 54.8 | 38.9 | 56.3 | 36.9 | 74 | 62.4 | 59.9 | 69.3 | 67.1 | 280.6 | 306.7 | 319 | 317.1 | 263.7 | 222.7 | 293 | 262.6 | 388.5 | 342.6
1956 | 1782 | -6.2 | 0 | 0 | 246.3 | 243.7 | 220.3 | 212.4 | 235.6 | 37.2 | 2.4 | 57.1 | 3.9 | 252 | 0.1 | 48.2 | 53.8 | 39.1 | 56.3 | 36.8 | 73.4 | 62.7 | 60.1 | 69.2 | 67.1 | 280.6 | 306.6 | 318.8 | 316.9 | 263.5 | 222.5 | 292.8 | 262.3 | 388.1 | 342.4
1957 | 1783 | -6 | 0 | 0 | 246.3 | 243.6 | 220.1 | 212.2 | 235.8 | 37.1 | 18.4 | 57.1 | 3.9 | 226.3 | 1.6 | 48.1 | 52.9 | 39.2 | 56.1 | 36.9 | 73.2 | 62.8 | 60.2 | 69.1 | 67.2 | 280.6 | 306.5 | 318.6 | 316.7 | 263.3 | 222.3 | 292.7 | 262.1 | 387.8 | 342.2
1958 | 1784 | -5.8 | 0 | 0 | 246.1 | 243.4 | 219.9 | 211.9 | 235.2 | 37.1 | 18.4 | 57 | 4 | 211.1 | 4.7 | 48.1 | 52.7 | 39.5 | 56.2 | 36.9 | 72.8 | 63.3 | 60.5 | 69 | 67.3 | 280.7 | 306.4 | 318.5 | 316.4 | 263.1 | 222.1 | 292.5 | 261.9 | 387.5 | 342
1959 | 1785 | -5.8 | 0 | 0 | 246 | 243.1 | 219.7 | 211.7 | 233.8 | 37.1 | 18.4 | 57 | 4 | 222.2 | 5 | 48 | 53.7 | 40.7 | 60 | 36.9 | 72.7 | 63.6 | 61.1 | 69 | 67.3 | 280.5 | 306.3 | 318.3 | 316.2 | 262.9 | 221.9 | 292.3 | 261.6 | 387.2 | 341.8
1960 | 1786 | -5.9 | 0 | 0 | 245.8 | 242.9 | 219.4 | 211.6 | 232.7 | 37.1 | 20 | 56.9 | 4.1 | 252 | 4.9 | 48 | 54.7 | 40.8 | 58.3 | 36.9 | 73.2 | 63.2 | 61.7 | 69.2 | 67.4 | 280.4 | 306.2 | 318.1 | 316 | 262.7 | 221.7 | 292.2 | 261.4 | 386.9 | 341.6
1961 | 1787 | -6 | 0 | 0 | 245.5 | 243 | 219.2 | 211.5 | 231.8 | 37.1 | 31.4 | 56.9 | 4.3 | 265.2 | 5.2 | 48 | 54.8 | 40.5 | 57.6 | 36.9 | 73.1 | 63.1 | 62.4 | 69.1 | 67.5 | 280.6 | 306.1 | 317.9 | 315.8 | 262.5 | 221.5 | 292 | 261.2 | 386.6 | 341.4
1962 | 1788 | -6 | 0 | 0 | 245.2 | 243.1 | 219 | 211.3 | 231.1 | 37.1 | 37.5 | 56.9 | 4.2 | 228.9 | 6.7 | 48 | 54.1 | 40.2 | 58.1 | 36.9 | 72.7 | 62.9 | 61.9 | 69 | 67.6 | 280.6 | 306 | 317.7 | 315.5 | 262.3 | 221.4 | 291.8 | 261 | 386.3 | 341.2
1963 | 1789 | -6.1 | 0 | 0 | 245 | 242.9 | 218.7 | 211.1 | 230.7 | 37.1 | 39.4 | 56.8 | 4.3 | 243.7 | 7.4 | 48 | 53.7 | 39.8 | 57 | 36.8 | 72.4 | 63.7 | 61.7 | 68.9 | 67.7 | 280.5 | 305.9 | 317.5 | 315.3 | 262.2 | 221.2 | 291.6 | 260.7 | 385.9 | 341
1964 | 1790 | -6.2 | 0 | 0 | 245 | 242.6 | 218.5 | 211 | 230.1 | 37.1 | 40 | 56.7 | 4.2 | 230.6 | 8 | 47.9 | 53.7 | 39.5 | 57.4 | 36.8 | 72.6 | 63.4 | 61.9 | 68.8 | 67.8 | 280.4 | 305.8 | 317.3 | 315.1 | 262 | 221 | 291.4 | 260.5 | 385.6 | 340.8
1965 | 1791 | -6.1 | 0 | 0 | 245 | 242.6 | 218.3 | 210.9 | 229.3 | 37 | 40.3 | 56.6 | 3.9 | 231 | 7.6 | 47.9 | 53 | 39.2 | 57.9 | 36.7 | 72.8 | 63.6 | 62.3 | 68.8 | 67.8 | 280.4 | 305.7 | 317.1 | 314.9 | 261.8 | 220.8 | 291.2 | 260.3 | 385.3 | 340.6
1966 | 1792 | -6.1 | 0 | 0 | 244.9 | 242.6 | 218.1 | 210.7 | 229.1 | 37 | 40.4 | 56.6 | 3.7 | 236.3 | 6.5 | 48 | 52.8 | 39 | 57.5 | 36.6 | 72.7 | 63.8 | 62 | 68.9 | 67.7 | 280.3 | 305.6 | 316.9 | 314.7 | 261.6 | 220.6 | 291 | 260.1 | 385 | 340.4
1967 | 1793 | -6 | 0 | 0 | 244.7 | 242.6 | 217.9 | 210.5 | 228.7 | 36.9 | 40.5 | 56.6 | 3.2 | 233.5 | 6.6 | 48 | 51.6 | 38.7 | 56.6 | 36.6 | 72.8 | 64 | 61.5 | 68.9 | 67.6 | 280.4 | 305.4 | 316.7 | 314.4 | 261.4 | 220.5 | 290.8 | 259.9 | 384.7 | 340.2
1968 | 1794 | -6.1 | 0 | 0 | 244.4 | 242.4 | 217.8 | 210.5 | 228.6 | 36.9 | 40.4 | 56.5 | 3.4 | 240.1 | 7.5 | 48 | 50.8 | 38.5 | 54.6 | 36.5 | 73 | 63.6 | 61.7 | 69 | 67.2 | 280.7 | 305.3 | 316.5 | 314.2 | 261.2 | 220.3 | 290.6 | 259.6 | 384.4 | 340
1969 | 1795 | -6.1 | 0 | 0 | 244.2 | 242.1 | 217.7 | 210.4 | 228.8 | 36.9 | 40.4 | 56.5 | 3.8 | 234 | 7.8 | 48 | 50.2 | 38.3 | 55.1 | 36.5 | 72.9 | 63.2 | 61.9 | 69 | 67.3 | 280.7 | 305.2 | 316.3 | 314 | 261 | 220 | 290.4 | 259.4 | 384.1 | 339.8
1970 | 1796 | -6.1 | 0 | 0 | 243.9 | 241.7 | 217.6 | 210.3 | 229.5 | 36.9 | 40.2 | 56.4 | 3.6 | 233.6 | 7.8 | 48.1 | 50 | 38.2 | 55.6 | 36.5 | 72.8 | 62.8 | 62.1 | 69 | 67.5 | 280.9 | 305.1 | 316.1 | 313.8 | 260.8 | 219.8 | 290.2 | 259.2 | 383.8 | 339.6
1971 | 1797 | -6 | 0 | 0 | 243.6 | 241.5 | 217.5 | 210.1 | 229.1 | 36.9 | 39.8 | 56.4 | 3.6 | 241.4 | 7.3 | 48.1 | 49.6 | 38.1 | 55.7 | 36.6 | 72.4 | 63.1 | 62.4 | 68.9 | 67.6 | 280.8 | 305 | 315.9 | 313.5 | 260.6 | 219.6 | 290 | 258.9 | 383.5 | 339.4
1972 | 1798 | -5.6 | 0 | 0 | 243.3 | 241.3 | 217.5 | 210 | 228.5 | 36.8 | 39.4 | 56.3 | 3.9 | 239.5 | 7.1 | 48 | 49.7 | 37.8 | 55.6 | 36.5 | 72.2 | 63.5 | 62.2 | 68.9 | 67.4 | 280.4 | 304.9 | 315.7 | 313.3 | 260.3 | 219.4 | 289.8 | 258.7 | 383.2 | 339.2
1973 | 1799 | -5.5 | 0 | 0 | 243.1 | 240.9 | 217.3 | 209.9 | 229.1 | 36.9 | 38.9 | 56.3 | 3.6 | 236.8 | 6.9 | 48 | 49.2 | 37.6 | 54.8 | 36.5 | 72.3 | 63.2 | 61.6 | 68.9 | 67.7 | 280.5 | 304.8 | 315.5 | 313.1 | 260.1 | 219.2 | 289.6 | 258.5 | 382.9 | 339
1974 | 1800 | -5.8 | 0 | 0 | 242.7 | 240.8 | 217.1 | 209.7 | 229 | 36.9 | 38.3 | 56.2 | 3.6 | 236.8 | 6.5 | 48 | 48.3 | 37.4 | 53.7 | 36.4 | 72.4 | 63.2 | 60.3 | 69 | 67.8 | 280.7 | 304.7 | 315.3 | 312.8 | 259.9 | 219 | 289.4 | 258.3 | 382.5 | 338.8
1975 | 1801 | -6.1 | 0 | 0 | 242.5 | 240.6 | 216.8 | 209.6 | 229.5 | 36.9 | 37.5 | 56.2 | 3.7 | 238.6 | 6 | 48 | 47.6 | 37.2 | 55 | 36.3 | 72.5 | 63.2 | 59 | 69 | 67.9 | 280.9 | 304.6 | 315.1 | 312.6 | 259.7 | 218.8 | 289.3 | 258.1 | 382.2 | 338.6
1976 | 1802 | -6.2 | 0 | 0 | 242.4 | 240.5 | 216.6 | 209.4 | 229.9 | 36.9 | 36.6 | 56.1 | 3.6 | 237.4 | 5.9 | 48 | 46.9 | 37 | 55.2 | 36.2 | 72.4 | 63.1 | 57.7 | 69 | 67.9 | 280.8 | 304.5 | 315 | 312.4 | 259.5 | 218.7 | 289.1 | 257.8 | 381.9 | 338.4
1977 | 1803 | -6 | 0 | 0 | 242.4 | 240.2 | 216.4 | 209.3 | 229.8 | 36.8 | 35.7 | 56 | 3.7 | 241 | 6 | 48 | 47.1 | 36.8 | 55.4 | 36.2 | 72.6 | 63.3 | 59.2 | 69 | 67.7 | 280.8 | 304.4 | 314.8 | 312.2 | 259.4 | 218.5 | 288.9 | 257.6 | 381.6 | 338.2
1978 | 1804 | -5.8 | 0 | 0 | 242.2 | 240 | 216.2 | 209.3 | 229.8 | 36.8 | 34.6 | 55.9 | 4.1 | 238.7 | 6.1 | 48 | 47.7 | 36.7 | 55.5 | 36.1 | 72.9 | 62.4 | 60 | 69 | 67.4 | 280.7 | 304.3 | 314.6 | 311.9 | 259.1 | 218.3 | 288.7 | 257.4 | 381.3 | 338
1979 | 1805 | -5.8 | 0 | 0 | 242 | 239.9 | 216.1 | 209.1 | 230 | 36.8 | 33.5 | 55.8 | 4.1 | 247.3 | 6.1 | 47.9 | 47.5 | 36.5 | 55.5 | 36.1 | 72.9 | 61.2 | 59.1 | 69 | 67.4 | 280.5 | 304.2 | 314.4 | 311.7 | 258.9 | 218.2 | 288.5 | 257.2 | 381 | 337.8
1980 | 1806 | -6 | 0 | 0 | 241.8 | 239.8 | 216 | 209 | 230.1 | 36.8 | 32.4 | 55.8 | 3.5 | 239.4 | 6.2 | 47.9 | 47.2 | 36.4 | 55.2 | 36 | 72.6 | 61.1 | 58.3 | 68.8 | 67.4 | 280.5 | 304.1 | 314.2 | 311.5 | 258.7 | 218 | 288.3 | 257 | 380.7 | 337.6
1981 | 1807 | -6.1 | 0 | 0 | 241.5 | 239.6 | 215.8 | 208.9 | 230 | 36.7 | 31.2 | 55.7 | 3.6 | 237.7 | 6 | 47.9 | 47 | 36.3 | 54.9 | 36 | 72.7 | 61.3 | 59 | 68.8 | 67.5 | 280.6 | 304 | 314 | 311.3 | 258.5 | 217.8 | 288.1 | 256.8 | 380.4 | 337.4
1982 | 1808 | -6.1 | 0 | 0 | 241.2 | 239.3 | 215.5 | 208.7 | 230 | 36.7 | 29.9 | 55.7 | 3.8 | 248.5 | 5.7 | 47.9 | 47 | 36.2 | 55.5 | 35.9 | 72.5 | 61.1 | 59.5 | 68.8 | 67.6 | 280.7 | 303.9 | 313.8 | 311 | 258.3 | 217.6 | 287.9 | 256.5 | 380.1 | 337.2
1983 | 1809 | -6.1 | 0 | 0 | 240.8 | 239.1 | 215.3 | 208.5 | 230.2 | 36.7 | 28.6 | 55.6 | 4.1 | 260.6 | 4.7 | 47.9 | 46.8 | 36 | 56 | 35.8 | 72.2 | 61 | 60.3 | 68.7 | 67.7 | 280.8 | 303.8 | 313.6 | 310.8 | 258.1 | 217.4 | 287.7 | 256.3 | 379.8 | 337
1984 | 1810 | -6.1 | 0 | 0 | 240.6 | 238.9 | 215.2 | 208.3 | 230 | 36.7 | 27.3 | 55.6 | 3.7 | 256 | 4 | 47.8 | 46.6 | 35.9 | 55.9 | 35.8 | 72 | 61 | 60.6 | 68.6 | 67.6 | 280.7 | 303.7 | 313.4 | 310.6 | 257.8 | 217.2 | 287.5 | 256.1 | 379.5 | 336.8
1985 | 1811 | -6 | 0 | 0 | 240.6 | 238.8 | 215 | 208.2 | 229.6 | 36.7 | 26.1 | 55.6 | 3.9 | 252.2 | 3.4 | 47.8 | 46.4 | 35.9 | 56.6 | 35.7 | 71.7 | 60.8 | 60.8 | 68.5 | 67.8 | 280.7 | 303.6 | 313.3 | 310.4 | 257.6 | 217 | 287.3 | 255.9 | 379.2 | 336.6
1986 | 1812 | -5.9 | 0 | 0 | 240.5 | 238.4 | 215 | 208.1 | 229.3 | 36.6 | 24.8 | 55.6 | 4.1 | 248.5 | 3.4 | 47.8 | 46.1 | 36 | 56.7 | 35.7 | 71.5 | 60.5 | 60.9 | 68.5 | 67.6 | 280.8 | 303.5 | 313.1 | 310.1 | 257.5 | 216.8 | 287.1 | 255.7 | 378.9 | 336.4
1987 | 1813 | -5.7 | 0 | 0 | 240.4 | 238 | 214.9 | 207.9 | 229.3 | 36.6 | 23.6 | 55.6 | 3.7 | 247.3 | 4.4 | 47.7 | 45.7 | 35.9 | 56.3 | 35.6 | 71.6 | 60.3 | 60.3 | 68.5 | 67.7 | 280.8 | 303.4 | 312.9 | 309.9 | 257.3 | 216.7 | 286.9 | 255.5 | 378.6 | 336.2
1988 | 1814 | -5.9 | 0 | 0 | 240.4 | 237.8 | 214.8 | 207.7 | 229.5 | 36.6 | 22.5 | 55.5 | 3.8 | 235.3 | 4.9 | 47.7 | 45.8 | 35.9 | 56.2 | 35.7 | 71.5 | 60.6 | 59.6 | 68.5 | 67.8 | 280.7 | 303.3 | 312.7 | 309.7 | 257.1 | 216.5 | 286.7 | 255.3 | 378.3 | 336
1989 | 1815 | -5.9 | 0 | 0 | 240.2 | 237.4 | 214.6 | 207.6 | 229.7 | 36.5 | 21.4 | 55.5 | 3.8 | 244.5 | 5.1 | 47.7 | 45.7 | 35.8 | 55.4 | 35.7 | 71.5 | 60.9 | 60.3 | 68.5 | 67.9 | 280.9 | 303.2 | 312.5 | 309.5 | 256.9 | 216.4 | 286.5 | 255.1 | 378 | 335.8
1990 | 1816 | -6.1 | 0 | 0 | 239.8 | 237.3 | 214.4 | 207.5 | 229.7 | 36.5 | 20.4 | 55.4 | 3.8 | 249.8 | 5.5 | 47.7 | 45.7 | 35.7 | 54.8 | 35.7 | 71.7 | 61.4 | 60.1 | 68.6 | 68 | 280.9 | 303.1 | 312.3 | 309.3 | 256.8 | 216.2 | 286.4 | 254.8 | 377.7 | 335.6
1991 | 1817 | -6.1 | 0 | 0 | 239.5 | 237.3 | 214.3 | 207.5 | 229.6 | 36.5 | 19.4 | 55.4 | 3.6 | 252.8 | 5.6 | 47.7 | 45.7 | 35.7 | 54 | 35.6 | 71.9 | 61.7 | 61.2 | 68.6 | 68.1 | 280.9 | 303 | 312.1 | 309.1 | 256.6 | 216.1 | 286.2 | 254.7 | 377.4 | 335.4
1992 | 1818 | -6.3 | 0 | 0 | 239.4 | 237.3 | 214.2 | 207.3 | 229.8 | 36.4 | 18.5 | 55.3 | 3.5 | 265.2 | 5.3 | 47.7 | 45.6 | 35.8 | 53.3 | 35.6 | 72 | 61.4 | 61.9 | 68.7 | 68 | 280.8 | 302.9 | 312 | 308.8 | 256.4 | 215.9 | 286 | 254.5 | 377.1 | 335.2
1993 | 1819 | -6.2 | 0 | 0 | 239.4 | 237.1 | 214 | 207.1 | 230.1 | 36.4 | 17.7 | 55.3 | 3.5 | 259.8 | 5.3 | 47.7 | 45.7 | 35.9 | 53.8 | 35.6 | 72 | 61.4 | 61.4 | 68.7 | 68 | 280.8 | 302.8 | 311.8 | 308.6 | 256.2 | 215.8 | 285.8 | 254.2 | 376.8 | 335
1994 | 1820 | -6.2 | 0 | 0 | 239.2 | 236.9 | 214 | 206.8 | 230.2 | 36.4 | 17 | 55.3 | 3.8 | 257.1 | 5.2 | 47.6 | 45.4 | 35.8 | 53.1 | 35.6 | 71.8 | 61.6 | 60.9 | 68.7 | 67.9 | 280.6 | 302.7 | 311.6 | 308.4 | 256 | 215.6 | 285.7 | 254.1 | 376.5 | 334.8
1995 | 1821 | -6.1 | 0 | 0 | 239.2 | 236.7 | 213.8 | 206.6 | 230.6 | 36.4 | 16.3 | 55.3 | 3.8 | 254.8 | 5.3 | 47.6 | 45.4 | 35.8 | 52.3 | 35.6 | 71.9 | 61.5 | 60.4 | 68.6 | 67.8 | 280.7 | 302.5 | 311.4 | 308.2 | 255.9 | 215.4 | 285.5 | 253.9 | 376.2 | 334.6
1996 | 1822 | -6 | 0 | 0 | 239.1 | 236.2 | 213.7 | 206.4 | 231 | 36.4 | 15.7 | 55.3 | 3.6 | 252.6 | 5.1 | 47.6 | 45.2 | 35.8 | 51.5 | 35.6 | 71.9 | 61.6 | 60.5 | 68.5 | 67.8 | 280.9 | 302.4 | 311.2 | 308 | 255.7 | 215.2 | 285.3 | 253.6 | 376 | 334.4
1997 | 1823 | -5.9 | 0 | 0 | 239 | 235.9 | 213.6 | 206.3 | 231.4 | 36.3 | 15.2 | 55.3 | 3.7 | 245 | 4.7 | 47.6 | 45.1 | 35.8 | 51.2 | 35.6 | 72.4 | 61.6 | 59.4 | 68.6 | 67.7 | 280.9 | 302.4 | 311 | 307.8 | 255.5 | 215.1 | 285.1 | 253.4 | 375.7 | 334.2
1998 | 1824 | -6 | 0 | 0 | 238.8 | 235.8 | 213.3 | 206.1 | 231.6 | 36.3 | 14.8 | 55.3 | 3.8 | 244.3 | 4.6 | 47.6 | 45.3 | 36 | 51.5 | 35.6 | 72.6 | 62 | 60.3 | 68.5 | 67.7 | 281 | 302.3 | 310.9 | 307.5 | 255.3 | 214.9 | 285 | 253.3 | 375.4 | 334
1999 | 1825 | -6.1 | 0 | 0 | 238.6 | 235.7 | 213.1 | 206 | 231.6 | 36.3 | 14.4 | 55.3 | 4.1 | 245.8 | 4.7 | 47.5 | 45.2 | 36.1 | 51.5 | 35.5 | 72.4 | 62.2 | 61 | 68.5 | 67.8 | 280.9 | 302.1 | 310.7 | 307.3 | 255.1 | 214.8 | 284.8 | 253.1 | 375.1 | 333.8
2000 | 1826 | -6.1 | 0 | 0 | 238.2 | 235.6 | 213 | 205.8 | 231.5 | 36.3 | 14.2 | 55.3 | 3.9 | 247 | 4.9 | 47.5 | 45 | 36 | 51.2 | 35.5 | 72.6 | 61.9 | 61 | 68.6 | 67.6 | 280.6 | 302 | 310.5 | 307.1 | 255 | 214.6 | 284.6 | 252.8 | 374.8 | 333.6
2001 | 1827 | -6 | 0 | 0 | 238 | 235.6 | 212.8 | 205.7 | 231.3 | 36.2 | 14 | 55.3 | 3.7 | 239.9 | 4.8 | 47.5 | 45.3 | 35.9 | 51.3 | 35.4 | 72.3 | 62.1 | 61.1 | 68.4 | 67.7 | 280.6 | 301.9 | 310.3 | 306.9 | 254.8 | 214.4 | 284.4 | 252.6 | 374.5 | 333.4
2002 | 1828 | -6.1 | 0 | 0 | 237.9 | 235.7 | 212.7 | 205.6 | 231.3 | 36.2 | 13.8 | 55.3 | 3.8 | 242.5 | 5 | 47.4 | 44.9 | 35.8 | 52.9 | 35.4 | 72.3 | 62.3 | 61.6 | 68.4 | 67.8 | 280.8 | 301.8 | 310.1 | 306.7 | 254.7 | 214.3 | 284.3 | 252.4 | 374.2 | 333.3
2003 | 1829 | -6.1 | 0 | 0 | 237.7 | 235.4 | 212.5 | 205.5 | 231.7 | 36.2 | 13.7 | 55.3 | 3.9 | 250.6 | 5 | 47.4 | 44.5 | 35.6 | 54 | 35.3 | 72.3 | 62.1 | 60.7 | 68.4 | 67.8 | 281 | 301.7 | 309.9 | 306.5 | 254.5 | 214.1 | 284.1 | 252.2 | 373.9 | 333.1
2004 | 1830 | -5.9 | 0 | 0 | 237.5 | 234.9 | 212.3 | 205.4 | 232.2 | 36.1 | 13.7 | 55.2 | 3.5 | 249.5 | 5 | 47.4 | 44.4 | 35.6 | 54.4 | 35.3 | 72.2 | 62 | 60.8 | 68.5 | 67.9 | 281.1 | 301.6 | 309.8 | 306.3 | 254.4 | 214 | 283.9 | 252 | 373.6 | 332.9
2005 | 1831 | -5.8 | 0 | 0 | 237.4 | 234.6 | 212.1 | 205.3 | 232.6 | 36.1 | 13.8 | 55.2 | 3.7 | 237 | 5.1 | 47.3 | 44.7 | 35.5 | 54.4 | 35.3 | 72.3 | 61.9 | 60.6 | 68.5 | 68 | 281 | 301.5 | 309.6 | 306 | 254.2 | 213.9 | 283.7 | 251.8 | 373.4 | 332.7
2006 | 1832 | -5.9 | 0 | 0 | 237.3 | 234.6 | 211.9 | 205.1 | 233.1 | 36.1 | 13.9 | 55.1 | 3.2 | 231.5 | 5.3 | 47.3 | 44.8 | 35.6 | 54.2 | 35.3 | 72.4 | 61.9 | 60.4 | 68.5 | 67.9 | 280.7 | 301.4 | 309.4 | 305.8 | 254 | 213.8 | 283.6 | 251.6 | 373 | 332.5
2007 | 1833 | -5.9 | 0 | 0 | 237.1 | 234.4 | 211.8 | 205 | 233.5 | 36 | 14.1 | 55.1 | 3.7 | 249.6 | 5.1 | 47.3 | 44.4 | 35.5 | 53.8 | 35.4 | 72.6 | 61.7 | 59.3 | 68.6 | 67.9 | 280.7 | 301.3 | 309.2 | 305.6 | 253.8 | 213.6 | 283.5 | 251.5 | 372.8 | 332.3
2008 | 1834 | -6 | 0 | 0 | 236.9 | 234 | 211.7 | 204.9 | 233.9 | 36 | 14.3 | 55 | 3.5 | 252.1 | 5.1 | 47.3 | 43.9 | 35.4 | 54.1 | 35.4 | 72.6 | 60.9 | 57.8 | 68.6 | 68 | 280.9 | 301.2 | 309 | 305.4 | 253.6 | 213.5 | 283.2 | 251.2 | 372.5 | 332.1
2009 | 1835 | -6 | 0 | 0 | 236.8 | 233.8 | 211.6 | 204.7 | 234.1 | 36 | 14.6 | 54.9 | 3.3 | 237 | 6.4 | 47.3 | 43.9 | 35.3 | 54.6 | 35.5 | 72.7 | 60.7 | 58.3 | 68.6 | 68.1 | 280.9 | 301.1 | 308.9 | 305.2 | 253.5 | 213.3 | 283.1 | 251 | 372.2 | 331.9
2010 | 1836 | -6 | 0 | 0 | 236.5 | 233.7 | 211.5 | 204.6 | 234.3 | 35.9 | 14.9 | 54.9 | 3.7 | 250 | 7.7 | 47.3 | 43.6 | 35.2 | 54.7 | 35.4 | 72.4 | 60.7 | 60.3 | 68.5 | 68.1 | 280.9 | 301 | 308.7 | 305 | 253.3 | 213.2 | 282.9 | 250.8 | 371.9 | 331.7
2011 | 1837 | -5.8 | 0 | 0 | 236 | 233.7 | 211.4 | 204.5 | 234.4 | 35.9 | 15.2 | 54.8 | 3.8 | 250 | 7.7 | 47.2 | 43.5 | 35.2 | 53.7 | 35.4 | 72.6 | 60.8 | 60 | 68.5 | 68.1 | 280.8 | 300.9 | 308.5 | 304.7 | 253.2 | 213.1 | 282.7 | 250.6 | 371.6 | 331.5
2012 | 1838 | -5.8 | 0 | 0 | 235.5 | 233.7 | 211.3 | 204.4 | 234.6 | 35.9 | 15.6 | 54.7 | 4 | 238.9 | 7.2 | 47.2 | 43.4 | 35.1 | 52.8 | 35.4 | 72.6 | 60.5 | 60.6 | 68.5 | 68.2 | 280.9 | 300.8 | 308.3 | 304.5 | 253 | 212.9 | 282.6 | 250.4 | 371.3 | 331.3
2013 | 1839 | -5.8 | 0 | 0 | 235.2 | 233.7 | 211.2 | 204.1 | 234.7 | 35.8 | 16 | 54.6 | 3.8 | 243.6 | 7.2 | 47.2 | 43.6 | 35.1 | 53.3 | 35.5 | 72.4 | 60.6 | 60.2 | 68.4 | 68.4 | 281 | 300.7 | 308.1 | 304.3 | 252.8 | 212.8 | 282.4 | 250.2 | 371.1 | 331.1
2014 | 1840 | -5.9 | 0 | 0 | 235 | 233.6 | 211.1 | 203.8 | 234.8 | 35.7 | 16.4 | 54.5 | 3.8 | 242.3 | 7.2 | 47.1 | 43.5 | 35 | 53.3 | 35.4 | 72.9 | 61.1 | 60 | 68.5 | 68.4 | 280.8 | 300.6 | 308 | 304.1 | 252.7 | 212.7 | 282.2 | 250 | 370.8 | 330.9
2015 | 1841 | -5.9 | 0 | 0 | 234.8 | 233.4 | 210.9 | 203.6 | 234.5 | 35.6 | 16.8 | 54.4 | 4.2 | 244.4 | 7.6 | 47.1 | 43.6 | 35 | 53.5 | 35.4 | 73 | 61.5 | 59.9 | 68.6 | 68.6 | 280.8 | 300.5 | 307.8 | 303.9 | 252.5 | 212.5 | 282 | 249.8 | 370.5 | 330.7
2016 | 1842 | -6.1 | 0 | 0 | 234.6 | 233 | 210.7 | 203.4 | 234.1 | 35.5 | 17.2 | 54.4 | 3.9 | 244.8 | 8.3 | 47.1 | 43.8 | 34.9 | 53.3 | 35.4 | 72.9 | 61.1 | 61.3 | 68.6 | 68.6 | 281 | 300.4 | 307.6 | 303.7 | 252.3 | 212.4 | 281.9 | 249.6 | 370.2 | 330.5
2017 | 1843 | -6.2 | 0 | 0 | 234.3 | 232.8 | 210.5 | 203.3 | 233.7 | 35.5 | 17.6 | 54.3 | 3.8 | 248.5 | 8.5 | 47.1 | 43.9 | 34.8 | 52.9 | 35.4 | 73.1 | 60.9 | 61.5 | 68.6 | 68.6 | 280.9 | 300.3 | 307.4 | 303.5 | 252.2 | 212.3 | 281.7 | 249.5 | 369.9 | 330.3
2018 | 1844 | -6 | 0 | 0 | 234.2 | 232.7 | 210.3 | 203.2 | 233.3 | 35.4 | 18 | 54.2 | 3.2 | 251.4 | 8.8 | 47.1 | 43.2 | 34.8 | 53.3 | 35.3 | 73.3 | 60.4 | 60.8 | 68.7 | 68.7 | 280.8 | 300.2 | 307.3 | 303.3 | 252 | 212.2 | 281.5 | 249.3 | 369.6 | 330.1
2019 | 1845 | -5.6 | 0 | 0 | 234.1 | 232.7 | 210.1 | 203 | 233.1 | 35.4 | 18.4 | 54.2 | 3.4 | 250.1 | 9.1 | 47.1 | 43 | 34.7 | 54 | 35.1 | 73.4 | 61 | 59.5 | 68.8 | 68.7 | 280.6 | 300.1 | 307.1 | 303 | 251.8 | 212.1 | 281.3 | 249 | 369.3 | 330
2020 | 1846 | -5.8 | 0 | 0 | 233.8 | 232.7 | 209.9 | 202.8 | 233.2 | 35.4 | 18.7 | 54.1 | 3.6 | 257.1 | 9.1 | 47 | 43.1 | 34.6 | 53.9 | 34.9 | 73.3 | 60.8 | 61.1 | 68.8 | 68.6 | 280.9 | 300 | 306.9 | 302.8 | 251.7 | 211.9 | 281.2 | 248.9 | 369.1 | 329.8
2021 | 1847 | -5.8 | 0 | 0 | 233.6 | 232.6 | 209.9 | 202.7 | 233.4 | 35.3 | 19 | 54 | 3.7 | 257.1 | 8.6 | 47 | 42.4 | 34.5 | 53.7 | 34.9 | 73.1 | 60.3 | 60.1 | 68.8 | 68.8 | 280.9 | 299.9 | 306.7 | 302.6 | 251.5 | 211.8 | 281 | 248.7 | 368.8 | 329.6
2022 | 1848 | -5.9 | 0 | 0 | 233.4 | 232.5 | 209.9 | 202.5 | 233.7 | 35.3 | 19.3 | 54 | 4.1 | 254.2 | 8.4 | 47 | 42.3 | 34.3 | 53.5 | 34.9 | 73 | 59.3 | 61.7 | 68.7 | 68.9 | 280.9 | 299.8 | 306.6 | 302.4 | 251.4 | 211.7 | 280.8 | 248.5 | 368.5 | 329.4
2023 | 1849 | -6 | 0 | 0 | 233.4 | 232.2 | 209.9 | 202.4 | 233.9 | 35.2 | 19.5 | 53.9 | 4.3 | 256.4 | 8.6 | 46.9 | 42.8 | 34.2 | 52.9 | 34.9 | 73.3 | 58.9 | 62.1 | 68.8 | 68.9 | 280.8 | 299.7 | 306.4 | 302.2 | 251.2 | 211.6 | 280.7 | 248.3 | 368.2 | 329.2
2024 | 1850 | -6 | 0 | 0 | 233.4 | 231.9 | 209.8 | 202.3 | 234.1 | 35.2 | 19.8 | 53.9 | 4.1 | 257.6 | 8.7 | 46.9 | 42.9 | 34.1 | 53.3 | 34.9 | 73.1 | 58.2 | 60.6 | 68.7 | 68.8 | 280.9 | 299.6 | 306.2 | 302 | 251 | 211.4 | 280.4 | 248.1 | 367.9 | 329
2025 | 1851 | -6.1 | 0 | 0 | 233.2 | 231.8 | 209.6 | 202.3 | 234.2 | 35.2 | 19.9 | 53.9 | 3.8 | 255 | 8.6 | 46.9 | 42.7 | 34.1 | 53.8 | 34.8 | 73.2 | 58.2 | 58.5 | 68.8 | 68.9 | 280.8 | 299.4 | 306 | 301.8 | 250.9 | 211.3 | 280.3 | 247.9 | 367.7 | 328.8
2026 | 1852 | -6.1 | 0 | 0 | 233.2 | 231.8 | 209.3 | 202.1 | 234.3 | 35.2 | 20.1 | 53.9 | 3.5 | 254.8 | 8.7 | 46.9 | 42.9 | 34 | 53.9 | 34.8 | 73.3 | 58.3 | 59 | 68.9 | 68.6 | 280.7 | 299.4 | 305.9 | 301.6 | 250.8 | 211.2 | 280.2 | 247.7 | 367.4 | 328.6
2027 | 1853 | -6.2 | 0 | 0 | 233.1 | 231.7 | 209.1 | 202 | 234.1 | 35.2 | 20.2 | 53.8 | 3.7 | 259.2 | 8.7 | 46.8 | 42.7 | 33.9 | 54 | 34.8 | 73.6 | 58.5 | 59.4 | 69 | 68.4 | 280.9 | 299.2 | 305.7 | 301.4 | 250.6 | 211.1 | 280 | 247.5 | 367.1 | 328.4
2028 | 1854 | -6.1 | 0 | 0 | 232.9 | 231.6 | 209 | 201.9 | 233.6 | 35.1 | 20.4 | 53.8 | 4 | 259.4 | 8.6 | 46.8 | 42.5 | 33.8 | 53.9 | 34.7 | 73.8 | 58.4 | 59.4 | 69.1 | 68.4 | 281 | 299.1 | 305.5 | 301.1 | 250.5 | 210.9 | 279.8 | 247.3 | 366.8 | 328.2
2029 | 1855 | -6 | 0 | 0 | 232.6 | 231.3 | 208.9 | 201.7 | 233.2 | 35.1 | 20.5 | 53.8 | 3.6 | 256.3 | 8.5 | 46.8 | 42.2 | 33.8 | 54.1 | 34.7 | 73.3 | 58.5 | 59.7 | 69.2 | 68.5 | 280.9 | 299 | 305.3 | 300.9 | 250.3 | 210.8 | 279.6 | 247.1 | 366.5 | 328
2030 | 1856 | -6 | 0 | 0 | 232.3 | 231.1 | 208.8 | 201.6 | 233.1 | 35.1 | 20.5 | 53.7 | 3.6 | 252.5 | 8.1 | 46.7 | 42.1 | 33.7 | 53.9 | 34.7 | 73.5 | 59.3 | 59.5 | 69.2 | 68.4 | 281 | 298.9 | 305.2 | 300.7 | 250.1 | 210.6 | 279.5 | 247 | 366.3 | 327.9
2031 | 1857 | -6 | 0 | 0 | 232.2 | 230.9 | 208.6 | 201.5 | 233.2 | 35.1 | 20.6 | 53.7 | 4.1 | 261.2 | 8 | 46.7 | 41.9 | 33.7 | 54.4 | 34.6 | 73.8 | 59.9 | 59 | 69.3 | 68.5 | 280.9 | 298.8 | 305 | 300.5 | 250 | 210.5 | 279.3 | 246.8 | 366 | 327.7
2032 | 1858 | -5.8 | 0 | 0 | 232 | 230.7 | 208.5 | 201.4 | 233.2 | 35.1 | 20.7 | 53.7 | 3.9 | 252.2 | 8.5 | 46.7 | 41.7 | 33.6 | 54.2 | 34.6 | 74 | 59.8 | 58.7 | 69.4 | 68.7 | 280.7 | 298.7 | 304.8 | 300.3 | 249.8 | 210.3 | 279.1 | 246.6 | 365.7 | 327.5
2033 | 1859 | -6 | 0 | 0 | 231.8 | 230.5 | 208.4 | 201.2 | 233.3 | 35 | 20.7 | 53.7 | 3.8 | 234.7 | 8.2 | 46.7 | 42.1 | 33.6 | 54.5 | 34.6 | 73.9 | 60 | 59.8 | 69.4 | 68.9 | 280.6 | 298.6 | 304.6 | 300.1 | 249.7 | 210.2 | 279 | 246.4 | 365.4 | 327.3
2034 | 1860 | -6 | 0 | 0 | 231.8 | 230.3 | 208.3 | 201 | 233.5 | 35 | 20.8 | 53.6 | 3.8 | 244.3 | 7.9 | 46.7 | 42.8 | 33.6 | 54.5 | 34.6 | 74 | 59.9 | 60.9 | 69.5 | 68.9 | 280.8 | 298.5 | 304.5 | 299.9 | 249.5 | 210 | 278.8 | 246.2 | 365.1 | 327.1
2035 | 1861 | -6 | 0 | 0 | 231.8 | 230.2 | 208.1 | 200.8 | 233.7 | 34.9 | 20.8 | 53.5 | 3.5 | 237.1 | 7.6 | 46.7 | 42.8 | 33.6 | 53.8 | 34.7 | 74 | 59.2 | 61.3 | 69.5 | 69 | 280.9 | 298.4 | 304.3 | 299.7 | 249.3 | 209.8 | 278.7 | 246.1 | 364.9 | 326.9
2036 | 1862 | -6 | 0 | 0 | 231.7 | 229.8 | 207.9 | 200.8 | 233.8 | 34.8 | 20.8 | 53.4 | 3.9 | 251.8 | 6.9 | 46.6 | 42.7 | 33.5 | 52.8 | 34.7 | 74 | 59.4 | 60.2 | 69.5 | 69.1 | 280.9 | 298.3 | 304.1 | 299.5 | 249.1 | 209.6 | 278.5 | 245.8 | 364.6 | 326.7
2037 | 1863 | -6 | 0 | 0 | 231.6 | 229.5 | 207.7 | 200.6 | 233.8 | 34.8 | 20.8 | 53.3 | 3.7 | 233 | 6.5 | 46.6 | 42.9 | 33.6 | 52 | 34.7 | 74.3 | 59.6 | 59.3 | 69.5 | 68.9 | 280.9 | 298.2 | 304 | 299.3 | 249 | 209.4 | 278.4 | 245.7 | 364.3 | 326.5
2038 | 1864 | -6.1 | 0 | 0 | 231.4 | 229.4 | 207.5 | 200.5 | 233.7 | 34.7 | 20.8 | 53.3 | 3.6 | 244.7 | 6.6 | 46.6 | 43.3 | 33.7 | 51.9 | 34.7 | 74.5 | 59.8 | 57.4 | 69.6 | 68.8 | 280.9 | 298.1 | 303.8 | 299.1 | 248.8 | 209.2 | 278.2 | 245.5 | 364.1 | 326.4
2039 | 1865 | -6 | 0 | 0 | 230.9 | 229.1 | 207.4 | 200.4 | 233.7 | 34.7 | 20.9 | 53.3 | 3.6 | 260.2 | 6.2 | 46.5 | 43.7 | 33.9 | 51.3 | 34.7 | 74.7 | 59.7 | 58.3 | 69.7 | 68.8 | 281 | 298 | 303.6 | 298.9 | 248.7 | 209.1 | 278 | 245.3 | 363.8 | 326.2
2040 | 1866 | -5.9 | 0 | 0 | 230.7 | 229 | 207.3 | 200.4 | 233.7 | 34.6 | 20.9 | 53.3 | 3.6 | 240.1 | 6.2 | 46.5 | 43.2 | 33.8 | 51.1 | 34.7 | 74.7 | 59.6 | 57.1 | 69.7 | 68.9 | 281 | 297.9 | 303.4 | 298.7 | 248.5 | 208.9 | 277.9 | 245.1 | 363.5 | 326
2041 | 1867 | -5.8 | 0 | 0 | 230.5 | 228.8 | 207.1 | 200.2 | 233.6 | 34.6 | 20.9 | 53.2 | 3.5 | 246.8 | 6.3 | 46.5 | 43.6 | 33.7 | 50.7 | 34.7 | 74.2 | 59.7 | 54.5 | 69.7 | 68.9 | 280.8 | 297.8 | 303.3 | 298.4 | 248.4 | 208.8 | 277.7 | 244.9 | 363.3 | 325.8
2042 | 1868 | -5.6 | 0 | 0 | 230.4 | 228.8 | 207 | 200 | 233.4 | 34.6 | 20.9 | 53.2 | 3.4 | 261.4 | 6 | 46.5 | 44 | 33.6 | 51.2 | 34.6 | 74.2 | 59.8 | 51.5 | 69.6 | 68.8 | 280.7 | 297.7 | 303.1 | 298.2 | 248.2 | 208.6 | 277.5 | 244.7 | 363 | 325.6
2043 | 1869 | -5.7 | 0 | 0 | 230.2 | 228.7 | 206.9 | 199.9 | 233.4 | 34.5 | 20.9 | 53.2 | 3.3 | 250 | 5.3 | 46.4 | 44.2 | 33.6 | 50.3 | 34.5 | 73.9 | 59.9 | 50.9 | 69.5 | 69 | 280.6 | 297.6 | 302.9 | 298 | 248 | 208.5 | 277.4 | 244.5 | 362.7 | 325.4
2044 | 1870 | -6 | 0 | 0 | 229.9 | 228.6 | 206.8 | 199.8 | 233.1 | 34.5 | 20.9 | 53.2 | 3.5 | 233.4 | 4.6 | 46.4 | 44.2 | 33.6 | 50.4 | 34.5 | 74 | 59.3 | 52.9 | 69.4 | 68.8 | 280.9 | 297.5 | 302.8 | 297.8 | 247.8 | 208.3 | 277.2 | 244.3 | 362.4 | 325.2
2045 | 1871 | -6.1 | 0 | 0 | 229.8 | 228.4 | 206.7 | 199.7 | 232.9 | 34.5 | 20.8 | 53.2 | 3.7 | 220.6 | 4.4 | 46.4 | 44.1 | 33.5 | 49.3 | 34.5 | 73.9 | 59 | 53.2 | 69.5 | 68.7 | 280.9 | 297.4 | 302.6 | 297.6 | 247.6 | 208.1 | 277.1 | 244.1 | 362.2 | 325
2046 | 1872 | -6.2 | 0 | 0 | 229.7 | 228.1 | 206.5 | 199.5 | 232.9 | 34.4 | 20.8 | 53.2 | 3.8 | 239.9 | 3.9 | 46.3 | 44.2 | 33.5 | 49.6 | 34.5 | 73.7 | 59.9 | 55.2 | 69.5 | 68.6 | 280.9 | 297.2 | 302.4 | 297.4 | 247.4 | 208 | 276.9 | 244 | 361.9 | 324.8
2047 | 1873 | -6.2 | 0 | 0 | 229.5 | 227.8 | 206.4 | 199.3 | 232.9 | 34.4 | 20.8 | 53.2 | 3.6 | 253.1 | 4 | 46.3 | 44.5 | 33.5 | 50.6 | 34.5 | 74.3 | 60.9 | 52.5 | 69.5 | 68.1 | 280.9 | 297.1 | 302.3 | 297.2 | 247.2 | 207.8 | 276.8 | 243.8 | 361.6 | 324.6
2048 | 1874 | -6.2 | 0 | 0 | 229.2 | 227.7 | 206.3 | 199.2 | 232.7 | 34.3 | 20.8 | 53.2 | 3.8 | 244.2 | 4.3 | 46.3 | 44.1 | 33.5 | 51.1 | 34.5 | 74.3 | 61.3 | 50.5 | 69.5 | 67.9 | 280.6 | 297 | 302.1 | 297 | 247.1 | 207.6 | 276.6 | 243.6 | 361.4 | 324.5
2049 | 1875 | -6.2 | 0 | 0 | 229.1 | 227.5 | 206.1 | 199.2 | 232.6 | 34.3 | 20.8 | 53.2 | 3.6 | 253.2 | 4.3 | 46.3 | 43.7 | 33.4 | 51.9 | 34.3 | 74.7 | 61.1 | 51.7 | 69.6 | 68.1 | 280.6 | 296.9 | 301.9 | 296.8 | 246.9 | 207.5 | 276.4 | 243.4 | 361.1 | 324.3
2050 | 1876 | -6.1 | 0 | 0 | 229 | 227.2 | 205.9 | 199.1 | 232.7 | 34.2 | 20.8 | 53.1 | 3.5 | 257.1 | 4.4 | 46.2 | 43.4 | 33.4 | 52 | 34.3 | 74.6 | 61.7 | 52.4 | 69.8 | 68.1 | 280.6 | 296.8 | 301.8 | 296.6 | 246.8 | 207.3 | 276.2 | 243.2 | 360.8 | 324.1
2051 | 1877 | -6 | 0 | 0 | 229 | 227.1 | 205.8 | 198.9 | 232.7 | 34.2 | 20.7 | 53 | 3.6 | 254.5 | 4.1 | 46.2 | 43.3 | 33.3 | 52.2 | 34.2 | 74.3 | 60.9 | 55 | 69.8 | 68.2 | 280.6 | 296.7 | 301.6 | 296.4 | 246.6 | 207.1 | 276 | 243 | 360.5 | 323.9
2052 | 1878 | -6 | 0 | 0 | 228.9 | 227 | 205.8 | 198.8 | 232.7 | 34.2 | 20.7 | 53 | 3.2 | 247.9 | 3.8 | 46.2 | 43.6 | 33.3 | 52.3 | 34.2 | 74.6 | 60.4 | 53.9 | 69.9 | 68 | 280.7 | 296.6 | 301.4 | 296.2 | 246.4 | 207 | 275.9 | 242.9 | 360.3 | 323.7
2053 | 1879 | -5.8 | 0 | 0 | 228.8 | 226.8 | 205.7 | 198.7 | 232.8 | 34.2 | 20.7 | 53 | 3.2 | 259.4 | 3.7 | 46.2 | 43.6 | 33.2 | 52.5 | 34.2 | 74.6 | 59.9 | 54.2 | 69.9 | 68 | 280.9 | 296.5 | 301.3 | 296 | 246.2 | 206.8 | 275.7 | 242.7 | 360 | 323.5
2054 | 1880 | -5.6 | 0 | 0 | 228.8 | 226.7 | 205.6 | 198.5 | 232.8 | 34.1 | 20.7 | 53 | 3.3 | 270.1 | 3.3 | 46.1 | 44.1 | 33.1 | 52.4 | 34.2 | 74.2 | 59.3 | 56.4 | 69.8 | 68.2 | 280.9 | 296.4 | 301.1 | 295.8 | 246 | 206.7 | 275.5 | 242.5 | 359.7 | 323.4
2055 | 1881 | -5.5 | 0 | 0 | 228.9 | 226.5 | 205.4 | 198.3 | 232.7 | 34.1 | 20.7 | 53 | 3.2 | 248.7 | 3.1 | 46.1 | 44.1 | 33.1 | 52.5 | 34.2 | 74.4 | 58.5 | 56.8 | 69.7 | 68.3 | 280.9 | 296.3 | 300.9 | 295.6 | 245.8 | 206.6 | 275.3 | 242.4 | 359.5 | 323.2
2056 | 1882 | -5.7 | 0 | 0 | 228.9 | 226.4 | 205.4 | 198.2 | 232.7 | 34.1 | 20.7 | 53 | 3.4 | 226.2 | 3 | 46.1 | 44.2 | 33 | 52.2 | 34.2 | 74.2 | 57.9 | 56.2 | 69.8 | 68.5 | 280.6 | 296.2 | 300.8 | 295.4 | 245.7 | 206.5 | 275.2 | 242.2 | 359.2 | 323
2057 | 1883 | -5.8 | 0 | 0 | 228.9 | 226.2 | 205.3 | 198.1 | 232.6 | 34.1 | 20.6 | 53 | 3.5 | 215.8 | 2.8 | 46.1 | 44.3 | 32.9 | 51.9 | 34.1 | 74.4 | 58.2 | 56.8 | 69.9 | 68.6 | 280.6 | 296.1 | 300.6 | 295.2 | 245.5 | 206.3 | 275 | 242 | 359 | 322.8
2058 | 1884 | -6.1 | 0 | 0 | 228.9 | 225.7 | 205.2 | 197.9 | 232.4 | 34 | 20.6 | 53 | 3.3 | 233.6 | 2.4 | 46 | 44 | 32.9 | 52.5 | 34.1 | 74.9 | 59.1 | 58.2 | 70 | 68.8 | 280.6 | 296 | 300.4 | 295 | 245.3 | 206.2 | 274.8 | 241.8 | 358.7 | 322.6
2059 | 1885 | -6 | 0 | 0 | 228.8 | 225.4 | 205 | 197.7 | 232.3 | 34 | 20.6 | 53 | 3.2 | 262.4 | 2.3 | 46 | 44.1 | 32.8 | 52.8 | 34.1 | 75.1 | 59 | 58.9 | 70.1 | 68.8 | 280.6 | 295.9 | 300.2 | 294.8 | 245.2 | 206 | 274.7 | 241.6 | 358.4 | 322.5
2060 | 1886 | -5.9 | 0 | 0 | 228.6 | 225.3 | 204.8 | 197.6 | 232.2 | 34 | 20.6 | 52.9 | 3.2 | 263.1 | 2.5 | 46 | 44.3 | 32.8 | 52.3 | 34.1 | 74.8 | 59.3 | 58.2 | 70.1 | 68.8 | 280.8 | 295.8 | 300.1 | 294.6 | 245 | 205.8 | 274.5 | 241.5 | 358.2 | 322.3
2061 | 1887 | -5.9 | 0 | 0 | 228.2 | 225.4 | 204.6 | 197.6 | 232.1 | 33.9 | 20.6 | 52.9 | 3.7 | 244.6 | 3.1 | 46 | 44.3 | 32.8 | 51.6 | 34.1 | 74.3 | 58.7 | 57.3 | 70.1 | 68.5 | 280.9 | 295.7 | 299.9 | 294.4 | 244.9 | 205.7 | 274.4 | 241.3 | 357.9 | 322.1
2062 | 1888 | -6 | 0 | 0 | 228 | 225.4 | 204.5 | 197.4 | 231.9 | 33.9 | 20.5 | 52.8 | 3.9 | 255.1 | 3.6 | 45.9 | 44.3 | 32.7 | 51.7 | 34 | 74.1 | 58.7 | 54.8 | 70 | 68.1 | 280.9 | 295.6 | 299.8 | 294.2 | 244.7 | 205.6 | 274.2 | 241.1 | 357.6 | 321.9
2063 | 1889 | -5.9 | 0 | 0 | 227.9 | 225.2 | 204.4 | 197.3 | 231.8 | 33.9 | 20.5 | 52.8 | 3.3 | 253.7 | 3.8 | 45.9 | 44.5 | 32.7 | 51.9 | 34 | 74.4 | 59.1 | 52.1 | 70 | 68 | 280.7 | 295.5 | 299.6 | 294 | 244.5 | 205.5 | 274 | 241 | 357.4 | 321.7
2064 | 1890 | -6 | 0 | 0 | 227.7 | 225.1 | 204.2 | 197.2 | 231.7 | 33.9 | 20.5 | 52.7 | 3.2 | 259.3 | 4.4 | 45.9 | 44.5 | 32.7 | 51.9 | 34 | 74.2 | 59.8 | 52.5 | 70.1 | 68 | 280.5 | 295.3 | 299.4 | 293.8 | 244.4 | 205.3 | 273.9 | 240.8 | 357.1 | 321.5
2065 | 1891 | -6 | 0 | 0 | 227.5 | 225 | 204 | 197.1 | 231.6 | 33.8 | 20.5 | 52.7 | 3.3 | 265.2 | 4.9 | 45.8 | 44.6 | 32.7 | 52 | 34 | 73.9 | 62.4 | 54.2 | 70.1 | 68.2 | 280.5 | 295.3 | 299.3 | 293.6 | 244.2 | 205.2 | 273.7 | 240.6 | 356.9 | 321.3
2066 | 1892 | -6.1 | 0 | 0 | 227.2 | 224.7 | 203.8 | 196.9 | 231.5 | 33.8 | 20.5 | 52.7 | 3.2 | 259.2 | 5.4 | 45.8 | 44.8 | 32.8 | 52.8 | 33.9 | 74.3 | 62.5 | 53.5 | 70 | 68.4 | 280.4 | 295.1 | 299.1 | 293.4 | 244 | 205.1 | 273.5 | 240.4 | 356.6 | 321.2
2067 | 1893 | -5.9 | 0 | 0 | 227.1 | 224.5 | 203.7 | 196.7 | 231.4 | 33.8 | 20.5 | 52.6 | 3 | 259.2 | 5.9 | 45.8 | 45.2 | 33 | 52.2 | 33.9 | 74.3 | 60.6 | 53.9 | 70 | 68.4 | 280.5 | 295 | 298.9 | 293.2 | 243.9 | 204.9 | 273.4 | 240.3 | 356.3 | 321
2068 | 1894 | -5.7 | 0 | 0 | 227.1 | 224.4 | 203.6 | 196.6 | 231.3 | 33.7 | 20.5 | 52.6 | 3.1 | 263 | 6 | 45.7 | 45.3 | 33.2 | 51.9 | 33.9 | 74.2 | 60.5 | 54.5 | 70 | 68.4 | 280.5 | 294.9 | 298.8 | 293 | 243.7 | 204.8 | 273.2 | 240.1 | 356.1 | 320.8
2069 | 1895 | -5.7 | 0 | 0 | 226.9 | 224.2 | 203.6 | 196.4 | 231.2 | 33.7 | 20.5 | 52.5 | 2.9 | 254.5 | 5.9 | 45.7 | 45.4 | 33.2 | 52.1 | 33.8 | 74.7 | 60.1 | 55.3 | 70.1 | 68.6 | 280.6 | 294.8 | 298.6 | 292.8 | 243.6 | 204.6 | 273.1 | 239.9 | 355.8 | 320.6
2070 | 1896 | -5.9 | 0 | 0 | 226.7 | 224.1 | 203.4 | 196.2 | 231.1 | 33.7 | 20.5 | 52.5 | 3 | 251 | 6 | 45.6 | 45.5 | 33.2 | 52.1 | 33.8 | 75 | 59.7 | 56.4 | 70.2 | 68.6 | 280.5 | 294.7 | 298.5 | 292.6 | 243.4 | 204.5 | 272.9 | 239.7 | 355.5 | 320.4
2071 | 1897 | -5.9 | 0 | 0 | 226.5 | 224 | 203.2 | 196 | 231 | 33.7 | 20.4 | 52.5 | 3.3 | 264.9 | 6.2 | 45.6 | 45.8 | 33.2 | 51.5 | 33.7 | 75.2 | 59.9 | 57 | 70.2 | 68.6 | 280.4 | 294.6 | 298.3 | 292.4 | 243.3 | 204.3 | 272.7 | 239.5 | 355.3 | 320.3
2072 | 1898 | -5.9 | 0 | 0 | 226.4 | 223.7 | 203.1 | 195.9 | 230.9 | 33.7 | 20.4 | 52.5 | 3.7 | 252.9 | 6.2 | 45.6 | 46.1 | 33.2 | 50.9 | 33.7 | 75 | 60.6 | 57.7 | 70.2 | 68.7 | 280.3 | 294.5 | 298.1 | 292.2 | 243.1 | 204.1 | 272.6 | 239.3 | 355 | 320.1
2073 | 1899 | -6.1 | 0 | 0 | 226.3 | 223.2 | 203 | 195.8 | 230.9 | 33.6 | 20.4 | 52.5 | 3.4 | 252.2 | 6.3 | 45.5 | 46.1 | 33.1 | 50.9 | 33.7 | 75.1 | 63.2 | 57.7 | 70.3 | 68.7 | 280.4 | 294.4 | 298 | 292 | 243 | 204 | 272.4 | 239.2 | 354.8 | 319.9
2074 | 1900 | -6.2 | 0 | 0 | 226.2 | 222.7 | 202.9 | 195.7 | 230.9 | 33.6 | 20.4 | 52.5 | 3.5 | 262 | 5.9 | 45.5 | 46.3 | 33.1 | 51.2 | 33.7 | 75.3 | 63.3 | 57.8 | 70.2 | 68.5 | 280.4 | 294.3 | 297.8 | 291.8 | 242.8 | 203.8 | 272.2 | 239 | 354.5 | 319.7
2075 | 1901 | -6.1 | 0 | 0 | 225.9 | 222.3 | 202.8 | 195.7 | 230.8 | 33.6 | 20.4 | 52.5 | 3.4 | 261.2 | 5.6 | 45.5 | 46.7 | 33 | 51 | 33.7 | 75.3 | 63.4 | 57.5 | 70.4 | 68.4 | 280.5 | 294.2 | 297.6 | 291.6 | 242.6 | 203.7 | 272.1 | 238.8 | 354.3 | 319.5
2076 | 1902 | -6 | 0 | 0 | 225.7 | 222 | 202.7 | 195.6 | 230.8 | 33.5 | 20.4 | 52.5 | 3.5 | 260.4 | 5.5 | 45.5 | 46.8 | 32.9 | 51.4 | 33.7 | 75.1 | 63.2 | 57.5 | 70.5 | 68.4 | 280.5 | 294.1 | 297.5 | 291.4 | 242.5 | 203.5 | 271.9 | 238.7 | 354 | 319.4
2077 | 1903 | -6.1 | 0 | 0 | 225.5 | 221.8 | 202.6 | 195.6 | 230.7 | 33.5 | 20.4 | 52.4 | 3.3 | 252 | 5.1 | 45.5 | 46.8 | 32.8 | 51.7 | 33.8 | 75.3 | 62.1 | 57.8 | 70.5 | 68.5 | 280.5 | 294 | 297.3 | 291.2 | 242.3 | 203.3 | 271.8 | 238.5 | 353.7 | 319.2
2078 | 1904 | -6.1 | 0 | 0 | 225.3 | 221.7 | 202.5 | 195.5 | 230.7 | 33.5 | 20.4 | 52.4 | 3.6 | 246.3 | 5 | 45.4 | 46.8 | 32.7 | 50.8 | 33.8 | 75.5 | 61.6 | 56.8 | 70.4 | 68.5 | 280.5 | 293.9 | 297.2 | 291 | 242.2 | 203.2 | 271.6 | 238.3 | 353.5 | 319
2079 | 1905 | -6.2 | 0 | 0 | 225.3 | 221.6 | 202.4 | 195.3 | 230.7 | 33.5 | 20.4 | 52.3 | 3.4 | 251.2 | 5.2 | 45.4 | 46.9 | 32.6 | 51.1 | 33.8 | 75.7 | 61.6 | 56.2 | 70.5 | 68.5 | 280.5 | 293.8 | 297 | 290.8 | 242.1 | 203.1 | 271.5 | 238.2 | 353.2 | 318.8
2080 | 1906 | -6 | 0 | 0 | 225.1 | 221.5 | 202.2 | 195.1 | 230.6 | 33.6 | 20.3 | 52.3 | 3.4 | 257.8 | 5.5 | 45.4 | 47 | 32.5 | 51.7 | 33.8 | 75.8 | 62.5 | 56.9 | 70.6 | 68.5 | 280.5 | 293.7 | 296.8 | 290.6 | 241.9 | 203 | 271.3 | 238 | 353 | 318.7
2081 | 1907 | -5.9 | 0 | 0 | 225 | 221.5 | 202.1 | 194.9 | 230.6 | 33.5 | 20.3 | 52.2 | 3.7 | 260 | 5.6 | 45.4 | 47 | 32.4 | 52.3 | 33.8 | 75.9 | 62.6 | 57.4 | 70.5 | 68.4 | 280.5 | 293.6 | 296.7 | 290.4 | 241.8 | 202.9 | 271.1 | 237.8 | 352.7 | 318.5
2082 | 1908 | -5.9 | 0 | 0 | 224.9 | 221.5 | 202.1 | 194.7 | 230.5 | 33.6 | 20.3 | 52.2 | 3.1 | 244.9 | 5.9 | 45.4 | 47 | 32.3 | 52.6 | 33.8 | 76 | 62.4 | 58.6 | 70.7 | 68.5 | 280.5 | 293.5 | 296.5 | 290.2 | 241.6 | 202.8 | 271 | 237.7 | 352.5 | 318.3
2083 | 1909 | -5.9 | 0 | 0 | 224.6 | 221.4 | 202 | 194.6 | 230.4 | 33.6 | 20.3 | 52.2 | 3.8 | 242.6 | 5.8 | 45.4 | 47.1 | 32.2 | 52.3 | 33.7 | 76.1 | 61.7 | 59.4 | 70.8 | 68.7 | 280.5 | 293.4 | 296.4 | 290.1 | 241.5 | 202.7 | 270.9 | 237.5 | 352.2 | 318.1
2084 | 1910 | -5.9 | 0 | 0 | 224.5 | 221.3 | 201.8 | 194.4 | 230.3 | 33.6 | 20.3 | 52.2 | 3.4 | 242 | 5.3 | 45.3 | 47.2 | 32.1 | 52.6 | 33.7 | 75.9 | 61.2 | 59.9 | 70.8 | 68.8 | 280.4 | 293.3 | 296.2 | 289.9 | 241.4 | 202.5 | 270.7 | 237.3 | 352 | 318
2085 | 1911 | -5.8 | 0 | 0 | 224.3 | 221.2 | 201.7 | 194.2 | 230.2 | 33.6 | 20.3 | 52.2 | 3.2 | 254.4 | 5.2 | 45.3 | 47.5 | 32.1 | 52.8 | 33.8 | 75.9 | 61.4 | 59 | 70.8 | 68.7 | 280.3 | 293.1 | 296 | 289.7 | 241.2 | 202.4 | 270.6 | 237.1 | 351.7 | 317.8
2086 | 1912 | -5.9 | 0 | 0 | 224.2 | 221 | 201.6 | 194 | 230 | 33.6 | 20.3 | 52.3 | 2.9 | 257.8 | 5.1 | 45.3 | 47.8 | 32.1 | 51.5 | 33.8 | 76.1 | 61.2 | 57.6 | 70.8 | 68.7 | 280.2 | 293 | 295.9 | 289.5 | 241.1 | 202.3 | 270.4 | 236.9 | 351.5 | 317.6
2087 | 1913 | -6.1 | 0 | 0 | 224 | 220.9 | 201.5 | 193.9 | 229.9 | 33.6 | 20.3 | 52.2 | 2.8 | 247.6 | 5 | 45.3 | 47.6 | 32.1 | 50 | 33.8 | 76.1 | 60.2 | 56.2 | 70.9 | 68.5 | 280.2 | 292.9 | 295.7 | 289.3 | 241 | 202.2 | 270.3 | 236.8 | 351.2 | 317.4
2088 | 1914 | -6.1 | 0 | 0 | 223.7 | 220.7 | 201.3 | 193.9 | 229.7 | 33.5 | 20.3 | 52.2 | 3 | 259.9 | 4.8 | 45.3 | 47.8 | 32.1 | 49.5 | 33.8 | 76.1 | 59.4 | 54.5 | 70.9 | 68.5 | 280.2 | 292.8 | 295.6 | 289.1 | 240.9 | 202.1 | 270.2 | 236.7 | 351 | 317.3
2089 | 1915 | -6.1 | 0 | 0 | 223.5 | 220.7 | 201.1 | 193.7 | 229.5 | 33.5 | 20.3 | 52.2 | 2.9 | 262.1 | 4.4 | 45.3 | 48.1 | 32 | 49.1 | 33.9 | 76.1 | 58.9 | 54.4 | 70.9 | 68.5 | 280.2 | 292.7 | 295.4 | 288.9 | 240.7 | 202 | 270 | 236.5 | 350.7 | 317.1
2090 | 1916 | -6 | 0 | 0 | 223.3 | 220.7 | 201 | 193.6 | 229.2 | 33.5 | 20.2 | 52.2 | 3.2 | 236.6 | 4.1 | 45.2 | 48.2 | 31.9 | 48.9 | 33.9 | 76.2 | 58.8 | 53.6 | 70.8 | 68.2 | 280.3 | 292.6 | 295.3 | 288.7 | 240.6 | 201.9 | 269.8 | 236.3 | 350.5 | 317
2091 | 1917 | -6.1 | 0 | 0 | 223 | 220.6 | 200.8 | 193.5 | 228.9 | 33.5 | 20.2 | 52.2 | 3 | 204.3 | 4 | 45.2 | 48.5 | 31.9 | 49.8 | 33.9 | 76 | 58.6 | 52.3 | 70.9 | 68.2 | 280.4 | 292.5 | 295.1 | 288.5 | 240.4 | 201.8 | 269.6 | 236.2 | 350.2 | 316.8
2092 | 1918 | -5.9 | 0 | 0 | 222.7 | 220.4 | 200.8 | 193.3 | 228.2 | 33.5 | 20.2 | 52.1 | 3.2 | 226.7 | 4 | 45.2 | 48.7 | 31.9 | 50.4 | 33.8 | 76 | 58.6 | 51.7 | 71.1 | 68.3 | 280.4 | 292.4 | 294.9 | 288.3 | 240.3 | 201.7 | 269.5 | 236 | 350 | 316.6
2093 | 1919 | -6 | 0 | 0 | 222.6 | 220.3 | 200.7 | 193.3 | 227.3 | 33.5 | 20.2 | 52.1 | 3.6 | 250.9 | 4.4 | 45.1 | 48.8 | 31.8 | 50.2 | 33.7 | 76.1 | 58.1 | 51 | 71 | 68.5 | 280.4 | 292.3 | 294.8 | 288.1 | 240.2 | 201.5 | 269.4 | 235.8 | 349.7 | 316.5
2094 | 1920 | -5.9 | 0 | 0 | 222.5 | 220.3 | 200.6 | 193.2 | 226.6 | 33.4 | 20.2 | 52.1 | 3.3 | 222.7 | 4.7 | 45.1 | 48.9 | 31.8 | 50.2 | 33.7 | 76.1 | 57.9 | 49.4 | 70.9 | 68.4 | 280.4 | 292.2 | 294.6 | 287.9 | 240 | 201.4 | 269.2 | 235.7 | 349.5 | 316.3
2095 | 1921 | -5.5 | 0 | 0 | 222.3 | 220.2 | 200.4 | 193.1 | 226.1 | 33.4 | 20.2 | 52 | 3.3 | 224.5 | 4.8 | 45.1 | 49.4 | 31.8 | 50.2 | 33.6 | 76.1 | 58.3 | 51.1 | 70.8 | 68.1 | 280.4 | 292.1 | 294.5 | 287.7 | 239.9 | 201.3 | 269 | 235.5 | 349.2 | 316.1
2096 | 1922 | -5.6 | 0 | 0 | 222.2 | 219.8 | 200.3 | 192.9 | 225.9 | 33.4 | 20.2 | 52 | 3.6 | 251.1 | 4.4 | 45.1 | 49.3 | 31.8 | 49.4 | 33.5 | 76.1 | 58.2 | 53 | 70.7 | 68.1 | 280.4 | 292 | 294.3 | 287.6 | 239.7 | 201.2 | 268.9 | 235.3 | 349 | 315.9
2097 | 1923 | -6 | 0 | 0 | 222.2 | 219.4 | 200.1 | 192.9 | 225.8 | 33.4 | 20.2 | 51.9 | 3.5 | 257.6 | 4.2 | 45.1 | 49.6 | 31.8 | 49.8 | 33.6 | 76 | 58.4 | 54.1 | 70.6 | 68.1 | 280.3 | 291.9 | 294.2 | 287.4 | 239.6 | 201 | 268.7 | 235.2 | 348.7 | 315.8
2098 | 1924 | -6.1 | 0 | 0 | 222.1 | 219.1 | 200 | 192.8 | 225.8 | 33.4 | 20.2 | 51.9 | 3.6 | 248 | 4.4 | 45 | 49.8 | 31.7 | 50.5 | 33.6 | 76.1 | 59.2 | 54.4 | 70.6 | 67.9 | 280.2 | 291.8 | 294 | 287.2 | 239.4 | 200.9 | 268.6 | 235 | 348.5 | 315.6
2099 | 1925 | -6 | 0 | 0 | 222 | 218.9 | 199.8 | 192.7 | 225.6 | 33.3 | 20.2 | 51.8 | 3.5 | 236.8 | 4.5 | 45 | 50.1 | 31.6 | 50.2 | 33.6 | 76.2 | 59.2 | 53.9 | 70.7 | 67.6 | 280.2 | 291.7 | 293.9 | 287 | 239.3 | 200.8 | 268.4 | 234.9 | 348.2 | 315.4
2100 | 1926 | -5.7 | 0 | 0 | 221.9 | 218.8 | 199.7 | 192.5 | 225.1 | 33.3 | 20.2 | 51.8 | 3.6 | 239.8 | 4.1 | 45 | 50.5 | 31.6 | 51 | 33.6 | 76.2 | 59.4 | 53.7 | 70.8 | 67.7 | 280.2 | 291.6 | 293.7 | 286.8 | 239.1 | 200.6 | 268.2 | 234.7 | 348 | 315.3
2101 | 1927 | -5.7 | 0 | 0 | 221.7 | 218.8 | 199.5 | 192.4 | 224.8 | 33.3 | 20.2 | 51.8 | 3.3 | 246 | 3.7 | 45 | 50.9 | 31.6 | 51.3 | 33.7 | 76.2 | 59.1 | 53.9 | 70.7 | 67.8 | 280.2 | 291.5 | 293.5 | 286.6 | 239 | 200.5 | 268.1 | 234.5 | 347.8 | 315.1
2102 | 1928 | -5.8 | 0 | 0 | 221.6 | 218.8 | 199.5 | 192.2 | 224.5 | 33.3 | 20.2 | 51.7 | 3.7 | 246.8 | 3.3 | 45 | 51.2 | 31.6 | 50.5 | 33.7 | 76.2 | 58.9 | 54.4 | 70.7 | 67.9 | 280.2 | 291.4 | 293.4 | 286.4 | 238.9 | 200.4 | 267.9 | 234.4 | 347.5 | 315
2103 | 1929 | -5.9 | 0 | 0 | 221.4 | 218.7 | 199.4 | 192 | 224.3 | 33.3 | 20.2 | 51.7 | 3.4 | 245.9 | 2.8 | 45 | 51.4 | 31.6 | 50.7 | 33.7 | 76.1 | 59 | 54.7 | 70.6 | 67.8 | 280.3 | 291.2 | 293.2 | 286.2 | 238.8 | 200.3 | 267.8 | 234.2 | 347.3 | 314.8
2104 | 1930 | -6.1 | 0 | 0 | 221.3 | 218.5 | 199.2 | 191.9 | 224.2 | 33.3 | 20.2 | 51.6 | 3.3 | 244.7 | 2.4 | 45 | 51.8 | 31.6 | 51.4 | 33.8 | 76.1 | 58.7 | 54 | 70.6 | 67.5 | 280.3 | 291.1 | 293.1 | 286 | 238.7 | 200.2 | 267.6 | 234.1 | 347 | 314.6
2105 | 1931 | -6.1 | 0 | 0 | 221.1 | 218.3 | 199.1 | 191.8 | 224.1 | 33.2 | 20.2 | 51.6 | 3.5 | 242.6 | 2.2 | 45 | 52.1 | 31.6 | 51.7 | 33.8 | 76.1 | 58.7 | 54.8 | 70.8 | 67.6 | 280.3 | 291 | 292.9 | 285.9 | 238.5 | 200.1 | 267.5 | 233.9 | 346.8 | 314.5
2106 | 1932 | -6.1 | 0 | 0 | 220.8 | 218 | 199 | 191.7 | 223.8 | 33.2 | 20.2 | 51.5 | 3.3 | 242 | 2.4 | 44.9 | 52.5 | 31.6 | 50.3 | 33.7 | 76.1 | 58.1 | 55.2 | 70.7 | 67.9 | 280.3 | 290.9 | 292.8 | 285.7 | 238.4 | 199.9 | 267.3 | 233.7 | 346.5 | 314.3
2107 | 1933 | -6.1 | 0 | 0 | 220.5 | 217.8 | 198.7 | 191.6 | 223.4 | 33.1 | 20.1 | 51.5 | 3.2 | 241.6 | 2.6 | 44.9 | 52.9 | 31.5 | 49.1 | 33.7 | 76.1 | 57.5 | 55.4 | 70.6 | 68.2 | 280.2 | 290.8 | 292.6 | 285.5 | 238.2 | 199.8 | 267.2 | 233.6 | 346.3 | 314.1
2108 | 1934 | -6.1 | 0 | 0 | 220.5 | 217.5 | 198.7 | 191.5 | 223.1 | 33.1 | 20.1 | 51.5 | 3.1 | 231.9 | 2.5 | 44.9 | 53.2 | 31.5 | 48.4 | 33.7 | 76.1 | 57.7 | 56 | 70.7 | 68.4 | 280.1 | 290.7 | 292.4 | 285.3 | 238.1 | 199.7 | 267 | 233.4 | 346 | 314
2109 | 1935 | -6.1 | 0 | 0 | 220.4 | 217.4 | 198.6 | 191.4 | 222.8 | 33 | 20.1 | 51.4 | 3.3 | 210.8 | 2.2 | 44.9 | 53.6 | 31.5 | 49.2 | 33.7 | 76 | 58 | 56.8 | 70.5 | 68.4 | 280.1 | 290.6 | 292.3 | 285.1 | 237.9 | 199.6 | 266.9 | 233.2 | 345.8 | 313.8
2110 | 1936 | -6 | 0 | 0 | 220.3 | 217.4 | 198.6 | 191.3 | 222.5 | 33 | 20.1 | 51.5 | 3.5 | 200.6 | 1.9 | 44.8 | 54 | 31.4 | 50.2 | 33.7 | 75.9 | 57.8 | 57.7 | 70.4 | 68.2 | 280.1 | 290.5 | 292.1 | 284.9 | 237.8 | 199.5 | 266.8 | 233.1 | 345.5 | 313.6
2111 | 1937 | -6.1 | 0 | 0 | 220.1 | 217.2 | 198.5 | 191.3 | 222 | 32.9 | 20.1 | 51.5 | 3.4 | 211.4 | 1.6 | 44.8 | 54.2 | 31.5 | 50.2 | 33.7 | 75.9 | 58 | 57.5 | 70.6 | 68.4 | 280.1 | 290.4 | 292 | 284.8 | 237.6 | 199.4 | 266.6 | 232.9 | 345.3 | 313.5
2112 | 1938 | -6.2 | 0 | 0 | 220 | 217.2 | 198.5 | 191.1 | 221.4 | 32.9 | 20.1 | 51.5 | 3.7 | 232.3 | 1.6 | 44.8 | 54.4 | 31.4 | 49 | 33.7 | 75.7 | 57.9 | 58.3 | 70.5 | 68.4 | 280.1 | 290.3 | 291.8 | 284.6 | 237.5 | 199.3 | 266.5 | 232.8 | 345 | 313.3
2113 | 1939 | -6.2 | 0 | 0 | 219.9 | 217.2 | 198.3 | 191 | 221.2 | 32.8 | 20.1 | 51.6 | 3.3 | 243.5 | 1.9 | 44.7 | 54.7 | 31.4 | 48.1 | 33.7 | 75.7 | 58.1 | 58.4 | 70.3 | 68.4 | 280.2 | 290.2 | 291.7 | 284.4 | 237.4 | 199.2 | 266.3 | 232.6 | 344.8 | 313.1
2114 | 1940 | -6.2 | 0 | 0 | 219.7 | 217.2 | 198.1 | 190.8 | 221.2 | 32.8 | 20.1 | 51.5 | 3.6 | 241.1 | 2.2 | 44.7 | 55.2 | 31.5 | 48.8 | 33.7 | 75.7 | 58.3 | 57.7 | 70.1 | 68.4 | 280.2 | 290.1 | 291.5 | 284.2 | 237.3 | 199.1 | 266.1 | 232.4 | 344.6 | 313
2115 | 1941 | -6.1 | 0 | 0 | 219.5 | 217.1 | 197.8 | 190.6 | 221.2 | 32.7 | 20.1 | 51.5 | 3.4 | 231.8 | 2.3 | 44.7 | 55.6 | 31.5 | 49.4 | 33.7 | 75.8 | 58.7 | 56.9 | 70 | 68.5 | 280.1 | 290 | 291.4 | 284 | 237.2 | 199 | 266 | 232.3 | 344.3 | 312.8
2116 | 1942 | -6.1 | 0 | 0 | 219.4 | 217 | 197.7 | 190.5 | 221.1 | 32.7 | 20.1 | 51.5 | 3.2 | 227.6 | 2.4 | 44.7 | 55.7 | 31.4 | 49.2 | 33.6 | 75.8 | 59.5 | 56.7 | 69.9 | 68.6 | 280 | 289.9 | 291.2 | 283.8 | 237 | 198.8 | 265.8 | 232.2 | 344.1 | 312.6
2117 | 1943 | -6.1 | 0 | 0 | 219.3 | 217 | 197.7 | 190.3 | 221.1 | 32.7 | 20.1 | 51.4 | 3.2 | 226.9 | 2.9 | 44.6 | 56 | 31.4 | 49 | 33.6 | 75.8 | 60.4 | 55 | 70.1 | 68.5 | 280 | 289.8 | 291.1 | 283.7 | 237 | 198.8 | 265.7 | 232 | 343.8 | 312.5
2118 | 1944 | -6.1 | 0 | 0 | 219.2 | 216.9 | 197.6 | 190.2 | 221.1 | 32.7 | 20.1 | 51.4 | 3.1 | 228.9 | 3 | 44.6 | 56.3 | 31.3 | 49.9 | 33.6 | 75.6 | 60.2 | 52.3 | 70.2 | 68.4 | 280 | 289.7 | 290.9 | 283.5 | 236.8 | 198.7 | 265.5 | 231.9 | 343.6 | 312.3
2119 | 1945 | -6.1 | 0 | 0 | 219.1 | 216.7 | 197.5 | 190.1 | 221 | 32.7 | 20.1 | 51.4 | 3.2 | 232.7 | 3.2 | 44.6 | 56.6 | 31.2 | 50.4 | 33.5 | 75.7 | 60.6 | 50.8 | 70.3 | 68.3 | 280.1 | 289.6 | 290.8 | 283.3 | 236.7 | 198.6 | 265.4 | 231.7 | 343.3 | 312.1
2120 | 1946 | -6.1 | 0 | 0 | 218.9 | 216.5 | 197.4 | 189.9 | 220.9 | 32.8 | 20.1 | 51.3 | 3.2 | 232.6 | 3.3 | 44.6 | 56.9 | 31.2 | 50.1 | 33.5 | 75.7 | 61.5 | 51.6 | 70.3 | 68.3 | 280 | 289.4 | 290.6 | 283.1 | 236.5 | 198.5 | 265.2 | 231.6 | 343.1 | 312
2121 | 1947 | -6.3 | 0 | 0 | 218.8 | 216.2 | 197.3 | 189.9 | 220.7 | 32.8 | 20.1 | 51.3 | 3.8 | 228.3 | 3.2 | 44.6 | 57.2 | 31.1 | 50.2 | 33.5 | 75.8 | 61.3 | 53.5 | 70.3 | 68.2 | 280 | 289.3 | 290.5 | 282.9 | 236.3 | 198.4 | 265 | 231.4 | 342.9 | 311.8
2122 | 1948 | -6.2 | 0 | 0 | 218.6 | 216 | 197.2 | 189.8 | 220.5 | 32.7 | 20.1 | 51.3 | 3.5 | 228.9 | 3.1 | 44.6 | 57.4 | 31.1 | 50.7 | 33.5 | 75.7 | 61.3 | 54.1 | 70.2 | 68.2 | 280.1 | 289.2 | 290.3 | 282.7 | 236.2 | 198.2 | 264.8 | 231.2 | 342.6 | 311.6
2123 | 1949 | -6.2 | 0 | 0 | 218.5 | 216 | 197.1 | 189.6 | 220.4 | 32.7 | 20.1 | 51.3 | 3.3 | 229.3 | 3.3 | 44.6 | 57.4 | 31 | 50.8 | 33.5 | 75.7 | 60.9 | 54.9 | 70.1 | 68.1 | 280.1 | 289.1 | 290.2 | 282.6 | 236 | 198.1 | 264.7 | 231.1 | 342.4 | 311.5
2124 | 1950 | -6 | 0 | 0 | 218.3 | 215.9 | 197 | 189.4 | 220.4 | 32.7 | 20.1 | 51.3 | 3.3 | 229 | 3.2 | 44.6 | 57.7 | 31 | 50.6 | 33.5 | 75.7 | 60.5 | 55.6 | 70 | 68 | 280 | 289 | 290 | 282.4 | 235.9 | 197.9 | 264.6 | 231 | 342.1 | 311.3
2125 | 1951 | -6.2 | 0 | 0 | 218.1 | 215.9 | 196.8 | 189.3 | 220.4 | 32.6 | 20.1 | 51.2 | 3.3 | 229.1 | 3 | 44.5 | 57.8 | 31 | 50.1 | 33.5 | 75.8 | 60.6 | 55.3 | 70.2 | 68.1 | 280 | 288.9 | 289.9 | 282.2 | 235.8 | 197.8 | 264.4 | 230.8 | 341.9 | 311.2
2126 | 1952 | -6.2 | 0 | 0 | 218 | 215.9 | 196.8 | 189.1 | 220.4 | 32.6 | 20.1 | 51.2 | 4 | 229 | 2.6 | 44.5 | 58.1 | 30.9 | 50.2 | 33.5 | 75.9 | 60.4 | 55.4 | 70.3 | 68.1 | 280 | 288.8 | 289.7 | 282 | 235.7 | 197.7 | 264.3 | 230.7 | 341.7 | 311
2127 | 1953 | -6.2 | 0 | 0 | 217.8 | 215.6 | 196.6 | 189 | 220.5 | 32.5 | 20.1 | 51.1 | 3.5 | 228.4 | 2.3 | 44.5 | 58.5 | 30.9 | 50.6 | 33.5 | 75.9 | 60.2 | 56 | 70.4 | 68.1 | 279.9 | 288.7 | 289.6 | 281.8 | 235.5 | 197.5 | 264.2 | 230.5 | 341.4 | 310.8
2128 | 1954 | -6.2 | 0 | 0 | 217.6 | 215.4 | 196.5 | 189 | 220.5 | 32.5 | 20.1 | 51 | 3.5 | 228.1 | 2.2 | 44.5 | 58.7 | 30.9 | 51.1 | 33.5 | 75 | 59.9 | 56 | 70.4 | 67.8 | 279.9 | 288.6 | 289.4 | 281.6 | 235.4 | 197.4 | 264 | 230.3 | 341.2 | 310.7
2129 | 1955 | -6 | 0 | 0 | 217.5 | 215.1 | 196.5 | 188.9 | 220.5 | 32.5 | 20.1 | 51 | 3.4 | 228.7 | 2.5 | 44.5 | 58.9 | 30.9 | 51.4 | 33.5 | 74.8 | 60.8 | 56.3 | 70.4 | 67.9 | 279.8 | 288.5 | 289.3 | 281.5 | 235.3 | 197.3 | 263.8 | 230.2 | 340.9 | 310.5
2130 | 1956 | -6.1 | 0 | 0 | 217.4 | 214.8 | 196.4 | 188.8 | 220.5 | 32.5 | 20.1 | 50.9 | 3.4 | 210.6 | 2.8 | 44.4 | 59.2 | 30.8 | 51 | 33.5 | 75.1 | 60.7 | 57.2 | 70.3 | 68.1 | 279.9 | 288.4 | 289.1 | 281.3 | 235.1 | 197.2 | 263.7 | 230.1 | 340.7 | 310.4
2131 | 1957 | -6.3 | 0 | 0 | 217.2 | 214.5 | 196.2 | 188.7 | 220.4 | 32.4 | 20.1 | 50.9 | 3.4 | 181.9 | 3.1 | 44.4 | 59.3 | 30.8 | 50.1 | 33.4 | 75.3 | 60.6 | 58.5 | 70.1 | 68 | 279.9 | 288.3 | 289 | 281.1 | 234.9 | 197 | 263.5 | 229.9 | 340.5 | 310.2
2132 | 1958 | -6.3 | 0 | 0 | 217 | 214.4 | 196.1 | 188.6 | 220.3 | 32.4 | 20.1 | 50.9 | 3.7 | 194.1 | 3.3 | 44.4 | 59.4 | 30.9 | 49.9 | 33.4 | 74.9 | 60.5 | 59 | 70 | 67.9 | 279.9 | 288.2 | 288.8 | 280.9 | 234.8 | 196.9 | 263.4 | 229.8 | 340.2 | 310
2133 | 1959 | -6.2 | 0 | 0 | 216.7 | 214.2 | 195.9 | 188.5 | 220.3 | 32.4 | 20.1 | 50.9 | 3.5 | 215.9 | 3.5 | 44.4 | 59.7 | 30.9 | 50.4 | 33.5 | 74.7 | 61.1 | 59.6 | 69.9 | 67.8 | 279.9 | 288.1 | 288.7 | 280.7 | 234.6 | 196.7 | 263.2 | 229.6 | 340 | 309.9
2134 | 1960 | -6.2 | 0 | 0 | 216.4 | 214.2 | 195.7 | 188.4 | 220.3 | 32.4 | 20.1 | 50.9 | 3.3 | 226.3 | 3.4 | 44.3 | 59.8 | 30.9 | 50.8 | 33.4 | 75 | 62.1 | 60.9 | 69.9 | 67.8 | 279.9 | 288 | 288.5 | 280.6 | 234.5 | 196.6 | 263 | 229.4 | 339.8 | 309.7
2135 | 1961 | -6.1 | 0 | 0 | 216 | 214.1 | 195.6 | 188.4 | 220.2 | 32.3 | 20.1 | 50.9 | 3.4 | 226.2 | 3 | 44.3 | 60 | 30.9 | 51 | 33.4 | 75.3 | 62.3 | 62.1 | 69.8 | 67.8 | 279.9 | 287.9 | 288.4 | 280.4 | 234.4 | 196.4 | 262.9 | 229.3 | 339.5 | 309.6
2136 | 1962 | -6.1 | 0 | 0 | 215.6 | 213.9 | 195.6 | 188.3 | 220.1 | 32.3 | 20.1 | 50.9 | 3.1 | 235.1 | 2.6 | 44.3 | 60.3 | 30.9 | 51.3 | 33.4 | 74.9 | 61.6 | 63.2 | 70 | 67.9 | 279.8 | 287.8 | 288.2 | 280.2 | 234.2 | 196.3 | 262.7 | 229.2 | 339.3 | 309.4
2137 | 1963 | -6.1 | 0 | 0 | 215.6 | 213.5 | 195.5 | 188.2 | 220 | 32.3 | 20.1 | 50.9 | 3.2 | 256.1 | 2.5 | 44.2 | 60.6 | 30.8 | 50.2 | 33.3 | 74.9 | 62.1 | 64.5 | 70 | 68 | 279.7 | 287.6 | 288.1 | 280 | 234 | 196.1 | 262.5 | 229 | 339.1 | 309.2
2138 | 1964 | -6.1 | 0 | 0 | 215.6 | 213.2 | 195.4 | 188 | 219.8 | 32.2 | 20.1 | 50.8 | 3.2 | 265.6 | 2.5 | 44.2 | 60.9 | 30.8 | 50.1 | 33.3 | 75 | 62.2 | 65.3 | 69.6 | 67.9 | 279.8 | 287.5 | 288 | 279.8 | 233.9 | 196 | 262.4 | 228.9 | 338.8 | 309.1
2139 | 1965 | -6.1 | 0 | 0 | 215.7 | 212.9 | 195.3 | 187.8 | 219.7 | 32.2 | 20.1 | 50.8 | 3 | 257.8 | 2.8 | 44.2 | 61.1 | 30.8 | 50.7 | 33.3 | 74.8 | 62.4 | 66.3 | 69.6 | 67.9 | 279.7 | 287.4 | 287.8 | 279.7 | 233.7 | 195.8 | 262.2 | 228.7 | 338.6 | 308.9
2140 | 1966 | -6.1 | 0 | 0 | 215.6 | 212.8 | 195.2 | 187.6 | 219.6 | 32.2 | 20.1 | 50.8 | 3.2 | 242.7 | 3 | 44.2 | 61.1 | 30.7 | 51 | 33.3 | 75.1 | 62.9 | 66.8 | 69.6 | 67.6 | 279.7 | 287.3 | 287.6 | 279.5 | 233.5 | 195.6 | 262.1 | 228.5 | 338.4 | 308.7
2141 | 1967 | -6.1 | 0 | 0 | 215.4 | 212.8 | 195.1 | 187.5 | 219.5 | 32.2 | 20.1 | 50.7 | 3.3 | 235.7 | 3 | 44.2 | 61.3 | 30.7 | 50.7 | 33.3 | 75.2 | 63.3 | 67.6 | 69.8 | 67.6 | 279.7 | 287.2 | 287.5 | 279.3 | 233.4 | 195.5 | 261.9 | 228.4 | 338.1 | 308.6
2142 | 1968 | -6.2 | 0 | 0 | 215.2 | 212.8 | 194.9 | 187.5 | 219.4 | 32.2 | 20.1 | 50.7 | 3.6 | 235.3 | 2.9 | 44.1 | 61.5 | 30.7 | 50.2 | 33.4 | 75.3 | 63.6 | 68.7 | 69.8 | 67.8 | 279.7 | 287.1 | 287.4 | 279.1 | 233.2 | 195.3 | 261.8 | 228.3 | 337.9 | 308.4
2143 | 1969 | -6.1 | 0 | 0 | 215 | 212.8 | 194.8 | 187.5 | 219.3 | 32.2 | 20.1 | 50.7 | 4 | 238.9 | 2.7 | 44.1 | 61.5 | 30.7 | 50.2 | 33.4 | 75.4 | 63.2 | 69.3 | 69.7 | 67.9 | 279.7 | 287 | 287.2 | 278.9 | 233.1 | 195.2 | 261.6 | 228.1 | 337.7 | 308.3
2144 | 1970 | -6 | 0 | 0 | 214.9 | 212.8 | 194.6 | 187.4 | 219.2 | 32.2 | 20.1 | 50.6 | 3.8 | 242.7 | 2.8 | 44.1 | 61.6 | 30.6 | 50.5 | 33.4 | 75.4 | 63 | 69.9 | 69.7 | 68 | 279.7 | 286.9 | 287.1 | 278.8 | 232.9 | 195 | 261.4 | 228 | 337.4 | 308.1
2145 | 1971 | -5.9 | 0 | 0 | 214.8 | 212.7 | 194.5 | 187.4 | 219.1 | 32.2 | 20.1 | 50.6 | 3.6 | 234.4 | 2.9 | 44.1 | 61.5 | 30.6 | 50.2 | 33.3 | 75.4 | 63.5 | 70.5 | 69.6 | 67.8 | 279.7 | 286.8 | 286.9 | 278.6 | 232.8 | 194.9 | 261.3 | 227.8 | 337.2 | 308
2146 | 1972 | -5.8 | 0 | 0 | 214.7 | 212.4 | 194.4 | 187.2 | 218.8 | 32.2 | 20.1 | 50.5 | 3.7 | 230.4 | 3.1 | 44.1 | 61.7 | 30.6 | 49.9 | 33.3 | 75.4 | 63 | 71.3 | 69.7 | 67.9 | 279.7 | 286.7 | 286.8 | 278.4 | 232.6 | 194.7 | 261.1 | 227.7 | 337 | 307.8
2147 | 1973 | -6 | 0 | 0 | 214.6 | 212 | 194.3 | 187.1 | 218.6 | 32.2 | 20.1 | 50.5 | 3.6 | 220.5 | 3.2 | 44 | 61.6 | 30.6 | 49.8 | 33.3 | 75.4 | 63 | 71.5 | 69.7 | 67.8 | 279.7 | 286.6 | 286.6 | 278.2 | 232.5 | 194.6 | 261 | 227.5 | 336.7 | 307.6
2148 | 1974 | -6 | 0 | 0 | 214.5 | 212 | 194.2 | 187.1 | 218.6 | 32.2 | 20.1 | 50.4 | 3.5 | 210.1 | 3.6 | 44 | 61.5 | 30.6 | 49.3 | 33.3 | 75 | 63.4 | 72.4 | 69.8 | 67.6 | 279.7 | 286.5 | 286.5 | 278 | 232.4 | 194.5 | 260.9 | 227.4 | 336.5 | 307.5
2149 | 1975 | -6 | 0 | 0 | 214.3 | 212 | 194.2 | 187.1 | 218.5 | 32.2 | 20.1 | 50.4 | 3.8 | 203.9 | 4 | 44 | 61.6 | 30.6 | 49.3 | 33.3 | 75.2 | 63.6 | 72.8 | 69.7 | 67.6 | 279.6 | 286.4 | 286.3 | 277.8 | 232.2 | 194.4 | 260.7 | 227.2 | 336.3 | 307.3
2150 | 1976 | -6 | 0 | 0 | 214.2 | 211.8 | 194.1 | 186.9 | 218.4 | 32.1 | 20.1 | 50.4 | 3.6 | 202.7 | 4.7 | 44 | 61.8 | 30.5 | 50 | 33.3 | 75.3 | 63.9 | 73.5 | 69.7 | 67.6 | 279.6 | 286.3 | 286.2 | 277.7 | 232.1 | 194.3 | 260.5 | 227.1 | 336 | 307.1
2151 | 1977 | -6 | 0 | 0 | 214 | 211.4 | 193.9 | 186.7 | 218.3 | 32.1 | 20.1 | 50.4 | 3.8 | 203.5 | 4.7 | 44 | 62.1 | 30.5 | 50.7 | 33.3 | 75.4 | 64.1 | 74 | 69.8 | 67.6 | 279.6 | 286.2 | 286 | 277.5 | 231.9 | 194.1 | 260.3 | 227 | 335.8 | 307
2152 | 1978 | -6 | 0 | 0 | 213.9 | 211.1 | 193.7 | 186.6 | 218.3 | 32 | 20.1 | 50.4 | 3.8 | 233.3 | 4.7 | 43.9 | 62.3 | 30.4 | 49.4 | 33.4 | 75.3 | 64.6 | 74.2 | 69.7 | 67.5 | 279.6 | 286.1 | 285.9 | 277.3 | 231.7 | 194 | 260.2 | 226.7 | 335.6 | 306.8
2153 | 1979 | -5.9 | 0 | 0 | 213.7 | 211.2 | 193.6 | 186.4 | 218.2 | 32 | 20.1 | 50.4 | 3.7 | 217.4 | 4.7 | 43.9 | 62.5 | 30.4 | 49.8 | 33.4 | 75.3 | 65.1 | 74.9 | 69.6 | 67.8 | 279.5 | 285.9 | 285.7 | 277.2 | 231.6 | 193.8 | 260.1 | 226.7 | 335.4 | 306.7
2154 | 1980 | -6 | 0 | 0 | 213.1 | 211.3 | 193.6 | 186.3 | 218.2 | 32 | 20.1 | 50.3 | 3.6 | 190 | 4.9 | 43.9 | 62.4 | 30.3 | 48.3 | 33.4 | 75.1 | 64.9 | 75.2 | 69.4 | 67.9 | 279.5 | 285.8 | 285.6 | 277 | 231.4 | 193.7 | 259.9 | 226.5 | 335.1 | 306.5
2155 | 1981 | -6.1 | 0 | 0 | 212.9 | 211.4 | 193.5 | 186.3 | 218 | 32 | 20.1 | 50.3 | 3.4 | 203.8 | 4.8 | 43.9 | 62.5 | 30.2 | 48.1 | 33.5 | 75.1 | 64.7 | 75.7 | 69.3 | 67.8 | 279.5 | 285.7 | 285.5 | 276.8 | 231.3 | 193.6 | 259.8 | 226.3 | 334.9 | 306.4
2156 | 1982 | -6.1 | 0 | 0 | 212.9 | 211 | 193.4 | 186.2 | 217.8 | 32 | 20.1 | 50.3 | 3.4 | 215.1 | 4.7 | 43.9 | 62.7 | 30.2 | 48.8 | 33.5 | 75.1 | 65.6 | 76 | 69.5 | 67.8 | 279.4 | 285.6 | 285.3 | 276.6 | 231.1 | 193.4 | 259.7 | 226.2 | 334.7 | 306.2
2157 | 1983 | -6 | 0 | 0 | 212.8 | 210.8 | 193.4 | 186.1 | 217.7 | 32 | 20.1 | 50.3 | 3.4 | 208.8 | 4.8 | 43.8 | 62.8 | 30.1 | 48.2 | 33.5 | 75.1 | 66.7 | 76.6 | 69.6 | 67.8 | 279.4 | 285.5 | 285.2 | 276.4 | 231 | 193.3 | 259.5 | 226.1 | 334.4 | 306.1
2158 | 1984 | -5.9 | 0 | 0 | 212.7 | 210.7 | 193.3 | 185.9 | 217.5 | 32 | 20.1 | 50.3 | 3.5 | 209.1 | 4.8 | 43.8 | 62.8 | 30 | 47.9 | 33.5 | 75.2 | 67 | 77.3 | 69.6 | 67.7 | 279.4 | 285.4 | 285 | 276.3 | 230.9 | 193.2 | 259.3 | 225.9 | 334.2 | 305.9
2159 | 1985 | -5.8 | 0 | 0 | 212.7 | 210.6 | 193.2 | 185.7 | 217.4 | 32 | 20.1 | 50.3 | 3.4 | 219.8 | 4.4 | 43.8 | 62.7 | 30 | 49 | 33.5 | 75.3 | 67 | 77.5 | 69.7 | 67.8 | 279.3 | 285.3 | 284.9 | 276.1 | 230.7 | 193.1 | 259.2 | 225.8 | 334 | 305.7
2160 | 1986 | -5.6 | 0 | 0 | 212.8 | 210.4 | 193.1 | 185.6 | 217.3 | 32 | 20.1 | 50.3 | 3.4 | 230.5 | 3.7 | 43.8 | 62.9 | 29.9 | 50.1 | 33.5 | 75.4 | 67 | 77.8 | 69.7 | 67.7 | 279.3 | 285.2 | 284.7 | 275.9 | 230.6 | 193 | 259 | 225.6 | 333.8 | 305.6
2161 | 1987 | -5.8 | 0 | 0 | 212.8 | 210.4 | 193 | 185.6 | 216.7 | 32 | 20.1 | 50.3 | 3.3 | 237.4 | 3.1 | 43.8 | 62.9 | 29.8 | 49.5 | 33.6 | 75.3 | 66.7 | 78.3 | 69.7 | 67.7 | 279.3 | 285.1 | 284.6 | 275.7 | 230.4 | 192.9 | 258.9 | 225.5 | 333.5 | 305.4
2162 | 1988 | -5.8 | 0 | 0 | 212.7 | 210.4 | 192.9 | 185.5 | 215.9 | 31.9 | 20.1 | 50.3 | 3.4 | 241.2 | 2.9 | 43.7 | 62.9 | 29.7 | 47.9 | 33.6 | 75.3 | 66.6 | 78.7 | 69.7 | 67.6 | 279.3 | 285 | 284.5 | 275.5 | 230.3 | 192.7 | 258.8 | 225.3 | 333.3 | 305.3
2163 | 1989 | -5.6 | 0 | 0 | 212.5 | 210.3 | 192.8 | 185.4 | 215.4 | 31.9 | 20.1 | 50.2 | 3.5 | 239.2 | 2.8 | 43.7 | 62.8 | 29.7 | 46.6 | 33.5 | 74.3 | 66.8 | 79 | 69.5 | 67.4 | 279.3 | 284.9 | 284.3 | 275.4 | 230.1 | 192.6 | 258.6 | 225.2 | 333.1 | 305.1
2164 | 1990 | -5.7 | 0 | 0 | 212.3 | 210.2 | 192.6 | 185.3 | 215.4 | 32 | 20.1 | 50.2 | 3.5 | 230.7 | 2.7 | 43.7 | 62.7 | 29.7 | 46.4 | 33.5 | 73.8 | 67 | 79.7 | 69.3 | 67.3 | 279.4 | 284.8 | 284.2 | 275.2 | 230 | 192.5 | 258.5 | 225 | 332.8 | 304.9
2165 | 1991 | -6 | 0 | 0 | 212.2 | 210.1 | 192.5 | 185.2 | 215.4 | 32 | 20.1 | 50.2 | 3.5 | 217.8 | 2.4 | 43.7 | 62.9 | 29.7 | 46.2 | 33.5 | 73.4 | 66.7 | 80 | 69.3 | 67.3 | 279.3 | 284.7 | 284 | 275 | 229.9 | 192.4 | 258.3 | 224.9 | 332.6 | 304.8
2166 | 1992 | -6.2 | 0 | 0 | 212.1 | 210 | 192.4 | 185.1 | 215.4 | 32 | 20.1 | 50.2 | 3.6 | 218.7 | 2.3 | 43.8 | 62.9 | 29.6 | 45.6 | 33.4 | 72.7 | 65.7 | 80.3 | 69.3 | 67.3 | 279.3 | 284.6 | 283.9 | 274.8 | 229.8 | 192.3 | 258.2 | 224.8 | 332.4 | 304.6
2167 | 1993 | -6.2 | 0 | 0 | 212 | 209.8 | 192.3 | 184.9 | 215.4 | 32 | 20.1 | 50.1 | 3.6 | 245.9 | 2.3 | 43.8 | 62.8 | 29.6 | 46.1 | 33.3 | 72.7 | 65.5 | 80.6 | 69.2 | 67.1 | 279.4 | 284.5 | 283.7 | 274.7 | 229.7 | 192.2 | 258 | 224.6 | 332.2 | 304.5
2168 | 1994 | -5.9 | 0 | 0 | 211.8 | 209.4 | 192.1 | 184.8 | 215.4 | 32 | 20.1 | 50.2 | 3.7 | 268.4 | 2.3 | 43.8 | 62.8 | 29.6 | 47.5 | 33.2 | 73.1 | 65.9 | 80.9 | 69.1 | 67 | 279.3 | 284.4 | 283.6 | 274.5 | 229.6 | 192.1 | 257.9 | 224.5 | 332 | 304.3
2169 | 1995 | -5.8 | 0 | 0 | 211.7 | 209.1 | 191.9 | 184.7 | 215.5 | 31.9 | 20.1 | 50.1 | 3.4 | 259.9 | 2.6 | 43.7 | 62.9 | 29.6 | 47.8 | 33.2 | 73.4 | 66.6 | 81.3 | 69.3 | 66.9 | 279.3 | 284.2 | 283.5 | 274.3 | 229.5 | 192 | 257.8 | 224.4 | 331.7 | 304.2
2170 | 1996 | -5.9 | 0 | 0 | 211.6 | 209 | 191.7 | 184.6 | 215.5 | 31.9 | 20.1 | 50.1 | 3.1 | 244.8 | 2.8 | 43.7 | 63.1 | 29.6 | 48.6 | 33.1 | 73.8 | 67 | 81.7 | 69.3 | 66.9 | 279.2 | 284.2 | 283.3 | 274.1 | 229.3 | 191.9 | 257.6 | 224.2 | 331.5 | 304
2171 | 1997 | -5.8 | 0 | 0 | 211.5 | 209.1 | 191.6 | 184.5 | 215.5 | 31.9 | 20.1 | 50.1 | 3.7 | 238.9 | 2.9 | 43.7 | 63.2 | 29.6 | 49 | 33.1 | 74.1 | 67 | 81.9 | 69.4 | 66.8 | 279.1 | 284 | 283.2 | 274 | 229.2 | 191.8 | 257.5 | 224.1 | 331.3 | 303.8
2172 | 1998 | -6.1 | 0 | 0 | 211.3 | 209.1 | 191.5 | 184.4 | 215.4 | 31.9 | 20.1 | 50 | 3.4 | 232.1 | 3 | 43.7 | 63 | 29.5 | 49.2 | 33 | 74.2 | 66.8 | 82.2 | 69.4 | 66.9 | 279.1 | 283.9 | 283 | 273.8 | 229 | 191.7 | 257.3 | 224 | 331 | 303.7
2173 | 1999 | -6 | 0 | 0 | 211.2 | 208.9 | 191.3 | 184.3 | 215.4 | 31.8 | 20.1 | 49.9 | 3.6 | 228.7 | 3.2 | 43.7 | 62.8 | 29.5 | 48.6 | 33 | 74.3 | 66.1 | 82.6 | 69.2 | 66.8 | 279.1 | 283.8 | 282.9 | 273.6 | 228.9 | 191.6 | 257.2 | 223.9 | 330.8 | 303.5
2174 | 2000 | -6 | 0 | 0 | 211.2 | 208.7 | 191.3 | 184.1 | 215.4 | 31.8 | 20.1 | 49.9 | 3.8 | 237.3 | 3.6 | 43.6 | 62.8 | 29.5 | 48.3 | 32.9 | 74.4 | 66.1 | 83 | 69.3 | 66.8 | 279.1 | 283.7 | 282.8 | 273.4 | 228.7 | 191.4 | 257 | 223.7 | 330.6 | 303.4
2175 | 2001 | -6 | 0 | 0 | 211 | 208.3 | 191.2 | 184 | 215.4 | 31.8 | 20.1 | 49.9 | 3.1 | 243.4 | 3.8 | 43.6 | 62.8 | 29.5 | 48.2 | 32.8 | 74.5 | 66.2 | 83.2 | 69.3 | 66.9 | 279.1 | 283.6 | 282.6 | 273.3 | 228.5 | 191.3 | 256.9 | 223.6 | 330.4 | 303.2
2176 | 2002 | -6 | 0 | 0 | 211 | 208.1 | 191.1 | 184 | 215.4 | 31.8 | 20.1 | 49.9 | 3.2 | 241.8 | 4.4 | 43.6 | 62.7 | 29.6 | 48.2 | 32.7 | 74.5 | 66.2 | 83.4 | 69.3 | 66.9 | 279.1 | 283.5 | 282.5 | 273.1 | 228.4 | 191.2 | 256.8 | 223.4 | 330.2 | 303
2177 | 2003 | -5.8 | 0 | 0 | 210.9 | 208.2 | 191 | 183.9 | 215.4 | 31.7 | 20.1 | 49.8 | 3.2 | 243.1 | 5.5 | 43.6 | 62.7 | 29.6 | 48.7 | 32.5 | 74.5 | 66.3 | 83.9 | 69.2 | 66.8 | 279 | 283.4 | 282.3 | 272.9 | 228.4 | 191.1 | 256.6 | 223.3 | 329.9 | 302.9
2178 | 2004 | -5.8 | 0 | 0 | 210.6 | 208.2 | 190.9 | 183.8 | 215.3 | 31.7 | 20.1 | 49.8 | 3.3 | 242.3 | 6.2 | 43.6 | 62.8 | 29.6 | 48.7 | 32.5 | 74.5 | 66.2 | 84.5 | 69.3 | 66.6 | 279 | 283.3 | 282.2 | 272.8 | 228.2 | 190.9 | 256.5 | 223.1 | 329.7 | 302.7
2179 | 2005 | -6 | 0 | 0 | 210.5 | 208.1 | 190.7 | 183.7 | 215.3 | 31.7 | 20.1 | 49.7 | 3.3 | 244.4 | 6.3 | 43.5 | 62.8 | 29.6 | 48 | 32.5 | 73.8 | 66.3 | 84.7 | 69.2 | 66.3 | 278.9 | 283.2 | 282.1 | 272.6 | 228.1 | 190.8 | 256.3 | 223 | 329.5 | 302.6
2180 | 2006 | -6.3 | 0 | 0 | 210.4 | 207.9 | 190.6 | 183.5 | 215.2 | 31.7 | 20.1 | 49.7 | 3.6 | 246.6 | 6.4 | 43.5 | 62.8 | 29.6 | 48.4 | 32.6 | 73.4 | 66.3 | 85.1 | 69.1 | 66.2 | 278.9 | 283.1 | 281.9 | 272.4 | 227.9 | 190.7 | 256.1 | 222.9 | 329.3 | 302.4
2181 | 2007 | -6.3 | 0 | 0 | 210.1 | 207.7 | 190.6 | 183.4 | 215 | 31.6 | 20.1 | 49.7 | 3.4 | 247.2 | 6.2 | 43.5 | 63 | 29.5 | 48.9 | 32.6 | 72.4 | 66.5 | 85.5 | 68.9 | 66.2 | 278.9 | 283 | 281.8 | 272.2 | 227.8 | 190.7 | 256 | 222.7 | 329 | 302.3
2182 | 2008 | -6.3 | 0 | 0 | 209.4 | 207.7 | 190.5 | 183.1 | 214.8 | 31.6 | 20.1 | 49.6 | 3.5 | 250.9 | 5.9 | 43.5 | 63.2 | 29.7 | 49.1 | 32.6 | 72.2 | 67 | 85.8 | 68.7 | 66.2 | 278.9 | 282.9 | 281.6 | 272.1 | 227.7 | 190.6 | 255.9 | 222.6 | 328.8 | 302.1
2183 | 2009 | -6.1 | 0 | 0 | 209.1 | 207.6 | 190.4 | 182.9 | 214.7 | 31.6 | 20.1 | 49.5 | 3.2 | 255 | 5.6 | 43.5 | 63.4 | 29.8 | 48.9 | 32.6 | 72.7 | 67.7 | 86.1 | 68.7 | 66.3 | 278.8 | 282.8 | 281.5 | 271.9 | 227.6 | 190.4 | 255.7 | 222.5 | 328.6 | 302
2184 | 2010 | -6.1 | 0 | 0 | 208.9 | 207.4 | 190.3 | 182.9 | 214.7 | 31.6 | 20.1 | 49.5 | 3.6 | 254.7 | 5.3 | 43.5 | 63.5 | 29.7 | 48.2 | 32.6 | 73.1 | 68.5 | 86.5 | 68.8 | 66.3 | 278.8 | 282.7 | 281.4 | 271.7 | 227.4 | 190.3 | 255.5 | 222.3 | 328.4 | 301.8
2185 | 2011 | -5.9 | 0 | 0 | 208.9 | 207.2 | 190.1 | 182.8 | 214.6 | 31.5 | 20.1 | 49.4 | 3.4 | 259.7 | 4.9 | 43.5 | 63.5 | 29.8 | 47.6 | 32.6 | 73.4 | 68.8 | 86.6 | 68.9 | 66.4 | 278.8 | 282.6 | 281.2 | 271.6 | 227.3 | 190.2 | 255.4 | 222.2 | 328.2 | 301.7
2186 | 2012 | -5.9 | 0 | 0 | 208.8 | 207.1 | 189.9 | 182.7 | 214.4 | 31.5 | 20.1 | 49.3 | 3.2 | 263.2 | 4.6 | 43.5 | 63.4 | 29.7 | 47.8 | 32.5 | 73.5 | 69.1 | 87 | 68.8 | 66.1 | 278.8 | 282.5 | 281.1 | 271.4 | 227.2 | 190.1 | 255.3 | 222 | 328 | 301.5
2187 | 2013 | -6 | 0 | 0 | 208.7 | 207.1 | 189.8 | 182.7 | 214.3 | 31.6 | 20.1 | 49.3 | 2.9 | 252.8 | 4.9 | 43.4 | 63.2 | 29.6 | 48.1 | 32.5 | 73.4 | 69.1 | 87.2 | 68.8 | 66.2 | 278.8 | 282.4 | 281 | 271.2 | 227.1 | 190 | 255.1 | 221.9 | 327.7 | 301.4
2188 | 2014 | -6.1 | 0 | 0 | 208.5 | 207 | 189.7 | 182.6 | 214.1 | 31.6 | 20.1 | 49.2 | 3.3 | 248.1 | 5 | 43.4 | 63.3 | 29.6 | 48.4 | 32.4 | 73.5 | 69.5 | 87.5 | 68.7 | 66 | 278.7 | 282.3 | 280.8 | 271 | 227 | 189.8 | 255 | 221.8 | 327.5 | 301.2
2189 | 2015 | -6.1 | 0 | 0 | 208.6 | 206.8 | 189.5 | 182.6 | 214 | 31.6 | 20.1 | 49.2 | 3.2 | 246.5 | 5 | 43.4 | 63.1 | 29.5 | 48.8 | 32.4 | 73.7 | 70.2 | 87.7 | 68.7 | 65.9 | 278.7 | 282.2 | 280.7 | 270.9 | 226.8 | 189.7 | 254.8 | 221.6 | 327.3 | 301.1
2190 | 2016 | -6.1 | 0 | 0 | 208.5 | 206.7 | 189.4 | 182.5 | 213.8 | 31.5 | 20.1 | 49.2 | 3.3 | 242.9 | 4.9 | 43.4 | 63.1 | 29.4 | 48.9 | 32.2 | 73.5 | 71.3 | 87.9 | 68.8 | 66.1 | 278.7 | 282 | 280.5 | 270.7 | 226.6 | 189.6 | 254.6 | 221.5 | 327.1 | 300.9
2191 | 2017 | -6 | 0 | 0 | 208.4 | 206.6 | 189.3 | 182.5 | 213.7 | 31.5 | 20.1 | 49.2 | 3.8 | 254.8 | 4.5 | 43.4 | 63.1 | 29.5 | 49.1 | 32.1 | 73.4 | 71.9 | 88.2 | 68.8 | 66.3 | 278.7 | 281.9 | 280.4 | 270.5 | 226.5 | 189.5 | 254.5 | 221.4 | 326.9 | 300.7
2192 | 2018 | -5.9 | 0 | 0 | 208.2 | 206.4 | 189.3 | 182.4 | 213.6 | 31.5 | 20.1 | 49.2 | 3.7 | 261.2 | 4.1 | 43.3 | 63.3 | 29.6 | 48.7 | 32.2 | 73.5 | 72.1 | 88.3 | 68.4 | 66.4 | 278.6 | 281.8 | 280.3 | 270.3 | 226.4 | 189.4 | 254.4 | 221.2 | 326.6 | 300.6
2193 | 2019 | -6 | 0 | 0 | 208 | 206.3 | 189.2 | 182.3 | 213.5 | 31.5 | 20.1 | 49.1 | 3.9 | 251.8 | 4 | 43.3 | 63.4 | 29.6 | 48.4 | 32.2 | 73.3 | 72.1 | 88.4 | 68.4 | 66.4 | 278.6 | 281.7 | 280.1 | 270.2 | 226.2 | 189.2 | 254.2 | 221.1 | 326.4 | 300.4
2194 | 2020 | -6.1 | 0 | 0 | 208 | 206.3 | 189.2 | 182.2 | 213.2 | 31.5 | 20.1 | 49.1 | 3.6 | 215.7 | 3.9 | 43.3 | 63.4 | 29.6 | 48.6 | 32.2 | 73.3 | 72.6 | 88.7 | 68.5 | 66.5 | 278.6 | 281.6 | 280 | 270 | 226.1 | 189.1 | 254.1 | 220.9 | 326.2 | 300.3
2195 | 2021 | -6.1 | 0 | 0 | 207.9 | 206.1 | 189.1 | 182.1 | 212.9 | 31.5 | 20.1 | 49.1 | 3.5 | 204.5 | 3.6 | 43.3 | 63.4 | 29.5 | 49.1 | 32.2 | 73.5 | 73.2 | 88.6 | 68.4 | 66.2 | 278.6 | 281.5 | 279.8 | 269.8 | 226 | 189 | 254 | 220.8 | 326 | 300.1
2196 | 2022 | -6.2 | 0 | 0 | 207.9 | 205.9 | 188.8 | 182 | 212.7 | 31.5 | 20.1 | 49 | 3.3 | 203 | 3.3 | 43.3 | 63.4 | 29.4 | 49.5 | 32.2 | 73.6 | 74 | 88.7 | 68.5 | 66.3 | 278.6 | 281.4 | 279.7 | 269.7 | 225.9 | 188.9 | 253.8 | 220.6 | 325.8 | 300
2197 | 2023 | -6.2 | 0 | 0 | 207.8 | 205.8 | 188.6 | 182 | 212.5 | 31.5 | 20.1 | 49 | 3.6 | 206.5 | 3.2 | 43.3 | 63.5 | 29.4 | 49.5 | 32.2 | 73.8 | 74.3 | 88.8 | 68.6 | 66.2 | 278.5 | 281.3 | 279.6 | 269.5 | 225.8 | 188.7 | 253.7 | 220.5 | 325.6 | 299.8
2198 | 2024 | -6 | 0 | 0 | 207.7 | 205.8 | 188.6 | 181.9 | 212.6 | 31.4 | 20.2 | 48.9 | 3.4 | 207 | 3.1 | 43.3 | 63.4 | 29.3 | 49.2 | 32.2 | 72.8 | 74.3 | 88.7 | 68.5 | 66 | 278.5 | 281.2 | 279.5 | 269.3 | 225.7 | 188.6 | 253.5 | 220.4 | 325.4 | 299.7
2199 | 2025 | -5.8 | 0 | 0 | 207.5 | 205.7 | 188.4 | 181.9 | 212.6 | 31.4 | 20.2 | 48.9 | 3.4 | 206.7 | 3.4 | 43.3 | 63.3 | 29.2 | 48.6 | 32.1 | 72.1 | 74.5 | 89 | 68.2 | 65.9 | 278.5 | 281.1 | 279.3 | 269.2 | 225.5 | 188.5 | 253.4 | 220.3 | 325.1 | 299.5
2200 | 2026 | -5.7 | 0 | 0 | 207.3 | 205.6 | 188.4 | 181.7 | 212.6 | 31.4 | 20.2 | 49 | 3.6 | 206.9 | 3.9 | 43.3 | 63.3 | 29.2 | 49.2 | 32.1 | 72.3 | 75 | 89.3 | 68.2 | 65.7 | 278.5 | 281 | 279.2 | 269 | 225.4 | 188.4 | 253.2 | 220.1 | 324.9 | 299.4
2201 | 2027 | -5.5 | 0 | 0 | 207 | 205.5 | 188.3 | 181.6 | 212.5 | 31.4 | 20.2 | 49 | 3.7 | 211.6 | 4.2 | 43.3 | 63.1 | 29.1 | 49.1 | 32.1 | 72.3 | 75.5 | 89.6 | 68.3 | 65.9 | 278.5 | 280.9 | 279 | 268.8 | 225.3 | 188.3 | 253.1 | 220 | 324.7 | 299.2
2202 | 2028 | -5.7 | 0 | 0 | 206.8 | 205.4 | 188.2 | 181.3 | 212.3 | 31.4 | 20.2 | 48.9 | 3.6 | 211.1 | 4.4 | 43.3 | 63 | 29 | 49.1 | 32.1 | 72.6 | 75.7 | 89.8 | 68.2 | 66.1 | 278.5 | 280.8 | 278.9 | 268.7 | 225.2 | 188.2 | 253 | 219.9 | 324.5 | 299.1
2203 | 2029 | -5.4 | 0 | 0 | 206.9 | 205.3 | 188 | 181.2 | 212.1 | 31.3 | 20.2 | 48.9 | 3.9 | 201.3 | 4.4 | 43.3 | 63.1 | 29 | 48.5 | 32.1 | 72.8 | 76 | 90 | 68 | 66.1 | 278.4 | 280.7 | 278.8 | 268.5 | 225.1 | 188.1 | 252.8 | 219.7 | 324.3 | 298.9
2204 | 2030 | -5.6 | 0 | 0 | 206.8 | 205.1 | 188 | 181.2 | 211.9 | 31.3 | 20.2 | 48.8 | 3.7 | 199.1 | 3.7 | 43.3 | 63.1 | 29.1 | 47.8 | 32 | 73.1 | 75.8 | 90.1 | 67.7 | 66 | 278.4 | 280.6 | 278.6 | 268.3 | 225 | 188 | 252.7 | 219.6 | 324.1 | 298.7
2205 | 2031 | -5.9 | 0 | 0 | 206.6 | 204.8 | 188 | 181.1 | 211.8 | 31.2 | 20.2 | 48.8 | 3.6 | 205.4 | 4 | 43.3 | 62.9 | 29.1 | 47.2 | 32 | 72.9 | 75.6 | 90.1 | 67.7 | 66 | 278.4 | 280.5 | 278.5 | 268.2 | 224.9 | 187.9 | 252.6 | 219.5 | 323.9 | 298.6
2206 | 2032 | -6 | 0 | 0 | 206.5 | 204.7 | 187.9 | 181.1 | 211.7 | 31.2 | 20.2 | 48.7 | 3.7 | 212.3 | 4.7 | 43.3 | 62.8 | 29.1 | 47.4 | 32 | 72.9 | 75.6 | 90.1 | 67.6 | 65.9 | 278.4 | 280.4 | 278.4 | 268 | 224.8 | 187.8 | 252.5 | 219.4 | 323.7 | 298.4
2207 | 2033 | -6.2 | 0 | 0 | 206.3 | 204.7 | 187.8 | 181.1 | 211.6 | 31.2 | 20.2 | 48.7 | 3.6 | 210.5 | 4.8 | 43.3 | 62.8 | 29.3 | 47.1 | 32 | 72.8 | 75.2 | 90.3 | 67.6 | 65.9 | 278.3 | 280.3 | 278.2 | 267.8 | 224.6 | 187.6 | 252.4 | 219.2 | 323.4 | 298.3
2208 | 2034 | -6.3 | 0 | 0 | 206.2 | 204.7 | 187.7 | 181.1 | 211.5 | 31.2 | 20.2 | 48.7 | 3.4 | 210 | 4.5 | 43.2 | 62.6 | 29.6 | 47.6 | 32 | 72.8 | 75.4 | 90.3 | 67.7 | 65.7 | 278.3 | 280.2 | 278.1 | 267.6 | 224.5 | 187.5 | 252.2 | 219.1 | 323.2 | 298.1
2209 | 2035 | -6.1 | 0 | 0 | 206.1 | 204.7 | 187.5 | 181 | 211.4 | 31.2 | 20.2 | 48.6 | 3.2 | 213.7 | 4.5 | 43.2 | 62.5 | 29.6 | 46.8 | 32 | 73 | 75.9 | 90.3 | 67.7 | 65.7 | 278.2 | 280.1 | 278 | 267.5 | 224.4 | 187.4 | 252 | 218.9 | 323 | 298
2210 | 2036 | -5.8 | 0 | 0 | 206 | 204.5 | 187.3 | 180.9 | 211.2 | 31.2 | 20.2 | 48.6 | 3.4 | 214.9 | 4.7 | 43.2 | 62.4 | 29.5 | 45.9 | 31.9 | 73 | 76.2 | 90.5 | 67.8 | 65.7 | 278.2 | 280 | 277.8 | 267.3 | 224.2 | 187.3 | 251.9 | 218.8 | 322.8 | 297.8
2211 | 2037 | -5.8 | 0 | 0 | 206 | 204.4 | 187.1 | 180.8 | 211.1 | 31.2 | 20.2 | 48.6 | 3.4 | 217.1 | 5.2 | 43.2 | 62.4 | 29.5 | 45.8 | 31.9 | 73 | 76.5 | 90.5 | 67.8 | 65.8 | 278.2 | 279.9 | 277.7 | 267.2 | 224.1 | 187.2 | 251.8 | 218.7 | 322.6 | 297.7
2212 | 2038 | -6 | 0 | 0 | 205.9 | 204.2 | 187.1 | 180.6 | 211.1 | 31.2 | 20.2 | 48.6 | 3.2 | 219.6 | 6.2 | 43.3 | 62.5 | 29.6 | 46.4 | 31.9 | 73.2 | 77 | 90.6 | 67.8 | 65.9 | 278.2 | 279.8 | 277.6 | 267 | 223.9 | 187.1 | 251.6 | 218.5 | 322.4 | 297.5
2213 | 2039 | -6 | 0 | 0 | 205.9 | 203.9 | 187.1 | 180.5 | 211 | 31.1 | 20.2 | 48.6 | 3.5 | 210.2 | 6.2 | 43.3 | 62.4 | 29.5 | 46.5 | 31.9 | 73.2 | 77.5 | 90.7 | 67.6 | 66 | 278.1 | 279.7 | 277.4 | 266.8 | 223.8 | 187 | 251.5 | 218.4 | 322.2 | 297.4
2214 | 2040 | -6.1 | 0 | 0 | 205.9 | 203.7 | 187.1 | 180.4 | 210.9 | 31.1 | 20.2 | 48.6 | 3.7 | 205.8 | 6 | 43.3 | 62.4 | 29.4 | 46.8 | 31.8 | 73 | 77.1 | 90.6 | 67.3 | 65.7 | 278.1 | 279.6 | 277.3 | 266.6 | 223.7 | 186.8 | 251.3 | 218.3 | 322 | 297.2
2215 | 2041 | -6 | 0 | 0 | 205.8 | 203.6 | 187 | 180.4 | 210.8 | 31.1 | 20.2 | 48.6 | 3.9 | 217.7 | 5.5 | 43.3 | 62.4 | 29.4 | 47.8 | 31.8 | 72.8 | 76.9 | 90.7 | 67.3 | 65.5 | 278.1 | 279.5 | 277.2 | 266.5 | 223.6 | 186.7 | 251.2 | 218.1 | 321.8 | 297.1
2216 | 2042 | -5.7 | 0 | 0 | 205.7 | 203.4 | 186.9 | 180.3 | 210.7 | 31.1 | 20.2 | 48.6 | 4 | 234.2 | 5.1 | 43.3 | 62.2 | 29.4 | 48.3 | 31.8 | 73 | 77.4 | 90.8 | 67.5 | 65.4 | 278.1 | 279.4 | 277.1 | 266.3 | 223.5 | 186.5 | 251 | 218 | 321.6 | 296.9
2217 | 2043 | -5.8 | 0 | 0 | 205.4 | 203.2 | 186.7 | 180.1 | 210.6 | 31.1 | 20.2 | 48.6 | 3.8 | 231.9 | 5 | 43.2 | 62.1 | 29.5 | 48.3 | 31.8 | 73 | 78 | 90.8 | 67.6 | 65.3 | 278.1 | 279.3 | 276.9 | 266.1 | 223.4 | 186.4 | 250.9 | 217.9 | 321.4 | 296.8
2218 | 2044 | -6 | 0 | 0 | 205.2 | 203 | 186.6 | 180 | 210.4 | 31.1 | 20.2 | 48.5 | 3.6 | 225.8 | 4.8 | 43.2 | 62.3 | 29.5 | 48.6 | 31.8 | 72.9 | 78.8 | 90.8 | 67.6 | 65.6 | 278 | 279.2 | 276.8 | 266 | 223.3 | 186.3 | 250.8 | 217.8 | 321.1 | 296.6
2219 | 2045 | -6 | 0 | 0 | 205 | 202.8 | 186.5 | 180 | 210.2 | 31.1 | 20.2 | 48.5 | 3.7 | 202.2 | 5 | 43.2 | 62.4 | 29.5 | 49.1 | 31.8 | 73.1 | 79.5 | 90.8 | 67.7 | 65.7 | 278 | 279.1 | 276.6 | 265.8 | 223.2 | 186.2 | 250.6 | 217.6 | 320.9 | 296.5
2220 | 2046 | -5.9 | 0 | 0 | 205 | 202.8 | 186.4 | 179.9 | 210.1 | 31.1 | 20.2 | 48.4 | 3.9 | 209.7 | 5.6 | 43.2 | 62.3 | 29.5 | 49 | 31.8 | 73.2 | 80 | 90.9 | 67.8 | 65.7 | 278 | 278.9 | 276.5 | 265.6 | 223 | 186.2 | 250.5 | 217.5 | 320.7 | 296.3
2221 | 2047 | -6 | 0 | 0 | 205 | 202.7 | 186.3 | 179.8 | 210.1 | 31 | 20.2 | 48.3 | 3.6 | 215.5 | 5.9 | 43.2 | 62.2 | 29.5 | 48.9 | 31.8 | 73.1 | 80.2 | 90.7 | 67.6 | 65.7 | 278 | 278.9 | 276.4 | 265.5 | 222.9 | 186.1 | 250.3 | 217.4 | 320.5 | 296.2
2222 | 2048 | -5.9 | 0 | 0 | 205 | 202.5 | 186.2 | 179.7 | 210 | 31 | 20.2 | 48.3 | 3.7 | 220.4 | 5.8 | 43.2 | 62.3 | 29.5 | 48.9 | 31.8 | 73 | 80.1 | 90.7 | 67.5 | 65.7 | 278 | 278.7 | 276.2 | 265.3 | 222.8 | 186 | 250.2 | 217.2 | 320.3 | 296
2223 | 2049 | -5.9 | 0 | 0 | 204.9 | 202.4 | 186.1 | 179.6 | 209.9 | 31 | 20.2 | 48.2 | 3.4 | 221.3 | 5.6 | 43.1 | 62.2 | 29.4 | 48.9 | 31.9 | 73.2 | 80.4 | 90.8 | 67.6 | 65.8 | 278 | 278.6 | 276.1 | 265.2 | 222.7 | 185.9 | 250.1 | 217.1 | 320.1 | 295.9
2224 | 2050 | -5.9 | 0 | 0 | 204.7 | 202.1 | 186.1 | 179.4 | 209.8 | 31 | 20.2 | 48.2 | 3.5 | 212.8 | 5.7 | 43.1 | 62 | 29.3 | 48.7 | 31.9 | 73.2 | 80.7 | 90.8 | 67.6 | 66 | 277.9 | 278.5 | 276 | 265 | 222.5 | 185.8 | 249.9 | 217 | 319.9 | 295.7
2225 | 2051 | -5.9 | 0 | 0 | 204.6 | 201.8 | 186 | 179.2 | 209.7 | 30.9 | 20.2 | 48.1 | 3.7 | 235.7 | 5.9 | 43.1 | 62 | 29.2 | 48.8 | 31.8 | 73.1 | 80.6 | 90.8 | 67.6 | 66 | 277.9 | 278.4 | 275.8 | 264.8 | 222.3 | 185.7 | 249.8 | 216.9 | 319.7 | 295.6
2226 | 2052 | -5.8 | 0 | 0 | 204.5 | 201.6 | 185.9 | 179.1 | 209.6 | 30.9 | 20.2 | 48.1 | 3.6 | 200 | 4.8 | 43.1 | 62 | 29.1 | 48.7 | 31.8 | 73.2 | 81 | 90.8 | 67.7 | 66.2 | 277.8 | 278.3 | 275.7 | 264.7 | 222.2 | 185.6 | 249.6 | 216.7 | 319.5 | 295.4
2227 | 2053 | -5.8 | 0 | 0 | 204.5 | 201.5 | 185.8 | 179 | 209.5 | 30.9 | 20.2 | 48 | 3.4 | 195.1 | 4.6 | 43.1 | 62 | 29 | 48.6 | 31.8 | 73.3 | 81.2 | 90.9 | 67.8 | 66.2 | 277.8 | 278.2 | 275.6 | 264.5 | 222.1 | 185.5 | 249.5 | 216.6 | 319.3 | 295.3
2228 | 2054 | -5.8 | 0 | 0 | 204.4 | 201.5 | 185.7 | 178.9 | 209.4 | 30.9 | 20.2 | 48 | 3.3 | 220.9 | 4.2 | 43 | 62 | 28.9 | 48.2 | 31.9 | 72.9 | 81.3 | 90.9 | 67.7 | 65.7 | 277.8 | 278.1 | 275.5 | 264.3 | 221.9 | 185.4 | 249.4 | 216.5 | 319.1 | 295.1
2229 | 2055 | -5.8 | 0 | 0 | 204.4 | 201.5 | 185.6 | 178.8 | 209.3 | 30.9 | 20.2 | 48 | 3.1 | 214.2 | 4.1 | 43 | 62 | 28.8 | 48.4 | 31.9 | 72.5 | 81.6 | 91 | 67.6 | 65.3 | 277.7 | 278 | 275.3 | 264.2 | 221.8 | 185.3 | 249.2 | 216.4 | 318.9 | 295
2230 | 2056 | -5.9 | 0 | 0 | 204.3 | 201.4 | 185.4 | 178.4 | 209.3 | 30.8 | 20.2 | 48 | 3.5 | 198.4 | 4.2 | 43 | 62 | 28.7 | 48.6 | 31.9 | 72.7 | 82 | 90.9 | 67.6 | 65.2 | 277.7 | 277.9 | 275.2 | 264 | 221.6 | 185.2 | 249 | 216.2 | 318.7 | 294.8
2231 | 2057 | -5.9 | 0 | 0 | 204.2 | 201.2 | 185.3 | 178.2 | 209.2 | 30.8 | 20.2 | 48 | 3.4 | 208.7 | 5 | 43 | 62.1 | 28.6 | 48.8 | 31.9 | 72.7 | 82.5 | 91 | 67.6 | 65.1 | 277.7 | 277.8 | 275.1 | 263.8 | 221.5 | 185.1 | 248.9 | 216.1 | 318.5 | 294.7
2232 | 2058 | -5.9 | 0 | 0 | 204.1 | 200.9 | 185.2 | 178.1 | 209 | 30.7 | 20.2 | 48 | 3.5 | 212.5 | 5.6 | 43 | 62.1 | 28.5 | 48.6 | 31.9 | 72.9 | 83 | 90.8 | 67.6 | 65.1 | 277.7 | 277.7 | 274.9 | 263.7 | 221.4 | 185 | 248.8 | 216 | 318.3 | 294.5
2233 | 2059 | -6.1 | 0 | 0 | 204 | 200.7 | 185 | 178 | 208.9 | 30.7 | 20.2 | 48 | 3.5 | 207.5 | 6.1 | 43 | 62.1 | 28.6 | 47.5 | 32 | 72.9 | 83.5 | 90.9 | 67.6 | 64.7 | 277.6 | 277.6 | 274.8 | 263.5 | 221.3 | 184.9 | 248.6 | 215.9 | 318.1 | 294.4
2234 | 2060 | -6.2 | 0 | 0 | 203.9 | 200.7 | 184.7 | 177.8 | 208.7 | 30.7 | 20.2 | 48 | 3.9 | 208.2 | 5.9 | 43 | 61.9 | 28.5 | 47.1 | 32 | 72.2 | 83.6 | 90.8 | 67.6 | 64.3 | 277.6 | 277.5 | 274.7 | 263.4 | 221.2 | 184.8 | 248.5 | 215.7 | 317.9 | 294.2
2235 | 2061 | -6 | 0 | 0 | 203.7 | 200.6 | 184.5 | 177.7 | 208.5 | 30.6 | 20.2 | 48 | 3.6 | 207.8 | 5.5 | 42.9 | 61.8 | 28.5 | 47.4 | 32 | 71.5 | 83.8 | 90.9 | 67.5 | 64.3 | 277.6 | 277.4 | 274.5 | 263.2 | 221.1 | 184.7 | 248.4 | 215.6 | 317.7 | 294.1
2236 | 2062 | -6 | 0 | 0 | 203.6 | 200.4 | 184.3 | 177.6 | 208.4 | 30.6 | 20.2 | 48 | 3.5 | 206.5 | 5.7 | 42.9 | 61.8 | 28.4 | 48.2 | 31.9 | 71.6 | 84.9 | 91 | 67.5 | 64.4 | 277.6 | 277.3 | 274.4 | 263 | 221 | 184.6 | 248.2 | 215.5 | 317.5 | 293.9
2237 | 2063 | -5.9 | 0 | 0 | 203.5 | 200.4 | 184.2 | 177.5 | 208.3 | 30.6 | 20.2 | 48 | 3.5 | 206.1 | 6.1 | 42.9 | 61.7 | 28.4 | 48.4 | 31.9 | 71.8 | 85.7 | 91.1 | 67.5 | 64.7 | 277.6 | 277.2 | 274.3 | 262.9 | 220.8 | 184.5 | 248.1 | 215.3 | 317.3 | 293.8
2238 | 2064 | -6 | 0 | 0 | 203.3 | 200.4 | 184.1 | 177.4 | 208.2 | 30.5 | 20.2 | 48 | 3.5 | 204.4 | 6.8 | 42.9 | 61.8 | 28.5 | 48.6 | 32 | 72.1 | 86 | 91.1 | 67.5 | 64.8 | 277.5 | 277.1 | 274.1 | 262.7 | 220.7 | 184.4 | 248 | 215.2 | 317.1 | 293.6
2239 | 2065 | -6.1 | 0 | 0 | 203.2 | 200.4 | 184 | 177.4 | 208.2 | 30.5 | 20.2 | 48 | 4 | 214.1 | 7.2 | 42.9 | 61.7 | 28.5 | 48.7 | 32 | 72.2 | 86.5 | 91.1 | 67.4 | 64.4 | 277.5 | 277 | 274 | 262.6 | 220.5 | 184.3 | 247.8 | 215.1 | 316.8 | 293.5
2240 | 2066 | -6.1 | 0 | 0 | 203.1 | 200.4 | 183.9 | 177.3 | 208.1 | 30.5 | 20.3 | 47.9 | 3.9 | 208.1 | 7.2 | 42.8 | 61.6 | 28.5 | 48.3 | 32 | 72.1 | 86.8 | 91.1 | 67.3 | 64.3 | 277.5 | 276.9 | 273.9 | 262.4 | 220.4 | 184.1 | 247.7 | 215 | 316.7 | 293.3
2241 | 2067 | -5.9 | 0 | 0 | 202.9 | 200.2 | 183.8 | 177.2 | 208.1 | 30.4 | 20.3 | 47.8 | 3.6 | 208.2 | 6.3 | 42.8 | 61.6 | 28.4 | 48.4 | 31.9 | 72.2 | 87.7 | 91.1 | 67.4 | 64.5 | 277.4 | 276.8 | 273.7 | 262.2 | 220.3 | 184 | 247.5 | 214.8 | 316.5 | 293.2
2242 | 2068 | -5.9 | 0 | 0 | 202.7 | 200 | 183.7 | 177.2 | 208 | 30.4 | 20.2 | 47.8 | 3.9 | 213.4 | 5.8 | 42.8 | 61.6 | 28.4 | 48.9 | 31.8 | 72.2 | 88.5 | 91.2 | 67.6 | 64.6 | 277.4 | 276.7 | 273.6 | 262.1 | 220.1 | 183.9 | 247.4 | 214.7 | 316.3 | 293
2243 | 2069 | -5.9 | 0 | 0 | 202.6 | 199.8 | 183.7 | 177.1 | 207.9 | 30.4 | 20.3 | 47.8 | 4 | 223.2 | 5.3 | 42.8 | 61.6 | 28.4 | 48.7 | 31.8 | 72.4 | 88.7 | 91.2 | 67.5 | 64.8 | 277.4 | 276.6 | 273.5 | 261.9 | 220 | 183.8 | 247.2 | 214.6 | 316.1 | 292.9
2244 | 2070 | -5.7 | 0 | 0 | 202.6 | 199.7 | 183.6 | 177 | 207.8 | 30.3 | 20.3 | 47.7 | 4.3 | 235.4 | 4.8 | 42.8 | 61.5 | 28.4 | 48.4 | 31.8 | 72.5 | 88.4 | 91.1 | 67.2 | 64.8 | 277.3 | 276.5 | 273.4 | 261.7 | 219.9 | 183.7 | 247.1 | 214.4 | 315.9 | 292.7
2245 | 2071 | -5.5 | 0 | 0 | 202.5 | 199.7 | 183.4 | 176.9 | 207.6 | 30.3 | 20.3 | 47.7 | 3.6 | 213.2 | 4.5 | 42.8 | 61.4 | 28.3 | 48.1 | 31.8 | 72.6 | 88.1 | 91.1 | 67.1 | 64.6 | 277.3 | 276.4 | 273.3 | 261.6 | 219.7 | 183.5 | 246.9 | 214.3 | 315.7 | 292.6
2246 | 2072 | -5.7 | 0 | 0 | 202.5 | 199.7 | 183.4 | 176.7 | 206.9 | 30.3 | 20.3 | 47.6 | 3.4 | 206.4 | 4.7 | 42.8 | 61.4 | 28.3 | 48.3 | 31.8 | 72.7 | 88.1 | 91.1 | 67.1 | 64.7 | 277.3 | 276.3 | 273.1 | 261.4 | 219.6 | 183.4 | 246.8 | 214.2 | 315.5 | 292.4
2247 | 2073 | -5.9 | 0 | 0 | 202.3 | 199.5 | 183.3 | 176.6 | 205.9 | 30.3 | 20.3 | 47.6 | 3.5 | 210.8 | 5.5 | 42.8 | 61.4 | 28.4 | 47.7 | 31.7 | 72.6 | 87.6 | 91.1 | 67.1 | 64.7 | 277.2 | 276.2 | 273 | 261.3 | 219.5 | 183.3 | 246.7 | 214.1 | 315.3 | 292.3
2248 | 2074 | -6 | 0 | 0 | 202 | 199.4 | 183.1 | 176.5 | 204.7 | 30.3 | 20.3 | 47.7 | 3.5 | 219.4 | 5.5 | 42.8 | 61.4 | 28.4 | 47.2 | 31.6 | 72.3 | 87.1 | 91.1 | 67.1 | 64.7 | 277.2 | 276.1 | 272.9 | 261.1 | 219.4 | 183.3 | 246.5 | 213.9 | 315.1 | 292.1
2249 | 2075 | -6.1 | 0 | 0 | 201.7 | 199.3 | 182.8 | 176.4 | 204.6 | 30.2 | 20.3 | 47.7 | 3.4 | 223.3 | 6.2 | 42.7 | 61.4 | 28.4 | 47.5 | 31.7 | 72.4 | 87.1 | 91 | 67.1 | 64.8 | 277.2 | 276 | 272.7 | 260.9 | 219.2 | 183.2 | 246.3 | 213.8 | 314.9 | 292
2250 | 2076 | -6.1 | 0 | 0 | 201.5 | 199.1 | 182.5 | 176.3 | 204.9 | 30.2 | 20.3 | 47.7 | 3.5 | 200.6 | 6.7 | 42.7 | 61.4 | 28.4 | 47.6 | 31.7 | 72.5 | 87.3 | 91 | 67.2 | 64.8 | 277.2 | 275.8 | 272.6 | 260.8 | 219 | 183.1 | 246.2 | 213.7 | 314.7 | 291.8
2251 | 2077 | -6.1 | 0 | 0 | 201.4 | 199 | 182.4 | 176.1 | 205 | 30.2 | 20.3 | 47.7 | 3.4 | 209.8 | 7.3 | 42.7 | 61.3 | 28.3 | 47.3 | 31.7 | 72.5 | 88.1 | 91 | 67.3 | 64.8 | 277.1 | 275.7 | 272.5 | 260.6 | 218.9 | 183 | 246 | 213.6 | 314.5 | 291.7
2252 | 2078 | -6.1 | 0 | 0 | 201.3 | 198.9 | 182.4 | 176 | 205.2 | 30.2 | 20.3 | 47.6 | 3.4 | 213 | 7.6 | 42.8 | 61.2 | 28.3 | 47.4 | 31.7 | 72.6 | 88.3 | 90.8 | 67.2 | 64.8 | 277.1 | 275.6 | 272.4 | 260.5 | 218.8 | 182.9 | 245.9 | 213.4 | 314.3 | 291.5
2253 | 2079 | -6 | 0 | 0 | 201.4 | 198.7 | 182.3 | 175.8 | 205.3 | 30.2 | 20.3 | 47.5 | 3.4 | 207.1 | 7.7 | 42.8 | 61.3 | 28.4 | 47.6 | 31.6 | 72.5 | 88.5 | 90.7 | 67.3 | 64.9 | 277.1 | 275.5 | 272.2 | 260.3 | 218.7 | 182.8 | 245.8 | 213.3 | 314.1 | 291.4
2254 | 2080 | -5.8 | 0 | 0 | 201.3 | 198.3 | 182.2 | 175.6 | 205.3 | 30.2 | 20.3 | 47.5 | 3.4 | 207.6 | 7.3 | 42.7 | 61.3 | 28.3 | 46.8 | 31.6 | 72.6 | 88.7 | 90.8 | 67.3 | 65 | 277.1 | 275.4 | 272.1 | 260.1 | 218.6 | 182.7 | 245.7 | 213.2 | 313.9 | 291.3
2255 | 2081 | -5.9 | 0 | 0 | 201.3 | 198.2 | 182 | 175.5 | 205.3 | 30.2 | 20.3 | 47.4 | 3.2 | 206.9 | 7 | 42.7 | 61.3 | 28.3 | 46.8 | 31.6 | 72.5 | 88.6 | 90.9 | 67.3 | 64.9 | 277 | 275.3 | 272 | 260 | 218.5 | 182.6 | 245.6 | 213.1 | 313.7 | 291.1
2256 | 2082 | -6.1 | 0 | 0 | 201.2 | 198.1 | 182 | 175.4 | 205.3 | 30.2 | 20.3 | 47.4 | 2.9 | 204.6 | 6.8 | 42.7 | 61.4 | 28.3 | 47.4 | 31.6 | 72.5 | 88.8 | 91 | 67.3 | 65.1 | 277 | 275.2 | 271.8 | 259.8 | 218.4 | 182.5 | 245.5 | 213 | 313.5 | 291
2257 | 2083 | -6.2 | 0 | 0 | 201.1 | 197.9 | 181.9 | 175.3 | 205.3 | 30.2 | 20.3 | 47.4 | 3 | 214.3 | 6 | 42.7 | 61.4 | 28.3 | 47.4 | 31.6 | 72.5 | 88.5 | 91.1 | 67.2 | 64.8 | 277 | 275.1 | 271.7 | 259.7 | 218.2 | 182.4 | 245.3 | 212.8 | 313.3 | 290.8
2258 | 2084 | -6.1 | 0 | 0 | 200.9 | 197.9 | 181.7 | 175.3 | 205.3 | 30.2 | 20.3 | 47.4 | 3.1 | 232.1 | 5.2 | 42.7 | 61.2 | 28.3 | 47.8 | 31.6 | 72.4 | 88.7 | 91.2 | 67.1 | 64.6 | 276.9 | 275 | 271.6 | 259.5 | 218.1 | 182.3 | 245.1 | 212.7 | 313.1 | 290.7
2259 | 2085 | -6.1 | 0 | 0 | 200.7 | 197.8 | 181.6 | 175.3 | 205.3 | 30.2 | 20.3 | 47.4 | 3.4 | 240.5 | 4.2 | 42.7 | 61.3 | 28.2 | 47.6 | 31.7 | 72.4 | 89 | 91.3 | 67 | 64.2 | 276.9 | 274.9 | 271.5 | 259.3 | 218 | 182.1 | 245 | 212.6 | 312.9 | 290.5
2260 | 2086 | -6.2 | 0 | 0 | 200.6 | 197.6 | 181.4 | 175.3 | 205.4 | 30.1 | 20.3 | 47.3 | 3.4 | 247.3 | 3.5 | 42.7 | 61.1 | 28.3 | 47.9 | 31.7 | 72.3 | 89.6 | 91.2 | 66.9 | 64.3 | 276.9 | 274.8 | 271.3 | 259.2 | 217.9 | 182 | 244.8 | 212.4 | 312.7 | 290.4
2261 | 2087 | -6.1 | 0 | 0 | 200.4 | 197.4 | 181.4 | 175.1 | 205.5 | 30.1 | 20.3 | 47.3 | 3.5 | 230.9 | 3.2 | 42.7 | 61 | 28.3 | 48 | 31.7 | 72.4 | 89.8 | 91.2 | 66.7 | 64.2 | 276.9 | 274.7 | 271.2 | 259 | 217.8 | 181.9 | 244.7 | 212.3 | 312.5 | 290.2
2262 | 2088 | -6.1 | 0 | 0 | 200.4 | 197.2 | 181.3 | 175 | 205.5 | 30.1 | 20.3 | 47.3 | 3.3 | 210.3 | 4.4 | 42.7 | 61 | 28.2 | 48.6 | 31.8 | 72 | 89.6 | 91.3 | 66.8 | 64.2 | 276.9 | 274.6 | 271.1 | 258.9 | 217.7 | 181.8 | 244.5 | 212.2 | 312.3 | 290.1
2263 | 2089 | -5.9 | 0 | 0 | 200.3 | 196.8 | 181.2 | 174.9 | 205.5 | 30.1 | 20.3 | 47.3 | 3.4 | 219.4 | 5.1 | 42.6 | 61.1 | 28.1 | 48.3 | 31.7 | 72 | 90.1 | 91.1 | 66.8 | 64 | 276.8 | 274.5 | 271 | 258.7 | 217.5 | 181.7 | 244.4 | 212.1 | 312.1 | 289.9
2264 | 2090 | -5.9 | 0 | 0 | 200.2 | 196.6 | 181.2 | 174.8 | 205.5 | 30.1 | 20.3 | 47.3 | 3.3 | 198.1 | 5.7 | 42.6 | 61.1 | 28 | 48.3 | 31.7 | 71.9 | 90.7 | 90.9 | 66.9 | 63.8 | 276.8 | 274.4 | 270.8 | 258.5 | 217.3 | 181.6 | 244.2 | 211.9 | 311.9 | 289.8
2265 | 2091 | -5.9 | 0 | 0 | 200.1 | 196.7 | 181.1 | 174.6 | 205.5 | 30.1 | 20.3 | 47.3 | 3.7 | 206.4 | 6.4 | 42.6 | 61.1 | 28 | 48.8 | 31.6 | 72.1 | 91.1 | 91 | 66.9 | 64.2 | 276.8 | 274.3 | 270.7 | 258.4 | 217.2 | 181.5 | 244.2 | 211.8 | 311.7 | 289.7
2266 | 2092 | -6 | 0 | 0 | 200 | 196.6 | 180.8 | 174.5 | 205.5 | 30.2 | 20.3 | 47.2 | 3.6 | 211.2 | 7 | 42.6 | 61.1 | 27.9 | 48.9 | 31.6 | 72 | 91.2 | 91 | 66.8 | 64.3 | 276.7 | 274.2 | 270.6 | 258.2 | 217.1 | 181.4 | 244.1 | 211.7 | 311.5 | 289.5
2267 | 2093 | -6 | 0 | 0 | 199.9 | 196.4 | 180.8 | 174.4 | 205.5 | 30.2 | 20.3 | 47.2 | 3.3 | 216.8 | 7.1 | 42.6 | 61 | 27.9 | 48.4 | 31.6 | 71.7 | 91.7 | 90.9 | 66.9 | 64.4 | 276.7 | 274.1 | 270.5 | 258.1 | 217 | 181.2 | 243.9 | 211.6 | 311.4 | 289.4
2268 | 2094 | -5.9 | 0 | 0 | 199.7 | 196.2 | 180.8 | 174.2 | 205.5 | 30.1 | 20.3 | 47.1 | 2.9 | 215.8 | 6.8 | 42.6 | 61 | 27.8 | 47.9 | 31.6 | 71.9 | 92.3 | 90.9 | 66.9 | 64.8 | 276.7 | 274 | 270.3 | 257.9 | 216.8 | 181.1 | 243.8 | 211.4 | 311.1 | 289.2
2269 | 2095 | -6 | 0 | 0 | 199.6 | 196.2 | 180.7 | 174.2 | 205.4 | 30.1 | 20.3 | 47.1 | 3.3 | 200.5 | 6.7 | 42.5 | 60.9 | 27.9 | 48.4 | 31.5 | 71.9 | 92.2 | 90.8 | 66.8 | 64.8 | 276.6 | 273.9 | 270.2 | 257.7 | 216.8 | 181 | 243.7 | 211.3 | 310.9 | 289.1
2270 | 2096 | -6.1 | 0 | 0 | 199.5 | 196.1 | 180.7 | 174.1 | 205.3 | 30.1 | 20.4 | 47 | 3.1 | 209.2 | 6.8 | 42.5 | 60.8 | 27.9 | 48.2 | 31.5 | 71.8 | 92.3 | 91 | 66.9 | 64.9 | 276.6 | 273.8 | 270.1 | 257.6 | 216.7 | 180.9 | 243.5 | 211.2 | 310.7 | 288.9
2271 | 2097 | -6 | 0 | 0 | 199.4 | 195.9 | 180.5 | 173.9 | 205.3 | 30 | 20.4 | 47 | 3.1 | 206.5 | 6.8 | 42.6 | 60.9 | 27.8 | 48.2 | 31.5 | 71.9 | 92.3 | 91 | 66.7 | 64.7 | 276.5 | 273.7 | 270 | 257.4 | 216.6 | 180.8 | 243.3 | 211.1 | 310.6 | 288.8
2272 | 2098 | -6 | 0 | 0 | 199.4 | 195.7 | 180.2 | 173.7 | 205.2 | 30 | 20.4 | 47 | 3 | 190 | 6.2 | 42.5 | 60.8 | 27.6 | 48.7 | 31.4 | 71.8 | 92.1 | 91.1 | 66.2 | 64.2 | 276.5 | 273.6 | 269.8 | 257.3 | 216.5 | 180.7 | 243.2 | 211 | 310.4 | 288.6
2273 | 2099 | -6 | 0 | 0 | 199.2 | 195.4 | 180 | 173.6 | 205.1 | 30 | 20.4 | 46.9 | 3.2 | 193.4 | 6.1 | 42.6 | 60.8 | 27.5 | 48.2 | 31.4 | 71.6 | 92.2 | 91.1 | 66 | 64 | 276.4 | 273.5 | 269.7 | 257.1 | 216.4 | 180.6 | 243.1 | 210.8 | 310.2 | 288.5
2274 | 2100 | -6.1 | 0 | 0 | 199 | 195.2 | 179.9 | 173.6 | 205.1 | 30 | 20.4 | 46.9 | 3.3 | 204.7 | 5.6 | 42.5 | 60.9 | 27.4 | 47.9 | 31.2 | 71.5 | 92.4 | 91.2 | 66.1 | 64.2 | 276.4 | 273.4 | 269.6 | 257 | 216.3 | 180.5 | 243 | 210.7 | 310 | 288.4
2275 | 2101 | -6.2 | 0 | 0 | 198.8 | 195.1 | 179.8 | 173.5 | 205 | 30 | 20.4 | 46.9 | 3.4 | 199.4 | 5 | 42.5 | 60.9 | 27.2 | 47.5 | 31 | 71.5 | 92.7 | 91.2 | 66 | 64.2 | 276.4 | 273.3 | 269.5 | 256.8 | 216.2 | 180.5 | 242.9 | 210.6 | 309.8 | 288.2
2276 | 2102 | -6.3 | 0 | 0 | 198.5 | 195.1 | 179.6 | 173.4 | 205 | 29.9 | 20.4 | 46.9 | 3.3 | 191.9 | 5.2 | 42.5 | 61 | 27.1 | 46.8 | 30.9 | 71.6 | 92.9 | 91.2 | 66.1 | 64 | 276.3 | 273.2 | 269.3 | 256.7 | 216.1 | 180.4 | 242.7 | 210.5 | 309.6 | 288.1
2277 | 2103 | -6.2 | 0 | 0 | 198.2 | 195 | 179.4 | 173.4 | 205 | 29.9 | 20.4 | 46.9 | 3.4 | 191 | 5.7 | 42.5 | 61 | 26.9 | 46.3 | 30.8 | 71.8 | 93.3 | 91.2 | 66.3 | 63.7 | 276.3 | 273.1 | 269.2 | 256.5 | 216 | 180.3 | 242.6 | 210.4 | 309.4 | 287.9
2278 | 2104 | -6.1 | 0 | 0 | 198.2 | 194.8 | 179.3 | 173.4 | 205 | 29.9 | 20.4 | 46.9 | 3.3 | 205.5 | 6.1 | 42.5 | 61 | 26.9 | 46.6 | 30.7 | 71.8 | 93.4 | 91.1 | 66.4 | 63.7 | 276.3 | 273 | 269.1 | 256.4 | 215.9 | 180.3 | 242.4 | 210.2 | 309.2 | 287.8
2279 | 2105 | -6.1 | 0 | 0 | 198.2 | 194.7 | 179.3 | 173.3 | 204.9 | 29.9 | 20.4 | 46.9 | 3.4 | 199.5 | 6.1 | 42.4 | 60.9 | 26.8 | 46.4 | 30.6 | 71.8 | 93.5 | 91 | 66.4 | 63.9 | 276.2 | 272.9 | 269 | 256.2 | 215.7 | 180.2 | 242.3 | 210.1 | 309 | 287.7
2280 | 2106 | -6.1 | 0 | 0 | 197.9 | 194.8 | 179.2 | 173.1 | 204.9 | 29.9 | 20.4 | 47 | 3.3 | 194.1 | 5.9 | 42.4 | 61 | 26.7 | 46.6 | 30.6 | 71.8 | 93.8 | 90.9 | 66.5 | 63.9 | 276.2 | 272.8 | 268.9 | 256.1 | 215.6 | 180.1 | 242.2 | 210 | 308.9 | 287.5
2281 | 2107 | -6 | 0 | 0 | 197.8 | 194.6 | 179 | 172.9 | 204.8 | 29.9 | 20.4 | 47 | 3.2 | 198.2 | 5.7 | 42.4 | 60.8 | 26.6 | 46.7 | 30.5 | 71.8 | 94 | 90.8 | 66.5 | 64.1 | 276.2 | 272.7 | 268.7 | 255.9 | 215.5 | 179.9 | 242.1 | 209.9 | 308.7 | 287.4
2282 | 2108 | -6 | 0 | 0 | 197.7 | 194.4 | 178.9 | 172.7 | 204.7 | 29.9 | 20.4 | 47 | 3.1 | 205.3 | 5.8 | 42.4 | 60.7 | 26.5 | 46.7 | 30.4 | 71.8 | 93.9 | 90.6 | 66.4 | 64.1 | 276.1 | 272.6 | 268.6 | 255.7 | 215.4 | 179.9 | 241.9 | 209.8 | 308.5 | 287.2
2283 | 2109 | -6 | 0 | 0 | 197.6 | 194.3 | 178.9 | 172.6 | 204.5 | 29.9 | 20.4 | 47 | 2.9 | 201.9 | 6 | 42.4 | 60.7 | 26.4 | 46.4 | 30.3 | 71.7 | 93.9 | 90.6 | 66.5 | 64 | 276.1 | 272.5 | 268.5 | 255.6 | 215.3 | 179.8 | 241.8 | 209.6 | 308.3 | 287.1
2284 | 2110 | -6 | 0 | 0 | 197.5 | 194.3 | 178.8 | 172.6 | 204.4 | 29.9 | 20.4 | 47 | 3.2 | 196.6 | 5.8 | 42.3 | 60.8 | 26.4 | 46.6 | 30.3 | 71.8 | 94 | 90.6 | 66.5 | 64.2 | 276.1 | 272.4 | 268.4 | 255.4 | 215.3 | 179.7 | 241.7 | 209.5 | 308.1 | 286.9
2285 | 2111 | -5.7 | 0 | 0 | 197.4 | 194.4 | 178.8 | 172.5 | 204.3 | 29.9 | 20.4 | 47 | 3.3 | 197.5 | 5.4 | 42.3 | 60.7 | 26.4 | 46.4 | 30.3 | 71.7 | 93.7 | 90.7 | 66.4 | 64.3 | 276 | 272.3 | 268.2 | 255.3 | 215.2 | 179.5 | 241.5 | 209.4 | 307.9 | 286.8
2286 | 2112 | -5.8 | 0 | 0 | 197.4 | 194.1 | 178.7 | 172.5 | 204.2 | 29.8 | 20.4 | 47 | 3.3 | 197.8 | 5.3 | 42.3 | 60.7 | 26.3 | 46.7 | 30.2 | 71.6 | 93.5 | 90.6 | 66.4 | 64.3 | 276 | 272.2 | 268.1 | 255.1 | 215.1 | 179.4 | 241.4 | 209.3 | 307.7 | 286.7
2287 | 2113 | -6.1 | 0 | 0 | 197.3 | 193.8 | 178.7 | 172.4 | 204.1 | 29.8 | 20.4 | 47 | 3.3 | 194.4 | 5.5 | 42.3 | 60.5 | 26.3 | 46.9 | 30.1 | 71.6 | 93.7 | 90.6 | 66.4 | 64.4 | 276 | 272.1 | 268 | 255 | 215 | 179.3 | 241.3 | 209.2 | 307.5 | 286.5
2288 | 2114 | -6.1 | 0 | 0 | 197.1 | 193.6 | 178.6 | 172.3 | 204 | 29.8 | 20.4 | 46.9 | 3.3 | 204.7 | 5.9 | 42.3 | 60.5 | 26.4 | 47.3 | 30.2 | 71.7 | 93.8 | 90.6 | 66.3 | 64.3 | 275.9 | 272 | 267.9 | 254.8 | 214.8 | 179.2 | 241.1 | 209 | 307.4 | 286.4
2289 | 2115 | -6.2 | 0 | 0 | 197 | 193.4 | 178.5 | 172.2 | 203.9 | 29.8 | 20.4 | 46.9 | 3.3 | 207.4 | 6.1 | 42.3 | 60.4 | 26.3 | 47.1 | 30.1 | 71.5 | 93.9 | 90.5 | 66.3 | 64.1 | 275.9 | 271.9 | 267.7 | 254.7 | 214.7 | 179.1 | 241 | 208.9 | 307.2 | 286.2
2290 | 2116 | -6.1 | 0 | 0 | 196.9 | 193.2 | 178.5 | 172.1 | 203.8 | 29.7 | 20.4 | 46.9 | 3.3 | 205.7 | 6.4 | 42.3 | 60.2 | 26.3 | 47 | 30.1 | 71.5 | 94.4 | 90.6 | 66.3 | 64 | 275.9 | 271.8 | 267.6 | 254.5 | 214.6 | 179.1 | 240.9 | 208.8 | 307 | 286.1
2291 | 2117 | -6 | 0 | 0 | 196.8 | 193.1 | 178.4 | 172 | 203.7 | 29.7 | 20.4 | 46.8 | 3.3 | 207.9 | 6.4 | 42.3 | 60.3 | 26.3 | 47.3 | 30 | 71.6 | 94.6 | 90.6 | 66.2 | 63.7 | 275.8 | 271.7 | 267.5 | 254.4 | 214.5 | 179 | 240.8 | 208.7 | 306.8 | 286
2292 | 2118 | -6.1 | 0 | 0 | 196.4 | 193 | 178.3 | 171.8 | 203.6 | 29.7 | 20.4 | 46.8 | 3.2 | 215.6 | 6 | 42.2 | 60.3 | 26.3 | 47.5 | 30 | 71.5 | 94.8 | 90.7 | 66.1 | 63.4 | 275.8 | 271.6 | 267.4 | 254.2 | 214.4 | 178.9 | 240.7 | 208.6 | 306.6 | 285.8
2293 | 2119 | -6.2 | 0 | 0 | 195.6 | 192.8 | 178.1 | 171.7 | 203.5 | 29.6 | 20.4 | 46.7 | 3.3 | 202.1 | 6 | 42.2 | 60.4 | 26.2 | 46.4 | 29.8 | 71.6 | 95.1 | 90.7 | 66.1 | 63.5 | 275.7 | 271.5 | 267.3 | 254.1 | 214.3 | 178.9 | 240.6 | 208.5 | 306.4 | 285.7
2294 | 2120 | -6.3 | 0 | 0 | 195.4 | 192.8 | 177.8 | 171.7 | 203.5 | 29.6 | 20.4 | 46.6 | 3.2 | 195.4 | 6.4 | 42.2 | 60.3 | 26.2 | 46.7 | 29.8 | 71.6 | 95.4 | 90.8 | 66.2 | 63.5 | 275.7 | 271.4 | 267.1 | 253.9 | 214.2 | 178.8 | 240.4 | 208.3 | 306.2 | 285.5
2295 | 2121 | -6.1 | 0 | 0 | 195.4 | 192.8 | 177.7 | 171.7 | 203.5 | 29.6 | 20.4 | 46.6 | 3.3 | 199.4 | 7 | 42.2 | 60.4 | 26.2 | 47 | 29.9 | 71.4 | 96 | 90.8 | 66.4 | 63.6 | 275.7 | 271.2 | 267 | 253.8 | 214.1 | 178.7 | 240.3 | 208.2 | 306 | 285.4
2296 | 2122 | -6 | 0 | 0 | 195.4 | 192.7 | 177.5 | 171.6 | 203.5 | 29.5 | 20.4 | 46.6 | 3.3 | 200.2 | 6.7 | 42.1 | 60.6 | 26.2 | 46.4 | 29.9 | 71.5 | 96.3 | 90.7 | 66.4 | 63.6 | 275.6 | 271.2 | 266.9 | 253.6 | 214 | 178.6 | 240.2 | 208.1 | 305.9 | 285.2
2297 | 2123 | -5.9 | 0 | 0 | 195.4 | 192.7 | 177.5 | 171.4 | 203.5 | 29.5 | 20.4 | 46.6 | 3.5 | 206.5 | 6.7 | 42.1 | 60.7 | 26.2 | 46.1 | 29.9 | 71.5 | 96.2 | 90.8 | 66.2 | 63.6 | 275.6 | 271 | 266.8 | 253.5 | 213.9 | 178.5 | 240 | 208 | 305.7 | 285.1
2298 | 2124 | -5.9 | 0 | 0 | 195.4 | 192.5 | 177.4 | 171.2 | 203.5 | 29.5 | 20.4 | 46.6 | 3.4 | 209.3 | 6.6 | 42.1 | 60.5 | 26.3 | 46.3 | 29.8 | 71.4 | 96 | 90.8 | 66.1 | 63.5 | 275.6 | 270.9 | 266.7 | 253.3 | 213.8 | 178.4 | 239.9 | 207.9 | 305.5 | 285
2299 | 2125 | -6.1 | 0 | 0 | 195.3 | 192.5 | 177.3 | 171 | 203.5 | 29.4 | 20.4 | 46.6 | 3.4 | 208.4 | 6.2 | 42.1 | 60.4 | 26.4 | 46.8 | 29.9 | 71.5 | 96.2 | 90.8 | 66.2 | 63.5 | 275.5 | 270.8 | 266.5 | 253.2 | 213.7 | 178.3 | 239.8 | 207.8 | 305.3 | 284.8
2300 | 2126 | -6.2 | 0 | 0 | 195.2 | 192.5 | 177.1 | 171 | 203.4 | 29.4 | 20.4 | 46.6 | 3.3 | 211 | 5.8 | 42.1 | 60.3 | 26.4 | 46.8 | 30 | 71.6 | 96.4 | 90.8 | 66.2 | 63.7 | 275.5 | 270.7 | 266.4 | 253 | 213.6 | 178.2 | 239.7 | 207.7 | 305.1 | 284.7
2301 | 2127 | -6.2 | 0 | 0 | 195.2 | 192.4 | 177.1 | 171 | 203.3 | 29.4 | 20.4 | 46.6 | 3.3 | 209.7 | 5.4 | 42.1 | 60.2 | 26.4 | 46.8 | 30 | 71.6 | 96.6 | 90.9 | 66.1 | 63.7 | 275.5 | 270.6 | 266.3 | 252.9 | 213.5 | 178 | 239.5 | 207.5 | 304.9 | 284.6
2302 | 2128 | -6.2 | 0 | 0 | 195.2 | 192.1 | 177.1 | 170.9 | 203.2 | 29.3 | 20.4 | 46.6 | 3.2 | 212.8 | 5.1 | 42.1 | 60.2 | 26.4 | 47.5 | 30.1 | 71.6 | 96.6 | 90.9 | 66 | 63.6 | 275.4 | 270.5 | 266.2 | 252.7 | 213.4 | 177.9 | 239.4 | 207.4 | 304.7 | 284.4
2303 | 2129 | -6.1 | 0 | 0 | 195.1 | 191.9 | 177.1 | 170.8 | 203.1 | 29.3 | 20.4 | 46.5 | 3.4 | 215.9 | 5 | 42.1 | 60.3 | 26.4 | 46.7 | 30.3 | 71.6 | 96.4 | 90.8 | 66 | 63.4 | 275.4 | 270.4 | 266.1 | 252.6 | 213.4 | 177.8 | 239.3 | 207.3 | 304.5 | 284.3
2304 | 2130 | -5.9 | 0 | 0 | 194.9 | 191.6 | 177 | 170.7 | 202.9 | 29.3 | 20.4 | 46.5 | 3.2 | 213.3 | 5 | 42.1 | 60.3 | 26.5 | 45.9 | 30.3 | 71.5 | 96.5 | 90.7 | 66.1 | 63.3 | 275.4 | 270.3 | 265.9 | 252.4 | 213.3 | 177.7 | 239.2 | 207.2 | 304.4 | 284.1
2305 | 2131 | -6.1 | 0 | 0 | 194.6 | 191.4 | 176.9 | 170.6 | 202.8 | 29.3 | 20.4 | 46.4 | 3.3 | 216.8 | 4.9 | 42 | 60.2 | 26.5 | 46.1 | 30.4 | 71.6 | 96.5 | 90.7 | 66.1 | 63.2 | 275.4 | 270.2 | 265.8 | 252.3 | 213.2 | 177.6 | 239 | 207 | 304.2 | 284
2306 | 2132 | -6.1 | 0 | 0 | 194.5 | 191.3 | 176.8 | 170.6 | 202.7 | 29.2 | 20.4 | 46.4 | 3.1 | 218.1 | 4.8 | 42 | 60.3 | 26.5 | 46.5 | 30.4 | 71.6 | 96.6 | 90.7 | 66.1 | 63.1 | 275.3 | 270.1 | 265.7 | 252.1 | 213.1 | 177.5 | 238.9 | 207 | 304 | 283.9
2307 | 2133 | -6.1 | 0 | 0 | 194.5 | 191.5 | 176.6 | 170.5 | 202.6 | 29.2 | 20.4 | 46.4 | 3.1 | 216.3 | 5 | 42 | 60.2 | 26.5 | 46.3 | 30.4 | 71.5 | 96.9 | 90.9 | 66.1 | 63.1 | 275.3 | 270 | 265.6 | 252 | 213 | 177.5 | 238.8 | 206.8 | 303.8 | 283.7
2308 | 2134 | -6 | 0 | 0 | 194.7 | 191.5 | 176.3 | 170.4 | 202.5 | 29.2 | 20.4 | 46.4 | 3.4 | 214.9 | 5.2 | 42 | 60.1 | 26.4 | 46.8 | 30.3 | 71.4 | 97.3 | 90.9 | 66.1 | 63.1 | 275.2 | 269.9 | 265.5 | 251.8 | 212.9 | 177.4 | 238.7 | 206.8 | 303.6 | 283.6
2309 | 2135 | -6 | 0 | 0 | 194.6 | 191.3 | 176.2 | 170.4 | 202.5 | 29.1 | 20.4 | 46.4 | 3.3 | 210.2 | 5.3 | 42 | 60 | 26.4 | 47 | 30.2 | 71.4 | 97.7 | 90.9 | 66.1 | 63 | 275.2 | 269.8 | 265.3 | 251.7 | 212.8 | 177.4 | 238.6 | 206.6 | 303.5 | 283.4
2310 | 2136 | -5.7 | 0 | 0 | 194.4 | 191.2 | 176.1 | 170.3 | 202.4 | 29.1 | 20.4 | 46.4 | 3 | 216 | 5.7 | 42 | 59.9 | 26.4 | 46.1 | 30.1 | 71.2 | 97.8 | 90.9 | 65.9 | 62.8 | 275.2 | 269.7 | 265.2 | 251.5 | 212.7 | 177.3 | 238.4 | 206.5 | 303.3 | 283.3
2311 | 2137 | -5.6 | 0 | 0 | 194.2 | 191 | 176.1 | 170.2 | 202.3 | 29.1 | 20.4 | 46.3 | 3.5 | 210.7 | 6 | 42 | 59.7 | 26.4 | 46.2 | 30.1 | 70.8 | 97.6 | 90.9 | 65.7 | 62.6 | 275.1 | 269.6 | 265.1 | 251.4 | 212.6 | 177.2 | 238.3 | 206.4 | 303.1 | 283.2
2312 | 2138 | -5.9 | 0 | 0 | 194.1 | 190.8 | 176 | 170.2 | 202.2 | 29.1 | 20.4 | 46.3 | 4 | 209 | 5.8 | 42 | 59.4 | 26.4 | 45.8 | 30.2 | 70.7 | 97.7 | 90.8 | 65.6 | 62.6 | 275.1 | 269.5 | 265 | 251.2 | 212.5 | 177.1 | 238.2 | 206.3 | 302.9 | 283
2313 | 2139 | -6 | 0 | 0 | 194 | 190.8 | 176 | 170.1 | 202.1 | 29.1 | 20.4 | 46.3 | 3.6 | 212.9 | 5.6 | 42 | 59.4 | 26.4 | 45.5 | 30.3 | 71 | 97.9 | 90.7 | 65.6 | 62.9 | 275.1 | 269.4 | 264.9 | 251.1 | 212.4 | 177 | 238 | 206.2 | 302.7 | 282.9
2314 | 2140 | -6.2 | 0 | 0 | 193.8 | 190.7 | 175.9 | 170 | 202 | 29.1 | 20.5 | 46.2 | 3.9 | 200.6 | 7.2 | 42 | 59.4 | 26.4 | 45.5 | 30.3 | 71.1 | 97.8 | 90.7 | 65.7 | 63 | 275.1 | 269.3 | 264.8 | 251 | 212.3 | 176.9 | 237.9 | 206.1 | 302.6 | 282.8
2315 | 2141 | -6.1 | 0 | 0 | 193.7 | 190.4 | 175.9 | 169.9 | 201.9 | 29.2 | 20.5 | 46.2 | 4.1 | 217.5 | 7.7 | 42 | 59.5 | 26.3 | 46 | 30.3 | 71.2 | 98.1 | 90.6 | 65.6 | 62.8 | 275 | 269.3 | 264.6 | 250.8 | 212.2 | 176.8 | 237.8 | 206 | 302.4 | 282.6
2316 | 2142 | -6 | 0 | 0 | 193.7 | 190.3 | 175.8 | 169.8 | 201.8 | 29.2 | 20.5 | 46.2 | 3.7 | 223.5 | 6.9 | 42 | 59.5 | 26.3 | 46.5 | 30.3 | 71.2 | 98.3 | 90.4 | 65.5 | 62.6 | 275 | 269.1 | 264.5 | 250.7 | 212.1 | 176.7 | 237.6 | 205.9 | 302.2 | 282.5
2317 | 2143 | -5.9 | 0 | 0 | 193.7 | 190.1 | 175.7 | 169.7 | 201.7 | 29.2 | 20.5 | 46.2 | 3.8 | 204.2 | 7.4 | 42 | 59.5 | 26.3 | 47.2 | 30.3 | 71.1 | 98.5 | 90.3 | 65.6 | 62.7 | 275 | 269.1 | 264.4 | 250.5 | 212 | 176.6 | 237.5 | 205.8 | 302 | 282.4
2318 | 2144 | -5.8 | 0 | 0 | 193.6 | 189.9 | 175.7 | 169.6 | 201.6 | 29.3 | 20.5 | 46.1 | 3.7 | 207 | 8.1 | 42 | 59.5 | 26.3 | 47.6 | 30.3 | 71.2 | 98.8 | 90.3 | 65.7 | 62.6 | 274.9 | 269 | 264.3 | 250.4 | 211.9 | 176.5 | 237.4 | 205.7 | 301.8 | 282.2
2319 | 2145 | -5.6 | 0 | 0 | 193.6 | 190 | 175.6 | 169.5 | 201.6 | 29.3 | 20.5 | 46.1 | 3.9 | 212.4 | 8.2 | 42 | 59.7 | 26.3 | 47.6 | 30.3 | 71.2 | 99.1 | 90.2 | 65.7 | 62.6 | 274.9 | 268.9 | 264.2 | 250.2 | 211.8 | 176.4 | 237.3 | 205.6 | 301.6 | 282.1
2320 | 2146 | -5.9 | 0 | 0 | 193.5 | 190.2 | 175.4 | 169.3 | 201.5 | 29.3 | 20.5 | 46.1 | 3.4 | 209.7 | 8.4 | 42 | 59.8 | 26.3 | 47.9 | 30.3 | 71.2 | 99.3 | 90.2 | 65.4 | 62.4 | 274.8 | 268.8 | 264.1 | 250.1 | 211.7 | 176.3 | 237.2 | 205.5 | 301.5 | 281.9
2321 | 2147 | -6.2 | 0 | 0 | 193.4 | 190.3 | 175.4 | 169.3 | 201.5 | 29.2 | 20.5 | 46 | 3.7 | 210.8 | 8.8 | 41.9 | 59.9 | 26.3 | 47.8 | 30.3 | 71.2 | 99.2 | 90.1 | 65.1 | 62 | 274.8 | 268.7 | 263.9 | 249.9 | 211.6 | 176.2 | 237 | 205.3 | 301.3 | 281.8
2322 | 2148 | -6.1 | 0 | 0 | 193.1 | 190.3 | 175.4 | 169.3 | 201.5 | 29.2 | 20.5 | 46 | 3.8 | 218.9 | 8.5 | 41.9 | 59.9 | 26.4 | 47.3 | 30.3 | 71.2 | 99.5 | 90 | 65.3 | 61.9 | 274.8 | 268.6 | 263.8 | 249.8 | 211.5 | 176.1 | 236.9 | 205.2 | 301.1 | 281.7
2323 | 2149 | -5.8 | 0 | 0 | 192.9 | 190.1 | 175.3 | 169.3 | 201.4 | 29.2 | 20.5 | 46 | 3.8 | 221.5 | 7.7 | 41.9 | 60.1 | 26.4 | 47.6 | 30.4 | 71.3 | 99.9 | 89.9 | 65.4 | 62.3 | 274.7 | 268.5 | 263.7 | 249.7 | 211.4 | 176 | 236.8 | 205.1 | 300.9 | 281.5
2324 | 2150 | -5.9 | 0 | 0 | 192.9 | 189.9 | 175.2 | 169.3 | 201.4 | 29.2 | 20.5 | 46 | 3.5 | 219 | 6.9 | 41.9 | 60.2 | 26.4 | 48 | 30.4 | 71.1 | 99.7 | 89.9 | 65.4 | 62.3 | 274.7 | 268.4 | 263.6 | 249.5 | 211.3 | 175.9 | 236.7 | 205 | 300.8 | 281.4
2325 | 2151 | -6 | 0 | 0 | 192.8 | 189.9 | 175.3 | 169.2 | 201.3 | 29.2 | 20.5 | 45.9 | 3.7 | 216.4 | 6.1 | 41.8 | 60.2 | 26.4 | 48.1 | 30.4 | 71 | 99.9 | 89.6 | 65.5 | 62.2 | 274.7 | 268.3 | 263.5 | 249.4 | 211.2 | 175.8 | 236.5 | 204.9 | 300.6 | 281.2
2326 | 2152 | -6.1 | 0 | 0 | 192.6 | 189.8 | 175.2 | 169.2 | 201.2 | 29.2 | 20.5 | 45.9 | 3.4 | 231 | 5.1 | 41.8 | 60 | 26.3 | 47.7 | 30.4 | 71 | 100.4 | 89.6 | 65.5 | 62.2 | 274.6 | 268.2 | 263.4 | 249.2 | 211.2 | 175.8 | 236.4 | 204.8 | 300.4 | 281.1
2327 | 2153 | -6.2 | 0 | 0 | 192.5 | 189.5 | 175 | 169.1 | 201.1 | 29.2 | 20.5 | 45.9 | 3.3 | 245 | 4.8 | 41.8 | 60 | 26.3 | 47.4 | 30.4 | 70.8 | 100.6 | 89.6 | 65.4 | 62 | 274.6 | 268.1 | 263.2 | 249.1 | 211 | 175.7 | 236.3 | 204.7 | 300.2 | 281
2328 | 2154 | -6.2 | 0 | 0 | 192.4 | 189.2 | 175 | 169 | 201 | 29.2 | 20.5 | 45.9 | 3.4 | 232.4 | 4.6 | 41.8 | 60.1 | 26.4 | 47.3 | 30.4 | 70.5 | 100.9 | 89.7 | 65.4 | 62.4 | 274.6 | 268 | 263.1 | 248.9 | 211 | 175.6 | 236.3 | 204.6 | 300.1 | 280.8
2329 | 2155 | -6 | 0 | 0 | 192.3 | 189.1 | 174.9 | 169 | 201 | 29.2 | 20.5 | 45.9 | 3.1 | 226.6 | 4.3 | 41.8 | 60 | 26.4 | 47.5 | 30.5 | 70.7 | 101 | 89.8 | 65.3 | 62.7 | 274.5 | 267.9 | 263 | 248.8 | 210.8 | 175.5 | 236.1 | 204.5 | 299.9 | 280.7
2330 | 2156 | -6 | 0 | 0 | 192.1 | 189.2 | 174.8 | 169 | 200.9 | 29.2 | 20.5 | 45.9 | 3.2 | 232.6 | 3.9 | 41.7 | 59.7 | 26.4 | 47.1 | 30.5 | 70.7 | 101.1 | 90 | 65.1 | 62.8 | 274.5 | 267.8 | 262.9 | 248.6 | 210.7 | 175.4 | 236 | 204.4 | 299.7 | 280.6
2331 | 2157 | -6.2 | 0 | 0 | 191.9 | 189.1 | 174.6 | 168.9 | 200.9 | 29.2 | 20.5 | 45.9 | 3.2 | 223.4 | 3.3 | 41.7 | 59.6 | 26.4 | 46.7 | 30.5 | 70.8 | 101.2 | 90 | 64.9 | 62.9 | 274.5 | 267.7 | 262.8 | 248.5 | 210.6 | 175.3 | 235.9 | 204.3 | 299.5 | 280.4
2332 | 2158 | -6.2 | 0 | 0 | 191.8 | 189 | 174.4 | 168.8 | 200.8 | 29.2 | 20.5 | 45.9 | 3.6 | 211.3 | 3.1 | 41.8 | 59.6 | 26.4 | 47.1 | 30.5 | 70.7 | 101.3 | 90.1 | 64.9 | 62.9 | 274.4 | 267.6 | 262.7 | 248.3 | 210.5 | 175.2 | 235.8 | 204.2 | 299.4 | 280.3
2333 | 2159 | -6.1 | 0 | 0 | 191.7 | 189 | 174.4 | 168.8 | 200.7 | 29.2 | 20.5 | 45.9 | 3.7 | 225.8 | 3.2 | 41.7 | 59.6 | 26.5 | 47 | 30.6 | 70.7 | 101.4 | 90 | 64.8 | 62.9 | 274.4 | 267.5 | 262.6 | 248.2 | 210.4 | 175.1 | 235.6 | 204 | 299.2 | 280.1
2334 | 2160 | -6.1 | 0 | 0 | 191.6 | 189 | 174.4 | 168.8 | 200.6 | 29.2 | 20.5 | 45.9 | 3.5 | 258.1 | 3.6 | 41.7 | 59.7 | 26.5 | 47.1 | 30.6 | 70.7 | 101.4 | 89.9 | 64.7 | 62.8 | 274.4 | 267.4 | 262.4 | 248.1 | 210.3 | 175 | 235.6 | 203.9 | 299 | 280
2335 | 2161 | -6.2 | 0 | 0 | 191.6 | 189.1 | 174.3 | 168.8 | 200.5 | 29.2 | 20.5 | 45.9 | 3.1 | 257.6 | 4.7 | 41.7 | 59.7 | 26.5 | 47.4 | 30.6 | 70.7 | 101.5 | 89.8 | 64.7 | 62.5 | 274.3 | 267.3 | 262.3 | 247.9 | 210.2 | 174.9 | 235.4 | 203.8 | 298.8 | 279.9
2336 | 2162 | -6.2 | 0 | 0 | 191.6 | 189 | 174.2 | 168.7 | 200.4 | 29.2 | 20.5 | 45.8 | 3 | 244.8 | 5.2 | 41.7 | 59.8 | 26.4 | 47.3 | 30.6 | 70.6 | 101.8 | 89.7 | 64.9 | 62.3 | 274.3 | 267.2 | 262.2 | 247.8 | 210.1 | 174.9 | 235.3 | 203.7 | 298.7 | 279.7
2337 | 2163 | -6.2 | 0 | 0 | 191.4 | 188.8 | 174.1 | 168.6 | 200.3 | 29.2 | 20.5 | 45.8 | 3 | 249.6 | 5.6 | 41.7 | 59.8 | 26.4 | 47.6 | 30.6 | 70.6 | 102.2 | 89.6 | 64.9 | 62 | 274.3 | 267.1 | 262.1 | 247.6 | 210 | 174.8 | 235.2 | 203.6 | 298.5 | 279.6
2338 | 2164 | -6 | 0 | 0 | 191.2 | 188.6 | 174.1 | 168.5 | 200.2 | 29.2 | 20.5 | 45.8 | 3.3 | 234.8 | 5.2 | 41.7 | 59.7 | 26.4 | 46.9 | 30.7 | 70.7 | 102.5 | 89.6 | 64.8 | 61.7 | 274.3 | 267 | 262 | 247.5 | 209.9 | 174.7 | 235 | 203.5 | 298.3 | 279.5
2339 | 2165 | -6 | 0 | 0 | 191.1 | 188.5 | 174 | 168.4 | 200.1 | 29.2 | 20.5 | 45.8 | 3.1 | 232.8 | 4.9 | 41.7 | 59.6 | 26.3 | 46.2 | 30.7 | 70.8 | 102.6 | 89.4 | 64.8 | 62 | 274.2 | 266.9 | 261.9 | 247.4 | 209.8 | 174.6 | 234.9 | 203.4 | 298.1 | 279.3
2340 | 2166 | -6.1 | 0 | 0 | 191.1 | 188.4 | 174 | 168.3 | 200 | 29.1 | 20.5 | 45.8 | 3 | 240.4 | 4.3 | 41.7 | 59.5 | 26.3 | 46.5 | 30.7 | 70.9 | 102.9 | 89.4 | 64.9 | 62 | 274.2 | 266.8 | 261.8 | 247.2 | 209.6 | 174.5 | 234.8 | 203.3 | 298 | 279.2
2341 | 2167 | -6.2 | 0 | 0 | 191 | 188.4 | 173.9 | 168.2 | 200 | 29.2 | 20.5 | 45.8 | 3 | 237 | 3.9 | 41.6 | 59.3 | 26.3 | 45.9 | 30.7 | 70.8 | 103 | 89.4 | 64.7 | 62 | 274.1 | 266.7 | 261.6 | 247.1 | 209.5 | 174.4 | 234.6 | 203.2 | 297.8 | 279.1
2342 | 2168 | -6.2 | 0 | 0 | 191 | 188.3 | 173.7 | 168.1 | 199.9 | 29.2 | 20.5 | 45.7 | 3.2 | 237.9 | 3.6 | 41.6 | 59.3 | 26.3 | 45.8 | 30.7 | 70.7 | 102.7 | 89.3 | 64.4 | 61.9 | 274.1 | 266.6 | 261.5 | 246.9 | 209.4 | 174.3 | 234.6 | 203.1 | 297.6 | 278.9
2343 | 2169 | -6.3 | 0 | 0 | 190.9 | 188.1 | 173.7 | 168.1 | 199.8 | 29.1 | 20.5 | 45.7 | 3.6 | 234.5 | 3.5 | 41.6 | 59.4 | 26.2 | 45.8 | 30.7 | 70.3 | 102.6 | 89.1 | 64.3 | 62 | 274 | 266.5 | 261.4 | 246.8 | 209.3 | 174.2 | 234.5 | 202.9 | 297.4 | 278.8
2344 | 2170 | -6.2 | 0 | 0 | 190.7 | 188 | 173.7 | 168 | 199.8 | 29.1 | 20.5 | 45.7 | 3.7 | 228.9 | 3.3 | 41.6 | 59.4 | 26.2 | 44.8 | 30.6 | 69.4 | 102.5 | 89.1 | 64.1 | 61.8 | 274 | 266.4 | 261.3 | 246.6 | 209.2 | 174.1 | 234.3 | 202.9 | 297.3 | 278.7
2345 | 2171 | -6.1 | 0 | 0 | 190.5 | 187.9 | 173.5 | 167.9 | 199.7 | 29.1 | 20.5 | 45.7 | 3.6 | 231.5 | 3 | 41.6 | 59.4 | 26.2 | 44.4 | 30.6 | 69.3 | 102.8 | 89.1 | 64.1 | 61.8 | 273.9 | 266.3 | 261.2 | 246.5 | 209.1 | 174 | 234.2 | 202.7 | 297.1 | 278.5
2346 | 2172 | -6.1 | 0 | 0 | 190.3 | 187.7 | 173.4 | 167.9 | 199.6 | 29.1 | 20.5 | 45.6 | 3.3 | 226.1 | 3.1 | 41.6 | 59.3 | 26.2 | 45 | 30.6 | 69.1 | 103.1 | 89.3 | 64.1 | 61.9 | 273.9 | 266.2 | 261.1 | 246.4 | 209.1 | 173.9 | 234 | 202.6 | 296.9 | 278.4
2347 | 2173 | -6 | 0 | 0 | 190.2 | 187.5 | 173.2 | 167.7 | 199.5 | 29.1 | 20.5 | 45.6 | 3.5 | 211.5 | 2.9 | 41.5 | 59.1 | 26.2 | 45.6 | 30.6 | 68.5 | 103.2 | 89.4 | 64 | 62 | 273.9 | 266.1 | 261 | 246.2 | 208.9 | 173.8 | 233.9 | 202.5 | 296.7 | 278.3
2348 | 2174 | -6 | 0 | 0 | 190.2 | 187.2 | 173 | 167.6 | 199.4 | 29.1 | 20.5 | 45.6 | 3.2 | 220.6 | 3 | 41.5 | 59 | 26.2 | 45.5 | 30.5 | 68.4 | 103.3 | 89.4 | 64 | 61.9 | 273.8 | 266 | 260.9 | 246.1 | 208.8 | 173.8 | 233.7 | 202.4 | 296.6 | 278.1
2349 | 2175 | -6 | 0 | 0 | 190.2 | 187.1 | 172.7 | 167.5 | 199.3 | 29.1 | 20.5 | 45.6 | 3.6 | 227.8 | 3 | 41.5 | 59 | 26.2 | 46.1 | 30.5 | 68.7 | 103.4 | 89.3 | 63.8 | 61.9 | 273.8 | 265.9 | 260.7 | 245.9 | 208.7 | 173.7 | 233.7 | 202.3 | 296.4 | 278
2350 | 2176 | -6 | 0 | 0 | 190.1 | 186.9 | 172.5 | 167.4 | 199.2 | 29.1 | 20.5 | 45.6 | 3.7 | 219.9 | 2.8 | 41.5 | 59 | 26.2 | 46.4 | 30.5 | 68.8 | 103.5 | 89.1 | 63.8 | 61.8 | 273.8 | 265.8 | 260.6 | 245.8 | 208.6 | 173.6 | 233.6 | 202.2 | 296.2 | 277.8
2351 | 2177 | -6 | 0 | 0 | 189.9 | 186.7 | 172.4 | 167.4 | 199 | 29.1 | 20.5 | 45.6 | 3.3 | 229.3 | 2.8 | 41.5 | 58.9 | 26.3 | 46.6 | 30.4 | 68.8 | 103.9 | 89 | 63.9 | 61.6 | 273.7 | 265.7 | 260.5 | 245.6 | 208.5 | 173.6 | 233.4 | 202.1 | 296.1 | 277.7
2352 | 2178 | -6.1 | 0 | 0 | 189.7 | 186.5 | 172.4 | 167.3 | 198.9 | 29.1 | 20.5 | 45.6 | 3.2 | 235.6 | 3.3 | 41.5 | 58.7 | 26.2 | 45.9 | 30.4 | 69 | 104.5 | 89 | 63.9 | 61.7 | 273.7 | 265.6 | 260.4 | 245.5 | 208.4 | 173.5 | 233.3 | 202 | 295.9 | 277.6
2353 | 2179 | -6 | 0 | 0 | 189.6 | 186.4 | 172.5 | 167.2 | 198.8 | 29.1 | 20.5 | 45.6 | 3.2 | 209.2 | 3.9 | 41.5 | 58.6 | 26.2 | 45.1 | 30.5 | 68.4 | 104.5 | 89.1 | 63.9 | 61.8 | 273.7 | 265.6 | 260.3 | 245.3 | 208.3 | 173.4 | 233.1 | 201.9 | 295.7 | 277.5
2354 | 2180 | -5.9 | 0 | 0 | 189.5 | 186.2 | 172.3 | 167 | 198.6 | 29.1 | 20.5 | 45.6 | 3.2 | 209.1 | 4.3 | 41.5 | 58.6 | 26.2 | 44.3 | 30.6 | 68 | 104.7 | 89.1 | 63.7 | 61.9 | 273.6 | 265.5 | 260.2 | 245.2 | 208.2 | 173.3 | 233 | 201.8 | 295.6 | 277.3
2355 | 2181 | -6 | 0 | 0 | 189.6 | 186 | 172.2 | 166.9 | 198.5 | 29.1 | 20.5 | 45.6 | 3.2 | 232.3 | 4.2 | 41.5 | 58.5 | 26.2 | 44.4 | 30.6 | 68.1 | 104.9 | 89 | 63.6 | 62 | 273.6 | 265.4 | 260.1 | 245.1 | 208.1 | 173.2 | 232.9 | 201.7 | 295.4 | 277.2
2356 | 2182 | -6 | 0 | 0 | 189.6 | 185.9 | 172.1 | 166.8 | 198.4 | 29.1 | 20.5 | 45.5 | 3.1 | 219.4 | 3.9 | 41.5 | 58.6 | 26.1 | 44.8 | 30.6 | 68.5 | 105.4 | 88.9 | 63.7 | 62.2 | 273.5 | 265.3 | 260 | 244.9 | 208 | 173 | 232.7 | 201.5 | 295.2 | 277.1
2357 | 2183 | -6 | 0 | 0 | 189.4 | 185.9 | 172 | 166.5 | 198.3 | 29.1 | 20.5 | 45.5 | 3.3 | 226.1 | 3.4 | 41.4 | 58.6 | 26.1 | 45.3 | 30.6 | 68.8 | 105.3 | 89 | 63.6 | 62.3 | 273.5 | 265.2 | 259.8 | 244.8 | 207.8 | 173 | 232.7 | 201.5 | 295 | 276.9
2358 | 2184 | -6.2 | 0 | 0 | 189.3 | 185.7 | 171.9 | 166.5 | 198.2 | 29.1 | 20.5 | 45.5 | 3.5 | 257.7 | 2.9 | 41.4 | 58.5 | 26 | 45.1 | 30.6 | 68.4 | 104.9 | 88.9 | 63.5 | 62 | 273.5 | 265.1 | 259.7 | 244.6 | 207.7 | 172.9 | 232.5 | 201.3 | 294.9 | 276.8
2359 | 2185 | -6.3 | 0 | 0 | 189.1 | 185.5 | 171.8 | 166.4 | 198 | 29.1 | 20.5 | 45.5 | 3.4 | 278.5 | 2.7 | 41.4 | 58.3 | 26 | 45.7 | 30.5 | 68.3 | 104.9 | 88.6 | 63.5 | 61.8 | 273.4 | 265 | 259.6 | 244.5 | 207.6 | 172.8 | 232.4 | 201.3 | 294.7 | 276.7
2360 | 2186 | -6.2 | 0 | 0 | 189 | 185.4 | 171.8 | 166.4 | 197.9 | 29.1 | 20.5 | 45.4 | 3.1 | 276 | 2.7 | 41.4 | 58.1 | 26 | 46.2 | 30.3 | 68.5 | 105.1 | 88.5 | 63.6 | 61.7 | 273.4 | 264.9 | 259.5 | 244.4 | 207.5 | 172.7 | 232.3 | 201.1 | 294.5 | 276.5
2361 | 2187 | -6.2 | 0 | 0 | 188.7 | 185.3 | 171.8 | 166.4 | 197.8 | 29.1 | 20.5 | 45.4 | 3.2 | 261.7 | 2.9 | 41.4 | 58 | 26 | 45.7 | 30.2 | 68.8 | 105.5 | 88.5 | 63.6 | 61.7 | 273.3 | 264.8 | 259.4 | 244.2 | 207.4 | 172.6 | 232.1 | 201 | 294.4 | 276.4
2362 | 2188 | -6.3 | 0 | 0 | 188.3 | 185.3 | 171.5 | 166.4 | 197.8 | 29.1 | 20.5 | 45.4 | 3.1 | 235.1 | 2.9 | 41.4 | 57.9 | 25.9 | 45.1 | 30.2 | 68.6 | 105.4 | 88.4 | 63.6 | 61.1 | 273.3 | 264.7 | 259.3 | 244.1 | 207.3 | 172.5 | 232.1 | 200.9 | 294.2 | 276.3
2363 | 2189 | -6.3 | 0 | 0 | 188.2 | 185.3 | 171.5 | 166.4 | 197.7 | 29.1 | 20.5 | 45.3 | 3.2 | 233.9 | 3.2 | 41.4 | 57.8 | 25.9 | 45.2 | 30.1 | 68.2 | 105.3 | 88.3 | 63.4 | 60.9 | 273.2 | 264.6 | 259.2 | 243.9 | 207.2 | 172.4 | 232 | 200.8 | 294 | 276.1
2364 | 2190 | -6.2 | 0 | 0 | 188.2 | 185.2 | 171.4 | 166.4 | 197.6 | 29.1 | 20.5 | 45.3 | 3.4 | 246.7 | 3.8 | 41.4 | 57.8 | 25.9 | 45.1 | 30.1 | 68.6 | 105.9 | 88.2 | 63.4 | 61.2 | 273.2 | 264.5 | 259.1 | 243.8 | 207.1 | 172.4 | 231.8 | 200.7 | 293.8 | 276
2365 | 2191 | -6.1 | 0 | 0 | 188.2 | 185.1 | 171.4 | 166.3 | 197.5 | 29 | 20.5 | 45.3 | 3.1 | 242.4 | 3.6 | 41.4 | 57.7 | 25.9 | 45.3 | 30.2 | 68.9 | 105.8 | 88.2 | 63.4 | 61.3 | 273.2 | 264.4 | 258.9 | 243.7 | 206.9 | 172.3 | 231.7 | 200.6 | 293.7 | 275.9
2366 | 2192 | -6.1 | 0 | 0 | 188.2 | 185 | 171.3 | 166.2 | 197.3 | 29 | 20.5 | 45.3 | 3.1 | 240.9 | 3.3 | 41.4 | 57.6 | 25.9 | 44.9 | 30.2 | 69 | 105.6 | 88.3 | 63.4 | 61.2 | 273.1 | 264.3 | 258.8 | 243.5 | 206.8 | 172.3 | 231.5 | 200.5 | 293.5 | 275.7
2367 | 2193 | -6 | 0 | 0 | 188.2 | 184.9 | 171.3 | 166 | 197.3 | 29 | 20.5 | 45.2 | 3.1 | 227.6 | 2.8 | 41.3 | 57.5 | 25.9 | 44.9 | 30.3 | 69 | 106 | 88.2 | 63.2 | 61.1 | 273.1 | 264.2 | 258.7 | 243.4 | 206.7 | 172.2 | 231.4 | 200.4 | 293.3 | 275.6
2368 | 2194 | -6.1 | 0 | 0 | 188 | 184.7 | 171.3 | 165.9 | 197.2 | 29 | 20.5 | 45.2 | 3.6 | 224.5 | 2.4 | 41.3 | 57.5 | 25.9 | 44.7 | 30.3 | 68.9 | 105.9 | 88.1 | 63 | 61.2 | 273 | 264.1 | 258.6 | 243.2 | 206.6 | 172.1 | 231.2 | 200.3 | 293.2 | 275.5
2369 | 2195 | -6.2 | 0 | 0 | 187.9 | 184.6 | 171.3 | 165.8 | 197.1 | 28.9 | 20.5 | 45.2 | 3.5 | 225.3 | 2.2 | 41.3 | 57.7 | 25.9 | 44.3 | 30.4 | 69.1 | 106.4 | 87.9 | 63.2 | 61.3 | 273 | 264 | 258.5 | 243.1 | 206.5 | 172 | 231.2 | 200.2 | 293 | 275.3
2370 | 2196 | -6.2 | 0 | 0 | 187.8 | 184.5 | 171.3 | 165.8 | 197 | 28.9 | 20.5 | 45.2 | 3.5 | 222.2 | 2.3 | 41.3 | 57.7 | 25.9 | 44.4 | 30.4 | 69.3 | 106.5 | 87.7 | 63.3 | 61.4 | 273 | 263.9 | 258.4 | 242.9 | 206.3 | 171.9 | 231 | 200.1 | 292.9 | 275.2
2371 | 2197 | -6.2 | 0 | 0 | 187.6 | 184.3 | 171.2 | 165.7 | 196.9 | 28.8 | 20.5 | 45.2 | 3.4 | 221.1 | 2.9 | 41.3 | 57.6 | 25.9 | 44.5 | 30.4 | 69.4 | 106.7 | 87.6 | 63.5 | 61.8 | 272.9 | 263.8 | 258.3 | 242.8 | 206.2 | 171.8 | 230.8 | 199.9 | 292.7 | 275.1
2372 | 2198 | -6.1 | 0 | 0 | 187.6 | 184.1 | 171 | 165.6 | 196.8 | 28.7 | 20.5 | 45.2 | 3 | 206.8 | 3.4 | 41.2 | 57.5 | 25.8 | 44.6 | 30.5 | 69.5 | 106.8 | 87.5 | 63.5 | 61.9 | 272.9 | 263.7 | 258.2 | 242.7 | 206.1 | 171.7 | 230.7 | 199.9 | 292.5 | 274.9
2373 | 2199 | -6.1 | 0 | 0 | 187.6 | 183.8 | 170.8 | 165.4 | 196.7 | 28.7 | 20.5 | 45.2 | 3.3 | 216 | 3.4 | 41.2 | 57.4 | 25.8 | 44.2 | 30.5 | 69.5 | 106.8 | 87.2 | 63.4 | 61.9 | 272.9 | 263.6 | 258.1 | 242.5 | 206 | 171.6 | 230.6 | 199.7 | 292.3 | 274.8
2374 | 2200 | -6.1 | 0 | 0 | 187.5 | 183.6 | 170.7 | 165.3 | 196.6 | 28.7 | 20.5 | 45.2 | 3.4 | 218.5 | 3.1 | 41.2 | 57.4 | 25.8 | 44.2 | 30.4 | 69.6 | 107 | 86.9 | 63.4 | 62 | 272.8 | 263.5 | 258 | 242.4 | 205.9 | 171.5 | 230.5 | 199.6 | 292.2 | 274.7
2375 | 2201 | -5.8 | 0 | 0 | 187.4 | 183.5 | 170.7 | 165.1 | 196.5 | 28.7 | 20.5 | 45.1 | 3.3 | 221.3 | 2.6 | 41.2 | 57.4 | 25.8 | 44.2 | 30.3 | 69.4 | 106.9 | 86.7 | 63.3 | 62.1 | 272.8 | 263.4 | 257.9 | 242.2 | 205.8 | 171.4 | 230.4 | 199.5 | 292 | 274.6
2376 | 2202 | -5.7 | 0 | 0 | 187.4 | 183.5 | 170.7 | 165 | 196.3 | 28.7 | 20.5 | 45.1 | 3.4 | 231.5 | 2.4 | 41.2 | 57.5 | 25.7 | 44.2 | 30.3 | 69.4 | 106.8 | 86.7 | 63.3 | 62.2 | 272.7 | 263.3 | 257.7 | 242.1 | 205.7 | 171.3 | 230.3 | 199.4 | 291.8 | 274.4
2377 | 2203 | -6 | 0 | 0 | 187.3 | 183.6 | 170.8 | 164.9 | 196.2 | 28.7 | 20.5 | 45.1 | 3.6 | 232.3 | 2.4 | 41.2 | 57.5 | 25.7 | 44.5 | 30.3 | 69.3 | 106.8 | 86.8 | 63.2 | 62.2 | 272.7 | 263.2 | 257.6 | 242 | 205.6 | 171.2 | 230.1 | 199.3 | 291.7 | 274.3
2378 | 2204 | -6.2 | 0 | 0 | 187.2 | 183.6 | 170.7 | 164.8 | 196.1 | 28.7 | 20.5 | 45.1 | 3.6 | 236.7 | 2.5 | 41.2 | 57.5 | 25.6 | 44.2 | 30.2 | 69.1 | 106.5 | 86.9 | 63.1 | 62 | 272.7 | 263.1 | 257.5 | 241.8 | 205.6 | 171.1 | 230 | 199.2 | 291.5 | 274.2
2379 | 2205 | -6.3 | 0 | 0 | 187.1 | 183.6 | 170.5 | 164.7 | 195.9 | 28.7 | 20.5 | 45.1 | 3.1 | 252.8 | 3.3 | 41.2 | 57.6 | 25.6 | 44.6 | 30 | 69 | 106.4 | 86.9 | 63 | 61.8 | 272.6 | 263.1 | 257.4 | 241.7 | 205.5 | 171 | 229.9 | 199.1 | 291.4 | 274
2380 | 2206 | -6.3 | 0 | 0 | 186.9 | 183.6 | 170.3 | 164.7 | 195.8 | 28.7 | 20.5 | 45 | 3 | 258.2 | 3.7 | 41.2 | 57.6 | 25.6 | 45.1 | 30 | 68.7 | 106.2 | 86.9 | 63 | 61.6 | 272.6 | 263 | 257.3 | 241.6 | 205.4 | 170.9 | 229.8 | 199 | 291.2 | 273.9
2381 | 2207 | -6.2 | 0 | 0 | 186.8 | 183.5 | 170.3 | 164.6 | 195.7 | 28.8 | 20.5 | 45 | 3.1 | 250.6 | 3.8 | 41.1 | 57.5 | 25.7 | 45.2 | 30.2 | 68.2 | 106.1 | 86.8 | 63 | 61.6 | 272.5 | 262.9 | 257.2 | 241.4 | 205.3 | 170.8 | 229.7 | 198.9 | 291 | 273.8
2382 | 2208 | -6.2 | 0 | 0 | 186.7 | 183.3 | 170.2 | 164.6 | 195.6 | 28.8 | 20.6 | 45 | 3.1 | 245.1 | 3.9 | 41.1 | 57.4 | 25.7 | 45.3 | 30.2 | 68.2 | 106.2 | 86.8 | 63 | 61.5 | 272.4 | 262.8 | 257.1 | 241.3 | 205.3 | 170.8 | 229.6 | 198.8 | 290.9 | 273.6
2383 | 2209 | -6 | 0 | 0 | 186.6 | 183.2 | 170.1 | 164.5 | 195.5 | 28.8 | 20.6 | 45 | 3.3 | 243.1 | 4.1 | 41.1 | 57.4 | 25.8 | 45.2 | 30.2 | 68.4 | 106.4 | 86.6 | 63 | 61.6 | 272.4 | 262.7 | 257 | 241.1 | 205.1 | 170.8 | 229.5 | 198.7 | 290.7 | 273.5
2384 | 2210 | -5.9 | 0 | 0 | 186.6 | 183 | 169.9 | 164.4 | 195.5 | 28.8 | 20.6 | 45 | 3.5 | 242.9 | 4.4 | 41.1 | 57.3 | 25.8 | 44.8 | 30 | 68.5 | 106.8 | 86.6 | 63.1 | 61.8 | 272.3 | 262.6 | 256.8 | 241 | 204.9 | 170.7 | 229.3 | 198.6 | 290.5 | 273.4
2385 | 2211 | -6.1 | 0 | 0 | 186.5 | 182.8 | 169.8 | 164.2 | 195.4 | 28.8 | 20.6 | 45 | 3.4 | 240.8 | 4.3 | 41.1 | 57.3 | 25.8 | 44.3 | 30 | 68.7 | 107.3 | 86.7 | 63.2 | 61.9 | 272.3 | 262.5 | 256.8 | 240.9 | 204.8 | 170.6 | 229.2 | 198.5 | 290.4 | 273.2
2386 | 2212 | -6 | 0 | 0 | 186.5 | 182.7 | 169.8 | 164.1 | 195.3 | 28.7 | 20.6 | 45 | 3.7 | 242.6 | 4.3 | 41.1 | 57.3 | 25.8 | 43.7 | 29.9 | 68.9 | 107.7 | 86.7 | 63.2 | 62 | 272.2 | 262.4 | 256.6 | 240.7 | 204.7 | 170.6 | 229.1 | 198.4 | 290.2 | 273.1
2387 | 2213 | -6 | 0 | 0 | 186.3 | 182.8 | 169.7 | 163.9 | 195.2 | 28.7 | 20.6 | 44.9 | 3.5 | 244.2 | 4.4 | 41.1 | 57.3 | 25.8 | 44.1 | 29.8 | 68.8 | 107.8 | 86.8 | 63 | 62 | 272.2 | 262.3 | 256.5 | 240.6 | 204.6 | 170.5 | 229 | 198.3 | 290 | 273
2388 | 2214 | -6.3 | 0 | 0 | 186.2 | 182.7 | 169.5 | 163.8 | 195.2 | 28.7 | 20.6 | 44.9 | 3.5 | 227.6 | 4.4 | 41 | 57.1 | 25.8 | 44.5 | 29.9 | 68.5 | 107.6 | 86.8 | 63 | 61.9 | 272.1 | 262.2 | 256.4 | 240.5 | 204.5 | 170.4 | 228.9 | 198.2 | 289.9 | 272.8
2389 | 2215 | -6.3 | 0 | 0 | 186 | 182.5 | 169.4 | 163.6 | 195.1 | 28.6 | 20.6 | 44.9 | 3.7 | 240.1 | 4.5 | 41 | 56.9 | 25.7 | 44.9 | 29.9 | 68.5 | 107.7 | 86.7 | 62.9 | 61.8 | 272.1 | 262.1 | 256.3 | 240.3 | 204.4 | 170.3 | 228.8 | 198.1 | 289.7 | 272.7
2390 | 2216 | -6.2 | 0 | 0 | 185.9 | 182.5 | 169.3 | 163.4 | 195 | 28.6 | 20.6 | 44.9 | 3.4 | 262.3 | 4.7 | 41 | 56.8 | 25.7 | 45.2 | 29.7 | 68.6 | 108.1 | 86.7 | 63 | 61.6 | 272 | 262 | 256.2 | 240.2 | 204.3 | 170.2 | 228.6 | 198 | 289.6 | 272.6
2391 | 2217 | -6.2 | 0 | 0 | 185.8 | 182.4 | 169.2 | 163.3 | 195 | 28.6 | 20.6 | 44.9 | 3.2 | 238.2 | 4.5 | 41 | 56.9 | 25.6 | 45.4 | 29.6 | 68.7 | 108.3 | 86.7 | 63 | 61.6 | 272 | 261.9 | 256.1 | 240 | 204.2 | 170.1 | 228.5 | 197.9 | 289.4 | 272.4
2392 | 2218 | -6.2 | 0 | 0 | 185.8 | 182.3 | 169 | 163.2 | 194.9 | 28.5 | 20.6 | 44.9 | 3.1 | 227.8 | 4.2 | 41 | 56.9 | 25.5 | 44.7 | 29.6 | 68.5 | 108.1 | 86.7 | 62.9 | 61.6 | 271.9 | 261.8 | 256 | 239.9 | 204.1 | 169.9 | 228.4 | 197.8 | 289.2 | 272.3
2393 | 2219 | -6.3 | 0 | 0 | 185.7 | 182.1 | 168.8 | 163.1 | 194.9 | 28.5 | 20.6 | 44.8 | 3.2 | 237.7 | 3.8 | 41 | 57 | 25.5 | 43.8 | 29.5 | 68.5 | 108 | 86.7 | 62.9 | 61.5 | 271.9 | 261.7 | 255.9 | 239.8 | 204 | 169.8 | 228.2 | 197.7 | 289.1 | 272.2
2394 | 2220 | -6.4 | 0 | 0 | 185.5 | 181.8 | 168.7 | 162.9 | 194.8 | 28.4 | 20.6 | 44.8 | 3.3 | 233.6 | 3.8 | 41 | 57 | 25.6 | 44.3 | 29.4 | 68.8 | 108.2 | 86.7 | 62.9 | 61.7 | 271.8 | 261.6 | 255.8 | 239.7 | 203.9 | 169.7 | 228.1 | 197.6 | 288.9 | 272.1
2395 | 2221 | -6.4 | 0 | 0 | 185.4 | 181.8 | 168.6 | 162.9 | 194.6 | 28.4 | 20.6 | 44.8 | 3.3 | 218.3 | 3.8 | 40.9 | 56.9 | 25.6 | 45 | 29.5 | 68.7 | 108 | 86.7 | 62.6 | 61.7 | 271.8 | 261.5 | 255.7 | 239.5 | 203.8 | 169.7 | 228 | 197.5 | 288.8 | 271.9
2396 | 2222 | -6.4 | 0 | 0 | 185.3 | 181.9 | 168.4 | 162.8 | 194.7 | 28.4 | 20.6 | 44.8 | 3.3 | 200.5 | 3.7 | 40.9 | 56.8 | 25.6 | 45.6 | 29.5 | 68.3 | 107.8 | 86.6 | 62.3 | 61.4 | 271.8 | 261.4 | 255.6 | 239.4 | 203.7 | 169.6 | 227.9 | 197.4 | 288.6 | 271.8
2397 | 2223 | -6.3 | 0 | 0 | 185.2 | 181.9 | 168.4 | 162.7 | 194.7 | 28.4 | 20.6 | 44.8 | 3.5 | 193.8 | 3.5 | 40.9 | 56.8 | 25.6 | 45.4 | 29.6 | 68.3 | 108.2 | 86.7 | 62.4 | 61.4 | 271.7 | 261.3 | 255.5 | 239.3 | 203.6 | 169.5 | 227.8 | 197.3 | 288.5 | 271.7
2398 | 2224 | -6.1 | 0 | 0 | 185.1 | 181.8 | 168.3 | 162.8 | 194.6 | 28.3 | 20.6 | 44.7 | 3.4 | 208.9 | 3.2 | 40.9 | 56.9 | 25.6 | 45.7 | 29.6 | 68.4 | 108.1 | 86.6 | 62.4 | 61.3 | 271.6 | 261.2 | 255.4 | 239.1 | 203.5 | 169.4 | 227.7 | 197.2 | 288.3 | 271.5
2399 | 2225 | -6.2 | 0 | 0 | 185 | 181.8 | 168.2 | 162.8 | 194.5 | 28.3 | 20.6 | 44.7 | 3.3 | 227.6 | 3 | 40.9 | 57 | 25.6 | 45.4 | 29.7 | 67.9 | 107.8 | 86.5 | 62.4 | 61.2 | 271.6 | 261.1 | 255.2 | 239 | 203.5 | 169.3 | 227.6 | 197.1 | 288.1 | 271.4
2400 | 2226 | -6.2 | 0 | 0 | 185 | 181.7 | 168.1 | 162.7 | 194.4 | 28.3 | 20.6 | 44.7 | 3 | 244.9 | 3 | 40.9 | 57 | 25.7 | 45.5 | 29.7 | 68.1 | 108 | 86.4 | 62.4 | 61.2 | 271.6 | 261.1 | 255.1 | 238.9 | 203.4 | 169.3 | 227.4 | 197 | 288 | 271.3
2401 | 2227 | -6.1 | 0 | 0 | 185 | 181.6 | 168.1 | 162.7 | 194.4 | 28.2 | 20.6 | 44.6 | 3.1 | 251.9 | 2.9 | 40.9 | 56.9 | 25.7 | 45.8 | 29.6 | 68.1 | 108.3 | 86.3 | 62.5 | 61.2 | 271.5 | 261 | 255 | 238.7 | 203.2 | 169.2 | 227.3 | 196.9 | 287.8 | 271.1
2402 | 2228 | -6.2 | 0 | 0 | 184.8 | 181.5 | 168 | 162.6 | 194.3 | 28.2 | 20.6 | 44.6 | 3 | 238.2 | 2.7 | 40.8 | 56.9 | 25.8 | 46.1 | 29.5 | 68.2 | 108.8 | 86.2 | 62.6 | 61.2 | 271.5 | 260.9 | 254.9 | 238.6 | 203.1 | 169.1 | 227.1 | 196.8 | 287.6 | 271
2403 | 2229 | -6.2 | 0 | 0 | 184.5 | 181.3 | 168 | 162.5 | 194.2 | 28.2 | 20.6 | 44.6 | 3.1 | 218.1 | 2.8 | 40.8 | 56.9 | 25.9 | 45.6 | 29.5 | 68.4 | 109.2 | 86.1 | 62.7 | 61.3 | 271.4 | 260.8 | 254.8 | 238.5 | 203 | 169 | 227 | 196.7 | 287.5 | 270.9
2404 | 2230 | -6.2 | 0 | 0 | 184.3 | 181.1 | 168 | 162.4 | 194.1 | 28.2 | 20.6 | 44.5 | 2.9 | 210.4 | 2.8 | 40.8 | 56.8 | 26 | 45.1 | 29.6 | 68.7 | 109.4 | 86 | 62.7 | 61.1 | 271.4 | 260.7 | 254.7 | 238.3 | 203 | 168.9 | 226.9 | 196.6 | 287.3 | 270.8
2405 | 2231 | -6.2 | 0 | 0 | 184.3 | 180.9 | 167.8 | 162.2 | 194 | 28.2 | 20.6 | 44.5 | 2.9 | 214.3 | 2.9 | 40.8 | 56.7 | 26 | 44.9 | 29.5 | 68.9 | 109.8 | 85.9 | 62.9 | 61.3 | 271.3 | 260.6 | 254.6 | 238.2 | 202.8 | 168.8 | 226.8 | 196.5 | 287.2 | 270.6
2406 | 2232 | -6.1 | 0 | 0 | 184.4 | 180.7 | 167.6 | 162.1 | 193.9 | 28.2 | 20.6 | 44.4 | 3.3 | 217.2 | 3.2 | 40.8 | 56.8 | 26.1 | 43.8 | 29.6 | 69 | 109.8 | 86 | 62.9 | 61.4 | 271.3 | 260.5 | 254.5 | 238.1 | 202.7 | 168.7 | 226.6 | 196.4 | 287 | 270.5
2407 | 2233 | -6.1 | 0 | 0 | 184.4 | 180.5 | 167.5 | 162 | 193.9 | 28.2 | 20.6 | 44.4 | 3.3 | 219.8 | 3.9 | 40.8 | 56.7 | 26 | 43 | 29.6 | 68.9 | 109.4 | 85.8 | 62.7 | 61.1 | 271.2 | 260.4 | 254.4 | 237.9 | 202.6 | 168.5 | 226.4 | 196.3 | 286.8 | 270.4
2408 | 2234 | -6 | 0 | 0 | 184.2 | 180.4 | 167.4 | 162 | 193.8 | 28.2 | 20.6 | 44.5 | 3.4 | 221 | 4.6 | 40.8 | 56.6 | 26 | 42.8 | 29.6 | 68.8 | 109 | 85.7 | 62.5 | 61 | 271.2 | 260.3 | 254.3 | 237.8 | 202.5 | 168.4 | 226.4 | 196.2 | 286.7 | 270.2
2409 | 2235 | -6 | 0 | 0 | 184 | 180.4 | 167.3 | 162 | 193.7 | 28.2 | 20.6 | 44.4 | 3.4 | 218 | 4.8 | 40.8 | 56.5 | 26 | 42.8 | 29.6 | 68.9 | 108.6 | 85.7 | 62.5 | 61.1 | 271.1 | 260.2 | 254.2 | 237.7 | 202.4 | 168.4 | 226.3 | 196.1 | 286.5 | 270.1
2410 | 2236 | -6 | 0 | 0 | 183.6 | 180.5 | 167.2 | 162 | 193.7 | 28.2 | 20.6 | 44.5 | 3.3 | 201.7 | 4.9 | 40.8 | 56.5 | 26.1 | 43.7 | 29.6 | 68.8 | 108.4 | 85.8 | 62.6 | 61 | 271.1 | 260.1 | 254.1 | 237.6 | 202.3 | 168.3 | 226.2 | 196 | 286.4 | 270
2411 | 2237 | -6 | 0 | 0 | 183.2 | 180.5 | 166.9 | 162 | 193.6 | 28.2 | 20.6 | 44.4 | 3.7 | 196.1 | 4.6 | 40.8 | 56.5 | 26.1 | 43.4 | 29.5 | 68.8 | 108.4 | 85.8 | 62.6 | 60.8 | 271 | 260 | 254 | 237.4 | 202.3 | 168.2 | 226.1 | 195.9 | 286.2 | 269.8
2412 | 2238 | -6 | 0 | 0 | 183 | 180.4 | 166.7 | 161.9 | 193.5 | 28.1 | 20.6 | 44.4 | 3.6 | 192.4 | 4.3 | 40.8 | 56.4 | 26.1 | 43.9 | 29.5 | 68.8 | 108.7 | 85.8 | 62.6 | 60.9 | 271 | 259.9 | 253.9 | 237.3 | 202.2 | 168.1 | 225.9 | 195.8 | 286 | 269.7
2413 | 2239 | -5.9 | 0 | 0 | 182.9 | 180.3 | 166.7 | 161.9 | 193.5 | 28.1 | 20.6 | 44.3 | 3.2 | 198.9 | 4.1 | 40.7 | 56.3 | 26.1 | 43.9 | 29.5 | 68.9 | 108.7 | 85.7 | 62.6 | 61.1 | 271 | 259.8 | 253.8 | 237.2 | 202.1 | 168 | 225.8 | 195.7 | 285.9 | 269.6
2414 | 2240 | -6.1 | 0 | 0 | 182.9 | 180 | 166.7 | 161.8 | 193.4 | 28.1 | 20.6 | 44.3 | 3.6 | 199.5 | 4 | 40.7 | 56.3 | 26.2 | 43.9 | 29.5 | 68.9 | 108.7 | 85.6 | 62.4 | 61.1 | 270.9 | 259.7 | 253.6 | 237 | 202 | 167.9 | 225.7 | 195.6 | 285.7 | 269.5
2415 | 2241 | -6.1 | 0 | 0 | 182.9 | 179.7 | 166.7 | 161.7 | 193.3 | 28.2 | 20.6 | 44.2 | 3.4 | 200.8 | 4 | 40.7 | 56.2 | 26.2 | 44 | 29.4 | 68.8 | 108.8 | 85.4 | 62.3 | 61.2 | 270.9 | 259.6 | 253.5 | 236.9 | 201.8 | 167.8 | 225.6 | 195.5 | 285.6 | 269.3
2416 | 2242 | -6.2 | 0 | 0 | 182.9 | 179.6 | 166.6 | 161.6 | 193.1 | 28.2 | 20.6 | 44.2 | 3.5 | 204.3 | 3.8 | 40.7 | 56.2 | 26.1 | 44.3 | 29.3 | 68.6 | 109 | 85.3 | 62.3 | 61.3 | 270.8 | 259.5 | 253.4 | 236.8 | 201.7 | 167.8 | 225.5 | 195.4 | 285.4 | 269.2
2417 | 2243 | -6.2 | 0 | 0 | 182.9 | 179.6 | 166.5 | 161.4 | 193 | 28.2 | 20.6 | 44.2 | 3.1 | 221.5 | 3.7 | 40.7 | 55.9 | 26.2 | 44.4 | 29.3 | 68.7 | 109.2 | 85.3 | 62.2 | 61.4 | 270.8 | 259.4 | 253.3 | 236.7 | 201.6 | 167.7 | 225.4 | 195.3 | 285.2 | 269.1
2418 | 2244 | -6.1 | 0 | 0 | 182.9 | 179.7 | 166.3 | 161.3 | 192.9 | 28.2 | 20.6 | 44.2 | 3.1 | 240.6 | 4.1 | 40.7 | 55.8 | 26.2 | 44.5 | 29.2 | 68.6 | 109.1 | 85.3 | 62 | 61.3 | 270.8 | 259.4 | 253.2 | 236.5 | 201.5 | 167.6 | 225.2 | 195.2 | 285.1 | 269
2419 | 2245 | -6.2 | 0 | 0 | 182.8 | 179.6 | 166.2 | 161.2 | 192.9 | 28.2 | 20.6 | 44.2 | 3.4 | 233.3 | 4 | 40.7 | 55.8 | 26.1 | 44.8 | 29.2 | 68.5 | 109 | 85.3 | 62 | 61 | 270.7 | 259.3 | 253.1 | 236.4 | 201.4 | 167.5 | 225.1 | 195.1 | 284.9 | 268.8
2420 | 2246 | -6.3 | 0 | 0 | 182.7 | 179.6 | 166.1 | 161 | 192.9 | 28.2 | 20.6 | 44.2 | 3.3 | 193 | 4 | 40.7 | 55.9 | 26.1 | 45.3 | 29.2 | 68.4 | 109 | 85.3 | 62.1 | 60.8 | 270.7 | 259.2 | 253 | 236.3 | 201.3 | 167.4 | 225 | 195 | 284.8 | 268.7
2421 | 2247 | -6.2 | 0 | 0 | 182.5 | 179.4 | 166.1 | 161 | 192.9 | 28.2 | 20.6 | 44.1 | 3.4 | 190.6 | 4 | 40.7 | 56 | 26 | 45.6 | 29.2 | 68.4 | 109.4 | 85.1 | 62.2 | 60.5 | 270.6 | 259.1 | 252.9 | 236.1 | 201.2 | 167.3 | 224.8 | 194.9 | 284.6 | 268.6
2422 | 2248 | -6 | 0 | 0 | 182.4 | 179.2 | 166.1 | 160.9 | 192.8 | 28.2 | 20.6 | 44.1 | 3.4 | 208.2 | 5 | 40.7 | 56 | 26 | 46 | 29.1 | 68.5 | 109.7 | 84.9 | 62.3 | 60.3 | 270.6 | 259 | 252.8 | 236 | 201.2 | 167.2 | 224.7 | 194.8 | 284.5 | 268.4
2423 | 2249 | -6.1 | 0 | 0 | 182.3 | 179.1 | 166 | 160.8 | 192.7 | 28.3 | 20.6 | 44.1 | 3.2 | 206 | 5.5 | 40.7 | 56.1 | 26 | 46.2 | 29.1 | 68.4 | 110 | 84.8 | 62.3 | 60.4 | 270.5 | 258.9 | 252.7 | 235.9 | 201 | 167.1 | 224.6 | 194.7 | 284.3 | 268.3
2424 | 2250 | -6.2 | 0 | 0 | 182.4 | 179 | 165.9 | 160.7 | 192.5 | 28.3 | 20.6 | 44.1 | 3.2 | 205.3 | 5.3 | 40.7 | 56.2 | 26 | 46 | 29.1 | 68.5 | 110.2 | 84.7 | 62.3 | 60.7 | 270.5 | 258.8 | 252.6 | 235.7 | 200.9 | 167 | 224.5 | 194.6 | 284.1 | 268.2
2425 | 2251 | -6.1 | 0 | 0 | 182.3 | 178.8 | 165.8 | 160.6 | 192.5 | 28.3 | 20.7 | 44.1 | 3 | 244 | 4.7 | 40.7 | 56.2 | 26 | 45.9 | 29.2 | 68.4 | 110.1 | 84.8 | 62.2 | 60.9 | 270.4 | 258.7 | 252.5 | 235.6 | 200.8 | 166.9 | 224.3 | 194.5 | 284 | 268
2426 | 2252 | -6.1 | 0 | 0 | 182.1 | 178.8 | 165.7 | 160.4 | 192.4 | 28.3 | 20.7 | 44.1 | 3.2 | 256.1 | 4 | 40.7 | 56.1 | 26 | 45.2 | 29.1 | 68.2 | 109.9 | 84.8 | 62.1 | 61 | 270.4 | 258.6 | 252.4 | 235.5 | 200.7 | 166.8 | 224.2 | 194.4 | 283.8 | 267.9
2427 | 2253 | -6.2 | 0 | 0 | 182 | 178.8 | 165.7 | 160.1 | 192.4 | 28.3 | 20.6 | 44.1 | 3.3 | 239.9 | 3.3 | 40.7 | 56.1 | 26 | 44.8 | 29.2 | 68 | 110 | 84.8 | 62.1 | 61 | 270.4 | 258.5 | 252.3 | 235.3 | 200.6 | 166.7 | 224.1 | 194.4 | 283.7 | 267.8
2428 | 2254 | -6.3 | 0 | 0 | 181.9 | 178.7 | 165.7 | 159.9 | 192.3 | 28.3 | 20.6 | 44.1 | 3.3 | 209.1 | 2.9 | 40.7 | 56.1 | 26.1 | 44.8 | 29.2 | 68 | 110.2 | 84.8 | 62 | 60.8 | 270.3 | 258.4 | 252.2 | 235.2 | 200.5 | 166.6 | 224 | 194.3 | 283.5 | 267.6
2429 | 2255 | -6 | 0 | 0 | 181.7 | 178.7 | 165.5 | 159.7 | 192.1 | 28.2 | 20.7 | 44.1 | 3.1 | 186 | 2.7 | 40.6 | 55.9 | 26.1 | 44.7 | 29.3 | 68.1 | 110.4 | 84.7 | 62 | 60.7 | 270.2 | 258.3 | 252.1 | 235.1 | 200.4 | 166.5 | 223.9 | 194.1 | 283.4 | 267.5
2430 | 2256 | -6 | 0 | 0 | 181.7 | 178.6 | 165.4 | 159.6 | 191.9 | 28.2 | 20.7 | 44 | 3.2 | 182.6 | 2.7 | 40.7 | 55.8 | 26.1 | 44.8 | 29.4 | 68.2 | 110.6 | 84.7 | 62 | 60.3 | 270.2 | 258.2 | 252 | 234.9 | 200.3 | 166.4 | 223.8 | 194 | 283.2 | 267.4
2431 | 2257 | -6.1 | 0 | 0 | 181.5 | 178.7 | 165.4 | 159.6 | 191.9 | 28.2 | 20.7 | 44 | 3 | 182.8 | 2.7 | 40.6 | 55.7 | 26.1 | 44.8 | 29.4 | 68.3 | 110.6 | 84.7 | 62 | 60.2 | 270.1 | 258.1 | 251.9 | 234.8 | 200.2 | 166.3 | 223.7 | 194 | 283 | 267.3
2432 | 2258 | -5.9 | 0 | 0 | 181.4 | 178.6 | 165.4 | 159.6 | 191.9 | 28.2 | 20.7 | 44 | 3 | 184.5 | 2.6 | 40.6 | 55.6 | 26.2 | 45 | 29.5 | 68.3 | 110.6 | 84.6 | 62 | 60.5 | 270.1 | 258.1 | 251.8 | 234.7 | 200.1 | 166.2 | 223.6 | 193.8 | 282.9 | 267.2
2433 | 2259 | -6 | 0 | 0 | 181.2 | 178.6 | 165.3 | 159.6 | 191.9 | 28.1 | 20.7 | 44 | 3.1 | 190.1 | 2.9 | 40.6 | 55.6 | 26.2 | 45.4 | 29.5 | 68.2 | 110.3 | 84.6 | 61.9 | 60.5 | 270.1 | 258 | 251.7 | 234.6 | 200 | 166.1 | 223.5 | 193.8 | 282.7 | 267
2434 | 2260 | -6 | 0 | 0 | 180.9 | 178.6 | 165.2 | 159.6 | 191.8 | 28.1 | 20.7 | 44 | 3.3 | 199.2 | 3.3 | 40.6 | 55.6 | 26.2 | 45.3 | 29.6 | 67.7 | 110 | 84.4 | 61.8 | 60.4 | 270 | 257.9 | 251.6 | 234.4 | 199.9 | 166 | 223.4 | 193.7 | 282.6 | 266.9
2435 | 2261 | -5.8 | 0 | 0 | 180.8 | 178.6 | 165.2 | 159.5 | 191.7 | 28.1 | 20.7 | 44 | 3.2 | 209.7 | 3.6 | 40.6 | 55.5 | 26.2 | 45.5 | 29.5 | 67.7 | 110.1 | 84.3 | 61.9 | 60.3 | 270 | 257.8 | 251.5 | 234.3 | 199.9 | 166 | 223.3 | 193.5 | 282.5 | 266.8
2436 | 2262 | -5.9 | 0 | 0 | 180.8 | 178.5 | 165.1 | 159.4 | 191.7 | 28 | 20.7 | 44 | 3.2 | 216.7 | 3.6 | 40.6 | 55.4 | 26.1 | 45.8 | 29.5 | 67.8 | 110.2 | 84.1 | 61.9 | 60.2 | 269.9 | 257.7 | 251.4 | 234.2 | 199.8 | 165.9 | 223.2 | 193.5 | 282.3 | 266.6
2437 | 2263 | -6.1 | 0 | 0 | 180.9 | 178.4 | 165 | 159.4 | 191.7 | 28 | 20.7 | 44 | 3.4 | 226.3 | 3.3 | 40.6 | 55.3 | 26.1 | 46.1 | 29.6 | 67.8 | 110.7 | 83.9 | 61.9 | 60.1 | 269.9 | 257.6 | 251.2 | 234 | 199.7 | 165.9 | 223.1 | 193.4 | 282.2 | 266.5
2438 | 2264 | -6.3 | 0 | 0 | 180.9 | 178.3 | 164.9 | 159.3 | 191.6 | 28 | 20.6 | 44 | 3.2 | 237.9 | 3 | 40.6 | 55.2 | 26 | 45.7 | 29.5 | 67.8 | 111.5 | 83.8 | 62 | 60.2 | 269.8 | 257.5 | 251.1 | 233.9 | 199.6 | 165.8 | 222.9 | 193.3 | 282 | 266.4
2439 | 2265 | -6.1 | 0 | 0 | 180.8 | 178.2 | 164.9 | 159.3 | 191.5 | 28 | 20.7 | 43.9 | 3.2 | 243 | 2.7 | 40.6 | 55.3 | 26 | 44.9 | 29.5 | 68 | 112 | 83.9 | 62 | 60.4 | 269.8 | 257.4 | 251 | 233.8 | 199.5 | 165.7 | 222.8 | 193.2 | 281.9 | 266.3
2440 | 2266 | -5.8 | 0 | 0 | 180.6 | 178.1 | 164.7 | 159.2 | 191.5 | 28 | 20.7 | 43.9 | 3.1 | 241 | 2.5 | 40.6 | 55.3 | 26 | 44.4 | 29.6 | 68.1 | 112 | 83.9 | 61.9 | 60.3 | 269.7 | 257.3 | 251 | 233.7 | 199.4 | 165.6 | 222.7 | 193.1 | 281.7 | 266.1
2441 | 2267 | -5.7 | 0 | 0 | 180.4 | 177.9 | 164.5 | 159.2 | 191.4 | 28 | 20.7 | 43.9 | 2.8 | 237.5 | 2.3 | 40.6 | 55.3 | 26 | 44.1 | 29.6 | 68.1 | 111.9 | 83.9 | 61.8 | 60.3 | 269.7 | 257.2 | 250.8 | 233.5 | 199.3 | 165.5 | 222.6 | 193 | 281.6 | 266
2442 | 2268 | -5.8 | 0 | 0 | 180.3 | 177.8 | 164.4 | 159.1 | 191.3 | 28 | 20.7 | 43.9 | 2.9 | 240.6 | 2.3 | 40.6 | 55.3 | 25.9 | 44.1 | 29.6 | 68.2 | 111.9 | 83.9 | 61.9 | 60.4 | 269.6 | 257.1 | 250.7 | 233.4 | 199.2 | 165.4 | 222.5 | 192.9 | 281.4 | 265.9
2443 | 2269 | -6 | 0 | 0 | 180.1 | 177.7 | 164.3 | 159.1 | 191.3 | 28 | 20.7 | 43.9 | 3.1 | 254.7 | 2.6 | 40.6 | 55.4 | 25.8 | 44.4 | 29.6 | 68.2 | 112.1 | 83.8 | 61.8 | 60.6 | 269.6 | 257 | 250.7 | 233.3 | 199.1 | 165.3 | 222.4 | 192.8 | 281.3 | 265.8
2444 | 2270 | -6 | 0 | 0 | 180 | 177.6 | 164.4 | 159.1 | 191.3 | 27.9 | 20.7 | 43.8 | 3.3 | 270.2 | 2.9 | 40.6 | 55.4 | 25.8 | 44.8 | 29.6 | 68.2 | 111.9 | 83.7 | 61.5 | 60.8 | 269.5 | 256.9 | 250.6 | 233.1 | 199 | 165.2 | 222.2 | 192.7 | 281.2 | 265.6
2445 | 2271 | -6.1 | 0 | 0 | 179.9 | 177.5 | 164.3 | 159.1 | 191.3 | 27.9 | 20.7 | 43.8 | 3.6 | 256 | 3.2 | 40.5 | 55.3 | 25.7 | 45 | 29.6 | 68.1 | 111.7 | 83.8 | 61.4 | 60.7 | 269.5 | 256.9 | 250.4 | 233 | 198.9 | 165.1 | 222.1 | 192.6 | 281 | 265.5
2446 | 2272 | -6.1 | 0 | 0 | 179.9 | 177.2 | 164.1 | 159.1 | 191.2 | 27.9 | 20.7 | 43.8 | 3.4 | 240 | 3.6 | 40.5 | 55.2 | 25.7 | 45.3 | 29.4 | 68 | 111.6 | 83.7 | 61.2 | 60.3 | 269.4 | 256.8 | 250.3 | 232.9 | 198.8 | 165 | 222 | 192.5 | 280.9 | 265.4
2447 | 2273 | -6.1 | 0 | 0 | 179.9 | 177 | 163.9 | 159.1 | 191 | 27.9 | 20.7 | 43.7 | 3.1 | 237.7 | 3.9 | 40.5 | 55.2 | 25.6 | 45 | 29.4 | 67.9 | 111.6 | 83.5 | 61 | 59.9 | 269.4 | 256.7 | 250.2 | 232.8 | 198.7 | 164.9 | 221.9 | 192.4 | 280.7 | 265.3
2448 | 2274 | -6.3 | 0 | 0 | 179.9 | 176.8 | 163.8 | 158.9 | 190.9 | 27.9 | 20.7 | 43.7 | 3.6 | 228.5 | 3.9 | 40.5 | 55.3 | 25.6 | 43.9 | 29.4 | 67.9 | 111.9 | 83.5 | 61.2 | 59.6 | 269.3 | 256.6 | 250.1 | 232.6 | 198.6 | 164.8 | 221.8 | 192.3 | 280.6 | 265.1
2449 | 2275 | -6.4 | 0 | 0 | 179.8 | 176.6 | 163.7 | 158.7 | 190.7 | 27.9 | 20.7 | 43.7 | 3.3 | 236.6 | 3.7 | 40.5 | 55.4 | 25.6 | 43.6 | 29.5 | 68 | 112.1 | 83.5 | 61.2 | 59.4 | 269.3 | 256.5 | 250 | 232.5 | 198.5 | 164.7 | 221.7 | 192.3 | 280.4 | 265
2450 | 2276 | -6 | 0 | 0 | 179.7 | 176.5 | 163.7 | 158.7 | 190.6 | 27.9 | 20.7 | 43.7 | 3.4 | 248.3 | 3.4 | 40.5 | 55.5 | 25.7 | 43.6 | 29.5 | 68 | 112 | 83.4 | 61.3 | 59.2 | 269.2 | 256.4 | 249.9 | 232.4 | 198.4 | 164.7 | 221.6 | 192.1 | 280.3 | 264.9
2451 | 2277 | -6 | 0 | 0 | 179.6 | 176.5 | 163.5 | 158.7 | 190.6 | 27.9 | 20.7 | 43.7 | 3.5 | 239.7 | 3.1 | 40.5 | 55.3 | 25.7 | 43.5 | 29.5 | 67.9 | 111.9 | 83.2 | 61.5 | 59.5 | 269.2 | 256.3 | 249.8 | 232.3 | 198.4 | 164.6 | 221.5 | 192 | 280.2 | 264.8
2452 | 2278 | -6.2 | 0 | 0 | 179.5 | 176.5 | 163.4 | 158.6 | 190.6 | 27.9 | 20.7 | 43.6 | 3.7 | 214.2 | 2.7 | 40.5 | 55.2 | 25.6 | 43.2 | 29.6 | 67.6 | 111.4 | 83.2 | 61.6 | 59.8 | 269.2 | 256.2 | 249.7 | 232.1 | 198.3 | 164.6 | 221.4 | 192 | 280 | 264.6
2453 | 2279 | -6.4 | 0 | 0 | 179.4 | 176.4 | 163.3 | 158.6 | 190.6 | 27.9 | 20.7 | 43.6 | 3.3 | 196 | 2.6 | 40.5 | 55.1 | 25.6 | 43.8 | 29.5 | 67.3 | 111.2 | 83.2 | 61.7 | 60 | 269.1 | 256.1 | 249.6 | 232 | 198.2 | 164.5 | 221.3 | 191.9 | 279.9 | 264.5
2454 | 2280 | -6.4 | 0 | 0 | 179.3 | 176.2 | 163.2 | 158.5 | 190.6 | 27.9 | 20.7 | 43.6 | 3 | 190.7 | 2.4 | 40.5 | 55.1 | 25.6 | 43 | 29.5 | 67.1 | 111.2 | 83.1 | 61.7 | 59.9 | 269.1 | 256 | 249.5 | 231.9 | 198.2 | 164.5 | 221.2 | 191.8 | 279.7 | 264.4
2455 | 2281 | -6.3 | 0 | 0 | 179.1 | 176 | 163.2 | 158.5 | 190.5 | 27.9 | 20.7 | 43.6 | 3.5 | 190.8 | 2.2 | 40.5 | 55.1 | 25.6 | 42.7 | 29.4 | 66.9 | 111.2 | 83 | 61.7 | 59.8 | 269 | 255.9 | 249.4 | 231.8 | 198.1 | 164.5 | 221.1 | 191.7 | 279.6 | 264.3
2456 | 2282 | -6 | 0 | 0 | 179.1 | 175.8 | 163.3 | 158.5 | 190.4 | 27.9 | 20.7 | 43.6 | 3.2 | 203.6 | 2.1 | 40.5 | 55.1 | 25.5 | 42.6 | 29.4 | 66.9 | 111.6 | 82.9 | 61.8 | 59.9 | 269 | 255.9 | 249.3 | 231.6 | 198 | 164.4 | 220.9 | 191.6 | 279.4 | 264.1
2457 | 2283 | -6.2 | 0 | 0 | 179 | 175.7 | 163.3 | 158.4 | 190.3 | 27.9 | 20.7 | 43.7 | 3.5 | 228.3 | 2.1 | 40.5 | 55 | 25.4 | 43 | 29.4 | 66.7 | 111.7 | 83.1 | 61.8 | 60.1 | 268.9 | 255.8 | 249.2 | 231.5 | 197.9 | 164.3 | 220.8 | 191.5 | 279.3 | 264
2458 | 2284 | -6.2 | 0 | 0 | 178.8 | 175.4 | 163.3 | 158.4 | 190.2 | 27.9 | 20.7 | 43.7 | 3.2 | 231.9 | 2.1 | 40.4 | 54.9 | 25.4 | 42.7 | 29.3 | 66.4 | 111.5 | 83.2 | 61.7 | 60.2 | 268.9 | 255.7 | 249.1 | 231.4 | 197.8 | 164.2 | 220.7 | 191.4 | 279.1 | 263.9
2459 | 2285 | -6.1 | 0 | 0 | 178.6 | 175.3 | 163.2 | 158.3 | 190.2 | 27.9 | 20.7 | 43.7 | 3.2 | 198.5 | 2.7 | 40.4 | 54.9 | 25.4 | 42.5 | 29.2 | 66.1 | 111.4 | 83.1 | 61.6 | 60.2 | 268.8 | 255.6 | 249 | 231.3 | 197.7 | 164.1 | 220.6 | 191.3 | 279 | 263.8
2460 | 2286 | -6.1 | 0 | 0 | 178.6 | 175.1 | 163.1 | 158.2 | 190.1 | 27.9 | 20.7 | 43.7 | 3.1 | 194.4 | 3.6 | 40.4 | 54.9 | 25.4 | 43 | 29.2 | 66 | 111.5 | 83 | 61.6 | 60.2 | 268.8 | 255.5 | 248.9 | 231.1 | 197.6 | 164 | 220.5 | 191.2 | 278.8 | 263.6
2461 | 2287 | -6.1 | 0 | 0 | 178.6 | 175 | 162.8 | 158.2 | 190.1 | 27.8 | 20.7 | 43.7 | 3.2 | 211.1 | 3.8 | 40.4 | 54.9 | 25.4 | 43.1 | 29.3 | 66.2 | 111.7 | 83 | 61.6 | 60.3 | 268.7 | 255.4 | 248.8 | 231 | 197.5 | 163.9 | 220.3 | 191.1 | 278.7 | 263.5
2462 | 2288 | -5.9 | 0 | 0 | 178.5 | 175 | 162.6 | 158.1 | 189.9 | 27.8 | 20.7 | 43.7 | 3 | 216.9 | 3.5 | 40.4 | 54.9 | 25.4 | 42.4 | 29.4 | 66.3 | 111.8 | 83 | 61.6 | 60.3 | 268.7 | 255.3 | 248.7 | 230.9 | 197.4 | 163.8 | 220.2 | 191 | 278.5 | 263.4
2463 | 2289 | -5.8 | 0 | 0 | 178.3 | 175.1 | 162.5 | 158 | 189.8 | 27.8 | 20.7 | 43.7 | 3 | 216.1 | 3.7 | 40.3 | 55 | 25.4 | 42.6 | 29.4 | 66.4 | 111.9 | 83.1 | 61.6 | 60.2 | 268.6 | 255.2 | 248.6 | 230.8 | 197.3 | 163.7 | 220.1 | 190.9 | 278.4 | 263.3
2464 | 2290 | -5.9 | 0 | 0 | 178.2 | 175 | 162.5 | 157.9 | 189.7 | 27.8 | 20.7 | 43.7 | 3.4 | 205.6 | 4.6 | 40.3 | 55 | 25.4 | 43 | 29.5 | 66.7 | 112 | 83 | 61.6 | 60.1 | 268.6 | 255.1 | 248.5 | 230.6 | 197.3 | 163.6 | 220 | 190.8 | 278.3 | 263.2
2465 | 2291 | -5.9 | 0 | 0 | 178 | 174.9 | 162.4 | 157.7 | 189.6 | 27.7 | 20.7 | 43.7 | 3.1 | 210 | 5 | 40.3 | 55 | 25.5 | 43.2 | 29.5 | 66.9 | 112.1 | 82.9 | 61.6 | 60.1 | 268.6 | 255 | 248.4 | 230.5 | 197.2 | 163.5 | 219.9 | 190.7 | 278.1 | 263
2466 | 2292 | -6.1 | 0 | 0 | 177.9 | 174.7 | 162.2 | 157.7 | 189.5 | 27.7 | 20.7 | 43.7 | 3 | 242.8 | 4.9 | 40.3 | 55.1 | 25.6 | 43.3 | 29.5 | 67 | 112 | 82.9 | 61.5 | 60.2 | 268.5 | 255 | 248.3 | 230.4 | 197.1 | 163.4 | 219.8 | 190.6 | 277.9 | 262.9
2467 | 2293 | -6.2 | 0 | 0 | 177.9 | 174.6 | 162.2 | 157.5 | 189.4 | 27.7 | 20.7 | 43.6 | 3.3 | 217.3 | 4.1 | 40.3 | 55.3 | 25.6 | 44 | 29.5 | 67.1 | 111.8 | 82.9 | 61.6 | 60.2 | 268.5 | 254.9 | 248.2 | 230.3 | 197 | 163.3 | 219.7 | 190.5 | 277.8 | 262.8
2468 | 2294 | -6.3 | 0 | 0 | 177.7 | 174.7 | 162.2 | 157.4 | 189.2 | 27.7 | 20.7 | 43.6 | 3.5 | 186 | 4.2 | 40.3 | 55.2 | 25.6 | 44.5 | 29.5 | 67.3 | 112 | 82.9 | 61.6 | 60.2 | 268.4 | 254.8 | 248.1 | 230.1 | 197 | 163.3 | 219.6 | 190.4 | 277.7 | 262.6
2469 | 2295 | -6.3 | 0 | 0 | 177.6 | 174.7 | 162.1 | 157.3 | 189.1 | 27.7 | 20.7 | 43.5 | 3.6 | 187 | 4.2 | 40.3 | 55.1 | 25.6 | 44.9 | 29.4 | 67.3 | 112.2 | 82.8 | 61.6 | 60.1 | 268.4 | 254.7 | 248 | 230 | 196.9 | 163.2 | 219.4 | 190.3 | 277.5 | 262.5
2470 | 2296 | -6.3 | 0 | 0 | 177.5 | 174.8 | 162 | 157.1 | 189 | 27.6 | 20.7 | 43.5 | 3.6 | 195.9 | 3.7 | 40.2 | 55.1 | 25.7 | 44.4 | 29.4 | 67.3 | 112.2 | 82.7 | 61.5 | 60.1 | 268.3 | 254.6 | 247.9 | 229.9 | 196.8 | 163.2 | 219.3 | 190.2 | 277.4 | 262.4
2471 | 2297 | -6.3 | 0 | 0 | 177.4 | 174.7 | 161.9 | 156.9 | 189 | 27.6 | 20.7 | 43.4 | 3.6 | 205 | 3.7 | 40.2 | 55 | 25.7 | 43.9 | 29.4 | 67.4 | 112.2 | 82.6 | 61.5 | 59.9 | 268.3 | 254.5 | 247.8 | 229.8 | 196.6 | 163.1 | 219.2 | 190.1 | 277.2 | 262.3
2472 | 2298 | -6.4 | 0 | 0 | 177.3 | 174.7 | 161.8 | 156.7 | 188.9 | 27.5 | 20.7 | 43.4 | 3.8 | 205.9 | 4.3 | 40.2 | 54.8 | 25.7 | 43.8 | 29.4 | 67.5 | 112.1 | 82.5 | 61.4 | 59.8 | 268.2 | 254.4 | 247.7 | 229.6 | 196.5 | 163 | 219.1 | 190 | 277.1 | 262.2
2473 | 2299 | -6.5 | 0 | 0 | 177.2 | 174.6 | 161.8 | 156.7 | 188.9 | 27.5 | 20.7 | 43.3 | 3.8 | 195.5 | 6.3 | 40.2 | 54.8 | 25.7 | 43.7 | 29.4 | 67.6 | 112 | 82.4 | 61.5 | 59.8 | 268.1 | 254.3 | 247.6 | 229.5 | 196.5 | 163 | 219 | 189.9 | 276.9 | 262
2474 | 2300 | -6.3 | 0 | 0 | 177.2 | 174.5 | 161.7 | 156.6 | 188.8 | 27.5 | 20.7 | 43.3 | 3.6 | 183.8 | 7.8 | 40.2 | 54.7 | 25.7 | 43.8 | 29.4 | 67.5 | 112.1 | 82.3 | 61.6 | 59.8 | 268.1 | 254.2 | 247.5 | 229.4 | 196.4 | 162.9 | 218.9 | 189.9 | 276.8 | 261.9
2475 | 2301 | -6.3 | 0 | 0 | 177.2 | 174.3 | 161.6 | 156.6 | 188.8 | 27.5 | 20.7 | 43.3 | 3.4 | 182.3 | 7.7 | 40.2 | 54.7 | 25.7 | 44 | 29.3 | 67.2 | 112.1 | 82.3 | 61.5 | 59.7 | 268 | 254.1 | 247.4 | 229.3 | 196.3 | 162.8 | 218.8 | 189.8 | 276.7 | 261.8
2476 | 2302 | -6.2 | 0 | 0 | 177.1 | 174 | 161.5 | 156.6 | 188.6 | 27.5 | 20.7 | 43.3 | 3.2 | 179.1 | 6.8 | 40.2 | 54.6 | 25.7 | 44 | 29.3 | 67.2 | 112.5 | 82.3 | 61.5 | 59.8 | 268 | 254.1 | 247.3 | 229.2 | 196.2 | 162.7 | 218.7 | 189.7 | 276.5 | 261.7
2477 | 2303 | -6.2 | 0 | 0 | 177 | 173.7 | 161.4 | 156.6 | 188.5 | 27.5 | 20.7 | 43.2 | 3.2 | 219.8 | 5.8 | 40.2 | 54.6 | 25.6 | 43.4 | 29.3 | 67.2 | 112.7 | 82.3 | 61.5 | 59.9 | 268 | 254 | 247.2 | 229 | 196.1 | 162.7 | 218.6 | 189.6 | 276.4 | 261.6
2478 | 2304 | -6.2 | 0 | 0 | 177 | 173.5 | 161.3 | 156.5 | 188.5 | 27.5 | 20.7 | 43.2 | 3 | 235.1 | 5.4 | 40.1 | 54.5 | 25.6 | 43 | 29.3 | 67.2 | 112.7 | 82.3 | 61.4 | 60.1 | 267.9 | 253.9 | 247.1 | 228.9 | 196 | 162.6 | 218.4 | 189.5 | 276.2 | 261.4
2479 | 2305 | -6.2 | 0 | 0 | 176.9 | 173.6 | 161.3 | 156.4 | 188.4 | 27.5 | 20.7 | 43.1 | 3.4 | 210.4 | 5.6 | 40.1 | 54.5 | 25.6 | 43.5 | 29.3 | 66.9 | 112.3 | 82.2 | 61.3 | 60.1 | 267.9 | 253.8 | 247 | 228.8 | 195.9 | 162.5 | 218.3 | 189.4 | 276.1 | 261.3
2480 | 2306 | -6.2 | 0 | 0 | 176.8 | 173.6 | 161.3 | 156.3 | 188.4 | 27.5 | 20.7 | 43.1 | 3.4 | 228.5 | 5.6 | 40.1 | 54.4 | 25.6 | 43.7 | 29.3 | 66.6 | 112.2 | 82.1 | 61.2 | 60 | 267.8 | 253.7 | 246.9 | 228.7 | 195.8 | 162.4 | 218.2 | 189.3 | 276 | 261.2
2481 | 2307 | -6.3 | 0 | 0 | 176.7 | 173.5 | 161.1 | 156.3 | 188.3 | 27.5 | 20.7 | 43.1 | 3.2 | 220.6 | 6.6 | 40.1 | 54.5 | 25.5 | 44 | 29.2 | 66.5 | 112.3 | 82 | 61.2 | 59.8 | 267.8 | 253.6 | 246.8 | 228.6 | 195.7 | 162.3 | 218.1 | 189.2 | 275.8 | 261.1
2482 | 2308 | -6.3 | 0 | 0 | 176.7 | 173.4 | 161 | 156.2 | 188.2 | 27.5 | 20.7 | 43.1 | 3.2 | 218.3 | 7.2 | 40 | 54.5 | 25.5 | 44.1 | 29.1 | 66.6 | 112.3 | 81.9 | 61.2 | 59.4 | 267.7 | 253.5 | 246.7 | 228.4 | 195.7 | 162.2 | 218 | 189.1 | 275.7 | 261
2483 | 2309 | -6 | 0 | 0 | 176.6 | 173.2 | 160.8 | 156.1 | 188.1 | 27.5 | 20.7 | 43.1 | 3.4 | 235.7 | 6.3 | 40 | 54.6 | 25.4 | 44.5 | 29.1 | 66.6 | 112.4 | 81.8 | 61.3 | 59.3 | 267.7 | 253.4 | 246.6 | 228.3 | 195.6 | 162.1 | 217.9 | 189 | 275.5 | 260.8
2484 | 2310 | -6 | 0 | 0 | 176.5 | 173.2 | 160.7 | 156 | 188 | 27.5 | 20.7 | 43 | 3.2 | 213.3 | 6.3 | 40 | 54.6 | 25.4 | 44.8 | 29.1 | 66.6 | 112.7 | 81.8 | 61.3 | 59.4 | 267.6 | 253.3 | 246.5 | 228.2 | 195.5 | 162 | 217.8 | 188.9 | 275.4 | 260.7
2485 | 2311 | -6.2 | 0 | 0 | 176.4 | 173.1 | 160.6 | 155.8 | 187.9 | 27.5 | 20.7 | 43 | 3.1 | 210.6 | 6.7 | 40 | 54.7 | 25.4 | 45.1 | 29 | 66.5 | 112.8 | 81.7 | 61.3 | 59.3 | 267.6 | 253.3 | 246.4 | 228.1 | 195.4 | 161.9 | 217.7 | 188.8 | 275.2 | 260.6
2486 | 2312 | -6.1 | 0 | 0 | 176.4 | 173 | 160.6 | 155.7 | 187.8 | 27.5 | 20.7 | 42.9 | 3.3 | 223.8 | 7.1 | 40 | 54.6 | 25.3 | 45.2 | 28.9 | 66.7 | 113.1 | 81.7 | 61.2 | 59.2 | 267.5 | 253.2 | 246.3 | 228 | 195.3 | 161.9 | 217.5 | 188.7 | 275.1 | 260.5
2487 | 2313 | -6.3 | 0 | 0 | 176.2 | 172.9 | 160.5 | 155.7 | 187.8 | 27.5 | 20.7 | 42.9 | 3 | 201.9 | 7.6 | 40 | 54.7 | 25.3 | 45.1 | 28.9 | 66.8 | 113.2 | 81.7 | 61.1 | 59.3 | 267.5 | 253.1 | 246.3 | 227.8 | 195.2 | 161.8 | 217.4 | 188.6 | 274.9 | 260.3
2488 | 2314 | -6.4 | 0 | 0 | 175.9 | 172.7 | 160.3 | 155.6 | 187.7 | 27.5 | 20.7 | 42.8 | 3 | 209.2 | 7.8 | 40 | 54.7 | 25.3 | 44.9 | 28.9 | 66.9 | 112.9 | 81.7 | 61.1 | 59.4 | 267.5 | 253 | 246.2 | 227.7 | 195.1 | 161.7 | 217.3 | 188.6 | 274.8 | 260.2
2489 | 2315 | -6.2 | 0 | 0 | 175.8 | 172.6 | 160.1 | 155.5 | 187.7 | 27.5 | 20.7 | 42.8 | 2.8 | 200 | 8.2 | 39.9 | 54.8 | 25.3 | 44.9 | 28.9 | 66.8 | 113.2 | 81.6 | 61.1 | 59.5 | 267.4 | 252.9 | 246.1 | 227.6 | 195 | 161.7 | 217.2 | 188.5 | 274.7 | 260.1
2490 | 2316 | -6 | 0 | 0 | 175.7 | 172.6 | 160 | 155.5 | 187.6 | 27.5 | 20.7 | 42.8 | 3.1 | 208.1 | 7.8 | 39.9 | 54.7 | 25.3 | 44.9 | 29 | 67 | 113.6 | 81.6 | 61.2 | 59.6 | 267.3 | 252.8 | 246 | 227.5 | 194.9 | 161.6 | 217.1 | 188.3 | 274.5 | 260
2491 | 2317 | -6.1 | 0 | 0 | 175.7 | 172.5 | 160 | 155.4 | 187.5 | 27.6 | 20.7 | 42.8 | 3.6 | 207.7 | 7.3 | 39.9 | 54.7 | 25.3 | 44.8 | 29 | 67.1 | 113.3 | 81.5 | 61.1 | 59.7 | 267.3 | 252.7 | 245.9 | 227.4 | 194.8 | 161.5 | 217 | 188.3 | 274.4 | 259.9
2492.1 | 2318.1 | -6.1 | 0 | 0 | 175.6 | 172.5 | 159.9 | 155.3 | 187.4 | 27.5 | 20.7 | 42.8 | 3.1 | 244.4 | 5.9 | 39.8 | 54.6 | 25.3 | 44.2 | 29 | 67 | 113 | 81.5 | 61.1 | 59.5 | 267.3 | 252.6 | 245.8 | 227.2 | 194.7 | 161.4 | 216.9 | 188.2 | 274.2 | 259.8
2493.1 | 2319.1 | -6.2 | 0 | 0 | 175.6 | 172.5 | 159.9 | 155.4 | 187.3 | 27.5 | 20.7 | 42.7 | 2.9 | 280.9 | 4.8 | 39.8 | 54.7 | 25.3 | 43.3 | 29 | 66.9 | 112.9 | 81.4 | 61.1 | 59.4 | 267.2 | 252.5 | 245.7 | 227.1 | 194.7 | 161.4 | 216.7 | 188.1 | 274.1 | 259.6
2494.1 | 2320.1 | -6.3 | 0 | 0 | 175.6 | 172.4 | 159.8 | 155.3 | 187.2 | 27.5 | 20.7 | 42.7 | 3 | 278.6 | 3.9 | 39.8 | 54.6 | 25.3 | 42.9 | 29 | 66.6 | 112.7 | 81.3 | 61 | 59.4 | 267.2 | 252.5 | 245.6 | 227 | 194.6 | 161.3 | 216.6 | 188 | 274 | 259.5
2495.1 | 2321.1 | -6.2 | 0 | 0 | 175.5 | 172.3 | 159.8 | 155 | 187.1 | 27.6 | 20.7 | 42.7 | 2.9 | 228.8 | 3.9 | 39.8 | 54.5 | 25.3 | 42.7 | 28.9 | 66.7 | 112.5 | 81.2 | 61 | 59.4 | 267.1 | 252.4 | 245.5 | 226.9 | 194.5 | 161.2 | 216.5 | 187.9 | 273.8 | 259.4
2496.1 | 2322.1 | -6.3 | 0 | 0 | 175.4 | 172.3 | 159.7 | 154.8 | 186.9 | 27.6 | 20.7 | 42.7 | 3 | 224.1 | 4.3 | 39.8 | 54.4 | 25.3 | 43.3 | 28.9 | 66.7 | 112.8 | 81.1 | 61.1 | 59.5 | 267.1 | 252.3 | 245.4 | 226.7 | 194.4 | 161.1 | 216.4 | 187.8 | 273.7 | 259.3
2497.1 | 2323.1 | -6.2 | 0 | 0 | 175.2 | 172.3 | 159.6 | 154.6 | 186.8 | 27.6 | 20.7 | 42.7 | 3.1 | 247.5 | 4.4 | 39.7 | 54.2 | 25.3 | 43.6 | 28.9 | 66.8 | 112.7 | 81.1 | 61.1 | 59.6 | 267 | 252.2 | 245.3 | 226.6 | 194.3 | 161 | 216.3 | 187.7 | 273.5 | 259.2
2498.1 | 2324.1 | -6.1 | 0 | 0 | 175.1 | 172.3 | 159.6 | 154.5 | 186.7 | 27.6 | 20.7 | 42.6 | 3 | 224.5 | 3.9 | 39.7 | 54.1 | 25.3 | 44 | 28.9 | 66.5 | 112.6 | 81.1 | 61.1 | 59.6 | 267 | 252.1 | 245.2 | 226.5 | 194.3 | 160.9 | 216.2 | 187.6 | 273.4 | 259
2499.1 | 2325.1 | -6 | 0 | 0 | 175.2 | 172.1 | 159.7 | 154.5 | 186.6 | 27.6 | 20.7 | 42.6 | 3.3 | 210 | 3.5 | 39.7 | 54 | 25.2 | 44 | 29 | 66.4 | 112.4 | 81.1 | 61.1 | 59.6 | 266.9 | 252 | 245.1 | 226.4 | 194.2 | 160.9 | 216.1 | 187.5 | 273.3 | 258.9
2500.1 | 2326.1 | -6 | 0 | 0 | 175.2 | 172 | 159.6 | 154.5 | 186.6 | 27.6 | 20.7 | 42.6 | 3.4 | 227.8 | 3.3 | 39.7 | 54 | 25.2 | 43.6 | 29 | 66.4 | 112.5 | 81 | 61.1 | 59.5 | 266.8 | 251.9 | 245 | 226.3 | 194.1 | 160.8 | 216 | 187.4 | 273.1 | 258.8
2501.1 | 2327.1 | -6 | 0 | 0 | 175.1 | 171.8 | 159.5 | 154.4 | 186.5 | 27.6 | 20.7 | 42.7 | 3.3 | 232 | 3.7 | 39.7 | 54 | 25.2 | 43.4 | 29 | 66.4 | 112.6 | 81 | 61 | 59.5 | 266.8 | 251.8 | 244.9 | 226.1 | 194 | 160.8 | 215.9 | 187.3 | 273 | 258.7
2502.1 | 2328.1 | -6 | 0 | 0 | 175 | 171.7 | 159.4 | 154.3 | 186.4 | 27.6 | 20.7 | 42.7 | 3.2 | 212 | 3.6 | 39.7 | 53.9 | 25.2 | 43.5 | 28.9 | 65.8 | 112.5 | 81 | 60.9 | 59.4 | 266.7 | 251.7 | 244.8 | 226 | 193.9 | 160.7 | 215.7 | 187.2 | 272.9 | 258.6
2503.1 | 2329.1 | -6.1 | 0 | 0 | 174.7 | 171.7 | 159.3 | 154.2 | 186.3 | 27.6 | 20.7 | 42.6 | 3.5 | 197.9 | 3.3 | 39.7 | 53.8 | 25.2 | 43.4 | 28.9 | 65.5 | 112.4 | 81 | 60.6 | 59.4 | 266.7 | 251.7 | 244.7 | 225.9 | 193.8 | 160.6 | 215.7 | 187.2 | 272.7 | 258.4
2504.1 | 2330.1 | -6.2 | 0 | 0 | 174.5 | 171.4 | 159.3 | 154.2 | 186.3 | 27.6 | 20.7 | 42.6 | 3.5 | 195.1 | 2.9 | 39.7 | 53.8 | 25.2 | 43.2 | 28.9 | 65.5 | 112.5 | 81 | 60.6 | 59.6 | 266.6 | 251.6 | 244.6 | 225.8 | 193.7 | 160.6 | 215.6 | 187.1 | 272.6 | 258.3
2505.1 | 2331.1 | -6.2 | 0 | 0 | 174.5 | 171.2 | 159.2 | 154.1 | 186.2 | 27.6 | 20.7 | 42.6 | 3.2 | 195.8 | 3.2 | 39.7 | 53.9 | 25.2 | 43.7 | 28.8 | 65.2 | 112.3 | 81 | 60.6 | 59.6 | 266.6 | 251.5 | 244.5 | 225.7 | 193.6 | 160.5 | 215.5 | 187 | 272.5 | 258.2
2506.1 | 2332.1 | -6.3 | 0 | 0 | 174.4 | 171.1 | 159.2 | 154.1 | 186 | 27.5 | 20.7 | 42.5 | 3.6 | 191.9 | 3.4 | 39.7 | 54 | 25.2 | 43.1 | 28.8 | 65.1 | 112.3 | 81 | 60.7 | 59.6 | 266.5 | 251.4 | 244.4 | 225.6 | 193.5 | 160.4 | 215.4 | 186.9 | 272.4 | 258.1
2507.1 | 2333.1 | -6.3 | 0 | 0 | 174.4 | 171 | 159 | 154 | 185.9 | 27.5 | 20.7 | 42.5 | 3.5 | 198.9 | 2.9 | 39.6 | 54.1 | 25.2 | 43.2 | 28.9 | 65.2 | 112.5 | 81 | 60.6 | 59.5 | 266.5 | 251.3 | 244.3 | 225.4 | 193.4 | 160.3 | 215.2 | 186.8 | 272.2 | 258
2508.1 | 2334.1 | -6.2 | 0 | 0 | 174.3 | 171 | 158.9 | 153.9 | 185.8 | 27.5 | 20.7 | 42.5 | 3.6 | 222.8 | 3 | 39.6 | 54 | 25.2 | 43.5 | 28.9 | 65.4 | 112.6 | 80.9 | 60.4 | 59.5 | 266.5 | 251.2 | 244.3 | 225.3 | 193.3 | 160.2 | 215.1 | 186.7 | 272.1 | 257.8
2509.1 | 2335.1 | -6.4 | 0 | 0 | 174.4 | 171 | 158.8 | 153.8 | 185.8 | 27.5 | 20.7 | 42.6 | 3.3 | 230 | 3.4 | 39.6 | 54.1 | 25.2 | 43.4 | 29 | 65.5 | 112.8 | 80.9 | 60.4 | 59.4 | 266.4 | 251.1 | 244.2 | 225.2 | 193.2 | 160.1 | 215 | 186.6 | 272 | 257.7
2510.1 | 2336.1 | -6.4 | 0 | 0 | 174.3 | 171 | 158.8 | 153.8 | 185.7 | 27.5 | 20.7 | 42.6 | 3.3 | 216.3 | 3.5 | 39.6 | 54.1 | 25.2 | 43.4 | 29 | 65.6 | 113.1 | 80.9 | 60.5 | 59.3 | 266.3 | 251 | 244.1 | 225.1 | 193.1 | 160 | 214.9 | 186.5 | 271.8 | 257.6
2511.1 | 2337.1 | -6.4 | 0 | 0 | 174.2 | 170.9 | 158.8 | 153.6 | 185.6 | 27.5 | 20.7 | 42.6 | 3.8 | 177.9 | 3.4 | 39.6 | 53.9 | 25.2 | 43.6 | 29 | 65.8 | 113.3 | 80.8 | 60.5 | 59.1 | 266.3 | 251 | 244 | 225 | 193 | 159.9 | 214.7 | 186.4 | 271.7 | 257.5
2512.1 | 2338.1 | -6.1 | 0 | 0 | 174.1 | 170.8 | 158.7 | 153.4 | 185.6 | 27.5 | 20.7 | 42.6 | 3.4 | 173.6 | 3.6 | 39.6 | 53.7 | 25.2 | 43.2 | 29 | 66 | 113.4 | 80.6 | 60.5 | 59 | 266.2 | 250.9 | 243.9 | 224.8 | 192.9 | 159.8 | 214.6 | 186.3 | 271.6 | 257.4
2513.1 | 2339.1 | -6.2 | 0 | 0 | 174 | 170.7 | 158.5 | 153.3 | 185.5 | 27.5 | 20.7 | 42.6 | 3.2 | 212.9 | 4.7 | 39.6 | 53.6 | 25.1 | 43.2 | 28.8 | 66.2 | 113.5 | 80.6 | 60.6 | 59.2 | 266.2 | 250.8 | 243.8 | 224.7 | 192.8 | 159.7 | 214.5 | 186.2 | 271.4 | 257.3
2514.1 | 2340.1 | -6.3 | 0 | 0 | 173.8 | 170.5 | 158.5 | 153.3 | 185.4 | 27.5 | 20.7 | 42.5 | 3.6 | 222 | 5.1 | 39.6 | 53.5 | 25 | 43 | 28.7 | 66.3 | 113.6 | 80.7 | 60.8 | 59.3 | 266.2 | 250.7 | 243.7 | 224.6 | 192.7 | 159.6 | 214.4 | 186.2 | 271.3 | 257.1
2515.1 | 2341.1 | -6.1 | 0 | 0 | 173.8 | 170.4 | 158.4 | 153.3 | 185.2 | 27.4 | 20.7 | 42.5 | 3.6 | 212.5 | 5.3 | 39.5 | 53.5 | 25 | 43 | 28.6 | 66.4 | 113.5 | 80.5 | 60.8 | 59.3 | 266.1 | 250.6 | 243.6 | 224.5 | 192.7 | 159.5 | 214.4 | 186.1 | 271.2 | 257
2516.1 | 2342.1 | -6.2 | 0 | 0 | 173.7 | 170.4 | 158.3 | 153.3 | 185.1 | 27.4 | 20.8 | 42.6 | 3.5 | 196.2 | 5.5 | 39.5 | 53.6 | 25 | 42.8 | 28.6 | 66.5 | 113.6 | 80.4 | 60.8 | 59.4 | 266.1 | 250.5 | 243.5 | 224.4 | 192.6 | 159.5 | 214.2 | 186 | 271 | 256.9
2517.1 | 2343.1 | -6.2 | 0 | 0 | 173.5 | 170.3 | 158.3 | 153.3 | 185 | 27.4 | 20.8 | 42.6 | 3 | 207 | 5.7 | 39.5 | 53.4 | 25 | 43.1 | 28.6 | 66.1 | 113.3 | 80.3 | 60.8 | 59.5 | 266 | 250.4 | 243.4 | 224.2 | 192.5 | 159.4 | 214.1 | 185.9 | 270.9 | 256.8
2518.1 | 2344.1 | -6.3 | 0 | 0 | 173.4 | 170.2 | 158.2 | 153.3 | 185 | 27.4 | 20.8 | 42.6 | 3 | 215 | 5 | 39.5 | 53.3 | 24.9 | 43.1 | 28.6 | 65.6 | 112.9 | 80.2 | 60.7 | 59.4 | 266 | 250.3 | 243.3 | 224.1 | 192.4 | 159.4 | 214 | 185.8 | 270.7 | 256.7
2519.1 | 2345.1 | -6.4 | 0 | 0 | 173.3 | 170 | 158 | 153.2 | 184.9 | 27.4 | 20.8 | 42.5 | 3.3 | 218.3 | 4.7 | 39.5 | 53.3 | 25 | 43.1 | 28.6 | 65.6 | 112.6 | 80.2 | 60.5 | 59.4 | 265.9 | 250.3 | 243.2 | 224 | 192.3 | 159.3 | 213.9 | 185.7 | 270.6 | 256.6
2520.1 | 2346.1 | -6.4 | 0 | 0 | 173.3 | 169.9 | 158 | 153.1 | 184.8 | 27.3 | 20.8 | 42.5 | 3.2 | 213.9 | 4.4 | 39.5 | 53.2 | 24.9 | 42.4 | 28.6 | 65.3 | 112.5 | 80.1 | 60.5 | 59.5 | 265.9 | 250.2 | 243.1 | 223.9 | 192.3 | 159.2 | 213.8 | 185.7 | 270.5 | 256.4
2521.1 | 2347.1 | -6.4 | 0 | 0 | 173.2 | 169.8 | 157.9 | 153.2 | 184.7 | 27.3 | 20.8 | 42.5 | 3.5 | 201.9 | 3.6 | 39.5 | 53.3 | 24.9 | 42.2 | 28.5 | 65.3 | 112.4 | 80.1 | 60.4 | 59.4 | 265.8 | 250.1 | 243 | 223.8 | 192.2 | 159.2 | 213.7 | 185.5 | 270.3 | 256.3
2522.1 | 2348.1 | -6.3 | 0 | 0 | 173 | 169.7 | 157.8 | 153.2 | 184.7 | 27.3 | 20.8 | 42.4 | 3.6 | 205 | 3.1 | 39.5 | 53.3 | 25 | 42.5 | 28.5 | 65.1 | 112.5 | 80.1 | 60.4 | 59.3 | 265.8 | 250 | 242.9 | 223.6 | 192.1 | 159.2 | 213.6 | 185.5 | 270.2 | 256.2
2523.1 | 2349.1 | -6.1 | 0 | 0 | 172.7 | 169.5 | 157.7 | 153.2 | 184.6 | 27.3 | 20.8 | 42.4 | 3.7 | 218.4 | 3 | 39.5 | 53.3 | 25 | 43 | 28.4 | 65.1 | 112.5 | 80 | 60.5 | 59.2 | 265.7 | 249.9 | 242.8 | 223.5 | 192 | 159.1 | 213.5 | 185.4 | 270 | 256.1
2524.1 | 2350.1 | -6 | 0 | 0 | 172.5 | 169.3 | 157.7 | 153.2 | 184.6 | 27.3 | 20.8 | 42.3 | 3.2 | 227.1 | 2.9 | 39.5 | 53.3 | 25 | 43.3 | 28.5 | 65 | 112.6 | 79.9 | 60.5 | 59.1 | 265.7 | 249.8 | 242.8 | 223.4 | 191.9 | 159 | 213.4 | 185.3 | 269.9 | 256
2525.1 | 2351.1 | -6.2 | 0 | 0 | 172.4 | 169.2 | 157.6 | 153.2 | 184.5 | 27.2 | 20.8 | 42.3 | 3.2 | 205.5 | 3.3 | 39.5 | 53.2 | 25 | 43.5 | 28.5 | 64.9 | 112.6 | 79.9 | 60.4 | 59 | 265.6 | 249.7 | 242.7 | 223.3 | 191.8 | 158.9 | 213.3 | 185.2 | 269.7 | 255.9
2526.1 | 2352.1 | -6.1 | 0 | 0 | 172.4 | 169.2 | 157.5 | 153.1 | 184.5 | 27.2 | 20.8 | 42.3 | 3.1 | 200.4 | 4.3 | 39.4 | 53.1 | 25 | 43.6 | 28.4 | 64.9 | 112.8 | 79.8 | 60.4 | 59 | 265.6 | 249.6 | 242.6 | 223.2 | 191.7 | 158.8 | 213.2 | 185.1 | 269.6 | 255.8
2527.1 | 2353.1 | -6.1 | 0 | 0 | 172.3 | 169.1 | 157.3 | 152.9 | 184.4 | 27.1 | 20.8 | 42.3 | 3.1 | 205.1 | 5.3 | 39.4 | 53 | 25.1 | 43.8 | 28.4 | 65 | 113 | 79.7 | 60.4 | 59.2 | 265.5 | 249.6 | 242.5 | 223.1 | 191.6 | 158.7 | 213.1 | 185 | 269.4 | 255.6
2528.1 | 2354.1 | -6.2 | 0 | 0 | 172.3 | 169 | 157.2 | 152.8 | 184.3 | 27.1 | 20.8 | 42.3 | 3.1 | 204.7 | 5.6 | 39.4 | 52.9 | 25.1 | 43.1 | 28.3 | 65.1 | 112.8 | 79.7 | 60.4 | 59.4 | 265.5 | 249.5 | 242.4 | 223 | 191.5 | 158.6 | 212.9 | 184.9 | 269.3 | 255.5
2529.1 | 2355.1 | -6.1 | 0 | 0 | 172.3 | 169 | 157.2 | 152.7 | 184.3 | 27.1 | 20.8 | 42.3 | 3.3 | 207.5 | 5.7 | 39.4 | 52.9 | 25.1 | 43.3 | 28.4 | 64.8 | 112.5 | 79.7 | 60.4 | 59.3 | 265.4 | 249.4 | 242.3 | 222.8 | 191.4 | 158.5 | 212.8 | 184.8 | 269.2 | 255.4
2530.1 | 2356.1 | -6.1 | 0 | 0 | 172.4 | 168.9 | 157.2 | 152.5 | 184.2 | 27.1 | 20.8 | 42.3 | 3.2 | 208.5 | 5.6 | 39.4 | 52.9 | 25.2 | 42.9 | 28.4 | 64.8 | 112.5 | 79.6 | 60.3 | 59.2 | 265.3 | 249.3 | 242.2 | 222.7 | 191.3 | 158.3 | 212.7 | 184.7 | 269 | 255.3
2531.1 | 2357.1 | -6.2 | 0 | 0 | 172.3 | 168.9 | 157.1 | 152.4 | 184.2 | 27.1 | 20.8 | 42.3 | 3.2 | 198.6 | 5.6 | 39.4 | 52.9 | 25.3 | 43 | 28.4 | 65.1 | 112.4 | 79.4 | 60.2 | 58.9 | 265.3 | 249.2 | 242.1 | 222.6 | 191.2 | 158.3 | 212.7 | 184.7 | 268.9 | 255.2
2532.1 | 2358.1 | -6.1 | 0 | 0 | 172.1 | 168.8 | 157.1 | 152.4 | 184.1 | 27.1 | 20.8 | 42.2 | 3.3 | 200.1 | 5.8 | 39.4 | 53 | 25.3 | 42.7 | 28.4 | 65.2 | 112.6 | 79.3 | 60.3 | 58.9 | 265.3 | 249.1 | 242 | 222.5 | 191.2 | 158.2 | 212.6 | 184.6 | 268.7 | 255.1
2533.1 | 2359.1 | -6 | 0 | 0 | 171.8 | 168.8 | 157 | 152.2 | 184 | 27.1 | 20.8 | 42.2 | 3.3 | 200.3 | 6 | 39.4 | 53.1 | 25.4 | 42.5 | 28.4 | 65.1 | 112.6 | 79.3 | 60.4 | 59 | 265.2 | 249 | 241.9 | 222.4 | 191.1 | 158.1 | 212.4 | 184.5 | 268.6 | 254.9
2534.1 | 2360.1 | -6 | 0 | 0 | 171.6 | 168.8 | 156.9 | 152.2 | 183.9 | 27.1 | 20.8 | 42.1 | 3.2 | 203.4 | 6.3 | 39.4 | 53 | 25.4 | 42.8 | 28.4 | 64.6 | 112.5 | 79.2 | 60.2 | 59.1 | 265.2 | 248.9 | 241.8 | 222.3 | 191.1 | 158 | 212.3 | 184.4 | 268.4 | 254.8
2535.1 | 2361.1 | -6.1 | 0 | 0 | 171.6 | 168.7 | 156.7 | 152.1 | 183.8 | 27 | 20.8 | 42.1 | 3 | 201.1 | 6.5 | 39.4 | 53 | 25.4 | 42.9 | 28.5 | 64.5 | 112.1 | 79.2 | 60.1 | 59.1 | 265.1 | 248.9 | 241.7 | 222.1 | 191 | 158 | 212.2 | 184.3 | 268.3 | 254.7
2536.1 | 2362.1 | -5.9 | 0 | 0 | 171.6 | 168.5 | 156.7 | 152.1 | 183.8 | 27 | 20.8 | 42.1 | 3 | 205.8 | 6.6 | 39.4 | 52.9 | 25.5 | 43.3 | 28.5 | 64.4 | 111.9 | 79.1 | 60.1 | 59.1 | 265.1 | 248.8 | 241.6 | 222 | 190.9 | 157.9 | 212.2 | 184.2 | 268.1 | 254.6

## First Electrical Failures
SCDU 1 Location G Bundle 10-4 PE Cable 'A' - Hot short failure to Path 4 | Time (s) | Offset Time (s) | C1 V1 | C1 V4 | SCDU-4 Location G Bundle 10-4 EPR Cable 'C' - Fuse Blow Failure | Time (s) | Offset Time (s) | C4 V1
| 0 | -174 | 127.8011 | 0.28746 |  | 0 | -174 | 124.5806
| 60 | -114 | 127.8011 | 0.19008 |  | 60 | -114 | 124.5806
| 120 | -54 | 127.8985 | 0.19008 |  | 120 | -54 | 124.7754
| 180 | 6 | 128.1907 | 0.19008 |  | 180 | 6 | 124.9702
| 240 | 66 | 127.6063 | -0.0047195 |  | 240 | 66 | 124.4832
| 300 | 126 | 129.5542 | -0.0047195 |  | 300 | 126 | 126.5285
| 360 | 186 | 129.4568 | 0.092701 |  | 360 | 186 | 126.2364
| 420 | 246 | 130.0412 | 0.28746 |  | 420 | 246 | 126.6259
| 480 | 306 | 129.6516 | 0.092701 |  | 480 | 306 | 126.6259
| 540 | 366 | 129.5542 | 0.092701 |  | 540 | 366 | 126.5285
| 600 | 426 | 129.6516 | 0.19008 |  | 600 | 426 | 126.6259
| 660 | 486 | 131.5022 | 0.28746 |  | 660 | 486 | 128.0869
| 720 | 546 | 129.749 | 0.19008 |  | 720 | 546 | 126.7233
| 780 | 606 | 130.1386 | 0.38488 |  | 780 | 606 | 126.6259
| 840 | 666 | 129.9438 | 0.19008 |  | 840 | 666 | 126.8207
| 900 | 726 | 129.8464 | 0.19008 |  | 900 | 726 | 126.7233
| 900.2 | 726.2 | 129.9438 | 0.19008 |  | 930 | 756 | 126.5285
| 900.4 | 726.4 | 129.8464 | 0.19008 |  | 960 | 786 | 126.8207
| 900.6 | 726.6 | 129.9438 | 0.19008 |  | 990 | 816 | 127.0155
| 900.8 | 726.8 | 129.9438 | 0.19008 |  | 1020 | 846 | 126.9181
| 901 | 727 | 129.9438 | 0.19008 |  | 1050 | 876 | 126.8207
| 901.2 | 727.2 | 129.9438 | 0.28746 |  | 1080 | 906 | 126.9181
| 901.4 | 727.4 | 129.9438 | 0.19008 |  | 1110 | 936 | 127.0155
| 901.6 | 727.6 | 129.9438 | 0.28746 |  | 1140 | 966 | 127.0155
| 901.8 | 727.8 | 129.9438 | 0.19008 |  | 1170 | 996 | 127.3077
| 902 | 728 | 129.8464 | 0.28746 |  | 1200 | 1026 | 127.1129
| 902.2 | 728.2 | 129.9438 | 0.28746 |  | 1210 | 1036 | 127.2103
| 902.4 | 728.4 | 129.9438 | 0.19008 |  | 1220 | 1046 | 127.6973
| 902.6 | 728.6 | 129.9438 | 0.28746 |  | 1230 | 1056 | 127.0155
| 902.8 | 728.8 | 129.9438 | 0.28746 |  | 1240 | 1066 | 127.3077
| 903 | 729 | 129.9438 | 0.28746 |  | 1250 | 1076 | 127.1129
| 903.2 | 729.2 | 129.9438 | 0.19008 |  | 1260 | 1086 | 127.3077
| 903.4 | 729.4 | 129.9438 | 0.28746 |  | 1270 | 1096 | 127.0155
| 903.6 | 729.6 | 129.9438 | 0.19008 |  | 1280 | 1106 | 127.1129
| 903.8 | 729.8 | 129.9438 | 0.28746 |  | 1290 | 1116 | 127.0155
| 904 | 730 | 129.9438 | 0.19008 |  | 1300 | 1126 | 127.3077
| 904.2 | 730.2 | 130.0412 | 0.19008 |  | 1310 | 1136 | 127.1129
| 904.4 | 730.4 | 130.0412 | 0.19008 |  | 1320 | 1146 | 127.1129
| 904.6 | 730.6 | 130.0412 | 0.19008 |  | 1330 | 1156 | 127.4051
| 904.8 | 730.8 | 130.0412 | 0.28746 |  | 1340 | 1166 | 127.2103
| 905 | 731 | 130.0412 | 0.28746 |  | 1350 | 1176 | 126.9181
| 905.2 | 731.2 | 130.0412 | 0.28746 |  | 1360 | 1186 | 127.2103
| 905.4 | 731.4 | 130.0412 | 0.28746 |  | 1370 | 1196 | 127.0155
| 905.6 | 731.6 | 130.0412 | 0.38488 |  | 1380 | 1206 | 127.5025
| 905.8 | 731.8 | 124.9766 | 82.0032 |  | 1390 | 1216 | 126.9181
| 906 | 732 | 105.2051 | 27.5585 |  | 1400 | 1226 | 127.2103
| 906.2 | 732.2 | 130.0412 | 18.7928 |  | 1410 | 1236 | 127.1129
| 906.4 | 732.4 | 129.6516 | 112.9752 |  | 1420 | 1246 | 126.8207
| 906.6 | 732.6 | 129.5542 | 127.5847 |  | 1430 | 1256 | 126.7233
| 906.8 | 732.8 | 129.6516 | 128.7535 |  | 1440 | 1266 | 126.9181
| 907 | 733 | 129.6516 | 128.9483 |  | 1450 | 1276 | 127.0155
| 907.2 | 733.2 | 129.6516 | 129.0457 |  | 1460 | 1286 | 127.0155
| 907.4 | 733.4 | 129.749 | 129.0457 |  | 1470 | 1296 | 127.1129
| 907.6 | 733.6 | 129.6516 | 129.0457 |  | 1480 | 1306 | 126.9181
| 907.8 | 733.8 | 129.6516 | 129.1431 |  | 1490 | 1316 | 126.9181
| 908 | 734 | 129.6516 | 129.0457 |  | 1500 | 1326 | 126.5285
| 908.2 | 734.2 | 129.749 | 129.1431 |  | 1510 | 1336 | 126.5285
| 908.4 | 734.4 | 129.749 | 129.1431 |  | 1520 | 1346 | 126.5285
| 908.6 | 734.6 | 129.749 | 129.2405 |  | 1530 | 1356 | 126.7233
| 908.8 | 734.8 | 129.749 | 129.1431 |  | 1535 | 1361 | 126.7233
| 909 | 735 | 129.749 | 129.2405 |  | 1540 | 1366 | 126.6259
| 909.2 | 735.2 | 129.749 | 129.2405 |  | 1545 | 1371 | 126.6259
| 909.4 | 735.4 | 129.8464 | 129.3379 |  | 1550 | 1376 | 126.4311
| 909.6 | 735.6 | 129.8464 | 129.2405 |  | 1550.2 | 1376.2 | 126.4311
| 909.8 | 735.8 | 129.8464 | 129.3379 |  | 1550.4 | 1376.4 | 126.5285
| 910 | 736 | 129.8464 | 129.3379 |  | 1550.6 | 1376.6 | 126.4311
| 910.2 | 736.2 | 129.8464 | 129.3379 |  | 1550.8 | 1376.8 | 126.4311
| 910.4 | 736.4 | 129.9438 | 129.3379 |  | 1551 | 1377 | 126.4311
| 910.6 | 736.6 | 129.8464 | 129.3379 |  | 1551.2 | 1377.2 | 126.4311
| 910.8 | 736.8 | 129.9438 | 129.3379 |  | 1551.4 | 1377.4 | 126.3337
| 911 | 737 | 129.8464 | 129.3379 |  | 1551.6 | 1377.6 | 126.3337
| 911.2 | 737.2 | 129.8464 | 129.3379 |  | 1551.8 | 1377.8 | 126.4311
| 911.4 | 737.4 | 129.9438 | 129.3379 |  | 1552 | 1378 | 126.3337
| 911.6 | 737.6 | 129.9438 | 129.4353 |  | 1552.2 | 1378.2 | 126.4311
| 911.8 | 737.8 | 130.0412 | 129.5326 |  | 1552.4 | 1378.4 | 126.3337
| 912 | 738 | 129.9438 | 129.4353 |  | 1552.6 | 1378.6 | 126.4311
| 912.2 | 738.2 | 129.9438 | 129.4353 |  | 1552.8 | 1378.8 | 126.4311
| 912.4 | 738.4 | 129.9438 | 129.5326 |  | 1553 | 1379 | 126.3337
| 912.6 | 738.6 | 129.9438 | 129.5326 |  | 1553.2 | 1379.2 | 126.4311
| 912.8 | 738.8 | 129.9438 | 129.5326 |  | 1553.4 | 1379.4 | 126.4311
| 913 | 739 | 129.9438 | 129.4353 |  | 1553.6 | 1379.6 | 126.3337
| 913.2 | 739.2 | 129.9438 | 129.4353 |  | 1553.8 | 1379.8 | 126.3337
| 913.4 | 739.4 | 129.9438 | 129.5326 |  | 1554 | 1380 | 126.3337
| 913.6 | 739.6 | 129.9438 | 129.4353 |  | 1554.2 | 1380.2 | 126.4311
| 913.8 | 739.8 | 129.9438 | 129.4353 |  | 1554.4 | 1380.4 | 126.4311
| 914 | 740 | 129.9438 | 129.5326 |  | 1554.6 | 1380.6 | 126.4311
| 914.2 | 740.2 | 129.9438 | 129.4353 |  | 1554.8 | 1380.8 | 126.4311
| 914.4 | 740.4 | 130.0412 | 129.4353 |  | 1555 | 1381 | 126.4311
| 914.6 | 740.6 | 129.9438 | 129.5326 |  | 1555.2 | 1381.2 | 126.4311
| 914.8 | 740.8 | 130.0412 | 129.5326 |  | 1555.4 | 1381.4 | 126.5285
| 915 | 741 | 130.0412 | 129.5326 |  | 1555.6 | 1381.6 | 126.4311
| 915.2 | 741.2 | 129.9438 | 129.5326 |  | 1555.8 | 1381.8 | 126.4311
| 915.4 | 741.4 | 130.0412 | 129.5326 |  | 1556 | 1382 | 126.3337
| 915.6 | 741.6 | 130.0412 | 129.5326 |  | 1556.2 | 1382.2 | 126.4311
| 915.8 | 741.8 | 130.1386 | 129.6301 |  | 1556.4 | 1382.4 | 126.4311
| 916 | 742 | 130.0412 | 129.5326 |  | 1556.6 | 1382.6 | 126.4311
| 916.2 | 742.2 | 130.0412 | 129.5326 |  | 1556.8 | 1382.8 | 126.4311
| 916.4 | 742.4 | 130.0412 | 129.5326 |  | 1557 | 1383 | 126.4311
| 916.6 | 742.6 | 130.0412 | 129.5326 |  | 1557.2 | 1383.2 | 126.5285
| 916.8 | 742.8 | 130.1386 | 129.5326 |  | 1557.4 | 1383.4 | 126.5285
| 917 | 743 | 130.0412 | 129.5326 |  | 1557.6 | 1383.6 | 126.4311
| 917.2 | 743.2 | 129.749 | 129.4353 |  | 1557.8 | 1383.8 | 126.5285
| 917.4 | 743.4 | 129.6516 | 129.3379 |  | 1558 | 1384 | 126.4311
| 917.6 | 743.6 | 129.5542 | 130.2144 |  | 1558.2 | 1384.2 | 126.5285
| 917.8 | 743.8 | 129.3595 | 130.3118 |  | 1558.4 | 1384.4 | 126.4311
| 918 | 744 | 129.262 | 129.7274 |  | 1558.6 | 1384.6 | 126.4311
| 918.2 | 744.2 | 129.9438 | 129.5326 |  | 1558.8 | 1384.8 | 126.4311
| 918.4 | 744.4 | 129.8464 | 129.5326 |  | 1559 | 1385 | 126.4311
| 918.6 | 744.6 | 129.9438 | 129.4353 |  | 1559.2 | 1385.2 | 126.4311
| 918.8 | 744.8 | 129.9438 | 129.4353 |  | 1559.4 | 1385.4 | 126.4311
| 919 | 745 | 129.9438 | 129.5326 |  | 1559.6 | 1385.6 | 126.4311
| 919.2 | 745.2 | 130.0412 | 129.5326 |  | 1559.8 | 1385.8 | 126.4311
| 919.4 | 745.4 | 130.0412 | 129.4353 |  | 1560 | 1386 | 126.4311
| 919.6 | 745.6 | 129.9438 | 129.5326 |  | 1560.2 | 1386.2 | 126.4311
| 919.8 | 745.8 | 130.0412 | 129.5326 |  | 1560.4 | 1386.4 | 126.4311
| 920 | 746 | 129.9438 | 129.5326 |  | 1560.6 | 1386.6 | 126.4311
| 920.2 | 746.2 | 130.0412 | 129.4353 |  | 1560.8 | 1386.8 | 126.4311
| 920.4 | 746.4 | 129.9438 | 129.4353 |  | 1561 | 1387 | 126.4311
| 920.6 | 746.6 | 129.9438 | 129.4353 |  | 1561.2 | 1387.2 | 126.4311
| 920.8 | 746.8 | 129.9438 | 129.4353 |  | 1561.4 | 1387.4 | 126.4311
| 921 | 747 | 129.9438 | 129.3379 |  | 1561.6 | 1387.6 | 126.4311
| 921.2 | 747.2 | 129.9438 | 129.3379 |  | 1561.8 | 1387.8 | 126.4311
| 921.4 | 747.4 | 129.9438 | 129.3379 |  | 1562 | 1388 | 126.3337
| 921.6 | 747.6 | 129.9438 | 129.3379 |  | 1562.2 | 1388.2 | 126.4311
| 921.8 | 747.8 | 129.9438 | 129.3379 |  | 1562.4 | 1388.4 | 126.4311
| 922 | 748 | 129.8464 | 129.3379 |  | 1562.6 | 1388.6 | 126.4311
| 922.2 | 748.2 | 129.8464 | 129.4353 |  | 1562.8 | 1388.8 | 126.4311
| 922.4 | 748.4 | 129.8464 | 129.3379 |  | 1563 | 1389 | 126.4311
| 922.6 | 748.6 | 129.8464 | 129.3379 |  | 1563.2 | 1389.2 | 126.4311
| 922.8 | 748.8 | 129.8464 | 129.3379 |  | 1563.4 | 1389.4 | 126.4311
| 923 | 749 | 129.8464 | 129.3379 |  | 1563.6 | 1389.6 | 126.3337
| 923.2 | 749.2 | 129.8464 | 129.3379 |  | 1563.8 | 1389.8 | 126.3337
| 923.4 | 749.4 | 129.8464 | 129.2405 |  | 1564 | 1390 | 126.3337
| 923.6 | 749.6 | 129.8464 | 129.3379 |  | 1564.2 | 1390.2 | 126.3337
| 923.8 | 749.8 | 129.749 | 129.2405 |  | 1564.4 | 1390.4 | 126.4311
| 924 | 750 | 129.749 | 129.1431 |  | 1564.6 | 1390.6 | 126.4311
| 924.2 | 750.2 | 129.8464 | 129.3379 |  | 1564.8 | 1390.8 | 126.4311
| 924.4 | 750.4 | 129.8464 | 129.2405 |  | 1565 | 1391 | 126.3337
| 924.6 | 750.6 | 129.6516 | 129.2405 |  | 1565.2 | 1391.2 | 126.3337
| 924.8 | 750.8 | 129.6516 | 129.1431 |  | 1565.4 | 1391.4 | 126.3337
| 925 | 751 | 129.6516 | 129.1431 |  | 1565.6 | 1391.6 | 126.4311
| 925.2 | 751.2 | 129.6516 | 129.2405 |  | 1565.8 | 1391.8 | 126.3337
| 925.4 | 751.4 | 129.749 | 129.2405 |  | 1566 | 1392 | 126.3337
| 925.6 | 751.6 | 129.749 | 129.2405 |  | 1566.2 | 1392.2 | 126.3337
| 925.8 | 751.8 | 129.6516 | 129.1431 |  | 1566.4 | 1392.4 | 126.4311
| 926 | 752 | 129.6516 | 129.0457 |  | 1566.6 | 1392.6 | 126.3337
| 926.2 | 752.2 | 129.6516 | 129.1431 |  | 1566.8 | 1392.8 | 126.3337
| 926.4 | 752.4 | 129.6516 | 129.0457 |  | 1567 | 1393 | 126.3337
| 926.6 | 752.6 | 129.6516 | 129.0457 |  | 1567.2 | 1393.2 | 20.8533
| 926.8 | 752.8 | 129.5542 | 129.0457 |  | 1567.4 | 1393.4 | 3.4193
| 927 | 753 | 129.5542 | 129.0457 |  | 1567.6 | 1393.6 | 1.374
| 927.2 | 753.2 | 129.4568 | 128.9483 |  | 1567.8 | 1393.8 | 0.88702
| 927.4 | 753.4 | 129.4568 | 129.0457 |  | 1568 | 1394 | 0.69222
| 927.6 | 753.6 | 129.5542 | 129.0457 |  | 1568.2 | 1394.2 | 0.59484
| 927.8 | 753.8 | 129.5542 | 128.9483 |  | 1568.4 | 1394.4 | 0.49742
| 928 | 754 | 129.3595 | 128.9483 |  | 1568.6 | 1394.6 | 0.49742
| 928.2 | 754.2 | 129.5542 | 128.9483 |  | 1568.8 | 1394.8 | 0.49742
| 928.4 | 754.4 | 129.5542 | 128.9483 |  | 1569 | 1395 | 0.40004
| 928.6 | 754.6 | 129.5542 | 128.9483 |  | 1569.2 | 1395.2 | 0.40004
| 928.8 | 754.8 | 129.4568 | 128.9483 |  | 1569.4 | 1395.4 | 0.30262
| 929 | 755 | 129.4568 | 128.9483 |  | 1569.6 | 1395.6 | 0.40004
| 929.2 | 755.2 | 129.5542 | 128.9483 |  | 1569.8 | 1395.8 | 0.40004
| 929.4 | 755.4 | 129.4568 | 128.9483 |  | 1570 | 1396 | 0.40004
| 929.6 | 755.6 | 129.5542 | 129.0457 |  | 1580 | 1406 | 0.20523
| 929.8 | 755.8 | 129.4568 | 128.9483 |  | 1590 | 1416 | 0.20523
| 930 | 756 | 129.4568 | 128.8509 |  | 1620 | 1446 | 0.20523
| 930.2 | 756.2 | 129.5542 | 128.9483 |  | 1680 | 1506 | 0.20523
| 930.4 | 756.4 | 129.4568 | 128.9483
| 930.6 | 756.6 | 129.4568 | 128.9483
| 930.8 | 756.8 | 129.4568 | 128.9483
| 931 | 757 | 129.4568 | 129.0457
| 931.2 | 757.2 | 129.4568 | 128.9483
| 931.4 | 757.4 | 129.4568 | 129.0457
| 931.6 | 757.6 | 129.4568 | 128.9483
| 931.8 | 757.8 | 129.4568 | 128.9483
| 932 | 758 | 129.4568 | 129.0457
| 932.2 | 758.2 | 129.4568 | 128.9483
| 932.4 | 758.4 | 129.4568 | 129.0457
| 932.6 | 758.6 | 129.4568 | 128.9483
| 932.8 | 758.8 | 129.4568 | 128.9483
| 933 | 759 | 129.5542 | 128.9483
| 933.2 | 759.2 | 129.4568 | 128.9483
| 933.4 | 759.4 | 129.4568 | 128.9483
| 933.6 | 759.6 | 129.5542 | 128.9483
| 933.8 | 759.8 | 129.4568 | 128.9483
| 934 | 760 | 129.4568 | 128.8509
| 934.2 | 760.2 | 129.4568 | 128.9483
| 934.4 | 760.4 | 129.4568 | 128.8509
| 934.6 | 760.6 | 129.3595 | 128.8509
| 934.8 | 760.8 | 129.4568 | 128.8509
| 935 | 761 | 129.3595 | 128.8509
| 935.2 | 761.2 | 129.3595 | 128.8509
| 935.4 | 761.4 | 129.3595 | 128.8509
| 935.6 | 761.6 | 129.3595 | 128.8509
| 935.8 | 761.8 | 129.3595 | 128.8509
| 936 | 762 | 129.3595 | 128.7535
| 936.2 | 762.2 | 129.3595 | 128.7535
| 936.4 | 762.4 | 129.3595 | 128.7535
| 936.6 | 762.6 | 129.3595 | 128.8509
| 936.8 | 762.8 | 129.262 | 128.7535
| 937 | 763 | 129.3595 | 128.8509
| 937.2 | 763.2 | 129.3595 | 128.8509
| 937.4 | 763.4 | 129.3595 | 128.8509
| 937.6 | 763.6 | 129.3595 | 128.7535
| 937.8 | 763.8 | 129.3595 | 128.8509
| 938 | 764 | 129.262 | 128.8509
| 938.2 | 764.2 | 129.3595 | 128.8509
| 938.4 | 764.4 | 129.3595 | 128.8509
| 938.6 | 764.6 | 129.3595 | 128.8509
| 938.8 | 764.8 | 129.3595 | 128.7535
| 939 | 765 | 129.262 | 128.8509
| 939.2 | 765.2 | 129.262 | 128.6561
| 939.4 | 765.4 | 129.3595 | 128.7535
| 939.6 | 765.6 | 129.262 | 128.7535
| 939.8 | 765.8 | 129.3595 | 128.8509
| 940 | 766 | 129.262 | 128.7535
| 940.2 | 766.2 | 129.3595 | 128.8509
| 940.4 | 766.4 | 129.4568 | 128.8509
| 940.6 | 766.6 | 129.3595 | 128.8509
| 940.8 | 766.8 | 129.4568 | 128.8509
| 941 | 767 | 129.3595 | 128.8509
| 941.2 | 767.2 | 129.3595 | 128.8509
| 941.4 | 767.4 | 129.4568 | 128.9483
| 941.6 | 767.6 | 129.4568 | 128.8509
| 941.8 | 767.8 | 129.4568 | 128.8509
| 942 | 768 | 129.3595 | 128.8509
| 942.2 | 768.2 | 129.3595 | 128.8509
| 942.4 | 768.4 | 129.4568 | 128.8509
| 942.6 | 768.6 | 129.3595 | 128.8509
| 942.8 | 768.8 | 129.3595 | 128.8509
| 943 | 769 | 129.3595 | 128.7535
| 943.2 | 769.2 | 129.3595 | 128.8509
| 943.4 | 769.4 | 129.3595 | 128.7535
| 943.6 | 769.6 | 129.3595 | 128.8509
| 943.8 | 769.8 | 129.3595 | 128.8509
| 944 | 770 | 129.262 | 128.7535
| 944.2 | 770.2 | 129.3595 | 128.8509
| 944.4 | 770.4 | 129.3595 | 128.7535
| 944.6 | 770.6 | 129.3595 | 128.7535
| 944.8 | 770.8 | 129.4568 | 128.9483
| 945 | 771 | 129.4568 | 128.9483
| 945.2 | 771.2 | 129.4568 | 128.8509
| 945.4 | 771.4 | 129.3595 | 128.9483
| 945.6 | 771.6 | 129.5542 | 128.9483
| 945.8 | 771.8 | 129.749 | 129.0457
| 946 | 772 | 129.8464 | 128.9483
| 946.2 | 772.2 | 129.9438 | 127.9743
| 946.4 | 772.4 | 129.8464 | 127.9743
| 946.6 | 772.6 | 130.6256 | 128.4613
| 946.8 | 772.8 | 130.1386 | 128.6561
| 947 | 773 | 129.6516 | 128.8509
| 947.2 | 773.2 | 129.5542 | 128.9483
| 947.4 | 773.4 | 129.4568 | 128.8509
| 947.6 | 773.6 | 129.4568 | 128.8509
| 947.8 | 773.8 | 129.4568 | 128.8509
| 948 | 774 | 129.3595 | 128.7535
| 948.2 | 774.2 | 129.4568 | 128.8509
| 948.4 | 774.4 | 129.3595 | 128.8509
| 948.6 | 774.6 | 129.3595 | 128.8509
| 948.8 | 774.8 | 129.3595 | 128.8509
| 949 | 775 | 129.3595 | 128.8509
| 949.2 | 775.2 | 129.3595 | 128.7535
| 949.4 | 775.4 | 129.3595 | 128.7535
| 949.6 | 775.6 | 129.3595 | 128.7535
| 949.8 | 775.8 | 129.3595 | 128.8509
| 950 | 776 | 129.262 | 128.8509
| 950.2 | 776.2 | 129.3595 | 128.8509
| 950.4 | 776.4 | 129.3595 | 128.8509
| 950.6 | 776.6 | 129.3595 | 128.8509
| 950.8 | 776.8 | 129.3595 | 128.8509
| 951 | 777 | 129.3595 | 128.7535
| 951.2 | 777.2 | 129.3595 | 128.8509
| 951.4 | 777.4 | 129.262 | 128.7535
| 951.6 | 777.6 | 129.3595 | 128.8509
| 951.8 | 777.8 | 129.3595 | 128.7535
| 952 | 778 | 129.262 | 128.6561
| 952.2 | 778.2 | 129.3595 | 128.7535
| 952.4 | 778.4 | 129.262 | 128.7535
| 952.6 | 778.6 | 129.262 | 128.7535
| 952.8 | 778.8 | 129.1647 | 128.6561
| 953 | 779 | 129.1647 | 128.6561
| 953.2 | 779.2 | 129.3595 | 128.7535
| 953.4 | 779.4 | 129.262 | 128.7535
| 953.6 | 779.6 | 129.262 | 128.7535
| 953.8 | 779.8 | 129.262 | 128.7535
| 954 | 780 | 129.1647 | 128.6561
| 954.2 | 780.2 | 129.262 | 128.7535
| 954.4 | 780.4 | 129.262 | 128.7535
| 954.6 | 780.6 | 129.262 | 128.7535
| 954.8 | 780.8 | 129.262 | 128.8509
| 955 | 781 | 129.262 | 128.8509
| 955.2 | 781.2 | 129.262 | 128.7535
| 955.4 | 781.4 | 129.262 | 128.7535
| 955.6 | 781.6 | 129.3595 | 128.8509
| 955.8 | 781.8 | 129.262 | 128.8509
| 956 | 782 | 129.262 | 128.8509
| 956.2 | 782.2 | 129.262 | 128.8509
| 956.4 | 782.4 | 129.3595 | 128.7535
| 956.6 | 782.6 | 129.3595 | 128.8509
| 956.8 | 782.8 | 129.262 | 128.8509
| 957 | 783 | 129.3595 | 128.8509
| 957.2 | 783.2 | 129.3595 | 128.8509
| 957.4 | 783.4 | 129.262 | 128.9483
| 957.6 | 783.6 | 129.3595 | 128.9483
| 957.8 | 783.8 | 129.3595 | 128.8509
| 958 | 784 | 129.3595 | 128.8509
| 958.2 | 784.2 | 129.3595 | 128.8509
| 958.4 | 784.4 | 129.3595 | 128.9483
| 958.6 | 784.6 | 129.4568 | 128.9483
| 958.8 | 784.8 | 129.4568 | 128.9483
| 959 | 785 | 129.4568 | 128.9483
| 959.2 | 785.2 | 129.4568 | 128.9483
| 959.4 | 785.4 | 129.4568 | 128.9483
| 959.6 | 785.6 | 129.4568 | 129.0457
| 959.8 | 785.8 | 129.4568 | 128.9483
| 960 | 786 | 129.4568 | 129.0457
| 960.2 | 786.2 | 129.4568 | 129.0457
| 960.4 | 786.4 | 129.5542 | 129.1431
| 960.6 | 786.6 | 129.5542 | 129.1431
| 960.8 | 786.8 | 129.5542 | 129.1431
| 961 | 787 | 129.6516 | 129.1431
| 961.2 | 787.2 | 129.5542 | 129.2405
| 961.4 | 787.4 | 129.6516 | 129.2405
| 961.6 | 787.6 | 129.5542 | 129.3379
| 961.8 | 787.8 | 129.6516 | 129.2405
| 962 | 788 | 129.6516 | 129.3379
| 962.2 | 788.2 | 129.749 | 129.3379
| 962.4 | 788.4 | 129.749 | 129.3379
| 962.6 | 788.6 | 129.749 | 129.4353
| 962.8 | 788.8 | 129.749 | 129.3379
| 963 | 789 | 129.8464 | 129.4353
| 963.2 | 789.2 | 129.8464 | 129.4353
| 963.4 | 789.4 | 129.8464 | 129.4353
| 963.6 | 789.6 | 129.8464 | 129.5326
| 963.8 | 789.8 | 129.8464 | 129.5326
| 964 | 790 | 129.8464 | 129.5326
| 964.2 | 790.2 | 130.0412 | 129.5326
| 964.4 | 790.4 | 129.9438 | 129.6301
| 964.6 | 790.6 | 129.9438 | 129.6301
| 964.8 | 790.8 | 129.9438 | 129.6301
| 965 | 791 | 130.0412 | 129.6301
| 965.2 | 791.2 | 129.9438 | 129.7274
| 965.4 | 791.4 | 129.9438 | 129.6301
| 965.6 | 791.6 | 129.9438 | 129.6301
| 965.8 | 791.8 | 130.0412 | 129.6301
| 966 | 792 | 129.9438 | 129.5326
| 966.2 | 792.2 | 130.0412 | 129.6301
| 966.4 | 792.4 | 130.0412 | 129.6301
| 966.6 | 792.6 | 130.0412 | 129.7274
| 966.8 | 792.8 | 130.0412 | 129.7274
| 967 | 793 | 130.0412 | 129.7274
| 967.2 | 793.2 | 130.1386 | 129.7274
| 967.4 | 793.4 | 130.1386 | 129.7274
| 967.6 | 793.6 | 130.1386 | 129.8249
| 967.8 | 793.8 | 130.236 | 129.8249
| 968 | 794 | 130.1386 | 129.8249
| 968.2 | 794.2 | 130.236 | 129.8249
| 968.4 | 794.4 | 130.1386 | 129.8249
| 968.6 | 794.6 | 130.1386 | 129.8249
| 968.8 | 794.8 | 130.236 | 129.8249
| 969 | 795 | 130.1386 | 129.7274
| 969.2 | 795.2 | 129.8464 | 129.6301
| 969.4 | 795.4 | 129.6516 | 130.7014
| 969.6 | 795.6 | 129.4568 | 130.5067
| 969.8 | 795.8 | 129.8464 | 130.0197
| 970 | 796 | 130.1386 | 129.8249
| 970.2 | 796.2 | 130.1386 | 129.8249
| 970.4 | 796.4 | 130.1386 | 129.8249
| 970.6 | 796.6 | 130.1386 | 129.8249
| 970.8 | 796.8 | 130.236 | 129.8249
| 971 | 797 | 130.1386 | 129.7274
| 971.2 | 797.2 | 130.1386 | 129.7274
| 971.4 | 797.4 | 130.1386 | 129.7274
| 971.6 | 797.6 | 130.1386 | 129.7274
| 971.8 | 797.8 | 130.1386 | 129.7274
| 972 | 798 | 130.0412 | 129.6301
| 972.2 | 798.2 | 130.0412 | 129.6301
| 972.4 | 798.4 | 130.0412 | 129.6301
| 972.6 | 798.6 | 130.0412 | 129.6301
| 972.8 | 798.8 | 130.0412 | 129.6301
| 973 | 799 | 129.9438 | 129.5326
| 973.2 | 799.2 | 130.0412 | 129.5326
| 973.4 | 799.4 | 129.9438 | 129.5326
| 973.6 | 799.6 | 129.9438 | 129.5326
| 973.8 | 799.8 | 129.9438 | 129.4353
| 974 | 800 | 129.8464 | 129.4353
| 974.2 | 800.2 | 129.9438 | 129.5326
| 974.4 | 800.4 | 129.8464 | 129.4353
| 974.6 | 800.6 | 129.8464 | 129.4353
| 974.8 | 800.8 | 129.8464 | 129.4353
| 975 | 801 | 129.8464 | 129.4353
| 975.2 | 801.2 | 129.8464 | 129.4353
| 975.4 | 801.4 | 129.8464 | 129.4353
| 975.6 | 801.6 | 129.8464 | 129.3379
| 975.8 | 801.8 | 129.8464 | 129.3379
| 976 | 802 | 129.749 | 129.3379
| 976.2 | 802.2 | 129.749 | 129.3379
| 976.4 | 802.4 | 129.749 | 129.3379
| 976.6 | 802.6 | 129.749 | 129.3379
| 976.8 | 802.8 | 129.749 | 129.3379
| 977 | 803 | 129.749 | 129.2405
| 977.2 | 803.2 | 129.749 | 129.3379
| 977.4 | 803.4 | 129.6516 | 129.2405
| 977.6 | 803.6 | 129.6516 | 129.2405
| 977.8 | 803.8 | 129.749 | 129.1431
| 978 | 804 | 129.5542 | 129.1431
| 978.2 | 804.2 | 129.5542 | 129.2405
| 978.4 | 804.4 | 129.6516 | 129.2405
| 978.6 | 804.6 | 129.6516 | 129.2405
| 978.8 | 804.8 | 129.5542 | 129.1431
| 979 | 805 | 129.6516 | 129.1431
| 979.2 | 805.2 | 129.5542 | 129.1431
| 979.4 | 805.4 | 129.5542 | 129.1431
| 979.6 | 805.6 | 129.5542 | 129.1431
| 979.8 | 805.8 | 129.5542 | 129.1431
| 980 | 806 | 129.5542 | 129.1431
| 980.2 | 806.2 | 129.5542 | 129.1431
| 980.4 | 806.4 | 129.4568 | 129.0457
| 980.6 | 806.6 | 129.5542 | 129.1431
| 980.8 | 806.8 | 129.4568 | 129.0457
| 981 | 807 | 129.5542 | 129.0457
| 981.2 | 807.2 | 129.5542 | 129.0457
| 981.4 | 807.4 | 129.5542 | 129.1431
| 981.6 | 807.6 | 129.5542 | 129.0457
| 981.8 | 807.8 | 129.4568 | 129.0457
| 982 | 808 | 129.4568 | 129.0457
| 982.2 | 808.2 | 129.4568 | 129.0457
| 982.4 | 808.4 | 129.4568 | 129.0457
| 982.6 | 808.6 | 129.4568 | 129.0457
| 982.8 | 808.8 | 129.5542 | 129.0457
| 983 | 809 | 129.5542 | 129.1431
| 983.2 | 809.2 | 129.5542 | 129.1431
| 983.4 | 809.4 | 129.5542 | 129.0457
| 983.6 | 809.6 | 129.5542 | 129.0457
| 983.8 | 809.8 | 129.5542 | 129.0457
| 984 | 810 | 129.4568 | 129.0457
| 984.2 | 810.2 | 129.4568 | 129.0457
| 984.4 | 810.4 | 129.4568 | 129.0457
| 984.6 | 810.6 | 129.4568 | 129.0457
| 984.8 | 810.8 | 129.4568 | 129.0457
| 985 | 811 | 129.4568 | 129.0457
| 985.2 | 811.2 | 129.4568 | 129.0457
| 985.4 | 811.4 | 129.4568 | 129.0457
| 985.6 | 811.6 | 129.4568 | 129.0457
| 985.8 | 811.8 | 129.4568 | 128.9483
| 986 | 812 | 129.4568 | 128.9483
| 986.2 | 812.2 | 129.4568 | 129.0457
| 986.4 | 812.4 | 129.4568 | 129.0457
| 986.6 | 812.6 | 129.4568 | 129.0457
| 986.8 | 812.8 | 129.3595 | 128.9483
| 987 | 813 | 129.4568 | 128.9483
| 987.2 | 813.2 | 129.3595 | 128.9483
| 987.4 | 813.4 | 129.3595 | 128.9483
| 987.6 | 813.6 | 129.4568 | 128.9483
| 987.8 | 813.8 | 129.3595 | 128.9483
| 988 | 814 | 129.3595 | 128.8509
| 988.2 | 814.2 | 129.3595 | 128.8509
| 988.4 | 814.4 | 129.3595 | 128.9483
| 988.6 | 814.6 | 129.3595 | 128.8509
| 988.8 | 814.8 | 129.3595 | 128.8509
| 989 | 815 | 129.3595 | 128.9483
| 989.2 | 815.2 | 129.3595 | 128.8509
| 989.4 | 815.4 | 129.4568 | 129.0457
| 989.6 | 815.6 | 129.3595 | 128.8509
| 989.8 | 815.8 | 129.3595 | 128.9483
| 990 | 816 | 129.3595 | 128.9483
| 990.2 | 816.2 | 129.4568 | 128.9483
| 990.4 | 816.4 | 129.5542 | 129.0457
| 990.6 | 816.6 | 129.5542 | 129.1431
| 990.8 | 816.8 | 129.6516 | 129.2405
| 991 | 817 | 129.6516 | 129.2405
| 991.2 | 817.2 | 129.5542 | 129.1431
| 991.4 | 817.4 | 129.6516 | 129.1431
| 991.6 | 817.6 | 129.5542 | 129.1431
| 991.8 | 817.8 | 129.6516 | 129.1431
| 992 | 818 | 129.5542 | 129.1431
| 992.2 | 818.2 | 129.5542 | 129.0457
| 992.4 | 818.4 | 129.5542 | 129.0457
| 992.6 | 818.6 | 129.6516 | 129.1431
| 992.8 | 818.8 | 129.5542 | 129.2405
| 993 | 819 | 129.6516 | 129.2405
| 993.2 | 819.2 | 129.6516 | 129.1431
| 993.4 | 819.4 | 129.6516 | 129.1431
| 993.6 | 819.6 | 129.6516 | 129.2405
| 993.8 | 819.8 | 129.6516 | 129.1431
| 994 | 820 | 129.5542 | 129.1431
| 994.2 | 820.2 | 129.6516 | 129.2405
| 994.4 | 820.4 | 129.6516 | 129.2405
| 994.6 | 820.6 | 129.6516 | 129.1431
| 994.8 | 820.8 | 129.749 | 129.2405
| 995 | 821 | 129.6516 | 129.1431
| 995.2 | 821.2 | 129.6516 | 129.2405
| 995.4 | 821.4 | 129.6516 | 129.1431
| 995.6 | 821.6 | 129.6516 | 129.1431
| 995.8 | 821.8 | 129.749 | 129.2405
| 996 | 822 | 129.5542 | 129.1431
| 996.2 | 822.2 | 129.6516 | 129.2405
| 996.4 | 822.4 | 129.6516 | 129.2405
| 996.6 | 822.6 | 129.6516 | 129.2405
| 996.8 | 822.8 | 129.749 | 129.2405
| 997 | 823 | 129.6516 | 129.1431
| 997.2 | 823.2 | 129.749 | 129.2405
| 997.4 | 823.4 | 129.6516 | 129.1431
| 997.6 | 823.6 | 129.6516 | 129.2405
| 997.8 | 823.8 | 129.6516 | 129.2405
| 998 | 824 | 129.6516 | 129.1431
| 998.2 | 824.2 | 129.6516 | 129.2405
| 998.4 | 824.4 | 129.749 | 129.2405
| 998.6 | 824.6 | 129.749 | 129.2405
| 998.8 | 824.8 | 129.6516 | 129.1431
| 999 | 825 | 129.6516 | 129.2405
| 999.2 | 825.2 | 129.749 | 129.2405
| 999.4 | 825.4 | 129.6516 | 129.2405
| 999.6 | 825.6 | 129.749 | 129.2405
| 999.8 | 825.8 | 129.6516 | 129.1431
| 1000 | 826 | 129.6516 | 129.1431
| 1000.2 | 826.2 | 129.749 | 129.3379
| 1000.4 | 826.4 | 129.8464 | 129.3379
| 1000.6 | 826.6 | 130.0412 | 129.3379
| 1000.8 | 826.8 | 130.1386 | 129.3379
| 1001 | 827 | 130.236 | 128.4613
| 1001.2 | 827.2 | 130.1386 | 128.4613
| 1001.4 | 827.4 | 130.1386 | 128.4613
| 1001.6 | 827.6 | 130.9178 | 128.7535
| 1001.8 | 827.8 | 130.236 | 128.9483
| 1002 | 828 | 129.749 | 129.0457
| 1002.2 | 828.2 | 129.6516 | 129.1431
| 1002.4 | 828.4 | 129.749 | 129.1431
| 1002.6 | 828.6 | 129.6516 | 129.1431
| 1002.8 | 828.8 | 129.5542 | 129.1431
| 1003 | 829 | 129.6516 | 129.1431
| 1003.2 | 829.2 | 129.5542 | 129.1431
| 1003.4 | 829.4 | 129.5542 | 129.0457
| 1003.6 | 829.6 | 129.5542 | 128.9483
| 1003.8 | 829.8 | 129.4568 | 129.1431
| 1004 | 830 | 129.5542 | 129.0457
| 1004.2 | 830.2 | 129.5542 | 129.0457
| 1004.4 | 830.4 | 129.5542 | 129.0457
| 1004.6 | 830.6 | 129.5542 | 129.1431
| 1004.8 | 830.8 | 129.5542 | 129.0457
| 1005 | 831 | 129.5542 | 129.0457
| 1005.2 | 831.2 | 129.4568 | 129.0457
| 1005.4 | 831.4 | 129.5542 | 129.0457
| 1005.6 | 831.6 | 129.4568 | 129.0457
| 1005.8 | 831.8 | 129.4568 | 129.0457
| 1006 | 832 | 129.4568 | 129.0457
| 1006.2 | 832.2 | 129.4568 | 129.0457
| 1006.4 | 832.4 | 129.4568 | 129.0457
| 1006.6 | 832.6 | 129.5542 | 129.1431
| 1006.8 | 832.8 | 129.4568 | 129.0457
| 1007 | 833 | 129.5542 | 129.0457
| 1007.2 | 833.2 | 129.5542 | 129.0457
| 1007.4 | 833.4 | 129.5542 | 129.0457
| 1007.6 | 833.6 | 129.5542 | 129.0457
| 1007.8 | 833.8 | 129.5542 | 129.0457
| 1008 | 834 | 129.5542 | 129.0457
| 1008.2 | 834.2 | 129.5542 | 129.0457
| 1008.4 | 834.4 | 129.5542 | 129.1431
| 1008.6 | 834.6 | 129.5542 | 129.0457
| 1008.8 | 834.8 | 129.5542 | 129.1431
| 1009 | 835 | 129.5542 | 129.0457
| 1009.2 | 835.2 | 129.4568 | 129.0457
| 1009.4 | 835.4 | 129.5542 | 129.0457
| 1009.6 | 835.6 | 129.5542 | 129.0457
| 1009.8 | 835.8 | 129.5542 | 129.1431
| 1010 | 836 | 129.4568 | 129.0457
| 1010.2 | 836.2 | 129.5542 | 129.0457
| 1010.4 | 836.4 | 129.5542 | 129.0457
| 1010.6 | 836.6 | 129.5542 | 129.0457
| 1010.8 | 836.8 | 129.5542 | 129.1431
| 1011 | 837 | 129.5542 | 129.0457
| 1011.2 | 837.2 | 129.5542 | 129.0457
| 1011.4 | 837.4 | 129.5542 | 129.0457
| 1011.6 | 837.6 | 129.4568 | 129.0457
| 1011.8 | 837.8 | 129.4568 | 129.0457
| 1012 | 838 | 129.3595 | 128.9483
| 1012.2 | 838.2 | 129.4568 | 129.0457
| 1012.4 | 838.4 | 129.4568 | 129.0457
| 1012.6 | 838.6 | 129.4568 | 129.0457
| 1012.8 | 838.8 | 129.4568 | 129.0457
| 1013 | 839 | 129.4568 | 129.0457
| 1013.2 | 839.2 | 129.4568 | 129.0457
| 1013.4 | 839.4 | 129.4568 | 129.0457
| 1013.6 | 839.6 | 129.5542 | 129.1431
| 1013.8 | 839.8 | 129.5542 | 129.0457
| 1014 | 840 | 129.5542 | 129.0457
| 1014.2 | 840.2 | 129.5542 | 129.1431
| 1014.4 | 840.4 | 129.4568 | 129.1431
| 1014.6 | 840.6 | 129.4568 | 129.1431
| 1014.8 | 840.8 | 129.5542 | 129.1431
| 1015 | 841 | 129.4568 | 129.1431
| 1015.2 | 841.2 | 128.9699 | 128.5587
| 1015.4 | 841.4 | 129.0672 | 128.7535
| 1015.6 | 841.6 | 129.262 | 128.8509
| 1015.8 | 841.8 | 129.1647 | 128.7535
| 1016 | 842 | 129.0672 | 128.7535
| 1016.2 | 842.2 | 129.1647 | 128.7535
| 1016.4 | 842.4 | 129.4568 | 129.0457
| 1016.6 | 842.6 | 129.5542 | 129.1431
| 1016.8 | 842.8 | 129.5542 | 129.1431
| 1017 | 843 | 129.5542 | 129.1431
| 1017.2 | 843.2 | 129.5542 | 129.1431
| 1017.4 | 843.4 | 129.5542 | 129.1431
| 1017.6 | 843.6 | 129.6516 | 129.2405
| 1017.8 | 843.8 | 129.6516 | 129.1431
| 1018 | 844 | 129.5542 | 129.1431
| 1018.2 | 844.2 | 129.6516 | 129.2405
| 1018.4 | 844.4 | 129.5542 | 129.2405
| 1018.6 | 844.6 | 129.5542 | 129.1431
| 1018.8 | 844.8 | 129.5542 | 129.1431
| 1019 | 845 | 129.5542 | 129.2405
| 1019.2 | 845.2 | 129.6516 | 129.1431
| 1019.4 | 845.4 | 129.5542 | 129.2405
| 1019.6 | 845.6 | 129.5542 | 129.2405
| 1019.8 | 845.8 | 129.6516 | 129.2405
| 1020 | 846 | 129.5542 | 129.2405
| 1020.2 | 846.2 | 129.6516 | 129.2405
| 1020.4 | 846.4 | 129.6516 | 129.2405
| 1020.6 | 846.6 | 129.6516 | 129.2405
| 1020.8 | 846.8 | 129.6516 | 129.1431
| 1021 | 847 | 129.6516 | 129.2405
| 1021.2 | 847.2 | 129.6516 | 129.2405
| 1021.4 | 847.4 | 129.749 | 129.3379
| 1021.6 | 847.6 | 129.749 | 129.3379
| 1021.8 | 847.8 | 129.6516 | 129.3379
| 1022 | 848 | 129.6516 | 129.3379
| 1022.2 | 848.2 | 129.6516 | 129.3379
| 1022.4 | 848.4 | 129.749 | 129.3379
| 1022.6 | 848.6 | 129.749 | 129.4353
| 1022.8 | 848.8 | 129.749 | 129.4353
| 1023 | 849 | 129.749 | 129.4353
| 1023.2 | 849.2 | 129.749 | 129.4353
| 1023.4 | 849.4 | 129.8464 | 129.4353
| 1023.6 | 849.6 | 129.8464 | 129.4353
| 1023.8 | 849.8 | 129.749 | 129.4353
| 1024 | 850 | 129.749 | 129.4353
| 1024.2 | 850.2 | 129.8464 | 129.4353
| 1024.4 | 850.4 | 129.8464 | 129.5326
| 1024.6 | 850.6 | 129.8464 | 129.4353
| 1024.8 | 850.8 | 129.8464 | 129.5326
| 1025 | 851 | 129.8464 | 129.5326
| 1025.2 | 851.2 | 129.9438 | 129.5326
| 1025.4 | 851.4 | 129.9438 | 129.6301
| 1025.6 | 851.6 | 129.9438 | 129.6301
| 1025.8 | 851.8 | 129.9438 | 129.6301
| 1026 | 852 | 130.0412 | 129.6301
| 1026.2 | 852.2 | 130.0412 | 129.7274
| 1026.4 | 852.4 | 130.0412 | 129.7274
| 1026.6 | 852.6 | 130.0412 | 129.7274
| 1026.8 | 852.8 | 130.0412 | 129.7274
| 1027 | 853 | 130.0412 | 129.7274
| 1027.2 | 853.2 | 130.0412 | 129.6301
| 1027.4 | 853.4 | 130.0412 | 129.6301
| 1027.6 | 853.6 | 130.0412 | 129.6301
| 1027.8 | 853.8 | 130.1386 | 129.7274
| 1028 | 854 | 130.0412 | 129.6301
| 1028.2 | 854.2 | 130.0412 | 129.6301
| 1028.4 | 854.4 | 130.1386 | 129.7274
| 1028.6 | 854.6 | 130.0412 | 129.7274
| 1028.8 | 854.8 | 130.1386 | 129.7274
| 1029 | 855 | 129.8464 | 129.4353
| 1029.2 | 855.2 | 129.8464 | 129.5326
| 1029.4 | 855.4 | 129.8464 | 129.5326
| 1029.6 | 855.6 | 129.8464 | 129.5326
| 1029.8 | 855.8 | 129.9438 | 129.6301
| 1030 | 856 | 129.8464 | 129.5326
| 1030.2 | 856.2 | 129.9438 | 129.6301
| 1030.4 | 856.4 | 129.9438 | 129.6301
| 1030.6 | 856.6 | 129.9438 | 129.6301
| 1030.8 | 856.8 | 130.0412 | 129.6301
| 1031 | 857 | 129.9438 | 129.6301
| 1031.2 | 857.2 | 129.9438 | 129.6301
| 1031.4 | 857.4 | 130.0412 | 129.6301
| 1031.6 | 857.6 | 129.9438 | 129.6301
| 1031.8 | 857.8 | 130.0412 | 129.6301
| 1032 | 858 | 129.9438 | 129.7274
| 1032.2 | 858.2 | 129.9438 | 129.7274
| 1032.4 | 858.4 | 130.0412 | 129.7274
| 1032.6 | 858.6 | 130.0412 | 129.7274
| 1032.8 | 858.8 | 130.0412 | 129.7274
| 1033 | 859 | 130.0412 | 129.7274
| 1033.2 | 859.2 | 130.0412 | 129.8249
| 1033.4 | 859.4 | 130.0412 | 129.7274
| 1033.6 | 859.6 | 129.9438 | 129.7274
| 1033.8 | 859.8 | 129.9438 | 129.6301
| 1034 | 860 | 129.9438 | 129.6301
| 1034.2 | 860.2 | 130.1386 | 129.8249
| 1034.4 | 860.4 | 130.0412 | 129.7274
| 1034.6 | 860.6 | 130.1386 | 129.8249
| 1034.8 | 860.8 | 130.1386 | 129.8249
| 1035 | 861 | 130.1386 | 129.9222
| 1035.2 | 861.2 | 130.1386 | 129.9222
| 1035.4 | 861.4 | 130.1386 | 129.8249
| 1035.6 | 861.6 | 130.1386 | 129.8249
| 1035.8 | 861.8 | 130.236 | 129.9222
| 1036 | 862 | 130.236 | 130.0197
| 1036.2 | 862.2 | 130.3334 | 130.0197
| 1036.4 | 862.4 | 130.3334 | 130.0197
| 1036.6 | 862.6 | 130.3334 | 130.0197
| 1036.8 | 862.8 | 130.3334 | 130.117
| 1037 | 863 | 130.3334 | 130.0197
| 1037.2 | 863.2 | 130.3334 | 130.0197
| 1037.4 | 863.4 | 130.3334 | 130.117
| 1037.6 | 863.6 | 130.3334 | 130.0197
| 1037.8 | 863.8 | 130.236 | 129.9222
| 1038 | 864 | 129.8464 | 129.7274
| 1038.2 | 864.2 | 129.8464 | 129.7274
| 1038.4 | 864.4 | 129.6516 | 130.9936
| 1038.6 | 864.6 | 129.749 | 130.9936
| 1038.8 | 864.8 | 129.3595 | 130.4092
| 1039 | 865 | 129.9438 | 130.117
| 1039.2 | 865.2 | 130.236 | 130.0197
| 1039.4 | 865.4 | 130.236 | 130.0197
| 1039.6 | 865.6 | 130.3334 | 130.0197
| 1039.8 | 865.8 | 130.236 | 129.9222
| 1040 | 866 | 130.236 | 129.9222
| 1040.2 | 866.2 | 130.3334 | 129.9222
| 1040.4 | 866.4 | 130.236 | 130.0197
| 1040.6 | 866.6 | 130.3334 | 130.0197
| 1040.8 | 866.8 | 130.3334 | 129.9222
| 1041 | 867 | 130.236 | 129.9222
| 1041.2 | 867.2 | 130.236 | 129.9222
| 1041.4 | 867.4 | 130.1386 | 129.9222
| 1041.6 | 867.6 | 130.236 | 129.9222
| 1041.8 | 867.8 | 130.1386 | 129.9222
| 1042 | 868 | 130.1386 | 129.8249
| 1042.2 | 868.2 | 130.236 | 129.8249
| 1042.4 | 868.4 | 130.1386 | 129.8249
| 1042.6 | 868.6 | 130.1386 | 129.8249
| 1042.8 | 868.8 | 130.1386 | 129.8249
| 1043 | 869 | 130.1386 | 129.7274
| 1043.2 | 869.2 | 130.0412 | 129.7274
| 1043.4 | 869.4 | 130.0412 | 129.7274
| 1043.6 | 869.6 | 130.0412 | 129.7274
| 1043.8 | 869.8 | 130.0412 | 129.6301
| 1044 | 870 | 130.0412 | 129.6301
| 1044.2 | 870.2 | 129.9438 | 129.6301
| 1044.4 | 870.4 | 129.9438 | 129.6301
| 1044.6 | 870.6 | 129.9438 | 129.6301
| 1044.8 | 870.8 | 129.8464 | 129.6301
| 1045 | 871 | 129.9438 | 129.6301
| 1045.2 | 871.2 | 129.9438 | 129.5326
| 1045.4 | 871.4 | 129.9438 | 129.6301
| 1045.6 | 871.6 | 129.9438 | 129.5326
| 1045.8 | 871.8 | 129.9438 | 129.5326
| 1046 | 872 | 129.9438 | 129.5326
| 1046.2 | 872.2 | 129.9438 | 129.6301
| 1046.4 | 872.4 | 129.9438 | 129.6301
| 1046.6 | 872.6 | 129.8464 | 129.5326
| 1046.8 | 872.8 | 129.9438 | 129.6301
| 1047 | 873 | 129.9438 | 129.6301
| 1047.2 | 873.2 | 129.8464 | 129.6301
| 1047.4 | 873.4 | 129.9438 | 129.6301
| 1047.6 | 873.6 | 129.9438 | 129.5326
| 1047.8 | 873.8 | 129.9438 | 129.6301
| 1048 | 874 | 129.8464 | 129.5326
| 1048.2 | 874.2 | 129.9438 | 129.5326
| 1048.4 | 874.4 | 129.9438 | 129.5326
| 1048.6 | 874.6 | 129.8464 | 129.5326
| 1048.8 | 874.8 | 129.8464 | 129.5326
| 1049 | 875 | 129.4568 | 129.0457
| 1049.2 | 875.2 | 129.5542 | 129.2405
| 1049.4 | 875.4 | 129.5542 | 129.2405
| 1049.6 | 875.6 | 129.6516 | 129.2405
| 1049.8 | 875.8 | 129.6516 | 129.2405
| 1050 | 876 | 129.5542 | 129.1431
| 1050.2 | 876.2 | 129.5542 | 129.2405
| 1050.4 | 876.4 | 129.5542 | 129.2405
| 1050.6 | 876.6 | 129.5542 | 129.1431
| 1050.8 | 876.8 | 129.4568 | 129.2405
| 1051 | 877 | 129.4568 | 129.0457
| 1051.2 | 877.2 | 129.4568 | 129.1431
| 1051.4 | 877.4 | 129.4568 | 129.0457
| 1051.6 | 877.6 | 129.3595 | 129.0457
| 1051.8 | 877.8 | 129.4568 | 129.1431
| 1052 | 878 | 129.3595 | 128.9483
| 1052.2 | 878.2 | 129.3595 | 128.9483
| 1052.4 | 878.4 | 129.3595 | 128.9483
| 1052.6 | 878.6 | 129.3595 | 128.9483
| 1052.8 | 878.8 | 129.3595 | 128.9483
| 1053 | 879 | 129.262 | 128.8509
| 1053.2 | 879.2 | 129.262 | 128.8509
| 1053.4 | 879.4 | 129.262 | 128.8509
| 1053.6 | 879.6 | 129.1647 | 128.7535
| 1053.8 | 879.8 | 129.1647 | 128.8509
| 1054 | 880 | 129.1647 | 128.7535
| 1054.2 | 880.2 | 129.1647 | 128.8509
| 1054.4 | 880.4 | 129.1647 | 128.6561
| 1054.6 | 880.6 | 129.1647 | 128.7535
| 1054.8 | 880.8 | 129.1647 | 128.7535
| 1055 | 881 | 129.1647 | 128.6561
| 1055.2 | 881.2 | 129.1647 | 128.6561
| 1055.4 | 881.4 | 129.1647 | 128.7535
| 1055.6 | 881.6 | 129.1647 | 128.7535
| 1055.8 | 881.8 | 128.9699 | 128.6561
| 1056 | 882 | 129.0672 | 128.7535
| 1056.2 | 882.2 | 129.1647 | 128.7535
| 1056.4 | 882.4 | 129.0672 | 128.6561
| 1056.6 | 882.6 | 129.0672 | 128.7535
| 1056.8 | 882.8 | 129.0672 | 128.6561
| 1057 | 883 | 129.0672 | 128.6561
| 1057.2 | 883.2 | 128.9699 | 128.6561
| 1057.4 | 883.4 | 128.9699 | 128.6561
| 1057.6 | 883.6 | 128.9699 | 128.5587
| 1057.8 | 883.8 | 129.0672 | 128.5587
| 1058 | 884 | 128.9699 | 128.5587
| 1058.2 | 884.2 | 128.9699 | 128.5587
| 1058.4 | 884.4 | 128.8725 | 128.5587
| 1058.6 | 884.6 | 128.9699 | 128.4613
| 1058.8 | 884.8 | 128.9699 | 128.4613
| 1059 | 885 | 128.8725 | 128.4613
| 1059.2 | 885.2 | 128.9699 | 128.4613
| 1059.4 | 885.4 | 128.8725 | 128.4613
| 1059.6 | 885.6 | 128.8725 | 128.4613
| 1059.8 | 885.8 | 128.8725 | 128.3639
| 1060 | 886 | 128.7751 | 128.3639
| 1060.2 | 886.2 | 128.7751 | 128.3639
| 1060.4 | 886.4 | 128.7751 | 128.3639
| 1060.6 | 886.6 | 128.8725 | 128.3639
| 1060.8 | 886.8 | 128.7751 | 128.3639
| 1061 | 887 | 128.7751 | 128.2665
| 1061.2 | 887.2 | 128.7751 | 128.2665
| 1061.4 | 887.4 | 128.6777 | 128.1691
| 1061.6 | 887.6 | 128.7751 | 128.2665
| 1061.8 | 887.8 | 128.7751 | 128.3639
| 1062 | 888 | 128.6777 | 128.2665
| 1062.2 | 888.2 | 128.6777 | 128.2665
| 1062.4 | 888.4 | 128.7751 | 128.2665
| 1062.6 | 888.6 | 128.7751 | 128.1691
| 1062.8 | 888.8 | 128.7751 | 128.1691
| 1063 | 889 | 128.6777 | 128.2665
| 1063.2 | 889.2 | 128.6777 | 128.2665
| 1063.4 | 889.4 | 128.5803 | 128.1691
| 1063.6 | 889.6 | 128.6777 | 128.1691
| 1063.8 | 889.8 | 128.5803 | 128.1691
| 1064 | 890 | 128.5803 | 128.1691
| 1064.2 | 890.2 | 128.5803 | 128.0717
| 1064.4 | 890.4 | 128.5803 | 128.1691
| 1064.6 | 890.6 | 128.4829 | 128.1691
| 1064.8 | 890.8 | 128.4829 | 128.1691
| 1065 | 891 | 128.6777 | 128.1691
| 1065.2 | 891.2 | 128.5803 | 128.1691
| 1065.4 | 891.4 | 128.5803 | 128.1691
| 1065.6 | 891.6 | 128.6777 | 128.2665
| 1065.8 | 891.8 | 128.6777 | 128.2665
| 1066 | 892 | 128.7751 | 128.2665
| 1066.2 | 892.2 | 128.6777 | 128.1691
| 1066.4 | 892.4 | 128.6777 | 128.2665
| 1066.6 | 892.6 | 128.7751 | 128.3639
| 1066.8 | 892.8 | 128.7751 | 128.3639
| 1067 | 893 | 128.8725 | 128.3639
| 1067.2 | 893.2 | 128.7751 | 128.2665
| 1067.4 | 893.4 | 128.8725 | 128.3639
| 1067.6 | 893.6 | 128.7751 | 128.3639
| 1067.8 | 893.8 | 128.6777 | 128.2665
| 1068 | 894 | 128.6777 | 128.2665
| 1068.2 | 894.2 | 128.6777 | 128.2665
| 1068.4 | 894.4 | 128.7751 | 128.2665
| 1068.6 | 894.6 | 128.6777 | 128.2665
| 1068.8 | 894.8 | 128.6777 | 128.1691
| 1069 | 895 | 128.6777 | 128.1691
| 1069.2 | 895.2 | 128.6777 | 128.1691
| 1069.4 | 895.4 | 128.5803 | 128.1691
| 1069.6 | 895.6 | 128.6777 | 128.0717
| 1069.8 | 895.8 | 128.6777 | 128.1691
| 1070 | 896 | 128.5803 | 128.0717
| 1070.2 | 896.2 | 128.6777 | 128.1691
| 1070.4 | 896.4 | 128.6777 | 128.1691
| 1070.6 | 896.6 | 128.5803 | 128.1691
| 1070.8 | 896.8 | 128.5803 | 128.2665
| 1071 | 897 | 128.6777 | 128.1691
| 1071.2 | 897.2 | 128.5803 | 128.0717
| 1071.4 | 897.4 | 128.5803 | 128.1691
| 1071.6 | 897.6 | 128.7751 | 128.2665
| 1071.8 | 897.8 | 129.1647 | 128.2665
| 1072 | 898 | 129.262 | 128.1691
| 1072.2 | 898.2 | 129.4568 | 127.0004
| 1072.4 | 898.4 | 129.262 | 127.5847
| 1072.6 | 898.6 | 128.8725 | 127.9743
| 1072.8 | 898.8 | 128.6777 | 128.0717
| 1073 | 899 | 128.6777 | 128.1691
| 1073.2 | 899.2 | 128.6777 | 128.2665
| 1073.4 | 899.4 | 128.6777 | 128.1691
| 1073.6 | 899.6 | 128.6777 | 128.1691
| 1073.8 | 899.8 | 128.6777 | 128.1691
| 1074 | 900 | 128.5803 | 128.0717
| 1074.2 | 900.2 | 128.5803 | 128.0717
| 1074.4 | 900.4 | 128.5803 | 128.0717
| 1074.6 | 900.6 | 128.5803 | 128.0717
| 1074.8 | 900.8 | 128.5803 | 128.0717
| 1075 | 901 | 128.5803 | 128.1691
| 1075.2 | 901.2 | 128.5803 | 128.0717
| 1075.4 | 901.4 | 128.5803 | 128.1691
| 1075.6 | 901.6 | 128.5803 | 128.1691
| 1075.8 | 901.8 | 128.6777 | 128.1691
| 1076 | 902 | 128.5803 | 128.1691
| 1076.2 | 902.2 | 128.6777 | 128.2665
| 1076.4 | 902.4 | 128.5803 | 128.1691
| 1076.6 | 902.6 | 128.5803 | 128.1691
| 1076.8 | 902.8 | 128.6777 | 128.1691
| 1077 | 903 | 128.5803 | 128.1691
| 1077.2 | 903.2 | 128.7751 | 128.2665
| 1077.4 | 903.4 | 128.6777 | 128.1691
| 1077.6 | 903.6 | 128.5803 | 128.1691
| 1077.8 | 903.8 | 128.6777 | 128.0717
| 1078 | 904 | 128.5803 | 128.0717
| 1078.2 | 904.2 | 128.5803 | 128.1691
| 1078.4 | 904.4 | 128.5803 | 128.0717
| 1078.6 | 904.6 | 128.5803 | 128.0717
| 1078.8 | 904.8 | 128.4829 | 128.0717
| 1079 | 905 | 128.4829 | 128.0717
| 1079.2 | 905.2 | 128.5803 | 128.1691
| 1079.4 | 905.4 | 128.5803 | 128.0717
| 1079.6 | 905.6 | 128.5803 | 128.1691
| 1079.8 | 905.8 | 128.5803 | 128.1691
| 1080 | 906 | 128.5803 | 128.0717
| 1080.2 | 906.2 | 128.5803 | 128.1691
| 1080.4 | 906.4 | 128.5803 | 128.1691
| 1080.6 | 906.6 | 128.6777 | 128.2665
| 1080.8 | 906.8 | 128.6777 | 128.2665
| 1081 | 907 | 128.6777 | 128.2665
| 1081.2 | 907.2 | 128.6777 | 128.2665
| 1081.4 | 907.4 | 128.6777 | 128.2665
| 1081.6 | 907.6 | 128.7751 | 128.2665
| 1081.8 | 907.8 | 128.6777 | 128.2665
| 1082 | 908 | 128.5803 | 128.1691
| 1082.2 | 908.2 | 128.9699 | 128.7535
| 1082.4 | 908.4 | 128.9699 | 128.6561
| 1082.6 | 908.6 | 121.8599 | 101.1903
| 1082.8 | 908.8 | 129.3595 | 114.4362
| 1083 | 909 | 125.4636 | 126.6108
| 1083.2 | 909.2 | 120.0094 | 108.6898
| 1083.4 | 909.4 | 127.8985 | 113.5596
| 1083.6 | 909.6 | 129.3595 | 120.1826
| 1083.8 | 909.8 | 116.8927 | 96.1257
| 1084 | 910 | 129.1647 | 127.5847
| 1084.2 | 910.2 | 128.8725 | 128.4613
| 1084.4 | 910.4 | 128.8725 | 128.4613
| 1084.6 | 910.6 | 128.8725 | 128.5587
| 1084.8 | 910.8 | 128.8725 | 128.4613
| 1085 | 911 | 128.9699 | 128.5587
| 1085.2 | 911.2 | 128.8725 | 128.5587
| 1085.4 | 911.4 | 128.9699 | 128.5587
| 1085.6 | 911.6 | 128.9699 | 128.5587
| 1085.8 | 911.8 | 128.9699 | 128.5587
| 1086 | 912 | 128.9699 | 128.4613
| 1086.2 | 912.2 | 128.9699 | 128.6561
| 1086.4 | 912.4 | 128.9699 | 128.5587
| 1086.6 | 912.6 | 128.9699 | 128.5587
| 1086.8 | 912.8 | 128.9699 | 128.5587
| 1087 | 913 | 128.9699 | 128.5587
| 1087.2 | 913.2 | 128.9699 | 128.5587
| 1087.4 | 913.4 | 128.9699 | 128.6561
| 1087.6 | 913.6 | 128.9699 | 128.6561
| 1087.8 | 913.8 | 128.9699 | 128.6561
| 1088 | 914 | 128.9699 | 128.6561
| 1088.2 | 914.2 | 128.9699 | 128.6561
| 1088.4 | 914.4 | 129.0672 | 128.7535
| 1088.6 | 914.6 | 129.0672 | 128.7535
| 1088.8 | 914.8 | 129.0672 | 128.7535
| 1089 | 915 | 129.0672 | 128.6561
| 1089.2 | 915.2 | 129.0672 | 128.7535
| 1089.4 | 915.4 | 129.0672 | 128.7535
| 1089.6 | 915.6 | 129.1647 | 128.8509
| 1089.8 | 915.8 | 129.1647 | 128.8509
| 1090 | 916 | 129.1647 | 128.8509
| 1090.2 | 916.2 | 129.262 | 128.9483
| 1090.4 | 916.4 | 129.3595 | 128.9483
| 1090.6 | 916.6 | 129.3595 | 128.9483
| 1090.8 | 916.8 | 129.262 | 129.0457
| 1091 | 917 | 129.4568 | 129.1431
| 1091.2 | 917.2 | 129.4568 | 129.1431
| 1091.4 | 917.4 | 129.4568 | 129.2405
| 1091.6 | 917.6 | 129.4568 | 129.2405
| 1091.8 | 917.8 | 129.5542 | 129.3379
| 1092 | 918 | 129.5542 | 129.2405
| 1092.2 | 918.2 | 129.6516 | 129.3379
| 1092.4 | 918.4 | 129.749 | 129.4353
| 1092.6 | 918.6 | 129.749 | 129.4353
| 1092.8 | 918.8 | 129.749 | 129.4353
| 1093 | 919 | 129.749 | 129.5326
| 1093.2 | 919.2 | 129.749 | 129.4353
| 1093.4 | 919.4 | 129.8464 | 129.5326
| 1093.6 | 919.6 | 129.9438 | 129.6301
| 1093.8 | 919.8 | 130.0412 | 129.7274
| 1094 | 920 | 129.9438 | 129.6301
| 1094.2 | 920.2 | 130.0412 | 129.7274
| 1094.4 | 920.4 | 130.0412 | 129.7274
| 1094.6 | 920.6 | 129.9438 | 129.7274
| 1094.8 | 920.8 | 129.9438 | 129.6301
| 1095 | 921 | 129.9438 | 129.7274
| 1095.2 | 921.2 | 130.0412 | 129.6301
| 1095.4 | 921.4 | 130.0412 | 129.8249
| 1095.6 | 921.6 | 130.0412 | 129.6301
| 1095.8 | 921.8 | 130.0412 | 129.8249
| 1096 | 922 | 129.9438 | 129.8249
| 1096.2 | 922.2 | 130.0412 | 129.8249
| 1096.4 | 922.4 | 130.1386 | 129.9222
| 1096.6 | 922.6 | 130.236 | 129.9222
| 1096.8 | 922.8 | 130.236 | 129.9222
| 1097 | 923 | 130.236 | 129.9222
| 1097.2 | 923.2 | 130.236 | 130.0197
| 1097.4 | 923.4 | 130.236 | 130.0197
| 1097.6 | 923.6 | 130.1386 | 129.9222
| 1097.8 | 923.8 | 129.6516 | 129.6301
| 1098 | 924 | 129.262 | 130.8962
| 1098.2 | 924.2 | 129.6516 | 130.117
| 1098.4 | 924.4 | 130.1386 | 129.9222
| 1098.6 | 924.6 | 130.1386 | 129.8249
| 1098.8 | 924.8 | 130.1386 | 129.9222
| 1099 | 925 | 130.1386 | 129.8249
| 1099.2 | 925.2 | 130.1386 | 129.8249
| 1099.4 | 925.4 | 130.1386 | 129.8249
| 1099.6 | 925.6 | 130.0412 | 129.8249
| 1099.8 | 925.8 | 130.0412 | 129.7274
| 1100 | 926 | 129.9438 | 129.6301
| 1100.2 | 926.2 | 129.9438 | 129.5326
| 1100.4 | 926.4 | 129.8464 | 129.5326
| 1100.6 | 926.6 | 129.8464 | 129.5326
| 1100.8 | 926.8 | 129.8464 | 129.5326
| 1101 | 927 | 129.749 | 129.4353
| 1101.2 | 927.2 | 129.749 | 129.4353
| 1101.4 | 927.4 | 129.749 | 129.3379
| 1101.6 | 927.6 | 129.6516 | 129.4353
| 1101.8 | 927.8 | 129.6516 | 129.3379
| 1102 | 928 | 129.6516 | 129.2405
| 1102.2 | 928.2 | 129.6516 | 129.2405
| 1102.4 | 928.4 | 129.5542 | 129.2405
| 1102.6 | 928.6 | 129.4568 | 129.2405
| 1102.8 | 928.8 | 129.4568 | 129.1431
| 1103 | 929 | 129.3595 | 129.1431
| 1103.2 | 929.2 | 129.4568 | 129.1431
| 1103.4 | 929.4 | 129.3595 | 128.9483
| 1103.6 | 929.6 | 129.262 | 128.8509
| 1103.8 | 929.8 | 129.262 | 128.8509
| 1104 | 930 | 129.0672 | 128.8509
| 1104.2 | 930.2 | 129.1647 | 128.8509
| 1104.4 | 930.4 | 129.0672 | 128.8509
| 1104.6 | 930.6 | 129.0672 | 128.6561
| 1104.8 | 930.8 | 129.1647 | 128.6561
| 1105 | 931 | 129.0672 | 128.7535
| 1105.2 | 931.2 | 129.1647 | 128.7535
| 1105.4 | 931.4 | 129.0672 | 128.7535
| 1105.6 | 931.6 | 129.0672 | 128.7535
| 1105.8 | 931.8 | 129.0672 | 128.6561
| 1106 | 932 | 128.9699 | 128.6561
| 1106.2 | 932.2 | 128.9699 | 128.6561
| 1106.4 | 932.4 | 128.9699 | 128.5587
| 1106.6 | 932.6 | 128.9699 | 128.5587
| 1106.8 | 932.8 | 128.9699 | 128.6561
| 1107 | 933 | 129.0672 | 128.6561
| 1107.2 | 933.2 | 128.9699 | 128.6561
| 1107.4 | 933.4 | 128.9699 | 128.5587
| 1107.6 | 933.6 | 128.9699 | 128.5587
| 1107.8 | 933.8 | 128.9699 | 128.4613
| 1108 | 934 | 128.7751 | 128.3639
| 1108.2 | 934.2 | 128.7751 | 128.3639
| 1108.4 | 934.4 | 128.7751 | 128.4613
| 1108.6 | 934.6 | 128.7751 | 128.3639
| 1108.8 | 934.8 | 128.7751 | 128.3639
| 1109 | 935 | 128.7751 | 128.3639
| 1109.2 | 935.2 | 128.6777 | 128.3639
| 1109.4 | 935.4 | 128.6777 | 128.2665
| 1109.6 | 935.6 | 128.6777 | 128.2665
| 1109.8 | 935.8 | 128.7751 | 128.2665
| 1110 | 936 | 128.6777 | 128.1691
| 1110.2 | 936.2 | 128.6777 | 128.1691
| 1110.4 | 936.4 | 128.6777 | 128.1691
| 1110.6 | 936.6 | 128.5803 | 128.1691
| 1110.8 | 936.8 | 128.5803 | 128.1691
| 1111 | 937 | 128.5803 | 128.2665
| 1111.2 | 937.2 | 128.6777 | 128.1691
| 1111.4 | 937.4 | 128.6777 | 128.1691
| 1111.6 | 937.6 | 128.6777 | 128.1691
| 1111.8 | 937.8 | 128.5803 | 128.1691
| 1112 | 938 | 128.5803 | 128.0717
| 1112.2 | 938.2 | 128.5803 | 128.0717
| 1112.4 | 938.4 | 128.5803 | 128.0717
| 1112.6 | 938.6 | 128.5803 | 128.1691
| 1112.8 | 938.8 | 128.5803 | 128.1691
| 1113 | 939 | 128.5803 | 128.1691
| 1113.2 | 939.2 | 128.6777 | 128.1691
| 1113.4 | 939.4 | 128.6777 | 128.1691
| 1113.6 | 939.6 | 128.6777 | 128.2665
| 1113.8 | 939.8 | 128.6777 | 128.2665
| 1114 | 940 | 128.5803 | 128.1691
| 1114.2 | 940.2 | 128.6777 | 128.2665
| 1114.4 | 940.4 | 128.7751 | 128.3639
| 1114.6 | 940.6 | 128.6777 | 128.2665
| 1114.8 | 940.8 | 128.7751 | 128.3639
| 1115 | 941 | 128.6777 | 128.3639
| 1115.2 | 941.2 | 128.7751 | 128.2665
| 1115.4 | 941.4 | 128.7751 | 128.2665
| 1115.6 | 941.6 | 128.7751 | 128.3639
| 1115.8 | 941.8 | 128.7751 | 128.3639
| 1116 | 942 | 128.6777 | 128.2665
| 1116.2 | 942.2 | 128.7751 | 128.3639
| 1116.4 | 942.4 | 128.7751 | 128.3639
| 1116.6 | 942.6 | 128.7751 | 128.3639
| 1116.8 | 942.8 | 128.7751 | 128.2665
| 1117 | 943 | 128.7751 | 128.2665
| 1117.2 | 943.2 | 128.7751 | 128.2665
| 1117.4 | 943.4 | 128.6777 | 128.2665
| 1117.6 | 943.6 | 128.6777 | 128.2665
| 1117.8 | 943.8 | 128.6777 | 128.2665
| 1118 | 944 | 128.6777 | 128.2665
| 1118.2 | 944.2 | 128.6777 | 128.1691
| 1118.4 | 944.4 | 128.6777 | 128.1691
| 1118.6 | 944.6 | 128.6777 | 128.2665
| 1118.8 | 944.8 | 128.6777 | 128.1691
| 1119 | 945 | 128.6777 | 128.2665
| 1119.2 | 945.2 | 128.6777 | 128.1691
| 1119.4 | 945.4 | 128.6777 | 128.2665
| 1119.6 | 945.6 | 128.5803 | 128.1691
| 1119.8 | 945.8 | 128.6777 | 128.1691
| 1120 | 946 | 128.6777 | 128.2665
| 1120.2 | 946.2 | 128.6777 | 128.2665
| 1120.4 | 946.4 | 128.9699 | 128.3639
| 1120.6 | 946.6 | 129.1647 | 128.5587
| 1120.8 | 946.8 | 129.3595 | 128.4613
| 1121 | 947 | 129.5542 | 127.6821
| 1121.2 | 947.2 | 129.5542 | 127.39
| 1121.4 | 947.4 | 129.3595 | 127.8769
| 1121.6 | 947.6 | 128.9699 | 128.0717
| 1121.8 | 947.8 | 128.7751 | 128.1691
| 1122 | 948 | 128.6777 | 128.1691
| 1122.2 | 948.2 | 128.5803 | 128.1691
| 1122.4 | 948.4 | 128.6777 | 128.2665
| 1122.6 | 948.6 | 128.6777 | 128.1691
| 1122.8 | 948.8 | 128.6777 | 128.2665
| 1123 | 949 | 128.6777 | 128.1691
| 1123.2 | 949.2 | 128.5803 | 128.1691
| 1123.4 | 949.4 | 128.6777 | 128.1691
| 1123.6 | 949.6 | 128.5803 | 128.0717
| 1123.8 | 949.8 | 128.5803 | 128.0717
| 1124 | 950 | 128.5803 | 128.0717
| 1124.2 | 950.2 | 128.5803 | 128.1691
| 1124.4 | 950.4 | 128.5803 | 128.1691
| 1124.6 | 950.6 | 128.5803 | 128.0717
| 1124.8 | 950.8 | 128.5803 | 128.1691
| 1125 | 951 | 128.5803 | 128.1691
| 1125.2 | 951.2 | 128.5803 | 128.1691
| 1125.4 | 951.4 | 128.5803 | 128.1691
| 1125.6 | 951.6 | 128.5803 | 128.1691
| 1125.8 | 951.8 | 128.6777 | 128.1691
| 1126 | 952 | 128.5803 | 128.1691
| 1126.2 | 952.2 | 128.6777 | 128.2665
| 1126.4 | 952.4 | 128.5803 | 128.2665
| 1126.6 | 952.6 | 128.6777 | 128.2665
| 1126.8 | 952.8 | 128.6777 | 128.2665
| 1127 | 953 | 128.5803 | 128.2665
| 1127.2 | 953.2 | 128.6777 | 128.2665
| 1127.4 | 953.4 | 128.5803 | 128.2665
| 1127.6 | 953.6 | 128.6777 | 128.2665
| 1127.8 | 953.8 | 128.6777 | 128.2665
| 1128 | 954 | 128.5803 | 128.1691
| 1128.2 | 954.2 | 128.6777 | 128.2665
| 1128.4 | 954.4 | 128.7751 | 128.2665
| 1128.6 | 954.6 | 128.5803 | 128.0717
| 1128.8 | 954.8 | 128.6777 | 128.1691
| 1129 | 955 | 128.5803 | 128.1691
| 1129.2 | 955.2 | 128.5803 | 128.1691
| 1129.4 | 955.4 | 128.5803 | 128.1691
| 1129.6 | 955.6 | 128.5803 | 128.1691
| 1129.8 | 955.8 | 128.6777 | 128.1691
| 1130 | 956 | 128.4829 | 128.0717
| 1130.2 | 956.2 | 128.5803 | 128.1691
| 1130.4 | 956.4 | 128.4829 | 128.0717
| 1130.6 | 956.6 | 116.4057 | 115.3128
| 1130.8 | 956.8 | 12.094 | 11.0985
| 1131 | 957 | 2.744 | 2.5276
| 1131.2 | 957.2 | 1.283 | 1.164
| 1131.4 | 957.4 | 0.89343 | 0.87186
| 1131.6 | 957.6 | 0.79601 | 0.67706
| 1131.8 | 957.8 | 0.60125 | 0.67706
| 1132 | 958 | 0.60125 | 0.67706
| 1133 | 959 | 0.50383 | 0.38488
| 1134 | 960 | 0.40645 | 0.48226
| 1135 | 961 | 0.40645 | 0.38488
| 1140 | 966 | 0.40645 | 0.38488
| 1200 | 1026 | 0.30903 | 0.19008
| 1260 | 1086 | 0.30903 | 0.19008
| 1320 | 1146 | 0.30903 | 0.28746
| 1380 | 1206 | 0.30903 | 0.28746
| 1440 | 1266 | 0.30903 | 0.28746
| 1500 | 1326 | 0.30903 | 0.19008
| 1560 | 1386 | 0.30903 | 0.19008