## IS Test Matrix
Intermediate Scale Test Matrix - Revision F (12-06-06)
|  | Comments: 1) All tests were conducted as open burns with a Propene (Propylene) gas sand burner 2) Colors identify test conditions grouped into the same test run | [14 empty] | ACTUAL TEST CONDITIONS
Burn Test # | Rev. E Test # | Loc. | Cable Insulation Material | [8 empty] | Number of Conductors |  |  |  | Conductor Size (AWG) |  |  |  |  | Cable Bundle Size |  |  |  |  | Water Spary Optionsl | Raceway Type
|  |  | Thermoset | [5 empty] | Thermoplastic
|  |  | XLPE | EPR | Silicone | XLPO | TS/TP | Vita-Link | PE | PVC | Tefzel | 3 | 2 | 7 | 12 | 8 | 12 | 14 | 16 | 18 | 1 | 3 | 6 | 12 | Load Tr | * | 12" Tray | 2.5" Cnd | Air Drop
Prelim 1 | Prelim 1 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 2 | Prelim 2 | A | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | X | [10 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 3 | Prelim 3 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
Prelim 4 | Prelim 4 | A | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
1 | 15 | A | X | [9 empty] | X | X | X |  | X |  | X | X |  |  |  |  | X |  | X
|  | B | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | D | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | E | X | [10 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
2 | 1 | A | X | [10 empty] | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [10 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | [5 empty] | X |  |  |  |  | X |  |  | X | [6 empty] | X |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 11 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [5 empty] | X
3 | 2 | A | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X | [9 empty] | X |  |  | X | [5 empty] | X |  |  |  | X
| 3 | A |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  |  |  |  | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 10 | E | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | [7 empty] | X |  | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
4 | 5 | A | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 6 | A | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
| 9 | C - A | [7 empty] | X |  |  |  | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [8 empty] | X |  |  |  | X |  |  |  |  | X | [5 empty] | X
5 | 4 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [6 empty] | X |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
| 7 | A | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X | [5 empty] | X |  | X | X
|  | C | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | X |  |  |  |  | X |  |  | X | X
|  | C - A | X | [10 empty] | X |  |  | X |  |  |  | X | [7 empty] | X
|  | E |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
|  | G |  | X | [9 empty] | X |  |  | X |  |  |  | X | [5 empty] | X
6 | 12 | A | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X |  |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
| 13 | C - A | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | A |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C |  | X | X | X | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  |  | X
7 | 14 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G |  | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
8 | 16 | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | A | X | [5 empty] | X | X |  |  | X | X | X |  | X |  | X | X |  |  | X |  |  |  | X
|  | C | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E | X | [5 empty] | X |  |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | [5 empty] | X |  |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
9 | 19 | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | E | X | [5 empty] | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X | X |  | X |  | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
10 | 20 | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | A | X | X | X | X | X |  |  |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | C | X | X | X | X | X |  |  | X |  |  |  | X | X |  | X |  |  | X |  |  | X |  |  | X | X
|  | E |  |  |  |  | X |  | X |  | X |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | G | X | X |  |  | X |  | X | X | X |  | X | X |  |  | X |  | X |  |  |  | X |  |  |  | X
11 | 21 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
12 | 24 | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | A | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | C | X | X |  | X | X |  |  | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [6 empty] | X
|  | G | X | X |  | X | X |  | X | X |  |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
13 | 25 | A | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | C | X | X |  | X | X | X | X |  | X |  |  | X |  |  | X | [7 empty] | X | X | X
|  | E | X | X | [9 empty] | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | F | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  | X |  | X | X |  | X |  |  | X |  |  | X | [5 empty] | X |  |  | X | X
14 | 27 | A | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | C | X | X |  | X | X |  | X | X | X |  |  | X |  |  | X | [7 empty] | X |  | X
|  | E |  |  |  |  | X |  | X | X |  |  |  | X |  |  | X |  |  |  |  | X | [5 empty] | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | F | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X
|  | G | X | X |  |  | X |  | X | X | X |  |  | X |  |  | X | [5 empty] | X |  |  |  | X

## Shorting Summary
Shorting Sequence for Open Burn Test 10, Location C, IRMS #2
Test conditions: Cable: Bundle of 6, XLPE (12/C, 18 AWG), EPR (7/C, 12 AWG), PVC (12/C, 18 AWG), TS/TP (7/C, 12 AWG), SR (7/C, 12 AWG), & XLPO (7/C, 12 AWG) control and instrument cables (Items 13, 2, 6, 3, 9, & 8). Cable specimens present: Six lengths of cable were monitored for electrical performance (A, B, C, D, E, & F [See Elect. Conn. Map]), a second bundle of 6 cables was monitored for temperature response. Raceway: 12" B-Line Series 2 tray (part number 248P09-12-144) located at position C in the Test Cell chamber with chamber end walls open and un-heated. Exposure conditions: Gas burner flow rate set to a nominal 250 kW heat release rate and increased to ~350 kW during the test. Electrical repsonse monitoring: IRMS system using 12 channels - two for each cable (see electrical connection map), cable tray was grounded. Thermal response monitoring: Four cable bundle temperatures (see thermocouple map) and the cable tray rung temperature. Gas burner initiated: Following 174 seconds of baseline data monitoring. Special Note: This test included activation of the water sprinkler after the gas burner was shut off.
DAQ Time | Burner Time | Event | Interpretation
174 | 0 | Ignited Gas Burner
304-309 | 130-135 | Conductors D7 & D8 both short to ground at less than 100 ohms (20 & 14) | Cable D shorts to ground
328 | 154 | Conductors D7 & D8 short together at less than 100 ohms (37) | Cable D shorted internally
343-345 | 169-171 | Conductors F11 & F12 both short to ground at less than 100 ohms (33 & 17) | Cable F shorts to ground
367 | 193 | Conductors F11 & F12 short together at less than 100 ohms (57) | Cable F shorted internally
426-441 | 252-267 | Conductors B3 & B4 both short to ground at less than 100 ohms (18 & 4) | Cable B shorts to ground
464 | 290 | Conductor C6 shorts to ground at less than 1000 ohms (125)
477 | 303 | Conductors C5 & C6 short together at less than 100 ohms (72) | Cable C shorted internally
555 | 381 | Conductors A1 & A2 short together at less than 100 ohms (34) | Cable A shorted internally
560-583 | 386-409 | Conductors A1 & A2 both short to ground at less than 1000 ohms (105 & 183) | Cable A shorts to ground
614 | 440 | Conductors B3 & B4 short together at less than 100 ohms (1) | Cable B shorted internally
640-649 | 466-475 | Conductor C5 shorts to ground at less than 100 ohms (4) and the existing ground fault on conductor C6 decreases to less than 100 ohms (1) | Cable C shorts to ground
745-767 | 571-593 | The existing ground faults on conductors A1 & A2 decrease to less than 100 ohms (2 & 2)
1614 | 1440 | Gas burner is shut off
1615-1618 | 1441-1444 | Conductors E9 & E10 both short to ground at less than 100 ohms (18 & 1) | Cable E shorts to ground
1667 | 1493 | Water sprinkler activated
1763 | 1589 | Water sprinkler shut off
1832 | 1658 | Conductors E9 & E10 short together at less than 100 ohms (1) | Cable E shorted internally
Additional Observations
Observation 1 | No cable to cable interactions were observed during this test.

## Thermocouple Map
Thermocouple map for TC's on and within the cable
|  |  |  | Cable A = | XLPE (12/C) | (Item #13)
|  |  |  | Cable B = | EPR (7/C) | (Item #2)
|  |  |  | Cable C = | PVC (12/C) | (Item #6)
|  |  |  | Cable D = | TS/TP (7/C) | (Item #3)
|  |  |  | Cable E = | SR (7/C) | (Item #9)
|  |  |  | Cable F = | XLPO (7/C) | (Item #8)
Translation to data file names used in "PenTemps" WorkSheet:
| Map Name |  | Location
| C1 | = | Center of bundle, under jacket
| C2 | = | Air above bundle
| C3 | = | Air below bundle
| C4 | = | Intra-bundle, center

## Elect Conn Map
Electrical connection map within the cables
|  |  |  | Cable A = | XLPE (12/C) | (Item #13)
|  |  |  | Cable B = | EPR (7/C) | (Item #2)
|  |  |  | Cable C = | PVC (12/C) | (Item #6)
|  |  |  | Cable D = | TS/TP (7/C) | (Item #3)
|  |  |  | Cable E = | SR (7/C) | (Item #9)
|  |  |  | Cable F = | XLPO (7/C) | (Item #8)
Cable tray rung below D-E-F
Cable Bundle Arrangement
Cable 7-Conductor Arrangement
| Lt Blue = | Even conductor set
| Lt Red = | Odd conductor set
| Gray = | Center conductor (not connected)
IRMS Electrical Connections

## C-C Individuals
Conductor to Conductor Resistances
Open Burn Test 10 |  |  | 2006-11-16 | 8:44
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW
Burner Time | A1-A2 | Burner Time | A1-B3 | Burner Time | A1-B4 | Burner Time | A1-C5 | Burner Time | A1-C6 | Burner Time | A2-B3 | Burner Time | A2-B4 | Burner Time | A2-C5 | Burner Time | A2-C6 | Burner Time | B3-B4 | Burner Time | B3-C5 | Burner Time | B3-C6 | Burner Time | B3-D7 | Burner Time | B3-D8 | Burner Time | B3-E9 | Burner Time | B3-E10 | Burner Time | B4-C5 | Burner Time | B4-C6 | Burner Time | B4-D7 | Burner Time | B4-D8 | Burner Time | B4-E9 | Burner Time | B4-E10 | Burner Time | C5-C6 | Burner Time | C5-E9 | Burner Time | C5-E10 | Burner Time | C5-F11 | Burner Time | C5-F12 | Burner Time | C6-E9 | Burner Time | C6-E10 | Burner Time | C6-F11 | Burner Time | C6-F12 | Burner Time | D7-D8 | Burner Time | D7-E9 | Burner Time | D7-E10 | Burner Time | D8-E9 | Burner Time | D8-E10 | Burner Time | E9-E10 | Burner Time | E9-F11 | Burner Time | E9-F12 | Burner Time | E10-F11 | Burner Time | E10-F12 | Burner Time | F11-F12
-173.5 | 508175.9997 | -171 | 517975.9997 | -168 | 515175.9997 | -165.5 | 519175.9997 | -162.5 | 511575.9997 | -143 | 513975.9997 | -140 | 520975.9997 | -137.5 | 516775.9997 | -134.5 | 518975.9997 | -115 | 509775.9997 | -112 | 514175.9997 | -109.5 | 511175.9997 | -106.5 | 516175.9997 | -103.5 | 488975.9997 | -101 | 491175.9997 | -98 | 513575.9997 | -89.5 | 518975.9997 | -87 | 513975.9997 | -84 | 525375.9997 | -81.5 | 524375.9997 | -78.5 | 518375.9997 | -75.5 | 470175.9997 | -67.5 | 521775.9997 | -59 | 517575.9997 | -56 | 492775.9997 | -53.5 | 520975.9997 | -50.5 | 513175.9997 | -42 | 512775.9997 | -39.5 | 519975.9997 | -36.5 | 520775.9997 | -33.5 | 516775.9997 | -31 | 519175.9997 | -28 | 498775.9997 | -25.5 | 523775.9997 | -17 | 523375.9997 | -14 | 507375.9997 | -5.5 | 511575.9997 | -3 | 523375.9997 | 4.4145e-07 | 516975.9997 | 2.5 | 523975.9997 | 5.5 | 467975.9997 | 8.5 | 525975.9997
11 | 508175.9997 | 14 | 517975.9997 | 16.5 | 515175.9997 | 19.5 | 519175.9997 | 22.5 | 511575.9997 | 42 | 513975.9997 | 44.5 | 520975.9997 | 47.5 | 516775.9997 | 50.5 | 518975.9997 | 70 | 509775.9997 | 72.5 | 514175.9997 | 75.5 | 511175.9997 | 78.5 | 516175.9997 | 81 | 488975.9997 | 84 | 491175.9997 | 86.5 | 513575.9997 | 95 | 518975.9997 | 98 | 513975.9997 | 100.5 | 525375.9997 | 103.5 | 524375.9997 | 106.5 | 518375.9997 | 109 | 470175.9997 | 117.5 | 521775.9997 | 126 | 517575.9997 | 128.5 | 492775.9997 | 131.5 | 520975.9997 | 134.5 | 513175.9997 | 142.5 | 512775.9997 | 145.5 | 519975.9997 | 148.5 | 520775.9997 | 151 | 516775.9997 | 154 | 37.1801 | 156.5 | 68824.2014 | 159.5 | 44229.5556 | 168 | 59926.55 | 170.5 | 54027.3516 | 179 | 511575.9997 | 182 | 523375.9997 | 184.5 | 516975.9997 | 187.5 | 523975.9997 | 190.5 | 467975.9997 | 193 | 57.2513
196 | 508175.9997 | 198.5 | 517975.9997 | 201.5 | 515175.9997 | 204.5 | 519175.9997 | 207 | 511575.9997 | 226.5 | 513975.9997 | 229.5 | 520975.9997 | 232 | 516775.9997 | 235 | 518975.9997 | 254.5 | 162973.9931 | 257.5 | 232592.764 | 260.5 | 216895.5693 | 263 | 1007.7462 | 266 | 822.6231 | 268.5 | 37730.3184 | 271.5 | 48928.473 | 279.5 | 102818.1883 | 282.5 | 64125.5236 | 285.5 | 11.8328 | 288.5 | 19.8044 | 291 | 8436.3725 | 294 | 5336.8649 | 302.5 | 71.7982 | 310.5 | 517575.9997 | 313.5 | 492775.9997 | 316.5 | 65034.4976 | 319 | 51227.5969 | 327.5 | 187901.3561 | 330.5 | 170305.2475 | 333 | 123.8073 | 335.5 | 1411.2289 | 338.5 | 5.2743 | 341.5 | 13435.3063 | 344.5 | 57327.055 | 352.5 | 29632.3382 | 355.5 | 60326.1102 | 364 | 511575.9997 | 366.5 | 523375.9997 | 369.5 | 516975.9997 | 372 | 523975.9997 | 375 | 467975.9997 | 377.5 | 10.7866
380.5 | 34.4728 | 383.5 | 291.4845 | 386.5 | 135.6997 | 389 | 104.6381 | 391.5 | 174.8236 | 411.5 | 312.8646 | 414 | 182.3237 | 417 | 253.0941 | 419.5 | 182.4696 | 439.5 | 0.89973 | 442 | 8.7934 | 445 | 14.0072 | 447.5 | 0.037856 | 450.5 | 0.72796 | 453.5 | 27732.3539 | 456.5 | 1537.7006 | 464.5 | 28.8763 | 467.5 | 20.8819 | 470 | 16.1385 | 473 | 15.6502 | 475.5 | 3337.3562 | 478.5 | 35830.3794 | 487 | 1050.3068 | 495.5 | 29732.2555 | 498 | 11735.6185 | 501 | 2.2676 | 503.5 | 28.2743 | 512 | 1537.7001 | 515 | 42429.84 | 518 | 31.5433 | 520.5 | 12.1597 | 523.5 | 25.6512 | 526.5 | 20333.9232 | 529 | 4537.1338 | 537.5 | 12935.5284 | 540.5 | 51227.9034 | 548.5 | 511575.9997 | 551.5 | 523375.9997 | 554.5 | 516975.9997 | 557 | 523975.9997 | 560 | 467975.9997 | 562.5 | 26.2432
565.5 | 837.7584 | 568.5 | 4.0593 | 571 | 30.7268 | 573.5 | 2.965 | 576.5 | 23.4246 | 596 | 25.3174 | 599 | 5.8233 | 601.5 | 0.19657 | 604.5 | 11.9373 | 624 | 1.9608 | 627 | 0.91873 | 629.5 | 0.46131 | 632.5 | 25.0427 | 635.5 | 22.9283 | 638 | 36830.5016 | 641 | 61226.0785 | 649.5 | 30.0717 | 652 | 19.3748 | 655 | 26.5357 | 657.5 | 13.0152 | 660.5 | 16634.791 | 663.5 | 1537.673 | 671.5 | 26.1608 | 680 | 45129.2806 | 683 | 10235.9228 | 685.5 | 20.2107 | 688.5 | 4.6158 | 697 | 32831.5973 | 699.5 | 2237.5697 | 702.5 | 22.8555 | 705.5 | 8.2081 | 708 | 0.18103 | 711 | 16034.7852 | 713.5 | 24433.3352 | 722 | 1537.7062 | 725 | 10535.9234 | 733.5 | 511575.9997 | 736 | 523375.9997 | 739 | 516975.9997 | 741.5 | 523975.9997 | 744.5 | 467975.9997 | 747.5 | 5.6893
750.5 | 7.2245 | 753 | 23.7534 | 755.5 | 0.92304 | 758.5 | 24.1652 | 761.5 | 0.31276 | 781 | 29.6757 | 784 | 27.6172 | 786.5 | 4.604 | 789.5 | 26.0421 | 809 | 0.086516 | 811.5 | 19.3072 | 814.5 | 22.9603 | 817.5 | 0.69136 | 820 | 10.1182 | 823 | 47728.2829 | 825.5 | 20733.9628 | 834 | 0.71138 | 837 | 25.7594 | 839.5 | 1.6421 | 842.5 | 30.4295 | 845.5 | 41829.9306 | 848 | 29831.6552 | 856.5 | 31.457 | 865 | 41429.9954 | 867.5 | 40629.7549 | 870.5 | 8.4848 | 873.5 | 0.18797 | 881.5 | 10835.8868 | 884.5 | 1537.7043 | 887.5 | 20.3361 | 890 | 26.6425 | 893 | 0.019373 | 895.5 | 9536.0881 | 898.5 | 51028.2576 | 907 | 52627.9445 | 909.5 | 47928.5536 | 918 | 511575.9997 | 921 | 523375.9997 | 923.5 | 516975.9997 | 926.5 | 523975.9997 | 929.5 | 467975.9997 | 932 | 0.10171
935 | 12.7572 | 937.5 | 30.6263 | 940.5 | 25.1103 | 943.5 | 25.1521 | 946 | 0.60163 | 965.5 | 4.426 | 968.5 | 0.45253 | 971.5 | 16.3994 | 974 | 0.46654 | 993.5 | 8.7111 | 996.5 | 2.0859 | 999.5 | 19.5778 | 1002 | 15.6696 | 1005 | 18.9237 | 1007.5 | 29531.9875 | 1010.5 | 43429.5437 | 1019 | 18.7254 | 1021.5 | 22.5467 | 1024.5 | 30.4137 | 1027.5 | 12.312 | 1030 | 15634.9839 | 1033 | 32930.996 | 1041.5 | 28.9851 | 1049.5 | 50328.2762 | 1052.5 | 45128.8419 | 1055.5 | 26.5325 | 1058 | 1.9267 | 1066.5 | 51627.9317 | 1069.5 | 12135.6661 | 1072 | 26.4835 | 1075 | 24.1977 | 1077.5 | 3.3503 | 1080.5 | 46228.7316 | 1083.5 | 35231.2736 | 1091.5 | 15734.9936 | 1094.5 | 19634.1303 | 1103 | 511575.9997 | 1105.5 | 523375.9997 | 1108.5 | 516975.9997 | 1111.5 | 523975.9997 | 1114 | 467975.9997 | 1117 | 16.2195
1119.5 | 25.4643 | 1122.5 | 3.9286 | 1125.5 | 27.4032 | 1128 | 7.8247 | 1131 | 22.5712 | 1150.5 | 15.0642 | 1153.5 | 4.5829 | 1156 | 6.0357 | 1159 | 0.93935 | 1178.5 | 1.2835 | 1181.5 | 16.3494 | 1184 | 0.90579 | 1187 | 13.9769 | 1189.5 | 20.3114 | 1192.5 | 23733.1681 | 1195.5 | 52827.7137 | 1203.5 | 22.5458 | 1206.5 | 22.7881 | 1209.5 | 25.9732 | 1212 | 16.6624 | 1215 | 50828.1947 | 1217.5 | 5236.8862 | 1226 | 0.95133 | 1234.5 | 17934.5349 | 1237.5 | 6736.6329 | 1240 | 0.94791 | 1243 | 12.0753 | 1251.5 | 22633.5861 | 1254 | 52627.8788 | 1257 | 1.9767 | 1259.5 | 0.92992 | 1262.5 | 16.8372 | 1265.5 | 8436.3086 | 1268 | 11435.8167 | 1276.5 | 46029.2053 | 1279.5 | 54327.2925 | 1287.5 | 511575.9997 | 1290.5 | 523375.9997 | 1293.5 | 516975.9997 | 1296 | 523975.9997 | 1299 | 467975.9997 | 1301.5 | 11.0782
1304.5 | 0.8928 | 1307.5 | 8.9846 | 1310 | 1.3202 | 1313 | 0.94021 | 1315.5 | 5.5861 | 1335.5 | 21.8874 | 1338 | 13.6964 | 1341 | 2.1435 | 1343.5 | 8.5802 | 1363.5 | 24.2211 | 1366 | 7.6565 | 1368.5 | 28.9629 | 1371.5 | 2.4888 | 1374.5 | 19.7042 | 1377.5 | 1537.6869 | 1380 | 8736.2989 | 1388.5 | 13.3573 | 1391.5 | 0.2148 | 1394 | 29.554 | 1397 | 8.0781 | 1399.5 | 1537.7034 | 1402.5 | 8836.1207 | 1411 | 22.9741 | 1419.5 | 29032.3907 | 1422 | 26832.5548 | 1425 | 27.9397 | 1427.5 | 11.6706 | 1436 | 34531.2658 | 1439 | 43929.5516 | 1441.5 | 0.94705 | 1444.5 | 4.5157 | 1447 | 8.3397 | 1450 | 16134.7651 | 1453 | 60626.4251 | 1461 | 46329.148 | 1464 | 1537.6969 | 1472.5 | 255737.9994 | 1475 | 841.3339 | 1478 | 16.4992 | 1480.5 | 6.8028 | 1483.5 | 0.31698 | 1486.5 | 19.3847
1489 | 5449.127 | 1492 | 18.8313 | 1494.5 | 27.1444 | 1497.5 | 33.4195 | 1500.5 | 16.4083 | 1520 | 18.1838 | 1522.5 | 12.8284 | 1525.5 | 13.2814 | 1528.5 | 31.0166 | 1548 | 982.7284 | 1550.5 | 4.8225 | 1553.5 | 31.3459 | 1556.5 | 23.0161 | 1559 | 0.80855 | 1562 | 9.9011 | 1565 | 32.1074 | 1573.5 | 36.0946 | 1576 | 24.8785 | 1578.5 | 4.2557 | 1581.5 | 30.2962 | 1584.5 | 8.3587 | 1587 | 20.9744 | 1595.5 | 3.6169 | 1604 | 0.93335 | 1606.5 | 2.7583 | 1609.5 | 0.86889 | 1612.5 | 21.3395 | 1621 | 27.7793 | 1623.5 | 0.78517 | 1626.5 | 0.82031 | 1629 | 7.3197 | 1632 | 0.94021 | 1634.5 | 2.2919 | 1637.5 | 0.95986 | 1646 | 26.994 | 1648.5 | 0.84878 | 1657.5 | 0.90752 | 1660 | 23.7159 | 1662.5 | 25.4889 | 1665.5 | 32.7031 | 1668.5 | 4.2117 | 1671 | 33.214
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## C-G Min
Minimum Conductor to Ground Resistances
Open Burn Test 10 |  |  | 2006-11-16 | 8:44
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW
Burner Time | A1-G |  | Burner Time | A2-G | Burner Time | B3-G | Burner Time | B4-G | Burner Time | C5-G | Burner Time | C6-G | Burner Time | D7-G | Burner Time | D8-G | Burner Time | E9-G | Burner Time | E10-G | Burner Time | F11-G | Burner Time | F12-G
-168.1 | 508176 |  | -145.7 | 508176 | -117.7222 | 488976 | -102.1111 | 470176 | -87.8889 | 492776 | -79.1667 | 511176 | -55 | 498776 | -49.4 | 488976 | -37.1111 | 491176 | -34 | 467976 | -16.4 | 520776 | -14 | 467976
16.7 | 508176 |  | 39.1 | 508176 | 67.1111 | 488976 | 82.6111 | 470176 | 96.9444 | 492776 | 105.7222 | 511176 | 129.8 | 20.3853 | 135.4 | 13.8264 | 147.6667 | 491176 | 150.7222 | 467976 | 168.5 | 33.2678 | 170.7 | 17.1361
201.5 | 508176 |  | 223.8 | 508176 | 251.8333 | 18.2176 | 267.3889 | 2.3685 | 281.7222 | 2522.2279 | 290.4444 | 124.5155 | 314.6 | 5.7413 | 320.2 | 8.2286 | 332.3889 | 491176.0003 | 335.6111 | 467976 | 353.1 | 2.3186 | 355.3 | 0.64235
386.2 | 105.4098 |  | 408.5 | 182.886 | 436.6111 | 0.6421 | 452.1111 | 1.3445 | 466.3889 | 3.8 | 475.1111 | 0.64311 | 499.3 | 1.8033 | 505 | 1.8908 | 517.2222 | 491176.0012 | 520.3333 | 467976 | 538 | 5.7808 | 540.2 | 0.6376
571 | 1.904 |  | 593.3 | 1.7472 | 621.3333 | 0.6411 | 636.8889 | 0.7018 | 651.1111 | 3.0719 | 659.8333 | 0.64135 | 684 | 1.739 | 689.6 | 0.63 | 701.8889 | 491175.9994 | 705 | 467976 | 722.6 | 7.1874 | 725 | 7.3077
755.8 | 0.63984 |  | 778.3 | 0.88845 | 806.1111 | 0.64135 | 821.6667 | 2.2608 | 835.9444 | 1.3578 | 844.7222 | 0.63415 | 868.8 | 1.5798 | 874.4 | 11.5906 | 886.6667 | 491176.0003 | 889.7222 | 467976 | 907.5 | 0.62903 | 909.7 | 2.9191
940.5 | 2.1309 |  | 962.9 | 2.0117 | 990.8333 | 0.63636 | 1006.4444 | 1.5689 | 1020.8333 | 3.4414 | 1029.5 | 1.1056 | 1053.6 | 0.62735 | 1059.2 | 0.62855 | 1071.3889 | 491176.0003 | 1074.6667 | 467976 | 1092.3 | 1.8921 | 1094.5 | 0.62663
1125.3 | 5.4286 |  | 1147.7 | 0.63513 | 1175.7222 | 0.64488 | 1191.2778 | 0.63268 | 1205.5556 | 0.6317 | 1214.2778 | 0.63785 | 1238.5 | 3.5457 | 1244 | 7.9576 | 1256.3333 | 491175.9994 | 1259.3889 | 467976 | 1277 | 0.62976 | 1279.3 | 2.0024
1310.1 | 0.63488 |  | 1332.5 | 3.6655 | 1360.5 | 0.67159 | 1376.0556 | 0.63612 | 1390.3889 | 11.8478 | 1399 | 0.63292 | 1423.1 | 6.9661 | 1428.7 | 0.65 | 1441 | 17.8387 | 1444.1111 | 1.0963 | 1461.7 | 19.7067 | 1464 | 4.5866
1494.7 | 17.7349 |  | 1517.1 | 10.1118 | 1545.1667 | 0.67435 | 1560.6667 | 5.7721 | 1575 | 0.63686 | 1583.7778 | 0.78992 | 1607.8 | 0.62927 | 1613.4 | 0.68968 | 1625.7778 | 0.64437 | 1628.8333 | 0.66912 | 1646.5 | 3.4702 | 1648.7 | 1.0704
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## F11-F12
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 160.5849 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 11 & 12 | Cable F | Odd -Even
Time-131 | N11 | N12 | Time-132 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R11-G | R12-G | R11-12
39037.3613 | 0 | 0 | 39037.3613 | 0 | 0 |  | 8.5 | 182.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525976 | 525976 | 525975.9997
39037.3634 | 1662 | 0 | 39037.3634 | 1574 | 0 |  | 193 | 367 | 101.4652 | 0 | 96.0928 | 0 | 1.0147 | 0 | 0.96093 | 0 | 1.0147 | 0.96093 | 58.2659 | 67.1144 | 57.2513
39037.3656 | 2344 | 0 | 39037.3656 | 2440 | 0 |  | 377.5 | 551.5 | 143.1013 | 0 | 148.9621 | 0 | 1.431 | 0 | 1.4896 | 0 | 1.431 | 1.4896 | 12.2176 | 7.8025 | 10.7866
39037.3677 | 2063 | 0 | 39037.3677 | 2027 | 0 |  | 562.5 | 736.5 | 125.9463 | 0 | 123.7485 | 0 | 1.2595 | 0 | 1.2375 | 0 | 1.2595 | 1.2375 | 27.5027 | 29.7671 | 26.2432
39037.3698 | 2454 | 0 | 39037.3699 | 2045 | 0 |  | 747.5 | 921.5 | 149.8168 | 0 | 124.8474 | 0 | 1.4982 | 0 | 1.2485 | 0 | 1.4982 | 1.2485 | 7.1874 | 28.6249 | 5.6893
39037.372 | 2592 | 0 | 39037.372 | 2530 | 0 |  | 932 | 1106 | 158.2418 | 0 | 154.4567 | 0 | 1.5824 | 0 | 1.5446 | 0 | 1.5824 | 1.5446 | 1.4807 | 3.9676 | 0.10171
39037.3741 | 2237 | 0 | 39037.3741 | 2614 | 0 |  | 1117 | 1291 | 136.569 | 0 | 159.5849 | 0 | 1.3657 | 0 | 1.5958 | 0 | 1.3657 | 1.5958 | 17.5852 | 0.62663 | 16.2195
39037.3763 | 2338 | 0 | 39037.3763 | 2259 | 0 |  | 1301.5 | 1475.5 | 142.735 | 0 | 137.9121 | 0 | 1.4274 | 0 | 1.3791 | 0 | 1.4274 | 1.3791 | 12.5056 | 16.44 | 11.0782
39037.3784 | 2179 | 0 | 39037.3784 | 2379 | 0 |  | 1486.5 | 1660.5 | 133.0281 | 0 | 145.2381 | 0 | 1.3303 | 0 | 1.4524 | 0 | 1.3303 | 1.4524 | 20.715 | 10.5666 | 19.3847
39037.3805 | 1957 | 0 | 39037.3806 | 2102 | 0 |  | 1671 | 1845 | 119.475 | 0 | 128.3272 | 0 | 1.1947 | 0 | 1.2833 | 0 | 1.1947 | 1.2833 | 34.4088 | 25.137 | 33.214

## E10-F12
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 142.8803 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 10 & 12 | Cable E | Even - | Cable F |  | Even
Time-129 | N11 | N12 | Time-130 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R12-G | R10-12
39037.3613 | 0 | 0 | 39037.3613 | 0 | 0 |  | 5.5 | 179.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 467976 | 467976 | 467975.9997
39037.3634 | 0 | 0 | 39037.3634 | 1998 | 0 |  | 190.5 | 364.5 | 0.030525 | 0 | 121.978 | 0 | 0.00030525 | 0 | 1.2198 | 0 | 0.00030525 | 1.2198 | 467976 | 17.1361 | 467975.9997
39037.3655 | 0 | 0 | 39037.3656 | 2282 | 0 |  | 375 | 549 | 0.030525 | 0 | 139.3162 | 0 | 0.00030525 | 0 | 1.3932 | 0 | 0.00030525 | 1.3932 | 467976 | 2.5583 | 467975.9997
39037.3677 | 0 | 0 | 39037.3677 | 2324 | 0 |  | 560 | 734 | 0.030525 | 0 | 141.8803 | 0 | 0.00030525 | 0 | 1.4188 | 0 | 0.00030525 | 1.4188 | 467976 | 0.70482 | 467975.9997
39037.3698 | 0 | 0 | 39037.3698 | 2181 | 0 |  | 744.5 | 918.5 | 0.030525 | 0 | 133.1502 | 0 | 0.00030525 | 0 | 1.3315 | 0 | 0.00030525 | 1.3315 | 467976 | 7.3077 | 467975.9997
39037.372 | 0 | 0 | 39037.372 | 2274 | 0 |  | 929.5 | 1103.5 | 0.030525 | 0 | 138.8278 | 0 | 0.00030525 | 0 | 1.3883 | 0 | 0.00030525 | 1.3883 | 467976 | 2.9191 | 467975.9997
39037.3741 | 0 | 0 | 39037.3741 | 2287 | 0 |  | 1114 | 1288 | 0.030525 | 0 | 139.6215 | 0 | 0.00030525 | 0 | 1.3962 | 0 | 0.00030525 | 1.3962 | 467976 | 2.3341 | 467975.9997
39037.3762 | 0 | 0 | 39037.3763 | 2026 | 0 |  | 1299 | 1473 | 0.030525 | 0 | 123.6874 | 0 | 0.00030525 | 0 | 1.2369 | 0 | 0.00030525 | 1.2369 | 467976 | 15.5173 | 467975.9997
39037.3784 | 2315 | 0 | 39037.3784 | 2119 | 0 |  | 1483.5 | 1657.5 | 141.3309 | 0 | 129.3651 | 0 | 1.4133 | 0 | 1.2937 | 0 | 1.4133 | 1.2937 | 1.0963 | 10.4474 | 0.31698
39037.3805 | 2217 | 0 | 39037.3805 | 1956 | 0 |  | 1668.5 | 1842.5 | 135.348 | 0 | 119.4139 | 0 | 1.3535 | 0 | 1.1941 | 0 | 1.3535 | 1.1941 | 5.5652 | 19.6513 | 4.2117

## E10-F11
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.9744 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 10 & 11 | Cable E | Even - | Cable F |  | Odd
Time-127 | N11 | N12 | Time-128 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R10-G | R11-G | R10-11
39037.3612 | 0 | 0 | 39037.3612 | 0 | 0 |  | 2.5 | 176.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523976 | 523976 | 523975.9997
39037.3634 | 0 | 0 | 39037.3634 | 1728 | 0 |  | 187.5 | 361.5 | 0.030525 | 0 | 105.4945 | 0 | 0.00030525 | 0 | 1.0549 | 0 | 0.00030525 | 1.0549 | 523976 | 51.6424 | 523975.9997
39037.3655 | 0 | 0 | 39037.3655 | 2561 | 0 |  | 372 | 546 | 0.030525 | 0 | 156.3492 | 0 | 0.00030525 | 0 | 1.5635 | 0 | 0.00030525 | 1.5635 | 523976 | 2.3186 | 523975.9997
39037.3676 | 0 | 0 | 39037.3677 | 2261 | 0 |  | 557 | 731 | 0.030525 | 0 | 138.0342 | 0 | 0.00030525 | 0 | 1.3803 | 0 | 0.00030525 | 1.3803 | 523976 | 15.8947 | 523975.9997
39037.3698 | 0 | 0 | 39037.3698 | 2314 | 0 |  | 741.5 | 915.5 | 0.030525 | 0 | 141.2698 | 0 | 0.00030525 | 0 | 1.4127 | 0 | 0.00030525 | 1.4127 | 523976 | 13.2403 | 523975.9997
39037.3719 | 0 | 0 | 39037.3719 | 2604 | 0 |  | 926.5 | 1100.5 | 0.030525 | 0 | 158.9744 | 0 | 0.00030525 | 0 | 1.5897 | 0 | 0.00030525 | 1.5897 | 523976 | 0.62903 | 523975.9997
39037.3741 | 0 | 0 | 39037.3741 | 2151 | 0 |  | 1111.5 | 1285.5 | 0.030525 | 0 | 131.3187 | 0 | 0.00030525 | 0 | 1.3132 | 0 | 0.00030525 | 1.3132 | 523976 | 21.8215 | 523975.9997
39037.3762 | 0 | 0 | 39037.3762 | 2101 | 0 |  | 1296 | 1470 | 0.030525 | 0 | 128.2662 | 0 | 0.00030525 | 0 | 1.2827 | 0 | 0.00030525 | 1.2827 | 523976 | 24.7206 | 523975.9997
39037.3783 | 2420 | 0 | 39037.3783 | 2189 | 0 |  | 1480.5 | 1654.5 | 147.7411 | 0 | 133.6386 | 0 | 1.4774 | 0 | 1.3364 | 0 | 1.4774 | 1.3364 | 8.2802 | 19.7067 | 6.8028
39037.3805 | 1957 | 0 | 39037.3805 | 1995 | 0 |  | 1665.5 | 1839.5 | 119.475 | 0 | 121.7949 | 0 | 1.1947 | 0 | 1.2179 | 0 | 1.1947 | 1.2179 | 33.8978 | 31.3474 | 32.7031

## E9-F12
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 157.8376 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 9 & 12 | Cable E | Odd - | Cable F |  | Even
Time-125 | N11 | N12 | Time-126 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R12-G | R9-12
39037.3612 | 0 | 0 | 39037.3612 | 0 | 0 |  | 4.4145e-07 | 174 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516976 | 516976 | 516975.9997
39037.3633 | 0 | 0 | 39037.3633 | 4 | 0 |  | 184.5 | 358.5 | 0.030525 | 0 | 0.2442 | 0 | 0.00030525 | 0 | 0.002442 | 0 | 0.00030525 | 0.002442 | 516976 | 64534.5 | 516975.9997
39037.3655 | 0 | 0 | 39037.3655 | 2224 | 0 |  | 369.5 | 543.5 | 0.030525 | 0 | 135.7753 | 0 | 0.00030525 | 0 | 1.3578 | 0 | 0.00030525 | 1.3578 | 516976 | 16.2491 | 516975.9997
39037.3676 | 0 | 0 | 39037.3676 | 2569 | 0 |  | 554.5 | 728.5 | 0.030525 | 0 | 156.8376 | 0 | 0.00030525 | 0 | 1.5684 | 0 | 0.00030525 | 1.5684 | 516976 | 0.6376 | 516975.9997
39037.3697 | 0 | 0 | 39037.3698 | 2010 | 0 |  | 739 | 913 | 0.030525 | 0 | 122.7106 | 0 | 0.00030525 | 0 | 1.2271 | 0 | 0.00030525 | 1.2271 | 516976 | 28.6259 | 516975.9997
39037.3719 | 0 | 0 | 39037.3719 | 2339 | 0 |  | 923.5 | 1097.5 | 0.030525 | 0 | 142.7961 | 0 | 0.00030525 | 0 | 1.428 | 0 | 0.00030525 | 1.428 | 516976 | 10.5336 | 516975.9997
39037.374 | 0 | 0 | 39037.374 | 2350 | 0 |  | 1108.5 | 1282.5 | 0.030525 | 0 | 143.4676 | 0 | 0.00030525 | 0 | 1.4347 | 0 | 0.00030525 | 1.4347 | 516976 | 10.0162 | 516975.9997
39037.3762 | 0 | 0 | 39037.3762 | 2238 | 0 |  | 1293.5 | 1467.5 | 0.030525 | 0 | 136.63 | 0 | 0.00030525 | 0 | 1.3663 | 0 | 0.00030525 | 1.3663 | 516976 | 15.5219 | 516975.9997
39037.3783 | 2194 | 0 | 39037.3783 | 2472 | 0 |  | 1478 | 1652 | 133.9438 | 0 | 150.9158 | 0 | 1.3394 | 0 | 1.5092 | 0 | 1.3394 | 1.5092 | 17.8387 | 4.5866 | 16.4992
39037.3804 | 2040 | 0 | 39037.3805 | 2558 | 0 |  | 1662.5 | 1836.5 | 124.5421 | 0 | 156.1661 | 0 | 1.2454 | 0 | 1.5617 | 0 | 1.2454 | 1.5617 | 26.7343 | 1.0704 | 25.4889

## E9-F11
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.7912 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 9 & 11 | Cable E | Odd - | Cable F |  | Odd
Time-123 | N11 | N12 | Time-124 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R11-G | R9-11
39037.3612 | 0 | 0 | 39037.3612 | 0 | 0 |  | -3 | 171 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523376 | 523376 | 523375.9997
39037.3633 | 0 | 0 | 39037.3633 | 1964 | 0 |  | 182 | 356 | 0.030525 | 0 | 119.9023 | 0 | 0.00030525 | 0 | 1.199 | 0 | 0.00030525 | 1.199 | 523376 | 33.2678 | 523375.9997
39037.3654 | 0 | 0 | 39037.3655 | 2376 | 0 |  | 366.5 | 540.5 | 0.030525 | 0 | 145.0549 | 0 | 0.00030525 | 0 | 1.4505 | 0 | 0.00030525 | 1.4505 | 523376 | 10.1591 | 523375.9997
39037.3676 | 0 | 0 | 39037.3676 | 2223 | 0 |  | 551.5 | 725.5 | 0.030525 | 0 | 135.7143 | 0 | 0.00030525 | 0 | 1.3571 | 0 | 0.00030525 | 1.3571 | 523376 | 17.7409 | 523375.9997
39037.3697 | 0 | 0 | 39037.3697 | 2268 | 0 |  | 736 | 910 | 0.030525 | 0 | 138.4615 | 0 | 0.00030525 | 0 | 1.3846 | 0 | 0.00030525 | 1.3846 | 523376 | 15.4048 | 523375.9997
39037.3719 | 0 | 0 | 39037.3719 | 2073 | 0 |  | 921 | 1095 | 0.030525 | 0 | 126.5568 | 0 | 0.00030525 | 0 | 1.2656 | 0 | 0.00030525 | 1.2656 | 523376 | 26.2605 | 523375.9997
39037.374 | 0 | 0 | 39037.374 | 2387 | 0 |  | 1105.5 | 1279.5 | 0.030525 | 0 | 145.7265 | 0 | 0.00030525 | 0 | 1.4573 | 0 | 0.00030525 | 1.4573 | 523376 | 9.6514 | 523375.9997
39037.3761 | 0 | 0 | 39037.3761 | 2601 | 0 |  | 1290.5 | 1464.5 | 0.030525 | 0 | 158.7912 | 0 | 0.00030525 | 0 | 1.5879 | 0 | 0.00030525 | 1.5879 | 523376 | 0.62976 | 523375.9997
39037.3783 | 278 | 0 | 39037.3783 | 2103 | 0 |  | 1475 | 1649 | 16.9719 | 0 | 128.3883 | 0 | 0.16972 | 0 | 1.2839 | 0 | 0.16972 | 1.2839 | 841.5036 | 24.4593 | 841.3339
39037.3804 | 2094 | 0 | 39037.3804 | 2148 | 0 |  | 1660 | 1834 | 127.8388 | 0 | 131.1355 | 0 | 1.2784 | 0 | 1.3114 | 0 | 1.2784 | 1.3114 | 24.9943 | 21.852 | 23.7159

## E9-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.1893 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 9 & 10 | Cable E | Odd -Even
Time-121 | N11 | N12 | Time-122 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R9-G | R10-G | R9-10
39037.3611 | 0 | 0 | 39037.3611 | 0 | 0 |  | -5.5 | 168.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3633 | 0 | 0 | 39037.3633 | 0 | 0 |  | 179 | 353 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3654 | 0 | 0 | 39037.3654 | 0 | 0 |  | 364 | 538 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3675 | 0 | 0 | 39037.3676 | 0 | 0 |  | 548.5 | 722.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3697 | 0 | 0 | 39037.3697 | 0 | 0 |  | 733.5 | 907.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3718 | 0 | 0 | 39037.3718 | 0 | 0 |  | 918 | 1092 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.374 | 0 | 0 | 39037.374 | 0 | 0 |  | 1103 | 1277 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3761 | 0 | 0 | 39037.3761 | 0 | 0 |  | 1287.5 | 1461.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3782 | 1 | 0 | 39037.3783 | 201 | 0 |  | 1472.5 | 1646.5 | 0.06105 | 0 | 12.2711 | 0 | 0.0006105 | 0 | 0.12271 | 0 | 0.0006105 | 0.12271 | 255738 | 1172.8259 | 255737.9994
39037.3804 | 2542 | 0 | 39037.3804 | 2484 | 0 |  | 1657.5 | 1831.5 | 155.1893 | 0 | 151.6484 | 0 | 1.5519 | 0 | 1.5165 | 0 | 1.5519 | 1.5165 | 0.64437 | 2.9944 | 0.90752

## D8-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 154.9072 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 8 & 10 | Cable D | Even - | Cable E |  | Even
Time-115 | N11 | N12 | Time-116 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R10-G | R8-10
39037.361 | 0 | 0 | 39037.3611 | 0 | 0 |  | -14 | 160 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 507376 | 507376 | 507375.9997
39037.3632 | 1996 | 1 | 39037.3632 | 0 | 0 |  | 170.5 | 344.5 | 121.8559 | 0.06105 | 0.030525 | 0 | 1.2186 | 0.0006105 | 0.00030525 | 0 | 1.2179 | 0.00030525 | 27.1368 | 507375.9994 | 54027.3516
39037.3653 | 1933 | 1 | 39037.3653 | 0 | 0 |  | 355.5 | 529.5 | 118.0098 | 0.06105 | 0.030525 | 0 | 1.1801 | 0.0006105 | 0.00030525 | 0 | 1.1795 | 0.00030525 | 31.2826 | 507375.9994 | 60326.1102
39037.3675 | 2024 | 1 | 39037.3675 | 0 | 0 |  | 540.5 | 714.5 | 123.5653 | 0.06105 | 0.030525 | 0 | 1.2357 | 0.0006105 | 0.00030525 | 0 | 1.235 | 0.00030525 | 25.3772 | 507376.0004 | 51227.9034
39037.3696 | 2431 | 1 | 39037.3696 | 0 | 0 |  | 725 | 899 | 148.4127 | 0.06105 | 0.030525 | 0 | 1.4841 | 0.0006105 | 0.00030525 | 0 | 1.4835 | 0.00030525 | 4.3778 | 507376.0004 | 10535.9234
39037.3717 | 2057 | 1 | 39037.3717 | 0 | 0 |  | 909.5 | 1083.5 | 125.58 | 0.06105 | 0.030525 | 0 | 1.2558 | 0.0006105 | 0.00030525 | 0 | 1.2552 | 0.00030525 | 23.3648 | 507376.0004 | 47928.5536
39037.3739 | 2340 | 1 | 39037.3739 | 0 | 0 |  | 1094.5 | 1268.5 | 142.8571 | 0.06105 | 0.030525 | 0 | 1.4286 | 0.0006105 | 0.00030525 | 0 | 1.428 | 0.00030525 | 8.4386 | 507376.0004 | 19634.1303
39037.376 | 1993 | 1 | 39037.376 | 0 | 0 |  | 1279.5 | 1453.5 | 121.6728 | 0.06105 | 0.030525 | 0 | 1.2167 | 0.0006105 | 0.00030525 | 0 | 1.2161 | 0.00030525 | 27.3283 | 507376.0004 | 54327.2925
39037.3781 | 2521 | 1 | 39037.3782 | 0 | 0 |  | 1464 | 1638 | 153.9072 | 0.06105 | 0.030525 | 0 | 1.5391 | 0.0006105 | 0.00030525 | 0 | 1.5385 | 0.00030525 | 0.65 | 507376.0004 | 1537.6969
39037.3803 | 2520 | 0 | 39037.3803 | 2019 | 0 |  | 1648.5 | 1822.5 | 153.8462 | 0 | 123.2601 | 0 | 1.5385 | 0 | 1.2326 | 0 | 1.5385 | 1.2326 | 0.68968 | 25.6751 | 0.84878

## D8-E9
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.7912 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 8 & 9 | Cable D | Even - | Cable E |  | Odd
Time-113 | N11 | N12 | Time-114 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R8-G | R9-G | R8-9
39037.361 | 0 | 0 | 39037.361 | 0 | 0 |  | -17 | 157 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523376 | 523376 | 523375.9997
39037.3631 | 2017 | 1 | 39037.3632 | 0 | 0 |  | 168 | 342 | 123.138 | 0.06105 | 0.030525 | 0 | 1.2314 | 0.0006105 | 0.00030525 | 0 | 1.2308 | 0.00030525 | 29.7808 | 523376.0005 | 59926.55
39037.3653 | 2320 | 1 | 39037.3653 | 0 | 0 |  | 352.5 | 526.5 | 141.6361 | 0.06105 | 0.030525 | 0 | 1.4164 | 0.0006105 | 0.00030525 | 0 | 1.4158 | 0.00030525 | 12.8236 | 523375.9995 | 29632.3382
39037.3674 | 2487 | 1 | 39037.3674 | 0 | 0 |  | 537.5 | 711.5 | 151.8315 | 0.06105 | 0.030525 | 0 | 1.5183 | 0.0006105 | 0.00030525 | 0 | 1.5177 | 0.00030525 | 5.2446 | 523376.0005 | 12935.5284
39037.3695 | 2601 | 1 | 39037.3696 | 0 | 0 |  | 722 | 896 | 158.7912 | 0.06105 | 0.030525 | 0 | 1.5879 | 0.0006105 | 0.00030525 | 0 | 1.5873 | 0.00030525 | 0.63 | 523376.0005 | 1537.7062
39037.3717 | 2090 | 1 | 39037.3717 | 0 | 0 |  | 907 | 1081 | 127.5946 | 0.06105 | 0.030525 | 0 | 1.2759 | 0.0006105 | 0.00030525 | 0 | 1.2753 | 0.00030525 | 25.2456 | 523376.0005 | 52627.9445
39037.3738 | 2459 | 1 | 39037.3738 | 0 | 0 |  | 1091.5 | 1265.5 | 150.1221 | 0.06105 | 0.030525 | 0 | 1.5012 | 0.0006105 | 0.00030525 | 0 | 1.5006 | 0.00030525 | 6.4435 | 523376.0005 | 15734.9936
39037.376 | 2156 | 1 | 39037.376 | 0 | 0 |  | 1276.5 | 1450.5 | 131.6239 | 0.06105 | 0.030525 | 0 | 1.3162 | 0.0006105 | 0.00030525 | 0 | 1.3156 | 0.00030525 | 21.4097 | 523375.9995 | 46029.2053
39037.3781 | 2153 | 1 | 39037.3781 | 0 | 0 |  | 1461 | 1635 | 131.4408 | 0.06105 | 0.030525 | 0 | 1.3144 | 0.0006105 | 0.00030525 | 0 | 1.3138 | 0.00030525 | 21.579 | 523375.9995 | 46329.148
39037.3802 | 2041 | 0 | 39037.3803 | 2215 | 0 |  | 1646 | 1820 | 124.6032 | 0 | 135.2259 | 0 | 1.246 | 0 | 1.3523 | 0 | 1.246 | 1.3523 | 28.2401 | 18.1661 | 26.994

## D7-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.9133 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 7 & 10 | Cable D | Odd - | Cable E |  | Even
Time-107 | N11 | N12 | Time-108 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R10-G | R7-10
39037.3609 | 0 | 0 | 39037.3609 | 0 | 0 |  | -25.5 | 148.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 523776 | 523776 | 523775.9997
39037.363 | 2176 | 1 | 39037.3631 | 0 | 0 |  | 159.5 | 333.5 | 132.8449 | 0.06105 | 0.030525 | 0 | 1.3284 | 0.0006105 | 0.00030525 | 0 | 1.3278 | 0.00030525 | 20.3853 | 523775.9999 | 44229.5556
39037.3652 | 2045 | 1 | 39037.3652 | 0 | 0 |  | 344.5 | 518.5 | 124.8474 | 0.06105 | 0.030525 | 0 | 1.2485 | 0.0006105 | 0.00030525 | 0 | 1.2479 | 0.00030525 | 28.1008 | 523776.0009 | 57327.055
39037.3673 | 2573 | 1 | 39037.3673 | 0 | 0 |  | 529 | 703 | 157.0818 | 0.06105 | 0.030525 | 0 | 1.5708 | 0.0006105 | 0.00030525 | 0 | 1.5702 | 0.00030525 | 1.8033 | 523775.9999 | 4537.1338
39037.3695 | 2374 | 1 | 39037.3695 | 0 | 0 |  | 713.5 | 887.5 | 144.9328 | 0.06105 | 0.030525 | 0 | 1.4493 | 0.0006105 | 0.00030525 | 0 | 1.4487 | 0.00030525 | 10.3405 | 523775.9999 | 24433.3352
39037.3716 | 2108 | 1 | 39037.3716 | 0 | 0 |  | 898.5 | 1072.5 | 128.6935 | 0.06105 | 0.030525 | 0 | 1.2869 | 0.0006105 | 0.00030525 | 0 | 1.2863 | 0.00030525 | 24.2705 | 523775.9999 | 51028.2576
39037.3737 | 2266 | 1 | 39037.3737 | 0 | 0 |  | 1083.5 | 1257.5 | 138.3394 | 0.06105 | 0.030525 | 0 | 1.3834 | 0.0006105 | 0.00030525 | 0 | 1.3828 | 0.00030525 | 15.6018 | 523775.9999 | 35231.2736
39037.3759 | 2504 | 1 | 39037.3759 | 0 | 0 |  | 1268 | 1442 | 152.8694 | 0.06105 | 0.030525 | 0 | 1.5287 | 0.0006105 | 0.00030525 | 0 | 1.5281 | 0.00030525 | 4.6097 | 523776.0009 | 11435.8167
39037.378 | 2012 | 1 | 39037.378 | 0 | 0 |  | 1453 | 1627 | 122.8327 | 0.06105 | 0.030525 | 0 | 1.2283 | 0.0006105 | 0.00030525 | 0 | 1.2277 | 0.00030525 | 30.2029 | 523775.9999 | 60626.4251
39037.3802 | 2603 | 0 | 39037.3802 | 2496 | 0 |  | 1637.5 | 1811.5 | 158.9133 | 0 | 152.381 | 0 | 1.5891 | 0 | 1.5238 | 0 | 1.5891 | 1.5238 | 0.62927 | 4.9431 | 0.95986

## D7-E9
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 152.2821 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 7 & 9 | Cable D | Odd - | Cable E |  | Odd
Time-105 | N11 | N12 | Time-106 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R9-G | R7-9
39037.3609 | 0 | 0 | 39037.3609 | 0 | 0 |  | -28 | 146 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 498776 | 498776 | 498775.9997
39037.363 | 1805 | 1 | 39037.363 | 0 | 0 |  | 156.5 | 330.5 | 110.1954 | 0.06105 | 0.030525 | 0 | 1.102 | 0.0006105 | 0.00030525 | 0 | 1.1013 | 0.00030525 | 38.214 | 498775.9997 | 68824.2014
39037.3652 | 2359 | 1 | 39037.3652 | 0 | 0 |  | 341.5 | 515.5 | 144.0171 | 0.06105 | 0.030525 | 0 | 1.4402 | 0.0006105 | 0.00030525 | 0 | 1.4396 | 0.00030525 | 5.7413 | 498776.0006 | 13435.3063
39037.3673 | 2290 | 1 | 39037.3673 | 0 | 0 |  | 526.5 | 700.5 | 139.8046 | 0.06105 | 0.030525 | 0 | 1.398 | 0.0006105 | 0.00030525 | 0 | 1.3974 | 0.00030525 | 8.9288 | 498776.0006 | 20333.9232
39037.3694 | 2333 | 1 | 39037.3694 | 0 | 0 |  | 711 | 885 | 142.4298 | 0.06105 | 0.030525 | 0 | 1.4243 | 0.0006105 | 0.00030525 | 0 | 1.4237 | 0.00030525 | 6.9202 | 498776.0006 | 16034.7852
39037.3716 | 2398 | 1 | 39037.3716 | 0 | 0 |  | 895.5 | 1069.5 | 146.398 | 0.06105 | 0.030525 | 0 | 1.464 | 0.0006105 | 0.00030525 | 0 | 1.4634 | 0.00030525 | 4.0209 | 498775.9997 | 9536.0881
39037.3737 | 2031 | 1 | 39037.3737 | 0 | 0 |  | 1080.5 | 1254.5 | 123.9927 | 0.06105 | 0.030525 | 0 | 1.2399 | 0.0006105 | 0.00030525 | 0 | 1.2393 | 0.00030525 | 22.8266 | 498775.9997 | 46228.7316
39037.3758 | 2409 | 1 | 39037.3759 | 0 | 0 |  | 1265.5 | 1439.5 | 147.0696 | 0.06105 | 0.030525 | 0 | 1.4707 | 0.0006105 | 0.00030525 | 0 | 1.4701 | 0.00030525 | 3.5457 | 498775.9997 | 8436.3086
39037.378 | 2332 | 1 | 39037.378 | 0 | 0 |  | 1450 | 1624 | 142.3687 | 0.06105 | 0.030525 | 0 | 1.4237 | 0.0006105 | 0.00030525 | 0 | 1.4231 | 0.00030525 | 6.9661 | 498775.9997 | 16134.7651
39037.3801 | 2404 | 0 | 39037.3801 | 2478 | 0 |  | 1634.5 | 1808.5 | 146.7643 | 0 | 151.2821 | 0 | 1.4676 | 0 | 1.5128 | 0 | 1.4676 | 1.5128 | 3.7596 | 0.66102 | 2.2919

## D7-D8
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.5092 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 7 & 8 | Cable D | Odd -Even
Time-103 | N11 | N12 | Time-104 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R7-G | R8-G | R7-8
39037.3608 | 0 | 0 | 39037.3609 | 0 | 0 |  | -31 | 143 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39037.363 | 1877 | 0 | 39037.363 | 2281 | 0 |  | 154 | 328 | 114.591 | 0 | 139.2552 | 0 | 1.1459 | 0 | 1.3926 | 0 | 1.1459 | 1.3926 | 38.3261 | 13.8264 | 37.1801
39037.3651 | 2432 | 0 | 39037.3651 | 2023 | 0 |  | 338.5 | 512.5 | 148.4737 | 0 | 123.5043 | 0 | 1.4847 | 0 | 1.235 | 0 | 1.4847 | 1.235 | 6.759 | 28.3431 | 5.2743
39037.3673 | 2046 | 0 | 39037.3673 | 1995 | 0 |  | 523.5 | 697.5 | 124.9084 | 0 | 121.7949 | 0 | 1.2491 | 0 | 1.2179 | 0 | 1.2491 | 1.2179 | 26.9003 | 30.1444 | 25.6512
39037.3694 | 2552 | 0 | 39037.3694 | 2089 | 0 |  | 708 | 882 | 155.7998 | 0 | 127.5336 | 0 | 1.558 | 0 | 1.2753 | 0 | 1.558 | 1.2753 | 1.739 | 24.2882 | 0.18103
39037.3715 | 2556 | 0 | 39037.3716 | 2188 | 0 |  | 893 | 1067 | 156.044 | 0 | 133.5775 | 0 | 1.5604 | 0 | 1.3358 | 0 | 1.5604 | 1.3358 | 1.5798 | 18.6645 | 0.019373
39037.3737 | 2476 | 0 | 39037.3737 | 2220 | 0 |  | 1077.5 | 1251.5 | 151.16 | 0 | 135.5311 | 0 | 1.5116 | 0 | 1.3553 | 0 | 1.5116 | 1.3553 | 4.8619 | 16.9541 | 3.3503
39037.3758 | 2197 | 0 | 39037.3758 | 2405 | 0 |  | 1262.5 | 1436.5 | 134.127 | 0 | 146.8254 | 0 | 1.3413 | 0 | 1.4683 | 0 | 1.3413 | 1.4683 | 18.1784 | 7.9576 | 16.8372
39037.3779 | 2365 | 0 | 39037.378 | 2340 | 0 |  | 1447 | 1621 | 144.3834 | 0 | 142.8571 | 0 | 1.4438 | 0 | 1.4286 | 0 | 1.4438 | 1.4286 | 9.7835 | 10.9564 | 8.3397
39037.3801 | 2580 | 0 | 39037.3801 | 2314 | 0 |  | 1632 | 1806 | 157.5092 | 0 | 141.2698 | 0 | 1.5751 | 0 | 1.4127 | 0 | 1.5751 | 1.4127 | 0.63488 | 12.2031 | 0.94021

## Raw IRMS Data
Time | DL1.V2000:B | DL1.V2001:B | DL1.V1500:B | Open Burn Test 10 |  |  | 2006-11-16 | 8:44
39037.3592 | 0 | 0 | 1 | Mix | 7-C | Tray C | IRMS | 2
39037.3613 | 0 | 0 | 1 |  | 250 kW |  | Bundle
39037.3635 | 0 | 0 | 1
39037.3656 | 1309 | 825 | 1
39037.3677 | 2494 | 1 | 1
39037.3699 | 2339 | 0 | 1
39037.372 | 2227 | 0 | 1
39037.3742 | 2006 | 0 | 1
39037.3763 | 2525 | 0 | 1
39037.3784 | 1947 | 1 | 1
1
39037.3592 | 0 | 0 | 2
39037.3613 | 0 | 0 | 2
39037.3635 | 0 | 0 | 2
39037.3656 | 1081 | 1018 | 2
39037.3678 | 2092 | 1 | 2
39037.3699 | 2519 | 0 | 2
39037.372 | 1972 | 0 | 2
39037.3742 | 2027 | 0 | 2
39037.3763 | 2018 | 0 | 2
39037.3784 | 2308 | 0 | 2
2
39037.3592 | 0 | 0 | 3
39037.3614 | 0 | 0 | 3
39037.3635 | 0 | 0 | 3
39037.3656 | 661 | 0 | 3
39037.3678 | 2454 | 0 | 3
39037.3699 | 2072 | 0 | 3
39037.372 | 1965 | 0 | 3
39037.3742 | 2457 | 0 | 3
39037.3763 | 2346 | 0 | 3
39037.3785 | 2156 | 0 | 3
3
39037.3592 | 0 | 0 | 4
39037.3614 | 0 | 0 | 4
39037.3635 | 0 | 0 | 4
39037.3656 | 2150 | 0 | 4
39037.3678 | 1981 | 0 | 4
39037.3699 | 2208 | 0 | 4
39037.3721 | 2574 | 0 | 4
39037.3742 | 2462 | 0 | 4
39037.3763 | 2386 | 0 | 4
39037.3785 | 2411 | 0 | 4
4
39037.3592 | 0 | 0 | 5
39037.3614 | 0 | 0 | 5
39037.3635 | 0 | 0 | 5
39037.3657 | 1090 | 0 | 5
39037.3678 | 1953 | 0 | 5
39037.3699 | 2560 | 0 | 5
39037.3721 | 2039 | 0 | 5
39037.3742 | 2003 | 0 | 5
39037.3764 | 2505 | 0 | 5
39037.3785 | 2007 | 0 | 5
5
39037.3593 | 0 | 0 | 6
39037.3614 | 0 | 0 | 6
39037.3635 | 0 | 0 | 6
39037.3657 | 2522 | 0 | 6
39037.3678 | 2322 | 0 | 6
39037.37 | 2481 | 0 | 6
39037.3721 | 2272 | 0 | 6
39037.3742 | 2006 | 0 | 6
39037.3764 | 2511 | 0 | 6
39037.3785 | 1887 | 0 | 6
6
39037.3593 | 0 | 0 | 7
39037.3614 | 0 | 0 | 7
39037.3636 | 0 | 0 | 7
39037.3657 | 1264 | 0 | 7
39037.3678 | 2485 | 0 | 7
39037.37 | 2070 | 0 | 7
39037.3721 | 2054 | 0 | 7
39037.3742 | 2376 | 0 | 7
39037.3764 | 2580 | 0 | 7
39037.3785 | 1929 | 0 | 7
7
39037.3593 | 0 | 0 | 8
39037.3614 | 0 | 0 | 8
39037.3636 | 0 | 0 | 8
39037.3657 | 1082 | 0 | 8
39037.3678 | 2519 | 0 | 8
39037.37 | 2405 | 0 | 8
39037.3721 | 2315 | 0 | 8
39037.3743 | 2550 | 0 | 8
39037.3764 | 2068 | 0 | 8
39037.3785 | 2547 | 0 | 8
8
39037.3593 | 0 | 0 | 9
39037.3615 | 0 | 0 | 9
39037.3636 | 0 | 0 | 9
39037.3657 | 929 | 0 | 9
39037.3679 | 2052 | 0 | 9
39037.37 | 2512 | 0 | 9
39037.3721 | 2505 | 0 | 9
39037.3743 | 2066 | 0 | 9
39037.3764 | 2390 | 0 | 9
39037.3786 | 2173 | 0 | 9
9
39037.3593 | 0 | 0 | 10
39037.3615 | 0 | 0 | 10
39037.3636 | 0 | 0 | 10
39037.3657 | 1308 | 0 | 10
39037.3679 | 1981 | 0 | 10
39037.37 | 2542 | 0 | 10
39037.3722 | 2165 | 0 | 10
39037.3743 | 1994 | 0 | 10
39037.3764 | 2386 | 0 | 10
39037.3786 | 2128 | 0 | 10
10
39037.3594 | 0 | 0 | 11
39037.3615 | 0 | 0 | 11
39037.3636 | 0 | 0 | 11
39037.3658 | 717 | 0 | 11
39037.3679 | 2242 | 0 | 11
39037.37 | 2538 | 0 | 11
39037.3722 | 2533 | 0 | 11
39037.3743 | 2298 | 0 | 11
39037.3765 | 2217 | 0 | 11
39037.3786 | 1992 | 0 | 11
11
39037.3594 | 0 | 0 | 12
39037.3615 | 0 | 0 | 12
39037.3636 | 2264 | 0 | 12
39037.3658 | 2421 | 0 | 12
39037.3679 | 2394 | 0 | 12
39037.3701 | 1984 | 0 | 12
39037.3722 | 2325 | 0 | 12
39037.3743 | 2612 | 0 | 12
39037.3765 | 2222 | 0 | 12
39037.3786 | 2002 | 0 | 12
12
39037.3594 | 0 | 0 | 13
39037.3615 | 0 | 0 | 13
39037.3637 | 0 | 0 | 13
39037.3658 | 1024 | 0 | 13
39037.3679 | 2461 | 0 | 13
39037.3701 | 2021 | 0 | 13
39037.3722 | 2014 | 0 | 13
39037.3744 | 2132 | 0 | 13
39037.3765 | 2377 | 0 | 13
39037.3786 | 1930 | 0 | 13
13
39037.3594 | 0 | 0 | 14
39037.3615 | 0 | 0 | 14
39037.3637 | 1538 | 0 | 14
39037.3658 | 1982 | 0 | 14
39037.368 | 2056 | 0 | 14
39037.3701 | 2211 | 0 | 14
39037.3722 | 2180 | 0 | 14
39037.3744 | 2612 | 0 | 14
39037.3765 | 2592 | 0 | 14
39037.3786 | 2165 | 0 | 14
14
39037.3594 | 0 | 0 | 15
39037.3616 | 0 | 0 | 15
39037.3637 | 0 | 0 | 15
39037.3658 | 986 | 0 | 15
39037.368 | 2528 | 0 | 15
39037.3701 | 2566 | 0 | 15
39037.3722 | 2554 | 0 | 15
39037.3744 | 2311 | 0 | 15
39037.3765 | 2487 | 0 | 15
39037.3787 | 2250 | 0 | 15
15
39037.3594 | 0 | 0 | 16
39037.3616 | 0 | 0 | 16
39037.3637 | 0 | 0 | 16
39037.3658 | 0 | 0 | 16
39037.368 | 0 | 0 | 16
39037.3701 | 0 | 0 | 16
39037.3723 | 0 | 0 | 16
39037.3744 | 0 | 0 | 16
39037.3765 | 0 | 0 | 16
39037.3787 | 2136 | 0 | 16
16
39037.3594 | 0 | 0 | 17
39037.3616 | 0 | 0 | 17
39037.3637 | 0 | 0 | 17
39037.3659 | 897 | 0 | 17
39037.368 | 2527 | 0 | 17
39037.3701 | 2029 | 0 | 17
39037.3723 | 2365 | 0 | 17
39037.3744 | 2223 | 0 | 17
39037.3766 | 2382 | 0 | 17
39037.3787 | 2478 | 0 | 17
17
39037.3595 | 0 | 0 | 18
39037.3616 | 0 | 0 | 18
39037.3637 | 0 | 0 | 18
39037.3659 | 0 | 0 | 18
39037.368 | 0 | 0 | 18
39037.3702 | 0 | 0 | 18
39037.3723 | 0 | 0 | 18
39037.3744 | 0 | 0 | 18
39037.3766 | 0 | 0 | 18
39037.3787 | 2096 | 0 | 18
18
39037.3595 | 0 | 0 | 19
39037.3616 | 0 | 0 | 19
39037.3637 | 0 | 0 | 19
39037.3659 | 1202 | 0 | 19
39037.368 | 2025 | 0 | 19
39037.3702 | 2130 | 0 | 19
39037.3723 | 2572 | 0 | 19
39037.3744 | 2206 | 0 | 19
39037.3766 | 2188 | 0 | 19
39037.3787 | 1920 | 0 | 19
19
39037.3595 | 0 | 0 | 20
39037.3616 | 0 | 0 | 20
39037.3638 | 2193 | 0 | 20
39037.3659 | 2593 | 0 | 20
39037.368 | 2201 | 0 | 20
39037.3702 | 2549 | 0 | 20
39037.3723 | 2185 | 0 | 20
39037.3745 | 2184 | 0 | 20
39037.3766 | 2294 | 0 | 20
39037.3787 | 2219 | 0 | 20
20
39037.3595 | 0 | 0 | 21
39037.3616 | 0 | 0 | 21
39037.3638 | 0 | 0 | 21
39037.3659 | 795 | 0 | 21
39037.3681 | 2529 | 0 | 21
39037.3702 | 2094 | 0 | 21
39037.3723 | 2570 | 0 | 21
39037.3745 | 2463 | 0 | 21
39037.3766 | 2164 | 0 | 21
39037.3788 | 2258 | 0 | 21
21
39037.3595 | 0 | 0 | 22
39037.3617 | 0 | 0 | 22
39037.3638 | 2147 | 0 | 22
39037.3659 | 2272 | 0 | 22
39037.3681 | 2394 | 0 | 22
39037.3702 | 2210 | 0 | 22
39037.3724 | 2279 | 0 | 22
39037.3745 | 2322 | 0 | 22
39037.3766 | 2175 | 0 | 22
39037.3788 | 1944 | 0 | 22
22
39037.3595 | 0 | 0 | 23
39037.3617 | 0 | 0 | 23
39037.3638 | 0 | 0 | 23
39037.366 | 622 | 0 | 23
39037.3681 | 2031 | 0 | 23
39037.3702 | 1964 | 0 | 23
39037.3724 | 2427 | 0 | 23
39037.3745 | 2208 | 0 | 23
39037.3767 | 2087 | 0 | 23
39037.3788 | 2151 | 0 | 23
23
39037.3596 | 0 | 0 | 24
39037.3617 | 0 | 0 | 24
39037.3638 | 0 | 0 | 24
39037.366 | 2333 | 0 | 24
39037.3681 | 1998 | 0 | 24
39037.3703 | 2554 | 0 | 24
39037.3724 | 2081 | 0 | 24
39037.3745 | 2048 | 0 | 24
39037.3767 | 2340 | 0 | 24
39037.3788 | 2323 | 0 | 24
24
39037.3596 | 0 | 0 | 25
39037.3617 | 0 | 0 | 25
39037.3639 | 0 | 0 | 25
39037.366 | 921 | 0 | 25
39037.3681 | 2428 | 0 | 25
39037.3703 | 2022 | 0 | 25
39037.3724 | 2554 | 0 | 25
39037.3745 | 2456 | 0 | 25
39037.3767 | 2264 | 0 | 25
39037.3788 | 2281 | 0 | 25
25
39037.3596 | 0 | 0 | 26
39037.3617 | 0 | 0 | 26
39037.3639 | 0 | 0 | 26
39037.366 | 967 | 0 | 26
39037.3681 | 2224 | 0 | 26
39037.3703 | 2381 | 0 | 26
39037.3724 | 2260 | 0 | 26
39037.3746 | 2589 | 0 | 26
39037.3767 | 2261 | 0 | 26
39037.3788 | 2303 | 0 | 26
26
39037.3596 | 0 | 0 | 27
39037.3617 | 0 | 0 | 27
39037.3639 | 0 | 0 | 27
39037.366 | 731 | 0 | 27
39037.3682 | 2540 | 0 | 27
39037.3703 | 2436 | 0 | 27
39037.3724 | 2195 | 0 | 27
39037.3746 | 2404 | 0 | 27
39037.3767 | 2493 | 0 | 27
39037.3789 | 2254 | 0 | 27
27
39037.3596 | 0 | 0 | 28
39037.3618 | 0 | 0 | 28
39037.3639 | 0 | 0 | 28
39037.366 | 1744 | 0 | 28
39037.3682 | 1968 | 0 | 28
39037.3703 | 1989 | 0 | 28
39037.3725 | 2253 | 0 | 28
39037.3746 | 2568 | 0 | 28
39037.3767 | 2077 | 0 | 28
39037.3789 | 2556 | 1 | 28
28
39037.3596 | 0 | 0 | 29
39037.3618 | 0 | 0 | 29
39037.3639 | 0 | 0 | 29
39037.3661 | 917 | 0 | 29
39037.3682 | 2290 | 0 | 29
39037.3703 | 2039 | 0 | 29
39037.3725 | 2544 | 0 | 29
39037.3746 | 2579 | 0 | 29
39037.3767 | 2359 | 0 | 29
39037.3789 | 1963 | 0 | 29
29
39037.3597 | 0 | 0 | 30
39037.3618 | 0 | 0 | 30
39037.3639 | 0 | 0 | 30
39037.3661 | 2162 | 0 | 30
39037.3682 | 2284 | 0 | 30
39037.3703 | 2542 | 0 | 30
39037.3725 | 2567 | 0 | 30
39037.3746 | 2071 | 0 | 30
39037.3768 | 2022 | 0 | 30
39037.3789 | 2092 | 1 | 30
30
39037.3597 | 0 | 0 | 31
39037.3618 | 0 | 0 | 31
39037.3639 | 0 | 0 | 31
39037.3661 | 1023 | 0 | 31
39037.3682 | 2463 | 0 | 31
39037.3704 | 2523 | 0 | 31
39037.3725 | 2264 | 0 | 31
39037.3746 | 2556 | 0 | 31
39037.3768 | 2102 | 0 | 31
39037.3789 | 2233 | 0 | 31
31
39037.3597 | 0 | 0 | 32
39037.3618 | 0 | 0 | 32
39037.364 | 2035 | 0 | 32
39037.3661 | 2011 | 0 | 32
39037.3682 | 2444 | 0 | 32
39037.3704 | 2342 | 0 | 32
39037.3725 | 2224 | 0 | 32
39037.3747 | 2243 | 0 | 32
39037.3768 | 2512 | 0 | 32
39037.3789 | 2455 | 0 | 32
32
39037.3597 | 0 | 0 | 33
39037.3618 | 0 | 0 | 33
39037.364 | 0 | 0 | 33
39037.3661 | 1023 | 0 | 33
39037.3683 | 2552 | 0 | 33
39037.3704 | 2268 | 0 | 33
39037.3725 | 2153 | 0 | 33
39037.3747 | 2546 | 0 | 33
39037.3768 | 2234 | 0 | 33
39037.3789 | 2064 | 0 | 33
33
39037.3597 | 0 | 0 | 34
39037.3619 | 0 | 0 | 34
39037.364 | 2027 | 0 | 34
39037.3661 | 2424 | 0 | 34
39037.3683 | 2267 | 0 | 34
39037.3704 | 2408 | 0 | 34
39037.3725 | 2223 | 0 | 34
39037.3747 | 2438 | 0 | 34
39037.3768 | 2561 | 0 | 34
39037.379 | 2225 | 0 | 34
34
39037.3597 | 0 | 0 | 35
39037.3619 | 0 | 0 | 35
39037.364 | 0 | 0 | 35
39037.3661 | 1462 | 0 | 35
39037.3683 | 1970 | 0 | 35
39037.3704 | 2362 | 0 | 35
39037.3726 | 2579 | 0 | 35
39037.3747 | 2020 | 0 | 35
39037.3768 | 2598 | 0 | 35
39037.379 | 1992 | 0 | 35
35
39037.3598 | 0 | 0 | 36
39037.3619 | 0 | 0 | 36
39037.364 | 0 | 0 | 36
39037.3662 | 0 | 0 | 36
39037.3683 | 0 | 0 | 36
39037.3704 | 0 | 0 | 36
39037.3726 | 0 | 0 | 36
39037.3747 | 0 | 0 | 36
39037.3769 | 0 | 0 | 36
39037.379 | 2029 | 0 | 36
36
39037.3598 | 0 | 0 | 37
39037.3619 | 0 | 0 | 37
39037.364 | 0 | 0 | 37
39037.3662 | 1410 | 0 | 37
39037.3683 | 2560 | 0 | 37
39037.3705 | 2251 | 0 | 37
39037.3726 | 2421 | 0 | 37
39037.3747 | 2094 | 0 | 37
39037.3769 | 2516 | 0 | 37
39037.379 | 1964 | 1 | 37
37
39037.3598 | 0 | 0 | 38
39037.3619 | 0 | 0 | 38
39037.3641 | 0 | 0 | 38
39037.3662 | 0 | 0 | 38
39037.3683 | 0 | 0 | 38
39037.3705 | 0 | 0 | 38
39037.3726 | 0 | 0 | 38
39037.3748 | 0 | 0 | 38
39037.3769 | 0 | 0 | 38
39037.379 | 1932 | 0 | 38
38
39037.3598 | 0 | 0 | 39
39037.3619 | 0 | 0 | 39
39037.3641 | 0 | 0 | 39
39037.3662 | 1464 | 0 | 39
39037.3684 | 2471 | 0 | 39
39037.3705 | 2151 | 0 | 39
39037.3726 | 2147 | 0 | 39
39037.3748 | 2310 | 0 | 39
39037.3769 | 2357 | 0 | 39
39037.3791 | 1992 | 0 | 39
39
39037.3598 | 0 | 0 | 40
39037.362 | 0 | 0 | 40
39037.3641 | 2165 | 0 | 40
39037.3662 | 2109 | 0 | 40
39037.3684 | 2350 | 0 | 40
39037.3705 | 1995 | 0 | 40
39037.3727 | 2596 | 0 | 40
39037.3748 | 2442 | 0 | 40
39037.3769 | 2563 | 0 | 40
39037.3791 | 2196 | 0 | 40
40
39037.3598 | 0 | 0 | 41
39037.362 | 0 | 0 | 41
39037.3641 | 0 | 0 | 41
39037.3662 | 1344 | 0 | 41
39037.3684 | 1976 | 0 | 41
39037.3705 | 2238 | 0 | 41
39037.3727 | 2352 | 0 | 41
39037.3748 | 2506 | 0 | 41
39037.3769 | 2316 | 0 | 41
39037.3791 | 2107 | 0 | 41
41
39037.3598 | 0 | 0 | 42
39037.362 | 0 | 0 | 42
39037.3641 | 2016 | 0 | 42
39037.3663 | 2311 | 0 | 42
39037.3684 | 2290 | 0 | 42
39037.3705 | 2061 | 0 | 42
39037.3727 | 2407 | 0 | 42
39037.3748 | 2546 | 0 | 42
39037.377 | 2152 | 0 | 42
39037.3791 | 1932 | 0 | 42
42
39037.3599 | 0 | 0 | 43
39037.362 | 0 | 0 | 43
39037.3641 | 90 | 1 | 43
39037.3663 | 2533 | 0 | 43
39037.3684 | 2464 | 0 | 43
39037.3706 | 2513 | 0 | 43
39037.3727 | 2315 | 0 | 43
39037.3748 | 2480 | 0 | 43
39037.377 | 2032 | 0 | 43
39037.3791 | 2458 | 2 | 43
43
39037.3599 | 0 | 0 | 44
39037.362 | 0 | 0 | 44
39037.3642 | 860 | 1 | 44
39037.3663 | 2495 | 0 | 44
39037.3684 | 2471 | 0 | 44
39037.3706 | 1963 | 0 | 44
39037.3727 | 2510 | 0 | 44
39037.3748 | 2162 | 0 | 44
39037.377 | 2102 | 0 | 44
39037.3791 | 2001 | 2 | 44
44
39037.3599 | 0 | 0 | 45
39037.362 | 0 | 0 | 45
39037.3642 | 244 | 0 | 45
39037.3663 | 2333 | 0 | 45
39037.3684 | 2555 | 0 | 45
39037.3706 | 2132 | 0 | 45
39037.3727 | 2482 | 0 | 45
39037.3749 | 2185 | 0 | 45
39037.377 | 2357 | 0 | 45
39037.3791 | 2419 | 0 | 45
45
39037.3599 | 0 | 0 | 46
39037.362 | 0 | 0 | 46
39037.3642 | 0 | 0 | 46
39037.3663 | 1918 | 0 | 46
39037.3685 | 2319 | 0 | 46
39037.3706 | 2256 | 0 | 46
39037.3727 | 2248 | 0 | 46
39037.3749 | 2091 | 0 | 46
39037.377 | 2299 | 0 | 46
39037.3792 | 2325 | 0 | 46
46
39037.3599 | 0 | 0 | 47
39037.3621 | 0 | 0 | 47
39037.3642 | 386 | 0 | 47
39037.3663 | 2216 | 0 | 47
39037.3685 | 2529 | 0 | 47
39037.3706 | 2058 | 0 | 47
39037.3728 | 2115 | 0 | 47
39037.3749 | 2540 | 0 | 47
39037.377 | 1964 | 0 | 47
39037.3792 | 1929 | 0 | 47
47
39037.3599 | 0 | 0 | 48
39037.3621 | 0 | 0 | 48
39037.3642 | 0 | 0 | 48
39037.3664 | 2320 | 0 | 48
39037.3685 | 2538 | 0 | 48
39037.3706 | 2020 | 0 | 48
39037.3728 | 2499 | 0 | 48
39037.3749 | 2075 | 0 | 48
39037.377 | 2042 | 0 | 48
39037.3792 | 2174 | 0 | 48
48
39037.36 | 0 | 0 | 49
39037.3621 | 0 | 0 | 49
39037.3642 | 233 | 0 | 49
39037.3664 | 2541 | 0 | 49
39037.3685 | 2044 | 0 | 49
39037.3707 | 2525 | 0 | 49
39037.3728 | 2206 | 0 | 49
39037.3749 | 2238 | 0 | 49
39037.3771 | 2482 | 0 | 49
39037.3792 | 2077 | 0 | 49
49
39037.36 | 0 | 0 | 50
39037.3621 | 0 | 0 | 50
39037.3643 | 1591 | 0 | 50
39037.3664 | 2024 | 0 | 50
39037.3685 | 1995 | 0 | 50
39037.3707 | 2097 | 0 | 50
39037.3728 | 2565 | 0 | 50
39037.375 | 2201 | 0 | 50
39037.3771 | 2038 | 0 | 50
39037.3792 | 2200 | 0 | 50
50
39037.36 | 0 | 0 | 51
39037.3621 | 0 | 0 | 51
39037.3643 | 265 | 0 | 51
39037.3664 | 2393 | 0 | 51
39037.3686 | 1970 | 0 | 51
39037.3707 | 2194 | 0 | 51
39037.3728 | 2035 | 0 | 51
39037.375 | 2012 | 0 | 51
39037.3771 | 2022 | 0 | 51
39037.3792 | 2429 | 0 | 51
51
39037.36 | 0 | 0 | 52
39037.3622 | 0 | 0 | 52
39037.3643 | 2089 | 0 | 52
39037.3664 | 2400 | 0 | 52
39037.3686 | 2020 | 0 | 52
39037.3707 | 2119 | 0 | 52
39037.3728 | 2343 | 0 | 52
39037.375 | 2246 | 0 | 52
39037.3771 | 2028 | 0 | 52
39037.3793 | 2207 | 0 | 52
52
39037.36 | 0 | 0 | 53
39037.3622 | 0 | 0 | 53
39037.3643 | 2078 | 0 | 53
39037.3664 | 2178 | 0 | 53
39037.3686 | 2087 | 0 | 53
39037.3707 | 1978 | 0 | 53
39037.3729 | 2160 | 0 | 53
39037.375 | 2218 | 0 | 53
39037.3771 | 2440 | 0 | 53
39037.3793 | 2208 | 0 | 53
53
39037.36 | 0 | 0 | 54
39037.3622 | 0 | 0 | 54
39037.3643 | 0 | 0 | 54
39037.3665 | 0 | 0 | 54
39037.3686 | 0 | 0 | 54
39037.3707 | 0 | 0 | 54
39037.3729 | 0 | 0 | 54
39037.375 | 0 | 0 | 54
39037.3772 | 0 | 0 | 54
39037.3793 | 1917 | 0 | 54
54
39037.3601 | 0 | 0 | 55
39037.3622 | 0 | 0 | 55
39037.3643 | 2078 | 0 | 55
39037.3665 | 2552 | 0 | 55
39037.3686 | 1955 | 0 | 55
39037.3708 | 2360 | 0 | 55
39037.3729 | 2133 | 0 | 55
39037.375 | 2039 | 0 | 55
39037.3772 | 2480 | 0 | 55
39037.3793 | 1927 | 0 | 55
55
39037.3601 | 0 | 0 | 56
39037.3622 | 0 | 0 | 56
39037.3644 | 0 | 0 | 56
39037.3665 | 0 | 0 | 56
39037.3686 | 0 | 0 | 56
39037.3708 | 0 | 0 | 56
39037.3729 | 0 | 0 | 56
39037.375 | 0 | 0 | 56
39037.3772 | 0 | 0 | 56
39037.3793 | 2052 | 0 | 56
56
39037.3601 | 0 | 0 | 57
39037.3622 | 0 | 0 | 57
39037.3644 | 2061 | 0 | 57
39037.3665 | 2019 | 0 | 57
39037.3686 | 2286 | 0 | 57
39037.3708 | 2563 | 0 | 57
39037.3729 | 2010 | 0 | 57
39037.3751 | 2029 | 0 | 57
39037.3772 | 1976 | 0 | 57
39037.3793 | 1974 | 0 | 57
57
39037.3601 | 0 | 0 | 58
39037.3622 | 0 | 0 | 58
39037.3644 | 2522 | 0 | 58
39037.3665 | 2210 | 0 | 58
39037.3687 | 2504 | 0 | 58
39037.3708 | 2603 | 0 | 58
39037.3729 | 2637 | 0 | 58
39037.3751 | 2210 | 0 | 58
39037.3772 | 2394 | 0 | 58
39037.3794 | 2425 | 0 | 58
58
39037.3601 | 0 | 0 | 59
39037.3623 | 0 | 0 | 59
39037.3644 | 1952 | 0 | 59
39037.3665 | 2083 | 0 | 59
39037.3687 | 2521 | 0 | 59
39037.3708 | 2007 | 0 | 59
39037.373 | 2121 | 0 | 59
39037.3751 | 2568 | 0 | 59
39037.3772 | 2482 | 0 | 59
39037.3794 | 1999 | 0 | 59
59
39037.3601 | 0 | 0 | 60
39037.3623 | 0 | 0 | 60
39037.3644 | 2334 | 0 | 60
39037.3666 | 2065 | 0 | 60
39037.3687 | 2369 | 0 | 60
39037.3708 | 2141 | 0 | 60
39037.373 | 2491 | 0 | 60
39037.3751 | 2593 | 0 | 60
39037.3772 | 2344 | 0 | 60
39037.3794 | 2507 | 0 | 60
60
39037.3602 | 0 | 0 | 61
39037.3623 | 0 | 0 | 61
39037.3644 | 1566 | 0 | 61
39037.3666 | 1995 | 0 | 61
39037.3687 | 1977 | 0 | 61
39037.3708 | 2538 | 0 | 61
39037.373 | 2162 | 0 | 61
39037.3751 | 2096 | 0 | 61
39037.3773 | 2262 | 0 | 61
39037.3794 | 1891 | 0 | 61
61
39037.3602 | 0 | 0 | 62
39037.3623 | 0 | 0 | 62
39037.3644 | 0 | 0 | 62
39037.3666 | 2347 | 0 | 62
39037.3687 | 2246 | 0 | 62
39037.3709 | 1990 | 0 | 62
39037.373 | 2206 | 0 | 62
39037.3751 | 2579 | 0 | 62
39037.3773 | 2100 | 0 | 62
39037.3794 | 2454 | 0 | 62
62
39037.3602 | 0 | 0 | 63
39037.3623 | 0 | 0 | 63
39037.3645 | 1928 | 0 | 63
39037.3666 | 2104 | 0 | 63
39037.3687 | 2130 | 0 | 63
39037.3709 | 2024 | 0 | 63
39037.373 | 2076 | 0 | 63
39037.3752 | 2072 | 0 | 63
39037.3773 | 2526 | 0 | 63
39037.3794 | 2038 | 0 | 63
63
39037.3602 | 0 | 0 | 64
39037.3623 | 0 | 0 | 64
39037.3645 | 0 | 0 | 64
39037.3666 | 1931 | 0 | 64
39037.3688 | 2554 | 0 | 64
39037.3709 | 2227 | 0 | 64
39037.373 | 2048 | 0 | 64
39037.3752 | 2019 | 0 | 64
39037.3773 | 2160 | 0 | 64
39037.3795 | 1958 | 0 | 64
64
39037.3602 | 0 | 0 | 65
39037.3624 | 0 | 0 | 65
39037.3645 | 2320 | 0 | 65
39037.3666 | 2236 | 0 | 65
39037.3688 | 2056 | 0 | 65
39037.3709 | 2546 | 0 | 65
39037.3731 | 1996 | 0 | 65
39037.3752 | 2065 | 0 | 65
39037.3773 | 2009 | 0 | 65
39037.3795 | 2484 | 0 | 65
65
39037.3602 | 0 | 0 | 66
39037.3624 | 0 | 0 | 66
39037.3645 | 2175 | 0 | 66
39037.3667 | 1990 | 0 | 66
39037.3688 | 2248 | 0 | 66
39037.3709 | 2579 | 0 | 66
39037.3731 | 2611 | 0 | 66
39037.3752 | 1995 | 0 | 66
39037.3773 | 2064 | 0 | 66
39037.3795 | 2226 | 0 | 66
66
39037.3603 | 0 | 0 | 67
39037.3624 | 0 | 0 | 67
39037.3645 | 2165 | 0 | 67
39037.3667 | 2241 | 0 | 67
39037.3688 | 2292 | 0 | 67
39037.3709 | 1992 | 0 | 67
39037.3731 | 2306 | 0 | 67
39037.3752 | 2222 | 0 | 67
39037.3774 | 2394 | 0 | 67
39037.3795 | 1994 | 0 | 67
67
39037.3603 | 0 | 0 | 68
39037.3624 | 0 | 0 | 68
39037.3645 | 2423 | 0 | 68
39037.3667 | 2033 | 0 | 68
39037.3688 | 2590 | 0 | 68
39037.371 | 2350 | 0 | 68
39037.3731 | 2606 | 0 | 68
39037.3752 | 2012 | 0 | 68
39037.3774 | 2476 | 0 | 68
39037.3795 | 2498 | 0 | 68
68
39037.3603 | 0 | 0 | 69
39037.3624 | 0 | 0 | 69
39037.3646 | 2507 | 0 | 69
39037.3667 | 2558 | 0 | 69
39037.3688 | 2425 | 0 | 69
39037.371 | 2173 | 0 | 69
39037.3731 | 2435 | 0 | 69
39037.3753 | 2083 | 0 | 69
39037.3774 | 2576 | 0 | 69
39037.3795 | 2361 | 0 | 69
69
39037.3603 | 0 | 0 | 70
39037.3624 | 0 | 0 | 70
39037.3646 | 0 | 0 | 70
39037.3667 | 0 | 0 | 70
39037.3689 | 0 | 0 | 70
39037.371 | 0 | 0 | 70
39037.3731 | 0 | 0 | 70
39037.3753 | 0 | 0 | 70
39037.3774 | 0 | 0 | 70
39037.3795 | 2240 | 0 | 70
70
39037.3603 | 0 | 0 | 71
39037.3625 | 0 | 0 | 71
39037.3646 | 2297 | 0 | 71
39037.3667 | 1992 | 0 | 71
39037.3689 | 2335 | 0 | 71
39037.371 | 2052 | 0 | 71
39037.3731 | 2021 | 0 | 71
39037.3753 | 2298 | 0 | 71
39037.3774 | 2262 | 0 | 71
39037.3796 | 1925 | 0 | 71
71
39037.3603 | 0 | 0 | 72
39037.3625 | 0 | 0 | 72
39037.3646 | 0 | 0 | 72
39037.3667 | 0 | 0 | 72
39037.3689 | 0 | 0 | 72
39037.371 | 0 | 0 | 72
39037.3732 | 0 | 0 | 72
39037.3753 | 0 | 0 | 72
39037.3774 | 0 | 0 | 72
39037.3796 | 2022 | 0 | 72
72
39037.3603 | 0 | 0 | 73
39037.3625 | 0 | 0 | 73
39037.3646 | 2015 | 0 | 73
39037.3668 | 2458 | 0 | 73
39037.3689 | 2111 | 0 | 73
39037.371 | 2037 | 0 | 73
39037.3732 | 1977 | 0 | 73
39037.3753 | 2124 | 0 | 73
39037.3775 | 2345 | 0 | 73
39037.3796 | 2464 | 0 | 73
73
39037.3604 | 0 | 0 | 74
39037.3625 | 0 | 0 | 74
39037.3646 | 2033 | 0 | 74
39037.3668 | 2142 | 0 | 74
39037.3689 | 2196 | 0 | 74
39037.3711 | 2027 | 0 | 74
39037.3732 | 2159 | 0 | 74
39037.3753 | 2606 | 0 | 74
39037.3775 | 2391 | 0 | 74
39037.3796 | 2437 | 0 | 74
74
39037.3604 | 0 | 0 | 75
39037.3625 | 0 | 0 | 75
39037.3647 | 2422 | 0 | 75
39037.3668 | 2416 | 0 | 75
39037.3689 | 2182 | 0 | 75
39037.3711 | 2325 | 0 | 75
39037.3732 | 2549 | 0 | 75
39037.3754 | 2449 | 0 | 75
39037.3775 | 2493 | 0 | 75
39037.3796 | 2009 | 0 | 75
75
39037.3604 | 0 | 0 | 76
39037.3625 | 0 | 0 | 76
39037.3647 | 2048 | 0 | 76
39037.3668 | 2540 | 0 | 76
39037.369 | 2031 | 0 | 76
39037.3711 | 2237 | 0 | 76
39037.3732 | 2428 | 0 | 76
39037.3754 | 2305 | 0 | 76
39037.3775 | 2100 | 0 | 76
39037.3796 | 2438 | 0 | 76
76
39037.3604 | 0 | 0 | 77
39037.3626 | 0 | 0 | 77
39037.3647 | 1011 | 918 | 77
39037.3668 | 2128 | 6 | 77
39037.369 | 2048 | 0 | 77
39037.3711 | 1967 | 0 | 77
39037.3733 | 2004 | 0 | 77
39037.3754 | 2593 | 0 | 77
39037.3775 | 2100 | 0 | 77
39037.3797 | 2482 | 0 | 77
77
39037.3604 | 0 | 0 | 78
39037.3626 | 0 | 0 | 78
39037.3647 | 1138 | 924 | 78
39037.3669 | 2267 | 5 | 78
39037.369 | 2511 | 0 | 78
39037.3711 | 2169 | 0 | 78
39037.3733 | 2088 | 0 | 78
39037.3754 | 2015 | 0 | 78
39037.3775 | 2155 | 0 | 78
39037.3797 | 2160 | 0 | 78
78
39037.3605 | 0 | 0 | 79
39037.3626 | 0 | 0 | 79
39037.3647 | 0 | 0 | 79
39037.3669 | 2099 | 0 | 79
39037.369 | 2497 | 0 | 79
39037.3711 | 2216 | 0 | 79
39037.3733 | 2512 | 0 | 79
39037.3754 | 2304 | 0 | 79
39037.3776 | 2151 | 0 | 79
39037.3797 | 2561 | 0 | 79
79
39037.3605 | 0 | 0 | 80
39037.3626 | 0 | 0 | 80
39037.3647 | 2153 | 0 | 80
39037.3669 | 2059 | 0 | 80
39037.369 | 2259 | 0 | 80
39037.3712 | 2505 | 0 | 80
39037.3733 | 2191 | 0 | 80
39037.3754 | 2044 | 0 | 80
39037.3776 | 2533 | 0 | 80
39037.3797 | 2555 | 0 | 80
80
39037.3605 | 0 | 0 | 81
39037.3626 | 0 | 0 | 81
39037.3648 | 0 | 0 | 81
39037.3669 | 2408 | 0 | 81
39037.369 | 1968 | 0 | 81
39037.3712 | 2041 | 0 | 81
39037.3733 | 2309 | 0 | 81
39037.3755 | 2156 | 0 | 81
39037.3776 | 2506 | 0 | 81
39037.3797 | 1995 | 0 | 81
81
39037.3605 | 0 | 0 | 82
39037.3626 | 1835 | 1 | 82
39037.3648 | 2350 | 0 | 82
39037.3669 | 2142 | 0 | 82
39037.3691 | 2533 | 0 | 82
39037.3712 | 2385 | 0 | 82
39037.3733 | 2581 | 0 | 82
39037.3755 | 2215 | 0 | 82
39037.3776 | 2345 | 0 | 82
39037.3797 | 2276 | 0 | 82
82
39037.3605 | 0 | 0 | 83
39037.3627 | 0 | 0 | 83
39037.3648 | 0 | 0 | 83
39037.3669 | 2290 | 0 | 83
39037.3691 | 2136 | 0 | 83
39037.3712 | 2173 | 0 | 83
39037.3733 | 2084 | 0 | 83
39037.3755 | 2408 | 0 | 83
39037.3776 | 2297 | 0 | 83
39037.3798 | 2572 | 0 | 83
83
39037.3605 | 0 | 0 | 84
39037.3627 | 0 | 0 | 84
39037.3648 | 0 | 0 | 84
39037.3669 | 0 | 0 | 84
39037.3691 | 0 | 0 | 84
39037.3712 | 0 | 0 | 84
39037.3734 | 0 | 0 | 84
39037.3755 | 0 | 0 | 84
39037.3776 | 0 | 0 | 84
39037.3798 | 2061 | 0 | 84
84
39037.3605 | 0 | 0 | 85
39037.3627 | 0 | 0 | 85
39037.3648 | 0 | 0 | 85
39037.367 | 2346 | 0 | 85
39037.3691 | 2361 | 0 | 85
39037.3712 | 2057 | 0 | 85
39037.3734 | 2012 | 0 | 85
39037.3755 | 2396 | 0 | 85
39037.3777 | 2195 | 0 | 85
39037.3798 | 2365 | 0 | 85
85
39037.3606 | 0 | 0 | 86
39037.3627 | 0 | 0 | 86
39037.3648 | 0 | 0 | 86
39037.367 | 0 | 0 | 86
39037.3691 | 0 | 0 | 86
39037.3712 | 0 | 0 | 86
39037.3734 | 0 | 0 | 86
39037.3755 | 0 | 0 | 86
39037.3777 | 0 | 0 | 86
39037.3798 | 2448 | 0 | 86
86
39037.3606 | 0 | 0 | 87
39037.3627 | 0 | 0 | 87
39037.3649 | 4 | 0 | 87
39037.367 | 2510 | 0 | 87
39037.3691 | 2144 | 0 | 87
39037.3713 | 2370 | 0 | 87
39037.3734 | 2039 | 0 | 87
39037.3755 | 2589 | 0 | 87
39037.3777 | 2017 | 0 | 87
39037.3798 | 2587 | 0 | 87
87
39037.3606 | 0 | 0 | 88
39037.3627 | 0 | 0 | 88
39037.3649 | 2127 | 0 | 88
39037.367 | 2463 | 0 | 88
39037.3691 | 2146 | 0 | 88
39037.3713 | 2376 | 0 | 88
39037.3734 | 2557 | 0 | 88
39037.3756 | 2236 | 0 | 88
39037.3777 | 2010 | 0 | 88
39037.3798 | 2518 | 0 | 88
88
39037.3606 | 0 | 0 | 89
39037.3628 | 0 | 0 | 89
39037.3649 | 5 | 0 | 89
39037.367 | 1982 | 0 | 89
39037.3692 | 2419 | 0 | 89
39037.3713 | 2532 | 0 | 89
39037.3734 | 2481 | 0 | 89
39037.3756 | 2262 | 0 | 89
39037.3777 | 2270 | 0 | 89
39037.3799 | 2093 | 0 | 89
89
39037.3606 | 0 | 0 | 90
39037.3628 | 0 | 0 | 90
39037.3649 | 2550 | 0 | 90
39037.367 | 2232 | 0 | 90
39037.3692 | 2382 | 0 | 90
39037.3713 | 2084 | 0 | 90
39037.3735 | 2365 | 0 | 90
39037.3756 | 2516 | 0 | 90
39037.3777 | 2267 | 0 | 90
39037.3799 | 2382 | 0 | 90
90
39037.3606 | 0 | 0 | 91
39037.3628 | 0 | 0 | 91
39037.3649 | 74 | 0 | 91
39037.3671 | 2479 | 0 | 91
39037.3692 | 2368 | 0 | 91
39037.3713 | 2064 | 0 | 91
39037.3735 | 2594 | 0 | 91
39037.3756 | 2365 | 0 | 91
39037.3778 | 2049 | 0 | 91
39037.3799 | 2248 | 0 | 91
91
39037.3607 | 0 | 0 | 92
39037.3628 | 0 | 0 | 92
39037.3649 | 2425 | 0 | 92
39037.3671 | 2096 | 0 | 92
39037.3692 | 2195 | 0 | 92
39037.3714 | 2621 | 0 | 92
39037.3735 | 2602 | 0 | 92
39037.3756 | 2053 | 0 | 92
39037.3778 | 2069 | 0 | 92
39037.3799 | 2186 | 0 | 92
92
39037.3607 | 0 | 0 | 93
39037.3628 | 0 | 0 | 93
39037.365 | 257 | 0 | 93
39037.3671 | 1992 | 0 | 93
39037.3692 | 2576 | 0 | 93
39037.3714 | 2200 | 0 | 93
39037.3735 | 1998 | 0 | 93
39037.3756 | 2359 | 0 | 93
39037.3778 | 2028 | 0 | 93
39037.3799 | 2517 | 0 | 93
93
39037.3607 | 0 | 0 | 94
39037.3628 | 2360 | 0 | 94
39037.365 | 2347 | 0 | 94
39037.3671 | 2373 | 0 | 94
39037.3692 | 2517 | 0 | 94
39037.3714 | 2166 | 0 | 94
39037.3735 | 1983 | 0 | 94
39037.3757 | 2194 | 0 | 94
39037.3778 | 1997 | 0 | 94
39037.3799 | 2066 | 0 | 94
94
39037.3607 | 0 | 0 | 95
39037.3628 | 0 | 0 | 95
39037.365 | 684 | 0 | 95
39037.3671 | 2548 | 0 | 95
39037.3693 | 2235 | 0 | 95
39037.3714 | 2455 | 0 | 95
39037.3735 | 2047 | 0 | 95
39037.3757 | 2337 | 0 | 95
39037.3778 | 2218 | 0 | 95
39037.38 | 1988 | 0 | 95
95
39037.3607 | 0 | 0 | 96
39037.3629 | 0 | 0 | 96
39037.365 | 0 | 0 | 96
39037.3671 | 0 | 0 | 96
39037.3693 | 0 | 0 | 96
39037.3714 | 0 | 0 | 96
39037.3736 | 0 | 0 | 96
39037.3757 | 0 | 0 | 96
39037.3778 | 0 | 0 | 96
39037.38 | 2326 | 0 | 96
96
39037.3607 | 0 | 0 | 97
39037.3629 | 0 | 0 | 97
39037.365 | 896 | 0 | 97
39037.3672 | 2175 | 0 | 97
39037.3693 | 2577 | 0 | 97
39037.3714 | 2584 | 0 | 97
39037.3736 | 2478 | 0 | 97
39037.3757 | 2073 | 0 | 97
39037.3778 | 2160 | 0 | 97
39037.38 | 2580 | 0 | 97
97
39037.3608 | 0 | 0 | 98
39037.3629 | 0 | 0 | 98
39037.365 | 0 | 0 | 98
39037.3672 | 0 | 0 | 98
39037.3693 | 0 | 0 | 98
39037.3714 | 0 | 0 | 98
39037.3736 | 0 | 0 | 98
39037.3757 | 0 | 0 | 98
39037.3779 | 0 | 0 | 98
39037.38 | 2494 | 0 | 98
98
39037.3608 | 0 | 0 | 99
39037.3629 | 0 | 0 | 99
39037.365 | 1160 | 0 | 99
39037.3672 | 1962 | 0 | 99
39037.3693 | 2098 | 0 | 99
39037.3715 | 2141 | 0 | 99
39037.3736 | 2039 | 0 | 99
39037.3757 | 2516 | 0 | 99
39037.3779 | 2588 | 0 | 99
39037.38 | 2544 | 0 | 99
99
39037.3608 | 0 | 0 | 100
39037.3629 | 0 | 0 | 100
39037.3651 | 2152 | 0 | 100
39037.3672 | 2360 | 0 | 100
39037.3693 | 2380 | 0 | 100
39037.3715 | 2253 | 0 | 100
39037.3736 | 2158 | 0 | 100
39037.3758 | 2446 | 0 | 100
39037.3779 | 2108 | 0 | 100
39037.38 | 2117 | 0 | 100
100
39037.3608 | 0 | 0 | 101
39037.3629 | 0 | 0 | 101
39037.3651 | 171 | 0 | 101
39037.3672 | 2276 | 0 | 101
39037.3694 | 2357 | 0 | 101
39037.3715 | 2021 | 0 | 101
39037.3736 | 2060 | 0 | 101
39037.3758 | 2568 | 0 | 101
39037.3779 | 2438 | 0 | 101
39037.38 | 2376 | 0 | 101
101
39037.3608 | 0 | 0 | 102
39037.363 | 0 | 0 | 102
39037.3651 | 2117 | 0 | 102
39037.3672 | 2119 | 0 | 102
39037.3694 | 2322 | 0 | 102
39037.3715 | 1990 | 0 | 102
39037.3737 | 2123 | 0 | 102
39037.3758 | 2208 | 0 | 102
39037.3779 | 2038 | 0 | 102
39037.3801 | 2426 | 0 | 102
102
39037.3608 | 0 | 0 | 103
39037.363 | 1877 | 0 | 103
39037.3651 | 2432 | 0 | 103
39037.3673 | 2046 | 0 | 103
39037.3694 | 2552 | 0 | 103
39037.3715 | 2556 | 0 | 103
39037.3737 | 2476 | 0 | 103
39037.3758 | 2197 | 0 | 103
39037.3779 | 2365 | 0 | 103
39037.3801 | 2580 | 0 | 103
103
39037.3609 | 0 | 0 | 104
39037.363 | 2281 | 0 | 104
39037.3651 | 2023 | 0 | 104
39037.3673 | 1995 | 0 | 104
39037.3694 | 2089 | 0 | 104
39037.3716 | 2188 | 0 | 104
39037.3737 | 2220 | 0 | 104
39037.3758 | 2405 | 0 | 104
39037.378 | 2340 | 0 | 104
39037.3801 | 2314 | 0 | 104
104
39037.3609 | 0 | 0 | 105
39037.363 | 1805 | 0 | 105
39037.3652 | 2359 | 0 | 105
39037.3673 | 2290 | 0 | 105
39037.3694 | 2333 | 0 | 105
39037.3716 | 2398 | 0 | 105
39037.3737 | 2031 | 0 | 105
39037.3758 | 2409 | 0 | 105
39037.378 | 2332 | 0 | 105
39037.3801 | 2404 | 0 | 105
105
39037.3609 | 0 | 0 | 106
39037.363 | 0 | 0 | 106
39037.3652 | 0 | 0 | 106
39037.3673 | 0 | 0 | 106
39037.3694 | 0 | 0 | 106
39037.3716 | 0 | 0 | 106
39037.3737 | 0 | 0 | 106
39037.3759 | 0 | 0 | 106
39037.378 | 0 | 0 | 106
39037.3801 | 2478 | 0 | 106
106
39037.3609 | 0 | 0 | 107
39037.363 | 2176 | 0 | 107
39037.3652 | 2045 | 0 | 107
39037.3673 | 2573 | 0 | 107
39037.3695 | 2374 | 0 | 107
39037.3716 | 2108 | 0 | 107
39037.3737 | 2266 | 0 | 107
39037.3759 | 2504 | 0 | 107
39037.378 | 2012 | 0 | 107
39037.3802 | 2603 | 0 | 107
107
39037.3609 | 0 | 0 | 108
39037.3631 | 0 | 0 | 108
39037.3652 | 0 | 0 | 108
39037.3673 | 0 | 0 | 108
39037.3695 | 0 | 0 | 108
39037.3716 | 0 | 0 | 108
39037.3737 | 0 | 0 | 108
39037.3759 | 0 | 0 | 108
39037.378 | 0 | 0 | 108
39037.3802 | 2496 | 0 | 108
108
39037.3609 | 0 | 0 | 109
39037.3631 | 2548 | 0 | 109
39037.3652 | 2005 | 0 | 109
39037.3673 | 2082 | 0 | 109
39037.3695 | 2582 | 0 | 109
39037.3716 | 2556 | 0 | 109
39037.3738 | 2571 | 0 | 109
39037.3759 | 2470 | 0 | 109
39037.378 | 2265 | 0 | 109
39037.3802 | 2012 | 0 | 109
109
39037.3609 | 0 | 0 | 110
39037.3631 | 0 | 0 | 110
39037.3652 | 2552 | 0 | 110
39037.3674 | 2374 | 0 | 110
39037.3695 | 2350 | 0 | 110
39037.3716 | 2419 | 0 | 110
39037.3738 | 2532 | 0 | 110
39037.3759 | 2556 | 0 | 110
39037.3781 | 2227 | 0 | 110
39037.3802 | 1967 | 0 | 110
110
39037.361 | 0 | 0 | 111
39037.3631 | 2010 | 0 | 111
39037.3652 | 2278 | 0 | 111
39037.3674 | 2556 | 0 | 111
39037.3695 | 2338 | 0 | 111
39037.3717 | 2248 | 0 | 111
39037.3738 | 2197 | 0 | 111
39037.3759 | 2354 | 0 | 111
39037.3781 | 2530 | 0 | 111
39037.3802 | 2266 | 0 | 111
111
39037.361 | 0 | 0 | 112
39037.3631 | 0 | 0 | 112
39037.3653 | 2383 | 0 | 112
39037.3674 | 2045 | 0 | 112
39037.3695 | 2004 | 0 | 112
39037.3717 | 2603 | 0 | 112
39037.3738 | 2563 | 0 | 112
39037.3759 | 2265 | 0 | 112
39037.3781 | 2427 | 0 | 112
39037.3802 | 2533 | 0 | 112
112
39037.361 | 0 | 0 | 113
39037.3631 | 2017 | 0 | 113
39037.3653 | 2320 | 0 | 113
39037.3674 | 2487 | 0 | 113
39037.3695 | 2601 | 0 | 113
39037.3717 | 2090 | 0 | 113
39037.3738 | 2459 | 0 | 113
39037.376 | 2156 | 0 | 113
39037.3781 | 2153 | 0 | 113
39037.3802 | 2041 | 0 | 113
113
39037.361 | 0 | 0 | 114
39037.3632 | 0 | 0 | 114
39037.3653 | 0 | 0 | 114
39037.3674 | 0 | 0 | 114
39037.3696 | 0 | 0 | 114
39037.3717 | 0 | 0 | 114
39037.3738 | 0 | 0 | 114
39037.376 | 0 | 0 | 114
39037.3781 | 0 | 0 | 114
39037.3803 | 2215 | 0 | 114
114
39037.361 | 0 | 0 | 115
39037.3632 | 1996 | 0 | 115
39037.3653 | 1933 | 0 | 115
39037.3675 | 2024 | 0 | 115
39037.3696 | 2431 | 0 | 115
39037.3717 | 2057 | 0 | 115
39037.3739 | 2340 | 0 | 115
39037.376 | 1993 | 0 | 115
39037.3781 | 2521 | 0 | 115
39037.3803 | 2520 | 0 | 115
115
39037.3611 | 0 | 0 | 116
39037.3632 | 0 | 0 | 116
39037.3653 | 0 | 0 | 116
39037.3675 | 0 | 0 | 116
39037.3696 | 0 | 0 | 116
39037.3717 | 0 | 0 | 116
39037.3739 | 0 | 0 | 116
39037.376 | 0 | 0 | 116
39037.3782 | 0 | 0 | 116
39037.3803 | 2019 | 0 | 116
116
39037.3611 | 0 | 0 | 117
39037.3632 | 2255 | 0 | 117
39037.3653 | 1993 | 0 | 117
39037.3675 | 2183 | 0 | 117
39037.3696 | 1979 | 0 | 117
39037.3718 | 2621 | 0 | 117
39037.3739 | 2164 | 0 | 117
39037.376 | 2277 | 0 | 117
39037.3782 | 2597 | 0 | 117
39037.3803 | 2255 | 0 | 117
117
39037.3611 | 0 | 0 | 118
39037.3632 | 0 | 0 | 118
39037.3654 | 2189 | 0 | 118
39037.3675 | 2394 | 0 | 118
39037.3696 | 2467 | 0 | 118
39037.3718 | 2506 | 0 | 118
39037.3739 | 2607 | 0 | 118
39037.3761 | 2376 | 0 | 118
39037.3782 | 2408 | 0 | 118
39037.3803 | 1953 | 0 | 118
118
39037.3611 | 0 | 0 | 119
39037.3632 | 2192 | 0 | 119
39037.3654 | 2384 | 0 | 119
39037.3675 | 2375 | 0 | 119
39037.3697 | 2005 | 0 | 119
39037.3718 | 2036 | 0 | 119
39037.3739 | 2035 | 0 | 119
39037.3761 | 2139 | 0 | 119
39037.3782 | 2224 | 0 | 119
39037.3803 | 2183 | 0 | 119
119
39037.3611 | 0 | 0 | 120
39037.3633 | 0 | 0 | 120
39037.3654 | 2291 | 0 | 120
39037.3675 | 2596 | 0 | 120
39037.3697 | 2095 | 0 | 120
39037.3718 | 2496 | 0 | 120
39037.3739 | 2297 | 0 | 120
39037.3761 | 2537 | 0 | 120
39037.3782 | 2023 | 0 | 120
39037.3804 | 2347 | 0 | 120
120
39037.3611 | 0 | 0 | 121
39037.3633 | 0 | 0 | 121
39037.3654 | 0 | 0 | 121
39037.3675 | 0 | 0 | 121
39037.3697 | 0 | 0 | 121
39037.3718 | 0 | 0 | 121
39037.374 | 0 | 0 | 121
39037.3761 | 0 | 0 | 121
39037.3782 | 1 | 0 | 121
39037.3804 | 2542 | 0 | 121
121
39037.3611 | 0 | 0 | 122
39037.3633 | 0 | 0 | 122
39037.3654 | 0 | 0 | 122
39037.3676 | 0 | 0 | 122
39037.3697 | 0 | 0 | 122
39037.3718 | 0 | 0 | 122
39037.374 | 0 | 0 | 122
39037.3761 | 0 | 0 | 122
39037.3783 | 201 | 0 | 122
39037.3804 | 2484 | 0 | 122
122
39037.3612 | 0 | 0 | 123
39037.3633 | 0 | 0 | 123
39037.3654 | 0 | 0 | 123
39037.3676 | 0 | 0 | 123
39037.3697 | 0 | 0 | 123
39037.3719 | 0 | 0 | 123
39037.374 | 0 | 0 | 123
39037.3761 | 0 | 0 | 123
39037.3783 | 278 | 0 | 123
39037.3804 | 2094 | 0 | 123
123
39037.3612 | 0 | 0 | 124
39037.3633 | 1964 | 0 | 124
39037.3655 | 2376 | 0 | 124
39037.3676 | 2223 | 0 | 124
39037.3697 | 2268 | 0 | 124
39037.3719 | 2073 | 0 | 124
39037.374 | 2387 | 0 | 124
39037.3761 | 2601 | 0 | 124
39037.3783 | 2103 | 0 | 124
39037.3804 | 2148 | 0 | 124
124
39037.3612 | 0 | 0 | 125
39037.3633 | 0 | 0 | 125
39037.3655 | 0 | 0 | 125
39037.3676 | 0 | 0 | 125
39037.3697 | 0 | 0 | 125
39037.3719 | 0 | 0 | 125
39037.374 | 0 | 0 | 125
39037.3762 | 0 | 0 | 125
39037.3783 | 2194 | 0 | 125
39037.3804 | 2040 | 0 | 125
125
39037.3612 | 0 | 0 | 126
39037.3633 | 4 | 0 | 126
39037.3655 | 2224 | 0 | 126
39037.3676 | 2569 | 0 | 126
39037.3698 | 2010 | 0 | 126
39037.3719 | 2339 | 0 | 126
39037.374 | 2350 | 0 | 126
39037.3762 | 2238 | 0 | 126
39037.3783 | 2472 | 0 | 126
39037.3805 | 2558 | 0 | 126
126
39037.3612 | 0 | 0 | 127
39037.3634 | 0 | 0 | 127
39037.3655 | 0 | 0 | 127
39037.3676 | 0 | 0 | 127
39037.3698 | 0 | 0 | 127
39037.3719 | 0 | 0 | 127
39037.3741 | 0 | 0 | 127
39037.3762 | 0 | 0 | 127
39037.3783 | 2420 | 0 | 127
39037.3805 | 1957 | 0 | 127
127
39037.3612 | 0 | 0 | 128
39037.3634 | 1728 | 0 | 128
39037.3655 | 2561 | 0 | 128
39037.3677 | 2261 | 0 | 128
39037.3698 | 2314 | 0 | 128
39037.3719 | 2604 | 0 | 128
39037.3741 | 2151 | 0 | 128
39037.3762 | 2101 | 0 | 128
39037.3783 | 2189 | 0 | 128
39037.3805 | 1995 | 0 | 128
128
39037.3613 | 0 | 0 | 129
39037.3634 | 0 | 0 | 129
39037.3655 | 0 | 0 | 129
39037.3677 | 0 | 0 | 129
39037.3698 | 0 | 0 | 129
39037.372 | 0 | 0 | 129
39037.3741 | 0 | 0 | 129
39037.3762 | 0 | 0 | 129
39037.3784 | 2315 | 0 | 129
39037.3805 | 2217 | 0 | 129
129
39037.3613 | 0 | 0 | 130
39037.3634 | 1998 | 0 | 130
39037.3656 | 2282 | 0 | 130
39037.3677 | 2324 | 0 | 130
39037.3698 | 2181 | 0 | 130
39037.372 | 2274 | 0 | 130
39037.3741 | 2287 | 0 | 130
39037.3763 | 2026 | 0 | 130
39037.3784 | 2119 | 0 | 130
39037.3805 | 1956 | 0 | 130
130
39037.3613 | 0 | 0 | 131
39037.3634 | 1662 | 0 | 131
39037.3656 | 2344 | 0 | 131
39037.3677 | 2063 | 0 | 131
39037.3698 | 2454 | 0 | 131
39037.372 | 2592 | 0 | 131
39037.3741 | 2237 | 0 | 131
39037.3763 | 2338 | 0 | 131
39037.3784 | 2179 | 0 | 131
39037.3805 | 1957 | 0 | 131
131
39037.3613 | 0 | 0 | 132
39037.3634 | 1574 | 0 | 132
39037.3656 | 2440 | 0 | 132
39037.3677 | 2027 | 0 | 132
39037.3699 | 2045 | 0 | 132
39037.372 | 2530 | 0 | 132
39037.3741 | 2614 | 0 | 132
39037.3763 | 2259 | 0 | 132
39037.3784 | 2379 | 0 | 132
39037.3806 | 2102 | 0 | 132
132

## C6-F12
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 157.7766 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 6 & 12 | Cable C | Even - | Cable F |  | Even
Time-101 | N11 | N12 | Time-102 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R12-G | R6-12
39037.3608 | 0 | 0 | 39037.3608 | 0 | 0 |  | -33.5 | 140.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516776 | 516776 | 516775.9997
39037.3629 | 0 | 0 | 39037.363 | 0 | 0 |  | 151 | 325 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516776 | 516776 | 516775.9997
39037.3651 | 171 | 0 | 39037.3651 | 2117 | 0 |  | 335.5 | 509.5 | 10.4396 | 0 | 129.243 | 0 | 0.1044 | 0 | 1.2924 | 0 | 0.1044 | 1.2924 | 1411.3333 | 22.0775 | 1411.2289
39037.3672 | 2276 | 0 | 39037.3672 | 2119 | 0 |  | 520.5 | 694.5 | 138.9499 | 0 | 129.3651 | 0 | 1.3895 | 0 | 1.2937 | 0 | 1.3895 | 1.2937 | 13.5492 | 21.9622 | 12.1597
39037.3694 | 2357 | 0 | 39037.3694 | 2322 | 0 |  | 705.5 | 879.5 | 143.895 | 0 | 141.7582 | 0 | 1.4389 | 0 | 1.4176 | 0 | 1.4389 | 1.4176 | 9.647 | 11.2997 | 8.2081
39037.3715 | 2021 | 0 | 39037.3715 | 1990 | 0 |  | 890 | 1064 | 123.3822 | 0 | 121.4896 | 0 | 1.2338 | 0 | 1.2149 | 0 | 1.2338 | 1.2149 | 27.8763 | 29.8683 | 26.6425
39037.3736 | 2060 | 0 | 39037.3737 | 2123 | 0 |  | 1075 | 1249 | 125.7631 | 0 | 129.6093 | 0 | 1.2576 | 0 | 1.2961 | 0 | 1.2576 | 1.2961 | 25.4553 | 21.7325 | 24.1977
39037.3758 | 2568 | 0 | 39037.3758 | 2208 | 0 |  | 1259.5 | 1433.5 | 156.7766 | 0 | 134.7985 | 0 | 1.5678 | 0 | 1.348 | 0 | 1.5678 | 1.348 | 0.63785 | 17.0462 | 0.92992
39037.3779 | 2438 | 0 | 39037.3779 | 2038 | 0 |  | 1444.5 | 1618.5 | 148.84 | 0 | 124.42 | 0 | 1.4884 | 0 | 1.2442 | 0 | 1.4884 | 1.2442 | 6.0041 | 26.8096 | 4.5157
39037.38 | 2376 | 0 | 39037.3801 | 2426 | 0 |  | 1629 | 1803 | 145.0549 | 0 | 148.1074 | 0 | 1.4505 | 0 | 1.4811 | 0 | 1.4505 | 1.4811 | 8.7702 | 6.5284 | 7.3197

## C6-F11
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.9976 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 6 & 11 | Cable C | Even - | Cable F |  | Odd
Time-99 | N11 | N12 | Time-100 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R11-G | R6-11
39037.3608 | 0 | 0 | 39037.3608 | 0 | 0 |  | -36.5 | 137.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39037.3629 | 0 | 0 | 39037.3629 | 0 | 0 |  | 148.5 | 322.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520776 | 520776 | 520775.9997
39037.365 | 1160 | 0 | 39037.3651 | 2152 | 0 |  | 333 | 507 | 70.8181 | 0 | 131.3797 | 0 | 0.70818 | 0 | 1.3138 | 0 | 0.70818 | 1.3138 | 124.5155 | 21.0214 | 123.8073
39037.3672 | 1962 | 0 | 39037.3672 | 2360 | 0 |  | 518 | 692 | 119.7802 | 0 | 144.0781 | 0 | 1.1978 | 0 | 1.4408 | 0 | 1.1978 | 1.4408 | 32.7411 | 10.3551 | 31.5433
39037.3693 | 2098 | 0 | 39037.3693 | 2380 | 0 |  | 702.5 | 876.5 | 128.083 | 0 | 145.2991 | 0 | 1.2808 | 0 | 1.453 | 0 | 1.2808 | 1.453 | 24.1363 | 9.4277 | 22.8555
39037.3715 | 2141 | 0 | 39037.3715 | 2253 | 0 |  | 887.5 | 1061.5 | 130.7082 | 0 | 137.5458 | 0 | 1.3071 | 0 | 1.3755 | 0 | 1.3071 | 1.3755 | 21.6432 | 15.5961 | 20.3361
39037.3736 | 2039 | 0 | 39037.3736 | 2158 | 0 |  | 1072 | 1246 | 124.4811 | 0 | 131.746 | 0 | 1.2448 | 0 | 1.3175 | 0 | 1.2448 | 1.3175 | 27.7283 | 20.6849 | 26.4835
39037.3757 | 2516 | 0 | 39037.3758 | 2446 | 0 |  | 1257 | 1431 | 153.602 | 0 | 149.3284 | 0 | 1.536 | 0 | 1.4933 | 0 | 1.536 | 1.4933 | 3.5127 | 6.4751 | 1.9767
39037.3779 | 2588 | 0 | 39037.3779 | 2108 | 0 |  | 1441.5 | 1615.5 | 157.9976 | 0 | 128.6935 | 0 | 1.58 | 0 | 1.2869 | 0 | 1.58 | 1.2869 | 0.63292 | 23.5474 | 0.94705
39037.38 | 2544 | 0 | 39037.38 | 2117 | 0 |  | 1626.5 | 1800.5 | 155.3114 | 0 | 129.243 | 0 | 1.5531 | 0 | 1.2924 | 0 | 1.5531 | 1.2924 | 2.3734 | 23.0222 | 0.82031

## C6-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.7534 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 6 & 10 | Cable C | Even - | Cable E |  | Even
Time-97 | N11 | N12 | Time-98 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R10-G | R6-10
39037.3607 | 0 | 0 | 39037.3608 | 0 | 0 |  | -39.5 | 134.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519976 | 519976 | 519975.9997
39037.3629 | 0 | 0 | 39037.3629 | 0 | 0 |  | 145.5 | 319.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519976 | 519976 | 519975.9997
39037.365 | 896 | 1 | 39037.365 | 0 | 0 |  | 330.5 | 504.5 | 54.7009 | 0.06105 | 0.030525 | 0 | 0.54701 | 0.0006105 | 0.00030525 | 0 | 0.5464 | 0.00030525 | 190.4336 | 519976.0006 | 170305.2475
39037.3672 | 2175 | 1 | 39037.3672 | 0 | 0 |  | 515 | 689 | 132.7839 | 0.06105 | 0.030525 | 0 | 1.3278 | 0.0006105 | 0.00030525 | 0 | 1.3272 | 0.00030525 | 19.5667 | 519976.0001 | 42429.84
39037.3693 | 2577 | 1 | 39037.3693 | 0 | 0 |  | 699.5 | 873.5 | 157.326 | 0.06105 | 0.030525 | 0 | 1.5733 | 0.0006105 | 0.00030525 | 0 | 1.5726 | 0.00030525 | 0.90761 | 519976.0001 | 2237.5697
39037.3714 | 2584 | 1 | 39037.3714 | 0 | 0 |  | 884.5 | 1058.5 | 157.7534 | 0.06105 | 0.030525 | 0 | 1.5775 | 0.0006105 | 0.00030525 | 0 | 1.5769 | 0.00030525 | 0.63415 | 519976.001 | 1537.7043
39037.3736 | 2478 | 1 | 39037.3736 | 0 | 0 |  | 1069.5 | 1243.5 | 151.2821 | 0.06105 | 0.030525 | 0 | 1.5128 | 0.0006105 | 0.00030525 | 0 | 1.5122 | 0.00030525 | 4.9407 | 519976.0001 | 12135.6661
39037.3757 | 2073 | 1 | 39037.3757 | 0 | 0 |  | 1254 | 1428 | 126.5568 | 0.06105 | 0.030525 | 0 | 1.2656 | 0.0006105 | 0.00030525 | 0 | 1.265 | 0.00030525 | 25.4527 | 519976.001 | 52627.8788
39037.3778 | 2160 | 1 | 39037.3779 | 0 | 0 |  | 1439 | 1613 | 131.8681 | 0.06105 | 0.030525 | 0 | 1.3187 | 0.0006105 | 0.00030525 | 0 | 1.3181 | 0.00030525 | 20.3974 | 519976.001 | 43929.5516
39037.38 | 2580 | 0 | 39037.38 | 2494 | 0 |  | 1623.5 | 1797.5 | 157.5092 | 0 | 152.2589 | 0 | 1.5751 | 0 | 1.5226 | 0 | 1.5751 | 1.5226 | 0.78992 | 4.2654 | 0.78517

## C6-E9
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.5556 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 6 & 9 | Cable C | Even - | Cable E |  | Odd
Time-95 | N11 | N12 | Time-96 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R6-G | R9-G | R6-9
39037.3607 | 0 | 0 | 39037.3607 | 0 | 0 |  | -42 | 132 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39037.3628 | 0 | 0 | 39037.3629 | 0 | 0 |  | 142.5 | 316.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 512776 | 512776 | 512775.9997
39037.365 | 684 | 1 | 39037.365 | 0 | 0 |  | 327.5 | 501.5 | 41.7582 | 0.06105 | 0.030525 | 0 | 0.41758 | 0.0006105 | 0.00030525 | 0 | 0.41697 | 0.00030525 | 275.3119 | 512776.0003 | 187901.3561
39037.3671 | 2548 | 1 | 39037.3671 | 0 | 0 |  | 512 | 686 | 155.5556 | 0.06105 | 0.030525 | 0 | 1.5556 | 0.0006105 | 0.00030525 | 0 | 1.5549 | 0.00030525 | 0.64311 | 512776 | 1537.7001
39037.3693 | 2235 | 1 | 39037.3693 | 0 | 0 |  | 697 | 871 | 136.4469 | 0.06105 | 0.030525 | 0 | 1.3645 | 0.0006105 | 0.00030525 | 0 | 1.3639 | 0.00030525 | 14.744 | 512776.001 | 32831.5973
39037.3714 | 2455 | 1 | 39037.3714 | 0 | 0 |  | 881.5 | 1055.5 | 149.8779 | 0.06105 | 0.030525 | 0 | 1.4988 | 0.0006105 | 0.00030525 | 0 | 1.4982 | 0.00030525 | 4.4572 | 512776.001 | 10835.8868
39037.3735 | 2047 | 1 | 39037.3736 | 0 | 0 |  | 1066.5 | 1240.5 | 124.9695 | 0.06105 | 0.030525 | 0 | 1.2497 | 0.0006105 | 0.00030525 | 0 | 1.2491 | 0.00030525 | 25.2874 | 512776 | 51627.9317
39037.3757 | 2337 | 1 | 39037.3757 | 0 | 0 |  | 1251.5 | 1425.5 | 142.674 | 0.06105 | 0.030525 | 0 | 1.4267 | 0.0006105 | 0.00030525 | 0 | 1.4261 | 0.00030525 | 9.7337 | 512776.001 | 22633.5861
39037.3778 | 2218 | 1 | 39037.3778 | 0 | 0 |  | 1436 | 1610 | 135.409 | 0.06105 | 0.030525 | 0 | 1.3541 | 0.0006105 | 0.00030525 | 0 | 1.3535 | 0.00030525 | 15.6238 | 512776 | 34531.2658
39037.38 | 1988 | 0 | 39037.38 | 2326 | 0 |  | 1621 | 1795 | 121.3675 | 0 | 142.0024 | 0 | 1.2137 | 0 | 1.42 | 0 | 1.2137 | 1.42 | 28.993 | 10.2485 | 27.7793

## C5-F12
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.6777 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 12 | Cable C | Odd - | Cable F |  | Even
Time-89 | N11 | N12 | Time-90 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R12-G | R5-12
39037.3606 | 0 | 0 | 39037.3606 | 0 | 0 |  | -50.5 | 123.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513176 | 513176 | 513175.9997
39037.3628 | 0 | 0 | 39037.3628 | 0 | 0 |  | 134.5 | 308.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513176 | 513176 | 513175.9997
39037.3649 | 5 | 0 | 39037.3649 | 2550 | 0 |  | 319 | 493 | 0.30525 | 0 | 155.6777 | 0 | 0.0030525 | 0 | 1.5568 | 0 | 0.0030525 | 1.5568 | 51227.6 | 0.64235 | 51227.5969
39037.367 | 1982 | 0 | 39037.367 | 2232 | 0 |  | 503.5 | 677.5 | 121.0012 | 0 | 136.2637 | 0 | 1.21 | 0 | 1.3626 | 0 | 1.21 | 1.3626 | 29.4844 | 14.9812 | 28.2743
39037.3692 | 2419 | 0 | 39037.3692 | 2382 | 0 |  | 688.5 | 862.5 | 147.6801 | 0 | 145.4212 | 0 | 1.4768 | 0 | 1.4542 | 0 | 1.4768 | 1.4542 | 6.0926 | 7.7406 | 4.6158
39037.3713 | 2532 | 0 | 39037.3713 | 2084 | 0 |  | 873.5 | 1047.5 | 154.5788 | 0 | 127.2283 | 0 | 1.5458 | 0 | 1.2723 | 0 | 1.5458 | 1.2723 | 1.3578 | 23.1468 | 0.18797
39037.3734 | 2481 | 0 | 39037.3735 | 2365 | 0 |  | 1058 | 1232 | 151.4652 | 0 | 144.3834 | 0 | 1.5147 | 0 | 1.4438 | 0 | 1.5147 | 1.4438 | 3.4414 | 8.515 | 1.9267
39037.3756 | 2262 | 0 | 39037.3756 | 2516 | 0 |  | 1243 | 1417 | 138.0952 | 0 | 153.602 | 0 | 1.381 | 0 | 1.536 | 0 | 1.381 | 1.536 | 13.4562 | 2.0024 | 12.0753
39037.3777 | 2270 | 0 | 39037.3777 | 2267 | 0 |  | 1427.5 | 1601.5 | 138.5836 | 0 | 138.4005 | 0 | 1.3858 | 0 | 1.384 | 0 | 1.3858 | 1.384 | 13.0564 | 13.206 | 11.6706
39037.3799 | 2093 | 0 | 39037.3799 | 2382 | 0 |  | 1612.5 | 1786.5 | 127.7778 | 0 | 145.4212 | 0 | 1.2778 | 0 | 1.4542 | 0 | 1.2778 | 1.4542 | 22.6173 | 7.7406 | 21.3395

## C5-F11
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.0586 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 11 | Cable C | Odd - | Cable F |  | Odd
Time-87 | N11 | N12 | Time-88 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R11-G | R5-11
39037.3606 | 0 | 0 | 39037.3606 | 0 | 0 |  | -53.5 | 120.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39037.3627 | 0 | 0 | 39037.3627 | 0 | 0 |  | 131.5 | 305.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39037.3649 | 4 | 0 | 39037.3649 | 2127 | 0 |  | 316.5 | 490.5 | 0.2442 | 0 | 129.8535 | 0 | 0.002442 | 0 | 1.2985 | 0 | 0.002442 | 1.2985 | 65034.5 | 22.4908 | 65034.4976
39037.367 | 2510 | 0 | 39037.367 | 2463 | 0 |  | 501 | 675 | 153.2357 | 0 | 150.3663 | 0 | 1.5324 | 0 | 1.5037 | 0 | 1.5324 | 1.5037 | 3.8 | 5.7808 | 2.2676
39037.3691 | 2144 | 0 | 39037.3691 | 2146 | 0 |  | 685.5 | 859.5 | 130.8913 | 0 | 131.0134 | 0 | 1.3089 | 0 | 1.3101 | 0 | 1.3089 | 1.3101 | 21.5196 | 21.4063 | 20.2107
39037.3713 | 2370 | 0 | 39037.3713 | 2376 | 0 |  | 870.5 | 1044.5 | 144.6886 | 0 | 145.0549 | 0 | 1.4469 | 0 | 1.4505 | 0 | 1.4469 | 1.4505 | 9.9316 | 9.654 | 8.4848
39037.3734 | 2039 | 0 | 39037.3734 | 2557 | 0 |  | 1055.5 | 1229.5 | 124.4811 | 0 | 156.105 | 0 | 1.2448 | 0 | 1.5611 | 0 | 1.2448 | 1.5611 | 27.7773 | 1.8921 | 26.5325
39037.3755 | 2589 | 0 | 39037.3756 | 2236 | 0 |  | 1240 | 1414 | 158.0586 | 0 | 136.5079 | 0 | 1.5806 | 0 | 1.3651 | 0 | 1.5806 | 1.3651 | 0.63268 | 16.5197 | 0.94791
39037.3777 | 2017 | 0 | 39037.3777 | 2010 | 0 |  | 1425 | 1599 | 123.138 | 0 | 122.7106 | 0 | 1.2314 | 0 | 1.2271 | 0 | 1.2314 | 1.2271 | 29.171 | 29.6209 | 27.9397
39037.3798 | 2587 | 0 | 39037.3798 | 2518 | 0 |  | 1609.5 | 1783.5 | 157.9365 | 0 | 153.7241 | 0 | 1.5794 | 0 | 1.5372 | 0 | 1.5794 | 1.5372 | 0.71048 | 3.4702 | 0.86889

## C5-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 150.4505 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 10 | Cable C | Odd - | Cable E |  | Even
Time-85 | N11 | N12 | Time-86 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R10-G | R5-10
39037.3605 | 0 | 0 | 39037.3606 | 0 | 0 |  | -56 | 118 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492776 | 492776 | 492775.9997
39037.3627 | 0 | 0 | 39037.3627 | 0 | 0 |  | 128.5 | 302.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492776 | 492776 | 492775.9997
39037.3648 | 0 | 0 | 39037.3648 | 0 | 0 |  | 313.5 | 487.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 492776 | 492776 | 492775.9997
39037.367 | 2346 | 1 | 39037.367 | 0 | 0 |  | 498 | 672 | 143.2234 | 0.06105 | 0.030525 | 0 | 1.4322 | 0.0006105 | 0.00030525 | 0 | 1.4316 | 0.00030525 | 5.0482 | 492775.9995 | 11735.6185
39037.3691 | 2361 | 1 | 39037.3691 | 0 | 0 |  | 683 | 857 | 144.1392 | 0.06105 | 0.030525 | 0 | 1.4414 | 0.0006105 | 0.00030525 | 0 | 1.4408 | 0.00030525 | 4.3805 | 492776.0004 | 10235.9228
39037.3712 | 2057 | 1 | 39037.3712 | 0 | 0 |  | 867.5 | 1041.5 | 125.58 | 0.06105 | 0.030525 | 0 | 1.2558 | 0.0006105 | 0.00030525 | 0 | 1.2552 | 0.00030525 | 19.8142 | 492775.9995 | 40629.7549
39037.3734 | 2012 | 1 | 39037.3734 | 0 | 0 |  | 1052.5 | 1226.5 | 122.8327 | 0.06105 | 0.030525 | 0 | 1.2283 | 0.0006105 | 0.00030525 | 0 | 1.2277 | 0.00030525 | 22.4953 | 492775.9995 | 45128.8419
39037.3755 | 2396 | 1 | 39037.3755 | 0 | 0 |  | 1237.5 | 1411.5 | 146.2759 | 0.06105 | 0.030525 | 0 | 1.4628 | 0.0006105 | 0.00030525 | 0 | 1.4621 | 0.00030525 | 2.8551 | 492776.0013 | 6736.6329
39037.3777 | 2195 | 1 | 39037.3777 | 0 | 0 |  | 1422 | 1596 | 134.0049 | 0.06105 | 0.030525 | 0 | 1.34 | 0.0006105 | 0.00030525 | 0 | 1.3394 | 0.00030525 | 12.278 | 492775.9995 | 26832.5548
39037.3798 | 2365 | 0 | 39037.3798 | 2448 | 0 |  | 1606.5 | 1780.5 | 144.3834 | 0 | 149.4505 | 0 | 1.4438 | 0 | 1.4945 | 0 | 1.4438 | 1.4945 | 4.2021 | 0.66912 | 2.7583

## C5-E9
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.0208 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 9 | Cable C | Odd - | Cable E |  | Odd
Time-83 | N11 | N12 | Time-84 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R9-G | R5-9
39037.3605 | 0 | 0 | 39037.3605 | 0 | 0 |  | -59 | 115 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39037.3627 | 0 | 0 | 39037.3627 | 0 | 0 |  | 126 | 300 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39037.3648 | 0 | 0 | 39037.3648 | 0 | 0 |  | 310.5 | 484.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517576 | 517576 | 517575.9997
39037.3669 | 2290 | 1 | 39037.3669 | 0 | 0 |  | 495.5 | 669.5 | 139.8046 | 0.06105 | 0.030525 | 0 | 1.398 | 0.0006105 | 0.00030525 | 0 | 1.3974 | 0.00030525 | 13.0354 | 517575.9998 | 29732.2555
39037.3691 | 2136 | 1 | 39037.3691 | 0 | 0 |  | 680 | 854 | 130.4029 | 0.06105 | 0.030525 | 0 | 1.304 | 0.0006105 | 0.00030525 | 0 | 1.3034 | 0.00030525 | 21.1888 | 517575.9998 | 45129.2806
39037.3712 | 2173 | 1 | 39037.3712 | 0 | 0 |  | 865 | 1039 | 132.6618 | 0.06105 | 0.030525 | 0 | 1.3266 | 0.0006105 | 0.00030525 | 0 | 1.326 | 0.00030525 | 19.1243 | 517575.9998 | 41429.9954
39037.3733 | 2084 | 1 | 39037.3734 | 0 | 0 |  | 1049.5 | 1223.5 | 127.2283 | 0.06105 | 0.030525 | 0 | 1.2723 | 0.0006105 | 0.00030525 | 0 | 1.2717 | 0.00030525 | 24.2141 | 517576.0007 | 50328.2762
39037.3755 | 2408 | 1 | 39037.3755 | 0 | 0 |  | 1234.5 | 1408.5 | 147.0085 | 0.06105 | 0.030525 | 0 | 1.4701 | 0.0006105 | 0.00030525 | 0 | 1.4695 | 0.00030525 | 7.494 | 517575.9998 | 17934.5349
39037.3776 | 2297 | 1 | 39037.3776 | 0 | 0 |  | 1419.5 | 1593.5 | 140.232 | 0.06105 | 0.030525 | 0 | 1.4023 | 0.0006105 | 0.00030525 | 0 | 1.4017 | 0.00030525 | 12.6908 | 517575.9998 | 29032.3907
39037.3798 | 2572 | 0 | 39037.3798 | 2061 | 0 |  | 1604 | 1778 | 157.0208 | 0 | 125.8242 | 0 | 1.5702 | 0 | 1.2582 | 0 | 1.5702 | 1.2582 | 0.63686 | 25.5885 | 0.93335

## C5-C6
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.3028 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 5 & 6 | Cable C | Odd-Even
Time-77 | N11 | N12 | Time-78 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R5-G | R6-G | R5-6
39037.3604 | 0 | 0 | 39037.3604 | 0 | 0 |  | -67.5 | 106.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521776 | 521776 | 521775.9997
39037.3626 | 0 | 0 | 39037.3626 | 0 | 0 |  | 117.5 | 291.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 521776 | 521776 | 521775.9997
39037.3647 | 1011 | 918 | 39037.3647 | 1138 | 924 |  | 302.5 | 476.5 | 61.7216 | 56.044 | 69.475 | 56.4103 | 0.61722 | 0.56044 | 0.69475 | 0.5641 | 0.056777 | 0.13065 | 2522.2279 | 3098.3944 | 71.7982
39037.3668 | 2128 | 6 | 39037.3669 | 2267 | 5 |  | 487 | 661 | 129.9145 | 0.3663 | 138.4005 | 0.30525 | 1.2991 | 0.003663 | 1.384 | 0.0030525 | 1.2955 | 1.381 | 23.1128 | 15.2823 | 1050.3068
39037.369 | 2048 | 0 | 39037.369 | 2511 | 0 |  | 671.5 | 845.5 | 125.0305 | 0 | 153.2967 | 0 | 1.2503 | 0 | 1.533 | 0 | 1.2503 | 1.533 | 27.4111 | 3.918 | 26.1608
39037.3711 | 1967 | 0 | 39037.3711 | 2169 | 0 |  | 856.5 | 1030.5 | 120.0855 | 0 | 132.4176 | 0 | 1.2009 | 0 | 1.3242 | 0 | 1.2009 | 1.3242 | 32.6579 | 20.3034 | 31.457
39037.3733 | 2004 | 0 | 39037.3733 | 2088 | 0 |  | 1041.5 | 1215.5 | 122.3443 | 0 | 127.4725 | 0 | 1.2234 | 0 | 1.2747 | 0 | 1.2234 | 1.2747 | 30.2086 | 24.9703 | 28.9851
39037.3754 | 2593 | 0 | 39037.3754 | 2015 | 0 |  | 1226 | 1400 | 158.3028 | 0 | 123.0159 | 0 | 1.583 | 0 | 1.2302 | 0 | 1.583 | 1.2302 | 0.6317 | 29.4978 | 0.95133
39037.3775 | 2100 | 0 | 39037.3775 | 2155 | 0 |  | 1411 | 1585 | 128.2051 | 0 | 131.5629 | 0 | 1.2821 | 0 | 1.3156 | 0 | 1.2821 | 1.3156 | 24.2562 | 21.0849 | 22.9741
39037.3797 | 2482 | 0 | 39037.3797 | 2160 | 0 |  | 1595.5 | 1769.5 | 151.5263 | 0 | 131.8681 | 0 | 1.5153 | 0 | 1.3187 | 0 | 1.5153 | 1.3187 | 5.1322 | 20.8046 | 3.6169

## B4-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 143.5519 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 10 | Cable B | Even - | Cable E |  | Even
Time-71 | N11 | N12 | Time-72 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R10-G | R4-10
39037.3603 | 0 | 0 | 39037.3603 | 0 | 0 |  | -75.5 | 98.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 470176 | 470176 | 470175.9997
39037.3625 | 0 | 0 | 39037.3625 | 0 | 0 |  | 109 | 283 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 470176 | 470176 | 470175.9997
39037.3646 | 2297 | 1 | 39037.3646 | 0 | 0 |  | 294 | 468 | 140.232 | 0.06105 | 0.030525 | 0 | 1.4023 | 0.0006105 | 0.00030525 | 0 | 1.4017 | 0.00030525 | 2.3685 | 470175.9995 | 5336.8649
39037.3667 | 1992 | 1 | 39037.3667 | 0 | 0 |  | 478.5 | 652.5 | 121.6117 | 0.06105 | 0.030525 | 0 | 1.2161 | 0.0006105 | 0.00030525 | 0 | 1.2155 | 0.00030525 | 18.0502 | 470176.0011 | 35830.3794
39037.3689 | 2335 | 1 | 39037.3689 | 0 | 0 |  | 663.5 | 837.5 | 142.5519 | 0.06105 | 0.030525 | 0 | 1.4255 | 0.0006105 | 0.00030525 | 0 | 1.4249 | 0.00030525 | 0.7018 | 470175.9995 | 1537.673
39037.371 | 2052 | 1 | 39037.371 | 0 | 0 |  | 848 | 1022 | 125.2747 | 0.06105 | 0.030525 | 0 | 1.2527 | 0.0006105 | 0.00030525 | 0 | 1.2521 | 0.00030525 | 14.5968 | 470176.0003 | 29831.6552
39037.3731 | 2021 | 1 | 39037.3732 | 0 | 0 |  | 1033 | 1207 | 123.3822 | 0.06105 | 0.030525 | 0 | 1.2338 | 0.0006105 | 0.00030525 | 0 | 1.2332 | 0.00030525 | 16.3554 | 470176.0011 | 32930.996
39037.3753 | 2298 | 1 | 39037.3753 | 0 | 0 |  | 1217.5 | 1391.5 | 140.293 | 0.06105 | 0.030525 | 0 | 1.4029 | 0.0006105 | 0.00030525 | 0 | 1.4023 | 0.00030525 | 2.3239 | 470175.9995 | 5236.8862
39037.3774 | 2262 | 1 | 39037.3774 | 0 | 0 |  | 1402.5 | 1576.5 | 138.0952 | 0.06105 | 0.030525 | 0 | 1.381 | 0.0006105 | 0.00030525 | 0 | 1.3803 | 0.00030525 | 3.9531 | 470176.0011 | 8836.1207
39037.3796 | 1925 | 0 | 39037.3796 | 2022 | 0 |  | 1587 | 1761 | 117.5214 | 0 | 123.4432 | 0 | 1.1752 | 0 | 1.2344 | 0 | 1.1752 | 1.2344 | 22.1496 | 16.2898 | 20.9744

## B4-E9
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.265 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 9 | Cable B | Even - | Cable E |  | Odd
Time-69 | N11 | N12 | Time-70 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R9-G | R4-9
39037.3603 | 0 | 0 | 39037.3603 | 0 | 0 |  | -78.5 | 95.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39037.3624 | 0 | 0 | 39037.3624 | 0 | 0 |  | 106.5 | 280.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518376 | 518376 | 518375.9997
39037.3646 | 2507 | 1 | 39037.3646 | 0 | 0 |  | 291 | 465 | 153.0525 | 0.06105 | 0.030525 | 0 | 1.5305 | 0.0006105 | 0.00030525 | 0 | 1.5299 | 0.00030525 | 3.407 | 518375.9999 | 8436.3725
39037.3667 | 2558 | 1 | 39037.3667 | 0 | 0 |  | 475.5 | 649.5 | 156.1661 | 0.06105 | 0.030525 | 0 | 1.5617 | 0.0006105 | 0.00030525 | 0 | 1.5611 | 0.00030525 | 1.3445 | 518375.9999 | 3337.3562
39037.3688 | 2425 | 1 | 39037.3689 | 0 | 0 |  | 660.5 | 834.5 | 148.0464 | 0.06105 | 0.030525 | 0 | 1.4805 | 0.0006105 | 0.00030525 | 0 | 1.4799 | 0.00030525 | 6.9051 | 518375.9999 | 16634.791
39037.371 | 2173 | 1 | 39037.371 | 0 | 0 |  | 845.5 | 1019.5 | 132.6618 | 0.06105 | 0.030525 | 0 | 1.3266 | 0.0006105 | 0.00030525 | 0 | 1.326 | 0.00030525 | 19.3085 | 518375.9999 | 41829.9306
39037.3731 | 2435 | 1 | 39037.3731 | 0 | 0 |  | 1030 | 1204 | 148.6569 | 0.06105 | 0.030525 | 0 | 1.4866 | 0.0006105 | 0.00030525 | 0 | 1.486 | 0.00030525 | 6.4659 | 518375.9989 | 15634.9839
39037.3753 | 2083 | 1 | 39037.3753 | 0 | 0 |  | 1215 | 1389 | 127.1673 | 0.06105 | 0.030525 | 0 | 1.2717 | 0.0006105 | 0.00030525 | 0 | 1.2711 | 0.00030525 | 24.4659 | 518375.9999 | 50828.1947
39037.3774 | 2576 | 1 | 39037.3774 | 0 | 0 |  | 1399.5 | 1573.5 | 157.265 | 0.06105 | 0.030525 | 0 | 1.5726 | 0.0006105 | 0.00030525 | 0 | 1.572 | 0.00030525 | 0.63612 | 518376.0009 | 1537.7034
39037.3795 | 2361 | 0 | 39037.3795 | 2240 | 0 |  | 1584.5 | 1758.5 | 144.1392 | 0 | 136.7521 | 0 | 1.4414 | 0 | 1.3675 | 0 | 1.4414 | 1.3675 | 9.8001 | 15.7312 | 8.3587

## B4-D8
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 160.0965 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 8 | Cable B | Even - | Cable D |  | Even
Time-67 | N11 | N12 | Time-68 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R8-G | R4-8
39037.3603 | 0 | 0 | 39037.3603 | 0 | 0 |  | -81.5 | 92.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39037.3624 | 0 | 0 | 39037.3624 | 0 | 0 |  | 103.5 | 277.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 524376 | 524376 | 524375.9997
39037.3645 | 2165 | 0 | 39037.3645 | 2423 | 0 |  | 288.5 | 462.5 | 132.1734 | 0 | 147.9243 | 0 | 1.3217 | 0 | 1.4792 | 0 | 1.3217 | 1.4792 | 21.1261 | 8.2286 | 19.8044
39037.3667 | 2241 | 0 | 39037.3667 | 2033 | 0 |  | 473 | 647 | 136.8132 | 0 | 124.1148 | 0 | 1.3681 | 0 | 1.2411 | 0 | 1.3681 | 1.2411 | 17.0183 | 28.9907 | 15.6502
39037.3688 | 2292 | 0 | 39037.3688 | 2590 | 0 |  | 657.5 | 831.5 | 139.9267 | 0 | 158.1197 | 0 | 1.3993 | 0 | 1.5812 | 0 | 1.3993 | 1.5812 | 14.4145 | 1.2502 | 13.0152
39037.3709 | 1992 | 0 | 39037.371 | 2350 | 0 |  | 842.5 | 1016.5 | 121.6117 | 0 | 143.4676 | 0 | 1.2161 | 0 | 1.4347 | 0 | 1.2161 | 1.4347 | 31.6456 | 11.5906 | 30.4295
39037.3731 | 2306 | 0 | 39037.3731 | 2606 | 0 |  | 1027.5 | 1201.5 | 140.7814 | 0 | 159.0965 | 0 | 1.4078 | 0 | 1.591 | 0 | 1.4078 | 1.591 | 13.7199 | 0.62855 | 12.312
39037.3752 | 2222 | 0 | 39037.3752 | 2012 | 0 |  | 1212 | 1386 | 135.6532 | 0 | 122.8327 | 0 | 1.3565 | 0 | 1.2283 | 0 | 1.3565 | 1.2283 | 18.0189 | 30.337 | 16.6624
39037.3774 | 2394 | 0 | 39037.3774 | 2476 | 0 |  | 1397 | 1571 | 146.1538 | 0 | 151.16 | 0 | 1.4615 | 0 | 1.5116 | 0 | 1.4615 | 1.5116 | 9.5397 | 5.912 | 8.0781
39037.3795 | 1994 | 0 | 39037.3795 | 2498 | 0 |  | 1581.5 | 1755.5 | 121.7338 | 0 | 152.5031 | 0 | 1.2173 | 0 | 1.525 | 0 | 1.2173 | 1.525 | 31.5135 | 4.9792 | 30.2962

## B4-D7
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 160.4017 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 7 | Cable B | Even - | Cable D |  | Odd
Time-65 | N11 | N12 | Time-66 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R7-G | R4-7
39037.3602 | 0 | 0 | 39037.3602 | 0 | 0 |  | -84 | 90 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525376 | 525376 | 525375.9997
39037.3624 | 0 | 0 | 39037.3624 | 0 | 0 |  | 100.5 | 274.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 525376 | 525376 | 525375.9997
39037.3645 | 2320 | 0 | 39037.3645 | 2175 | 0 |  | 285.5 | 459.5 | 141.6361 | 0 | 132.7839 | 0 | 1.4164 | 0 | 1.3278 | 0 | 1.4164 | 1.3278 | 13.2491 | 20.7991 | 11.8328
39037.3666 | 2236 | 0 | 39037.3667 | 1990 | 0 |  | 470 | 644 | 136.5079 | 0 | 121.4896 | 0 | 1.3651 | 0 | 1.2149 | 0 | 1.3651 | 1.2149 | 17.5036 | 32.0291 | 16.1385
39037.3688 | 2056 | 0 | 39037.3688 | 2248 | 0 |  | 655 | 829 | 125.5189 | 0 | 137.2405 | 0 | 1.2552 | 0 | 1.3724 | 0 | 1.2552 | 1.3724 | 27.7909 | 16.8763 | 26.5357
39037.3709 | 2546 | 0 | 39037.3709 | 2579 | 0 |  | 839.5 | 1013.5 | 155.4335 | 0 | 157.4481 | 0 | 1.5543 | 0 | 1.5745 | 0 | 1.5543 | 1.5745 | 3.1964 | 1.8759 | 1.6421
39037.3731 | 1996 | 0 | 39037.3731 | 2611 | 0 |  | 1024.5 | 1198.5 | 121.8559 | 0 | 159.4017 | 0 | 1.2186 | 0 | 1.594 | 0 | 1.2186 | 1.594 | 31.6323 | 0.62735 | 30.4137
39037.3752 | 2065 | 0 | 39037.3752 | 1995 | 0 |  | 1209.5 | 1383.5 | 126.0684 | 0 | 121.7949 | 0 | 1.2607 | 0 | 1.2179 | 0 | 1.2607 | 1.2179 | 27.2339 | 31.6982 | 25.9732
39037.3773 | 2009 | 0 | 39037.3773 | 2064 | 0 |  | 1394 | 1568 | 122.6496 | 0 | 126.0073 | 0 | 1.2265 | 0 | 1.2601 | 0 | 1.2265 | 1.2601 | 30.7805 | 27.2955 | 29.554
39037.3795 | 2484 | 0 | 39037.3795 | 2226 | 0 |  | 1578.5 | 1752.5 | 151.6484 | 0 | 135.8974 | 0 | 1.5165 | 0 | 1.359 | 0 | 1.5165 | 1.359 | 5.7721 | 18.0314 | 4.2557

## B4-C6
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.9219 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 6 | Cable B | Even - | Cable C |  | Even
Time-63 | N11 | N12 | Time-64 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R6-G | R4-6
39037.3602 | 0 | 0 | 39037.3602 | 0 | 0 |  | -87 | 87 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513976 | 513976 | 513975.9997
39037.3623 | 0 | 0 | 39037.3623 | 0 | 0 |  | 98 | 272 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513976 | 513976 | 513975.9997
39037.3645 | 1928 | 1 | 39037.3645 | 0 | 0 |  | 282.5 | 456.5 | 117.7045 | 0.06105 | 0.030525 | 0 | 1.177 | 0.0006105 | 0.00030525 | 0 | 1.1764 | 0.00030525 | 33.3358 | 513975.9996 | 64125.5236
39037.3666 | 2104 | 0 | 39037.3666 | 1931 | 0 |  | 467.5 | 641.5 | 128.4493 | 0 | 117.8877 | 0 | 1.2845 | 0 | 1.1789 | 0 | 1.2845 | 1.1789 | 22.1663 | 33.1113 | 20.8819
39037.3687 | 2130 | 0 | 39037.3688 | 2554 | 0 |  | 652 | 826 | 130.0366 | 0 | 155.9219 | 0 | 1.3004 | 0 | 1.5592 | 0 | 1.3004 | 1.5592 | 20.6751 | 0.64135 | 19.3748
39037.3709 | 2024 | 0 | 39037.3709 | 2227 | 0 |  | 837 | 1011 | 123.5653 | 0 | 135.9585 | 0 | 1.2357 | 0 | 1.3596 | 0 | 1.2357 | 1.3596 | 26.9951 | 15.4189 | 25.7594
39037.373 | 2076 | 0 | 39037.373 | 2048 | 0 |  | 1021.5 | 1195.5 | 126.7399 | 0 | 125.0305 | 0 | 1.2674 | 0 | 1.2503 | 0 | 1.2674 | 1.2503 | 23.8141 | 25.5068 | 22.5467
39037.3752 | 2072 | 0 | 39037.3752 | 2019 | 0 |  | 1206.5 | 1380.5 | 126.4957 | 0 | 123.2601 | 0 | 1.265 | 0 | 1.2326 | 0 | 1.265 | 1.2326 | 24.0531 | 27.3096 | 22.7881
39037.3773 | 2526 | 0 | 39037.3773 | 2160 | 0 |  | 1391.5 | 1565.5 | 154.2125 | 0 | 131.8681 | 0 | 1.5421 | 0 | 1.3187 | 0 | 1.5421 | 1.3187 | 1.7569 | 18.9991 | 0.2148
39037.3794 | 2038 | 0 | 39037.3795 | 1958 | 0 |  | 1576 | 1750 | 124.42 | 0 | 119.536 | 0 | 1.2442 | 0 | 1.1954 | 0 | 1.2442 | 1.1954 | 26.1227 | 31.2758 | 24.8785

## B4-C5
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.4481 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 4 & 5 | Cable B | Even - | Cable C |  | Odd
Time-61 | N11 | N12 | Time-62 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R4-G | R5-G | R4-5
39037.3602 | 0 | 0 | 39037.3602 | 0 | 0 |  | -89.5 | 84.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39037.3623 | 0 | 0 | 39037.3623 | 0 | 0 |  | 95 | 269 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39037.3644 | 1566 | 1 | 39037.3644 | 0 | 0 |  | 279.5 | 453.5 | 95.6044 | 0.06105 | 0.030525 | 0 | 0.95604 | 0.0006105 | 0.00030525 | 0 | 0.95543 | 0.00030525 | 65.7751 | 518976.0004 | 102818.1883
39037.3666 | 1995 | 0 | 39037.3666 | 2347 | 0 |  | 464.5 | 638.5 | 121.7949 | 0 | 143.2845 | 0 | 1.2179 | 0 | 1.4328 | 0 | 1.2179 | 1.4328 | 30.0942 | 10.5829 | 28.8763
39037.3687 | 1977 | 0 | 39037.3687 | 2246 | 0 |  | 649.5 | 823.5 | 120.696 | 0 | 137.1184 | 0 | 1.207 | 0 | 1.3712 | 0 | 1.207 | 1.3712 | 31.2787 | 15.5557 | 30.0717
39037.3708 | 2538 | 0 | 39037.3709 | 1990 | 0 |  | 834 | 1008 | 154.9451 | 0 | 121.4896 | 0 | 1.5495 | 0 | 1.2149 | 0 | 1.5495 | 1.2149 | 2.2608 | 30.4211 | 0.71138
39037.373 | 2162 | 0 | 39037.373 | 2206 | 0 |  | 1019 | 1193 | 131.9902 | 0 | 134.6764 | 0 | 1.3199 | 0 | 1.3468 | 0 | 1.3199 | 1.3468 | 20.0453 | 17.651 | 18.7254
39037.3751 | 2096 | 0 | 39037.3751 | 2579 | 0 |  | 1203.5 | 1377.5 | 127.9609 | 0 | 157.4481 | 0 | 1.2796 | 0 | 1.5745 | 0 | 1.2796 | 1.5745 | 23.8254 | 0.63513 | 22.5458
39037.3773 | 2262 | 0 | 39037.3773 | 2100 | 0 |  | 1388.5 | 1562.5 | 138.0952 | 0 | 128.2051 | 0 | 1.381 | 0 | 1.2821 | 0 | 1.381 | 1.2821 | 14.7383 | 23.5895 | 13.3573
39037.3794 | 1891 | 0 | 39037.3794 | 2454 | 0 |  | 1573.5 | 1747.5 | 115.4457 | 0 | 149.8168 | 0 | 1.1545 | 0 | 1.4982 | 0 | 1.1545 | 1.4982 | 37.2491 | 5.7612 | 36.0946

## B3-E10
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.7998 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 10 | Ch. 3 & 9 | Cable B | Odd - |  | Cable E | Even
Time-55 | N11 | N12 | Time-56 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R10-G | R3-10
39037.3601 | 0 | 0 | 39037.3601 | 0 | 0 |  | -98 | 76 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513576 | 513576 | 513575.9997
39037.3622 | 0 | 0 | 39037.3622 | 0 | 0 |  | 86.5 | 260.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513576 | 513576 | 513575.9997
39037.3643 | 2078 | 1 | 39037.3644 | 0 | 0 |  | 271.5 | 445.5 | 126.862 | 0.06105 | 0.030525 | 0 | 1.2686 | 0.0006105 | 0.00030525 | 0 | 1.268 | 0.00030525 | 23.61 | 513576.0001 | 48928.473
39037.3665 | 2552 | 1 | 39037.3665 | 0 | 0 |  | 456.5 | 630.5 | 155.7998 | 0.06105 | 0.030525 | 0 | 1.558 | 0.0006105 | 0.00030525 | 0 | 1.5574 | 0.00030525 | 0.6421 | 513576.0001 | 1537.7006
39037.3686 | 1955 | 1 | 39037.3686 | 0 | 0 |  | 641 | 815 | 119.3529 | 0.06105 | 0.030525 | 0 | 1.1935 | 0.0006105 | 0.00030525 | 0 | 1.1929 | 0.00030525 | 31.391 | 513576.0001 | 61226.0785
39037.3708 | 2360 | 1 | 39037.3708 | 0 | 0 |  | 825.5 | 999.5 | 144.0781 | 0.06105 | 0.030525 | 0 | 1.4408 | 0.0006105 | 0.00030525 | 0 | 1.4402 | 0.00030525 | 8.8334 | 513576.0001 | 20733.9628
39037.3729 | 2133 | 1 | 39037.3729 | 0 | 0 |  | 1010.5 | 1184.5 | 130.2198 | 0.06105 | 0.030525 | 0 | 1.3022 | 0.0006105 | 0.00030525 | 0 | 1.3016 | 0.00030525 | 20.4212 | 513576.0001 | 43429.5437
39037.375 | 2039 | 1 | 39037.375 | 0 | 0 |  | 1195.5 | 1369.5 | 124.4811 | 0.06105 | 0.030525 | 0 | 1.2448 | 0.0006105 | 0.00030525 | 0 | 1.2442 | 0.00030525 | 25.9755 | 513576.0001 | 52827.7137
39037.3772 | 2480 | 1 | 39037.3772 | 0 | 0 |  | 1380 | 1554 | 151.4042 | 0.06105 | 0.030525 | 0 | 1.514 | 0.0006105 | 0.00030525 | 0 | 1.5134 | 0.00030525 | 3.5651 | 513576.0001 | 8736.2989
39037.3793 | 1927 | 0 | 39037.3793 | 2052 | 0 |  | 1565 | 1739 | 117.6435 | 0 | 125.2747 | 0 | 1.1764 | 0 | 1.2527 | 0 | 1.1764 | 1.2527 | 33.2839 | 25.1647 | 32.1074

## B3-E9
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 149.9621 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 9 | Cable B | Odd - | Cable E |  | Odd
Time-53 | N11 | N12 | Time-54 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R9-G | R3-9
39037.36 | 0 | 0 | 39037.36 | 0 | 0 |  | -101 | 73 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 491176 | 491176 | 491175.9997
39037.3622 | 0 | 0 | 39037.3622 | 0 | 0 |  | 84 | 258 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 491176 | 491176 | 491175.9997
39037.3643 | 2078 | 1 | 39037.3643 | 0 | 0 |  | 268.5 | 442.5 | 126.862 | 0.06105 | 0.030525 | 0 | 1.2686 | 0.0006105 | 0.00030525 | 0 | 1.268 | 0.00030525 | 18.2176 | 491176.0003 | 37730.3184
39037.3664 | 2178 | 1 | 39037.3665 | 0 | 0 |  | 453.5 | 627.5 | 132.967 | 0.06105 | 0.030525 | 0 | 1.3297 | 0.0006105 | 0.00030525 | 0 | 1.3291 | 0.00030525 | 12.7873 | 491176.0012 | 27732.3539
39037.3686 | 2087 | 1 | 39037.3686 | 0 | 0 |  | 638 | 812 | 127.4115 | 0.06105 | 0.030525 | 0 | 1.2741 | 0.0006105 | 0.00030525 | 0 | 1.2735 | 0.00030525 | 17.7076 | 491175.9994 | 36830.5016
39037.3707 | 1978 | 1 | 39037.3707 | 0 | 0 |  | 823 | 997 | 120.757 | 0.06105 | 0.030525 | 0 | 1.2076 | 0.0006105 | 0.00030525 | 0 | 1.207 | 0.00030525 | 24.1973 | 491176.0003 | 47728.2829
39037.3729 | 2160 | 1 | 39037.3729 | 0 | 0 |  | 1007.5 | 1181.5 | 131.8681 | 0.06105 | 0.030525 | 0 | 1.3187 | 0.0006105 | 0.00030525 | 0 | 1.3181 | 0.00030525 | 13.7277 | 491176.0003 | 29531.9875
39037.375 | 2218 | 1 | 39037.375 | 0 | 0 |  | 1192.5 | 1366.5 | 135.409 | 0.06105 | 0.030525 | 0 | 1.3541 | 0.0006105 | 0.00030525 | 0 | 1.3535 | 0.00030525 | 10.7524 | 491175.9994 | 23733.1681
39037.3771 | 2440 | 1 | 39037.3772 | 0 | 0 |  | 1377.5 | 1551.5 | 148.9621 | 0.06105 | 0.030525 | 0 | 1.4896 | 0.0006105 | 0.00030525 | 0 | 1.489 | 0.00030525 | 0.67159 | 491176.0003 | 1537.6869
39037.3793 | 2208 | 0 | 39037.3793 | 1917 | 0 |  | 1562 | 1736 | 134.7985 | 0 | 117.033 | 0 | 1.348 | 0 | 1.1703 | 0 | 1.348 | 1.1703 | 11.2491 | 28.1367 | 9.9011

## B3-D8
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 149.2906 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 8 | Cable B | Odd - | Cable D |  | Even
Time-51 | N11 | N12 | Time-52 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R8-G | R3-8
39037.36 | 0 | 0 | 39037.36 | 0 | 0 |  | -103.5 | 70.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 488976 | 488976 | 488975.9997
39037.3621 | 0 | 0 | 39037.3622 | 0 | 0 |  | 81 | 255 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 488976 | 488976 | 488975.9997
39037.3643 | 265 | 0 | 39037.3643 | 2089 | 0 |  | 266 | 440 | 16.1783 | 0 | 127.5336 | 0 | 0.16178 | 0 | 1.2753 | 0 | 0.16178 | 1.2753 | 822.7849 | 17.0598 | 822.6231
39037.3664 | 2393 | 0 | 39037.3664 | 2400 | 0 |  | 450.5 | 624.5 | 146.0928 | 0 | 146.5201 | 0 | 1.4609 | 0 | 1.4652 | 0 | 1.4609 | 1.4652 | 2.1889 | 1.8908 | 0.72796
39037.3686 | 1970 | 0 | 39037.3686 | 2020 | 0 |  | 635.5 | 809.5 | 120.2686 | 0 | 123.3211 | 0 | 1.2027 | 0 | 1.2332 | 0 | 1.2027 | 1.2332 | 24.131 | 21.0584 | 22.9283
39037.3707 | 2194 | 0 | 39037.3707 | 2119 | 0 |  | 820 | 994 | 133.9438 | 0 | 129.3651 | 0 | 1.3394 | 0 | 1.2937 | 0 | 1.3394 | 1.2937 | 11.4576 | 15.4025 | 10.1182
39037.3728 | 2035 | 0 | 39037.3728 | 2343 | 0 |  | 1005 | 1179 | 124.2369 | 0 | 143.0403 | 0 | 1.2424 | 0 | 1.4304 | 0 | 1.2424 | 1.4304 | 20.1661 | 4.3696 | 18.9237
39037.375 | 2012 | 0 | 39037.375 | 2246 | 0 |  | 1189.5 | 1363.5 | 122.8327 | 0 | 137.1184 | 0 | 1.2283 | 0 | 1.3712 | 0 | 1.2283 | 1.3712 | 21.5398 | 8.8771 | 20.3114
39037.3771 | 2022 | 0 | 39037.3771 | 2028 | 0 |  | 1374.5 | 1548.5 | 123.4432 | 0 | 123.8095 | 0 | 1.2344 | 0 | 1.2381 | 0 | 1.2344 | 1.2381 | 20.9387 | 20.5809 | 19.7042
39037.3792 | 2429 | 0 | 39037.3793 | 2207 | 0 |  | 1559 | 1733 | 148.2906 | 0 | 134.7375 | 0 | 1.4829 | 0 | 1.3474 | 0 | 1.4829 | 1.3474 | 0.67435 | 10.8011 | 0.80855

## B3-D7
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 157.5934 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 7 | Cable B | Odd - | Cable D |  | Odd
Time-49 | N11 | N12 | Time-50 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R7-G | R3-7
39037.36 | 0 | 0 | 39037.36 | 0 | 0 |  | -106.5 | 67.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39037.3621 | 0 | 0 | 39037.3621 | 0 | 0 |  | 78.5 | 252.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516176 | 516176 | 516175.9997
39037.3642 | 233 | 0 | 39037.3643 | 1591 | 0 |  | 263 | 437 | 14.2247 | 0 | 97.1306 | 0 | 0.14225 | 0 | 0.97131 | 0 | 0.14225 | 0.97131 | 1007.8884 | 62.2489 | 1007.7462
39037.3664 | 2541 | 0 | 39037.3664 | 2024 | 0 |  | 447.5 | 621.5 | 155.1282 | 0 | 123.5653 | 0 | 1.5513 | 0 | 1.2357 | 0 | 1.5513 | 1.2357 | 1.5891 | 27.5385 | 0.037856
39037.3685 | 2044 | 0 | 39037.3685 | 1995 | 0 |  | 632.5 | 806.5 | 124.7863 | 0 | 121.7949 | 0 | 1.2479 | 0 | 1.2179 | 0 | 1.2479 | 1.2179 | 26.2906 | 29.3925 | 25.0427
39037.3707 | 2525 | 0 | 39037.3707 | 2097 | 0 |  | 817.5 | 991.5 | 154.1514 | 0 | 128.022 | 0 | 1.5415 | 0 | 1.2802 | 0 | 1.5415 | 1.2802 | 2.2329 | 23.0987 | 0.69136
39037.3728 | 2206 | 0 | 39037.3728 | 2565 | 0 |  | 1002 | 1176 | 134.6764 | 0 | 156.5934 | 0 | 1.3468 | 0 | 1.5659 | 0 | 1.3468 | 1.5659 | 17.0163 | 0.6386 | 15.6696
39037.3749 | 2238 | 0 | 39037.375 | 2201 | 0 |  | 1187 | 1361 | 136.63 | 0 | 134.3712 | 0 | 1.3663 | 0 | 1.3437 | 0 | 1.3663 | 1.3437 | 15.3432 | 17.2821 | 13.9769
39037.3771 | 2482 | 0 | 39037.3771 | 2038 | 0 |  | 1371.5 | 1545.5 | 151.5263 | 0 | 124.42 | 0 | 1.5153 | 0 | 1.2442 | 0 | 1.5153 | 1.2442 | 4.004 | 26.6624 | 2.4888
39037.3792 | 2077 | 0 | 39037.3792 | 2200 | 0 |  | 1556.5 | 1730.5 | 126.801 | 0 | 134.3101 | 0 | 1.268 | 0 | 1.3431 | 0 | 1.268 | 1.3431 | 24.2841 | 17.3355 | 23.0161

## B3-C6
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.0672 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 6 | Cable B | Odd - | Cable C |  | Even
Time-47 | N11 | N12 | Time-48 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R6-G | R3-6
39037.3599 | 0 | 0 | 39037.3599 | 0 | 0 |  | -109.5 | 64.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39037.3621 | 0 | 0 | 39037.3621 | 0 | 0 |  | 75.5 | 249.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511176 | 511176 | 511175.9997
39037.3642 | 386 | 1 | 39037.3642 | 0 | 0 |  | 260.5 | 434.5 | 23.5653 | 0.06105 | 0.030525 | 0 | 0.23565 | 0.0006105 | 0.00030525 | 0 | 0.23504 | 0.00030525 | 563.7354 | 511176 | 216895.5693
39037.3663 | 2216 | 0 | 39037.3664 | 2320 | 0 |  | 445 | 619 | 135.2869 | 0 | 141.6361 | 0 | 1.3529 | 0 | 1.4164 | 0 | 1.3529 | 1.4164 | 15.3601 | 10.1888 | 14.0072
39037.3685 | 2529 | 0 | 39037.3685 | 2538 | 0 |  | 629.5 | 803.5 | 154.3956 | 0 | 154.9451 | 0 | 1.544 | 0 | 1.5495 | 0 | 1.544 | 1.5495 | 1.0826 | 0.72419 | 0.46131
39037.3706 | 2058 | 0 | 39037.3706 | 2020 | 0 |  | 814.5 | 988.5 | 125.641 | 0 | 123.3211 | 0 | 1.2564 | 0 | 1.2332 | 0 | 1.2564 | 1.2332 | 24.2167 | 26.5535 | 22.9603
39037.3728 | 2115 | 0 | 39037.3728 | 2499 | 0 |  | 999.5 | 1173.5 | 129.1209 | 0 | 152.5641 | 0 | 1.2912 | 0 | 1.5256 | 0 | 1.2912 | 1.5256 | 20.869 | 2.2961 | 19.5778
39037.3749 | 2540 | 0 | 39037.3749 | 2075 | 0 |  | 1184 | 1358 | 155.0672 | 0 | 126.6789 | 0 | 1.5507 | 0 | 1.2668 | 0 | 1.5507 | 1.2668 | 0.64488 | 23.199 | 0.90579
39037.377 | 1964 | 0 | 39037.377 | 2042 | 0 |  | 1368.5 | 1542.5 | 119.9023 | 0 | 124.6642 | 0 | 1.199 | 0 | 1.2466 | 0 | 1.199 | 1.2466 | 30.1619 | 25.19 | 28.9629
39037.3792 | 1929 | 0 | 39037.3792 | 2174 | 0 |  | 1553.5 | 1727.5 | 117.7656 | 0 | 132.7228 | 0 | 1.1777 | 0 | 1.3272 | 0 | 1.1777 | 1.3272 | 32.5236 | 17.5888 | 31.3459

## B3-C5
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.9829 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 5 | Cable B | Odd - | Cable C |  | Odd
Time-45 | N11 | N12 | Time-46 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R5-G | R3-5
39037.3599 | 0 | 0 | 39037.3599 | 0 | 0 |  | -112 | 62 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514176 | 514176 | 514175.9997
39037.362 | 0 | 0 | 39037.362 | 0 | 0 |  | 72.5 | 246.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 514176 | 514176 | 514175.9997
39037.3642 | 244 | 1 | 39037.3642 | 0 | 0 |  | 257.5 | 431.5 | 14.8962 | 0.06105 | 0.030525 | 0 | 0.14896 | 0.0006105 | 0.00030525 | 0 | 0.14835 | 0.00030525 | 957.7703 | 514176.0001 | 232592.764
39037.3663 | 2333 | 0 | 39037.3663 | 1918 | 0 |  | 442 | 616 | 142.4298 | 0 | 117.094 | 0 | 1.4243 | 0 | 1.1709 | 0 | 1.4243 | 1.1709 | 10.2177 | 34.0657 | 8.7934
39037.3684 | 2555 | 0 | 39037.3685 | 2319 | 0 |  | 627 | 801 | 155.9829 | 0 | 141.5751 | 0 | 1.5598 | 0 | 1.4158 | 0 | 1.5598 | 1.4158 | 0.6411 | 10.8831 | 0.91873
39037.3706 | 2132 | 0 | 39037.3706 | 2256 | 0 |  | 811.5 | 985.5 | 130.1587 | 0 | 137.7289 | 0 | 1.3016 | 0 | 1.3773 | 0 | 1.3016 | 1.3773 | 20.6088 | 13.9796 | 19.3072
39037.3727 | 2482 | 0 | 39037.3727 | 2248 | 0 |  | 996.5 | 1170.5 | 151.5263 | 0 | 137.2405 | 0 | 1.5153 | 0 | 1.3724 | 0 | 1.5153 | 1.3724 | 3.6011 | 14.3852 | 2.0859
39037.3749 | 2185 | 0 | 39037.3749 | 2091 | 0 |  | 1181.5 | 1355.5 | 133.3944 | 0 | 127.6557 | 0 | 1.3339 | 0 | 1.2766 | 0 | 1.3339 | 1.2766 | 17.6833 | 22.9737 | 16.3494
39037.377 | 2357 | 0 | 39037.377 | 2299 | 0 |  | 1366 | 1540 | 143.895 | 0 | 140.3541 | 0 | 1.4389 | 0 | 1.4035 | 0 | 1.4389 | 1.4035 | 9.0955 | 11.8478 | 7.6565
39037.3791 | 2419 | 0 | 39037.3792 | 2325 | 0 |  | 1550.5 | 1724.5 | 147.6801 | 0 | 141.9414 | 0 | 1.4768 | 0 | 1.4194 | 0 | 1.4768 | 1.4194 | 6.2993 | 10.597 | 4.8225

## B3-B4
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 155.6398 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 3 & 4 | Cable B | Odd -Even
Time-43 | N11 | N12 | Time-44 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R3-G | R4-G | R3-4
39037.3599 | 0 | 0 | 39037.3599 | 0 | 0 |  | -115 | 59 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509776 | 509776 | 509775.9997
39037.362 | 0 | 0 | 39037.362 | 0 | 0 |  | 70 | 244 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 509776 | 509776 | 509775.9997
39037.3641 | 90 | 1 | 39037.3642 | 860 | 1 |  | 254.5 | 428.5 | 5.4945 | 0.06105 | 52.5031 | 0.06105 | 0.054945 | 0.0006105 | 0.52503 | 0.0006105 | 0.054335 | 0.52442 | 2779.2258 | 196.6765 | 162973.9931
39037.3663 | 2533 | 0 | 39037.3663 | 2495 | 0 |  | 439.5 | 613.5 | 154.6398 | 0 | 152.3199 | 0 | 1.5464 | 0 | 1.5232 | 0 | 1.5464 | 1.5232 | 0.64666 | 2.1796 | 0.89973
39037.3684 | 2464 | 0 | 39037.3684 | 2471 | 0 |  | 624 | 798 | 150.4274 | 0 | 150.8547 | 0 | 1.5043 | 0 | 1.5085 | 0 | 1.5043 | 1.5085 | 3.4651 | 3.172 | 1.9608
39037.3706 | 2513 | 0 | 39037.3706 | 1963 | 0 |  | 809 | 983 | 153.4188 | 0 | 119.8413 | 0 | 1.5342 | 0 | 1.1984 | 0 | 1.5342 | 1.1984 | 1.4477 | 29.8716 | 0.086516
39037.3727 | 2315 | 0 | 39037.3727 | 2510 | 0 |  | 993.5 | 1167.5 | 141.3309 | 0 | 153.2357 | 0 | 1.4133 | 0 | 1.5324 | 0 | 1.4133 | 1.5324 | 10.1244 | 1.5689 | 8.7111
39037.3748 | 2480 | 0 | 39037.3748 | 2162 | 0 |  | 1178.5 | 1352.5 | 151.4042 | 0 | 131.9902 | 0 | 1.514 | 0 | 1.3199 | 0 | 1.514 | 1.3199 | 2.7976 | 17.9177 | 1.2835
39037.377 | 2032 | 0 | 39037.377 | 2102 | 0 |  | 1363.5 | 1537.5 | 124.0537 | 0 | 128.3272 | 0 | 1.2405 | 0 | 1.2833 | 0 | 1.2405 | 1.2833 | 25.4616 | 21.2835 | 24.2211
39037.3791 | 2458 | 2 | 39037.3791 | 2001 | 2 |  | 1548 | 1722 | 150.0611 | 0.1221 | 122.1612 | 0.1221 | 1.5006 | 0.001221 | 1.2216 | 0.001221 | 1.4994 | 1.2204 | 3.7315 | 28.1885 | 982.7284

## A2-C6
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.4481 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 6 | Cable A | Even - | Cable C |  | Even
Time-29 | N11 | N12 | Time-30 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R6-G | R2-6
39037.3596 | 0 | 0 | 39037.3597 | 0 | 0 |  | -134.5 | 39.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39037.3618 | 0 | 0 | 39037.3618 | 0 | 0 |  | 50.5 | 224.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39037.3639 | 0 | 0 | 39037.3639 | 0 | 0 |  | 235 | 409 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 518976 | 518976 | 518975.9997
39037.3661 | 917 | 0 | 39037.3661 | 2162 | 0 |  | 419.5 | 593.5 | 55.9829 | 0 | 131.9902 | 0 | 0.55983 | 0 | 1.3199 | 0 | 0.55983 | 1.3199 | 183.0294 | 20.0453 | 182.4696
39037.3682 | 2290 | 0 | 39037.3682 | 2284 | 0 |  | 604.5 | 778.5 | 139.8046 | 0 | 139.4383 | 0 | 1.398 | 0 | 1.3944 | 0 | 1.398 | 1.3944 | 13.3354 | 13.6331 | 11.9373
39037.3703 | 2039 | 0 | 39037.3703 | 2542 | 0 |  | 789.5 | 963.5 | 124.4811 | 0 | 155.1893 | 0 | 1.2448 | 0 | 1.5519 | 0 | 1.2448 | 1.5519 | 27.2869 | 2.0999 | 26.0421
39037.3725 | 2544 | 0 | 39037.3725 | 2567 | 0 |  | 974 | 1148 | 155.3114 | 0 | 156.7155 | 0 | 1.5531 | 0 | 1.5672 | 0 | 1.5531 | 1.5672 | 2.0197 | 1.1056 | 0.46654
39037.3746 | 2579 | 0 | 39037.3746 | 2071 | 0 |  | 1159 | 1333 | 157.4481 | 0 | 126.4347 | 0 | 1.5745 | 0 | 1.2643 | 0 | 1.5745 | 1.2643 | 0.63513 | 25.3201 | 0.93935
39037.3767 | 2359 | 0 | 39037.3768 | 2022 | 0 |  | 1343.5 | 1517.5 | 144.0171 | 0 | 123.4432 | 0 | 1.4402 | 0 | 1.2344 | 0 | 1.4402 | 1.2344 | 10.0203 | 28.3571 | 8.5802
39037.3789 | 1963 | 0 | 39037.3789 | 2092 | 1 |  | 1528.5 | 1702.5 | 119.8413 | 0 | 127.7167 | 0.06105 | 1.1984 | 0 | 1.2772 | 0.0006105 | 1.1984 | 1.2766 | 32.215 | 24.1215 | 31.0166

## A2-C5
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 157.7766 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 5 | Cable A | Even - | Cable C |  | Odd
Time-27 | N11 | N12 | Time-28 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R5-G | R2-5
39037.3596 | 0 | 0 | 39037.3596 | 0 | 0 |  | -137.5 | 36.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516776 | 516776 | 516775.9997
39037.3617 | 0 | 0 | 39037.3618 | 0 | 0 |  | 47.5 | 221.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516776 | 516776 | 516775.9997
39037.3639 | 0 | 0 | 39037.3639 | 0 | 0 |  | 232 | 406 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 516776 | 516776 | 516775.9997
39037.366 | 731 | 0 | 39037.366 | 1744 | 0 |  | 417 | 591 | 44.6276 | 0 | 106.4713 | 0 | 0.44628 | 0 | 1.0647 | 0 | 0.44628 | 1.0647 | 253.5404 | 48.1869 | 253.0941
39037.3682 | 2540 | 0 | 39037.3682 | 1968 | 0 |  | 601.5 | 775.5 | 155.0672 | 0 | 120.1465 | 0 | 1.5507 | 0 | 1.2015 | 0 | 1.5507 | 1.2015 | 1.7472 | 31.3201 | 0.19657
39037.3703 | 2436 | 0 | 39037.3703 | 1989 | 0 |  | 786.5 | 960.5 | 148.7179 | 0 | 121.4286 | 0 | 1.4872 | 0 | 1.2143 | 0 | 1.4872 | 1.2143 | 6.0911 | 29.9336 | 4.604
39037.3724 | 2195 | 0 | 39037.3725 | 2253 | 0 |  | 971.5 | 1145.5 | 134.0049 | 0 | 137.5458 | 0 | 1.34 | 0 | 1.3755 | 0 | 1.34 | 1.3755 | 17.7394 | 14.7084 | 16.3994
39037.3746 | 2404 | 0 | 39037.3746 | 2568 | 0 |  | 1156 | 1330 | 146.7643 | 0 | 156.7766 | 0 | 1.4676 | 0 | 1.5678 | 0 | 1.4676 | 1.5678 | 7.5033 | 0.63785 | 6.0357
39037.3767 | 2493 | 0 | 39037.3767 | 2077 | 0 |  | 1341 | 1515 | 152.1978 | 0 | 126.801 | 0 | 1.522 | 0 | 1.268 | 0 | 1.522 | 1.268 | 3.6655 | 24.4285 | 2.1435
39037.3789 | 2254 | 0 | 39037.3789 | 2556 | 1 |  | 1525.5 | 1699.5 | 137.6068 | 0 | 156.044 | 0.06105 | 1.3761 | 0 | 1.5604 | 0.0006105 | 1.3761 | 1.5598 | 14.6575 | 1.1499 | 13.2814

## A2-B4
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 159.0586 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 4 | Cable A | Even - | Cable B |  | Even
Time-25 | N11 | N12 | Time-26 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R4-G | R2-4
39037.3596 | 0 | 0 | 39037.3596 | 0 | 0 |  | -140 | 34 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39037.3617 | 0 | 0 | 39037.3617 | 0 | 0 |  | 44.5 | 218.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39037.3639 | 0 | 0 | 39037.3639 | 0 | 0 |  | 229.5 | 403.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 520976 | 520976 | 520975.9997
39037.366 | 921 | 0 | 39037.366 | 967 | 0 |  | 414 | 588 | 56.2271 | 0 | 59.0354 | 0 | 0.56227 | 0 | 0.59035 | 0 | 0.56227 | 0.59035 | 182.886 | 169.4292 | 182.3237
39037.3681 | 2428 | 0 | 39037.3681 | 2224 | 0 |  | 599 | 773 | 148.2295 | 0 | 135.7753 | 0 | 1.4823 | 0 | 1.3578 | 0 | 1.4823 | 1.3578 | 7.3056 | 17.1484 | 5.8233
39037.3703 | 2022 | 0 | 39037.3703 | 2381 | 0 |  | 784 | 958 | 123.4432 | 0 | 145.3602 | 0 | 1.2344 | 0 | 1.4536 | 0 | 1.2344 | 1.4536 | 28.8516 | 9.4238 | 27.6172
39037.3724 | 2554 | 0 | 39037.3724 | 2260 | 0 |  | 968.5 | 1142.5 | 155.9219 | 0 | 137.9731 | 0 | 1.5592 | 0 | 1.3797 | 0 | 1.5592 | 1.3797 | 2.0117 | 15.2823 | 0.45253
39037.3745 | 2456 | 0 | 39037.3746 | 2589 | 0 |  | 1153.5 | 1327.5 | 149.9389 | 0 | 158.0586 | 0 | 1.4994 | 0 | 1.5806 | 0 | 1.4994 | 1.5806 | 6.0822 | 0.63268 | 4.5829
39037.3767 | 2264 | 0 | 39037.3767 | 2261 | 0 |  | 1338 | 1512 | 138.2173 | 0 | 138.0342 | 0 | 1.3822 | 0 | 1.3803 | 0 | 1.3822 | 1.3803 | 15.0786 | 15.2313 | 13.6964
39037.3788 | 2281 | 0 | 39037.3788 | 2303 | 0 |  | 1522.5 | 1696.5 | 139.2552 | 0 | 140.5983 | 0 | 1.3926 | 0 | 1.406 | 0 | 1.3926 | 1.406 | 14.221 | 13.1298 | 12.8284

## A2-B3
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.9219 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 2 & 3 | Cable A | Even - | Cable B |  | Odd
Time-23 | N11 | N12 | Time-24 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R2-G | R3-G | R2-3
39037.3595 | 0 | 0 | 39037.3596 | 0 | 0 |  | -143 | 31 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513976 | 513976 | 513975.9997
39037.3617 | 0 | 0 | 39037.3617 | 0 | 0 |  | 42 | 216 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513976 | 513976 | 513975.9997
39037.3638 | 0 | 0 | 39037.3638 | 0 | 0 |  | 226.5 | 400.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 513976 | 513976 | 513975.9997
39037.366 | 622 | 0 | 39037.366 | 2333 | 0 |  | 411.5 | 585.5 | 37.9731 | 0 | 142.4298 | 0 | 0.37973 | 0 | 1.4243 | 0 | 0.37973 | 1.4243 | 313.2444 | 10.1749 | 312.8646
39037.3681 | 2031 | 0 | 39037.3681 | 1998 | 0 |  | 596 | 770 | 123.9927 | 0 | 121.978 | 0 | 1.2399 | 0 | 1.2198 | 0 | 1.2399 | 1.2198 | 26.5574 | 28.6476 | 25.3174
39037.3702 | 1964 | 0 | 39037.3703 | 2554 | 0 |  | 781 | 955 | 119.9023 | 0 | 155.9219 | 0 | 1.199 | 0 | 1.5592 | 0 | 1.199 | 1.5592 | 30.8747 | 0.64135 | 29.6757
39037.3724 | 2427 | 0 | 39037.3724 | 2081 | 0 |  | 965.5 | 1139.5 | 148.1685 | 0 | 127.0452 | 0 | 1.4817 | 0 | 1.2705 | 0 | 1.4817 | 1.2705 | 5.9077 | 23.5166 | 4.426
39037.3745 | 2208 | 0 | 39037.3745 | 2048 | 0 |  | 1150.5 | 1324.5 | 134.7985 | 0 | 125.0305 | 0 | 1.348 | 0 | 1.2503 | 0 | 1.348 | 1.2503 | 16.4121 | 25.5068 | 15.0642
39037.3767 | 2087 | 0 | 39037.3767 | 2340 | 0 |  | 1335.5 | 1509.5 | 127.4115 | 0 | 142.8571 | 0 | 1.2741 | 0 | 1.4286 | 0 | 1.2741 | 1.4286 | 23.1615 | 9.8453 | 21.8874
39037.3788 | 2151 | 0 | 39037.3788 | 2323 | 0 |  | 1520 | 1694 | 131.3187 | 0 | 141.8193 | 0 | 1.3132 | 0 | 1.4182 | 0 | 1.3132 | 1.4182 | 19.497 | 10.6492 | 18.1838

## A1-C6
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 156.1893 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 6 | Cable A | Odd - | Cable C |  | Even
Time-9 | N11 | N12 | Time-10 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R6-G | R1-6
39037.3593 | 0 | 0 | 39037.3593 | 0 | 0 |  | -162.5 | 11.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3615 | 0 | 0 | 39037.3615 | 0 | 0 |  | 22.5 | 196.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3636 | 0 | 0 | 39037.3636 | 0 | 0 |  | 207 | 381 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 511576 | 511576 | 511575.9997
39037.3657 | 929 | 0 | 39037.3657 | 1308 | 0 |  | 391.5 | 565.5 | 56.7155 | 0 | 79.8535 | 0 | 0.56716 | 0 | 0.79853 | 0 | 0.56716 | 0.79853 | 175.3907 | 95.5948 | 174.8236
39037.3679 | 2052 | 0 | 39037.3679 | 1981 | 0 |  | 576.5 | 750.5 | 125.2747 | 0 | 120.9402 | 0 | 1.2527 | 0 | 1.2094 | 0 | 1.2527 | 1.2094 | 24.6774 | 29.1459 | 23.4246
39037.37 | 2512 | 0 | 39037.37 | 2542 | 0 |  | 761.5 | 935.5 | 153.3578 | 0 | 155.1893 | 0 | 1.5336 | 0 | 1.5519 | 0 | 1.5336 | 1.5519 | 1.8463 | 0.64437 | 0.31276
39037.3721 | 2505 | 0 | 39037.3722 | 2165 | 0 |  | 946 | 1120 | 152.9304 | 0 | 132.1734 | 0 | 1.5293 | 0 | 1.3217 | 0 | 1.5293 | 1.3217 | 2.1309 | 18.17 | 0.60163
39037.3743 | 2066 | 0 | 39037.3743 | 1994 | 0 |  | 1131 | 1305 | 126.1294 | 0 | 121.7338 | 0 | 1.2613 | 0 | 1.2173 | 0 | 1.2613 | 1.2173 | 23.8325 | 28.3039 | 22.5712
39037.3764 | 2390 | 0 | 39037.3764 | 2386 | 0 |  | 1315.5 | 1489.5 | 145.9096 | 0 | 145.6654 | 0 | 1.4591 | 0 | 1.4567 | 0 | 1.4591 | 1.4567 | 7.0452 | 7.2246 | 5.5861
39037.3786 | 2173 | 0 | 39037.3786 | 2128 | 0 |  | 1500.5 | 1674.5 | 132.6618 | 0 | 129.9145 | 0 | 1.3266 | 0 | 1.2991 | 0 | 1.3266 | 1.2991 | 17.7349 | 20.2246 | 16.4083

## A1-C5
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.5092 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 5 | Cable A | Odd - | Cable C |  | Odd
Time-7 | N11 | N12 | Time-8 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R5-G | R1-5
39037.3593 | 0 | 0 | 39037.3593 | 0 | 0 |  | -165.5 | 8.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39037.3614 | 0 | 0 | 39037.3614 | 0 | 0 |  | 19.5 | 193.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39037.3636 | 0 | 0 | 39037.3636 | 0 | 0 |  | 204.5 | 378.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 519176 | 519176 | 519175.9997
39037.3657 | 1264 | 0 | 39037.3657 | 1082 | 0 |  | 389 | 563 | 77.1673 | 0 | 66.0562 | 0 | 0.77167 | 0 | 0.66056 | 0 | 0.77167 | 0.66056 | 105.4098 | 139.9612 | 104.6381
39037.3678 | 2485 | 0 | 39037.3678 | 2519 | 0 |  | 573.5 | 747.5 | 151.7094 | 0 | 153.7851 | 0 | 1.5171 | 0 | 1.5379 | 0 | 1.5171 | 1.5379 | 4.4821 | 3.0719 | 2.965
39037.37 | 2070 | 0 | 39037.37 | 2405 | 0 |  | 758.5 | 932.5 | 126.3736 | 0 | 146.8254 | 0 | 1.2637 | 0 | 1.4683 | 0 | 1.2637 | 1.4683 | 25.429 | 7.9576 | 24.1652
39037.3721 | 2054 | 0 | 39037.3721 | 2315 | 0 |  | 943.5 | 1117.5 | 125.3968 | 0 | 141.3309 | 0 | 1.254 | 0 | 1.4133 | 0 | 1.254 | 1.4133 | 26.406 | 12.1546 | 25.1521
39037.3742 | 2376 | 0 | 39037.3743 | 2550 | 0 |  | 1128 | 1302 | 145.0549 | 0 | 155.6777 | 0 | 1.4505 | 0 | 1.5568 | 0 | 1.4505 | 1.5568 | 9.2753 | 1.8188 | 7.8247
39037.3764 | 2580 | 0 | 39037.3764 | 2068 | 0 |  | 1313 | 1487 | 157.5092 | 0 | 126.2515 | 0 | 1.5751 | 0 | 1.2625 | 0 | 1.5751 | 1.2625 | 0.63488 | 25.5503 | 0.94021
39037.3785 | 1929 | 0 | 39037.3785 | 2547 | 0 |  | 1497.5 | 1671.5 | 117.7656 | 0 | 155.4945 | 0 | 1.1777 | 0 | 1.5549 | 0 | 1.1777 | 1.5549 | 34.5972 | 1.9388 | 33.4195

## A1-B4
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 157.2882 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 4 | Cable A | Odd - | Cable B |  | Even
Time-5 | N11 | N12 | Time-6 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R4-G | R1-4
39037.3592 | 0 | 0 | 39037.3593 | 0 | 0 |  | -168 | 6 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39037.3614 | 0 | 0 | 39037.3614 | 0 | 0 |  | 16.5 | 190.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39037.3635 | 0 | 0 | 39037.3635 | 0 | 0 |  | 201.5 | 375.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 515176 | 515176 | 515175.9997
39037.3657 | 1090 | 0 | 39037.3657 | 2522 | 0 |  | 386.5 | 560.5 | 66.5446 | 0 | 153.9683 | 0 | 0.66545 | 0 | 1.5397 | 0 | 0.66545 | 1.5397 | 136.3651 | 2.1562 | 135.6997
39037.3678 | 1953 | 0 | 39037.3678 | 2322 | 0 |  | 571 | 745 | 119.2308 | 0 | 141.7582 | 0 | 1.1923 | 0 | 1.4176 | 0 | 1.1923 | 1.4176 | 31.9191 | 10.9552 | 30.7268
39037.3699 | 2560 | 0 | 39037.37 | 2481 | 0 |  | 755.5 | 929.5 | 156.2882 | 0 | 151.4652 | 0 | 1.5629 | 0 | 1.5147 | 0 | 1.5629 | 1.5147 | 0.63984 | 3.8444 | 0.92304
39037.3721 | 2039 | 0 | 39037.3721 | 2272 | 0 |  | 940.5 | 1114.5 | 124.4811 | 0 | 138.7057 | 0 | 1.2448 | 0 | 1.3871 | 0 | 1.2448 | 1.3871 | 26.3551 | 13.397 | 25.1103
39037.3742 | 2003 | 0 | 39037.3742 | 2006 | 0 |  | 1125.5 | 1299.5 | 122.2833 | 0 | 122.4664 | 0 | 1.2228 | 0 | 1.2247 | 0 | 1.2228 | 1.2247 | 28.6261 | 28.4337 | 27.4032
39037.3764 | 2505 | 0 | 39037.3764 | 2511 | 0 |  | 1310 | 1484 | 152.9304 | 0 | 153.2967 | 0 | 1.5293 | 0 | 1.533 | 0 | 1.5293 | 1.533 | 2.8495 | 2.6037 | 1.3202
39037.3785 | 2007 | 0 | 39037.3785 | 1887 | 0 |  | 1494.5 | 1668.5 | 122.5275 | 0 | 115.2015 | 0 | 1.2253 | 0 | 1.152 | 0 | 1.2253 | 1.152 | 28.3697 | 36.5331 | 27.1444

## A1-B3
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 158.1429 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 3 | Cable A | Odd - | Cable B |  | Odd
Time-3 | N11 | N12 | Time-4 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R3-G | R1-3
39037.3592 | 0 | 0 | 39037.3592 | 0 | 0 |  | -171 | 3 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39037.3614 | 0 | 0 | 39037.3614 | 0 | 0 |  | 14 | 188 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39037.3635 | 0 | 0 | 39037.3635 | 0 | 0 |  | 198.5 | 372.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 517976 | 517976 | 517975.9997
39037.3656 | 661 | 0 | 39037.3656 | 2150 | 0 |  | 383.5 | 557.5 | 40.3541 | 0 | 131.2576 | 0 | 0.40354 | 0 | 1.3126 | 0 | 0.40354 | 1.3126 | 291.888 | 20.4828 | 291.4845
39037.3678 | 2454 | 0 | 39037.3678 | 1981 | 0 |  | 568.5 | 742.5 | 149.8168 | 0 | 120.9402 | 0 | 1.4982 | 0 | 1.2094 | 0 | 1.4982 | 1.2094 | 5.5575 | 30.7612 | 4.0593
39037.3699 | 2072 | 0 | 39037.3699 | 2208 | 0 |  | 753 | 927 | 126.4957 | 0 | 134.7985 | 0 | 1.265 | 0 | 1.348 | 0 | 1.265 | 1.348 | 25.0183 | 17.3179 | 23.7534
39037.372 | 1965 | 0 | 39037.3721 | 2574 | 0 |  | 937.5 | 1111.5 | 119.9634 | 0 | 157.1429 | 0 | 1.1996 | 0 | 1.5714 | 0 | 1.1996 | 1.5714 | 31.826 | 0.63636 | 30.6263
39037.3742 | 2457 | 0 | 39037.3742 | 2462 | 0 |  | 1122.5 | 1296.5 | 150 | 0 | 150.3053 | 0 | 1.5 | 0 | 1.5031 | 0 | 1.5 | 1.5031 | 5.4286 | 5.2145 | 3.9286
39037.3763 | 2346 | 0 | 39037.3763 | 2386 | 0 |  | 1307.5 | 1481.5 | 143.2234 | 0 | 145.6654 | 0 | 1.4322 | 0 | 1.4567 | 0 | 1.4322 | 1.4567 | 10.4169 | 8.5658 | 8.9846
39037.3785 | 2156 | 0 | 39037.3785 | 2411 | 0 |  | 1492 | 1666 | 131.6239 | 0 | 147.1917 | 0 | 1.3162 | 0 | 1.4719 | 0 | 1.3162 | 1.4719 | 20.1475 | 7.4401 | 18.8313

## A1-A2
Open Burn Test 10 |  |  | 2006-11-16 | 8:44 |  |  | Vs = |  | 155.1514 |  | R = | 100
Mix | 7-C | Tray C | IRMS | 2
0 | 250 kW |  | Bundle | Ch. 1 & 2 | Cable A | Odd-Even
Time-1 | N11 | N12 | Time-2 | N21 |  |  | Burner Time | DAQ Time | V11 | V12 | V21 | V22 | I11 | I12 | I21 | I22 | Delta-I1 | Delta-I2 | R1-G | R2-G | R1-2
39037.3592 | 0 | 0 | 39037.3592 | 0 | 0 |  | -173.5 | 0.5 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508176 | 508176 | 508175.9997
39037.3613 | 0 | 0 | 39037.3613 | 0 | 0 |  | 11 | 185 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508176 | 508176 | 508175.9997
39037.3635 | 0 | 0 | 39037.3635 | 0 | 0 |  | 196 | 370 | 0.030525 | 0 | 0.030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0 | 0.00030525 | 0.00030525 | 508176 | 508176 | 508175.9997
39037.3656 | 1309 | 825 | 39037.3656 | 1081 | 1018 |  | 380.5 | 554.5 | 79.9145 | 50.3663 | 65.9951 | 62.149 | 0.79915 | 0.50366 | 0.65995 | 0.62149 | 0.29548 | 0.038462 | 146.5824 | 231.2594 | 34.4728
39037.3677 | 2494 | 1 | 39037.3678 | 2092 | 1 |  | 565.5 | 739.5 | 152.2589 | 0.06105 | 127.7167 | 0.06105 | 1.5226 | 0.0006105 | 1.2772 | 0.0006105 | 1.522 | 1.2766 | 1.904 | 22.0449 | 837.7584
39037.3699 | 2339 | 0 | 39037.3699 | 2519 | 0 |  | 750.5 | 924.5 | 142.7961 | 0 | 153.7851 | 0 | 1.428 | 0 | 1.5379 | 0 | 1.428 | 1.5379 | 8.6524 | 0.88845 | 7.2245
39037.372 | 2227 | 0 | 39037.372 | 1972 | 0 |  | 935 | 1109 | 135.9585 | 0 | 120.3907 | 0 | 1.3596 | 0 | 1.2039 | 0 | 1.3596 | 1.2039 | 14.1167 | 28.8732 | 12.7572
39037.3742 | 2006 | 0 | 39037.3742 | 2027 | 0 |  | 1119.5 | 1293.5 | 122.4664 | 0 | 123.7485 | 0 | 1.2247 | 0 | 1.2375 | 0 | 1.2247 | 1.2375 | 26.6889 | 25.3764 | 25.4643
39037.3763 | 2525 | 0 | 39037.3763 | 2018 | 0 |  | 1304.5 | 1478.5 | 154.1514 | 0 | 123.199 | 0 | 1.5415 | 0 | 1.232 | 0 | 1.5415 | 1.232 | 0.64871 | 25.9356 | 0.8928
39037.3784 | 1947 | 1 | 39037.3784 | 2308 | 0 |  | 1489 | 1663 | 118.8645 | 0.06105 | 140.9035 | 0 | 1.1886 | 0.0006105 | 1.409 | 0 | 1.188 | 1.409 | 30.6997 | 10.1118 | 5449.127

## Temps
DAQ Time | Burner Time | Bundle center | Air above bundle | Air below bundle | Intra-bundle | TRAY C
0 | -174 | 13.3 | 11.9 | 12.1 | 13.6 | 13.5
1 | -173 | 13.3 | 11.9 | 12.1 | 13.6 | 13.5
2 | -172 | 13.3 | 11.9 | 12.1 | 13.6 | 13.5
3 | -171 | 13.3 | 11.9 | 12 | 13.6 | 13.5
4 | -170 | 13.3 | 11.9 | 12 | 13.6 | 13.5
5 | -169 | 13.3 | 11.9 | 12 | 13.6 | 13.5
6 | -168 | 13.3 | 11.9 | 12 | 13.6 | 13.5
7 | -167 | 13.3 | 11.9 | 12 | 13.6 | 13.5
8 | -166 | 13.3 | 11.9 | 12 | 13.6 | 13.5
9 | -165 | 13.3 | 11.9 | 12 | 13.6 | 13.5
10 | -164 | 13.3 | 11.9 | 12 | 13.6 | 13.5
11 | -163 | 13.3 | 11.9 | 12 | 13.6 | 13.5
12 | -162 | 13.3 | 11.9 | 12 | 13.6 | 13.5
13 | -161 | 13.3 | 11.9 | 12 | 13.6 | 13.5
14 | -160 | 13.3 | 11.9 | 12 | 13.6 | 13.5
15 | -159 | 13.3 | 11.9 | 12 | 13.6 | 13.5
16 | -158 | 13.3 | 11.9 | 12 | 13.6 | 13.5
17 | -157 | 13.3 | 11.9 | 12 | 13.6 | 13.5
18 | -156 | 13.3 | 11.9 | 12 | 13.6 | 13.5
19 | -155 | 13.3 | 11.9 | 12 | 13.6 | 13.5
20 | -154 | 13.3 | 11.9 | 12 | 13.6 | 13.5
21 | -153 | 13.3 | 11.9 | 12 | 13.6 | 13.5
22 | -152 | 13.3 | 11.9 | 12 | 13.6 | 13.5
23 | -151 | 13.3 | 11.9 | 12 | 13.6 | 13.5
24 | -150 | 13.3 | 11.9 | 12 | 13.6 | 13.5
25 | -149 | 13.3 | 11.9 | 12 | 13.6 | 13.5
26 | -148 | 13.3 | 11.9 | 12 | 13.6 | 13.5
27 | -147 | 13.3 | 11.8 | 12 | 13.6 | 13.5
28 | -146 | 13.3 | 11.8 | 12 | 13.6 | 13.5
29 | -145 | 13.3 | 11.8 | 12 | 13.6 | 13.5
30 | -144 | 13.3 | 11.8 | 12 | 13.6 | 13.5
31 | -143 | 13.3 | 11.8 | 12 | 13.6 | 13.5
32 | -142 | 13.3 | 11.8 | 12 | 13.6 | 13.5
33 | -141 | 13.3 | 11.8 | 12 | 13.6 | 13.5
34 | -140 | 13.3 | 11.9 | 12 | 13.6 | 13.5
35 | -139 | 13.3 | 11.8 | 12 | 13.6 | 13.5
36 | -138 | 13.3 | 11.8 | 12 | 13.6 | 13.5
37 | -137 | 13.3 | 11.9 | 12 | 13.6 | 13.5
38 | -136 | 13.3 | 11.8 | 12 | 13.6 | 13.5
39 | -135 | 13.3 | 11.9 | 12 | 13.6 | 13.5
40 | -134 | 13.3 | 11.9 | 12 | 13.6 | 13.5
41 | -133 | 13.3 | 11.9 | 12 | 13.6 | 13.5
42 | -132 | 13.3 | 11.9 | 12 | 13.6 | 13.5
43 | -131 | 13.3 | 11.9 | 12 | 13.6 | 13.5
44 | -130 | 13.3 | 11.9 | 12 | 13.6 | 13.5
45 | -129 | 13.3 | 11.9 | 12 | 13.6 | 13.5
46 | -128 | 13.3 | 11.9 | 12 | 13.6 | 13.5
47 | -127 | 13.3 | 11.9 | 12 | 13.6 | 13.5
48 | -126 | 13.3 | 11.9 | 12 | 13.6 | 13.5
49 | -125 | 13.3 | 11.9 | 12 | 13.6 | 13.5
50 | -124 | 13.3 | 11.9 | 12 | 13.6 | 13.5
51 | -123 | 13.3 | 11.9 | 12 | 13.6 | 13.5
52 | -122 | 13.3 | 11.9 | 12 | 13.6 | 13.5
53 | -121 | 13.3 | 11.9 | 12 | 13.6 | 13.5
54 | -120 | 13.3 | 11.9 | 12 | 13.6 | 13.5
55 | -119 | 13.3 | 11.9 | 12 | 13.6 | 13.5
56 | -118 | 13.3 | 11.9 | 12 | 13.6 | 13.5
57 | -117 | 13.3 | 11.9 | 12 | 13.6 | 13.5
58 | -116 | 13.3 | 11.9 | 12 | 13.6 | 13.5
59 | -115 | 13.3 | 11.9 | 12 | 13.6 | 13.5
60 | -114 | 13.3 | 11.9 | 12 | 13.6 | 13.5
61 | -113 | 13.3 | 11.9 | 12 | 13.6 | 13.5
62 | -112 | 13.3 | 11.9 | 12 | 13.6 | 13.5
63 | -111 | 13.3 | 11.9 | 12 | 13.6 | 13.5
64 | -110 | 13.2 | 11.9 | 12 | 13.6 | 13.5
65 | -109 | 13.3 | 11.8 | 12 | 13.6 | 13.5
66 | -108 | 13.3 | 11.8 | 12 | 13.6 | 13.5
67 | -107 | 13.2 | 11.8 | 12 | 13.6 | 13.5
68 | -106 | 13.3 | 11.8 | 12 | 13.6 | 13.5
69 | -105 | 13.3 | 11.8 | 12 | 13.6 | 13.5
70 | -104 | 13.2 | 11.8 | 12 | 13.6 | 13.5
71 | -103 | 13.3 | 11.8 | 12 | 13.6 | 13.5
72 | -102 | 13.3 | 11.9 | 12 | 13.6 | 13.5
73 | -101 | 13.2 | 11.9 | 12 | 13.6 | 13.5
74 | -100 | 13.3 | 11.9 | 12 | 13.6 | 13.5
75 | -99 | 13.3 | 11.9 | 12 | 13.6 | 13.5
76 | -98 | 13.2 | 11.9 | 12 | 13.6 | 13.5
77 | -97 | 13.2 | 11.9 | 12 | 13.6 | 13.5
78 | -96 | 13.2 | 11.9 | 12 | 13.6 | 13.5
79 | -95 | 13.2 | 11.9 | 12 | 13.6 | 13.5
80 | -94 | 13.2 | 11.9 | 12 | 13.6 | 13.5
81 | -93 | 13.2 | 11.9 | 12 | 13.5 | 13.5
82 | -92 | 13.2 | 11.9 | 12 | 13.6 | 13.5
83 | -91 | 13.2 | 11.9 | 12 | 13.5 | 13.5
84 | -90 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
85 | -89 | 13.2 | 11.9 | 12 | 13.5 | 13.5
86 | -88 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
87 | -87 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
88 | -86 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
89 | -85 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
90 | -84 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
91 | -83 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
92 | -82 | 13.2 | 11.9 | 11.9 | 13.6 | 13.5
93 | -81 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
94 | -80 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
95 | -79 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
96 | -78 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
97 | -77 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
98 | -76 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
99 | -75 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
100 | -74 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
101 | -73 | 13.2 | 11.9 | 11.9 | 13.5 | 13.5
102 | -72 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
103 | -71 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
104 | -70 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
105 | -69 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
106 | -68 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
107 | -67 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
108 | -66 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
109 | -65 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
110 | -64 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
111 | -63 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
112 | -62 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
113 | -61 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
114 | -60 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
115 | -59 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
116 | -58 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
117 | -57 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
118 | -56 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
119 | -55 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
120 | -54 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
121 | -53 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
122 | -52 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
123 | -51 | 13.2 | 11.8 | 12 | 13.5 | 13.4
124 | -50 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
125 | -49 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
126 | -48 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
127 | -47 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
128 | -46 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
129 | -45 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
130 | -44 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
131 | -43 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
132 | -42 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
133 | -41 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
134 | -40 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
135 | -39 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
136 | -38 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
137 | -37 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
138 | -36 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
139 | -35 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
140 | -34 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
141 | -33 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
142 | -32 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
143 | -31 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
144 | -30 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
145 | -29 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
146 | -28 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
147 | -27 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
148 | -26 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
149 | -25 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
150 | -24 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
151 | -23 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
152 | -22 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
153 | -21 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
154 | -20 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
155 | -19 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
156 | -18 | 13.2 | 11.9 | 11.8 | 13.5 | 13.4
157 | -17 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
158 | -16 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
159 | -15 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
160 | -14 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
161 | -13 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
162 | -12 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
163 | -11 | 13.2 | 11.9 | 11.9 | 13.5 | 13.4
164 | -10 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
165 | -9 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
166 | -8 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
167 | -7 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
168 | -6 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
169 | -5 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
170 | -4 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
171 | -3 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
172 | -2 | 13.2 | 11.8 | 11.9 | 13.5 | 13.4
173 | -1 | 13.2 | 11.8 | 12 | 13.5 | 13.4
174 | 0 | 13.2 | 11.8 | 12 | 13.5 | 13.4
175 | 1 | 13.2 | 11.8 | 12 | 13.5 | 13.4
176 | 2 | 13.2 | 11.8 | 12 | 13.5 | 13.4
177 | 3 | 13.2 | 11.8 | 12 | 13.5 | 13.4
178 | 4 | 13.2 | 12.1 | 13.2 | 13.5 | 13.6
179 | 5 | 13.2 | 16.7 | 23.7 | 13.5 | 15.7
180 | 6 | 13.2 | 25.4 | 37.4 | 13.5 | 19.6
181 | 7 | 13.3 | 34.5 | 51.9 | 13.6 | 26.5
182 | 8 | 13.4 | 51.2 | 87.8 | 13.6 | 33.9
183 | 9 | 13.6 | 69.6 | 118.8 | 13.7 | 41.8
184 | 10 | 14 | 95.3 | 162.5 | 13.7 | 52.8
185 | 11 | 14.4 | 117.9 | 195.3 | 13.8 | 65.5
186 | 12 | 14.9 | 142.6 | 234.4 | 13.8 | 74.3
187 | 13 | 15.7 | 159.2 | 255.3 | 13.9 | 79.8
188 | 14 | 16.4 | 172.8 | 272.1 | 14 | 83.9
189 | 15 | 17.1 | 187.9 | 287.7 | 14.1 | 91.5
190 | 16 | 17.9 | 200.4 | 301.4 | 14.2 | 98.7
191 | 17 | 18.6 | 218.3 | 323.3 | 14.3 | 105.5
192 | 18 | 19.4 | 225.5 | 323.4 | 14.4 | 110.1
193 | 19 | 20.1 | 230.7 | 324.6 | 14.6 | 114.7
194 | 20 | 20.9 | 234 | 331.3 | 14.7 | 118.4
195 | 21 | 21.6 | 238.6 | 345.7 | 14.9 | 123.3
196 | 22 | 22.3 | 246.6 | 363.5 | 15.6 | 127.2
197 | 23 | 23 | 259.6 | 382.4 | 16.3 | 135.1
198 | 24 | 23.8 | 267.6 | 397.6 | 16.9 | 146.7
199 | 25 | 24.7 | 285.5 | 418.3 | 17.8 | 156.8
200 | 26 | 25.5 | 301.2 | 443.2 | 19.8 | 165.9
201 | 27 | 26.5 | 326.1 | 475.8 | 22 | 181.8
202 | 28 | 27.6 | 339.3 | 488.6 | 23.1 | 191.7
203 | 29 | 28.7 | 353.9 | 504.8 | 25.1 | 198.7
204 | 30 | 29.9 | 371.4 | 525.4 | 27.9 | 208.7
205 | 31 | 31 | 389.7 | 551.9 | 30.5 | 217.9
206 | 32 | 32.3 | 403.4 | 574.7 | 33.4 | 225.9
207 | 33 | 33.7 | 408.9 | 572.1 | 34.7 | 234.2
208 | 34 | 35 | 412.7 | 559.4 | 35.6 | 238.4
209 | 35 | 36.3 | 411.9 | 558.5 | 36.3 | 242.6
210 | 36 | 37.7 | 423.2 | 576.7 | 38 | 255.7
211 | 37 | 39 | 435 | 590.5 | 39.9 | 266.1
212 | 38 | 40.5 | 442 | 593.5 | 42.3 | 274.5
213 | 39 | 42 | 448.4 | 597 | 44.1 | 280.3
214 | 40 | 43.5 | 456.4 | 596.2 | 46.2 | 286.4
215 | 41 | 45.1 | 461.5 | 596.6 | 48 | 292.6
216 | 42 | 46.7 | 459.5 | 585.2 | 48.3 | 295.1
217 | 43 | 48.3 | 462.1 | 580.1 | 49.5 | 299.7
218 | 44 | 50 | 467.9 | 582.5 | 51.9 | 304.1
219 | 45 | 51.6 | 463.1 | 571.5 | 53.1 | 306.3
220 | 46 | 53.3 | 460.8 | 573.7 | 54 | 309.7
221 | 47 | 54.9 | 461.3 | 580.5 | 55.2 | 318.7
222 | 48 | 56.6 | 457.2 | 579.5 | 56.4 | 321.7
223 | 49 | 58.3 | 457 | 581.6 | 57.2 | 325
224 | 50 | 59.9 | 459.7 | 590.3 | 58.8 | 335.1
225 | 51 | 61.6 | 465.6 | 599.2 | 60 | 344.6
226 | 52 | 63.3 | 475.7 | 613 | 61.9 | 353
227 | 53 | 65 | 477 | 616.8 | 63.4 | 361.9
228 | 54 | 66.7 | 483.5 | 623.2 | 64.9 | 372.3
229 | 55 | 68.4 | 481.4 | 617.2 | 65.9 | 375.8
230 | 56 | 70.4 | 488.6 | 617 | 67.9 | 382.9
231 | 57 | 72.4 | 489.2 | 618.3 | 70 | 390
232 | 58 | 74.6 | 496.4 | 628.4 | 72 | 400.2
233 | 59 | 76.9 | 497.3 | 626.7 | 73.7 | 403.7
234 | 60 | 79.3 | 493.2 | 616.5 | 75.1 | 405.4
235 | 61 | 81.6 | 491.2 | 614.8 | 76.1 | 406.9
236 | 62 | 83.8 | 486.7 | 614.8 | 77 | 410
237 | 63 | 86.1 | 478.2 | 600.6 | 77.5 | 411.2
238 | 64 | 88.3 | 471.7 | 592.8 | 78.7 | 414.6
239 | 65 | 90.5 | 476.3 | 600.6 | 80.5 | 421.4
240 | 66 | 92.7 | 483.7 | 618.6 | 82.9 | 425.5
241 | 67 | 94.9 | 496.1 | 639.5 | 85.8 | 432.6
242 | 68 | 97.3 | 509.4 | 658.3 | 89.2 | 440
243 | 69 | 99.9 | 521.2 | 671.6 | 92 | 451
244 | 70 | 102.5 | 528.6 | 681.8 | 95.5 | 459.8
245 | 71 | 105.3 | 527.9 | 675 | 98.2 | 462.9
246 | 72 | 108 | 524.6 | 668.7 | 101 | 466.9
247 | 73 | 110.7 | 531.9 | 678.2 | 104.3 | 474
248 | 74 | 113.5 | 535.5 | 686.8 | 107.2 | 479.7
249 | 75 | 116.3 | 534.8 | 682.9 | 109.4 | 483
250 | 76 | 119 | 536.1 | 675.7 | 110.8 | 488.6
251 | 77 | 121.6 | 538.1 | 682.9 | 111.8 | 493.1
252 | 78 | 124.1 | 539.7 | 682.4 | 113.7 | 499.4
253 | 79 | 126.6 | 546 | 688.4 | 116 | 505.6
254 | 80 | 129.2 | 550.6 | 690.2 | 118.3 | 513.3
255 | 81 | 131.7 | 553.6 | 697.1 | 120.5 | 519.2
256 | 82 | 134.2 | 552.9 | 694.9 | 121.6 | 523.7
257 | 83 | 136.7 | 553.8 | 698.8 | 123.2 | 531.7
258 | 84 | 139 | 560.3 | 717.3 | 125.4 | 540.6
259 | 85 | 141.4 | 570.2 | 732.5 | 127.7 | 545.9
260 | 86 | 143.8 | 564.6 | 719.4 | 128.5 | 547.1
261 | 87 | 146.1 | 555.5 | 713.5 | 129.1 | 548.1
262 | 88 | 148.5 | 558.4 | 719.4 | 130.7 | 552.7
263 | 89 | 150.8 | 562.1 | 720.1 | 133.5 | 557.7
264 | 90 | 153.2 | 555.8 | 709.3 | 135.2 | 557.7
265 | 91 | 155.6 | 552.4 | 707.2 | 138.1 | 559.7
266 | 92 | 158 | 557.9 | 716.5 | 141.3 | 565.4
267 | 93 | 160.6 | 561.2 | 724.8 | 144.7 | 571.3
268 | 94 | 163.2 | 564.8 | 736.1 | 148 | 576.7
269 | 95 | 165.9 | 562.8 | 732.5 | 150.3 | 579.9
270 | 96 | 168.6 | 562.5 | 734.8 | 152.2 | 583.5
271 | 97 | 171.3 | 569.6 | 749.8 | 155.3 | 588.1
272 | 98 | 174.1 | 577.4 | 759.4 | 159.3 | 593
273 | 99 | 177.1 | 578.5 | 759.3 | 162.5 | 595.4
274 | 100 | 180.1 | 587 | 765.8 | 166.8 | 601.7
275 | 101 | 183.3 | 590.1 | 762.6 | 170.2 | 606.6
276 | 102 | 186.5 | 591.8 | 764.6 | 173.4 | 609.9
277 | 103 | 189.8 | 594.1 | 761.9 | 176.9 | 613.1
278 | 104 | 193 | 598.6 | 766.4 | 179.8 | 618.5
279 | 105 | 196.3 | 596.9 | 755.9 | 181.7 | 621.5
280 | 106 | 199.5 | 605 | 768.9 | 184.3 | 628.4
281 | 107 | 202.8 | 610 | 770.4 | 187.2 | 632.7
282 | 108 | 206 | 606.2 | 763.9 | 188.4 | 631.5
283 | 109 | 209.2 | 613.6 | 764.6 | 191.1 | 635.3
284 | 110 | 212.3 | 612.8 | 756.1 | 193 | 638.6
285 | 111 | 215.5 | 617.8 | 757.1 | 195.5 | 642.1
286 | 112 | 218.8 | 623.9 | 758.6 | 198.7 | 646.2
287 | 113 | 222 | 626 | 755.9 | 202.4 | 648.4
288 | 114 | 225.3 | 625.5 | 758.1 | 205.6 | 650.1
289 | 115 | 228.5 | 621.4 | 752.1 | 208.5 | 651.4
290 | 116 | 231.7 | 616.2 | 742.2 | 211.3 | 651.1
291 | 117 | 234.8 | 608.8 | 724.6 | 213.8 | 650.4
292 | 118 | 237.9 | 597.1 | 710.3 | 215.2 | 650.4
293 | 119 | 241 | 592 | 703.8 | 217.6 | 650.8
294 | 120 | 244 | 587.9 | 696.1 | 219.6 | 649.8
295 | 121 | 246.8 | 579 | 684.9 | 220.7 | 648.1
296 | 122 | 249.3 | 568.2 | 678.1 | 221.8 | 647.4
297 | 123 | 251.6 | 558.1 | 670.4 | 222.4 | 646.2
298 | 124 | 253.6 | 555 | 663.5 | 223.2 | 646
299 | 125 | 255.6 | 549.5 | 656.6 | 224.4 | 646.5
300 | 126 | 257.5 | 541.7 | 643 | 224.5 | 644.7
301 | 127 | 259.3 | 536.2 | 640.1 | 224.9 | 644.5
302 | 128 | 261 | 531.7 | 641.7 | 226.6 | 645.4
303 | 129 | 262.6 | 529.4 | 640.8 | 228.1 | 646.4
304 | 130 | 264.3 | 529.5 | 641 | 230.7 | 649.2
305 | 131 | 266 | 529.1 | 637 | 232.3 | 649.5
306 | 132 | 267.7 | 525.9 | 641.2 | 233.5 | 649.7
307 | 133 | 269.3 | 530.4 | 651.7 | 235.8 | 651.3
308 | 134 | 270.9 | 535.9 | 663.9 | 238.1 | 654
309 | 135 | 272.7 | 546.1 | 677.3 | 240.6 | 658.1
310 | 136 | 274.4 | 555.3 | 692.4 | 243.2 | 660.9
311 | 137 | 276.2 | 558.1 | 693.2 | 244.5 | 662.4
312 | 138 | 278 | 561.4 | 691.4 | 245.8 | 664.7
313 | 139 | 279.7 | 564.6 | 697 | 247 | 667.3
314 | 140 | 281.5 | 564 | 696.6 | 247.8 | 669.5
315 | 141 | 283.2 | 563.9 | 686.8 | 247.9 | 668.7
316 | 142 | 284.8 | 560.5 | 679.1 | 247.7 | 668.1
317 | 143 | 286.3 | 555.9 | 667.1 | 247.7 | 665.9
318 | 144 | 287.8 | 550.7 | 655.3 | 247.7 | 666
319 | 145 | 289.2 | 557.3 | 661.1 | 249 | 669.1
320 | 146 | 290.7 | 558.5 | 662.9 | 249.7 | 671.4
321 | 147 | 292.1 | 557 | 658.4 | 249.8 | 671.3
322 | 148 | 293.6 | 554.8 | 657.2 | 249.6 | 669.8
323 | 149 | 295 | 555.1 | 661.8 | 249.7 | 670
324 | 150 | 296.5 | 551.2 | 653.1 | 249.4 | 671.2
325 | 151 | 298 | 552.7 | 651.8 | 248.9 | 671.3
326 | 152 | 299.4 | 546.9 | 640.2 | 248.8 | 670.2
327 | 153 | 300.9 | 549.3 | 635.8 | 248.9 | 670.4
328 | 154 | 302.4 | 558.4 | 640.5 | 249.5 | 672.7
329 | 155 | 303.8 | 564.1 | 637 | 250.4 | 673.2
330 | 156 | 305.3 | 566.5 | 636.1 | 251.2 | 673.4
331 | 157 | 306.8 | 563.9 | 634 | 251.7 | 672.4
332 | 158 | 308.3 | 564.9 | 653.1 | 252 | 672.7
333 | 159 | 309.7 | 570.1 | 670.2 | 252.1 | 674.8
334 | 160 | 311.2 | 575.7 | 677.1 | 252.5 | 676.9
335 | 161 | 312.7 | 575.7 | 680 | 252.6 | 677.4
336 | 162 | 314.3 | 582.8 | 692.5 | 253 | 680.3
337 | 163 | 315.9 | 585.3 | 691.8 | 253.3 | 682
338 | 164 | 317.5 | 585.6 | 687.2 | 253.4 | 680.7
339 | 165 | 319.1 | 588.7 | 680.2 | 253.4 | 678.6
340 | 166 | 320.8 | 582.8 | 670.1 | 253.2 | 677.1
341 | 167 | 322.4 | 584.2 | 675.9 | 253.2 | 676.5
342 | 168 | 324 | 581 | 682.9 | 253.3 | 676.3
343 | 169 | 325.6 | 580.9 | 693.3 | 253.3 | 679.1
344 | 170 | 327.1 | 588.4 | 702.8 | 253.9 | 682.1
345 | 171 | 328.6 | 601.2 | 718.7 | 254.5 | 685.4
346 | 172 | 330.2 | 610.3 | 714.8 | 254.7 | 685.5
347 | 173 | 331.8 | 606.5 | 704.7 | 254.3 | 685.2
348 | 174 | 333.4 | 607.8 | 708.3 | 253.8 | 688.4
349 | 175 | 335 | 605.4 | 696.3 | 253.6 | 688.2
350 | 176 | 336.5 | 607.3 | 699.7 | 253.4 | 688.1
351 | 177 | 338 | 610.8 | 715.9 | 253 | 689.5
352 | 178 | 339.5 | 622 | 726.3 | 252.8 | 692.9
353 | 179 | 341 | 635.1 | 737.5 | 253.1 | 698.1
354 | 180 | 342.5 | 639.6 | 745.1 | 253.1 | 699.7
355 | 181 | 344.1 | 641.7 | 736.2 | 252.7 | 699.8
356 | 182 | 345.7 | 641.4 | 737.7 | 252.3 | 699.7
357 | 183 | 347.3 | 638.5 | 739.1 | 251.8 | 699.4
358 | 184 | 348.9 | 632.9 | 730.6 | 251.3 | 698.9
359 | 185 | 350.5 | 637.9 | 731.7 | 251.2 | 701.1
360 | 186 | 352 | 645.5 | 736.9 | 251 | 702.9
361 | 187 | 353.6 | 648.9 | 744.4 | 250.8 | 706.5
362 | 188 | 355.2 | 653.3 | 751.2 | 250.6 | 708.2
363 | 189 | 356.7 | 656 | 755.1 | 250.3 | 709.1
364 | 190 | 358.4 | 665.1 | 765.9 | 249.9 | 713.7
365 | 191 | 360 | 670 | 767.8 | 249.4 | 715.9
366 | 192 | 361.6 | 671 | 763.9 | 249 | 716.4
367 | 193 | 363.3 | 670.5 | 766.5 | 248.4 | 718.3
368 | 194 | 364.9 | 672.3 | 771.7 | 247.8 | 720.9
369 | 195 | 366.5 | 674.3 | 773.7 | 247.4 | 722.7
370 | 196 | 368.1 | 672.7 | 776.7 | 247.2 | 722.1
371 | 197 | 369.7 | 675 | 779.1 | 246.9 | 723.8
372 | 198 | 371.3 | 678.1 | 775.2 | 246.8 | 725.9
373 | 199 | 373 | 674.2 | 762.5 | 247.2 | 722.9
374 | 200 | 374.6 | 678 | 772.9 | 247.7 | 724.4
375 | 201 | 376.2 | 673.3 | 768.9 | 248.1 | 725.7
376 | 202 | 377.8 | 671.5 | 765.9 | 248.7 | 726
377 | 203 | 379.5 | 672.9 | 765.1 | 249.3 | 727.3
378 | 204 | 381.1 | 672.8 | 765.3 | 250 | 727.7
379 | 205 | 382.7 | 675 | 765.3 | 250.8 | 727.9
380 | 206 | 384.3 | 677.2 | 765.4 | 251.6 | 728.2
381 | 207 | 385.9 | 683.9 | 772 | 252.5 | 730.2
382 | 208 | 387.5 | 690.3 | 780.2 | 253.3 | 734.3
383 | 209 | 389 | 691.5 | 773.2 | 254.1 | 735.7
384 | 210 | 390.7 | 690.9 | 766.1 | 254.9 | 733.8
385 | 211 | 392.4 | 685.6 | 757.2 | 255.8 | 732.4
386 | 212 | 394 | 685.5 | 758.9 | 256.7 | 733.2
387 | 213 | 395.6 | 685.5 | 766.1 | 257.7 | 733.9
388 | 214 | 397.2 | 693.1 | 779.1 | 258.7 | 736.5
389 | 215 | 398.8 | 693.1 | 782.4 | 259.8 | 737.3
390 | 216 | 400.4 | 691.5 | 782.9 | 260.9 | 738.8
391 | 217 | 402.1 | 686.6 | 779.2 | 261.9 | 738.7
392 | 218 | 403.8 | 688.2 | 787.3 | 262.9 | 739.5
393 | 219 | 405.4 | 688.4 | 785.8 | 263.9 | 740.6
394 | 220 | 407.1 | 686.5 | 783.6 | 264.8 | 740.2
395 | 221 | 408.7 | 683.7 | 774.3 | 265.5 | 740.1
396 | 222 | 410.3 | 684.9 | 781.1 | 266.3 | 741
397 | 223 | 411.9 | 684.6 | 782.5 | 267.4 | 741.3
398 | 224 | 413.5 | 677.6 | 776.7 | 268.5 | 741.2
399 | 225 | 415 | 670.7 | 765 | 269.5 | 741.6
400 | 226 | 416.6 | 666.9 | 760.1 | 270.6 | 741.9
401 | 227 | 418.1 | 664.3 | 762.6 | 271.7 | 742.4
402 | 228 | 419.6 | 663.3 | 761.6 | 272.9 | 742.3
403 | 229 | 421.1 | 668.8 | 765.1 | 274 | 743.1
404 | 230 | 422.5 | 670.6 | 766.4 | 275.1 | 744.2
405 | 231 | 423.9 | 672.2 | 766.2 | 276 | 744.6
406 | 232 | 425.4 | 669.2 | 763.1 | 277 | 744.3
407 | 233 | 426.9 | 662.7 | 754.6 | 278.1 | 744.1
408 | 234 | 428.5 | 663.9 | 756.2 | 279.4 | 745.4
409 | 235 | 430 | 667.1 | 767 | 280.9 | 746.9
410 | 236 | 431.6 | 674.3 | 778.2 | 282.3 | 749.6
411 | 237 | 433.4 | 679.2 | 786 | 283.8 | 750.4
412 | 238 | 435.2 | 678.7 | 786.3 | 285.3 | 751.5
413 | 239 | 437.2 | 678 | 785.3 | 286.6 | 752
414 | 240 | 439.3 | 679.1 | 783.2 | 288.1 | 753.3
415 | 241 | 441.4 | 678.5 | 781.1 | 289.6 | 753.8
416 | 242 | 443.5 | 677.5 | 776.3 | 291 | 752.4
417 | 243 | 445.7 | 680.4 | 770.1 | 292.6 | 751.2
418 | 244 | 448 | 680.5 | 767 | 294.2 | 751.5
419 | 245 | 450.1 | 675 | 760.1 | 295.7 | 751.5
420 | 246 | 452.2 | 672 | 755.8 | 297.2 | 751.5
421 | 247 | 454.2 | 669.3 | 760.3 | 298.6 | 752.3
422 | 248 | 456 | 667.1 | 756.7 | 300 | 753
423 | 249 | 457.9 | 663.4 | 742.5 | 301.3 | 751.4
424 | 250 | 459.9 | 658.8 | 738.1 | 302.7 | 750.5
425 | 251 | 461.7 | 655.1 | 739.6 | 304.1 | 750.9
426 | 252 | 463.5 | 652.5 | 735.3 | 305.5 | 750.9
427 | 253 | 465.3 | 649.1 | 729.6 | 306.9 | 750
428 | 254 | 467.1 | 647.5 | 720.8 | 308.2 | 749.5
429 | 255 | 469 | 649.1 | 718.2 | 309.5 | 749.6
430 | 256 | 470.9 | 649 | 715.9 | 310.8 | 750.5
431 | 257 | 472.8 | 648.4 | 714.9 | 312.1 | 750.3
432 | 258 | 474.8 | 647.7 | 711 | 313.3 | 749.2
433 | 259 | 476.8 | 645.2 | 710.6 | 314.5 | 749
434 | 260 | 478.8 | 643.2 | 705.3 | 315.7 | 749.1
435 | 261 | 480.9 | 642.3 | 701.7 | 316.8 | 749.1
436 | 262 | 482.9 | 641.3 | 695.1 | 317.9 | 748.2
437 | 263 | 485 | 641.9 | 694.5 | 319 | 748.4
438 | 264 | 487 | 639.7 | 692.7 | 320.1 | 749.5
439 | 265 | 488.9 | 639.3 | 693.7 | 321.2 | 749.8
440 | 266 | 490.8 | 636.6 | 690.4 | 322.3 | 749.4
441 | 267 | 492.7 | 637 | 694.8 | 323.4 | 750.3
442 | 268 | 494.7 | 632.7 | 693.4 | 324.6 | 749.9
443 | 269 | 496.6 | 634.2 | 696.5 | 325.7 | 750.5
444 | 270 | 498.4 | 636.5 | 701.1 | 326.8 | 750.9
445 | 271 | 500.1 | 638.8 | 709.4 | 327.9 | 750.9
446 | 272 | 501.9 | 642.2 | 718.6 | 329 | 752.6
447 | 273 | 503.7 | 640.5 | 717.9 | 330.1 | 752.3
448 | 274 | 505.6 | 639.7 | 725.1 | 331.2 | 752.1
449 | 275 | 507.4 | 640 | 730.6 | 332.2 | 753.2
450 | 276 | 509.3 | 651.3 | 743.4 | 333.2 | 754.3
451 | 277 | 511.3 | 659.5 | 753.9 | 334.3 | 756.1
452 | 278 | 513.1 | 661.6 | 755.1 | 335.3 | 756.8
453 | 279 | 515 | 663.9 | 760.7 | 336.3 | 757.3
454 | 280 | 516.9 | 670.8 | 768.6 | 337.4 | 758
455 | 281 | 518.9 | 674.8 | 771.2 | 338.5 | 757.9
456 | 282 | 521 | 673.4 | 771.3 | 339.6 | 758.5
457 | 283 | 523.1 | 674.6 | 773.3 | 340.7 | 758.4
458 | 284 | 525.3 | 677.9 | 776.6 | 341.8 | 759.1
459 | 285 | 527.5 | 672.2 | 767.4 | 342.9 | 757.8
460 | 286 | 529.7 | 672.6 | 771.4 | 344 | 758.2
461 | 287 | 531.8 | 672.5 | 773.5 | 345.3 | 758.2
462 | 288 | 533.7 | 668.4 | 769.6 | 346.6 | 758.2
463 | 289 | 535.6 | 663.9 | 764.5 | 347.8 | 757.1
464 | 290 | 537.4 | 662.2 | 760.3 | 349.1 | 757.4
465 | 291 | 539.3 | 655.4 | 751.8 | 350.4 | 757.2
466 | 292 | 541.1 | 646.5 | 747.3 | 351.8 | 757.1
467 | 293 | 543 | 641.7 | 740.3 | 353.1 | 756
468 | 294 | 544.9 | 638.7 | 736.6 | 354.6 | 755.9
469 | 295 | 546.7 | 634.5 | 731 | 356 | 755.2
470 | 296 | 548.5 | 631.7 | 734.7 | 357.5 | 754.7
471 | 297 | 550.2 | 629.8 | 735.9 | 359 | 755.9
472 | 298 | 551.9 | 632.3 | 733.7 | 360.5 | 756.5
473 | 299 | 553.6 | 630.1 | 735.3 | 362.1 | 756.3
474 | 300 | 555.2 | 634.4 | 743.9 | 363.6 | 756.9
475 | 301 | 556.8 | 634.9 | 747.4 | 365.3 | 755.8
476 | 302 | 558.3 | 631.2 | 745.6 | 367 | 755
477 | 303 | 559.9 | 628.5 | 744.7 | 368.6 | 754.9
478 | 304 | 561.5 | 624.7 | 741 | 370.5 | 754.1
479 | 305 | 563.2 | 623.8 | 733.7 | 372.3 | 753.4
480 | 306 | 565 | 621.2 | 723.9 | 374.1 | 752.8
481 | 307 | 566.7 | 618.6 | 711.9 | 376 | 751.3
482 | 308 | 568.4 | 620.4 | 709.5 | 377.9 | 749.4
483 | 309 | 570.1 | 619.4 | 705.4 | 380 | 748.6
484 | 310 | 572 | 616.8 | 700.4 | 382 | 747.4
485 | 311 | 573.9 | 614.7 | 700.1 | 384.1 | 746
486 | 312 | 575.7 | 620.7 | 711.6 | 386.1 | 746.7
487 | 313 | 577.4 | 627.6 | 720.2 | 388.3 | 747.9
488 | 314 | 578.9 | 631.5 | 724.2 | 390.5 | 747.8
489 | 315 | 580.4 | 632.7 | 726.6 | 392.5 | 747.2
490 | 316 | 582.2 | 631.5 | 726.5 | 394.6 | 746.9
491 | 317 | 583.9 | 634.6 | 737.1 | 396.7 | 748.1
492 | 318 | 585.4 | 637.1 | 742 | 398.8 | 748
493 | 319 | 586.8 | 639.6 | 746.8 | 400.9 | 749.2
494 | 320 | 588.2 | 640.3 | 752.3 | 402.9 | 749.3
495 | 321 | 589.7 | 644 | 758.2 | 405 | 749.3
496 | 322 | 591.3 | 649.3 | 764.4 | 407.1 | 750.1
497 | 323 | 592.9 | 648.2 | 756.8 | 409.2 | 748.7
498 | 324 | 594.7 | 642.9 | 747.3 | 411.3 | 746.8
499 | 325 | 596.4 | 643.5 | 750.3 | 413.3 | 747.9
500 | 326 | 597.9 | 646.5 | 756.3 | 415.3 | 749.5
501 | 327 | 599.4 | 649.5 | 756 | 417.4 | 748.9
502 | 328 | 601.1 | 650.9 | 755.3 | 419.5 | 748.6
503 | 329 | 602.8 | 645.8 | 745.7 | 421.6 | 747.4
504 | 330 | 604.8 | 643.6 | 741 | 423.6 | 747.5
505 | 331 | 607 | 639.9 | 737.2 | 425.6 | 747.3
506 | 332 | 609.3 | 635.3 | 731.4 | 427.7 | 747.6
507 | 333 | 611.7 | 633.1 | 731.3 | 429.8 | 748.5
508 | 334 | 613.8 | 633 | 734.9 | 431.8 | 748.8
509 | 335 | 615.9 | 632.7 | 736.1 | 434 | 747.8
510 | 336 | 618.1 | 634.4 | 737.1 | 436.1 | 747.8
511 | 337 | 620.2 | 636.3 | 735.5 | 438.3 | 746.9
512 | 338 | 622.4 | 635.8 | 738.4 | 440.4 | 746.7
513 | 339 | 624.4 | 638.5 | 742.9 | 442.7 | 747.2
514 | 340 | 626.4 | 641.4 | 744.9 | 444.9 | 746.7
515 | 341 | 628.4 | 645.4 | 746.4 | 447.1 | 747.6
516 | 342 | 630.3 | 639.9 | 738.3 | 449.4 | 747.4
517 | 343 | 632.3 | 640.8 | 739.9 | 451.7 | 748.2
518 | 344 | 634.3 | 644 | 743 | 454.1 | 747.7
519 | 345 | 636.4 | 639.6 | 729.9 | 456.5 | 748
520 | 346 | 639 | 633.6 | 720.8 | 459 | 746.4
521 | 347 | 641.8 | 625.2 | 711 | 461.5 | 745.1
522 | 348 | 644.4 | 620.7 | 705.7 | 464.1 | 744.8
523 | 349 | 646.8 | 621.2 | 706.9 | 466.6 | 745.7
524 | 350 | 648.9 | 624 | 705.2 | 469.2 | 745.9
525 | 351 | 651 | 623.3 | 705.8 | 471.9 | 746.6
526 | 352 | 652.9 | 625.2 | 710.1 | 474.5 | 747.5
527 | 353 | 654.8 | 621.7 | 707.4 | 477.3 | 747.9
528 | 354 | 656.6 | 618.2 | 703.5 | 480.1 | 748.2
529 | 355 | 658.4 | 615.1 | 702.4 | 482.9 | 748.4
530 | 356 | 659.9 | 610.5 | 698 | 485.8 | 748.7
531 | 357 | 661.6 | 609.5 | 699.7 | 488.7 | 748.5
532 | 358 | 663 | 613.3 | 706.4 | 491.6 | 750.5
533 | 359 | 664.2 | 618.6 | 713.5 | 494.5 | 751.5
534 | 360 | 665.3 | 621.9 | 719.3 | 497.4 | 752.2
535 | 361 | 666.2 | 617.4 | 713.9 | 500.2 | 752.1
536 | 362 | 667.3 | 622.8 | 721.2 | 503.1 | 753.3
537 | 363 | 668.6 | 630.9 | 724 | 506 | 753.6
538 | 364 | 670.1 | 629.3 | 716.8 | 508.9 | 751.6
539 | 365 | 671.8 | 626.1 | 712 | 511.8 | 750.2
540 | 366 | 673.3 | 629.1 | 720.3 | 514.8 | 752.2
541 | 367 | 674.5 | 637.4 | 732.5 | 517.8 | 753.5
542 | 368 | 675.5 | 646.4 | 735.8 | 520.7 | 753.9
543 | 369 | 676.6 | 642.5 | 730.5 | 523.6 | 753.5
544 | 370 | 678 | 641.4 | 728.8 | 526.4 | 754.1
545 | 371 | 679.4 | 641.5 | 725.8 | 529.1 | 752.1
546 | 372 | 681.1 | 647.8 | 733.9 | 531.8 | 752.3
547 | 373 | 682.4 | 652.1 | 740.2 | 534.5 | 753.5
548 | 374 | 683.4 | 658.1 | 746.9 | 537 | 755.8
549 | 375 | 684.2 | 661.5 | 752.8 | 539.4 | 757.5
550 | 376 | 685 | 659.1 | 746.7 | 541.6 | 757.1
551 | 377 | 686 | 661.9 | 748.2 | 543.7 | 758.3
552 | 378 | 686.9 | 654.1 | 742.6 | 545.8 | 756.7
553 | 379 | 688 | 646 | 739 | 547.8 | 756.7
554 | 380 | 689.2 | 638 | 736.7 | 549.8 | 757.6
555 | 381 | 690.4 | 637 | 738.3 | 551.7 | 757.5
556 | 382 | 691.6 | 638.9 | 740.9 | 553.7 | 757.8
557 | 383 | 692.9 | 646.2 | 744.5 | 555.6 | 758
558 | 384 | 694.2 | 649.2 | 746.4 | 557.5 | 757.6
559 | 385 | 695.4 | 645.2 | 740.2 | 559.4 | 756.6
560 | 386 | 696.4 | 648.2 | 744 | 561.1 | 755.8
561 | 387 | 697.3 | 651 | 747.3 | 563 | 756.2
562 | 388 | 698.1 | 649.4 | 747.2 | 564.9 | 756.9
563 | 389 | 698.9 | 649 | 749.7 | 566.6 | 757.2
564 | 390 | 699.6 | 660.2 | 754.1 | 568.3 | 758.2
565 | 391 | 700.5 | 662.1 | 756 | 569.9 | 757.6
566 | 392 | 701.2 | 663.7 | 753.7 | 571.6 | 758.4
567 | 393 | 702 | 663.8 | 755.4 | 573.2 | 759
568 | 394 | 702.7 | 663 | 754.1 | 574.8 | 760
569 | 395 | 703.3 | 664.7 | 750.6 | 576.3 | 758.9
570 | 396 | 704.1 | 658.9 | 746.1 | 577.8 | 758.7
571 | 397 | 704.9 | 655.6 | 740.3 | 579.4 | 758.5
572 | 398 | 705.7 | 650.2 | 733.3 | 580.8 | 757.8
573 | 399 | 706.5 | 643.8 | 727.5 | 582.4 | 757.1
574 | 400 | 707.3 | 639.8 | 728.1 | 583.8 | 756.7
575 | 401 | 707.8 | 639.4 | 731.4 | 585.3 | 757
576 | 402 | 708.4 | 644.3 | 736.5 | 586.8 | 758
577 | 403 | 709 | 653.5 | 742.4 | 588.3 | 758.8
578 | 404 | 709.7 | 650.9 | 741.7 | 590 | 758.3
579 | 405 | 710.4 | 650.6 | 743.7 | 591.5 | 759.2
580 | 406 | 711 | 650.4 | 745.2 | 593 | 759.1
581 | 407 | 711.5 | 651.2 | 747.4 | 594.5 | 759
582 | 408 | 712.1 | 641.1 | 736 | 596 | 758.5
583 | 409 | 712.8 | 630.9 | 726.3 | 597.5 | 758.3
584 | 410 | 713.5 | 628.8 | 719.7 | 598.9 | 757.3
585 | 411 | 713.8 | 631.3 | 717.6 | 600.3 | 756.1
586 | 412 | 714.2 | 624.7 | 713.8 | 601.7 | 755.4
587 | 413 | 714.4 | 621.2 | 717.6 | 603.1 | 754.7
588 | 414 | 714.3 | 623.4 | 721.7 | 604.4 | 755.8
589 | 415 | 714.3 | 627.9 | 728.6 | 605.7 | 756.8
590 | 416 | 714.5 | 622.8 | 721.2 | 606.9 | 755.2
591 | 417 | 714.8 | 614.4 | 714.5 | 608.1 | 753.9
592 | 418 | 715 | 618.9 | 719.8 | 609.5 | 754.8
593 | 419 | 715.1 | 627.8 | 731.5 | 610.8 | 755.7
594 | 420 | 715.3 | 641.8 | 740.2 | 612.2 | 755.6
595 | 421 | 715.5 | 648.5 | 744.9 | 613.6 | 756.7
596 | 422 | 715.6 | 657.5 | 750.5 | 614.8 | 756.7
597 | 423 | 715.6 | 656.2 | 748.5 | 616.1 | 756.4
598 | 424 | 716 | 655.2 | 746.8 | 617.3 | 754.1
599 | 425 | 716.6 | 650 | 739.8 | 618.6 | 752.8
600 | 426 | 717.2 | 647.2 | 737 | 619.9 | 751.2
601 | 427 | 717.6 | 645.8 | 737.1 | 621.2 | 751.4
602 | 428 | 717.8 | 642.2 | 738.5 | 622.6 | 750.1
603 | 429 | 717.9 | 648.9 | 744.2 | 623.8 | 749.7
604 | 430 | 718 | 653.4 | 744 | 625.1 | 751.2
605 | 431 | 718.2 | 660.6 | 752.6 | 626.5 | 752.4
606 | 432 | 718.4 | 659.5 | 756.9 | 628 | 751.6
607 | 433 | 718.7 | 658.6 | 760.9 | 629.5 | 751.2
608 | 434 | 719 | 649.1 | 751.7 | 630.9 | 749.7
609 | 435 | 719.4 | 638.1 | 739.9 | 632.3 | 746.4
610 | 436 | 719.9 | 641.5 | 745.1 | 633.8 | 746.9
611 | 437 | 720.1 | 642.3 | 747.9 | 635.4 | 748.6
612 | 438 | 720.5 | 640.9 | 743.8 | 637.1 | 748.9
613 | 439 | 721.1 | 643.1 | 744.6 | 638.6 | 749.9
614 | 440 | 721.5 | 649 | 753 | 640.1 | 751.3
615 | 441 | 721.8 | 658.4 | 759.1 | 641.6 | 753.2
616 | 442 | 722.4 | 671.8 | 767.4 | 643.1 | 755.1
617 | 443 | 723.1 | 684.1 | 773.4 | 644.6 | 756.4
618 | 444 | 723.9 | 687.8 | 778 | 646 | 757.3
619 | 445 | 724.8 | 694.7 | 780.1 | 647.3 | 758.9
620 | 446 | 725.3 | 688.7 | 779.1 | 648.6 | 760.6
621 | 447 | 725.9 | 679 | 772.6 | 649.9 | 759.9
622 | 448 | 726.6 | 684.3 | 773.7 | 651.1 | 761.2
623 | 449 | 727.4 | 685 | 772.4 | 652.4 | 761.5
624 | 450 | 728.1 | 692.5 | 776.7 | 653.6 | 762.8
625 | 451 | 728.7 | 692.9 | 774.3 | 654.8 | 763.6
626 | 452 | 729.2 | 681.1 | 766.7 | 656 | 764.7
627 | 453 | 729.9 | 669.8 | 755.8 | 657.2 | 763.6
628 | 454 | 730.8 | 661.1 | 746.7 | 658.5 | 762.8
629 | 455 | 731.6 | 657.8 | 743.5 | 659.7 | 762.1
630 | 456 | 732.1 | 659.8 | 749.4 | 661 | 763.2
631 | 457 | 732.5 | 657.9 | 749 | 662.1 | 763.7
632 | 458 | 732.8 | 656.6 | 749.3 | 663.1 | 764.4
633 | 459 | 733.3 | 651.8 | 744.4 | 664.3 | 764.2
634 | 460 | 733.9 | 646.5 | 741.1 | 665.5 | 762.6
635 | 461 | 734.3 | 640.3 | 736 | 666.7 | 762
636 | 462 | 734.9 | 639.4 | 738.6 | 667.9 | 762.5
637 | 463 | 735.3 | 645.5 | 744.8 | 669.2 | 763.9
638 | 464 | 735.9 | 653.4 | 750.7 | 670.5 | 765.1
639 | 465 | 736.3 | 657.3 | 753.6 | 671.8 | 766.5
640 | 466 | 736.6 | 662.2 | 755.8 | 672.9 | 767.7
641 | 467 | 737 | 667 | 759.5 | 673.9 | 768.6
642 | 468 | 737.4 | 669.2 | 763.5 | 675 | 771.2
643 | 469 | 737.9 | 670.8 | 765.1 | 676.1 | 771.9
644 | 470 | 738.4 | 673.7 | 769 | 677.2 | 771.6
645 | 471 | 738.9 | 677.4 | 772.8 | 678.1 | 772.6
646 | 472 | 739.5 | 676.8 | 773.5 | 679.2 | 774.2
647 | 473 | 740.3 | 675.4 | 775.7 | 680.3 | 776
648 | 474 | 740.9 | 674.4 | 773.9 | 681.3 | 776.5
649 | 475 | 741.5 | 672.7 | 768 | 682.2 | 776.6
650 | 476 | 742.3 | 666.3 | 763.8 | 683.2 | 775.8
651 | 477 | 742.7 | 662.2 | 762.4 | 684.1 | 775.1
652 | 478 | 743.2 | 660 | 761 | 684.9 | 775.2
653 | 479 | 743.7 | 652.9 | 754.2 | 685.7 | 773.6
654 | 480 | 744.1 | 653.7 | 755.6 | 686.5 | 773
655 | 481 | 744.4 | 657.4 | 759.2 | 687.1 | 773.4
656 | 482 | 744.6 | 661 | 758.8 | 687.8 | 773.8
657 | 483 | 745 | 662.2 | 758.4 | 688.5 | 773.6
658 | 484 | 745.5 | 663 | 758.7 | 689.3 | 773.3
659 | 485 | 745.9 | 663.9 | 759.6 | 690 | 773.9
660 | 486 | 746.1 | 666.2 | 762 | 690.7 | 775.6
661 | 487 | 746.3 | 671 | 764 | 691.4 | 775.5
662 | 488 | 746.4 | 674 | 765.7 | 692 | 776.5
663 | 489 | 746.6 | 670.3 | 763.3 | 692.6 | 777.6
664 | 490 | 747.1 | 667.3 | 766 | 693.4 | 777.7
665 | 491 | 747.5 | 682.5 | 773.4 | 694.2 | 778.9
666 | 492 | 747.9 | 691 | 780.3 | 695 | 780.5
667 | 493 | 748.3 | 696 | 787.1 | 695.8 | 781.8
668 | 494 | 748.7 | 706.5 | 792.6 | 696.5 | 782
669 | 495 | 749.1 | 711.3 | 795 | 697 | 783
670 | 496 | 749.4 | 718.3 | 797.8 | 697.6 | 783.3
671 | 497 | 749.6 | 723.8 | 799.7 | 698 | 782.5
672 | 498 | 749.9 | 734.2 | 803.8 | 698.5 | 783.4
673 | 499 | 750.5 | 737.4 | 803.9 | 698.9 | 783.3
674 | 500 | 751.1 | 741.9 | 805.2 | 699.5 | 785.2
675 | 501 | 751.6 | 746.7 | 805.8 | 700.1 | 786.7
676 | 502 | 752 | 747.9 | 808.9 | 700.6 | 787.1
677 | 503 | 752.3 | 748.3 | 811.1 | 701.1 | 787.2
678 | 504 | 752.5 | 742.5 | 808.8 | 701.7 | 788.5
679 | 505 | 753 | 741.3 | 810.5 | 702.2 | 790
680 | 506 | 753.6 | 747.6 | 811.9 | 702.9 | 791.4
681 | 507 | 754.2 | 755.9 | 813.5 | 703.5 | 791.9
682 | 508 | 754.7 | 758.2 | 817.4 | 704.3 | 792.2
683 | 509 | 755.3 | 763.5 | 819 | 704.8 | 791.3
684 | 510 | 755.9 | 769.7 | 819.9 | 705.4 | 790.7
685 | 511 | 756.5 | 769.7 | 818.8 | 705.9 | 790.2
686 | 512 | 757 | 767.2 | 817.9 | 706.3 | 787.8
687 | 513 | 757.3 | 771.2 | 818.5 | 706.7 | 789.9
688 | 514 | 757.7 | 773 | 819.4 | 707.2 | 790.2
689 | 515 | 757.9 | 771.2 | 820.2 | 707.8 | 790.4
690 | 516 | 758.2 | 776 | 820.7 | 708.2 | 791.9
691 | 517 | 758.4 | 771.2 | 823.3 | 708.6 | 792.3
692 | 518 | 758.7 | 772.1 | 822.8 | 708.8 | 792
693 | 519 | 759 | 777.2 | 822.4 | 709.2 | 792.7
694 | 520 | 759.4 | 780.9 | 822.5 | 709.5 | 793
695 | 521 | 759.7 | 785.9 | 821.9 | 709.8 | 792.4
696 | 522 | 759.9 | 789.5 | 822.4 | 710.3 | 793.2
697 | 523 | 759.9 | 787 | 821.3 | 710.5 | 794.1
698 | 524 | 759.9 | 784.8 | 821.1 | 711 | 795.1
699 | 525 | 760 | 779.2 | 817.9 | 711.4 | 795.7
700 | 526 | 760.3 | 777.6 | 818.7 | 711.8 | 796.4
701 | 527 | 760.6 | 771.3 | 817 | 712.1 | 796.8
702 | 528 | 760.9 | 770.8 | 814.9 | 712.5 | 796.4
703 | 529 | 760.9 | 770.8 | 814.5 | 712.9 | 795.6
704 | 530 | 760.8 | 764.4 | 810.5 | 713.2 | 794.9
705 | 531 | 760.8 | 762.8 | 810.6 | 713.6 | 794.7
706 | 532 | 760.6 | 765.3 | 813 | 714.2 | 795.7
707 | 533 | 760.5 | 766.9 | 812.3 | 714.8 | 796.3
708 | 534 | 760.5 | 761.5 | 809.5 | 715.2 | 796.6
709 | 535 | 760.5 | 762 | 808.1 | 715.6 | 797.4
710 | 536 | 760.6 | 766.4 | 809.1 | 715.9 | 797.6
711 | 537 | 760.8 | 772.9 | 812.6 | 716.4 | 798.2
712 | 538 | 761.1 | 777.4 | 814.8 | 717 | 798.7
713 | 539 | 761.2 | 778.9 | 814.1 | 717.5 | 797.8
714 | 540 | 761.2 | 780.8 | 814.1 | 717.9 | 796.5
715 | 541 | 761.3 | 775.7 | 810.8 | 718.3 | 794.4
716 | 542 | 761.3 | 768.4 | 811.2 | 718.8 | 794.8
717 | 543 | 761.4 | 767.1 | 809.9 | 719.4 | 794.5
718 | 544 | 761.4 | 764.9 | 810.8 | 720 | 794.8
719 | 545 | 761.7 | 764.1 | 812.8 | 720.8 | 795
720 | 546 | 761.9 | 770.3 | 815.3 | 721.7 | 794.9
721 | 547 | 762.2 | 774.1 | 817.6 | 722.5 | 793
722 | 548 | 762.4 | 776.9 | 817.2 | 723.3 | 793.4
723 | 549 | 762.5 | 771.8 | 814.1 | 724 | 793.4
724 | 550 | 762.6 | 766.2 | 810.5 | 724.7 | 793.2
725 | 551 | 762.6 | 769.6 | 812.8 | 725.5 | 793
726 | 552 | 762.7 | 776.4 | 814.7 | 726.2 | 792.2
727 | 553 | 762.8 | 776.8 | 814.9 | 727 | 793.1
728 | 554 | 763 | 773.4 | 815.6 | 727.7 | 794.4
729 | 555 | 763.3 | 771.8 | 816 | 728.5 | 795
730 | 556 | 763.6 | 771.4 | 815.1 | 729.2 | 794
731 | 557 | 763.8 | 773 | 816.6 | 730 | 794
732 | 558 | 764.1 | 773.1 | 817.8 | 730.7 | 794.7
733 | 559 | 764.4 | 773.3 | 817.1 | 731.2 | 794.4
734 | 560 | 764.7 | 773.9 | 815.1 | 731.9 | 794.9
735 | 561 | 764.9 | 775.9 | 814.9 | 732.5 | 795.1
736 | 562 | 764.9 | 778 | 814.5 | 733.2 | 794.9
737 | 563 | 765.4 | 779.6 | 813.6 | 734.1 | 795.5
738 | 564 | 766 | 776.5 | 812.2 | 735.1 | 795.9
739 | 565 | 766.3 | 769.1 | 809.8 | 736 | 796
740 | 566 | 766.5 | 763.5 | 806.8 | 737 | 796.8
741 | 567 | 766.8 | 753.4 | 800 | 737.9 | 797.4
742 | 568 | 766.8 | 743.6 | 794.9 | 738.7 | 796.8
743 | 569 | 766.7 | 737.7 | 791 | 739.3 | 797.1
744 | 570 | 766.7 | 734.7 | 789.8 | 739.9 | 796.5
745 | 571 | 766.6 | 730 | 788.6 | 740.5 | 796.1
746 | 572 | 766.3 | 722.7 | 782.4 | 740.9 | 796.3
747 | 573 | 766.4 | 707.8 | 770.5 | 741.1 | 793.8
748 | 574 | 766.4 | 695.4 | 769.4 | 741.4 | 792.5
749 | 575 | 766.4 | 683.4 | 762.2 | 741.7 | 791.4
750 | 576 | 766.4 | 688 | 765.3 | 741.9 | 791.5
751 | 577 | 766.3 | 690.4 | 771.2 | 742.3 | 791.8
752 | 578 | 766.2 | 692 | 775.1 | 742.7 | 793.9
753 | 579 | 766.2 | 687.7 | 770.1 | 743.2 | 792.8
754 | 580 | 766.4 | 678.4 | 761.9 | 743.8 | 790.3
755 | 581 | 766.6 | 672 | 761 | 744.3 | 790.2
756 | 582 | 766.6 | 672.4 | 764.3 | 744.9 | 789.8
757 | 583 | 766.6 | 674.1 | 767.1 | 745.4 | 787.9
758 | 584 | 766.7 | 672.5 | 766.9 | 746 | 786.7
759 | 585 | 766.8 | 675.1 | 769.2 | 746.4 | 787.5
760 | 586 | 766.7 | 688.8 | 776.5 | 746.9 | 788.5
761 | 587 | 766.7 | 703.4 | 780.4 | 747.5 | 789.1
762 | 588 | 766.6 | 714.4 | 782.4 | 748.1 | 789.9
763 | 589 | 766.6 | 723.1 | 783.7 | 748.6 | 790.8
764 | 590 | 766.8 | 728.4 | 787.4 | 749 | 791.8
765 | 591 | 767 | 732 | 786.1 | 749.3 | 792.4
766 | 592 | 767 | 732.5 | 786.8 | 749.7 | 792
767 | 593 | 767 | 739.6 | 789.7 | 750.3 | 792.9
768 | 594 | 767.3 | 736.4 | 784.9 | 750.7 | 791.6
769 | 595 | 767.3 | 739.3 | 787.8 | 751 | 791.4
770 | 596 | 767.2 | 743.9 | 788.5 | 751.3 | 791
771 | 597 | 767.5 | 733.2 | 783.6 | 751.8 | 788.8
772 | 598 | 767.7 | 719.1 | 777.9 | 752.3 | 787.7
773 | 599 | 767.9 | 704.9 | 768.1 | 752.8 | 786.4
774 | 600 | 768.2 | 692.3 | 757.3 | 753.2 | 784
775 | 601 | 768.4 | 686.1 | 755.6 | 753.7 | 782.6
776 | 602 | 768.3 | 685.3 | 760.9 | 754.3 | 782.5
777 | 603 | 768.2 | 688.1 | 759.5 | 754.8 | 782
778 | 604 | 768.5 | 680.5 | 750.9 | 755.4 | 778.9
779 | 605 | 768.8 | 672.9 | 740.1 | 756 | 776.4
780 | 606 | 769.3 | 665.9 | 730.4 | 756.4 | 773
781 | 607 | 769.4 | 656.6 | 727.8 | 757 | 771.5
782 | 608 | 769.6 | 649.8 | 723.7 | 757.5 | 768.7
783 | 609 | 770 | 641 | 718.2 | 758 | 767.6
784 | 610 | 770.1 | 634.7 | 721.2 | 758.5 | 767.1
785 | 611 | 769.9 | 634.1 | 728.7 | 759 | 767.4
786 | 612 | 769.5 | 640.1 | 740 | 759.5 | 768
787 | 613 | 769 | 646.6 | 746.8 | 759.8 | 769.8
788 | 614 | 768.8 | 652.4 | 752.9 | 760.2 | 771
789 | 615 | 768.6 | 658.6 | 755.6 | 760.6 | 770.7
790 | 616 | 768.5 | 671 | 763.2 | 761.1 | 773
791 | 617 | 768.3 | 685.1 | 773.4 | 761.4 | 774
792 | 618 | 768.2 | 699.1 | 782.4 | 761.8 | 774.4
793 | 619 | 768.2 | 696.2 | 775.2 | 762 | 771.9
794 | 620 | 768.5 | 685.9 | 767 | 762.2 | 770.6
795 | 621 | 768.6 | 680.9 | 766.2 | 762.4 | 771.7
796 | 622 | 768.4 | 689.8 | 773.6 | 762.7 | 774.1
797 | 623 | 768.2 | 690.8 | 774 | 763.1 | 775.3
798 | 624 | 768 | 703.5 | 777.5 | 763.3 | 776.7
799 | 625 | 767.7 | 714.3 | 781 | 763.4 | 777.7
800 | 626 | 767.5 | 717.9 | 787.6 | 763.6 | 779.6
801 | 627 | 767.3 | 722.3 | 791.7 | 763.8 | 781.5
802 | 628 | 767.4 | 716.3 | 787.3 | 764.2 | 781.7
803 | 629 | 767.9 | 699.8 | 770.2 | 764.4 | 777.6
804 | 630 | 768.5 | 685.1 | 757.6 | 764.7 | 775.5
805 | 631 | 768.7 | 686.8 | 764.3 | 764.9 | 775.5
806 | 632 | 768.6 | 691.7 | 767.9 | 765.1 | 776.6
807 | 633 | 768.6 | 692.1 | 769.1 | 765.3 | 776.4
808 | 634 | 768.4 | 692.1 | 769.4 | 765.5 | 777.2
809 | 635 | 768.2 | 696.1 | 773.5 | 765.8 | 778.3
810 | 636 | 767.8 | 705.2 | 778.1 | 765.9 | 779.1
811 | 637 | 767.5 | 709.8 | 783.2 | 765.9 | 779.8
812 | 638 | 767.2 | 711.9 | 783.9 | 765.9 | 779.7
813 | 639 | 767.1 | 708.8 | 784.4 | 765.9 | 780.3
814 | 640 | 767.1 | 697.9 | 776.1 | 766 | 778.7
815 | 641 | 767.3 | 694.6 | 774.2 | 766.2 | 777.8
816 | 642 | 767.4 | 692.8 | 777 | 766.2 | 776.7
817 | 643 | 767.2 | 700.1 | 783.6 | 766.3 | 777
818 | 644 | 767 | 699.8 | 783.3 | 766.4 | 775.6
819 | 645 | 767.2 | 688.2 | 775.9 | 766.5 | 772.5
820 | 646 | 767.3 | 677.8 | 766.8 | 766.7 | 770.2
821 | 647 | 767.5 | 666.8 | 760.2 | 766.8 | 769.7
822 | 648 | 767.4 | 664.3 | 762.5 | 767.1 | 769.7
823 | 649 | 767.1 | 671.9 | 771.1 | 767.2 | 769.9
824 | 650 | 766.9 | 675.7 | 772.8 | 767.4 | 769.8
825 | 651 | 766.7 | 674.8 | 768.3 | 767.6 | 768.3
826 | 652 | 766.8 | 670.6 | 760.6 | 768 | 767.6
827 | 653 | 767 | 667 | 760.6 | 768.3 | 766.7
828 | 654 | 767 | 672.5 | 760.8 | 768.6 | 766.4
829 | 655 | 767.1 | 671.8 | 756.3 | 768.9 | 765.5
830 | 656 | 767.2 | 665.8 | 753.3 | 769.1 | 764.5
831 | 657 | 767 | 665 | 756 | 769.3 | 764.9
832 | 658 | 766.9 | 659.8 | 759.8 | 769.6 | 764.5
833 | 659 | 767 | 659.5 | 762.2 | 769.9 | 765.7
834 | 660 | 767.3 | 660.8 | 765.5 | 770.2 | 765.9
835 | 661 | 767.4 | 673.6 | 770.2 | 770.3 | 767
836 | 662 | 767.5 | 697.6 | 777.5 | 770.5 | 767.7
837 | 663 | 767.5 | 716.4 | 787.8 | 770.7 | 768.7
838 | 664 | 767.6 | 727.1 | 793 | 770.8 | 769.4
839 | 665 | 767.8 | 733.5 | 796.1 | 770.8 | 770.2
840 | 666 | 767.9 | 732.2 | 797.3 | 770.8 | 771.1
841 | 667 | 768.1 | 719.7 | 792.1 | 770.9 | 769.5
842 | 668 | 768.2 | 710.4 | 789.6 | 771 | 768.7
843 | 669 | 768 | 708.1 | 792.8 | 771 | 770.5
844 | 670 | 767.7 | 718 | 797.8 | 771.1 | 772.1
845 | 671 | 767.7 | 717.1 | 798.2 | 771.2 | 771.4
846 | 672 | 767.6 | 722.1 | 802.9 | 771.4 | 773.2
847 | 673 | 767.7 | 732.5 | 807.7 | 771.7 | 773.7
848 | 674 | 767.7 | 737.7 | 810.9 | 771.8 | 773.9
849 | 675 | 767.7 | 739.7 | 810.7 | 771.9 | 774.3
850 | 676 | 767.8 | 751.8 | 813.3 | 772 | 775.1
851 | 677 | 768 | 762.7 | 814.1 | 772.3 | 775
852 | 678 | 768.2 | 765.8 | 817.9 | 772.4 | 775.7
853 | 679 | 768.6 | 773.2 | 817.3 | 772.6 | 777.5
854 | 680 | 769.1 | 779.2 | 818 | 772.9 | 778
855 | 681 | 769.4 | 779.1 | 818.4 | 773.1 | 778.2
856 | 682 | 769.7 | 770.5 | 811.6 | 773.1 | 776.5
857 | 683 | 769.8 | 772.7 | 814.2 | 773.1 | 776.9
858 | 684 | 769.8 | 771.3 | 815 | 773.4 | 776.7
859 | 685 | 769.9 | 775.7 | 816.5 | 773.4 | 774.5
860 | 686 | 769.8 | 781.3 | 816.2 | 773.3 | 775.2
861 | 687 | 769.7 | 785.3 | 817.3 | 773.2 | 775.6
862 | 688 | 769.9 | 788.8 | 819 | 773.3 | 776.4
863 | 689 | 769.9 | 792.2 | 818.5 | 773.6 | 777.9
864 | 690 | 770.1 | 797.3 | 822.3 | 774 | 777.8
865 | 691 | 770.1 | 794.5 | 822 | 774.3 | 777.4
866 | 692 | 770.3 | 786 | 821.6 | 774.6 | 777.2
867 | 693 | 770.3 | 775.8 | 820.6 | 775 | 777.5
868 | 694 | 770.3 | 774.7 | 822.4 | 775.3 | 778
869 | 695 | 770.3 | 781 | 822.4 | 775.8 | 778.7
870 | 696 | 770.7 | 775 | 819.5 | 776.2 | 779.4
871 | 697 | 771 | 766.6 | 816.4 | 776.7 | 779.7
872 | 698 | 771.3 | 759.3 | 813.9 | 777.1 | 778.7
873 | 699 | 771.6 | 756.2 | 813.2 | 777.5 | 780.4
874 | 700 | 771.7 | 745.9 | 809.3 | 778 | 779.9
875 | 701 | 771.9 | 735.8 | 804.3 | 778.5 | 780.2
876 | 702 | 771.9 | 730.2 | 799.2 | 778.8 | 779.8
877 | 703 | 772 | 719.7 | 792.8 | 779.2 | 778.4
878 | 704 | 772.1 | 712.3 | 787.4 | 779.5 | 776.4
879 | 705 | 772.1 | 712.5 | 792 | 779.8 | 775.6
880 | 706 | 772.1 | 708.9 | 791 | 780.2 | 775.5
881 | 707 | 772.1 | 700.8 | 788.2 | 780.3 | 774.1
882 | 708 | 772.1 | 695.8 | 785.6 | 780.4 | 773.2
883 | 709 | 772.3 | 686.4 | 781 | 780.6 | 771
884 | 710 | 772.1 | 682.3 | 781.7 | 780.7 | 769.7
885 | 711 | 772 | 679.9 | 778.1 | 780.8 | 770.2
886 | 712 | 771.7 | 685.7 | 783.9 | 780.9 | 771.1
887 | 713 | 771.4 | 686.5 | 784.2 | 780.9 | 770.3
888 | 714 | 771.4 | 684.4 | 781.7 | 780.9 | 769.4
889 | 715 | 771.3 | 681 | 780.4 | 781 | 767.4
890 | 716 | 771.1 | 681.3 | 783.5 | 781 | 766.4
891 | 717 | 770.8 | 689.6 | 785.7 | 780.8 | 765.5
892 | 718 | 770.9 | 687.6 | 784 | 780.6 | 764.7
893 | 719 | 771.1 | 691 | 784.9 | 780.6 | 764.4
894 | 720 | 770.9 | 692.5 | 783.5 | 780.5 | 765.1
895 | 721 | 770.8 | 701.5 | 787.1 | 780.4 | 767
896 | 722 | 771 | 700.2 | 786 | 780.6 | 767.4
897 | 723 | 771 | 699.3 | 790.7 | 780.7 | 766.2
898 | 724 | 770.9 | 698.6 | 790.5 | 780.8 | 765.3
899 | 725 | 770.9 | 698.9 | 792.9 | 780.9 | 765.1
900 | 726 | 770.8 | 706.4 | 800.5 | 780.9 | 765
901 | 727 | 770.5 | 710.9 | 803.3 | 780.9 | 765.9
902 | 728 | 770.2 | 719.2 | 804.4 | 780.9 | 767.5
903 | 729 | 769.9 | 735.2 | 807 | 780.9 | 768.9
904 | 730 | 769.8 | 745.3 | 809.2 | 781 | 769.8
905 | 731 | 769.8 | 752.2 | 810.2 | 781 | 771.4
906 | 732 | 769.8 | 755.5 | 813.3 | 781.1 | 773.5
907 | 733 | 769.9 | 760.3 | 814.6 | 781.2 | 775.3
908 | 734 | 770.3 | 762.6 | 817.5 | 781.3 | 777.3
909 | 735 | 770.6 | 756 | 816.2 | 781.4 | 778.4
910 | 736 | 770.9 | 750.3 | 814.6 | 781.6 | 778
911 | 737 | 770.8 | 756 | 816.5 | 781.6 | 778.7
912 | 738 | 771.2 | 766.2 | 817.7 | 781.9 | 779.9
913 | 739 | 771.6 | 771.9 | 819.9 | 782.3 | 780.4
914 | 740 | 772 | 773 | 819.9 | 782.6 | 779.1
915 | 741 | 772.5 | 770.9 | 818.7 | 782.8 | 777.4
916 | 742 | 772.6 | 779.1 | 821 | 782.9 | 778.7
917 | 743 | 772.9 | 783.9 | 821.2 | 783.2 | 778.7
918 | 744 | 772.9 | 789 | 820.2 | 783.4 | 779.1
919 | 745 | 772.9 | 793 | 820.9 | 783.6 | 781.2
920 | 746 | 773.1 | 798.5 | 820.8 | 783.7 | 782
921 | 747 | 773.2 | 802.5 | 821.6 | 783.8 | 782.1
922 | 748 | 773.5 | 805.3 | 823.3 | 783.8 | 782.6
923 | 749 | 773.5 | 804.7 | 826 | 784 | 784.7
924 | 750 | 773.5 | 807 | 824.3 | 784.2 | 785.6
925 | 751 | 773.7 | 805.3 | 823.3 | 784.3 | 786
926 | 752 | 773.6 | 806.1 | 824.8 | 784.4 | 786.9
927 | 753 | 773.5 | 796.8 | 823.6 | 784.6 | 788
928 | 754 | 773.6 | 800 | 825.1 | 785 | 788.4
929 | 755 | 773.7 | 801.2 | 825.5 | 785.3 | 788.9
930 | 756 | 773.9 | 800.5 | 826 | 785.5 | 788.6
931 | 757 | 774.2 | 804.4 | 826.1 | 785.8 | 789.1
932 | 758 | 774.8 | 801.5 | 823.4 | 786 | 789.1
933 | 759 | 775.7 | 795 | 819.5 | 786.4 | 788.6
934 | 760 | 776.1 | 793.2 | 821.7 | 786.7 | 787.6
935 | 761 | 776 | 793.9 | 820.4 | 786.8 | 787
936 | 762 | 775.8 | 794.6 | 820.1 | 786.9 | 787.2
937 | 763 | 775.7 | 783.8 | 815.6 | 787 | 786.6
938 | 764 | 775.9 | 769 | 808.6 | 787.2 | 785.5
939 | 765 | 776.1 | 757.9 | 800.9 | 787.4 | 785.3
940 | 766 | 776.3 | 744.7 | 790.7 | 787.6 | 782.5
941 | 767 | 776.4 | 734.9 | 784.3 | 787.9 | 781.7
942 | 768 | 776.1 | 728.1 | 784 | 788.2 | 780.7
943 | 769 | 775.8 | 719 | 783.4 | 788.5 | 779.5
944 | 770 | 775.7 | 712.5 | 781.9 | 788.7 | 778.8
945 | 771 | 776.2 | 695.4 | 767.9 | 789 | 776.3
946 | 772 | 776.3 | 690.7 | 771.4 | 789.2 | 775.9
947 | 773 | 776.2 | 684.9 | 768.1 | 789.3 | 775.8
948 | 774 | 776.3 | 688.5 | 775.5 | 789.7 | 776.7
949 | 775 | 776 | 695.2 | 784.9 | 790 | 778.1
950 | 776 | 775.7 | 704.5 | 792 | 790.1 | 779.5
951 | 777 | 775.3 | 714.4 | 797 | 790.1 | 780.4
952 | 778 | 774.7 | 729.6 | 801.5 | 790.4 | 780.6
953 | 779 | 774.1 | 739.4 | 802.8 | 790.7 | 779.9
954 | 780 | 773.4 | 739.3 | 798.8 | 791.1 | 779.8
955 | 781 | 772.4 | 750.4 | 805.3 | 791.5 | 781
956 | 782 | 771.8 | 758.7 | 808.5 | 791.8 | 782
957 | 783 | 771.4 | 764.7 | 809.4 | 792.1 | 782.7
958 | 784 | 771.2 | 765.5 | 810.5 | 792.3 | 783.6
959 | 785 | 771.2 | 769.7 | 811.6 | 792.6 | 786
960 | 786 | 771.2 | 769.5 | 813.1 | 792.9 | 786.5
961 | 787 | 771.3 | 777.1 | 813.1 | 793.2 | 785.5
962 | 788 | 771.6 | 774.9 | 812.5 | 793.3 | 784.4
963 | 789 | 772.1 | 764.9 | 806.3 | 793.6 | 782.4
964 | 790 | 772.2 | 752.2 | 803.1 | 794 | 781.4
965 | 791 | 771.7 | 749 | 803.1 | 794.5 | 780
966 | 792 | 771.3 | 758.3 | 807.8 | 794.8 | 780
967 | 793 | 771.3 | 762.9 | 808.3 | 794.9 | 779.7
968 | 794 | 771 | 762.1 | 810.1 | 795 | 778.6
969 | 795 | 770.3 | 764.6 | 812.4 | 795.1 | 778.3
970 | 796 | 769.7 | 757.8 | 810 | 795.1 | 779.1
971 | 797 | 769.4 | 760.3 | 814 | 795.2 | 780.6
972 | 798 | 769.4 | 769.4 | 818.8 | 795.4 | 781.2
973 | 799 | 769.7 | 767.5 | 818.5 | 795.5 | 782.7
974 | 800 | 769.7 | 769.6 | 814 | 795.6 | 783.4
975 | 801 | 770.1 | 767.6 | 809.7 | 796 | 783.3
976 | 802 | 770.1 | 778.9 | 813 | 796.2 | 785.2
977 | 803 | 770.3 | 782 | 816.9 | 796.3 | 785.8
978 | 804 | 770.6 | 787.5 | 819 | 796.4 | 787.3
979 | 805 | 770.9 | 796.3 | 822.3 | 796.5 | 788.6
980 | 806 | 771.6 | 800.7 | 826.4 | 796.8 | 787.7
981 | 807 | 771.6 | 804.4 | 827.7 | 796.9 | 788.3
982 | 808 | 771.7 | 812.8 | 827.1 | 797 | 789.5
983 | 809 | 772 | 815.8 | 826.3 | 797.2 | 789.5
984 | 810 | 772.1 | 819 | 825.1 | 797.3 | 789.7
985 | 811 | 772.3 | 819.3 | 825.9 | 797.4 | 789.8
986 | 812 | 772.5 | 819 | 826.1 | 797.5 | 790.9
987 | 813 | 772.6 | 821.1 | 824.7 | 797.7 | 791.3
988 | 814 | 772.5 | 817.7 | 826.5 | 797.8 | 790.5
989 | 815 | 772.7 | 813.9 | 826.4 | 798 | 792.2
990 | 816 | 773.2 | 800.3 | 825.6 | 798.3 | 791.5
991 | 817 | 773.2 | 792.1 | 824.5 | 798.7 | 790
992 | 818 | 773.5 | 773.6 | 814.8 | 799.2 | 789.2
993 | 819 | 774 | 758.9 | 809.4 | 799.8 | 787.1
994 | 820 | 773.7 | 748.7 | 808 | 800.4 | 788.3
995 | 821 | 773.8 | 746 | 809.8 | 801 | 788.6
996 | 822 | 773.6 | 760.5 | 812.7 | 801.4 | 789.3
997 | 823 | 773.4 | 766.3 | 814.6 | 801.5 | 789.9
998 | 824 | 773.5 | 767.1 | 818.7 | 801.7 | 789.2
999 | 825 | 773.3 | 776.1 | 821 | 801.8 | 790
1000 | 826 | 773.1 | 782.9 | 822.9 | 801.9 | 791
1001 | 827 | 773.2 | 790.7 | 824.8 | 801.9 | 791.5
1002 | 828 | 773.2 | 799.9 | 825 | 801.8 | 792
1003 | 829 | 773.3 | 802.1 | 826.1 | 801.6 | 792.5
1004 | 830 | 773.3 | 804.6 | 825.6 | 801.4 | 793.5
1005 | 831 | 773.5 | 804 | 826.3 | 801.3 | 794.8
1006 | 832 | 773.8 | 799.5 | 826.5 | 801.4 | 793.2
1007 | 833 | 773.7 | 801.9 | 825.4 | 801.4 | 792.8
1008 | 834 | 773.5 | 800.7 | 823.5 | 801.4 | 791.7
1009 | 835 | 773.4 | 805.7 | 827.1 | 801.5 | 791.8
1010 | 836 | 773.5 | 800.6 | 827.2 | 801.5 | 791.5
1011 | 837 | 773.7 | 782.8 | 822.9 | 801.8 | 789.9
1012 | 838 | 773.8 | 776.9 | 819.9 | 802.3 | 789.2
1013 | 839 | 774.1 | 772.1 | 817.4 | 802.8 | 789.3
1014 | 840 | 773.9 | 769.1 | 817.1 | 803.3 | 789.9
1015 | 841 | 774.2 | 755.5 | 808.1 | 803.6 | 789
1016 | 842 | 774.4 | 748.7 | 805.4 | 804 | 787.5
1017 | 843 | 774.3 | 744.8 | 802.8 | 804.5 | 787.3
1018 | 844 | 774.1 | 734.7 | 801.2 | 804.6 | 786.6
1019 | 845 | 773.7 | 730 | 802.6 | 804.8 | 787
1020 | 846 | 773.5 | 742.2 | 808.6 | 805.1 | 788.4
1021 | 847 | 773.2 | 751.8 | 812.5 | 805.1 | 789
1022 | 848 | 773 | 753.7 | 812.8 | 804.9 | 788.8
1023 | 849 | 772.6 | 753.7 | 812.4 | 804.7 | 790.3
1024 | 850 | 772.4 | 763 | 817.4 | 804.7 | 792
1025 | 851 | 772.3 | 763.7 | 818.3 | 804.6 | 792.3
1026 | 852 | 772 | 767.5 | 817.4 | 804.4 | 791
1027 | 853 | 771.6 | 776.1 | 820.3 | 804.3 | 791.4
1028 | 854 | 771.5 | 785.3 | 823.2 | 804.1 | 789.8
1029 | 855 | 771.5 | 779.4 | 821.6 | 803.8 | 791
1030 | 856 | 771.6 | 780.7 | 821.8 | 803.6 | 792.1
1031 | 857 | 771.5 | 793 | 823.7 | 803.6 | 790.7
1032 | 858 | 771.8 | 800.6 | 825.3 | 803.3 | 789.1
1033 | 859 | 772 | 807.4 | 825.5 | 803.2 | 787.8
1034 | 860 | 772.1 | 807 | 826.4 | 803.2 | 786.3
1035 | 861 | 772 | 800.4 | 821.7 | 803.4 | 782.2
1036 | 862 | 771.6 | 806.8 | 823.6 | 803.4 | 781.1
1037 | 863 | 771.4 | 808.5 | 826.8 | 803.5 | 782.2
1038 | 864 | 771.4 | 810 | 828.8 | 803.5 | 784
1039 | 865 | 771.4 | 811.1 | 828.7 | 803.8 | 785.2
1040 | 866 | 771.7 | 814.2 | 827.6 | 804.1 | 785.6
1041 | 867 | 771.8 | 818.6 | 826.1 | 804.2 | 785.1
1042 | 868 | 771.9 | 819.2 | 828.8 | 804.3 | 786.1
1043 | 869 | 771.9 | 819.8 | 830.7 | 804.4 | 784.8
1044 | 870 | 772.2 | 817.7 | 830.6 | 804.5 | 785.6
1045 | 871 | 772.3 | 814.6 | 831.5 | 804.8 | 785.9
1046 | 872 | 772.6 | 807.6 | 830.8 | 805 | 786.5
1047 | 873 | 772.6 | 798.8 | 829.2 | 805.5 | 784.9
1048 | 874 | 772.5 | 785.9 | 821.7 | 805.8 | 783.8
1049 | 875 | 772.4 | 778.3 | 819.7 | 806.2 | 782.4
1050 | 876 | 772 | 776.2 | 820.7 | 806.6 | 780.6
1051 | 877 | 771.7 | 764.4 | 815.1 | 806.8 | 777.8
1052 | 878 | 771.9 | 745 | 803.1 | 806.8 | 774.5
1053 | 879 | 771.9 | 739.1 | 801.2 | 806.9 | 774.2
1054 | 880 | 771.7 | 746.5 | 803.7 | 807 | 775.2
1055 | 881 | 772 | 744.7 | 802 | 806.9 | 776.7
1056 | 882 | 772.4 | 738.7 | 799.9 | 807.1 | 776.8
1057 | 883 | 772.5 | 729.3 | 794.7 | 807.3 | 775.8
1058 | 884 | 772.7 | 714.4 | 786.7 | 807.6 | 775
1059 | 885 | 773.2 | 707.4 | 777.8 | 808.1 | 773.5
1060 | 886 | 773.2 | 707.4 | 782.9 | 808.7 | 774.5
1061 | 887 | 772.5 | 717.4 | 788.2 | 809 | 775.4
1062 | 888 | 771.6 | 728.5 | 790.4 | 808.9 | 775.6
1063 | 889 | 771.1 | 739.3 | 797.1 | 808.7 | 776.9
1064 | 890 | 770.8 | 749.7 | 799 | 808.5 | 777.5
1065 | 891 | 770.5 | 751.3 | 796.9 | 808.1 | 777.2
1066 | 892 | 770.1 | 736.6 | 790 | 807.8 | 775.4
1067 | 893 | 769.8 | 729.4 | 785.8 | 807.8 | 773.9
1068 | 894 | 769.8 | 714.2 | 772.7 | 807.7 | 772.3
1069 | 895 | 769.9 | 704.2 | 765.8 | 807.5 | 771
1070 | 896 | 769.7 | 691.5 | 759.1 | 807.7 | 769.4
1071 | 897 | 770 | 679.4 | 751.5 | 807.8 | 768.4
1072 | 898 | 770.4 | 669.4 | 740.6 | 807.9 | 766.5
1073 | 899 | 770.2 | 667.3 | 740 | 807.9 | 766.6
1074 | 900 | 770.6 | 660.4 | 733.4 | 808 | 765.7
1075 | 901 | 770.9 | 660 | 740.5 | 807.8 | 766.2
1076 | 902 | 770.9 | 660.8 | 746.4 | 807.7 | 765.9
1077 | 903 | 770.8 | 665.2 | 754.4 | 807.5 | 766.8
1078 | 904 | 770.9 | 662.1 | 745.9 | 807.4 | 767.2
1079 | 905 | 770.3 | 676 | 757 | 806.8 | 769.5
1080 | 906 | 769.8 | 674.5 | 755.1 | 806.8 | 769.5
1081 | 907 | 769.5 | 677.5 | 762 | 806.2 | 771.3
1082 | 908 | 769.3 | 692.9 | 769.4 | 805.5 | 772.8
1083 | 909 | 768.9 | 697.2 | 774.2 | 804.9 | 773.3
1084 | 910 | 768.6 | 696.3 | 775.7 | 804.4 | 773
1085 | 911 | 768.7 | 702.4 | 779.2 | 803.6 | 773.5
1086 | 912 | 768.4 | 719.4 | 788.9 | 803.2 | 774.9
1087 | 913 | 768.5 | 719.9 | 790.1 | 803 | 775.3
1088 | 914 | 768.4 | 720.7 | 792 | 802.4 | 777
1089 | 915 | 768.2 | 721 | 795.6 | 802.3 | 776.1
1090 | 916 | 767.8 | 728.5 | 801.2 | 802.1 | 775.8
1091 | 917 | 767.3 | 731.8 | 804.9 | 801.5 | 775.9
1092 | 918 | 767.5 | 732.8 | 805 | 800.8 | 777.9
1093 | 919 | 768 | 725.8 | 799 | 800.7 | 778.6
1094 | 920 | 768.6 | 710.7 | 788.3 | 800.6 | 777.3
1095 | 921 | 769 | 710.4 | 790.7 | 800.7 | 777.6
1096 | 922 | 769.3 | 714 | 790 | 800.8 | 778.2
1097 | 923 | 769.8 | 712.2 | 789.9 | 801.2 | 777.5
1098 | 924 | 769.7 | 721.8 | 794.8 | 801.3 | 778.6
1099 | 925 | 769.5 | 731 | 799.2 | 801.4 | 779.2
1100 | 926 | 769 | 725.9 | 798.1 | 801.3 | 777.5
1101 | 927 | 768.6 | 722.5 | 795.8 | 800.8 | 776.9
1102 | 928 | 768.3 | 724.9 | 798.6 | 800.3 | 778.1
1103 | 929 | 768.5 | 741.8 | 802.3 | 800.1 | 780.4
1104 | 930 | 768.4 | 752 | 806 | 799.6 | 780.7
1105 | 931 | 768.5 | 758.2 | 808.5 | 798.8 | 781.8
1106 | 932 | 769 | 755 | 809 | 798.5 | 782.2
1107 | 933 | 769.5 | 738.9 | 802.7 | 798.3 | 781
1108 | 934 | 770.3 | 726.1 | 792.2 | 798.1 | 780.3
1109 | 935 | 770 | 724.9 | 794.4 | 798 | 782.3
1110 | 936 | 769.8 | 726.7 | 797.1 | 797.8 | 783.2
1111 | 937 | 769.6 | 729.5 | 798 | 798.2 | 780.6
1112 | 938 | 769.7 | 727.4 | 795.3 | 798.1 | 779.8
1113 | 939 | 769.6 | 718.6 | 790.6 | 798 | 778.8
1114 | 940 | 770.1 | 701 | 775.7 | 798.4 | 776.4
1115 | 941 | 770.2 | 694.4 | 774.8 | 798.8 | 773.3
1116 | 942 | 769.4 | 707.1 | 781.2 | 799.1 | 774
1117 | 943 | 769 | 719.2 | 789.6 | 799.1 | 774.8
1118 | 944 | 768.8 | 734.4 | 795.4 | 799 | 777
1119 | 945 | 768.7 | 749.6 | 801.6 | 798.8 | 778.2
1120 | 946 | 768.8 | 748.8 | 805 | 799 | 777.8
1121 | 947 | 768.5 | 747.6 | 808.1 | 798.8 | 775.4
1122 | 948 | 768.4 | 749.3 | 806.3 | 798.9 | 773.6
1123 | 949 | 768.4 | 739.5 | 803.2 | 798.9 | 772
1124 | 950 | 768 | 733.9 | 802.9 | 798.6 | 772.5
1125 | 951 | 767.7 | 721.5 | 793.6 | 798.5 | 770.5
1126 | 952 | 768 | 706.1 | 778 | 798.4 | 768.4
1127 | 953 | 768.2 | 696.3 | 765.8 | 798.4 | 767.4
1128 | 954 | 768.2 | 690.3 | 763.4 | 799 | 766.8
1129 | 955 | 767.8 | 690.4 | 767.6 | 799.8 | 767.7
1130 | 956 | 767.4 | 694.1 | 773.9 | 799.6 | 768
1131 | 957 | 766.7 | 710.1 | 780.7 | 799 | 769.1
1132 | 958 | 766.4 | 713.9 | 784.2 | 798.4 | 769.1
1133 | 959 | 766.4 | 705.9 | 779.1 | 798 | 767.7
1134 | 960 | 765.7 | 713.1 | 783.2 | 797.8 | 768.9
1135 | 961 | 765.2 | 721 | 785.9 | 797.8 | 768.2
1136 | 962 | 764.7 | 722.6 | 789.3 | 797.7 | 769.1
1137 | 963 | 764 | 721.4 | 788.4 | 797.5 | 769.2
1138 | 964 | 763.9 | 715.8 | 783 | 797.5 | 768.2
1139 | 965 | 763.6 | 712.3 | 780.2 | 797.2 | 766.6
1140 | 966 | 763.1 | 709.8 | 779.1 | 797 | 765.5
1141 | 967 | 762.7 | 714.3 | 783.7 | 796.7 | 765.5
1142 | 968 | 762.4 | 711.2 | 782.7 | 797 | 763.6
1143 | 969 | 762.5 | 711.7 | 787.1 | 797 | 762.5
1144 | 970 | 762.4 | 719.5 | 792.6 | 796.6 | 763.8
1145 | 971 | 762.6 | 721.3 | 792.2 | 796.1 | 764.6
1146 | 972 | 763 | 734.1 | 795.1 | 795.2 | 767.2
1147 | 973 | 763.1 | 736.9 | 796.7 | 795 | 767.7
1148 | 974 | 763.8 | 736.7 | 797.1 | 794.6 | 767.1
1149 | 975 | 764.8 | 718.8 | 786.1 | 794.4 | 765.6
1150 | 976 | 765.8 | 702.5 | 773.5 | 794.8 | 763.7
1151 | 977 | 766.4 | 692.1 | 771.8 | 795.7 | 760.9
1152 | 978 | 766.2 | 686 | 773.6 | 795.9 | 760.3
1153 | 979 | 765.9 | 682.5 | 774.3 | 796 | 761.8
1154 | 980 | 765.9 | 685.2 | 778 | 796.3 | 762.6
1155 | 981 | 765.6 | 700.6 | 784.2 | 796.4 | 764.3
1156 | 982 | 765.2 | 705.8 | 783.5 | 796.2 | 766.2
1157 | 983 | 765 | 714.6 | 786.7 | 795.6 | 767.6
1158 | 984 | 764.5 | 708.7 | 784.8 | 795.8 | 766.7
1159 | 985 | 764.1 | 704.3 | 782.1 | 795.4 | 767.2
1160 | 986 | 763.9 | 707.8 | 784.6 | 795 | 768.3
1161 | 987 | 763.9 | 707.8 | 784.8 | 795 | 767.6
1162 | 988 | 764 | 720.3 | 792 | 794.7 | 769.5
1163 | 989 | 763.9 | 737.7 | 798.3 | 794.2 | 771.1
1164 | 990 | 764.1 | 744.3 | 803.8 | 793.7 | 773.1
1165 | 991 | 764.2 | 750.6 | 807.6 | 792.8 | 774.4
1166 | 992 | 764.4 | 754.3 | 807.8 | 792.6 | 775.1
1167 | 993 | 764.7 | 752.1 | 805.5 | 792.3 | 776
1168 | 994 | 764.7 | 761.2 | 807.6 | 792.5 | 777.1
1169 | 995 | 765 | 771 | 811.1 | 791.6 | 779.3
1170 | 996 | 765.2 | 779.1 | 815.1 | 791.7 | 780.7
1171 | 997 | 765.6 | 775.3 | 815.9 | 791.4 | 781.6
1172 | 998 | 766.2 | 760.9 | 814 | 790.8 | 781.7
1173 | 999 | 766.4 | 758.1 | 812.9 | 791.2 | 781.1
1174 | 1000 | 766.3 | 760 | 814.3 | 791.6 | 781.3
1175 | 1001 | 766.6 | 766.4 | 818.8 | 791.3 | 783.6
1176 | 1002 | 767.3 | 767.9 | 821.2 | 791.4 | 784.6
1177 | 1003 | 768 | 776.1 | 823 | 791.5 | 786.3
1178 | 1004 | 768.5 | 784.1 | 824.8 | 791.9 | 787
1179 | 1005 | 769.4 | 767.6 | 818.8 | 792.4 | 786.9
1180 | 1006 | 770.3 | 747.8 | 800.9 | 792.7 | 784.1
1181 | 1007 | 771.2 | 731.1 | 787 | 793.3 | 780.8
1182 | 1008 | 771.2 | 726.9 | 791.3 | 793.6 | 782.3
1183 | 1009 | 771.6 | 716 | 792 | 793.7 | 781.7
1184 | 1010 | 772.1 | 714.8 | 788.1 | 794.3 | 780.5
1185 | 1011 | 772.6 | 707.4 | 779.7 | 795.2 | 778.3
1186 | 1012 | 773.2 | 696.1 | 772.8 | 795.4 | 774.9
1187 | 1013 | 772.9 | 695.9 | 777.7 | 796.2 | 773
1188 | 1014 | 772.4 | 702.3 | 783.4 | 796 | 772.1
1189 | 1015 | 771.8 | 720.5 | 792.7 | 796 | 774.1
1190 | 1016 | 771.6 | 740.7 | 801.6 | 795.6 | 775.8
1191 | 1017 | 771.8 | 742.3 | 802.8 | 795.7 | 774
1192 | 1018 | 771.8 | 750.8 | 805.7 | 795.2 | 775.2
1193 | 1019 | 771.9 | 752.8 | 810.5 | 794.7 | 778
1194 | 1020 | 772 | 764.1 | 815.8 | 794.7 | 779.5
1195 | 1021 | 772 | 775.7 | 820.4 | 794.4 | 779
1196 | 1022 | 772.2 | 784.8 | 822.4 | 793.7 | 781.5
1197 | 1023 | 772.7 | 791 | 823.6 | 793.1 | 783.5
1198 | 1024 | 773 | 795.2 | 824.1 | 792.8 | 783.5
1199 | 1025 | 773.5 | 789 | 825.5 | 792.8 | 783.5
1200 | 1026 | 773.6 | 787.5 | 823.1 | 792.8 | 784.4
1201 | 1027 | 773.6 | 788 | 825.5 | 792.8 | 784.3
1202 | 1028 | 773.5 | 793 | 827.5 | 792.2 | 786.7
1203 | 1029 | 773.7 | 800 | 828.3 | 791.8 | 787.9
1204 | 1030 | 774.1 | 796.2 | 833.5 | 792.6 | 787.4
1205 | 1031 | 774 | 797.6 | 836.8 | 792.7 | 788.8
1206 | 1032 | 774 | 788.3 | 835.9 | 792.9 | 786.3
1207 | 1033 | 773.9 | 774.5 | 828 | 792.8 | 784.1
1208 | 1034 | 774.5 | 767.1 | 820.4 | 792.7 | 783.6
1209 | 1035 | 774.2 | 760.1 | 816 | 792.7 | 782.1
1210 | 1036 | 774.2 | 760.8 | 816.1 | 793.5 | 783.1
1211 | 1037 | 774.2 | 761.6 | 816.3 | 793.6 | 784.8
1212 | 1038 | 774.5 | 754.9 | 814.4 | 793.6 | 784.5
1213 | 1039 | 774.9 | 745.2 | 810.6 | 794 | 783.9
1214 | 1040 | 774.7 | 743.9 | 810.5 | 794.7 | 782.3
1215 | 1041 | 775.1 | 741.5 | 804.8 | 795.7 | 782.3
1216 | 1042 | 775 | 746 | 809.2 | 796.1 | 781.8
1217 | 1043 | 774.9 | 749.2 | 809.9 | 796.4 | 782.4
1218 | 1044 | 774.8 | 744.5 | 807.8 | 796.1 | 781
1219 | 1045 | 774.8 | 744.1 | 806.2 | 795.8 | 783.1
1220 | 1046 | 775 | 737.9 | 800 | 795.8 | 782.5
1221 | 1047 | 774.9 | 736.1 | 802.5 | 796.5 | 781.5
1222 | 1048 | 774.9 | 748.8 | 807.1 | 796.3 | 783.4
1223 | 1049 | 774.8 | 750.7 | 809.4 | 796.3 | 784.2
1224 | 1050 | 774.8 | 750.1 | 813.2 | 795.7 | 784.1
1225 | 1051 | 774.9 | 756.9 | 817.9 | 795.8 | 785.5
1226 | 1052 | 775.4 | 751.1 | 816.4 | 796.3 | 785.7
1227 | 1053 | 776.2 | 738.3 | 807.1 | 796.3 | 785
1228 | 1054 | 777.6 | 722 | 784 | 796.3 | 783.2
1229 | 1055 | 778 | 715.6 | 783.4 | 797 | 782.9
1230 | 1056 | 778.7 | 706.7 | 780.2 | 797.4 | 781.7
1231 | 1057 | 778.5 | 710 | 788.4 | 797.8 | 781.3
1232 | 1058 | 778.2 | 712.5 | 792.5 | 797.8 | 782.6
1233 | 1059 | 778.1 | 723.3 | 798.4 | 798.5 | 783.4
1234 | 1060 | 778.4 | 723.9 | 800.1 | 798.3 | 784.2
1235 | 1061 | 778.2 | 729.5 | 804.9 | 797.6 | 786
1236 | 1062 | 778.2 | 726.7 | 801.4 | 797.7 | 786.5
1237 | 1063 | 777.7 | 732 | 802.7 | 797.7 | 787.2
1238 | 1064 | 777.2 | 737.1 | 804.1 | 797.6 | 788.2
1239 | 1065 | 776.5 | 745.1 | 806.6 | 797.6 | 789.6
1240 | 1066 | 775.9 | 746.7 | 806.9 | 797.8 | 790.3
1241 | 1067 | 775.8 | 741.7 | 806.9 | 797.5 | 791
1242 | 1068 | 775.3 | 753.6 | 809.5 | 797.4 | 791.9
1243 | 1069 | 775.2 | 755.4 | 810.9 | 797.2 | 792.7
1244 | 1070 | 775.5 | 758.3 | 809.6 | 796.5 | 793.7
1245 | 1071 | 775.3 | 767.9 | 813.3 | 796.3 | 794.3
1246 | 1072 | 775 | 775.6 | 817.4 | 796.5 | 795.1
1247 | 1073 | 774.8 | 774.6 | 818.6 | 796.1 | 795.4
1248 | 1074 | 774.9 | 772.9 | 821.2 | 795.8 | 795.8
1249 | 1075 | 775.3 | 764.8 | 814.9 | 794.8 | 795.2
1250 | 1076 | 775.9 | 753.3 | 809.9 | 794.4 | 794.9
1251 | 1077 | 776.1 | 748.3 | 808.2 | 795.3 | 792.8
1252 | 1078 | 776.1 | 754.5 | 813 | 796.3 | 793.7
1253 | 1079 | 776.1 | 762.2 | 818.3 | 796.3 | 795.6
1254 | 1080 | 776.1 | 751.7 | 814.4 | 795.4 | 796.3
1255 | 1081 | 776.5 | 742.5 | 807.3 | 795.6 | 795.5
1256 | 1082 | 776.2 | 757.3 | 811.7 | 795.6 | 796.8
1257 | 1083 | 776.5 | 775.2 | 815.9 | 795.6 | 798
1258 | 1084 | 776.4 | 786.3 | 818.6 | 795 | 798.8
1259 | 1085 | 776.3 | 782.7 | 822.2 | 794.9 | 797.3
1260 | 1086 | 776.7 | 770.5 | 818.7 | 794.6 | 795.4
1261 | 1087 | 776.4 | 767.7 | 820.5 | 794 | 797
1262 | 1088 | 776.5 | 779.4 | 828.6 | 793.8 | 799.1
1263 | 1089 | 776.4 | 775 | 826.9 | 793.7 | 800.6
1264 | 1090 | 776.5 | 781.4 | 826.8 | 793.4 | 802
1265 | 1091 | 776.5 | 791.1 | 829.9 | 793.8 | 802.6
1266 | 1092 | 776.8 | 795.3 | 830 | 793.5 | 803.6
1267 | 1093 | 776.8 | 795.4 | 831.3 | 792.5 | 804.6
1268 | 1094 | 777 | 791.7 | 834.8 | 792 | 805.9
1269 | 1095 | 777.5 | 793 | 831.6 | 792.4 | 805.4
1270 | 1096 | 778.6 | 780.2 | 824.5 | 793 | 803
1271 | 1097 | 778.7 | 765 | 812.9 | 793.2 | 803.8
1272 | 1098 | 779 | 747.6 | 799.8 | 793.8 | 801.1
1273 | 1099 | 778.7 | 748.9 | 805.2 | 794.9 | 799.6
1274 | 1100 | 778.7 | 763.1 | 812.2 | 795.8 | 799.9
1275 | 1101 | 778.8 | 760.4 | 812.3 | 795.9 | 799.3
1276 | 1102 | 778.6 | 759.2 | 812.4 | 795.2 | 800.4
1277 | 1103 | 778.3 | 762.1 | 814.9 | 795.2 | 801.1
1278 | 1104 | 778 | 768.1 | 815.3 | 795.5 | 801.8
1279 | 1105 | 777.7 | 780.2 | 818 | 795.3 | 802.1
1280 | 1106 | 777.8 | 788.1 | 818.2 | 794.8 | 803.3
1281 | 1107 | 778 | 781.1 | 821.5 | 794.4 | 801.4
1282 | 1108 | 777.7 | 784.1 | 822.9 | 794.2 | 800.1
1283 | 1109 | 777.8 | 792.8 | 826.6 | 794 | 800.7
1284 | 1110 | 777.9 | 800.3 | 830.9 | 794.1 | 800.2
1285 | 1111 | 778 | 806.5 | 829.5 | 793.3 | 801.5
1286 | 1112 | 778 | 811.1 | 830.4 | 791.9 | 802.5
1287 | 1113 | 778.2 | 812.4 | 828.9 | 791.4 | 802.8
1288 | 1114 | 778.4 | 814.8 | 833.1 | 791.8 | 802.8
1289 | 1115 | 778.7 | 818.5 | 831.6 | 791.5 | 804.9
1290 | 1116 | 778.9 | 820.6 | 828.4 | 791 | 805.4
1291 | 1117 | 779.2 | 822.3 | 829.2 | 790.7 | 806.4
1292 | 1118 | 779.2 | 819.2 | 828.3 | 790.5 | 806.9
1293 | 1119 | 779.1 | 806 | 827.8 | 790.6 | 806
1294 | 1120 | 779.1 | 789.2 | 829.6 | 789.8 | 803.5
1295 | 1121 | 779.2 | 775.5 | 830.6 | 790.4 | 803.4
1296 | 1122 | 778.7 | 782.6 | 830 | 790.7 | 804.7
1297 | 1123 | 778.7 | 792.1 | 831.3 | 791.1 | 806.1
1298 | 1124 | 778.7 | 792.4 | 832.5 | 791.6 | 806.4
1299 | 1125 | 778.7 | 794.4 | 829.1 | 792 | 807
1300 | 1126 | 778.5 | 798.6 | 829.9 | 791.6 | 808.3
1301 | 1127 | 778.5 | 801 | 833.7 | 791.6 | 809.4
1302 | 1128 | 778.5 | 803.5 | 833.2 | 791.2 | 809.5
1303 | 1129 | 778.5 | 804.9 | 831.6 | 791 | 809.9
1304 | 1130 | 778.5 | 797.1 | 832.3 | 791.4 | 808.8
1305 | 1131 | 778.3 | 801.4 | 833.5 | 791.1 | 809.8
1306 | 1132 | 778.1 | 811.6 | 829.6 | 791.2 | 811.1
1307 | 1133 | 778.1 | 815.6 | 829 | 791.1 | 812.3
1308 | 1134 | 778 | 808.3 | 829.9 | 791.4 | 812
1309 | 1135 | 778 | 804.8 | 831.7 | 791 | 813.1
1310 | 1136 | 778.2 | 809.8 | 833.7 | 790.7 | 814.4
1311 | 1137 | 778.2 | 813.1 | 832.2 | 790.3 | 815
1312 | 1138 | 778.2 | 815.2 | 835.3 | 790.9 | 815.7
1313 | 1139 | 778 | 803.4 | 836.7 | 791.1 | 814.4
1314 | 1140 | 777.7 | 796.9 | 838.2 | 791.4 | 812.7
1315 | 1141 | 777.5 | 796 | 835.2 | 792.2 | 811.9
1316 | 1142 | 777.5 | 783.9 | 829.5 | 792 | 811.8
1317 | 1143 | 777.5 | 776 | 827.7 | 792.1 | 810.7
1318 | 1144 | 776.8 | 783.8 | 827.7 | 792.2 | 812
1319 | 1145 | 776.8 | 785.8 | 830.4 | 792.4 | 813
1320 | 1146 | 776.6 | 778.9 | 830.3 | 792.3 | 812.6
1321 | 1147 | 776.5 | 777.3 | 831.5 | 792.6 | 811
1322 | 1148 | 776.5 | 786 | 829.4 | 792.4 | 812
1323 | 1149 | 776.6 | 785.6 | 829.8 | 792.8 | 811.8
1324 | 1150 | 777.2 | 771.5 | 825.2 | 792.9 | 809.4
1325 | 1151 | 777 | 768.3 | 822.4 | 792.3 | 810.4
1326 | 1152 | 776.1 | 784.4 | 824.6 | 792.3 | 812.3
1327 | 1153 | 775.8 | 795.9 | 823.5 | 792.7 | 812.8
1328 | 1154 | 775.9 | 798 | 824.7 | 793.2 | 813.6
1329 | 1155 | 776.2 | 797.1 | 827.2 | 792.4 | 814
1330 | 1156 | 776.1 | 791.1 | 827.2 | 792.3 | 814.9
1331 | 1157 | 775.7 | 781.5 | 825.6 | 792.5 | 814.5
1332 | 1158 | 775.4 | 784.2 | 825.6 | 792.4 | 814.7
1333 | 1159 | 775.4 | 782.6 | 827.9 | 792.7 | 813
1334 | 1160 | 775.6 | 768.1 | 821.3 | 792.9 | 809.5
1335 | 1161 | 774.8 | 764.5 | 819.3 | 792.2 | 810.5
1336 | 1162 | 774.3 | 762.2 | 820.6 | 792.5 | 810.3
1337 | 1163 | 773.8 | 768.4 | 821.5 | 792.6 | 809.8
1338 | 1164 | 773.7 | 777.4 | 822.7 | 792.9 | 809.9
1339 | 1165 | 773.7 | 771.1 | 822.3 | 793.2 | 809.4
1340 | 1166 | 773.7 | 773.8 | 825.9 | 792.9 | 811.5
1341 | 1167 | 773.6 | 779.6 | 828.2 | 793.1 | 812.8
1342 | 1168 | 773.2 | 782.7 | 828.3 | 792.3 | 813.9
1343 | 1169 | 773.1 | 778.8 | 830.1 | 792.2 | 812.7
1344 | 1170 | 773 | 775.9 | 829.6 | 792.6 | 812.5
1345 | 1171 | 773.2 | 771 | 828.7 | 792.6 | 812.6
1346 | 1172 | 773.1 | 772.4 | 828.1 | 792.9 | 811.1
1347 | 1173 | 773.2 | 770.8 | 828.5 | 792.5 | 812.9
1348 | 1174 | 773.1 | 770.8 | 827 | 791.8 | 813.4
1349 | 1175 | 773.2 | 778.8 | 830.9 | 792.3 | 815
1350 | 1176 | 773.3 | 783.1 | 831.2 | 792.3 | 815.9
1351 | 1177 | 773.2 | 787.3 | 835.1 | 792 | 816.5
1352 | 1178 | 773.1 | 792.2 | 834.7 | 791.6 | 816.4
1353 | 1179 | 772.6 | 795.7 | 835.4 | 791.2 | 816.8
1354 | 1180 | 772.2 | 796 | 837.1 | 790.5 | 815.8
1355 | 1181 | 772 | 799.6 | 839.2 | 790 | 814.8
1356 | 1182 | 771.8 | 800.1 | 837.7 | 789.6 | 814.5
1357 | 1183 | 771.9 | 793.7 | 838.9 | 789.2 | 813.4
1358 | 1184 | 771.8 | 796.2 | 838.4 | 788.6 | 812.5
1359 | 1185 | 771.9 | 797.4 | 835.9 | 787.7 | 813.6
1360 | 1186 | 771.9 | 795 | 836.7 | 787.7 | 811.9
1361 | 1187 | 771.9 | 801.3 | 835 | 787.6 | 811.8
1362 | 1188 | 771.8 | 805 | 837.8 | 787.2 | 811.7
1363 | 1189 | 772 | 801 | 837.8 | 787.2 | 811
1364 | 1190 | 772 | 792.7 | 835.8 | 786.5 | 811.4
1365 | 1191 | 771.9 | 789.1 | 837.7 | 785.9 | 811.6
1366 | 1192 | 772.1 | 785.2 | 835.6 | 786.6 | 809.8
1367 | 1193 | 772 | 768.5 | 827.3 | 787.2 | 808.2
1368 | 1194 | 772 | 762.1 | 821.7 | 786.9 | 808.3
1369 | 1195 | 772.4 | 752.7 | 814.2 | 787.2 | 806
1370 | 1196 | 772.1 | 750.1 | 812.6 | 787.5 | 805
1371 | 1197 | 772.3 | 739.3 | 801.6 | 788.5 | 803.5
1372 | 1198 | 772 | 732.7 | 798.3 | 789.2 | 802.1
1373 | 1199 | 771.5 | 738.7 | 801.6 | 789.7 | 803.4
1374 | 1200 | 771.4 | 745.1 | 803 | 790.2 | 803.1
1375 | 1201 | 771.7 | 741.9 | 800.5 | 790.3 | 802.5
1376 | 1202 | 771.7 | 747.1 | 804.8 | 789.9 | 801.8
1377 | 1203 | 771.8 | 744.6 | 807.4 | 790.2 | 803.2
1378 | 1204 | 771.9 | 744.9 | 807.2 | 790.7 | 801.3
1379 | 1205 | 771.7 | 753.5 | 814.8 | 791.6 | 799.7
1380 | 1206 | 771.7 | 761.2 | 820.5 | 791.8 | 799.9
1381 | 1207 | 772.3 | 758.2 | 821.6 | 792 | 799.3
1382 | 1208 | 772.8 | 742.3 | 812 | 791.5 | 798
1383 | 1209 | 773.2 | 728.5 | 799.9 | 791.7 | 793.9
1384 | 1210 | 773.1 | 720.2 | 796.7 | 792.3 | 791.5
1385 | 1211 | 772.9 | 721.2 | 797.1 | 792.3 | 791.5
1386 | 1212 | 772.1 | 726.4 | 804.4 | 791.9 | 792.4
1387 | 1213 | 772.1 | 737.1 | 809.5 | 792.4 | 792.7
1388 | 1214 | 771.9 | 743.4 | 813.9 | 791.9 | 794.7
1389 | 1215 | 771.9 | 746.1 | 815.1 | 791.5 | 796
1390 | 1216 | 771.6 | 757.1 | 816.6 | 791 | 797.1
1391 | 1217 | 771.4 | 764.4 | 820.9 | 790.7 | 798.1
1392 | 1218 | 771.4 | 769.6 | 821 | 790.1 | 799
1393 | 1219 | 771.9 | 756.2 | 820.9 | 790 | 797.2
1394 | 1220 | 771.9 | 756 | 821.5 | 790 | 796.7
1395 | 1221 | 771.7 | 757.6 | 824.7 | 790.5 | 796
1396 | 1222 | 771.7 | 766.5 | 825.7 | 789.8 | 798.8
1397 | 1223 | 771.7 | 776.9 | 824.4 | 789.5 | 799.5
1398 | 1224 | 772.2 | 783.8 | 826 | 790 | 800.2
1399 | 1225 | 772.5 | 789 | 826.4 | 789.8 | 801.8
1400 | 1226 | 772.5 | 791.3 | 833.5 | 789.8 | 800.2
1401 | 1227 | 771.7 | 796.2 | 835.3 | 789.9 | 798.1
1402 | 1228 | 771.4 | 783.6 | 830.4 | 790.3 | 797.6
1403 | 1229 | 771.1 | 771.6 | 820.2 | 789.3 | 798.2
1404 | 1230 | 770.5 | 771 | 814.4 | 789.4 | 797.6
1405 | 1231 | 769.8 | 777.3 | 818.1 | 790 | 798.9
1406 | 1232 | 769.4 | 779.5 | 821.6 | 790.1 | 800.5
1407 | 1233 | 769.2 | 773.2 | 819.4 | 789.9 | 801.2
1408 | 1234 | 769.2 | 767.8 | 816.1 | 789.7 | 801.2
1409 | 1235 | 769 | 765.8 | 813.4 | 790.1 | 801.5
1410 | 1236 | 769.5 | 762.4 | 807 | 790.7 | 801.2
1411 | 1237 | 769.1 | 758.6 | 803 | 791.5 | 800.8
1412 | 1238 | 768.4 | 760 | 803.3 | 791.6 | 801.9
1413 | 1239 | 767.6 | 768.1 | 806.8 | 791.4 | 803.8
1414 | 1240 | 766.9 | 772.9 | 809.3 | 791.1 | 805.3
1415 | 1241 | 766.6 | 769.7 | 814.1 | 790.5 | 807.3
1416 | 1242 | 766.6 | 765.3 | 814 | 790 | 807.2
1417 | 1243 | 767.3 | 752.5 | 809.2 | 790.5 | 805.1
1418 | 1244 | 766.9 | 756.2 | 811.9 | 790.5 | 805.4
1419 | 1245 | 766.7 | 761.8 | 814.6 | 790.1 | 806.2
1420 | 1246 | 766.4 | 764.3 | 816.4 | 790.3 | 807.7
1421 | 1247 | 766.1 | 767.7 | 817 | 790.1 | 808.4
1422 | 1248 | 765.5 | 771.5 | 817.2 | 789.8 | 808.4
1423 | 1249 | 765.1 | 775.3 | 818.5 | 790.1 | 808.3
1424 | 1250 | 764.9 | 784.4 | 821.7 | 790 | 809.2
1425 | 1251 | 764.8 | 788.2 | 823 | 789.9 | 810.1
1426 | 1252 | 764.6 | 787.9 | 819.4 | 789.4 | 809.9
1427 | 1253 | 764.1 | 789.4 | 819.3 | 788.5 | 810.9
1428 | 1254 | 764 | 788 | 821.3 | 788 | 812.2
1429 | 1255 | 763.8 | 782.8 | 819 | 788.2 | 812.9
1430 | 1256 | 763.6 | 782.3 | 818.3 | 788.6 | 812.6
1431 | 1257 | 763.5 | 778.3 | 816.7 | 789 | 812.8
1432 | 1258 | 763.7 | 771.8 | 814.8 | 789.4 | 811.8
1433 | 1259 | 763.6 | 780.9 | 817.1 | 789.1 | 813.6
1434 | 1260 | 763.6 | 787.4 | 814.9 | 788.8 | 813.1
1435 | 1261 | 763.3 | 793.8 | 817.2 | 788.8 | 812.1
1436 | 1262 | 763.6 | 786.6 | 822.3 | 789.3 | 810.9
1437 | 1263 | 764 | 770.3 | 814.2 | 789.6 | 807.4
1438 | 1264 | 764.2 | 760.2 | 803.9 | 789.2 | 806.5
1439 | 1265 | 763.5 | 767.5 | 806.1 | 788.6 | 808.1
1440 | 1266 | 762.7 | 776.4 | 807.8 | 788.2 | 808.7
1441 | 1267 | 762.2 | 777.3 | 808.8 | 787.8 | 809.5
1442 | 1268 | 761.9 | 780.8 | 813 | 787.6 | 810.7
1443 | 1269 | 762.1 | 787.8 | 815.5 | 788 | 811.7
1444 | 1270 | 762.3 | 784 | 817.5 | 787.7 | 813.2
1445 | 1271 | 762.4 | 787.8 | 817.7 | 787.3 | 814.3
1446 | 1272 | 762.6 | 793 | 818.3 | 787.4 | 815.3
1447 | 1273 | 762.4 | 799.4 | 818.2 | 787.2 | 815.8
1448 | 1274 | 762.9 | 805.5 | 823.4 | 787.7 | 815.5
1449 | 1275 | 763.1 | 808.8 | 824.8 | 787.7 | 814.8
1450 | 1276 | 763.1 | 808.4 | 823.3 | 787.1 | 815.5
1451 | 1277 | 762.5 | 806.9 | 819.7 | 786.2 | 815.6
1452 | 1278 | 761.8 | 807.3 | 818.3 | 785.6 | 816.3
1453 | 1279 | 761.5 | 806 | 817.3 | 785.1 | 817
1454 | 1280 | 761.4 | 805.8 | 818 | 784.4 | 818.4
1455 | 1281 | 761.6 | 803.2 | 819.2 | 784.9 | 820.4
1456 | 1282 | 761.6 | 807.5 | 814.1 | 785.2 | 820.6
1457 | 1283 | 762 | 807.6 | 816.4 | 785.7 | 820.8
1458 | 1284 | 762.5 | 803.6 | 816.4 | 786.2 | 819.5
1459 | 1285 | 762.9 | 797.8 | 817.6 | 786.6 | 817.6
1460 | 1286 | 762.7 | 795.5 | 821.8 | 787.2 | 815.6
1461 | 1287 | 762.3 | 788.4 | 823.8 | 787.2 | 816.5
1462 | 1288 | 762.2 | 774.2 | 818.1 | 787 | 816.7
1463 | 1289 | 762.4 | 760.6 | 801.2 | 787.8 | 815.7
1464 | 1290 | 762.8 | 743.3 | 784.8 | 788.5 | 814.7
1465 | 1291 | 762.5 | 740.3 | 787.3 | 789.2 | 815.2
1466 | 1292 | 762.1 | 741.5 | 790.4 | 789.7 | 815
1467 | 1293 | 761.7 | 733.2 | 786.8 | 790 | 813.7
1468 | 1294 | 761.7 | 728.2 | 780.5 | 790.5 | 811.6
1469 | 1295 | 761.3 | 745.9 | 789.1 | 790.2 | 812.9
1470 | 1296 | 761.3 | 757.9 | 798 | 790.6 | 813.4
1471 | 1297 | 760.8 | 760 | 800.6 | 790.6 | 812.5
1472 | 1298 | 760.6 | 766 | 803.9 | 790.2 | 813
1473 | 1299 | 760 | 775.4 | 805.2 | 789.8 | 814.6
1474 | 1300 | 759.6 | 776.5 | 803.9 | 789.3 | 816
1475 | 1301 | 759.2 | 778.2 | 803.8 | 788.7 | 816.6
1476 | 1302 | 758.7 | 782.4 | 804.9 | 788.5 | 817.4
1477 | 1303 | 758.8 | 787.6 | 808.4 | 788.9 | 817
1478 | 1304 | 759.2 | 790.2 | 811.5 | 789.4 | 815.8
1479 | 1305 | 759.2 | 793.6 | 813.2 | 789.2 | 816.9
1480 | 1306 | 759.5 | 798.6 | 814.1 | 788.6 | 818.1
1481 | 1307 | 759.1 | 797.1 | 811.2 | 788.1 | 819.1
1482 | 1308 | 758.6 | 798.5 | 809 | 787.6 | 818.6
1483 | 1309 | 758.4 | 799.8 | 813.1 | 787.6 | 816.6
1484 | 1310 | 758 | 800.1 | 815.9 | 787.7 | 817.2
1485 | 1311 | 757.4 | 802 | 813.3 | 786.9 | 817.8
1486 | 1312 | 757.1 | 802.4 | 810.2 | 786.6 | 818.1
1487 | 1313 | 756.9 | 806.1 | 808.6 | 786.1 | 818.5
1488 | 1314 | 756.7 | 808.8 | 807 | 786.2 | 818.6
1489 | 1315 | 756.7 | 807.2 | 806.8 | 786.4 | 819.4
1490 | 1316 | 756.3 | 801 | 807.7 | 786 | 818.2
1491 | 1317 | 755.9 | 788.2 | 808.6 | 786.2 | 815.2
1492 | 1318 | 755.5 | 778.2 | 806.3 | 786.4 | 812.7
1493 | 1319 | 754.9 | 776.2 | 801.3 | 786.6 | 813.3
1494 | 1320 | 754.8 | 770.3 | 795.1 | 787.2 | 812.9
1495 | 1321 | 754.4 | 773.9 | 794.9 | 787.7 | 813.1
1496 | 1322 | 754.7 | 774.4 | 795.3 | 788.5 | 813.9
1497 | 1323 | 754.3 | 778.3 | 796.8 | 788.4 | 814.9
1498 | 1324 | 754.2 | 783 | 797.5 | 788.6 | 815
1499 | 1325 | 753.9 | 788.1 | 793.5 | 788.4 | 815.2
1500 | 1326 | 753.8 | 789 | 794.3 | 788.1 | 815.6
1501 | 1327 | 754.1 | 772.2 | 791.7 | 788.6 | 813.9
1502 | 1328 | 754.3 | 760.1 | 786.1 | 788.7 | 812.8
1503 | 1329 | 754.1 | 772.4 | 789.2 | 788.6 | 813.5
1504 | 1330 | 754.4 | 776.3 | 791.8 | 789.2 | 813.4
1505 | 1331 | 754.7 | 774.9 | 793.7 | 789.3 | 813.3
1506 | 1332 | 754.7 | 782.9 | 794.6 | 789.2 | 814.1
1507 | 1333 | 754.7 | 780.4 | 792.9 | 789.3 | 814.8
1508 | 1334 | 754.6 | 782.6 | 792 | 789.4 | 816.2
1509 | 1335 | 754.1 | 792.4 | 789 | 789.5 | 816.5
1510 | 1336 | 754.1 | 791.8 | 789.2 | 789.8 | 816.6
1511 | 1337 | 754.4 | 778.9 | 790.1 | 790.3 | 815.2
1512 | 1338 | 754.3 | 769.2 | 787.3 | 790.8 | 814.6
1513 | 1339 | 754.2 | 761.3 | 783.7 | 791.3 | 813.4
1514 | 1340 | 753.9 | 759.3 | 782.9 | 791.5 | 813.6
1515 | 1341 | 753.6 | 766.5 | 785 | 791.4 | 814.3
1516 | 1342 | 753.7 | 760.4 | 782.7 | 792.1 | 813.6
1517 | 1343 | 753.7 | 754.7 | 780.8 | 792.2 | 813.4
1518 | 1344 | 754 | 757 | 781.5 | 792.8 | 813.8
1519 | 1345 | 753.9 | 752.8 | 778.1 | 793.2 | 813.5
1520 | 1346 | 753.8 | 743.3 | 772.2 | 793.2 | 813.2
1521 | 1347 | 753.3 | 749.7 | 773.8 | 793.2 | 814.7
1522 | 1348 | 752.9 | 758.7 | 775.4 | 793.1 | 815.5
1523 | 1349 | 752.7 | 767 | 779.8 | 792.5 | 817.2
1524 | 1350 | 752.3 | 765.7 | 782.9 | 792.1 | 818.6
1525 | 1351 | 752.1 | 763.3 | 784.3 | 792.2 | 818.3
1526 | 1352 | 752.3 | 771.8 | 786.4 | 792.1 | 819.4
1527 | 1353 | 752.5 | 771.1 | 787.3 | 792.3 | 819.4
1528 | 1354 | 752.2 | 773.9 | 786.1 | 792.5 | 819.2
1529 | 1355 | 751.8 | 772.1 | 786.2 | 792.6 | 819.5
1530 | 1356 | 751.5 | 769.9 | 785.2 | 792.3 | 819.9
1531 | 1357 | 751.4 | 759.1 | 782.5 | 792.7 | 818.3
1532 | 1358 | 750.7 | 745.6 | 776.8 | 793.2 | 817.6
1533 | 1359 | 749.6 | 744.4 | 775.6 | 793.3 | 816.6
1534 | 1360 | 749 | 744.3 | 774.5 | 793.4 | 816.1
1535 | 1361 | 749.1 | 737.3 | 765.5 | 793.8 | 815.4
1536 | 1362 | 749.1 | 725.7 | 752.8 | 794.2 | 812.8
1537 | 1363 | 748.3 | 723.1 | 756.3 | 794.4 | 812.3
1538 | 1364 | 747.1 | 734.5 | 763.2 | 793.8 | 813.2
1539 | 1365 | 745.9 | 747.1 | 767.3 | 793 | 813
1540 | 1366 | 745 | 758.9 | 770.5 | 792.1 | 814
1541 | 1367 | 744.7 | 766.4 | 773.6 | 791.6 | 813.7
1542 | 1368 | 744.2 | 768.6 | 774.3 | 791.2 | 811.8
1543 | 1369 | 744 | 769.9 | 777.5 | 790.9 | 811
1544 | 1370 | 744 | 776.1 | 783 | 790.4 | 811.1
1545 | 1371 | 743.6 | 775.2 | 785.7 | 789.9 | 811.5
1546 | 1372 | 743.2 | 779.5 | 788.3 | 789.5 | 812.1
1547 | 1373 | 742.8 | 779.5 | 788 | 789 | 812.2
1548 | 1374 | 742.5 | 766 | 785 | 788.9 | 810.2
1549 | 1375 | 742.4 | 764.7 | 784.1 | 788.8 | 810.8
1550 | 1376 | 742.5 | 771.2 | 787.9 | 789.1 | 809
1551 | 1377 | 743.3 | 769.7 | 787.9 | 789.2 | 810.1
1552 | 1378 | 743.9 | 747.2 | 777.8 | 789.6 | 808
1553 | 1379 | 743.5 | 734.7 | 771 | 790.4 | 806.3
1554 | 1380 | 743.2 | 729.6 | 767.7 | 790.9 | 805.1
1555 | 1381 | 742.9 | 725.5 | 765.2 | 791.3 | 803.3
1556 | 1382 | 742.4 | 743 | 772.9 | 790.6 | 805.6
1557 | 1383 | 741.9 | 752 | 776.3 | 789.9 | 806.4
1558 | 1384 | 741.3 | 748.4 | 779.5 | 789.3 | 806.8
1559 | 1385 | 740.8 | 747.3 | 780.1 | 788.5 | 806.8
1560 | 1386 | 741.1 | 749.9 | 784.8 | 788.4 | 806.1
1561 | 1387 | 741 | 749.1 | 785.4 | 788.3 | 805.7
1562 | 1388 | 740.6 | 759.5 | 787.6 | 787.9 | 806.9
1563 | 1389 | 740.4 | 767.7 | 785.7 | 787.4 | 807.3
1564 | 1390 | 740.1 | 769.8 | 788.7 | 786.8 | 807
1565 | 1391 | 739.7 | 769.6 | 790.7 | 786.2 | 808.3
1566 | 1392 | 739.7 | 758.5 | 787.5 | 786.2 | 807.9
1567 | 1393 | 739.4 | 753.2 | 783.6 | 786.5 | 807
1568 | 1394 | 738.9 | 757.3 | 784.6 | 786.5 | 808.2
1569 | 1395 | 738.4 | 759.8 | 786.1 | 786.4 | 807.6
1570 | 1396 | 738.7 | 751.9 | 783.8 | 786.7 | 807.6
1571 | 1397 | 738.5 | 746.9 | 782.8 | 787.3 | 807.9
1572 | 1398 | 738.1 | 746.6 | 784.1 | 787.3 | 808.2
1573 | 1399 | 737.5 | 757.2 | 785.2 | 786.9 | 809
1574 | 1400 | 736.9 | 758 | 785.4 | 786.5 | 810.3
1575 | 1401 | 736.7 | 752.2 | 781.1 | 786.4 | 810.2
1576 | 1402 | 736.1 | 755.1 | 780.2 | 786.4 | 811.5
1577 | 1403 | 735.1 | 752.2 | 777.4 | 785.9 | 811.6
1578 | 1404 | 734 | 757 | 780.3 | 785.2 | 812.7
1579 | 1405 | 733.3 | 758.3 | 781.5 | 784.7 | 812.2
1580 | 1406 | 733.4 | 757.1 | 782.3 | 784.2 | 811.7
1581 | 1407 | 733.3 | 761 | 783.5 | 783.9 | 812.3
1582 | 1408 | 733.5 | 760.4 | 786 | 784 | 812.6
1583 | 1409 | 733.9 | 755.9 | 785.9 | 784 | 812.4
1584 | 1410 | 733.8 | 754.4 | 787.7 | 784.1 | 813.1
1585 | 1411 | 733.4 | 749.1 | 785.7 | 784.2 | 812.3
1586 | 1412 | 732.8 | 737.5 | 779.1 | 784.4 | 810.6
1587 | 1413 | 732.3 | 739.4 | 780 | 784.4 | 809.9
1588 | 1414 | 732.5 | 727.2 | 774.7 | 785 | 808.6
1589 | 1415 | 732.1 | 725.1 | 773.6 | 785.3 | 807.2
1590 | 1416 | 731.3 | 731.6 | 777.3 | 785.1 | 808.1
1591 | 1417 | 731 | 730 | 777.5 | 785.1 | 807.5
1592 | 1418 | 730.7 | 721.8 | 772.7 | 785.2 | 805.2
1593 | 1419 | 730.5 | 718.8 | 771.9 | 785 | 804.5
1594 | 1420 | 730.3 | 716.6 | 773.9 | 785.3 | 805.9
1595 | 1421 | 730.4 | 717.7 | 774.6 | 785.2 | 806.4
1596 | 1422 | 729.8 | 711.3 | 771.1 | 785.3 | 804.9
1597 | 1423 | 729 | 721.7 | 774.3 | 784.6 | 804.8
1598 | 1424 | 728.7 | 722.9 | 776.3 | 784 | 805.4
1599 | 1425 | 728.5 | 722.5 | 777.3 | 784 | 805.6
1600 | 1426 | 728 | 723.8 | 776.1 | 783.5 | 804.7
1601 | 1427 | 728.2 | 720.8 | 773.7 | 783.2 | 804.2
1602 | 1428 | 728.6 | 717.1 | 769.3 | 783.9 | 802.5
1603 | 1429 | 728.5 | 716.6 | 768.6 | 784.6 | 802.9
1604 | 1430 | 727.9 | 726.4 | 772.9 | 784.4 | 804.1
1605 | 1431 | 727.6 | 738.9 | 779.3 | 784 | 805.4
1606 | 1432 | 727 | 744.3 | 781.7 | 783.4 | 805.9
1607 | 1433 | 726.7 | 746.7 | 782.6 | 782.7 | 807.8
1608 | 1434 | 727 | 746.9 | 784.4 | 782.4 | 808.6
1609 | 1435 | 726.9 | 753.7 | 784.9 | 782.3 | 810.1
1610 | 1436 | 726.8 | 752.5 | 787.9 | 782 | 811.8
1611 | 1437 | 726.4 | 756.3 | 788.9 | 781.7 | 812.3
1612 | 1438 | 726 | 762 | 788.9 | 781.2 | 811.2
1613 | 1439 | 725.5 | 757.8 | 789.7 | 781.5 | 811.4
1614 | 1440 | 725.2 | 751.1 | 786.9 | 781.6 | 810.6
1615 | 1441 | 725.3 | 737.5 | 779.3 | 782.2 | 810
1616 | 1442 | 725.3 | 719.7 | 764.9 | 782.9 | 807.4
1617 | 1443 | 725.2 | 696.2 | 733.5 | 783.8 | 797.7
1618 | 1444 | 724.6 | 672.7 | 707.7 | 784.2 | 788.6
1619 | 1445 | 723.6 | 651.8 | 684.2 | 784.1 | 779.8
1620 | 1446 | 722.3 | 633.4 | 663 | 783.7 | 772
1621 | 1447 | 721 | 616.9 | 644.9 | 782.9 | 765
1622 | 1448 | 719.7 | 602 | 627.3 | 781.3 | 759
1623 | 1449 | 718.5 | 588.8 | 612.3 | 779.7 | 753.4
1624 | 1450 | 717.5 | 576.5 | 598.5 | 778.2 | 747.8
1625 | 1451 | 716.2 | 564.3 | 587 | 776.7 | 742.5
1626 | 1452 | 714.9 | 553.5 | 575.7 | 775 | 737.3
1627 | 1453 | 713.7 | 542.4 | 565.8 | 773.6 | 731.6
1628 | 1454 | 712.7 | 532.8 | 557 | 771.8 | 726
1629 | 1455 | 711.2 | 525 | 547.1 | 769.7 | 720.8
1630 | 1456 | 710 | 517 | 538.8 | 767.7 | 715.4
1631 | 1457 | 708.6 | 509.6 | 530.7 | 766 | 710.2
1632 | 1458 | 707.1 | 502.4 | 522.5 | 764.1 | 705.1
1633 | 1459 | 705.9 | 496.2 | 515.7 | 762.5 | 699.8
1634 | 1460 | 705 | 489.9 | 508.8 | 760.9 | 694.7
1635 | 1461 | 703.9 | 484.4 | 501.8 | 759 | 689.7
1636 | 1462 | 702.7 | 478.8 | 495.7 | 757.1 | 685
1637 | 1463 | 701.5 | 473.7 | 489.3 | 755.3 | 680.8
1638 | 1464 | 700.1 | 469.2 | 483.3 | 753.1 | 675.9
1639 | 1465 | 698.7 | 465.2 | 477.9 | 750.7 | 671.4
1640 | 1466 | 696.8 | 463.9 | 471.4 | 748.1 | 668
1641 | 1467 | 694.9 | 463.8 | 467.2 | 744.4 | 664.8
1642 | 1468 | 693.2 | 464 | 463.1 | 740.3 | 661
1643 | 1469 | 691.6 | 463.7 | 458.4 | 736.8 | 657.4
1644 | 1470 | 690 | 463 | 454.2 | 733.3 | 653.9
1645 | 1471 | 688.3 | 462.2 | 450.1 | 729.8 | 650.9
1646 | 1472 | 686.6 | 461.4 | 446.6 | 726.2 | 647.2
1647 | 1473 | 684.9 | 459.8 | 441.9 | 723.3 | 644
1648 | 1474 | 683.3 | 457.5 | 436.5 | 720.7 | 640
1649 | 1475 | 682.3 | 453.4 | 430.9 | 718.7 | 636.5
1650 | 1476 | 681 | 451.5 | 426.2 | 716.6 | 633.2
1651 | 1477 | 679.2 | 450.8 | 421.7 | 713.6 | 629.4
1652 | 1478 | 677.9 | 449.4 | 416.7 | 711.5 | 626.1
1653 | 1479 | 676.5 | 446.9 | 411.7 | 709.6 | 623.2
1654 | 1480 | 675.6 | 443.4 | 407.3 | 707.9 | 619.5
1655 | 1481 | 674.6 | 440.4 | 403.3 | 706.1 | 616.2
1656 | 1482 | 673.8 | 435 | 398.9 | 704.8 | 612.3
1657 | 1483 | 673 | 430.4 | 394.8 | 703.7 | 609
1658 | 1484 | 671.8 | 427.4 | 390.5 | 702.1 | 606.5
1659 | 1485 | 670.7 | 424.1 | 387.1 | 700.4 | 603.5
1660 | 1486 | 669.4 | 422.9 | 385.7 | 698.4 | 600
1661 | 1487 | 668 | 421.7 | 384.9 | 696.3 | 597.1
1662 | 1488 | 666.9 | 417.9 | 383.9 | 694.7 | 594.4
1663 | 1489 | 665.9 | 416.1 | 382.6 | 692.8 | 591.1
1664 | 1490 | 665.1 | 413.1 | 380.3 | 691.2 | 587.7
1665 | 1491 | 663.3 | 407.4 | 376.4 | 689.3 | 582.2
1666 | 1492 | 661.6 | 402.7 | 372.9 | 687.5 | 577.9
1667 | 1493 | 655.6 | 395.6 | 368.5 | 684.3 | 573.3
1668 | 1494 | 648.1 | 360 | 363 | 678.6 | 566.7
1669 | 1495 | 600.2 | 332.3 | 351.4 | 640.2 | 553.4
1670 | 1496 | 474.2 | 322.1 | 302.3 | 575.8 | 546.4
1671 | 1497 | 421.8 | 283.5 | 255.7 | 532.5 | 539.2
1672 | 1498 | 314.6 | 216.7 | 232.6 | 496 | 534.7
1673 | 1499 | 220.1 | 167.2 | 221.2 | 394.7 | 529.5
1674 | 1500 | 207.4 | 143.3 | 214.6 | 299.7 | 519.5
1675 | 1501 | 204 | 110.4 | 195.2 | 285.8 | 510.5
1676 | 1502 | 200.5 | 106.9 | 141.1 | 270.4 | 503.5
1677 | 1503 | 197.6 | 108.8 | 98.5 | 251.6 | 497.5
1678 | 1504 | 194.7 | 109.3 | 85.7 | 235.5 | 492.1
1679 | 1505 | 190.8 | 108.6 | 87.3 | 220.2 | 482.5
1680 | 1506 | 186.4 | 105.3 | 85.2 | 211.4 | 477.6
1681 | 1507 | 182.5 | 102.7 | 83.7 | 204.4 | 471.9
1682 | 1508 | 176.5 | 104.6 | 81.2 | 196.9 | 472
1683 | 1509 | 174.4 | 101.3 | 82.6 | 189.9 | 464.3
1684 | 1510 | 168.1 | 101.1 | 82 | 177.1 | 456.5
1685 | 1511 | 165.4 | 95.8 | 84.6 | 157.1 | 448
1686 | 1512 | 164.9 | 100.1 | 86.5 | 151.2 | 435.9
1687 | 1513 | 162.7 | 103.6 | 85.7 | 148 | 411.7
1688 | 1514 | 163.1 | 99.3 | 85.5 | 146.5 | 420.2
1689 | 1515 | 161.7 | 96.7 | 87.5 | 141.8 | 406.9
1690 | 1516 | 160.1 | 100.2 | 87.4 | 133.9 | 376.6
1691 | 1517 | 154.5 | 104 | 84.3 | 124.4 | 318.7
1692 | 1518 | 148.5 | 95.4 | 70.1 | 119.4 | 198.4
1693 | 1519 | 151.1 | 92.4 | 67.1 | 115.3 | 99
1694 | 1520 | 144 | 89.1 | 70.8 | 110.3 | 91.7
1695 | 1521 | 138.6 | 88.2 | 71.9 | 105.6 | 88.4
1696 | 1522 | 136.5 | 86.9 | 73.4 | 103.4 | 86.4
1697 | 1523 | 139.1 | 88.4 | 77.8 | 102.4 | 84.6
1698 | 1524 | 137.5 | 90.1 | 79.5 | 99.4 | 83.8
1699 | 1525 | 134.4 | 93.7 | 77.5 | 96.9 | 82.6
1700 | 1526 | 138 | 95.6 | 70.6 | 95.7 | 82
1701 | 1527 | 134.6 | 97.5 | 60.5 | 95.5 | 81.3
1702 | 1528 | 120.5 | 92.2 | 61.5 | 94.5 | 79.7
1703 | 1529 | 106.6 | 92.8 | 60.9 | 92.9 | 76.9
1704 | 1530 | 106.5 | 90.9 | 61.3 | 92.8 | 74.4
1705 | 1531 | 110.7 | 88.2 | 62.2 | 91.4 | 72.6
1706 | 1532 | 106.2 | 85.2 | 60.1 | 89.5 | 71.1
1707 | 1533 | 105.3 | 83 | 58.1 | 88.7 | 69.4
1708 | 1534 | 106.4 | 84.7 | 58.8 | 87.7 | 67.6
1709 | 1535 | 105.3 | 84.4 | 59.9 | 87.5 | 64.3
1710 | 1536 | 97.9 | 83.5 | 57.9 | 86.7 | 62.8
1711 | 1537 | 93.2 | 81.5 | 60.1 | 87.1 | 61.3
1712 | 1538 | 89.2 | 85 | 61.9 | 86.8 | 58.8
1713 | 1539 | 89 | 85.6 | 51.5 | 85.8 | 55.6
1714 | 1540 | 89 | 88.4 | 50.3 | 84.7 | 51
1715 | 1541 | 90.4 | 89.2 | 52.5 | 83.9 | 48.9
1716 | 1542 | 92.3 | 88.9 | 54.9 | 82.7 | 48.9
1717 | 1543 | 90.8 | 86.6 | 56.3 | 82.4 | 48.5
1718 | 1544 | 87.3 | 84.6 | 56.6 | 82.5 | 47.7
1719 | 1545 | 90.4 | 83.8 | 58.2 | 83 | 46.9
1720 | 1546 | 90 | 83.1 | 60.3 | 80.6 | 46.2
1721 | 1547 | 91.2 | 83.2 | 60.6 | 80.5 | 45.4
1722 | 1548 | 87.5 | 85.9 | 57.4 | 78.3 | 45.3
1723 | 1549 | 84.3 | 81.8 | 57.9 | 79.3 | 45
1724 | 1550 | 82.6 | 81.4 | 57.5 | 78 | 45.1
1725 | 1551 | 81.8 | 81.5 | 58.3 | 77.7 | 45.4
1726 | 1552 | 76.6 | 81.6 | 58.7 | 76.2 | 45.1
1727 | 1553 | 76.5 | 82.2 | 51.8 | 75.1 | 44.1
1728 | 1554 | 75.1 | 80.9 | 52.2 | 74.8 | 44.5
1729 | 1555 | 76.8 | 80.3 | 47.2 | 75.7 | 44.6
1730 | 1556 | 79.9 | 81.5 | 50.3 | 76.5 | 45
1731 | 1557 | 78.9 | 77.3 | 53.3 | 75.4 | 45.4
1732 | 1558 | 78.7 | 78.3 | 54 | 74.7 | 45.3
1733 | 1559 | 77.5 | 79 | 51.6 | 75 | 44.2
1734 | 1560 | 80 | 78.8 | 47.3 | 74.7 | 43.6
1735 | 1561 | 80.9 | 78 | 50.8 | 74 | 43
1736 | 1562 | 82.1 | 75.4 | 53.1 | 72.5 | 42.2
1737 | 1563 | 80.8 | 76.1 | 55.3 | 72.4 | 41.8
1738 | 1564 | 75.2 | 74.5 | 57.2 | 73.1 | 41.3
1739 | 1565 | 73.6 | 76.1 | 58.5 | 73.4 | 40.5
1740 | 1566 | 76.6 | 77.3 | 55.4 | 72.5 | 39.2
1741 | 1567 | 79.5 | 77.2 | 56.8 | 70.2 | 38.8
1742 | 1568 | 80.3 | 75.8 | 55.1 | 69.7 | 39.2
1743 | 1569 | 77.5 | 75.3 | 50.7 | 69.5 | 39.5
1744 | 1570 | 76.7 | 73.8 | 50.1 | 69.1 | 39.5
1745 | 1571 | 74.4 | 75 | 43.7 | 67.9 | 39.1
1746 | 1572 | 72.3 | 76.8 | 45.6 | 67.4 | 39.4
1747 | 1573 | 72 | 79.9 | 46.7 | 67.2 | 39.7
1748 | 1574 | 72.4 | 78.4 | 39 | 66.9 | 39.7
1749 | 1575 | 71.3 | 75.2 | 42.7 | 66 | 39.4
1750 | 1576 | 72.6 | 74.8 | 45.1 | 65.8 | 39.5
1751 | 1577 | 72.4 | 74.2 | 49 | 65.8 | 39.2
1752 | 1578 | 73 | 78 | 44.1 | 66.3 | 39.1
1753 | 1579 | 74.3 | 78.1 | 45.2 | 65.4 | 39.1
1754 | 1580 | 74.2 | 74.9 | 46.5 | 66.2 | 38.8
1755 | 1581 | 73.7 | 75.3 | 44.6 | 66.5 | 39.1
1756 | 1582 | 71.3 | 77.1 | 46.9 | 64.3 | 39.4
1757 | 1583 | 70.5 | 75 | 47.1 | 63.3 | 39.8
1758 | 1584 | 72.4 | 77.1 | 48.5 | 64 | 39.6
1759 | 1585 | 73.7 | 75.1 | 51.8 | 64.5 | 39.1
1760 | 1586 | 71.7 | 76.8 | 53.4 | 61.9 | 38.4
1761 | 1587 | 69.7 | 75.3 | 50.3 | 61.1 | 38.4
1762 | 1588 | 67.9 | 74.3 | 41.2 | 60.5 | 38.5
1763 | 1589 | 70.2 | 75.5 | 41.1 | 59 | 38
1764 | 1590 | 69.3 | 75.1 | 43.3 | 58.6 | 37.7
1765 | 1591 | 74 | 73 | 45.1 | 59 | 37.7
1766 | 1592 | 75.5 | 69.9 | 47.5 | 59 | 38
1767 | 1593 | 76.8 | 69 | 49.3 | 59.1 | 38.2
1768 | 1594 | 79.9 | 69.3 | 50.8 | 60.1 | 39
1769 | 1595 | 81.8 | 70.1 | 52.5 | 61 | 39.9
1770 | 1596 | 83.7 | 70.5 | 54 | 62.3 | 40.7
1771 | 1597 | 85.5 | 70.3 | 55.1 | 63.1 | 41.4
1772 | 1598 | 86.5 | 69.9 | 56.1 | 63.9 | 42
1773 | 1599 | 87.5 | 70 | 56.9 | 64.9 | 42.5
1774 | 1600 | 88.4 | 70.6 | 57.5 | 66.1 | 43.1
1775 | 1601 | 89.4 | 71.3 | 57.8 | 66.9 | 43.7
1776 | 1602 | 90 | 71.1 | 58.4 | 67.9 | 44.3
1777 | 1603 | 90.4 | 70.1 | 58.4 | 68.8 | 44.9
1778 | 1604 | 90.9 | 70 | 58.6 | 69.5 | 45.3
1779 | 1605 | 90.9 | 69.3 | 58.5 | 70.2 | 45.8
1780 | 1606 | 90.8 | 69.1 | 58.3 | 70.6 | 46.3
1781 | 1607 | 90.9 | 69.6 | 57.9 | 70.9 | 46.7
1782 | 1608 | 90.7 | 71.2 | 58.1 | 71.2 | 47.1
1783 | 1609 | 91.2 | 71.1 | 58.3 | 71.5 | 47.5
1784 | 1610 | 91.7 | 70.9 | 58.3 | 72 | 47.9
1785 | 1611 | 91.6 | 69.6 | 58.5 | 72.2 | 48.3
1786 | 1612 | 90.8 | 69.1 | 58.5 | 72.1 | 48.7
1787 | 1613 | 91.2 | 68.7 | 58.8 | 72.2 | 49.3
1788 | 1614 | 91.3 | 68.4 | 58.7 | 72.2 | 49.7
1789 | 1615 | 90.4 | 68.3 | 58.5 | 72.1 | 50.1
1790 | 1616 | 90.2 | 68.4 | 58.5 | 72.4 | 50.3
1791 | 1617 | 90.2 | 68.5 | 58.5 | 72.5 | 50.6
1792 | 1618 | 90.1 | 69.1 | 58.6 | 72.6 | 51.1
1793 | 1619 | 90.2 | 67.9 | 58.5 | 72.6 | 51.4
1794 | 1620 | 90.1 | 67.1 | 58.5 | 72.6 | 51.8
1795 | 1621 | 89.6 | 66.6 | 58.6 | 72.7 | 52.1
1796 | 1622 | 88.9 | 66.2 | 59.2 | 72.9 | 52.4
1797 | 1623 | 88.6 | 66.1 | 59.2 | 73 | 52.7
1798 | 1624 | 88.1 | 67.5 | 59.4 | 73 | 53
1799 | 1625 | 88 | 68.3 | 59.8 | 73 | 53.4
1800 | 1626 | 87.8 | 68.9 | 60 | 72.7 | 53.8
1801 | 1627 | 87.5 | 67.6 | 59.8 | 72.6 | 54.1
1802 | 1628 | 87.4 | 66.7 | 59.7 | 72.5 | 54.4
1803 | 1629 | 87.1 | 66.4 | 59.5 | 72.4 | 54.7
1804 | 1630 | 86.8 | 66.1 | 58.3 | 72.4 | 55
1805 | 1631 | 86.4 | 65.2 | 57.1 | 72.4 | 55.3
1806 | 1632 | 86.2 | 64.7 | 56.6 | 72.6 | 55.7
1807 | 1633 | 86.4 | 65.3 | 56.2 | 72.7 | 55.9
1808 | 1634 | 86.5 | 65.6 | 55.2 | 72.7 | 56.1
1809 | 1635 | 86.3 | 66.9 | 54.3 | 72.6 | 56.3
1810 | 1636 | 86.3 | 67 | 53.9 | 72.9 | 56.5
1811 | 1637 | 86.1 | 66.3 | 53.6 | 72.8 | 56.7
1812 | 1638 | 85.8 | 66.5 | 53.9 | 72.6 | 56.9
1813 | 1639 | 85.8 | 67 | 53.6 | 72.5 | 57.1
1814 | 1640 | 85.8 | 66.3 | 53.3 | 72.5 | 57.3
1815 | 1641 | 86 | 66 | 52.7 | 72.5 | 57.5
1816 | 1642 | 85.3 | 65.9 | 52.4 | 72.1 | 57.6
1817 | 1643 | 84.8 | 65.7 | 52.8 | 72 | 57.9
1818 | 1644 | 84.7 | 65.7 | 52.8 | 71.9 | 58.1
1819 | 1645 | 84.6 | 66.2 | 53.2 | 72 | 58.3
1820 | 1646 | 84.5 | 65.7 | 53.6 | 72 | 58.6
1821 | 1647 | 84.1 | 64.8 | 54 | 72 | 58.9
1822 | 1648 | 83.6 | 64.4 | 53.9 | 71.9 | 59
1823 | 1649 | 83.6 | 64.9 | 53.6 | 71.8 | 59.2
1824 | 1650 | 83.9 | 65 | 53.2 | 72.1 | 59.3
1825 | 1651 | 84 | 64.7 | 52.9 | 72.3 | 59.5
1826 | 1652 | 83.9 | 64.1 | 52.5 | 72.4 | 59.7
1827 | 1653 | 83.8 | 63.6 | 52.4 | 72.4 | 59.9
1828 | 1654 | 84 | 64.6 | 52 | 72.4 | 60
1829 | 1655 | 84 | 65.9 | 51.8 | 72.5 | 60.1
1830 | 1656 | 83.8 | 65.9 | 52 | 72.5 | 60.2
1831 | 1657 | 83.5 | 65.5 | 51.6 | 72.3 | 60.4
1832 | 1658 | 83.4 | 65.9 | 51.7 | 72.1 | 60.6
1833 | 1659 | 83.6 | 66.4 | 52.3 | 72.2 | 60.8
1834 | 1660 | 84 | 66.4 | 53 | 72.3 | 61
1835 | 1661 | 84.2 | 66.7 | 54.1 | 72.4 | 61.1
1836 | 1662 | 84.1 | 66 | 53.5 | 72.6 | 61.3
1837 | 1663 | 83.9 | 66.2 | 52.5 | 72.5 | 61.5
1838 | 1664 | 83.8 | 66.1 | 52.1 | 72.5 | 61.6
1839 | 1665 | 83.7 | 66 | 51.5 | 72.6 | 61.6
1840 | 1666 | 83.7 | 65 | 50.2 | 72.6 | 61.7
1841 | 1667 | 83.6 | 63.7 | 49.5 | 72.6 | 61.6
1842 | 1668 | 83.4 | 64.4 | 48.8 | 72.6 | 61.6
1843 | 1669 | 83.3 | 64.6 | 47.8 | 72.6 | 61.7
1844 | 1670 | 83.3 | 64.7 | 48.2 | 72.6 | 61.8
1845 | 1671 | 82.6 | 64.6 | 47.9 | 72.5 | 61.9
1846 | 1672 | 82.3 | 64 | 48.6 | 72.3 | 62.1
1847 | 1673 | 82.2 | 63.8 | 50.3 | 72.3 | 62.2
1848 | 1674 | 82.2 | 64.1 | 49.8 | 72.3 | 62.4
1849 | 1675 | 82 | 64.2 | 49.4 | 72.3 | 62.5
1850 | 1676 | 81.4 | 64 | 49.1 | 72 | 62.6
1851 | 1677 | 81.3 | 63.9 | 49.7 | 71.9 | 62.7
1852 | 1678 | 81.1 | 64 | 51.7 | 71.8 | 62.9
1853 | 1679 | 80.7 | 64.5 | 53.3 | 71.8 | 63
1854 | 1680 | 80.5 | 64.3 | 54 | 71.8 | 63
1855 | 1681 | 80.3 | 63.4 | 54.5 | 71.7 | 63.1
1856 | 1682 | 80 | 63.6 | 54.9 | 71.7 | 63.3
1857 | 1683 | 80 | 63.6 | 55.1 | 71.6 | 63.4
1858 | 1684 | 79.9 | 64.3 | 54.9 | 71.5 | 63.4
1859 | 1685 | 79.9 | 64 | 54.4 | 71.4 | 63.6
1860 | 1686 | 79.8 | 63.9 | 54.6 | 71.4 | 63.7
1861 | 1687 | 79.8 | 64.5 | 55 | 71.5 | 63.9
1862 | 1688 | 79.6 | 64.3 | 54.9 | 71.5 | 63.9
1863 | 1689 | 79.7 | 64 | 55.7 | 71.6 | 64
1864 | 1690 | 79.9 | 64 | 55.8 | 71.6 | 64
1865 | 1691 | 80 | 63.7 | 55.9 | 71.7 | 64
1866 | 1692 | 79.9 | 63.3 | 55.5 | 71.7 | 64
1867 | 1693 | 79.7 | 63.5 | 54.9 | 71.6 | 64
1868 | 1694 | 79.8 | 64.3 | 55.6 | 71.6 | 64
1869 | 1695 | 80.1 | 64.4 | 56.3 | 71.7 | 64
1870 | 1696 | 80.1 | 63.8 | 55.8 | 71.8 | 64
1871 | 1697 | 79.7 | 63.8 | 56 | 71.8 | 64
1872 | 1698 | 79.3 | 63.1 | 55.7 | 71.6 | 64.2
1873 | 1699 | 79.2 | 63 | 55.1 | 71.4 | 64.4
1874 | 1700 | 79.2 | 62.3 | 54.5 | 71.4 | 64.6
1875 | 1701 | 79 | 62 | 55.3 | 71.2 | 64.7
1876 | 1702 | 79 | 62.2 | 55.7 | 71.2 | 64.8
1877 | 1703 | 78.8 | 62.7 | 54.8 | 71.1 | 64.8
1878 | 1704 | 78.9 | 63.6 | 54.5 | 71.1 | 64.8
1879 | 1705 | 79 | 63.7 | 54.3 | 71.2 | 64.9
1880 | 1706 | 79.1 | 63.5 | 53.8 | 71.2 | 64.9
1881 | 1707 | 79.2 | 64.1 | 54.1 | 71.3 | 64.8
1882 | 1708 | 79.1 | 63.3 | 54.7 | 71.3 | 64.9
1883 | 1709 | 79 | 63.1 | 55.2 | 71.2 | 64.9
1884 | 1710 | 78.4 | 63 | 55.2 | 71 | 65
1885 | 1711 | 78 | 63.3 | 55.8 | 70.8 | 65
1886 | 1712 | 78.1 | 62.6 | 56.7 | 70.8 | 65.1
1887 | 1713 | 78 | 62.2 | 57.1 | 70.9 | 65.3
1888 | 1714 | 78 | 62.2 | 56.6 | 71 | 65.4
1889 | 1715 | 77.9 | 62.6 | 55.8 | 71 | 65.1
1890 | 1716 | 78.1 | 63 | 54.3 | 71.1 | 65.1
1891 | 1717 | 78.3 | 62.8 | 52.9 | 71.1 | 64.9
1892 | 1718 | 78.3 | 63.1 | 51.9 | 71.1 | 64.9
1893 | 1719 | 78.5 | 63.4 | 51.2 | 71.1 | 65
1894 | 1720 | 78.6 | 63.2 | 51.8 | 71.2 | 65.1
1895 | 1721 | 78.5 | 62.9 | 51.8 | 71.2 | 65
1896 | 1722 | 78.2 | 62.6 | 52.7 | 71.1 | 65
1897 | 1723 | 78 | 62.5 | 54.1 | 70.9 | 65.2
1898 | 1724 | 77.6 | 62.4 | 55 | 70.8 | 65.3
1899 | 1725 | 77.5 | 62.6 | 55.4 | 70.8 | 65.2
1900 | 1726 | 77.5 | 62.7 | 55.8 | 70.7 | 65.3
1901 | 1727 | 77.1 | 62.7 | 55.9 | 70.6 | 65.3
1902 | 1728 | 76.5 | 62.7 | 55.9 | 70.3 | 65.4
1903 | 1729 | 76.1 | 62.7 | 56.5 | 70.1 | 65.3
1904 | 1730 | 76.2 | 62.8 | 57.2 | 70.1 | 65.2
1905 | 1731 | 76.1 | 62.4 | 57.4 | 70.1 | 65.3
1906 | 1732 | 76 | 61.8 | 58 | 70.1 | 65.4
1907 | 1733 | 75.9 | 61.9 | 58.4 | 70 | 65.4
1908 | 1734 | 75.9 | 62.5 | 58.8 | 70 | 65.5
1909 | 1735 | 75.8 | 63 | 58.8 | 69.9 | 65.5
1910 | 1736 | 76.2 | 62.6 | 58.6 | 70 | 65.5
1911 | 1737 | 76.4 | 62.8 | 59 | 70 | 65.6
1912 | 1738 | 76.4 | 62.9 | 59.6 | 70 | 65.6
1913 | 1739 | 76.5 | 62.7 | 59.9 | 70.1 | 65.8
1914 | 1740 | 75.7 | 63.2 | 60 | 69.8 | 65.9
1915 | 1741 | 75.7 | 64.2 | 60.1 | 69.7 | 65.9
1916 | 1742 | 75.5 | 63.9 | 59.7 | 69.6 | 65.8
1917 | 1743 | 75.4 | 63 | 59.8 | 69.6 | 65.9
1918 | 1744 | 75.2 | 63.1 | 59.9 | 69.5 | 65.9
1919 | 1745 | 75.1 | 62.9 | 59.8 | 69.4 | 66
1920 | 1746 | 74.9 | 63.1 | 59.7 | 69.3 | 66.1
1921 | 1747 | 75.2 | 62.2 | 59.7 | 69.3 | 66.2
1922 | 1748 | 75.2 | 62 | 59.8 | 69.3 | 66.1
1923 | 1749 | 75.4 | 62.5 | 59.6 | 69.4 | 66.1
1924 | 1750 | 75.3 | 63.5 | 59.9 | 69.5 | 66.2
1925 | 1751 | 75.1 | 64.1 | 60.4 | 69.5 | 66.4
1926 | 1752 | 74.8 | 63.9 | 60.7 | 69.4 | 66.5
1927 | 1753 | 75 | 64.3 | 60.6 | 69.4 | 66.7
1928 | 1754 | 75 | 64.4 | 60.1 | 69.4 | 66.7
1929 | 1755 | 75.2 | 63.7 | 59.4 | 69.4 | 66.7
1930 | 1756 | 75.3 | 63.7 | 59.5 | 69.5 | 66.7
1931 | 1757 | 75.4 | 63.7 | 59.7 | 69.6 | 66.8
1932 | 1758 | 75.2 | 63.5 | 60.1 | 69.6 | 66.9
1933 | 1759 | 75.2 | 63.5 | 60.5 | 69.6 | 67
1934 | 1760 | 75.2 | 63.4 | 60.3 | 69.6 | 67
1935 | 1761 | 75.3 | 63.5 | 60.6 | 69.6 | 67
1936 | 1762 | 75.1 | 64.3 | 60.8 | 69.6 | 67.1
1937 | 1763 | 74.7 | 64.3 | 61.1 | 69.5 | 67
1938 | 1764 | 74.7 | 64.5 | 61.5 | 69.4 | 67.1
1939 | 1765 | 74.8 | 64.1 | 61.3 | 69.5 | 67.1
1940 | 1766 | 74.7 | 63.7 | 60.9 | 69.5 | 67
1941 | 1767 | 74.7 | 63.2 | 60.3 | 69.5 | 66.6
1942 | 1768 | 74.5 | 62.9 | 59.7 | 69.5 | 66.6
1943 | 1769 | 74.2 | 63 | 59.5 | 69.4 | 66.6
1944 | 1770 | 74.4 | 62.6 | 59.5 | 69.4 | 66.7
1945 | 1771 | 74.6 | 62.6 | 59.2 | 69.5 | 66.7
1946 | 1772 | 74.9 | 63.1 | 59.1 | 69.6 | 66.7
1947 | 1773 | 75 | 63.3 | 59.4 | 69.6 | 66.8
1948 | 1774 | 74.9 | 63.3 | 59.8 | 69.7 | 66.8
1949 | 1775 | 75 | 63.1 | 59.5 | 69.7 | 66.9
1950 | 1776 | 75.2 | 62.7 | 59.5 | 69.8 | 67
1951 | 1777 | 75.1 | 62.9 | 60 | 69.7 | 67.1
1952 | 1778 | 74.7 | 62.2 | 59.8 | 69.6 | 67.1
1953 | 1779 | 74.3 | 61.6 | 59.7 | 69.4 | 67.1
1954 | 1780 | 74.2 | 61.8 | 59.8 | 69.2 | 67.1
1955 | 1781 | 74 | 62.4 | 59.9 | 69.3 | 67.1
1956 | 1782 | 73.4 | 62.7 | 60.1 | 69.2 | 67.1
1957 | 1783 | 73.2 | 62.8 | 60.2 | 69.1 | 67.2
1958 | 1784 | 72.8 | 63.3 | 60.5 | 69 | 67.3
1959 | 1785 | 72.7 | 63.6 | 61.1 | 69 | 67.3
1960 | 1786 | 73.2 | 63.2 | 61.7 | 69.2 | 67.4
1961 | 1787 | 73.1 | 63.1 | 62.4 | 69.1 | 67.5
1962 | 1788 | 72.7 | 62.9 | 61.9 | 69 | 67.6
1963 | 1789 | 72.4 | 63.7 | 61.7 | 68.9 | 67.7
1964 | 1790 | 72.6 | 63.4 | 61.9 | 68.8 | 67.8
1965 | 1791 | 72.8 | 63.6 | 62.3 | 68.8 | 67.8
1966 | 1792 | 72.7 | 63.8 | 62 | 68.9 | 67.7
1967 | 1793 | 72.8 | 64 | 61.5 | 68.9 | 67.6
1968 | 1794 | 73 | 63.6 | 61.7 | 69 | 67.2
1969 | 1795 | 72.9 | 63.2 | 61.9 | 69 | 67.3
1970 | 1796 | 72.8 | 62.8 | 62.1 | 69 | 67.5
1971 | 1797 | 72.4 | 63.1 | 62.4 | 68.9 | 67.6
1972 | 1798 | 72.2 | 63.5 | 62.2 | 68.9 | 67.4
1973 | 1799 | 72.3 | 63.2 | 61.6 | 68.9 | 67.7
1974 | 1800 | 72.4 | 63.2 | 60.3 | 69 | 67.8
1975 | 1801 | 72.5 | 63.2 | 59 | 69 | 67.9
1976 | 1802 | 72.4 | 63.1 | 57.7 | 69 | 67.9
1977 | 1803 | 72.6 | 63.3 | 59.2 | 69 | 67.7
1978 | 1804 | 72.9 | 62.4 | 60 | 69 | 67.4
1979 | 1805 | 72.9 | 61.2 | 59.1 | 69 | 67.4
1980 | 1806 | 72.6 | 61.1 | 58.3 | 68.8 | 67.4
1981 | 1807 | 72.7 | 61.3 | 59 | 68.8 | 67.5
1982 | 1808 | 72.5 | 61.1 | 59.5 | 68.8 | 67.6
1983 | 1809 | 72.2 | 61 | 60.3 | 68.7 | 67.7
1984 | 1810 | 72 | 61 | 60.6 | 68.6 | 67.6
1985 | 1811 | 71.7 | 60.8 | 60.8 | 68.5 | 67.8
1986 | 1812 | 71.5 | 60.5 | 60.9 | 68.5 | 67.6
1987 | 1813 | 71.6 | 60.3 | 60.3 | 68.5 | 67.7
1988 | 1814 | 71.5 | 60.6 | 59.6 | 68.5 | 67.8
1989 | 1815 | 71.5 | 60.9 | 60.3 | 68.5 | 67.9
1990 | 1816 | 71.7 | 61.4 | 60.1 | 68.6 | 68
1991 | 1817 | 71.9 | 61.7 | 61.2 | 68.6 | 68.1
1992 | 1818 | 72 | 61.4 | 61.9 | 68.7 | 68
1993 | 1819 | 72 | 61.4 | 61.4 | 68.7 | 68
1994 | 1820 | 71.8 | 61.6 | 60.9 | 68.7 | 67.9
1995 | 1821 | 71.9 | 61.5 | 60.4 | 68.6 | 67.8
1996 | 1822 | 71.9 | 61.6 | 60.5 | 68.5 | 67.8
1997 | 1823 | 72.4 | 61.6 | 59.4 | 68.6 | 67.7
1998 | 1824 | 72.6 | 62 | 60.3 | 68.5 | 67.7
1999 | 1825 | 72.4 | 62.2 | 61 | 68.5 | 67.8
2000 | 1826 | 72.6 | 61.9 | 61 | 68.6 | 67.6
2001 | 1827 | 72.3 | 62.1 | 61.1 | 68.4 | 67.7
2002 | 1828 | 72.3 | 62.3 | 61.6 | 68.4 | 67.8
2003 | 1829 | 72.3 | 62.1 | 60.7 | 68.4 | 67.8
2004 | 1830 | 72.2 | 62 | 60.8 | 68.5 | 67.9
2005 | 1831 | 72.3 | 61.9 | 60.6 | 68.5 | 68
2006 | 1832 | 72.4 | 61.9 | 60.4 | 68.5 | 67.9
2007 | 1833 | 72.6 | 61.7 | 59.3 | 68.6 | 67.9
2008 | 1834 | 72.6 | 60.9 | 57.8 | 68.6 | 68
2009 | 1835 | 72.7 | 60.7 | 58.3 | 68.6 | 68.1
2010 | 1836 | 72.4 | 60.7 | 60.3 | 68.5 | 68.1
2011 | 1837 | 72.6 | 60.8 | 60 | 68.5 | 68.1
2012 | 1838 | 72.6 | 60.5 | 60.6 | 68.5 | 68.2
2013 | 1839 | 72.4 | 60.6 | 60.2 | 68.4 | 68.4
2014 | 1840 | 72.9 | 61.1 | 60 | 68.5 | 68.4
2015 | 1841 | 73 | 61.5 | 59.9 | 68.6 | 68.6
2016 | 1842 | 72.9 | 61.1 | 61.3 | 68.6 | 68.6
2017 | 1843 | 73.1 | 60.9 | 61.5 | 68.6 | 68.6
2018 | 1844 | 73.3 | 60.4 | 60.8 | 68.7 | 68.7
2019 | 1845 | 73.4 | 61 | 59.5 | 68.8 | 68.7
2020 | 1846 | 73.3 | 60.8 | 61.1 | 68.8 | 68.6
2021 | 1847 | 73.1 | 60.3 | 60.1 | 68.8 | 68.8
2022 | 1848 | 73 | 59.3 | 61.7 | 68.7 | 68.9
2023 | 1849 | 73.3 | 58.9 | 62.1 | 68.8 | 68.9
2024 | 1850 | 73.1 | 58.2 | 60.6 | 68.7 | 68.8
2025 | 1851 | 73.2 | 58.2 | 58.5 | 68.8 | 68.9
2026 | 1852 | 73.3 | 58.3 | 59 | 68.9 | 68.6
2027 | 1853 | 73.6 | 58.5 | 59.4 | 69 | 68.4
2028 | 1854 | 73.8 | 58.4 | 59.4 | 69.1 | 68.4
2029 | 1855 | 73.3 | 58.5 | 59.7 | 69.2 | 68.5
2030 | 1856 | 73.5 | 59.3 | 59.5 | 69.2 | 68.4
2031 | 1857 | 73.8 | 59.9 | 59 | 69.3 | 68.5
2032 | 1858 | 74 | 59.8 | 58.7 | 69.4 | 68.7
2033 | 1859 | 73.9 | 60 | 59.8 | 69.4 | 68.9
2034 | 1860 | 74 | 59.9 | 60.9 | 69.5 | 68.9
2035 | 1861 | 74 | 59.2 | 61.3 | 69.5 | 69
2036 | 1862 | 74 | 59.4 | 60.2 | 69.5 | 69.1
2037 | 1863 | 74.3 | 59.6 | 59.3 | 69.5 | 68.9
2038 | 1864 | 74.5 | 59.8 | 57.4 | 69.6 | 68.8
2039 | 1865 | 74.7 | 59.7 | 58.3 | 69.7 | 68.8
2040 | 1866 | 74.7 | 59.6 | 57.1 | 69.7 | 68.9
2041 | 1867 | 74.2 | 59.7 | 54.5 | 69.7 | 68.9
2042 | 1868 | 74.2 | 59.8 | 51.5 | 69.6 | 68.8
2043 | 1869 | 73.9 | 59.9 | 50.9 | 69.5 | 69
2044 | 1870 | 74 | 59.3 | 52.9 | 69.4 | 68.8
2045 | 1871 | 73.9 | 59 | 53.2 | 69.5 | 68.7
2046 | 1872 | 73.7 | 59.9 | 55.2 | 69.5 | 68.6
2047 | 1873 | 74.3 | 60.9 | 52.5 | 69.5 | 68.1
2048 | 1874 | 74.3 | 61.3 | 50.5 | 69.5 | 67.9
2049 | 1875 | 74.7 | 61.1 | 51.7 | 69.6 | 68.1
2050 | 1876 | 74.6 | 61.7 | 52.4 | 69.8 | 68.1
2051 | 1877 | 74.3 | 60.9 | 55 | 69.8 | 68.2
2052 | 1878 | 74.6 | 60.4 | 53.9 | 69.9 | 68
2053 | 1879 | 74.6 | 59.9 | 54.2 | 69.9 | 68
2054 | 1880 | 74.2 | 59.3 | 56.4 | 69.8 | 68.2
2055 | 1881 | 74.4 | 58.5 | 56.8 | 69.7 | 68.3
2056 | 1882 | 74.2 | 57.9 | 56.2 | 69.8 | 68.5
2057 | 1883 | 74.4 | 58.2 | 56.8 | 69.9 | 68.6
2058 | 1884 | 74.9 | 59.1 | 58.2 | 70 | 68.8
2059 | 1885 | 75.1 | 59 | 58.9 | 70.1 | 68.8
2060 | 1886 | 74.8 | 59.3 | 58.2 | 70.1 | 68.8
2061 | 1887 | 74.3 | 58.7 | 57.3 | 70.1 | 68.5
2062 | 1888 | 74.1 | 58.7 | 54.8 | 70 | 68.1
2063 | 1889 | 74.4 | 59.1 | 52.1 | 70 | 68
2064 | 1890 | 74.2 | 59.8 | 52.5 | 70.1 | 68
2065 | 1891 | 73.9 | 62.4 | 54.2 | 70.1 | 68.2
2066 | 1892 | 74.3 | 62.5 | 53.5 | 70 | 68.4
2067 | 1893 | 74.3 | 60.6 | 53.9 | 70 | 68.4
2068 | 1894 | 74.2 | 60.5 | 54.5 | 70 | 68.4
2069 | 1895 | 74.7 | 60.1 | 55.3 | 70.1 | 68.6
2070 | 1896 | 75 | 59.7 | 56.4 | 70.2 | 68.6
2071 | 1897 | 75.2 | 59.9 | 57 | 70.2 | 68.6
2072 | 1898 | 75 | 60.6 | 57.7 | 70.2 | 68.7
2073 | 1899 | 75.1 | 63.2 | 57.7 | 70.3 | 68.7
2074 | 1900 | 75.3 | 63.3 | 57.8 | 70.2 | 68.5
2075 | 1901 | 75.3 | 63.4 | 57.5 | 70.4 | 68.4
2076 | 1902 | 75.1 | 63.2 | 57.5 | 70.5 | 68.4
2077 | 1903 | 75.3 | 62.1 | 57.8 | 70.5 | 68.5
2078 | 1904 | 75.5 | 61.6 | 56.8 | 70.4 | 68.5
2079 | 1905 | 75.7 | 61.6 | 56.2 | 70.5 | 68.5
2080 | 1906 | 75.8 | 62.5 | 56.9 | 70.6 | 68.5
2081 | 1907 | 75.9 | 62.6 | 57.4 | 70.5 | 68.4
2082 | 1908 | 76 | 62.4 | 58.6 | 70.7 | 68.5
2083 | 1909 | 76.1 | 61.7 | 59.4 | 70.8 | 68.7
2084 | 1910 | 75.9 | 61.2 | 59.9 | 70.8 | 68.8
2085 | 1911 | 75.9 | 61.4 | 59 | 70.8 | 68.7
2086 | 1912 | 76.1 | 61.2 | 57.6 | 70.8 | 68.7
2087 | 1913 | 76.1 | 60.2 | 56.2 | 70.9 | 68.5
2088 | 1914 | 76.1 | 59.4 | 54.5 | 70.9 | 68.5
2089 | 1915 | 76.1 | 58.9 | 54.4 | 70.9 | 68.5
2090 | 1916 | 76.2 | 58.8 | 53.6 | 70.8 | 68.2
2091 | 1917 | 76 | 58.6 | 52.3 | 70.9 | 68.2
2092 | 1918 | 76 | 58.6 | 51.7 | 71.1 | 68.3
2093 | 1919 | 76.1 | 58.1 | 51 | 71 | 68.5
2094 | 1920 | 76.1 | 57.9 | 49.4 | 70.9 | 68.4
2095 | 1921 | 76.1 | 58.3 | 51.1 | 70.8 | 68.1
2096 | 1922 | 76.1 | 58.2 | 53 | 70.7 | 68.1
2097 | 1923 | 76 | 58.4 | 54.1 | 70.6 | 68.1
2098 | 1924 | 76.1 | 59.2 | 54.4 | 70.6 | 67.9
2099 | 1925 | 76.2 | 59.2 | 53.9 | 70.7 | 67.6
2100 | 1926 | 76.2 | 59.4 | 53.7 | 70.8 | 67.7
2101 | 1927 | 76.2 | 59.1 | 53.9 | 70.7 | 67.8
2102 | 1928 | 76.2 | 58.9 | 54.4 | 70.7 | 67.9
2103 | 1929 | 76.1 | 59 | 54.7 | 70.6 | 67.8
2104 | 1930 | 76.1 | 58.7 | 54 | 70.6 | 67.5
2105 | 1931 | 76.1 | 58.7 | 54.8 | 70.8 | 67.6
2106 | 1932 | 76.1 | 58.1 | 55.2 | 70.7 | 67.9
2107 | 1933 | 76.1 | 57.5 | 55.4 | 70.6 | 68.2
2108 | 1934 | 76.1 | 57.7 | 56 | 70.7 | 68.4
2109 | 1935 | 76 | 58 | 56.8 | 70.5 | 68.4
2110 | 1936 | 75.9 | 57.8 | 57.7 | 70.4 | 68.2
2111 | 1937 | 75.9 | 58 | 57.5 | 70.6 | 68.4
2112 | 1938 | 75.7 | 57.9 | 58.3 | 70.5 | 68.4
2113 | 1939 | 75.7 | 58.1 | 58.4 | 70.3 | 68.4
2114 | 1940 | 75.7 | 58.3 | 57.7 | 70.1 | 68.4
2115 | 1941 | 75.8 | 58.7 | 56.9 | 70 | 68.5
2116 | 1942 | 75.8 | 59.5 | 56.7 | 69.9 | 68.6
2117 | 1943 | 75.8 | 60.4 | 55 | 70.1 | 68.5
2118 | 1944 | 75.6 | 60.2 | 52.3 | 70.2 | 68.4
2119 | 1945 | 75.7 | 60.6 | 50.8 | 70.3 | 68.3
2120 | 1946 | 75.7 | 61.5 | 51.6 | 70.3 | 68.3
2121 | 1947 | 75.8 | 61.3 | 53.5 | 70.3 | 68.2
2122 | 1948 | 75.7 | 61.3 | 54.1 | 70.2 | 68.2
2123 | 1949 | 75.7 | 60.9 | 54.9 | 70.1 | 68.1
2124 | 1950 | 75.7 | 60.5 | 55.6 | 70 | 68
2125 | 1951 | 75.8 | 60.6 | 55.3 | 70.2 | 68.1
2126 | 1952 | 75.9 | 60.4 | 55.4 | 70.3 | 68.1
2127 | 1953 | 75.9 | 60.2 | 56 | 70.4 | 68.1
2128 | 1954 | 75 | 59.9 | 56 | 70.4 | 67.8
2129 | 1955 | 74.8 | 60.8 | 56.3 | 70.4 | 67.9
2130 | 1956 | 75.1 | 60.7 | 57.2 | 70.3 | 68.1
2131 | 1957 | 75.3 | 60.6 | 58.5 | 70.1 | 68
2132 | 1958 | 74.9 | 60.5 | 59 | 70 | 67.9
2133 | 1959 | 74.7 | 61.1 | 59.6 | 69.9 | 67.8
2134 | 1960 | 75 | 62.1 | 60.9 | 69.9 | 67.8
2135 | 1961 | 75.3 | 62.3 | 62.1 | 69.8 | 67.8
2136 | 1962 | 74.9 | 61.6 | 63.2 | 70 | 67.9
2137 | 1963 | 74.9 | 62.1 | 64.5 | 70 | 68
2138 | 1964 | 75 | 62.2 | 65.3 | 69.6 | 67.9
2139 | 1965 | 74.8 | 62.4 | 66.3 | 69.6 | 67.9
2140 | 1966 | 75.1 | 62.9 | 66.8 | 69.6 | 67.6
2141 | 1967 | 75.2 | 63.3 | 67.6 | 69.8 | 67.6
2142 | 1968 | 75.3 | 63.6 | 68.7 | 69.8 | 67.8
2143 | 1969 | 75.4 | 63.2 | 69.3 | 69.7 | 67.9
2144 | 1970 | 75.4 | 63 | 69.9 | 69.7 | 68
2145 | 1971 | 75.4 | 63.5 | 70.5 | 69.6 | 67.8
2146 | 1972 | 75.4 | 63 | 71.3 | 69.7 | 67.9
2147 | 1973 | 75.4 | 63 | 71.5 | 69.7 | 67.8
2148 | 1974 | 75 | 63.4 | 72.4 | 69.8 | 67.6
2149 | 1975 | 75.2 | 63.6 | 72.8 | 69.7 | 67.6
2150 | 1976 | 75.3 | 63.9 | 73.5 | 69.7 | 67.6
2151 | 1977 | 75.4 | 64.1 | 74 | 69.8 | 67.6
2152 | 1978 | 75.3 | 64.6 | 74.2 | 69.7 | 67.5
2153 | 1979 | 75.3 | 65.1 | 74.9 | 69.6 | 67.8
2154 | 1980 | 75.1 | 64.9 | 75.2 | 69.4 | 67.9
2155 | 1981 | 75.1 | 64.7 | 75.7 | 69.3 | 67.8
2156 | 1982 | 75.1 | 65.6 | 76 | 69.5 | 67.8
2157 | 1983 | 75.1 | 66.7 | 76.6 | 69.6 | 67.8
2158 | 1984 | 75.2 | 67 | 77.3 | 69.6 | 67.7
2159 | 1985 | 75.3 | 67 | 77.5 | 69.7 | 67.8
2160 | 1986 | 75.4 | 67 | 77.8 | 69.7 | 67.7
2161 | 1987 | 75.3 | 66.7 | 78.3 | 69.7 | 67.7
2162 | 1988 | 75.3 | 66.6 | 78.7 | 69.7 | 67.6
2163 | 1989 | 74.3 | 66.8 | 79 | 69.5 | 67.4
2164 | 1990 | 73.8 | 67 | 79.7 | 69.3 | 67.3
2165 | 1991 | 73.4 | 66.7 | 80 | 69.3 | 67.3
2166 | 1992 | 72.7 | 65.7 | 80.3 | 69.3 | 67.3
2167 | 1993 | 72.7 | 65.5 | 80.6 | 69.2 | 67.1
2168 | 1994 | 73.1 | 65.9 | 80.9 | 69.1 | 67
2169 | 1995 | 73.4 | 66.6 | 81.3 | 69.3 | 66.9
2170 | 1996 | 73.8 | 67 | 81.7 | 69.3 | 66.9
2171 | 1997 | 74.1 | 67 | 81.9 | 69.4 | 66.8
2172 | 1998 | 74.2 | 66.8 | 82.2 | 69.4 | 66.9
2173 | 1999 | 74.3 | 66.1 | 82.6 | 69.2 | 66.8
2174 | 2000 | 74.4 | 66.1 | 83 | 69.3 | 66.8
2175 | 2001 | 74.5 | 66.2 | 83.2 | 69.3 | 66.9
2176 | 2002 | 74.5 | 66.2 | 83.4 | 69.3 | 66.9
2177 | 2003 | 74.5 | 66.3 | 83.9 | 69.2 | 66.8
2178 | 2004 | 74.5 | 66.2 | 84.5 | 69.3 | 66.6
2179 | 2005 | 73.8 | 66.3 | 84.7 | 69.2 | 66.3
2180 | 2006 | 73.4 | 66.3 | 85.1 | 69.1 | 66.2
2181 | 2007 | 72.4 | 66.5 | 85.5 | 68.9 | 66.2
2182 | 2008 | 72.2 | 67 | 85.8 | 68.7 | 66.2
2183 | 2009 | 72.7 | 67.7 | 86.1 | 68.7 | 66.3
2184 | 2010 | 73.1 | 68.5 | 86.5 | 68.8 | 66.3
2185 | 2011 | 73.4 | 68.8 | 86.6 | 68.9 | 66.4
2186 | 2012 | 73.5 | 69.1 | 87 | 68.8 | 66.1
2187 | 2013 | 73.4 | 69.1 | 87.2 | 68.8 | 66.2
2188 | 2014 | 73.5 | 69.5 | 87.5 | 68.7 | 66
2189 | 2015 | 73.7 | 70.2 | 87.7 | 68.7 | 65.9
2190 | 2016 | 73.5 | 71.3 | 87.9 | 68.8 | 66.1
2191 | 2017 | 73.4 | 71.9 | 88.2 | 68.8 | 66.3
2192 | 2018 | 73.5 | 72.1 | 88.3 | 68.4 | 66.4
2193 | 2019 | 73.3 | 72.1 | 88.4 | 68.4 | 66.4
2194 | 2020 | 73.3 | 72.6 | 88.7 | 68.5 | 66.5
2195 | 2021 | 73.5 | 73.2 | 88.6 | 68.4 | 66.2
2196 | 2022 | 73.6 | 74 | 88.7 | 68.5 | 66.3
2197 | 2023 | 73.8 | 74.3 | 88.8 | 68.6 | 66.2
2198 | 2024 | 72.8 | 74.3 | 88.7 | 68.5 | 66
2199 | 2025 | 72.1 | 74.5 | 89 | 68.2 | 65.9
2200 | 2026 | 72.3 | 75 | 89.3 | 68.2 | 65.7
2201 | 2027 | 72.3 | 75.5 | 89.6 | 68.3 | 65.9
2202 | 2028 | 72.6 | 75.7 | 89.8 | 68.2 | 66.1
2203 | 2029 | 72.8 | 76 | 90 | 68 | 66.1
2204 | 2030 | 73.1 | 75.8 | 90.1 | 67.7 | 66
2205 | 2031 | 72.9 | 75.6 | 90.1 | 67.7 | 66
2206 | 2032 | 72.9 | 75.6 | 90.1 | 67.6 | 65.9
2207 | 2033 | 72.8 | 75.2 | 90.3 | 67.6 | 65.9
2208 | 2034 | 72.8 | 75.4 | 90.3 | 67.7 | 65.7
2209 | 2035 | 73 | 75.9 | 90.3 | 67.7 | 65.7
2210 | 2036 | 73 | 76.2 | 90.5 | 67.8 | 65.7
2211 | 2037 | 73 | 76.5 | 90.5 | 67.8 | 65.8
2212 | 2038 | 73.2 | 77 | 90.6 | 67.8 | 65.9
2213 | 2039 | 73.2 | 77.5 | 90.7 | 67.6 | 66
2214 | 2040 | 73 | 77.1 | 90.6 | 67.3 | 65.7
2215 | 2041 | 72.8 | 76.9 | 90.7 | 67.3 | 65.5
2216 | 2042 | 73 | 77.4 | 90.8 | 67.5 | 65.4
2217 | 2043 | 73 | 78 | 90.8 | 67.6 | 65.3
2218 | 2044 | 72.9 | 78.8 | 90.8 | 67.6 | 65.6
2219 | 2045 | 73.1 | 79.5 | 90.8 | 67.7 | 65.7
2220 | 2046 | 73.2 | 80 | 90.9 | 67.8 | 65.7
2221 | 2047 | 73.1 | 80.2 | 90.7 | 67.6 | 65.7
2222 | 2048 | 73 | 80.1 | 90.7 | 67.5 | 65.7
2223 | 2049 | 73.2 | 80.4 | 90.8 | 67.6 | 65.8
2224 | 2050 | 73.2 | 80.7 | 90.8 | 67.6 | 66
2225 | 2051 | 73.1 | 80.6 | 90.8 | 67.6 | 66
2226 | 2052 | 73.2 | 81 | 90.8 | 67.7 | 66.2
2227 | 2053 | 73.3 | 81.2 | 90.9 | 67.8 | 66.2
2228 | 2054 | 72.9 | 81.3 | 90.9 | 67.7 | 65.7
2229 | 2055 | 72.5 | 81.6 | 91 | 67.6 | 65.3
2230 | 2056 | 72.7 | 82 | 90.9 | 67.6 | 65.2
2231 | 2057 | 72.7 | 82.5 | 91 | 67.6 | 65.1
2232 | 2058 | 72.9 | 83 | 90.8 | 67.6 | 65.1
2233 | 2059 | 72.9 | 83.5 | 90.9 | 67.6 | 64.7
2234 | 2060 | 72.2 | 83.6 | 90.8 | 67.6 | 64.3
2235 | 2061 | 71.5 | 83.8 | 90.9 | 67.5 | 64.3
2236 | 2062 | 71.6 | 84.9 | 91 | 67.5 | 64.4
2237 | 2063 | 71.8 | 85.7 | 91.1 | 67.5 | 64.7
2238 | 2064 | 72.1 | 86 | 91.1 | 67.5 | 64.8
2239 | 2065 | 72.2 | 86.5 | 91.1 | 67.4 | 64.4
2240 | 2066 | 72.1 | 86.8 | 91.1 | 67.3 | 64.3
2241 | 2067 | 72.2 | 87.7 | 91.1 | 67.4 | 64.5
2242 | 2068 | 72.2 | 88.5 | 91.2 | 67.6 | 64.6
2243 | 2069 | 72.4 | 88.7 | 91.2 | 67.5 | 64.8
2244 | 2070 | 72.5 | 88.4 | 91.1 | 67.2 | 64.8
2245 | 2071 | 72.6 | 88.1 | 91.1 | 67.1 | 64.6
2246 | 2072 | 72.7 | 88.1 | 91.1 | 67.1 | 64.7
2247 | 2073 | 72.6 | 87.6 | 91.1 | 67.1 | 64.7
2248 | 2074 | 72.3 | 87.1 | 91.1 | 67.1 | 64.7
2249 | 2075 | 72.4 | 87.1 | 91 | 67.1 | 64.8
2250 | 2076 | 72.5 | 87.3 | 91 | 67.2 | 64.8
2251 | 2077 | 72.5 | 88.1 | 91 | 67.3 | 64.8
2252 | 2078 | 72.6 | 88.3 | 90.8 | 67.2 | 64.8
2253 | 2079 | 72.5 | 88.5 | 90.7 | 67.3 | 64.9
2254 | 2080 | 72.6 | 88.7 | 90.8 | 67.3 | 65
2255 | 2081 | 72.5 | 88.6 | 90.9 | 67.3 | 64.9
2256 | 2082 | 72.5 | 88.8 | 91 | 67.3 | 65.1
2257 | 2083 | 72.5 | 88.5 | 91.1 | 67.2 | 64.8
2258 | 2084 | 72.4 | 88.7 | 91.2 | 67.1 | 64.6
2259 | 2085 | 72.4 | 89 | 91.3 | 67 | 64.2
2260 | 2086 | 72.3 | 89.6 | 91.2 | 66.9 | 64.3
2261 | 2087 | 72.4 | 89.8 | 91.2 | 66.7 | 64.2
2262 | 2088 | 72 | 89.6 | 91.3 | 66.8 | 64.2
2263 | 2089 | 72 | 90.1 | 91.1 | 66.8 | 64
2264 | 2090 | 71.9 | 90.7 | 90.9 | 66.9 | 63.8
2265 | 2091 | 72.1 | 91.1 | 91 | 66.9 | 64.2
2266 | 2092 | 72 | 91.2 | 91 | 66.8 | 64.3
2267 | 2093 | 71.7 | 91.7 | 90.9 | 66.9 | 64.4
2268 | 2094 | 71.9 | 92.3 | 90.9 | 66.9 | 64.8
2269 | 2095 | 71.9 | 92.2 | 90.8 | 66.8 | 64.8
2270 | 2096 | 71.8 | 92.3 | 91 | 66.9 | 64.9
2271 | 2097 | 71.9 | 92.3 | 91 | 66.7 | 64.7
2272 | 2098 | 71.8 | 92.1 | 91.1 | 66.2 | 64.2
2273 | 2099 | 71.6 | 92.2 | 91.1 | 66 | 64
2274 | 2100 | 71.5 | 92.4 | 91.2 | 66.1 | 64.2
2275 | 2101 | 71.5 | 92.7 | 91.2 | 66 | 64.2
2276 | 2102 | 71.6 | 92.9 | 91.2 | 66.1 | 64
2277 | 2103 | 71.8 | 93.3 | 91.2 | 66.3 | 63.7
2278 | 2104 | 71.8 | 93.4 | 91.1 | 66.4 | 63.7
2279 | 2105 | 71.8 | 93.5 | 91 | 66.4 | 63.9
2280 | 2106 | 71.8 | 93.8 | 90.9 | 66.5 | 63.9
2281 | 2107 | 71.8 | 94 | 90.8 | 66.5 | 64.1
2282 | 2108 | 71.8 | 93.9 | 90.6 | 66.4 | 64.1
2283 | 2109 | 71.7 | 93.9 | 90.6 | 66.5 | 64
2284 | 2110 | 71.8 | 94 | 90.6 | 66.5 | 64.2
2285 | 2111 | 71.7 | 93.7 | 90.7 | 66.4 | 64.3
2286 | 2112 | 71.6 | 93.5 | 90.6 | 66.4 | 64.3
2287 | 2113 | 71.6 | 93.7 | 90.6 | 66.4 | 64.4
2288 | 2114 | 71.7 | 93.8 | 90.6 | 66.3 | 64.3
2289 | 2115 | 71.5 | 93.9 | 90.5 | 66.3 | 64.1
2290 | 2116 | 71.5 | 94.4 | 90.6 | 66.3 | 64
2291 | 2117 | 71.6 | 94.6 | 90.6 | 66.2 | 63.7
2292 | 2118 | 71.5 | 94.8 | 90.7 | 66.1 | 63.4
2293 | 2119 | 71.6 | 95.1 | 90.7 | 66.1 | 63.5
2294 | 2120 | 71.6 | 95.4 | 90.8 | 66.2 | 63.5
2295 | 2121 | 71.4 | 96 | 90.8 | 66.4 | 63.6
2296 | 2122 | 71.5 | 96.3 | 90.7 | 66.4 | 63.6
2297 | 2123 | 71.5 | 96.2 | 90.8 | 66.2 | 63.6
2298 | 2124 | 71.4 | 96 | 90.8 | 66.1 | 63.5
2299 | 2125 | 71.5 | 96.2 | 90.8 | 66.2 | 63.5
2300 | 2126 | 71.6 | 96.4 | 90.8 | 66.2 | 63.7
2301 | 2127 | 71.6 | 96.6 | 90.9 | 66.1 | 63.7
2302 | 2128 | 71.6 | 96.6 | 90.9 | 66 | 63.6
2303 | 2129 | 71.6 | 96.4 | 90.8 | 66 | 63.4
2304 | 2130 | 71.5 | 96.5 | 90.7 | 66.1 | 63.3
2305 | 2131 | 71.6 | 96.5 | 90.7 | 66.1 | 63.2
2306 | 2132 | 71.6 | 96.6 | 90.7 | 66.1 | 63.1
2307 | 2133 | 71.5 | 96.9 | 90.9 | 66.1 | 63.1
2308 | 2134 | 71.4 | 97.3 | 90.9 | 66.1 | 63.1
2309 | 2135 | 71.4 | 97.7 | 90.9 | 66.1 | 63
2310 | 2136 | 71.2 | 97.8 | 90.9 | 65.9 | 62.8
2311 | 2137 | 70.8 | 97.6 | 90.9 | 65.7 | 62.6
2312 | 2138 | 70.7 | 97.7 | 90.8 | 65.6 | 62.6
2313 | 2139 | 71 | 97.9 | 90.7 | 65.6 | 62.9
2314 | 2140 | 71.1 | 97.8 | 90.7 | 65.7 | 63
2315 | 2141 | 71.2 | 98.1 | 90.6 | 65.6 | 62.8
2316 | 2142 | 71.2 | 98.3 | 90.4 | 65.5 | 62.6
2317 | 2143 | 71.1 | 98.5 | 90.3 | 65.6 | 62.7
2318 | 2144 | 71.2 | 98.8 | 90.3 | 65.7 | 62.6
2319 | 2145 | 71.2 | 99.1 | 90.2 | 65.7 | 62.6
2320 | 2146 | 71.2 | 99.3 | 90.2 | 65.4 | 62.4
2321 | 2147 | 71.2 | 99.2 | 90.1 | 65.1 | 62
2322 | 2148 | 71.2 | 99.5 | 90 | 65.3 | 61.9
2323 | 2149 | 71.3 | 99.9 | 89.9 | 65.4 | 62.3
2324 | 2150 | 71.1 | 99.7 | 89.9 | 65.4 | 62.3
2325 | 2151 | 71 | 99.9 | 89.6 | 65.5 | 62.2
2326 | 2152 | 71 | 100.4 | 89.6 | 65.5 | 62.2
2327 | 2153 | 70.8 | 100.6 | 89.6 | 65.4 | 62
2328 | 2154 | 70.5 | 100.9 | 89.7 | 65.4 | 62.4
2329 | 2155 | 70.7 | 101 | 89.8 | 65.3 | 62.7
2330 | 2156 | 70.7 | 101.1 | 90 | 65.1 | 62.8
2331 | 2157 | 70.8 | 101.2 | 90 | 64.9 | 62.9
2332 | 2158 | 70.7 | 101.3 | 90.1 | 64.9 | 62.9
2333 | 2159 | 70.7 | 101.4 | 90 | 64.8 | 62.9
2334 | 2160 | 70.7 | 101.4 | 89.9 | 64.7 | 62.8
2335 | 2161 | 70.7 | 101.5 | 89.8 | 64.7 | 62.5
2336 | 2162 | 70.6 | 101.8 | 89.7 | 64.9 | 62.3
2337 | 2163 | 70.6 | 102.2 | 89.6 | 64.9 | 62
2338 | 2164 | 70.7 | 102.5 | 89.6 | 64.8 | 61.7
2339 | 2165 | 70.8 | 102.6 | 89.4 | 64.8 | 62
2340 | 2166 | 70.9 | 102.9 | 89.4 | 64.9 | 62
2341 | 2167 | 70.8 | 103 | 89.4 | 64.7 | 62
2342 | 2168 | 70.7 | 102.7 | 89.3 | 64.4 | 61.9
2343 | 2169 | 70.3 | 102.6 | 89.1 | 64.3 | 62
2344 | 2170 | 69.4 | 102.5 | 89.1 | 64.1 | 61.8
2345 | 2171 | 69.3 | 102.8 | 89.1 | 64.1 | 61.8
2346 | 2172 | 69.1 | 103.1 | 89.3 | 64.1 | 61.9
2347 | 2173 | 68.5 | 103.2 | 89.4 | 64 | 62
2348 | 2174 | 68.4 | 103.3 | 89.4 | 64 | 61.9
2349 | 2175 | 68.7 | 103.4 | 89.3 | 63.8 | 61.9
2350 | 2176 | 68.8 | 103.5 | 89.1 | 63.8 | 61.8
2351 | 2177 | 68.8 | 103.9 | 89 | 63.9 | 61.6
2352 | 2178 | 69 | 104.5 | 89 | 63.9 | 61.7
2353 | 2179 | 68.4 | 104.5 | 89.1 | 63.9 | 61.8
2354 | 2180 | 68 | 104.7 | 89.1 | 63.7 | 61.9
2355 | 2181 | 68.1 | 104.9 | 89 | 63.6 | 62
2356 | 2182 | 68.5 | 105.4 | 88.9 | 63.7 | 62.2
2357 | 2183 | 68.8 | 105.3 | 89 | 63.6 | 62.3
2358 | 2184 | 68.4 | 104.9 | 88.9 | 63.5 | 62
2359 | 2185 | 68.3 | 104.9 | 88.6 | 63.5 | 61.8
2360 | 2186 | 68.5 | 105.1 | 88.5 | 63.6 | 61.7
2361 | 2187 | 68.8 | 105.5 | 88.5 | 63.6 | 61.7
2362 | 2188 | 68.6 | 105.4 | 88.4 | 63.6 | 61.1
2363 | 2189 | 68.2 | 105.3 | 88.3 | 63.4 | 60.9
2364 | 2190 | 68.6 | 105.9 | 88.2 | 63.4 | 61.2
2365 | 2191 | 68.9 | 105.8 | 88.2 | 63.4 | 61.3
2366 | 2192 | 69 | 105.6 | 88.3 | 63.4 | 61.2
2367 | 2193 | 69 | 106 | 88.2 | 63.2 | 61.1
2368 | 2194 | 68.9 | 105.9 | 88.1 | 63 | 61.2
2369 | 2195 | 69.1 | 106.4 | 87.9 | 63.2 | 61.3
2370 | 2196 | 69.3 | 106.5 | 87.7 | 63.3 | 61.4
2371 | 2197 | 69.4 | 106.7 | 87.6 | 63.5 | 61.8
2372 | 2198 | 69.5 | 106.8 | 87.5 | 63.5 | 61.9
2373 | 2199 | 69.5 | 106.8 | 87.2 | 63.4 | 61.9
2374 | 2200 | 69.6 | 107 | 86.9 | 63.4 | 62
2375 | 2201 | 69.4 | 106.9 | 86.7 | 63.3 | 62.1
2376 | 2202 | 69.4 | 106.8 | 86.7 | 63.3 | 62.2
2377 | 2203 | 69.3 | 106.8 | 86.8 | 63.2 | 62.2
2378 | 2204 | 69.1 | 106.5 | 86.9 | 63.1 | 62
2379 | 2205 | 69 | 106.4 | 86.9 | 63 | 61.8
2380 | 2206 | 68.7 | 106.2 | 86.9 | 63 | 61.6
2381 | 2207 | 68.2 | 106.1 | 86.8 | 63 | 61.6
2382 | 2208 | 68.2 | 106.2 | 86.8 | 63 | 61.5
2383 | 2209 | 68.4 | 106.4 | 86.6 | 63 | 61.6
2384 | 2210 | 68.5 | 106.8 | 86.6 | 63.1 | 61.8
2385 | 2211 | 68.7 | 107.3 | 86.7 | 63.2 | 61.9
2386 | 2212 | 68.9 | 107.7 | 86.7 | 63.2 | 62
2387 | 2213 | 68.8 | 107.8 | 86.8 | 63 | 62
2388 | 2214 | 68.5 | 107.6 | 86.8 | 63 | 61.9
2389 | 2215 | 68.5 | 107.7 | 86.7 | 62.9 | 61.8
2390 | 2216 | 68.6 | 108.1 | 86.7 | 63 | 61.6
2391 | 2217 | 68.7 | 108.3 | 86.7 | 63 | 61.6
2392 | 2218 | 68.5 | 108.1 | 86.7 | 62.9 | 61.6
2393 | 2219 | 68.5 | 108 | 86.7 | 62.9 | 61.5
2394 | 2220 | 68.8 | 108.2 | 86.7 | 62.9 | 61.7
2395 | 2221 | 68.7 | 108 | 86.7 | 62.6 | 61.7
2396 | 2222 | 68.3 | 107.8 | 86.6 | 62.3 | 61.4
2397 | 2223 | 68.3 | 108.2 | 86.7 | 62.4 | 61.4
2398 | 2224 | 68.4 | 108.1 | 86.6 | 62.4 | 61.3
2399 | 2225 | 67.9 | 107.8 | 86.5 | 62.4 | 61.2
2400 | 2226 | 68.1 | 108 | 86.4 | 62.4 | 61.2
2401 | 2227 | 68.1 | 108.3 | 86.3 | 62.5 | 61.2
2402 | 2228 | 68.2 | 108.8 | 86.2 | 62.6 | 61.2
2403 | 2229 | 68.4 | 109.2 | 86.1 | 62.7 | 61.3
2404 | 2230 | 68.7 | 109.4 | 86 | 62.7 | 61.1
2405 | 2231 | 68.9 | 109.8 | 85.9 | 62.9 | 61.3
2406 | 2232 | 69 | 109.8 | 86 | 62.9 | 61.4
2407 | 2233 | 68.9 | 109.4 | 85.8 | 62.7 | 61.1
2408 | 2234 | 68.8 | 109 | 85.7 | 62.5 | 61
2409 | 2235 | 68.9 | 108.6 | 85.7 | 62.5 | 61.1
2410 | 2236 | 68.8 | 108.4 | 85.8 | 62.6 | 61
2411 | 2237 | 68.8 | 108.4 | 85.8 | 62.6 | 60.8
2412 | 2238 | 68.8 | 108.7 | 85.8 | 62.6 | 60.9
2413 | 2239 | 68.9 | 108.7 | 85.7 | 62.6 | 61.1
2414 | 2240 | 68.9 | 108.7 | 85.6 | 62.4 | 61.1
2415 | 2241 | 68.8 | 108.8 | 85.4 | 62.3 | 61.2
2416 | 2242 | 68.6 | 109 | 85.3 | 62.3 | 61.3
2417 | 2243 | 68.7 | 109.2 | 85.3 | 62.2 | 61.4
2418 | 2244 | 68.6 | 109.1 | 85.3 | 62 | 61.3
2419 | 2245 | 68.5 | 109 | 85.3 | 62 | 61
2420 | 2246 | 68.4 | 109 | 85.3 | 62.1 | 60.8
2421 | 2247 | 68.4 | 109.4 | 85.1 | 62.2 | 60.5
2422 | 2248 | 68.5 | 109.7 | 84.9 | 62.3 | 60.3
2423 | 2249 | 68.4 | 110 | 84.8 | 62.3 | 60.4
2424 | 2250 | 68.5 | 110.2 | 84.7 | 62.3 | 60.7
2425 | 2251 | 68.4 | 110.1 | 84.8 | 62.2 | 60.9
2426 | 2252 | 68.2 | 109.9 | 84.8 | 62.1 | 61
2427 | 2253 | 68 | 110 | 84.8 | 62.1 | 61
2428 | 2254 | 68 | 110.2 | 84.8 | 62 | 60.8
2429 | 2255 | 68.1 | 110.4 | 84.7 | 62 | 60.7
2430 | 2256 | 68.2 | 110.6 | 84.7 | 62 | 60.3
2431 | 2257 | 68.3 | 110.6 | 84.7 | 62 | 60.2
2432 | 2258 | 68.3 | 110.6 | 84.6 | 62 | 60.5
2433 | 2259 | 68.2 | 110.3 | 84.6 | 61.9 | 60.5
2434 | 2260 | 67.7 | 110 | 84.4 | 61.8 | 60.4
2435 | 2261 | 67.7 | 110.1 | 84.3 | 61.9 | 60.3
2436 | 2262 | 67.8 | 110.2 | 84.1 | 61.9 | 60.2
2437 | 2263 | 67.8 | 110.7 | 83.9 | 61.9 | 60.1
2438 | 2264 | 67.8 | 111.5 | 83.8 | 62 | 60.2
2439 | 2265 | 68 | 112 | 83.9 | 62 | 60.4
2440 | 2266 | 68.1 | 112 | 83.9 | 61.9 | 60.3
2441 | 2267 | 68.1 | 111.9 | 83.9 | 61.8 | 60.3
2442 | 2268 | 68.2 | 111.9 | 83.9 | 61.9 | 60.4
2443 | 2269 | 68.2 | 112.1 | 83.8 | 61.8 | 60.6
2444 | 2270 | 68.2 | 111.9 | 83.7 | 61.5 | 60.8
2445 | 2271 | 68.1 | 111.7 | 83.8 | 61.4 | 60.7
2446 | 2272 | 68 | 111.6 | 83.7 | 61.2 | 60.3
2447 | 2273 | 67.9 | 111.6 | 83.5 | 61 | 59.9
2448 | 2274 | 67.9 | 111.9 | 83.5 | 61.2 | 59.6
2449 | 2275 | 68 | 112.1 | 83.5 | 61.2 | 59.4
2450 | 2276 | 68 | 112 | 83.4 | 61.3 | 59.2
2451 | 2277 | 67.9 | 111.9 | 83.2 | 61.5 | 59.5
2452 | 2278 | 67.6 | 111.4 | 83.2 | 61.6 | 59.8
2453 | 2279 | 67.3 | 111.2 | 83.2 | 61.7 | 60
2454 | 2280 | 67.1 | 111.2 | 83.1 | 61.7 | 59.9
2455 | 2281 | 66.9 | 111.2 | 83 | 61.7 | 59.8
2456 | 2282 | 66.9 | 111.6 | 82.9 | 61.8 | 59.9
2457 | 2283 | 66.7 | 111.7 | 83.1 | 61.8 | 60.1
2458 | 2284 | 66.4 | 111.5 | 83.2 | 61.7 | 60.2
2459 | 2285 | 66.1 | 111.4 | 83.1 | 61.6 | 60.2
2460 | 2286 | 66 | 111.5 | 83 | 61.6 | 60.2
2461 | 2287 | 66.2 | 111.7 | 83 | 61.6 | 60.3
2462 | 2288 | 66.3 | 111.8 | 83 | 61.6 | 60.3
2463 | 2289 | 66.4 | 111.9 | 83.1 | 61.6 | 60.2
2464 | 2290 | 66.7 | 112 | 83 | 61.6 | 60.1
2465 | 2291 | 66.9 | 112.1 | 82.9 | 61.6 | 60.1
2466 | 2292 | 67 | 112 | 82.9 | 61.5 | 60.2
2467 | 2293 | 67.1 | 111.8 | 82.9 | 61.6 | 60.2
2468 | 2294 | 67.3 | 112 | 82.9 | 61.6 | 60.2
2469 | 2295 | 67.3 | 112.2 | 82.8 | 61.6 | 60.1
2470 | 2296 | 67.3 | 112.2 | 82.7 | 61.5 | 60.1
2471 | 2297 | 67.4 | 112.2 | 82.6 | 61.5 | 59.9
2472 | 2298 | 67.5 | 112.1 | 82.5 | 61.4 | 59.8
2473 | 2299 | 67.6 | 112 | 82.4 | 61.5 | 59.8
2474 | 2300 | 67.5 | 112.1 | 82.3 | 61.6 | 59.8
2475 | 2301 | 67.2 | 112.1 | 82.3 | 61.5 | 59.7
2476 | 2302 | 67.2 | 112.5 | 82.3 | 61.5 | 59.8
2477 | 2303 | 67.2 | 112.7 | 82.3 | 61.5 | 59.9
2478 | 2304 | 67.2 | 112.7 | 82.3 | 61.4 | 60.1
2479 | 2305 | 66.9 | 112.3 | 82.2 | 61.3 | 60.1
2480 | 2306 | 66.6 | 112.2 | 82.1 | 61.2 | 60
2481 | 2307 | 66.5 | 112.3 | 82 | 61.2 | 59.8
2482 | 2308 | 66.6 | 112.3 | 81.9 | 61.2 | 59.4
2483 | 2309 | 66.6 | 112.4 | 81.8 | 61.3 | 59.3
2484 | 2310 | 66.6 | 112.7 | 81.8 | 61.3 | 59.4
2485 | 2311 | 66.5 | 112.8 | 81.7 | 61.3 | 59.3
2486 | 2312 | 66.7 | 113.1 | 81.7 | 61.2 | 59.2
2487 | 2313 | 66.8 | 113.2 | 81.7 | 61.1 | 59.3
2488 | 2314 | 66.9 | 112.9 | 81.7 | 61.1 | 59.4
2489 | 2315 | 66.8 | 113.2 | 81.6 | 61.1 | 59.5
2490 | 2316 | 67 | 113.6 | 81.6 | 61.2 | 59.6
2491 | 2317 | 67.1 | 113.3 | 81.5 | 61.1 | 59.7
2492.1 | 2318.1 | 67 | 113 | 81.5 | 61.1 | 59.5
2493.1 | 2319.1 | 66.9 | 112.9 | 81.4 | 61.1 | 59.4
2494.1 | 2320.1 | 66.6 | 112.7 | 81.3 | 61 | 59.4
2495.1 | 2321.1 | 66.7 | 112.5 | 81.2 | 61 | 59.4
2496.1 | 2322.1 | 66.7 | 112.8 | 81.1 | 61.1 | 59.5
2497.1 | 2323.1 | 66.8 | 112.7 | 81.1 | 61.1 | 59.6
2498.1 | 2324.1 | 66.5 | 112.6 | 81.1 | 61.1 | 59.6
2499.1 | 2325.1 | 66.4 | 112.4 | 81.1 | 61.1 | 59.6
2500.1 | 2326.1 | 66.4 | 112.5 | 81 | 61.1 | 59.5
2501.1 | 2327.1 | 66.4 | 112.6 | 81 | 61 | 59.5
2502.1 | 2328.1 | 65.8 | 112.5 | 81 | 60.9 | 59.4
2503.1 | 2329.1 | 65.5 | 112.4 | 81 | 60.6 | 59.4
2504.1 | 2330.1 | 65.5 | 112.5 | 81 | 60.6 | 59.6
2505.1 | 2331.1 | 65.2 | 112.3 | 81 | 60.6 | 59.6
2506.1 | 2332.1 | 65.1 | 112.3 | 81 | 60.7 | 59.6
2507.1 | 2333.1 | 65.2 | 112.5 | 81 | 60.6 | 59.5
2508.1 | 2334.1 | 65.4 | 112.6 | 80.9 | 60.4 | 59.5
2509.1 | 2335.1 | 65.5 | 112.8 | 80.9 | 60.4 | 59.4
2510.1 | 2336.1 | 65.6 | 113.1 | 80.9 | 60.5 | 59.3
2511.1 | 2337.1 | 65.8 | 113.3 | 80.8 | 60.5 | 59.1
2512.1 | 2338.1 | 66 | 113.4 | 80.6 | 60.5 | 59
2513.1 | 2339.1 | 66.2 | 113.5 | 80.6 | 60.6 | 59.2
2514.1 | 2340.1 | 66.3 | 113.6 | 80.7 | 60.8 | 59.3
2515.1 | 2341.1 | 66.4 | 113.5 | 80.5 | 60.8 | 59.3
2516.1 | 2342.1 | 66.5 | 113.6 | 80.4 | 60.8 | 59.4
2517.1 | 2343.1 | 66.1 | 113.3 | 80.3 | 60.8 | 59.5
2518.1 | 2344.1 | 65.6 | 112.9 | 80.2 | 60.7 | 59.4
2519.1 | 2345.1 | 65.6 | 112.6 | 80.2 | 60.5 | 59.4
2520.1 | 2346.1 | 65.3 | 112.5 | 80.1 | 60.5 | 59.5
2521.1 | 2347.1 | 65.3 | 112.4 | 80.1 | 60.4 | 59.4
2522.1 | 2348.1 | 65.1 | 112.5 | 80.1 | 60.4 | 59.3
2523.1 | 2349.1 | 65.1 | 112.5 | 80 | 60.5 | 59.2
2524.1 | 2350.1 | 65 | 112.6 | 79.9 | 60.5 | 59.1
2525.1 | 2351.1 | 64.9 | 112.6 | 79.9 | 60.4 | 59
2526.1 | 2352.1 | 64.9 | 112.8 | 79.8 | 60.4 | 59
2527.1 | 2353.1 | 65 | 113 | 79.7 | 60.4 | 59.2
2528.1 | 2354.1 | 65.1 | 112.8 | 79.7 | 60.4 | 59.4
2529.1 | 2355.1 | 64.8 | 112.5 | 79.7 | 60.4 | 59.3
2530.1 | 2356.1 | 64.8 | 112.5 | 79.6 | 60.3 | 59.2
2531.1 | 2357.1 | 65.1 | 112.4 | 79.4 | 60.2 | 58.9
2532.1 | 2358.1 | 65.2 | 112.6 | 79.3 | 60.3 | 58.9
2533.1 | 2359.1 | 65.1 | 112.6 | 79.3 | 60.4 | 59
2534.1 | 2360.1 | 64.6 | 112.5 | 79.2 | 60.2 | 59.1
2535.1 | 2361.1 | 64.5 | 112.1 | 79.2 | 60.1 | 59.1
2536.1 | 2362.1 | 64.4 | 111.9 | 79.1 | 60.1 | 59.1

## Test Facts
Last row in IRMS data sheets: | 15
Time when Penlight power was initiated: | 174